## Test Conditions
DESIREE-FIRE Test Number 28 - Circuit Simulator Data Only
Test Date: | 2009-08-10
DCSim DAQ Start Time | 15:18
DCSim Time for Synchronization | 15:38
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 15:36
Fire Time | 15:45
Offset | 0:27 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1620 | seconds
Heat Source Offset | 0:09 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 518 | seconds
Heat Source Stop Time | 16:49
Test Duration | 1:04 | hour:minutes:seconds
| 3820 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.20312 | 123.4497 | -66.7786 | 56.3187 | 0.012286 | -9.4002e-05 | 0.0011025 | 0.055645 | -0.0011772 | 0.064426 | 0.0077831 | -0.00027553 | -0.00076913 | 0.063159 | 0.0050876 | 0.063436 | -66.8526 | 0.028878 | -66.7781 | 56.2793 | 56.0922 | 56.2253 | -66.8879 | -66.8161 | 0.03241 | -66.8689 | 56.1665 | 56.2939 | 56.1552 | -66.9966 | -0.10932 | -0.039356 | -0.074008 | 0.000511 | 0.10983 | -0.22648 | -0.093397 | -0.218 | -0.15217 | -0.037501 | -0.090321 | 0.12768 | -0.024776 | -0.16351 | 123.0579 | 122.8707 | 123.0038 | 66.8074 | -123.2065 | 122.9451 | 123.0725 | 122.9337 | 66.811 | -123.3152
0.85938 | 123.3765 | -66.8015 | 56.3187 | -0.010607 | -9.4002e-05 | 0.0013163 | 0.055432 | -0.0011772 | 0.064426 | 0.0077831 | -0.00027553 | -0.00076913 | 0.062945 | 0.0050876 | 0.063222 | -66.848 | 0.0243 | -66.7552 | 56.2564 | 56.0189 | 56.1657 | -66.8467 | -66.8206 | 0.023253 | -66.8689 | 56.1619 | 56.2939 | 56.0132 | -66.992 | -0.045219 | -0.062248 | -0.046541 | 0.046292 | 0.091511 | -0.29974 | -0.15292 | -0.19053 | -0.15675 | -0.019191 | -0.067432 | 0.1231 | -0.024776 | -0.30545 | 123.0579 | 122.8204 | 122.9672 | 66.8258 | -123.1653 | 122.9634 | 123.0953 | 122.8147 | 66.8247 | -123.3107
1.7969 | 123.349 | -66.8106 | 56.337 | 0.0046549 | 0.000547 | 0.00088894 | 0.0565 | -0.0011772 | 0.063785 | -0.0074779 | 0.00015167 | -0.00012813 | 0.062731 | 0.0053012 | 0.062795 | -66.848 | 0.019721 | -66.7368 | 56.2473 | 55.9594 | 56.1886 | -66.6818 | -66.8069 | 0.018674 | -66.8689 | 56.1619 | 56.2847 | 55.9216 | -66.992 | 0.12878 | -0.089715 | -0.037386 | 0.07376 | -0.055018 | -0.37758 | -0.14834 | -0.18138 | -0.17506 | 0.0037 | -0.058277 | 0.1231 | -0.052244 | -0.41533 | 123.0579 | 122.77 | 122.9992 | 66.8303 | -123.0188 | 122.9725 | 123.0953 | 122.7323 | 66.8293 | -123.329
2.7969 | 123.3856 | -66.7648 | 56.3416 | -0.010607 | 0.000547 | 0.0011025 | 0.055432 | -0.0011772 | 0.063571 | 0.0077831 | 0.00015167 | -0.00034193 | 0.062518 | 0.0048738 | 0.062581 | -66.848 | 0.0243 | -66.7414 | 56.2564 | 56.0327 | 56.1932 | -66.8055 | -66.8069 | 0.023253 | -66.8551 | 56.1619 | 56.2939 | 55.9354 | -66.9966 | -0.040629 | -0.085136 | -0.083162 | 0.023405 | 0.064034 | -0.30889 | -0.14833 | -0.23173 | -0.17964 | -0.042076 | -0.090317 | 0.14142 | -0.047664 | -0.40617 | 123.0212 | 122.7975 | 122.9581 | 66.7891 | -123.147 | 122.9267 | 123.0587 | 122.7002 | 66.7881 | -123.3381
3.8594 | 123.381 | -66.8015 | 56.3278 | 0.0046549 | 0.0007606 | 0.0011025 | 0.055645 | -0.00074998 | 0.063785 | 0.00015261 | 0.00015167 | -0.00012813 | 0.062518 | 0.0050876 | 0.062795 | -66.8526 | 0.028878 | -66.7552 | 56.2473 | 55.9228 | 56.1429 | -66.8329 | -66.8069 | 0.023253 | -66.8643 | 56.1619 | 56.2893 | 55.9262 | -66.9966 | -0.031482 | -0.08056 | -0.051119 | 0.046292 | 0.077774 | -0.40506 | -0.18497 | -0.19511 | -0.1659 | -0.005455 | -0.062854 | 0.13226 | -0.03851 | -0.4016 | 123.0487 | 122.7242 | 122.9443 | 66.8303 | -123.1608 | 122.9634 | 123.0908 | 122.7277 | 66.8247 | -123.3244
4.7969 | 123.3032 | -66.8015 | 56.3599 | 0.012286 | 0.0003334 | 0.00088894 | 0.055432 | -0.00074998 | 0.063999 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.062518 | 0.0048738 | 0.062581 | -66.848 | 0.028878 | -66.7506 | 56.2473 | 55.9594 | 56.12 | -66.8146 | -66.8069 | 0.023253 | -66.8643 | 56.1619 | 56.2893 | 55.9537 | -66.9966 | -0.013166 | -0.1126 | -0.046541 | 0.05087 | 0.064036 | -0.40047 | -0.2399 | -0.19511 | -0.19795 | -0.005455 | -0.062854 | 0.13226 | -0.070553 | -0.40617 | 123.0487 | 122.7608 | 122.9214 | 66.8303 | -123.1745 | 122.9634 | 123.0908 | 122.7551 | 66.8247 | -123.3564
5.7969 | 123.4222 | -66.7786 | 56.3232 | 0.0046549 | 0.000547 | 0.0011025 | 0.055432 | -0.00096358 | 0.063571 | 0.00015261 | 0.00036527 | -0.00034193 | 0.062731 | 0.0050876 | 0.063222 | -66.8434 | 0.019721 | -66.746 | 56.2427 | 55.9548 | 56.1062 | -66.8146 | -66.8023 | 0.023253 | -66.8643 | 56.1619 | 56.2847 | 55.8163 | -66.9966 | -0.036055 | -0.08056 | -0.064851 | 0.032559 | 0.068614 | -0.36843 | -0.21702 | -0.218 | -0.16132 | -0.023765 | -0.085743 | 0.13226 | -0.038511 | -0.50691 | 123.0212 | 122.7334 | 122.8848 | 66.7983 | -123.1379 | 122.9405 | 123.0633 | 122.5949 | 66.8018 | -123.3198
6.7969 | 123.2895 | -66.8198 | 56.3828 | 0.0046549 | 0.0001196 | 0.0013163 | 0.055432 | -0.0016046 | 0.063999 | 0.0077831 | -0.00027553 | 8.5466e-05 | 0.062518 | 0.0053012 | 0.062154 | -66.848 | 0.028878 | -66.7643 | 56.2381 | 55.9273 | 56.0925 | -66.7963 | -66.8069 | 0.027831 | -66.8689 | 56.1573 | 56.2893 | 55.8163 | -67.0011 | 0.023459 | -0.14465 | -0.028231 | 0.055445 | 0.031986 | -0.45541 | -0.29026 | -0.18138 | -0.22541 | 0.012855 | -0.049122 | 0.13226 | -0.093441 | -0.56641 | 123.0579 | 122.7471 | 122.9123 | 66.8486 | -123.1791 | 122.9771 | 123.1091 | 122.6361 | 66.8476 | -123.3839
7.875 | 123.2758 | -66.7923 | 56.3553 | 0.012286 | 0.0003334 | 0.0013163 | 0.055218 | -0.001391 | 0.064212 | 0.00015261 | 0.00015167 | -0.00034193 | 0.062518 | 0.0053012 | 0.062581 | -66.8526 | 0.0243 | -66.7552 | 56.2381 | 55.964 | 56.1657 | -66.81 | -66.8069 | 0.027831 | -66.8689 | 56.1573 | 56.2939 | 55.8209 | -67.0011 | -0.017743 | -0.11718 | -0.060275 | 0.037136 | 0.054879 | -0.39131 | -0.18954 | -0.20885 | -0.19795 | -0.014611 | -0.076588 | 0.13226 | -0.061397 | -0.53437 | 123.0304 | 122.7563 | 122.958 | 66.8166 | -123.1653 | 122.9496 | 123.0862 | 122.6132 | 66.8201 | -123.3564
8.7969 | 123.3307 | -66.7877 | 56.3416 | -0.0029761 | -9.4002e-05 | 0.00088894 | 0.055645 | -0.00096358 | 0.063999 | 0.0077831 | 0.00036527 | -0.00012813 | 0.062518 | 0.0050876 | 0.062795 | -66.8434 | 0.0243 | -66.7506 | 56.2381 | 55.9548 | 56.1383 | -66.8146 | -66.8069 | 0.018674 | -66.8643 | 56.1619 | 56.2847 | 55.8209 | -66.9966 | -0.026899 | -0.10345 | -0.055695 | 0.037137 | 0.064036 | -0.38674 | -0.20328 | -0.20885 | -0.17964 | -0.019188 | -0.076587 | 0.13226 | -0.056822 | -0.52064 | 123.0258 | 122.7425 | 122.926 | 66.812 | -123.1562 | 122.9496 | 123.0725 | 122.6086 | 66.8064 | -123.3381
9.8594 | 123.3582 | -66.7969 | 56.282 | -0.0029761 | 0.000547 | 0.0013163 | 0.055645 | -0.00096358 | 0.063571 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.062518 | 0.0050876 | 0.063008 | -66.8434 | 0.0243 | -66.7552 | 56.2427 | 55.9686 | 56.1612 | -66.8192 | -66.8069 | 0.023253 | -66.8689 | 56.1619 | 56.2893 | 55.8209 | -66.992 | -0.022323 | -0.039361 | -0.04654 | 0.041714 | 0.064037 | -0.31349 | -0.12087 | -0.19511 | -0.12013 | -0.010033 | -0.07201 | 0.1231 | 0.007267 | -0.46113 | 123.0396 | 122.7654 | 122.958 | 66.8212 | -123.1012 | 122.9588 | 123.0862 | 122.6178 | 66.8201 | -123.274
10.7969 | 123.2941 | -66.8152 | 56.369 | -0.0029761 | 0.0003334 | 0.00067514 | 0.055004 | -0.0011772 | 0.063571 | 0.00015261 | 0.00036527 | -0.00034193 | 0.062304 | 0.0050876 | 0.062367 | -66.8434 | 0.0243 | -66.7552 | 56.2427 | 55.9365 | 56.1291 | -66.81 | -66.8069 | 0.023253 | -66.8643 | 56.1665 | 56.2847 | 55.8209 | -67.0011 | 0.005146 | -0.12634 | -0.028229 | 0.060025 | 0.054879 | -0.43252 | -0.2399 | -0.18596 | -0.20252 | 0.008278 | -0.049121 | 0.13684 | -0.084288 | -0.5481 | 123.0579 | 122.7517 | 122.9443 | 66.8395 | -123.1791 | 122.9817 | 123.0999 | 122.6361 | 66.8384 | -123.3702
11.7969 | 123.3398 | -66.806 | 56.3461 | 0.0046549 | 0.000547 | 0.0013163 | 0.055432 | -0.0011772 | 0.063785 | 0.0077831 | 0.00015167 | -0.00012813 | 0.062518 | 0.0050876 | 0.063008 | -66.8434 | 0.0243 | -66.7552 | 56.2335 | 55.9411 | 56.1429 | -66.7688 | -66.8069 | 0.023253 | -66.8551 | 56.1619 | 56.2893 | 55.8301 | -67.0011 | 0.0372 | -0.11261 | -0.037385 | 0.050869 | 0.013669 | -0.40505 | -0.20328 | -0.19511 | -0.18421 | -0.000878 | -0.049119 | 0.14599 | -0.05682 | -0.51606 | 123.0396 | 122.7471 | 122.9489 | 66.8303 | -123.115 | 122.9679 | 123.0953 | 122.6361 | 66.8293 | -123.3473
12.7969 | 123.2986 | -66.8381 | 56.337 | -0.0029761 | 0.000547 | 0.0011025 | 0.055645 | -0.001391 | 0.063999 | 0.0077831 | 0.00015167 | -0.00012813 | 0.062518 | 0.0050876 | 0.062581 | -66.848 | 0.028878 | -66.7506 | 56.2473 | 55.9411 | 56.1657 | -66.7917 | -66.8069 | 0.018674 | -66.8551 | 56.1665 | 56.2847 | 55.8255 | -66.992 | 0.046349 | -0.089715 | -0.00992 | 0.087491 | 0.041142 | -0.3959 | -0.17123 | -0.15391 | -0.17048 | 0.031166 | -0.017075 | 0.13684 | -0.052244 | -0.51148 | 123.0853 | 122.7792 | 123.0038 | 66.867 | -123.1287 | 123.0046 | 123.1228 | 122.6636 | 66.8567 | -123.329
13.8594 | 123.381 | -66.7969 | 56.3278 | 0.019917 | 0.000547 | 0.0013163 | 0.055645 | -0.0011772 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.062518 | 0.0050876 | 0.062367 | -66.8434 | 0.0243 | -66.7552 | 56.2427 | 55.9686 | 56.1154 | -66.7734 | -66.8023 | 0.023253 | -66.8689 | 56.1619 | 56.2893 | 55.8209 | -67.0011 | 0.023466 | -0.085138 | -0.04654 | 0.041714 | 0.018248 | -0.35927 | -0.21244 | -0.20427 | -0.1659 | -0.005454 | -0.07201 | 0.13226 | -0.03851 | -0.50691 | 123.0396 | 122.7654 | 122.9123 | 66.8212 | -123.1012 | 122.9588 | 123.0862 | 122.6178 | 66.8201 | -123.329
14.7969 | 123.3261 | -66.806 | 56.3507 | 0.0046549 | 0.0003334 | 0.00088894 | 0.055004 | -0.001391 | 0.063999 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062518 | 0.0053012 | 0.062367 | -66.8434 | 0.0243 | -66.7506 | 56.2427 | 55.9457 | 56.1016 | -66.8238 | -66.8023 | 0.027831 | -66.8643 | 56.1619 | 56.2893 | 55.8209 | -66.992 | -0.017747 | -0.10803 | -0.037385 | 0.055447 | 0.073194 | -0.40505 | -0.24906 | -0.18596 | -0.18879 | 0.003701 | -0.058277 | 0.12768 | -0.061398 | -0.52979 | 123.0487 | 122.7517 | 122.9077 | 66.8303 | -123.1745 | 122.9679 | 123.0953 | 122.6269 | 66.8339 | -123.3427
15.7969 | 123.4268 | -66.774 | 56.3232 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055645 | -0.0011772 | 0.063785 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062731 | 0.0050876 | 0.063008 | -66.848 | 0.0243 | -66.7597 | 56.2381 | 55.9273 | 56.1474 | -66.7963 | -66.8023 | 0.027831 | -66.8689 | 56.1619 | 56.2802 | 55.8255 | -67.0011 | -0.022317 | -0.085138 | -0.074007 | 0.014247 | 0.036564 | -0.3959 | -0.17581 | -0.22716 | -0.16132 | -0.028342 | -0.094898 | 0.13226 | -0.043089 | -0.49775 | 123.0121 | 122.7013 | 122.9214 | 66.7983 | -123.1195 | 122.9359 | 123.0541 | 122.5995 | 66.8018 | -123.3244
16.8594 | 123.4039 | -66.7786 | 56.3278 | 0.0046549 | 0.0003334 | 0.0013163 | 0.055432 | -0.0011772 | 0.063785 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0050876 | 0.062581 | -66.8343 | 0.015142 | -66.7506 | 56.2427 | 55.8999 | 56.0833 | -66.7826 | -66.8069 | 0.018674 | -66.8689 | 56.1528 | 56.2939 | 55.8301 | -66.9966 | -0.004003 | -0.085138 | -0.055694 | 0.027981 | 0.031984 | -0.42795 | -0.24449 | -0.218 | -0.17506 | -0.028344 | -0.090321 | 0.12768 | -0.033931 | -0.49775 | 123.0212 | 122.6784 | 122.8619 | 66.7937 | -123.1104 | 122.9313 | 123.0725 | 122.6086 | 66.7972 | -123.3244
17.7969 | 123.2529 | -66.8472 | 56.3278 | 0.0046549 | 0.0003334 | 0.0013163 | 0.055218 | -0.00096358 | 0.063571 | 0.00015261 | 0.00015167 | -0.00055553 | 0.06209 | 0.0053012 | 0.062367 | -66.848 | 0.0243 | -66.7506 | 56.2473 | 55.9823 | 56.1337 | -66.8375 | -66.8023 | 0.023253 | -66.8643 | 56.1573 | 56.2847 | 55.8255 | -67.0011 | 0.009715 | -0.08056 | -0.000765 | 0.096646 | 0.086931 | -0.34553 | -0.19412 | -0.15391 | -0.17048 | 0.0449 | -0.017078 | 0.13684 | -0.043089 | -0.50233 | 123.0945 | 122.8295 | 122.9809 | 66.8715 | -123.1653 | 123.0046 | 123.132 | 122.6727 | 66.8705 | -123.329
18.7969 | 123.3261 | -66.8152 | 56.337 | 0.012286 | 0.0003334 | 0.0011025 | 0.055432 | -0.0011772 | 0.063785 | 0.00015261 | -0.00048933 | 8.5466e-05 | 0.062518 | 0.0053012 | 0.062581 | -66.8434 | 0.0243 | -66.7506 | 56.2427 | 55.9319 | 56.1566 | -66.8329 | -66.8069 | 0.023253 | -66.8597 | 56.1665 | 56.2939 | 55.8209 | -66.9966 | -0.017749 | -0.094293 | -0.028229 | 0.064603 | 0.082352 | -0.40505 | -0.18039 | -0.18138 | -0.17048 | 0.008278 | -0.044542 | 0.13684 | -0.043086 | -0.51606 | 123.0579 | 122.7471 | 122.9718 | 66.8395 | -123.1699 | 122.9817 | 123.1091 | 122.6361 | 66.8384 | -123.3335
19.7969 | 123.2941 | -66.8152 | 56.3599 | 0.012286 | 0.0007606 | 0.0013163 | 0.054791 | -0.0011772 | 0.063785 | -0.0074779 | -0.00027553 | -0.00034193 | 0.06209 | 0.0053012 | 0.062367 | -66.8434 | 0.0243 | -66.7506 | 56.2473 | 55.9686 | 56.1566 | -66.778 | -66.8069 | 0.03241 | -66.8643 | 56.1619 | 56.2893 | 55.8255 | -66.992 | 0.037198 | -0.1126 | -0.028229 | 0.064603 | 0.027405 | -0.39131 | -0.20327 | -0.1768 | -0.19795 | 0.008278 | -0.049121 | 0.12768 | -0.070553 | -0.53437 | 123.0624 | 122.7837 | 122.9718 | 66.8395 | -123.1379 | 122.9771 | 123.1045 | 122.6407 | 66.8476 | -123.3518
20.8594 | 123.436 | -66.7831 | 56.3049 | -0.0029761 | 0.0001196 | 0.0011025 | 0.055432 | -0.00096358 | 0.063999 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0053012 | 0.062367 | -66.8434 | 0.019721 | -66.7506 | 56.2427 | 55.9365 | 56.1749 | -66.7871 | -66.7977 | 0.018674 | -66.8643 | 56.1573 | 56.2893 | 55.8255 | -66.9966 | -0.004004 | -0.06225 | -0.060273 | 0.032559 | 0.036563 | -0.36843 | -0.13003 | -0.21342 | -0.14759 | -0.014608 | -0.081165 | 0.13226 | -0.015622 | -0.47944 | 123.0258 | 122.7196 | 122.958 | 66.8029 | -123.0921 | 122.9405 | 123.0725 | 122.6086 | 66.8018 | -123.3015
21.7969 | 123.3856 | -66.7923 | 56.3141 | 0.0046549 | 0.0001196 | 0.00088894 | 0.055218 | -0.0011772 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.062304 | 0.0053012 | 0.062367 | -66.8434 | 0.019721 | -66.7552 | 56.2427 | 55.964 | 56.1703 | -66.8329 | -66.8069 | 0.027831 | -66.8643 | 56.1573 | 56.2847 | 55.8255 | -67.0011 | -0.040638 | -0.071405 | -0.051118 | 0.037136 | 0.077774 | -0.35011 | -0.14376 | -0.20885 | -0.15675 | -0.014611 | -0.07201 | 0.13684 | -0.029356 | -0.48859 | 123.035 | 122.7563 | 122.9626 | 66.812 | -123.147 | 122.9496 | 123.077 | 122.6178 | 66.8201 | -123.3152
22.7969 | 123.3398 | -66.8152 | 56.3461 | 0.0046549 | 0.000547 | 0.0011025 | 0.055432 | -0.0011772 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0055148 | 0.062367 | -66.8388 | 0.028878 | -66.746 | 56.2427 | 55.9365 | 56.1429 | -66.8284 | -66.8069 | 0.023253 | -66.8689 | 56.1528 | 56.2893 | 55.8209 | -66.992 | -0.01317 | -0.10345 | -0.023651 | 0.069181 | 0.082351 | -0.40963 | -0.20328 | -0.1768 | -0.19337 | 0.008278 | -0.053699 | 0.1231 | -0.05682 | -0.52522 | 123.0579 | 122.7517 | 122.958 | 66.8441 | -123.1745 | 122.9679 | 123.1045 | 122.6361 | 66.8384 | -123.3381
23.7969 | 123.2712 | -66.8015 | 56.3507 | 0.012286 | 0.0001196 | 0.0011025 | 0.055218 | -0.0011772 | 0.063571 | 0.015414 | 0.00015167 | -0.00034193 | 0.06209 | 0.0053012 | 0.062154 | -66.848 | 0.0243 | -66.7506 | 56.2381 | 55.9273 | 56.1337 | -66.81 | -66.8069 | 0.018674 | -66.8597 | 56.1573 | 56.2847 | 55.8255 | -66.9966 | -0.008587 | -0.1126 | -0.046541 | 0.05087 | 0.059457 | -0.42336 | -0.21701 | -0.19511 | -0.19337 | -0.005455 | -0.058275 | 0.13684 | -0.065977 | -0.52521 | 123.0396 | 122.7288 | 122.9351 | 66.8258 | -123.1607 | 122.9588 | 123.0862 | 122.6269 | 66.8201 | -123.3473
24.7969 | 123.2803 | -66.8289 | 56.3553 | -0.0029761 | 0.0001196 | 0.0011025 | 0.055218 | -0.00096358 | 0.063785 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0053012 | 0.062795 | -66.8434 | 0.019721 | -66.7506 | 56.2473 | 55.964 | 56.1429 | -66.8421 | -66.8023 | 0.023253 | -66.8597 | 56.1665 | 56.2893 | 55.8255 | -66.992 | -0.013175 | -0.10803 | -0.014497 | 0.078335 | 0.09151 | -0.39131 | -0.21243 | -0.16307 | -0.18879 | 0.026589 | -0.03081 | 0.13226 | -0.065976 | -0.52979 | 123.0762 | 122.7929 | 122.9718 | 66.8486 | -123.1974 | 122.9954 | 123.1182 | 122.6544 | 66.8522 | -123.3473
25.8594 | 123.4131 | -66.7877 | 56.3324 | -0.0029761 | 0.0003334 | 0.0011025 | 0.055218 | -0.0011772 | 0.063358 | -0.0074779 | -6.1934e-05 | -0.00012813 | 0.06209 | 0.0053012 | 0.062367 | -66.8434 | 0.0243 | -66.7597 | 56.2381 | 55.9411 | 56.1245 | -66.8238 | -66.8069 | 0.03241 | -66.8689 | 56.1573 | 56.2847 | 55.8163 | -66.992 | -0.036057 | -0.094293 | -0.055695 | 0.02798 | 0.064037 | -0.39132 | -0.20786 | -0.20427 | -0.17506 | -0.019188 | -0.081165 | 0.1231 | -0.047666 | -0.51606 | 123.0258 | 122.7288 | 122.9123 | 66.812 | -123.1562 | 122.9451 | 123.0725 | 122.6041 | 66.8201 | -123.3244
26.7969 | 123.317 | -66.8152 | 56.3278 | -0.0029761 | 0.0003334 | 0.0013163 | 0.055218 | -0.0011772 | 0.063785 | 0.015414 | 0.00015167 | -0.00034193 | 0.06209 | 0.0053012 | 0.062581 | -66.8434 | 0.028878 | -66.7552 | 56.2473 | 55.964 | 56.152 | -66.8329 | -66.7977 | 0.023253 | -66.8597 | 56.1573 | 56.2893 | 55.8163 | -67.0011 | -0.017749 | -0.08056 | -0.028229 | 0.060025 | 0.077774 | -0.36385 | -0.17581 | -0.18596 | -0.17048 | 0.017436 | -0.044542 | 0.14141 | -0.03851 | -0.51148 | 123.0624 | 122.7792 | 122.9672 | 66.8441 | -123.1608 | 122.9725 | 123.1045 | 122.6315 | 66.8384 | -123.329
27.7969 | 123.262 | -66.8838 | 56.3049 | -0.0029761 | 0.0003334 | 0.0013163 | 0.055432 | -0.00096358 | 0.063785 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0050876 | 0.062367 | -66.8434 | 0.028878 | -66.7506 | 56.2427 | 55.9594 | 56.1657 | -66.8238 | -66.8069 | 0.023253 | -66.8643 | 56.1573 | 56.2802 | 55.8163 | -67.0057 | 0.060073 | -0.06225 | 0.040435 | 0.13327 | 0.073194 | -0.34554 | -0.13919 | -0.12187 | -0.14759 | 0.076942 | 0.019543 | 0.14142 | -0.024779 | -0.4886 | 123.1265 | 122.8432 | 123.0496 | 66.9127 | -123.1287 | 123.0412 | 123.164 | 122.7002 | 66.9071 | -123.3107
28.7969 | 123.317 | -66.806 | 56.3416 | -0.0029761 | 0.0003334 | 0.0015299 | 0.055004 | -0.00074998 | 0.063785 | 0.00015261 | 0.00015167 | -0.00034193 | 0.062304 | 0.0057286 | 0.062367 | -66.8434 | 0.019721 | -66.7506 | 56.2381 | 55.9411 | 56.1429 | -66.8284 | -66.8069 | 0.03241 | -66.8597 | 56.1619 | 56.2847 | 55.8255 | -67.0057 | -0.022326 | -0.10345 | -0.037385 | 0.055447 | 0.077773 | -0.40047 | -0.1987 | -0.19969 | -0.17964 | -0.000878 | -0.053698 | 0.14599 | -0.056822 | -0.51606 | 123.0441 | 122.7471 | 122.9489 | 66.8258 | -123.1699 | 122.9679 | 123.0908 | 122.6315 | 66.8384 | -123.3473
29.8594 | 123.4131 | -66.7786 | 56.2958 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055432 | -0.0011772 | 0.063358 | 0.00015261 | 0.00036527 | -0.00012813 | 0.062304 | 0.0057286 | 0.062367 | -66.8434 | 0.019721 | -66.7643 | 56.2427 | 55.9319 | 56.1612 | -66.8192 | -66.8069 | 0.023253 | -66.8643 | 56.1573 | 56.2847 | 55.8255 | -67.0011 | -0.040634 | -0.053094 | -0.064851 | 0.014246 | 0.05488 | -0.36385 | -0.13461 | -0.22258 | -0.13844 | -0.028344 | -0.085743 | 0.13684 | -0.011045 | -0.47028 | 123.0212 | 122.7105 | 122.9397 | 66.7983 | -123.115 | 122.9359 | 123.0633 | 122.6041 | 66.8018 | -123.2969
30.7969 | 123.2758 | -66.8289 | 56.3507 | -0.0029761 | 0.0003334 | 0.0013163 | 0.055218 | -0.00096358 | 0.063358 | 0.00015261 | 0.00015167 | -0.00034193 | 0.062304 | 0.0053012 | 0.062154 | -66.8388 | 0.0243 | -66.746 | 56.2427 | 55.909 | 56.1429 | -66.7551 | -66.7977 | 0.023253 | -66.8597 | 56.1619 | 56.2847 | 55.8209 | -67.0011 | 0.073825 | -0.10803 | -0.009919 | 0.082913 | 0.009088 | -0.44168 | -0.20785 | -0.17222 | -0.18879 | 0.031168 | -0.03081 | 0.14141 | -0.065977 | -0.52979 | 123.0716 | 122.7379 | 122.9718 | 66.8532 | -123.1058 | 122.9908 | 123.1136 | 122.6498 | 66.8522 | -123.3519
31.7969 | 123.3078 | -66.8243 | 56.3324 | -0.0029761 | 0.0001196 | 0.0011025 | 0.055218 | -0.001391 | 0.063785 | -0.0074779 | 0.00015167 | -0.00034193 | 0.062518 | 0.0057286 | 0.062367 | -66.8343 | 0.0243 | -66.7506 | 56.2427 | 55.9365 | 56.1383 | -66.8055 | -66.8023 | 0.023253 | -66.8643 | 56.1619 | 56.2893 | 55.8163 | -67.0103 | 0.01888 | -0.089715 | -0.009917 | 0.073758 | 0.054878 | -0.3959 | -0.19412 | -0.18596 | -0.17048 | 0.022012 | -0.039966 | 0.14599 | -0.043087 | -0.51606 | 123.067 | 122.7608 | 122.9626 | 66.8486 | -123.1379 | 122.9863 | 123.1137 | 122.6407 | 66.8476 | -123.3427
32.8125 | 123.3032 | -66.8381 | 56.3416 | 0.0046549 | 0.0003334 | 0.00067514 | 0.055218 | -0.0011772 | 0.063999 | 0.00015261 | 0.00015167 | -0.00034193 | 0.062304 | 0.0057286 | 0.062367 | -66.8343 | 0.028878 | -66.7506 | 56.2289 | 55.9273 | 56.0833 | -66.8146 | -66.8069 | 0.027831 | -66.8597 | 56.1573 | 56.2893 | 55.8255 | -67.0011 | 0.023455 | -0.11261 | 0.003816 | 0.087491 | 0.064036 | -0.41421 | -0.25822 | -0.16307 | -0.18421 | 0.031166 | -0.021654 | 0.14141 | -0.052243 | -0.51606 | 123.067 | 122.7654 | 122.9214 | 66.867 | -123.1562 | 122.9954 | 123.1274 | 122.6636 | 66.8659 | -123.3427
33.8438 | 123.4039 | -66.774 | 56.3049 | 0.0046549 | 0.0001196 | 0.0011025 | 0.055432 | -0.0011772 | 0.063571 | 0.015414 | 0.00015167 | -0.00034193 | 0.062304 | 0.0055148 | 0.062154 | -66.8434 | 0.019721 | -66.7414 | 56.2381 | 55.9411 | 56.1291 | -66.8329 | -66.7977 | 0.018674 | -66.8597 | 56.1619 | 56.2847 | 55.8163 | -66.9966 | -0.058948 | -0.066828 | -0.069428 | 0.03256 | 0.091508 | -0.36385 | -0.17581 | -0.22258 | -0.14301 | -0.023763 | -0.085741 | 0.13684 | -0.020201 | -0.4886 | 123.0121 | 122.7151 | 122.9031 | 66.7937 | -123.1379 | 122.9359 | 123.0587 | 122.5903 | 66.7927 | -123.3015
34.7969 | 123.3719 | -66.806 | 56.3049 | -0.0029761 | 0.0003334 | 0.00088894 | 0.055218 | -0.001391 | 0.063999 | 0.00015261 | -6.1934e-05 | -0.00012813 | 0.062304 | 0.0057286 | 0.06194 | -66.8434 | 0.028878 | -66.7552 | 56.2473 | 55.9457 | 56.1566 | -66.8192 | -66.8023 | 0.027831 | -66.8643 | 56.1573 | 56.2847 | 55.8209 | -66.9966 | -0.013168 | -0.057672 | -0.037385 | 0.050869 | 0.064037 | -0.35927 | -0.14834 | -0.19053 | -0.14759 | 0.003701 | -0.058277 | 0.13226 | -0.020201 | -0.48402 | 123.0533 | 122.7517 | 122.9626 | 66.8349 | -123.1241 | 122.9634 | 123.0908 | 122.6269 | 66.8339 | -123.3015
35.8594 | 123.3215 | -66.8198 | 56.3736 | -0.0029761 | 0.0001196 | 0.00088894 | 0.055432 | -0.001391 | 0.063571 | -0.0074779 | -6.1934e-05 | -0.00012813 | 0.062304 | 0.0053012 | 0.062154 | -66.8434 | 0.028878 | -66.7506 | 56.2427 | 55.9228 | 56.1429 | -66.8284 | -66.7977 | 0.023253 | -66.8643 | 56.1619 | 56.2847 | 55.8118 | -67.0011 | -0.008593 | -0.13091 | -0.023652 | 0.06918 | 0.077773 | -0.45083 | -0.23074 | -0.18138 | -0.21168 | 0.022013 | -0.044544 | 0.13684 | -0.088865 | -0.56184 | 123.0624 | 122.7425 | 122.9626 | 66.8486 | -123.202 | 122.9817 | 123.1045 | 122.6315 | 66.843 | -123.3747
36.7969 | 123.2941 | -66.8381 | 56.3187 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055432 | -0.00074998 | 0.063785 | 0.00015261 | 0.00015167 | -0.00034193 | 0.062518 | 0.0057286 | 0.062367 | -66.8388 | 0.0243 | -66.746 | 56.2473 | 55.9411 | 56.1886 | -66.778 | -66.8023 | 0.023253 | -66.8597 | 56.1619 | 56.2939 | 55.8072 | -67.0011 | 0.060086 | -0.071405 | -0.000763 | 0.092069 | 0.031983 | -0.37759 | -0.13003 | -0.16307 | -0.15675 | 0.035745 | -0.021654 | 0.14141 | -0.024776 | -0.51149 | 123.0853 | 122.7792 | 123.0267 | 66.8624 | -123.0967 | 123 | 123.132 | 122.6453 | 66.8613 | -123.3198
37.7969 | 123.3627 | -66.806 | 56.2958 | -0.0029761 | 0.000547 | 0.0013163 | 0.055218 | -0.00096358 | 0.063358 | -0.015108 | -0.00027553 | -0.00034193 | 0.06209 | 0.0059422 | 0.062367 | -66.8434 | 0.019721 | -66.746 | 56.2427 | 55.9365 | 56.1337 | -66.8009 | -66.7977 | 0.018674 | -66.8735 | 56.1573 | 56.2893 | 55.8209 | -67.0011 | 0.005148 | -0.053094 | -0.037385 | 0.060025 | 0.054877 | -0.35927 | -0.16208 | -0.19511 | -0.13844 | 0.00828 | -0.067434 | 0.12768 | -0.006466 | -0.47486 | 123.0487 | 122.7425 | 122.9397 | 66.8258 | -123.0967 | 122.9634 | 123.0953 | 122.6269 | 66.8247 | -123.2969
38.8594 | 123.3078 | -66.8106 | 56.3507 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055218 | -0.0016046 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.06209 | 0.0055148 | 0.062367 | -66.8388 | 0.033457 | -66.7414 | 56.2427 | 55.9502 | 56.1291 | -66.8421 | -66.7932 | 0.014095 | -66.8597 | 56.1619 | 56.2893 | 55.8163 | -67.0011 | -0.031485 | -0.10803 | -0.028229 | 0.069181 | 0.10067 | -0.40047 | -0.22159 | -0.19053 | -0.18879 | 0.017436 | -0.04912 | 0.14141 | -0.061398 | -0.53437 | 123.0533 | 122.7608 | 122.9397 | 66.8441 | -123.1928 | 122.9725 | 123.0999 | 122.6269 | 66.8247 | -123.3519
39.7969 | 123.2758 | -66.861 | 56.3004 | -0.0029761 | 0.0003334 | 0.0013163 | 0.054791 | -0.0011772 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.06209 | 0.0053012 | 0.062367 | -66.8388 | 0.028878 | -66.7506 | 56.2427 | 55.964 | 56.1383 | -66.7871 | -66.8023 | 0.014095 | -66.8597 | 56.1528 | 56.2847 | 55.8163 | -66.9966 | 0.073816 | -0.057672 | 0.022125 | 0.11038 | 0.036563 | -0.33638 | -0.16208 | -0.1356 | -0.14759 | 0.058633 | 0.001234 | 0.13684 | -0.015623 | -0.48402 | 123.1036 | 122.8249 | 122.9992 | 66.8898 | -123.0875 | 123.0137 | 123.1457 | 122.6773 | 66.8751 | -123.2969
40.7969 | 123.4177 | -66.8015 | 56.2912 | -0.010607 | 0.0003334 | 0.0011025 | 0.055432 | -0.0011772 | 0.063358 | 0.00015261 | -0.00027553 | -0.00034193 | 0.062304 | 0.0057286 | 0.062581 | -66.8388 | 0.028878 | -66.7506 | 56.2381 | 55.9228 | 56.1383 | -66.778 | -66.7932 | 0.018674 | -66.8597 | 56.1619 | 56.2847 | 55.8255 | -67.0057 | 0.023465 | -0.053095 | -0.037384 | 0.05087 | 0.027405 | -0.36843 | -0.15292 | -0.20427 | -0.12928 | 0.008281 | -0.058275 | 0.14599 | -0.006468 | -0.4657 | 123.0396 | 122.7242 | 122.9397 | 66.8303 | -123.0692 | 122.9634 | 123.0862 | 122.6269 | 66.8201 | -123.2969
41.7969 | 123.3261 | -66.8289 | 56.3095 | -0.0029761 | 0.0001196 | 0.0015299 | 0.055218 | -0.0011772 | 0.063785 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.062518 | 0.0057286 | 0.062154 | -66.8297 | 0.0243 | -66.7506 | 56.2381 | 55.9411 | 56.1566 | -66.8467 | -66.8023 | 0.018674 | -66.8597 | 56.1573 | 56.2802 | 55.8209 | -67.0011 | -0.017754 | -0.071405 | -0.000762 | 0.078335 | 0.096089 | -0.36843 | -0.15292 | -0.17222 | -0.15217 | 0.026589 | -0.03081 | 0.14141 | -0.029356 | -0.48859 | 123.067 | 122.77 | 122.9855 | 66.8532 | -123.1562 | 122.9863 | 123.1091 | 122.6498 | 66.8476 | -123.3107
42.875 | 123.3627 | -66.8015 | 56.2912 | -0.0029761 | -9.4002e-05 | 0.00088894 | 0.055218 | -0.0011772 | 0.063571 | 0.0077831 | -6.1934e-05 | -0.00012813 | 0.061877 | 0.0059422 | 0.062367 | -66.8388 | 0.0243 | -66.746 | 56.2427 | 55.9686 | 56.1429 | -66.8238 | -66.7932 | 0.018674 | -66.8735 | 56.1619 | 56.2847 | 55.8163 | -67.0011 | -0.022324 | -0.048517 | -0.037384 | 0.055448 | 0.077772 | -0.32265 | -0.14835 | -0.19969 | -0.12928 | 0.008281 | -0.072011 | 0.12768 | -0.006468 | -0.47486 | 123.0441 | 122.77 | 122.9443 | 66.8258 | -123.115 | 122.9634 | 123.0862 | 122.6178 | 66.8201 | -123.2923
43.7969 | 123.3124 | -66.8289 | 56.3278 | 0.012286 | -0.0003076 | 0.0013163 | 0.055218 | -0.00096358 | 0.063999 | -0.0074779 | 0.00015167 | -0.00034193 | 0.06209 | 0.0057286 | 0.062154 | -66.8388 | 0.019721 | -66.746 | 56.2381 | 55.9457 | 56.1245 | -66.8421 | -66.8023 | 0.023253 | -66.8551 | 56.1665 | 56.2802 | 55.8209 | -66.9966 | -0.013175 | -0.089716 | -0.009919 | 0.082913 | 0.096088 | -0.38216 | -0.20328 | -0.16765 | -0.16132 | 0.026589 | -0.026231 | 0.14142 | -0.047667 | -0.50691 | 123.067 | 122.7746 | 122.9535 | 66.8486 | -123.1699 | 122.9954 | 123.1091 | 122.6498 | 66.8522 | -123.3244
44.8594 | 123.2758 | -66.8289 | 56.3461 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055432 | -0.001391 | 0.063571 | 0.00015261 | -0.00027553 | -0.00055553 | 0.06209 | 0.0059422 | 0.062154 | -66.8343 | 0.0243 | -66.7506 | 56.2427 | 55.9136 | 56.152 | -66.8375 | -66.8023 | 0.023253 | -66.8643 | 56.1619 | 56.2893 | 55.8209 | -66.9966 | -0.008596 | -0.10345 | -0.00534 | 0.078335 | 0.086931 | -0.43252 | -0.19412 | -0.16765 | -0.18421 | 0.026589 | -0.035389 | 0.13226 | -0.05682 | -0.52522 | 123.0716 | 122.7425 | 122.9809 | 66.8532 | -123.1836 | 122.9908 | 123.1182 | 122.6498 | 66.8522 | -123.3427
45.7969 | 123.3856 | -66.8015 | 56.3004 | -0.010607 | 0.0001196 | 0.0011025 | 0.055218 | -0.0011772 | 0.063999 | 0.0077831 | -0.00027553 | -0.00055553 | 0.062304 | 0.0057286 | 0.062154 | -66.8434 | 0.028878 | -66.7506 | 56.2427 | 55.9502 | 56.1291 | -66.7459 | -66.7977 | 0.027831 | -66.8597 | 56.1573 | 56.2847 | 55.8209 | -67.0011 | 0.055518 | -0.057672 | -0.041962 | 0.05087 | -0.004648 | -0.35012 | -0.17124 | -0.19969 | -0.14301 | 0.003703 | -0.058275 | 0.14141 | -0.015623 | -0.47944 | 123.0441 | 122.7517 | 122.9306 | 66.8303 | -123.0463 | 122.9588 | 123.0862 | 122.6224 | 66.8293 | -123.3015
46.7969 | 123.381 | -66.7969 | 56.2958 | 0.0046549 | 0.0001196 | 0.00088894 | 0.055432 | -0.0016046 | 0.063571 | 0.0077831 | -6.1934e-05 | -0.00012813 | 0.062304 | 0.0059422 | 0.062154 | -66.8434 | 0.028878 | -66.746 | 56.2335 | 55.9594 | 56.1245 | -66.7871 | -66.8023 | 0.018674 | -66.8597 | 56.1573 | 56.2847 | 55.8209 | -67.0057 | 0.009729 | -0.062251 | -0.04654 | 0.05087 | 0.041141 | -0.33638 | -0.17124 | -0.20885 | -0.13844 | -0.005454 | -0.062853 | 0.14599 | -0.011045 | -0.47486 | 123.0304 | 122.7563 | 122.9214 | 66.8258 | -123.0829 | 122.9542 | 123.0816 | 122.6178 | 66.8155 | -123.3015
47.8906 | 123.2986 | -66.8106 | 56.3553 | -0.010607 | 0.0001196 | 0.0013163 | 0.055432 | -0.0011772 | 0.063571 | -0.0074779 | -0.00027553 | -0.00034193 | 0.061877 | 0.0059422 | 0.062367 | -66.8343 | 0.019721 | -66.7597 | 56.2381 | 55.9457 | 56.1474 | -66.8329 | -66.7977 | 0.018674 | -66.8643 | 56.1619 | 56.2847 | 55.8163 | -67.0011 | -0.022327 | -0.11718 | -0.02365 | 0.050868 | 0.073195 | -0.40963 | -0.20785 | -0.19053 | -0.19337 | 0.012858 | -0.053699 | 0.13684 | -0.070555 | -0.53895 | 123.0487 | 122.7563 | 122.958 | 66.8303 | -123.1882 | 122.9725 | 123.0953 | 122.6269 | 66.8293 | -123.3564
48.7969 | 123.3765 | -66.8015 | 56.3049 | -0.010607 | -9.4002e-05 | 0.0013163 | 0.055432 | -0.001391 | 0.063358 | 0.0077831 | -0.00027553 | -0.00012813 | 0.061877 | 0.0061558 | 0.062367 | -66.8388 | 0.0243 | -66.7506 | 56.2335 | 55.9731 | 56.1291 | -66.8329 | -66.7932 | 0.018674 | -66.8643 | 56.1573 | 56.2893 | 55.8209 | -66.9966 | -0.031482 | -0.071407 | -0.037384 | 0.05087 | 0.082352 | -0.3318 | -0.17581 | -0.19511 | -0.14759 | 0.008281 | -0.062854 | 0.13226 | -0.015622 | -0.48402 | 123.035 | 122.7746 | 122.9306 | 66.8258 | -123.1379 | 122.9588 | 123.0908 | 122.6224 | 66.8201 | -123.3015
49.8438 | 123.2758 | -66.8198 | 56.3416 | 0.0046549 | 0.0003334 | 0.0013163 | 0.054791 | -0.001391 | 0.063571 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.06209 | 0.0057286 | 0.062581 | -66.8297 | 0.0243 | -66.7552 | 56.2473 | 55.9594 | 56.1474 | -66.8284 | -66.8023 | 0.023253 | -66.8597 | 56.1665 | 56.2802 | 55.8209 | -67.0057 | -0.008593 | -0.094293 | -0.009917 | 0.064602 | 0.073195 | -0.38216 | -0.19412 | -0.18596 | -0.17506 | 0.017434 | -0.039965 | 0.14599 | -0.0614 | -0.52064 | 123.067 | 122.7792 | 122.9672 | 66.8441 | -123.1699 | 122.9863 | 123.0999 | 122.6407 | 66.843 | -123.3473
50.7969 | 123.349 | -66.7831 | 56.2958 | -0.0029761 | 0.0001196 | 0.0011025 | 0.055432 | -0.001391 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0057286 | 0.061726 | -66.8434 | 0.0243 | -66.746 | 56.2427 | 55.9411 | 56.1657 | -66.7826 | -66.7932 | 0.018674 | -66.8597 | 56.1528 | 56.2847 | 55.8759 | -67.0057 | 0.000575 | -0.053094 | -0.060273 | 0.037137 | 0.036562 | -0.3547 | -0.13003 | -0.22258 | -0.14302 | -0.01003 | -0.076586 | 0.14599 | -0.011045 | -0.41992 | 123.0258 | 122.7242 | 122.9489 | 66.8074 | -123.0783 | 122.9359 | 123.0679 | 122.659 | 66.8018 | -123.3015
51.7969 | 123.3673 | -66.7831 | 56.3049 | -0.0029761 | 0.0003334 | 0.0013163 | 0.055432 | -0.00096358 | 0.063571 | 0.0077831 | 0.00015167 | -0.00012813 | 0.06209 | 0.0057286 | 0.06194 | -66.8343 | 0.033457 | -66.7552 | 56.2747 | 56.0739 | 56.2207 | -66.8925 | -66.8023 | 0.027831 | -66.8643 | 56.1619 | 56.2893 | 56.0636 | -67.0011 | -0.10932 | -0.030201 | -0.051116 | 0.027981 | 0.1373 | -0.23106 | -0.084242 | -0.218 | -0.14301 | -0.019187 | -0.081165 | 0.13684 | -0.015622 | -0.24135 | 123.0579 | 122.857 | 123.0038 | 66.8166 | -123.1974 | 122.9451 | 123.0725 | 122.8467 | 66.811 | -123.3061
52.8125 | 123.2986 | -66.8289 | 56.337 | -0.010607 | 0.0001196 | 0.0011025 | 0.055004 | -0.00096358 | 0.063358 | -0.0074779 | -0.00027553 | -0.00034193 | 0.06209 | 0.0061558 | 0.06194 | -66.8297 | 0.038035 | -66.7643 | 56.261 | 56.0739 | 56.2298 | -66.9016 | -66.8023 | 0.03241 | -66.8551 | 56.1619 | 56.2893 | 56.0315 | -67.0011 | -0.072701 | -0.07598 | -0.000762 | 0.0646 | 0.1373 | -0.26311 | -0.10713 | -0.17222 | -0.17506 | 0.026589 | -0.026231 | 0.14599 | -0.047665 | -0.30544 | 123.0899 | 122.9028 | 123.0588 | 66.867 | -123.2386 | 122.9908 | 123.1182 | 122.8604 | 66.8613 | -123.3381
53.7969 | 123.3582 | -66.7969 | 56.2866 | -0.0029761 | -0.0003076 | 0.0011025 | 0.055218 | -0.001391 | 0.063358 | 0.00015261 | 0.00015167 | -0.00012813 | 0.06209 | 0.0057286 | 0.062367 | -66.8343 | 0.038035 | -66.7597 | 56.2702 | 56.0784 | 56.2161 | -66.8925 | -66.8115 | 0.036989 | -66.8597 | 56.1619 | 56.2847 | 56.0498 | -66.9966 | -0.095586 | -0.016469 | -0.037383 | 0.037135 | 0.13272 | -0.20817 | -0.07051 | -0.19969 | -0.1247 | -0.014612 | -0.062853 | 0.13684 | -0.00189 | -0.23678 | 123.067 | 122.8753 | 123.013 | 66.8349 | -123.1791 | 122.9588 | 123.0816 | 122.8467 | 66.8339 | -123.2832
54.7969 | 123.4085 | -66.7648 | 56.3232 | 0.0046549 | 0.0001196 | 0.0011025 | 0.055645 | -0.00096358 | 0.063358 | 0.00015261 | -0.00027553 | -0.00055553 | 0.061877 | 0.0059422 | 0.062367 | -66.8343 | 0.033457 | -66.7689 | 56.2702 | 56.083 | 56.2344 | -66.897 | -66.7977 | 0.027831 | -66.8643 | 56.1528 | 56.2847 | 56.1277 | -67.0057 | -0.13221 | -0.05309 | -0.069426 | -0.004064 | 0.12814 | -0.24021 | -0.088817 | -0.24089 | -0.17048 | -0.032918 | -0.099475 | 0.14142 | -0.038511 | -0.19556 | 123.035 | 122.8479 | 122.9993 | 66.7983 | -123.2203 | 122.9176 | 123.0496 | 122.8925 | 66.7927 | -123.329
55.8594 | 123.381 | -66.7969 | 56.2866 | -0.018238 | -9.4002e-05 | 0.0015299 | 0.055859 | -0.00096358 | 0.063785 | -0.0074779 | 0.00015167 | -0.00055553 | 0.06209 | 0.0061558 | 0.06194 | -66.8297 | 0.038035 | -66.7552 | 56.2839 | 56.0876 | 56.2298 | -66.897 | -66.8023 | 0.027831 | -66.8643 | 56.1528 | 56.2893 | 56.059 | -66.9966 | -0.10017 | -0.002734 | -0.032805 | 0.041714 | 0.14188 | -0.19901 | -0.056774 | -0.19969 | -0.13386 | -0.005454 | -0.067432 | 0.13226 | 0.002689 | -0.22762 | 123.0808 | 122.8845 | 123.0267 | 66.8349 | -123.1837 | 122.9496 | 123.0862 | 122.8559 | 66.8247 | -123.2832
56.7969 | 123.3444 | -66.7923 | 56.3232 | 0.0046549 | 0.0003334 | 0.0011025 | 0.055645 | -0.0016046 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.00055553 | 0.061877 | 0.0059422 | 0.06194 | -66.8388 | 0.038035 | -66.7689 | 56.2793 | 56.0876 | 56.2344 | -66.9016 | -66.8023 | 0.041567 | -66.8597 | 56.1619 | 56.2939 | 56.0178 | -67.0103 | -0.10932 | -0.043933 | -0.04654 | 0.023401 | 0.13272 | -0.23564 | -0.088817 | -0.218 | -0.16132 | -0.010032 | -0.067431 | 0.15057 | -0.029353 | -0.30545 | 123.0716 | 122.8799 | 123.0267 | 66.8303 | -123.2249 | 122.9542 | 123.0862 | 122.8101 | 66.8339 | -123.3335
57.875 | 123.2986 | -66.8106 | 56.3644 | 0.012286 | 0.0003334 | 0.0013163 | 0.054791 | -0.0011772 | 0.063144 | 0.023044 | 0.00015167 | -0.00034193 | 0.06209 | 0.0059422 | 0.062367 | -66.8251 | 0.042614 | -66.7643 | 56.2702 | 56.083 | 56.2298 | -66.8925 | -66.8023 | 0.03241 | -66.8643 | 56.1528 | 56.2893 | 56.0361 | -67.0011 | -0.081853 | -0.094289 | -0.014494 | 0.04629 | 0.12814 | -0.28141 | -0.13459 | -0.19053 | -0.21168 | 0.008279 | -0.053699 | 0.13684 | -0.075131 | -0.32833 | 123.0808 | 122.8936 | 123.0405 | 66.8532 | -123.2569 | 122.9634 | 123.0999 | 122.8467 | 66.843 | -123.3656
58.7969 | 123.3902 | -66.7694 | 56.3278 | -0.010607 | -0.0003076 | 0.0013163 | 0.055645 | -0.00074998 | 0.063358 | 0.00015261 | -0.00048933 | -0.00034193 | 0.061877 | 0.0059422 | 0.062154 | -66.8343 | 0.033457 | -66.7414 | 56.2564 | 56.083 | 56.2161 | -66.8787 | -66.7932 | 0.027831 | -66.8551 | 56.1573 | 56.2893 | 56.1689 | -66.9966 | -0.10932 | -0.071403 | -0.064849 | 0.027982 | 0.1373 | -0.24479 | -0.11171 | -0.22716 | -0.17048 | -0.023763 | -0.08574 | 0.14142 | -0.03851 | -0.15893 | 123.0258 | 122.8524 | 122.9855 | 66.8029 | -123.2065 | 122.9267 | 123.0587 | 122.9383 | 66.7972 | -123.3244
59.7969 | 123.3856 | -66.7648 | 56.3187 | 0.0046549 | -9.4002e-05 | 0.0013163 | 0.055859 | -0.001391 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.00012813 | 0.061877 | 0.0061558 | 0.062154 | -66.8434 | 0.028878 | -66.7368 | 56.2473 | 56.0968 | 56.207 | -66.8741 | -66.8023 | 0.027831 | -66.8551 | 56.1573 | 56.2939 | 56.1139 | -67.0011 | -0.10931 | -0.071405 | -0.078583 | 0.027984 | 0.1373 | -0.2219 | -0.11171 | -0.23631 | -0.16133 | -0.037497 | -0.090317 | 0.14599 | -0.024776 | -0.20472 | 123.0121 | 122.8616 | 122.9718 | 66.7937 | -123.1928 | 122.9222 | 123.0587 | 122.8788 | 66.7927 | -123.3198
60.8594 | 123.3582 | -66.806 | 56.2866 | -0.0029761 | 0.0003334 | 0.0013163 | 0.055645 | -0.00096358 | 0.063571 | 0.00015261 | -0.00048933 | -0.00012813 | 0.06209 | 0.0059422 | 0.062154 | -66.8343 | 0.019721 | -66.746 | 56.261 | 56.1242 | 56.2115 | -66.8421 | -66.8023 | 0.023253 | -66.8643 | 56.1528 | 56.2939 | 56.2055 | -66.992 | -0.036063 | -0.025626 | -0.028228 | 0.060025 | 0.096088 | -0.16238 | -0.075089 | -0.18596 | -0.13386 | 0.003701 | -0.058277 | 0.12768 | 0.007268 | -0.081103 | 123.067 | 122.9303 | 123.0176 | 66.8258 | -123.1287 | 122.9588 | 123.0999 | 123.0115 | 66.8293 | -123.2786
61.7969 | 123.3398 | -66.806 | 56.3416 | -0.010607 | 0.000547 | 0.0015299 | 0.055645 | -0.001391 | 0.063999 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.061877 | 0.0063696 | 0.062154 | -66.8434 | 0.0243 | -66.746 | 56.2518 | 56.1151 | 56.1978 | -66.8604 | -66.7977 | 0.023253 | -66.8643 | 56.1619 | 56.2939 | 56.0041 | -67.0011 | -0.054378 | -0.089714 | -0.037385 | 0.060025 | 0.1144 | -0.22647 | -0.14376 | -0.19511 | -0.17964 | 0.00828 | -0.058277 | 0.13684 | -0.047664 | -0.33749 | 123.0579 | 122.9211 | 123.0038 | 66.8303 | -123.202 | 122.9679 | 123.0999 | 122.8101 | 66.8293 | -123.3427
62.875 | 123.2437 | -66.8289 | 56.3095 | -0.010607 | 0.0001196 | 0.0011025 | 0.055432 | -0.001391 | 0.063999 | 0.0077831 | -0.00027553 | -0.00055553 | 0.062304 | 0.0061558 | 0.062367 | -66.8251 | 0.033457 | -66.7506 | 56.2427 | 56.1059 | 56.2115 | -66.8604 | -66.8023 | 0.03241 | -66.8597 | 56.1573 | 56.2847 | 56.0819 | -67.0057 | -0.03149 | -0.066827 | 0.003816 | 0.078335 | 0.10983 | -0.20359 | -0.097977 | -0.1768 | -0.15217 | 0.026589 | -0.03081 | 0.14599 | -0.024778 | -0.22761 | 123.0716 | 122.9348 | 123.0404 | 66.8624 | -123.1699 | 122.9863 | 123.1136 | 122.9108 | 66.8613 | -123.3152
63.7969 | 123.3582 | -66.806 | 56.3095 | 0.0046549 | -0.0003076 | 0.0015299 | 0.055218 | -0.0016046 | 0.063999 | 0.00015261 | -0.00048933 | -0.00055553 | 0.062304 | 0.0061558 | 0.062367 | -66.8434 | 0.019721 | -66.7414 | 56.2427 | 56.083 | 56.2024 | -66.8513 | -66.8115 | 0.027831 | -66.8689 | 56.1528 | 56.2893 | 55.9629 | -67.0011 | -0.045221 | -0.066827 | -0.037385 | 0.064603 | 0.10982 | -0.22648 | -0.10713 | -0.19511 | -0.15675 | -0.005457 | -0.062855 | 0.13226 | -0.020199 | -0.34666 | 123.0487 | 122.8891 | 123.0084 | 66.8258 | -123.1608 | 122.9588 | 123.0953 | 122.7689 | 66.8339 | -123.3107
64.8594 | 123.3673 | -66.7831 | 56.3507 | -0.0029761 | -0.0003076 | 0.0011025 | 0.055218 | -0.0016046 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.00076913 | 0.06209 | 0.0065832 | 0.062154 | -66.8434 | 0.0243 | -66.7506 | 56.2473 | 56.083 | 56.2024 | -66.8558 | -66.8115 | 0.018674 | -66.8643 | 56.1619 | 56.2939 | 56.1414 | -67.0057 | -0.072688 | -0.10345 | -0.060273 | 0.032559 | 0.10525 | -0.26768 | -0.14833 | -0.22258 | -0.18879 | -0.028345 | -0.081165 | 0.14142 | -0.056819 | -0.20929 | 123.0304 | 122.8662 | 122.9855 | 66.8074 | -123.2065 | 122.9451 | 123.077 | 122.9246 | 66.8018 | -123.3564
65.7969 | 123.3719 | -66.7603 | 56.3324 | 0.012286 | 0.0001196 | 0.0011025 | 0.055004 | -0.0011772 | 0.063571 | 0.00015261 | -0.00048933 | -0.00034193 | 0.062304 | 0.0061558 | 0.062154 | -66.8343 | 0.0243 | -66.7506 | 56.2473 | 56.0556 | 56.2024 | -66.8604 | -66.7932 | 0.027831 | -66.8643 | 56.1573 | 56.2939 | 56.027 | -67.0057 | -0.10015 | -0.085137 | -0.074004 | 0.009671 | 0.10983 | -0.27684 | -0.13002 | -0.24547 | -0.17506 | -0.032918 | -0.10405 | 0.14142 | -0.038508 | -0.30544 | 123.0075 | 122.8158 | 122.9626 | 66.7846 | -123.1928 | 122.9176 | 123.0541 | 122.7872 | 66.7881 | -123.3381
66.7969 | 123.2986 | -66.8243 | 56.3599 | 0.0046549 | -0.0005214 | 0.0011025 | 0.055004 | -0.0016046 | 0.064853 | 0.015414 | -0.00070293 | -0.00098273 | 0.062518 | 0.0065832 | 0.062154 | -66.8297 | 0.028878 | -66.7872 | 56.2473 | 56.0647 | 56.207 | -66.8604 | -66.839 | 0.018674 | -66.8597 | 56.1619 | 56.2893 | 56.0636 | -67.0011 | -0.036067 | -0.1126 | -0.005339 | 0.037132 | 0.073199 | -0.29515 | -0.15291 | -0.1768 | -0.19795 | -0.014618 | -0.035387 | 0.14141 | -0.070553 | -0.29628 | 123.0716 | 122.8891 | 123.0313 | 66.8532 | -123.2203 | 122.9863 | 123.1137 | 122.8879 | 66.843 | -123.361
67.875 | 123.2849 | -66.8427 | 56.3278 | 0.0046549 | -0.0003076 | 0.0011025 | 0.055004 | -0.0018182 | 0.063999 | 0.0077831 | -0.00070293 | -0.00055553 | 0.062304 | 0.0065832 | 0.062154 | -66.8297 | 0.047193 | -66.7964 | 56.3068 | 56.1105 | 56.2619 | -66.8696 | -66.8298 | 0.041567 | -66.8689 | 56.1573 | 56.2847 | 56.0041 | -67.0103 | -0.026915 | -0.021041 | 0.012971 | 0.046285 | 0.0732 | -0.21732 | -0.065923 | -0.16765 | -0.17048 | 0.01285 | -0.026234 | 0.14142 | -0.043089 | -0.32376 | 123.1494 | 122.9532 | 123.1045 | 66.8898 | -123.1974 | 123 | 123.1274 | 122.8467 | 66.8842 | -123.3381
68.7969 | 123.2712 | -66.806 | 56.3736 | 0.0046549 | -0.0003076 | 0.0013163 | 0.054791 | -0.00096358 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.061877 | 0.0061558 | 0.06194 | -66.8343 | 0.042614 | -66.7781 | 56.293 | 56.0922 | 56.2482 | -66.8604 | -66.8206 | 0.041567 | -66.8597 | 56.1573 | 56.2939 | 55.9995 | -67.0103 | -0.054378 | -0.080552 | -0.028228 | 0.027977 | 0.082355 | -0.28141 | -0.12543 | -0.20427 | -0.21626 | -0.014614 | -0.053698 | 0.15057 | -0.079707 | -0.37411 | 123.0991 | 122.8982 | 123.0542 | 66.8486 | -123.234 | 122.9634 | 123.0999 | 122.8055 | 66.8476 | -123.3839
69.7969 | 123.3078 | -66.8015 | 56.3507 | 0.0046549 | -9.4002e-05 | 0.0013163 | 0.055004 | -0.001391 | 0.063571 | 0.015414 | -6.1934e-05 | -0.00076913 | 0.061663 | 0.0063696 | 0.062367 | -66.8388 | 0.038035 | -66.7735 | 56.2793 | 56.0601 | 56.2161 | -66.8284 | -66.8069 | 0.023253 | -66.8643 | 56.1528 | 56.2939 | 55.9216 | -67.0011 | -0.026903 | -0.071399 | -0.037384 | 0.027979 | 0.054882 | -0.29058 | -0.1346 | -0.19969 | -0.19795 | -0.005455 | -0.062854 | 0.13684 | -0.056819 | -0.42906 | 123.0808 | 122.8616 | 123.0176 | 66.8395 | -123.1791 | 122.9542 | 123.0953 | 122.7231 | 66.8247 | -123.3519
70.8594 | 123.4451 | -66.7877 | 56.3187 | 0.0046549 | 0.0001196 | 0.0013163 | 0.055432 | -0.0011772 | 0.063144 | 0.00015261 | -0.00027553 | -0.00012813 | 0.06209 | 0.0059422 | 0.061726 | -66.8297 | 0.038035 | -66.7643 | 56.2656 | 56.051 | 56.2253 | -66.8558 | -66.8023 | 0.027831 | -66.8551 | 56.1573 | 56.2847 | 55.94 | -67.0011 | -0.06811 | -0.053091 | -0.04196 | 0.023402 | 0.091512 | -0.26769 | -0.093397 | -0.21342 | -0.16133 | -0.014609 | -0.067429 | 0.14599 | -0.033934 | -0.37871 | 123.0533 | 122.8387 | 123.013 | 66.8258 | -123.1745 | 122.9451 | 123.0725 | 122.7277 | 66.8156 | -123.3198
71.7969 | 123.3307 | -66.7786 | 56.3416 | 0.0046549 | -9.4002e-05 | 0.00088894 | 0.055004 | -0.001391 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.062304 | 0.0063696 | 0.062154 | -66.8297 | 0.028878 | -66.7597 | 56.2656 | 56.0143 | 56.2024 | -66.8558 | -66.8023 | 0.018674 | -66.8643 | 56.1619 | 56.2939 | 55.8896 | -67.0057 | -0.077266 | -0.075979 | -0.051116 | 0.018824 | 0.09609 | -0.32721 | -0.13918 | -0.22716 | -0.17964 | -0.023765 | -0.085743 | 0.14142 | -0.047664 | -0.45196 | 123.0441 | 122.7929 | 122.9809 | 66.8074 | -123.1974 | 122.9405 | 123.0725 | 122.6682 | 66.7972 | -123.3473
72.7969 | 123.3261 | -66.8518 | 56.2866 | 0.0046549 | -0.0003076 | 0.0013163 | 0.055218 | -0.0011772 | 0.063571 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0063696 | 0.062154 | -66.8388 | 0.028878 | -66.746 | 56.2656 | 56.0693 | 56.2161 | -66.8421 | -66.7932 | 0.03241 | -66.8597 | 56.1619 | 56.2939 | 55.9079 | -67.0011 | 0.009714 | -0.021047 | 0.01297 | 0.1058 | 0.096088 | -0.21733 | -0.07051 | -0.14934 | -0.1247 | 0.058635 | -0.007921 | 0.14141 | 0.007268 | -0.37871 | 123.1174 | 122.9211 | 123.0679 | 66.8807 | -123.1287 | 123.0137 | 123.1457 | 122.7597 | 66.8842 | -123.2878
73.7969 | 123.2803 | -66.8198 | 56.369 | 0.012286 | -0.0003076 | 0.0013163 | 0.055218 | -0.001391 | 0.063785 | 0.015414 | -0.00027553 | -0.00076913 | 0.06209 | 0.0063696 | 0.062154 | -66.8343 | 0.033457 | -66.7506 | 56.261 | 56.0693 | 56.2161 | -66.865 | -66.7977 | 0.03241 | -66.8597 | 56.1573 | 56.2893 | 55.8575 | -66.992 | -0.045224 | -0.10802 | -0.014495 | 0.06918 | 0.1144 | -0.29973 | -0.15291 | -0.17222 | -0.21168 | 0.022013 | -0.039965 | 0.13226 | -0.079709 | -0.51148 | 123.0808 | 122.8891 | 123.0359 | 66.8532 | -123.234 | 122.9771 | 123.1091 | 122.6773 | 66.8522 | -123.361
74.8594 | 123.3902 | -66.7877 | 56.3278 | 0.0046549 | -0.0003076 | 0.0011025 | 0.055004 | -0.001391 | 0.063571 | 0.015414 | -6.1934e-05 | -0.00034193 | 0.061877 | 0.0059422 | 0.062154 | -66.8343 | 0.033457 | -66.7414 | 56.2564 | 56.0601 | 56.2161 | -66.8513 | -66.7932 | 0.027831 | -66.8643 | 56.1528 | 56.2893 | 55.9583 | -67.0057 | -0.063531 | -0.071403 | -0.046538 | 0.046293 | 0.10982 | -0.26769 | -0.11171 | -0.218 | -0.17506 | -0.005452 | -0.076587 | 0.14142 | -0.03851 | -0.36955 | 123.0441 | 122.8479 | 123.0038 | 66.8212 | -123.1791 | 122.9405 | 123.077 | 122.746 | 66.8156 | -123.3335
75.7969 | 123.3078 | -66.7877 | 56.3599 | 0.0046549 | 0.0003334 | 0.00088894 | 0.055218 | -0.0011772 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00012813 | 0.062304 | 0.0065832 | 0.061726 | -66.8297 | 0.028878 | -66.7414 | 56.2473 | 56.0601 | 56.2115 | -66.8558 | -66.7932 | 0.027831 | -66.8506 | 56.1619 | 56.2939 | 55.9445 | -67.0011 | -0.06811 | -0.1126 | -0.04196 | 0.046293 | 0.1144 | -0.29973 | -0.14833 | -0.21342 | -0.19795 | -0.005452 | -0.06285 | 0.15057 | -0.065974 | -0.41532 | 123.035 | 122.8479 | 122.9993 | 66.8166 | -123.2157 | 122.9496 | 123.0816 | 122.7323 | 66.8156 | -123.361
76.7969 | 123.2986 | -66.806 | 56.3461 | 0.012286 | -9.4002e-05 | 0.0013163 | 0.055218 | -0.0016046 | 0.063358 | -0.0074779 | -0.00027553 | -0.00034193 | 0.06209 | 0.0063696 | 0.062154 | -66.8388 | 0.028878 | -66.7414 | 56.2427 | 56.0556 | 56.2115 | -66.8696 | -66.8023 | 0.023253 | -66.8643 | 56.1619 | 56.2939 | 56.0086 | -67.0011 | -0.063536 | -0.10345 | -0.032807 | 0.064603 | 0.12814 | -0.29058 | -0.1346 | -0.19511 | -0.18421 | 0.003701 | -0.058277 | 0.13684 | -0.052241 | -0.33749 | 123.0487 | 122.8616 | 123.0176 | 66.8349 | -123.2157 | 122.9679 | 123.0999 | 122.8147 | 66.8293 | -123.3473
77.875 | 123.3032 | -66.8381 | 56.3187 | -0.010607 | -0.0003076 | 0.00088894 | 0.055004 | -0.001391 | 0.063785 | 0.0077831 | -0.00027553 | -0.00055553 | 0.061877 | 0.0065832 | 0.062367 | -66.8297 | 0.033457 | -66.7414 | 56.2473 | 56.051 | 56.2024 | -66.865 | -66.7977 | 0.03241 | -66.8506 | 56.1573 | 56.2893 | 56.0544 | -66.9966 | -0.026913 | -0.071405 | 0.008394 | 0.096647 | 0.12356 | -0.26769 | -0.11629 | -0.15849 | -0.16133 | 0.040324 | -0.012496 | 0.14599 | -0.029355 | -0.26424 | 123.0853 | 122.889 | 123.0404 | 66.8715 | -123.1837 | 122.9954 | 123.1274 | 122.8925 | 66.8705 | -123.3152
78.7969 | 123.2803 | -66.7969 | 56.3278 | -0.0029761 | -9.4002e-05 | 0.0011025 | 0.054791 | -0.0016046 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.061877 | 0.0065832 | 0.061513 | -66.8343 | 0.019721 | -66.7368 | 56.2473 | 56.0556 | 56.2024 | -66.865 | -66.7977 | 0.027831 | -66.8551 | 56.1573 | 56.2847 | 56.1277 | -67.0057 | -0.068112 | -0.08056 | -0.037383 | 0.060027 | 0.12814 | -0.27227 | -0.12544 | -0.20885 | -0.17048 | -0.000875 | -0.058274 | 0.15057 | -0.043089 | -0.20014 | 123.0441 | 122.8524 | 122.9993 | 66.8166 | -123.1928 | 122.9542 | 123.0816 | 122.9246 | 66.8247 | -123.3335
79.7969 | 123.3307 | -66.806 | 56.3416 | 0.0046549 | -0.0003076 | 0.00067514 | 0.054791 | -0.00096358 | 0.063358 | -0.0074779 | -0.00027553 | -0.00034193 | 0.061663 | 0.0061558 | 0.062154 | -66.8251 | 0.0243 | -66.7368 | 56.2427 | 56.0556 | 56.2024 | -66.8604 | -66.7932 | 0.027831 | -66.8643 | 56.1573 | 56.2939 | 56.0453 | -67.0057 | -0.054378 | -0.098871 | -0.019072 | 0.069182 | 0.12356 | -0.286 | -0.13918 | -0.19969 | -0.18421 | 0.012858 | -0.058277 | 0.14142 | -0.047664 | -0.29629 | 123.0487 | 122.8616 | 123.0084 | 66.8303 | -123.202 | 122.9634 | 123.0999 | 122.8513 | 66.8339 | -123.3473
80.7969 | 123.2391 | -66.8381 | 56.3416 | -0.0029761 | -9.4002e-05 | 0.0011025 | 0.055218 | -0.001391 | 0.063358 | 0.00015261 | -6.1934e-05 | -0.00034193 | 0.062304 | 0.0063696 | 0.061726 | -66.8343 | 0.028878 | -66.7414 | 56.2427 | 56.0556 | 56.1978 | -66.8604 | -66.8023 | 0.023253 | -66.8551 | 56.1528 | 56.2939 | 55.8438 | -67.0057 | -0.022334 | -0.098871 | 0.003816 | 0.096647 | 0.11898 | -0.286 | -0.14376 | -0.16765 | -0.18879 | 0.035745 | -0.017075 | 0.15057 | -0.047664 | -0.49774 | 123.0808 | 122.8936 | 123.0359 | 66.867 | -123.202 | 122.9908 | 123.132 | 122.6819 | 66.8613 | -123.3473
81.7969 | 123.2712 | -66.8152 | 56.3416 | -0.010607 | -9.4002e-05 | 0.0013163 | 0.055218 | -0.0016046 | 0.06293 | -0.0074779 | -0.00027553 | -0.00012813 | 0.061877 | 0.0061558 | 0.062154 | -66.8297 | 0.0243 | -66.7414 | 56.2381 | 56.0464 | 56.207 | -66.8604 | -66.7977 | 0.027831 | -66.8597 | 56.1573 | 56.2893 | 55.9262 | -67.0011 | -0.045222 | -0.10345 | -0.014494 | 0.073759 | 0.11898 | -0.29516 | -0.1346 | -0.18596 | -0.18421 | 0.017436 | -0.044542 | 0.14141 | -0.052243 | -0.41533 | 123.0533 | 122.8616 | 123.0221 | 66.8395 | -123.202 | 122.9725 | 123.1045 | 122.7414 | 66.843 | -123.3427
82.7969 | 123.2849 | -66.8564 | 56.3461 | -0.0029761 | -9.4002e-05 | 0.0013163 | 0.055432 | -0.0011772 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.06209 | 0.0061558 | 0.06194 | -66.8343 | 0.033457 | -66.7368 | 56.2427 | 56.0327 | 56.1978 | -66.8604 | -66.7977 | 0.03241 | -66.8597 | 56.1528 | 56.2893 | 55.9674 | -67.0011 | -0.004024 | -0.10345 | 0.022126 | 0.11954 | 0.12356 | -0.31347 | -0.14833 | -0.14476 | -0.19337 | 0.058634 | -0.003344 | 0.14141 | -0.05682 | -0.3787 | 123.0991 | 122.889 | 123.0542 | 66.8898 | -123.2065 | 123.0091 | 123.1457 | 122.8238 | 66.8888 | -123.3473
83.7969 | 123.2941 | -66.8243 | 56.3507 | -0.010607 | -9.4002e-05 | 0.0013163 | 0.054791 | -0.001391 | 0.063785 | 0.0077831 | -0.00027553 | -0.00055553 | 0.061877 | 0.0065832 | 0.06194 | -66.8343 | 0.033457 | -66.7414 | 56.2427 | 56.0556 | 56.2024 | -66.865 | -66.7977 | 0.03241 | -66.846 | 56.1528 | 56.2893 | 56.0544 | -66.9966 | -0.040646 | -0.10803 | -0.009917 | 0.082914 | 0.12356 | -0.29515 | -0.14833 | -0.17222 | -0.19795 | 0.026591 | -0.021651 | 0.15057 | -0.061398 | -0.29628 | 123.067 | 122.8799 | 123.0267 | 66.8578 | -123.2157 | 122.9771 | 123.1137 | 122.8788 | 66.8568 | -123.3473
84.7969 | 123.2803 | -66.8335 | 56.3141 | 0.0046549 | -9.4002e-05 | 0.0011025 | 0.055218 | -0.0016046 | 0.063785 | -0.0074779 | -6.1934e-05 | -0.00076913 | 0.061877 | 0.0063696 | 0.062154 | -66.8343 | 0.033457 | -66.7414 | 56.261 | 56.0556 | 56.2115 | -66.8467 | -66.7886 | 0.03241 | -66.8551 | 56.1528 | 56.2893 | 56.0086 | -67.0011 | -0.013176 | -0.053092 | -0.000762 | 0.092069 | 0.10524 | -0.25853 | -0.10256 | -0.16765 | -0.16133 | 0.044903 | -0.021653 | 0.14599 | -0.024777 | -0.30545 | 123.0945 | 122.889 | 123.045 | 66.867 | -123.1608 | 122.9863 | 123.1228 | 122.8421 | 66.8659 | -123.3152
85.8594 | 123.317 | -66.8243 | 56.3278 | 0.0046549 | 0.0003334 | 0.0013163 | 0.055218 | -0.0011772 | 0.063358 | 0.0077831 | 0.00015167 | -0.00055553 | 0.061663 | 0.0065832 | 0.061726 | -66.8297 | 0.033457 | -66.746 | 56.2656 | 56.0784 | 56.2207 | -66.8741 | -66.7977 | 0.036989 | -66.8643 | 56.1665 | 56.2939 | 56.0544 | -67.0057 | -0.049804 | -0.062246 | -0.005339 | 0.078336 | 0.12814 | -0.24937 | -0.10713 | -0.18138 | -0.16132 | 0.026591 | -0.039966 | 0.14142 | -0.033931 | -0.2734 | 123.0899 | 122.9028 | 123.045 | 66.8578 | -123.202 | 122.9908 | 123.1182 | 122.8788 | 66.8613 | -123.3335
86.7969 | 123.3765 | -66.8198 | 56.3049 | -0.0029761 | -0.0003076 | 0.0011025 | 0.055218 | -0.001391 | 0.063358 | -0.015108 | -0.00027553 | -0.00055553 | 0.061877 | 0.0065832 | 0.06194 | -66.8343 | 0.047193 | -66.7506 | 56.2656 | 56.083 | 56.2344 | -66.8833 | -66.7886 | 0.036989 | -66.8597 | 56.1619 | 56.2939 | 56.0132 | -67.0011 | -0.06354 | -0.039358 | -0.014495 | 0.06918 | 0.13272 | -0.2219 | -0.070507 | -0.18138 | -0.14301 | 0.03117 | -0.039965 | 0.14141 | -0.011043 | -0.29172 | 123.0853 | 122.9028 | 123.0542 | 66.867 | -123.1882 | 122.9817 | 123.1137 | 122.833 | 66.8568 | -123.3061
87.7969 | 123.3353 | -66.7969 | 56.3095 | 0.0046549 | 0.0001196 | 0.00088894 | 0.055432 | -0.001391 | 0.063571 | -0.0074779 | -0.00027553 | -0.00055553 | 0.061663 | 0.006797 | 0.06194 | -66.8343 | 0.047193 | -66.7597 | 56.2702 | 56.0784 | 56.239 | -66.8787 | -66.7977 | 0.036989 | -66.8551 | 56.1573 | 56.2893 | 55.9491 | -67.0057 | -0.081849 | -0.039357 | -0.037383 | 0.037135 | 0.11898 | -0.23106 | -0.070505 | -0.20885 | -0.15217 | -0.000875 | -0.058274 | 0.15057 | -0.020199 | -0.36039 | 123.067 | 122.8753 | 123.0359 | 66.8441 | -123.1882 | 122.9542 | 123.0862 | 122.746 | 66.8339 | -123.3152
88.7969 | 123.3719 | -66.7831 | 56.2729 | -0.018238 | -0.0003076 | 0.0011025 | 0.055218 | -0.0011772 | 0.063358 | -0.0074779 | -6.1934e-05 | -0.00034193 | 0.061877 | 0.0065832 | 0.061726 | -66.8343 | 0.042614 | -66.7643 | 56.2747 | 56.083 | 56.2436 | -66.8833 | -66.8069 | 0.03241 | -66.8597 | 56.1573 | 56.2847 | 56.0132 | -67.0011 | -0.10016 | 0.001843 | -0.051116 | 0.018824 | 0.11898 | -0.18986 | -0.029305 | -0.218 | -0.11555 | -0.023766 | -0.076586 | 0.14141 | 0.011843 | -0.25967 | 123.0579 | 122.8662 | 123.0267 | 66.8258 | -123.1562 | 122.9405 | 123.0679 | 122.7964 | 66.8156 | -123.274
89.8594 | 123.2895 | -66.7877 | 56.3782 | 0.0046549 | 0.0001196 | 0.0013163 | 0.055004 | -0.0016046 | 0.063571 | 0.015414 | -0.00027553 | -0.00055553 | 0.06209 | 0.0065832 | 0.06194 | -66.8297 | 0.042614 | -66.7735 | 56.2885 | 56.0922 | 56.2436 | -66.9108 | -66.8069 | 0.03241 | -66.8551 | 56.1573 | 56.2893 | 56.1826 | -67.0011 | -0.12306 | -0.089708 | -0.04196 | 0.014246 | 0.1373 | -0.28599 | -0.13459 | -0.21342 | -0.22084 | -0.019188 | -0.067429 | 0.14599 | -0.088864 | -0.19555 | 123.0762 | 122.8799 | 123.0313 | 66.8303 | -123.289 | 122.9451 | 123.077 | 122.9703 | 66.8201 | -123.3793
90.7969 | 123.3902 | -66.7923 | 56.2729 | 0.0046549 | -9.4002e-05 | 0.0015299 | 0.055218 | -0.001391 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.061663 | 0.006797 | 0.06194 | -66.8388 | 0.042614 | -66.7826 | 56.2885 | 56.1059 | 56.2482 | -66.9108 | -66.8115 | 0.041567 | -66.8597 | 56.1573 | 56.2939 | 56.2467 | -67.0103 | -0.11848 | 0.015578 | -0.04654 | 0.009666 | 0.12815 | -0.16697 | -0.024727 | -0.218 | -0.11555 | -0.01919 | -0.067431 | 0.15057 | 0.021001 | -0.026163 | 123.0808 | 122.8982 | 123.0405 | 66.8349 | -123.1837 | 122.9496 | 123.0862 | 123.039 | 66.8339 | -123.2832
91.7969 | 123.2483 | -66.8289 | 56.3416 | 0.0046549 | -0.0003076 | 0.0011025 | 0.055218 | -0.0016046 | 0.063358 | 0.00015261 | 0.00015167 | -0.00034193 | 0.06209 | 0.0065832 | 0.061726 | -66.8297 | 0.042614 | -66.7735 | 56.2885 | 56.1059 | 56.2573 | -66.9199 | -66.8115 | 0.036989 | -66.8551 | 56.1573 | 56.2939 | 56.2467 | -66.9966 | -0.091017 | -0.053087 | -0.000762 | 0.055444 | 0.14646 | -0.23563 | -0.084235 | -0.16765 | -0.18421 | 0.017431 | -0.026231 | 0.14142 | -0.047664 | -0.094828 | 123.1174 | 122.9348 | 123.0862 | 66.8715 | -123.2615 | 122.9863 | 123.1228 | 123.0756 | 66.8659 | -123.3381
92.875 | 123.3398 | -66.8015 | 56.2912 | 0.0046549 | -0.0003076 | 0.0013163 | 0.055004 | -0.0018182 | 0.063785 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.06209 | 0.006797 | 0.061726 | -66.8297 | 0.047193 | -66.7872 | 56.2976 | 56.1197 | 56.2573 | -66.9245 | -66.8206 | 0.041567 | -66.8643 | 56.1573 | 56.2939 | 56.2788 | -67.0011 | -0.12306 | 0.006424 | -0.028227 | 0.014244 | 0.1373 | -0.17154 | -0.033881 | -0.19969 | -0.13386 | -0.019191 | -0.062854 | 0.13684 | 0.00269 | -0.012423 | 123.0991 | 122.9211 | 123.0588 | 66.8486 | -123.2157 | 122.9588 | 123.0953 | 123.0802 | 66.843 | -123.2923
93.7969 | 123.3902 | -66.7831 | 56.2912 | -0.0029761 | -0.0003076 | 0.0015299 | 0.055004 | -0.0018182 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.062304 | 0.006797 | 0.062154 | -66.8297 | 0.051771 | -66.7826 | 56.3022 | 56.1334 | 56.2619 | -66.9245 | -66.8252 | 0.055303 | -66.8597 | 56.1573 | 56.2985 | 56.2284 | -67.0011 | -0.14137 | 0.011002 | -0.046538 | 0.000511 | 0.14188 | -0.1578 | -0.029302 | -0.218 | -0.13386 | -0.042081 | -0.076586 | 0.14141 | 0.007268 | -0.062788 | 123.0853 | 122.9165 | 123.045 | 66.8349 | -123.2157 | 122.9405 | 123.0816 | 123.0116 | 66.8384 | -123.2923
94.7969 | 123.3398 | -66.7786 | 56.337 | -0.0029761 | -0.000735 | 0.0013163 | 0.055218 | -0.0018182 | 0.064212 | 0.0077831 | -0.00048933 | -0.00098273 | 0.06209 | 0.006797 | 0.062367 | -66.8297 | 0.05635 | -66.7964 | 56.3068 | 56.2067 | 56.2619 | -66.9291 | -66.8298 | 0.041567 | -66.8597 | 56.1528 | 56.2985 | 56.1231 | -67.0057 | -0.15053 | -0.030196 | -0.051116 | -0.017802 | 0.13273 | -0.13032 | -0.075078 | -0.22716 | -0.18422 | -0.051237 | -0.081164 | 0.14599 | -0.038508 | -0.21387 | 123.0853 | 122.9852 | 123.0405 | 66.8349 | -123.2661 | 122.9313 | 123.077 | 122.9017 | 66.8201 | -123.3427
95.8594 | 123.3627 | -66.806 | 56.2729 | -0.010607 | -0.000735 | 0.0011025 | 0.055004 | -0.0022456 | 0.063999 | -0.0074779 | -0.00091653 | -0.00098273 | 0.06209 | 0.0065832 | 0.062367 | -66.8251 | 0.05635 | -66.8009 | 56.3068 | 56.1563 | 56.2665 | -66.8925 | -66.8344 | 0.036989 | -66.8551 | 56.1573 | 56.2939 | 56.059 | -67.0011 | -0.086431 | 0.033891 | -0.019072 | 0.005086 | 0.091517 | -0.1166 | -0.006412 | -0.19511 | -0.11555 | -0.02835 | -0.049119 | 0.14599 | 0.021001 | -0.21389 | 123.1128 | 122.9623 | 123.0725 | 66.8624 | -123.1653 | 122.9634 | 123.0999 | 122.865 | 66.843 | -123.274
96.7969 | 123.349 | -66.7831 | 56.3141 | 0.0046549 | -0.0011624 | 0.00088894 | 0.054791 | -0.002032 | 0.064212 | 0.0077831 | -0.00070293 | -0.00098273 | 0.062304 | 0.006797 | 0.062154 | -66.8297 | 0.033457 | -66.7918 | 56.2702 | 56.0693 | 56.207 | -66.865 | -66.8298 | 0.023253 | -66.8551 | 56.1528 | 56.2893 | 56.0498 | -67.0103 | -0.081845 | -0.043935 | -0.046538 | -0.008646 | 0.073199 | -0.2448 | -0.10713 | -0.22716 | -0.16133 | -0.046659 | -0.072007 | 0.15515 | -0.024777 | -0.26424 | 123.0533 | 122.8524 | 122.9901 | 66.8166 | -123.1791 | 122.9359 | 123.0725 | 122.833 | 66.8064 | -123.3244
97.7969 | 123.4772 | -66.7282 | 56.3644 | 0.0046549 | -0.0011624 | 0.00088894 | 0.055004 | -0.002032 | 0.064426 | 0.0077831 | -0.00070293 | -0.00098273 | 0.062304 | 0.006797 | 0.062367 | -66.8297 | 0.019721 | -66.746 | 56.2518 | 56.0647 | 56.2115 | -66.8604 | -66.8161 | 0.027831 | -66.8551 | 56.1619 | 56.2985 | 56.0865 | -67.0103 | -0.1322 | -0.1126 | -0.10147 | -0.017795 | 0.1144 | -0.29973 | -0.15291 | -0.28209 | -0.20252 | -0.087855 | -0.12694 | 0.15515 | -0.065974 | -0.27797 | 122.98 | 122.7929 | 122.9397 | 66.7479 | -123.2248 | 122.8901 | 123.0267 | 122.8147 | 66.756 | -123.3747
98.7969 | 123.3444 | -66.7877 | 56.3095 | -0.010607 | -0.0003076 | 0.0013163 | 0.054791 | -0.0016046 | 0.063571 | 0.00015261 | -0.00027553 | -0.00055553 | 0.061877 | 0.006797 | 0.061726 | -66.8297 | 0.028878 | -66.746 | 56.2427 | 56.0739 | 56.2024 | -66.8604 | -66.7932 | 0.023253 | -66.8551 | 56.1573 | 56.2893 | 56.0819 | -67.0011 | -0.072688 | -0.066827 | -0.04196 | 0.041715 | 0.1144 | -0.23564 | -0.10713 | -0.21342 | -0.15217 | -0.005452 | -0.067429 | 0.14599 | -0.020199 | -0.22761 | 123.0304 | 122.8616 | 122.9901 | 66.8166 | -123.1699 | 122.9451 | 123.077 | 122.8696 | 66.811 | -123.3107
99.8594 | 123.4085 | -66.8015 | 56.2912 | -0.0029761 | -0.0003076 | 0.0013163 | 0.054791 | -0.001391 | 0.062717 | -0.015108 | -0.00027553 | -0.00055553 | 0.06209 | 0.006797 | 0.06194 | -66.8205 | 0.028878 | -66.7552 | 56.2381 | 56.0784 | 56.207 | -66.8604 | -66.7977 | 0.023253 | -66.8551 | 56.1528 | 56.2939 | 56.0407 | -67.0057 | -0.058955 | -0.053095 | -0.01907 | 0.046292 | 0.10525 | -0.21275 | -0.084245 | -0.20427 | -0.13844 | 0.003703 | -0.053696 | 0.15057 | 0.00269 | -0.25051 | 123.0396 | 122.8799 | 123.0084 | 66.8303 | -123.1516 | 122.9542 | 123.0953 | 122.8421 | 66.8247 | -123.2969
100.7969 | 123.3627 | -66.7923 | 56.3095 | 0.0046549 | -9.4002e-05 | 0.0011025 | 0.055432 | -0.00096358 | 0.063571 | 0.0077831 | -6.1934e-05 | -0.00034193 | 0.061877 | 0.006797 | 0.061726 | -66.8343 | 0.019721 | -66.746 | 56.2381 | 56.0784 | 56.2115 | -66.8513 | -66.8023 | 0.023253 | -66.8597 | 56.1528 | 56.2939 | 56.0819 | -67.0011 | -0.058954 | -0.071405 | -0.041961 | 0.046292 | 0.10525 | -0.23106 | -0.097977 | -0.20885 | -0.15675 | -0.010032 | -0.067431 | 0.14141 | -0.01562 | -0.22761 | 123.0304 | 122.8707 | 123.0038 | 66.812 | -123.1608 | 122.9451 | 123.0862 | 122.8742 | 66.8156 | -123.3107
101.8594 | 123.3215 | -66.7831 | 56.3049 | -0.0029761 | -0.0005214 | 0.0013163 | 0.055004 | -0.0018182 | 0.063571 | -0.0074779 | -0.00070293 | -0.00076913 | 0.062304 | 0.006797 | 0.062367 | -66.8297 | 0.028878 | -66.7597 | 56.2381 | 56.083 | 56.207 | -66.8513 | -66.8069 | 0.023253 | -66.8551 | 56.1528 | 56.2893 | 56.1368 | -67.0057 | -0.068109 | -0.066828 | -0.046538 | 0.023402 | 0.091511 | -0.2219 | -0.097978 | -0.22258 | -0.15217 | -0.023766 | -0.072007 | 0.15057 | -0.015622 | -0.16809 | 123.0212 | 122.8662 | 122.9901 | 66.812 | -123.1562 | 122.9359 | 123.0725 | 122.92 | 66.8064 | -123.3107
102.7969 | 123.3765 | -66.774 | 56.3416 | -0.0029761 | -0.000735 | 0.0011025 | 0.054791 | -0.0016046 | 0.063999 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061877 | 0.0072242 | 0.061726 | -66.8251 | 0.0243 | -66.7643 | 56.2473 | 56.083 | 56.2024 | -66.8513 | -66.8161 | 0.018674 | -66.8551 | 56.1528 | 56.2893 | 56.146 | -67.0057 | -0.077264 | -0.094293 | -0.051115 | 0.009669 | 0.086933 | -0.25853 | -0.13918 | -0.23174 | -0.18879 | -0.042078 | -0.081162 | 0.15057 | -0.052243 | -0.19556 | 123.0212 | 122.857 | 122.9764 | 66.7983 | -123.1928 | 122.9267 | 123.0633 | 122.92 | 66.7927 | -123.3473
103.7969 | 123.3536 | -66.7694 | 56.337 | 0.0046549 | -0.0009486 | 0.00088894 | 0.055218 | -0.001391 | 0.063999 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061877 | 0.0070106 | 0.06194 | -66.8297 | 0.0243 | -66.7643 | 56.2473 | 56.083 | 56.2024 | -66.8558 | -66.8161 | 0.023253 | -66.8414 | 56.1665 | 56.2939 | 56.1552 | -67.0057 | -0.086421 | -0.089715 | -0.060271 | 0.005091 | 0.091512 | -0.25395 | -0.1346 | -0.23631 | -0.17048 | -0.046656 | -0.072004 | 0.16431 | -0.043086 | -0.18182 | 123.0167 | 122.8524 | 122.9718 | 66.7937 | -123.1928 | 122.9359 | 123.0633 | 122.9246 | 66.7927 | -123.3427
104.8594 | 123.3582 | -66.7877 | 56.3049 | -0.0029761 | -0.000735 | 0.0011025 | 0.055218 | -0.0018182 | 0.063999 | 0.015414 | -0.00027553 | -0.00076913 | 0.061877 | 0.006797 | 0.061726 | -66.8251 | 0.015142 | -66.7597 | 56.2289 | 56.0876 | 56.207 | -66.8513 | -66.8161 | 0.027831 | -66.8551 | 56.1665 | 56.2893 | 56.1552 | -66.9966 | -0.063531 | -0.075985 | -0.037382 | 0.02798 | 0.091511 | -0.21733 | -0.097978 | -0.20885 | -0.13844 | -0.028345 | -0.067429 | 0.14142 | -0.015622 | -0.14978 | 123.0167 | 122.8753 | 122.9947 | 66.8029 | -123.1562 | 122.9542 | 123.077 | 122.9429 | 66.8156 | -123.3015
105.7969 | 123.349 | -66.7831 | 56.3232 | -0.0029761 | -0.0009486 | 0.0011025 | 0.055432 | -0.0018182 | 0.063999 | 0.015414 | -0.00070293 | -0.00098273 | 0.061877 | 0.0070106 | 0.06194 | -66.8251 | 0.028878 | -66.7552 | 56.2473 | 56.0922 | 56.1978 | -66.8513 | -66.8115 | 0.023253 | -66.8506 | 56.1665 | 56.2893 | 56.1094 | -66.9966 | -0.068109 | -0.075982 | -0.04196 | 0.027981 | 0.09609 | -0.23106 | -0.12544 | -0.21342 | -0.15675 | -0.028345 | -0.067428 | 0.14599 | -0.033932 | -0.21388 | 123.0304 | 122.8753 | 122.9809 | 66.812 | -123.1745 | 122.9496 | 123.0725 | 122.8925 | 66.8064 | -123.3198
106.7969 | 123.3902 | -66.774 | 56.3049 | 0.0046549 | -0.0003076 | 0.0011025 | 0.054791 | -0.0018182 | 0.063785 | 0.015414 | -0.00048933 | -0.00076913 | 0.06209 | 0.0072242 | 0.062154 | -66.8297 | 0.019721 | -66.746 | 56.2427 | 56.0922 | 56.2115 | -66.8604 | -66.8161 | 0.027831 | -66.8597 | 56.1528 | 56.2939 | 56.146 | -67.0011 | -0.086421 | -0.06225 | -0.055693 | 0.027982 | 0.1144 | -0.21275 | -0.0934 | -0.22716 | -0.15217 | -0.042078 | -0.085741 | 0.14141 | -0.011043 | -0.15894 | 123.0167 | 122.8662 | 122.9855 | 66.7937 | -123.1653 | 122.9267 | 123.0679 | 122.92 | 66.8018 | -123.3061
107.875 | 123.5092 | -66.7374 | 56.3782 | -0.0029761 | -0.0005214 | 0.0013163 | 0.055218 | -0.0016046 | 0.063999 | 0.0077831 | -0.00027553 | -0.00034193 | 0.061877 | 0.006797 | 0.062154 | -66.8251 | 0.0243 | -66.746 | 56.2335 | 56.1013 | 56.207 | -66.8513 | -66.8161 | 0.027831 | -66.8506 | 56.1573 | 56.2893 | 56.146 | -67.0103 | -0.11389 | -0.14465 | -0.087736 | -0.008639 | 0.10525 | -0.27683 | -0.17122 | -0.27294 | -0.22084 | -0.078699 | -0.1132 | 0.15973 | -0.088864 | -0.23218 | 122.9709 | 122.8387 | 122.9443 | 66.7617 | -123.2294 | 122.8947 | 123.0267 | 122.8834 | 66.7652 | -123.3885
108.7969 | 123.3948 | -66.7557 | 56.3324 | -0.0029761 | -0.0005214 | 0.0013163 | 0.055218 | -0.0018182 | 0.063785 | 0.00015261 | -0.00048933 | -0.00076913 | 0.06209 | 0.0072242 | 0.062154 | -66.8297 | 0.0243 | -66.746 | 56.2381 | 56.0968 | 56.207 | -66.8513 | -66.8115 | 0.027831 | -66.8551 | 56.1573 | 56.2893 | 56.1414 | -67.0011 | -0.095575 | -0.094293 | -0.074004 | 0.009671 | 0.10525 | -0.23563 | -0.12544 | -0.24547 | -0.17506 | -0.055811 | -0.099473 | 0.14599 | -0.043087 | -0.19098 | 122.9938 | 122.8524 | 122.9626 | 66.78 | -123.1836 | 122.913 | 123.045 | 122.8971 | 66.7835 | -123.3335
109.7969 | 123.4131 | -66.7648 | 56.3004 | -0.0029761 | -0.000735 | 0.0011025 | 0.055218 | -0.001391 | 0.063785 | 0.0077831 | -0.00027553 | -0.00034193 | 0.061663 | 0.006797 | 0.06194 | -66.8297 | 0.0243 | -66.746 | 56.2473 | 56.0876 | 56.2024 | -66.8558 | -66.8023 | 0.027831 | -66.8551 | 56.1573 | 56.2893 | 56.0727 | -67.0103 | -0.090998 | -0.053094 | -0.064848 | 0.018827 | 0.10983 | -0.21275 | -0.097979 | -0.24547 | -0.14301 | -0.037497 | -0.090317 | 0.15515 | -0.011044 | -0.22762 | 123.0121 | 122.8524 | 122.9672 | 66.7891 | -123.1562 | 122.9222 | 123.0541 | 122.8376 | 66.7927 | -123.3107
110.7969 | 123.3673 | -66.7603 | 56.3324 | 0.0046549 | -0.000735 | 0.0011025 | 0.055004 | -0.0016046 | 0.063785 | -0.0074779 | -6.1934e-05 | -0.00076913 | 0.061449 | 0.006797 | 0.06194 | -66.8343 | 0.0243 | -66.7414 | 56.2381 | 56.1059 | 56.2024 | -66.865 | -66.8115 | 0.027831 | -66.8506 | 56.1528 | 56.2802 | 56.0865 | -67.0057 | -0.10473 | -0.094293 | -0.074004 | 0.018827 | 0.12356 | -0.22648 | -0.13002 | -0.24547 | -0.17964 | -0.051233 | -0.090316 | 0.15515 | -0.052244 | -0.24592 | 122.9984 | 122.8662 | 122.9626 | 66.7846 | -123.1974 | 122.913 | 123.0404 | 122.8467 | 66.7881 | -123.3381
111.8594 | 123.381 | -66.774 | 56.282 | -0.0029761 | -0.0009486 | 0.0011025 | 0.055218 | -0.0016046 | 0.063571 | -0.0074779 | -0.00027553 | -0.00055553 | 0.061663 | 0.0070106 | 0.06194 | -66.8251 | 0.028878 | -66.746 | 56.2381 | 56.0922 | 56.2024 | -66.8467 | -66.8206 | 0.023253 | -66.8506 | 56.1573 | 56.2847 | 56.059 | -67.0011 | -0.072685 | -0.043939 | -0.051115 | 0.027982 | 0.10067 | -0.18986 | -0.079668 | -0.22716 | -0.1247 | -0.046657 | -0.076583 | 0.15057 | 0.002688 | -0.22304 | 123.0121 | 122.8662 | 122.9764 | 66.8029 | -123.1287 | 122.9313 | 123.0587 | 122.833 | 66.7972 | -123.2832
112.7969 | 123.3948 | -66.7511 | 56.3049 | 0.0046549 | -0.000735 | 0.0015299 | 0.055432 | -0.0018182 | 0.063358 | 0.015414 | 0.00015167 | -0.00034193 | 0.061877 | 0.0065832 | 0.061726 | -66.8205 | 0.028878 | -66.7368 | 56.2381 | 56.1013 | 56.207 | -66.8558 | -66.8069 | 0.023253 | -66.846 | 56.1573 | 56.2847 | 56.0361 | -67.0103 | -0.10473 | -0.066828 | -0.069424 | 0.014251 | 0.11898 | -0.20359 | -0.097978 | -0.2592 | -0.14759 | -0.055809 | -0.094893 | 0.16431 | -0.020201 | -0.26882 | 122.9892 | 122.8524 | 122.9581 | 66.78 | -123.1608 | 122.9084 | 123.0358 | 122.7872 | 66.7744 | -123.3152
113.7969 | 123.3948 | -66.7603 | 56.3461 | -0.010607 | -0.000735 | 0.0013163 | 0.055218 | -0.0016046 | 0.063571 | -0.0074779 | -0.00048933 | -0.00055553 | 0.061663 | 0.0070106 | 0.061726 | -66.8251 | 0.028878 | -66.746 | 56.2335 | 56.0922 | 56.2115 | -66.8558 | -66.8069 | 0.023253 | -66.8551 | 56.1528 | 56.2893 | 56.0315 | -67.0103 | -0.095576 | -0.11261 | -0.064848 | 0.014249 | 0.10983 | -0.25395 | -0.1346 | -0.25005 | -0.19337 | -0.046654 | -0.094895 | 0.15515 | -0.05682 | -0.3146 | 122.9938 | 122.8524 | 122.9718 | 66.7891 | -123.202 | 122.913 | 123.0496 | 122.7918 | 66.7835 | -123.3564
114.7969 | 123.3032 | -66.7969 | 56.3416 | 0.012286 | -9.4002e-05 | 0.0011025 | 0.055218 | -0.0016046 | 0.063358 | 0.0077831 | -0.00027553 | -0.00012813 | 0.061449 | 0.0070106 | 0.06194 | -66.8205 | 0.0243 | -66.746 | 56.2473 | 56.1059 | 56.2115 | -66.8513 | -66.7977 | 0.014095 | -66.8551 | 56.1573 | 56.2847 | 56.0865 | -67.0011 | -0.054376 | -0.094293 | -0.023648 | 0.05087 | 0.10525 | -0.23563 | -0.13002 | -0.20427 | -0.18421 | -0.000875 | -0.058274 | 0.14599 | -0.056822 | -0.25508 | 123.0441 | 122.9028 | 123.0084 | 66.8212 | -123.1928 | 122.9542 | 123.0816 | 122.8833 | 66.811 | -123.3427
115.8594 | 123.3994 | -66.7786 | 56.3278 | -0.0029761 | -0.0005214 | 0.0013163 | 0.055218 | -0.002032 | 0.063358 | 0.00015261 | -0.00027553 | -0.00034193 | 0.061663 | 0.007438 | 0.061513 | -66.8205 | 0.028878 | -66.746 | 56.2473 | 56.0968 | 56.207 | -66.8467 | -66.7886 | 0.027831 | -66.8551 | 56.1573 | 56.2847 | 56.0178 | -67.0057 | -0.068108 | -0.08056 | -0.041959 | 0.032559 | 0.10067 | -0.23106 | -0.12087 | -0.22716 | -0.17048 | -0.010029 | -0.076585 | 0.15057 | -0.043089 | -0.31003 | 123.0258 | 122.8753 | 122.9855 | 66.8074 | -123.1745 | 122.9359 | 123.0633 | 122.7964 | 66.8064 | -123.3335
116.7969 | 123.3032 | -66.8198 | 56.3644 | -0.010607 | -0.0005214 | 0.0015299 | 0.055432 | -0.0016046 | 0.063358 | 0.00015261 | -0.00048933 | -0.00076913 | 0.06209 | 0.0070106 | 0.06194 | -66.8205 | 0.0243 | -66.7414 | 56.2381 | 56.1151 | 56.207 | -66.8513 | -66.7977 | 0.018674 | -66.8506 | 56.1619 | 56.2847 | 56.0315 | -67.0011 | -0.031488 | -0.12634 | -0.00076 | 0.078336 | 0.10982 | -0.24936 | -0.15749 | -0.18138 | -0.20252 | 0.022013 | -0.030807 | 0.15057 | -0.07971 | -0.33291 | 123.0579 | 122.9348 | 123.0267 | 66.8441 | -123.2157 | 122.9817 | 123.1045 | 122.8513 | 66.8384 | -123.3656
117.7969 | 123.3032 | -66.7877 | 56.3599 | 0.0046549 | -0.0003076 | 0.0011025 | 0.055432 | -0.0018182 | 0.063358 | 0.00015261 | -0.00027553 | -0.00034193 | 0.061663 | 0.007438 | 0.062154 | -66.8297 | 0.0243 | -66.746 | 56.2473 | 56.0968 | 56.2161 | -66.8467 | -66.7977 | 0.023253 | -66.8551 | 56.1573 | 56.2893 | 56.0407 | -67.0011 | -0.058952 | -0.1126 | -0.04196 | 0.041715 | 0.10067 | -0.2631 | -0.14375 | -0.21342 | -0.20252 | -0.01003 | -0.067429 | 0.14599 | -0.070553 | -0.31917 | 123.035 | 122.8845 | 123.0038 | 66.812 | -123.2065 | 122.9451 | 123.077 | 122.8284 | 66.811 | -123.361
118.7969 | 123.3627 | -66.7831 | 56.3187 | -0.0029761 | 0.0001196 | 0.0013163 | 0.055218 | -0.0018182 | 0.063358 | 0.0077831 | -6.1934e-05 | -0.00055553 | 0.061877 | 0.0072242 | 0.061726 | -66.8251 | 0.028878 | -66.746 | 56.2473 | 56.0968 | 56.2115 | -66.8558 | -66.7932 | 0.027831 | -66.8643 | 56.1528 | 56.2893 | 56.0086 | -67.0057 | -0.072688 | -0.071405 | -0.04196 | 0.037137 | 0.10983 | -0.2219 | -0.10713 | -0.22258 | -0.16591 | -0.01003 | -0.081165 | 0.14142 | -0.029355 | -0.31003 | 123.0304 | 122.8799 | 122.9947 | 66.812 | -123.1745 | 122.9359 | 123.0725 | 122.7918 | 66.811 | -123.3244
119.8594 | 123.3124 | -66.7786 | 56.282 | -0.010607 | -0.0003076 | 0.0015299 | 0.055218 | -0.0016046 | 0.063571 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061449 | 0.0070106 | 0.061726 | -66.8343 | 0.028878 | -66.746 | 56.2427 | 56.1059 | 56.207 | -66.8513 | -66.7977 | 0.027831 | -66.846 | 56.1665 | 56.2847 | 56.059 | -67.0057 | -0.072687 | -0.039361 | -0.055694 | 0.032559 | 0.10525 | -0.17612 | -0.075089 | -0.22716 | -0.11555 | -0.019186 | -0.067428 | 0.15973 | 0.002688 | -0.22304 | 123.0212 | 122.8845 | 122.9855 | 66.8074 | -123.1333 | 122.9451 | 123.0633 | 122.8376 | 66.8064 | -123.2878
120.7969 | 123.3032 | -66.8106 | 56.3599 | 0.0046549 | -0.0005214 | 0.0013163 | 0.055218 | -0.002032 | 0.063358 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061449 | 0.0072242 | 0.06194 | -66.8251 | 0.028878 | -66.746 | 56.2473 | 56.1105 | 56.2161 | -66.8558 | -66.7977 | 0.023253 | -66.8506 | 56.1573 | 56.2893 | 56.0407 | -67.0103 | -0.045222 | -0.1126 | -0.014494 | 0.064603 | 0.10983 | -0.24936 | -0.14375 | -0.19969 | -0.20252 | 0.012858 | -0.039962 | 0.15973 | -0.070553 | -0.31917 | 123.0579 | 122.9211 | 123.0267 | 66.8395 | -123.2157 | 122.9679 | 123.0999 | 122.8513 | 66.8339 | -123.3702
121.7969 | 123.3444 | -66.7969 | 56.3324 | -0.0029761 | -0.0003076 | 0.0011025 | 0.055004 | -0.0016046 | 0.063358 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061877 | 0.007438 | 0.061726 | -66.8205 | 0.0243 | -66.7506 | 56.2381 | 56.1059 | 56.2115 | -66.8513 | -66.8023 | 0.023253 | -66.8506 | 56.1528 | 56.2939 | 56.0224 | -67.0103 | -0.054376 | -0.094293 | -0.023648 | 0.046292 | 0.10067 | -0.22648 | -0.12087 | -0.21343 | -0.17964 | -0.005454 | -0.053695 | 0.15973 | -0.038508 | -0.31002 | 123.035 | 122.9028 | 123.0084 | 66.8212 | -123.1836 | 122.9496 | 123.0908 | 122.8192 | 66.8201 | -123.3427
122.875 | 123.2803 | -66.8152 | 56.3599 | 0.0046549 | -0.0005214 | 0.0015299 | 0.055218 | -0.001391 | 0.063571 | 0.0077831 | -0.00048933 | -0.00034193 | 0.061663 | 0.0072242 | 0.061726 | -66.8251 | 0.028878 | -66.746 | 56.2427 | 56.1105 | 56.207 | -66.8513 | -66.7977 | 0.023253 | -66.8506 | 56.1619 | 56.2893 | 56.0544 | -67.0057 | -0.036065 | -0.11718 | -0.009916 | 0.069181 | 0.10525 | -0.24936 | -0.15291 | -0.19054 | -0.19795 | 0.017436 | -0.035384 | 0.15515 | -0.070553 | -0.30544 | 123.0579 | 122.9257 | 123.0221 | 66.8441 | -123.2111 | 122.9771 | 123.1045 | 122.8696 | 66.8384 | -123.3656
123.7969 | 123.1934 | -66.806 | 56.3416 | 0.0046549 | -0.000735 | 0.00088894 | 0.055218 | -0.0018182 | 0.063571 | 0.00015261 | -0.00027553 | -0.00034193 | 0.061877 | 0.0070106 | 0.061726 | -66.8297 | 0.028878 | -66.7414 | 56.2518 | 56.1151 | 56.2024 | -66.8513 | -66.7977 | 0.023253 | -66.8551 | 56.1528 | 56.2847 | 56.0224 | -66.9966 | -0.045221 | -0.089714 | -0.02365 | 0.064603 | 0.10982 | -0.22647 | -0.13918 | -0.19053 | -0.18879 | 0.00828 | -0.049119 | 0.14142 | -0.056822 | -0.31918 | 123.0579 | 122.9211 | 123.0084 | 66.8349 | -123.1928 | 122.9588 | 123.0908 | 122.8284 | 66.8293 | -123.3381
124.8594 | 123.3627 | -66.7877 | 56.2866 | -0.0029761 | -0.0005214 | 0.0011025 | 0.055218 | -0.001391 | 0.063571 | 0.0077831 | -6.1934e-05 | -0.00098273 | 0.061663 | 0.0070106 | 0.061726 | -66.8251 | 0.028878 | -66.7506 | 56.2473 | 56.0922 | 56.2024 | -66.8513 | -66.7977 | 0.023253 | -66.8506 | 56.1528 | 56.2847 | 56.0315 | -67.0149 | -0.063531 | -0.039361 | -0.037382 | 0.037137 | 0.10067 | -0.19444 | -0.084246 | -0.22716 | -0.13386 | -0.01003 | -0.06285 | 0.16431 | -0.00189 | -0.25509 | 123.035 | 122.8799 | 122.9901 | 66.8166 | -123.1379 | 122.9405 | 123.0725 | 122.8193 | 66.811 | -123.3015
125.7969 | 123.3536 | -66.7877 | 56.3232 | -0.0029761 | -0.000735 | 0.0011025 | 0.055004 | -0.0011772 | 0.063358 | 0.00015261 | -0.00048933 | -0.00034193 | 0.061663 | 0.0070106 | 0.06194 | -66.8297 | 0.0243 | -66.746 | 56.2473 | 56.1105 | 56.2115 | -66.865 | -66.7886 | 0.03241 | -66.8506 | 56.1528 | 56.2893 | 56.0361 | -67.0057 | -0.077267 | -0.075982 | -0.04196 | 0.041715 | 0.11898 | -0.21274 | -0.11171 | -0.218 | -0.17048 | -0.000873 | -0.06285 | 0.15515 | -0.033932 | -0.28713 | 123.035 | 122.8982 | 122.9993 | 66.812 | -123.1882 | 122.9405 | 123.077 | 122.8238 | 66.8201 | -123.329
126.7969 | 123.2941 | -66.7923 | 56.3507 | 0.012286 | -0.000735 | 0.0011025 | 0.055004 | -0.0022456 | 0.063358 | 0.00015261 | -0.00027553 | -0.00055553 | 0.061449 | 0.007438 | 0.061726 | -66.8297 | 0.019721 | -66.7414 | 56.2473 | 56.1059 | 56.2115 | -66.8421 | -66.7977 | 0.027831 | -66.8506 | 56.1573 | 56.2847 | 56.0178 | -67.0057 | -0.049796 | -0.10345 | -0.037383 | 0.05087 | 0.10067 | -0.24479 | -0.13918 | -0.21343 | -0.19337 | -0.005453 | -0.058273 | 0.15515 | -0.065977 | -0.33291 | 123.0396 | 122.8982 | 123.0038 | 66.812 | -123.1928 | 122.9496 | 123.077 | 122.8101 | 66.8201 | -123.3564
127.7969 | 123.2529 | -66.8381 | 56.3324 | -0.0029761 | -0.0005214 | 0.00088894 | 0.055004 | -0.0018182 | 0.063571 | 0.0077831 | -0.00048933 | -0.00055553 | 0.061663 | 0.0072242 | 0.061513 | -66.8251 | 0.0243 | -66.7414 | 56.2427 | 56.1013 | 56.2161 | -66.8558 | -66.7932 | 0.027831 | -66.8506 | 56.1482 | 56.2802 | 55.9812 | -67.0011 | -0.017756 | -0.089715 | 0.012972 | 0.096647 | 0.1144 | -0.23105 | -0.11629 | -0.16307 | -0.18422 | 0.044902 | -0.012496 | 0.15057 | -0.052244 | -0.35123 | 123.0808 | 122.9394 | 123.0542 | 66.8624 | -123.1882 | 122.9863 | 123.1182 | 122.8192 | 66.8659 | -123.3335
128.7969 | 123.3032 | -66.8243 | 56.2866 | 0.0046549 | -0.000735 | 0.0013163 | 0.055218 | -0.0018182 | 0.063358 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061877 | 0.007438 | 0.061726 | -66.8159 | 0.028878 | -66.7414 | 56.2427 | 56.1013 | 56.207 | -66.8604 | -66.7977 | 0.027831 | -66.8506 | 56.1573 | 56.2847 | 56.0315 | -67.0103 | -0.036067 | -0.043939 | 0.008396 | 0.082914 | 0.11898 | -0.18528 | -0.079667 | -0.18596 | -0.12928 | 0.026591 | -0.026229 | 0.15973 | -0.00189 | -0.25509 | 123.067 | 122.9257 | 123.0313 | 66.8532 | -123.147 | 122.9817 | 123.1091 | 122.8559 | 66.8522 | -123.2969
129.7969 | 123.2712 | -66.8152 | 56.3599 | 0.0046549 | -0.000735 | 0.00088894 | 0.055218 | -0.0018182 | 0.063571 | 0.015414 | -0.00027553 | -0.00076913 | 0.061236 | 0.0076516 | 0.061513 | -66.8297 | 0.028878 | -66.746 | 56.2427 | 56.1105 | 56.2115 | -66.8513 | -66.8023 | 0.03241 | -66.8551 | 56.1619 | 56.2847 | 56.0453 | -67.0149 | -0.036065 | -0.11718 | -0.014494 | 0.069181 | 0.10525 | -0.24936 | -0.14833 | -0.19969 | -0.19795 | 0.012857 | -0.039963 | 0.15973 | -0.075132 | -0.3146 | 123.0579 | 122.9257 | 123.0267 | 66.8441 | -123.2111 | 122.9771 | 123.0999 | 122.8605 | 66.8476 | -123.3747
130.7969 | 123.3124 | -66.7969 | 56.3187 | -0.0029761 | -0.000735 | 0.0013163 | 0.055218 | -0.0016046 | 0.063571 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061663 | 0.007438 | 0.06194 | -66.8251 | 0.019721 | -66.746 | 56.2427 | 56.0968 | 56.2115 | -66.8513 | -66.8115 | 0.023253 | -66.8551 | 56.1573 | 56.2893 | 56.059 | -67.0057 | -0.054376 | -0.075983 | -0.028227 | 0.05087 | 0.10525 | -0.2219 | -0.10713 | -0.20885 | -0.16133 | -0.014612 | -0.058274 | 0.15057 | -0.029355 | -0.25966 | 123.0396 | 122.8936 | 123.0084 | 66.8166 | -123.1699 | 122.9542 | 123.0862 | 122.8559 | 66.8201 | -123.3244
131.7969 | 123.2574 | -66.8198 | 56.3599 | 0.0046549 | -0.0003076 | 0.00088894 | 0.054791 | -0.0018182 | 0.063785 | 0.015414 | -0.00048933 | -0.00076913 | 0.061663 | 0.007438 | 0.06194 | -66.8251 | 0.0243 | -66.7414 | 56.2381 | 56.0968 | 56.2115 | -66.8513 | -66.8023 | 0.027831 | -66.846 | 56.1482 | 56.2893 | 56.059 | -67.0057 | -0.031488 | -0.12176 | -0.005339 | 0.078336 | 0.10982 | -0.2631 | -0.14833 | -0.18596 | -0.21168 | 0.017434 | -0.026229 | 0.15973 | -0.070553 | -0.30086 | 123.0579 | 122.9165 | 123.0313 | 66.8441 | -123.2111 | 122.9679 | 123.1091 | 122.8788 | 66.8476 | -123.3656
132.7969 | 123.2712 | -66.8381 | 56.3232 | 0.0046549 | -0.000735 | 0.0013163 | 0.055218 | -0.0018182 | 0.063571 | 0.00015261 | -0.00048933 | -0.00034193 | 0.061663 | 0.007438 | 0.061726 | -66.8205 | 0.028878 | -66.7414 | 56.2473 | 56.1059 | 56.2161 | -66.8513 | -66.8115 | 0.023253 | -66.8551 | 56.1573 | 56.2847 | 56.027 | -67.0011 | -0.013177 | -0.075982 | 0.017551 | 0.096647 | 0.10982 | -0.21732 | -0.10713 | -0.16307 | -0.1659 | 0.026587 | -0.017075 | 0.14599 | -0.038511 | -0.29629 | 123.0853 | 122.944 | 123.0542 | 66.867 | -123.1745 | 122.9954 | 123.1228 | 122.865 | 66.8613 | -123.3244
133.8594 | 123.3948 | -66.7603 | 56.3095 | -0.0029761 | -0.0003076 | 0.0013163 | 0.055432 | -0.0018182 | 0.063358 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061877 | 0.0070106 | 0.061513 | -66.8251 | 0.028878 | -66.7368 | 56.2518 | 56.0968 | 56.207 | -66.8513 | -66.8023 | 0.027831 | -66.8551 | 56.1528 | 56.2847 | 56.0911 | -67.0149 | -0.090997 | -0.05767 | -0.064848 | 0.023406 | 0.1144 | -0.21274 | -0.10255 | -0.25463 | -0.15675 | -0.042075 | -0.094895 | 0.15973 | -0.024778 | -0.21846 | 123.0121 | 122.857 | 122.9672 | 66.7891 | -123.1608 | 122.913 | 123.045 | 122.8513 | 66.7881 | -123.3244
134.7969 | 123.2574 | -66.806 | 56.337 | 0.0046549 | -0.0005214 | 0.0015299 | 0.055004 | -0.002032 | 0.063785 | 0.015414 | -0.00048933 | -0.00076913 | 0.061663 | 0.0072242 | 0.061513 | -66.8297 | 0.028878 | -66.746 | 56.2381 | 56.1013 | 56.2115 | -66.8604 | -66.8069 | 0.03241 | -66.846 | 56.1619 | 56.2847 | 56.0773 | -67.0011 | -0.054378 | -0.098871 | -0.02365 | 0.060025 | 0.1144 | -0.23563 | -0.12544 | -0.19511 | -0.17506 | -0.000878 | -0.039962 | 0.15515 | -0.052244 | -0.25966 | 123.0441 | 122.9074 | 123.0176 | 66.8349 | -123.1974 | 122.9679 | 123.0908 | 122.8833 | 66.8384 | -123.3381
135.7969 | 123.2254 | -66.8198 | 56.3232 | -0.010607 | -0.000735 | 0.0011025 | 0.054791 | -0.0016046 | 0.063571 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061663 | 0.0072242 | 0.061726 | -66.8159 | 0.028878 | -66.7506 | 56.2427 | 56.0968 | 56.2161 | -66.8558 | -66.8161 | 0.023253 | -66.8551 | 56.1528 | 56.2802 | 56.0682 | -67.0103 | -0.036067 | -0.08056 | 0.003818 | 0.06918 | 0.10525 | -0.22648 | -0.10713 | -0.19054 | -0.17048 | 0.003698 | -0.035386 | 0.15515 | -0.043089 | -0.25508 | 123.0624 | 122.9165 | 123.0359 | 66.8486 | -123.1791 | 122.9725 | 123.0999 | 122.8879 | 66.843 | -123.3335
136.7969 | 123.23 | -66.8427 | 56.337 | -0.0029761 | -0.0003076 | 0.0011025 | 0.055004 | -0.0018182 | 0.063571 | -0.0074779 | -6.1934e-05 | -0.00098273 | 0.06209 | 0.007438 | 0.061726 | -66.8251 | 0.0243 | -66.7368 | 56.2381 | 56.1013 | 56.2115 | -66.8558 | -66.7977 | 0.03241 | -66.8506 | 56.1573 | 56.2893 | 56.1139 | -67.0103 | -0.013179 | -0.098871 | 0.017549 | 0.1058 | 0.11898 | -0.23563 | -0.12544 | -0.16765 | -0.17964 | 0.044901 | -0.007919 | 0.15973 | -0.047665 | -0.22303 | 123.0808 | 122.944 | 123.0542 | 66.867 | -123.1928 | 123 | 123.132 | 122.9566 | 66.8751 | -123.3473
137.875 | 123.3627 | -66.7877 | 56.3004 | 0.0046549 | -0.000735 | 0.0011025 | 0.055645 | -0.002032 | 0.063144 | 0.015414 | -0.00048933 | -0.00055553 | 0.061449 | 0.007438 | 0.061726 | -66.8297 | 0.0243 | -66.7368 | 56.2381 | 56.1013 | 56.2115 | -66.8604 | -66.8069 | 0.014095 | -66.8506 | 56.1573 | 56.2802 | 56.0911 | -67.0057 | -0.072688 | -0.06225 | -0.04196 | 0.050872 | 0.12356 | -0.19901 | -0.088822 | -0.218 | -0.14301 | -0.019188 | -0.06285 | 0.15515 | -0.020201 | -0.2093 | 123.0258 | 122.8891 | 122.9993 | 66.812 | -123.1608 | 122.9451 | 123.0679 | 122.8788 | 66.8018 | -123.3061
138.7969 | 123.2712 | -66.8381 | 56.337 | 0.0046549 | -0.000735 | 0.0011025 | 0.055432 | -0.002032 | 0.063571 | 0.00015261 | -0.00048933 | -0.00034193 | 0.061877 | 0.007438 | 0.061513 | -66.8251 | 0.028878 | -66.7414 | 56.2473 | 56.1013 | 56.207 | -66.8604 | -66.8069 | 0.03241 | -66.8551 | 56.1619 | 56.2985 | 56.1689 | -67.0103 | -0.022334 | -0.089715 | 0.012972 | 0.096647 | 0.11898 | -0.23563 | -0.13002 | -0.17223 | -0.17506 | 0.031166 | -0.017075 | 0.15515 | -0.038508 | -0.16809 | 123.0853 | 122.9394 | 123.045 | 66.867 | -123.1974 | 123 | 123.1365 | 123.007 | 66.8705 | -123.3473
139.7969 | 123.3261 | -66.806 | 56.3232 | -0.0029761 | -0.000735 | 0.00088894 | 0.054791 | -0.0016046 | 0.063785 | 0.0077831 | -0.00027553 | -0.00076913 | 0.061877 | 0.0078652 | 0.061726 | -66.8251 | 0.0243 | -66.7414 | 56.2518 | 56.0922 | 56.207 | -66.8558 | -66.8069 | 0.027831 | -66.8551 | 56.1619 | 56.2802 | 56.1277 | -67.0103 | -0.0498 | -0.071403 | -0.019072 | 0.064603 | 0.1144 | -0.23106 | -0.11629 | -0.20427 | -0.16132 | -0.000878 | -0.049119 | 0.15515 | -0.043089 | -0.19556 | 123.0579 | 122.8982 | 123.013 | 66.8303 | -123.1791 | 122.9679 | 123.0862 | 122.9337 | 66.8339 | -123.3335
140.8594 | 123.3627 | -66.774 | 56.3004 | -0.0029761 | -0.0011624 | 0.0011025 | 0.055432 | -0.002032 | 0.063785 | 0.00015261 | -0.00027553 | -0.00076913 | 0.061663 | 0.0076516 | 0.06194 | -66.8205 | 0.028878 | -66.7368 | 56.2381 | 56.0922 | 56.2161 | -66.8558 | -66.8023 | 0.023253 | -66.8506 | 56.1619 | 56.2893 | 56.1552 | -67.0057 | -0.081843 | -0.06225 | -0.046536 | 0.037139 | 0.11898 | -0.20817 | -0.084243 | -0.23174 | -0.13844 | -0.028342 | -0.076583 | 0.15515 | -0.011044 | -0.1452 | 123.0121 | 122.8662 | 122.9901 | 66.8029 | -123.1562 | 122.9359 | 123.0633 | 122.9291 | 66.7972 | -123.3061
141.7969 | 123.23 | -66.8198 | 56.3278 | 0.0046549 | -0.000735 | 0.0013163 | 0.054791 | -0.0016046 | 0.063785 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061449 | 0.0076516 | 0.061513 | -66.8251 | 0.028878 | -66.7414 | 56.2427 | 56.0922 | 56.2115 | -66.8513 | -66.8069 | 0.027831 | -66.8506 | 56.1528 | 56.2893 | 56.1185 | -67.0103 | -0.031488 | -0.085138 | -0.005339 | 0.078336 | 0.10982 | -0.23564 | -0.11629 | -0.19054 | -0.17506 | 0.012855 | -0.030807 | 0.15973 | -0.03851 | -0.2093 | 123.0624 | 122.9119 | 123.0313 | 66.8486 | -123.1791 | 122.9725 | 123.1091 | 122.9383 | 66.8476 | -123.3381
142.7969 | 123.3719 | -66.8106 | 56.3095 | 0.0046549 | -0.0011624 | 0.0013163 | 0.055004 | -0.0018182 | 0.063999 | 0.0077831 | -0.00048933 | -0.00055553 | 0.061663 | 0.0078652 | 0.061513 | -66.8251 | 0.033457 | -66.7368 | 56.2473 | 56.0968 | 56.207 | -66.8467 | -66.8069 | 0.027831 | -66.8551 | 56.1619 | 56.2985 | 56.1277 | -67.0011 | -0.036064 | -0.062249 | -0.014494 | 0.07376 | 0.10982 | -0.21274 | -0.10255 | -0.19053 | -0.14759 | 0.0037 | -0.044541 | 0.14599 | -0.011042 | -0.18183 | 123.0579 | 122.9074 | 123.0176 | 66.8441 | -123.1562 | 122.9725 | 123.1091 | 122.9383 | 66.8384 | -123.3107
143.7969 | 123.3215 | -66.7831 | 56.3187 | -0.010607 | -0.0009486 | 0.00088894 | 0.055432 | -0.0018182 | 0.063571 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061449 | 0.0076516 | 0.061513 | -66.8251 | 0.019721 | -66.7506 | 56.2381 | 56.0922 | 56.207 | -66.8558 | -66.8115 | 0.027831 | -66.8551 | 56.1573 | 56.2939 | 56.0956 | -67.0103 | -0.072688 | -0.080561 | -0.04196 | 0.032559 | 0.10525 | -0.22648 | -0.11171 | -0.22716 | -0.16133 | -0.028345 | -0.072007 | 0.15515 | -0.024776 | -0.22303 | 123.0212 | 122.8753 | 122.9901 | 66.8029 | -123.1745 | 122.9405 | 123.077 | 122.8788 | 66.811 | -123.329
144.7969 | 123.3994 | -66.7786 | 56.2958 | 0.012286 | -0.0011624 | 0.0011025 | 0.055218 | -0.0016046 | 0.063785 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061449 | 0.008079 | 0.061726 | -66.8205 | 0.028878 | -66.746 | 56.2381 | 56.0876 | 56.2115 | -66.8513 | -66.8069 | 0.027831 | -66.8506 | 56.1573 | 56.2939 | 56.1506 | -67.0011 | -0.072687 | -0.057672 | -0.041959 | 0.032559 | 0.10525 | -0.20817 | -0.084244 | -0.22258 | -0.13844 | -0.028344 | -0.072006 | 0.15057 | -0.001887 | -0.1452 | 123.0167 | 122.8662 | 122.9901 | 66.8074 | -123.147 | 122.9359 | 123.0725 | 122.9291 | 66.8064 | -123.2969
145.7969 | 123.3719 | -66.7831 | 56.3049 | -0.0029761 | -0.000735 | 0.0011025 | 0.055004 | -0.002032 | 0.063785 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061663 | 0.0076516 | 0.061513 | -66.8205 | 0.028878 | -66.7506 | 56.2427 | 56.0876 | 56.2024 | -66.8558 | -66.8069 | 0.023253 | -66.8506 | 56.1528 | 56.2893 | 56.1368 | -67.0057 | -0.072688 | -0.06225 | -0.037381 | 0.032559 | 0.10525 | -0.21733 | -0.10256 | -0.22258 | -0.15217 | -0.023766 | -0.067428 | 0.15515 | -0.015622 | -0.16809 | 123.0258 | 122.8707 | 122.9855 | 66.812 | -123.1608 | 122.9359 | 123.0725 | 122.92 | 66.8064 | -123.3107
146.7969 | 123.3307 | -66.8106 | 56.2866 | 0.0046549 | -0.0009486 | 0.0011025 | 0.054577 | -0.0018182 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061663 | 0.0076516 | 0.061726 | -66.8251 | 0.019721 | -66.746 | 56.2381 | 56.083 | 56.2115 | -66.8467 | -66.8115 | 0.027831 | -66.8551 | 56.1528 | 56.2847 | 56.1414 | -67.0011 | -0.036064 | -0.048517 | -0.014494 | 0.064603 | 0.10067 | -0.20359 | -0.075089 | -0.19053 | -0.13386 | -0.000879 | -0.044541 | 0.14599 | -0.00189 | -0.1452 | 123.0487 | 122.8936 | 123.0221 | 66.8303 | -123.1333 | 122.9634 | 123.0953 | 122.952 | 66.8384 | -123.2878
147.7969 | 123.436 | -66.7923 | 56.2592 | -0.0029761 | -0.0009486 | 0.00088894 | 0.055004 | -0.0018182 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061663 | 0.0076516 | 0.06194 | -66.8205 | 0.0243 | -66.7597 | 56.2518 | 56.0876 | 56.2115 | -66.8513 | -66.8115 | 0.03241 | -66.8506 | 56.1528 | 56.2893 | 56.1506 | -67.0103 | -0.058954 | -0.007316 | -0.028226 | 0.032557 | 0.091511 | -0.17155 | -0.047623 | -0.218 | -0.10639 | -0.01919 | -0.058273 | 0.15973 | 0.030155 | -0.10858 | 123.0441 | 122.8799 | 123.0038 | 66.8166 | -123.1104 | 122.9451 | 123.0816 | 122.9429 | 66.8247 | -123.2695
148.7969 | 123.2529 | -66.7969 | 56.3782 | 0.0046549 | -0.0009486 | 0.0013163 | 0.054791 | -0.002032 | 0.063785 | 0.00015261 | -0.00091653 | -0.00055553 | 0.061449 | 0.0076516 | 0.06194 | -66.8205 | 0.0243 | -66.7414 | 56.2381 | 56.0922 | 56.2115 | -66.8558 | -66.8115 | 0.027831 | -66.8551 | 56.1528 | 56.2939 | 56.1597 | -66.9966 | -0.058955 | -0.14007 | -0.023648 | 0.055448 | 0.1144 | -0.28599 | -0.16664 | -0.19969 | -0.22541 | -0.014612 | -0.058274 | 0.14142 | -0.084285 | -0.21844 | 123.035 | 122.8891 | 123.0084 | 66.8212 | -123.234 | 122.9496 | 123.0908 | 122.9566 | 66.8247 | -123.3747
149.7969 | 123.3902 | -66.7603 | 56.2866 | 0.0046549 | -0.0011624 | 0.0011025 | 0.055004 | -0.002032 | 0.063358 | -0.0074779 | -0.00048933 | -0.0011965 | 0.061236 | 0.0082926 | 0.061513 | -66.8159 | 0.0243 | -66.7689 | 56.2427 | 56.083 | 56.2115 | -66.8558 | -66.8115 | 0.027831 | -66.8551 | 56.1528 | 56.2893 | 56.1506 | -67.0011 | -0.095576 | -0.043939 | -0.055691 | -0.008642 | 0.086934 | -0.20359 | -0.075089 | -0.24089 | -0.13386 | -0.051233 | -0.094895 | 0.14599 | 0.002689 | -0.13605 | 123.0029 | 122.8433 | 122.9718 | 66.7846 | -123.1425 | 122.913 | 123.0496 | 122.9108 | 66.7881 | -123.2878
150.875 | 123.3765 | -66.7465 | 56.3187 | 0.012286 | -0.0009486 | 0.0013163 | 0.055004 | -0.002032 | 0.063785 | 0.0077831 | -0.00048933 | -0.00055553 | 0.061877 | 0.008079 | 0.06194 | -66.8205 | 0.0243 | -66.7552 | 56.2473 | 56.1013 | 56.2115 | -66.8558 | -66.8069 | 0.018674 | -66.8506 | 56.1573 | 56.2802 | 56.1506 | -67.0103 | -0.10931 | -0.071405 | -0.074002 | -0.00864 | 0.10067 | -0.21732 | -0.10713 | -0.26378 | -0.16133 | -0.060387 | -0.10405 | 0.15973 | -0.038512 | -0.16809 | 122.9938 | 122.8479 | 122.9581 | 66.7708 | -123.1745 | 122.9039 | 123.0267 | 122.8971 | 66.7652 | -123.329
151.7969 | 123.3765 | -66.7877 | 56.282 | 0.0046549 | -0.000735 | 0.0015299 | 0.055218 | -0.002032 | 0.063999 | 0.015414 | -0.00048933 | -0.00076913 | 0.061449 | 0.0078652 | 0.061726 | -66.8251 | 0.028878 | -66.7643 | 56.2427 | 56.083 | 56.2161 | -66.8513 | -66.8115 | 0.027831 | -66.8551 | 56.1573 | 56.2939 | 56.1277 | -67.0057 | -0.063531 | -0.039361 | -0.037382 | 0.023402 | 0.086933 | -0.19902 | -0.065932 | -0.218 | -0.1247 | -0.023767 | -0.067429 | 0.15057 | 0.011846 | -0.15436 | 123.0304 | 122.8707 | 123.0038 | 66.8166 | -123.1333 | 122.9451 | 123.0816 | 122.9154 | 66.8156 | -123.2878
152.8594 | 123.349 | -66.7694 | 56.3004 | 0.0046549 | -0.000735 | 0.0013163 | 0.055432 | -0.002032 | 0.063999 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061877 | 0.0078652 | 0.061513 | -66.8251 | 0.0243 | -66.7643 | 56.2473 | 56.0968 | 56.2115 | -66.8558 | -66.8161 | 0.027831 | -66.8506 | 56.1528 | 56.2847 | 56.146 | -67.0103 | -0.086421 | -0.053094 | -0.055693 | 0.005091 | 0.091512 | -0.20359 | -0.088822 | -0.24089 | -0.14759 | -0.046656 | -0.081161 | 0.15973 | -0.015623 | -0.15436 | 123.0167 | 122.8662 | 122.9809 | 66.7937 | -123.1562 | 122.9222 | 123.0541 | 122.9154 | 66.7972 | -123.3107
153.7969 | 123.3124 | -66.7877 | 56.3324 | 0.0046549 | -0.0009486 | 0.0011025 | 0.054791 | -0.002032 | 0.064212 | 0.00015261 | -0.00027553 | -0.00098273 | 0.061663 | 0.0076516 | 0.061299 | -66.8159 | 0.0243 | -66.7689 | 56.2427 | 56.0922 | 56.2115 | -66.8558 | -66.8161 | 0.03241 | -66.846 | 56.1528 | 56.2893 | 56.1552 | -67.0103 | -0.06811 | -0.089715 | -0.028225 | 0.018824 | 0.086934 | -0.24021 | -0.12087 | -0.22258 | -0.17964 | -0.028345 | -0.058272 | 0.16431 | -0.043087 | -0.17724 | 123.0304 | 122.8799 | 122.9993 | 66.812 | -123.1882 | 122.9405 | 123.077 | 122.9429 | 66.8201 | -123.3427
154.7969 | 123.349 | -66.7786 | 56.3049 | -0.0029761 | -0.0009486 | 0.0011025 | 0.055004 | -0.0016046 | 0.063999 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061449 | 0.0078652 | 0.061513 | -66.8205 | 0.028878 | -66.7552 | 56.2427 | 56.1059 | 56.2161 | -66.8558 | -66.8069 | 0.023253 | -66.8551 | 56.1528 | 56.2939 | 56.1414 | -67.0103 | -0.077266 | -0.06225 | -0.041959 | 0.023403 | 0.10067 | -0.19901 | -0.088821 | -0.23174 | -0.15217 | -0.028344 | -0.076585 | 0.15515 | -0.011043 | -0.16351 | 123.0212 | 122.8845 | 122.9947 | 66.8074 | -123.1608 | 122.9313 | 123.0725 | 122.92 | 66.8018 | -123.3152
155.7969 | 123.2529 | -66.7831 | 56.3599 | -0.0029761 | -0.0009486 | 0.0011025 | 0.054791 | -0.0018182 | 0.063785 | 0.015414 | -0.00091653 | -0.00076913 | 0.061663 | 0.0076516 | 0.06194 | -66.8205 | 0.033457 | -66.7689 | 56.2335 | 56.0922 | 56.2161 | -66.8513 | -66.8115 | 0.03241 | -66.8414 | 56.1528 | 56.2847 | 56.1414 | -67.0103 | -0.068109 | -0.12634 | -0.037381 | 0.014246 | 0.082355 | -0.26768 | -0.14375 | -0.22716 | -0.2071 | -0.028345 | -0.058271 | 0.16889 | -0.075132 | -0.21844 | 123.0167 | 122.8753 | 122.9993 | 66.8166 | -123.2111 | 122.9359 | 123.0679 | 122.9246 | 66.8156 | -123.3702
156.7969 | 123.3902 | -66.7465 | 56.3187 | -0.0029761 | -0.0011624 | 0.0011025 | 0.054791 | -0.001391 | 0.063571 | 0.0077831 | -0.00027553 | -0.00076913 | 0.061877 | 0.0078652 | 0.061513 | -66.8205 | 0.0243 | -66.7643 | 56.2427 | 56.083 | 56.207 | -66.8467 | -66.8115 | 0.023253 | -66.8506 | 56.1482 | 56.2939 | 56.1506 | -67.0103 | -0.10015 | -0.075983 | -0.074002 | -0.017797 | 0.082354 | -0.23564 | -0.11171 | -0.26378 | -0.17048 | -0.064966 | -0.10405 | 0.15973 | -0.024776 | -0.16809 | 122.9892 | 122.8295 | 122.9535 | 66.7708 | -123.1653 | 122.8947 | 123.0404 | 122.8971 | 66.7698 | -123.329
157.7969 | 123.3215 | -66.7831 | 56.3187 | -0.010607 | -0.0009486 | 0.0011025 | 0.055432 | -0.002032 | 0.063571 | -0.0074779 | -0.00048933 | -0.00076913 | 0.061449 | 0.0078652 | 0.061513 | -66.8251 | 0.028878 | -66.7689 | 56.2427 | 56.0784 | 56.2115 | -66.8604 | -66.8069 | 0.03241 | -66.846 | 56.1619 | 56.2847 | 56.146 | -67.0103 | -0.077266 | -0.075983 | -0.04196 | 0.014246 | 0.091512 | -0.24022 | -0.10713 | -0.22716 | -0.15675 | -0.023766 | -0.06285 | 0.16431 | -0.033934 | -0.17267 | 123.0258 | 122.8616 | 122.9947 | 66.812 | -123.1791 | 122.9451 | 123.0679 | 122.9291 | 66.8156 | -123.329
158.8125 | 123.3582 | -66.774 | 56.2775 | -0.010607 | -0.0011624 | 0.0013163 | 0.054791 | -0.0018182 | 0.063785 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061449 | 0.0078652 | 0.061513 | -66.8205 | 0.0243 | -66.7506 | 56.2427 | 56.0876 | 56.207 | -66.8467 | -66.8115 | 0.027831 | -66.8506 | 56.1573 | 56.2847 | 56.1414 | -67.0103 | -0.072685 | -0.034784 | -0.046536 | 0.023404 | 0.096089 | -0.18986 | -0.070512 | -0.23631 | -0.12013 | -0.0375 | -0.076583 | 0.15973 | 0.007265 | -0.13605 | 123.0167 | 122.8616 | 122.9809 | 66.7983 | -123.1241 | 122.9313 | 123.0587 | 122.9154 | 66.8018 | -123.2878
159.7969 | 123.317 | -66.7786 | 56.3049 | -0.0029761 | -0.0009486 | 0.00088894 | 0.055218 | -0.002032 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061663 | 0.007438 | 0.061086 | -66.8159 | 0.028878 | -66.7643 | 56.2381 | 56.0922 | 56.2115 | -66.8513 | -66.8115 | 0.027831 | -66.8414 | 56.1528 | 56.2847 | 56.1368 | -67.0149 | -0.072687 | -0.066828 | -0.037381 | 0.014246 | 0.086933 | -0.21275 | -0.0934 | -0.23632 | -0.15217 | -0.032923 | -0.062849 | 0.17347 | -0.020201 | -0.16809 | 123.0167 | 122.8707 | 122.9901 | 66.8074 | -123.1562 | 122.9313 | 123.0633 | 122.9154 | 66.8064 | -123.3198
160.875 | 123.3215 | -66.8015 | 56.3507 | -0.0029761 | -0.0009486 | 0.0015299 | 0.055218 | -0.0018182 | 0.063571 | -0.0074779 | -0.00048933 | -0.0011965 | 0.061663 | 0.008079 | 0.06194 | -66.8205 | 0.0243 | -66.7552 | 56.2473 | 56.0922 | 56.2115 | -66.8421 | -66.8115 | 0.023253 | -66.8506 | 56.1665 | 56.2893 | 56.1552 | -67.0057 | -0.04064 | -0.10345 | -0.01907 | 0.046292 | 0.086932 | -0.25852 | -0.13918 | -0.20427 | -0.18421 | -0.010034 | -0.049117 | 0.15515 | -0.061398 | -0.19555 | 123.0487 | 122.8936 | 123.013 | 66.8258 | -123.1928 | 122.9679 | 123.0908 | 122.9566 | 66.8247 | -123.3564
161.7969 | 123.3902 | -66.7557 | 56.3141 | 0.0046549 | -0.0011624 | 0.0013163 | 0.055004 | -0.002032 | 0.063571 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061449 | 0.0078652 | 0.061513 | -66.8251 | 0.028878 | -66.7643 | 56.2335 | 56.083 | 56.207 | -66.8513 | -66.8161 | 0.03241 | -66.846 | 56.1619 | 56.2847 | 56.1368 | -67.0011 | -0.095575 | -0.080562 | -0.069426 | -0.008642 | 0.086933 | -0.23106 | -0.10713 | -0.24547 | -0.15217 | -0.060389 | -0.090316 | 0.15515 | -0.029356 | -0.17725 | 122.9892 | 122.8387 | 122.9626 | 66.7846 | -123.1653 | 122.9176 | 123.0404 | 122.8925 | 66.7881 | -123.3152
162.7969 | 123.3215 | -66.7511 | 56.369 | -0.0029761 | -0.001376 | 0.0011025 | 0.055004 | -0.0018182 | 0.063571 | 0.015414 | -0.00048933 | -0.00076913 | 0.061663 | 0.0078652 | 0.061299 | -66.8159 | 0.028878 | -66.7643 | 56.2335 | 56.083 | 56.2161 | -66.8604 | -66.8115 | 0.03241 | -66.8506 | 56.1619 | 56.2893 | 56.1368 | -67.0103 | -0.10931 | -0.13549 | -0.064846 | -0.013219 | 0.09609 | -0.28599 | -0.15291 | -0.2592 | -0.2071 | -0.060388 | -0.099471 | 0.15973 | -0.079709 | -0.23218 | 122.9846 | 122.8341 | 122.9672 | 66.78 | -123.2294 | 122.913 | 123.0404 | 122.8879 | 66.7835 | -123.3793
163.8906 | 123.381 | -66.7923 | 56.2866 | -0.0029761 | -0.0009486 | 0.0015299 | 0.054791 | -0.0016046 | 0.063785 | -0.0074779 | -0.00027553 | -0.00098273 | 0.061449 | 0.0078652 | 0.061299 | -66.8205 | 0.028878 | -66.7643 | 56.2427 | 56.083 | 56.2115 | -66.8558 | -66.8069 | 0.023253 | -66.8506 | 56.1619 | 56.2893 | 56.146 | -67.0057 | -0.063533 | -0.043939 | -0.028226 | 0.027979 | 0.091512 | -0.20359 | -0.075089 | -0.21343 | -0.1247 | -0.014611 | -0.058273 | 0.15515 | 0.002689 | -0.14062 | 123.035 | 122.8753 | 123.0038 | 66.8212 | -123.1425 | 122.9542 | 123.0816 | 122.9383 | 66.8156 | -123.2923
164.7969 | 123.3261 | -66.7786 | 56.3644 | 0.0046549 | -0.0011624 | 0.0011025 | 0.054791 | -0.002032 | 0.063785 | 0.015414 | -0.00027553 | -0.00034193 | 0.061449 | 0.008079 | 0.061299 | -66.8205 | 0.0243 | -66.7597 | 56.2381 | 56.0922 | 56.2161 | -66.8558 | -66.8023 | 0.023253 | -66.846 | 56.1528 | 56.2893 | 56.1506 | -67.0103 | -0.077266 | -0.12634 | -0.041959 | 0.018824 | 0.09609 | -0.27226 | -0.14833 | -0.23174 | -0.21168 | -0.023765 | -0.067428 | 0.16431 | -0.075131 | -0.21387 | 123.0167 | 122.8707 | 122.9947 | 66.8029 | -123.2203 | 122.9313 | 123.0679 | 122.9291 | 66.8018 | -123.3747
165.8594 | 123.2803 | -66.7877 | 56.3141 | 0.0046549 | -0.000735 | 0.0011025 | 0.054577 | -0.0022456 | 0.063999 | 0.015414 | -0.00048933 | -0.00076913 | 0.061449 | 0.0078652 | 0.061513 | -66.8159 | 0.028878 | -66.7643 | 56.2427 | 56.0968 | 56.207 | -66.8513 | -66.8069 | 0.03241 | -66.8506 | 56.1482 | 56.2985 | 56.146 | -67.0057 | -0.063531 | -0.071405 | -0.028225 | 0.023402 | 0.086933 | -0.21732 | -0.10713 | -0.218 | -0.16591 | -0.019188 | -0.06285 | 0.15515 | -0.01562 | -0.16809 | 123.0304 | 122.8845 | 122.9947 | 66.8166 | -123.1653 | 122.9359 | 123.0862 | 122.9337 | 66.8201 | -123.3198
166.7969 | 123.381 | -66.7786 | 56.2729 | 0.012286 | -0.0009486 | 0.0011025 | 0.055004 | -0.0018182 | 0.063785 | -0.0074779 | -0.00048933 | -0.00098273 | 0.061449 | 0.008079 | 0.061299 | -66.8159 | 0.0243 | -66.7643 | 56.2381 | 56.0784 | 56.2115 | -66.8558 | -66.8023 | 0.03241 | -66.8506 | 56.1573 | 56.2893 | 56.1414 | -67.0149 | -0.077266 | -0.034784 | -0.037381 | 0.014246 | 0.091512 | -0.19444 | -0.061356 | -0.23632 | -0.11555 | -0.023765 | -0.072006 | 0.16431 | 0.016422 | -0.13147 | 123.0167 | 122.857 | 122.9901 | 66.8029 | -123.1287 | 122.9359 | 123.0679 | 122.92 | 66.811 | -123.2878
167.7969 | 123.3673 | -66.7419 | 56.3278 | 0.0046549 | -0.0015898 | 0.0013163 | 0.054791 | -0.0018182 | 0.063785 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061236 | 0.008079 | 0.061513 | -66.8205 | 0.019721 | -66.7689 | 56.2335 | 56.083 | 56.2161 | -66.8513 | -66.8115 | 0.023253 | -66.846 | 56.1528 | 56.2985 | 56.1368 | -67.0149 | -0.10931 | -0.094295 | -0.07858 | -0.026953 | 0.082355 | -0.24479 | -0.11171 | -0.27294 | -0.17506 | -0.069544 | -0.10405 | 0.16889 | -0.029353 | -0.19098 | 122.9755 | 122.825 | 122.9581 | 66.7617 | -123.1791 | 122.8947 | 123.0404 | 122.8788 | 66.7652 | -123.3427
168.8125 | 123.3307 | -66.774 | 56.2775 | 0.0046549 | -0.001376 | 0.0013163 | 0.055218 | -0.0018182 | 0.063785 | 0.00015261 | -0.00091653 | -0.00098273 | 0.061663 | 0.008079 | 0.061513 | -66.8205 | 0.033457 | -66.7643 | 56.2335 | 56.0876 | 56.2115 | -66.8513 | -66.8023 | 0.023253 | -66.8506 | 56.1573 | 56.2847 | 56.1552 | -67.0057 | -0.077264 | -0.043941 | -0.046536 | 0.009669 | 0.086933 | -0.18986 | -0.065934 | -0.23174 | -0.12013 | -0.028342 | -0.076583 | 0.15515 | 0.007265 | -0.12231 | 123.0075 | 122.8616 | 122.9855 | 66.8074 | -123.1287 | 122.9313 | 123.0587 | 122.9291 | 66.7972 | -123.2832
169.7969 | 123.2849 | -66.7923 | 56.369 | 0.012286 | -0.0011624 | 0.0011025 | 0.055004 | -0.0022456 | 0.063785 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061022 | 0.008079 | 0.061726 | -66.8251 | 0.028878 | -66.7643 | 56.2427 | 56.083 | 56.207 | -66.8513 | -66.8069 | 0.03241 | -66.8551 | 56.1482 | 56.2939 | 56.1506 | -67.0103 | -0.058954 | -0.12634 | -0.032805 | 0.027979 | 0.086933 | -0.28599 | -0.16206 | -0.218 | -0.22084 | -0.014611 | -0.062852 | 0.15515 | -0.07513 | -0.21844 | 123.035 | 122.8753 | 122.9993 | 66.8212 | -123.2203 | 122.9405 | 123.0862 | 122.9429 | 66.8247 | -123.3793
170.8594 | 123.349 | -66.7923 | 56.4011 | -0.0029761 | -0.0011624 | 0.0011025 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.0078652 | 0.061513 | -66.8159 | 0.038035 | -66.7552 | 56.2473 | 56.0876 | 56.207 | -66.8604 | -66.8069 | 0.027831 | -66.8368 | 56.1619 | 56.2893 | 56.1506 | -67.0057 | -0.068111 | -0.1538 | -0.023648 | 0.037136 | 0.10525 | -0.31346 | -0.19411 | -0.21343 | -0.23915 | -0.014611 | -0.044537 | 0.16889 | -0.11175 | -0.25049 | 123.0396 | 122.8799 | 122.9993 | 66.8303 | -123.2615 | 122.9542 | 123.0816 | 122.9429 | 66.8201 | -123.4068
171.7969 | 123.3307 | -66.774 | 56.2775 | 0.0046549 | -0.000735 | 0.00067514 | 0.055004 | -0.0018182 | 0.063785 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061449 | 0.0078652 | 0.061513 | -66.8251 | 0.019721 | -66.7643 | 56.2335 | 56.0876 | 56.2161 | -66.8513 | -66.7977 | 0.023253 | -66.8551 | 56.1528 | 56.2893 | 56.146 | -67.0103 | -0.077264 | -0.043941 | -0.051115 | 0.009669 | 0.086933 | -0.18986 | -0.061355 | -0.23631 | -0.12471 | -0.023763 | -0.081162 | 0.15515 | 0.011844 | -0.13147 | 123.0075 | 122.8616 | 122.9901 | 66.7937 | -123.1287 | 122.9267 | 123.0633 | 122.92 | 66.7972 | -123.2878
172.7969 | 123.2941 | -66.7969 | 56.3507 | -0.0029761 | -0.0011624 | 0.0011025 | 0.055432 | -0.0018182 | 0.063999 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061449 | 0.0082926 | 0.061299 | -66.8159 | 0.0243 | -66.7689 | 56.2381 | 56.083 | 56.2253 | -66.8558 | -66.8069 | 0.03241 | -66.846 | 56.1573 | 56.2893 | 56.146 | -67.0057 | -0.058955 | -0.1126 | -0.01907 | 0.027979 | 0.086934 | -0.26768 | -0.12544 | -0.20885 | -0.19337 | -0.010033 | -0.049117 | 0.15973 | -0.061398 | -0.20471 | 123.035 | 122.8799 | 123.0221 | 66.8212 | -123.2065 | 122.9542 | 123.0862 | 122.9429 | 66.8293 | -123.3564
173.7969 | 123.2529 | -66.8015 | 56.3324 | 0.0046549 | -0.0011624 | 0.0011025 | 0.054577 | -0.0018182 | 0.063571 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061663 | 0.0082926 | 0.061299 | -66.8159 | 0.038035 | -66.7552 | 56.2335 | 56.0968 | 56.2115 | -66.8558 | -66.8069 | 0.023253 | -66.8414 | 56.1573 | 56.2939 | 56.1506 | -67.0103 | -0.054377 | -0.098872 | -0.014492 | 0.046292 | 0.10067 | -0.23563 | -0.12087 | -0.20885 | -0.17506 | -0.005455 | -0.03996 | 0.16889 | -0.038508 | -0.18182 | 123.035 | 122.8982 | 123.013 | 66.8395 | -123.1882 | 122.9588 | 123.0953 | 122.952 | 66.8247 | -123.3427
174.8594 | 123.2849 | -66.7969 | 56.3507 | 0.0046549 | -0.0009486 | 0.0013163 | 0.054577 | -0.0022456 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061663 | 0.0082926 | 0.061086 | -66.8251 | 0.028878 | -66.7597 | 56.2381 | 56.083 | 56.2253 | -66.8558 | -66.8069 | 0.03241 | -66.8368 | 56.1528 | 56.2847 | 56.146 | -67.0057 | -0.058955 | -0.1126 | -0.028227 | 0.037135 | 0.09609 | -0.26768 | -0.12544 | -0.20885 | -0.19795 | -0.010033 | -0.039959 | 0.16889 | -0.065977 | -0.20471 | 123.035 | 122.8799 | 123.0221 | 66.8258 | -123.2065 | 122.9496 | 123.0816 | 122.9429 | 66.8293 | -123.3564
175.7969 | 123.2986 | -66.806 | 56.3232 | -0.0029761 | -0.001376 | 0.0011025 | 0.054791 | -0.002032 | 0.063999 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061877 | 0.0082926 | 0.061299 | -66.8159 | 0.028878 | -66.7552 | 56.2381 | 56.0968 | 56.2115 | -66.8604 | -66.8115 | 0.03241 | -66.846 | 56.1528 | 56.2985 | 56.1414 | -67.0103 | -0.054378 | -0.085138 | -0.009915 | 0.050869 | 0.10525 | -0.22648 | -0.11171 | -0.20427 | -0.17048 | -0.005457 | -0.039962 | 0.16431 | -0.024775 | -0.18182 | 123.0441 | 122.9028 | 123.0176 | 66.8349 | -123.1837 | 122.9588 | 123.1045 | 122.9474 | 66.8384 | -123.3335
176.8125 | 123.2437 | -66.7969 | 56.3416 | 0.0046549 | -0.0011624 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061449 | 0.0078652 | 0.061086 | -66.8159 | 0.0243 | -66.7689 | 56.2427 | 56.0922 | 56.2161 | -66.8558 | -66.8115 | 0.027831 | -66.846 | 56.1528 | 56.2939 | 56.1506 | -67.0057 | -0.058955 | -0.098871 | -0.01907 | 0.027979 | 0.086934 | -0.24937 | -0.12544 | -0.20885 | -0.18879 | -0.014612 | -0.049117 | 0.15973 | -0.047664 | -0.19098 | 123.0396 | 122.8891 | 123.013 | 66.8212 | -123.1974 | 122.9496 | 123.0908 | 122.9475 | 66.8247 | -123.3473
177.7969 | 123.2666 | -66.7877 | 56.2958 | -0.0029761 | -0.0011624 | 0.0011025 | 0.054791 | -0.0024592 | 0.063785 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061877 | 0.0082926 | 0.061513 | -66.8159 | 0.033457 | -66.7506 | 56.2427 | 56.0922 | 56.2161 | -66.8558 | -66.8023 | 0.027831 | -66.8551 | 56.1573 | 56.2847 | 56.1552 | -67.0057 | -0.06811 | -0.053094 | -0.028225 | 0.037137 | 0.10525 | -0.20359 | -0.079665 | -0.218 | -0.13844 | -0.014609 | -0.067429 | 0.15057 | -0.011045 | -0.14062 | 123.0304 | 122.8799 | 123.0038 | 66.8212 | -123.1516 | 122.9451 | 123.0725 | 122.9429 | 66.8156 | -123.3015
178.7969 | 123.2941 | -66.8106 | 56.3049 | 0.0046549 | -0.0011624 | 0.0013163 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00048933 | -0.0011965 | 0.061449 | 0.008079 | 0.061086 | -66.8159 | 0.0243 | -66.7552 | 56.2335 | 56.0922 | 56.2115 | -66.8558 | -66.8069 | 0.027831 | -66.8414 | 56.1528 | 56.2847 | 56.1323 | -67.0103 | -0.045222 | -0.071407 | -0.005337 | 0.055447 | 0.10067 | -0.21275 | -0.0934 | -0.19969 | -0.15217 | 0.0037 | -0.030805 | 0.16889 | -0.020201 | -0.17267 | 123.0441 | 122.9028 | 123.0221 | 66.8349 | -123.1608 | 122.9634 | 123.0953 | 122.9429 | 66.8384 | -123.3152
179.8594 | 123.2803 | -66.8198 | 56.3232 | -0.0029761 | -0.001376 | 0.0013163 | 0.054791 | -0.002032 | 0.063999 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061236 | 0.008079 | 0.061726 | -66.8114 | 0.033457 | -66.7597 | 56.2427 | 56.1059 | 56.2207 | -66.8558 | -66.8069 | 0.03241 | -66.8414 | 56.1528 | 56.2847 | 56.1597 | -67.0103 | -0.036067 | -0.08056 | 0.008396 | 0.060023 | 0.09609 | -0.21732 | -0.10255 | -0.19054 | -0.17048 | 0.012855 | -0.02165 | 0.16889 | -0.038511 | -0.16351 | 123.0624 | 122.9257 | 123.0405 | 66.8532 | -123.1791 | 122.9725 | 123.1045 | 122.9795 | 66.8522 | -123.3335
180.7969 | 123.2529 | -66.7969 | 56.3141 | 0.012286 | -0.001376 | 0.0013163 | 0.055218 | -0.002032 | 0.063571 | -0.0074779 | -0.00027553 | -0.0011965 | 0.061663 | 0.0082926 | 0.061299 | -66.8205 | 0.0243 | -66.7643 | 56.2335 | 56.0968 | 56.2207 | -66.8604 | -66.8069 | 0.027831 | -66.8414 | 56.1482 | 56.2893 | 56.146 | -67.0103 | -0.063533 | -0.080562 | -0.023648 | 0.032557 | 0.09609 | -0.21732 | -0.093397 | -0.21343 | -0.16591 | -0.010033 | -0.044538 | 0.16889 | -0.024777 | -0.16809 | 123.0304 | 122.8936 | 123.0176 | 66.8212 | -123.1745 | 122.9451 | 123.0862 | 122.9429 | 66.8247 | -123.3244
181.8125 | 123.2574 | -66.8427 | 56.3232 | -0.010607 | -0.0011624 | 0.00088894 | 0.055004 | -0.0018182 | 0.063785 | 0.0077831 | -0.00091653 | -0.00098273 | 0.061449 | 0.0085064 | 0.061086 | -66.8205 | 0.0243 | -66.7643 | 56.2427 | 56.0922 | 56.2161 | -66.8513 | -66.8115 | 0.018674 | -66.846 | 56.1482 | 56.2939 | 56.1414 | -67.0103 | -0.0086 | -0.08056 | 0.022128 | 0.078333 | 0.086933 | -0.23106 | -0.10713 | -0.16765 | -0.17506 | 0.031164 | -0.003341 | 0.16431 | -0.029353 | -0.18182 | 123.0853 | 122.9348 | 123.0588 | 66.867 | -123.1745 | 122.9908 | 123.1365 | 122.9841 | 66.8613 | -123.3335
182.8594 | 123.2346 | -66.806 | 56.3599 | -0.010607 | -0.0011624 | 0.0011025 | 0.055218 | -0.002032 | 0.063785 | 0.015414 | -0.00048933 | -0.00098273 | 0.061663 | 0.0082926 | 0.061299 | -66.8114 | 0.0243 | -66.7552 | 56.2381 | 56.083 | 56.2207 | -66.8513 | -66.8115 | 0.03241 | -66.8414 | 56.1573 | 56.2893 | 56.1643 | -67.0149 | -0.045221 | -0.12176 | -0.005337 | 0.050869 | 0.09609 | -0.27684 | -0.13917 | -0.20885 | -0.20252 | -0.005457 | -0.035383 | 0.17347 | -0.070553 | -0.19555 | 123.0441 | 122.8891 | 123.0267 | 66.8303 | -123.2111 | 122.9634 | 123.0953 | 122.9703 | 66.8384 | -123.3747
183.7969 | 123.2162 | -66.8198 | 56.3232 | -0.0029761 | -0.0011624 | 0.0015299 | 0.054791 | -0.002032 | 0.063999 | 0.00015261 | -0.00070293 | -0.0011965 | 0.061877 | 0.0082926 | 0.061299 | -66.8205 | 0.033457 | -66.7597 | 56.2427 | 56.0968 | 56.2161 | -66.8513 | -66.8115 | 0.027831 | -66.846 | 56.1528 | 56.2939 | 56.1414 | -67.0011 | -0.031488 | -0.08056 | -0.00076 | 0.060023 | 0.091511 | -0.22648 | -0.10713 | -0.18138 | -0.17048 | 0.008276 | -0.026229 | 0.15515 | -0.029353 | -0.18182 | 123.0624 | 122.9165 | 123.0359 | 66.8532 | -123.1745 | 122.9725 | 123.1137 | 122.9612 | 66.8476 | -123.3244
184.7969 | 123.2391 | -66.8106 | 56.3232 | -0.0029761 | -0.0011624 | 0.0013163 | 0.055004 | -0.002032 | 0.063785 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061236 | 0.0085064 | 0.061513 | -66.8205 | 0.033457 | -66.7643 | 56.2381 | 56.0968 | 56.2161 | -66.8513 | -66.8069 | 0.027831 | -66.846 | 56.1528 | 56.2939 | 56.1414 | -67.0103 | -0.040643 | -0.085138 | -0.009915 | 0.04629 | 0.086933 | -0.22648 | -0.10713 | -0.19969 | -0.17048 | 0.0037 | -0.035384 | 0.16431 | -0.029353 | -0.18182 | 123.0487 | 122.9074 | 123.0267 | 66.8441 | -123.1745 | 122.9634 | 123.1045 | 122.952 | 66.8384 | -123.3335
185.8594 | 123.3078 | -66.7923 | 56.3278 | 0.0046549 | -0.0011624 | 0.0011025 | 0.054791 | -0.002032 | 0.063785 | 0.015414 | -0.00070293 | -0.00055553 | 0.061449 | 0.0082926 | 0.061299 | -66.8297 | 0.028878 | -66.7552 | 56.2381 | 56.0876 | 56.2161 | -66.8604 | -66.8069 | 0.027831 | -66.846 | 56.1619 | 56.2893 | 56.1368 | -67.0103 | -0.068111 | -0.089716 | -0.037383 | 0.037136 | 0.10525 | -0.24021 | -0.11171 | -0.218 | -0.1659 | -0.014611 | -0.053695 | 0.16431 | -0.03851 | -0.19098 | 123.0304 | 122.8799 | 123.0084 | 66.8212 | -123.1882 | 122.9542 | 123.0816 | 122.9291 | 66.8201 | -123.3381
186.8125 | 123.262 | -66.8015 | 56.3461 | 0.0046549 | -0.0009486 | 0.0013163 | 0.054577 | -0.0016046 | 0.063785 | -0.0074779 | -0.00091653 | -0.00076913 | 0.061449 | 0.0082926 | 0.061299 | -66.8159 | 0.028878 | -66.7689 | 56.2335 | 56.083 | 56.2161 | -66.8513 | -66.8069 | 0.023253 | -66.8506 | 56.1528 | 56.2847 | 56.1552 | -67.0057 | -0.049798 | -0.11261 | -0.014492 | 0.032557 | 0.082355 | -0.2631 | -0.13002 | -0.20427 | -0.19337 | -0.005455 | -0.049117 | 0.15515 | -0.061399 | -0.19098 | 123.035 | 122.8845 | 123.0176 | 66.8303 | -123.1974 | 122.9542 | 123.0862 | 122.9566 | 66.8247 | -123.3519
187.7969 | 123.2346 | -66.8152 | 56.3416 | 0.012286 | -0.001376 | 0.0015299 | 0.054577 | -0.002032 | 0.063144 | 0.015414 | -0.00070293 | -0.00055553 | 0.061236 | 0.00872 | 0.061299 | -66.8114 | 0.028878 | -66.7643 | 56.2427 | 56.0876 | 56.2207 | -66.8558 | -66.8069 | 0.03241 | -66.8414 | 56.1528 | 56.2802 | 56.1414 | -67.0057 | -0.040644 | -0.098871 | 0.003819 | 0.050868 | 0.091512 | -0.25395 | -0.12086 | -0.19054 | -0.18879 | 0.008278 | -0.026227 | 0.16431 | -0.0614 | -0.20013 | 123.0579 | 122.9028 | 123.0359 | 66.8441 | -123.1974 | 122.9679 | 123.0953 | 122.9566 | 66.8476 | -123.3473
188.7969 | 123.3444 | -66.7603 | 56.3004 | 0.0046549 | -0.0011624 | 0.0013163 | 0.054791 | -0.0022456 | 0.063999 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.0082926 | 0.061299 | -66.8251 | 0.0243 | -66.7643 | 56.2381 | 56.0968 | 56.2161 | -66.8421 | -66.8069 | 0.03241 | -66.846 | 56.1573 | 56.2893 | 56.1323 | -67.0057 | -0.081839 | -0.06225 | -0.064848 | -0.004064 | 0.077775 | -0.20359 | -0.084243 | -0.24547 | -0.14301 | -0.046654 | -0.085738 | 0.15973 | -0.011044 | -0.16809 | 122.9984 | 122.857 | 122.9764 | 66.7846 | -123.1424 | 122.9176 | 123.0496 | 122.8925 | 66.7927 | -123.3061
189.7969 | 123.2346 | -66.8243 | 56.3095 | -0.0029761 | -0.001376 | 0.0011025 | 0.054577 | -0.0024592 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.00076913 | 0.061022 | 0.0082926 | 0.061726 | -66.8159 | 0.028878 | -66.7506 | 56.2473 | 56.0922 | 56.2115 | -66.8329 | -66.8115 | 0.03241 | -66.8414 | 56.1528 | 56.2939 | 56.146 | -67.0057 | -0.008594 | -0.062249 | 0.008396 | 0.073758 | 0.082352 | -0.21732 | -0.097977 | -0.18138 | -0.15675 | 0.012854 | -0.017072 | 0.16431 | -0.01562 | -0.16351 | 123.0716 | 122.9165 | 123.0359 | 66.8532 | -123.1424 | 122.9771 | 123.1182 | 122.9703 | 66.8568 | -123.3152
190.7969 | 123.3765 | -66.7877 | 56.2683 | 0.012286 | -0.001376 | 0.0011025 | 0.055004 | -0.002032 | 0.063785 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061236 | 0.0085064 | 0.061299 | -66.8114 | 0.019721 | -66.7552 | 56.2381 | 56.0922 | 56.2161 | -66.8421 | -66.8023 | 0.027831 | -66.8414 | 56.1482 | 56.2802 | 56.1368 | -67.0011 | -0.054373 | -0.030207 | -0.023647 | 0.032559 | 0.086932 | -0.17613 | -0.0522 | -0.21342 | -0.12013 | -0.014609 | -0.053693 | 0.15973 | 0.011842 | -0.13147 | 123.0258 | 122.8799 | 123.0038 | 66.8074 | -123.1104 | 122.9359 | 123.0679 | 122.9246 | 66.8156 | -123.2695
191.875 | 123.349 | -66.7877 | 56.2866 | 0.0046549 | -0.0009486 | 0.0013163 | 0.055004 | -0.002032 | 0.063571 | 0.00015261 | -0.00027553 | -0.00076913 | 0.061449 | 0.0085064 | 0.061299 | -66.8205 | 0.028878 | -66.7597 | 56.2381 | 56.0922 | 56.2161 | -66.8513 | -66.8069 | 0.023253 | -66.846 | 56.1573 | 56.2847 | 56.1552 | -67.0103 | -0.063531 | -0.048517 | -0.032803 | 0.02798 | 0.091511 | -0.19444 | -0.07051 | -0.22258 | -0.12928 | -0.019188 | -0.058272 | 0.16431 | -0.00189 | -0.13147 | 123.0258 | 122.8799 | 123.0038 | 66.8166 | -123.1379 | 122.9451 | 123.0725 | 122.9429 | 66.811 | -123.2969
192.7969 | 123.3444 | -66.7923 | 56.3141 | -0.010607 | -0.001376 | 0.0015299 | 0.054791 | -0.002032 | 0.063571 | 0.00015261 | -0.00027553 | -0.00076913 | 0.061663 | 0.00872 | 0.061086 | -66.8114 | 0.033457 | -66.7597 | 56.2427 | 56.0968 | 56.207 | -66.8421 | -66.8023 | 0.027831 | -66.8414 | 56.1573 | 56.2847 | 56.1414 | -67.0103 | -0.049796 | -0.071405 | -0.01907 | 0.032557 | 0.082353 | -0.21732 | -0.10713 | -0.218 | -0.15675 | -0.010032 | -0.049116 | 0.16889 | -0.029356 | -0.17267 | 123.035 | 122.8891 | 122.9993 | 66.8258 | -123.1562 | 122.9496 | 123.077 | 122.9337 | 66.8201 | -123.3244
193.8594 | 123.2574 | -66.806 | 56.337 | 0.0046549 | -0.0015898 | 0.0011025 | 0.055004 | -0.002032 | 0.063785 | -0.0074779 | -0.00070293 | -0.00076913 | 0.061663 | 0.0085064 | 0.061513 | -66.8159 | 0.028878 | -66.7643 | 56.2473 | 56.0876 | 56.2253 | -66.8558 | -66.8069 | 0.027831 | -66.8551 | 56.1528 | 56.2939 | 56.1506 | -67.0057 | -0.0498 | -0.089715 | -0.009915 | 0.041712 | 0.091512 | -0.24937 | -0.11171 | -0.19969 | -0.18422 | -0.000878 | -0.049119 | 0.15057 | -0.043086 | -0.1864 | 123.0533 | 122.8936 | 123.0313 | 66.8349 | -123.1928 | 122.9588 | 123.0999 | 122.9566 | 66.8339 | -123.3427
194.7969 | 123.3078 | -66.7786 | 56.3141 | 0.0046549 | -0.001376 | 0.0013163 | 0.055004 | -0.002032 | 0.063785 | 0.00015261 | -0.00027553 | -0.00098273 | 0.061236 | 0.0085064 | 0.061299 | -66.8205 | 0.0243 | -66.7506 | 56.2427 | 56.0876 | 56.2161 | -66.8513 | -66.8023 | 0.027831 | -66.846 | 56.1528 | 56.2893 | 56.1506 | -67.0149 | -0.072687 | -0.071405 | -0.041959 | 0.027981 | 0.10067 | -0.22648 | -0.097976 | -0.23632 | -0.16133 | -0.023765 | -0.067428 | 0.16889 | -0.024777 | -0.16351 | 123.0212 | 122.8662 | 122.9947 | 66.8029 | -123.1653 | 122.9313 | 123.0679 | 122.9291 | 66.8064 | -123.329
195.8594 | 123.2254 | -66.8198 | 56.3507 | -0.010607 | -0.0015898 | 0.0013163 | 0.055218 | -0.002032 | 0.063785 | 0.015414 | -0.00070293 | -0.00055553 | 0.061236 | 0.0085064 | 0.061299 | -66.8159 | 0.028878 | -66.7506 | 56.2427 | 56.0922 | 56.2207 | -66.8604 | -66.8069 | 0.03241 | -66.846 | 56.1665 | 56.2893 | 56.1506 | -67.0057 | -0.040645 | -0.10803 | 0.003818 | 0.06918 | 0.10983 | -0.25852 | -0.13002 | -0.18596 | -0.18421 | 0.012855 | -0.026229 | 0.15973 | -0.061398 | -0.20013 | 123.0624 | 122.9119 | 123.0405 | 66.8486 | -123.2111 | 122.9863 | 123.1091 | 122.9703 | 66.8522 | -123.3564
196.7969 | 123.3032 | -66.7877 | 56.3507 | -0.0029761 | -0.0015898 | 0.0011025 | 0.054791 | -0.002032 | 0.063999 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061236 | 0.0089336 | 0.061299 | -66.8114 | 0.028878 | -66.7506 | 56.2381 | 56.0922 | 56.2207 | -66.8513 | -66.8023 | 0.027831 | -66.846 | 56.1573 | 56.2847 | 56.1414 | -67.0057 | -0.063531 | -0.1126 | -0.023647 | 0.037137 | 0.10067 | -0.25852 | -0.13002 | -0.218 | -0.19337 | -0.014609 | -0.058272 | 0.15973 | -0.065977 | -0.20929 | 123.0258 | 122.8799 | 123.0084 | 66.8166 | -123.202 | 122.9451 | 123.0725 | 122.9291 | 66.8156 | -123.3564
197.7969 | 123.2849 | -66.8243 | 56.3049 | -0.010607 | -0.0015898 | 0.0011025 | 0.054791 | -0.002032 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061449 | 0.0082926 | 0.061513 | -66.8114 | 0.033457 | -66.7414 | 56.2427 | 56.0968 | 56.2161 | -66.8558 | -66.8069 | 0.027831 | -66.8368 | 56.1528 | 56.2893 | 56.146 | -67.0103 | -0.031489 | -0.06225 | 0.012974 | 0.082914 | 0.1144 | -0.20817 | -0.088821 | -0.18596 | -0.15217 | 0.017433 | -0.012493 | 0.17347 | -0.015622 | -0.15894 | 123.067 | 122.9211 | 123.0405 | 66.8578 | -123.1608 | 122.9771 | 123.1137 | 122.9703 | 66.8522 | -123.3152
198.8594 | 123.2254 | -66.8015 | 56.3232 | -0.0029761 | -0.001376 | 0.0013163 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00091653 | -0.0011965 | 0.061663 | 0.00872 | 0.061513 | -66.8114 | 0.028878 | -66.746 | 56.2335 | 56.1013 | 56.2207 | -66.8558 | -66.8069 | 0.03241 | -66.8414 | 56.1573 | 56.2939 | 56.146 | -67.0057 | -0.054377 | -0.089717 | -0.009914 | 0.055448 | 0.10983 | -0.2219 | -0.10255 | -0.20427 | -0.1659 | -0.005455 | -0.03996 | 0.16431 | -0.029353 | -0.17725 | 123.035 | 122.9028 | 123.0221 | 66.8303 | -123.1791 | 122.9588 | 123.0953 | 122.9474 | 66.8339 | -123.329
199.7969 | 123.3902 | -66.7786 | 56.3095 | 0.0046549 | -0.0015898 | 0.0015299 | 0.055004 | -0.002673 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.00872 | 0.061299 | -66.8068 | 0.0243 | -66.7506 | 56.2335 | 56.0922 | 56.2115 | -66.8513 | -66.8115 | 0.018674 | -66.8551 | 56.1528 | 56.2893 | 56.1552 | -67.0149 | -0.072687 | -0.075984 | -0.028224 | 0.027981 | 0.10067 | -0.21732 | -0.097977 | -0.23632 | -0.15675 | -0.032923 | -0.076585 | 0.15973 | -0.020199 | -0.15436 | 123.0121 | 122.8707 | 122.9901 | 66.8029 | -123.1608 | 122.9313 | 123.0679 | 122.9337 | 66.7972 | -123.3244
200.7969 | 123.3627 | -66.7648 | 56.2958 | -0.0029761 | -0.0011624 | 0.0017435 | 0.055218 | -0.002032 | 0.063571 | 0.00015261 | -0.00027553 | -0.0011965 | 0.061663 | 0.00872 | 0.061513 | -66.8159 | 0.028878 | -66.7552 | 56.2427 | 56.0876 | 56.2161 | -66.8421 | -66.8069 | 0.014095 | -66.846 | 56.1573 | 56.2893 | 56.146 | -67.0057 | -0.077261 | -0.053094 | -0.051113 | 0.009671 | 0.086932 | -0.20817 | -0.079665 | -0.24089 | -0.13844 | -0.042076 | -0.08116 | 0.15973 | -0.006466 | -0.14978 | 123.0075 | 122.8524 | 122.9809 | 66.7937 | -123.1379 | 122.9222 | 123.0541 | 122.9108 | 66.7789 | -123.3015
201.875 | 123.317 | -66.7969 | 56.3187 | 0.0046549 | -0.0018034 | 0.0011025 | 0.055432 | -0.0022456 | 0.063571 | 0.015414 | -0.00048933 | -0.00098273 | 0.061663 | 0.0082926 | 0.061299 | -66.8159 | 0.0243 | -66.746 | 56.2473 | 56.0876 | 56.2207 | -66.8604 | -66.8069 | 0.023253 | -66.8368 | 56.1528 | 56.2847 | 56.1506 | -67.0149 | -0.063533 | -0.071405 | -0.01907 | 0.05087 | 0.1144 | -0.23106 | -0.097975 | -0.21801 | -0.16591 | -0.010033 | -0.039959 | 0.17805 | -0.033934 | -0.16809 | 123.0441 | 122.8845 | 123.0176 | 66.8212 | -123.1791 | 122.9496 | 123.0816 | 122.9475 | 66.8201 | -123.3335
202.7969 | 123.3124 | -66.7786 | 56.3232 | -0.0029761 | -0.0011624 | 0.0013163 | 0.055004 | -0.0018182 | 0.063571 | 0.015414 | -0.00048933 | -0.0011965 | 0.061236 | 0.00872 | 0.061513 | -66.8159 | 0.0243 | -66.7506 | 56.2381 | 56.0876 | 56.2207 | -66.8513 | -66.8023 | 0.03241 | -66.8506 | 56.1482 | 56.2893 | 56.1414 | -67.0103 | -0.072687 | -0.085138 | -0.037381 | 0.027981 | 0.10067 | -0.23564 | -0.10255 | -0.23174 | -0.17506 | -0.023765 | -0.072006 | 0.15973 | -0.033932 | -0.18182 | 123.0167 | 122.8662 | 122.9993 | 66.8029 | -123.1745 | 122.9267 | 123.0679 | 122.92 | 66.811 | -123.3335
203.7969 | 123.3856 | -66.7465 | 56.2958 | -0.0029761 | -0.0015898 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.00015261 | -0.00048933 | -0.00076913 | 0.060808 | 0.00872 | 0.061299 | -66.8159 | 0.028878 | -66.7506 | 56.2381 | 56.0922 | 56.2115 | -66.8467 | -66.8115 | 0.027831 | -66.8506 | 56.1528 | 56.2847 | 56.146 | -67.0103 | -0.10015 | -0.057672 | -0.069424 | -0.004062 | 0.096089 | -0.20359 | -0.084244 | -0.26378 | -0.14302 | -0.064966 | -0.10405 | 0.15973 | -0.011045 | -0.14978 | 122.9846 | 122.8387 | 122.9581 | 66.7754 | -123.1424 | 122.8993 | 123.0313 | 122.8925 | 66.7744 | -123.3061
204.875 | 123.3994 | -66.7648 | 56.3187 | 0.0046549 | -0.001376 | 0.0011025 | 0.055004 | -0.0022456 | 0.063785 | 0.015414 | -0.00027553 | -0.00076913 | 0.061236 | 0.0085064 | 0.061086 | -66.8159 | 0.028878 | -66.7552 | 56.2427 | 56.0968 | 56.2253 | -66.8513 | -66.8069 | 0.027831 | -66.8368 | 56.1573 | 56.2847 | 56.146 | -67.0057 | -0.086419 | -0.075983 | -0.051113 | 0.009671 | 0.09609 | -0.2219 | -0.093397 | -0.24089 | -0.16133 | -0.042076 | -0.072002 | 0.16889 | -0.033934 | -0.17267 | 123.0075 | 122.8616 | 122.9901 | 66.7937 | -123.1699 | 122.9222 | 123.0496 | 122.9108 | 66.7927 | -123.3244
205.7969 | 123.3765 | -66.7786 | 56.2912 | 0.0046549 | -0.0018034 | 0.0011025 | 0.055004 | -0.0024592 | 0.063571 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061022 | 0.00872 | 0.061299 | -66.8068 | 0.028878 | -66.7597 | 56.2427 | 56.0876 | 56.2115 | -66.8558 | -66.8069 | 0.023253 | -66.8551 | 56.1528 | 56.2939 | 56.146 | -67.0103 | -0.077266 | -0.048517 | -0.028224 | 0.018824 | 0.09609 | -0.20359 | -0.079667 | -0.23174 | -0.13844 | -0.028344 | -0.076585 | 0.15515 | 0.00269 | -0.1452 | 123.0212 | 122.8662 | 122.9901 | 66.8074 | -123.147 | 122.9313 | 123.0725 | 122.9246 | 66.8018 | -123.3015
206.7969 | 123.3078 | -66.7694 | 56.3599 | -0.0029761 | -0.0015898 | 0.0011025 | 0.055004 | -0.0022456 | 0.063785 | 0.00015261 | -0.00027553 | -0.00098273 | 0.061449 | 0.0085064 | 0.061513 | -66.8205 | 0.0243 | -66.7368 | 56.2381 | 56.1013 | 56.2115 | -66.8467 | -66.8069 | 0.027831 | -66.846 | 56.1573 | 56.2847 | 56.1552 | -67.0103 | -0.077263 | -0.12176 | -0.051114 | 0.032561 | 0.10982 | -0.25852 | -0.14833 | -0.24089 | -0.20252 | -0.037499 | -0.076583 | 0.16431 | -0.075132 | -0.20471 | 123.0075 | 122.8708 | 122.9809 | 66.7937 | -123.2065 | 122.9267 | 123.0541 | 122.9246 | 66.7972 | -123.3702
207.7969 | 123.3994 | -66.7419 | 56.2958 | 0.012286 | -0.0015898 | 0.00088894 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061236 | 0.0082926 | 0.061299 | -66.8114 | 0.028878 | -66.7414 | 56.2518 | 56.0876 | 56.2115 | -66.8558 | -66.8069 | 0.018674 | -66.846 | 56.1482 | 56.2893 | 56.1094 | -67.0103 | -0.11389 | -0.043937 | -0.069424 | 0.000516 | 0.1144 | -0.20817 | -0.084244 | -0.26836 | -0.14759 | -0.064965 | -0.10405 | 0.16431 | -0.006466 | -0.18641 | 122.9938 | 122.8295 | 122.9535 | 66.7708 | -123.1516 | 122.8901 | 123.0313 | 122.8513 | 66.7606 | -123.3061
208.7969 | 123.3627 | -66.7603 | 56.337 | 0.012286 | -0.001376 | 0.0013163 | 0.055004 | -0.0022456 | 0.063785 | 0.0077831 | -0.00070293 | -0.0011965 | 0.061236 | 0.0089336 | 0.061513 | -66.8114 | 0.0243 | -66.7506 | 56.2381 | 56.0922 | 56.2161 | -66.8558 | -66.8023 | 0.027831 | -66.8551 | 56.1528 | 56.2847 | 56.1414 | -67.0103 | -0.095576 | -0.098871 | -0.051113 | 0.009671 | 0.10525 | -0.24479 | -0.12086 | -0.25005 | -0.18422 | -0.042075 | -0.094895 | 0.15515 | -0.052244 | -0.19556 | 122.9984 | 122.8524 | 122.9764 | 66.7846 | -123.1928 | 122.913 | 123.045 | 122.9017 | 66.7881 | -123.3473
209.7969 | 123.3902 | -66.7648 | 56.2958 | 0.0046549 | -0.0015898 | 0.0011025 | 0.055218 | -0.002032 | 0.063571 | -0.0074779 | -0.00048933 | -0.00098273 | 0.061022 | 0.00872 | 0.061513 | -66.8159 | 0.028878 | -66.7552 | 56.2427 | 56.1013 | 56.2161 | -66.8467 | -66.8069 | 0.018674 | -66.8414 | 56.1528 | 56.2756 | 56.1231 | -67.0149 | -0.08184 | -0.053094 | -0.051113 | 0.009671 | 0.091511 | -0.19443 | -0.079665 | -0.25005 | -0.14302 | -0.042076 | -0.076581 | 0.17347 | -0.020202 | -0.17267 | 123.0075 | 122.8662 | 122.9809 | 66.7937 | -123.1424 | 122.9176 | 123.0404 | 122.8879 | 66.7835 | -123.3107
210.7969 | 123.381 | -66.7419 | 56.3141 | 0.0046549 | -0.0015898 | 0.0015299 | 0.054791 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.0011965 | 0.061449 | 0.0089336 | 0.061299 | -66.8205 | 0.028878 | -66.746 | 56.2427 | 56.1013 | 56.2253 | -66.8558 | -66.8069 | 0.023253 | -66.8368 | 56.1528 | 56.2893 | 56.1368 | -67.0057 | -0.11389 | -0.071405 | -0.07858 | -0.004062 | 0.10983 | -0.21274 | -0.088819 | -0.26378 | -0.16133 | -0.064965 | -0.094891 | 0.16889 | -0.024777 | -0.17725 | 122.9846 | 122.8433 | 122.9672 | 66.7708 | -123.1699 | 122.8947 | 123.0313 | 122.8788 | 66.7652 | -123.3198
211.7969 | 123.3856 | -66.7099 | 56.3187 | 0.012286 | -0.001376 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061236 | 0.0089336 | 0.061726 | -66.8114 | 0.0243 | -66.746 | 56.2473 | 56.0922 | 56.2253 | -66.8513 | -66.8023 | 0.023253 | -66.846 | 56.1528 | 56.2847 | 56.146 | -67.0057 | -0.14135 | -0.071405 | -0.10147 | -0.036105 | 0.10525 | -0.22648 | -0.093397 | -0.29582 | -0.16591 | -0.092429 | -0.13609 | 0.15973 | -0.033934 | -0.17267 | 122.9572 | 122.8021 | 122.9352 | 66.7342 | -123.1699 | 122.8627 | 122.9946 | 122.8559 | 66.7332 | -123.3244
212.875 | 123.2803 | -66.7877 | 56.3278 | -0.0029761 | -0.0015898 | 0.0011025 | 0.055004 | -0.0022456 | 0.063358 | 0.0077831 | -0.00091653 | -0.00098273 | 0.061663 | 0.0089336 | 0.061299 | -66.8114 | 0.0243 | -66.7414 | 56.2427 | 56.0922 | 56.2207 | -66.8604 | -66.8069 | 0.027831 | -66.8368 | 56.1573 | 56.2893 | 56.1597 | -67.0103 | -0.072688 | -0.085138 | -0.023647 | 0.046293 | 0.11898 | -0.23564 | -0.10713 | -0.22258 | -0.17048 | -0.019188 | -0.049114 | 0.17347 | -0.03851 | -0.16809 | 123.0304 | 122.8799 | 123.0084 | 66.812 | -123.1882 | 122.9451 | 123.077 | 122.9475 | 66.8156 | -123.3381
213.7969 | 123.3673 | -66.7694 | 56.2729 | 0.0046549 | -0.0015898 | 0.0011025 | 0.055218 | -0.0022456 | 0.063785 | 0.015414 | -0.00091653 | -0.00098273 | 0.061449 | 0.00872 | 0.061513 | -66.8205 | 0.0243 | -66.7552 | 56.2335 | 56.0968 | 56.2207 | -66.8513 | -66.8023 | 0.023253 | -66.846 | 56.1528 | 56.2802 | 56.1277 | -67.0057 | -0.081842 | -0.039363 | -0.051114 | 0.014248 | 0.09609 | -0.17612 | -0.052198 | -0.23631 | -0.12013 | -0.03292 | -0.076583 | 0.15973 | 0.007265 | -0.14521 | 123.0029 | 122.8662 | 122.9901 | 66.7937 | -123.1241 | 122.9222 | 123.0496 | 122.8971 | 66.7927 | -123.2786
214.7969 | 123.3673 | -66.7557 | 56.3049 | 0.0046549 | -0.0018034 | 0.0015299 | 0.055004 | -0.002032 | 0.063571 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061449 | 0.00872 | 0.061513 | -66.8159 | 0.028878 | -66.7597 | 56.2427 | 56.0968 | 56.2207 | -66.8513 | -66.8115 | 0.023253 | -66.8368 | 56.1573 | 56.2847 | 56.1277 | -67.0149 | -0.095575 | -0.06225 | -0.060269 | -0.004064 | 0.091511 | -0.20817 | -0.084242 | -0.2592 | -0.14759 | -0.055811 | -0.081158 | 0.17805 | -0.020201 | -0.17725 | 122.9984 | 122.8524 | 122.9764 | 66.7846 | -123.1562 | 122.913 | 123.0404 | 122.8834 | 66.7789 | -123.3198
215.7969 | 123.2986 | -66.806 | 56.3278 | -0.0029761 | -0.0015898 | 0.0013163 | 0.054577 | -0.002032 | 0.063571 | 0.015414 | -0.00070293 | -0.00098273 | 0.061236 | 0.0089336 | 0.061299 | -66.8159 | 0.028878 | -66.7552 | 56.2381 | 56.0922 | 56.2207 | -66.8513 | -66.8069 | 0.027831 | -66.8414 | 56.1573 | 56.2847 | 56.1506 | -67.0011 | -0.045221 | -0.089716 | -0.009915 | 0.050869 | 0.09609 | -0.23564 | -0.10713 | -0.19511 | -0.17048 | -0.000878 | -0.035383 | 0.15973 | -0.043089 | -0.17724 | 123.0441 | 122.8982 | 123.0267 | 66.8349 | -123.1791 | 122.9634 | 123.0908 | 122.9566 | 66.8339 | -123.329
216.8594 | 123.3765 | -66.7374 | 56.3049 | 0.019917 | -0.0018034 | 0.00088894 | 0.055218 | -0.0022456 | 0.063571 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061449 | 0.0091474 | 0.061513 | -66.8159 | 0.033457 | -66.7552 | 56.2335 | 56.1013 | 56.2161 | -66.8513 | -66.8023 | 0.023253 | -66.846 | 56.1482 | 56.2756 | 56.1506 | -67.0103 | -0.11389 | -0.071407 | -0.078579 | -0.017795 | 0.09609 | -0.20359 | -0.088821 | -0.27294 | -0.15675 | -0.064963 | -0.10863 | 0.16431 | -0.029358 | -0.15436 | 122.9709 | 122.8387 | 122.9535 | 66.7708 | -123.1562 | 122.8855 | 123.0129 | 122.8879 | 66.7606 | -123.3152
217.7969 | 123.2117 | -66.7786 | 56.3416 | 0.0046549 | -0.0015898 | 0.0013163 | 0.054577 | -0.002032 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061663 | 0.0089336 | 0.061513 | -66.8068 | 0.028878 | -66.7552 | 56.2427 | 56.0968 | 56.2161 | -66.8604 | -66.8069 | 0.023253 | -66.846 | 56.1573 | 56.2847 | 56.1552 | -67.0103 | -0.081844 | -0.098871 | -0.028224 | 0.023403 | 0.10525 | -0.24479 | -0.12544 | -0.23174 | -0.18421 | -0.028344 | -0.067428 | 0.16431 | -0.056822 | -0.1864 | 123.0212 | 122.8753 | 122.9947 | 66.8074 | -123.202 | 122.9359 | 123.0633 | 122.9337 | 66.8018 | -123.3519
218.7969 | 123.2666 | -66.8335 | 56.3095 | -0.010607 | -0.0018034 | 0.0011025 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061449 | 0.0091474 | 0.061726 | -66.8114 | 0.038035 | -66.7597 | 56.2427 | 56.0876 | 56.2115 | -66.8467 | -66.8069 | 0.036989 | -66.8368 | 56.1436 | 56.2847 | 56.1414 | -67.0103 | -0.013176 | -0.066827 | 0.022129 | 0.073756 | 0.086932 | -0.2219 | -0.097977 | -0.17681 | -0.16591 | 0.026588 | -0.003338 | 0.17347 | -0.024778 | -0.16809 | 123.0762 | 122.9211 | 123.045 | 66.8715 | -123.1562 | 122.9771 | 123.1182 | 122.9749 | 66.8705 | -123.3198
219.7969 | 123.2346 | -66.7969 | 56.3553 | 0.012286 | -0.002017 | 0.0015299 | 0.054791 | -0.0022456 | 0.063571 | 0.0077831 | -0.00048933 | -0.0011965 | 0.061236 | 0.0085064 | 0.061726 | -66.8159 | 0.0243 | -66.7643 | 56.2473 | 56.0968 | 56.2161 | -66.8604 | -66.8023 | 0.03241 | -66.8368 | 56.1573 | 56.2847 | 56.1506 | -67.0103 | -0.063533 | -0.10803 | -0.01907 | 0.032557 | 0.09609 | -0.25852 | -0.13918 | -0.21343 | -0.19795 | -0.005454 | -0.039959 | 0.17347 | -0.070555 | -0.20471 | 123.0441 | 122.8936 | 123.013 | 66.8212 | -123.2157 | 122.9542 | 123.0816 | 122.9475 | 66.8293 | -123.3656
220.7969 | 123.262 | -66.8106 | 56.3416 | -0.0029761 | -0.0018034 | 0.0011025 | 0.054791 | -0.0022456 | 0.063785 | 0.015414 | -0.00070293 | -0.00076913 | 0.061449 | 0.0091474 | 0.061726 | -66.8068 | 0.028878 | -66.7506 | 56.2473 | 56.0968 | 56.2115 | -66.8558 | -66.8206 | 0.027831 | -66.846 | 56.1528 | 56.2893 | 56.1368 | -67.0103 | -0.045222 | -0.094293 | 0.00382 | 0.060025 | 0.10525 | -0.24479 | -0.13002 | -0.19969 | -0.18879 | -0.010036 | -0.035384 | 0.16431 | -0.052243 | -0.20471 | 123.0579 | 122.9074 | 123.0221 | 66.8395 | -123.1974 | 122.9634 | 123.0999 | 122.9474 | 66.8384 | -123.3519
221.7969 | 123.2941 | -66.7923 | 56.3232 | -0.0029761 | -0.0015898 | 0.0013163 | 0.054791 | -0.002032 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061236 | 0.0089336 | 0.061513 | -66.8068 | 0.0243 | -66.7643 | 56.2427 | 56.0922 | 56.2253 | -66.8558 | -66.8023 | 0.023253 | -66.8506 | 56.1573 | 56.2847 | 56.1552 | -67.0149 | -0.063533 | -0.08056 | -0.014491 | 0.027979 | 0.091512 | -0.23106 | -0.097974 | -0.22258 | -0.1659 | -0.010032 | -0.058273 | 0.16431 | -0.038511 | -0.16809 | 123.035 | 122.8845 | 123.0176 | 66.8166 | -123.1791 | 122.9496 | 123.077 | 122.9475 | 66.8156 | -123.3381
222.7969 | 123.2803 | -66.8198 | 56.3232 | -0.0029761 | -0.0018034 | 0.00088894 | 0.054577 | -0.0022456 | 0.063785 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061236 | 0.0091474 | 0.061086 | -66.8068 | 0.028878 | -66.7597 | 56.2427 | 56.0876 | 56.2207 | -66.8558 | -66.8023 | 0.023253 | -66.846 | 56.1573 | 56.2847 | 56.146 | -67.0103 | -0.036067 | -0.08056 | 0.012975 | 0.060023 | 0.09609 | -0.23564 | -0.10255 | -0.19054 | -0.1659 | 0.017434 | -0.026229 | 0.16431 | -0.038511 | -0.17725 | 123.0624 | 122.9074 | 123.0405 | 66.8486 | -123.1791 | 122.9771 | 123.1045 | 122.9658 | 66.843 | -123.3335
223.8594 | 123.2391 | -66.8289 | 56.3232 | 0.012286 | -0.0015898 | 0.0013163 | 0.055004 | -0.0022456 | 0.063358 | 0.0077831 | -0.0011301 | -0.00076913 | 0.061449 | 0.0089336 | 0.061726 | -66.8022 | 0.0243 | -66.7552 | 56.2473 | 56.0968 | 56.2161 | -66.8467 | -66.8115 | 0.018674 | -66.846 | 56.1573 | 56.2847 | 56.1368 | -67.0149 | -0.017754 | -0.075982 | 0.026708 | 0.073757 | 0.091511 | -0.22648 | -0.10713 | -0.18596 | -0.1659 | 0.017431 | -0.017074 | 0.16889 | -0.038511 | -0.1864 | 123.0762 | 122.9257 | 123.045 | 66.8532 | -123.1699 | 122.9863 | 123.1136 | 122.9658 | 66.8476 | -123.3381
224.7969 | 123.3124 | -66.7923 | 56.2775 | -0.0029761 | -0.0018034 | 0.0015299 | 0.055004 | -0.0024592 | 0.063571 | 0.00015261 | -6.1934e-05 | -0.0011965 | 0.061663 | 0.0091474 | 0.061726 | -66.8068 | 0.0243 | -66.7597 | 56.2335 | 56.083 | 56.2115 | -66.8513 | -66.8069 | 0.023253 | -66.8368 | 56.1528 | 56.2893 | 56.1414 | -67.0149 | -0.058954 | -0.043941 | -0.014491 | 0.032557 | 0.091511 | -0.19444 | -0.065934 | -0.22258 | -0.12471 | -0.014611 | -0.044537 | 0.17805 | 0.011844 | -0.13605 | 123.0258 | 122.8753 | 123.0038 | 66.8166 | -123.1287 | 122.9451 | 123.0816 | 122.9337 | 66.8156 | -123.2923
225.7969 | 123.4314 | -66.7648 | 56.2958 | 0.0046549 | -0.0015898 | 0.0013163 | 0.054791 | -0.0022456 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.0091474 | 0.061299 | -66.8159 | 0.0243 | -66.7597 | 56.2335 | 56.083 | 56.2161 | -66.8467 | -66.8069 | 0.03241 | -66.846 | 56.1528 | 56.2847 | 56.1368 | -67.0149 | -0.08184 | -0.062251 | -0.051113 | 0.005092 | 0.086932 | -0.21275 | -0.079665 | -0.25005 | -0.14302 | -0.042076 | -0.08116 | 0.16889 | -0.011045 | -0.15894 | 122.9984 | 122.8479 | 122.9809 | 66.7891 | -123.1424 | 122.9176 | 123.0496 | 122.9017 | 66.7972 | -123.3107
226.7969 | 123.2529 | -66.8243 | 56.3324 | -0.0029761 | -0.0015898 | 0.0013163 | 0.055004 | -0.002032 | 0.063785 | 0.015414 | -0.00091653 | -0.00076913 | 0.061449 | 0.0089336 | 0.061513 | -66.8114 | 0.028878 | -66.7597 | 56.2335 | 56.1013 | 56.2161 | -66.8558 | -66.8069 | 0.03241 | -66.8368 | 56.1573 | 56.2802 | 56.1552 | -67.0103 | -0.031489 | -0.098872 | 0.012974 | 0.064601 | 0.09609 | -0.23105 | -0.11629 | -0.18596 | -0.17506 | 0.017433 | -0.012493 | 0.17347 | -0.052244 | -0.17724 | 123.0579 | 122.9257 | 123.0405 | 66.8532 | -123.1882 | 122.9817 | 123.1045 | 122.9795 | 66.8568 | -123.3427
227.7969 | 123.349 | -66.7877 | 56.282 | 0.0046549 | -0.0018034 | 0.0013163 | 0.055004 | -0.0022456 | 0.063999 | 0.015414 | -0.00048933 | -0.00098273 | 0.061236 | 0.0091474 | 0.061299 | -66.8068 | 0.028878 | -66.7506 | 56.2427 | 56.0876 | 56.2161 | -66.8467 | -66.8069 | 0.023253 | -66.846 | 56.1573 | 56.2939 | 56.1414 | -67.0103 | -0.058952 | -0.039361 | -0.019068 | 0.037137 | 0.096089 | -0.19444 | -0.065932 | -0.22258 | -0.1247 | -0.019188 | -0.058272 | 0.16431 | 0.011846 | -0.14062 | 123.0304 | 122.8753 | 123.0038 | 66.8166 | -123.1287 | 122.9451 | 123.0816 | 122.9291 | 66.811 | -123.2923
228.7969 | 123.2574 | -66.8152 | 56.3278 | 0.012286 | -0.0018034 | 0.0013163 | 0.054791 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061236 | 0.009361 | 0.061299 | -66.8114 | 0.028878 | -66.7552 | 56.2381 | 56.0922 | 56.2207 | -66.8513 | -66.8023 | 0.023253 | -66.846 | 56.1482 | 56.2847 | 56.146 | -67.0103 | -0.036065 | -0.089716 | 0.003819 | 0.060025 | 0.09609 | -0.23564 | -0.10713 | -0.19512 | -0.17964 | 0.012857 | -0.030806 | 0.16431 | -0.043089 | -0.18182 | 123.0533 | 122.9074 | 123.0359 | 66.8441 | -123.1791 | 122.9634 | 123.0999 | 122.9612 | 66.8384 | -123.3381
229.7969 | 123.2758 | -66.7877 | 56.337 | -0.0029761 | -0.0015898 | 0.0015299 | 0.054791 | -0.0022456 | 0.063571 | 0.0077831 | -0.00027553 | -0.00076913 | 0.061449 | 0.00872 | 0.061513 | -66.8068 | 0.033457 | -66.7552 | 56.2427 | 56.0968 | 56.2253 | -66.8558 | -66.8069 | 0.027831 | -66.846 | 56.1573 | 56.2847 | 56.1689 | -67.0103 | -0.06811 | -0.094293 | -0.019068 | 0.032559 | 0.10067 | -0.24021 | -0.11171 | -0.22258 | -0.17964 | -0.019188 | -0.058272 | 0.16431 | -0.052244 | -0.16809 | 123.0304 | 122.8845 | 123.013 | 66.8212 | -123.1928 | 122.9451 | 123.0725 | 122.9566 | 66.8156 | -123.3473
230.875 | 123.2986 | -66.774 | 56.2912 | 0.0046549 | -0.0015898 | 0.0013163 | 0.054577 | -0.002032 | 0.063785 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061022 | 0.0091474 | 0.061299 | -66.8114 | 0.0243 | -66.7552 | 56.2335 | 56.1013 | 56.2207 | -66.8467 | -66.8023 | 0.023253 | -66.8414 | 56.1573 | 56.2847 | 56.1323 | -67.0103 | -0.072685 | -0.057674 | -0.03738 | 0.018826 | 0.091511 | -0.18986 | -0.070509 | -0.23631 | -0.13386 | -0.028342 | -0.067426 | 0.16889 | -0.006468 | -0.15894 | 123.0075 | 122.8753 | 122.9947 | 66.7983 | -123.1379 | 122.9313 | 123.0587 | 122.9062 | 66.7972 | -123.3015
231.7969 | 123.2758 | -66.7877 | 56.3004 | -0.0029761 | -0.0015898 | 0.0013163 | 0.054577 | -0.0022456 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061236 | 0.0091474 | 0.061513 | -66.8114 | 0.038035 | -66.7506 | 56.2427 | 56.0968 | 56.2253 | -66.8513 | -66.7977 | 0.027831 | -66.846 | 56.1528 | 56.2893 | 56.1414 | -67.0149 | -0.063531 | -0.057672 | -0.023647 | 0.037137 | 0.10067 | -0.20359 | -0.075086 | -0.22716 | -0.14759 | -0.01003 | -0.058272 | 0.16889 | -0.011044 | -0.15894 | 123.0304 | 122.8845 | 123.013 | 66.8258 | -123.1516 | 122.9405 | 123.077 | 122.9291 | 66.8156 | -123.3152
232.8594 | 123.2391 | -66.806 | 56.3324 | 0.012286 | -0.0018034 | 0.0015299 | 0.054577 | -0.0022456 | 0.063999 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061236 | 0.0091474 | 0.061726 | -66.8022 | 0.019721 | -66.7643 | 56.2381 | 56.1013 | 56.2253 | -66.8558 | -66.8069 | 0.03241 | -66.846 | 56.1482 | 56.2847 | 56.146 | -67.0103 | -0.0498 | -0.094293 | 0.00382 | 0.041712 | 0.091512 | -0.23105 | -0.10713 | -0.20427 | -0.18422 | -0.000878 | -0.039962 | 0.16431 | -0.047666 | -0.1864 | 123.0441 | 122.9074 | 123.0313 | 66.8258 | -123.1882 | 122.9542 | 123.0908 | 122.952 | 66.8384 | -123.3427
233.7969 | 123.3353 | -66.7557 | 56.2775 | -0.010607 | -0.0018034 | 0.0015299 | 0.054791 | -0.0024592 | 0.063144 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061022 | 0.009361 | 0.061299 | -66.8114 | 0.033457 | -66.7597 | 56.2381 | 56.0922 | 56.2298 | -66.8421 | -66.8115 | 0.027831 | -66.846 | 56.1573 | 56.2847 | 56.1414 | -67.0103 | -0.086417 | -0.039362 | -0.055691 | -0.004064 | 0.082353 | -0.18528 | -0.047619 | -0.25463 | -0.12013 | -0.055811 | -0.090316 | 0.16431 | 0.007265 | -0.13605 | 122.9938 | 122.8479 | 122.9855 | 66.7891 | -123.1196 | 122.913 | 123.0404 | 122.8971 | 66.7835 | -123.2878
234.7969 | 123.3582 | -66.7969 | 56.2592 | -0.0029761 | -0.0018034 | 0.0013163 | 0.054791 | -0.0022456 | 0.063785 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061449 | 0.0089336 | 0.061513 | -66.8114 | 0.0243 | -66.7552 | 56.2381 | 56.0784 | 56.2207 | -66.8513 | -66.8069 | 0.027831 | -66.846 | 56.1528 | 56.2893 | 56.1368 | -67.0057 | -0.054376 | -0.021051 | -0.014492 | 0.041714 | 0.09609 | -0.18071 | -0.038465 | -0.20885 | -0.10639 | -0.010033 | -0.049117 | 0.15973 | 0.030155 | -0.12232 | 123.035 | 122.8753 | 123.0176 | 66.8212 | -123.1104 | 122.9496 | 123.0862 | 122.9337 | 66.8247 | -123.2649
235.8594 | 123.317 | -66.7419 | 56.3004 | 0.0046549 | -0.001376 | 0.0011025 | 0.055218 | -0.002032 | 0.063358 | 0.015414 | -0.00048933 | -0.00076913 | 0.061022 | 0.0091474 | 0.060872 | -66.8159 | 0.028878 | -66.7552 | 56.2335 | 56.0876 | 56.2253 | -66.8513 | -66.8023 | 0.023253 | -66.8414 | 56.1528 | 56.2939 | 56.1368 | -67.0011 | -0.10931 | -0.066829 | -0.074002 | -0.013218 | 0.09609 | -0.21275 | -0.075086 | -0.2592 | -0.14759 | -0.060386 | -0.09947 | 0.15973 | -0.006465 | -0.16351 | 122.9755 | 122.8295 | 122.9672 | 66.7708 | -123.1516 | 122.8947 | 123.0358 | 122.8788 | 66.7652 | -123.3015
236.7969 | 123.3856 | -66.7511 | 56.3004 | 0.012286 | -0.0018034 | 0.0013163 | 0.054791 | -0.0022456 | 0.063358 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.0091474 | 0.061086 | -66.8114 | 0.015142 | -66.7597 | 56.2381 | 56.0968 | 56.2207 | -66.8513 | -66.8069 | 0.027831 | -66.8414 | 56.1528 | 56.2847 | 56.146 | -67.0057 | -0.10015 | -0.06225 | -0.060268 | -0.008641 | 0.091511 | -0.20359 | -0.079664 | -0.25462 | -0.14759 | -0.055809 | -0.090314 | 0.16431 | -0.015623 | -0.15436 | 122.9892 | 122.8479 | 122.9718 | 66.7662 | -123.1516 | 122.9039 | 123.0358 | 122.8971 | 66.7789 | -123.3061
237.8594 | 123.3536 | -66.7923 | 56.2866 | -0.010607 | -0.0018034 | 0.0011025 | 0.054577 | -0.0024592 | 0.063571 | 0.0077831 | -0.00070293 | -0.0011965 | 0.061022 | 0.0091474 | 0.061299 | -66.8114 | 0.028878 | -66.7597 | 56.2335 | 56.0922 | 56.2207 | -66.8513 | -66.8023 | 0.018674 | -66.8414 | 56.1482 | 56.2893 | 56.1323 | -67.0149 | -0.058954 | -0.053096 | -0.01907 | 0.032557 | 0.091511 | -0.19444 | -0.065931 | -0.22258 | -0.13844 | -0.010032 | -0.049116 | 0.17347 | 0.002689 | -0.15436 | 123.0258 | 122.8845 | 123.013 | 66.8212 | -123.1379 | 122.9405 | 123.0816 | 122.9246 | 66.811 | -123.3015
238.7969 | 123.3307 | -66.7603 | 56.3004 | -0.0029761 | -0.002017 | 0.0011025 | 0.054791 | -0.0022456 | 0.063571 | 0.00015261 | -0.00048933 | -0.0011965 | 0.061022 | 0.009361 | 0.061299 | -66.8114 | 0.028878 | -66.7552 | 56.2335 | 56.0922 | 56.2253 | -66.8421 | -66.8023 | 0.023253 | -66.8414 | 56.1573 | 56.2985 | 56.146 | -67.0195 | -0.081839 | -0.066829 | -0.051113 | 0.005093 | 0.086932 | -0.20817 | -0.075086 | -0.2592 | -0.14301 | -0.042075 | -0.081159 | 0.17805 | -0.001887 | -0.15436 | 122.9938 | 122.8524 | 122.9855 | 66.7891 | -123.1424 | 122.9176 | 123.0587 | 122.9062 | 66.7835 | -123.3198
239.875 | 123.3673 | -66.7465 | 56.2775 | 0.0046549 | -0.002017 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061022 | 0.0089336 | 0.061299 | -66.8068 | 0.028878 | -66.7643 | 56.2335 | 56.083 | 56.2115 | -66.8421 | -66.8069 | 0.023253 | -66.8368 | 56.1482 | 56.2847 | 56.1414 | -67.0057 | -0.095572 | -0.043941 | -0.060267 | -0.017797 | 0.077775 | -0.19444 | -0.065934 | -0.2592 | -0.12928 | -0.060387 | -0.090313 | 0.16889 | 0.007265 | -0.13605 | 122.98 | 122.8295 | 122.9581 | 66.7754 | -123.1196 | 122.8947 | 123.0313 | 122.8879 | 66.7698 | -123.2832
240.7969 | 123.3215 | -66.7831 | 56.2912 | -0.018238 | -0.002017 | 0.0011025 | 0.055004 | -0.0022456 | 0.063785 | 0.00015261 | -0.00091653 | -0.00076913 | 0.061236 | 0.0095746 | 0.061513 | -66.8068 | 0.028878 | -66.7552 | 56.2381 | 56.1013 | 56.2207 | -66.8421 | -66.7977 | 0.027831 | -66.8506 | 56.1573 | 56.2847 | 56.1414 | -67.0149 | -0.058951 | -0.053095 | -0.023646 | 0.027981 | 0.086932 | -0.18986 | -0.070509 | -0.23174 | -0.13386 | -0.014608 | -0.067428 | 0.16431 | -0.006468 | -0.14978 | 123.0212 | 122.8845 | 123.0038 | 66.812 | -123.1333 | 122.9405 | 123.0679 | 122.9246 | 66.811 | -123.3061
241.8594 | 123.2895 | -66.7831 | 56.3004 | -0.010607 | -0.0022308 | 0.0013163 | 0.055004 | -0.0022456 | 0.063785 | -0.0074779 | -0.00070293 | -0.0011965 | 0.061022 | 0.0095746 | 0.061513 | -66.8068 | 0.028878 | -66.7597 | 56.2335 | 56.0922 | 56.2161 | -66.8513 | -66.8069 | 0.018674 | -66.8414 | 56.1528 | 56.2939 | 56.1414 | -67.0195 | -0.068109 | -0.066829 | -0.023646 | 0.023402 | 0.091511 | -0.20817 | -0.084243 | -0.23632 | -0.14759 | -0.023766 | -0.058271 | 0.17805 | -0.006465 | -0.15894 | 123.0167 | 122.8753 | 122.9993 | 66.812 | -123.1516 | 122.9359 | 123.077 | 122.9246 | 66.8018 | -123.3198
242.7969 | 123.2391 | -66.7969 | 56.3599 | 0.0046549 | -0.002017 | 0.0013163 | 0.054791 | -0.0022456 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061236 | 0.0095746 | 0.061086 | -66.8022 | 0.0243 | -66.7552 | 56.2381 | 56.083 | 56.2253 | -66.8513 | -66.8023 | 0.03241 | -66.8368 | 56.1573 | 56.2939 | 56.1414 | -67.0057 | -0.054376 | -0.12176 | -0.005335 | 0.041714 | 0.09609 | -0.27684 | -0.13459 | -0.20885 | -0.20252 | -0.005454 | -0.039959 | 0.16889 | -0.065974 | -0.21844 | 123.035 | 122.8799 | 123.0221 | 66.8212 | -123.2111 | 122.9542 | 123.0908 | 122.9383 | 66.8293 | -123.3656
243.8594 | 123.349 | -66.7831 | 56.2683 | -0.010607 | -0.0022308 | 0.0015299 | 0.054791 | -0.0022456 | 0.063358 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060808 | 0.009361 | 0.061299 | -66.8068 | 0.033457 | -66.7552 | 56.2427 | 56.0968 | 56.2207 | -66.8513 | -66.8023 | 0.027831 | -66.8368 | 56.1528 | 56.2802 | 56.1277 | -67.0103 | -0.068109 | -0.025629 | -0.023646 | 0.027981 | 0.09609 | -0.17155 | -0.047621 | -0.22716 | -0.11555 | -0.019187 | -0.053692 | 0.17347 | 0.011842 | -0.14063 | 123.0258 | 122.8799 | 123.0038 | 66.8166 | -123.1196 | 122.9359 | 123.0633 | 122.9108 | 66.811 | -123.2786
244.7969 | 123.3627 | -66.774 | 56.3095 | 0.012286 | -0.0015898 | 0.00088894 | 0.055218 | -0.0022456 | 0.063358 | 0.0077831 | -0.00048933 | -0.00076913 | 0.061236 | 0.009361 | 0.061299 | -66.8114 | 0.0243 | -66.7506 | 56.2335 | 56.0922 | 56.2161 | -66.8329 | -66.7977 | 0.023253 | -66.8414 | 56.1482 | 56.2939 | 56.1414 | -67.0149 | -0.058948 | -0.075984 | -0.03738 | 0.023404 | 0.082352 | -0.21732 | -0.093398 | -0.24089 | -0.16133 | -0.023763 | -0.067426 | 0.17347 | -0.01562 | -0.16809 | 123.0075 | 122.8662 | 122.9901 | 66.7983 | -123.1424 | 122.9222 | 123.0679 | 122.9154 | 66.7972 | -123.3244
245.7969 | 123.3353 | -66.7648 | 56.2958 | 0.0046549 | -0.0018034 | 0.0013163 | 0.054791 | -0.0022456 | 0.063358 | -0.0074779 | -0.00070293 | -0.00098273 | 0.061236 | 0.0095746 | 0.061726 | -66.8022 | 0.0243 | -66.7597 | 56.2427 | 56.0922 | 56.2207 | -66.8467 | -66.8069 | 0.023253 | -66.8414 | 56.1573 | 56.2893 | 56.1277 | -67.0103 | -0.08184 | -0.053094 | -0.037378 | 0.005092 | 0.086932 | -0.20359 | -0.075086 | -0.24547 | -0.13844 | -0.042076 | -0.076581 | 0.16889 | -0.006466 | -0.16809 | 123.0075 | 122.857 | 122.9855 | 66.7891 | -123.1424 | 122.9222 | 123.0541 | 122.8925 | 66.7881 | -123.3061
246.7969 | 123.3536 | -66.7557 | 56.3141 | -0.0029761 | -0.0024444 | 0.0013163 | 0.055218 | -0.002032 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061236 | 0.0089336 | 0.061513 | -66.8068 | 0.0243 | -66.7597 | 56.2289 | 56.0922 | 56.2161 | -66.8467 | -66.8023 | 0.027831 | -66.8414 | 56.1528 | 56.2893 | 56.1323 | -67.0195 | -0.090996 | -0.08514 | -0.051112 | -0.004064 | 0.086932 | -0.2219 | -0.097976 | -0.26378 | -0.16133 | -0.046653 | -0.085737 | 0.17805 | -0.024777 | -0.18183 | 122.9846 | 122.8479 | 122.9718 | 66.78 | -123.1608 | 122.9084 | 123.045 | 122.8879 | 66.7835 | -123.3335
247.7969 | 123.3078 | -66.7969 | 56.3141 | 0.012286 | -0.0015898 | 0.0013163 | 0.055004 | -0.002032 | 0.063144 | 0.00015261 | -0.00048933 | -0.00055553 | 0.061236 | 0.009361 | 0.061086 | -66.8114 | 0.019721 | -66.7597 | 56.2381 | 56.0784 | 56.2298 | -66.8421 | -66.7977 | 0.014095 | -66.846 | 56.1482 | 56.2802 | 56.1323 | -67.0149 | -0.045218 | -0.075983 | -0.014492 | 0.037135 | 0.082353 | -0.23564 | -0.08424 | -0.21801 | -0.16591 | -0.000875 | -0.049117 | 0.16889 | -0.033934 | -0.18183 | 123.035 | 122.8753 | 123.0267 | 66.8166 | -123.1562 | 122.9451 | 123.077 | 122.9291 | 66.811 | -123.329
248.7969 | 123.2849 | -66.806 | 56.3461 | -0.0029761 | -0.002017 | 0.0011025 | 0.055004 | -0.002032 | 0.063144 | 0.00015261 | -0.00091653 | -0.00076913 | 0.061236 | 0.0097884 | 0.061086 | -66.8114 | 0.038035 | -66.7643 | 56.2427 | 56.083 | 56.2161 | -66.8467 | -66.8023 | 0.027831 | -66.846 | 56.1482 | 56.2939 | 56.1323 | -67.0103 | -0.040642 | -0.10345 | -0.005337 | 0.041712 | 0.082354 | -0.2631 | -0.13002 | -0.20427 | -0.19795 | 0.003701 | -0.039962 | 0.16431 | -0.052241 | -0.21387 | 123.0487 | 122.8891 | 123.0221 | 66.8441 | -123.1928 | 122.9542 | 123.0999 | 122.9383 | 66.8339 | -123.3564
249.7969 | 123.3673 | -66.7648 | 56.2775 | 0.0046549 | -0.002017 | 0.0013163 | 0.054791 | -0.0022456 | 0.063358 | 0.015414 | -0.00048933 | -0.00076913 | 0.061022 | 0.0091474 | 0.061513 | -66.8159 | 0.0243 | -66.7506 | 56.2335 | 56.0922 | 56.2207 | -66.8421 | -66.7932 | 0.018674 | -66.8414 | 56.1528 | 56.2847 | 56.1323 | -67.0149 | -0.077261 | -0.043941 | -0.051113 | 0.014249 | 0.09151 | -0.18528 | -0.056776 | -0.25005 | -0.12471 | -0.02834 | -0.076581 | 0.17347 | 0.007265 | -0.14521 | 122.9984 | 122.857 | 122.9855 | 66.7891 | -123.1196 | 122.9176 | 123.0496 | 122.8971 | 66.7835 | -123.2923
250.8594 | 123.2483 | -66.7969 | 56.3187 | 0.0046549 | -0.0018034 | 0.00088894 | 0.055004 | -0.0022456 | 0.063358 | 0.00015261 | -6.1934e-05 | -0.00076913 | 0.061022 | 0.0097884 | 0.061299 | -66.8068 | 0.033457 | -66.7506 | 56.2427 | 56.0876 | 56.2207 | -66.8558 | -66.7977 | 0.027831 | -66.846 | 56.1482 | 56.2847 | 56.1368 | -67.0103 | -0.058955 | -0.075983 | -0.009913 | 0.046292 | 0.10525 | -0.23106 | -0.097975 | -0.21343 | -0.17048 | -0.000875 | -0.049117 | 0.16431 | -0.033934 | -0.18183 | 123.0396 | 122.8845 | 123.0176 | 66.8303 | -123.1745 | 122.9451 | 123.0816 | 122.9337 | 66.8247 | -123.329
251.7969 | 123.3307 | -66.7786 | 56.3095 | -0.018238 | -0.002017 | 0.0013163 | 0.054791 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00076913 | 0.060808 | 0.009361 | 0.061513 | -66.8022 | 0.0243 | -66.7552 | 56.2289 | 56.083 | 56.2161 | -66.8513 | -66.8023 | 0.023253 | -66.8414 | 56.1528 | 56.2893 | 56.1414 | -67.0149 | -0.072687 | -0.080562 | -0.023646 | 0.023403 | 0.09609 | -0.22648 | -0.093398 | -0.23632 | -0.15675 | -0.023765 | -0.062849 | 0.17347 | -0.020199 | -0.16809 | 123.0075 | 122.8616 | 122.9947 | 66.8029 | -123.1608 | 122.9313 | 123.0679 | 122.92 | 66.8018 | -123.3244
252.8594 | 123.3261 | -66.7694 | 56.3049 | 0.0046549 | -0.0018034 | 0.0011025 | 0.055004 | -0.0022456 | 0.063785 | 0.0077831 | -0.00091653 | -0.0011965 | 0.061449 | 0.009361 | 0.061086 | -66.8068 | 0.033457 | -66.7597 | 56.2381 | 56.0876 | 56.2253 | -66.8558 | -66.8023 | 0.027831 | -66.8277 | 56.1573 | 56.2847 | 56.1506 | -67.0149 | -0.086421 | -0.066828 | -0.037379 | 0.009669 | 0.09609 | -0.21733 | -0.079664 | -0.24547 | -0.14759 | -0.03292 | -0.058268 | 0.1872 | -0.020201 | -0.15436 | 123.0075 | 122.857 | 122.9947 | 66.8029 | -123.1608 | 122.9267 | 123.0541 | 122.92 | 66.7972 | -123.3198
253.7969 | 123.3719 | -66.7694 | 56.2683 | -0.010607 | -0.002017 | 0.00088894 | 0.055004 | -0.002032 | 0.063571 | 0.0077831 | -0.00091653 | -0.00055553 | 0.061022 | 0.0091474 | 0.061299 | -66.8068 | 0.033457 | -66.7506 | 56.2381 | 56.0739 | 56.2207 | -66.8467 | -66.7977 | 0.027831 | -66.8414 | 56.1573 | 56.2847 | 56.1231 | -67.0149 | -0.077263 | -0.030207 | -0.037379 | 0.018826 | 0.096089 | -0.19444 | -0.047621 | -0.24547 | -0.11097 | -0.028341 | -0.072004 | 0.17347 | 0.01642 | -0.14521 | 123.0075 | 122.8433 | 122.9901 | 66.8029 | -123.115 | 122.9267 | 123.0541 | 122.8925 | 66.7972 | -123.2832
254.7969 | 123.2529 | -66.7969 | 56.3416 | -0.010607 | -0.0022308 | 0.0013163 | 0.054363 | -0.0022456 | 0.063571 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061449 | 0.0097884 | 0.061086 | -66.8114 | 0.038035 | -66.7643 | 56.2427 | 56.0922 | 56.2207 | -66.8513 | -66.8023 | 0.027831 | -66.8414 | 56.1573 | 56.2893 | 56.146 | -67.0103 | -0.054376 | -0.098871 | -0.014492 | 0.032557 | 0.086933 | -0.24937 | -0.12086 | -0.21343 | -0.18421 | -0.005454 | -0.044538 | 0.16889 | -0.052243 | -0.19556 | 123.0396 | 122.8891 | 123.0176 | 66.8349 | -123.1928 | 122.9542 | 123.0862 | 122.9429 | 66.8247 | -123.3519
255.7969 | 123.3032 | -66.7831 | 56.3004 | -0.0029761 | -0.0022308 | 0.0013163 | 0.054577 | -0.0022456 | 0.063571 | -0.0074779 | -0.00048933 | -0.0011965 | 0.061022 | 0.0095746 | 0.061513 | -66.8068 | 0.0243 | -66.7643 | 56.2381 | 56.0922 | 56.2253 | -66.8467 | -66.8023 | 0.023253 | -66.8368 | 56.1528 | 56.2847 | 56.1277 | -67.0149 | -0.06353 | -0.06225 | -0.023646 | 0.018824 | 0.082354 | -0.20817 | -0.075086 | -0.23174 | -0.14759 | -0.019187 | -0.053692 | 0.17805 | -0.015623 | -0.17267 | 123.0212 | 122.8753 | 123.0084 | 66.8074 | -123.147 | 122.9359 | 123.0679 | 122.9108 | 66.8064 | -123.3152
256.7969 | 123.2391 | -66.7969 | 56.3461 | -0.010607 | -0.002017 | 0.0013163 | 0.054791 | -0.0024592 | 0.063785 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061022 | 0.0097884 | 0.061513 | -66.8068 | 0.038035 | -66.7643 | 56.2381 | 56.0968 | 56.2298 | -66.8513 | -66.8069 | 0.023253 | -66.846 | 56.1573 | 56.2939 | 56.1368 | -67.0149 | -0.054376 | -0.10803 | -0.009913 | 0.032557 | 0.086933 | -0.24937 | -0.11628 | -0.21801 | -0.18879 | -0.010033 | -0.049117 | 0.16889 | -0.052241 | -0.20929 | 123.035 | 122.8936 | 123.0267 | 66.8349 | -123.1974 | 122.9542 | 123.0908 | 122.9337 | 66.8201 | -123.361
257.8594 | 123.3627 | -66.7923 | 56.2729 | -0.010607 | -0.0018034 | 0.0011025 | 0.054577 | -0.0022456 | 0.063785 | 0.00015261 | -0.00048933 | -0.00055553 | 0.060808 | 0.0097884 | 0.061299 | -66.8068 | 0.028878 | -66.7552 | 56.2381 | 56.0968 | 56.2207 | -66.8558 | -66.8069 | 0.03241 | -66.8414 | 56.1573 | 56.2847 | 56.1506 | -67.0057 | -0.063533 | -0.034784 | -0.014491 | 0.037136 | 0.10067 | -0.17612 | -0.052198 | -0.21343 | -0.11555 | -0.014611 | -0.049116 | 0.16431 | 0.011843 | -0.12231 | 123.0304 | 122.8891 | 123.013 | 66.8212 | -123.1287 | 122.9496 | 123.077 | 122.9429 | 66.8247 | -123.2786
258.7969 | 123.3673 | -66.7328 | 56.3004 | -0.0029761 | -0.002017 | 0.0011025 | 0.055004 | -0.002032 | 0.063785 | 0.0077831 | -0.00091653 | -0.00098273 | 0.061022 | 0.0097884 | 0.061299 | -66.8114 | 0.019721 | -66.7643 | 56.2289 | 56.083 | 56.2161 | -66.8467 | -66.8115 | 0.023253 | -66.8368 | 56.1482 | 56.2985 | 56.1414 | -67.0057 | -0.11388 | -0.071407 | -0.078579 | -0.03153 | 0.082354 | -0.21733 | -0.084243 | -0.27293 | -0.15217 | -0.078699 | -0.10405 | 0.16889 | -0.001887 | -0.15894 | 122.9617 | 122.8158 | 122.9489 | 66.7525 | -123.147 | 122.881 | 123.0313 | 122.8742 | 66.756 | -123.3061
259.8906 | 123.2483 | -66.806 | 56.3507 | -0.0029761 | -0.0022308 | 0.0015299 | 0.055004 | -0.002673 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061022 | 0.009361 | 0.061513 | -66.8022 | 0.033457 | -66.7552 | 56.2427 | 56.083 | 56.2298 | -66.8375 | -66.7977 | 0.027831 | -66.8368 | 56.1528 | 56.2893 | 56.146 | -67.0103 | -0.031484 | -0.10803 | 0.00382 | 0.050869 | 0.082353 | -0.26768 | -0.12086 | -0.20427 | -0.19795 | 0.00828 | -0.030804 | 0.17347 | -0.061398 | -0.20471 | 123.0487 | 122.8891 | 123.0359 | 66.8395 | -123.1882 | 122.9588 | 123.0953 | 122.952 | 66.8339 | -123.361
260.7969 | 123.3307 | -66.7648 | 56.3049 | -0.0029761 | -0.0018034 | 0.0013163 | 0.054791 | -0.002032 | 0.063358 | 0.015414 | -0.00048933 | -0.00098273 | 0.061236 | 0.0097884 | 0.061513 | -66.8068 | 0.0243 | -66.7414 | 56.2381 | 56.0876 | 56.2207 | -66.8421 | -66.7977 | 0.023253 | -66.8368 | 56.1528 | 56.2847 | 56.1368 | -67.0103 | -0.077261 | -0.066828 | -0.041956 | 0.023405 | 0.10067 | -0.21733 | -0.084242 | -0.24547 | -0.15217 | -0.032918 | -0.072002 | 0.17347 | -0.020201 | -0.16809 | 123.0029 | 122.8524 | 122.9855 | 66.7891 | -123.147 | 122.9176 | 123.0496 | 122.9017 | 66.7881 | -123.3152
261.7969 | 123.317 | -66.7786 | 56.3049 | -0.0029761 | -0.002017 | 0.0011025 | 0.054791 | -0.0022456 | 0.063358 | 0.00015261 | -0.00048933 | -0.0014101 | 0.061236 | 0.009361 | 0.061086 | -66.8022 | 0.028878 | -66.7506 | 56.2381 | 56.0922 | 56.2253 | -66.8421 | -66.7977 | 0.027831 | -66.8368 | 56.1528 | 56.2893 | 56.1323 | -67.0103 | -0.063529 | -0.066828 | -0.023646 | 0.027981 | 0.09151 | -0.21275 | -0.079664 | -0.23174 | -0.15217 | -0.019186 | -0.05827 | 0.17347 | -0.015622 | -0.17267 | 123.0167 | 122.8707 | 123.0038 | 66.8074 | -123.147 | 122.9313 | 123.0679 | 122.9108 | 66.8064 | -123.3152
262.875 | 123.262 | -66.7877 | 56.3141 | -0.0029761 | -0.002017 | 0.0013163 | 0.054791 | -0.0024592 | 0.063358 | 0.0077831 | -0.00091653 | -0.0011965 | 0.061236 | 0.0095746 | 0.061299 | -66.8068 | 0.033457 | -66.7506 | 56.2473 | 56.1013 | 56.2161 | -66.8284 | -66.7932 | 0.03241 | -66.8414 | 56.1482 | 56.2847 | 56.146 | -67.0149 | -0.040636 | -0.066827 | -0.019068 | 0.037137 | 0.077773 | -0.21274 | -0.097976 | -0.22716 | -0.16591 | -0.005452 | -0.053693 | 0.17347 | -0.029356 | -0.16809 | 123.035 | 122.8891 | 123.0038 | 66.8212 | -123.1424 | 122.9359 | 123.0725 | 122.9337 | 66.8201 | -123.329
263.7969 | 123.3398 | -66.7557 | 56.3049 | -0.010607 | -0.002017 | 0.0011025 | 0.054577 | -0.002032 | 0.063571 | 0.00015261 | -0.00048933 | -0.00076913 | 0.061022 | 0.0095746 | 0.061299 | -66.8068 | 0.028878 | -66.7552 | 56.2244 | 56.0922 | 56.2207 | -66.8558 | -66.7977 | 0.027831 | -66.8368 | 56.1482 | 56.2939 | 56.1368 | -67.0103 | -0.10015 | -0.080564 | -0.051112 | 0.000515 | 0.10067 | -0.21275 | -0.084242 | -0.25463 | -0.15675 | -0.042074 | -0.081158 | 0.17347 | -0.011043 | -0.16809 | 122.98 | 122.8479 | 122.9764 | 66.7846 | -123.1608 | 122.9039 | 123.0496 | 122.8925 | 66.7835 | -123.3152
264.8594 | 123.2483 | -66.774 | 56.369 | 0.012286 | -0.0024444 | 0.0013163 | 0.054791 | -0.002673 | 0.063358 | 0.015414 | -0.00070293 | -0.0014101 | 0.061449 | 0.0097884 | 0.061299 | -66.8022 | 0.028878 | -66.7597 | 56.2381 | 56.0968 | 56.2298 | -66.8513 | -66.8023 | 0.027831 | -66.8368 | 56.1528 | 56.2847 | 56.1414 | -67.0103 | -0.077264 | -0.13092 | -0.028223 | 0.014247 | 0.091511 | -0.27226 | -0.13917 | -0.23631 | -0.21626 | -0.028342 | -0.062847 | 0.17347 | -0.084288 | -0.2276 | 123.0121 | 122.8708 | 123.0038 | 66.8029 | -123.2203 | 122.9267 | 123.0587 | 122.9154 | 66.8018 | -123.3793
265.7969 | 123.2483 | -66.774 | 56.3416 | 0.0046549 | -0.0022308 | 0.0015299 | 0.054791 | -0.0024592 | 0.063358 | 0.00015261 | -0.00091653 | -0.00076913 | 0.061022 | 0.010002 | 0.061299 | -66.8068 | 0.033457 | -66.7414 | 56.2335 | 56.083 | 56.2161 | -66.8421 | -66.7977 | 0.023253 | -66.8368 | 56.1528 | 56.2893 | 56.1506 | -67.0149 | -0.068106 | -0.10803 | -0.032801 | 0.03256 | 0.10067 | -0.25853 | -0.12544 | -0.24089 | -0.18879 | -0.023763 | -0.062847 | 0.17805 | -0.052243 | -0.19098 | 123.0075 | 122.857 | 122.9901 | 66.8074 | -123.1836 | 122.9267 | 123.0633 | 122.9246 | 66.7972 | -123.3564
266.8594 | 123.3215 | -66.8106 | 56.3049 | -0.0029761 | -0.002017 | 0.0011025 | 0.055004 | -0.0022456 | 0.063571 | -0.0074779 | -0.00070293 | -0.0011965 | 0.061022 | 0.010002 | 0.061086 | -66.8114 | 0.028878 | -66.7552 | 56.2427 | 56.0922 | 56.2298 | -66.8558 | -66.8023 | 0.027831 | -66.8368 | 56.1528 | 56.2847 | 56.1368 | -67.0149 | -0.045222 | -0.06225 | -0.000759 | 0.055447 | 0.10067 | -0.21275 | -0.075085 | -0.20427 | -0.15217 | 0.008279 | -0.026226 | 0.17805 | -0.020201 | -0.16809 | 123.0533 | 122.9028 | 123.0405 | 66.8395 | -123.1608 | 122.9634 | 123.0953 | 122.9474 | 66.8384 | -123.3198
267.7969 | 123.3444 | -66.7465 | 56.3049 | -0.010607 | -0.002017 | 0.0011025 | 0.055004 | -0.0022456 | 0.063144 | 0.015414 | -0.00048933 | -0.00098273 | 0.061022 | 0.010002 | 0.061299 | -66.8114 | 0.0243 | -66.7506 | 56.2427 | 56.0968 | 56.2253 | -66.8467 | -66.8023 | 0.027831 | -66.8368 | 56.1482 | 56.2847 | 56.1323 | -67.0103 | -0.10015 | -0.06225 | -0.064846 | -0.004062 | 0.096089 | -0.20817 | -0.079664 | -0.26378 | -0.15675 | -0.055808 | -0.090313 | 0.17347 | -0.020201 | -0.17267 | 122.9892 | 122.8433 | 122.9718 | 66.7708 | -123.1516 | 122.8947 | 123.0313 | 122.8788 | 66.7744 | -123.3152
268.7969 | 123.3673 | -66.7511 | 56.3095 | 0.0046549 | -0.0024444 | 0.0015299 | 0.054791 | -0.0024592 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061236 | 0.010002 | 0.061513 | -66.8022 | 0.028878 | -66.7506 | 56.2473 | 56.0922 | 56.2298 | -66.8513 | -66.7932 | 0.03241 | -66.8323 | 56.1528 | 56.2893 | 56.1552 | -67.0149 | -0.10015 | -0.062249 | -0.051111 | 0.000516 | 0.10067 | -0.21732 | -0.079662 | -0.26378 | -0.15675 | -0.042073 | -0.081157 | 0.18262 | -0.020199 | -0.15436 | 122.9984 | 122.8433 | 122.9809 | 66.78 | -123.1608 | 122.9039 | 123.0404 | 122.9063 | 66.7835 | -123.3244
269.7969 | 123.2666 | -66.7831 | 56.3187 | 0.0046549 | -0.0024444 | 0.0015299 | 0.054577 | -0.002032 | 0.063358 | 0.0077831 | -0.00091653 | -0.0011965 | 0.061236 | 0.0097884 | 0.061513 | -66.8068 | 0.028878 | -66.7506 | 56.2427 | 56.0922 | 56.2207 | -66.8513 | -66.8023 | 0.027831 | -66.8414 | 56.1528 | 56.2847 | 56.146 | -67.0149 | -0.068109 | -0.075983 | -0.023646 | 0.032559 | 0.10067 | -0.22648 | -0.097975 | -0.23174 | -0.16591 | -0.019187 | -0.058271 | 0.17347 | -0.033934 | -0.17267 | 123.0258 | 122.8753 | 123.0038 | 66.812 | -123.1699 | 122.9359 | 123.0679 | 122.9291 | 66.811 | -123.3335
270.875 | 123.1842 | -66.7831 | 56.3278 | 0.0046549 | -0.0022308 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061449 | 0.010002 | 0.061513 | -66.8114 | 0.0243 | -66.7552 | 56.2335 | 56.0876 | 56.2253 | -66.8513 | -66.7886 | 0.027831 | -66.8368 | 56.1528 | 56.2847 | 56.1552 | -67.0195 | -0.068109 | -0.094295 | -0.028225 | 0.027981 | 0.09609 | -0.24021 | -0.10255 | -0.23632 | -0.17506 | -0.005451 | -0.053692 | 0.18263 | -0.043089 | -0.17267 | 123.0167 | 122.8707 | 123.0084 | 66.8074 | -123.1791 | 122.9359 | 123.0679 | 122.9383 | 66.811 | -123.3473
271.7969 | 123.2986 | -66.7786 | 56.3141 | 0.0046549 | -0.0022308 | 0.0011025 | 0.054363 | -0.0024592 | 0.063358 | 0.015414 | -0.00091653 | -0.00098273 | 0.061236 | 0.0097884 | 0.061299 | -66.8068 | 0.028878 | -66.7506 | 56.2427 | 56.1013 | 56.2253 | -66.8558 | -66.7977 | 0.027831 | -66.8414 | 56.1528 | 56.2939 | 56.1414 | -67.0057 | -0.077266 | -0.071405 | -0.028224 | 0.027981 | 0.10525 | -0.21274 | -0.088819 | -0.22716 | -0.16133 | -0.019186 | -0.062849 | 0.16431 | -0.020198 | -0.17267 | 123.0212 | 122.8799 | 123.0038 | 66.8074 | -123.1699 | 122.9313 | 123.0725 | 122.92 | 66.8064 | -123.3198
272.7969 | 123.2254 | -66.8152 | 56.3278 | 0.0046549 | -0.0022308 | 0.00088894 | 0.054791 | -0.0024592 | 0.063571 | -0.0074779 | -0.00070293 | -0.0011965 | 0.061022 | 0.010002 | 0.061513 | -66.8022 | 0.028878 | -66.7552 | 56.2335 | 56.1013 | 56.2253 | -66.8513 | -66.7977 | 0.036989 | -66.8323 | 56.1482 | 56.2802 | 56.1552 | -67.0103 | -0.036065 | -0.094295 | 0.012976 | 0.060025 | 0.09609 | -0.22648 | -0.10255 | -0.19512 | -0.17964 | 0.017436 | -0.01707 | 0.17804 | -0.047667 | -0.17267 | 123.0487 | 122.9165 | 123.0405 | 66.8441 | -123.1791 | 122.9634 | 123.0953 | 122.9703 | 66.8522 | -123.3381
273.8594 | 123.2666 | -66.806 | 56.3095 | -0.010607 | -0.0024444 | 0.0011025 | 0.055004 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060808 | 0.0095746 | 0.061299 | -66.8022 | 0.028878 | -66.746 | 56.2381 | 56.1013 | 56.2253 | -66.8558 | -66.7932 | 0.027831 | -66.8368 | 56.1482 | 56.2893 | 56.1506 | -67.0103 | -0.0498 | -0.071405 | 0.00382 | 0.060025 | 0.10983 | -0.20817 | -0.084241 | -0.20427 | -0.16133 | 0.012858 | -0.030804 | 0.17347 | -0.020199 | -0.15893 | 123.0441 | 122.9074 | 123.0313 | 66.8349 | -123.1653 | 122.9542 | 123.0953 | 122.9566 | 66.8339 | -123.3198
274.7969 | 123.2529 | -66.7648 | 56.337 | -0.0029761 | -0.0018034 | 0.0013163 | 0.054577 | -0.0024592 | 0.063571 | 0.015414 | -0.00091653 | -0.00076913 | 0.061236 | 0.010002 | 0.061726 | -66.8022 | 0.0243 | -66.746 | 56.2381 | 56.0922 | 56.2253 | -66.8558 | -66.7977 | 0.018674 | -66.8414 | 56.1619 | 56.2847 | 56.1414 | -67.0149 | -0.090998 | -0.098871 | -0.037378 | 0.018827 | 0.10983 | -0.24479 | -0.11171 | -0.25005 | -0.17506 | -0.032918 | -0.076581 | 0.17347 | -0.052244 | -0.19556 | 123.0029 | 122.857 | 122.9901 | 66.7891 | -123.1928 | 122.9267 | 123.0496 | 122.9062 | 66.7835 | -123.3519
275.7969 | 123.2483 | -66.7877 | 56.3232 | 0.0046549 | -0.0018034 | 0.0011025 | 0.054363 | -0.002673 | 0.063571 | 0.0077831 | -0.00070293 | -0.0011965 | 0.061236 | 0.010002 | 0.061513 | -66.8114 | 0.033457 | -66.746 | 56.2381 | 56.0922 | 56.2298 | -66.8513 | -66.7977 | 0.023253 | -66.8368 | 56.1573 | 56.2893 | 56.1506 | -67.0103 | -0.063531 | -0.085138 | -0.023647 | 0.041715 | 0.10525 | -0.23106 | -0.093395 | -0.22258 | -0.1659 | -0.01003 | -0.049114 | 0.17347 | -0.033932 | -0.17267 | 123.0258 | 122.8799 | 123.0176 | 66.8212 | -123.1745 | 122.9451 | 123.077 | 122.9383 | 66.811 | -123.3335
276.7969 | 123.3673 | -66.7419 | 56.3004 | -0.010607 | -0.0022308 | 0.0011025 | 0.054791 | -0.0022456 | 0.063571 | 0.0077831 | -0.00070293 | -0.0014101 | 0.061022 | 0.0095746 | 0.061299 | -66.8022 | 0.028878 | -66.746 | 56.2381 | 56.083 | 56.2207 | -66.8513 | -66.7977 | 0.036989 | -66.8368 | 56.1528 | 56.2939 | 56.146 | -67.0149 | -0.10931 | -0.06225 | -0.060267 | -0.004062 | 0.10525 | -0.21733 | -0.079664 | -0.27294 | -0.14759 | -0.055807 | -0.094891 | 0.17805 | -0.006465 | -0.15436 | 122.98 | 122.825 | 122.9626 | 66.7708 | -123.1516 | 122.8947 | 123.0358 | 122.8879 | 66.7789 | -123.3152
277.7969 | 123.2758 | -66.774 | 56.3232 | 0.0046549 | -0.0022308 | 0.0011025 | 0.054791 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061236 | 0.010216 | 0.061086 | -66.8022 | 0.028878 | -66.7506 | 56.2427 | 56.0968 | 56.2161 | -66.8513 | -66.7977 | 0.027831 | -66.8277 | 56.1528 | 56.2847 | 56.1414 | -67.0103 | -0.077264 | -0.08056 | -0.028223 | 0.023404 | 0.10067 | -0.22648 | -0.10713 | -0.23631 | -0.17048 | -0.023763 | -0.05369 | 0.18262 | -0.038511 | -0.18182 | 123.0167 | 122.8708 | 122.9901 | 66.8029 | -123.1745 | 122.9267 | 123.0587 | 122.9154 | 66.8018 | -123.3335
278.8594 | 123.3719 | -66.7328 | 56.3049 | -0.0029761 | -0.0022308 | 0.0013163 | 0.054791 | -0.002673 | 0.063358 | 0.015414 | -0.00091653 | -0.0011965 | 0.061022 | 0.010002 | 0.061299 | -66.8022 | 0.0243 | -66.7506 | 56.2335 | 56.0876 | 56.2253 | -66.8467 | -66.7977 | 0.018674 | -66.8368 | 56.1619 | 56.2893 | 56.1323 | -67.0057 | -0.11388 | -0.071407 | -0.069422 | -0.017795 | 0.096089 | -0.21733 | -0.079664 | -0.27293 | -0.14301 | -0.064962 | -0.10405 | 0.16889 | -0.015622 | -0.17267 | 122.9663 | 122.8204 | 122.9581 | 66.7571 | -123.1516 | 122.8947 | 123.0221 | 122.865 | 66.7515 | -123.3107
279.7969 | 123.2666 | -66.7969 | 56.3736 | 0.0046549 | -0.0024444 | 0.0013163 | 0.054577 | -0.0024592 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061236 | 0.010002 | 0.060872 | -66.8022 | 0.033457 | -66.7368 | 56.2381 | 56.0876 | 56.2298 | -66.8513 | -66.7886 | 0.027831 | -66.8277 | 56.1573 | 56.2893 | 56.146 | -67.0103 | -0.054376 | -0.13549 | -0.005335 | 0.060027 | 0.1144 | -0.28599 | -0.14375 | -0.21343 | -0.21626 | 0.008282 | -0.030802 | 0.18262 | -0.084286 | -0.2276 | 123.035 | 122.8845 | 123.0267 | 66.8303 | -123.2248 | 122.9542 | 123.0862 | 122.9429 | 66.8247 | -123.3839
280.7969 | 123.2712 | -66.8106 | 56.2958 | 0.0046549 | -0.002658 | 0.00088894 | 0.054577 | -0.0022456 | 0.063358 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061022 | 0.010002 | 0.061086 | -66.8022 | 0.028878 | -66.746 | 56.2381 | 56.0968 | 56.2253 | -66.8513 | -66.7977 | 0.027831 | -66.8368 | 56.1482 | 56.2893 | 56.1368 | -67.0057 | -0.040643 | -0.057672 | 0.008398 | 0.064603 | 0.10525 | -0.19901 | -0.070508 | -0.19511 | -0.14759 | 0.012858 | -0.026226 | 0.16889 | -0.006466 | -0.15894 | 123.0487 | 122.9074 | 123.0359 | 66.8395 | -123.147 | 122.9588 | 123.0999 | 122.9474 | 66.8384 | -123.3015
281.7969 | 123.2437 | -66.7877 | 56.3461 | 0.0046549 | -0.0024444 | 0.0011025 | 0.054791 | -0.0022456 | 0.063358 | 0.015414 | -0.00048933 | -0.00098273 | 0.061022 | 0.0097884 | 0.061086 | -66.8068 | 0.0243 | -66.7643 | 56.2427 | 56.1105 | 56.2344 | -66.8558 | -66.7977 | 0.027831 | -66.8414 | 56.1482 | 56.2847 | 56.1368 | -67.0149 | -0.06811 | -0.10345 | -0.019068 | 0.023402 | 0.091512 | -0.23563 | -0.11171 | -0.22716 | -0.19795 | -0.01003 | -0.053693 | 0.17347 | -0.061399 | -0.20929 | 123.0304 | 122.8982 | 123.0221 | 66.812 | -123.202 | 122.9359 | 123.0725 | 122.9246 | 66.8156 | -123.361
282.8594 | 123.317 | -66.7694 | 56.3324 | 0.012286 | -0.0024444 | 0.0013163 | 0.054791 | -0.002032 | 0.063785 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060808 | 0.0097884 | 0.061299 | -66.8022 | 0.033457 | -66.7368 | 56.2289 | 56.1013 | 56.2298 | -66.8467 | -66.8023 | 0.018674 | -66.8368 | 56.1573 | 56.2893 | 56.1597 | -67.0149 | -0.077263 | -0.10345 | -0.032801 | 0.032561 | 0.10982 | -0.23105 | -0.10255 | -0.24547 | -0.17506 | -0.03292 | -0.067425 | 0.17805 | -0.043087 | -0.17267 | 122.9984 | 122.8708 | 122.9993 | 66.8029 | -123.1791 | 122.9267 | 123.0587 | 122.9291 | 66.7881 | -123.3473
283.7969 | 123.23 | -66.7786 | 56.337 | 0.0046549 | -0.0024444 | 0.00088894 | 0.054577 | -0.0024592 | 0.063785 | 0.015414 | -0.00070293 | -0.0011965 | 0.061449 | 0.010002 | 0.061086 | -66.8068 | 0.028878 | -66.746 | 56.2427 | 56.0968 | 56.2253 | -66.8513 | -66.7886 | 0.027831 | -66.8323 | 56.1528 | 56.2893 | 56.1414 | -67.0103 | -0.072687 | -0.094293 | -0.028224 | 0.032559 | 0.10525 | -0.24021 | -0.11171 | -0.23174 | -0.18422 | -0.010029 | -0.053692 | 0.17804 | -0.047665 | -0.19556 | 123.0212 | 122.8753 | 123.0038 | 66.8074 | -123.1882 | 122.9313 | 123.0679 | 122.92 | 66.8064 | -123.3473
284.7969 | 123.2437 | -66.7923 | 56.3324 | -0.0029761 | -0.0022308 | 0.0015299 | 0.054577 | -0.0024592 | 0.063358 | -0.0074779 | -0.0013437 | -0.00098273 | 0.060808 | 0.0097884 | 0.061513 | -66.8068 | 0.033457 | -66.746 | 56.2427 | 56.1013 | 56.2298 | -66.8467 | -66.8023 | 0.036989 | -66.8323 | 56.1528 | 56.2939 | 56.146 | -67.0149 | -0.054375 | -0.089715 | -0.014491 | 0.046292 | 0.10067 | -0.23105 | -0.10255 | -0.22258 | -0.17964 | -0.010032 | -0.039959 | 0.18262 | -0.038508 | -0.1864 | 123.035 | 122.8936 | 123.0221 | 66.8258 | -123.1791 | 122.9451 | 123.0862 | 122.9383 | 66.8293 | -123.3473
285.7969 | 123.2895 | -66.7877 | 56.2866 | 0.0046549 | -0.0024444 | 0.0013163 | 0.054363 | -0.0024592 | 0.063571 | 0.015414 | -0.00091653 | -0.0014101 | 0.060808 | 0.0095746 | 0.061299 | -66.8022 | 0.0243 | -66.746 | 56.2335 | 56.083 | 56.2207 | -66.8558 | -66.7932 | 0.023253 | -66.8323 | 56.1528 | 56.2802 | 56.1506 | -67.0195 | -0.06811 | -0.053096 | -0.01449 | 0.041715 | 0.10983 | -0.20359 | -0.065931 | -0.23174 | -0.13386 | -0.005452 | -0.044536 | 0.1872 | -0.006468 | -0.13605 | 123.0212 | 122.8707 | 123.0084 | 66.812 | -123.1425 | 122.9405 | 123.0679 | 122.9383 | 66.811 | -123.3061
286.7969 | 123.2803 | -66.7694 | 56.3324 | -0.0029761 | -0.0022308 | 0.0013163 | 0.054577 | -0.0024592 | 0.063571 | 0.00015261 | -0.00070293 | -0.0014101 | 0.061236 | 0.010216 | 0.061299 | -66.8114 | 0.028878 | -66.746 | 56.2473 | 56.1013 | 56.2253 | -66.8513 | -66.7932 | 0.018674 | -66.8323 | 56.1482 | 56.2893 | 56.146 | -67.0103 | -0.081842 | -0.085137 | -0.041958 | 0.023404 | 0.10525 | -0.23105 | -0.10713 | -0.24089 | -0.18422 | -0.023763 | -0.062847 | 0.17804 | -0.043087 | -0.1864 | 123.0167 | 122.8708 | 122.9947 | 66.7983 | -123.1836 | 122.9176 | 123.0587 | 122.9154 | 66.7881 | -123.3427
287.8594 | 123.2071 | -66.7877 | 56.369 | 0.012286 | -0.0022308 | 0.0013163 | 0.054791 | -0.002673 | 0.063358 | 0.0077831 | -0.00027553 | -0.00076913 | 0.061022 | 0.010216 | 0.061299 | -66.7976 | 0.0243 | -66.7552 | 56.2335 | 56.1013 | 56.2298 | -66.8513 | -66.8023 | 0.027831 | -66.8368 | 56.1482 | 56.2893 | 56.1506 | -67.0195 | -0.063531 | -0.13549 | -0.009911 | 0.032559 | 0.09609 | -0.26768 | -0.13917 | -0.23174 | -0.22084 | -0.014609 | -0.049114 | 0.18263 | -0.079709 | -0.21844 | 123.0212 | 122.8891 | 123.0176 | 66.812 | -123.2203 | 122.9359 | 123.077 | 122.9383 | 66.8156 | -123.3885
288.7969 | 123.2758 | -66.7786 | 56.3232 | -0.0029761 | -0.0024444 | 0.0011025 | 0.054577 | -0.0022456 | 0.063785 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061236 | 0.0095746 | 0.061299 | -66.7976 | 0.028878 | -66.746 | 56.2427 | 56.0922 | 56.2298 | -66.8467 | -66.8023 | 0.03241 | -66.8368 | 56.1573 | 56.2985 | 56.1323 | -67.0195 | -0.068108 | -0.08056 | -0.019067 | 0.032559 | 0.10067 | -0.23106 | -0.093395 | -0.24089 | -0.1659 | -0.023765 | -0.05827 | 0.18263 | -0.024775 | -0.19098 | 123.0212 | 122.8707 | 123.0084 | 66.8074 | -123.1699 | 122.9359 | 123.077 | 122.9108 | 66.811 | -123.3427
289.7969 | 123.2849 | -66.7831 | 56.3232 | 0.0046549 | -0.002658 | 0.0013163 | 0.054363 | -0.002673 | 0.063358 | 0.0077831 | -0.00048933 | -0.00076913 | 0.060808 | 0.0097884 | 0.061513 | -66.7976 | 0.028878 | -66.7643 | 56.2427 | 56.0968 | 56.2298 | -66.8558 | -66.8023 | 0.027831 | -66.8414 | 56.1482 | 56.2939 | 56.1323 | -67.0195 | -0.072688 | -0.08056 | -0.014489 | 0.018824 | 0.091512 | -0.22648 | -0.093395 | -0.23632 | -0.17506 | -0.019187 | -0.058271 | 0.17805 | -0.029353 | -0.19098 | 123.0258 | 122.8799 | 123.013 | 66.812 | -123.1791 | 122.9313 | 123.077 | 122.9154 | 66.811 | -123.3427
290.7969 | 123.23 | -66.8015 | 56.3278 | 0.0046549 | -0.002658 | 0.0015299 | 0.054791 | -0.002673 | 0.063571 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061022 | 0.010216 | 0.061299 | -66.7976 | 0.033457 | -66.7506 | 56.2427 | 56.0922 | 56.2298 | -66.8604 | -66.8023 | 0.027831 | -66.8368 | 56.1528 | 56.2802 | 56.1414 | -67.0149 | -0.058955 | -0.085138 | 0.003822 | 0.05087 | 0.10983 | -0.23564 | -0.097973 | -0.21343 | -0.17506 | -0.000876 | -0.035381 | 0.17805 | -0.047667 | -0.1864 | 123.0441 | 122.8936 | 123.0313 | 66.8349 | -123.1882 | 122.9542 | 123.0816 | 122.9429 | 66.8293 | -123.3427
291.8594 | 123.3444 | -66.7465 | 56.3232 | -0.0029761 | -0.0024444 | 0.0011025 | 0.054577 | -0.0022456 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060595 | 0.010216 | 0.061086 | -66.7976 | 0.019721 | -66.7552 | 56.2335 | 56.0922 | 56.2253 | -66.8467 | -66.8023 | 0.027831 | -66.8414 | 56.1528 | 56.2939 | 56.1414 | -67.0103 | -0.10015 | -0.089717 | -0.05111 | -0.00864 | 0.091511 | -0.23106 | -0.097974 | -0.26378 | -0.17048 | -0.055808 | -0.094892 | 0.16889 | -0.029353 | -0.18182 | 122.98 | 122.8387 | 122.9718 | 66.7662 | -123.1699 | 122.8993 | 123.0404 | 122.8879 | 66.7744 | -123.3335
292.7969 | 123.2071 | -66.8198 | 56.337 | -0.0029761 | -0.0024444 | 0.0015299 | 0.054577 | -0.0024592 | 0.063785 | -0.0074779 | -0.00070293 | -0.00098273 | 0.061022 | 0.010216 | 0.061086 | -66.8022 | 0.028878 | -66.7597 | 56.2427 | 56.0968 | 56.2298 | -66.8375 | -66.7977 | 0.03241 | -66.8323 | 56.1528 | 56.2893 | 56.1414 | -67.0149 | -0.017751 | -0.094293 | 0.017553 | 0.060023 | 0.077774 | -0.24021 | -0.10713 | -0.19512 | -0.18422 | 0.022013 | -0.012493 | 0.18262 | -0.047665 | -0.19556 | 123.0624 | 122.9165 | 123.0496 | 66.8486 | -123.1745 | 122.9725 | 123.1091 | 122.9612 | 66.8522 | -123.3519
293.8594 | 123.3307 | -66.7648 | 56.3095 | -0.0029761 | -0.0024444 | 0.0013163 | 0.054791 | -0.0024592 | 0.063144 | 0.0077831 | -0.00091653 | -0.00076913 | 0.061022 | 0.010429 | 0.061299 | -66.8068 | 0.028878 | -66.7414 | 56.2381 | 56.0876 | 56.2298 | -66.8513 | -66.7977 | 0.018674 | -66.8323 | 56.1573 | 56.2847 | 56.1414 | -67.0103 | -0.086419 | -0.071405 | -0.041956 | 0.023405 | 0.10982 | -0.2219 | -0.079662 | -0.24547 | -0.15217 | -0.032918 | -0.067424 | 0.17804 | -0.024778 | -0.16809 | 123.0029 | 122.8524 | 122.9947 | 66.7937 | -123.1608 | 122.9222 | 123.0496 | 122.9062 | 66.7835 | -123.3198
294.7969 | 123.1705 | -66.8289 | 56.3095 | -0.018238 | -0.0022308 | 0.0017435 | 0.054363 | -0.0024592 | 0.063571 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060808 | 0.010002 | 0.061086 | -66.7976 | 0.0243 | -66.7506 | 56.2381 | 56.0968 | 56.2207 | -66.8558 | -66.8023 | 0.03241 | -66.8368 | 56.1436 | 56.2847 | 56.146 | -67.0149 | -0.026912 | -0.071405 | 0.031287 | 0.078335 | 0.10525 | -0.21274 | -0.088819 | -0.18596 | -0.16591 | 0.026589 | -0.007916 | 0.17805 | -0.024778 | -0.16351 | 123.067 | 122.9257 | 123.0496 | 66.8532 | -123.1653 | 122.9725 | 123.1136 | 122.9749 | 66.8613 | -123.3244
295.7969 | 123.3536 | -66.7557 | 56.2866 | -0.010607 | -0.002658 | 0.0013163 | 0.055004 | -0.0024592 | 0.063571 | 0.015414 | -0.00048933 | -0.0011965 | 0.061022 | 0.010216 | 0.061299 | -66.8022 | 0.033457 | -66.7552 | 56.2381 | 56.0968 | 56.2298 | -66.8513 | -66.7932 | 0.023253 | -66.8323 | 56.1528 | 56.2893 | 56.146 | -67.0149 | -0.095575 | -0.048517 | -0.046534 | 0.000515 | 0.09609 | -0.18986 | -0.056774 | -0.2592 | -0.13386 | -0.037496 | -0.07658 | 0.18262 | 0.002689 | -0.14062 | 122.9938 | 122.8524 | 122.9855 | 66.7891 | -123.1379 | 122.9084 | 123.045 | 122.9017 | 66.7789 | -123.3015
296.8594 | 123.2254 | -66.7694 | 56.3507 | -0.0029761 | -0.0024444 | 0.0013163 | 0.054577 | -0.0024592 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061022 | 0.010216 | 0.061086 | -66.8022 | 0.033457 | -66.746 | 56.2381 | 56.0968 | 56.2161 | -66.8421 | -66.8023 | 0.027831 | -66.8277 | 56.1528 | 56.2893 | 56.1368 | -67.0149 | -0.072684 | -0.1126 | -0.032801 | 0.023404 | 0.096088 | -0.25394 | -0.1346 | -0.24547 | -0.19795 | -0.03292 | -0.058268 | 0.1872 | -0.061398 | -0.21387 | 123.0075 | 122.8662 | 122.9855 | 66.8029 | -123.1928 | 122.9222 | 123.0587 | 122.9062 | 66.7972 | -123.3656
297.7969 | 123.2574 | -66.7969 | 56.3095 | -0.0029761 | -0.002658 | 0.00088894 | 0.054791 | -0.0022456 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061022 | 0.010429 | 0.061299 | -66.8114 | 0.0243 | -66.7506 | 56.2381 | 56.0922 | 56.2298 | -66.8467 | -66.8023 | 0.03241 | -66.8368 | 56.1528 | 56.2802 | 56.146 | -67.0149 | -0.049797 | -0.071405 | -0.014492 | 0.046292 | 0.096089 | -0.21732 | -0.079662 | -0.21801 | -0.15675 | -0.005454 | -0.039959 | 0.17805 | -0.029356 | -0.16351 | 123.035 | 122.8891 | 123.0267 | 66.8212 | -123.1562 | 122.9496 | 123.077 | 122.9429 | 66.8293 | -123.3244
298.7969 | 123.2346 | -66.7969 | 56.2912 | -0.010607 | -0.0030854 | 0.0011025 | 0.054363 | -0.0024592 | 0.063358 | -0.0074779 | -0.00048933 | -0.00098273 | 0.060808 | 0.010429 | 0.061086 | -66.8022 | 0.038035 | -66.7506 | 56.2427 | 56.1013 | 56.2253 | -66.8513 | -66.7932 | 0.027831 | -66.8368 | 56.1482 | 56.2847 | 56.1414 | -67.024 | -0.054376 | -0.048517 | -0.005335 | 0.046292 | 0.10067 | -0.18986 | -0.065931 | -0.22716 | -0.14302 | 0.003703 | -0.039959 | 0.1872 | -0.006468 | -0.14978 | 123.0396 | 122.8982 | 123.0221 | 66.8349 | -123.1424 | 122.9451 | 123.0816 | 122.9383 | 66.8247 | -123.3152
299.7969 | 123.2346 | -66.8518 | 56.3278 | 0.0046549 | -0.0024444 | 0.0013163 | 0.054791 | -0.002032 | 0.063571 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061022 | 0.010643 | 0.061299 | -66.8022 | 0.028878 | -66.7506 | 56.2289 | 56.1013 | 56.2253 | -66.8513 | -66.7932 | 0.027831 | -66.8323 | 56.1528 | 56.2893 | 56.1368 | -67.0149 | 0.000556 | -0.098873 | 0.049597 | 0.10122 | 0.10067 | -0.22648 | -0.10255 | -0.16307 | -0.17506 | 0.058635 | 0.019551 | 0.18262 | -0.03851 | -0.19098 | 123.0808 | 122.9531 | 123.0771 | 66.8807 | -123.1791 | 123.0046 | 123.1411 | 122.9886 | 66.8796 | -123.3427
300.7969 | 123.3261 | -66.7328 | 56.2546 | -0.010607 | -0.002658 | 0.0013163 | 0.054577 | -0.0022456 | 0.063571 | -0.015108 | -0.00048933 | -0.0011965 | 0.060808 | 0.010429 | 0.061086 | -66.8022 | 0.033457 | -66.7414 | 56.2335 | 56.1013 | 56.2344 | -66.8467 | -66.7977 | 0.027831 | -66.8323 | 56.1573 | 56.2893 | 56.1414 | -67.0195 | -0.11388 | -0.021053 | -0.069422 | -0.008639 | 0.10524 | -0.15324 | -0.020153 | -0.28667 | -0.097239 | -0.064962 | -0.099468 | 0.1872 | 0.034732 | -0.11316 | 122.9663 | 122.8341 | 122.9672 | 66.7662 | -123.1012 | 122.8901 | 123.0221 | 122.8742 | 66.7606 | -123.274
301.7969 | 123.2254 | -66.7648 | 56.3416 | -0.018238 | -0.0028718 | 0.0011025 | 0.054577 | -0.0022456 | 0.063571 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060808 | 0.010216 | 0.061299 | -66.8068 | 0.033457 | -66.7552 | 56.2473 | 56.0968 | 56.2344 | -66.8558 | -66.7977 | 0.027831 | -66.8277 | 56.1528 | 56.2939 | 56.1414 | -67.0149 | -0.090998 | -0.094293 | -0.041956 | 0.009671 | 0.10067 | -0.24479 | -0.10713 | -0.25005 | -0.18879 | -0.032918 | -0.062845 | 0.1872 | -0.047664 | -0.20013 | 123.0121 | 122.8616 | 122.9993 | 66.7983 | -123.1974 | 122.9176 | 123.0587 | 122.9062 | 66.7927 | -123.3564
302.8594 | 123.3215 | -66.7831 | 56.2912 | 0.0046549 | -0.0028718 | 0.0015299 | 0.054577 | -0.002032 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061022 | 0.010216 | 0.060872 | -66.8068 | 0.028878 | -66.7506 | 56.2335 | 56.1013 | 56.2253 | -66.8513 | -66.7886 | 0.023253 | -66.8277 | 56.1619 | 56.2939 | 56.1323 | -67.0195 | -0.068109 | -0.057674 | -0.023646 | 0.032559 | 0.10067 | -0.18986 | -0.065931 | -0.23632 | -0.12928 | -0.005451 | -0.044535 | 0.19178 | 0.00269 | -0.15894 | 123.0167 | 122.8845 | 123.0084 | 66.812 | -123.1424 | 122.9451 | 123.077 | 122.9154 | 66.8064 | -123.3107
303.7969 | 123.2574 | -66.8106 | 56.2958 | -0.0029761 | -0.002658 | 0.0013163 | 0.054577 | -0.002673 | 0.063144 | -0.0074779 | -0.00048933 | -0.00098273 | 0.060808 | 0.010429 | 0.060872 | -66.8068 | 0.033457 | -66.746 | 56.2381 | 56.1013 | 56.2298 | -66.8467 | -66.7977 | 0.023253 | -66.8323 | 56.1528 | 56.2939 | 56.1368 | -67.0149 | -0.036064 | -0.057672 | 0.00382 | 0.064603 | 0.10067 | -0.19443 | -0.065929 | -0.20427 | -0.14302 | 0.012858 | -0.021648 | 0.18262 | -0.001887 | -0.15894 | 123.0487 | 122.912 | 123.0405 | 66.8441 | -123.1424 | 122.9634 | 123.1045 | 122.9474 | 66.8339 | -123.3107
304.8594 | 123.1979 | -66.774 | 56.3232 | -0.0029761 | -0.0022308 | 0.0015299 | 0.054363 | -0.0024592 | 0.063358 | -0.0074779 | -0.00070293 | -0.00055553 | 0.061022 | 0.010857 | 0.061299 | -66.8022 | 0.0243 | -66.7414 | 56.2381 | 56.1059 | 56.2207 | -66.8467 | -66.7977 | 0.03241 | -66.8368 | 56.1482 | 56.2893 | 56.146 | -67.024 | -0.072685 | -0.085138 | -0.028223 | 0.03256 | 0.10524 | -0.21732 | -0.10255 | -0.25005 | -0.17506 | -0.023763 | -0.062847 | 0.1872 | -0.033932 | -0.17725 | 123.0121 | 122.8799 | 122.9947 | 66.7983 | -123.1699 | 122.9222 | 123.0633 | 122.92 | 66.8064 | -123.3473
305.7969 | 123.2574 | -66.7648 | 56.3004 | -0.0029761 | -0.002658 | 0.0011025 | 0.054791 | -0.0022456 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061022 | 0.010429 | 0.060872 | -66.8022 | 0.028878 | -66.7506 | 56.2473 | 56.0876 | 56.2253 | -66.8513 | -66.7977 | 0.023253 | -66.8368 | 56.1528 | 56.2893 | 56.146 | -67.0149 | -0.086419 | -0.053094 | -0.037378 | 0.014249 | 0.10067 | -0.21275 | -0.075086 | -0.25005 | -0.14759 | -0.032918 | -0.072002 | 0.17805 | -0.011044 | -0.15436 | 123.0121 | 122.8524 | 122.9901 | 66.7937 | -123.1516 | 122.9176 | 123.0541 | 122.9108 | 66.7881 | -123.3152
306.7969 | 123.3627 | -66.7603 | 56.25 | -0.0029761 | -0.0024444 | 0.0013163 | 0.054577 | -0.0024592 | 0.063144 | 0.0077831 | -0.00048933 | -0.00098273 | 0.060808 | 0.010216 | 0.061299 | -66.7976 | 0.033457 | -66.7552 | 56.2381 | 56.0968 | 56.2253 | -66.8467 | -66.7932 | 0.023253 | -66.8323 | 56.1528 | 56.2939 | 56.1368 | -67.0195 | -0.086418 | -0.011896 | -0.037377 | 0.005093 | 0.091511 | -0.15324 | -0.024732 | -0.2592 | -0.09724 | -0.032918 | -0.072002 | 0.1872 | 0.043889 | -0.11316 | 122.9984 | 122.857 | 122.9855 | 66.7937 | -123.0967 | 122.913 | 123.0541 | 122.8971 | 66.7835 | -123.2695
307.8594 | 123.1842 | -66.8106 | 56.3187 | -0.0029761 | -0.002658 | 0.0011025 | 0.054791 | -0.002673 | 0.063144 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061236 | 0.010429 | 0.061086 | -66.8022 | 0.028878 | -66.746 | 56.2473 | 56.0876 | 56.2207 | -66.8421 | -66.7886 | 0.023253 | -66.8368 | 56.139 | 56.2939 | 56.1414 | -67.0195 | -0.031485 | -0.071405 | 0.008398 | 0.064603 | 0.096088 | -0.23106 | -0.097975 | -0.20885 | -0.17964 | 0.022015 | -0.026226 | 0.18263 | -0.024776 | -0.17725 | 123.0579 | 122.8982 | 123.0313 | 66.8395 | -123.1608 | 122.9496 | 123.1045 | 122.952 | 66.8339 | -123.3381
308.7969 | 123.2895 | -66.7557 | 56.2912 | -0.0029761 | -0.002017 | 0.0011025 | 0.054791 | -0.0024592 | 0.063358 | 0.00015261 | -0.00048933 | -0.00034193 | 0.061022 | 0.010429 | 0.061086 | -66.8022 | 0.028878 | -66.7414 | 56.2381 | 56.0739 | 56.2253 | -66.8421 | -66.7977 | 0.018674 | -66.8323 | 56.1482 | 56.2893 | 56.1414 | -67.0149 | -0.086417 | -0.053095 | -0.046534 | 0.014249 | 0.10067 | -0.21733 | -0.065931 | -0.2592 | -0.14302 | -0.042074 | -0.07658 | 0.18262 | -0.001889 | -0.14978 | 122.9938 | 122.8295 | 122.9809 | 66.7846 | -123.1333 | 122.9039 | 123.045 | 122.8971 | 66.7743 | -123.3061
309.7969 | 123.3353 | -66.7603 | 56.2683 | -0.010607 | -0.002658 | 0.0013163 | 0.054363 | -0.0024592 | 0.063358 | -0.0074779 | -0.00070293 | -0.00076913 | 0.060808 | 0.010216 | 0.060658 | -66.8022 | 0.028878 | -66.7506 | 56.2427 | 56.0922 | 56.2298 | -66.8467 | -66.7932 | 0.027831 | -66.8323 | 56.1482 | 56.2939 | 56.1368 | -67.0103 | -0.086418 | -0.025629 | -0.041956 | 0.009671 | 0.096089 | -0.17613 | -0.038464 | -0.25005 | -0.12013 | -0.032918 | -0.072002 | 0.17804 | 0.025578 | -0.13147 | 123.0029 | 122.8524 | 122.9901 | 66.7891 | -123.115 | 122.9084 | 123.0541 | 122.8971 | 66.7881 | -123.2786
310.7969 | 123.2574 | -66.7694 | 56.3644 | 0.0046549 | -0.002658 | 0.0011025 | 0.054577 | -0.0022456 | 0.063358 | 0.00015261 | -0.00048933 | -0.00098273 | 0.060808 | 0.010643 | 0.061086 | -66.8068 | 0.0243 | -66.7506 | 56.2427 | 56.0968 | 56.2253 | -66.8558 | -66.7932 | 0.027831 | -66.8277 | 56.1528 | 56.2985 | 56.1323 | -67.0195 | -0.086421 | -0.12176 | -0.037379 | 0.018826 | 0.10525 | -0.26768 | -0.13917 | -0.25005 | -0.21168 | -0.023763 | -0.058268 | 0.19178 | -0.065974 | -0.23218 | 123.0121 | 122.8662 | 122.9947 | 66.7937 | -123.2203 | 122.9222 | 123.0679 | 122.9017 | 66.7972 | -123.3839
311.7969 | 123.3215 | -66.7511 | 56.2683 | 0.0046549 | -0.0028718 | 0.0013163 | 0.054577 | -0.002673 | 0.06293 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060808 | 0.010857 | 0.060872 | -66.8022 | 0.033457 | -66.7414 | 56.2381 | 56.0922 | 56.2207 | -66.8513 | -66.7932 | 0.027831 | -66.8323 | 56.1573 | 56.2939 | 56.1414 | -67.0149 | -0.10015 | -0.030207 | -0.051111 | 0.009672 | 0.10982 | -0.17613 | -0.047621 | -0.26378 | -0.11097 | -0.042073 | -0.081157 | 0.18262 | 0.025578 | -0.12689 | 122.9892 | 122.8433 | 122.9718 | 66.7846 | -123.1196 | 122.9084 | 123.045 | 122.8925 | 66.7789 | -123.2832
312.8594 | 123.3215 | -66.7557 | 56.3141 | 0.012286 | -0.0024444 | 0.0013163 | 0.055004 | -0.0024592 | 0.063144 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061022 | 0.010429 | 0.061086 | -66.7976 | 0.0243 | -66.746 | 56.2335 | 56.0968 | 56.2253 | -66.8513 | -66.7977 | 0.023253 | -66.8323 | 56.1482 | 56.2939 | 56.146 | -67.0149 | -0.095575 | -0.080562 | -0.041955 | 0.009671 | 0.10525 | -0.21732 | -0.088819 | -0.2592 | -0.16591 | -0.042074 | -0.07658 | 0.18262 | -0.020198 | -0.16809 | 122.9892 | 122.8524 | 122.9809 | 66.78 | -123.1653 | 122.9039 | 123.0496 | 122.9017 | 66.7789 | -123.329
313.7969 | 123.2758 | -66.7694 | 56.3004 | -0.0029761 | -0.0024444 | 0.0013163 | 0.054791 | -0.0024592 | 0.063571 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060808 | 0.010643 | 0.061299 | -66.8068 | 0.0243 | -66.7552 | 56.2381 | 56.0922 | 56.2298 | -66.8513 | -66.7977 | 0.027831 | -66.8277 | 56.1528 | 56.2985 | 56.146 | -67.0195 | -0.081842 | -0.06225 | -0.037379 | 0.014248 | 0.09609 | -0.20817 | -0.070507 | -0.25005 | -0.14759 | -0.028341 | -0.058268 | 0.19178 | -0.001887 | -0.15436 | 123.0075 | 122.8616 | 122.9993 | 66.7937 | -123.1516 | 122.9222 | 123.0679 | 122.9154 | 66.7972 | -123.3198
314.8594 | 123.2254 | -66.7969 | 56.3416 | 0.0046549 | -0.002658 | 0.0011025 | 0.055004 | -0.0024592 | 0.063144 | 0.0077831 | -0.00070293 | -0.0014101 | 0.060381 | 0.010216 | 0.061086 | -66.7976 | 0.028878 | -66.7552 | 56.2381 | 56.0968 | 56.2298 | -66.8513 | -66.7977 | 0.027831 | -66.8323 | 56.1482 | 56.2939 | 56.1414 | -67.0149 | -0.054376 | -0.10345 | -0.000756 | 0.041714 | 0.09609 | -0.24479 | -0.11171 | -0.21801 | -0.19337 | -0.000875 | -0.035381 | 0.18262 | -0.047664 | -0.20013 | 123.035 | 122.8936 | 123.0267 | 66.8258 | -123.1928 | 122.9451 | 123.0908 | 122.9383 | 66.8247 | -123.3564
315.7969 | 123.3765 | -66.7465 | 56.3049 | 0.0046549 | -0.0030854 | 0.0013163 | 0.054577 | -0.002673 | 0.063358 | -0.015108 | -0.00070293 | -0.00098273 | 0.061022 | 0.010216 | 0.061086 | -66.7976 | 0.019721 | -66.746 | 56.2289 | 56.1013 | 56.2253 | -66.8467 | -66.7932 | 0.03241 | -66.8368 | 56.1528 | 56.2847 | 56.1368 | -67.0195 | -0.10015 | -0.075985 | -0.05111 | 0.000516 | 0.10067 | -0.20359 | -0.079664 | -0.27294 | -0.15217 | -0.046651 | -0.090313 | 0.18263 | -0.020201 | -0.16809 | 122.9755 | 122.8479 | 122.9718 | 66.7662 | -123.1516 | 122.8993 | 123.0313 | 122.8834 | 66.7789 | -123.3244
316.7969 | 123.3765 | -66.7145 | 56.2866 | 0.0046549 | -0.002658 | 0.0011025 | 0.055004 | -0.0024592 | 0.063358 | 0.015414 | -0.00048933 | -0.0011965 | 0.060808 | 0.010857 | 0.060872 | -66.7976 | 0.033457 | -66.7506 | 56.2427 | 56.1059 | 56.2298 | -66.8421 | -66.7977 | 0.018674 | -66.8277 | 56.1528 | 56.2939 | 56.1414 | -67.0149 | -0.12762 | -0.043939 | -0.083153 | -0.036105 | 0.09151 | -0.1807 | -0.056774 | -0.3004 | -0.13386 | -0.083272 | -0.1132 | 0.1872 | 0.007268 | -0.1452 | 122.9572 | 122.8204 | 122.9443 | 66.7479 | -123.1287 | 122.8672 | 123.0084 | 122.8559 | 66.7332 | -123.3015
317.7969 | 123.3032 | -66.7694 | 56.2958 | -0.0029761 | -0.0028718 | 0.0013163 | 0.054577 | -0.002673 | 0.06293 | 0.0077831 | -0.00070293 | -0.00076913 | 0.061022 | 0.010643 | 0.061086 | -66.8022 | 0.033457 | -66.746 | 56.2289 | 56.0968 | 56.2253 | -66.8421 | -66.7886 | 0.03241 | -66.8231 | 56.1436 | 56.2847 | 56.1368 | -67.0195 | -0.072684 | -0.066829 | -0.032801 | 0.023404 | 0.096088 | -0.19901 | -0.070508 | -0.25005 | -0.15217 | -0.019184 | -0.053689 | 0.19636 | -0.011045 | -0.15894 | 122.9984 | 122.8662 | 122.9947 | 66.8029 | -123.1379 | 122.913 | 123.0541 | 122.9062 | 66.8018 | -123.3152
318.8594 | 123.3398 | -66.7648 | 56.3049 | 0.012286 | -0.002658 | 0.0011025 | 0.054791 | -0.002032 | 0.063358 | 0.015414 | -0.00070293 | -0.0011965 | 0.061022 | 0.010857 | 0.061086 | -66.8022 | 0.028878 | -66.746 | 56.2335 | 56.1013 | 56.2253 | -66.8467 | -66.7977 | 0.027831 | -66.8323 | 56.1528 | 56.2939 | 56.146 | -67.0149 | -0.08184 | -0.071407 | -0.037378 | 0.018827 | 0.10067 | -0.20359 | -0.079664 | -0.25005 | -0.15217 | -0.032918 | -0.067424 | 0.18262 | -0.011043 | -0.15894 | 122.9984 | 122.8662 | 122.9901 | 66.7937 | -123.1516 | 122.9176 | 123.0587 | 122.9108 | 66.7927 | -123.3198
319.7969 | 123.3353 | -66.7328 | 56.3049 | 0.0046549 | -0.0030854 | 0.0015299 | 0.054791 | -0.002673 | 0.063144 | 0.015414 | -0.00070293 | -0.00098273 | 0.060595 | 0.010216 | 0.060872 | -66.8022 | 0.0243 | -66.7506 | 56.2381 | 56.1013 | 56.2253 | -66.8513 | -66.7886 | 0.03241 | -66.8323 | 56.1482 | 56.2893 | 56.146 | -67.0195 | -0.11846 | -0.066828 | -0.069422 | -0.017795 | 0.10067 | -0.20359 | -0.079664 | -0.28667 | -0.15675 | -0.055805 | -0.099468 | 0.1872 | -0.015622 | -0.15894 | 122.9709 | 122.8341 | 122.9581 | 66.7571 | -123.1562 | 122.881 | 123.0221 | 122.8788 | 66.7652 | -123.3244
320.7969 | 123.2254 | -66.8243 | 56.3416 | 0.012286 | -0.003299 | 0.0011025 | 0.054791 | -0.002673 | 0.063785 | 0.015414 | -0.00091653 | -0.00055553 | 0.061022 | 0.010429 | 0.061086 | -66.7976 | 0.033457 | -66.7414 | 56.2381 | 56.0922 | 56.2207 | -66.8558 | -66.7932 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.146 | -67.0149 | -0.031489 | -0.10345 | 0.02671 | 0.082914 | 0.1144 | -0.24937 | -0.12086 | -0.19054 | -0.19337 | 0.031169 | 0.001243 | 0.19178 | -0.052243 | -0.19556 | 123.0624 | 122.9165 | 123.045 | 66.8578 | -123.1974 | 122.9725 | 123.1137 | 122.9703 | 66.8476 | -123.3564
321.8594 | 123.3032 | -66.7877 | 56.2729 | 0.012286 | -0.0028718 | 0.0015299 | 0.054577 | -0.0022456 | 0.063144 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060808 | 0.010429 | 0.060872 | -66.8022 | 0.028878 | -66.746 | 56.2381 | 56.0876 | 56.2253 | -66.8421 | -66.7932 | 0.027831 | -66.8368 | 56.1482 | 56.2939 | 56.1368 | -67.0195 | -0.054373 | -0.034784 | -0.01449 | 0.041715 | 0.096088 | -0.18528 | -0.04762 | -0.23174 | -0.12471 | -0.005452 | -0.049114 | 0.18263 | 0.021001 | -0.13605 | 123.0258 | 122.8753 | 123.013 | 66.8166 | -123.115 | 122.9359 | 123.0816 | 122.9246 | 66.8156 | -123.2923
322.7969 | 123.2117 | -66.8015 | 56.3324 | 0.0046549 | -0.0030854 | 0.0013163 | 0.055004 | -0.002673 | 0.063144 | 0.00015261 | -0.00091653 | -0.0011965 | 0.061022 | 0.010429 | 0.061086 | -66.8022 | 0.028878 | -66.7552 | 56.2335 | 56.0922 | 56.2253 | -66.8467 | -66.8023 | 0.027831 | -66.8277 | 56.1436 | 56.2985 | 56.1506 | -67.0149 | -0.045219 | -0.098872 | -0.000757 | 0.046292 | 0.091511 | -0.24021 | -0.10713 | -0.21343 | -0.18879 | -0.000876 | -0.026224 | 0.1872 | -0.03393 | -0.18182 | 123.035 | 122.8936 | 123.0267 | 66.8303 | -123.1791 | 122.9451 | 123.0999 | 122.952 | 66.8293 | -123.3473
323.7969 | 123.262 | -66.7786 | 56.3461 | 0.0046549 | -0.002658 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060808 | 0.010857 | 0.060658 | -66.7976 | 0.028878 | -66.7552 | 56.2381 | 56.0968 | 56.2253 | -66.8421 | -66.7932 | 0.027831 | -66.8323 | 56.1528 | 56.2939 | 56.146 | -67.0195 | -0.063529 | -0.10803 | -0.019067 | 0.023403 | 0.086932 | -0.24937 | -0.12086 | -0.24089 | -0.19337 | -0.014608 | -0.053692 | 0.1872 | -0.052241 | -0.20013 | 123.0167 | 122.8753 | 123.0038 | 66.8074 | -123.1882 | 122.9313 | 123.0725 | 122.9246 | 66.8064 | -123.3656
324.8594 | 123.3307 | -66.7465 | 56.3004 | 0.012286 | -0.0030854 | 0.0011025 | 0.054791 | -0.0024592 | 0.063571 | 0.00015261 | -0.00091653 | -0.00098273 | 0.061022 | 0.010643 | 0.061299 | -66.7976 | 0.028878 | -66.7506 | 56.2381 | 56.1059 | 56.2161 | -66.8467 | -66.7977 | 0.023253 | -66.8368 | 56.1573 | 56.2939 | 56.146 | -67.0149 | -0.10015 | -0.06225 | -0.05111 | -0.004062 | 0.096089 | -0.19443 | -0.084243 | -0.26836 | -0.14301 | -0.051229 | -0.090313 | 0.17805 | -0.006465 | -0.15436 | 122.9846 | 122.8524 | 122.9626 | 66.7754 | -123.147 | 122.9039 | 123.0404 | 122.8925 | 66.7698 | -123.3152
325.7969 | 123.2437 | -66.7694 | 56.3095 | 0.0046549 | -0.0028718 | 0.0013163 | 0.054577 | -0.0028866 | 0.063358 | -0.0074779 | -0.00048933 | -0.0011965 | 0.061022 | 0.010429 | 0.061086 | -66.8068 | 0.028878 | -66.7414 | 56.2427 | 56.0922 | 56.2344 | -66.8558 | -66.7932 | 0.023253 | -66.8323 | 56.1482 | 56.2939 | 56.1506 | -67.0195 | -0.086421 | -0.066827 | -0.037379 | 0.027982 | 0.1144 | -0.21732 | -0.075084 | -0.25005 | -0.16133 | -0.023763 | -0.062847 | 0.1872 | -0.01562 | -0.15893 | 123.0121 | 122.8616 | 123.0038 | 66.7983 | -123.1653 | 122.9176 | 123.0633 | 122.92 | 66.7927 | -123.329
326.7969 | 123.2483 | -66.7831 | 56.3232 | -0.0029761 | -0.0030854 | 0.0013163 | 0.054577 | -0.0024592 | 0.063999 | 0.00015261 | -0.00070293 | -0.0014101 | 0.060808 | 0.010857 | 0.060872 | -66.7976 | 0.033457 | -66.746 | 56.2427 | 56.1105 | 56.2298 | -66.8558 | -66.8023 | 0.03241 | -66.8323 | 56.1528 | 56.2893 | 56.1506 | -67.0103 | -0.072688 | -0.08056 | -0.014489 | 0.037137 | 0.10983 | -0.21274 | -0.093395 | -0.22716 | -0.17048 | -0.019187 | -0.049114 | 0.17804 | -0.033932 | -0.17267 | 123.0258 | 122.8936 | 123.013 | 66.8166 | -123.1791 | 122.9359 | 123.0725 | 122.9337 | 66.8156 | -123.3335
327.8594 | 123.2529 | -66.7969 | 56.3141 | -0.0029761 | -0.0030854 | 0.0013163 | 0.054577 | -0.002673 | 0.063785 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060808 | 0.010643 | 0.060658 | -66.7885 | 0.028878 | -66.746 | 56.2427 | 56.0968 | 56.239 | -66.8513 | -66.7932 | 0.027831 | -66.8323 | 56.1436 | 56.2985 | 56.1414 | -67.0149 | -0.054376 | -0.071405 | 0.0084 | 0.05087 | 0.10525 | -0.21732 | -0.075083 | -0.21801 | -0.17048 | 0.003703 | -0.035381 | 0.18262 | -0.01562 | -0.17267 | 123.0396 | 122.8936 | 123.0359 | 66.8258 | -123.1653 | 122.9405 | 123.0953 | 122.9383 | 66.8247 | -123.329
328.7969 | 123.2391 | -66.7969 | 56.2912 | -0.0029761 | -0.002658 | 0.0013163 | 0.054577 | -0.002673 | 0.063358 | 0.0077831 | -0.00091653 | -0.00076913 | 0.060595 | 0.010857 | 0.060872 | -66.7931 | 0.028878 | -66.746 | 56.2381 | 56.0968 | 56.2344 | -66.8558 | -66.7932 | 0.03241 | -66.8277 | 56.1528 | 56.2847 | 56.1414 | -67.0195 | -0.058955 | -0.053095 | 0.003822 | 0.05087 | 0.10983 | -0.19443 | -0.056774 | -0.22258 | -0.13844 | 0.003703 | -0.030802 | 0.19178 | -0.006468 | -0.14978 | 123.035 | 122.8936 | 123.0313 | 66.8258 | -123.147 | 122.9496 | 123.0816 | 122.9383 | 66.8293 | -123.3107
329.7969 | 123.2117 | -66.7877 | 56.3232 | -0.0029761 | -0.0028718 | 0.0011025 | 0.054577 | -0.0022456 | 0.063571 | 0.00015261 | -0.00048933 | -0.00098273 | 0.061236 | 0.010857 | 0.060658 | -66.7976 | 0.0243 | -66.7506 | 56.2381 | 56.0876 | 56.2344 | -66.8513 | -66.7977 | 0.036989 | -66.8323 | 56.1482 | 56.2893 | 56.1414 | -67.0103 | -0.063531 | -0.085138 | -0.009911 | 0.037137 | 0.10067 | -0.23564 | -0.088817 | -0.22258 | -0.17506 | -0.01003 | -0.044536 | 0.17804 | -0.033932 | -0.18182 | 123.0258 | 122.8753 | 123.0221 | 66.812 | -123.1745 | 122.9359 | 123.077 | 122.9291 | 66.8247 | -123.3335
330.7969 | 123.2666 | -66.7877 | 56.282 | 0.0046549 | -0.0030854 | 0.0011025 | 0.054577 | -0.002673 | 0.063358 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061022 | 0.01107 | 0.061086 | -66.7931 | 0.033457 | -66.7597 | 56.2381 | 56.1013 | 56.2298 | -66.8421 | -66.7886 | 0.027831 | -66.8277 | 56.1482 | 56.2847 | 56.146 | -67.0195 | -0.054373 | -0.043939 | -0.005333 | 0.02798 | 0.082353 | -0.1807 | -0.052196 | -0.23174 | -0.13386 | -0.000873 | -0.039957 | 0.19178 | 0.002688 | -0.13605 | 123.0258 | 122.8891 | 123.0176 | 66.8212 | -123.1241 | 122.9359 | 123.0725 | 122.9337 | 66.8156 | -123.3015
331.8594 | 123.2071 | -66.7923 | 56.337 | -0.0029761 | -0.003299 | 0.0011025 | 0.054791 | -0.002673 | 0.063571 | 0.015414 | -0.00070293 | -0.00098273 | 0.061022 | 0.010643 | 0.060872 | -66.8022 | 0.033457 | -66.746 | 56.2335 | 56.1059 | 56.2344 | -66.8513 | -66.7886 | 0.027831 | -66.8323 | 56.1528 | 56.2802 | 56.146 | -67.0149 | -0.058954 | -0.10345 | -0.009913 | 0.046292 | 0.10525 | -0.23105 | -0.10255 | -0.22258 | -0.18422 | 0.003704 | -0.039959 | 0.18262 | -0.056822 | -0.19098 | 123.0258 | 122.8982 | 123.0267 | 66.8258 | -123.1882 | 122.9451 | 123.0725 | 122.9383 | 66.8201 | -123.3519
332.7969 | 123.2895 | -66.7694 | 56.2866 | -0.010607 | -0.0030854 | 0.0013163 | 0.055218 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060595 | 0.010429 | 0.060872 | -66.8022 | 0.0243 | -66.7506 | 56.2381 | 56.0922 | 56.2344 | -66.8467 | -66.7886 | 0.018674 | -66.8323 | 56.1482 | 56.2893 | 56.1368 | -67.024 | -0.077263 | -0.048517 | -0.032801 | 0.018826 | 0.096089 | -0.19444 | -0.052196 | -0.25463 | -0.13844 | -0.019184 | -0.062847 | 0.19178 | 0.002689 | -0.14978 | 123.0075 | 122.8616 | 123.0038 | 66.7937 | -123.1333 | 122.9176 | 123.0587 | 122.9062 | 66.7881 | -123.3107
333.7969 | 123.23 | -66.7786 | 56.3232 | -0.010607 | -0.0028718 | 0.0013163 | 0.054577 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.00076913 | 0.061022 | 0.01107 | 0.060658 | -66.7976 | 0.033457 | -66.746 | 56.2335 | 56.0922 | 56.2344 | -66.8513 | -66.7886 | 0.027831 | -66.8277 | 56.1528 | 56.2847 | 56.146 | -67.0149 | -0.072687 | -0.089717 | -0.019067 | 0.032559 | 0.10525 | -0.23106 | -0.088817 | -0.23632 | -0.17048 | -0.010029 | -0.049113 | 0.1872 | -0.038511 | -0.17725 | 123.0121 | 122.8707 | 123.013 | 66.812 | -123.1745 | 122.9313 | 123.0633 | 122.9246 | 66.8064 | -123.3381
334.7969 | 123.3398 | -66.7557 | 56.2775 | -0.0029761 | -0.0028718 | 0.0015299 | 0.054791 | -0.0024592 | 0.063358 | -0.0074779 | -0.00091653 | -0.0011965 | 0.060808 | 0.01107 | 0.061086 | -66.8022 | 0.0243 | -66.7368 | 56.2335 | 56.083 | 56.2207 | -66.8513 | -66.7886 | 0.03241 | -66.8323 | 56.1482 | 56.2847 | 56.1368 | -67.0103 | -0.095575 | -0.043941 | -0.046534 | 0.018828 | 0.1144 | -0.19444 | -0.056776 | -0.25463 | -0.12928 | -0.032917 | -0.07658 | 0.17804 | 0.007265 | -0.14063 | 122.9892 | 122.8387 | 122.9764 | 66.78 | -123.1287 | 122.9039 | 123.0404 | 122.8925 | 66.7881 | -123.2878
335.7969 | 123.3627 | -66.7328 | 56.2958 | 0.012286 | -0.0028718 | 0.0011025 | 0.054791 | -0.0028866 | 0.063144 | 0.0077831 | -0.0011301 | -0.00098273 | 0.060808 | 0.010857 | 0.060872 | -66.7976 | 0.0243 | -66.7552 | 56.2427 | 56.1105 | 56.2253 | -66.8513 | -66.7932 | 0.018674 | -66.8323 | 56.1436 | 56.2893 | 56.1414 | -67.0195 | -0.11846 | -0.053094 | -0.064843 | -0.022373 | 0.09609 | -0.18528 | -0.070508 | -0.28667 | -0.15217 | -0.060384 | -0.099468 | 0.1872 | -0.006466 | -0.15436 | 122.9755 | 122.8433 | 122.9581 | 66.7571 | -123.147 | 122.8764 | 123.0221 | 122.8742 | 66.7515 | -123.3152
336.8594 | 123.2254 | -66.8106 | 56.3004 | -0.0029761 | -0.0028718 | 0.0015299 | 0.054791 | -0.0024592 | 0.06293 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060808 | 0.01107 | 0.061299 | -66.7976 | 0.0243 | -66.7414 | 56.2335 | 56.0876 | 56.2298 | -66.8513 | -66.7932 | 0.027831 | -66.8277 | 56.1573 | 56.2939 | 56.1414 | -67.0149 | -0.040643 | -0.066829 | 0.012977 | 0.069181 | 0.10982 | -0.21275 | -0.070507 | -0.20427 | -0.14301 | 0.017436 | -0.017069 | 0.1872 | -0.006465 | -0.15894 | 123.0441 | 122.8982 | 123.0405 | 66.8349 | -123.1516 | 122.9679 | 123.1045 | 122.952 | 66.8384 | -123.3152
337.7969 | 123.2941 | -66.7694 | 56.2958 | -0.0029761 | -0.0030854 | 0.0015299 | 0.054791 | -0.0024592 | 0.063571 | 0.0077831 | -0.00091653 | -0.00098273 | 0.061022 | 0.010643 | 0.060872 | -66.7976 | 0.033457 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8421 | -66.784 | 0.023253 | -66.8277 | 56.1528 | 56.2985 | 56.1414 | -67.0195 | -0.072684 | -0.062251 | -0.028222 | 0.023404 | 0.096088 | -0.19443 | -0.061351 | -0.25005 | -0.14302 | -0.014605 | -0.058268 | 0.19178 | 0.002691 | -0.15436 | 123.0029 | 122.8708 | 123.0038 | 66.8029 | -123.1379 | 122.9222 | 123.0679 | 122.9108 | 66.7927 | -123.3152
338.7969 | 123.2849 | -66.7831 | 56.2958 | 0.0046549 | -0.0028718 | 0.0013163 | 0.055004 | -0.0028866 | 0.06293 | 0.00015261 | -0.00070293 | -0.0011965 | 0.061022 | 0.010857 | 0.061086 | -66.8022 | 0.028878 | -66.7414 | 56.2289 | 56.1013 | 56.2298 | -66.8467 | -66.7977 | 0.027831 | -66.8277 | 56.1528 | 56.2939 | 56.1414 | -67.0195 | -0.06353 | -0.066829 | -0.019068 | 0.041715 | 0.10524 | -0.19443 | -0.065929 | -0.23632 | -0.14302 | -0.014608 | -0.044535 | 0.19178 | -0.001887 | -0.15436 | 123.0121 | 122.8845 | 123.013 | 66.812 | -123.1424 | 122.9359 | 123.077 | 122.9246 | 66.811 | -123.3152
339.7969 | 123.3032 | -66.7557 | 56.3049 | 0.0046549 | -0.0028718 | 0.0013163 | 0.054577 | -0.002673 | 0.063571 | 0.00015261 | -0.00091653 | -0.00098273 | 0.061022 | 0.010857 | 0.060872 | -66.7976 | 0.028878 | -66.7414 | 56.2381 | 56.0968 | 56.2298 | -66.8467 | -66.7932 | 0.03241 | -66.8323 | 56.1573 | 56.2893 | 56.1368 | -67.0195 | -0.090996 | -0.066828 | -0.041955 | 0.014249 | 0.10524 | -0.20817 | -0.075085 | -0.26378 | -0.14759 | -0.037496 | -0.07658 | 0.1872 | -0.015622 | -0.16809 | 122.9938 | 122.8524 | 122.9855 | 66.7846 | -123.1516 | 122.913 | 123.045 | 122.8925 | 66.7881 | -123.3244
340.7969 | 123.2391 | -66.7923 | 56.3232 | -0.0029761 | -0.003299 | 0.00067514 | 0.054149 | -0.0024592 | 0.063144 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060595 | 0.011284 | 0.061086 | -66.7931 | 0.033457 | -66.7368 | 56.2335 | 56.1059 | 56.2344 | -66.8513 | -66.7886 | 0.03241 | -66.8277 | 56.1436 | 56.2939 | 56.1368 | -67.0195 | -0.058954 | -0.089717 | -0.000756 | 0.055449 | 0.1144 | -0.21732 | -0.088817 | -0.22716 | -0.17964 | 0.003704 | -0.03538 | 0.19178 | -0.029353 | -0.1864 | 123.0258 | 122.8982 | 123.0267 | 66.8258 | -123.1745 | 122.9359 | 123.0862 | 122.9291 | 66.8247 | -123.3427
341.7969 | 123.2986 | -66.7465 | 56.3232 | -0.0029761 | -0.0028718 | 0.0015299 | 0.054791 | -0.0028866 | 0.063358 | 0.00015261 | -0.00070293 | -0.00076913 | 0.060595 | 0.01107 | 0.060872 | -66.7976 | 0.028878 | -66.7506 | 56.2427 | 56.1013 | 56.2253 | -66.8421 | -66.7886 | 0.023253 | -66.8277 | 56.1528 | 56.2893 | 56.1323 | -67.0195 | -0.095572 | -0.08056 | -0.05111 | -0.004062 | 0.09151 | -0.2219 | -0.097974 | -0.27294 | -0.17048 | -0.042072 | -0.081156 | 0.19178 | -0.033932 | -0.19098 | 122.9892 | 122.8479 | 122.9718 | 66.7754 | -123.1653 | 122.8993 | 123.0358 | 122.8788 | 66.7698 | -123.3427
342.7969 | 123.262 | -66.7648 | 56.3095 | 0.0046549 | -0.003299 | 0.0013163 | 0.054577 | -0.0024592 | 0.063358 | 0.0077831 | -0.00070293 | -0.0014101 | 0.060808 | 0.010857 | 0.061086 | -66.7976 | 0.028878 | -66.7368 | 56.2335 | 56.1059 | 56.2344 | -66.8558 | -66.8023 | 0.027831 | -66.8277 | 56.1528 | 56.2893 | 56.1414 | -67.0103 | -0.090998 | -0.075984 | -0.032799 | 0.027984 | 0.11898 | -0.20359 | -0.075084 | -0.24547 | -0.15675 | -0.037497 | -0.062845 | 0.18262 | -0.020199 | -0.16809 | 122.9984 | 122.8708 | 122.9993 | 66.7937 | -123.1653 | 122.9176 | 123.0541 | 122.9062 | 66.7927 | -123.3198
343.8594 | 123.317 | -66.7603 | 56.2729 | 0.0046549 | -0.0030854 | 0.0013163 | 0.055004 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.010643 | 0.061086 | -66.7931 | 0.0243 | -66.746 | 56.2335 | 56.0968 | 56.2253 | -66.8375 | -66.7886 | 0.023253 | -66.8323 | 56.1436 | 56.2847 | 56.1506 | -67.0195 | -0.07726 | -0.039363 | -0.032799 | 0.014249 | 0.091509 | -0.17612 | -0.04762 | -0.2592 | -0.12929 | -0.028339 | -0.072002 | 0.1872 | 0.011843 | -0.12231 | 122.9938 | 122.857 | 122.9855 | 66.7846 | -123.1104 | 122.9039 | 123.045 | 122.9108 | 66.7835 | -123.2923
344.7969 | 123.2529 | -66.7648 | 56.337 | 0.0046549 | -0.0028718 | 0.00088894 | 0.054791 | -0.0024592 | 0.063144 | 0.00015261 | -0.00070293 | -0.00076913 | 0.060595 | 0.011284 | 0.060872 | -66.8022 | 0.033457 | -66.746 | 56.2381 | 56.0922 | 56.2298 | -66.8467 | -66.7932 | 0.027831 | -66.8231 | 56.1528 | 56.2939 | 56.1506 | -67.0195 | -0.08184 | -0.098871 | -0.037378 | 0.018827 | 0.10067 | -0.24479 | -0.10713 | -0.25463 | -0.18422 | -0.02834 | -0.058266 | 0.19636 | -0.043086 | -0.1864 | 123.0029 | 122.857 | 122.9947 | 66.7983 | -123.1836 | 122.9176 | 123.0587 | 122.9154 | 66.7927 | -123.3564
345.7969 | 123.3444 | -66.7648 | 56.2637 | -0.0029761 | -0.0028718 | 0.0013163 | 0.054363 | -0.0024592 | 0.063358 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060595 | 0.01107 | 0.060872 | -66.7885 | 0.028878 | -66.7414 | 56.2289 | 56.0922 | 56.2298 | -66.8513 | -66.7886 | 0.027831 | -66.8323 | 56.1436 | 56.2893 | 56.146 | -67.0149 | -0.086419 | -0.034786 | -0.023643 | 0.023405 | 0.10982 | -0.17155 | -0.033886 | -0.25005 | -0.12013 | -0.023761 | -0.067424 | 0.18262 | 0.025577 | -0.11774 | 122.9938 | 122.857 | 122.9947 | 66.7937 | -123.115 | 122.9084 | 123.0541 | 122.9108 | 66.7927 | -123.2786
346.8594 | 123.3353 | -66.7282 | 56.2912 | 0.0046549 | -0.0028718 | 0.0017435 | 0.054791 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060167 | 0.01107 | 0.061086 | -66.7976 | 0.028878 | -66.7506 | 56.2381 | 56.1013 | 56.2344 | -66.8558 | -66.7886 | 0.027831 | -66.8277 | 56.1482 | 56.2847 | 56.1368 | -67.0195 | -0.12762 | -0.053095 | -0.069421 | -0.022373 | 0.10525 | -0.18986 | -0.056774 | -0.29125 | -0.14302 | -0.060383 | -0.099467 | 0.19178 | -0.006468 | -0.15436 | 122.9663 | 122.8296 | 122.9626 | 66.7571 | -123.147 | 122.8764 | 123.0129 | 122.865 | 66.756 | -123.3107
347.7969 | 123.2254 | -66.7877 | 56.3187 | -0.0029761 | -0.0030854 | 0.0011025 | 0.054577 | -0.0024592 | 0.06293 | -0.015108 | -0.00091653 | -0.00098273 | 0.060595 | 0.01107 | 0.061086 | -66.7976 | 0.033457 | -66.746 | 56.2381 | 56.0968 | 56.2344 | -66.8513 | -66.7932 | 0.027831 | -66.8231 | 56.1528 | 56.2939 | 56.1368 | -67.0195 | -0.063531 | -0.080561 | -0.009911 | 0.041715 | 0.10525 | -0.2219 | -0.08424 | -0.23174 | -0.16591 | -0.005452 | -0.035378 | 0.19636 | -0.024776 | -0.18183 | 123.0258 | 122.8845 | 123.0221 | 66.8212 | -123.1699 | 122.9405 | 123.0816 | 122.9246 | 66.8156 | -123.3381
348.7969 | 123.262 | -66.7877 | 56.3232 | -0.0029761 | -0.003299 | 0.0013163 | 0.054363 | -0.0024592 | 0.063358 | 0.0077831 | -0.00048933 | -0.00098273 | 0.061022 | 0.011284 | 0.060872 | -66.7931 | 0.033457 | -66.7414 | 56.2335 | 56.0876 | 56.239 | -66.8467 | -66.7932 | 0.036989 | -66.8231 | 56.1528 | 56.2985 | 56.1323 | -67.0195 | -0.058952 | -0.089717 | -0.005333 | 0.046293 | 0.10524 | -0.23564 | -0.084238 | -0.23174 | -0.17048 | -0.005452 | -0.035378 | 0.19636 | -0.024775 | -0.19098 | 123.0212 | 122.8753 | 123.0267 | 66.8212 | -123.1699 | 122.9405 | 123.0862 | 122.92 | 66.8247 | -123.3427
349.7969 | 123.2574 | -66.7694 | 56.3553 | 0.012286 | -0.002658 | 0.00088894 | 0.054363 | -0.0028866 | 0.063144 | -0.0074779 | -0.00070293 | -0.00098273 | 0.060808 | 0.011284 | 0.061086 | -66.7976 | 0.0243 | -66.7552 | 56.2427 | 56.1059 | 56.239 | -66.8467 | -66.7886 | 0.03241 | -66.8323 | 56.1528 | 56.2985 | 56.1368 | -67.0149 | -0.077263 | -0.1126 | -0.028222 | 0.014248 | 0.091511 | -0.24936 | -0.11628 | -0.24547 | -0.20253 | -0.019184 | -0.062847 | 0.18262 | -0.056819 | -0.21845 | 123.0121 | 122.8753 | 123.0084 | 66.7937 | -123.202 | 122.9222 | 123.0679 | 122.9062 | 66.8018 | -123.3702
350.7969 | 123.3307 | -66.774 | 56.2683 | 0.0046549 | -0.0028718 | 0.0013163 | 0.054577 | -0.0024592 | 0.06293 | -0.0074779 | -0.00070293 | -0.00076913 | 0.060808 | 0.011284 | 0.061299 | -66.7976 | 0.038035 | -66.7323 | 56.2427 | 56.0922 | 56.2253 | -66.8513 | -66.7932 | 0.023253 | -66.8185 | 56.1528 | 56.303 | 56.1231 | -67.0195 | -0.077264 | -0.025629 | -0.023644 | 0.041717 | 0.11898 | -0.17613 | -0.043043 | -0.24547 | -0.11555 | -0.019185 | -0.044532 | 0.20094 | 0.034735 | -0.14521 | 123.0167 | 122.8662 | 122.9993 | 66.812 | -123.1196 | 122.9267 | 123.077 | 122.8971 | 66.7972 | -123.2878
351.7969 | 123.262 | -66.7969 | 56.2958 | 0.0046549 | -0.002658 | 0.0015299 | 0.054577 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060808 | 0.011284 | 0.061299 | -66.7976 | 0.028878 | -66.746 | 56.2381 | 56.1059 | 56.2344 | -66.8513 | -66.7977 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.1506 | -67.0149 | -0.054376 | -0.057672 | -0.000756 | 0.05087 | 0.10525 | -0.18985 | -0.061351 | -0.21801 | -0.14759 | -0.000875 | -0.026223 | 0.19178 | -0.006466 | -0.1452 | 123.035 | 122.9028 | 123.0313 | 66.8258 | -123.147 | 122.9451 | 123.0862 | 122.9475 | 66.8201 | -123.3107
352.7969 | 123.3353 | -66.7648 | 56.2683 | -0.0029761 | -0.0028718 | 0.00088894 | 0.054363 | -0.0024592 | 0.063144 | 0.0077831 | -0.00048933 | -0.00098273 | 0.060381 | 0.01107 | 0.060872 | -66.7931 | 0.0243 | -66.7414 | 56.2381 | 56.0968 | 56.2298 | -66.8467 | -66.7886 | 0.023253 | -66.8277 | 56.1482 | 56.2893 | 56.1414 | -67.0149 | -0.08184 | -0.030207 | -0.028221 | 0.023405 | 0.10524 | -0.17155 | -0.038464 | -0.25005 | -0.12013 | -0.023761 | -0.062845 | 0.1872 | 0.020999 | -0.12689 | 123.0029 | 122.8616 | 122.9947 | 66.7891 | -123.115 | 122.913 | 123.0541 | 122.9062 | 66.7881 | -123.2832
353.7969 | 123.1934 | -66.7877 | 56.3095 | -0.010607 | -0.0030854 | 0.0013163 | 0.054149 | -0.0024592 | 0.063144 | -0.0074779 | -0.00070293 | -0.00076913 | 0.061022 | 0.011498 | 0.061086 | -66.8022 | 0.033457 | -66.7414 | 56.2427 | 56.1013 | 56.239 | -66.8513 | -66.7886 | 0.027831 | -66.8323 | 56.1482 | 56.2985 | 56.1323 | -67.0149 | -0.063531 | -0.066827 | -0.01449 | 0.046293 | 0.10982 | -0.20817 | -0.070505 | -0.22716 | -0.16133 | -0.000873 | -0.044536 | 0.18262 | -0.011042 | -0.17725 | 123.0304 | 122.8891 | 123.0267 | 66.8212 | -123.1608 | 122.9359 | 123.0862 | 122.92 | 66.8156 | -123.3244
354.8594 | 123.1888 | -66.8015 | 56.3141 | -0.0029761 | -0.003299 | 0.0015299 | 0.054577 | -0.002673 | 0.063571 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.011498 | 0.060872 | -66.8022 | 0.038035 | -66.7414 | 56.2427 | 56.083 | 56.239 | -66.8558 | -66.7977 | 0.027831 | -66.8231 | 56.1436 | 56.2847 | 56.1323 | -67.0195 | -0.054377 | -0.071405 | -0.000757 | 0.060026 | 0.1144 | -0.23106 | -0.075083 | -0.21801 | -0.17048 | 0.003703 | -0.021645 | 0.19636 | -0.029356 | -0.18183 | 123.0441 | 122.8845 | 123.0405 | 66.8395 | -123.1699 | 122.9451 | 123.0862 | 122.9337 | 66.8293 | -123.3335
355.8125 | 123.2208 | -66.7831 | 56.3278 | -0.0029761 | -0.0035128 | 0.0015299 | 0.054363 | -0.0024592 | 0.063785 | 0.00015261 | -0.00091653 | -0.0011965 | 0.061022 | 0.011284 | 0.060872 | -66.7931 | 0.0243 | -66.7414 | 56.2427 | 56.0968 | 56.239 | -66.8467 | -66.784 | 0.036989 | -66.8323 | 56.1528 | 56.2893 | 56.1414 | -67.0195 | -0.06353 | -0.085138 | -0.009911 | 0.041715 | 0.10524 | -0.23106 | -0.088816 | -0.23632 | -0.17506 | -0.000872 | -0.049114 | 0.1872 | -0.03851 | -0.1864 | 123.0258 | 122.8799 | 123.0221 | 66.8074 | -123.1745 | 122.9359 | 123.0725 | 122.9246 | 66.8201 | -123.3473
356.7969 | 123.3078 | -66.7603 | 56.2454 | 0.0046549 | -0.0028718 | 0.0011025 | 0.054791 | -0.002673 | 0.06293 | -0.0074779 | -0.00070293 | -0.00076913 | 0.061236 | 0.011498 | 0.061086 | -66.7931 | 0.0243 | -66.7506 | 56.2289 | 56.083 | 56.2344 | -66.8513 | -66.7932 | 0.027831 | -66.8323 | 56.1482 | 56.2893 | 56.146 | -67.0149 | -0.090997 | -0.016475 | -0.032799 | 0.009671 | 0.10067 | -0.16239 | -0.010997 | -0.25463 | -0.09724 | -0.032918 | -0.072002 | 0.18262 | 0.043888 | -0.099426 | 122.9892 | 122.8433 | 122.9947 | 66.7846 | -123.0967 | 122.9084 | 123.0496 | 122.9062 | 66.7881 | -123.2603
357.7969 | 123.2895 | -66.7557 | 56.2912 | -0.0029761 | -0.0030854 | 0.0011025 | 0.054791 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.00055553 | 0.060808 | 0.011498 | 0.060872 | -66.7885 | 0.028878 | -66.7552 | 56.2381 | 56.1059 | 56.2298 | -66.8375 | -66.7886 | 0.023253 | -66.8231 | 56.1528 | 56.2802 | 56.1368 | -67.0195 | -0.081838 | -0.053095 | -0.032799 | 0.000515 | 0.082353 | -0.18528 | -0.061352 | -0.26378 | -0.13844 | -0.032917 | -0.067422 | 0.19636 | -0.011046 | -0.15436 | 122.9938 | 122.8616 | 122.9855 | 66.7846 | -123.1287 | 122.9084 | 123.0358 | 122.8925 | 66.7789 | -123.3107
358.7969 | 123.2758 | -66.7694 | 56.2912 | 0.0046549 | -0.003299 | 0.0013163 | 0.055004 | -0.0028866 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060595 | 0.011284 | 0.061299 | -66.7931 | 0.028878 | -66.746 | 56.2381 | 56.1013 | 56.2298 | -66.8421 | -66.7932 | 0.023253 | -66.8277 | 56.1482 | 56.2893 | 56.1368 | -67.0103 | -0.072684 | -0.053095 | -0.023644 | 0.023404 | 0.096088 | -0.18986 | -0.061352 | -0.24089 | -0.14302 | -0.023763 | -0.058268 | 0.18262 | -0.001889 | -0.15436 | 123.0075 | 122.8708 | 122.9993 | 66.7983 | -123.1333 | 122.9176 | 123.0587 | 122.9062 | 66.7927 | -123.3015
359.7969 | 123.3307 | -66.7877 | 56.2683 | -0.0029761 | -0.0028718 | 0.00088894 | 0.054791 | -0.0024592 | 0.063358 | 0.00015261 | -0.00070293 | -0.00055553 | 0.060808 | 0.011284 | 0.060872 | -66.7976 | 0.033457 | -66.7552 | 56.2427 | 56.1013 | 56.2253 | -66.8467 | -66.7932 | 0.027831 | -66.8277 | 56.1436 | 56.303 | 56.1323 | -67.0195 | -0.058952 | -0.025629 | -0.009911 | 0.032559 | 0.091511 | -0.16697 | -0.043043 | -0.23174 | -0.12471 | -0.005452 | -0.039957 | 0.19178 | 0.034735 | -0.13605 | 123.0304 | 122.8891 | 123.013 | 66.8212 | -123.115 | 122.9313 | 123.0908 | 122.92 | 66.8156 | -123.2878
360.7969 | 123.2712 | -66.7603 | 56.3553 | 0.0046549 | -0.0028718 | 0.0013163 | 0.054363 | -0.0022456 | 0.063358 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060808 | 0.011284 | 0.060658 | -66.7931 | 0.0243 | -66.7552 | 56.2335 | 56.0968 | 56.239 | -66.8604 | -66.784 | 0.03241 | -66.8231 | 56.1436 | 56.2893 | 56.1643 | -67.0149 | -0.10015 | -0.12176 | -0.032799 | 0.005093 | 0.10525 | -0.25852 | -0.11628 | -0.25463 | -0.21168 | -0.02376 | -0.062844 | 0.19178 | -0.065976 | -0.19098 | 122.9938 | 122.857 | 122.9993 | 66.7846 | -123.2157 | 122.9039 | 123.0496 | 122.9246 | 66.7927 | -123.3702
361.8594 | 123.3353 | -66.7328 | 56.2729 | -0.0029761 | -0.0028718 | 0.0013163 | 0.055004 | -0.0024592 | 0.063358 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060808 | 0.011711 | 0.060872 | -66.7885 | 0.033457 | -66.746 | 56.2381 | 56.0968 | 56.2298 | -66.8421 | -66.7886 | 0.023253 | -66.8323 | 56.1482 | 56.2893 | 56.1368 | -67.0103 | -0.10931 | -0.034784 | -0.055687 | -0.013217 | 0.096088 | -0.17612 | -0.043041 | -0.27751 | -0.12471 | -0.055805 | -0.099468 | 0.17804 | 0.016422 | -0.13605 | 122.9709 | 122.8296 | 122.9626 | 66.7662 | -123.115 | 122.881 | 123.0221 | 122.8696 | 66.756 | -123.2832
362.7969 | 123.3398 | -66.7419 | 56.3049 | 0.0046549 | -0.0030854 | 0.0015299 | 0.054577 | -0.002673 | 0.063358 | 0.023044 | -0.00048933 | -0.0014101 | 0.060595 | 0.011284 | 0.061086 | -66.7976 | 0.0243 | -66.746 | 56.2381 | 56.0968 | 56.2344 | -66.8513 | -66.7977 | 0.027831 | -66.8277 | 56.1528 | 56.2939 | 56.1414 | -67.0195 | -0.10931 | -0.066828 | -0.055688 | -0.004062 | 0.10525 | -0.20817 | -0.070507 | -0.27752 | -0.15217 | -0.055807 | -0.085734 | 0.19178 | -0.011043 | -0.16351 | 122.98 | 122.8387 | 122.9764 | 66.7662 | -123.1562 | 122.8947 | 123.0358 | 122.8834 | 66.7698 | -123.3244
363.8594 | 123.1888 | -66.7877 | 56.3141 | 0.0046549 | -0.0030854 | 0.0013163 | 0.054363 | -0.002673 | 0.063358 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060595 | 0.011711 | 0.060872 | -66.7976 | 0.033457 | -66.7414 | 56.2427 | 56.1059 | 56.2344 | -66.8513 | -66.7886 | 0.018674 | -66.8277 | 56.1573 | 56.2893 | 56.1277 | -67.0149 | -0.063531 | -0.071405 | -0.009911 | 0.046293 | 0.10982 | -0.20817 | -0.079662 | -0.22716 | -0.15675 | -0.000873 | -0.039957 | 0.1872 | -0.024777 | -0.18641 | 123.0304 | 122.8936 | 123.0221 | 66.8212 | -123.1653 | 122.9451 | 123.077 | 122.9154 | 66.8064 | -123.329
364.7969 | 123.3582 | -66.7145 | 56.282 | 0.019917 | -0.0030854 | 0.0013163 | 0.054577 | -0.0024592 | 0.063571 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060381 | 0.011284 | 0.061086 | -66.7885 | 0.0243 | -66.746 | 56.2335 | 56.083 | 56.2253 | -66.8467 | -66.7932 | 0.018674 | -66.8277 | 56.1482 | 56.2847 | 56.146 | -67.0286 | -0.13219 | -0.048518 | -0.073997 | -0.031527 | 0.10067 | -0.19902 | -0.056775 | -0.31414 | -0.13386 | -0.078694 | -0.1132 | 0.20094 | 0.002688 | -0.13605 | 122.948 | 122.7975 | 122.9397 | 66.7388 | -123.1287 | 122.8627 | 122.9992 | 122.8605 | 66.7332 | -123.3107
365.7969 | 123.2986 | -66.7877 | 56.2912 | -0.0029761 | -0.0035128 | 0.0011025 | 0.054577 | -0.002673 | 0.063571 | -0.0074779 | -0.00070293 | -0.00055553 | 0.060595 | 0.011711 | 0.060872 | -66.7976 | 0.028878 | -66.7414 | 56.2381 | 56.0968 | 56.2344 | -66.8375 | -66.7886 | 0.03241 | -66.8368 | 56.1482 | 56.2893 | 56.1368 | -67.0195 | -0.049794 | -0.053095 | -0.009911 | 0.046293 | 0.096087 | -0.19443 | -0.056774 | -0.23174 | -0.14302 | -0.000873 | -0.049114 | 0.18263 | -0.001889 | -0.15436 | 123.0258 | 122.8845 | 123.0221 | 66.8166 | -123.1287 | 122.9359 | 123.077 | 122.9246 | 66.8201 | -123.3107
366.8594 | 123.3536 | -66.7557 | 56.3141 | 0.0046549 | -0.0030854 | 0.0013163 | 0.054577 | -0.002673 | 0.06293 | 0.0077831 | -0.0011301 | -0.00076913 | 0.060595 | 0.011284 | 0.061299 | -66.7885 | 0.0243 | -66.746 | 56.2381 | 56.1059 | 56.239 | -66.8421 | -66.7932 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.1414 | -67.0103 | -0.086417 | -0.075983 | -0.032799 | 0.009671 | 0.096088 | -0.20817 | -0.075083 | -0.25463 | -0.16591 | -0.037496 | -0.067422 | 0.1872 | -0.024777 | -0.17267 | 122.9938 | 122.8616 | 122.9947 | 66.78 | -123.1562 | 122.9039 | 123.045 | 122.8971 | 66.7789 | -123.3244
367.7969 | 123.1384 | -66.7603 | 56.3873 | -0.0029761 | -0.0037264 | 0.0013163 | 0.054577 | -0.002673 | 0.063144 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060381 | 0.011498 | 0.060872 | -66.7931 | 0.028878 | -66.7368 | 56.2335 | 56.1059 | 56.239 | -66.8421 | -66.7932 | 0.023253 | -66.8368 | 56.1436 | 56.2802 | 56.1323 | -67.0149 | -0.081839 | -0.1538 | -0.032799 | 0.023406 | 0.10525 | -0.28141 | -0.14832 | -0.25463 | -0.24373 | -0.032918 | -0.07658 | 0.17805 | -0.10718 | -0.25507 | 122.9938 | 122.8662 | 122.9993 | 66.7891 | -123.2294 | 122.9039 | 123.0404 | 122.8925 | 66.7835 | -123.4022
368.8594 | 123.3261 | -66.7374 | 56.2866 | -0.0029761 | -0.003299 | 0.0015299 | 0.054577 | -0.0024592 | 0.063144 | 0.0077831 | -0.00048933 | -0.00098273 | 0.060595 | 0.011284 | 0.060658 | -66.7976 | 0.028878 | -66.746 | 56.2381 | 56.0968 | 56.2344 | -66.8467 | -66.7886 | 0.027831 | -66.8323 | 56.1482 | 56.2939 | 56.1323 | -67.0195 | -0.10931 | -0.048517 | -0.060265 | -0.008639 | 0.10067 | -0.18986 | -0.052196 | -0.28209 | -0.13844 | -0.051227 | -0.09489 | 0.1872 | 0.007268 | -0.15436 | 122.9755 | 122.8341 | 122.9718 | 66.7662 | -123.1333 | 122.8855 | 123.0313 | 122.8696 | 66.7652 | -123.3061
369.7969 | 123.2391 | -66.7877 | 56.3461 | 0.0046549 | -0.0030854 | 0.0011025 | 0.054363 | -0.0028866 | 0.063144 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060595 | 0.011284 | 0.060872 | -66.7976 | 0.0243 | -66.7414 | 56.2473 | 56.1059 | 56.2344 | -66.8467 | -66.784 | 0.023253 | -66.8185 | 56.1528 | 56.2893 | 56.1414 | -67.0195 | -0.058952 | -0.09887 | -0.009911 | 0.046293 | 0.10524 | -0.24021 | -0.11171 | -0.23174 | -0.19337 | 0.003706 | -0.030799 | 0.20094 | -0.05682 | -0.20471 | 123.035 | 122.8936 | 123.0221 | 66.812 | -123.1928 | 122.9405 | 123.077 | 122.9291 | 66.811 | -123.3656
370.7969 | 123.2117 | -66.7969 | 56.2912 | -0.010607 | -0.003299 | 0.0015299 | 0.054577 | -0.002673 | 0.063358 | -0.0074779 | -0.00091653 | -0.00076913 | 0.061022 | 0.011711 | 0.060872 | -66.7931 | 0.028878 | -66.7368 | 56.2427 | 56.0968 | 56.239 | -66.8467 | -66.7886 | 0.036989 | -66.8231 | 56.1436 | 56.2893 | 56.146 | -67.0195 | -0.049797 | -0.048517 | 0.003822 | 0.060027 | 0.10982 | -0.19443 | -0.052195 | -0.22258 | -0.1476 | 0.008282 | -0.026223 | 0.19636 | -0.001889 | -0.1452 | 123.0396 | 122.8936 | 123.0359 | 66.8258 | -123.1379 | 122.9405 | 123.0862 | 122.9429 | 66.8339 | -123.3107
371.8594 | 123.3307 | -66.7694 | 56.2912 | 0.0046549 | -0.003299 | 0.0015299 | 0.054791 | -0.002673 | 0.06293 | 0.015414 | -0.0011301 | -0.00098273 | 0.060808 | 0.011284 | 0.060658 | -66.7976 | 0.028878 | -66.7414 | 56.2427 | 56.0922 | 56.2344 | -66.8421 | -66.7794 | 0.027831 | -66.8185 | 56.1528 | 56.2893 | 56.1414 | -67.0195 | -0.072684 | -0.048517 | -0.028222 | 0.027982 | 0.10067 | -0.19901 | -0.056774 | -0.25005 | -0.13844 | -0.010027 | -0.04911 | 0.20094 | -0.001889 | -0.14978 | 123.0121 | 122.8616 | 123.0038 | 66.7983 | -123.1333 | 122.9222 | 123.0587 | 122.9108 | 66.7972 | -123.3107
372.7969 | 123.2529 | -66.8015 | 56.3324 | -0.010607 | -0.003299 | 0.0013163 | 0.054577 | -0.002673 | 0.063358 | 0.015414 | -0.00070293 | -0.00098273 | 0.061022 | 0.011498 | 0.060872 | -66.7931 | 0.0243 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8467 | -66.7932 | 0.03241 | -66.8277 | 56.1482 | 56.2802 | 56.146 | -67.0195 | -0.045219 | -0.098872 | 0.0084 | 0.055448 | 0.10067 | -0.23105 | -0.097972 | -0.21801 | -0.18422 | 0.008281 | -0.026224 | 0.19178 | -0.052244 | -0.1864 | 123.035 | 122.9028 | 123.0359 | 66.8258 | -123.1791 | 122.9496 | 123.0816 | 122.9474 | 66.8339 | -123.3519
373.7969 | 123.262 | -66.7786 | 56.3278 | 0.012286 | -0.0028718 | 0.0015299 | 0.054791 | -0.002673 | 0.063571 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060595 | 0.011498 | 0.060872 | -66.7885 | 0.033457 | -66.7506 | 56.2335 | 56.0876 | 56.2344 | -66.8513 | -66.7886 | 0.027831 | -66.8323 | 56.1482 | 56.2939 | 56.146 | -67.0195 | -0.072687 | -0.094295 | -0.009911 | 0.027981 | 0.10067 | -0.24021 | -0.093395 | -0.24089 | -0.17964 | -0.010029 | -0.053692 | 0.1872 | -0.033931 | -0.18182 | 123.0121 | 122.8662 | 123.013 | 66.812 | -123.1791 | 122.9267 | 123.0725 | 122.9246 | 66.8064 | -123.3473
374.7969 | 123.2803 | -66.7694 | 56.3141 | 0.0046549 | -0.0035128 | 0.0013163 | 0.054577 | -0.002673 | 0.063358 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060595 | 0.011498 | 0.061299 | -66.7976 | 0.038035 | -66.7414 | 56.2427 | 56.0968 | 56.239 | -66.8421 | -66.7932 | 0.027831 | -66.8231 | 56.1573 | 56.2893 | 56.146 | -67.0149 | -0.072684 | -0.071405 | -0.028222 | 0.027982 | 0.10067 | -0.21732 | -0.075083 | -0.24547 | -0.15675 | -0.023763 | -0.053689 | 0.19178 | -0.024777 | -0.16809 | 123.0121 | 122.8662 | 123.0084 | 66.8074 | -123.1562 | 122.9267 | 123.0587 | 122.9154 | 66.7972 | -123.329
375.7969 | 123.317 | -66.7603 | 56.2958 | -0.0029761 | -0.003299 | 0.0015299 | 0.054577 | -0.002673 | 0.063571 | 0.015414 | -0.00091653 | -0.00098273 | 0.060808 | 0.011498 | 0.060872 | -66.7839 | 0.028878 | -66.7414 | 56.2427 | 56.1059 | 56.239 | -66.8467 | -66.7932 | 0.023253 | -66.8277 | 56.1482 | 56.2939 | 56.1414 | -67.0195 | -0.086418 | -0.053094 | -0.023642 | 0.018827 | 0.10524 | -0.18985 | -0.056772 | -0.2592 | -0.14759 | -0.032918 | -0.067423 | 0.19178 | -0.001887 | -0.15436 | 123.0029 | 122.8662 | 122.9993 | 66.7891 | -123.1424 | 122.9084 | 123.0541 | 122.9017 | 66.7835 | -123.3152
376.8594 | 123.2849 | -66.7786 | 56.3049 | 0.0046549 | -0.003299 | 0.0011025 | 0.055004 | -0.002673 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.061022 | 0.011711 | 0.061086 | -66.7931 | 0.019721 | -66.7414 | 56.2427 | 56.0876 | 56.2436 | -66.8513 | -66.7886 | 0.027831 | -66.8277 | 56.1573 | 56.2939 | 56.1414 | -67.0195 | -0.072687 | -0.06225 | -0.014489 | 0.037137 | 0.10982 | -0.21733 | -0.061349 | -0.24089 | -0.14759 | -0.010029 | -0.049113 | 0.19178 | -0.011043 | -0.16351 | 123.0212 | 122.8662 | 123.0221 | 66.7983 | -123.1562 | 122.9359 | 123.0725 | 122.92 | 66.8064 | -123.3244
377.7969 | 123.3353 | -66.7786 | 56.2775 | -0.010607 | -0.003299 | 0.0011025 | 0.054363 | -0.002673 | 0.063358 | 0.00015261 | -0.0011301 | -0.00076913 | 0.060595 | 0.011711 | 0.061086 | -66.7885 | 0.028878 | -66.746 | 56.2427 | 56.0739 | 56.2298 | -66.8421 | -66.7886 | 0.027831 | -66.8231 | 56.1482 | 56.2893 | 56.1323 | -67.0195 | -0.063529 | -0.034784 | -0.009911 | 0.032559 | 0.096088 | -0.2036 | -0.047619 | -0.24089 | -0.12928 | -0.010029 | -0.044534 | 0.19636 | 0.011844 | -0.14521 | 123.0212 | 122.8524 | 123.0084 | 66.8074 | -123.1196 | 122.9267 | 123.0679 | 122.9108 | 66.8064 | -123.2969
378.7969 | 123.2117 | -66.806 | 56.3049 | -0.010607 | -0.003299 | 0.0013163 | 0.054363 | -0.002673 | 0.063358 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060808 | 0.011711 | 0.060872 | -66.7839 | 0.028878 | -66.7368 | 56.2335 | 56.0968 | 56.239 | -66.8467 | -66.784 | 0.03241 | -66.8231 | 56.1482 | 56.2939 | 56.1323 | -67.0149 | -0.040642 | -0.071407 | 0.022134 | 0.069182 | 0.10982 | -0.20817 | -0.065928 | -0.20885 | -0.15675 | 0.022016 | -0.017068 | 0.19178 | -0.011043 | -0.17267 | 123.0396 | 122.9028 | 123.045 | 66.8349 | -123.1516 | 122.9542 | 123.0999 | 122.9383 | 66.8384 | -123.3198
379.8594 | 123.3307 | -66.7419 | 56.3049 | 0.012286 | -0.003299 | 0.0015299 | 0.054791 | -0.002673 | 0.063358 | 0.00015261 | -0.0011301 | -0.0011965 | 0.060595 | 0.011498 | 0.060872 | -66.7931 | 0.028878 | -66.746 | 56.2381 | 56.1013 | 56.2298 | -66.8513 | -66.7932 | 0.018674 | -66.8277 | 56.1482 | 56.2847 | 56.1414 | -67.0195 | -0.10931 | -0.066828 | -0.05111 | -0.004062 | 0.10525 | -0.20359 | -0.075085 | -0.27752 | -0.15675 | -0.051229 | -0.085734 | 0.19178 | -0.020201 | -0.16351 | 122.98 | 122.8433 | 122.9718 | 66.7708 | -123.1562 | 122.8901 | 123.0267 | 122.8834 | 66.7606 | -123.3244
380.7969 | 123.3261 | -66.7236 | 56.2683 | -0.0029761 | -0.0035128 | 0.0015299 | 0.054363 | -0.002673 | 0.063358 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.011711 | 0.060658 | -66.7931 | 0.033457 | -66.7552 | 56.2381 | 56.0876 | 56.2344 | -66.8421 | -66.7932 | 0.027831 | -66.8231 | 56.1482 | 56.2847 | 56.1323 | -67.0195 | -0.11846 | -0.030207 | -0.06942 | -0.031528 | 0.086932 | -0.1807 | -0.033886 | -0.29583 | -0.12013 | -0.069539 | -0.099465 | 0.19636 | 0.01642 | -0.13605 | 122.9617 | 122.8112 | 122.9581 | 66.7571 | -123.1104 | 122.8718 | 123.0084 | 122.8559 | 66.7515 | -123.2878
381.7969 | 123.1796 | -66.8198 | 56.3141 | 0.0046549 | -0.0035128 | 0.0011025 | 0.054577 | -0.002673 | 0.063144 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060595 | 0.012139 | 0.060872 | -66.7885 | 0.0243 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8467 | -66.784 | 0.023253 | -66.8231 | 56.1482 | 56.2939 | 56.1368 | -67.024 | -0.026909 | -0.080562 | 0.031288 | 0.073758 | 0.10067 | -0.21274 | -0.079662 | -0.20427 | -0.16591 | 0.035749 | -0.003335 | 0.20094 | -0.020198 | -0.17725 | 123.0533 | 122.9211 | 123.0542 | 66.8441 | -123.1608 | 122.9679 | 123.1137 | 122.9566 | 66.843 | -123.3381
382.7969 | 123.2986 | -66.7694 | 56.2958 | -0.010607 | -0.003299 | 0.00088894 | 0.054577 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060808 | 0.011284 | 0.061086 | -66.7931 | 0.033457 | -66.746 | 56.2427 | 56.0968 | 56.2298 | -66.8558 | -66.784 | 0.023253 | -66.8277 | 56.1528 | 56.2939 | 56.146 | -67.024 | -0.086421 | -0.053094 | -0.023644 | 0.023404 | 0.10983 | -0.19901 | -0.065929 | -0.25463 | -0.14302 | -0.014605 | -0.058268 | 0.19636 | -0.001887 | -0.14978 | 123.0121 | 122.8662 | 122.9993 | 66.8029 | -123.1516 | 122.9222 | 123.0633 | 122.9154 | 66.7927 | -123.3198
383.7969 | 123.2758 | -66.7465 | 56.3461 | 0.012286 | -0.0035128 | 0.0013163 | 0.054363 | -0.0022456 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060808 | 0.011711 | 0.061086 | -66.7931 | 0.0243 | -66.746 | 56.2381 | 56.1059 | 56.239 | -66.8513 | -66.7932 | 0.027831 | -66.8323 | 56.1528 | 56.2893 | 56.1368 | -67.0195 | -0.10473 | -0.10803 | -0.046532 | 0.000516 | 0.10525 | -0.24021 | -0.10713 | -0.27294 | -0.19337 | -0.046651 | -0.085735 | 0.1872 | -0.05682 | -0.20929 | 122.9846 | 122.8524 | 122.9855 | 66.7708 | -123.1974 | 122.8993 | 123.0358 | 122.8834 | 66.7744 | -123.3656
384.8594 | 123.23 | -66.7831 | 56.3278 | -0.018238 | -0.003299 | 0.0013163 | 0.054791 | -0.002673 | 0.063144 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060808 | 0.011925 | 0.060872 | -66.7931 | 0.033457 | -66.746 | 56.2381 | 56.1105 | 56.239 | -66.8513 | -66.784 | 0.023253 | -66.8277 | 56.1528 | 56.2985 | 56.1552 | -67.0149 | -0.068109 | -0.089716 | -0.009911 | 0.037137 | 0.10525 | -0.21732 | -0.088816 | -0.23174 | -0.17506 | -0.000872 | -0.044535 | 0.1872 | -0.029353 | -0.17267 | 123.0212 | 122.8936 | 123.0221 | 66.8166 | -123.1791 | 122.9359 | 123.0816 | 122.9383 | 66.8064 | -123.3427
385.7969 | 123.3444 | -66.7557 | 56.3095 | -0.0029761 | -0.003299 | 0.0011025 | 0.055004 | -0.002673 | 0.063571 | 0.00015261 | -0.00091653 | -0.00098273 | 0.061022 | 0.011711 | 0.060872 | -66.7976 | 0.028878 | -66.7506 | 56.2381 | 56.0968 | 56.239 | -66.8421 | -66.7932 | 0.023253 | -66.8231 | 56.1528 | 56.2847 | 56.1368 | -67.0057 | -0.086417 | -0.071405 | -0.041955 | 0.005093 | 0.09151 | -0.21274 | -0.070505 | -0.25005 | -0.15675 | -0.037496 | -0.067422 | 0.18262 | -0.024778 | -0.17267 | 122.9938 | 122.8524 | 122.9947 | 66.7846 | -123.1516 | 122.9084 | 123.0404 | 122.8925 | 66.7789 | -123.3152
386.7969 | 123.2437 | -66.8015 | 56.3004 | 0.0046549 | -0.003299 | 0.0011025 | 0.054363 | -0.002673 | 0.06293 | 0.0077831 | -0.00070293 | -0.00098273 | 0.061022 | 0.011711 | 0.061086 | -66.7885 | 0.028878 | -66.7323 | 56.2335 | 56.0784 | 56.239 | -66.8467 | -66.784 | 0.023253 | -66.8231 | 56.139 | 56.2893 | 56.1414 | -67.0195 | -0.045219 | -0.066829 | 0.012978 | 0.069183 | 0.1144 | -0.22191 | -0.06135 | -0.21801 | -0.16133 | 0.017439 | -0.021645 | 0.19636 | -0.011044 | -0.15894 | 123.035 | 122.8799 | 123.0405 | 66.8303 | -123.147 | 122.9405 | 123.0908 | 122.9429 | 66.8247 | -123.3198
387.7969 | 123.349 | -66.7648 | 56.2454 | -0.0029761 | -0.0037264 | 0.0015299 | 0.054791 | -0.002673 | 0.063144 | 0.0077831 | -0.00091653 | -0.00076913 | 0.060595 | 0.011711 | 0.061086 | -66.7885 | 0.033457 | -66.7323 | 56.2381 | 56.1013 | 56.2344 | -66.8284 | -66.7794 | 0.03241 | -66.8231 | 56.1573 | 56.2893 | 56.1323 | -67.0149 | -0.063524 | -0.007318 | -0.023643 | 0.032562 | 0.096086 | -0.14408 | -0.010997 | -0.25005 | -0.088083 | -0.014604 | -0.058266 | 0.19178 | 0.043888 | -0.11316 | 123.0029 | 122.8662 | 122.9993 | 66.7983 | -123.0738 | 122.9222 | 123.0541 | 122.8971 | 66.7972 | -123.2603
388.8594 | 123.2117 | -66.7877 | 56.3232 | 0.0046549 | -0.0035128 | 0.0015299 | 0.054577 | -0.0031002 | 0.063358 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060808 | 0.012352 | 0.060872 | -66.7931 | 0.038035 | -66.7414 | 56.2335 | 56.0968 | 56.2436 | -66.8513 | -66.7749 | 0.027831 | -66.8277 | 56.1482 | 56.2893 | 56.1414 | -67.0195 | -0.063531 | -0.089717 | -0.005333 | 0.046293 | 0.10982 | -0.22648 | -0.079659 | -0.23174 | -0.17506 | 0.012863 | -0.039957 | 0.19178 | -0.033932 | -0.18182 | 123.0212 | 122.8845 | 123.0313 | 66.8258 | -123.1745 | 122.9359 | 123.077 | 122.9291 | 66.8156 | -123.3427
389.7969 | 123.3215 | -66.7511 | 56.25 | -0.0029761 | -0.0035128 | 0.0013163 | 0.054577 | -0.002673 | 0.063358 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060381 | 0.011711 | 0.061086 | -66.7931 | 0.033457 | -66.7414 | 56.2381 | 56.0922 | 56.239 | -66.8421 | -66.7886 | 0.027831 | -66.8185 | 56.1528 | 56.2939 | 56.1506 | -67.0195 | -0.090994 | -0.011896 | -0.041954 | 0.009672 | 0.10067 | -0.15781 | -0.010996 | -0.26836 | -0.09724 | -0.037494 | -0.06742 | 0.20094 | 0.043889 | -0.099425 | 122.9892 | 122.8433 | 122.9901 | 66.7846 | -123.0921 | 122.9039 | 123.045 | 122.9017 | 66.7789 | -123.2695
390.875 | 123.2025 | -66.7831 | 56.3187 | -0.010607 | -0.0035128 | 0.0011025 | 0.054363 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060595 | 0.012139 | 0.060872 | -66.7931 | 0.038035 | -66.746 | 56.2381 | 56.1059 | 56.239 | -66.8513 | -66.784 | 0.027831 | -66.8277 | 56.1482 | 56.2893 | 56.1414 | -67.024 | -0.068109 | -0.080561 | -0.009911 | 0.037137 | 0.10525 | -0.21274 | -0.079661 | -0.2409 | -0.17048 | -0.000872 | -0.044535 | 0.19636 | -0.029355 | -0.17725 | 123.0212 | 122.8891 | 123.0221 | 66.8212 | -123.1699 | 122.9313 | 123.0725 | 122.9246 | 66.811 | -123.3427
391.7969 | 123.3902 | -66.7603 | 56.3004 | -0.0029761 | -0.0037264 | 0.0017435 | 0.054363 | -0.0024592 | 0.063144 | 0.0077831 | -0.0011301 | -0.00076913 | 0.060808 | 0.011711 | 0.060658 | -66.7885 | 0.028878 | -66.7414 | 56.2289 | 56.0968 | 56.239 | -66.8421 | -66.784 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.1277 | -67.0195 | -0.081839 | -0.071407 | -0.028221 | 0.018827 | 0.10067 | -0.20359 | -0.06135 | -0.2592 | -0.15217 | -0.02376 | -0.062844 | 0.19636 | -0.011044 | -0.17267 | 122.9892 | 122.857 | 122.9993 | 66.7891 | -123.1424 | 122.9084 | 123.0496 | 122.8879 | 66.7835 | -123.3198
392.7969 | 123.3307 | -66.7648 | 56.3004 | -0.0029761 | -0.0030854 | 0.0015299 | 0.054363 | -0.0028866 | 0.063144 | 0.015414 | -0.00070293 | -0.00098273 | 0.060808 | 0.011711 | 0.060872 | -66.7931 | 0.0243 | -66.7506 | 56.2335 | 56.0968 | 56.2253 | -66.8467 | -66.7886 | 0.03241 | -66.8277 | 56.1482 | 56.2893 | 56.1506 | -67.0149 | -0.08184 | -0.066829 | -0.028221 | 0.014249 | 0.096089 | -0.20359 | -0.075086 | -0.25005 | -0.15217 | -0.023761 | -0.062845 | 0.1872 | -0.011044 | -0.14978 | 122.9984 | 122.8616 | 122.9901 | 66.7891 | -123.147 | 122.913 | 123.0541 | 122.9154 | 66.7972 | -123.3152
393.7969 | 123.3307 | -66.7694 | 56.2729 | -0.0029761 | -0.0035128 | 0.00088894 | 0.054791 | -0.002673 | 0.063358 | -0.015108 | -0.0011301 | -0.0011965 | 0.060381 | 0.012139 | 0.060872 | -66.7885 | 0.028878 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8467 | -66.7886 | 0.027831 | -66.8139 | 56.1528 | 56.2985 | 56.146 | -67.0195 | -0.077263 | -0.039363 | -0.019066 | 0.023404 | 0.10067 | -0.17155 | -0.038463 | -0.25005 | -0.12013 | -0.019184 | -0.044532 | 0.20552 | 0.025579 | -0.12689 | 123.0029 | 122.8708 | 123.0038 | 66.7983 | -123.1196 | 122.9222 | 123.0679 | 122.9154 | 66.7972 | -123.2923
394.7969 | 123.2666 | -66.774 | 56.2912 | 0.0046549 | -0.0035128 | 0.0013163 | 0.055218 | -0.0031002 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060595 | 0.011925 | 0.060658 | -66.8022 | 0.033457 | -66.7414 | 56.2427 | 56.0922 | 56.2298 | -66.8513 | -66.7886 | 0.023253 | -66.8277 | 56.1528 | 56.2847 | 56.1368 | -67.024 | -0.077264 | -0.048517 | -0.028223 | 0.03256 | 0.10982 | -0.19901 | -0.061352 | -0.25005 | -0.13844 | -0.014606 | -0.05369 | 0.19636 | -0.006468 | -0.15436 | 123.0167 | 122.8662 | 123.0038 | 66.8074 | -123.1424 | 122.9267 | 123.0587 | 122.9108 | 66.7972 | -123.3152
395.7969 | 123.3673 | -66.7145 | 56.3324 | 0.0046549 | -0.0037264 | 0.0011025 | 0.054577 | -0.0024592 | 0.063358 | 0.023044 | -0.00070293 | -0.00098273 | 0.060808 | 0.012139 | 0.060872 | -66.7885 | 0.0243 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8421 | -66.784 | 0.027831 | -66.8277 | 56.1528 | 56.2893 | 56.1277 | -67.0195 | -0.12762 | -0.098872 | -0.073997 | -0.031527 | 0.096088 | -0.23105 | -0.097972 | -0.30498 | -0.17964 | -0.069536 | -0.1132 | 0.19178 | -0.043087 | -0.20472 | 122.948 | 122.8158 | 122.9489 | 66.7388 | -123.1745 | 122.8672 | 123.0038 | 122.8422 | 66.7423 | -123.3519
396.8594 | 123.1888 | -66.7877 | 56.3232 | -0.0029761 | -0.0035128 | 0.0011025 | 0.054149 | -0.002673 | 0.063358 | -0.0074779 | -0.00048933 | -0.0011965 | 0.060595 | 0.012352 | 0.060872 | -66.7839 | 0.028878 | -66.7414 | 56.2381 | 56.0922 | 56.239 | -66.8513 | -66.7794 | 0.03241 | -66.8231 | 56.1619 | 56.2939 | 56.146 | -67.0195 | -0.063531 | -0.085138 | 0.003824 | 0.046293 | 0.10982 | -0.23106 | -0.084238 | -0.23174 | -0.16132 | 0.008284 | -0.035378 | 0.19636 | -0.029353 | -0.17725 | 123.0258 | 122.8799 | 123.0267 | 66.8166 | -123.1745 | 122.9496 | 123.0816 | 122.9337 | 66.8201 | -123.3427
397.7969 | 123.3215 | -66.7648 | 56.3004 | -0.0029761 | -0.0035128 | 0.0015299 | 0.054791 | -0.0028866 | 0.063144 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060808 | 0.011925 | 0.061086 | -66.7931 | 0.033457 | -66.746 | 56.2427 | 56.1013 | 56.2344 | -66.8375 | -66.7886 | 0.036989 | -66.8185 | 56.1573 | 56.2893 | 56.1323 | -67.024 | -0.072682 | -0.057672 | -0.028221 | 0.018827 | 0.091509 | -0.19901 | -0.065929 | -0.25921 | -0.14301 | -0.023761 | -0.053687 | 0.20552 | -0.011044 | -0.16809 | 123.0075 | 122.8662 | 122.9993 | 66.7983 | -123.1379 | 122.9222 | 123.0541 | 122.8971 | 66.8018 | -123.3244
398.8594 | 123.1796 | -66.7831 | 56.3187 | -0.0029761 | -0.0035128 | 0.0015299 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.00048933 | -0.00055553 | 0.060595 | 0.012139 | 0.060658 | -66.7931 | 0.028878 | -66.7414 | 56.2381 | 56.1105 | 56.2344 | -66.8558 | -66.784 | 0.03241 | -66.8231 | 56.1482 | 56.2893 | 56.1368 | -67.0286 | -0.072688 | -0.080561 | -0.009911 | 0.041715 | 0.1144 | -0.20817 | -0.08424 | -0.24547 | -0.17048 | -0.000872 | -0.039956 | 0.20552 | -0.029355 | -0.18183 | 123.0212 | 122.8936 | 123.0176 | 66.812 | -123.1745 | 122.9313 | 123.0725 | 122.92 | 66.8156 | -123.3473
399.7969 | 123.2574 | -66.7694 | 56.3187 | -0.010607 | -0.0035128 | 0.0013163 | 0.054577 | -0.002673 | 0.063144 | 0.0077831 | -0.00070293 | -0.00055553 | 0.060595 | 0.011925 | 0.060658 | -66.7885 | 0.019721 | -66.746 | 56.2381 | 56.1013 | 56.2436 | -66.8421 | -66.7886 | 0.03241 | -66.8277 | 56.1528 | 56.2939 | 56.1368 | -67.0195 | -0.072684 | -0.080561 | -0.019066 | 0.023404 | 0.096088 | -0.21732 | -0.075082 | -0.25005 | -0.16591 | -0.019184 | -0.058268 | 0.19178 | -0.024776 | -0.18183 | 123.0075 | 122.8708 | 123.013 | 66.7891 | -123.1608 | 122.9222 | 123.0633 | 122.9062 | 66.8018 | -123.3381
400.875 | 123.3032 | -66.7694 | 56.2912 | 0.0046549 | -0.003299 | 0.0013163 | 0.054791 | -0.0028866 | 0.063358 | 0.0077831 | -0.0011301 | -0.00076913 | 0.061022 | 0.012352 | 0.060872 | -66.7885 | 0.033457 | -66.7414 | 56.2381 | 56.1013 | 56.2436 | -66.8513 | -66.784 | 0.023253 | -66.8231 | 56.1482 | 56.2985 | 56.1506 | -67.024 | -0.081842 | -0.053095 | -0.019066 | 0.027982 | 0.10982 | -0.18986 | -0.047616 | -0.25463 | -0.14302 | -0.014605 | -0.053689 | 0.20094 | 0.007268 | -0.14062 | 123.0075 | 122.8708 | 123.013 | 66.8029 | -123.1424 | 122.9176 | 123.0679 | 122.92 | 66.7927 | -123.3152
401.7969 | 123.3353 | -66.7419 | 56.3004 | -0.0029761 | -0.0037264 | 0.0013163 | 0.054791 | -0.0024592 | 0.063358 | 0.0077831 | -0.00027553 | -0.00076913 | 0.060595 | 0.012139 | 0.060658 | -66.7931 | 0.028878 | -66.7414 | 56.2335 | 56.1013 | 56.239 | -66.8467 | -66.7794 | 0.027831 | -66.8185 | 56.1436 | 56.2893 | 56.1277 | -67.0195 | -0.10473 | -0.066829 | -0.05111 | 0.000516 | 0.10524 | -0.19901 | -0.06135 | -0.27752 | -0.15675 | -0.037493 | -0.076576 | 0.20094 | -0.011044 | -0.17267 | 122.9755 | 122.8433 | 122.9809 | 66.7708 | -123.147 | 122.8855 | 123.0313 | 122.8696 | 66.7698 | -123.3198
402.7969 | 123.2208 | -66.7465 | 56.3507 | -0.0029761 | -0.0037264 | 0.0013163 | 0.054577 | -0.0024592 | 0.063358 | 0.0077831 | -0.00048933 | -0.0011965 | 0.060808 | 0.011925 | 0.060658 | -66.7976 | 0.033457 | -66.746 | 56.2381 | 56.1013 | 56.239 | -66.8421 | -66.784 | 0.036989 | -66.8277 | 56.1528 | 56.2847 | 56.1368 | -67.0195 | -0.095572 | -0.1126 | -0.05111 | 0.000516 | 0.096088 | -0.24937 | -0.1117 | -0.27294 | -0.19795 | -0.037493 | -0.081156 | 0.19178 | -0.065977 | -0.21387 | 122.9846 | 122.8479 | 122.9855 | 66.78 | -123.1928 | 122.8993 | 123.0313 | 122.8834 | 66.7835 | -123.3702
403.8594 | 123.3444 | -66.7465 | 56.2729 | 0.012286 | -0.0037264 | 0.0011025 | 0.054577 | -0.0028866 | 0.063358 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.012139 | 0.060872 | -66.7885 | 0.033457 | -66.7506 | 56.2335 | 56.0922 | 56.239 | -66.8421 | -66.784 | 0.023253 | -66.8277 | 56.1573 | 56.2939 | 56.1368 | -67.0149 | -0.095572 | -0.039363 | -0.041954 | -0.004062 | 0.09151 | -0.1807 | -0.033884 | -0.26836 | -0.11555 | -0.037493 | -0.081156 | 0.1872 | 0.021001 | -0.13605 | 122.98 | 122.8387 | 122.9855 | 66.78 | -123.115 | 122.9039 | 123.0404 | 122.8834 | 66.7698 | -123.2878
404.7969 | 123.3124 | -66.7465 | 56.3141 | 0.0046549 | -0.0037264 | 0.0011025 | 0.054577 | -0.002673 | 0.063358 | 0.015414 | -0.00070293 | -0.00076913 | 0.060595 | 0.011925 | 0.060658 | -66.7885 | 0.038035 | -66.7414 | 56.2381 | 56.083 | 56.239 | -66.8467 | -66.784 | 0.018674 | -66.8277 | 56.1528 | 56.2939 | 56.1368 | -67.0149 | -0.10015 | -0.075983 | -0.041954 | 0.005094 | 0.10524 | -0.23106 | -0.075083 | -0.26836 | -0.16133 | -0.037493 | -0.081156 | 0.1872 | -0.020198 | -0.17725 | 122.9846 | 122.8295 | 122.9855 | 66.7846 | -123.1608 | 122.8993 | 123.0404 | 122.8834 | 66.7652 | -123.329
405.7969 | 123.2986 | -66.7648 | 56.3049 | -0.0029761 | -0.0035128 | 0.0011025 | 0.054149 | -0.002673 | 0.063144 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060808 | 0.012352 | 0.060658 | -66.7885 | 0.038035 | -66.7414 | 56.2381 | 56.0968 | 56.2344 | -66.8467 | -66.784 | 0.023253 | -66.8185 | 56.1482 | 56.2939 | 56.1323 | -67.0195 | -0.08184 | -0.066828 | -0.023643 | 0.023405 | 0.10524 | -0.20817 | -0.070507 | -0.25463 | -0.15675 | -0.019182 | -0.053687 | 0.20094 | -0.011043 | -0.17267 | 123.0029 | 122.8616 | 122.9993 | 66.8029 | -123.1516 | 122.913 | 123.0587 | 122.8971 | 66.7881 | -123.3244
406.7969 | 123.3261 | -66.7236 | 56.3187 | 0.0046549 | -0.0035128 | 0.0011025 | 0.054363 | -0.002673 | 0.063144 | 0.015414 | -0.00048933 | -0.0014101 | 0.060595 | 0.012566 | 0.060658 | -66.7885 | 0.0243 | -66.7506 | 56.2381 | 56.1059 | 56.2344 | -66.8513 | -66.7886 | 0.023253 | -66.8185 | 56.1528 | 56.2893 | 56.1277 | -67.0195 | -0.12762 | -0.080561 | -0.064842 | -0.02695 | 0.10067 | -0.21274 | -0.08424 | -0.29583 | -0.16591 | -0.06496 | -0.094886 | 0.20094 | -0.029355 | -0.19098 | 122.9617 | 122.8296 | 122.9581 | 66.7479 | -123.1699 | 122.8764 | 123.0129 | 122.8513 | 66.7469 | -123.3381
407.8594 | 123.3582 | -66.7282 | 56.3049 | 0.012286 | -0.0037264 | 0.0015299 | 0.054577 | -0.0028866 | 0.063144 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060595 | 0.012139 | 0.060872 | -66.7885 | 0.033457 | -66.7552 | 56.2427 | 56.0922 | 56.2436 | -66.8421 | -66.784 | 0.023253 | -66.8277 | 56.1482 | 56.2893 | 56.1277 | -67.0149 | -0.11388 | -0.06225 | -0.060265 | -0.026951 | 0.086932 | -0.21275 | -0.061349 | -0.28667 | -0.15675 | -0.055804 | -0.099467 | 0.1872 | -0.015622 | -0.17725 | 122.9709 | 122.8204 | 122.9718 | 66.7617 | -123.147 | 122.8764 | 123.0175 | 122.8559 | 66.7515 | -123.3198
408.7969 | 123.2025 | -66.7465 | 56.337 | 0.0046549 | -0.0037264 | 0.0013163 | 0.054363 | -0.0024592 | 0.063358 | 0.00015261 | -0.0013437 | -0.00098273 | 0.060595 | 0.012139 | 0.060658 | -66.7931 | 0.033457 | -66.7414 | 56.2335 | 56.0968 | 56.2436 | -66.8467 | -66.784 | 0.023253 | -66.8277 | 56.139 | 56.2985 | 56.1414 | -67.0195 | -0.10015 | -0.10345 | -0.046532 | 0.005094 | 0.10524 | -0.24021 | -0.093392 | -0.27294 | -0.19795 | -0.037493 | -0.081156 | 0.19178 | -0.038508 | -0.19556 | 122.98 | 122.8433 | 122.9901 | 66.78 | -123.1836 | 122.8855 | 123.045 | 122.8879 | 66.7698 | -123.3564
409.7969 | 123.2803 | -66.7236 | 56.3232 | 0.0046549 | -0.0035128 | 0.0017435 | 0.054363 | -0.002673 | 0.063358 | 0.015414 | -0.00091653 | -0.00076913 | 0.060595 | 0.011925 | 0.060872 | -66.7839 | 0.033457 | -66.7414 | 56.2381 | 56.1105 | 56.2298 | -66.8467 | -66.784 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.1414 | -67.0195 | -0.12304 | -0.085138 | -0.060263 | -0.017794 | 0.10524 | -0.21274 | -0.093395 | -0.29583 | -0.17506 | -0.060381 | -0.099465 | 0.19636 | -0.033932 | -0.18182 | 122.9617 | 122.8341 | 122.9535 | 66.7571 | -123.1699 | 122.8718 | 123.0129 | 122.8651 | 66.7469 | -123.3427
410.7969 | 123.2437 | -66.7969 | 56.3141 | 0.0046549 | -0.0037264 | 0.0011025 | 0.054577 | -0.002673 | 0.063358 | -0.0074779 | -0.0011301 | -0.0011965 | 0.060381 | 0.012352 | 0.060872 | -66.7885 | 0.028878 | -66.746 | 56.2335 | 56.1013 | 56.2344 | -66.8513 | -66.7886 | 0.03241 | -66.8231 | 56.1436 | 56.2893 | 56.146 | -67.024 | -0.054376 | -0.080562 | 0.0084 | 0.05087 | 0.10525 | -0.21274 | -0.079662 | -0.22716 | -0.17048 | 0.008282 | -0.026223 | 0.20094 | -0.024777 | -0.16809 | 123.0304 | 122.8982 | 123.0313 | 66.8258 | -123.1653 | 122.9405 | 123.0862 | 122.9429 | 66.8293 | -123.3381
411.7969 | 123.3398 | -66.7328 | 56.2866 | 0.012286 | -0.0039402 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | 0.015414 | -0.00048933 | -0.0016237 | 0.060381 | 0.012352 | 0.060872 | -66.7839 | 0.028878 | -66.7368 | 56.2335 | 56.0968 | 56.239 | -66.8421 | -66.7794 | 0.023253 | -66.8277 | 56.1482 | 56.2893 | 56.146 | -67.024 | -0.10931 | -0.053096 | -0.051108 | -0.00406 | 0.10525 | -0.18986 | -0.047617 | -0.29125 | -0.13844 | -0.046648 | -0.094889 | 0.19636 | 0.002689 | -0.14062 | 122.9663 | 122.8296 | 122.9718 | 66.7617 | -123.1287 | 122.881 | 123.0221 | 122.8788 | 66.756 | -123.3107
412.7969 | 123.2529 | -66.7419 | 56.3278 | -0.010607 | -0.0035128 | 0.0015299 | 0.054577 | -0.0031002 | 0.063144 | -0.0074779 | -0.0011301 | -0.0011965 | 0.060808 | 0.012139 | 0.060872 | -66.7885 | 0.033457 | -66.7414 | 56.2381 | 56.1105 | 56.239 | -66.8513 | -66.784 | 0.018674 | -66.8185 | 56.1482 | 56.2893 | 56.1506 | -67.024 | -0.10931 | -0.089716 | -0.046532 | 0.000516 | 0.10982 | -0.21732 | -0.088816 | -0.28209 | -0.17964 | -0.042071 | -0.076576 | 0.20552 | -0.03851 | -0.17724 | 122.98 | 122.8524 | 122.9809 | 66.7754 | -123.1791 | 122.8901 | 123.0313 | 122.8925 | 66.7606 | -123.3519
413.8594 | 123.3032 | -66.7557 | 56.2958 | -0.0029761 | -0.0039402 | 0.00088894 | 0.054791 | -0.0024592 | 0.063358 | 0.015414 | -0.00091653 | -0.00098273 | 0.060808 | 0.012352 | 0.060658 | -66.7931 | 0.0243 | -66.7368 | 56.2335 | 56.0922 | 56.2436 | -66.8513 | -66.784 | 0.027831 | -66.8185 | 56.1482 | 56.2939 | 56.1368 | -67.024 | -0.095575 | -0.062251 | -0.037377 | 0.018828 | 0.1144 | -0.20359 | -0.052193 | -0.26836 | -0.14759 | -0.028338 | -0.062843 | 0.20552 | -0.001887 | -0.15894 | 122.9892 | 122.8479 | 122.9993 | 66.78 | -123.147 | 122.9039 | 123.0496 | 122.8925 | 66.7835 | -123.3198
414.7969 | 123.2483 | -66.7236 | 56.3278 | 0.0046549 | -0.0041538 | 0.0013163 | 0.055004 | -0.002673 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060381 | 0.012139 | 0.060658 | -66.7885 | 0.019721 | -66.746 | 56.2381 | 56.1059 | 56.2344 | -66.8467 | -66.7932 | 0.018674 | -66.8231 | 56.1528 | 56.2802 | 56.1368 | -67.0195 | -0.12304 | -0.089716 | -0.064842 | -0.022372 | 0.10067 | -0.2219 | -0.093395 | -0.29583 | -0.17506 | -0.069539 | -0.099465 | 0.19636 | -0.047667 | -0.19098 | 122.9617 | 122.8296 | 122.9581 | 66.7434 | -123.1745 | 122.8764 | 123.0038 | 122.8605 | 66.7423 | -123.3473
415.875 | 123.2117 | -66.7831 | 56.3416 | -0.0029761 | -0.0037264 | 0.0015299 | 0.054577 | -0.002673 | 0.063144 | 0.015414 | -0.00091653 | -0.00098273 | 0.060595 | 0.012139 | 0.061086 | -66.7885 | 0.033457 | -66.746 | 56.2381 | 56.0968 | 56.2344 | -66.8558 | -66.7794 | 0.027831 | -66.8231 | 56.1528 | 56.2893 | 56.1323 | -67.0195 | -0.072688 | -0.10345 | -0.005333 | 0.037137 | 0.10983 | -0.24479 | -0.10713 | -0.23632 | -0.18879 | 0.003706 | -0.039956 | 0.19636 | -0.052243 | -0.20929 | 123.0212 | 122.8799 | 123.0176 | 66.8166 | -123.1974 | 122.9359 | 123.0725 | 122.9154 | 66.811 | -123.361
416.7969 | 123.2803 | -66.774 | 56.3416 | -0.0029761 | -0.0039402 | 0.0013163 | 0.054363 | -0.002673 | 0.063144 | 0.0077831 | -0.00070293 | -0.0011965 | 0.061022 | 0.011925 | 0.061086 | -66.7885 | 0.028878 | -66.746 | 56.2381 | 56.1059 | 56.239 | -66.8375 | -66.7886 | 0.018674 | -66.8277 | 56.1482 | 56.2893 | 56.1277 | -67.024 | -0.063527 | -0.10345 | -0.014488 | 0.027982 | 0.091509 | -0.23563 | -0.10255 | -0.25005 | -0.19337 | -0.014606 | -0.05369 | 0.19636 | -0.052243 | -0.21387 | 123.0121 | 122.8799 | 123.013 | 66.8029 | -123.1791 | 122.9222 | 123.0633 | 122.9017 | 66.7927 | -123.3656
417.7969 | 123.1705 | -66.7923 | 56.3232 | -0.0029761 | -0.0037264 | 0.0013163 | 0.054363 | -0.002673 | 0.063144 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060381 | 0.012352 | 0.060658 | -66.7931 | 0.028878 | -66.7368 | 56.2427 | 56.0968 | 56.239 | -66.8467 | -66.784 | 0.018674 | -66.8139 | 56.1528 | 56.2939 | 56.146 | -67.0195 | -0.054375 | -0.08056 | -0.000756 | 0.055449 | 0.10982 | -0.22648 | -0.084238 | -0.22716 | -0.17048 | 0.008283 | -0.021644 | 0.20552 | -0.029353 | -0.17725 | 123.035 | 122.8891 | 123.0313 | 66.8212 | -123.1699 | 122.9451 | 123.0862 | 122.9383 | 66.811 | -123.3427
418.7969 | 123.2758 | -66.7648 | 56.3187 | 0.0046549 | -0.0037264 | 0.0015299 | 0.054149 | -0.0028866 | 0.063358 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.012566 | 0.061086 | -66.7885 | 0.0243 | -66.746 | 56.2335 | 56.1013 | 56.239 | -66.8513 | -66.784 | 0.027831 | -66.8185 | 56.1573 | 56.2939 | 56.1506 | -67.024 | -0.086419 | -0.08514 | -0.023643 | 0.018827 | 0.10525 | -0.21732 | -0.079661 | -0.25921 | -0.16133 | -0.019182 | -0.053687 | 0.20552 | -0.024776 | -0.16809 | 122.9984 | 122.8662 | 123.0038 | 66.7891 | -123.1699 | 122.9222 | 123.0587 | 122.9154 | 66.7927 | -123.3427
419.8594 | 123.2895 | -66.7694 | 56.3187 | 0.0046549 | -0.0037264 | 0.0013163 | 0.054363 | -0.002673 | 0.06293 | 0.015414 | -0.00048933 | -0.00076913 | 0.060381 | 0.012139 | 0.060658 | -66.7885 | 0.028878 | -66.7368 | 56.2244 | 56.1105 | 56.2436 | -66.8238 | -66.784 | 0.023253 | -66.8231 | 56.1482 | 56.2893 | 56.146 | -67.0195 | -0.054368 | -0.094297 | -0.019066 | 0.032561 | 0.086929 | -0.20817 | -0.075082 | -0.25005 | -0.17048 | -0.014605 | -0.053689 | 0.19636 | -0.029355 | -0.17267 | 122.9938 | 122.8799 | 123.013 | 66.7983 | -123.1424 | 122.9176 | 123.0587 | 122.9154 | 66.7927 | -123.3381
420.7969 | 123.2071 | -66.7969 | 56.3095 | -0.010607 | -0.0035128 | 0.0013163 | 0.054363 | -0.0028866 | 0.063358 | 0.00015261 | -0.00091653 | -0.00076913 | 0.060167 | 0.012139 | 0.060445 | -66.7885 | 0.028878 | -66.746 | 56.2335 | 56.1013 | 56.2436 | -66.8513 | -66.784 | 0.027831 | -66.8323 | 56.1573 | 56.2939 | 56.1368 | -67.0332 | -0.054376 | -0.075984 | 0.0084 | 0.05087 | 0.10525 | -0.20817 | -0.065926 | -0.23632 | -0.15217 | 0.012861 | -0.035381 | 0.20094 | -0.01562 | -0.17267 | 123.0304 | 122.8982 | 123.0405 | 66.8258 | -123.1608 | 122.9542 | 123.0908 | 122.9337 | 66.8247 | -123.3427
421.8594 | 123.2391 | -66.7877 | 56.3324 | -0.0029761 | -0.0035128 | 0.0011025 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060595 | 0.012566 | 0.060658 | -66.7885 | 0.0243 | -66.746 | 56.2335 | 56.0922 | 56.239 | -66.8513 | -66.7749 | 0.03241 | -66.8231 | 56.1482 | 56.2893 | 56.1323 | -67.024 | -0.063531 | -0.098872 | -0.000755 | 0.041715 | 0.10525 | -0.24021 | -0.093393 | -0.23632 | -0.18422 | 0.012863 | -0.035378 | 0.20094 | -0.043087 | -0.20014 | 123.0212 | 122.8799 | 123.0267 | 66.812 | -123.1836 | 122.9359 | 123.077 | 122.92 | 66.8201 | -123.3564
422.7969 | 123.2162 | -66.7969 | 56.3187 | 0.0046549 | -0.0039402 | 0.0013163 | 0.054363 | -0.0028866 | 0.063358 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060381 | 0.012566 | 0.060872 | -66.7839 | 0.033457 | -66.746 | 56.2381 | 56.1059 | 56.2436 | -66.8467 | -66.784 | 0.027831 | -66.8231 | 56.1482 | 56.2893 | 56.146 | -67.0195 | -0.049797 | -0.080561 | 0.012979 | 0.05087 | 0.10067 | -0.21274 | -0.075082 | -0.22258 | -0.17048 | 0.012861 | -0.026223 | 0.19636 | -0.029355 | -0.17267 | 123.035 | 122.9028 | 123.0405 | 66.8303 | -123.1653 | 122.9451 | 123.0862 | 122.9429 | 66.8247 | -123.3381
423.7969 | 123.2574 | -66.7694 | 56.3095 | -0.0029761 | -0.0037264 | 0.0015299 | 0.054363 | -0.0028866 | 0.063358 | -0.0074779 | -0.0013437 | -0.0014101 | 0.060595 | 0.01278 | 0.060872 | -66.7839 | 0.028878 | -66.7414 | 56.2335 | 56.0968 | 56.2436 | -66.8467 | -66.7886 | 0.027831 | -66.8185 | 56.1482 | 56.2847 | 56.1368 | -67.0195 | -0.077263 | -0.075984 | -0.014487 | 0.027982 | 0.10524 | -0.21274 | -0.065926 | -0.25005 | -0.16133 | -0.019184 | -0.04911 | 0.20094 | -0.024778 | -0.17267 | 123.0029 | 122.8662 | 123.013 | 66.7983 | -123.1562 | 122.9176 | 123.0541 | 122.9062 | 66.7972 | -123.329
424.7969 | 123.2025 | -66.7786 | 56.3095 | -0.0029761 | -0.0035128 | 0.0015299 | 0.054577 | -0.0028866 | 0.063358 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060595 | 0.012139 | 0.060872 | -66.7839 | 0.033457 | -66.7506 | 56.2427 | 56.1013 | 56.2344 | -66.8558 | -66.7794 | 0.027831 | -66.8277 | 56.1482 | 56.2847 | 56.1506 | -67.0195 | -0.077266 | -0.066827 | -0.005332 | 0.027981 | 0.10525 | -0.20817 | -0.075084 | -0.24089 | -0.16133 | -0.000872 | -0.049113 | 0.19178 | -0.024778 | -0.15893 | 123.0212 | 122.8799 | 123.013 | 66.812 | -123.1653 | 122.9267 | 123.0633 | 122.9291 | 66.8064 | -123.329
425.7969 | 123.1888 | -66.8152 | 56.3461 | -0.010607 | -0.0041538 | 0.0015299 | 0.054577 | -0.002673 | 0.063144 | 0.015414 | -0.0011301 | -0.0011965 | 0.060808 | 0.012352 | 0.060658 | -66.7839 | 0.033457 | -66.7323 | 56.2335 | 56.1105 | 56.2436 | -66.8558 | -66.784 | 0.027831 | -66.8185 | 56.1482 | 56.2847 | 56.1368 | -67.0195 | -0.040644 | -0.11261 | 0.03129 | 0.082916 | 0.12356 | -0.23563 | -0.10255 | -0.20427 | -0.19795 | 0.031172 | -0.003333 | 0.20094 | -0.061399 | -0.20929 | 123.0487 | 122.9257 | 123.0588 | 66.8486 | -123.202 | 122.9634 | 123.0999 | 122.952 | 66.843 | -123.3656
426.8594 | 123.2117 | -66.774 | 56.3553 | 0.0046549 | -0.0037264 | 0.0013163 | 0.054363 | -0.002673 | 0.063144 | 0.015414 | -0.0011301 | -0.0011965 | 0.060381 | 0.012139 | 0.060658 | -66.7931 | 0.028878 | -66.7368 | 56.2427 | 56.1105 | 56.2436 | -66.8421 | -66.784 | 0.027831 | -66.8185 | 56.1482 | 56.2939 | 56.1368 | -67.0195 | -0.068106 | -0.1126 | -0.019066 | 0.037139 | 0.10525 | -0.24479 | -0.1117 | -0.24547 | -0.2071 | -0.010027 | -0.044532 | 0.20094 | -0.061397 | -0.21845 | 123.0167 | 122.8845 | 123.0176 | 66.8029 | -123.1974 | 122.9222 | 123.0679 | 122.9108 | 66.8018 | -123.3747
427.7969 | 123.2117 | -66.7877 | 56.3461 | -0.0029761 | -0.0035128 | 0.0011025 | 0.054577 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.012352 | 0.060658 | -66.7839 | 0.038035 | -66.746 | 56.2335 | 56.1059 | 56.239 | -66.8467 | -66.7886 | 0.018674 | -66.8277 | 56.1482 | 56.2939 | 56.146 | -67.0195 | -0.058952 | -0.11261 | 0.003824 | 0.041715 | 0.10067 | -0.24021 | -0.10713 | -0.23174 | -0.19795 | -0.000873 | -0.039957 | 0.19178 | -0.052241 | -0.20013 | 123.0212 | 122.8936 | 123.0267 | 66.8258 | -123.1928 | 122.9359 | 123.0816 | 122.9337 | 66.8064 | -123.3656
428.7969 | 123.175 | -66.7923 | 56.2729 | -0.010607 | -0.0041538 | 0.0013163 | 0.054577 | -0.0028866 | 0.063358 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060381 | 0.012566 | 0.060445 | -66.7885 | 0.028878 | -66.746 | 56.2427 | 56.1059 | 56.2436 | -66.8467 | -66.784 | 0.03241 | -66.8277 | 56.1528 | 56.2985 | 56.1368 | -67.0195 | -0.054375 | -0.030206 | 0.003822 | 0.046292 | 0.10067 | -0.16697 | -0.029305 | -0.22716 | -0.12013 | 0.008283 | -0.03538 | 0.19178 | 0.025579 | -0.13605 | 123.035 | 122.8982 | 123.0359 | 66.8212 | -123.1196 | 122.9451 | 123.0908 | 122.9291 | 66.8247 | -123.2923
429.7969 | 123.2346 | -66.7969 | 56.2912 | -0.0029761 | -0.0039402 | 0.0011025 | 0.054791 | -0.002673 | 0.063144 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060808 | 0.012352 | 0.060445 | -66.7885 | 0.028878 | -66.7414 | 56.2289 | 56.0876 | 56.2436 | -66.8421 | -66.7749 | 0.027831 | -66.8185 | 56.1528 | 56.2893 | 56.1506 | -67.0195 | -0.045218 | -0.062252 | 0.0084 | 0.055448 | 0.10067 | -0.20359 | -0.047616 | -0.22258 | -0.13844 | 0.022018 | -0.021644 | 0.20094 | -0.001889 | -0.14062 | 123.0258 | 122.8845 | 123.0405 | 66.8258 | -123.1333 | 122.9496 | 123.0862 | 122.9475 | 66.8247 | -123.3107
430.7969 | 123.2803 | -66.7603 | 56.2729 | -0.0029761 | -0.0037264 | 0.0013163 | 0.055004 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.012566 | 0.060658 | -66.7885 | 0.028878 | -66.746 | 56.2335 | 56.1105 | 56.2436 | -66.8467 | -66.784 | 0.018674 | -66.8231 | 56.1482 | 56.2847 | 56.1414 | -67.0103 | -0.086418 | -0.039363 | -0.028221 | 0.014249 | 0.10067 | -0.16239 | -0.029305 | -0.25005 | -0.12471 | -0.02376 | -0.062844 | 0.1872 | 0.011843 | -0.13147 | 122.9938 | 122.8708 | 123.0038 | 66.7891 | -123.1196 | 122.9084 | 123.045 | 122.9017 | 66.7789 | -123.2832
431.8594 | 123.2391 | -66.7831 | 56.3278 | -0.0029761 | -0.0041538 | 0.0015299 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060595 | 0.012352 | 0.061086 | -66.7839 | 0.033457 | -66.746 | 56.2381 | 56.1105 | 56.2482 | -66.8513 | -66.784 | 0.018674 | -66.8231 | 56.1528 | 56.2847 | 56.1506 | -67.0149 | -0.068109 | -0.089716 | -0.000754 | 0.037137 | 0.10525 | -0.21732 | -0.079659 | -0.23174 | -0.17506 | -0.000872 | -0.039956 | 0.19178 | -0.043089 | -0.17724 | 123.0212 | 122.8936 | 123.0313 | 66.8166 | -123.1791 | 122.9359 | 123.0679 | 122.9337 | 66.8018 | -123.3427
432.7969 | 123.2758 | -66.7648 | 56.2683 | -0.018238 | -0.0041538 | 0.0013163 | 0.054363 | -0.0028866 | 0.063144 | 0.0077831 | -0.00070293 | -0.00076913 | 0.060381 | 0.01278 | 0.060658 | -66.7885 | 0.028878 | -66.7368 | 56.2335 | 56.1059 | 56.2436 | -66.8467 | -66.784 | 0.03241 | -66.8231 | 56.1436 | 56.2893 | 56.1552 | -67.024 | -0.08184 | -0.034786 | -0.023643 | 0.027984 | 0.10982 | -0.16239 | -0.024728 | -0.25921 | -0.12471 | -0.019182 | -0.058266 | 0.20094 | 0.020999 | -0.11316 | 122.9984 | 122.8708 | 123.0084 | 66.7937 | -123.115 | 122.9084 | 123.0541 | 122.92 | 66.7972 | -123.2923
433.8594 | 123.2437 | -66.7511 | 56.3187 | 0.0046549 | -0.0041538 | 0.0013163 | 0.054363 | -0.0028866 | 0.063144 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060381 | 0.01278 | 0.060658 | -66.7839 | 0.028878 | -66.7506 | 56.2381 | 56.1059 | 56.2436 | -66.8421 | -66.784 | 0.023253 | -66.8185 | 56.1436 | 56.2893 | 56.1414 | -67.0149 | -0.090994 | -0.080561 | -0.032797 | 0.000516 | 0.09151 | -0.21274 | -0.075082 | -0.26378 | -0.17506 | -0.032915 | -0.06742 | 0.19636 | -0.029355 | -0.17725 | 122.9892 | 122.857 | 122.9947 | 66.78 | -123.1608 | 122.8947 | 123.0404 | 122.8925 | 66.7744 | -123.3335
434.7969 | 123.2849 | -66.7694 | 56.2912 | -0.0029761 | -0.0041538 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00070293 | -0.0014101 | 0.060167 | 0.01278 | 0.060658 | -66.7885 | 0.028878 | -66.7414 | 56.2335 | 56.1059 | 56.239 | -66.8467 | -66.7886 | 0.018674 | -66.8231 | 56.1528 | 56.2893 | 56.1368 | -67.024 | -0.077263 | -0.057674 | -0.019066 | 0.027982 | 0.10524 | -0.18528 | -0.052195 | -0.25463 | -0.13844 | -0.019184 | -0.053689 | 0.20094 | -0.001889 | -0.15436 | 123.0029 | 122.8753 | 123.0084 | 66.7983 | -123.1379 | 122.9222 | 123.0587 | 122.9062 | 66.7881 | -123.3152
435.875 | 123.3353 | -66.7465 | 56.3004 | 0.0046549 | -0.0041538 | 0.0013163 | 0.054363 | -0.0024592 | 0.063144 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060381 | 0.01278 | 0.060445 | -66.7885 | 0.028878 | -66.7506 | 56.2381 | 56.1059 | 56.239 | -66.8375 | -66.7794 | 0.03241 | -66.8277 | 56.1482 | 56.2939 | 56.1323 | -67.0149 | -0.090993 | -0.06225 | -0.041954 | -0.004062 | 0.086931 | -0.19443 | -0.06135 | -0.26836 | -0.15217 | -0.032915 | -0.081156 | 0.1872 | -0.006465 | -0.16809 | 122.9846 | 122.8524 | 122.9855 | 66.7754 | -123.1379 | 122.8947 | 123.0404 | 122.8788 | 66.7789 | -123.3152
436.7969 | 123.317 | -66.7282 | 56.3049 | -0.0029761 | -0.0039402 | 0.0013163 | 0.054791 | -0.002673 | 0.06293 | 0.015414 | -0.0011301 | -0.0011965 | 0.060381 | 0.012566 | 0.060658 | -66.7885 | 0.033457 | -66.746 | 56.2381 | 56.1013 | 56.239 | -66.8421 | -66.784 | 0.018674 | -66.8185 | 56.1436 | 56.2939 | 56.1368 | -67.0286 | -0.11388 | -0.066828 | -0.060265 | -0.017795 | 0.096088 | -0.20359 | -0.065928 | -0.30041 | -0.16133 | -0.055804 | -0.090309 | 0.2101 | -0.011043 | -0.16809 | 122.9663 | 122.8296 | 122.9672 | 66.7617 | -123.147 | 122.8718 | 123.0221 | 122.865 | 66.7469 | -123.3335
437.7969 | 123.3078 | -66.7419 | 56.2729 | -0.0029761 | -0.0039402 | 0.0013163 | 0.054577 | -0.0024592 | 0.06293 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060595 | 0.01278 | 0.060445 | -66.7839 | 0.033457 | -66.746 | 56.2381 | 56.1013 | 56.2344 | -66.8421 | -66.7794 | 0.023253 | -66.8231 | 56.1482 | 56.2985 | 56.1368 | -67.0195 | -0.10015 | -0.034784 | -0.041953 | -0.004062 | 0.096088 | -0.17155 | -0.038463 | -0.27752 | -0.12471 | -0.037493 | -0.081155 | 0.19636 | 0.025579 | -0.13605 | 122.98 | 122.8433 | 122.9764 | 66.7754 | -123.115 | 122.8901 | 123.0404 | 122.8788 | 66.7652 | -123.2923
438.7969 | 123.2712 | -66.7694 | 56.3049 | 0.0046549 | -0.0039402 | 0.0013163 | 0.054791 | -0.002673 | 0.063358 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060595 | 0.01278 | 0.060445 | -66.7931 | 0.028878 | -66.7506 | 56.2381 | 56.1059 | 56.2436 | -66.8558 | -66.784 | 0.023253 | -66.8231 | 56.1573 | 56.2847 | 56.1323 | -67.024 | -0.086421 | -0.066828 | -0.023644 | 0.018826 | 0.10525 | -0.19901 | -0.061349 | -0.25463 | -0.14759 | -0.014605 | -0.053689 | 0.20094 | -0.020201 | -0.17267 | 123.0075 | 122.8753 | 123.013 | 66.7983 | -123.1608 | 122.9267 | 123.0541 | 122.9017 | 66.7927 | -123.329
439.7969 | 123.2986 | -66.7511 | 56.3049 | -0.010607 | -0.0041538 | 0.0013163 | 0.054791 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060381 | 0.012566 | 0.060445 | -66.7793 | 0.0243 | -66.7506 | 56.2335 | 56.0968 | 56.239 | -66.8467 | -66.7794 | 0.023253 | -66.8231 | 56.1528 | 56.2939 | 56.1277 | -67.0195 | -0.095573 | -0.071407 | -0.028219 | 0.000516 | 0.096089 | -0.20817 | -0.065928 | -0.26836 | -0.15217 | -0.028337 | -0.071999 | 0.19636 | -0.011043 | -0.17725 | 122.9846 | 122.8479 | 122.9901 | 66.7754 | -123.1516 | 122.9039 | 123.045 | 122.8788 | 66.7744 | -123.3244
440.875 | 123.2666 | -66.7419 | 56.3278 | -0.0029761 | -0.0039402 | 0.0015299 | 0.054363 | -0.002673 | 0.062717 | 0.00015261 | -0.00091653 | -0.0016237 | 0.060808 | 0.012566 | 0.060658 | -66.7885 | 0.033457 | -66.7552 | 56.2381 | 56.1105 | 56.2436 | -66.8513 | -66.784 | 0.018674 | -66.8231 | 56.1482 | 56.2939 | 56.1506 | -67.024 | -0.10931 | -0.089716 | -0.046532 | -0.013218 | 0.09609 | -0.21732 | -0.084237 | -0.28209 | -0.17964 | -0.042071 | -0.081155 | 0.20094 | -0.033931 | -0.17724 | 122.98 | 122.8524 | 122.9855 | 66.7754 | -123.1791 | 122.8901 | 123.0358 | 122.8925 | 66.7606 | -123.3519
441.7969 | 123.2849 | -66.7557 | 56.2729 | -0.0029761 | -0.0043674 | 0.0017435 | 0.054791 | -0.0028866 | 0.06293 | 0.00015261 | -0.00091653 | -0.0014101 | 0.060167 | 0.012566 | 0.060658 | -66.7885 | 0.033457 | -66.746 | 56.2335 | 56.1105 | 56.2436 | -66.8513 | -66.7794 | 0.027831 | -66.8094 | 56.1528 | 56.303 | 56.1323 | -67.0286 | -0.095575 | -0.039363 | -0.032799 | 0.009671 | 0.10525 | -0.16239 | -0.029305 | -0.27294 | -0.12013 | -0.02376 | -0.053686 | 0.21925 | 0.030158 | -0.14063 | 122.9892 | 122.8662 | 122.9993 | 66.7891 | -123.1241 | 122.9084 | 123.0587 | 122.8879 | 66.7835 | -123.3015
442.8594 | 123.3582 | -66.7099 | 56.3187 | -0.0029761 | -0.0043674 | 0.00088894 | 0.054577 | -0.0028866 | 0.06293 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060595 | 0.012993 | 0.060658 | -66.7839 | 0.033457 | -66.746 | 56.2335 | 56.1105 | 56.239 | -66.8513 | -66.7794 | 0.018674 | -66.8231 | 56.1573 | 56.2847 | 56.1414 | -67.024 | -0.14135 | -0.08514 | -0.073996 | -0.036105 | 0.10525 | -0.20817 | -0.079661 | -0.31414 | -0.16133 | -0.069536 | -0.1132 | 0.20094 | -0.033934 | -0.17725 | 122.9434 | 122.8204 | 122.9489 | 66.7434 | -123.1699 | 122.8672 | 122.9946 | 122.8513 | 66.7286 | -123.3427
443.7969 | 123.2941 | -66.7465 | 56.2912 | 0.0046549 | -0.0037264 | 0.0013163 | 0.054363 | -0.0028866 | 0.063144 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060595 | 0.01278 | 0.060445 | -66.7839 | 0.028878 | -66.746 | 56.2381 | 56.1059 | 56.2436 | -66.8467 | -66.784 | 0.036989 | -66.8277 | 56.1436 | 56.2893 | 56.1323 | -67.024 | -0.10015 | -0.053095 | -0.037375 | 0.000516 | 0.10067 | -0.18528 | -0.047616 | -0.27752 | -0.1476 | -0.037493 | -0.081156 | 0.19636 | -0.001889 | -0.15894 | 122.9846 | 122.8524 | 122.9901 | 66.7754 | -123.1379 | 122.8901 | 123.0358 | 122.8788 | 66.7835 | -123.3152
444.7969 | 123.2941 | -66.7419 | 56.3416 | -0.0029761 | -0.0045812 | 0.0013163 | 0.055004 | -0.0028866 | 0.063358 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060445 | -66.7839 | 0.028878 | -66.746 | 56.2335 | 56.1059 | 56.239 | -66.8467 | -66.7749 | 0.023253 | -66.8185 | 56.1482 | 56.2893 | 56.1552 | -67.0149 | -0.10473 | -0.10803 | -0.041953 | -0.004062 | 0.10067 | -0.23563 | -0.10255 | -0.27294 | -0.19337 | -0.032914 | -0.076576 | 0.19636 | -0.052243 | -0.1864 | 122.9755 | 122.8479 | 122.9809 | 66.7708 | -123.1882 | 122.8901 | 123.0313 | 122.8971 | 66.7652 | -123.3564
445.7969 | 123.3444 | -66.7099 | 56.2866 | 0.0046549 | -0.0041538 | 0.0011025 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060595 | 0.01278 | 0.060445 | -66.7793 | 0.019721 | -66.7368 | 56.2335 | 56.1105 | 56.2436 | -66.8513 | -66.7794 | 0.018674 | -66.8185 | 56.1482 | 56.2985 | 56.1552 | -67.024 | -0.14135 | -0.053096 | -0.069418 | -0.026948 | 0.1144 | -0.17612 | -0.043038 | -0.31414 | -0.13844 | -0.069536 | -0.10862 | 0.20552 | 0.011846 | -0.13147 | 122.9434 | 122.8204 | 122.9535 | 66.7296 | -123.1379 | 122.8581 | 123.0084 | 122.8651 | 66.7286 | -123.3107
446.7969 | 123.2483 | -66.7419 | 56.337 | 0.0046549 | -0.0041538 | 0.0015299 | 0.054363 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060595 | 0.01278 | 0.060445 | -66.7885 | 0.0243 | -66.7368 | 56.2381 | 56.1105 | 56.239 | -66.8421 | -66.784 | 0.027831 | -66.8231 | 56.1528 | 56.2893 | 56.146 | -67.0195 | -0.10015 | -0.098871 | -0.046532 | 0.005095 | 0.10525 | -0.22648 | -0.097971 | -0.27752 | -0.18422 | -0.042071 | -0.081155 | 0.19636 | -0.047665 | -0.19098 | 122.98 | 122.8524 | 122.9809 | 66.7662 | -123.1791 | 122.8947 | 123.0313 | 122.8879 | 66.7698 | -123.3564
447.7969 | 123.3765 | -66.7328 | 56.282 | 0.0046549 | -0.0039402 | 0.0013163 | 0.054577 | -0.002673 | 0.063144 | 0.0077831 | -0.0011301 | -0.00076913 | 0.060381 | 0.012352 | 0.060658 | -66.7885 | 0.0243 | -66.7414 | 56.2427 | 56.1105 | 56.2436 | -66.8513 | -66.784 | 0.018674 | -66.8231 | 56.1482 | 56.2939 | 56.1506 | -67.024 | -0.11846 | -0.039361 | -0.055687 | -0.008639 | 0.10982 | -0.17154 | -0.03846 | -0.29125 | -0.13386 | -0.051226 | -0.09031 | 0.20094 | 0.011846 | -0.13147 | 122.9755 | 122.8433 | 122.9764 | 66.7571 | -123.1333 | 122.881 | 123.0267 | 122.8834 | 66.7515 | -123.3061
448.8594 | 123.3078 | -66.7374 | 56.3416 | 0.019917 | -0.0041538 | 0.0013163 | 0.054363 | -0.002673 | 0.063144 | 0.015414 | -0.0011301 | -0.00098273 | 0.060381 | 0.012566 | 0.060872 | -66.7885 | 0.028878 | -66.7277 | 56.2335 | 56.1151 | 56.239 | -66.8421 | -66.784 | 0.014095 | -66.8185 | 56.1482 | 56.2939 | 56.146 | -67.024 | -0.10473 | -0.10803 | -0.051109 | 0.009674 | 0.1144 | -0.22647 | -0.10255 | -0.28667 | -0.19337 | -0.046648 | -0.081153 | 0.20552 | -0.047664 | -0.19556 | 122.9709 | 122.8524 | 122.9764 | 66.7662 | -123.1836 | 122.8855 | 123.0313 | 122.8834 | 66.7515 | -123.3656
449.7969 | 123.3032 | -66.7328 | 56.3141 | 0.0046549 | -0.0043674 | 0.0013163 | 0.054577 | -0.0031002 | 0.063144 | -0.0074779 | -0.00091653 | -0.0014101 | 0.060595 | 0.01278 | 0.060658 | -66.7885 | 0.028878 | -66.7506 | 56.2335 | 56.1013 | 56.2482 | -66.8467 | -66.7886 | 0.027831 | -66.8231 | 56.1482 | 56.2893 | 56.1277 | -67.024 | -0.11388 | -0.080562 | -0.055687 | -0.017795 | 0.096089 | -0.21274 | -0.065926 | -0.29125 | -0.16591 | -0.055805 | -0.09031 | 0.20094 | -0.024777 | -0.18641 | 122.9663 | 122.8341 | 122.9809 | 66.7617 | -123.1608 | 122.881 | 123.0221 | 122.8605 | 66.7606 | -123.3381
450.7969 | 123.1979 | -66.774 | 56.3187 | -0.010607 | -0.0043674 | 0.0011025 | 0.054363 | -0.0028866 | 0.062717 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060595 | 0.01278 | 0.060658 | -66.7839 | 0.028878 | -66.746 | 56.2427 | 56.1059 | 56.2436 | -66.8513 | -66.7794 | 0.027831 | -66.8231 | 56.1436 | 56.2939 | 56.1506 | -67.024 | -0.077264 | -0.075983 | -0.009909 | 0.027982 | 0.10525 | -0.21274 | -0.075082 | -0.25005 | -0.17506 | -0.005449 | -0.049111 | 0.20094 | -0.024776 | -0.16809 | 123.0167 | 122.8799 | 123.0176 | 66.8029 | -123.1699 | 122.9176 | 123.0679 | 122.9246 | 66.8018 | -123.3427
451.7969 | 123.1842 | -66.7786 | 56.3324 | -0.0029761 | -0.0039402 | 0.0011025 | 0.054363 | -0.002673 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.01278 | 0.060872 | -66.7885 | 0.0243 | -66.7368 | 56.2381 | 56.1105 | 56.2482 | -66.8421 | -66.7886 | 0.027831 | -66.8139 | 56.1573 | 56.2985 | 56.1506 | -67.024 | -0.063529 | -0.094293 | -0.009911 | 0.041716 | 0.10525 | -0.2219 | -0.084236 | -0.24547 | -0.17506 | -0.010029 | -0.035377 | 0.2101 | -0.03393 | -0.18182 | 123.0167 | 122.8891 | 123.0267 | 66.8029 | -123.1745 | 122.9359 | 123.077 | 122.9291 | 66.8064 | -123.3564
452.8594 | 123.1934 | -66.7374 | 56.3324 | -0.0029761 | -0.0037264 | 0.0015299 | 0.054363 | -0.002673 | 0.063358 | 0.015414 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060445 | -66.7793 | 0.028878 | -66.7414 | 56.2427 | 56.1151 | 56.2344 | -66.8375 | -66.7794 | 0.027831 | -66.8185 | 56.1482 | 56.2893 | 56.1414 | -67.024 | -0.10015 | -0.089715 | -0.041952 | -0.004061 | 0.096087 | -0.21732 | -0.097972 | -0.28667 | -0.18422 | -0.04207 | -0.081153 | 0.20552 | -0.043087 | -0.19098 | 122.98 | 122.8524 | 122.9718 | 66.7662 | -123.1699 | 122.8855 | 123.0267 | 122.8788 | 66.7652 | -123.3564
453.7969 | 123.2117 | -66.7923 | 56.3553 | -0.0029761 | -0.0045812 | 0.0011025 | 0.054363 | -0.0031002 | 0.06293 | 0.023044 | -0.0011301 | -0.0011965 | 0.060381 | 0.012993 | 0.060872 | -66.7793 | 0.028878 | -66.7414 | 56.2335 | 56.1013 | 56.2436 | -66.8467 | -66.7749 | 0.023253 | -66.8185 | 56.1482 | 56.2893 | 56.1506 | -67.0195 | -0.054375 | -0.12176 | 0.012979 | 0.05087 | 0.10524 | -0.25394 | -0.1117 | -0.22716 | -0.2071 | 0.01744 | -0.026222 | 0.20094 | -0.065976 | -0.20471 | 123.0258 | 122.8936 | 123.0359 | 66.8212 | -123.202 | 122.9405 | 123.0816 | 122.9429 | 66.8156 | -123.3747
454.8594 | 123.2895 | -66.7145 | 56.3416 | 0.019917 | -0.0043674 | 0.0013163 | 0.054791 | -0.0028866 | 0.063358 | 0.023044 | -0.00091653 | -0.0014101 | 0.060381 | 0.01278 | 0.060872 | -66.7885 | 0.0243 | -66.7368 | 56.2427 | 56.1013 | 56.2436 | -66.8467 | -66.7794 | 0.023253 | -66.8231 | 56.1436 | 56.2939 | 56.1414 | -67.0286 | -0.13219 | -0.098871 | -0.073997 | -0.02237 | 0.10982 | -0.24021 | -0.09797 | -0.31414 | -0.19795 | -0.064958 | -0.10862 | 0.20552 | -0.047664 | -0.20013 | 122.9572 | 122.8158 | 122.9581 | 66.7388 | -123.1882 | 122.8581 | 123.0084 | 122.8559 | 66.7377 | -123.3702
455.7969 | 123.2254 | -66.7831 | 56.3324 | -0.0029761 | -0.0039402 | 0.0013163 | 0.054149 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060872 | -66.7793 | 0.033457 | -66.7368 | 56.2335 | 56.1105 | 56.239 | -66.8467 | -66.7749 | 0.027831 | -66.8185 | 56.1482 | 56.2847 | 56.1368 | -67.0195 | -0.06353 | -0.098872 | 0.003824 | 0.046294 | 0.10982 | -0.2219 | -0.093393 | -0.23632 | -0.18422 | 0.008285 | -0.035377 | 0.20094 | -0.047666 | -0.19556 | 123.0167 | 122.8936 | 123.0221 | 66.8166 | -123.1791 | 122.9313 | 123.0679 | 122.92 | 66.811 | -123.3519
456.7969 | 123.1934 | -66.774 | 56.3141 | -0.0029761 | -0.0045812 | 0.00088894 | 0.054577 | -0.0028866 | 0.063358 | 0.00015261 | -0.00070293 | -0.00098273 | 0.060808 | 0.012993 | 0.060658 | -66.7793 | 0.033457 | -66.746 | 56.2427 | 56.1105 | 56.2527 | -66.8513 | -66.7794 | 0.018674 | -66.8139 | 56.1528 | 56.2939 | 56.1323 | -67.024 | -0.077264 | -0.071405 | -0.005331 | 0.027982 | 0.10525 | -0.20359 | -0.061347 | -0.25005 | -0.16133 | -0.005449 | -0.039954 | 0.2101 | -0.020198 | -0.18183 | 123.0167 | 122.8845 | 123.0267 | 66.8074 | -123.1653 | 122.9267 | 123.0679 | 122.9062 | 66.7927 | -123.3381
457.7969 | 123.2483 | -66.7648 | 56.3049 | -0.0029761 | -0.0041538 | 0.0013163 | 0.054577 | -0.0031002 | 0.062717 | 0.015414 | -0.00091653 | -0.0011965 | 0.060381 | 0.01278 | 0.060658 | -66.7839 | 0.028878 | -66.7506 | 56.2381 | 56.1013 | 56.2344 | -66.8513 | -66.784 | 0.027831 | -66.8231 | 56.1482 | 56.2893 | 56.1368 | -67.0195 | -0.086419 | -0.066828 | -0.019064 | 0.014249 | 0.10067 | -0.20359 | -0.070507 | -0.25463 | -0.15675 | -0.019182 | -0.058266 | 0.19636 | -0.015622 | -0.16809 | 123.0029 | 122.8662 | 122.9993 | 66.7937 | -123.1562 | 122.913 | 123.0541 | 122.9017 | 66.7927 | -123.3244
458.8594 | 123.1934 | -66.7648 | 56.3324 | 0.0046549 | -0.0041538 | 0.0013163 | 0.054363 | -0.0028866 | 0.063358 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060167 | 0.013207 | 0.060445 | -66.7931 | 0.015142 | -66.7368 | 56.2427 | 56.1059 | 56.2482 | -66.8467 | -66.784 | 0.027831 | -66.8185 | 56.1528 | 56.2939 | 56.146 | -67.024 | -0.08184 | -0.089715 | -0.028221 | 0.027984 | 0.10982 | -0.22648 | -0.084236 | -0.25921 | -0.17964 | -0.019182 | -0.053687 | 0.20552 | -0.038508 | -0.1864 | 123.0075 | 122.8708 | 123.013 | 66.78 | -123.1791 | 122.9176 | 123.0587 | 122.9108 | 66.7927 | -123.3564
459.7969 | 123.2483 | -66.7511 | 56.3049 | -0.0029761 | -0.0041538 | 0.0013163 | 0.054149 | -0.0031002 | 0.063144 | 0.015414 | -0.0011301 | -0.00098273 | 0.060381 | 0.012566 | 0.060872 | -66.7885 | 0.028878 | -66.7368 | 56.2381 | 56.1059 | 56.2573 | -66.8513 | -66.784 | 0.023253 | -66.8231 | 56.1619 | 56.2847 | 56.1414 | -67.0195 | -0.10015 | -0.066828 | -0.037376 | 0.014251 | 0.1144 | -0.19901 | -0.047614 | -0.26836 | -0.14301 | -0.032915 | -0.071999 | 0.19636 | -0.020201 | -0.16351 | 122.9892 | 122.857 | 123.0084 | 66.78 | -123.1562 | 122.913 | 123.0358 | 122.8925 | 66.7744 | -123.3244
460.7969 | 123.2986 | -66.7648 | 56.2683 | -0.0029761 | -0.0043674 | 0.0013163 | 0.054577 | -0.0028866 | 0.06293 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060595 | 0.013207 | 0.060872 | -66.7931 | 0.0243 | -66.7414 | 56.2335 | 56.1105 | 56.2482 | -66.8421 | -66.7749 | 0.027831 | -66.8185 | 56.1482 | 56.2893 | 56.1323 | -67.024 | -0.077261 | -0.034786 | -0.028221 | 0.023405 | 0.10067 | -0.15781 | -0.02015 | -0.25921 | -0.12013 | -0.010025 | -0.053687 | 0.20552 | 0.020999 | -0.13605 | 122.9984 | 122.8753 | 123.013 | 66.7891 | -123.1104 | 122.913 | 123.0541 | 122.8971 | 66.7927 | -123.2923
461.8594 | 123.3307 | -66.7557 | 56.2546 | -0.0029761 | -0.0045812 | 0.0011025 | 0.054363 | -0.0028866 | 0.063144 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060167 | 0.012993 | 0.060658 | -66.7793 | 0.033457 | -66.746 | 56.2335 | 56.1059 | 56.2436 | -66.8421 | -66.7749 | 0.023253 | -66.8185 | 56.1482 | 56.2939 | 56.1414 | -67.024 | -0.086417 | -0.021053 | -0.023642 | 0.009671 | 0.096088 | -0.14866 | -0.010995 | -0.26836 | -0.1064 | -0.019181 | -0.062843 | 0.20552 | 0.039311 | -0.11316 | 122.9892 | 122.8616 | 122.9993 | 66.7891 | -123.0967 | 122.9039 | 123.0496 | 122.8971 | 66.7789 | -123.2786
462.7969 | 123.2712 | -66.7969 | 56.2958 | -0.0029761 | -0.0043674 | 0.0013163 | 0.054577 | -0.0028866 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060167 | 0.012993 | 0.060658 | -66.7793 | 0.033457 | -66.7414 | 56.2381 | 56.1013 | 56.2482 | -66.8467 | -66.7794 | 0.027831 | -66.8231 | 56.1482 | 56.2847 | 56.1368 | -67.0195 | -0.049797 | -0.057672 | 0.017557 | 0.055448 | 0.10524 | -0.19443 | -0.047615 | -0.22258 | -0.14759 | 0.017439 | -0.026223 | 0.19636 | -0.011045 | -0.15894 | 123.035 | 122.8982 | 123.045 | 66.8303 | -123.1424 | 122.9451 | 123.0816 | 122.9337 | 66.8247 | -123.3152
463.8594 | 123.2712 | -66.7877 | 56.3553 | -0.0029761 | -0.0043674 | 0.0015299 | 0.054577 | -0.0031002 | 0.063144 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060381 | 0.012993 | 0.060658 | -66.7885 | 0.0243 | -66.7506 | 56.2335 | 56.1059 | 56.2436 | -66.8558 | -66.7749 | 0.014095 | -66.8231 | 56.1436 | 56.2847 | 56.1323 | -67.0286 | -0.06811 | -0.12176 | -0.000755 | 0.037137 | 0.10525 | -0.24936 | -0.1117 | -0.2409 | -0.21168 | 0.012863 | -0.035378 | 0.20552 | -0.070555 | -0.22303 | 123.0212 | 122.8936 | 123.0313 | 66.812 | -123.2111 | 122.9313 | 123.0725 | 122.92 | 66.8018 | -123.3839
464.7969 | 123.3215 | -66.7786 | 56.2729 | -0.0029761 | -0.0041538 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | -0.0074779 | -0.0011301 | -0.0011965 | 0.060167 | 0.013421 | 0.060872 | -66.7793 | 0.019721 | -66.7506 | 56.2289 | 56.1105 | 56.2436 | -66.8329 | -66.784 | 0.014095 | -66.8277 | 56.1436 | 56.2939 | 56.1185 | -67.0195 | -0.054371 | -0.043941 | -0.000754 | 0.027981 | 0.082352 | -0.16239 | -0.029305 | -0.24089 | -0.12929 | -0.00545 | -0.049113 | 0.19178 | 0.021001 | -0.15436 | 123.0075 | 122.8891 | 123.0221 | 66.7983 | -123.1058 | 122.9222 | 123.0725 | 122.8971 | 66.7927 | -123.2923
465.7969 | 123.262 | -66.7786 | 56.2683 | 0.0046549 | -0.0043674 | 0.0013163 | 0.054791 | -0.0024592 | 0.06293 | 0.015414 | -0.00091653 | -0.00076913 | 0.060167 | 0.012993 | 0.060231 | -66.7839 | 0.0243 | -66.746 | 56.2381 | 56.0968 | 56.2436 | -66.8513 | -66.7794 | 0.018674 | -66.8139 | 56.1482 | 56.2893 | 56.1185 | -67.0286 | -0.072687 | -0.030207 | -0.005332 | 0.032559 | 0.10525 | -0.17155 | -0.024728 | -0.25005 | -0.12013 | -0.000872 | -0.035377 | 0.21467 | 0.020999 | -0.14979 | 123.0167 | 122.8753 | 123.0221 | 66.8029 | -123.1196 | 122.9267 | 123.0679 | 122.8971 | 66.7972 | -123.2969
466.7969 | 123.2208 | -66.7374 | 56.3461 | 0.0046549 | -0.0045812 | 0.0013163 | 0.054363 | -0.0031002 | 0.063358 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.013207 | 0.060872 | -66.7839 | 0.0243 | -66.7506 | 56.2381 | 56.1105 | 56.2482 | -66.8238 | -66.7749 | 0.023253 | -66.8139 | 56.1528 | 56.303 | 56.1414 | -67.0149 | -0.086411 | -0.10803 | -0.04653 | -0.013217 | 0.073194 | -0.23563 | -0.097969 | -0.27751 | -0.19337 | -0.037491 | -0.076575 | 0.20094 | -0.043084 | -0.20471 | 122.9755 | 122.8479 | 122.9855 | 66.7617 | -123.1699 | 122.8901 | 123.0404 | 122.8788 | 66.7606 | -123.361
467.8594 | 123.3078 | -66.7511 | 56.282 | -0.0029761 | -0.0045812 | 0.0015299 | 0.054791 | -0.002673 | 0.063358 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.013207 | 0.060231 | -66.7839 | 0.0243 | -66.7506 | 56.2381 | 56.0922 | 56.2436 | -66.8467 | -66.7749 | 0.023253 | -66.8185 | 56.1482 | 56.2939 | 56.1368 | -67.024 | -0.095573 | -0.043939 | -0.032797 | 0.000516 | 0.096089 | -0.18986 | -0.03846 | -0.27294 | -0.13386 | -0.023758 | -0.06742 | 0.20552 | 0.011846 | -0.1452 | 122.9892 | 122.8433 | 122.9947 | 66.7754 | -123.1287 | 122.8993 | 123.045 | 122.8879 | 66.7744 | -123.3061
468.7969 | 123.2666 | -66.7603 | 56.2729 | -0.0029761 | -0.0043674 | 0.0011025 | 0.054791 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060872 | -66.7793 | 0.019721 | -66.746 | 56.2381 | 56.0922 | 56.239 | -66.8513 | -66.7794 | 0.027831 | -66.8231 | 56.1482 | 56.2939 | 56.1231 | -67.0195 | -0.090997 | -0.034784 | -0.019064 | 0.014249 | 0.10525 | -0.1807 | -0.033884 | -0.2592 | -0.12471 | -0.019182 | -0.062844 | 0.19636 | 0.021001 | -0.14979 | 122.9984 | 122.8524 | 122.9993 | 66.78 | -123.1241 | 122.9084 | 123.0541 | 122.8834 | 66.7881 | -123.2923
469.8594 | 123.3078 | -66.7511 | 56.2729 | -0.0029761 | -0.0043674 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060658 | -66.7793 | 0.0243 | -66.7414 | 56.2381 | 56.0968 | 56.2436 | -66.8467 | -66.7794 | 0.018674 | -66.8185 | 56.1482 | 56.2985 | 56.1368 | -67.0286 | -0.095573 | -0.034784 | -0.028219 | 0.009672 | 0.10524 | -0.17612 | -0.029305 | -0.27752 | -0.12471 | -0.028337 | -0.06742 | 0.2101 | 0.025579 | -0.13605 | 122.9892 | 122.8479 | 122.9947 | 66.7754 | -123.1196 | 122.8993 | 123.0496 | 122.8879 | 66.7698 | -123.3015
470.7969 | 123.2803 | -66.7511 | 56.3141 | -0.0029761 | -0.0045812 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060595 | 0.013421 | 0.060445 | -66.7839 | 0.033457 | -66.7506 | 56.2381 | 56.1013 | 56.2436 | -66.8467 | -66.784 | 0.027831 | -66.8185 | 56.1528 | 56.303 | 56.1368 | -67.024 | -0.095573 | -0.075983 | -0.032797 | 0.000516 | 0.096089 | -0.21274 | -0.070504 | -0.27294 | -0.16133 | -0.032915 | -0.06742 | 0.20552 | -0.011041 | -0.17725 | 122.9892 | 122.8524 | 122.9947 | 66.7846 | -123.1608 | 122.9039 | 123.0541 | 122.8879 | 66.7789 | -123.3381
471.7969 | 123.1705 | -66.7786 | 56.3599 | 0.012286 | -0.0041538 | 0.0017435 | 0.054577 | -0.0028866 | 0.063144 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.013421 | 0.060658 | -66.7839 | 0.033457 | -66.7506 | 56.2381 | 56.1013 | 56.2482 | -66.8513 | -66.7794 | 0.018674 | -66.8139 | 56.1482 | 56.2985 | 56.146 | -67.0195 | -0.072687 | -0.12176 | -0.005332 | 0.027981 | 0.10067 | -0.25852 | -0.1117 | -0.24089 | -0.21168 | -0.000872 | -0.035377 | 0.20552 | -0.061396 | -0.21387 | 123.0167 | 122.8799 | 123.0267 | 66.812 | -123.2111 | 122.9267 | 123.077 | 122.9246 | 66.7972 | -123.3793
472.7969 | 123.317 | -66.7511 | 56.2866 | 0.0046549 | -0.0041538 | 0.0013163 | 0.054791 | -0.0031002 | 0.062503 | 0.00015261 | -0.00070293 | -0.00076913 | 0.060381 | 0.013207 | 0.060231 | -66.7793 | 0.0243 | -66.7414 | 56.2335 | 56.083 | 56.2436 | -66.8421 | -66.784 | 0.018674 | -66.8277 | 56.1482 | 56.2985 | 56.1368 | -67.024 | -0.090994 | -0.053096 | -0.028219 | 0.009672 | 0.10067 | -0.20359 | -0.043038 | -0.27294 | -0.13844 | -0.032915 | -0.076578 | 0.19636 | 0.011846 | -0.14978 | 122.9846 | 122.8341 | 122.9947 | 66.7754 | -123.1287 | 122.8993 | 123.0496 | 122.8879 | 66.7698 | -123.3107
473.8594 | 123.1796 | -66.7923 | 56.3049 | -0.0029761 | -0.0043674 | 0.0011025 | 0.054149 | -0.002673 | 0.06293 | 0.0077831 | -0.00048933 | -0.0014101 | 0.060381 | 0.013207 | 0.060658 | -66.7747 | 0.033457 | -66.7506 | 56.2335 | 56.1013 | 56.2436 | -66.8375 | -66.7749 | 0.027831 | -66.8139 | 56.1482 | 56.2985 | 56.1323 | -67.0195 | -0.045217 | -0.071407 | 0.017558 | 0.041714 | 0.086931 | -0.20359 | -0.061349 | -0.22716 | -0.15675 | 0.01744 | -0.021644 | 0.20552 | -0.006465 | -0.17267 | 123.0258 | 122.8936 | 123.0359 | 66.8258 | -123.1424 | 122.9405 | 123.0908 | 122.9246 | 66.8201 | -123.3244
474.7969 | 123.317 | -66.7419 | 56.3049 | 0.0046549 | -0.0045812 | 0.0013163 | 0.054791 | -0.0028866 | 0.063144 | 0.00015261 | -0.0011301 | -0.00076913 | 0.060167 | 0.013207 | 0.060658 | -66.7793 | 0.0243 | -66.746 | 56.2427 | 56.0968 | 56.2436 | -66.8421 | -66.7749 | 0.014095 | -66.8277 | 56.1482 | 56.2939 | 56.1414 | -67.0195 | -0.10015 | -0.06225 | -0.037375 | -0.004062 | 0.096088 | -0.20817 | -0.061349 | -0.27752 | -0.15675 | -0.032914 | -0.085734 | 0.19178 | -0.011043 | -0.16351 | 122.9846 | 122.8387 | 122.9855 | 66.7662 | -123.147 | 122.8901 | 123.0358 | 122.8834 | 66.756 | -123.3244
475.7969 | 123.3307 | -66.7236 | 56.2729 | 0.012286 | -0.0045812 | 0.0015299 | 0.054791 | -0.0031002 | 0.063358 | 0.0077831 | -0.00048933 | -0.00098273 | 0.060381 | 0.013207 | 0.060872 | -66.7793 | 0.019721 | -66.7414 | 56.2335 | 56.1013 | 56.2436 | -66.8467 | -66.7749 | 0.018674 | -66.8139 | 56.1482 | 56.303 | 56.1323 | -67.024 | -0.12304 | -0.039363 | -0.055685 | -0.017794 | 0.10524 | -0.17155 | -0.029305 | -0.3004 | -0.12471 | -0.051224 | -0.090308 | 0.2101 | 0.030158 | -0.14063 | 122.9572 | 122.825 | 122.9672 | 66.7434 | -123.1196 | 122.8718 | 123.0267 | 122.8559 | 66.7423 | -123.2969
476.8594 | 123.2117 | -66.7557 | 56.3461 | 0.012286 | -0.0045812 | 0.0013163 | 0.054791 | -0.0031002 | 0.062717 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.01278 | 0.060658 | -66.7747 | 0.0243 | -66.746 | 56.2381 | 56.1105 | 56.2436 | -66.8421 | -66.7794 | 0.027831 | -66.8185 | 56.1436 | 56.2939 | 56.1277 | -67.0286 | -0.086417 | -0.10803 | -0.019063 | 0.009671 | 0.096088 | -0.23563 | -0.10255 | -0.27294 | -0.20253 | -0.02376 | -0.062843 | 0.2101 | -0.052241 | -0.21845 | 122.9938 | 122.8662 | 122.9993 | 66.78 | -123.1882 | 122.8993 | 123.0496 | 122.8834 | 66.7835 | -123.3747
477.7969 | 123.3261 | -66.7465 | 56.3141 | 0.0046549 | -0.0043674 | 0.0015299 | 0.054577 | -0.0031002 | 0.06293 | -0.015108 | -0.0011301 | -0.00098273 | 0.060167 | 0.013207 | 0.060658 | -66.7793 | 0.019721 | -66.7323 | 56.2335 | 56.1013 | 56.2436 | -66.8467 | -66.7794 | 0.018674 | -66.8094 | 56.1573 | 56.2939 | 56.1323 | -67.0286 | -0.10015 | -0.080562 | -0.032797 | 0.014251 | 0.1144 | -0.21274 | -0.070504 | -0.28209 | -0.15675 | -0.032915 | -0.062841 | 0.21925 | -0.020198 | -0.18183 | 122.98 | 122.8479 | 122.9901 | 66.7662 | -123.1608 | 122.9039 | 123.0404 | 122.8788 | 66.7652 | -123.3427
478.7969 | 123.2849 | -66.7191 | 56.3095 | -0.010607 | -0.0043674 | 0.0011025 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00070293 | -0.0014101 | 0.060167 | 0.013421 | 0.060445 | -66.7747 | 0.0243 | -66.7414 | 56.2289 | 56.0922 | 56.2436 | -66.8467 | -66.7749 | 0.023253 | -66.8139 | 56.1528 | 56.2893 | 56.1506 | -67.0286 | -0.12762 | -0.080562 | -0.055684 | -0.022372 | 0.10524 | -0.21732 | -0.065926 | -0.30956 | -0.15675 | -0.055802 | -0.094886 | 0.21467 | -0.020199 | -0.15893 | 122.948 | 122.8112 | 122.9626 | 66.7434 | -123.1562 | 122.8718 | 123.0084 | 122.8696 | 66.7423 | -123.3381
479.8594 | 123.2758 | -66.7465 | 56.3095 | 0.0046549 | -0.0043674 | 0.0013163 | 0.054791 | -0.002673 | 0.06293 | 0.0077831 | -0.00091653 | -0.00076913 | 0.060381 | 0.013207 | 0.060445 | -66.7747 | 0.028878 | -66.7368 | 56.2335 | 56.0968 | 56.2436 | -66.8421 | -66.7703 | 0.018674 | -66.8185 | 56.1528 | 56.2847 | 56.1368 | -67.024 | -0.095572 | -0.075984 | -0.028218 | 0.009673 | 0.10525 | -0.21274 | -0.065926 | -0.27752 | -0.15675 | -0.023757 | -0.071998 | 0.20552 | -0.024778 | -0.17267 | 122.98 | 122.8433 | 122.9901 | 66.7754 | -123.1516 | 122.8993 | 123.0313 | 122.8834 | 66.7652 | -123.3335
480.7969 | 123.1613 | -66.7648 | 56.3599 | -0.0029761 | -0.0045812 | 0.0011025 | 0.054363 | -0.002673 | 0.063144 | 0.0077831 | -0.00091653 | -0.00076913 | 0.060167 | 0.013634 | 0.060658 | -66.7747 | 0.028878 | -66.746 | 56.2427 | 56.0968 | 56.2482 | -66.8467 | -66.7749 | 0.023253 | -66.8139 | 56.1482 | 56.2985 | 56.1506 | -67.0195 | -0.08184 | -0.11718 | -0.009907 | 0.018827 | 0.10067 | -0.2631 | -0.1117 | -0.25463 | -0.21168 | -0.010025 | -0.049109 | 0.20552 | -0.061396 | -0.20929 | 123.0075 | 122.8616 | 123.013 | 66.7937 | -123.2065 | 122.913 | 123.0633 | 122.9154 | 66.7881 | -123.3793
481.8594 | 123.2117 | -66.7648 | 56.3232 | -0.0029761 | -0.0050084 | 0.0015299 | 0.054577 | -0.0028866 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060381 | 0.013421 | 0.060872 | -66.7747 | 0.028878 | -66.7414 | 56.2335 | 56.1105 | 56.2482 | -66.8467 | -66.7703 | 0.027831 | -66.8139 | 56.1482 | 56.2893 | 56.1368 | -67.0286 | -0.08184 | -0.089717 | -0.009907 | 0.023405 | 0.10524 | -0.21274 | -0.075081 | -0.26378 | -0.17506 | -0.005446 | -0.049109 | 0.21467 | -0.033932 | -0.1864 | 122.9984 | 122.8753 | 123.013 | 66.7937 | -123.1699 | 122.913 | 123.0541 | 122.9017 | 66.7927 | -123.3519
482.7969 | 123.2895 | -66.7465 | 56.3187 | 0.012286 | -0.0045812 | 0.0015299 | 0.054577 | -0.0028866 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.013421 | 0.060658 | -66.7747 | 0.019721 | -66.7414 | 56.2427 | 56.1105 | 56.2482 | -66.8513 | -66.784 | 0.014095 | -66.8094 | 56.1436 | 56.2893 | 56.1231 | -67.024 | -0.10473 | -0.075983 | -0.028218 | 0.005094 | 0.10982 | -0.20817 | -0.070504 | -0.27752 | -0.17506 | -0.037493 | -0.062841 | 0.21468 | -0.029355 | -0.19556 | 122.9892 | 122.857 | 122.9947 | 66.7662 | -123.1699 | 122.8901 | 123.0358 | 122.8696 | 66.7606 | -123.3427
483.7969 | 123.3353 | -66.7328 | 56.2912 | -0.010607 | -0.0047948 | 0.0013163 | 0.054791 | -0.0031002 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059954 | 0.013634 | 0.060445 | -66.7747 | 0.033457 | -66.7414 | 56.2335 | 56.1059 | 56.2482 | -66.8375 | -66.7749 | 0.018674 | -66.8185 | 56.1482 | 56.2893 | 56.1277 | -67.024 | -0.10473 | -0.057674 | -0.041951 | -0.008639 | 0.096087 | -0.18528 | -0.043038 | -0.29125 | -0.14302 | -0.042069 | -0.085731 | 0.20552 | -0.001889 | -0.16352 | 122.9663 | 122.8387 | 122.9809 | 66.7662 | -123.1287 | 122.881 | 123.0221 | 122.8605 | 66.7515 | -123.3152
484.8594 | 123.262 | -66.7282 | 56.3141 | 0.012286 | -0.0045812 | 0.0013163 | 0.054363 | -0.0031002 | 0.063358 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.013634 | 0.060658 | -66.7793 | 0.019721 | -66.7414 | 56.2381 | 56.1059 | 56.239 | -66.8467 | -66.7794 | 0.018674 | -66.8185 | 56.1482 | 56.2985 | 56.146 | -67.024 | -0.11846 | -0.075983 | -0.051108 | -0.013217 | 0.10524 | -0.20817 | -0.075083 | -0.29583 | -0.16591 | -0.051226 | -0.090309 | 0.20552 | -0.01562 | -0.16809 | 122.9663 | 122.8341 | 122.9672 | 66.7479 | -123.1608 | 122.8764 | 123.0267 | 122.8742 | 66.7469 | -123.3381
485.7969 | 123.23 | -66.7511 | 56.3232 | -0.0029761 | -0.0047948 | 0.0015299 | 0.054363 | -0.0028866 | 0.062503 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060167 | 0.013421 | 0.060658 | -66.7793 | 0.028878 | -66.746 | 56.2381 | 56.1105 | 56.2482 | -66.8513 | -66.7794 | 0.023253 | -66.8094 | 56.1528 | 56.2939 | 56.1506 | -67.024 | -0.10015 | -0.085138 | -0.028219 | 0.005094 | 0.10525 | -0.21274 | -0.075081 | -0.27294 | -0.17048 | -0.028337 | -0.058263 | 0.21468 | -0.029353 | -0.17267 | 122.9892 | 122.8616 | 122.9993 | 66.78 | -123.1745 | 122.9039 | 123.045 | 122.9017 | 66.7744 | -123.3473
486.7969 | 123.2712 | -66.7786 | 56.3278 | 0.0046549 | -0.0047948 | 0.0015299 | 0.054577 | -0.0031002 | 0.063144 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.013634 | 0.060658 | -66.7793 | 0.028878 | -66.7414 | 56.2381 | 56.1151 | 56.2482 | -66.8421 | -66.7749 | 0.023253 | -66.8094 | 56.1482 | 56.2985 | 56.146 | -67.024 | -0.063529 | -0.089716 | -0.000754 | 0.037137 | 0.10067 | -0.21274 | -0.079659 | -0.24547 | -0.17964 | 0.003707 | -0.030798 | 0.21468 | -0.029353 | -0.18182 | 123.0167 | 122.8936 | 123.0267 | 66.8074 | -123.1699 | 122.9267 | 123.077 | 122.9246 | 66.8018 | -123.3519
487.7969 | 123.2162 | -66.7603 | 56.3553 | 0.0046549 | -0.0047948 | 0.0013163 | 0.054149 | -0.0031002 | 0.063358 | 0.00015261 | -0.00091653 | -0.0011965 | 0.059954 | 0.013421 | 0.060872 | -66.7702 | 0.0243 | -66.7414 | 56.2427 | 56.1013 | 56.2436 | -66.8467 | -66.7749 | 0.023253 | -66.8139 | 56.1573 | 56.2985 | 56.1414 | -67.0195 | -0.086418 | -0.1126 | -0.009907 | 0.018827 | 0.10524 | -0.25394 | -0.1117 | -0.2592 | -0.19795 | -0.014603 | -0.053687 | 0.20552 | -0.056819 | -0.21387 | 123.0029 | 122.8616 | 123.0038 | 66.7846 | -123.202 | 122.9176 | 123.0587 | 122.9017 | 66.7835 | -123.3747
488.7969 | 123.2254 | -66.7831 | 56.3187 | 0.0046549 | -0.0047948 | 0.0015299 | 0.054577 | -0.003314 | 0.062717 | 0.015414 | -0.00091653 | -0.0016237 | 0.060381 | 0.013634 | 0.060445 | -66.7839 | 0.028878 | -66.7414 | 56.2427 | 56.1197 | 56.2482 | -66.8467 | -66.7794 | 0.03241 | -66.8185 | 56.1528 | 56.2985 | 56.1368 | -67.0286 | -0.06353 | -0.075983 | -0.000754 | 0.041715 | 0.10524 | -0.19901 | -0.070504 | -0.24547 | -0.16591 | 0.003706 | -0.035377 | 0.2101 | -0.020198 | -0.18183 | 123.0258 | 122.9028 | 123.0313 | 66.812 | -123.1653 | 122.9359 | 123.0816 | 122.92 | 66.8156 | -123.3473
489.7969 | 123.2071 | -66.7969 | 56.337 | 0.012286 | -0.0045812 | 0.0015299 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060381 | 0.013207 | 0.060658 | -66.7793 | 0.033457 | -66.7414 | 56.2427 | 56.1105 | 56.2436 | -66.8467 | -66.784 | 0.018674 | -66.8231 | 56.1528 | 56.2985 | 56.146 | -67.024 | -0.049797 | -0.094293 | 0.017557 | 0.055448 | 0.10524 | -0.22648 | -0.093392 | -0.22716 | -0.18422 | 0.012861 | -0.026223 | 0.20094 | -0.038508 | -0.19098 | 123.0396 | 122.9074 | 123.0405 | 66.8303 | -123.1836 | 122.9496 | 123.0953 | 122.9429 | 66.8155 | -123.361
490.875 | 123.2391 | -66.7786 | 56.3049 | 0.0046549 | -0.0047948 | 0.0013163 | 0.054577 | -0.0031002 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060381 | 0.013848 | 0.060872 | -66.7747 | 0.028878 | -66.7368 | 56.2427 | 56.1105 | 56.2482 | -66.8558 | -66.7794 | 0.018674 | -66.8185 | 56.1436 | 56.2985 | 56.146 | -67.024 | -0.077266 | -0.06225 | 0.003825 | 0.041716 | 0.11898 | -0.19443 | -0.056771 | -0.24547 | -0.16133 | -0.000872 | -0.039955 | 0.20552 | -0.006465 | -0.15894 | 123.0212 | 122.8891 | 123.0267 | 66.8074 | -123.1608 | 122.9222 | 123.077 | 122.9246 | 66.7972 | -123.329
491.7969 | 123.2346 | -66.7603 | 56.2958 | 0.019917 | -0.0047948 | 0.0017435 | 0.054363 | -0.003314 | 0.06293 | 0.00015261 | -0.0013437 | -0.0011965 | 0.060381 | 0.014062 | 0.060872 | -66.7747 | 0.0243 | -66.7323 | 56.2335 | 56.1059 | 56.2436 | -66.8513 | -66.7794 | 0.023253 | -66.8139 | 56.1482 | 56.2939 | 56.1414 | -67.0332 | -0.090997 | -0.062251 | -0.014485 | 0.027984 | 0.11898 | -0.18985 | -0.052193 | -0.27294 | -0.14759 | -0.019182 | -0.053687 | 0.21925 | -0.001887 | -0.15436 | 122.9938 | 122.8662 | 123.0038 | 66.7846 | -123.147 | 122.9084 | 123.0541 | 122.9017 | 66.7835 | -123.329
492.7969 | 123.1979 | -66.7969 | 56.3187 | -0.0029761 | -0.0043674 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.013421 | 0.060872 | -66.7793 | 0.028878 | -66.7323 | 56.2427 | 56.0922 | 56.2482 | -66.8513 | -66.7794 | 0.027831 | -66.8277 | 56.1528 | 56.2893 | 56.1414 | -67.0195 | -0.054376 | -0.075983 | 0.017557 | 0.064605 | 0.11898 | -0.22648 | -0.070504 | -0.22258 | -0.16591 | 0.017439 | -0.030802 | 0.19178 | -0.029355 | -0.17725 | 123.0396 | 122.8891 | 123.045 | 66.8258 | -123.1699 | 122.9496 | 123.0862 | 122.9383 | 66.8247 | -123.3381
493.7969 | 123.2346 | -66.7648 | 56.3324 | 0.0046549 | -0.0050084 | 0.0015299 | 0.054577 | -0.0031002 | 0.063144 | 0.00015261 | -0.0013437 | -0.0011965 | 0.060167 | 0.013634 | 0.061086 | -66.7747 | 0.0243 | -66.7368 | 56.2427 | 56.1013 | 56.2482 | -66.8604 | -66.7749 | 0.027831 | -66.8185 | 56.1482 | 56.2847 | 56.1506 | -67.024 | -0.095576 | -0.089715 | -0.009907 | 0.027984 | 0.12356 | -0.23105 | -0.084236 | -0.25921 | -0.18422 | -0.010025 | -0.053687 | 0.20552 | -0.047666 | -0.18182 | 123.0075 | 122.8662 | 123.013 | 66.7891 | -123.1928 | 122.913 | 123.0496 | 122.9154 | 66.7927 | -123.3564
494.7969 | 123.1659 | -66.8152 | 56.3049 | -0.010607 | -0.0047948 | 0.0017435 | 0.054363 | -0.0031002 | 0.063144 | 0.023044 | -0.00091653 | -0.0011965 | 0.060167 | 0.014062 | 0.060231 | -66.7793 | 0.019721 | -66.7323 | 56.2335 | 56.1105 | 56.2482 | -66.8467 | -66.7794 | 0.018674 | -66.8185 | 56.1436 | 56.2939 | 56.146 | -67.0195 | -0.031486 | -0.071407 | 0.035868 | 0.082916 | 0.1144 | -0.19443 | -0.056771 | -0.20427 | -0.16133 | 0.03575 | -0.003333 | 0.20094 | -0.011043 | -0.15894 | 123.0487 | 122.9257 | 123.0633 | 66.8349 | -123.1516 | 122.9588 | 123.1091 | 122.9612 | 66.8339 | -123.3244
495.875 | 123.262 | -66.7648 | 56.2958 | 0.012286 | -0.0045812 | 0.0013163 | 0.054149 | -0.0031002 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060595 | 0.013848 | 0.060658 | -66.7747 | 0.019721 | -66.7368 | 56.2427 | 56.0968 | 56.2527 | -66.8467 | -66.7749 | 0.018674 | -66.8185 | 56.1482 | 56.2939 | 56.1368 | -67.024 | -0.08184 | -0.053094 | -0.009907 | 0.027984 | 0.10982 | -0.19901 | -0.043036 | -0.25921 | -0.14759 | -0.010025 | -0.053687 | 0.20552 | -0.001887 | -0.15894 | 123.0075 | 122.8616 | 123.0176 | 66.7846 | -123.1424 | 122.913 | 123.0587 | 122.9017 | 66.7835 | -123.3198
496.7969 | 123.1979 | -66.8152 | 56.3141 | -0.0029761 | -0.0047948 | 0.0013163 | 0.054577 | -0.0031002 | 0.062717 | 0.015414 | -0.00091653 | -0.0011965 | 0.060595 | 0.013848 | 0.060658 | -66.7747 | 0.0243 | -66.7414 | 56.2381 | 56.1013 | 56.2527 | -66.8467 | -66.7703 | 0.027831 | -66.8231 | 56.1528 | 56.2939 | 56.1414 | -67.0195 | -0.031486 | -0.075983 | 0.040447 | 0.073759 | 0.10524 | -0.21274 | -0.061347 | -0.20427 | -0.16133 | 0.044908 | -0.007912 | 0.19636 | -0.020198 | -0.17267 | 123.0533 | 122.9165 | 123.0679 | 66.8395 | -123.1608 | 122.9679 | 123.1091 | 122.9566 | 66.843 | -123.3335
497.7969 | 123.2346 | -66.7877 | 56.3004 | 0.0046549 | -0.0045812 | 0.0013163 | 0.054149 | -0.0028866 | 0.06293 | -0.0074779 | -0.00091653 | -0.00076913 | 0.060381 | 0.013848 | 0.060872 | -66.7656 | 0.0243 | -66.746 | 56.2381 | 56.1059 | 56.2482 | -66.8513 | -66.7794 | 0.027831 | -66.8185 | 56.1482 | 56.2939 | 56.1414 | -67.0195 | -0.063531 | -0.06225 | 0.022137 | 0.041715 | 0.10525 | -0.19443 | -0.052193 | -0.23174 | -0.15217 | 0.008284 | -0.030799 | 0.20094 | -0.006465 | -0.15894 | 123.0258 | 122.8936 | 123.0359 | 66.812 | -123.1516 | 122.9359 | 123.0816 | 122.9291 | 66.8156 | -123.3198
498.8594 | 123.2529 | -66.7511 | 56.3232 | 0.0046549 | -0.0047948 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060167 | 0.013634 | 0.060445 | -66.7793 | 0.033457 | -66.7414 | 56.2427 | 56.1105 | 56.2527 | -66.8421 | -66.7794 | 0.023253 | -66.8139 | 56.1482 | 56.2939 | 56.1231 | -67.024 | -0.090994 | -0.08056 | -0.028219 | 0.009672 | 0.10067 | -0.21274 | -0.070502 | -0.27294 | -0.17506 | -0.028337 | -0.062842 | 0.2101 | -0.029353 | -0.20014 | 122.9938 | 122.8616 | 123.0038 | 66.7846 | -123.1653 | 122.8993 | 123.045 | 122.8742 | 66.7744 | -123.3473
499.7969 | 123.1888 | -66.8015 | 56.3416 | 0.012286 | -0.0045812 | 0.0011025 | 0.053936 | -0.0031002 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.060381 | 0.013634 | 0.060872 | -66.7702 | 0.028878 | -66.7414 | 56.2335 | 56.1059 | 56.2482 | -66.8513 | -66.7794 | 0.023253 | -66.8185 | 56.1528 | 56.2939 | 56.1414 | -67.0195 | -0.049798 | -0.10803 | 0.031292 | 0.060026 | 0.10982 | -0.23563 | -0.093392 | -0.21801 | -0.18879 | 0.022017 | -0.017066 | 0.20094 | -0.047664 | -0.20013 | 123.035 | 122.9074 | 123.0496 | 66.8303 | -123.1928 | 122.9542 | 123.0953 | 122.9429 | 66.8247 | -123.361
500.7969 | 123.2941 | -66.7511 | 56.2912 | 0.0046549 | -0.0047948 | 0.0013163 | 0.054791 | -0.0028866 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.013634 | 0.060872 | -66.7702 | 0.0243 | -66.7323 | 56.2381 | 56.1059 | 56.239 | -66.8375 | -66.7749 | 0.027831 | -66.8139 | 56.1436 | 56.2939 | 56.1414 | -67.0286 | -0.086415 | -0.053095 | -0.019062 | 0.018829 | 0.10524 | -0.18528 | -0.052195 | -0.27752 | -0.1476 | -0.023758 | -0.062842 | 0.21467 | 0.00269 | -0.14978 | 122.9892 | 122.857 | 122.9901 | 66.7754 | -123.1287 | 122.8947 | 123.045 | 122.8925 | 66.7789 | -123.3198
501.8594 | 123.2071 | -66.7648 | 56.3187 | 0.0046549 | -0.0050084 | 0.0017435 | 0.054149 | -0.003314 | 0.06293 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060381 | 0.014062 | 0.060872 | -66.7702 | 0.0243 | -66.746 | 56.2427 | 56.1013 | 56.2573 | -66.8467 | -66.7794 | 0.018674 | -66.8139 | 56.1528 | 56.2985 | 56.1506 | -67.0286 | -0.08184 | -0.075983 | -0.005329 | 0.018827 | 0.10067 | -0.21732 | -0.061347 | -0.26378 | -0.16591 | -0.014604 | -0.049109 | 0.21467 | -0.020198 | -0.16809 | 123.0075 | 122.8662 | 123.0221 | 66.7891 | -123.1653 | 122.9176 | 123.0633 | 122.9154 | 66.7835 | -123.3473
502.7969 | 123.3078 | -66.7374 | 56.2775 | 0.019917 | -0.0052222 | 0.0015299 | 0.054149 | -0.0028866 | 0.063144 | 0.0077831 | -0.00091653 | -0.00055553 | 0.060381 | 0.013848 | 0.060445 | -66.7747 | 0.019721 | -66.7506 | 56.2427 | 56.1059 | 56.2482 | -66.8467 | -66.7749 | 0.023253 | -66.8139 | 56.1482 | 56.2893 | 56.1368 | -67.0195 | -0.10931 | -0.034784 | -0.037373 | -0.013217 | 0.096089 | -0.17154 | -0.029305 | -0.28209 | -0.12928 | -0.037491 | -0.076575 | 0.20552 | 0.011844 | -0.14063 | 122.98 | 122.8433 | 122.9855 | 66.7571 | -123.1241 | 122.8855 | 123.0267 | 122.8742 | 66.7606 | -123.2969
503.7969 | 123.2391 | -66.7877 | 56.2958 | -0.010607 | -0.0045812 | 0.0015299 | 0.054363 | -0.0031002 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060167 | 0.013848 | 0.060231 | -66.7747 | 0.033457 | -66.7414 | 56.2381 | 56.0876 | 56.2482 | -66.8467 | -66.7611 | 0.023253 | -66.8185 | 56.1482 | 56.2939 | 56.1277 | -67.024 | -0.058952 | -0.057672 | 0.012981 | 0.046293 | 0.10524 | -0.20817 | -0.047615 | -0.23632 | -0.14759 | 0.026599 | -0.030799 | 0.20552 | -0.001887 | -0.16809 | 123.0258 | 122.8753 | 123.0359 | 66.8212 | -123.1424 | 122.9359 | 123.0816 | 122.9154 | 66.811 | -123.3198
504.7969 | 123.2712 | -66.7374 | 56.3141 | -0.0029761 | -0.0050084 | 0.0015299 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.0011301 | -0.0014101 | 0.060167 | 0.013634 | 0.060231 | -66.7747 | 0.0243 | -66.7368 | 56.2335 | 56.1059 | 56.2527 | -66.8467 | -66.7794 | 0.023253 | -66.8185 | 56.1528 | 56.2985 | 56.1368 | -67.0286 | -0.10931 | -0.080562 | -0.037373 | 0.000518 | 0.10982 | -0.20817 | -0.061347 | -0.29125 | -0.16133 | -0.04207 | -0.081153 | 0.2101 | -0.01562 | -0.17725 | 122.9709 | 122.8433 | 122.9901 | 66.7617 | -123.1608 | 122.8901 | 123.0358 | 122.8742 | 66.7606 | -123.3427
505.875 | 123.3261 | -66.7282 | 56.2866 | 0.0046549 | -0.0050084 | 0.00088894 | 0.054577 | -0.0031002 | 0.06293 | -0.0074779 | -0.0011301 | -0.00076913 | 0.060381 | 0.013848 | 0.060231 | -66.7793 | 0.028878 | -66.7368 | 56.2427 | 56.0968 | 56.2436 | -66.8558 | -66.7749 | 0.014095 | -66.8277 | 56.1482 | 56.2939 | 56.146 | -67.0195 | -0.12762 | -0.043939 | -0.051108 | -0.008638 | 0.11898 | -0.18986 | -0.043038 | -0.29125 | -0.13844 | -0.046647 | -0.099467 | 0.19178 | 0.007268 | -0.14062 | 122.9709 | 122.825 | 122.9718 | 66.7571 | -123.1425 | 122.8764 | 123.0221 | 122.8742 | 66.7423 | -123.3061
506.7969 | 123.2941 | -66.7465 | 56.2866 | -0.0029761 | -0.0052222 | 0.0015299 | 0.054791 | -0.0028866 | 0.062503 | 0.00015261 | -0.00091653 | -0.00098273 | 0.060167 | 0.013848 | 0.060658 | -66.7747 | 0.0243 | -66.7368 | 56.2381 | 56.1013 | 56.2482 | -66.8467 | -66.7703 | 0.018674 | -66.8185 | 56.1528 | 56.2939 | 56.1277 | -67.024 | -0.10015 | -0.048517 | -0.028218 | 0.009673 | 0.10982 | -0.18528 | -0.03846 | -0.27752 | -0.13386 | -0.023757 | -0.071998 | 0.20552 | 0.007268 | -0.15894 | 122.9846 | 122.8479 | 122.9947 | 66.7708 | -123.1333 | 122.8993 | 123.0404 | 122.8742 | 66.7652 | -123.3107
507.7969 | 123.3078 | -66.7099 | 56.2866 | 0.0046549 | -0.0050084 | 0.0015299 | 0.054577 | -0.002673 | 0.063144 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060167 | 0.014062 | 0.060872 | -66.7747 | 0.028878 | -66.7414 | 56.2427 | 56.1059 | 56.2482 | -66.8513 | -66.784 | 0.014095 | -66.8139 | 56.1482 | 56.2939 | 56.1323 | -67.024 | -0.14135 | -0.043939 | -0.064839 | -0.031527 | 0.10982 | -0.1807 | -0.03846 | -0.31414 | -0.13844 | -0.074114 | -0.10404 | 0.2101 | 0.007268 | -0.15436 | 122.9526 | 122.8158 | 122.9581 | 66.7388 | -123.1379 | 122.8581 | 123.0038 | 122.8422 | 66.724 | -123.3107
508.8594 | 123.2986 | -66.7557 | 56.2683 | -0.0029761 | -0.0050084 | 0.0013163 | 0.054363 | -0.0028866 | 0.062503 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.013634 | 0.060231 | -66.7702 | 0.0243 | -66.7277 | 56.2335 | 56.0968 | 56.2436 | -66.8558 | -66.7703 | 0.018674 | -66.8139 | 56.1528 | 56.2939 | 56.1368 | -67.0195 | -0.10015 | -0.034786 | -0.014485 | 0.027984 | 0.12814 | -0.17155 | -0.024728 | -0.26378 | -0.11555 | -0.014602 | -0.058265 | 0.20552 | 0.025578 | -0.13147 | 122.9892 | 122.8524 | 122.9993 | 66.78 | -123.1241 | 122.9084 | 123.0496 | 122.8925 | 66.7743 | -123.2878
509.7969 | 123.2849 | -66.7557 | 56.282 | -0.0029761 | -0.0050084 | 0.0015299 | 0.054363 | -0.002673 | 0.062717 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.014062 | 0.060658 | -66.7702 | 0.0243 | -66.7414 | 56.2244 | 56.1013 | 56.2436 | -66.8421 | -66.7794 | 0.023253 | -66.8139 | 56.1436 | 56.2985 | 56.1414 | -67.024 | -0.086417 | -0.057675 | -0.014485 | 0.014249 | 0.10067 | -0.1807 | -0.03846 | -0.26836 | -0.13844 | -0.02376 | -0.058265 | 0.2101 | 0.016424 | -0.14062 | 122.98 | 122.857 | 122.9993 | 66.78 | -123.1241 | 122.8993 | 123.0541 | 122.8971 | 66.7789 | -123.3061
510.875 | 123.3124 | -66.7282 | 56.3049 | 0.0046549 | -0.0052222 | 0.0015299 | 0.054791 | -0.0028866 | 0.06293 | 0.0077831 | -0.0011301 | -0.00098273 | 0.060381 | 0.014062 | 0.060231 | -66.7747 | 0.0243 | -66.7368 | 56.2335 | 56.0968 | 56.2482 | -66.8467 | -66.7657 | 0.009516 | -66.8139 | 56.1482 | 56.2847 | 56.1368 | -67.0286 | -0.11846 | -0.071407 | -0.046529 | -0.008638 | 0.10982 | -0.20817 | -0.056771 | -0.30041 | -0.15675 | -0.037489 | -0.085731 | 0.21467 | -0.020201 | -0.16809 | 122.9617 | 122.825 | 122.9764 | 66.7525 | -123.1516 | 122.8764 | 123.0129 | 122.865 | 66.7377 | -123.3335
511.7969 | 123.2666 | -66.7465 | 56.2912 | -0.0029761 | -0.0045812 | 0.0015299 | 0.054791 | -0.0031002 | 0.062717 | -0.0074779 | -0.00091653 | -0.00076913 | 0.060381 | 0.014275 | 0.060445 | -66.7747 | 0.0243 | -66.7323 | 56.2381 | 56.1105 | 56.2527 | -66.8375 | -66.7749 | 0.014095 | -66.8185 | 56.1528 | 56.2893 | 56.146 | -67.024 | -0.090993 | -0.053095 | -0.028218 | 0.014251 | 0.10524 | -0.1807 | -0.038459 | -0.27752 | -0.13844 | -0.028336 | -0.071998 | 0.20552 | -0.001889 | -0.1452 | 122.9846 | 122.857 | 122.9993 | 66.7708 | -123.1287 | 122.8993 | 123.0358 | 122.8925 | 66.7606 | -123.3152
512.8594 | 123.2803 | -66.7419 | 56.282 | -0.0029761 | -0.0047948 | 0.0015299 | 0.054577 | -0.003314 | 0.062717 | -0.0074779 | -0.00070293 | -0.0011965 | 0.060381 | 0.014062 | 0.060445 | -66.7793 | 0.028878 | -66.746 | 56.2335 | 56.0922 | 56.2436 | -66.8421 | -66.7749 | 0.023253 | -66.8185 | 56.1528 | 56.2985 | 56.146 | -67.0286 | -0.10015 | -0.048518 | -0.037375 | -0.004062 | 0.096088 | -0.18986 | -0.03846 | -0.28667 | -0.12928 | -0.032914 | -0.076576 | 0.2101 | 0.016424 | -0.13605 | 122.9755 | 122.8341 | 122.9855 | 66.7708 | -123.1241 | 122.8947 | 123.0404 | 122.8879 | 66.7652 | -123.3107
513.7969 | 123.2803 | -66.7191 | 56.2958 | 0.0046549 | -0.0052222 | 0.0017435 | 0.054577 | -0.0028866 | 0.062503 | 0.00015261 | -0.0011301 | -0.0011965 | 0.060167 | 0.014275 | 0.060445 | -66.7747 | 0.0243 | -66.7323 | 56.2473 | 56.1059 | 56.2482 | -66.8421 | -66.7703 | 0.018674 | -66.8185 | 56.1436 | 56.2985 | 56.1368 | -67.024 | -0.12304 | -0.048516 | -0.055684 | -0.013215 | 0.10982 | -0.18985 | -0.047615 | -0.30498 | -0.15217 | -0.051223 | -0.099464 | 0.20552 | 0.002691 | -0.15894 | 122.9663 | 122.825 | 122.9672 | 66.7434 | -123.1379 | 122.8627 | 123.0175 | 122.8559 | 66.7377 | -123.3198
514.7969 | 123.3215 | -66.7282 | 56.282 | -0.0029761 | -0.0054358 | 0.0015299 | 0.054791 | -0.0028866 | 0.06293 | 0.00015261 | -0.00070293 | -0.00076913 | 0.060381 | 0.013848 | 0.060445 | -66.7747 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2527 | -66.8375 | -66.7657 | 0.018674 | -66.8231 | 56.1528 | 56.2985 | 56.1277 | -67.0286 | -0.1093 | -0.043939 | -0.046529 | -0.008638 | 0.10067 | -0.17154 | -0.029303 | -0.30041 | -0.12928 | -0.037489 | -0.094888 | 0.20552 | 0.016424 | -0.15436 | 122.9663 | 122.8387 | 122.981 | 66.7571 | -123.1196 | 122.881 | 123.0267 | 122.8559 | 66.7469 | -123.3107
515.7969 | 123.2254 | -66.7465 | 56.3416 | 0.0046549 | -0.0050084 | 0.0011025 | 0.054577 | -0.003314 | 0.06293 | -0.0074779 | -0.00091653 | -0.00076913 | 0.060167 | 0.013848 | 0.060231 | -66.7793 | 0.0243 | -66.7414 | 56.2381 | 56.1151 | 56.2436 | -66.8467 | -66.7749 | 0.014095 | -66.8231 | 56.1482 | 56.2985 | 56.1368 | -67.0332 | -0.10015 | -0.10345 | -0.032797 | 0.005094 | 0.10524 | -0.22647 | -0.09797 | -0.28667 | -0.19337 | -0.028336 | -0.076577 | 0.2101 | -0.043086 | -0.20471 | 122.9846 | 122.8616 | 122.9901 | 66.7708 | -123.1882 | 122.8947 | 123.045 | 122.8834 | 66.7606 | -123.3747
516.7969 | 123.3078 | -66.7236 | 56.3187 | -0.0029761 | -0.0052222 | 0.0015299 | 0.054791 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.014275 | 0.060445 | -66.7702 | 0.028878 | -66.7277 | 56.2335 | 56.1013 | 56.2482 | -66.8513 | -66.7657 | 0.014095 | -66.8139 | 56.1573 | 56.2939 | 56.1277 | -67.0286 | -0.12762 | -0.08514 | -0.046528 | -0.004059 | 0.12356 | -0.21732 | -0.070504 | -0.30498 | -0.16133 | -0.042066 | -0.090308 | 0.21467 | -0.024776 | -0.19098 | 122.9572 | 122.825 | 122.9718 | 66.7525 | -123.1699 | 122.881 | 123.0175 | 122.8513 | 66.7377 | -123.3473
517.8594 | 123.2803 | -66.7328 | 56.2729 | -0.0029761 | -0.0047948 | 0.0013163 | 0.054791 | -0.0028866 | 0.062717 | 0.00015261 | -0.0011301 | -0.0014101 | 0.05974 | 0.013848 | 0.060445 | -66.7747 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2573 | -66.8467 | -66.7749 | 0.023253 | -66.8094 | 56.1528 | 56.2985 | 56.146 | -67.0332 | -0.11388 | -0.034784 | -0.041951 | -0.00406 | 0.10982 | -0.16239 | -0.01557 | -0.30041 | -0.12013 | -0.042069 | -0.076574 | 0.22383 | 0.025579 | -0.12689 | 122.9709 | 122.8433 | 122.9901 | 66.7617 | -123.1196 | 122.8855 | 123.0313 | 122.8788 | 66.756 | -123.3061
518.7969 | 123.1796 | -66.7786 | 56.337 | 0.0046549 | -0.0050084 | 0.0015299 | 0.054577 | -0.0031002 | 0.06293 | 0.015414 | -0.0011301 | -0.00076913 | 0.060167 | 0.013848 | 0.060445 | -66.7747 | 0.028878 | -66.7277 | 56.2381 | 56.1105 | 56.2527 | -66.8513 | -66.7703 | 0.018674 | -66.8139 | 56.1482 | 56.2985 | 56.146 | -67.0332 | -0.072687 | -0.098871 | 0.003825 | 0.050872 | 0.12356 | -0.22648 | -0.084235 | -0.25463 | -0.18879 | 0.008286 | -0.035377 | 0.21925 | -0.038508 | -0.19098 | 123.0167 | 122.8891 | 123.0313 | 66.8074 | -123.1882 | 122.9267 | 123.077 | 122.9246 | 66.7972 | -123.3702
519.7969 | 123.2895 | -66.7374 | 56.3187 | 0.012286 | -0.0050084 | 0.00088894 | 0.054149 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.059954 | 0.014062 | 0.060231 | -66.7793 | 0.019721 | -66.7414 | 56.2427 | 56.1105 | 56.2527 | -66.8329 | -66.7749 | 0.018674 | -66.8139 | 56.1528 | 56.2985 | 56.1414 | -67.0286 | -0.095569 | -0.075983 | -0.041952 | -0.004061 | 0.091508 | -0.20817 | -0.065925 | -0.29125 | -0.16591 | -0.037491 | -0.076575 | 0.21467 | -0.020198 | -0.17725 | 122.98 | 122.8479 | 122.9901 | 66.7571 | -123.1516 | 122.8901 | 123.0358 | 122.8788 | 66.756 | -123.3473
520.7969 | 123.2391 | -66.774 | 56.3141 | 0.0046549 | -0.0052222 | 0.0013163 | 0.054577 | -0.0031002 | 0.06293 | -0.0074779 | -0.00091653 | -0.00055553 | 0.060595 | 0.014062 | 0.060658 | -66.7793 | 0.0243 | -66.7323 | 56.2381 | 56.1013 | 56.2527 | -66.8513 | -66.7657 | 0.014095 | -66.8139 | 56.1482 | 56.303 | 56.1414 | -67.0195 | -0.077264 | -0.075983 | -0.005331 | 0.041717 | 0.11898 | -0.21274 | -0.061347 | -0.24547 | -0.16591 | 0.008288 | -0.039954 | 0.20552 | -0.011041 | -0.17267 | 123.0121 | 122.8753 | 123.0267 | 66.7983 | -123.1653 | 122.9222 | 123.077 | 122.9154 | 66.7881 | -123.3335
521.8594 | 123.2849 | -66.7419 | 56.2775 | -0.010607 | -0.0050084 | 0.0013163 | 0.054577 | -0.0028866 | 0.062717 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060167 | 0.014275 | 0.060445 | -66.7747 | 0.0243 | -66.7231 | 56.2381 | 56.1105 | 56.2482 | -66.8421 | -66.7794 | 0.014095 | -66.8094 | 56.1482 | 56.2985 | 56.1368 | -67.024 | -0.10015 | -0.039362 | -0.032796 | 0.01883 | 0.11898 | -0.16697 | -0.029305 | -0.28209 | -0.12928 | -0.037493 | -0.067419 | 0.21468 | 0.021001 | -0.14063 | 122.98 | 122.8524 | 122.9901 | 66.7662 | -123.1196 | 122.8901 | 123.0404 | 122.8788 | 66.756 | -123.3015
522.7969 | 123.2346 | -66.7694 | 56.3782 | 0.0046549 | -0.0050084 | 0.0017435 | 0.054149 | -0.002673 | 0.062717 | 0.00015261 | -0.00070293 | -0.0014101 | 0.060167 | 0.014062 | 0.060231 | -66.7702 | 0.0243 | -66.7323 | 56.2427 | 56.0922 | 56.2482 | -66.8421 | -66.7611 | 0.014095 | -66.8094 | 56.1528 | 56.2939 | 56.1414 | -67.0332 | -0.072684 | -0.13549 | -0.000752 | 0.037139 | 0.10982 | -0.28599 | -0.13001 | -0.26379 | -0.22541 | 0.008288 | -0.039953 | 0.22383 | -0.084285 | -0.23676 | 123.0121 | 122.8616 | 123.0176 | 66.7937 | -123.2203 | 122.9222 | 123.0633 | 122.9108 | 66.7835 | -123.4114
523.7969 | 123.2574 | -66.7282 | 56.3049 | 0.0046549 | -0.0050084 | 0.0013163 | 0.054149 | -0.0028866 | 0.062503 | 0.015414 | -0.0011301 | -0.00098273 | 0.059954 | 0.014062 | 0.060445 | -66.7702 | 0.019721 | -66.7323 | 56.2427 | 56.1059 | 56.2482 | -66.8375 | -66.7657 | 0.018674 | -66.8139 | 56.1573 | 56.2939 | 56.146 | -67.0286 | -0.1093 | -0.06225 | -0.041951 | -0.00406 | 0.10524 | -0.19901 | -0.056771 | -0.30041 | -0.14759 | -0.037489 | -0.085731 | 0.21467 | -0.011043 | -0.15894 | 122.9709 | 122.8341 | 122.9764 | 66.7479 | -123.1424 | 122.8855 | 123.0221 | 122.8742 | 66.7469 | -123.3335
524.8594 | 123.2803 | -66.7236 | 56.2958 | 0.0046549 | -0.0050084 | 0.0013163 | 0.054577 | -0.003314 | 0.062717 | 0.0077831 | -0.00070293 | -0.00098273 | 0.060167 | 0.014062 | 0.060231 | -66.7702 | 0.019721 | -66.7323 | 56.2381 | 56.1151 | 56.2619 | -66.8421 | -66.7749 | 0.018674 | -66.8139 | 56.1436 | 56.2985 | 56.1277 | -67.0286 | -0.11846 | -0.057672 | -0.046528 | -0.008637 | 0.10982 | -0.1807 | -0.033879 | -0.30498 | -0.15217 | -0.051224 | -0.090308 | 0.21467 | 0.002691 | -0.16809 | 122.9617 | 122.8387 | 122.9855 | 66.7434 | -123.1379 | 122.8672 | 123.0221 | 122.8513 | 66.7423 | -123.3244
525.7969 | 123.2208 | -66.7511 | 56.3141 | -0.0029761 | -0.0052222 | 0.0013163 | 0.054363 | -0.0028866 | 0.062717 | 0.00015261 | -0.0011301 | -0.00076913 | 0.059954 | 0.014275 | 0.060658 | -66.7747 | 0.019721 | -66.7323 | 56.2335 | 56.1059 | 56.2573 | -66.8513 | -66.7703 | 0.023253 | -66.8139 | 56.1436 | 56.2985 | 56.1323 | -67.0286 | -0.10015 | -0.080562 | -0.02364 | 0.018829 | 0.11898 | -0.20817 | -0.056769 | -0.27752 | -0.17048 | -0.019179 | -0.062842 | 0.21467 | -0.01562 | -0.18183 | 122.9846 | 122.857 | 123.0084 | 66.7708 | -123.1653 | 122.8947 | 123.0496 | 122.8834 | 66.7744 | -123.3427
526.7969 | 123.2208 | -66.7557 | 56.3004 | 0.0046549 | -0.0047948 | 0.0013163 | 0.054363 | -0.0028866 | 0.062503 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060167 | 0.013848 | 0.060231 | -66.7702 | 0.0243 | -66.7368 | 56.2381 | 56.0968 | 56.2573 | -66.8467 | -66.7657 | 0.018674 | -66.8139 | 56.1528 | 56.2893 | 56.1231 | -67.0286 | -0.090996 | -0.06225 | -0.014485 | 0.018828 | 0.10982 | -0.20359 | -0.043036 | -0.27294 | -0.14759 | -0.010023 | -0.058265 | 0.21467 | -0.011044 | -0.17725 | 122.9938 | 122.8524 | 123.013 | 66.78 | -123.147 | 122.9084 | 123.045 | 122.8788 | 66.7743 | -123.329
527.8594 | 123.2803 | -66.7557 | 56.282 | -0.0029761 | -0.0054358 | 0.0015299 | 0.055004 | -0.002673 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060167 | 0.014489 | 0.060445 | -66.7747 | 0.0243 | -66.7277 | 56.2335 | 56.1013 | 56.2482 | -66.8421 | -66.7703 | 0.018674 | -66.8185 | 56.1528 | 56.303 | 56.1323 | -67.0195 | -0.086417 | -0.048518 | -0.019063 | 0.027984 | 0.1144 | -0.1807 | -0.033882 | -0.26378 | -0.12928 | -0.014602 | -0.062843 | 0.20094 | 0.021003 | -0.14978 | 122.9892 | 122.857 | 123.0038 | 66.78 | -123.1241 | 122.9084 | 123.0587 | 122.8879 | 66.7743 | -123.3015
528.7969 | 123.2254 | -66.7694 | 56.3049 | -0.0029761 | -0.0050084 | 0.0015299 | 0.054149 | -0.003314 | 0.062717 | 0.00015261 | -0.00091653 | -0.00098273 | 0.059954 | 0.014275 | 0.060231 | -66.7702 | 0.019721 | -66.7323 | 56.2427 | 56.0968 | 56.2573 | -66.8467 | -66.7749 | 0.014095 | -66.8185 | 56.1436 | 56.2939 | 56.1414 | -67.0286 | -0.077263 | -0.06225 | -0.000752 | 0.037139 | 0.1144 | -0.20817 | -0.047614 | -0.25921 | -0.16133 | -0.005448 | -0.04911 | 0.2101 | -0.011043 | -0.16351 | 123.0121 | 122.8662 | 123.0267 | 66.7891 | -123.1516 | 122.913 | 123.0633 | 122.9108 | 66.7835 | -123.3335
529.8594 | 123.1979 | -66.7511 | 56.3507 | 0.012286 | -0.0054358 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060381 | 0.014489 | 0.060231 | -66.7747 | 0.019721 | -66.7323 | 56.2427 | 56.1013 | 56.2482 | -66.8467 | -66.7749 | 0.027831 | -66.8185 | 56.1573 | 56.2893 | 56.1506 | -67.024 | -0.095573 | -0.10803 | -0.02364 | 0.018829 | 0.1144 | -0.24937 | -0.10255 | -0.27294 | -0.19337 | -0.023758 | -0.06742 | 0.20552 | -0.061398 | -0.20013 | 122.9938 | 122.8524 | 122.9993 | 66.7708 | -123.1974 | 122.9084 | 123.0404 | 122.9017 | 66.7789 | -123.3747
530.7969 | 123.2895 | -66.7465 | 56.2454 | -0.0029761 | -0.0054358 | 0.0013163 | 0.054577 | -0.003314 | 0.063358 | 0.00015261 | -0.0011301 | -0.00076913 | 0.060167 | 0.014489 | 0.060231 | -66.7702 | 0.015142 | -66.7368 | 56.2427 | 56.0968 | 56.2482 | -66.8329 | -66.7749 | 0.018674 | -66.8139 | 56.1436 | 56.2985 | 56.1323 | -67.024 | -0.086414 | -0.00274 | -0.02364 | 0.009673 | 0.096087 | -0.14866 | 0.002739 | -0.27752 | -0.10182 | -0.028336 | -0.06742 | 0.2101 | 0.053045 | -0.11316 | 122.9892 | 122.8433 | 122.9947 | 66.7617 | -123.0784 | 122.8901 | 123.045 | 122.8788 | 66.7652 | -123.2695
531.7969 | 123.2346 | -66.7419 | 56.2958 | -0.010607 | -0.0052222 | 0.0013163 | 0.054363 | -0.0031002 | 0.06293 | 0.0077831 | -0.0011301 | -0.00076913 | 0.060167 | 0.014275 | 0.060445 | -66.7747 | 0.028878 | -66.7414 | 56.2427 | 56.0922 | 56.2573 | -66.8467 | -66.7703 | 0.023253 | -66.8139 | 56.1482 | 56.2939 | 56.1414 | -67.024 | -0.10473 | -0.053094 | -0.032796 | 0.000516 | 0.10524 | -0.20359 | -0.038458 | -0.28209 | -0.14759 | -0.028335 | -0.071998 | 0.2101 | -0.001887 | -0.15436 | 122.9846 | 122.8341 | 122.9993 | 66.7708 | -123.1424 | 122.8901 | 123.0358 | 122.8834 | 66.7652 | -123.3198
532.7969 | 123.175 | -66.7923 | 56.3049 | -0.010607 | -0.0056496 | 0.0013163 | 0.054149 | -0.0031002 | 0.06293 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060381 | 0.014489 | 0.060872 | -66.7702 | 0.019721 | -66.7414 | 56.2427 | 56.1105 | 56.2573 | -66.8467 | -66.7749 | 0.023253 | -66.8139 | 56.1482 | 56.2893 | 56.1368 | -67.024 | -0.054375 | -0.06225 | 0.022136 | 0.05087 | 0.10524 | -0.19443 | -0.047614 | -0.23174 | -0.15675 | 0.01744 | -0.021644 | 0.2101 | -0.015622 | -0.16809 | 123.035 | 122.9028 | 123.0496 | 66.812 | -123.1516 | 122.9405 | 123.0816 | 122.9291 | 66.8156 | -123.329
533.7969 | 123.2117 | -66.7603 | 56.3141 | 0.0046549 | -0.0054358 | 0.0017435 | 0.054363 | -0.003314 | 0.063358 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059954 | 0.014275 | 0.060658 | -66.7747 | 0.0243 | -66.7414 | 56.2473 | 56.1059 | 56.2527 | -66.8513 | -66.7703 | 0.014095 | -66.8048 | 56.1436 | 56.2893 | 56.1323 | -67.0286 | -0.090997 | -0.066827 | -0.014485 | 0.018827 | 0.10982 | -0.20817 | -0.061347 | -0.26836 | -0.17048 | -0.010024 | -0.044529 | 0.22383 | -0.024777 | -0.18183 | 123.0075 | 122.8662 | 123.013 | 66.7846 | -123.1653 | 122.9039 | 123.0496 | 122.8925 | 66.7743 | -123.3427
534.8594 | 123.1796 | -66.7831 | 56.337 | 0.0046549 | -0.0054358 | 0.0011025 | 0.054577 | -0.0028866 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.014489 | 0.060658 | -66.7793 | 0.0243 | -66.7368 | 56.2381 | 56.1013 | 56.2619 | -66.8467 | -66.7794 | 0.018674 | -66.8139 | 56.1528 | 56.303 | 56.146 | -67.0286 | -0.06353 | -0.098871 | 0.003824 | 0.046294 | 0.10982 | -0.23563 | -0.075078 | -0.24547 | -0.18422 | 0.003706 | -0.030799 | 0.21467 | -0.033929 | -0.19098 | 123.0212 | 122.8845 | 123.045 | 66.8074 | -123.1836 | 122.9359 | 123.0862 | 122.9291 | 66.8018 | -123.3656
535.7969 | 123.2483 | -66.7557 | 56.282 | -0.010607 | -0.0052222 | 0.0013163 | 0.054363 | -0.0031002 | 0.062503 | -0.0074779 | -0.0011301 | -0.0011965 | 0.060381 | 0.014275 | 0.060658 | -66.761 | 0.0243 | -66.7368 | 56.2335 | 56.1105 | 56.2482 | -66.8467 | -66.7657 | 0.018674 | -66.8139 | 56.1528 | 56.2893 | 56.1506 | -67.0195 | -0.090996 | -0.048518 | -0.005328 | 0.018828 | 0.10982 | -0.17154 | -0.033882 | -0.26378 | -0.12928 | -0.010023 | -0.058265 | 0.20552 | 0.007267 | -0.13147 | 122.9892 | 122.8662 | 123.0038 | 66.78 | -123.1287 | 122.9084 | 123.045 | 122.9063 | 66.7743 | -123.3015
536.7969 | 123.1796 | -66.7923 | 56.3324 | -0.0029761 | -0.0054358 | 0.0013163 | 0.054577 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060167 | 0.014062 | 0.060445 | -66.7702 | 0.019721 | -66.7368 | 56.2473 | 56.1013 | 56.2527 | -66.8467 | -66.7749 | 0.023253 | -66.8094 | 56.1528 | 56.2939 | 56.1552 | -67.0195 | -0.054375 | -0.085137 | 0.022136 | 0.055449 | 0.10982 | -0.23105 | -0.079657 | -0.22716 | -0.17964 | 0.01744 | -0.017065 | 0.2101 | -0.038508 | -0.17724 | 123.0396 | 122.8936 | 123.045 | 66.812 | -123.1791 | 122.9451 | 123.0862 | 122.9475 | 66.8156 | -123.3519
537.8438 | 123.1888 | -66.7465 | 56.3141 | 0.012286 | -0.0054358 | 0.0015299 | 0.054363 | -0.003314 | 0.063144 | 0.00015261 | -0.00091653 | -0.00076913 | 0.060381 | 0.013848 | 0.060445 | -66.7702 | 0.015142 | -66.7414 | 56.2381 | 56.1105 | 56.2527 | -66.8467 | -66.7703 | 0.014095 | -66.8094 | 56.1573 | 56.2985 | 56.1414 | -67.024 | -0.10015 | -0.075983 | -0.02364 | 0.005094 | 0.10524 | -0.20359 | -0.061347 | -0.27752 | -0.15675 | -0.023757 | -0.062841 | 0.21468 | -0.01562 | -0.17267 | 122.9846 | 122.857 | 122.9993 | 66.7617 | -123.1608 | 122.9039 | 123.045 | 122.8879 | 66.7606 | -123.3381
538.7969 | 123.2162 | -66.7511 | 56.2958 | -0.0029761 | -0.0058632 | 0.0015299 | 0.055004 | -0.0028866 | 0.063358 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060167 | 0.014489 | 0.060231 | -66.7702 | 0.028878 | -66.7414 | 56.2289 | 56.1059 | 56.2482 | -66.8467 | -66.7749 | 0.009516 | -66.8094 | 56.1436 | 56.2985 | 56.1414 | -67.0195 | -0.095573 | -0.066829 | -0.019062 | 0.009672 | 0.10524 | -0.18985 | -0.047615 | -0.26836 | -0.15217 | -0.023758 | -0.058263 | 0.2101 | 0.002691 | -0.15436 | 122.98 | 122.857 | 122.9993 | 66.78 | -123.1424 | 122.8947 | 123.0496 | 122.8925 | 66.7606 | -123.3152
539.7969 | 123.1659 | -66.7786 | 56.337 | -0.0029761 | -0.0056496 | 0.0015299 | 0.054363 | -0.0031002 | 0.06293 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060167 | 0.014489 | 0.060658 | -66.7702 | 0.019721 | -66.7414 | 56.2427 | 56.1197 | 56.2527 | -66.8375 | -66.7749 | 0.018674 | -66.8094 | 56.1528 | 56.2985 | 56.1414 | -67.0286 | -0.05895 | -0.094293 | 0.008403 | 0.037137 | 0.096087 | -0.21732 | -0.084235 | -0.25005 | -0.18422 | 0.003707 | -0.030798 | 0.21925 | -0.038508 | -0.19556 | 123.0212 | 122.8982 | 123.0313 | 66.7983 | -123.1745 | 122.9313 | 123.077 | 122.92 | 66.7972 | -123.3656
540.7969 | 123.3124 | -66.7191 | 56.2912 | -0.0029761 | -0.0054358 | 0.0015299 | 0.054791 | -0.0028866 | 0.063144 | 0.00015261 | -0.0011301 | -0.0014101 | 0.059954 | 0.014275 | 0.060658 | -66.7747 | 0.019721 | -66.7368 | 56.2335 | 56.1059 | 56.2573 | -66.8467 | -66.7703 | 0.018674 | -66.8139 | 56.1528 | 56.2985 | 56.146 | -67.0286 | -0.12762 | -0.057674 | -0.055684 | -0.017793 | 0.10982 | -0.18528 | -0.033881 | -0.30956 | -0.13844 | -0.051223 | -0.094886 | 0.21467 | 0.007268 | -0.1452 | 122.9526 | 122.825 | 122.9764 | 66.7388 | -123.1379 | 122.8718 | 123.0175 | 122.8651 | 66.7377 | -123.3198
541.8281 | 123.1888 | -66.7511 | 56.3049 | 0.0046549 | -0.0054358 | 0.0013163 | 0.054149 | -0.0031002 | 0.063144 | 0.00015261 | -0.00091653 | -0.0014101 | 0.060381 | 0.014275 | 0.060445 | -66.7747 | 0.0243 | -66.7414 | 56.2381 | 56.1151 | 56.2482 | -66.8467 | -66.7794 | 0.018674 | -66.8139 | 56.1573 | 56.2893 | 56.1323 | -67.0286 | -0.095573 | -0.066828 | -0.02364 | 0.009672 | 0.10524 | -0.18985 | -0.056771 | -0.27752 | -0.14759 | -0.028337 | -0.062842 | 0.21467 | -0.015622 | -0.17267 | 122.9892 | 122.8662 | 122.9993 | 66.7754 | -123.1516 | 122.9084 | 123.0404 | 122.8834 | 66.7698 | -123.3335
542.7969 | 123.3124 | -66.7557 | 56.2592 | -0.010607 | -0.0052222 | 0.0015299 | 0.054791 | -0.0028866 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.060167 | 0.014703 | 0.060658 | -66.7747 | 0.028878 | -66.7368 | 56.2427 | 56.0968 | 56.2482 | -66.8467 | -66.7703 | 0.018674 | -66.8094 | 56.1528 | 56.2939 | 56.1231 | -67.0286 | -0.090996 | -0.016473 | -0.019063 | 0.018828 | 0.10982 | -0.16239 | -0.010994 | -0.27294 | -0.10639 | -0.014602 | -0.053686 | 0.21925 | 0.034734 | -0.13605 | 122.9984 | 122.8524 | 123.0038 | 66.7846 | -123.1058 | 122.9084 | 123.0496 | 122.8788 | 66.7743 | -123.2878
543.7969 | 123.2346 | -66.7694 | 56.3095 | -0.0029761 | -0.0056496 | 0.0013163 | 0.054577 | -0.0031002 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.014275 | 0.060658 | -66.7747 | 0.019721 | -66.746 | 56.2381 | 56.1151 | 56.2619 | -66.8467 | -66.7749 | 0.018674 | -66.8048 | 56.1573 | 56.2939 | 56.1368 | -67.0286 | -0.077263 | -0.071405 | -0.00533 | 0.023404 | 0.10067 | -0.19443 | -0.047612 | -0.25921 | -0.15217 | -0.005448 | -0.035374 | 0.22383 | -0.01562 | -0.17267 | 123.0075 | 122.8845 | 123.0313 | 66.7891 | -123.1562 | 122.9267 | 123.0633 | 122.9062 | 66.7881 | -123.3381
544.7969 | 123.2986 | -66.7557 | 56.2729 | -0.0029761 | -0.0054358 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.060167 | 0.014489 | 0.060231 | -66.7702 | 0.028878 | -66.746 | 56.2381 | 56.0968 | 56.2527 | -66.8421 | -66.7703 | 0.023253 | -66.8094 | 56.1482 | 56.2939 | 56.1368 | -67.0332 | -0.086417 | -0.034784 | -0.014485 | 0.009671 | 0.096088 | -0.17612 | -0.020148 | -0.27752 | -0.12471 | -0.014602 | -0.053686 | 0.22383 | 0.021001 | -0.13605 | 122.9938 | 122.8524 | 123.0084 | 66.7846 | -123.115 | 122.9039 | 123.0496 | 122.8925 | 66.7789 | -123.3061
545.7969 | 123.3124 | -66.7465 | 56.2637 | -0.010607 | -0.0050084 | 0.0011025 | 0.054363 | -0.0031002 | 0.063144 | 0.0077831 | -0.0013437 | -0.00098273 | 0.05974 | 0.014489 | 0.060445 | -66.7747 | 0.0243 | -66.7323 | 56.2381 | 56.1013 | 56.2482 | -66.8467 | -66.7703 | 0.014095 | -66.8048 | 56.1482 | 56.303 | 56.1277 | -67.0286 | -0.10015 | -0.025629 | -0.028218 | 0.014251 | 0.1144 | -0.16239 | -0.015572 | -0.28209 | -0.11555 | -0.023757 | -0.058262 | 0.22383 | 0.039313 | -0.13605 | 122.9846 | 122.8479 | 122.9947 | 66.7708 | -123.1104 | 122.8947 | 123.0496 | 122.8742 | 66.7606 | -123.2923
546.8594 | 123.1705 | -66.8152 | 56.2683 | -0.018238 | -0.0052222 | 0.0017435 | 0.054363 | -0.0031002 | 0.063144 | 0.015414 | -0.00091653 | -0.00098273 | 0.05974 | 0.014489 | 0.060658 | -66.7702 | 0.019721 | -66.7414 | 56.2335 | 56.0968 | 56.2527 | -66.8421 | -66.7703 | 0.018674 | -66.8048 | 56.1573 | 56.2939 | 56.1414 | -67.0286 | -0.026907 | -0.034786 | 0.045025 | 0.073759 | 0.10067 | -0.17155 | -0.015571 | -0.21343 | -0.11097 | 0.044908 | 0.010403 | 0.22383 | 0.025578 | -0.12689 | 123.0487 | 122.9119 | 123.0679 | 66.8349 | -123.1104 | 122.9725 | 123.1091 | 122.9566 | 66.8339 | -123.2969
547.7969 | 123.3261 | -66.7511 | 56.2637 | -0.010607 | -0.0054358 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | -0.0074779 | -0.00048933 | -0.00098273 | 0.060381 | 0.014703 | 0.060658 | -66.7747 | 0.015142 | -66.7368 | 56.2335 | 56.0968 | 56.2573 | -66.8421 | -66.7794 | 0.014095 | -66.8185 | 56.1482 | 56.2939 | 56.1414 | -67.0286 | -0.090994 | -0.030208 | -0.02364 | 0.014251 | 0.10525 | -0.16697 | -0.006415 | -0.27752 | -0.11555 | -0.028337 | -0.06742 | 0.2101 | 0.030156 | -0.12232 | 122.9846 | 122.8479 | 123.0084 | 66.7662 | -123.1058 | 122.8993 | 123.045 | 122.8925 | 66.7652 | -123.2923
548.7969 | 123.262 | -66.7374 | 56.3004 | -0.0029761 | -0.0054358 | 0.0017435 | 0.054363 | -0.003314 | 0.063358 | 0.0077831 | -0.00070293 | -0.0011965 | 0.060167 | 0.014703 | 0.060445 | -66.7747 | 0.019721 | -66.7414 | 56.2381 | 56.0876 | 56.2482 | -66.8467 | -66.7703 | 0.009516 | -66.8094 | 56.1573 | 56.2985 | 56.146 | -67.0286 | -0.10931 | -0.06225 | -0.037373 | -0.004061 | 0.10524 | -0.21275 | -0.052193 | -0.29125 | -0.14301 | -0.032912 | -0.071996 | 0.21925 | -0.001887 | -0.15436 | 122.9755 | 122.825 | 122.9855 | 66.7571 | -123.147 | 122.8947 | 123.0358 | 122.8834 | 66.7469 | -123.329
549.8594 | 123.1934 | -66.7648 | 56.3324 | 0.0046549 | -0.0056496 | 0.0011025 | 0.054791 | -0.003314 | 0.06293 | -0.0074779 | -0.0013437 | -0.00076913 | 0.05974 | 0.014489 | 0.060658 | -66.7702 | 0.0243 | -66.7368 | 56.2335 | 56.1105 | 56.2527 | -66.8513 | -66.7749 | 0.023253 | -66.8139 | 56.1573 | 56.2893 | 56.1414 | -67.024 | -0.086419 | -0.098872 | -0.005329 | 0.027984 | 0.1144 | -0.2219 | -0.079657 | -0.25921 | -0.17506 | -0.010025 | -0.049109 | 0.2101 | -0.043087 | -0.19098 | 122.9984 | 122.8753 | 123.0176 | 66.7891 | -123.1836 | 122.9222 | 123.0541 | 122.9062 | 66.7881 | -123.3564
550.7969 | 123.175 | -66.7603 | 56.337 | 0.0046549 | -0.0056496 | 0.0015299 | 0.054791 | -0.003314 | 0.063358 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060167 | 0.014916 | 0.060445 | -66.7702 | 0.015142 | -66.7277 | 56.2335 | 56.1013 | 56.2482 | -66.8467 | -66.7749 | 0.018674 | -66.8048 | 56.1482 | 56.2893 | 56.146 | -67.0195 | -0.086418 | -0.10345 | -0.009907 | 0.032562 | 0.11898 | -0.23563 | -0.088814 | -0.2592 | -0.18879 | -0.014603 | -0.044529 | 0.21468 | -0.047665 | -0.19098 | 122.9938 | 122.8616 | 123.0084 | 66.7754 | -123.1836 | 122.9084 | 123.0496 | 122.9062 | 66.7789 | -123.3564
551.7969 | 123.2712 | -66.7603 | 56.2683 | 0.0046549 | -0.0054358 | 0.0013163 | 0.054577 | -0.0028866 | 0.063144 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060167 | 0.014703 | 0.060445 | -66.7702 | 0.015142 | -66.7414 | 56.2381 | 56.1242 | 56.2527 | -66.8421 | -66.7749 | 0.018674 | -66.8094 | 56.1528 | 56.2939 | 56.1368 | -67.0286 | -0.081839 | -0.030207 | -0.009907 | 0.018827 | 0.10067 | -0.14407 | -0.015571 | -0.26836 | -0.11555 | -0.014603 | -0.049108 | 0.21925 | 0.025578 | -0.13147 | 122.9984 | 122.8845 | 123.013 | 66.7754 | -123.1104 | 122.913 | 123.0541 | 122.8971 | 66.7789 | -123.2969
552.7969 | 123.2529 | -66.7465 | 56.2866 | -0.010607 | -0.0056496 | 0.0015299 | 0.054363 | -0.003314 | 0.06293 | -0.0074779 | -0.0011301 | -0.00098273 | 0.060381 | 0.014489 | 0.060445 | -66.7839 | 0.028878 | -66.7323 | 56.2289 | 56.1105 | 56.2573 | -66.8329 | -66.7703 | 0.023253 | -66.8094 | 56.1436 | 56.2985 | 56.1414 | -67.0286 | -0.086414 | -0.057674 | -0.037375 | 0.014251 | 0.10067 | -0.17612 | -0.029303 | -0.28209 | -0.14302 | -0.023757 | -0.062841 | 0.21925 | 0.011846 | -0.1452 | 122.9755 | 122.857 | 123.0038 | 66.7754 | -123.1196 | 122.8901 | 123.045 | 122.8879 | 66.7698 | -123.3152
553.7969 | 123.2483 | -66.7374 | 56.2683 | -0.0029761 | -0.0052222 | 0.0017435 | 0.054577 | -0.0035276 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.014703 | 0.060658 | -66.7839 | 0.0243 | -66.7368 | 56.2381 | 56.1059 | 56.2573 | -66.8421 | -66.7703 | 0.009516 | -66.8094 | 56.1528 | 56.2985 | 56.146 | -67.0286 | -0.10473 | -0.030207 | -0.04653 | 0.000518 | 0.10525 | -0.16239 | -0.010993 | -0.29125 | -0.11555 | -0.032912 | -0.071996 | 0.21925 | 0.030156 | -0.12232 | 122.9755 | 122.8433 | 122.9947 | 66.7617 | -123.1104 | 122.8901 | 123.0358 | 122.8834 | 66.7469 | -123.2969
554.7969 | 123.3078 | -66.7282 | 56.2958 | -0.0029761 | -0.0050084 | 0.0015299 | 0.054577 | -0.003314 | 0.063358 | 0.00015261 | -0.0011301 | -0.00076913 | 0.060167 | 0.014489 | 0.060658 | -66.7702 | 0.019721 | -66.7368 | 56.2427 | 56.0968 | 56.2527 | -66.8329 | -66.7749 | 0.018674 | -66.8139 | 56.1573 | 56.2847 | 56.1368 | -67.024 | -0.10473 | -0.053094 | -0.041951 | -0.008638 | 0.096087 | -0.19901 | -0.043036 | -0.29583 | -0.13844 | -0.046647 | -0.085731 | 0.2101 | -0.011045 | -0.15894 | 122.9709 | 122.825 | 122.981 | 66.7479 | -123.1287 | 122.8855 | 123.0129 | 122.865 | 66.7469 | -123.3198
555.7969 | 123.2117 | -66.7282 | 56.337 | -0.010607 | -0.0054358 | 0.0015299 | 0.054577 | -0.0035276 | 0.063144 | 0.0077831 | -0.00091653 | -0.0016237 | 0.060381 | 0.014275 | 0.060231 | -66.7747 | 0.0243 | -66.7323 | 56.2427 | 56.1105 | 56.2573 | -66.8513 | -66.7749 | 0.014095 | -66.8094 | 56.1482 | 56.2939 | 56.1414 | -67.0195 | -0.12304 | -0.094293 | -0.046529 | -0.00406 | 0.11898 | -0.22648 | -0.079657 | -0.29125 | -0.18879 | -0.046647 | -0.081152 | 0.2101 | -0.043086 | -0.19556 | 122.9709 | 122.8387 | 122.9855 | 66.7525 | -123.1882 | 122.8764 | 123.0221 | 122.8696 | 66.7423 | -123.3564
556.7969 | 123.317 | -66.7282 | 56.3004 | 0.0046549 | -0.0056496 | 0.0013163 | 0.054791 | -0.0028866 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.059954 | 0.014275 | 0.060658 | -66.7702 | 0.0243 | -66.7368 | 56.2335 | 56.1059 | 56.2527 | -66.8421 | -66.7703 | 0.014095 | -66.8139 | 56.1482 | 56.2939 | 56.1414 | -67.0332 | -0.11388 | -0.066829 | -0.041951 | -0.008638 | 0.10525 | -0.19443 | -0.047614 | -0.30499 | -0.15217 | -0.042068 | -0.085731 | 0.21925 | -0.006465 | -0.15894 | 122.9617 | 122.8341 | 122.981 | 66.7525 | -123.1424 | 122.8764 | 123.0221 | 122.8696 | 66.7423 | -123.3335
557.8594 | 123.1796 | -66.7648 | 56.3507 | -0.0029761 | -0.0058632 | 0.0011025 | 0.054577 | -0.003314 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060167 | 0.014703 | 0.060231 | -66.7702 | 0.019721 | -66.7277 | 56.2381 | 56.1105 | 56.2527 | -66.8375 | -66.7703 | 0.014095 | -66.8048 | 56.1482 | 56.2939 | 56.1506 | -67.0286 | -0.072682 | -0.1126 | -0.005329 | 0.03714 | 0.10982 | -0.24021 | -0.097968 | -0.26378 | -0.20253 | -0.005446 | -0.039951 | 0.22383 | -0.056819 | -0.20013 | 123.0029 | 122.8753 | 123.0176 | 66.7846 | -123.1882 | 122.913 | 123.0587 | 122.9154 | 66.7789 | -123.3793
558.7969 | 123.2895 | -66.7099 | 56.2958 | 0.0046549 | -0.0054358 | 0.0015299 | 0.054577 | -0.003314 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.060595 | 0.014489 | 0.060445 | -66.7702 | 0.019721 | -66.7323 | 56.2335 | 56.1059 | 56.2482 | -66.8375 | -66.7703 | 0.014095 | -66.8139 | 56.1482 | 56.2939 | 56.146 | -67.0332 | -0.12761 | -0.062251 | -0.060261 | -0.02237 | 0.10524 | -0.18985 | -0.047615 | -0.3233 | -0.14759 | -0.060378 | -0.10404 | 0.21925 | -0.001887 | -0.14978 | 122.9434 | 122.8158 | 122.9581 | 66.7296 | -123.1333 | 122.8581 | 123.0038 | 122.8559 | 66.724 | -123.329
559.7969 | 123.3032 | -66.7099 | 56.2958 | 0.0046549 | -0.0056496 | 0.0013163 | 0.054791 | -0.003314 | 0.06293 | 0.0077831 | -0.0011301 | -0.00098273 | 0.060167 | 0.014916 | 0.060658 | -66.7702 | 0.019721 | -66.7323 | 56.2381 | 56.1151 | 56.2482 | -66.8513 | -66.7703 | 0.018674 | -66.8139 | 56.1436 | 56.2939 | 56.1323 | -67.0378 | -0.14135 | -0.057672 | -0.060261 | -0.02237 | 0.11898 | -0.1807 | -0.047615 | -0.32787 | -0.15217 | -0.060378 | -0.10404 | 0.22383 | -0.001887 | -0.16352 | 122.948 | 122.825 | 122.9581 | 66.7296 | -123.147 | 122.8535 | 123.0038 | 122.8422 | 66.7286 | -123.3336
560.7969 | 123.2117 | -66.7465 | 56.3187 | 0.0046549 | -0.0054358 | 0.0011025 | 0.054149 | -0.0028866 | 0.06293 | 0.0077831 | -0.0011301 | -0.0014101 | 0.060167 | 0.014703 | 0.060658 | -66.7702 | 0.019721 | -66.7368 | 56.2335 | 56.1105 | 56.2527 | -66.8421 | -66.7749 | 0.018674 | -66.8094 | 56.1482 | 56.2939 | 56.1368 | -67.0332 | -0.095572 | -0.08514 | -0.02364 | 0.009673 | 0.10525 | -0.20817 | -0.065925 | -0.28667 | -0.17048 | -0.028336 | -0.062841 | 0.22383 | -0.024776 | -0.18183 | 122.98 | 122.857 | 122.9993 | 66.7662 | -123.1608 | 122.8947 | 123.0404 | 122.8834 | 66.7652 | -123.3519
561.7969 | 123.3353 | -66.7328 | 56.2729 | -0.0029761 | -0.0058632 | 0.0015299 | 0.054577 | -0.0031002 | 0.06293 | -0.0074779 | -0.00091653 | -0.0011965 | 0.060167 | 0.014703 | 0.060872 | -66.7747 | 0.019721 | -66.7368 | 56.2381 | 56.1059 | 56.2527 | -66.8284 | -66.7703 | 0.014095 | -66.8048 | 56.1528 | 56.2939 | 56.146 | -67.024 | -0.095568 | -0.034784 | -0.041951 | -0.00406 | 0.091508 | -0.16697 | -0.020148 | -0.29125 | -0.12013 | -0.03749 | -0.071995 | 0.21925 | 0.021001 | -0.12689 | 122.9709 | 122.8387 | 122.9855 | 66.7525 | -123.1012 | 122.8855 | 123.0267 | 122.8788 | 66.7469 | -123.2969
562.7969 | 123.262 | -66.7923 | 56.2958 | -0.0029761 | -0.0060768 | 0.0013163 | 0.054149 | -0.003314 | 0.062717 | 0.0077831 | -0.0013437 | -0.00076913 | 0.060167 | 0.014275 | 0.060231 | -66.7656 | 0.0243 | -66.7368 | 56.2427 | 56.1013 | 56.2573 | -66.8467 | -66.7703 | 0.018674 | -66.8048 | 56.1573 | 56.2985 | 56.146 | -67.0286 | -0.054375 | -0.053094 | 0.026714 | 0.055449 | 0.10982 | -0.19443 | -0.038458 | -0.23632 | -0.13844 | 0.022019 | -0.012486 | 0.22383 | 0.002691 | -0.14978 | 123.035 | 122.8936 | 123.0496 | 66.8166 | -123.1424 | 122.9496 | 123.0908 | 122.9383 | 66.811 | -123.3244
563.7969 | 123.2986 | -66.7328 | 56.3141 | 0.012286 | -0.0056496 | 0.0017435 | 0.053936 | -0.003314 | 0.063144 | -0.0074779 | -0.00091653 | -0.00098273 | 0.060167 | 0.014916 | 0.060872 | -66.7656 | 0.0243 | -66.7368 | 56.2427 | 56.1013 | 56.2527 | -66.8421 | -66.7749 | 0.014095 | -66.8139 | 56.1482 | 56.2985 | 56.1323 | -67.0286 | -0.10931 | -0.071405 | -0.032795 | -0.00406 | 0.10525 | -0.21274 | -0.061347 | -0.29583 | -0.16591 | -0.042069 | -0.081153 | 0.21467 | -0.01562 | -0.18183 | 122.9755 | 122.8341 | 122.9855 | 66.7571 | -123.1562 | 122.881 | 123.0313 | 122.865 | 66.7469 | -123.3427
564.7969 | 123.2071 | -66.7511 | 56.3095 | -0.0029761 | -0.0056496 | 0.0013163 | 0.054577 | -0.003314 | 0.06293 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059954 | 0.015344 | 0.060872 | -66.7656 | 0.010564 | -66.7323 | 56.2427 | 56.1013 | 56.2482 | -66.8513 | -66.7657 | 0.018674 | -66.8094 | 56.1528 | 56.2939 | 56.1368 | -67.0286 | -0.10015 | -0.066827 | -0.014484 | 0.018829 | 0.11898 | -0.20817 | -0.061348 | -0.27752 | -0.15675 | -0.0146 | -0.058263 | 0.21925 | -0.01562 | -0.17267 | 122.9938 | 122.8524 | 122.9993 | 66.7617 | -123.1608 | 122.9039 | 123.045 | 122.8879 | 66.7698 | -123.3381
565.7969 | 123.2071 | -66.7877 | 56.2866 | -0.0029761 | -0.0054358 | 0.0015299 | 0.054149 | -0.0028866 | 0.063144 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059954 | 0.014489 | 0.060658 | -66.7793 | 0.015142 | -66.7323 | 56.2427 | 56.1013 | 56.2527 | -66.8467 | -66.7703 | 0.023253 | -66.8094 | 56.1482 | 56.2939 | 56.1368 | -67.0195 | -0.058952 | -0.043939 | 0.008402 | 0.05545 | 0.1144 | -0.18528 | -0.033881 | -0.23174 | -0.13844 | 0.017442 | -0.021642 | 0.2101 | 0.007268 | -0.14978 | 123.0304 | 122.8891 | 123.0405 | 66.8029 | -123.1333 | 122.9359 | 123.0816 | 122.9246 | 66.811 | -123.3061
566.8594 | 123.3215 | -66.7465 | 56.2775 | 0.012286 | -0.0056496 | 0.0011025 | 0.054363 | -0.003314 | 0.063144 | 0.00015261 | -0.0013437 | -0.00098273 | 0.060167 | 0.014703 | 0.060445 | -66.7747 | 0.019721 | -66.7277 | 56.2335 | 56.1151 | 56.2527 | -66.8421 | -66.7749 | 0.009516 | -66.8048 | 56.1482 | 56.2985 | 56.1368 | -67.0286 | -0.095572 | -0.043941 | -0.028218 | 0.018829 | 0.1144 | -0.16239 | -0.024726 | -0.28209 | -0.12928 | -0.028336 | -0.058262 | 0.22383 | 0.021001 | -0.14063 | 122.98 | 122.8616 | 122.9993 | 66.7662 | -123.1196 | 122.8947 | 123.045 | 122.8834 | 66.756 | -123.3061
567.7969 | 123.2437 | -66.774 | 56.2866 | -0.0029761 | -0.0056496 | 0.0013163 | 0.054149 | -0.003314 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.059954 | 0.014916 | 0.060658 | -66.7793 | 0.0243 | -66.7414 | 56.2427 | 56.1151 | 56.2527 | -66.8467 | -66.7657 | 0.018674 | -66.8139 | 56.1482 | 56.2985 | 56.1368 | -67.0332 | -0.072685 | -0.043939 | -0.005331 | 0.03256 | 0.10524 | -0.17154 | -0.033881 | -0.25921 | -0.13844 | 0.008288 | -0.039954 | 0.21925 | 0.011846 | -0.14978 | 123.0167 | 122.8891 | 123.0267 | 66.7983 | -123.1333 | 122.9222 | 123.0725 | 122.9108 | 66.7927 | -123.3198
568.7969 | 123.262 | -66.7648 | 56.3049 | 0.012286 | -0.0056496 | 0.0017435 | 0.054363 | -0.0035276 | 0.062717 | 0.015414 | -0.00091653 | -0.00098273 | 0.060381 | 0.014916 | 0.060872 | -66.7747 | 0.019721 | -66.7414 | 56.2473 | 56.1197 | 56.2619 | -66.8329 | -66.7703 | 0.018674 | -66.8048 | 56.1482 | 56.2985 | 56.1368 | -67.0332 | -0.068103 | -0.057672 | -0.009907 | 0.023405 | 0.091508 | -0.18527 | -0.043035 | -0.26836 | -0.15675 | -0.005446 | -0.039951 | 0.22841 | -0.006465 | -0.16809 | 123.0121 | 122.8845 | 123.0267 | 66.7846 | -123.1379 | 122.913 | 123.0633 | 122.9017 | 66.7835 | -123.3381
569.8594 | 123.2712 | -66.7603 | 56.2775 | 0.012286 | -0.0056496 | 0.0015299 | 0.054577 | -0.003314 | 0.06293 | 0.00015261 | -0.00091653 | -0.0014101 | 0.059954 | 0.014916 | 0.060445 | -66.761 | 0.0243 | -66.7323 | 56.2381 | 56.1013 | 56.2527 | -66.8421 | -66.7749 | 0.014095 | -66.8139 | 56.1573 | 56.2985 | 56.1368 | -67.0286 | -0.081839 | -0.039362 | -0.00075 | 0.027984 | 0.10982 | -0.17612 | -0.024726 | -0.26836 | -0.12013 | -0.014603 | -0.053687 | 0.21467 | 0.021001 | -0.14063 | 122.9984 | 122.8616 | 123.013 | 66.7846 | -123.1196 | 122.9176 | 123.0587 | 122.8971 | 66.7743 | -123.3061
570.7969 | 123.2208 | -66.7877 | 56.3095 | 0.0046549 | -0.0058632 | 0.0011025 | 0.054363 | -0.0031002 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.060167 | 0.014703 | 0.059804 | -66.7702 | 0.028878 | -66.7323 | 56.2381 | 56.1105 | 56.2527 | -66.8467 | -66.7703 | 0.014095 | -66.8094 | 56.1482 | 56.2985 | 56.1414 | -67.024 | -0.058952 | -0.071405 | 0.017559 | 0.05545 | 0.1144 | -0.19901 | -0.056769 | -0.23632 | -0.16133 | 0.017442 | -0.021642 | 0.21468 | -0.011042 | -0.16809 | 123.0258 | 122.8982 | 123.0405 | 66.8166 | -123.1562 | 122.9359 | 123.0862 | 122.9291 | 66.8018 | -123.3335
571.8594 | 123.2895 | -66.7282 | 56.2775 | -0.010607 | -0.0054358 | 0.0015299 | 0.054791 | -0.003314 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059954 | 0.014703 | 0.060017 | -66.7702 | 0.0243 | -66.7368 | 56.2335 | 56.1059 | 56.2436 | -66.8375 | -66.7749 | 0.018674 | -66.8094 | 56.1528 | 56.303 | 56.1368 | -67.0286 | -0.1093 | -0.043941 | -0.041951 | -0.008638 | 0.10067 | -0.17154 | -0.033883 | -0.30041 | -0.12471 | -0.046647 | -0.081152 | 0.21925 | 0.02558 | -0.14063 | 122.9617 | 122.8341 | 122.9718 | 66.7525 | -123.115 | 122.881 | 123.0313 | 122.865 | 66.7469 | -123.3061
572.7969 | 123.3215 | -66.7465 | 56.2775 | -0.0029761 | -0.0054358 | 0.0011025 | 0.054363 | -0.003314 | 0.062503 | -0.015108 | -0.0011301 | -0.00098273 | 0.060167 | 0.014703 | 0.060658 | -66.7656 | 0.019721 | -66.7368 | 56.2381 | 56.1105 | 56.2573 | -66.8375 | -66.7749 | 0.009516 | -66.8094 | 56.1528 | 56.303 | 56.1323 | -67.0332 | -0.090993 | -0.039362 | -0.019062 | 0.009673 | 0.10067 | -0.16697 | -0.020148 | -0.28667 | -0.12471 | -0.028336 | -0.062841 | 0.22383 | 0.02558 | -0.14521 | 122.9846 | 122.857 | 123.0038 | 66.7662 | -123.115 | 122.8993 | 123.0496 | 122.8788 | 66.756 | -123.3107
573.7969 | 123.2117 | -66.774 | 56.3141 | 0.012286 | -0.0054358 | 0.0013163 | 0.054577 | -0.0028866 | 0.06293 | 0.00015261 | -0.0011301 | -0.00076913 | 0.059954 | 0.01513 | 0.060658 | -66.7702 | 0.0243 | -66.7231 | 56.2473 | 56.1013 | 56.2573 | -66.8467 | -66.7657 | 0.018674 | -66.8139 | 56.1528 | 56.303 | 56.1368 | -67.0286 | -0.072685 | -0.066827 | 0.003826 | 0.050874 | 0.12356 | -0.21274 | -0.056769 | -0.25463 | -0.16133 | 0.008288 | -0.039954 | 0.21467 | -0.011041 | -0.17725 | 123.0212 | 122.8753 | 123.0313 | 66.7983 | -123.1608 | 122.9267 | 123.077 | 122.9108 | 66.7927 | -123.3427
574.7969 | 123.1659 | -66.7648 | 56.3187 | -0.010607 | -0.0058632 | 0.0011025 | 0.054149 | -0.003314 | 0.06293 | -0.0074779 | -0.00091653 | -0.00076913 | 0.060167 | 0.014703 | 0.060231 | -66.761 | 0.0243 | -66.7323 | 56.2473 | 56.1105 | 56.2619 | -66.8467 | -66.7703 | 0.014095 | -66.8139 | 56.1482 | 56.303 | 56.1414 | -67.0286 | -0.08184 | -0.071405 | 0.003828 | 0.032562 | 0.1144 | -0.20817 | -0.056768 | -0.26378 | -0.17048 | -0.005446 | -0.049109 | 0.21467 | -0.015619 | -0.17725 | 123.0121 | 122.8753 | 123.0267 | 66.7891 | -123.1653 | 122.913 | 123.0679 | 122.9062 | 66.7789 | -123.3473
575.7969 | 123.2483 | -66.7557 | 56.3095 | -0.0029761 | -0.0058632 | 0.0013163 | 0.054363 | -0.003314 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.014489 | 0.060445 | -66.7702 | 0.0243 | -66.7414 | 56.2381 | 56.1105 | 56.2619 | -66.8513 | -66.7749 | 0.018674 | -66.8094 | 56.1482 | 56.303 | 56.1323 | -67.0332 | -0.095575 | -0.071405 | -0.014485 | 0.014249 | 0.10982 | -0.19901 | -0.047612 | -0.27752 | -0.16133 | -0.019181 | -0.053686 | 0.22383 | -0.006463 | -0.17725 | 122.9938 | 122.8662 | 123.0176 | 66.78 | -123.1608 | 122.9039 | 123.0587 | 122.8879 | 66.7743 | -123.3427
576.8594 | 123.3078 | -66.7282 | 56.2912 | -0.0029761 | -0.0056496 | 0.0013163 | 0.054577 | -0.003314 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060595 | 0.014916 | 0.060231 | -66.7656 | 0.015142 | -66.7414 | 56.2381 | 56.1242 | 56.2573 | -66.8513 | -66.7749 | 0.014095 | -66.8048 | 56.1436 | 56.3076 | 56.1552 | -67.0286 | -0.12304 | -0.053095 | -0.037373 | -0.013217 | 0.10982 | -0.16696 | -0.033881 | -0.30041 | -0.1476 | -0.046647 | -0.076573 | 0.22383 | 0.016425 | -0.13605 | 122.9663 | 122.8524 | 122.9855 | 66.7434 | -123.1424 | 122.8718 | 123.0358 | 122.8834 | 66.7423 | -123.3198
577.7969 | 123.2254 | -66.7328 | 56.282 | -0.0029761 | -0.0058632 | 0.0013163 | 0.054149 | -0.0031002 | 0.063144 | -0.0074779 | -0.0013437 | -0.0011965 | 0.059954 | 0.014916 | 0.060231 | -66.7702 | 0.015142 | -66.7323 | 56.2427 | 56.1151 | 56.2573 | -66.8513 | -66.7749 | 0.014095 | -66.8048 | 56.1482 | 56.303 | 56.1414 | -67.0286 | -0.11846 | -0.039361 | -0.037373 | 0.000518 | 0.11898 | -0.16696 | -0.024725 | -0.29583 | -0.13386 | -0.042069 | -0.071995 | 0.22383 | 0.021003 | -0.14062 | 122.9755 | 122.8479 | 122.9901 | 66.7479 | -123.1333 | 122.881 | 123.0358 | 122.8742 | 66.7469 | -123.3107
578.7969 | 123.2895 | -66.7969 | 56.3095 | 0.0046549 | -0.0060768 | 0.0015299 | 0.054149 | -0.003314 | 0.062717 | -0.0074779 | -0.0011301 | -0.0011965 | 0.059954 | 0.014703 | 0.060658 | -66.7702 | 0.0243 | -66.7414 | 56.2427 | 56.1151 | 56.2527 | -66.8467 | -66.7703 | 0.018674 | -66.8094 | 56.1528 | 56.303 | 56.1368 | -67.0286 | -0.049797 | -0.066827 | 0.026714 | 0.055448 | 0.10524 | -0.19443 | -0.056769 | -0.23174 | -0.15675 | 0.026597 | -0.012487 | 0.21925 | -0.006463 | -0.17267 | 123.0396 | 122.912 | 123.0496 | 66.8212 | -123.1562 | 122.9496 | 123.0999 | 122.9337 | 66.8155 | -123.3381
579.7969 | 123.2162 | -66.7694 | 56.2912 | 0.0046549 | -0.0058632 | 0.0015299 | 0.053936 | -0.0035276 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060381 | 0.015344 | 0.060445 | -66.7656 | 0.019721 | -66.7323 | 56.2381 | 56.1059 | 56.2619 | -66.8421 | -66.784 | 0.018674 | -66.8048 | 56.1482 | 56.2939 | 56.1552 | -67.0286 | -0.072684 | -0.053095 | 0.003826 | 0.037139 | 0.10982 | -0.18528 | -0.029302 | -0.25921 | -0.14302 | -0.014605 | -0.035374 | 0.22383 | 0.00269 | -0.13605 | 123.0075 | 122.8753 | 123.0313 | 66.7891 | -123.1333 | 122.9176 | 123.0633 | 122.9246 | 66.7881 | -123.3198
580.7969 | 123.2666 | -66.7603 | 56.2775 | 0.012286 | -0.0062906 | 0.0013163 | 0.054363 | -0.003314 | 0.063144 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060381 | 0.01513 | 0.060872 | -66.7656 | 0.019721 | -66.7368 | 56.2427 | 56.1013 | 56.2573 | -66.8421 | -66.7703 | 0.009516 | -66.8094 | 56.1573 | 56.2985 | 56.1368 | -67.0286 | -0.081839 | -0.034784 | -0.005329 | 0.023406 | 0.10525 | -0.17612 | -0.020148 | -0.26836 | -0.12013 | -0.010024 | -0.049108 | 0.21925 | 0.021001 | -0.14063 | 123.0029 | 122.8616 | 123.0176 | 66.78 | -123.1196 | 122.9176 | 123.0587 | 122.8971 | 66.7698 | -123.3061
581.7969 | 123.2117 | -66.7786 | 56.3232 | 0.012286 | -0.0058632 | 0.0013163 | 0.054577 | -0.0031002 | 0.063144 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059954 | 0.014916 | 0.060658 | -66.7656 | 0.015142 | -66.7414 | 56.2427 | 56.1151 | 56.2573 | -66.8513 | -66.7749 | 0.014095 | -66.8185 | 56.1436 | 56.2985 | 56.1277 | -67.0286 | -0.072687 | -0.08056 | 0.012981 | 0.037137 | 0.10982 | -0.20816 | -0.065924 | -0.25005 | -0.17964 | 0.003707 | -0.039955 | 0.2101 | -0.024775 | -0.19556 | 123.0212 | 122.8936 | 123.0359 | 66.7937 | -123.1745 | 122.9222 | 123.077 | 122.9062 | 66.7927 | -123.3519
582.7969 | 123.1796 | -66.7694 | 56.3187 | 0.0046549 | -0.0060768 | 0.0011025 | 0.054363 | -0.003314 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.05974 | 0.014916 | 0.060445 | -66.7747 | 0.019721 | -66.7368 | 56.2427 | 56.1013 | 56.2619 | -66.8467 | -66.7703 | 0.014095 | -66.8094 | 56.1482 | 56.303 | 56.1414 | -67.0286 | -0.077263 | -0.075983 | -0.00533 | 0.032561 | 0.10982 | -0.21732 | -0.056768 | -0.25921 | -0.17048 | -0.000869 | -0.039953 | 0.21925 | -0.015619 | -0.17725 | 123.0121 | 122.8708 | 123.0313 | 66.7891 | -123.1653 | 122.9176 | 123.0725 | 122.9108 | 66.7835 | -123.3473
583.7969 | 123.1934 | -66.7603 | 56.3141 | 0.0046549 | -0.0062906 | 0.00088894 | 0.054577 | -0.0035276 | 0.063358 | 0.015414 | -0.00070293 | -0.0014101 | 0.060167 | 0.01513 | 0.060445 | -66.7747 | 0.0243 | -66.7414 | 56.2381 | 56.1151 | 56.2573 | -66.8467 | -66.7749 | 0.018674 | -66.8094 | 56.1528 | 56.2939 | 56.1368 | -67.0286 | -0.086418 | -0.075983 | -0.014485 | 0.018827 | 0.10524 | -0.19901 | -0.056769 | -0.26836 | -0.16133 | -0.014603 | -0.049108 | 0.21925 | -0.020198 | -0.17725 | 122.9984 | 122.8753 | 123.0176 | 66.7846 | -123.1608 | 122.913 | 123.0541 | 122.8971 | 66.7789 | -123.3427
584.7969 | 123.1979 | -66.7694 | 56.3049 | 0.0046549 | -0.0062906 | 0.0011025 | 0.054363 | -0.003314 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059954 | 0.015344 | 0.060445 | -66.7702 | 0.015142 | -66.7506 | 56.2381 | 56.1059 | 56.2573 | -66.8421 | -66.7657 | 0.023253 | -66.8094 | 56.1482 | 56.2939 | 56.146 | -67.0332 | -0.072684 | -0.066828 | -0.000752 | 0.018826 | 0.09151 | -0.19901 | -0.047614 | -0.26379 | -0.15675 | 0.00371 | -0.039953 | 0.22383 | -0.011043 | -0.15894 | 123.0075 | 122.8753 | 123.0267 | 66.7846 | -123.147 | 122.9176 | 123.0633 | 122.9154 | 66.7927 | -123.3381
585.875 | 123.2574 | -66.7603 | 56.282 | -0.0029761 | -0.0062906 | 0.0011025 | 0.054363 | -0.0035276 | 0.063144 | -0.0074779 | -0.0011301 | -0.0011965 | 0.060167 | 0.015344 | 0.060658 | -66.7747 | 0.0243 | -66.7506 | 56.2427 | 56.1197 | 56.2482 | -66.8421 | -66.7794 | 0.009516 | -66.8048 | 56.1528 | 56.2939 | 56.1368 | -67.024 | -0.081839 | -0.039361 | -0.014485 | 0.009671 | 0.09151 | -0.16239 | -0.033882 | -0.26378 | -0.12928 | -0.019182 | -0.044529 | 0.21925 | 0.011846 | -0.1452 | 123.0029 | 122.8799 | 123.0084 | 66.7846 | -123.1241 | 122.913 | 123.0541 | 122.8971 | 66.7698 | -123.3061
586.7969 | 123.2208 | -66.7969 | 56.2866 | -0.0029761 | -0.0062906 | 0.0011025 | 0.054577 | -0.003314 | 0.063144 | 0.00015261 | -0.00091653 | -0.0011965 | 0.059954 | 0.01513 | 0.060872 | -66.7702 | 0.0243 | -66.746 | 56.2335 | 56.1151 | 56.2573 | -66.8421 | -66.7749 | 0.023253 | -66.8139 | 56.1528 | 56.2985 | 56.1414 | -67.0332 | -0.045218 | -0.053096 | 0.026714 | 0.05087 | 0.096088 | -0.17154 | -0.029303 | -0.23632 | -0.13386 | 0.022018 | -0.017066 | 0.21925 | 0.011846 | -0.1452 | 123.0304 | 122.912 | 123.0542 | 66.8212 | -123.1287 | 122.9496 | 123.0953 | 122.9383 | 66.8201 | -123.3198
587.7969 | 123.1659 | -66.7831 | 56.2958 | -0.0029761 | -0.0060768 | 0.0013163 | 0.054577 | -0.003314 | 0.063144 | 0.0077831 | -0.0013437 | -0.0014101 | 0.05974 | 0.01513 | 0.060658 | -66.7656 | 0.015142 | -66.7414 | 56.2335 | 56.1151 | 56.2619 | -66.8513 | -66.7703 | 0.018674 | -66.8094 | 56.1573 | 56.303 | 56.1368 | -67.0332 | -0.068109 | -0.062251 | 0.017559 | 0.041715 | 0.10982 | -0.1807 | -0.033879 | -0.25005 | -0.13844 | 0.012864 | -0.02622 | 0.22383 | 0.00727 | -0.15894 | 123.0167 | 122.8982 | 123.045 | 66.7983 | -123.147 | 122.9405 | 123.0862 | 122.92 | 66.8018 | -123.329
588.8594 | 123.2254 | -66.7694 | 56.3095 | 0.0046549 | -0.0060768 | 0.0015299 | 0.054149 | -0.003314 | 0.063144 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.014916 | 0.060658 | -66.7656 | 0.015142 | -66.746 | 56.2381 | 56.1151 | 56.2665 | -66.8467 | -66.7749 | 0.018674 | -66.8002 | 56.1482 | 56.2985 | 56.1552 | -67.0286 | -0.077263 | -0.071405 | 0.003826 | 0.023404 | 0.10067 | -0.19443 | -0.043033 | -0.25921 | -0.16133 | -0.005448 | -0.030796 | 0.22841 | -0.011042 | -0.15436 | 123.0075 | 122.8845 | 123.0359 | 66.7846 | -123.1562 | 122.9176 | 123.0679 | 122.9246 | 66.7881 | -123.3381
589.7969 | 123.2208 | -66.7877 | 56.2912 | 0.0046549 | -0.0065042 | 0.0013163 | 0.054577 | -0.003314 | 0.063144 | -0.0074779 | -0.0011301 | -0.0014101 | 0.060167 | 0.015344 | 0.060445 | -66.7564 | 0.0243 | -66.7414 | 56.2427 | 56.1151 | 56.2573 | -66.8375 | -66.7749 | 0.018674 | -66.8139 | 56.1436 | 56.3076 | 56.1414 | -67.0286 | -0.049794 | -0.048517 | 0.031294 | 0.046293 | 0.096087 | -0.17612 | -0.033881 | -0.2409 | -0.1476 | 0.012863 | -0.026221 | 0.21467 | 0.016425 | -0.14978 | 123.0304 | 122.9028 | 123.045 | 66.812 | -123.1287 | 122.9313 | 123.0953 | 122.9291 | 66.8064 | -123.3198
590.7969 | 123.3444 | -66.7191 | 56.3049 | 0.012286 | -0.0062906 | 0.0015299 | 0.054791 | -0.0028866 | 0.063144 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.01513 | 0.060445 | -66.7747 | 0.010564 | -66.746 | 56.2381 | 56.1197 | 56.2527 | -66.8421 | -66.7703 | 0.014095 | -66.8094 | 56.1482 | 56.303 | 56.1414 | -67.0286 | -0.12304 | -0.066828 | -0.055684 | -0.02695 | 0.096088 | -0.18527 | -0.052192 | -0.30956 | -0.15675 | -0.051223 | -0.090307 | 0.21925 | -0.001886 | -0.16351 | 122.9572 | 122.8387 | 122.9718 | 66.7296 | -123.147 | 122.8672 | 123.0221 | 122.8605 | 66.7331 | -123.3335
591.8594 | 123.2117 | -66.7694 | 56.337 | 0.0046549 | -0.0060768 | 0.0013163 | 0.054149 | -0.003314 | 0.063358 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060167 | 0.015344 | 0.060445 | -66.7656 | 0.019721 | -66.746 | 56.2427 | 56.1197 | 56.2665 | -66.8375 | -66.7749 | 0.018674 | -66.8002 | 56.1528 | 56.2939 | 56.1552 | -67.0332 | -0.068105 | -0.094293 | 0.003826 | 0.023404 | 0.091509 | -0.21732 | -0.070499 | -0.26379 | -0.18422 | -0.005448 | -0.030796 | 0.23299 | -0.043086 | -0.18182 | 123.0121 | 122.8891 | 123.0359 | 66.7891 | -123.1745 | 122.9222 | 123.0633 | 122.9246 | 66.7881 | -123.3702
592.7969 | 123.2529 | -66.7282 | 56.2912 | 0.012286 | -0.0058632 | 0.0011025 | 0.054577 | -0.0035276 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059954 | 0.015344 | 0.060872 | -66.7702 | 0.019721 | -66.746 | 56.2381 | 56.1105 | 56.2573 | -66.8329 | -66.7703 | 0.009516 | -66.8094 | 56.1619 | 56.2939 | 56.1323 | -67.0332 | -0.10473 | -0.053095 | -0.041951 | -0.017795 | 0.08693 | -0.1807 | -0.033881 | -0.30499 | -0.12928 | -0.042068 | -0.081152 | 0.22383 | 0.00269 | -0.15894 | 122.9663 | 122.8387 | 122.9855 | 66.7479 | -123.1241 | 122.8901 | 123.0221 | 122.8605 | 66.7377 | -123.3244
593.7969 | 123.3032 | -66.7557 | 56.2683 | -0.0029761 | -0.0065042 | 0.0015299 | 0.054149 | -0.003314 | 0.063144 | 0.0077831 | -0.00070293 | -0.0014101 | 0.059954 | 0.015344 | 0.060445 | -66.7702 | 0.015142 | -66.7368 | 56.2427 | 56.1105 | 56.2619 | -66.8421 | -66.7749 | 0.014095 | -66.8002 | 56.1573 | 56.2985 | 56.1323 | -67.0332 | -0.086417 | -0.025629 | -0.014485 | 0.018828 | 0.10525 | -0.15781 | -0.006414 | -0.27752 | -0.11097 | -0.019181 | -0.044529 | 0.23299 | 0.030156 | -0.13605 | 122.9984 | 122.8662 | 123.0176 | 66.7708 | -123.1104 | 122.913 | 123.0541 | 122.8879 | 66.7698 | -123.3015
594.7969 | 123.2758 | -66.7465 | 56.2866 | -0.0029761 | -0.0062906 | 0.00088894 | 0.054791 | -0.003314 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.060167 | 0.01513 | 0.060445 | -66.7702 | 0.015142 | -66.7414 | 56.2427 | 56.1013 | 56.2573 | -66.8513 | -66.7794 | 0.018674 | -66.8094 | 56.1482 | 56.2939 | 56.1368 | -67.0286 | -0.10473 | -0.043939 | -0.02364 | 0.005094 | 0.10982 | -0.18528 | -0.029303 | -0.28209 | -0.13844 | -0.032915 | -0.062841 | 0.21925 | 0.007268 | -0.14978 | 122.9892 | 122.8479 | 123.0038 | 66.7617 | -123.1379 | 122.8947 | 123.0404 | 122.8834 | 66.7652 | -123.3152
595.7969 | 123.2986 | -66.7328 | 56.3324 | 0.0046549 | -0.0060768 | 0.0011025 | 0.054577 | -0.003314 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.060167 | 0.015771 | 0.060445 | -66.7656 | 0.019721 | -66.746 | 56.2335 | 56.1105 | 56.2573 | -66.8421 | -66.7703 | 0.014095 | -66.8094 | 56.1482 | 56.2985 | 56.1368 | -67.0286 | -0.10931 | -0.098872 | -0.032795 | -0.013217 | 0.096088 | -0.2219 | -0.075079 | -0.29583 | -0.18422 | -0.03749 | -0.076574 | 0.21925 | -0.03393 | -0.19556 | 122.9663 | 122.8433 | 122.9901 | 66.7525 | -123.1745 | 122.881 | 123.0313 | 122.8696 | 66.7469 | -123.361
596.7969 | 123.3032 | -66.7191 | 56.3187 | -0.0029761 | -0.0062906 | 0.0011025 | 0.055004 | -0.003314 | 0.063144 | 0.00015261 | -0.0015573 | -0.00098273 | 0.05974 | 0.015344 | 0.060445 | -66.7702 | 0.010564 | -66.7414 | 56.2289 | 56.1197 | 56.2573 | -66.8513 | -66.7749 | 0.009516 | -66.8139 | 56.1436 | 56.2939 | 56.1506 | -67.0286 | -0.1322 | -0.089718 | -0.051106 | -0.022372 | 0.10982 | -0.19901 | -0.061347 | -0.30956 | -0.17506 | -0.055802 | -0.094886 | 0.21467 | -0.024776 | -0.16809 | 122.948 | 122.8387 | 122.9764 | 66.7296 | -123.1699 | 122.8627 | 123.0129 | 122.8696 | 66.7286 | -123.3473
597.8594 | 123.2071 | -66.7694 | 56.3095 | -0.0029761 | -0.0065042 | 0.0011025 | 0.054149 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.059954 | 0.015344 | 0.060445 | -66.7656 | 0.019721 | -66.7368 | 56.2335 | 56.1105 | 56.2573 | -66.8375 | -66.7703 | 0.018674 | -66.8139 | 56.1482 | 56.303 | 56.1323 | -67.0286 | -0.068105 | -0.075984 | 0.003826 | 0.032561 | 0.10067 | -0.19901 | -0.052191 | -0.25921 | -0.16133 | -0.000869 | -0.044532 | 0.21467 | -0.006463 | -0.17725 | 123.0029 | 122.8799 | 123.0267 | 66.7891 | -123.147 | 122.9176 | 123.0725 | 122.9017 | 66.7881 | -123.3381
598.7969 | 123.3353 | -66.7099 | 56.282 | -0.010607 | -0.0065042 | 0.0011025 | 0.054577 | -0.0035276 | 0.06293 | 0.0077831 | -0.00091653 | -0.00098273 | 0.059527 | 0.015344 | 0.060231 | -66.7747 | 0.015142 | -66.7414 | 56.2335 | 56.1105 | 56.2619 | -66.8467 | -66.7794 | 0.014095 | -66.8048 | 56.1573 | 56.2985 | 56.1277 | -67.0332 | -0.13677 | -0.048518 | -0.064839 | -0.031527 | 0.10524 | -0.17154 | -0.020146 | -0.3233 | -0.1247 | -0.069536 | -0.094883 | 0.22841 | 0.016424 | -0.15436 | 122.9434 | 122.8204 | 122.9718 | 66.725 | -123.1287 | 122.8672 | 123.0084 | 122.8376 | 66.724 | -123.3152
599.8594 | 123.1201 | -66.7831 | 56.3187 | -0.0029761 | -0.0060768 | 0.0011025 | 0.054577 | -0.003314 | 0.06293 | 0.0077831 | -0.00091653 | -0.0011965 | 0.060167 | 0.015558 | 0.060658 | -66.7747 | 0.019721 | -66.7414 | 56.2381 | 56.1242 | 56.2619 | -66.8467 | -66.7703 | 0.009516 | -66.8094 | 56.1528 | 56.2939 | 56.1414 | -67.0332 | -0.06353 | -0.080561 | 0.008403 | 0.041715 | 0.10524 | -0.19443 | -0.056768 | -0.25005 | -0.16591 | 0.012864 | -0.02622 | 0.22383 | -0.024776 | -0.17725 | 123.0212 | 122.9074 | 123.045 | 66.8029 | -123.1653 | 122.9359 | 123.077 | 122.9246 | 66.7927 | -123.3519
600.7969 | 123.2483 | -66.7511 | 56.3278 | -0.010607 | -0.0065042 | 0.0015299 | 0.054149 | -0.003314 | 0.063144 | -0.0074779 | -0.0011301 | -0.00098273 | 0.060167 | 0.01513 | 0.060872 | -66.7702 | 0.015142 | -66.7368 | 56.2427 | 56.1151 | 56.2619 | -66.8467 | -66.7703 | 0.018674 | -66.8048 | 56.1528 | 56.303 | 56.1414 | -67.0378 | -0.095573 | -0.085138 | -0.019062 | 0.014251 | 0.10982 | -0.21274 | -0.065923 | -0.28668 | -0.17506 | -0.019179 | -0.053684 | 0.23299 | -0.024774 | -0.1864 | 122.9938 | 122.8662 | 123.013 | 66.7662 | -123.1745 | 122.9039 | 123.0541 | 122.8925 | 66.7698 | -123.3656
601.8594 | 123.2437 | -66.7694 | 56.2958 | 0.0046549 | -0.0062906 | 0.0013163 | 0.054577 | -0.0031002 | 0.063144 | 0.00015261 | -0.0011301 | -0.0011965 | 0.060167 | 0.015344 | 0.060231 | -66.7656 | 0.015142 | -66.7368 | 56.2381 | 56.1151 | 56.2619 | -66.8375 | -66.7657 | 0.014095 | -66.8048 | 56.1573 | 56.2985 | 56.1323 | -67.0332 | -0.068105 | -0.057672 | 0.003826 | 0.032561 | 0.10067 | -0.1807 | -0.033879 | -0.26379 | -0.13844 | 0.00371 | -0.035374 | 0.22841 | 0.002691 | -0.16352 | 123.0075 | 122.8845 | 123.0313 | 66.7846 | -123.1333 | 122.9267 | 123.0679 | 122.9017 | 66.7835 | -123.329
602.7969 | 123.2529 | -66.7145 | 56.3141 | 0.0046549 | -0.0062906 | 0.0011025 | 0.054577 | -0.0031002 | 0.063358 | 0.015414 | -0.00091653 | -0.0011965 | 0.060167 | 0.01513 | 0.060231 | -66.7656 | 0.015142 | -66.746 | 56.2381 | 56.1242 | 56.2665 | -66.8467 | -66.7749 | 0.009516 | -66.8094 | 56.1482 | 56.303 | 56.146 | -67.0286 | -0.13219 | -0.075983 | -0.051105 | -0.031527 | 0.10067 | -0.18985 | -0.047611 | -0.31414 | -0.16591 | -0.060379 | -0.094884 | 0.21925 | -0.011041 | -0.16809 | 122.9526 | 122.8387 | 122.981 | 66.7296 | -123.1608 | 122.8627 | 123.0175 | 122.8605 | 66.724 | -123.3427
603.7969 | 123.3215 | -66.6962 | 56.3004 | 0.0046549 | -0.0065042 | 0.0011025 | 0.054577 | -0.003314 | 0.062717 | 0.023044 | -0.0013437 | -0.00098273 | 0.05974 | 0.015344 | 0.060231 | -66.7747 | 0.0243 | -66.7368 | 56.2427 | 56.1151 | 56.2573 | -66.8467 | -66.7657 | 0.014095 | -66.8139 | 56.1436 | 56.2985 | 56.1368 | -67.0286 | -0.1505 | -0.057672 | -0.078572 | -0.040681 | 0.10982 | -0.18527 | -0.043036 | -0.33245 | -0.15675 | -0.069532 | -0.11777 | 0.21467 | -0.001887 | -0.16351 | 122.9388 | 122.8112 | 122.9535 | 66.7205 | -123.147 | 122.8398 | 122.9946 | 122.833 | 66.7103 | -123.329
604.8594 | 123.2666 | -66.7465 | 56.2775 | 0.012286 | -0.0065042 | 0.0013163 | 0.054791 | -0.003314 | 0.062717 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060167 | 0.01513 | 0.060231 | -66.7656 | 0.005985 | -66.746 | 56.2335 | 56.1105 | 56.2573 | -66.8467 | -66.7794 | 0.014095 | -66.8185 | 56.1482 | 56.303 | 56.1414 | -67.0332 | -0.10015 | -0.043941 | -0.019062 | 0.000516 | 0.10067 | -0.16697 | -0.020148 | -0.28667 | -0.12928 | -0.032915 | -0.071998 | 0.21468 | 0.02558 | -0.13605 | 122.98 | 122.857 | 123.0038 | 66.7525 | -123.1241 | 122.8947 | 123.0496 | 122.8879 | 66.7606 | -123.3107
605.7969 | 123.2254 | -66.7328 | 56.3141 | 0.012286 | -0.0065042 | 0.0011025 | 0.054363 | -0.003314 | 0.06293 | 0.015414 | -0.00091653 | -0.0011965 | 0.05974 | 0.015558 | 0.060231 | -66.7702 | 0.015142 | -66.7368 | 56.2381 | 56.1059 | 56.2619 | -66.8329 | -66.7657 | 0.014095 | -66.8048 | 56.1436 | 56.2939 | 56.1323 | -67.024 | -0.10015 | -0.075983 | -0.037373 | -0.00406 | 0.096087 | -0.20817 | -0.05219 | -0.29125 | -0.17048 | -0.032911 | -0.071995 | 0.21925 | -0.020198 | -0.18183 | 122.9709 | 122.8387 | 122.9947 | 66.7479 | -123.147 | 122.8764 | 123.0267 | 122.865 | 66.7469 | -123.3381
606.7969 | 123.2208 | -66.7694 | 56.3461 | 0.0046549 | -0.0062906 | 0.0015299 | 0.054363 | -0.003314 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059954 | 0.015558 | 0.060017 | -66.7702 | 0.019721 | -66.746 | 56.2427 | 56.1151 | 56.2619 | -66.8421 | -66.7703 | 0.018674 | -66.8094 | 56.1528 | 56.2939 | 56.1414 | -67.0286 | -0.072684 | -0.10345 | -0.000752 | 0.023404 | 0.096088 | -0.23105 | -0.084233 | -0.25921 | -0.19337 | -0.000869 | -0.039953 | 0.21925 | -0.052241 | -0.20471 | 123.0121 | 122.8845 | 123.0313 | 66.7891 | -123.1882 | 122.9222 | 123.0633 | 122.9108 | 66.7881 | -123.3747
607.7969 | 123.2162 | -66.7419 | 56.3278 | 0.0046549 | -0.0069316 | 0.0011025 | 0.054363 | -0.003314 | 0.062717 | 0.00015261 | -0.0013437 | -0.0014101 | 0.05974 | 0.01513 | 0.060658 | -66.7702 | 0.0243 | -66.746 | 56.2473 | 56.1059 | 56.2619 | -66.8467 | -66.7657 | 0.014095 | -66.8139 | 56.1482 | 56.303 | 56.1414 | -67.0332 | -0.10473 | -0.08056 | -0.028218 | -0.004062 | 0.10067 | -0.2219 | -0.065923 | -0.29125 | -0.17964 | -0.023756 | -0.071998 | 0.21925 | -0.024774 | -0.1864 | 122.9892 | 122.8479 | 123.0038 | 66.7662 | -123.1745 | 122.8901 | 123.045 | 122.8834 | 66.756 | -123.361
608.7969 | 123.2529 | -66.7557 | 56.3141 | 0.0046549 | -0.0062906 | 0.0011025 | 0.054363 | -0.003314 | 0.06293 | 0.015414 | -0.0013437 | -0.00098273 | 0.060167 | 0.015558 | 0.060658 | -66.7702 | 0.019721 | -66.7506 | 56.2427 | 56.1197 | 56.2573 | -66.8421 | -66.7794 | 0.014095 | -66.8048 | 56.1573 | 56.3076 | 56.146 | -67.0286 | -0.086417 | -0.071405 | -0.014485 | 0.005093 | 0.09151 | -0.19443 | -0.056769 | -0.27294 | -0.15675 | -0.02376 | -0.049107 | 0.22383 | -0.006463 | -0.16809 | 122.9984 | 122.8753 | 123.013 | 66.7754 | -123.1562 | 122.913 | 123.0633 | 122.9017 | 66.7698 | -123.3427
609.8594 | 123.2666 | -66.7465 | 56.2729 | -0.0029761 | -0.0062906 | 0.0013163 | 0.054363 | -0.003314 | 0.06293 | 0.015414 | -0.0011301 | -0.0011965 | 0.05974 | 0.015558 | 0.060658 | -66.7656 | 0.019721 | -66.7323 | 56.2335 | 56.1105 | 56.2573 | -66.8375 | -66.7703 | 0.004938 | -66.8094 | 56.1573 | 56.2893 | 56.146 | -67.024 | -0.090993 | -0.039363 | -0.019062 | 0.014251 | 0.10524 | -0.16239 | -0.01557 | -0.27752 | -0.11555 | -0.023757 | -0.062841 | 0.21468 | 0.016422 | -0.12689 | 122.98 | 122.857 | 123.0038 | 66.7662 | -123.1104 | 122.9039 | 123.0358 | 122.8925 | 66.7515 | -123.2969
610.7969 | 123.3124 | -66.7465 | 56.2775 | -0.010607 | -0.0065042 | 0.0015299 | 0.054149 | -0.003314 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059954 | 0.015771 | 0.060017 | -66.7702 | 0.010564 | -66.746 | 56.2473 | 56.1059 | 56.2665 | -66.8513 | -66.7657 | 0.018674 | -66.8094 | 56.1528 | 56.2985 | 56.1323 | -67.0378 | -0.10473 | -0.030206 | -0.02364 | 0.000516 | 0.10525 | -0.17154 | -0.01099 | -0.29125 | -0.12471 | -0.019178 | -0.062841 | 0.22841 | 0.021001 | -0.14521 | 122.9938 | 122.8524 | 123.013 | 66.7571 | -123.1287 | 122.8993 | 123.045 | 122.8788 | 66.7652 | -123.3152
611.7969 | 123.2162 | -66.7465 | 56.3324 | 0.0046549 | -0.0065042 | 0.0013163 | 0.054149 | -0.0037412 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.059954 | 0.015558 | 0.060658 | -66.7702 | 0.019721 | -66.7506 | 56.2335 | 56.1105 | 56.2665 | -66.8467 | -66.7657 | 0.018674 | -66.8094 | 56.1436 | 56.2939 | 56.1323 | -67.0286 | -0.10015 | -0.098872 | -0.02364 | -0.004062 | 0.096089 | -0.2219 | -0.065921 | -0.28209 | -0.18879 | -0.019178 | -0.062841 | 0.21925 | -0.038508 | -0.20014 | 122.98 | 122.857 | 123.013 | 66.7662 | -123.1791 | 122.8901 | 123.0404 | 122.8788 | 66.7652 | -123.361
612.7969 | 123.1842 | -66.7877 | 56.3049 | 0.0046549 | -0.0067178 | 0.0013163 | 0.054149 | -0.003314 | 0.062503 | 0.00015261 | -0.00070293 | -0.0011965 | 0.060167 | 0.015771 | 0.060445 | -66.7656 | 0.019721 | -66.7414 | 56.2381 | 56.1151 | 56.2711 | -66.8467 | -66.7703 | 0.014095 | -66.8185 | 56.1436 | 56.2985 | 56.1552 | -67.0286 | -0.058952 | -0.066828 | 0.022137 | 0.046293 | 0.10524 | -0.18985 | -0.033878 | -0.2409 | -0.16133 | 0.017442 | -0.030799 | 0.2101 | -0.006465 | -0.14978 | 123.0258 | 122.9028 | 123.0588 | 66.8074 | -123.1516 | 122.9313 | 123.0862 | 122.9429 | 66.8018 | -123.3335
613.7969 | 123.2162 | -66.7694 | 56.3095 | 0.012286 | -0.0062906 | 0.0013163 | 0.054363 | -0.0037412 | 0.06293 | 0.015414 | -0.0013437 | -0.0011965 | 0.05974 | 0.015558 | 0.060445 | -66.7656 | 0.015142 | -66.7414 | 56.2381 | 56.1105 | 56.2619 | -66.8467 | -66.7703 | 0.018674 | -66.8048 | 56.1436 | 56.2893 | 56.146 | -67.0286 | -0.077263 | -0.071405 | 0.003826 | 0.027982 | 0.10524 | -0.19901 | -0.047612 | -0.25921 | -0.16591 | -0.000869 | -0.035374 | 0.22383 | -0.020199 | -0.16351 | 123.0075 | 122.8799 | 123.0313 | 66.7846 | -123.1562 | 122.913 | 123.0587 | 122.9154 | 66.7881 | -123.3381
614.8594 | 123.1842 | -66.7694 | 56.3095 | 0.0046549 | -0.0065042 | 0.0013163 | 0.054149 | -0.0031002 | 0.06293 | 0.0077831 | -0.00091653 | -0.00076913 | 0.060381 | 0.015558 | 0.060445 | -66.7656 | 0.019721 | -66.7368 | 56.2427 | 56.1197 | 56.2665 | -66.8421 | -66.7657 | 0.009516 | -66.8094 | 56.1528 | 56.303 | 56.1323 | -67.0286 | -0.072684 | -0.066827 | 0.003826 | 0.032561 | 0.10525 | -0.18985 | -0.043033 | -0.25921 | -0.15675 | 0.00371 | -0.039953 | 0.21925 | -0.006463 | -0.17725 | 123.0121 | 122.8891 | 123.0359 | 66.7891 | -123.1516 | 122.9222 | 123.0725 | 122.9017 | 66.7789 | -123.3381
615.7969 | 123.1979 | -66.7694 | 56.3049 | 0.0046549 | -0.0062906 | 0.0013163 | 0.054149 | -0.003314 | 0.06293 | -0.0074779 | -0.0011301 | -0.0016237 | 0.059954 | 0.015558 | 0.060231 | -66.7702 | 0.015142 | -66.746 | 56.2427 | 56.1105 | 56.2573 | -66.8467 | -66.7749 | 0.014095 | -66.8048 | 56.1528 | 56.3076 | 56.1368 | -67.0378 | -0.077263 | -0.06225 | -0.000752 | 0.023404 | 0.10067 | -0.19443 | -0.047614 | -0.26837 | -0.15217 | -0.005448 | -0.035374 | 0.23299 | 0.002692 | -0.16809 | 123.0121 | 122.8799 | 123.0267 | 66.7846 | -123.1516 | 122.9222 | 123.077 | 122.9062 | 66.7835 | -123.3427
616.7969 | 123.2117 | -66.7969 | 56.3095 | 0.012286 | -0.0067178 | 0.0011025 | 0.054149 | -0.003314 | 0.062717 | 0.0077831 | -0.0013437 | -0.0011965 | 0.060167 | 0.015558 | 0.060445 | -66.7747 | 0.019721 | -66.746 | 56.2335 | 56.1105 | 56.2665 | -66.8238 | -66.7657 | 0.014095 | -66.8048 | 56.1482 | 56.2985 | 56.1414 | -67.0286 | -0.026902 | -0.075984 | 0.022136 | 0.05087 | 0.077772 | -0.19901 | -0.043033 | -0.23174 | -0.16133 | 0.031176 | -0.007908 | 0.22383 | -0.011042 | -0.16809 | 123.0304 | 122.9074 | 123.0634 | 66.8166 | -123.1333 | 122.9451 | 123.0953 | 122.9383 | 66.811 | -123.3381
617.7969 | 123.1842 | -66.8015 | 56.3095 | -0.010607 | -0.0069316 | 0.0013163 | 0.054149 | -0.0031002 | 0.06293 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.01513 | 0.060445 | -66.761 | 0.019721 | -66.7414 | 56.2427 | 56.1105 | 56.2619 | -66.8467 | -66.7749 | 0.014095 | -66.7956 | 56.1528 | 56.2939 | 56.146 | -67.0332 | -0.045219 | -0.066827 | 0.040449 | 0.060026 | 0.10524 | -0.19901 | -0.047612 | -0.23174 | -0.15675 | 0.026596 | 0.005827 | 0.23757 | -0.01562 | -0.16351 | 123.0441 | 122.912 | 123.0633 | 66.8212 | -123.1562 | 122.9542 | 123.0953 | 122.9474 | 66.8155 | -123.3427
618.7969 | 123.3398 | -66.7465 | 56.2454 | 0.0046549 | -0.0067178 | 0.0013163 | 0.054791 | -0.003314 | 0.062717 | 0.00015261 | -0.00091653 | -0.0011965 | 0.060381 | 0.015344 | 0.060017 | -66.7702 | 0.015142 | -66.7368 | 56.2335 | 56.1105 | 56.2527 | -66.8467 | -66.7657 | 0.009516 | -66.8094 | 56.1528 | 56.2985 | 56.1506 | -67.0378 | -0.10015 | -0.011897 | -0.02364 | 0.009673 | 0.10982 | -0.13492 | 0.007318 | -0.29125 | -0.092662 | -0.019178 | -0.062841 | 0.22841 | 0.053045 | -0.094847 | 122.98 | 122.857 | 122.9993 | 66.7617 | -123.0921 | 122.8993 | 123.045 | 122.8971 | 66.756 | -123.2832
619.7969 | 123.1979 | -66.7694 | 56.3232 | -0.0029761 | -0.0062906 | 0.0011025 | 0.054149 | -0.0031002 | 0.06293 | -0.0074779 | -0.0011301 | -0.00076913 | 0.05974 | 0.015771 | 0.060231 | -66.7656 | 0.019721 | -66.746 | 56.2473 | 56.1197 | 56.2665 | -66.8467 | -66.7703 | 0.018674 | -66.8048 | 56.1482 | 56.303 | 56.1414 | -67.0332 | -0.077263 | -0.075982 | 0.003826 | 0.023404 | 0.10067 | -0.20358 | -0.056766 | -0.26379 | -0.17506 | -0.000869 | -0.035374 | 0.22841 | -0.020196 | -0.18182 | 123.0167 | 122.8891 | 123.0359 | 66.7891 | -123.1699 | 122.9176 | 123.0725 | 122.9108 | 66.7881 | -123.3564
620.7969 | 123.3032 | -66.7099 | 56.3141 | 0.0046549 | -0.0065042 | 0.0013163 | 0.054791 | -0.0035276 | 0.062717 | -0.0074779 | -0.00070293 | -0.0011965 | 0.05974 | 0.015344 | 0.060445 | -66.7747 | 0.019721 | -66.7506 | 56.2381 | 56.1197 | 56.2573 | -66.8513 | -66.7703 | 0.014095 | -66.8048 | 56.1619 | 56.303 | 56.1368 | -67.024 | -0.14135 | -0.075983 | -0.064839 | -0.040683 | 0.10067 | -0.19443 | -0.056769 | -0.31414 | -0.15217 | -0.060378 | -0.094883 | 0.21925 | -0.011041 | -0.17725 | 122.948 | 122.8296 | 122.9672 | 66.7296 | -123.1653 | 122.8718 | 123.0129 | 122.8467 | 66.724 | -123.3381
621.8594 | 123.2346 | -66.7786 | 56.3278 | -0.0029761 | -0.0065042 | 0.0015299 | 0.053936 | -0.003314 | 0.06293 | 0.00015261 | -0.00091653 | -0.00098273 | 0.05974 | 0.015771 | 0.060872 | -66.7747 | 0.019721 | -66.7414 | 56.2427 | 56.1059 | 56.2573 | -66.8467 | -66.7703 | 0.014095 | -66.8048 | 56.1528 | 56.303 | 56.1552 | -67.0332 | -0.068108 | -0.085138 | 0.003825 | 0.037137 | 0.10524 | -0.2219 | -0.070502 | -0.25463 | -0.17506 | 0.008286 | -0.026219 | 0.22841 | -0.024774 | -0.17267 | 123.0212 | 122.8845 | 123.0359 | 66.7983 | -123.1745 | 122.9313 | 123.0816 | 122.9337 | 66.7927 | -123.361
622.7969 | 123.2986 | -66.7236 | 56.2546 | 0.0046549 | -0.0062906 | 0.0011025 | 0.054363 | -0.003314 | 0.062717 | -0.015108 | -0.0011301 | -0.00098273 | 0.060167 | 0.015558 | 0.060658 | -66.7702 | 0.0243 | -66.7368 | 56.2381 | 56.1059 | 56.2665 | -66.8421 | -66.7749 | 0.014095 | -66.8048 | 56.1528 | 56.303 | 56.1368 | -67.0332 | -0.11846 | -0.016474 | -0.046528 | -0.013215 | 0.10525 | -0.14866 | 0.011898 | -0.30956 | -0.10182 | -0.051224 | -0.08115 | 0.22841 | 0.048468 | -0.11774 | 122.9617 | 122.8296 | 122.9901 | 66.7479 | -123.0967 | 122.8764 | 123.0267 | 122.8605 | 66.7377 | -123.2878
624.0625 | 123.175 | -66.7877 | 56.3049 | -0.0029761 | -0.0062906 | 0.0013163 | 0.054363 | -0.0035276 | 0.06293 | -0.015108 | -0.0011301 | -0.00076913 | 0.059954 | 0.015771 | 0.060231 | -66.7702 | 0.019721 | -66.7414 | 56.2427 | 56.1197 | 56.2619 | -66.8421 | -66.7703 | 0.014095 | -66.8094 | 56.1528 | 56.2985 | 56.1414 | -67.0195 | -0.054373 | -0.06225 | 0.017559 | 0.046293 | 0.10067 | -0.18527 | -0.043035 | -0.23174 | -0.15217 | 0.017442 | -0.021642 | 0.2101 | -0.006465 | -0.16351 | 123.0304 | 122.9074 | 123.0496 | 66.8074 | -123.147 | 122.9405 | 123.0862 | 122.9291 | 66.8018 | -123.3244
624.7969 | 123.2803 | -66.7603 | 56.2729 | -0.0029761 | -0.0060768 | 0.0011025 | 0.054363 | -0.003314 | 0.062503 | -0.0074779 | -0.0011301 | -0.00098273 | 0.059954 | 0.015771 | 0.060445 | -66.7656 | 0.019721 | -66.7368 | 56.2381 | 56.1151 | 56.2573 | -66.8375 | -66.7657 | 0.009516 | -66.8002 | 56.1528 | 56.3076 | 56.1323 | -67.024 | -0.07726 | -0.034784 | -0.005329 | 0.023406 | 0.10067 | -0.15781 | -0.01557 | -0.26378 | -0.12013 | -0.005445 | -0.039951 | 0.22383 | 0.034736 | -0.14063 | 122.9984 | 122.8753 | 123.0176 | 66.78 | -123.1104 | 122.913 | 123.0679 | 122.8925 | 66.7698 | -123.2969
625.875 | 123.2437 | -66.7557 | 56.3461 | -0.0029761 | -0.0065042 | 0.0013163 | 0.054149 | -0.0035276 | 0.063144 | 0.00015261 | -0.0013437 | -0.0011965 | 0.060167 | 0.015985 | 0.060445 | -66.7747 | 0.019721 | -66.7506 | 56.2427 | 56.1197 | 56.2665 | -66.8604 | -66.7749 | 0.014095 | -66.8048 | 56.1482 | 56.2985 | 56.1414 | -67.0378 | -0.10473 | -0.10345 | -0.019063 | 0.005093 | 0.10983 | -0.22647 | -0.079654 | -0.2821 | -0.19795 | -0.019181 | -0.049107 | 0.23299 | -0.047663 | -0.20471 | 122.9984 | 122.8753 | 123.0222 | 66.7754 | -123.2065 | 122.9039 | 123.0541 | 122.8971 | 66.7698 | -123.3839
626.7969 | 123.262 | -66.7603 | 56.2866 | 0.0046549 | -0.0067178 | 0.0013163 | 0.054577 | -0.003314 | 0.062717 | -0.015108 | -0.0013437 | -0.0011965 | 0.05974 | 0.015985 | 0.060658 | -66.7656 | 0.019721 | -66.746 | 56.2427 | 56.1151 | 56.2573 | -66.8421 | -66.7703 | 0.009516 | -66.8048 | 56.1528 | 56.3122 | 56.1414 | -67.0332 | -0.081839 | -0.043939 | -0.005329 | 0.014249 | 0.096088 | -0.17154 | -0.029303 | -0.27294 | -0.13386 | -0.010024 | -0.044529 | 0.22841 | 0.025582 | -0.1452 | 123.0029 | 122.8753 | 123.0176 | 66.78 | -123.1287 | 122.913 | 123.0725 | 122.9017 | 66.7698 | -123.3198
627.7969 | 123.2803 | -66.7282 | 56.25 | -0.0029761 | -0.0065042 | 0.0011025 | 0.054363 | -0.003314 | 0.062717 | -0.0074779 | -0.0011301 | -0.0011965 | 0.059954 | 0.015558 | 0.060231 | -66.761 | 0.015142 | -66.7506 | 56.2473 | 56.1013 | 56.2527 | -66.8375 | -66.7657 | 0.009516 | -66.8048 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.1093 | -0.00274 | -0.032794 | -0.022373 | 0.086931 | -0.14866 | 0.00274 | -0.30499 | -0.10182 | -0.037489 | -0.076573 | 0.22841 | 0.053046 | -0.104 | 122.9755 | 122.8296 | 122.981 | 66.7434 | -123.0875 | 122.8764 | 123.0313 | 122.8742 | 66.7377 | -123.2832
628.7969 | 123.2574 | -66.7236 | 56.2958 | 0.0046549 | -0.0065042 | 0.0013163 | 0.054791 | -0.0031002 | 0.062717 | 0.015414 | -0.0013437 | -0.00098273 | 0.059954 | 0.015558 | 0.060658 | -66.7702 | 0.019721 | -66.7368 | 56.2381 | 56.1197 | 56.2619 | -66.8421 | -66.7611 | 0.009516 | -66.8002 | 56.1573 | 56.2985 | 56.1414 | -67.0332 | -0.11846 | -0.057672 | -0.046528 | -0.013215 | 0.10525 | -0.17612 | -0.033879 | -0.30956 | -0.13844 | -0.037488 | -0.076572 | 0.23299 | 0.002691 | -0.15436 | 122.9617 | 122.8433 | 122.9855 | 66.7434 | -123.1379 | 122.881 | 123.0221 | 122.8651 | 66.7331 | -123.329
629.7969 | 123.2849 | -66.7099 | 56.2912 | -0.0029761 | -0.0069316 | 0.0011025 | 0.054149 | -0.0031002 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.015771 | 0.060445 | -66.761 | 0.019721 | -66.7414 | 56.2381 | 56.1105 | 56.2482 | -66.8421 | -66.7657 | 0.014095 | -66.8094 | 56.1573 | 56.3076 | 56.146 | -67.0286 | -0.13219 | -0.053095 | -0.051104 | -0.031527 | 0.10067 | -0.1807 | -0.043038 | -0.31872 | -0.13386 | -0.055799 | -0.099462 | 0.21925 | 0.016425 | -0.1452 | 122.948 | 122.8204 | 122.9581 | 66.7296 | -123.1333 | 122.8672 | 123.0175 | 122.8559 | 66.724 | -123.3198
630.7969 | 123.3078 | -66.7145 | 56.2866 | -0.0029761 | -0.0071452 | 0.0013163 | 0.054149 | -0.0028866 | 0.06293 | 0.0077831 | -0.0011301 | -0.00076913 | 0.059954 | 0.015771 | 0.060658 | -66.7656 | 0.019721 | -66.7368 | 56.2381 | 56.1197 | 56.2573 | -66.8513 | -66.7703 | 0.009516 | -66.8048 | 56.1528 | 56.303 | 56.1506 | -67.0332 | -0.13677 | -0.048517 | -0.051105 | -0.02237 | 0.1144 | -0.16696 | -0.029303 | -0.31872 | -0.13386 | -0.0558 | -0.090305 | 0.22841 | 0.016425 | -0.13605 | 122.9526 | 122.8341 | 122.9718 | 66.7342 | -123.1379 | 122.8672 | 123.0175 | 122.8651 | 66.724 | -123.3198
631.7969 | 123.2574 | -66.7374 | 56.2775 | -0.0029761 | -0.0069316 | 0.0015299 | 0.054363 | -0.003314 | 0.06293 | 0.0077831 | -0.0011301 | -0.00076913 | 0.05974 | 0.015771 | 0.060445 | -66.761 | 0.015142 | -66.7414 | 56.2381 | 56.1151 | 56.2619 | -66.8421 | -66.7794 | 0.009516 | -66.8048 | 56.1528 | 56.303 | 56.1323 | -67.0286 | -0.10473 | -0.039362 | -0.023638 | -0.004061 | 0.10067 | -0.16239 | -0.015569 | -0.29125 | -0.12471 | -0.04207 | -0.067417 | 0.22383 | 0.02558 | -0.14521 | 122.9755 | 122.8524 | 122.9993 | 66.7525 | -123.1196 | 122.8901 | 123.0404 | 122.8696 | 66.7469 | -123.3061
632.8594 | 123.2071 | -66.7831 | 56.3187 | -0.0029761 | -0.0071452 | 0.0013163 | 0.054363 | -0.003314 | 0.062717 | 0.0077831 | -0.0011301 | -0.0018375 | 0.059954 | 0.015558 | 0.060658 | -66.761 | 0.019721 | -66.7414 | 56.2427 | 56.1059 | 56.2665 | -66.8513 | -66.7657 | 0.014095 | -66.8002 | 56.1482 | 56.303 | 56.1368 | -67.0332 | -0.068109 | -0.075983 | 0.022138 | 0.041715 | 0.10982 | -0.21274 | -0.052189 | -0.25005 | -0.17048 | 0.017443 | -0.017063 | 0.23299 | -0.015619 | -0.18183 | 123.0258 | 122.8891 | 123.0496 | 66.8029 | -123.1699 | 122.9313 | 123.0862 | 122.92 | 66.7972 | -123.3519
633.7969 | 123.1796 | -66.7053 | 56.3141 | -0.018238 | -0.0067178 | 0.0013163 | 0.054577 | -0.0035276 | 0.063144 | 0.015414 | -0.0011301 | -0.00098273 | 0.060167 | 0.015771 | 0.060445 | -66.7747 | 0.019721 | -66.7323 | 56.2427 | 56.1151 | 56.2573 | -66.8467 | -66.7657 | 0.004938 | -66.8048 | 56.1482 | 56.3076 | 56.1414 | -67.0286 | -0.14135 | -0.071405 | -0.069417 | -0.026948 | 0.1144 | -0.19901 | -0.056769 | -0.32329 | -0.16591 | -0.060377 | -0.099461 | 0.22383 | -0.006463 | -0.17267 | 122.948 | 122.8204 | 122.9626 | 66.725 | -123.1608 | 122.8535 | 123.0129 | 122.8467 | 66.7103 | -123.3427
634.7969 | 123.2758 | -66.7099 | 56.2866 | -0.0029761 | -0.0069316 | 0.0015299 | 0.054791 | -0.0035276 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.060167 | 0.015558 | 0.060445 | -66.7702 | 0.010564 | -66.746 | 56.2381 | 56.1059 | 56.2619 | -66.8421 | -66.7611 | 0.009516 | -66.8139 | 56.1528 | 56.303 | 56.146 | -67.0286 | -0.13219 | -0.048517 | -0.060261 | -0.036105 | 0.096088 | -0.1807 | -0.024724 | -0.31872 | -0.13386 | -0.051221 | -0.10404 | 0.21467 | 0.016425 | -0.14062 | 122.948 | 122.8158 | 122.9718 | 66.7205 | -123.1287 | 122.8627 | 123.0129 | 122.8559 | 66.7194 | -123.3152
635.7969 | 123.2803 | -66.7236 | 56.3004 | 0.0046549 | -0.0067178 | 0.0013163 | 0.054577 | -0.0037412 | 0.062717 | 0.00015261 | -0.00091653 | -0.00076913 | 0.059954 | 0.015985 | 0.060445 | -66.7656 | 0.015142 | -66.7414 | 56.2381 | 56.1197 | 56.2619 | -66.8467 | -66.7703 | 0.014095 | -66.8094 | 56.1482 | 56.303 | 56.1368 | -67.0286 | -0.12304 | -0.06225 | -0.04195 | -0.017794 | 0.10524 | -0.1807 | -0.038457 | -0.30498 | -0.15217 | -0.046645 | -0.085729 | 0.21925 | 0.002692 | -0.16351 | 122.9617 | 122.8433 | 122.9855 | 66.7388 | -123.147 | 122.8718 | 123.0267 | 122.8605 | 66.7377 | -123.329
636.8594 | 123.3124 | -66.687 | 56.3324 | 0.0046549 | -0.0071452 | 0.0013163 | 0.054577 | -0.0031002 | 0.062717 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059527 | 0.015985 | 0.060017 | -66.7656 | 0.015142 | -66.746 | 56.2427 | 56.1013 | 56.2619 | -66.8421 | -66.7657 | 0.004938 | -66.8094 | 56.1573 | 56.2985 | 56.1414 | -67.0332 | -0.15508 | -0.089715 | -0.078571 | -0.058993 | 0.096088 | -0.23105 | -0.0705 | -0.34618 | -0.17506 | -0.078687 | -0.12235 | 0.22383 | -0.03393 | -0.19098 | 122.9297 | 122.7884 | 122.9489 | 66.7022 | -123.1745 | 122.8444 | 122.9855 | 122.8284 | 66.6919 | -123.3656
637.7969 | 123.2895 | -66.7511 | 56.3004 | 0.012286 | -0.0071452 | 0.0011025 | 0.054577 | -0.0031002 | 0.063144 | 0.0077831 | -0.0015573 | -0.00098273 | 0.059954 | 0.015985 | 0.060231 | -66.7656 | 0.019721 | -66.7368 | 56.2289 | 56.1059 | 56.2619 | -66.8375 | -66.7611 | 0.014095 | -66.8048 | 56.1528 | 56.303 | 56.146 | -67.0332 | -0.086415 | -0.071407 | -0.014484 | 0.014251 | 0.10067 | -0.19443 | -0.038457 | -0.2821 | -0.14759 | -0.010022 | -0.053684 | 0.22841 | 0.002692 | -0.15436 | 122.98 | 122.857 | 123.013 | 66.7708 | -123.1379 | 122.9039 | 123.0541 | 122.8971 | 66.7652 | -123.3335
638.7969 | 123.3032 | -66.7236 | 56.3049 | -0.0029761 | -0.0065042 | 0.0013163 | 0.054577 | -0.003314 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.015771 | 0.060231 | -66.7656 | 0.015142 | -66.7368 | 56.2335 | 56.1151 | 56.2573 | -66.8467 | -66.7611 | 0.014095 | -66.8002 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.12304 | -0.071407 | -0.04195 | -0.013215 | 0.10982 | -0.18985 | -0.047614 | -0.30956 | -0.15675 | -0.037488 | -0.076572 | 0.23299 | -0.001886 | -0.15894 | 122.9572 | 122.8387 | 122.981 | 66.7388 | -123.1516 | 122.8718 | 123.0267 | 122.8696 | 66.7377 | -123.3381
639.8594 | 123.1934 | -66.7557 | 56.3049 | 0.012286 | -0.0073588 | 0.0011025 | 0.054149 | -0.003314 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059954 | 0.015985 | 0.060658 | -66.7656 | 0.019721 | -66.7414 | 56.2473 | 56.1242 | 56.2665 | -66.8375 | -66.7611 | 0.009516 | -66.8002 | 56.1528 | 56.303 | 56.1368 | -67.0332 | -0.081838 | -0.057672 | -0.009907 | 0.014249 | 0.096087 | -0.1807 | -0.038456 | -0.27752 | -0.15217 | -0.005445 | -0.044529 | 0.23299 | -0.001886 | -0.16809 | 123.0029 | 122.8799 | 123.0222 | 66.7754 | -123.1424 | 122.9084 | 123.0587 | 122.8925 | 66.7652 | -123.3381
640.7969 | 123.1888 | -66.774 | 56.3461 | -0.0029761 | -0.0071452 | 0.0011025 | 0.054149 | -0.003314 | 0.06293 | 0.0077831 | -0.0011301 | -0.0014101 | 0.059527 | 0.015985 | 0.060445 | -66.761 | 0.010564 | -66.7323 | 56.2381 | 56.1151 | 56.2619 | -66.8421 | -66.7657 | 0.009516 | -66.8048 | 56.1528 | 56.3076 | 56.1414 | -67.0378 | -0.068106 | -0.10803 | 0.012983 | 0.041717 | 0.10982 | -0.23105 | -0.084233 | -0.26379 | -0.19337 | 0.008288 | -0.030796 | 0.23299 | -0.038506 | -0.20471 | 123.0121 | 122.8891 | 123.0359 | 66.7846 | -123.1882 | 122.9267 | 123.0816 | 122.9154 | 66.7835 | -123.3839
641.7969 | 123.2986 | -66.7145 | 56.2866 | 0.0046549 | -0.0069316 | 0.0011025 | 0.054577 | -0.0035276 | 0.062717 | 0.0077831 | -0.0011301 | -0.0011965 | 0.060167 | 0.016199 | 0.060017 | -66.761 | 0.015142 | -66.7323 | 56.2381 | 56.1013 | 56.2573 | -66.8375 | -66.7657 | 0.014095 | -66.8094 | 56.139 | 56.303 | 56.146 | -67.0332 | -0.12304 | -0.048517 | -0.046526 | -0.017792 | 0.10524 | -0.18528 | -0.029303 | -0.31872 | -0.1476 | -0.051221 | -0.094884 | 0.22383 | 0.016425 | -0.14062 | 122.9526 | 122.8158 | 122.9718 | 66.7296 | -123.1241 | 122.8535 | 123.0175 | 122.8605 | 66.7286 | -123.3198
642.7969 | 123.3032 | -66.6916 | 56.3049 | 0.0046549 | -0.0067178 | 0.0011025 | 0.054363 | -0.003314 | 0.063144 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.016199 | 0.060445 | -66.7656 | 0.010564 | -66.7323 | 56.2427 | 56.1242 | 56.2711 | -66.8421 | -66.7657 | 0.014095 | -66.8094 | 56.1573 | 56.303 | 56.1323 | -67.0332 | -0.1505 | -0.06225 | -0.073994 | -0.040681 | 0.10982 | -0.1807 | -0.033878 | -0.34161 | -0.14759 | -0.07411 | -0.11777 | 0.22383 | -0.001886 | -0.17267 | 122.9343 | 122.8158 | 122.9626 | 66.7022 | -123.147 | 122.8489 | 122.9946 | 122.8238 | 66.7057 | -123.3381
643.7969 | 123.3261 | -66.7053 | 56.282 | -0.0029761 | -0.0069316 | 0.0011025 | 0.054149 | -0.0037412 | 0.062717 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059954 | 0.015771 | 0.060445 | -66.7656 | 0.015142 | -66.7414 | 56.2381 | 56.1059 | 56.2619 | -66.8421 | -66.7703 | 0.009516 | -66.8094 | 56.1482 | 56.303 | 56.1368 | -67.0332 | -0.13677 | -0.043939 | -0.060261 | -0.036105 | 0.10067 | -0.17612 | -0.020146 | -0.32787 | -0.13386 | -0.064956 | -0.10404 | 0.22383 | 0.021003 | -0.1452 | 122.9434 | 122.8112 | 122.9672 | 66.7205 | -123.1241 | 122.8535 | 123.0084 | 122.8422 | 66.7148 | -123.3152
644.7969 | 123.2666 | -66.7099 | 56.3232 | -0.0029761 | -0.0071452 | 0.0011025 | 0.054149 | -0.0031002 | 0.062717 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059954 | 0.015771 | 0.060445 | -66.761 | 0.010564 | -66.7368 | 56.2427 | 56.1151 | 56.2619 | -66.8467 | -66.7703 | 0.004938 | -66.8002 | 56.1482 | 56.3076 | 56.146 | -67.0332 | -0.13677 | -0.08056 | -0.051104 | -0.026948 | 0.10982 | -0.20816 | -0.061345 | -0.3233 | -0.17506 | -0.060378 | -0.090305 | 0.23299 | -0.015618 | -0.17725 | 122.9526 | 122.825 | 122.9718 | 66.7205 | -123.1699 | 122.8581 | 123.0175 | 122.8559 | 66.7148 | -123.3564
645.7969 | 123.4177 | -66.7007 | 56.3507 | 0.0046549 | -0.0067178 | 0.0011025 | 0.054149 | -0.003314 | 0.062289 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059954 | 0.015985 | 0.060231 | -66.761 | 0.015142 | -66.7323 | 56.2427 | 56.1105 | 56.2573 | -66.8467 | -66.7703 | 0.009516 | -66.7956 | 56.1482 | 56.3076 | 56.1368 | -67.024 | -0.14593 | -0.10803 | -0.060259 | -0.031525 | 0.1144 | -0.24021 | -0.09339 | -0.32329 | -0.20253 | -0.069533 | -0.094881 | 0.22841 | -0.043084 | -0.21387 | 122.9434 | 122.8112 | 122.9581 | 66.7159 | -123.1974 | 122.8489 | 123.0084 | 122.8376 | 66.7103 | -123.3747
646.8594 | 123.2941 | -66.7419 | 56.2317 | -0.0029761 | -0.0067178 | 0.0013163 | 0.054363 | -0.0035276 | 0.063144 | 0.00015261 | -0.0011301 | -0.00076913 | 0.060167 | 0.016199 | 0.060445 | -66.7656 | 0.010564 | -66.7368 | 56.2427 | 56.1013 | 56.2665 | -66.8467 | -66.7611 | 0.009516 | -66.8094 | 56.1436 | 56.2985 | 56.1368 | -67.0286 | -0.10473 | 0.010993 | -0.02364 | 0.005095 | 0.10982 | -0.13035 | 0.034787 | -0.28667 | -0.088086 | -0.019178 | -0.067419 | 0.21925 | 0.066778 | -0.09485 | 122.9846 | 122.8433 | 123.0084 | 66.7525 | -123.0784 | 122.8855 | 123.0404 | 122.8788 | 66.7515 | -123.2603
647.7969 | 123.3078 | -66.7236 | 56.3187 | -0.010607 | -0.0065042 | 0.0011025 | 0.054577 | -0.0035276 | 0.062503 | 0.00015261 | -0.00091653 | -0.00076913 | 0.059527 | 0.016199 | 0.060658 | -66.7702 | 0.010564 | -66.7277 | 56.2473 | 56.1105 | 56.2665 | -66.8375 | -66.7611 | 0.000359 | -66.8002 | 56.1436 | 56.303 | 56.1414 | -67.0286 | -0.11388 | -0.071405 | -0.046528 | -0.004059 | 0.10982 | -0.20817 | -0.052189 | -0.30498 | -0.17506 | -0.037488 | -0.076572 | 0.22841 | -0.015619 | -0.17725 | 122.9709 | 122.8341 | 122.9901 | 66.7342 | -123.1562 | 122.8672 | 123.0267 | 122.8651 | 66.724 | -123.3473
648.875 | 123.2071 | -66.774 | 56.2866 | -0.0029761 | -0.0065042 | 0.0013163 | 0.054363 | -0.003314 | 0.062717 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059954 | 0.015985 | 0.060231 | -66.7656 | 0.019721 | -66.7368 | 56.2335 | 56.1151 | 56.2619 | -66.8467 | -66.7611 | 0.009516 | -66.8002 | 56.1528 | 56.303 | 56.1277 | -67.0332 | -0.072685 | -0.053096 | 0.008404 | 0.037139 | 0.10982 | -0.17154 | -0.024724 | -0.25921 | -0.13386 | 0.012866 | -0.026218 | 0.23299 | 0.016425 | -0.15894 | 123.0075 | 122.8891 | 123.0359 | 66.7937 | -123.1333 | 122.9267 | 123.077 | 122.9017 | 66.7835 | -123.3198
649.7969 | 123.3032 | -66.7328 | 56.337 | -0.0029761 | -0.0071452 | 0.0013163 | 0.054577 | -0.0035276 | 0.062717 | 0.00015261 | -0.0011301 | -0.0011965 | 0.05974 | 0.015771 | 0.060445 | -66.761 | 0.010564 | -66.7368 | 56.2381 | 56.1151 | 56.2619 | -66.8421 | -66.7657 | 0.009516 | -66.8048 | 56.1528 | 56.2893 | 56.1323 | -67.0378 | -0.10931 | -0.098871 | -0.028216 | -0.00406 | 0.10525 | -0.2219 | -0.075078 | -0.30499 | -0.18422 | -0.032911 | -0.071995 | 0.23299 | -0.047665 | -0.20472 | 122.9709 | 122.8479 | 122.9947 | 66.7434 | -123.1791 | 122.8855 | 123.0221 | 122.865 | 66.7423 | -123.3747
650.875 | 123.3032 | -66.7511 | 56.2592 | -0.0029761 | -0.0069316 | 0.0013163 | 0.054577 | -0.0035276 | 0.062717 | 0.015414 | -0.0011301 | -0.0011965 | 0.05974 | 0.015985 | 0.060445 | -66.761 | 0.019721 | -66.746 | 56.2381 | 56.1059 | 56.2665 | -66.8467 | -66.7657 | 0.014095 | -66.8002 | 56.1528 | 56.2985 | 56.1277 | -67.0378 | -0.095573 | -0.021051 | -0.009905 | 0.005094 | 0.10067 | -0.15323 | 0.007321 | -0.28668 | -0.10639 | -0.0146 | -0.049106 | 0.23757 | 0.039312 | -0.13147 | 122.9892 | 122.857 | 123.0176 | 66.7708 | -123.1058 | 122.9039 | 123.0496 | 122.8788 | 66.7652 | -123.2969
651.9219 | 123.3444 | -66.7282 | 56.2683 | 0.0046549 | -0.0069316 | 0.0011025 | 0.054577 | -0.003314 | 0.06293 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059954 | 0.015985 | 0.060231 | -66.761 | 0.015142 | -66.7368 | 56.2381 | 56.1105 | 56.2665 | -66.8513 | -66.7749 | 0.009516 | -66.8048 | 56.1528 | 56.2985 | 56.1414 | -67.0332 | -0.12304 | -0.030207 | -0.032794 | -0.008638 | 0.1144 | -0.15781 | -0.001835 | -0.30499 | -0.11555 | -0.046647 | -0.076573 | 0.22841 | 0.030156 | -0.12689 | 122.9663 | 122.8387 | 122.9947 | 66.7434 | -123.1196 | 122.881 | 123.0267 | 122.8696 | 66.7377 | -123.3015
652.7969 | 123.1842 | -66.7419 | 56.3507 | -0.0029761 | -0.0067178 | 0.0013163 | 0.054577 | -0.0037412 | 0.062717 | 0.0077831 | -0.0013437 | -0.00098273 | 0.05974 | 0.016199 | 0.060231 | -66.7564 | 0.010564 | -66.7414 | 56.2381 | 56.1151 | 56.2711 | -66.8467 | -66.7703 | 0.009516 | -66.8094 | 56.1482 | 56.2985 | 56.146 | -67.0286 | -0.10473 | -0.1126 | -0.014483 | 0.000516 | 0.10524 | -0.23563 | -0.079654 | -0.28667 | -0.20253 | -0.028335 | -0.067419 | 0.21925 | -0.052241 | -0.20471 | 122.98 | 122.857 | 123.013 | 66.7525 | -123.1974 | 122.8901 | 123.0404 | 122.8879 | 66.7515 | -123.3793
653.8594 | 123.2941 | -66.7099 | 56.282 | 0.0046549 | -0.0071452 | 0.0011025 | 0.054791 | -0.003314 | 0.06293 | 0.015414 | -0.0013437 | -0.0011965 | 0.059954 | 0.015771 | 0.060445 | -66.761 | 0.010564 | -66.7323 | 56.2381 | 56.1059 | 56.2665 | -66.8421 | -66.7703 | 0.009516 | -66.8048 | 56.1482 | 56.2985 | 56.146 | -67.0332 | -0.13219 | -0.043939 | -0.051104 | -0.02237 | 0.10982 | -0.17612 | -0.015567 | -0.3233 | -0.13386 | -0.060378 | -0.094883 | 0.22841 | 0.016424 | -0.13605 | 122.948 | 122.8158 | 122.9764 | 66.7205 | -123.1241 | 122.8581 | 123.0084 | 122.8559 | 66.7194 | -123.3152
654.875 | 123.175 | -66.7465 | 56.3141 | 0.0046549 | -0.0071452 | 0.0013163 | 0.054363 | -0.0035276 | 0.062717 | 0.0077831 | -0.0013437 | -0.0011965 | 0.05974 | 0.016199 | 0.060017 | -66.761 | 0.019721 | -66.746 | 56.2427 | 56.1105 | 56.2573 | -66.8467 | -66.7611 | 0.009516 | -66.8048 | 56.1482 | 56.2893 | 56.1414 | -67.0424 | -0.10015 | -0.071405 | -0.014483 | 0.000516 | 0.10067 | -0.20359 | -0.056769 | -0.29583 | -0.16591 | -0.0146 | -0.058262 | 0.23757 | -0.024777 | -0.17267 | 122.9892 | 122.857 | 123.0038 | 66.7662 | -123.1608 | 122.8947 | 123.0358 | 122.8879 | 66.756 | -123.3564
655.8281 | 123.2758 | -66.7236 | 56.3141 | -0.0029761 | -0.0073588 | 0.0011025 | 0.053936 | -0.003314 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059954 | 0.016412 | 0.060231 | -66.7564 | 0.019721 | -66.7368 | 56.2335 | 56.1242 | 56.2665 | -66.8513 | -66.7657 | 0.009516 | -66.8094 | 56.1482 | 56.2985 | 56.1597 | -67.0332 | -0.12762 | -0.080562 | -0.032793 | -0.013215 | 0.1144 | -0.18985 | -0.047611 | -0.30956 | -0.16591 | -0.042066 | -0.085729 | 0.22383 | -0.01562 | -0.15436 | 122.9572 | 122.8479 | 122.9901 | 66.7434 | -123.1653 | 122.8718 | 123.0221 | 122.8834 | 66.7331 | -123.3473
656.8594 | 123.262 | -66.7374 | 56.2775 | -0.010607 | -0.0069316 | 0.00088894 | 0.054363 | -0.0037412 | 0.063144 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059527 | 0.015985 | 0.060445 | -66.761 | 0.019721 | -66.7368 | 56.2381 | 56.1242 | 56.2573 | -66.8513 | -66.7565 | 0.009516 | -66.8048 | 56.1482 | 56.303 | 56.1368 | -67.0332 | -0.11389 | -0.039362 | -0.023638 | 0.000518 | 0.1144 | -0.15323 | -0.020148 | -0.29583 | -0.12928 | -0.019176 | -0.067417 | 0.22841 | 0.02558 | -0.14063 | 122.9755 | 122.8616 | 122.9947 | 66.7571 | -123.1287 | 122.8855 | 123.0404 | 122.8742 | 66.7469 | -123.3107
657.7969 | 123.2208 | -66.7328 | 56.3324 | 0.0046549 | -0.0069316 | 0.0013163 | 0.054363 | -0.003955 | 0.062717 | 0.0077831 | -0.0011301 | -0.00076913 | 0.060167 | 0.016199 | 0.060445 | -66.7656 | 0.005985 | -66.7368 | 56.2427 | 56.1151 | 56.2665 | -66.8467 | -66.7657 | 0.004938 | -66.8094 | 56.1436 | 56.2985 | 56.1414 | -67.0286 | -0.11388 | -0.089715 | -0.032795 | -0.00406 | 0.10982 | -0.21732 | -0.065921 | -0.29583 | -0.18879 | -0.032911 | -0.076574 | 0.21925 | -0.03393 | -0.19098 | 122.9755 | 122.8479 | 122.9993 | 66.7388 | -123.1791 | 122.8764 | 123.0313 | 122.8742 | 66.7377 | -123.361
658.7969 | 123.2117 | -66.7786 | 56.3095 | 0.012286 | -0.0069316 | 0.00088894 | 0.054577 | -0.003314 | 0.062503 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059527 | 0.015985 | 0.060231 | -66.761 | 0.010564 | -66.7368 | 56.2427 | 56.1197 | 56.2619 | -66.8467 | -66.7565 | 0.009516 | -66.8002 | 56.1528 | 56.303 | 56.146 | -67.0286 | -0.068108 | -0.066827 | 0.01756 | 0.041716 | 0.10982 | -0.18985 | -0.047612 | -0.25005 | -0.15675 | 0.022022 | -0.021641 | 0.22841 | -0.006463 | -0.16351 | 123.0212 | 122.8982 | 123.0405 | 66.7891 | -123.1562 | 122.9313 | 123.0816 | 122.9246 | 66.7881 | -123.3381
659.7969 | 123.1979 | -66.7053 | 56.3095 | -0.0029761 | -0.0073588 | 0.0013163 | 0.054149 | -0.003314 | 0.062503 | 0.0077831 | -0.0013437 | -0.0011965 | 0.05974 | 0.016199 | 0.060658 | -66.7656 | 0.015142 | -66.7277 | 56.2381 | 56.1242 | 56.2619 | -66.8467 | -66.7657 | 0.009516 | -66.8048 | 56.1482 | 56.2985 | 56.1414 | -67.0378 | -0.14135 | -0.071405 | -0.060261 | -0.02237 | 0.11898 | -0.18527 | -0.047612 | -0.33245 | -0.16133 | -0.060377 | -0.099461 | 0.23299 | -0.011042 | -0.16809 | 122.9434 | 122.8296 | 122.9672 | 66.7205 | -123.1562 | 122.8535 | 123.0038 | 122.8467 | 66.7148 | -123.3473
660.7969 | 123.2391 | -66.7465 | 56.3095 | 0.0046549 | -0.0075726 | 0.0013163 | 0.054577 | -0.003314 | 0.063358 | -0.0074779 | -0.0011301 | -0.0011965 | 0.05974 | 0.016199 | 0.060445 | -66.761 | 0.015142 | -66.7414 | 56.2381 | 56.1242 | 56.2665 | -66.8238 | -66.7749 | 0.009516 | -66.8048 | 56.1528 | 56.3076 | 56.146 | -67.0286 | -0.077256 | -0.071405 | -0.014483 | 0.005094 | 0.08235 | -0.18527 | -0.043033 | -0.28209 | -0.15675 | -0.028336 | -0.058262 | 0.22383 | -0.001885 | -0.16351 | 122.9846 | 122.8708 | 123.013 | 66.7617 | -123.1333 | 122.8993 | 123.0541 | 122.8925 | 66.756 | -123.3381
661.8438 | 123.2758 | -66.7511 | 56.282 | -0.010607 | -0.0071452 | 0.0011025 | 0.054363 | -0.0035276 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.05974 | 0.015771 | 0.060445 | -66.7564 | 0.019721 | -66.7277 | 56.2381 | 56.1105 | 56.2573 | -66.8467 | -66.7657 | 0.004938 | -66.8048 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.095573 | -0.043939 | -0.005327 | 0.023407 | 0.11898 | -0.17154 | -0.024725 | -0.2821 | -0.13386 | -0.0146 | -0.053684 | 0.22841 | 0.021003 | -0.13605 | 122.9892 | 122.8616 | 123.0084 | 66.7708 | -123.1287 | 122.8993 | 123.0541 | 122.8971 | 66.756 | -123.3152
662.7969 | 123.1979 | -66.7374 | 56.3278 | -0.0029761 | -0.0071452 | 0.0011025 | 0.054577 | -0.0035276 | 0.063144 | 0.00015261 | -0.0013437 | -0.0014101 | 0.059954 | 0.016199 | 0.060231 | -66.7702 | 0.010564 | -66.7414 | 56.2427 | 56.1151 | 56.2665 | -66.8467 | -66.7749 | 0.009516 | -66.8048 | 56.1482 | 56.303 | 56.1506 | -67.0378 | -0.10931 | -0.085138 | -0.032795 | -0.004061 | 0.10524 | -0.21274 | -0.061344 | -0.30041 | -0.17964 | -0.037491 | -0.067417 | 0.23299 | -0.024774 | -0.17724 | 122.98 | 122.8524 | 123.0038 | 66.7479 | -123.1745 | 122.8855 | 123.0404 | 122.8879 | 66.7469 | -123.3656
663.8438 | 123.3582 | -66.6779 | 56.282 | -0.010607 | -0.0073588 | 0.0011025 | 0.054363 | -0.0037412 | 0.062717 | 0.0077831 | -0.0013437 | -0.00098273 | 0.060167 | 0.016412 | 0.060658 | -66.761 | 0.010564 | -66.7506 | 56.2381 | 56.1288 | 56.2665 | -66.8513 | -66.7703 | 0.004938 | -66.8002 | 56.1528 | 56.2985 | 56.1368 | -67.0286 | -0.17339 | -0.043939 | -0.083148 | -0.072727 | 0.10067 | -0.15323 | -0.015567 | -0.35076 | -0.12928 | -0.092422 | -0.12235 | 0.22841 | 0.016424 | -0.1452 | 122.916 | 122.8067 | 122.9443 | 66.6884 | -123.1333 | 122.8306 | 122.9763 | 122.8147 | 66.6828 | -123.3107
664.7969 | 123.1796 | -66.7694 | 56.3141 | 0.0046549 | -0.0073588 | 0.0015299 | 0.054149 | -0.0037412 | 0.063144 | 0.0077831 | -0.0013437 | -0.0011965 | 0.05974 | 0.016412 | 0.060658 | -66.7656 | 0.010564 | -66.7414 | 56.2473 | 56.1242 | 56.2665 | -66.8467 | -66.7657 | 0.004938 | -66.8002 | 56.1528 | 56.2985 | 56.1414 | -67.0332 | -0.077263 | -0.066827 | 0.003826 | 0.027982 | 0.10524 | -0.18985 | -0.047611 | -0.26379 | -0.16133 | 0.00371 | -0.030796 | 0.23299 | -0.01562 | -0.17267 | 123.0167 | 122.8936 | 123.0359 | 66.78 | -123.1608 | 122.9222 | 123.0679 | 122.9108 | 66.7743 | -123.3473
665.7969 | 123.1888 | -66.7465 | 56.3232 | 0.0046549 | -0.0073588 | 0.0017435 | 0.053936 | -0.0035276 | 0.06293 | 0.015414 | -0.0011301 | -0.0011965 | 0.059954 | 0.01684 | 0.060445 | -66.7656 | 0.015142 | -66.746 | 56.2427 | 56.1105 | 56.2665 | -66.8329 | -66.7657 | 0.009516 | -66.8002 | 56.1528 | 56.3076 | 56.1552 | -67.0332 | -0.086414 | -0.08056 | -0.019062 | 0.000516 | 0.08693 | -0.21274 | -0.056766 | -0.28667 | -0.17048 | -0.019178 | -0.053684 | 0.23299 | -0.015618 | -0.16809 | 122.9892 | 122.857 | 123.013 | 66.7617 | -123.1562 | 122.8993 | 123.0541 | 122.9017 | 66.756 | -123.3564
666.7969 | 123.2208 | -66.7419 | 56.2637 | -0.010607 | -0.0075726 | 0.0011025 | 0.054363 | -0.003314 | 0.062717 | -0.015108 | -0.0013437 | -0.0011965 | 0.05974 | 0.016412 | 0.060017 | -66.761 | 0.015142 | -66.746 | 56.2335 | 56.1151 | 56.2619 | -66.8375 | -66.7749 | 0.014095 | -66.7956 | 56.1528 | 56.3122 | 56.1323 | -67.0378 | -0.095571 | -0.030208 | -0.019061 | -0.004062 | 0.091509 | -0.14865 | -0.001836 | -0.29583 | -0.11097 | -0.032914 | -0.053683 | 0.24215 | 0.04847 | -0.13147 | 122.9755 | 122.857 | 123.0038 | 66.7571 | -123.1012 | 122.8947 | 123.0541 | 122.8742 | 66.756 | -123.3015
667.7969 | 123.2071 | -66.7511 | 56.3141 | 0.012286 | -0.0073588 | 0.0013163 | 0.054363 | -0.0028866 | 0.06293 | 0.015414 | -0.0013437 | -0.0011965 | 0.05974 | 0.016626 | 0.060445 | -66.761 | 0.010564 | -66.746 | 56.2427 | 56.1242 | 56.2619 | -66.8467 | -66.7749 | 0.009516 | -66.8048 | 56.1436 | 56.3076 | 56.146 | -67.0332 | -0.095573 | -0.071405 | -0.009905 | 0.005094 | 0.10067 | -0.18985 | -0.05219 | -0.2821 | -0.17048 | -0.023758 | -0.053684 | 0.22841 | -0.006463 | -0.16809 | 122.9938 | 122.8753 | 123.013 | 66.7617 | -123.1608 | 122.8947 | 123.0587 | 122.8971 | 66.7606 | -123.3473
668.7969 | 123.2025 | -66.7648 | 56.3004 | -0.018238 | -0.0071452 | 0.0015299 | 0.054363 | -0.003955 | 0.063144 | 0.00015261 | -0.00091653 | -0.00098273 | 0.05974 | 0.016412 | 0.060445 | -66.7656 | 0.015142 | -66.7368 | 56.2427 | 56.1105 | 56.2711 | -66.8421 | -66.7703 | 0.009516 | -66.8048 | 56.1528 | 56.303 | 56.1323 | -67.0286 | -0.077261 | -0.057672 | -0.000751 | 0.027984 | 0.10525 | -0.18985 | -0.0293 | -0.26378 | -0.14759 | -0.005446 | -0.039951 | 0.22383 | 0.002692 | -0.16809 | 123.0075 | 122.8753 | 123.0359 | 66.78 | -123.1424 | 122.9176 | 123.0679 | 122.8971 | 66.7743 | -123.329
669.8438 | 123.2574 | -66.7419 | 56.2958 | -0.0029761 | -0.0077862 | 0.0011025 | 0.054791 | -0.003314 | 0.06293 | -0.0074779 | -0.0013437 | -0.00076913 | 0.060167 | 0.016199 | 0.060231 | -66.761 | 0.015142 | -66.746 | 56.2473 | 56.1242 | 56.2665 | -66.8375 | -66.7657 | 0.018674 | -66.8002 | 56.1528 | 56.3076 | 56.1506 | -67.0332 | -0.095571 | -0.048516 | -0.019061 | -0.004062 | 0.091509 | -0.17154 | -0.0293 | -0.29125 | -0.14302 | -0.023756 | -0.058262 | 0.23299 | 0.011848 | -0.1452 | 122.9892 | 122.8662 | 123.0084 | 66.7571 | -123.1333 | 122.8947 | 123.0496 | 122.8925 | 66.7606 | -123.329
670.7969 | 123.2346 | -66.7328 | 56.2958 | 0.0046549 | -0.0073588 | 0.0015299 | 0.054363 | -0.0037412 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.059954 | 0.016412 | 0.060231 | -66.7564 | 0.010564 | -66.7414 | 56.2427 | 56.1151 | 56.2665 | -66.8467 | -66.7657 | 0.004938 | -66.7956 | 56.1528 | 56.303 | 56.1368 | -67.0378 | -0.11388 | -0.053094 | -0.023638 | -0.008639 | 0.10524 | -0.1807 | -0.0293 | -0.30499 | -0.14302 | -0.032911 | -0.062838 | 0.24215 | 0.00727 | -0.15894 | 122.9755 | 122.8479 | 122.9993 | 66.7434 | -123.1424 | 122.8855 | 123.0358 | 122.8696 | 66.7377 | -123.3336
671.8438 | 123.1705 | -66.7648 | 56.282 | -0.010607 | -0.0075726 | 0.0013163 | 0.054363 | -0.0035276 | 0.06293 | 0.015414 | -0.0015573 | -0.0011965 | 0.05974 | 0.016412 | 0.060445 | -66.7564 | 0.010564 | -66.7414 | 56.2427 | 56.1242 | 56.2665 | -66.8513 | -66.7703 | 0.004938 | -66.8094 | 56.1619 | 56.2985 | 56.1506 | -67.0286 | -0.086419 | -0.039361 | 0.008406 | 0.023405 | 0.10982 | -0.15781 | -0.015567 | -0.26378 | -0.12013 | -0.005446 | -0.04453 | 0.21925 | 0.016424 | -0.13147 | 123.0075 | 122.8891 | 123.0313 | 66.7754 | -123.1333 | 122.9267 | 123.0633 | 122.9154 | 66.7698 | -123.3107
672.7969 | 123.1522 | -66.7694 | 56.3141 | -0.0029761 | -0.0075726 | 0.0011025 | 0.054363 | -0.0035276 | 0.062717 | -0.0074779 | -0.00091653 | -0.00076913 | 0.059527 | 0.016626 | 0.060445 | -66.7518 | 0.015142 | -66.7506 | 56.2335 | 56.1197 | 56.2619 | -66.8421 | -66.7703 | 0.009516 | -66.8002 | 56.1482 | 56.3076 | 56.1368 | -67.0424 | -0.072684 | -0.080562 | 0.017562 | 0.018826 | 0.09151 | -0.19443 | -0.05219 | -0.27294 | -0.16591 | -0.000869 | -0.030796 | 0.24215 | -0.006463 | -0.17725 | 123.0029 | 122.8891 | 123.0313 | 66.7846 | -123.1562 | 122.9176 | 123.077 | 122.9062 | 66.7789 | -123.3564
673.8438 | 123.2529 | -66.7557 | 56.2958 | -0.0029761 | -0.0075726 | 0.0011025 | 0.054363 | -0.0035276 | 0.063144 | 0.0077831 | -0.0013437 | -0.00098273 | 0.060167 | 0.016626 | 0.060017 | -66.761 | 0.010564 | -66.746 | 56.2427 | 56.1242 | 56.2665 | -66.8421 | -66.7703 | 0.009516 | -66.791 | 56.1482 | 56.2985 | 56.1414 | -67.0286 | -0.086417 | -0.053094 | -0.005328 | 0.009671 | 0.096088 | -0.17154 | -0.0293 | -0.27294 | -0.14759 | -0.014602 | -0.035371 | 0.23757 | 0.002691 | -0.15436 | 122.9984 | 122.8799 | 123.0222 | 66.7662 | -123.1379 | 122.9039 | 123.0541 | 122.8971 | 66.7652 | -123.3244
674.7969 | 123.2117 | -66.7557 | 56.3324 | -0.0029761 | -0.0071452 | 0.0011025 | 0.054149 | -0.0035276 | 0.06293 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059954 | 0.016626 | 0.060445 | -66.7656 | 0.019721 | -66.746 | 56.2473 | 56.1197 | 56.2711 | -66.8375 | -66.7657 | 0.004938 | -66.8002 | 56.1573 | 56.303 | 56.1414 | -67.0332 | -0.081838 | -0.085137 | -0.009907 | 0.009671 | 0.091509 | -0.21274 | -0.061343 | -0.27752 | -0.17506 | -0.010023 | -0.044529 | 0.23299 | -0.029351 | -0.19098 | 123.0029 | 122.8753 | 123.0267 | 66.7754 | -123.1699 | 122.913 | 123.0587 | 122.8971 | 66.7606 | -123.3656
675.7969 | 123.2712 | -66.7328 | 56.282 | -0.0029761 | -0.0075726 | 0.0011025 | 0.054363 | -0.0035276 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.016412 | 0.060445 | -66.761 | 0.010564 | -66.7414 | 56.2427 | 56.1197 | 56.2756 | -66.8467 | -66.7611 | 0.009516 | -66.8002 | 56.1573 | 56.303 | 56.1506 | -67.0378 | -0.11388 | -0.039361 | -0.028216 | -0.008639 | 0.10524 | -0.16239 | -0.00641 | -0.30499 | -0.1247 | -0.028333 | -0.067417 | 0.23757 | 0.021003 | -0.13147 | 122.9755 | 122.8524 | 123.0084 | 66.7434 | -123.1287 | 122.8901 | 123.0358 | 122.8834 | 66.7423 | -123.3198
676.8438 | 123.1842 | -66.7374 | 56.3324 | 0.019917 | -0.0073588 | 0.0013163 | 0.054363 | -0.0035276 | 0.062503 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059954 | 0.016412 | 0.060445 | -66.7564 | 0.001407 | -66.746 | 56.2381 | 56.1105 | 56.2665 | -66.8421 | -66.7657 | 0.014095 | -66.8048 | 56.1528 | 56.3076 | 56.1414 | -67.0424 | -0.10473 | -0.094293 | -0.01906 | -0.008639 | 0.096088 | -0.2219 | -0.065921 | -0.30499 | -0.17964 | -0.028333 | -0.067417 | 0.23757 | -0.024773 | -0.19098 | 122.9755 | 122.8479 | 123.0038 | 66.7388 | -123.1745 | 122.8901 | 123.045 | 122.8788 | 66.7515 | -123.3748
677.7969 | 123.23 | -66.774 | 56.2729 | 0.0046549 | -0.0073588 | 0.0013163 | 0.054363 | -0.0031002 | 0.062717 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059954 | 0.016626 | 0.060445 | -66.761 | 0.010564 | -66.746 | 56.2381 | 56.1105 | 56.2665 | -66.8467 | -66.7611 | 0.004938 | -66.8002 | 56.1528 | 56.3076 | 56.1277 | -67.0332 | -0.072685 | -0.034784 | 0.012983 | 0.027982 | 0.10067 | -0.16239 | -0.006412 | -0.25921 | -0.12013 | 0.012866 | -0.026218 | 0.23299 | 0.034736 | -0.14521 | 123.0121 | 122.8845 | 123.0405 | 66.7846 | -123.1196 | 122.9267 | 123.0816 | 122.9017 | 66.7789 | -123.3061
678.7969 | 123.2895 | -66.7282 | 56.2683 | 0.012286 | -0.0073588 | 0.0011025 | 0.054149 | -0.003314 | 0.062289 | 0.00015261 | -0.0017711 | -0.00098273 | 0.059954 | 0.016626 | 0.060445 | -66.761 | 0.010564 | -66.7414 | 56.2335 | 56.1105 | 56.2619 | -66.8329 | -66.7611 | 0.014095 | -66.8048 | 56.1528 | 56.3122 | 56.1414 | -67.0424 | -0.10473 | -0.034786 | -0.032794 | -0.013217 | 0.091508 | -0.15781 | -0.006414 | -0.31414 | -0.11555 | -0.032911 | -0.076573 | 0.23757 | 0.043892 | -0.12689 | 122.9617 | 122.8387 | 122.9901 | 66.7388 | -123.1012 | 122.881 | 123.0404 | 122.8696 | 66.7423 | -123.3107
679.7969 | 123.1842 | -66.7786 | 56.2912 | -0.018238 | -0.0071452 | 0.0011025 | 0.054149 | -0.0035276 | 0.06293 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059954 | 0.016412 | 0.060231 | -66.7656 | 0.010564 | -66.746 | 56.2335 | 56.1151 | 56.2711 | -66.8467 | -66.7657 | 0.009516 | -66.7956 | 56.1528 | 56.303 | 56.1506 | -67.0286 | -0.068108 | -0.057674 | 0.012981 | 0.032559 | 0.10067 | -0.17612 | -0.020145 | -0.25005 | -0.13844 | 0.012865 | -0.017062 | 0.23299 | 0.011847 | -0.14062 | 123.0121 | 122.8936 | 123.0496 | 66.7891 | -123.1379 | 122.9313 | 123.0816 | 122.9291 | 66.7881 | -123.3198
680.7969 | 123.262 | -66.7328 | 56.2775 | -0.010607 | -0.0075726 | 0.0013163 | 0.054363 | -0.0035276 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059527 | 0.016412 | 0.060445 | -66.761 | 0.010564 | -66.7414 | 56.2381 | 56.1059 | 56.2665 | -66.8375 | -66.7611 | 0.009516 | -66.7956 | 56.1528 | 56.3122 | 56.1231 | -67.0378 | -0.10473 | -0.039362 | -0.028216 | -0.008639 | 0.096087 | -0.17154 | -0.01099 | -0.30499 | -0.12471 | -0.028333 | -0.062838 | 0.24215 | 0.034737 | -0.15436 | 122.9709 | 122.8387 | 122.9993 | 66.7434 | -123.115 | 122.8855 | 123.045 | 122.8559 | 66.7423 | -123.3152
681.7969 | 123.1888 | -66.774 | 56.2958 | -0.010607 | -0.0073588 | 0.0015299 | 0.054363 | -0.003314 | 0.062717 | 0.00015261 | -0.0011301 | -0.0011965 | 0.05974 | 0.016626 | 0.060231 | -66.761 | 0.015142 | -66.7277 | 56.2427 | 56.1151 | 56.2665 | -66.8375 | -66.7565 | 0.000359 | -66.7956 | 56.1573 | 56.303 | 56.1323 | -67.0378 | -0.063527 | -0.053094 | 0.012983 | 0.046295 | 0.10982 | -0.1807 | -0.0293 | -0.26379 | -0.13844 | 0.017445 | -0.021639 | 0.24215 | 0.00727 | -0.16352 | 123.0167 | 122.8891 | 123.0405 | 66.7891 | -123.1333 | 122.9313 | 123.077 | 122.9062 | 66.7743 | -123.3336
682.7969 | 123.2758 | -66.7282 | 56.282 | -0.0029761 | -0.0073588 | 0.0017435 | 0.054577 | -0.0035276 | 0.062717 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059527 | 0.01684 | 0.060231 | -66.7564 | 0.005985 | -66.7368 | 56.2427 | 56.1197 | 56.2665 | -66.8467 | -66.7703 | 0.000359 | -66.8048 | 56.1528 | 56.2985 | 56.1414 | -67.0332 | -0.11846 | -0.039361 | -0.028216 | -0.008638 | 0.10982 | -0.16239 | -0.015567 | -0.30499 | -0.12928 | -0.042068 | -0.076573 | 0.22841 | 0.016424 | -0.14062 | 122.9709 | 122.8479 | 122.9947 | 66.7342 | -123.1287 | 122.881 | 123.0267 | 122.8696 | 66.7286 | -123.3152
683.8438 | 123.2574 | -66.7236 | 56.2866 | 0.0046549 | -0.0077862 | 0.0015299 | 0.054363 | -0.0035276 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.060167 | 0.016626 | 0.060231 | -66.7564 | 0.010564 | -66.7506 | 56.2381 | 56.1197 | 56.2711 | -66.8467 | -66.7703 | 0.004938 | -66.8002 | 56.1528 | 56.3076 | 56.1231 | -67.0332 | -0.12304 | -0.048517 | -0.032793 | -0.02695 | 0.096089 | -0.16696 | -0.015567 | -0.30956 | -0.13386 | -0.046645 | -0.076572 | 0.23299 | 0.021003 | -0.16352 | 122.9617 | 122.8433 | 122.9947 | 66.7342 | -123.1333 | 122.8764 | 123.0313 | 122.8467 | 66.7286 | -123.3198
684.7969 | 123.2849 | -66.7236 | 56.2775 | 0.0046549 | -0.0071452 | 0.0015299 | 0.054363 | -0.0037412 | 0.063144 | -0.0074779 | -0.0011301 | -0.00098273 | 0.059954 | 0.01684 | 0.060231 | -66.7564 | 0.005985 | -66.7323 | 56.2381 | 56.1151 | 56.2619 | -66.8375 | -66.7657 | 0.004938 | -66.7956 | 56.1573 | 56.2939 | 56.1323 | -67.0378 | -0.11388 | -0.039362 | -0.032793 | -0.008637 | 0.10524 | -0.16239 | -0.015569 | -0.31414 | -0.12013 | -0.042066 | -0.071993 | 0.24215 | 0.016423 | -0.14521 | 122.9617 | 122.8387 | 122.9855 | 66.7296 | -123.115 | 122.881 | 123.0175 | 122.8559 | 66.7286 | -123.3152
685.7969 | 123.2803 | -66.7099 | 56.2729 | -0.0029761 | -0.0077862 | 0.0013163 | 0.054149 | -0.0035276 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.05974 | 0.016626 | 0.060445 | -66.7564 | 0.010564 | -66.7414 | 56.2381 | 56.1105 | 56.2665 | -66.8467 | -66.7703 | 0.009516 | -66.8048 | 56.1528 | 56.2985 | 56.146 | -67.0332 | -0.13677 | -0.034784 | -0.046526 | -0.031527 | 0.10524 | -0.16239 | -0.006412 | -0.3233 | -0.12013 | -0.060378 | -0.094883 | 0.22841 | 0.025579 | -0.12689 | 122.948 | 122.8204 | 122.9764 | 66.7205 | -123.1196 | 122.8627 | 123.0084 | 122.8559 | 66.7194 | -123.3061
686.8438 | 123.2483 | -66.774 | 56.3049 | -0.0029761 | -0.0071452 | 0.00088894 | 0.054149 | -0.0037412 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.016412 | 0.060445 | -66.7564 | 0.015142 | -66.7368 | 56.2427 | 56.1197 | 56.2619 | -66.8467 | -66.7703 | 0.009516 | -66.8002 | 56.1528 | 56.303 | 56.1323 | -67.0332 | -0.072685 | -0.06225 | 0.017561 | 0.037139 | 0.10982 | -0.18527 | -0.043035 | -0.25921 | -0.15217 | 0.003709 | -0.026218 | 0.23299 | -0.001886 | -0.17267 | 123.0167 | 122.8936 | 123.0359 | 66.7891 | -123.1516 | 122.9267 | 123.077 | 122.9062 | 66.7835 | -123.3381
687.7969 | 123.262 | -66.7419 | 56.2912 | 0.0046549 | -0.0075726 | 0.0013163 | 0.054149 | -0.0037412 | 0.06293 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059954 | 0.016412 | 0.060445 | -66.761 | 0.005985 | -66.7414 | 56.2381 | 56.1059 | 56.2711 | -66.8467 | -66.7703 | 0.004938 | -66.8002 | 56.1528 | 56.3076 | 56.1323 | -67.0332 | -0.10473 | -0.053095 | -0.019061 | 0.000516 | 0.10524 | -0.18528 | -0.020145 | -0.29125 | -0.13844 | -0.028335 | -0.058262 | 0.23299 | 0.016425 | -0.15894 | 122.98 | 122.8479 | 123.013 | 66.7479 | -123.1379 | 122.8947 | 123.0496 | 122.8742 | 66.7469 | -123.3244
688.7969 | 123.3078 | -66.7099 | 56.3004 | -0.0029761 | -0.0075726 | 0.0011025 | 0.054791 | -0.0035276 | 0.06293 | -0.0074779 | -0.0013437 | -0.00076913 | 0.059527 | 0.016626 | 0.060231 | -66.7564 | 0.010564 | -66.746 | 56.2381 | 56.1151 | 56.2711 | -66.8467 | -66.7611 | 0.004938 | -66.8002 | 56.1528 | 56.3076 | 56.1368 | -67.0332 | -0.13677 | -0.06225 | -0.046526 | -0.036105 | 0.10067 | -0.18527 | -0.0293 | -0.3233 | -0.14759 | -0.051221 | -0.090305 | 0.23299 | 0.00727 | -0.16351 | 122.948 | 122.825 | 122.981 | 66.7205 | -123.147 | 122.8627 | 123.0175 | 122.8467 | 66.7148 | -123.3335
689.7969 | 123.2437 | -66.7282 | 56.2866 | -0.0029761 | -0.0077862 | 0.0011025 | 0.054149 | -0.0037412 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.016626 | 0.060231 | -66.7518 | 0.010564 | -66.746 | 56.2427 | 56.1197 | 56.2619 | -66.8421 | -66.7657 | 0.009516 | -66.8094 | 56.1482 | 56.303 | 56.1414 | -67.0378 | -0.11388 | -0.043939 | -0.023637 | -0.017795 | 0.096088 | -0.16696 | -0.024724 | -0.30956 | -0.13844 | -0.037489 | -0.081152 | 0.22841 | 0.016425 | -0.1452 | 122.9709 | 122.8479 | 122.9901 | 66.7388 | -123.1287 | 122.8764 | 123.0313 | 122.8696 | 66.7377 | -123.3244
690.8438 | 123.2986 | -66.7282 | 56.3049 | -0.0029761 | -0.0075726 | 0.0015299 | 0.054363 | -0.0037412 | 0.062717 | -0.0074779 | -0.0013437 | -0.00076913 | 0.059527 | 0.016626 | 0.060445 | -66.761 | 0.015142 | -66.7368 | 56.2473 | 56.1105 | 56.2619 | -66.8329 | -66.7611 | 0.004938 | -66.8002 | 56.1436 | 56.303 | 56.146 | -67.0286 | -0.10473 | -0.057672 | -0.032794 | -0.008638 | 0.096087 | -0.19443 | -0.043035 | -0.30041 | -0.16133 | -0.032911 | -0.071995 | 0.22841 | -0.001886 | -0.15894 | 122.9755 | 122.8387 | 122.9901 | 66.7434 | -123.1379 | 122.8718 | 123.0313 | 122.8742 | 66.7331 | -123.3335
691.7969 | 123.2849 | -66.7145 | 56.2866 | 0.0046549 | -0.0073588 | 0.0015299 | 0.054577 | -0.003314 | 0.062717 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059527 | 0.016412 | 0.060445 | -66.761 | 0.001407 | -66.746 | 56.2335 | 56.1151 | 56.2711 | -66.8421 | -66.7703 | 0.009516 | -66.8048 | 56.1482 | 56.303 | 56.1277 | -67.0332 | -0.12762 | -0.053096 | -0.046526 | -0.031527 | 0.096088 | -0.17154 | -0.015567 | -0.31872 | -0.13844 | -0.0558 | -0.090305 | 0.22841 | 0.016425 | -0.15894 | 122.948 | 122.8296 | 122.9855 | 66.7159 | -123.1287 | 122.8627 | 123.0175 | 122.8422 | 66.724 | -123.3198
692.8438 | 123.2803 | -66.7465 | 56.3416 | -0.0029761 | -0.0077862 | 0.00088894 | 0.054577 | -0.0035276 | 0.06293 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059527 | 0.01684 | 0.060445 | -66.7564 | 0.010564 | -66.746 | 56.2381 | 56.1105 | 56.2665 | -66.8421 | -66.7703 | 0.004938 | -66.8048 | 56.1482 | 56.303 | 56.1368 | -67.0332 | -0.095572 | -0.10345 | -0.009905 | 0.000516 | 0.096088 | -0.23105 | -0.075077 | -0.28667 | -0.19337 | -0.023757 | -0.058262 | 0.22841 | -0.038507 | -0.20471 | 122.9846 | 122.857 | 123.013 | 66.7571 | -123.1836 | 122.8947 | 123.0496 | 122.8834 | 66.7515 | -123.3747
693.7969 | 123.2803 | -66.7419 | 56.2775 | 0.0046549 | -0.0073588 | 0.0011025 | 0.054577 | -0.003314 | 0.063358 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.01684 | 0.060231 | -66.761 | 0.010564 | -66.7414 | 56.2427 | 56.1105 | 56.2619 | -66.8467 | -66.7749 | 0.004938 | -66.8094 | 56.1482 | 56.3122 | 56.1506 | -67.0378 | -0.10473 | -0.034784 | -0.019061 | 0.000516 | 0.10524 | -0.16697 | -0.015569 | -0.29583 | -0.12928 | -0.032914 | -0.067419 | 0.22841 | 0.034737 | -0.12689 | 122.9846 | 122.8524 | 123.0038 | 66.7525 | -123.1241 | 122.8901 | 123.0541 | 122.8925 | 66.7469 | -123.3152
694.7969 | 123.3398 | -66.7007 | 56.3049 | -0.010607 | -0.0073588 | 0.0011025 | 0.054577 | -0.0037412 | 0.062717 | 0.015414 | -0.0013437 | -0.00076913 | 0.059954 | 0.016626 | 0.060231 | -66.761 | 0.010564 | -66.746 | 56.2427 | 56.1242 | 56.2711 | -66.8513 | -66.7611 | 0.004938 | -66.8002 | 56.1528 | 56.3076 | 56.1414 | -67.0378 | -0.15051 | -0.06225 | -0.060259 | -0.04526 | 0.10525 | -0.1807 | -0.033878 | -0.33703 | -0.15217 | -0.060376 | -0.09946 | 0.23757 | 0.002692 | -0.16351 | 122.9434 | 122.825 | 122.9718 | 66.7113 | -123.1562 | 122.8535 | 123.0084 | 122.8422 | 66.7057 | -123.3427
695.7969 | 123.2986 | -66.7145 | 56.2866 | -0.0029761 | -0.0075726 | 0.0013163 | 0.054577 | -0.0037412 | 0.063144 | 0.015414 | -0.0013437 | -0.00098273 | 0.059954 | 0.016626 | 0.060445 | -66.761 | 0.005985 | -66.7368 | 56.2427 | 56.1151 | 56.2756 | -66.8421 | -66.7611 | 0.004938 | -66.8048 | 56.1528 | 56.3076 | 56.1414 | -67.0424 | -0.12762 | -0.043939 | -0.046526 | -0.02237 | 0.10525 | -0.17154 | -0.010988 | -0.32788 | -0.13386 | -0.046643 | -0.090305 | 0.23757 | 0.021003 | -0.1452 | 122.9572 | 122.8296 | 122.9901 | 66.7205 | -123.1287 | 122.8672 | 123.0221 | 122.8559 | 66.7194 | -123.329
696.7969 | 123.3261 | -66.7053 | 56.3141 | -0.0029761 | -0.0075726 | 0.0013163 | 0.054149 | -0.003955 | 0.063144 | 0.0077831 | -0.0011301 | -0.0014101 | 0.05974 | 0.01684 | 0.060231 | -66.7564 | 0.001407 | -66.746 | 56.2473 | 56.1059 | 56.2619 | -66.8421 | -66.7657 | 0.000359 | -66.8002 | 56.1573 | 56.303 | 56.1277 | -67.0424 | -0.13677 | -0.066827 | -0.051104 | -0.040683 | 0.096088 | -0.20817 | -0.05219 | -0.33703 | -0.15675 | -0.060377 | -0.094883 | 0.24215 | -0.011041 | -0.18641 | 122.9526 | 122.8112 | 122.9672 | 66.7067 | -123.1562 | 122.8627 | 123.0084 | 122.833 | 66.7057 | -123.3564
697.8438 | 123.1705 | -66.7969 | 56.3187 | -0.0029761 | -0.0075726 | 0.00088894 | 0.054363 | -0.0037412 | 0.062717 | 0.00015261 | -0.0011301 | -0.0014101 | 0.05974 | 0.017053 | 0.060445 | -66.7518 | 0.005985 | -66.746 | 56.2473 | 56.1151 | 56.2711 | -66.8467 | -66.7703 | 0.009516 | -66.7956 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.049797 | -0.071405 | 0.045028 | 0.05087 | 0.10067 | -0.20359 | -0.047611 | -0.23632 | -0.17048 | 0.026597 | 0.001249 | 0.23757 | -0.015619 | -0.17267 | 123.0441 | 122.912 | 123.0679 | 66.8029 | -123.1653 | 122.9451 | 123.0999 | 122.9429 | 66.8064 | -123.3519
698.7969 | 123.1979 | -66.774 | 56.3324 | 0.0046549 | -0.008 | 0.0011025 | 0.054577 | -0.003955 | 0.063144 | -0.0074779 | -0.0013437 | -0.0014101 | 0.059954 | 0.016412 | 0.060017 | -66.7564 | 0.005985 | -66.7414 | 56.2381 | 56.1151 | 56.2665 | -66.8467 | -66.7611 | 0.009516 | -66.8048 | 56.1528 | 56.3076 | 56.146 | -67.0378 | -0.072685 | -0.094293 | 0.017561 | 0.03256 | 0.10524 | -0.21732 | -0.065921 | -0.26379 | -0.17964 | 0.012866 | -0.030796 | 0.23299 | -0.024773 | -0.1864 | 123.0121 | 122.8891 | 123.0405 | 66.78 | -123.1791 | 122.9267 | 123.0816 | 122.92 | 66.7835 | -123.3702
699.7969 | 123.3307 | -66.7099 | 56.337 | 0.0046549 | -0.0077862 | 0.0013163 | 0.054577 | -0.0037412 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059527 | 0.016626 | 0.060231 | -66.761 | 0.005985 | -66.746 | 56.2381 | 56.1151 | 56.2619 | -66.8467 | -66.7657 | 0.000359 | -66.8002 | 56.1573 | 56.303 | 56.1552 | -67.0378 | -0.13677 | -0.098871 | -0.051104 | -0.036105 | 0.10067 | -0.2219 | -0.075078 | -0.32787 | -0.17964 | -0.055799 | -0.090305 | 0.23757 | -0.033929 | -0.18182 | 122.948 | 122.825 | 122.9718 | 66.7159 | -123.1836 | 122.8672 | 123.0129 | 122.8651 | 66.7103 | -123.3747
700.8438 | 123.2208 | -66.6733 | 56.2958 | 0.0046549 | -0.0075726 | 0.0011025 | 0.054791 | -0.0037412 | 0.06293 | 0.0077831 | -0.00091653 | -0.0014101 | 0.05974 | 0.01684 | 0.059804 | -66.761 | 0.010564 | -66.746 | 56.2427 | 56.1197 | 56.2665 | -66.8467 | -66.7657 | 0.009516 | -66.7956 | 56.1482 | 56.2985 | 56.1368 | -67.0332 | -0.17339 | -0.053094 | -0.087725 | -0.072726 | 0.10067 | -0.17612 | -0.0293 | -0.35992 | -0.14759 | -0.09242 | -0.12235 | 0.23757 | 0.002691 | -0.15894 | 122.916 | 122.7929 | 122.9398 | 66.6838 | -123.1424 | 122.8215 | 122.9717 | 122.8101 | 66.6828 | -123.329
701.7969 | 123.3124 | -66.7328 | 56.2866 | 0.0046549 | -0.0075726 | 0.0011025 | 0.054577 | -0.0035276 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059954 | 0.01684 | 0.060231 | -66.7564 | 0.005985 | -66.7414 | 56.2473 | 56.1197 | 56.2756 | -66.8421 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.303 | 56.1506 | -67.0378 | -0.10931 | -0.039361 | -0.023638 | -0.008639 | 0.10067 | -0.16696 | -0.010988 | -0.30499 | -0.13844 | -0.028333 | -0.067417 | 0.23757 | 0.016425 | -0.13605 | 122.98 | 122.8524 | 123.0084 | 66.7388 | -123.1287 | 122.881 | 123.0358 | 122.8834 | 66.7331 | -123.3244
702.8438 | 123.2346 | -66.7648 | 56.3095 | -0.0029761 | -0.0073588 | 0.0011025 | 0.054149 | -0.003955 | 0.062503 | -0.0074779 | -0.0011301 | -0.0011965 | 0.059954 | 0.017053 | 0.060017 | -66.7564 | 0.010564 | -66.7368 | 56.2381 | 56.1151 | 56.2756 | -66.8421 | -66.7657 | 0.004938 | -66.8002 | 56.1573 | 56.2939 | 56.1368 | -67.0332 | -0.077261 | -0.071405 | 0.008406 | 0.027984 | 0.10525 | -0.19443 | -0.033876 | -0.26836 | -0.15217 | -0.000867 | -0.035373 | 0.23299 | -0.01562 | -0.17267 | 123.0029 | 122.8799 | 123.0405 | 66.7754 | -123.1516 | 122.9222 | 123.0587 | 122.9017 | 66.7698 | -123.3427
703.7969 | 123.3032 | -66.7282 | 56.3095 | 0.0046549 | -0.0077862 | 0.0013163 | 0.054577 | -0.003314 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.059527 | 0.016626 | 0.060017 | -66.761 | 0.010564 | -66.7368 | 56.2427 | 56.1197 | 56.2711 | -66.8375 | -66.7611 | 0.014095 | -66.8048 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.1093 | -0.066827 | -0.032794 | -0.008638 | 0.10067 | -0.18985 | -0.038455 | -0.30499 | -0.16133 | -0.032911 | -0.076573 | 0.22841 | -0.006463 | -0.16351 | 122.9709 | 122.8479 | 122.9993 | 66.7388 | -123.147 | 122.8764 | 123.0313 | 122.8742 | 66.7423 | -123.3427
704.8438 | 123.2254 | -66.7557 | 56.2775 | 0.0046549 | -0.0077862 | 0.0017435 | 0.054363 | -0.003955 | 0.062717 | -0.015108 | -0.0011301 | -0.00098273 | 0.060167 | 0.017267 | 0.060231 | -66.761 | 0.005985 | -66.7368 | 56.2473 | 56.1151 | 56.2665 | -66.8467 | -66.7611 | 0.009516 | -66.7956 | 56.1482 | 56.303 | 56.1368 | -67.0378 | -0.090996 | -0.030206 | -0.005328 | 0.018828 | 0.10982 | -0.16239 | -0.01099 | -0.2821 | -0.12928 | -0.005445 | -0.03995 | 0.24215 | 0.02558 | -0.14063 | 123.0029 | 122.8708 | 123.0222 | 66.7617 | -123.1241 | 122.9039 | 123.0587 | 122.8925 | 66.7652 | -123.3152
705.7969 | 123.2208 | -66.7603 | 56.3507 | 0.0046549 | -0.0075726 | 0.0015299 | 0.054363 | -0.0035276 | 0.062503 | 0.023044 | -0.00091653 | -0.0011965 | 0.05974 | 0.016626 | 0.060231 | -66.7518 | -0.003172 | -66.7414 | 56.2381 | 56.1242 | 56.2711 | -66.8421 | -66.7611 | 0.000359 | -66.7956 | 56.1528 | 56.303 | 56.1414 | -67.0332 | -0.081839 | -0.1126 | 0.008407 | 0.018827 | 0.10067 | -0.22647 | -0.079654 | -0.27294 | -0.19795 | -0.000867 | -0.035372 | 0.23757 | -0.047662 | -0.20929 | 122.9984 | 122.8845 | 123.0313 | 66.7571 | -123.1928 | 122.913 | 123.0633 | 122.9017 | 66.7606 | -123.3839
706.7969 | 123.2025 | -66.7511 | 56.3232 | -0.0029761 | -0.0077862 | 0.0015299 | 0.054149 | -0.0037412 | 0.062717 | 0.0077831 | -0.0015573 | -0.00098273 | 0.059313 | 0.01684 | 0.060445 | -66.761 | 0.005985 | -66.7323 | 56.2427 | 56.1242 | 56.2802 | -66.8375 | -66.7611 | 0.004938 | -66.8002 | 56.1482 | 56.303 | 56.1277 | -67.0378 | -0.086415 | -0.08056 | -0.009905 | 0.018829 | 0.10524 | -0.199 | -0.043031 | -0.28668 | -0.17506 | -0.010022 | -0.049106 | 0.23757 | -0.020196 | -0.19556 | 122.9938 | 122.8753 | 123.0313 | 66.7571 | -123.1608 | 122.8993 | 123.0541 | 122.8788 | 66.756 | -123.361
707.7969 | 123.1979 | -66.7465 | 56.3232 | 0.012286 | -0.0077862 | 0.0013163 | 0.054363 | -0.0037412 | 0.062717 | 0.00015261 | -0.0013437 | -0.0014101 | 0.059954 | 0.01684 | 0.060445 | -66.761 | 0.010564 | -66.7368 | 56.2427 | 56.1288 | 56.2711 | -66.8467 | -66.7611 | 0.004938 | -66.8048 | 56.1436 | 56.303 | 56.1323 | -67.0378 | -0.10015 | -0.08056 | -0.014483 | 0.009673 | 0.10982 | -0.19443 | -0.052188 | -0.29125 | -0.17964 | -0.0146 | -0.058262 | 0.23299 | -0.020196 | -0.19098 | 122.9892 | 122.8753 | 123.0176 | 66.7571 | -123.1699 | 122.8901 | 123.0496 | 122.8788 | 66.7515 | -123.361
708.7969 | 123.2071 | -66.7282 | 56.3278 | -0.010607 | -0.0082136 | 0.00088894 | 0.054363 | -0.003955 | 0.062717 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059954 | 0.017267 | 0.060445 | -66.7564 | 0.010564 | -66.746 | 56.2473 | 56.1105 | 56.2665 | -66.8467 | -66.7657 | 0.000359 | -66.7956 | 56.1482 | 56.2985 | 56.1414 | -67.0332 | -0.11846 | -0.08056 | -0.028216 | -0.017795 | 0.10067 | -0.21732 | -0.061344 | -0.30499 | -0.17964 | -0.037489 | -0.067416 | 0.23757 | -0.029353 | -0.1864 | 122.9755 | 122.8387 | 122.9947 | 66.7388 | -123.1745 | 122.8764 | 123.0267 | 122.8696 | 66.7286 | -123.361
709.8438 | 123.3856 | -66.7648 | 56.2546 | -0.0029761 | -0.0077862 | 0.00088894 | 0.054363 | -0.003314 | 0.062717 | -0.0074779 | -0.0017711 | -0.0011965 | 0.059954 | 0.01684 | 0.060445 | -66.7656 | 0.005985 | -66.746 | 56.2381 | 56.1105 | 56.2711 | -66.8375 | -66.7657 | 0.004938 | -66.8048 | 56.1482 | 56.3076 | 56.1277 | -67.0286 | -0.072682 | -0.016474 | -0.000751 | 0.018827 | 0.091509 | -0.14408 | 0.016476 | -0.26378 | -0.1064 | -0.000867 | -0.039951 | 0.22383 | 0.053046 | -0.1269 | 123.0029 | 122.8753 | 123.0359 | 66.7708 | -123.0921 | 122.913 | 123.0725 | 122.8925 | 66.7698 | -123.2832
710.7969 | 123.1796 | -66.7603 | 56.3004 | 0.012286 | -0.0075726 | 0.0011025 | 0.054149 | -0.003955 | 0.06293 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059954 | 0.017053 | 0.060445 | -66.7564 | 0.005985 | -66.746 | 56.2427 | 56.1105 | 56.2711 | -66.8421 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.2985 | 56.1414 | -67.0424 | -0.081839 | -0.057672 | 0.003828 | 0.014249 | 0.096088 | -0.18985 | -0.0293 | -0.2821 | -0.15217 | -0.000867 | -0.039951 | 0.24215 | -0.001887 | -0.15894 | 123.0029 | 122.8708 | 123.0313 | 66.7662 | -123.1424 | 122.9084 | 123.0587 | 122.9017 | 66.7606 | -123.3427
711.7969 | 123.1888 | -66.7419 | 56.3141 | -0.0029761 | -0.0082136 | 0.0017435 | 0.054577 | -0.0037412 | 0.062717 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059954 | 0.01684 | 0.060445 | -66.7518 | 0.010564 | -66.7414 | 56.2427 | 56.1242 | 56.2756 | -66.8558 | -66.7703 | 0.004938 | -66.8002 | 56.1436 | 56.303 | 56.1414 | -67.0469 | -0.11389 | -0.071405 | -0.009904 | 0.000516 | 0.1144 | -0.18985 | -0.038454 | -0.30499 | -0.17048 | -0.028335 | -0.058262 | 0.24673 | -0.011041 | -0.17267 | 122.9846 | 122.8662 | 123.0176 | 66.7525 | -123.1699 | 122.8855 | 123.045 | 122.8834 | 66.7469 | -123.361
712.7969 | 123.2162 | -66.7557 | 56.3232 | 0.012286 | -0.0082136 | 0.0011025 | 0.053936 | -0.0037412 | 0.063358 | -0.015108 | -0.0015573 | -0.00098273 | 0.060167 | 0.017053 | 0.060445 | -66.7564 | 0.010564 | -66.7414 | 56.2427 | 56.1288 | 56.2756 | -66.8558 | -66.7611 | 0.000359 | -66.7956 | 56.1482 | 56.3076 | 56.146 | -67.0424 | -0.10015 | -0.08056 | -0.00075 | 0.014249 | 0.1144 | -0.19443 | -0.047609 | -0.28668 | -0.17506 | -0.005445 | -0.03995 | 0.24673 | -0.015618 | -0.17725 | 122.9984 | 122.8845 | 123.0313 | 66.7662 | -123.1791 | 122.9039 | 123.0633 | 122.9017 | 66.756 | -123.3656
713.8438 | 123.2117 | -66.7648 | 56.3095 | -0.0029761 | -0.008 | 0.0013163 | 0.053936 | -0.0035276 | 0.062717 | -0.015108 | -0.0015573 | -0.0011965 | 0.059954 | 0.017053 | 0.060231 | -66.7564 | 0.005985 | -66.746 | 56.2473 | 56.1059 | 56.2802 | -66.8375 | -66.7703 | 0.004938 | -66.8048 | 56.1482 | 56.2939 | 56.1506 | -67.0378 | -0.072682 | -0.062249 | 0.008406 | 0.018827 | 0.091509 | -0.20359 | -0.029298 | -0.27294 | -0.16133 | -0.005446 | -0.039951 | 0.23299 | -0.01562 | -0.15893 | 123.0121 | 122.8708 | 123.045 | 66.7708 | -123.147 | 122.913 | 123.0587 | 122.9154 | 66.7698 | -123.3473
714.7969 | 123.2208 | -66.7831 | 56.3095 | -0.010607 | -0.008 | 0.0015299 | 0.053936 | -0.003955 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.017267 | 0.060231 | -66.7518 | 0.010564 | -66.7506 | 56.2381 | 56.1197 | 56.2756 | -66.8513 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.303 | 56.1368 | -67.0332 | -0.068109 | -0.071405 | 0.031295 | 0.032559 | 0.10067 | -0.18985 | -0.033876 | -0.25005 | -0.16133 | 0.022021 | -0.017063 | 0.23299 | -0.006463 | -0.17267 | 123.0212 | 122.9028 | 123.0588 | 66.7937 | -123.1608 | 122.9313 | 123.0862 | 122.92 | 66.7835 | -123.3427
715.7969 | 123.2437 | -66.7648 | 56.2866 | 0.012286 | -0.0077862 | 0.0013163 | 0.054577 | -0.0035276 | 0.062717 | 0.0077831 | -0.0013437 | -0.00076913 | 0.059954 | 0.017267 | 0.060445 | -66.7473 | 0.005985 | -66.746 | 56.2473 | 56.1197 | 56.2756 | -66.8467 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.303 | 56.146 | -67.0332 | -0.08184 | -0.039361 | 0.017563 | 0.018827 | 0.10067 | -0.16696 | -0.010988 | -0.26836 | -0.13844 | 0.003711 | -0.035373 | 0.23299 | 0.016425 | -0.14062 | 123.0121 | 122.8845 | 123.0405 | 66.7708 | -123.1333 | 122.913 | 123.0679 | 122.9108 | 66.7652 | -123.3198
716.7969 | 123.1567 | -66.7877 | 56.2912 | -0.0029761 | -0.008 | 0.0013163 | 0.054149 | -0.0037412 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.017053 | 0.060231 | -66.7473 | 0.005985 | -66.7368 | 56.2518 | 56.1242 | 56.2711 | -66.8467 | -66.7611 | 0.004938 | -66.8002 | 56.1528 | 56.303 | 56.146 | -67.0424 | -0.058952 | -0.03936 | 0.040451 | 0.050872 | 0.10982 | -0.16696 | -0.020145 | -0.25463 | -0.13844 | 0.026599 | -0.012485 | 0.24215 | 0.011847 | -0.1452 | 123.0396 | 122.912 | 123.0588 | 66.7937 | -123.1379 | 122.9405 | 123.0908 | 122.9337 | 66.7927 | -123.3336
717.8438 | 123.3673 | -66.6962 | 56.3049 | 0.012286 | -0.0082136 | 0.0013163 | 0.054363 | -0.0035276 | 0.063144 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059313 | 0.017053 | 0.060445 | -66.7518 | 0.005985 | -66.7506 | 56.2381 | 56.1242 | 56.2711 | -66.8375 | -66.7703 | -0.00422 | -66.8002 | 56.1436 | 56.303 | 56.1414 | -67.0378 | -0.14135 | -0.066828 | -0.05568 | -0.054416 | 0.086931 | -0.1807 | -0.033878 | -0.34161 | -0.16133 | -0.074111 | -0.10404 | 0.23757 | -0.001886 | -0.16351 | 122.9343 | 122.8204 | 122.9672 | 66.7022 | -123.1424 | 122.8398 | 122.9992 | 122.8376 | 66.6919 | -123.3427
718.7969 | 123.2391 | -66.7877 | 56.2592 | 0.0046549 | -0.0077862 | 0.0011025 | 0.054577 | -0.0035276 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.017267 | 0.060445 | -66.761 | 0.005985 | -66.7506 | 56.2335 | 56.1197 | 56.2665 | -66.8421 | -66.7657 | 0.000359 | -66.7865 | 56.1482 | 56.3076 | 56.146 | -67.0378 | -0.054373 | -0.02563 | 0.026716 | 0.037137 | 0.09151 | -0.1395 | 0.007321 | -0.25005 | -0.11097 | 0.022021 | 0.001251 | 0.25131 | 0.048469 | -0.11316 | 123.0212 | 122.9074 | 123.0542 | 66.7937 | -123.1012 | 122.9359 | 123.0953 | 122.9337 | 66.7881 | -123.2969
719.7969 | 123.1705 | -66.7511 | 56.3187 | 0.0046549 | -0.0077862 | 0.0015299 | 0.054363 | -0.0035276 | 0.062717 | -0.0074779 | -0.0015573 | -0.00055553 | 0.05974 | 0.017481 | 0.060231 | -66.7518 | 0.010564 | -66.746 | 56.2427 | 56.1197 | 56.2711 | -66.8558 | -66.7657 | 0.000359 | -66.791 | 56.1482 | 56.303 | 56.1506 | -67.0332 | -0.10473 | -0.075983 | -0.000748 | 0.005094 | 0.10983 | -0.19901 | -0.047611 | -0.2821 | -0.17048 | -0.0146 | -0.039948 | 0.24215 | -0.015619 | -0.16809 | 122.9938 | 122.8708 | 123.0222 | 66.7617 | -123.1745 | 122.8993 | 123.0541 | 122.9017 | 66.7515 | -123.3519
720.8438 | 123.2117 | -66.7603 | 56.3324 | 0.012286 | -0.0082136 | 0.0013163 | 0.054149 | -0.0037412 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.05974 | 0.017481 | 0.060445 | -66.761 | 0.010564 | -66.746 | 56.2427 | 56.1197 | 56.2756 | -66.8513 | -66.7611 | 0.004938 | -66.7956 | 56.1482 | 56.303 | 56.1414 | -67.0424 | -0.090997 | -0.089715 | -0.00075 | 0.014249 | 0.10525 | -0.21274 | -0.056764 | -0.2821 | -0.18422 | -0.000867 | -0.035372 | 0.24673 | -0.029351 | -0.19098 | 123.0029 | 122.8799 | 123.0359 | 66.7708 | -123.1836 | 122.9084 | 123.0633 | 122.9017 | 66.7652 | -123.3748
721.7969 | 123.1659 | -66.7511 | 56.3004 | -0.010607 | -0.008 | 0.0013163 | 0.054149 | -0.0035276 | 0.063144 | 0.015414 | -0.0011301 | -0.0011965 | 0.059313 | 0.017267 | 0.060231 | -66.761 | 0.010564 | -66.7414 | 56.2473 | 56.1151 | 56.2665 | -66.8513 | -66.7657 | 0.000359 | -66.8002 | 56.1528 | 56.3076 | 56.1277 | -67.0378 | -0.10015 | -0.053094 | -0.009905 | 0.009672 | 0.10982 | -0.18527 | -0.033878 | -0.28668 | -0.14759 | -0.0146 | -0.049106 | 0.23757 | 0.00727 | -0.17267 | 122.9984 | 122.8662 | 123.0176 | 66.7617 | -123.1516 | 122.9039 | 123.0587 | 122.8788 | 66.7515 | -123.3381
722.7969 | 123.2895 | -66.7374 | 56.2408 | -0.0029761 | -0.0082136 | 0.0015299 | 0.054363 | -0.003314 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.05974 | 0.017053 | 0.060017 | -66.7518 | 0.005985 | -66.746 | 56.2473 | 56.1151 | 56.2711 | -66.8467 | -66.7611 | 0.000359 | -66.8002 | 56.1436 | 56.3076 | 56.1506 | -67.0378 | -0.10931 | 0.006415 | -0.014481 | -0.008639 | 0.10067 | -0.12577 | 0.030209 | -0.30041 | -0.097242 | -0.023755 | -0.062839 | 0.23757 | 0.066779 | -0.09027 | 122.9846 | 122.8524 | 123.0084 | 66.7434 | -123.0875 | 122.881 | 123.045 | 122.8879 | 66.7377 | -123.2786
723.7969 | 123.1384 | -66.7694 | 56.3187 | -0.0029761 | -0.008 | 0.00088894 | 0.054149 | -0.0037412 | 0.06293 | 0.0077831 | -0.0015573 | -0.00098273 | 0.05974 | 0.017267 | 0.060231 | -66.7518 | 0.005985 | -66.7414 | 56.2427 | 56.1105 | 56.2665 | -66.8467 | -66.7657 | 0.000359 | -66.8002 | 56.1482 | 56.3076 | 56.1368 | -67.0378 | -0.077263 | -0.075983 | 0.017562 | 0.027982 | 0.10524 | -0.20817 | -0.052189 | -0.26837 | -0.17048 | 0.00371 | -0.030796 | 0.23757 | -0.011041 | -0.18183 | 123.0121 | 122.8799 | 123.0359 | 66.7754 | -123.1653 | 122.9176 | 123.077 | 122.9062 | 66.7698 | -123.3564
724.7969 | 123.3032 | -66.7145 | 56.2546 | -0.0029761 | -0.008 | 0.0011025 | 0.054149 | -0.0037412 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.017267 | 0.060231 | -66.7564 | 0.010564 | -66.7414 | 56.2427 | 56.1242 | 56.2665 | -66.8421 | -66.7657 | 0.004938 | -66.8002 | 56.1528 | 56.303 | 56.146 | -67.0378 | -0.12762 | -0.011896 | -0.041948 | -0.026949 | 0.10067 | -0.13034 | 0.011898 | -0.3233 | -0.10182 | -0.051221 | -0.085727 | 0.23757 | 0.048468 | -0.10858 | 122.9572 | 122.8387 | 122.981 | 66.725 | -123.0967 | 122.8672 | 123.0175 | 122.8605 | 66.7194 | -123.2924
725.8438 | 123.2208 | -66.7511 | 56.337 | 0.0046549 | -0.0082136 | 0.0013163 | 0.054149 | -0.0041686 | 0.06293 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.017267 | 0.060445 | -66.761 | 0.010564 | -66.7414 | 56.2381 | 56.1242 | 56.2756 | -66.8513 | -66.7749 | 0.000359 | -66.7956 | 56.1482 | 56.3122 | 56.1552 | -67.0332 | -0.10015 | -0.098871 | -0.009905 | 0.009672 | 0.10982 | -0.21274 | -0.061342 | -0.2821 | -0.18879 | -0.023758 | -0.044527 | 0.23757 | -0.024772 | -0.18182 | 122.9892 | 122.8753 | 123.0267 | 66.7617 | -123.1882 | 122.8993 | 123.0633 | 122.9063 | 66.7515 | -123.3702
726.7969 | 123.2895 | -66.7511 | 56.2592 | -0.010607 | -0.0077862 | 0.0015299 | 0.054363 | -0.003955 | 0.06293 | 0.0077831 | -0.0015573 | -0.00098273 | 0.059527 | 0.017481 | 0.060231 | -66.7518 | 0.001407 | -66.7414 | 56.2427 | 56.1197 | 56.2756 | -66.8467 | -66.7611 | -0.00422 | -66.7956 | 56.1436 | 56.2985 | 56.1231 | -67.0286 | -0.095573 | -0.016473 | -0.000748 | 0.009672 | 0.10524 | -0.1395 | 0.016478 | -0.27752 | -0.11555 | -0.010022 | -0.044527 | 0.23299 | 0.039312 | -0.13605 | 122.9938 | 122.8708 | 123.0267 | 66.7525 | -123.1058 | 122.8947 | 123.0496 | 122.8742 | 66.7469 | -123.2878
727.7969 | 123.1979 | -66.7694 | 56.2912 | -0.0029761 | -0.008 | 0.0011025 | 0.054363 | -0.0037412 | 0.06293 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.017267 | 0.060231 | -66.7564 | 0.010564 | -66.7368 | 56.2381 | 56.1151 | 56.2756 | -66.8467 | -66.7703 | 0.000359 | -66.8002 | 56.1482 | 56.2985 | 56.1368 | -67.0424 | -0.077263 | -0.053095 | 0.012983 | 0.032561 | 0.10982 | -0.17612 | -0.015566 | -0.27294 | -0.14302 | -0.000869 | -0.030796 | 0.24215 | 0.007268 | -0.15436 | 123.0075 | 122.8845 | 123.045 | 66.78 | -123.1379 | 122.9176 | 123.0679 | 122.9062 | 66.7698 | -123.3336
728.7969 | 123.2895 | -66.7145 | 56.2775 | -0.0029761 | -0.0082136 | 0.0011025 | 0.054363 | -0.0035276 | 0.063144 | 0.00015261 | -0.0011301 | -0.00076913 | 0.05974 | 0.017267 | 0.060017 | -66.7564 | 0.005985 | -66.7414 | 56.2381 | 56.1197 | 56.2756 | -66.8421 | -66.7703 | 0.000359 | -66.7956 | 56.1482 | 56.3076 | 56.1323 | -67.0378 | -0.12762 | -0.039362 | -0.041948 | -0.026949 | 0.10067 | -0.15781 | -0.001833 | -0.3233 | -0.12928 | -0.0558 | -0.081148 | 0.24215 | 0.030158 | -0.14521 | 122.9526 | 122.8341 | 122.9901 | 66.7205 | -123.1196 | 122.8627 | 123.0221 | 122.8467 | 66.7148 | -123.3152
729.7969 | 123.2941 | -66.7465 | 56.2546 | 0.0046549 | -0.008 | 0.0015299 | 0.054577 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059954 | 0.017267 | 0.060231 | -66.7564 | 0.005985 | -66.7368 | 56.2473 | 56.1242 | 56.2711 | -66.8467 | -66.7657 | 0.000359 | -66.791 | 56.1528 | 56.3076 | 56.1414 | -67.0378 | -0.10015 | -0.007318 | -0.009905 | 0.009673 | 0.10982 | -0.13034 | 0.016476 | -0.29125 | -0.10182 | -0.019178 | -0.044526 | 0.24673 | 0.053046 | -0.11316 | 122.9938 | 122.8708 | 123.0176 | 66.7525 | -123.1012 | 122.8993 | 123.0541 | 122.8879 | 66.7469 | -123.2924
730.7969 | 123.2437 | -66.7557 | 56.2729 | -0.0029761 | -0.0082136 | 0.0011025 | 0.054791 | -0.0037412 | 0.063358 | -0.0074779 | -0.0015573 | -0.0014101 | 0.059954 | 0.017053 | 0.059804 | -66.761 | 0.005985 | -66.7368 | 56.2427 | 56.1151 | 56.2756 | -66.8513 | -66.7657 | 0.004938 | -66.8002 | 56.1436 | 56.2985 | 56.1323 | -67.0378 | -0.095575 | -0.030206 | -0.005328 | 0.018828 | 0.1144 | -0.15781 | 0.002745 | -0.2821 | -0.12929 | -0.010023 | -0.044529 | 0.23757 | 0.025579 | -0.14063 | 122.9984 | 122.8708 | 123.0313 | 66.7617 | -123.1241 | 122.8993 | 123.0541 | 122.8879 | 66.7606 | -123.3107
731.8438 | 123.23 | -66.7191 | 56.3416 | 0.012286 | -0.008 | 0.0011025 | 0.054577 | -0.003955 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.017694 | 0.060017 | -66.7564 | 0.005985 | -66.746 | 56.2518 | 56.1151 | 56.2711 | -66.8375 | -66.7657 | 0.000359 | -66.8002 | 56.1482 | 56.2985 | 56.1597 | -67.0378 | -0.11846 | -0.089714 | -0.037371 | -0.02695 | 0.091509 | -0.22647 | -0.070499 | -0.31872 | -0.19337 | -0.046644 | -0.08115 | 0.23757 | -0.043086 | -0.18182 | 122.9709 | 122.8341 | 122.9901 | 66.725 | -123.1791 | 122.8672 | 123.0175 | 122.8788 | 66.7194 | -123.3793
732.7969 | 123.2391 | -66.7328 | 56.3187 | 0.0046549 | -0.0077862 | 0.0013163 | 0.054577 | -0.0035276 | 0.062717 | 0.015414 | -0.0015573 | -0.00098273 | 0.059527 | 0.017267 | 0.060017 | -66.761 | 0.005985 | -66.746 | 56.2427 | 56.1197 | 56.2802 | -66.8375 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.303 | 56.1368 | -67.0424 | -0.10473 | -0.075983 | -0.028216 | -0.013217 | 0.091509 | -0.19901 | -0.038454 | -0.30957 | -0.17048 | -0.028333 | -0.067417 | 0.24215 | -0.015619 | -0.18183 | 122.9755 | 122.8524 | 123.013 | 66.7388 | -123.1562 | 122.881 | 123.0358 | 122.8696 | 66.7331 | -123.361
733.7969 | 123.2483 | -66.7419 | 56.25 | -0.010607 | -0.0082136 | 0.0013163 | 0.054363 | -0.0035276 | 0.06293 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059313 | 0.017267 | 0.059804 | -66.7564 | 0.005985 | -66.7368 | 56.2381 | 56.1151 | 56.2802 | -66.8421 | -66.7749 | -0.00422 | -66.7956 | 56.1482 | 56.2985 | 56.146 | -67.0424 | -0.10015 | -0.011896 | -0.014483 | 0.005095 | 0.10525 | -0.13492 | 0.030211 | -0.30041 | -0.10182 | -0.032914 | -0.053683 | 0.24673 | 0.048467 | -0.104 | 122.98 | 122.857 | 123.0222 | 66.7479 | -123.0921 | 122.8901 | 123.0404 | 122.8879 | 66.7377 | -123.2924
734.7969 | 123.2666 | -66.7603 | 56.3049 | 0.0046549 | -0.0082136 | 0.0011025 | 0.054149 | -0.0037412 | 0.063358 | 0.0077831 | -0.00091653 | -0.00098273 | 0.05974 | 0.017267 | 0.060231 | -66.7518 | 0.010564 | -66.746 | 56.2381 | 56.1242 | 56.2802 | -66.8467 | -66.7703 | -0.008798 | -66.8048 | 56.1528 | 56.3076 | 56.1368 | -67.0286 | -0.086418 | -0.066828 | 0.008407 | 0.014249 | 0.10067 | -0.1807 | -0.024721 | -0.26836 | -0.15217 | -0.010024 | -0.044529 | 0.22383 | 0.002692 | -0.16809 | 122.9984 | 122.8845 | 123.0405 | 66.7708 | -123.1516 | 122.913 | 123.0679 | 122.8971 | 66.7515 | -123.3335
735.7969 | 123.2712 | -66.7236 | 56.2637 | -0.0029761 | -0.0077862 | 0.0011025 | 0.054791 | -0.0035276 | 0.063144 | 0.0077831 | -0.0013437 | -0.00076913 | 0.05974 | 0.017694 | 0.060231 | -66.7564 | 0.005985 | -66.746 | 56.2473 | 56.1059 | 56.2711 | -66.8421 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.3076 | 56.1414 | -67.0424 | -0.11846 | -0.016473 | -0.032793 | -0.022372 | 0.096088 | -0.15781 | 0.007321 | -0.31872 | -0.11555 | -0.037488 | -0.076572 | 0.24215 | 0.043891 | -0.12232 | 122.9709 | 122.8296 | 122.9947 | 66.7296 | -123.1058 | 122.8718 | 123.0313 | 122.8651 | 66.724 | -123.3061
736.8438 | 123.1613 | -66.7786 | 56.3049 | 0.0046549 | -0.0084272 | 0.0011025 | 0.054363 | -0.003955 | 0.063144 | 0.00015261 | -0.0013437 | -0.00076913 | 0.05974 | 0.017481 | 0.060231 | -66.7473 | 0.001407 | -66.7414 | 56.2427 | 56.1105 | 56.2711 | -66.8375 | -66.7657 | 0.000359 | -66.8002 | 56.1528 | 56.303 | 56.1506 | -67.0378 | -0.05895 | -0.06225 | 0.031295 | 0.037137 | 0.096087 | -0.19443 | -0.033878 | -0.25921 | -0.15217 | 0.012865 | -0.021641 | 0.23757 | -0.001886 | -0.15436 | 123.0212 | 122.8891 | 123.0496 | 66.78 | -123.1424 | 122.9313 | 123.0816 | 122.9291 | 66.7789 | -123.3427
737.7969 | 123.2574 | -66.7511 | 56.282 | -0.0029761 | -0.0084272 | 0.0011025 | 0.054577 | -0.003314 | 0.06293 | 0.00015261 | -0.0015573 | -0.0014101 | 0.05974 | 0.017481 | 0.059804 | -66.7564 | 0.005985 | -66.7368 | 56.2335 | 56.1151 | 56.2711 | -66.8467 | -66.7657 | -0.00422 | -66.8002 | 56.1528 | 56.3076 | 56.1323 | -67.0332 | -0.095573 | -0.048518 | -0.005327 | 0.014251 | 0.10982 | -0.16696 | -0.010989 | -0.2821 | -0.12928 | -0.0146 | -0.049106 | 0.23299 | 0.025581 | -0.14978 | 122.9846 | 122.8662 | 123.0222 | 66.7571 | -123.1287 | 122.9039 | 123.0587 | 122.8834 | 66.7469 | -123.3152
738.7969 | 123.2941 | -66.7328 | 56.2958 | -0.0029761 | -0.0082136 | 0.00088894 | 0.055004 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.05974 | 0.017267 | 0.060017 | -66.7518 | 0.001407 | -66.746 | 56.2427 | 56.1288 | 56.2711 | -66.8375 | -66.7657 | 0.004938 | -66.791 | 56.1528 | 56.303 | 56.1368 | -67.0378 | -0.10473 | -0.053094 | -0.019059 | -0.013217 | 0.091509 | -0.16696 | -0.024722 | -0.30499 | -0.14302 | -0.032911 | -0.058259 | 0.24673 | 0.00727 | -0.15894 | 122.9755 | 122.8616 | 123.0038 | 66.7342 | -123.1333 | 122.8855 | 123.0358 | 122.8696 | 66.7377 | -123.3336
739.7969 | 123.2849 | -66.7236 | 56.3187 | 0.0046549 | -0.0084272 | 0.0011025 | 0.054363 | -0.0035276 | 0.063144 | 0.0077831 | -0.0013437 | -0.00098273 | 0.05974 | 0.017694 | 0.060231 | -66.7564 | 0.005985 | -66.746 | 56.2473 | 56.1288 | 56.2711 | -66.8467 | -66.7611 | 0.000359 | -66.7956 | 56.139 | 56.2939 | 56.1414 | -67.0424 | -0.12304 | -0.071405 | -0.032793 | -0.022372 | 0.10067 | -0.18985 | -0.047611 | -0.31872 | -0.17964 | -0.037488 | -0.071993 | 0.24673 | -0.024776 | -0.17725 | 122.9709 | 122.8524 | 122.9947 | 66.7296 | -123.1653 | 122.8627 | 123.0175 | 122.8651 | 66.724 | -123.361
740.8594 | 123.1934 | -66.7419 | 56.3324 | -0.0029761 | -0.008641 | 0.00088894 | 0.054363 | -0.0037412 | 0.063144 | -0.0074779 | -0.0015573 | -0.00098273 | 0.05974 | 0.017267 | 0.060017 | -66.7564 | 0.005985 | -66.7506 | 56.2518 | 56.1151 | 56.2802 | -66.8467 | -66.7657 | 0.000359 | -66.8002 | 56.1436 | 56.3076 | 56.1368 | -67.0378 | -0.10473 | -0.080558 | -0.014483 | -0.00864 | 0.096089 | -0.21732 | -0.052186 | -0.29583 | -0.18879 | -0.023756 | -0.058262 | 0.23757 | -0.024773 | -0.19556 | 122.9938 | 122.857 | 123.0222 | 66.7479 | -123.1791 | 122.8855 | 123.0496 | 122.8788 | 66.7423 | -123.3702
741.7969 | 123.2346 | -66.7511 | 56.2775 | -0.0029761 | -0.008641 | 0.0013163 | 0.054363 | -0.003955 | 0.063144 | 0.0077831 | -0.0011301 | -0.00076913 | 0.05974 | 0.018122 | 0.059804 | -66.7473 | 0.005985 | -66.7414 | 56.2427 | 56.1059 | 56.2756 | -66.8513 | -66.7703 | 0.000359 | -66.8002 | 56.1528 | 56.303 | 56.146 | -67.0332 | -0.10015 | -0.034784 | 0.00383 | 0.009672 | 0.10982 | -0.17154 | -0.001833 | -0.2821 | -0.12471 | -0.019179 | -0.049106 | 0.23299 | 0.02558 | -0.13147 | 122.9938 | 122.857 | 123.0267 | 66.7571 | -123.1287 | 122.9039 | 123.0541 | 122.8971 | 66.7515 | -123.3107
742.7969 | 123.317 | -66.6779 | 56.3049 | 0.012286 | -0.0082136 | 0.0011025 | 0.054363 | -0.0037412 | 0.06293 | 0.015414 | -0.0011301 | -0.0011965 | 0.059527 | 0.017267 | 0.060231 | -66.7518 | 0.010564 | -66.7506 | 56.2381 | 56.1013 | 56.2802 | -66.8421 | -66.7611 | -0.008798 | -66.8002 | 56.1482 | 56.3076 | 56.146 | -67.0424 | -0.16424 | -0.066828 | -0.073991 | -0.072727 | 0.09151 | -0.20359 | -0.024721 | -0.3645 | -0.15675 | -0.083265 | -0.12235 | 0.24215 | 0.002692 | -0.15894 | 122.916 | 122.7792 | 122.9581 | 66.6884 | -123.147 | 122.826 | 122.9855 | 122.8239 | 66.6691 | -123.3473
743.8438 | 123.2071 | -66.7557 | 56.2912 | -0.010607 | -0.0088546 | 0.0013163 | 0.054149 | -0.0037412 | 0.063144 | 0.00015261 | -0.0017711 | -0.0011965 | 0.05974 | 0.017267 | 0.060017 | -66.7473 | 0.005985 | -66.746 | 56.2427 | 56.1242 | 56.2711 | -66.8467 | -66.7657 | 0.000359 | -66.7956 | 56.1482 | 56.3122 | 56.1323 | -67.0332 | -0.090996 | -0.048517 | 0.008407 | 0.009671 | 0.10067 | -0.16696 | -0.020145 | -0.27752 | -0.14302 | -0.010023 | -0.03995 | 0.23757 | 0.021004 | -0.15894 | 122.9984 | 122.8799 | 123.0267 | 66.7617 | -123.1379 | 122.9039 | 123.0679 | 122.8879 | 66.756 | -123.3244
744.7969 | 123.3078 | -66.6916 | 56.3004 | 0.0046549 | -0.0082136 | 0.0011025 | 0.054577 | -0.0037412 | 0.063358 | 0.00015261 | -0.0015573 | -0.0014101 | 0.05974 | 0.017481 | 0.060231 | -66.7564 | 0.005985 | -66.7368 | 56.2427 | 56.138 | 56.2756 | -66.8467 | -66.7611 | 0.000359 | -66.791 | 56.1482 | 56.3076 | 56.146 | -67.0378 | -0.15508 | -0.057672 | -0.064837 | -0.045259 | 0.10982 | -0.16238 | -0.024721 | -0.34619 | -0.15217 | -0.069532 | -0.099458 | 0.24673 | 0.00727 | -0.15436 | 122.9343 | 122.8296 | 122.9672 | 66.6976 | -123.147 | 122.8398 | 122.9992 | 122.8376 | 66.6919 | -123.3381
745.8438 | 123.2025 | -66.7603 | 56.3278 | -0.0029761 | -0.0082136 | 0.0015299 | 0.054149 | -0.0037412 | 0.06293 | -0.0074779 | -0.0013437 | -0.00098273 | 0.05974 | 0.017481 | 0.060231 | -66.7518 | 0.001407 | -66.746 | 56.2381 | 56.1242 | 56.2848 | -66.8375 | -66.7565 | 0.000359 | -66.791 | 56.1482 | 56.3076 | 56.1506 | -67.0378 | -0.07726 | -0.089716 | 0.008407 | 0.014249 | 0.091509 | -0.20358 | -0.04303 | -0.27752 | -0.17964 | 0.003712 | -0.030793 | 0.24673 | -0.020196 | -0.17724 | 122.9984 | 122.8845 | 123.045 | 66.7617 | -123.1653 | 122.9084 | 123.0679 | 122.9108 | 66.7606 | -123.3656
746.7969 | 123.2803 | -66.7236 | 56.3095 | 0.012286 | -0.008641 | 0.0013163 | 0.054577 | -0.003955 | 0.06293 | 0.0077831 | -0.0013437 | -0.00076913 | 0.059527 | 0.017481 | 0.060231 | -66.761 | 0.005985 | -66.7414 | 56.2427 | 56.1151 | 56.2802 | -66.8421 | -66.7657 | -0.00422 | -66.7956 | 56.1482 | 56.3076 | 56.1414 | -67.0378 | -0.11846 | -0.066827 | -0.037371 | -0.017794 | 0.10067 | -0.19443 | -0.029298 | -0.31414 | -0.16133 | -0.042066 | -0.071993 | 0.24215 | -0.001885 | -0.16809 | 122.9663 | 122.8387 | 123.0038 | 66.7296 | -123.1516 | 122.8718 | 123.0313 | 122.8651 | 66.7194 | -123.3473
747.7969 | 123.3124 | -66.7007 | 56.2683 | 0.019917 | -0.008641 | 0.0013163 | 0.054577 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059527 | 0.017908 | 0.060017 | -66.761 | -0.007751 | -66.746 | 56.2427 | 56.1151 | 56.2711 | -66.8467 | -66.7611 | -0.008798 | -66.8002 | 56.1573 | 56.303 | 56.1552 | -67.0286 | -0.14593 | -0.025629 | -0.060259 | -0.04526 | 0.10067 | -0.15323 | 0.002743 | -0.32787 | -0.11097 | -0.060376 | -0.09946 | 0.22841 | 0.034735 | -0.11316 | 122.9434 | 122.8158 | 122.9718 | 66.693 | -123.115 | 122.8581 | 123.0038 | 122.8559 | 66.6919 | -123.2969
748.7969 | 123.2758 | -66.7053 | 56.3416 | 0.012286 | -0.008641 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0011301 | -0.0014101 | 0.05974 | 0.017694 | 0.060445 | -66.7564 | 0.001407 | -66.7368 | 56.2427 | 56.1288 | 56.2756 | -66.8467 | -66.7611 | -0.00422 | -66.8002 | 56.1528 | 56.303 | 56.1506 | -67.0424 | -0.14135 | -0.098871 | -0.051104 | -0.031526 | 0.10982 | -0.21274 | -0.06592 | -0.33703 | -0.18879 | -0.055799 | -0.094883 | 0.24215 | -0.038507 | -0.19098 | 122.948 | 122.8341 | 122.981 | 66.7067 | -123.1882 | 122.8581 | 123.0084 | 122.8559 | 66.7011 | -123.3839
749.8438 | 123.1338 | -66.774 | 56.3049 | -0.0029761 | -0.0082136 | 0.0013163 | 0.054363 | -0.0037412 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059527 | 0.017481 | 0.060445 | -66.7564 | 0.001407 | -66.7368 | 56.2473 | 56.1334 | 56.2802 | -66.8467 | -66.7611 | 0.000359 | -66.7956 | 56.1482 | 56.3076 | 56.1552 | -67.0424 | -0.072685 | -0.057672 | 0.017561 | 0.037139 | 0.10982 | -0.17154 | -0.024721 | -0.26837 | -0.15675 | 0.012866 | -0.021639 | 0.24673 | 0.002692 | -0.14978 | 123.0212 | 122.9074 | 123.0542 | 66.7754 | -123.1516 | 122.9222 | 123.0816 | 122.9291 | 66.7743 | -123.3473
750.7969 | 123.1934 | -66.7603 | 56.337 | 0.012286 | -0.008641 | 0.00088894 | 0.054149 | -0.0037412 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059313 | 0.017481 | 0.060231 | -66.761 | -0.003172 | -66.7368 | 56.2427 | 56.138 | 56.2711 | -66.8513 | -66.7611 | -0.013377 | -66.7956 | 56.1482 | 56.303 | 56.1506 | -67.0424 | -0.090997 | -0.094293 | -0.00075 | 0.023406 | 0.1144 | -0.199 | -0.065921 | -0.2821 | -0.18879 | -0.000867 | -0.035372 | 0.24673 | -0.033929 | -0.1864 | 123.0029 | 122.8982 | 123.0313 | 66.7571 | -123.1882 | 122.9084 | 123.0633 | 122.9108 | 66.7469 | -123.3793
751.7969 | 123.3032 | -66.6916 | 56.2912 | 0.019917 | -0.008641 | 0.0015299 | 0.054363 | -0.0037412 | 0.06293 | 0.0077831 | -0.0015573 | -0.0014101 | 0.059527 | 0.017481 | 0.060445 | -66.7564 | 0.010564 | -66.7506 | 56.2381 | 56.1334 | 56.2711 | -66.8467 | -66.7611 | -0.00422 | -66.7956 | 56.1482 | 56.303 | 56.1506 | -67.0424 | -0.15508 | -0.053095 | -0.064837 | -0.058994 | 0.096089 | -0.1578 | -0.020145 | -0.35076 | -0.14302 | -0.069532 | -0.10404 | 0.24673 | 0.011847 | -0.14062 | 122.9297 | 122.825 | 122.9626 | 66.7022 | -123.1379 | 122.8398 | 122.9946 | 122.8422 | 66.6874 | -123.3336
752.7969 | 123.1796 | -66.7282 | 56.3461 | 0.0046549 | -0.0084272 | 0.0015299 | 0.054149 | -0.0037412 | 0.063144 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059527 | 0.017694 | 0.060017 | -66.7518 | 0.001407 | -66.746 | 56.2381 | 56.1151 | 56.2756 | -66.8421 | -66.7565 | -0.00422 | -66.791 | 56.1482 | 56.303 | 56.1552 | -67.0332 | -0.11388 | -0.10803 | -0.023637 | -0.017795 | 0.096088 | -0.23105 | -0.070497 | -0.30499 | -0.19795 | -0.028332 | -0.062837 | 0.24215 | -0.043084 | -0.19098 | 122.9663 | 122.8433 | 123.0038 | 66.7296 | -123.1882 | 122.8764 | 123.0313 | 122.8834 | 66.724 | -123.3793
753.7969 | 123.2529 | -66.7236 | 56.2912 | -0.0029761 | -0.0084272 | 0.00088894 | 0.054149 | -0.0041686 | 0.06293 | 0.015414 | -0.0013437 | -0.00076913 | 0.059527 | 0.017908 | 0.060231 | -66.7518 | -0.007751 | -66.746 | 56.2427 | 56.1197 | 56.2756 | -66.8467 | -66.7657 | -0.008798 | -66.8002 | 56.1482 | 56.3122 | 56.1552 | -67.0424 | -0.12304 | -0.048517 | -0.028214 | -0.022372 | 0.10067 | -0.17154 | -0.015566 | -0.31872 | -0.14302 | -0.042066 | -0.076572 | 0.24215 | 0.021004 | -0.13605 | 122.9663 | 122.8433 | 122.9993 | 66.7159 | -123.1379 | 122.8718 | 123.0358 | 122.8788 | 66.7148 | -123.3336
754.8438 | 123.1796 | -66.7648 | 56.2958 | -0.0029761 | -0.0088546 | 0.0011025 | 0.054363 | -0.003955 | 0.063144 | 0.00015261 | -0.0011301 | -0.00055553 | 0.059527 | 0.017908 | 0.059804 | -66.7564 | 0.001407 | -66.746 | 56.2427 | 56.1288 | 56.2756 | -66.8467 | -66.7611 | -0.00422 | -66.791 | 56.1436 | 56.3122 | 56.1368 | -67.0332 | -0.08184 | -0.053094 | 0.008406 | 0.018827 | 0.10067 | -0.16696 | -0.020143 | -0.26836 | -0.15217 | 0.003711 | -0.026215 | 0.24215 | 0.016427 | -0.15894 | 123.0075 | 122.8936 | 123.0405 | 66.7662 | -123.1424 | 122.9084 | 123.077 | 122.9017 | 66.7606 | -123.329
755.7969 | 123.262 | -66.7007 | 56.3095 | 0.019917 | -0.0084272 | 0.0011025 | 0.054363 | -0.003955 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.017694 | 0.060231 | -66.7564 | 0.005985 | -66.746 | 56.2427 | 56.1242 | 56.2711 | -66.8421 | -66.7703 | 0.000359 | -66.791 | 56.1528 | 56.3168 | 56.1506 | -67.0378 | -0.14135 | -0.066827 | -0.055681 | -0.04526 | 0.096088 | -0.18527 | -0.038455 | -0.33703 | -0.15675 | -0.069533 | -0.090302 | 0.24673 | 0.007273 | -0.15893 | 122.9434 | 122.825 | 122.9718 | 66.7067 | -123.1516 | 122.8535 | 123.0175 | 122.8513 | 66.7011 | -123.3473
756.7969 | 123.1476 | -66.7374 | 56.3599 | 0.0046549 | -0.0084272 | 0.0013163 | 0.054149 | -0.0035276 | 0.063144 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059954 | 0.018122 | 0.060017 | -66.7564 | 0.001407 | -66.7506 | 56.2473 | 56.1242 | 56.2756 | -66.8421 | -66.7611 | -0.00422 | -66.7956 | 56.1436 | 56.3122 | 56.146 | -67.0286 | -0.10473 | -0.1126 | -0.01906 | -0.013217 | 0.09151 | -0.23563 | -0.08423 | -0.29125 | -0.21626 | -0.023755 | -0.05826 | 0.23299 | -0.04766 | -0.21387 | 122.9846 | 122.8616 | 123.013 | 66.7388 | -123.202 | 122.881 | 123.0496 | 122.8834 | 66.7331 | -123.3885
757.7969 | 123.2391 | -66.7374 | 56.3049 | -0.0029761 | -0.0084272 | 0.0011025 | 0.054363 | -0.0041686 | 0.06293 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.017481 | 0.060017 | -66.7564 | 0.001407 | -66.7597 | 56.2427 | 56.1242 | 56.2802 | -66.8513 | -66.7657 | -0.008798 | -66.8048 | 56.1528 | 56.3076 | 56.1552 | -67.0424 | -0.11389 | -0.06225 | -0.01906 | -0.022374 | 0.091511 | -0.1807 | -0.024721 | -0.30499 | -0.15217 | -0.028333 | -0.067417 | 0.23757 | 0.002692 | -0.14978 | 122.98 | 122.8616 | 123.0176 | 66.7388 | -123.1562 | 122.8901 | 123.045 | 122.8925 | 66.7286 | -123.3473
758.7969 | 123.1567 | -66.7603 | 56.3553 | -0.0029761 | -0.008641 | 0.0013163 | 0.054363 | -0.0041686 | 0.06293 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059313 | 0.018122 | 0.060445 | -66.7518 | 0.001407 | -66.7368 | 56.2427 | 56.1242 | 56.2756 | -66.8467 | -66.7657 | -0.00422 | -66.7956 | 56.1528 | 56.303 | 56.1414 | -67.0424 | -0.086418 | -0.1126 | 0.008407 | 0.023406 | 0.10982 | -0.23105 | -0.079653 | -0.2821 | -0.20253 | -0.005445 | -0.035372 | 0.24673 | -0.05224 | -0.21387 | 123.0029 | 122.8845 | 123.0359 | 66.7617 | -123.202 | 122.913 | 123.0633 | 122.9017 | 66.756 | -123.3976
759.8438 | 123.2437 | -66.7328 | 56.2912 | -0.010607 | -0.0088546 | 0.0013163 | 0.054577 | -0.0037412 | 0.06293 | -0.0074779 | -0.0017711 | -0.0011965 | 0.058886 | 0.017694 | 0.060017 | -66.761 | -0.003172 | -66.7506 | 56.2335 | 56.1197 | 56.2756 | -66.8467 | -66.7611 | -0.00422 | -66.7956 | 56.1482 | 56.3076 | 56.1323 | -67.0515 | -0.11388 | -0.057674 | -0.028216 | -0.017795 | 0.096089 | -0.17154 | -0.015566 | -0.31872 | -0.14302 | -0.028333 | -0.062838 | 0.25588 | 0.016425 | -0.15894 | 122.9663 | 122.8524 | 123.0084 | 66.7296 | -123.1379 | 122.881 | 123.0404 | 122.865 | 66.7286 | -123.3427
760.7969 | 123.1979 | -66.7603 | 56.3232 | -0.010607 | -0.0084272 | 0.0015299 | 0.054363 | -0.0041686 | 0.062717 | -0.0074779 | -0.0015573 | -0.00098273 | 0.059527 | 0.017694 | 0.060017 | -66.7564 | 0.001407 | -66.746 | 56.2427 | 56.1242 | 56.2802 | -66.8467 | -66.7657 | 0.004938 | -66.7956 | 56.1619 | 56.3076 | 56.1414 | -67.0378 | -0.086418 | -0.08056 | 0.003828 | 0.014249 | 0.10067 | -0.199 | -0.043031 | -0.27752 | -0.16132 | -0.005445 | -0.035372 | 0.24215 | -0.015618 | -0.18182 | 123.0029 | 122.8845 | 123.0405 | 66.7617 | -123.1699 | 122.9222 | 123.0679 | 122.9017 | 66.7652 | -123.361
761.7969 | 123.1613 | -66.7831 | 56.3141 | 0.0046549 | -0.0084272 | 0.0011025 | 0.053936 | -0.003955 | 0.06293 | 0.0077831 | -0.0013437 | -0.0018375 | 0.05974 | 0.018122 | 0.060017 | -66.7473 | 0.001407 | -66.7414 | 56.2427 | 56.1288 | 56.2756 | -66.8513 | -66.7657 | -0.00422 | -66.7956 | 56.1436 | 56.303 | 56.1414 | -67.0424 | -0.068109 | -0.071405 | 0.035873 | 0.041715 | 0.10982 | -0.18527 | -0.038454 | -0.25921 | -0.17048 | 0.017443 | -0.012484 | 0.24673 | -0.011041 | -0.17267 | 123.0258 | 122.912 | 123.0588 | 66.7845 | -123.1653 | 122.9267 | 123.0862 | 122.9246 | 66.7789 | -123.3564
762.8438 | 123.2529 | -66.6962 | 56.282 | -0.0029761 | -0.0088546 | 0.0015299 | 0.054363 | -0.0037412 | 0.063144 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059313 | 0.017908 | 0.060231 | -66.7518 | -0.003172 | -66.746 | 56.2427 | 56.1242 | 56.2756 | -66.8558 | -66.7611 | -0.013377 | -66.7956 | 56.1482 | 56.3076 | 56.1506 | -67.0378 | -0.15966 | -0.039361 | -0.05568 | -0.049838 | 0.10983 | -0.15781 | -0.00641 | -0.34161 | -0.13386 | -0.064954 | -0.099459 | 0.24215 | 0.025581 | -0.13147 | 122.9388 | 122.8204 | 122.9718 | 66.693 | -123.1379 | 122.8443 | 123.0038 | 122.8467 | 66.6828 | -123.3198
763.7969 | 123.1796 | -66.7419 | 56.3507 | -0.0029761 | -0.0088546 | 0.0019573 | 0.054363 | -0.0037412 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.017908 | 0.060017 | -66.7518 | 0.001407 | -66.7323 | 56.2427 | 56.1288 | 56.2756 | -66.8421 | -66.7657 | -0.008798 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0378 | -0.10015 | -0.10803 | -0.009904 | 0.009673 | 0.10982 | -0.22189 | -0.075075 | -0.29583 | -0.19795 | -0.023756 | -0.049104 | 0.24673 | -0.038505 | -0.20471 | 122.9846 | 122.8708 | 123.0176 | 66.7434 | -123.1928 | 122.8947 | 123.0541 | 122.8879 | 66.7331 | -123.3885
764.7969 | 123.1979 | -66.7419 | 56.3141 | 0.012286 | -0.008641 | 0.0013163 | 0.053936 | -0.003955 | 0.06293 | 0.0077831 | -0.0017711 | -0.0011965 | 0.059954 | 0.017481 | 0.060017 | -66.7564 | 0.001407 | -66.7368 | 56.2518 | 56.1288 | 56.2848 | -66.8421 | -66.752 | 0.004938 | -66.791 | 56.1528 | 56.3076 | 56.1368 | -67.0378 | -0.10015 | -0.062248 | -0.014483 | 0.005095 | 0.10525 | -0.18527 | -0.029297 | -0.29583 | -0.16133 | -0.01002 | -0.049104 | 0.24673 | -0.006463 | -0.17725 | 122.9938 | 122.8708 | 123.0267 | 66.7434 | -123.1562 | 122.8947 | 123.0496 | 122.8788 | 66.7469 | -123.3519
765.8281 | 123.3398 | -66.7099 | 56.2637 | 0.012286 | -0.0090682 | 0.0017435 | 0.054363 | -0.0035276 | 0.062717 | -0.0074779 | -0.0011301 | -0.0011965 | 0.059527 | 0.018335 | 0.059804 | -66.7518 | -0.003172 | -66.7368 | 56.2473 | 56.1242 | 56.2756 | -66.8467 | -66.7565 | -0.00422 | -66.7865 | 56.1528 | 56.3076 | 56.1368 | -67.0286 | -0.13677 | -0.016473 | -0.041947 | -0.026948 | 0.10982 | -0.1395 | 0.0119 | -0.31872 | -0.11097 | -0.046642 | -0.076569 | 0.24215 | 0.043891 | -0.12689 | 122.9572 | 122.8341 | 122.9855 | 66.7067 | -123.1104 | 122.8627 | 123.0175 | 122.8467 | 66.7057 | -123.2923
766.7969 | 123.1888 | -66.7419 | 56.3004 | -0.010607 | -0.0088546 | 0.0017435 | 0.054149 | -0.0037412 | 0.062717 | 0.0077831 | -0.0015573 | -0.00098273 | 0.05974 | 0.017694 | 0.060231 | -66.7518 | 0.005985 | -66.7323 | 56.2427 | 56.1242 | 56.2756 | -66.8513 | -66.7565 | -0.00422 | -66.8002 | 56.1528 | 56.3122 | 56.1414 | -67.0378 | -0.10931 | -0.057672 | -0.009904 | 0.009673 | 0.11898 | -0.17612 | -0.024721 | -0.29583 | -0.14759 | -0.014599 | -0.058262 | 0.23757 | 0.011849 | -0.15894 | 122.9846 | 122.8662 | 123.0176 | 66.7479 | -123.1516 | 122.8947 | 123.0541 | 122.8834 | 66.7377 | -123.3381
767.7969 | 123.1842 | -66.7557 | 56.337 | -0.0029761 | -0.0088546 | 0.0015299 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.00055553 | 0.059313 | 0.018122 | 0.059804 | -66.7518 | 0.005985 | -66.7277 | 56.2473 | 56.1288 | 56.2848 | -66.8467 | -66.7565 | -0.00422 | -66.8048 | 56.1528 | 56.303 | 56.146 | -67.0332 | -0.090996 | -0.089715 | 0.003829 | 0.027984 | 0.11898 | -0.20816 | -0.052185 | -0.27752 | -0.18422 | -0.000866 | -0.049107 | 0.22841 | -0.033929 | -0.19098 | 123.0029 | 122.8845 | 123.0405 | 66.7617 | -123.1836 | 122.9084 | 123.0587 | 122.9017 | 66.7515 | -123.3702
768.7969 | 123.1979 | -66.7465 | 56.3049 | 0.0046549 | -0.0090682 | 0.0013163 | 0.054363 | -0.003955 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.017908 | 0.060017 | -66.7518 | 0.001407 | -66.7323 | 56.2518 | 56.1197 | 56.2802 | -66.8558 | -66.7565 | 0.000359 | -66.791 | 56.1482 | 56.3122 | 56.1506 | -67.0332 | -0.10931 | -0.053093 | -0.005326 | 0.014251 | 0.12356 | -0.18527 | -0.024721 | -0.28667 | -0.15675 | -0.010021 | -0.044526 | 0.24215 | 0.007271 | -0.15436 | 122.9984 | 122.8662 | 123.0267 | 66.7479 | -123.1608 | 122.8947 | 123.0587 | 122.8971 | 66.7469 | -123.3381
769.7969 | 123.1934 | -66.7328 | 56.3187 | 0.0046549 | -0.0088546 | 0.0011025 | 0.054149 | -0.0035276 | 0.062717 | 0.0077831 | -0.0011301 | -0.00076913 | 0.05974 | 0.018122 | 0.060231 | -66.7473 | -0.003172 | -66.7231 | 56.2427 | 56.1288 | 56.2802 | -66.8467 | -66.7611 | 0.000359 | -66.791 | 56.1482 | 56.3122 | 56.1506 | -67.0378 | -0.11388 | -0.075983 | -0.014481 | 0.009675 | 0.12356 | -0.18985 | -0.038454 | -0.30499 | -0.17048 | -0.028333 | -0.058259 | 0.24673 | -0.006462 | -0.16809 | 122.9755 | 122.8616 | 123.013 | 66.7296 | -123.1653 | 122.881 | 123.045 | 122.8834 | 66.7331 | -123.3564
770.8438 | 123.1842 | -66.7328 | 56.3278 | -0.010607 | -0.008641 | 0.0013163 | 0.053722 | -0.0035276 | 0.062503 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059313 | 0.017908 | 0.059804 | -66.7564 | -0.003172 | -66.7277 | 56.2473 | 56.1242 | 56.2756 | -66.8513 | -66.7565 | 0.000359 | -66.7956 | 56.1482 | 56.3168 | 56.146 | -67.0332 | -0.11846 | -0.08056 | -0.023638 | 0.005096 | 0.12356 | -0.20358 | -0.052187 | -0.30041 | -0.17964 | -0.023754 | -0.062838 | 0.23757 | -0.011038 | -0.18182 | 122.98 | 122.857 | 123.0084 | 66.7296 | -123.1791 | 122.881 | 123.0496 | 122.8788 | 66.7331 | -123.361
771.8281 | 123.1979 | -66.7236 | 56.3095 | 0.0046549 | -0.008641 | 0.0015299 | 0.053936 | -0.0037412 | 0.062717 | 0.015414 | -0.0015573 | -0.00076913 | 0.059527 | 0.017694 | 0.060231 | -66.7518 | -0.007751 | -66.7368 | 56.2564 | 56.1288 | 56.2802 | -66.8467 | -66.7565 | -0.00422 | -66.791 | 56.1482 | 56.3076 | 56.146 | -67.0424 | -0.12304 | -0.053092 | -0.028214 | -0.013215 | 0.10982 | -0.18069 | -0.029298 | -0.31872 | -0.16133 | -0.032909 | -0.067414 | 0.25131 | -0.001885 | -0.16351 | 122.9801 | 122.8524 | 123.0038 | 66.7159 | -123.1562 | 122.8718 | 123.0313 | 122.8696 | 66.7194 | -123.3519
772.8594 | 123.1796 | -66.7831 | 56.3141 | 0.0046549 | -0.0084272 | 0.0015299 | 0.053936 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059527 | 0.017694 | 0.060017 | -66.7518 | -0.003172 | -66.7323 | 56.2473 | 56.1288 | 56.2802 | -66.8421 | -66.7657 | 0.004938 | -66.791 | 56.1482 | 56.3122 | 56.1506 | -67.0378 | -0.058951 | -0.066827 | 0.031295 | 0.050872 | 0.10982 | -0.18527 | -0.033876 | -0.25463 | -0.16591 | 0.017443 | -0.007905 | 0.24673 | -0.001884 | -0.16351 | 123.0304 | 122.912 | 123.0634 | 66.78 | -123.1562 | 122.9313 | 123.0953 | 122.9337 | 66.7881 | -123.3519
773.7969 | 123.2117 | -66.7511 | 56.3141 | 0.019917 | -0.0088546 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0017711 | -0.0011965 | 0.059527 | 0.018122 | 0.060231 | -66.7518 | 0.005985 | -66.7368 | 56.2518 | 56.138 | 56.2756 | -66.8467 | -66.7657 | 0.000359 | -66.791 | 56.1573 | 56.3076 | 56.1368 | -67.0469 | -0.095573 | -0.062248 | -0.000748 | 0.014251 | 0.10982 | -0.17611 | -0.038454 | -0.29583 | -0.15675 | -0.0146 | -0.039948 | 0.25588 | -0.006463 | -0.17725 | 123.0029 | 122.8891 | 123.0267 | 66.7571 | -123.1608 | 122.9084 | 123.0587 | 122.8879 | 66.7515 | -123.361
774.8125 | 123.1476 | -66.7648 | 56.3095 | -0.010607 | -0.0088546 | 0.0013163 | 0.054149 | -0.0037412 | 0.062503 | -0.0074779 | -0.0013437 | -0.0011965 | 0.059313 | 0.017908 | 0.060231 | -66.7427 | 0.005985 | -66.7368 | 56.2518 | 56.1197 | 56.2802 | -66.8467 | -66.7565 | -0.008798 | -66.7865 | 56.1482 | 56.3076 | 56.1323 | -67.0378 | -0.08184 | -0.05767 | 0.022141 | 0.027984 | 0.10982 | -0.18985 | -0.029298 | -0.27294 | -0.16133 | 0.00829 | -0.021637 | 0.25131 | -0.001885 | -0.17725 | 123.0167 | 122.8845 | 123.045 | 66.7708 | -123.1562 | 122.913 | 123.0725 | 122.8971 | 66.756 | -123.3473
775.875 | 123.2162 | -66.7328 | 56.3232 | 0.0046549 | -0.0088546 | 0.0011025 | 0.054363 | -0.0035276 | 0.06293 | 0.0077831 | -0.0011301 | -0.0011965 | 0.059527 | 0.018122 | 0.060017 | -66.7518 | 0.001407 | -66.7368 | 56.2473 | 56.1242 | 56.2802 | -66.8467 | -66.7611 | -0.013377 | -66.791 | 56.1436 | 56.2985 | 56.1552 | -67.0469 | -0.11388 | -0.075982 | -0.019059 | -0.00406 | 0.10982 | -0.199 | -0.043031 | -0.31414 | -0.17964 | -0.028333 | -0.058259 | 0.25588 | -0.024775 | -0.16809 | 122.98 | 122.857 | 123.013 | 66.7342 | -123.1699 | 122.8764 | 123.0313 | 122.8879 | 66.7194 | -123.3702
776.7969 | 123.2254 | -66.7694 | 56.282 | -0.0029761 | -0.0090682 | 0.0011025 | 0.054363 | -0.0035276 | 0.062503 | -0.0074779 | -0.0015573 | -0.00076913 | 0.059099 | 0.018122 | 0.060017 | -66.7518 | 0.005985 | -66.7368 | 56.2473 | 56.1242 | 56.2802 | -66.8467 | -66.7611 | -0.00422 | -66.8002 | 56.1482 | 56.3076 | 56.1414 | -67.0378 | -0.077263 | -0.034783 | 0.017562 | 0.032561 | 0.10982 | -0.15781 | -0.001832 | -0.26837 | -0.13386 | 0.008288 | -0.030796 | 0.23757 | 0.025581 | -0.14062 | 123.0167 | 122.8936 | 123.0496 | 66.7754 | -123.1287 | 122.9176 | 123.077 | 122.9108 | 66.7652 | -123.3198
777.7969 | 123.1842 | -66.7465 | 56.3004 | -0.0029761 | -0.0090682 | 0.0011025 | 0.053936 | -0.0037412 | 0.062503 | -0.0074779 | -0.0013437 | -0.00098273 | 0.05974 | 0.018122 | 0.059804 | -66.7518 | 0.001407 | -66.7414 | 56.2473 | 56.1197 | 56.2802 | -66.8467 | -66.752 | 0.000359 | -66.791 | 56.1528 | 56.2985 | 56.1277 | -67.0378 | -0.10015 | -0.053094 | -0.005326 | 0.005094 | 0.10524 | -0.1807 | -0.020143 | -0.29125 | -0.14759 | -0.005442 | -0.044526 | 0.24673 | -0.001887 | -0.17267 | 122.9938 | 122.8662 | 123.0267 | 66.7479 | -123.147 | 122.8993 | 123.045 | 122.8742 | 66.7469 | -123.3381
778.7969 | 123.1476 | -66.774 | 56.3095 | 0.0046549 | -0.0088546 | 0.0015299 | 0.054363 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.00098273 | 0.059527 | 0.017908 | 0.05959 | -66.7564 | 0.005985 | -66.7414 | 56.2381 | 56.1105 | 56.2802 | -66.8421 | -66.7611 | 0.000359 | -66.8002 | 56.1482 | 56.303 | 56.146 | -67.0424 | -0.068106 | -0.071405 | 0.017561 | 0.03256 | 0.10067 | -0.19901 | -0.029298 | -0.26837 | -0.16133 | 0.012866 | -0.026218 | 0.24215 | -0.006463 | -0.16351 | 123.0121 | 122.8845 | 123.0542 | 66.78 | -123.1516 | 122.9222 | 123.077 | 122.92 | 66.7743 | -123.3519
779.7969 | 123.1796 | -66.7694 | 56.3141 | -0.0029761 | -0.0088546 | 0.0013163 | 0.054149 | -0.0041686 | 0.062503 | 0.0077831 | -0.0015573 | -0.00055553 | 0.059527 | 0.018335 | 0.060017 | -66.7564 | 0.001407 | -66.7368 | 56.2518 | 56.1334 | 56.2848 | -66.8375 | -66.7611 | 0.000359 | -66.8002 | 56.1436 | 56.2985 | 56.1506 | -67.0378 | -0.068105 | -0.062248 | 0.012983 | 0.032561 | 0.10067 | -0.18069 | -0.029297 | -0.26837 | -0.17048 | 0.008288 | -0.030796 | 0.23757 | -0.01562 | -0.16351 | 123.0212 | 122.9028 | 123.0542 | 66.7708 | -123.1516 | 122.913 | 123.0679 | 122.92 | 66.7698 | -123.3519
780.7969 | 123.2483 | -66.7465 | 56.2958 | 0.0046549 | -0.0088546 | 0.0011025 | 0.054149 | -0.003955 | 0.062717 | -0.0074779 | -0.0011301 | -0.00098273 | 0.059527 | 0.017908 | 0.05959 | -66.7518 | -0.003172 | -66.7368 | 56.2427 | 56.1334 | 56.2802 | -66.8467 | -66.7611 | -0.008798 | -66.7956 | 56.1482 | 56.3076 | 56.146 | -67.0469 | -0.10015 | -0.053094 | -0.005326 | 0.009673 | 0.10982 | -0.16238 | -0.015565 | -0.30041 | -0.14759 | -0.0146 | -0.049105 | 0.25131 | 0.011848 | -0.14978 | 122.9892 | 122.8799 | 123.0267 | 66.7433 | -123.1424 | 122.8947 | 123.0541 | 122.8925 | 66.7377 | -123.3427
781.8594 | 123.2071 | -66.7465 | 56.3049 | -0.0029761 | -0.0088546 | 0.0015299 | 0.053936 | -0.003955 | 0.062717 | 0.00015261 | -0.00091653 | -0.00076913 | 0.059527 | 0.018335 | 0.060017 | -66.7518 | 0.005985 | -66.7368 | 56.2473 | 56.1242 | 56.2711 | -66.8467 | -66.7611 | -0.00422 | -66.791 | 56.1528 | 56.3076 | 56.1414 | -67.0378 | -0.10015 | -0.057672 | -0.005326 | 0.009673 | 0.10982 | -0.1807 | -0.033878 | -0.29125 | -0.15217 | -0.0146 | -0.044526 | 0.24673 | 0.002692 | -0.16351 | 122.9938 | 122.8708 | 123.0176 | 66.7525 | -123.1516 | 122.8993 | 123.0541 | 122.8879 | 66.7423 | -123.3427
782.7969 | 123.2574 | -66.7557 | 56.2637 | -0.010607 | -0.008641 | 0.0015299 | 0.054149 | -0.0037412 | 0.062503 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059313 | 0.018335 | 0.060231 | -66.7473 | -0.003172 | -66.746 | 56.2381 | 56.1288 | 56.2711 | -66.8421 | -66.7565 | -0.008798 | -66.7956 | 56.1482 | 56.3076 | 56.1368 | -67.0378 | -0.086417 | -0.025629 | 0.008407 | 0.009671 | 0.096088 | -0.13492 | 0.007321 | -0.2821 | -0.11555 | -0.000866 | -0.03995 | 0.24215 | 0.043891 | -0.12689 | 122.9938 | 122.8845 | 123.0267 | 66.7525 | -123.1058 | 122.9039 | 123.0633 | 122.8925 | 66.7469 | -123.3015
783.7969 | 123.1705 | -66.7419 | 56.3049 | 0.012286 | -0.0088546 | 0.0015299 | 0.053936 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059527 | 0.018335 | 0.060231 | -66.761 | 0.001407 | -66.746 | 56.2381 | 56.1242 | 56.2894 | -66.8467 | -66.7657 | -0.00422 | -66.791 | 56.1528 | 56.2985 | 56.1506 | -67.0378 | -0.10473 | -0.066828 | -0.019061 | -0.004062 | 0.10067 | -0.1807 | -0.015563 | -0.29583 | -0.15217 | -0.023756 | -0.049104 | 0.24673 | -0.006465 | -0.15436 | 122.98 | 122.8662 | 123.0313 | 66.7434 | -123.1516 | 122.8947 | 123.0404 | 122.8925 | 66.7377 | -123.3427
784.8594 | 123.1934 | -66.7557 | 56.3049 | 0.0046549 | -0.0088546 | 0.0013163 | 0.054363 | -0.0041686 | 0.062717 | -0.0074779 | -0.0011301 | -0.00076913 | 0.05974 | 0.018122 | 0.059804 | -66.7473 | 0.005985 | -66.746 | 56.2518 | 56.1334 | 56.2802 | -66.8467 | -66.7611 | -0.00422 | -66.8002 | 56.1528 | 56.3076 | 56.1414 | -67.0424 | -0.090996 | -0.053093 | 0.008407 | 0.009671 | 0.10067 | -0.17154 | -0.024721 | -0.28668 | -0.15217 | -0.005445 | -0.044529 | 0.24215 | 0.002692 | -0.16351 | 123.0075 | 122.8891 | 123.0359 | 66.7617 | -123.1516 | 122.9084 | 123.0633 | 122.8971 | 66.7515 | -123.3473
785.7969 | 123.1613 | -66.7648 | 56.3049 | 0.0046549 | -0.0088546 | 0.0015299 | 0.053936 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059313 | 0.018122 | 0.059804 | -66.7564 | -0.003172 | -66.7506 | 56.2518 | 56.1105 | 56.2756 | -66.8467 | -66.7611 | -0.00422 | -66.8002 | 56.1482 | 56.303 | 56.1414 | -67.0424 | -0.08184 | -0.053093 | 0.008406 | 0.014249 | 0.096089 | -0.19443 | -0.029299 | -0.27752 | -0.15675 | 0.003711 | -0.035373 | 0.24215 | -0.001886 | -0.16351 | 123.0167 | 122.8753 | 123.0405 | 66.7617 | -123.1516 | 122.913 | 123.0679 | 122.9062 | 66.7606 | -123.3473
786.7969 | 123.2986 | -66.7191 | 56.2866 | -0.0029761 | -0.0088546 | 0.0011025 | 0.054363 | -0.0037412 | 0.062503 | -0.0074779 | -0.0017711 | -0.00098273 | 0.059099 | 0.018122 | 0.059804 | -66.7473 | 0.010564 | -66.746 | 56.2427 | 56.1197 | 56.2711 | -66.8467 | -66.7474 | -0.008798 | -66.7956 | 56.1528 | 56.3122 | 56.1506 | -67.0424 | -0.12762 | -0.043939 | -0.028214 | -0.02695 | 0.10067 | -0.16696 | -0.015567 | -0.3233 | -0.13386 | -0.02833 | -0.076571 | 0.24673 | 0.025582 | -0.13605 | 122.9617 | 122.8387 | 122.9901 | 66.7296 | -123.1333 | 122.8718 | 123.0313 | 122.8696 | 66.7103 | -123.329
787.7969 | 123.2391 | -66.7557 | 56.2729 | -0.0029761 | -0.0088546 | 0.0011025 | 0.054149 | -0.003955 | 0.062717 | -0.0074779 | -0.0011301 | -0.00076913 | 0.059313 | 0.018549 | 0.05959 | -66.7473 | 0.005985 | -66.7368 | 56.2427 | 56.1242 | 56.2802 | -66.8421 | -66.7611 | -0.008798 | -66.791 | 56.1482 | 56.3122 | 56.1552 | -67.0424 | -0.086417 | -0.030206 | 0.008407 | 0.018828 | 0.10525 | -0.14865 | 0.007323 | -0.28668 | -0.12471 | -0.005445 | -0.035371 | 0.25131 | 0.039315 | -0.11774 | 122.9984 | 122.8799 | 123.0359 | 66.7617 | -123.115 | 122.9039 | 123.0679 | 122.9108 | 66.7469 | -123.3152
788.8594 | 123.2025 | -66.7786 | 56.3141 | -0.010607 | -0.009282 | 0.0017435 | 0.054149 | -0.003955 | 0.06293 | 0.00015261 | -0.0011301 | -0.00076913 | 0.05974 | 0.018122 | 0.060017 | -66.7518 | -0.003172 | -66.7506 | 56.2381 | 56.1288 | 56.2756 | -66.8467 | -66.752 | -0.008798 | -66.7956 | 56.1482 | 56.3076 | 56.1414 | -67.0378 | -0.068108 | -0.075983 | 0.026717 | 0.027981 | 0.096089 | -0.18527 | -0.038454 | -0.25921 | -0.16591 | 0.026601 | -0.017062 | 0.24215 | -0.006463 | -0.17267 | 123.0167 | 122.9074 | 123.0542 | 66.7754 | -123.1608 | 122.9267 | 123.0862 | 122.92 | 66.7698 | -123.3519
789.7969 | 123.2483 | -66.7465 | 56.2866 | -0.010607 | -0.0088546 | 0.0013163 | 0.054149 | -0.003955 | 0.062289 | -0.0074779 | -0.0011301 | -0.00098273 | 0.059313 | 0.018335 | 0.060017 | -66.7564 | -0.007751 | -66.7368 | 56.2473 | 56.1288 | 56.2711 | -66.8375 | -66.7565 | -0.008798 | -66.7956 | 56.1528 | 56.303 | 56.1323 | -67.0424 | -0.090993 | -0.039361 | -0.009905 | 0.009673 | 0.10067 | -0.1578 | -0.015567 | -0.29583 | -0.13386 | -0.010021 | -0.049105 | 0.24673 | 0.016425 | -0.15436 | 122.9938 | 122.8753 | 123.0176 | 66.7388 | -123.1241 | 122.8993 | 123.0496 | 122.8788 | 66.7377 | -123.329
790.7969 | 123.2529 | -66.7282 | 56.2958 | -0.018238 | -0.0090682 | 0.0013163 | 0.054577 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059527 | 0.018335 | 0.059804 | -66.7518 | -0.003172 | -66.746 | 56.2473 | 56.1288 | 56.2802 | -66.8421 | -66.752 | -0.008798 | -66.7956 | 56.1573 | 56.3076 | 56.1368 | -67.0424 | -0.11388 | -0.048516 | -0.023637 | -0.017795 | 0.096088 | -0.16696 | -0.015565 | -0.31414 | -0.13844 | -0.023753 | -0.067416 | 0.24673 | 0.011848 | -0.15894 | 122.9755 | 122.857 | 123.0084 | 66.725 | -123.1379 | 122.8855 | 123.0358 | 122.865 | 66.7194 | -123.3381
791.7969 | 123.2758 | -66.7191 | 56.2592 | -0.0029761 | -0.0088546 | 0.0013163 | 0.054363 | -0.0041686 | 0.062289 | 0.00015261 | -0.0011301 | -0.0011965 | 0.059313 | 0.018335 | 0.060017 | -66.7473 | 0.001407 | -66.7277 | 56.2427 | 56.1151 | 56.2802 | -66.8513 | -66.7611 | -0.008798 | -66.7956 | 56.1436 | 56.303 | 56.1414 | -67.0378 | -0.1322 | -0.016473 | -0.028214 | -0.008637 | 0.12356 | -0.14408 | 0.021056 | -0.31872 | -0.11555 | -0.042066 | -0.076571 | 0.24215 | 0.043891 | -0.11774 | 122.9617 | 122.8341 | 122.9993 | 66.7205 | -123.1104 | 122.8627 | 123.0221 | 122.8605 | 66.7103 | -123.2969
792.7969 | 123.3078 | -66.7282 | 56.3004 | -0.010607 | -0.009282 | 0.0013163 | 0.054149 | -0.003955 | 0.062503 | 0.00015261 | -0.0015573 | -0.00055553 | 0.059099 | 0.018335 | 0.05959 | -66.7564 | -0.003172 | -66.7414 | 56.2427 | 56.1242 | 56.2848 | -66.8421 | -66.7657 | -0.013377 | -66.7865 | 56.1482 | 56.303 | 56.1414 | -67.0469 | -0.11388 | -0.057672 | -0.028216 | -0.013217 | 0.10067 | -0.17612 | -0.015564 | -0.31872 | -0.15217 | -0.037489 | -0.058259 | 0.26046 | 0.002692 | -0.15894 | 122.9709 | 122.8524 | 123.013 | 66.725 | -123.1424 | 122.8764 | 123.0313 | 122.8696 | 66.7148 | -123.3473
793.7969 | 123.2986 | -66.7282 | 56.2866 | -0.0029761 | -0.009282 | 0.0013163 | 0.054149 | -0.0035276 | 0.062289 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059527 | 0.017908 | 0.059804 | -66.7473 | -0.003172 | -66.746 | 56.2427 | 56.1151 | 56.2802 | -66.8375 | -66.7611 | -0.008798 | -66.8002 | 56.1528 | 56.303 | 56.146 | -67.0332 | -0.1093 | -0.043939 | -0.019059 | -0.017795 | 0.091509 | -0.17154 | -0.00641 | -0.30499 | -0.13386 | -0.032911 | -0.071995 | 0.23299 | 0.016425 | -0.14062 | 122.9709 | 122.8433 | 123.0084 | 66.725 | -123.1241 | 122.881 | 123.0313 | 122.8742 | 66.7194 | -123.3198
794.7969 | 123.2208 | -66.7328 | 56.3004 | -0.0029761 | -0.009282 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059313 | 0.018335 | 0.059804 | -66.7518 | -0.003172 | -66.7368 | 56.2381 | 56.1197 | 56.2802 | -66.8329 | -66.7565 | -0.013377 | -66.8002 | 56.1482 | 56.3214 | 56.146 | -67.0469 | -0.10015 | -0.06225 | -0.019059 | -0.00406 | 0.096087 | -0.1807 | -0.020143 | -0.31414 | -0.15217 | -0.023754 | -0.067417 | 0.24673 | 0.021006 | -0.15436 | 122.9709 | 122.8524 | 123.013 | 66.7296 | -123.1333 | 122.881 | 123.0541 | 122.8788 | 66.7194 | -123.3473
795.7969 | 123.2941 | -66.7374 | 56.3004 | -0.010607 | -0.009282 | 0.0013163 | 0.054363 | -0.003955 | 0.062503 | -0.0074779 | -0.0013437 | -0.00076913 | 0.05974 | 0.018549 | 0.05959 | -66.7518 | 0.001407 | -66.7414 | 56.2381 | 56.1242 | 56.2756 | -66.8467 | -66.7657 | -0.013377 | -66.791 | 56.1528 | 56.3122 | 56.1368 | -67.0378 | -0.10931 | -0.06225 | -0.014481 | -0.004061 | 0.10524 | -0.17612 | -0.024721 | -0.30041 | -0.14759 | -0.028333 | -0.053681 | 0.24673 | 0.011849 | -0.16351 | 122.9755 | 122.8616 | 123.013 | 66.7388 | -123.147 | 122.8901 | 123.0496 | 122.8742 | 66.724 | -123.3381
796.7969 | 123.262 | -66.7191 | 56.3049 | 0.0046549 | -0.0088546 | 0.00088894 | 0.054791 | -0.0037412 | 0.063144 | 0.015414 | -0.0013437 | -0.00098273 | 0.059527 | 0.018122 | 0.059804 | -66.7473 | 0.001407 | -66.7414 | 56.2427 | 56.1334 | 56.2802 | -66.8467 | -66.7565 | -0.013377 | -66.8002 | 56.1528 | 56.3122 | 56.1414 | -67.0424 | -0.12762 | -0.06225 | -0.028214 | -0.022372 | 0.10524 | -0.17154 | -0.024721 | -0.3233 | -0.15217 | -0.037487 | -0.08115 | 0.24215 | 0.007271 | -0.16351 | 122.9617 | 122.8525 | 122.9993 | 66.7205 | -123.1516 | 122.8718 | 123.0313 | 122.8605 | 66.7057 | -123.3473
797.7969 | 123.262 | -66.7191 | 56.2866 | -0.0029761 | -0.009282 | 0.0013163 | 0.054577 | -0.0041686 | 0.06293 | 0.0077831 | -0.0013437 | -0.00076913 | 0.059313 | 0.018335 | 0.060017 | -66.7518 | 0.001407 | -66.746 | 56.2473 | 56.1242 | 56.2756 | -66.8375 | -66.752 | -0.008798 | -66.8048 | 56.1528 | 56.303 | 56.1506 | -67.0332 | -0.11846 | -0.039361 | -0.032792 | -0.02695 | 0.091509 | -0.16238 | -0.010988 | -0.31414 | -0.13386 | -0.032908 | -0.085728 | 0.22841 | 0.016425 | -0.13605 | 122.9663 | 122.8433 | 122.9947 | 66.7205 | -123.1241 | 122.8718 | 123.0221 | 122.8696 | 66.7103 | -123.3198
798.8594 | 123.1613 | -66.7648 | 56.3232 | -0.0029761 | -0.009282 | 0.0013163 | 0.054149 | -0.003955 | 0.062289 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.018335 | 0.05959 | -66.7518 | 0.005985 | -66.7414 | 56.2427 | 56.1334 | 56.2802 | -66.8513 | -66.7565 | 0.000359 | -66.7956 | 56.1573 | 56.3122 | 56.146 | -67.0424 | -0.086419 | -0.08056 | 0.012985 | 0.023405 | 0.10982 | -0.18985 | -0.043031 | -0.27752 | -0.1659 | 0.00829 | -0.030794 | 0.24673 | -0.011039 | -0.17725 | 123.0075 | 122.8982 | 123.045 | 66.7708 | -123.1745 | 122.9222 | 123.077 | 122.9108 | 66.7652 | -123.3656
799.7969 | 123.2895 | -66.7007 | 56.2775 | -0.0029761 | -0.009282 | 0.0015299 | 0.054149 | -0.0037412 | 0.063144 | 0.015414 | -0.0013437 | -0.00076913 | 0.059527 | 0.018335 | 0.060017 | -66.7564 | 0.001407 | -66.746 | 56.2473 | 56.1334 | 56.2756 | -66.8558 | -66.7611 | -0.008798 | -66.7956 | 56.1482 | 56.3122 | 56.1552 | -67.0378 | -0.15508 | -0.030206 | -0.055681 | -0.04526 | 0.10983 | -0.14407 | -0.001833 | -0.33703 | -0.12928 | -0.060376 | -0.094881 | 0.24215 | 0.034737 | -0.12231 | 122.948 | 122.8341 | 122.9764 | 66.7022 | -123.1333 | 122.8489 | 123.0129 | 122.8559 | 66.6919 | -123.3152
800.7969 | 123.2529 | -66.7282 | 56.3416 | -0.010607 | -0.0094956 | 0.0011025 | 0.054363 | -0.0037412 | 0.063144 | 0.0077831 | -0.0013437 | -0.00098273 | 0.05974 | 0.018335 | 0.060017 | -66.7518 | -0.003172 | -66.7506 | 56.2381 | 56.1334 | 56.2802 | -66.8421 | -66.7611 | -0.008798 | -66.791 | 56.1528 | 56.2985 | 56.1552 | -67.0424 | -0.11388 | -0.10345 | -0.023637 | -0.022373 | 0.09151 | -0.20816 | -0.061342 | -0.31414 | -0.18879 | -0.032911 | -0.062837 | 0.25131 | -0.043086 | -0.1864 | 122.9663 | 122.8616 | 123.0084 | 66.725 | -123.1836 | 122.881 | 123.0267 | 122.8834 | 66.7194 | -123.3839
801.7969 | 123.2712 | -66.7282 | 56.2866 | -0.0029761 | -0.008641 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.05974 | 0.018549 | 0.059804 | -66.7427 | -0.003172 | -66.746 | 56.2473 | 56.1334 | 56.2848 | -66.8467 | -66.7611 | -0.013377 | -66.8048 | 56.1619 | 56.3122 | 56.1368 | -67.0424 | -0.11846 | -0.039361 | -0.014481 | -0.017795 | 0.10067 | -0.15323 | -0.001831 | -0.31414 | -0.1247 | -0.032911 | -0.076573 | 0.23757 | 0.025582 | -0.14978 | 122.9755 | 122.8616 | 123.013 | 66.725 | -123.1333 | 122.8901 | 123.0404 | 122.865 | 66.7148 | -123.329
802.8125 | 123.262 | -66.7511 | 56.2775 | -0.018238 | -0.009282 | 0.0015299 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059099 | 0.018763 | 0.059376 | -66.7564 | -0.003172 | -66.746 | 56.2427 | 56.1151 | 56.2848 | -66.8421 | -66.7565 | -0.013377 | -66.7956 | 56.1573 | 56.3122 | 56.1506 | -67.0424 | -0.090994 | -0.034784 | -0.005327 | 0.005094 | 0.096088 | -0.16239 | 0.007324 | -0.29125 | -0.12013 | -0.005443 | -0.044527 | 0.24673 | 0.034737 | -0.12689 | 122.9938 | 122.8662 | 123.0359 | 66.7479 | -123.1196 | 122.9084 | 123.0633 | 122.9017 | 66.7377 | -123.3198
803.8594 | 123.2574 | -66.7465 | 56.2866 | 0.0046549 | -0.0094956 | 0.0011025 | 0.054577 | -0.0037412 | 0.062717 | -0.0074779 | -0.0013437 | -0.0014101 | 0.059527 | 0.018122 | 0.060017 | -66.7518 | -0.003172 | -66.7597 | 56.2427 | 56.1197 | 56.2848 | -66.8467 | -66.7565 | -0.013377 | -66.8002 | 56.1482 | 56.3076 | 56.1323 | -67.0469 | -0.10015 | -0.043939 | -0.005326 | -0.013219 | 0.086932 | -0.16696 | -0.001831 | -0.30041 | -0.13844 | -0.010021 | -0.053684 | 0.24673 | 0.021003 | -0.15436 | 122.9892 | 122.8662 | 123.0313 | 66.7433 | -123.1333 | 122.8947 | 123.0541 | 122.8788 | 66.7331 | -123.3336
804.7969 | 123.2758 | -66.6916 | 56.2866 | 0.0046549 | -0.0097092 | 0.0011025 | 0.054363 | -0.0041686 | 0.062717 | 0.015414 | -0.0015573 | -0.0014101 | 0.059527 | 0.018549 | 0.059804 | -66.7473 | -0.003172 | -66.7552 | 56.2427 | 56.1288 | 56.2848 | -66.8329 | -66.7611 | -0.017956 | -66.791 | 56.1482 | 56.3076 | 56.1323 | -67.0378 | -0.14135 | -0.043939 | -0.05568 | -0.063572 | 0.077774 | -0.1578 | -0.001831 | -0.34619 | -0.13844 | -0.069532 | -0.099458 | 0.24673 | 0.021003 | -0.15436 | 122.9343 | 122.8204 | 122.9764 | 66.6884 | -123.1196 | 122.8398 | 122.9992 | 122.8238 | 66.6736 | -123.3244
805.7969 | 123.2071 | -66.7603 | 56.3416 | -0.0029761 | -0.009282 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.015414 | -0.0015573 | -0.00076913 | 0.059527 | 0.018549 | 0.05959 | -66.7518 | -0.003172 | -66.7506 | 56.2473 | 56.1242 | 56.2894 | -66.8467 | -66.7565 | -0.008798 | -66.7956 | 56.1573 | 56.303 | 56.146 | -67.0424 | -0.086418 | -0.094293 | 0.008407 | 0.009671 | 0.096089 | -0.21732 | -0.052184 | -0.2821 | -0.18421 | 0.003712 | -0.035372 | 0.24673 | -0.038507 | -0.19556 | 123.0075 | 122.8845 | 123.0496 | 66.7571 | -123.1882 | 122.9176 | 123.0633 | 122.9062 | 66.7515 | -123.3839
806.7969 | 123.3261 | -66.7099 | 56.2775 | 0.0046549 | -0.009923 | 0.0015299 | 0.054363 | -0.0037412 | 0.06293 | -0.0074779 | -0.0013437 | -0.00098273 | 0.05974 | 0.018549 | 0.05959 | -66.7473 | -0.007751 | -66.7552 | 56.2427 | 56.1334 | 56.2848 | -66.8421 | -66.7657 | -0.008798 | -66.7865 | 56.1482 | 56.3076 | 56.1414 | -67.0378 | -0.13219 | -0.034784 | -0.037369 | -0.045261 | 0.086932 | -0.14407 | 0.007324 | -0.32787 | -0.12928 | -0.055799 | -0.076569 | 0.25131 | 0.030158 | -0.13605 | 122.9526 | 122.8433 | 122.9947 | 66.7021 | -123.1196 | 122.8581 | 123.0175 | 122.8513 | 66.7011 | -123.3152
807.7969 | 123.2849 | -66.7099 | 56.2912 | -0.010607 | -0.0097092 | 0.0011025 | 0.054577 | -0.0041686 | 0.062717 | 0.0077831 | -0.0015573 | -0.00098273 | 0.05974 | 0.018549 | 0.059804 | -66.7518 | -0.007751 | -66.746 | 56.2381 | 56.1334 | 56.2848 | -66.8421 | -66.7565 | -0.017956 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0424 | -0.13219 | -0.053095 | -0.041947 | -0.036105 | 0.096088 | -0.1578 | -0.006409 | -0.33245 | -0.13844 | -0.046642 | -0.081147 | 0.25131 | 0.021004 | -0.1452 | 122.948 | 122.8433 | 122.9947 | 66.7021 | -123.1333 | 122.8627 | 123.0221 | 122.8559 | 66.6919 | -123.3336
808.8281 | 123.2574 | -66.7282 | 56.2637 | 0.0046549 | -0.009282 | 0.0013163 | 0.054363 | -0.0041686 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059313 | 0.018549 | 0.060017 | -66.7427 | -0.007751 | -66.7414 | 56.2381 | 56.1288 | 56.2802 | -66.8421 | -66.7611 | -0.013377 | -66.791 | 56.1436 | 56.3122 | 56.146 | -67.0424 | -0.11388 | -0.025629 | -0.014481 | -0.013217 | 0.10067 | -0.13492 | 0.016478 | -0.31414 | -0.12013 | -0.032911 | -0.062837 | 0.25131 | 0.04847 | -0.11774 | 122.9663 | 122.857 | 123.0084 | 66.7205 | -123.1058 | 122.8718 | 123.0404 | 122.8742 | 66.7148 | -123.3061
809.8281 | 123.2986 | -66.7099 | 56.2866 | 0.0046549 | -0.0094956 | 0.0011025 | 0.054577 | -0.0043822 | 0.06293 | 0.0077831 | -0.0011301 | -0.00098273 | 0.05974 | 0.018549 | 0.05959 | -66.7427 | -0.007751 | -66.746 | 56.2427 | 56.1242 | 56.2848 | -66.8467 | -66.7565 | -0.013377 | -66.791 | 56.1528 | 56.3076 | 56.146 | -67.0424 | -0.13677 | -0.043939 | -0.032791 | -0.036105 | 0.10067 | -0.16238 | -0.001831 | -0.33245 | -0.13386 | -0.046642 | -0.081147 | 0.25131 | 0.021003 | -0.14062 | 122.9526 | 122.8341 | 122.9947 | 66.7021 | -123.1333 | 122.8627 | 123.0175 | 122.8559 | 66.6965 | -123.329
810.8594 | 123.2666 | -66.7145 | 56.2683 | -0.0029761 | -0.0094956 | 0.0011025 | 0.054149 | -0.0035276 | 0.06293 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059313 | 0.018549 | 0.059804 | -66.7473 | -0.003172 | -66.746 | 56.2381 | 56.1197 | 56.2848 | -66.8467 | -66.7565 | -0.008798 | -66.7956 | 56.1528 | 56.3076 | 56.1414 | -67.0424 | -0.13219 | -0.030207 | -0.032791 | -0.031527 | 0.10067 | -0.14865 | 0.016479 | -0.32788 | -0.11555 | -0.042064 | -0.081148 | 0.24673 | 0.039313 | -0.12689 | 122.9526 | 122.8341 | 122.9993 | 66.7113 | -123.115 | 122.8672 | 123.0221 | 122.8559 | 66.7057 | -123.3107
811.7969 | 123.3124 | -66.7099 | 56.3278 | 0.0046549 | -0.009282 | 0.0013163 | 0.054363 | -0.0037412 | 0.062289 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059313 | 0.018549 | 0.059804 | -66.7427 | -0.012329 | -66.746 | 56.2381 | 56.1288 | 56.2802 | -66.8467 | -66.7611 | -0.013377 | -66.7956 | 56.1482 | 56.3122 | 56.1597 | -67.0378 | -0.13677 | -0.089716 | -0.032791 | -0.036105 | 0.10067 | -0.199 | -0.047609 | -0.32787 | -0.17964 | -0.051221 | -0.085726 | 0.24215 | -0.015617 | -0.16809 | 122.948 | 122.8387 | 122.9901 | 66.6976 | -123.1745 | 122.8581 | 123.0221 | 122.8696 | 66.6965 | -123.3656
812.8594 | 123.2712 | -66.7465 | 56.2775 | -0.0029761 | -0.009282 | 0.0011025 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059099 | 0.018763 | 0.05959 | -66.7518 | -0.003172 | -66.7414 | 56.2427 | 56.1334 | 56.2802 | -66.8513 | -66.7565 | -0.013377 | -66.7956 | 56.1482 | 56.303 | 56.1552 | -67.0424 | -0.10473 | -0.034784 | -0.005326 | 0.005094 | 0.10982 | -0.14407 | 0.002745 | -0.29583 | -0.12928 | -0.010021 | -0.049105 | 0.24673 | 0.02558 | -0.12231 | 122.9892 | 122.8799 | 123.0267 | 66.7433 | -123.1287 | 122.8947 | 123.0496 | 122.9017 | 66.7331 | -123.3198
813.7969 | 123.2483 | -66.6962 | 56.2729 | 0.0046549 | -0.0090682 | 0.0015299 | 0.054149 | -0.0041686 | 0.062503 | 0.015414 | -0.0011301 | -0.00098273 | 0.059313 | 0.018976 | 0.059804 | -66.7518 | -0.012329 | -66.7414 | 56.2427 | 56.138 | 56.2802 | -66.8467 | -66.7657 | -0.013377 | -66.791 | 56.1528 | 56.3168 | 56.1506 | -67.0378 | -0.1505 | -0.030206 | -0.05568 | -0.04526 | 0.10524 | -0.13491 | 0.007323 | -0.34161 | -0.12013 | -0.069532 | -0.09488 | 0.24673 | 0.043894 | -0.12231 | 122.9388 | 122.8341 | 122.9764 | 66.6838 | -123.1196 | 122.8489 | 123.0129 | 122.8467 | 66.6828 | -123.3107
814.7969 | 123.175 | -66.7465 | 56.3461 | -0.0029761 | -0.0097092 | 0.0017435 | 0.054149 | -0.003955 | 0.062503 | 0.015414 | -0.0013437 | -0.00055553 | 0.059313 | 0.018976 | 0.060231 | -66.7473 | -0.003172 | -66.746 | 56.2381 | 56.1288 | 56.2848 | -66.8467 | -66.7565 | -0.00422 | -66.7956 | 56.1436 | 56.3168 | 56.1552 | -67.0424 | -0.10015 | -0.10803 | -0.000748 | 0.000516 | 0.10067 | -0.21731 | -0.06134 | -0.29583 | -0.20253 | -0.010021 | -0.049105 | 0.24673 | -0.029348 | -0.19098 | 122.9846 | 122.8753 | 123.0313 | 66.7433 | -123.1928 | 122.8901 | 123.0633 | 122.9017 | 66.7423 | -123.3885
815.8594 | 123.2803 | -66.7053 | 56.2775 | -0.0029761 | -0.0097092 | 0.0013163 | 0.054149 | -0.0035276 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059527 | 0.01919 | 0.05959 | -66.7427 | -0.003172 | -66.7506 | 56.2473 | 56.1288 | 56.2802 | -66.8513 | -66.7611 | -0.008798 | -66.791 | 56.1528 | 56.3076 | 56.146 | -67.0424 | -0.14593 | -0.030206 | -0.037369 | -0.045261 | 0.10067 | -0.14865 | 0.002745 | -0.33703 | -0.12471 | -0.055799 | -0.085725 | 0.25131 | 0.030158 | -0.13147 | 122.9526 | 122.8341 | 122.9855 | 66.7021 | -123.1287 | 122.8581 | 123.0129 | 122.8513 | 66.6965 | -123.3198
816.7969 | 123.1796 | -66.7419 | 56.337 | -0.010607 | -0.0097092 | 0.0011025 | 0.054363 | -0.0041686 | 0.06293 | 0.0077831 | -0.0015573 | -0.0014101 | 0.059527 | 0.018763 | 0.059804 | -66.7518 | -0.003172 | -66.7323 | 56.2427 | 56.1288 | 56.2894 | -66.8513 | -66.752 | -0.008798 | -66.791 | 56.1528 | 56.303 | 56.146 | -67.0378 | -0.10931 | -0.094293 | -0.009904 | 0.009673 | 0.11898 | -0.20816 | -0.047606 | -0.29583 | -0.18422 | -0.01002 | -0.049104 | 0.24673 | -0.033929 | -0.19098 | 122.9846 | 122.8708 | 123.0313 | 66.7388 | -123.1882 | 122.8947 | 123.045 | 122.8879 | 66.7331 | -123.3747
817.8594 | 123.2803 | -66.7419 | 56.282 | -0.010607 | -0.0097092 | 0.0013163 | 0.054363 | -0.003955 | 0.062503 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059527 | 0.018763 | 0.059163 | -66.7518 | -0.007751 | -66.7414 | 56.2427 | 56.1242 | 56.2802 | -66.8375 | -66.7565 | -0.013377 | -66.791 | 56.1528 | 56.3076 | 56.1368 | -67.0424 | -0.095571 | -0.039361 | -0.009904 | 0.000516 | 0.096087 | -0.15781 | -0.001832 | -0.30041 | -0.12928 | -0.014599 | -0.049104 | 0.25131 | 0.025581 | -0.1452 | 122.9846 | 122.8662 | 123.0222 | 66.7342 | -123.1196 | 122.8947 | 123.0496 | 122.8788 | 66.7286 | -123.3244
818.7969 | 123.1567 | -66.7557 | 56.3461 | 0.0046549 | -0.009282 | 0.0011025 | 0.053722 | -0.0037412 | 0.062717 | 0.0077831 | -0.0015573 | -0.00098273 | 0.05974 | 0.018976 | 0.059376 | -66.7473 | -0.012329 | -66.7368 | 56.2473 | 56.1334 | 56.2894 | -66.8421 | -66.752 | -0.008798 | -66.7956 | 56.1528 | 56.3122 | 56.1506 | -67.0515 | -0.086417 | -0.09887 | 0.008407 | 0.018828 | 0.10525 | -0.21274 | -0.056761 | -0.29583 | -0.19337 | 0.003713 | -0.03995 | 0.25588 | -0.033927 | -0.19555 | 123.0029 | 122.8891 | 123.045 | 66.7433 | -123.1882 | 122.9084 | 123.0679 | 122.9063 | 66.7469 | -123.3976
819.8438 | 123.1613 | -66.7694 | 56.2866 | 0.0046549 | -0.009282 | 0.0013163 | 0.054363 | -0.003955 | 0.062717 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059527 | 0.018763 | 0.05959 | -66.7518 | -0.007751 | -66.746 | 56.2473 | 56.1242 | 56.2848 | -66.8421 | -66.7611 | -0.008798 | -66.791 | 56.1482 | 56.3122 | 56.1414 | -67.0469 | -0.072684 | -0.039361 | 0.017562 | 0.023404 | 0.096088 | -0.16238 | -0.001831 | -0.27752 | -0.13844 | 0.008288 | -0.021638 | 0.25588 | 0.025582 | -0.1452 | 123.0167 | 122.8936 | 123.0542 | 66.7617 | -123.1287 | 122.9176 | 123.0816 | 122.9108 | 66.7606 | -123.3336
820.8281 | 123.2849 | -66.7465 | 56.2958 | -0.0029761 | -0.009923 | 0.0011025 | 0.054363 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059313 | 0.018549 | 0.059804 | -66.7518 | -0.007751 | -66.746 | 56.2473 | 56.1334 | 56.2848 | -66.8421 | -66.7611 | -0.013377 | -66.7956 | 56.1573 | 56.3076 | 56.1414 | -67.0424 | -0.095572 | -0.048516 | -0.005326 | 0.000516 | 0.096088 | -0.16238 | -0.010986 | -0.29583 | -0.13844 | -0.0146 | -0.049105 | 0.24673 | 0.011848 | -0.15436 | 122.9938 | 122.8799 | 123.0313 | 66.7388 | -123.1379 | 122.9039 | 123.0541 | 122.8879 | 66.7331 | -123.3381
821.8594 | 123.3032 | -66.7145 | 56.2866 | 0.012286 | -0.0097092 | 0.0017435 | 0.054363 | -0.003955 | 0.06293 | 0.015414 | -0.0013437 | -0.0011965 | 0.05974 | 0.018763 | 0.060017 | -66.7473 | -0.003172 | -66.7414 | 56.2427 | 56.1334 | 56.2848 | -66.8513 | -66.7611 | -0.008798 | -66.791 | 56.1528 | 56.3076 | 56.146 | -67.0424 | -0.13677 | -0.043939 | -0.032791 | -0.026949 | 0.10982 | -0.15323 | -0.001831 | -0.32788 | -0.13386 | -0.046643 | -0.076569 | 0.25131 | 0.021003 | -0.14062 | 122.9572 | 122.8479 | 122.9993 | 66.7113 | -123.1379 | 122.8672 | 123.0221 | 122.8605 | 66.7057 | -123.329
822.7969 | 123.2162 | -66.7648 | 56.3278 | -0.0029761 | -0.0094956 | 0.0011025 | 0.054149 | -0.0037412 | 0.062503 | 0.0077831 | -0.0015573 | -0.00098273 | 0.059099 | 0.018976 | 0.059804 | -66.7518 | -0.007751 | -66.7368 | 56.2427 | 56.1426 | 56.2848 | -66.8513 | -66.7565 | -0.008798 | -66.8002 | 56.1482 | 56.3076 | 56.146 | -67.0424 | -0.086419 | -0.085138 | 0.012985 | 0.027984 | 0.1144 | -0.18527 | -0.04303 | -0.27752 | -0.17964 | 0.00829 | -0.035373 | 0.24215 | -0.020196 | -0.18182 | 123.0075 | 122.9074 | 123.0496 | 66.7571 | -123.1791 | 122.913 | 123.0725 | 122.9108 | 66.756 | -123.3702
823.8594 | 123.2574 | -66.7236 | 56.2775 | 0.012286 | -0.009923 | 0.0011025 | 0.054363 | -0.0043822 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.059313 | 0.018763 | 0.05959 | -66.7427 | -0.007751 | -66.7368 | 56.2518 | 56.1242 | 56.2802 | -66.8467 | -66.7565 | -0.013377 | -66.7956 | 56.1482 | 56.303 | 56.1506 | -67.0424 | -0.12304 | -0.025627 | -0.019058 | -0.013215 | 0.10982 | -0.15323 | 0.002745 | -0.31872 | -0.12928 | -0.032909 | -0.071993 | 0.24673 | 0.02558 | -0.12689 | 122.9755 | 122.8479 | 123.0038 | 66.7159 | -123.1241 | 122.8718 | 123.0267 | 122.8742 | 66.7103 | -123.3198
824.7969 | 123.175 | -66.7694 | 56.3278 | -0.0029761 | -0.0094956 | 0.0013163 | 0.054363 | -0.0041686 | 0.06293 | 0.00015261 | -0.0015573 | -0.00076913 | 0.05974 | 0.018976 | 0.060231 | -66.7518 | -0.003172 | -66.7414 | 56.2473 | 56.1334 | 56.2848 | -66.8467 | -66.7611 | -0.013377 | -66.7956 | 56.1482 | 56.3076 | 56.146 | -67.0515 | -0.077263 | -0.08056 | 0.017562 | 0.027982 | 0.10524 | -0.19443 | -0.04303 | -0.2821 | -0.17964 | 0.008288 | -0.026217 | 0.25588 | -0.020196 | -0.18182 | 123.0167 | 122.9028 | 123.0542 | 66.7662 | -123.1745 | 122.9176 | 123.077 | 122.9154 | 66.756 | -123.3793
825.7969 | 123.1796 | -66.7465 | 56.3232 | 0.0046549 | -0.0097092 | 0.0011025 | 0.054149 | -0.0041686 | 0.063144 | 0.0077831 | -0.0015573 | -0.0014101 | 0.059527 | 0.018549 | 0.059804 | -66.7473 | -0.007751 | -66.746 | 56.2473 | 56.138 | 56.2848 | -66.8467 | -66.752 | -0.017956 | -66.791 | 56.1528 | 56.303 | 56.1597 | -67.0469 | -0.10015 | -0.075982 | -0.000748 | 0.000516 | 0.10067 | -0.18527 | -0.038452 | -0.30041 | -0.17048 | -0.005442 | -0.044526 | 0.25588 | -0.020196 | -0.16351 | 122.9938 | 122.8845 | 123.0313 | 66.7388 | -123.1699 | 122.8993 | 123.0496 | 122.9063 | 66.7286 | -123.3702
826.7969 | 123.1567 | -66.7557 | 56.337 | 0.0046549 | -0.0097092 | 0.0011025 | 0.054149 | -0.003955 | 0.062503 | 0.0077831 | -0.0019847 | -0.00098273 | 0.059313 | 0.018763 | 0.059804 | -66.7473 | -0.012329 | -66.7323 | 56.2473 | 56.138 | 56.2848 | -66.8467 | -66.7611 | -0.017956 | -66.791 | 56.1528 | 56.3122 | 56.1597 | -67.0424 | -0.090996 | -0.089715 | 0.008407 | 0.023406 | 0.1144 | -0.199 | -0.052185 | -0.28668 | -0.18422 | -0.005445 | -0.035371 | 0.25131 | -0.024772 | -0.17724 | 123.0029 | 122.8936 | 123.0405 | 66.7433 | -123.1836 | 122.9084 | 123.0679 | 122.9154 | 66.7377 | -123.3793
827.7969 | 123.2437 | -66.7374 | 56.3095 | 0.0046549 | -0.009923 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.023044 | -0.0017711 | -0.0011965 | 0.059313 | 0.018549 | 0.059804 | -66.7518 | -0.003172 | -66.7368 | 56.2427 | 56.138 | 56.2848 | -66.8467 | -66.7611 | -0.013377 | -66.791 | 56.1528 | 56.303 | 56.1552 | -67.0424 | -0.10931 | -0.066827 | -0.014481 | 0.000518 | 0.10982 | -0.17153 | -0.024719 | -0.30499 | -0.15675 | -0.023755 | -0.053681 | 0.25131 | -0.006463 | -0.15436 | 122.98 | 122.8753 | 123.0222 | 66.7342 | -123.1562 | 122.8901 | 123.0404 | 122.8925 | 66.724 | -123.3519
828.7969 | 123.2071 | -66.7328 | 56.3141 | -0.0029761 | -0.0097092 | 0.0013163 | 0.053936 | -0.0041686 | 0.06293 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059527 | 0.018976 | 0.059804 | -66.7518 | -0.012329 | -66.7368 | 56.2473 | 56.1242 | 56.2894 | -66.8329 | -66.7611 | -0.008798 | -66.7956 | 56.1573 | 56.2985 | 56.1506 | -67.0469 | -0.10015 | -0.066827 | -0.019059 | -0.00406 | 0.096087 | -0.18985 | -0.024718 | -0.31414 | -0.15675 | -0.028333 | -0.062838 | 0.25131 | -0.01562 | -0.16351 | 122.98 | 122.857 | 123.0222 | 66.7205 | -123.147 | 122.8901 | 123.0313 | 122.8834 | 66.724 | -123.361
829.7969 | 123.1705 | -66.7511 | 56.3553 | 0.012286 | -0.010137 | 0.0013163 | 0.054363 | -0.0037412 | 0.062717 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.018763 | 0.060017 | -66.7473 | -0.007751 | -66.7414 | 56.2473 | 56.138 | 56.2894 | -66.8604 | -66.752 | -0.008798 | -66.791 | 56.1482 | 56.3122 | 56.1643 | -67.0424 | -0.10931 | -0.10803 | 0.00383 | 0.009672 | 0.11898 | -0.21731 | -0.065917 | -0.29125 | -0.2071 | -0.000864 | -0.039948 | 0.25131 | -0.043083 | -0.19098 | 122.9984 | 122.8891 | 123.0405 | 66.7433 | -123.2157 | 122.8993 | 123.0633 | 122.9154 | 66.7423 | -123.3976
830.8594 | 123.1888 | -66.7786 | 56.282 | -0.0029761 | -0.009923 | 0.0015299 | 0.054363 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.018549 | 0.059804 | -66.7518 | -0.012329 | -66.746 | 56.2427 | 56.138 | 56.2756 | -66.8467 | -66.7565 | -0.013377 | -66.7956 | 56.1573 | 56.303 | 56.1552 | -67.0424 | -0.068108 | -0.039361 | 0.026717 | 0.032559 | 0.10067 | -0.14407 | -0.00641 | -0.26379 | -0.1247 | 0.022022 | -0.017062 | 0.24673 | 0.021003 | -0.12689 | 123.0212 | 122.9165 | 123.0542 | 66.7662 | -123.1287 | 122.9359 | 123.0816 | 122.9337 | 66.7652 | -123.3244
831.7969 | 123.175 | -66.7465 | 56.3141 | 0.0046549 | -0.0097092 | 0.0011025 | 0.054149 | -0.0037412 | 0.063144 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059527 | 0.018763 | 0.060017 | -66.7518 | -0.007751 | -66.7368 | 56.2518 | 56.1334 | 56.2894 | -66.8558 | -66.752 | -0.013377 | -66.791 | 56.1436 | 56.3076 | 56.146 | -67.0469 | -0.10931 | -0.062248 | -0.005326 | 0.009673 | 0.11898 | -0.18069 | -0.024718 | -0.30041 | -0.17048 | -0.005442 | -0.044526 | 0.25588 | -0.006463 | -0.16809 | 122.9984 | 122.8799 | 123.0359 | 66.7388 | -123.1699 | 122.8901 | 123.0541 | 122.8925 | 66.7331 | -123.361
832.8594 | 123.2758 | -66.687 | 56.2866 | 0.0046549 | -0.010137 | 0.0015299 | 0.054149 | -0.003955 | 0.062717 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059527 | 0.018549 | 0.05959 | -66.7473 | -0.007751 | -66.7414 | 56.2335 | 56.1288 | 56.2848 | -66.8421 | -66.7657 | -0.013377 | -66.7956 | 56.1482 | 56.3122 | 56.1552 | -67.0378 | -0.15508 | -0.053096 | -0.060257 | -0.054415 | 0.10067 | -0.1578 | -0.001831 | -0.35076 | -0.13844 | -0.078687 | -0.10861 | 0.24215 | 0.025582 | -0.13147 | 122.9205 | 122.8158 | 122.9718 | 66.6793 | -123.1287 | 122.8352 | 122.9992 | 122.8422 | 66.6736 | -123.3244
833.7969 | 123.1659 | -66.7557 | 56.3507 | 0.0046549 | -0.0097092 | 0.0015299 | 0.053722 | -0.0041686 | 0.063144 | 0.0077831 | -0.0015573 | -0.0014101 | 0.059099 | 0.018763 | 0.059376 | -66.7473 | -0.007751 | -66.746 | 56.2381 | 56.138 | 56.2848 | -66.8467 | -66.7611 | -0.013377 | -66.7956 | 56.1436 | 56.303 | 56.1552 | -67.0424 | -0.090996 | -0.1126 | 0.008407 | 0.009671 | 0.10067 | -0.21273 | -0.065918 | -0.28668 | -0.2071 | -0.005445 | -0.03995 | 0.24673 | -0.047662 | -0.19555 | 122.9938 | 122.8936 | 123.0405 | 66.7479 | -123.1974 | 122.8993 | 123.0587 | 122.9108 | 66.7423 | -123.3931
834.7969 | 123.1888 | -66.774 | 56.3095 | 0.0046549 | -0.0097092 | 0.0013163 | 0.054149 | -0.0037412 | 0.062503 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059527 | 0.018976 | 0.05959 | -66.7473 | -0.012329 | -66.746 | 56.2473 | 56.1334 | 56.2802 | -66.8513 | -66.7565 | -0.008798 | -66.7865 | 56.1482 | 56.3076 | 56.1552 | -67.0469 | -0.077264 | -0.062249 | 0.026718 | 0.027982 | 0.10525 | -0.17611 | -0.029298 | -0.27294 | -0.16133 | 0.017445 | -0.012482 | 0.26046 | -0.001885 | -0.15436 | 123.0212 | 122.9074 | 123.0542 | 66.7617 | -123.1608 | 122.9222 | 123.0816 | 122.9291 | 66.7652 | -123.3564
835.7969 | 123.1979 | -66.7511 | 56.3187 | -0.0029761 | -0.009923 | 0.0013163 | 0.054363 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059527 | 0.018976 | 0.059804 | -66.7518 | -0.012329 | -66.746 | 56.2473 | 56.1197 | 56.2848 | -66.8558 | -66.7565 | -0.00422 | -66.791 | 56.1482 | 56.303 | 56.146 | -67.0378 | -0.10473 | -0.071405 | -0.000748 | 0.005094 | 0.10983 | -0.19901 | -0.033875 | -0.28668 | -0.17048 | -0.005443 | -0.039948 | 0.24673 | -0.015619 | -0.17267 | 122.9984 | 122.8708 | 123.0359 | 66.7388 | -123.1745 | 122.8993 | 123.0541 | 122.8971 | 66.7469 | -123.3564
836.8594 | 123.2025 | -66.7694 | 56.3187 | -0.0029761 | -0.0097092 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059313 | 0.018976 | 0.060017 | -66.7473 | -0.012329 | -66.746 | 56.2335 | 56.1426 | 56.2848 | -66.8513 | -66.7611 | -0.017956 | -66.7865 | 56.1482 | 56.3168 | 56.1552 | -67.0424 | -0.081842 | -0.08514 | 0.02214 | 0.023404 | 0.10525 | -0.17611 | -0.033875 | -0.27294 | -0.17048 | 0.008288 | -0.01706 | 0.25588 | -0.001883 | -0.16351 | 123.0029 | 122.912 | 123.0542 | 66.7571 | -123.1699 | 122.9176 | 123.0862 | 122.9246 | 66.7515 | -123.361
837.7969 | 123.1522 | -66.774 | 56.3049 | -0.0029761 | -0.010137 | 0.0015299 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.05974 | 0.018976 | 0.05959 | -66.7427 | 0.001407 | -66.7323 | 56.2427 | 56.1471 | 56.2802 | -66.8329 | -66.7657 | -0.013377 | -66.7865 | 56.139 | 56.3076 | 56.146 | -67.0424 | -0.058948 | -0.06225 | 0.031296 | 0.041717 | 0.10067 | -0.1578 | -0.024721 | -0.26837 | -0.16591 | 0.008288 | -0.012482 | 0.25588 | 0.002692 | -0.15894 | 123.0167 | 122.9211 | 123.0542 | 66.7754 | -123.1379 | 122.913 | 123.0816 | 122.92 | 66.7606 | -123.3473
838.8594 | 123.1705 | -66.7511 | 56.337 | -0.0029761 | -0.0097092 | 0.00088894 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059527 | 0.018763 | 0.05959 | -66.7518 | -0.007751 | -66.7368 | 56.2381 | 56.1334 | 56.2756 | -66.8513 | -66.752 | -0.017956 | -66.7956 | 56.1528 | 56.303 | 56.146 | -67.0469 | -0.10015 | -0.098871 | -0.000748 | 0.014251 | 0.1144 | -0.20358 | -0.061342 | -0.29583 | -0.18422 | -0.000864 | -0.044527 | 0.25131 | -0.033929 | -0.19098 | 122.9892 | 122.8845 | 123.0267 | 66.7433 | -123.1882 | 122.9039 | 123.0541 | 122.8971 | 66.7331 | -123.3839
839.7969 | 123.2208 | -66.7648 | 56.3324 | 0.0046549 | -0.009923 | 0.0013163 | 0.054149 | -0.0037412 | 0.06293 | 0.015414 | -0.0013437 | -0.00098273 | 0.059527 | 0.018976 | 0.059804 | -66.7381 | -0.003172 | -66.7414 | 56.2473 | 56.1334 | 56.2894 | -66.8513 | -66.7565 | -0.017956 | -66.7956 | 56.1482 | 56.2985 | 56.1597 | -67.0378 | -0.086419 | -0.085137 | 0.02672 | 0.023405 | 0.10982 | -0.199 | -0.043028 | -0.27294 | -0.18422 | 0.00829 | -0.030794 | 0.24215 | -0.03393 | -0.17267 | 123.0121 | 122.8982 | 123.0542 | 66.7617 | -123.1836 | 122.913 | 123.0633 | 122.9246 | 66.7469 | -123.3702
840.875 | 123.1705 | -66.7419 | 56.3095 | 0.0046549 | -0.0097092 | 0.0011025 | 0.053936 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059313 | 0.018763 | 0.05959 | -66.7473 | -0.012329 | -66.7368 | 56.2427 | 56.138 | 56.2939 | -66.8513 | -66.752 | -0.008798 | -66.7865 | 56.1482 | 56.3168 | 56.1414 | -67.0424 | -0.10931 | -0.066827 | -0.005326 | 0.005095 | 0.1144 | -0.17153 | -0.015562 | -0.30041 | -0.16133 | -0.01002 | -0.044526 | 0.25588 | 0.007273 | -0.16809 | 122.9846 | 122.8799 | 123.0359 | 66.7296 | -123.1608 | 122.8901 | 123.0587 | 122.8834 | 66.7331 | -123.3519
841.7969 | 123.1796 | -66.7511 | 56.3095 | 0.0046549 | -0.0097092 | 0.0015299 | 0.054363 | -0.0041686 | 0.062503 | 0.00015261 | -0.0017711 | -0.00076913 | 0.059527 | 0.018976 | 0.05959 | -66.7427 | -0.012329 | -66.7368 | 56.2473 | 56.1334 | 56.2848 | -66.8467 | -66.752 | -0.017956 | -66.7956 | 56.1573 | 56.3122 | 56.1414 | -67.0424 | -0.095573 | -0.062249 | 0.008408 | 0.014251 | 0.10982 | -0.17611 | -0.024719 | -0.29125 | -0.15217 | -0.000864 | -0.044527 | 0.24673 | 0.002694 | -0.16809 | 122.9984 | 122.8845 | 123.0359 | 66.7388 | -123.1562 | 122.9084 | 123.0633 | 122.8925 | 66.7331 | -123.3519
842.7969 | 123.2803 | -66.7282 | 56.2637 | -0.010607 | -0.010137 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | -0.0074779 | -0.0015573 | -0.0011965 | 0.059313 | 0.018976 | 0.059804 | -66.7381 | -0.007751 | -66.7414 | 56.2473 | 56.1242 | 56.2802 | -66.8467 | -66.7474 | -0.013377 | -66.7956 | 56.1573 | 56.3122 | 56.146 | -67.0424 | -0.11846 | -0.016473 | -0.009902 | -0.013217 | 0.10524 | -0.1395 | 0.016478 | -0.31414 | -0.10639 | -0.019175 | -0.067416 | 0.24673 | 0.04847 | -0.11774 | 122.9755 | 122.8524 | 123.0084 | 66.7205 | -123.1104 | 122.8855 | 123.0404 | 122.8742 | 66.7148 | -123.3061
843.8594 | 123.2208 | -66.7511 | 56.3187 | -0.0029761 | -0.009923 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059313 | 0.01919 | 0.059804 | -66.7473 | -0.007751 | -66.7368 | 56.2518 | 56.1334 | 56.2894 | -66.8467 | -66.7565 | -0.017956 | -66.791 | 56.1482 | 56.3122 | 56.1597 | -67.0515 | -0.095573 | -0.066826 | 0.00383 | 0.014251 | 0.10982 | -0.18527 | -0.029296 | -0.30041 | -0.17048 | -0.005443 | -0.039948 | 0.26046 | -0.006462 | -0.15893 | 123.0029 | 122.8845 | 123.0405 | 66.7433 | -123.1653 | 122.8993 | 123.0633 | 122.9108 | 66.7331 | -123.3702
844.7969 | 123.3765 | -66.7648 | 56.2683 | -0.0029761 | -0.009923 | 0.0013163 | 0.054577 | -0.003955 | 0.06293 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059313 | 0.01919 | 0.059804 | -66.7473 | -0.012329 | -66.746 | 56.2427 | 56.138 | 56.2894 | -66.8375 | -66.7565 | -0.017956 | -66.791 | 56.1528 | 56.3214 | 56.1552 | -67.0378 | -0.072682 | -0.025629 | 0.017563 | 0.018827 | 0.091509 | -0.13034 | 0.021058 | -0.27294 | -0.11555 | 0.00829 | -0.026215 | 0.24673 | 0.053049 | -0.11316 | 123.0075 | 122.9028 | 123.0542 | 66.7525 | -123.1058 | 122.9176 | 123.0862 | 122.92 | 66.7469 | -123.3061
845.8594 | 123.2712 | -66.7557 | 56.3049 | -0.0029761 | -0.010137 | 0.0011025 | 0.054149 | -0.003955 | 0.062503 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059313 | 0.018763 | 0.059376 | -66.7473 | -0.007751 | -66.7414 | 56.2427 | 56.1242 | 56.2894 | -66.8421 | -66.7611 | -0.017956 | -66.8002 | 56.1482 | 56.3122 | 56.1414 | -67.0469 | -0.086417 | -0.06225 | 0.008407 | 0.014249 | 0.10067 | -0.1807 | -0.015563 | -0.29126 | -0.15675 | -0.005445 | -0.044529 | 0.24673 | 0.007271 | -0.16351 | 122.9984 | 122.8799 | 123.045 | 66.7479 | -123.147 | 122.9039 | 123.0679 | 122.8971 | 66.7377 | -123.3519
846.7969 | 123.2986 | -66.7145 | 56.2683 | 0.0046549 | -0.010137 | 0.0013163 | 0.054363 | -0.003955 | 0.06293 | 0.0077831 | -0.0015573 | -0.00098273 | 0.059313 | 0.01919 | 0.060017 | -66.7564 | -0.003172 | -66.746 | 56.2427 | 56.1334 | 56.2802 | -66.8558 | -66.752 | -0.017956 | -66.791 | 56.1528 | 56.3122 | 56.1506 | -67.0469 | -0.14135 | -0.025629 | -0.041948 | -0.031527 | 0.10983 | -0.13492 | 0.0119 | -0.33245 | -0.11555 | -0.037485 | -0.076569 | 0.25588 | 0.043892 | -0.11774 | 122.9572 | 122.8479 | 122.9947 | 66.7113 | -123.1241 | 122.8672 | 123.0267 | 122.8651 | 66.6965 | -123.3152
847.7969 | 123.1842 | -66.7786 | 56.3049 | -0.0029761 | -0.0097092 | 0.0011025 | 0.053936 | -0.0041686 | 0.06293 | 0.0077831 | -0.0017711 | -0.0011965 | 0.058886 | 0.018976 | 0.05959 | -66.7427 | -0.007751 | -66.7506 | 56.2473 | 56.1288 | 56.2848 | -66.8421 | -66.7565 | -0.017956 | -66.7865 | 56.1528 | 56.3168 | 56.1368 | -67.0469 | -0.063529 | -0.057672 | 0.035873 | 0.027981 | 0.09151 | -0.17612 | -0.020142 | -0.26837 | -0.15217 | 0.022022 | -0.007905 | 0.26046 | 0.01185 | -0.16809 | 123.0258 | 122.9074 | 123.0634 | 66.7708 | -123.147 | 122.9313 | 123.0953 | 122.9154 | 66.7606 | -123.3519
848.8594 | 123.2117 | -66.7603 | 56.3324 | -0.010607 | -0.01035 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.015414 | -0.0013437 | -0.0011965 | 0.059313 | 0.019617 | 0.05959 | -66.7473 | -0.007751 | -66.7414 | 56.2427 | 56.138 | 56.2848 | -66.8421 | -66.752 | -0.013377 | -66.7865 | 56.1482 | 56.3076 | 56.146 | -67.0424 | -0.081839 | -0.089715 | 0.012985 | 0.018827 | 0.10067 | -0.19442 | -0.047607 | -0.2821 | -0.18422 | 0.008291 | -0.026215 | 0.25588 | -0.024773 | -0.1864 | 123.0029 | 122.8982 | 123.045 | 66.7525 | -123.1745 | 122.9084 | 123.0679 | 122.9062 | 66.7469 | -123.3748
849.7969 | 123.1659 | -66.774 | 56.3004 | 0.0046549 | -0.010137 | 0.0011025 | 0.054363 | -0.0041686 | 0.062717 | 0.015414 | -0.0015573 | -0.0011965 | 0.059313 | 0.01919 | 0.05959 | -66.7473 | 0.001407 | -66.7323 | 56.2518 | 56.138 | 56.2894 | -66.8467 | -66.7565 | -0.017956 | -66.791 | 56.1573 | 56.3122 | 56.1506 | -67.0424 | -0.072685 | -0.048515 | 0.026718 | 0.041717 | 0.1144 | -0.16238 | -0.010985 | -0.26837 | -0.14301 | 0.017445 | -0.01706 | 0.25131 | 0.011849 | -0.14978 | 123.0258 | 122.912 | 123.0634 | 66.7754 | -123.147 | 122.9313 | 123.0862 | 122.9246 | 66.756 | -123.3427
850.7969 | 123.2117 | -66.7419 | 56.3141 | 0.0046549 | -0.0097092 | 0.0015299 | 0.054149 | -0.0041686 | 0.062717 | 0.0077831 | -0.0017711 | -0.0011965 | 0.059313 | 0.018763 | 0.05959 | -66.7518 | -0.003172 | -66.7368 | 56.2427 | 56.1197 | 56.2894 | -66.8421 | -66.752 | -0.013377 | -66.791 | 56.1528 | 56.303 | 56.1597 | -67.0378 | -0.10015 | -0.071405 | -0.009904 | 0.005095 | 0.10525 | -0.19443 | -0.024718 | -0.29583 | -0.16133 | -0.01002 | -0.049104 | 0.24673 | -0.011041 | -0.15436 | 122.9846 | 122.8616 | 123.0313 | 66.7388 | -123.1562 | 122.8947 | 123.045 | 122.9017 | 66.7286 | -123.3519
851.7969 | 123.2895 | -66.7282 | 56.25 | -0.0029761 | -0.0097092 | 0.0015299 | 0.054363 | -0.003955 | 0.062717 | 0.00015261 | -0.0013437 | -0.0011965 | 0.059099 | 0.018976 | 0.05959 | -66.7427 | -0.003172 | -66.7414 | 56.2473 | 56.1288 | 56.2894 | -66.8467 | -66.752 | -0.013377 | -66.7865 | 56.1573 | 56.3122 | 56.146 | -67.0424 | -0.11846 | -0.00274 | -0.014481 | -0.013217 | 0.10524 | -0.12118 | 0.039369 | -0.31414 | -0.092661 | -0.023753 | -0.058259 | 0.25588 | 0.062203 | -0.104 | 122.9755 | 122.857 | 123.0176 | 66.725 | -123.0967 | 122.8855 | 123.0404 | 122.8742 | 66.7148 | -123.2924
852.7969 | 123.2162 | -66.7328 | 56.2912 | -0.0029761 | -0.01035 | 0.0015299 | 0.054363 | -0.003955 | 0.062717 | 0.0077831 | -0.0011301 | -0.00098273 | 0.059099 | 0.019617 | 0.059804 | -66.7473 | -0.007751 | -66.746 | 56.2473 | 56.1288 | 56.2848 | -66.8467 | -66.7657 | -0.022535 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0424 | -0.11388 | -0.043939 | -0.014481 | -0.013217 | 0.10067 | -0.16238 | -0.006409 | -0.30957 | -0.13844 | -0.032911 | -0.058259 | 0.25131 | 0.021004 | -0.1452 | 122.98 | 122.8616 | 123.0176 | 66.725 | -123.1379 | 122.8855 | 123.045 | 122.8788 | 66.7103 | -123.3336
853.8438 | 123.1659 | -66.7236 | 56.3416 | 0.0046549 | -0.010137 | 0.0011025 | 0.054149 | -0.003955 | 0.062503 | 0.0077831 | -0.0019847 | -0.0011965 | 0.059527 | 0.019404 | 0.05959 | -66.7427 | -0.007751 | -66.7414 | 56.2473 | 56.1334 | 56.2894 | -66.8467 | -66.7611 | -0.013377 | -66.7956 | 56.1528 | 56.3122 | 56.1552 | -67.0424 | -0.12304 | -0.094293 | -0.019058 | -0.017794 | 0.10524 | -0.20816 | -0.052184 | -0.31872 | -0.18879 | -0.037488 | -0.071993 | 0.24673 | -0.02935 | -0.1864 | 122.9709 | 122.857 | 123.013 | 66.7159 | -123.1882 | 122.8764 | 123.0358 | 122.8788 | 66.7103 | -123.3839
854.7969 | 123.2162 | -66.7465 | 56.2775 | -0.0029761 | -0.010137 | 0.0011025 | 0.054791 | -0.0041686 | 0.062503 | 0.030675 | -0.0015573 | -0.00098273 | 0.059313 | 0.019404 | 0.05959 | -66.7473 | -0.003172 | -66.7414 | 56.2427 | 56.1334 | 56.2848 | -66.8467 | -66.7565 | -0.017956 | -66.7956 | 56.1528 | 56.3122 | 56.1414 | -67.0424 | -0.10015 | -0.034784 | -0.000748 | 0.005094 | 0.10524 | -0.14407 | 0.007324 | -0.29583 | -0.12471 | -0.010021 | -0.049105 | 0.24673 | 0.034737 | -0.13605 | 122.9892 | 122.8799 | 123.0313 | 66.7433 | -123.1241 | 122.8993 | 123.0587 | 122.8879 | 66.7286 | -123.3198
855.7969 | 123.2574 | -66.7282 | 56.3004 | 0.0046549 | -0.009923 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.059099 | 0.019617 | 0.059804 | -66.7427 | -0.007751 | -66.7368 | 56.2427 | 56.1288 | 56.2939 | -66.8513 | -66.752 | -0.017956 | -66.791 | 56.1482 | 56.3168 | 56.1506 | -67.0469 | -0.12304 | -0.057672 | -0.014481 | -0.008638 | 0.1144 | -0.17154 | -0.006407 | -0.31872 | -0.15217 | -0.023753 | -0.062837 | 0.25588 | 0.016428 | -0.14978 | 122.9709 | 122.857 | 123.0222 | 66.7205 | -123.1516 | 122.8764 | 123.045 | 122.8788 | 66.7103 | -123.3473
856.7969 | 123.2758 | -66.7053 | 56.2958 | 0.012286 | -0.009923 | 0.0011025 | 0.054577 | -0.0043822 | 0.062717 | 0.015414 | -0.0015573 | -0.0011965 | 0.059527 | 0.01919 | 0.059804 | -66.7427 | -0.007751 | -66.7414 | 56.2518 | 56.1288 | 56.2848 | -66.8375 | -66.7611 | -0.022535 | -66.7956 | 56.1482 | 56.3214 | 56.146 | -67.0424 | -0.13219 | -0.043937 | -0.037369 | -0.036105 | 0.096087 | -0.16696 | -0.010986 | -0.33703 | -0.14759 | -0.055799 | -0.090304 | 0.24673 | 0.025584 | -0.14978 | 122.9572 | 122.8341 | 122.9901 | 66.6976 | -123.1333 | 122.8535 | 123.0267 | 122.8513 | 66.6828 | -123.3381
857.7969 | 123.2437 | -66.7282 | 56.2912 | -0.0029761 | -0.010137 | 0.0011025 | 0.053936 | -0.0037412 | 0.062717 | 0.015414 | -0.0013437 | -0.0014101 | 0.059099 | 0.018976 | 0.05959 | -66.7473 | -0.012329 | -66.7368 | 56.2427 | 56.1242 | 56.2939 | -66.8467 | -66.7565 | -0.013377 | -66.791 | 56.1528 | 56.3122 | 56.1414 | -67.0424 | -0.11846 | -0.048517 | -0.019059 | -0.008638 | 0.10982 | -0.16696 | 0.002748 | -0.31414 | -0.13844 | -0.028332 | -0.062837 | 0.25131 | 0.021004 | -0.14978 | 122.9709 | 122.8524 | 123.0222 | 66.7159 | -123.1379 | 122.881 | 123.0404 | 122.8696 | 66.7148 | -123.3336
858.8594 | 123.2529 | -66.7328 | 56.2912 | -0.010607 | -0.009923 | 0.0015299 | 0.053936 | -0.0037412 | 0.06293 | 0.015414 | -0.0015573 | -0.00098273 | 0.058886 | 0.01919 | 0.05959 | -66.7427 | -0.016908 | -66.7414 | 56.2518 | 56.138 | 56.2894 | -66.8513 | -66.7657 | -0.013377 | -66.7956 | 56.1573 | 56.3122 | 56.1368 | -67.0424 | -0.11846 | -0.03936 | -0.009903 | -0.008639 | 0.10982 | -0.15322 | -0.00183 | -0.30957 | -0.13386 | -0.032911 | -0.062838 | 0.24673 | 0.021004 | -0.15436 | 122.9846 | 122.8708 | 123.0222 | 66.7159 | -123.1424 | 122.8901 | 123.045 | 122.8696 | 66.7194 | -123.3336
859.7969 | 123.2941 | -66.7374 | 56.2775 | 0.0046549 | -0.01035 | 0.0013163 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0013437 | -0.0014101 | 0.059099 | 0.019404 | 0.059804 | -66.7518 | -0.007751 | -66.7368 | 56.2473 | 56.1288 | 56.2939 | -66.8467 | -66.752 | -0.017956 | -66.7956 | 56.1528 | 56.3168 | 56.1506 | -67.0515 | -0.10931 | -0.030206 | -0.014481 | 0.000518 | 0.10982 | -0.14865 | 0.016481 | -0.31414 | -0.12471 | -0.014597 | -0.05826 | 0.25588 | 0.039316 | -0.12689 | 122.9846 | 122.8662 | 123.0313 | 66.7296 | -123.1241 | 122.8901 | 123.0541 | 122.8879 | 66.7194 | -123.329
860.7969 | 123.3032 | -66.687 | 56.3416 | 0.0046549 | -0.010137 | 0.0013163 | 0.054149 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059313 | 0.019404 | 0.05959 | -66.7473 | -0.012329 | -66.746 | 56.2473 | 56.1242 | 56.2848 | -66.8421 | -66.7565 | -0.017956 | -66.7956 | 56.1528 | 56.3076 | 56.146 | -67.0378 | -0.15508 | -0.094293 | -0.060257 | -0.058993 | 0.096088 | -0.21732 | -0.056763 | -0.35076 | -0.18879 | -0.06953 | -0.10861 | 0.24215 | -0.033929 | -0.19556 | 122.9343 | 122.8112 | 122.9718 | 66.6747 | -123.1836 | 122.8398 | 122.9946 | 122.833 | 66.6691 | -123.3793
861.7969 | 123.2666 | -66.7328 | 56.3004 | -0.0029761 | -0.010137 | 0.0011025 | 0.054363 | -0.0043822 | 0.062717 | -0.0074779 | -0.0015573 | -0.0011965 | 0.059099 | 0.019404 | 0.059804 | -66.7518 | -0.012329 | -66.7552 | 56.2427 | 56.1288 | 56.2848 | -66.8558 | -66.7565 | -0.017956 | -66.791 | 56.1528 | 56.3076 | 56.1506 | -67.0469 | -0.12304 | -0.057672 | -0.019059 | -0.022373 | 0.10067 | -0.17154 | -0.015564 | -0.31414 | -0.14759 | -0.023754 | -0.058259 | 0.25588 | 0.00727 | -0.14978 | 122.9755 | 122.8616 | 123.0176 | 66.7205 | -123.1562 | 122.8855 | 123.0404 | 122.8834 | 66.7148 | -123.3473
862.8594 | 123.2758 | -66.7328 | 56.2866 | -0.0029761 | -0.01035 | 0.0013163 | 0.054149 | -0.0043822 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.059099 | 0.01919 | 0.059804 | -66.7518 | -0.012329 | -66.7414 | 56.2427 | 56.1288 | 56.2848 | -66.8421 | -66.7611 | -0.013377 | -66.7865 | 56.1528 | 56.3214 | 56.1506 | -67.0424 | -0.10931 | -0.043939 | -0.019059 | -0.008639 | 0.10067 | -0.1578 | -0.001831 | -0.30957 | -0.13386 | -0.028333 | -0.053681 | 0.25588 | 0.034739 | -0.13605 | 122.9755 | 122.8616 | 123.0176 | 66.7205 | -123.1287 | 122.8855 | 123.0541 | 122.8834 | 66.7194 | -123.329
863.7969 | 123.23 | -66.7236 | 56.3141 | 0.0046549 | -0.009923 | 0.0015299 | 0.054577 | -0.003955 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.059527 | 0.019404 | 0.05959 | -66.7473 | -0.012329 | -66.746 | 56.2427 | 56.1334 | 56.2894 | -66.8421 | -66.7611 | -0.017956 | -66.7819 | 56.1528 | 56.3122 | 56.146 | -67.0469 | -0.11846 | -0.071405 | -0.023636 | -0.022372 | 0.096088 | -0.18069 | -0.024718 | -0.3233 | -0.16133 | -0.037488 | -0.058257 | 0.26504 | -0.001884 | -0.16809 | 122.9663 | 122.857 | 123.013 | 66.7113 | -123.1562 | 122.8764 | 123.0358 | 122.8696 | 66.7057 | -123.361
864.7969 | 123.2574 | -66.6962 | 56.3141 | -0.0029761 | -0.01035 | 0.0011025 | 0.053936 | -0.003955 | 0.06293 | 0.0077831 | -0.0019847 | -0.00098273 | 0.059313 | 0.019831 | 0.059804 | -66.7473 | -0.007751 | -66.7414 | 56.2427 | 56.1242 | 56.2894 | -66.8513 | -66.7565 | -0.013377 | -66.7865 | 56.1482 | 56.3214 | 56.1506 | -67.0424 | -0.15508 | -0.071405 | -0.051102 | -0.04526 | 0.10982 | -0.18985 | -0.024718 | -0.34619 | -0.16591 | -0.060375 | -0.090302 | 0.25588 | 0.007273 | -0.16351 | 122.9388 | 122.8204 | 122.9855 | 66.6884 | -123.1653 | 122.8443 | 123.0175 | 122.8467 | 66.6828 | -123.3564
865.7969 | 123.2712 | -66.6779 | 56.3049 | -0.0029761 | -0.0097092 | 0.0013163 | 0.054363 | -0.003955 | 0.062717 | 0.015414 | -0.0013437 | -0.00098273 | 0.059527 | 0.019831 | 0.059804 | -66.7518 | -0.016908 | -66.7323 | 56.2381 | 56.1334 | 56.2848 | -66.8513 | -66.7611 | -0.017956 | -66.791 | 56.1573 | 56.3168 | 56.1506 | -67.0469 | -0.17339 | -0.066828 | -0.073991 | -0.054414 | 0.11898 | -0.17154 | -0.020142 | -0.36908 | -0.14759 | -0.083265 | -0.11319 | 0.25588 | 0.01185 | -0.15436 | 122.916 | 122.8113 | 122.9626 | 66.6609 | -123.1562 | 122.8352 | 122.9946 | 122.8284 | 66.6599 | -123.3519
866.7969 | 123.2574 | -66.7145 | 56.3049 | 0.0046549 | -0.0097092 | 0.0015299 | 0.054363 | -0.0041686 | 0.062503 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059099 | 0.01919 | 0.059376 | -66.7427 | -0.012329 | -66.7368 | 56.2473 | 56.138 | 56.2848 | -66.8421 | -66.7474 | -0.013377 | -66.791 | 56.1528 | 56.3076 | 56.1552 | -67.0469 | -0.12762 | -0.057672 | -0.028213 | -0.02237 | 0.10525 | -0.16696 | -0.020142 | -0.33245 | -0.15217 | -0.032907 | -0.076569 | 0.25588 | 0.002692 | -0.14978 | 122.9617 | 122.8525 | 122.9993 | 66.7021 | -123.147 | 122.8672 | 123.0221 | 122.8696 | 66.7011 | -123.3519
867.8594 | 123.2758 | -66.7419 | 56.2729 | -0.0029761 | -0.0097092 | 0.0015299 | 0.054363 | -0.0043822 | 0.062289 | -0.0074779 | -0.0015573 | -0.00076913 | 0.059099 | 0.019617 | 0.059376 | -66.7427 | -0.007751 | -66.7277 | 56.2518 | 56.1334 | 56.2802 | -66.8467 | -66.752 | -0.022535 | -66.8002 | 56.1573 | 56.3122 | 56.1323 | -67.0424 | -0.10473 | -0.021049 | -0.000748 | 0.014251 | 0.11898 | -0.13949 | 0.007323 | -0.30041 | -0.11555 | -0.01002 | -0.058262 | 0.24215 | 0.039315 | -0.14063 | 122.9938 | 122.8753 | 123.0222 | 66.7342 | -123.1196 | 122.8993 | 123.0541 | 122.8742 | 66.7194 | -123.3152
868.7969 | 123.2666 | -66.7099 | 56.3232 | 0.0046549 | -0.009923 | 0.0011025 | 0.053936 | -0.0037412 | 0.062503 | -0.0074779 | -0.0011301 | -0.00098273 | 0.059099 | 0.019617 | 0.05959 | -66.7427 | -0.007751 | -66.7231 | 56.2473 | 56.1334 | 56.2939 | -66.8513 | -66.752 | -0.017956 | -66.791 | 56.1573 | 56.303 | 56.1552 | -67.0424 | -0.14135 | -0.075982 | -0.032791 | -0.013213 | 0.12814 | -0.18985 | -0.029295 | -0.33245 | -0.1659 | -0.042063 | -0.081147 | 0.25131 | -0.020196 | -0.16809 | 122.9572 | 122.8433 | 123.0038 | 66.7021 | -123.1745 | 122.8672 | 123.0129 | 122.8651 | 66.6919 | -123.3656
869.7969 | 123.2803 | -66.6962 | 56.3141 | 0.019917 | -0.01035 | 0.0015299 | 0.054363 | -0.0037412 | 0.062717 | 0.0077831 | -0.0013437 | -0.0011965 | 0.058886 | 0.01919 | 0.059804 | -66.7381 | -0.012329 | -66.7277 | 56.2381 | 56.1288 | 56.2848 | -66.8467 | -66.752 | -0.022535 | -66.7865 | 56.1528 | 56.3076 | 56.1414 | -67.0424 | -0.1505 | -0.075983 | -0.041945 | -0.031525 | 0.11898 | -0.18527 | -0.029297 | -0.34619 | -0.16133 | -0.055796 | -0.090302 | 0.25588 | -0.006463 | -0.17267 | 122.9343 | 122.825 | 122.981 | 66.6838 | -123.1608 | 122.8489 | 123.0038 | 122.8376 | 66.6736 | -123.3564
870.7969 | 123.1979 | -66.7419 | 56.337 | -0.0029761 | -0.0097092 | 0.0013163 | 0.053722 | -0.003955 | 0.062503 | 0.015414 | -0.00091653 | -0.00034193 | 0.059313 | 0.019404 | 0.059376 | -66.7473 | -0.007751 | -66.7231 | 56.2381 | 56.138 | 56.2848 | -66.8513 | -66.752 | -0.017956 | -66.791 | 56.1573 | 56.3122 | 56.146 | -67.0469 | -0.10931 | -0.098871 | -0.005326 | 0.01883 | 0.12814 | -0.199 | -0.052185 | -0.30499 | -0.17964 | -0.01002 | -0.049104 | 0.25588 | -0.024772 | -0.19098 | 122.98 | 122.8799 | 123.0267 | 66.7342 | -123.1882 | 122.8993 | 123.0541 | 122.8879 | 66.724 | -123.3839
871.8594 | 123.262 | -66.7099 | 56.2958 | -0.0029761 | -0.0097092 | 0.0015299 | 0.054363 | -0.003955 | 0.062289 | 0.00015261 | -0.0011301 | -0.00076913 | 0.059313 | 0.019617 | 0.059376 | -66.7473 | -0.016908 | -66.7277 | 56.2427 | 56.1288 | 56.2848 | -66.8513 | -66.7428 | -0.022535 | -66.7956 | 56.1436 | 56.3122 | 56.1414 | -67.0424 | -0.14135 | -0.053094 | -0.037369 | -0.017792 | 0.12356 | -0.16696 | -0.010986 | -0.33245 | -0.15217 | -0.032906 | -0.085726 | 0.24673 | 0.016427 | -0.15436 | 122.9526 | 122.8387 | 122.9947 | 66.693 | -123.147 | 122.8535 | 123.0221 | 122.8513 | 66.6874 | -123.3381
872.7969 | 123.1613 | -66.7374 | 56.337 | 0.0046549 | -0.009923 | 0.0013163 | 0.054149 | -0.0035276 | 0.062289 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059313 | 0.019404 | 0.05959 | -66.7473 | -0.007751 | -66.7277 | 56.2473 | 56.1197 | 56.2939 | -66.8513 | -66.7428 | -0.027113 | -66.791 | 56.1482 | 56.3122 | 56.1414 | -67.0469 | -0.11389 | -0.089715 | -0.009903 | 0.009674 | 0.12356 | -0.21732 | -0.043028 | -0.30957 | -0.18879 | -0.00544 | -0.053681 | 0.25588 | -0.024772 | -0.19556 | 122.9846 | 122.857 | 123.0313 | 66.7296 | -123.1882 | 122.8855 | 123.0496 | 122.8788 | 66.7103 | -123.3839
873.8594 | 123.1796 | -66.7419 | 56.282 | -0.0029761 | -0.01035 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | -0.0074779 | -0.0013437 | -0.00076913 | 0.059313 | 0.019404 | 0.059376 | -66.7473 | -0.007751 | -66.7231 | 56.2518 | 56.1288 | 56.2848 | -66.8467 | -66.7474 | -0.022535 | -66.791 | 56.1528 | 56.3214 | 56.1506 | -67.0424 | -0.10473 | -0.030204 | -0.005326 | 0.01883 | 0.12356 | -0.15323 | 0.002747 | -0.30041 | -0.12928 | -0.005442 | -0.049104 | 0.25131 | 0.039317 | -0.13147 | 122.9938 | 122.8708 | 123.0267 | 66.7342 | -123.1287 | 122.8947 | 123.0633 | 122.8925 | 66.7194 | -123.3244
874.7969 | 123.2162 | -66.7191 | 56.3049 | 0.0046549 | -0.010137 | 0.0015299 | 0.053722 | -0.0037412 | 0.062289 | 0.0077831 | -0.0011301 | -0.00055553 | 0.058672 | 0.019617 | 0.059804 | -66.7518 | -0.016908 | -66.7277 | 56.2518 | 56.138 | 56.2939 | -66.8421 | -66.752 | -0.017956 | -66.7865 | 56.1573 | 56.3076 | 56.1323 | -67.0378 | -0.12304 | -0.053093 | -0.032792 | -0.008637 | 0.1144 | -0.16696 | -0.010985 | -0.31872 | -0.14759 | -0.032908 | -0.067414 | 0.25131 | 0.002692 | -0.17267 | 122.9709 | 122.857 | 123.013 | 66.7021 | -123.147 | 122.8764 | 123.0267 | 122.8513 | 66.7011 | -123.3427
875.7969 | 123.3078 | -66.6916 | 56.3004 | 0.0046549 | -0.010137 | 0.0015299 | 0.054149 | -0.003955 | 0.062289 | -0.0074779 | -0.0013437 | -0.00055553 | 0.059099 | 0.019617 | 0.05959 | -66.7564 | -0.007751 | -66.7231 | 56.2427 | 56.138 | 56.2802 | -66.8513 | -66.752 | -0.017956 | -66.7865 | 56.1528 | 56.3122 | 56.1368 | -67.0469 | -0.15966 | -0.057672 | -0.064837 | -0.031524 | 0.12814 | -0.16238 | -0.020143 | -0.35534 | -0.14759 | -0.060374 | -0.09488 | 0.26046 | 0.011849 | -0.16351 | 122.9343 | 122.8296 | 122.9718 | 66.6838 | -123.1516 | 122.8443 | 123.0038 | 122.8284 | 66.6736 | -123.3473
876.8594 | 123.2849 | -66.7053 | 56.3187 | -0.0029761 | -0.01035 | 0.0013163 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0011301 | -0.00076913 | 0.059313 | 0.019404 | 0.05959 | -66.7473 | -0.016908 | -66.7185 | 56.2473 | 56.1334 | 56.2848 | -66.8467 | -66.752 | -0.017956 | -66.7819 | 56.1528 | 56.3122 | 56.146 | -67.0469 | -0.14135 | -0.071405 | -0.041947 | -0.013213 | 0.12814 | -0.18527 | -0.033875 | -0.34161 | -0.16591 | -0.046641 | -0.076568 | 0.26504 | -0.006462 | -0.17267 | 122.9526 | 122.8387 | 122.9901 | 66.6884 | -123.1653 | 122.8581 | 123.0175 | 122.8513 | 66.6874 | -123.3656
877.7969 | 123.2986 | -66.7191 | 56.2912 | 0.0046549 | -0.010137 | 0.0015299 | 0.054149 | -0.0041686 | 0.062503 | 0.0077831 | -0.0013437 | -0.00076913 | 0.059313 | 0.019617 | 0.05959 | -66.7518 | -0.021486 | -66.7277 | 56.2427 | 56.1288 | 56.2894 | -66.8421 | -66.7474 | -0.017956 | -66.7956 | 56.1482 | 56.3076 | 56.1414 | -67.0424 | -0.12304 | -0.048517 | -0.032792 | -0.008637 | 0.1144 | -0.16238 | -0.00183 | -0.3233 | -0.14302 | -0.02833 | -0.076571 | 0.24673 | 0.016425 | -0.14978 | 122.9617 | 122.8479 | 123.0084 | 66.6976 | -123.1333 | 122.8672 | 123.0267 | 122.8605 | 66.7011 | -123.3336
878.7969 | 123.175 | -66.7419 | 56.337 | -0.0029761 | -0.010137 | 0.0015299 | 0.054149 | -0.003955 | 0.06293 | 0.00015261 | -0.0013437 | -0.00055553 | 0.058886 | 0.019617 | 0.059163 | -66.7473 | -0.012329 | -66.7368 | 56.2518 | 56.1334 | 56.2939 | -66.8421 | -66.7565 | -0.017956 | -66.7956 | 56.1528 | 56.3168 | 56.146 | -67.0515 | -0.10015 | -0.085136 | -0.005326 | 0.005095 | 0.10525 | -0.20358 | -0.043028 | -0.30957 | -0.18422 | -0.014599 | -0.053683 | 0.25588 | -0.020193 | -0.19098 | 122.9938 | 122.8753 | 123.0359 | 66.7296 | -123.1791 | 122.8947 | 123.0587 | 122.8879 | 66.724 | -123.3885
879.7969 | 123.349 | -66.7145 | 56.2775 | 0.012286 | -0.01035 | 0.0015299 | 0.054363 | -0.0037412 | 0.062503 | -0.0074779 | -0.0015573 | -0.0011965 | 0.059313 | 0.019831 | 0.059804 | -66.7427 | -0.021486 | -66.7277 | 56.2473 | 56.138 | 56.2985 | -66.8513 | -66.752 | -0.017956 | -66.8002 | 56.1482 | 56.3259 | 56.1414 | -67.0469 | -0.13677 | -0.030206 | -0.028213 | -0.013214 | 0.12356 | -0.13949 | 0.02106 | -0.33245 | -0.12928 | -0.037485 | -0.085727 | 0.24673 | 0.048473 | -0.13605 | 122.9617 | 122.8525 | 123.013 | 66.693 | -123.1287 | 122.8627 | 123.0404 | 122.8559 | 66.6965 | -123.3244
880.7969 | 123.1934 | -66.7557 | 56.3278 | -0.0029761 | -0.010564 | 0.0013163 | 0.053722 | -0.003955 | 0.062503 | 0.00015261 | -0.0013437 | -0.00076913 | 0.058886 | 0.019617 | 0.059376 | -66.7473 | -0.012329 | -66.7277 | 56.2427 | 56.1426 | 56.2894 | -66.8467 | -66.752 | -0.022535 | -66.791 | 56.1436 | 56.3214 | 56.1506 | -67.0424 | -0.090996 | -0.085138 | 0.008407 | 0.027984 | 0.11898 | -0.18527 | -0.038451 | -0.28668 | -0.18422 | 0.003713 | -0.035371 | 0.25131 | -0.00646 | -0.17724 | 122.9984 | 122.8982 | 123.045 | 66.7433 | -123.1745 | 122.8993 | 123.077 | 122.9063 | 66.7331 | -123.3702
881.7969 | 123.2712 | -66.7236 | 56.2866 | 0.012286 | -0.01035 | 0.0013163 | 0.054363 | -0.0037412 | 0.062717 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059527 | 0.01919 | 0.059376 | -66.7473 | -0.012329 | -66.7323 | 56.2427 | 56.1288 | 56.2848 | -66.8467 | -66.7611 | -0.022535 | -66.7956 | 56.1528 | 56.3122 | 56.1414 | -67.0469 | -0.12304 | -0.043939 | -0.023636 | -0.008637 | 0.1144 | -0.1578 | -0.001831 | -0.3233 | -0.13386 | -0.037488 | -0.071993 | 0.25131 | 0.025582 | -0.1452 | 122.9663 | 122.8524 | 123.0084 | 66.7113 | -123.1333 | 122.8764 | 123.0358 | 122.8651 | 66.7011 | -123.3336
882.7969 | 123.1659 | -66.7603 | 56.3507 | 0.0046549 | -0.01035 | 0.0015299 | 0.054149 | -0.0041686 | 0.062717 | 0.015414 | -0.0017711 | -0.00098273 | 0.059313 | 0.019617 | 0.05959 | -66.7427 | -0.021486 | -66.7414 | 56.2473 | 56.138 | 56.2939 | -66.8513 | -66.7611 | -0.017956 | -66.7865 | 56.1482 | 56.3214 | 56.146 | -67.0469 | -0.090997 | -0.10345 | 0.017563 | 0.018827 | 0.10982 | -0.21273 | -0.056761 | -0.28668 | -0.20253 | -0.000867 | -0.026215 | 0.26046 | -0.029348 | -0.20471 | 123.0075 | 122.8982 | 123.0542 | 66.7388 | -123.202 | 122.9084 | 123.0816 | 122.9062 | 66.7423 | -123.3976
883.7969 | 123.2254 | -66.7328 | 56.3232 | 0.012286 | -0.01035 | 0.0015299 | 0.054149 | -0.003955 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059099 | 0.019831 | 0.05959 | -66.7473 | -0.012329 | -66.7414 | 56.2473 | 56.1426 | 56.2939 | -66.8284 | -66.7565 | -0.017956 | -66.7819 | 56.1482 | 56.3122 | 56.1552 | -67.0378 | -0.095568 | -0.075982 | -0.014481 | -0.008639 | 0.086929 | -0.18069 | -0.029295 | -0.30499 | -0.17506 | -0.023754 | -0.049102 | 0.25588 | -0.011039 | -0.16809 | 122.98 | 122.8753 | 123.0267 | 66.7205 | -123.1516 | 122.881 | 123.045 | 122.8879 | 66.7148 | -123.361
884.8594 | 123.1979 | -66.7282 | 56.3416 | -0.0029761 | -0.010564 | 0.0013163 | 0.053722 | -0.0041686 | 0.063144 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.019831 | 0.059376 | -66.7518 | -0.016908 | -66.7414 | 56.2518 | 56.1288 | 56.2894 | -66.8467 | -66.7565 | -0.022535 | -66.791 | 56.1528 | 56.303 | 56.1506 | -67.0424 | -0.11846 | -0.089714 | -0.023637 | -0.013217 | 0.10524 | -0.21274 | -0.052184 | -0.31414 | -0.18879 | -0.028332 | -0.062837 | 0.25131 | -0.038507 | -0.19098 | 122.98 | 122.857 | 123.0176 | 66.7113 | -123.1882 | 122.881 | 123.0313 | 122.8788 | 66.7057 | -123.3839
885.7969 | 123.1842 | -66.7465 | 56.3416 | -0.0029761 | -0.01035 | 0.0011025 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059099 | 0.019831 | 0.05959 | -66.7473 | -0.016908 | -66.7414 | 56.2473 | 56.1426 | 56.2894 | -66.8467 | -66.7565 | -0.022535 | -66.791 | 56.1482 | 56.3076 | 56.1597 | -67.0424 | -0.10015 | -0.094293 | -0.000748 | 0.005094 | 0.10524 | -0.199 | -0.052184 | -0.29583 | -0.19337 | -0.010021 | -0.044526 | 0.25131 | -0.033929 | -0.18182 | 122.9938 | 122.8891 | 123.0359 | 66.7296 | -123.1882 | 122.8947 | 123.0541 | 122.9063 | 66.724 | -123.3839
886.7969 | 123.2025 | -66.7419 | 56.3278 | 0.0046549 | -0.010564 | 0.00088894 | 0.053936 | -0.0043822 | 0.06293 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059313 | 0.019404 | 0.05959 | -66.7473 | -0.012329 | -66.746 | 56.2473 | 56.1242 | 56.2802 | -66.8513 | -66.7657 | -0.022535 | -66.7956 | 56.1482 | 56.3122 | 56.1552 | -67.0561 | -0.10931 | -0.08056 | -0.005326 | -0.004062 | 0.10525 | -0.20358 | -0.047609 | -0.31415 | -0.17964 | -0.023756 | -0.053683 | 0.26046 | -0.015617 | -0.17267 | 122.9892 | 122.8662 | 123.0222 | 66.7296 | -123.1791 | 122.8901 | 123.0541 | 122.8971 | 66.7194 | -123.3839
887.8594 | 123.2666 | -66.7236 | 56.282 | -0.0029761 | -0.01035 | 0.0011025 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0017711 | -0.0011965 | 0.059313 | 0.020045 | 0.05959 | -66.7473 | -0.012329 | -66.7414 | 56.2473 | 56.1242 | 56.2894 | -66.8375 | -66.7565 | -0.027113 | -66.7865 | 56.1573 | 56.3076 | 56.1414 | -67.0469 | -0.11388 | -0.034783 | -0.023636 | -0.017794 | 0.096087 | -0.15781 | 0.007326 | -0.3233 | -0.1247 | -0.032909 | -0.062836 | 0.26046 | 0.025581 | -0.14062 | 122.9709 | 122.8479 | 123.013 | 66.7113 | -123.1196 | 122.881 | 123.0313 | 122.8651 | 66.6965 | -123.329
888.7969 | 123.1705 | -66.7374 | 56.3324 | -0.0029761 | -0.010564 | 0.0011025 | 0.054363 | -0.0041686 | 0.06293 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059099 | 0.019831 | 0.059376 | -66.7427 | -0.012329 | -66.7414 | 56.2427 | 56.1471 | 56.2894 | -66.8513 | -66.7565 | -0.027113 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0469 | -0.11389 | -0.089715 | -0.005325 | -0.004061 | 0.10982 | -0.18527 | -0.043028 | -0.30957 | -0.17964 | -0.019176 | -0.053681 | 0.25588 | -0.020194 | -0.1864 | 122.98 | 122.8845 | 123.0267 | 66.725 | -123.1836 | 122.8901 | 123.0496 | 122.8834 | 66.7103 | -123.3793
889.7969 | 123.2208 | -66.7099 | 56.3278 | 0.0046549 | -0.01035 | 0.0013163 | 0.054363 | -0.0043822 | 0.06293 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.020258 | 0.05959 | -66.7427 | -0.012329 | -66.7414 | 56.2473 | 56.138 | 56.2802 | -66.8375 | -66.7657 | -0.022535 | -66.7819 | 56.1528 | 56.3122 | 56.1597 | -67.0515 | -0.12761 | -0.08056 | -0.032791 | -0.031527 | 0.096087 | -0.18985 | -0.047609 | -0.34161 | -0.17506 | -0.055799 | -0.07199 | 0.26962 | -0.015617 | -0.16809 | 122.9572 | 122.8479 | 122.9901 | 66.6976 | -123.1653 | 122.8627 | 123.0221 | 122.8696 | 66.6874 | -123.3793
890.7969 | 123.1659 | -66.7465 | 56.3049 | -0.0029761 | -0.010564 | 0.0013163 | 0.053936 | -0.003955 | 0.062503 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059313 | 0.019831 | 0.05959 | -66.7381 | -0.016908 | -66.7414 | 56.2427 | 56.1288 | 56.3031 | -66.8467 | -66.7657 | -0.022535 | -66.7819 | 56.1573 | 56.3168 | 56.1506 | -67.0469 | -0.10015 | -0.06225 | 0.008409 | 0.005094 | 0.10524 | -0.17612 | -0.001828 | -0.30041 | -0.14759 | -0.019178 | -0.035369 | 0.26504 | 0.01185 | -0.15436 | 122.9892 | 122.8753 | 123.0496 | 66.7296 | -123.1516 | 122.9039 | 123.0633 | 122.8971 | 66.724 | -123.3519
891.7969 | 123.143 | -66.7465 | 56.3416 | 0.0046549 | -0.01035 | 0.0015299 | 0.054363 | -0.0043822 | 0.062717 | 0.015414 | -0.0015573 | -0.0011965 | 0.059099 | 0.020045 | 0.05959 | -66.7518 | -0.016908 | -66.7323 | 56.2518 | 56.1426 | 56.2894 | -66.8513 | -66.7611 | -0.017956 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0469 | -0.10473 | -0.089714 | -0.005326 | 0.014251 | 0.11898 | -0.199 | -0.052184 | -0.30041 | -0.18879 | -0.0146 | -0.044526 | 0.25588 | -0.02935 | -0.19556 | 122.9984 | 122.8891 | 123.0359 | 66.7296 | -123.1928 | 122.8993 | 123.0587 | 122.8925 | 66.7286 | -123.3885
892.8594 | 123.2574 | -66.7145 | 56.2729 | -0.0029761 | -0.010778 | 0.0017435 | 0.054577 | -0.003955 | 0.062717 | -0.0074779 | -0.0015573 | -0.00098273 | 0.059313 | 0.020045 | 0.05959 | -66.7427 | -0.016908 | -66.7368 | 56.2427 | 56.138 | 56.2894 | -66.8467 | -66.7611 | -0.027113 | -66.791 | 56.1528 | 56.3122 | 56.1552 | -67.0515 | -0.13219 | -0.030206 | -0.028213 | -0.02237 | 0.10982 | -0.13491 | 0.016481 | -0.33703 | -0.12013 | -0.046643 | -0.076569 | 0.26046 | 0.039315 | -0.11774 | 122.9572 | 122.8525 | 123.0038 | 66.6976 | -123.1196 | 122.8672 | 123.0267 | 122.8696 | 66.6874 | -123.3244
893.7969 | 123.1567 | -66.7236 | 56.3828 | 0.0046549 | -0.010564 | 0.0015299 | 0.053936 | -0.0041686 | 0.062717 | 0.00015261 | -0.0013437 | -0.00098273 | 0.059313 | 0.019831 | 0.059376 | -66.7473 | -0.016908 | -66.7414 | 56.2518 | 56.138 | 56.2939 | -66.8513 | -66.7565 | -0.017956 | -66.791 | 56.1482 | 56.3168 | 56.146 | -67.0561 | -0.12762 | -0.13091 | -0.023636 | -0.017794 | 0.10982 | -0.24478 | -0.088804 | -0.33246 | -0.23457 | -0.032909 | -0.067414 | 0.26504 | -0.065969 | -0.23676 | 122.9755 | 122.8616 | 123.0176 | 66.7067 | -123.234 | 122.8718 | 123.0404 | 122.8696 | 66.7057 | -123.4388
894.8594 | 123.3078 | -66.7007 | 56.3004 | -0.0029761 | -0.01035 | 0.0015299 | 0.054577 | -0.0041686 | 0.06293 | 0.0077831 | -0.0013437 | -0.0011965 | 0.059313 | 0.019831 | 0.05959 | -66.7518 | -0.012329 | -66.7414 | 56.2427 | 56.138 | 56.2894 | -66.8513 | -66.752 | -0.022535 | -66.7865 | 56.1573 | 56.3168 | 56.1506 | -67.0561 | -0.15051 | -0.057672 | -0.051102 | -0.040682 | 0.10982 | -0.16238 | -0.010985 | -0.35534 | -0.14301 | -0.051218 | -0.085724 | 0.26962 | 0.016428 | -0.14978 | 122.9434 | 122.8387 | 122.9901 | 66.6884 | -123.1516 | 122.8581 | 123.0175 | 122.8513 | 66.6782 | -123.3564
895.7969 | 123.1934 | -66.7328 | 56.337 | -0.0029761 | -0.010778 | 0.0011025 | 0.053936 | -0.0043822 | 0.062717 | 0.00015261 | -0.0017711 | -0.0011965 | 0.059099 | 0.019831 | 0.059804 | -66.7427 | -0.016908 | -66.7414 | 56.2473 | 56.138 | 56.2848 | -66.8467 | -66.752 | -0.022535 | -66.791 | 56.1482 | 56.303 | 56.1506 | -67.0469 | -0.11388 | -0.089715 | -0.009903 | -0.008639 | 0.10524 | -0.199 | -0.052185 | -0.31414 | -0.18879 | -0.019175 | -0.058259 | 0.25588 | -0.033929 | -0.1864 | 122.98 | 122.8708 | 123.0176 | 66.7159 | -123.1836 | 122.881 | 123.0358 | 122.8834 | 66.7103 | -123.3839
896.7969 | 123.2071 | -66.7419 | 56.337 | -0.010607 | -0.010564 | 0.0013163 | 0.053936 | -0.003955 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.020045 | 0.05959 | -66.7427 | -0.021486 | -66.7552 | 56.2473 | 56.1334 | 56.2894 | -66.8513 | -66.7565 | -0.022535 | -66.791 | 56.1528 | 56.3122 | 56.146 | -67.0469 | -0.10931 | -0.089715 | -0.000748 | -0.013218 | 0.09609 | -0.20358 | -0.047606 | -0.30499 | -0.18422 | -0.014599 | -0.049104 | 0.25588 | -0.024772 | -0.19098 | 122.9892 | 122.8753 | 123.0313 | 66.7205 | -123.1882 | 122.8947 | 123.0541 | 122.8879 | 66.7194 | -123.3839
897.8594 | 123.2895 | -66.7053 | 56.3095 | -0.0029761 | -0.010564 | 0.0011025 | 0.054149 | -0.0043822 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.019831 | 0.05959 | -66.7473 | -0.016908 | -66.7368 | 56.2427 | 56.138 | 56.2848 | -66.8421 | -66.752 | -0.017956 | -66.7956 | 56.1573 | 56.3076 | 56.1597 | -67.0469 | -0.13677 | -0.066827 | -0.041947 | -0.031526 | 0.10525 | -0.17153 | -0.024719 | -0.34161 | -0.15217 | -0.046641 | -0.090304 | 0.25131 | -0.001885 | -0.14978 | 122.948 | 122.8433 | 122.9901 | 66.6884 | -123.1516 | 122.8627 | 123.0129 | 122.8651 | 66.6874 | -123.3564
898.7969 | 123.1659 | -66.7694 | 56.3049 | -0.0029761 | -0.01035 | 0.0015299 | 0.053936 | -0.0041686 | 0.06293 | -0.0074779 | -0.0017711 | -0.0011965 | 0.059313 | 0.020045 | 0.059804 | -66.7427 | -0.021486 | -66.7414 | 56.2518 | 56.1288 | 56.2939 | -66.8513 | -66.7611 | -0.017956 | -66.791 | 56.1436 | 56.3076 | 56.1414 | -67.0469 | -0.081842 | -0.053093 | 0.026718 | 0.027982 | 0.10982 | -0.17612 | -0.010985 | -0.27752 | -0.16133 | 0.008288 | -0.021638 | 0.25588 | 0.002692 | -0.16351 | 123.0212 | 122.8982 | 123.0634 | 66.7479 | -123.1562 | 122.913 | 123.077 | 122.9108 | 66.7515 | -123.3519
899.7969 | 123.2117 | -66.7694 | 56.3278 | -0.010607 | -0.010564 | 0.0013163 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.020045 | 0.059804 | -66.7473 | -0.012329 | -66.7277 | 56.2564 | 56.1334 | 56.2939 | -66.8558 | -66.7474 | -0.022535 | -66.7865 | 56.1528 | 56.3122 | 56.146 | -67.0561 | -0.086421 | -0.071403 | 0.02214 | 0.041717 | 0.12814 | -0.19443 | -0.033873 | -0.28668 | -0.17506 | 0.022024 | -0.01706 | 0.26962 | -0.015617 | -0.18182 | 123.0258 | 122.9028 | 123.0634 | 66.7571 | -123.1837 | 122.9222 | 123.0816 | 122.9154 | 66.7469 | -123.3839
900.8594 | 123.1934 | -66.7419 | 56.3095 | 0.0046549 | -0.010991 | 0.0013163 | 0.053722 | -0.003955 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.059099 | 0.019831 | 0.059376 | -66.7427 | -0.016908 | -66.7414 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7611 | -0.022535 | -66.7865 | 56.1482 | 56.3168 | 56.1506 | -67.0515 | -0.10015 | -0.062249 | -0.000748 | 0.000516 | 0.10067 | -0.16696 | -0.010983 | -0.30957 | -0.16133 | -0.019178 | -0.044526 | 0.26504 | 0.007273 | -0.15893 | 122.9892 | 122.8845 | 123.0405 | 66.725 | -123.1516 | 122.8901 | 123.0587 | 122.8925 | 66.7194 | -123.361
901.7969 | 123.1934 | -66.7557 | 56.3049 | -0.0029761 | -0.010778 | 0.0011025 | 0.053936 | -0.0043822 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059313 | 0.020045 | 0.059804 | -66.7473 | -0.012329 | -66.7323 | 56.2564 | 56.1426 | 56.2985 | -66.8421 | -66.7611 | -0.031692 | -66.791 | 56.1573 | 56.3122 | 56.1414 | -67.0424 | -0.086417 | -0.048515 | 0.008407 | 0.023406 | 0.10982 | -0.16238 | -0.006406 | -0.28668 | -0.14759 | -0.005445 | -0.035371 | 0.25131 | 0.007271 | -0.16351 | 123.0121 | 122.8982 | 123.0542 | 66.7433 | -123.147 | 122.913 | 123.0679 | 122.8971 | 66.724 | -123.3473
902.7969 | 123.1613 | -66.7694 | 56.3141 | -0.0029761 | -0.01035 | 0.0011025 | 0.053936 | -0.0041686 | 0.062717 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059313 | 0.019831 | 0.05959 | -66.7427 | -0.012329 | -66.7323 | 56.2473 | 56.138 | 56.2894 | -66.8467 | -66.7611 | -0.027113 | -66.791 | 56.1482 | 56.3168 | 56.1506 | -67.0424 | -0.077263 | -0.066827 | 0.026718 | 0.037139 | 0.1144 | -0.17611 | -0.024718 | -0.27294 | -0.16591 | 0.008288 | -0.021638 | 0.25131 | 0.002695 | -0.16351 | 123.0167 | 122.9074 | 123.0588 | 66.7571 | -123.1608 | 122.9176 | 123.0862 | 122.92 | 66.7423 | -123.3564
903.7969 | 123.1705 | -66.7648 | 56.3095 | -0.010607 | -0.010778 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059099 | 0.020258 | 0.05959 | -66.7427 | -0.016908 | -66.7368 | 56.2518 | 56.138 | 56.2985 | -66.8558 | -66.752 | -0.022535 | -66.7956 | 56.1436 | 56.3076 | 56.146 | -67.0469 | -0.090998 | -0.05767 | 0.022141 | 0.027984 | 0.11898 | -0.17153 | -0.010983 | -0.2821 | -0.16591 | 0.012869 | -0.030794 | 0.25131 | -0.001885 | -0.16351 | 123.0167 | 122.9028 | 123.0634 | 66.7479 | -123.1653 | 122.9084 | 123.0725 | 122.9108 | 66.7423 | -123.3564
904.7969 | 123.23 | -66.7511 | 56.2729 | -0.0029761 | -0.01035 | 0.0011025 | 0.054149 | -0.0041686 | 0.062503 | -0.0074779 | -0.0011301 | -0.00098273 | 0.058886 | 0.020045 | 0.059163 | -66.7518 | -0.016908 | -66.7368 | 56.2473 | 56.1242 | 56.2939 | -66.8421 | -66.752 | -0.017956 | -66.7865 | 56.1528 | 56.3122 | 56.146 | -67.0515 | -0.090994 | -0.025628 | -0.000748 | 0.014251 | 0.10525 | -0.14865 | 0.021059 | -0.30041 | -0.12013 | -0.000864 | -0.03537 | 0.26504 | 0.039315 | -0.12689 | 122.9984 | 122.8753 | 123.045 | 66.7342 | -123.115 | 122.9039 | 123.0633 | 122.8971 | 66.7331 | -123.3244
905.8594 | 123.1888 | -66.7603 | 56.3278 | -0.010607 | -0.01035 | 0.0013163 | 0.053722 | -0.003955 | 0.062503 | 0.015414 | -0.0017711 | -0.00098273 | 0.059099 | 0.019831 | 0.059163 | -66.7473 | -0.016908 | -66.7323 | 56.2518 | 56.1426 | 56.2894 | -66.8513 | -66.7474 | -0.031692 | -66.8002 | 56.1573 | 56.3076 | 56.146 | -67.0469 | -0.090997 | -0.075981 | 0.012985 | 0.027984 | 0.11898 | -0.18527 | -0.038451 | -0.28668 | -0.17048 | 0.012869 | -0.039951 | 0.24673 | -0.020196 | -0.18182 | 123.0121 | 122.9028 | 123.0496 | 66.7433 | -123.1791 | 122.9176 | 123.0679 | 122.9062 | 66.7286 | -123.3748
906.7969 | 123.143 | -66.774 | 56.2866 | -0.0029761 | -0.010564 | 0.0011025 | 0.053508 | -0.0041686 | 0.062289 | -0.0074779 | -0.0013437 | -0.00098273 | 0.059099 | 0.020258 | 0.05959 | -66.7427 | -0.016908 | -66.7323 | 56.2473 | 56.1334 | 56.2939 | -66.8513 | -66.752 | -0.027113 | -66.7865 | 56.1528 | 56.3168 | 56.1597 | -67.0515 | -0.077264 | -0.039361 | 0.031296 | 0.041717 | 0.11898 | -0.15323 | 0.007326 | -0.27752 | -0.13386 | 0.022024 | -0.012482 | 0.26504 | 0.030161 | -0.12689 | 123.0212 | 122.9074 | 123.0679 | 66.7571 | -123.1379 | 122.9267 | 123.0908 | 122.9337 | 66.7469 | -123.3381
907.7969 | 123.1338 | -66.7923 | 56.3141 | -0.0029761 | -0.010564 | 0.0013163 | 0.053936 | -0.0041686 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.020045 | 0.059804 | -66.7427 | -0.016908 | -66.7368 | 56.2564 | 56.1288 | 56.2985 | -66.8558 | -66.7565 | -0.013377 | -66.791 | 56.1528 | 56.3076 | 56.1414 | -67.0515 | -0.063533 | -0.05767 | 0.049606 | 0.055449 | 0.11898 | -0.18527 | -0.015561 | -0.25921 | -0.16133 | 0.035755 | 0.00125 | 0.26046 | -0.006463 | -0.17267 | 123.0487 | 122.9211 | 123.0908 | 66.7754 | -123.1699 | 122.9451 | 123.0999 | 122.9337 | 66.7789 | -123.3656
908.7969 | 123.2941 | -66.7282 | 56.2683 | -0.018238 | -0.01035 | 0.0013163 | 0.053936 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.020045 | 0.05959 | -66.7427 | -0.021486 | -66.7414 | 56.2518 | 56.1242 | 56.2939 | -66.8467 | -66.7565 | -0.017956 | -66.7956 | 56.1528 | 56.3168 | 56.146 | -67.0469 | -0.11846 | -0.016472 | -0.014481 | -0.013217 | 0.10524 | -0.14407 | 0.025636 | -0.31872 | -0.11555 | -0.028332 | -0.067416 | 0.25131 | 0.048471 | -0.12232 | 122.98 | 122.8524 | 123.0222 | 66.7067 | -123.115 | 122.881 | 123.045 | 122.8742 | 66.7103 | -123.3152
909.7969 | 123.1659 | -66.774 | 56.3278 | 0.0046549 | -0.010991 | 0.0013163 | 0.054577 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059099 | 0.020258 | 0.05959 | -66.7473 | -0.016908 | -66.7368 | 56.2473 | 56.1334 | 56.2939 | -66.8421 | -66.7565 | -0.027113 | -66.7956 | 56.1528 | 56.3168 | 56.1506 | -67.0424 | -0.068106 | -0.08056 | 0.026718 | 0.037139 | 0.10525 | -0.19443 | -0.033873 | -0.26837 | -0.17506 | 0.017445 | -0.021639 | 0.24673 | -0.011038 | -0.17724 | 123.0212 | 122.9074 | 123.0679 | 66.7571 | -123.1699 | 122.9267 | 123.0908 | 122.9246 | 66.7469 | -123.3702
910.8594 | 123.23 | -66.7328 | 56.2454 | -0.010607 | -0.010564 | 0.0013163 | 0.054149 | -0.0041686 | 0.062289 | 0.00015261 | -0.0011301 | -0.00055553 | 0.058886 | 0.020258 | 0.059163 | -66.7518 | -0.016908 | -66.7323 | 56.2473 | 56.1288 | 56.2985 | -66.8558 | -66.752 | -0.027113 | -66.7819 | 56.1528 | 56.3168 | 56.1368 | -67.0469 | -0.12304 | 0.001838 | -0.019059 | 0.000518 | 0.12356 | -0.11661 | 0.053104 | -0.31414 | -0.092662 | -0.019175 | -0.049102 | 0.26504 | 0.07136 | -0.10858 | 122.98 | 122.8616 | 123.0313 | 66.7159 | -123.1013 | 122.8855 | 123.0496 | 122.8696 | 66.7057 | -123.2924
911.7969 | 123.1888 | -66.7328 | 56.2866 | -0.010607 | -0.010778 | 0.0013163 | 0.054363 | -0.0043822 | 0.062503 | -0.0074779 | -0.0011301 | -0.00076913 | 0.059099 | 0.020258 | 0.059376 | -66.7427 | -0.012329 | -66.7323 | 56.2564 | 56.138 | 56.2985 | -66.8467 | -66.7565 | -0.027113 | -66.7956 | 56.1528 | 56.3168 | 56.1597 | -67.0515 | -0.11388 | -0.030204 | -0.009903 | 0.000518 | 0.1144 | -0.14865 | 0.011905 | -0.31872 | -0.13386 | -0.023754 | -0.062838 | 0.25588 | 0.030161 | -0.12689 | 122.9892 | 122.8708 | 123.0313 | 66.7205 | -123.1333 | 122.8855 | 123.0496 | 122.8925 | 66.7057 | -123.3381
912.8594 | 123.2803 | -66.7053 | 56.2637 | -0.0029761 | -0.010778 | 0.0011025 | 0.054149 | -0.0041686 | 0.062717 | -0.015108 | -0.0013437 | -0.00098273 | 0.059099 | 0.020258 | 0.05959 | -66.7518 | -0.016908 | -66.7323 | 56.2473 | 56.1334 | 56.3031 | -66.8513 | -66.7474 | -0.022535 | -66.791 | 56.1482 | 56.3076 | 56.1552 | -67.0469 | -0.14593 | -0.016473 | -0.046525 | -0.026948 | 0.11898 | -0.13034 | 0.039371 | -0.34161 | -0.11555 | -0.042063 | -0.085725 | 0.25588 | 0.043891 | -0.10858 | 122.9526 | 122.8387 | 123.0084 | 66.6884 | -123.115 | 122.8535 | 123.0129 | 122.8605 | 66.6828 | -123.3107
913.7969 | 123.2574 | -66.7328 | 56.282 | -0.0029761 | -0.010564 | 0.0015299 | 0.053722 | -0.0041686 | 0.06293 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058886 | 0.020258 | 0.059376 | -66.7473 | -0.021486 | -66.7414 | 56.2473 | 56.1288 | 56.2894 | -66.8421 | -66.7565 | -0.022535 | -66.7956 | 56.1528 | 56.3168 | 56.1414 | -67.0515 | -0.10931 | -0.034783 | -0.014481 | -0.008639 | 0.10067 | -0.15323 | 0.007326 | -0.31872 | -0.12928 | -0.023754 | -0.062838 | 0.25588 | 0.034739 | -0.14062 | 122.98 | 122.8616 | 123.0222 | 66.7113 | -123.1241 | 122.8855 | 123.0496 | 122.8742 | 66.7103 | -123.3336
914.7969 | 123.2391 | -66.7145 | 56.3095 | -0.0029761 | -0.010778 | 0.0011025 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.0014101 | 0.059313 | 0.020045 | 0.059163 | -66.7427 | -0.007751 | -66.7368 | 56.2427 | 56.1426 | 56.2939 | -66.8467 | -66.7565 | -0.031692 | -66.791 | 56.1528 | 56.3168 | 56.1506 | -67.0469 | -0.13219 | -0.066827 | -0.028213 | -0.02237 | 0.10982 | -0.16696 | -0.015562 | -0.33245 | -0.15675 | -0.042064 | -0.076569 | 0.25588 | 0.007273 | -0.15893 | 122.9572 | 122.857 | 123.0084 | 66.7067 | -123.1562 | 122.8672 | 123.0313 | 122.8651 | 66.6828 | -123.3564
915.7969 | 123.2437 | -66.7099 | 56.282 | -0.0029761 | -0.010778 | 0.0013163 | 0.053936 | -0.0041686 | 0.062717 | -0.0074779 | -0.0015573 | -0.00098273 | 0.058886 | 0.020258 | 0.059804 | -66.7427 | -0.016908 | -66.7323 | 56.2518 | 56.1334 | 56.2939 | -66.8421 | -66.752 | -0.027113 | -66.7865 | 56.1528 | 56.3076 | 56.1506 | -67.0515 | -0.13219 | -0.030204 | -0.032791 | -0.02237 | 0.10982 | -0.14865 | 0.011904 | -0.34161 | -0.12928 | -0.042063 | -0.076569 | 0.26504 | 0.025581 | -0.13147 | 122.9617 | 122.8433 | 123.0038 | 66.693 | -123.1241 | 122.8627 | 123.0175 | 122.8605 | 66.6828 | -123.3336
916.8594 | 123.2346 | -66.7282 | 56.3004 | -0.0029761 | -0.010564 | 0.00088894 | 0.054149 | -0.0041686 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058886 | 0.020258 | 0.059376 | -66.7473 | -0.016908 | -66.7414 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7565 | -0.027113 | -66.7865 | 56.1528 | 56.3122 | 56.1414 | -67.0469 | -0.11388 | -0.053094 | -0.019059 | -0.013217 | 0.10067 | -0.1578 | -0.001828 | -0.31872 | -0.14759 | -0.028332 | -0.058259 | 0.26046 | 0.011849 | -0.15894 | 122.9755 | 122.8708 | 123.0267 | 66.7113 | -123.1424 | 122.881 | 123.0404 | 122.8696 | 66.7011 | -123.3473
917.7969 | 123.2712 | -66.7282 | 56.2729 | 0.0046549 | -0.010991 | 0.0015299 | 0.054149 | -0.0043822 | 0.062717 | 0.015414 | -0.0015573 | -0.00098273 | 0.059313 | 0.020258 | 0.05959 | -66.7427 | -0.026065 | -66.746 | 56.2473 | 56.1334 | 56.2894 | -66.8421 | -66.7565 | -0.022535 | -66.791 | 56.1528 | 56.3168 | 56.1368 | -67.0469 | -0.11388 | -0.025628 | -0.014481 | -0.017795 | 0.096088 | -0.13949 | 0.016481 | -0.31872 | -0.12013 | -0.028332 | -0.062837 | 0.25588 | 0.043894 | -0.13605 | 122.9755 | 122.8616 | 123.0176 | 66.7021 | -123.115 | 122.881 | 123.045 | 122.865 | 66.7057 | -123.3198
918.7969 | 123.2529 | -66.6962 | 56.2958 | -0.0029761 | -0.011205 | 0.0011025 | 0.053936 | -0.0043822 | 0.06293 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059313 | 0.020045 | 0.059376 | -66.7335 | -0.021486 | -66.7414 | 56.2473 | 56.138 | 56.2939 | -66.8467 | -66.7611 | -0.027113 | -66.791 | 56.1573 | 56.3168 | 56.1552 | -67.0469 | -0.1505 | -0.048516 | -0.037367 | -0.04526 | 0.10524 | -0.1578 | -0.001829 | -0.35076 | -0.13844 | -0.064954 | -0.09488 | 0.25588 | 0.021006 | -0.14062 | 122.9434 | 122.8341 | 122.9901 | 66.6747 | -123.1424 | 122.8535 | 123.0129 | 122.8513 | 66.6691 | -123.3427
919.7969 | 123.2483 | -66.7236 | 56.2958 | -0.010607 | -0.010564 | 0.0013163 | 0.054363 | -0.0041686 | 0.062503 | -0.0074779 | -0.0017711 | -0.0014101 | 0.058886 | 0.020258 | 0.05959 | -66.7427 | -0.016908 | -66.7368 | 56.2473 | 56.1334 | 56.2939 | -66.8375 | -66.7565 | -0.027113 | -66.7865 | 56.1482 | 56.3168 | 56.146 | -67.0515 | -0.11388 | -0.048516 | -0.019058 | -0.013215 | 0.10067 | -0.16238 | -0.001829 | -0.32788 | -0.14759 | -0.032909 | -0.062836 | 0.26504 | 0.021006 | -0.14978 | 122.9709 | 122.857 | 123.0176 | 66.7067 | -123.1333 | 122.8718 | 123.0404 | 122.8696 | 66.6965 | -123.3473
920.7969 | 123.2941 | -66.7053 | 56.2958 | 0.012286 | -0.011205 | 0.0011025 | 0.054149 | -0.0043822 | 0.063144 | 0.00015261 | -0.0017711 | -0.00076913 | 0.059099 | 0.020258 | 0.059163 | -66.7427 | -0.016908 | -66.7414 | 56.2473 | 56.138 | 56.3031 | -66.8467 | -66.7565 | -0.031692 | -66.791 | 56.1573 | 56.3122 | 56.146 | -67.0469 | -0.14135 | -0.048516 | -0.037369 | -0.036105 | 0.10524 | -0.1578 | 0.007328 | -0.34161 | -0.13844 | -0.05122 | -0.085725 | 0.25588 | 0.016427 | -0.14978 | 122.9526 | 122.8433 | 123.0084 | 66.6884 | -123.1424 | 122.8627 | 123.0175 | 122.8513 | 66.6736 | -123.3427
921.7969 | 123.23 | -66.7236 | 56.282 | -0.0029761 | -0.010778 | 0.0013163 | 0.054577 | -0.0041686 | 0.06293 | 0.00015261 | -0.0017711 | -0.00098273 | 0.059313 | 0.020258 | 0.05959 | -66.7473 | -0.021486 | -66.7323 | 56.2518 | 56.1426 | 56.2985 | -66.8513 | -66.7565 | -0.022535 | -66.791 | 56.1528 | 56.3168 | 56.1506 | -67.0469 | -0.12762 | -0.030204 | -0.023636 | -0.008637 | 0.11898 | -0.13949 | 0.016483 | -0.3233 | -0.12928 | -0.032909 | -0.067414 | 0.25588 | 0.034739 | -0.13147 | 122.9755 | 122.8662 | 123.0222 | 66.7021 | -123.1333 | 122.8764 | 123.0404 | 122.8742 | 66.7011 | -123.329
922.7969 | 123.3032 | -66.6779 | 56.3232 | 0.0046549 | -0.010778 | 0.0013163 | 0.054149 | -0.003955 | 0.062717 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058886 | 0.020258 | 0.059376 | -66.7381 | -0.021486 | -66.746 | 56.2473 | 56.1426 | 56.2939 | -66.8513 | -66.7565 | -0.027113 | -66.7956 | 56.1528 | 56.3076 | 56.1414 | -67.0469 | -0.17339 | -0.075982 | -0.060256 | -0.068149 | 0.10525 | -0.18069 | -0.029295 | -0.36908 | -0.17048 | -0.078686 | -0.11777 | 0.25131 | -0.015618 | -0.18182 | 122.9251 | 122.8204 | 122.9718 | 66.6564 | -123.1745 | 122.8306 | 122.9855 | 122.8193 | 66.6507 | -123.3702
923.7969 | 123.2483 | -66.7191 | 56.2866 | 0.0046549 | -0.011205 | 0.0011025 | 0.054577 | -0.0041686 | 0.06293 | -0.0074779 | -0.0015573 | -0.00098273 | 0.059099 | 0.020472 | 0.059376 | -66.7518 | -0.016908 | -66.7414 | 56.2564 | 56.1242 | 56.2894 | -66.8375 | -66.7565 | -0.027113 | -66.791 | 56.1482 | 56.3122 | 56.1414 | -67.0424 | -0.11846 | -0.030204 | -0.032792 | -0.022372 | 0.096087 | -0.16238 | 0.002748 | -0.3233 | -0.13844 | -0.037487 | -0.071992 | 0.25131 | 0.025582 | -0.1452 | 122.9755 | 122.8433 | 123.0084 | 66.7021 | -123.1241 | 122.8672 | 123.0313 | 122.8605 | 66.6919 | -123.329
924.8594 | 123.2941 | -66.7145 | 56.3141 | 0.0046549 | -0.011205 | 0.0013163 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.0011965 | 0.058886 | 0.020045 | 0.059163 | -66.7427 | -0.026065 | -66.746 | 56.2473 | 56.138 | 56.2985 | -66.8467 | -66.7611 | -0.027113 | -66.791 | 56.1528 | 56.3168 | 56.1597 | -67.0561 | -0.13219 | -0.066827 | -0.028213 | -0.031527 | 0.10067 | -0.17611 | -0.015561 | -0.34161 | -0.16133 | -0.046643 | -0.076569 | 0.26504 | 0.002695 | -0.15436 | 122.9617 | 122.8525 | 123.013 | 66.6884 | -123.1608 | 122.8672 | 123.0313 | 122.8742 | 66.6874 | -123.3702
925.7969 | 123.23 | -66.7053 | 56.337 | 0.0046549 | -0.010564 | 0.0013163 | 0.054363 | -0.0041686 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.020258 | 0.059376 | -66.7473 | -0.021486 | -66.7414 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7474 | -0.031692 | -66.791 | 56.1619 | 56.3259 | 56.1506 | -67.0424 | -0.13677 | -0.089715 | -0.041947 | -0.036105 | 0.10067 | -0.19442 | -0.038449 | -0.33703 | -0.17506 | -0.042063 | -0.085725 | 0.25131 | -0.011036 | -0.1864 | 122.9526 | 122.8479 | 123.0038 | 66.6838 | -123.1791 | 122.8672 | 123.0313 | 122.8559 | 66.6736 | -123.3793
926.7969 | 123.2803 | -66.7191 | 56.2729 | -0.010607 | -0.010778 | 0.00067514 | 0.053936 | -0.0041686 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059313 | 0.020472 | 0.059376 | -66.7381 | -0.016908 | -66.7414 | 56.2473 | 56.1334 | 56.2939 | -66.8421 | -66.7565 | -0.022535 | -66.791 | 56.1619 | 56.3214 | 56.1597 | -67.0515 | -0.12304 | -0.025628 | -0.019057 | -0.022372 | 0.10067 | -0.13949 | 0.021059 | -0.33245 | -0.11097 | -0.037487 | -0.071992 | 0.26046 | 0.048472 | -0.11316 | 122.9663 | 122.8525 | 123.013 | 66.7021 | -123.115 | 122.881 | 123.0404 | 122.8788 | 66.6965 | -123.3244
927.7969 | 123.2712 | -66.7145 | 56.3278 | -0.0029761 | -0.010991 | 0.00088894 | 0.054363 | -0.0043822 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.020472 | 0.059376 | -66.7473 | -0.016908 | -66.7368 | 56.2473 | 56.1426 | 56.2939 | -66.8513 | -66.752 | -0.027113 | -66.791 | 56.1573 | 56.3214 | 56.1643 | -67.0424 | -0.13677 | -0.08056 | -0.032791 | -0.02237 | 0.1144 | -0.18527 | -0.033873 | -0.32788 | -0.17048 | -0.037485 | -0.076569 | 0.25131 | -0.00646 | -0.16351 | 122.9617 | 122.857 | 123.0084 | 66.6976 | -123.1791 | 122.8718 | 123.0358 | 122.8788 | 66.6874 | -123.3702
928.7969 | 123.2758 | -66.6824 | 56.2912 | 0.0046549 | -0.011419 | 0.00088894 | 0.054363 | -0.0043822 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058672 | 0.020686 | 0.059376 | -66.7427 | -0.021486 | -66.746 | 56.2427 | 56.1334 | 56.2985 | -66.8467 | -66.7565 | -0.031692 | -66.791 | 56.1573 | 56.3214 | 56.1689 | -67.0469 | -0.16424 | -0.048517 | -0.060257 | -0.063571 | 0.10067 | -0.1578 | 0.007327 | -0.3645 | -0.13386 | -0.074108 | -0.10861 | 0.25588 | 0.030161 | -0.12231 | 122.9251 | 122.8158 | 122.981 | 66.6609 | -123.1379 | 122.8398 | 123.0038 | 122.8513 | 66.6507 | -123.3381
929.7969 | 123.2391 | -66.7145 | 56.2775 | -0.0029761 | -0.010991 | 0.0015299 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.020472 | 0.05959 | -66.7518 | -0.016908 | -66.7552 | 56.2518 | 56.1288 | 56.2939 | -66.8421 | -66.7565 | -0.031692 | -66.7956 | 56.1528 | 56.3259 | 56.1643 | -67.0515 | -0.12762 | -0.025627 | -0.037369 | -0.040683 | 0.086932 | -0.14865 | 0.016481 | -0.33703 | -0.12471 | -0.042064 | -0.081148 | 0.25588 | 0.048473 | -0.11315 | 122.9663 | 122.8433 | 123.0084 | 66.6976 | -123.1196 | 122.8672 | 123.0404 | 122.8788 | 66.6828 | -123.329
930.7969 | 123.1522 | -66.7603 | 56.3461 | 0.012286 | -0.011205 | 0.0013163 | 0.053936 | -0.0043822 | 0.06293 | 0.00015261 | -0.0013437 | -0.00055553 | 0.058886 | 0.020472 | 0.059376 | -66.7427 | -0.016908 | -66.7368 | 56.2427 | 56.1426 | 56.2985 | -66.8467 | -66.7565 | -0.022535 | -66.7865 | 56.1528 | 56.3259 | 56.1552 | -67.0469 | -0.086418 | -0.10345 | 0.017563 | 0.023406 | 0.10982 | -0.20358 | -0.047604 | -0.28668 | -0.19337 | 0.003712 | -0.026215 | 0.26046 | -0.020191 | -0.19098 | 123.0029 | 122.9028 | 123.0588 | 66.7433 | -123.1928 | 122.913 | 123.0862 | 122.9154 | 66.7377 | -123.3931
931.7969 | 123.2803 | -66.7099 | 56.3095 | 0.0046549 | -0.011205 | 0.0011025 | 0.054363 | -0.0041686 | 0.06293 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059099 | 0.020686 | 0.059376 | -66.7564 | -0.021486 | -66.7368 | 56.2518 | 56.1426 | 56.2894 | -66.8375 | -66.7611 | -0.027113 | -66.7865 | 56.1528 | 56.3168 | 56.1506 | -67.0561 | -0.12761 | -0.05767 | -0.046526 | -0.026948 | 0.10067 | -0.16696 | -0.02014 | -0.34619 | -0.15675 | -0.051221 | -0.076569 | 0.26962 | 0.007273 | -0.15893 | 122.9617 | 122.8525 | 122.9993 | 66.6884 | -123.147 | 122.8627 | 123.0267 | 122.8605 | 66.6828 | -123.3656
932.7969 | 123.2483 | -66.6962 | 56.3232 | 0.012286 | -0.010991 | 0.00088894 | 0.054149 | -0.0041686 | 0.06293 | 0.0077831 | -0.0015573 | -0.0011965 | 0.059313 | 0.020258 | 0.059376 | -66.7427 | -0.021486 | -66.746 | 56.2427 | 56.1426 | 56.2939 | -66.8421 | -66.7565 | -0.031692 | -66.7865 | 56.1528 | 56.3168 | 56.146 | -67.0424 | -0.14593 | -0.08056 | -0.046524 | -0.049838 | 0.096088 | -0.18069 | -0.029295 | -0.34619 | -0.17048 | -0.060375 | -0.090302 | 0.25588 | -0.00646 | -0.17725 | 122.9388 | 122.8387 | 122.9901 | 66.6747 | -123.1653 | 122.8489 | 123.0129 | 122.8422 | 66.6645 | -123.3656
933.8594 | 123.2117 | -66.7145 | 56.2958 | -0.0029761 | -0.011205 | 0.00067514 | 0.054577 | -0.0043822 | 0.063144 | -0.0074779 | -0.0013437 | -0.00098273 | 0.058886 | 0.020899 | 0.05959 | -66.7473 | -0.012329 | -66.746 | 56.2427 | 56.1426 | 56.3031 | -66.8421 | -66.7474 | -0.027113 | -66.791 | 56.1528 | 56.3168 | 56.1552 | -67.0469 | -0.12762 | -0.053094 | -0.032791 | -0.031527 | 0.096088 | -0.15322 | 0.007328 | -0.33245 | -0.14302 | -0.032907 | -0.076569 | 0.25588 | 0.021006 | -0.14062 | 122.9572 | 122.857 | 123.0176 | 66.7021 | -123.1379 | 122.8672 | 123.0313 | 122.8696 | 66.6874 | -123.3427
934.7969 | 123.2529 | -66.7145 | 56.3049 | -0.010607 | -0.011419 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.023044 | -0.0017711 | -0.0011965 | 0.059313 | 0.020472 | 0.059376 | -66.7381 | -0.021486 | -66.746 | 56.2473 | 56.1426 | 56.3031 | -66.8467 | -66.7611 | -0.027113 | -66.7865 | 56.1528 | 56.3168 | 56.1643 | -67.0424 | -0.13219 | -0.057672 | -0.023634 | -0.031527 | 0.10067 | -0.16238 | -0.001828 | -0.32788 | -0.15217 | -0.046643 | -0.071991 | 0.25588 | 0.01185 | -0.14062 | 122.9617 | 122.857 | 123.0176 | 66.693 | -123.1516 | 122.8672 | 123.0313 | 122.8788 | 66.6874 | -123.3473
935.7969 | 123.2803 | -66.7053 | 56.3141 | 0.0046549 | -0.011205 | 0.0013163 | 0.054149 | -0.004596 | 0.062717 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059527 | 0.020472 | 0.059804 | -66.7473 | -0.021486 | -66.7414 | 56.2518 | 56.138 | 56.2985 | -66.8329 | -66.7611 | -0.022535 | -66.7819 | 56.1573 | 56.3214 | 56.1552 | -67.0515 | -0.12761 | -0.062248 | -0.041947 | -0.036105 | 0.091508 | -0.17611 | -0.015561 | -0.34619 | -0.15675 | -0.055799 | -0.076568 | 0.26962 | 0.007273 | -0.15893 | 122.9572 | 122.8433 | 123.0038 | 66.6838 | -123.147 | 122.8627 | 123.0267 | 122.8605 | 66.6828 | -123.3656
936.7969 | 123.1934 | -66.7282 | 56.3187 | 0.0046549 | -0.011419 | 0.0011025 | 0.053936 | -0.004596 | 0.06293 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058886 | 0.020686 | 0.05959 | -66.7427 | -0.026065 | -66.746 | 56.2518 | 56.1471 | 56.2985 | -66.8467 | -66.7565 | -0.027113 | -66.7865 | 56.1573 | 56.3214 | 56.1552 | -67.0515 | -0.11846 | -0.066826 | -0.014481 | -0.017795 | 0.10067 | -0.17153 | -0.020139 | -0.3233 | -0.16133 | -0.028332 | -0.058259 | 0.26504 | 0.002695 | -0.16351 | 122.98 | 122.8753 | 123.0267 | 66.7021 | -123.1653 | 122.8855 | 123.0496 | 122.8834 | 66.7011 | -123.3702
937.7969 | 123.2712 | -66.7236 | 56.2775 | -0.0029761 | -0.010778 | 0.0013163 | 0.054149 | -0.0043822 | 0.06293 | -0.0074779 | -0.0015573 | -0.00076913 | 0.058672 | 0.020258 | 0.05959 | -66.7381 | -0.021486 | -66.7414 | 56.2427 | 56.138 | 56.2939 | -66.8467 | -66.752 | -0.022535 | -66.7819 | 56.1573 | 56.3168 | 56.146 | -67.0515 | -0.12304 | -0.034784 | -0.014479 | -0.017794 | 0.10524 | -0.13949 | 0.016481 | -0.32788 | -0.12013 | -0.02833 | -0.058257 | 0.26962 | 0.039316 | -0.13147 | 122.9663 | 122.8616 | 123.0176 | 66.7021 | -123.1241 | 122.881 | 123.0404 | 122.8696 | 66.7011 | -123.329
938.7969 | 123.2208 | -66.7191 | 56.3416 | 0.0046549 | -0.011419 | 0.0013163 | 0.054363 | -0.003955 | 0.06293 | 0.015414 | -0.0019847 | -0.00098273 | 0.059099 | 0.020472 | 0.059376 | -66.7427 | -0.021486 | -66.7368 | 56.2473 | 56.1288 | 56.2894 | -66.8467 | -66.7565 | -0.031692 | -66.7865 | 56.1528 | 56.3214 | 56.146 | -67.0515 | -0.12762 | -0.094293 | -0.023636 | -0.017793 | 0.10982 | -0.21274 | -0.052184 | -0.33245 | -0.18879 | -0.037487 | -0.067414 | 0.26504 | -0.020193 | -0.19556 | 122.9663 | 122.8479 | 123.0084 | 66.6976 | -123.1882 | 122.8718 | 123.0404 | 122.8651 | 66.6874 | -123.3931
939.7969 | 123.2758 | -66.7053 | 56.2866 | 0.0046549 | -0.011419 | 0.0011025 | 0.053722 | -0.0041686 | 0.06293 | 0.015414 | -0.0017711 | -0.0011965 | 0.058886 | 0.020686 | 0.05959 | -66.7473 | -0.021486 | -66.7506 | 56.2518 | 56.138 | 56.2894 | -66.8375 | -66.752 | -0.031692 | -66.791 | 56.1573 | 56.3214 | 56.1506 | -67.0515 | -0.13219 | -0.034782 | -0.041947 | -0.045261 | 0.086931 | -0.14865 | 0.002748 | -0.34619 | -0.12928 | -0.046641 | -0.085725 | 0.26046 | 0.034739 | -0.13605 | 122.9572 | 122.8433 | 122.9947 | 66.6838 | -123.1241 | 122.8627 | 123.0267 | 122.8559 | 66.6736 | -123.3381
940.8594 | 123.2574 | -66.7282 | 56.2775 | 0.0046549 | -0.011205 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0017711 | -0.0014101 | 0.059313 | 0.020472 | 0.059376 | -66.7473 | -0.030644 | -66.7506 | 56.2427 | 56.1334 | 56.2985 | -66.8513 | -66.7474 | -0.027113 | -66.791 | 56.1573 | 56.3259 | 56.1552 | -67.0469 | -0.12304 | -0.034784 | -0.019059 | -0.022373 | 0.10067 | -0.14407 | 0.02106 | -0.31872 | -0.12013 | -0.019175 | -0.062837 | 0.25588 | 0.048473 | -0.12231 | 122.9709 | 122.8616 | 123.0267 | 66.6976 | -123.1287 | 122.8855 | 123.0541 | 122.8834 | 66.7011 | -123.3244
941.7969 | 123.1888 | -66.7191 | 56.3095 | 0.0046549 | -0.011419 | 0.00088894 | 0.054149 | -0.0043822 | 0.062717 | 0.0077831 | -0.0013437 | -0.00098273 | 0.059527 | 0.020258 | 0.059163 | -66.7473 | -0.021486 | -66.746 | 56.2518 | 56.1426 | 56.3031 | -66.8467 | -66.7565 | -0.031692 | -66.7819 | 56.1528 | 56.3214 | 56.1414 | -67.0515 | -0.12762 | -0.05767 | -0.028214 | -0.02695 | 0.10067 | -0.16696 | -0.006405 | -0.33245 | -0.15675 | -0.037487 | -0.062835 | 0.26962 | 0.011851 | -0.16809 | 122.9709 | 122.8616 | 123.0222 | 66.6976 | -123.1562 | 122.8718 | 123.0404 | 122.8605 | 66.6874 | -123.361
942.8594 | 123.2208 | -66.7419 | 56.2683 | 0.0046549 | -0.010991 | 0.00088894 | 0.054363 | -0.003955 | 0.062717 | -0.0074779 | -0.0015573 | -0.00098273 | 0.059099 | 0.020686 | 0.059163 | -66.7427 | -0.021486 | -66.7414 | 56.2427 | 56.138 | 56.2939 | -66.8421 | -66.752 | -0.022535 | -66.7865 | 56.1528 | 56.3122 | 56.1506 | -67.0561 | -0.10015 | -0.025629 | -0.000748 | 0.000516 | 0.10067 | -0.13034 | 0.025636 | -0.31415 | -0.11555 | -0.01002 | -0.044526 | 0.26962 | 0.043892 | -0.11774 | 122.9846 | 122.8799 | 123.0359 | 66.7205 | -123.1104 | 122.8947 | 123.0541 | 122.8925 | 66.7194 | -123.3244
943.7969 | 123.2391 | -66.7145 | 56.2958 | 0.0046549 | -0.011419 | 0.0013163 | 0.054149 | -0.0041686 | 0.063144 | 0.015414 | -0.0013437 | -0.00098273 | 0.059099 | 0.020899 | 0.059163 | -66.7381 | -0.026065 | -66.746 | 56.2518 | 56.138 | 56.2939 | -66.8421 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3168 | 56.1506 | -67.0469 | -0.12762 | -0.043937 | -0.023634 | -0.031527 | 0.096088 | -0.1578 | -0.001829 | -0.33245 | -0.13844 | -0.037485 | -0.071991 | 0.26046 | 0.021006 | -0.1452 | 122.9663 | 122.8525 | 123.0084 | 66.6884 | -123.1379 | 122.8718 | 123.0313 | 122.8651 | 66.6782 | -123.3427
944.7969 | 123.2162 | -66.7191 | 56.3461 | 0.0046549 | -0.011205 | 0.0011025 | 0.054149 | -0.0043822 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.020686 | 0.059376 | -66.7427 | -0.021486 | -66.7506 | 56.2473 | 56.1471 | 56.3031 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1482 | 56.3122 | 56.1552 | -67.0469 | -0.1322 | -0.09887 | -0.023636 | -0.031528 | 0.10067 | -0.199 | -0.043026 | -0.32788 | -0.19795 | -0.032908 | -0.067414 | 0.26046 | -0.033927 | -0.19098 | 122.9663 | 122.8662 | 123.0222 | 66.6976 | -123.1974 | 122.8672 | 123.0313 | 122.8742 | 66.6874 | -123.3931
945.8594 | 123.2712 | -66.7145 | 56.2958 | -0.0029761 | -0.011205 | 0.00088894 | 0.054577 | -0.0041686 | 0.062717 | 0.023044 | -0.0015573 | -0.00076913 | 0.059099 | 0.020686 | 0.059376 | -66.7427 | -0.021486 | -66.7368 | 56.2427 | 56.1426 | 56.2985 | -66.8467 | -66.7611 | -0.031692 | -66.791 | 56.1619 | 56.3122 | 56.1597 | -67.0515 | -0.13219 | -0.053094 | -0.028213 | -0.02237 | 0.10982 | -0.15322 | 0.00275 | -0.33703 | -0.13386 | -0.046643 | -0.076569 | 0.26046 | 0.016427 | -0.13604 | 122.9572 | 122.857 | 123.013 | 66.693 | -123.1424 | 122.8764 | 123.0267 | 122.8742 | 66.6828 | -123.3473
946.7969 | 123.1934 | -66.7557 | 56.3187 | 0.0046549 | -0.011419 | 0.0013163 | 0.053936 | -0.0043822 | 0.06293 | 0.015414 | -0.0019847 | -0.0014101 | 0.059099 | 0.020686 | 0.05959 | -66.7427 | -0.016908 | -66.746 | 56.2518 | 56.138 | 56.3031 | -66.8467 | -66.7565 | -0.022535 | -66.7819 | 56.1528 | 56.3168 | 56.1506 | -67.0424 | -0.090996 | -0.066826 | 0.012985 | 0.009671 | 0.10067 | -0.18069 | -0.015561 | -0.28668 | -0.16591 | -0.000866 | -0.026214 | 0.26046 | -0.001883 | -0.16809 | 123.0075 | 122.8936 | 123.0588 | 66.7388 | -123.1653 | 122.9084 | 123.0725 | 122.9063 | 66.7331 | -123.361
947.8594 | 123.2117 | -66.7374 | 56.2912 | -0.0029761 | -0.011205 | 0.00088894 | 0.054149 | -0.004596 | 0.062717 | -0.0074779 | -0.0011301 | -0.00098273 | 0.058886 | 0.020686 | 0.059376 | -66.7427 | -0.026065 | -66.7414 | 56.2427 | 56.1471 | 56.3031 | -66.8604 | -66.7611 | -0.036271 | -66.791 | 56.1528 | 56.3076 | 56.146 | -67.0469 | -0.12304 | -0.048517 | -0.005325 | -0.004061 | 0.11898 | -0.14407 | 0.011905 | -0.30957 | -0.13844 | -0.023755 | -0.053681 | 0.25588 | 0.016425 | -0.1452 | 122.98 | 122.8845 | 123.0405 | 66.7113 | -123.1516 | 122.8901 | 123.045 | 122.8834 | 66.7011 | -123.3381
948.7969 | 123.2117 | -66.7236 | 56.3416 | 0.0046549 | -0.011205 | 0.00088894 | 0.053722 | -0.0041686 | 0.063144 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059099 | 0.021113 | 0.059376 | -66.7427 | -0.026065 | -66.746 | 56.2473 | 56.1426 | 56.3031 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1482 | 56.3168 | 56.1597 | -67.0515 | -0.12762 | -0.094293 | -0.019058 | -0.022372 | 0.10525 | -0.199 | -0.038449 | -0.32788 | -0.19337 | -0.02833 | -0.062836 | 0.26504 | -0.024771 | -0.18182 | 122.9709 | 122.8662 | 123.0267 | 66.6976 | -123.1928 | 122.8718 | 123.0404 | 122.8834 | 66.6919 | -123.3931
949.7969 | 123.2666 | -66.6916 | 56.3004 | 0.012286 | -0.011632 | 0.0013163 | 0.054149 | -0.0041686 | 0.062717 | 0.015414 | -0.0019847 | -0.00098273 | 0.058886 | 0.020899 | 0.059376 | -66.7473 | -0.030644 | -66.7414 | 56.2518 | 56.138 | 56.2985 | -66.8329 | -66.7565 | -0.031692 | -66.7865 | 56.1528 | 56.3168 | 56.1552 | -67.0561 | -0.14135 | -0.048515 | -0.05568 | -0.049838 | 0.091508 | -0.16238 | -0.001828 | -0.3645 | -0.14759 | -0.064953 | -0.09488 | 0.26962 | 0.016428 | -0.1452 | 122.9434 | 122.8296 | 122.9901 | 66.6609 | -123.1333 | 122.8443 | 123.0084 | 122.8467 | 66.6599 | -123.3564
950.7969 | 123.2071 | -66.7419 | 56.337 | 0.012286 | -0.011419 | 0.0011025 | 0.053722 | -0.0043822 | 0.062717 | 0.015414 | -0.0019847 | -0.00076913 | 0.059099 | 0.020472 | 0.059376 | -66.7381 | -0.021486 | -66.7506 | 56.2564 | 56.1426 | 56.2985 | -66.8558 | -66.7565 | -0.027113 | -66.7773 | 56.1482 | 56.3168 | 56.146 | -67.0515 | -0.11389 | -0.080558 | 0.003831 | -0.00864 | 0.10525 | -0.19442 | -0.038449 | -0.30957 | -0.18879 | -0.014599 | -0.035368 | 0.2742 | -0.020193 | -0.19098 | 122.9984 | 122.8845 | 123.0405 | 66.7205 | -123.1928 | 122.8901 | 123.0587 | 122.8879 | 66.7148 | -123.3885
951.875 | 123.1567 | -66.7786 | 56.2683 | -0.010607 | -0.011632 | 0.0011025 | 0.054149 | -0.0043822 | 0.062717 | -0.0074779 | -0.0015573 | -0.00098273 | 0.059099 | 0.020899 | 0.059376 | -66.7427 | -0.016908 | -66.746 | 56.2518 | 56.1288 | 56.2985 | -66.8467 | -66.7428 | -0.027113 | -66.791 | 56.1573 | 56.3214 | 56.1506 | -67.0561 | -0.068108 | -0.016472 | 0.035873 | 0.032559 | 0.10067 | -0.13949 | 0.030215 | -0.27752 | -0.11097 | 0.035758 | -0.012483 | 0.26504 | 0.053049 | -0.11774 | 123.0304 | 122.9074 | 123.0771 | 66.7617 | -123.115 | 122.9359 | 123.0999 | 122.9291 | 66.7515 | -123.3244
952.7969 | 123.1934 | -66.7557 | 56.3278 | 0.012286 | -0.011419 | 0.0013163 | 0.053936 | -0.0041686 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.020472 | 0.059376 | -66.7427 | -0.021486 | -66.746 | 56.2473 | 56.138 | 56.3031 | -66.8558 | -66.7657 | -0.027113 | -66.7819 | 56.1482 | 56.3168 | 56.1643 | -67.0469 | -0.10015 | -0.08056 | 0.012985 | 0.009671 | 0.10983 | -0.18985 | -0.024716 | -0.29126 | -0.17964 | -0.010023 | -0.026214 | 0.26504 | -0.011038 | -0.16351 | 123.0029 | 122.8936 | 123.0588 | 66.7342 | -123.1837 | 122.9039 | 123.0725 | 122.92 | 66.7286 | -123.3748
953.7969 | 123.2483 | -66.7007 | 56.3095 | 0.0046549 | -0.011632 | 0.0013163 | 0.054149 | -0.004596 | 0.063144 | 0.00015261 | -0.0017711 | -0.0011965 | 0.059099 | 0.020686 | 0.059163 | -66.7473 | -0.021486 | -66.746 | 56.2518 | 56.1334 | 56.3077 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1528 | 56.3122 | 56.1552 | -67.0424 | -0.15051 | -0.05767 | -0.046524 | -0.04526 | 0.10525 | -0.17611 | -0.001826 | -0.34161 | -0.15675 | -0.051218 | -0.085724 | 0.25588 | 0.002694 | -0.15436 | 122.9526 | 122.8341 | 123.0084 | 66.6793 | -123.1608 | 122.8535 | 123.0129 | 122.8559 | 66.6691 | -123.3519
954.7969 | 123.1934 | -66.7557 | 56.3187 | 0.0046549 | -0.011846 | 0.0013163 | 0.053936 | -0.0043822 | 0.063144 | 0.0077831 | -0.0015573 | -0.00055553 | 0.058886 | 0.020899 | 0.058949 | -66.7381 | -0.030644 | -66.7506 | 56.2473 | 56.1426 | 56.3031 | -66.8421 | -66.7565 | -0.031692 | -66.791 | 56.1573 | 56.3168 | 56.1643 | -67.0515 | -0.086417 | -0.071405 | 0.017564 | 0.005093 | 0.09151 | -0.17611 | -0.015561 | -0.29583 | -0.16133 | -0.000866 | -0.035371 | 0.26046 | -0.001883 | -0.15435 | 123.0029 | 122.8982 | 123.0588 | 66.725 | -123.1608 | 122.913 | 123.0725 | 122.92 | 66.724 | -123.3702
955.7969 | 123.1842 | -66.7374 | 56.3324 | 0.0046549 | -0.011419 | 0.00088894 | 0.054363 | -0.0050232 | 0.06293 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058886 | 0.020686 | 0.059804 | -66.7427 | -0.026065 | -66.7414 | 56.2473 | 56.1426 | 56.3077 | -66.8467 | -66.7565 | -0.027113 | -66.7819 | 56.1482 | 56.3168 | 56.1506 | -67.0424 | -0.10931 | -0.085137 | -0.005325 | -0.004061 | 0.10524 | -0.18984 | -0.024714 | -0.30499 | -0.18422 | -0.019176 | -0.044524 | 0.26046 | -0.015615 | -0.18182 | 122.9846 | 122.8799 | 123.045 | 66.7113 | -123.1791 | 122.8855 | 123.0541 | 122.8879 | 66.7103 | -123.3748
956.7969 | 123.2391 | -66.7099 | 56.2866 | 0.0046549 | -0.011632 | 0.0011025 | 0.054363 | -0.0043822 | 0.063144 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.020686 | 0.059376 | -66.7473 | -0.016908 | -66.7414 | 56.2473 | 56.1426 | 56.2985 | -66.8467 | -66.752 | -0.031692 | -66.7956 | 56.1482 | 56.3168 | 56.1368 | -67.0561 | -0.13677 | -0.039361 | -0.037369 | -0.031527 | 0.10524 | -0.14407 | 0.011905 | -0.34619 | -0.13844 | -0.042063 | -0.085726 | 0.26046 | 0.030161 | -0.14978 | 122.9572 | 122.8525 | 123.0084 | 66.693 | -123.1333 | 122.8581 | 123.0267 | 122.8467 | 66.6782 | -123.3427
957.7969 | 123.2208 | -66.7191 | 56.3049 | 0.012286 | -0.011632 | 0.0011025 | 0.054363 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058672 | 0.021113 | 0.05959 | -66.7473 | -0.030644 | -66.7368 | 56.2473 | 56.1426 | 56.2939 | -66.8467 | -66.752 | -0.031692 | -66.791 | 56.1573 | 56.3122 | 56.1689 | -67.0561 | -0.12762 | -0.057672 | -0.028214 | -0.017793 | 0.10982 | -0.16238 | -0.010985 | -0.33703 | -0.14759 | -0.032908 | -0.071992 | 0.26504 | 0.007271 | -0.13604 | 122.9663 | 122.8616 | 123.013 | 66.6884 | -123.1516 | 122.8764 | 123.0313 | 122.8879 | 66.6874 | -123.361
958.7969 | 123.2071 | -66.7419 | 56.3324 | -0.0029761 | -0.011419 | 0.00088894 | 0.053936 | -0.0043822 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.021327 | 0.05959 | -66.7427 | -0.021486 | -66.7552 | 56.2564 | 56.1426 | 56.3031 | -66.8467 | -66.752 | -0.031692 | -66.7865 | 56.1573 | 56.3214 | 56.1643 | -67.0561 | -0.10473 | -0.07598 | -0.000748 | -0.013218 | 0.091511 | -0.18984 | -0.029293 | -0.31415 | -0.17506 | -0.01002 | -0.044526 | 0.26962 | -0.011037 | -0.16809 | 122.9984 | 122.8845 | 123.045 | 66.7205 | -123.1791 | 122.8993 | 123.0633 | 122.9063 | 66.7103 | -123.3885
959.8438 | 123.2758 | -66.7374 | 56.2866 | 0.0046549 | -0.011419 | 0.0015299 | 0.054149 | -0.0041686 | 0.062503 | 0.015414 | -0.0015573 | -0.0011965 | 0.058886 | 0.020686 | 0.059376 | -66.7473 | -0.016908 | -66.7552 | 56.2473 | 56.1334 | 56.3031 | -66.8467 | -66.7611 | -0.031692 | -66.7819 | 56.1619 | 56.3168 | 56.1506 | -67.0515 | -0.10931 | -0.039361 | -0.009903 | -0.017795 | 0.091511 | -0.15323 | 0.016483 | -0.31414 | -0.1247 | -0.023755 | -0.044524 | 0.26962 | 0.030161 | -0.13605 | 122.9846 | 122.8708 | 123.0405 | 66.7205 | -123.1333 | 122.8993 | 123.0541 | 122.8879 | 66.7057 | -123.3381
960.7969 | 123.1705 | -66.7648 | 56.2912 | 0.0046549 | -0.011632 | 0.0013163 | 0.053936 | -0.004596 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058886 | 0.020686 | 0.059376 | -66.7335 | -0.016908 | -66.746 | 56.2518 | 56.1334 | 56.3077 | -66.8467 | -66.752 | -0.031692 | -66.7865 | 56.1528 | 56.3122 | 56.1643 | -67.0515 | -0.08184 | -0.03936 | 0.031298 | 0.018827 | 0.10067 | -0.1578 | 0.016484 | -0.28668 | -0.13844 | 0.012869 | -0.021637 | 0.26504 | 0.021004 | -0.12689 | 123.0167 | 122.8982 | 123.0725 | 66.7479 | -123.1379 | 122.9176 | 123.077 | 122.9291 | 66.7331 | -123.3427
961.7969 | 123.143 | -66.7648 | 56.3461 | -0.0029761 | -0.011632 | 0.0013163 | 0.054149 | -0.004596 | 0.062503 | 0.015414 | -0.0015573 | -0.0011965 | 0.058886 | 0.020899 | 0.059376 | -66.7381 | -0.021486 | -66.7552 | 56.2564 | 56.1471 | 56.2985 | -66.8467 | -66.752 | -0.031692 | -66.7865 | 56.1573 | 56.3122 | 56.1689 | -67.0515 | -0.08184 | -0.089713 | 0.02672 | 0.009671 | 0.091511 | -0.199 | -0.047604 | -0.28668 | -0.18879 | 0.012869 | -0.021637 | 0.26504 | -0.033927 | -0.17724 | 123.0212 | 122.912 | 123.0634 | 66.7433 | -123.1928 | 122.9222 | 123.077 | 122.9337 | 66.7331 | -123.3976
962.7969 | 123.143 | -66.7557 | 56.3278 | -0.0029761 | -0.011419 | 0.0013163 | 0.054149 | -0.004596 | 0.06293 | 0.00015261 | -0.0015573 | -0.0011965 | 0.059099 | 0.020899 | 0.059163 | -66.7473 | -0.021486 | -66.746 | 56.2518 | 56.1426 | 56.3031 | -66.8513 | -66.7565 | -0.031692 | -66.7956 | 56.1573 | 56.3168 | 56.1643 | -67.0515 | -0.095575 | -0.075981 | 0.008407 | 0.009671 | 0.10525 | -0.18527 | -0.024716 | -0.29583 | -0.17048 | -0.000866 | -0.03995 | 0.25588 | -0.011038 | -0.16351 | 123.0075 | 122.8982 | 123.0588 | 66.7342 | -123.1791 | 122.913 | 123.0725 | 122.92 | 66.724 | -123.3793
963.7969 | 123.1888 | -66.7465 | 56.3416 | -0.0029761 | -0.011419 | 0.0013163 | 0.053722 | -0.0043822 | 0.062717 | 0.0077831 | -0.0017711 | -0.0011965 | 0.059099 | 0.020899 | 0.059376 | -66.7427 | -0.021486 | -66.7414 | 56.2518 | 56.1471 | 56.3031 | -66.8558 | -66.7565 | -0.027113 | -66.7865 | 56.1573 | 56.3122 | 56.146 | -67.0607 | -0.10931 | -0.089714 | 0.00383 | 0.005094 | 0.1144 | -0.19442 | -0.038449 | -0.31415 | -0.18421 | -0.010021 | -0.039948 | 0.2742 | -0.02935 | -0.19556 | 122.9984 | 122.8937 | 123.0496 | 66.725 | -123.1974 | 122.9039 | 123.0587 | 122.8925 | 66.7194 | -123.4022
964.7969 | 123.2254 | -66.7603 | 56.3141 | -0.0029761 | -0.011419 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059313 | 0.020899 | 0.059376 | -66.7335 | -0.021486 | -66.746 | 56.2473 | 56.1426 | 56.3031 | -66.8513 | -66.7611 | -0.031692 | -66.7819 | 56.1528 | 56.3076 | 56.1368 | -67.0515 | -0.090997 | -0.066827 | 0.02672 | 0.014249 | 0.10525 | -0.17153 | -0.010983 | -0.29126 | -0.16133 | -0.000867 | -0.021636 | 0.26962 | -0.006463 | -0.17725 | 123.0075 | 122.9028 | 123.0634 | 66.7388 | -123.1653 | 122.913 | 123.0679 | 122.8971 | 66.7286 | -123.3656
965.8594 | 123.1705 | -66.7328 | 56.3141 | 0.0046549 | -0.011846 | 0.0011025 | 0.053936 | -0.004596 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059313 | 0.020899 | 0.05959 | -66.7427 | -0.021486 | -66.7277 | 56.2518 | 56.1334 | 56.3077 | -66.8421 | -66.752 | -0.027113 | -66.7865 | 56.1573 | 56.3214 | 56.1506 | -67.0515 | -0.10931 | -0.062248 | -0.009903 | 0.005096 | 0.1144 | -0.18069 | -0.006404 | -0.31872 | -0.15675 | -0.019175 | -0.053681 | 0.26504 | 0.007273 | -0.16351 | 122.9846 | 122.8662 | 123.0405 | 66.7113 | -123.1562 | 122.8901 | 123.0541 | 122.8834 | 66.7057 | -123.3656
966.7969 | 123.1934 | -66.7374 | 56.3141 | -0.010607 | -0.011419 | 0.00088894 | 0.053936 | -0.0043822 | 0.062717 | -0.0074779 | -0.0013437 | -0.00098273 | 0.058886 | 0.021113 | 0.059376 | -66.7427 | -0.026065 | -66.7414 | 56.2564 | 56.1334 | 56.2985 | -66.8558 | -66.752 | -0.036271 | -66.791 | 56.1573 | 56.3168 | 56.1414 | -67.0515 | -0.11846 | -0.05767 | -0.005325 | -0.004061 | 0.1144 | -0.18069 | -0.015561 | -0.31414 | -0.15675 | -0.014597 | -0.053681 | 0.26046 | 0.002695 | -0.17267 | 122.9938 | 122.8708 | 123.0359 | 66.7113 | -123.1699 | 122.8947 | 123.0541 | 122.8788 | 66.7011 | -123.3656
967.8594 | 123.1842 | -66.7145 | 56.3278 | 0.0046549 | -0.011419 | 0.0011025 | 0.054149 | -0.004596 | 0.062289 | 0.0077831 | -0.0017711 | -0.0011965 | 0.059099 | 0.020899 | 0.058949 | -66.7473 | -0.021486 | -66.7323 | 56.2518 | 56.1471 | 56.3077 | -66.8513 | -66.7565 | -0.027113 | -66.7865 | 56.1573 | 56.3122 | 56.1368 | -67.0469 | -0.13677 | -0.075981 | -0.032791 | -0.017792 | 0.11898 | -0.18069 | -0.020137 | -0.33245 | -0.17048 | -0.042064 | -0.071991 | 0.26046 | -0.015617 | -0.19098 | 122.9663 | 122.8616 | 123.0222 | 66.693 | -123.1791 | 122.8718 | 123.0267 | 122.8513 | 66.6874 | -123.3748
968.7969 | 123.1705 | -66.7374 | 56.3141 | -0.010607 | -0.011419 | 0.0011025 | 0.053936 | -0.003955 | 0.062717 | -0.0074779 | -0.0017711 | -0.0011965 | 0.059099 | 0.020472 | 0.059163 | -66.7381 | -0.021486 | -66.7323 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7474 | -0.031692 | -66.7865 | 56.1573 | 56.3122 | 56.1552 | -67.0561 | -0.10473 | -0.066827 | -0.000746 | 0.005096 | 0.10982 | -0.17153 | -0.015561 | -0.31872 | -0.15675 | -0.010019 | -0.049103 | 0.26962 | -0.001884 | -0.15893 | 122.9846 | 122.8799 | 123.0359 | 66.7159 | -123.1562 | 122.8947 | 123.0496 | 122.8925 | 66.7057 | -123.3702
969.8594 | 123.1934 | -66.7328 | 56.3004 | -0.0029761 | -0.011632 | 0.00088894 | 0.053936 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058672 | 0.020686 | 0.059376 | -66.7473 | -0.021486 | -66.7323 | 56.2473 | 56.1426 | 56.3077 | -66.8558 | -66.752 | -0.027113 | -66.791 | 56.1528 | 56.3076 | 56.1597 | -67.0515 | -0.12304 | -0.053094 | -0.014481 | 0.000518 | 0.12356 | -0.1578 | 0.007329 | -0.31872 | -0.14759 | -0.019175 | -0.058259 | 0.26046 | 0.00727 | -0.14062 | 122.98 | 122.8753 | 123.0405 | 66.7113 | -123.1562 | 122.8855 | 123.0404 | 122.8925 | 66.7057 | -123.3519
970.7969 | 123.23 | -66.7557 | 56.2958 | -0.010607 | -0.011419 | 0.0011025 | 0.054363 | -0.0041686 | 0.062503 | 0.00015261 | -0.0019847 | -0.00055553 | 0.059099 | 0.020899 | 0.059376 | -66.7427 | -0.026065 | -66.7277 | 56.2427 | 56.1288 | 56.2985 | -66.8467 | -66.7382 | -0.031692 | -66.7865 | 56.1573 | 56.3168 | 56.146 | -67.0469 | -0.090996 | -0.053094 | 0.012985 | 0.027984 | 0.11898 | -0.16696 | 0.00275 | -0.29126 | -0.13844 | 0.017449 | -0.030793 | 0.26046 | 0.021006 | -0.14978 | 122.9984 | 122.8845 | 123.0542 | 66.7296 | -123.1424 | 122.913 | 123.0725 | 122.9017 | 66.724 | -123.3427
971.7969 | 123.2117 | -66.7236 | 56.3141 | -0.0029761 | -0.011205 | 0.00088894 | 0.053722 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00055553 | 0.058886 | 0.021327 | 0.059376 | -66.7335 | -0.021486 | -66.7368 | 56.2518 | 56.138 | 56.3077 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1528 | 56.3122 | 56.1368 | -67.0515 | -0.12762 | -0.062248 | -0.009901 | -0.013215 | 0.1144 | -0.17611 | -0.006404 | -0.32788 | -0.16133 | -0.02833 | -0.062836 | 0.26504 | -0.001884 | -0.17725 | 122.9755 | 122.8616 | 123.0313 | 66.7021 | -123.1653 | 122.8764 | 123.0358 | 122.8605 | 66.6919 | -123.3656
972.7969 | 123.2117 | -66.7465 | 56.3049 | -0.010607 | -0.011632 | 0.0013163 | 0.053508 | -0.0048096 | 0.062717 | -0.0074779 | -0.0017711 | -0.00055553 | 0.059099 | 0.020686 | 0.059376 | -66.7335 | -0.030644 | -66.7414 | 56.2564 | 56.138 | 56.3077 | -66.8467 | -66.752 | -0.036271 | -66.7819 | 56.1528 | 56.3168 | 56.1552 | -67.0469 | -0.10015 | -0.048515 | 0.012987 | 0.005094 | 0.10524 | -0.16696 | 0.002751 | -0.30041 | -0.15217 | -0.005442 | -0.035369 | 0.26504 | 0.01185 | -0.14978 | 123.0029 | 122.8845 | 123.0542 | 66.7159 | -123.1516 | 122.8993 | 123.0633 | 122.9017 | 66.7103 | -123.3519
973.7969 | 123.1613 | -66.7603 | 56.3095 | -0.0029761 | -0.011205 | 0.00088894 | 0.054363 | -0.003955 | 0.062717 | -0.0074779 | -0.0019847 | -0.00055553 | 0.058672 | 0.021327 | 0.059376 | -66.7381 | -0.030644 | -66.7323 | 56.2518 | 56.138 | 56.3031 | -66.8604 | -66.7657 | -0.031692 | -66.7819 | 56.1528 | 56.3168 | 56.1414 | -67.0515 | -0.10015 | -0.05767 | 0.022142 | 0.027984 | 0.12814 | -0.17153 | -0.006405 | -0.29126 | -0.15675 | -0.005445 | -0.021636 | 0.26962 | 0.007273 | -0.16809 | 123.0121 | 122.8982 | 123.0634 | 66.7296 | -123.1699 | 122.913 | 123.077 | 122.9017 | 66.7286 | -123.361
974.7969 | 123.2666 | -66.7419 | 56.25 | -0.010607 | -0.011205 | 0.00067514 | 0.054149 | -0.004596 | 0.062503 | -0.015108 | -0.0013437 | -0.00076913 | 0.058672 | 0.020686 | 0.059376 | -66.7335 | -0.030644 | -66.7323 | 56.2564 | 56.1288 | 56.3031 | -66.8421 | -66.7611 | -0.031692 | -66.7865 | 56.1619 | 56.3214 | 56.1506 | -67.0515 | -0.10015 | 0.006417 | 0.008409 | 0.009673 | 0.10982 | -0.12118 | 0.053104 | -0.30957 | -0.088083 | -0.019178 | -0.044526 | 0.26504 | 0.07136 | -0.099425 | 122.9984 | 122.8708 | 123.045 | 66.7113 | -123.0921 | 122.9039 | 123.0633 | 122.8925 | 66.7103 | -123.3015
975.8594 | 123.1842 | -66.7557 | 56.3232 | 0.0046549 | -0.011419 | 0.0011025 | 0.054149 | -0.0043822 | 0.062717 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058886 | 0.020899 | 0.059376 | -66.7381 | -0.026065 | -66.7277 | 56.2427 | 56.1471 | 56.3031 | -66.8467 | -66.752 | -0.027113 | -66.7819 | 56.1573 | 56.3214 | 56.1597 | -67.0515 | -0.090996 | -0.08056 | 0.017564 | 0.027984 | 0.11898 | -0.17611 | -0.020138 | -0.29583 | -0.1659 | 0.003713 | -0.026214 | 0.26962 | -0.001882 | -0.16351 | 122.9984 | 122.9028 | 123.0588 | 66.7296 | -123.1699 | 122.913 | 123.077 | 122.9154 | 66.7286 | -123.3748
976.7969 | 123.2666 | -66.7282 | 56.2775 | -0.0029761 | -0.011205 | 0.0011025 | 0.053936 | -0.0043822 | 0.062289 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.020899 | 0.058949 | -66.7381 | -0.026065 | -66.7277 | 56.2473 | 56.1288 | 56.3077 | -66.8421 | -66.7474 | -0.031692 | -66.7865 | 56.1573 | 56.3168 | 56.1643 | -67.0561 | -0.11388 | -0.030206 | -0.009902 | 0.000518 | 0.1144 | -0.14865 | 0.030217 | -0.32788 | -0.12013 | -0.019175 | -0.058259 | 0.26962 | 0.039316 | -0.11315 | 122.9755 | 122.857 | 123.0359 | 66.7021 | -123.1196 | 122.8855 | 123.045 | 122.8925 | 66.6965 | -123.3336
977.8594 | 123.1979 | -66.7328 | 56.3187 | 0.0046549 | -0.011419 | 0.0011025 | 0.053936 | -0.0043822 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058458 | 0.021113 | 0.059163 | -66.7473 | -0.030644 | -66.7323 | 56.2518 | 56.1288 | 56.3031 | -66.8467 | -66.752 | -0.027113 | -66.791 | 56.1573 | 56.3168 | 56.1597 | -67.0561 | -0.11388 | -0.066826 | -0.014481 | 0.000518 | 0.1144 | -0.18985 | -0.015561 | -0.3233 | -0.16133 | -0.019175 | -0.058259 | 0.26504 | -0.001883 | -0.15893 | 122.9846 | 122.8616 | 123.0359 | 66.7021 | -123.1653 | 122.8901 | 123.0496 | 122.8925 | 66.7057 | -123.3748
978.7969 | 123.2437 | -66.7465 | 56.2637 | -0.010607 | -0.011419 | 0.0011025 | 0.053722 | -0.0043822 | 0.062503 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.021113 | 0.059376 | -66.7381 | -0.021486 | -66.7368 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7474 | -0.036271 | -66.7865 | 56.1573 | 56.3259 | 56.1414 | -67.0515 | -0.095572 | -0.016473 | 0.008409 | 0.009673 | 0.10525 | -0.12118 | 0.034793 | -0.30499 | -0.10639 | -0.000864 | -0.039948 | 0.26504 | 0.062206 | -0.12232 | 122.9938 | 122.8891 | 123.045 | 66.725 | -123.1058 | 122.9039 | 123.0725 | 122.8879 | 66.7103 | -123.3152
979.8594 | 123.1796 | -66.7831 | 56.3141 | -0.018238 | -0.011632 | 0.0011025 | 0.053936 | -0.0043822 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.020899 | 0.059163 | -66.7427 | -0.030644 | -66.7368 | 56.2473 | 56.1334 | 56.3031 | -66.8513 | -66.752 | -0.027113 | -66.7819 | 56.1573 | 56.3122 | 56.1597 | -67.0515 | -0.068109 | -0.066827 | 0.040451 | 0.046294 | 0.1144 | -0.18069 | -0.010983 | -0.26837 | -0.15675 | 0.031179 | 0.001252 | 0.26962 | -0.001884 | -0.15436 | 123.0304 | 122.9165 | 123.0862 | 66.7525 | -123.1653 | 122.9405 | 123.0953 | 122.9429 | 66.756 | -123.3656
980.7969 | 123.2529 | -66.7145 | 56.2866 | -0.0029761 | -0.011632 | 0.0015299 | 0.054149 | -0.0043822 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.020686 | 0.059163 | -66.7427 | -0.026065 | -66.7368 | 56.2518 | 56.1288 | 56.3031 | -66.8375 | -66.7565 | -0.031692 | -66.791 | 56.1573 | 56.3214 | 56.1552 | -67.0561 | -0.12304 | -0.034782 | -0.028213 | -0.02237 | 0.10067 | -0.1578 | 0.016483 | -0.34161 | -0.12928 | -0.042064 | -0.076569 | 0.26504 | 0.034739 | -0.13147 | 122.9663 | 122.8433 | 123.0176 | 66.6884 | -123.1241 | 122.8718 | 123.0358 | 122.8696 | 66.6828 | -123.3427
981.8594 | 123.1888 | -66.7191 | 56.3278 | -0.0029761 | -0.011632 | 0.0011025 | 0.053722 | -0.0043822 | 0.062503 | 0.0077831 | -0.0013437 | -0.0011965 | 0.058886 | 0.021327 | 0.059163 | -66.7381 | -0.026065 | -66.7506 | 56.2473 | 56.1471 | 56.3031 | -66.8467 | -66.7474 | -0.027113 | -66.7819 | 56.1528 | 56.3214 | 56.1689 | -67.0607 | -0.12762 | -0.08056 | -0.019057 | -0.031528 | 0.096089 | -0.18069 | -0.024716 | -0.34161 | -0.17506 | -0.02833 | -0.062835 | 0.27878 | -0.00646 | -0.15893 | 122.9663 | 122.8662 | 123.0222 | 66.693 | -123.1745 | 122.8718 | 123.0404 | 122.8879 | 66.6919 | -123.3885
982.7969 | 123.23 | -66.7191 | 56.2866 | 0.012286 | -0.011846 | 0.0011025 | 0.054149 | -0.004596 | 0.062503 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059099 | 0.021327 | 0.058949 | -66.7427 | -0.030644 | -66.746 | 56.2473 | 56.138 | 56.2985 | -66.8467 | -66.752 | -0.031692 | -66.7865 | 56.1482 | 56.3122 | 56.1414 | -67.0561 | -0.12762 | -0.039361 | -0.023636 | -0.02695 | 0.10067 | -0.14865 | 0.011905 | -0.33703 | -0.13844 | -0.032908 | -0.067414 | 0.26962 | 0.025582 | -0.1452 | 122.9663 | 122.857 | 123.0176 | 66.6884 | -123.1333 | 122.8672 | 123.0313 | 122.8605 | 66.6874 | -123.3427
983.7969 | 123.23 | -66.7557 | 56.3187 | -0.018238 | -0.011846 | 0.0011025 | 0.053722 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.0011965 | 0.058672 | 0.020899 | 0.058949 | -66.7473 | -0.021486 | -66.7414 | 56.2427 | 56.1471 | 56.3077 | -66.8513 | -66.752 | -0.036271 | -66.7819 | 56.1528 | 56.3168 | 56.146 | -67.0561 | -0.095575 | -0.075983 | 0.008407 | 0.014249 | 0.10982 | -0.17153 | -0.010982 | -0.30041 | -0.16591 | 0.003713 | -0.026214 | 0.2742 | -0.001883 | -0.17267 | 122.9984 | 122.9028 | 123.0634 | 66.7342 | -123.1699 | 122.9084 | 123.0725 | 122.9017 | 66.7194 | -123.3748
984.8594 | 123.3124 | -66.7053 | 56.2637 | 0.0046549 | -0.011632 | 0.00088894 | 0.053936 | -0.0041686 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.059313 | 0.021113 | 0.058949 | -66.7473 | -0.026065 | -66.7368 | 56.2473 | 56.1426 | 56.3031 | -66.8421 | -66.752 | -0.036271 | -66.7819 | 56.1573 | 56.3168 | 56.146 | -67.0469 | -0.13677 | -0.016473 | -0.041947 | -0.031526 | 0.10525 | -0.12118 | 0.039371 | -0.34161 | -0.10639 | -0.046641 | -0.076568 | 0.26504 | 0.053049 | -0.11774 | 122.9526 | 122.8479 | 123.0084 | 66.6793 | -123.1058 | 122.8627 | 123.0221 | 122.8513 | 66.6691 | -123.3107
985.8125 | 123.1522 | -66.7694 | 56.3095 | 0.0046549 | -0.01206 | 0.0011025 | 0.054149 | -0.0041686 | 0.062503 | -0.015108 | -0.0017711 | -0.00076913 | 0.059099 | 0.021327 | 0.059376 | -66.7427 | -0.030644 | -66.7368 | 56.2518 | 56.1426 | 56.3031 | -66.8421 | -66.7611 | -0.031692 | -66.7865 | 56.1573 | 56.3259 | 56.1552 | -67.0515 | -0.072684 | -0.05767 | 0.026718 | 0.032561 | 0.10525 | -0.16696 | -0.006405 | -0.2821 | -0.15217 | 0.008288 | -0.01706 | 0.26504 | 0.01643 | -0.15436 | 123.0212 | 122.912 | 123.0725 | 66.7388 | -123.1516 | 122.9267 | 123.0953 | 122.9246 | 66.7377 | -123.361
986.7969 | 123.2483 | -66.7282 | 56.282 | -0.010607 | -0.011632 | 0.0015299 | 0.054363 | -0.0043822 | 0.062289 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.021327 | 0.059163 | -66.7427 | -0.026065 | -66.7368 | 56.2473 | 56.1426 | 56.2985 | -66.8513 | -66.752 | -0.031692 | -66.791 | 56.1619 | 56.3214 | 56.146 | -67.0515 | -0.12304 | -0.034783 | -0.014481 | -0.008638 | 0.1144 | -0.13949 | 0.016483 | -0.3233 | -0.12013 | -0.023753 | -0.062837 | 0.26046 | 0.039317 | -0.13605 | 122.9755 | 122.8708 | 123.0267 | 66.7021 | -123.1333 | 122.8901 | 123.0496 | 122.8742 | 66.6965 | -123.3336
987.8594 | 123.1201 | -66.774 | 56.3049 | 0.0046549 | -0.011419 | 0.0013163 | 0.053936 | -0.0043822 | 0.06293 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058672 | 0.020899 | 0.059163 | -66.7335 | -0.030644 | -66.7368 | 56.2518 | 56.1426 | 56.2985 | -66.8513 | -66.752 | -0.031692 | -66.791 | 56.1573 | 56.3168 | 56.146 | -67.0424 | -0.077264 | -0.053093 | 0.040453 | 0.037139 | 0.1144 | -0.16238 | -0.006406 | -0.26837 | -0.14759 | 0.022024 | -0.01706 | 0.25131 | 0.01185 | -0.15894 | 123.0258 | 122.9165 | 123.0725 | 66.7433 | -123.1562 | 122.9313 | 123.0908 | 122.92 | 66.7423 | -123.3473
988.7969 | 123.2391 | -66.7053 | 56.2866 | 0.0046549 | -0.011846 | 0.0011025 | 0.054149 | -0.0048096 | 0.062717 | 0.00015261 | -0.0013437 | -0.00076913 | 0.059099 | 0.02154 | 0.058949 | -66.7473 | -0.030644 | -66.746 | 56.2473 | 56.1517 | 56.3077 | -66.8513 | -66.7474 | -0.031692 | -66.7865 | 56.1573 | 56.3214 | 56.1552 | -67.0515 | -0.14593 | -0.039361 | -0.041947 | -0.040683 | 0.10525 | -0.13491 | 0.021062 | -0.34619 | -0.12928 | -0.042063 | -0.081147 | 0.26504 | 0.034739 | -0.13147 | 122.9526 | 122.857 | 123.013 | 66.6747 | -123.1379 | 122.8627 | 123.0267 | 122.8605 | 66.6736 | -123.3381
989.7969 | 123.2895 | -66.7191 | 56.2271 | -0.010607 | -0.01206 | 0.0015299 | 0.053936 | -0.004596 | 0.062717 | -0.0074779 | -0.0017711 | -0.00076913 | 0.058672 | 0.021113 | 0.058949 | -66.7381 | -0.026065 | -66.746 | 56.2427 | 56.138 | 56.2985 | -66.8513 | -66.752 | -0.036271 | -66.7865 | 56.1528 | 56.3168 | 56.1643 | -67.0515 | -0.1322 | 0.01557 | -0.019057 | -0.02695 | 0.10525 | -0.089138 | 0.071414 | -0.33245 | -0.074352 | -0.032908 | -0.067414 | 0.26504 | 0.08967 | -0.062801 | 122.9617 | 122.857 | 123.0176 | 66.693 | -123.0784 | 122.8718 | 123.0358 | 122.8834 | 66.6828 | -123.2786
990.7969 | 123.2849 | -66.6687 | 56.282 | 0.0046549 | -0.011846 | 0.0011025 | 0.053936 | -0.004596 | 0.062503 | 0.015414 | -0.0017711 | -0.00076913 | 0.058672 | 0.021327 | 0.058949 | -66.7427 | -0.030644 | -66.7368 | 56.2473 | 56.1426 | 56.3031 | -66.8467 | -66.752 | -0.036271 | -66.7773 | 56.1573 | 56.3259 | 56.1552 | -67.0561 | -0.17797 | -0.034783 | -0.07399 | -0.068147 | 0.10982 | -0.13949 | 0.021061 | -0.38739 | -0.1247 | -0.083262 | -0.10861 | 0.27878 | 0.043896 | -0.12689 | 122.916 | 122.8113 | 122.9718 | 66.6381 | -123.1287 | 122.826 | 122.9946 | 122.8239 | 66.6324 | -123.3381
991.7969 | 123.2437 | -66.7007 | 56.2729 | 0.0046549 | -0.01206 | 0.0011025 | 0.054149 | -0.0043822 | 0.062289 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059313 | 0.02154 | 0.059163 | -66.7335 | -0.026065 | -66.746 | 56.2518 | 56.138 | 56.2985 | -66.8467 | -66.752 | -0.036271 | -66.7865 | 56.1619 | 56.3214 | 56.1506 | -67.0561 | -0.14593 | -0.021049 | -0.032789 | -0.04526 | 0.10067 | -0.13491 | 0.025638 | -0.35534 | -0.11097 | -0.051218 | -0.085724 | 0.26962 | 0.048472 | -0.12231 | 122.9526 | 122.8387 | 122.9993 | 66.6747 | -123.1196 | 122.8627 | 123.0221 | 122.8513 | 66.6645 | -123.329
992.7969 | 123.2574 | -66.7053 | 56.3095 | -0.0029761 | -0.01206 | 0.00067514 | 0.054149 | -0.0043822 | 0.062503 | 0.0077831 | -0.0015573 | -0.00076913 | 0.059099 | 0.02154 | 0.058949 | -66.7381 | -0.026065 | -66.7414 | 56.2427 | 56.1426 | 56.2939 | -66.8558 | -66.7474 | -0.050007 | -66.791 | 56.1573 | 56.3122 | 56.1506 | -67.0515 | -0.15051 | -0.066827 | -0.03279 | -0.036105 | 0.1144 | -0.16696 | -0.015562 | -0.34619 | -0.15217 | -0.042063 | -0.085725 | 0.26046 | 0.002694 | -0.15893 | 122.948 | 122.8479 | 122.9993 | 66.6793 | -123.1653 | 122.8627 | 123.0175 | 122.8559 | 66.6553 | -123.361
993.8594 | 123.262 | -66.7053 | 56.2729 | -0.0029761 | -0.011846 | 0.0013163 | 0.054149 | -0.004596 | 0.062717 | -0.0074779 | -0.0015573 | -0.00076913 | 0.058672 | 0.021327 | 0.059376 | -66.7381 | -0.021486 | -66.7368 | 56.2473 | 56.1426 | 56.2985 | -66.8513 | -66.752 | -0.036271 | -66.7819 | 56.1528 | 56.3214 | 56.1597 | -67.0561 | -0.14593 | -0.025628 | -0.03279 | -0.031526 | 0.1144 | -0.13034 | 0.025638 | -0.35077 | -0.12013 | -0.046641 | -0.076568 | 0.2742 | 0.048472 | -0.11316 | 122.9526 | 122.8479 | 123.0038 | 66.6838 | -123.1241 | 122.8581 | 123.0267 | 122.8651 | 66.6691 | -123.329
994.7969 | 123.2666 | -66.7282 | 56.282 | -0.0029761 | -0.011846 | 0.00088894 | 0.054149 | -0.0041686 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058672 | 0.021327 | 0.059163 | -66.729 | -0.030644 | -66.7368 | 56.2473 | 56.138 | 56.3031 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1619 | 56.3214 | 56.1552 | -67.0561 | -0.12304 | -0.034783 | -0.000746 | -0.008638 | 0.1144 | -0.14407 | 0.021061 | -0.32788 | -0.12013 | -0.023753 | -0.058259 | 0.26962 | 0.039317 | -0.12689 | 122.9755 | 122.8662 | 123.0313 | 66.6976 | -123.1333 | 122.8901 | 123.0496 | 122.8834 | 66.6965 | -123.3381
995.8594 | 123.2254 | -66.7236 | 56.282 | -0.0029761 | -0.011632 | 0.0011025 | 0.054149 | -0.0048096 | 0.062503 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.021113 | 0.059376 | -66.7427 | -0.026065 | -66.7506 | 56.2473 | 56.1426 | 56.2985 | -66.8513 | -66.7611 | -0.036271 | -66.7819 | 56.1573 | 56.3168 | 56.1506 | -67.0515 | -0.12762 | -0.034783 | -0.019058 | -0.02695 | 0.10067 | -0.13949 | 0.016483 | -0.32788 | -0.1247 | -0.037488 | -0.058257 | 0.26962 | 0.034739 | -0.13147 | 122.9709 | 122.8662 | 123.0222 | 66.6976 | -123.1333 | 122.881 | 123.0404 | 122.8742 | 66.6874 | -123.3336
996.7969 | 123.2895 | -66.7007 | 56.3004 | 0.0046549 | -0.011846 | 0.0013163 | 0.054149 | -0.0043822 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058886 | 0.02154 | 0.059376 | -66.7335 | -0.030644 | -66.746 | 56.2518 | 56.1334 | 56.3077 | -66.8467 | -66.7657 | -0.036271 | -66.7865 | 56.1619 | 56.3168 | 56.1506 | -67.0515 | -0.14593 | -0.048515 | -0.032789 | -0.04526 | 0.10067 | -0.16696 | 0.007329 | -0.35076 | -0.13844 | -0.064954 | -0.085724 | 0.26504 | 0.016428 | -0.14978 | 122.9526 | 122.8341 | 123.0084 | 66.6701 | -123.147 | 122.8627 | 123.0175 | 122.8513 | 66.6645 | -123.3519
997.7969 | 123.23 | -66.7145 | 56.3095 | 0.0046549 | -0.01206 | 0.0011025 | 0.054149 | -0.003955 | 0.062503 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058672 | 0.021327 | 0.059376 | -66.7381 | -0.026065 | -66.7552 | 56.2473 | 56.1426 | 56.3077 | -66.8513 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3168 | 56.1414 | -67.0561 | -0.13677 | -0.062249 | -0.023634 | -0.040683 | 0.09609 | -0.16696 | -0.001826 | -0.34161 | -0.15217 | -0.037485 | -0.071991 | 0.26962 | 0.007273 | -0.16809 | 122.9617 | 122.857 | 123.0222 | 66.6884 | -123.1608 | 122.8718 | 123.0313 | 122.8559 | 66.6782 | -123.3656
998.7969 | 123.2758 | -66.7145 | 56.3095 | 0.0046549 | -0.011846 | 0.0013163 | 0.054149 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.021754 | 0.059163 | -66.7335 | -0.030644 | -66.7506 | 56.2473 | 56.1426 | 56.2985 | -66.8421 | -66.7565 | -0.031692 | -66.7865 | 56.1573 | 56.3168 | 56.1414 | -67.0607 | -0.12762 | -0.062249 | -0.019056 | -0.036105 | 0.09151 | -0.16696 | -0.010983 | -0.34619 | -0.15217 | -0.042064 | -0.071991 | 0.2742 | 0.007273 | -0.16809 | 122.9617 | 122.857 | 123.013 | 66.6838 | -123.1516 | 122.8718 | 123.0313 | 122.8559 | 66.6828 | -123.3702
999.8594 | 123.1659 | -66.7603 | 56.3324 | 0.0046549 | -0.011846 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058886 | 0.021113 | 0.059376 | -66.7381 | -0.021486 | -66.746 | 56.2473 | 56.1288 | 56.3031 | -66.8467 | -66.7565 | -0.040849 | -66.7865 | 56.1573 | 56.3214 | 56.1597 | -67.0652 | -0.086418 | -0.085137 | 0.022142 | 0.014249 | 0.10067 | -0.20358 | -0.029293 | -0.30499 | -0.17506 | 0.003712 | -0.026215 | 0.27878 | -0.011037 | -0.17267 | 123.0075 | 122.8891 | 123.0634 | 66.7388 | -123.1791 | 122.9176 | 123.0816 | 122.92 | 66.7194 | -123.3976
1000.7969 | 123.1476 | -66.7236 | 56.3416 | 0.012286 | -0.01206 | 0.0011025 | 0.053936 | -0.004596 | 0.06293 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058886 | 0.021113 | 0.059163 | -66.7381 | -0.021486 | -66.746 | 56.2518 | 56.1517 | 56.3123 | -66.8467 | -66.7703 | -0.036271 | -66.7819 | 56.1528 | 56.3168 | 56.1414 | -67.0561 | -0.12304 | -0.089714 | -0.014479 | -0.022372 | 0.10067 | -0.18984 | -0.029291 | -0.33246 | -0.18879 | -0.046645 | -0.058257 | 0.2742 | -0.024771 | -0.20013 | 122.9755 | 122.8753 | 123.0359 | 66.7021 | -123.1882 | 122.8764 | 123.0404 | 122.8651 | 66.6874 | -123.3976
1001.7969 | 123.2529 | -66.7145 | 56.2729 | 0.0046549 | -0.01206 | 0.0013163 | 0.053722 | -0.0041686 | 0.06293 | 0.00015261 | -0.0019847 | -0.00098273 | 0.059313 | 0.02154 | 0.059163 | -66.7473 | -0.035222 | -66.7414 | 56.2427 | 56.138 | 56.3077 | -66.8513 | -66.752 | -0.036271 | -66.791 | 56.1482 | 56.3259 | 56.1506 | -67.0607 | -0.13677 | -0.030206 | -0.032791 | -0.026949 | 0.10982 | -0.13491 | 0.034795 | -0.34619 | -0.12471 | -0.037485 | -0.076569 | 0.26962 | 0.053051 | -0.12231 | 122.9572 | 122.8525 | 123.0222 | 66.6793 | -123.1241 | 122.8627 | 123.0404 | 122.8651 | 66.6782 | -123.3336
1002.7969 | 123.2986 | -66.7007 | 56.3049 | -0.010607 | -0.01206 | 0.0011025 | 0.054149 | -0.004596 | 0.06293 | 0.00015261 | -0.0017711 | -0.00055553 | 0.058458 | 0.021327 | 0.059163 | -66.7381 | -0.030644 | -66.746 | 56.2518 | 56.1334 | 56.2985 | -66.8467 | -66.7565 | -0.036271 | -66.791 | 56.1528 | 56.3214 | 56.146 | -67.0607 | -0.14593 | -0.053093 | -0.037367 | -0.04526 | 0.10067 | -0.17154 | -0.006406 | -0.35992 | -0.15217 | -0.055797 | -0.090302 | 0.26962 | 0.016428 | -0.15894 | 122.9526 | 122.8341 | 122.9993 | 66.6701 | -123.1516 | 122.8535 | 123.0221 | 122.8467 | 66.6645 | -123.3656
1003.7969 | 123.2254 | -66.7328 | 56.2958 | -0.0029761 | -0.012273 | 0.0013163 | 0.054149 | -0.0043822 | 0.062717 | -0.0074779 | -0.0017711 | -0.0014101 | 0.058886 | 0.021113 | 0.058949 | -66.7335 | -0.039801 | -66.7552 | 56.2518 | 56.1426 | 56.3031 | -66.8513 | -66.7611 | -0.031692 | -66.7865 | 56.1528 | 56.3168 | 56.1552 | -67.0561 | -0.11846 | -0.043937 | -0.000746 | -0.022373 | 0.09609 | -0.15322 | 0.007328 | -0.3233 | -0.14302 | -0.028333 | -0.053681 | 0.26962 | 0.021006 | -0.14062 | 122.9846 | 122.8753 | 123.0359 | 66.693 | -123.147 | 122.8855 | 123.0496 | 122.8879 | 66.7011 | -123.3519
1004.7969 | 123.2529 | -66.6962 | 56.3324 | 0.012286 | -0.012487 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058886 | 0.021113 | 0.059376 | -66.7335 | -0.035222 | -66.7414 | 56.2473 | 56.138 | 56.3031 | -66.8513 | -66.7565 | -0.040849 | -66.7819 | 56.1573 | 56.3122 | 56.1506 | -67.0561 | -0.15508 | -0.085137 | -0.037367 | -0.04526 | 0.10982 | -0.19442 | -0.029293 | -0.35992 | -0.17506 | -0.060375 | -0.085723 | 0.2742 | -0.020194 | -0.18182 | 122.9434 | 122.8341 | 122.9993 | 66.6609 | -123.1836 | 122.8535 | 123.0084 | 122.8467 | 66.6553 | -123.3885
1005.7969 | 123.2758 | -66.6962 | 56.3187 | 0.012286 | -0.01206 | 0.0011025 | 0.053722 | -0.004596 | 0.06293 | 0.00015261 | -0.0015573 | -0.00076913 | 0.059099 | 0.02154 | 0.058735 | -66.7381 | -0.030644 | -66.746 | 56.2564 | 56.1426 | 56.3031 | -66.8421 | -66.7611 | -0.036271 | -66.7819 | 56.1573 | 56.3214 | 56.1552 | -67.0561 | -0.14593 | -0.062248 | -0.041945 | -0.049838 | 0.096088 | -0.17611 | -0.015561 | -0.35992 | -0.16133 | -0.064954 | -0.085723 | 0.2742 | 0.002695 | -0.16351 | 122.9526 | 122.8387 | 122.9993 | 66.6655 | -123.1608 | 122.8535 | 123.0175 | 122.8513 | 66.6599 | -123.3748
1006.8594 | 123.2254 | -66.7099 | 56.282 | -0.010607 | -0.012273 | 0.00088894 | 0.054149 | -0.004596 | 0.06293 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058886 | 0.021968 | 0.059163 | -66.7427 | -0.026065 | -66.7506 | 56.2427 | 56.138 | 56.2985 | -66.8467 | -66.7474 | -0.036271 | -66.791 | 56.1528 | 56.3214 | 56.1506 | -67.0561 | -0.13677 | -0.039361 | -0.032791 | -0.040683 | 0.096089 | -0.14407 | 0.016483 | -0.34619 | -0.12928 | -0.037485 | -0.081147 | 0.26504 | 0.039317 | -0.13147 | 122.9526 | 122.8479 | 123.0084 | 66.6838 | -123.1287 | 122.8627 | 123.0313 | 122.8605 | 66.6736 | -123.3381
1007.7969 | 123.2986 | -66.6916 | 56.2958 | -0.018238 | -0.01206 | 0.0011025 | 0.054363 | -0.0041686 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058672 | 0.02154 | 0.059376 | -66.7335 | -0.030644 | -66.7506 | 56.2518 | 56.1471 | 56.3031 | -66.8421 | -66.7611 | -0.045428 | -66.7956 | 56.1573 | 56.3214 | 56.1506 | -67.0561 | -0.1505 | -0.043937 | -0.041945 | -0.058994 | 0.09151 | -0.14864 | 0.007328 | -0.3645 | -0.13844 | -0.069532 | -0.10404 | 0.26046 | 0.025584 | -0.1452 | 122.9434 | 122.8387 | 122.9947 | 66.6609 | -123.1379 | 122.8489 | 123.0129 | 122.8422 | 66.6462 | -123.3519
1008.7969 | 123.2391 | -66.7053 | 56.3553 | 0.0046549 | -0.01206 | 0.0013163 | 0.053936 | -0.0048096 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058886 | 0.02154 | 0.05959 | -66.7381 | -0.030644 | -66.7368 | 56.2564 | 56.1426 | 56.3077 | -66.8513 | -66.7611 | -0.040849 | -66.791 | 56.1528 | 56.3214 | 56.1552 | -67.0561 | -0.14593 | -0.098869 | -0.03279 | -0.031526 | 0.1144 | -0.21273 | -0.047603 | -0.35077 | -0.20253 | -0.055799 | -0.085725 | 0.26504 | -0.033926 | -0.20013 | 122.9617 | 122.8479 | 123.013 | 66.6747 | -123.2065 | 122.8581 | 123.0267 | 122.8605 | 66.6645 | -123.4114
1009.7969 | 123.3124 | -66.687 | 56.2866 | 0.019917 | -0.012273 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.021113 | 0.058949 | -66.7381 | -0.035222 | -66.746 | 56.2564 | 56.1426 | 56.2985 | -66.8421 | -66.752 | -0.040849 | -66.7865 | 56.1482 | 56.3168 | 56.1552 | -67.0515 | -0.15508 | -0.030204 | -0.0511 | -0.058993 | 0.096088 | -0.14407 | 0.011905 | -0.3645 | -0.13844 | -0.064951 | -0.099457 | 0.26504 | 0.030161 | -0.13147 | 122.9434 | 122.8296 | 122.9855 | 66.6518 | -123.1287 | 122.8352 | 123.0038 | 122.8422 | 66.6462 | -123.3381
1010.7969 | 123.1522 | -66.7236 | 56.3507 | -0.0029761 | -0.012273 | 0.00088894 | 0.054149 | -0.0043822 | 0.06293 | 0.0077831 | -0.0015573 | -0.0011965 | 0.058886 | 0.02154 | 0.058949 | -66.7427 | -0.030644 | -66.7506 | 56.2473 | 56.1471 | 56.3077 | -66.8467 | -66.7474 | -0.031692 | -66.7865 | 56.1619 | 56.3168 | 56.1552 | -67.0515 | -0.12304 | -0.10345 | -0.019058 | -0.02695 | 0.096089 | -0.20358 | -0.043025 | -0.32788 | -0.18879 | -0.023752 | -0.062836 | 0.26504 | -0.033926 | -0.19555 | 122.9709 | 122.8708 | 123.0313 | 66.693 | -123.1974 | 122.8856 | 123.0404 | 122.8788 | 66.6919 | -123.4022
1011.8594 | 123.2712 | -66.7099 | 56.2546 | -0.0029761 | -0.012487 | 0.0015299 | 0.054149 | -0.0043822 | 0.062717 | 0.00015261 | -0.0015573 | -0.0011965 | 0.058886 | 0.021754 | 0.059163 | -66.7427 | -0.030644 | -66.7506 | 56.2518 | 56.1426 | 56.3031 | -66.8467 | -66.7565 | -0.036271 | -66.7865 | 56.1528 | 56.3259 | 56.1552 | -67.0561 | -0.13677 | -0.002739 | -0.032791 | -0.040683 | 0.096089 | -0.11203 | 0.048526 | -0.34619 | -0.10182 | -0.046642 | -0.076569 | 0.26962 | 0.071361 | -0.099425 | 122.9617 | 122.8525 | 123.013 | 66.6793 | -123.1012 | 122.8627 | 123.0358 | 122.8651 | 66.6736 | -123.3107
1012.7969 | 123.2025 | -66.7328 | 56.3416 | -0.0029761 | -0.01206 | 0.0011025 | 0.053722 | -0.004596 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.059099 | 0.021327 | 0.059376 | -66.7381 | -0.026065 | -66.7506 | 56.2518 | 56.1426 | 56.3077 | -66.8558 | -66.7565 | -0.036271 | -66.7819 | 56.1573 | 56.3168 | 56.146 | -67.0607 | -0.12304 | -0.089714 | -0.005324 | -0.017795 | 0.10525 | -0.199 | -0.03387 | -0.32788 | -0.18421 | -0.023754 | -0.049102 | 0.27878 | -0.024771 | -0.19556 | 122.9846 | 122.8753 | 123.0405 | 66.7067 | -123.1974 | 122.8901 | 123.0496 | 122.8788 | 66.6965 | -123.4022
1013.7969 | 123.2391 | -66.7053 | 56.3004 | 0.0046549 | -0.012273 | 0.0011025 | 0.054149 | -0.0043822 | 0.06293 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058886 | 0.02154 | 0.059163 | -66.7335 | -0.035222 | -66.7552 | 56.2564 | 56.1517 | 56.3031 | -66.8604 | -66.7474 | -0.027113 | -66.7865 | 56.1528 | 56.3168 | 56.1597 | -67.0561 | -0.15509 | -0.043937 | -0.028212 | -0.049839 | 0.10525 | -0.14864 | 0.00275 | -0.35077 | -0.14759 | -0.042063 | -0.081147 | 0.26962 | 0.016428 | -0.14062 | 122.9617 | 122.857 | 123.0084 | 66.6701 | -123.1608 | 122.8581 | 123.0221 | 122.8651 | 66.6782 | -123.3564
1014.7969 | 123.1888 | -66.7557 | 56.3416 | 0.012286 | -0.012273 | 0.0013163 | 0.053936 | -0.0048096 | 0.063144 | 0.00015261 | -0.0013437 | -0.00076913 | 0.058886 | 0.021968 | 0.059163 | -66.7381 | -0.035222 | -66.746 | 56.2473 | 56.1426 | 56.3077 | -66.8513 | -66.7474 | -0.036271 | -66.7819 | 56.1528 | 56.3259 | 56.1597 | -67.0561 | -0.095575 | -0.094293 | 0.017564 | 0.009671 | 0.10525 | -0.199 | -0.03387 | -0.30041 | -0.18879 | 0.008291 | -0.026214 | 0.2742 | -0.015614 | -0.18182 | 123.0029 | 122.8982 | 123.0634 | 66.7205 | -123.1928 | 122.9084 | 123.0816 | 122.9154 | 66.7194 | -123.3976
1015.8594 | 123.1934 | -66.7282 | 56.3187 | 0.012286 | -0.012273 | 0.00088894 | 0.053936 | -0.0048096 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.021754 | 0.059163 | -66.7335 | -0.026065 | -66.7552 | 56.2564 | 56.1563 | 56.3168 | -66.8467 | -66.752 | -0.036271 | -66.7773 | 56.1528 | 56.3214 | 56.1597 | -67.0561 | -0.11846 | -0.062248 | -0.005324 | -0.026951 | 0.091511 | -0.16238 | -0.001825 | -0.32788 | -0.16591 | -0.023753 | -0.049101 | 0.27878 | 0.002695 | -0.15893 | 122.9846 | 122.8845 | 123.0451 | 66.7021 | -123.1653 | 122.881 | 123.0496 | 122.8879 | 66.6919 | -123.3748
1016.7969 | 123.175 | -66.7419 | 56.3507 | 0.012286 | -0.012273 | 0.0011025 | 0.053508 | -0.0043822 | 0.062717 | 0.015414 | -0.0017711 | -0.00098273 | 0.058886 | 0.02154 | 0.059376 | -66.7335 | -0.026065 | -66.746 | 56.2473 | 56.1426 | 56.3031 | -66.8558 | -66.752 | -0.031692 | -66.7865 | 56.1619 | 56.3259 | 56.146 | -67.0561 | -0.11389 | -0.10345 | 0.008409 | -0.004062 | 0.10983 | -0.20815 | -0.047604 | -0.31415 | -0.18879 | -0.01002 | -0.044526 | 0.26962 | -0.024769 | -0.20471 | 122.9892 | 122.8845 | 123.045 | 66.7159 | -123.2065 | 122.9039 | 123.0679 | 122.8879 | 66.7103 | -123.4068
1017.7969 | 123.1842 | -66.7694 | 56.3324 | 0.0046549 | -0.01206 | 0.0013163 | 0.053936 | -0.0043822 | 0.062717 | -0.0074779 | -0.0017711 | -0.0011965 | 0.058886 | 0.021327 | 0.058949 | -66.7381 | -0.026065 | -66.7506 | 56.2518 | 56.1334 | 56.3031 | -66.8467 | -66.752 | -0.031692 | -66.7773 | 56.1482 | 56.3168 | 56.1552 | -67.0607 | -0.077263 | -0.080558 | 0.031297 | 0.018826 | 0.096089 | -0.199 | -0.029293 | -0.29126 | -0.18422 | 0.017446 | -0.007902 | 0.28336 | -0.015615 | -0.17724 | 123.0212 | 122.9028 | 123.0725 | 66.7433 | -123.1791 | 122.9176 | 123.0862 | 122.9246 | 66.7377 | -123.3931
1018.7969 | 123.2117 | -66.7328 | 56.3141 | 0.0046549 | -0.012273 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | 0.00015261 | -0.0019847 | -0.0014101 | 0.058886 | 0.021754 | 0.059376 | -66.7381 | -0.026065 | -66.7506 | 56.2564 | 56.1471 | 56.3031 | -66.8558 | -66.752 | -0.036271 | -66.7819 | 56.1573 | 56.3259 | 56.1597 | -67.0607 | -0.12304 | -0.05767 | -0.005324 | -0.017795 | 0.10525 | -0.16696 | -0.010983 | -0.32788 | -0.15675 | -0.019175 | -0.049102 | 0.27878 | 0.011852 | -0.15436 | 122.9892 | 122.8799 | 123.0359 | 66.7067 | -123.1699 | 122.8901 | 123.0587 | 122.8925 | 66.6965 | -123.3748
1019.7969 | 123.1476 | -66.7282 | 56.3187 | 0.012286 | -0.012487 | 0.0011025 | 0.053936 | -0.0043822 | 0.062503 | 0.0077831 | -0.0017711 | -0.0011965 | 0.058672 | 0.02154 | 0.058735 | -66.7335 | -0.039801 | -66.7597 | 56.2518 | 56.1471 | 56.3031 | -66.8421 | -66.7565 | -0.040849 | -66.7819 | 56.1573 | 56.3122 | 56.1506 | -67.0515 | -0.11388 | -0.066826 | -0.005324 | -0.03153 | 0.082353 | -0.17153 | -0.015561 | -0.3233 | -0.16133 | -0.028332 | -0.05368 | 0.26962 | -0.006462 | -0.16809 | 122.98 | 122.8753 | 123.0313 | 66.6884 | -123.1608 | 122.8855 | 123.0404 | 122.8788 | 66.6874 | -123.3702
1020.8594 | 123.1659 | -66.7831 | 56.3004 | -0.0029761 | -0.01206 | 0.0011025 | 0.053722 | -0.0048096 | 0.062503 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.021968 | 0.05959 | -66.7381 | -0.026065 | -66.7597 | 56.2564 | 56.1471 | 56.3123 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1619 | 56.3214 | 56.1552 | -67.0515 | -0.068109 | -0.043937 | 0.04503 | 0.023402 | 0.091511 | -0.15322 | 0.011908 | -0.26837 | -0.13844 | 0.031179 | -0.003327 | 0.26504 | 0.021006 | -0.1452 | 123.0396 | 122.9303 | 123.0954 | 66.7571 | -123.1516 | 122.9451 | 123.1045 | 122.9383 | 66.7514 | -123.3519
1021.7969 | 123.1522 | -66.7328 | 56.3278 | -0.0029761 | -0.012273 | 0.00088894 | 0.053722 | -0.0048096 | 0.062717 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058886 | 0.021754 | 0.05959 | -66.7381 | -0.030644 | -66.7552 | 56.2564 | 56.1517 | 56.3214 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1482 | 56.3305 | 56.1643 | -67.0515 | -0.11846 | -0.071403 | -0.005324 | -0.022373 | 0.09609 | -0.17611 | -0.006401 | -0.31872 | -0.17964 | -0.019175 | -0.053681 | 0.26504 | 0.002697 | -0.16351 | 122.9892 | 122.8845 | 123.0542 | 66.7021 | -123.1791 | 122.881 | 123.0633 | 122.8971 | 66.6919 | -123.3793
1022.8594 | 123.2574 | -66.7053 | 56.3278 | -0.0029761 | -0.012487 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.021968 | 0.058949 | -66.7381 | -0.030644 | -66.7552 | 56.2518 | 56.1517 | 56.3077 | -66.8513 | -66.7611 | -0.036271 | -66.791 | 56.1619 | 56.3214 | 56.1414 | -67.0561 | -0.14593 | -0.075981 | -0.03279 | -0.049839 | 0.09609 | -0.17611 | -0.020137 | -0.35077 | -0.1659 | -0.055799 | -0.085725 | 0.26504 | -0.00646 | -0.1864 | 122.9572 | 122.857 | 123.013 | 66.6747 | -123.1791 | 122.8672 | 123.0267 | 122.8467 | 66.6691 | -123.3839
1023.7969 | 123.1522 | -66.7465 | 56.3324 | 0.0046549 | -0.012487 | 0.00088894 | 0.054149 | -0.0043822 | 0.062503 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058886 | 0.021968 | 0.059163 | -66.7427 | -0.035222 | -66.746 | 56.2564 | 56.1563 | 56.3077 | -66.8467 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3259 | 56.1552 | -67.0469 | -0.10015 | -0.07598 | 0.00383 | 0.000516 | 0.10067 | -0.17611 | -0.024714 | -0.30041 | -0.17506 | -0.005442 | -0.039948 | 0.26046 | -0.006458 | -0.17724 | 123.0029 | 122.9028 | 123.0542 | 66.7113 | -123.1791 | 122.9039 | 123.0725 | 122.9017 | 66.7103 | -123.3793
1024.7969 | 123.1842 | -66.7557 | 56.3141 | 0.0046549 | -0.012701 | 0.00088894 | 0.053936 | -0.0043822 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058886 | 0.021754 | 0.059163 | -66.7381 | -0.030644 | -66.7506 | 56.2564 | 56.1563 | 56.3031 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1528 | 56.3168 | 56.1506 | -67.0515 | -0.095575 | -0.05767 | 0.017564 | 0.005093 | 0.10067 | -0.1578 | -0.010983 | -0.29583 | -0.16133 | 0.008291 | -0.030793 | 0.26504 | 0.002695 | -0.16351 | 123.0121 | 122.912 | 123.0588 | 66.725 | -123.1653 | 122.9084 | 123.0725 | 122.9063 | 66.7194 | -123.3656
1025.7969 | 123.1979 | -66.7374 | 56.3278 | 0.0046549 | -0.012273 | 0.00067514 | 0.053936 | -0.0048096 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058672 | 0.02154 | 0.058949 | -66.7381 | -0.030644 | -66.7506 | 56.2518 | 56.1563 | 56.3077 | -66.8513 | -66.752 | -0.031692 | -66.7865 | 56.1573 | 56.3168 | 56.1552 | -67.0515 | -0.11389 | -0.075981 | -0.000746 | -0.013217 | 0.10067 | -0.17153 | -0.020137 | -0.31414 | -0.17048 | -0.014597 | -0.049103 | 0.26504 | -0.011038 | -0.17267 | 122.9892 | 122.8937 | 123.045 | 66.7067 | -123.1791 | 122.8947 | 123.0541 | 122.8925 | 66.7057 | -123.3793
1026.8594 | 123.2574 | -66.7191 | 56.3187 | 0.0046549 | -0.012273 | 0.00088894 | 0.053722 | -0.0041686 | 0.062717 | -0.0074779 | -0.0015573 | -0.0014101 | 0.058886 | 0.021968 | 0.059163 | -66.7473 | -0.039801 | -66.7506 | 56.2473 | 56.1517 | 56.3031 | -66.8513 | -66.7565 | -0.036271 | -66.791 | 56.1573 | 56.3214 | 56.1643 | -67.0561 | -0.1322 | -0.071405 | -0.028214 | -0.031528 | 0.10067 | -0.16695 | -0.015561 | -0.33703 | -0.16133 | -0.037487 | -0.071992 | 0.26504 | 0.002695 | -0.15435 | 122.9663 | 122.8708 | 123.0222 | 66.6793 | -123.1699 | 122.8764 | 123.0404 | 122.8834 | 66.6828 | -123.3748
1027.7969 | 123.2117 | -66.7145 | 56.3095 | 0.0046549 | -0.012487 | 0.00046154 | 0.053936 | -0.004596 | 0.06293 | 0.015414 | -0.0017711 | -0.0014101 | 0.058458 | 0.021754 | 0.058735 | -66.7335 | -0.030644 | -66.7552 | 56.2564 | 56.1563 | 56.3077 | -66.8513 | -66.7565 | -0.036271 | -66.7819 | 56.1528 | 56.3214 | 56.1552 | -67.0652 | -0.13677 | -0.053092 | -0.019056 | -0.040683 | 0.09609 | -0.15322 | -0.001826 | -0.35077 | -0.15675 | -0.042064 | -0.067412 | 0.28336 | 0.011851 | -0.15436 | 122.9709 | 122.8708 | 123.0222 | 66.6838 | -123.1608 | 122.8672 | 123.0358 | 122.8696 | 66.6782 | -123.3748
1028.7969 | 123.143 | -66.7831 | 56.3095 | -0.0029761 | -0.012487 | 0.0011025 | 0.054363 | -0.004596 | 0.062717 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058672 | 0.02154 | 0.059376 | -66.7381 | -0.026065 | -66.746 | 56.2518 | 56.1517 | 56.3123 | -66.8467 | -66.752 | -0.036271 | -66.7819 | 56.1619 | 56.3168 | 56.1597 | -67.0561 | -0.06353 | -0.05767 | 0.04503 | 0.037137 | 0.10067 | -0.1578 | 0.002753 | -0.27295 | -0.14759 | 0.031179 | 0.001252 | 0.2742 | 0.007273 | -0.14978 | 123.035 | 122.9349 | 123.0954 | 66.7571 | -123.1562 | 122.9451 | 123.0999 | 122.9429 | 66.7469 | -123.3656
1029.7969 | 123.1522 | -66.7603 | 56.3049 | -0.018238 | -0.012487 | 0.0013163 | 0.054149 | -0.0043822 | 0.062503 | 0.015414 | -0.0019847 | -0.00098273 | 0.058886 | 0.022181 | 0.058949 | -66.7335 | -0.026065 | -66.7506 | 56.2564 | 56.1471 | 56.3077 | -66.8558 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3259 | 56.1689 | -67.0607 | -0.095576 | -0.048515 | 0.02672 | 0.009671 | 0.10525 | -0.1578 | 0.002751 | -0.30041 | -0.14759 | 0.008291 | -0.026215 | 0.2742 | 0.021007 | -0.13604 | 123.0167 | 122.9074 | 123.0679 | 66.7342 | -123.1608 | 122.9176 | 123.0862 | 122.9291 | 66.724 | -123.3656
1030.8594 | 123.2162 | -66.7511 | 56.3141 | -0.0029761 | -0.012487 | 0.0011025 | 0.053936 | -0.0043822 | 0.062503 | 0.0077831 | -0.0017711 | -0.0014101 | 0.058672 | 0.021754 | 0.059163 | -66.7335 | -0.035222 | -66.7506 | 56.2518 | 56.1471 | 56.3168 | -66.8513 | -66.7565 | -0.040849 | -66.7819 | 56.1573 | 56.3259 | 56.1597 | -67.0515 | -0.10015 | -0.062248 | 0.017565 | 0.000516 | 0.10067 | -0.16696 | 0.002753 | -0.30041 | -0.15675 | -0.005443 | -0.030791 | 0.26962 | 0.011852 | -0.15436 | 123.0029 | 122.8982 | 123.0679 | 66.7159 | -123.1653 | 122.9084 | 123.077 | 122.9108 | 66.7103 | -123.3656
1031.7969 | 123.1613 | -66.7328 | 56.2958 | 0.0046549 | -0.012487 | 0.00088894 | 0.053936 | -0.0048096 | 0.062503 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058672 | 0.021754 | 0.05959 | -66.7335 | -0.030644 | -66.7506 | 56.2518 | 56.1471 | 56.3031 | -66.865 | -66.7565 | -0.036271 | -66.7865 | 56.1619 | 56.3214 | 56.1552 | -67.0561 | -0.1322 | -0.043937 | -0.000746 | -0.017795 | 0.1144 | -0.14864 | 0.007328 | -0.3233 | -0.13386 | -0.023754 | -0.053681 | 0.26962 | 0.025584 | -0.14062 | 122.9846 | 122.8799 | 123.0359 | 66.7021 | -123.1608 | 122.8947 | 123.0541 | 122.8879 | 66.6965 | -123.3519
1032.7969 | 123.2758 | -66.7099 | 56.2592 | -0.0029761 | -0.012701 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058886 | 0.021754 | 0.059376 | -66.7335 | -0.035222 | -66.7552 | 56.2518 | 56.1471 | 56.3077 | -66.8421 | -66.7611 | -0.040849 | -66.7819 | 56.1619 | 56.3259 | 56.1323 | -67.0561 | -0.13219 | -0.007316 | -0.023634 | -0.045261 | 0.086932 | -0.11202 | 0.048528 | -0.34619 | -0.097238 | -0.051221 | -0.07199 | 0.2742 | 0.066784 | -0.12689 | 122.9617 | 122.857 | 123.0176 | 66.6747 | -123.1012 | 122.8718 | 123.0358 | 122.8422 | 66.6691 | -123.3152
1033.8594 | 123.175 | -66.7419 | 56.3324 | 0.012286 | -0.012914 | 0.00088894 | 0.053936 | -0.0048096 | 0.062717 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058886 | 0.021968 | 0.058949 | -66.7381 | -0.030644 | -66.7506 | 56.2518 | 56.1517 | 56.3168 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1528 | 56.3259 | 56.1597 | -67.0561 | -0.10931 | -0.080558 | 0.003831 | -0.00864 | 0.10067 | -0.18069 | -0.015557 | -0.31415 | -0.17964 | -0.005442 | -0.044526 | 0.26962 | -0.006458 | -0.17267 | 122.9938 | 122.8937 | 123.0588 | 66.7113 | -123.1836 | 122.8947 | 123.0679 | 122.9017 | 66.7057 | -123.3885
1034.7969 | 123.2529 | -66.7236 | 56.2729 | 0.0046549 | -0.012273 | 0.0011025 | 0.053936 | -0.0050232 | 0.062289 | 0.0077831 | -0.0017711 | -0.00098273 | 0.059099 | 0.022181 | 0.059163 | -66.7381 | -0.026065 | -66.746 | 56.2473 | 56.1334 | 56.3031 | -66.8467 | -66.7428 | -0.031692 | -66.791 | 56.1528 | 56.3259 | 56.1506 | -67.0607 | -0.12304 | -0.025628 | -0.014479 | -0.022372 | 0.10067 | -0.13949 | 0.030216 | -0.33704 | -0.12013 | -0.019173 | -0.067414 | 0.26962 | 0.053051 | -0.12231 | 122.9709 | 122.857 | 123.0267 | 66.6976 | -123.1196 | 122.8764 | 123.0496 | 122.8742 | 66.6919 | -123.3336
1035.8594 | 123.2849 | -66.687 | 56.2454 | 0.0046549 | -0.012487 | 0.0011025 | 0.054149 | -0.0048096 | 0.062289 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058886 | 0.021968 | 0.059163 | -66.7381 | -0.035222 | -66.7414 | 56.2564 | 56.1471 | 56.3031 | -66.8558 | -66.7565 | -0.036271 | -66.7865 | 56.1528 | 56.3305 | 56.1414 | -67.0561 | -0.16882 | 0.010995 | -0.0511 | -0.054415 | 0.1144 | -0.09829 | 0.057682 | -0.36908 | -0.092662 | -0.06953 | -0.099457 | 0.26962 | 0.085095 | -0.104 | 122.9434 | 122.8341 | 122.9901 | 66.6518 | -123.1013 | 122.8398 | 123.0175 | 122.8284 | 66.6507 | -123.3015
1036.7969 | 123.2574 | -66.7145 | 56.2729 | 0.0046549 | -0.012273 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | -0.015108 | -0.0015573 | -0.00098273 | 0.058672 | 0.021968 | 0.059376 | -66.729 | -0.035222 | -66.746 | 56.2564 | 56.138 | 56.3123 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1619 | 56.3305 | 56.1552 | -67.0607 | -0.13677 | -0.016471 | -0.014478 | -0.031527 | 0.10525 | -0.13491 | 0.039374 | -0.34619 | -0.11097 | -0.032907 | -0.071991 | 0.2742 | 0.057629 | -0.11774 | 122.9709 | 122.8525 | 123.0267 | 66.6793 | -123.1241 | 122.8764 | 123.045 | 122.8696 | 66.6782 | -123.3336
1037.7969 | 123.2483 | -66.7145 | 56.2592 | 0.0046549 | -0.012273 | 0.0011025 | 0.054149 | -0.0048096 | 0.062289 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058672 | 0.022181 | 0.058949 | -66.729 | -0.030644 | -66.7323 | 56.2427 | 56.1471 | 56.2985 | -66.8421 | -66.752 | -0.036271 | -66.7865 | 56.1528 | 56.3305 | 56.1414 | -67.0607 | -0.12762 | -0.016473 | -0.014478 | -0.017792 | 0.10982 | -0.11202 | 0.039371 | -0.34619 | -0.10639 | -0.037485 | -0.071991 | 0.2742 | 0.071362 | -0.11774 | 122.9572 | 122.8616 | 123.013 | 66.6838 | -123.1012 | 122.8672 | 123.045 | 122.8559 | 66.6782 | -123.3198
1038.7969 | 123.2391 | -66.7374 | 56.3232 | 0.012286 | -0.012487 | 0.0011025 | 0.054363 | -0.004596 | 0.062503 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058672 | 0.021968 | 0.059163 | -66.7427 | -0.030644 | -66.746 | 56.2473 | 56.138 | 56.3123 | -66.8421 | -66.7474 | -0.036271 | -66.791 | 56.1528 | 56.3305 | 56.1414 | -67.0515 | -0.10473 | -0.075982 | -0.005325 | -0.008639 | 0.096088 | -0.18527 | -0.01098 | -0.31414 | -0.17048 | -0.010019 | -0.053681 | 0.26046 | 0.007275 | -0.18182 | 122.9846 | 122.8753 | 123.0496 | 66.7067 | -123.1653 | 122.8901 | 123.0679 | 122.8788 | 66.7011 | -123.3748
1039.7969 | 123.2574 | -66.7191 | 56.2912 | -0.010607 | -0.012701 | 0.0013163 | 0.054149 | -0.004596 | 0.062503 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058886 | 0.021968 | 0.058949 | -66.7335 | -0.039801 | -66.7368 | 56.2518 | 56.138 | 56.2985 | -66.8558 | -66.752 | -0.040849 | -66.7865 | 56.1528 | 56.3305 | 56.1414 | -67.0561 | -0.13678 | -0.03936 | -0.014479 | -0.017793 | 0.11898 | -0.15322 | 0.007327 | -0.33703 | -0.13844 | -0.032908 | -0.067414 | 0.26962 | 0.039318 | -0.14978 | 122.9709 | 122.857 | 123.0176 | 66.6793 | -123.147 | 122.8718 | 123.0496 | 122.8605 | 66.6782 | -123.3473
1040.8594 | 123.2574 | -66.7007 | 56.2912 | -0.0029761 | -0.012701 | 0.00088894 | 0.053722 | -0.004596 | 0.062503 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.021754 | 0.059163 | -66.7381 | -0.035222 | -66.746 | 56.2473 | 56.1471 | 56.3031 | -66.8375 | -66.7565 | -0.040849 | -66.7819 | 56.1619 | 56.3305 | 56.1506 | -67.0607 | -0.13677 | -0.043939 | -0.037367 | -0.04526 | 0.091509 | -0.14407 | 0.011905 | -0.35992 | -0.12928 | -0.055797 | -0.081145 | 0.27878 | 0.039318 | -0.14062 | 122.948 | 122.8479 | 123.0038 | 66.6655 | -123.1287 | 122.8627 | 123.0313 | 122.8513 | 66.6599 | -123.3519
1041.7969 | 123.2437 | -66.7374 | 56.3049 | -0.010607 | -0.012701 | 0.0011025 | 0.053936 | -0.004596 | 0.062503 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058458 | 0.021754 | 0.059163 | -66.7381 | -0.030644 | -66.7323 | 56.2381 | 56.1426 | 56.3077 | -66.8558 | -66.752 | -0.036271 | -66.7819 | 56.1528 | 56.3259 | 56.1506 | -67.0515 | -0.11846 | -0.066828 | -0.000746 | 0.005096 | 0.12356 | -0.16238 | 0.002751 | -0.31414 | -0.15217 | -0.014597 | -0.044524 | 0.26962 | 0.021007 | -0.15436 | 122.9755 | 122.8799 | 123.045 | 66.7067 | -123.1608 | 122.8901 | 123.0633 | 122.8879 | 66.7011 | -123.3564
1042.875 | 123.2941 | -66.7191 | 56.282 | -0.0029761 | -0.012701 | 0.0011025 | 0.054149 | -0.0050232 | 0.062503 | -0.0074779 | -0.0017711 | -0.0011965 | 0.059099 | 0.021754 | 0.059163 | -66.7335 | -0.035222 | -66.746 | 56.2473 | 56.1471 | 56.3123 | -66.8513 | -66.7474 | -0.031692 | -66.7865 | 56.1528 | 56.3305 | 56.1552 | -67.0561 | -0.1322 | -0.034783 | -0.014479 | -0.02695 | 0.10525 | -0.13491 | 0.030219 | -0.33703 | -0.12928 | -0.02833 | -0.067414 | 0.26962 | 0.048474 | -0.12689 | 122.9663 | 122.8662 | 123.0313 | 66.6838 | -123.1333 | 122.8718 | 123.0496 | 122.8742 | 66.6874 | -123.3381
1043.7969 | 123.2208 | -66.7191 | 56.2958 | -0.0029761 | -0.012273 | 0.00067514 | 0.053722 | -0.0048096 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.021968 | 0.058735 | -66.7381 | -0.030644 | -66.7368 | 56.2473 | 56.1471 | 56.3031 | -66.8513 | -66.752 | -0.040849 | -66.7819 | 56.1482 | 56.3259 | 56.146 | -67.0561 | -0.1322 | -0.048516 | -0.019057 | -0.017793 | 0.1144 | -0.14864 | 0.007328 | -0.33703 | -0.14759 | -0.032908 | -0.062835 | 0.2742 | 0.030163 | -0.14978 | 122.9663 | 122.8662 | 123.0222 | 66.6884 | -123.147 | 122.8672 | 123.045 | 122.8651 | 66.6782 | -123.3519
1044.7969 | 123.2986 | -66.6779 | 56.3095 | -0.010607 | -0.012701 | 0.0011025 | 0.053936 | -0.004596 | 0.062289 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058672 | 0.021968 | 0.059163 | -66.7427 | -0.035222 | -66.746 | 56.2427 | 56.1517 | 56.3031 | -66.8467 | -66.7474 | -0.036271 | -66.7865 | 56.1573 | 56.3214 | 56.1597 | -67.0561 | -0.16882 | -0.066827 | -0.064835 | -0.068149 | 0.10067 | -0.1578 | -0.006405 | -0.37823 | -0.15217 | -0.069529 | -0.10861 | 0.26962 | 0.011851 | -0.14978 | 122.9205 | 122.8296 | 122.981 | 66.6426 | -123.1562 | 122.8352 | 122.9992 | 122.8376 | 66.6416 | -123.3656
1045.8594 | 123.2437 | -66.6824 | 56.3004 | 0.0046549 | -0.012487 | 0.0011025 | 0.054149 | -0.004596 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058886 | 0.022395 | 0.059163 | -66.729 | -0.030644 | -66.746 | 56.2564 | 56.1334 | 56.3077 | -66.8513 | -66.7474 | -0.045428 | -66.7773 | 56.1528 | 56.3305 | 56.146 | -67.0561 | -0.16882 | -0.043937 | -0.046522 | -0.063571 | 0.10525 | -0.16696 | 0.007329 | -0.37365 | -0.14759 | -0.064951 | -0.094877 | 0.27878 | 0.030163 | -0.15436 | 122.9389 | 122.8158 | 122.9901 | 66.6518 | -123.1516 | 122.8352 | 123.013 | 122.8284 | 66.637 | -123.3564
1046.7969 | 123.2803 | -66.7007 | 56.2866 | -0.0029761 | -0.012914 | 0.00088894 | 0.053936 | -0.004596 | 0.062503 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058886 | 0.022181 | 0.059163 | -66.7427 | -0.035222 | -66.7368 | 56.2518 | 56.138 | 56.3123 | -66.8513 | -66.7474 | -0.040849 | -66.7865 | 56.1573 | 56.3214 | 56.1643 | -67.0515 | -0.15051 | -0.034782 | -0.041946 | -0.036103 | 0.1144 | -0.14865 | 0.025641 | -0.35076 | -0.12928 | -0.04664 | -0.085724 | 0.26504 | 0.034739 | -0.12231 | 122.9526 | 122.8387 | 123.013 | 66.6655 | -123.1379 | 122.8581 | 123.0221 | 122.8651 | 66.6599 | -123.3381
1047.8594 | 123.2895 | -66.7053 | 56.2958 | -0.0029761 | -0.012273 | 0.00088894 | 0.053936 | -0.0048096 | 0.062289 | -0.0074779 | -0.0015573 | -0.00098273 | 0.058458 | 0.021968 | 0.058949 | -66.7427 | -0.035222 | -66.7414 | 56.261 | 56.138 | 56.3168 | -66.8513 | -66.7474 | -0.040849 | -66.791 | 56.1573 | 56.3305 | 56.1368 | -67.0607 | -0.14593 | -0.034781 | -0.037369 | -0.036105 | 0.10982 | -0.1578 | 0.021064 | -0.35535 | -0.13844 | -0.042063 | -0.085725 | 0.26962 | 0.034741 | -0.15894 | 122.9663 | 122.8433 | 123.0222 | 66.6701 | -123.147 | 122.8627 | 123.0358 | 122.8422 | 66.6645 | -123.3564
1048.7969 | 123.2208 | -66.7099 | 56.3141 | 0.0046549 | -0.012273 | 0.0011025 | 0.053936 | -0.0048096 | 0.062289 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058672 | 0.022181 | 0.058949 | -66.7427 | -0.030644 | -66.7368 | 56.2564 | 56.1517 | 56.3123 | -66.8604 | -66.7474 | -0.040849 | -66.7865 | 56.1573 | 56.3259 | 56.1643 | -67.0561 | -0.15051 | -0.05767 | -0.032791 | -0.026948 | 0.12356 | -0.16238 | -0.001825 | -0.34619 | -0.15675 | -0.037485 | -0.076569 | 0.26962 | 0.011852 | -0.14978 | 122.9663 | 122.8616 | 123.0222 | 66.6793 | -123.1745 | 122.8672 | 123.0358 | 122.8742 | 66.6691 | -123.3702
1049.8438 | 123.1247 | -66.7786 | 56.3187 | -0.0029761 | -0.012487 | 0.0013163 | 0.053722 | -0.0041686 | 0.062076 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058672 | 0.022181 | 0.059163 | -66.729 | -0.035222 | -66.7368 | 56.2564 | 56.1471 | 56.3123 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1528 | 56.3214 | 56.1552 | -67.0561 | -0.072687 | -0.062248 | 0.049608 | 0.041716 | 0.1144 | -0.17153 | -0.006403 | -0.27752 | -0.16591 | 0.031179 | -0.007905 | 0.26962 | 0.002695 | -0.16351 | 123.035 | 122.9257 | 123.0908 | 66.7433 | -123.1699 | 122.9313 | 123.0999 | 122.9337 | 66.7423 | -123.3748
1050.7969 | 123.2071 | -66.7374 | 56.3187 | 0.012286 | -0.012701 | 0.00067514 | 0.053722 | -0.004596 | 0.062289 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058458 | 0.022181 | 0.058949 | -66.7427 | -0.030644 | -66.7368 | 56.2518 | 56.1426 | 56.3123 | -66.8467 | -66.7428 | -0.036271 | -66.7865 | 56.1436 | 56.3259 | 56.1506 | -67.0561 | -0.10931 | -0.066826 | -0.005325 | 0.000518 | 0.10982 | -0.17611 | -0.006403 | -0.31872 | -0.17506 | -0.00544 | -0.049103 | 0.26962 | 0.007274 | -0.16809 | 122.9892 | 122.8799 | 123.0496 | 66.7067 | -123.1653 | 122.881 | 123.0633 | 122.8879 | 66.7011 | -123.3748
1051.7969 | 123.2529 | -66.7191 | 56.2958 | 0.012286 | -0.012701 | 0.0011025 | 0.054363 | -0.0048096 | 0.062289 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059099 | 0.022181 | 0.059804 | -66.7427 | -0.030644 | -66.7323 | 56.2473 | 56.1471 | 56.3123 | -66.8467 | -66.7428 | -0.040849 | -66.7819 | 56.1573 | 56.3259 | 56.1552 | -67.0607 | -0.12762 | -0.048516 | -0.023636 | -0.013215 | 0.1144 | -0.14864 | 0.016486 | -0.34161 | -0.13844 | -0.023751 | -0.062835 | 0.27878 | 0.030163 | -0.14062 | 122.9663 | 122.8662 | 123.0313 | 66.6884 | -123.1424 | 122.8764 | 123.045 | 122.8742 | 66.6782 | -123.3564
1052.7969 | 123.2712 | -66.7191 | 56.2637 | 0.0046549 | -0.012487 | 0.00067514 | 0.053936 | -0.004596 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058886 | 0.022181 | 0.058949 | -66.7335 | -0.035222 | -66.7277 | 56.2518 | 56.1517 | 56.3077 | -66.8467 | -66.7474 | -0.036271 | -66.7819 | 56.1573 | 56.3259 | 56.146 | -67.0607 | -0.12762 | -0.011894 | -0.014479 | -0.008637 | 0.11898 | -0.11202 | 0.04395 | -0.34161 | -0.10639 | -0.02833 | -0.062835 | 0.27878 | 0.062206 | -0.11774 | 122.9709 | 122.8708 | 123.0267 | 66.6838 | -123.1104 | 122.8764 | 123.045 | 122.8651 | 66.6828 | -123.3244
1053.8594 | 123.23 | -66.7191 | 56.2958 | 0.0046549 | -0.012273 | 0.0011025 | 0.053936 | -0.0048096 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058672 | 0.021968 | 0.058949 | -66.7427 | -0.030644 | -66.7323 | 56.2518 | 56.1517 | 56.3077 | -66.8421 | -66.7428 | -0.040849 | -66.7865 | 56.1573 | 56.3214 | 56.1689 | -67.0607 | -0.12304 | -0.043937 | -0.023636 | -0.013215 | 0.10982 | -0.14406 | 0.011907 | -0.34161 | -0.13844 | -0.023751 | -0.067414 | 0.2742 | 0.025584 | -0.12689 | 122.9709 | 122.8708 | 123.0267 | 66.6884 | -123.1379 | 122.8764 | 123.0404 | 122.8879 | 66.6782 | -123.3564
1054.7969 | 123.1338 | -66.7282 | 56.337 | 0.0046549 | -0.012487 | 0.0011025 | 0.054149 | -0.0043822 | 0.062289 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058672 | 0.021754 | 0.059163 | -66.7381 | -0.030644 | -66.7368 | 56.2518 | 56.1563 | 56.3123 | -66.8467 | -66.7474 | -0.040849 | -66.7865 | 56.1619 | 56.3214 | 56.146 | -67.0607 | -0.11846 | -0.085136 | -0.009902 | -0.008638 | 0.10982 | -0.18069 | -0.024713 | -0.33246 | -0.17506 | -0.019175 | -0.058259 | 0.2742 | -0.015615 | -0.19098 | 122.98 | 122.8845 | 123.0405 | 66.6976 | -123.1836 | 122.8901 | 123.0496 | 122.8742 | 66.6874 | -123.3976
1055.7969 | 123.2529 | -66.7236 | 56.3232 | 0.0046549 | -0.012487 | 0.0013163 | 0.053936 | -0.0043822 | 0.062503 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058458 | 0.022395 | 0.058949 | -66.7335 | -0.035222 | -66.7368 | 56.2518 | 56.1471 | 56.3123 | -66.8558 | -66.752 | -0.036271 | -66.791 | 56.1573 | 56.3214 | 56.1368 | -67.0515 | -0.1322 | -0.071403 | -0.009901 | -0.013215 | 0.11898 | -0.17611 | -0.01098 | -0.32788 | -0.1659 | -0.02833 | -0.067414 | 0.26046 | -0.001882 | -0.1864 | 122.9755 | 122.8708 | 123.0359 | 66.6884 | -123.1791 | 122.881 | 123.045 | 122.8605 | 66.6874 | -123.3748
1056.8594 | 123.1796 | -66.7145 | 56.337 | 0.0046549 | -0.012914 | 0.0013163 | 0.053936 | -0.0048096 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.021968 | 0.058949 | -66.7427 | -0.035222 | -66.7277 | 56.2518 | 56.1426 | 56.3123 | -66.8513 | -66.7474 | -0.050007 | -66.7819 | 56.1573 | 56.3259 | 56.1643 | -67.0607 | -0.13677 | -0.085136 | -0.028213 | -0.013214 | 0.12356 | -0.19442 | -0.024713 | -0.34619 | -0.17964 | -0.032907 | -0.067412 | 0.27878 | -0.011036 | -0.17266 | 122.9663 | 122.857 | 123.0267 | 66.6793 | -123.1882 | 122.8718 | 123.0404 | 122.8788 | 66.6645 | -123.3976
1057.7969 | 123.1796 | -66.7923 | 56.3095 | 0.0046549 | -0.012487 | 0.0011025 | 0.053936 | -0.004596 | 0.062503 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.022181 | 0.059163 | -66.7473 | -0.030644 | -66.7414 | 56.2518 | 56.1471 | 56.3031 | -66.8513 | -66.7428 | -0.040849 | -66.7865 | 56.1573 | 56.3259 | 56.1552 | -67.0515 | -0.058954 | -0.05767 | 0.045028 | 0.05087 | 0.10982 | -0.16238 | -0.006405 | -0.25921 | -0.15217 | 0.049491 | 0.005828 | 0.26504 | 0.01643 | -0.15436 | 123.0441 | 122.9394 | 123.0954 | 66.7617 | -123.1608 | 122.9496 | 123.1182 | 122.9475 | 66.7514 | -123.361
1058.7969 | 123.2208 | -66.7374 | 56.3049 | 0.0046549 | -0.012487 | 0.0011025 | 0.053936 | -0.004596 | 0.06293 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058886 | 0.022395 | 0.059376 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1517 | 56.3077 | -66.8467 | -66.7474 | -0.036271 | -66.7865 | 56.1528 | 56.3305 | 56.1643 | -67.0607 | -0.10931 | -0.048515 | 0.003832 | -0.008639 | 0.10067 | -0.15322 | 0.002751 | -0.3233 | -0.15217 | -0.010019 | -0.049103 | 0.2742 | 0.025585 | -0.14062 | 122.9938 | 122.8891 | 123.045 | 66.7021 | -123.1516 | 122.8901 | 123.0679 | 122.9017 | 66.7011 | -123.3656
1059.7969 | 123.143 | -66.7328 | 56.3324 | 0.012286 | -0.012914 | 0.0013163 | 0.053722 | -0.0048096 | 0.062289 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058245 | 0.022181 | 0.058949 | -66.7335 | -0.035222 | -66.746 | 56.2518 | 56.1471 | 56.3123 | -66.8513 | -66.7474 | -0.031692 | -66.7865 | 56.1528 | 56.3259 | 56.1552 | -67.0607 | -0.11846 | -0.080558 | -0.000746 | -0.013217 | 0.10525 | -0.18527 | -0.020135 | -0.32788 | -0.17964 | -0.014597 | -0.053681 | 0.2742 | -0.006458 | -0.17724 | 122.9846 | 122.8799 | 123.0451 | 66.6976 | -123.1836 | 122.8855 | 123.0587 | 122.8879 | 66.7011 | -123.3931
1060.8594 | 123.1934 | -66.7282 | 56.337 | 0.012286 | -0.013342 | 0.0011025 | 0.053722 | -0.0050232 | 0.06293 | 0.0077831 | -0.0019847 | -0.00055553 | 0.058886 | 0.022395 | 0.059376 | -66.7244 | -0.030644 | -66.7597 | 56.2473 | 56.1517 | 56.3168 | -66.8467 | -66.7565 | -0.040849 | -66.7773 | 56.1573 | 56.3305 | 56.1552 | -67.0561 | -0.11846 | -0.089715 | 0.003833 | -0.03153 | 0.086932 | -0.18526 | -0.020135 | -0.32788 | -0.17964 | -0.028332 | -0.049101 | 0.27878 | -0.006458 | -0.18182 | 122.9755 | 122.8799 | 123.0451 | 66.6976 | -123.1836 | 122.8855 | 123.0587 | 122.8834 | 66.6874 | -123.3931
1061.7969 | 123.1842 | -66.7511 | 56.3049 | 0.0046549 | -0.012701 | 0.0011025 | 0.053936 | -0.0050232 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.059099 | 0.022609 | 0.058949 | -66.7427 | -0.039801 | -66.7506 | 56.2518 | 56.1471 | 56.3077 | -66.8467 | -66.7565 | -0.040849 | -66.7773 | 56.1619 | 56.3305 | 56.1506 | -67.0652 | -0.095573 | -0.053093 | 0.008408 | 0.000516 | 0.096089 | -0.1578 | 0.002751 | -0.31415 | -0.14301 | -0.005443 | -0.026212 | 0.28794 | 0.025585 | -0.15436 | 123.0029 | 122.8982 | 123.0588 | 66.7113 | -123.1516 | 122.913 | 123.0816 | 122.9017 | 66.7103 | -123.3702
1062.7969 | 123.1979 | -66.7282 | 56.3278 | 0.0046549 | -0.012914 | 0.00088894 | 0.053936 | -0.0048096 | 0.06293 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058672 | 0.022181 | 0.058949 | -66.7381 | -0.044379 | -66.7506 | 56.2564 | 56.1563 | 56.3077 | -66.8558 | -66.7474 | -0.036271 | -66.7819 | 56.1573 | 56.3305 | 56.1643 | -67.0607 | -0.12762 | -0.071403 | -0.009902 | -0.022373 | 0.10525 | -0.17153 | -0.020137 | -0.33246 | -0.17048 | -0.019175 | -0.05368 | 0.27878 | 0.002697 | -0.16351 | 122.9846 | 122.8845 | 123.0359 | 66.6838 | -123.1837 | 122.8855 | 123.0587 | 122.8925 | 66.6919 | -123.3885
1063.8594 | 123.1659 | -66.7419 | 56.3141 | 0.0046549 | -0.012701 | 0.0015299 | 0.053722 | -0.004596 | 0.06293 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058886 | 0.022181 | 0.058735 | -66.7381 | -0.030644 | -66.7506 | 56.2473 | 56.1426 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1573 | 56.3259 | 56.1597 | -67.0698 | -0.10931 | -0.066827 | 0.003831 | -0.00864 | 0.10067 | -0.17153 | 0.002753 | -0.32788 | -0.15675 | -0.01002 | -0.044526 | 0.28336 | 0.011852 | -0.15436 | 122.9892 | 122.8845 | 123.0588 | 66.7113 | -123.1653 | 122.8993 | 123.0679 | 122.9017 | 66.7011 | -123.3839
1064.7969 | 123.175 | -66.7374 | 56.3141 | -0.0029761 | -0.012914 | 0.00088894 | 0.053722 | -0.0048096 | 0.063144 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058672 | 0.022395 | 0.058949 | -66.729 | -0.035222 | -66.7506 | 56.2564 | 56.1471 | 56.3168 | -66.8558 | -66.7611 | -0.040849 | -66.7819 | 56.1619 | 56.3214 | 56.1597 | -67.0561 | -0.11846 | -0.05767 | 0.00841 | -0.013217 | 0.10525 | -0.16696 | 0.002753 | -0.31872 | -0.15217 | -0.023755 | -0.044524 | 0.2742 | 0.007273 | -0.15436 | 122.9938 | 122.8845 | 123.0542 | 66.7021 | -123.1699 | 122.8993 | 123.0587 | 122.8971 | 66.6965 | -123.3702
1065.7969 | 123.1934 | -66.7374 | 56.3232 | 0.0046549 | -0.012914 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058672 | 0.022395 | 0.058735 | -66.7381 | -0.035222 | -66.7552 | 56.2564 | 56.1517 | 56.3123 | -66.8604 | -66.7565 | -0.031692 | -66.7773 | 56.1528 | 56.3305 | 56.1597 | -67.0652 | -0.12304 | -0.066825 | -0.000746 | -0.017795 | 0.10525 | -0.17153 | -0.01098 | -0.32788 | -0.17048 | -0.019176 | -0.039945 | 0.28794 | 0.007275 | -0.16351 | 122.9938 | 122.8891 | 123.0496 | 66.7021 | -123.1837 | 122.8901 | 123.0679 | 122.8971 | 66.7057 | -123.3885
1066.7969 | 123.1842 | -66.7374 | 56.2958 | 0.0046549 | -0.012487 | 0.00088894 | 0.053936 | -0.0048096 | 0.063144 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058672 | 0.022395 | 0.059163 | -66.7381 | -0.030644 | -66.7506 | 56.2518 | 56.1609 | 56.3123 | -66.8467 | -66.7474 | -0.036271 | -66.7819 | 56.1573 | 56.3259 | 56.1597 | -67.0561 | -0.10931 | -0.043937 | -0.000746 | -0.013217 | 0.096089 | -0.13491 | 0.016486 | -0.31872 | -0.13844 | -0.010019 | -0.044524 | 0.2742 | 0.030163 | -0.13604 | 122.9892 | 122.8982 | 123.0496 | 66.7067 | -123.1424 | 122.8947 | 123.0633 | 122.8971 | 66.7011 | -123.3519
1067.7969 | 123.1796 | -66.7786 | 56.337 | -0.0029761 | -0.013128 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.022609 | 0.059163 | -66.7381 | -0.035222 | -66.7414 | 56.2518 | 56.1563 | 56.3123 | -66.8604 | -66.7565 | -0.040849 | -66.7819 | 56.1528 | 56.3305 | 56.1597 | -67.0515 | -0.081844 | -0.085136 | 0.040452 | 0.037137 | 0.11898 | -0.18069 | -0.024713 | -0.27295 | -0.18422 | 0.022022 | -0.003326 | 0.26962 | -0.006458 | -0.17724 | 123.0304 | 122.9349 | 123.0908 | 66.7433 | -123.1974 | 122.9313 | 123.1091 | 122.9383 | 66.7377 | -123.3885
1068.7969 | 123.2071 | -66.7511 | 56.3187 | -0.010607 | -0.012914 | 0.0013163 | 0.053936 | -0.0048096 | 0.06293 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058672 | 0.022395 | 0.058735 | -66.7381 | -0.035222 | -66.746 | 56.261 | 56.1563 | 56.3077 | -66.8513 | -66.752 | -0.036271 | -66.7819 | 56.1619 | 56.3305 | 56.1552 | -67.0607 | -0.10015 | -0.05767 | 0.012987 | 0.005094 | 0.10525 | -0.16238 | -0.010982 | -0.30957 | -0.15675 | -0.000864 | -0.030791 | 0.27878 | 0.011852 | -0.16351 | 123.0121 | 122.9074 | 123.0588 | 66.7159 | -123.1699 | 122.913 | 123.0816 | 122.9063 | 66.7148 | -123.3793
1069.7969 | 123.1888 | -66.7374 | 56.2866 | 0.0046549 | -0.012914 | 0.0011025 | 0.053936 | -0.0050232 | 0.062503 | 0.00015261 | -0.0015573 | -0.0011965 | 0.058672 | 0.022181 | 0.058949 | -66.7244 | -0.039801 | -66.7414 | 56.2564 | 56.1517 | 56.3123 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1528 | 56.3305 | 56.1506 | -67.0607 | -0.11389 | -0.030204 | 0.012989 | -0.004061 | 0.10982 | -0.13491 | 0.025641 | -0.3233 | -0.13386 | -0.010019 | -0.044524 | 0.27878 | 0.043896 | -0.13605 | 122.9938 | 122.8891 | 123.0496 | 66.6976 | -123.1379 | 122.8901 | 123.0679 | 122.8879 | 66.6965 | -123.3473
1070.7969 | 123.1567 | -66.7648 | 56.282 | -0.010607 | -0.013128 | 0.0011025 | 0.053936 | -0.0043822 | 0.063144 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058672 | 0.022395 | 0.058949 | -66.7335 | -0.026065 | -66.7506 | 56.2564 | 56.1517 | 56.3123 | -66.8467 | -66.7565 | -0.040849 | -66.7819 | 56.1528 | 56.3214 | 56.1552 | -67.0607 | -0.08184 | -0.025626 | 0.031298 | 0.014249 | 0.096089 | -0.13033 | 0.030219 | -0.29584 | -0.12928 | 0.00829 | -0.017058 | 0.27878 | 0.039317 | -0.12689 | 123.0212 | 122.9165 | 123.0771 | 66.7388 | -123.1287 | 122.9176 | 123.0862 | 122.92 | 66.724 | -123.3427
1071.8594 | 123.3124 | -66.7007 | 56.282 | -0.0029761 | -0.012914 | 0.0011025 | 0.054149 | -0.0043822 | 0.06293 | 0.00015261 | -0.0017711 | -0.00034193 | 0.058458 | 0.022609 | 0.059163 | -66.7335 | -0.035222 | -66.7414 | 56.2564 | 56.1517 | 56.3077 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3259 | 56.1552 | -67.0652 | -0.15051 | -0.025626 | -0.032789 | -0.040682 | 0.10982 | -0.13033 | 0.02564 | -0.3645 | -0.1247 | -0.04664 | -0.081145 | 0.28336 | 0.043896 | -0.12689 | 122.9572 | 122.8525 | 123.0084 | 66.6655 | -123.1333 | 122.8581 | 123.0267 | 122.8559 | 66.6599 | -123.3473
1072.7969 | 123.1338 | -66.7511 | 56.3141 | -0.010607 | -0.013128 | 0.0011025 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0017711 | -0.00055553 | 0.058886 | 0.022395 | 0.058949 | -66.7335 | -0.026065 | -66.7552 | 56.2564 | 56.1563 | 56.3123 | -66.8558 | -66.7428 | -0.036271 | -66.7819 | 56.1573 | 56.3351 | 56.1597 | -67.0607 | -0.10473 | -0.05767 | 0.017565 | -0.004062 | 0.10067 | -0.1578 | -0.001825 | -0.30957 | -0.15675 | 0.008293 | -0.030791 | 0.27878 | 0.021009 | -0.15436 | 123.0075 | 122.9074 | 123.0634 | 66.725 | -123.1699 | 122.9084 | 123.0862 | 122.9108 | 66.7148 | -123.3748
1073.7969 | 123.1842 | -66.7557 | 56.337 | -0.010607 | -0.013342 | 0.0011025 | 0.054149 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058458 | 0.022395 | 0.059163 | -66.7381 | -0.030644 | -66.7506 | 56.2564 | 56.1517 | 56.3123 | -66.8467 | -66.752 | -0.040849 | -66.7773 | 56.1573 | 56.3305 | 56.1552 | -67.0607 | -0.090996 | -0.080558 | 0.017564 | 0.005093 | 0.096089 | -0.18526 | -0.024713 | -0.30499 | -0.17964 | 0.003713 | -0.021635 | 0.28336 | -0.006458 | -0.18182 | 123.0121 | 122.9074 | 123.0679 | 66.725 | -123.1836 | 122.913 | 123.0862 | 122.9108 | 66.7148 | -123.3976
1074.7969 | 123.1567 | -66.7648 | 56.3278 | 0.0046549 | -0.012914 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058672 | 0.022609 | 0.058949 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1609 | 56.3214 | -66.8558 | -66.7474 | -0.031692 | -66.7819 | 56.1619 | 56.3305 | 56.1643 | -67.0652 | -0.090998 | -0.066825 | 0.040455 | 0.018827 | 0.10983 | -0.16695 | -0.006401 | -0.30042 | -0.1659 | 0.017447 | -0.017058 | 0.28336 | 0.002697 | -0.16351 | 123.0258 | 122.9257 | 123.0863 | 66.7296 | -123.1837 | 122.9267 | 123.0953 | 122.9291 | 66.7331 | -123.3931
1075.8594 | 123.1659 | -66.7419 | 56.3095 | 0.0046549 | -0.013128 | 0.00088894 | 0.053722 | -0.004596 | 0.06293 | -0.0074779 | -0.0017711 | -0.0011965 | 0.058458 | 0.023036 | 0.058949 | -66.7335 | -0.035222 | -66.7597 | 56.261 | 56.1471 | 56.3123 | -66.8513 | -66.7565 | -0.040849 | -66.791 | 56.1528 | 56.3305 | 56.1643 | -67.0652 | -0.10931 | -0.048514 | 0.008409 | -0.017797 | 0.091511 | -0.16238 | 0.002753 | -0.3233 | -0.15675 | -0.014599 | -0.049104 | 0.2742 | 0.021008 | -0.1452 | 123.0029 | 122.8891 | 123.0542 | 66.7067 | -123.1608 | 122.8947 | 123.0725 | 122.9063 | 66.7011 | -123.3748
1076.7969 | 123.1979 | -66.7511 | 56.3187 | -0.0029761 | -0.013128 | 0.0013163 | 0.054363 | -0.004596 | 0.063144 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058886 | 0.022395 | 0.058735 | -66.7335 | -0.035222 | -66.7597 | 56.261 | 56.1563 | 56.3077 | -66.8513 | -66.7474 | -0.045428 | -66.7865 | 56.1482 | 56.3214 | 56.1689 | -67.0607 | -0.10015 | -0.05767 | 0.017565 | -0.008641 | 0.091511 | -0.16238 | -0.010982 | -0.30957 | -0.17048 | 0.003714 | -0.03537 | 0.2742 | 0.002695 | -0.14978 | 123.0121 | 122.9074 | 123.0588 | 66.7159 | -123.1699 | 122.8993 | 123.0725 | 122.92 | 66.7057 | -123.3793
1077.7969 | 123.1338 | -66.7465 | 56.3095 | 0.0046549 | -0.013128 | 0.0013163 | 0.053936 | -0.0050232 | 0.062503 | 0.015414 | -0.0019847 | -0.00098273 | 0.058672 | 0.022609 | 0.058949 | -66.7381 | -0.030644 | -66.7597 | 56.2564 | 56.1426 | 56.3168 | -66.8558 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3351 | 56.1552 | -67.0607 | -0.10931 | -0.053092 | 0.008409 | -0.013219 | 0.09609 | -0.16696 | 0.007331 | -0.31415 | -0.15217 | -0.005442 | -0.039948 | 0.2742 | 0.025587 | -0.15436 | 123.0029 | 122.8891 | 123.0634 | 66.7159 | -123.1653 | 122.9039 | 123.0816 | 122.9017 | 66.7103 | -123.3702
1078.8594 | 123.1842 | -66.7191 | 56.3416 | 0.012286 | -0.013128 | 0.00088894 | 0.054149 | -0.004596 | 0.062717 | 0.015414 | -0.0021983 | -0.00098273 | 0.058672 | 0.022395 | 0.059163 | -66.7381 | -0.039801 | -66.7506 | 56.2518 | 56.1426 | 56.3077 | -66.8513 | -66.752 | -0.045428 | -66.791 | 56.1573 | 56.3305 | 56.1597 | -67.0607 | -0.1322 | -0.089714 | -0.019057 | -0.031528 | 0.10067 | -0.199 | -0.03387 | -0.34161 | -0.18421 | -0.032908 | -0.071992 | 0.26962 | -0.011036 | -0.18182 | 122.9709 | 122.8616 | 123.0267 | 66.6793 | -123.1928 | 122.8764 | 123.0496 | 122.8788 | 66.6736 | -123.4022
1079.7969 | 123.1522 | -66.7511 | 56.3049 | -0.0029761 | -0.012914 | 0.00088894 | 0.053722 | -0.004596 | 0.062503 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058886 | 0.022395 | 0.059163 | -66.7335 | -0.035222 | -66.7552 | 56.2564 | 56.1517 | 56.3123 | -66.8513 | -66.7565 | -0.031692 | -66.7773 | 56.1573 | 56.3214 | 56.1414 | -67.0561 | -0.10015 | -0.048515 | 0.017565 | -0.004062 | 0.09609 | -0.15322 | 0.00733 | -0.30499 | -0.14759 | -0.005443 | -0.026212 | 0.27878 | 0.016428 | -0.16351 | 123.0075 | 122.9028 | 123.0634 | 66.7159 | -123.1562 | 122.9084 | 123.0725 | 122.8925 | 66.7194 | -123.361
1080.7969 | 123.2849 | -66.7053 | 56.2637 | -0.0029761 | -0.013342 | 0.0011025 | 0.054149 | -0.004596 | 0.06293 | 0.00015261 | -0.0017711 | -0.00055553 | 0.058672 | 0.022609 | 0.058949 | -66.7335 | -0.030644 | -66.7506 | 56.2518 | 56.1471 | 56.3123 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1573 | 56.3214 | 56.1597 | -67.0607 | -0.14593 | -0.011894 | -0.028212 | -0.045261 | 0.10067 | -0.1166 | 0.048529 | -0.35535 | -0.10639 | -0.046641 | -0.081147 | 0.2742 | 0.057627 | -0.104 | 122.9572 | 122.8525 | 123.0176 | 66.6747 | -123.115 | 122.8627 | 123.0267 | 122.8651 | 66.6645 | -123.3244
1081.8594 | 123.1842 | -66.7419 | 56.3644 | 0.0046549 | -0.012914 | 0.00067514 | 0.054149 | -0.0050232 | 0.06293 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058672 | 0.022822 | 0.058735 | -66.7381 | -0.035222 | -66.746 | 56.2564 | 56.1517 | 56.3214 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1573 | 56.3351 | 56.178 | -67.0561 | -0.10931 | -0.10802 | 0.003831 | -0.004062 | 0.10525 | -0.21273 | -0.043022 | -0.31415 | -0.2071 | -0.01002 | -0.044526 | 0.26962 | -0.029345 | -0.18639 | 122.9984 | 122.8937 | 123.0634 | 66.7067 | -123.2157 | 122.8993 | 123.077 | 122.92 | 66.7011 | -123.4205
1082.7969 | 123.3398 | -66.7236 | 56.2637 | -0.0029761 | -0.013555 | 0.00088894 | 0.053936 | -0.004596 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058886 | 0.023036 | 0.058735 | -66.729 | -0.039801 | -66.7506 | 56.2564 | 56.1609 | 56.3123 | -66.8513 | -66.752 | -0.045428 | -66.7819 | 56.1619 | 56.3351 | 56.1597 | -67.0561 | -0.12762 | -0.007316 | -0.005323 | -0.02695 | 0.10067 | -0.10287 | 0.048529 | -0.33246 | -0.10182 | -0.02833 | -0.058257 | 0.2742 | 0.071363 | -0.104 | 122.9801 | 122.8845 | 123.0359 | 66.6838 | -123.115 | 122.8856 | 123.0587 | 122.8834 | 66.6782 | -123.3198
1083.7969 | 123.2025 | -66.7374 | 56.3004 | -0.010607 | -0.013342 | 0.00088894 | 0.053722 | -0.0050232 | 0.063144 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058458 | 0.022822 | 0.059163 | -66.7335 | -0.035222 | -66.7552 | 56.261 | 56.1471 | 56.3123 | -66.8513 | -66.752 | -0.031692 | -66.7819 | 56.1573 | 56.3305 | 56.146 | -67.0561 | -0.11389 | -0.039359 | 0.003832 | -0.017795 | 0.09609 | -0.15322 | 0.011908 | -0.31872 | -0.14301 | -0.014597 | -0.044524 | 0.2742 | 0.030163 | -0.15436 | 122.9984 | 122.8845 | 123.0496 | 66.7021 | -123.1516 | 122.8947 | 123.0679 | 122.8834 | 66.7057 | -123.3564
1084.7969 | 123.2712 | -66.7236 | 56.2729 | -0.010607 | -0.013128 | 0.00067514 | 0.054149 | -0.0050232 | 0.062503 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058672 | 0.022609 | 0.059163 | -66.7381 | -0.026065 | -66.746 | 56.2564 | 56.138 | 56.3077 | -66.8467 | -66.752 | -0.045428 | -66.791 | 56.1619 | 56.3305 | 56.1689 | -67.0652 | -0.12304 | -0.016471 | -0.014479 | -0.022372 | 0.10067 | -0.13491 | 0.034795 | -0.34161 | -0.11097 | -0.02833 | -0.067414 | 0.2742 | 0.057629 | -0.104 | 122.9801 | 122.8616 | 123.0313 | 66.6976 | -123.1196 | 122.8856 | 123.0542 | 122.8925 | 66.6782 | -123.3381
1085.8594 | 123.2483 | -66.7694 | 56.2958 | -0.0029761 | -0.013128 | 0.00088894 | 0.054577 | -0.0050232 | 0.062717 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058672 | 0.022822 | 0.058949 | -66.7335 | -0.030644 | -66.7597 | 56.2518 | 56.138 | 56.3077 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3259 | 56.146 | -67.0607 | -0.081842 | -0.043937 | 0.035875 | 0.009669 | 0.091511 | -0.1578 | 0.011907 | -0.29126 | -0.13386 | 0.017446 | -0.01706 | 0.2742 | 0.030163 | -0.14978 | 123.0212 | 122.9074 | 123.0771 | 66.7388 | -123.147 | 122.9313 | 123.0953 | 122.9154 | 66.7286 | -123.3564
1086.7969 | 123.2574 | -66.7236 | 56.3095 | 0.0046549 | -0.013342 | 0.00088894 | 0.054363 | -0.0050232 | 0.063144 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058672 | 0.022822 | 0.059163 | -66.7427 | -0.035222 | -66.7506 | 56.2564 | 56.1471 | 56.3123 | -66.8467 | -66.7611 | -0.036271 | -66.7956 | 56.1619 | 56.3305 | 56.1597 | -67.0607 | -0.12304 | -0.053092 | -0.019058 | -0.02695 | 0.096089 | -0.16238 | 0.002753 | -0.33704 | -0.14759 | -0.037488 | -0.071993 | 0.26504 | 0.021008 | -0.14978 | 122.9801 | 122.8708 | 123.0359 | 66.6884 | -123.1562 | 122.8856 | 123.0542 | 122.8834 | 66.6874 | -123.3702
1087.7969 | 123.2712 | -66.7328 | 56.2592 | 0.0046549 | -0.013769 | 0.0011025 | 0.054149 | -0.0041686 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058886 | 0.022822 | 0.059163 | -66.7335 | -0.035222 | -66.746 | 56.2518 | 56.1426 | 56.3123 | -66.8467 | -66.7565 | -0.036271 | -66.7773 | 56.1573 | 56.3259 | 56.1414 | -67.0607 | -0.11388 | -0.007316 | -0.000746 | -0.013217 | 0.10067 | -0.1166 | 0.053107 | -0.32788 | -0.10182 | -0.023754 | -0.044523 | 0.28336 | 0.066784 | -0.11774 | 122.9846 | 122.8753 | 123.0451 | 66.6976 | -123.1058 | 122.8901 | 123.0587 | 122.8742 | 66.6965 | -123.3198
1088.8594 | 123.2437 | -66.7007 | 56.2912 | 0.0046549 | -0.013342 | 0.00088894 | 0.054149 | -0.0050232 | 0.062717 | -0.0074779 | -0.0017711 | -0.00076913 | 0.058886 | 0.022609 | 0.059163 | -66.7335 | -0.030644 | -66.7414 | 56.2564 | 56.1517 | 56.3077 | -66.8558 | -66.7474 | -0.045428 | -66.791 | 56.1619 | 56.3259 | 56.1506 | -67.0561 | -0.15508 | -0.034782 | -0.032789 | -0.040682 | 0.1144 | -0.13949 | 0.016484 | -0.35534 | -0.12928 | -0.04664 | -0.090302 | 0.26504 | 0.03474 | -0.14062 | 122.9572 | 122.8525 | 123.0084 | 66.6701 | -123.147 | 122.8627 | 123.0267 | 122.8513 | 66.6553 | -123.3473
1089.7969 | 123.2346 | -66.7191 | 56.2866 | 0.0046549 | -0.013128 | 0.0013163 | 0.054363 | -0.0043822 | 0.062503 | 0.015414 | -0.0017711 | -0.00076913 | 0.058886 | 0.022181 | 0.059376 | -66.7335 | -0.035222 | -66.7552 | 56.2564 | 56.1334 | 56.3031 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3214 | 56.1506 | -67.0607 | -0.1322 | -0.030204 | -0.014479 | -0.036106 | 0.09609 | -0.15323 | 0.016483 | -0.34161 | -0.12928 | -0.02833 | -0.062835 | 0.27878 | 0.034739 | -0.13605 | 122.9755 | 122.8525 | 123.0222 | 66.6838 | -123.1379 | 122.8764 | 123.0404 | 122.8696 | 66.6782 | -123.3473
1090.8594 | 123.2483 | -66.7053 | 56.337 | -0.0029761 | -0.013128 | 0.0011025 | 0.054149 | -0.0050232 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058672 | 0.022609 | 0.059163 | -66.7427 | -0.035222 | -66.7506 | 56.2518 | 56.1609 | 56.3123 | -66.8513 | -66.7474 | -0.050007 | -66.7865 | 56.1573 | 56.3259 | 56.1506 | -67.0561 | -0.14593 | -0.085136 | -0.037369 | -0.045261 | 0.10067 | -0.17611 | -0.024713 | -0.35077 | -0.17964 | -0.042063 | -0.081147 | 0.26962 | -0.011036 | -0.1864 | 122.9572 | 122.8662 | 123.0176 | 66.6701 | -123.1882 | 122.8627 | 123.0313 | 122.8559 | 66.6553 | -123.3931
1091.7969 | 123.2117 | -66.7099 | 56.2912 | -0.0029761 | -0.013342 | 0.0011025 | 0.054149 | -0.0048096 | 0.062503 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058672 | 0.022822 | 0.059163 | -66.7335 | -0.030644 | -66.746 | 56.2564 | 56.1517 | 56.3123 | -66.8467 | -66.752 | -0.040849 | -66.791 | 56.1573 | 56.3305 | 56.1597 | -67.0515 | -0.13677 | -0.034782 | -0.023634 | -0.036105 | 0.10067 | -0.13949 | 0.021063 | -0.34161 | -0.13386 | -0.042063 | -0.081147 | 0.26046 | 0.039318 | -0.13147 | 122.9663 | 122.8616 | 123.0222 | 66.6793 | -123.1379 | 122.8672 | 123.0404 | 122.8696 | 66.6691 | -123.3427
1092.7969 | 123.2895 | -66.7191 | 56.3004 | -0.0029761 | -0.013128 | 0.00088894 | 0.054363 | -0.0048096 | 0.06293 | -0.0074779 | -0.0015573 | -0.00076913 | 0.058672 | 0.022822 | 0.059163 | -66.7381 | -0.035222 | -66.7506 | 56.2564 | 56.1426 | 56.3168 | -66.8375 | -66.7565 | -0.036271 | -66.7865 | 56.1619 | 56.3259 | 56.1597 | -67.0652 | -0.11846 | -0.043937 | -0.019057 | -0.031528 | 0.086931 | -0.1578 | 0.016486 | -0.34619 | -0.13844 | -0.037487 | -0.067414 | 0.27878 | 0.025585 | -0.14062 | 122.9755 | 122.8616 | 123.0359 | 66.6838 | -123.1379 | 122.881 | 123.045 | 122.8788 | 66.6828 | -123.3656
1093.7969 | 123.2437 | -66.7191 | 56.3049 | 0.0046549 | -0.013342 | 0.0011025 | 0.054149 | -0.0050232 | 0.063144 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058886 | 0.022822 | 0.059376 | -66.7381 | -0.030644 | -66.7552 | 56.2564 | 56.1471 | 56.3123 | -66.8467 | -66.7565 | -0.040849 | -66.7865 | 56.1573 | 56.3259 | 56.1552 | -67.0652 | -0.12762 | -0.048515 | -0.019057 | -0.036106 | 0.091511 | -0.1578 | 0.00733 | -0.34619 | -0.14759 | -0.037487 | -0.067414 | 0.27878 | 0.021007 | -0.14978 | 122.9755 | 122.8662 | 123.0313 | 66.6884 | -123.1516 | 122.8764 | 123.045 | 122.8742 | 66.6782 | -123.3702
1094.7969 | 123.3032 | -66.6962 | 56.3095 | 0.0046549 | -0.013342 | 0.00088894 | 0.053936 | -0.0043822 | 0.062717 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058458 | 0.022822 | 0.058949 | -66.7427 | -0.035222 | -66.7414 | 56.2564 | 56.1517 | 56.3077 | -66.8467 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3259 | 56.1597 | -67.0607 | -0.1505 | -0.053092 | -0.046524 | -0.04526 | 0.10524 | -0.1578 | -0.001826 | -0.3645 | -0.15217 | -0.055796 | -0.090302 | 0.2742 | 0.01643 | -0.14978 | 122.9526 | 122.8479 | 123.0038 | 66.6609 | -123.1562 | 122.8535 | 123.0221 | 122.8559 | 66.6599 | -123.3702
1095.7969 | 123.317 | -66.6916 | 56.2958 | 0.0046549 | -0.013555 | 0.0011025 | 0.053936 | -0.004596 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.023036 | 0.058949 | -66.7381 | -0.048958 | -66.7414 | 56.2564 | 56.1517 | 56.3123 | -66.8467 | -66.752 | -0.040849 | -66.791 | 56.1528 | 56.3259 | 56.1552 | -67.0607 | -0.15508 | -0.039359 | -0.046523 | -0.049838 | 0.10524 | -0.14406 | 0.016486 | -0.36908 | -0.14302 | -0.060374 | -0.099458 | 0.26962 | 0.030163 | -0.14062 | 122.948 | 122.8433 | 123.0039 | 66.6426 | -123.1424 | 122.8443 | 123.0175 | 122.8467 | 66.6507 | -123.3564
1096.8594 | 123.2162 | -66.7328 | 56.2958 | -0.0029761 | -0.013128 | 0.0011025 | 0.053936 | -0.0043822 | 0.062717 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058672 | 0.022822 | 0.058735 | -66.7335 | -0.035222 | -66.7368 | 56.2518 | 56.1471 | 56.3077 | -66.8513 | -66.7565 | -0.036271 | -66.7819 | 56.1573 | 56.3259 | 56.1506 | -67.0607 | -0.11846 | -0.043937 | -0.000746 | -0.00406 | 0.1144 | -0.14864 | 0.011907 | -0.32788 | -0.13844 | -0.023754 | -0.049102 | 0.27878 | 0.030163 | -0.1452 | 122.9846 | 122.8799 | 123.0405 | 66.6976 | -123.147 | 122.8901 | 123.0587 | 122.8834 | 66.6965 | -123.3564
1097.7969 | 123.2391 | -66.6962 | 56.2912 | 0.0046549 | -0.013128 | 0.0011025 | 0.054363 | -0.004596 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.022822 | 0.059376 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1563 | 56.3123 | -66.8421 | -66.752 | -0.050007 | -66.7819 | 56.1528 | 56.3259 | 56.1506 | -67.0652 | -0.14593 | -0.034782 | -0.037367 | -0.049838 | 0.096088 | -0.13491 | 0.021063 | -0.36908 | -0.13844 | -0.055796 | -0.085723 | 0.28336 | 0.03474 | -0.14062 | 122.9526 | 122.8525 | 123.0084 | 66.6609 | -123.1333 | 122.8489 | 123.0221 | 122.8467 | 66.6462 | -123.3564
1098.8594 | 123.2574 | -66.7145 | 56.2958 | 0.0046549 | -0.013555 | 0.0011025 | 0.054363 | -0.0048096 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058672 | 0.022822 | 0.058949 | -66.729 | -0.035222 | -66.746 | 56.2518 | 56.1563 | 56.3123 | -66.8604 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3305 | 56.146 | -67.0652 | -0.14593 | -0.043937 | -0.014478 | -0.031527 | 0.1144 | -0.13949 | 0.016486 | -0.35077 | -0.13844 | -0.032907 | -0.067412 | 0.28336 | 0.034741 | -0.14978 | 122.9663 | 122.8708 | 123.0267 | 66.6793 | -123.1562 | 122.8718 | 123.045 | 122.8605 | 66.6736 | -123.361
1099.7969 | 123.2849 | -66.6916 | 56.2912 | 0.0046549 | -0.013342 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058672 | 0.023036 | 0.058735 | -66.7335 | -0.039801 | -66.746 | 56.2518 | 56.1517 | 56.3168 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3305 | 56.1506 | -67.0607 | -0.15966 | -0.03936 | -0.041945 | -0.054416 | 0.10525 | -0.13949 | 0.025641 | -0.36908 | -0.13386 | -0.055796 | -0.090301 | 0.27878 | 0.039318 | -0.14062 | 122.9434 | 122.8433 | 123.0084 | 66.6518 | -123.1424 | 122.8489 | 123.0221 | 122.8422 | 66.6507 | -123.3519
1100.7969 | 123.1979 | -66.7419 | 56.3095 | -0.0029761 | -0.013128 | 0.00088894 | 0.053936 | -0.0050232 | 0.062289 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058458 | 0.022609 | 0.058308 | -66.7335 | -0.030644 | -66.7414 | 56.2564 | 56.1517 | 56.3214 | -66.8558 | -66.7474 | -0.040849 | -66.7819 | 56.1528 | 56.3259 | 56.1552 | -67.0607 | -0.11389 | -0.053092 | 0.008409 | 0.000516 | 0.1144 | -0.1578 | 0.01191 | -0.31873 | -0.15675 | -0.005442 | -0.039947 | 0.27878 | 0.01643 | -0.15436 | 122.9984 | 122.8937 | 123.0634 | 66.7113 | -123.1653 | 122.8947 | 123.0679 | 122.8971 | 66.7011 | -123.3702
1101.7969 | 123.2941 | -66.6824 | 56.282 | -0.0029761 | -0.013555 | 0.0011025 | 0.054149 | -0.004596 | 0.062289 | 0.0077831 | -0.0017711 | -0.00055553 | 0.058245 | 0.022609 | 0.058522 | -66.7381 | -0.035222 | -66.746 | 56.2564 | 56.138 | 56.3123 | -66.8513 | -66.7565 | -0.036271 | -66.7865 | 56.1573 | 56.3259 | 56.1552 | -67.0652 | -0.16882 | -0.025626 | -0.055678 | -0.063571 | 0.10525 | -0.14407 | 0.030219 | -0.38281 | -0.1247 | -0.074108 | -0.10403 | 0.27878 | 0.043896 | -0.12689 | 122.9389 | 122.8204 | 122.9947 | 66.6472 | -123.1333 | 122.8398 | 123.0084 | 122.8376 | 66.6462 | -123.3473
1102.7969 | 123.1705 | -66.7557 | 56.3461 | 0.0046549 | -0.013342 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058245 | 0.022822 | 0.058949 | -66.7335 | -0.039801 | -66.746 | 56.2564 | 56.1563 | 56.3123 | -66.8375 | -66.752 | -0.045428 | -66.7865 | 56.1619 | 56.3351 | 56.1689 | -67.0607 | -0.081838 | -0.089713 | 0.022142 | 0.009671 | 0.091509 | -0.18984 | -0.033868 | -0.30499 | -0.18421 | 0.003713 | -0.030793 | 0.2742 | -0.011034 | -0.17724 | 123.0121 | 122.912 | 123.0679 | 66.7159 | -123.1836 | 122.9176 | 123.0908 | 122.9246 | 66.7102 | -123.4068
1103.8594 | 123.2986 | -66.6916 | 56.2866 | -0.0029761 | -0.013555 | 0.0015299 | 0.054149 | -0.0048096 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058458 | 0.02325 | 0.058735 | -66.7381 | -0.035222 | -66.7506 | 56.2564 | 56.1426 | 56.3123 | -66.8467 | -66.7428 | -0.031692 | -66.7819 | 56.1528 | 56.3259 | 56.1552 | -67.0607 | -0.15508 | -0.030204 | -0.046523 | -0.058994 | 0.096089 | -0.14407 | 0.025641 | -0.36908 | -0.13386 | -0.051217 | -0.090301 | 0.27878 | 0.039318 | -0.13147 | 122.948 | 122.8341 | 123.0039 | 66.6564 | -123.1333 | 122.8443 | 123.0175 | 122.8467 | 66.6599 | -123.3473
1104.7969 | 123.1247 | -66.7145 | 56.3644 | -0.0029761 | -0.013342 | 0.00088894 | 0.053722 | -0.0048096 | 0.06293 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058672 | 0.023036 | 0.058735 | -66.7335 | -0.039801 | -66.7414 | 56.261 | 56.1517 | 56.3168 | -66.8467 | -66.752 | -0.045428 | -66.7865 | 56.1665 | 56.3351 | 56.1552 | -67.0652 | -0.13219 | -0.10345 | -0.019056 | -0.026949 | 0.10524 | -0.21273 | -0.047601 | -0.35077 | -0.19794 | -0.037485 | -0.071991 | 0.27878 | -0.029345 | -0.20929 | 122.9755 | 122.8662 | 123.0313 | 66.6747 | -123.2111 | 122.881 | 123.0496 | 122.8696 | 66.669 | -123.4297
1105.8594 | 123.2483 | -66.7191 | 56.2637 | -0.0029761 | -0.013342 | 0.00088894 | 0.053936 | -0.0048096 | 0.062717 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058458 | 0.02325 | 0.058735 | -66.729 | -0.035222 | -66.7368 | 56.2518 | 56.1563 | 56.3168 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1665 | 56.3259 | 56.1643 | -67.0561 | -0.1322 | -0.011894 | -0.009901 | -0.017793 | 0.1144 | -0.10744 | 0.053107 | -0.33703 | -0.097237 | -0.02833 | -0.062835 | 0.2742 | 0.062206 | -0.099422 | 122.9709 | 122.8753 | 123.0359 | 66.6838 | -123.115 | 122.8856 | 123.045 | 122.8834 | 66.6782 | -123.3198
1106.7969 | 123.1567 | -66.7236 | 56.3461 | 0.0046549 | -0.013555 | 0.0011025 | 0.053936 | -0.0050232 | 0.062717 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058245 | 0.022609 | 0.058949 | -66.7381 | -0.039801 | -66.746 | 56.2564 | 56.1609 | 56.3168 | -66.8558 | -66.7474 | -0.036271 | -66.7819 | 56.1619 | 56.3305 | 56.1552 | -67.0744 | -0.1322 | -0.089713 | -0.014479 | -0.022372 | 0.10983 | -0.18526 | -0.02929 | -0.35077 | -0.18421 | -0.023752 | -0.058257 | 0.29251 | -0.015613 | -0.19098 | 122.9801 | 122.8845 | 123.0405 | 66.6838 | -123.202 | 122.8856 | 123.0542 | 122.8788 | 66.6874 | -123.4205
1107.7969 | 123.1522 | -66.7374 | 56.3187 | -0.0029761 | -0.013342 | 0.0011025 | 0.053722 | -0.0048096 | 0.062503 | 0.0077831 | -0.0019847 | -0.00055553 | 0.058458 | 0.02325 | 0.058735 | -66.7381 | -0.039801 | -66.7414 | 56.2564 | 56.1517 | 56.3168 | -66.8513 | -66.7428 | -0.036271 | -66.7773 | 56.1573 | 56.3305 | 56.146 | -67.0561 | -0.11389 | -0.062248 | -0.000746 | -0.004061 | 0.10982 | -0.16695 | -0.001825 | -0.31872 | -0.16133 | -0.00544 | -0.039945 | 0.27878 | 0.011852 | -0.17267 | 122.9938 | 122.8891 | 123.0542 | 66.6976 | -123.1699 | 122.8947 | 123.0679 | 122.8834 | 66.7011 | -123.3748
1108.8594 | 123.2666 | -66.7099 | 56.3049 | -0.010607 | -0.013555 | 0.00088894 | 0.054149 | -0.0048096 | 0.062503 | 0.0077831 | -0.0013437 | -0.00076913 | 0.058672 | 0.023036 | 0.058949 | -66.7381 | -0.035222 | -66.7414 | 56.2473 | 56.1563 | 56.3123 | -66.8421 | -66.7474 | -0.036271 | -66.7819 | 56.1528 | 56.3259 | 56.1414 | -67.0652 | -0.13219 | -0.057672 | -0.028212 | -0.031527 | 0.10067 | -0.14864 | 0.00733 | -0.35535 | -0.15217 | -0.037485 | -0.07199 | 0.28336 | 0.021007 | -0.16351 | 122.9572 | 122.8662 | 123.0222 | 66.6747 | -123.147 | 122.8627 | 123.0358 | 122.8513 | 66.6736 | -123.3702
1109.7969 | 123.175 | -66.7282 | 56.3141 | 0.012286 | -0.013128 | 0.0011025 | 0.054149 | -0.004596 | 0.062289 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058458 | 0.023036 | 0.058735 | -66.7427 | -0.035222 | -66.746 | 56.2473 | 56.1426 | 56.3168 | -66.8467 | -66.752 | -0.040849 | -66.7819 | 56.1573 | 56.3351 | 56.1643 | -67.0652 | -0.11846 | -0.066827 | -0.014481 | -0.017795 | 0.10067 | -0.17153 | 0.002753 | -0.33704 | -0.15675 | -0.023753 | -0.05368 | 0.28336 | 0.021009 | -0.14978 | 122.9755 | 122.8708 | 123.0451 | 66.693 | -123.1608 | 122.8855 | 123.0633 | 122.8925 | 66.6874 | -123.3793
1110.8594 | 123.1476 | -66.7603 | 56.3049 | 0.0046549 | -0.013342 | 0.00088894 | 0.053722 | -0.004596 | 0.062717 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058886 | 0.02325 | 0.058949 | -66.7427 | -0.035222 | -66.7368 | 56.2518 | 56.1563 | 56.3214 | -66.8513 | -66.7428 | -0.040849 | -66.7819 | 56.1619 | 56.3214 | 56.1552 | -67.0652 | -0.090997 | -0.053093 | 0.017563 | 0.023406 | 0.1144 | -0.14864 | 0.016487 | -0.30499 | -0.14301 | 0.017448 | -0.021636 | 0.28336 | 0.016428 | -0.14978 | 123.0121 | 122.9165 | 123.0817 | 66.725 | -123.1562 | 122.9222 | 123.0816 | 122.9154 | 66.7194 | -123.3702
1111.7969 | 123.1796 | -66.7603 | 56.3278 | -0.010607 | -0.013342 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058672 | 0.023036 | 0.058949 | -66.7335 | -0.044379 | -66.7414 | 56.2564 | 56.1609 | 56.3214 | -66.8421 | -66.7474 | -0.040849 | -66.791 | 56.1665 | 56.3305 | 56.1414 | -67.0607 | -0.081839 | -0.071403 | 0.02672 | 0.018827 | 0.10067 | -0.16695 | -0.006401 | -0.30041 | -0.16132 | 0.012869 | -0.030793 | 0.26962 | 0.002697 | -0.1864 | 123.0167 | 122.9211 | 123.0817 | 66.7159 | -123.1699 | 122.9267 | 123.0908 | 122.9017 | 66.7194 | -123.3885
1112.7969 | 123.2025 | -66.7603 | 56.2912 | -0.010607 | -0.013769 | 0.00088894 | 0.053722 | -0.0048096 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058672 | 0.023036 | 0.058949 | -66.729 | -0.039801 | -66.7506 | 56.2518 | 56.1563 | 56.3168 | -66.8558 | -66.7565 | -0.031692 | -66.7819 | 56.1528 | 56.3305 | 56.1735 | -67.0607 | -0.095576 | -0.03936 | 0.031298 | 0.009671 | 0.10525 | -0.13491 | 0.025641 | -0.30041 | -0.13844 | 0.003712 | -0.021636 | 0.27878 | 0.039318 | -0.11773 | 123.0121 | 122.9165 | 123.0771 | 66.7205 | -123.147 | 122.913 | 123.0908 | 122.9337 | 66.7286 | -123.3519
1113.7969 | 123.1842 | -66.7374 | 56.3187 | -0.0029761 | -0.013769 | 0.00088894 | 0.053936 | -0.0043822 | 0.06293 | 0.015414 | -0.0017711 | -0.00076913 | 0.058458 | 0.02325 | 0.058735 | -66.7244 | -0.035222 | -66.7414 | 56.2518 | 56.1609 | 56.3168 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3259 | 56.1597 | -67.0652 | -0.11389 | -0.066826 | 0.012989 | -0.004061 | 0.10982 | -0.1578 | -0.001825 | -0.32788 | -0.16133 | -0.010019 | -0.044524 | 0.28336 | 0.007274 | -0.15893 | 122.9892 | 122.8982 | 123.0542 | 66.7021 | -123.1699 | 122.8947 | 123.0633 | 122.8971 | 66.6965 | -123.3839
1114.8594 | 123.1567 | -66.7374 | 56.3278 | 0.012286 | -0.013555 | 0.00088894 | 0.053936 | -0.004596 | 0.06293 | 0.015414 | -0.0019847 | -0.00098273 | 0.058031 | 0.023463 | 0.058949 | -66.729 | -0.035222 | -66.7506 | 56.2518 | 56.1609 | 56.3168 | -66.8558 | -66.752 | -0.036271 | -66.7727 | 56.1619 | 56.3397 | 56.1552 | -67.0652 | -0.11846 | -0.075981 | 0.00841 | -0.013217 | 0.10525 | -0.16695 | -0.01098 | -0.32788 | -0.1659 | -0.014597 | -0.035366 | 0.29251 | 0.011855 | -0.17267 | 122.9892 | 122.8982 | 123.0542 | 66.7021 | -123.1837 | 122.8993 | 123.077 | 122.8925 | 66.7011 | -123.3931
1115.7969 | 123.1934 | -66.7191 | 56.3004 | -0.0029761 | -0.013342 | 0.0011025 | 0.053936 | -0.0048096 | 0.062717 | -0.015108 | -0.0019847 | -0.00098273 | 0.058458 | 0.023463 | 0.058949 | -66.7244 | -0.030644 | -66.7552 | 56.261 | 56.1471 | 56.3214 | -66.8513 | -66.7565 | -0.040849 | -66.7819 | 56.1619 | 56.3305 | 56.1689 | -67.0652 | -0.1322 | -0.039359 | -0.005322 | -0.036106 | 0.09609 | -0.15322 | 0.021065 | -0.34619 | -0.13844 | -0.037487 | -0.062835 | 0.28336 | 0.030163 | -0.13146 | 122.9801 | 122.8662 | 123.0405 | 66.6884 | -123.1516 | 122.881 | 123.0496 | 122.8879 | 66.6782 | -123.3656
1116.7969 | 123.1842 | -66.7419 | 56.3141 | -0.0029761 | -0.013769 | 0.00088894 | 0.053936 | -0.0050232 | 0.062503 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058245 | 0.023036 | 0.058735 | -66.729 | -0.030644 | -66.7506 | 56.2564 | 56.1517 | 56.3168 | -66.8467 | -66.7565 | -0.040849 | -66.7773 | 56.1619 | 56.3305 | 56.1597 | -67.0607 | -0.10473 | -0.05767 | 0.012987 | -0.00864 | 0.096089 | -0.16238 | 0.002753 | -0.31873 | -0.15217 | -0.014599 | -0.035368 | 0.28336 | 0.01643 | -0.15436 | 122.9984 | 122.8937 | 123.0588 | 66.7113 | -123.1608 | 122.9039 | 123.0725 | 122.9017 | 66.7011 | -123.3748
1117.8594 | 123.2849 | -66.6916 | 56.3049 | 0.0046549 | -0.013555 | 0.0011025 | 0.054363 | -0.004596 | 0.063358 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058245 | 0.023463 | 0.058949 | -66.7335 | -0.044379 | -66.746 | 56.2518 | 56.1471 | 56.3168 | -66.8513 | -66.7474 | -0.045428 | -66.7819 | 56.1573 | 56.3305 | 56.1689 | -67.0652 | -0.15966 | -0.053093 | -0.041945 | -0.054416 | 0.10525 | -0.1578 | 0.011908 | -0.37366 | -0.14759 | -0.055796 | -0.090301 | 0.28336 | 0.025585 | -0.13604 | 122.9434 | 122.8387 | 123.0084 | 66.6472 | -123.1562 | 122.8489 | 123.0221 | 122.8605 | 66.6462 | -123.3702
1118.7969 | 123.1659 | -66.7465 | 56.3049 | 0.012286 | -0.013769 | 0.00088894 | 0.053722 | -0.0048096 | 0.06293 | 0.0077831 | -0.0015573 | -0.00076913 | 0.058672 | 0.02325 | 0.058949 | -66.7381 | -0.035222 | -66.7506 | 56.2564 | 56.1517 | 56.326 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.1506 | -67.0607 | -0.11389 | -0.048515 | 0.008409 | -0.004062 | 0.10983 | -0.15322 | 0.021065 | -0.31415 | -0.14301 | -0.000864 | -0.039948 | 0.2742 | 0.030164 | -0.15436 | 123.0029 | 122.8982 | 123.0725 | 66.7113 | -123.1653 | 122.9084 | 123.0816 | 122.8971 | 66.7103 | -123.3656
1119.7969 | 123.1522 | -66.7282 | 56.3416 | 0.0046549 | -0.013769 | 0.00088894 | 0.053508 | -0.0048096 | 0.062289 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058886 | 0.023036 | 0.058735 | -66.7335 | -0.035222 | -66.7506 | 56.2564 | 56.1471 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7773 | 56.1619 | 56.3305 | 56.1597 | -67.0652 | -0.12304 | -0.085136 | -0.005324 | -0.022373 | 0.10067 | -0.19442 | -0.024713 | -0.33704 | -0.17964 | -0.023753 | -0.049101 | 0.28794 | -0.011036 | -0.18182 | 122.9846 | 122.8753 | 123.0451 | 66.693 | -123.1928 | 122.8901 | 123.0587 | 122.8879 | 66.6874 | -123.4068
1120.8594 | 123.1888 | -66.7511 | 56.2912 | -0.0029761 | -0.013769 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | 0.015414 | -0.0015573 | -0.0011965 | 0.058458 | 0.023036 | 0.058949 | -66.7335 | -0.030644 | -66.7552 | 56.2564 | 56.1471 | 56.326 | -66.8558 | -66.7565 | -0.036271 | -66.7865 | 56.1482 | 56.3305 | 56.1552 | -67.0652 | -0.10473 | -0.034782 | 0.017565 | -0.004062 | 0.10067 | -0.14407 | 0.034798 | -0.31415 | -0.14302 | -0.005443 | -0.03537 | 0.27878 | 0.039318 | -0.13605 | 123.0075 | 122.8982 | 123.0771 | 66.7205 | -123.147 | 122.8993 | 123.0816 | 122.9063 | 66.7148 | -123.3564
1121.7969 | 123.1979 | -66.7191 | 56.3324 | 0.012286 | -0.013555 | 0.00067514 | 0.053936 | -0.0050232 | 0.063144 | -0.0074779 | -0.0015573 | -0.0011965 | 0.058672 | 0.02325 | 0.059163 | -66.729 | -0.030644 | -66.746 | 56.261 | 56.1654 | 56.3214 | -66.8558 | -66.7611 | -0.040849 | -66.7865 | 56.1528 | 56.3305 | 56.1506 | -67.0652 | -0.13678 | -0.071402 | -0.009901 | -0.02695 | 0.10983 | -0.16695 | -0.010978 | -0.34619 | -0.17964 | -0.042066 | -0.067414 | 0.27878 | -0.00188 | -0.18182 | 122.9801 | 122.8845 | 123.0405 | 66.6884 | -123.1882 | 122.8718 | 123.0496 | 122.8696 | 66.6782 | -123.3976
1122.7969 | 123.2025 | -66.7236 | 56.3141 | 0.012286 | -0.013769 | 0.00088894 | 0.053722 | -0.0050232 | 0.062503 | -0.0074779 | -0.0017711 | -0.00076913 | 0.058672 | 0.02325 | 0.058949 | -66.7335 | -0.039801 | -66.7506 | 56.261 | 56.1426 | 56.3214 | -66.8513 | -66.752 | -0.036271 | -66.7819 | 56.1573 | 56.3351 | 56.1689 | -67.0652 | -0.12762 | -0.053092 | -0.009901 | -0.02695 | 0.10067 | -0.17153 | 0.007332 | -0.34161 | -0.15675 | -0.02833 | -0.058257 | 0.28336 | 0.021009 | -0.1452 | 122.9846 | 122.8662 | 123.0451 | 66.6838 | -123.1653 | 122.881 | 123.0587 | 122.8925 | 66.6874 | -123.3793
1123.8594 | 123.2071 | -66.7328 | 56.2958 | -0.0029761 | -0.013342 | 0.00088894 | 0.053508 | -0.0048096 | 0.06293 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.023463 | 0.058522 | -66.7335 | -0.030644 | -66.7552 | 56.2473 | 56.1471 | 56.3214 | -66.8513 | -66.7565 | -0.040849 | -66.7773 | 56.1619 | 56.3351 | 56.1689 | -67.0607 | -0.11846 | -0.048516 | -0.000746 | -0.022373 | 0.09609 | -0.14864 | 0.025643 | -0.32788 | -0.13386 | -0.023754 | -0.044523 | 0.28336 | 0.03932 | -0.12689 | 122.98 | 122.8799 | 123.0542 | 66.7021 | -123.147 | 122.8947 | 123.0679 | 122.9017 | 66.6919 | -123.3564
1124.7969 | 123.1705 | -66.7786 | 56.282 | 0.0046549 | -0.013769 | 0.0013163 | 0.053936 | -0.004596 | 0.062717 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058886 | 0.023036 | 0.058522 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1563 | 56.3168 | -66.8558 | -66.752 | -0.045428 | -66.7865 | 56.1619 | 56.3305 | 56.1597 | -67.0698 | -0.077266 | -0.025626 | 0.04503 | 0.032559 | 0.10983 | -0.12575 | 0.034797 | -0.29126 | -0.12013 | 0.026601 | -0.007905 | 0.28336 | 0.048474 | -0.12231 | 123.035 | 122.9349 | 123.0954 | 66.7433 | -123.1379 | 122.9405 | 123.1091 | 122.9383 | 66.7331 | -123.3519
1125.7969 | 123.175 | -66.7648 | 56.2958 | 0.0046549 | -0.013769 | 0.00088894 | 0.053936 | -0.0050232 | 0.062503 | 0.00015261 | -0.0021983 | -0.0011965 | 0.058245 | 0.023463 | 0.058949 | -66.729 | -0.030644 | -66.7506 | 56.2564 | 56.1517 | 56.3214 | -66.8513 | -66.7565 | -0.040849 | -66.791 | 56.1573 | 56.3351 | 56.1506 | -67.0607 | -0.086419 | -0.039359 | 0.035876 | 0.014249 | 0.10067 | -0.14406 | 0.025643 | -0.29584 | -0.13844 | 0.00829 | -0.026215 | 0.26962 | 0.03932 | -0.1452 | 123.0212 | 122.9165 | 123.0863 | 66.7342 | -123.147 | 122.9222 | 123.0999 | 122.9154 | 66.724 | -123.3564
1126.8594 | 123.2712 | -66.7007 | 56.3095 | -0.0029761 | -0.014196 | 0.0011025 | 0.053722 | -0.0050232 | 0.062503 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.022822 | 0.058735 | -66.7335 | -0.035222 | -66.746 | 56.2518 | 56.1517 | 56.3123 | -66.8467 | -66.7565 | -0.036271 | -66.7773 | 56.1619 | 56.3397 | 56.1689 | -67.0652 | -0.14593 | -0.05767 | -0.032789 | -0.04526 | 0.10067 | -0.1578 | 0.002753 | -0.3645 | -0.14759 | -0.055797 | -0.076566 | 0.28794 | 0.030166 | -0.14062 | 122.9526 | 122.8525 | 123.013 | 66.6655 | -123.1562 | 122.8627 | 123.0404 | 122.8696 | 66.6645 | -123.3748
1127.7969 | 123.143 | -66.7511 | 56.3141 | 0.0046549 | -0.013983 | 0.00067514 | 0.053936 | -0.0043822 | 0.062717 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058672 | 0.023036 | 0.058949 | -66.7335 | -0.035222 | -66.7414 | 56.261 | 56.1517 | 56.3214 | -66.8513 | -66.7474 | -0.040849 | -66.7865 | 56.1665 | 56.3397 | 56.146 | -67.0744 | -0.10015 | -0.053092 | 0.017565 | 0.009672 | 0.10982 | -0.16238 | 0.007332 | -0.32331 | -0.14759 | 0.003714 | -0.03537 | 0.28794 | 0.025588 | -0.16809 | 123.0121 | 122.9028 | 123.0725 | 66.7159 | -123.1653 | 122.9176 | 123.0908 | 122.8971 | 66.7103 | -123.3885
1128.8594 | 123.2208 | -66.7053 | 56.3004 | -0.010607 | -0.013342 | 0.00088894 | 0.053936 | -0.004596 | 0.062503 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058458 | 0.023463 | 0.058949 | -66.7335 | -0.035222 | -66.746 | 56.2518 | 56.1471 | 56.3168 | -66.8421 | -66.752 | -0.036271 | -66.7819 | 56.1665 | 56.3351 | 56.1552 | -67.0652 | -0.13677 | -0.048515 | -0.028212 | -0.040683 | 0.096088 | -0.15322 | 0.016486 | -0.35993 | -0.13386 | -0.046641 | -0.076568 | 0.28336 | 0.034742 | -0.1452 | 122.9572 | 122.8525 | 123.0222 | 66.6701 | -123.1424 | 122.8718 | 123.0404 | 122.8605 | 66.6691 | -123.3656
1129.7969 | 123.1796 | -66.7557 | 56.3187 | 0.0046549 | -0.013769 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | 0.015414 | -0.0017711 | -0.00098273 | 0.058672 | 0.02325 | 0.058735 | -66.7335 | -0.030644 | -66.7414 | 56.261 | 56.1517 | 56.326 | -66.8513 | -66.7474 | -0.036271 | -66.7773 | 56.1573 | 56.3351 | 56.1552 | -67.0652 | -0.095575 | -0.05767 | 0.022142 | 0.014249 | 0.10982 | -0.16695 | 0.007332 | -0.30957 | -0.16133 | 0.008291 | -0.021635 | 0.28794 | 0.016431 | -0.16351 | 123.0167 | 122.9074 | 123.0817 | 66.725 | -123.1699 | 122.913 | 123.0908 | 122.9108 | 66.7194 | -123.3839
1130.7969 | 123.2574 | -66.7328 | 56.282 | -0.0029761 | -0.013769 | 0.0013163 | 0.054149 | -0.0048096 | 0.062289 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058672 | 0.02325 | 0.058522 | -66.7335 | -0.035222 | -66.7323 | 56.2518 | 56.1334 | 56.3123 | -66.8421 | -66.7428 | -0.036271 | -66.7819 | 56.1619 | 56.3397 | 56.146 | -67.0652 | -0.10931 | -0.030204 | -0.000746 | 0.000518 | 0.10982 | -0.14865 | 0.030219 | -0.33246 | -0.12013 | -0.010018 | -0.049102 | 0.28336 | 0.057632 | -0.13605 | 122.9846 | 122.8662 | 123.0451 | 66.6976 | -123.1241 | 122.8947 | 123.0725 | 122.8788 | 66.6965 | -123.3473
1131.7969 | 123.143 | -66.7648 | 56.3049 | -0.0029761 | -0.013555 | 0.00088894 | 0.053722 | -0.004596 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058458 | 0.023677 | 0.058735 | -66.7335 | -0.035222 | -66.7277 | 56.261 | 56.1517 | 56.3306 | -66.8467 | -66.7428 | -0.040849 | -66.7865 | 56.1573 | 56.3351 | 56.1414 | -67.0607 | -0.08184 | -0.043937 | 0.031298 | 0.03714 | 0.11898 | -0.15322 | 0.025644 | -0.29584 | -0.14759 | 0.022026 | -0.021637 | 0.2742 | 0.030164 | -0.16351 | 123.0258 | 122.9165 | 123.0954 | 66.7296 | -123.1516 | 122.9222 | 123.0999 | 122.9062 | 66.724 | -123.3656
1132.7969 | 123.2666 | -66.7282 | 56.2912 | -0.010607 | -0.013555 | 0.0011025 | 0.054363 | -0.004596 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058458 | 0.023463 | 0.058949 | -66.7335 | -0.035222 | -66.7323 | 56.2518 | 56.138 | 56.3214 | -66.8513 | -66.7382 | -0.050007 | -66.7865 | 56.1619 | 56.3305 | 56.1506 | -67.0744 | -0.12304 | -0.03936 | -0.005324 | -0.00406 | 0.11898 | -0.15322 | 0.03022 | -0.34619 | -0.12928 | -0.010017 | -0.058259 | 0.28794 | 0.039318 | -0.14062 | 122.98 | 122.8662 | 123.0496 | 66.693 | -123.1424 | 122.8901 | 123.0587 | 122.8788 | 66.6782 | -123.3656
1133.7969 | 123.1979 | -66.7236 | 56.3919 | 0.0046549 | -0.013128 | 0.0011025 | 0.053722 | -0.004596 | 0.062289 | 0.0077831 | -0.0015573 | -0.00055553 | 0.058672 | 0.02325 | 0.059163 | -66.7244 | -0.035222 | -66.7368 | 56.261 | 56.1517 | 56.326 | -66.8558 | -66.7428 | -0.045428 | -66.7819 | 56.1528 | 56.3351 | 56.1643 | -67.0698 | -0.1322 | -0.13091 | -0.000744 | -0.013215 | 0.11898 | -0.2402 | -0.06591 | -0.34619 | -0.23915 | -0.019173 | -0.058257 | 0.28794 | -0.056811 | -0.2276 | 122.9846 | 122.8753 | 123.0496 | 66.6884 | -123.2477 | 122.8764 | 123.0587 | 122.8879 | 66.6782 | -123.4617
1134.7969 | 123.2529 | -66.7053 | 56.2683 | 0.0046549 | -0.013983 | 0.00088894 | 0.054149 | -0.0048096 | 0.062503 | 0.0077831 | -0.0013437 | -0.00076913 | 0.058886 | 0.023891 | 0.058735 | -66.7335 | -0.044379 | -66.7368 | 56.261 | 56.1426 | 56.3168 | -66.8467 | -66.752 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.1597 | -67.0607 | -0.14135 | -0.007316 | -0.028212 | -0.031526 | 0.10982 | -0.12576 | 0.048529 | -0.35535 | -0.10639 | -0.046641 | -0.081147 | 0.2742 | 0.066785 | -0.10858 | 122.9663 | 122.8479 | 123.0222 | 66.6609 | -123.115 | 122.8672 | 123.0404 | 122.8651 | 66.6691 | -123.329
1135.7969 | 123.2346 | -66.7053 | 56.2546 | -0.0029761 | -0.013983 | 0.00088894 | 0.054149 | -0.0050232 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058458 | 0.023463 | 0.058735 | -66.7381 | -0.039801 | -66.7414 | 56.261 | 56.1517 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3305 | 56.1552 | -67.0561 | -0.14593 | 0.006417 | -0.03279 | -0.036105 | 0.10982 | -0.10287 | 0.062262 | -0.35077 | -0.092661 | -0.046641 | -0.081147 | 0.26962 | 0.075939 | -0.099425 | 122.9663 | 122.857 | 123.0222 | 66.6655 | -123.1058 | 122.8672 | 123.0358 | 122.8605 | 66.6645 | -123.3107
1136.8594 | 123.1018 | -66.7694 | 56.3141 | 0.0046549 | -0.013983 | 0.00088894 | 0.053936 | -0.0050232 | 0.062289 | 0.015414 | -0.0017711 | -0.0011965 | 0.058458 | 0.023677 | 0.059163 | -66.7335 | -0.030644 | -66.7323 | 56.261 | 56.1471 | 56.3123 | -66.8513 | -66.752 | -0.031692 | -66.7773 | 56.1665 | 56.3351 | 56.146 | -67.0652 | -0.081842 | -0.053092 | 0.035875 | 0.037139 | 0.11898 | -0.16696 | -0.001825 | -0.29584 | -0.14759 | 0.017446 | -0.007902 | 0.28794 | 0.021009 | -0.16809 | 123.0304 | 122.9165 | 123.0817 | 66.7388 | -123.1653 | 122.9359 | 123.1045 | 122.9154 | 66.7377 | -123.3793
1137.7969 | 123.2666 | -66.7465 | 56.2592 | -0.0029761 | -0.013983 | 0.00088894 | 0.054149 | -0.0050232 | 0.062717 | 0.015414 | -0.0015573 | -0.00098273 | 0.058458 | 0.02325 | 0.058735 | -66.7335 | -0.030644 | -66.7506 | 56.261 | 56.1517 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7819 | 56.1619 | 56.3397 | 56.1597 | -67.0652 | -0.10473 | 0.00184 | 0.012987 | -0.004062 | 0.10067 | -0.10744 | 0.057685 | -0.31873 | -0.097238 | -0.005442 | -0.035369 | 0.28336 | 0.08052 | -0.099423 | 123.0075 | 122.8982 | 123.0634 | 66.7159 | -123.1104 | 122.9084 | 123.0862 | 122.9063 | 66.7057 | -123.3244
1138.875 | 123.2666 | -66.6687 | 56.3416 | 0.012286 | -0.013983 | 0.0011025 | 0.053936 | -0.0048096 | 0.062717 | 0.015414 | -0.0017711 | -0.0011965 | 0.058672 | 0.02325 | 0.058949 | -66.7473 | -0.035222 | -66.7506 | 56.261 | 56.1471 | 56.3123 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.1506 | -67.0607 | -0.18255 | -0.080558 | -0.078568 | -0.081882 | 0.10067 | -0.19442 | -0.029291 | -0.39197 | -0.17964 | -0.078684 | -0.11777 | 0.2742 | -0.006457 | -0.19098 | 122.9297 | 122.8158 | 122.981 | 66.6335 | -123.1928 | 122.8306 | 123.0038 | 122.8193 | 66.6324 | -123.4022
1139.7969 | 123.2758 | -66.7053 | 56.2775 | -0.0029761 | -0.013983 | 0.0011025 | 0.054149 | -0.0050232 | 0.06293 | -0.0074779 | -0.0021983 | -0.00076913 | 0.058245 | 0.023463 | 0.058735 | -66.7335 | -0.030644 | -66.7552 | 56.261 | 56.1471 | 56.3168 | -66.8558 | -66.752 | -0.031692 | -66.7819 | 56.1619 | 56.3351 | 56.1643 | -67.0652 | -0.15051 | -0.016471 | -0.028212 | -0.049839 | 0.10067 | -0.13033 | 0.039374 | -0.35993 | -0.11555 | -0.046641 | -0.076568 | 0.28336 | 0.05763 | -0.11315 | 122.9663 | 122.8525 | 123.0222 | 66.6747 | -123.1333 | 122.8672 | 123.0404 | 122.8696 | 66.6736 | -123.3427
1140.7969 | 123.2666 | -66.7099 | 56.2912 | 0.0046549 | -0.013983 | 0.00046154 | 0.054149 | -0.004596 | 0.062717 | 0.023044 | -0.0015573 | -0.00076913 | 0.058245 | 0.02325 | 0.058522 | -66.729 | -0.030644 | -66.7506 | 56.2564 | 56.1563 | 56.3168 | -66.8467 | -66.752 | -0.036271 | -66.7865 | 56.1619 | 56.3305 | 56.1506 | -67.0652 | -0.13677 | -0.034782 | -0.019056 | -0.040683 | 0.096089 | -0.13491 | 0.025641 | -0.35535 | -0.12928 | -0.042063 | -0.076569 | 0.27878 | 0.039318 | -0.14062 | 122.9663 | 122.8662 | 123.0267 | 66.6793 | -123.1379 | 122.8718 | 123.0404 | 122.8605 | 66.6736 | -123.3564
1141.7969 | 123.2162 | -66.7328 | 56.3004 | -0.010607 | -0.013769 | 0.0011025 | 0.053722 | -0.0048096 | 0.06293 | 0.00015261 | -0.0015573 | -0.00055553 | 0.058245 | 0.023463 | 0.058949 | -66.7335 | -0.030644 | -66.7506 | 56.2564 | 56.1517 | 56.3214 | -66.8467 | -66.7428 | -0.036271 | -66.7865 | 56.1573 | 56.3351 | 56.1552 | -67.0652 | -0.11388 | -0.043937 | -0.000746 | -0.017795 | 0.096089 | -0.14864 | 0.021065 | -0.33246 | -0.14301 | -0.010018 | -0.053681 | 0.27878 | 0.034742 | -0.1452 | 122.9892 | 122.8845 | 123.0542 | 66.7021 | -123.147 | 122.8901 | 123.0679 | 122.8879 | 66.6965 | -123.3656
1142.7969 | 123.2712 | -66.687 | 56.2866 | -0.0029761 | -0.014196 | 0.00088894 | 0.053936 | -0.0050232 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058458 | 0.023463 | 0.058735 | -66.729 | -0.035222 | -66.7414 | 56.2564 | 56.1563 | 56.3214 | -66.8558 | -66.752 | -0.045428 | -66.7773 | 56.1665 | 56.3305 | 56.1597 | -67.0607 | -0.16882 | -0.030204 | -0.041944 | -0.054415 | 0.1144 | -0.13033 | 0.034798 | -0.37366 | -0.12012 | -0.064951 | -0.090299 | 0.28336 | 0.043896 | -0.12689 | 122.9434 | 122.8433 | 123.0084 | 66.6518 | -123.1425 | 122.8535 | 123.0175 | 122.8467 | 66.6416 | -123.3473
1143.8125 | 123.2254 | -66.7465 | 56.3049 | -0.0029761 | -0.01441 | 0.0011025 | 0.053936 | -0.004596 | 0.062289 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058458 | 0.023036 | 0.058735 | -66.729 | -0.044379 | -66.7506 | 56.2564 | 56.1517 | 56.3168 | -66.8558 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3305 | 56.1552 | -67.0698 | -0.10931 | -0.048515 | 0.017565 | -0.004062 | 0.10525 | -0.15322 | 0.011908 | -0.32331 | -0.14301 | -0.005442 | -0.039948 | 0.28336 | 0.025585 | -0.14978 | 123.0029 | 122.8982 | 123.0634 | 66.7021 | -123.1608 | 122.9084 | 123.077 | 122.9017 | 66.7057 | -123.3748
1144.7969 | 123.2803 | -66.7099 | 56.3141 | 0.0046549 | -0.014196 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058458 | 0.023463 | 0.058949 | -66.7335 | -0.039801 | -66.746 | 56.2564 | 56.1609 | 56.3214 | -66.8558 | -66.752 | -0.036271 | -66.7819 | 56.1573 | 56.3351 | 56.1689 | -67.0607 | -0.14593 | -0.05767 | -0.023634 | -0.036105 | 0.10983 | -0.15322 | 0.007332 | -0.35077 | -0.15675 | -0.042063 | -0.07199 | 0.27878 | 0.021009 | -0.1452 | 122.9663 | 122.8708 | 123.0313 | 66.6701 | -123.1699 | 122.8672 | 123.045 | 122.8788 | 66.6736 | -123.3748
1145.7969 | 123.2758 | -66.7099 | 56.3141 | 0.0046549 | -0.01441 | 0.00088894 | 0.053936 | -0.0048096 | 0.06293 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058458 | 0.023463 | 0.058735 | -66.7244 | -0.044379 | -66.7552 | 56.2518 | 56.1563 | 56.3168 | -66.8513 | -66.752 | -0.031692 | -66.791 | 56.1573 | 56.3305 | 56.1643 | -67.0698 | -0.14135 | -0.062248 | -0.014477 | -0.045261 | 0.09609 | -0.1578 | 0.002753 | -0.35993 | -0.15675 | -0.042063 | -0.081147 | 0.27878 | 0.01643 | -0.14978 | 122.9617 | 122.8662 | 123.0267 | 66.6655 | -123.1653 | 122.8672 | 123.0404 | 122.8742 | 66.6782 | -123.3839
1146.8594 | 123.2071 | -66.7145 | 56.2958 | 0.0046549 | -0.014196 | 0.00067514 | 0.053936 | -0.0048096 | 0.062503 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058458 | 0.023463 | 0.058949 | -66.7335 | -0.035222 | -66.7506 | 56.2564 | 56.1609 | 56.3214 | -66.8558 | -66.7565 | -0.045428 | -66.7865 | 56.1528 | 56.3305 | 56.1597 | -67.0698 | -0.14135 | -0.039359 | -0.019056 | -0.036105 | 0.10525 | -0.13491 | 0.025643 | -0.35535 | -0.14302 | -0.042064 | -0.071991 | 0.28336 | 0.034741 | -0.13604 | 122.9709 | 122.8753 | 123.0359 | 66.6793 | -123.1516 | 122.8672 | 123.045 | 122.8742 | 66.669 | -123.3656
1147.7969 | 123.2666 | -66.6824 | 56.2912 | 0.0046549 | -0.014196 | 0.00067514 | 0.053936 | -0.0052368 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058886 | 0.023677 | 0.058735 | -66.7335 | -0.030644 | -66.7506 | 56.2564 | 56.1517 | 56.3123 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.1643 | -67.0652 | -0.16882 | -0.034782 | -0.0511 | -0.068149 | 0.10067 | -0.13949 | 0.021063 | -0.38281 | -0.12928 | -0.064951 | -0.10403 | 0.27878 | 0.043897 | -0.12689 | 122.9389 | 122.8341 | 122.9947 | 66.6518 | -123.1424 | 122.8444 | 123.0175 | 122.8467 | 66.6462 | -123.3564
1148.7969 | 123.2483 | -66.7053 | 56.2637 | -0.0029761 | -0.014196 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058245 | 0.023891 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2518 | 56.1517 | 56.3123 | -66.8513 | -66.7565 | -0.036271 | -66.7819 | 56.1528 | 56.3305 | 56.1597 | -67.0652 | -0.14593 | -0.011894 | -0.019055 | -0.040683 | 0.10525 | -0.11202 | 0.048529 | -0.35993 | -0.11097 | -0.05122 | -0.076568 | 0.28336 | 0.066784 | -0.104 | 122.9572 | 122.857 | 123.0176 | 66.6701 | -123.115 | 122.8581 | 123.0358 | 122.8651 | 66.6691 | -123.329
1149.8594 | 123.23 | -66.7145 | 56.2912 | 0.0046549 | -0.014196 | 0.0011025 | 0.054149 | -0.0048096 | 0.062717 | 0.00015261 | -0.0015573 | -0.00076913 | 0.058245 | 0.023677 | 0.058949 | -66.729 | -0.035222 | -66.7552 | 56.2564 | 56.1654 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7819 | 56.1619 | 56.3259 | 56.1643 | -67.0652 | -0.13677 | -0.034782 | -0.014478 | -0.040683 | 0.09609 | -0.12575 | 0.025641 | -0.35077 | -0.12928 | -0.037485 | -0.067412 | 0.28336 | 0.03474 | -0.12689 | 122.9709 | 122.8799 | 123.0313 | 66.6793 | -123.1424 | 122.8764 | 123.0404 | 122.8788 | 66.6736 | -123.3564
1150.7969 | 123.143 | -66.7282 | 56.3599 | -0.010607 | -0.014196 | 0.00088894 | 0.053936 | -0.0050232 | 0.062503 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058458 | 0.023677 | 0.059163 | -66.7381 | -0.035222 | -66.7552 | 56.261 | 56.1609 | 56.3214 | -66.8513 | -66.7474 | -0.040849 | -66.7865 | 56.1619 | 56.3259 | 56.1735 | -67.0698 | -0.12304 | -0.098868 | -0.009902 | -0.026951 | 0.09609 | -0.19899 | -0.038444 | -0.34162 | -0.19795 | -0.019175 | -0.058259 | 0.28336 | -0.033924 | -0.18639 | 122.9892 | 122.8891 | 123.0496 | 66.693 | -123.2111 | 122.8901 | 123.0541 | 122.9017 | 66.6874 | -123.4297
1151.8594 | 123.1796 | -66.7557 | 56.3461 | -0.0029761 | -0.01441 | 0.00088894 | 0.053936 | -0.0048096 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058458 | 0.023677 | 0.058735 | -66.7244 | -0.035222 | -66.7552 | 56.2518 | 56.1563 | 56.3123 | -66.8467 | -66.752 | -0.045428 | -66.791 | 56.1573 | 56.3305 | 56.1552 | -67.0607 | -0.090996 | -0.094291 | 0.031299 | 0.000515 | 0.091511 | -0.18984 | -0.033868 | -0.30499 | -0.18879 | 0.003713 | -0.035371 | 0.26962 | -0.015613 | -0.19098 | 123.0075 | 122.912 | 123.0679 | 66.7205 | -123.1928 | 122.913 | 123.0862 | 122.9108 | 66.7102 | -123.4068
1152.8125 | 123.2346 | -66.6962 | 56.2775 | -0.0029761 | -0.014196 | 0.00088894 | 0.054149 | -0.0048096 | 0.062717 | 0.0077831 | -0.0017711 | -0.0011965 | 0.058458 | 0.023677 | 0.059163 | -66.7335 | -0.030644 | -66.7414 | 56.2518 | 56.1334 | 56.3077 | -66.8421 | -66.7428 | -0.054586 | -66.7865 | 56.1528 | 56.3305 | 56.1689 | -67.0607 | -0.14593 | -0.025627 | -0.037367 | -0.04526 | 0.10067 | -0.14407 | 0.030217 | -0.3645 | -0.12471 | -0.046639 | -0.090302 | 0.2742 | 0.053051 | -0.10858 | 122.948 | 122.8296 | 123.0038 | 66.6655 | -123.1196 | 122.8489 | 123.0267 | 122.8651 | 66.6416 | -123.3381
1153.8906 | 123.2529 | -66.7145 | 56.2775 | -0.0029761 | -0.01441 | 0.00067514 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058458 | 0.023891 | 0.058735 | -66.729 | -0.035222 | -66.746 | 56.2518 | 56.1471 | 56.3123 | -66.8467 | -66.7565 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.1506 | -67.0652 | -0.13219 | -0.025627 | -0.014478 | -0.031527 | 0.10067 | -0.13033 | 0.034796 | -0.35077 | -0.11555 | -0.042064 | -0.071991 | 0.27878 | 0.05763 | -0.12689 | 122.9663 | 122.8616 | 123.0267 | 66.6793 | -123.1241 | 122.8764 | 123.0496 | 122.8651 | 66.6782 | -123.3427
1154.7969 | 123.0881 | -66.7328 | 56.3461 | -0.0029761 | -0.013983 | 0.00067514 | 0.053936 | -0.0048096 | 0.062503 | 0.015414 | -0.0021983 | -0.00076913 | 0.058672 | 0.023677 | 0.058735 | -66.7244 | -0.026065 | -66.7506 | 56.2518 | 56.1609 | 56.3214 | -66.8558 | -66.752 | -0.036271 | -66.7865 | 56.1619 | 56.3259 | 56.1643 | -67.0652 | -0.12304 | -0.094291 | 0.008411 | -0.017795 | 0.10525 | -0.18526 | -0.024711 | -0.33246 | -0.18421 | -0.019175 | -0.053681 | 0.27878 | -0.020191 | -0.18182 | 122.9846 | 122.8937 | 123.0542 | 66.7067 | -123.202 | 122.8947 | 123.0587 | 122.8971 | 66.6965 | -123.4114
1155.7969 | 123.2254 | -66.7282 | 56.3095 | -0.0029761 | -0.014624 | 0.0011025 | 0.053722 | -0.004596 | 0.06293 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058886 | 0.023677 | 0.058522 | -66.7335 | -0.044379 | -66.7414 | 56.2473 | 56.1517 | 56.3214 | -66.8558 | -66.752 | -0.040849 | -66.7773 | 56.1573 | 56.3259 | 56.1506 | -67.0698 | -0.12762 | -0.062249 | -0.005324 | -0.013217 | 0.1144 | -0.1578 | 0.01191 | -0.34162 | -0.15217 | -0.023753 | -0.049101 | 0.29252 | 0.01643 | -0.15893 | 122.9755 | 122.8799 | 123.0496 | 66.6838 | -123.1653 | 122.8855 | 123.0541 | 122.8788 | 66.6874 | -123.3793
1156.7969 | 123.1567 | -66.7236 | 56.3416 | -0.0029761 | -0.013983 | 0.00088894 | 0.054149 | -0.0050232 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.023463 | 0.058522 | -66.729 | -0.039801 | -66.7552 | 56.261 | 56.1563 | 56.3214 | -66.8421 | -66.7382 | -0.036271 | -66.7819 | 56.1573 | 56.3443 | 56.1552 | -67.0607 | -0.11846 | -0.080558 | -0.005323 | -0.031528 | 0.086932 | -0.18526 | -0.020134 | -0.33704 | -0.18421 | -0.014594 | -0.058257 | 0.27878 | 0.0027 | -0.1864 | 122.9846 | 122.8799 | 123.0451 | 66.6838 | -123.1836 | 122.881 | 123.0679 | 122.8788 | 66.6874 | -123.4022
1157.7969 | 123.2666 | -66.6962 | 56.2775 | -0.0029761 | -0.013769 | 0.00067514 | 0.053936 | -0.0048096 | 0.06293 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058245 | 0.023677 | 0.058735 | -66.7244 | -0.035222 | -66.7506 | 56.261 | 56.1517 | 56.326 | -66.8467 | -66.752 | -0.050007 | -66.7819 | 56.1619 | 56.3305 | 56.1506 | -67.0698 | -0.1505 | -0.016471 | -0.02821 | -0.054416 | 0.096089 | -0.12575 | 0.048531 | -0.37366 | -0.11555 | -0.055796 | -0.085723 | 0.28794 | 0.053051 | -0.12689 | 122.9572 | 122.8479 | 123.0222 | 66.6609 | -123.1241 | 122.8581 | 123.0267 | 122.8467 | 66.6462 | -123.3473
1158.8125 | 123.175 | -66.7191 | 56.3049 | -0.010607 | -0.014196 | 0.0011025 | 0.053722 | -0.0050232 | 0.06293 | 0.015414 | -0.0017711 | -0.0011965 | 0.058672 | 0.023891 | 0.058522 | -66.7335 | -0.035222 | -66.7414 | 56.2656 | 56.1517 | 56.3214 | -66.8558 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3397 | 56.1552 | -67.0698 | -0.13678 | -0.039358 | -0.014479 | -0.022372 | 0.1144 | -0.15322 | 0.016487 | -0.35077 | -0.14759 | -0.02833 | -0.062835 | 0.28794 | 0.034743 | -0.14978 | 122.9846 | 122.8708 | 123.0405 | 66.6838 | -123.1608 | 122.8764 | 123.0587 | 122.8742 | 66.6782 | -123.3748
1159.7969 | 123.1476 | -66.7557 | 56.3232 | -0.0029761 | -0.013983 | 0.00067514 | 0.053936 | -0.0048096 | 0.06293 | 0.015414 | -0.0017711 | -0.00076913 | 0.058458 | 0.024104 | 0.058735 | -66.7335 | -0.039801 | -66.7597 | 56.2564 | 56.1517 | 56.326 | -66.8513 | -66.7565 | -0.040849 | -66.7682 | 56.1573 | 56.3351 | 56.1597 | -67.0698 | -0.095575 | -0.066825 | 0.022142 | -0.004064 | 0.091511 | -0.17153 | 0.002755 | -0.31415 | -0.1659 | -0.000866 | -0.012478 | 0.30167 | 0.011854 | -0.16351 | 123.0121 | 122.9074 | 123.0817 | 66.7159 | -123.1745 | 122.913 | 123.0908 | 122.9154 | 66.7148 | -123.3931
1160.8594 | 123.143 | -66.7465 | 56.3187 | -0.0029761 | -0.014196 | 0.0011025 | 0.053936 | -0.0050232 | 0.062717 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058458 | 0.023463 | 0.058949 | -66.729 | -0.030644 | -66.7552 | 56.2564 | 56.1609 | 56.3214 | -66.8513 | -66.7474 | -0.036271 | -66.7819 | 56.1619 | 56.3259 | 56.1689 | -67.0698 | -0.10473 | -0.062248 | 0.017565 | -0.00864 | 0.09609 | -0.1578 | 0.002754 | -0.32331 | -0.15675 | -0.000864 | -0.035369 | 0.28794 | 0.007274 | -0.14978 | 123.0029 | 122.9074 | 123.0679 | 66.7159 | -123.1699 | 122.9084 | 123.0725 | 122.9154 | 66.7103 | -123.3885
1161.7969 | 123.1979 | -66.7419 | 56.3141 | 0.0046549 | -0.014196 | 0.00088894 | 0.053722 | -0.004596 | 0.06293 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058886 | 0.023891 | 0.058949 | -66.7244 | -0.039801 | -66.746 | 56.2656 | 56.1563 | 56.326 | -66.8558 | -66.7565 | -0.036271 | -66.7819 | 56.1665 | 56.3305 | 56.1643 | -67.0652 | -0.11389 | -0.048513 | 0.017566 | -0.004062 | 0.10983 | -0.1578 | 0.01191 | -0.3233 | -0.14759 | -0.014599 | -0.039947 | 0.28336 | 0.01643 | -0.14978 | 123.0075 | 122.8982 | 123.0679 | 66.7021 | -123.1699 | 122.9084 | 123.0725 | 122.9063 | 66.7057 | -123.3793
1162.7969 | 123.1522 | -66.774 | 56.3095 | -0.0029761 | -0.014196 | 0.00067514 | 0.053722 | -0.0048096 | 0.062717 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058672 | 0.023677 | 0.058735 | -66.7244 | -0.039801 | -66.746 | 56.2564 | 56.1654 | 56.3168 | -66.8513 | -66.752 | -0.036271 | -66.7819 | 56.1619 | 56.3397 | 56.1643 | -67.0652 | -0.077264 | -0.053092 | 0.04961 | 0.027982 | 0.10525 | -0.14406 | 0.007331 | -0.29126 | -0.14759 | 0.022024 | -0.007903 | 0.28336 | 0.030166 | -0.1452 | 123.0304 | 122.9394 | 123.0908 | 66.7342 | -123.1608 | 122.9359 | 123.1137 | 122.9383 | 66.7377 | -123.3748
1163.8125 | 123.1522 | -66.7465 | 56.337 | 0.012286 | -0.014196 | 0.00067514 | 0.054363 | -0.0050232 | 0.062717 | 0.023044 | -0.0019847 | -0.0011965 | 0.058245 | 0.023677 | 0.058735 | -66.7335 | -0.030644 | -66.7414 | 56.2518 | 56.1471 | 56.3214 | -66.8513 | -66.752 | -0.040849 | -66.7773 | 56.1665 | 56.3351 | 56.1506 | -67.0698 | -0.10473 | -0.085136 | 0.012987 | 0.005094 | 0.10982 | -0.18984 | -0.015556 | -0.32331 | -0.17048 | -0.005442 | -0.03079 | 0.29252 | -0.001879 | -0.1864 | 122.9984 | 122.8937 | 123.0679 | 66.7159 | -123.1882 | 122.913 | 123.0816 | 122.8971 | 66.7057 | -123.4068
1164.7969 | 123.1796 | -66.7374 | 56.3187 | -0.0029761 | -0.01441 | 0.0011025 | 0.053936 | -0.004596 | 0.062503 | 0.0077831 | -0.0015573 | -0.00098273 | 0.058672 | 0.023891 | 0.058522 | -66.729 | -0.035222 | -66.7414 | 56.261 | 56.1563 | 56.3168 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3305 | 56.1552 | -67.0652 | -0.11389 | -0.05767 | 0.00841 | -0.004061 | 0.10982 | -0.16238 | -0.001825 | -0.32788 | -0.16133 | -0.010019 | -0.044524 | 0.28336 | 0.011852 | -0.16351 | 122.9984 | 122.8937 | 123.0542 | 66.7021 | -123.1699 | 122.8947 | 123.0679 | 122.8925 | 66.6965 | -123.3839
1165.8594 | 123.2986 | -66.7236 | 56.2546 | 0.0046549 | -0.014196 | 0.00067514 | 0.054149 | -0.0048096 | 0.062717 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058672 | 0.023677 | 0.058735 | -66.7335 | -0.030644 | -66.7506 | 56.2518 | 56.1563 | 56.3168 | -66.8329 | -66.752 | -0.031692 | -66.7819 | 56.1619 | 56.3351 | 56.1597 | -67.0652 | -0.1093 | -0.002739 | -0.009901 | -0.02695 | 0.082352 | -0.098288 | 0.062262 | -0.34161 | -0.092661 | -0.02833 | -0.058257 | 0.28336 | 0.080518 | -0.094846 | 122.9755 | 122.8799 | 123.0405 | 66.693 | -123.0875 | 122.8856 | 123.0587 | 122.8834 | 66.6919 | -123.3198
1166.7969 | 123.1842 | -66.7648 | 56.3232 | -0.0029761 | -0.01441 | 0.00088894 | 0.054149 | -0.0050232 | 0.063144 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058458 | 0.024104 | 0.058949 | -66.7335 | -0.039801 | -66.746 | 56.261 | 56.1609 | 56.3306 | -66.8558 | -66.752 | -0.045428 | -66.791 | 56.1619 | 56.3305 | 56.1689 | -67.079 | -0.090998 | -0.062247 | 0.031298 | 0.018827 | 0.10983 | -0.16237 | 0.007334 | -0.31415 | -0.16132 | 0.012869 | -0.026215 | 0.28794 | 0.007275 | -0.15435 | 123.0258 | 122.9257 | 123.0954 | 66.725 | -123.1791 | 122.9267 | 123.0953 | 122.9337 | 66.7194 | -123.4022
1167.7969 | 123.1796 | -66.7374 | 56.3416 | 0.0046549 | -0.014196 | 0.0011025 | 0.053722 | -0.0050232 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.023891 | 0.059163 | -66.7335 | -0.035222 | -66.7552 | 56.2656 | 56.1471 | 56.3214 | -66.8467 | -66.7474 | -0.040849 | -66.7727 | 56.1665 | 56.3259 | 56.1597 | -67.0698 | -0.10931 | -0.075979 | 0.003832 | -0.017795 | 0.091511 | -0.19442 | -0.020134 | -0.33246 | -0.17506 | -0.010019 | -0.035366 | 0.29709 | -0.015614 | -0.18182 | 123.0029 | 122.8845 | 123.0588 | 66.7021 | -123.1882 | 122.9039 | 123.0633 | 122.8971 | 66.6965 | -123.4114
1168.8906 | 123.2391 | -66.7328 | 56.2729 | -0.0029761 | -0.01441 | 0.0011025 | 0.053722 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058458 | 0.024104 | 0.058949 | -66.7335 | -0.044379 | -66.7368 | 56.2518 | 56.1563 | 56.3214 | -66.8467 | -66.7428 | -0.045428 | -66.7865 | 56.1573 | 56.3305 | 56.1506 | -67.0607 | -0.11388 | -0.021049 | -0.000746 | -0.00406 | 0.10982 | -0.1166 | 0.048531 | -0.32788 | -0.11555 | -0.010018 | -0.053681 | 0.2742 | 0.057629 | -0.12231 | 122.9846 | 122.8891 | 123.0542 | 66.6884 | -123.1196 | 122.8901 | 123.0633 | 122.8834 | 66.6874 | -123.3336
1169.7969 | 123.2025 | -66.7374 | 56.3187 | -0.0029761 | -0.01441 | 0.00067514 | 0.053508 | -0.004596 | 0.062503 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058458 | 0.023677 | 0.058522 | -66.7381 | -0.035222 | -66.7506 | 56.2656 | 56.1609 | 56.3352 | -66.8467 | -66.7474 | -0.040849 | -66.7819 | 56.1665 | 56.3305 | 56.1689 | -67.0698 | -0.10931 | -0.053091 | -0.000746 | -0.013217 | 0.096089 | -0.1578 | 0.01649 | -0.33246 | -0.15217 | -0.010019 | -0.044524 | 0.28794 | 0.011852 | -0.14978 | 123.0029 | 122.8982 | 123.0725 | 66.7021 | -123.1653 | 122.9039 | 123.0679 | 122.9063 | 66.6965 | -123.3885
1170.7969 | 123.2483 | -66.7236 | 56.2454 | 0.0046549 | -0.014196 | 0.00067514 | 0.053936 | -0.0048096 | 0.062717 | -0.0074779 | -0.0017711 | -0.0011965 | 0.058245 | 0.023891 | 0.058949 | -66.7335 | -0.039801 | -66.7506 | 56.2518 | 56.1563 | 56.3214 | -66.8513 | -66.7474 | -0.036271 | -66.7773 | 56.1665 | 56.3305 | 56.1643 | -67.0744 | -0.12762 | 0.006417 | -0.009901 | -0.02695 | 0.10067 | -0.089132 | 0.075997 | -0.35077 | -0.078926 | -0.023752 | -0.053678 | 0.29709 | 0.085095 | -0.081111 | 122.9755 | 122.8799 | 123.0451 | 66.6838 | -123.0967 | 122.8901 | 123.0542 | 122.8879 | 66.6874 | -123.3198
1171.8594 | 123.1384 | -66.7236 | 56.3644 | 0.0046549 | -0.01441 | 0.00067514 | 0.054149 | -0.0048096 | 0.06293 | 0.023044 | -0.0021983 | -0.00076913 | 0.058672 | 0.024104 | 0.058735 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1654 | 56.326 | -66.8467 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3305 | 56.1597 | -67.0744 | -0.12304 | -0.10802 | -0.009901 | -0.022372 | 0.10067 | -0.19899 | -0.038444 | -0.35077 | -0.20252 | -0.02833 | -0.062836 | 0.28794 | -0.033924 | -0.20471 | 122.9801 | 122.8891 | 123.0496 | 66.6884 | -123.2111 | 122.8856 | 123.0542 | 122.8834 | 66.6828 | -123.4388
1172.7969 | 123.175 | -66.7511 | 56.2958 | -0.0029761 | -0.014196 | 0.00088894 | 0.053936 | -0.0048096 | 0.06293 | 0.00015261 | -0.0019847 | -0.00055553 | 0.058672 | 0.023677 | 0.058735 | -66.729 | -0.030644 | -66.7414 | 56.2518 | 56.1609 | 56.3168 | -66.8558 | -66.752 | -0.040849 | -66.7819 | 56.1619 | 56.3259 | 56.1506 | -67.0698 | -0.10473 | -0.043937 | 0.022143 | 0.009672 | 0.1144 | -0.13491 | 0.021064 | -0.31873 | -0.13386 | -0.000864 | -0.030791 | 0.28794 | 0.030163 | -0.1452 | 123.0029 | 122.912 | 123.0679 | 66.7205 | -123.1516 | 122.913 | 123.077 | 122.9017 | 66.7103 | -123.3656
1173.8125 | 123.2208 | -66.7053 | 56.3324 | 0.0046549 | -0.014624 | 0.00067514 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058672 | 0.023891 | 0.058735 | -66.7335 | -0.039801 | -66.7506 | 56.2564 | 56.1563 | 56.3352 | -66.8467 | -66.7428 | -0.040849 | -66.7865 | 56.1619 | 56.3259 | 56.1506 | -67.0607 | -0.14135 | -0.07598 | -0.028212 | -0.045261 | 0.096089 | -0.17611 | 0.002758 | -0.35535 | -0.17048 | -0.037484 | -0.081147 | 0.2742 | -0.006458 | -0.18182 | 122.9617 | 122.8616 | 123.0405 | 66.6655 | -123.1791 | 122.8672 | 123.0313 | 122.8559 | 66.6645 | -123.3931
1174.7969 | 123.1522 | -66.7603 | 56.337 | 0.0046549 | -0.014196 | 0.00067514 | 0.053936 | -0.0050232 | 0.062503 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058458 | 0.023677 | 0.058949 | -66.729 | -0.039801 | -66.746 | 56.2564 | 56.1426 | 56.3352 | -66.8558 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3305 | 56.1597 | -67.0652 | -0.095576 | -0.080558 | 0.031298 | 0.014249 | 0.10983 | -0.19442 | -0.00182 | -0.30499 | -0.17964 | 0.012869 | -0.021636 | 0.28336 | -0.006458 | -0.17724 | 123.0167 | 122.9028 | 123.0954 | 66.7205 | -123.1928 | 122.9176 | 123.0908 | 122.92 | 66.7194 | -123.4022
1175.7969 | 123.1567 | -66.7694 | 56.3004 | -0.010607 | -0.01441 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | -0.0074779 | -0.0024119 | -0.0011965 | 0.058458 | 0.024104 | 0.058735 | -66.7198 | -0.039801 | -66.746 | 56.261 | 56.1563 | 56.326 | -66.8467 | -66.752 | -0.040849 | -66.7865 | 56.1665 | 56.3351 | 56.1552 | -67.0698 | -0.077263 | -0.039359 | 0.04961 | 0.023404 | 0.10067 | -0.14406 | 0.025643 | -0.30042 | -0.13386 | 0.017446 | -0.01706 | 0.28336 | 0.034742 | -0.1452 | 123.0304 | 122.9257 | 123.0954 | 66.7296 | -123.147 | 122.9359 | 123.1045 | 122.9246 | 66.7286 | -123.3702
1176.7969 | 123.1613 | -66.7648 | 56.3278 | -0.018238 | -0.01441 | 0.00088894 | 0.053936 | -0.0050232 | 0.062717 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058672 | 0.023891 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.1517 | 56.3214 | -66.8604 | -66.752 | -0.036271 | -66.7865 | 56.1665 | 56.3305 | 56.1643 | -67.0561 | -0.095576 | -0.071403 | 0.040455 | 0.018827 | 0.1144 | -0.17611 | -0.006401 | -0.29126 | -0.16132 | 0.012869 | -0.021637 | 0.26962 | 0.002697 | -0.16351 | 123.0212 | 122.9165 | 123.0863 | 66.7296 | -123.1882 | 122.9313 | 123.0953 | 122.9291 | 66.7286 | -123.3839
1177.7969 | 123.2071 | -66.7603 | 56.3049 | 0.0046549 | -0.014837 | 0.00067514 | 0.053722 | -0.0048096 | 0.062717 | 0.00015261 | -0.0017711 | -0.00055553 | 0.058458 | 0.024318 | 0.058522 | -66.7335 | -0.030644 | -66.7368 | 56.2564 | 56.1563 | 56.3214 | -66.8558 | -66.7428 | -0.040849 | -66.7865 | 56.1573 | 56.3351 | 56.1597 | -67.0652 | -0.095576 | -0.048515 | 0.02672 | 0.023406 | 0.11898 | -0.14864 | 0.016487 | -0.30499 | -0.14759 | 0.017448 | -0.026215 | 0.27878 | 0.030164 | -0.1452 | 123.0167 | 122.9165 | 123.0817 | 66.7296 | -123.1608 | 122.9176 | 123.0953 | 122.92 | 66.7194 | -123.3702
1178.875 | 123.2346 | -66.7282 | 56.25 | -0.0029761 | -0.01441 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0021983 | -0.00098273 | 0.057817 | 0.023891 | 0.058735 | -66.729 | -0.035222 | -66.7414 | 56.2518 | 56.1426 | 56.3214 | -66.8467 | -66.7565 | -0.040849 | -66.791 | 56.1619 | 56.3397 | 56.1597 | -67.0652 | -0.11846 | 0.001839 | -0.000746 | -0.013217 | 0.10524 | -0.10745 | 0.071419 | -0.33704 | -0.088083 | -0.028332 | -0.062837 | 0.2742 | 0.089675 | -0.090268 | 122.98 | 122.8708 | 123.0496 | 66.693 | -123.0967 | 122.8901 | 123.0679 | 122.8879 | 66.6874 | -123.3152
1179.7969 | 123.1522 | -66.7648 | 56.3049 | -0.010607 | -0.014196 | 0.0011025 | 0.054149 | -0.004596 | 0.062503 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058458 | 0.024104 | 0.058949 | -66.729 | -0.035222 | -66.7506 | 56.261 | 56.1609 | 56.3306 | -66.8604 | -66.7474 | -0.045428 | -66.7773 | 56.1573 | 56.3397 | 56.1597 | -67.0698 | -0.095576 | -0.043937 | 0.035876 | 0.014249 | 0.10983 | -0.14406 | 0.025644 | -0.30499 | -0.14759 | 0.017447 | -0.012479 | 0.29252 | 0.034743 | -0.1452 | 123.0258 | 122.9257 | 123.0954 | 66.7296 | -123.1653 | 122.9222 | 123.1045 | 122.9246 | 66.7194 | -123.3748
1180.8594 | 123.2666 | -66.687 | 56.2683 | 0.0046549 | -0.01441 | 0.00088894 | 0.054149 | -0.004596 | 0.06293 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058672 | 0.023891 | 0.058735 | -66.7335 | -0.035222 | -66.7368 | 56.2564 | 56.1609 | 56.3214 | -66.8513 | -66.752 | -0.045428 | -66.7819 | 56.1665 | 56.3351 | 56.1597 | -67.0744 | -0.16424 | -0.011894 | -0.046522 | -0.049836 | 0.1144 | -0.10744 | 0.053108 | -0.38739 | -0.10181 | -0.064951 | -0.094878 | 0.29251 | 0.066785 | -0.10858 | 122.9434 | 122.8479 | 123.0084 | 66.6518 | -123.1196 | 122.8535 | 123.0221 | 122.8467 | 66.6416 | -123.3427
1181.7969 | 123.1247 | -66.7694 | 56.3187 | -0.0029761 | -0.01441 | 0.00088894 | 0.053722 | -0.0048096 | 0.06293 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058458 | 0.023891 | 0.058949 | -66.7244 | -0.030644 | -66.746 | 56.2564 | 56.1563 | 56.326 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1573 | 56.3305 | 56.1552 | -67.0652 | -0.081842 | -0.062248 | 0.045032 | 0.023404 | 0.10525 | -0.16238 | 0.007332 | -0.29584 | -0.16133 | 0.017446 | -0.01706 | 0.27878 | 0.011852 | -0.16351 | 123.0258 | 122.9257 | 123.0954 | 66.7388 | -123.1699 | 122.9267 | 123.0999 | 122.9246 | 66.7286 | -123.3839
1182.7969 | 123.2666 | -66.7282 | 56.2775 | 0.0046549 | -0.014624 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | 0.00015261 | -0.0021983 | -0.00055553 | 0.058458 | 0.023677 | 0.058735 | -66.7381 | -0.030644 | -66.7414 | 56.261 | 56.1609 | 56.3168 | -66.8558 | -66.752 | -0.045428 | -66.7819 | 56.1619 | 56.3351 | 56.1506 | -67.0698 | -0.12762 | -0.016471 | -0.009902 | -0.013217 | 0.1144 | -0.1166 | 0.039374 | -0.34162 | -0.11555 | -0.023753 | -0.05368 | 0.28794 | 0.05763 | -0.12689 | 122.9892 | 122.8891 | 123.0451 | 66.6976 | -123.1333 | 122.8901 | 123.0633 | 122.8788 | 66.6828 | -123.3473
1183.875 | 123.2254 | -66.7374 | 56.2729 | -0.0029761 | -0.014624 | 0.0011025 | 0.054363 | -0.0050232 | 0.062717 | -0.0074779 | -0.0017711 | -0.00055553 | 0.058458 | 0.024104 | 0.058735 | -66.729 | -0.035222 | -66.7368 | 56.2564 | 56.1609 | 56.326 | -66.8513 | -66.752 | -0.040849 | -66.7865 | 56.1528 | 56.3305 | 56.1552 | -67.0698 | -0.11389 | -0.016471 | 0.00841 | 0.000518 | 0.1144 | -0.11202 | 0.053109 | -0.33246 | -0.12013 | -0.014597 | -0.049103 | 0.28336 | 0.057629 | -0.11774 | 122.9938 | 122.8982 | 123.0634 | 66.7021 | -123.1241 | 122.8901 | 123.0679 | 122.8925 | 66.6965 | -123.3427
1184.7969 | 123.1796 | -66.7465 | 56.3049 | 0.0046549 | -0.015051 | 0.0011025 | 0.054149 | -0.0048096 | 0.06293 | -0.0074779 | -0.0017711 | -0.00098273 | 0.058245 | 0.024318 | 0.058949 | -66.7335 | -0.035222 | -66.746 | 56.261 | 56.1517 | 56.3214 | -66.8467 | -66.7382 | -0.027113 | -66.7773 | 56.1573 | 56.3305 | 56.1643 | -67.0698 | -0.10015 | -0.043937 | 0.012987 | 0.000516 | 0.10067 | -0.15322 | 0.016487 | -0.32331 | -0.14759 | 0.008294 | -0.03079 | 0.29252 | 0.025585 | -0.14062 | 123.0075 | 122.8982 | 123.0679 | 66.7113 | -123.1516 | 122.9039 | 123.077 | 122.9108 | 66.7194 | -123.3748
1185.7969 | 123.2071 | -66.7374 | 56.2912 | -0.0029761 | -0.01441 | 0.0013163 | 0.053722 | -0.0050232 | 0.06293 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058245 | 0.023891 | 0.058735 | -66.729 | -0.035222 | -66.7368 | 56.2564 | 56.138 | 56.326 | -66.8513 | -66.7428 | -0.040849 | -66.7819 | 56.1619 | 56.3351 | 56.1597 | -67.0607 | -0.11389 | -0.034782 | 0.00841 | 0.000518 | 0.1144 | -0.15322 | 0.034798 | -0.3233 | -0.12928 | -0.00544 | -0.044524 | 0.27878 | 0.043897 | -0.13147 | 122.9938 | 122.8753 | 123.0634 | 66.7021 | -123.1424 | 122.8993 | 123.0725 | 122.8971 | 66.6965 | -123.3519
1186.7969 | 123.262 | -66.6962 | 56.3187 | 0.0046549 | -0.014624 | 0.00067514 | 0.053936 | -0.004596 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058458 | 0.024104 | 0.058308 | -66.729 | -0.035222 | -66.746 | 56.2564 | 56.1517 | 56.3214 | -66.8513 | -66.7382 | -0.040849 | -66.7773 | 56.1711 | 56.3351 | 56.1689 | -67.0744 | -0.15508 | -0.062248 | -0.032789 | -0.049838 | 0.10525 | -0.16695 | 0.002754 | -0.37824 | -0.14759 | -0.04206 | -0.081144 | 0.29709 | 0.016431 | -0.14978 | 122.9526 | 122.8479 | 123.0176 | 66.6609 | -123.1699 | 122.8672 | 123.0313 | 122.8651 | 66.6553 | -123.3931
1187.7969 | 123.1522 | -66.7511 | 56.3004 | -0.018238 | -0.014624 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058458 | 0.023891 | 0.058735 | -66.7244 | -0.035222 | -66.7414 | 56.2564 | 56.1609 | 56.3214 | -66.8558 | -66.752 | -0.036271 | -66.7865 | 56.1619 | 56.3305 | 56.1552 | -67.0652 | -0.10473 | -0.043937 | 0.026722 | 0.009672 | 0.1144 | -0.13949 | 0.021065 | -0.31415 | -0.13844 | -0.000864 | -0.03537 | 0.27878 | 0.030163 | -0.1452 | 123.0075 | 122.912 | 123.0725 | 66.7159 | -123.1562 | 122.913 | 123.0816 | 122.9063 | 66.7148 | -123.3656
1188.7969 | 123.2803 | -66.7145 | 56.3141 | -0.0029761 | -0.014624 | 0.00067514 | 0.053936 | -0.0052368 | 0.062503 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058458 | 0.023677 | 0.058949 | -66.7335 | -0.035222 | -66.7414 | 56.2518 | 56.1654 | 56.326 | -66.8558 | -66.7474 | -0.040849 | -66.7819 | 56.1619 | 56.3305 | 56.1597 | -67.0698 | -0.14135 | -0.062248 | -0.019056 | -0.026949 | 0.1144 | -0.14864 | 0.01191 | -0.35535 | -0.15217 | -0.032907 | -0.067412 | 0.28794 | 0.01643 | -0.15436 | 122.9663 | 122.8799 | 123.0405 | 66.6793 | -123.1699 | 122.8764 | 123.045 | 122.8742 | 66.6736 | -123.3839
1189.8594 | 123.2071 | -66.7374 | 56.3049 | -0.010607 | -0.014837 | 0.00067514 | 0.053722 | -0.0052368 | 0.062717 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058458 | 0.024104 | 0.058735 | -66.7244 | -0.039801 | -66.7414 | 56.261 | 56.1563 | 56.3306 | -66.8375 | -66.7474 | -0.036271 | -66.7819 | 56.1573 | 56.3259 | 56.1689 | -67.0698 | -0.10015 | -0.043937 | 0.012989 | -0.004061 | 0.096087 | -0.14864 | 0.025644 | -0.33246 | -0.14759 | -0.010019 | -0.044524 | 0.28794 | 0.021007 | -0.13604 | 122.9984 | 122.8937 | 123.0679 | 66.6976 | -123.1424 | 122.8947 | 123.0633 | 122.9063 | 66.7011 | -123.3748
1190.7969 | 123.2712 | -66.7007 | 56.282 | -0.0029761 | -0.014624 | 0.0013163 | 0.054149 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058672 | 0.024318 | 0.058735 | -66.729 | -0.039801 | -66.746 | 56.2518 | 56.1609 | 56.3214 | -66.8558 | -66.7474 | -0.040849 | -66.7773 | 56.1711 | 56.3351 | 56.1689 | -67.0698 | -0.15508 | -0.030204 | -0.028211 | -0.04526 | 0.10983 | -0.12118 | 0.039376 | -0.36908 | -0.11097 | -0.04664 | -0.076566 | 0.29252 | 0.053053 | -0.11315 | 122.9526 | 122.8616 | 123.0222 | 66.6609 | -123.1379 | 122.8718 | 123.0358 | 122.8696 | 66.6599 | -123.3519
1191.7969 | 123.1842 | -66.7511 | 56.3141 | -0.010607 | -0.01441 | 0.00067514 | 0.053936 | -0.0050232 | 0.06293 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.024532 | 0.058949 | -66.7381 | -0.039801 | -66.7414 | 56.261 | 56.1609 | 56.3214 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1619 | 56.3351 | 56.1597 | -67.0698 | -0.10473 | -0.053092 | 0.012987 | 0.009672 | 0.1144 | -0.15322 | 0.007332 | -0.31873 | -0.15217 | 0.003714 | -0.03537 | 0.28336 | 0.021009 | -0.15436 | 123.0121 | 122.912 | 123.0725 | 66.7113 | -123.1699 | 122.913 | 123.0862 | 122.9108 | 66.7103 | -123.3839
1192.7969 | 123.2162 | -66.7191 | 56.2637 | -0.010607 | -0.014624 | 0.00088894 | 0.054363 | -0.0050232 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.058458 | 0.024318 | 0.058735 | -66.7244 | -0.026065 | -66.7368 | 56.2518 | 56.1563 | 56.326 | -66.8467 | -66.752 | -0.050007 | -66.7819 | 56.1573 | 56.3305 | 56.1597 | -67.0607 | -0.12762 | -0.011894 | -0.005322 | -0.017793 | 0.10982 | -0.10744 | 0.062264 | -0.34161 | -0.10639 | -0.032908 | -0.062835 | 0.27878 | 0.066784 | -0.104 | 122.9709 | 122.8753 | 123.0451 | 66.693 | -123.1104 | 122.8764 | 123.0496 | 122.8788 | 66.669 | -123.3244
1193.875 | 123.2483 | -66.7053 | 56.2958 | 0.012286 | -0.014837 | 0.00067514 | 0.053936 | -0.0048096 | 0.06293 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058245 | 0.024532 | 0.058735 | -66.729 | -0.039801 | -66.7414 | 56.261 | 56.1563 | 56.3214 | -66.8558 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3351 | 56.1597 | -67.0698 | -0.15051 | -0.034781 | -0.023634 | -0.036105 | 0.1144 | -0.13949 | 0.025643 | -0.3645 | -0.13386 | -0.046641 | -0.081147 | 0.28336 | 0.03932 | -0.13604 | 122.9663 | 122.8616 | 123.0267 | 66.6655 | -123.1516 | 122.8672 | 123.0404 | 122.8651 | 66.6645 | -123.3656
1194.7969 | 123.262 | -66.6916 | 56.3049 | 0.0046549 | -0.014837 | 0.00088894 | 0.053936 | -0.0048096 | 0.063144 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058672 | 0.024104 | 0.058522 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1654 | 56.3214 | -66.8467 | -66.7474 | -0.040849 | -66.7773 | 56.1619 | 56.3443 | 56.1643 | -67.0698 | -0.15508 | -0.048515 | -0.041945 | -0.054416 | 0.10067 | -0.13949 | 0.016487 | -0.37824 | -0.14301 | -0.055796 | -0.085722 | 0.29252 | 0.039321 | -0.14062 | 122.948 | 122.857 | 123.013 | 66.6564 | -123.1516 | 122.8535 | 123.0358 | 122.8559 | 66.6507 | -123.3748
1195.7969 | 123.2483 | -66.7099 | 56.2958 | 0.0046549 | -0.015051 | 0.00088894 | 0.054363 | -0.0050232 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058245 | 0.024318 | 0.058949 | -66.7335 | -0.039801 | -66.746 | 56.2564 | 56.1609 | 56.3214 | -66.8558 | -66.7474 | -0.036271 | -66.7773 | 56.1528 | 56.3351 | 56.1506 | -67.0652 | -0.14593 | -0.039359 | -0.023634 | -0.036105 | 0.10983 | -0.13491 | 0.025643 | -0.35535 | -0.14302 | -0.037485 | -0.067411 | 0.28794 | 0.03932 | -0.1452 | 122.9663 | 122.8708 | 123.0313 | 66.6701 | -123.1516 | 122.8627 | 123.045 | 122.8605 | 66.6736 | -123.361
1196.7969 | 123.23 | -66.6962 | 56.3049 | 0.019917 | -0.015051 | 0.00067514 | 0.054363 | -0.0054506 | 0.062717 | 0.00015261 | -0.0021983 | -0.0011965 | 0.058458 | 0.024318 | 0.058735 | -66.7244 | -0.039801 | -66.7506 | 56.2564 | 56.1609 | 56.326 | -66.8558 | -66.7474 | -0.036271 | -66.7773 | 56.1619 | 56.3351 | 56.1689 | -67.0698 | -0.15966 | -0.048515 | -0.02821 | -0.054416 | 0.10525 | -0.14406 | 0.021065 | -0.37366 | -0.14301 | -0.051218 | -0.081144 | 0.29252 | 0.030164 | -0.13604 | 122.9526 | 122.857 | 123.0222 | 66.6564 | -123.1608 | 122.8581 | 123.0313 | 122.8651 | 66.6599 | -123.3748
1197.7969 | 123.2895 | -66.7099 | 56.2866 | -0.0029761 | -0.015051 | 0.0011025 | 0.053936 | -0.0052368 | 0.063144 | 0.00015261 | -0.0021983 | -0.0011965 | 0.058458 | 0.023891 | 0.058949 | -66.7381 | -0.030644 | -66.7506 | 56.2564 | 56.1609 | 56.3168 | -66.8513 | -66.752 | -0.040849 | -66.7773 | 56.1665 | 56.3351 | 56.1506 | -67.0698 | -0.14135 | -0.030204 | -0.028212 | -0.040683 | 0.10067 | -0.12575 | 0.030219 | -0.35993 | -0.12012 | -0.042063 | -0.067411 | 0.29252 | 0.048475 | -0.13605 | 122.9663 | 122.8708 | 123.0267 | 66.6793 | -123.1379 | 122.8764 | 123.045 | 122.8605 | 66.6691 | -123.3564
1198.875 | 123.2208 | -66.7145 | 56.3278 | -0.0029761 | -0.014837 | 0.0011025 | 0.053936 | -0.0052368 | 0.062503 | 0.015414 | -0.0021983 | -0.00076913 | 0.058245 | 0.024532 | 0.058308 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.1609 | 56.3214 | -66.8513 | -66.7428 | -0.040849 | -66.791 | 56.1573 | 56.3351 | 56.1597 | -67.0652 | -0.13677 | -0.071403 | -0.009899 | -0.031527 | 0.10525 | -0.16695 | -0.006401 | -0.35077 | -0.17048 | -0.028328 | -0.076569 | 0.2742 | 0.007276 | -0.16809 | 122.9709 | 122.8753 | 123.0359 | 66.6793 | -123.1791 | 122.8718 | 123.0496 | 122.8742 | 66.6736 | -123.3931
1199.7969 | 123.23 | -66.7191 | 56.2912 | -0.0029761 | -0.014624 | 0.0011025 | 0.054363 | -0.0048096 | 0.062717 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058458 | 0.024532 | 0.058522 | -66.729 | -0.026065 | -66.7368 | 56.2564 | 56.1654 | 56.326 | -66.8513 | -66.7474 | -0.045428 | -66.7865 | 56.1619 | 56.3351 | 56.1506 | -67.0652 | -0.1322 | -0.034782 | -0.009901 | -0.017793 | 0.1144 | -0.12575 | 0.034798 | -0.34619 | -0.12928 | -0.02833 | -0.067414 | 0.27878 | 0.043897 | -0.14062 | 122.9755 | 122.8845 | 123.0451 | 66.693 | -123.1424 | 122.881 | 123.0542 | 122.8696 | 66.6736 | -123.3564
1200.7969 | 123.1842 | -66.7282 | 56.3461 | -0.0029761 | -0.014837 | 0.00088894 | 0.054149 | -0.0048096 | 0.06293 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058672 | 0.024532 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.17 | 56.326 | -66.8513 | -66.7474 | -0.050007 | -66.7819 | 56.1665 | 56.3305 | 56.1643 | -67.0698 | -0.12304 | -0.089713 | 0.003833 | -0.017795 | 0.10525 | -0.1761 | -0.020133 | -0.34162 | -0.17963 | -0.019175 | -0.05368 | 0.28794 | -0.015613 | -0.18182 | 122.9846 | 122.8982 | 123.0542 | 66.693 | -123.1974 | 122.8947 | 123.0587 | 122.8925 | 66.6782 | -123.416
1201.8594 | 123.2437 | -66.7465 | 56.2775 | -0.0029761 | -0.015051 | 0.00088894 | 0.053936 | -0.0050232 | 0.062289 | -0.0074779 | -0.0024119 | -0.00098273 | 0.058245 | 0.024745 | 0.058522 | -66.7244 | -0.035222 | -66.7368 | 56.2564 | 56.1563 | 56.3306 | -66.8513 | -66.7474 | -0.040849 | -66.7819 | 56.1665 | 56.3443 | 56.1506 | -67.0698 | -0.10473 | -0.021049 | 0.022144 | 0.009673 | 0.1144 | -0.12118 | 0.05311 | -0.32331 | -0.11097 | -0.000864 | -0.035369 | 0.28794 | 0.066787 | -0.12689 | 123.0029 | 122.9028 | 123.0771 | 66.7113 | -123.1287 | 122.913 | 123.0908 | 122.8971 | 66.7057 | -123.3473
1202.7969 | 123.2849 | -66.6916 | 56.2775 | 0.0046549 | -0.015051 | 0.00067514 | 0.054149 | -0.0050232 | 0.06293 | 0.015414 | -0.0019847 | -0.00098273 | 0.058458 | 0.024318 | 0.058735 | -66.729 | -0.030644 | -66.7552 | 56.2564 | 56.1654 | 56.326 | -66.8513 | -66.752 | -0.036271 | -66.7773 | 56.1619 | 56.3397 | 56.1643 | -67.0698 | -0.15966 | -0.021049 | -0.037367 | -0.063572 | 0.09609 | -0.11202 | 0.048531 | -0.37824 | -0.11555 | -0.060374 | -0.085722 | 0.29252 | 0.062209 | -0.11315 | 122.948 | 122.857 | 123.0176 | 66.6609 | -123.1287 | 122.8535 | 123.0313 | 122.8559 | 66.6553 | -123.3473
1203.7969 | 123.1705 | -66.7419 | 56.3004 | -0.0029761 | -0.015051 | 0.00088894 | 0.053508 | -0.0052368 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058672 | 0.024532 | 0.058308 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1563 | 56.326 | -66.8558 | -66.7474 | -0.036271 | -66.7819 | 56.1619 | 56.3305 | 56.1552 | -67.0698 | -0.11389 | -0.039359 | 0.017566 | -0.004062 | 0.10983 | -0.14406 | 0.025643 | -0.32788 | -0.13844 | -0.005442 | -0.039947 | 0.28794 | 0.030163 | -0.1452 | 123.0029 | 122.8982 | 123.0679 | 66.7067 | -123.1562 | 122.9039 | 123.0725 | 122.8971 | 66.7057 | -123.3702
1204.8594 | 123.2941 | -66.6916 | 56.3187 | -0.010607 | -0.014624 | 0.00067514 | 0.054149 | -0.0052368 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058245 | 0.024318 | 0.058735 | -66.7335 | -0.035222 | -66.7323 | 56.2564 | 56.1563 | 56.3214 | -66.8604 | -66.7474 | -0.040849 | -66.7819 | 56.1573 | 56.3305 | 56.1597 | -67.0744 | -0.16882 | -0.062248 | -0.041945 | -0.040681 | 0.12814 | -0.16238 | 0.002754 | -0.38282 | -0.16133 | -0.055796 | -0.090301 | 0.29251 | 0.011852 | -0.15893 | 122.948 | 122.8479 | 123.013 | 66.6564 | -123.1791 | 122.8489 | 123.0221 | 122.8513 | 66.6507 | -123.3931
1205.7969 | 123.262 | -66.6824 | 56.3004 | 0.012286 | -0.014837 | 0.00088894 | 0.054149 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058458 | 0.024318 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.1563 | 56.3306 | -66.8467 | -66.752 | -0.040849 | -66.7865 | 56.1573 | 56.3351 | 56.1552 | -67.0652 | -0.16424 | -0.043937 | -0.041943 | -0.063571 | 0.10067 | -0.14406 | 0.030222 | -0.38281 | -0.14301 | -0.069529 | -0.10403 | 0.27878 | 0.034742 | -0.1452 | 122.9389 | 122.8387 | 123.013 | 66.6472 | -123.147 | 122.8398 | 123.0175 | 122.8376 | 66.6416 | -123.3656
1206.7969 | 123.1705 | -66.7419 | 56.3782 | 0.0046549 | -0.015051 | 0.00024794 | 0.053508 | -0.0052368 | 0.062717 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058458 | 0.024104 | 0.058522 | -66.7335 | -0.039801 | -66.7368 | 56.2564 | 56.1609 | 56.3352 | -66.8558 | -66.7474 | -0.045428 | -66.7819 | 56.1665 | 56.3397 | 56.1689 | -67.0698 | -0.11389 | -0.12176 | 0.008409 | 0.005095 | 0.11898 | -0.21731 | -0.043019 | -0.32788 | -0.21168 | -0.005442 | -0.039947 | 0.28794 | -0.038499 | -0.20929 | 122.9984 | 122.9028 | 123.0771 | 66.7021 | -123.234 | 122.9084 | 123.0816 | 122.9108 | 66.6965 | -123.448
1207.7969 | 123.2758 | -66.6779 | 56.2866 | -0.0029761 | -0.014624 | 0.00067514 | 0.053722 | -0.0052368 | 0.062076 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058672 | 0.024104 | 0.058522 | -66.7335 | -0.035222 | -66.746 | 56.2473 | 56.1517 | 56.326 | -66.8467 | -66.7474 | -0.045428 | -66.7819 | 56.1528 | 56.3305 | 56.1552 | -67.0698 | -0.16882 | -0.039361 | -0.055678 | -0.068149 | 0.10067 | -0.13491 | 0.039376 | -0.39197 | -0.13386 | -0.069529 | -0.10403 | 0.28794 | 0.043896 | -0.13147 | 122.9251 | 122.8296 | 123.0039 | 66.6426 | -123.1333 | 122.8306 | 123.0084 | 122.833 | 66.6324 | -123.3564
1208.7969 | 123.1613 | -66.7557 | 56.3324 | -0.0029761 | -0.014624 | 0.00067514 | 0.053936 | -0.0050232 | 0.06293 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058245 | 0.024532 | 0.058735 | -66.729 | -0.030644 | -66.746 | 56.261 | 56.1609 | 56.3306 | -66.8467 | -66.752 | -0.031692 | -66.7819 | 56.1573 | 56.3351 | 56.1597 | -67.0698 | -0.090996 | -0.071402 | 0.02672 | 0.009671 | 0.10067 | -0.17153 | -0.001821 | -0.31415 | -0.17506 | 0.003713 | -0.026214 | 0.28794 | 0.002699 | -0.17267 | 123.0167 | 122.9165 | 123.0863 | 66.725 | -123.1791 | 122.913 | 123.0908 | 122.9154 | 66.724 | -123.4022
1209.8594 | 123.2712 | -66.7328 | 56.2958 | -0.0029761 | -0.015478 | 0.00067514 | 0.054363 | -0.0052368 | 0.062717 | 0.0077831 | -0.0019847 | -0.0011965 | 0.058245 | 0.024532 | 0.058735 | -66.729 | -0.035222 | -66.7414 | 56.261 | 56.1654 | 56.326 | -66.8513 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3305 | 56.1552 | -67.0744 | -0.11846 | -0.034781 | 0.003832 | -0.008639 | 0.10982 | -0.13033 | 0.030221 | -0.34162 | -0.13844 | -0.019175 | -0.053681 | 0.28794 | 0.034741 | -0.14062 | 122.9938 | 122.8982 | 123.0588 | 66.6976 | -123.147 | 122.8901 | 123.0633 | 122.8879 | 66.6965 | -123.3702
1210.7969 | 123.1384 | -66.7419 | 56.3049 | -0.0029761 | -0.014837 | 0.00088894 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0017711 | -0.0011965 | 0.058458 | 0.024745 | 0.058735 | -66.729 | -0.035222 | -66.7368 | 56.2564 | 56.17 | 56.3352 | -66.8421 | -66.7474 | -0.036271 | -66.7819 | 56.1619 | 56.3397 | 56.1597 | -67.0698 | -0.10015 | -0.048515 | 0.012987 | 0.005095 | 0.10525 | -0.13491 | 0.030223 | -0.32788 | -0.14301 | -0.005442 | -0.039947 | 0.28794 | 0.034743 | -0.1452 | 122.9984 | 122.912 | 123.0771 | 66.7067 | -123.147 | 122.9039 | 123.0816 | 122.9017 | 66.7057 | -123.3748
1211.7969 | 123.1384 | -66.7648 | 56.3416 | 0.012286 | -0.015051 | 0.0011025 | 0.053936 | -0.0052368 | 0.062503 | 0.0077831 | -0.0013437 | -0.00098273 | 0.058886 | 0.024532 | 0.058522 | -66.7335 | -0.035222 | -66.746 | 56.2564 | 56.1517 | 56.326 | -66.8604 | -66.752 | -0.040849 | -66.791 | 56.1665 | 56.3305 | 56.1643 | -67.0744 | -0.095576 | -0.085136 | 0.031298 | 0.018827 | 0.1144 | -0.18984 | -0.015556 | -0.30957 | -0.17506 | 0.012869 | -0.026215 | 0.28336 | -0.011036 | -0.17724 | 123.0212 | 122.9165 | 123.0908 | 66.7296 | -123.202 | 122.9313 | 123.0953 | 122.9291 | 66.724 | -123.416
1212.7969 | 123.2117 | -66.7145 | 56.3187 | 0.0046549 | -0.015478 | 0.00088894 | 0.053936 | -0.0048096 | 0.062717 | 0.00015261 | -0.0024119 | -0.00034193 | 0.058245 | 0.024318 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.1609 | 56.3306 | -66.8467 | -66.752 | -0.040849 | -66.7865 | 56.1619 | 56.3351 | 56.1735 | -67.0744 | -0.13219 | -0.062248 | -0.009899 | -0.031527 | 0.10067 | -0.1578 | 0.011911 | -0.35993 | -0.15675 | -0.037485 | -0.071991 | 0.28794 | 0.016431 | -0.1452 | 122.9709 | 122.8753 | 123.0451 | 66.6793 | -123.1653 | 122.8764 | 123.0496 | 122.8879 | 66.6736 | -123.3931
1213.7969 | 123.1476 | -66.7786 | 56.3004 | -0.010607 | -0.014837 | 0.00067514 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058458 | 0.024532 | 0.058735 | -66.729 | -0.030644 | -66.746 | 56.2564 | 56.1563 | 56.326 | -66.8558 | -66.752 | -0.040849 | -66.7773 | 56.1665 | 56.3397 | 56.1735 | -67.0698 | -0.077266 | -0.043937 | 0.049608 | 0.032559 | 0.10983 | -0.14406 | 0.025643 | -0.29126 | -0.13386 | 0.026601 | 0.001253 | 0.29252 | 0.039321 | -0.12689 | 123.035 | 122.9349 | 123.1046 | 66.7479 | -123.1562 | 122.9451 | 123.1182 | 122.952 | 66.7377 | -123.3702
1214.7969 | 123.2025 | -66.7282 | 56.2866 | 0.0046549 | -0.015051 | 0.0011025 | 0.053722 | -0.0048096 | 0.06293 | 0.015414 | -0.0021983 | -0.00098273 | 0.058031 | 0.024532 | 0.058308 | -66.729 | -0.039801 | -66.7552 | 56.261 | 56.1654 | 56.3306 | -66.8604 | -66.752 | -0.040849 | -66.7819 | 56.1573 | 56.3351 | 56.1552 | -67.0698 | -0.1322 | -0.025626 | -0.000746 | -0.026951 | 0.10525 | -0.12117 | 0.043955 | -0.34162 | -0.12928 | -0.023753 | -0.05368 | 0.28794 | 0.048475 | -0.13147 | 122.9892 | 122.8937 | 123.0588 | 66.6884 | -123.147 | 122.8855 | 123.0633 | 122.8834 | 66.6874 | -123.3564
1215.8594 | 123.0377 | -66.806 | 56.25 | -0.010607 | -0.015051 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058458 | 0.024318 | 0.058735 | -66.7335 | -0.030644 | -66.746 | 56.2564 | 56.1609 | 56.326 | -66.8513 | -66.7428 | -0.036271 | -66.7865 | 56.1619 | 56.3397 | 56.1552 | -67.0652 | -0.045221 | 0.006417 | 0.072496 | 0.060025 | 0.10525 | -0.089132 | 0.075997 | -0.25922 | -0.088083 | 0.063224 | 0.019561 | 0.27878 | 0.089675 | -0.094847 | 123.0624 | 122.9669 | 123.132 | 66.7754 | -123.1013 | 122.9679 | 123.1457 | 122.9612 | 66.7698 | -123.3152
1216.7969 | 123.1384 | -66.774 | 56.3232 | -0.0029761 | -0.014837 | 0.00088894 | 0.053722 | -0.0048096 | 0.062503 | -0.0074779 | -0.0017711 | -0.00055553 | 0.058458 | 0.023891 | 0.058522 | -66.7335 | -0.035222 | -66.7414 | 56.2656 | 56.1563 | 56.3306 | -66.8558 | -66.752 | -0.045428 | -66.791 | 56.1573 | 56.3397 | 56.1689 | -67.0698 | -0.081843 | -0.057668 | 0.040453 | 0.03256 | 0.1144 | -0.16695 | 0.007334 | -0.29584 | -0.1659 | 0.022024 | -0.01706 | 0.27878 | 0.016433 | -0.15435 | 123.0396 | 122.9303 | 123.1046 | 66.7388 | -123.1791 | 122.9313 | 123.1137 | 122.9429 | 66.7286 | -123.3931
1217.8594 | 123.1476 | -66.7099 | 56.3187 | 0.0046549 | -0.015051 | 0.00046154 | 0.053936 | -0.0048096 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058245 | 0.024318 | 0.058949 | -66.7244 | -0.030644 | -66.7414 | 56.261 | 56.1609 | 56.3397 | -66.8604 | -66.7382 | -0.036271 | -66.7865 | 56.1619 | 56.3305 | 56.1552 | -67.0744 | -0.15051 | -0.05767 | -0.014477 | -0.031527 | 0.11898 | -0.1578 | 0.021068 | -0.3645 | -0.15675 | -0.028327 | -0.076569 | 0.28794 | 0.011852 | -0.16351 | 122.9709 | 122.8708 | 123.0496 | 66.6793 | -123.1791 | 122.8718 | 123.0404 | 122.8651 | 66.6736 | -123.3931
1218.7969 | 123.1293 | -66.7557 | 56.3141 | 0.0046549 | -0.015265 | 0.00067514 | 0.053722 | -0.0048096 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058245 | 0.024104 | 0.058522 | -66.7335 | -0.035222 | -66.7368 | 56.261 | 56.1563 | 56.3214 | -66.8513 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3351 | 56.1597 | -67.0698 | -0.095575 | -0.053092 | 0.022142 | 0.018828 | 0.1144 | -0.1578 | 0.007332 | -0.31415 | -0.14759 | 0.008291 | -0.026214 | 0.28794 | 0.021009 | -0.15436 | 123.0167 | 122.912 | 123.0771 | 66.7205 | -123.1653 | 122.9222 | 123.0908 | 122.9154 | 66.7194 | -123.3839
1219.8594 | 123.1384 | -66.7419 | 56.3232 | 0.0046549 | -0.015051 | 0.00067514 | 0.053722 | -0.0048096 | 0.062289 | 0.0077831 | -0.0024119 | -0.00098273 | 0.058245 | 0.024745 | 0.058735 | -66.7335 | -0.039801 | -66.7506 | 56.261 | 56.1563 | 56.326 | -66.8558 | -66.7474 | -0.036271 | -66.7865 | 56.1665 | 56.3351 | 56.1552 | -67.079 | -0.11389 | -0.062247 | 0.008409 | -0.00864 | 0.10525 | -0.16695 | 0.002755 | -0.33704 | -0.15675 | -0.005442 | -0.044526 | 0.29251 | 0.011854 | -0.16809 | 123.0029 | 122.8982 | 123.0679 | 66.7021 | -123.1791 | 122.9084 | 123.077 | 122.8971 | 66.7057 | -123.4022
1220.7969 | 123.2346 | -66.7282 | 56.2775 | -0.010607 | -0.015051 | 0.00067514 | 0.054149 | -0.0052368 | 0.062289 | 0.0077831 | -0.0021983 | -0.00055553 | 0.058245 | 0.024532 | 0.058735 | -66.729 | -0.035222 | -66.7506 | 56.261 | 56.1609 | 56.3306 | -66.8513 | -66.7428 | -0.045428 | -66.7819 | 56.1573 | 56.3351 | 56.1643 | -67.0698 | -0.12304 | -0.016471 | -0.000746 | -0.022373 | 0.10067 | -0.1166 | 0.05311 | -0.34162 | -0.12013 | -0.014596 | -0.05368 | 0.28794 | 0.05763 | -0.11315 | 122.9892 | 122.8891 | 123.0588 | 66.693 | -123.1287 | 122.8855 | 123.0633 | 122.8925 | 66.6828 | -123.3473
1221.7969 | 123.1659 | -66.7465 | 56.3095 | -0.0029761 | -0.014837 | 0.00088894 | 0.053936 | -0.0052368 | 0.062717 | -0.0074779 | -0.0017711 | -0.0011965 | 0.058245 | 0.024532 | 0.058308 | -66.7381 | -0.035222 | -66.746 | 56.2702 | 56.17 | 56.3306 | -66.8604 | -66.7428 | -0.040849 | -66.7819 | 56.1619 | 56.3351 | 56.1643 | -67.0652 | -0.11389 | -0.039357 | 0.008409 | 0.000516 | 0.1144 | -0.13948 | 0.021067 | -0.31873 | -0.14759 | 0.003715 | -0.035369 | 0.28336 | 0.025587 | -0.1452 | 123.0167 | 122.9165 | 123.0771 | 66.7113 | -123.1699 | 122.9084 | 123.0816 | 122.9108 | 66.7057 | -123.3748
1222.7969 | 123.1476 | -66.7465 | 56.2958 | -0.010607 | -0.015051 | 0.00088894 | 0.053936 | -0.0052368 | 0.062076 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058458 | 0.024532 | 0.058522 | -66.729 | -0.039801 | -66.7414 | 56.2564 | 56.1654 | 56.326 | -66.8604 | -66.7474 | -0.036271 | -66.791 | 56.1619 | 56.3397 | 56.1643 | -67.0744 | -0.11389 | -0.039359 | 0.017565 | 0.005094 | 0.11898 | -0.13033 | 0.030221 | -0.32788 | -0.13386 | -0.000864 | -0.044526 | 0.28336 | 0.043899 | -0.13146 | 123.0029 | 122.912 | 123.0725 | 66.7067 | -123.1562 | 122.9084 | 123.0862 | 122.9108 | 66.7103 | -123.3702
1223.875 | 123.2437 | -66.7145 | 56.282 | 0.0046549 | -0.014837 | 0.0011025 | 0.053722 | -0.0052368 | 0.062503 | -0.015108 | -0.0019847 | -0.00055553 | 0.058031 | 0.024745 | 0.058308 | -66.7244 | -0.030644 | -66.7323 | 56.2564 | 56.1563 | 56.326 | -66.8604 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3351 | 56.1506 | -67.0744 | -0.14593 | -0.025626 | -0.009899 | -0.017792 | 0.12814 | -0.12575 | 0.043954 | -0.35993 | -0.11555 | -0.032907 | -0.067412 | 0.29251 | 0.053053 | -0.13147 | 122.9709 | 122.8708 | 123.0405 | 66.6838 | -123.1425 | 122.881 | 123.0496 | 122.8651 | 66.6782 | -123.3564
1224.7969 | 123.175 | -66.774 | 56.3095 | -0.010607 | -0.014837 | 0.0011025 | 0.053722 | -0.0048096 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058031 | 0.024318 | 0.058522 | -66.7244 | -0.030644 | -66.7368 | 56.261 | 56.1563 | 56.3397 | -66.8467 | -66.7428 | -0.031692 | -66.7819 | 56.1528 | 56.3351 | 56.146 | -67.0744 | -0.072685 | -0.048514 | 0.04961 | 0.037139 | 0.10982 | -0.15322 | 0.030224 | -0.30042 | -0.15675 | 0.031181 | -0.007903 | 0.29251 | 0.025587 | -0.16351 | 123.035 | 122.9303 | 123.1137 | 66.7433 | -123.1562 | 122.9267 | 123.1091 | 122.92 | 66.7423 | -123.3839
1225.8594 | 123.2071 | -66.7282 | 56.3599 | 0.0046549 | -0.015051 | 0.0011025 | 0.053722 | -0.0050232 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058245 | 0.024532 | 0.058735 | -66.7244 | -0.030644 | -66.7277 | 56.261 | 56.1471 | 56.3352 | -66.8604 | -66.7382 | -0.040849 | -66.791 | 56.1711 | 56.3351 | 56.1643 | -67.0744 | -0.1322 | -0.098868 | 0.003833 | 0.000518 | 0.13272 | -0.21273 | -0.024708 | -0.34619 | -0.18879 | -0.010017 | -0.062837 | 0.28336 | -0.024767 | -0.19555 | 122.9892 | 122.8753 | 123.0634 | 66.6976 | -123.2203 | 122.8993 | 123.0633 | 122.8925 | 66.6874 | -123.4343
1226.7969 | 123.1842 | -66.7374 | 56.2729 | -0.0029761 | -0.014837 | 0.0013163 | 0.053936 | -0.0048096 | 0.062503 | 0.00015261 | -0.0021983 | -0.0011965 | 0.058245 | 0.024532 | 0.058522 | -66.7335 | -0.030644 | -66.7277 | 56.261 | 56.1563 | 56.3214 | -66.8513 | -66.7428 | -0.045428 | -66.7819 | 56.1619 | 56.3397 | 56.1552 | -67.0744 | -0.11389 | -0.011893 | 0.003832 | 0.009674 | 0.12356 | -0.1166 | 0.048531 | -0.33704 | -0.11097 | -0.00544 | -0.044524 | 0.29251 | 0.066787 | -0.11774 | 122.9984 | 122.8937 | 123.0588 | 66.7067 | -123.1241 | 122.8993 | 123.077 | 122.8925 | 66.6919 | -123.3473
1227.8594 | 123.1522 | -66.7648 | 56.3141 | 0.0046549 | -0.014837 | 0.00088894 | 0.053936 | -0.0050232 | 0.062076 | -0.015108 | -0.0017711 | -0.00098273 | 0.058245 | 0.024745 | 0.058522 | -66.7244 | -0.035222 | -66.7323 | 56.261 | 56.1609 | 56.326 | -66.8513 | -66.7428 | -0.045428 | -66.7865 | 56.1665 | 56.3397 | 56.1506 | -67.0744 | -0.086419 | -0.053092 | 0.040455 | 0.032562 | 0.11898 | -0.15322 | 0.01191 | -0.30957 | -0.14759 | 0.022026 | -0.021637 | 0.28794 | 0.025588 | -0.16351 | 123.0258 | 122.9257 | 123.0908 | 66.7296 | -123.1653 | 122.9313 | 123.1045 | 122.9154 | 66.7194 | -123.3885
1228.7969 | 123.2391 | -66.7007 | 56.3004 | 0.0046549 | -0.014837 | 0.00067514 | 0.054363 | -0.0048096 | 0.062076 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058672 | 0.024745 | 0.058522 | -66.7335 | -0.035222 | -66.7277 | 56.2564 | 56.1563 | 56.3306 | -66.8513 | -66.7474 | -0.040849 | -66.791 | 56.1573 | 56.3397 | 56.1552 | -67.0744 | -0.15051 | -0.043937 | -0.032789 | -0.026947 | 0.12356 | -0.14406 | 0.030222 | -0.37366 | -0.14301 | -0.04664 | -0.090302 | 0.28336 | 0.039321 | -0.1452 | 122.9572 | 122.857 | 123.0313 | 66.6655 | -123.1516 | 122.8581 | 123.0404 | 122.8559 | 66.6599 | -123.3748
1229.8594 | 123.1934 | -66.7145 | 56.3141 | -0.0029761 | -0.015265 | 0.0011025 | 0.053722 | -0.0052368 | 0.062076 | -0.0074779 | -0.0017711 | -0.00034193 | 0.058245 | 0.024318 | 0.058522 | -66.729 | -0.035222 | -66.7231 | 56.261 | 56.1654 | 56.3306 | -66.8513 | -66.7382 | -0.036271 | -66.7819 | 56.1665 | 56.3397 | 56.1735 | -67.0744 | -0.13677 | -0.053092 | -0.014478 | -0.008635 | 0.12814 | -0.14864 | 0.016489 | -0.35993 | -0.14759 | -0.023749 | -0.067412 | 0.29251 | 0.025588 | -0.14062 | 122.9755 | 122.8799 | 123.0451 | 66.6793 | -123.1653 | 122.881 | 123.0542 | 122.8879 | 66.6782 | -123.3885
1230.7969 | 123.2346 | -66.7328 | 56.2958 | -0.0029761 | -0.015051 | 0.00067514 | 0.053936 | -0.004596 | 0.062076 | -0.015108 | -0.0017711 | -0.00076913 | 0.058458 | 0.024959 | 0.058522 | -66.729 | -0.030644 | -66.7323 | 56.261 | 56.1563 | 56.3306 | -66.8558 | -66.7428 | -0.040849 | -66.791 | 56.1619 | 56.3397 | 56.1643 | -67.0698 | -0.12304 | -0.034781 | 0.003832 | 0.000518 | 0.12356 | -0.13949 | 0.0348 | -0.33704 | -0.13386 | -0.010018 | -0.058259 | 0.27878 | 0.043899 | -0.13146 | 122.9938 | 122.8891 | 123.0634 | 66.7021 | -123.1516 | 122.8947 | 123.0725 | 122.8971 | 66.6919 | -123.3656
1231.7969 | 123.2437 | -66.7374 | 56.25 | -0.0029761 | -0.015265 | 0.0011025 | 0.053936 | -0.0048096 | 0.062503 | 0.00015261 | -0.0017711 | -0.00076913 | 0.058031 | 0.024745 | 0.058735 | -66.7244 | -0.035222 | -66.7277 | 56.2564 | 56.1609 | 56.326 | -66.8604 | -66.7474 | -0.045428 | -66.7773 | 56.1665 | 56.3351 | 56.1735 | -67.0744 | -0.12304 | 0.006417 | 0.012989 | 0.009674 | 0.13272 | -0.089132 | 0.075997 | -0.33704 | -0.083504 | -0.010019 | -0.039945 | 0.29709 | 0.085096 | -0.076532 | 122.9938 | 122.8982 | 123.0634 | 66.7021 | -123.1104 | 122.9039 | 123.0725 | 122.9108 | 66.6919 | -123.3244
1232.7969 | 123.2758 | -66.7236 | 56.2729 | -0.010607 | -0.015265 | 0.00067514 | 0.053936 | -0.0050232 | 0.062503 | 0.00015261 | -0.0017711 | -0.00055553 | 0.058245 | 0.024532 | 0.058522 | -66.7244 | -0.035222 | -66.7368 | 56.2656 | 56.1563 | 56.3306 | -66.8604 | -66.7474 | -0.040849 | -66.7865 | 56.1619 | 56.3397 | 56.146 | -67.0744 | -0.13678 | -0.007314 | -0.000744 | -0.013215 | 0.12356 | -0.1166 | 0.057688 | -0.35077 | -0.11097 | -0.023752 | -0.062836 | 0.28794 | 0.066787 | -0.12689 | 122.9892 | 122.8799 | 123.0542 | 66.6884 | -123.1333 | 122.8856 | 123.0633 | 122.8696 | 66.6828 | -123.3473
1233.7969 | 123.23 | -66.7374 | 56.2866 | -0.010607 | -0.015265 | 0.00067514 | 0.054149 | -0.0050232 | 0.062503 | 0.00015261 | -0.0015573 | -0.00055553 | 0.058245 | 0.024745 | 0.058522 | -66.7244 | -0.030644 | -66.7414 | 56.261 | 56.1609 | 56.326 | -66.8604 | -66.7382 | -0.045428 | -66.7865 | 56.1619 | 56.3443 | 56.1597 | -67.0652 | -0.12304 | -0.025626 | 0.012989 | -0.004061 | 0.11898 | -0.12575 | 0.039376 | -0.32788 | -0.1247 | -0.000861 | -0.049103 | 0.27878 | 0.057632 | -0.12689 | 122.9984 | 122.8982 | 123.0634 | 66.7067 | -123.147 | 122.8993 | 123.0816 | 122.8971 | 66.6919 | -123.3519
1234.7969 | 123.2117 | -66.7145 | 56.3049 | -0.0029761 | -0.014837 | 0.00088894 | 0.053722 | -0.0050232 | 0.062289 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058031 | 0.024745 | 0.058522 | -66.7335 | -0.026065 | -66.7277 | 56.2564 | 56.1609 | 56.326 | -66.8558 | -66.7382 | -0.040849 | -66.791 | 56.1619 | 56.3351 | 56.1597 | -67.079 | -0.14135 | -0.048515 | -0.019056 | -0.013214 | 0.12814 | -0.14406 | 0.021065 | -0.3645 | -0.14301 | -0.023749 | -0.076569 | 0.28794 | 0.030164 | -0.1452 | 122.9709 | 122.8753 | 123.0405 | 66.6884 | -123.1608 | 122.8764 | 123.0496 | 122.8742 | 66.6736 | -123.3839
1235.7969 | 123.2666 | -66.7145 | 56.3049 | -0.010607 | -0.015478 | 0.00088894 | 0.054149 | -0.0050232 | 0.062289 | 0.00015261 | -0.0019847 | -0.00055553 | 0.058245 | 0.024745 | 0.058949 | -66.729 | -0.030644 | -66.7368 | 56.2564 | 56.1517 | 56.326 | -66.8558 | -66.7336 | -0.045428 | -66.7865 | 56.1573 | 56.3351 | 56.1552 | -67.079 | -0.14135 | -0.048515 | -0.014478 | -0.02237 | 0.11898 | -0.15322 | 0.021065 | -0.3645 | -0.14759 | -0.019171 | -0.071991 | 0.29251 | 0.030164 | -0.14978 | 122.9709 | 122.8662 | 123.0405 | 66.6838 | -123.1608 | 122.8718 | 123.0496 | 122.8696 | 66.669 | -123.3839
1236.8594 | 123.2574 | -66.7007 | 56.2683 | -0.010607 | -0.014837 | 0.00046154 | 0.054149 | -0.0050232 | 0.062503 | 0.00015261 | -0.0015573 | -0.00098273 | 0.058245 | 0.025173 | 0.058094 | -66.729 | -0.035222 | -66.746 | 56.2564 | 56.1563 | 56.3352 | -66.8558 | -66.7474 | -0.031692 | -66.7819 | 56.1665 | 56.3351 | 56.1597 | -67.0744 | -0.15508 | -0.011894 | -0.028211 | -0.04526 | 0.10983 | -0.11202 | 0.066844 | -0.37366 | -0.10181 | -0.04664 | -0.081145 | 0.29251 | 0.066785 | -0.10858 | 122.9572 | 122.857 | 123.0359 | 66.6655 | -123.1241 | 122.8672 | 123.0358 | 122.8605 | 66.6691 | -123.3427
1237.7969 | 123.2666 | -66.7282 | 56.2729 | -0.010607 | -0.015478 | 0.0011025 | 0.053722 | -0.0054506 | 0.06293 | 0.015414 | -0.0017711 | -0.00098273 | 0.058458 | 0.024959 | 0.058735 | -66.729 | -0.035222 | -66.7368 | 56.261 | 56.1609 | 56.3352 | -66.8467 | -66.7474 | -0.031692 | -66.7865 | 56.1619 | 56.3305 | 56.1506 | -67.0744 | -0.11846 | -0.011893 | -0.000746 | -0.008638 | 0.10982 | -0.11202 | 0.062267 | -0.34619 | -0.11097 | -0.019175 | -0.058259 | 0.28794 | 0.057629 | -0.12231 | 122.9892 | 122.8891 | 123.0634 | 66.693 | -123.1196 | 122.8901 | 123.0587 | 122.8788 | 66.6965 | -123.3473
1238.875 | 123.143 | -66.7419 | 56.3782 | 0.0046549 | -0.015692 | 0.0011025 | 0.053722 | -0.0048096 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058245 | 0.024745 | 0.058522 | -66.7335 | -0.030644 | -66.746 | 56.261 | 56.1609 | 56.3352 | -66.8558 | -66.752 | -0.036271 | -66.7865 | 56.1573 | 56.3351 | 56.1735 | -67.0652 | -0.11389 | -0.11718 | 0.008409 | -0.004062 | 0.10983 | -0.21731 | -0.043019 | -0.3233 | -0.22084 | -0.01002 | -0.044526 | 0.27878 | -0.043078 | -0.20471 | 123.0029 | 122.9028 | 123.0771 | 66.7113 | -123.234 | 122.8993 | 123.077 | 122.9154 | 66.7057 | -123.4434
1239.7969 | 123.1522 | -66.7648 | 56.3416 | 0.012286 | -0.015478 | 0.00088894 | 0.053936 | -0.0050232 | 0.062503 | 0.023044 | -0.0017711 | -0.00098273 | 0.058458 | 0.024532 | 0.058522 | -66.7244 | -0.030644 | -66.7414 | 56.2564 | 56.17 | 56.3214 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1665 | 56.3351 | 56.1552 | -67.0744 | -0.090998 | -0.085136 | 0.040455 | 0.023405 | 0.1144 | -0.17153 | -0.020134 | -0.30957 | -0.17506 | 0.017447 | -0.021637 | 0.28794 | -0.006457 | -0.1864 | 123.0212 | 122.9349 | 123.0863 | 66.7342 | -123.1974 | 122.9313 | 123.0999 | 122.92 | 66.724 | -123.416
1240.7969 | 123.2941 | -66.7053 | 56.2866 | 0.019917 | -0.015265 | 0.0011025 | 0.053722 | -0.004596 | 0.062289 | 0.015414 | -0.0015573 | -0.00076913 | 0.058245 | 0.024959 | 0.058735 | -66.729 | -0.030644 | -66.746 | 56.2518 | 56.1471 | 56.3306 | -66.8513 | -66.7428 | -0.045428 | -66.7865 | 56.1619 | 56.3443 | 56.1552 | -67.079 | -0.14593 | -0.034782 | -0.023634 | -0.040683 | 0.10525 | -0.13949 | 0.043955 | -0.37366 | -0.1247 | -0.037484 | -0.081147 | 0.29251 | 0.057632 | -0.13147 | 122.9572 | 122.8525 | 123.0359 | 66.6747 | -123.1379 | 122.8672 | 123.0496 | 122.8605 | 66.6599 | -123.3656
1241.7969 | 123.2483 | -66.7099 | 56.2775 | -0.010607 | -0.015265 | 0.0011025 | 0.053936 | -0.0052368 | 0.062503 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058031 | 0.024745 | 0.058308 | -66.7244 | -0.035222 | -66.7414 | 56.2564 | 56.1609 | 56.3352 | -66.8513 | -66.7474 | -0.045428 | -66.791 | 56.1619 | 56.3351 | 56.1506 | -67.0744 | -0.14135 | -0.021049 | -0.014477 | -0.031527 | 0.10982 | -0.1166 | 0.057689 | -0.3645 | -0.11555 | -0.037485 | -0.081147 | 0.28336 | 0.05763 | -0.12689 | 122.9663 | 122.8708 | 123.0451 | 66.6747 | -123.1287 | 122.8718 | 123.045 | 122.8605 | 66.6645 | -123.3519
1242.8594 | 123.1888 | -66.7374 | 56.3095 | -0.010607 | -0.015692 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0024119 | -0.00055553 | 0.058245 | 0.024745 | 0.058308 | -66.7244 | -0.030644 | -66.7414 | 56.2656 | 56.17 | 56.326 | -66.8558 | -66.7428 | -0.050007 | -66.7819 | 56.1665 | 56.3397 | 56.178 | -67.0698 | -0.11846 | -0.043935 | 0.012989 | -0.004061 | 0.1144 | -0.13948 | 0.016488 | -0.33246 | -0.14301 | -0.00544 | -0.044524 | 0.28794 | 0.030166 | -0.13146 | 123.0029 | 122.9074 | 123.0634 | 66.7067 | -123.1653 | 122.9039 | 123.077 | 122.9154 | 66.6874 | -123.3793
1243.7969 | 123.2071 | -66.6962 | 56.3278 | 0.0046549 | -0.015265 | 0.00088894 | 0.054149 | -0.0050232 | 0.062289 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058245 | 0.024745 | 0.058094 | -66.7244 | -0.035222 | -66.7414 | 56.2564 | 56.1654 | 56.3306 | -66.8604 | -66.7474 | -0.040849 | -66.7865 | 56.1619 | 56.3443 | 56.1643 | -67.0698 | -0.16424 | -0.071403 | -0.02821 | -0.04526 | 0.11898 | -0.16237 | 0.002756 | -0.37366 | -0.1659 | -0.051218 | -0.090302 | 0.28336 | 0.016433 | -0.16351 | 122.9526 | 122.8616 | 123.0267 | 66.6609 | -123.1882 | 122.8581 | 123.0404 | 122.8605 | 66.6553 | -123.3976
1244.8594 | 123.1888 | -66.7053 | 56.3416 | 0.0046549 | -0.015692 | 0.0013163 | 0.053936 | -0.0052368 | 0.062289 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058458 | 0.024745 | 0.058308 | -66.729 | -0.039801 | -66.7414 | 56.261 | 56.1654 | 56.3306 | -66.8467 | -66.752 | -0.036271 | -66.7819 | 56.1619 | 56.3351 | 56.178 | -67.0744 | -0.14135 | -0.080558 | -0.023634 | -0.036105 | 0.10524 | -0.17611 | -0.010977 | -0.36908 | -0.17964 | -0.046641 | -0.076568 | 0.29251 | -0.006457 | -0.16351 | 122.9663 | 122.8708 | 123.0359 | 66.6655 | -123.1882 | 122.8672 | 123.0404 | 122.8834 | 66.6691 | -123.416
1245.7969 | 123.2162 | -66.7465 | 56.3004 | -0.010607 | -0.015478 | 0.00088894 | 0.054149 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058458 | 0.024745 | 0.058522 | -66.729 | -0.030644 | -66.7368 | 56.261 | 56.1654 | 56.3306 | -66.8513 | -66.7428 | -0.045428 | -66.7819 | 56.1665 | 56.3305 | 56.1597 | -67.0744 | -0.10473 | -0.039359 | 0.017565 | 0.009673 | 0.1144 | -0.13491 | 0.030222 | -0.32788 | -0.13386 | 0.003715 | -0.035369 | 0.29251 | 0.030163 | -0.14062 | 123.0075 | 122.912 | 123.0771 | 66.7159 | -123.1516 | 122.913 | 123.077 | 122.9063 | 66.7011 | -123.3748
1246.8594 | 123.2391 | -66.7236 | 56.2912 | -0.0029761 | -0.015692 | 0.0011025 | 0.053936 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.00055553 | 0.058031 | 0.024318 | 0.058522 | -66.7335 | -0.044379 | -66.7414 | 56.2518 | 56.17 | 56.3306 | -66.8558 | -66.7474 | -0.040849 | -66.7819 | 56.1665 | 56.3305 | 56.1643 | -67.0744 | -0.1322 | -0.03936 | -0.009901 | -0.017794 | 0.1144 | -0.12117 | 0.039377 | -0.35077 | -0.1247 | -0.023752 | -0.058257 | 0.29251 | 0.039318 | -0.12689 | 122.9755 | 122.8937 | 123.0542 | 66.6793 | -123.147 | 122.8901 | 123.0542 | 122.8879 | 66.6828 | -123.3656
1247.7969 | 123.2346 | -66.7236 | 56.3049 | 0.0046549 | -0.015478 | 0.00088894 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0017711 | -0.00098273 | 0.058245 | 0.024959 | 0.058094 | -66.729 | -0.039801 | -66.7414 | 56.2564 | 56.1563 | 56.3352 | -66.8513 | -66.7382 | -0.036271 | -66.791 | 56.1619 | 56.3397 | 56.1643 | -67.0698 | -0.12762 | -0.048515 | -0.005323 | -0.017794 | 0.10982 | -0.14864 | 0.030223 | -0.34619 | -0.14301 | -0.014594 | -0.067414 | 0.27878 | 0.034743 | -0.14062 | 122.9801 | 122.8799 | 123.0588 | 66.6838 | -123.1562 | 122.8856 | 123.0633 | 122.8879 | 66.6874 | -123.3748
1248.7969 | 123.1247 | -66.7465 | 56.3644 | 0.0046549 | -0.015478 | 0.00067514 | 0.053722 | -0.0048096 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058245 | 0.024745 | 0.058308 | -66.7335 | -0.039801 | -66.7368 | 56.2564 | 56.1609 | 56.3352 | -66.8558 | -66.7428 | -0.040849 | -66.7865 | 56.1619 | 56.3305 | 56.1872 | -67.079 | -0.10931 | -0.10802 | 0.012987 | 0.009673 | 0.11898 | -0.20357 | -0.029286 | -0.33246 | -0.20252 | 0.003715 | -0.039948 | 0.29251 | -0.033924 | -0.17724 | 123.0029 | 122.9074 | 123.0817 | 66.7067 | -123.2203 | 122.9084 | 123.077 | 122.9337 | 66.7057 | -123.4434
1249.8594 | 123.2574 | -66.7053 | 56.3049 | 0.0046549 | -0.015478 | 0.0011025 | 0.054149 | -0.0048096 | 0.062717 | 0.015414 | -0.0021983 | -0.00098273 | 0.058458 | 0.025173 | 0.058735 | -66.7198 | -0.035222 | -66.7368 | 56.2564 | 56.1609 | 56.3306 | -66.8513 | -66.7382 | -0.040849 | -66.7865 | 56.1665 | 56.3397 | 56.1643 | -67.079 | -0.14593 | -0.048515 | -0.014477 | -0.031526 | 0.1144 | -0.14406 | 0.025644 | -0.37366 | -0.13844 | -0.032905 | -0.081147 | 0.29251 | 0.034743 | -0.14062 | 122.9617 | 122.8662 | 123.0359 | 66.6701 | -123.1562 | 122.8718 | 123.045 | 122.8696 | 66.6645 | -123.3839
1250.7969 | 123.1567 | -66.7328 | 56.3416 | 0.0046549 | -0.015478 | 0.0011025 | 0.053936 | -0.0054506 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058458 | 0.024959 | 0.058522 | -66.7381 | -0.030644 | -66.7414 | 56.2564 | 56.17 | 56.326 | -66.8558 | -66.7474 | -0.036271 | -66.7773 | 56.1665 | 56.3397 | 56.1597 | -67.0698 | -0.12304 | -0.085136 | -0.005324 | -0.008639 | 0.1144 | -0.17153 | -0.015556 | -0.33704 | -0.17506 | -0.014597 | -0.044523 | 0.29252 | -0.001878 | -0.18182 | 122.9892 | 122.9028 | 123.0588 | 66.7021 | -123.1974 | 122.8993 | 123.0725 | 122.8925 | 66.6965 | -123.4114
1251.8594 | 123.1293 | -66.7603 | 56.2866 | -0.010607 | -0.015692 | 0.00088894 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058245 | 0.025173 | 0.058522 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.1609 | 56.3306 | -66.8558 | -66.7382 | -0.040849 | -66.7819 | 56.1619 | 56.3259 | 56.1643 | -67.079 | -0.095576 | -0.025626 | 0.031298 | 0.018827 | 0.1144 | -0.12575 | 0.043955 | -0.31873 | -0.1247 | 0.022027 | -0.021636 | 0.29709 | 0.039318 | -0.12231 | 123.0212 | 122.9211 | 123.0908 | 66.7296 | -123.1425 | 122.9222 | 123.0862 | 122.9246 | 66.7194 | -123.3656
1252.7969 | 123.2117 | -66.7191 | 56.3324 | 0.012286 | -0.015265 | 0.00088894 | 0.053722 | -0.0054506 | 0.06293 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058245 | 0.024959 | 0.058308 | -66.7335 | -0.039801 | -66.7414 | 56.2656 | 56.1609 | 56.326 | -66.8421 | -66.7428 | -0.040849 | -66.7819 | 56.1711 | 56.3351 | 56.1689 | -67.0698 | -0.12304 | -0.066823 | -0.014479 | -0.022372 | 0.10067 | -0.17153 | -0.0064 | -0.35077 | -0.16132 | -0.023751 | -0.062835 | 0.28794 | 0.002699 | -0.16351 | 122.9846 | 122.8799 | 123.0451 | 66.6793 | -123.1745 | 122.8901 | 123.0542 | 122.8879 | 66.6782 | -123.4022
1253.8594 | 123.23 | -66.7099 | 56.2866 | -0.0029761 | -0.015692 | 0.00088894 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058672 | 0.024959 | 0.058735 | -66.7335 | -0.039801 | -66.7368 | 56.2564 | 56.1563 | 56.3306 | -66.8513 | -66.7382 | -0.036271 | -66.7865 | 56.1619 | 56.3351 | 56.178 | -67.079 | -0.14135 | -0.030204 | -0.023634 | -0.026948 | 0.1144 | -0.13033 | 0.043955 | -0.36908 | -0.1247 | -0.028327 | -0.076569 | 0.29251 | 0.048475 | -0.10857 | 122.9663 | 122.8662 | 123.0405 | 66.6701 | -123.1379 | 122.8718 | 123.045 | 122.8879 | 66.6736 | -123.3656
1254.7969 | 123.1293 | -66.7557 | 56.337 | -0.0029761 | -0.015051 | 0.00046154 | 0.053936 | -0.0056642 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058245 | 0.025173 | 0.058522 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1609 | 56.3306 | -66.8558 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.3397 | 56.1735 | -67.0881 | -0.10015 | -0.07598 | 0.031299 | 0.009671 | 0.10983 | -0.17611 | -0.006399 | -0.33246 | -0.1659 | 0.008291 | -0.030793 | 0.30167 | 0.0027 | -0.16351 | 123.0167 | 122.9165 | 123.0863 | 66.7205 | -123.1928 | 122.9267 | 123.0954 | 122.9291 | 66.7194 | -123.4251
1255.7969 | 123.2941 | -66.7053 | 56.2912 | -0.0029761 | -0.015478 | 0.00067514 | 0.054149 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00055553 | 0.058245 | 0.025173 | 0.058522 | -66.729 | -0.026065 | -66.746 | 56.2656 | 56.1746 | 56.3352 | -66.8513 | -66.7474 | -0.036271 | -66.7865 | 56.1665 | 56.3351 | 56.1597 | -67.079 | -0.14593 | -0.025625 | -0.023634 | -0.040683 | 0.10525 | -0.11659 | 0.043956 | -0.37366 | -0.1247 | -0.042063 | -0.081147 | 0.29251 | 0.043897 | -0.13147 | 122.9709 | 122.8799 | 123.0405 | 66.6793 | -123.1424 | 122.8718 | 123.0404 | 122.8651 | 66.6691 | -123.3702
1256.8594 | 123.262 | -66.7053 | 56.2775 | -0.0029761 | -0.015478 | 0.0011025 | 0.053722 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058458 | 0.025173 | 0.058522 | -66.729 | -0.030644 | -66.7414 | 56.2564 | 56.17 | 56.326 | -66.8467 | -66.7382 | -0.036271 | -66.7819 | 56.1619 | 56.3397 | 56.1689 | -67.079 | -0.14135 | -0.021049 | -0.023634 | -0.036105 | 0.10524 | -0.10744 | 0.048531 | -0.37366 | -0.11555 | -0.032905 | -0.076568 | 0.29709 | 0.062209 | -0.10858 | 122.9617 | 122.8753 | 123.0313 | 66.6747 | -123.1241 | 122.8672 | 123.045 | 122.8742 | 66.6691 | -123.3564
1257.7969 | 123.2712 | -66.7007 | 56.2912 | 0.0046549 | -0.015692 | 0.0011025 | 0.053722 | -0.0052368 | 0.062717 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058245 | 0.024959 | 0.058522 | -66.729 | -0.035222 | -66.746 | 56.261 | 56.1563 | 56.3352 | -66.8513 | -66.752 | -0.045428 | -66.7865 | 56.1665 | 56.3397 | 56.1643 | -67.0698 | -0.15051 | -0.030204 | -0.028211 | -0.04526 | 0.10525 | -0.13491 | 0.043956 | -0.36908 | -0.1247 | -0.051218 | -0.085724 | 0.28336 | 0.048476 | -0.12689 | 122.9617 | 122.857 | 123.0359 | 66.6655 | -123.1424 | 122.8672 | 123.0404 | 122.8651 | 66.6553 | -123.361
1258.7969 | 123.2071 | -66.7191 | 56.3461 | -0.010607 | -0.015692 | 0.00088894 | 0.053936 | -0.0050232 | 0.062717 | 0.015414 | -0.0021983 | -0.00076913 | 0.058245 | 0.024959 | 0.058735 | -66.7335 | -0.035222 | -66.746 | 56.2656 | 56.1609 | 56.3397 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1711 | 56.3443 | 56.1689 | -67.0744 | -0.13678 | -0.080556 | -0.014479 | -0.02695 | 0.10983 | -0.18526 | -0.006397 | -0.35535 | -0.17506 | -0.02833 | -0.067414 | 0.28794 | -0.001877 | -0.17724 | 122.9846 | 122.8799 | 123.0588 | 66.6838 | -123.202 | 122.8901 | 123.0633 | 122.8879 | 66.6782 | -123.4205
1259.8594 | 123.2574 | -66.6641 | 56.3141 | 0.0046549 | -0.015478 | 0.00067514 | 0.054149 | -0.0050232 | 0.062717 | 0.015414 | -0.0021983 | -0.00098273 | 0.058245 | 0.025173 | 0.058522 | -66.729 | -0.035222 | -66.7414 | 56.2564 | 56.1563 | 56.3306 | -66.8558 | -66.7428 | -0.036271 | -66.791 | 56.1619 | 56.3305 | 56.1826 | -67.0744 | -0.19171 | -0.05767 | -0.064832 | -0.077303 | 0.1144 | -0.1578 | 0.016489 | -0.41028 | -0.15217 | -0.078682 | -0.12692 | 0.28336 | 0.01643 | -0.13146 | 122.9205 | 122.8204 | 122.9947 | 66.6289 | -123.1699 | 122.826 | 122.9946 | 122.8467 | 66.6279 | -123.3885
1260.7969 | 123.1567 | -66.7511 | 56.3187 | -0.010607 | -0.015478 | 0.00067514 | 0.053508 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058245 | 0.025173 | 0.058522 | -66.7335 | -0.030644 | -66.7414 | 56.2702 | 56.1654 | 56.326 | -66.8604 | -66.7428 | -0.036271 | -66.7865 | 56.1665 | 56.3305 | 56.1643 | -67.0744 | -0.10931 | -0.048513 | 0.017565 | 0.009672 | 0.11898 | -0.15322 | 0.007332 | -0.32331 | -0.15217 | 0.008293 | -0.03537 | 0.28794 | 0.011852 | -0.15435 | 123.0213 | 122.9165 | 123.0771 | 66.7205 | -123.1791 | 122.9176 | 123.0816 | 122.9154 | 66.7148 | -123.3931
1261.7969 | 123.2117 | -66.7236 | 56.3324 | 0.0046549 | -0.015478 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | 0.015414 | -0.0019847 | -0.00098273 | 0.058031 | 0.025386 | 0.058735 | -66.7335 | -0.026065 | -66.7506 | 56.2564 | 56.1563 | 56.3306 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1711 | 56.3397 | 56.1689 | -67.0836 | -0.1322 | -0.07598 | -0.009901 | -0.02695 | 0.10525 | -0.17611 | -0.001821 | -0.35993 | -0.16132 | -0.023752 | -0.062836 | 0.29709 | 0.007278 | -0.16351 | 122.9801 | 122.8799 | 123.0542 | 66.6976 | -123.1882 | 122.8947 | 123.0633 | 122.8925 | 66.6828 | -123.416
1262.7969 | 123.143 | -66.7648 | 56.3278 | -0.0029761 | -0.015692 | 0.0011025 | 0.053295 | -0.0052368 | 0.06293 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058245 | 0.025173 | 0.058094 | -66.7198 | -0.035222 | -66.7552 | 56.2564 | 56.17 | 56.3352 | -66.8558 | -66.7428 | -0.036271 | -66.791 | 56.1619 | 56.3351 | 56.1689 | -67.079 | -0.090998 | -0.071403 | 0.045033 | 0.009671 | 0.10067 | -0.15779 | 0.007335 | -0.31415 | -0.1659 | 0.022026 | -0.026215 | 0.28794 | 0.007276 | -0.15893 | 123.0212 | 122.9349 | 123.1 | 66.7296 | -123.1837 | 122.9267 | 123.0999 | 122.9337 | 66.7286 | -123.4068
1263.7969 | 123.1247 | -66.7511 | 56.3049 | 0.0046549 | -0.015478 | 0.00067514 | 0.053508 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058245 | 0.025173 | 0.058308 | -66.7198 | -0.030644 | -66.746 | 56.2656 | 56.1746 | 56.3397 | -66.8558 | -66.7474 | -0.040849 | -66.7956 | 56.1619 | 56.3397 | 56.1643 | -67.0744 | -0.10473 | -0.039358 | 0.0313 | 0.005094 | 0.10983 | -0.13033 | 0.034801 | -0.32331 | -0.14301 | 0.003714 | -0.044527 | 0.27878 | 0.034743 | -0.14062 | 123.0167 | 122.9257 | 123.0908 | 66.7205 | -123.1608 | 122.913 | 123.0908 | 122.9154 | 66.7103 | -123.3793
1264.8594 | 123.1979 | -66.7374 | 56.3187 | -0.0029761 | -0.015906 | 0.0013163 | 0.053722 | -0.0056642 | 0.062717 | 0.00015261 | -0.0021983 | -0.00055553 | 0.058031 | 0.025173 | 0.058308 | -66.7244 | -0.030644 | -66.7506 | 56.2702 | 56.1746 | 56.3397 | -66.8558 | -66.7474 | -0.045428 | -66.7865 | 56.1619 | 56.3351 | 56.178 | -67.0698 | -0.11846 | -0.048513 | 0.012989 | -0.013217 | 0.10525 | -0.14406 | 0.021068 | -0.33246 | -0.15675 | -0.010019 | -0.049103 | 0.28336 | 0.016431 | -0.14062 | 123.0075 | 122.912 | 123.0771 | 66.7067 | -123.1745 | 122.8993 | 123.0725 | 122.9154 | 66.6919 | -123.3885
1265.7969 | 123.1384 | -66.7648 | 56.3278 | -0.0029761 | -0.015692 | 0.00088894 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058031 | 0.025173 | 0.058522 | -66.7335 | -0.030644 | -66.746 | 56.2564 | 56.1792 | 56.3443 | -66.8513 | -66.7428 | -0.031692 | -66.7819 | 56.1619 | 56.3351 | 56.1597 | -67.079 | -0.086419 | -0.071403 | 0.031298 | 0.018827 | 0.10525 | -0.14864 | 0.016492 | -0.31415 | -0.1659 | 0.022026 | -0.017058 | 0.29709 | 0.007276 | -0.16809 | 123.0212 | 122.944 | 123.1091 | 66.7342 | -123.1791 | 122.9267 | 123.0999 | 122.9246 | 66.7331 | -123.4068
1266.7969 | 123.175 | -66.7603 | 56.3278 | -0.0029761 | -0.015692 | 0.0011025 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058031 | 0.024959 | 0.058735 | -66.729 | -0.026065 | -66.7414 | 56.261 | 56.1746 | 56.3352 | -66.8558 | -66.7474 | -0.036271 | -66.7865 | 56.1573 | 56.3397 | 56.178 | -67.0744 | -0.095576 | -0.066825 | 0.031298 | 0.018827 | 0.1144 | -0.15322 | 0.007335 | -0.31415 | -0.17048 | 0.012869 | -0.026215 | 0.28794 | 0.011855 | -0.14977 | 123.0212 | 122.9349 | 123.0954 | 66.7342 | -123.1837 | 122.9176 | 123.0999 | 122.9383 | 66.724 | -123.4022
1267.7969 | 123.1705 | -66.7236 | 56.3416 | -0.010607 | -0.015478 | 0.0013163 | 0.053508 | -0.0048096 | 0.062503 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058031 | 0.025386 | 0.058949 | -66.7335 | -0.026065 | -66.7414 | 56.2564 | 56.1746 | 56.3397 | -66.8604 | -66.752 | -0.040849 | -66.7865 | 56.1711 | 56.3397 | 56.178 | -67.079 | -0.13678 | -0.085136 | -0.009901 | -0.017794 | 0.11898 | -0.16695 | -0.00182 | -0.35535 | -0.17048 | -0.02833 | -0.062836 | 0.29251 | -0.001878 | -0.16351 | 122.9801 | 122.8982 | 123.0634 | 66.6976 | -123.202 | 122.8947 | 123.0633 | 122.9017 | 66.6828 | -123.4205
1268.8594 | 123.1247 | -66.7282 | 56.3232 | 0.0046549 | -0.015692 | 0.00067514 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0024119 | -0.0011965 | 0.058245 | 0.025173 | 0.058308 | -66.729 | -0.035222 | -66.7414 | 56.2656 | 56.17 | 56.3352 | -66.8513 | -66.7382 | -0.040849 | -66.791 | 56.1711 | 56.3397 | 56.1643 | -67.079 | -0.12304 | -0.057668 | -0.000746 | -0.013217 | 0.10982 | -0.15322 | 0.011913 | -0.35077 | -0.15217 | -0.010017 | -0.062837 | 0.28794 | 0.016433 | -0.15893 | 122.9938 | 122.8982 | 123.0634 | 66.693 | -123.1745 | 122.8993 | 123.0679 | 122.8925 | 66.6874 | -123.4022
1269.7969 | 123.1613 | -66.7191 | 56.3232 | 0.0046549 | -0.015692 | 0.00088894 | 0.053936 | -0.0056642 | 0.062717 | 0.0077831 | -0.0017711 | -0.00076913 | 0.058458 | 0.025386 | 0.058308 | -66.7244 | -0.035222 | -66.7506 | 56.2564 | 56.1838 | 56.3352 | -66.8467 | -66.752 | -0.040849 | -66.7865 | 56.1665 | 56.3305 | 56.1689 | -67.0698 | -0.12762 | -0.066825 | -0.005322 | -0.031528 | 0.096089 | -0.13948 | 0.011913 | -0.35077 | -0.15675 | -0.032908 | -0.067414 | 0.28336 | 0.007275 | -0.15435 | 122.9755 | 122.9028 | 123.0542 | 66.6838 | -123.1699 | 122.8856 | 123.0496 | 122.8879 | 66.6782 | -123.3931
1270.7969 | 123.262 | -66.7053 | 56.25 | -0.0029761 | -0.015692 | 0.0011025 | 0.053936 | -0.0052368 | 0.06293 | 0.00015261 | -0.0019847 | -0.0011965 | 0.058458 | 0.025173 | 0.058735 | -66.7244 | -0.030644 | -66.7506 | 56.2656 | 56.17 | 56.3352 | -66.8558 | -66.752 | -0.045428 | -66.791 | 56.1619 | 56.3351 | 56.1506 | -67.0836 | -0.15051 | 0.015574 | -0.019055 | -0.045261 | 0.10525 | -0.079974 | 0.085155 | -0.37824 | -0.088083 | -0.046641 | -0.085725 | 0.29251 | 0.085096 | -0.099425 | 122.9709 | 122.8753 | 123.0405 | 66.6747 | -123.1058 | 122.8672 | 123.0404 | 122.8559 | 66.6599 | -123.3336
1271.7969 | 123.1888 | -66.7328 | 56.3187 | 0.012286 | -0.015478 | 0.00067514 | 0.053936 | -0.0056642 | 0.062503 | -0.0074779 | -0.0021983 | -0.00076913 | 0.058245 | 0.025173 | 0.058308 | -66.7381 | -0.026065 | -66.7552 | 56.261 | 56.1654 | 56.3352 | -66.8513 | -66.7428 | -0.045428 | -66.7865 | 56.1711 | 56.3351 | 56.1552 | -67.0744 | -0.11846 | -0.05767 | -0.005324 | -0.022373 | 0.09609 | -0.15322 | 0.01649 | -0.34162 | -0.14759 | -0.010018 | -0.053681 | 0.28794 | 0.016431 | -0.16351 | 122.9938 | 122.8982 | 123.0679 | 66.7067 | -123.1699 | 122.9039 | 123.0679 | 122.8879 | 66.6874 | -123.3931
1272.7969 | 123.143 | -66.7694 | 56.3095 | 0.0046549 | -0.016119 | 0.00088894 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.058245 | 0.025386 | 0.058735 | -66.729 | -0.030644 | -66.7552 | 56.261 | 56.17 | 56.3306 | -66.8558 | -66.7428 | -0.040849 | -66.791 | 56.1619 | 56.3397 | 56.1597 | -67.079 | -0.086421 | -0.048514 | 0.040453 | 0.014248 | 0.10067 | -0.13948 | 0.021067 | -0.30957 | -0.14759 | 0.026603 | -0.021638 | 0.28794 | 0.030166 | -0.14978 | 123.0304 | 122.9394 | 123.1 | 66.7388 | -123.1653 | 122.9313 | 123.1091 | 122.9291 | 66.7286 | -123.3885
1273.8594 | 123.1796 | -66.7557 | 56.3416 | -0.010607 | -0.015692 | 0.00088894 | 0.053508 | -0.0050232 | 0.062717 | 0.00015261 | -0.0019847 | -0.00098273 | 0.057817 | 0.025173 | 0.058522 | -66.7244 | -0.030644 | -66.7368 | 56.2656 | 56.1654 | 56.3397 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1665 | 56.3305 | 56.1689 | -67.079 | -0.10473 | -0.075979 | 0.031299 | 0.018828 | 0.12356 | -0.17611 | -0.00182 | -0.32331 | -0.17506 | 0.008291 | -0.030793 | 0.29251 | -0.011036 | -0.17266 | 123.0212 | 122.9211 | 123.0954 | 66.725 | -123.202 | 122.9222 | 123.0862 | 122.9246 | 66.7194 | -123.4205
1274.7969 | 123.1247 | -66.7648 | 56.3095 | -0.0029761 | -0.016119 | 0.0011025 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0021983 | -0.0011965 | 0.057817 | 0.025173 | 0.058522 | -66.7335 | -0.030644 | -66.7506 | 56.261 | 56.1746 | 56.3306 | -66.8513 | -66.7474 | -0.040849 | -66.7773 | 56.1619 | 56.3351 | 56.1735 | -67.079 | -0.086419 | -0.048514 | 0.031298 | 0.014249 | 0.10067 | -0.1349 | 0.021067 | -0.31415 | -0.14759 | 0.017447 | -0.012479 | 0.30167 | 0.025587 | -0.13604 | 123.0258 | 122.9394 | 123.0954 | 66.7342 | -123.1608 | 122.9267 | 123.0999 | 122.9383 | 66.724 | -123.3885
1275.7969 | 123.1934 | -66.7236 | 56.2729 | 0.0046549 | -0.016119 | 0.0011025 | 0.053936 | -0.0050232 | 0.062289 | -0.0074779 | -0.0019847 | -0.00076913 | 0.057817 | 0.025386 | 0.058522 | -66.729 | -0.026065 | -66.7506 | 56.261 | 56.1563 | 56.3352 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1711 | 56.3397 | 56.1689 | -67.079 | -0.1322 | -0.011893 | -0.005323 | -0.02695 | 0.10525 | -0.1166 | 0.062267 | -0.35535 | -0.10181 | -0.023752 | -0.062836 | 0.29251 | 0.066787 | -0.104 | 122.9846 | 122.8799 | 123.0588 | 66.6976 | -123.1287 | 122.8947 | 123.0633 | 122.8925 | 66.6828 | -123.3519
1276.7969 | 123.2849 | -66.7007 | 56.2592 | 0.0046549 | -0.015692 | 0.00088894 | 0.053936 | -0.0048096 | 0.06293 | 0.00015261 | -0.0024119 | -0.00034193 | 0.058031 | 0.025814 | 0.058735 | -66.729 | -0.035222 | -66.7414 | 56.261 | 56.1563 | 56.3306 | -66.8558 | -66.7474 | -0.031692 | -66.7819 | 56.1711 | 56.3397 | 56.1735 | -67.079 | -0.15508 | 0.00184 | -0.028211 | -0.040682 | 0.1144 | -0.10287 | 0.071421 | -0.37824 | -0.088081 | -0.04664 | -0.081145 | 0.29709 | 0.08052 | -0.085687 | 122.9617 | 122.857 | 123.0313 | 66.6655 | -123.115 | 122.8718 | 123.0404 | 122.8742 | 66.6691 | -123.3381
1277.8594 | 123.1888 | -66.6962 | 56.337 | -0.0029761 | -0.015692 | 0.00067514 | 0.053722 | -0.0054506 | 0.063144 | 0.015414 | -0.0019847 | -0.00055553 | 0.058245 | 0.0256 | 0.058522 | -66.7335 | -0.035222 | -66.746 | 56.261 | 56.1654 | 56.3443 | -66.8604 | -66.7382 | -0.036271 | -66.791 | 56.1665 | 56.3443 | 56.1552 | -67.0744 | -0.16424 | -0.07598 | -0.037367 | -0.049838 | 0.1144 | -0.17153 | 0.007337 | -0.37824 | -0.17048 | -0.04206 | -0.09488 | 0.28336 | 0.007278 | -0.18182 | 122.9572 | 122.8616 | 123.0405 | 66.6609 | -123.1974 | 122.8627 | 123.0404 | 122.8513 | 66.6599 | -123.4114
1278.7969 | 123.2666 | -66.7099 | 56.2637 | 0.0046549 | -0.015692 | 0.00067514 | 0.054149 | -0.0054506 | 0.06293 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058245 | 0.024959 | 0.058522 | -66.729 | -0.026065 | -66.7506 | 56.261 | 56.1609 | 56.3443 | -66.8558 | -66.7474 | -0.050007 | -66.7819 | 56.1665 | 56.3397 | 56.1735 | -67.0744 | -0.14593 | -0.002738 | -0.019056 | -0.040683 | 0.10525 | -0.10287 | 0.080579 | -0.3645 | -0.097237 | -0.037485 | -0.07199 | 0.29251 | 0.075942 | -0.090265 | 122.9709 | 122.8708 | 123.0542 | 66.6838 | -123.1196 | 122.8764 | 123.0496 | 122.8834 | 66.6599 | -123.3381
1279.8594 | 123.2208 | -66.7282 | 56.3324 | -0.0029761 | -0.015906 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | -0.0074779 | -0.0024119 | -0.0011965 | 0.058031 | 0.025173 | 0.058735 | -66.7198 | -0.035222 | -66.746 | 56.2656 | 56.17 | 56.3397 | -66.8604 | -66.752 | -0.031692 | -66.7865 | 56.1619 | 56.3397 | 56.1735 | -67.0744 | -0.1322 | -0.066823 | 0.008411 | -0.017795 | 0.1144 | -0.16237 | 0.007336 | -0.34619 | -0.17048 | -0.023753 | -0.058259 | 0.28794 | 0.007278 | -0.15893 | 122.9938 | 122.8982 | 123.0679 | 66.693 | -123.1928 | 122.8901 | 123.0679 | 122.9017 | 66.6965 | -123.4068
1280.7969 | 123.2483 | -66.7007 | 56.2958 | -0.010607 | -0.015692 | 0.0011025 | 0.054149 | -0.0052368 | 0.062717 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058458 | 0.025386 | 0.058308 | -66.7244 | -0.035222 | -66.7414 | 56.2656 | 56.17 | 56.3306 | -66.8513 | -66.752 | -0.045428 | -66.791 | 56.1573 | 56.3443 | 56.1552 | -67.0744 | -0.15051 | -0.030202 | -0.023632 | -0.040682 | 0.10982 | -0.12575 | 0.0348 | -0.37366 | -0.13844 | -0.051218 | -0.090302 | 0.28336 | 0.048477 | -0.14062 | 122.9663 | 122.8708 | 123.0313 | 66.6655 | -123.147 | 122.8581 | 123.045 | 122.8559 | 66.6553 | -123.3702
1281.7969 | 123.1476 | -66.774 | 56.3187 | 0.0046549 | -0.015906 | 0.00088894 | 0.053508 | -0.0052368 | 0.063144 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058458 | 0.025814 | 0.058522 | -66.7335 | -0.039801 | -66.7414 | 56.2564 | 56.17 | 56.3306 | -66.8558 | -66.7428 | -0.040849 | -66.7865 | 56.1619 | 56.3443 | 56.1735 | -67.0744 | -0.081843 | -0.062248 | 0.040453 | 0.03256 | 0.1144 | -0.14864 | 0.011911 | -0.30042 | -0.15675 | 0.031181 | -0.012482 | 0.28794 | 0.025588 | -0.1452 | 123.0304 | 122.944 | 123.1046 | 66.7342 | -123.1745 | 122.9359 | 123.1182 | 122.9475 | 66.7331 | -123.3931
1282.8594 | 123.1796 | -66.7511 | 56.3416 | 0.0046549 | -0.016333 | 0.00088894 | 0.053722 | -0.0054506 | 0.062717 | 0.015414 | -0.0024119 | -0.0011965 | 0.058245 | 0.025814 | 0.058522 | -66.7244 | -0.030644 | -66.746 | 56.2656 | 56.1609 | 56.3397 | -66.8604 | -66.7428 | -0.040849 | -66.7956 | 56.1665 | 56.3443 | 56.1597 | -67.0744 | -0.10931 | -0.075979 | 0.026722 | 0.005094 | 0.1144 | -0.18068 | -0.00182 | -0.32331 | -0.17506 | 0.008293 | -0.044527 | 0.27878 | 0.0027 | -0.18182 | 123.0167 | 122.912 | 123.0908 | 66.7205 | -123.202 | 122.9176 | 123.0954 | 122.9108 | 66.7103 | -123.416
1283.7969 | 123.2391 | -66.7282 | 56.2912 | 0.0046549 | -0.015692 | 0.00088894 | 0.054149 | -0.0052368 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058245 | 0.025814 | 0.058308 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1746 | 56.3352 | -66.8467 | -66.752 | -0.045428 | -66.7865 | 56.1665 | 56.3397 | 56.1597 | -67.0744 | -0.11846 | -0.030204 | 0.003833 | -0.017795 | 0.10067 | -0.11659 | 0.043956 | -0.34619 | -0.1247 | -0.023753 | -0.058259 | 0.28794 | 0.048476 | -0.13147 | 122.9892 | 122.9028 | 123.0634 | 66.693 | -123.1379 | 122.8947 | 123.0679 | 122.8879 | 66.6828 | -123.3656
1284.7969 | 123.2254 | -66.687 | 56.2866 | -0.0029761 | -0.016333 | 0.0011025 | 0.053936 | -0.0050232 | 0.062503 | -0.0074779 | -0.0015573 | -0.00098273 | 0.058245 | 0.0256 | 0.058735 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.1654 | 56.3352 | -66.8513 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3488 | 56.1643 | -67.079 | -0.16424 | -0.025626 | -0.041944 | -0.054415 | 0.10982 | -0.12117 | 0.048534 | -0.39197 | -0.12012 | -0.055794 | -0.10404 | 0.28794 | 0.062211 | -0.12231 | 122.948 | 122.8525 | 123.0222 | 66.6564 | -123.1379 | 122.8535 | 123.0358 | 122.8513 | 66.6507 | -123.3656
1285.7969 | 123.2346 | -66.7053 | 56.3141 | -0.010607 | -0.016119 | 0.00067514 | 0.053936 | -0.0054506 | 0.062289 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.0256 | 0.058949 | -66.7335 | -0.030644 | -66.746 | 56.261 | 56.1517 | 56.3352 | -66.8558 | -66.7474 | -0.036271 | -66.7819 | 56.1619 | 56.3397 | 56.1735 | -67.079 | -0.15051 | -0.053092 | -0.028212 | -0.040683 | 0.10983 | -0.16238 | 0.021068 | -0.37366 | -0.15217 | -0.042063 | -0.076568 | 0.29709 | 0.025588 | -0.14062 | 122.9663 | 122.857 | 123.0405 | 66.6747 | -123.1699 | 122.8672 | 123.045 | 122.8788 | 66.6691 | -123.3931
1286.7969 | 123.23 | -66.7191 | 56.282 | -0.0029761 | -0.015906 | 0.00067514 | 0.054149 | -0.0050232 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058458 | 0.025386 | 0.058949 | -66.7335 | -0.030644 | -66.7368 | 56.2564 | 56.1609 | 56.3352 | -66.8467 | -66.7382 | -0.040849 | -66.7865 | 56.1665 | 56.3351 | 56.1552 | -67.0836 | -0.12762 | -0.025626 | -0.014479 | -0.017793 | 0.10982 | -0.12118 | 0.053112 | -0.36451 | -0.11555 | -0.019172 | -0.067414 | 0.29709 | 0.053053 | -0.12689 | 122.9755 | 122.8799 | 123.0542 | 66.6884 | -123.1287 | 122.8856 | 123.0542 | 122.8742 | 66.6782 | -123.3656
1287.7969 | 123.2391 | -66.7374 | 56.282 | -0.010607 | -0.016119 | 0.00088894 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0017711 | -0.00098273 | 0.057817 | 0.0256 | 0.058308 | -66.7381 | -0.026065 | -66.7506 | 56.2564 | 56.1654 | 56.3352 | -66.8467 | -66.7474 | -0.036271 | -66.791 | 56.1711 | 56.3397 | 56.1597 | -67.079 | -0.10931 | -0.025626 | -0.000746 | -0.013217 | 0.096089 | -0.1166 | 0.053112 | -0.34162 | -0.11097 | -0.010019 | -0.053681 | 0.28794 | 0.057632 | -0.12231 | 122.9938 | 122.9028 | 123.0725 | 66.7113 | -123.1287 | 122.9084 | 123.077 | 122.8971 | 66.7011 | -123.361
1288.8594 | 123.2483 | -66.6779 | 56.3187 | -0.0029761 | -0.016119 | 0.00067514 | 0.054149 | -0.0050232 | 0.062717 | 0.00015261 | -0.0026255 | -0.00076913 | 0.058031 | 0.025814 | 0.058308 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1746 | 56.3306 | -66.8604 | -66.7474 | -0.040849 | -66.7865 | 56.1711 | 56.3443 | 56.1597 | -67.079 | -0.18255 | -0.05767 | -0.046521 | -0.068149 | 0.1144 | -0.14406 | 0.011911 | -0.40113 | -0.14759 | -0.069529 | -0.10861 | 0.29251 | 0.025588 | -0.15893 | 122.9389 | 122.8525 | 123.0084 | 66.6426 | -123.1791 | 122.8489 | 123.0221 | 122.8376 | 66.637 | -123.3976
1289.7969 | 123.2483 | -66.6962 | 56.2729 | 0.0046549 | -0.015906 | 0.0011025 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058031 | 0.025386 | 0.058522 | -66.729 | -0.035222 | -66.746 | 56.2564 | 56.17 | 56.3397 | -66.8513 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3397 | 56.1643 | -67.079 | -0.15508 | -0.016471 | -0.032789 | -0.049838 | 0.10525 | -0.10286 | 0.066845 | -0.38282 | -0.10639 | -0.051218 | -0.085723 | 0.29709 | 0.066787 | -0.10858 | 122.9526 | 122.8662 | 123.0359 | 66.6609 | -123.1241 | 122.8627 | 123.0358 | 122.8605 | 66.6599 | -123.3519
1290.875 | 123.1613 | -66.7099 | 56.3416 | -0.0029761 | -0.015906 | 0.0011025 | 0.053936 | -0.0050232 | 0.06293 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058031 | 0.0256 | 0.058735 | -66.7244 | -0.030644 | -66.7323 | 56.261 | 56.1609 | 56.3306 | -66.8558 | -66.7428 | -0.036271 | -66.7819 | 56.1528 | 56.3305 | 56.1689 | -67.0744 | -0.14593 | -0.080558 | -0.014477 | -0.02237 | 0.12356 | -0.18068 | -0.010977 | -0.3645 | -0.18879 | -0.032906 | -0.07199 | 0.29251 | -0.011036 | -0.17266 | 122.9709 | 122.8708 | 123.0405 | 66.6793 | -123.1974 | 122.8627 | 123.0404 | 122.8788 | 66.6736 | -123.416
1291.7969 | 123.23 | -66.7282 | 56.2408 | -0.010607 | -0.016333 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058031 | 0.0256 | 0.058308 | -66.7335 | -0.030644 | -66.7414 | 56.2564 | 56.1654 | 56.3397 | -66.8467 | -66.7382 | -0.027113 | -66.7819 | 56.1619 | 56.3351 | 56.1643 | -67.0836 | -0.11846 | 0.015572 | -0.005324 | -0.013217 | 0.10524 | -0.075398 | 0.098888 | -0.35535 | -0.078928 | -0.010017 | -0.05368 | 0.30167 | 0.094251 | -0.076534 | 122.9846 | 122.8937 | 123.0679 | 66.6976 | -123.0875 | 122.8901 | 123.0633 | 122.8925 | 66.7011 | -123.3244
1292.7969 | 123.2483 | -66.7191 | 56.2637 | -0.0029761 | -0.015692 | 0.0011025 | 0.054149 | -0.0052368 | 0.062717 | 0.0077831 | -0.0017711 | -0.00034193 | 0.058031 | 0.0256 | 0.058308 | -66.729 | -0.039801 | -66.7368 | 56.2564 | 56.17 | 56.3306 | -66.8467 | -66.7474 | -0.040849 | -66.791 | 56.1665 | 56.3397 | 56.1643 | -67.0836 | -0.12762 | -0.007316 | -0.009901 | -0.017793 | 0.10982 | -0.093707 | 0.066843 | -0.36451 | -0.097237 | -0.02833 | -0.071992 | 0.29251 | 0.075942 | -0.099422 | 122.9755 | 122.8891 | 123.0496 | 66.6793 | -123.1104 | 122.8856 | 123.0587 | 122.8834 | 66.6782 | -123.3473
1293.8594 | 123.1705 | -66.6458 | 56.3141 | 0.012286 | -0.015692 | 0.0011025 | 0.053936 | -0.0054506 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058245 | 0.025814 | 0.058522 | -66.7244 | -0.030644 | -66.7368 | 56.2564 | 56.17 | 56.3443 | -66.8513 | -66.7428 | -0.040849 | -66.7819 | 56.1665 | 56.3305 | 56.1552 | -67.0744 | -0.20544 | -0.05767 | -0.078564 | -0.091035 | 0.1144 | -0.14406 | 0.030225 | -0.42859 | -0.14759 | -0.096993 | -0.13608 | 0.29251 | 0.01643 | -0.15893 | 122.9022 | 122.8158 | 122.9901 | 66.6152 | -123.1653 | 122.8123 | 122.9763 | 122.801 | 66.605 | -123.3885
1294.7969 | 123.23 | -66.7053 | 56.2729 | -0.0029761 | -0.015906 | 0.0011025 | 0.053722 | -0.0048096 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057817 | 0.025814 | 0.058094 | -66.7244 | -0.030644 | -66.7323 | 56.2564 | 56.17 | 56.3397 | -66.8558 | -66.7336 | -0.036271 | -66.791 | 56.1711 | 56.3443 | 56.1552 | -67.079 | -0.15051 | -0.016471 | -0.019055 | -0.026948 | 0.12356 | -0.10286 | 0.066845 | -0.37366 | -0.10181 | -0.028327 | -0.085725 | 0.28794 | 0.071365 | -0.11774 | 122.9617 | 122.8753 | 123.0451 | 66.6747 | -123.1287 | 122.8764 | 123.0496 | 122.8605 | 66.6691 | -123.3519
1295.7969 | 123.2254 | -66.7099 | 56.3095 | 0.0046549 | -0.015478 | 0.0013163 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058458 | 0.025814 | 0.058522 | -66.7335 | -0.030644 | -66.7277 | 56.2564 | 56.1563 | 56.326 | -66.8558 | -66.7336 | -0.040849 | -66.791 | 56.1665 | 56.3397 | 56.1643 | -67.0836 | -0.14593 | -0.053092 | -0.023634 | -0.017792 | 0.12814 | -0.15322 | 0.016488 | -0.37366 | -0.14301 | -0.023749 | -0.081147 | 0.29251 | 0.030166 | -0.1452 | 122.9663 | 122.8662 | 123.0359 | 66.6793 | -123.1653 | 122.8764 | 123.0496 | 122.8742 | 66.6691 | -123.3931
1296.7969 | 123.2849 | -66.6916 | 56.3141 | -0.0029761 | -0.015692 | 0.0011025 | 0.053936 | -0.0054506 | 0.061862 | 0.00015261 | -0.0019847 | -0.00055553 | 0.058031 | 0.025173 | 0.058094 | -66.729 | -0.026065 | -66.7323 | 56.261 | 56.1654 | 56.3397 | -66.8513 | -66.7428 | -0.045428 | -66.7956 | 56.1665 | 56.3397 | 56.1643 | -67.079 | -0.15966 | -0.053092 | -0.037367 | -0.040681 | 0.11898 | -0.14864 | 0.025646 | -0.38739 | -0.14759 | -0.051217 | -0.10404 | 0.28336 | 0.025588 | -0.14978 | 122.9526 | 122.857 | 123.0313 | 66.6655 | -123.1653 | 122.8581 | 123.0313 | 122.8559 | 66.6462 | -123.3931
1297.7969 | 123.2574 | -66.7145 | 56.2775 | -0.0029761 | -0.016119 | 0.0011025 | 0.053936 | -0.0052368 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058458 | 0.025814 | 0.058308 | -66.729 | -0.026065 | -66.7277 | 56.2656 | 56.17 | 56.3352 | -66.8513 | -66.7428 | -0.040849 | -66.7865 | 56.1711 | 56.3443 | 56.1735 | -67.0836 | -0.13677 | -0.011892 | -0.014478 | -0.013214 | 0.12356 | -0.10744 | 0.057689 | -0.36908 | -0.10639 | -0.028328 | -0.071991 | 0.29709 | 0.066787 | -0.104 | 122.9801 | 122.8845 | 123.0496 | 66.6884 | -123.1287 | 122.8856 | 123.0587 | 122.8879 | 66.6736 | -123.361
1298.8594 | 123.2712 | -66.7053 | 56.2912 | -0.010607 | -0.015906 | 0.0011025 | 0.054149 | -0.0052368 | 0.062717 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058245 | 0.0256 | 0.058308 | -66.7335 | -0.026065 | -66.746 | 56.261 | 56.1609 | 56.3352 | -66.8375 | -66.7474 | -0.040849 | -66.791 | 56.1665 | 56.3397 | 56.1552 | -67.0836 | -0.13219 | -0.030204 | -0.028212 | -0.040683 | 0.091509 | -0.13033 | 0.043956 | -0.37824 | -0.1247 | -0.042063 | -0.085725 | 0.29251 | 0.048476 | -0.13605 | 122.9663 | 122.8662 | 123.0405 | 66.6793 | -123.1287 | 122.8718 | 123.045 | 122.8605 | 66.6645 | -123.3748
1299.7969 | 123.23 | -66.7053 | 56.282 | 0.0046549 | -0.016119 | 0.00088894 | 0.054149 | -0.0052368 | 0.062717 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058031 | 0.025814 | 0.058094 | -66.729 | -0.035222 | -66.7414 | 56.261 | 56.17 | 56.3352 | -66.8558 | -66.7428 | -0.040849 | -66.791 | 56.1711 | 56.3443 | 56.1552 | -67.0881 | -0.15051 | -0.021048 | -0.023634 | -0.036105 | 0.1144 | -0.11202 | 0.053112 | -0.38282 | -0.11097 | -0.037484 | -0.085725 | 0.29709 | 0.06221 | -0.12689 | 122.9663 | 122.8753 | 123.0405 | 66.6701 | -123.1379 | 122.8764 | 123.0496 | 122.8605 | 66.6645 | -123.3702
1300.8594 | 123.2162 | -66.7053 | 56.3324 | -0.0029761 | -0.015906 | 0.0011025 | 0.053722 | -0.0050232 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058031 | 0.026028 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.2564 | 56.17 | 56.3352 | -66.865 | -66.7428 | -0.040849 | -66.7819 | 56.1665 | 56.3397 | 56.1735 | -67.079 | -0.15967 | -0.07598 | -0.019055 | -0.040683 | 0.11898 | -0.16237 | 0.002758 | -0.37366 | -0.1659 | -0.037484 | -0.076568 | 0.29709 | 0.007278 | -0.15893 | 122.9617 | 122.8753 | 123.0405 | 66.6701 | -123.1974 | 122.8718 | 123.045 | 122.8788 | 66.6645 | -123.4114
1301.7969 | 123.23 | -66.7007 | 56.2866 | 0.012286 | -0.015906 | 0.00088894 | 0.053936 | -0.0054506 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058458 | 0.025814 | 0.058735 | -66.729 | -0.026065 | -66.746 | 56.2564 | 56.17 | 56.3397 | -66.8513 | -66.7474 | -0.036271 | -66.791 | 56.1711 | 56.3443 | 56.1643 | -67.0836 | -0.15051 | -0.030204 | -0.028211 | -0.04526 | 0.10525 | -0.11659 | 0.053112 | -0.38282 | -0.11555 | -0.04664 | -0.090302 | 0.29251 | 0.057632 | -0.12231 | 122.9572 | 122.8708 | 123.0405 | 66.6747 | -123.1379 | 122.8718 | 123.045 | 122.8651 | 66.6645 | -123.3702
1302.7969 | 123.2803 | -66.7007 | 56.3049 | -0.0029761 | -0.016119 | 0.0011025 | 0.054149 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00055553 | 0.058458 | 0.0256 | 0.058735 | -66.7244 | -0.035222 | -66.746 | 56.261 | 56.1563 | 56.3443 | -66.8513 | -66.7382 | -0.045428 | -66.7819 | 56.1573 | 56.3397 | 56.1689 | -67.0836 | -0.15051 | -0.043937 | -0.023632 | -0.04526 | 0.10525 | -0.14864 | 0.03938 | -0.38282 | -0.14759 | -0.037482 | -0.081145 | 0.30167 | 0.034743 | -0.13604 | 122.9617 | 122.857 | 123.0451 | 66.6655 | -123.1562 | 122.8581 | 123.0404 | 122.8696 | 66.6553 | -123.3885
1303.7969 | 123.2803 | -66.6687 | 56.282 | 0.0046549 | -0.015906 | 0.00088894 | 0.053722 | -0.0048096 | 0.062503 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058458 | 0.025814 | 0.058094 | -66.7244 | -0.035222 | -66.7414 | 56.2564 | 56.17 | 56.3352 | -66.8513 | -66.7382 | -0.036271 | -66.791 | 56.1619 | 56.3397 | 56.146 | -67.079 | -0.18255 | -0.025626 | -0.055676 | -0.072726 | 0.10982 | -0.11202 | 0.053112 | -0.41028 | -0.12013 | -0.069526 | -0.12235 | 0.28794 | 0.057632 | -0.13605 | 122.9251 | 122.8387 | 123.0039 | 66.6335 | -123.1333 | 122.8306 | 123.0084 | 122.8147 | 66.6324 | -123.361
1304.8594 | 123.2162 | -66.7328 | 56.2912 | -0.010607 | -0.016333 | 0.00088894 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058031 | 0.0256 | 0.058308 | -66.729 | -0.035222 | -66.7506 | 56.2656 | 56.1563 | 56.3352 | -66.8604 | -66.7474 | -0.036271 | -66.791 | 56.1665 | 56.3443 | 56.1506 | -67.079 | -0.12762 | -0.025625 | 0.003832 | -0.017795 | 0.10983 | -0.13491 | 0.043956 | -0.34619 | -0.1247 | -0.014597 | -0.058259 | 0.28794 | 0.053054 | -0.14062 | 122.9984 | 122.8891 | 123.0679 | 66.6976 | -123.1516 | 122.8993 | 123.077 | 122.8834 | 66.6965 | -123.3702
1305.7969 | 123.2437 | -66.7099 | 56.3049 | 0.0046549 | -0.015906 | 0.00067514 | 0.054149 | -0.0052368 | 0.062289 | -0.0074779 | -0.0019847 | -0.00055553 | 0.058031 | 0.025814 | 0.058094 | -66.729 | -0.035222 | -66.7368 | 56.261 | 56.1654 | 56.3352 | -66.8558 | -66.7428 | -0.040849 | -66.7865 | 56.1665 | 56.3397 | 56.1597 | -67.0836 | -0.14593 | -0.043937 | -0.019056 | -0.026948 | 0.11898 | -0.13949 | 0.030223 | -0.37366 | -0.13844 | -0.032906 | -0.076569 | 0.29709 | 0.034743 | -0.1452 | 122.9709 | 122.8753 | 123.0451 | 66.6747 | -123.1608 | 122.8764 | 123.0496 | 122.8696 | 66.6691 | -123.3885
1306.8594 | 123.1934 | -66.7053 | 56.3141 | 0.0046549 | -0.016119 | 0.0011025 | 0.053936 | -0.0056642 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058245 | 0.0256 | 0.057881 | -66.729 | -0.030644 | -66.7368 | 56.2564 | 56.17 | 56.326 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1665 | 56.3443 | 56.1552 | -67.0744 | -0.15051 | -0.05767 | -0.023634 | -0.031526 | 0.11898 | -0.14406 | 0.01191 | -0.36908 | -0.14759 | -0.037484 | -0.081147 | 0.28794 | 0.030166 | -0.15893 | 122.9617 | 122.8753 | 123.0313 | 66.6747 | -123.1699 | 122.8718 | 123.0496 | 122.8605 | 66.6736 | -123.3885
1307.7969 | 123.2529 | -66.687 | 56.2912 | -0.0029761 | -0.016119 | 0.00088894 | 0.053722 | -0.0052368 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057604 | 0.025814 | 0.058522 | -66.729 | -0.021486 | -66.7368 | 56.261 | 56.1609 | 56.3352 | -66.8604 | -66.7428 | -0.036271 | -66.7819 | 56.1619 | 56.3443 | 56.1643 | -67.079 | -0.1734 | -0.030204 | -0.041944 | -0.049836 | 0.12356 | -0.13033 | 0.043956 | -0.39197 | -0.12928 | -0.055794 | -0.094878 | 0.29709 | 0.053054 | -0.12689 | 122.948 | 122.8479 | 123.0222 | 66.6655 | -123.1516 | 122.8489 | 123.0313 | 122.8513 | 66.6507 | -123.3702
1308.8594 | 123.1567 | -66.7145 | 56.3599 | 0.0046549 | -0.015906 | 0.00088894 | 0.053936 | -0.0054506 | 0.062289 | 0.015414 | -0.0021983 | -0.00076913 | 0.058245 | 0.025814 | 0.058308 | -66.729 | -0.039801 | -66.7323 | 56.2564 | 56.1654 | 56.3352 | -66.8558 | -66.7336 | -0.040849 | -66.7865 | 56.1757 | 56.3351 | 56.1689 | -67.079 | -0.14135 | -0.10345 | -0.014478 | -0.017792 | 0.12356 | -0.19442 | -0.024708 | -0.3645 | -0.18421 | -0.019171 | -0.071991 | 0.29251 | -0.024767 | -0.19097 | 122.9709 | 122.8799 | 123.0496 | 66.6747 | -123.2157 | 122.8901 | 123.0496 | 122.8834 | 66.6736 | -123.4388
1309.7969 | 123.2254 | -66.7007 | 56.3187 | -0.0029761 | -0.015906 | 0.0013163 | 0.054149 | -0.0052368 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.058031 | 0.025814 | 0.058308 | -66.7335 | -0.035222 | -66.7323 | 56.261 | 56.17 | 56.3397 | -66.865 | -66.7428 | -0.036271 | -66.7819 | 56.1665 | 56.3397 | 56.1826 | -67.0744 | -0.16424 | -0.05767 | -0.032789 | -0.031525 | 0.13272 | -0.14864 | 0.021068 | -0.37366 | -0.15217 | -0.042061 | -0.081145 | 0.29251 | 0.02101 | -0.13604 | 122.9617 | 122.8708 | 123.0405 | 66.6655 | -123.1837 | 122.8672 | 123.0404 | 122.8834 | 66.6645 | -123.3931
1310.7969 | 123.2574 | -66.6733 | 56.3324 | -0.0029761 | -0.015692 | 0.0011025 | 0.054149 | -0.0052368 | 0.062503 | 0.0077831 | -0.0024119 | -0.00055553 | 0.058245 | 0.0256 | 0.058094 | -66.7244 | -0.030644 | -66.7323 | 56.261 | 56.1654 | 56.3306 | -66.8558 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3351 | 56.1689 | -67.0744 | -0.18255 | -0.071402 | -0.051098 | -0.058991 | 0.12356 | -0.16695 | -0.001821 | -0.40113 | -0.1659 | -0.069527 | -0.11777 | 0.28336 | 0.002699 | -0.16351 | 122.9343 | 122.8387 | 123.0039 | 66.6426 | -123.1882 | 122.8398 | 123.0084 | 122.8422 | 66.637 | -123.4068
1311.8594 | 123.2666 | -66.7191 | 56.25 | -0.0029761 | -0.016119 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058245 | 0.025814 | 0.058735 | -66.729 | -0.026065 | -66.7506 | 56.261 | 56.1654 | 56.3443 | -66.8558 | -66.7474 | -0.031692 | -66.7956 | 56.1711 | 56.3443 | 56.1597 | -67.079 | -0.13678 | 0.010995 | -0.009901 | -0.031528 | 0.10525 | -0.084553 | 0.094312 | -0.35993 | -0.078926 | -0.02833 | -0.076571 | 0.28336 | 0.094253 | -0.090268 | 122.9801 | 122.8845 | 123.0634 | 66.693 | -123.1058 | 122.8901 | 123.0633 | 122.8788 | 66.6874 | -123.329
1312.7969 | 123.2758 | -66.6962 | 56.3049 | 0.0046549 | -0.016119 | 0.00067514 | 0.053936 | -0.0050232 | 0.062717 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058031 | 0.026028 | 0.058522 | -66.7335 | -0.035222 | -66.7414 | 56.2656 | 56.1746 | 56.3397 | -66.8513 | -66.7428 | -0.045428 | -66.7773 | 56.1757 | 56.3397 | 56.1735 | -67.0744 | -0.15508 | -0.039358 | -0.037367 | -0.04526 | 0.10982 | -0.13033 | 0.034801 | -0.37824 | -0.12928 | -0.046639 | -0.081144 | 0.29709 | 0.034743 | -0.13146 | 122.9617 | 122.8708 | 123.0359 | 66.6609 | -123.1562 | 122.8718 | 123.0358 | 122.8696 | 66.6507 | -123.3793
1313.7969 | 123.2758 | -66.6962 | 56.2958 | 0.012286 | -0.016119 | 0.00088894 | 0.053722 | -0.0052368 | 0.062503 | -0.0074779 | -0.0019847 | -0.0011965 | 0.058031 | 0.025814 | 0.058522 | -66.7244 | -0.030644 | -66.7506 | 56.2656 | 56.1609 | 56.3306 | -66.8513 | -66.7336 | -0.045428 | -66.7819 | 56.1619 | 56.3351 | 56.1643 | -67.0836 | -0.15508 | -0.030202 | -0.02821 | -0.054416 | 0.10067 | -0.13491 | 0.0348 | -0.38739 | -0.13386 | -0.037482 | -0.085723 | 0.30167 | 0.03932 | -0.13146 | 122.9617 | 122.857 | 123.0267 | 66.6655 | -123.147 | 122.8581 | 123.0313 | 122.8605 | 66.6507 | -123.3793
1314.7969 | 123.1934 | -66.7145 | 56.3095 | 0.0046549 | -0.016119 | 0.00088894 | 0.053936 | -0.0054506 | 0.062289 | 0.015414 | -0.0021983 | -0.00098273 | 0.058458 | 0.025814 | 0.058735 | -66.7244 | -0.030644 | -66.7368 | 56.2564 | 56.17 | 56.3397 | -66.865 | -66.7474 | -0.036271 | -66.7819 | 56.1711 | 56.3351 | 56.1735 | -67.079 | -0.15051 | -0.053092 | -0.009899 | -0.02237 | 0.12814 | -0.13948 | 0.030224 | -0.3645 | -0.13844 | -0.032907 | -0.067412 | 0.29709 | 0.025587 | -0.13604 | 122.9709 | 122.8845 | 123.0542 | 66.6838 | -123.1745 | 122.8856 | 123.0496 | 122.8879 | 66.6782 | -123.3885
1315.7969 | 123.2208 | -66.7145 | 56.2958 | -0.0029761 | -0.016333 | 0.00046154 | 0.053722 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058245 | 0.025814 | 0.058094 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.1609 | 56.3352 | -66.8513 | -66.7428 | -0.040849 | -66.791 | 56.1711 | 56.3351 | 56.1689 | -67.079 | -0.13677 | -0.034781 | -0.014478 | -0.026949 | 0.10982 | -0.13491 | 0.039379 | -0.3645 | -0.1247 | -0.028328 | -0.076569 | 0.28794 | 0.03932 | -0.12689 | 122.9755 | 122.8753 | 123.0496 | 66.6838 | -123.147 | 122.8856 | 123.0496 | 122.8834 | 66.6736 | -123.3748
1316.8594 | 123.2712 | -66.6962 | 56.3232 | 0.0046549 | -0.016547 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.015414 | -0.0021983 | -0.0011965 | 0.057817 | 0.026028 | 0.058308 | -66.729 | -0.035222 | -66.7552 | 56.261 | 56.1654 | 56.3397 | -66.8375 | -66.7474 | -0.040849 | -66.7865 | 56.1665 | 56.3351 | 56.1643 | -67.079 | -0.14135 | -0.062247 | -0.032789 | -0.058994 | 0.082353 | -0.1578 | 0.016491 | -0.38282 | -0.15675 | -0.051218 | -0.090302 | 0.29251 | 0.011854 | -0.15893 | 122.9572 | 122.8616 | 123.0359 | 66.6609 | -123.1608 | 122.8627 | 123.0313 | 122.8605 | 66.6553 | -123.4022
1317.7969 | 123.1705 | -66.7328 | 56.3461 | 0.0046549 | -0.016119 | 0.00088894 | 0.053936 | -0.0050232 | 0.062289 | 0.00015261 | -0.0024119 | -0.00098273 | 0.058031 | 0.025814 | 0.058308 | -66.7335 | -0.030644 | -66.746 | 56.261 | 56.1838 | 56.3397 | -66.8604 | -66.7382 | -0.040849 | -66.7819 | 56.1619 | 56.3351 | 56.1689 | -67.0836 | -0.12762 | -0.085135 | -0.000746 | -0.013217 | 0.1144 | -0.16237 | -0.006397 | -0.35077 | -0.18421 | -0.005439 | -0.049102 | 0.30167 | -0.011034 | -0.17724 | 122.9938 | 122.9166 | 123.0725 | 66.7021 | -123.2065 | 122.8947 | 123.0679 | 122.9017 | 66.6919 | -123.4297
1318.8594 | 123.2391 | -66.7099 | 56.2729 | -0.010607 | -0.016333 | 0.00088894 | 0.053722 | -0.0054506 | 0.062503 | 0.0077831 | -0.0024119 | -0.00076913 | 0.058245 | 0.026028 | 0.058522 | -66.7335 | -0.030644 | -66.7552 | 56.2702 | 56.17 | 56.3352 | -66.8329 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.3397 | 56.1552 | -67.0836 | -0.12304 | -0.002736 | -0.023634 | -0.045261 | 0.077774 | -0.10286 | 0.062267 | -0.37366 | -0.10181 | -0.037485 | -0.076569 | 0.29709 | 0.066787 | -0.11774 | 122.9801 | 122.8799 | 123.0451 | 66.6793 | -123.1058 | 122.881 | 123.0496 | 122.8651 | 66.6736 | -123.3564
1319.7969 | 123.2849 | -66.7191 | 56.3232 | 0.012286 | -0.016547 | 0.0011025 | 0.053722 | -0.0056642 | 0.062503 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058031 | 0.026241 | 0.058522 | -66.7244 | -0.035222 | -66.7506 | 56.261 | 56.1746 | 56.3397 | -66.8558 | -66.752 | -0.045428 | -66.791 | 56.1665 | 56.3397 | 56.1643 | -67.079 | -0.13678 | -0.062247 | -0.005322 | -0.031528 | 0.10525 | -0.14864 | 0.016491 | -0.35993 | -0.15675 | -0.032908 | -0.071992 | 0.28794 | 0.016433 | -0.15893 | 122.9801 | 122.8937 | 123.0588 | 66.6838 | -123.1791 | 122.8856 | 123.0587 | 122.8834 | 66.6736 | -123.4022
1320.7969 | 123.1293 | -66.7603 | 56.3004 | -0.0029761 | -0.016333 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058245 | 0.026028 | 0.058522 | -66.729 | -0.026065 | -66.746 | 56.261 | 56.1792 | 56.3443 | -66.8604 | -66.7428 | -0.031692 | -66.7865 | 56.1619 | 56.3351 | 56.1689 | -67.0836 | -0.10015 | -0.039359 | 0.031298 | 0.014249 | 0.1144 | -0.12117 | 0.043958 | -0.32331 | -0.13844 | 0.017448 | -0.026215 | 0.29709 | 0.034742 | -0.13146 | 123.0212 | 122.9394 | 123.1046 | 66.7342 | -123.1608 | 122.9222 | 123.0953 | 122.9291 | 66.7286 | -123.3839
1321.7969 | 123.2574 | -66.6962 | 56.3232 | 0.012286 | -0.016333 | 0.00067514 | 0.053508 | -0.0052368 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058031 | 0.025386 | 0.058522 | -66.729 | -0.030644 | -66.7414 | 56.2564 | 56.1792 | 56.3443 | -66.8467 | -66.7428 | -0.036271 | -66.791 | 56.1619 | 56.3397 | 56.1597 | -67.079 | -0.1505 | -0.066825 | -0.032789 | -0.04526 | 0.10524 | -0.14406 | 0.02107 | -0.38282 | -0.16132 | -0.046639 | -0.09488 | 0.28794 | 0.016433 | -0.16351 | 122.9526 | 122.8754 | 123.0405 | 66.6655 | -123.1699 | 122.8581 | 123.0358 | 122.8559 | 66.6599 | -123.4022
1322.8594 | 123.1567 | -66.7236 | 56.337 | 0.0046549 | -0.016333 | 0.00088894 | 0.053508 | -0.0050232 | 0.06293 | 0.015414 | -0.0019847 | -0.0011965 | 0.058245 | 0.026455 | 0.058735 | -66.7335 | -0.026065 | -66.746 | 56.2702 | 56.1654 | 56.3397 | -66.8558 | -66.7382 | -0.050007 | -66.7819 | 56.1619 | 56.3397 | 56.1597 | -67.0836 | -0.1322 | -0.066823 | -0.009901 | -0.022372 | 0.10983 | -0.17153 | 0.002758 | -0.35993 | -0.17506 | -0.014594 | -0.058257 | 0.30167 | 0.0027 | -0.17724 | 122.9938 | 122.8891 | 123.0634 | 66.6976 | -123.1928 | 122.8856 | 123.0633 | 122.8834 | 66.6736 | -123.4205
1323.7969 | 123.1796 | -66.7328 | 56.3416 | -0.0029761 | -0.016119 | 0.00088894 | 0.053722 | -0.0052368 | 0.062289 | 0.015414 | -0.0021983 | -0.00098273 | 0.058245 | 0.026241 | 0.058522 | -66.729 | -0.026065 | -66.7323 | 56.2564 | 56.1746 | 56.3397 | -66.865 | -66.7474 | -0.040849 | -66.7865 | 56.1573 | 56.3397 | 56.1826 | -67.079 | -0.1322 | -0.085136 | 0.003832 | 0.000518 | 0.13272 | -0.16695 | -0.00182 | -0.34619 | -0.18421 | -0.014597 | -0.053681 | 0.29251 | -0.001878 | -0.15893 | 122.9892 | 122.9074 | 123.0725 | 66.7067 | -123.2065 | 122.8901 | 123.0725 | 122.9154 | 66.6919 | -123.4205
1324.7969 | 123.1476 | -66.7191 | 56.3507 | 0.0046549 | -0.016333 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0017711 | -0.0011965 | 0.058245 | 0.026241 | 0.058308 | -66.729 | -0.035222 | -66.746 | 56.2656 | 56.1517 | 56.3306 | -66.8558 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3351 | 56.1735 | -67.0744 | -0.13678 | -0.085134 | -0.009901 | -0.02695 | 0.10983 | -0.199 | -0.020132 | -0.35535 | -0.18421 | -0.023751 | -0.071992 | 0.28336 | -0.015612 | -0.17724 | 122.9846 | 122.8708 | 123.0496 | 66.6838 | -123.2065 | 122.8856 | 123.0542 | 122.8925 | 66.6828 | -123.4251
1325.7969 | 123.2208 | -66.7053 | 56.3324 | 0.0046549 | -0.015906 | 0.00088894 | 0.054149 | -0.0050232 | 0.062503 | 0.015414 | -0.0019847 | -0.00098273 | 0.058245 | 0.026028 | 0.058308 | -66.729 | -0.030644 | -66.7368 | 56.2656 | 56.17 | 56.3443 | -66.8558 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3351 | 56.1689 | -67.0927 | -0.15051 | -0.066823 | -0.023634 | -0.031526 | 0.11898 | -0.16237 | 0.011915 | -0.3874 | -0.1659 | -0.042063 | -0.076568 | 0.31083 | 0.002699 | -0.16351 | 122.9709 | 122.8753 | 123.0496 | 66.6747 | -123.1882 | 122.8718 | 123.0404 | 122.8742 | 66.6691 | -123.4251
1326.7969 | 123.1613 | -66.774 | 56.3278 | -0.0029761 | -0.016761 | 0.00067514 | 0.053722 | -0.0052368 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.058031 | 0.025814 | 0.058094 | -66.7244 | -0.035222 | -66.7414 | 56.2702 | 56.1654 | 56.3397 | -66.8558 | -66.7474 | -0.040849 | -66.7865 | 56.1665 | 56.3443 | 56.1597 | -67.0744 | -0.081843 | -0.057668 | 0.04961 | 0.03256 | 0.1144 | -0.16237 | 0.011913 | -0.30042 | -0.16132 | 0.026602 | -0.012482 | 0.28794 | 0.016433 | -0.16809 | 123.0441 | 122.9394 | 123.1137 | 66.7388 | -123.1837 | 122.9405 | 123.1182 | 122.9337 | 66.7331 | -123.4022
1327.8594 | 123.2071 | -66.7099 | 56.2958 | -0.0029761 | -0.016333 | 0.00067514 | 0.054149 | -0.0056642 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058245 | 0.025814 | 0.058094 | -66.7335 | -0.035222 | -66.7368 | 56.2656 | 56.1609 | 56.3352 | -66.8604 | -66.7428 | -0.040849 | -66.7819 | 56.1619 | 56.3397 | 56.1643 | -67.079 | -0.15051 | -0.030202 | -0.023634 | -0.026948 | 0.12356 | -0.13491 | 0.039379 | -0.36908 | -0.13386 | -0.032906 | -0.07199 | 0.29709 | 0.043899 | -0.13146 | 122.9755 | 122.8708 | 123.0451 | 66.6747 | -123.1562 | 122.8718 | 123.0496 | 122.8742 | 66.6691 | -123.3748
1328.7969 | 123.2162 | -66.7328 | 56.337 | -0.0029761 | -0.016547 | 0.00088894 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0024119 | -0.00098273 | 0.058245 | 0.026241 | 0.058522 | -66.7335 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.3443 | -66.8604 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3397 | 56.1643 | -67.0836 | -0.12762 | -0.066823 | -0.000746 | -0.008639 | 0.11898 | -0.16237 | 0.007337 | -0.35077 | -0.17048 | -0.014597 | -0.049102 | 0.30167 | 0.0027 | -0.17266 | 123.0029 | 122.9074 | 123.0771 | 66.7067 | -123.1974 | 122.8993 | 123.0725 | 122.8971 | 66.6965 | -123.4205
1329.7969 | 123.175 | -66.7236 | 56.3278 | 0.0046549 | -0.016547 | 0.00067514 | 0.053722 | -0.0050232 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058031 | 0.026028 | 0.058308 | -66.729 | -0.035222 | -66.746 | 56.2656 | 56.1609 | 56.3397 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.3397 | 56.1689 | -67.0836 | -0.13678 | -0.062246 | -0.005323 | -0.022372 | 0.1144 | -0.16695 | 0.011913 | -0.35993 | -0.15675 | -0.019173 | -0.058257 | 0.30167 | 0.011855 | -0.15893 | 122.9892 | 122.8845 | 123.0634 | 66.6884 | -123.1882 | 122.8947 | 123.0633 | 122.8925 | 66.6965 | -123.4114
1330.7969 | 123.1888 | -66.7191 | 56.3095 | -0.010607 | -0.016547 | 0.00046154 | 0.053722 | -0.0056642 | 0.06293 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058458 | 0.026028 | 0.058094 | -66.7244 | -0.026065 | -66.7506 | 56.261 | 56.1838 | 56.3443 | -66.865 | -66.752 | -0.031692 | -66.7819 | 56.1665 | 56.3397 | 56.1552 | -67.0744 | -0.14593 | -0.048514 | -0.005322 | -0.031528 | 0.1144 | -0.12575 | 0.034803 | -0.35535 | -0.14301 | -0.032908 | -0.062835 | 0.29251 | 0.030166 | -0.15436 | 122.9801 | 122.9028 | 123.0634 | 66.693 | -123.1745 | 122.8856 | 123.0587 | 122.8742 | 66.6874 | -123.3839
1331.7969 | 123.1659 | -66.7282 | 56.3461 | 0.0046549 | -0.016547 | 0.00088894 | 0.053508 | -0.0052368 | 0.062503 | 0.00015261 | -0.0017711 | -0.0011965 | 0.058031 | 0.026241 | 0.058094 | -66.7244 | -0.035222 | -66.746 | 56.2656 | 56.1746 | 56.3443 | -66.8513 | -66.7474 | -0.031692 | -66.7819 | 56.1619 | 56.3351 | 56.1643 | -67.079 | -0.12304 | -0.080556 | 0.003833 | -0.017795 | 0.10525 | -0.17153 | -0.001818 | -0.35077 | -0.18421 | -0.019175 | -0.05368 | 0.29709 | -0.011034 | -0.18182 | 122.9938 | 122.9028 | 123.0725 | 66.693 | -123.1974 | 122.8901 | 123.0633 | 122.8925 | 66.6965 | -123.4251
1332.7969 | 123.1476 | -66.8015 | 56.3004 | -0.0029761 | -0.016547 | 0.00046154 | 0.054149 | -0.0052368 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.058031 | 0.026241 | 0.058522 | -66.7244 | -0.030644 | -66.746 | 56.2656 | 56.1654 | 56.3397 | -66.8558 | -66.7428 | -0.036271 | -66.7773 | 56.1665 | 56.3397 | 56.1597 | -67.079 | -0.054377 | -0.03478 | 0.077076 | 0.055448 | 0.10983 | -0.13491 | 0.039379 | -0.27753 | -0.13386 | 0.058647 | 0.024142 | 0.30167 | 0.039321 | -0.14062 | 123.067 | 122.9669 | 123.1412 | 66.7708 | -123.1562 | 122.9679 | 123.1411 | 122.9612 | 66.7652 | -123.3793
1333.7969 | 123.1888 | -66.7328 | 56.337 | -0.010607 | -0.016547 | 0.00067514 | 0.054149 | -0.0054506 | 0.062717 | 0.023044 | -0.0019847 | -0.0011965 | 0.058245 | 0.026028 | 0.058522 | -66.729 | -0.026065 | -66.746 | 56.2656 | 56.1838 | 56.3443 | -66.8604 | -66.7382 | -0.036271 | -66.791 | 56.1619 | 56.3397 | 56.1735 | -67.079 | -0.12762 | -0.071401 | 0.003832 | -0.013217 | 0.1144 | -0.15321 | 0.007337 | -0.34619 | -0.17506 | -0.005439 | -0.058259 | 0.28794 | 0.0027 | -0.16351 | 122.9984 | 122.9166 | 123.0771 | 66.7067 | -123.1974 | 122.8947 | 123.0725 | 122.9063 | 66.6965 | -123.416
1334.8594 | 123.2391 | -66.6824 | 56.3324 | 0.0046549 | -0.016761 | 0.00088894 | 0.053936 | -0.0052368 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.057817 | 0.026455 | 0.058308 | -66.729 | -0.035222 | -66.746 | 56.261 | 56.1746 | 56.3397 | -66.8558 | -66.7382 | -0.040849 | -66.791 | 56.1619 | 56.3397 | 56.178 | -67.079 | -0.1734 | -0.071402 | -0.046522 | -0.063571 | 0.10983 | -0.15779 | 0.007336 | -0.39655 | -0.17048 | -0.055793 | -0.10861 | 0.28794 | 0.007278 | -0.15435 | 122.9434 | 122.857 | 123.0222 | 66.6472 | -123.1882 | 122.8444 | 123.0221 | 122.8605 | 66.6416 | -123.4114
1335.7969 | 123.2025 | -66.7374 | 56.3095 | -0.0029761 | -0.016547 | 0.00088894 | 0.054363 | -0.0052368 | 0.062717 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058245 | 0.026455 | 0.058308 | -66.7335 | -0.026065 | -66.7552 | 56.2702 | 56.1746 | 56.3443 | -66.8558 | -66.7474 | -0.036271 | -66.7865 | 56.1619 | 56.3397 | 56.1597 | -67.0836 | -0.11846 | -0.039357 | 0.003832 | -0.017795 | 0.10067 | -0.1349 | 0.034803 | -0.3462 | -0.14759 | -0.010019 | -0.049103 | 0.29709 | 0.030166 | -0.14978 | 123.0075 | 122.912 | 123.0817 | 66.7113 | -123.1653 | 122.8993 | 123.077 | 122.8971 | 66.7011 | -123.3931
1336.7969 | 123.1476 | -66.7465 | 56.3141 | 0.012286 | -0.016333 | 0.00046154 | 0.054149 | -0.0054506 | 0.062503 | 0.015414 | -0.0019847 | -0.00055553 | 0.058031 | 0.026455 | 0.058094 | -66.7244 | -0.026065 | -66.7414 | 56.261 | 56.17 | 56.3489 | -66.865 | -66.7474 | -0.036271 | -66.7819 | 56.1711 | 56.3488 | 56.1689 | -67.0881 | -0.11847 | -0.053092 | 0.022144 | 0.005094 | 0.12356 | -0.14406 | 0.034803 | -0.34162 | -0.14301 | -0.000864 | -0.035369 | 0.30625 | 0.034745 | -0.1452 | 123.0075 | 122.9165 | 123.0954 | 66.7205 | -123.1791 | 122.9176 | 123.0954 | 122.9154 | 66.7103 | -123.4022
1337.7969 | 123.1888 | -66.7419 | 56.2958 | -0.0029761 | -0.016547 | 0.00088894 | 0.054149 | -0.0054506 | 0.062503 | 0.00015261 | -0.0019847 | -0.00055553 | 0.058031 | 0.026028 | 0.058522 | -66.7244 | -0.035222 | -66.746 | 56.2656 | 56.1746 | 56.3443 | -66.8558 | -66.7474 | -0.027113 | -66.7865 | 56.1757 | 56.3443 | 56.1643 | -67.0744 | -0.11389 | -0.030202 | 0.017566 | -0.004062 | 0.10983 | -0.12117 | 0.048536 | -0.33246 | -0.12012 | -0.005442 | -0.044526 | 0.28794 | 0.048477 | -0.13146 | 123.0075 | 122.9165 | 123.0863 | 66.7067 | -123.1516 | 122.9176 | 123.0862 | 122.9063 | 66.7148 | -123.3702
1338.7969 | 123.23 | -66.7099 | 56.2866 | -0.010607 | -0.016547 | 0.0011025 | 0.054149 | -0.0052368 | 0.062503 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058031 | 0.026455 | 0.058522 | -66.7381 | -0.026065 | -66.7414 | 56.261 | 56.17 | 56.3397 | -66.8604 | -66.7474 | -0.031692 | -66.7819 | 56.1619 | 56.3443 | 56.1643 | -67.0881 | -0.15051 | -0.025626 | -0.028212 | -0.031527 | 0.11898 | -0.11659 | 0.053112 | -0.37824 | -0.1247 | -0.037485 | -0.07199 | 0.30625 | 0.057632 | -0.12231 | 122.9709 | 122.8799 | 123.0496 | 66.6838 | -123.147 | 122.8718 | 123.0542 | 122.8742 | 66.6782 | -123.3748
1339.7969 | 123.1567 | -66.7328 | 56.3095 | -0.010607 | -0.016761 | 0.00046154 | 0.053936 | -0.0052368 | 0.062717 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.026241 | 0.058094 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.17 | 56.3397 | -66.8604 | -66.7382 | -0.036271 | -66.7682 | 56.1665 | 56.3397 | 56.1506 | -67.0836 | -0.12762 | -0.043935 | 0.003832 | -0.008639 | 0.11898 | -0.13948 | 0.030224 | -0.35077 | -0.14301 | -0.005439 | -0.035366 | 0.31541 | 0.030166 | -0.15893 | 122.9984 | 122.9028 | 123.0725 | 66.7021 | -123.1699 | 122.8993 | 123.0725 | 122.8834 | 66.6965 | -123.3931
1340.8594 | 123.1659 | -66.7419 | 56.337 | 0.0046549 | -0.016761 | 0.00067514 | 0.053508 | -0.0050232 | 0.062503 | 0.0077831 | -0.0021983 | -0.0011965 | 0.058031 | 0.026455 | 0.058094 | -66.7244 | -0.030644 | -66.7368 | 56.2656 | 56.1746 | 56.3443 | -66.8604 | -66.7428 | -0.036271 | -66.791 | 56.1573 | 56.3351 | 56.1735 | -67.0836 | -0.11847 | -0.071401 | 0.017566 | 0.005095 | 0.12356 | -0.16237 | 0.007337 | -0.34162 | -0.17964 | -0.000863 | -0.049104 | 0.29251 | -0.001879 | -0.16351 | 123.0075 | 122.9165 | 123.0863 | 66.7113 | -123.1974 | 122.8993 | 123.077 | 122.9154 | 66.7057 | -123.4205
1341.7969 | 123.1567 | -66.7648 | 56.3095 | -0.010607 | -0.016761 | 0.00088894 | 0.053936 | -0.0054506 | 0.062076 | -0.015108 | -0.0021983 | -0.00098273 | 0.058031 | 0.026241 | 0.058522 | -66.7335 | -0.026065 | -66.7323 | 56.261 | 56.1563 | 56.3352 | -66.8513 | -66.7382 | -0.036271 | -66.7865 | 56.1711 | 56.3443 | 56.1735 | -67.0881 | -0.086419 | -0.048514 | 0.031298 | 0.032562 | 0.11898 | -0.15322 | 0.025646 | -0.32331 | -0.13844 | 0.026605 | -0.021637 | 0.30167 | 0.034744 | -0.13604 | 123.0258 | 122.9211 | 123.1 | 66.7388 | -123.1608 | 122.9359 | 123.1091 | 122.9383 | 66.7286 | -123.3976
1342.7969 | 123.2803 | -66.7236 | 56.2729 | -0.010607 | -0.016761 | 0.00088894 | 0.054149 | -0.0050232 | 0.062076 | 0.00015261 | -0.0021983 | -0.00098273 | 0.058245 | 0.026028 | 0.058308 | -66.729 | -0.030644 | -66.7368 | 56.2564 | 56.17 | 56.3443 | -66.8513 | -66.7382 | -0.031692 | -66.7956 | 56.1665 | 56.3397 | 56.178 | -67.0836 | -0.12762 | -0.016471 | -0.005323 | -0.013215 | 0.1144 | -0.10286 | 0.071424 | -0.35993 | -0.10639 | -0.014594 | -0.071993 | 0.28794 | 0.066787 | -0.094842 | 122.9801 | 122.8937 | 123.0679 | 66.693 | -123.1241 | 122.8901 | 123.0633 | 122.9017 | 66.6919 | -123.3564
1343.7969 | 123.1338 | -66.7648 | 56.3324 | -0.0029761 | -0.016547 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00055553 | 0.057817 | 0.026455 | 0.058308 | -66.7244 | -0.030644 | -66.746 | 56.2656 | 56.1792 | 56.3443 | -66.8604 | -66.7382 | -0.036271 | -66.7819 | 56.1573 | 56.3397 | 56.1735 | -67.0927 | -0.095576 | -0.066823 | 0.040455 | 0.018827 | 0.1144 | -0.15321 | 0.011915 | -0.32789 | -0.17506 | 0.026605 | -0.017058 | 0.31083 | 0.007278 | -0.15893 | 123.0304 | 122.944 | 123.1091 | 66.7342 | -123.1928 | 122.9222 | 123.1045 | 122.9383 | 66.7286 | -123.4251
1344.7969 | 123.2254 | -66.7374 | 56.3004 | 0.012286 | -0.016547 | 0.0011025 | 0.054363 | -0.0052368 | 0.062503 | 0.0077831 | -0.0017711 | -0.00055553 | 0.057817 | 0.025814 | 0.058308 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.3443 | -66.8604 | -66.7474 | -0.036271 | -66.7819 | 56.1757 | 56.3351 | 56.1597 | -67.079 | -0.12304 | -0.030202 | 0.00841 | -0.004061 | 0.11898 | -0.12575 | 0.043958 | -0.34162 | -0.1247 | -0.010019 | -0.044524 | 0.29709 | 0.034742 | -0.14062 | 123.0075 | 122.912 | 123.0817 | 66.7113 | -123.1608 | 122.913 | 123.0725 | 122.8971 | 66.7011 | -123.3793
1345.7969 | 123.1476 | -66.7831 | 56.337 | 0.0046549 | -0.016761 | 0.00088894 | 0.053722 | -0.0054506 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.058245 | 0.026455 | 0.058308 | -66.7335 | -0.030644 | -66.7414 | 56.2656 | 56.1746 | 56.3443 | -66.8558 | -66.7382 | -0.031692 | -66.7819 | 56.1665 | 56.3488 | 56.1735 | -67.0881 | -0.072688 | -0.071401 | 0.049608 | 0.041715 | 0.1144 | -0.16237 | 0.007337 | -0.305 | -0.17048 | 0.044915 | 0.001252 | 0.30625 | 0.011857 | -0.16351 | 123.0487 | 122.9577 | 123.1275 | 66.7525 | -123.1928 | 122.9496 | 123.132 | 122.9566 | 66.7514 | -123.4251
1346.7969 | 123.23 | -66.7191 | 56.2958 | 0.0046549 | -0.016547 | 0.0011025 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00055553 | 0.057817 | 0.026669 | 0.058522 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.17 | 56.3397 | -66.8558 | -66.7474 | -0.036271 | -66.7773 | 56.1711 | 56.3443 | 56.1597 | -67.0881 | -0.13678 | -0.030202 | -0.009901 | -0.022372 | 0.1144 | -0.12575 | 0.043957 | -0.36909 | -0.1247 | -0.02833 | -0.058256 | 0.31083 | 0.048477 | -0.13604 | 122.9846 | 122.8891 | 123.0588 | 66.6884 | -123.1516 | 122.8901 | 123.0633 | 122.8788 | 66.6828 | -123.3839
1347.8594 | 123.2162 | -66.7465 | 56.2958 | 0.012286 | -0.016547 | 0.00088894 | 0.053722 | -0.0050232 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058031 | 0.026241 | 0.058308 | -66.7335 | -0.021486 | -66.7368 | 56.2702 | 56.1654 | 56.3443 | -66.8604 | -66.7428 | -0.031692 | -66.7819 | 56.1711 | 56.3397 | 56.1597 | -67.0744 | -0.11389 | -0.025624 | 0.012987 | 0.009673 | 0.12356 | -0.13033 | 0.048536 | -0.32788 | -0.1247 | 0.003715 | -0.035369 | 0.29251 | 0.043899 | -0.13604 | 123.0167 | 122.912 | 123.0908 | 66.725 | -123.1562 | 122.9176 | 123.0862 | 122.9063 | 66.7148 | -123.3702
1348.7969 | 123.2529 | -66.7191 | 56.2683 | -0.018238 | -0.016761 | 0.00067514 | 0.054363 | -0.0050232 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057817 | 0.026241 | 0.058735 | -66.729 | -0.026065 | -66.7277 | 56.2702 | 56.1746 | 56.3397 | -66.8558 | -66.7474 | -0.031692 | -66.7865 | 56.1711 | 56.3443 | 56.1597 | -67.0881 | -0.13678 | 0.001841 | -0.009901 | -0.008637 | 0.12814 | -0.093706 | 0.071422 | -0.36909 | -0.097237 | -0.02833 | -0.067414 | 0.30167 | 0.075942 | -0.10858 | 122.9892 | 122.8937 | 123.0588 | 66.693 | -123.1241 | 122.8901 | 123.0633 | 122.8788 | 66.6874 | -123.3565
1349.8594 | 123.1659 | -66.7603 | 56.3324 | -0.0029761 | -0.016974 | 0.00067514 | 0.053722 | -0.0052368 | 0.062503 | -0.015108 | -0.0017711 | -0.00076913 | 0.058031 | 0.026882 | 0.058522 | -66.729 | -0.021486 | -66.7506 | 56.2702 | 56.1792 | 56.3443 | -66.8604 | -66.7382 | -0.036271 | -66.7773 | 56.1711 | 56.3351 | 56.1597 | -67.0927 | -0.10015 | -0.062245 | 0.031298 | 0.009671 | 0.10983 | -0.15321 | 0.011915 | -0.33247 | -0.16132 | 0.022027 | -0.017057 | 0.31541 | 0.002699 | -0.17267 | 123.0304 | 122.9394 | 123.1046 | 66.7388 | -123.1928 | 122.9313 | 123.0953 | 122.92 | 66.724 | -123.4251
1350.8125 | 123.2025 | -66.7374 | 56.3461 | -0.0029761 | -0.016761 | 0.00088894 | 0.053722 | -0.0052368 | 0.062717 | -0.0074779 | -0.0019847 | -0.00098273 | 0.058245 | 0.026455 | 0.058522 | -66.729 | -0.035222 | -66.7368 | 56.261 | 56.1563 | 56.3443 | -66.865 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3351 | 56.1689 | -67.0927 | -0.12762 | -0.085135 | 0.00841 | 0.000518 | 0.12814 | -0.18984 | -0.001818 | -0.35535 | -0.17506 | -0.00544 | -0.049103 | 0.30625 | -0.011034 | -0.17724 | 122.9984 | 122.8937 | 123.0817 | 66.7021 | -123.2111 | 122.9084 | 123.0725 | 122.9063 | 66.7057 | -123.4389
1351.7969 | 123.2758 | -66.7099 | 56.2775 | -0.010607 | -0.016761 | 0.00067514 | 0.053722 | -0.0052368 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058031 | 0.026455 | 0.058735 | -66.729 | -0.026065 | -66.7368 | 56.2656 | 56.1746 | 56.3443 | -66.8604 | -66.7382 | -0.036271 | -66.7865 | 56.1665 | 56.3443 | 56.1597 | -67.0836 | -0.15051 | -0.011892 | -0.019056 | -0.026948 | 0.12356 | -0.10286 | 0.066846 | -0.37366 | -0.11097 | -0.028327 | -0.076569 | 0.29709 | 0.066787 | -0.11773 | 122.9755 | 122.8845 | 123.0542 | 66.6838 | -123.1379 | 122.8764 | 123.0542 | 122.8696 | 66.6736 | -123.361
1352.8594 | 123.23 | -66.7145 | 56.2729 | 0.0046549 | -0.016974 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | -0.015108 | -0.0021983 | -0.00055553 | 0.058031 | 0.026455 | 0.057881 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.1746 | 56.3397 | -66.8558 | -66.7428 | -0.036271 | -66.7819 | 56.1665 | 56.3443 | 56.178 | -67.0836 | -0.14135 | -0.007314 | -0.014478 | -0.026949 | 0.1144 | -0.098283 | 0.066845 | -0.36908 | -0.10639 | -0.028328 | -0.067412 | 0.30167 | 0.071365 | -0.094842 | 122.9801 | 122.8891 | 123.0542 | 66.6838 | -123.1287 | 122.881 | 123.0587 | 122.8925 | 66.6782 | -123.3564
1353.7969 | 123.2437 | -66.7191 | 56.2912 | -0.0029761 | -0.016761 | 0.00088894 | 0.053508 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058031 | 0.026669 | 0.058735 | -66.729 | -0.026065 | -66.7323 | 56.261 | 56.1609 | 56.3397 | -66.8604 | -66.7474 | -0.027113 | -66.7956 | 56.1711 | 56.3443 | 56.1643 | -67.0836 | -0.14135 | -0.030204 | -0.009901 | -0.013215 | 0.12814 | -0.13033 | 0.048534 | -0.36451 | -0.12013 | -0.02833 | -0.076571 | 0.28794 | 0.053054 | -0.12689 | 122.9801 | 122.8799 | 123.0588 | 66.693 | -123.1516 | 122.8901 | 123.0633 | 122.8834 | 66.6919 | -123.3748
1354.8594 | 123.1293 | -66.7603 | 56.3278 | -0.0029761 | -0.017402 | 0.0011025 | 0.053722 | -0.0054506 | 0.062076 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058031 | 0.026241 | 0.058308 | -66.7244 | -0.026065 | -66.7414 | 56.2702 | 56.1654 | 56.3397 | -66.8604 | -66.7474 | -0.040849 | -66.7773 | 56.1665 | 56.3443 | 56.1735 | -67.0836 | -0.10015 | -0.057668 | 0.035877 | 0.018827 | 0.11898 | -0.16237 | 0.011913 | -0.32331 | -0.16132 | 0.012869 | -0.017057 | 0.30625 | 0.016433 | -0.15435 | 123.0304 | 122.9257 | 123.1 | 66.7342 | -123.1882 | 122.9267 | 123.1045 | 122.9337 | 66.7194 | -123.4114
1355.7969 | 123.1247 | -66.7511 | 56.337 | -0.018238 | -0.016761 | 0.0011025 | 0.054149 | -0.0054506 | 0.062289 | 0.0077831 | -0.0021983 | -0.00055553 | 0.058031 | 0.026455 | 0.058308 | -66.7244 | -0.030644 | -66.7414 | 56.2656 | 56.1654 | 56.3489 | -66.8604 | -66.7382 | -0.036271 | -66.7865 | 56.1711 | 56.3397 | 56.1689 | -67.0836 | -0.10931 | -0.071401 | 0.026722 | 0.009672 | 0.11898 | -0.17153 | 0.011915 | -0.33246 | -0.1659 | 0.012872 | -0.03537 | 0.29709 | 0.0027 | -0.16809 | 123.0167 | 122.9165 | 123.1 | 66.7205 | -123.1974 | 122.9222 | 123.0908 | 122.92 | 66.7148 | -123.4205
1356.7969 | 123.2437 | -66.7191 | 56.2729 | -0.0029761 | -0.016547 | 0.0011025 | 0.053722 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00034193 | 0.058031 | 0.026241 | 0.058308 | -66.729 | -0.030644 | -66.7368 | 56.261 | 56.1654 | 56.3397 | -66.8513 | -66.7382 | -0.036271 | -66.7865 | 56.1757 | 56.3443 | 56.178 | -67.079 | -0.1322 | -0.011893 | -0.009901 | -0.017793 | 0.1144 | -0.10744 | 0.066845 | -0.35993 | -0.097235 | -0.019172 | -0.067414 | 0.29251 | 0.071365 | -0.094842 | 122.9801 | 122.8845 | 123.0588 | 66.6884 | -123.1241 | 122.8947 | 123.0633 | 122.8971 | 66.6828 | -123.3519
1357.8594 | 123.1888 | -66.7374 | 56.3141 | -0.0029761 | -0.016761 | 0.00067514 | 0.053508 | -0.0050232 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057604 | 0.026669 | 0.058522 | -66.7198 | -0.030644 | -66.7323 | 56.2656 | 56.17 | 56.3397 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3443 | 56.1735 | -67.0744 | -0.11846 | -0.048513 | 0.017567 | 0.005096 | 0.12356 | -0.14406 | 0.025646 | -0.33704 | -0.14301 | -0.00544 | -0.049103 | 0.28794 | 0.030166 | -0.14062 | 123.0029 | 122.9074 | 123.0771 | 66.7067 | -123.1699 | 122.9084 | 123.0816 | 122.9108 | 66.7057 | -123.3885
1358.7969 | 123.2437 | -66.7145 | 56.2775 | -0.0029761 | -0.016333 | 0.00088894 | 0.053936 | -0.0054506 | 0.062503 | 0.00015261 | -0.0019847 | -0.00034193 | 0.057817 | 0.026455 | 0.058094 | -66.7335 | -0.030644 | -66.7368 | 56.2656 | 56.1654 | 56.3397 | -66.8513 | -66.7291 | -0.036271 | -66.791 | 56.1665 | 56.3397 | 56.1689 | -67.0836 | -0.13677 | -0.011892 | -0.019056 | -0.02237 | 0.1144 | -0.11202 | 0.062267 | -0.36908 | -0.11097 | -0.014592 | -0.076569 | 0.29251 | 0.062209 | -0.10858 | 122.9801 | 122.8799 | 123.0542 | 66.6838 | -123.1287 | 122.881 | 123.0542 | 122.8834 | 66.6782 | -123.361
1359.7969 | 123.2666 | -66.7099 | 56.2637 | -0.010607 | -0.016547 | 0.00088894 | 0.053722 | -0.0054506 | 0.062076 | -0.0074779 | -0.0019847 | -0.00034193 | 0.05739 | 0.026669 | 0.058522 | -66.7244 | -0.026065 | -66.7277 | 56.2656 | 56.17 | 56.3443 | -66.8604 | -66.7382 | -0.031692 | -66.791 | 56.1665 | 56.3397 | 56.1597 | -67.0927 | -0.15051 | 0.001841 | -0.014477 | -0.017792 | 0.13272 | -0.093707 | 0.080579 | -0.38282 | -0.097237 | -0.028327 | -0.081147 | 0.30167 | 0.075942 | -0.104 | 122.9755 | 122.8799 | 123.0542 | 66.6838 | -123.1241 | 122.8764 | 123.0496 | 122.8696 | 66.6782 | -123.3565
1360.7969 | 123.1613 | -66.7603 | 56.3049 | 0.0046549 | -0.016761 | 0.00046154 | 0.053936 | -0.0052368 | 0.062076 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057817 | 0.026455 | 0.057881 | -66.7244 | -0.026065 | -66.7277 | 56.261 | 56.1838 | 56.3397 | -66.865 | -66.7428 | -0.036271 | -66.7865 | 56.1711 | 56.3443 | 56.178 | -67.0698 | -0.10473 | -0.043937 | 0.035877 | 0.032562 | 0.13729 | -0.12117 | 0.034801 | -0.30957 | -0.13386 | 0.017448 | -0.026215 | 0.28336 | 0.039321 | -0.12689 | 123.0212 | 122.944 | 123.1 | 66.7342 | -123.1699 | 122.9313 | 123.1045 | 122.9383 | 66.724 | -123.3748
1361.7969 | 123.262 | -66.7191 | 56.3004 | -0.0029761 | -0.016761 | 0.0011025 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058031 | 0.026241 | 0.058308 | -66.7427 | -0.016908 | -66.7277 | 56.261 | 56.1746 | 56.3397 | -66.8558 | -66.7428 | -0.036271 | -66.7819 | 56.1665 | 56.3488 | 56.1552 | -67.0973 | -0.13678 | -0.039359 | -0.023636 | -0.008637 | 0.12814 | -0.12575 | 0.039379 | -0.37824 | -0.13386 | -0.023751 | -0.062835 | 0.31541 | 0.048478 | -0.1452 | 122.9801 | 122.8937 | 123.0588 | 66.7021 | -123.1562 | 122.8856 | 123.0679 | 122.8742 | 66.6828 | -123.3977
1362.7969 | 123.2895 | -66.7007 | 56.2912 | 0.0046549 | -0.016974 | 0.00067514 | 0.053722 | -0.0054506 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.058245 | 0.026669 | 0.058522 | -66.7198 | -0.030644 | -66.7368 | 56.261 | 56.1654 | 56.3443 | -66.8513 | -66.7382 | -0.036271 | -66.7956 | 56.1665 | 56.3443 | 56.1735 | -67.0881 | -0.15051 | -0.030204 | -0.019054 | -0.036103 | 0.1144 | -0.12575 | 0.053113 | -0.3874 | -0.1247 | -0.037482 | -0.094881 | 0.29251 | 0.053054 | -0.11773 | 122.9617 | 122.8662 | 123.0451 | 66.6701 | -123.1424 | 122.8672 | 123.045 | 122.8742 | 66.6645 | -123.3793
1363.8594 | 123.2574 | -66.7145 | 56.3278 | 0.012286 | -0.016974 | 0.0011025 | 0.053722 | -0.0052368 | 0.062289 | 0.00015261 | -0.0017711 | -0.00098273 | 0.057817 | 0.026455 | 0.058735 | -66.7244 | -0.026065 | -66.7414 | 56.261 | 56.1563 | 56.3397 | -66.8604 | -66.7428 | -0.036271 | -66.7819 | 56.1711 | 56.3488 | 56.1643 | -67.079 | -0.14593 | -0.066825 | -0.009899 | -0.026949 | 0.11898 | -0.17153 | 0.011913 | -0.3645 | -0.15675 | -0.028328 | -0.067412 | 0.29709 | 0.021012 | -0.16351 | 122.9755 | 122.8708 | 123.0542 | 66.6884 | -123.1882 | 122.8856 | 123.0633 | 122.8788 | 66.6782 | -123.4068
1364.7969 | 123.2208 | -66.7007 | 56.3187 | -0.0029761 | -0.016761 | 0.00088894 | 0.053936 | -0.0052368 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.026669 | 0.058522 | -66.729 | -0.030644 | -66.7368 | 56.2656 | 56.1563 | 56.3443 | -66.8558 | -66.7382 | -0.031692 | -66.791 | 56.1665 | 56.3443 | 56.178 | -67.0836 | -0.15508 | -0.053091 | -0.028211 | -0.036103 | 0.11898 | -0.16238 | 0.025647 | -0.38282 | -0.15217 | -0.037482 | -0.090302 | 0.29251 | 0.025588 | -0.14062 | 122.9663 | 122.857 | 123.0451 | 66.6701 | -123.1745 | 122.8672 | 123.045 | 122.8788 | 66.6691 | -123.4022
1365.7969 | 123.2025 | -66.6779 | 56.3324 | -0.0029761 | -0.016974 | 0.0011025 | 0.053936 | -0.0052368 | 0.062289 | 0.0077831 | -0.0017711 | -0.00098273 | 0.058245 | 0.026669 | 0.058308 | -66.729 | -0.026065 | -66.7414 | 56.261 | 56.17 | 56.3397 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1665 | 56.3443 | 56.1689 | -67.0836 | -0.17797 | -0.071402 | -0.0511 | -0.063571 | 0.1144 | -0.16237 | 0.007336 | -0.40571 | -0.1659 | -0.06495 | -0.10861 | 0.29709 | 0.011856 | -0.16351 | 122.9389 | 122.8479 | 123.0176 | 66.6518 | -123.1882 | 122.8444 | 123.0221 | 122.8467 | 66.6462 | -123.416
1366.8594 | 123.2803 | -66.6916 | 56.282 | -0.0029761 | -0.016547 | 0.0011025 | 0.054149 | -0.0052368 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057817 | 0.026455 | 0.058308 | -66.729 | -0.035222 | -66.7323 | 56.2656 | 56.1746 | 56.3397 | -66.8604 | -66.7382 | -0.036271 | -66.7819 | 56.1665 | 56.3397 | 56.1689 | -67.0836 | -0.16882 | -0.016469 | -0.037367 | -0.040681 | 0.12814 | -0.10744 | 0.05769 | -0.39197 | -0.11555 | -0.046638 | -0.090301 | 0.30167 | 0.057632 | -0.11315 | 122.9572 | 122.8662 | 123.0313 | 66.6564 | -123.1425 | 122.8581 | 123.0313 | 122.8605 | 66.6553 | -123.3656
1367.7969 | 123.2666 | -66.7099 | 56.2592 | 0.012286 | -0.016974 | 0.00067514 | 0.053936 | -0.0052368 | 0.062076 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058031 | 0.026669 | 0.058308 | -66.729 | -0.026065 | -66.7414 | 56.261 | 56.1746 | 56.3443 | -66.8513 | -66.7382 | -0.031692 | -66.7865 | 56.1665 | 56.3443 | 56.1506 | -67.0881 | -0.14135 | 0.00184 | -0.019056 | -0.031527 | 0.10982 | -0.08455 | 0.085157 | -0.37824 | -0.092659 | -0.028327 | -0.076569 | 0.30167 | 0.085098 | -0.10858 | 122.9709 | 122.8845 | 123.0542 | 66.6838 | -123.1104 | 122.8764 | 123.0542 | 122.8605 | 66.6782 | -123.3473
1368.7969 | 123.2849 | -66.6595 | 56.3324 | 0.0046549 | -0.017188 | 0.0015299 | 0.053936 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058031 | 0.026455 | 0.058735 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.1746 | 56.3443 | -66.8604 | -66.7428 | -0.031692 | -66.7865 | 56.1573 | 56.3488 | 56.1689 | -67.0881 | -0.20086 | -0.071402 | -0.06941 | -0.081881 | 0.11898 | -0.15779 | 0.011915 | -0.42859 | -0.17506 | -0.08326 | -0.12692 | 0.30167 | 0.016435 | -0.16351 | 122.9205 | 122.8342 | 123.0039 | 66.6289 | -123.1928 | 122.8169 | 123.0084 | 122.8284 | 66.6279 | -123.4205
1369.7969 | 123.2071 | -66.7191 | 56.2866 | -0.010607 | -0.016974 | 0.00067514 | 0.054149 | -0.0054506 | 0.062289 | 0.015414 | -0.0021983 | -0.00098273 | 0.058245 | 0.026882 | 0.058308 | -66.729 | -0.035222 | -66.746 | 56.261 | 56.1654 | 56.3352 | -66.8558 | -66.7474 | -0.036271 | -66.7865 | 56.1757 | 56.3534 | 56.1689 | -67.0927 | -0.13678 | -0.025626 | -0.009901 | -0.02695 | 0.10983 | -0.12117 | 0.048534 | -0.37367 | -0.11097 | -0.02833 | -0.067414 | 0.30625 | 0.066789 | -0.11773 | 122.9801 | 122.8845 | 123.0542 | 66.6838 | -123.1425 | 122.8947 | 123.0725 | 122.8879 | 66.6828 | -123.3793
1370.8125 | 123.2574 | -66.7236 | 56.2775 | 0.0046549 | -0.017188 | 0.00088894 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.05739 | 0.026669 | 0.058308 | -66.7335 | -0.026065 | -66.7368 | 56.2656 | 56.17 | 56.3443 | -66.865 | -66.7474 | -0.027113 | -66.791 | 56.1711 | 56.3488 | 56.1689 | -67.0881 | -0.14135 | -0.011892 | -0.009901 | -0.013215 | 0.12814 | -0.10744 | 0.066846 | -0.36451 | -0.10639 | -0.023752 | -0.067414 | 0.29709 | 0.071366 | -0.10858 | 122.9892 | 122.8937 | 123.0679 | 66.6976 | -123.1425 | 122.8947 | 123.0725 | 122.8925 | 66.6965 | -123.3656
1371.8594 | 123.1934 | -66.7282 | 56.3553 | -0.0029761 | -0.016974 | 0.00067514 | 0.053722 | -0.0056642 | 0.062717 | -0.0074779 | -0.0024119 | -0.00098273 | 0.058031 | 0.026455 | 0.058522 | -66.7244 | -0.026065 | -66.7414 | 56.261 | 56.1792 | 56.3443 | -66.8604 | -66.752 | -0.031692 | -66.7865 | 56.1757 | 56.3397 | 56.178 | -67.0881 | -0.1322 | -0.094291 | 0.003833 | -0.013217 | 0.11898 | -0.1761 | -0.010974 | -0.35993 | -0.17963 | -0.023753 | -0.058259 | 0.30167 | -0.015611 | -0.17724 | 122.9892 | 122.9074 | 123.0725 | 66.7021 | -123.2157 | 122.9039 | 123.0679 | 122.9063 | 66.6965 | -123.4434
1372.7969 | 123.2208 | -66.7099 | 56.2958 | 0.0046549 | -0.016974 | 0.00088894 | 0.054149 | -0.0054506 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057817 | 0.026882 | 0.058308 | -66.7335 | -0.035222 | -66.7414 | 56.261 | 56.17 | 56.3443 | -66.8513 | -66.7428 | -0.031692 | -66.791 | 56.1757 | 56.3488 | 56.178 | -67.0927 | -0.14135 | -0.034781 | -0.023634 | -0.031527 | 0.10982 | -0.12575 | 0.048536 | -0.38282 | -0.12012 | -0.032906 | -0.081147 | 0.30167 | 0.053056 | -0.11773 | 122.9709 | 122.8799 | 123.0542 | 66.6747 | -123.147 | 122.8856 | 123.0587 | 122.8879 | 66.6782 | -123.3885
1373.8594 | 123.2254 | -66.7007 | 56.3049 | -0.0029761 | -0.016974 | 0.00088894 | 0.054149 | -0.0052368 | 0.062717 | 0.0077831 | -0.0024119 | -0.0011965 | 0.057817 | 0.026669 | 0.058094 | -66.7244 | -0.030644 | -66.7506 | 56.261 | 56.1792 | 56.3489 | -66.8558 | -66.7382 | -0.036271 | -66.7865 | 56.1619 | 56.3443 | 56.178 | -67.0836 | -0.15508 | -0.043937 | -0.023632 | -0.049838 | 0.10525 | -0.12575 | 0.043958 | -0.38282 | -0.14301 | -0.037482 | -0.085724 | 0.29709 | 0.039321 | -0.12689 | 122.9617 | 122.8799 | 123.0496 | 66.6701 | -123.1608 | 122.8627 | 123.045 | 122.8788 | 66.6645 | -123.3885
1374.7969 | 123.2941 | -66.6962 | 56.3232 | -0.010607 | -0.016761 | 0.0011025 | 0.053722 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057604 | 0.027096 | 0.058308 | -66.7335 | -0.030644 | -66.7506 | 56.2702 | 56.17 | 56.3489 | -66.8513 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3534 | 56.178 | -67.0836 | -0.15508 | -0.05309 | -0.037367 | -0.054416 | 0.10067 | -0.15322 | 0.025648 | -0.38739 | -0.15217 | -0.046639 | -0.090302 | 0.29709 | 0.030168 | -0.1452 | 122.9663 | 122.8662 | 123.0451 | 66.6655 | -123.1745 | 122.8672 | 123.0496 | 122.8742 | 66.6645 | -123.4068
1375.875 | 123.1201 | -66.7145 | 56.337 | 0.012286 | -0.017188 | 0.00088894 | 0.053936 | -0.0054506 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057604 | 0.026882 | 0.058522 | -66.7335 | -0.035222 | -66.7368 | 56.2656 | 56.1654 | 56.3352 | -66.8604 | -66.7428 | -0.031692 | -66.7819 | 56.1619 | 56.3443 | 56.1826 | -67.0836 | -0.14593 | -0.071401 | -0.019056 | -0.02237 | 0.12356 | -0.17153 | -0.00182 | -0.36908 | -0.17506 | -0.028328 | -0.067412 | 0.30167 | 0.007278 | -0.15435 | 122.9801 | 122.8799 | 123.0496 | 66.6793 | -123.1974 | 122.8764 | 123.0587 | 122.8971 | 66.6828 | -123.4205
1376.7969 | 123.2162 | -66.7191 | 56.3004 | -0.010607 | -0.016974 | 0.00046154 | 0.054149 | -0.0052368 | 0.062289 | 0.00015261 | -0.0017711 | -0.00098273 | 0.057817 | 0.026669 | 0.058735 | -66.7335 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.3397 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1757 | 56.3488 | 56.1643 | -67.0836 | -0.14135 | -0.030202 | -0.014479 | -0.022372 | 0.11898 | -0.12575 | 0.039379 | -0.36451 | -0.1247 | -0.02833 | -0.067414 | 0.29709 | 0.048478 | -0.13604 | 122.9892 | 122.8937 | 123.0588 | 66.693 | -123.1608 | 122.8947 | 123.0679 | 122.8834 | 66.6828 | -123.3839
1377.7969 | 123.1934 | -66.7419 | 56.3232 | -0.0029761 | -0.017188 | 0.00067514 | 0.053936 | -0.0052368 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.058031 | 0.026882 | 0.058308 | -66.7244 | -0.035222 | -66.7506 | 56.2702 | 56.17 | 56.3397 | -66.865 | -66.7474 | -0.031692 | -66.7865 | 56.1711 | 56.3488 | 56.1643 | -67.0881 | -0.12304 | -0.05309 | 0.017566 | -0.00864 | 0.1144 | -0.15322 | 0.016491 | -0.3462 | -0.15217 | -0.005442 | -0.044526 | 0.30167 | 0.02559 | -0.15893 | 123.0121 | 122.912 | 123.0817 | 66.7067 | -123.1882 | 122.913 | 123.0908 | 122.9063 | 66.7103 | -123.4114
1378.7969 | 123.2117 | -66.7236 | 56.3416 | 0.0046549 | -0.016974 | 0.00088894 | 0.054149 | -0.0052368 | 0.06293 | 0.015414 | -0.0017711 | -0.0011965 | 0.058245 | 0.027096 | 0.058308 | -66.7335 | -0.021486 | -66.746 | 56.2564 | 56.17 | 56.3489 | -66.8558 | -66.7382 | -0.036271 | -66.791 | 56.1757 | 56.3534 | 56.1643 | -67.0881 | -0.1322 | -0.085136 | -0.009901 | -0.022372 | 0.10983 | -0.17153 | 0.007337 | -0.36451 | -0.1659 | -0.014594 | -0.067414 | 0.29709 | 0.011857 | -0.17724 | 122.9801 | 122.8937 | 123.0725 | 66.7021 | -123.1974 | 122.8993 | 123.077 | 122.8879 | 66.6874 | -123.4297
1379.9375 | 123.1293 | -66.7465 | 56.3416 | 0.0046549 | -0.017402 | 0.00067514 | 0.053722 | -0.0052368 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.058031 | 0.026669 | 0.058308 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1654 | 56.3443 | -66.865 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3488 | 56.1552 | -67.0881 | -0.11847 | -0.071401 | 0.012987 | 0.000516 | 0.11898 | -0.17611 | 0.002759 | -0.34162 | -0.17506 | 0.003715 | -0.044526 | 0.29709 | 0.007279 | -0.1864 | 123.0167 | 122.912 | 123.0908 | 66.7159 | -123.2065 | 122.913 | 123.0954 | 122.9017 | 66.7103 | -123.4297
1381.1719 | 123.1888 | -66.7282 | 56.3141 | -0.010607 | -0.016974 | 0.00046154 | 0.053508 | -0.0052368 | 0.062503 | -0.015108 | -0.0024119 | -0.00098273 | 0.057604 | 0.026882 | 0.058308 | -66.7335 | -0.026065 | -66.746 | 56.261 | 56.1792 | 56.3489 | -66.8513 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3488 | 56.1689 | -67.0744 | -0.12304 | -0.053092 | -0.005324 | -0.017795 | 0.10525 | -0.1349 | 0.034803 | -0.34619 | -0.14759 | -0.019175 | -0.05368 | 0.29251 | 0.034745 | -0.1452 | 122.9892 | 122.9074 | 123.0771 | 66.7021 | -123.1653 | 122.8947 | 123.077 | 122.8971 | 66.6919 | -123.3885
1382.4688 | 123.1796 | -66.7099 | 56.369 | -0.010607 | -0.016974 | 0.0011025 | 0.053936 | -0.0054506 | 0.062717 | -0.0074779 | -0.0021983 | -0.00076913 | 0.058031 | 0.026669 | 0.057881 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.17 | 56.3397 | -66.8558 | -66.7428 | -0.027113 | -66.7865 | 56.1665 | 56.3397 | 56.1826 | -67.0836 | -0.14593 | -0.10802 | -0.019056 | -0.031527 | 0.1144 | -0.19899 | -0.029286 | -0.37366 | -0.20252 | -0.032906 | -0.076569 | 0.29709 | -0.029344 | -0.18639 | 122.9709 | 122.8799 | 123.0496 | 66.6793 | -123.2248 | 122.8764 | 123.0496 | 122.8925 | 66.6828 | -123.4526
1383.9219 | 123.1934 | -66.7145 | 56.3416 | -0.0029761 | -0.017188 | 0.00088894 | 0.053722 | -0.0052368 | 0.062289 | 0.015414 | -0.0024119 | -0.00098273 | 0.057604 | 0.026669 | 0.058094 | -66.7244 | -0.021486 | -66.746 | 56.2656 | 56.17 | 56.3443 | -66.8696 | -66.7428 | -0.036271 | -66.7819 | 56.1711 | 56.3488 | 56.1918 | -67.0836 | -0.15509 | -0.075979 | -0.009899 | -0.031527 | 0.12356 | -0.17153 | 0.002759 | -0.36908 | -0.17048 | -0.028328 | -0.067412 | 0.30167 | 0.007279 | -0.14977 | 122.9801 | 122.8845 | 123.0588 | 66.693 | -123.2111 | 122.8856 | 123.0633 | 122.9063 | 66.6782 | -123.4251
1384.4688 | 123.1567 | -66.7419 | 56.3141 | 0.0046549 | -0.017188 | 0.0011025 | 0.053508 | -0.0056642 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058031 | 0.026882 | 0.058522 | -66.729 | -0.021486 | -66.7506 | 56.2702 | 56.1792 | 56.3535 | -66.865 | -66.752 | -0.036271 | -66.7773 | 56.1711 | 56.3397 | 56.1826 | -67.0836 | -0.12304 | -0.043935 | 0.012987 | -0.00864 | 0.1144 | -0.1349 | 0.039382 | -0.34162 | -0.14301 | -0.01002 | -0.035368 | 0.30625 | 0.025588 | -0.13146 | 123.0121 | 122.9211 | 123.0954 | 66.7205 | -123.1791 | 122.913 | 123.0816 | 122.9246 | 66.7057 | -123.3976
1386.5 | 123.1796 | -66.7007 | 56.3324 | -0.0029761 | -0.017402 | 0.00088894 | 0.053722 | -0.0056642 | 0.06293 | 0.015414 | -0.0019847 | -0.00076913 | 0.057817 | 0.026882 | 0.058522 | -66.7335 | -0.021486 | -66.746 | 56.2702 | 56.1792 | 56.3626 | -66.8558 | -66.752 | -0.022535 | -66.7865 | 56.1665 | 56.3488 | 56.178 | -67.0881 | -0.15508 | -0.062245 | -0.032789 | -0.04526 | 0.10983 | -0.15321 | 0.030229 | -0.3874 | -0.1659 | -0.051218 | -0.085724 | 0.30167 | 0.016435 | -0.15435 | 122.9709 | 122.8799 | 123.0634 | 66.6793 | -123.1882 | 122.8672 | 123.0496 | 122.8788 | 66.6782 | -123.4205
1387.5938 | 123.2117 | -66.7374 | 56.3049 | 0.0046549 | -0.017402 | 0.00067514 | 0.053722 | -0.0054506 | 0.062503 | -0.0074779 | -0.0019847 | -0.00076913 | 0.057817 | 0.027096 | 0.058308 | -66.7335 | -0.026065 | -66.7506 | 56.2656 | 56.1838 | 56.3489 | -66.8558 | -66.7474 | -0.027113 | -66.7819 | 56.1665 | 56.3488 | 56.1826 | -67.079 | -0.11846 | -0.039358 | 0.003832 | -0.013217 | 0.10525 | -0.12117 | 0.043958 | -0.34162 | -0.13844 | -0.010019 | -0.044524 | 0.29709 | 0.0439 | -0.12231 | 123.0029 | 122.9211 | 123.0863 | 66.7113 | -123.1608 | 122.9039 | 123.0862 | 122.92 | 66.7103 | -123.3839
1388.4375 | 123.1567 | -66.7419 | 56.3187 | -0.010607 | -0.017615 | 0.00088894 | 0.053722 | -0.0056642 | 0.062717 | 0.00015261 | -0.0026255 | -0.0014101 | 0.057817 | 0.02731 | 0.058308 | -66.729 | -0.026065 | -66.746 | 56.2702 | 56.1746 | 56.3489 | -66.8604 | -66.7428 | -0.031692 | -66.7865 | 56.1619 | 56.3443 | 56.178 | -67.0927 | -0.11847 | -0.048513 | 0.012987 | -0.004062 | 0.1144 | -0.14406 | 0.030225 | -0.35078 | -0.15675 | -0.000863 | -0.044526 | 0.30625 | 0.025588 | -0.14062 | 123.0121 | 122.9165 | 123.0908 | 66.7159 | -123.1791 | 122.9039 | 123.0862 | 122.92 | 66.7103 | -123.4114
1392.9062 | 123.1613 | -66.7282 | 56.3553 | -0.0029761 | -0.017188 | 0.0011025 | 0.053722 | -0.0054506 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.058245 | 0.026882 | 0.058308 | -66.7198 | -0.021486 | -66.7414 | 56.2702 | 56.1792 | 56.3535 | -66.8558 | -66.7428 | -0.027113 | -66.7819 | 56.1665 | 56.3443 | 56.178 | -67.0881 | -0.12762 | -0.085134 | 0.008411 | -0.013217 | 0.1144 | -0.1761 | -0.001817 | -0.35993 | -0.18879 | -0.014596 | -0.05368 | 0.30625 | -0.011033 | -0.17724 | 122.9984 | 122.9074 | 123.0817 | 66.7067 | -123.2111 | 122.8947 | 123.0725 | 122.9063 | 66.7011 | -123.4434
1393.5156 | 123.1522 | -66.7419 | 56.3004 | -0.0029761 | -0.017615 | 0.00046154 | 0.053508 | -0.0056642 | 0.062503 | 0.015414 | -0.0019847 | -0.00098273 | 0.058031 | 0.026882 | 0.058522 | -66.729 | -0.026065 | -66.7368 | 56.261 | 56.17 | 56.3535 | -66.865 | -66.7428 | -0.036271 | -66.7865 | 56.1665 | 56.3534 | 56.1643 | -67.0881 | -0.12304 | -0.039359 | 0.012987 | 0.005095 | 0.12814 | -0.13033 | 0.053115 | -0.3462 | -0.13386 | -0.000863 | -0.044526 | 0.30167 | 0.053056 | -0.13604 | 123.0029 | 122.912 | 123.0954 | 66.7159 | -123.1653 | 122.9084 | 123.0954 | 122.9063 | 66.7057 | -123.3885
1394.0625 | 123.1705 | -66.7236 | 56.3416 | 0.0046549 | -0.017615 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058031 | 0.026669 | 0.058308 | -66.7198 | -0.026065 | -66.7323 | 56.2656 | 56.1563 | 56.3443 | -66.8696 | -66.752 | -0.022535 | -66.7773 | 56.1665 | 56.3488 | 56.1918 | -67.079 | -0.14593 | -0.075979 | 0.003834 | -0.008637 | 0.1373 | -0.18526 | 0.002759 | -0.35535 | -0.17506 | -0.02833 | -0.053678 | 0.30167 | 0.007279 | -0.14977 | 122.9892 | 122.8799 | 123.0679 | 66.6976 | -123.2111 | 122.8901 | 123.0725 | 122.9154 | 66.7011 | -123.4205
1394.7969 | 123.1979 | -66.7282 | 56.2958 | -0.0029761 | -0.017188 | 0.00067514 | 0.053508 | -0.0054506 | 0.062717 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058031 | 0.026882 | 0.058308 | -66.729 | -0.021486 | -66.7414 | 56.2702 | 56.1883 | 56.3489 | -66.8604 | -66.7474 | -0.027113 | -66.7819 | 56.1711 | 56.358 | 56.1689 | -67.0836 | -0.1322 | -0.025624 | -0.000746 | -0.013217 | 0.11898 | -0.10743 | 0.053114 | -0.35535 | -0.1247 | -0.019175 | -0.05368 | 0.30167 | 0.062213 | -0.12689 | 122.9984 | 122.9166 | 123.0771 | 66.7067 | -123.1562 | 122.8993 | 123.0862 | 122.8971 | 66.7011 | -123.3793
1395.7969 | 123.2208 | -66.7236 | 56.2729 | -0.0029761 | -0.017188 | 0.00067514 | 0.053936 | -0.0052368 | 0.062076 | -0.0074779 | -0.0021983 | -0.00098273 | 0.057604 | 0.026669 | 0.058308 | -66.729 | -0.021486 | -66.746 | 56.2656 | 56.1746 | 56.3443 | -66.8558 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3488 | 56.1735 | -67.0881 | -0.1322 | -0.007314 | -0.005323 | -0.022372 | 0.10983 | -0.098283 | 0.071424 | -0.36451 | -0.10639 | -0.019173 | -0.067414 | 0.29709 | 0.075944 | -0.09942 | 122.9892 | 122.8982 | 123.0679 | 66.7021 | -123.1287 | 122.8901 | 123.0725 | 122.8971 | 66.6874 | -123.361
1396.7969 | 123.2803 | -66.6779 | 56.3049 | -0.0029761 | -0.017615 | 0.0011025 | 0.053936 | -0.0054506 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058031 | 0.026882 | 0.057667 | -66.7381 | -0.035222 | -66.7414 | 56.2564 | 56.1746 | 56.3397 | -66.8558 | -66.7428 | -0.031692 | -66.7819 | 56.1757 | 56.3443 | 56.1735 | -67.0881 | -0.17797 | -0.048515 | -0.060256 | -0.063571 | 0.1144 | -0.13033 | 0.034801 | -0.41028 | -0.12928 | -0.06495 | -0.10403 | 0.30625 | 0.039321 | -0.13146 | 122.9343 | 122.8525 | 123.0176 | 66.6426 | -123.1608 | 122.8535 | 123.0221 | 122.8513 | 66.6462 | -123.3931
1397.7969 | 123.2117 | -66.7191 | 56.2958 | -0.0029761 | -0.017402 | 0.00046154 | 0.053936 | -0.0056642 | 0.06293 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057817 | 0.027096 | 0.058308 | -66.7381 | -0.035222 | -66.746 | 56.2702 | 56.1792 | 56.3443 | -66.8604 | -66.7382 | -0.027113 | -66.7865 | 56.1711 | 56.3488 | 56.178 | -67.0927 | -0.14135 | -0.025624 | -0.019057 | -0.02695 | 0.1144 | -0.11659 | 0.048536 | -0.37367 | -0.1247 | -0.019172 | -0.067414 | 0.30625 | 0.053056 | -0.11773 | 122.9892 | 122.8982 | 123.0634 | 66.6838 | -123.1562 | 122.8901 | 123.0679 | 122.8971 | 66.6919 | -123.3885
1398.7969 | 123.2483 | -66.7007 | 56.3004 | -0.0029761 | -0.017402 | 0.00088894 | 0.054149 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00098273 | 0.058245 | 0.027096 | 0.058308 | -66.729 | -0.026065 | -66.7506 | 56.2702 | 56.1792 | 56.3443 | -66.8696 | -66.7382 | -0.022535 | -66.7865 | 56.1665 | 56.3488 | 56.1643 | -67.0881 | -0.16882 | -0.030202 | -0.028211 | -0.049838 | 0.11898 | -0.12117 | 0.043958 | -0.3874 | -0.13386 | -0.037482 | -0.085724 | 0.30167 | 0.048478 | -0.13604 | 122.9709 | 122.8799 | 123.0451 | 66.6747 | -123.1699 | 122.8672 | 123.0496 | 122.8651 | 66.6782 | -123.3885
1399.7969 | 123.2529 | -66.7236 | 56.3187 | 0.0046549 | -0.017402 | 0.0011025 | 0.053936 | -0.0054506 | 0.062717 | 0.0077831 | -0.0019847 | -0.00098273 | 0.057817 | 0.02731 | 0.057881 | -66.7381 | -0.026065 | -66.7552 | 56.261 | 56.17 | 56.3489 | -66.8467 | -66.7428 | -0.031692 | -66.7819 | 56.1711 | 56.3488 | 56.1506 | -67.0836 | -0.12304 | -0.05767 | -0.014479 | -0.031528 | 0.091511 | -0.14864 | 0.030225 | -0.35993 | -0.14759 | -0.019173 | -0.058257 | 0.30167 | 0.030167 | -0.16809 | 122.9846 | 122.8937 | 123.0725 | 66.6976 | -123.1653 | 122.8947 | 123.0725 | 122.8742 | 66.6919 | -123.4022
1400.7969 | 123.3078 | -66.6779 | 56.3232 | -0.018238 | -0.017188 | 0.00088894 | 0.054149 | -0.0050232 | 0.062289 | 0.0077831 | -0.0021983 | -0.0011965 | 0.05739 | 0.02731 | 0.058094 | -66.729 | -0.026065 | -66.746 | 56.2656 | 56.1838 | 56.3397 | -66.8558 | -66.7474 | -0.036271 | -66.791 | 56.1711 | 56.3443 | 56.1643 | -67.0881 | -0.17797 | -0.057668 | -0.0511 | -0.068149 | 0.10983 | -0.13948 | 0.016491 | -0.41028 | -0.15217 | -0.069529 | -0.11319 | 0.29709 | 0.021011 | -0.15893 | 122.9434 | 122.8616 | 123.0176 | 66.6518 | -123.1791 | 122.8489 | 123.0221 | 122.8422 | 66.6416 | -123.4114
1401.8594 | 123.2529 | -66.7007 | 56.2912 | 0.0046549 | -0.017402 | 0.00088894 | 0.054149 | -0.0056642 | 0.062503 | 0.015414 | -0.0021983 | -0.00076913 | 0.058031 | 0.026882 | 0.058094 | -66.729 | -0.026065 | -66.746 | 56.261 | 56.1838 | 56.3443 | -66.8558 | -66.7428 | -0.027113 | -66.7865 | 56.1665 | 56.3397 | 56.1552 | -67.079 | -0.15508 | -0.030204 | -0.028211 | -0.04526 | 0.10983 | -0.10744 | 0.053113 | -0.37824 | -0.1247 | -0.042061 | -0.085724 | 0.29251 | 0.048476 | -0.13605 | 122.9617 | 122.8845 | 123.0451 | 66.6747 | -123.147 | 122.8672 | 123.0404 | 122.8559 | 66.6736 | -123.3702
1402.7969 | 123.2758 | -66.7282 | 56.2866 | -0.0029761 | -0.017615 | 0.0011025 | 0.053722 | -0.0056642 | 0.062717 | 0.00015261 | -0.0026255 | -0.0011965 | 0.058031 | 0.026882 | 0.058094 | -66.7244 | -0.026065 | -66.746 | 56.2656 | 56.1746 | 56.3535 | -66.8558 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.3488 | 56.1872 | -67.0881 | -0.12762 | -0.021047 | 0.003833 | -0.017795 | 0.10983 | -0.11202 | 0.066848 | -0.35993 | -0.11097 | -0.014596 | -0.05368 | 0.30625 | 0.062211 | -0.099417 | 122.9938 | 122.9028 | 123.0817 | 66.7021 | -123.1425 | 122.9039 | 123.077 | 122.9154 | 66.7011 | -123.3748
1403.7969 | 123.317 | -66.6916 | 56.3095 | -0.010607 | -0.017615 | 0.00088894 | 0.053936 | -0.0056642 | 0.062503 | 0.00015261 | -0.0019847 | -0.00034193 | 0.057817 | 0.027096 | 0.058522 | -66.7244 | -0.030644 | -66.746 | 56.2656 | 56.1746 | 56.3443 | -66.8467 | -66.7382 | -0.027113 | -66.7773 | 56.1619 | 56.3443 | 56.1643 | -67.0836 | -0.15508 | -0.043935 | -0.032788 | -0.054416 | 0.10067 | -0.1349 | 0.034803 | -0.39197 | -0.14759 | -0.046638 | -0.085722 | 0.30625 | 0.034744 | -0.1452 | 122.9572 | 122.8662 | 123.0359 | 66.6609 | -123.1562 | 122.8535 | 123.0358 | 122.8559 | 66.6645 | -123.3931
1404.7969 | 123.2391 | -66.6962 | 56.3507 | 0.0046549 | -0.017615 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | -0.0074779 | -0.0021983 | -0.00098273 | 0.058031 | 0.02731 | 0.058308 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1792 | 56.3443 | -66.8513 | -66.7474 | -0.027113 | -66.7819 | 56.1711 | 56.3351 | 56.1735 | -67.0881 | -0.15508 | -0.080556 | -0.037367 | -0.049838 | 0.10525 | -0.17152 | -0.006396 | -0.39197 | -0.17963 | -0.051218 | -0.085723 | 0.30625 | -0.015612 | -0.17724 | 122.9663 | 122.8754 | 123.0405 | 66.6655 | -123.202 | 122.8672 | 123.0313 | 122.8696 | 66.6691 | -123.4388
1405.7969 | 123.2574 | -66.6824 | 56.3187 | -0.0029761 | -0.017402 | 0.00088894 | 0.053936 | -0.0052368 | 0.062717 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.027096 | 0.058522 | -66.7381 | -0.021486 | -66.746 | 56.2656 | 56.1746 | 56.3443 | -66.8604 | -66.7336 | -0.036271 | -66.791 | 56.1711 | 56.3488 | 56.1689 | -67.0881 | -0.17797 | -0.053091 | -0.055678 | -0.063571 | 0.1144 | -0.14406 | 0.025647 | -0.40571 | -0.14759 | -0.051215 | -0.10861 | 0.29709 | 0.030167 | -0.14978 | 122.948 | 122.857 | 123.0267 | 66.6609 | -123.1791 | 122.8535 | 123.0313 | 122.8513 | 66.6462 | -123.4068
1406.8594 | 123.1842 | -66.7191 | 56.3461 | 0.0046549 | -0.017615 | 0.0011025 | 0.053722 | -0.0054506 | 0.062717 | 0.015414 | -0.0021983 | -0.00098273 | 0.057604 | 0.02731 | 0.058308 | -66.7335 | -0.026065 | -66.7414 | 56.2656 | 56.1746 | 56.3535 | -66.865 | -66.7428 | -0.040849 | -66.7819 | 56.1665 | 56.3488 | 56.1689 | -67.0881 | -0.14593 | -0.080556 | -0.014479 | -0.022372 | 0.12356 | -0.17153 | 0.007339 | -0.36909 | -0.17963 | -0.023751 | -0.062835 | 0.30625 | 0.002702 | -0.17724 | 122.9846 | 122.8937 | 123.0725 | 66.693 | -123.2111 | 122.8856 | 123.0679 | 122.8879 | 66.6782 | -123.4343
1407.7969 | 123.2437 | -66.7191 | 56.3049 | 0.0046549 | -0.017402 | 0.00088894 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058031 | 0.02731 | 0.058308 | -66.7335 | -0.026065 | -66.7368 | 56.2656 | 56.1609 | 56.3443 | -66.8604 | -66.7428 | -0.036271 | -66.791 | 56.1757 | 56.3397 | 56.178 | -67.0881 | -0.14135 | -0.039358 | -0.014479 | -0.017793 | 0.12356 | -0.14406 | 0.03938 | -0.36909 | -0.12928 | -0.023751 | -0.071992 | 0.29709 | 0.034743 | -0.12689 | 122.9846 | 122.8799 | 123.0634 | 66.693 | -123.1653 | 122.8947 | 123.0587 | 122.8971 | 66.6828 | -123.3931
1408.7969 | 123.2117 | -66.7099 | 56.3324 | -0.0029761 | -0.017615 | 0.0011025 | 0.053936 | -0.0054506 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057604 | 0.02731 | 0.058522 | -66.729 | -0.030644 | -66.746 | 56.2656 | 56.1746 | 56.3535 | -66.8604 | -66.7428 | -0.031692 | -66.791 | 56.1711 | 56.3443 | 56.1735 | -67.0927 | -0.15051 | -0.066823 | -0.019056 | -0.036105 | 0.1144 | -0.15779 | 0.021072 | -0.38282 | -0.16132 | -0.032906 | -0.081147 | 0.30167 | 0.011856 | -0.15893 | 122.9755 | 122.8845 | 123.0634 | 66.6793 | -123.1928 | 122.881 | 123.0542 | 122.8834 | 66.6782 | -123.4251
1409.7969 | 123.2986 | -66.6733 | 56.2958 | -0.0029761 | -0.017615 | 0.00067514 | 0.053936 | -0.0054506 | 0.062289 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057604 | 0.02731 | 0.058094 | -66.729 | -0.026065 | -66.7414 | 56.2656 | 56.17 | 56.3443 | -66.8604 | -66.7428 | -0.036271 | -66.791 | 56.1665 | 56.3443 | 56.1735 | -67.0881 | -0.18713 | -0.030202 | -0.055677 | -0.068148 | 0.11898 | -0.12575 | 0.048536 | -0.41486 | -0.12928 | -0.069527 | -0.11777 | 0.29709 | 0.048477 | -0.12231 | 122.9389 | 122.8433 | 123.0176 | 66.6472 | -123.1562 | 122.8398 | 123.0175 | 122.8467 | 66.637 | -123.3839
1410.7969 | 123.2803 | -66.7099 | 56.3095 | 0.012286 | -0.017615 | 0.00067514 | 0.054149 | -0.0056642 | 0.062289 | 0.0077831 | -0.0026255 | -0.00098273 | 0.05739 | 0.02731 | 0.058094 | -66.729 | -0.026065 | -66.7323 | 56.2747 | 56.1792 | 56.3489 | -66.8558 | -66.7382 | -0.036271 | -66.7819 | 56.1665 | 56.3488 | 56.1735 | -67.0836 | -0.14593 | -0.034778 | -0.019056 | -0.02237 | 0.12356 | -0.13032 | 0.039381 | -0.37366 | -0.14301 | -0.028327 | -0.07199 | 0.30167 | 0.039323 | -0.13604 | 122.9846 | 122.8891 | 123.0588 | 66.6838 | -123.1653 | 122.8764 | 123.0587 | 122.8834 | 66.6736 | -123.3931
1411.7969 | 123.2574 | -66.7053 | 56.3141 | -0.0029761 | -0.017402 | 0.00067514 | 0.054149 | -0.0056642 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.058031 | 0.027096 | 0.058094 | -66.729 | -0.030644 | -66.7506 | 56.2702 | 56.17 | 56.3489 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.3534 | 56.178 | -67.0881 | -0.15051 | -0.043935 | -0.023634 | -0.045261 | 0.10525 | -0.14406 | 0.034803 | -0.38282 | -0.13843 | -0.037484 | -0.081147 | 0.30167 | 0.039323 | -0.13604 | 122.9755 | 122.8753 | 123.0542 | 66.6747 | -123.1699 | 122.881 | 123.0587 | 122.8834 | 66.6736 | -123.4022
1412.7969 | 123.175 | -66.7191 | 56.3507 | 0.0046549 | -0.017615 | 0.00088894 | 0.053936 | -0.0054506 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.02731 | 0.058735 | -66.729 | -0.026065 | -66.7368 | 56.2656 | 56.1838 | 56.3443 | -66.865 | -66.7382 | -0.040849 | -66.7819 | 56.1665 | 56.3488 | 56.1689 | -67.0881 | -0.14593 | -0.085134 | -0.009901 | -0.017793 | 0.12814 | -0.16694 | -0.006396 | -0.36909 | -0.18421 | -0.019172 | -0.062835 | 0.30625 | -0.001876 | -0.18182 | 122.9846 | 122.9028 | 123.0634 | 66.693 | -123.2157 | 122.8856 | 123.0679 | 122.8879 | 66.6782 | -123.4388
1413.7969 | 123.2895 | -66.6916 | 56.3004 | 0.0046549 | -0.017402 | 0.0011025 | 0.053936 | -0.0052368 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057604 | 0.02731 | 0.058308 | -66.7381 | -0.030644 | -66.7414 | 56.2656 | 56.1838 | 56.3443 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1665 | 56.3534 | 56.1735 | -67.0881 | -0.16882 | -0.03478 | -0.046523 | -0.049838 | 0.11898 | -0.11659 | 0.043958 | -0.39655 | -0.13386 | -0.055796 | -0.09488 | 0.30167 | 0.053056 | -0.12689 | 122.9572 | 122.8754 | 123.0359 | 66.6609 | -123.1608 | 122.8581 | 123.045 | 122.8651 | 66.6553 | -123.3885
1414.7969 | 123.175 | -66.7145 | 56.3324 | 0.0046549 | -0.017829 | 0.00088894 | 0.053722 | -0.0054506 | 0.063144 | 0.0077831 | -0.0019847 | -0.00098273 | 0.058031 | 0.027523 | 0.058308 | -66.729 | -0.026065 | -66.746 | 56.2702 | 56.1746 | 56.3489 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1665 | 56.3534 | 56.178 | -67.079 | -0.14593 | -0.062245 | -0.014478 | -0.031527 | 0.1144 | -0.15779 | 0.016493 | -0.3645 | -0.1659 | -0.032907 | -0.071991 | 0.29251 | 0.021013 | -0.15435 | 122.9846 | 122.8891 | 123.0634 | 66.6884 | -123.1928 | 122.881 | 123.0679 | 122.8925 | 66.6782 | -123.4114
1415.8594 | 123.2803 | -66.7145 | 56.2958 | 0.019917 | -0.017829 | 0.00088894 | 0.053936 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.058031 | 0.02731 | 0.058094 | -66.7244 | -0.035222 | -66.746 | 56.2656 | 56.1792 | 56.3489 | -66.8558 | -66.7428 | -0.040849 | -66.791 | 56.1665 | 56.358 | 56.1689 | -67.0836 | -0.14135 | -0.030202 | -0.009899 | -0.031527 | 0.10983 | -0.11659 | 0.053114 | -0.36908 | -0.12928 | -0.028328 | -0.076569 | 0.29251 | 0.062213 | -0.12689 | 122.9801 | 122.8937 | 123.0634 | 66.6793 | -123.1516 | 122.881 | 123.0725 | 122.8834 | 66.6736 | -123.3793
1416.7969 | 123.1659 | -66.7557 | 56.3416 | -0.0029761 | -0.017615 | 0.00088894 | 0.053508 | -0.0056642 | 0.062717 | 0.015414 | -0.0019847 | -0.00076913 | 0.057817 | 0.027523 | 0.058308 | -66.729 | -0.030644 | -66.7414 | 56.261 | 56.1792 | 56.3535 | -66.8604 | -66.7382 | -0.031692 | -66.7819 | 56.1711 | 56.3534 | 56.1735 | -67.0881 | -0.10473 | -0.080558 | 0.02672 | 0.014249 | 0.11898 | -0.16237 | 0.011916 | -0.33246 | -0.17048 | 0.017449 | -0.026214 | 0.30625 | 0.011857 | -0.16808 | 123.0167 | 122.9349 | 123.1091 | 66.725 | -123.202 | 122.9267 | 123.1091 | 122.9291 | 66.724 | -123.4297
1417.7969 | 123.2437 | -66.6962 | 56.3232 | 0.0046549 | -0.017402 | 0.00088894 | 0.054149 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00076913 | 0.058031 | 0.02731 | 0.058308 | -66.729 | -0.026065 | -66.7414 | 56.2656 | 56.17 | 56.3443 | -66.8558 | -66.7428 | -0.036271 | -66.7819 | 56.1665 | 56.3534 | 56.1735 | -67.0836 | -0.15966 | -0.057668 | -0.032789 | -0.04526 | 0.1144 | -0.15322 | 0.02107 | -0.38739 | -0.15675 | -0.046639 | -0.085723 | 0.30167 | 0.030168 | -0.14977 | 122.9617 | 122.8662 | 123.0405 | 66.6701 | -123.1791 | 122.8627 | 123.0496 | 122.8696 | 66.6599 | -123.4068
1418.7969 | 123.1842 | -66.7236 | 56.337 | -0.0029761 | -0.017615 | 0.00046154 | 0.053508 | -0.0052368 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.057817 | 0.027523 | 0.058522 | -66.7244 | -0.030644 | -66.7414 | 56.2656 | 56.1654 | 56.3489 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.3443 | 56.1643 | -67.0973 | -0.13678 | -0.071401 | -0.000744 | -0.017794 | 0.11898 | -0.17153 | 0.011915 | -0.37367 | -0.1659 | -0.023752 | -0.062836 | 0.31083 | 0.007278 | -0.17266 | 122.9892 | 122.8891 | 123.0725 | 66.693 | -123.1974 | 122.8947 | 123.0679 | 122.8879 | 66.6874 | -123.4343
1419.8594 | 123.2437 | -66.7374 | 56.2775 | 0.0046549 | -0.017615 | 0.00088894 | 0.053508 | -0.0052368 | 0.062289 | 0.015414 | -0.0024119 | -0.00076913 | 0.058031 | 0.02731 | 0.058308 | -66.729 | -0.026065 | -66.7323 | 56.2656 | 56.1792 | 56.3443 | -66.8558 | -66.7336 | -0.031692 | -66.7865 | 56.1711 | 56.3488 | 56.1552 | -67.0836 | -0.11846 | -0.011892 | 0.00841 | 0.005096 | 0.12356 | -0.098282 | 0.066846 | -0.3462 | -0.10639 | 0.003717 | -0.049103 | 0.29709 | 0.071366 | -0.12231 | 123.0029 | 122.9166 | 123.0817 | 66.7113 | -123.1333 | 122.9084 | 123.0862 | 122.8925 | 66.7057 | -123.361
1420.7969 | 123.1934 | -66.7374 | 56.3461 | -0.010607 | -0.017615 | 0.0011025 | 0.053508 | -0.0058778 | 0.062289 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057817 | 0.027737 | 0.058522 | -66.7244 | -0.030644 | -66.7414 | 56.2656 | 56.1792 | 56.3443 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3488 | 56.1735 | -67.0881 | -0.11846 | -0.080556 | 0.012989 | -0.004061 | 0.1144 | -0.16695 | -0.001818 | -0.35077 | -0.17506 | -0.00544 | -0.049103 | 0.30167 | 0.002702 | -0.17266 | 123.0029 | 122.9166 | 123.0817 | 66.7067 | -123.202 | 122.9084 | 123.0862 | 122.9108 | 66.7057 | -123.4343
1421.7969 | 123.2071 | -66.7191 | 56.369 | -0.010607 | -0.017829 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057817 | 0.026669 | 0.057881 | -66.729 | -0.026065 | -66.7368 | 56.2702 | 56.1609 | 56.3535 | -66.865 | -66.7382 | -0.036271 | -66.7773 | 56.1665 | 56.3534 | 56.1643 | -67.0881 | -0.14593 | -0.098867 | -0.009901 | -0.017793 | 0.12814 | -0.20815 | -0.01555 | -0.36909 | -0.20252 | -0.019172 | -0.058256 | 0.31083 | -0.015609 | -0.20471 | 122.9892 | 122.8799 | 123.0725 | 66.693 | -123.234 | 122.8856 | 123.0725 | 122.8834 | 66.6828 | -123.4572
1422.8594 | 123.2529 | -66.7099 | 56.3095 | 0.0046549 | -0.017615 | 0.00088894 | 0.053722 | -0.0052368 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.02731 | 0.058094 | -66.7381 | -0.026065 | -66.7368 | 56.2702 | 56.1609 | 56.3535 | -66.8604 | -66.7382 | -0.036271 | -66.791 | 56.1665 | 56.3534 | 56.1735 | -67.0927 | -0.15051 | -0.039357 | -0.028212 | -0.026948 | 0.12356 | -0.14864 | 0.04396 | -0.38282 | -0.14301 | -0.028327 | -0.081147 | 0.30167 | 0.043901 | -0.13604 | 122.9801 | 122.8708 | 123.0634 | 66.6838 | -123.1699 | 122.8764 | 123.0633 | 122.8834 | 66.6736 | -123.4022
1423.7969 | 123.2117 | -66.7282 | 56.3873 | 0.012286 | -0.017615 | 0.00088894 | 0.053508 | -0.0058778 | 0.062503 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057817 | 0.027523 | 0.058094 | -66.7244 | -0.030644 | -66.7414 | 56.2656 | 56.1792 | 56.3535 | -66.8513 | -66.7336 | -0.036271 | -66.7773 | 56.1711 | 56.3488 | 56.1735 | -67.0881 | -0.12304 | -0.12176 | 0.003833 | -0.013217 | 0.10982 | -0.20815 | -0.03386 | -0.35993 | -0.21626 | -0.005439 | -0.049101 | 0.31083 | -0.038497 | -0.21386 | 122.9938 | 122.9074 | 123.0817 | 66.6976 | -123.2386 | 122.8993 | 123.077 | 122.9017 | 66.6919 | -123.4755
1424.7969 | 123.175 | -66.7419 | 56.3278 | 0.0046549 | -0.017829 | 0.00088894 | 0.053722 | -0.0054506 | 0.062503 | -0.0074779 | -0.0019847 | -0.00055553 | 0.058031 | 0.02731 | 0.058308 | -66.729 | -0.021486 | -66.7414 | 56.2747 | 56.1746 | 56.358 | -66.8696 | -66.7428 | -0.036271 | -66.7819 | 56.1665 | 56.3626 | 56.178 | -67.0973 | -0.12762 | -0.053089 | 0.012987 | 0.000516 | 0.12814 | -0.15322 | 0.030228 | -0.35536 | -0.16132 | -0.000863 | -0.039947 | 0.31541 | 0.034748 | -0.14977 | 123.0167 | 122.9165 | 123.1 | 66.7205 | -123.1974 | 122.9084 | 123.1045 | 122.92 | 66.7057 | -123.4251
1425.7969 | 123.2254 | -66.7191 | 56.3736 | 0.0046549 | -0.017615 | 0.00088894 | 0.053722 | -0.0058778 | 0.062076 | 0.0077831 | -0.0021983 | -0.00055553 | 0.058031 | 0.027096 | 0.057881 | -66.7244 | -0.030644 | -66.7323 | 56.2656 | 56.1838 | 56.3535 | -66.8696 | -66.7382 | -0.036271 | -66.791 | 56.1711 | 56.3488 | 56.1643 | -67.0927 | -0.15051 | -0.10802 | -0.005322 | -0.013215 | 0.1373 | -0.18983 | -0.020127 | -0.37367 | -0.20252 | -0.019172 | -0.071992 | 0.30167 | -0.024764 | -0.20929 | 122.9846 | 122.9028 | 123.0725 | 66.6884 | -123.2432 | 122.8901 | 123.0679 | 122.8834 | 66.6828 | -123.4663
1426.7969 | 123.2208 | -66.7328 | 56.3187 | -0.0029761 | -0.017615 | 0.00067514 | 0.053936 | -0.0054506 | 0.062289 | -0.015108 | -0.0024119 | -0.00076913 | 0.057604 | 0.02731 | 0.058308 | -66.7335 | -0.021486 | -66.7323 | 56.2656 | 56.1746 | 56.358 | -66.8558 | -66.7382 | -0.027113 | -66.7819 | 56.1711 | 56.3488 | 56.1643 | -67.0927 | -0.12304 | -0.053091 | -0.000746 | 0.000518 | 0.12356 | -0.14406 | 0.039383 | -0.35993 | -0.14759 | -0.005439 | -0.049102 | 0.31083 | 0.030167 | -0.15435 | 122.9984 | 122.9074 | 123.0908 | 66.7113 | -123.1745 | 122.9039 | 123.0816 | 122.8971 | 66.7057 | -123.4114
1427.8594 | 123.2712 | -66.7145 | 56.2775 | 0.0046549 | -0.017615 | 0.0011025 | 0.053722 | -0.0052368 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.058031 | 0.02731 | 0.058094 | -66.7335 | -0.026065 | -66.746 | 56.2702 | 56.17 | 56.3397 | -66.8604 | -66.7474 | -0.031692 | -66.7819 | 56.1802 | 56.3488 | 56.1689 | -67.0973 | -0.14593 | -0.007314 | -0.019056 | -0.031527 | 0.1144 | -0.10744 | 0.062267 | -0.38282 | -0.097235 | -0.032907 | -0.067412 | 0.31541 | 0.071366 | -0.10858 | 122.9846 | 122.8845 | 123.0542 | 66.6884 | -123.1379 | 122.8947 | 123.0633 | 122.8834 | 66.6828 | -123.3748
1428.7969 | 123.175 | -66.7328 | 56.3278 | -0.0029761 | -0.017829 | 0.00067514 | 0.053722 | -0.0054506 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.058031 | 0.027523 | 0.058522 | -66.729 | -0.016908 | -66.746 | 56.2747 | 56.1792 | 56.3535 | -66.865 | -66.7428 | -0.022535 | -66.7773 | 56.1757 | 56.3534 | 56.178 | -67.0973 | -0.1322 | -0.053089 | 0.003832 | -0.013217 | 0.11898 | -0.14864 | 0.025649 | -0.36451 | -0.15217 | -0.010018 | -0.044523 | 0.31999 | 0.02559 | -0.14977 | 123.0075 | 122.912 | 123.0863 | 66.7159 | -123.1928 | 122.9084 | 123.0862 | 122.9108 | 66.7103 | -123.4251
1429.7969 | 123.1888 | -66.7328 | 56.3324 | -0.010607 | -0.018043 | 0.00046154 | 0.053722 | -0.0056642 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.02731 | 0.058094 | -66.7335 | -0.016908 | -66.7368 | 56.2702 | 56.1838 | 56.3535 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.3488 | 56.178 | -67.0881 | -0.12762 | -0.062245 | -0.000746 | -0.00406 | 0.12356 | -0.14863 | 0.021072 | -0.35535 | -0.16132 | -0.010018 | -0.049102 | 0.30625 | 0.016435 | -0.15435 | 123.0029 | 122.9166 | 123.0863 | 66.7159 | -123.1928 | 122.9039 | 123.0816 | 122.9108 | 66.7057 | -123.4205
1430.8594 | 123.1979 | -66.7282 | 56.3416 | -0.0029761 | -0.017615 | 0.0011025 | 0.053722 | -0.0054506 | 0.062076 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057604 | 0.027523 | 0.058308 | -66.7244 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.3535 | -66.8604 | -66.7474 | -0.027113 | -66.7865 | 56.1757 | 56.3534 | 56.1643 | -67.0927 | -0.1322 | -0.071401 | 0.003833 | -0.013217 | 0.11898 | -0.16695 | 0.011916 | -0.36451 | -0.1659 | -0.019175 | -0.058259 | 0.30625 | 0.011857 | -0.17724 | 122.9984 | 122.9028 | 123.0817 | 66.7021 | -123.202 | 122.9039 | 123.0816 | 122.8925 | 66.7011 | -123.4343
1431.7969 | 123.1842 | -66.7603 | 56.3416 | 0.0046549 | -0.017829 | 0.00088894 | 0.053722 | -0.0052368 | 0.063144 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.027523 | 0.057881 | -66.7198 | -0.021486 | -66.7506 | 56.2702 | 56.1838 | 56.3489 | -66.8696 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3534 | 56.178 | -67.0927 | -0.10931 | -0.071401 | 0.040455 | 0.009671 | 0.11898 | -0.15779 | 0.007337 | -0.33247 | -0.17048 | 0.017448 | -0.026215 | 0.30625 | 0.011857 | -0.16351 | 123.0304 | 122.944 | 123.1091 | 66.7388 | -123.2111 | 122.9313 | 123.1137 | 122.9383 | 66.7286 | -123.4343
1432.7969 | 123.1705 | -66.7603 | 56.3004 | -0.0029761 | -0.017829 | 0.00088894 | 0.053508 | -0.0054506 | 0.062289 | -0.0074779 | -0.0019847 | -0.00076913 | 0.057817 | 0.027523 | 0.057881 | -66.729 | -0.016908 | -66.7552 | 56.2656 | 56.1654 | 56.358 | -66.8604 | -66.7382 | -0.031692 | -66.7773 | 56.1665 | 56.3488 | 56.1643 | -67.0836 | -0.10015 | -0.03478 | 0.031298 | 0.005093 | 0.10525 | -0.13491 | 0.057694 | -0.32331 | -0.13386 | 0.022027 | -0.017057 | 0.30625 | 0.048478 | -0.13604 | 123.0258 | 122.9257 | 123.1183 | 66.7433 | -123.1608 | 122.9267 | 123.1091 | 122.9246 | 66.7286 | -123.3839
1433.7969 | 123.1888 | -66.7465 | 56.3141 | -0.0029761 | -0.017829 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.015414 | -0.0019847 | -0.0011965 | 0.057817 | 0.02731 | 0.057881 | -66.7335 | -0.021486 | -66.7506 | 56.2656 | 56.1883 | 56.3489 | -66.8558 | -66.7474 | -0.031692 | -66.7819 | 56.1665 | 56.3488 | 56.1597 | -67.0927 | -0.10931 | -0.048513 | 0.012987 | -0.004062 | 0.10525 | -0.12575 | 0.034803 | -0.3462 | -0.14759 | -0.000864 | -0.035369 | 0.31083 | 0.034745 | -0.15436 | 123.0121 | 122.9349 | 123.0954 | 66.725 | -123.1699 | 122.913 | 123.0954 | 122.9063 | 66.7148 | -123.4068
1434.8594 | 123.1842 | -66.7511 | 56.3278 | -0.010607 | -0.017402 | 0.00067514 | 0.053722 | -0.0058778 | 0.063144 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057604 | 0.027951 | 0.058308 | -66.729 | -0.030644 | -66.7552 | 56.2656 | 56.1838 | 56.3489 | -66.8604 | -66.7382 | -0.036271 | -66.7773 | 56.1711 | 56.3488 | 56.1872 | -67.0881 | -0.10931 | -0.062246 | 0.022143 | -0.004062 | 0.10525 | -0.14406 | 0.02107 | -0.33704 | -0.15675 | 0.012872 | -0.026212 | 0.31083 | 0.021012 | -0.14062 | 123.0167 | 122.9349 | 123.1 | 66.7205 | -123.1882 | 122.9222 | 123.0999 | 122.9383 | 66.7148 | -123.416
1435.7969 | 123.1796 | -66.7603 | 56.337 | -0.0029761 | -0.017829 | 0.0011025 | 0.053722 | -0.0054506 | 0.062076 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.02731 | 0.057667 | -66.7335 | -0.030644 | -66.7323 | 56.2747 | 56.1792 | 56.3535 | -66.8558 | -66.7382 | -0.031692 | -66.7865 | 56.1711 | 56.3488 | 56.1735 | -67.0836 | -0.095576 | -0.062244 | 0.02672 | 0.027984 | 0.12356 | -0.15779 | 0.016494 | -0.32331 | -0.1659 | 0.022027 | -0.026215 | 0.29709 | 0.011857 | -0.16351 | 123.035 | 122.9394 | 123.1137 | 66.7296 | -123.1928 | 122.9313 | 123.1091 | 122.9337 | 66.7286 | -123.4205
1436.7969 | 123.1293 | -66.7648 | 56.3095 | 0.0046549 | -0.018043 | 0.00024794 | 0.053508 | -0.0054506 | 0.06293 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057604 | 0.027737 | 0.058308 | -66.7244 | -0.021486 | -66.7323 | 56.2747 | 56.1792 | 56.3489 | -66.865 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.358 | 56.1826 | -67.0881 | -0.10016 | -0.034778 | 0.040455 | 0.032562 | 0.13272 | -0.13032 | 0.039381 | -0.32331 | -0.13844 | 0.017447 | -0.021637 | 0.30167 | 0.04848 | -0.12688 | 123.0396 | 122.944 | 123.1137 | 66.7433 | -123.1745 | 122.9359 | 123.1228 | 122.9475 | 66.7286 | -123.3976
1437.7969 | 123.2071 | -66.7557 | 56.3507 | -0.0029761 | -0.018043 | 0.00067514 | 0.053508 | -0.0054506 | 0.062289 | 0.0077831 | -0.0026255 | -0.00076913 | 0.05739 | 0.028164 | 0.058094 | -66.7335 | -0.021486 | -66.7368 | 56.2656 | 56.1792 | 56.3535 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1665 | 56.3488 | 56.1552 | -67.0881 | -0.10473 | -0.085134 | 0.022142 | 0.018828 | 0.12356 | -0.17152 | 0.002761 | -0.33246 | -0.18421 | 0.01287 | -0.026214 | 0.30625 | -0.001876 | -0.19555 | 123.0212 | 122.9349 | 123.1091 | 66.7342 | -123.2111 | 122.9222 | 123.1045 | 122.9108 | 66.7286 | -123.4388
1438.8594 | 123.2162 | -66.687 | 56.3324 | 0.012286 | -0.017829 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057817 | 0.02731 | 0.058094 | -66.729 | -0.030644 | -66.7368 | 56.2656 | 56.1746 | 56.3443 | -66.8558 | -66.7428 | -0.036271 | -66.7727 | 56.1711 | 56.3534 | 56.1643 | -67.0881 | -0.16882 | -0.066823 | -0.041944 | -0.049836 | 0.11898 | -0.15779 | 0.011915 | -0.40113 | -0.16132 | -0.055794 | -0.08572 | 0.31541 | 0.021013 | -0.16809 | 122.9526 | 122.8616 | 123.0313 | 66.6564 | -123.1882 | 122.8581 | 123.0404 | 122.8513 | 66.6507 | -123.4205
1439.7969 | 123.2117 | -66.7465 | 56.3095 | 0.012286 | -0.017615 | 0.00088894 | 0.053508 | -0.0054506 | 0.062289 | 0.0077831 | -0.0019847 | -0.00055553 | 0.057817 | 0.027096 | 0.058094 | -66.7244 | -0.021486 | -66.7277 | 56.2793 | 56.1792 | 56.358 | -66.8467 | -66.7382 | -0.031692 | -66.7819 | 56.1711 | 56.3488 | 56.1689 | -67.079 | -0.10015 | -0.0302 | 0.022144 | 0.018829 | 0.11898 | -0.13032 | 0.048539 | -0.33246 | -0.13844 | 0.008294 | -0.035369 | 0.29709 | 0.039323 | -0.14062 | 123.0258 | 122.9257 | 123.1046 | 66.725 | -123.1562 | 122.9176 | 123.0954 | 122.9154 | 66.7148 | -123.3885
1440.8594 | 123.1338 | -66.7282 | 56.3278 | 0.012286 | -0.017615 | 0.00088894 | 0.053508 | -0.0058778 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.058031 | 0.027523 | 0.057881 | -66.7335 | -0.026065 | -66.746 | 56.2656 | 56.1792 | 56.3535 | -66.8604 | -66.7428 | -0.022535 | -66.7819 | 56.1711 | 56.3397 | 56.1826 | -67.0836 | -0.1322 | -0.062246 | -0.005324 | -0.017795 | 0.1144 | -0.14864 | 0.025649 | -0.35535 | -0.15675 | -0.014596 | -0.05368 | 0.30167 | 0.011855 | -0.1452 | 122.9938 | 122.9074 | 123.0817 | 66.7021 | -123.1882 | 122.8993 | 123.0679 | 122.9108 | 66.7057 | -123.4114
1441.7969 | 123.2391 | -66.7328 | 56.3049 | -0.0029761 | -0.018043 | 0.00046154 | 0.053722 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00055553 | 0.058031 | 0.027523 | 0.058308 | -66.7335 | -0.026065 | -66.7368 | 56.2702 | 56.1838 | 56.3535 | -66.8513 | -66.7336 | -0.031692 | -66.7865 | 56.1757 | 56.3534 | 56.1597 | -67.0881 | -0.11846 | -0.03478 | -0.000746 | -0.00406 | 0.1144 | -0.12117 | 0.048537 | -0.35535 | -0.12928 | -0.000861 | -0.053681 | 0.30167 | 0.048478 | -0.1452 | 123.0029 | 122.9166 | 123.0863 | 66.7067 | -123.1562 | 122.9084 | 123.0862 | 122.8925 | 66.7011 | -123.3931
1442.7969 | 123.1842 | -66.7557 | 56.3049 | -0.0029761 | -0.018256 | 0.00088894 | 0.054149 | -0.0052368 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057604 | 0.027737 | 0.058094 | -66.7198 | -0.021486 | -66.7414 | 56.261 | 56.1792 | 56.3443 | -66.8558 | -66.7382 | -0.031692 | -66.7865 | 56.1665 | 56.3534 | 56.1872 | -67.0927 | -0.10015 | -0.043937 | 0.035877 | 0.014249 | 0.1144 | -0.12575 | 0.03938 | -0.33704 | -0.13844 | 0.017449 | -0.030793 | 0.30625 | 0.048478 | -0.11773 | 123.0167 | 122.9349 | 123.1 | 66.7342 | -123.1608 | 122.9222 | 123.1091 | 122.9429 | 66.724 | -123.3977
1443.7969 | 123.2117 | -66.7557 | 56.3324 | 0.0046549 | -0.018043 | 0.00046154 | 0.053508 | -0.0052368 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.027523 | 0.057881 | -66.7335 | -0.026065 | -66.7506 | 56.2656 | 56.17 | 56.3626 | -66.8696 | -66.7428 | -0.036271 | -66.791 | 56.1711 | 56.358 | 56.1643 | -67.0836 | -0.11389 | -0.066823 | 0.022142 | 0.005093 | 0.11898 | -0.16237 | 0.030229 | -0.32789 | -0.16132 | 0.01287 | -0.035371 | 0.29251 | 0.025592 | -0.16809 | 123.0212 | 122.9257 | 123.1183 | 66.7296 | -123.202 | 122.9267 | 123.1137 | 122.92 | 66.7194 | -123.416
1444.8594 | 123.1522 | -66.7648 | 56.3049 | -0.0029761 | -0.018043 | 0.00088894 | 0.053508 | -0.0056642 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.058031 | 0.027737 | 0.058094 | -66.7244 | -0.021486 | -66.746 | 56.2702 | 56.1792 | 56.3489 | -66.8604 | -66.7428 | -0.031692 | -66.7819 | 56.1711 | 56.3534 | 56.1689 | -67.0881 | -0.095576 | -0.03478 | 0.040455 | 0.018827 | 0.1144 | -0.12575 | 0.043958 | -0.32331 | -0.13386 | 0.022026 | -0.017058 | 0.30625 | 0.048478 | -0.13604 | 123.035 | 122.944 | 123.1137 | 66.7433 | -123.1653 | 122.9359 | 123.1182 | 122.9337 | 66.7331 | -123.3931
1445.7969 | 123.1796 | -66.7374 | 56.3187 | 0.0046549 | -0.017829 | 0.00067514 | 0.053722 | -0.0054506 | 0.062717 | 0.00015261 | -0.0019847 | -0.00076913 | 0.057817 | 0.027737 | 0.057881 | -66.729 | -0.030644 | -66.746 | 56.2702 | 56.1838 | 56.3489 | -66.8513 | -66.7428 | -0.040849 | -66.7865 | 56.1802 | 56.3488 | 56.1735 | -67.0836 | -0.11389 | -0.048513 | 0.00841 | -0.008639 | 0.10525 | -0.1349 | 0.030225 | -0.3462 | -0.13843 | -0.00544 | -0.049103 | 0.29709 | 0.030167 | -0.1452 | 123.0075 | 122.9211 | 123.0863 | 66.7067 | -123.1699 | 122.9176 | 123.0862 | 122.9108 | 66.6965 | -123.4022
1446.7969 | 123.1201 | -66.7511 | 56.3187 | -0.010607 | -0.018043 | 0.00088894 | 0.053936 | -0.0054506 | 0.062717 | -0.0074779 | -0.0026255 | -0.00098273 | 0.057604 | 0.027523 | 0.058094 | -66.7244 | -0.021486 | -66.746 | 56.2702 | 56.1792 | 56.3626 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1665 | 56.3488 | 56.1643 | -67.0927 | -0.11389 | -0.048513 | 0.026722 | 0.005094 | 0.11898 | -0.13948 | 0.043961 | -0.34162 | -0.15217 | 0.008293 | -0.030791 | 0.31083 | 0.030167 | -0.15435 | 123.0213 | 122.9303 | 123.1137 | 66.7296 | -123.1837 | 122.9176 | 123.0999 | 122.9154 | 66.724 | -123.4114
1447.8594 | 123.111 | -66.7557 | 56.3049 | -0.010607 | -0.018684 | 0.00088894 | 0.053722 | -0.0054506 | 0.062076 | 0.0077831 | -0.0019847 | -0.00098273 | 0.057604 | 0.027523 | 0.057881 | -66.7244 | -0.026065 | -66.746 | 56.2747 | 56.1838 | 56.3626 | -66.8558 | -66.7428 | -0.027113 | -66.7865 | 56.1665 | 56.3443 | 56.178 | -67.0973 | -0.10015 | -0.030201 | 0.031299 | 0.009671 | 0.10983 | -0.12117 | 0.057694 | -0.34162 | -0.13844 | 0.01287 | -0.030793 | 0.31083 | 0.039321 | -0.12689 | 123.0304 | 122.9394 | 123.1183 | 66.7296 | -123.1608 | 122.9222 | 123.0999 | 122.9337 | 66.7286 | -123.4022
1448.7969 | 123.1384 | -66.7603 | 56.3049 | -0.0029761 | -0.018043 | 0.00067514 | 0.053722 | -0.0056642 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.027737 | 0.057881 | -66.729 | -0.026065 | -66.7552 | 56.2702 | 56.1746 | 56.3489 | -66.8604 | -66.7474 | -0.022535 | -66.791 | 56.1757 | 56.358 | 56.1552 | -67.0927 | -0.10015 | -0.03478 | 0.031298 | 0.005093 | 0.10525 | -0.13033 | 0.043958 | -0.33247 | -0.12928 | 0.012869 | -0.030793 | 0.30167 | 0.053057 | -0.14978 | 123.0304 | 122.9349 | 123.1091 | 66.7342 | -123.1653 | 122.9359 | 123.1182 | 122.9154 | 66.7377 | -123.3977
1449.8594 | 123.1613 | -66.7603 | 56.3553 | 0.012286 | -0.018043 | 0.00046154 | 0.053722 | -0.0058778 | 0.062289 | 0.0077831 | -0.0024119 | -0.00098273 | 0.057817 | 0.027737 | 0.058094 | -66.7381 | -0.030644 | -66.7414 | 56.2702 | 56.1792 | 56.3535 | -66.865 | -66.7428 | -0.027113 | -66.791 | 56.1757 | 56.3534 | 56.1826 | -67.0927 | -0.10473 | -0.085134 | 0.022142 | 0.018827 | 0.12356 | -0.1761 | -0.001817 | -0.33247 | -0.17963 | 0.017448 | -0.030793 | 0.30167 | -0.001876 | -0.17266 | 123.0304 | 122.9394 | 123.1137 | 66.7296 | -123.2203 | 122.9359 | 123.1137 | 122.9429 | 66.7331 | -123.448
1450.7969 | 123.1384 | -66.7694 | 56.2958 | -0.0029761 | -0.018684 | 0.00088894 | 0.053722 | -0.0056642 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057604 | 0.027523 | 0.058094 | -66.729 | -0.026065 | -66.746 | 56.2793 | 56.17 | 56.3443 | -66.8604 | -66.7474 | -0.031692 | -66.7819 | 56.1711 | 56.3488 | 56.178 | -67.0927 | -0.090999 | -0.016467 | 0.040453 | 0.023404 | 0.1144 | -0.12575 | 0.048536 | -0.32331 | -0.1247 | 0.022024 | -0.012481 | 0.31083 | 0.053056 | -0.11773 | 123.0487 | 122.9394 | 123.1137 | 66.7433 | -123.1562 | 122.9405 | 123.1182 | 122.9475 | 66.7377 | -123.3885
1451.7969 | 123.1979 | -66.7191 | 56.3141 | -0.0029761 | -0.01847 | 0.00088894 | 0.053722 | -0.0056642 | 0.062289 | -0.0074779 | -0.0024119 | -0.00098273 | 0.057817 | 0.027737 | 0.058094 | -66.7335 | -0.026065 | -66.7552 | 56.2793 | 56.1746 | 56.3535 | -66.8604 | -66.752 | -0.027113 | -66.7819 | 56.1665 | 56.3443 | 56.1918 | -67.0927 | -0.14135 | -0.034778 | -0.014479 | -0.036106 | 0.10525 | -0.13948 | 0.039382 | -0.37367 | -0.14759 | -0.032908 | -0.062835 | 0.31083 | 0.030166 | -0.1223 | 122.9984 | 122.8937 | 123.0725 | 66.693 | -123.1745 | 122.8856 | 123.0633 | 122.9108 | 66.6919 | -123.4068
1452.8594 | 123.2529 | -66.6962 | 56.2683 | -0.010607 | -0.018256 | 0.00088894 | 0.053722 | -0.0058778 | 0.062289 | 0.0077831 | -0.0024119 | -0.00098273 | 0.057817 | 0.027951 | 0.057881 | -66.729 | -0.021486 | -66.746 | 56.2656 | 56.1838 | 56.3535 | -66.8604 | -66.7428 | -0.036271 | -66.7865 | 56.1711 | 56.358 | 56.1689 | -67.0927 | -0.16424 | -0.002737 | -0.032789 | -0.049838 | 0.1144 | -0.084548 | 0.085158 | -0.39655 | -0.097237 | -0.046639 | -0.090302 | 0.30625 | 0.089678 | -0.099422 | 122.9617 | 122.8799 | 123.0496 | 66.6747 | -123.1287 | 122.8672 | 123.0542 | 122.8651 | 66.6599 | -123.361
1453.7969 | 123.1888 | -66.7557 | 56.3324 | -0.0029761 | -0.018043 | 0.00088894 | 0.053508 | -0.0056642 | 0.06293 | -0.015108 | -0.0021983 | -0.00055553 | 0.057817 | 0.027737 | 0.057881 | -66.7244 | -0.021486 | -66.7368 | 56.2656 | 56.1883 | 56.358 | -66.8604 | -66.7382 | -0.036271 | -66.7819 | 56.1711 | 56.358 | 56.178 | -67.0881 | -0.10473 | -0.066823 | 0.031299 | 0.018828 | 0.12356 | -0.14406 | 0.025651 | -0.33246 | -0.16132 | 0.017449 | -0.026214 | 0.30625 | 0.025592 | -0.15435 | 123.0212 | 122.944 | 123.1137 | 66.7342 | -123.1928 | 122.9267 | 123.1137 | 122.9337 | 66.7194 | -123.4205
1454.8594 | 123.1567 | -66.7511 | 56.3232 | 0.0046549 | -0.01847 | 0.0011025 | 0.053722 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.0011965 | 0.057817 | 0.02731 | 0.058308 | -66.729 | -0.026065 | -66.746 | 56.2702 | 56.1746 | 56.3443 | -66.8558 | -66.7474 | -0.027113 | -66.7819 | 56.1757 | 56.3534 | 56.178 | -67.0973 | -0.10473 | -0.05309 | 0.022143 | 0.005094 | 0.10983 | -0.14864 | 0.02107 | -0.3462 | -0.14759 | 0.003714 | -0.030791 | 0.31541 | 0.030168 | -0.1452 | 123.0213 | 122.9257 | 123.0954 | 66.725 | -123.1791 | 122.9268 | 123.1045 | 122.9291 | 66.724 | -123.4205
1455.7969 | 123.1796 | -66.7465 | 56.3187 | -0.010607 | -0.018256 | 0.00046154 | 0.053936 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057817 | 0.027523 | 0.058094 | -66.7335 | -0.030644 | -66.746 | 56.2747 | 56.1838 | 56.3489 | -66.865 | -66.7474 | -0.031692 | -66.7819 | 56.1757 | 56.3534 | 56.1826 | -67.0881 | -0.11847 | -0.043934 | 0.012987 | 0.000516 | 0.11898 | -0.1349 | 0.030225 | -0.34162 | -0.14301 | -0.000864 | -0.035369 | 0.30625 | 0.034745 | -0.13604 | 123.0213 | 122.9303 | 123.0954 | 66.7159 | -123.1837 | 122.9222 | 123.0999 | 122.9291 | 66.7148 | -123.4068
1456.8594 | 123.2849 | -66.7236 | 56.2637 | -0.0029761 | -0.018256 | 0.00046154 | 0.053722 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057817 | 0.027951 | 0.058094 | -66.7335 | -0.016908 | -66.746 | 56.2702 | 56.1838 | 56.3535 | -66.865 | -66.7428 | -0.031692 | -66.7819 | 56.1711 | 56.3534 | 56.1826 | -67.0927 | -0.14135 | 0.006419 | -0.009901 | -0.022372 | 0.11898 | -0.07997 | 0.089736 | -0.36909 | -0.092659 | -0.019173 | -0.058257 | 0.31083 | 0.089677 | -0.081108 | 122.9938 | 122.9074 | 123.0771 | 66.7067 | -123.1287 | 122.8947 | 123.077 | 122.9063 | 66.6919 | -123.3565
1457.7969 | 123.2391 | -66.7145 | 56.3187 | 0.012286 | -0.018256 | 0.00088894 | 0.053936 | -0.0058778 | 0.062503 | 0.015414 | -0.0021983 | -0.00076913 | 0.057817 | 0.027737 | 0.057881 | -66.7335 | -0.021486 | -66.7552 | 56.261 | 56.1609 | 56.3443 | -66.8558 | -66.7428 | -0.031692 | -66.7819 | 56.1802 | 56.3626 | 56.1643 | -67.0881 | -0.14135 | -0.05767 | -0.019056 | -0.040683 | 0.10067 | -0.1578 | 0.025647 | -0.37366 | -0.13843 | -0.028328 | -0.067412 | 0.30625 | 0.043903 | -0.15435 | 122.9755 | 122.8753 | 123.0588 | 66.693 | -123.1745 | 122.8947 | 123.077 | 122.8788 | 66.6828 | -123.4068
1458.7969 | 123.1384 | -66.7648 | 56.3416 | 0.0046549 | -0.018256 | 0.00088894 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057604 | 0.027737 | 0.058094 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.1746 | 56.3397 | -66.865 | -66.7382 | -0.031692 | -66.7819 | 56.1757 | 56.3626 | 56.1643 | -67.0881 | -0.10016 | -0.075979 | 0.035876 | 0.023405 | 0.12356 | -0.16695 | -0.00182 | -0.32331 | -0.1659 | 0.026605 | -0.017058 | 0.30625 | 0.021015 | -0.17724 | 123.0304 | 122.9394 | 123.1046 | 66.7342 | -123.2065 | 122.9405 | 123.1274 | 122.9291 | 66.7331 | -123.4297
1459.8594 | 123.1613 | -66.7374 | 56.3736 | -0.010607 | -0.018043 | 0.00067514 | 0.053936 | -0.0058778 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.058031 | 0.027951 | 0.058522 | -66.729 | -0.030644 | -66.7368 | 56.2656 | 56.1792 | 56.3535 | -66.8604 | -66.7474 | -0.031692 | -66.7865 | 56.1711 | 56.358 | 56.1826 | -67.0881 | -0.12304 | -0.10802 | 0.00841 | 0.000518 | 0.12356 | -0.19441 | -0.020127 | -0.35077 | -0.20252 | -0.010019 | -0.049103 | 0.30167 | -0.015607 | -0.19097 | 123.0029 | 122.9166 | 123.0908 | 66.7067 | -123.234 | 122.9084 | 123.0954 | 122.92 | 66.7057 | -123.4617
1460.7969 | 123.1888 | -66.7465 | 56.2958 | -0.0029761 | -0.018256 | 0.00046154 | 0.053936 | -0.0056642 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057817 | 0.028164 | 0.058308 | -66.7335 | -0.026065 | -66.7414 | 56.2702 | 56.1654 | 56.3535 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1711 | 56.3534 | 56.1689 | -67.0927 | -0.11847 | -0.025624 | 0.012987 | 0.005094 | 0.12356 | -0.13033 | 0.057693 | -0.3462 | -0.1247 | 0.003715 | -0.035369 | 0.31083 | 0.057634 | -0.12689 | 123.0167 | 122.912 | 123.1 | 66.7205 | -123.1608 | 122.9176 | 123.0999 | 122.9154 | 66.724 | -123.3885
1461.7969 | 123.111 | -66.7831 | 56.3095 | -0.0029761 | -0.01847 | 0.00088894 | 0.053508 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057176 | 0.027737 | 0.057881 | -66.7335 | -0.030644 | -66.7506 | 56.2747 | 56.17 | 56.3535 | -66.8696 | -66.7474 | -0.036271 | -66.7819 | 56.1665 | 56.3534 | 56.1735 | -67.0973 | -0.086424 | -0.034778 | 0.049608 | 0.032559 | 0.11898 | -0.13948 | 0.04396 | -0.31416 | -0.14301 | 0.035757 | 0.001252 | 0.31541 | 0.043901 | -0.13604 | 123.0579 | 122.9532 | 123.1366 | 66.7525 | -123.1791 | 122.9496 | 123.1366 | 122.9566 | 66.7469 | -123.4068
1462.8594 | 123.2117 | -66.7328 | 56.282 | -0.0029761 | -0.01847 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.027737 | 0.058308 | -66.7244 | -0.021486 | -66.7506 | 56.2702 | 56.1792 | 56.3535 | -66.8604 | -66.7382 | -0.031692 | -66.7819 | 56.1711 | 56.3534 | 56.1735 | -67.0927 | -0.12762 | -0.011891 | 0.008411 | -0.017795 | 0.10983 | -0.10286 | 0.071426 | -0.35993 | -0.11097 | -0.005439 | -0.049102 | 0.31083 | 0.071367 | -0.10858 | 123.0029 | 122.912 | 123.0863 | 66.7113 | -123.1425 | 122.9039 | 123.0862 | 122.9063 | 66.7011 | -123.3748
1463.7969 | 123.1476 | -66.7557 | 56.3187 | -0.0029761 | -0.018043 | 0.00067514 | 0.053936 | -0.0056642 | 0.062076 | -0.0074779 | -0.0024119 | -0.0014101 | 0.058031 | 0.028164 | 0.058094 | -66.729 | -0.026065 | -66.7597 | 56.2702 | 56.1838 | 56.358 | -66.8604 | -66.7428 | -0.027113 | -66.791 | 56.1802 | 56.358 | 56.1597 | -67.0973 | -0.10473 | -0.048513 | 0.02672 | -0.004064 | 0.10067 | -0.1349 | 0.039383 | -0.34162 | -0.13843 | 0.01287 | -0.035371 | 0.30625 | 0.039324 | -0.15893 | 123.0258 | 122.9394 | 123.1137 | 66.7296 | -123.1791 | 122.9359 | 123.1137 | 122.9154 | 66.7286 | -123.416
1464.7969 | 123.2346 | -66.6962 | 56.2729 | 0.0046549 | -0.018256 | 0.00088894 | 0.053722 | -0.0056642 | 0.062076 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057817 | 0.028164 | 0.057881 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.3535 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3534 | 56.1689 | -67.0927 | -0.15966 | -0.002736 | -0.032789 | -0.04526 | 0.1144 | -0.098283 | 0.080581 | -0.39655 | -0.10181 | -0.046639 | -0.090302 | 0.30625 | 0.080522 | -0.104 | 122.9663 | 122.8708 | 123.0496 | 66.6701 | -123.1287 | 122.8672 | 123.0496 | 122.8651 | 66.6645 | -123.3656
1465.8594 | 123.1888 | -66.7145 | 56.3141 | 0.0046549 | -0.018043 | 0.0011025 | 0.053722 | -0.0052368 | 0.062717 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057817 | 0.027737 | 0.058094 | -66.7244 | -0.026065 | -66.746 | 56.2702 | 56.17 | 56.3489 | -66.8604 | -66.7474 | -0.036271 | -66.7773 | 56.1757 | 56.3488 | 56.178 | -67.0927 | -0.14593 | -0.043935 | -0.009899 | -0.031527 | 0.1144 | -0.14406 | 0.034803 | -0.37824 | -0.13843 | -0.032907 | -0.062833 | 0.31541 | 0.034745 | -0.13604 | 122.9846 | 122.8845 | 123.0634 | 66.6884 | -123.1745 | 122.8901 | 123.0633 | 122.8925 | 66.6782 | -123.4068
1466.7969 | 123.262 | -66.6962 | 56.2637 | 0.0046549 | -0.018256 | 0.0013163 | 0.053936 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057817 | 0.028164 | 0.057881 | -66.7335 | -0.021486 | -66.7414 | 56.2747 | 56.1883 | 56.358 | -66.865 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.3488 | 56.1643 | -67.0881 | -0.16882 | 0.010998 | -0.037367 | -0.04526 | 0.12356 | -0.075391 | 0.094315 | -0.39197 | -0.092659 | -0.051218 | -0.090302 | 0.30167 | 0.085099 | -0.099422 | 122.9709 | 122.8845 | 123.0542 | 66.6747 | -123.1287 | 122.8672 | 123.045 | 122.8605 | 66.6599 | -123.3519
1467.8594 | 123.2941 | -66.7236 | 56.2729 | 0.0046549 | -0.018043 | 0.00046154 | 0.053722 | -0.0054506 | 0.062289 | 0.00015261 | -0.0024119 | -0.00034193 | 0.057817 | 0.027737 | 0.058094 | -66.729 | -0.030644 | -66.746 | 56.2702 | 56.1792 | 56.3535 | -66.8604 | -66.7428 | -0.036271 | -66.7819 | 56.1757 | 56.3534 | 56.1735 | -67.0927 | -0.13678 | -0.002736 | -0.005323 | -0.022372 | 0.1144 | -0.093704 | 0.080581 | -0.36909 | -0.097235 | -0.019173 | -0.058257 | 0.31083 | 0.080522 | -0.09942 | 122.9938 | 122.9028 | 123.0771 | 66.693 | -123.1333 | 122.8993 | 123.077 | 122.8971 | 66.6874 | -123.3656
1468.7969 | 123.2758 | -66.7511 | 56.2683 | -0.0029761 | -0.018256 | 0.00067514 | 0.053722 | -0.0054506 | 0.062289 | 0.015414 | -0.0019847 | -0.00076913 | 0.057604 | 0.028164 | 0.058308 | -66.7335 | -0.026065 | -66.746 | 56.2702 | 56.1838 | 56.3535 | -66.8513 | -66.7382 | -0.022535 | -66.7819 | 56.1665 | 56.3534 | 56.178 | -67.0927 | -0.10015 | 0.001841 | 0.017565 | 0.005094 | 0.10525 | -0.084548 | 0.085158 | -0.34162 | -0.10181 | 0.012872 | -0.030791 | 0.31083 | 0.085099 | -0.090265 | 123.0213 | 122.9349 | 123.1046 | 66.725 | -123.1196 | 122.9176 | 123.1045 | 122.9291 | 66.7286 | -123.361
1469.7969 | 123.175 | -66.7557 | 56.3095 | -0.010607 | -0.01847 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058031 | 0.028164 | 0.058308 | -66.7335 | -0.026065 | -66.7506 | 56.2702 | 56.1792 | 56.3489 | -66.8604 | -66.752 | -0.027113 | -66.7819 | 56.1757 | 56.3488 | 56.1735 | -67.0881 | -0.10473 | -0.039357 | 0.022142 | 0.005093 | 0.10983 | -0.13032 | 0.039381 | -0.33246 | -0.13386 | 0.003713 | -0.026214 | 0.30625 | 0.039323 | -0.13604 | 123.0258 | 122.9349 | 123.1046 | 66.7296 | -123.1699 | 122.9313 | 123.1045 | 122.9291 | 66.7286 | -123.3976
1470.7969 | 123.3124 | -66.7282 | 56.2637 | 0.0046549 | -0.01847 | 0.00088894 | 0.054149 | -0.0054506 | 0.062289 | 0.015414 | -0.0021983 | -0.00098273 | 0.057604 | 0.027951 | 0.057667 | -66.729 | -0.021486 | -66.7414 | 56.2702 | 56.1838 | 56.3535 | -66.8604 | -66.7474 | -0.031692 | -66.791 | 56.1711 | 56.3534 | 56.1643 | -67.0881 | -0.1322 | 0.006419 | -0.000746 | -0.013217 | 0.11898 | -0.07997 | 0.089736 | -0.35993 | -0.092659 | -0.019175 | -0.062837 | 0.29709 | 0.089677 | -0.099422 | 122.9984 | 122.912 | 123.0817 | 66.7067 | -123.1241 | 122.8993 | 123.0816 | 122.8925 | 66.6965 | -123.3519
1471.7969 | 123.1567 | -66.7511 | 56.3141 | 0.0046549 | -0.018256 | 0.0011025 | 0.053722 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.028164 | 0.058094 | -66.729 | -0.030644 | -66.7414 | 56.2702 | 56.17 | 56.3535 | -66.8558 | -66.7382 | -0.027113 | -66.7819 | 56.1757 | 56.3488 | 56.178 | -67.0927 | -0.10473 | -0.043935 | 0.022143 | 0.009672 | 0.1144 | -0.14406 | 0.039382 | -0.34162 | -0.13843 | 0.012872 | -0.030791 | 0.31083 | 0.034745 | -0.13604 | 123.0213 | 122.9211 | 123.1046 | 66.7205 | -123.1699 | 122.9268 | 123.0999 | 122.9291 | 66.724 | -123.4068
1472.7969 | 123.2574 | -66.7191 | 56.2866 | -0.018238 | -0.018256 | 0.00088894 | 0.053508 | -0.0056642 | 0.062076 | -0.0074779 | -0.0021983 | -0.00055553 | 0.058245 | 0.028164 | 0.058308 | -66.7335 | -0.021486 | -66.7414 | 56.2702 | 56.1838 | 56.3535 | -66.8558 | -66.7382 | -0.036271 | -66.7865 | 56.1711 | 56.3488 | 56.1643 | -67.0881 | -0.13678 | -0.016469 | -0.014479 | -0.022372 | 0.1144 | -0.10286 | 0.066848 | -0.36909 | -0.11555 | -0.019172 | -0.067414 | 0.30167 | 0.062211 | -0.12231 | 122.9892 | 122.9028 | 123.0725 | 66.6976 | -123.1425 | 122.8901 | 123.0679 | 122.8834 | 66.6828 | -123.3748
1473.7969 | 123.1338 | -66.7557 | 56.3141 | -0.010607 | -0.018256 | 0.00067514 | 0.053722 | -0.0054506 | 0.062503 | -0.0074779 | -0.0021983 | -0.00076913 | 0.058031 | 0.027737 | 0.057667 | -66.7335 | -0.026065 | -66.7368 | 56.2702 | 56.1838 | 56.3535 | -66.8558 | -66.7382 | -0.027113 | -66.791 | 56.1757 | 56.3443 | 56.178 | -67.0927 | -0.10015 | -0.043935 | 0.022142 | 0.018828 | 0.11898 | -0.13032 | 0.039382 | -0.33704 | -0.13843 | 0.017449 | -0.035371 | 0.30167 | 0.030166 | -0.13604 | 123.0258 | 122.9394 | 123.1091 | 66.7296 | -123.1699 | 122.9313 | 123.0999 | 122.9337 | 66.7286 | -123.4068
1474.7969 | 123.2391 | -66.7282 | 56.2775 | -0.0029761 | -0.018256 | 0.0013163 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057604 | 0.027951 | 0.058094 | -66.7335 | -0.026065 | -66.7368 | 56.261 | 56.1838 | 56.358 | -66.865 | -66.7428 | -0.031692 | -66.7819 | 56.1711 | 56.3488 | 56.1597 | -67.0927 | -0.13678 | -0.016471 | -0.005324 | -0.008638 | 0.12814 | -0.093703 | 0.080582 | -0.36451 | -0.10639 | -0.014596 | -0.05368 | 0.31083 | 0.071366 | -0.11773 | 122.9892 | 122.912 | 123.0863 | 66.7021 | -123.1425 | 122.8993 | 123.077 | 122.8879 | 66.6965 | -123.3702
1475.7969 | 123.1705 | -66.774 | 56.3324 | -0.010607 | -0.018256 | 0.00067514 | 0.053936 | -0.0056642 | 0.062503 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057817 | 0.027951 | 0.058094 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1746 | 56.358 | -66.865 | -66.7382 | -0.031692 | -66.791 | 56.1711 | 56.3488 | 56.1643 | -67.0927 | -0.091 | -0.062245 | 0.040453 | 0.027982 | 0.11898 | -0.15779 | 0.025651 | -0.31873 | -0.16132 | 0.03576 | -0.01706 | 0.30167 | 0.016435 | -0.16809 | 123.0441 | 122.9486 | 123.132 | 66.7433 | -123.1974 | 122.9451 | 123.1228 | 122.9383 | 66.7423 | -123.4251
1476.8594 | 123.1613 | -66.7465 | 56.3416 | 0.0046549 | -0.01847 | 0.0011025 | 0.053722 | -0.0056642 | 0.062503 | 0.00015261 | -0.0019847 | -0.00055553 | 0.057817 | 0.027737 | 0.058094 | -66.7244 | -0.026065 | -66.7368 | 56.2702 | 56.1929 | 56.3626 | -66.865 | -66.7428 | -0.036271 | -66.7773 | 56.1757 | 56.3488 | 56.178 | -67.0927 | -0.11847 | -0.071401 | 0.022144 | 0.009673 | 0.12814 | -0.14863 | 0.021073 | -0.3462 | -0.1659 | 0.003715 | -0.03079 | 0.31541 | 0.007279 | -0.16351 | 123.0167 | 122.9394 | 123.1091 | 66.7205 | -123.2065 | 122.9222 | 123.0954 | 122.9246 | 66.7103 | -123.4343
1477.7969 | 123.2254 | -66.7145 | 56.2775 | -0.0029761 | -0.01847 | 0.00046154 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057604 | 0.027951 | 0.057881 | -66.7335 | -0.030644 | -66.746 | 56.2656 | 56.17 | 56.358 | -66.8604 | -66.7336 | -0.027113 | -66.7865 | 56.1711 | 56.3488 | 56.1964 | -67.0927 | -0.14593 | -0.011892 | -0.019056 | -0.031527 | 0.1144 | -0.10744 | 0.080582 | -0.37824 | -0.10639 | -0.019171 | -0.071991 | 0.30625 | 0.071366 | -0.081105 | 122.9801 | 122.8845 | 123.0725 | 66.6838 | -123.1379 | 122.8856 | 123.0633 | 122.9108 | 66.6874 | -123.3702
1478.7969 | 123.2849 | -66.7191 | 56.2729 | -0.0029761 | -0.018256 | 0.00088894 | 0.053508 | -0.0054506 | 0.061862 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057604 | 0.028378 | 0.057881 | -66.7244 | -0.021486 | -66.7414 | 56.2656 | 56.17 | 56.3626 | -66.8558 | -66.7428 | -0.017956 | -66.7865 | 56.1757 | 56.3626 | 56.1689 | -67.0881 | -0.13678 | -0.007314 | -0.005322 | -0.022372 | 0.1144 | -0.10286 | 0.089738 | -0.36909 | -0.097235 | -0.023751 | -0.067414 | 0.30167 | 0.08968 | -0.104 | 122.9846 | 122.8891 | 123.0817 | 66.6976 | -123.1287 | 122.8947 | 123.0816 | 122.8879 | 66.7011 | -123.361
1479.7969 | 123.3032 | -66.7282 | 56.2683 | -0.0029761 | -0.018256 | 0.00067514 | 0.053936 | -0.0056642 | 0.062503 | 0.015414 | -0.0019847 | -0.00098273 | 0.057176 | 0.027951 | 0.058094 | -66.7335 | -0.030644 | -66.7368 | 56.261 | 56.1838 | 56.3535 | -66.865 | -66.7428 | -0.027113 | -66.791 | 56.1711 | 56.3488 | 56.1735 | -67.0973 | -0.13678 | -0.007316 | -0.005324 | -0.008638 | 0.12814 | -0.084548 | 0.085158 | -0.36909 | -0.097237 | -0.014596 | -0.062837 | 0.30625 | 0.080521 | -0.094843 | 122.9892 | 122.912 | 123.0817 | 66.6976 | -123.1333 | 122.8993 | 123.077 | 122.9017 | 66.7011 | -123.3656
1480.7969 | 123.2666 | -66.7191 | 56.2912 | -0.0029761 | -0.018684 | 0.00088894 | 0.053936 | -0.0052368 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.05739 | 0.027737 | 0.058094 | -66.729 | -0.021486 | -66.7368 | 56.261 | 56.1746 | 56.358 | -66.8604 | -66.7382 | -0.036271 | -66.7865 | 56.1757 | 56.3488 | 56.1552 | -67.0881 | -0.14135 | -0.030204 | -0.009901 | -0.017793 | 0.12356 | -0.11659 | 0.066849 | -0.36909 | -0.11555 | -0.019172 | -0.067414 | 0.30167 | 0.057633 | -0.13605 | 122.9801 | 122.8937 | 123.0771 | 66.6976 | -123.1516 | 122.8947 | 123.0679 | 122.8742 | 66.6828 | -123.3793
1481.8594 | 123.1705 | -66.7374 | 56.3416 | 0.0046549 | -0.018256 | 0.00046154 | 0.053295 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057817 | 0.027951 | 0.058094 | -66.729 | -0.026065 | -66.7368 | 56.2702 | 56.1883 | 56.3626 | -66.8558 | -66.7474 | -0.027113 | -66.7819 | 56.1665 | 56.3488 | 56.1597 | -67.0973 | -0.11846 | -0.071401 | 0.00841 | 0.000518 | 0.11898 | -0.15321 | 0.021073 | -0.35993 | -0.17506 | -0.010019 | -0.044524 | 0.31541 | 0.007279 | -0.18182 | 123.0075 | 122.9257 | 123.1 | 66.7113 | -123.1974 | 122.9039 | 123.0862 | 122.8971 | 66.7103 | -123.4389
1482.7969 | 123.2712 | -66.7236 | 56.2683 | -0.0029761 | -0.018043 | 0.00088894 | 0.054149 | -0.0058778 | 0.062289 | -0.0074779 | -0.0024119 | -0.00076913 | 0.058031 | 0.028378 | 0.058094 | -66.7335 | -0.026065 | -66.7368 | 56.2656 | 56.17 | 56.3626 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1757 | 56.3488 | 56.1826 | -67.0927 | -0.13678 | -0.002737 | -0.009901 | -0.013215 | 0.12356 | -0.098285 | 0.094315 | -0.36909 | -0.092658 | -0.023752 | -0.062836 | 0.30625 | 0.080521 | -0.085686 | 122.9892 | 122.8937 | 123.0863 | 66.6976 | -123.1287 | 122.8993 | 123.0725 | 122.9063 | 66.6874 | -123.361
1483.7969 | 123.2803 | -66.7191 | 56.2546 | -0.0029761 | -0.01847 | 0.00046154 | 0.053936 | -0.0056642 | 0.062717 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.028164 | 0.057881 | -66.7335 | -0.021486 | -66.7368 | 56.2702 | 56.1654 | 56.358 | -66.8558 | -66.7428 | -0.027113 | -66.7865 | 56.1757 | 56.3626 | 56.1826 | -67.0973 | -0.13678 | 0.015574 | -0.014479 | -0.017793 | 0.11898 | -0.089131 | 0.10347 | -0.37824 | -0.078925 | -0.023751 | -0.067414 | 0.31083 | 0.10799 | -0.071953 | 122.9892 | 122.8845 | 123.0771 | 66.6976 | -123.1104 | 122.8947 | 123.0816 | 122.9017 | 66.6919 | -123.3519
1484.8594 | 123.1338 | -66.7831 | 56.3324 | -0.010607 | -0.018256 | 0.00088894 | 0.053722 | -0.0058778 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057817 | 0.027737 | 0.058308 | -66.7335 | -0.021486 | -66.7323 | 56.2747 | 56.1883 | 56.3535 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3488 | 56.1872 | -67.0927 | -0.081845 | -0.057666 | 0.049608 | 0.050872 | 0.13272 | -0.14406 | 0.021072 | -0.30958 | -0.15217 | 0.040336 | 0.001252 | 0.31083 | 0.016435 | -0.14519 | 123.0579 | 122.9715 | 123.1366 | 66.7617 | -123.1974 | 122.9634 | 123.132 | 122.9703 | 66.756 | -123.4251
1485.7969 | 123.2529 | -66.6962 | 56.2866 | 0.0046549 | -0.01847 | 0.00088894 | 0.053508 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.027951 | 0.058094 | -66.7244 | -0.021486 | -66.7368 | 56.2656 | 56.1792 | 56.3535 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.358 | 56.1643 | -67.1019 | -0.16882 | -0.021047 | -0.02821 | -0.040681 | 0.12814 | -0.10744 | 0.066848 | -0.40571 | -0.11097 | -0.046639 | -0.085723 | 0.31999 | 0.071368 | -0.12231 | 122.9617 | 122.8754 | 123.0496 | 66.6747 | -123.1516 | 122.8718 | 123.0542 | 122.8605 | 66.6691 | -123.3885
1486.7969 | 123.3536 | -66.6916 | 56.2637 | -0.010607 | -0.01847 | 0.00088894 | 0.053936 | -0.0054506 | 0.062289 | 0.015414 | -0.0017711 | -0.00055553 | 0.057604 | 0.028164 | 0.057881 | -66.7381 | -0.021486 | -66.7368 | 56.2747 | 56.1746 | 56.358 | -66.8604 | -66.7336 | -0.022535 | -66.7819 | 56.1757 | 56.3534 | 56.1735 | -67.0927 | -0.16882 | 0.010998 | -0.046523 | -0.045259 | 0.12356 | -0.089128 | 0.094315 | -0.40113 | -0.08808 | -0.04206 | -0.090301 | 0.31083 | 0.089677 | -0.090265 | 122.9663 | 122.8662 | 123.0496 | 66.6701 | -123.1241 | 122.8672 | 123.045 | 122.8651 | 66.6691 | -123.3565
1487.8594 | 123.2483 | -66.7511 | 56.3049 | -0.0029761 | -0.018684 | 0.00067514 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.057604 | 0.028164 | 0.057881 | -66.7244 | -0.021486 | -66.7323 | 56.2747 | 56.1838 | 56.3626 | -66.865 | -66.7291 | -0.022535 | -66.7819 | 56.1711 | 56.358 | 56.1643 | -67.0973 | -0.11389 | -0.030201 | 0.026722 | 0.018829 | 0.13272 | -0.12117 | 0.057694 | -0.3462 | -0.13386 | 0.022029 | -0.030791 | 0.31541 | 0.053057 | -0.14062 | 123.0258 | 122.9349 | 123.1137 | 66.7296 | -123.1699 | 122.9222 | 123.1091 | 122.9154 | 66.7286 | -123.4022
1488.7969 | 123.2712 | -66.7282 | 56.3049 | -0.0029761 | -0.01847 | 0.0011025 | 0.054149 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057604 | 0.027737 | 0.057881 | -66.729 | -0.026065 | -66.7277 | 56.2656 | 56.1838 | 56.358 | -66.8558 | -66.7291 | -0.031692 | -66.7727 | 56.1711 | 56.3626 | 56.1735 | -67.0836 | -0.12762 | -0.039358 | -0.000746 | 0.000518 | 0.12814 | -0.12117 | 0.053116 | -0.35535 | -0.13386 | -0.00086 | -0.044522 | 0.31083 | 0.057636 | -0.13146 | 122.9938 | 122.912 | 123.0863 | 66.7021 | -123.1608 | 122.8993 | 123.0908 | 122.9017 | 66.6965 | -123.3885
1489.7969 | 123.2574 | -66.7328 | 56.2866 | -0.010607 | -0.01847 | 0.00067514 | 0.053722 | -0.0054506 | 0.062289 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.027737 | 0.057881 | -66.7244 | -0.026065 | -66.7368 | 56.2702 | 56.1883 | 56.3672 | -66.8604 | -66.7336 | -0.027113 | -66.7819 | 56.1665 | 56.3534 | 56.1735 | -67.0927 | -0.12762 | -0.016469 | 0.008411 | -0.00406 | 0.12356 | -0.098279 | 0.080584 | -0.35993 | -0.12012 | -0.000861 | -0.049102 | 0.31083 | 0.066789 | -0.11315 | 123.0029 | 122.9211 | 123.1 | 66.7067 | -123.147 | 122.8993 | 123.0862 | 122.9063 | 66.7057 | -123.3793
1490.7969 | 123.2391 | -66.7419 | 56.3004 | -0.0029761 | -0.018256 | 0.00088894 | 0.053936 | -0.0054506 | 0.062076 | -0.0074779 | -0.0019847 | -0.00076913 | 0.05739 | 0.028164 | 0.057881 | -66.729 | -0.026065 | -66.7368 | 56.2702 | 56.1792 | 56.3535 | -66.8558 | -66.7428 | -0.022535 | -66.791 | 56.1757 | 56.3534 | 56.1506 | -67.0927 | -0.11389 | -0.030202 | 0.012987 | 0.005095 | 0.11898 | -0.12117 | 0.053115 | -0.35078 | -0.1247 | -0.000863 | -0.049104 | 0.30167 | 0.053056 | -0.14978 | 123.0121 | 122.9211 | 123.0954 | 66.7159 | -123.1562 | 122.9176 | 123.0954 | 122.8925 | 66.7194 | -123.3931
1491.8594 | 123.1796 | -66.7465 | 56.3095 | -0.0029761 | -0.01847 | 0.00088894 | 0.053936 | -0.0058778 | 0.062289 | -0.0074779 | -0.0021983 | -0.00055553 | 0.057604 | 0.028378 | 0.057881 | -66.729 | -0.021486 | -66.7368 | 56.2656 | 56.1838 | 56.3535 | -66.8604 | -66.7382 | -0.031692 | -66.7773 | 56.1757 | 56.3534 | 56.1689 | -67.0927 | -0.11389 | -0.043935 | 0.017565 | 0.009673 | 0.12356 | -0.12575 | 0.04396 | -0.3462 | -0.13386 | 0.008294 | -0.03079 | 0.31541 | 0.043901 | -0.14062 | 123.0121 | 122.9303 | 123.1 | 66.725 | -123.1699 | 122.9222 | 123.0999 | 122.9154 | 66.7148 | -123.4022
1492.7969 | 123.2346 | -66.7191 | 56.3095 | -0.010607 | -0.018684 | 0.0011025 | 0.053722 | -0.0056642 | 0.061862 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057604 | 0.027951 | 0.057667 | -66.7244 | -0.026065 | -66.7506 | 56.2702 | 56.1792 | 56.3626 | -66.8604 | -66.7474 | -0.036271 | -66.791 | 56.1757 | 56.3488 | 56.1735 | -67.0927 | -0.14135 | -0.039357 | -0.005322 | -0.031528 | 0.10983 | -0.13032 | 0.053117 | -0.37367 | -0.13386 | -0.02833 | -0.071992 | 0.30167 | 0.039323 | -0.13604 | 122.9892 | 122.8982 | 123.0817 | 66.693 | -123.1699 | 122.8947 | 123.0679 | 122.8925 | 66.6828 | -123.4022
1493.7969 | 123.2483 | -66.7145 | 56.2775 | -0.010607 | -0.018684 | 0.00088894 | 0.053722 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00055553 | 0.058031 | 0.028378 | 0.058308 | -66.7335 | -0.021486 | -66.7506 | 56.2702 | 56.1609 | 56.3626 | -66.8513 | -66.7428 | -0.036271 | -66.7865 | 56.1711 | 56.3534 | 56.1689 | -67.0881 | -0.13677 | -0.007314 | -0.019056 | -0.036105 | 0.10067 | -0.1166 | 0.08516 | -0.37366 | -0.10639 | -0.028328 | -0.071991 | 0.30167 | 0.075944 | -0.10858 | 122.9846 | 122.8753 | 123.0771 | 66.693 | -123.1287 | 122.8856 | 123.0679 | 122.8834 | 66.6782 | -123.3656
1494.8594 | 123.2529 | -66.7374 | 56.2866 | 0.0046549 | -0.018897 | 0.00067514 | 0.054149 | -0.0056642 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057604 | 0.028164 | 0.058094 | -66.7244 | -0.030644 | -66.7506 | 56.261 | 56.1838 | 56.358 | -66.8558 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.3534 | 56.1643 | -67.0927 | -0.11846 | -0.025626 | 0.012989 | -0.013217 | 0.10525 | -0.10286 | 0.071427 | -0.35535 | -0.11097 | -0.00544 | -0.049103 | 0.30625 | 0.066789 | -0.12231 | 122.9984 | 122.9211 | 123.0954 | 66.7067 | -123.1425 | 122.913 | 123.0908 | 122.9017 | 66.7057 | -123.3793
1495.7969 | 123.2666 | -66.7282 | 56.2454 | -0.010607 | -0.018684 | 0.00088894 | 0.053722 | -0.0052368 | 0.062503 | 0.0077831 | -0.0021983 | -0.00098273 | 0.057817 | 0.028164 | 0.058094 | -66.7244 | -0.026065 | -66.7506 | 56.2702 | 56.17 | 56.358 | -66.8604 | -66.7382 | -0.031692 | -66.7819 | 56.1757 | 56.3488 | 56.1735 | -67.0927 | -0.1322 | 0.02473 | 0.003833 | -0.022373 | 0.10983 | -0.075396 | 0.11263 | -0.36451 | -0.069769 | -0.010017 | -0.05368 | 0.31083 | 0.10341 | -0.071954 | 122.9984 | 122.8982 | 123.0863 | 66.7021 | -123.1058 | 122.9039 | 123.077 | 122.9017 | 66.6965 | -123.3381
1496.8594 | 123.2483 | -66.7053 | 56.282 | -0.0029761 | -0.018684 | 0.00046154 | 0.054149 | -0.0056642 | 0.062289 | 0.00015261 | -0.0019847 | -0.00098273 | 0.058031 | 0.028378 | 0.057667 | -66.7244 | -0.026065 | -66.746 | 56.261 | 56.1883 | 56.3626 | -66.865 | -66.7474 | -0.027113 | -66.791 | 56.1757 | 56.3534 | 56.1826 | -67.0881 | -0.15967 | -0.021048 | -0.019055 | -0.040683 | 0.11898 | -0.093701 | 0.080583 | -0.38282 | -0.10639 | -0.042063 | -0.085725 | 0.29709 | 0.071367 | -0.099418 | 122.9663 | 122.8937 | 123.0679 | 66.6793 | -123.147 | 122.881 | 123.0587 | 122.8879 | 66.6782 | -123.3702
1497.7969 | 123.23 | -66.7282 | 56.2683 | -0.0029761 | -0.018684 | 0.00067514 | 0.053722 | -0.0056642 | 0.062717 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.028378 | 0.057881 | -66.729 | -0.021486 | -66.7414 | 56.2702 | 56.1792 | 56.358 | -66.8604 | -66.7428 | -0.031692 | -66.7819 | 56.1757 | 56.3534 | 56.1872 | -67.0973 | -0.1322 | 0.001841 | -0.000746 | -0.013217 | 0.11898 | -0.089127 | 0.089737 | -0.36909 | -0.092658 | -0.014596 | -0.05368 | 0.31541 | 0.085099 | -0.081107 | 122.9984 | 122.9074 | 123.0863 | 66.7067 | -123.1287 | 122.9039 | 123.0816 | 122.9154 | 66.6965 | -123.3656
1498.7969 | 123.2162 | -66.7328 | 56.3232 | -0.010607 | -0.018684 | 0.00067514 | 0.054149 | -0.0058778 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.05739 | 0.028378 | 0.057881 | -66.729 | -0.026065 | -66.7368 | 56.2702 | 56.1838 | 56.3535 | -66.8558 | -66.7428 | -0.036271 | -66.7865 | 56.1802 | 56.3488 | 56.178 | -67.0927 | -0.12304 | -0.05309 | 0.003832 | -0.00406 | 0.11898 | -0.13948 | 0.030227 | -0.35993 | -0.14301 | -0.010018 | -0.053681 | 0.30625 | 0.02559 | -0.1452 | 123.0029 | 122.9166 | 123.0863 | 66.7067 | -123.1791 | 122.913 | 123.0816 | 122.9108 | 66.6965 | -123.416
1499.7969 | 123.2986 | -66.7236 | 56.3049 | -0.0029761 | -0.018684 | 0.00088894 | 0.053722 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.028378 | 0.058094 | -66.7244 | -0.030644 | -66.7414 | 56.2702 | 56.1746 | 56.3626 | -66.8604 | -66.7474 | -0.027113 | -66.7819 | 56.1665 | 56.3534 | 56.1826 | -67.0881 | -0.13678 | -0.03478 | -0.000744 | -0.017794 | 0.11898 | -0.13033 | 0.057694 | -0.36451 | -0.13844 | -0.023752 | -0.058257 | 0.30625 | 0.048478 | -0.12231 | 122.9938 | 122.8982 | 123.0863 | 66.693 | -123.1653 | 122.8901 | 123.077 | 122.9063 | 66.6965 | -123.3931
1500.7969 | 123.2117 | -66.7007 | 56.2958 | 0.0046549 | -0.018684 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057604 | 0.027951 | 0.058094 | -66.729 | -0.021486 | -66.7414 | 56.261 | 56.1792 | 56.358 | -66.8558 | -66.7382 | -0.031692 | -66.7773 | 56.1757 | 56.3534 | 56.1689 | -67.0973 | -0.15508 | -0.034781 | -0.028211 | -0.040682 | 0.1144 | -0.11659 | 0.062272 | -0.39655 | -0.12012 | -0.037482 | -0.076566 | 0.31999 | 0.057634 | -0.12689 | 122.9617 | 122.8799 | 123.0588 | 66.6793 | -123.1516 | 122.8764 | 123.0542 | 122.8696 | 66.6691 | -123.3931
1501.7969 | 123.2712 | -66.6962 | 56.2912 | -0.018238 | -0.019111 | 0.0011025 | 0.053936 | -0.0056642 | 0.062289 | 0.0077831 | -0.0024119 | -0.00076913 | 0.05739 | 0.028164 | 0.058094 | -66.7335 | -0.026065 | -66.7414 | 56.2656 | 56.1792 | 56.358 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.3626 | 56.1826 | -67.0927 | -0.16882 | -0.025625 | -0.037367 | -0.04526 | 0.12356 | -0.11201 | 0.066849 | -0.39655 | -0.12013 | -0.046639 | -0.085723 | 0.31083 | 0.071369 | -0.10857 | 122.9617 | 122.8754 | 123.0542 | 66.6701 | -123.1562 | 122.8672 | 123.0587 | 122.8788 | 66.6691 | -123.3839
1502.8594 | 123.175 | -66.7374 | 56.3507 | 0.0046549 | -0.018684 | 0.0011025 | 0.053722 | -0.0056642 | 0.062289 | -0.0074779 | -0.0028393 | -0.00076913 | 0.05739 | 0.028378 | 0.057667 | -66.729 | -0.021486 | -66.746 | 56.2702 | 56.1929 | 56.3626 | -66.8604 | -66.7382 | -0.022535 | -66.7865 | 56.1711 | 56.3534 | 56.1826 | -67.0927 | -0.12304 | -0.080556 | 0.00841 | -0.008639 | 0.1144 | -0.15779 | 0.011918 | -0.35535 | -0.17963 | -0.000861 | -0.049103 | 0.30625 | 0.002702 | -0.16808 | 123.0075 | 122.9303 | 123.1 | 66.7159 | -123.2111 | 122.9084 | 123.0908 | 122.92 | 66.7148 | -123.4434
1503.7969 | 123.23 | -66.687 | 56.2546 | -0.010607 | -0.018684 | 0.0011025 | 0.053936 | -0.0054506 | 0.062503 | 0.0077831 | -0.0019847 | -0.00076913 | 0.057604 | 0.028592 | 0.058094 | -66.7244 | -0.026065 | -66.746 | 56.2656 | 56.1838 | 56.3626 | -66.865 | -66.7336 | -0.027113 | -66.7865 | 56.1802 | 56.3534 | 56.178 | -67.0927 | -0.17798 | 0.010996 | -0.037365 | -0.058993 | 0.11898 | -0.070815 | 0.10805 | -0.40571 | -0.074347 | -0.046637 | -0.099457 | 0.30625 | 0.098832 | -0.076532 | 122.9526 | 122.8708 | 123.0496 | 66.6609 | -123.1196 | 122.8672 | 123.0404 | 122.8651 | 66.6599 | -123.3473
1504.8594 | 123.2803 | -66.6733 | 56.2866 | 0.0046549 | -0.018684 | 0.0011025 | 0.053508 | -0.0056642 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.057604 | 0.028592 | 0.057667 | -66.7244 | -0.030644 | -66.746 | 56.2702 | 56.1838 | 56.358 | -66.8604 | -66.7428 | -0.031692 | -66.791 | 56.1665 | 56.358 | 56.1826 | -67.0927 | -0.18713 | -0.016469 | -0.051098 | -0.072726 | 0.1144 | -0.10286 | 0.071427 | -0.41944 | -0.12012 | -0.069527 | -0.11777 | 0.30167 | 0.071368 | -0.104 | 122.9434 | 122.857 | 123.0313 | 66.6426 | -123.147 | 122.8398 | 123.0313 | 122.8559 | 66.6416 | -123.3793
1505.7969 | 123.2712 | -66.7236 | 56.282 | 0.0046549 | -0.018684 | 0.00067514 | 0.053722 | -0.0056642 | 0.062717 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057817 | 0.028592 | 0.057881 | -66.729 | -0.021486 | -66.7414 | 56.261 | 56.1838 | 56.358 | -66.8604 | -66.7428 | -0.027113 | -66.791 | 56.1711 | 56.3534 | 56.178 | -67.0927 | -0.13678 | -0.021048 | -0.005323 | -0.017794 | 0.11898 | -0.09828 | 0.076005 | -0.36909 | -0.11097 | -0.019173 | -0.067414 | 0.30167 | 0.071367 | -0.104 | 122.9846 | 122.9074 | 123.0817 | 66.7021 | -123.1425 | 122.8947 | 123.077 | 122.9017 | 66.6965 | -123.3748
1506.7969 | 123.2071 | -66.7191 | 56.2912 | -0.0029761 | -0.018684 | 0.00088894 | 0.053508 | -0.0056642 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057604 | 0.028592 | 0.058094 | -66.7244 | -0.021486 | -66.7414 | 56.2702 | 56.1838 | 56.3626 | -66.8604 | -66.7428 | -0.031692 | -66.791 | 56.1757 | 56.3534 | 56.1735 | -67.1019 | -0.14135 | -0.021047 | -0.005322 | -0.022372 | 0.11898 | -0.10744 | 0.071427 | -0.38282 | -0.11555 | -0.023751 | -0.071992 | 0.31083 | 0.062211 | -0.11773 | 122.9892 | 122.9028 | 123.0817 | 66.6976 | -123.1516 | 122.8947 | 123.0725 | 122.8925 | 66.6874 | -123.3931
1507.7969 | 123.2803 | -66.7099 | 56.2912 | -0.0029761 | -0.018897 | 0.00088894 | 0.053936 | -0.0056642 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.057604 | 0.028378 | 0.058094 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1838 | 56.358 | -66.8558 | -66.7382 | -0.022535 | -66.791 | 56.1757 | 56.3488 | 56.1735 | -67.0927 | -0.14593 | -0.021047 | -0.023634 | -0.036105 | 0.10983 | -0.10744 | 0.066849 | -0.38282 | -0.11555 | -0.028327 | -0.081147 | 0.30167 | 0.057633 | -0.11773 | 122.9801 | 122.8937 | 123.0679 | 66.6793 | -123.147 | 122.8856 | 123.0587 | 122.8834 | 66.6874 | -123.3839
1508.7969 | 123.2162 | -66.7007 | 56.3187 | 0.0046549 | -0.019111 | 0.00067514 | 0.053722 | -0.0058778 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.058245 | 0.028592 | 0.057881 | -66.7381 | -0.026065 | -66.7414 | 56.2702 | 56.1746 | 56.358 | -66.8604 | -66.7382 | -0.031692 | -66.7865 | 56.1757 | 56.358 | 56.178 | -67.0881 | -0.15966 | -0.048513 | -0.037367 | -0.040682 | 0.11898 | -0.14406 | 0.039383 | -0.3874 | -0.14301 | -0.037482 | -0.085724 | 0.30167 | 0.039324 | -0.14062 | 122.9709 | 122.8753 | 123.0588 | 66.6747 | -123.1791 | 122.8764 | 123.0587 | 122.8788 | 66.6691 | -123.4068
1509.8594 | 123.2071 | -66.7145 | 56.3004 | -0.0029761 | -0.018897 | 0.00088894 | 0.053508 | -0.0056642 | 0.062503 | -0.0074779 | -0.0026255 | -0.00055553 | 0.057817 | 0.028378 | 0.058094 | -66.729 | -0.026065 | -66.746 | 56.2702 | 56.1929 | 56.358 | -66.8604 | -66.7428 | -0.027113 | -66.791 | 56.1757 | 56.358 | 56.1643 | -67.0927 | -0.14593 | -0.030202 | -0.014478 | -0.031527 | 0.1144 | -0.10743 | 0.057694 | -0.37824 | -0.1247 | -0.028328 | -0.076569 | 0.30167 | 0.057635 | -0.13604 | 122.9846 | 122.9074 | 123.0725 | 66.6884 | -123.1608 | 122.8901 | 123.0725 | 122.8788 | 66.6874 | -123.3931
1510.7969 | 123.2483 | -66.687 | 56.3049 | -0.010607 | -0.018684 | 0.00067514 | 0.054149 | -0.0058778 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057817 | 0.028378 | 0.058308 | -66.729 | -0.030644 | -66.7414 | 56.2747 | 56.1838 | 56.3535 | -66.865 | -66.7474 | -0.036271 | -66.7865 | 56.1757 | 56.3534 | 56.1826 | -67.0881 | -0.17798 | -0.030201 | -0.041944 | -0.054415 | 0.12356 | -0.12117 | 0.048537 | -0.40113 | -0.12928 | -0.060373 | -0.099457 | 0.30167 | 0.048478 | -0.12231 | 122.9617 | 122.8708 | 123.0405 | 66.6564 | -123.1699 | 122.8627 | 123.0404 | 122.8696 | 66.6507 | -123.3931
1511.8594 | 123.2162 | -66.7145 | 56.3232 | -0.0029761 | -0.018897 | 0.00067514 | 0.054149 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.028592 | 0.058094 | -66.7335 | -0.035222 | -66.7552 | 56.2793 | 56.1883 | 56.3672 | -66.865 | -66.752 | -0.031692 | -66.7819 | 56.1757 | 56.3534 | 56.1872 | -67.1019 | -0.15051 | -0.043933 | -0.019056 | -0.040683 | 0.10983 | -0.1349 | 0.043963 | -0.3874 | -0.14759 | -0.037485 | -0.067412 | 0.31999 | 0.030168 | -0.13604 | 122.9938 | 122.9028 | 123.0817 | 66.6793 | -123.1882 | 122.8901 | 123.0679 | 122.9017 | 66.6828 | -123.4251
1512.7969 | 123.2529 | -66.7007 | 56.2958 | -0.0029761 | -0.018897 | 0.00088894 | 0.054363 | -0.0056642 | 0.062503 | 0.0077831 | -0.0021983 | -0.00055553 | 0.057817 | 0.028805 | 0.057881 | -66.7244 | -0.030644 | -66.746 | 56.2702 | 56.1838 | 56.3535 | -66.8558 | -66.7428 | -0.027113 | -66.7819 | 56.1665 | 56.358 | 56.1689 | -67.0927 | -0.15508 | -0.025624 | -0.023632 | -0.04526 | 0.10983 | -0.11201 | 0.057693 | -0.39198 | -0.12928 | -0.042061 | -0.081145 | 0.31083 | 0.062213 | -0.12689 | 122.9709 | 122.8845 | 123.0542 | 66.6701 | -123.1516 | 122.8672 | 123.0587 | 122.8696 | 66.6736 | -123.3885
1513.7969 | 123.2666 | -66.7236 | 56.2958 | 0.0046549 | -0.018897 | 0.00088894 | 0.053508 | -0.0058778 | 0.062076 | 0.00015261 | -0.0024119 | -0.00055553 | 0.05739 | 0.028592 | 0.058094 | -66.7244 | -0.030644 | -66.7414 | 56.2702 | 56.1838 | 56.3626 | -66.8604 | -66.7474 | -0.031692 | -66.7727 | 56.1757 | 56.3534 | 56.1597 | -67.0973 | -0.13678 | -0.025624 | -0.000744 | -0.017794 | 0.11898 | -0.11201 | 0.06685 | -0.37367 | -0.12012 | -0.023752 | -0.049099 | 0.32457 | 0.057634 | -0.13604 | 122.9938 | 122.9074 | 123.0863 | 66.693 | -123.1562 | 122.8993 | 123.077 | 122.8834 | 66.6919 | -123.3931
1514.8594 | 123.2391 | -66.7191 | 56.3141 | -0.010607 | -0.018684 | 0.00088894 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.028164 | 0.058094 | -66.7381 | -0.035222 | -66.746 | 56.2747 | 56.1838 | 56.358 | -66.865 | -66.7428 | -0.031692 | -66.7819 | 56.1802 | 56.3534 | 56.1597 | -67.0927 | -0.14593 | -0.039356 | -0.019057 | -0.02695 | 0.11898 | -0.13032 | 0.043961 | -0.37367 | -0.13386 | -0.023751 | -0.062835 | 0.31083 | 0.039323 | -0.15436 | 122.9938 | 122.9028 | 123.0771 | 66.6838 | -123.1791 | 122.8993 | 123.0725 | 122.8788 | 66.6874 | -123.4068
1515.7969 | 123.2254 | -66.7557 | 56.3004 | -0.0029761 | -0.018684 | 0.00067514 | 0.053936 | -0.0054506 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.05739 | 0.029019 | 0.057881 | -66.729 | -0.030644 | -66.7506 | 56.2656 | 56.1838 | 56.358 | -66.865 | -66.7428 | -0.031692 | -66.7773 | 56.1757 | 56.358 | 56.1597 | -67.0973 | -0.10931 | -0.03478 | 0.02672 | 0.005093 | 0.1144 | -0.11659 | 0.057694 | -0.34162 | -0.1247 | 0.01287 | -0.021635 | 0.31999 | 0.057635 | -0.14062 | 123.0212 | 122.9394 | 123.1137 | 66.725 | -123.1653 | 122.9313 | 123.1137 | 122.9154 | 66.724 | -123.3977
1516.8594 | 123.2254 | -66.7511 | 56.337 | -0.0029761 | -0.018897 | 0.00088894 | 0.053722 | -0.0056642 | 0.062717 | -0.0074779 | -0.0024119 | -0.00076913 | 0.05739 | 0.028378 | 0.057881 | -66.7244 | -0.026065 | -66.7506 | 56.2747 | 56.1929 | 56.3672 | -66.865 | -66.7474 | -0.027113 | -66.791 | 56.1757 | 56.3488 | 56.2009 | -67.0927 | -0.11389 | -0.062244 | 0.026722 | 0.000516 | 0.1144 | -0.14405 | 0.03023 | -0.34162 | -0.16132 | 0.003714 | -0.039948 | 0.30167 | 0.011857 | -0.13604 | 123.0258 | 122.944 | 123.1183 | 66.725 | -123.202 | 122.9268 | 123.0999 | 122.952 | 66.724 | -123.4297
1517.7969 | 123.2391 | -66.7145 | 56.282 | -0.0029761 | -0.018684 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.028805 | 0.058094 | -66.729 | -0.021486 | -66.7323 | 56.2702 | 56.1929 | 56.358 | -66.865 | -66.7382 | -0.027113 | -66.7819 | 56.1757 | 56.3534 | 56.1643 | -67.0973 | -0.15051 | -0.011891 | -0.014478 | -0.017792 | 0.13272 | -0.089122 | 0.076005 | -0.38282 | -0.10639 | -0.023749 | -0.067412 | 0.31541 | 0.071367 | -0.11773 | 122.9846 | 122.9074 | 123.0725 | 66.693 | -123.147 | 122.8901 | 123.0679 | 122.8788 | 66.6874 | -123.3793
1518.7969 | 123.2895 | -66.7145 | 56.3141 | 0.012286 | -0.018897 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0019847 | -0.00076913 | 0.05739 | 0.028592 | 0.057881 | -66.729 | -0.021486 | -66.7368 | 56.2656 | 56.1838 | 56.3535 | -66.8604 | -66.752 | -0.036271 | -66.791 | 56.1665 | 56.3488 | 56.1689 | -67.0927 | -0.14593 | -0.048513 | -0.014478 | -0.02237 | 0.12356 | -0.13032 | 0.039382 | -0.37824 | -0.14759 | -0.037485 | -0.076569 | 0.30167 | 0.034745 | -0.1452 | 122.9801 | 122.8982 | 123.0679 | 66.693 | -123.1745 | 122.881 | 123.0633 | 122.8834 | 66.6782 | -123.4068
1519.7969 | 123.2254 | -66.7236 | 56.3095 | -0.0029761 | -0.019111 | 0.00088894 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.028592 | 0.057881 | -66.729 | -0.021486 | -66.7368 | 56.2702 | 56.1792 | 56.358 | -66.8604 | -66.7428 | -0.031692 | -66.7865 | 56.1711 | 56.3488 | 56.178 | -67.0927 | -0.13678 | -0.039357 | -0.005323 | -0.013215 | 0.12356 | -0.13032 | 0.048539 | -0.36909 | -0.13844 | -0.019173 | -0.062836 | 0.30625 | 0.039323 | -0.13146 | 122.9938 | 122.9028 | 123.0817 | 66.7021 | -123.1699 | 122.8947 | 123.0725 | 122.9017 | 66.6919 | -123.4022
1520.8594 | 123.262 | -66.7145 | 56.2775 | -0.0029761 | -0.019111 | 0.00024794 | 0.053722 | -0.0058778 | 0.062503 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057604 | 0.028592 | 0.058094 | -66.7244 | -0.016908 | -66.7506 | 56.2656 | 56.1883 | 56.3626 | -66.8513 | -66.7428 | -0.027113 | -66.7819 | 56.1894 | 56.358 | 56.1735 | -67.0973 | -0.13677 | -0.011892 | -0.009899 | -0.036105 | 0.10067 | -0.089124 | 0.08516 | -0.38282 | -0.088078 | -0.028328 | -0.067412 | 0.31541 | 0.080523 | -0.104 | 122.9801 | 122.9028 | 123.0771 | 66.6976 | -123.1287 | 122.9039 | 123.0725 | 122.8879 | 66.6874 | -123.3748
1521.7969 | 123.23 | -66.7236 | 56.2958 | -0.010607 | -0.019111 | 0.00046154 | 0.053722 | -0.0056642 | 0.062503 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057817 | 0.028592 | 0.057881 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.1792 | 56.358 | -66.8604 | -66.7382 | -0.027113 | -66.7819 | 56.1711 | 56.3488 | 56.1643 | -67.1019 | -0.13678 | -0.025624 | -0.005323 | -0.017794 | 0.11898 | -0.11659 | 0.062272 | -0.37824 | -0.1247 | -0.014594 | -0.058257 | 0.31999 | 0.053056 | -0.13146 | 122.9938 | 122.9028 | 123.0817 | 66.6976 | -123.1562 | 122.8947 | 123.0725 | 122.8879 | 66.6965 | -123.3977
1522.7969 | 123.2941 | -66.7007 | 56.3324 | 0.0046549 | -0.018897 | 0.00067514 | 0.053722 | -0.0056642 | 0.061862 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057604 | 0.028378 | 0.057667 | -66.7335 | -0.026065 | -66.7414 | 56.2656 | 56.1929 | 56.3626 | -66.8604 | -66.7382 | -0.022535 | -66.7773 | 56.1757 | 56.358 | 56.1872 | -67.0973 | -0.15966 | -0.066823 | -0.032789 | -0.040682 | 0.11898 | -0.13948 | 0.030229 | -0.39655 | -0.15674 | -0.037482 | -0.076566 | 0.31999 | 0.025592 | -0.14519 | 122.9663 | 122.8937 | 123.0634 | 66.6747 | -123.1928 | 122.8764 | 123.0587 | 122.8879 | 66.6782 | -123.4297
1523.7969 | 123.2574 | -66.6916 | 56.3232 | -0.0029761 | -0.019111 | 0.00067514 | 0.053936 | -0.0058778 | 0.062503 | 0.015414 | -0.0026255 | -0.00055553 | 0.057604 | 0.028805 | 0.058094 | -66.729 | -0.016908 | -66.7552 | 56.2793 | 56.1746 | 56.358 | -66.8558 | -66.7382 | -0.027113 | -66.7819 | 56.1665 | 56.358 | 56.1552 | -67.0927 | -0.16424 | -0.043933 | -0.037367 | -0.063572 | 0.10067 | -0.14864 | 0.034806 | -0.40113 | -0.15675 | -0.046638 | -0.090301 | 0.31083 | 0.034747 | -0.16809 | 122.9709 | 122.8662 | 123.0496 | 66.6747 | -123.1791 | 122.8581 | 123.0496 | 122.8467 | 66.6645 | -123.416
1524.7969 | 123.1293 | -66.7328 | 56.3461 | 0.0046549 | -0.019111 | 0.00067514 | 0.053508 | -0.0054506 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057817 | 0.028805 | 0.057881 | -66.7335 | -0.030644 | -66.7506 | 56.2702 | 56.1838 | 56.358 | -66.8696 | -66.7428 | -0.022535 | -66.7865 | 56.1711 | 56.358 | 56.178 | -67.0927 | -0.13678 | -0.075978 | -0.000746 | -0.017795 | 0.11898 | -0.16237 | 0.011918 | -0.35993 | -0.17506 | -0.010018 | -0.053681 | 0.30625 | 0.011859 | -0.16808 | 123.0029 | 122.9166 | 123.0908 | 66.7021 | -123.2157 | 122.9039 | 123.0908 | 122.9108 | 66.7103 | -123.4389
1525.8594 | 123.2208 | -66.7328 | 56.2408 | 0.0046549 | -0.018897 | 0.00088894 | 0.053508 | -0.0058778 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057604 | 0.028592 | 0.057667 | -66.7244 | -0.026065 | -66.746 | 56.2702 | 56.1838 | 56.358 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3534 | 56.1643 | -67.0927 | -0.12762 | 0.029307 | 0.008411 | -0.013217 | 0.1144 | -0.057082 | 0.1172 | -0.35993 | -0.060614 | -0.010018 | -0.049102 | 0.31083 | 0.11256 | -0.076534 | 123.0029 | 122.9166 | 123.0908 | 66.7067 | -123.1013 | 122.913 | 123.0862 | 122.8971 | 66.7057 | -123.3336
1526.7969 | 123.2666 | -66.7007 | 56.3004 | -0.0029761 | -0.019325 | 0.00088894 | 0.053722 | -0.0054506 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057604 | 0.028592 | 0.058094 | -66.7335 | -0.021486 | -66.746 | 56.2702 | 56.1838 | 56.358 | -66.8604 | -66.7474 | -0.027113 | -66.7956 | 56.1757 | 56.3534 | 56.1735 | -67.0973 | -0.15966 | -0.030202 | -0.032789 | -0.04526 | 0.1144 | -0.11659 | 0.057694 | -0.39655 | -0.1247 | -0.04664 | -0.094881 | 0.30167 | 0.053056 | -0.12689 | 122.9709 | 122.8845 | 123.0588 | 66.6793 | -123.1608 | 122.8764 | 123.0542 | 122.8742 | 66.6736 | -123.3977
1527.7969 | 123.2254 | -66.7236 | 56.2958 | 0.0046549 | -0.019111 | 0.00067514 | 0.053722 | -0.0058778 | 0.062076 | 0.00015261 | -0.0021983 | -0.00098273 | 0.057604 | 0.028805 | 0.057881 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.1746 | 56.3626 | -66.865 | -66.7428 | -0.022535 | -66.791 | 56.1757 | 56.358 | 56.1826 | -67.0927 | -0.14135 | -0.030202 | -0.005323 | -0.017794 | 0.12356 | -0.12117 | 0.06685 | -0.36909 | -0.12012 | -0.019173 | -0.067414 | 0.30167 | 0.062213 | -0.11315 | 122.9892 | 122.8982 | 123.0863 | 66.693 | -123.1608 | 122.8993 | 123.0816 | 122.9063 | 66.7011 | -123.3885
1528.7969 | 123.2071 | -66.7191 | 56.3416 | -0.0029761 | -0.019111 | 0.0011025 | 0.053722 | -0.0054506 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.058031 | 0.028805 | 0.057667 | -66.729 | -0.021486 | -66.746 | 56.2656 | 56.1838 | 56.358 | -66.8604 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.358 | 56.1964 | -67.0881 | -0.14135 | -0.075979 | -0.009901 | -0.02695 | 0.1144 | -0.15779 | 0.016495 | -0.36909 | -0.1659 | -0.023751 | -0.067414 | 0.30167 | 0.016436 | -0.14519 | 122.9846 | 122.9028 | 123.0771 | 66.6976 | -123.202 | 122.8947 | 123.077 | 122.9154 | 66.6874 | -123.4297
1529.8594 | 123.2758 | -66.6916 | 56.2866 | 0.0046549 | -0.019111 | 0.00067514 | 0.054149 | -0.0058778 | 0.062503 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057604 | 0.028805 | 0.057881 | -66.729 | -0.021486 | -66.746 | 56.2747 | 56.17 | 56.3626 | -66.8513 | -66.7428 | -0.022535 | -66.7865 | 56.1757 | 56.358 | 56.178 | -67.0973 | -0.15966 | -0.01189 | -0.037367 | -0.054416 | 0.10525 | -0.11659 | 0.076005 | -0.40571 | -0.11097 | -0.051217 | -0.09488 | 0.31083 | 0.071368 | -0.10857 | 122.9663 | 122.8616 | 123.0542 | 66.6701 | -123.1379 | 122.8672 | 123.0496 | 122.8696 | 66.6691 | -123.3839
1530.7969 | 123.2071 | -66.7236 | 56.3507 | 0.0046549 | -0.019325 | 0.00067514 | 0.053722 | -0.0060916 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.028592 | 0.057667 | -66.729 | -0.030644 | -66.7368 | 56.2747 | 56.1883 | 56.3626 | -66.8558 | -66.7428 | -0.022535 | -66.791 | 56.1711 | 56.3626 | 56.2009 | -67.1019 | -0.1322 | -0.075977 | -0.005323 | -0.013215 | 0.11898 | -0.16237 | 0.011918 | -0.37824 | -0.17963 | -0.019173 | -0.067414 | 0.31083 | 0.01186 | -0.14977 | 122.9984 | 122.912 | 123.0863 | 66.693 | -123.2065 | 122.8947 | 123.0862 | 122.9246 | 66.7011 | -123.4526
1531.8594 | 123.2941 | -66.7099 | 56.2683 | -0.0029761 | -0.019325 | 0.00067514 | 0.053722 | -0.0060916 | 0.062289 | -0.0074779 | -0.0024119 | -0.00098273 | 0.056963 | 0.029019 | 0.057881 | -66.729 | -0.016908 | -66.746 | 56.2702 | 56.1838 | 56.3672 | -66.8558 | -66.752 | -0.027113 | -66.7865 | 56.1757 | 56.3534 | 56.1826 | -67.0881 | -0.14593 | 0.001841 | -0.019056 | -0.036105 | 0.10983 | -0.084548 | 0.098894 | -0.37824 | -0.092658 | -0.042063 | -0.076569 | 0.30167 | 0.085099 | -0.085686 | 122.9801 | 122.8937 | 123.0771 | 66.693 | -123.1241 | 122.8856 | 123.0633 | 122.8925 | 66.6828 | -123.3565
1532.7969 | 123.1842 | -66.7191 | 56.3461 | -0.010607 | -0.019325 | 0.00088894 | 0.053508 | -0.0054506 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.058031 | 0.029019 | 0.057881 | -66.729 | -0.030644 | -66.746 | 56.2793 | 56.1883 | 56.3672 | -66.8696 | -66.7474 | -0.036271 | -66.7773 | 56.1757 | 56.358 | 56.1689 | -67.1019 | -0.15051 | -0.066821 | -0.009901 | -0.02695 | 0.12356 | -0.15779 | 0.021075 | -0.38282 | -0.17048 | -0.02833 | -0.058256 | 0.32457 | 0.011859 | -0.17724 | 122.9984 | 122.9074 | 123.0863 | 66.6884 | -123.2157 | 122.8947 | 123.077 | 122.8879 | 66.6828 | -123.448
1533.7969 | 123.2574 | -66.6687 | 56.2912 | 0.012286 | -0.019325 | 0.00046154 | 0.053936 | -0.0060916 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057604 | 0.028592 | 0.058308 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1838 | 56.3626 | -66.865 | -66.7428 | -0.031692 | -66.791 | 56.1757 | 56.3534 | 56.1689 | -67.0973 | -0.19629 | -0.021047 | -0.064833 | -0.077304 | 0.11898 | -0.10744 | 0.071427 | -0.4286 | -0.11555 | -0.074105 | -0.12235 | 0.30625 | 0.062211 | -0.12231 | 122.9389 | 122.8525 | 123.0313 | 66.6381 | -123.1562 | 122.8444 | 123.0221 | 122.8376 | 66.637 | -123.3885
1534.7969 | 123.1842 | -66.7419 | 56.3507 | 0.0046549 | -0.019111 | 0.00088894 | 0.053722 | -0.0060916 | 0.062289 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057604 | 0.028592 | 0.058094 | -66.729 | -0.030644 | -66.7414 | 56.2656 | 56.1883 | 56.3626 | -66.8467 | -66.7428 | -0.031692 | -66.7819 | 56.1757 | 56.3534 | 56.178 | -67.0927 | -0.10473 | -0.085134 | 0.012987 | 0.000516 | 0.10524 | -0.16237 | 0.011918 | -0.35078 | -0.17506 | -0.000863 | -0.039947 | 0.31083 | 0.002702 | -0.17266 | 123.0075 | 122.9303 | 123.1046 | 66.7113 | -123.1974 | 122.9176 | 123.0954 | 122.92 | 66.7103 | -123.4434
1535.7969 | 123.2712 | -66.6824 | 56.3095 | 0.0046549 | -0.019111 | 0.0011025 | 0.053722 | -0.0058778 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057817 | 0.028378 | 0.057881 | -66.7335 | -0.026065 | -66.746 | 56.2747 | 56.1792 | 56.3626 | -66.8604 | -66.7474 | -0.036271 | -66.7865 | 56.1711 | 56.3626 | 56.1826 | -67.1065 | -0.17797 | -0.034778 | -0.0511 | -0.063571 | 0.1144 | -0.13032 | 0.053117 | -0.42402 | -0.13844 | -0.064951 | -0.10403 | 0.31999 | 0.053059 | -0.12688 | 122.9572 | 122.8616 | 123.0451 | 66.6564 | -123.1699 | 122.8535 | 123.045 | 122.8651 | 66.6462 | -123.416
1536.7969 | 123.175 | -66.7236 | 56.3416 | 0.012286 | -0.019111 | 0.00046154 | 0.053722 | -0.0058778 | 0.062076 | -0.0074779 | -0.0024119 | -0.00055553 | 0.057176 | 0.028592 | 0.058094 | -66.729 | -0.021486 | -66.7368 | 56.2656 | 56.1883 | 56.358 | -66.8558 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.3626 | 56.178 | -67.0973 | -0.1322 | -0.075979 | -0.005323 | -0.013215 | 0.11898 | -0.15321 | 0.016495 | -0.37367 | -0.17048 | -0.019173 | -0.058257 | 0.31541 | 0.021015 | -0.16351 | 122.9892 | 122.912 | 123.0817 | 66.7021 | -123.1974 | 122.8947 | 123.0862 | 122.9017 | 66.6965 | -123.4389
1537.7969 | 123.2666 | -66.6779 | 56.3004 | 0.0046549 | -0.019111 | 0.00067514 | 0.053936 | -0.0058778 | 0.062076 | 0.00015261 | -0.0024119 | -0.00034193 | 0.057176 | 0.029019 | 0.058522 | -66.7335 | -0.021486 | -66.7368 | 56.2747 | 56.1883 | 56.3672 | -66.8696 | -66.7382 | -0.031692 | -66.7727 | 56.1757 | 56.3534 | 56.1689 | -67.0973 | -0.19171 | -0.025623 | -0.055678 | -0.058992 | 0.13272 | -0.11201 | 0.066851 | -0.41944 | -0.1247 | -0.060371 | -0.094876 | 0.32457 | 0.053056 | -0.13146 | 122.9526 | 122.8662 | 123.0451 | 66.6564 | -123.1699 | 122.8535 | 123.0313 | 122.8467 | 66.6462 | -123.3977
1538.7969 | 123.1888 | -66.7374 | 56.4056 | 0.019917 | -0.019111 | 0.0011025 | 0.053508 | -0.0056642 | 0.062076 | -0.0074779 | -0.0024119 | -0.00055553 | 0.057604 | 0.028805 | 0.057667 | -66.7244 | -0.026065 | -66.7323 | 56.2747 | 56.1746 | 56.3626 | -66.865 | -66.7428 | -0.031692 | -66.7773 | 56.1757 | 56.3626 | 56.1643 | -67.0973 | -0.12762 | -0.13091 | 0.012989 | 0.005096 | 0.13272 | -0.23103 | -0.043014 | -0.35993 | -0.22999 | -0.00544 | -0.039945 | 0.31999 | -0.043072 | -0.24133 | 123.0121 | 122.912 | 123.1 | 66.7113 | -123.2706 | 122.913 | 123.0999 | 122.9017 | 66.7057 | -123.5029
1539.7969 | 123.1522 | -66.7007 | 56.3324 | 0.0046549 | -0.019111 | 0.0011025 | 0.053295 | -0.0058778 | 0.061862 | -0.0074779 | -0.0021983 | -0.00034193 | 0.057604 | 0.028805 | 0.057881 | -66.7335 | -0.026065 | -66.7231 | 56.2747 | 56.1792 | 56.358 | -66.865 | -66.7382 | -0.027113 | -66.7773 | 56.1711 | 56.3626 | 56.1826 | -67.0927 | -0.16424 | -0.057666 | -0.032789 | -0.022368 | 0.14187 | -0.15321 | 0.025651 | -0.39198 | -0.16132 | -0.037482 | -0.076566 | 0.31541 | 0.030171 | -0.14977 | 122.9755 | 122.8799 | 123.0588 | 66.6747 | -123.1974 | 122.8718 | 123.0633 | 122.8834 | 66.6736 | -123.4251
1540.7969 | 123.175 | -66.7191 | 56.3599 | 0.0046549 | -0.019111 | 0.00067514 | 0.053508 | -0.0054506 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.028805 | 0.057881 | -66.7244 | -0.026065 | -66.7277 | 56.261 | 56.1883 | 56.3535 | -66.865 | -66.7336 | -0.027113 | -66.7865 | 56.1711 | 56.3626 | 56.1826 | -67.0927 | -0.14593 | -0.098868 | -0.005322 | -0.008637 | 0.13729 | -0.17152 | -0.006394 | -0.37367 | -0.18879 | -0.014594 | -0.067414 | 0.30625 | 0.002705 | -0.17724 | 122.9801 | 122.9074 | 123.0725 | 66.693 | -123.2249 | 122.8901 | 123.0816 | 122.9017 | 66.6919 | -123.4526
1541.7969 | 123.2941 | -66.7099 | 56.3141 | -0.0029761 | -0.019111 | 0.00067514 | 0.053936 | -0.0056642 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057604 | 0.028805 | 0.058094 | -66.7335 | -0.026065 | -66.746 | 56.2656 | 56.1792 | 56.3626 | -66.8604 | -66.7382 | -0.027113 | -66.7865 | 56.1802 | 56.3626 | 56.1826 | -67.0927 | -0.15051 | -0.048513 | -0.023634 | -0.036105 | 0.1144 | -0.1349 | 0.048539 | -0.38282 | -0.13386 | -0.028327 | -0.076569 | 0.30625 | 0.048481 | -0.13146 | 122.9755 | 122.8891 | 123.0725 | 66.6838 | -123.1745 | 122.8901 | 123.0725 | 122.8925 | 66.6828 | -123.4068
1542.8594 | 123.2346 | -66.7328 | 56.2866 | 0.019917 | -0.018897 | 0.00088894 | 0.053936 | -0.0056642 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.028805 | 0.057667 | -66.7244 | -0.021486 | -66.7552 | 56.2747 | 56.1883 | 56.3626 | -66.8696 | -66.7382 | -0.031692 | -66.7865 | 56.1711 | 56.3534 | 56.178 | -67.1019 | -0.13678 | -0.01189 | 0.008411 | -0.022373 | 0.11441 | -0.098279 | 0.076005 | -0.36909 | -0.11555 | -0.005439 | -0.053681 | 0.31541 | 0.066789 | -0.10857 | 123.0075 | 122.9211 | 123.0954 | 66.7113 | -123.1562 | 122.9039 | 123.0862 | 122.9108 | 66.7011 | -123.3885
1543.7969 | 123.1384 | -66.7465 | 56.3324 | -0.0029761 | -0.019325 | 0.00046154 | 0.053508 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00034193 | 0.057176 | 0.028805 | 0.057881 | -66.7244 | -0.021486 | -66.7506 | 56.2793 | 56.1838 | 56.3626 | -66.865 | -66.752 | -0.022535 | -66.7865 | 56.1802 | 56.3626 | 56.1826 | -67.0927 | -0.11847 | -0.053088 | 0.022144 | -0.004062 | 0.1144 | -0.14863 | 0.030229 | -0.3462 | -0.15217 | -0.005442 | -0.039948 | 0.30625 | 0.030171 | -0.14977 | 123.0258 | 122.9303 | 123.1091 | 66.725 | -123.1974 | 122.9268 | 123.1091 | 122.9291 | 66.724 | -123.4251
1544.8594 | 123.1338 | -66.7511 | 56.3187 | 0.0046549 | -0.019111 | 0.00024794 | 0.053508 | -0.0058778 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057817 | 0.029019 | 0.058094 | -66.729 | -0.026065 | -66.7506 | 56.2747 | 56.1929 | 56.3626 | -66.8558 | -66.7474 | -0.031692 | -66.7819 | 56.1711 | 56.358 | 56.1643 | -67.1019 | -0.10473 | -0.043934 | 0.022143 | 0.000516 | 0.10525 | -0.12574 | 0.043961 | -0.35078 | -0.14759 | 0.003714 | -0.030791 | 0.31999 | 0.039324 | -0.15435 | 123.0258 | 122.944 | 123.1137 | 66.725 | -123.1745 | 122.9222 | 123.1091 | 122.9154 | 66.7194 | -123.4205
1545.7969 | 123.1842 | -66.7328 | 56.337 | 0.0046549 | -0.019752 | 0.00046154 | 0.053508 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057604 | 0.029019 | 0.057667 | -66.7335 | -0.026065 | -66.7506 | 56.2793 | 56.1975 | 56.3626 | -66.865 | -66.7382 | -0.031692 | -66.7819 | 56.1757 | 56.3626 | 56.178 | -67.0973 | -0.1322 | -0.057666 | -0.000746 | -0.017795 | 0.1144 | -0.13948 | 0.025651 | -0.36451 | -0.16132 | -0.005439 | -0.049102 | 0.31541 | 0.025593 | -0.15893 | 123.0121 | 122.9303 | 123.0954 | 66.7067 | -123.202 | 122.9084 | 123.0954 | 122.9108 | 66.7011 | -123.4343
1546.7969 | 123.1796 | -66.7282 | 56.3416 | 0.0046549 | -0.018897 | 0.00046154 | 0.053722 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.057817 | 0.029019 | 0.057881 | -66.7244 | -0.021486 | -66.7506 | 56.2747 | 56.1838 | 56.3764 | -66.8696 | -66.7474 | -0.027113 | -66.791 | 56.1757 | 56.358 | 56.1964 | -67.1019 | -0.14136 | -0.066822 | 0.003833 | -0.022373 | 0.11898 | -0.15779 | 0.034809 | -0.37367 | -0.1659 | -0.019175 | -0.062837 | 0.31083 | 0.016436 | -0.14519 | 123.0029 | 122.912 | 123.1046 | 66.7067 | -123.2111 | 122.9039 | 123.0862 | 122.9246 | 66.7011 | -123.4434
1547.7969 | 123.2483 | -66.7328 | 56.3004 | 0.0046549 | -0.019325 | 0.00024794 | 0.053936 | -0.0058778 | 0.062503 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057604 | 0.028805 | 0.058094 | -66.7335 | -0.021486 | -66.746 | 56.2747 | 56.1792 | 56.3672 | -66.8604 | -66.7474 | -0.027113 | -66.7773 | 56.1711 | 56.3626 | 56.1872 | -67.0973 | -0.12762 | -0.025623 | -0.000746 | -0.013217 | 0.1144 | -0.12117 | 0.066851 | -0.36451 | -0.12928 | -0.014597 | -0.044523 | 0.31999 | 0.062214 | -0.11315 | 123.0075 | 122.912 | 123.1 | 66.7113 | -123.1608 | 122.9039 | 123.0954 | 122.92 | 66.7057 | -123.3977
1548.7969 | 123.23 | -66.7191 | 56.2958 | -0.0029761 | -0.019325 | 0.00046154 | 0.053722 | -0.0060916 | 0.062076 | 0.00015261 | -0.0021983 | -0.0011965 | 0.057817 | 0.028805 | 0.058308 | -66.7198 | -0.012329 | -66.7414 | 56.261 | 56.1838 | 56.3626 | -66.8513 | -66.7428 | -0.017956 | -66.7819 | 56.1757 | 56.3671 | 56.1872 | -67.1019 | -0.1322 | -0.034781 | -0.000744 | -0.022372 | 0.10982 | -0.11201 | 0.06685 | -0.38282 | -0.12012 | -0.023751 | -0.062835 | 0.31999 | 0.07137 | -0.10857 | 122.9801 | 122.9028 | 123.0817 | 66.7067 | -123.147 | 122.8947 | 123.0862 | 122.9063 | 66.7011 | -123.3977
1549.7969 | 123.2071 | -66.7236 | 56.3644 | 0.012286 | -0.019538 | 0.00067514 | 0.054149 | -0.0056642 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.05739 | 0.029019 | 0.057881 | -66.729 | -0.030644 | -66.746 | 56.2702 | 56.1929 | 56.3672 | -66.8696 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.358 | 56.2101 | -67.0973 | -0.14593 | -0.094289 | -0.005323 | -0.022372 | 0.12356 | -0.17152 | 0.002764 | -0.37367 | -0.18879 | -0.019173 | -0.062836 | 0.31083 | -0.006452 | -0.15434 | 122.9938 | 122.9166 | 123.0908 | 66.693 | -123.234 | 122.8993 | 123.0816 | 122.9337 | 66.6919 | -123.4617
1550.7969 | 123.1613 | -66.7236 | 56.3507 | 0.0046549 | -0.019538 | 0.00088894 | 0.053722 | -0.0058778 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057817 | 0.028805 | 0.057881 | -66.7244 | -0.021486 | -66.7414 | 56.2702 | 56.1975 | 56.3718 | -66.8696 | -66.7474 | -0.031692 | -66.7819 | 56.1757 | 56.3534 | 56.2193 | -67.0973 | -0.14593 | -0.080556 | -0.000744 | -0.017794 | 0.12814 | -0.15321 | 0.021076 | -0.37367 | -0.17506 | -0.023752 | -0.058257 | 0.31541 | 0.002702 | -0.13145 | 122.9938 | 122.9211 | 123.0954 | 66.7021 | -123.2203 | 122.8993 | 123.077 | 122.9429 | 66.6919 | -123.448
1551.7969 | 123.1979 | -66.7053 | 56.337 | 0.0046549 | -0.019538 | 0.0011025 | 0.053722 | -0.0058778 | 0.062503 | -0.0074779 | -0.0024119 | -0.00098273 | 0.05739 | 0.029019 | 0.057881 | -66.729 | -0.021486 | -66.7552 | 56.2702 | 56.1883 | 56.3672 | -66.8696 | -66.7474 | -0.036271 | -66.7773 | 56.1711 | 56.3488 | 56.1964 | -67.1019 | -0.16424 | -0.066823 | -0.023634 | -0.049839 | 0.11441 | -0.14863 | 0.03023 | -0.39656 | -0.1659 | -0.042063 | -0.071989 | 0.32457 | 0.011857 | -0.14061 | 122.9755 | 122.8937 | 123.0725 | 66.6838 | -123.2065 | 122.8764 | 123.0542 | 122.9017 | 66.6691 | -123.4389
1552.8594 | 123.2391 | -66.7236 | 56.3095 | 0.0046549 | -0.019325 | 0.00067514 | 0.054363 | -0.0060916 | 0.062503 | 0.015414 | -0.0026255 | -0.00098273 | 0.057604 | 0.029019 | 0.058094 | -66.7335 | -0.026065 | -66.746 | 56.2747 | 56.1929 | 56.3626 | -66.865 | -66.7428 | -0.027113 | -66.7865 | 56.1757 | 56.358 | 56.2009 | -67.0973 | -0.14135 | -0.034778 | -0.009901 | -0.022372 | 0.11898 | -0.11659 | 0.053117 | -0.37367 | -0.13386 | -0.019173 | -0.062836 | 0.31083 | 0.04848 | -0.10857 | 122.9984 | 122.9166 | 123.0863 | 66.6976 | -123.1745 | 122.8993 | 123.0816 | 122.9246 | 66.6965 | -123.4068
1553.7969 | 123.1888 | -66.7282 | 56.2912 | -0.0029761 | -0.019752 | 0.00046154 | 0.053936 | -0.0056642 | 0.062717 | -0.0074779 | -0.0028393 | -0.00076913 | 0.057604 | 0.029019 | 0.058094 | -66.7198 | -0.016908 | -66.7597 | 56.261 | 56.1929 | 56.3626 | -66.8696 | -66.7474 | -0.027113 | -66.7819 | 56.1757 | 56.3626 | 56.1826 | -67.1019 | -0.14136 | -0.030204 | 0.008411 | -0.03153 | 0.10983 | -0.098278 | 0.071427 | -0.37367 | -0.11555 | -0.019175 | -0.05368 | 0.31999 | 0.071369 | -0.10857 | 122.9892 | 122.9211 | 123.0908 | 66.7113 | -123.1608 | 122.9039 | 123.0908 | 122.9108 | 66.7011 | -123.3931
1554.7969 | 123.175 | -66.7236 | 56.3507 | -0.010607 | -0.019325 | 0.00067514 | 0.053722 | -0.0054506 | 0.062717 | 0.00015261 | -0.0028393 | -0.00098273 | 0.057604 | 0.029019 | 0.058308 | -66.7244 | -0.021486 | -66.746 | 56.2747 | 56.2021 | 56.3672 | -66.8696 | -66.7474 | -0.027113 | -66.7865 | 56.1757 | 56.358 | 56.1964 | -67.0927 | -0.14593 | -0.075977 | -0.000744 | -0.022372 | 0.12356 | -0.14863 | 0.016497 | -0.36909 | -0.17506 | -0.023752 | -0.062836 | 0.30625 | 0.007281 | -0.15435 | 122.9984 | 122.9257 | 123.0908 | 66.7021 | -123.2203 | 122.8993 | 123.0816 | 122.92 | 66.6965 | -123.4434
1555.8594 | 123.2346 | -66.7099 | 56.2683 | -0.0029761 | -0.019966 | 0.00046154 | 0.053722 | -0.0058778 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.029446 | 0.058094 | -66.7381 | -0.026065 | -66.7368 | 56.2656 | 56.1838 | 56.3718 | -66.865 | -66.7474 | -0.022535 | -66.7819 | 56.1802 | 56.358 | 56.2055 | -67.0927 | -0.15509 | -0.002737 | -0.028212 | -0.026948 | 0.12814 | -0.084548 | 0.10347 | -0.38282 | -0.08808 | -0.037485 | -0.07199 | 0.31083 | 0.089678 | -0.062793 | 122.9755 | 122.8937 | 123.0817 | 66.6838 | -123.1333 | 122.8901 | 123.0679 | 122.9154 | 66.6874 | -123.361
1556.7969 | 123.175 | -66.7374 | 56.3416 | -0.0029761 | -0.019538 | 0.00088894 | 0.053936 | -0.0063052 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.05739 | 0.028805 | 0.057667 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.1929 | 56.3626 | -66.8696 | -66.7474 | -0.031692 | -66.7819 | 56.1757 | 56.358 | 56.2009 | -67.0927 | -0.1322 | -0.071401 | 0.00841 | -0.004061 | 0.12814 | -0.14863 | 0.021073 | -0.35535 | -0.1659 | -0.010019 | -0.044524 | 0.31083 | 0.016436 | -0.14061 | 123.0075 | 122.9303 | 123.1 | 66.7113 | -123.2111 | 122.913 | 123.0954 | 122.9383 | 66.7057 | -123.4343
1557.8594 | 123.23 | -66.7328 | 56.2912 | 0.0046549 | -0.019752 | 0.00067514 | 0.054149 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057604 | 0.029019 | 0.057667 | -66.729 | -0.026065 | -66.746 | 56.2747 | 56.1883 | 56.3626 | -66.8604 | -66.7428 | -0.031692 | -66.7819 | 56.1757 | 56.3671 | 56.1964 | -67.1065 | -0.12762 | -0.016468 | 0.003832 | -0.013217 | 0.1144 | -0.10286 | 0.071427 | -0.37367 | -0.11555 | -0.010018 | -0.049102 | 0.32457 | 0.075947 | -0.094838 | 123.0075 | 122.9211 | 123.0954 | 66.7067 | -123.1516 | 122.9084 | 123.0999 | 122.9291 | 66.7011 | -123.3977
1558.7969 | 123.1705 | -66.7511 | 56.3095 | 0.0046549 | -0.019752 | 0.00046154 | 0.053936 | -0.0058778 | 0.062503 | 0.0077831 | -0.0024119 | -0.00098273 | 0.05739 | 0.029233 | 0.058094 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.1792 | 56.3718 | -66.8696 | -66.7474 | -0.027113 | -66.7865 | 56.1802 | 56.358 | 56.178 | -67.0927 | -0.11847 | -0.039357 | 0.022143 | 0.009672 | 0.12814 | -0.13032 | 0.062275 | -0.34162 | -0.12928 | 0.003714 | -0.03537 | 0.30625 | 0.04848 | -0.13146 | 123.0213 | 122.9303 | 123.1229 | 66.725 | -123.1791 | 122.9313 | 123.1091 | 122.9291 | 66.724 | -123.4022
1559.7969 | 123.1613 | -66.7374 | 56.3461 | -0.0029761 | -0.019752 | 0.0011025 | 0.053936 | -0.0058778 | 0.062503 | 0.023044 | -0.0026255 | -0.00076913 | 0.05739 | 0.029233 | 0.057881 | -66.729 | -0.016908 | -66.7506 | 56.2702 | 56.1975 | 56.3672 | -66.8696 | -66.7474 | -0.031692 | -66.7865 | 56.1802 | 56.3488 | 56.1872 | -67.1019 | -0.1322 | -0.075978 | 0.00841 | -0.013217 | 0.11898 | -0.14863 | 0.021075 | -0.36451 | -0.1659 | -0.010019 | -0.049103 | 0.31541 | 0.002702 | -0.15893 | 123.0075 | 122.9349 | 123.1046 | 66.7205 | -123.2157 | 122.9176 | 123.0862 | 122.9246 | 66.7057 | -123.448
1560.7969 | 123.1888 | -66.7465 | 56.337 | -0.010607 | -0.019752 | 0.00067514 | 0.053295 | -0.0058778 | 0.062503 | 0.015414 | -0.0030529 | -0.00098273 | 0.057817 | 0.029233 | 0.058094 | -66.729 | -0.016908 | -66.746 | 56.2702 | 56.1975 | 56.3718 | -66.865 | -66.7428 | -0.017956 | -66.7819 | 56.1757 | 56.3626 | 56.1964 | -67.1019 | -0.11847 | -0.066823 | 0.017565 | 0.000516 | 0.11898 | -0.13948 | 0.034809 | -0.35536 | -0.16132 | 0.003715 | -0.035369 | 0.31999 | 0.025593 | -0.14061 | 123.0167 | 122.944 | 123.1183 | 66.7296 | -123.202 | 122.9222 | 123.1091 | 122.9429 | 66.7286 | -123.4389
1561.8594 | 123.3124 | -66.6916 | 56.3095 | 0.0046549 | -0.019538 | 0.00088894 | 0.054149 | -0.0054506 | 0.062717 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.029233 | 0.057881 | -66.729 | -0.026065 | -66.746 | 56.2793 | 56.1929 | 56.358 | -66.8604 | -66.7428 | -0.027113 | -66.7865 | 56.1802 | 56.3534 | 56.2055 | -67.0973 | -0.16882 | -0.0302 | -0.037367 | -0.054416 | 0.1144 | -0.11659 | 0.048539 | -0.40571 | -0.12928 | -0.051217 | -0.09488 | 0.31083 | 0.043901 | -0.10399 | 122.9709 | 122.8845 | 123.0496 | 66.6655 | -123.1699 | 122.8718 | 123.045 | 122.8971 | 66.6645 | -123.4068
1562.7969 | 123.2162 | -66.6962 | 56.4056 | 0.0046549 | -0.019966 | 0.00046154 | 0.053722 | -0.0058778 | 0.062503 | 0.0077831 | -0.0026255 | -0.00076913 | 0.057817 | 0.029233 | 0.057667 | -66.7335 | -0.016908 | -66.746 | 56.2747 | 56.1838 | 56.3626 | -66.865 | -66.7474 | -0.022535 | -66.7773 | 56.1711 | 56.358 | 56.1689 | -67.0927 | -0.16882 | -0.13091 | -0.037367 | -0.049838 | 0.11898 | -0.22188 | -0.043014 | -0.39655 | -0.23457 | -0.051218 | -0.081144 | 0.31541 | -0.047651 | -0.23675 | 122.9709 | 122.8799 | 123.0588 | 66.6793 | -123.2706 | 122.8672 | 123.0542 | 122.8651 | 66.6736 | -123.4984
1563.7969 | 123.1522 | -66.7053 | 56.3461 | -0.0029761 | -0.019538 | 0.00067514 | 0.053508 | -0.0058778 | 0.062503 | 0.023044 | -0.0024119 | -0.00076913 | 0.057176 | 0.029233 | 0.057881 | -66.729 | -0.026065 | -66.7414 | 56.2793 | 56.1975 | 56.3672 | -66.8741 | -66.7428 | -0.027113 | -66.7865 | 56.1802 | 56.358 | 56.1872 | -67.0973 | -0.16882 | -0.066821 | -0.023634 | -0.036105 | 0.13272 | -0.14863 | 0.021075 | -0.39198 | -0.1659 | -0.037484 | -0.081147 | 0.31083 | 0.011859 | -0.15893 | 122.9846 | 122.9028 | 123.0725 | 66.6793 | -123.2203 | 122.8856 | 123.0633 | 122.8925 | 66.6782 | -123.4434
1564.7969 | 123.1659 | -66.7374 | 56.3232 | -0.0029761 | -0.019752 | 0.0011025 | 0.053508 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.05739 | 0.029446 | 0.058094 | -66.7335 | -0.021486 | -66.746 | 56.2793 | 56.1883 | 56.3672 | -66.8604 | -66.7474 | -0.031692 | -66.7865 | 56.1848 | 56.358 | 56.1735 | -67.0927 | -0.12304 | -0.043933 | 0.003832 | -0.008639 | 0.1144 | -0.1349 | 0.043963 | -0.35535 | -0.13843 | -0.010019 | -0.049103 | 0.30625 | 0.034747 | -0.14977 | 123.0167 | 122.9257 | 123.1046 | 66.7159 | -123.1837 | 122.9222 | 123.0954 | 122.9108 | 66.7057 | -123.416
1565.7969 | 123.2117 | -66.6779 | 56.3141 | -0.0029761 | -0.019752 | 0.00046154 | 0.053722 | -0.0056642 | 0.062289 | -0.0074779 | -0.0021983 | -0.00076913 | 0.05739 | 0.029019 | 0.057881 | -66.7335 | -0.030644 | -66.746 | 56.2702 | 56.1929 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.358 | 56.1918 | -67.1019 | -0.19171 | -0.043935 | -0.055678 | -0.068149 | 0.12356 | -0.12117 | 0.062275 | -0.42402 | -0.13843 | -0.06495 | -0.10403 | 0.31999 | 0.043902 | -0.1223 | 122.948 | 122.8708 | 123.0542 | 66.6472 | -123.1837 | 122.8535 | 123.0358 | 122.8696 | 66.6507 | -123.416
1566.8594 | 123.2071 | -66.7191 | 56.3278 | 0.0046549 | -0.019538 | 0.00046154 | 0.053722 | -0.0056642 | 0.062076 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.029233 | 0.058094 | -66.7335 | -0.021486 | -66.7368 | 56.2702 | 56.1883 | 56.3718 | -66.8696 | -66.7382 | -0.031692 | -66.791 | 56.1711 | 56.3626 | 56.1964 | -67.1019 | -0.15051 | -0.057668 | -0.014479 | -0.017793 | 0.13272 | -0.13948 | 0.043964 | -0.38282 | -0.15675 | -0.019172 | -0.071992 | 0.31083 | 0.034748 | -0.13146 | 122.9892 | 122.9074 | 123.0908 | 66.6976 | -123.1974 | 122.8901 | 123.0816 | 122.9154 | 66.6874 | -123.4297
1567.7969 | 123.2666 | -66.7236 | 56.3278 | -0.0029761 | -0.019325 | 0.00067514 | 0.053508 | -0.0054506 | 0.061862 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057176 | 0.028805 | 0.057881 | -66.729 | -0.026065 | -66.7414 | 56.2702 | 56.2021 | 56.3718 | -66.8696 | -66.7382 | -0.022535 | -66.7819 | 56.1757 | 56.3626 | 56.178 | -67.1019 | -0.14593 | -0.057668 | -0.005323 | -0.017794 | 0.12814 | -0.12574 | 0.043964 | -0.37824 | -0.15217 | -0.014594 | -0.058257 | 0.31999 | 0.034748 | -0.14977 | 122.9938 | 122.9257 | 123.0954 | 66.6976 | -123.1974 | 122.8993 | 123.0862 | 122.9017 | 66.7011 | -123.4297
1568.7969 | 123.1888 | -66.7145 | 56.3416 | -0.0029761 | -0.019966 | 0.00088894 | 0.053722 | -0.0056642 | 0.062289 | 0.00015261 | -0.0021983 | -0.00098273 | 0.05739 | 0.029233 | 0.057881 | -66.729 | -0.021486 | -66.7368 | 56.2747 | 56.2021 | 56.3718 | -66.865 | -66.7428 | -0.022535 | -66.7773 | 56.1757 | 56.3671 | 56.1689 | -67.1019 | -0.15051 | -0.066822 | -0.014478 | -0.02237 | 0.12814 | -0.13947 | 0.030231 | -0.3874 | -0.1659 | -0.028328 | -0.062833 | 0.32457 | 0.025593 | -0.17266 | 122.9892 | 122.9166 | 123.0863 | 66.693 | -123.2065 | 122.8901 | 123.0816 | 122.8834 | 66.6919 | -123.4434
1569.7969 | 123.2483 | -66.6962 | 56.3095 | -0.0029761 | -0.019752 | 0.00088894 | 0.053936 | -0.0058778 | 0.062076 | 0.00015261 | -0.0024119 | -0.00098273 | 0.05739 | 0.029446 | 0.057667 | -66.729 | -0.035222 | -66.7414 | 56.2702 | 56.1883 | 56.3718 | -66.865 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.3671 | 56.1689 | -67.0973 | -0.16882 | -0.039357 | -0.032789 | -0.04526 | 0.12356 | -0.12117 | 0.062275 | -0.40113 | -0.13386 | -0.046639 | -0.090302 | 0.31083 | 0.057637 | -0.14062 | 122.9663 | 122.8845 | 123.068 | 66.6609 | -123.1745 | 122.8718 | 123.0633 | 122.8651 | 66.6645 | -123.4068
1570.7969 | 123.1705 | -66.7465 | 56.3324 | -0.0029761 | -0.019752 | 0.00067514 | 0.053936 | -0.0058778 | 0.062076 | 0.00015261 | -0.0019847 | -0.00098273 | 0.05739 | 0.029446 | 0.057881 | -66.7198 | -0.035222 | -66.7368 | 56.2747 | 56.1883 | 56.3626 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.3626 | 56.1826 | -67.1019 | -0.12305 | -0.057666 | 0.026722 | 0.009673 | 0.13272 | -0.14406 | 0.030229 | -0.35536 | -0.16132 | 0.003715 | -0.035369 | 0.31999 | 0.030171 | -0.14977 | 123.0213 | 122.9349 | 123.1091 | 66.7113 | -123.202 | 122.9176 | 123.1091 | 122.9291 | 66.7194 | -123.4343
1571.8594 | 123.2758 | -66.6916 | 56.3095 | -0.0029761 | -0.019966 | 0.00067514 | 0.054149 | -0.0056642 | 0.062289 | 0.015414 | -0.0026255 | -0.00098273 | 0.057817 | 0.029019 | 0.057881 | -66.7198 | -0.026065 | -66.7368 | 56.2747 | 56.1792 | 56.3718 | -66.8604 | -66.7382 | -0.027113 | -66.7819 | 56.1848 | 56.3626 | 56.1964 | -67.1019 | -0.16882 | -0.034778 | -0.02821 | -0.045259 | 0.12356 | -0.13032 | 0.062275 | -0.41029 | -0.1247 | -0.046638 | -0.090301 | 0.31999 | 0.053059 | -0.11315 | 122.9663 | 122.8708 | 123.0634 | 66.6655 | -123.1699 | 122.8764 | 123.0542 | 122.8879 | 66.6645 | -123.4114
1572.7969 | 123.1979 | -66.7191 | 56.3232 | 0.0046549 | -0.019325 | 0.00067514 | 0.053508 | -0.0058778 | 0.062076 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.028805 | 0.057881 | -66.7244 | -0.021486 | -66.746 | 56.2747 | 56.1883 | 56.3672 | -66.8604 | -66.7336 | -0.027113 | -66.7865 | 56.1848 | 56.3626 | 56.1735 | -67.1019 | -0.14135 | -0.048511 | -0.005322 | -0.02695 | 0.1144 | -0.1349 | 0.043963 | -0.38282 | -0.13843 | -0.014594 | -0.067414 | 0.31541 | 0.039326 | -0.14977 | 122.9938 | 122.9074 | 123.0863 | 66.6976 | -123.1837 | 122.9039 | 123.0816 | 122.8925 | 66.6919 | -123.4251
1573.7969 | 123.23 | -66.7053 | 56.3095 | 0.012286 | -0.019966 | 0.00046154 | 0.053508 | -0.0058778 | 0.062076 | 0.0077831 | -0.0026255 | -0.00055553 | 0.05739 | 0.029446 | 0.057453 | -66.729 | -0.016908 | -66.7368 | 56.2747 | 56.1929 | 56.3718 | -66.8741 | -66.7382 | -0.027113 | -66.7819 | 56.1848 | 56.3671 | 56.1735 | -67.0973 | -0.16882 | -0.034778 | -0.023634 | -0.031526 | 0.1373 | -0.11659 | 0.062275 | -0.39198 | -0.1247 | -0.032905 | -0.076568 | 0.31541 | 0.057637 | -0.13604 | 122.9801 | 122.8982 | 123.0771 | 66.6884 | -123.1837 | 122.8901 | 123.0725 | 122.8788 | 66.6782 | -123.4068
1574.8594 | 123.2483 | -66.7053 | 56.3141 | 0.0046549 | -0.019752 | 0.00046154 | 0.053295 | -0.0058778 | 0.062076 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057604 | 0.029446 | 0.057881 | -66.729 | -0.030644 | -66.7368 | 56.2702 | 56.1838 | 56.3626 | -66.865 | -66.7382 | -0.027113 | -66.7865 | 56.1757 | 56.3626 | 56.178 | -67.1019 | -0.15967 | -0.043935 | -0.023634 | -0.031526 | 0.12814 | -0.13032 | 0.048539 | -0.39656 | -0.13843 | -0.032905 | -0.081147 | 0.31541 | 0.048481 | -0.13604 | 122.9755 | 122.8891 | 123.0679 | 66.6747 | -123.1791 | 122.881 | 123.0679 | 122.8834 | 66.6782 | -123.416
1575.7969 | 123.2803 | -66.6733 | 56.3004 | -0.0029761 | -0.019966 | 0.00046154 | 0.053722 | -0.0054506 | 0.061862 | 0.00015261 | -0.0021983 | -0.00055553 | 0.057604 | 0.029446 | 0.057881 | -66.7244 | -0.026065 | -66.7368 | 56.2702 | 56.1883 | 56.3764 | -66.8604 | -66.7245 | -0.022535 | -66.791 | 56.1802 | 56.358 | 56.1826 | -67.1019 | -0.18713 | -0.030202 | -0.051098 | -0.063569 | 0.12356 | -0.11201 | 0.076008 | -0.4286 | -0.12012 | -0.051212 | -0.11777 | 0.31083 | 0.057635 | -0.11773 | 122.9434 | 122.8616 | 123.0496 | 66.6472 | -123.1608 | 122.8535 | 123.0313 | 122.8559 | 66.6507 | -123.4022
1576.8594 | 123.2346 | -66.6824 | 56.3416 | -0.0029761 | -0.019325 | 3.4136e-05 | 0.053508 | -0.0054506 | 0.062289 | -0.0074779 | -0.0021983 | -0.00034193 | 0.057604 | 0.029019 | 0.057667 | -66.7335 | -0.021486 | -66.7323 | 56.2793 | 56.1929 | 56.3626 | -66.865 | -66.7291 | -0.017956 | -66.791 | 56.1757 | 56.3717 | 56.1689 | -67.1019 | -0.18255 | -0.062244 | -0.0511 | -0.049836 | 0.13272 | -0.14863 | 0.021073 | -0.41944 | -0.1659 | -0.046636 | -0.10861 | 0.31083 | 0.030172 | -0.17266 | 122.9617 | 122.8754 | 123.0451 | 66.6609 | -123.2065 | 122.8581 | 123.0542 | 122.8513 | 66.6645 | -123.4434
1577.7969 | 123.2803 | -66.687 | 56.3278 | -0.010607 | -0.019752 | 0.00067514 | 0.053722 | -0.0056642 | 0.061862 | 0.00015261 | -0.0019847 | -0.00055553 | 0.05739 | 0.029233 | 0.058094 | -66.729 | -0.021486 | -66.7323 | 56.2702 | 56.1883 | 56.3718 | -66.865 | -66.7336 | -0.027113 | -66.7819 | 56.1848 | 56.3626 | 56.1643 | -67.0973 | -0.17798 | -0.057668 | -0.041944 | -0.045258 | 0.13272 | -0.13948 | 0.043964 | -0.41029 | -0.14301 | -0.046637 | -0.094878 | 0.31541 | 0.034748 | -0.16351 | 122.9572 | 122.8754 | 123.0588 | 66.6655 | -123.1928 | 122.8718 | 123.0496 | 122.8513 | 66.6599 | -123.4251
1578.7969 | 123.1659 | -66.7145 | 56.3232 | 0.0046549 | -0.019752 | 0.00067514 | 0.053508 | -0.0056642 | 0.062289 | 0.00015261 | -0.0024119 | -0.00034193 | 0.057176 | 0.029446 | 0.057881 | -66.729 | -0.021486 | -66.7414 | 56.2747 | 56.1838 | 56.3764 | -66.865 | -66.7291 | -0.027113 | -66.7819 | 56.1802 | 56.3626 | 56.178 | -67.0973 | -0.15051 | -0.048511 | -0.014478 | -0.026949 | 0.12356 | -0.13948 | 0.05312 | -0.38282 | -0.14301 | -0.014592 | -0.067412 | 0.31541 | 0.039326 | -0.1452 | 122.9892 | 122.8982 | 123.0908 | 66.693 | -123.1882 | 122.8947 | 123.077 | 122.8925 | 66.6874 | -123.4205
1579.7969 | 123.1567 | -66.7328 | 56.3782 | 0.0046549 | -0.019966 | 0.00067514 | 0.053722 | -0.0056642 | 0.062503 | -0.0074779 | -0.0024119 | -0.00034193 | 0.05739 | 0.029446 | 0.057453 | -66.7244 | -0.021486 | -66.7277 | 56.2702 | 56.1883 | 56.3626 | -66.865 | -66.7245 | -0.027113 | -66.7819 | 56.1757 | 56.358 | 56.1826 | -67.0973 | -0.1322 | -0.10802 | 0.008411 | 0.005096 | 0.13729 | -0.18983 | -0.015548 | -0.36451 | -0.20252 | 0.008297 | -0.049102 | 0.31541 | -0.020185 | -0.19555 | 123.0029 | 122.9211 | 123.0954 | 66.7113 | -123.2432 | 122.9084 | 123.0908 | 122.9154 | 66.7057 | -123.4755
1580.7969 | 123.1613 | -66.7282 | 56.3416 | 0.0046549 | -0.019966 | 0.00067514 | 0.053722 | -0.0054506 | 0.062503 | 0.0077831 | -0.0021983 | -0.00055553 | 0.05739 | 0.029233 | 0.057881 | -66.7335 | -0.026065 | -66.7368 | 56.2747 | 56.1883 | 56.3764 | -66.8696 | -66.7382 | -0.022535 | -66.7773 | 56.1802 | 56.3626 | 56.178 | -67.0973 | -0.14136 | -0.066822 | -0.005324 | -0.008638 | 0.13272 | -0.15321 | 0.034809 | -0.36909 | -0.16132 | -0.010017 | -0.049101 | 0.31999 | 0.021015 | -0.16351 | 123.0029 | 122.9166 | 123.1046 | 66.7021 | -123.2111 | 122.9084 | 123.0908 | 122.9063 | 66.7057 | -123.4389
1581.7969 | 123.2712 | -66.6916 | 56.337 | 0.012286 | -0.019325 | 0.00067514 | 0.053722 | -0.0056642 | 0.062076 | 0.00015261 | -0.0021983 | -0.00055553 | 0.05739 | 0.029446 | 0.057881 | -66.7335 | -0.030644 | -66.7368 | 56.2793 | 56.1929 | 56.3626 | -66.8696 | -66.7382 | -0.027113 | -66.7865 | 56.1757 | 56.358 | 56.1826 | -67.0973 | -0.17798 | -0.057666 | -0.041945 | -0.045259 | 0.13272 | -0.14405 | 0.025651 | -0.40571 | -0.16132 | -0.046638 | -0.09488 | 0.31083 | 0.021014 | -0.15435 | 122.9709 | 122.8845 | 123.0542 | 66.6609 | -123.2065 | 122.8672 | 123.0496 | 122.8742 | 66.6645 | -123.4343
1582.7969 | 123.2208 | -66.7145 | 56.3232 | -0.0029761 | -0.019752 | 0.00067514 | 0.053936 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057604 | 0.029019 | 0.057881 | -66.729 | -0.026065 | -66.7323 | 56.2747 | 56.1929 | 56.3718 | -66.8696 | -66.7382 | -0.022535 | -66.7773 | 56.1802 | 56.3626 | 56.2009 | -67.1065 | -0.15509 | -0.048511 | -0.014478 | -0.017792 | 0.1373 | -0.13032 | 0.048542 | -0.39198 | -0.14301 | -0.023749 | -0.062833 | 0.32914 | 0.039326 | -0.1223 | 122.9892 | 122.9074 | 123.0863 | 66.6884 | -123.1928 | 122.8947 | 123.077 | 122.9154 | 66.6919 | -123.4297
1583.8594 | 123.3261 | -66.655 | 56.3187 | 0.0046549 | -0.019752 | 0.00046154 | 0.053722 | -0.0056642 | 0.061862 | 0.0077831 | -0.0021983 | -0.00098273 | 0.05739 | 0.029446 | 0.057667 | -66.7198 | -0.030644 | -66.7323 | 56.2793 | 56.1883 | 56.3626 | -66.8696 | -66.7382 | -0.027113 | -66.7865 | 56.1757 | 56.3626 | 56.2055 | -67.0927 | -0.2146 | -0.039356 | -0.064831 | -0.077302 | 0.1373 | -0.13032 | 0.043961 | -0.43775 | -0.14301 | -0.083259 | -0.1315 | 0.30625 | 0.043903 | -0.11315 | 122.9343 | 122.8433 | 123.0176 | 66.6243 | -123.1882 | 122.8306 | 123.0175 | 122.8605 | 66.6279 | -123.4114
1584.7969 | 123.2071 | -66.7328 | 56.3461 | 0.0046549 | -0.019538 | 0.00088894 | 0.053508 | -0.0058778 | 0.062289 | -0.0074779 | -0.0026255 | -0.00098273 | 0.057817 | 0.02966 | 0.057881 | -66.729 | -0.026065 | -66.7368 | 56.2793 | 56.1883 | 56.3764 | -66.8741 | -66.7474 | -0.022535 | -66.7773 | 56.1802 | 56.3534 | 56.1826 | -67.1019 | -0.14136 | -0.066821 | 0.003832 | -0.00406 | 0.1373 | -0.15779 | 0.030232 | -0.36909 | -0.1659 | -0.014597 | -0.044523 | 0.32457 | 0.00728 | -0.16351 | 123.0121 | 122.9211 | 123.1091 | 66.7067 | -123.2203 | 122.913 | 123.0862 | 122.9154 | 66.7103 | -123.448
1585.8594 | 123.2025 | -66.7374 | 56.3049 | 0.0046549 | -0.019538 | 0.00067514 | 0.053722 | -0.0058778 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057604 | 0.029233 | 0.057881 | -66.729 | -0.026065 | -66.7414 | 56.2747 | 56.1883 | 56.3718 | -66.8696 | -66.7428 | -0.031692 | -66.7865 | 56.1848 | 56.3626 | 56.1826 | -67.0973 | -0.1322 | -0.030201 | 0.00841 | -0.004061 | 0.12814 | -0.11659 | 0.066852 | -0.35993 | -0.12012 | -0.00544 | -0.049103 | 0.31083 | 0.057636 | -0.12231 | 123.0121 | 122.9257 | 123.1091 | 66.7113 | -123.1745 | 122.9222 | 123.0999 | 122.92 | 66.7057 | -123.4022
1586.7969 | 123.1796 | -66.7557 | 56.3324 | 0.0046549 | -0.019752 | 0.00046154 | 0.053722 | -0.0058778 | 0.062289 | 0.015414 | -0.0024119 | -0.00076913 | 0.05739 | 0.029446 | 0.057667 | -66.729 | -0.026065 | -66.7414 | 56.2793 | 56.1929 | 56.3718 | -66.865 | -66.7428 | -0.022535 | -66.7865 | 56.1757 | 56.358 | 56.1918 | -67.0973 | -0.10931 | -0.053088 | 0.02672 | 0.014249 | 0.12356 | -0.13948 | 0.039387 | -0.34162 | -0.15674 | 0.01287 | -0.030793 | 0.31083 | 0.025592 | -0.14061 | 123.035 | 122.9486 | 123.1275 | 66.7296 | -123.1974 | 122.9313 | 123.1137 | 122.9475 | 66.7331 | -123.4297
1587.8594 | 123.2849 | -66.7053 | 56.2912 | -0.0029761 | -0.020393 | 0.00046154 | 0.053936 | -0.0058778 | 0.062076 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.02966 | 0.057881 | -66.7244 | -0.021486 | -66.7414 | 56.2839 | 56.1929 | 56.3718 | -66.8604 | -66.7336 | -0.022535 | -66.7865 | 56.1757 | 56.3534 | 56.1872 | -67.0927 | -0.15509 | -0.007312 | -0.019055 | -0.036105 | 0.11898 | -0.098278 | 0.080585 | -0.3874 | -0.11555 | -0.028327 | -0.081147 | 0.30625 | 0.062211 | -0.10399 | 122.9892 | 122.8982 | 123.0771 | 66.6838 | -123.1516 | 122.881 | 123.0587 | 122.8925 | 66.6828 | -123.3839
1588.7969 | 123.1979 | -66.7191 | 56.3553 | 0.0046549 | -0.019966 | 0.00067514 | 0.053508 | -0.0060916 | 0.061862 | -0.0074779 | -0.0024119 | -0.00076913 | 0.05739 | 0.029446 | 0.057881 | -66.7244 | -0.021486 | -66.746 | 56.2793 | 56.1792 | 56.3672 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.358 | 56.178 | -67.0973 | -0.14135 | -0.075977 | -0.005322 | -0.02695 | 0.1144 | -0.1761 | 0.011919 | -0.37824 | -0.17963 | -0.023751 | -0.062835 | 0.31541 | 0.002703 | -0.17724 | 122.9984 | 122.8982 | 123.0863 | 66.6976 | -123.2157 | 122.8947 | 123.077 | 122.8971 | 66.6919 | -123.4526
1589.7969 | 123.2666 | -66.7007 | 56.337 | -0.0029761 | -0.019966 | 0.00067514 | 0.053936 | -0.0056642 | 0.062717 | 0.0077831 | -0.0021983 | -0.00098273 | 0.056963 | 0.029233 | 0.057881 | -66.7335 | -0.021486 | -66.7368 | 56.2747 | 56.1792 | 56.3626 | -66.865 | -66.7382 | -0.036271 | -66.7865 | 56.1802 | 56.3626 | 56.1918 | -67.1019 | -0.16424 | -0.062244 | -0.032789 | -0.036103 | 0.12814 | -0.15779 | 0.025651 | -0.40113 | -0.15674 | -0.037482 | -0.085724 | 0.31541 | 0.025593 | -0.14519 | 122.9755 | 122.8799 | 123.0634 | 66.6793 | -123.202 | 122.881 | 123.0633 | 122.8925 | 66.6645 | -123.4389
1590.8594 | 123.2712 | -66.687 | 56.3049 | 0.0046549 | -0.020393 | 0.00046154 | 0.053722 | -0.0056642 | 0.062289 | 0.0077831 | -0.0024119 | -0.0011965 | 0.05739 | 0.029446 | 0.057881 | -66.7381 | -0.030644 | -66.7506 | 56.2747 | 56.1929 | 56.3672 | -66.8696 | -66.7382 | -0.036271 | -66.7819 | 56.1802 | 56.3626 | 56.2009 | -67.111 | -0.18255 | -0.030201 | -0.0511 | -0.063571 | 0.11898 | -0.11201 | 0.062273 | -0.42402 | -0.1247 | -0.051215 | -0.094878 | 0.32914 | 0.057636 | -0.10399 | 122.9617 | 122.8799 | 123.0542 | 66.6564 | -123.1745 | 122.8672 | 123.0496 | 122.888 | 66.6507 | -123.416
1591.7969 | 123.2574 | -66.6962 | 56.3187 | -0.0029761 | -0.019966 | 0.00088894 | 0.053722 | -0.0058778 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.05739 | 0.02966 | 0.057881 | -66.729 | -0.021486 | -66.7414 | 56.2747 | 56.1838 | 56.3718 | -66.8604 | -66.7382 | -0.022535 | -66.7819 | 56.1848 | 56.358 | 56.1872 | -67.1019 | -0.16424 | -0.043934 | -0.032789 | -0.04526 | 0.11898 | -0.1349 | 0.053119 | -0.40571 | -0.13386 | -0.04206 | -0.085723 | 0.31999 | 0.039324 | -0.13146 | 122.9709 | 122.8799 | 123.068 | 66.6747 | -123.1791 | 122.881 | 123.0542 | 122.8834 | 66.6736 | -123.4205
1592.7969 | 123.2117 | -66.7374 | 56.337 | 0.0046549 | -0.019966 | 0.00067514 | 0.053722 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057176 | 0.029446 | 0.058094 | -66.729 | -0.021486 | -66.7368 | 56.2702 | 56.1883 | 56.3718 | -66.8741 | -66.7428 | -0.017956 | -66.7865 | 56.1757 | 56.3626 | 56.2055 | -67.1019 | -0.13678 | -0.066823 | 0.00841 | 0.000518 | 0.1373 | -0.14863 | 0.034809 | -0.36451 | -0.16132 | -0.00544 | -0.049103 | 0.31541 | 0.025593 | -0.13146 | 123.0075 | 122.9257 | 123.1091 | 66.7159 | -123.2111 | 122.913 | 123.0999 | 122.9429 | 66.7194 | -123.4389
1593.8594 | 123.2941 | -66.7145 | 56.2912 | 0.0046549 | -0.019966 | 0.00046154 | 0.053722 | -0.0060916 | 0.062076 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057176 | 0.02966 | 0.057667 | -66.7198 | -0.016908 | -66.7506 | 56.2747 | 56.1929 | 56.3718 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3671 | 56.1964 | -67.1019 | -0.14593 | -0.016468 | -0.005321 | -0.036105 | 0.10983 | -0.098278 | 0.080585 | -0.3874 | -0.11097 | -0.028328 | -0.067412 | 0.31999 | 0.075947 | -0.094838 | 122.9892 | 122.9074 | 123.0863 | 66.6976 | -123.1516 | 122.8947 | 123.0816 | 122.9108 | 66.6874 | -123.3931
1594.7969 | 123.1934 | -66.7282 | 56.3278 | -0.0029761 | -0.019966 | 0.00088894 | 0.053508 | -0.0060916 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.05739 | 0.029446 | 0.058094 | -66.729 | -0.016908 | -66.7552 | 56.2839 | 56.1975 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.791 | 56.1757 | 56.3671 | 56.1872 | -67.1019 | -0.14136 | -0.043933 | -0.000746 | -0.026951 | 0.11441 | -0.13032 | 0.043964 | -0.37367 | -0.15217 | -0.014596 | -0.062837 | 0.31083 | 0.039326 | -0.14062 | 123.0121 | 122.9257 | 123.1 | 66.7113 | -123.1974 | 122.9039 | 123.0954 | 122.9154 | 66.7057 | -123.4297
1595.7969 | 123.2025 | -66.7145 | 56.3141 | -0.0029761 | -0.020393 | 0.00088894 | 0.053936 | -0.0056642 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.056963 | 0.029446 | 0.057667 | -66.7335 | -0.021486 | -66.7552 | 56.2839 | 56.1883 | 56.3718 | -66.865 | -66.7382 | -0.022535 | -66.7773 | 56.1711 | 56.358 | 56.1826 | -67.1065 | -0.15051 | -0.0302 | -0.019056 | -0.040683 | 0.10983 | -0.12575 | 0.057697 | -0.39198 | -0.14301 | -0.023749 | -0.062833 | 0.32914 | 0.043902 | -0.13146 | 122.9984 | 122.9028 | 123.0863 | 66.693 | -123.1791 | 122.8856 | 123.0725 | 122.8971 | 66.6919 | -123.4205
1596.8594 | 123.2758 | -66.7053 | 56.2958 | -0.0029761 | -0.019966 | 0.00067514 | 0.053508 | -0.0058778 | 0.061862 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.02966 | 0.057667 | -66.729 | -0.021486 | -66.7414 | 56.2747 | 56.1929 | 56.3718 | -66.8604 | -66.7474 | -0.031692 | -66.7773 | 56.1711 | 56.358 | 56.1872 | -67.1019 | -0.15509 | -0.021045 | -0.023634 | -0.036105 | 0.11898 | -0.10285 | 0.076008 | -0.39656 | -0.1247 | -0.042063 | -0.071989 | 0.32457 | 0.062213 | -0.10857 | 122.9801 | 122.8982 | 123.0771 | 66.6838 | -123.1562 | 122.8764 | 123.0633 | 122.8925 | 66.6736 | -123.3977
1597.7969 | 123.2025 | -66.7328 | 56.337 | 0.0046549 | -0.019966 | 0.00088894 | 0.053936 | -0.0060916 | 0.062717 | 0.0077831 | -0.0024119 | -0.00055553 | 0.05739 | 0.029874 | 0.058094 | -66.7335 | -0.026065 | -66.7506 | 56.2702 | 56.1883 | 56.3626 | -66.8604 | -66.7474 | -0.027113 | -66.7773 | 56.1848 | 56.358 | 56.2009 | -67.1019 | -0.12762 | -0.066823 | -0.000746 | -0.017795 | 0.10983 | -0.14863 | 0.025651 | -0.36909 | -0.15217 | -0.014597 | -0.044523 | 0.32457 | 0.021014 | -0.13604 | 123.0029 | 122.9211 | 123.0954 | 66.7067 | -123.1974 | 122.9176 | 123.0908 | 122.9337 | 66.7057 | -123.4389
1598.7969 | 123.175 | -66.7511 | 56.3324 | -0.0029761 | -0.020179 | 0.00046154 | 0.053722 | -0.0060916 | 0.062289 | 0.0077831 | -0.0026255 | -0.00098273 | 0.057176 | 0.029874 | 0.057881 | -66.7244 | -0.016908 | -66.7506 | 56.2793 | 56.2021 | 56.3718 | -66.8741 | -66.7428 | -0.027113 | -66.7865 | 56.1757 | 56.3626 | 56.1826 | -67.1019 | -0.12305 | -0.053088 | 0.026722 | 0.000516 | 0.12356 | -0.13032 | 0.039387 | -0.35078 | -0.15674 | 0.008293 | -0.03537 | 0.31541 | 0.030171 | -0.14977 | 123.0304 | 122.9532 | 123.1229 | 66.7342 | -123.2065 | 122.9268 | 123.1137 | 122.9337 | 66.724 | -123.4343
1599.7969 | 123.1705 | -66.7648 | 56.3278 | 0.0046549 | -0.020179 | 0.00088894 | 0.053722 | -0.0058778 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057604 | 0.02966 | 0.057881 | -66.729 | -0.021486 | -66.7552 | 56.2747 | 56.2067 | 56.3718 | -66.865 | -66.7428 | -0.031692 | -66.7865 | 56.1757 | 56.3534 | 56.2101 | -67.1065 | -0.10016 | -0.053089 | 0.035876 | 0.009671 | 0.10983 | -0.12116 | 0.043964 | -0.34162 | -0.15217 | 0.022026 | -0.021637 | 0.31999 | 0.02559 | -0.11772 | 123.0396 | 122.9715 | 123.1366 | 66.7433 | -123.1928 | 122.9405 | 123.1182 | 122.9749 | 66.7331 | -123.4343
1600.8594 | 123.2758 | -66.6916 | 56.2912 | 0.0046549 | -0.020393 | 0.00046154 | 0.053722 | -0.0060916 | 0.062076 | -0.0074779 | -0.0028393 | -0.00012813 | 0.057176 | 0.029233 | 0.058094 | -66.7244 | -0.026065 | -66.746 | 56.2747 | 56.1792 | 56.3672 | -66.865 | -66.7382 | -0.022535 | -66.7865 | 56.1802 | 56.358 | 56.2055 | -67.1019 | -0.1734 | -0.016468 | -0.032788 | -0.054416 | 0.11898 | -0.11201 | 0.076006 | -0.41029 | -0.11097 | -0.046638 | -0.09488 | 0.31541 | 0.06679 | -0.085681 | 122.9663 | 122.8708 | 123.0588 | 66.6655 | -123.1562 | 122.8718 | 123.0496 | 122.8971 | 66.6691 | -123.3931
1601.7969 | 123.1567 | -66.7191 | 56.3461 | -0.0029761 | -0.020393 | 0.00046154 | 0.053295 | -0.0060916 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057817 | 0.030087 | 0.057881 | -66.7244 | -0.026065 | -66.7414 | 56.2793 | 56.1883 | 56.3718 | -66.865 | -66.7474 | -0.031692 | -66.7819 | 56.1848 | 56.358 | 56.2009 | -67.111 | -0.14593 | -0.066821 | -0.005322 | -0.022372 | 0.12356 | -0.15779 | 0.025654 | -0.39198 | -0.16132 | -0.02833 | -0.062835 | 0.32914 | 0.011859 | -0.14519 | 122.9984 | 122.9074 | 123.0908 | 66.693 | -123.2111 | 122.9039 | 123.077 | 122.92 | 66.6874 | -123.4572
1602.7969 | 123.1796 | -66.7374 | 56.3507 | 0.0046549 | -0.020179 | 0.00067514 | 0.053722 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.05739 | 0.029446 | 0.057453 | -66.7244 | -0.026065 | -66.7552 | 56.2702 | 56.1883 | 56.3672 | -66.8604 | -66.7382 | -0.022535 | -66.7773 | 56.1711 | 56.358 | 56.1872 | -67.1019 | -0.12304 | -0.080556 | 0.012989 | -0.017795 | 0.10525 | -0.16237 | 0.016497 | -0.36451 | -0.17963 | -0.000861 | -0.039945 | 0.32457 | 0.007281 | -0.1635 | 123.0075 | 122.9257 | 123.1046 | 66.7113 | -123.2111 | 122.9084 | 123.0954 | 122.9246 | 66.7148 | -123.4526
1603.7969 | 123.1705 | -66.7328 | 56.3507 | 0.0046549 | -0.020393 | 0.00046154 | 0.053722 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00076913 | 0.05739 | 0.029446 | 0.057881 | -66.7335 | -0.021486 | -66.7552 | 56.2747 | 56.1838 | 56.3626 | -66.8696 | -66.7428 | -0.031692 | -66.7773 | 56.1802 | 56.3671 | 56.1918 | -67.0973 | -0.13678 | -0.075977 | -0.000746 | -0.022373 | 0.11441 | -0.16694 | 0.011918 | -0.36451 | -0.17048 | -0.010018 | -0.044523 | 0.31999 | 0.016438 | -0.15893 | 123.0075 | 122.9166 | 123.0954 | 66.7113 | -123.2203 | 122.913 | 123.0999 | 122.9246 | 66.7011 | -123.448
1604.7969 | 123.2025 | -66.7465 | 56.3049 | -0.0029761 | -0.019966 | 0.00088894 | 0.053936 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057817 | 0.029874 | 0.057881 | -66.729 | -0.021486 | -66.7506 | 56.2793 | 56.1838 | 56.3672 | -66.865 | -66.7474 | -0.017956 | -66.7773 | 56.1848 | 56.3717 | 56.2055 | -67.0973 | -0.11847 | -0.025623 | 0.017565 | -0.004062 | 0.1144 | -0.12117 | 0.062273 | -0.35078 | -0.12012 | -0.000864 | -0.03079 | 0.31999 | 0.066793 | -0.099414 | 123.0258 | 122.9303 | 123.1137 | 66.725 | -123.1699 | 122.9313 | 123.1182 | 122.952 | 66.7286 | -123.4022
1605.7969 | 123.1842 | -66.7236 | 56.3507 | -0.0029761 | -0.020179 | 0.00067514 | 0.053722 | -0.0063052 | 0.062289 | 0.0077831 | -0.0026255 | -0.00055553 | 0.05739 | 0.030087 | 0.058094 | -66.7198 | -0.026065 | -66.7414 | 56.2747 | 56.1975 | 56.3764 | -66.8741 | -66.7428 | -0.017956 | -66.7865 | 56.1757 | 56.3671 | 56.178 | -67.1065 | -0.15051 | -0.075977 | 0.003834 | -0.017794 | 0.13272 | -0.15321 | 0.025654 | -0.38282 | -0.17506 | -0.019173 | -0.062836 | 0.31999 | 0.016438 | -0.17266 | 122.9984 | 122.9211 | 123.1 | 66.6976 | -123.2249 | 122.8993 | 123.0908 | 122.9017 | 66.7057 | -123.4572
1606.8594 | 123.1384 | -66.7236 | 56.2912 | -0.0029761 | -0.020179 | 0.00046154 | 0.053722 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.05739 | 0.030087 | 0.057453 | -66.729 | -0.012329 | -66.7506 | 56.2793 | 56.2067 | 56.3626 | -66.8696 | -66.7474 | -0.022535 | -66.7727 | 56.1802 | 56.3626 | 56.1964 | -67.1065 | -0.14593 | -0.01189 | -0.005323 | -0.02695 | 0.11898 | -0.084541 | 0.071427 | -0.38282 | -0.11097 | -0.023752 | -0.049099 | 0.33372 | 0.071369 | -0.094838 | 123.0029 | 122.9303 | 123.0863 | 66.7113 | -123.1608 | 122.9039 | 123.0862 | 122.92 | 66.7011 | -123.3977
1607.7969 | 123.2071 | -66.7236 | 56.3324 | 0.012286 | -0.020179 | 0.00067514 | 0.053508 | -0.0063052 | 0.062289 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057817 | 0.029874 | 0.057453 | -66.729 | -0.021486 | -66.7552 | 56.2747 | 56.1929 | 56.3764 | -66.8741 | -66.7428 | -0.027113 | -66.7773 | 56.1802 | 56.3671 | 56.2055 | -67.1019 | -0.15051 | -0.057666 | -0.005323 | -0.031528 | 0.11898 | -0.13948 | 0.043965 | -0.37824 | -0.15217 | -0.019173 | -0.053678 | 0.32457 | 0.034749 | -0.12688 | 122.9984 | 122.9166 | 123.1 | 66.7021 | -123.2065 | 122.9039 | 123.0908 | 122.9292 | 66.6965 | -123.4343
1608.8594 | 123.143 | -66.7465 | 56.3507 | -0.010607 | -0.020179 | 0.00024794 | 0.053722 | -0.0060916 | 0.06293 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.02966 | 0.057881 | -66.729 | -0.021486 | -66.7552 | 56.2793 | 56.2021 | 56.3718 | -66.8696 | -66.7474 | -0.027113 | -66.7865 | 56.1802 | 56.3626 | 56.1826 | -67.1019 | -0.12305 | -0.071399 | 0.017565 | -0.00864 | 0.11441 | -0.14863 | 0.021076 | -0.35536 | -0.17048 | -0.000864 | -0.039948 | 0.31541 | 0.01186 | -0.16808 | 123.0258 | 122.9486 | 123.1183 | 66.725 | -123.2203 | 122.9268 | 123.1091 | 122.9291 | 66.7194 | -123.4526
1609.7969 | 123.1888 | -66.7557 | 56.3416 | 0.012286 | -0.020393 | 0.00046154 | 0.053508 | -0.0058778 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.05739 | 0.030087 | 0.058094 | -66.729 | -0.016908 | -66.746 | 56.2793 | 56.1929 | 56.3718 | -66.8696 | -66.7382 | -0.022535 | -66.7865 | 56.1848 | 56.358 | 56.1872 | -67.1065 | -0.11389 | -0.062244 | 0.02672 | 0.009671 | 0.12356 | -0.14863 | 0.030231 | -0.35078 | -0.15674 | 0.017449 | -0.030793 | 0.31999 | 0.016436 | -0.15435 | 123.035 | 122.9486 | 123.1275 | 66.7388 | -123.2111 | 122.9405 | 123.1137 | 122.9429 | 66.7331 | -123.448
1610.7969 | 123.2071 | -66.7191 | 56.2958 | -0.0029761 | -0.020179 | 0.00046154 | 0.053722 | -0.0065188 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.057604 | 0.02966 | 0.057881 | -66.7244 | -0.021486 | -66.7414 | 56.2747 | 56.1838 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7819 | 56.1757 | 56.3626 | 56.2009 | -67.0927 | -0.15051 | -0.021045 | -0.005322 | -0.022372 | 0.12814 | -0.11201 | 0.076008 | -0.37367 | -0.12012 | -0.023751 | -0.062835 | 0.31083 | 0.066792 | -0.094837 | 122.9938 | 122.9028 | 123.0908 | 66.6976 | -123.1653 | 122.8947 | 123.0816 | 122.92 | 66.6965 | -123.3885
1611.7969 | 123.1934 | -66.7419 | 56.3187 | -0.0029761 | -0.019966 | 0.00067514 | 0.053508 | -0.0060916 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057604 | 0.029874 | 0.057881 | -66.7244 | -0.021486 | -66.7506 | 56.2839 | 56.2021 | 56.3672 | -66.865 | -66.7474 | -0.027113 | -66.7773 | 56.1757 | 56.358 | 56.1872 | -67.1019 | -0.12304 | -0.034778 | 0.017566 | -0.00864 | 0.1144 | -0.11659 | 0.04854 | -0.35993 | -0.14301 | -0.005442 | -0.035368 | 0.32457 | 0.039324 | -0.13146 | 123.0258 | 122.944 | 123.1091 | 66.7205 | -123.1837 | 122.9176 | 123.0999 | 122.9291 | 66.7148 | -123.4205
1612.7969 | 123.1888 | -66.7465 | 56.3095 | -0.0029761 | -0.020179 | 0.00067514 | 0.053508 | -0.0060916 | 0.062717 | 0.0077831 | -0.0026255 | -0.00098273 | 0.057176 | 0.030087 | 0.058094 | -66.729 | -0.016908 | -66.7552 | 56.2793 | 56.1792 | 56.3672 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1711 | 56.3671 | 56.2009 | -67.1019 | -0.11847 | -0.0302 | 0.017565 | -0.00864 | 0.10983 | -0.13032 | 0.057696 | -0.35536 | -0.13844 | 0.003715 | -0.035369 | 0.31999 | 0.057637 | -0.10857 | 123.0258 | 122.9257 | 123.1137 | 66.7296 | -123.1745 | 122.9176 | 123.1137 | 122.9475 | 66.724 | -123.4114
1613.8594 | 123.2574 | -66.6824 | 56.3095 | 0.0046549 | -0.02082 | 0.00067514 | 0.053722 | -0.0056642 | 0.062076 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057604 | 0.029874 | 0.058094 | -66.729 | -0.021486 | -66.746 | 56.2747 | 56.1883 | 56.3672 | -66.8604 | -66.7474 | -0.022535 | -66.7819 | 56.1802 | 56.3626 | 56.1872 | -67.1019 | -0.17797 | -0.034778 | -0.046522 | -0.063571 | 0.1144 | -0.12117 | 0.057696 | -0.41944 | -0.12928 | -0.064951 | -0.099456 | 0.31999 | 0.053059 | -0.1223 | 122.9572 | 122.8708 | 123.0496 | 66.6609 | -123.1699 | 122.8627 | 123.045 | 122.8696 | 66.6599 | -123.4114
1614.7969 | 123.1476 | -66.7694 | 56.3049 | -0.010607 | -0.020179 | 0.00024794 | 0.053508 | -0.0060916 | 0.062503 | 0.0077831 | -0.0026255 | -0.00098273 | 0.05739 | 0.030087 | 0.058094 | -66.7335 | -0.021486 | -66.7506 | 56.2793 | 56.1929 | 56.3764 | -66.8604 | -66.7428 | -0.031692 | -66.7773 | 56.1757 | 56.3626 | 56.1918 | -67.111 | -0.090999 | -0.025623 | 0.035875 | 0.018826 | 0.10983 | -0.11201 | 0.07143 | -0.34163 | -0.12928 | 0.026603 | -0.007902 | 0.33372 | 0.057636 | -0.11315 | 123.0487 | 122.9623 | 123.1458 | 66.7479 | -123.1653 | 122.9451 | 123.132 | 122.9612 | 66.7377 | -123.416
1615.7969 | 123.2117 | -66.7328 | 56.3187 | -0.010607 | -0.020607 | 0.00046154 | 0.053508 | -0.0060916 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057604 | 0.029874 | 0.057667 | -66.729 | -0.016908 | -66.7414 | 56.2793 | 56.1975 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7819 | 56.1802 | 56.3671 | 56.1918 | -67.1065 | -0.13678 | -0.039356 | 0.003832 | -0.008639 | 0.12814 | -0.12117 | 0.053119 | -0.37367 | -0.13843 | -0.010018 | -0.049102 | 0.32457 | 0.048481 | -0.12688 | 123.0121 | 122.9303 | 123.1046 | 66.7159 | -123.1882 | 122.913 | 123.0999 | 122.9246 | 66.7103 | -123.4251
1616.7969 | 123.1842 | -66.7419 | 56.3278 | -0.0029761 | -0.020393 | 0.00046154 | 0.053722 | -0.0058778 | 0.062289 | 0.0077831 | -0.0028393 | -0.00098273 | 0.057604 | 0.030087 | 0.057881 | -66.7244 | -0.021486 | -66.7506 | 56.2793 | 56.2021 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7773 | 56.1802 | 56.3626 | 56.1964 | -67.1019 | -0.12762 | -0.048511 | 0.017566 | -0.00864 | 0.11898 | -0.12574 | 0.043964 | -0.35993 | -0.14759 | -0.000863 | -0.035368 | 0.32457 | 0.034748 | -0.13146 | 123.0213 | 122.944 | 123.1137 | 66.7205 | -123.1974 | 122.9222 | 123.1045 | 122.9383 | 66.7194 | -123.4297
1617.7969 | 123.1842 | -66.7419 | 56.3324 | -0.0029761 | -0.020607 | 0.00067514 | 0.053295 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.05739 | 0.030087 | 0.058094 | -66.7198 | -0.021486 | -66.7552 | 56.2702 | 56.1929 | 56.3764 | -66.8741 | -66.7382 | -0.022535 | -66.7773 | 56.1757 | 56.358 | 56.1918 | -67.1019 | -0.1322 | -0.062245 | 0.022144 | -0.013218 | 0.11898 | -0.13948 | 0.043965 | -0.35993 | -0.15674 | 0.003716 | -0.035368 | 0.32457 | 0.025592 | -0.14061 | 123.0121 | 122.9349 | 123.1183 | 66.7205 | -123.2065 | 122.9176 | 123.0999 | 122.9337 | 66.7194 | -123.4343
1618.7969 | 123.1705 | -66.7465 | 56.3095 | -0.0029761 | -0.020393 | 0.00067514 | 0.053936 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057817 | 0.02966 | 0.058094 | -66.7198 | -0.021486 | -66.7597 | 56.2793 | 56.2067 | 56.3672 | -66.8558 | -66.7428 | -0.031692 | -66.7819 | 56.1802 | 56.3626 | 56.1918 | -67.0973 | -0.10931 | -0.0302 | 0.026722 | -0.013219 | 0.09609 | -0.10285 | 0.057696 | -0.35078 | -0.12928 | 0.003715 | -0.035369 | 0.31541 | 0.053059 | -0.11773 | 123.0258 | 122.9532 | 123.1137 | 66.725 | -123.1653 | 122.9268 | 123.1091 | 122.9383 | 66.7148 | -123.4068
1619.8594 | 123.2208 | -66.7374 | 56.3095 | 0.012286 | -0.020393 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.05739 | 0.030087 | 0.058094 | -66.729 | -0.021486 | -66.7506 | 56.2839 | 56.1883 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7727 | 56.1757 | 56.358 | 56.178 | -67.1065 | -0.1322 | -0.025622 | 0.00841 | -0.013217 | 0.11898 | -0.12117 | 0.062275 | -0.36909 | -0.13386 | -0.00544 | -0.035366 | 0.33372 | 0.04848 | -0.13146 | 123.0213 | 122.9257 | 123.1091 | 66.7159 | -123.1791 | 122.913 | 123.0954 | 122.9154 | 66.7148 | -123.416
1620.7969 | 123.1613 | -66.7419 | 56.2912 | -0.010607 | -0.020393 | 0.00046154 | 0.053722 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.05739 | 0.030087 | 0.057881 | -66.729 | -0.016908 | -66.7414 | 56.2747 | 56.1883 | 56.3718 | -66.865 | -66.7428 | -0.031692 | -66.7819 | 56.1757 | 56.3626 | 56.1872 | -67.1019 | -0.12304 | -0.016468 | 0.012987 | 0.000516 | 0.12356 | -0.10286 | 0.080585 | -0.35993 | -0.11555 | -0.000863 | -0.039947 | 0.31999 | 0.071369 | -0.10399 | 123.0167 | 122.9303 | 123.1137 | 66.725 | -123.1562 | 122.9176 | 123.1045 | 122.9291 | 66.7103 | -123.3931
1621.7969 | 123.1888 | -66.7374 | 56.3095 | 0.0046549 | -0.02082 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | -0.0074779 | -0.0026255 | -0.00098273 | 0.05739 | 0.029874 | 0.057881 | -66.729 | -0.021486 | -66.7552 | 56.2747 | 56.1975 | 56.3809 | -66.8833 | -66.7474 | -0.022535 | -66.7819 | 56.1757 | 56.3671 | 56.2055 | -67.1019 | -0.14594 | -0.034778 | 0.00841 | -0.017795 | 0.12814 | -0.11201 | 0.071432 | -0.36451 | -0.13386 | -0.010019 | -0.044524 | 0.31999 | 0.057637 | -0.10399 | 123.0121 | 122.9349 | 123.1183 | 66.7159 | -123.1928 | 122.913 | 123.1045 | 122.9429 | 66.7148 | -123.4114
1622.8594 | 123.1842 | -66.7328 | 56.3507 | 0.012286 | -0.020607 | 0.00046154 | 0.053722 | -0.0058778 | 0.06293 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057604 | 0.030087 | 0.057667 | -66.7244 | -0.021486 | -66.746 | 56.2793 | 56.1929 | 56.3718 | -66.8696 | -66.7428 | -0.031692 | -66.7865 | 56.1802 | 56.3671 | 56.1918 | -67.1019 | -0.13678 | -0.071399 | 0.008411 | -0.013217 | 0.12356 | -0.15779 | 0.021076 | -0.36909 | -0.17048 | -0.010018 | -0.053681 | 0.31541 | 0.016438 | -0.15893 | 123.0121 | 122.9257 | 123.1046 | 66.7113 | -123.2203 | 122.913 | 123.0999 | 122.9246 | 66.7011 | -123.4526
1623.7969 | 123.1659 | -66.7511 | 56.3278 | -0.0029761 | -0.020607 | 0.00046154 | 0.053722 | -0.0060916 | 0.062503 | 0.0077831 | -0.0028393 | -0.00098273 | 0.057817 | 0.030087 | 0.058308 | -66.7244 | -0.026065 | -66.746 | 56.2702 | 56.1975 | 56.3809 | -66.8696 | -66.7474 | -0.022535 | -66.7819 | 56.1757 | 56.3626 | 56.1872 | -67.1019 | -0.11847 | -0.057668 | 0.026722 | 0.005094 | 0.12356 | -0.13032 | 0.053121 | -0.35078 | -0.15217 | 0.003714 | -0.030791 | 0.31999 | 0.034748 | -0.14062 | 123.0213 | 122.9486 | 123.132 | 66.725 | -123.1974 | 122.9268 | 123.1137 | 122.9383 | 66.7286 | -123.4297
1624.8594 | 123.1888 | -66.7328 | 56.3141 | -0.010607 | -0.021034 | 0.00046154 | 0.053508 | -0.0058778 | 0.062717 | 0.0077831 | -0.0026255 | -0.00098273 | 0.057604 | 0.029874 | 0.058094 | -66.729 | -0.012329 | -66.746 | 56.2793 | 56.1838 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1711 | 56.358 | 56.2009 | -67.1019 | -0.13678 | -0.034778 | 0.003832 | -0.013217 | 0.12356 | -0.13032 | 0.062275 | -0.36909 | -0.14301 | -0.010018 | -0.049102 | 0.31999 | 0.043902 | -0.11315 | 123.0121 | 122.9166 | 123.1091 | 66.7205 | -123.1837 | 122.9039 | 123.0908 | 122.9337 | 66.7057 | -123.416
1625.7969 | 123.1934 | -66.7328 | 56.3004 | -0.010607 | -0.020393 | 0.00088894 | 0.053508 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.05739 | 0.029874 | 0.057881 | -66.7244 | -0.026065 | -66.746 | 56.2793 | 56.2067 | 56.3718 | -66.8604 | -66.7428 | -0.036271 | -66.7865 | 56.1757 | 56.3626 | 56.2009 | -67.1065 | -0.12762 | -0.021045 | 0.008411 | -0.013217 | 0.1144 | -0.093696 | 0.07143 | -0.37367 | -0.1247 | -0.010018 | -0.053681 | 0.31999 | 0.062214 | -0.099415 | 123.0121 | 122.9394 | 123.1046 | 66.7067 | -123.1608 | 122.9084 | 123.0954 | 122.9337 | 66.6965 | -123.4068
1626.7969 | 123.2025 | -66.7511 | 56.3004 | 0.0046549 | -0.020393 | 0.00046154 | 0.053722 | -0.0058778 | 0.062503 | -0.0074779 | -0.0024119 | -0.00055553 | 0.05739 | 0.030087 | 0.057881 | -66.7244 | -0.012329 | -66.7643 | 56.2747 | 56.1975 | 56.3809 | -66.8741 | -66.7428 | -0.031692 | -66.7819 | 56.1848 | 56.3626 | 56.1735 | -67.1065 | -0.12305 | -0.025623 | 0.026722 | -0.013219 | 0.10983 | -0.10285 | 0.080587 | -0.35536 | -0.11554 | 0.008293 | -0.030791 | 0.32457 | 0.062214 | -0.12689 | 123.0258 | 122.9486 | 123.132 | 66.7388 | -123.1745 | 122.9359 | 123.1137 | 122.9246 | 66.7194 | -123.4068
1627.8594 | 123.143 | -66.7557 | 56.3232 | -0.010607 | -0.020607 | 0.00088894 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057176 | 0.030301 | 0.057667 | -66.7244 | -0.021486 | -66.746 | 56.2793 | 56.2021 | 56.3809 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1757 | 56.3671 | 56.2009 | -67.1065 | -0.10931 | -0.043933 | 0.031299 | 0.009671 | 0.11898 | -0.12116 | 0.057699 | -0.35078 | -0.14759 | 0.01287 | -0.026214 | 0.32457 | 0.043904 | -0.1223 | 123.035 | 122.9578 | 123.1366 | 66.7342 | -123.1882 | 122.9313 | 123.1228 | 122.9566 | 66.7331 | -123.4297
1628.7969 | 123.175 | -66.7419 | 56.3187 | -0.010607 | -0.02082 | 0.00067514 | 0.053508 | -0.0058778 | 0.062503 | -0.0074779 | -0.0021983 | -0.00076913 | 0.057604 | 0.030301 | 0.057881 | -66.7244 | -0.012329 | -66.7414 | 56.2747 | 56.1929 | 56.3764 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1757 | 56.358 | 56.1964 | -67.1065 | -0.12762 | -0.043934 | 0.017566 | 0.000516 | 0.12814 | -0.12574 | 0.057697 | -0.36451 | -0.14301 | 0.003716 | -0.039947 | 0.32457 | 0.039324 | -0.1223 | 123.0167 | 122.9349 | 123.1183 | 66.7296 | -123.1882 | 122.9176 | 123.0999 | 122.9383 | 66.7148 | -123.4251
1629.8594 | 123.1384 | -66.7786 | 56.3461 | 0.012286 | -0.020179 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | -0.0074779 | -0.0028393 | -0.00076913 | 0.05739 | 0.029874 | 0.057667 | -66.7335 | -0.021486 | -66.7506 | 56.2747 | 56.1929 | 56.3718 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.3717 | 56.1826 | -67.0927 | -0.091002 | -0.071399 | 0.04503 | 0.027981 | 0.11898 | -0.15321 | 0.025654 | -0.31416 | -0.17048 | 0.035758 | -0.003326 | 0.31083 | 0.025595 | -0.16351 | 123.0533 | 122.9715 | 123.1503 | 66.7571 | -123.2157 | 122.9542 | 123.1503 | 122.9612 | 66.7515 | -123.4389
1630.7969 | 123.1567 | -66.7557 | 56.3232 | -0.010607 | -0.020607 | 0.00067514 | 0.053722 | -0.0060916 | 0.062717 | 0.0077831 | -0.0026255 | -0.00098273 | 0.05739 | 0.029874 | 0.057881 | -66.729 | -0.016908 | -66.746 | 56.2793 | 56.1975 | 56.3718 | -66.8696 | -66.7474 | -0.017956 | -66.7819 | 56.1802 | 56.3671 | 56.178 | -67.1065 | -0.11389 | -0.043933 | 0.02672 | 0.009671 | 0.12356 | -0.12574 | 0.048542 | -0.35078 | -0.14301 | 0.008291 | -0.026214 | 0.32457 | 0.043904 | -0.1452 | 123.035 | 122.9532 | 123.1275 | 66.7388 | -123.1928 | 122.9359 | 123.1228 | 122.9337 | 66.7377 | -123.4297
1631.8594 | 123.2117 | -66.7191 | 56.3324 | -0.0029761 | -0.02082 | 0.00046154 | 0.053936 | -0.0060916 | 0.062503 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057604 | 0.030087 | 0.057667 | -66.729 | -0.016908 | -66.7552 | 56.2747 | 56.1975 | 56.3764 | -66.8696 | -66.7428 | -0.022535 | -66.791 | 56.1757 | 56.3626 | 56.1872 | -67.1065 | -0.15051 | -0.057666 | -0.009901 | -0.036106 | 0.11441 | -0.1349 | 0.043965 | -0.3874 | -0.15674 | -0.023751 | -0.071992 | 0.31541 | 0.030171 | -0.14519 | 122.9938 | 122.9166 | 123.0954 | 66.7021 | -123.202 | 122.8947 | 123.0816 | 122.9063 | 66.6965 | -123.4389
1632.7969 | 123.143 | -66.7511 | 56.3049 | -0.010607 | -0.020607 | 0.00088894 | 0.053722 | -0.0058778 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.05739 | 0.030301 | 0.057667 | -66.7244 | -0.016908 | -66.746 | 56.2793 | 56.1929 | 56.3718 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1802 | 56.3626 | 56.1918 | -67.1019 | -0.11847 | -0.025623 | 0.026722 | 0.005094 | 0.12356 | -0.11201 | 0.066852 | -0.35078 | -0.1247 | 0.012872 | -0.030791 | 0.31999 | 0.057636 | -0.11315 | 123.0304 | 122.944 | 123.1229 | 66.7342 | -123.1745 | 122.9313 | 123.1137 | 122.9429 | 66.724 | -123.4068
1633.8594 | 123.1705 | -66.7557 | 56.3095 | 0.0046549 | -0.02082 | 0.00067514 | 0.053722 | -0.0058778 | 0.06293 | 0.0077831 | -0.0026255 | -0.00098273 | 0.05739 | 0.029874 | 0.057881 | -66.729 | -0.016908 | -66.7506 | 56.2747 | 56.1929 | 56.3718 | -66.865 | -66.7382 | -0.017956 | -66.791 | 56.1848 | 56.3671 | 56.2101 | -67.1019 | -0.10931 | -0.034778 | 0.02672 | 0.005093 | 0.1144 | -0.11659 | 0.062275 | -0.3462 | -0.1247 | 0.017449 | -0.035371 | 0.31083 | 0.057637 | -0.099412 | 123.0304 | 122.9486 | 123.1275 | 66.7388 | -123.1745 | 122.9405 | 123.1228 | 122.9658 | 66.7377 | -123.4114
1634.7969 | 123.3032 | -66.7191 | 56.2546 | -0.0029761 | -0.02082 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | -0.0074779 | -0.0026255 | -0.00098273 | 0.05739 | 0.030515 | 0.057667 | -66.7244 | -0.021486 | -66.7414 | 56.2793 | 56.2067 | 56.3809 | -66.8696 | -66.7428 | -0.027113 | -66.7727 | 56.1757 | 56.358 | 56.1872 | -67.1019 | -0.15051 | 0.024731 | -0.005322 | -0.022372 | 0.12814 | -0.04792 | 0.12636 | -0.38282 | -0.078925 | -0.023751 | -0.053677 | 0.32914 | 0.10341 | -0.067374 | 122.9984 | 122.9257 | 123.1 | 66.6976 | -123.1241 | 122.8947 | 123.077 | 122.9063 | 66.6919 | -123.3565
1635.8594 | 123.1567 | -66.7419 | 56.3278 | -0.010607 | -0.020607 | 0.00067514 | 0.053936 | -0.0063052 | 0.062717 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057604 | 0.030087 | 0.057881 | -66.7198 | -0.016908 | -66.7552 | 56.2793 | 56.2067 | 56.3764 | -66.8741 | -66.7474 | -0.017956 | -66.7727 | 56.1757 | 56.3671 | 56.1964 | -67.1065 | -0.1322 | -0.048511 | 0.022144 | -0.013218 | 0.11898 | -0.12116 | 0.048542 | -0.36451 | -0.15217 | -0.005442 | -0.030789 | 0.33372 | 0.039326 | -0.13146 | 123.0213 | 122.9486 | 123.1183 | 66.725 | -123.202 | 122.9176 | 123.1091 | 122.9383 | 66.724 | -123.4343
1636.7969 | 123.2529 | -66.7191 | 56.282 | -0.010607 | -0.020393 | 0.00067514 | 0.053722 | -0.0056642 | 0.062503 | -0.015108 | -0.0024119 | -0.00098273 | 0.057176 | 0.030087 | 0.057453 | -66.7335 | -0.021486 | -66.7506 | 56.2747 | 56.1929 | 56.3672 | -66.865 | -66.7382 | -0.022535 | -66.7819 | 56.1802 | 56.3626 | 56.1964 | -67.1065 | -0.14593 | -0.007312 | -0.014479 | -0.031528 | 0.1144 | -0.089122 | 0.085162 | -0.3874 | -0.10181 | -0.019172 | -0.062835 | 0.32457 | 0.080525 | -0.085682 | 122.9938 | 122.912 | 123.0863 | 66.6976 | -123.147 | 122.8993 | 123.0816 | 122.9154 | 66.6965 | -123.3885
1637.7969 | 123.1384 | -66.7465 | 56.3416 | -0.0029761 | -0.02082 | 0.00046154 | 0.053508 | -0.0060916 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.057604 | 0.030301 | 0.057881 | -66.729 | -0.016908 | -66.7414 | 56.2702 | 56.2021 | 56.3764 | -66.8696 | -66.7474 | -0.022535 | -66.7865 | 56.1802 | 56.3626 | 56.1964 | -67.1065 | -0.12305 | -0.071401 | 0.017565 | 0.005094 | 0.12814 | -0.13947 | 0.034809 | -0.35993 | -0.16132 | -0.000864 | -0.039948 | 0.31999 | 0.021015 | -0.14519 | 123.0167 | 122.9486 | 123.1229 | 66.7296 | -123.2111 | 122.9268 | 123.1091 | 122.9429 | 66.724 | -123.448
1638.7969 | 123.262 | -66.7236 | 56.282 | -0.0029761 | -0.02082 | 0.00024794 | 0.053722 | -0.0063052 | 0.06293 | 0.00015261 | -0.0021983 | -0.00034193 | 0.05739 | 0.029874 | 0.057881 | -66.729 | -0.021486 | -66.746 | 56.2747 | 56.1929 | 56.3718 | -66.8604 | -66.7474 | -0.027113 | -66.7865 | 56.1848 | 56.3671 | 56.1826 | -67.1065 | -0.13678 | -0.007312 | -0.005323 | -0.022372 | 0.1144 | -0.089122 | 0.089741 | -0.38282 | -0.097233 | -0.023752 | -0.062836 | 0.31999 | 0.085103 | -0.099418 | 122.9984 | 122.9166 | 123.0954 | 66.7021 | -123.1425 | 122.9084 | 123.0908 | 122.9063 | 66.6965 | -123.3885
1639.7969 | 123.262 | -66.7099 | 56.2958 | -0.0029761 | -0.020607 | 0.00067514 | 0.054149 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.030515 | 0.057667 | -66.7244 | -0.021486 | -66.746 | 56.2793 | 56.1838 | 56.3764 | -66.8696 | -66.7474 | -0.031692 | -66.7773 | 56.1848 | 56.358 | 56.2147 | -67.111 | -0.15967 | -0.016467 | -0.014477 | -0.036105 | 0.12356 | -0.11201 | 0.080586 | -0.40113 | -0.11097 | -0.037485 | -0.067411 | 0.33372 | 0.062213 | -0.081101 | 122.9892 | 122.8937 | 123.0863 | 66.6884 | -123.1653 | 122.8947 | 123.0679 | 122.9246 | 66.6782 | -123.4068
1640.7969 | 123.2803 | -66.7145 | 56.2683 | -0.0029761 | -0.020393 | 0.00046154 | 0.053508 | -0.0060916 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.05739 | 0.029874 | 0.057667 | -66.7198 | -0.021486 | -66.7506 | 56.2793 | 56.1929 | 56.3718 | -66.865 | -66.7428 | -0.027113 | -66.7865 | 56.1802 | 56.3626 | 56.1964 | -67.1065 | -0.15051 | 0.010998 | -0.005321 | -0.036105 | 0.1144 | -0.07539 | 0.10347 | -0.39198 | -0.08808 | -0.028328 | -0.071991 | 0.31999 | 0.094257 | -0.07195 | 122.9938 | 122.9074 | 123.0863 | 66.693 | -123.1333 | 122.8947 | 123.077 | 122.9108 | 66.6874 | -123.3748
1641.7969 | 123.2025 | -66.7465 | 56.3232 | -0.0029761 | -0.020607 | 0.00067514 | 0.053722 | -0.0060916 | 0.062503 | -0.015108 | -0.0024119 | -0.00076913 | 0.05739 | 0.030087 | 0.057881 | -66.7198 | -0.021486 | -66.7414 | 56.2793 | 56.1929 | 56.3764 | -66.8696 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3626 | 56.1918 | -67.1065 | -0.12305 | -0.043933 | 0.026722 | 0.005094 | 0.12814 | -0.13032 | 0.05312 | -0.35993 | -0.13843 | 0.003715 | -0.035369 | 0.32457 | 0.039326 | -0.13146 | 123.0258 | 122.9394 | 123.1229 | 66.725 | -123.1928 | 122.9313 | 123.1091 | 122.9383 | 66.724 | -123.4297
1642.8594 | 123.1842 | -66.7465 | 56.337 | -0.0029761 | -0.02082 | 0.00067514 | 0.053508 | -0.0056642 | 0.062289 | 0.0077831 | -0.0021983 | -0.00076913 | 0.05739 | 0.030301 | 0.057881 | -66.729 | -0.012329 | -66.7506 | 56.2747 | 56.2021 | 56.3809 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3626 | 56.1735 | -67.111 | -0.12762 | -0.062244 | 0.017565 | -0.004062 | 0.12356 | -0.1349 | 0.043966 | -0.36451 | -0.15217 | 0.003715 | -0.035369 | 0.32914 | 0.025593 | -0.16351 | 123.0213 | 122.9486 | 123.1275 | 66.7342 | -123.2111 | 122.9313 | 123.1091 | 122.92 | 66.724 | -123.448
1643.7969 | 123.143 | -66.7786 | 56.3187 | -0.010607 | -0.021034 | 0.00067514 | 0.053295 | -0.0056642 | 0.062717 | -0.0074779 | -0.0026255 | -0.0011965 | 0.057176 | 0.030515 | 0.058094 | -66.7198 | -0.021486 | -66.746 | 56.2793 | 56.1838 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3671 | 56.1826 | -67.1019 | -0.091002 | -0.039356 | 0.058765 | 0.032559 | 0.12356 | -0.1349 | 0.053119 | -0.32331 | -0.13386 | 0.035758 | -0.003326 | 0.31999 | 0.048481 | -0.13604 | 123.0579 | 122.9623 | 123.1503 | 66.7571 | -123.1882 | 122.9634 | 123.1457 | 122.9612 | 66.756 | -123.4205
1644.875 | 123.1613 | -66.7419 | 56.3416 | 0.012286 | -0.02082 | 0.00046154 | 0.053508 | -0.0056642 | 0.062503 | 0.00015261 | -0.0026255 | -0.00098273 | 0.05739 | 0.030087 | 0.057667 | -66.7198 | -0.026065 | -66.7506 | 56.2839 | 56.2021 | 56.3809 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1848 | 56.3671 | 56.1964 | -67.111 | -0.12762 | -0.057666 | 0.022144 | -0.00864 | 0.11898 | -0.13947 | 0.039388 | -0.36909 | -0.15674 | -0.000863 | -0.039947 | 0.32914 | 0.025593 | -0.14519 | 123.0258 | 122.944 | 123.1229 | 66.7159 | -123.2111 | 122.9268 | 123.1091 | 122.9383 | 66.7148 | -123.4526
1645.7969 | 123.2391 | -66.7145 | 56.2775 | -0.0029761 | -0.020607 | 0.00046154 | 0.053722 | -0.0060916 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.05739 | 0.02966 | 0.057881 | -66.729 | -0.016908 | -66.746 | 56.2747 | 56.2021 | 56.3672 | -66.865 | -66.7428 | -0.031692 | -66.7773 | 56.1802 | 56.3671 | 56.178 | -67.111 | -0.15051 | -0.002735 | -0.014478 | -0.031527 | 0.11898 | -0.075387 | 0.089739 | -0.39656 | -0.097235 | -0.028328 | -0.062833 | 0.33372 | 0.08968 | -0.09942 | 122.9892 | 122.9166 | 123.0817 | 66.6976 | -123.1425 | 122.8947 | 123.0816 | 122.8925 | 66.6828 | -123.3885
1646.7969 | 123.2346 | -66.7053 | 56.282 | -0.010607 | -0.02082 | 0.00046154 | 0.053936 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057604 | 0.030942 | 0.057667 | -66.7335 | -0.021486 | -66.7506 | 56.2793 | 56.2021 | 56.3764 | -66.8741 | -66.7382 | -0.022535 | -66.7819 | 56.1802 | 56.3626 | 56.1826 | -67.1019 | -0.16882 | -0.002734 | -0.028212 | -0.045261 | 0.12356 | -0.079964 | 0.094319 | -0.39656 | -0.10181 | -0.032905 | -0.076568 | 0.31999 | 0.080525 | -0.099418 | 122.9846 | 122.9074 | 123.0817 | 66.6838 | -123.1562 | 122.8856 | 123.0679 | 122.8879 | 66.6828 | -123.3839
1647.7969 | 123.2666 | -66.6824 | 56.2775 | 0.0046549 | -0.020607 | 0.00067514 | 0.053295 | -0.0060916 | 0.062289 | 0.0077831 | -0.0024119 | -0.00034193 | 0.057176 | 0.030301 | 0.057667 | -66.729 | -0.016908 | -66.7414 | 56.2656 | 56.1929 | 56.3809 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1802 | 56.3626 | 56.1872 | -67.0973 | -0.18713 | -0.011892 | -0.046522 | -0.058993 | 0.12814 | -0.084545 | 0.10348 | -0.41487 | -0.097235 | -0.055793 | -0.099456 | 0.31541 | 0.085102 | -0.090262 | 122.948 | 122.8754 | 123.0634 | 66.6655 | -123.147 | 122.8627 | 123.045 | 122.8696 | 66.6553 | -123.3748
1648.8594 | 123.1888 | -66.7374 | 56.3461 | 0.012286 | -0.020393 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056963 | 0.030301 | 0.057881 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.2021 | 56.3672 | -66.8741 | -66.7474 | -0.022535 | -66.7865 | 56.1757 | 56.3671 | 56.1689 | -67.1065 | -0.13678 | -0.066821 | 0.00841 | -0.013217 | 0.12356 | -0.14405 | 0.021075 | -0.36909 | -0.17048 | -0.010019 | -0.049103 | 0.31999 | 0.021016 | -0.17724 | 123.0167 | 122.9394 | 123.1046 | 66.7205 | -123.2203 | 122.913 | 123.1045 | 122.9063 | 66.7148 | -123.4526
1649.7969 | 123.262 | -66.6962 | 56.3278 | 0.012286 | -0.021034 | 0.00088894 | 0.053722 | -0.0058778 | 0.062717 | -0.0074779 | -0.0026255 | -0.00098273 | 0.057176 | 0.030301 | 0.057667 | -66.729 | -0.021486 | -66.7506 | 56.2747 | 56.1975 | 56.3764 | -66.865 | -66.7474 | -0.027113 | -66.7865 | 56.1802 | 56.3626 | 56.2009 | -67.111 | -0.16882 | -0.053089 | -0.032789 | -0.054416 | 0.1144 | -0.13032 | 0.048542 | -0.41487 | -0.14759 | -0.051218 | -0.090302 | 0.32457 | 0.034748 | -0.12688 | 122.9709 | 122.8937 | 123.0725 | 66.6747 | -123.1928 | 122.8764 | 123.0587 | 122.8971 | 66.6691 | -123.4389
1650.8594 | 123.2437 | -66.7053 | 56.2729 | -0.0029761 | -0.02082 | 0.00067514 | 0.054363 | -0.0063052 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057176 | 0.030087 | 0.057453 | -66.729 | -0.016908 | -66.746 | 56.2747 | 56.1838 | 56.3718 | -66.8696 | -66.7382 | -0.022535 | -66.7773 | 56.1757 | 56.3626 | 56.178 | -67.111 | -0.16424 | 0.001843 | -0.023634 | -0.040683 | 0.12356 | -0.089125 | 0.098896 | -0.40571 | -0.097235 | -0.032905 | -0.071989 | 0.33372 | 0.08968 | -0.094842 | 122.9801 | 122.8891 | 123.0771 | 66.6884 | -123.1425 | 122.881 | 123.0679 | 122.8834 | 66.6828 | -123.3839
1651.7969 | 123.2529 | -66.7053 | 56.2775 | 0.0046549 | -0.021034 | 0.00067514 | 0.053722 | -0.0063052 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.030301 | 0.058094 | -66.7244 | -0.012329 | -66.7552 | 56.2793 | 56.1883 | 56.3672 | -66.8604 | -66.7428 | -0.027113 | -66.7727 | 56.1802 | 56.3671 | 56.1872 | -67.1065 | -0.15509 | 0.001843 | -0.019055 | -0.049839 | 0.10525 | -0.089124 | 0.089739 | -0.40113 | -0.097235 | -0.037484 | -0.06741 | 0.33372 | 0.08968 | -0.090262 | 122.9846 | 122.8937 | 123.0725 | 66.693 | -123.1379 | 122.8856 | 123.0725 | 122.8925 | 66.6782 | -123.3839
1652.8594 | 123.175 | -66.7236 | 56.3141 | -0.010607 | -0.021034 | 0.00067514 | 0.053295 | -0.0058778 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057817 | 0.030301 | 0.057667 | -66.7244 | -0.016908 | -66.7597 | 56.2839 | 56.1975 | 56.3718 | -66.8696 | -66.7474 | -0.022535 | -66.7773 | 56.1802 | 56.3671 | 56.2101 | -67.1065 | -0.14593 | -0.0302 | -0.000744 | -0.036107 | 0.10983 | -0.11659 | 0.057697 | -0.38282 | -0.13386 | -0.023752 | -0.053678 | 0.32914 | 0.053059 | -0.10399 | 123.0075 | 122.9211 | 123.0954 | 66.7067 | -123.1837 | 122.9039 | 123.0908 | 122.9337 | 66.7011 | -123.4205
1653.7969 | 123.2437 | -66.7191 | 56.2729 | 0.012286 | -0.02082 | 0.00067514 | 0.053508 | -0.0058778 | 0.062717 | 0.00015261 | -0.0026255 | -0.0011965 | 0.05739 | 0.030515 | 0.057881 | -66.7381 | -0.021486 | -66.7506 | 56.2747 | 56.1746 | 56.3764 | -66.865 | -66.7474 | -0.031692 | -66.7819 | 56.1894 | 56.3626 | 56.2009 | -67.0973 | -0.14593 | 0.001843 | -0.019057 | -0.031528 | 0.1144 | -0.098283 | 0.10347 | -0.37824 | -0.0835 | -0.02833 | -0.062835 | 0.31541 | 0.08968 | -0.071949 | 122.9938 | 122.8937 | 123.0954 | 66.6976 | -123.1379 | 122.9084 | 123.0816 | 122.92 | 66.6874 | -123.3702
1654.7969 | 123.1888 | -66.7328 | 56.3278 | 0.0046549 | -0.021034 | 0.00067514 | 0.053508 | -0.0060916 | 0.062717 | 0.0077831 | -0.0024119 | -0.0011965 | 0.05739 | 0.030728 | 0.057453 | -66.7335 | -0.016908 | -66.7552 | 56.2839 | 56.1975 | 56.3764 | -66.8741 | -66.7474 | -0.022535 | -66.7865 | 56.1802 | 56.3717 | 56.2009 | -67.111 | -0.14136 | -0.043933 | -0.000746 | -0.022373 | 0.11898 | -0.13032 | 0.048542 | -0.37825 | -0.14759 | -0.014597 | -0.053681 | 0.32457 | 0.043905 | -0.12688 | 123.0167 | 122.9303 | 123.1091 | 66.7159 | -123.202 | 122.913 | 123.1045 | 122.9337 | 66.7103 | -123.4389
1655.8594 | 123.2574 | -66.7236 | 56.282 | -0.0029761 | -0.021248 | 0.00088894 | 0.053722 | -0.0060916 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.05739 | 0.030515 | 0.057881 | -66.729 | -0.021486 | -66.746 | 56.2747 | 56.1838 | 56.3764 | -66.8787 | -66.7336 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.2147 | -67.1065 | -0.15509 | -0.007312 | -0.005323 | -0.022372 | 0.13272 | -0.09828 | 0.094319 | -0.38282 | -0.097233 | -0.010016 | -0.058257 | 0.32457 | 0.089682 | -0.067368 | 122.9984 | 122.9074 | 123.1 | 66.7021 | -123.1608 | 122.9084 | 123.0954 | 122.9383 | 66.7011 | -123.3885
1656.7969 | 123.2574 | -66.7236 | 56.2958 | 0.0046549 | -0.02082 | 0.00046154 | 0.053722 | -0.0056642 | 0.062717 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057176 | 0.030301 | 0.057667 | -66.7198 | -0.026065 | -66.7414 | 56.2747 | 56.1975 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1757 | 56.3671 | 56.1826 | -67.1019 | -0.14593 | -0.021045 | 0.003834 | -0.017794 | 0.12814 | -0.098276 | 0.080586 | -0.37824 | -0.12012 | -0.019173 | -0.058257 | 0.31999 | 0.07137 | -0.11315 | 122.9984 | 122.9211 | 123.1 | 66.6976 | -123.1653 | 122.8993 | 123.0908 | 122.9063 | 66.6965 | -123.3977
1657.8594 | 123.143 | -66.774 | 56.3553 | -0.010607 | -0.021034 | 0.00024794 | 0.053722 | -0.0063052 | 0.06293 | 0.00015261 | -0.0030529 | -0.00076913 | 0.057176 | 0.030515 | 0.057881 | -66.729 | -0.016908 | -66.7552 | 56.2839 | 56.1929 | 56.3809 | -66.865 | -66.752 | -0.022535 | -66.7773 | 56.1757 | 56.3671 | 56.2101 | -67.1019 | -0.091 | -0.071399 | 0.045031 | 0.018826 | 0.10983 | -0.16237 | 0.025655 | -0.32789 | -0.17963 | 0.022024 | -0.003324 | 0.32457 | 0.01186 | -0.14519 | 123.0579 | 122.9669 | 123.1549 | 66.7571 | -123.2203 | 122.9496 | 123.1411 | 122.9841 | 66.7515 | -123.4572
1658.7969 | 123.2941 | -66.7099 | 56.3049 | -0.0029761 | -0.020607 | 0.00067514 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.05739 | 0.030942 | 0.057881 | -66.729 | -0.016908 | -66.7552 | 56.2793 | 56.1883 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7865 | 56.1757 | 56.3763 | 56.2009 | -67.111 | -0.15967 | -0.025623 | -0.019056 | -0.045261 | 0.11441 | -0.11659 | 0.066852 | -0.40113 | -0.12928 | -0.032906 | -0.076569 | 0.32457 | 0.071371 | -0.10399 | 122.9892 | 122.8982 | 123.0817 | 66.693 | -123.1745 | 122.8856 | 123.0862 | 122.9108 | 66.6874 | -123.416
1659.8594 | 123.2758 | -66.687 | 56.3049 | 0.0046549 | -0.021248 | 0.00046154 | 0.053936 | -0.0058778 | 0.062289 | 0.00015261 | -0.0021983 | -0.0014101 | 0.05739 | 0.030942 | 0.057881 | -66.729 | -0.021486 | -66.7597 | 56.2793 | 56.1792 | 56.3764 | -66.8741 | -66.7474 | -0.022535 | -66.7865 | 56.1802 | 56.3717 | 56.2055 | -67.1065 | -0.18713 | -0.025623 | -0.041944 | -0.072728 | 0.11441 | -0.12575 | 0.07143 | -0.41944 | -0.1247 | -0.060373 | -0.099457 | 0.31999 | 0.066793 | -0.099414 | 122.9663 | 122.8662 | 123.0634 | 66.6655 | -123.1791 | 122.8672 | 123.0587 | 122.8925 | 66.6645 | -123.4114
1660.7969 | 123.2895 | -66.7053 | 56.3004 | -0.010607 | -0.021461 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057176 | 0.030515 | 0.057667 | -66.7244 | -0.035222 | -66.7597 | 56.2793 | 56.1975 | 56.3718 | -66.8787 | -66.7382 | -0.027113 | -66.7819 | 56.1757 | 56.3671 | 56.1918 | -67.111 | -0.1734 | -0.021045 | -0.019055 | -0.054418 | 0.11898 | -0.10285 | 0.07143 | -0.40571 | -0.1247 | -0.032905 | -0.076568 | 0.32914 | 0.066792 | -0.10857 | 122.9846 | 122.9028 | 123.0771 | 66.6701 | -123.1791 | 122.881 | 123.0725 | 122.8971 | 66.6782 | -123.4114
1661.7969 | 123.2254 | -66.7053 | 56.3095 | -0.0029761 | -0.021248 | 0.00024794 | 0.053722 | -0.0058778 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057604 | 0.030301 | 0.057881 | -66.7335 | -0.016908 | -66.7597 | 56.2702 | 56.1975 | 56.3764 | -66.8513 | -66.7428 | -0.022535 | -66.7865 | 56.1848 | 56.3717 | 56.178 | -67.1019 | -0.14593 | -0.039357 | -0.028212 | -0.054418 | 0.091511 | -0.11201 | 0.066853 | -0.39656 | -0.1247 | -0.037484 | -0.081147 | 0.31541 | 0.062216 | -0.13146 | 122.9755 | 122.9028 | 123.0817 | 66.6884 | -123.1608 | 122.8901 | 123.077 | 122.8834 | 66.6828 | -123.4114
1662.8594 | 123.1522 | -66.7648 | 56.3232 | -0.0029761 | -0.021034 | 0.00067514 | 0.053508 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057604 | 0.030515 | 0.057667 | -66.7198 | -0.016908 | -66.746 | 56.2839 | 56.1929 | 56.3718 | -66.8787 | -66.7382 | -0.022535 | -66.7819 | 56.1757 | 56.3717 | 56.2009 | -67.111 | -0.11389 | -0.039355 | 0.045033 | 0.018827 | 0.13272 | -0.13032 | 0.048542 | -0.3462 | -0.14759 | 0.026605 | -0.017058 | 0.32914 | 0.048483 | -0.1223 | 123.0487 | 122.9578 | 123.1366 | 66.7479 | -123.202 | 122.9405 | 123.1366 | 122.9658 | 66.7423 | -123.4343
1663.7969 | 123.23 | -66.7328 | 56.3141 | 0.0046549 | -0.021248 | 0.00088894 | 0.053722 | -0.0063052 | 0.062503 | 0.0077831 | -0.0024119 | -0.00076913 | 0.05739 | 0.030301 | 0.057667 | -66.729 | -0.016908 | -66.7506 | 56.2747 | 56.1838 | 56.3718 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1802 | 56.3717 | 56.1918 | -67.1156 | -0.1322 | -0.039356 | 0.003832 | -0.017795 | 0.1144 | -0.13032 | 0.057697 | -0.38283 | -0.13386 | -0.010018 | -0.049102 | 0.33372 | 0.057638 | -0.1223 | 123.0075 | 122.9166 | 123.1046 | 66.7159 | -123.1791 | 122.913 | 123.1045 | 122.9246 | 66.7103 | -123.4297
1664.7969 | 123.1705 | -66.7374 | 56.4056 | -0.0029761 | -0.021034 | 0.00024794 | 0.053722 | -0.0060916 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.05739 | 0.030301 | 0.057667 | -66.7244 | -0.016908 | -66.7597 | 56.2793 | 56.2021 | 56.3764 | -66.8787 | -66.7428 | -0.031692 | -66.7773 | 56.1802 | 56.3626 | 56.2193 | -67.1065 | -0.14136 | -0.12633 | 0.012989 | -0.022374 | 0.11898 | -0.20356 | -0.029278 | -0.36909 | -0.22541 | -0.00544 | -0.039945 | 0.32914 | -0.043072 | -0.18639 | 123.0167 | 122.9394 | 123.1137 | 66.7205 | -123.2844 | 122.9176 | 123.0999 | 122.9566 | 66.7057 | -123.5121
1665.8594 | 123.1659 | -66.7465 | 56.2912 | -0.0029761 | -0.021034 | 0.00067514 | 0.053722 | -0.0058778 | 0.062717 | -0.0074779 | -0.0024119 | -0.00076913 | 0.057176 | 0.030515 | 0.057881 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.1883 | 56.3855 | -66.8741 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3626 | 56.1964 | -67.1019 | -0.12762 | -0.01189 | 0.017565 | -0.004062 | 0.12356 | -0.10286 | 0.09432 | -0.35536 | -0.11097 | 0.003715 | -0.035369 | 0.31999 | 0.071369 | -0.094838 | 123.0258 | 122.9349 | 123.132 | 66.7296 | -123.1653 | 122.9268 | 123.1091 | 122.9429 | 66.7194 | -123.3931
1666.7969 | 123.2941 | -66.7053 | 56.3004 | 0.0046549 | -0.02082 | 0.00067514 | 0.053508 | -0.0060916 | 0.062289 | 0.0077831 | -0.0026255 | -0.00076913 | 0.05739 | 0.030515 | 0.057667 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.1883 | 56.3809 | -66.8604 | -66.7428 | -0.027113 | -66.7819 | 56.1848 | 56.3626 | 56.1872 | -67.1065 | -0.15509 | -0.021045 | -0.023634 | -0.045261 | 0.10983 | -0.11201 | 0.080587 | -0.40113 | -0.11554 | -0.037484 | -0.076568 | 0.32457 | 0.062214 | -0.11315 | 122.9846 | 122.8937 | 123.0863 | 66.6884 | -123.1608 | 122.8901 | 123.0679 | 122.8925 | 66.6782 | -123.4068
1667.7969 | 123.2162 | -66.7099 | 56.3278 | 0.0046549 | -0.02082 | 0.00067514 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057604 | 0.030728 | 0.057667 | -66.729 | -0.012329 | -66.7597 | 56.2793 | 56.1746 | 56.3764 | -66.8696 | -66.7382 | -0.031692 | -66.7727 | 56.1894 | 56.3626 | 56.1872 | -67.0927 | -0.15967 | -0.048511 | -0.019056 | -0.04984 | 0.10983 | -0.15322 | 0.048542 | -0.38282 | -0.13843 | -0.028327 | -0.062832 | 0.31999 | 0.034748 | -0.14062 | 122.9892 | 122.8845 | 123.0863 | 66.6976 | -123.1974 | 122.8993 | 123.0725 | 122.8971 | 66.6782 | -123.4205
1668.7969 | 123.2803 | -66.7053 | 56.3324 | -0.0029761 | -0.02082 | 0.00046154 | 0.053722 | -0.0060916 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.057604 | 0.030728 | 0.057881 | -66.7381 | -0.021486 | -66.7597 | 56.2793 | 56.1929 | 56.3718 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.1802 | 56.3717 | 56.2009 | -67.1019 | -0.1734 | -0.053088 | -0.03279 | -0.054418 | 0.11898 | -0.13948 | 0.039387 | -0.39656 | -0.15217 | -0.042063 | -0.076568 | 0.31999 | 0.039328 | -0.13146 | 122.9846 | 122.8982 | 123.0771 | 66.6838 | -123.2111 | 122.8856 | 123.077 | 122.9063 | 66.6874 | -123.4343
1669.7969 | 123.2254 | -66.7145 | 56.3141 | 0.0046549 | -0.021248 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0024119 | -0.00055553 | 0.05739 | 0.030728 | 0.058094 | -66.7335 | -0.026065 | -66.7597 | 56.2747 | 56.2021 | 56.3718 | -66.8696 | -66.7474 | -0.036271 | -66.7819 | 56.1848 | 56.3717 | 56.178 | -67.1156 | -0.15509 | -0.039356 | -0.019056 | -0.045262 | 0.10983 | -0.11201 | 0.057697 | -0.40114 | -0.12928 | -0.032907 | -0.067412 | 0.33372 | 0.057638 | -0.13604 | 122.9892 | 122.9166 | 123.0863 | 66.6884 | -123.1837 | 122.8993 | 123.0862 | 122.8925 | 66.6782 | -123.4297
1670.7969 | 123.3261 | -66.6733 | 56.3187 | 0.0046549 | -0.021034 | 0.00088894 | 0.053722 | -0.0063052 | 0.06293 | 0.00015261 | -0.0026255 | -0.00055553 | 0.05739 | 0.030515 | 0.057667 | -66.7335 | -0.012329 | -66.7506 | 56.2793 | 56.1975 | 56.3809 | -66.865 | -66.7382 | -0.027113 | -66.7819 | 56.1802 | 56.3717 | 56.1826 | -67.1065 | -0.19171 | -0.039356 | -0.060255 | -0.077304 | 0.1144 | -0.12117 | 0.062276 | -0.43318 | -0.13843 | -0.064948 | -0.10861 | 0.32457 | 0.05306 | -0.13604 | 122.9526 | 122.8708 | 123.0542 | 66.6609 | -123.1837 | 122.8535 | 123.045 | 122.8559 | 66.6462 | -123.4251
1671.7969 | 123.23 | -66.7053 | 56.3187 | 0.0046549 | -0.021034 | 0.00046154 | 0.053722 | -0.0060916 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.057604 | 0.030728 | 0.057667 | -66.7335 | -0.021486 | -66.7597 | 56.2793 | 56.1975 | 56.3764 | -66.865 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.3626 | 56.2193 | -67.1156 | -0.15967 | -0.039356 | -0.028212 | -0.054418 | 0.10525 | -0.12117 | 0.057697 | -0.41029 | -0.13386 | -0.037484 | -0.076568 | 0.33372 | 0.043903 | -0.099411 | 122.9846 | 122.9028 | 123.0817 | 66.6838 | -123.1837 | 122.8901 | 123.0679 | 122.9246 | 66.6874 | -123.4343
1672.7969 | 123.2574 | -66.687 | 56.3187 | -0.0029761 | -0.021034 | 0.00024794 | 0.053722 | -0.0060916 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.057817 | 0.030942 | 0.057667 | -66.7244 | -0.021486 | -66.7597 | 56.2747 | 56.1929 | 56.3764 | -66.8696 | -66.7428 | -0.022535 | -66.7865 | 56.1802 | 56.3626 | 56.1918 | -67.1065 | -0.18255 | -0.043934 | -0.037365 | -0.072728 | 0.10983 | -0.12574 | 0.057697 | -0.41944 | -0.13843 | -0.055794 | -0.099457 | 0.31999 | 0.043903 | -0.12688 | 122.9617 | 122.8799 | 123.0634 | 66.6655 | -123.1882 | 122.8672 | 123.0496 | 122.8788 | 66.6645 | -123.4251
1673.8594 | 123.1888 | -66.7694 | 56.3232 | 0.0046549 | -0.021461 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.05739 | 0.030515 | 0.057881 | -66.729 | -0.021486 | -66.7552 | 56.2747 | 56.1975 | 56.3764 | -66.8696 | -66.7474 | -0.022535 | -66.7819 | 56.1711 | 56.3671 | 56.1826 | -67.111 | -0.10016 | -0.048511 | 0.040453 | 0.014248 | 0.11441 | -0.12574 | 0.05312 | -0.34163 | -0.15217 | 0.022024 | -0.012481 | 0.32914 | 0.043904 | -0.14062 | 123.0441 | 122.9669 | 123.1458 | 66.7479 | -123.1928 | 122.9405 | 123.1366 | 122.952 | 66.7469 | -123.4343
1674.7969 | 123.2483 | -66.7191 | 56.3324 | -0.0029761 | -0.021461 | 0.00046154 | 0.053295 | -0.0060916 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.05739 | 0.030515 | 0.057667 | -66.729 | -0.026065 | -66.7506 | 56.2839 | 56.1975 | 56.3809 | -66.8375 | -66.7428 | -0.027113 | -66.7865 | 56.1894 | 56.358 | 56.1918 | -67.1065 | -0.11846 | -0.04851 | -0.009901 | -0.031528 | 0.086931 | -0.1349 | 0.048544 | -0.3874 | -0.14301 | -0.023751 | -0.067414 | 0.31999 | 0.025592 | -0.14061 | 123.0029 | 122.9166 | 123.1 | 66.693 | -123.1699 | 122.9084 | 123.077 | 122.9108 | 66.6919 | -123.4389
1675.7969 | 123.2666 | -66.7191 | 56.3141 | 0.0046549 | -0.021034 | 0.00024794 | 0.053722 | -0.0063052 | 0.06293 | 0.0077831 | -0.0024119 | -0.00034193 | 0.057604 | 0.030728 | 0.057667 | -66.7244 | -0.021486 | -66.7643 | 56.2747 | 56.2067 | 56.3672 | -66.865 | -66.7474 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.2055 | -67.111 | -0.14593 | -0.039356 | -0.005322 | -0.045263 | 0.10067 | -0.10743 | 0.053118 | -0.39198 | -0.12928 | -0.02833 | -0.062835 | 0.32914 | 0.057638 | -0.10857 | 122.9938 | 122.9257 | 123.0863 | 66.6976 | -123.1791 | 122.9039 | 123.0908 | 122.9246 | 66.6965 | -123.4251
1676.8594 | 123.1705 | -66.7419 | 56.3232 | 0.0046549 | -0.02082 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | -0.0074779 | -0.0026255 | -0.00055553 | 0.057604 | 0.030515 | 0.057453 | -66.7244 | -0.016908 | -66.746 | 56.2747 | 56.2021 | 56.3764 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1848 | 56.3763 | 56.2101 | -67.1065 | -0.12762 | -0.048511 | 0.017566 | -0.004062 | 0.12356 | -0.12116 | 0.05312 | -0.36451 | -0.13843 | 0.003716 | -0.039947 | 0.32457 | 0.053061 | -0.11315 | 123.0167 | 122.944 | 123.1183 | 66.725 | -123.1928 | 122.9268 | 123.1182 | 122.952 | 66.7148 | -123.4297
1677.7969 | 123.2574 | -66.7053 | 56.3049 | -0.0029761 | -0.021248 | 0.00024794 | 0.054149 | -0.0065188 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.05739 | 0.030728 | 0.057881 | -66.7335 | -0.021486 | -66.7552 | 56.2747 | 56.1929 | 56.3764 | -66.8696 | -66.7382 | -0.022535 | -66.7819 | 56.1757 | 56.3763 | 56.1964 | -67.1065 | -0.16424 | -0.030201 | -0.028212 | -0.049839 | 0.11441 | -0.11201 | 0.07143 | -0.40113 | -0.12928 | -0.032905 | -0.076568 | 0.32457 | 0.071371 | -0.10857 | 122.9801 | 122.8982 | 123.0817 | 66.6838 | -123.1745 | 122.881 | 123.0816 | 122.9017 | 66.6828 | -123.4114
1678.7969 | 123.2712 | -66.7145 | 56.3232 | 0.0046549 | -0.021461 | 0.00046154 | 0.053508 | -0.0060916 | 0.062289 | 0.0077831 | -0.0028393 | -0.00076913 | 0.05739 | 0.030942 | 0.05724 | -66.729 | -0.016908 | -66.7643 | 56.2793 | 56.1929 | 56.3809 | -66.8696 | -66.7474 | -0.022535 | -66.7773 | 56.1802 | 56.3763 | 56.2009 | -67.1065 | -0.15509 | -0.043933 | -0.014478 | -0.04984 | 0.10525 | -0.13032 | 0.057699 | -0.39198 | -0.14301 | -0.032907 | -0.062833 | 0.32914 | 0.053061 | -0.1223 | 122.9938 | 122.9074 | 123.0954 | 66.6976 | -123.1928 | 122.8947 | 123.0908 | 122.9154 | 66.6919 | -123.4297
1679.7969 | 123.2071 | -66.6962 | 56.3004 | -0.0029761 | -0.021248 | 0.00024794 | 0.053936 | -0.0063052 | 0.062717 | 0.015414 | -0.0028393 | -0.00076913 | 0.057176 | 0.030515 | 0.057667 | -66.7198 | -0.021486 | -66.7552 | 56.2839 | 56.2021 | 56.3809 | -66.8604 | -66.7428 | -0.027113 | -66.7865 | 56.1848 | 56.3626 | 56.1964 | -67.1065 | -0.16424 | -0.016467 | -0.023632 | -0.058994 | 0.10525 | -0.098275 | 0.080587 | -0.41029 | -0.11554 | -0.046639 | -0.090302 | 0.31999 | 0.062214 | -0.10399 | 122.9801 | 122.8982 | 123.0771 | 66.6747 | -123.1608 | 122.881 | 123.0587 | 122.8925 | 66.6691 | -123.4068
1680.7969 | 123.2483 | -66.6641 | 56.3095 | 0.0046549 | -0.021675 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057176 | 0.030942 | 0.057453 | -66.7335 | -0.021486 | -66.7643 | 56.2747 | 56.1929 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7727 | 56.1757 | 56.3626 | 56.1918 | -67.0973 | -0.20544 | -0.034778 | -0.06941 | -0.10019 | 0.10525 | -0.11659 | 0.066853 | -0.43318 | -0.13386 | -0.078682 | -0.10861 | 0.32457 | 0.053059 | -0.11773 | 122.9389 | 122.857 | 123.0405 | 66.6426 | -123.1791 | 122.8398 | 123.0267 | 122.8559 | 66.637 | -123.4068
1681.8594 | 123.2758 | -66.7328 | 56.2958 | -0.010607 | -0.02082 | 0.00067514 | 0.053508 | -0.0060916 | 0.062289 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057176 | 0.030728 | 0.057453 | -66.7335 | -0.026065 | -66.7689 | 56.2793 | 56.2021 | 56.3718 | -66.8696 | -66.7428 | -0.022535 | -66.7865 | 56.1802 | 56.3717 | 56.2147 | -67.1065 | -0.13678 | -0.016467 | -0.000746 | -0.036108 | 0.10067 | -0.093697 | 0.076008 | -0.37367 | -0.11554 | -0.010018 | -0.053681 | 0.31999 | 0.075949 | -0.081101 | 123.0121 | 122.9349 | 123.1046 | 66.7067 | -123.1653 | 122.913 | 123.1045 | 122.9475 | 66.7103 | -123.4022
1682.7969 | 123.1979 | -66.7145 | 56.3599 | 0.012286 | -0.021461 | 0.00067514 | 0.053722 | -0.0060916 | 0.062717 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057176 | 0.030942 | 0.057667 | -66.7244 | -0.026065 | -66.7552 | 56.2793 | 56.2067 | 56.3809 | -66.8696 | -66.7382 | -0.027113 | -66.7865 | 56.1802 | 56.3671 | 56.1918 | -67.111 | -0.15509 | -0.080554 | -0.009899 | -0.040683 | 0.11441 | -0.1532 | 0.021078 | -0.39656 | -0.17963 | -0.023749 | -0.071991 | 0.32457 | 0.007283 | -0.16808 | 122.9938 | 122.9211 | 123.0954 | 66.6884 | -123.2294 | 122.8947 | 123.0816 | 122.9063 | 66.6874 | -123.4709
1683.7969 | 123.3032 | -66.6962 | 56.3278 | 0.0046549 | -0.021248 | 0.00046154 | 0.053722 | -0.0060916 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.05739 | 0.030728 | 0.057453 | -66.7198 | -0.021486 | -66.7597 | 56.2747 | 56.1838 | 56.3764 | -66.865 | -66.7428 | -0.017956 | -66.7865 | 56.1757 | 56.3671 | 56.2009 | -67.111 | -0.16882 | -0.053089 | -0.023632 | -0.063573 | 0.10525 | -0.14406 | 0.048542 | -0.41487 | -0.15217 | -0.046639 | -0.090302 | 0.32457 | 0.039326 | -0.12688 | 122.9709 | 122.8799 | 123.0725 | 66.6747 | -123.1928 | 122.8718 | 123.0633 | 122.8971 | 66.6782 | -123.4389
1684.8594 | 123.2712 | -66.7053 | 56.3095 | 0.0046549 | -0.021248 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.057176 | 0.030728 | 0.058094 | -66.7244 | -0.021486 | -66.7552 | 56.2793 | 56.2021 | 56.3809 | -66.8696 | -66.7428 | -0.027113 | -66.7773 | 56.1848 | 56.3717 | 56.1918 | -67.111 | -0.16424 | -0.0302 | -0.019055 | -0.049839 | 0.11441 | -0.10743 | 0.071432 | -0.40571 | -0.1247 | -0.037484 | -0.071989 | 0.33372 | 0.062216 | -0.11773 | 122.9846 | 122.9074 | 123.0863 | 66.6838 | -123.1791 | 122.8901 | 123.077 | 122.8971 | 66.6782 | -123.4205
1685.7969 | 123.2574 | -66.7007 | 56.2958 | -0.0029761 | -0.021461 | 0.00046154 | 0.053936 | -0.0063052 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.057176 | 0.030728 | 0.057667 | -66.7244 | -0.021486 | -66.7552 | 56.2702 | 56.1975 | 56.3809 | -66.8604 | -66.7382 | -0.027113 | -66.7865 | 56.1848 | 56.3671 | 56.2009 | -67.111 | -0.15966 | -0.025624 | -0.023632 | -0.054416 | 0.10525 | -0.098276 | 0.085165 | -0.41029 | -0.11097 | -0.037482 | -0.085724 | 0.32457 | 0.07137 | -0.094837 | 122.9709 | 122.8982 | 123.0817 | 66.6793 | -123.1562 | 122.8856 | 123.0679 | 122.9017 | 66.6736 | -123.4068
1686.7969 | 123.1796 | -66.7419 | 56.3553 | -0.0029761 | -0.021034 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.0077831 | -0.0026255 | -0.00055553 | 0.05739 | 0.030942 | 0.057881 | -66.729 | -0.007751 | -66.7506 | 56.2793 | 56.2021 | 56.3764 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.1757 | 56.3717 | 56.178 | -67.111 | -0.1322 | -0.075977 | 0.012987 | -0.00864 | 0.12356 | -0.15321 | 0.021076 | -0.36909 | -0.17963 | -0.000863 | -0.039947 | 0.32914 | 0.016439 | -0.17724 | 123.0213 | 122.944 | 123.1183 | 66.7342 | -123.2294 | 122.9176 | 123.1137 | 122.92 | 66.7194 | -123.4663
1687.8594 | 123.2758 | -66.7282 | 56.2683 | 0.0046549 | -0.021675 | 0.00067514 | 0.053722 | -0.0056642 | 0.062503 | 0.0077831 | -0.0024119 | -0.00055553 | 0.057604 | 0.030942 | 0.05724 | -66.7335 | -0.021486 | -66.7552 | 56.2747 | 56.1838 | 56.3809 | -66.865 | -66.7428 | -0.022535 | -66.791 | 56.1757 | 56.3671 | 56.1964 | -67.1065 | -0.13678 | 0.00642 | -0.005324 | -0.026951 | 0.10983 | -0.084548 | 0.11263 | -0.37825 | -0.092658 | -0.014596 | -0.062837 | 0.31541 | 0.098835 | -0.07195 | 123.0029 | 122.912 | 123.1092 | 66.7067 | -123.1333 | 122.9039 | 123.0954 | 122.9246 | 66.7057 | -123.3748
1688.7969 | 123.1659 | -66.7191 | 56.3461 | -0.010607 | -0.021248 | 0.00088894 | 0.053722 | -0.0063052 | 0.063144 | 0.00015261 | -0.0026255 | -0.00055553 | 0.05739 | 0.030728 | 0.057453 | -66.729 | -0.021486 | -66.7597 | 56.2839 | 56.1975 | 56.3764 | -66.8787 | -66.752 | -0.022535 | -66.7773 | 56.1848 | 56.3671 | 56.2147 | -67.111 | -0.15967 | -0.062243 | -0.009901 | -0.040685 | 0.11898 | -0.14863 | 0.030232 | -0.39198 | -0.16132 | -0.032908 | -0.058256 | 0.33372 | 0.021016 | -0.13146 | 123.0029 | 122.9166 | 123.0954 | 66.6976 | -123.2249 | 122.9039 | 123.0862 | 122.9337 | 66.6965 | -123.4572
1689.7969 | 123.262 | -66.6916 | 56.3507 | 0.012286 | -0.021461 | 0.00067514 | 0.053295 | -0.0058778 | 0.062289 | 0.015414 | -0.0028393 | -0.00055553 | 0.056963 | 0.030728 | 0.057881 | -66.7244 | -0.021486 | -66.7643 | 56.2747 | 56.1975 | 56.3764 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.1802 | 56.3626 | 56.2055 | -67.1065 | -0.18256 | -0.075977 | -0.032788 | -0.072729 | 0.10983 | -0.15321 | 0.025654 | -0.41487 | -0.17048 | -0.051217 | -0.090301 | 0.32457 | 0.01186 | -0.14519 | 122.9663 | 122.8891 | 123.068 | 66.6701 | -123.2249 | 122.8718 | 123.0542 | 122.8971 | 66.6691 | -123.4572
1690.7969 | 123.1796 | -66.7374 | 56.3644 | 0.0046549 | -0.021248 | 0.00024794 | 0.053295 | -0.0060916 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056963 | 0.031156 | 0.057881 | -66.7244 | -0.016908 | -66.7552 | 56.2793 | 56.1975 | 56.3764 | -66.8604 | -66.7428 | -0.017956 | -66.7865 | 56.1802 | 56.3717 | 56.2101 | -67.111 | -0.12304 | -0.085132 | 0.012989 | -0.017795 | 0.10525 | -0.16694 | 0.011921 | -0.37367 | -0.18421 | -0.00544 | -0.049103 | 0.32457 | 0.007284 | -0.15434 | 123.0167 | 122.9349 | 123.1137 | 66.7205 | -123.2248 | 122.9176 | 123.1091 | 122.9475 | 66.7194 | -123.4755
1691.8594 | 123.3444 | -66.7374 | 56.2912 | -0.0029761 | -0.021461 | 0.00046154 | 0.053295 | -0.0060916 | 0.062717 | -0.015108 | -0.0026255 | -0.00055553 | 0.05739 | 0.031156 | 0.057667 | -66.7335 | -0.021486 | -66.7597 | 56.2793 | 56.2021 | 56.3718 | -66.8513 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3717 | 56.1964 | -67.1019 | -0.11389 | -0.01189 | 0.003832 | -0.022374 | 0.091511 | -0.08912 | 0.080585 | -0.36451 | -0.10181 | -0.010019 | -0.044524 | 0.31999 | 0.080526 | -0.094838 | 123.0167 | 122.9394 | 123.1091 | 66.7159 | -123.1424 | 122.9268 | 123.1091 | 122.9337 | 66.7194 | -123.3931
1692.7969 | 123.1796 | -66.7374 | 56.3324 | 0.012286 | -0.021461 | 0.00024794 | 0.053081 | -0.0058778 | 0.062289 | 0.0077831 | -0.0024119 | -0.00076913 | 0.05739 | 0.031369 | 0.057667 | -66.7244 | -0.016908 | -66.7597 | 56.2793 | 56.1975 | 56.3809 | -66.8696 | -66.7428 | -0.017956 | -66.791 | 56.1802 | 56.3763 | 56.1964 | -67.1019 | -0.1322 | -0.053088 | 0.012989 | -0.022374 | 0.10983 | -0.1349 | 0.048544 | -0.36451 | -0.15217 | -0.00544 | -0.053681 | 0.31083 | 0.043906 | -0.13604 | 123.0167 | 122.9349 | 123.1183 | 66.7205 | -123.202 | 122.9176 | 123.1137 | 122.9337 | 66.7194 | -123.4343
1693.7969 | 123.2803 | -66.7145 | 56.3004 | 0.012286 | -0.021248 | 0.00024794 | 0.053295 | -0.0058778 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057176 | 0.030942 | 0.057453 | -66.7244 | -0.026065 | -66.7552 | 56.2747 | 56.2021 | 56.3809 | -66.8513 | -66.7428 | -0.017956 | -66.7865 | 56.1802 | 56.3671 | 56.2009 | -67.1156 | -0.13677 | -0.025623 | -0.009899 | -0.040683 | 0.09609 | -0.098275 | 0.080587 | -0.40114 | -0.12012 | -0.028328 | -0.071991 | 0.32914 | 0.066792 | -0.099415 | 122.9892 | 122.9166 | 123.0954 | 66.6884 | -123.1516 | 122.8947 | 123.0816 | 122.9154 | 66.6965 | -123.416
1694.7969 | 123.2025 | -66.7282 | 56.3232 | 0.0046549 | -0.021248 | 0.00046154 | 0.053722 | -0.0060916 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.057176 | 0.031156 | 0.057453 | -66.7244 | -0.016908 | -66.7552 | 56.2747 | 56.2021 | 56.3764 | -66.8787 | -66.7382 | -0.022535 | -66.7819 | 56.1802 | 56.3717 | 56.1918 | -67.111 | -0.15051 | -0.048511 | 0.003833 | -0.026951 | 0.12356 | -0.12116 | 0.05312 | -0.38282 | -0.14301 | -0.010017 | -0.05368 | 0.32914 | 0.048483 | -0.13146 | 123.0029 | 122.9303 | 123.1046 | 66.7113 | -123.202 | 122.9084 | 123.0999 | 122.92 | 66.7057 | -123.4343
1695.7969 | 123.1522 | -66.7191 | 56.3416 | -0.0029761 | -0.021248 | 0.00088894 | 0.053508 | -0.0060916 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057604 | 0.030942 | 0.057453 | -66.7244 | -0.016908 | -66.7506 | 56.2747 | 56.2021 | 56.3809 | -66.8787 | -66.7474 | -0.027113 | -66.7865 | 56.1802 | 56.3717 | 56.2147 | -67.111 | -0.15967 | -0.066822 | -0.005322 | -0.031528 | 0.12814 | -0.13947 | 0.039388 | -0.39198 | -0.16132 | -0.02833 | -0.067414 | 0.32457 | 0.030172 | -0.12688 | 122.9938 | 122.9211 | 123.1 | 66.7021 | -123.2203 | 122.8993 | 123.0908 | 122.9337 | 66.6919 | -123.4526
1696.7969 | 123.2025 | -66.7465 | 56.337 | -0.0029761 | -0.021461 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | -0.0074779 | -0.0026255 | -0.00098273 | 0.05739 | 0.030942 | 0.057881 | -66.729 | -0.016908 | -66.7552 | 56.2839 | 56.2021 | 56.3855 | -66.8741 | -66.7428 | -0.027113 | -66.7819 | 56.1894 | 56.3717 | 56.1964 | -67.111 | -0.12762 | -0.053088 | 0.017565 | -0.00864 | 0.11898 | -0.1349 | 0.048544 | -0.36451 | -0.14759 | 0.003715 | -0.035369 | 0.32914 | 0.03475 | -0.14061 | 123.0304 | 122.9486 | 123.132 | 66.7296 | -123.2111 | 122.9359 | 123.1182 | 122.9429 | 66.7194 | -123.448
1697.8594 | 123.2208 | -66.7145 | 56.3095 | -0.010607 | -0.021034 | 0.00046154 | 0.053722 | -0.0058778 | 0.062289 | -0.0074779 | -0.0026255 | -0.00098273 | 0.057604 | 0.031369 | 0.057667 | -66.729 | -0.021486 | -66.7506 | 56.2747 | 56.2067 | 56.3809 | -66.8604 | -66.7382 | -0.022535 | -66.7819 | 56.1757 | 56.3671 | 56.1964 | -67.1065 | -0.14593 | -0.034778 | -0.014478 | -0.036105 | 0.10983 | -0.10285 | 0.071432 | -0.39198 | -0.13386 | -0.023749 | -0.067412 | 0.32457 | 0.057637 | -0.11315 | 122.9892 | 122.9211 | 123.0954 | 66.693 | -123.1699 | 122.8901 | 123.0816 | 122.9108 | 66.6919 | -123.416
1698.7969 | 123.23 | -66.7465 | 56.3461 | 0.0046549 | -0.021675 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.057176 | 0.030942 | 0.057881 | -66.7244 | -0.021486 | -66.7506 | 56.2793 | 56.1929 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3626 | 56.1918 | -67.111 | -0.12305 | -0.066821 | 0.022144 | -0.004062 | 0.11898 | -0.15321 | 0.030232 | -0.36451 | -0.1659 | 0.003715 | -0.035369 | 0.32914 | 0.016438 | -0.15435 | 123.0258 | 122.9394 | 123.1229 | 66.725 | -123.2157 | 122.9268 | 123.1091 | 122.9383 | 66.7194 | -123.4572
1699.8594 | 123.349 | -66.6595 | 56.3461 | 0.012286 | -0.021248 | 0.00046154 | 0.053722 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00076913 | 0.05739 | 0.030942 | 0.057453 | -66.729 | -0.021486 | -66.746 | 56.2747 | 56.1975 | 56.3718 | -66.8604 | -66.7428 | -0.027113 | -66.7865 | 56.1802 | 56.3671 | 56.2009 | -67.111 | -0.20086 | -0.071399 | -0.06941 | -0.086459 | 0.1144 | -0.14863 | 0.025654 | -0.45149 | -0.1659 | -0.08326 | -0.12692 | 0.32457 | 0.021016 | -0.14519 | 122.9343 | 122.857 | 123.0313 | 66.6381 | -123.2065 | 122.8398 | 123.0267 | 122.8605 | 66.6324 | -123.4572
1700.7969 | 123.1659 | -66.7236 | 56.3461 | -0.0029761 | -0.021461 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.057176 | 0.030942 | 0.057881 | -66.729 | -0.012329 | -66.7552 | 56.2793 | 56.2067 | 56.3855 | -66.8787 | -66.7382 | -0.013377 | -66.7865 | 56.1848 | 56.3763 | 56.1964 | -67.111 | -0.15509 | -0.066821 | -0.005323 | -0.031528 | 0.12356 | -0.13947 | 0.039389 | -0.3874 | -0.16132 | -0.014594 | -0.062836 | 0.32457 | 0.030173 | -0.14977 | 123.0029 | 122.9303 | 123.1092 | 66.7113 | -123.2249 | 122.9084 | 123.0999 | 122.92 | 66.7103 | -123.4572
1701.7969 | 123.2025 | -66.7328 | 56.3736 | 0.0046549 | -0.021461 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0028393 | -0.00076913 | 0.057176 | 0.031156 | 0.057667 | -66.729 | -0.016908 | -66.7597 | 56.2793 | 56.1975 | 56.3809 | -66.8741 | -66.7474 | -0.022535 | -66.7819 | 56.1802 | 56.3671 | 56.2055 | -67.1065 | -0.14136 | -0.094287 | 0.003832 | -0.026952 | 0.11441 | -0.1761 | 0.007345 | -0.37367 | -0.19337 | -0.014597 | -0.049102 | 0.32457 | -0.00645 | -0.16808 | 123.0121 | 122.9303 | 123.1137 | 66.7159 | -123.2477 | 122.913 | 123.0999 | 122.9383 | 66.7103 | -123.4801
1702.7969 | 123.1888 | -66.7374 | 56.3187 | 0.0046549 | -0.021248 | 0.00067514 | 0.053722 | -0.0060916 | 0.062289 | -0.0074779 | -0.0026255 | -0.00034193 | 0.056963 | 0.031156 | 0.057881 | -66.7244 | -0.007751 | -66.7552 | 56.2885 | 56.2158 | 56.3764 | -66.8696 | -66.7474 | -0.017956 | -66.791 | 56.1848 | 56.3671 | 56.2147 | -67.1065 | -0.1322 | -0.030199 | 0.012989 | -0.017795 | 0.11441 | -0.10285 | 0.057697 | -0.36909 | -0.13386 | -0.010019 | -0.053681 | 0.31541 | 0.048481 | -0.10399 | 123.0258 | 122.9532 | 123.1137 | 66.7296 | -123.1882 | 122.9222 | 123.1045 | 122.952 | 66.7194 | -123.4251
1703.7969 | 123.1705 | -66.7328 | 56.3416 | -0.0029761 | -0.021461 | 0.00046154 | 0.053508 | -0.0060916 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057604 | 0.031156 | 0.057667 | -66.7244 | -0.021486 | -66.7552 | 56.293 | 56.2112 | 56.3855 | -66.8741 | -66.7382 | -0.022535 | -66.7819 | 56.1848 | 56.3626 | 56.2284 | -67.1065 | -0.14136 | -0.048509 | 0.008411 | -0.022373 | 0.11898 | -0.13032 | 0.043966 | -0.37367 | -0.15674 | -0.005439 | -0.049102 | 0.32457 | 0.021015 | -0.11314 | 123.0258 | 122.944 | 123.1183 | 66.7113 | -123.2157 | 122.9176 | 123.0954 | 122.9612 | 66.7103 | -123.448
1704.8594 | 123.1567 | -66.7374 | 56.337 | -0.0029761 | -0.021461 | 0.00046154 | 0.053295 | -0.0058778 | 0.062503 | 0.0077831 | -0.0026255 | -0.00034193 | 0.05739 | 0.031369 | 0.057667 | -66.7244 | -0.021486 | -66.7506 | 56.2839 | 56.2021 | 56.3809 | -66.8787 | -66.7474 | -0.022535 | -66.7819 | 56.1848 | 56.3671 | 56.2009 | -67.1019 | -0.14136 | -0.053088 | 0.012989 | -0.013217 | 0.12814 | -0.1349 | 0.043966 | -0.36451 | -0.15217 | -0.010019 | -0.044524 | 0.31999 | 0.030171 | -0.13604 | 123.0213 | 122.9394 | 123.1183 | 66.7159 | -123.2157 | 122.9222 | 123.1045 | 122.9383 | 66.7148 | -123.4389
1705.7969 | 123.1613 | -66.7374 | 56.3644 | -0.0029761 | -0.021675 | 0.00088894 | 0.053722 | -0.0060916 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.05739 | 0.031156 | 0.057881 | -66.7244 | -0.012329 | -66.7552 | 56.2702 | 56.1975 | 56.3809 | -66.8696 | -66.7382 | -0.022535 | -66.7865 | 56.1894 | 56.3671 | 56.2009 | -67.1065 | -0.1322 | -0.094289 | 0.012989 | -0.017795 | 0.11441 | -0.16694 | 0.0165 | -0.36909 | -0.17505 | -0.000861 | -0.049103 | 0.31999 | 0.002705 | -0.1635 | 123.0075 | 122.9349 | 123.1183 | 66.725 | -123.234 | 122.9268 | 123.1045 | 122.9383 | 66.7148 | -123.4709
1706.8594 | 123.2803 | -66.6916 | 56.3095 | -0.0029761 | -0.021461 | 0.00067514 | 0.053722 | -0.0060916 | 0.062503 | 0.015414 | -0.0028393 | -0.00055553 | 0.057176 | 0.030942 | 0.057667 | -66.729 | -0.016908 | -66.7552 | 56.2747 | 56.2067 | 56.3764 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1757 | 56.3717 | 56.2055 | -67.1065 | -0.17798 | -0.034778 | -0.037367 | -0.063572 | 0.11441 | -0.10285 | 0.066853 | -0.41487 | -0.13386 | -0.046638 | -0.090301 | 0.32457 | 0.062216 | -0.10399 | 122.9663 | 122.8982 | 123.068 | 66.6747 | -123.1791 | 122.8672 | 123.0633 | 122.8971 | 66.6645 | -123.416
1707.7969 | 123.1338 | -66.7374 | 56.3187 | 0.012286 | -0.021461 | 0.00024794 | 0.053295 | -0.0060916 | 0.062289 | 0.0077831 | -0.0028393 | -0.00055553 | 0.05739 | 0.031156 | 0.057667 | -66.7244 | -0.016908 | -66.7506 | 56.2885 | 56.1975 | 56.3809 | -66.8696 | -66.7382 | -0.022535 | -66.7865 | 56.1802 | 56.3671 | 56.2101 | -67.1156 | -0.1322 | -0.030199 | 0.012989 | -0.013217 | 0.11898 | -0.12117 | 0.062276 | -0.37825 | -0.13843 | -0.000861 | -0.049103 | 0.32914 | 0.048481 | -0.10857 | 123.0258 | 122.9349 | 123.1183 | 66.7205 | -123.1882 | 122.9176 | 123.1045 | 122.9475 | 66.7148 | -123.4343
1708.7969 | 123.1659 | -66.7557 | 56.3278 | -0.0029761 | -0.021675 | 0.00067514 | 0.053508 | -0.0063052 | 0.062717 | -0.015108 | -0.0026255 | -0.00076913 | 0.057176 | 0.030942 | 0.057667 | -66.7335 | -0.021486 | -66.7506 | 56.2793 | 56.2158 | 56.3855 | -66.8787 | -66.7428 | -0.022535 | -66.7819 | 56.1802 | 56.3671 | 56.2101 | -67.1065 | -0.12305 | -0.048511 | 0.022142 | 0.005093 | 0.12814 | -0.112 | 0.057699 | -0.35078 | -0.14759 | 0.01287 | -0.026214 | 0.32457 | 0.039326 | -0.11772 | 123.035 | 122.9715 | 123.1412 | 66.7342 | -123.2065 | 122.9359 | 123.1228 | 122.9658 | 66.7331 | -123.4343
1709.7969 | 123.1705 | -66.7419 | 56.3416 | 0.012286 | -0.021034 | 0.00067514 | 0.053508 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.031156 | 0.057667 | -66.729 | -0.021486 | -66.7552 | 56.2839 | 56.1975 | 56.3855 | -66.8787 | -66.7474 | -0.017956 | -66.7773 | 56.1894 | 56.3717 | 56.2101 | -67.1065 | -0.13678 | -0.057666 | 0.012987 | -0.013218 | 0.12356 | -0.14405 | 0.043966 | -0.36451 | -0.15216 | -0.005442 | -0.035368 | 0.32914 | 0.030172 | -0.13146 | 123.0258 | 122.9394 | 123.1275 | 66.7205 | -123.2203 | 122.9313 | 123.1137 | 122.952 | 66.724 | -123.448
1710.8594 | 123.2025 | -66.7328 | 56.3278 | 0.012286 | -0.021461 | 0.00088894 | 0.053508 | -0.0060916 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.030728 | 0.057026 | -66.7381 | -0.007751 | -66.7552 | 56.2747 | 56.2021 | 56.3809 | -66.8879 | -66.7474 | -0.017956 | -66.7819 | 56.1848 | 56.3671 | 56.2009 | -67.1156 | -0.15509 | -0.053089 | -0.005324 | -0.022373 | 0.13272 | -0.12574 | 0.053121 | -0.38283 | -0.14301 | -0.014597 | -0.049102 | 0.33372 | 0.039326 | -0.12688 | 123.0075 | 122.9349 | 123.1137 | 66.725 | -123.2157 | 122.9176 | 123.0999 | 122.9337 | 66.7148 | -123.4434
1711.7969 | 123.1979 | -66.7328 | 56.3324 | -0.0029761 | -0.021461 | 0.00046154 | 0.053081 | -0.0058778 | 0.062503 | 0.00015261 | -0.0026255 | -0.00098273 | 0.05739 | 0.031156 | 0.057453 | -66.7198 | -0.016908 | -66.7597 | 56.2839 | 56.1929 | 56.3764 | -66.8604 | -66.7474 | -0.027113 | -66.7819 | 56.1802 | 56.3717 | 56.2009 | -67.1019 | -0.12762 | -0.04851 | 0.012989 | -0.026952 | 0.10067 | -0.13948 | 0.043965 | -0.36909 | -0.15217 | -0.014597 | -0.049102 | 0.31999 | 0.039328 | -0.13146 | 123.0167 | 122.9257 | 123.1091 | 66.7159 | -123.1928 | 122.913 | 123.1045 | 122.9337 | 66.7057 | -123.4343
1712.8594 | 123.2346 | -66.7007 | 56.3141 | 0.0046549 | -0.021461 | 0.00024794 | 0.053508 | -0.0065188 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.056963 | 0.031156 | 0.057453 | -66.7244 | -0.021486 | -66.7552 | 56.2793 | 56.1975 | 56.3855 | -66.8696 | -66.7428 | -0.022535 | -66.7819 | 56.1802 | 56.358 | 56.2101 | -67.1156 | -0.16882 | -0.034778 | -0.023632 | -0.054416 | 0.11441 | -0.11659 | 0.071432 | -0.41487 | -0.13386 | -0.042061 | -0.081145 | 0.33372 | 0.043902 | -0.10399 | 122.9801 | 122.8982 | 123.0863 | 66.6793 | -123.1837 | 122.881 | 123.0587 | 122.9108 | 66.6782 | -123.4297
1713.7969 | 123.2117 | -66.7603 | 56.3461 | 0.0046549 | -0.021675 | 0.0011025 | 0.053508 | -0.0063052 | 0.062076 | -0.0074779 | -0.0026255 | -0.00076913 | 0.057176 | 0.031369 | 0.057453 | -66.7335 | -0.016908 | -66.7597 | 56.2839 | 56.1975 | 56.3855 | -66.8696 | -66.7474 | -0.022535 | -66.7819 | 56.1802 | 56.3763 | 56.2238 | -67.111 | -0.10931 | -0.062243 | 0.02672 | 0.000514 | 0.10983 | -0.14863 | 0.039389 | -0.35078 | -0.1659 | 0.012869 | -0.021636 | 0.32914 | 0.030173 | -0.1223 | 123.0441 | 122.9578 | 123.1458 | 66.7433 | -123.2157 | 122.9405 | 123.1366 | 122.9841 | 66.7377 | -123.4572
1714.8594 | 123.1934 | -66.7374 | 56.3324 | 0.0046549 | -0.021675 | 0.00046154 | 0.053722 | -0.0060916 | 0.062289 | -0.0074779 | -0.0026255 | -0.00076913 | 0.057176 | 0.030942 | 0.05724 | -66.7335 | -0.016908 | -66.7506 | 56.2839 | 56.1975 | 56.3764 | -66.8696 | -66.7474 | -0.027113 | -66.7819 | 56.1757 | 56.3717 | 56.2238 | -67.111 | -0.1322 | -0.04851 | 0.003832 | -0.013217 | 0.11898 | -0.1349 | 0.043965 | -0.37367 | -0.15674 | -0.010019 | -0.044524 | 0.32914 | 0.039328 | -0.10856 | 123.0213 | 122.9349 | 123.1137 | 66.7205 | -123.202 | 122.913 | 123.1091 | 122.9612 | 66.7103 | -123.4434
1715.7969 | 123.1934 | -66.7465 | 56.3416 | -0.010607 | -0.021248 | 0.00046154 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057176 | 0.031369 | 0.057881 | -66.729 | -0.021486 | -66.7506 | 56.2793 | 56.1975 | 56.3809 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.194 | 56.3717 | 56.2193 | -67.1202 | -0.12305 | -0.062244 | 0.017565 | -0.004062 | 0.11898 | -0.14405 | 0.039388 | -0.37367 | -0.14759 | 0.008294 | -0.035369 | 0.3383 | 0.030172 | -0.1223 | 123.0258 | 122.944 | 123.1275 | 66.725 | -123.2111 | 122.9405 | 123.1182 | 122.9658 | 66.7194 | -123.4617
1716.7969 | 123.1384 | -66.7648 | 56.3232 | -0.0029761 | -0.021675 | 0.00067514 | 0.053081 | -0.0058778 | 0.062503 | 0.00015261 | -0.0021983 | -0.00098273 | 0.05739 | 0.031156 | 0.057881 | -66.7244 | -0.016908 | -66.746 | 56.2839 | 56.2021 | 56.3855 | -66.8787 | -66.7474 | -0.031692 | -66.791 | 56.1848 | 56.3626 | 56.2009 | -67.1065 | -0.11389 | -0.039355 | 0.040455 | 0.018827 | 0.13272 | -0.12116 | 0.062277 | -0.34162 | -0.13843 | 0.017447 | -0.026215 | 0.31541 | 0.039326 | -0.1223 | 123.0487 | 122.9669 | 123.1504 | 66.7479 | -123.202 | 122.9496 | 123.1274 | 122.9658 | 66.7331 | -123.4297
1717.8594 | 123.3032 | -66.6916 | 56.2958 | 0.0046549 | -0.021248 | 0.00067514 | 0.053295 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.057176 | 0.031156 | 0.057453 | -66.7335 | -0.016908 | -66.7368 | 56.2839 | 56.1975 | 56.3809 | -66.8696 | -66.7291 | -0.027113 | -66.7865 | 56.1802 | 56.3671 | 56.1826 | -67.111 | -0.17798 | -0.011889 | -0.041945 | -0.045259 | 0.13272 | -0.098276 | 0.085165 | -0.41945 | -0.11554 | -0.037481 | -0.09488 | 0.32457 | 0.07137 | -0.11315 | 122.9755 | 122.8891 | 123.0725 | 66.6747 | -123.1653 | 122.8718 | 123.0587 | 122.8742 | 66.6645 | -123.4068
1718.7969 | 123.1338 | -66.7694 | 56.3141 | -0.0029761 | -0.021461 | 0.00088894 | 0.053722 | -0.0063052 | 0.062503 | -0.0074779 | -0.0024119 | -0.00034193 | 0.057604 | 0.031369 | 0.057667 | -66.7244 | -0.016908 | -66.7414 | 56.2793 | 56.1838 | 56.3718 | -66.8696 | -66.7291 | -0.017956 | -66.7865 | 56.1894 | 56.3717 | 56.2009 | -67.1065 | -0.10016 | -0.034778 | 0.045032 | 0.027982 | 0.12814 | -0.13032 | 0.057697 | -0.33705 | -0.1247 | 0.040339 | -0.01706 | 0.31999 | 0.057638 | -0.11315 | 123.0487 | 122.9532 | 123.1412 | 66.7525 | -123.1837 | 122.9588 | 123.1411 | 122.9703 | 66.7515 | -123.4205
1719.7969 | 123.1659 | -66.7465 | 56.3278 | -0.0029761 | -0.021461 | 0.00067514 | 0.053508 | -0.0058778 | 0.062503 | -0.0074779 | -0.0026255 | -0.00055553 | 0.056963 | 0.030942 | 0.057667 | -66.729 | -0.016908 | -66.7414 | 56.2747 | 56.2112 | 56.3809 | -66.8787 | -66.7336 | -0.027113 | -66.7819 | 56.1848 | 56.3717 | 56.1872 | -67.1065 | -0.1322 | -0.053089 | 0.017565 | 0.005094 | 0.1373 | -0.11658 | 0.053121 | -0.35993 | -0.14301 | 0.012872 | -0.035369 | 0.32457 | 0.043905 | -0.14062 | 123.0213 | 122.9578 | 123.1275 | 66.7296 | -123.2065 | 122.9313 | 123.1182 | 122.9337 | 66.7194 | -123.4343
1720.7969 | 123.1567 | -66.7328 | 56.3141 | 0.0046549 | -0.021461 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.015414 | -0.0024119 | -0.00076913 | 0.056963 | 0.031156 | 0.057453 | -66.729 | -0.016908 | -66.7368 | 56.2793 | 56.2021 | 56.3855 | -66.8696 | -66.7291 | -0.017956 | -66.7865 | 56.1848 | 56.3671 | 56.1826 | -67.1156 | -0.13678 | -0.034778 | 0.003832 | -0.00406 | 0.13272 | -0.11201 | 0.071432 | -0.38283 | -0.12928 | 0.003718 | -0.053681 | 0.32914 | 0.053059 | -0.13146 | 123.0121 | 122.9349 | 123.1183 | 66.7159 | -123.1837 | 122.9176 | 123.0999 | 122.9154 | 66.7148 | -123.4297
1721.7969 | 123.175 | -66.7099 | 56.3599 | -0.0029761 | -0.021675 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057176 | 0.031583 | 0.057881 | -66.729 | -0.007751 | -66.746 | 56.2793 | 56.1929 | 56.3809 | -66.8833 | -66.7336 | -0.017956 | -66.7819 | 56.1848 | 56.3671 | 56.2055 | -67.111 | -0.1734 | -0.080554 | -0.019056 | -0.036105 | 0.1373 | -0.16694 | 0.021078 | -0.40113 | -0.17505 | -0.023749 | -0.07199 | 0.32914 | 0.007283 | -0.15434 | 122.9892 | 122.9028 | 123.0908 | 66.7021 | -123.2432 | 122.8947 | 123.077 | 122.9154 | 66.6919 | -123.4709
1722.7969 | 123.1705 | -66.774 | 56.3141 | 0.0046549 | -0.021675 | 0.00046154 | 0.053295 | -0.0060916 | 0.062289 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057176 | 0.031369 | 0.057453 | -66.7244 | -0.016908 | -66.7414 | 56.2793 | 56.2021 | 56.3809 | -66.8741 | -66.7291 | -0.017956 | -66.7865 | 56.1848 | 56.3671 | 56.1964 | -67.111 | -0.10016 | -0.034778 | 0.04961 | 0.03256 | 0.13272 | -0.11201 | 0.066854 | -0.33705 | -0.12928 | 0.044917 | -0.012482 | 0.32457 | 0.053059 | -0.11773 | 123.0533 | 122.9761 | 123.1549 | 66.7571 | -123.1882 | 122.9588 | 123.1411 | 122.9703 | 66.756 | -123.4251
1723.8594 | 123.317 | -66.687 | 56.3141 | -0.0029761 | -0.021248 | 0.00046154 | 0.053936 | -0.0060916 | 0.062076 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057176 | 0.030942 | 0.05724 | -66.729 | -0.012329 | -66.7368 | 56.2793 | 56.1975 | 56.3718 | -66.8696 | -66.7336 | -0.017956 | -66.791 | 56.1848 | 56.3671 | 56.2147 | -67.111 | -0.18255 | -0.034778 | -0.041944 | -0.049836 | 0.13272 | -0.11659 | 0.057697 | -0.42402 | -0.12928 | -0.046637 | -0.10404 | 0.31999 | 0.053059 | -0.099412 | 122.9663 | 122.8845 | 123.0588 | 66.6747 | -123.1837 | 122.8718 | 123.0542 | 122.9017 | 66.6691 | -123.4251
1724.7969 | 123.2162 | -66.7053 | 56.3004 | -0.0029761 | -0.021889 | 0.00046154 | 0.053936 | -0.0060916 | 0.062503 | -0.0074779 | -0.0026255 | -0.00055553 | 0.05739 | 0.030942 | 0.05724 | -66.729 | -0.012329 | -66.7414 | 56.2656 | 56.1838 | 56.3855 | -66.8696 | -66.7382 | -0.022535 | -66.7819 | 56.1802 | 56.3671 | 56.2055 | -67.1156 | -0.16424 | -0.03478 | -0.023634 | -0.036105 | 0.12814 | -0.11659 | 0.085165 | -0.41029 | -0.12012 | -0.032905 | -0.076568 | 0.33372 | 0.066792 | -0.094836 | 122.9709 | 122.8891 | 123.0908 | 66.693 | -123.1699 | 122.8856 | 123.0725 | 122.9108 | 66.6828 | -123.416
1725.7969 | 123.1567 | -66.7694 | 56.3461 | -0.010607 | -0.021889 | 0.00088894 | 0.053508 | -0.0063052 | 0.062076 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056749 | 0.031156 | 0.057453 | -66.729 | -0.016908 | -66.7414 | 56.2839 | 56.2021 | 56.3855 | -66.8741 | -66.7336 | -0.027113 | -66.7819 | 56.1848 | 56.3671 | 56.1918 | -67.111 | -0.10474 | -0.062243 | 0.040453 | 0.027982 | 0.13272 | -0.14405 | 0.039389 | -0.34163 | -0.16132 | 0.03576 | -0.012481 | 0.32914 | 0.021016 | -0.15435 | 123.0533 | 122.9715 | 123.1549 | 66.7525 | -123.2203 | 122.9542 | 123.1366 | 122.9612 | 66.7423 | -123.4572
1726.7969 | 123.1567 | -66.774 | 56.3416 | 0.0046549 | -0.021675 | 0.00024794 | 0.053508 | -0.0060916 | 0.06293 | -0.0074779 | -0.0026255 | -0.00098273 | 0.056963 | 0.031369 | 0.057667 | -66.7335 | -0.012329 | -66.746 | 56.2885 | 56.1929 | 56.3809 | -66.8787 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3809 | 56.2376 | -67.1065 | -0.10474 | -0.053087 | 0.040453 | 0.027982 | 0.13272 | -0.14863 | 0.039388 | -0.33247 | -0.15674 | 0.031181 | -0.007903 | 0.32457 | 0.039329 | -0.10398 | 123.0625 | 122.9669 | 123.1549 | 66.7617 | -123.2203 | 122.9588 | 123.1549 | 123.0116 | 66.7515 | -123.448
1727.7969 | 123.1888 | -66.7053 | 56.3416 | 0.0046549 | -0.021461 | 0.00046154 | 0.053508 | -0.0060916 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.057176 | 0.031156 | 0.057881 | -66.729 | -0.012329 | -66.746 | 56.2839 | 56.2067 | 56.3855 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.3671 | 56.2101 | -67.111 | -0.16882 | -0.057666 | -0.023634 | -0.040683 | 0.12814 | -0.1349 | 0.043966 | -0.40571 | -0.15674 | -0.037484 | -0.076568 | 0.32914 | 0.025593 | -0.13146 | 122.9892 | 122.912 | 123.0908 | 66.693 | -123.2157 | 122.8901 | 123.0725 | 122.9154 | 66.6874 | -123.4526
1728.8594 | 123.2025 | -66.7648 | 56.3278 | -0.0029761 | -0.021889 | 0.00046154 | 0.053508 | -0.0063052 | 0.06293 | -0.0074779 | -0.0028393 | -0.00055553 | 0.056963 | 0.031156 | 0.057667 | -66.729 | -0.007751 | -66.7552 | 56.2885 | 56.1883 | 56.3764 | -66.8787 | -66.7474 | -0.027113 | -66.7865 | 56.194 | 56.3671 | 56.2147 | -67.111 | -0.11389 | -0.039354 | 0.035876 | 0.009671 | 0.12356 | -0.13948 | 0.048542 | -0.3462 | -0.13385 | 0.017447 | -0.021637 | 0.32457 | 0.039326 | -0.11315 | 123.0533 | 122.9532 | 123.1412 | 66.7571 | -123.2065 | 122.9588 | 123.132 | 122.9795 | 66.7377 | -123.4389
1729.7969 | 123.1796 | -66.7648 | 56.2775 | -0.0029761 | -0.021675 | 0.00024794 | 0.053722 | -0.0063052 | 0.062717 | 0.0077831 | -0.0024119 | -0.00076913 | 0.057176 | 0.031369 | 0.057453 | -66.7244 | -0.012329 | -66.7506 | 56.2839 | 56.1883 | 56.3855 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.1894 | 56.3763 | 56.1918 | -67.1065 | -0.10931 | 0.006421 | 0.040455 | 0.014249 | 0.12356 | -0.089124 | 0.10805 | -0.34162 | -0.088078 | 0.022026 | -0.017058 | 0.32457 | 0.098837 | -0.085684 | 123.0487 | 122.9532 | 123.1504 | 66.7525 | -123.1516 | 122.9542 | 123.1411 | 122.9566 | 66.7469 | -123.3839
1730.7969 | 123.2574 | -66.7374 | 56.2775 | -0.010607 | -0.021675 | 0.00046154 | 0.053722 | -0.0063052 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.031369 | 0.057453 | -66.729 | -0.012329 | -66.7552 | 56.2747 | 56.2021 | 56.3855 | -66.8696 | -66.7428 | -0.017956 | -66.7773 | 56.1757 | 56.3809 | 56.1918 | -67.1156 | -0.1322 | -0.002735 | 0.00841 | -0.017795 | 0.11441 | -0.075387 | 0.10805 | -0.37825 | -0.10181 | -0.00544 | -0.039945 | 0.3383 | 0.10342 | -0.085684 | 123.0121 | 122.9394 | 123.1229 | 66.725 | -123.147 | 122.913 | 123.1182 | 122.9291 | 66.7194 | -123.3931
1731.7969 | 123.1567 | -66.7786 | 56.3049 | -0.0029761 | -0.022102 | 0.00046154 | 0.053508 | -0.0060916 | 0.062503 | -0.0074779 | -0.0026255 | -0.0011965 | 0.057176 | 0.031369 | 0.057667 | -66.7244 | -0.016908 | -66.7597 | 56.2885 | 56.1929 | 56.3855 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1848 | 56.3717 | 56.2055 | -67.1065 | -0.086423 | -0.016466 | 0.054187 | 0.018824 | 0.10525 | -0.11201 | 0.080587 | -0.32789 | -0.12012 | 0.035758 | -0.003326 | 0.32457 | 0.066793 | -0.099414 | 123.067 | 122.9715 | 123.1641 | 66.7617 | -123.1699 | 122.9634 | 123.1503 | 122.9841 | 66.7515 | -123.4114
1732.7969 | 123.2529 | -66.7053 | 56.2912 | -0.0029761 | -0.021675 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.05739 | 0.031583 | 0.057667 | -66.7335 | -0.012329 | -66.7643 | 56.2747 | 56.2067 | 56.3855 | -66.8741 | -66.7336 | -0.017956 | -66.7819 | 56.1848 | 56.3717 | 56.178 | -67.1202 | -0.16882 | -0.016468 | -0.028212 | -0.058996 | 0.10983 | -0.084541 | 0.09432 | -0.41487 | -0.10639 | -0.028327 | -0.076568 | 0.3383 | 0.080526 | -0.11315 | 122.9801 | 122.912 | 123.0908 | 66.693 | -123.1653 | 122.8901 | 123.077 | 122.8834 | 66.6874 | -123.4114
1733.7969 | 123.1567 | -66.7648 | 56.3416 | 0.0046549 | -0.021889 | 0.00046154 | 0.053508 | -0.0065188 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.056963 | 0.031583 | 0.057881 | -66.7244 | -0.012329 | -66.7506 | 56.2793 | 56.1929 | 56.3855 | -66.8741 | -66.7474 | -0.022535 | -66.7819 | 56.1848 | 56.3671 | 56.1826 | -67.111 | -0.10931 | -0.062244 | 0.040455 | 0.014249 | 0.12356 | -0.14863 | 0.043966 | -0.3462 | -0.15674 | 0.017447 | -0.017058 | 0.32914 | 0.025593 | -0.15893 | 123.0441 | 122.9578 | 123.1504 | 66.7525 | -123.2157 | 122.9496 | 123.132 | 122.9475 | 66.7423 | -123.4526
1734.7969 | 123.2666 | -66.7191 | 56.2454 | -0.0029761 | -0.021889 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.05739 | 0.031156 | 0.057453 | -66.7198 | -0.016908 | -66.7552 | 56.2839 | 56.2112 | 56.3855 | -66.8741 | -66.7382 | -0.022535 | -66.7865 | 56.1802 | 56.3763 | 56.2284 | -67.1065 | -0.15509 | 0.038465 | -0.000744 | -0.036106 | 0.11898 | -0.034185 | 0.1401 | -0.3874 | -0.065191 | -0.019172 | -0.067414 | 0.31999 | 0.13088 | -0.017011 | 123.0029 | 122.9303 | 123.1046 | 66.7021 | -123.1196 | 122.8993 | 123.0954 | 122.9475 | 66.6965 | -123.3519
1735.7969 | 123.2483 | -66.7282 | 56.3095 | 0.0046549 | -0.021889 | 0.00046154 | 0.053295 | -0.0065188 | 0.06293 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057176 | 0.031583 | 0.057667 | -66.729 | -0.012329 | -66.7597 | 56.2793 | 56.2067 | 56.3855 | -66.8741 | -66.7474 | -0.017956 | -66.7865 | 56.1757 | 56.3763 | 56.2055 | -67.111 | -0.14593 | -0.0302 | -0.000746 | -0.03153 | 0.11441 | -0.10285 | 0.07601 | -0.38282 | -0.13386 | -0.019175 | -0.058259 | 0.32457 | 0.066794 | -0.10399 | 123.0075 | 122.9349 | 123.1137 | 66.7159 | -123.1837 | 122.9039 | 123.1045 | 122.9337 | 66.7103 | -123.4205
1736.8594 | 123.1979 | -66.7465 | 56.3782 | -0.0029761 | -0.021889 | 0.00024794 | 0.053295 | -0.0065188 | 0.062717 | 0.00015261 | -0.0024119 | -0.00076913 | 0.057176 | 0.031369 | 0.057667 | -66.7381 | -0.016908 | -66.7506 | 56.2839 | 56.2112 | 56.3855 | -66.8741 | -66.7428 | -0.017956 | -66.7727 | 56.1848 | 56.3671 | 56.2055 | -67.111 | -0.12762 | -0.094287 | 0.008409 | -0.004062 | 0.12356 | -0.16694 | 0.007345 | -0.36451 | -0.19336 | 0.003715 | -0.026211 | 0.3383 | -0.011028 | -0.17266 | 123.0304 | 122.9578 | 123.132 | 66.7296 | -123.2523 | 122.9313 | 123.1137 | 122.952 | 66.7286 | -123.4892
1737.7969 | 123.175 | -66.7191 | 56.3049 | -0.010607 | -0.022102 | 0.00046154 | 0.053081 | -0.0060916 | 0.062717 | 0.00015261 | -0.0024119 | -0.00098273 | 0.056963 | 0.031583 | 0.057881 | -66.7335 | -0.021486 | -66.7597 | 56.2839 | 56.2021 | 56.3855 | -66.8833 | -66.752 | -0.017956 | -66.7819 | 56.1802 | 56.3763 | 56.233 | -67.111 | -0.16425 | -0.021045 | -0.014479 | -0.040685 | 0.12356 | -0.10285 | 0.080587 | -0.39198 | -0.1247 | -0.032908 | -0.062835 | 0.32914 | 0.071371 | -0.071942 | 123.0029 | 122.9211 | 123.1046 | 66.6976 | -123.1882 | 122.8993 | 123.0954 | 122.952 | 66.7011 | -123.416
1738.7969 | 123.2574 | -66.7099 | 56.2683 | 0.0046549 | -0.021889 | 0.00067514 | 0.053722 | -0.0060916 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056749 | 0.031797 | 0.057453 | -66.7244 | -0.012329 | -66.7552 | 56.2747 | 56.2067 | 56.3809 | -66.8558 | -66.7428 | -0.022535 | -66.7819 | 56.1894 | 56.3717 | 56.2055 | -67.111 | -0.14593 | 0.00642 | -0.014477 | -0.045261 | 0.10067 | -0.061653 | 0.11263 | -0.40113 | -0.078923 | -0.032906 | -0.07199 | 0.32914 | 0.10341 | -0.062793 | 122.9846 | 122.9166 | 123.0908 | 66.6976 | -123.1241 | 122.8993 | 123.0816 | 122.9154 | 66.6874 | -123.3793
1739.7969 | 123.2803 | -66.7145 | 56.282 | -0.0029761 | -0.021889 | 0.00046154 | 0.053508 | -0.0065188 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.05739 | 0.031369 | 0.057453 | -66.7244 | -0.012329 | -66.7506 | 56.2839 | 56.2021 | 56.3809 | -66.8513 | -66.7474 | -0.027113 | -66.7865 | 56.1848 | 56.3626 | 56.2284 | -67.111 | -0.13677 | 0.001844 | -0.009899 | -0.036105 | 0.10067 | -0.079964 | 0.098898 | -0.39656 | -0.097233 | -0.032907 | -0.071991 | 0.32457 | 0.080525 | -0.053632 | 122.9984 | 122.9166 | 123.0954 | 66.7021 | -123.1333 | 122.8993 | 123.077 | 122.9429 | 66.6874 | -123.3931
1740.7969 | 123.175 | -66.7465 | 56.3461 | 0.012286 | -0.022102 | 0.00046154 | 0.053295 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057604 | 0.031369 | 0.057453 | -66.7244 | -0.007751 | -66.7643 | 56.2885 | 56.2021 | 56.3764 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.3763 | 56.1918 | -67.1156 | -0.12762 | -0.057664 | 0.022144 | -0.017797 | 0.10983 | -0.14405 | 0.030232 | -0.36909 | -0.16132 | 0.003715 | -0.035369 | 0.33372 | 0.030173 | -0.15435 | 123.035 | 122.9486 | 123.1229 | 66.7388 | -123.2203 | 122.9313 | 123.1228 | 122.9383 | 66.7286 | -123.4617
1741.7969 | 123.1613 | -66.7511 | 56.3095 | 0.0046549 | -0.021889 | 0.00024794 | 0.053722 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056963 | 0.031583 | 0.057453 | -66.729 | -0.003172 | -66.7552 | 56.2793 | 56.2021 | 56.3809 | -66.865 | -66.7428 | -0.017956 | -66.7773 | 56.1894 | 56.3763 | 56.1918 | -67.1156 | -0.11389 | -0.0302 | 0.022143 | -0.004062 | 0.10983 | -0.10743 | 0.071432 | -0.36451 | -0.12012 | 0.008293 | -0.026212 | 0.3383 | 0.066794 | -0.11773 | 123.0304 | 122.9532 | 123.132 | 66.7479 | -123.1745 | 122.9405 | 123.1274 | 122.9429 | 66.7331 | -123.4251
1742.7969 | 123.23 | -66.7099 | 56.3004 | 0.0046549 | -0.021889 | 3.4136e-05 | 0.053295 | -0.0060916 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.031369 | 0.057667 | -66.7335 | -0.007751 | -66.7552 | 56.2839 | 56.2067 | 56.3901 | -66.865 | -66.7474 | -0.017956 | -66.7773 | 56.1848 | 56.3671 | 56.2101 | -67.111 | -0.15509 | -0.016467 | -0.023634 | -0.045261 | 0.10983 | -0.093696 | 0.089744 | -0.40113 | -0.11554 | -0.037485 | -0.067411 | 0.33372 | 0.066792 | -0.090257 | 122.9938 | 122.9166 | 123.1 | 66.7021 | -123.1653 | 122.8947 | 123.077 | 122.92 | 66.6919 | -123.4114
1743.7969 | 123.2986 | -66.6962 | 56.3049 | -0.010607 | -0.022316 | 0.00046154 | 0.053508 | -0.0060916 | 0.062503 | -0.0074779 | -0.0028393 | -0.00076913 | 0.05739 | 0.031797 | 0.05724 | -66.7244 | -0.012329 | -66.7506 | 56.2839 | 56.1929 | 56.3809 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.1894 | 56.3717 | 56.2193 | -67.111 | -0.17798 | -0.021045 | -0.02821 | -0.054416 | 0.12356 | -0.11201 | 0.076009 | -0.41487 | -0.11554 | -0.046639 | -0.085723 | 0.32914 | 0.066793 | -0.085678 | 122.9801 | 122.8891 | 123.0771 | 66.6838 | -123.1791 | 122.8856 | 123.0679 | 122.9154 | 66.6782 | -123.416
1744.7969 | 123.2208 | -66.7145 | 56.3049 | -0.010607 | -0.021889 | 0.00046154 | 0.053508 | -0.0065188 | 0.062503 | 0.015414 | -0.0024119 | -0.00034193 | 0.056963 | 0.031369 | 0.057667 | -66.7244 | -0.026065 | -66.7643 | 56.2793 | 56.1975 | 56.3855 | -66.8741 | -66.7428 | -0.031692 | -66.7819 | 56.1802 | 56.3717 | 56.1964 | -67.111 | -0.15967 | -0.025623 | -0.009899 | -0.04984 | 0.10983 | -0.10743 | 0.080587 | -0.39656 | -0.1247 | -0.028328 | -0.067412 | 0.32914 | 0.066793 | -0.10857 | 122.9938 | 122.912 | 123.1 | 66.6884 | -123.1791 | 122.8947 | 123.0862 | 122.9108 | 66.6828 | -123.416
1745.875 | 123.1567 | -66.7191 | 56.3736 | -0.0029761 | -0.022102 | 0.00067514 | 0.053722 | -0.0063052 | 0.062503 | 0.015414 | -0.0026255 | -0.00055553 | 0.057176 | 0.031797 | 0.057667 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.2067 | 56.3809 | -66.8696 | -66.7382 | -0.017956 | -66.7819 | 56.1848 | 56.3671 | 56.1918 | -67.1156 | -0.15051 | -0.094287 | -0.009901 | -0.031528 | 0.11898 | -0.16694 | 0.007345 | -0.39656 | -0.18879 | -0.019172 | -0.062835 | 0.33372 | -0.00645 | -0.18181 | 122.9984 | 122.9257 | 123.1 | 66.7021 | -123.2432 | 122.9039 | 123.0862 | 122.9108 | 66.7011 | -123.4892
1746.7969 | 123.2483 | -66.7282 | 56.3187 | -0.010607 | -0.022102 | 0.00046154 | 0.053722 | -0.0060916 | 0.062076 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056963 | 0.031369 | 0.057667 | -66.729 | -0.016908 | -66.7597 | 56.2793 | 56.1975 | 56.3855 | -66.8787 | -66.752 | -0.022535 | -66.7865 | 56.1848 | 56.3809 | 56.1964 | -67.1156 | -0.15051 | -0.039356 | -0.000746 | -0.03153 | 0.11898 | -0.12117 | 0.066854 | -0.3874 | -0.13386 | -0.023753 | -0.058259 | 0.32914 | 0.062217 | -0.1223 | 123.0075 | 122.9257 | 123.1137 | 66.7113 | -123.1974 | 122.913 | 123.1091 | 122.9246 | 66.7057 | -123.4343
1747.7969 | 123.2437 | -66.7053 | 56.2866 | 0.0046549 | -0.021675 | 0.00046154 | 0.053722 | -0.0063052 | 0.062503 | -0.015108 | -0.0024119 | -0.00076913 | 0.057176 | 0.031797 | 0.057881 | -66.7244 | -0.016908 | -66.7506 | 56.2793 | 56.2158 | 56.3764 | -66.8696 | -66.7428 | -0.031692 | -66.7865 | 56.1848 | 56.3717 | 56.1964 | -67.1156 | -0.16424 | -0.007312 | -0.019055 | -0.045261 | 0.11898 | -0.070805 | 0.089741 | -0.41029 | -0.10181 | -0.037484 | -0.081147 | 0.32914 | 0.085104 | -0.09026 | 122.9846 | 122.9211 | 123.0817 | 66.6884 | -123.1562 | 122.8901 | 123.077 | 122.9017 | 66.6736 | -123.4022
1748.7969 | 123.2483 | -66.7053 | 56.3095 | 0.0046549 | -0.022316 | 0.00024794 | 0.053936 | -0.0058778 | 0.062503 | 0.0077831 | -0.0028393 | -0.00076913 | 0.057176 | 0.031797 | 0.057667 | -66.7244 | -0.016908 | -66.7368 | 56.2747 | 56.2021 | 56.3809 | -66.8696 | -66.7382 | -0.017956 | -66.7773 | 56.194 | 56.3717 | 56.2284 | -67.1156 | -0.16424 | -0.034778 | -0.019055 | -0.031526 | 0.13272 | -0.10743 | 0.071432 | -0.41029 | -0.11554 | -0.032905 | -0.071989 | 0.3383 | 0.062216 | -0.081098 | 122.9801 | 122.9074 | 123.0863 | 66.6884 | -123.1791 | 122.8993 | 123.077 | 122.9337 | 66.6874 | -123.4251
1749.7969 | 123.2391 | -66.7236 | 56.3095 | 0.0046549 | -0.022102 | 0.00067514 | 0.053508 | -0.0063052 | 0.062289 | 0.015414 | -0.0028393 | -0.00098273 | 0.057176 | 0.031369 | 0.057667 | -66.729 | -0.012329 | -66.746 | 56.2793 | 56.1929 | 56.3901 | -66.865 | -66.7382 | -0.022535 | -66.7773 | 56.1894 | 56.3671 | 56.2055 | -67.1065 | -0.14135 | -0.0302 | -0.005323 | -0.022372 | 0.11898 | -0.11659 | 0.080589 | -0.38282 | -0.12012 | -0.014594 | -0.053678 | 0.32914 | 0.057637 | -0.10399 | 123.0029 | 122.9166 | 123.1137 | 66.7113 | -123.1745 | 122.913 | 123.0908 | 122.9292 | 66.7011 | -123.416
1750.7969 | 123.2162 | -66.7328 | 56.3461 | -0.0029761 | -0.021889 | 0.00067514 | 0.053295 | -0.0065188 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.057176 | 0.031369 | 0.05724 | -66.7244 | -0.012329 | -66.746 | 56.2839 | 56.1929 | 56.3855 | -66.8741 | -66.7474 | -0.017956 | -66.7819 | 56.1802 | 56.3671 | 56.2055 | -67.111 | -0.14136 | -0.062243 | 0.008411 | -0.013217 | 0.12814 | -0.15321 | 0.039389 | -0.37825 | -0.1659 | -0.014597 | -0.049102 | 0.32914 | 0.021016 | -0.14061 | 123.0167 | 122.9257 | 123.1183 | 66.7205 | -123.2203 | 122.913 | 123.0999 | 122.9383 | 66.7148 | -123.4572
1751.7969 | 123.2391 | -66.7282 | 56.3095 | 0.0046549 | -0.021889 | 0.00046154 | 0.053722 | -0.0063052 | 0.06293 | -0.015108 | -0.0026255 | -0.00076913 | 0.057176 | 0.031369 | 0.057881 | -66.7244 | -0.016908 | -66.7506 | 56.293 | 56.2021 | 56.3855 | -66.865 | -66.7428 | -0.022535 | -66.7773 | 56.1848 | 56.3717 | 56.1964 | -67.111 | -0.13678 | -0.016465 | 0.003833 | -0.022373 | 0.1144 | -0.10743 | 0.07601 | -0.38282 | -0.1247 | -0.014596 | -0.049101 | 0.33372 | 0.062216 | -0.11315 | 123.0213 | 122.9303 | 123.1137 | 66.7113 | -123.1745 | 122.913 | 123.0999 | 122.9246 | 66.7057 | -123.4205
1752.8594 | 123.1476 | -66.7465 | 56.3461 | -0.0029761 | -0.021889 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0021983 | -0.00076913 | 0.057176 | 0.031369 | 0.057453 | -66.729 | -0.016908 | -66.7414 | 56.2793 | 56.2021 | 56.3901 | -66.8696 | -66.7382 | -0.022535 | -66.7865 | 56.1848 | 56.3717 | 56.2055 | -67.1202 | -0.12305 | -0.066821 | 0.017565 | 0.005094 | 0.12814 | -0.14405 | 0.043968 | -0.37367 | -0.16132 | 0.008294 | -0.039948 | 0.33372 | 0.025595 | -0.14061 | 123.0258 | 122.9486 | 123.1366 | 66.7296 | -123.2157 | 122.9313 | 123.1182 | 122.952 | 66.724 | -123.4663
1753.7969 | 123.2162 | -66.7191 | 56.2866 | -0.0029761 | -0.022316 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056963 | 0.031797 | 0.057667 | -66.729 | -0.007751 | -66.7368 | 56.2839 | 56.1975 | 56.3901 | -66.8741 | -66.7336 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.1872 | -67.1156 | -0.15509 | -0.002734 | -0.009901 | -0.017793 | 0.1373 | -0.089121 | 0.10348 | -0.39656 | -0.10181 | -0.014594 | -0.062835 | 0.33372 | 0.085104 | -0.099417 | 123.0029 | 122.9166 | 123.1092 | 66.7113 | -123.1608 | 122.9039 | 123.0908 | 122.9063 | 66.6965 | -123.4022
1754.7969 | 123.2803 | -66.7053 | 56.3049 | -0.0029761 | -0.021889 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00034193 | 0.056963 | 0.031583 | 0.05724 | -66.729 | -0.016908 | -66.7414 | 56.2839 | 56.1883 | 56.3809 | -66.8696 | -66.7382 | -0.027113 | -66.7819 | 56.1894 | 56.3671 | 56.1964 | -67.1065 | -0.16424 | -0.021045 | -0.023634 | -0.036105 | 0.12814 | -0.11659 | 0.076009 | -0.40113 | -0.11554 | -0.032905 | -0.076568 | 0.32457 | 0.062214 | -0.10857 | 122.9892 | 122.8937 | 123.0863 | 66.6884 | -123.1745 | 122.8947 | 123.0725 | 122.9017 | 66.6782 | -123.4114
1755.8594 | 123.2117 | -66.6916 | 56.2958 | -0.0029761 | -0.022102 | 0.00024794 | 0.053508 | -0.0060916 | 0.062076 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057176 | 0.031583 | 0.05724 | -66.729 | -0.030644 | -66.746 | 56.2839 | 56.1838 | 56.3809 | -66.8696 | -66.7382 | -0.022535 | -66.7819 | 56.1894 | 56.3763 | 56.1872 | -67.1156 | -0.17798 | -0.011889 | -0.037367 | -0.054416 | 0.12356 | -0.11201 | 0.085165 | -0.42403 | -0.10639 | -0.046638 | -0.090301 | 0.33372 | 0.080527 | -0.10857 | 122.9755 | 122.8754 | 123.0725 | 66.6609 | -123.1653 | 122.881 | 123.0679 | 122.8788 | 66.6691 | -123.4114
1756.7969 | 123.317 | -66.7053 | 56.3507 | 0.0046549 | -0.021889 | 0.00024794 | 0.053722 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056963 | 0.031797 | 0.057453 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.2067 | 56.3809 | -66.8741 | -66.7474 | -0.022535 | -66.7865 | 56.1848 | 56.3717 | 56.178 | -67.111 | -0.16882 | -0.066821 | -0.023634 | -0.031526 | 0.1373 | -0.14405 | 0.030233 | -0.40571 | -0.1659 | -0.042063 | -0.081147 | 0.32457 | 0.021017 | -0.17266 | 122.9892 | 122.912 | 123.0863 | 66.693 | -123.2249 | 122.8901 | 123.077 | 122.8834 | 66.6828 | -123.4617
1757.7969 | 123.2574 | -66.7053 | 56.3324 | 0.0046549 | -0.022316 | 0.00046154 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057176 | 0.031583 | 0.057667 | -66.729 | -0.021486 | -66.7506 | 56.2839 | 56.1975 | 56.3855 | -66.8741 | -66.7428 | -0.027113 | -66.7819 | 56.1894 | 56.3717 | 56.2147 | -67.1156 | -0.16882 | -0.04851 | -0.023634 | -0.045261 | 0.12356 | -0.1349 | 0.053122 | -0.41029 | -0.14301 | -0.037484 | -0.076568 | 0.33372 | 0.039328 | -0.11772 | 122.9892 | 122.9028 | 123.0908 | 66.6838 | -123.2065 | 122.8947 | 123.077 | 122.92 | 66.6782 | -123.448
1758.8594 | 123.2574 | -66.7053 | 56.3049 | -0.010607 | -0.022102 | 0.00024794 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00034193 | 0.057176 | 0.031797 | 0.057667 | -66.7381 | -0.021486 | -66.7368 | 56.2793 | 56.2021 | 56.3809 | -66.8741 | -66.7474 | -0.027113 | -66.7865 | 56.1802 | 56.3671 | 56.1964 | -67.111 | -0.16882 | -0.025623 | -0.03279 | -0.031526 | 0.1373 | -0.10285 | 0.076009 | -0.40571 | -0.1247 | -0.042063 | -0.081147 | 0.32457 | 0.062214 | -0.10857 | 122.9846 | 122.9074 | 123.0863 | 66.6838 | -123.1791 | 122.8856 | 123.0725 | 122.9017 | 66.6782 | -123.416
1759.7969 | 123.2391 | -66.6916 | 56.3141 | -0.0029761 | -0.021889 | 0.00046154 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057176 | 0.031583 | 0.057881 | -66.7335 | -0.007751 | -66.7368 | 56.2747 | 56.2021 | 56.3809 | -66.8741 | -66.7382 | -0.027113 | -66.7819 | 56.1894 | 56.3671 | 56.178 | -67.1202 | -0.18256 | -0.039356 | -0.041945 | -0.045259 | 0.1373 | -0.11201 | 0.066854 | -0.4286 | -0.1247 | -0.046638 | -0.090301 | 0.3383 | 0.053059 | -0.13604 | 122.9663 | 122.8937 | 123.0725 | 66.6838 | -123.1882 | 122.881 | 123.0587 | 122.8696 | 66.6645 | -123.4343
1760.8594 | 123.1705 | -66.7191 | 56.3416 | 0.012286 | -0.021675 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | 0.00015261 | -0.0026255 | -0.00034193 | 0.056749 | 0.031797 | 0.057453 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.2067 | 56.3855 | -66.8741 | -66.7428 | -0.027113 | -66.7819 | 56.194 | 56.3717 | 56.2193 | -67.1202 | -0.15509 | -0.062244 | -0.009901 | -0.031528 | 0.12356 | -0.1349 | 0.043966 | -0.40114 | -0.14759 | -0.023751 | -0.062835 | 0.3383 | 0.030172 | -0.1223 | 122.9984 | 122.9257 | 123.1046 | 66.7021 | -123.2157 | 122.913 | 123.0908 | 122.9383 | 66.6919 | -123.4617
1761.7969 | 123.2483 | -66.7236 | 56.3141 | -0.010607 | -0.022102 | 0.00024794 | 0.053722 | -0.0063052 | 0.062289 | -0.0074779 | -0.0026255 | -0.00055553 | 0.056749 | 0.03201 | 0.057453 | -66.7335 | -0.021486 | -66.7368 | 56.2885 | 56.2067 | 56.3764 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1802 | 56.3671 | 56.1826 | -67.1156 | -0.14593 | -0.025621 | -0.009901 | -0.013215 | 0.13272 | -0.10743 | 0.062275 | -0.39198 | -0.13386 | -0.019173 | -0.058257 | 0.33372 | 0.053059 | -0.13146 | 123.0121 | 122.9303 | 123.1 | 66.7021 | -123.1837 | 122.9039 | 123.0908 | 122.9063 | 66.6965 | -123.4297
1762.7969 | 123.2483 | -66.7053 | 56.3141 | 0.012286 | -0.021889 | 0.00067514 | 0.053722 | -0.0065188 | 0.062503 | 0.0077831 | -0.0026255 | -0.00098273 | 0.056963 | 0.032224 | 0.057667 | -66.729 | -0.012329 | -66.7368 | 56.2793 | 56.2021 | 56.3809 | -66.8696 | -66.752 | -0.022535 | -66.7865 | 56.1802 | 56.3717 | 56.2055 | -67.1156 | -0.16424 | -0.034778 | -0.023634 | -0.031526 | 0.13272 | -0.11201 | 0.066854 | -0.41029 | -0.13386 | -0.046641 | -0.081147 | 0.32914 | 0.057638 | -0.10857 | 122.9846 | 122.9074 | 123.0863 | 66.693 | -123.1837 | 122.8856 | 123.077 | 122.9108 | 66.6828 | -123.4297
1763.8594 | 123.2803 | -66.7145 | 56.2866 | 0.0046549 | -0.022102 | 0.00024794 | 0.053722 | -0.0060916 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.05739 | 0.031797 | 0.057453 | -66.7244 | -0.021486 | -66.7414 | 56.2839 | 56.2067 | 56.3809 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.2055 | -67.1065 | -0.15051 | -0.002734 | -0.009899 | -0.026949 | 0.12356 | -0.079963 | 0.09432 | -0.39198 | -0.10181 | -0.028328 | -0.067412 | 0.32457 | 0.085104 | -0.081103 | 122.9984 | 122.9211 | 123.0954 | 66.693 | -123.1516 | 122.8993 | 123.0862 | 122.92 | 66.6919 | -123.3931
1764.7969 | 123.23 | -66.7145 | 56.3416 | -0.0029761 | -0.022316 | 0.00046154 | 0.053295 | -0.0063052 | 0.062717 | -0.0074779 | -0.0028393 | -0.00098273 | 0.057176 | 0.031797 | 0.057667 | -66.7198 | -0.007751 | -66.7506 | 56.2839 | 56.2067 | 56.3855 | -66.8741 | -66.7428 | -0.017956 | -66.7865 | 56.1802 | 56.3763 | 56.1872 | -67.111 | -0.15967 | -0.057666 | -0.005321 | -0.036105 | 0.12356 | -0.1349 | 0.043966 | -0.39656 | -0.16132 | -0.028328 | -0.071991 | 0.32457 | 0.03475 | -0.15435 | 122.9984 | 122.9211 | 123.1 | 66.7067 | -123.2157 | 122.8947 | 123.0908 | 122.9017 | 66.6965 | -123.4526
1765.7969 | 123.2666 | -66.7007 | 56.3141 | -0.0029761 | -0.022316 | 0.00046154 | 0.053722 | -0.0065188 | 0.062076 | 0.0077831 | -0.0024119 | -0.00076913 | 0.05739 | 0.031797 | 0.057667 | -66.7244 | -0.016908 | -66.7368 | 56.2839 | 56.2021 | 56.3764 | -66.8696 | -66.7382 | -0.027113 | -66.7865 | 56.194 | 56.3671 | 56.1918 | -67.1156 | -0.16882 | -0.0302 | -0.023632 | -0.036103 | 0.13272 | -0.11201 | 0.062275 | -0.41487 | -0.12012 | -0.037482 | -0.085724 | 0.32914 | 0.053059 | -0.1223 | 122.9846 | 122.9028 | 123.0771 | 66.6838 | -123.1837 | 122.8947 | 123.0679 | 122.8925 | 66.6736 | -123.4297
1766.7969 | 123.1293 | -66.7191 | 56.3507 | -0.010607 | -0.022316 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056963 | 0.031797 | 0.057453 | -66.729 | -0.016908 | -66.746 | 56.2793 | 56.2112 | 56.3855 | -66.8696 | -66.7428 | -0.027113 | -66.7773 | 56.1802 | 56.3717 | 56.2101 | -67.111 | -0.15051 | -0.071399 | -0.009901 | -0.02695 | 0.12356 | -0.13947 | 0.034811 | -0.39198 | -0.17048 | -0.023751 | -0.058256 | 0.33372 | 0.021017 | -0.14061 | 122.9984 | 122.9303 | 123.1046 | 66.7021 | -123.2203 | 122.8993 | 123.0908 | 122.9292 | 66.6919 | -123.4617
1767.7969 | 123.2849 | -66.6962 | 56.3187 | 0.012286 | -0.022316 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0030529 | -0.00055553 | 0.057176 | 0.031797 | 0.057453 | -66.7244 | -0.012329 | -66.7368 | 56.2793 | 56.1929 | 56.3809 | -66.8696 | -66.7428 | -0.031692 | -66.791 | 56.1848 | 56.3717 | 56.1964 | -67.1248 | -0.1734 | -0.039356 | -0.02821 | -0.040681 | 0.13272 | -0.12574 | 0.062276 | -0.4286 | -0.13386 | -0.046639 | -0.09488 | 0.33372 | 0.05306 | -0.1223 | 122.9755 | 122.8891 | 123.0771 | 66.6838 | -123.1882 | 122.881 | 123.0679 | 122.8925 | 66.6645 | -123.4434
1768.7969 | 123.2117 | -66.7053 | 56.3416 | -0.010607 | -0.022316 | 0.00046154 | 0.053722 | -0.0063052 | 0.062289 | -0.0074779 | -0.0024119 | -0.00055553 | 0.056963 | 0.031797 | 0.057881 | -66.729 | -0.021486 | -66.746 | 56.2793 | 56.2021 | 56.3855 | -66.8787 | -66.7474 | -0.027113 | -66.7773 | 56.1848 | 56.3717 | 56.2101 | -67.1202 | -0.1734 | -0.062244 | -0.023634 | -0.040683 | 0.13272 | -0.13947 | 0.043966 | -0.41487 | -0.15674 | -0.042063 | -0.071989 | 0.34288 | 0.030172 | -0.13146 | 122.9846 | 122.9074 | 123.0908 | 66.6838 | -123.2203 | 122.8901 | 123.077 | 122.9154 | 66.6782 | -123.4617
1769.7969 | 123.3032 | -66.6916 | 56.282 | 0.0046549 | -0.02253 | 0.00046154 | 0.053081 | -0.0063052 | 0.062717 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057176 | 0.031583 | 0.057667 | -66.7244 | -0.016908 | -66.7552 | 56.2747 | 56.1929 | 56.3855 | -66.8741 | -66.7382 | -0.022535 | -66.7727 | 56.1802 | 56.3717 | 56.2009 | -67.1156 | -0.18256 | -0.007312 | -0.032788 | -0.063572 | 0.11898 | -0.089122 | 0.10348 | -0.42403 | -0.10181 | -0.046638 | -0.081143 | 0.34288 | 0.089682 | -0.081104 | 122.9663 | 122.8845 | 123.0771 | 66.6747 | -123.1562 | 122.8718 | 123.0633 | 122.8925 | 66.6691 | -123.3977
1770.7969 | 123.1293 | -66.7236 | 56.3828 | -0.0029761 | -0.022102 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00034193 | 0.056535 | 0.031797 | 0.057667 | -66.7244 | -0.016908 | -66.7323 | 56.2839 | 56.1929 | 56.3855 | -66.8741 | -66.7382 | -0.022535 | -66.7819 | 56.1802 | 56.3717 | 56.1826 | -67.1156 | -0.15051 | -0.098864 | -0.000744 | -0.008637 | 0.14187 | -0.18983 | 0.002768 | -0.39198 | -0.20252 | -0.014594 | -0.058257 | 0.33372 | -0.011026 | -0.20013 | 123.0075 | 122.9166 | 123.1092 | 66.7067 | -123.2569 | 122.9039 | 123.0954 | 122.9063 | 66.7011 | -123.4984
1771.8594 | 123.143 | -66.774 | 56.3141 | -0.010607 | -0.021675 | 0.00024794 | 0.053508 | -0.0065188 | 0.062289 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057176 | 0.031797 | 0.05724 | -66.729 | -0.016908 | -66.746 | 56.2702 | 56.1975 | 56.3901 | -66.8741 | -66.7428 | -0.022535 | -66.7773 | 56.1894 | 56.3763 | 56.1964 | -67.1156 | -0.10016 | -0.043935 | 0.045031 | 0.027982 | 0.12814 | -0.11659 | 0.076011 | -0.34163 | -0.1247 | 0.031181 | -0.003324 | 0.3383 | 0.062216 | -0.11773 | 123.0441 | 122.9715 | 123.1641 | 66.7571 | -123.1882 | 122.9634 | 123.1503 | 122.9703 | 66.7515 | -123.4297
1772.7969 | 123.1522 | -66.7053 | 56.3599 | 0.0046549 | -0.022102 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | -0.0074779 | -0.0026255 | -0.00034193 | 0.056963 | 0.031797 | 0.057453 | -66.7335 | -0.007751 | -66.7368 | 56.2839 | 56.1975 | 56.3855 | -66.865 | -66.7428 | -0.027113 | -66.7819 | 56.1848 | 56.3763 | 56.1918 | -67.1156 | -0.15967 | -0.075976 | -0.028212 | -0.031526 | 0.12814 | -0.16236 | 0.025656 | -0.41029 | -0.17505 | -0.037484 | -0.076568 | 0.33372 | 0.01644 | -0.16808 | 122.9892 | 122.9028 | 123.0908 | 66.6976 | -123.2249 | 122.8901 | 123.0816 | 122.8971 | 66.6782 | -123.4755
1773.7969 | 123.2941 | -66.6916 | 56.3049 | -0.0029761 | -0.022102 | 3.4136e-05 | 0.053722 | -0.0060916 | 0.062076 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056963 | 0.031797 | 0.057453 | -66.7244 | -0.021486 | -66.7414 | 56.2793 | 56.2112 | 56.3855 | -66.8741 | -66.7291 | -0.022535 | -66.7865 | 56.1848 | 56.3763 | 56.1735 | -67.1156 | -0.18256 | -0.025623 | -0.032788 | -0.049838 | 0.13272 | -0.093695 | 0.080587 | -0.42403 | -0.12012 | -0.037481 | -0.09488 | 0.32914 | 0.071371 | -0.13146 | 122.9709 | 122.9028 | 123.0771 | 66.6701 | -123.1791 | 122.8764 | 123.0679 | 122.8651 | 66.6691 | -123.4205
1774.7969 | 123.1934 | -66.7099 | 56.3324 | -0.0029761 | -0.02253 | 0.00046154 | 0.053081 | -0.0063052 | 0.062076 | 0.0077831 | -0.0024119 | -0.00055553 | 0.056749 | 0.031797 | 0.057453 | -66.7244 | -0.016908 | -66.746 | 56.293 | 56.2112 | 56.3855 | -66.8833 | -66.7382 | -0.022535 | -66.7865 | 56.1894 | 56.3717 | 56.2101 | -67.1156 | -0.1734 | -0.039353 | -0.014477 | -0.036105 | 0.1373 | -0.12116 | 0.053122 | -0.40571 | -0.14301 | -0.028327 | -0.076569 | 0.32914 | 0.039328 | -0.1223 | 123.0029 | 122.9211 | 123.0954 | 66.693 | -123.2157 | 122.8993 | 123.0816 | 122.92 | 66.6874 | -123.448
1775.7969 | 123.2666 | -66.7007 | 56.3141 | -0.0029761 | -0.022102 | 0.00024794 | 0.053508 | -0.0063052 | 0.062289 | 0.015414 | -0.0026255 | -0.00034193 | 0.057176 | 0.031583 | 0.057453 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.2021 | 56.3855 | -66.8558 | -66.7382 | -0.027113 | -66.7865 | 56.1894 | 56.3763 | 56.2147 | -67.1202 | -0.15508 | -0.0302 | -0.028211 | -0.036103 | 0.11898 | -0.11201 | 0.071432 | -0.41945 | -0.1247 | -0.037482 | -0.085724 | 0.33372 | 0.062216 | -0.099412 | 122.9846 | 122.9028 | 123.0863 | 66.6884 | -123.1699 | 122.8901 | 123.077 | 122.9154 | 66.6736 | -123.4343
1776.7969 | 123.1338 | -66.7557 | 56.3599 | -0.010607 | -0.021889 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056963 | 0.031797 | 0.057667 | -66.7198 | -0.007751 | -66.7368 | 56.2885 | 56.2021 | 56.3947 | -66.865 | -66.7428 | -0.022535 | -66.7865 | 56.1848 | 56.3763 | 56.1826 | -67.1202 | -0.10931 | -0.071397 | 0.035877 | 0.018828 | 0.12814 | -0.15778 | 0.034814 | -0.36452 | -0.17505 | 0.01287 | -0.030793 | 0.33372 | 0.01644 | -0.17724 | 123.0441 | 122.9578 | 123.1504 | 66.7479 | -123.2249 | 122.9405 | 123.132 | 122.9383 | 66.7331 | -123.4801
1777.8594 | 123.143 | -66.774 | 56.3187 | -0.0029761 | -0.022316 | 0.00046154 | 0.053081 | -0.0060916 | 0.062076 | 0.0077831 | -0.0028393 | -0.00034193 | 0.056535 | 0.031797 | 0.057026 | -66.7335 | -0.012329 | -66.7323 | 56.2885 | 56.2112 | 56.3947 | -66.8741 | -66.7291 | -0.022535 | -66.7819 | 56.1802 | 56.3671 | 56.1964 | -67.1156 | -0.10016 | -0.030199 | 0.040453 | 0.041717 | 0.14187 | -0.10743 | 0.076012 | -0.34163 | -0.13843 | 0.044917 | -0.007903 | 0.33372 | 0.048481 | -0.1223 | 123.0625 | 122.9852 | 123.1687 | 66.7617 | -123.1928 | 122.9542 | 123.1411 | 122.9703 | 66.7515 | -123.4343
1778.7969 | 123.1567 | -66.7511 | 56.3232 | 0.0046549 | -0.022316 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062289 | 0.00015261 | -0.0026255 | -0.00098273 | 0.05739 | 0.031797 | 0.057453 | -66.729 | -0.012329 | -66.7368 | 56.293 | 56.1975 | 56.3855 | -66.8741 | -66.7291 | -0.027113 | -66.7819 | 56.1848 | 56.3671 | 56.2238 | -67.1156 | -0.12305 | -0.030198 | 0.022143 | 0.014251 | 0.1373 | -0.12574 | 0.062277 | -0.36451 | -0.13843 | 0.022029 | -0.030791 | 0.33372 | 0.043904 | -0.09941 | 123.0441 | 122.9486 | 123.1366 | 66.7388 | -123.1974 | 122.9359 | 123.1182 | 122.9749 | 66.724 | -123.4389
1779.8594 | 123.1613 | -66.7603 | 56.3461 | 0.012286 | -0.02253 | 3.4136e-05 | 0.053295 | -0.0063052 | 0.062289 | -0.0074779 | -0.0026255 | -0.00076913 | 0.057176 | 0.032224 | 0.057667 | -66.729 | -0.012329 | -66.7277 | 56.2839 | 56.1975 | 56.3947 | -66.8741 | -66.7336 | -0.017956 | -66.7773 | 56.1894 | 56.3671 | 56.2147 | -67.1202 | -0.11389 | -0.062243 | 0.031298 | 0.032562 | 0.14645 | -0.14863 | 0.048547 | -0.35994 | -0.15674 | 0.026605 | -0.017057 | 0.34288 | 0.021016 | -0.13146 | 123.0441 | 122.9578 | 123.1549 | 66.7479 | -123.2203 | 122.9496 | 123.1274 | 122.9749 | 66.7423 | -123.4663
1780.7969 | 123.1979 | -66.7328 | 56.3187 | -0.018238 | -0.022316 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00098273 | 0.057176 | 0.03201 | 0.05724 | -66.7244 | -0.016908 | -66.7368 | 56.2885 | 56.2021 | 56.3809 | -66.865 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.1872 | -67.1202 | -0.1322 | -0.030199 | 0.008411 | -0.00406 | 0.12814 | -0.11659 | 0.062276 | -0.38741 | -0.13386 | -0.010018 | -0.049102 | 0.3383 | 0.05306 | -0.13146 | 123.0213 | 122.9349 | 123.1137 | 66.7159 | -123.1837 | 122.9176 | 123.1045 | 122.92 | 66.7103 | -123.4389
1781.8594 | 123.2666 | -66.7053 | 56.3004 | 0.0046549 | -0.022316 | 0.00046154 | 0.053508 | -0.0060916 | 0.062289 | -0.0074779 | -0.0026255 | -0.00055553 | 0.056963 | 0.032224 | 0.057453 | -66.7244 | -0.016908 | -66.7368 | 56.2839 | 56.2067 | 56.3855 | -66.8696 | -66.7428 | -0.027113 | -66.7819 | 56.1848 | 56.3717 | 56.178 | -67.1202 | -0.16424 | -0.016467 | -0.019055 | -0.031526 | 0.13272 | -0.093696 | 0.085165 | -0.41487 | -0.11554 | -0.037484 | -0.076568 | 0.3383 | 0.071371 | -0.12231 | 122.9892 | 122.912 | 123.0908 | 66.6884 | -123.1699 | 122.8901 | 123.077 | 122.8834 | 66.6782 | -123.4205
1782.7969 | 123.1567 | -66.7236 | 56.3919 | -0.0029761 | -0.022743 | 0.00046154 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057176 | 0.03201 | 0.05724 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.2067 | 56.3901 | -66.8787 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.3717 | 56.2147 | -67.1202 | -0.15509 | -0.10802 | -0.005323 | -0.013215 | 0.14188 | -0.18525 | -0.001809 | -0.39656 | -0.2071 | -0.019173 | -0.058257 | 0.3383 | -0.020182 | -0.17723 | 123.0075 | 122.9303 | 123.1137 | 66.7113 | -123.2706 | 122.9084 | 123.0954 | 122.9383 | 66.7057 | -123.5121
1783.7969 | 123.2941 | -66.6733 | 56.3004 | -0.0029761 | -0.022316 | 0.00024794 | 0.053722 | -0.0060916 | 0.062289 | 0.0077831 | -0.0026255 | -0.00034193 | 0.056963 | 0.03201 | 0.057453 | -66.7244 | -0.016908 | -66.7414 | 56.2793 | 56.1975 | 56.3901 | -66.865 | -66.7382 | -0.022535 | -66.791 | 56.1848 | 56.3717 | 56.2147 | -67.1156 | -0.19171 | -0.021045 | -0.051098 | -0.068148 | 0.12356 | -0.10285 | 0.089744 | -0.44233 | -0.11554 | -0.064948 | -0.11777 | 0.32457 | 0.071371 | -0.085679 | 122.9526 | 122.8708 | 123.0634 | 66.6564 | -123.1653 | 122.8581 | 123.045 | 122.888 | 66.6507 | -123.416
1784.7969 | 123.1934 | -66.7236 | 56.3461 | 0.0046549 | -0.022316 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0021983 | -0.00076913 | 0.057176 | 0.032224 | 0.057667 | -66.7335 | -0.021486 | -66.7414 | 56.2839 | 56.1883 | 56.3855 | -66.8787 | -66.7474 | -0.017956 | -66.7727 | 56.1894 | 56.3717 | 56.1918 | -67.1202 | -0.15509 | -0.062243 | -0.009901 | -0.017794 | 0.1373 | -0.15779 | 0.039389 | -0.39656 | -0.15674 | -0.023752 | -0.049099 | 0.34746 | 0.025595 | -0.15435 | 123.0075 | 122.912 | 123.1092 | 66.7021 | -123.2249 | 122.913 | 123.0954 | 122.9154 | 66.7057 | -123.4663
1785.7969 | 123.1613 | -66.6916 | 56.3095 | 0.0046549 | -0.02253 | 0.00046154 | 0.053295 | -0.0060916 | 0.062717 | 0.0077831 | -0.0028393 | -0.00098273 | 0.057176 | 0.031797 | 0.057667 | -66.7244 | -0.021486 | -66.7414 | 56.293 | 56.2067 | 56.3855 | -66.8696 | -66.7428 | -0.013377 | -66.7865 | 56.1848 | 56.3717 | 56.1964 | -67.1202 | -0.17798 | -0.016465 | -0.032788 | -0.049838 | 0.12814 | -0.10285 | 0.07601 | -0.4286 | -0.1247 | -0.051217 | -0.09488 | 0.33372 | 0.062216 | -0.11315 | 122.9846 | 122.8982 | 123.0771 | 66.6701 | -123.1791 | 122.8764 | 123.0633 | 122.8879 | 66.6782 | -123.4297
1786.7969 | 123.1705 | -66.7145 | 56.3599 | 0.0046549 | -0.022743 | 0.00046154 | 0.053508 | -0.0065188 | 0.062503 | -0.0074779 | -0.0030529 | -0.00098273 | 0.056535 | 0.03201 | 0.057667 | -66.7244 | -0.016908 | -66.7414 | 56.2793 | 56.2067 | 56.3947 | -66.8696 | -66.7382 | -0.017956 | -66.7865 | 56.1848 | 56.3671 | 56.2147 | -67.111 | -0.15509 | -0.080554 | -0.009899 | -0.026949 | 0.12814 | -0.1532 | 0.034814 | -0.39656 | -0.17505 | -0.023749 | -0.071991 | 0.32457 | 0.007283 | -0.14519 | 122.9938 | 122.9211 | 123.1092 | 66.6976 | -123.2294 | 122.8993 | 123.0816 | 122.9292 | 66.6965 | -123.4709
1787.8594 | 123.2529 | -66.7236 | 56.2866 | -0.0029761 | -0.022316 | 0.00046154 | 0.053722 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056963 | 0.031797 | 0.057667 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.1975 | 56.3947 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3671 | 56.1964 | -67.1202 | -0.15051 | -0.002734 | -0.005323 | -0.013215 | 0.1373 | -0.089121 | 0.10806 | -0.39656 | -0.10181 | -0.019173 | -0.058257 | 0.3383 | 0.080525 | -0.09026 | 123.0075 | 122.9211 | 123.1183 | 66.7113 | -123.1608 | 122.9084 | 123.0908 | 122.92 | 66.7011 | -123.4068
1788.7969 | 123.2208 | -66.7099 | 56.3461 | 0.0046549 | -0.022102 | 0.00046154 | 0.053508 | -0.0065188 | 0.062076 | 0.00015261 | -0.0024119 | -0.00055553 | 0.057604 | 0.03201 | 0.057453 | -66.729 | -0.012329 | -66.7414 | 56.2793 | 56.2067 | 56.3901 | -66.8787 | -66.7336 | -0.022535 | -66.7819 | 56.1894 | 56.3671 | 56.2101 | -67.111 | -0.16882 | -0.066821 | -0.019056 | -0.031527 | 0.1373 | -0.13947 | 0.043968 | -0.40113 | -0.15674 | -0.023749 | -0.07199 | 0.32914 | 0.021016 | -0.13603 | 122.9892 | 122.9166 | 123.1 | 66.6976 | -123.2249 | 122.8993 | 123.077 | 122.92 | 66.6874 | -123.4572
1789.8594 | 123.262 | -66.7053 | 56.2958 | 0.012286 | -0.02253 | 0.00046154 | 0.053936 | -0.0063052 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057176 | 0.031797 | 0.057453 | -66.729 | -0.016908 | -66.7368 | 56.2885 | 56.1975 | 56.3855 | -66.8787 | -66.7336 | -0.017956 | -66.7819 | 56.1894 | 56.3763 | 56.1918 | -67.1156 | -0.1734 | -0.00731 | -0.023634 | -0.031526 | 0.14188 | -0.098276 | 0.089743 | -0.41029 | -0.10639 | -0.028327 | -0.076568 | 0.33372 | 0.080527 | -0.10399 | 122.9938 | 122.9028 | 123.0908 | 66.6884 | -123.1745 | 122.8947 | 123.0816 | 122.8971 | 66.6874 | -123.4114
1790.7969 | 123.2162 | -66.7053 | 56.3507 | 0.0046549 | -0.02253 | 0.00046154 | 0.053295 | -0.0058778 | 0.062503 | -0.0074779 | -0.0026255 | -0.00034193 | 0.056963 | 0.03201 | 0.057667 | -66.7244 | -0.016908 | -66.7368 | 56.2885 | 56.2021 | 56.3901 | -66.8696 | -66.7428 | -0.022535 | -66.7865 | 56.1848 | 56.3671 | 56.2101 | -67.1156 | -0.16424 | -0.062242 | -0.019055 | -0.031526 | 0.13272 | -0.14863 | 0.03939 | -0.41029 | -0.1659 | -0.037484 | -0.081147 | 0.32914 | 0.016438 | -0.14061 | 122.9938 | 122.9074 | 123.0954 | 66.6884 | -123.2203 | 122.8901 | 123.0725 | 122.9154 | 66.6828 | -123.4663
1791.8594 | 123.2162 | -66.7099 | 56.3004 | -0.0029761 | -0.02253 | 0.00067514 | 0.054149 | -0.0065188 | 0.062503 | -0.0074779 | -0.0024119 | -0.00076913 | 0.056963 | 0.032224 | 0.057453 | -66.7335 | -0.012329 | -66.7414 | 56.2839 | 56.2067 | 56.3947 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3671 | 56.2147 | -67.111 | -0.16882 | -0.016467 | -0.023634 | -0.031527 | 0.1373 | -0.093696 | 0.094323 | -0.40113 | -0.11097 | -0.037485 | -0.07199 | 0.32914 | 0.066792 | -0.085679 | 122.9938 | 122.9166 | 123.1046 | 66.6976 | -123.1791 | 122.8993 | 123.077 | 122.9246 | 66.6919 | -123.4114
1792.7969 | 123.1705 | -66.7465 | 56.3507 | -0.010607 | -0.022316 | 0.00046154 | 0.053295 | -0.0063052 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056963 | 0.032224 | 0.057667 | -66.729 | -0.016908 | -66.746 | 56.2885 | 56.2067 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.7819 | 56.1894 | 56.3763 | 56.1872 | -67.111 | -0.1322 | -0.062242 | 0.017565 | 0.000516 | 0.13272 | -0.14405 | 0.043969 | -0.36451 | -0.16132 | 0.003715 | -0.035369 | 0.32914 | 0.025595 | -0.1635 | 123.035 | 122.9532 | 123.1412 | 66.7296 | -123.2294 | 122.9359 | 123.1228 | 122.9337 | 66.724 | -123.4617
1793.8594 | 123.2666 | -66.7282 | 56.2683 | 0.0046549 | -0.02253 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056749 | 0.032224 | 0.057667 | -66.7335 | -0.016908 | -66.746 | 56.2793 | 56.2067 | 56.3809 | -66.8741 | -66.7474 | -0.022535 | -66.7773 | 56.1894 | 56.3671 | 56.2055 | -67.111 | -0.14593 | 0.010998 | -0.005324 | -0.017795 | 0.12814 | -0.061653 | 0.11263 | -0.38282 | -0.078923 | -0.019175 | -0.049101 | 0.33372 | 0.098835 | -0.062793 | 123.0075 | 122.9349 | 123.1092 | 66.7113 | -123.1425 | 122.9176 | 123.0954 | 122.9337 | 66.7057 | -123.3793
1794.7969 | 123.1888 | -66.7465 | 56.3644 | 0.0046549 | -0.022957 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062289 | 0.0077831 | -0.0026255 | -0.00076913 | 0.056963 | 0.032224 | 0.057667 | -66.7244 | -0.012329 | -66.746 | 56.2885 | 56.2067 | 56.3993 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3671 | 56.1872 | -67.1156 | -0.1322 | -0.075975 | 0.022144 | 0.000516 | 0.13272 | -0.15778 | 0.034814 | -0.36909 | -0.17505 | -0.000864 | -0.035369 | 0.33372 | 0.002705 | -0.17724 | 123.035 | 122.9532 | 123.1458 | 66.7342 | -123.2432 | 122.9359 | 123.1137 | 122.9337 | 66.7286 | -123.4801
1795.8281 | 123.2758 | -66.7053 | 56.3141 | 0.012286 | -0.02253 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.0077831 | -0.0026255 | -0.00098273 | 0.057176 | 0.032224 | 0.057667 | -66.729 | -0.016908 | -66.7414 | 56.2839 | 56.1975 | 56.3901 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.1848 | 56.3717 | 56.2009 | -67.1156 | -0.1734 | -0.0302 | -0.023634 | -0.036105 | 0.1373 | -0.11659 | 0.076011 | -0.41029 | -0.12928 | -0.042063 | -0.076568 | 0.33372 | 0.057638 | -0.11315 | 122.9892 | 122.9028 | 123.0954 | 66.6884 | -123.1928 | 122.8901 | 123.077 | 122.9063 | 66.6919 | -123.4297
1796.8594 | 123.2574 | -66.7053 | 56.3232 | 0.0046549 | -0.02253 | 0.00024794 | 0.053722 | -0.0065188 | 0.062076 | -0.015108 | -0.0026255 | -0.00076913 | 0.056749 | 0.032224 | 0.057453 | -66.7244 | -0.016908 | -66.7368 | 56.2793 | 56.2021 | 56.3855 | -66.8833 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3717 | 56.2284 | -67.1156 | -0.17798 | -0.043933 | -0.019055 | -0.031526 | 0.14646 | -0.12116 | 0.062277 | -0.41029 | -0.13385 | -0.032905 | -0.081147 | 0.32914 | 0.048483 | -0.094831 | 122.9846 | 122.9074 | 123.0908 | 66.6884 | -123.2065 | 122.8947 | 123.077 | 122.9337 | 66.6874 | -123.4389
1797.7969 | 123.1979 | -66.7191 | 56.3507 | 0.0046549 | -0.02253 | 0.00024794 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056963 | 0.031797 | 0.057667 | -66.7335 | -0.012329 | -66.746 | 56.2793 | 56.2112 | 56.3947 | -66.8787 | -66.7428 | -0.013377 | -66.7819 | 56.1802 | 56.3717 | 56.2193 | -67.1202 | -0.15967 | -0.071399 | -0.014479 | -0.02695 | 0.13272 | -0.13947 | 0.043969 | -0.40114 | -0.17048 | -0.023751 | -0.062835 | 0.3383 | 0.021017 | -0.13145 | 122.9984 | 122.9303 | 123.1137 | 66.7067 | -123.2294 | 122.8993 | 123.0908 | 122.9383 | 66.7057 | -123.4709
1798.9844 | 123.1522 | -66.7557 | 56.3599 | 0.0046549 | -0.022957 | 0.00067514 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056963 | 0.032438 | 0.057667 | -66.729 | -0.003172 | -66.7414 | 56.2839 | 56.2158 | 56.3993 | -66.8741 | -66.7382 | -0.013377 | -66.791 | 56.1894 | 56.3717 | 56.2055 | -67.1156 | -0.11847 | -0.075976 | 0.02672 | 0.014249 | 0.13272 | -0.14405 | 0.039392 | -0.35994 | -0.17047 | 0.017449 | -0.035371 | 0.32457 | 0.011862 | -0.15434 | 123.0396 | 122.9715 | 123.1549 | 66.7525 | -123.234 | 122.9451 | 123.1274 | 122.9612 | 66.7423 | -123.4755
1799.9219 | 123.23 | -66.7236 | 56.2958 | -0.0029761 | -0.022957 | 0.00046154 | 0.053722 | -0.0065188 | 0.062503 | 0.00015261 | -0.0024119 | -0.00098273 | 0.057176 | 0.03201 | 0.057453 | -66.7198 | -0.016908 | -66.7368 | 56.2793 | 56.1929 | 56.3855 | -66.8696 | -66.7382 | -0.027113 | -66.7865 | 56.1848 | 56.3809 | 56.1826 | -67.1248 | -0.14593 | -0.016467 | 0.003834 | -0.013215 | 0.13272 | -0.10285 | 0.089743 | -0.40114 | -0.11097 | -0.014594 | -0.062836 | 0.3383 | 0.085106 | -0.11315 | 123.0029 | 122.9166 | 123.1092 | 66.7067 | -123.1653 | 122.9084 | 123.1045 | 122.9063 | 66.6965 | -123.4205
1800.7969 | 123.1888 | -66.7648 | 56.3507 | -0.010607 | -0.02253 | 0.00024794 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0026255 | -0.00076913 | 0.057176 | 0.031583 | 0.05724 | -66.729 | -0.012329 | -66.746 | 56.2885 | 56.2021 | 56.3901 | -66.8787 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.3671 | 56.2147 | -67.1156 | -0.11389 | -0.062242 | 0.035876 | 0.018827 | 0.13272 | -0.14863 | 0.03939 | -0.35078 | -0.15674 | 0.017447 | -0.021637 | 0.32914 | 0.016438 | -0.13603 | 123.0533 | 122.9669 | 123.1549 | 66.7525 | -123.2294 | 122.9588 | 123.132 | 122.9795 | 66.7515 | -123.4663
1801.7969 | 123.2071 | -66.7191 | 56.3416 | 0.0046549 | -0.02253 | 0.00046154 | 0.053081 | -0.0063052 | 0.062503 | 0.0077831 | -0.0024119 | -0.00098273 | 0.056963 | 0.03201 | 0.057453 | -66.7198 | -0.021486 | -66.7368 | 56.2839 | 56.2112 | 56.3947 | -66.8833 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.2147 | -67.1202 | -0.16425 | -0.057666 | -0.000744 | -0.017793 | 0.14646 | -0.13032 | 0.053124 | -0.40114 | -0.15674 | -0.023751 | -0.062835 | 0.3383 | 0.030172 | -0.12688 | 123.0029 | 122.9303 | 123.1137 | 66.6976 | -123.2249 | 122.9039 | 123.0908 | 122.9337 | 66.6965 | -123.4617
1802.7969 | 123.2254 | -66.7465 | 56.3278 | 0.0046549 | -0.02253 | 0.00046154 | 0.053508 | -0.0060916 | 0.062503 | -0.0074779 | -0.0028393 | -0.00055553 | 0.056963 | 0.03201 | 0.057667 | -66.729 | -0.016908 | -66.7552 | 56.2885 | 56.2021 | 56.3947 | -66.8787 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3717 | 56.2055 | -67.111 | -0.1322 | -0.039354 | 0.017565 | -0.00864 | 0.12356 | -0.12574 | 0.066857 | -0.36451 | -0.13843 | 0.008294 | -0.039948 | 0.32457 | 0.043905 | -0.1223 | 123.035 | 122.9486 | 123.1412 | 66.7296 | -123.2065 | 122.9359 | 123.1182 | 122.952 | 66.7286 | -123.4389
1803.7969 | 123.1613 | -66.7557 | 56.3461 | -0.0029761 | -0.022743 | 0.00024794 | 0.053508 | -0.0065188 | 0.062717 | 0.015414 | -0.0026255 | -0.00076913 | 0.056963 | 0.032224 | 0.057453 | -66.7244 | -0.016908 | -66.7414 | 56.2793 | 56.1975 | 56.3901 | -66.8833 | -66.7382 | -0.022535 | -66.7819 | 56.1757 | 56.3717 | 56.2238 | -67.1202 | -0.12763 | -0.066821 | 0.031299 | 0.014249 | 0.14188 | -0.14863 | 0.043968 | -0.36452 | -0.17048 | 0.017449 | -0.026214 | 0.3383 | 0.025595 | -0.1223 | 123.035 | 122.9532 | 123.1458 | 66.7388 | -123.2294 | 122.9313 | 123.1274 | 122.9795 | 66.7331 | -123.4663
1804.8594 | 123.143 | -66.7603 | 56.3461 | -0.0029761 | -0.022957 | 0.00046154 | 0.053295 | -0.0063052 | 0.062503 | 0.00015261 | -0.0026255 | -0.0011965 | 0.056963 | 0.032438 | 0.057667 | -66.7244 | -0.016908 | -66.7414 | 56.2839 | 56.2158 | 56.3947 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.1848 | 56.3717 | 56.2147 | -67.1202 | -0.11847 | -0.062243 | 0.035877 | 0.018827 | 0.1373 | -0.13031 | 0.048547 | -0.35994 | -0.16132 | 0.012869 | -0.021636 | 0.3383 | 0.025595 | -0.13146 | 123.0441 | 122.9761 | 123.1549 | 66.7433 | -123.2249 | 122.9451 | 123.132 | 122.9749 | 66.7423 | -123.4663
1805.7969 | 123.1384 | -66.7511 | 56.337 | -0.0029761 | -0.02253 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056749 | 0.032224 | 0.057667 | -66.7198 | -0.012329 | -66.7552 | 56.2885 | 56.2067 | 56.3901 | -66.8833 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.3717 | 56.2055 | -67.1202 | -0.1322 | -0.048509 | 0.0313 | -0.004062 | 0.12814 | -0.13032 | 0.053123 | -0.36909 | -0.14301 | 0.008293 | -0.030791 | 0.3383 | 0.03475 | -0.13146 | 123.0396 | 122.9578 | 123.1412 | 66.7388 | -123.2203 | 122.9451 | 123.1228 | 122.9566 | 66.7331 | -123.4572
1806.7969 | 123.143 | -66.7694 | 56.282 | -0.0029761 | -0.022957 | 0.00024794 | 0.053508 | -0.0065188 | 0.06293 | 0.030675 | -0.0028393 | -0.00076913 | 0.05739 | 0.032438 | 0.057453 | -66.7381 | -0.012329 | -66.746 | 56.2885 | 56.1975 | 56.3855 | -66.8787 | -66.7382 | -0.013377 | -66.7865 | 56.1894 | 56.3717 | 56.2193 | -67.1156 | -0.10932 | 0.006423 | 0.031297 | 0.023404 | 0.13272 | -0.084543 | 0.10348 | -0.3462 | -0.092655 | 0.031182 | -0.01706 | 0.32914 | 0.089682 | -0.062789 | 123.0579 | 122.9669 | 123.1549 | 66.7571 | -123.1608 | 122.9588 | 123.1411 | 122.9887 | 66.756 | -123.3977
1807.8594 | 123.1979 | -66.7236 | 56.3461 | -0.010607 | -0.022743 | 0.00024794 | 0.053508 | -0.0060916 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.057176 | 0.032224 | 0.057453 | -66.729 | -0.021486 | -66.7506 | 56.293 | 56.2021 | 56.3993 | -66.8741 | -66.7474 | -0.022535 | -66.7819 | 56.1848 | 56.3763 | 56.2147 | -67.1202 | -0.15051 | -0.053086 | -0.005323 | -0.02695 | 0.12356 | -0.14405 | 0.053125 | -0.39656 | -0.16132 | -0.023752 | -0.058257 | 0.3383 | 0.030173 | -0.13146 | 123.0167 | 122.9257 | 123.1229 | 66.7021 | -123.2203 | 122.9084 | 123.0999 | 122.9383 | 66.7011 | -123.4663
1808.7969 | 123.1567 | -66.7328 | 56.3141 | -0.0029761 | -0.022957 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.057176 | 0.032438 | 0.057453 | -66.7244 | -0.012329 | -66.7552 | 56.2885 | 56.1929 | 56.3901 | -66.8741 | -66.752 | -0.022535 | -66.791 | 56.1848 | 56.3717 | 56.1872 | -67.1248 | -0.14136 | -0.025621 | 0.008411 | -0.022373 | 0.11898 | -0.12117 | 0.076011 | -0.39198 | -0.12928 | -0.019175 | -0.058259 | 0.33372 | 0.057638 | -0.12688 | 123.0213 | 122.9257 | 123.1229 | 66.7205 | -123.1882 | 122.9176 | 123.1045 | 122.92 | 66.7103 | -123.4389
1809.7969 | 123.1888 | -66.7465 | 56.3461 | 0.019917 | -0.02253 | 0.00024794 | 0.053722 | -0.0067326 | 0.062076 | 0.0077831 | -0.0028393 | -0.00098273 | 0.057176 | 0.032224 | 0.057667 | -66.729 | -0.007751 | -66.7414 | 56.2885 | 56.1975 | 56.3947 | -66.8787 | -66.7474 | -0.008798 | -66.7773 | 56.1848 | 56.3717 | 56.2101 | -67.1156 | -0.1322 | -0.057664 | 0.017565 | 0.005094 | 0.1373 | -0.14863 | 0.048547 | -0.36909 | -0.16132 | -0.000864 | -0.03079 | 0.3383 | 0.025595 | -0.13603 | 123.035 | 122.944 | 123.1412 | 66.7388 | -123.2249 | 122.9313 | 123.1182 | 122.9566 | 66.7377 | -123.4617
1810.7969 | 123.1338 | -66.7557 | 56.3278 | -0.018238 | -0.022957 | 0.00024794 | 0.053081 | -0.0065188 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.057176 | 0.03201 | 0.057667 | -66.729 | -0.016908 | -66.746 | 56.2885 | 56.2158 | 56.3855 | -66.8787 | -66.7474 | -0.008798 | -66.7773 | 56.194 | 56.3763 | 56.2101 | -67.1156 | -0.12305 | -0.039354 | 0.02672 | 0.009671 | 0.13272 | -0.112 | 0.057699 | -0.35994 | -0.13385 | 0.008291 | -0.021635 | 0.3383 | 0.048483 | -0.11772 | 123.0441 | 122.9715 | 123.1412 | 66.7388 | -123.2065 | 122.9496 | 123.132 | 122.9658 | 66.7469 | -123.4434
1811.8594 | 123.2712 | -66.7236 | 56.2866 | -0.0029761 | -0.022743 | 0.00024794 | 0.053295 | -0.0063052 | 0.06293 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056963 | 0.032224 | 0.057453 | -66.729 | -0.012329 | -66.7597 | 56.2747 | 56.2158 | 56.3855 | -66.8741 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3717 | 56.2284 | -67.1202 | -0.15051 | -0.01189 | -0.005323 | -0.036107 | 0.11441 | -0.070805 | 0.098898 | -0.39656 | -0.097233 | -0.014594 | -0.062836 | 0.33372 | 0.085104 | -0.05821 | 122.9984 | 122.9394 | 123.1092 | 66.7113 | -123.1608 | 122.913 | 123.0954 | 122.952 | 66.7057 | -123.4068
1812.7969 | 123.2208 | -66.7603 | 56.2866 | -0.0029761 | -0.022957 | -0.00017946 | 0.053508 | -0.0063052 | 0.06293 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056963 | 0.032651 | 0.057453 | -66.7335 | -0.016908 | -66.7552 | 56.293 | 56.2021 | 56.3901 | -66.8741 | -66.7474 | -0.008798 | -66.7865 | 56.1894 | 56.3671 | 56.233 | -67.1202 | -0.11389 | 0.006423 | 0.02672 | 0.005093 | 0.11898 | -0.084542 | 0.10348 | -0.35994 | -0.097233 | 0.012869 | -0.026215 | 0.33372 | 0.080525 | -0.053631 | 123.0533 | 122.9623 | 123.1504 | 66.7433 | -123.1608 | 122.9496 | 123.1274 | 122.9932 | 66.7515 | -123.4068
1813.7969 | 123.1979 | -66.7465 | 56.3278 | -0.010607 | -0.022743 | 0.00024794 | 0.053081 | -0.0065188 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056963 | 0.032651 | 0.057453 | -66.7335 | -0.007751 | -66.7506 | 56.2885 | 56.2158 | 56.3993 | -66.8741 | -66.7428 | -0.017956 | -66.7773 | 56.1802 | 56.3717 | 56.2147 | -67.1248 | -0.12762 | -0.039354 | 0.012987 | -0.004062 | 0.12356 | -0.112 | 0.071435 | -0.37825 | -0.14759 | 0.003715 | -0.03079 | 0.34746 | 0.043905 | -0.11315 | 123.035 | 122.9623 | 123.1458 | 66.7388 | -123.202 | 122.9268 | 123.1182 | 122.9612 | 66.7286 | -123.4526
1814.8594 | 123.2529 | -66.7145 | 56.3278 | 0.0046549 | -0.023384 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.03201 | 0.057453 | -66.7244 | -0.016908 | -66.7506 | 56.2885 | 56.2021 | 56.3855 | -66.8741 | -66.7428 | -0.017956 | -66.7773 | 56.1802 | 56.3717 | 56.1826 | -67.1156 | -0.15967 | -0.039354 | -0.009899 | -0.036105 | 0.12356 | -0.12574 | 0.057699 | -0.40114 | -0.14759 | -0.028328 | -0.062833 | 0.3383 | 0.043905 | -0.1452 | 123.0029 | 122.9166 | 123.1 | 66.6976 | -123.202 | 122.8947 | 123.0862 | 122.8971 | 66.6965 | -123.4434
1815.7969 | 123.1934 | -66.7328 | 56.337 | 0.0046549 | -0.02253 | 3.4136e-05 | 0.053508 | -0.0065188 | 0.063144 | 0.00015261 | -0.0028393 | -0.0011965 | 0.057176 | 0.032651 | 0.057453 | -66.7244 | -0.016908 | -66.7552 | 56.2885 | 56.2112 | 56.3947 | -66.8787 | -66.7474 | -0.017956 | -66.7773 | 56.1894 | 56.3717 | 56.2055 | -67.1248 | -0.14594 | -0.048509 | 0.008411 | -0.022373 | 0.12356 | -0.12574 | 0.057702 | -0.39198 | -0.14759 | -0.014597 | -0.044523 | 0.34746 | 0.03475 | -0.13146 | 123.0213 | 122.944 | 123.1275 | 66.7159 | -123.2157 | 122.9222 | 123.1045 | 122.9383 | 66.7148 | -123.4617
1816.7969 | 123.2529 | -66.7191 | 56.2958 | -0.0029761 | -0.022957 | 0.00067514 | 0.053508 | -0.0067326 | 0.06293 | 0.0077831 | -0.0028393 | -0.0011965 | 0.056963 | 0.032651 | 0.057453 | -66.7244 | -0.016908 | -66.746 | 56.2839 | 56.2067 | 56.3993 | -66.8696 | -66.7474 | -0.031692 | -66.7819 | 56.1848 | 56.3763 | 56.2101 | -67.1248 | -0.15051 | -0.011889 | -0.005322 | -0.02695 | 0.12356 | -0.089118 | 0.10348 | -0.40572 | -0.11097 | -0.02833 | -0.062835 | 0.34288 | 0.080527 | -0.085679 | 123.0029 | 122.9257 | 123.1183 | 66.7021 | -123.1653 | 122.9039 | 123.0954 | 122.9292 | 66.6874 | -123.4205
1817.7969 | 123.1934 | -66.7419 | 56.3416 | -0.010607 | -0.022743 | 3.4136e-05 | 0.052867 | -0.0063052 | 0.06293 | -0.0074779 | -0.0028393 | -0.00076913 | 0.057176 | 0.032224 | 0.057667 | -66.729 | -0.016908 | -66.7597 | 56.293 | 56.2067 | 56.3993 | -66.8925 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.3717 | 56.233 | -67.1202 | -0.15052 | -0.048509 | 0.012987 | -0.017797 | 0.13272 | -0.1349 | 0.057702 | -0.37825 | -0.15674 | -0.000863 | -0.039947 | 0.3383 | 0.030172 | -0.10856 | 123.035 | 122.9486 | 123.1412 | 66.725 | -123.234 | 122.9268 | 123.1137 | 122.9749 | 66.724 | -123.4617
1818.7969 | 123.262 | -66.7328 | 56.2683 | 0.0046549 | -0.022957 | 0.00046154 | 0.053295 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056963 | 0.032651 | 0.05724 | -66.729 | -0.007751 | -66.7506 | 56.2839 | 56.2067 | 56.3809 | -66.8696 | -66.7428 | -0.013377 | -66.7819 | 56.194 | 56.3763 | 56.2055 | -67.1202 | -0.13678 | 0.015576 | 0.003832 | -0.017795 | 0.11898 | -0.061653 | 0.11263 | -0.38741 | -0.074344 | -0.010018 | -0.049102 | 0.3383 | 0.10799 | -0.062793 | 123.0167 | 122.9394 | 123.1137 | 66.725 | -123.1379 | 122.9268 | 123.1091 | 122.9383 | 66.7194 | -123.3885
1819.7969 | 123.143 | -66.7603 | 56.3049 | 0.0046549 | -0.022957 | 0.00024794 | 0.053508 | -0.0065188 | 0.06293 | -0.015108 | -0.0026255 | -0.00055553 | 0.056749 | 0.032651 | 0.057453 | -66.7244 | -0.021486 | -66.7414 | 56.2885 | 56.2067 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.7819 | 56.1848 | 56.3671 | 56.2284 | -67.1156 | -0.11847 | -0.016466 | 0.035877 | 0.018827 | 0.1373 | -0.098274 | 0.089745 | -0.35536 | -0.12012 | 0.017448 | -0.021636 | 0.33372 | 0.062214 | -0.076521 | 123.0487 | 122.9669 | 123.1549 | 66.7388 | -123.1837 | 122.9451 | 123.1274 | 122.9887 | 66.7377 | -123.4205
1820.8594 | 123.143 | -66.7374 | 56.3507 | 0.012286 | -0.022957 | 0.00024794 | 0.053295 | -0.0065188 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.05739 | 0.03201 | 0.057453 | -66.7335 | -0.012329 | -66.7414 | 56.2839 | 56.1929 | 56.3901 | -66.8741 | -66.7428 | -0.017956 | -66.7727 | 56.1802 | 56.3717 | 56.2055 | -67.1202 | -0.13678 | -0.066821 | 0.003832 | -0.004061 | 0.13272 | -0.15779 | 0.03939 | -0.38283 | -0.17048 | -0.00544 | -0.035366 | 0.34746 | 0.021017 | -0.14519 | 123.0213 | 122.9303 | 123.1275 | 66.725 | -123.2249 | 122.9176 | 123.1091 | 122.9429 | 66.7194 | -123.4709
1821.7969 | 123.2574 | -66.7282 | 56.3049 | 0.0046549 | -0.02253 | 0.00046154 | 0.053722 | -0.0067326 | 0.062717 | 0.0077831 | -0.0026255 | -0.00098273 | 0.056749 | 0.032438 | 0.05724 | -66.7335 | -0.012329 | -66.7506 | 56.2793 | 56.2067 | 56.3947 | -66.8741 | -66.7474 | -0.027113 | -66.7819 | 56.1848 | 56.3717 | 56.2193 | -67.1202 | -0.14593 | -0.025623 | -0.005324 | -0.022373 | 0.12356 | -0.098274 | 0.089745 | -0.39198 | -0.12012 | -0.019175 | -0.05368 | 0.3383 | 0.066793 | -0.085678 | 123.0075 | 122.9349 | 123.1229 | 66.7159 | -123.1791 | 122.913 | 123.0999 | 122.9475 | 66.7011 | -123.4251
1822.7969 | 123.2666 | -66.6824 | 56.2866 | -0.0029761 | -0.022957 | 0.00024794 | 0.053508 | -0.0060916 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056535 | 0.032438 | 0.05724 | -66.7381 | -0.016908 | -66.7414 | 56.2885 | 56.2067 | 56.3947 | -66.8787 | -66.7382 | -0.017956 | -66.7819 | 56.1894 | 56.3717 | 56.2147 | -67.1156 | -0.19629 | 0.001845 | -0.055678 | -0.058993 | 0.1373 | -0.079963 | 0.10806 | -0.43318 | -0.097233 | -0.055793 | -0.099456 | 0.33372 | 0.085104 | -0.071946 | 122.9709 | 122.8891 | 123.0771 | 66.6655 | -123.1653 | 122.8718 | 123.0542 | 122.8971 | 66.6645 | -123.4022
1823.7969 | 123.1934 | -66.7603 | 56.3507 | 0.012286 | -0.022957 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056749 | 0.032438 | 0.057667 | -66.7244 | -0.016908 | -66.7552 | 56.2839 | 56.2158 | 56.3901 | -66.8833 | -66.7474 | -0.017956 | -66.7865 | 56.194 | 56.3717 | 56.2055 | -67.1248 | -0.12305 | -0.066821 | 0.035877 | 0.005093 | 0.12814 | -0.13489 | 0.03939 | -0.36452 | -0.15674 | 0.012869 | -0.026215 | 0.3383 | 0.021017 | -0.14519 | 123.0441 | 122.9761 | 123.1504 | 66.7433 | -123.234 | 122.9542 | 123.132 | 122.9658 | 66.7423 | -123.4755
1824.7969 | 123.2758 | -66.7236 | 56.282 | 0.0046549 | -0.023384 | 0.00024794 | 0.053508 | -0.0065188 | 0.062289 | -0.0074779 | -0.0028393 | -0.00055553 | 0.05739 | 0.032224 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.2839 | 56.2204 | 56.3947 | -66.8741 | -66.7382 | -0.022535 | -66.7865 | 56.1985 | 56.3763 | 56.2376 | -67.1202 | -0.15051 | 0.001844 | -0.009901 | -0.022372 | 0.12814 | -0.061648 | 0.11263 | -0.39656 | -0.083498 | -0.014594 | -0.062836 | 0.33372 | 0.09426 | -0.044475 | 123.0075 | 122.944 | 123.1183 | 66.7113 | -123.1562 | 122.9222 | 123.0999 | 122.9612 | 66.7011 | -123.4022
1825.8594 | 123.1659 | -66.7465 | 56.3507 | 0.012286 | -0.022957 | 0.00024794 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056963 | 0.032438 | 0.057453 | -66.729 | -0.012329 | -66.746 | 56.2885 | 56.2021 | 56.3993 | -66.8741 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.3809 | 56.2055 | -67.1294 | -0.12762 | -0.062242 | 0.017565 | 0.000516 | 0.12814 | -0.14863 | 0.048547 | -0.38283 | -0.15674 | -0.000864 | -0.035369 | 0.34746 | 0.030174 | -0.14519 | 123.035 | 122.9486 | 123.1458 | 66.7342 | -123.2249 | 122.9405 | 123.1274 | 122.952 | 66.7286 | -123.4801
1826.7969 | 123.2666 | -66.7007 | 56.3095 | -0.010607 | -0.022957 | 3.4136e-05 | 0.053295 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056749 | 0.032438 | 0.057453 | -66.7335 | -0.003172 | -66.7414 | 56.2885 | 56.1975 | 56.3901 | -66.8787 | -66.7428 | -0.017956 | -66.791 | 56.1894 | 56.3717 | 56.2238 | -67.1156 | -0.17798 | -0.021043 | -0.032789 | -0.040682 | 0.1373 | -0.11201 | 0.080589 | -0.41487 | -0.12012 | -0.042061 | -0.090302 | 0.32457 | 0.062216 | -0.085677 | 122.9892 | 122.8982 | 123.0908 | 66.6976 | -123.1882 | 122.8901 | 123.0725 | 122.9246 | 66.6828 | -123.4251
1827.7969 | 123.1293 | -66.7511 | 56.3232 | -0.0029761 | -0.022743 | 0.00024794 | 0.053508 | -0.0065188 | 0.062289 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056749 | 0.032438 | 0.057453 | -66.729 | -0.012329 | -66.7414 | 56.2885 | 56.2021 | 56.3901 | -66.8787 | -66.7382 | -0.022535 | -66.7773 | 56.1894 | 56.3809 | 56.2055 | -67.1248 | -0.12763 | -0.034776 | 0.022143 | 0.009672 | 0.1373 | -0.12116 | 0.066856 | -0.37367 | -0.13385 | 0.012872 | -0.026212 | 0.34746 | 0.05764 | -0.11772 | 123.0396 | 122.9532 | 123.1412 | 66.7388 | -123.202 | 122.9405 | 123.132 | 122.9566 | 66.7286 | -123.448
1828.7969 | 123.262 | -66.7328 | 56.2866 | -0.0029761 | -0.023171 | 0.00067514 | 0.053508 | -0.0069462 | 0.062289 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056535 | 0.032438 | 0.057453 | -66.729 | -0.012329 | -66.746 | 56.2839 | 56.2067 | 56.3855 | -66.8741 | -66.7382 | -0.022535 | -66.7819 | 56.1848 | 56.3809 | 56.2101 | -67.1248 | -0.14136 | -0.002734 | 0.003832 | -0.013217 | 0.12814 | -0.079963 | 0.098898 | -0.39198 | -0.10181 | -0.005439 | -0.049102 | 0.34288 | 0.094261 | -0.076524 | 123.0167 | 122.9394 | 123.1183 | 66.7205 | -123.1608 | 122.9176 | 123.1137 | 122.9429 | 66.7103 | -123.4114
1829.7969 | 123.1476 | -66.7465 | 56.3507 | 0.0046549 | -0.023171 | 0.00046154 | 0.053508 | -0.0060916 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.032651 | 0.057453 | -66.7152 | -0.012329 | -66.7506 | 56.2839 | 56.2067 | 56.3901 | -66.8741 | -66.7428 | -0.013377 | -66.7773 | 56.1848 | 56.3855 | 56.2101 | -67.1248 | -0.12762 | -0.066821 | 0.031301 | -0.004062 | 0.12356 | -0.14405 | 0.03939 | -0.37825 | -0.1659 | 0.003715 | -0.03079 | 0.34746 | 0.034753 | -0.14061 | 123.0304 | 122.9532 | 123.1366 | 66.7342 | -123.2249 | 122.9313 | 123.132 | 122.9566 | 66.7331 | -123.4755
1830.8594 | 123.2391 | -66.7236 | 56.3965 | 0.012286 | -0.022957 | 0.00024794 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056963 | 0.032651 | 0.057453 | -66.729 | -0.012329 | -66.746 | 56.2885 | 56.2204 | 56.3947 | -66.8787 | -66.7382 | -0.013377 | -66.7819 | 56.1894 | 56.3855 | 56.2101 | -67.1202 | -0.15509 | -0.10802 | -0.005323 | -0.022372 | 0.13272 | -0.17609 | -0.001807 | -0.39656 | -0.2071 | -0.014594 | -0.058257 | 0.3383 | -0.011023 | -0.18639 | 123.0121 | 122.944 | 123.1183 | 66.7113 | -123.2752 | 122.913 | 123.1091 | 122.9337 | 66.7103 | -123.5167
1831.7969 | 123.143 | -66.7694 | 56.3187 | -0.0029761 | -0.022957 | 3.4136e-05 | 0.053295 | -0.0063052 | 0.062289 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056749 | 0.032438 | 0.057667 | -66.729 | -0.007751 | -66.7368 | 56.2747 | 56.2021 | 56.3993 | -66.8787 | -66.7336 | -0.022535 | -66.7865 | 56.1894 | 56.3763 | 56.2193 | -67.1156 | -0.10932 | -0.043934 | 0.040453 | 0.032561 | 0.14188 | -0.11659 | 0.08059 | -0.3462 | -0.12928 | 0.03576 | -0.01706 | 0.32914 | 0.057638 | -0.099411 | 123.0441 | 122.9715 | 123.1687 | 66.7617 | -123.1974 | 122.9588 | 123.1457 | 122.9887 | 66.7469 | -123.4343
1832.8594 | 123.2254 | -66.7465 | 56.3416 | 0.0046549 | -0.023171 | 0.00067514 | 0.053722 | -0.0065188 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056963 | 0.032651 | 0.057026 | -66.729 | -0.007751 | -66.746 | 56.2793 | 56.1975 | 56.3947 | -66.8787 | -66.7428 | -0.017956 | -66.7727 | 56.194 | 56.3763 | 56.2147 | -67.1248 | -0.1322 | -0.062244 | 0.017565 | 0.000516 | 0.13272 | -0.14405 | 0.053124 | -0.37825 | -0.14759 | 0.003715 | -0.026211 | 0.35204 | 0.03475 | -0.12688 | 123.0258 | 122.944 | 123.1412 | 66.7388 | -123.2203 | 122.9405 | 123.1228 | 122.9612 | 66.7286 | -123.4663
1833.7969 | 123.1659 | -66.7511 | 56.3004 | 0.012286 | -0.022957 | 0.00024794 | 0.053508 | -0.0065188 | 0.062076 | 0.015414 | -0.0028393 | -0.00098273 | 0.056963 | 0.032224 | 0.057453 | -66.729 | -0.007751 | -66.7414 | 56.2885 | 56.2021 | 56.3947 | -66.8787 | -66.7382 | -0.017956 | -66.7819 | 56.1848 | 56.3717 | 56.2101 | -67.1156 | -0.12763 | -0.011888 | 0.022143 | 0.009672 | 0.1373 | -0.098275 | 0.094323 | -0.36451 | -0.11554 | 0.012872 | -0.030791 | 0.33372 | 0.071371 | -0.090257 | 123.0396 | 122.9532 | 123.1458 | 66.7433 | -123.1791 | 122.9359 | 123.1228 | 122.9612 | 66.7331 | -123.416
1834.8594 | 123.1338 | -66.7328 | 56.3599 | 0.019917 | -0.02253 | 0.00046154 | 0.053295 | -0.0065188 | 0.062503 | -0.0074779 | -0.0024119 | -0.00076913 | 0.056749 | 0.032438 | 0.057026 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.2021 | 56.3993 | -66.8787 | -66.7428 | -0.017956 | -66.7865 | 56.194 | 56.3763 | 56.2101 | -67.1248 | -0.14594 | -0.075976 | 0.003832 | -0.00406 | 0.14188 | -0.15778 | 0.039392 | -0.39198 | -0.1659 | -0.010018 | -0.053681 | 0.3383 | 0.01644 | -0.14977 | 123.0167 | 122.9349 | 123.132 | 66.7205 | -123.2386 | 122.9268 | 123.1091 | 122.9429 | 66.7148 | -123.4846
1835.7969 | 123.1201 | -66.7694 | 56.3141 | -0.0029761 | -0.022957 | 0.00046154 | 0.053508 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056749 | 0.032438 | 0.05724 | -66.7244 | -0.012329 | -66.7414 | 56.2885 | 56.2112 | 56.3947 | -66.8741 | -66.7382 | -0.017956 | -66.7819 | 56.1894 | 56.3717 | 56.2055 | -67.1156 | -0.10474 | -0.025621 | 0.045032 | 0.027982 | 0.13272 | -0.10285 | 0.08059 | -0.3462 | -0.1247 | 0.031182 | -0.012481 | 0.33372 | 0.057638 | -0.10857 | 123.0579 | 122.9806 | 123.1641 | 66.7571 | -123.1882 | 122.9588 | 123.1411 | 122.9749 | 66.7515 | -123.4297
1836.7969 | 123.2162 | -66.7557 | 56.2866 | 0.0046549 | -0.023171 | 0.00024794 | 0.053295 | -0.0063052 | 0.062289 | -0.0074779 | -0.0024119 | -0.00098273 | 0.056749 | 0.032651 | 0.057026 | -66.7244 | -0.007751 | -66.7368 | 56.293 | 56.2067 | 56.3993 | -66.8879 | -66.7291 | -0.013377 | -66.7819 | 56.1894 | 56.3763 | 56.233 | -67.1202 | -0.13221 | 0.006423 | 0.031299 | 0.018828 | 0.15103 | -0.079963 | 0.11263 | -0.36452 | -0.097233 | 0.026606 | -0.026214 | 0.3383 | 0.089682 | -0.053631 | 123.0487 | 122.9623 | 123.1549 | 66.7479 | -123.1745 | 122.9451 | 123.132 | 122.9887 | 66.7423 | -123.4068
1837.7969 | 123.1613 | -66.7603 | 56.337 | 0.0046549 | -0.022957 | 0.00024794 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.032438 | 0.057026 | -66.7152 | -0.007751 | -66.7323 | 56.2839 | 56.2112 | 56.3947 | -66.8833 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.3671 | 56.2101 | -67.111 | -0.12305 | -0.053088 | 0.045034 | 0.027984 | 0.15103 | -0.12574 | 0.057702 | -0.35078 | -0.14759 | 0.022027 | -0.017057 | 0.33372 | 0.030171 | -0.12688 | 123.0441 | 122.9715 | 123.1549 | 66.7525 | -123.2203 | 122.9496 | 123.1274 | 122.9704 | 66.7469 | -123.448
1838.7969 | 123.2391 | -66.7465 | 56.2637 | -0.018238 | -0.023384 | 0.00046154 | 0.053295 | -0.0063052 | 0.062289 | 0.0077831 | -0.0024119 | -0.00055553 | 0.056535 | 0.032438 | 0.05724 | -66.729 | -0.012329 | -66.7368 | 56.2793 | 56.2067 | 56.3947 | -66.8741 | -66.7336 | -0.022535 | -66.7819 | 56.1894 | 56.3809 | 56.2009 | -67.1248 | -0.12762 | 0.015576 | 0.017565 | 0.009673 | 0.1373 | -0.057075 | 0.13094 | -0.37825 | -0.074345 | 0.012872 | -0.035369 | 0.34288 | 0.11715 | -0.062794 | 123.0258 | 122.9532 | 123.1412 | 66.7342 | -123.1379 | 122.9359 | 123.1274 | 122.9475 | 66.724 | -123.3885
1839.8594 | 123.2483 | -66.7282 | 56.3187 | -0.010607 | -0.022957 | 0.00024794 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.056963 | 0.032865 | 0.057667 | -66.7335 | -0.021486 | -66.7414 | 56.2839 | 56.2112 | 56.3947 | -66.8787 | -66.7336 | -0.022535 | -66.7819 | 56.1894 | 56.3763 | 56.1826 | -67.1202 | -0.15051 | -0.034778 | -0.005324 | -0.013217 | 0.1373 | -0.10743 | 0.076012 | -0.39198 | -0.12928 | -0.005439 | -0.05368 | 0.3383 | 0.057638 | -0.13604 | 123.0121 | 122.9394 | 123.1229 | 66.7067 | -123.1974 | 122.9176 | 123.1045 | 122.9108 | 66.7057 | -123.4389
1840.7969 | 123.2574 | -66.7191 | 56.2683 | -0.010607 | -0.023171 | 0.00046154 | 0.053722 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056963 | 0.032651 | 0.05724 | -66.729 | -0.012329 | -66.7368 | 56.2839 | 56.1975 | 56.3947 | -66.8741 | -66.7382 | -0.017956 | -66.7865 | 56.1848 | 56.3717 | 56.1872 | -67.1294 | -0.15509 | 0.015576 | -0.009901 | -0.017793 | 0.1373 | -0.070811 | 0.12637 | -0.4103 | -0.083501 | -0.019172 | -0.067414 | 0.34288 | 0.10341 | -0.081107 | 123.0029 | 122.9166 | 123.1137 | 66.7067 | -123.1425 | 122.9039 | 123.0908 | 122.9063 | 66.7011 | -123.3977
1841.8438 | 123.2025 | -66.7465 | 56.3782 | 0.0046549 | -0.022957 | 3.4136e-05 | 0.053295 | -0.0063052 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.032438 | 0.05724 | -66.7244 | -0.012329 | -66.7368 | 56.2885 | 56.1975 | 56.3993 | -66.8833 | -66.7382 | -0.022535 | -66.7865 | 56.1894 | 56.3717 | 56.2147 | -67.1248 | -0.13678 | -0.089708 | 0.022144 | 0.009673 | 0.14646 | -0.18067 | 0.021081 | -0.37825 | -0.18879 | 0.008294 | -0.039948 | 0.3383 | -0.006449 | -0.1635 | 123.035 | 122.944 | 123.1458 | 66.7342 | -123.2615 | 122.9359 | 123.1182 | 122.9612 | 66.724 | -123.5029
1842.7969 | 123.2574 | -66.7282 | 56.2592 | -0.0029761 | -0.022957 | 0.00024794 | 0.053295 | -0.0063052 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056749 | 0.032651 | 0.05724 | -66.7335 | -0.012329 | -66.7414 | 56.2885 | 56.2112 | 56.3947 | -66.8741 | -66.7291 | -0.017956 | -66.7865 | 56.194 | 56.3671 | 56.2147 | -67.1202 | -0.14593 | 0.029311 | -0.005324 | -0.013217 | 0.13272 | -0.047918 | 0.13552 | -0.39198 | -0.065188 | -0.00086 | -0.058259 | 0.33372 | 0.10799 | -0.04448 | 123.0167 | 122.9394 | 123.1229 | 66.7159 | -123.1333 | 122.9222 | 123.0954 | 122.9429 | 66.7103 | -123.3793
1843.7969 | 123.1613 | -66.7511 | 56.3095 | 0.0046549 | -0.023171 | 3.4136e-05 | 0.053081 | -0.0063052 | 0.062503 | 0.0077831 | -0.0026255 | -0.00076913 | 0.056535 | 0.032651 | 0.057453 | -66.7335 | -0.007751 | -66.746 | 56.2885 | 56.2067 | 56.3993 | -66.8879 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3809 | 56.2101 | -67.1156 | -0.13678 | -0.021043 | 0.017565 | 0.005094 | 0.14188 | -0.10285 | 0.089746 | -0.36451 | -0.12012 | 0.012872 | -0.03537 | 0.32914 | 0.071373 | -0.099412 | 123.0396 | 122.9578 | 123.1504 | 66.7433 | -123.1974 | 122.9405 | 123.132 | 122.9612 | 66.7331 | -123.4251
1844.7969 | 123.2574 | -66.7282 | 56.2775 | -0.010607 | -0.022957 | 0.00067514 | 0.053508 | -0.0063052 | 0.062717 | -0.015108 | -0.0026255 | -0.00055553 | 0.056963 | 0.032651 | 0.057026 | -66.7244 | -0.016908 | -66.7323 | 56.2839 | 56.2112 | 56.3947 | -66.8696 | -66.752 | -0.017956 | -66.7865 | 56.1894 | 56.3809 | 56.2009 | -67.1294 | -0.14136 | 0.006421 | 0.003833 | -0.00406 | 0.1373 | -0.066229 | 0.11721 | -0.40114 | -0.088078 | -0.023753 | -0.058259 | 0.34288 | 0.10342 | -0.076527 | 123.0121 | 122.9394 | 123.1229 | 66.7113 | -123.147 | 122.9176 | 123.1091 | 122.9291 | 66.7103 | -123.4068
1845.7969 | 123.1384 | -66.7603 | 56.3416 | 0.0046549 | -0.023171 | 0.00046154 | 0.053722 | -0.0065188 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056963 | 0.032438 | 0.05724 | -66.729 | -0.007751 | -66.7368 | 56.2839 | 56.2112 | 56.3993 | -66.8787 | -66.7382 | -0.008798 | -66.7819 | 56.1894 | 56.3717 | 56.2055 | -67.1248 | -0.11847 | -0.057666 | 0.031298 | 0.023406 | 0.14188 | -0.13032 | 0.057702 | -0.36452 | -0.15216 | 0.022027 | -0.021636 | 0.34288 | 0.030172 | -0.13603 | 123.0441 | 122.9715 | 123.1595 | 66.7525 | -123.2203 | 122.9496 | 123.132 | 122.9658 | 66.7515 | -123.4663
1846.8594 | 123.2208 | -66.7328 | 56.3232 | -0.010607 | -0.022957 | 3.4136e-05 | 0.053722 | -0.0065188 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057176 | 0.032651 | 0.05724 | -66.729 | -0.021486 | -66.7414 | 56.2839 | 56.2067 | 56.3947 | -66.8696 | -66.7428 | -0.022535 | -66.7773 | 56.1848 | 56.3809 | 56.2055 | -67.1248 | -0.13678 | -0.039355 | 0.003832 | -0.008639 | 0.12814 | -0.11658 | 0.071435 | -0.39198 | -0.13843 | -0.010018 | -0.044523 | 0.34746 | 0.05764 | -0.11772 | 123.0167 | 122.9394 | 123.1275 | 66.7113 | -123.1928 | 122.9176 | 123.1137 | 122.9383 | 66.7103 | -123.448
1847.7969 | 123.1293 | -66.7511 | 56.3278 | -0.010607 | -0.023171 | 0.00046154 | 0.053081 | -0.0063052 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.033079 | 0.05724 | -66.7244 | -0.003172 | -66.7414 | 56.2885 | 56.2021 | 56.3947 | -66.8741 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3809 | 56.2009 | -67.1248 | -0.12305 | -0.039354 | 0.026722 | 0.009672 | 0.13272 | -0.12574 | 0.066857 | -0.37367 | -0.13843 | 0.012872 | -0.03537 | 0.3383 | 0.053062 | -0.12688 | 123.0396 | 122.9532 | 123.1458 | 66.7479 | -123.202 | 122.9405 | 123.132 | 122.952 | 66.7331 | -123.4526
1848.7969 | 123.2986 | -66.7374 | 56.2729 | 0.0046549 | -0.023171 | 0.00067514 | 0.053722 | -0.0065188 | 0.062717 | 0.0077831 | -0.0028393 | -0.00098273 | 0.056963 | 0.032438 | 0.057453 | -66.729 | -0.012329 | -66.7323 | 56.2885 | 56.2067 | 56.3947 | -66.8787 | -66.7382 | -0.022535 | -66.7865 | 56.194 | 56.3763 | 56.1964 | -67.1156 | -0.14136 | 0.015578 | 0.00841 | 0.005096 | 0.14645 | -0.06623 | 0.12179 | -0.37825 | -0.078921 | -0.000861 | -0.049103 | 0.32914 | 0.10341 | -0.076527 | 123.0258 | 122.944 | 123.132 | 66.725 | -123.1516 | 122.9313 | 123.1137 | 122.9337 | 66.7148 | -123.3885
1849.8594 | 123.175 | -66.6962 | 56.3644 | -0.0029761 | -0.022957 | 0.00046154 | 0.053508 | -0.0063052 | 0.062503 | 0.015414 | -0.0024119 | -0.00055553 | 0.056963 | 0.032865 | 0.05724 | -66.729 | -0.021486 | -66.746 | 56.2839 | 56.2021 | 56.3947 | -66.8741 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.3717 | 56.1964 | -67.1248 | -0.17798 | -0.080554 | -0.032789 | -0.049838 | 0.12814 | -0.16236 | 0.030236 | -0.4286 | -0.17505 | -0.04206 | -0.081144 | 0.34746 | 0.007284 | -0.16808 | 122.9801 | 122.8982 | 123.0908 | 66.6747 | -123.2386 | 122.8856 | 123.0679 | 122.8925 | 66.6828 | -123.4892
1850.7969 | 123.2162 | -66.7557 | 56.3141 | -0.0029761 | -0.023384 | 0.00024794 | 0.053508 | -0.0065188 | 0.062503 | 0.015414 | -0.0028393 | -0.00076913 | 0.056963 | 0.032865 | 0.057453 | -66.7244 | -0.007751 | -66.7506 | 56.293 | 56.2067 | 56.3947 | -66.8696 | -66.7382 | -0.022535 | -66.7819 | 56.1894 | 56.3763 | 56.2055 | -67.1248 | -0.11389 | -0.021043 | 0.031299 | 0.005093 | 0.11898 | -0.10743 | 0.08059 | -0.3691 | -0.1247 | 0.017449 | -0.026214 | 0.34288 | 0.062216 | -0.10857 | 123.0487 | 122.9623 | 123.1504 | 66.7479 | -123.1837 | 122.9451 | 123.132 | 122.9612 | 66.7331 | -123.4389
1851.7969 | 123.1247 | -66.7786 | 56.3507 | 0.0046549 | -0.023171 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062076 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056749 | 0.032651 | 0.05724 | -66.7244 | -0.012329 | -66.746 | 56.2885 | 56.2204 | 56.3993 | -66.8741 | -66.7382 | -0.017956 | -66.7956 | 56.1894 | 56.3763 | 56.2009 | -67.1202 | -0.095581 | -0.062242 | 0.054187 | 0.032559 | 0.12814 | -0.13031 | 0.048547 | -0.34163 | -0.16132 | 0.040337 | -0.017062 | 0.32457 | 0.025595 | -0.14977 | 123.067 | 122.999 | 123.1778 | 66.7662 | -123.2249 | 122.968 | 123.1549 | 122.9795 | 66.7606 | -123.4709
1852.7969 | 123.2712 | -66.7099 | 56.3095 | 0.0046549 | -0.022957 | 0.00046154 | 0.053295 | -0.0065188 | 0.062717 | -0.015108 | -0.0028393 | -0.00098273 | 0.056749 | 0.032651 | 0.057453 | -66.7244 | -0.016908 | -66.7414 | 56.2885 | 56.2112 | 56.3901 | -66.8741 | -66.7382 | -0.017956 | -66.7865 | 56.194 | 56.3809 | 56.1964 | -67.1202 | -0.16424 | -0.021043 | -0.014477 | -0.031527 | 0.13272 | -0.098272 | 0.080589 | -0.41029 | -0.11554 | -0.028327 | -0.076569 | 0.33372 | 0.071373 | -0.11315 | 122.9984 | 122.9211 | 123.1 | 66.693 | -123.1837 | 122.9039 | 123.0908 | 122.9063 | 66.6919 | -123.4297
1853.7969 | 123.1567 | -66.7648 | 56.3507 | -0.0029761 | -0.023171 | 0.00024794 | 0.053508 | -0.0067326 | 0.062503 | 0.015414 | -0.0028393 | -0.00055553 | 0.057176 | 0.032651 | 0.057453 | -66.729 | -0.016908 | -66.7506 | 56.2793 | 56.2112 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.7819 | 56.1894 | 56.3809 | 56.2147 | -67.1248 | -0.11389 | -0.071399 | 0.035876 | 0.014249 | 0.12814 | -0.13947 | 0.043969 | -0.35994 | -0.16132 | 0.022026 | -0.017058 | 0.34288 | 0.030174 | -0.13603 | 123.0441 | 122.9761 | 123.1595 | 66.7479 | -123.2294 | 122.9542 | 123.1457 | 122.9795 | 66.7423 | -123.4755
1854.8594 | 123.1796 | -66.7465 | 56.3324 | -0.010607 | -0.022957 | 3.4136e-05 | 0.053508 | -0.0065188 | 0.062717 | 0.00015261 | -0.0024119 | -0.00055553 | 0.056535 | 0.032865 | 0.05724 | -66.729 | -0.007751 | -66.746 | 56.2839 | 56.1975 | 56.3855 | -66.8741 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.3763 | 56.2147 | -67.1202 | -0.12762 | -0.04851 | 0.017565 | 0.000516 | 0.12814 | -0.1349 | 0.053122 | -0.37367 | -0.13843 | -0.000864 | -0.035369 | 0.3383 | 0.043906 | -0.11772 | 123.0304 | 122.944 | 123.132 | 66.7388 | -123.2065 | 122.9405 | 123.1228 | 122.9612 | 66.7286 | -123.4526
1855.7969 | 123.143 | -66.7603 | 56.2958 | 0.0046549 | -0.023384 | 3.4136e-05 | 0.053081 | -0.0065188 | 0.062503 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056749 | 0.032651 | 0.05724 | -66.7335 | -0.007751 | -66.746 | 56.2839 | 56.2204 | 56.3947 | -66.8696 | -66.7428 | -0.013377 | -66.7956 | 56.194 | 56.3717 | 56.1964 | -67.1248 | -0.10931 | -0.011889 | 0.02672 | 0.014249 | 0.12356 | -0.075381 | 0.098901 | -0.36452 | -0.10181 | 0.017448 | -0.035372 | 0.32914 | 0.075949 | -0.099415 | 123.0441 | 122.9806 | 123.1549 | 66.7525 | -123.1653 | 122.9542 | 123.132 | 122.9566 | 66.7469 | -123.4205
1856.7969 | 123.2803 | -66.7328 | 56.2729 | -0.0029761 | -0.023171 | 0.00046154 | 0.053508 | -0.0063052 | 0.062717 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056749 | 0.032865 | 0.057667 | -66.7335 | -0.012329 | -66.7506 | 56.2885 | 56.2021 | 56.3901 | -66.8787 | -66.7474 | -0.022535 | -66.7956 | 56.194 | 56.3809 | 56.2238 | -67.1248 | -0.14594 | 0.015578 | -0.000746 | -0.017795 | 0.12814 | -0.070809 | 0.11721 | -0.39198 | -0.078921 | -0.014597 | -0.062838 | 0.32914 | 0.10799 | -0.049056 | 123.0213 | 122.9349 | 123.1229 | 66.7205 | -123.1516 | 122.9268 | 123.1137 | 122.9566 | 66.7103 | -123.3977
1857.8438 | 123.1659 | -66.7328 | 56.337 | -0.010607 | -0.023384 | 0.00046154 | 0.053508 | -0.0065188 | 0.06293 | 0.015414 | -0.0026255 | -0.00098273 | 0.056749 | 0.032865 | 0.057453 | -66.7335 | -0.012329 | -66.7552 | 56.293 | 56.2112 | 56.3993 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.194 | 56.3855 | 56.2193 | -67.1294 | -0.14136 | -0.043931 | -0.000746 | -0.022373 | 0.11898 | -0.12574 | 0.06228 | -0.39656 | -0.14301 | -0.010018 | -0.049102 | 0.34746 | 0.048486 | -0.11772 | 123.0258 | 122.944 | 123.132 | 66.7205 | -123.2111 | 122.9268 | 123.1182 | 122.952 | 66.7103 | -123.4663
1858.7969 | 123.2758 | -66.7191 | 56.2729 | -0.010607 | -0.023384 | 0.00024794 | 0.053722 | -0.0065188 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.057176 | 0.033292 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.2885 | 56.2112 | 56.3993 | -66.8787 | -66.7428 | -0.017956 | -66.7819 | 56.1848 | 56.39 | 56.2055 | -67.1294 | -0.15967 | 0.015578 | -0.014479 | -0.02695 | 0.13272 | -0.061651 | 0.12637 | -0.4103 | -0.088078 | -0.023751 | -0.062835 | 0.34746 | 0.11715 | -0.06737 | 123.0075 | 122.9303 | 123.1183 | 66.7067 | -123.1516 | 122.9039 | 123.1091 | 122.9246 | 66.7011 | -123.4022
1859.8594 | 123.1934 | -66.7419 | 56.3278 | -0.0029761 | -0.023171 | 0.00046154 | 0.052867 | -0.0065188 | 0.062503 | 0.0077831 | -0.0026255 | -0.00076913 | 0.056963 | 0.033292 | 0.05724 | -66.7244 | -0.012329 | -66.7506 | 56.2885 | 56.2158 | 56.3993 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.3763 | 56.2009 | -67.1202 | -0.14136 | -0.039354 | 0.017566 | -0.00864 | 0.13272 | -0.112 | 0.071435 | -0.37825 | -0.13385 | -0.005442 | -0.044526 | 0.33372 | 0.048483 | -0.12688 | 123.0304 | 122.9578 | 123.1412 | 66.7296 | -123.2111 | 122.9359 | 123.1182 | 122.9429 | 66.7286 | -123.448
1860.7969 | 123.2437 | -66.7282 | 56.3141 | 0.0046549 | -0.023171 | 0.00046154 | 0.053508 | -0.0065188 | 0.062289 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056749 | 0.032865 | 0.057453 | -66.729 | -0.012329 | -66.7414 | 56.2839 | 56.2158 | 56.4038 | -66.8787 | -66.7336 | -0.017956 | -66.7819 | 56.194 | 56.3809 | 56.1964 | -67.1248 | -0.15051 | -0.0302 | -0.000746 | -0.013217 | 0.1373 | -0.098271 | 0.089747 | -0.39656 | -0.12012 | -0.005439 | -0.05368 | 0.34288 | 0.066795 | -0.11773 | 123.0121 | 122.944 | 123.132 | 66.7159 | -123.1928 | 122.9222 | 123.1091 | 122.9246 | 66.7103 | -123.4389
1861.7969 | 123.23 | -66.7419 | 56.2958 | -0.010607 | -0.023598 | 0.00046154 | 0.053722 | -0.0065188 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056749 | 0.033079 | 0.05724 | -66.729 | -0.016908 | -66.746 | 56.2839 | 56.1975 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.7865 | 56.194 | 56.3763 | 56.2055 | -67.1294 | -0.13678 | -0.011889 | 0.012987 | -0.004062 | 0.13272 | -0.098276 | 0.098901 | -0.38741 | -0.10181 | -0.000863 | -0.044526 | 0.34288 | 0.080527 | -0.090258 | 123.0258 | 122.9394 | 123.1366 | 66.725 | -123.1745 | 122.9359 | 123.1182 | 122.9475 | 66.7194 | -123.4251
1862.8594 | 123.1338 | -66.7694 | 56.3416 | 0.0046549 | -0.022957 | 0.00024794 | 0.053722 | -0.0067326 | 0.06293 | 0.00015261 | -0.0026255 | -0.00076913 | 0.057176 | 0.032865 | 0.057026 | -66.7244 | -0.012329 | -66.7368 | 56.2839 | 56.2021 | 56.3993 | -66.8787 | -66.7382 | -0.013377 | -66.7819 | 56.1802 | 56.3763 | 56.2055 | -67.1294 | -0.10932 | -0.057666 | 0.045032 | 0.032561 | 0.14188 | -0.13947 | 0.057702 | -0.35994 | -0.16132 | 0.031182 | -0.012481 | 0.34746 | 0.03475 | -0.13603 | 123.0533 | 122.9715 | 123.1687 | 66.7571 | -123.2203 | 122.9496 | 123.1457 | 122.9749 | 66.756 | -123.4709
1863.7969 | 123.1384 | -66.7648 | 56.3416 | -0.0029761 | -0.023171 | 0.00024794 | 0.052867 | -0.0065188 | 0.062717 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056322 | 0.033079 | 0.057453 | -66.7335 | -0.016908 | -66.7414 | 56.2885 | 56.2112 | 56.3947 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.3809 | 56.2238 | -67.1202 | -0.10931 | -0.053087 | 0.031298 | 0.023405 | 0.13272 | -0.13032 | 0.053124 | -0.35536 | -0.14759 | 0.022026 | -0.017058 | 0.3383 | 0.039329 | -0.11772 | 123.0533 | 122.9761 | 123.1595 | 66.7479 | -123.2157 | 122.9588 | 123.1457 | 122.9887 | 66.7469 | -123.4617
1864.7969 | 123.2437 | -66.7374 | 56.2637 | -0.010607 | -0.023384 | 0.00024794 | 0.053508 | -0.0063052 | 0.062503 | -0.0074779 | -0.0026255 | -0.00055553 | 0.056535 | 0.032865 | 0.05724 | -66.729 | -0.012329 | -66.746 | 56.293 | 56.2021 | 56.3947 | -66.8741 | -66.7428 | -0.017956 | -66.7819 | 56.1894 | 56.3763 | 56.2284 | -67.1202 | -0.13678 | 0.029311 | 0.00841 | -0.008639 | 0.12814 | -0.061654 | 0.13094 | -0.38283 | -0.074345 | -0.00544 | -0.044524 | 0.3383 | 0.11257 | -0.035322 | 123.0304 | 122.9394 | 123.132 | 66.725 | -123.1379 | 122.9268 | 123.1137 | 122.9658 | 66.7194 | -123.3839
1865.8594 | 123.2071 | -66.7465 | 56.3278 | -0.0029761 | -0.023384 | 0.00024794 | 0.053081 | -0.0060916 | 0.062717 | 0.00015261 | -0.0026255 | -0.0011965 | 0.056963 | 0.032651 | 0.05724 | -66.7244 | -0.007751 | -66.7368 | 56.2976 | 56.2067 | 56.3947 | -66.8833 | -66.7428 | -0.022535 | -66.7773 | 56.1894 | 56.3763 | 56.2193 | -67.1248 | -0.13678 | -0.030197 | 0.022144 | 0.009673 | 0.14646 | -0.12116 | 0.066857 | -0.37825 | -0.13843 | 0.003715 | -0.03079 | 0.34746 | 0.048483 | -0.10857 | 123.0441 | 122.9532 | 123.1412 | 66.7388 | -123.2111 | 122.9359 | 123.1228 | 122.9658 | 66.724 | -123.4526
1866.7969 | 123.2162 | -66.7282 | 56.282 | -0.018238 | -0.023384 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.032865 | 0.057026 | -66.7244 | -0.016908 | -66.7414 | 56.2885 | 56.1883 | 56.3993 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.194 | 56.3763 | 56.2147 | -67.1248 | -0.15509 | 0.006423 | 0.003833 | -0.013217 | 0.14188 | -0.093701 | 0.11721 | -0.39656 | -0.088076 | -0.014596 | -0.058259 | 0.3383 | 0.09426 | -0.067368 | 123.0167 | 122.9166 | 123.1275 | 66.7113 | -123.1653 | 122.9222 | 123.1045 | 122.9429 | 66.7103 | -123.4068
1867.7969 | 123.3582 | -66.7465 | 56.2912 | -0.0029761 | -0.023598 | 0.00046154 | 0.053508 | -0.0065188 | 0.062717 | -0.015108 | -0.0028393 | -0.00034193 | 0.056749 | 0.032865 | 0.057453 | -66.729 | -0.012329 | -66.746 | 56.2839 | 56.2021 | 56.3901 | -66.8787 | -66.7428 | -0.013377 | -66.7773 | 56.194 | 56.3809 | 56.233 | -67.1202 | -0.1322 | -0.007312 | 0.017565 | 0.000516 | 0.13272 | -0.08912 | 0.098899 | -0.37367 | -0.097232 | 0.003715 | -0.03079 | 0.34288 | 0.089683 | -0.058209 | 123.0304 | 122.9486 | 123.1366 | 66.7342 | -123.1699 | 122.9405 | 123.1274 | 122.9795 | 66.7331 | -123.4114
1868.8594 | 123.2666 | -66.6962 | 56.282 | -0.010607 | -0.023598 | 0.00046154 | 0.053722 | -0.0065188 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056963 | 0.032651 | 0.057667 | -66.7198 | -0.007751 | -66.7368 | 56.2885 | 56.2067 | 56.3947 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.3763 | 56.2193 | -67.1156 | -0.18256 | 0.006423 | -0.023632 | -0.040681 | 0.14188 | -0.075385 | 0.11263 | -0.41945 | -0.088076 | -0.051218 | -0.085723 | 0.33372 | 0.09426 | -0.062789 | 122.9846 | 122.9028 | 123.0908 | 66.6884 | -123.1608 | 122.8901 | 123.0725 | 122.9154 | 66.6782 | -123.3977
1869.7969 | 123.2666 | -66.7374 | 56.282 | -0.010607 | -0.023384 | 0.00024794 | 0.053722 | -0.0067326 | 0.062717 | -0.0074779 | -0.0028393 | -0.00098273 | 0.056322 | 0.032865 | 0.05724 | -66.7244 | -0.012329 | -66.7506 | 56.2885 | 56.2112 | 56.3993 | -66.8787 | -66.7474 | -0.008798 | -66.7819 | 56.1894 | 56.3809 | 56.2193 | -67.1339 | -0.14136 | 0.006423 | 0.012989 | -0.013217 | 0.12814 | -0.070806 | 0.11721 | -0.39656 | -0.092655 | -0.010019 | -0.044524 | 0.35204 | 0.098839 | -0.062789 | 123.0258 | 122.9486 | 123.1366 | 66.725 | -123.1608 | 122.9268 | 123.1182 | 122.9566 | 66.7286 | -123.416
1870.7969 | 123.2437 | -66.7099 | 56.3141 | 0.0046549 | -0.023598 | 0.00046154 | 0.053508 | -0.0065188 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.056963 | 0.032865 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.293 | 56.2112 | 56.3947 | -66.8741 | -66.7474 | -0.022535 | -66.791 | 56.1985 | 56.3763 | 56.2101 | -67.1248 | -0.16424 | -0.021043 | -0.023634 | -0.036105 | 0.12814 | -0.10285 | 0.08059 | -0.41487 | -0.11554 | -0.037485 | -0.081147 | 0.33372 | 0.062216 | -0.10399 | 123.0029 | 122.9211 | 123.1046 | 66.6976 | -123.1882 | 122.9084 | 123.0862 | 122.92 | 66.6874 | -123.4389
1871.7969 | 123.2574 | -66.7145 | 56.3278 | -0.0029761 | -0.023812 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062717 | -0.0074779 | -0.0028393 | -0.00076913 | 0.056535 | 0.032865 | 0.057026 | -66.729 | -0.007751 | -66.7506 | 56.2885 | 56.1975 | 56.3993 | -66.8787 | -66.7382 | -0.017956 | -66.7865 | 56.194 | 56.3809 | 56.2193 | -67.1248 | -0.16425 | -0.039354 | -0.014478 | -0.036105 | 0.12814 | -0.13032 | 0.071435 | -0.41029 | -0.13385 | -0.023749 | -0.071991 | 0.3383 | 0.053062 | -0.10857 | 123.0029 | 122.912 | 123.1137 | 66.7067 | -123.2065 | 122.9084 | 123.0954 | 122.9337 | 66.6965 | -123.4526
1872.7969 | 123.2437 | -66.7282 | 56.3278 | 0.0046549 | -0.023812 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062717 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056749 | 0.032865 | 0.057453 | -66.7244 | -0.012329 | -66.7506 | 56.2885 | 56.2112 | 56.3947 | -66.8833 | -66.7474 | -0.022535 | -66.7819 | 56.1848 | 56.3717 | 56.1964 | -67.1294 | -0.15509 | -0.039354 | 0.003833 | -0.022373 | 0.13272 | -0.11658 | 0.066857 | -0.40114 | -0.14301 | -0.019175 | -0.05368 | 0.34746 | 0.043905 | -0.13146 | 123.0167 | 122.9394 | 123.1229 | 66.7159 | -123.2111 | 122.913 | 123.0999 | 122.9246 | 66.7057 | -123.4572
1873.8594 | 123.1796 | -66.7191 | 56.369 | -0.0029761 | -0.023384 | 3.4136e-05 | 0.053722 | -0.0065188 | 0.062717 | 0.0077831 | -0.0024119 | -0.00055553 | 0.056749 | 0.032865 | 0.05724 | -66.729 | -0.016908 | -66.7552 | 56.293 | 56.2112 | 56.3993 | -66.8879 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.3855 | 56.233 | -67.1294 | -0.16883 | -0.075975 | -0.009901 | -0.036106 | 0.13272 | -0.15778 | 0.030236 | -0.4103 | -0.17963 | -0.019172 | -0.058256 | 0.35204 | 0.016442 | -0.13603 | 123.0121 | 122.9303 | 123.1183 | 66.7021 | -123.2569 | 122.9084 | 123.1045 | 122.952 | 66.7057 | -123.4984
1874.7969 | 123.262 | -66.7053 | 56.3324 | 0.0046549 | -0.023812 | 0.00024794 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056963 | 0.032651 | 0.05724 | -66.729 | -0.016908 | -66.7414 | 56.2839 | 56.2112 | 56.4038 | -66.8787 | -66.7382 | -0.017956 | -66.7865 | 56.1848 | 56.3809 | 56.2376 | -67.1248 | -0.1734 | -0.04851 | -0.023634 | -0.036105 | 0.1373 | -0.12116 | 0.071437 | -0.41945 | -0.14759 | -0.032905 | -0.081147 | 0.3383 | 0.048485 | -0.094829 | 122.9892 | 122.9166 | 123.1092 | 66.6884 | -123.2111 | 122.8901 | 123.0862 | 122.9429 | 66.6874 | -123.4572
1875.8594 | 123.2071 | -66.7328 | 56.337 | -0.0029761 | -0.023171 | 0.00024794 | 0.053295 | -0.0065188 | 0.062289 | 0.00015261 | -0.0026255 | -0.00034193 | 0.056963 | 0.033079 | 0.05724 | -66.729 | -0.016908 | -66.7368 | 56.2839 | 56.2158 | 56.4038 | -66.8787 | -66.7382 | -0.017956 | -66.7773 | 56.1894 | 56.3763 | 56.2055 | -67.1248 | -0.14594 | -0.053088 | 0.003832 | -0.00406 | 0.14188 | -0.12116 | 0.066859 | -0.39198 | -0.14759 | -0.005439 | -0.044523 | 0.34746 | 0.039328 | -0.13146 | 123.0167 | 122.9486 | 123.1366 | 66.7159 | -123.2157 | 122.9222 | 123.1091 | 122.9383 | 66.7148 | -123.4617
1876.7969 | 123.2986 | -66.7053 | 56.3141 | 0.0046549 | -0.023171 | 0.00046154 | 0.053295 | -0.0069462 | 0.062289 | 0.015414 | -0.0030529 | -0.00055553 | 0.056749 | 0.033079 | 0.05724 | -66.7244 | -0.007751 | -66.7368 | 56.2885 | 56.2067 | 56.3993 | -66.8787 | -66.7428 | -0.017956 | -66.791 | 56.1985 | 56.39 | 56.2147 | -67.1294 | -0.1734 | -0.025621 | -0.019055 | -0.031526 | 0.14188 | -0.10743 | 0.085168 | -0.42403 | -0.11554 | -0.037484 | -0.085725 | 0.3383 | 0.075952 | -0.099412 | 122.9938 | 122.912 | 123.1046 | 66.6976 | -123.1928 | 122.9039 | 123.0954 | 122.92 | 66.6874 | -123.4434
1877.7969 | 123.2941 | -66.687 | 56.2729 | -0.0029761 | -0.023598 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062076 | -0.0074779 | -0.0024119 | -0.00055553 | 0.057176 | 0.032865 | 0.057026 | -66.729 | -0.003172 | -66.746 | 56.2839 | 56.2067 | 56.3947 | -66.8833 | -66.7336 | -0.017956 | -66.7865 | 56.1894 | 56.3809 | 56.2055 | -67.1339 | -0.19629 | 0.010999 | -0.041944 | -0.058993 | 0.1373 | -0.06623 | 0.12179 | -0.44692 | -0.0835 | -0.046637 | -0.099457 | 0.34746 | 0.10799 | -0.06737 | 122.9709 | 122.8937 | 123.0817 | 66.6838 | -123.1562 | 122.8764 | 123.0679 | 122.8925 | 66.6691 | -123.4068
1878.7969 | 123.2574 | -66.7191 | 56.3095 | -0.0029761 | -0.023384 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.057176 | 0.032865 | 0.057453 | -66.7244 | -0.003172 | -66.7323 | 56.2885 | 56.2112 | 56.3993 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3809 | 56.2147 | -67.1294 | -0.16425 | -0.021043 | -0.005322 | -0.013215 | 0.15103 | -0.098272 | 0.089746 | -0.4103 | -0.12012 | -0.02833 | -0.062835 | 0.34746 | 0.071373 | -0.094834 | 123.0075 | 122.9303 | 123.1183 | 66.7159 | -123.1928 | 122.9084 | 123.0999 | 122.9337 | 66.7011 | -123.4389
1879.7969 | 123.2346 | -66.7145 | 56.3232 | -0.0029761 | -0.023812 | 0.00024794 | 0.053508 | -0.0065188 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056535 | 0.033292 | 0.05724 | -66.7198 | -0.016908 | -66.7414 | 56.2747 | 56.1929 | 56.3993 | -66.8696 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3809 | 56.2055 | -67.1248 | -0.15509 | -0.048511 | -0.005321 | -0.026949 | 0.12814 | -0.13032 | 0.076013 | -0.41029 | -0.13385 | -0.032907 | -0.067412 | 0.34288 | 0.05764 | -0.11772 | 122.9892 | 122.9074 | 123.1137 | 66.6976 | -123.1928 | 122.9039 | 123.0954 | 122.92 | 66.6965 | -123.448
1880.7969 | 123.3902 | -66.6916 | 56.369 | 0.012286 | -0.023812 | 0.00046154 | 0.053295 | -0.0069462 | 0.062289 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056963 | 0.033079 | 0.057026 | -66.7335 | -0.012329 | -66.7414 | 56.2793 | 56.2204 | 56.3993 | -66.8741 | -66.7428 | -0.027113 | -66.7773 | 56.1894 | 56.3809 | 56.2147 | -67.1294 | -0.18256 | -0.08971 | -0.041945 | -0.049838 | 0.13272 | -0.14862 | 0.030236 | -0.43776 | -0.17963 | -0.051217 | -0.085722 | 0.35204 | 0.011863 | -0.15434 | 122.9709 | 122.912 | 123.0908 | 66.6793 | -123.2432 | 122.881 | 123.0725 | 122.9063 | 66.6645 | -123.4984
1881.7969 | 123.2208 | -66.7145 | 56.3507 | -0.018238 | -0.023598 | 0.00046154 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056963 | 0.033079 | 0.05724 | -66.729 | -0.012329 | -66.7368 | 56.2885 | 56.2021 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.7865 | 56.194 | 56.3855 | 56.2055 | -67.1248 | -0.16425 | -0.062242 | -0.014478 | -0.02237 | 0.14188 | -0.14863 | 0.043969 | -0.41029 | -0.15674 | -0.028328 | -0.071991 | 0.3383 | 0.034753 | -0.14519 | 123.0029 | 122.9166 | 123.1092 | 66.7021 | -123.2294 | 122.9084 | 123.0999 | 122.92 | 66.6919 | -123.4755
1882.7969 | 123.262 | -66.7191 | 56.3095 | 0.012286 | -0.023598 | 0.00024794 | 0.053295 | -0.0067326 | 0.062717 | 0.015414 | -0.0028393 | -0.00034193 | 0.056535 | 0.033079 | 0.057453 | -66.729 | -0.003172 | -66.7414 | 56.293 | 56.2112 | 56.3947 | -66.8833 | -66.7336 | -0.017956 | -66.7773 | 56.194 | 56.3809 | 56.2193 | -67.1248 | -0.16425 | -0.016465 | -0.009901 | -0.022372 | 0.14188 | -0.098272 | 0.085168 | -0.40572 | -0.11554 | -0.014594 | -0.058256 | 0.34746 | 0.071373 | -0.090255 | 123.0121 | 122.9303 | 123.1137 | 66.7159 | -123.1928 | 122.913 | 123.0999 | 122.9383 | 66.7011 | -123.4343
1883.7969 | 123.262 | -66.7099 | 56.3187 | 0.0046549 | -0.023812 | 0.00046154 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056749 | 0.032651 | 0.056599 | -66.7244 | -0.003172 | -66.7368 | 56.293 | 56.2021 | 56.4038 | -66.8787 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.3855 | 56.2009 | -67.1248 | -0.16882 | -0.025621 | -0.014477 | -0.026948 | 0.14188 | -0.11659 | 0.085169 | -0.41487 | -0.12928 | -0.028327 | -0.067411 | 0.34746 | 0.066796 | -0.11773 | 123.0029 | 122.912 | 123.1137 | 66.7067 | -123.1974 | 122.8993 | 123.0954 | 122.9108 | 66.6965 | -123.4434
1884.7969 | 123.2071 | -66.7053 | 56.369 | -0.0029761 | -0.023598 | 0.00046154 | 0.053722 | -0.0065188 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056535 | 0.033292 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.2885 | 56.2067 | 56.3947 | -66.8879 | -66.7474 | -0.027113 | -66.7819 | 56.1894 | 56.3855 | 56.2009 | -67.1248 | -0.18256 | -0.080553 | -0.028212 | -0.040683 | 0.14188 | -0.16236 | 0.025658 | -0.41945 | -0.17963 | -0.042063 | -0.076568 | 0.34288 | 0.016442 | -0.16808 | 122.9938 | 122.912 | 123.1 | 66.693 | -123.2569 | 122.8947 | 123.0908 | 122.9063 | 66.6782 | -123.4938
1885.8594 | 123.2712 | -66.774 | 56.337 | -0.0029761 | -0.023812 | 0.00024794 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0026255 | -0.00055553 | 0.056749 | 0.033079 | 0.057667 | -66.7244 | -0.012329 | -66.7414 | 56.2839 | 56.2204 | 56.3993 | -66.8925 | -66.7474 | -0.008798 | -66.7819 | 56.194 | 56.3809 | 56.2101 | -67.1248 | -0.11847 | -0.053088 | 0.04961 | 0.03256 | 0.15103 | -0.11658 | 0.06228 | -0.35078 | -0.14301 | 0.026602 | -0.007903 | 0.34288 | 0.043907 | -0.12688 | 123.0579 | 122.9944 | 123.1732 | 66.7617 | -123.2294 | 122.968 | 123.1549 | 122.9841 | 66.7652 | -123.4617
1886.7969 | 123.2666 | -66.6962 | 56.3095 | 0.0046549 | -0.023812 | 0.00024794 | 0.053295 | -0.0065188 | 0.062717 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056963 | 0.033079 | 0.057026 | -66.7335 | -0.016908 | -66.746 | 56.2793 | 56.2158 | 56.3947 | -66.8787 | -66.752 | -0.013377 | -66.7819 | 56.1985 | 56.3763 | 56.2009 | -67.1248 | -0.18256 | -0.0302 | -0.037367 | -0.049838 | 0.13272 | -0.093693 | 0.085168 | -0.4286 | -0.11096 | -0.055796 | -0.085723 | 0.34288 | 0.066794 | -0.10857 | 122.9755 | 122.912 | 123.0908 | 66.6793 | -123.1882 | 122.8947 | 123.0725 | 122.8971 | 66.6828 | -123.4343
1887.7969 | 123.2529 | -66.6916 | 56.3232 | -0.010607 | -0.023812 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062289 | 0.0077831 | -0.0024119 | -0.00098273 | 0.056749 | 0.03372 | 0.057026 | -66.7244 | -0.012329 | -66.7414 | 56.293 | 56.2067 | 56.3947 | -66.8696 | -66.7474 | -0.013377 | -66.7819 | 56.1894 | 56.3809 | 56.2009 | -67.1294 | -0.17798 | -0.030198 | -0.032788 | -0.049838 | 0.12814 | -0.11658 | 0.071435 | -0.43776 | -0.13385 | -0.055796 | -0.090301 | 0.34746 | 0.05764 | -0.1223 | 122.9846 | 122.8982 | 123.0863 | 66.6793 | -123.1928 | 122.881 | 123.0725 | 122.8925 | 66.6782 | -123.4526
1888.7969 | 123.23 | -66.7282 | 56.3416 | 0.012286 | -0.023598 | -0.00017946 | 0.053295 | -0.0065188 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056749 | 0.033079 | 0.057026 | -66.7335 | -0.016908 | -66.7414 | 56.2976 | 56.2158 | 56.3993 | -66.8741 | -66.7428 | -0.022535 | -66.7819 | 56.1894 | 56.3809 | 56.2284 | -67.1294 | -0.14593 | -0.04393 | -0.005324 | -0.013217 | 0.13272 | -0.12574 | 0.057702 | -0.40114 | -0.15216 | -0.014596 | -0.05368 | 0.34746 | 0.039329 | -0.11314 | 123.0258 | 122.944 | 123.1275 | 66.7113 | -123.2157 | 122.9176 | 123.1091 | 122.9566 | 66.7057 | -123.4709
1889.7969 | 123.2529 | -66.7053 | 56.337 | -0.0029761 | -0.023598 | 0.00024794 | 0.053722 | -0.0065188 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.056749 | 0.033506 | 0.057026 | -66.7244 | -0.012329 | -66.7552 | 56.2885 | 56.2021 | 56.3993 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.1894 | 56.3809 | 56.2101 | -67.1294 | -0.1734 | -0.048509 | -0.019055 | -0.049839 | 0.12356 | -0.1349 | 0.06228 | -0.42403 | -0.14759 | -0.042063 | -0.076568 | 0.34746 | 0.043907 | -0.12688 | 122.9938 | 122.9074 | 123.1046 | 66.693 | -123.2157 | 122.8947 | 123.0862 | 122.9154 | 66.6919 | -123.4663
1890.7969 | 123.1934 | -66.7099 | 56.3278 | -0.010607 | -0.023812 | 0.00046154 | 0.053081 | -0.0067326 | 0.062717 | 0.015414 | -0.0030529 | -0.00055553 | 0.057176 | 0.033292 | 0.057453 | -66.729 | -0.007751 | -66.7506 | 56.2839 | 56.2204 | 56.3993 | -66.8833 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.39 | 56.1964 | -67.1248 | -0.1734 | -0.043933 | -0.019056 | -0.040683 | 0.13272 | -0.10742 | 0.071435 | -0.41487 | -0.13843 | -0.028327 | -0.067411 | 0.34746 | 0.062219 | -0.13146 | 122.9938 | 122.9303 | 123.1092 | 66.7021 | -123.2111 | 122.8993 | 123.0999 | 122.9063 | 66.6965 | -123.4526
1891.7969 | 123.262 | -66.7053 | 56.3187 | -0.0029761 | -0.024025 | 0.00024794 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056749 | 0.033079 | 0.05724 | -66.7244 | -0.012329 | -66.746 | 56.2885 | 56.2112 | 56.3947 | -66.8787 | -66.7336 | -0.013377 | -66.7865 | 56.1894 | 56.3809 | 56.2055 | -67.1202 | -0.1734 | -0.030199 | -0.019055 | -0.040683 | 0.13272 | -0.10743 | 0.076012 | -0.41487 | -0.12928 | -0.028327 | -0.081147 | 0.33372 | 0.062217 | -0.11315 | 122.9938 | 122.9166 | 123.1 | 66.693 | -123.1974 | 122.8947 | 123.0862 | 122.9108 | 66.6919 | -123.4389
1892.8594 | 123.2254 | -66.7145 | 56.3049 | -0.0029761 | -0.023812 | 3.4136e-05 | 0.053508 | -0.0063052 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.056963 | 0.033079 | 0.05724 | -66.729 | -0.007751 | -66.7506 | 56.2839 | 56.2112 | 56.3947 | -66.8787 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.3855 | 56.2101 | -67.1248 | -0.16425 | -0.021045 | -0.014478 | -0.036105 | 0.12814 | -0.093695 | 0.089745 | -0.41029 | -0.11097 | -0.032907 | -0.071991 | 0.3383 | 0.080529 | -0.094835 | 122.9984 | 122.9257 | 123.1092 | 66.7067 | -123.1837 | 122.9084 | 123.0999 | 122.9246 | 66.7011 | -123.4297
1893.7969 | 123.2574 | -66.7236 | 56.3507 | -0.0029761 | -0.023812 | -0.00017946 | 0.053722 | -0.0065188 | 0.062503 | 0.0077831 | -0.0026255 | -0.00098273 | 0.056749 | 0.033079 | 0.057026 | -66.729 | -0.016908 | -66.7414 | 56.2885 | 56.2112 | 56.3947 | -66.8879 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.39 | 56.2009 | -67.1248 | -0.16425 | -0.062242 | -0.005323 | -0.017794 | 0.14646 | -0.13947 | 0.043969 | -0.40114 | -0.15674 | -0.019173 | -0.058257 | 0.34288 | 0.039331 | -0.14977 | 123.0121 | 122.9349 | 123.1183 | 66.7067 | -123.2386 | 122.9176 | 123.1137 | 122.9246 | 66.7057 | -123.4755
1894.8594 | 123.2208 | -66.7191 | 56.3232 | 0.0046549 | -0.024025 | -0.00017946 | 0.053722 | -0.0067326 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.033506 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.293 | 56.2158 | 56.4038 | -66.8833 | -66.7428 | -0.017956 | -66.791 | 56.1985 | 56.3855 | 56.2101 | -67.1248 | -0.16425 | -0.030198 | -0.014479 | -0.02695 | 0.1373 | -0.10743 | 0.080592 | -0.40572 | -0.1247 | -0.023751 | -0.071992 | 0.33372 | 0.062219 | -0.11315 | 123.0121 | 122.9349 | 123.1229 | 66.7067 | -123.2065 | 122.9176 | 123.1045 | 122.9292 | 66.7011 | -123.448
1895.7969 | 123.3032 | -66.7282 | 56.3278 | -0.0029761 | -0.023812 | 0.00024794 | 0.053508 | -0.0063052 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.056749 | 0.032865 | 0.05724 | -66.7335 | -0.012329 | -66.746 | 56.2885 | 56.2204 | 56.4038 | -66.8696 | -66.7382 | -0.017956 | -66.7773 | 56.1894 | 56.3855 | 56.2009 | -67.1248 | -0.14136 | -0.039354 | -0.005324 | -0.017795 | 0.12356 | -0.10742 | 0.076014 | -0.39656 | -0.13843 | -0.010017 | -0.049101 | 0.34746 | 0.057641 | -0.12688 | 123.0167 | 122.9486 | 123.132 | 66.7159 | -123.1974 | 122.9176 | 123.1137 | 122.9291 | 66.7103 | -123.4526
1896.7969 | 123.1613 | -66.7328 | 56.3553 | -0.0029761 | -0.024239 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062503 | 0.015414 | -0.0028393 | -0.00055553 | 0.056749 | 0.033292 | 0.057667 | -66.7198 | -0.007751 | -66.7506 | 56.2885 | 56.2158 | 56.3993 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3809 | 56.2009 | -67.1248 | -0.14594 | -0.06682 | 0.012989 | -0.017795 | 0.12814 | -0.13947 | 0.043969 | -0.39198 | -0.1659 | -0.014597 | -0.049102 | 0.34288 | 0.025596 | -0.15435 | 123.0213 | 122.9486 | 123.132 | 66.725 | -123.234 | 122.9222 | 123.1137 | 122.9337 | 66.7148 | -123.4801
1897.7969 | 123.317 | -66.6824 | 56.3049 | 0.0046549 | -0.024239 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056535 | 0.033292 | 0.057026 | -66.7335 | -0.007751 | -66.7414 | 56.293 | 56.2204 | 56.3947 | -66.8833 | -66.752 | -0.017956 | -66.7865 | 56.1894 | 56.3763 | 56.1964 | -67.1294 | -0.20087 | -0.011888 | -0.0511 | -0.058993 | 0.14188 | -0.084537 | 0.089745 | -0.44692 | -0.11554 | -0.069529 | -0.10403 | 0.34288 | 0.071371 | -0.10857 | 122.9755 | 122.9028 | 123.0771 | 66.6747 | -123.1882 | 122.8718 | 123.0587 | 122.8788 | 66.6645 | -123.4343
1898.7969 | 123.2346 | -66.6779 | 56.3507 | -0.010607 | -0.023812 | 3.4136e-05 | 0.053508 | -0.0063052 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056963 | 0.033292 | 0.05724 | -66.7335 | -0.016908 | -66.7643 | 56.293 | 56.2021 | 56.3947 | -66.8833 | -66.7474 | -0.013377 | -66.7819 | 56.194 | 56.3855 | 56.1964 | -67.1339 | -0.20545 | -0.057664 | -0.055678 | -0.086462 | 0.11898 | -0.14863 | 0.043969 | -0.45607 | -0.15674 | -0.069529 | -0.10403 | 0.35204 | 0.034753 | -0.15435 | 122.9709 | 122.8799 | 123.0725 | 66.6609 | -123.234 | 122.8718 | 123.0633 | 122.8742 | 66.6645 | -123.4846
1899.7969 | 123.2803 | -66.7007 | 56.3095 | -0.0029761 | -0.023598 | 0.00024794 | 0.053295 | -0.0065188 | 0.062717 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056535 | 0.032651 | 0.05724 | -66.7244 | -0.007751 | -66.7506 | 56.2885 | 56.1975 | 56.3993 | -66.865 | -66.7382 | -0.017956 | -66.7819 | 56.194 | 56.3809 | 56.2055 | -67.1294 | -0.16424 | -0.021043 | -0.023632 | -0.049838 | 0.1144 | -0.11201 | 0.089746 | -0.42861 | -0.11554 | -0.037482 | -0.081145 | 0.34746 | 0.071373 | -0.10399 | 122.9892 | 122.8982 | 123.1 | 66.693 | -123.1745 | 122.8947 | 123.0816 | 122.9063 | 66.6828 | -123.4389
1900.7969 | 123.1567 | -66.7419 | 56.3644 | -0.010607 | -0.023812 | 0.00024794 | 0.053081 | -0.0067326 | 0.062503 | 0.0077831 | -0.0032665 | -0.00076913 | 0.056963 | 0.033292 | 0.05724 | -66.7198 | -0.012329 | -66.7552 | 56.2976 | 56.2204 | 56.4038 | -66.8787 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.3809 | 56.2193 | -67.1294 | -0.13678 | -0.066818 | 0.022144 | -0.013218 | 0.12356 | -0.14405 | 0.039393 | -0.38741 | -0.17047 | -0.000863 | -0.039947 | 0.34746 | 0.016441 | -0.14519 | 123.0396 | 122.9623 | 123.1458 | 66.7296 | -123.2432 | 122.9359 | 123.1228 | 122.9612 | 66.724 | -123.4938
1901.7969 | 123.2849 | -66.7099 | 56.2958 | 0.0046549 | -0.024239 | 3.4136e-05 | 0.052867 | -0.0069462 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056749 | 0.03372 | 0.05724 | -66.729 | -0.012329 | -66.746 | 56.293 | 56.2112 | 56.4084 | -66.8696 | -66.752 | -0.017956 | -66.7819 | 56.1848 | 56.3809 | 56.1918 | -67.1294 | -0.15967 | -0.002732 | -0.019056 | -0.036105 | 0.12356 | -0.084539 | 0.11264 | -0.41945 | -0.11097 | -0.042063 | -0.07199 | 0.34746 | 0.085106 | -0.10399 | 123.0029 | 122.9211 | 123.1183 | 66.6976 | -123.1653 | 122.8947 | 123.0908 | 122.9017 | 66.6919 | -123.4251
1902.7969 | 123.1613 | -66.7099 | 56.3278 | -0.0029761 | -0.024025 | 0.00024794 | 0.053081 | -0.0065188 | 0.062503 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056749 | 0.033506 | 0.057026 | -66.7198 | -0.012329 | -66.7552 | 56.2885 | 56.2158 | 56.3993 | -66.8787 | -66.7428 | -0.017956 | -66.7865 | 56.1894 | 56.3717 | 56.2009 | -67.1248 | -0.16882 | -0.039354 | -0.009899 | -0.045261 | 0.12356 | -0.112 | 0.071435 | -0.41487 | -0.13843 | -0.032906 | -0.076569 | 0.3383 | 0.043905 | -0.12688 | 122.9984 | 122.9257 | 123.1092 | 66.6976 | -123.2065 | 122.8993 | 123.0816 | 122.9108 | 66.6919 | -123.4526
1903.7969 | 123.2529 | -66.7053 | 56.3049 | -0.010607 | -0.023812 | 0.00024794 | 0.053081 | -0.0063052 | 0.062717 | 0.00015261 | -0.0026255 | -0.00034193 | 0.056963 | 0.033079 | 0.057026 | -66.7335 | -0.007751 | -66.746 | 56.2885 | 56.2021 | 56.3947 | -66.8787 | -66.7428 | -0.022535 | -66.791 | 56.194 | 56.3763 | 56.2055 | -67.1294 | -0.1734 | -0.016466 | -0.028212 | -0.040683 | 0.13272 | -0.10285 | 0.089745 | -0.42403 | -0.11097 | -0.037484 | -0.085725 | 0.3383 | 0.071371 | -0.099414 | 122.9938 | 122.9074 | 123.1 | 66.6976 | -123.1837 | 122.8993 | 123.0816 | 122.9108 | 66.6828 | -123.4343
1904.7969 | 123.1613 | -66.7511 | 56.3461 | 0.0046549 | -0.024025 | 0.00024794 | 0.053295 | -0.0065188 | 0.062717 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056749 | 0.033079 | 0.057453 | -66.729 | -0.007751 | -66.7414 | 56.2885 | 56.2158 | 56.4084 | -66.8833 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.3809 | 56.2193 | -67.1294 | -0.1322 | -0.057664 | 0.022143 | 0.009672 | 0.14188 | -0.13031 | 0.062282 | -0.37825 | -0.15674 | 0.012872 | -0.026212 | 0.35204 | 0.034752 | -0.12688 | 123.0396 | 122.9669 | 123.1595 | 66.7433 | -123.2294 | 122.9405 | 123.132 | 122.9704 | 66.7377 | -123.4755
1905.7969 | 123.2849 | -66.7191 | 56.3004 | 0.0046549 | -0.023812 | -0.00017946 | 0.053508 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056749 | 0.033292 | 0.05724 | -66.7198 | -0.012329 | -66.7414 | 56.2885 | 56.2067 | 56.3947 | -66.8741 | -66.7336 | -0.008798 | -66.7865 | 56.194 | 56.3809 | 56.1918 | -67.1294 | -0.15509 | -0.011888 | -0.000744 | -0.022372 | 0.13272 | -0.093696 | 0.094323 | -0.4103 | -0.10639 | -0.014594 | -0.067414 | 0.34288 | 0.080528 | -0.10857 | 123.0075 | 122.9257 | 123.1137 | 66.7067 | -123.1745 | 122.913 | 123.0999 | 122.9108 | 66.7103 | -123.4297
1906.7969 | 123.0698 | -66.7236 | 56.3599 | 0.0046549 | -0.024025 | 0.00024794 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.033292 | 0.05724 | -66.7244 | -0.012329 | -66.746 | 56.2839 | 56.2204 | 56.4084 | -66.8833 | -66.7428 | -0.017956 | -66.7819 | 56.2031 | 56.3763 | 56.2238 | -67.1294 | -0.15967 | -0.075976 | -0.000744 | -0.022372 | 0.1373 | -0.13947 | 0.048549 | -0.40572 | -0.15674 | -0.019173 | -0.058257 | 0.34746 | 0.01644 | -0.13603 | 123.0075 | 122.944 | 123.132 | 66.7113 | -123.2432 | 122.9268 | 123.0999 | 122.9475 | 66.7057 | -123.4892
1907.8594 | 123.1842 | -66.7465 | 56.3232 | 0.0046549 | -0.024239 | 3.4136e-05 | 0.053081 | -0.0063052 | 0.062503 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056749 | 0.033292 | 0.05724 | -66.729 | -0.016908 | -66.746 | 56.2885 | 56.2021 | 56.4038 | -66.8833 | -66.752 | -0.013377 | -66.791 | 56.1848 | 56.3717 | 56.233 | -67.1248 | -0.13678 | -0.034776 | 0.017565 | 0.000516 | 0.1373 | -0.12116 | 0.080592 | -0.37825 | -0.13843 | -0.005442 | -0.044526 | 0.33372 | 0.048483 | -0.090252 | 123.035 | 122.9486 | 123.1504 | 66.7296 | -123.2065 | 122.9313 | 123.1182 | 122.9795 | 66.7331 | -123.448
1908.7969 | 123.1842 | -66.7557 | 56.3187 | -0.0029761 | -0.024025 | -0.00039306 | 0.053295 | -0.0069462 | 0.062289 | 0.00015261 | -0.0028393 | -0.00076913 | 0.057176 | 0.033292 | 0.05724 | -66.729 | -0.012329 | -66.7552 | 56.293 | 56.2158 | 56.4038 | -66.8925 | -66.752 | -0.022535 | -66.7819 | 56.1894 | 56.3855 | 56.2238 | -67.1248 | -0.13679 | -0.025621 | 0.02672 | 0.000515 | 0.1373 | -0.10285 | 0.085169 | -0.3691 | -0.12928 | 0.003713 | -0.026214 | 0.34288 | 0.066796 | -0.094833 | 123.0487 | 122.9715 | 123.1595 | 66.7433 | -123.2111 | 122.9451 | 123.1411 | 122.9795 | 66.7331 | -123.4434
1909.7969 | 123.1613 | -66.7648 | 56.3461 | -0.0029761 | -0.024025 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.06293 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056749 | 0.03372 | 0.057026 | -66.7335 | -0.003172 | -66.7597 | 56.2885 | 56.2204 | 56.413 | -66.8833 | -66.7474 | -0.022535 | -66.7865 | 56.1894 | 56.3763 | 56.2193 | -67.1339 | -0.11847 | -0.057664 | 0.031298 | 0.005092 | 0.12356 | -0.12573 | 0.066861 | -0.3691 | -0.15674 | 0.017447 | -0.021637 | 0.34746 | 0.030173 | -0.12688 | 123.0533 | 122.9852 | 123.1778 | 66.7617 | -123.2294 | 122.9542 | 123.1411 | 122.9841 | 66.7423 | -123.4801
1910.7969 | 123.175 | -66.7603 | 56.3187 | -0.010607 | -0.024239 | 0.00024794 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.057176 | 0.033292 | 0.057453 | -66.729 | -0.007751 | -66.7506 | 56.2976 | 56.2112 | 56.3993 | -66.8833 | -66.7291 | -0.00422 | -66.791 | 56.194 | 56.3809 | 56.2238 | -67.1294 | -0.12305 | -0.021042 | 0.031298 | 0.009671 | 0.13272 | -0.10743 | 0.08059 | -0.3691 | -0.1247 | 0.031184 | -0.030793 | 0.3383 | 0.062217 | -0.094833 | 123.0579 | 122.9715 | 123.1595 | 66.7525 | -123.202 | 122.9542 | 123.1411 | 122.9841 | 66.756 | -123.448
1911.8594 | 123.1567 | -66.7191 | 56.3416 | 0.012286 | -0.024239 | -0.00017946 | 0.053295 | -0.0065188 | 0.062717 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056749 | 0.033506 | 0.057453 | -66.729 | -0.007751 | -66.7552 | 56.2839 | 56.2158 | 56.4084 | -66.8833 | -66.7428 | -0.022535 | -66.791 | 56.194 | 56.3717 | 56.2238 | -67.1294 | -0.16425 | -0.057666 | -0.009901 | -0.036106 | 0.12814 | -0.12574 | 0.066859 | -0.4103 | -0.14759 | -0.023751 | -0.071992 | 0.3383 | 0.030172 | -0.11772 | 123.0029 | 122.9349 | 123.1275 | 66.7113 | -123.2249 | 122.913 | 123.0908 | 122.9429 | 66.6965 | -123.4709
1912.7969 | 123.2666 | -66.7374 | 56.2637 | -0.0029761 | -0.024239 | 0.00024794 | 0.053295 | -0.0067326 | 0.06293 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056963 | 0.033079 | 0.057453 | -66.729 | -0.012329 | -66.746 | 56.2885 | 56.2158 | 56.4038 | -66.8833 | -66.7336 | -0.017956 | -66.7819 | 56.194 | 56.3763 | 56.2284 | -67.1339 | -0.14594 | 0.024733 | 0.00841 | -0.008639 | 0.1373 | -0.047917 | 0.1401 | -0.39656 | -0.069766 | 0.003717 | -0.044524 | 0.35204 | 0.11257 | -0.035322 | 123.0258 | 122.9532 | 123.1412 | 66.725 | -123.147 | 122.9313 | 123.1137 | 122.9658 | 66.7194 | -123.3977
1913.7969 | 123.1979 | -66.7374 | 56.3324 | -0.0029761 | -0.024239 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056749 | 0.033506 | 0.057453 | -66.7335 | -0.012329 | -66.7552 | 56.293 | 56.2112 | 56.3947 | -66.8833 | -66.7428 | -0.008798 | -66.7819 | 56.194 | 56.3809 | 56.2101 | -67.1294 | -0.14594 | -0.039353 | 0.003832 | -0.017795 | 0.12814 | -0.12116 | 0.06228 | -0.39198 | -0.13843 | -0.00544 | -0.044524 | 0.34746 | 0.048485 | -0.1223 | 123.0304 | 122.9486 | 123.132 | 66.725 | -123.2157 | 122.9313 | 123.1182 | 122.9475 | 66.7286 | -123.4617
1914.8594 | 123.2803 | -66.7099 | 56.3095 | -0.010607 | -0.024239 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056963 | 0.033933 | 0.057026 | -66.7244 | -0.012329 | -66.746 | 56.293 | 56.2204 | 56.3947 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.1985 | 56.3809 | 56.2009 | -67.1294 | -0.1734 | -0.016465 | -0.014477 | -0.036105 | 0.1373 | -0.089114 | 0.085168 | -0.41945 | -0.11096 | -0.032906 | -0.076569 | 0.34288 | 0.071373 | -0.10857 | 123.0029 | 122.9303 | 123.1046 | 66.6976 | -123.1928 | 122.9084 | 123.0908 | 122.9108 | 66.6919 | -123.4389
1915.7969 | 123.1934 | -66.7282 | 56.337 | -0.0029761 | -0.024025 | 0.00024794 | 0.053295 | -0.0067326 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056535 | 0.033506 | 0.056812 | -66.7335 | -0.012329 | -66.746 | 56.2976 | 56.2204 | 56.4038 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.1985 | 56.3809 | 56.2147 | -67.1294 | -0.15509 | -0.039352 | -0.005324 | -0.017795 | 0.1373 | -0.11658 | 0.066859 | -0.40114 | -0.13843 | -0.019175 | -0.05368 | 0.34746 | 0.043907 | -0.1223 | 123.0258 | 122.9486 | 123.132 | 66.7159 | -123.2203 | 122.9268 | 123.1091 | 122.9429 | 66.7103 | -123.4663
1916.8594 | 123.1796 | -66.7603 | 56.3232 | -0.010607 | -0.024666 | -0.00017946 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056535 | 0.033506 | 0.05724 | -66.729 | -0.007751 | -66.7597 | 56.2885 | 56.2112 | 56.4084 | -66.8833 | -66.7565 | -0.017956 | -66.7819 | 56.1848 | 56.3809 | 56.2193 | -67.1248 | -0.12305 | -0.034776 | 0.031298 | 0.000514 | 0.12356 | -0.11201 | 0.08517 | -0.36452 | -0.13843 | 0.003712 | -0.021636 | 0.34288 | 0.05764 | -0.10399 | 123.0487 | 122.9715 | 123.1687 | 66.7525 | -123.2065 | 122.9451 | 123.1411 | 122.9795 | 66.7423 | -123.448
1917.7969 | 123.2117 | -66.7328 | 56.282 | -0.0029761 | -0.024453 | 0.00024794 | 0.053295 | -0.0067326 | 0.06293 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.033506 | 0.057453 | -66.7198 | -0.012329 | -66.7597 | 56.2839 | 56.2158 | 56.4038 | -66.8787 | -66.7428 | -0.008798 | -66.7773 | 56.1985 | 56.3763 | 56.2101 | -67.1385 | -0.14594 | 0.001844 | 0.012989 | -0.026952 | 0.11898 | -0.066227 | 0.12179 | -0.40572 | -0.083498 | -0.010018 | -0.044523 | 0.3612 | 0.09426 | -0.071946 | 123.0167 | 122.9486 | 123.1366 | 66.7205 | -123.1608 | 122.9313 | 123.1091 | 122.9429 | 66.724 | -123.4206
1918.7969 | 123.2071 | -66.7603 | 56.3141 | -0.010607 | -0.024239 | -0.00017946 | 0.053081 | -0.0065188 | 0.062289 | 0.015414 | -0.0030529 | -0.00055553 | 0.056963 | 0.033292 | 0.056599 | -66.7335 | -0.007751 | -66.7552 | 56.2839 | 56.2204 | 56.3993 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.194 | 56.3809 | 56.2101 | -67.1339 | -0.12305 | -0.0302 | 0.02672 | 0.005093 | 0.12814 | -0.093692 | 0.085168 | -0.37367 | -0.12012 | 0.012869 | -0.026215 | 0.34746 | 0.066795 | -0.10399 | 123.0441 | 122.9806 | 123.1595 | 66.7525 | -123.1974 | 122.9542 | 123.1411 | 122.9704 | 66.7515 | -123.448
1919.7969 | 123.1842 | -66.7374 | 56.3095 | 0.012286 | -0.024453 | 3.4136e-05 | 0.052867 | -0.0065188 | 0.06293 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056535 | 0.033292 | 0.057026 | -66.7244 | -0.007751 | -66.7552 | 56.2976 | 56.225 | 56.4038 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.1894 | 56.3763 | 56.2284 | -67.1294 | -0.14594 | -0.011886 | 0.012989 | -0.017795 | 0.12814 | -0.084536 | 0.094325 | -0.39198 | -0.12012 | -0.00544 | -0.049103 | 0.34288 | 0.066794 | -0.081098 | 123.035 | 122.9623 | 123.1412 | 66.7296 | -123.1928 | 122.9268 | 123.1137 | 122.9658 | 66.724 | -123.4389
1920.7969 | 123.1934 | -66.7145 | 56.2637 | 0.0046549 | -0.024666 | 0.00024794 | 0.053295 | -0.0069462 | 0.062717 | 0.015414 | -0.0028393 | -0.00055553 | 0.056963 | 0.03372 | 0.057026 | -66.7244 | -0.012329 | -66.7552 | 56.293 | 56.2158 | 56.3993 | -66.8833 | -66.7474 | -0.017956 | -66.7865 | 56.1894 | 56.3855 | 56.2055 | -67.1339 | -0.16882 | 0.029311 | -0.009899 | -0.040683 | 0.12814 | -0.047917 | 0.13552 | -0.41945 | -0.074345 | -0.032907 | -0.071991 | 0.34746 | 0.12173 | -0.058215 | 123.0075 | 122.9303 | 123.1137 | 66.7021 | -123.147 | 122.9039 | 123.0999 | 122.92 | 66.6965 | -123.3977
1921.7969 | 123.1384 | -66.7694 | 56.3324 | -0.010607 | -0.024239 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.057176 | 0.03372 | 0.057026 | -66.7198 | -0.012329 | -66.7506 | 56.2885 | 56.2158 | 56.4038 | -66.8833 | -66.7382 | -0.00422 | -66.7865 | 56.1894 | 56.3717 | 56.2193 | -67.1248 | -0.11389 | -0.043931 | 0.04961 | 0.018826 | 0.13272 | -0.11658 | 0.071437 | -0.35536 | -0.14301 | 0.031182 | -0.01706 | 0.3383 | 0.039328 | -0.11314 | 123.0579 | 122.9852 | 123.1732 | 66.7571 | -123.2157 | 122.9588 | 123.1411 | 122.9887 | 66.7652 | -123.4572
1922.8594 | 123.2162 | -66.7328 | 56.3507 | -0.0029761 | -0.024239 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056322 | 0.033506 | 0.05724 | -66.7198 | -0.012329 | -66.7552 | 56.2839 | 56.2296 | 56.4038 | -66.8879 | -66.7428 | -0.013377 | -66.791 | 56.194 | 56.3855 | 56.2193 | -67.1294 | -0.15509 | -0.066821 | 0.012989 | -0.022373 | 0.13272 | -0.12116 | 0.053126 | -0.39656 | -0.15674 | -0.010018 | -0.058259 | 0.3383 | 0.034753 | -0.13145 | 123.0167 | 122.9623 | 123.1366 | 66.7205 | -123.2386 | 122.9268 | 123.1182 | 122.952 | 66.7194 | -123.4801
1923.7969 | 123.143 | -66.7511 | 56.3004 | 0.0046549 | -0.024025 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062289 | -0.015108 | -0.0028393 | -0.00055553 | 0.056749 | 0.03372 | 0.05724 | -66.7244 | -0.007751 | -66.7414 | 56.293 | 56.2204 | 56.4084 | -66.8741 | -66.7382 | -0.017956 | -66.7865 | 56.1894 | 56.3855 | 56.2193 | -67.1294 | -0.12305 | -0.00731 | 0.026722 | 0.009672 | 0.13272 | -0.079959 | 0.10806 | -0.37825 | -0.11097 | 0.012872 | -0.03537 | 0.34288 | 0.085107 | -0.0811 | 123.0441 | 122.9715 | 123.1595 | 66.7433 | -123.1745 | 122.9405 | 123.1366 | 122.9704 | 66.7331 | -123.4297
1924.7969 | 123.2849 | -66.7145 | 56.282 | -0.0029761 | -0.024453 | -0.00039306 | 0.053508 | -0.0065188 | 0.06293 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.033933 | 0.056812 | -66.7244 | -0.012329 | -66.7414 | 56.2839 | 56.2112 | 56.4084 | -66.8741 | -66.7428 | -0.017956 | -66.7773 | 56.1894 | 56.3809 | 56.2193 | -67.1339 | -0.15967 | 0.001844 | -0.009899 | -0.026949 | 0.13272 | -0.070806 | 0.12637 | -0.41945 | -0.092655 | -0.028328 | -0.062833 | 0.35662 | 0.098839 | -0.062789 | 122.9984 | 122.9257 | 123.1229 | 66.7021 | -123.1562 | 122.9039 | 123.0954 | 122.9337 | 66.6965 | -123.416
1925.7969 | 123.1476 | -66.7648 | 56.3324 | -0.0029761 | -0.024025 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062289 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.03372 | 0.05724 | -66.7335 | -0.012329 | -66.7368 | 56.2885 | 56.1975 | 56.4038 | -66.8787 | -66.7428 | -0.017956 | -66.7819 | 56.1894 | 56.3855 | 56.2055 | -67.1339 | -0.11389 | -0.043931 | 0.031298 | 0.027984 | 0.14188 | -0.1349 | 0.071437 | -0.3691 | -0.14301 | 0.022026 | -0.017058 | 0.35204 | 0.053064 | -0.12688 | 123.0533 | 122.9623 | 123.1687 | 66.7525 | -123.2111 | 122.9542 | 123.1503 | 122.9703 | 66.7469 | -123.4663
1926.8594 | 123.1659 | -66.7648 | 56.3141 | -0.018238 | -0.024239 | 3.4136e-05 | 0.053295 | -0.0063052 | 0.062717 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056963 | 0.03372 | 0.057026 | -66.7198 | -0.016908 | -66.746 | 56.2839 | 56.2204 | 56.4038 | -66.8833 | -66.7474 | -0.013377 | -66.791 | 56.194 | 56.3763 | 56.2193 | -67.1339 | -0.11847 | -0.0302 | 0.045033 | 0.018827 | 0.1373 | -0.093692 | 0.089747 | -0.3691 | -0.12012 | 0.017447 | -0.026215 | 0.34288 | 0.062216 | -0.094833 | 123.0487 | 122.9852 | 123.1687 | 66.7479 | -123.1974 | 122.9588 | 123.1411 | 122.9841 | 66.7515 | -123.448
1927.7969 | 123.2574 | -66.7511 | 56.2912 | 0.0046549 | -0.024453 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062076 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056963 | 0.033933 | 0.05724 | -66.729 | -0.016908 | -66.7506 | 56.293 | 56.2067 | 56.3993 | -66.8833 | -66.7474 | -0.017956 | -66.7865 | 56.194 | 56.3809 | 56.2193 | -67.1294 | -0.1322 | 0.001845 | 0.022143 | 0.000516 | 0.13272 | -0.084541 | 0.10806 | -0.37825 | -0.097232 | 0.003714 | -0.03537 | 0.34288 | 0.089683 | -0.071945 | 123.0441 | 122.9578 | 123.1504 | 66.7342 | -123.1745 | 122.9451 | 123.132 | 122.9704 | 66.7331 | -123.4205
1928.8594 | 123.2849 | -66.7191 | 56.2729 | -0.018238 | -0.024453 | 0.00024794 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056749 | 0.033506 | 0.057026 | -66.7198 | -0.003172 | -66.7506 | 56.2839 | 56.2112 | 56.3993 | -66.8833 | -66.7428 | -0.013377 | -66.7819 | 56.194 | 56.39 | 56.2421 | -67.1294 | -0.16425 | 0.010999 | -0.000744 | -0.031528 | 0.13272 | -0.061651 | 0.12637 | -0.4103 | -0.078921 | -0.023751 | -0.062835 | 0.34746 | 0.11715 | -0.030741 | 123.0029 | 122.9303 | 123.1183 | 66.7159 | -123.1562 | 122.913 | 123.1091 | 122.9612 | 66.7057 | -123.4022
1929.7969 | 123.2071 | -66.7282 | 56.3278 | 0.0046549 | -0.024453 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | 0.0077831 | -0.0032665 | -0.00076913 | 0.056535 | 0.033506 | 0.05724 | -66.729 | -0.003172 | -66.7414 | 56.293 | 56.2112 | 56.3993 | -66.8879 | -66.7382 | -0.017956 | -66.7819 | 56.1894 | 56.3855 | 56.2193 | -67.1202 | -0.15967 | -0.034776 | -0.000746 | -0.013217 | 0.14646 | -0.11658 | 0.071435 | -0.39198 | -0.13843 | -0.010017 | -0.05368 | 0.3383 | 0.057641 | -0.10857 | 123.0213 | 122.9394 | 123.1275 | 66.725 | -123.2157 | 122.9176 | 123.1137 | 122.9475 | 66.7103 | -123.448
1930.8594 | 123.1567 | -66.7419 | 56.3416 | -0.0029761 | -0.024666 | 0.00024794 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056749 | 0.03372 | 0.05724 | -66.7244 | -0.012329 | -66.7506 | 56.2839 | 56.2021 | 56.4038 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.1985 | 56.3855 | 56.2421 | -67.1339 | -0.13678 | -0.057666 | 0.017566 | -0.00864 | 0.12814 | -0.13947 | 0.062281 | -0.39199 | -0.14301 | -0.005442 | -0.039947 | 0.35204 | 0.043908 | -0.099406 | 123.0258 | 122.944 | 123.1458 | 66.7296 | -123.2203 | 122.9405 | 123.1274 | 122.9841 | 66.7286 | -123.4755
1931.7969 | 123.2666 | -66.7328 | 56.2592 | 0.012286 | -0.024025 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062503 | -0.0074779 | -0.0028393 | -0.00076913 | 0.057176 | 0.033933 | 0.057026 | -66.729 | -0.012329 | -66.7552 | 56.2885 | 56.2112 | 56.4038 | -66.8741 | -66.7428 | -0.017956 | -66.7865 | 56.1894 | 56.3809 | 56.2376 | -67.1339 | -0.14136 | 0.029311 | 0.003832 | -0.022373 | 0.11898 | -0.047918 | 0.14468 | -0.40114 | -0.069767 | -0.010018 | -0.053681 | 0.34746 | 0.12173 | -0.021587 | 123.0213 | 122.944 | 123.1366 | 66.7205 | -123.1333 | 122.9222 | 123.1137 | 122.9704 | 66.7148 | -123.3931
1932.7969 | 123.2162 | -66.7145 | 56.3232 | 0.0046549 | -0.024239 | -0.00017946 | 0.053508 | -0.0067326 | 0.06293 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.033506 | 0.057026 | -66.7381 | -0.012329 | -66.7552 | 56.2839 | 56.225 | 56.3947 | -66.8879 | -66.7428 | -0.022535 | -66.791 | 56.1894 | 56.3946 | 56.2055 | -67.1294 | -0.1734 | -0.039355 | -0.023634 | -0.040683 | 0.13272 | -0.098269 | 0.071435 | -0.41487 | -0.13385 | -0.028328 | -0.076569 | 0.3383 | 0.071376 | -0.11772 | 122.9984 | 122.9395 | 123.1092 | 66.7021 | -123.2111 | 122.9039 | 123.1091 | 122.92 | 66.6919 | -123.4526
1933.8594 | 123.1384 | -66.7648 | 56.337 | 0.0046549 | -0.024239 | 0.00024794 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056749 | 0.03372 | 0.05724 | -66.7244 | -0.016908 | -66.7506 | 56.2885 | 56.2158 | 56.3947 | -66.8787 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.39 | 56.2147 | -67.1339 | -0.11389 | -0.048509 | 0.040455 | 0.014249 | 0.12814 | -0.12116 | 0.057702 | -0.3691 | -0.14301 | 0.017447 | -0.017058 | 0.35204 | 0.053064 | -0.1223 | 123.0533 | 122.9806 | 123.1595 | 66.7479 | -123.2157 | 122.9588 | 123.1549 | 122.9795 | 66.7469 | -123.4709
1934.7969 | 123.2346 | -66.7374 | 56.3187 | 0.0046549 | -0.024239 | 3.4136e-05 | 0.053722 | -0.0067326 | 0.062503 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056749 | 0.033506 | 0.057026 | -66.7244 | -0.007751 | -66.7506 | 56.293 | 56.2158 | 56.4038 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.194 | 56.3855 | 56.2376 | -67.1294 | -0.14594 | -0.025621 | 0.012989 | -0.013217 | 0.13272 | -0.10285 | 0.085169 | -0.39198 | -0.1247 | -0.010019 | -0.049103 | 0.34288 | 0.066796 | -0.081097 | 123.0304 | 122.9532 | 123.1412 | 66.7296 | -123.202 | 122.9313 | 123.1228 | 122.9749 | 66.7286 | -123.448
1935.7969 | 123.2803 | -66.7007 | 56.3141 | -0.010607 | -0.024025 | 0.00024794 | 0.053508 | -0.0067326 | 0.062503 | 0.015414 | -0.0026255 | -0.00098273 | 0.056535 | 0.03372 | 0.05724 | -66.729 | -0.012329 | -66.746 | 56.2793 | 56.2112 | 56.3947 | -66.8787 | -66.7382 | -0.017956 | -66.7865 | 56.194 | 56.3855 | 56.2376 | -67.1294 | -0.17798 | -0.034778 | -0.028211 | -0.04526 | 0.13272 | -0.10285 | 0.08059 | -0.42861 | -0.12012 | -0.037482 | -0.085724 | 0.34288 | 0.071374 | -0.076519 | 122.9801 | 122.912 | 123.0954 | 66.6884 | -123.1928 | 122.8947 | 123.0862 | 122.9383 | 66.6828 | -123.4434
1936.8594 | 123.1659 | -66.7374 | 56.3278 | -0.010607 | -0.024239 | 0.00024794 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056535 | 0.033933 | 0.05724 | -66.7244 | -0.016908 | -66.7506 | 56.2839 | 56.2067 | 56.4084 | -66.8787 | -66.7428 | -0.022535 | -66.7865 | 56.194 | 56.3855 | 56.2009 | -67.1294 | -0.14136 | -0.043933 | 0.012989 | -0.013217 | 0.12814 | -0.12116 | 0.080592 | -0.39198 | -0.13385 | -0.00544 | -0.049103 | 0.34288 | 0.057641 | -0.12688 | 123.0213 | 122.944 | 123.1458 | 66.7205 | -123.2065 | 122.9313 | 123.1228 | 122.9383 | 66.7148 | -123.4572
1937.7969 | 123.2849 | -66.7236 | 56.2729 | -0.010607 | -0.024666 | 3.4136e-05 | 0.053081 | -0.0065188 | 0.062289 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056535 | 0.033506 | 0.056812 | -66.729 | -0.012329 | -66.7552 | 56.2885 | 56.2204 | 56.4038 | -66.8787 | -66.7428 | -0.013377 | -66.7819 | 56.194 | 56.3809 | 56.2101 | -67.1294 | -0.15509 | 0.015578 | -0.005323 | -0.031528 | 0.12356 | -0.052493 | 0.13095 | -0.40572 | -0.078921 | -0.019173 | -0.058257 | 0.34746 | 0.10799 | -0.062791 | 123.0121 | 122.944 | 123.1275 | 66.7113 | -123.1516 | 122.9176 | 123.1045 | 122.9337 | 66.7103 | -123.4022
1938.7969 | 123.2666 | -66.7007 | 56.3095 | -0.0029761 | -0.024453 | 3.4136e-05 | 0.053936 | -0.0065188 | 0.062289 | 0.0077831 | -0.0026255 | -0.00055553 | 0.056963 | 0.033506 | 0.05724 | -66.7244 | -0.012329 | -66.746 | 56.2839 | 56.2112 | 56.4084 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.194 | 56.3809 | 56.2193 | -67.1339 | -0.18714 | -0.025622 | -0.023632 | -0.04526 | 0.14188 | -0.098272 | 0.098903 | -0.43318 | -0.11554 | -0.042061 | -0.085724 | 0.34746 | 0.071373 | -0.090255 | 122.9846 | 122.912 | 123.1092 | 66.6884 | -123.1974 | 122.8947 | 123.0816 | 122.92 | 66.6919 | -123.4434
1939.7969 | 123.2803 | -66.7145 | 56.3049 | -0.010607 | -0.024239 | 0.00024794 | 0.053508 | -0.0069462 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056749 | 0.03372 | 0.057453 | -66.7335 | -0.012329 | -66.7506 | 56.2839 | 56.2067 | 56.3901 | -66.8833 | -66.7474 | -0.017956 | -66.7773 | 56.194 | 56.39 | 56.2421 | -67.1248 | -0.16882 | -0.021045 | -0.019056 | -0.036105 | 0.13272 | -0.098274 | 0.085166 | -0.41029 | -0.11097 | -0.032907 | -0.062833 | 0.34746 | 0.085107 | -0.062785 | 122.9984 | 122.9211 | 123.1046 | 66.7021 | -123.1882 | 122.9084 | 123.1045 | 122.9566 | 66.6965 | -123.4297
1940.7969 | 123.2529 | -66.7145 | 56.3278 | -0.0029761 | -0.024666 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056963 | 0.033506 | 0.057026 | -66.7335 | -0.007751 | -66.7552 | 56.2839 | 56.2067 | 56.4038 | -66.8833 | -66.7428 | -0.017956 | -66.7819 | 56.1985 | 56.3809 | 56.2147 | -67.1385 | -0.16882 | -0.043933 | -0.019056 | -0.040683 | 0.12814 | -0.12116 | 0.076014 | -0.42403 | -0.12927 | -0.028328 | -0.067412 | 0.35662 | 0.053062 | -0.11315 | 122.9984 | 122.9211 | 123.1183 | 66.7067 | -123.2111 | 122.913 | 123.0954 | 122.9292 | 66.6965 | -123.4663
1941.8594 | 123.1796 | -66.7694 | 56.3004 | -0.0029761 | -0.024453 | 3.4136e-05 | 0.052867 | -0.0067326 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.033933 | 0.05724 | -66.7335 | -0.007751 | -66.7506 | 56.2885 | 56.2112 | 56.4084 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.3855 | 56.1964 | -67.1339 | -0.11389 | -0.011888 | 0.035875 | 0.018826 | 0.13272 | -0.089117 | 0.10806 | -0.36452 | -0.10639 | 0.022024 | -0.012481 | 0.35204 | 0.085107 | -0.10399 | 123.0579 | 122.9806 | 123.1778 | 66.7617 | -123.1837 | 122.9634 | 123.1549 | 122.9658 | 66.7515 | -123.4343
1942.7969 | 123.2895 | -66.6779 | 56.3141 | 0.0046549 | -0.024239 | 0.00046154 | 0.053508 | -0.0069462 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056963 | 0.03372 | 0.057453 | -66.729 | -0.012329 | -66.7414 | 56.2793 | 56.2021 | 56.3947 | -66.8787 | -66.7382 | -0.013377 | -66.7773 | 56.1894 | 56.39 | 56.2284 | -67.1294 | -0.20087 | -0.034778 | -0.0511 | -0.063571 | 0.1373 | -0.11201 | 0.08059 | -0.45149 | -0.1247 | -0.060371 | -0.099455 | 0.35204 | 0.075952 | -0.085676 | 122.9572 | 122.8799 | 123.0725 | 66.6655 | -123.1928 | 122.8672 | 123.0679 | 122.9063 | 66.6645 | -123.4434
1943.7969 | 123.23 | -66.7328 | 56.2912 | -0.0029761 | -0.024453 | -0.00039306 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056535 | 0.034147 | 0.057026 | -66.7244 | -0.007751 | -66.7506 | 56.2885 | 56.2296 | 56.4084 | -66.8879 | -66.7428 | -0.017956 | -66.791 | 56.194 | 56.3809 | 56.2009 | -67.1339 | -0.15509 | -0.002733 | 0.008411 | -0.017795 | 0.1373 | -0.061647 | 0.11721 | -0.40114 | -0.097232 | -0.010018 | -0.058259 | 0.34288 | 0.089683 | -0.09026 | 123.0213 | 122.9623 | 123.1412 | 66.725 | -123.1791 | 122.9268 | 123.1137 | 122.9337 | 66.7148 | -123.4251
1944.7969 | 123.3078 | -66.7007 | 56.3232 | -0.0029761 | -0.024239 | 0.00024794 | 0.053508 | -0.0067326 | 0.06293 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056535 | 0.034147 | 0.056812 | -66.729 | -0.007751 | -66.7506 | 56.2839 | 56.225 | 56.4038 | -66.8787 | -66.7428 | -0.017956 | -66.7819 | 56.1985 | 56.3855 | 56.2147 | -67.1294 | -0.17798 | -0.039355 | -0.028211 | -0.049838 | 0.12814 | -0.098269 | 0.080592 | -0.42861 | -0.1247 | -0.042061 | -0.081145 | 0.34746 | 0.062219 | -0.10857 | 122.9846 | 122.9257 | 123.1046 | 66.693 | -123.202 | 122.8993 | 123.0862 | 122.9154 | 66.6828 | -123.4526
1945.7969 | 123.2117 | -66.7099 | 56.3187 | 0.0046549 | -0.024453 | 0.00046154 | 0.053508 | -0.0067326 | 0.062717 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056749 | 0.033933 | 0.056812 | -66.7335 | -0.003172 | -66.7552 | 56.2839 | 56.2158 | 56.4038 | -66.8787 | -66.7428 | -0.027113 | -66.7819 | 56.194 | 56.3763 | 56.2055 | -67.1339 | -0.16882 | -0.034778 | -0.023634 | -0.045261 | 0.12356 | -0.10285 | 0.085169 | -0.42403 | -0.1247 | -0.032906 | -0.07199 | 0.35204 | 0.057638 | -0.11315 | 122.9938 | 122.9257 | 123.1137 | 66.7067 | -123.1974 | 122.9039 | 123.0862 | 122.9154 | 66.6828 | -123.4526
1946.8594 | 123.2025 | -66.7328 | 56.3049 | 0.0046549 | -0.02488 | 0.00024794 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056749 | 0.03372 | 0.057026 | -66.7198 | -0.012329 | -66.746 | 56.2885 | 56.225 | 56.4084 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.1985 | 56.3855 | 56.2009 | -67.1294 | -0.15051 | -0.016466 | 0.012989 | -0.013217 | 0.1373 | -0.079959 | 0.10348 | -0.39656 | -0.10639 | -0.010018 | -0.053681 | 0.34288 | 0.080529 | -0.10399 | 123.0213 | 122.9578 | 123.1412 | 66.7205 | -123.1882 | 122.9313 | 123.1182 | 122.9337 | 66.7194 | -123.4343
1947.7969 | 123.2574 | -66.7145 | 56.2958 | 0.012286 | -0.024666 | 0.00024794 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.033933 | 0.057026 | -66.7244 | -0.016908 | -66.7506 | 56.2885 | 56.2158 | 56.4038 | -66.8787 | -66.7428 | -0.013377 | -66.7865 | 56.194 | 56.3855 | 56.2284 | -67.1339 | -0.16425 | -0.00731 | -0.009899 | -0.036105 | 0.12814 | -0.07996 | 0.10806 | -0.41945 | -0.10181 | -0.028328 | -0.071991 | 0.34746 | 0.089685 | -0.067365 | 123.0029 | 122.9303 | 123.1183 | 66.6976 | -123.1745 | 122.9084 | 123.0999 | 122.9429 | 66.7011 | -123.4297
1948.7969 | 123.262 | -66.687 | 56.337 | 0.0046549 | -0.024666 | 3.4136e-05 | 0.052867 | -0.0067326 | 0.06293 | 0.0077831 | -0.0032665 | -0.00034193 | 0.056322 | 0.033933 | 0.05724 | -66.7198 | -0.012329 | -66.7506 | 56.2885 | 56.225 | 56.4038 | -66.8787 | -66.7474 | -0.017956 | -66.791 | 56.1985 | 56.3855 | 56.2101 | -67.1339 | -0.19171 | -0.048509 | -0.032787 | -0.063571 | 0.12814 | -0.112 | 0.066859 | -0.44692 | -0.13843 | -0.060373 | -0.10404 | 0.34288 | 0.048486 | -0.12688 | 122.9755 | 122.912 | 123.0908 | 66.6747 | -123.2157 | 122.8856 | 123.0725 | 122.8971 | 66.6691 | -123.4709
1949.8594 | 123.175 | -66.7694 | 56.3187 | -0.0029761 | -0.024453 | 0.00024794 | 0.053295 | -0.0067326 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056749 | 0.034147 | 0.057026 | -66.7244 | -0.012329 | -66.7552 | 56.293 | 56.2204 | 56.4084 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.1985 | 56.3809 | 56.2147 | -67.1248 | -0.11389 | -0.025621 | 0.045032 | 0.014248 | 0.12814 | -0.09827 | 0.089747 | -0.35536 | -0.12012 | 0.026603 | -0.01706 | 0.3383 | 0.062217 | -0.10399 | 123.0625 | 122.9898 | 123.1778 | 66.7571 | -123.202 | 122.968 | 123.1503 | 122.9841 | 66.7515 | -123.4434
1950.7969 | 123.262 | -66.687 | 56.3461 | -0.0029761 | -0.024453 | 0.00024794 | 0.053295 | -0.0065188 | 0.062503 | 0.0077831 | -0.0034801 | -0.00098273 | 0.056322 | 0.034147 | 0.056812 | -66.729 | -0.007751 | -66.7643 | 56.2839 | 56.2204 | 56.4038 | -66.8833 | -66.7474 | -0.008798 | -66.791 | 56.1894 | 56.39 | 56.2421 | -67.1294 | -0.19629 | -0.062243 | -0.041944 | -0.077306 | 0.11898 | -0.12573 | 0.057704 | -0.44234 | -0.15674 | -0.060373 | -0.10404 | 0.3383 | 0.043909 | -0.10398 | 122.9709 | 122.9074 | 123.0908 | 66.6793 | -123.2294 | 122.8764 | 123.0771 | 122.9292 | 66.6782 | -123.4755
1951.7969 | 123.2391 | -66.7191 | 56.3141 | -0.010607 | -0.024239 | -0.00017946 | 0.053508 | -0.0069462 | 0.062717 | 0.00015261 | -0.0028393 | -0.0011965 | 0.056963 | 0.03372 | 0.05724 | -66.7244 | -0.012329 | -66.7552 | 56.2885 | 56.2204 | 56.4038 | -66.8787 | -66.7474 | -0.017956 | -66.7865 | 56.2031 | 56.3855 | 56.1918 | -67.1248 | -0.15967 | -0.025621 | -0.005322 | -0.036106 | 0.12356 | -0.093692 | 0.089747 | -0.40572 | -0.11096 | -0.02833 | -0.067414 | 0.3383 | 0.071374 | -0.1223 | 123.0075 | 122.9394 | 123.1229 | 66.7067 | -123.1928 | 122.9222 | 123.1045 | 122.9108 | 66.7011 | -123.4389
1952.8594 | 123.2574 | -66.7236 | 56.3095 | -0.0029761 | -0.024666 | 3.4136e-05 | 0.053295 | -0.0063052 | 0.063144 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056749 | 0.03372 | 0.056812 | -66.7335 | -0.003172 | -66.746 | 56.2839 | 56.2112 | 56.413 | -66.8696 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.3855 | 56.2055 | -67.1339 | -0.14593 | -0.025622 | -0.009901 | -0.022372 | 0.12356 | -0.098272 | 0.10348 | -0.4103 | -0.11554 | -0.023752 | -0.062836 | 0.34746 | 0.075952 | -0.10399 | 123.0075 | 122.9349 | 123.1366 | 66.7205 | -123.1791 | 122.9176 | 123.1091 | 122.9292 | 66.7103 | -123.4434
1953.7969 | 123.262 | -66.7328 | 56.2958 | -0.010607 | -0.02488 | -0.00017946 | 0.053722 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056963 | 0.033933 | 0.057026 | -66.729 | -0.012329 | -66.7597 | 56.2885 | 56.225 | 56.3993 | -66.8741 | -66.7474 | -0.017956 | -66.7819 | 56.194 | 56.3855 | 56.2238 | -67.1294 | -0.14136 | -0.00731 | 0.003832 | -0.026952 | 0.11441 | -0.070803 | 0.10348 | -0.39656 | -0.10181 | -0.014597 | -0.049102 | 0.34746 | 0.089685 | -0.071944 | 123.0213 | 122.9578 | 123.132 | 66.7205 | -123.1699 | 122.9268 | 123.1182 | 122.9566 | 66.7148 | -123.4251
1954.8594 | 123.2574 | -66.7145 | 56.2912 | 0.0046549 | -0.024666 | -0.00017946 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056535 | 0.034147 | 0.056812 | -66.7244 | -0.007751 | -66.7552 | 56.293 | 56.2158 | 56.4038 | -66.8787 | -66.7428 | -0.022535 | -66.7865 | 56.1985 | 56.39 | 56.2055 | -67.1202 | -0.16425 | 0.001845 | -0.009899 | -0.040683 | 0.12356 | -0.075383 | 0.11264 | -0.40572 | -0.092654 | -0.028328 | -0.071991 | 0.33372 | 0.09884 | -0.085681 | 123.0075 | 122.9303 | 123.1183 | 66.7067 | -123.1699 | 122.913 | 123.1045 | 122.92 | 66.6919 | -123.4114
1955.7969 | 123.3032 | -66.7007 | 56.3232 | -0.0029761 | -0.024666 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056749 | 0.034147 | 0.057026 | -66.7244 | -0.007751 | -66.746 | 56.293 | 56.2204 | 56.4084 | -66.8787 | -66.7428 | -0.013377 | -66.7773 | 56.194 | 56.3809 | 56.2147 | -67.1339 | -0.17798 | -0.030198 | -0.023632 | -0.04526 | 0.13272 | -0.10285 | 0.08517 | -0.43318 | -0.12927 | -0.042061 | -0.076566 | 0.35662 | 0.05764 | -0.10857 | 122.9938 | 122.9211 | 123.1092 | 66.693 | -123.202 | 122.8947 | 123.0816 | 122.9154 | 66.6874 | -123.4572
1956.7969 | 123.1567 | -66.7465 | 56.3873 | 0.0046549 | -0.024666 | -0.00039306 | 0.053081 | -0.0067326 | 0.06293 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056963 | 0.033933 | 0.057026 | -66.7244 | -0.007751 | -66.7597 | 56.2839 | 56.2296 | 56.4038 | -66.8833 | -66.7428 | -0.017956 | -66.791 | 56.2077 | 56.3855 | 56.2284 | -67.1294 | -0.13678 | -0.10344 | 0.022144 | -0.013219 | 0.12356 | -0.15778 | 0.016505 | -0.38283 | -0.17963 | 0.003715 | -0.044526 | 0.3383 | -0.001868 | -0.15892 | 123.0304 | 122.9761 | 123.1504 | 66.7388 | -123.2706 | 122.9542 | 123.132 | 122.9749 | 66.7286 | -123.5167
1957.7969 | 123.3078 | -66.7099 | 56.3232 | -0.010607 | -0.02488 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.06293 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056963 | 0.033506 | 0.057026 | -66.7244 | -0.007751 | -66.7414 | 56.293 | 56.225 | 56.3993 | -66.8833 | -66.7382 | -0.017956 | -66.7865 | 56.194 | 56.3809 | 56.2147 | -67.1339 | -0.1734 | -0.030198 | -0.014477 | -0.031527 | 0.14188 | -0.098269 | 0.076013 | -0.42403 | -0.12927 | -0.028327 | -0.076569 | 0.34746 | 0.05764 | -0.10857 | 123.0029 | 122.9349 | 123.1092 | 66.7021 | -123.2065 | 122.9039 | 123.0908 | 122.9246 | 66.6919 | -123.4572
1958.7969 | 123.1613 | -66.7282 | 56.3507 | -0.0029761 | -0.02488 | 0.00024794 | 0.053295 | -0.0069462 | 0.062717 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056749 | 0.033933 | 0.056812 | -66.729 | -0.007751 | -66.746 | 56.293 | 56.2204 | 56.4084 | -66.8787 | -66.7474 | -0.013377 | -66.7773 | 56.1894 | 56.3946 | 56.2147 | -67.1248 | -0.15051 | -0.057664 | -0.000746 | -0.017795 | 0.13272 | -0.13031 | 0.057704 | -0.39656 | -0.16132 | -0.019175 | -0.049101 | 0.34746 | 0.04391 | -0.13603 | 123.0213 | 122.9486 | 123.1366 | 66.7205 | -123.2294 | 122.9176 | 123.1228 | 122.9429 | 66.7148 | -123.4755
1959.8594 | 123.2849 | -66.7145 | 56.3187 | -0.0029761 | -0.02488 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056535 | 0.033933 | 0.057026 | -66.7244 | -0.016908 | -66.7506 | 56.293 | 56.225 | 56.4038 | -66.8696 | -66.7474 | -0.022535 | -66.7819 | 56.1985 | 56.3809 | 56.233 | -67.1248 | -0.15509 | -0.025621 | -0.009899 | -0.036105 | 0.11898 | -0.093692 | 0.085169 | -0.41029 | -0.12012 | -0.032907 | -0.067412 | 0.34288 | 0.062217 | -0.085675 | 123.0075 | 122.9395 | 123.1183 | 66.6976 | -123.1882 | 122.913 | 123.0954 | 122.9475 | 66.6919 | -123.4434
1960.7969 | 123.1659 | -66.7328 | 56.3644 | -0.010607 | -0.024666 | 0.00024794 | 0.053081 | -0.0069462 | 0.062503 | 0.015414 | -0.0028393 | -0.00076913 | 0.056535 | 0.034361 | 0.057026 | -66.7244 | -0.007751 | -66.746 | 56.2839 | 56.225 | 56.4038 | -66.8833 | -66.7428 | -0.017956 | -66.791 | 56.1985 | 56.3809 | 56.2147 | -67.1339 | -0.15051 | -0.080554 | 0.008411 | -0.013217 | 0.1373 | -0.13947 | 0.039393 | -0.40114 | -0.1659 | -0.010018 | -0.058259 | 0.34288 | 0.016441 | -0.14977 | 123.0167 | 122.9578 | 123.1366 | 66.725 | -123.2477 | 122.9313 | 123.1137 | 122.9475 | 66.7148 | -123.4984
1961.7969 | 123.1796 | -66.7007 | 56.3095 | 0.0046549 | -0.02488 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056963 | 0.034147 | 0.057026 | -66.7244 | -0.007751 | -66.746 | 56.2885 | 56.2204 | 56.4084 | -66.8833 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.39 | 56.2101 | -67.1385 | -0.18256 | -0.021043 | -0.023632 | -0.04526 | 0.1373 | -0.089114 | 0.098903 | -0.43776 | -0.11554 | -0.042061 | -0.081145 | 0.35662 | 0.08053 | -0.099412 | 122.9892 | 122.9211 | 123.1092 | 66.693 | -123.1928 | 122.8947 | 123.0908 | 122.9108 | 66.6828 | -123.448
1962.8594 | 123.23 | -66.7236 | 56.2958 | 0.0046549 | -0.025094 | -0.00017946 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056963 | 0.033933 | 0.056812 | -66.7335 | -0.007751 | -66.7552 | 56.2885 | 56.2296 | 56.4038 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.194 | 56.3809 | 56.2147 | -67.1339 | -0.15509 | -0.00731 | -0.009901 | -0.031528 | 0.12356 | -0.066224 | 0.10806 | -0.4103 | -0.10181 | -0.023752 | -0.058257 | 0.35204 | 0.085106 | -0.081101 | 123.0121 | 122.9532 | 123.1275 | 66.7159 | -123.1745 | 122.9176 | 123.1045 | 122.9383 | 66.7103 | -123.4297
1963.7969 | 123.2803 | -66.6824 | 56.3141 | -0.0029761 | -0.02488 | -0.00017946 | 0.053508 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056322 | 0.034147 | 0.057026 | -66.729 | -0.007751 | -66.7368 | 56.2976 | 56.225 | 56.4084 | -66.8833 | -66.7428 | -0.022535 | -66.7865 | 56.1985 | 56.3809 | 56.2238 | -67.1385 | -0.20087 | -0.016464 | -0.046522 | -0.054414 | 0.14646 | -0.089114 | 0.094325 | -0.45607 | -0.11554 | -0.060372 | -0.10403 | 0.35204 | 0.066795 | -0.090255 | 122.9801 | 122.9074 | 123.0908 | 66.6747 | -123.1974 | 122.881 | 123.0633 | 122.9063 | 66.6599 | -123.4526
1964.7969 | 123.2254 | -66.7511 | 56.3461 | 0.0046549 | -0.024666 | 0.00046154 | 0.053081 | -0.0071598 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056535 | 0.034361 | 0.05724 | -66.7198 | -0.012329 | -66.7506 | 56.293 | 56.225 | 56.4084 | -66.8833 | -66.7474 | -0.008798 | -66.7773 | 56.194 | 56.3855 | 56.2284 | -67.1294 | -0.1322 | -0.053086 | 0.0313 | 0.000516 | 0.13272 | -0.12116 | 0.062282 | -0.37825 | -0.15216 | 0.003714 | -0.026212 | 0.35204 | 0.039331 | -0.11772 | 123.0441 | 122.9761 | 123.1595 | 66.7388 | -123.2294 | 122.9451 | 123.1366 | 122.9795 | 66.7423 | -123.4755
1965.7969 | 123.175 | -66.7282 | 56.3553 | -0.010607 | -0.02488 | 0.00024794 | 0.053081 | -0.0065188 | 0.062503 | 0.015414 | -0.0030529 | -0.00076913 | 0.056535 | 0.034147 | 0.057026 | -66.7244 | -0.007751 | -66.7368 | 56.2885 | 56.2296 | 56.4038 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.3809 | 56.233 | -67.1294 | -0.15967 | -0.06682 | 0.003833 | -0.008638 | 0.15103 | -0.12573 | 0.048548 | -0.40114 | -0.15216 | -0.019175 | -0.058259 | 0.34288 | 0.025596 | -0.1223 | 123.0167 | 122.9578 | 123.132 | 66.7205 | -123.2432 | 122.9313 | 123.1091 | 122.9612 | 66.7148 | -123.4846
1966.7969 | 123.1522 | -66.7328 | 56.3095 | 0.0046549 | -0.024666 | 3.4136e-05 | 0.052867 | -0.0065188 | 0.062717 | -0.0074779 | -0.0026255 | -0.00098273 | 0.056749 | 0.034147 | 0.05724 | -66.7335 | -0.007751 | -66.7368 | 56.293 | 56.2158 | 56.4084 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.194 | 56.39 | 56.2193 | -67.1339 | -0.15509 | -0.016465 | -0.000746 | -0.00406 | 0.15103 | -0.093693 | 0.098903 | -0.40114 | -0.11554 | -0.010018 | -0.053681 | 0.34746 | 0.08053 | -0.090255 | 123.0258 | 122.9486 | 123.1412 | 66.725 | -123.1974 | 122.9268 | 123.1228 | 122.952 | 66.724 | -123.4434
1967.8438 | 123.2666 | -66.7374 | 56.2683 | -0.0029761 | -0.025094 | -0.00017946 | 0.053722 | -0.0067326 | 0.06293 | -0.0074779 | -0.0030529 | -0.00098273 | 0.056535 | 0.034147 | 0.05724 | -66.7198 | -0.012329 | -66.746 | 56.293 | 56.2296 | 56.413 | -66.8879 | -66.7474 | -0.017956 | -66.791 | 56.1985 | 56.3855 | 56.2193 | -67.1294 | -0.15052 | 0.024733 | 0.017567 | -0.008639 | 0.14188 | -0.038759 | 0.14468 | -0.39198 | -0.069766 | -0.010019 | -0.053681 | 0.3383 | 0.11715 | -0.049057 | 123.0304 | 122.9669 | 123.1504 | 66.725 | -123.1562 | 122.9359 | 123.1228 | 122.9566 | 66.7194 | -123.3977
1968.7969 | 123.2208 | -66.7603 | 56.3324 | 0.0046549 | -0.02488 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062717 | -0.0074779 | -0.0030529 | -0.00098273 | 0.056535 | 0.034147 | 0.057453 | -66.729 | -0.003172 | -66.7506 | 56.293 | 56.2341 | 56.4176 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.1985 | 56.3855 | 56.2193 | -67.1294 | -0.12305 | -0.039353 | 0.031298 | 0.009671 | 0.13272 | -0.098266 | 0.085173 | -0.3691 | -0.13385 | 0.012869 | -0.021636 | 0.34746 | 0.053064 | -0.11314 | 123.0533 | 122.9944 | 123.1778 | 66.7571 | -123.2157 | 122.9588 | 123.1457 | 122.9795 | 66.7423 | -123.4617
1969.7969 | 123.1567 | -66.7511 | 56.3599 | -0.0029761 | -0.025094 | 0.00024794 | 0.053295 | -0.0069462 | 0.062503 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056963 | 0.033933 | 0.05724 | -66.7244 | -0.007751 | -66.7552 | 56.293 | 56.2296 | 56.4084 | -66.8833 | -66.7382 | -0.013377 | -66.7819 | 56.194 | 56.39 | 56.233 | -67.1294 | -0.1322 | -0.066819 | 0.026722 | -0.004062 | 0.12814 | -0.13031 | 0.048549 | -0.37825 | -0.1659 | 0.012872 | -0.030791 | 0.34746 | 0.030176 | -0.12687 | 123.0441 | 122.9807 | 123.1595 | 66.7433 | -123.2432 | 122.9451 | 123.1411 | 122.9841 | 66.7377 | -123.4892
1970.8594 | 123.1567 | -66.7465 | 56.3461 | 0.0046549 | -0.024666 | -0.00039306 | 0.053508 | -0.0069462 | 0.062503 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056535 | 0.033933 | 0.056812 | -66.7244 | -0.007751 | -66.7597 | 56.293 | 56.2296 | 56.4084 | -66.8741 | -66.752 | -0.017956 | -66.7865 | 56.2031 | 56.39 | 56.2193 | -67.1339 | -0.12762 | -0.053086 | 0.022144 | -0.013219 | 0.11441 | -0.11658 | 0.062282 | -0.38741 | -0.14301 | -0.005442 | -0.039948 | 0.34746 | 0.043909 | -0.12688 | 123.0396 | 122.9761 | 123.1549 | 66.7388 | -123.2203 | 122.9496 | 123.1366 | 122.9658 | 66.7286 | -123.4801
1971.7969 | 123.2391 | -66.7374 | 56.3965 | 0.0046549 | -0.025094 | 3.4136e-05 | 0.053081 | -0.0065188 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056749 | 0.034574 | 0.05724 | -66.7244 | -0.012329 | -66.7597 | 56.293 | 56.2204 | 56.4176 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.39 | 56.2193 | -67.1339 | -0.15052 | -0.10344 | 0.012989 | -0.022374 | 0.12814 | -0.17609 | 0.021086 | -0.39656 | -0.20252 | -0.010019 | -0.049103 | 0.34746 | -0.006445 | -0.17723 | 123.0304 | 122.9578 | 123.1549 | 66.725 | -123.2844 | 122.9313 | 123.1274 | 122.9566 | 66.724 | -123.5304
1972.7969 | 123.1338 | -66.7694 | 56.3278 | -0.0029761 | -0.024666 | -0.00017946 | 0.053081 | -0.0069462 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.034361 | 0.057026 | -66.7244 | -0.003172 | -66.7506 | 56.293 | 56.225 | 56.413 | -66.8833 | -66.7565 | -0.017956 | -66.7819 | 56.2031 | 56.3855 | 56.2101 | -67.1385 | -0.11389 | -0.034776 | 0.045032 | 0.018826 | 0.13272 | -0.10285 | 0.085171 | -0.3691 | -0.1247 | 0.012867 | -0.012481 | 0.35662 | 0.057641 | -0.11772 | 123.0625 | 122.9944 | 123.1824 | 66.7662 | -123.2111 | 122.9725 | 123.1549 | 122.9795 | 66.7515 | -123.4663
1973.8594 | 123.1567 | -66.7419 | 56.3461 | 0.0046549 | -0.02488 | -0.00017946 | 0.052867 | -0.0069462 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056749 | 0.034361 | 0.057026 | -66.7244 | -0.007751 | -66.7506 | 56.293 | 56.2341 | 56.4084 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.1894 | 56.3855 | 56.2421 | -67.1339 | -0.14136 | -0.053086 | 0.017566 | -0.00864 | 0.13272 | -0.112 | 0.062282 | -0.39199 | -0.15674 | -0.005442 | -0.039947 | 0.35204 | 0.039331 | -0.10398 | 123.035 | 122.9761 | 123.1504 | 66.7342 | -123.2294 | 122.9313 | 123.1274 | 122.9841 | 66.724 | -123.4801
1974.7969 | 123.1934 | -66.7374 | 56.3416 | 0.0046549 | -0.025094 | -0.00039306 | 0.052867 | -0.0067326 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056535 | 0.034361 | 0.057026 | -66.7244 | -0.007751 | -66.7597 | 56.2976 | 56.2204 | 56.4084 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.39 | 56.2238 | -67.1385 | -0.15052 | -0.04393 | 0.012989 | -0.022374 | 0.12814 | -0.12116 | 0.066859 | -0.40114 | -0.13385 | -0.010019 | -0.049103 | 0.35204 | 0.048486 | -0.11772 | 123.035 | 122.9578 | 123.1458 | 66.7296 | -123.2294 | 122.9451 | 123.1274 | 122.9612 | 66.724 | -123.4801
1975.7969 | 123.1979 | -66.7328 | 56.3187 | -0.010607 | -0.02488 | 0.00024794 | 0.053081 | -0.0067326 | 0.062289 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056749 | 0.033933 | 0.05724 | -66.729 | -0.012329 | -66.7552 | 56.293 | 56.2204 | 56.413 | -66.8833 | -66.7474 | -0.013377 | -66.7819 | 56.1985 | 56.3855 | 56.2238 | -67.1431 | -0.15051 | -0.025621 | 0.003832 | -0.022373 | 0.12814 | -0.09827 | 0.094326 | -0.4103 | -0.12012 | -0.014597 | -0.049102 | 0.3612 | 0.066796 | -0.094833 | 123.0258 | 122.9532 | 123.1458 | 66.7205 | -123.202 | 122.9313 | 123.1182 | 122.9566 | 66.7194 | -123.4618
1976.7969 | 123.1247 | -66.7648 | 56.2637 | -0.0029761 | -0.02488 | -0.00017946 | 0.053508 | -0.0069462 | 0.062717 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056535 | 0.034147 | 0.057026 | -66.7244 | -0.003172 | -66.7735 | 56.293 | 56.225 | 56.4084 | -66.8879 | -66.7474 | -0.022535 | -66.7819 | 56.194 | 56.3855 | 56.2147 | -67.1294 | -0.12305 | 0.029311 | 0.040455 | -0.008642 | 0.11441 | -0.03876 | 0.14468 | -0.36452 | -0.069766 | 0.017447 | -0.017058 | 0.34746 | 0.12173 | -0.049058 | 123.0579 | 122.9898 | 123.1732 | 66.7617 | -123.1516 | 122.9588 | 123.1503 | 122.9795 | 66.7423 | -123.3931
1977.7969 | 123.2025 | -66.7374 | 56.3278 | -0.0029761 | -0.025094 | 0.00024794 | 0.052867 | -0.0067326 | 0.06293 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056749 | 0.034574 | 0.057026 | -66.7198 | 0.001407 | -66.746 | 56.2885 | 56.2158 | 56.413 | -66.8879 | -66.752 | -0.00422 | -66.7773 | 56.1985 | 56.3855 | 56.2193 | -67.1385 | -0.15052 | -0.039354 | 0.017567 | -0.008639 | 0.14188 | -0.112 | 0.085171 | -0.40114 | -0.12927 | -0.014597 | -0.039945 | 0.3612 | 0.057641 | -0.10857 | 123.0258 | 122.9532 | 123.1504 | 66.7388 | -123.2157 | 122.9359 | 123.1228 | 122.9566 | 66.7331 | -123.4663
1978.7969 | 123.1476 | -66.7648 | 56.2958 | -0.010607 | -0.025307 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | -0.0074779 | -0.0028393 | -0.00055553 | 0.056322 | 0.034574 | 0.057026 | -66.7335 | -0.007751 | -66.7414 | 56.2976 | 56.2158 | 56.413 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.2031 | 56.3855 | 56.233 | -67.1339 | -0.11847 | 0.001847 | 0.031298 | 0.023405 | 0.14188 | -0.07996 | 0.11722 | -0.3691 | -0.092652 | 0.022026 | -0.021637 | 0.34746 | 0.089685 | -0.062786 | 123.0625 | 122.9806 | 123.1778 | 66.7571 | -123.1791 | 122.968 | 123.1503 | 122.9978 | 66.7469 | -123.4297
1979.7969 | 123.1842 | -66.7374 | 56.3278 | -0.0029761 | -0.025307 | -0.00017946 | 0.053081 | -0.0065188 | 0.06293 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056963 | 0.034574 | 0.05724 | -66.729 | -0.012329 | -66.7414 | 56.2885 | 56.2204 | 56.4084 | -66.8879 | -66.7382 | -0.017956 | -66.7819 | 56.194 | 56.3855 | 56.2376 | -67.1294 | -0.15052 | -0.039354 | 0.00841 | -0.004061 | 0.14646 | -0.10742 | 0.080592 | -0.39198 | -0.13385 | -0.000861 | -0.044524 | 0.34746 | 0.057641 | -0.090252 | 123.0258 | 122.9578 | 123.1458 | 66.725 | -123.2157 | 122.9313 | 123.1228 | 122.9749 | 66.7194 | -123.4572
1980.8594 | 123.1979 | -66.7419 | 56.3416 | -0.0029761 | -0.025094 | -0.00039306 | 0.053081 | -0.0065188 | 0.062717 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.034361 | 0.05724 | -66.729 | -0.012329 | -66.746 | 56.2976 | 56.2296 | 56.4084 | -66.8833 | -66.7428 | -0.008798 | -66.7773 | 56.2031 | 56.39 | 56.2147 | -67.1385 | -0.14136 | -0.04393 | 0.012987 | -0.004062 | 0.1373 | -0.112 | 0.066859 | -0.39656 | -0.13843 | -0.000863 | -0.035368 | 0.3612 | 0.048486 | -0.12688 | 123.0396 | 122.9715 | 123.1504 | 66.7296 | -123.2249 | 122.9451 | 123.132 | 122.9566 | 66.7331 | -123.4801
1981.7969 | 123.2025 | -66.7282 | 56.3324 | 0.012286 | -0.025094 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056108 | 0.034574 | 0.056812 | -66.729 | 0.001407 | -66.7506 | 56.293 | 56.2204 | 56.4084 | -66.8833 | -66.7428 | -0.008798 | -66.7865 | 56.2031 | 56.3855 | 56.2101 | -67.1385 | -0.15509 | -0.039353 | -0.000746 | -0.022373 | 0.13272 | -0.112 | 0.076015 | -0.4103 | -0.12927 | -0.014596 | -0.058259 | 0.35204 | 0.053064 | -0.1223 | 123.0213 | 122.9486 | 123.1366 | 66.7296 | -123.2157 | 122.9313 | 123.1137 | 122.9383 | 66.7194 | -123.4709
1982.8594 | 123.1979 | -66.7465 | 56.3278 | -0.010607 | -0.025521 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062717 | -0.0074779 | -0.0028393 | -0.00055553 | 0.056749 | 0.034361 | 0.05724 | -66.729 | -0.003172 | -66.7552 | 56.2976 | 56.2341 | 56.4084 | -66.8879 | -66.7428 | -0.013377 | -66.7865 | 56.1985 | 56.3855 | 56.2147 | -67.1294 | -0.14136 | -0.030197 | 0.017565 | -0.00864 | 0.13272 | -0.093689 | 0.080592 | -0.38283 | -0.12927 | 0.003715 | -0.039948 | 0.34288 | 0.057641 | -0.11315 | 123.0441 | 122.9807 | 123.1549 | 66.7433 | -123.2157 | 122.9451 | 123.132 | 122.9612 | 66.7331 | -123.4572
1983.7969 | 123.1384 | -66.7465 | 56.2912 | -0.010607 | -0.02488 | 0.00024794 | 0.053295 | -0.0069462 | 0.062717 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056749 | 0.034361 | 0.05724 | -66.729 | -0.012329 | -66.7552 | 56.2976 | 56.2112 | 56.413 | -66.8879 | -66.7428 | -0.008798 | -66.791 | 56.1985 | 56.39 | 56.2467 | -67.1294 | -0.14136 | 0.006424 | 0.017565 | -0.00864 | 0.13272 | -0.079962 | 0.12179 | -0.38283 | -0.092654 | 0.003715 | -0.044526 | 0.3383 | 0.09884 | -0.044474 | 123.0441 | 122.9578 | 123.1595 | 66.7342 | -123.1791 | 122.9451 | 123.1366 | 122.9932 | 66.7377 | -123.4205
1984.7969 | 123.2666 | -66.7007 | 56.2729 | 0.0046549 | -0.025094 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062076 | -0.015108 | -0.0030529 | -0.00076913 | 0.056535 | 0.034147 | 0.05724 | -66.7335 | -0.007751 | -66.7552 | 56.293 | 56.225 | 56.4084 | -66.8741 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3855 | 56.2055 | -67.1339 | -0.1734 | 0.020156 | -0.032789 | -0.054416 | 0.11898 | -0.047915 | 0.13552 | -0.43318 | -0.069764 | -0.04664 | -0.081145 | 0.35204 | 0.11257 | -0.06737 | 122.9938 | 122.9257 | 123.1092 | 66.693 | -123.147 | 122.9039 | 123.0862 | 122.9063 | 66.6874 | -123.4068
1985.8594 | 123.1705 | -66.7282 | 56.3782 | -0.0029761 | -0.025094 | -0.00017946 | 0.053081 | -0.0069462 | 0.062717 | 0.015414 | -0.0028393 | -0.00076913 | 0.056963 | 0.034361 | 0.057026 | -66.729 | -0.012329 | -66.7506 | 56.293 | 56.2158 | 56.4084 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2031 | 56.39 | 56.2193 | -67.1294 | -0.15509 | -0.08513 | -0.000746 | -0.022373 | 0.13272 | -0.16236 | 0.030238 | -0.40114 | -0.17505 | -0.014596 | -0.058259 | 0.34288 | 0.011865 | -0.15892 | 123.0213 | 122.944 | 123.1366 | 66.7159 | -123.2615 | 122.9313 | 123.1182 | 122.9475 | 66.7148 | -123.5075
1986.7969 | 123.2346 | -66.7282 | 56.2729 | -0.0029761 | -0.025094 | -0.00039306 | 0.053508 | -0.0067326 | 0.062717 | 0.0077831 | -0.0026255 | -0.00076913 | 0.056535 | 0.034361 | 0.056599 | -66.729 | -0.007751 | -66.7506 | 56.2839 | 56.2158 | 56.413 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.1985 | 56.39 | 56.2101 | -67.1294 | -0.15509 | 0.010999 | -0.000746 | -0.022373 | 0.13272 | -0.057072 | 0.1401 | -0.40114 | -0.074343 | -0.019175 | -0.05368 | 0.34746 | 0.11715 | -0.062791 | 123.0121 | 122.944 | 123.1412 | 66.7205 | -123.1562 | 122.9268 | 123.1182 | 122.9383 | 66.7103 | -123.4022
1987.8438 | 123.2437 | -66.7191 | 56.3416 | 0.0046549 | -0.02488 | -0.00039306 | 0.053508 | -0.0069462 | 0.062717 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056749 | 0.034361 | 0.05724 | -66.7335 | -0.012329 | -66.7552 | 56.2885 | 56.2204 | 56.413 | -66.8879 | -66.7382 | -0.017956 | -66.7819 | 56.2031 | 56.3855 | 56.2284 | -67.1294 | -0.16883 | -0.053087 | -0.014479 | -0.036106 | 0.13272 | -0.12116 | 0.071438 | -0.4103 | -0.13843 | -0.019172 | -0.062835 | 0.34746 | 0.043908 | -0.11314 | 123.0075 | 122.9394 | 123.132 | 66.7067 | -123.2294 | 122.9222 | 123.1045 | 122.9475 | 66.7011 | -123.4709
1988.7969 | 123.2483 | -66.7328 | 56.3187 | -0.010607 | -0.025094 | -0.00017946 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056535 | 0.033933 | 0.05724 | -66.729 | -0.007751 | -66.7552 | 56.293 | 56.2158 | 56.4084 | -66.8879 | -66.7382 | -0.017956 | -66.7819 | 56.2031 | 56.39 | 56.2284 | -67.1294 | -0.15509 | -0.025621 | 0.003832 | -0.022373 | 0.13272 | -0.10285 | 0.089747 | -0.39656 | -0.11554 | -0.005439 | -0.049102 | 0.34746 | 0.071374 | -0.090254 | 123.0258 | 122.9486 | 123.1412 | 66.725 | -123.2065 | 122.9359 | 123.1228 | 122.9612 | 66.7148 | -123.448
1989.8594 | 123.2666 | -66.7053 | 56.3049 | 0.012286 | -0.025094 | -0.00017946 | 0.053081 | -0.0067326 | 0.062717 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056749 | 0.034147 | 0.056812 | -66.729 | -0.003172 | -66.7552 | 56.2976 | 56.2067 | 56.4084 | -66.8925 | -66.7474 | -0.017956 | -66.7865 | 56.194 | 56.39 | 56.2009 | -67.1339 | -0.18714 | -0.007309 | -0.023634 | -0.049839 | 0.1373 | -0.098274 | 0.10348 | -0.42861 | -0.11097 | -0.042063 | -0.081147 | 0.34746 | 0.085107 | -0.10399 | 123.0029 | 122.912 | 123.1137 | 66.7021 | -123.1974 | 122.8993 | 123.0954 | 122.9063 | 66.6874 | -123.4389
1990.7969 | 123.2483 | -66.7236 | 56.3278 | 0.0046549 | -0.025094 | 3.4136e-05 | 0.053508 | -0.0071598 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.034574 | 0.05724 | -66.7335 | -0.003172 | -66.7506 | 56.2885 | 56.2204 | 56.4084 | -66.8741 | -66.7474 | -0.017956 | -66.7865 | 56.1985 | 56.39 | 56.2238 | -67.1477 | -0.15051 | -0.039354 | -0.009901 | -0.02695 | 0.12356 | -0.10742 | 0.080592 | -0.42403 | -0.12927 | -0.023752 | -0.062836 | 0.3612 | 0.062219 | -0.10399 | 123.0121 | 122.944 | 123.132 | 66.7205 | -123.202 | 122.9222 | 123.1137 | 122.9475 | 66.7057 | -123.4755
1991.7969 | 123.2712 | -66.6962 | 56.3095 | -0.010607 | -0.02488 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062717 | 0.0077831 | -0.0026255 | -0.00055553 | 0.056749 | 0.034361 | 0.05724 | -66.729 | -0.007751 | -66.7414 | 56.293 | 56.2021 | 56.4084 | -66.8741 | -66.7382 | -0.013377 | -66.7773 | 56.1985 | 56.3855 | 56.2284 | -67.1385 | -0.17798 | -0.016465 | -0.032789 | -0.04526 | 0.13272 | -0.10743 | 0.098903 | -0.44234 | -0.11096 | -0.04206 | -0.081144 | 0.3612 | 0.075952 | -0.081098 | 122.9892 | 122.8982 | 123.1046 | 66.6884 | -123.1837 | 122.8947 | 123.0816 | 122.9246 | 66.6828 | -123.448
1992.7969 | 123.2666 | -66.7145 | 56.3049 | 0.0046549 | -0.025521 | 0.00024794 | 0.053508 | -0.0065188 | 0.062717 | 0.015414 | -0.0028393 | -0.00055553 | 0.056749 | 0.034147 | 0.057026 | -66.7244 | -0.012329 | -66.7552 | 56.2839 | 56.2112 | 56.4038 | -66.8925 | -66.7474 | -0.017956 | -66.791 | 56.2031 | 56.39 | 56.1918 | -67.1385 | -0.17798 | -0.021045 | -0.009899 | -0.040683 | 0.1373 | -0.093695 | 0.098902 | -0.42403 | -0.10181 | -0.032907 | -0.076569 | 0.34746 | 0.085107 | -0.11315 | 122.9984 | 122.9257 | 123.1183 | 66.7021 | -123.1974 | 122.9176 | 123.1045 | 122.9063 | 66.6965 | -123.4434
1993.7969 | 123.262 | -66.7282 | 56.3004 | -0.0029761 | -0.025307 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062503 | -0.015108 | -0.0030529 | -0.00076913 | 0.056322 | 0.034147 | 0.056812 | -66.729 | -0.012329 | -66.7643 | 56.2885 | 56.2204 | 56.4038 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.1985 | 56.3809 | 56.2147 | -67.1339 | -0.15967 | -0.011888 | -0.000746 | -0.036108 | 0.12356 | -0.079959 | 0.10348 | -0.40572 | -0.10181 | -0.019175 | -0.058259 | 0.34746 | 0.080528 | -0.085679 | 123.0167 | 122.9486 | 123.132 | 66.7159 | -123.1882 | 122.9268 | 123.1091 | 122.9429 | 66.7194 | -123.4343
1994.8594 | 123.262 | -66.7099 | 56.3644 | 0.012286 | -0.025307 | 0.00024794 | 0.053508 | -0.0065188 | 0.062503 | 0.015414 | -0.0028393 | -0.00098273 | 0.056749 | 0.035002 | 0.056812 | -66.7335 | -0.012329 | -66.7597 | 56.2976 | 56.225 | 56.4038 | -66.8879 | -66.752 | -0.013377 | -66.7819 | 56.2031 | 56.3855 | 56.2193 | -67.1339 | -0.17798 | -0.066818 | -0.023634 | -0.04984 | 0.12814 | -0.13947 | 0.039393 | -0.42403 | -0.16132 | -0.042063 | -0.07199 | 0.35204 | 0.02102 | -0.14519 | 123.0075 | 122.9349 | 123.1137 | 66.6976 | -123.2523 | 122.913 | 123.0954 | 122.9292 | 66.6965 | -123.4984
1995.7969 | 123.2346 | -66.7282 | 56.2912 | -0.0029761 | -0.025307 | -0.00017946 | 0.053508 | -0.0067326 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.034361 | 0.057026 | -66.7335 | -0.007751 | -66.7506 | 56.2885 | 56.2204 | 56.4084 | -66.8879 | -66.7428 | -0.017956 | -66.7773 | 56.2031 | 56.3855 | 56.2284 | -67.1339 | -0.15967 | -0.002733 | -0.005324 | -0.022373 | 0.1373 | -0.070804 | 0.11721 | -0.40572 | -0.088075 | -0.014596 | -0.049101 | 0.35662 | 0.094262 | -0.062788 | 123.0167 | 122.9486 | 123.1366 | 66.7205 | -123.1791 | 122.9313 | 123.1137 | 122.9566 | 66.7103 | -123.4251
1996.7969 | 123.2803 | -66.6779 | 56.3095 | -0.010607 | -0.025307 | -0.00017946 | 0.053081 | -0.0065188 | 0.062289 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056535 | 0.034361 | 0.05724 | -66.729 | -0.007751 | -66.7506 | 56.2885 | 56.2158 | 56.4084 | -66.8787 | -66.7382 | -0.017956 | -66.7819 | 56.1985 | 56.3763 | 56.2147 | -67.1294 | -0.20087 | -0.021043 | -0.0511 | -0.072727 | 0.12814 | -0.093693 | 0.098903 | -0.45149 | -0.11096 | -0.060371 | -0.10403 | 0.34746 | 0.066794 | -0.094834 | 122.9663 | 122.8937 | 123.0863 | 66.6701 | -123.1882 | 122.8764 | 123.0542 | 122.8925 | 66.6599 | -123.4389
1997.7969 | 123.2712 | -66.7282 | 56.3416 | -0.010607 | -0.025521 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.06293 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056749 | 0.034574 | 0.057026 | -66.7244 | -0.003172 | -66.7552 | 56.293 | 56.2021 | 56.4084 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.2031 | 56.3809 | 56.2284 | -67.1339 | -0.15967 | -0.048509 | 0.003833 | -0.026951 | 0.13272 | -0.13947 | 0.066859 | -0.40572 | -0.13843 | -0.019175 | -0.058259 | 0.34746 | 0.039329 | -0.11314 | 123.0213 | 122.9303 | 123.1366 | 66.725 | -123.2294 | 122.9313 | 123.1091 | 122.9566 | 66.7194 | -123.4755
1998.7969 | 123.2712 | -66.6824 | 56.3004 | 0.0046549 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062717 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056749 | 0.034574 | 0.057026 | -66.7335 | -0.007751 | -66.7643 | 56.293 | 56.2158 | 56.413 | -66.8787 | -66.7474 | -0.017956 | -66.7865 | 56.1985 | 56.39 | 56.2467 | -67.1385 | -0.19629 | -0.00731 | -0.0511 | -0.081884 | 0.11441 | -0.084538 | 0.11264 | -0.45607 | -0.10181 | -0.064951 | -0.10403 | 0.35204 | 0.089685 | -0.053629 | 122.9755 | 122.8982 | 123.0954 | 66.6747 | -123.1791 | 122.881 | 123.0725 | 122.9292 | 66.6645 | -123.4389
1999.875 | 123.2208 | -66.7236 | 56.3416 | 0.0046549 | -0.02488 | -0.00039306 | 0.053295 | -0.0067326 | 0.062503 | 0.015414 | -0.0026255 | -0.00076913 | 0.056535 | 0.034574 | 0.05724 | -66.7244 | -0.007751 | -66.7689 | 56.2976 | 56.225 | 56.4176 | -66.8879 | -66.7428 | -0.017956 | -66.7819 | 56.2031 | 56.39 | 56.2147 | -67.1339 | -0.16425 | -0.04393 | -0.000744 | -0.045263 | 0.11899 | -0.11658 | 0.076017 | -0.4103 | -0.13843 | -0.019173 | -0.058257 | 0.35204 | 0.048486 | -0.12688 | 123.0213 | 122.9486 | 123.1412 | 66.7159 | -123.2294 | 122.9268 | 123.1137 | 122.9383 | 66.7057 | -123.4755
2000.7969 | 123.2483 | -66.6916 | 56.3187 | 0.0046549 | -0.025307 | -0.00017946 | 0.053081 | -0.0067326 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.034574 | 0.057026 | -66.729 | -0.007751 | -66.7506 | 56.293 | 56.2204 | 56.4176 | -66.8925 | -66.7428 | -0.017956 | -66.7819 | 56.194 | 56.3855 | 56.2238 | -67.1431 | -0.20087 | -0.025621 | -0.037367 | -0.058994 | 0.14188 | -0.09827 | 0.098905 | -0.4515 | -0.1247 | -0.051217 | -0.090301 | 0.3612 | 0.066796 | -0.094833 | 122.9846 | 122.912 | 123.1092 | 66.6838 | -123.2111 | 122.8856 | 123.077 | 122.9154 | 66.6736 | -123.4618
2001.7969 | 123.262 | -66.7099 | 56.3004 | -0.010607 | -0.025307 | -0.00017946 | 0.053295 | -0.0069462 | 0.062503 | -0.0074779 | -0.0026255 | -0.00076913 | 0.056963 | 0.034788 | 0.057026 | -66.7244 | -0.012329 | -66.7643 | 56.2976 | 56.2112 | 56.4084 | -66.8833 | -66.7428 | -0.013377 | -66.7819 | 56.2031 | 56.39 | 56.2009 | -67.1339 | -0.1734 | -0.002731 | -0.014477 | -0.054418 | 0.11898 | -0.089117 | 0.10806 | -0.42403 | -0.09723 | -0.032906 | -0.07199 | 0.35204 | 0.089685 | -0.099415 | 123.0075 | 122.9211 | 123.1183 | 66.6976 | -123.1837 | 122.913 | 123.0999 | 122.9108 | 66.6965 | -123.4343
2002.8594 | 123.2666 | -66.7191 | 56.3049 | -0.0029761 | -0.025307 | 0.00024794 | 0.053081 | -0.0069462 | 0.06293 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056108 | 0.034361 | 0.05724 | -66.7335 | -0.012329 | -66.7414 | 56.2885 | 56.225 | 56.413 | -66.8833 | -66.7428 | -0.013377 | -66.791 | 56.2077 | 56.3763 | 56.2193 | -67.1339 | -0.16425 | -0.016466 | -0.014479 | -0.022372 | 0.14188 | -0.079959 | 0.10806 | -0.41487 | -0.09723 | -0.023751 | -0.071992 | 0.34288 | 0.071371 | -0.085678 | 123.0075 | 122.944 | 123.132 | 66.7067 | -123.1882 | 122.9268 | 123.0954 | 122.9383 | 66.7057 | -123.4389
2003.7969 | 123.2941 | -66.687 | 56.3187 | 0.012286 | -0.02488 | -0.00017946 | 0.053081 | -0.0069462 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056535 | 0.034361 | 0.056599 | -66.7244 | -0.007751 | -66.7506 | 56.2976 | 56.2204 | 56.4084 | -66.8879 | -66.7474 | -0.017956 | -66.7773 | 56.2031 | 56.3855 | 56.2467 | -67.1385 | -0.20087 | -0.021042 | -0.037365 | -0.063571 | 0.1373 | -0.09827 | 0.089747 | -0.4515 | -0.11554 | -0.060373 | -0.090299 | 0.3612 | 0.066796 | -0.07194 | 122.9846 | 122.9074 | 123.0954 | 66.6793 | -123.2065 | 122.8901 | 123.0725 | 122.9337 | 66.6691 | -123.4572
2004.7969 | 123.1796 | -66.7465 | 56.3507 | -0.0029761 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0065188 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056108 | 0.034574 | 0.056812 | -66.729 | -0.003172 | -66.7552 | 56.2885 | 56.2204 | 56.413 | -66.8741 | -66.7382 | -0.017956 | -66.7819 | 56.1985 | 56.3809 | 56.2193 | -67.1339 | -0.12762 | -0.062242 | 0.017565 | -0.00864 | 0.11898 | -0.13031 | 0.062283 | -0.38741 | -0.15216 | 0.008294 | -0.035369 | 0.35204 | 0.030174 | -0.13145 | 123.035 | 122.9669 | 123.1595 | 66.7433 | -123.2249 | 122.9451 | 123.1274 | 122.9658 | 66.7286 | -123.4846
2005.8594 | 123.2758 | -66.7191 | 56.2775 | -0.0029761 | -0.025307 | -0.00017946 | 0.053295 | -0.0071598 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056535 | 0.034788 | 0.05724 | -66.7244 | -0.003172 | -66.7552 | 56.293 | 56.2112 | 56.4038 | -66.8879 | -66.7474 | -0.013377 | -66.7773 | 56.2031 | 56.3855 | 56.2147 | -67.1339 | -0.16883 | 0.015578 | -0.005322 | -0.036106 | 0.13272 | -0.066229 | 0.12637 | -0.41487 | -0.074342 | -0.02833 | -0.058256 | 0.35662 | 0.108 | -0.062791 | 123.0121 | 122.9303 | 123.1229 | 66.7159 | -123.1653 | 122.9222 | 123.1045 | 122.9337 | 66.7057 | -123.4114
2006.7969 | 123.1613 | -66.774 | 56.3644 | -0.0029761 | -0.025307 | -0.00017946 | 0.053081 | -0.0069462 | 0.062717 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056749 | 0.034788 | 0.056812 | -66.7198 | -0.003172 | -66.7552 | 56.2976 | 56.2387 | 56.4176 | -66.8741 | -66.7474 | -0.013377 | -66.7819 | 56.2077 | 56.3855 | 56.2193 | -67.1385 | -0.10016 | -0.066818 | 0.054188 | 0.018826 | 0.11898 | -0.12573 | 0.053129 | -0.36452 | -0.15674 | 0.026602 | -0.007903 | 0.35662 | 0.02102 | -0.14519 | 123.0716 | 123.0127 | 123.1916 | 66.7708 | -123.2386 | 122.9817 | 123.1594 | 122.9932 | 66.7606 | -123.5029
2007.7969 | 123.2895 | -66.6779 | 56.3416 | 0.0046549 | -0.02488 | 0.00024794 | 0.053081 | -0.0067326 | 0.06293 | 0.015414 | -0.0028393 | -0.00076913 | 0.056535 | 0.034574 | 0.057026 | -66.729 | -0.007751 | -66.7506 | 56.293 | 56.2067 | 56.4176 | -66.8925 | -66.7428 | -0.017956 | -66.7865 | 56.1985 | 56.3809 | 56.2193 | -67.1385 | -0.2146 | -0.048509 | -0.0511 | -0.072727 | 0.14188 | -0.1349 | 0.076017 | -0.46065 | -0.14301 | -0.06495 | -0.10861 | 0.35204 | 0.039329 | -0.1223 | 122.9709 | 122.8845 | 123.0954 | 66.6701 | -123.234 | 122.8764 | 123.0587 | 122.8971 | 66.6599 | -123.4801
2008.875 | 123.2025 | -66.7236 | 56.2866 | -0.0029761 | -0.025307 | -0.00017946 | 0.053295 | -0.0069462 | 0.06293 | -0.0074779 | -0.0030529 | -0.00076913 | 0.056322 | 0.034361 | 0.057026 | -66.7335 | -0.003172 | -66.746 | 56.293 | 56.225 | 56.4084 | -66.8879 | -66.7474 | -0.013377 | -66.7773 | 56.1985 | 56.3855 | 56.2467 | -67.1339 | -0.16425 | 0.006423 | -0.009901 | -0.022372 | 0.14188 | -0.061648 | 0.12179 | -0.4103 | -0.088076 | -0.023752 | -0.053678 | 0.35662 | 0.09884 | -0.039896 | 123.0167 | 122.9486 | 123.132 | 66.7205 | -123.1745 | 122.9222 | 123.1091 | 122.9704 | 66.7103 | -123.4205
2009.7969 | 123.2346 | -66.7236 | 56.3416 | 0.0046549 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056108 | 0.034361 | 0.056812 | -66.729 | -0.012329 | -66.746 | 56.293 | 56.225 | 56.413 | -66.8879 | -66.7428 | -0.013377 | -66.7819 | 56.1985 | 56.39 | 56.2147 | -67.1385 | -0.16425 | -0.048509 | -0.005323 | -0.022372 | 0.14188 | -0.11658 | 0.071438 | -0.41487 | -0.14301 | -0.019173 | -0.058257 | 0.35662 | 0.048486 | -0.12688 | 123.0167 | 122.9486 | 123.1366 | 66.7113 | -123.2294 | 122.9222 | 123.1137 | 122.9383 | 66.7103 | -123.4801
2010.7969 | 123.2254 | -66.7511 | 56.337 | -0.0029761 | -0.025307 | 0.00024794 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.034574 | 0.056812 | -66.729 | -0.007751 | -66.7506 | 56.3022 | 56.2204 | 56.4221 | -66.8925 | -66.7382 | -0.017956 | -66.7865 | 56.194 | 56.3855 | 56.2238 | -67.1339 | -0.14136 | -0.034774 | 0.022143 | 0.000516 | 0.14188 | -0.11658 | 0.085173 | -0.38283 | -0.14301 | 0.012872 | -0.03537 | 0.34746 | 0.048486 | -0.11314 | 123.0533 | 122.9715 | 123.1732 | 66.7433 | -123.2294 | 122.9451 | 123.1366 | 122.9749 | 66.7331 | -123.4709
2011.7969 | 123.1796 | -66.7465 | 56.3416 | 0.012286 | -0.025521 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062503 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056963 | 0.034574 | 0.056599 | -66.729 | -0.003172 | -66.7552 | 56.293 | 56.2296 | 56.4176 | -66.8925 | -66.7428 | -0.008798 | -66.7865 | 56.1985 | 56.3855 | 56.2193 | -67.1385 | -0.14594 | -0.048509 | 0.017565 | -0.00864 | 0.1373 | -0.112 | 0.076017 | -0.39199 | -0.14301 | 0.003715 | -0.039948 | 0.35204 | 0.043908 | -0.1223 | 123.0396 | 122.9761 | 123.1641 | 66.7433 | -123.234 | 122.9451 | 123.132 | 122.9658 | 66.7377 | -123.4801
2012.7969 | 123.1979 | -66.7191 | 56.3278 | -0.010607 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056749 | 0.034361 | 0.05724 | -66.729 | -0.003172 | -66.7506 | 56.293 | 56.2296 | 56.413 | -66.8879 | -66.7474 | -0.022535 | -66.7773 | 56.194 | 56.39 | 56.2238 | -67.1385 | -0.16883 | -0.034776 | -0.009901 | -0.031528 | 0.1373 | -0.098268 | 0.085171 | -0.41945 | -0.13385 | -0.02833 | -0.058256 | 0.3612 | 0.062219 | -0.10399 | 123.0121 | 122.9486 | 123.132 | 66.7159 | -123.2157 | 122.913 | 123.1091 | 122.9429 | 66.6965 | -123.4663
2013.7969 | 123.1705 | -66.7419 | 56.3324 | -0.010607 | -0.025521 | 3.4136e-05 | 0.052867 | -0.0069462 | 0.062503 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.034574 | 0.056812 | -66.7335 | -0.003172 | -66.7506 | 56.2885 | 56.2204 | 56.4084 | -66.8879 | -66.7382 | -0.008798 | -66.7819 | 56.194 | 56.39 | 56.2284 | -67.1339 | -0.14594 | -0.043931 | 0.008409 | -0.00864 | 0.1373 | -0.112 | 0.076015 | -0.39199 | -0.13843 | 0.003716 | -0.039947 | 0.35204 | 0.057642 | -0.10399 | 123.0304 | 122.9623 | 123.1504 | 66.7388 | -123.2203 | 122.9359 | 123.132 | 122.9704 | 66.7331 | -123.4663
2014.8906 | 123.2391 | -66.7191 | 56.2866 | 0.0046549 | -0.025307 | 0.00024794 | 0.053508 | -0.0069462 | 0.06293 | 0.00015261 | -0.0026255 | -0.00098273 | 0.056322 | 0.034574 | 0.056812 | -66.7244 | -0.012329 | -66.7643 | 56.2885 | 56.2204 | 56.413 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.3946 | 56.2467 | -67.1294 | -0.16883 | 0.001845 | -0.005322 | -0.045263 | 0.12356 | -0.066226 | 0.12637 | -0.4103 | -0.083497 | -0.02833 | -0.067414 | 0.34288 | 0.108 | -0.039896 | 123.0075 | 122.9394 | 123.132 | 66.7067 | -123.1745 | 122.9222 | 123.1137 | 122.9658 | 66.7057 | -123.416
2015.7969 | 123.175 | -66.7557 | 56.3599 | 0.0046549 | -0.025521 | -0.00017946 | 0.053081 | -0.0071598 | 0.063144 | -0.015108 | -0.0028393 | -0.00076913 | 0.056749 | 0.034788 | 0.057453 | -66.7244 | -0.003172 | -66.7643 | 56.293 | 56.2204 | 56.413 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.1985 | 56.3855 | 56.2376 | -67.1294 | -0.12763 | -0.066819 | 0.031299 | -0.008642 | 0.11898 | -0.13947 | 0.053128 | -0.37367 | -0.16132 | 0.01287 | -0.030793 | 0.34288 | 0.025598 | -0.12229 | 123.0487 | 122.9761 | 123.1687 | 66.7525 | -123.2432 | 122.9542 | 123.1411 | 122.9932 | 66.7377 | -123.4892
2016.7969 | 123.1659 | -66.7328 | 56.3187 | 0.0046549 | -0.025521 | 3.4136e-05 | 0.052654 | -0.0065188 | 0.062289 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056322 | 0.034788 | 0.05724 | -66.729 | -0.007751 | -66.7597 | 56.2976 | 56.2112 | 56.4176 | -66.8879 | -66.7428 | -0.017956 | -66.7819 | 56.1985 | 56.39 | 56.2284 | -67.1339 | -0.15509 | -0.021042 | 0.003832 | -0.026952 | 0.12814 | -0.10743 | 0.098905 | -0.40114 | -0.12012 | -0.010018 | -0.049102 | 0.35204 | 0.071374 | -0.090254 | 123.0304 | 122.944 | 123.1504 | 66.725 | -123.2065 | 122.9313 | 123.1228 | 122.9612 | 66.7148 | -123.4526
2017.7969 | 123.1705 | -66.7328 | 56.3187 | -0.0029761 | -0.025521 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062717 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056322 | 0.034788 | 0.057026 | -66.7381 | -0.003172 | -66.7643 | 56.293 | 56.225 | 56.4176 | -66.8879 | -66.7474 | -0.008798 | -66.7773 | 56.194 | 56.3855 | 56.2193 | -67.1339 | -0.15509 | -0.025621 | -0.005324 | -0.03153 | 0.12356 | -0.093692 | 0.098905 | -0.40114 | -0.1247 | -0.014597 | -0.044523 | 0.35662 | 0.066796 | -0.099411 | 123.0258 | 122.9578 | 123.1504 | 66.7296 | -123.2065 | 122.9268 | 123.1182 | 122.952 | 66.724 | -123.4526
2018.7969 | 123.23 | -66.7282 | 56.3004 | -0.0029761 | -0.025094 | -0.00017946 | 0.053295 | -0.0069462 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056535 | 0.034574 | 0.056812 | -66.729 | -0.007751 | -66.7597 | 56.3022 | 56.2341 | 56.413 | -66.8787 | -66.7474 | -0.00422 | -66.7865 | 56.2031 | 56.3855 | 56.2284 | -67.1339 | -0.15051 | 0.001847 | -0.000746 | -0.03153 | 0.11898 | -0.066223 | 0.11264 | -0.40572 | -0.09723 | -0.019175 | -0.058259 | 0.34746 | 0.085107 | -0.071943 | 123.0304 | 122.9623 | 123.1412 | 66.7205 | -123.1791 | 122.9313 | 123.1137 | 122.9566 | 66.724 | -123.4343
2019.8906 | 123.2346 | -66.6962 | 56.3095 | -0.010607 | -0.025094 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.06293 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056535 | 0.034574 | 0.05724 | -66.7244 | -0.007751 | -66.7689 | 56.2976 | 56.2204 | 56.413 | -66.8787 | -66.752 | -0.017956 | -66.791 | 56.2077 | 56.39 | 56.2009 | -67.1339 | -0.18256 | -0.011886 | -0.02821 | -0.072729 | 0.10983 | -0.089114 | 0.10348 | -0.43776 | -0.10181 | -0.055796 | -0.09488 | 0.34288 | 0.08053 | -0.10857 | 122.9938 | 122.9166 | 123.1092 | 66.6884 | -123.1882 | 122.9039 | 123.0862 | 122.8971 | 66.6782 | -123.4434
2020.7969 | 123.2025 | -66.7694 | 56.3141 | -0.0029761 | -0.025521 | -0.00039306 | 0.053081 | -0.0065188 | 0.062503 | -0.0074779 | -0.0030529 | -0.00076913 | 0.056535 | 0.034574 | 0.05724 | -66.729 | -0.016908 | -66.7643 | 56.2976 | 56.2296 | 56.413 | -66.8833 | -66.7565 | -0.008798 | -66.7727 | 56.1985 | 56.3855 | 56.2101 | -67.1339 | -0.11389 | -0.016464 | 0.040453 | 0.005091 | 0.11898 | -0.084535 | 0.098904 | -0.36452 | -0.11554 | 0.012867 | -0.003323 | 0.3612 | 0.071374 | -0.10399 | 123.067 | 122.999 | 123.1824 | 66.7525 | -123.1974 | 122.968 | 123.1549 | 122.9795 | 66.7606 | -123.448
2021.7969 | 123.2437 | -66.7374 | 56.3232 | -0.0029761 | -0.025521 | -0.00017946 | 0.053081 | -0.0071598 | 0.062717 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056535 | 0.035215 | 0.057026 | -66.7335 | -0.012329 | -66.7643 | 56.3022 | 56.2296 | 56.413 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.39 | 56.2238 | -67.1294 | -0.14594 | -0.021041 | 0.003832 | -0.026952 | 0.11898 | -0.09369 | 0.089749 | -0.39198 | -0.11554 | -0.010019 | -0.049103 | 0.34288 | 0.066797 | -0.09941 | 123.0396 | 122.9669 | 123.1504 | 66.725 | -123.2065 | 122.9451 | 123.1274 | 122.9612 | 66.724 | -123.4526
2022.8594 | 123.1705 | -66.7648 | 56.3324 | 0.0046549 | -0.025307 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | 0.015414 | -0.0030529 | -0.00076913 | 0.056322 | 0.035215 | 0.056812 | -66.729 | -0.007751 | -66.7735 | 56.2976 | 56.225 | 56.4084 | -66.8925 | -66.7428 | -0.017956 | -66.7773 | 56.194 | 56.39 | 56.233 | -67.1294 | -0.12763 | -0.034774 | 0.035876 | -0.008642 | 0.11899 | -0.10742 | 0.076015 | -0.36452 | -0.13843 | 0.022026 | -0.012479 | 0.35204 | 0.057642 | -0.099407 | 123.0625 | 122.9898 | 123.1732 | 66.7571 | -123.2249 | 122.9588 | 123.1549 | 122.9978 | 66.7469 | -123.4617
2023.7969 | 123.2574 | -66.7236 | 56.2866 | -0.010607 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.056749 | 0.034788 | 0.05724 | -66.7244 | -0.012329 | -66.7643 | 56.293 | 56.2112 | 56.4176 | -66.8787 | -66.7565 | -0.017956 | -66.7773 | 56.2031 | 56.3809 | 56.2421 | -67.1294 | -0.15509 | 0.006423 | -0.000744 | -0.040685 | 0.11441 | -0.075384 | 0.13095 | -0.40572 | -0.083497 | -0.032909 | -0.053678 | 0.35204 | 0.094261 | -0.044474 | 123.0167 | 122.9349 | 123.1412 | 66.7113 | -123.1653 | 122.9268 | 123.1045 | 122.9658 | 66.7057 | -123.416
2024.8125 | 123.1338 | -66.774 | 56.3278 | -0.010607 | -0.025735 | 0.00024794 | 0.053081 | -0.0067326 | 0.062717 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056535 | 0.034788 | 0.056812 | -66.729 | -0.012329 | -66.7689 | 56.293 | 56.2112 | 56.4176 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.1985 | 56.3855 | 56.2238 | -67.1339 | -0.10932 | -0.034776 | 0.045031 | 0.005091 | 0.11441 | -0.11658 | 0.08975 | -0.35994 | -0.12927 | 0.026602 | -0.012482 | 0.34746 | 0.057641 | -0.10399 | 123.067 | 122.9852 | 123.1916 | 66.7617 | -123.2111 | 122.9725 | 123.1594 | 122.9978 | 66.7606 | -123.4617
2025.7969 | 123.2025 | -66.7374 | 56.3004 | -0.0029761 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.034574 | 0.057026 | -66.7244 | -0.012329 | -66.7689 | 56.2885 | 56.225 | 56.4176 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2031 | 56.3855 | 56.2147 | -67.1339 | -0.14594 | -0.011888 | 0.012989 | -0.03153 | 0.11441 | -0.075381 | 0.11722 | -0.39656 | -0.09723 | -0.00544 | -0.049103 | 0.34746 | 0.085107 | -0.085679 | 123.0258 | 122.9623 | 123.1549 | 66.725 | -123.1837 | 122.9405 | 123.1228 | 122.952 | 66.724 | -123.4343
2026.7969 | 123.2529 | -66.7053 | 56.2775 | -0.010607 | -0.025735 | 3.4136e-05 | 0.053508 | -0.0073736 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056322 | 0.035002 | 0.057026 | -66.729 | -0.007751 | -66.7643 | 56.2885 | 56.2158 | 56.4176 | -66.8787 | -66.7474 | -0.022535 | -66.7865 | 56.2077 | 56.3763 | 56.2284 | -67.1385 | -0.1734 | 0.011 | -0.023634 | -0.058996 | 0.11441 | -0.06165 | 0.1401 | -0.43319 | -0.069764 | -0.042063 | -0.081147 | 0.35204 | 0.098837 | -0.049055 | 122.9938 | 122.9211 | 123.1229 | 66.6976 | -123.1562 | 122.913 | 123.0816 | 122.9337 | 66.6828 | -123.416
2027.7969 | 123.2483 | -66.7282 | 56.3324 | 0.019917 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062076 | 0.00015261 | -0.0028393 | -0.00098273 | 0.056108 | 0.034788 | 0.056812 | -66.7198 | -0.012329 | -66.7597 | 56.293 | 56.2296 | 56.4084 | -66.8833 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3809 | 56.233 | -67.1339 | -0.15509 | -0.039353 | 0.008411 | -0.03153 | 0.12356 | -0.10285 | 0.076015 | -0.40572 | -0.12927 | -0.019175 | -0.05368 | 0.35204 | 0.048485 | -0.099407 | 123.0213 | 122.9578 | 123.1366 | 66.7159 | -123.2157 | 122.9313 | 123.1091 | 122.9612 | 66.7148 | -123.4663
2028.7969 | 123.1476 | -66.7511 | 56.3553 | -0.0029761 | -0.025307 | -0.00017946 | 0.053295 | -0.0069462 | 0.06293 | 0.0077831 | -0.0034801 | -0.00055553 | 0.056749 | 0.034788 | 0.05724 | -66.729 | -0.012329 | -66.7597 | 56.3022 | 56.2296 | 56.4176 | -66.8833 | -66.7474 | -0.017956 | -66.7865 | 56.2077 | 56.3855 | 56.2193 | -67.1248 | -0.1322 | -0.053085 | 0.022143 | -0.008641 | 0.12356 | -0.12573 | 0.062284 | -0.37367 | -0.14758 | 0.003714 | -0.03537 | 0.3383 | 0.030175 | -0.13603 | 123.0533 | 122.9807 | 123.1687 | 66.7388 | -123.2386 | 122.9588 | 123.1366 | 122.9704 | 66.7331 | -123.4801
2029.875 | 123.2986 | -66.6641 | 56.3187 | 0.0046549 | -0.025735 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00098273 | 0.056322 | 0.035002 | 0.056599 | -66.7335 | -0.003172 | -66.7552 | 56.2885 | 56.225 | 56.413 | -66.8787 | -66.7565 | -0.017956 | -66.7865 | 56.2031 | 56.3855 | 56.2376 | -67.1339 | -0.2146 | -0.030199 | -0.06941 | -0.091037 | 0.12356 | -0.093692 | 0.094326 | -0.4698 | -0.11554 | -0.092418 | -0.12234 | 0.34746 | 0.066796 | -0.081097 | 122.9526 | 122.8891 | 123.0771 | 66.661 | -123.1974 | 122.8672 | 123.0496 | 122.9017 | 66.6462 | -123.4526
2030.7969 | 123.2391 | -66.7145 | 56.3095 | -0.0029761 | -0.025735 | 0.00024794 | 0.053508 | -0.0067326 | 0.062717 | 0.0077831 | -0.0024119 | -0.00034193 | 0.056535 | 0.034788 | 0.056812 | -66.7335 | -0.007751 | -66.7506 | 56.2885 | 56.2067 | 56.413 | -66.8787 | -66.7474 | -0.017956 | -66.7865 | 56.194 | 56.39 | 56.2147 | -67.1339 | -0.16425 | -0.021043 | -0.019056 | -0.036105 | 0.12814 | -0.10285 | 0.10348 | -0.41945 | -0.11554 | -0.032907 | -0.071991 | 0.34746 | 0.08053 | -0.094834 | 123.0029 | 122.9211 | 123.1275 | 66.7067 | -123.1882 | 122.9084 | 123.1045 | 122.9292 | 66.6965 | -123.4434
2031.7969 | 123.2758 | -66.7007 | 56.3004 | -0.010607 | -0.025307 | 3.4136e-05 | 0.053081 | -0.0065188 | 0.062503 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056108 | 0.035215 | 0.057026 | -66.729 | -0.007751 | -66.7552 | 56.2885 | 56.2021 | 56.4084 | -66.8833 | -66.7382 | -0.008798 | -66.7865 | 56.1985 | 56.3809 | 56.2284 | -67.1294 | -0.18256 | -0.011888 | -0.028211 | -0.054416 | 0.12814 | -0.098275 | 0.10806 | -0.42861 | -0.10181 | -0.037482 | -0.085724 | 0.34288 | 0.080528 | -0.071943 | 122.9892 | 122.9028 | 123.1092 | 66.693 | -123.1837 | 122.8993 | 123.0816 | 122.9292 | 66.6919 | -123.4297
2032.7969 | 123.2849 | -66.6779 | 56.2866 | 0.0046549 | -0.025521 | 0.00024794 | 0.053295 | -0.0069462 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056535 | 0.035215 | 0.056599 | -66.729 | -0.012329 | -66.7552 | 56.293 | 56.2204 | 56.413 | -66.8787 | -66.752 | -0.013377 | -66.7819 | 56.1985 | 56.3763 | 56.2101 | -67.1339 | -0.20087 | 0.006423 | -0.0511 | -0.077305 | 0.12356 | -0.066226 | 0.12637 | -0.45607 | -0.088076 | -0.074107 | -0.10403 | 0.35204 | 0.089682 | -0.076524 | 122.9709 | 122.8983 | 123.0908 | 66.6655 | -123.1653 | 122.8764 | 123.0542 | 122.888 | 66.6645 | -123.4205
2033.7969 | 123.2437 | -66.7145 | 56.337 | 0.0046549 | -0.025735 | 0.00024794 | 0.053081 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056749 | 0.035002 | 0.056599 | -66.7335 | -0.021486 | -66.7552 | 56.2885 | 56.225 | 56.413 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.2031 | 56.39 | 56.2101 | -67.1385 | -0.16882 | -0.048509 | -0.019056 | -0.040683 | 0.12814 | -0.112 | 0.076016 | -0.42403 | -0.13385 | -0.028328 | -0.071991 | 0.35204 | 0.053064 | -0.12688 | 123.0029 | 122.9395 | 123.1275 | 66.693 | -123.2203 | 122.9176 | 123.1045 | 122.9246 | 66.6965 | -123.4755
2034.8906 | 123.1613 | -66.7465 | 56.3644 | 0.012286 | -0.025521 | -0.00017946 | 0.053081 | -0.0069462 | 0.062717 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056322 | 0.034788 | 0.057026 | -66.7198 | -0.012329 | -66.7506 | 56.2976 | 56.2387 | 56.413 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3809 | 56.2147 | -67.1339 | -0.1322 | -0.066818 | 0.026722 | -0.004062 | 0.12814 | -0.12573 | 0.04855 | -0.38741 | -0.16132 | -0.000864 | -0.035369 | 0.35204 | 0.016441 | -0.14977 | 123.0441 | 122.9852 | 123.1595 | 66.7342 | -123.2432 | 122.9496 | 123.1274 | 122.9612 | 66.7331 | -123.4984
2035.7969 | 123.2574 | -66.7099 | 56.2729 | 0.0046549 | -0.025735 | -0.00017946 | 0.052867 | -0.0069462 | 0.062717 | 0.00015261 | -0.0032665 | -0.00034193 | 0.056322 | 0.035002 | 0.056812 | -66.7244 | -0.007751 | -66.7552 | 56.293 | 56.225 | 56.413 | -66.8879 | -66.7382 | -0.017956 | -66.7819 | 56.1985 | 56.39 | 56.2238 | -67.1294 | -0.17798 | 0.020156 | -0.014477 | -0.045261 | 0.13272 | -0.047915 | 0.1401 | -0.41945 | -0.074343 | -0.028327 | -0.07199 | 0.34746 | 0.11715 | -0.049056 | 123.0029 | 122.9349 | 123.1229 | 66.7021 | -123.1608 | 122.9084 | 123.0999 | 122.9337 | 66.6919 | -123.4022
2036.8594 | 123.2483 | -66.7099 | 56.3187 | 0.0046549 | -0.025735 | -0.00017946 | 0.053508 | -0.0069462 | 0.06293 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056322 | 0.034788 | 0.056812 | -66.729 | -0.003172 | -66.746 | 56.293 | 56.2296 | 56.4176 | -66.8787 | -66.752 | -0.013377 | -66.7819 | 56.2031 | 56.39 | 56.2101 | -67.1339 | -0.16882 | -0.025621 | -0.019056 | -0.036105 | 0.13272 | -0.089113 | 0.098905 | -0.42403 | -0.11554 | -0.042063 | -0.07199 | 0.35204 | 0.071374 | -0.10857 | 123.0029 | 122.9395 | 123.1275 | 66.7067 | -123.1974 | 122.913 | 123.0999 | 122.92 | 66.6965 | -123.4526
2037.7969 | 123.2712 | -66.7007 | 56.3278 | 0.0046549 | -0.025735 | -0.00017946 | 0.053508 | -0.0069462 | 0.06293 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.034361 | 0.056812 | -66.7381 | -0.003172 | -66.7643 | 56.2976 | 56.2296 | 56.4221 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.1985 | 56.3855 | 56.2009 | -67.1385 | -0.18256 | -0.030197 | -0.037367 | -0.063573 | 0.11898 | -0.098268 | 0.094328 | -0.43776 | -0.12927 | -0.04664 | -0.085724 | 0.35204 | 0.057641 | -0.12688 | 122.9984 | 122.9303 | 123.1229 | 66.6976 | -123.2111 | 122.8993 | 123.0862 | 122.9017 | 66.6874 | -123.4663
2038.7969 | 123.1659 | -66.7328 | 56.3782 | 0.0046549 | -0.025735 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056322 | 0.034788 | 0.056812 | -66.7335 | -0.007751 | -66.7597 | 56.2976 | 56.225 | 56.4176 | -66.8879 | -66.7474 | -0.013377 | -66.7773 | 56.2077 | 56.3946 | 56.2467 | -67.1294 | -0.15509 | -0.080551 | -0.000746 | -0.026952 | 0.12814 | -0.1532 | 0.039396 | -0.39656 | -0.17047 | -0.014597 | -0.044523 | 0.35204 | 0.016444 | -0.13145 | 123.0304 | 122.9578 | 123.1504 | 66.725 | -123.2661 | 122.9405 | 123.1274 | 122.9795 | 66.7194 | -123.5075
2039.8125 | 123.2254 | -66.6962 | 56.3278 | -0.0029761 | -0.025948 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.035215 | 0.056812 | -66.7381 | -0.003172 | -66.7552 | 56.2976 | 56.2158 | 56.4084 | -66.8833 | -66.7428 | -0.017956 | -66.7865 | 56.2031 | 56.39 | 56.2467 | -67.1431 | -0.18714 | -0.030197 | -0.041945 | -0.058994 | 0.12814 | -0.112 | 0.080592 | -0.44692 | -0.1247 | -0.046639 | -0.090302 | 0.35662 | 0.062219 | -0.081095 | 122.9938 | 122.912 | 123.1046 | 66.693 | -123.2111 | 122.8993 | 123.0862 | 122.9429 | 66.6782 | -123.4709
2040.8594 | 123.2803 | -66.7053 | 56.3095 | 0.012286 | -0.025948 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062503 | 0.00015261 | -0.0024119 | -0.00055553 | 0.056535 | 0.035002 | 0.057026 | -66.729 | -0.012329 | -66.7414 | 56.2976 | 56.2204 | 56.4221 | -66.8787 | -66.7428 | -0.022535 | -66.7865 | 56.2077 | 56.39 | 56.2193 | -67.1339 | -0.1734 | -0.011886 | -0.023634 | -0.036105 | 0.1373 | -0.089114 | 0.11264 | -0.42861 | -0.10181 | -0.037484 | -0.081147 | 0.34746 | 0.08053 | -0.090255 | 123.0029 | 122.9257 | 123.1275 | 66.693 | -123.1882 | 122.913 | 123.0954 | 122.9246 | 66.6828 | -123.4434
2041.7969 | 123.2529 | -66.7236 | 56.3187 | 0.0046549 | -0.025521 | -0.00017946 | 0.053295 | -0.0069462 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056749 | 0.035002 | 0.056599 | -66.7244 | -0.007751 | -66.7368 | 56.2885 | 56.2296 | 56.4084 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2031 | 56.39 | 56.2193 | -67.1385 | -0.15967 | -0.030199 | -0.000744 | -0.013215 | 0.14646 | -0.089113 | 0.089747 | -0.41487 | -0.11554 | -0.019173 | -0.062836 | 0.35204 | 0.071374 | -0.099411 | 123.0121 | 122.9532 | 123.132 | 66.7159 | -123.202 | 122.9268 | 123.1137 | 122.9429 | 66.7103 | -123.4572
2042.7969 | 123.2391 | -66.7007 | 56.3736 | 0.0046549 | -0.025521 | -0.00017946 | 0.053295 | -0.0067326 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.035429 | 0.05724 | -66.729 | -0.007751 | -66.7414 | 56.2976 | 56.2296 | 56.413 | -66.8879 | -66.7428 | -0.017956 | -66.7819 | 56.2031 | 56.39 | 56.2238 | -67.1385 | -0.18714 | -0.075973 | -0.028211 | -0.040682 | 0.14646 | -0.14404 | 0.039395 | -0.43776 | -0.17047 | -0.042061 | -0.081145 | 0.35662 | 0.016443 | -0.14976 | 122.9984 | 122.9303 | 123.1137 | 66.693 | -123.2615 | 122.9039 | 123.0908 | 122.9246 | 66.6828 | -123.5121
2043.8594 | 123.3078 | -66.6962 | 56.3232 | 0.0046549 | -0.025735 | -0.00017946 | 0.053295 | -0.0071598 | 0.062717 | 0.0077831 | -0.0028393 | -0.00034193 | 0.056322 | 0.034574 | 0.056812 | -66.7244 | -0.007751 | -66.7552 | 56.3022 | 56.2204 | 56.4084 | -66.8879 | -66.7565 | -0.008798 | -66.7819 | 56.1985 | 56.39 | 56.2193 | -67.1339 | -0.19172 | -0.021041 | -0.02821 | -0.058994 | 0.13272 | -0.10285 | 0.08517 | -0.43776 | -0.1247 | -0.060375 | -0.085723 | 0.35204 | 0.066797 | -0.10399 | 122.9984 | 122.9166 | 123.1046 | 66.6884 | -123.2111 | 122.8947 | 123.0862 | 122.9154 | 66.6874 | -123.4572
2044.7969 | 123.1338 | -66.7328 | 56.3461 | -0.0029761 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056749 | 0.035002 | 0.056812 | -66.7198 | -0.003172 | -66.7552 | 56.2976 | 56.2158 | 56.4084 | -66.8833 | -66.7474 | -0.013377 | -66.7819 | 56.1985 | 56.3946 | 56.2284 | -67.1385 | -0.15051 | -0.048507 | 0.012989 | -0.022373 | 0.12814 | -0.13031 | 0.062282 | -0.40572 | -0.14758 | -0.014597 | -0.049102 | 0.35662 | 0.048488 | -0.11772 | 123.0304 | 122.9486 | 123.1412 | 66.7296 | -123.2294 | 122.9313 | 123.1274 | 122.9612 | 66.7194 | -123.4846
2045.8594 | 123.2529 | -66.7282 | 56.3141 | 0.0046549 | -0.025521 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062289 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056322 | 0.035215 | 0.056812 | -66.7335 | -0.007751 | -66.7552 | 56.3022 | 56.2296 | 56.4176 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.1985 | 56.3946 | 56.2101 | -67.1339 | -0.15967 | -0.011886 | -0.005324 | -0.026951 | 0.13272 | -0.084535 | 0.10348 | -0.40572 | -0.11554 | -0.019175 | -0.058259 | 0.34746 | 0.080531 | -0.10399 | 123.0304 | 122.9578 | 123.1458 | 66.7205 | -123.202 | 122.9268 | 123.1228 | 122.9383 | 66.7194 | -123.448
2046.7969 | 123.2117 | -66.7603 | 56.3507 | 0.0046549 | -0.025735 | 0.00024794 | 0.053295 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056535 | 0.035215 | 0.057026 | -66.7244 | 0.001407 | -66.7506 | 56.2976 | 56.2112 | 56.4176 | -66.8833 | -66.7428 | -0.00422 | -66.7865 | 56.2077 | 56.3855 | 56.2284 | -67.1339 | -0.12305 | -0.053085 | 0.035877 | 0.009671 | 0.13272 | -0.13947 | 0.066862 | -0.37367 | -0.14301 | 0.017448 | -0.026215 | 0.34746 | 0.034753 | -0.1223 | 123.0579 | 122.9715 | 123.1778 | 66.7617 | -123.234 | 122.968 | 123.1457 | 122.9887 | 66.756 | -123.4846
2047.7969 | 123.1705 | -66.7191 | 56.3461 | -0.0029761 | -0.025521 | -0.00017946 | 0.052867 | -0.0067326 | 0.062503 | 0.015414 | -0.0028393 | -0.00034193 | 0.056535 | 0.035002 | 0.056812 | -66.729 | -0.012329 | -66.7552 | 56.2839 | 56.2158 | 56.4176 | -66.8833 | -66.7474 | -0.017956 | -66.7819 | 56.2031 | 56.39 | 56.2193 | -67.1339 | -0.16425 | -0.062243 | -0.009901 | -0.036106 | 0.12814 | -0.13031 | 0.07144 | -0.41487 | -0.14301 | -0.02833 | -0.062835 | 0.35204 | 0.043909 | -0.12688 | 123.0029 | 122.9349 | 123.1366 | 66.7067 | -123.2294 | 122.9222 | 123.1091 | 122.9383 | 66.7011 | -123.4801
2048.7969 | 123.23 | -66.7099 | 56.337 | -0.0029761 | -0.025948 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.06293 | 0.0077831 | -0.0028393 | -0.00034193 | 0.056535 | 0.035215 | 0.056812 | -66.7244 | -0.012329 | -66.7506 | 56.3114 | 56.225 | 56.4221 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.194 | 56.3946 | 56.2193 | -67.1431 | -0.1734 | -0.025617 | -0.014477 | -0.040683 | 0.13272 | -0.112 | 0.085173 | -0.43319 | -0.14301 | -0.037485 | -0.076569 | 0.35662 | 0.057643 | -0.11772 | 123.0213 | 122.9349 | 123.132 | 66.6976 | -123.2203 | 122.9039 | 123.1045 | 122.9292 | 66.6965 | -123.4801
2049.7969 | 123.1384 | -66.7648 | 56.3141 | -0.010607 | -0.025735 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056749 | 0.035002 | 0.05724 | -66.7244 | -0.012329 | -66.7552 | 56.3022 | 56.2296 | 56.4176 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3855 | 56.2193 | -67.1339 | -0.11389 | -0.011886 | 0.040455 | 0.009671 | 0.12356 | -0.084535 | 0.10348 | -0.3691 | -0.11096 | 0.017447 | -0.017058 | 0.35204 | 0.071374 | -0.094833 | 123.067 | 122.9944 | 123.1824 | 66.7525 | -123.1928 | 122.968 | 123.1503 | 122.9841 | 66.7515 | -123.448
2050.8594 | 123.1338 | -66.7786 | 56.337 | -0.0029761 | -0.025735 | 0.00024794 | 0.052867 | -0.0069462 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.035215 | 0.056812 | -66.729 | -0.007751 | -66.7552 | 56.3022 | 56.225 | 56.4176 | -66.8833 | -66.7474 | -0.00422 | -66.7819 | 56.2031 | 56.39 | 56.2238 | -67.1339 | -0.10474 | -0.034774 | 0.049608 | 0.023403 | 0.12814 | -0.112 | 0.080595 | -0.35536 | -0.13385 | 0.031179 | -0.003326 | 0.35204 | 0.053064 | -0.11314 | 123.0808 | 123.0035 | 123.1961 | 66.7708 | -123.2203 | 122.9817 | 123.1686 | 123.0024 | 66.7743 | -123.4709
2051.7969 | 123.1842 | -66.7145 | 56.3278 | -0.0029761 | -0.025735 | 0.00024794 | 0.053081 | -0.0069462 | 0.062717 | 0.015414 | -0.0028393 | -0.00055553 | 0.056535 | 0.035215 | 0.056812 | -66.7244 | -0.003172 | -66.7552 | 56.3022 | 56.2387 | 56.4267 | -66.8879 | -66.7428 | -0.008798 | -66.791 | 56.2031 | 56.3855 | 56.2284 | -67.1339 | -0.1734 | -0.025619 | -0.009899 | -0.040683 | 0.13272 | -0.08911 | 0.098907 | -0.41945 | -0.1247 | -0.028328 | -0.076569 | 0.34288 | 0.057641 | -0.099409 | 123.0167 | 122.9532 | 123.1412 | 66.7113 | -123.2157 | 122.9176 | 123.0999 | 122.9429 | 66.7057 | -123.4617
2052.7969 | 123.1567 | -66.7648 | 56.3232 | 0.0046549 | -0.025521 | 0.00024794 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056749 | 0.035002 | 0.057026 | -66.7244 | -0.012329 | -66.7689 | 56.293 | 56.2112 | 56.4176 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2031 | 56.39 | 56.2376 | -67.1385 | -0.11847 | -0.030198 | 0.040455 | -0.004064 | 0.11441 | -0.11201 | 0.094328 | -0.37368 | -0.12012 | 0.017447 | -0.021637 | 0.35204 | 0.066797 | -0.085674 | 123.0579 | 122.9761 | 123.1824 | 66.7525 | -123.2065 | 122.968 | 123.1549 | 123.0024 | 66.756 | -123.4617
2053.7969 | 123.1293 | -66.7557 | 56.3278 | 0.012286 | -0.026162 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062717 | -0.0074779 | -0.0032665 | -0.00098273 | 0.056322 | 0.035002 | 0.056812 | -66.729 | 0.001407 | -66.7552 | 56.3022 | 56.225 | 56.4221 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2077 | 56.39 | 56.2101 | -67.1385 | -0.12763 | -0.025619 | 0.02672 | 0.000515 | 0.12814 | -0.10285 | 0.094328 | -0.38283 | -0.12012 | 0.008291 | -0.030793 | 0.35204 | 0.062219 | -0.11772 | 123.0579 | 122.9806 | 123.1778 | 66.7571 | -123.2111 | 122.9634 | 123.1457 | 122.9658 | 66.7469 | -123.4663
2054.7969 | 123.2483 | -66.7191 | 56.3049 | 0.0046549 | -0.025521 | -0.00017946 | 0.053722 | -0.0069462 | 0.062503 | 0.0077831 | -0.0028393 | -0.00034193 | 0.056322 | 0.035429 | 0.057026 | -66.7335 | 0.001407 | -66.7643 | 56.3022 | 56.225 | 56.413 | -66.8787 | -66.7428 | -0.013377 | -66.791 | 56.194 | 56.39 | 56.2238 | -67.1294 | -0.15967 | -0.002731 | -0.014479 | -0.045263 | 0.11441 | -0.079959 | 0.10806 | -0.4103 | -0.11097 | -0.023751 | -0.071992 | 0.3383 | 0.085107 | -0.0811 | 123.0213 | 122.944 | 123.132 | 66.7205 | -123.1837 | 122.913 | 123.1091 | 122.9429 | 66.7057 | -123.4343
2055.8594 | 123.1522 | -66.7374 | 56.3782 | 0.012286 | -0.025521 | 0.00024794 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056108 | 0.035215 | 0.057026 | -66.7244 | -0.003172 | -66.7552 | 56.2976 | 56.2296 | 56.4221 | -66.8787 | -66.7428 | -0.008798 | -66.7819 | 56.1985 | 56.3855 | 56.2238 | -67.1339 | -0.14136 | -0.080551 | 0.012989 | -0.017795 | 0.12356 | -0.14862 | 0.043974 | -0.39656 | -0.17963 | -0.00544 | -0.044524 | 0.35204 | 0.007287 | -0.15434 | 123.035 | 122.9669 | 123.1595 | 66.7342 | -123.2569 | 122.9359 | 123.1228 | 122.9612 | 66.7286 | -123.5121
2056.7969 | 123.143 | -66.7786 | 56.3416 | -0.0029761 | -0.025735 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00076913 | 0.056535 | 0.035215 | 0.056812 | -66.7244 | -0.003172 | -66.7552 | 56.2976 | 56.225 | 56.4267 | -66.8787 | -66.752 | -0.008798 | -66.7773 | 56.2031 | 56.3855 | 56.233 | -67.1385 | -0.10016 | -0.04393 | 0.054187 | 0.023403 | 0.12356 | -0.11658 | 0.085174 | -0.35994 | -0.13843 | 0.026601 | 0.001253 | 0.3612 | 0.043908 | -0.10856 | 123.0762 | 123.0035 | 123.2053 | 66.7754 | -123.2203 | 122.9817 | 123.164 | 123.0116 | 66.7698 | -123.4801
2057.7969 | 123.2117 | -66.7236 | 56.3461 | -0.010607 | -0.026162 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062503 | 0.0077831 | -0.0032665 | -0.00076913 | 0.056322 | 0.035215 | 0.057026 | -66.729 | -0.007751 | -66.7643 | 56.2885 | 56.2158 | 56.4221 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.39 | 56.2147 | -67.1431 | -0.16425 | -0.057664 | -0.005323 | -0.040685 | 0.12356 | -0.13031 | 0.076018 | -0.41945 | -0.14301 | -0.023752 | -0.062836 | 0.35662 | 0.043909 | -0.13146 | 123.0121 | 122.9394 | 123.1458 | 66.7159 | -123.234 | 122.9268 | 123.1137 | 122.9383 | 66.7103 | -123.4892
2058.8594 | 123.2346 | -66.7419 | 56.2958 | 0.0046549 | -0.025948 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056322 | 0.035215 | 0.056812 | -66.7244 | 0.001407 | -66.7552 | 56.293 | 56.2158 | 56.4221 | -66.8787 | -66.7382 | -0.008798 | -66.791 | 56.1985 | 56.3946 | 56.2238 | -67.1431 | -0.13678 | -0.002732 | 0.017566 | -0.013218 | 0.12356 | -0.07996 | 0.12637 | -0.40114 | -0.097231 | 0.003716 | -0.049104 | 0.35204 | 0.098842 | -0.071944 | 123.035 | 122.9578 | 123.1641 | 66.7434 | -123.1745 | 122.9405 | 123.1366 | 122.9658 | 66.7331 | -123.4389
2059.7969 | 123.2574 | -66.7282 | 56.2958 | -0.0029761 | -0.025735 | -0.00017946 | 0.053722 | -0.0071598 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056535 | 0.035002 | 0.056812 | -66.7335 | -0.012329 | -66.7597 | 56.293 | 56.2158 | 56.413 | -66.8833 | -66.7474 | -0.008798 | -66.7819 | 56.2031 | 56.3855 | 56.2284 | -67.1294 | -0.15509 | -0.002732 | -0.005324 | -0.03153 | 0.12356 | -0.07996 | 0.11722 | -0.40114 | -0.092652 | -0.019175 | -0.05368 | 0.34746 | 0.089685 | -0.067365 | 123.0213 | 122.944 | 123.1412 | 66.7159 | -123.1791 | 122.9313 | 123.1137 | 122.9566 | 66.7194 | -123.4251
2060.7969 | 123.2437 | -66.7236 | 56.2775 | -0.0029761 | -0.025735 | -0.00017946 | 0.053508 | -0.0067326 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056108 | 0.035002 | 0.057026 | -66.7198 | 0.005985 | -66.7643 | 56.2976 | 56.2204 | 56.4176 | -66.8879 | -66.7474 | -0.013377 | -66.7819 | 56.2123 | 56.3946 | 56.2238 | -67.1385 | -0.16425 | 0.020157 | 0.003834 | -0.040685 | 0.12356 | -0.057071 | 0.1401 | -0.41487 | -0.065185 | -0.023752 | -0.058257 | 0.35662 | 0.11715 | -0.053634 | 123.0213 | 122.944 | 123.1412 | 66.7296 | -123.1653 | 122.9359 | 123.1183 | 122.9475 | 66.7103 | -123.416
2061.8594 | 123.1567 | -66.7557 | 56.337 | -0.0029761 | -0.026162 | -0.00017946 | 0.053722 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.035215 | 0.057026 | -66.729 | -0.003172 | -66.7506 | 56.3022 | 56.2296 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7773 | 56.1985 | 56.39 | 56.2238 | -67.1339 | -0.13221 | -0.034774 | 0.02672 | 0.005093 | 0.1373 | -0.10742 | 0.089752 | -0.37825 | -0.13843 | 0.008291 | -0.021635 | 0.35662 | 0.053064 | -0.11314 | 123.0579 | 122.9852 | 123.1824 | 66.7525 | -123.2249 | 122.9542 | 123.1457 | 122.9795 | 66.7469 | -123.4709
2062.7969 | 123.2712 | -66.7328 | 56.2912 | -0.010607 | -0.025948 | 0.00046154 | 0.053508 | -0.0065188 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056322 | 0.035643 | 0.056599 | -66.7198 | -0.007751 | -66.7552 | 56.293 | 56.2204 | 56.413 | -66.8833 | -66.752 | -0.00422 | -66.7819 | 56.1985 | 56.3855 | 56.2147 | -67.1385 | -0.15051 | 0.001845 | 0.012989 | -0.022373 | 0.12814 | -0.070804 | 0.12179 | -0.40572 | -0.092654 | -0.019175 | -0.049102 | 0.35662 | 0.094262 | -0.076524 | 123.0258 | 122.9532 | 123.1458 | 66.725 | -123.1745 | 122.9313 | 123.1182 | 122.9475 | 66.7286 | -123.4297
2063.7969 | 123.1522 | -66.7648 | 56.337 | 0.0046549 | -0.025735 | 3.4136e-05 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056749 | 0.035002 | 0.056812 | -66.729 | -0.003172 | -66.7689 | 56.2976 | 56.2296 | 56.4176 | -66.8925 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.39 | 56.2009 | -67.1294 | -0.12763 | -0.039352 | 0.035876 | -0.004064 | 0.12356 | -0.10742 | 0.080595 | -0.36452 | -0.12927 | 0.017447 | -0.021637 | 0.34288 | 0.053064 | -0.13604 | 123.0625 | 122.9944 | 123.1824 | 66.7617 | -123.2294 | 122.9725 | 123.1549 | 122.9658 | 66.7515 | -123.4663
2064.875 | 123.2483 | -66.7282 | 56.3049 | -0.0029761 | -0.025521 | -0.00017946 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056108 | 0.035002 | 0.056812 | -66.7244 | 0.001407 | -66.7597 | 56.293 | 56.2204 | 56.4221 | -66.8879 | -66.7428 | -0.013377 | -66.791 | 56.2077 | 56.3809 | 56.2193 | -67.1385 | -0.15967 | -0.011888 | 0.003833 | -0.03153 | 0.12814 | -0.084537 | 0.11722 | -0.4103 | -0.09723 | -0.014596 | -0.062837 | 0.34746 | 0.07595 | -0.085678 | 123.0213 | 122.9486 | 123.1504 | 66.7296 | -123.1928 | 122.9359 | 123.1091 | 122.9475 | 66.7148 | -123.4434
2065.7969 | 123.2758 | -66.6824 | 56.3004 | -0.0029761 | -0.025948 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.035215 | 0.057026 | -66.7244 | -0.003172 | -66.7643 | 56.2976 | 56.2158 | 56.4221 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2031 | 56.3992 | 56.2513 | -67.1339 | -0.20087 | -0.002731 | -0.041943 | -0.081884 | 0.11898 | -0.084538 | 0.12179 | -0.45149 | -0.09723 | -0.064951 | -0.10403 | 0.34746 | 0.098843 | -0.04905 | 122.9801 | 122.8982 | 123.1046 | 66.6793 | -123.1837 | 122.8856 | 123.0816 | 122.9337 | 66.6736 | -123.4343
2066.8594 | 123.2758 | -66.7191 | 56.3461 | -0.0029761 | -0.025735 | -0.00017946 | 0.053508 | -0.0069462 | 0.062289 | 0.015414 | -0.0028393 | -0.00055553 | 0.056322 | 0.035215 | 0.057026 | -66.729 | -0.003172 | -66.7597 | 56.3068 | 56.2341 | 56.4176 | -66.8787 | -66.752 | -0.00422 | -66.7865 | 56.2031 | 56.39 | 56.2055 | -67.1385 | -0.15967 | -0.039351 | -0.009901 | -0.040685 | 0.11898 | -0.112 | 0.07144 | -0.41945 | -0.14301 | -0.032908 | -0.067414 | 0.35204 | 0.043909 | -0.14061 | 123.0258 | 122.9532 | 123.1366 | 66.7159 | -123.2249 | 122.9222 | 123.1091 | 122.9246 | 66.7148 | -123.4846
2067.7969 | 123.2666 | -66.7236 | 56.2958 | -0.0029761 | -0.025735 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062503 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056749 | 0.035002 | 0.056812 | -66.7198 | -0.003172 | -66.7552 | 56.2976 | 56.2204 | 56.4176 | -66.8787 | -66.7428 | -0.013377 | -66.7773 | 56.2077 | 56.39 | 56.2238 | -67.1339 | -0.15509 | 0.001847 | 0.003834 | -0.031528 | 0.12356 | -0.075381 | 0.12179 | -0.4103 | -0.088074 | -0.019173 | -0.053678 | 0.35662 | 0.094263 | -0.071944 | 123.0213 | 122.944 | 123.1412 | 66.7205 | -123.1745 | 122.9313 | 123.1137 | 122.9475 | 66.7103 | -123.4297
2068.7969 | 123.2758 | -66.7145 | 56.3278 | 0.0046549 | -0.026376 | -0.00039306 | 0.053722 | -0.0071598 | 0.062503 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056535 | 0.035429 | 0.057026 | -66.7198 | -0.007751 | -66.7597 | 56.293 | 56.2296 | 56.4221 | -66.8787 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3855 | 56.2284 | -67.1431 | -0.16425 | -0.034776 | -0.005321 | -0.045262 | 0.11898 | -0.098268 | 0.094328 | -0.42861 | -0.1247 | -0.032907 | -0.067412 | 0.3612 | 0.057641 | -0.099409 | 123.0075 | 122.944 | 123.1366 | 66.7067 | -123.2065 | 122.9176 | 123.0999 | 122.9429 | 66.7011 | -123.4709
2069.875 | 123.1888 | -66.7191 | 56.3232 | -0.010607 | -0.026162 | 3.4136e-05 | 0.053508 | -0.0071598 | 0.062289 | 0.00015261 | -0.0024119 | -0.00076913 | 0.056535 | 0.035215 | 0.056599 | -66.729 | -0.007751 | -66.7597 | 56.3022 | 56.225 | 56.4176 | -66.8925 | -66.7428 | -0.017956 | -66.791 | 56.2031 | 56.3809 | 56.2193 | -67.1339 | -0.17341 | -0.021041 | -0.009901 | -0.040685 | 0.13272 | -0.098269 | 0.094328 | -0.41487 | -0.12012 | -0.023751 | -0.071992 | 0.34288 | 0.05764 | -0.10399 | 123.0213 | 122.944 | 123.1366 | 66.7113 | -123.2157 | 122.9222 | 123.0999 | 122.9383 | 66.7011 | -123.4572
2070.7969 | 123.2895 | -66.687 | 56.3141 | 0.012286 | -0.026162 | -0.00017946 | 0.053508 | -0.0071598 | 0.062717 | -0.0074779 | -0.0024119 | -0.00098273 | 0.056535 | 0.035643 | 0.056812 | -66.7244 | 0.005985 | -66.7506 | 56.293 | 56.2387 | 56.4176 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.1985 | 56.39 | 56.2101 | -67.1339 | -0.20087 | -0.021043 | -0.037365 | -0.063571 | 0.1373 | -0.075377 | 0.10348 | -0.44692 | -0.11554 | -0.060373 | -0.094878 | 0.35204 | 0.075952 | -0.10399 | 122.9801 | 122.9257 | 123.1046 | 66.693 | -123.202 | 122.8856 | 123.0771 | 122.8971 | 66.6782 | -123.448
2071.7969 | 123.2666 | -66.7282 | 56.3095 | -0.0029761 | -0.025948 | -0.00017946 | 0.053722 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056749 | 0.035429 | 0.056599 | -66.7244 | -0.003172 | -66.7506 | 56.293 | 56.2158 | 56.4221 | -66.8787 | -66.7428 | -0.013377 | -66.7819 | 56.194 | 56.3809 | 56.2193 | -67.1477 | -0.15051 | -0.016465 | 0.003833 | -0.022373 | 0.12814 | -0.093693 | 0.11264 | -0.41946 | -0.11554 | -0.014596 | -0.05368 | 0.36578 | 0.071373 | -0.090255 | 123.0213 | 122.944 | 123.1504 | 66.725 | -123.1882 | 122.9222 | 123.1091 | 122.9475 | 66.7148 | -123.4572
2072.8594 | 123.3124 | -66.6916 | 56.3324 | 0.0046549 | -0.026162 | 3.4136e-05 | 0.053722 | -0.0069462 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.035215 | 0.056812 | -66.7244 | -0.003172 | -66.7552 | 56.2976 | 56.225 | 56.4176 | -66.8925 | -66.7382 | -0.008798 | -66.7819 | 56.2031 | 56.3855 | 56.2238 | -67.1385 | -0.20087 | -0.034774 | -0.032788 | -0.063572 | 0.1373 | -0.10742 | 0.085173 | -0.44692 | -0.12927 | -0.046638 | -0.090301 | 0.35662 | 0.053064 | -0.10856 | 122.9892 | 122.9166 | 123.1092 | 66.6884 | -123.2249 | 122.8947 | 123.077 | 122.9154 | 66.6828 | -123.4709
2073.7969 | 123.2391 | -66.7145 | 56.3416 | -0.0029761 | -0.025948 | -0.00017946 | 0.053508 | -0.0071598 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056322 | 0.035429 | 0.05724 | -66.7244 | -0.007751 | -66.7552 | 56.293 | 56.225 | 56.4176 | -66.8787 | -66.7382 | -0.017956 | -66.7865 | 56.2031 | 56.3855 | 56.2009 | -67.1385 | -0.16425 | -0.048509 | -0.009899 | -0.040683 | 0.12356 | -0.11658 | 0.076017 | -0.42403 | -0.13843 | -0.023749 | -0.071991 | 0.35204 | 0.043908 | -0.14061 | 123.0075 | 122.9395 | 123.132 | 66.7067 | -123.2203 | 122.9176 | 123.0999 | 122.9154 | 66.6965 | -123.4801
2074.7969 | 123.1842 | -66.7603 | 56.3553 | -0.0029761 | -0.025735 | -0.00017946 | 0.052867 | -0.0067326 | 0.062717 | 0.00015261 | -0.0032665 | -0.00034193 | 0.056322 | 0.035215 | 0.056812 | -66.729 | -0.003172 | -66.7552 | 56.2976 | 56.2341 | 56.4176 | -66.8741 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.3855 | 56.2101 | -67.1339 | -0.11389 | -0.057663 | 0.031298 | 0.005093 | 0.11898 | -0.12116 | 0.062284 | -0.37367 | -0.14758 | 0.017448 | -0.026215 | 0.34746 | 0.030175 | -0.14519 | 123.0579 | 122.9944 | 123.1778 | 66.7571 | -123.2294 | 122.968 | 123.1457 | 122.9704 | 66.7515 | -123.4892
2075.7969 | 123.2758 | -66.7191 | 56.3141 | 0.012286 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062289 | -0.0074779 | -0.0032665 | -0.00055553 | 0.056322 | 0.035002 | 0.056599 | -66.7244 | -0.012329 | -66.7414 | 56.2839 | 56.2296 | 56.413 | -66.8833 | -66.7291 | -0.013377 | -66.7819 | 56.2077 | 56.3809 | 56.2055 | -67.1385 | -0.16425 | -0.0302 | -0.005322 | -0.022372 | 0.14188 | -0.084535 | 0.098904 | -0.41945 | -0.10639 | -0.010015 | -0.062835 | 0.35662 | 0.066795 | -0.10857 | 123.0029 | 122.9486 | 123.132 | 66.7067 | -123.1974 | 122.9268 | 123.0999 | 122.9246 | 66.7057 | -123.4526
2076.7969 | 123.2574 | -66.6824 | 56.337 | 0.0046549 | -0.025521 | -0.00017946 | 0.053081 | -0.0067326 | 0.061862 | 0.00015261 | -0.0028393 | -0.00055553 | 0.055895 | 0.035429 | 0.056599 | -66.7198 | -0.007751 | -66.746 | 56.2976 | 56.2158 | 56.4221 | -66.8787 | -66.7428 | -0.013377 | -66.7865 | 56.2077 | 56.3763 | 56.2101 | -67.1385 | -0.19629 | -0.039352 | -0.037365 | -0.063571 | 0.13272 | -0.12116 | 0.085173 | -0.45607 | -0.12927 | -0.060372 | -0.10403 | 0.35204 | 0.039328 | -0.12688 | 122.9801 | 122.8982 | 123.1046 | 66.6747 | -123.2157 | 122.8901 | 123.0587 | 122.8925 | 66.6691 | -123.4755
2077.8594 | 123.2254 | -66.7328 | 56.3141 | 0.0046549 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | -0.0074779 | -0.0026255 | -0.00055553 | 0.056322 | 0.035643 | 0.057026 | -66.729 | -0.007751 | -66.746 | 56.293 | 56.2296 | 56.413 | -66.8833 | -66.7291 | -0.008798 | -66.7865 | 56.2031 | 56.39 | 56.2284 | -67.1431 | -0.15051 | -0.021043 | 0.003832 | -0.013217 | 0.1373 | -0.084535 | 0.098904 | -0.4103 | -0.11096 | 0.003718 | -0.053681 | 0.35662 | 0.075952 | -0.085676 | 123.0258 | 122.9623 | 123.1458 | 66.725 | -123.1974 | 122.9359 | 123.1228 | 122.9612 | 66.724 | -123.4572
2078.7969 | 123.2666 | -66.6962 | 56.3461 | 0.0046549 | -0.025521 | -0.00039306 | 0.053295 | -0.0071598 | 0.062076 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056535 | 0.035429 | 0.056812 | -66.729 | -0.007751 | -66.7414 | 56.2976 | 56.225 | 56.4176 | -66.8833 | -66.7291 | 0.000359 | -66.7773 | 56.2031 | 56.3946 | 56.2376 | -67.1339 | -0.18714 | -0.048507 | -0.032789 | -0.04526 | 0.14188 | -0.12116 | 0.07144 | -0.43776 | -0.14301 | -0.032903 | -0.081144 | 0.35662 | 0.048488 | -0.10856 | 122.9938 | 122.9211 | 123.1137 | 66.6884 | -123.2294 | 122.8993 | 123.0908 | 122.9337 | 66.6965 | -123.4801
2079.875 | 123.317 | -66.7007 | 56.3187 | 0.0046549 | -0.025521 | -0.00017946 | 0.053295 | -0.0067326 | 0.062076 | 0.00015261 | -0.0026255 | -0.00034193 | 0.056322 | 0.035429 | 0.056812 | -66.729 | -0.012329 | -66.7414 | 56.293 | 56.225 | 56.413 | -66.8741 | -66.7336 | -0.013377 | -66.7865 | 56.1985 | 56.39 | 56.2193 | -67.1385 | -0.1734 | -0.025621 | -0.028211 | -0.040682 | 0.13272 | -0.093692 | 0.094326 | -0.43776 | -0.12012 | -0.032904 | -0.085724 | 0.35204 | 0.071374 | -0.099411 | 122.9938 | 122.9257 | 123.1137 | 66.6884 | -123.1928 | 122.8993 | 123.0908 | 122.92 | 66.6874 | -123.4572
2080.7969 | 123.1659 | -66.7465 | 56.3736 | 0.012286 | -0.025521 | -0.00017946 | 0.052867 | -0.0069462 | 0.061862 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056322 | 0.035643 | 0.057026 | -66.729 | 0.001407 | -66.7414 | 56.2976 | 56.225 | 56.4267 | -66.8833 | -66.7291 | -0.00422 | -66.7865 | 56.2077 | 56.3855 | 56.2101 | -67.1339 | -0.13678 | -0.075973 | 0.017565 | 0.005094 | 0.14188 | -0.14862 | 0.053131 | -0.38741 | -0.16589 | 0.017451 | -0.039948 | 0.34746 | 0.011865 | -0.1635 | 123.0441 | 122.9715 | 123.1732 | 66.7479 | -123.2569 | 122.9542 | 123.132 | 122.9566 | 66.7423 | -123.5075
2081.7969 | 123.2895 | -66.6962 | 56.3232 | 0.0046549 | -0.025735 | 3.4136e-05 | 0.053295 | -0.0065188 | 0.062289 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056749 | 0.035215 | 0.056599 | -66.7198 | -0.003172 | -66.746 | 56.293 | 56.2112 | 56.4221 | -66.8879 | -66.7245 | -0.013377 | -66.7773 | 56.2077 | 56.39 | 56.233 | -67.1431 | -0.19172 | -0.030198 | -0.023632 | -0.049838 | 0.14188 | -0.11201 | 0.098906 | -0.44692 | -0.11554 | -0.028324 | -0.081144 | 0.36578 | 0.066797 | -0.090252 | 122.9892 | 122.9074 | 123.1183 | 66.693 | -123.2111 | 122.9039 | 123.0862 | 122.9292 | 66.6828 | -123.4663
2082.7969 | 123.23 | -66.7236 | 56.3416 | 0.012286 | -0.025735 | -0.00017946 | 0.053081 | -0.0069462 | 0.061862 | -0.0074779 | -0.0026255 | -0.00098273 | 0.056535 | 0.035215 | 0.056812 | -66.7244 | -0.003172 | -66.7506 | 56.3022 | 56.2158 | 56.4176 | -66.8879 | -66.7336 | -0.017956 | -66.7865 | 56.2031 | 56.3946 | 56.2421 | -67.1385 | -0.16425 | -0.039352 | -0.000744 | -0.02695 | 0.1373 | -0.12574 | 0.076017 | -0.41487 | -0.13843 | -0.010016 | -0.062836 | 0.35204 | 0.053065 | -0.099406 | 123.0258 | 122.9394 | 123.1412 | 66.7205 | -123.2294 | 122.9268 | 123.1183 | 122.9658 | 66.7057 | -123.4801
2083.7969 | 123.2941 | -66.6916 | 56.337 | 0.012286 | -0.025948 | 3.4136e-05 | 0.053508 | -0.0067326 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.035643 | 0.056599 | -66.7244 | -0.007751 | -66.7506 | 56.2976 | 56.225 | 56.413 | -66.8879 | -66.7382 | -0.013377 | -66.7865 | 56.2031 | 56.3946 | 56.2147 | -67.1385 | -0.19629 | -0.039352 | -0.032788 | -0.058994 | 0.1373 | -0.112 | 0.076016 | -0.44692 | -0.13385 | -0.046638 | -0.09488 | 0.35204 | 0.057643 | -0.1223 | 122.9892 | 122.9166 | 123.1046 | 66.6838 | -123.2249 | 122.8947 | 123.0862 | 122.9063 | 66.6782 | -123.4755
2084.7969 | 123.1705 | -66.7557 | 56.337 | 0.0046549 | -0.025735 | 0.00024794 | 0.052867 | -0.0071598 | 0.062289 | 0.023044 | -0.0028393 | -0.00098273 | 0.056322 | 0.035856 | 0.056812 | -66.729 | -0.003172 | -66.7552 | 56.3022 | 56.2296 | 56.4313 | -66.8879 | -66.7336 | -0.013377 | -66.7819 | 56.1985 | 56.39 | 56.2467 | -67.1385 | -0.13221 | -0.034774 | 0.02672 | 0.000515 | 0.13272 | -0.10742 | 0.09433 | -0.38283 | -0.13843 | 0.022027 | -0.026214 | 0.35662 | 0.053064 | -0.09025 | 123.0579 | 122.9852 | 123.187 | 66.7525 | -123.2249 | 122.9542 | 123.1457 | 123.0024 | 66.7423 | -123.4755
2085.7969 | 123.2117 | -66.7236 | 56.3461 | 0.012286 | -0.026376 | -0.00017946 | 0.052867 | -0.0071598 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.035643 | 0.057026 | -66.7244 | -0.003172 | -66.7597 | 56.293 | 56.225 | 56.413 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.1985 | 56.39 | 56.2193 | -67.1431 | -0.16425 | -0.053086 | -0.000744 | -0.036107 | 0.12814 | -0.12116 | 0.066861 | -0.41945 | -0.14758 | -0.023752 | -0.058257 | 0.3612 | 0.043909 | -0.12688 | 123.0167 | 122.9486 | 123.1366 | 66.7205 | -123.234 | 122.9222 | 123.1137 | 122.9429 | 66.7148 | -123.4892
2086.7969 | 123.2666 | -66.7374 | 56.3324 | -0.0029761 | -0.025948 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062289 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056108 | 0.035429 | 0.057026 | -66.7244 | -0.007751 | -66.7689 | 56.3022 | 56.225 | 56.4267 | -66.8879 | -66.7474 | -0.013377 | -66.7819 | 56.1985 | 56.3946 | 56.2238 | -67.1339 | -0.15052 | -0.030196 | 0.012989 | -0.03153 | 0.11899 | -0.10742 | 0.09433 | -0.39656 | -0.13385 | -0.010019 | -0.044524 | 0.35204 | 0.062221 | -0.10856 | 123.0396 | 122.9623 | 123.1641 | 66.7296 | -123.2203 | 122.9359 | 123.132 | 122.9612 | 66.724 | -123.4663
2087.7969 | 123.2254 | -66.7511 | 56.3141 | -0.0029761 | -0.025948 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | -0.0074779 | -0.0030529 | -0.00076913 | 0.056322 | 0.035429 | 0.057026 | -66.729 | -0.003172 | -66.7597 | 56.293 | 56.225 | 56.4221 | -66.8833 | -66.7428 | -0.008798 | -66.7773 | 56.2031 | 56.3946 | 56.2467 | -67.1385 | -0.1322 | -0.021043 | 0.022143 | -0.008641 | 0.12356 | -0.089114 | 0.10806 | -0.38741 | -0.11096 | 0.008293 | -0.026212 | 0.3612 | 0.080531 | -0.067362 | 123.0441 | 122.9761 | 123.1732 | 66.7479 | -123.1974 | 122.9542 | 123.1457 | 122.9978 | 66.7423 | -123.4526
2088.7969 | 123.2254 | -66.7328 | 56.3324 | -0.0029761 | -0.025948 | 0.00024794 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.035429 | 0.056599 | -66.729 | 0.001407 | -66.746 | 56.2976 | 56.2433 | 56.4221 | -66.8879 | -66.7474 | -0.013377 | -66.7819 | 56.2077 | 56.3946 | 56.2147 | -67.1385 | -0.15509 | -0.034774 | 0.003832 | -0.013217 | 0.14188 | -0.089108 | 0.089751 | -0.40572 | -0.1247 | -0.014597 | -0.049102 | 0.35662 | 0.062221 | -0.11772 | 123.0304 | 122.9761 | 123.1549 | 66.7342 | -123.2203 | 122.9405 | 123.1274 | 122.9475 | 66.7194 | -123.4709
2089.7969 | 123.1934 | -66.7374 | 56.3461 | -0.0029761 | -0.026162 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062717 | -0.0074779 | -0.0032665 | -0.00076913 | 0.056322 | 0.035429 | 0.056599 | -66.729 | 0.001407 | -66.7552 | 56.3022 | 56.2296 | 56.413 | -66.8833 | -66.7428 | -0.008798 | -66.791 | 56.2077 | 56.39 | 56.2284 | -67.1385 | -0.14594 | -0.043929 | 0.00841 | -0.017795 | 0.12814 | -0.11658 | 0.066861 | -0.40114 | -0.13843 | -0.00544 | -0.053681 | 0.34746 | 0.043909 | -0.11772 | 123.0396 | 122.9669 | 123.1504 | 66.7388 | -123.2294 | 122.9451 | 123.1274 | 122.9658 | 66.7286 | -123.4846
2090.7969 | 123.2071 | -66.7465 | 56.3187 | -0.0029761 | -0.026376 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.056535 | 0.035643 | 0.057026 | -66.7244 | -0.003172 | -66.7689 | 56.3022 | 56.2296 | 56.4221 | -66.8925 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.3946 | 56.2376 | -67.1385 | -0.14594 | -0.016464 | 0.022144 | -0.022375 | 0.12356 | -0.089113 | 0.10348 | -0.39199 | -0.11096 | -0.000864 | -0.039948 | 0.35204 | 0.075953 | -0.081097 | 123.0487 | 122.9761 | 123.1687 | 66.7433 | -123.2111 | 122.9542 | 123.1411 | 122.9841 | 66.7331 | -123.4572
2091.7969 | 123.2346 | -66.7236 | 56.3324 | 0.0046549 | -0.026162 | 3.4136e-05 | 0.053081 | -0.0067326 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056535 | 0.035643 | 0.056812 | -66.7244 | -0.007751 | -66.7552 | 56.3022 | 56.2204 | 56.413 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2077 | 56.39 | 56.2421 | -67.1385 | -0.15967 | -0.030196 | -0.000744 | -0.031528 | 0.12814 | -0.112 | 0.080594 | -0.41487 | -0.1247 | -0.019173 | -0.062836 | 0.35204 | 0.057642 | -0.09025 | 123.0258 | 122.944 | 123.1366 | 66.7159 | -123.2157 | 122.9313 | 123.1137 | 122.9658 | 66.7103 | -123.4709
2092.8594 | 123.2071 | -66.7328 | 56.3461 | -0.0029761 | -0.026162 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.035429 | 0.057026 | -66.7244 | -0.007751 | -66.7552 | 56.2885 | 56.2341 | 56.4221 | -66.8833 | -66.7382 | -0.013377 | -66.791 | 56.2077 | 56.3809 | 56.2147 | -67.1339 | -0.15051 | -0.057664 | 0.008411 | -0.022373 | 0.12814 | -0.112 | 0.076018 | -0.40114 | -0.13843 | -0.005439 | -0.058259 | 0.34288 | 0.034752 | -0.13146 | 123.0213 | 122.9669 | 123.1549 | 66.725 | -123.2294 | 122.9405 | 123.1137 | 122.9475 | 66.7194 | -123.4801
2093.7969 | 123.1979 | -66.7328 | 56.3324 | -0.010607 | -0.026162 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056963 | 0.035429 | 0.057026 | -66.729 | -0.007751 | -66.7597 | 56.2976 | 56.2204 | 56.4221 | -66.8925 | -66.7428 | -0.017956 | -66.7819 | 56.2031 | 56.39 | 56.2238 | -67.1339 | -0.15967 | -0.034774 | 0.003832 | -0.026952 | 0.13272 | -0.112 | 0.089751 | -0.40114 | -0.12927 | -0.010018 | -0.049102 | 0.35204 | 0.057642 | -0.10856 | 123.0304 | 122.9532 | 123.1549 | 66.725 | -123.2249 | 122.9359 | 123.1228 | 122.9566 | 66.7148 | -123.4663
2094.7969 | 123.2758 | -66.7282 | 56.2683 | -0.0029761 | -0.025948 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.06293 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.035643 | 0.056385 | -66.7335 | 0.005985 | -66.7552 | 56.2885 | 56.2341 | 56.4267 | -66.8787 | -66.7474 | -0.008798 | -66.7865 | 56.2169 | 56.3855 | 56.2101 | -67.1385 | -0.15051 | 0.020155 | -0.005324 | -0.026951 | 0.12356 | -0.03418 | 0.15842 | -0.4103 | -0.051452 | -0.019175 | -0.058259 | 0.35204 | 0.11715 | -0.058214 | 123.0167 | 122.9623 | 123.1549 | 66.7342 | -123.147 | 122.9451 | 123.1137 | 122.9383 | 66.7194 | -123.4068
2095.8594 | 123.175 | -66.7511 | 56.3644 | -0.010607 | -0.025948 | -0.00017946 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056535 | 0.035856 | 0.057026 | -66.7335 | 0.001407 | -66.7506 | 56.2976 | 56.2387 | 56.4221 | -66.8879 | -66.7474 | -0.022535 | -66.791 | 56.1985 | 56.3946 | 56.233 | -67.1385 | -0.13678 | -0.066818 | 0.017565 | 0.000516 | 0.1373 | -0.12573 | 0.057707 | -0.38741 | -0.1659 | 0.003714 | -0.039948 | 0.34746 | 0.030177 | -0.13145 | 123.0487 | 122.9898 | 123.1732 | 66.7525 | -123.2523 | 122.9496 | 123.1457 | 122.9841 | 66.7286 | -123.5029
2096.7969 | 123.1888 | -66.7603 | 56.3278 | 0.012286 | -0.026162 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.035643 | 0.056812 | -66.7244 | -0.003172 | -66.7597 | 56.2976 | 56.2204 | 56.4221 | -66.8833 | -66.7428 | -0.00422 | -66.7819 | 56.2031 | 56.3855 | 56.2421 | -67.1385 | -0.12305 | -0.030197 | 0.035877 | 0.000514 | 0.12356 | -0.10742 | 0.094328 | -0.37825 | -0.1247 | 0.017448 | -0.021636 | 0.35662 | 0.057641 | -0.085673 | 123.0579 | 122.9806 | 123.1824 | 66.7571 | -123.2111 | 122.9634 | 123.1457 | 123.0024 | 66.756 | -123.4663
2097.8594 | 123.1934 | -66.7145 | 56.3324 | -0.010607 | -0.026162 | -0.00017946 | 0.053081 | -0.0071598 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.035643 | 0.056812 | -66.7335 | -0.012329 | -66.7552 | 56.2976 | 56.2296 | 56.4221 | -66.8787 | -66.7382 | -0.00422 | -66.7819 | 56.2077 | 56.39 | 56.2147 | -67.1431 | -0.16425 | -0.034774 | -0.019056 | -0.040683 | 0.12356 | -0.10285 | 0.089751 | -0.42861 | -0.1247 | -0.023749 | -0.067412 | 0.3612 | 0.057642 | -0.11772 | 123.0121 | 122.944 | 123.1366 | 66.7021 | -123.2111 | 122.9222 | 123.1045 | 122.9292 | 66.7103 | -123.4755
2098.7969 | 123.1888 | -66.7603 | 56.3553 | -0.0029761 | -0.026589 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062717 | -0.015108 | -0.0030529 | -0.00055553 | 0.056535 | 0.035429 | 0.057026 | -66.7381 | -0.003172 | -66.7506 | 56.3022 | 56.2296 | 56.4176 | -66.8879 | -66.7382 | -0.00422 | -66.7865 | 56.2031 | 56.39 | 56.233 | -67.1431 | -0.12763 | -0.053085 | 0.022142 | 0.009671 | 0.1373 | -0.12573 | 0.062284 | -0.38283 | -0.15216 | 0.022027 | -0.026215 | 0.35662 | 0.034753 | -0.1223 | 123.0625 | 122.9898 | 123.1778 | 66.7571 | -123.2432 | 122.9634 | 123.1503 | 122.9932 | 66.756 | -123.4984
2099.875 | 123.2208 | -66.7511 | 56.2912 | -0.010607 | -0.025948 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.0077831 | -0.0028393 | -0.00076913 | 0.056322 | 0.035643 | 0.056812 | -66.7244 | 0.001407 | -66.7643 | 56.2976 | 56.2204 | 56.4176 | -66.8879 | -66.752 | -0.008798 | -66.7773 | 56.2031 | 56.3946 | 56.2421 | -67.1385 | -0.13678 | 0.006424 | 0.026722 | -0.013219 | 0.12356 | -0.070804 | 0.12637 | -0.38741 | -0.088075 | -0.000864 | -0.026212 | 0.3612 | 0.10342 | -0.049052 | 123.0487 | 122.9715 | 123.1687 | 66.7525 | -123.1791 | 122.9542 | 123.1457 | 122.9932 | 66.7423 | -123.4297
2100.7969 | 123.1934 | -66.7648 | 56.3232 | -0.010607 | -0.026162 | -0.00060686 | 0.053295 | -0.0071598 | 0.062289 | -0.0074779 | -0.0032665 | -0.00034193 | 0.056535 | 0.035643 | 0.057026 | -66.7335 | 0.001407 | -66.7506 | 56.293 | 56.225 | 56.4267 | -66.8833 | -66.752 | -0.013377 | -66.7956 | 56.1985 | 56.3992 | 56.2513 | -67.1294 | -0.11847 | -0.030198 | 0.031298 | 0.014249 | 0.13272 | -0.098269 | 0.10348 | -0.36452 | -0.1247 | 0.012869 | -0.030794 | 0.33372 | 0.075955 | -0.071938 | 123.0579 | 122.9898 | 123.1916 | 66.7662 | -123.2065 | 122.9634 | 123.164 | 123.0161 | 66.7515 | -123.4526
2101.7969 | 123.1796 | -66.7374 | 56.3232 | -0.0029761 | -0.026376 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062717 | -0.0074779 | -0.0032665 | -0.00034193 | 0.056322 | 0.035643 | 0.056812 | -66.7381 | 0.001407 | -66.7552 | 56.2976 | 56.2341 | 56.4267 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.39 | 56.2193 | -67.1431 | -0.15052 | -0.025619 | -0.000746 | -0.017795 | 0.13272 | -0.089111 | 0.10348 | -0.40572 | -0.11554 | -0.00544 | -0.049103 | 0.35662 | 0.066797 | -0.10399 | 123.035 | 122.9715 | 123.1641 | 66.7388 | -123.2111 | 122.9451 | 123.1274 | 122.9566 | 66.7286 | -123.4663
2102.7969 | 123.2849 | -66.7145 | 56.282 | -0.0029761 | -0.025948 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00098273 | 0.056535 | 0.035643 | 0.057026 | -66.729 | -0.003172 | -66.7552 | 56.2976 | 56.2158 | 56.4267 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.3946 | 56.2147 | -67.1385 | -0.16882 | 0.01558 | -0.014478 | -0.040683 | 0.12814 | -0.066227 | 0.14468 | -0.42403 | -0.078919 | -0.032907 | -0.071991 | 0.35204 | 0.11257 | -0.067368 | 123.0121 | 122.9303 | 123.1412 | 66.7113 | -123.1653 | 122.9176 | 123.1091 | 122.9292 | 66.7011 | -123.4206
2103.8594 | 123.175 | -66.7419 | 56.3416 | 0.0046549 | -0.026376 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062289 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056108 | 0.035643 | 0.056599 | -66.7244 | 0.001407 | -66.7506 | 56.293 | 56.2341 | 56.4221 | -66.8925 | -66.7428 | -0.008798 | -66.7819 | 56.2077 | 56.39 | 56.2421 | -67.1385 | -0.15052 | -0.048509 | 0.017566 | -0.00864 | 0.14188 | -0.10742 | 0.080595 | -0.39656 | -0.13385 | -0.000863 | -0.039947 | 0.35662 | 0.048486 | -0.099406 | 123.035 | 122.9761 | 123.1641 | 66.7434 | -123.234 | 122.9496 | 123.132 | 122.9841 | 66.7331 | -123.4801
2104.8125 | 123.175 | -66.7786 | 56.3324 | -0.0029761 | -0.026162 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056108 | 0.035856 | 0.05724 | -66.729 | -0.007751 | -66.7552 | 56.3022 | 56.2433 | 56.4221 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.2031 | 56.39 | 56.1964 | -67.1339 | -0.10932 | -0.030196 | 0.049608 | 0.023403 | 0.13272 | -0.089108 | 0.089751 | -0.35536 | -0.12927 | 0.031179 | -0.007905 | 0.34746 | 0.057642 | -0.13604 | 123.0808 | 123.0219 | 123.2007 | 66.7708 | -123.2203 | 122.9817 | 123.1686 | 122.9749 | 66.7698 | -123.4663
2105.7969 | 123.1613 | -66.7786 | 56.3324 | -0.010607 | -0.026162 | -0.00017946 | 0.052867 | -0.0073736 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.056108 | 0.03607 | 0.056599 | -66.729 | 0.001407 | -66.7552 | 56.3022 | 56.2341 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.2077 | 56.3855 | 56.233 | -67.1431 | -0.10932 | -0.030196 | 0.049608 | 0.023403 | 0.13272 | -0.098266 | 0.09433 | -0.36452 | -0.1247 | 0.031179 | -0.007905 | 0.35662 | 0.053064 | -0.099407 | 123.0808 | 123.0127 | 123.2053 | 66.78 | -123.2203 | 122.9863 | 123.164 | 123.0116 | 66.7698 | -123.4755
2106.7969 | 123.2437 | -66.7145 | 56.2912 | -0.0029761 | -0.026162 | 3.4136e-05 | 0.053295 | -0.0067326 | 0.062289 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056535 | 0.035429 | 0.056599 | -66.7335 | 0.001407 | -66.7552 | 56.2885 | 56.2204 | 56.4221 | -66.8787 | -66.7474 | -0.008798 | -66.7773 | 56.2031 | 56.3946 | 56.2055 | -67.1385 | -0.16425 | -0.002733 | -0.019056 | -0.040683 | 0.12356 | -0.070804 | 0.13095 | -0.42403 | -0.088075 | -0.032907 | -0.062833 | 0.3612 | 0.10342 | -0.085681 | 123.0029 | 122.9349 | 123.1366 | 66.7159 | -123.1699 | 122.9176 | 123.1091 | 122.92 | 66.7057 | -123.4297
2107.7969 | 123.2758 | -66.7099 | 56.3004 | -0.0029761 | -0.026376 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | 0.0077831 | -0.0028393 | -0.00055553 | 0.056535 | 0.035643 | 0.057026 | -66.7244 | -0.012329 | -66.7506 | 56.2976 | 56.2296 | 56.4313 | -66.8833 | -66.7428 | -0.013377 | -66.7819 | 56.2031 | 56.3855 | 56.2421 | -67.1339 | -0.1734 | -0.002731 | -0.014477 | -0.040683 | 0.13272 | -0.070802 | 0.13095 | -0.42403 | -0.09723 | -0.032906 | -0.07199 | 0.35204 | 0.085107 | -0.058207 | 123.0075 | 122.9395 | 123.1412 | 66.6976 | -123.1837 | 122.913 | 123.0954 | 122.952 | 66.6965 | -123.4343
2108.8594 | 123.1659 | -66.7511 | 56.3278 | -0.0029761 | -0.026376 | -0.00017946 | 0.053295 | -0.0071598 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056108 | 0.03607 | 0.057026 | -66.729 | -0.003172 | -66.7643 | 56.293 | 56.225 | 56.4221 | -66.8833 | -66.7565 | -0.00422 | -66.7819 | 56.1985 | 56.3946 | 56.2421 | -67.1385 | -0.1322 | -0.034776 | 0.022143 | -0.013219 | 0.11898 | -0.10285 | 0.094328 | -0.38741 | -0.12927 | -0.005443 | -0.030791 | 0.35662 | 0.066798 | -0.085673 | 123.0441 | 122.9761 | 123.1732 | 66.7479 | -123.2111 | 122.9496 | 123.1457 | 122.9932 | 66.7469 | -123.4663
2109.7969 | 123.2941 | -66.7191 | 56.337 | -0.0029761 | -0.026589 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062076 | 0.00015261 | -0.0026255 | -0.00076913 | 0.056535 | 0.035856 | 0.057026 | -66.7335 | -0.007751 | -66.7506 | 56.293 | 56.2433 | 56.4267 | -66.8833 | -66.752 | -0.013377 | -66.791 | 56.2031 | 56.39 | 56.1964 | -67.1385 | -0.16425 | -0.043931 | -0.014479 | -0.031528 | 0.13272 | -0.093686 | 0.089752 | -0.41945 | -0.13385 | -0.032908 | -0.071992 | 0.34746 | 0.053064 | -0.14061 | 123.0121 | 122.9623 | 123.1458 | 66.7113 | -123.2203 | 122.9222 | 123.1091 | 122.9154 | 66.7057 | -123.4755
2110.7969 | 123.2391 | -66.7282 | 56.3095 | -0.0029761 | -0.026376 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.015414 | -0.0032665 | -0.00098273 | 0.056322 | 0.035643 | 0.057026 | -66.729 | -0.012329 | -66.7552 | 56.293 | 56.2341 | 56.4267 | -66.8925 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.39 | 56.2147 | -67.1431 | -0.16425 | -0.016465 | -0.000746 | -0.026951 | 0.1373 | -0.075378 | 0.11722 | -0.41488 | -0.10638 | -0.019175 | -0.058259 | 0.35662 | 0.08053 | -0.094834 | 123.0213 | 122.9623 | 123.1549 | 66.7159 | -123.202 | 122.9313 | 123.1182 | 122.9429 | 66.7148 | -123.4526
2111.8594 | 123.1888 | -66.7419 | 56.3278 | -0.018238 | -0.026376 | 0.00046154 | 0.052867 | -0.0069462 | 0.062503 | -0.0074779 | -0.0030529 | -0.00098273 | 0.056322 | 0.03607 | 0.056812 | -66.7244 | 0.001407 | -66.7506 | 56.3022 | 56.2296 | 56.4221 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.39 | 56.2055 | -67.1385 | -0.14594 | -0.025619 | 0.017566 | -0.00864 | 0.1373 | -0.098268 | 0.094328 | -0.39656 | -0.12012 | -0.000863 | -0.044526 | 0.35204 | 0.062219 | -0.1223 | 123.0441 | 122.9715 | 123.1641 | 66.7434 | -123.2157 | 122.9496 | 123.132 | 122.9475 | 66.7331 | -123.4663
2112.7969 | 123.2437 | -66.7282 | 56.2912 | -0.0029761 | -0.026376 | 0.00024794 | 0.053295 | -0.0071598 | 0.062503 | 0.015414 | -0.0030529 | -0.00076913 | 0.056322 | 0.035856 | 0.05724 | -66.7335 | -0.012329 | -66.7552 | 56.293 | 56.2204 | 56.413 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2031 | 56.39 | 56.2147 | -67.1339 | -0.15967 | 0.001845 | -0.005324 | -0.026951 | 0.13272 | -0.070804 | 0.12179 | -0.40572 | -0.088075 | -0.019175 | -0.058259 | 0.34746 | 0.09884 | -0.076524 | 123.0213 | 122.9486 | 123.1412 | 66.7159 | -123.1791 | 122.9313 | 123.1182 | 122.9429 | 66.7148 | -123.4251
2113.7969 | 123.23 | -66.7282 | 56.3049 | -0.010607 | -0.025948 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.035856 | 0.057026 | -66.729 | -0.003172 | -66.746 | 56.293 | 56.2158 | 56.413 | -66.8879 | -66.7428 | -0.013377 | -66.7819 | 56.2031 | 56.39 | 56.2376 | -67.1431 | -0.15967 | -0.011888 | -0.000746 | -0.017795 | 0.14188 | -0.089116 | 0.10806 | -0.41488 | -0.10181 | -0.014596 | -0.05368 | 0.3612 | 0.085107 | -0.067364 | 123.0213 | 122.944 | 123.1412 | 66.725 | -123.1928 | 122.9313 | 123.1182 | 122.9658 | 66.7148 | -123.448
2114.875 | 123.143 | -66.7648 | 56.3324 | -0.0029761 | -0.026376 | -0.00017946 | 0.053081 | -0.0069462 | 0.062289 | -0.0074779 | -0.0028393 | -0.00055553 | 0.056322 | 0.035856 | 0.056812 | -66.7244 | 0.005985 | -66.7552 | 56.3068 | 56.2296 | 56.4176 | -66.8879 | -66.752 | -0.00422 | -66.7727 | 56.2077 | 56.39 | 56.2284 | -67.1385 | -0.12305 | -0.025618 | 0.040455 | 0.009671 | 0.13272 | -0.10285 | 0.085173 | -0.37368 | -0.1247 | 0.012869 | -0.0079 | 0.36578 | 0.057642 | -0.10399 | 123.0716 | 122.9944 | 123.1824 | 66.7708 | -123.2203 | 122.9725 | 123.1549 | 122.9932 | 66.7606 | -123.4709
2115.7969 | 123.2849 | -66.6916 | 56.3232 | -0.0029761 | -0.026803 | -0.00017946 | 0.053295 | -0.0069462 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056108 | 0.035429 | 0.056599 | -66.729 | -0.003172 | -66.7597 | 56.3022 | 56.2341 | 56.4221 | -66.8879 | -66.7474 | -0.017956 | -66.7865 | 56.2077 | 56.39 | 56.2101 | -67.1385 | -0.19629 | -0.021041 | -0.037367 | -0.068151 | 0.12814 | -0.089111 | 0.098906 | -0.44692 | -0.11554 | -0.055796 | -0.09488 | 0.35204 | 0.066797 | -0.11315 | 122.9938 | 122.9257 | 123.1137 | 66.6884 | -123.2111 | 122.8993 | 123.0816 | 122.9017 | 66.6736 | -123.4617
2116.8594 | 123.23 | -66.7099 | 56.3736 | 0.0046549 | -0.026589 | 0.00024794 | 0.053295 | -0.0069462 | 0.062503 | 0.015414 | -0.0030529 | -0.00076913 | 0.056749 | 0.035643 | 0.056812 | -66.7335 | -0.007751 | -66.7597 | 56.2885 | 56.2158 | 56.4221 | -66.8879 | -66.7474 | -0.013377 | -66.7956 | 56.2031 | 56.39 | 56.2284 | -67.1294 | -0.17798 | -0.08513 | -0.023634 | -0.04984 | 0.12814 | -0.15778 | 0.048552 | -0.41945 | -0.17047 | -0.037485 | -0.085726 | 0.33372 | 0.016443 | -0.14518 | 122.9984 | 122.9257 | 123.132 | 66.7021 | -123.2615 | 122.913 | 123.0999 | 122.9383 | 66.6965 | -123.5029
2117.7969 | 123.23 | -66.7053 | 56.3187 | -0.018238 | -0.026589 | 3.4136e-05 | 0.053722 | -0.0069462 | 0.062289 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056535 | 0.035643 | 0.056599 | -66.7381 | -0.003172 | -66.7506 | 56.293 | 56.225 | 56.4267 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.3946 | 56.2147 | -67.1385 | -0.17798 | -0.025621 | -0.03279 | -0.045261 | 0.13272 | -0.093692 | 0.10806 | -0.43319 | -0.10638 | -0.042063 | -0.081147 | 0.35204 | 0.075953 | -0.10399 | 122.9984 | 122.9303 | 123.132 | 66.7021 | -123.202 | 122.9176 | 123.0999 | 122.92 | 66.6965 | -123.4572
2118.8594 | 123.2758 | -66.7007 | 56.3095 | -0.0029761 | -0.026803 | -0.00017946 | 0.053722 | -0.0067326 | 0.062503 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056108 | 0.035643 | 0.056812 | -66.7335 | -0.003172 | -66.7506 | 56.2976 | 56.2341 | 56.4221 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.3946 | 56.2421 | -67.1477 | -0.18714 | -0.011886 | -0.032789 | -0.049838 | 0.1373 | -0.075378 | 0.11264 | -0.44692 | -0.10181 | -0.042061 | -0.085724 | 0.3612 | 0.085109 | -0.067362 | 122.9984 | 122.9349 | 123.1229 | 66.6976 | -123.1974 | 122.9084 | 123.0954 | 122.9429 | 66.6919 | -123.4572
2119.7969 | 123.1979 | -66.7007 | 56.3416 | 0.012286 | -0.026589 | 3.4136e-05 | 0.052867 | -0.0071598 | 0.062076 | -0.0074779 | -0.0032665 | -0.00076913 | 0.056535 | 0.03607 | 0.05724 | -66.7381 | -0.007751 | -66.7597 | 56.2976 | 56.225 | 56.4221 | -66.8787 | -66.752 | -0.008798 | -66.7819 | 56.2123 | 56.3946 | 56.233 | -67.1385 | -0.17798 | -0.04393 | -0.037367 | -0.058995 | 0.11898 | -0.11658 | 0.080595 | -0.43776 | -0.12927 | -0.051218 | -0.081145 | 0.35662 | 0.053065 | -0.10856 | 122.9984 | 122.9257 | 123.1229 | 66.693 | -123.2203 | 122.913 | 123.0954 | 122.9337 | 66.6919 | -123.4801
2120.8594 | 123.2208 | -66.7099 | 56.3095 | 0.0046549 | -0.026589 | -0.00017946 | 0.053508 | -0.0069462 | 0.062503 | -0.0074779 | -0.0028393 | -0.00076913 | 0.056322 | 0.035643 | 0.056812 | -66.7381 | -0.007751 | -66.7597 | 56.293 | 56.2204 | 56.413 | -66.8879 | -66.7428 | -0.008798 | -66.7819 | 56.2031 | 56.39 | 56.233 | -67.1385 | -0.17798 | -0.016465 | -0.028212 | -0.04984 | 0.12814 | -0.089114 | 0.10348 | -0.42861 | -0.10638 | -0.032906 | -0.07199 | 0.35662 | 0.08053 | -0.076519 | 123.0029 | 122.9303 | 123.1229 | 66.7021 | -123.1974 | 122.913 | 123.0999 | 122.9429 | 66.7011 | -123.448
2121.7969 | 123.2483 | -66.7007 | 56.3232 | -0.0029761 | -0.026589 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0034801 | -0.00076913 | 0.056108 | 0.035856 | 0.056812 | -66.7335 | -0.007751 | -66.7643 | 56.2976 | 56.2204 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2077 | 56.3855 | 56.2193 | -67.1339 | -0.18714 | -0.025619 | -0.032789 | -0.063573 | 0.12356 | -0.10285 | 0.10348 | -0.43318 | -0.11554 | -0.04664 | -0.081145 | 0.35204 | 0.062219 | -0.10399 | 122.9984 | 122.9211 | 123.1275 | 66.693 | -123.2111 | 122.9084 | 123.0862 | 122.92 | 66.6919 | -123.4572
2122.7969 | 123.1796 | -66.7374 | 56.3507 | 0.0046549 | -0.026803 | 0.00046154 | 0.053295 | -0.0069462 | 0.062503 | 0.0077831 | -0.0032665 | -0.00034193 | 0.056322 | 0.03607 | 0.056812 | -66.729 | -0.003172 | -66.7643 | 56.293 | 56.2296 | 56.4176 | -66.8833 | -66.7474 | -0.013377 | -66.7865 | 56.2123 | 56.3992 | 56.2147 | -67.1431 | -0.14594 | -0.057664 | 0.00841 | -0.026952 | 0.11898 | -0.12116 | 0.066862 | -0.40572 | -0.13843 | -0.010019 | -0.049103 | 0.35662 | 0.048489 | -0.13603 | 123.0304 | 122.9669 | 123.1549 | 66.7342 | -123.234 | 122.9496 | 123.1366 | 122.952 | 66.724 | -123.4938
2123.7969 | 123.2162 | -66.6962 | 56.3553 | -0.0029761 | -0.026162 | -0.00017946 | 0.053295 | -0.0067326 | 0.06293 | 0.015414 | -0.0032665 | -0.00055553 | 0.056322 | 0.03607 | 0.056812 | -66.729 | 0.005985 | -66.7506 | 56.2885 | 56.2296 | 56.4221 | -66.8833 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.3946 | 56.2238 | -67.1385 | -0.18714 | -0.06682 | -0.032789 | -0.054416 | 0.13272 | -0.12573 | 0.066862 | -0.44234 | -0.14758 | -0.046639 | -0.090302 | 0.35204 | 0.039332 | -0.13145 | 122.9846 | 122.9257 | 123.1183 | 66.7022 | -123.2386 | 122.9039 | 123.0908 | 122.92 | 66.6874 | -123.4938
2124.7969 | 123.2346 | -66.7923 | 56.337 | -0.0029761 | -0.026376 | 3.4136e-05 | 0.052867 | -0.0071598 | 0.062717 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056322 | 0.03607 | 0.056599 | -66.729 | -0.007751 | -66.7552 | 56.3022 | 56.2387 | 56.4221 | -66.8879 | -66.7428 | -0.00422 | -66.7819 | 56.2123 | 56.3992 | 56.2284 | -67.1385 | -0.095585 | -0.034774 | 0.063341 | 0.037136 | 0.13272 | -0.098265 | 0.085173 | -0.34621 | -0.12469 | 0.049491 | 0.010407 | 0.35662 | 0.062222 | -0.10856 | 123.0945 | 123.031 | 123.2144 | 66.7845 | -123.2249 | 123.0046 | 123.1915 | 123.0207 | 66.7881 | -123.4755
2125.8594 | 123.2208 | -66.7557 | 56.2866 | 0.0046549 | -0.026376 | 3.4136e-05 | 0.052867 | -0.0069462 | 0.062503 | 0.015414 | -0.0032665 | -0.00098273 | 0.056322 | 0.03607 | 0.056812 | -66.729 | -0.007751 | -66.7552 | 56.293 | 56.2204 | 56.4221 | -66.8925 | -66.752 | -0.008798 | -66.7819 | 56.2077 | 56.3946 | 56.2193 | -67.1385 | -0.13679 | 0.006423 | 0.02672 | 0.000515 | 0.1373 | -0.066226 | 0.13553 | -0.38283 | -0.078919 | 0.003713 | -0.026214 | 0.35662 | 0.108 | -0.067367 | 123.0487 | 122.9761 | 123.1778 | 66.7479 | -123.1791 | 122.9634 | 123.1503 | 122.9749 | 66.7469 | -123.4251
2126.7969 | 123.1979 | -66.7328 | 56.4148 | -0.0029761 | -0.026589 | -0.00017946 | 0.053081 | -0.0067326 | 0.062503 | 0.015414 | -0.0032665 | -0.00076913 | 0.056322 | 0.035856 | 0.056599 | -66.7335 | 0.001407 | -66.7643 | 56.3022 | 56.2387 | 56.4267 | -66.8833 | -66.7428 | -0.008798 | -66.7773 | 56.2077 | 56.3855 | 56.2238 | -67.1477 | -0.15051 | -0.11259 | -0.000746 | -0.03153 | 0.11898 | -0.17609 | 0.011932 | -0.41488 | -0.20709 | -0.010018 | -0.044523 | 0.37036 | -0.029334 | -0.19096 | 123.035 | 122.9715 | 123.1595 | 66.7342 | -123.2981 | 122.9405 | 123.1182 | 122.9566 | 66.724 | -123.5625
2127.8594 | 123.2574 | -66.7007 | 56.3141 | 0.012286 | -0.026803 | -0.00017946 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.03607 | 0.057026 | -66.7381 | -0.007751 | -66.7643 | 56.293 | 56.2433 | 56.4267 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2031 | 56.3855 | 56.233 | -67.1339 | -0.18256 | -0.021043 | -0.037367 | -0.063573 | 0.11898 | -0.070798 | 0.11264 | -0.43318 | -0.11096 | -0.042061 | -0.085724 | 0.34746 | 0.071374 | -0.081097 | 122.9938 | 122.944 | 123.1275 | 66.693 | -123.1974 | 122.9039 | 123.0862 | 122.9337 | 66.6874 | -123.448
2128.7969 | 123.2025 | -66.7419 | 56.3461 | 0.012286 | -0.026589 | -0.00017946 | 0.053508 | -0.0073736 | 0.062717 | 0.015414 | -0.0030529 | -0.00098273 | 0.056322 | 0.035856 | 0.056812 | -66.7335 | -0.003172 | -66.7552 | 56.293 | 56.225 | 56.4221 | -66.8879 | -66.7474 | -0.00422 | -66.7819 | 56.2031 | 56.3992 | 56.2101 | -67.1385 | -0.14594 | -0.053086 | 0.008409 | -0.013218 | 0.13272 | -0.12116 | 0.076018 | -0.39656 | -0.14301 | -0.005442 | -0.039947 | 0.35662 | 0.053067 | -0.13603 | 123.035 | 122.9669 | 123.1641 | 66.7388 | -123.234 | 122.9451 | 123.1411 | 122.952 | 66.7377 | -123.4846
2129.7969 | 123.2071 | -66.7419 | 56.3416 | -0.010607 | -0.026803 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062717 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.03607 | 0.056812 | -66.7244 | -0.003172 | -66.7597 | 56.2976 | 56.2296 | 56.4267 | -66.8925 | -66.7428 | -0.008798 | -66.7819 | 56.2077 | 56.39 | 56.2238 | -67.1339 | -0.15052 | -0.04393 | 0.017566 | -0.017797 | 0.13272 | -0.112 | 0.085174 | -0.39199 | -0.13385 | -0.000863 | -0.039947 | 0.35204 | 0.048486 | -0.11772 | 123.0396 | 122.9715 | 123.1687 | 66.7388 | -123.234 | 122.9496 | 123.132 | 122.9658 | 66.7331 | -123.4755
2130.8594 | 123.1567 | -66.7465 | 56.3599 | -0.0029761 | -0.026376 | 3.4136e-05 | 0.052867 | -0.0071598 | 0.062076 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056535 | 0.036284 | 0.056599 | -66.7335 | -0.003172 | -66.7689 | 56.3068 | 56.2296 | 56.4267 | -66.8879 | -66.7474 | -0.013377 | -66.7819 | 56.2123 | 56.3946 | 56.2009 | -67.1431 | -0.14136 | -0.053084 | 0.012987 | -0.022375 | 0.11899 | -0.13031 | 0.066864 | -0.39657 | -0.14758 | -0.000864 | -0.035369 | 0.3612 | 0.034755 | -0.15892 | 123.0533 | 122.9761 | 123.1732 | 66.7433 | -123.2477 | 122.9588 | 123.1411 | 122.9475 | 66.7331 | -123.5029
2131.7969 | 123.3032 | -66.7099 | 56.3095 | 0.019917 | -0.026803 | -0.00017946 | 0.053508 | -0.0071598 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.035856 | 0.056812 | -66.7244 | -0.007751 | -66.7552 | 56.2976 | 56.225 | 56.4267 | -66.8879 | -66.752 | -0.013377 | -66.7819 | 56.2077 | 56.39 | 56.2147 | -67.1431 | -0.17798 | -0.011886 | -0.014477 | -0.045261 | 0.13272 | -0.084536 | 0.11722 | -0.43319 | -0.10181 | -0.042063 | -0.07199 | 0.3612 | 0.08053 | -0.094834 | 123.0075 | 122.9349 | 123.1366 | 66.7021 | -123.1974 | 122.9176 | 123.0999 | 122.9246 | 66.6965 | -123.4526
2132.8594 | 123.1567 | -66.7191 | 56.3507 | -0.0029761 | -0.026376 | -0.00039306 | 0.053295 | -0.0075872 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056322 | 0.036284 | 0.056812 | -66.729 | -0.007751 | -66.7552 | 56.293 | 56.2296 | 56.4221 | -66.8879 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.39 | 56.2421 | -67.1385 | -0.16883 | -0.057664 | -0.009901 | -0.036106 | 0.13272 | -0.12116 | 0.07144 | -0.41945 | -0.14301 | -0.02833 | -0.067414 | 0.35204 | 0.039331 | -0.10856 | 123.0121 | 122.9486 | 123.1412 | 66.7113 | -123.2386 | 122.9268 | 123.1091 | 122.9612 | 66.7057 | -123.4892
2133.7969 | 123.175 | -66.7236 | 56.3461 | -0.010607 | -0.026589 | -0.00017946 | 0.053508 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056535 | 0.035643 | 0.056812 | -66.7335 | -0.003172 | -66.7552 | 56.2976 | 56.2433 | 56.4221 | -66.8879 | -66.7428 | -0.00422 | -66.791 | 56.2077 | 56.3946 | 56.2238 | -67.1385 | -0.16425 | -0.048507 | -0.009901 | -0.031528 | 0.13272 | -0.10284 | 0.076018 | -0.41487 | -0.13843 | -0.019173 | -0.067414 | 0.34746 | 0.048488 | -0.1223 | 123.0213 | 122.9669 | 123.1458 | 66.7205 | -123.234 | 122.9313 | 123.1183 | 122.9475 | 66.7194 | -123.4846
2134.8594 | 123.262 | -66.7465 | 56.2775 | -0.0029761 | -0.026803 | -0.00017946 | 0.053722 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00034193 | 0.056535 | 0.035856 | 0.056812 | -66.729 | -0.003172 | -66.7597 | 56.3022 | 56.2158 | 56.4221 | -66.8925 | -66.7474 | -0.017956 | -66.7865 | 56.2077 | 56.39 | 56.233 | -67.1477 | -0.14594 | 0.024735 | 0.017565 | -0.013219 | 0.13272 | -0.06165 | 0.14468 | -0.40114 | -0.069764 | -0.000864 | -0.039948 | 0.3612 | 0.11257 | -0.044476 | 123.0487 | 122.9623 | 123.1687 | 66.7433 | -123.1699 | 122.9542 | 123.1366 | 122.9795 | 66.7286 | -123.4251
2135.7969 | 123.1979 | -66.7374 | 56.3278 | 0.0046549 | -0.027017 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062717 | 0.00015261 | -0.0034801 | -0.00076913 | 0.056108 | 0.03607 | 0.056812 | -66.729 | 0.001407 | -66.7597 | 56.3068 | 56.2387 | 56.4221 | -66.8925 | -66.7428 | -0.008798 | -66.7819 | 56.2123 | 56.39 | 56.2376 | -67.1385 | -0.1551 | -0.021041 | 0.00841 | -0.022374 | 0.13272 | -0.08911 | 0.094328 | -0.40114 | -0.11554 | -0.00544 | -0.044524 | 0.35662 | 0.062219 | -0.090252 | 123.0441 | 122.9761 | 123.1595 | 66.7388 | -123.2203 | 122.9496 | 123.1274 | 122.9749 | 66.7286 | -123.4663
2136.7969 | 123.3078 | -66.7374 | 56.2866 | -0.0029761 | -0.026803 | -0.00017946 | 0.053508 | -0.0073736 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.03607 | 0.056812 | -66.7335 | 0.001407 | -66.7643 | 56.2976 | 56.2204 | 56.4267 | -66.8879 | -66.7428 | -0.013377 | -66.7865 | 56.2123 | 56.39 | 56.2238 | -67.1339 | -0.15052 | 0.011002 | 0.003832 | -0.026952 | 0.12356 | -0.066226 | 0.14011 | -0.39656 | -0.07434 | -0.00544 | -0.049103 | 0.34746 | 0.10342 | -0.062789 | 123.035 | 122.9578 | 123.1641 | 66.7388 | -123.1745 | 122.9496 | 123.1274 | 122.9612 | 66.724 | -123.4205
2137.8594 | 123.175 | -66.7557 | 56.3461 | 0.0046549 | -0.026376 | -0.00017946 | 0.053081 | -0.0069462 | 0.062503 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056322 | 0.036284 | 0.056812 | -66.729 | -0.003172 | -66.7643 | 56.3068 | 56.2204 | 56.4221 | -66.8925 | -66.752 | -0.008798 | -66.7865 | 56.2077 | 56.3946 | 56.2376 | -67.1385 | -0.13679 | -0.039351 | 0.02672 | -0.008642 | 0.12814 | -0.12573 | 0.076018 | -0.38283 | -0.13843 | 0.003713 | -0.030793 | 0.35204 | 0.048488 | -0.10856 | 123.0625 | 122.9761 | 123.1778 | 66.7525 | -123.2386 | 122.9634 | 123.1503 | 122.9932 | 66.7469 | -123.4846
2138.7969 | 123.1888 | -66.7648 | 56.3278 | -0.0029761 | -0.026803 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062289 | 0.015414 | -0.0032665 | -0.00098273 | 0.056322 | 0.03607 | 0.056812 | -66.7335 | 0.001407 | -66.7597 | 56.293 | 56.2158 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2031 | 56.3855 | 56.2193 | -67.1477 | -0.12305 | -0.034776 | 0.031298 | 0.005092 | 0.12814 | -0.112 | 0.098907 | -0.38283 | -0.1247 | 0.017447 | -0.017058 | 0.36578 | 0.057641 | -0.10857 | 123.0579 | 122.9806 | 123.1916 | 66.7662 | -123.2157 | 122.968 | 123.1503 | 122.9841 | 66.756 | -123.4755
2139.8594 | 123.2254 | -66.7419 | 56.3507 | 0.012286 | -0.026589 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.03607 | 0.056812 | -66.7335 | -0.007751 | -66.7506 | 56.3022 | 56.2204 | 56.4313 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2031 | 56.39 | 56.2284 | -67.1339 | -0.14594 | -0.048507 | 0.008409 | -0.00864 | 0.1373 | -0.13031 | 0.080597 | -0.39199 | -0.14758 | -0.005442 | -0.039947 | 0.35204 | 0.039331 | -0.1223 | 123.0441 | 122.9623 | 123.1732 | 66.7342 | -123.2386 | 122.9451 | 123.132 | 122.9704 | 66.7331 | -123.4846
2140.7969 | 123.1979 | -66.7328 | 56.3095 | -0.010607 | -0.027017 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062076 | -0.0074779 | -0.0032665 | -0.00076913 | 0.056108 | 0.03607 | 0.056599 | -66.729 | -0.003172 | -66.7597 | 56.2976 | 56.225 | 56.4267 | -66.8925 | -66.752 | -0.013377 | -66.7819 | 56.1985 | 56.3946 | 56.2376 | -67.1339 | -0.15967 | -0.011886 | 0.003832 | -0.026952 | 0.13272 | -0.084536 | 0.11722 | -0.40114 | -0.11096 | -0.019175 | -0.049102 | 0.35204 | 0.085109 | -0.071941 | 123.0304 | 122.9578 | 123.1595 | 66.7296 | -123.202 | 122.9313 | 123.1274 | 122.9704 | 66.7194 | -123.4434
2141.7969 | 123.1659 | -66.7374 | 56.3416 | -0.0029761 | -0.027017 | 0.00024794 | 0.053081 | -0.0071598 | 0.062289 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056108 | 0.036497 | 0.056812 | -66.7198 | 0.001407 | -66.7506 | 56.293 | 56.2433 | 56.4221 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2031 | 56.3992 | 56.2376 | -67.1385 | -0.15052 | -0.048509 | 0.017567 | -0.013217 | 0.1373 | -0.098264 | 0.080595 | -0.40114 | -0.13843 | -0.010019 | -0.044524 | 0.35662 | 0.057644 | -0.10398 | 123.0304 | 122.9807 | 123.1595 | 66.7388 | -123.2294 | 122.9405 | 123.1366 | 122.9749 | 66.7286 | -123.4801
2142.7969 | 123.2437 | -66.7145 | 56.2912 | -0.010607 | -0.026589 | -0.00017946 | 0.053508 | -0.0069462 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056322 | 0.03607 | 0.056812 | -66.729 | -0.007751 | -66.7597 | 56.3022 | 56.225 | 56.4176 | -66.8833 | -66.7474 | -0.013377 | -66.7819 | 56.2123 | 56.3946 | 56.2421 | -67.1522 | -0.16882 | 0.011002 | -0.014478 | -0.045262 | 0.12356 | -0.066226 | 0.12637 | -0.43777 | -0.078918 | -0.032907 | -0.067412 | 0.37035 | 0.10342 | -0.049052 | 123.0167 | 122.9395 | 123.132 | 66.7067 | -123.1745 | 122.9268 | 123.1091 | 122.9566 | 66.7011 | -123.4434
2143.8594 | 123.1567 | -66.7694 | 56.3919 | 0.0046549 | -0.026803 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.0077831 | -0.0034801 | -0.00055553 | 0.056108 | 0.03607 | 0.056812 | -66.729 | -0.007751 | -66.7552 | 56.293 | 56.2433 | 56.4221 | -66.897 | -66.7474 | -0.013377 | -66.7819 | 56.2031 | 56.3946 | 56.2284 | -67.1385 | -0.12763 | -0.098863 | 0.040453 | 0.014248 | 0.14188 | -0.14862 | 0.030241 | -0.3691 | -0.18878 | 0.022024 | -0.012481 | 0.35662 | 0.002711 | -0.1635 | 123.0625 | 123.0127 | 123.1916 | 66.7617 | -123.2889 | 122.9725 | 123.164 | 122.9978 | 66.756 | -123.5304
2144.7969 | 123.2391 | -66.7236 | 56.3141 | -0.0029761 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062503 | 0.023044 | -0.0034801 | -0.00055553 | 0.056108 | 0.03607 | 0.056385 | -66.7335 | -0.003172 | -66.7597 | 56.2976 | 56.2387 | 56.4221 | -66.8787 | -66.7428 | -0.00422 | -66.7819 | 56.2123 | 56.3992 | 56.2009 | -67.1385 | -0.15509 | -0.016464 | -0.009901 | -0.036107 | 0.11898 | -0.075377 | 0.10806 | -0.41487 | -0.10181 | -0.019173 | -0.058257 | 0.35662 | 0.08511 | -0.11315 | 123.0213 | 122.9623 | 123.1458 | 66.7205 | -123.1928 | 122.9359 | 123.1228 | 122.9246 | 66.7194 | -123.4526
2145.7969 | 123.1842 | -66.7511 | 56.3461 | 0.0046549 | -0.027017 | 0.00024794 | 0.053508 | -0.0071598 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056108 | 0.03607 | 0.056812 | -66.7335 | -0.007751 | -66.7552 | 56.3022 | 56.225 | 56.4221 | -66.8879 | -66.7428 | -0.00422 | -66.7865 | 56.1985 | 56.3992 | 56.233 | -67.1385 | -0.13678 | -0.043929 | 0.017565 | -0.004062 | 0.13272 | -0.12116 | 0.076018 | -0.38741 | -0.14758 | 0.008293 | -0.03537 | 0.35204 | 0.053067 | -0.11314 | 123.0533 | 122.9761 | 123.1732 | 66.7433 | -123.234 | 122.9496 | 123.1503 | 122.9841 | 66.7469 | -123.4846
2146.7969 | 123.2849 | -66.7282 | 56.2683 | 0.0046549 | -0.026803 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.036284 | 0.056599 | -66.729 | 0.005985 | -66.7597 | 56.3022 | 56.2296 | 56.4221 | -66.897 | -66.752 | -0.008798 | -66.7956 | 56.2031 | 56.3946 | 56.2193 | -67.1431 | -0.16883 | 0.03389 | -0.000746 | -0.03153 | 0.1373 | -0.038759 | 0.15384 | -0.41488 | -0.065187 | -0.023753 | -0.067416 | 0.34746 | 0.12631 | -0.049057 | 123.0304 | 122.9578 | 123.1504 | 66.7342 | -123.1654 | 122.9313 | 123.1228 | 122.9475 | 66.7194 | -123.4114
2147.7969 | 123.2483 | -66.7145 | 56.3049 | 0.012286 | -0.027017 | -0.00039306 | 0.053722 | -0.0071598 | 0.06293 | -0.0074779 | -0.0030529 | -0.00076913 | 0.056535 | 0.03607 | 0.057026 | -66.7427 | -0.003172 | -66.7552 | 56.293 | 56.2387 | 56.4267 | -66.8925 | -66.7474 | -0.008798 | -66.791 | 56.2077 | 56.3992 | 56.2193 | -67.1339 | -0.17798 | -0.011888 | -0.028213 | -0.040683 | 0.1373 | -0.066222 | 0.12179 | -0.41945 | -0.09723 | -0.032907 | -0.076569 | 0.34288 | 0.094265 | -0.085678 | 123.0075 | 122.9532 | 123.1412 | 66.7113 | -123.1974 | 122.9222 | 123.1137 | 122.9337 | 66.7057 | -123.4389
2148.8594 | 123.175 | -66.7557 | 56.3232 | -0.0029761 | -0.026803 | 0.00024794 | 0.053081 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056108 | 0.03607 | 0.056599 | -66.7335 | -0.003172 | -66.7643 | 56.3114 | 56.2387 | 56.4267 | -66.8879 | -66.7474 | 0.004938 | -66.791 | 56.2031 | 56.3946 | 56.2238 | -67.1385 | -0.13221 | -0.011884 | 0.022142 | -0.008642 | 0.12356 | -0.084532 | 0.10348 | -0.38283 | -0.12012 | 0.008291 | -0.035371 | 0.34746 | 0.071376 | -0.09941 | 123.067 | 122.9944 | 123.1824 | 66.7525 | -123.2111 | 122.9588 | 123.1503 | 122.9795 | 66.7606 | -123.4617
2149.7969 | 123.3032 | -66.7374 | 56.2637 | -0.010607 | -0.027017 | 0.00024794 | 0.053081 | -0.0071598 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056108 | 0.036284 | 0.056599 | -66.7244 | -0.003172 | -66.7643 | 56.3068 | 56.2204 | 56.4267 | -66.8925 | -66.7474 | -0.008798 | -66.791 | 56.2123 | 56.3946 | 56.2284 | -67.1431 | -0.1551 | 0.043046 | 0.012989 | -0.026952 | 0.12814 | -0.043338 | 0.16299 | -0.40572 | -0.051452 | -0.010019 | -0.053681 | 0.35204 | 0.13088 | -0.035322 | 123.0441 | 122.9578 | 123.1641 | 66.7342 | -123.1562 | 122.9496 | 123.132 | 122.9658 | 66.7286 | -123.4068
2150.7969 | 123.2208 | -66.7145 | 56.3278 | -0.0029761 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062717 | -0.0074779 | -0.0030529 | -0.00076913 | 0.056108 | 0.036497 | 0.056812 | -66.729 | -0.003172 | -66.7597 | 56.2976 | 56.2296 | 56.4313 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.39 | 56.2284 | -67.1385 | -0.1734 | -0.030197 | -0.014478 | -0.045262 | 0.12814 | -0.098268 | 0.10348 | -0.42403 | -0.12012 | -0.028328 | -0.071991 | 0.35204 | 0.062219 | -0.099409 | 123.0121 | 122.944 | 123.1458 | 66.7113 | -123.2157 | 122.9222 | 123.1045 | 122.9429 | 66.7057 | -123.4663
2151.8594 | 123.1522 | -66.7419 | 56.3461 | -0.0029761 | -0.02723 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.056535 | 0.036497 | 0.056812 | -66.7198 | 0.001407 | -66.7643 | 56.2976 | 56.2112 | 56.4359 | -66.8879 | -66.752 | -0.008798 | -66.7773 | 56.2077 | 56.39 | 56.2421 | -67.1477 | -0.14594 | -0.048507 | 0.022144 | -0.022375 | 0.12356 | -0.13489 | 0.089754 | -0.40572 | -0.13843 | -0.01002 | -0.035368 | 0.37036 | 0.043909 | -0.10398 | 123.0396 | 122.9532 | 123.1778 | 66.7434 | -123.234 | 122.9496 | 123.132 | 122.9841 | 66.7331 | -123.4938
2152.7969 | 123.2712 | -66.7282 | 56.282 | -0.0029761 | -0.027017 | 3.4136e-05 | 0.053081 | -0.0073736 | 0.062289 | 0.0077831 | -0.0032665 | -0.0011965 | 0.056108 | 0.036497 | 0.057026 | -66.729 | -0.003172 | -66.7643 | 56.3022 | 56.2433 | 56.4267 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2169 | 56.3946 | 56.2147 | -67.1385 | -0.15509 | 0.020158 | -0.000746 | -0.036108 | 0.11898 | -0.038754 | 0.14468 | -0.4103 | -0.065184 | -0.019175 | -0.058259 | 0.35204 | 0.11257 | -0.067368 | 123.0304 | 122.9715 | 123.1549 | 66.725 | -123.1653 | 122.9451 | 123.1228 | 122.9429 | 66.7194 | -123.4206
2153.8594 | 123.1522 | -66.7694 | 56.3232 | 0.0046549 | -0.027017 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056108 | 0.036284 | 0.057026 | -66.729 | 0.001407 | -66.7552 | 56.2976 | 56.2341 | 56.4221 | -66.8925 | -66.7474 | -0.013377 | -66.7865 | 56.2077 | 56.3946 | 56.2101 | -67.1385 | -0.12305 | -0.025619 | 0.040453 | 0.014248 | 0.1373 | -0.089111 | 0.098906 | -0.3691 | -0.11554 | 0.022024 | -0.01706 | 0.35204 | 0.071376 | -0.11315 | 123.067 | 123.0035 | 123.1916 | 66.7708 | -123.2157 | 122.9771 | 123.164 | 122.9795 | 66.756 | -123.4617
2154.7969 | 123.1888 | -66.7007 | 56.3599 | -0.0029761 | -0.026803 | -0.00017946 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055895 | 0.036497 | 0.056812 | -66.7427 | -0.003172 | -66.7643 | 56.3022 | 56.2341 | 56.4221 | -66.8925 | -66.7474 | -0.00422 | -66.7865 | 56.2031 | 56.39 | 56.2421 | -67.1385 | -0.19172 | -0.057662 | -0.041946 | -0.063573 | 0.12814 | -0.12573 | 0.062285 | -0.43776 | -0.15674 | -0.04664 | -0.085724 | 0.35204 | 0.030176 | -0.11772 | 123.0029 | 122.9349 | 123.1229 | 66.6976 | -123.2523 | 122.9039 | 123.0908 | 122.9429 | 66.6965 | -123.4984
2155.7969 | 123.2483 | -66.7191 | 56.3004 | 0.0046549 | -0.027017 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00098273 | 0.056535 | 0.036284 | 0.057026 | -66.7335 | 0.001407 | -66.7552 | 56.3022 | 56.2204 | 56.4221 | -66.8879 | -66.7428 | -0.013377 | -66.7865 | 56.2077 | 56.3946 | 56.2376 | -67.1385 | -0.16883 | 0.001847 | -0.014479 | -0.036106 | 0.13272 | -0.079959 | 0.12179 | -0.41945 | -0.092652 | -0.023751 | -0.067414 | 0.35204 | 0.094264 | -0.062786 | 123.0213 | 122.9394 | 123.1412 | 66.7205 | -123.1882 | 122.9268 | 123.1137 | 122.9566 | 66.7057 | -123.4389
2156.8594 | 123.2574 | -66.7145 | 56.3095 | -0.0029761 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.056322 | 0.03607 | 0.056599 | -66.729 | -0.003172 | -66.7597 | 56.3022 | 56.2387 | 56.4267 | -66.8925 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.3855 | 56.233 | -67.1339 | -0.17798 | -0.007308 | -0.014478 | -0.045262 | 0.13272 | -0.070799 | 0.11722 | -0.41945 | -0.10181 | -0.028328 | -0.071991 | 0.34746 | 0.075952 | -0.076519 | 123.0167 | 122.9532 | 123.1412 | 66.7113 | -123.202 | 122.9222 | 123.0999 | 122.9475 | 66.7057 | -123.4434
2157.7969 | 123.2254 | -66.7282 | 56.3324 | 0.0046549 | -0.027017 | -0.00017946 | 0.053081 | -0.0067326 | 0.062503 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056322 | 0.036497 | 0.056812 | -66.729 | 0.001407 | -66.7735 | 56.3022 | 56.2158 | 56.4176 | -66.8879 | -66.752 | -0.008798 | -66.7819 | 56.2077 | 56.39 | 56.1964 | -67.1385 | -0.15967 | -0.030196 | -0.000746 | -0.045264 | 0.11441 | -0.11658 | 0.085173 | -0.4103 | -0.1247 | -0.023753 | -0.05368 | 0.35662 | 0.057642 | -0.13604 | 123.0304 | 122.944 | 123.1458 | 66.7296 | -123.2203 | 122.9359 | 123.1182 | 122.9246 | 66.7194 | -123.4709
2158.8594 | 123.2162 | -66.7191 | 56.337 | 0.0046549 | -0.026803 | -0.00017946 | 0.053508 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056108 | 0.036284 | 0.056812 | -66.7244 | -0.003172 | -66.746 | 56.2976 | 56.225 | 56.4359 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2031 | 56.39 | 56.2513 | -67.1477 | -0.16883 | -0.039352 | -0.005322 | -0.02695 | 0.14188 | -0.112 | 0.098909 | -0.42861 | -0.13385 | -0.02833 | -0.062835 | 0.36578 | 0.053064 | -0.085671 | 123.0167 | 122.944 | 123.1549 | 66.7159 | -123.2249 | 122.9222 | 123.1091 | 122.9704 | 66.7103 | -123.4846
2159.7969 | 123.2941 | -66.7099 | 56.3324 | 0.0046549 | -0.026803 | -0.00039306 | 0.053295 | -0.0071598 | 0.062289 | 0.0077831 | -0.0030529 | -0.00076913 | 0.055895 | 0.036284 | 0.056812 | -66.729 | -0.003172 | -66.7597 | 56.2976 | 56.2296 | 56.4313 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.1985 | 56.3855 | 56.2147 | -67.1385 | -0.17798 | -0.034774 | -0.019056 | -0.04984 | 0.12814 | -0.10285 | 0.098908 | -0.42861 | -0.13385 | -0.037485 | -0.076569 | 0.35204 | 0.053064 | -0.11772 | 123.0075 | 122.9395 | 123.1412 | 66.7067 | -123.2203 | 122.9084 | 123.0954 | 122.9246 | 66.7011 | -123.4709
2160.7969 | 123.2529 | -66.6916 | 56.3461 | -0.0029761 | -0.026589 | 3.4136e-05 | 0.053508 | -0.0073736 | 0.062717 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055895 | 0.036284 | 0.056812 | -66.729 | -0.012329 | -66.7552 | 56.2976 | 56.2296 | 56.4313 | -66.8879 | -66.7474 | -0.008798 | -66.791 | 56.2123 | 56.3946 | 56.2055 | -67.1339 | -0.19629 | -0.048507 | -0.037367 | -0.063572 | 0.13272 | -0.11658 | 0.085175 | -0.44234 | -0.13385 | -0.055796 | -0.099458 | 0.34288 | 0.048488 | -0.14061 | 122.9892 | 122.9211 | 123.1229 | 66.6793 | -123.234 | 122.9039 | 123.0862 | 122.8971 | 66.6828 | -123.4801
2161.7969 | 123.1476 | -66.7419 | 56.3461 | -0.0029761 | -0.027017 | 0.00024794 | 0.053295 | -0.0069462 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056535 | 0.036497 | 0.056385 | -66.7244 | -0.003172 | -66.7506 | 56.2976 | 56.2341 | 56.4313 | -66.8787 | -66.7382 | -0.008798 | -66.791 | 56.2031 | 56.39 | 56.2147 | -67.1431 | -0.13678 | -0.048507 | 0.017566 | -0.00864 | 0.12814 | -0.112 | 0.085175 | -0.40114 | -0.14301 | 0.003716 | -0.049104 | 0.35204 | 0.043909 | -0.13146 | 123.0396 | 122.9761 | 123.1732 | 66.7388 | -123.2249 | 122.9451 | 123.132 | 122.9566 | 66.7331 | -123.4892
2162.8594 | 123.262 | -66.7236 | 56.3095 | -0.0029761 | -0.026803 | -0.00017946 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055895 | 0.035856 | 0.056812 | -66.729 | -0.007751 | -66.746 | 56.2976 | 56.2341 | 56.4313 | -66.8879 | -66.7382 | -0.013377 | -66.791 | 56.2077 | 56.39 | 56.2467 | -67.1431 | -0.16425 | -0.011886 | -0.005323 | -0.022372 | 0.14188 | -0.075378 | 0.1218 | -0.41945 | -0.10181 | -0.014594 | -0.067414 | 0.35204 | 0.08053 | -0.062784 | 123.0213 | 122.9578 | 123.1549 | 66.7159 | -123.1974 | 122.9313 | 123.1137 | 122.9704 | 66.7103 | -123.4526
2163.7969 | 123.2437 | -66.7053 | 56.3416 | 0.0046549 | -0.026803 | 0.00024794 | 0.053081 | -0.0075872 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055895 | 0.036284 | 0.056599 | -66.7335 | 0.001407 | -66.7506 | 56.2976 | 56.2433 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7819 | 56.2077 | 56.3946 | 56.2101 | -67.1431 | -0.18256 | -0.04393 | -0.028212 | -0.045261 | 0.1373 | -0.098264 | 0.085174 | -0.43776 | -0.13385 | -0.042063 | -0.076568 | 0.3612 | 0.053065 | -0.13146 | 123.0029 | 122.9486 | 123.132 | 66.7067 | -123.2294 | 122.913 | 123.0999 | 122.9154 | 66.6965 | -123.4846
2164.7969 | 123.1613 | -66.7511 | 56.3416 | 0.0046549 | -0.02723 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056322 | 0.036497 | 0.056812 | -66.729 | 0.001407 | -66.7597 | 56.3022 | 56.225 | 56.4267 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3855 | 56.2284 | -67.1477 | -0.13678 | -0.039352 | 0.022143 | -0.008641 | 0.12814 | -0.11658 | 0.085174 | -0.39657 | -0.13385 | 0.003714 | -0.03537 | 0.3612 | 0.043908 | -0.11314 | 123.0533 | 122.9761 | 123.1778 | 66.7525 | -123.2294 | 122.9588 | 123.1366 | 122.9795 | 66.7469 | -123.4892
2165.8594 | 123.2483 | -66.7191 | 56.3141 | -0.010607 | -0.027017 | -0.00017946 | 0.053295 | -0.0071598 | 0.062076 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056322 | 0.036497 | 0.056812 | -66.7427 | -0.003172 | -66.746 | 56.2976 | 56.2341 | 56.4267 | -66.8787 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2147 | -67.1431 | -0.15967 | -0.016464 | -0.023636 | -0.02695 | 0.13272 | -0.079956 | 0.11264 | -0.42403 | -0.10639 | -0.02833 | -0.067414 | 0.35662 | 0.08511 | -0.099412 | 123.0167 | 122.9532 | 123.1458 | 66.7159 | -123.1928 | 122.9268 | 123.1183 | 122.9337 | 66.7148 | -123.4572
2166.7969 | 123.2117 | -66.7419 | 56.3873 | 0.0046549 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.036284 | 0.056812 | -66.729 | 0.001407 | -66.7506 | 56.3022 | 56.2387 | 56.4313 | -66.8879 | -66.7428 | -0.008798 | -66.7865 | 56.2031 | 56.3946 | 56.2513 | -67.1431 | -0.14594 | -0.085128 | 0.012987 | -0.00864 | 0.1373 | -0.14862 | 0.043976 | -0.40114 | -0.1842 | -0.000863 | -0.044526 | 0.35662 | 0.007289 | -0.13603 | 123.0441 | 122.9807 | 123.1732 | 66.7434 | -123.2752 | 122.9451 | 123.1366 | 122.9932 | 66.7331 | -123.5304
2167.7969 | 123.1613 | -66.7374 | 56.369 | -0.0029761 | -0.027444 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062076 | 0.0077831 | -0.0034801 | -0.00098273 | 0.056108 | 0.036284 | 0.056599 | -66.7335 | 0.001407 | -66.7552 | 56.3022 | 56.2387 | 56.4221 | -66.8879 | -66.7428 | -0.00422 | -66.7865 | 56.1985 | 56.39 | 56.2101 | -67.1431 | -0.15052 | -0.066818 | 0.003832 | -0.017795 | 0.13272 | -0.13031 | 0.053129 | -0.40572 | -0.17047 | -0.00544 | -0.049103 | 0.35662 | 0.02102 | -0.15892 | 123.0396 | 122.9761 | 123.1595 | 66.7388 | -123.2569 | 122.9359 | 123.1274 | 122.9475 | 66.7331 | -123.5121
2168.7969 | 123.1659 | -66.7648 | 56.3232 | -0.0029761 | -0.026803 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056535 | 0.036711 | 0.056812 | -66.7381 | -0.003172 | -66.7552 | 56.3068 | 56.225 | 56.4221 | -66.8879 | -66.7428 | -0.008798 | -66.7819 | 56.1985 | 56.3946 | 56.2101 | -67.1431 | -0.12305 | -0.016463 | 0.02672 | 0.009671 | 0.13272 | -0.098269 | 0.098906 | -0.37825 | -0.1247 | 0.022026 | -0.017058 | 0.3612 | 0.071376 | -0.11315 | 123.0716 | 122.9898 | 123.187 | 66.7617 | -123.2111 | 122.9634 | 123.1594 | 122.9749 | 66.756 | -123.4663
2169.7969 | 123.2025 | -66.7374 | 56.3278 | 0.0046549 | -0.02723 | -0.00017946 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055895 | 0.036711 | 0.056599 | -66.729 | -0.012329 | -66.7597 | 56.3068 | 56.225 | 56.4221 | -66.8879 | -66.752 | -0.008798 | -66.7819 | 56.2031 | 56.3946 | 56.2284 | -67.1477 | -0.15052 | -0.021041 | 0.00841 | -0.022374 | 0.12814 | -0.10285 | 0.094328 | -0.4103 | -0.1247 | -0.014597 | -0.044524 | 0.36578 | 0.066798 | -0.099409 | 123.0441 | 122.9623 | 123.1595 | 66.725 | -123.2157 | 122.9405 | 123.132 | 122.9658 | 66.7286 | -123.4755
2170.7969 | 123.1567 | -66.7557 | 56.3095 | -0.0029761 | -0.026803 | -0.00039306 | 0.053081 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055895 | 0.036497 | 0.056812 | -66.7244 | -0.003172 | -66.7552 | 56.3068 | 56.2433 | 56.4313 | -66.8925 | -66.7428 | -0.008798 | -66.7865 | 56.2031 | 56.3946 | 56.2284 | -67.1385 | -0.13679 | -0.00273 | 0.031299 | 0.000515 | 0.1373 | -0.06622 | 0.1218 | -0.38283 | -0.10638 | 0.01287 | -0.030793 | 0.35204 | 0.085109 | -0.081098 | 123.0625 | 122.999 | 123.187 | 66.7525 | -123.202 | 122.9588 | 123.1503 | 122.9841 | 66.7469 | -123.448
2171.7969 | 123.1888 | -66.7282 | 56.3278 | -0.0029761 | -0.027017 | -0.00017946 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.036711 | 0.056812 | -66.729 | 0.001407 | -66.7643 | 56.3114 | 56.2387 | 56.4313 | -66.8833 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.4038 | 56.2147 | -67.1431 | -0.15509 | -0.016462 | -0.000746 | -0.036108 | 0.11898 | -0.08911 | 0.10348 | -0.41488 | -0.12012 | -0.014596 | -0.058259 | 0.35662 | 0.075955 | -0.11315 | 123.0396 | 122.9669 | 123.1595 | 66.7296 | -123.2111 | 122.9359 | 123.132 | 122.9429 | 66.7194 | -123.4709
2172.8594 | 123.1705 | -66.7603 | 56.3644 | -0.0029761 | -0.027017 | -0.00017946 | 0.053081 | -0.0071598 | 0.061862 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056108 | 0.036284 | 0.056812 | -66.729 | 0.001407 | -66.7597 | 56.3022 | 56.2341 | 56.4221 | -66.8879 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.39 | 56.2193 | -67.1385 | -0.12763 | -0.06224 | 0.031298 | 0.000514 | 0.12814 | -0.13031 | 0.057707 | -0.37825 | -0.15216 | 0.012869 | -0.026215 | 0.35204 | 0.025598 | -0.14519 | 123.0625 | 122.9944 | 123.1824 | 66.7617 | -123.2523 | 122.9725 | 123.1503 | 122.9795 | 66.7515 | -123.5029
2173.7969 | 123.1796 | -66.7694 | 56.3782 | -0.0029761 | -0.02723 | -0.00039306 | 0.053081 | -0.0069462 | 0.062503 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056108 | 0.036284 | 0.056812 | -66.7335 | -0.007751 | -66.7597 | 56.2976 | 56.2341 | 56.4267 | -66.8879 | -66.7382 | -0.008798 | -66.7865 | 56.2031 | 56.3946 | 56.2193 | -67.1477 | -0.11847 | -0.080551 | 0.035875 | 0.009669 | 0.12814 | -0.14404 | 0.048553 | -0.37826 | -0.17505 | 0.031182 | -0.01706 | 0.3612 | 0.016444 | -0.15892 | 123.067 | 123.0035 | 123.1961 | 66.7617 | -123.2661 | 122.9725 | 123.164 | 122.9887 | 66.7606 | -123.5258
2174.7969 | 123.1384 | -66.7511 | 56.3095 | -0.0029761 | -0.02723 | -0.00039306 | 0.053081 | -0.0073736 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056108 | 0.036497 | 0.056812 | -66.7244 | 0.001407 | -66.7597 | 56.3022 | 56.2296 | 56.4359 | -66.8925 | -66.7428 | -0.008798 | -66.7956 | 56.2031 | 56.3946 | 56.2193 | -67.1431 | -0.14136 | -0.007308 | 0.026722 | -0.008641 | 0.13272 | -0.079957 | 0.12638 | -0.39199 | -0.10638 | 0.008293 | -0.044527 | 0.34746 | 0.085109 | -0.090255 | 123.0533 | 122.9807 | 123.187 | 66.7525 | -123.202 | 122.9542 | 123.1457 | 122.9704 | 66.7423 | -123.4526
2175.8594 | 123.2208 | -66.7328 | 56.3553 | 0.012286 | -0.02723 | 3.4136e-05 | 0.053508 | -0.0071598 | 0.062717 | -0.015108 | -0.0030529 | -0.00076913 | 0.056535 | 0.03607 | 0.056812 | -66.7244 | -0.003172 | -66.7597 | 56.2976 | 56.2341 | 56.4313 | -66.8925 | -66.752 | -0.008798 | -66.7865 | 56.2077 | 56.3992 | 56.2467 | -67.1431 | -0.15967 | -0.057663 | 0.008411 | -0.026952 | 0.13272 | -0.12116 | 0.076019 | -0.4103 | -0.14758 | -0.019175 | -0.053681 | 0.35662 | 0.043911 | -0.10856 | 123.0304 | 122.9669 | 123.1641 | 66.7296 | -123.2477 | 122.9405 | 123.132 | 122.9795 | 66.724 | -123.4984
2176.7969 | 123.2986 | -66.7236 | 56.2729 | -0.010607 | -0.027444 | -0.00017946 | 0.052867 | -0.0069462 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056322 | 0.036497 | 0.057026 | -66.729 | 0.001407 | -66.7597 | 56.2976 | 56.2387 | 56.4267 | -66.897 | -66.752 | -0.008798 | -66.7865 | 56.2031 | 56.3946 | 56.2238 | -67.1477 | -0.17341 | 0.024735 | -0.005323 | -0.036107 | 0.1373 | -0.034178 | 0.15384 | -0.42403 | -0.069764 | -0.02833 | -0.062836 | 0.3612 | 0.12173 | -0.049056 | 123.0213 | 122.9623 | 123.1504 | 66.725 | -123.1699 | 122.9268 | 123.1183 | 122.9475 | 66.7148 | -123.4206
2177.8125 | 123.1979 | -66.7282 | 56.3416 | -0.010607 | -0.02723 | 3.4136e-05 | 0.052867 | -0.0069462 | 0.062503 | 0.0077831 | -0.0030529 | -0.00055553 | 0.056108 | 0.036711 | 0.056812 | -66.729 | -0.003172 | -66.7689 | 56.2976 | 56.2341 | 56.4405 | -66.8925 | -66.752 | -0.00422 | -66.7865 | 56.2123 | 56.3946 | 56.2284 | -67.1385 | -0.16425 | -0.04393 | -0.000746 | -0.040686 | 0.12356 | -0.10742 | 0.09891 | -0.4103 | -0.12927 | -0.023753 | -0.058259 | 0.35204 | 0.053065 | -0.11314 | 123.0258 | 122.9623 | 123.1687 | 66.725 | -123.234 | 122.9405 | 123.1228 | 122.9566 | 66.724 | -123.4801
2178.8594 | 123.1522 | -66.7511 | 56.3095 | -0.0029761 | -0.027017 | -0.00017946 | 0.053295 | -0.0067326 | 0.062289 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056322 | 0.036497 | 0.056599 | -66.729 | -0.003172 | -66.7506 | 56.3068 | 56.2296 | 56.4313 | -66.8879 | -66.7428 | -0.013377 | -66.791 | 56.2123 | 56.4038 | 56.2101 | -67.1477 | -0.13678 | -0.00273 | 0.022143 | 0.000516 | 0.1373 | -0.079957 | 0.1218 | -0.39657 | -0.097228 | 0.008293 | -0.039948 | 0.35662 | 0.094266 | -0.099412 | 123.0579 | 122.9807 | 123.1824 | 66.7479 | -123.1974 | 122.9634 | 123.1549 | 122.9612 | 66.7377 | -123.4572
2179.7969 | 123.2758 | -66.7328 | 56.2958 | -0.0029761 | -0.026803 | -0.00017946 | 0.053081 | -0.0069462 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055895 | 0.036497 | 0.056812 | -66.7335 | -0.003172 | -66.7552 | 56.2976 | 56.225 | 56.4221 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.2193 | -67.1431 | -0.15509 | 0.001847 | -0.000746 | -0.022373 | 0.13272 | -0.070803 | 0.12637 | -0.4103 | -0.083495 | -0.014597 | -0.053681 | 0.35662 | 0.10342 | -0.076522 | 123.0304 | 122.9578 | 123.1549 | 66.7296 | -123.1837 | 122.9451 | 123.132 | 122.952 | 66.7286 | -123.4389
2180.7969 | 123.2529 | -66.7419 | 56.2958 | -0.0029761 | -0.027017 | -0.00017946 | 0.053295 | -0.0069462 | 0.062076 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055895 | 0.036497 | 0.056599 | -66.7335 | -0.007751 | -66.7552 | 56.2976 | 56.2204 | 56.4267 | -66.8879 | -66.7336 | -0.00422 | -66.791 | 56.2123 | 56.3992 | 56.2009 | -67.1477 | -0.14594 | 0.001847 | 0.008409 | -0.013218 | 0.13272 | -0.075381 | 0.13095 | -0.40572 | -0.083495 | 0.008294 | -0.049104 | 0.35662 | 0.10342 | -0.094837 | 123.0396 | 122.9623 | 123.1687 | 66.7342 | -123.1837 | 122.9542 | 123.1411 | 122.9429 | 66.7377 | -123.4434
2181.7969 | 123.262 | -66.7374 | 56.3049 | 0.0046549 | -0.027017 | -0.00039306 | 0.053081 | -0.0071598 | 0.062076 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056108 | 0.036711 | 0.056599 | -66.7335 | -0.007751 | -66.7597 | 56.3022 | 56.2341 | 56.4221 | -66.8833 | -66.7428 | -0.00422 | -66.7865 | 56.2031 | 56.3992 | 56.2467 | -67.1385 | -0.14594 | -0.002731 | 0.003832 | -0.022374 | 0.12356 | -0.070801 | 0.11722 | -0.40114 | -0.10181 | -0.00544 | -0.049103 | 0.35204 | 0.094265 | -0.058207 | 123.0396 | 122.9715 | 123.1595 | 66.7296 | -123.1882 | 122.9405 | 123.1366 | 122.9841 | 66.7331 | -123.4434
2182.7969 | 123.2391 | -66.7191 | 56.3278 | 0.012286 | -0.027017 | -0.00039306 | 0.053081 | -0.0071598 | 0.061862 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056108 | 0.036711 | 0.056599 | -66.729 | -0.003172 | -66.7689 | 56.293 | 56.225 | 56.4359 | -66.8833 | -66.7382 | -0.008798 | -66.791 | 56.2123 | 56.39 | 56.2101 | -67.1477 | -0.16425 | -0.034776 | -0.009901 | -0.049841 | 0.11441 | -0.10285 | 0.10806 | -0.42861 | -0.11554 | -0.019172 | -0.071992 | 0.35662 | 0.062219 | -0.11772 | 123.0121 | 122.944 | 123.1549 | 66.7159 | -123.2111 | 122.9313 | 123.1091 | 122.9292 | 66.7103 | -123.4755
2183.7969 | 123.2895 | -66.7145 | 56.3141 | -0.0029761 | -0.027444 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062289 | 0.00015261 | -0.0034801 | -0.0011965 | 0.056322 | 0.036497 | 0.056599 | -66.729 | 0.001407 | -66.7597 | 56.3068 | 56.2479 | 56.4267 | -66.897 | -66.752 | -0.008798 | -66.7819 | 56.2123 | 56.3992 | 56.2101 | -67.1385 | -0.18256 | -0.007308 | -0.014478 | -0.045262 | 0.1373 | -0.066219 | 0.11264 | -0.42403 | -0.10181 | -0.037485 | -0.067412 | 0.35662 | 0.08511 | -0.10399 | 123.0213 | 122.9623 | 123.1412 | 66.7159 | -123.2111 | 122.9268 | 123.1137 | 122.9246 | 66.7057 | -123.4526
2184.8594 | 123.2391 | -66.7145 | 56.3049 | 0.0046549 | -0.027017 | 3.4136e-05 | 0.053508 | -0.0069462 | 0.062717 | 0.0077831 | -0.0034801 | -0.00076913 | 0.056108 | 0.036497 | 0.057026 | -66.7381 | -0.003172 | -66.7506 | 56.3068 | 56.2296 | 56.4221 | -66.8833 | -66.7474 | 0.000359 | -66.791 | 56.2077 | 56.3946 | 56.1872 | -67.1477 | -0.16882 | 0.001847 | -0.023634 | -0.036105 | 0.13272 | -0.07538 | 0.11722 | -0.43319 | -0.09723 | -0.032907 | -0.076569 | 0.35662 | 0.089686 | -0.11773 | 123.0213 | 122.944 | 123.1366 | 66.7113 | -123.1882 | 122.9222 | 123.1091 | 122.9017 | 66.7148 | -123.4526
2185.7969 | 123.2666 | -66.7191 | 56.3049 | -0.010607 | -0.027017 | -0.00017946 | 0.053295 | -0.0071598 | 0.062717 | -0.0074779 | -0.0032665 | -0.00098273 | 0.056108 | 0.036711 | 0.056599 | -66.729 | -0.007751 | -66.7597 | 56.3022 | 56.2341 | 56.4267 | -66.8833 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.4038 | 56.2193 | -67.1385 | -0.16425 | -0.002731 | -0.009901 | -0.040685 | 0.12356 | -0.070801 | 0.12179 | -0.41945 | -0.09723 | -0.02833 | -0.067414 | 0.35204 | 0.098843 | -0.085678 | 123.0213 | 122.9532 | 123.1458 | 66.7113 | -123.1882 | 122.9268 | 123.1228 | 122.9383 | 66.7148 | -123.4434
2186.7969 | 123.2758 | -66.7053 | 56.3141 | 0.0046549 | -0.027444 | 3.4136e-05 | 0.053295 | -0.0069462 | 0.062717 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055895 | 0.036497 | 0.056599 | -66.729 | -0.003172 | -66.7552 | 56.3022 | 56.2341 | 56.4267 | -66.8833 | -66.7474 | 0.000359 | -66.791 | 56.2123 | 56.3992 | 56.2193 | -67.1385 | -0.17798 | -0.011886 | -0.023634 | -0.049839 | 0.12814 | -0.079956 | 0.11264 | -0.43319 | -0.10181 | -0.042063 | -0.085725 | 0.34746 | 0.08511 | -0.094833 | 123.0075 | 122.9395 | 123.132 | 66.7021 | -123.1974 | 122.9176 | 123.1045 | 122.9246 | 66.7057 | -123.4526
2187.8594 | 123.3627 | -66.7099 | 56.3095 | -0.0029761 | -0.027444 | -0.00039306 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.036711 | 0.056599 | -66.7335 | -0.003172 | -66.746 | 56.3022 | 56.2158 | 56.4313 | -66.8833 | -66.7428 | -0.008798 | -66.7819 | 56.1985 | 56.3992 | 56.233 | -67.1385 | -0.1734 | -0.007308 | -0.023634 | -0.036105 | 0.1373 | -0.093693 | 0.1218 | -0.42861 | -0.11096 | -0.032906 | -0.07199 | 0.35662 | 0.089688 | -0.076519 | 123.0121 | 122.9257 | 123.1412 | 66.7067 | -123.1928 | 122.9084 | 123.1091 | 122.9429 | 66.7011 | -123.448
2188.7969 | 123.2529 | -66.7007 | 56.3553 | -0.0029761 | -0.02723 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056535 | 0.036711 | 0.056812 | -66.7381 | 0.005985 | -66.7552 | 56.3068 | 56.2158 | 56.4313 | -66.8833 | -66.7474 | -0.008798 | -66.7865 | 56.2077 | 56.3992 | 56.233 | -67.1385 | -0.18256 | -0.048507 | -0.037367 | -0.054416 | 0.12814 | -0.13947 | 0.076019 | -0.43776 | -0.14758 | -0.04664 | -0.085724 | 0.35204 | 0.043911 | -0.1223 | 123.0075 | 122.9166 | 123.132 | 66.7067 | -123.2386 | 122.9084 | 123.0999 | 122.9337 | 66.6919 | -123.4938
2189.8594 | 123.2712 | -66.6962 | 56.3278 | 0.0046549 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062717 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056322 | 0.036711 | 0.056599 | -66.7381 | -0.003172 | -66.7552 | 56.3022 | 56.225 | 56.4221 | -66.8833 | -66.7428 | -0.00422 | -66.7956 | 56.2077 | 56.39 | 56.2238 | -67.1385 | -0.18714 | -0.025619 | -0.041945 | -0.058994 | 0.12814 | -0.10285 | 0.094328 | -0.44234 | -0.12012 | -0.046639 | -0.099459 | 0.34288 | 0.062219 | -0.10399 | 122.9984 | 122.9211 | 123.1183 | 66.693 | -123.2111 | 122.9039 | 123.0862 | 122.92 | 66.6919 | -123.4663
2190.7969 | 123.2666 | -66.6824 | 56.337 | -0.0029761 | -0.02723 | -0.00017946 | 0.053295 | -0.0071598 | 0.062289 | 0.015414 | -0.0030529 | -0.00076913 | 0.056108 | 0.036497 | 0.056812 | -66.7381 | -0.003172 | -66.7597 | 56.3068 | 56.2387 | 56.4313 | -66.8925 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.3946 | 56.2284 | -67.1477 | -0.21003 | -0.030196 | -0.055678 | -0.077306 | 0.13272 | -0.098265 | 0.09433 | -0.46523 | -0.12469 | -0.064951 | -0.10403 | 0.3612 | 0.057643 | -0.10856 | 122.9892 | 122.9211 | 123.1137 | 66.6793 | -123.2294 | 122.8947 | 123.0771 | 122.9108 | 66.6736 | -123.4846
2191.8594 | 123.23 | -66.7007 | 56.2866 | -0.0029761 | -0.027658 | -0.00017946 | 0.053295 | -0.0071598 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.036711 | 0.05724 | -66.7335 | -0.003172 | -66.7643 | 56.2976 | 56.2296 | 56.4359 | -66.8696 | -66.7474 | -0.00422 | -66.7819 | 56.2031 | 56.39 | 56.1918 | -67.1477 | -0.16882 | 0.011002 | -0.032789 | -0.063573 | 0.10525 | -0.057069 | 0.14926 | -0.44692 | -0.083497 | -0.04664 | -0.081145 | 0.36578 | 0.10342 | -0.094839 | 122.9984 | 122.9303 | 123.1366 | 66.6976 | -123.1562 | 122.9039 | 123.0908 | 122.8925 | 66.6965 | -123.4343
2192.7969 | 123.2025 | -66.7374 | 56.3644 | -0.010607 | -0.027017 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055681 | 0.036497 | 0.056599 | -66.7335 | -0.003172 | -66.7506 | 56.3022 | 56.2387 | 56.4267 | -66.8879 | -66.7474 | -0.00422 | -66.791 | 56.2123 | 56.3946 | 56.2376 | -67.1385 | -0.15052 | -0.06224 | 0.003832 | -0.013217 | 0.1373 | -0.12573 | 0.062286 | -0.40114 | -0.15216 | -0.010019 | -0.053681 | 0.34746 | 0.030177 | -0.12687 | 123.0396 | 122.9761 | 123.1641 | 66.7342 | -123.2523 | 122.9496 | 123.132 | 122.9749 | 66.7331 | -123.5029
2193.7969 | 123.2758 | -66.6962 | 56.3187 | 0.0046549 | -0.02723 | -0.00017946 | 0.053295 | -0.0071598 | 0.062076 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.036497 | 0.056812 | -66.7244 | 0.001407 | -66.7597 | 56.3022 | 56.2112 | 56.4267 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3946 | 56.2238 | -67.1431 | -0.19172 | -0.016464 | -0.02821 | -0.063573 | 0.12814 | -0.10743 | 0.10806 | -0.44692 | -0.11096 | -0.051218 | -0.090302 | 0.35662 | 0.075953 | -0.094833 | 122.9984 | 122.9074 | 123.1229 | 66.6976 | -123.2065 | 122.9039 | 123.0908 | 122.92 | 66.6919 | -123.4618
2194.8594 | 123.1842 | -66.7328 | 56.369 | -0.0029761 | -0.027658 | 3.4136e-05 | 0.052867 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056108 | 0.036711 | 0.056385 | -66.7244 | -0.007751 | -66.7552 | 56.3022 | 56.225 | 56.4359 | -66.8925 | -66.752 | -0.013377 | -66.7865 | 56.2077 | 56.3946 | 56.2559 | -67.1431 | -0.15967 | -0.066818 | 0.008411 | -0.022373 | 0.1373 | -0.14405 | 0.066865 | -0.4103 | -0.16132 | -0.019175 | -0.053681 | 0.35662 | 0.025599 | -0.11314 | 123.035 | 122.9578 | 123.1687 | 66.725 | -123.2615 | 122.9405 | 123.1274 | 122.9887 | 66.7194 | -123.5121
2195.7969 | 123.1567 | -66.7694 | 56.3278 | -0.010607 | -0.027444 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056108 | 0.036284 | 0.057026 | -66.7335 | -0.007751 | -66.7552 | 56.3068 | 56.2341 | 56.4359 | -66.8879 | -66.7428 | -0.00422 | -66.7819 | 56.2123 | 56.39 | 56.2101 | -67.1431 | -0.11847 | -0.021041 | 0.035875 | 0.014248 | 0.13272 | -0.093689 | 0.10806 | -0.37368 | -0.11554 | 0.026603 | -0.012481 | 0.3612 | 0.062219 | -0.11772 | 123.0762 | 123.0035 | 123.2053 | 66.7617 | -123.2157 | 122.9817 | 123.1594 | 122.9795 | 66.7652 | -123.4709
2196.7969 | 123.2071 | -66.7282 | 56.3416 | -0.0029761 | -0.02723 | 3.4136e-05 | 0.053081 | -0.0073736 | 0.061862 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056322 | 0.036284 | 0.056385 | -66.7335 | 0.005985 | -66.7552 | 56.293 | 56.2433 | 56.4313 | -66.8925 | -66.7382 | -0.00422 | -66.791 | 56.2123 | 56.39 | 56.2101 | -67.1385 | -0.16425 | -0.048509 | -0.005324 | -0.026951 | 0.1373 | -0.098264 | 0.089752 | -0.4103 | -0.12927 | -0.010017 | -0.062837 | 0.34746 | 0.048486 | -0.13146 | 123.0213 | 122.9715 | 123.1595 | 66.7342 | -123.234 | 122.9405 | 123.1182 | 122.9383 | 66.724 | -123.4801
2197.8594 | 123.2437 | -66.7236 | 56.3232 | 0.0046549 | -0.027444 | 3.4136e-05 | 0.053508 | -0.0071598 | 0.062289 | -0.0074779 | -0.0028393 | -0.00076913 | 0.055895 | 0.036711 | 0.056599 | -66.7335 | -0.003172 | -66.7552 | 56.2976 | 56.2479 | 56.4313 | -66.8787 | -66.7428 | -0.008798 | -66.791 | 56.2077 | 56.3946 | 56.2101 | -67.1477 | -0.15509 | -0.025619 | -0.009901 | -0.031528 | 0.12356 | -0.075374 | 0.10806 | -0.42403 | -0.11554 | -0.019173 | -0.067414 | 0.35662 | 0.071376 | -0.11315 | 123.0213 | 122.9715 | 123.1549 | 66.7205 | -123.202 | 122.9313 | 123.1183 | 122.9337 | 66.7148 | -123.4709
2198.7969 | 123.23 | -66.7145 | 56.3553 | -0.0029761 | -0.02723 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.061862 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056108 | 0.036497 | 0.056599 | -66.729 | -0.003172 | -66.7506 | 56.3022 | 56.2387 | 56.4313 | -66.897 | -66.7474 | -0.008798 | -66.791 | 56.2031 | 56.3855 | 56.2559 | -67.1431 | -0.18256 | -0.053085 | -0.014478 | -0.036105 | 0.14646 | -0.11658 | 0.076019 | -0.42861 | -0.15216 | -0.032907 | -0.076569 | 0.35204 | 0.030175 | -0.099403 | 123.0167 | 122.9532 | 123.1458 | 66.7113 | -123.2523 | 122.9176 | 123.0999 | 122.9704 | 66.7057 | -123.4984
2199.7969 | 123.1979 | -66.7145 | 56.3278 | -0.0029761 | -0.02723 | -0.00039306 | 0.053081 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055681 | 0.036711 | 0.056385 | -66.7335 | -0.003172 | -66.7552 | 56.3022 | 56.2296 | 56.4313 | -66.897 | -66.7428 | -0.008798 | -66.7865 | 56.2077 | 56.39 | 56.2605 | -67.1385 | -0.18256 | -0.025619 | -0.019056 | -0.040683 | 0.14188 | -0.098268 | 0.10348 | -0.42403 | -0.12012 | -0.028328 | -0.071991 | 0.35204 | 0.062219 | -0.067359 | 123.0167 | 122.944 | 123.1458 | 66.7113 | -123.2249 | 122.9222 | 123.1045 | 122.9749 | 66.7057 | -123.4663
2200.7969 | 123.2254 | -66.7557 | 56.2454 | -0.0029761 | -0.027017 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055895 | 0.036925 | 0.056599 | -66.7244 | 0.001407 | -66.746 | 56.2976 | 56.2433 | 56.4359 | -66.8879 | -66.7382 | -0.00422 | -66.791 | 56.2077 | 56.3992 | 56.1918 | -67.1477 | -0.13221 | 0.052201 | 0.031299 | 0.009671 | 0.14188 | -0.002133 | 0.19046 | -0.39199 | -0.03772 | 0.017449 | -0.035371 | 0.35662 | 0.15378 | -0.05364 | 123.0533 | 122.999 | 123.1916 | 66.7571 | -123.1333 | 122.9634 | 123.1549 | 122.9475 | 66.7515 | -123.3931
2201.7969 | 123.1567 | -66.7419 | 56.3553 | -0.010607 | -0.02723 | 3.4136e-05 | 0.053081 | -0.0073736 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055895 | 0.037139 | 0.056812 | -66.729 | -0.003172 | -66.7506 | 56.3022 | 56.2433 | 56.4267 | -66.8833 | -66.7428 | -0.008798 | -66.7865 | 56.2169 | 56.3946 | 56.2284 | -67.1477 | -0.14136 | -0.053085 | 0.012987 | -0.00864 | 0.13272 | -0.112 | 0.071441 | -0.40572 | -0.13843 | -0.000863 | -0.044526 | 0.3612 | 0.039332 | -0.12687 | 123.0441 | 122.9852 | 123.1687 | 66.7388 | -123.2386 | 122.9588 | 123.1366 | 122.9704 | 66.7331 | -123.503
2202.8594 | 123.1338 | -66.7282 | 56.3736 | -0.0029761 | -0.027444 | -0.00017946 | 0.052867 | -0.0071598 | 0.062503 | 0.00015261 | -0.0028393 | -0.00098273 | 0.055895 | 0.036925 | 0.056385 | -66.7335 | -0.003172 | -66.7552 | 56.3022 | 56.2296 | 56.4359 | -66.897 | -66.7428 | -0.00422 | -66.7773 | 56.2031 | 56.3946 | 56.2376 | -67.1477 | -0.16883 | -0.071395 | -0.005324 | -0.026951 | 0.14188 | -0.14404 | 0.062288 | -0.41946 | -0.17047 | -0.014596 | -0.049101 | 0.37036 | 0.021022 | -0.13603 | 123.0304 | 122.9578 | 123.1641 | 66.725 | -123.2706 | 122.9313 | 123.1228 | 122.9658 | 66.724 | -123.5213
2203.7969 | 123.1842 | -66.7282 | 56.3324 | 0.0046549 | -0.02723 | 0.00024794 | 0.053081 | -0.0069462 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.056108 | 0.036711 | 0.056385 | -66.7335 | -0.003172 | -66.7506 | 56.3022 | 56.2433 | 56.4267 | -66.8925 | -66.7474 | -0.008798 | -66.791 | 56.2123 | 56.39 | 56.2284 | -67.1522 | -0.16425 | -0.030196 | -0.005324 | -0.022373 | 0.14188 | -0.089108 | 0.09433 | -0.42403 | -0.12012 | -0.019175 | -0.062837 | 0.3612 | 0.057642 | -0.10399 | 123.0304 | 122.9715 | 123.1549 | 66.725 | -123.2249 | 122.9405 | 123.1182 | 122.9566 | 66.7194 | -123.4846
2204.7969 | 123.175 | -66.7694 | 56.3324 | -0.0029761 | -0.027658 | -0.00017946 | 0.053081 | -0.0075872 | 0.062076 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056108 | 0.036711 | 0.056812 | -66.7244 | -0.012329 | -66.746 | 56.3114 | 56.2112 | 56.4313 | -66.8925 | -66.7474 | -0.008798 | -66.7819 | 56.2077 | 56.3946 | 56.2147 | -67.1431 | -0.12305 | -0.021039 | 0.045032 | 0.023404 | 0.14646 | -0.12116 | 0.098908 | -0.37368 | -0.1247 | 0.022024 | -0.012481 | 0.3612 | 0.062221 | -0.11772 | 123.0808 | 122.9806 | 123.2007 | 66.7571 | -123.2249 | 122.9771 | 123.164 | 122.9841 | 66.7606 | -123.4755
2205.8594 | 123.2849 | -66.7282 | 56.2912 | -0.0029761 | -0.027444 | -0.00017946 | 0.053081 | -0.0069462 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056322 | 0.036925 | 0.056599 | -66.729 | 0.001407 | -66.7552 | 56.3114 | 56.2341 | 56.4359 | -66.8787 | -66.7428 | -0.00422 | -66.791 | 56.2169 | 56.3946 | 56.2193 | -67.1385 | -0.15051 | 0.020159 | -0.000746 | -0.026951 | 0.12356 | -0.057068 | 0.14469 | -0.4103 | -0.07434 | -0.014596 | -0.062837 | 0.34746 | 0.10342 | -0.071945 | 123.0396 | 122.9623 | 123.1641 | 66.7296 | -123.1699 | 122.9451 | 123.1228 | 122.9475 | 66.724 | -123.4297
2206.7969 | 123.1247 | -66.7786 | 56.3232 | -0.010607 | -0.027444 | -0.00039306 | 0.053081 | -0.0071598 | 0.062076 | 0.0077831 | -0.0030529 | -0.00076913 | 0.056108 | 0.036925 | 0.056599 | -66.7381 | 0.001407 | -66.7506 | 56.3022 | 56.2387 | 56.4267 | -66.8925 | -66.7474 | -0.00422 | -66.7773 | 56.2123 | 56.3946 | 56.2193 | -67.1477 | -0.1139 | -0.021041 | 0.040452 | 0.027981 | 0.14188 | -0.084532 | 0.10348 | -0.3691 | -0.11096 | 0.031179 | 0.001253 | 0.37036 | 0.071376 | -0.10399 | 123.0808 | 123.0173 | 123.2053 | 66.78 | -123.2157 | 122.9908 | 123.1732 | 122.9978 | 66.7743 | -123.4709
2207.7969 | 123.2849 | -66.7099 | 56.2775 | -0.010607 | -0.027658 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.062289 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056108 | 0.036925 | 0.056599 | -66.729 | 0.001407 | -66.746 | 56.2976 | 56.2433 | 56.4267 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2123 | 56.3992 | 56.2467 | -67.1431 | -0.1734 | 0.020157 | -0.019056 | -0.036105 | 0.1373 | -0.034177 | 0.14926 | -0.43319 | -0.065185 | -0.032906 | -0.076569 | 0.35662 | 0.12173 | -0.030741 | 123.0075 | 122.9532 | 123.1366 | 66.7113 | -123.1608 | 122.9222 | 123.1091 | 122.9566 | 66.6965 | -123.4206
2208.8594 | 123.1613 | -66.7374 | 56.337 | -0.0029761 | -0.027658 | -0.00017946 | 0.053081 | -0.0071598 | 0.062076 | 0.0077831 | -0.0030529 | -0.00055553 | 0.055895 | 0.036925 | 0.056812 | -66.7335 | 0.001407 | -66.7552 | 56.3022 | 56.2296 | 56.4405 | -66.8833 | -66.7336 | -0.008798 | -66.7773 | 56.2077 | 56.3946 | 56.2238 | -67.1568 | -0.14594 | -0.034774 | 0.003832 | -0.017795 | 0.12814 | -0.10742 | 0.10349 | -0.41946 | -0.12927 | 0.003717 | -0.039945 | 0.37951 | 0.057643 | -0.11314 | 123.0396 | 122.9669 | 123.1778 | 66.7388 | -123.2203 | 122.9451 | 123.132 | 122.9612 | 66.7286 | -123.4938
2209.7969 | 123.1567 | -66.7511 | 56.3324 | -0.0029761 | -0.027444 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | -0.015108 | -0.0032665 | -0.00076913 | 0.055895 | 0.036497 | 0.056599 | -66.729 | 0.001407 | -66.7552 | 56.3068 | 56.2158 | 56.4267 | -66.8787 | -66.7382 | -0.008798 | -66.7865 | 56.2123 | 56.3946 | 56.2238 | -67.1477 | -0.12763 | -0.025618 | 0.022143 | -0.004062 | 0.12356 | -0.11658 | 0.09433 | -0.39657 | -0.12012 | 0.012872 | -0.03537 | 0.3612 | 0.062221 | -0.10856 | 123.0579 | 122.9669 | 123.1778 | 66.7525 | -123.2111 | 122.9634 | 123.1457 | 122.9749 | 66.7423 | -123.4801
2210.7969 | 123.2574 | -66.7236 | 56.3187 | -0.0029761 | -0.027658 | -0.00017946 | 0.053295 | -0.0073736 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.036711 | 0.056812 | -66.7381 | -0.007751 | -66.7506 | 56.3068 | 56.225 | 56.4267 | -66.8879 | -66.7382 | -0.008798 | -66.7865 | 56.2214 | 56.3946 | 56.2101 | -67.1385 | -0.16425 | -0.011886 | -0.014479 | -0.02695 | 0.1373 | -0.093692 | 0.10806 | -0.41487 | -0.097227 | -0.014594 | -0.062836 | 0.35204 | 0.075953 | -0.10857 | 123.0304 | 122.9486 | 123.1504 | 66.7159 | -123.2065 | 122.9451 | 123.1183 | 122.9337 | 66.7148 | -123.4572
2211.8594 | 123.2117 | -66.7145 | 56.3644 | 0.012286 | -0.027444 | -0.00060686 | 0.053081 | -0.0071598 | 0.062076 | -0.0074779 | -0.0028393 | -0.00034193 | 0.055895 | 0.036925 | 0.056385 | -66.7335 | 0.005985 | -66.7552 | 56.3068 | 56.2296 | 56.4313 | -66.8833 | -66.7382 | -0.00422 | -66.7819 | 56.2123 | 56.3992 | 56.233 | -67.1522 | -0.16882 | -0.057662 | -0.019056 | -0.040683 | 0.12814 | -0.13489 | 0.066864 | -0.43777 | -0.15216 | -0.023749 | -0.067412 | 0.37035 | 0.034756 | -0.13145 | 123.0213 | 122.944 | 123.1458 | 66.7205 | -123.2477 | 122.9268 | 123.1137 | 122.9475 | 66.7103 | -123.5167
2212.7969 | 123.1567 | -66.7831 | 56.3416 | -0.0029761 | -0.027444 | -0.00017946 | 0.053081 | -0.0071598 | 0.061862 | 0.0077831 | -0.0028393 | -0.00034193 | 0.056108 | 0.036925 | 0.056385 | -66.7335 | 0.001407 | -66.7506 | 56.3022 | 56.2387 | 56.4359 | -66.8925 | -66.7474 | -0.008798 | -66.791 | 56.2077 | 56.3992 | 56.2513 | -67.1431 | -0.10932 | -0.039352 | 0.049608 | 0.032559 | 0.14188 | -0.10284 | 0.094331 | -0.35994 | -0.13385 | 0.035757 | -0.007905 | 0.35204 | 0.057644 | -0.090249 | 123.0853 | 123.0219 | 123.219 | 66.7845 | -123.234 | 122.9908 | 123.1823 | 123.0344 | 66.7743 | -123.4846
2213.7969 | 123.1842 | -66.7786 | 56.3004 | -0.0029761 | -0.027444 | -0.00017946 | 0.053081 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.056108 | 0.036925 | 0.056385 | -66.7198 | -0.003172 | -66.7552 | 56.3022 | 56.2204 | 56.4313 | -66.8879 | -66.7474 | -0.013377 | -66.791 | 56.2031 | 56.3992 | 56.2101 | -67.1477 | -0.10932 | 0.001847 | 0.058765 | 0.023403 | 0.13272 | -0.079959 | 0.13095 | -0.3691 | -0.09723 | 0.031179 | -0.012483 | 0.35662 | 0.098843 | -0.090257 | 123.0808 | 122.999 | 123.2099 | 66.7754 | -123.1882 | 122.9817 | 123.1778 | 122.9887 | 66.7652 | -123.448
2214.7969 | 123.2117 | -66.7557 | 56.3278 | -0.0029761 | -0.027658 | -0.00039306 | 0.053295 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055895 | 0.036925 | 0.056385 | -66.7244 | 0.001407 | -66.7506 | 56.293 | 56.2387 | 56.4313 | -66.8833 | -66.7474 | -0.00422 | -66.7819 | 56.2031 | 56.3946 | 56.2193 | -67.1385 | -0.12763 | -0.034776 | 0.031299 | 0.005093 | 0.13272 | -0.08911 | 0.10348 | -0.38283 | -0.1247 | 0.008291 | -0.026214 | 0.35662 | 0.066798 | -0.10857 | 123.0487 | 122.9944 | 123.187 | 66.7571 | -123.2111 | 122.9588 | 123.1503 | 122.9749 | 66.7515 | -123.4663
2215.7969 | 123.2483 | -66.7603 | 56.282 | -0.018238 | -0.027658 | -0.00039306 | 0.053081 | -0.0069462 | 0.062289 | -0.0074779 | -0.0032665 | -0.00055553 | 0.056108 | 0.036711 | 0.056599 | -66.7335 | 0.005985 | -66.7643 | 56.3022 | 56.225 | 56.4267 | -66.8879 | -66.7428 | -0.008798 | -66.791 | 56.2169 | 56.3992 | 56.2238 | -67.1431 | -0.12763 | 0.020158 | 0.02672 | -0.004064 | 0.12356 | -0.05707 | 0.14468 | -0.38283 | -0.065184 | 0.017448 | -0.030793 | 0.35204 | 0.11715 | -0.058211 | 123.0625 | 122.9852 | 123.187 | 66.7662 | -123.1699 | 122.9771 | 123.1595 | 122.9841 | 66.7515 | -123.4251
2216.7969 | 123.2895 | -66.7053 | 56.2912 | -0.010607 | -0.02723 | -0.00039306 | 0.053295 | -0.0073736 | 0.062076 | -0.015108 | -0.0032665 | -0.00055553 | 0.056322 | 0.037139 | 0.056812 | -66.729 | 0.001407 | -66.7597 | 56.3114 | 56.225 | 56.4313 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2123 | 56.3946 | 56.2238 | -67.1477 | -0.17798 | 0.020159 | -0.023634 | -0.054418 | 0.12356 | -0.066226 | 0.14011 | -0.44234 | -0.078918 | -0.037484 | -0.081147 | 0.3612 | 0.10342 | -0.067367 | 123.0167 | 122.9303 | 123.1366 | 66.7067 | -123.1745 | 122.9176 | 123.0999 | 122.9292 | 66.6919 | -123.4389
2217.8594 | 123.1659 | -66.7557 | 56.3599 | -0.0029761 | -0.027658 | -0.00017946 | 0.052867 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055895 | 0.037352 | 0.057026 | -66.729 | 0.005985 | -66.7552 | 56.3068 | 56.2341 | 56.4359 | -66.8879 | -66.7382 | 0.000359 | -66.7865 | 56.2123 | 56.3992 | 56.2193 | -67.1522 | -0.13221 | -0.053084 | 0.02672 | 0.000515 | 0.13272 | -0.12573 | 0.076021 | -0.39657 | -0.14758 | 0.017449 | -0.030793 | 0.36577 | 0.039334 | -0.14061 | 123.0625 | 122.9898 | 123.1916 | 66.7617 | -123.2477 | 122.968 | 123.1549 | 122.9749 | 66.756 | -123.5121
2218.7969 | 123.2895 | -66.7328 | 56.2683 | -0.0029761 | -0.027444 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | -0.0074779 | -0.0030529 | -0.00034193 | 0.056322 | 0.036925 | 0.056385 | -66.729 | 0.001407 | -66.7552 | 56.3022 | 56.2387 | 56.4313 | -66.8879 | -66.7428 | -0.00422 | -66.7865 | 56.2077 | 56.39 | 56.2467 | -67.1477 | -0.15509 | 0.03389 | 0.003832 | -0.022373 | 0.13272 | -0.029601 | 0.16299 | -0.41488 | -0.060609 | -0.010018 | -0.053681 | 0.3612 | 0.12173 | -0.021586 | 123.035 | 122.9715 | 123.1641 | 66.7342 | -123.1562 | 122.9405 | 123.1228 | 122.9795 | 66.7286 | -123.416
2219.7969 | 123.1705 | -66.7786 | 56.3324 | -0.0029761 | -0.02723 | -0.00017946 | 0.053722 | -0.0073736 | 0.062076 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056322 | 0.036925 | 0.056599 | -66.7244 | 0.001407 | -66.7552 | 56.3022 | 56.225 | 56.4313 | -66.8925 | -66.752 | -0.00422 | -66.7865 | 56.2169 | 56.3946 | 56.2101 | -67.1477 | -0.1139 | -0.030196 | 0.054187 | 0.023403 | 0.1373 | -0.10742 | 0.098908 | -0.3691 | -0.11554 | 0.026601 | -0.007905 | 0.3612 | 0.062221 | -0.1223 | 123.0808 | 123.0035 | 123.2099 | 66.78 | -123.2249 | 122.9954 | 123.1732 | 122.9887 | 66.7743 | -123.4801
2220.8594 | 123.2483 | -66.7282 | 56.2683 | -0.0029761 | -0.027658 | -0.00039306 | 0.053508 | -0.0073736 | 0.062503 | 0.00015261 | -0.0028393 | -0.00076913 | 0.056322 | 0.036925 | 0.056812 | -66.7244 | 0.001407 | -66.7506 | 56.3068 | 56.2387 | 56.4359 | -66.8879 | -66.7428 | -0.00422 | -66.7865 | 56.1985 | 56.3946 | 56.2147 | -67.1431 | -0.15967 | 0.038468 | 0.003833 | -0.022373 | 0.1373 | -0.029601 | 0.16757 | -0.41488 | -0.069766 | -0.014596 | -0.058259 | 0.35662 | 0.12631 | -0.053636 | 123.035 | 122.9669 | 123.1641 | 66.7296 | -123.1562 | 122.9268 | 123.1228 | 122.9429 | 66.724 | -123.4114
2221.7969 | 123.175 | -66.7374 | 56.3507 | -0.0029761 | -0.02723 | -0.00060686 | 0.053081 | -0.0071598 | 0.062076 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055895 | 0.037139 | 0.056385 | -66.729 | 0.001407 | -66.7506 | 56.3114 | 56.2341 | 56.4405 | -66.8925 | -66.752 | 0.000359 | -66.7819 | 56.2077 | 56.39 | 56.2376 | -67.1522 | -0.1551 | -0.03935 | 0.00841 | -0.013217 | 0.14188 | -0.11658 | 0.089755 | -0.41488 | -0.14301 | -0.014597 | -0.044524 | 0.37035 | 0.039331 | -0.11314 | 123.0487 | 122.9715 | 123.1778 | 66.7388 | -123.2432 | 122.9451 | 123.1274 | 122.9749 | 66.7377 | -123.503
2222.8594 | 123.1338 | -66.7419 | 56.3461 | -0.010607 | -0.027658 | 3.4136e-05 | 0.053081 | -0.0075872 | 0.062503 | -0.0074779 | -0.0032665 | -0.00034193 | 0.056108 | 0.036711 | 0.056171 | -66.7335 | -0.003172 | -66.7597 | 56.3022 | 56.2433 | 56.4267 | -66.9016 | -66.752 | 0.000359 | -66.7819 | 56.2123 | 56.3855 | 56.2238 | -67.1477 | -0.15968 | -0.043929 | 0.008409 | -0.017797 | 0.14188 | -0.10284 | 0.080597 | -0.40572 | -0.13385 | -0.01002 | -0.039947 | 0.36578 | 0.039331 | -0.1223 | 123.0441 | 122.9852 | 123.1687 | 66.7388 | -123.2477 | 122.9542 | 123.1274 | 122.9658 | 66.7423 | -123.4938
2223.7969 | 123.1613 | -66.7694 | 56.3278 | -0.0029761 | -0.027444 | -0.00039306 | 0.053081 | -0.0073736 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.036711 | 0.056599 | -66.729 | 0.001407 | -66.7689 | 56.3022 | 56.225 | 56.4405 | -66.8879 | -66.7428 | -0.00422 | -66.791 | 56.1985 | 56.3992 | 56.2238 | -67.1431 | -0.11847 | -0.025619 | 0.040453 | 0.000513 | 0.11899 | -0.10285 | 0.11264 | -0.37368 | -0.12927 | 0.026603 | -0.021638 | 0.35204 | 0.071377 | -0.10399 | 123.0716 | 122.9944 | 123.2099 | 66.7708 | -123.2157 | 122.968 | 123.1686 | 122.9932 | 66.7652 | -123.4709
2224.7969 | 123.2895 | -66.7007 | 56.3278 | 0.0046549 | -0.027872 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062503 | -0.0074779 | -0.0028393 | -0.00034193 | 0.055895 | 0.037139 | 0.056599 | -66.729 | 0.001407 | -66.7597 | 56.3022 | 56.2387 | 56.4313 | -66.8833 | -66.752 | -0.013377 | -66.7956 | 56.2123 | 56.3946 | 56.1918 | -67.1477 | -0.18256 | -0.025619 | -0.028211 | -0.058995 | 0.12356 | -0.08911 | 0.10348 | -0.44692 | -0.11554 | -0.051218 | -0.094881 | 0.35204 | 0.066798 | -0.13604 | 123.0029 | 122.9395 | 123.132 | 66.7022 | -123.2111 | 122.913 | 123.0954 | 122.8925 | 66.6874 | -123.4755
2225.8594 | 123.23 | -66.7511 | 56.3828 | -0.010607 | -0.027444 | -0.00039306 | 0.052867 | -0.0071598 | 0.062289 | 0.0077831 | -0.0028393 | -0.00076913 | 0.055681 | 0.036711 | 0.056812 | -66.729 | -0.003172 | -66.7552 | 56.3114 | 56.2296 | 56.4359 | -66.8879 | -66.7428 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2376 | -67.1431 | -0.13678 | -0.071393 | 0.022143 | -0.004062 | 0.13272 | -0.1532 | 0.053133 | -0.39199 | -0.17505 | 0.008293 | -0.03537 | 0.35662 | 0.016446 | -0.14518 | 123.0625 | 122.9807 | 123.187 | 66.7479 | -123.2706 | 122.9588 | 123.1503 | 122.9887 | 66.7469 | -123.5258
2226.7969 | 123.262 | -66.7236 | 56.3232 | -0.010607 | -0.027658 | -0.00017946 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.056108 | 0.037352 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3022 | 56.2341 | 56.4313 | -66.8879 | -66.7565 | -0.008798 | -66.7819 | 56.2123 | 56.3946 | 56.2101 | -67.1477 | -0.16425 | -0.021041 | -0.009901 | -0.036107 | 0.12814 | -0.089111 | 0.10806 | -0.42403 | -0.11096 | -0.032909 | -0.058257 | 0.36578 | 0.071376 | -0.11315 | 123.0258 | 122.9578 | 123.1549 | 66.725 | -123.2111 | 122.9359 | 123.1183 | 122.9337 | 66.7148 | -123.4709
2227.7969 | 123.1705 | -66.7465 | 56.3644 | -0.0029761 | -0.028085 | 3.4136e-05 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.037139 | 0.057026 | -66.7335 | 0.005985 | -66.7552 | 56.3068 | 56.2296 | 56.4267 | -66.897 | -66.752 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2147 | -67.1431 | -0.15052 | -0.057662 | 0.012987 | -0.00864 | 0.14188 | -0.13489 | 0.062286 | -0.39657 | -0.15674 | -0.005442 | -0.039948 | 0.35662 | 0.034756 | -0.14977 | 123.0533 | 122.9761 | 123.1732 | 66.7525 | -123.2615 | 122.9542 | 123.1457 | 122.9612 | 66.7423 | -123.5075
2228.7969 | 123.2895 | -66.7145 | 56.2729 | -0.010607 | -0.027872 | -0.00017946 | 0.053508 | -0.0069462 | 0.062717 | 0.015414 | -0.0032665 | -0.00034193 | 0.056108 | 0.036711 | 0.056599 | -66.7335 | 0.001407 | -66.7689 | 56.3022 | 56.2341 | 56.4313 | -66.8925 | -66.7428 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.1964 | -67.1477 | -0.17798 | 0.029313 | -0.019056 | -0.054418 | 0.12356 | -0.038757 | 0.15842 | -0.43319 | -0.060607 | -0.028328 | -0.071991 | 0.3612 | 0.12631 | -0.076527 | 123.0167 | 122.9486 | 123.1458 | 66.7159 | -123.1653 | 122.9268 | 123.1137 | 122.9108 | 66.7103 | -123.4206
2229.8594 | 123.175 | -66.8106 | 56.337 | 0.0046549 | -0.027444 | -0.00039306 | 0.053081 | -0.0071598 | 0.062503 | 0.00015261 | -0.0028393 | -0.00034193 | 0.056108 | 0.037139 | 0.056599 | -66.729 | -0.003172 | -66.7552 | 56.3022 | 56.2387 | 56.4359 | -66.8925 | -66.752 | 0.000359 | -66.7819 | 56.2123 | 56.3992 | 56.2376 | -67.1477 | -0.081853 | -0.034774 | 0.081652 | 0.055447 | 0.1373 | -0.098265 | 0.098909 | -0.33706 | -0.12469 | 0.058645 | 0.028718 | 0.36578 | 0.062222 | -0.099407 | 123.1128 | 123.0493 | 123.2465 | 66.8074 | -123.2294 | 123.0229 | 123.2098 | 123.0482 | 66.811 | -123.4846
2230.7969 | 123.2346 | -66.7603 | 56.3095 | 0.0046549 | -0.027658 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056108 | 0.036925 | 0.056171 | -66.7335 | 0.001407 | -66.7643 | 56.3022 | 56.2296 | 56.4313 | -66.8879 | -66.7428 | -0.008798 | -66.791 | 56.2123 | 56.3992 | 56.2147 | -67.1477 | -0.12763 | -0.007308 | 0.02672 | -0.004064 | 0.12356 | -0.079957 | 0.1218 | -0.38741 | -0.097228 | 0.017448 | -0.030793 | 0.35662 | 0.089688 | -0.094834 | 123.0625 | 122.9898 | 123.1916 | 66.7617 | -123.1974 | 122.9725 | 123.1595 | 122.9749 | 66.7515 | -123.4572
2231.7969 | 123.2803 | -66.7145 | 56.2912 | -0.0029761 | -0.027872 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00034193 | 0.056108 | 0.037139 | 0.056599 | -66.729 | 0.005985 | -66.7552 | 56.3068 | 56.2204 | 56.4313 | -66.8925 | -66.7428 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2238 | -67.1431 | -0.17798 | 0.01558 | -0.014478 | -0.040683 | 0.1373 | -0.070804 | 0.14011 | -0.42861 | -0.083497 | -0.028328 | -0.071991 | 0.35662 | 0.108 | -0.067367 | 123.0213 | 122.9349 | 123.1458 | 66.7205 | -123.1837 | 122.9222 | 123.1137 | 122.9383 | 66.7103 | -123.4343
2232.8594 | 123.1659 | -66.7511 | 56.3461 | -0.010607 | -0.027658 | -0.00017946 | 0.053295 | -0.0075872 | 0.062503 | -0.0074779 | -0.0030529 | -0.00034193 | 0.055895 | 0.037139 | 0.056599 | -66.7335 | 0.001407 | -66.7506 | 56.3022 | 56.2341 | 56.4313 | -66.897 | -66.7474 | 0.000359 | -66.7865 | 56.2169 | 56.3992 | 56.233 | -67.1522 | -0.14594 | -0.043929 | 0.017565 | 0.000516 | 0.14646 | -0.112 | 0.085175 | -0.40114 | -0.12927 | 0.003714 | -0.03537 | 0.36577 | 0.053067 | -0.11314 | 123.0533 | 122.9852 | 123.1824 | 66.7525 | -123.2432 | 122.968 | 123.1503 | 122.9841 | 66.7515 | -123.4984
2233.7969 | 123.2666 | -66.7191 | 56.3187 | -0.0029761 | -0.027658 | -0.00017946 | 0.053295 | -0.0071598 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.056322 | 0.036925 | 0.056599 | -66.7381 | 0.001407 | -66.746 | 56.3068 | 56.2433 | 56.4359 | -66.8879 | -66.752 | -0.00422 | -66.7865 | 56.2169 | 56.3992 | 56.2147 | -67.1431 | -0.16883 | -0.011886 | -0.019057 | -0.02695 | 0.14188 | -0.075376 | 0.11722 | -0.42403 | -0.10181 | -0.032908 | -0.067414 | 0.35662 | 0.080532 | -0.10399 | 123.0258 | 122.9623 | 123.1549 | 66.7205 | -123.2065 | 122.9359 | 123.1183 | 122.9337 | 66.7148 | -123.4618
2234.7969 | 123.2254 | -66.7191 | 56.3599 | -0.0029761 | -0.027872 | -0.00017946 | 0.053081 | -0.0073736 | 0.062289 | 0.0077831 | -0.0030529 | -0.00098273 | 0.056108 | 0.036925 | 0.056812 | -66.7335 | -0.007751 | -66.7643 | 56.3022 | 56.2341 | 56.4313 | -66.8833 | -66.7428 | -0.008798 | -66.791 | 56.2123 | 56.4038 | 56.2559 | -67.1477 | -0.16425 | -0.057662 | -0.014479 | -0.045263 | 0.11898 | -0.12573 | 0.071442 | -0.42861 | -0.14758 | -0.023751 | -0.071992 | 0.35662 | 0.043912 | -0.10398 | 123.0213 | 122.9532 | 123.1504 | 66.7113 | -123.2432 | 122.9313 | 123.1228 | 122.9749 | 66.7103 | -123.5075
2235.7969 | 123.3032 | -66.7007 | 56.3049 | -0.018238 | -0.027872 | -0.00060686 | 0.053081 | -0.0067326 | 0.062503 | -0.0074779 | -0.0034801 | -0.00055553 | 0.056535 | 0.037139 | 0.056599 | -66.729 | -0.007751 | -66.7689 | 56.3068 | 56.2296 | 56.4267 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.3992 | 56.233 | -67.1477 | -0.18714 | 0.001847 | -0.028211 | -0.068151 | 0.11899 | -0.07538 | 0.12179 | -0.44692 | -0.092651 | -0.051218 | -0.090302 | 0.35662 | 0.094265 | -0.071942 | 123.0075 | 122.9303 | 123.1275 | 66.693 | -123.1928 | 122.913 | 123.0999 | 122.9337 | 66.6965 | -123.4526
2236.7969 | 123.3215 | -66.6916 | 56.3324 | -0.0029761 | -0.028085 | -0.00039306 | 0.053508 | -0.0073736 | 0.062717 | 0.0077831 | -0.0028393 | -0.00055553 | 0.055895 | 0.037352 | 0.056599 | -66.729 | -0.003172 | -66.7552 | 56.3114 | 56.2387 | 56.4313 | -66.8879 | -66.7474 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.2193 | -67.1477 | -0.19629 | -0.021039 | -0.037367 | -0.063572 | 0.13272 | -0.093687 | 0.098908 | -0.45608 | -0.11554 | -0.055796 | -0.099458 | 0.35662 | 0.071378 | -0.11314 | 123.0029 | 122.9303 | 123.1229 | 66.6884 | -123.2203 | 122.9084 | 123.0954 | 122.9108 | 66.6919 | -123.4801
2237.8594 | 123.2758 | -66.7374 | 56.2912 | 0.0046549 | -0.027872 | -0.00017946 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0028393 | -0.00055553 | 0.056108 | 0.036925 | 0.056599 | -66.7335 | 0.005985 | -66.7552 | 56.2976 | 56.2387 | 56.4359 | -66.8879 | -66.752 | -0.008798 | -66.7865 | 56.2077 | 56.3946 | 56.2009 | -67.1385 | -0.15052 | 0.006424 | 0.003832 | -0.017795 | 0.13272 | -0.052489 | 0.14469 | -0.40114 | -0.083497 | -0.014597 | -0.049103 | 0.35204 | 0.10342 | -0.09026 | 123.035 | 122.9761 | 123.1732 | 66.7434 | -123.1791 | 122.9451 | 123.132 | 122.9383 | 66.7286 | -123.4297
2238.7969 | 123.2941 | -66.6962 | 56.3507 | -0.0029761 | -0.028085 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056322 | 0.037352 | 0.057026 | -66.729 | -0.012329 | -66.7506 | 56.3068 | 56.2433 | 56.4313 | -66.8925 | -66.7474 | -0.008798 | -66.7865 | 56.2169 | 56.4038 | 56.2421 | -67.1477 | -0.19629 | -0.043929 | -0.032789 | -0.054416 | 0.14188 | -0.10742 | 0.080597 | -0.4515 | -0.13385 | -0.051218 | -0.090302 | 0.3612 | 0.053067 | -0.10856 | 123.0029 | 122.9395 | 123.1275 | 66.6838 | -123.2432 | 122.913 | 123.0999 | 122.9383 | 66.6874 | -123.4984
2239.8594 | 123.2941 | -66.6824 | 56.3232 | -0.0029761 | -0.027658 | -0.00017946 | 0.053508 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055895 | 0.036925 | 0.056385 | -66.729 | 0.005985 | -66.7506 | 56.3022 | 56.2433 | 56.4313 | -66.8879 | -66.7428 | 0.000359 | -66.7819 | 56.2123 | 56.4038 | 56.2101 | -67.1522 | -0.20545 | -0.021041 | -0.046522 | -0.068149 | 0.1373 | -0.079953 | 0.10806 | -0.46981 | -0.11096 | -0.060372 | -0.099456 | 0.37035 | 0.080533 | -0.11315 | 122.9846 | 122.9257 | 123.1137 | 66.6884 | -123.2111 | 122.8947 | 123.0862 | 122.8925 | 66.6828 | -123.4755
2240.7969 | 123.2941 | -66.6916 | 56.3507 | 0.012286 | -0.028299 | -0.00039306 | 0.053722 | -0.0075872 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.056108 | 0.037352 | 0.056171 | -66.7335 | 0.001407 | -66.7506 | 56.3022 | 56.2479 | 56.4359 | -66.8833 | -66.7428 | -0.00422 | -66.7865 | 56.2031 | 56.4038 | 56.233 | -67.1477 | -0.19171 | -0.048507 | -0.041945 | -0.058994 | 0.13272 | -0.10284 | 0.085176 | -0.45608 | -0.14758 | -0.051217 | -0.09488 | 0.3612 | 0.053067 | -0.11772 | 122.9938 | 122.9395 | 123.1275 | 66.693 | -123.234 | 122.8947 | 123.0954 | 122.9246 | 66.6874 | -123.4984
2241.7969 | 123.2758 | -66.7465 | 56.3278 | 0.0046549 | -0.028085 | -0.00060686 | 0.053295 | -0.0078008 | 0.062076 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055895 | 0.037352 | 0.056599 | -66.7381 | -0.007751 | -66.7597 | 56.3068 | 56.2387 | 56.4313 | -66.8925 | -66.7474 | -0.00422 | -66.7819 | 56.2123 | 56.3946 | 56.233 | -67.1522 | -0.14594 | -0.021041 | 0.008409 | -0.013219 | 0.13272 | -0.08911 | 0.10348 | -0.40572 | -0.11554 | -0.000864 | -0.035369 | 0.37035 | 0.066798 | -0.09483 | 123.0533 | 122.9852 | 123.1778 | 66.7388 | -123.2203 | 122.9588 | 123.1411 | 122.9795 | 66.7423 | -123.4801
2242.7969 | 123.2895 | -66.7007 | 56.337 | -0.0029761 | -0.027444 | -0.00039306 | 0.053295 | -0.0071598 | 0.062289 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055895 | 0.037566 | 0.056171 | -66.729 | 0.001407 | -66.7643 | 56.2976 | 56.2341 | 56.4313 | -66.8925 | -66.752 | -0.00422 | -66.791 | 56.2214 | 56.4038 | 56.233 | -67.1477 | -0.19172 | -0.039352 | -0.028211 | -0.063573 | 0.12814 | -0.10284 | 0.09433 | -0.44692 | -0.11554 | -0.051218 | -0.090302 | 0.35662 | 0.0668 | -0.10399 | 122.9984 | 122.9349 | 123.132 | 66.7022 | -123.2294 | 122.9222 | 123.1045 | 122.9337 | 66.6965 | -123.4846
2243.8594 | 123.1567 | -66.7694 | 56.3324 | -0.0029761 | -0.028085 | -0.00039306 | 0.053081 | -0.0075872 | 0.062289 | 0.0077831 | -0.0032665 | -0.00098273 | 0.056108 | 0.037139 | 0.056385 | -66.729 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.4405 | -66.8925 | -66.7565 | -0.008798 | -66.7819 | 56.2123 | 56.3992 | 56.2238 | -67.1477 | -0.12305 | -0.025618 | 0.040453 | 0.005091 | 0.12814 | -0.093687 | 0.10807 | -0.37826 | -0.12012 | 0.012867 | -0.012481 | 0.36578 | 0.0668 | -0.10856 | 123.0762 | 123.0081 | 123.2099 | 66.7708 | -123.2249 | 122.9817 | 123.1686 | 122.9932 | 66.7606 | -123.4801
2244.7969 | 123.1384 | -66.7694 | 56.3644 | -0.0029761 | -0.027658 | -0.00060686 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00098273 | 0.056322 | 0.036925 | 0.056812 | -66.729 | -0.003172 | -66.7643 | 56.3068 | 56.2341 | 56.4359 | -66.897 | -66.752 | 0.000359 | -66.7865 | 56.2077 | 56.3992 | 56.2193 | -67.1431 | -0.12763 | -0.057662 | 0.040453 | 0.005091 | 0.13272 | -0.13031 | 0.071443 | -0.37368 | -0.15674 | 0.017446 | -0.01706 | 0.35662 | 0.034756 | -0.14519 | 123.0762 | 123.0035 | 123.2053 | 66.7662 | -123.2615 | 122.9771 | 123.1686 | 122.9887 | 66.7698 | -123.5075
2245.7969 | 123.2758 | -66.7007 | 56.3416 | -0.0029761 | -0.027872 | -0.00017946 | 0.053295 | -0.0073736 | 0.062076 | 0.015414 | -0.0032665 | -0.00076913 | 0.055467 | 0.037139 | 0.056385 | -66.7381 | -0.003172 | -66.7643 | 56.3022 | 56.2433 | 56.4359 | -66.8879 | -66.7474 | 0.000359 | -66.7819 | 56.2169 | 56.39 | 56.2284 | -67.1477 | -0.18714 | -0.039352 | -0.037367 | -0.063573 | 0.12356 | -0.098264 | 0.094331 | -0.44692 | -0.12469 | -0.04664 | -0.081145 | 0.36578 | 0.048486 | -0.11314 | 123.0029 | 122.944 | 123.1366 | 66.6976 | -123.2294 | 122.9176 | 123.0908 | 122.9292 | 66.7011 | -123.4892
2246.8594 | 123.2117 | -66.7007 | 56.337 | -0.0029761 | -0.028085 | -0.00039306 | 0.053081 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00076913 | 0.055895 | 0.036925 | 0.056171 | -66.729 | -0.003172 | -66.7552 | 56.2976 | 56.2341 | 56.4313 | -66.897 | -66.7474 | -0.00422 | -66.7819 | 56.2123 | 56.3992 | 56.233 | -67.1522 | -0.1963 | -0.039352 | -0.028211 | -0.054416 | 0.14188 | -0.10284 | 0.09433 | -0.4515 | -0.12469 | -0.04664 | -0.081145 | 0.37035 | 0.062222 | -0.10399 | 122.9984 | 122.9349 | 123.132 | 66.6976 | -123.234 | 122.913 | 123.0999 | 122.9337 | 66.6965 | -123.4892
2247.7969 | 123.3307 | -66.6916 | 56.3095 | -0.010607 | -0.027658 | -0.00017946 | 0.053295 | -0.0071598 | 0.062076 | 0.0077831 | -0.0030529 | -0.0011965 | 0.055895 | 0.037566 | 0.056385 | -66.729 | -0.003172 | -66.7597 | 56.2976 | 56.2341 | 56.4313 | -66.8925 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.4038 | 56.2055 | -67.1477 | -0.20087 | -0.011886 | -0.037367 | -0.068151 | 0.13272 | -0.075378 | 0.1218 | -0.45608 | -0.097228 | -0.060374 | -0.099458 | 0.35662 | 0.094266 | -0.10399 | 122.9892 | 122.9257 | 123.1229 | 66.6884 | -123.202 | 122.9039 | 123.0954 | 122.8971 | 66.6874 | -123.4572
2248.8594 | 123.1567 | -66.7511 | 56.3828 | 0.0046549 | -0.027872 | -0.00017946 | 0.053295 | -0.0071598 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055895 | 0.037566 | 0.056385 | -66.7335 | -0.003172 | -66.7506 | 56.3068 | 56.2341 | 56.4313 | -66.897 | -66.7428 | -0.00422 | -66.7819 | 56.2077 | 56.4038 | 56.233 | -67.1431 | -0.14594 | -0.075972 | 0.017565 | 0.000516 | 0.14646 | -0.14862 | 0.048554 | -0.39199 | -0.17505 | 0.008293 | -0.030791 | 0.3612 | 0.021024 | -0.14976 | 123.0579 | 122.9852 | 123.1824 | 66.7479 | -123.2798 | 122.9588 | 123.1549 | 122.9841 | 66.7469 | -123.5258
2249.7969 | 123.143 | -66.7328 | 56.369 | 0.0046549 | -0.028085 | -0.00017946 | 0.053081 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00034193 | 0.056535 | 0.037352 | 0.056171 | -66.729 | 0.001407 | -66.7643 | 56.3022 | 56.225 | 56.4267 | -66.8879 | -66.7474 | -0.008798 | -66.7773 | 56.2123 | 56.39 | 56.2284 | -67.1431 | -0.15509 | -0.066818 | 0.003832 | -0.03153 | 0.12356 | -0.14405 | 0.057708 | -0.4103 | -0.15674 | -0.014597 | -0.044523 | 0.36578 | 0.02102 | -0.14061 | 123.035 | 122.9578 | 123.1595 | 66.7342 | -123.2569 | 122.9451 | 123.1228 | 122.9612 | 66.724 | -123.5121
2250.7969 | 123.1979 | -66.7419 | 56.3507 | 0.0046549 | -0.027658 | -0.00017946 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0028393 | -0.00055553 | 0.055681 | 0.036925 | 0.056599 | -66.729 | 0.001407 | -66.7597 | 56.3068 | 56.2433 | 56.4313 | -66.897 | -66.7474 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.2009 | -67.1477 | -0.1551 | -0.043929 | 0.012987 | -0.017797 | 0.1373 | -0.10742 | 0.080597 | -0.40572 | -0.13843 | -0.005442 | -0.044526 | 0.3612 | 0.048489 | -0.14977 | 123.0487 | 122.9852 | 123.1732 | 66.7434 | -123.2477 | 122.9542 | 123.1411 | 122.9429 | 66.7377 | -123.4984
2251.7969 | 123.1567 | -66.7603 | 56.3416 | -0.010607 | -0.027658 | -0.00017946 | 0.053081 | -0.0073736 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055681 | 0.037139 | 0.056812 | -66.729 | 0.001407 | -66.7552 | 56.3022 | 56.2296 | 56.4313 | -66.8925 | -66.7382 | -0.00422 | -66.791 | 56.2077 | 56.4038 | 56.2238 | -67.1522 | -0.13221 | -0.039352 | 0.031298 | 0.005093 | 0.1373 | -0.112 | 0.089752 | -0.39199 | -0.13385 | 0.022027 | -0.030793 | 0.3612 | 0.062222 | -0.11772 | 123.0625 | 122.9898 | 123.1916 | 66.7617 | -123.234 | 122.968 | 123.164 | 122.9841 | 66.756 | -123.4938
2252.7969 | 123.2162 | -66.7419 | 56.3507 | -0.0029761 | -0.028085 | -0.00017946 | 0.053081 | -0.0071598 | 0.062289 | 0.015414 | -0.0034801 | -0.00076913 | 0.055681 | 0.037352 | 0.056599 | -66.7335 | 0.001407 | -66.7643 | 56.2976 | 56.2387 | 56.4359 | -66.8925 | -66.7611 | 0.000359 | -66.7865 | 56.2169 | 56.3946 | 56.2147 | -67.1477 | -0.15052 | -0.053085 | 0.008409 | -0.022375 | 0.12814 | -0.112 | 0.085176 | -0.40572 | -0.13385 | -0.019178 | -0.044526 | 0.3612 | 0.04391 | -0.13603 | 123.0396 | 122.9807 | 123.1778 | 66.7434 | -123.2432 | 122.9588 | 123.1366 | 122.9566 | 66.7423 | -123.4984
2253.8594 | 123.2849 | -66.7053 | 56.337 | 0.0046549 | -0.028085 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055681 | 0.037352 | 0.056171 | -66.729 | 0.001407 | -66.7689 | 56.2976 | 56.2296 | 56.4313 | -66.8925 | -66.7474 | 0.000359 | -66.7865 | 56.2077 | 56.3992 | 56.2009 | -67.1477 | -0.18714 | -0.039352 | -0.023634 | -0.063574 | 0.12356 | -0.10742 | 0.09433 | -0.44234 | -0.12927 | -0.042063 | -0.081147 | 0.3612 | 0.062222 | -0.13604 | 123.0029 | 122.9349 | 123.1366 | 66.7067 | -123.2294 | 122.913 | 123.1045 | 122.9063 | 66.7057 | -123.4846
2254.7969 | 123.1567 | -66.7786 | 56.3187 | 0.012286 | -0.027872 | 3.4136e-05 | 0.052654 | -0.0071598 | 0.062076 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055681 | 0.037352 | 0.056599 | -66.7335 | -0.003172 | -66.7552 | 56.3114 | 56.2341 | 56.4313 | -66.8879 | -66.752 | 0.000359 | -66.7865 | 56.2123 | 56.3946 | 56.233 | -67.1522 | -0.10932 | -0.007307 | 0.04503 | 0.023403 | 0.13272 | -0.084534 | 0.11264 | -0.37368 | -0.10638 | 0.026601 | -0.007905 | 0.36577 | 0.075953 | -0.085675 | 123.0899 | 123.0127 | 123.2099 | 66.7754 | -123.2065 | 122.9908 | 123.1732 | 123.0116 | 66.7789 | -123.4709
2255.7969 | 123.1934 | -66.7603 | 56.369 | 0.012286 | -0.028085 | -0.00039306 | 0.052867 | -0.0073736 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.056322 | 0.037352 | 0.056599 | -66.7335 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.4405 | -66.8925 | -66.752 | -0.013377 | -66.791 | 56.2169 | 56.3946 | 56.2376 | -67.1477 | -0.13221 | -0.06224 | 0.02672 | -0.004064 | 0.12814 | -0.13031 | 0.071444 | -0.38741 | -0.15216 | 0.008291 | -0.030793 | 0.35662 | 0.025599 | -0.13145 | 123.067 | 122.999 | 123.2007 | 66.7617 | -123.2615 | 122.9771 | 123.1549 | 122.9978 | 66.7469 | -123.5167
2256.7969 | 123.2162 | -66.7328 | 56.3324 | 0.012286 | -0.027872 | -0.00039306 | 0.052654 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.056108 | 0.037566 | 0.056385 | -66.729 | 0.001407 | -66.7597 | 56.3114 | 56.2433 | 56.4359 | -66.9016 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2421 | -67.1431 | -0.16883 | -0.021039 | 0.003832 | -0.026952 | 0.14188 | -0.089108 | 0.10349 | -0.4103 | -0.1247 | -0.014597 | -0.053681 | 0.35662 | 0.0668 | -0.09025 | 123.0441 | 122.9761 | 123.1687 | 66.7342 | -123.234 | 122.9405 | 123.132 | 122.9749 | 66.7286 | -123.4755
2257.7969 | 123.2162 | -66.7465 | 56.3416 | 0.0046549 | -0.028085 | -0.00017946 | 0.052867 | -0.0071598 | 0.062289 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055895 | 0.037566 | 0.056385 | -66.7335 | 0.010564 | -66.7643 | 56.3068 | 56.2204 | 56.445 | -66.8879 | -66.7474 | -0.00422 | -66.791 | 56.2077 | 56.3992 | 56.2147 | -67.1431 | -0.14136 | -0.034774 | 0.012987 | -0.017797 | 0.12356 | -0.12116 | 0.10349 | -0.39657 | -0.13385 | -0.000864 | -0.044526 | 0.35204 | 0.057644 | -0.12688 | 123.0533 | 122.9669 | 123.1916 | 66.7571 | -123.2294 | 122.9542 | 123.1457 | 122.9612 | 66.7423 | -123.4846
2258.8594 | 123.23 | -66.7145 | 56.3599 | 0.0046549 | -0.028085 | -0.00017946 | 0.052867 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00076913 | 0.056108 | 0.037566 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3068 | 56.2387 | 56.4405 | -66.8879 | -66.7474 | -0.00422 | -66.791 | 56.2123 | 56.4038 | 56.233 | -67.1477 | -0.1734 | -0.053084 | -0.019056 | -0.045262 | 0.12814 | -0.12115 | 0.0806 | -0.43319 | -0.14758 | -0.032907 | -0.076569 | 0.35662 | 0.043912 | -0.12687 | 123.0213 | 122.9532 | 123.1549 | 66.7159 | -123.2477 | 122.9268 | 123.1183 | 122.9475 | 66.7103 | -123.5075
2259.7969 | 123.1796 | -66.7465 | 56.337 | 0.0046549 | -0.027658 | -0.00039306 | 0.052867 | -0.0071598 | 0.062289 | -0.0074779 | -0.0028393 | -0.00034193 | 0.056108 | 0.037139 | 0.056385 | -66.7381 | 0.001407 | -66.7597 | 56.3022 | 56.2341 | 56.4359 | -66.8925 | -66.7474 | -0.008798 | -66.7773 | 56.2169 | 56.3992 | 56.2101 | -67.1431 | -0.14594 | -0.034774 | 0.008409 | -0.013219 | 0.13272 | -0.10284 | 0.098909 | -0.39657 | -0.12012 | -0.000864 | -0.03079 | 0.36578 | 0.062222 | -0.12688 | 123.0487 | 122.9807 | 123.1824 | 66.7479 | -123.2294 | 122.9634 | 123.1457 | 122.9566 | 66.7377 | -123.4801
2260.7969 | 123.262 | -66.7282 | 56.2729 | 0.0046549 | -0.027872 | -0.00017946 | 0.053295 | -0.0073736 | 0.062076 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056108 | 0.037352 | 0.056385 | -66.7335 | -0.007751 | -66.7552 | 56.3022 | 56.2341 | 56.4359 | -66.8925 | -66.7336 | -0.013377 | -66.7819 | 56.2123 | 56.3992 | 56.2467 | -67.1477 | -0.16425 | 0.029313 | -0.005324 | -0.026951 | 0.1373 | -0.038757 | 0.163 | -0.41946 | -0.060607 | -0.005439 | -0.05368 | 0.36578 | 0.12631 | -0.026163 | 123.0304 | 122.9623 | 123.1641 | 66.7205 | -123.1653 | 122.9405 | 123.1274 | 122.9749 | 66.7148 | -123.4206
2261.8594 | 123.1522 | -66.7511 | 56.3782 | -0.0029761 | -0.027658 | -0.00039306 | 0.052867 | -0.0075872 | 0.062076 | -0.0074779 | -0.0030529 | -0.00034193 | 0.056108 | 0.037139 | 0.056385 | -66.729 | -0.003172 | -66.7552 | 56.3022 | 56.225 | 56.4359 | -66.8879 | -66.7336 | -0.00422 | -66.7773 | 56.2077 | 56.4084 | 56.2193 | -67.1477 | -0.13678 | -0.075973 | 0.022143 | -0.004062 | 0.13272 | -0.1532 | 0.05771 | -0.39657 | -0.17047 | 0.01745 | -0.026212 | 0.37036 | 0.03018 | -0.15892 | 123.0533 | 122.9761 | 123.187 | 66.7479 | -123.2661 | 122.9588 | 123.1595 | 122.9704 | 66.7469 | -123.5258
2262.7969 | 123.1705 | -66.7603 | 56.3416 | -0.0029761 | -0.028085 | -0.00039306 | 0.053295 | -0.0073736 | 0.062076 | -0.015108 | -0.0030529 | -0.00012813 | 0.056108 | 0.037139 | 0.056171 | -66.7335 | 0.010564 | -66.7552 | 56.3114 | 56.2387 | 56.4405 | -66.8925 | -66.7336 | -0.00422 | -66.7865 | 56.2123 | 56.4038 | 56.1826 | -67.1522 | -0.13221 | -0.030195 | 0.02672 | 0.005093 | 0.1373 | -0.10284 | 0.09891 | -0.39199 | -0.12927 | 0.026605 | -0.026215 | 0.36577 | 0.062222 | -0.15893 | 123.0716 | 122.999 | 123.2007 | 66.7708 | -123.234 | 122.9725 | 123.164 | 122.9429 | 66.756 | -123.4938
2263.7969 | 123.1476 | -66.7511 | 56.3232 | -0.0029761 | -0.027872 | -0.00017946 | 0.052867 | -0.0071598 | 0.061862 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055681 | 0.037566 | 0.056599 | -66.729 | -0.007751 | -66.7597 | 56.3068 | 56.2433 | 56.4359 | -66.8833 | -66.7382 | 0.000359 | -66.7819 | 56.2031 | 56.3992 | 56.2238 | -67.1431 | -0.1322 | -0.016463 | 0.022143 | -0.008641 | 0.12356 | -0.079953 | 0.11264 | -0.39199 | -0.12012 | 0.012872 | -0.030791 | 0.3612 | 0.075955 | -0.09941 | 123.0579 | 122.9944 | 123.187 | 66.7433 | -123.2065 | 122.9542 | 123.1503 | 122.9749 | 66.7515 | -123.4663
2264.8594 | 123.2117 | -66.7511 | 56.3141 | -0.0029761 | -0.027872 | -0.00017946 | 0.053081 | -0.0073736 | 0.061648 | -0.015108 | -0.0032665 | -0.00034193 | 0.055895 | 0.037352 | 0.056599 | -66.7244 | 0.001407 | -66.7552 | 56.3022 | 56.2296 | 56.4405 | -66.8925 | -66.7428 | -0.008798 | -66.7865 | 56.2169 | 56.4038 | 56.2284 | -67.1477 | -0.14136 | -0.011886 | 0.026722 | -0.004062 | 0.1373 | -0.084535 | 0.12638 | -0.39657 | -0.097228 | 0.008293 | -0.03537 | 0.3612 | 0.089688 | -0.085676 | 123.0533 | 122.9807 | 123.1916 | 66.7525 | -123.2065 | 122.968 | 123.1549 | 122.9795 | 66.7423 | -123.4618
2265.7969 | 123.2071 | -66.7648 | 56.3141 | -0.010607 | -0.027872 | -0.00017946 | 0.053081 | -0.0073736 | 0.062076 | 0.015414 | -0.0028393 | -0.00012813 | 0.055681 | 0.037139 | 0.056171 | -66.7335 | 0.001407 | -66.7597 | 56.3068 | 56.2158 | 56.4405 | -66.8879 | -66.7336 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.2193 | -67.1568 | -0.12305 | -0.007308 | 0.031298 | 0.005092 | 0.12814 | -0.098271 | 0.12638 | -0.39199 | -0.10181 | 0.031183 | -0.021637 | 0.37035 | 0.08511 | -0.094833 | 123.0716 | 122.9806 | 123.2053 | 66.7662 | -123.202 | 122.9771 | 123.164 | 122.9841 | 66.7606 | -123.4709
2266.7969 | 123.2208 | -66.7786 | 56.3278 | -0.0029761 | -0.027658 | -0.00017946 | 0.053295 | -0.0073736 | 0.061862 | -0.0074779 | -0.0030529 | -0.00034193 | 0.055895 | 0.037139 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3068 | 56.2296 | 56.4405 | -66.8925 | -66.7382 | 0.000359 | -66.7865 | 56.2077 | 56.3946 | 56.1872 | -67.1477 | -0.1139 | -0.021041 | 0.04503 | 0.018824 | 0.13272 | -0.098268 | 0.11264 | -0.3691 | -0.12012 | 0.040337 | -0.007905 | 0.3612 | 0.066798 | -0.14062 | 123.0853 | 123.0081 | 123.219 | 66.78 | -123.2203 | 122.9863 | 123.1732 | 122.9658 | 66.7789 | -123.4755
2267.8594 | 123.2025 | -66.7831 | 56.3004 | -0.0029761 | -0.027658 | -0.00060686 | 0.053081 | -0.0071598 | 0.062289 | -0.0074779 | -0.0030529 | -0.00034193 | 0.055895 | 0.037352 | 0.056171 | -66.7244 | -0.003172 | -66.7597 | 56.3114 | 56.2204 | 56.4359 | -66.8879 | -66.7428 | 0.000359 | -66.7819 | 56.2123 | 56.39 | 56.2147 | -67.1522 | -0.10474 | 0.011004 | 0.058765 | 0.023402 | 0.12814 | -0.079959 | 0.13553 | -0.3691 | -0.088073 | 0.040336 | 0.001252 | 0.37035 | 0.089685 | -0.085679 | 123.0945 | 123.0035 | 123.219 | 66.78 | -123.1882 | 122.9954 | 123.1732 | 122.9978 | 66.7835 | -123.4526
2268.7969 | 123.1796 | -66.7694 | 56.3232 | -0.0029761 | -0.028085 | 3.4136e-05 | 0.053081 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.037352 | 0.056385 | -66.7335 | 0.001407 | -66.7552 | 56.3068 | 56.225 | 56.4405 | -66.8833 | -66.7428 | -0.008798 | -66.7956 | 56.2077 | 56.3992 | 56.2147 | -67.1431 | -0.11389 | -0.016463 | 0.035875 | 0.014248 | 0.12814 | -0.098269 | 0.11722 | -0.37368 | -0.11554 | 0.026603 | -0.026217 | 0.34746 | 0.075955 | -0.10857 | 123.0762 | 122.9944 | 123.2099 | 66.7708 | -123.2065 | 122.9771 | 123.1686 | 122.9841 | 66.7606 | -123.4663
2269.8594 | 123.1796 | -66.7328 | 56.3507 | -0.0029761 | -0.028299 | 3.4136e-05 | 0.053081 | -0.0069462 | 0.061862 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055681 | 0.037139 | 0.056385 | -66.7244 | -0.003172 | -66.7506 | 56.3022 | 56.2479 | 56.4405 | -66.8925 | -66.7474 | -0.00422 | -66.7865 | 56.2169 | 56.39 | 56.2467 | -67.1522 | -0.15967 | -0.048507 | 0.008411 | -0.017795 | 0.14188 | -0.10284 | 0.089755 | -0.41946 | -0.13385 | -0.014597 | -0.053681 | 0.36577 | 0.039331 | -0.10398 | 123.035 | 122.9807 | 123.1733 | 66.7296 | -123.2432 | 122.9496 | 123.1228 | 122.9795 | 66.7286 | -123.503
2270.7969 | 123.2208 | -66.7511 | 56.2866 | -0.0029761 | -0.028299 | -0.00039306 | 0.053081 | -0.0075872 | 0.062076 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.037352 | 0.056599 | -66.729 | 0.001407 | -66.7506 | 56.3022 | 56.2341 | 56.4405 | -66.8787 | -66.7428 | -0.00422 | -66.7865 | 56.2077 | 56.3946 | 56.2009 | -67.1385 | -0.12763 | 0.01558 | 0.022143 | 0.000516 | 0.12814 | -0.05249 | 0.15384 | -0.38741 | -0.078919 | 0.008293 | -0.03537 | 0.35204 | 0.108 | -0.085682 | 123.0533 | 122.9852 | 123.1916 | 66.7525 | -123.1653 | 122.9588 | 123.1457 | 122.952 | 66.7469 | -123.4251
2271.7969 | 123.2941 | -66.7099 | 56.2912 | 0.0046549 | -0.028085 | -0.00017946 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056108 | 0.03778 | 0.056599 | -66.7335 | -0.003172 | -66.7643 | 56.3068 | 56.2387 | 56.4359 | -66.8925 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.39 | 56.2055 | -67.1431 | -0.18256 | 0.01558 | -0.023634 | -0.054418 | 0.12814 | -0.052489 | 0.14469 | -0.43319 | -0.078918 | -0.037485 | -0.076569 | 0.35662 | 0.09884 | -0.085681 | 123.0167 | 122.9486 | 123.1458 | 66.7067 | -123.1837 | 122.9222 | 123.0999 | 122.9154 | 66.7011 | -123.4343
2272.8594 | 123.1888 | -66.7465 | 56.3461 | 0.0046549 | -0.027872 | -0.00060686 | 0.052867 | -0.0073736 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.056108 | 0.037352 | 0.056599 | -66.7335 | -0.003172 | -66.7597 | 56.3159 | 56.2296 | 56.445 | -66.897 | -66.7428 | -0.008798 | -66.7865 | 56.2169 | 56.3992 | 56.233 | -67.1477 | -0.15052 | -0.030194 | 0.012987 | -0.013219 | 0.1373 | -0.11658 | 0.098911 | -0.40114 | -0.12927 | 0.003715 | -0.039948 | 0.3612 | 0.053067 | -0.11314 | 123.0625 | 122.9761 | 123.1916 | 66.7433 | -123.2432 | 122.9634 | 123.1457 | 122.9795 | 66.7377 | -123.4938
2273.7969 | 123.2162 | -66.7511 | 56.2958 | 0.0046549 | -0.028085 | -0.00017946 | 0.053081 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00012813 | 0.056108 | 0.03778 | 0.056599 | -66.729 | 0.001407 | -66.7506 | 56.3114 | 56.2433 | 56.4359 | -66.8833 | -66.7474 | -0.00422 | -66.791 | 56.2169 | 56.3946 | 56.2559 | -67.1385 | -0.1322 | 0.015582 | 0.022143 | 0.000516 | 0.13272 | -0.052487 | 0.14011 | -0.38741 | -0.078917 | 0.003714 | -0.039948 | 0.34746 | 0.098842 | -0.039893 | 123.0625 | 122.9944 | 123.187 | 66.7525 | -123.1791 | 122.968 | 123.1457 | 123.007 | 66.7469 | -123.4343
2274.7969 | 123.2391 | -66.7282 | 56.3232 | -0.0029761 | -0.028299 | 3.4136e-05 | 0.053508 | -0.0073736 | 0.062076 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055895 | 0.037352 | 0.056171 | -66.729 | 0.005985 | -66.746 | 56.3022 | 56.2433 | 56.445 | -66.8879 | -66.7428 | -0.013377 | -66.7819 | 56.2169 | 56.4038 | 56.2147 | -67.1614 | -0.15967 | -0.021041 | -0.000746 | -0.017795 | 0.14188 | -0.079953 | 0.1218 | -0.43319 | -0.10638 | -0.014596 | -0.05368 | 0.37951 | 0.080533 | -0.10857 | 123.0304 | 122.9715 | 123.1733 | 66.7342 | -123.2111 | 122.9451 | 123.132 | 122.9429 | 66.7148 | -123.4846
2275.8594 | 123.23 | -66.7282 | 56.3232 | -0.0029761 | -0.028299 | -0.00017946 | 0.053295 | -0.0071598 | 0.062076 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055895 | 0.037566 | 0.056385 | -66.7244 | -0.003172 | -66.7597 | 56.3114 | 56.225 | 56.4405 | -66.8925 | -66.7428 | -0.00422 | -66.7865 | 56.2123 | 56.4038 | 56.2147 | -67.1568 | -0.16425 | -0.011884 | 0.003833 | -0.03153 | 0.13272 | -0.098269 | 0.11722 | -0.42861 | -0.11096 | -0.014596 | -0.058259 | 0.37035 | 0.080533 | -0.10857 | 123.0396 | 122.9532 | 123.1687 | 66.725 | -123.2157 | 122.9405 | 123.132 | 122.9429 | 66.724 | -123.4801
2276.7969 | 123.2986 | -66.7191 | 56.2912 | -0.0029761 | -0.028513 | -0.00017946 | 0.053722 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.037566 | 0.056385 | -66.7335 | 0.001407 | -66.7597 | 56.3022 | 56.225 | 56.4405 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.3992 | 56.2238 | -67.1477 | -0.16883 | 0.011002 | -0.014479 | -0.040685 | 0.12814 | -0.066226 | 0.14926 | -0.42861 | -0.078918 | -0.032908 | -0.071992 | 0.35662 | 0.108 | -0.067367 | 123.0213 | 122.944 | 123.1595 | 66.7205 | -123.1791 | 122.9313 | 123.1183 | 122.9429 | 66.7148 | -123.4389
2277.7969 | 123.2849 | -66.7282 | 56.3049 | -0.010607 | -0.028513 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.037566 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3022 | 56.2341 | 56.4405 | -66.897 | -66.7474 | -0.008798 | -66.7956 | 56.2123 | 56.4038 | 56.2147 | -67.1431 | -0.16883 | -0.002731 | -0.005324 | -0.03153 | 0.1373 | -0.070801 | 0.13553 | -0.41488 | -0.092651 | -0.019175 | -0.067416 | 0.34746 | 0.098843 | -0.090257 | 123.0304 | 122.9623 | 123.1687 | 66.7342 | -123.202 | 122.9405 | 123.132 | 122.9429 | 66.7194 | -123.448
2278.7969 | 123.2529 | -66.7145 | 56.3278 | -0.0029761 | -0.028726 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055895 | 0.03778 | 0.056385 | -66.7381 | 0.001407 | -66.7552 | 56.2976 | 56.225 | 56.4313 | -66.8925 | -66.752 | 0.004938 | -66.791 | 56.2123 | 56.4084 | 56.2238 | -67.1477 | -0.17798 | -0.030197 | -0.023634 | -0.040683 | 0.1373 | -0.10285 | 0.10348 | -0.43319 | -0.11554 | -0.037485 | -0.076569 | 0.35662 | 0.080534 | -0.10399 | 123.0121 | 122.9395 | 123.1458 | 66.7159 | -123.2203 | 122.9268 | 123.1228 | 122.9383 | 66.7194 | -123.4755
2279.8594 | 123.2574 | -66.7282 | 56.3461 | -0.0029761 | -0.028513 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055681 | 0.037566 | 0.056171 | -66.7335 | 0.001407 | -66.7643 | 56.3068 | 56.2204 | 56.4359 | -66.8833 | -66.7428 | -0.013377 | -66.7865 | 56.2123 | 56.3946 | 56.2009 | -67.1477 | -0.15509 | -0.039351 | -0.005324 | -0.036108 | 0.11898 | -0.12573 | 0.089754 | -0.41946 | -0.13385 | -0.014596 | -0.058259 | 0.3612 | 0.048488 | -0.14519 | 123.035 | 122.9486 | 123.1641 | 66.7296 | -123.2294 | 122.9405 | 123.1228 | 122.9291 | 66.7148 | -123.4938
2280.7969 | 123.2712 | -66.7053 | 56.3278 | -0.010607 | -0.028299 | -0.00039306 | 0.053295 | -0.0078008 | 0.062289 | 0.0077831 | -0.0032665 | -0.00076913 | 0.055895 | 0.037566 | 0.056385 | -66.7335 | -0.003172 | -66.7643 | 56.3068 | 56.2524 | 56.4405 | -66.8879 | -66.752 | -0.013377 | -66.7865 | 56.2077 | 56.3946 | 56.233 | -67.1477 | -0.18256 | -0.021041 | -0.028212 | -0.058996 | 0.12356 | -0.075373 | 0.11264 | -0.44234 | -0.12012 | -0.046641 | -0.081147 | 0.3612 | 0.066798 | -0.09483 | 123.0121 | 122.9578 | 123.1458 | 66.7021 | -123.2157 | 122.913 | 123.0999 | 122.9383 | 66.6919 | -123.4755
2281.8594 | 123.2071 | -66.7648 | 56.3416 | -0.010607 | -0.028299 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055681 | 0.037566 | 0.056385 | -66.7244 | 0.001407 | -66.7689 | 56.3159 | 56.2204 | 56.4359 | -66.8879 | -66.752 | 0.000359 | -66.7819 | 56.2077 | 56.3946 | 56.2009 | -67.1522 | -0.12305 | -0.025617 | 0.040455 | -0.004064 | 0.11899 | -0.12116 | 0.094331 | -0.38741 | -0.13385 | 0.012869 | -0.017058 | 0.37035 | 0.053065 | -0.14061 | 123.0808 | 122.9852 | 123.2007 | 66.7662 | -123.2294 | 122.9725 | 123.1594 | 122.9658 | 66.7652 | -123.4938
2282.7969 | 123.2941 | -66.7419 | 56.3141 | -0.0029761 | -0.028513 | -0.00060686 | 0.053295 | -0.0071598 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055681 | 0.037566 | 0.056385 | -66.7244 | 0.005985 | -66.7689 | 56.3068 | 56.2296 | 56.4405 | -66.8833 | -66.7611 | -0.00422 | -66.791 | 56.2123 | 56.3946 | 56.2101 | -67.1477 | -0.14136 | -0.007308 | 0.017566 | -0.026953 | 0.11441 | -0.084535 | 0.12638 | -0.40572 | -0.10181 | -0.019178 | -0.049104 | 0.35662 | 0.080531 | -0.10399 | 123.0487 | 122.9715 | 123.1824 | 66.7479 | -123.1974 | 122.9542 | 123.1366 | 122.952 | 66.7377 | -123.4618
2283.8594 | 123.2895 | -66.6916 | 56.3324 | 0.0046549 | -0.028726 | -0.00039306 | 0.053081 | -0.0071598 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055681 | 0.03778 | 0.056385 | -66.7244 | 0.005985 | -66.7689 | 56.3114 | 56.2433 | 56.4496 | -66.8925 | -66.7474 | -0.008798 | -66.7956 | 56.2077 | 56.3992 | 56.2147 | -67.1522 | -0.20087 | -0.021039 | -0.032788 | -0.077307 | 0.12356 | -0.089108 | 0.11722 | -0.46066 | -0.1247 | -0.055796 | -0.10404 | 0.35662 | 0.0668 | -0.11772 | 123.0029 | 122.9349 | 123.1412 | 66.6976 | -123.2249 | 122.8993 | 123.0908 | 122.9063 | 66.6828 | -123.4846
2284.7969 | 123.1705 | -66.7236 | 56.3919 | 0.0046549 | -0.028299 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.037566 | 0.056812 | -66.729 | -0.003172 | -66.7689 | 56.3068 | 56.2296 | 56.4405 | -66.8879 | -66.7428 | -0.00422 | -66.7819 | 56.2123 | 56.3946 | 56.2193 | -67.1522 | -0.16425 | -0.085128 | -0.005323 | -0.045263 | 0.11899 | -0.16236 | 0.048556 | -0.42861 | -0.17963 | -0.019173 | -0.058257 | 0.37035 | 0.002711 | -0.17265 | 123.0304 | 122.9532 | 123.1641 | 66.7205 | -123.2798 | 122.9359 | 123.1183 | 122.9429 | 66.7194 | -123.5442
2285.7969 | 123.3078 | -66.6733 | 56.3095 | 0.0046549 | -0.028726 | -0.00039306 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055895 | 0.037566 | 0.056385 | -66.729 | -0.003172 | -66.7643 | 56.3068 | 56.2296 | 56.4405 | -66.897 | -66.752 | -0.00422 | -66.7819 | 56.2123 | 56.3946 | 56.2376 | -67.1477 | -0.22376 | -0.00273 | -0.055677 | -0.091039 | 0.13272 | -0.079957 | 0.13095 | -0.47439 | -0.097228 | -0.078684 | -0.10861 | 0.36578 | 0.085109 | -0.071941 | 122.9801 | 122.9028 | 123.1137 | 66.6701 | -123.2065 | 122.8856 | 123.0679 | 122.9108 | 66.6691 | -123.4572
2286.7969 | 123.2712 | -66.687 | 56.3141 | -0.0029761 | -0.028513 | 3.4136e-05 | 0.053081 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00076913 | 0.056108 | 0.037566 | 0.056171 | -66.7244 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.4359 | -66.8879 | -66.752 | -0.008798 | -66.791 | 56.2214 | 56.3992 | 56.233 | -67.1477 | -0.20087 | -0.007308 | -0.037365 | -0.077306 | 0.12356 | -0.075377 | 0.1218 | -0.46065 | -0.092649 | -0.064951 | -0.10404 | 0.35662 | 0.08511 | -0.081097 | 122.9938 | 122.9257 | 123.1229 | 66.6884 | -123.202 | 122.9084 | 123.0862 | 122.92 | 66.6782 | -123.4618
2287.7969 | 123.2254 | -66.7053 | 56.3828 | -0.0029761 | -0.028299 | -0.00017946 | 0.053081 | -0.0075872 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.03778 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3068 | 56.2433 | 56.4405 | -66.897 | -66.752 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.2605 | -67.1477 | -0.19172 | -0.075972 | -0.028212 | -0.054418 | 0.1373 | -0.13946 | 0.057712 | -0.44234 | -0.17047 | -0.046641 | -0.081147 | 0.3612 | 0.016446 | -0.12229 | 123.0121 | 122.9486 | 123.1458 | 66.7067 | -123.2798 | 122.9176 | 123.1045 | 122.9658 | 66.7011 | -123.5304
2288.7969 | 123.1934 | -66.7374 | 56.3782 | 0.0046549 | -0.028513 | -0.00060686 | 0.053508 | -0.0073736 | 0.062289 | 0.015414 | -0.0030529 | -0.00034193 | 0.055895 | 0.037993 | 0.056385 | -66.7335 | 0.001407 | -66.7552 | 56.3022 | 56.2524 | 56.4405 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2123 | 56.39 | 56.2055 | -67.1568 | -0.15052 | -0.075973 | 0.003832 | -0.017795 | 0.13272 | -0.12573 | 0.062289 | -0.41946 | -0.16589 | -0.010019 | -0.049103 | 0.37035 | 0.011865 | -0.17266 | 123.0396 | 122.9898 | 123.1778 | 66.7388 | -123.2661 | 122.9496 | 123.1274 | 122.9429 | 66.7331 | -123.535
2289.7969 | 123.2529 | -66.7282 | 56.337 | 0.0046549 | -0.028299 | -0.00017946 | 0.053722 | -0.0073736 | 0.061862 | -0.0074779 | -0.0030529 | -0.00076913 | 0.055895 | 0.037993 | 0.056599 | -66.729 | 0.005985 | -66.7552 | 56.3068 | 56.2341 | 56.4359 | -66.8925 | -66.7474 | -0.008798 | -66.7956 | 56.2123 | 56.3992 | 56.2605 | -67.1568 | -0.16425 | -0.030196 | -0.000746 | -0.026951 | 0.1373 | -0.10284 | 0.098909 | -0.42861 | -0.12469 | -0.019175 | -0.067416 | 0.3612 | 0.062222 | -0.076514 | 123.035 | 122.9623 | 123.1641 | 66.7342 | -123.2294 | 122.9405 | 123.1274 | 122.9887 | 66.7194 | -123.4938
2290.7969 | 123.2666 | -66.6962 | 56.3507 | 0.0046549 | -0.028513 | -0.00017946 | 0.053081 | -0.0075872 | 0.062503 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055681 | 0.03778 | 0.056599 | -66.7381 | -0.003172 | -66.7552 | 56.3068 | 56.2296 | 56.4405 | -66.8925 | -66.7474 | -0.00422 | -66.7819 | 56.2169 | 56.3992 | 56.2101 | -67.1477 | -0.19629 | -0.043929 | -0.041945 | -0.058994 | 0.1373 | -0.12116 | 0.089755 | -0.4515 | -0.13385 | -0.051218 | -0.085723 | 0.36578 | 0.048489 | -0.14061 | 123.0029 | 122.9257 | 123.1366 | 66.693 | -123.2432 | 122.913 | 123.0954 | 122.9063 | 66.6919 | -123.4984
2291.7969 | 123.2803 | -66.7007 | 56.3278 | 0.0046549 | -0.028726 | -0.00060686 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.03778 | 0.056385 | -66.7335 | -0.003172 | -66.7643 | 56.3022 | 56.2387 | 56.4313 | -66.8879 | -66.7474 | -0.008798 | -66.791 | 56.2169 | 56.3992 | 56.2238 | -67.1522 | -0.18714 | -0.025619 | -0.032789 | -0.063573 | 0.12356 | -0.08911 | 0.10348 | -0.4515 | -0.11096 | -0.04664 | -0.090302 | 0.3612 | 0.071377 | -0.10399 | 123.0029 | 122.9395 | 123.132 | 66.6976 | -123.2157 | 122.9176 | 123.0999 | 122.9246 | 66.6919 | -123.4801
2292.7969 | 123.1613 | -66.7282 | 56.3599 | -0.010607 | -0.02894 | -0.00039306 | 0.052867 | -0.0073736 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.03778 | 0.056385 | -66.729 | -0.003172 | -66.7643 | 56.3068 | 56.2433 | 56.445 | -66.897 | -66.7428 | -0.008798 | -66.7819 | 56.2123 | 56.39 | 56.2421 | -67.1477 | -0.16883 | -0.053084 | -0.000746 | -0.036108 | 0.13272 | -0.11657 | 0.085178 | -0.41946 | -0.14758 | -0.014596 | -0.05368 | 0.36578 | 0.030176 | -0.11772 | 123.035 | 122.9715 | 123.1733 | 66.725 | -123.2569 | 122.9405 | 123.1182 | 122.9704 | 66.7194 | -123.5075
2293.7969 | 123.4177 | -66.7007 | 56.3644 | 0.0046549 | -0.028726 | -0.00039306 | 0.054149 | -0.0073736 | 0.062503 | -0.0074779 | -0.0032665 | -0.00076913 | 0.055895 | 0.037566 | 0.055958 | -66.7244 | 0.001407 | -66.7597 | 56.2976 | 56.2387 | 56.4359 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2238 | -67.1477 | -0.18714 | -0.066818 | -0.023632 | -0.058995 | 0.12814 | -0.12573 | 0.071443 | -0.44692 | -0.15674 | -0.04664 | -0.085724 | 0.3612 | 0.034756 | -0.14061 | 122.9984 | 122.9395 | 123.1366 | 66.7022 | -123.2523 | 122.9084 | 123.0999 | 122.9246 | 66.6965 | -123.5121
2294.7969 | 123.1705 | -66.7557 | 56.3782 | 0.0046549 | -0.02894 | -0.00017946 | 0.053081 | -0.0071598 | 0.062076 | 0.0077831 | -0.0030529 | -0.00076913 | 0.055895 | 0.037566 | 0.056385 | -66.7335 | 0.010564 | -66.7597 | 56.3114 | 56.2387 | 56.4359 | -66.8879 | -66.7565 | -0.008798 | -66.7865 | 56.2031 | 56.4038 | 56.2055 | -67.1522 | -0.13221 | -0.066816 | 0.022142 | -0.004064 | 0.12814 | -0.13946 | 0.05771 | -0.39657 | -0.17505 | -0.000866 | -0.030793 | 0.36577 | 0.025601 | -0.17266 | 123.067 | 122.9944 | 123.1916 | 66.7662 | -123.2661 | 122.9588 | 123.1595 | 122.9612 | 66.7469 | -123.5304
2295.8594 | 123.2483 | -66.7328 | 56.3141 | -0.010607 | -0.028085 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00034193 | 0.055895 | 0.037566 | 0.056385 | -66.7335 | -0.003172 | -66.7597 | 56.3022 | 56.2387 | 56.445 | -66.8925 | -66.7474 | -0.008798 | -66.791 | 56.2123 | 56.3992 | 56.2421 | -67.1431 | -0.15967 | -0.011886 | -0.000746 | -0.026952 | 0.13272 | -0.075377 | 0.13095 | -0.4103 | -0.10181 | -0.014597 | -0.058259 | 0.35204 | 0.08511 | -0.07194 | 123.035 | 122.9715 | 123.1778 | 66.7296 | -123.2065 | 122.9451 | 123.132 | 122.9749 | 66.724 | -123.4572
2296.7969 | 123.2712 | -66.7511 | 56.3278 | -0.0029761 | -0.028085 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | -0.0074779 | -0.0030529 | -0.00076913 | 0.055681 | 0.037566 | 0.056599 | -66.729 | 0.001407 | -66.7552 | 56.3068 | 56.2296 | 56.4359 | -66.897 | -66.7428 | -0.008798 | -66.791 | 56.2123 | 56.3992 | 56.233 | -67.1477 | -0.14594 | -0.021041 | 0.022143 | -0.004062 | 0.14188 | -0.098268 | 0.10806 | -0.39657 | -0.11554 | 0.008293 | -0.039948 | 0.35662 | 0.071377 | -0.09483 | 123.0579 | 122.9807 | 123.187 | 66.7525 | -123.2249 | 122.9634 | 123.1503 | 122.9841 | 66.7423 | -123.4755
2297.7969 | 123.317 | -66.6916 | 56.337 | 0.0046549 | -0.028513 | -0.00017946 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.03778 | 0.056599 | -66.7335 | 0.001407 | -66.7552 | 56.2976 | 56.2524 | 56.4359 | -66.8879 | -66.752 | -0.00422 | -66.7865 | 56.1985 | 56.3992 | 56.2193 | -67.1568 | -0.19629 | -0.039352 | -0.041945 | -0.063572 | 0.13272 | -0.084528 | 0.098909 | -0.46523 | -0.13843 | -0.060374 | -0.09488 | 0.37035 | 0.062222 | -0.11772 | 122.9892 | 122.944 | 123.1275 | 66.693 | -123.2249 | 122.8901 | 123.0908 | 122.9108 | 66.6874 | -123.4938
2298.8594 | 123.1613 | -66.7557 | 56.3919 | -0.018238 | -0.028299 | -0.00039306 | 0.052867 | -0.0069462 | 0.062503 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055895 | 0.037993 | 0.056171 | -66.7244 | 0.001407 | -66.7643 | 56.3068 | 56.2433 | 56.445 | -66.9016 | -66.7474 | -0.008798 | -66.791 | 56.2123 | 56.4129 | 56.2376 | -67.1522 | -0.14594 | -0.085128 | 0.031299 | -0.008642 | 0.1373 | -0.14862 | 0.053134 | -0.39657 | -0.17963 | 0.008291 | -0.035371 | 0.3612 | 0.021025 | -0.15434 | 123.0625 | 122.999 | 123.2007 | 66.7571 | -123.2935 | 122.968 | 123.1686 | 122.9932 | 66.7469 | -123.5442
2299.7969 | 123.2941 | -66.6962 | 56.3232 | 0.0046549 | -0.028726 | -0.00082046 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.03778 | 0.056599 | -66.729 | 0.005985 | -66.7643 | 56.3068 | 56.2433 | 56.4359 | -66.897 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.3946 | 56.2284 | -67.1477 | -0.20087 | -0.016463 | -0.032789 | -0.068151 | 0.13272 | -0.079953 | 0.11264 | -0.4515 | -0.11096 | -0.051218 | -0.090302 | 0.3612 | 0.071376 | -0.094831 | 123.0029 | 122.9395 | 123.1321 | 66.7022 | -123.2203 | 122.9084 | 123.0908 | 122.9246 | 66.6874 | -123.4709
2300.8594 | 123.2071 | -66.7374 | 56.3507 | -0.0029761 | -0.028726 | -0.00017946 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.037993 | 0.056599 | -66.729 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.445 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.3946 | 56.233 | -67.1477 | -0.15052 | -0.043929 | 0.00841 | -0.026952 | 0.12356 | -0.112 | 0.094333 | -0.4103 | -0.13843 | -0.014597 | -0.053681 | 0.35662 | 0.04391 | -0.11772 | 123.0441 | 122.9761 | 123.1824 | 66.7388 | -123.2386 | 122.9496 | 123.132 | 122.9704 | 66.7331 | -123.4984
2301.7969 | 123.1338 | -66.7694 | 56.3004 | -0.0029761 | -0.02894 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055681 | 0.037566 | 0.056385 | -66.729 | 0.001407 | -66.7552 | 56.3068 | 56.2341 | 56.445 | -66.9016 | -66.752 | -0.008798 | -66.791 | 56.2077 | 56.4084 | 56.2147 | -67.1522 | -0.13221 | 0.006425 | 0.040453 | 0.014248 | 0.14646 | -0.066223 | 0.14469 | -0.38284 | -0.092652 | 0.017446 | -0.021638 | 0.3612 | 0.108 | -0.085679 | 123.0762 | 123.0035 | 123.2144 | 66.7708 | -123.202 | 122.9771 | 123.1778 | 122.9841 | 66.7606 | -123.4526
2302.8594 | 123.2803 | -66.687 | 56.3232 | 0.0046549 | -0.028513 | -0.00017946 | 0.053295 | -0.0071598 | 0.06293 | 0.015414 | -0.0036937 | -0.00055553 | 0.055895 | 0.03778 | 0.056599 | -66.7244 | 0.005985 | -66.7597 | 56.3159 | 56.2479 | 56.445 | -66.8879 | -66.7428 | -0.00422 | -66.7819 | 56.2123 | 56.3992 | 56.2101 | -67.1568 | -0.20087 | -0.007306 | -0.037365 | -0.072728 | 0.12814 | -0.075374 | 0.1218 | -0.46981 | -0.11096 | -0.055794 | -0.094878 | 0.37493 | 0.075955 | -0.11315 | 123.0029 | 122.9349 | 123.1321 | 66.693 | -123.2111 | 122.8993 | 123.0862 | 122.8971 | 66.6828 | -123.4801
2303.7969 | 123.2849 | -66.7282 | 56.3232 | 0.0046549 | -0.028726 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055895 | 0.037993 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3068 | 56.2296 | 56.445 | -66.8879 | -66.7474 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2101 | -67.1568 | -0.15967 | -0.016463 | -0.005324 | -0.03153 | 0.12814 | -0.09369 | 0.1218 | -0.42861 | -0.11554 | -0.019175 | -0.058259 | 0.37035 | 0.075955 | -0.11315 | 123.035 | 122.9578 | 123.1733 | 66.7342 | -123.2111 | 122.9359 | 123.1274 | 122.9383 | 66.724 | -123.4801
2304.7969 | 123.2071 | -66.7236 | 56.3644 | 0.0046549 | -0.028513 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.037993 | 0.056385 | -66.729 | 0.005985 | -66.7506 | 56.3114 | 56.2433 | 56.4496 | -66.8925 | -66.752 | -0.00422 | -66.7865 | 56.2169 | 56.3992 | 56.2376 | -67.1568 | -0.16883 | -0.053083 | -0.005323 | -0.02695 | 0.14188 | -0.12115 | 0.085179 | -0.43319 | -0.14758 | -0.02833 | -0.062836 | 0.37035 | 0.034756 | -0.12687 | 123.035 | 122.9669 | 123.1733 | 66.7296 | -123.2569 | 122.9405 | 123.1228 | 122.9612 | 66.7194 | -123.5213
2305.7969 | 123.1796 | -66.7465 | 56.3507 | -0.0029761 | -0.028726 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055681 | 0.037993 | 0.056171 | -66.729 | 0.001407 | -66.7689 | 56.3114 | 56.2204 | 56.445 | -66.8879 | -66.7565 | -0.00422 | -66.7819 | 56.2169 | 56.4038 | 56.2009 | -67.1522 | -0.14136 | -0.03935 | 0.017565 | -0.022375 | 0.11899 | -0.13031 | 0.094333 | -0.40572 | -0.13385 | -0.010021 | -0.035369 | 0.37035 | 0.053067 | -0.14977 | 123.0579 | 122.9669 | 123.1916 | 66.7479 | -123.2386 | 122.9634 | 123.1503 | 122.9475 | 66.7423 | -123.503
2306.8594 | 123.2254 | -66.7282 | 56.3324 | -0.0029761 | -0.028726 | -0.00060686 | 0.053508 | -0.0073736 | 0.062503 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055681 | 0.037993 | 0.055958 | -66.729 | 0.005985 | -66.7689 | 56.3068 | 56.2341 | 56.4405 | -66.9016 | -66.752 | -0.00422 | -66.7865 | 56.2123 | 56.3992 | 56.2284 | -67.1477 | -0.17341 | -0.025618 | -0.000746 | -0.040686 | 0.13272 | -0.098266 | 0.10807 | -0.41946 | -0.12012 | -0.023753 | -0.058259 | 0.3612 | 0.0668 | -0.10399 | 123.035 | 122.9623 | 123.1687 | 66.7342 | -123.234 | 122.9405 | 123.1274 | 122.9566 | 66.724 | -123.4801
2307.7969 | 123.1796 | -66.7557 | 56.3553 | 0.0046549 | -0.028726 | -0.00039306 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.03778 | 0.056385 | -66.7335 | 0.001407 | -66.7735 | 56.3068 | 56.2479 | 56.4496 | -66.8879 | -66.7565 | -0.00422 | -66.7865 | 56.2077 | 56.3992 | 56.2238 | -67.1431 | -0.13221 | -0.048507 | 0.022142 | -0.017798 | 0.11441 | -0.10742 | 0.094334 | -0.38741 | -0.14758 | -0.000866 | -0.030793 | 0.35662 | 0.043911 | -0.13145 | 123.0625 | 123.0035 | 123.2053 | 66.7571 | -123.2432 | 122.9634 | 123.1549 | 122.9795 | 66.7515 | -123.4984
2308.7969 | 123.1796 | -66.7465 | 56.337 | -0.010607 | -0.028726 | 3.4136e-05 | 0.053081 | -0.0071598 | 0.062289 | 0.00015261 | -0.0034801 | -0.00076913 | 0.056108 | 0.038421 | 0.056599 | -66.7381 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.4405 | -66.897 | -66.7565 | -0.008798 | -66.7865 | 56.2123 | 56.3992 | 56.2193 | -67.1568 | -0.15052 | -0.030196 | 0.008409 | -0.017797 | 0.13272 | -0.098265 | 0.10349 | -0.4103 | -0.12469 | -0.010021 | -0.039948 | 0.37035 | 0.062222 | -0.11772 | 123.0533 | 122.9852 | 123.187 | 66.7479 | -123.234 | 122.9588 | 123.1457 | 122.9658 | 66.7377 | -123.4938
2309.7969 | 123.2162 | -66.7694 | 56.3416 | -0.010607 | -0.028513 | -0.00060686 | 0.053508 | -0.0073736 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.056108 | 0.03778 | 0.056385 | -66.729 | 0.005985 | -66.7689 | 56.3159 | 56.2433 | 56.4405 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.39 | 56.2055 | -67.1431 | -0.11847 | -0.025617 | 0.040453 | 0.000513 | 0.11899 | -0.098264 | 0.09891 | -0.37368 | -0.12927 | 0.017446 | -0.021638 | 0.35204 | 0.048486 | -0.13603 | 123.0853 | 123.0127 | 123.2099 | 66.7754 | -123.2294 | 122.9817 | 123.1594 | 122.9749 | 66.7652 | -123.4846
2310.8594 | 123.1888 | -66.7648 | 56.3416 | -0.010607 | -0.028513 | 3.4136e-05 | 0.053081 | -0.0075872 | 0.062289 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056322 | 0.038207 | 0.056171 | -66.7381 | 0.001407 | -66.7735 | 56.3114 | 56.2433 | 56.4405 | -66.8879 | -66.752 | -0.00422 | -66.7865 | 56.2169 | 56.3992 | 56.2284 | -67.1431 | -0.12305 | -0.030195 | 0.02672 | -0.008642 | 0.11441 | -0.098264 | 0.09891 | -0.37825 | -0.12469 | 0.012869 | -0.021637 | 0.35662 | 0.057644 | -0.11314 | 123.0762 | 123.0081 | 123.2053 | 66.7662 | -123.2294 | 122.9817 | 123.164 | 122.9932 | 66.7606 | -123.4846
2311.7969 | 123.1476 | -66.7923 | 56.3416 | -0.0029761 | -0.028513 | -0.00039306 | 0.053295 | -0.0071598 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055681 | 0.037993 | 0.056385 | -66.729 | 0.010564 | -66.7597 | 56.3068 | 56.2433 | 56.445 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2077 | 56.3992 | 56.2284 | -67.1522 | -0.095585 | -0.034774 | 0.063341 | 0.032557 | 0.12814 | -0.098264 | 0.10349 | -0.35995 | -0.13385 | 0.040334 | 0.00125 | 0.3612 | 0.057644 | -0.11314 | 123.0991 | 123.0356 | 123.2373 | 66.8029 | -123.2294 | 123 | 123.1915 | 123.0207 | 66.7881 | -123.4938
2312.7969 | 123.175 | -66.7694 | 56.3553 | -0.010607 | -0.028513 | -0.00060686 | 0.052867 | -0.0075872 | 0.062289 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055895 | 0.037993 | 0.056599 | -66.729 | 0.005985 | -66.7643 | 56.3068 | 56.2387 | 56.445 | -66.8925 | -66.752 | -0.008798 | -66.7819 | 56.2214 | 56.3946 | 56.2605 | -67.1522 | -0.12305 | -0.048507 | 0.040453 | 0.005091 | 0.12814 | -0.11658 | 0.089755 | -0.38284 | -0.13385 | 0.017446 | -0.012481 | 0.37035 | 0.039332 | -0.094825 | 123.0762 | 123.0081 | 123.2144 | 66.7754 | -123.2477 | 122.9908 | 123.164 | 123.0299 | 66.7606 | -123.5075
2313.8594 | 123.2712 | -66.7374 | 56.3416 | -0.010607 | -0.02894 | -0.00060686 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.03778 | 0.056385 | -66.7381 | 0.001407 | -66.7689 | 56.3022 | 56.2387 | 56.4496 | -66.8925 | -66.752 | -0.008798 | -66.7773 | 56.2169 | 56.3946 | 56.2238 | -67.1477 | -0.1551 | -0.039352 | -0.000746 | -0.03153 | 0.12356 | -0.10284 | 0.10807 | -0.4103 | -0.12469 | -0.014597 | -0.039945 | 0.37036 | 0.053065 | -0.11772 | 123.0396 | 122.9761 | 123.187 | 66.7388 | -123.234 | 122.9542 | 123.132 | 122.9612 | 66.7286 | -123.4892
2314.7969 | 123.175 | -66.7557 | 56.3507 | 0.0046549 | -0.028726 | -0.00039306 | 0.053295 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055467 | 0.038634 | 0.056599 | -66.7244 | 0.005985 | -66.7597 | 56.3068 | 56.2341 | 56.4405 | -66.8879 | -66.752 | -0.013377 | -66.791 | 56.2077 | 56.3992 | 56.2193 | -67.1614 | -0.13221 | -0.043929 | 0.031299 | -0.004064 | 0.12814 | -0.11658 | 0.089755 | -0.40573 | -0.14301 | 0.003713 | -0.035371 | 0.37035 | 0.048489 | -0.13145 | 123.0625 | 122.9898 | 123.1961 | 66.7617 | -123.2386 | 122.9634 | 123.1549 | 122.9749 | 66.7423 | -123.5121
2315.7969 | 123.1613 | -66.7465 | 56.3416 | -0.010607 | -0.02894 | -0.00060686 | 0.053295 | -0.0073736 | 0.062717 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055467 | 0.03778 | 0.056599 | -66.7335 | 0.005985 | -66.7689 | 56.3022 | 56.2296 | 56.445 | -66.8925 | -66.752 | -0.008798 | -66.7865 | 56.2169 | 56.4038 | 56.2284 | -67.1522 | -0.14594 | -0.039352 | 0.012987 | -0.022375 | 0.12356 | -0.112 | 0.10349 | -0.40572 | -0.12469 | -0.005442 | -0.039948 | 0.36577 | 0.062222 | -0.11314 | 123.0487 | 122.9761 | 123.1916 | 66.7525 | -123.234 | 122.9634 | 123.1503 | 122.9749 | 66.7377 | -123.4938
2316.7969 | 123.1934 | -66.7603 | 56.337 | -0.0029761 | -0.02894 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.03778 | 0.056385 | -66.7335 | 0.005985 | -66.7689 | 56.2976 | 56.2387 | 56.4496 | -66.8925 | -66.752 | -0.00422 | -66.791 | 56.2169 | 56.4038 | 56.1918 | -67.1522 | -0.13221 | -0.039352 | 0.02672 | -0.008642 | 0.12356 | -0.098265 | 0.11265 | -0.39199 | -0.12012 | 0.008291 | -0.030793 | 0.3612 | 0.0668 | -0.14519 | 123.0579 | 122.999 | 123.2099 | 66.7662 | -123.2294 | 122.9771 | 123.164 | 122.952 | 66.756 | -123.4892
2317.8594 | 123.2071 | -66.7648 | 56.3095 | -0.018238 | -0.02894 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062717 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055467 | 0.037993 | 0.056599 | -66.729 | 0.001407 | -66.7735 | 56.3068 | 56.2296 | 56.4405 | -66.8925 | -66.7611 | -0.00422 | -66.7819 | 56.2214 | 56.3946 | 56.2009 | -67.1477 | -0.12763 | -0.00273 | 0.035876 | -0.008642 | 0.11899 | -0.079957 | 0.13095 | -0.38283 | -0.088071 | 0.003711 | -0.017058 | 0.36578 | 0.085109 | -0.10857 | 123.0716 | 122.9944 | 123.2053 | 66.7662 | -123.202 | 122.9863 | 123.1594 | 122.9658 | 66.7606 | -123.4572
2318.7969 | 123.1476 | -66.7465 | 56.3416 | -0.0029761 | -0.02894 | -0.00017946 | 0.052867 | -0.0078008 | 0.062503 | -0.015108 | -0.0034801 | -0.00076913 | 0.055895 | 0.038207 | 0.056599 | -66.729 | -0.003172 | -66.7643 | 56.3022 | 56.2296 | 56.445 | -66.897 | -66.752 | 0.004938 | -66.7819 | 56.2169 | 56.3992 | 56.2101 | -67.1568 | -0.15052 | -0.039352 | 0.017565 | -0.017797 | 0.13272 | -0.112 | 0.10349 | -0.4103 | -0.12469 | -0.005442 | -0.035369 | 0.37493 | 0.057644 | -0.13146 | 123.0487 | 122.9761 | 123.1916 | 66.7433 | -123.2386 | 122.9634 | 123.1457 | 122.9566 | 66.7515 | -123.4984
2319.7969 | 123.2162 | -66.7877 | 56.3278 | -0.0029761 | -0.028726 | -0.00082046 | 0.053081 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00034193 | 0.056108 | 0.03778 | 0.056385 | -66.7244 | 0.005985 | -66.7597 | 56.3022 | 56.225 | 56.4405 | -66.9016 | -66.7474 | -0.00422 | -66.7773 | 56.2123 | 56.3992 | 56.233 | -67.1477 | -0.1139 | -0.025619 | 0.063343 | 0.02798 | 0.14188 | -0.10285 | 0.11264 | -0.35995 | -0.11554 | 0.040335 | 0.010409 | 0.37036 | 0.071377 | -0.09483 | 123.0899 | 123.0127 | 123.2282 | 66.7937 | -123.2294 | 123 | 123.1869 | 123.0207 | 66.7835 | -123.4755
2320.8594 | 123.1888 | -66.774 | 56.3049 | -0.0029761 | -0.02894 | -0.00017946 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.038207 | 0.056171 | -66.7381 | 0.010564 | -66.7689 | 56.3068 | 56.2341 | 56.4405 | -66.897 | -66.752 | 0.000359 | -66.7865 | 56.2123 | 56.3992 | 56.233 | -67.1477 | -0.12305 | 0.001847 | 0.035875 | 0.005091 | 0.12814 | -0.070801 | 0.13553 | -0.37368 | -0.092651 | 0.022024 | -0.012482 | 0.3612 | 0.094265 | -0.071942 | 123.0808 | 123.0081 | 123.2144 | 66.7846 | -123.202 | 122.9863 | 123.1732 | 123.007 | 66.7743 | -123.4526
2321.7969 | 123.1476 | -66.7831 | 56.3278 | -0.0029761 | -0.02894 | -0.00039306 | 0.053081 | -0.0078008 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055895 | 0.038207 | 0.056599 | -66.7335 | 0.005985 | -66.7689 | 56.3159 | 56.2479 | 56.4405 | -66.9016 | -66.7565 | -0.00422 | -66.7865 | 56.2169 | 56.3992 | 56.2559 | -67.1568 | -0.11848 | -0.011884 | 0.049608 | 0.014246 | 0.13272 | -0.079952 | 0.11264 | -0.37368 | -0.11096 | 0.0266 | -0.003327 | 0.37035 | 0.071377 | -0.071937 | 123.0991 | 123.031 | 123.2236 | 66.7891 | -123.2294 | 123 | 123.1823 | 123.039 | 66.7789 | -123.4846
2322.8594 | 123.2803 | -66.7511 | 56.2866 | 0.0046549 | -0.02894 | -0.00039306 | 0.053081 | -0.0073736 | 0.062717 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055895 | 0.037993 | 0.056171 | -66.729 | 0.005985 | -66.7643 | 56.3068 | 56.2341 | 56.4405 | -66.9016 | -66.7474 | -0.008798 | -66.7865 | 56.2169 | 56.3992 | 56.2513 | -67.1522 | -0.15052 | 0.020158 | 0.022143 | -0.013219 | 0.1373 | -0.05249 | 0.15384 | -0.40114 | -0.069762 | 0.003714 | -0.03537 | 0.36577 | 0.11258 | -0.035317 | 123.0579 | 122.9852 | 123.1916 | 66.7571 | -123.1882 | 122.968 | 123.1503 | 123.0024 | 66.7423 | -123.4389
2323.7969 | 123.1659 | -66.7374 | 56.3461 | -0.010607 | -0.029154 | -0.00039306 | 0.053295 | -0.0080146 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.056108 | 0.038421 | 0.056385 | -66.7244 | 0.001407 | -66.7643 | 56.3068 | 56.2479 | 56.4405 | -66.8879 | -66.7657 | 0.000359 | -66.791 | 56.2123 | 56.4084 | 56.2421 | -67.1568 | -0.15052 | -0.039351 | 0.012989 | -0.026952 | 0.12356 | -0.098262 | 0.094333 | -0.41946 | -0.13385 | -0.028333 | -0.053681 | 0.36578 | 0.062224 | -0.10398 | 123.0441 | 122.9852 | 123.1778 | 66.7388 | -123.234 | 122.9496 | 123.1457 | 122.9795 | 66.7377 | -123.503
2324.7969 | 123.2437 | -66.7511 | 56.2866 | 0.0046549 | -0.028726 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | -0.0074779 | -0.0036937 | -0.00034193 | 0.056322 | 0.038207 | 0.056599 | -66.729 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.445 | -66.8833 | -66.752 | 0.000359 | -66.7865 | 56.2077 | 56.4038 | 56.2101 | -67.1477 | -0.1322 | 0.020158 | 0.022143 | -0.013219 | 0.11898 | -0.047911 | 0.15842 | -0.39657 | -0.078919 | -0.000864 | -0.03537 | 0.3612 | 0.11715 | -0.076524 | 123.0579 | 122.9898 | 123.1961 | 66.7525 | -123.1699 | 122.9588 | 123.1549 | 122.9612 | 66.7515 | -123.4343
2325.7969 | 123.2666 | -66.7328 | 56.2866 | -0.010607 | -0.028726 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055895 | 0.03778 | 0.056385 | -66.729 | -0.003172 | -66.7506 | 56.3114 | 56.2387 | 56.445 | -66.897 | -66.7611 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.2101 | -67.1568 | -0.16425 | 0.024737 | 0.003832 | -0.017795 | 0.14646 | -0.047911 | 0.15842 | -0.42404 | -0.069762 | -0.028333 | -0.058259 | 0.36578 | 0.11715 | -0.076524 | 123.0441 | 122.9715 | 123.1778 | 66.7296 | -123.1837 | 122.9496 | 123.1366 | 122.9429 | 66.7331 | -123.4434
2326.7969 | 123.23 | -66.7145 | 56.3004 | -0.010607 | -0.02894 | -0.00039306 | 0.053295 | -0.0071598 | 0.06293 | 0.00015261 | -0.0032665 | -0.00055553 | 0.056108 | 0.038207 | 0.056599 | -66.7244 | 0.005985 | -66.7552 | 56.3068 | 56.2387 | 56.445 | -66.8879 | -66.7474 | 0.000359 | -66.791 | 56.2169 | 56.3992 | 56.2055 | -67.1522 | -0.1734 | 0.006425 | -0.009899 | -0.040683 | 0.13272 | -0.061644 | 0.14469 | -0.43777 | -0.083495 | -0.032907 | -0.076569 | 0.3612 | 0.098843 | -0.094836 | 123.0213 | 122.9532 | 123.1595 | 66.7205 | -123.1882 | 122.9313 | 123.1137 | 122.92 | 66.7148 | -123.4526
2327.7969 | 123.2574 | -66.7191 | 56.2729 | -0.018238 | -0.02894 | -0.00039306 | 0.052654 | -0.0073736 | 0.062503 | 0.00015261 | -0.0036937 | -0.00012813 | 0.056322 | 0.038421 | 0.056385 | -66.7244 | 0.005985 | -66.7597 | 56.3068 | 56.2524 | 56.4405 | -66.897 | -66.752 | -0.00422 | -66.7865 | 56.2123 | 56.4084 | 56.2513 | -67.1568 | -0.17799 | 0.033891 | -0.005322 | -0.040685 | 0.1373 | -0.020441 | 0.16757 | -0.43777 | -0.060607 | -0.032908 | -0.067414 | 0.37035 | 0.13547 | -0.021584 | 123.0258 | 122.9715 | 123.1595 | 66.725 | -123.1699 | 122.9313 | 123.1274 | 122.9704 | 66.7148 | -123.4297
2328.7969 | 123.2254 | -66.7053 | 56.3232 | -0.018238 | -0.029154 | -0.00017946 | 0.053295 | -0.0071598 | 0.062289 | 0.015414 | -0.0032665 | -0.00055553 | 0.055681 | 0.038421 | 0.056385 | -66.7335 | 0.005985 | -66.7643 | 56.3068 | 56.2433 | 56.445 | -66.897 | -66.7565 | -0.00422 | -66.7819 | 56.2123 | 56.4038 | 56.2101 | -67.1477 | -0.19172 | -0.016463 | -0.028212 | -0.058996 | 0.13272 | -0.079953 | 0.1218 | -0.44234 | -0.11096 | -0.05122 | -0.076568 | 0.36578 | 0.080533 | -0.11315 | 123.0121 | 122.9486 | 123.1504 | 66.7113 | -123.2203 | 122.9176 | 123.1091 | 122.9154 | 66.7011 | -123.4709
2329.875 | 123.2483 | -66.7419 | 56.2958 | 0.012286 | -0.028726 | -0.00082046 | 0.053081 | -0.0078008 | 0.062289 | 0.0077831 | -0.0032665 | -0.00076913 | 0.056108 | 0.037993 | 0.056599 | -66.729 | 0.001407 | -66.7597 | 56.3068 | 56.2387 | 56.445 | -66.8879 | -66.7565 | -0.008798 | -66.7956 | 56.2214 | 56.4084 | 56.233 | -67.1522 | -0.14594 | 0.011003 | 0.012987 | -0.017797 | 0.12814 | -0.057066 | 0.14927 | -0.4103 | -0.074338 | -0.014599 | -0.053683 | 0.35662 | 0.11258 | -0.062786 | 123.0487 | 122.9807 | 123.187 | 66.7434 | -123.1837 | 122.9634 | 123.1503 | 122.9749 | 66.7331 | -123.448
2330.7969 | 123.2254 | -66.7191 | 56.3187 | -0.010607 | -0.029154 | -0.00039306 | 0.053295 | -0.0071598 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.056108 | 0.037993 | 0.056171 | -66.729 | 0.001407 | -66.7689 | 56.3068 | 56.2433 | 56.445 | -66.8925 | -66.7565 | 0.000359 | -66.791 | 56.2214 | 56.3992 | 56.2467 | -67.1522 | -0.17341 | -0.011886 | -0.009901 | -0.049841 | 0.12356 | -0.075376 | 0.12638 | -0.43319 | -0.097227 | -0.037487 | -0.071992 | 0.3612 | 0.080532 | -0.07194 | 123.0258 | 122.9623 | 123.1641 | 66.7205 | -123.2111 | 122.9405 | 123.1183 | 122.9658 | 66.7194 | -123.4709
2331.7969 | 123.2941 | -66.7053 | 56.3141 | 0.0046549 | -0.029154 | -0.00017946 | 0.053081 | -0.0073736 | 0.062717 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.038207 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3068 | 56.2341 | 56.4405 | -66.897 | -66.7474 | -0.008798 | -66.7773 | 56.2214 | 56.4038 | 56.233 | -67.1522 | -0.19172 | -0.007308 | -0.028212 | -0.054418 | 0.1373 | -0.079956 | 0.12638 | -0.44692 | -0.092649 | -0.042063 | -0.071989 | 0.37493 | 0.089688 | -0.081097 | 123.0121 | 122.9395 | 123.1458 | 66.7113 | -123.2111 | 122.9268 | 123.1091 | 122.9383 | 66.6965 | -123.4663
2332.8594 | 123.2895 | -66.7099 | 56.2958 | 0.0046549 | -0.029154 | -0.00017946 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055895 | 0.038421 | 0.056599 | -66.7335 | 0.001407 | -66.7735 | 56.3114 | 56.2524 | 56.4496 | -66.8787 | -66.7565 | 0.004938 | -66.791 | 56.2123 | 56.3946 | 56.2284 | -67.1568 | -0.16882 | 0.015582 | -0.023634 | -0.063574 | 0.10525 | -0.043329 | 0.15384 | -0.44692 | -0.083495 | -0.046642 | -0.081147 | 0.36578 | 0.098842 | -0.067365 | 123.0213 | 122.9623 | 123.1595 | 66.7113 | -123.1745 | 122.9222 | 123.1045 | 122.9383 | 66.7148 | -123.4526
2333.7969 | 123.2895 | -66.7099 | 56.2729 | -0.018238 | -0.029367 | -0.00060686 | 0.053295 | -0.0075872 | 0.062503 | 0.0077831 | -0.0030529 | -0.00098273 | 0.055895 | 0.037993 | 0.056171 | -66.7244 | 0.005985 | -66.7643 | 56.3114 | 56.2433 | 56.445 | -66.8925 | -66.7611 | 0.000359 | -66.791 | 56.2169 | 56.3992 | 56.2238 | -67.1522 | -0.18256 | 0.03847 | -0.014477 | -0.054418 | 0.12814 | -0.029599 | 0.17215 | -0.44234 | -0.056029 | -0.051221 | -0.081147 | 0.3612 | 0.12631 | -0.049056 | 123.0213 | 122.9532 | 123.1549 | 66.7159 | -123.1653 | 122.9268 | 123.1091 | 122.9337 | 66.7103 | -123.4251
2334.8594 | 123.1384 | -66.7511 | 56.337 | 0.0046549 | -0.029154 | -0.00039306 | 0.053295 | -0.0075872 | 0.062503 | -0.0074779 | -0.0034801 | -0.00034193 | 0.056322 | 0.037993 | 0.056385 | -66.729 | 0.001407 | -66.7643 | 56.3159 | 56.2387 | 56.4496 | -66.8879 | -66.7474 | 0.004938 | -66.7819 | 56.2169 | 56.4084 | 56.233 | -67.1522 | -0.13678 | -0.021039 | 0.022143 | -0.013219 | 0.12356 | -0.098265 | 0.11265 | -0.40114 | -0.12012 | 0.003714 | -0.030791 | 0.37035 | 0.071379 | -0.10399 | 123.067 | 122.9898 | 123.2007 | 66.7525 | -123.2249 | 122.968 | 123.1595 | 122.9841 | 66.756 | -123.4892
2335.7969 | 123.2529 | -66.7236 | 56.3232 | -0.0029761 | -0.028726 | -0.00039306 | 0.053295 | -0.0078008 | 0.062717 | 0.0077831 | -0.0032665 | -0.00076913 | 0.055895 | 0.038207 | 0.056599 | -66.729 | 0.010564 | -66.7781 | 56.3022 | 56.2387 | 56.4359 | -66.8879 | -66.7565 | -0.008798 | -66.7773 | 56.2123 | 56.4038 | 56.2284 | -67.1522 | -0.16425 | -0.021041 | -0.005323 | -0.05442 | 0.10983 | -0.084532 | 0.11264 | -0.42861 | -0.11096 | -0.032909 | -0.053678 | 0.37493 | 0.080533 | -0.094831 | 123.0258 | 122.9623 | 123.1595 | 66.7342 | -123.2111 | 122.9359 | 123.1274 | 122.952 | 66.7148 | -123.4755
2336.8594 | 123.2941 | -66.7282 | 56.2958 | 0.0046549 | -0.028726 | -0.00060686 | 0.053508 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.038207 | 0.056599 | -66.7335 | 0.005985 | -66.7781 | 56.3022 | 56.2479 | 56.445 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2077 | 56.4084 | 56.2193 | -67.1522 | -0.15967 | 0.006425 | -0.005324 | -0.049843 | 0.10983 | -0.047908 | 0.14927 | -0.42403 | -0.088074 | -0.023753 | -0.062837 | 0.3612 | 0.11258 | -0.076522 | 123.0304 | 122.9761 | 123.1733 | 66.7342 | -123.1837 | 122.9359 | 123.1366 | 122.9475 | 66.724 | -123.448
2337.7969 | 123.2483 | -66.7099 | 56.3004 | -0.010607 | -0.028726 | -0.00039306 | 0.053295 | -0.0075872 | 0.062289 | 0.0077831 | -0.0032665 | -0.00076913 | 0.055681 | 0.038421 | 0.056171 | -66.7381 | 0.005985 | -66.7689 | 56.3022 | 56.2387 | 56.4496 | -66.8787 | -66.752 | -0.008798 | -66.7956 | 56.2123 | 56.4084 | 56.2009 | -67.1477 | -0.16882 | 0.001847 | -0.028212 | -0.058996 | 0.10983 | -0.061644 | 0.14927 | -0.43777 | -0.088073 | -0.042063 | -0.085726 | 0.35204 | 0.108 | -0.099415 | 123.0121 | 122.9486 | 123.1595 | 66.7159 | -123.1791 | 122.9222 | 123.1183 | 122.9108 | 66.7011 | -123.448
2338.7969 | 123.3124 | -66.7007 | 56.3187 | 0.0046549 | -0.029154 | -0.00060686 | 0.053295 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055895 | 0.038207 | 0.056171 | -66.7335 | 0.001407 | -66.7689 | 56.3022 | 56.2479 | 56.4405 | -66.8925 | -66.7474 | -0.008798 | -66.7956 | 56.2169 | 56.4038 | 56.2055 | -67.1568 | -0.19172 | -0.016464 | -0.032789 | -0.068151 | 0.12356 | -0.070797 | 0.1218 | -0.45608 | -0.10181 | -0.04664 | -0.094881 | 0.3612 | 0.08511 | -0.11315 | 123.0029 | 122.9486 | 123.1412 | 66.7022 | -123.2111 | 122.9176 | 123.1045 | 122.9063 | 66.6919 | -123.4755
2339.8594 | 123.23 | -66.7282 | 56.3049 | -0.0029761 | -0.02894 | -0.00017946 | 0.053295 | -0.0073736 | 0.062289 | -0.0074779 | -0.0028393 | -0.00055553 | 0.055681 | 0.037993 | 0.056171 | -66.7335 | 0.001407 | -66.7506 | 56.3068 | 56.2296 | 56.445 | -66.8833 | -66.752 | 0.000359 | -66.7819 | 56.2169 | 56.4084 | 56.1964 | -67.1568 | -0.15509 | 0.001847 | -0.005324 | -0.022373 | 0.13272 | -0.07538 | 0.14011 | -0.42861 | -0.088073 | -0.023753 | -0.05368 | 0.37493 | 0.10342 | -0.10857 | 123.035 | 122.9578 | 123.1733 | 66.7296 | -123.1882 | 122.9451 | 123.1366 | 122.9246 | 66.7286 | -123.4618
2340.7969 | 123.175 | -66.7419 | 56.3782 | -0.0029761 | -0.029154 | -0.00039306 | 0.052867 | -0.0075872 | 0.062717 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055681 | 0.037993 | 0.056385 | -66.729 | 0.005985 | -66.7552 | 56.3068 | 56.2433 | 56.445 | -66.8925 | -66.752 | -0.00422 | -66.7819 | 56.2169 | 56.4038 | 56.233 | -67.1522 | -0.15052 | -0.071395 | 0.012987 | -0.013218 | 0.1373 | -0.13489 | 0.066867 | -0.4103 | -0.16132 | -0.01002 | -0.039947 | 0.37035 | 0.025601 | -0.14518 | 123.0487 | 122.9852 | 123.187 | 66.7479 | -123.2706 | 122.9588 | 123.1457 | 122.9749 | 66.7377 | -123.5304
2341.7969 | 123.2803 | -66.6962 | 56.3416 | 0.019917 | -0.028726 | -0.00039306 | 0.053722 | -0.0075872 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.038421 | 0.056385 | -66.7335 | 0.001407 | -66.7552 | 56.3114 | 56.2387 | 56.4496 | -66.8879 | -66.7428 | 0.000359 | -66.791 | 56.2123 | 56.4129 | 56.2193 | -67.1568 | -0.19172 | -0.030195 | -0.037367 | -0.058994 | 0.13272 | -0.10284 | 0.10807 | -0.46066 | -0.12927 | -0.046639 | -0.09488 | 0.36578 | 0.071379 | -0.1223 | 123.0075 | 122.9349 | 123.1458 | 66.6976 | -123.2294 | 122.9084 | 123.1091 | 122.9154 | 66.6965 | -123.4984
2342.8594 | 123.2758 | -66.7053 | 56.3004 | -0.0029761 | -0.02894 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055895 | 0.038207 | 0.055958 | -66.7335 | 0.001407 | -66.7552 | 56.3068 | 56.2387 | 56.4359 | -66.8879 | -66.7474 | -0.00422 | -66.7819 | 56.2123 | 56.4084 | 56.2193 | -67.1614 | -0.18256 | 0.006425 | -0.028212 | -0.049839 | 0.13272 | -0.061644 | 0.13553 | -0.45608 | -0.088073 | -0.042063 | -0.076568 | 0.37951 | 0.108 | -0.0811 | 123.0121 | 122.944 | 123.1412 | 66.7067 | -123.1882 | 122.9176 | 123.1137 | 122.9246 | 66.7011 | -123.4618
2343.7969 | 123.3078 | -66.6779 | 56.3141 | -0.010607 | -0.02894 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | 0.0077831 | -0.0032665 | -0.00055553 | 0.056108 | 0.038207 | 0.056171 | -66.7427 | 0.001407 | -66.7552 | 56.3114 | 56.2433 | 56.4496 | -66.8925 | -66.7428 | -0.008798 | -66.7819 | 56.2123 | 56.3992 | 56.2238 | -67.1568 | -0.2146 | -0.002729 | -0.064835 | -0.077305 | 0.1373 | -0.070798 | 0.13553 | -0.47897 | -0.10181 | -0.06495 | -0.10403 | 0.37493 | 0.08511 | -0.090255 | 122.9892 | 122.9211 | 123.1275 | 66.6793 | -123.2065 | 122.8901 | 123.0771 | 122.9017 | 66.6691 | -123.4709
2344.7969 | 123.1796 | -66.7191 | 56.337 | 0.0046549 | -0.02894 | 3.4136e-05 | 0.053081 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.038207 | 0.056385 | -66.7381 | -0.003172 | -66.7552 | 56.2976 | 56.2479 | 56.4359 | -66.8925 | -66.7474 | 0.000359 | -66.7819 | 56.2123 | 56.4038 | 56.2101 | -67.1477 | -0.17341 | -0.039352 | -0.019057 | -0.036106 | 0.1373 | -0.089107 | 0.098909 | -0.42861 | -0.12469 | -0.02833 | -0.062835 | 0.36578 | 0.0668 | -0.12688 | 123.0167 | 122.9669 | 123.1549 | 66.7159 | -123.2294 | 122.9313 | 123.1228 | 122.9292 | 66.7194 | -123.4846
2345.7969 | 123.2895 | -66.687 | 56.3232 | 0.0046549 | -0.029154 | -0.00017946 | 0.053295 | -0.0073736 | 0.062076 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055895 | 0.037993 | 0.056599 | -66.729 | 0.005985 | -66.7552 | 56.3068 | 56.2433 | 56.445 | -66.8879 | -66.7428 | -0.008798 | -66.791 | 56.2077 | 56.4038 | 56.2284 | -67.1522 | -0.20087 | -0.016463 | -0.041944 | -0.068149 | 0.13272 | -0.079953 | 0.1218 | -0.46523 | -0.11554 | -0.055794 | -0.10404 | 0.3612 | 0.080533 | -0.094831 | 122.9938 | 122.9303 | 123.1321 | 66.693 | -123.2111 | 122.8947 | 123.0908 | 122.9154 | 66.6782 | -123.4755
2346.7969 | 123.1888 | -66.7282 | 56.3507 | -0.0029761 | -0.02894 | -0.00060686 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.038421 | 0.056171 | -66.729 | 0.005985 | -66.7506 | 56.3068 | 56.2524 | 56.4542 | -66.897 | -66.752 | 0.000359 | -66.7956 | 56.2169 | 56.3946 | 56.233 | -67.1522 | -0.16883 | -0.043929 | -0.000746 | -0.022373 | 0.14646 | -0.098261 | 0.10349 | -0.42403 | -0.13385 | -0.023753 | -0.067416 | 0.35662 | 0.04391 | -0.11772 | 123.035 | 122.9807 | 123.1824 | 66.7342 | -123.2477 | 122.9451 | 123.1228 | 122.9612 | 66.7286 | -123.503
2347.8594 | 123.2346 | -66.7236 | 56.3095 | -0.010607 | -0.029367 | -0.00039306 | 0.053508 | -0.0071598 | 0.062503 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055895 | 0.038207 | 0.056385 | -66.7335 | 0.010564 | -66.7552 | 56.3068 | 56.2433 | 56.4542 | -66.8879 | -66.7428 | 0.000359 | -66.791 | 56.2123 | 56.4084 | 56.2193 | -67.1522 | -0.16425 | -0.00273 | -0.009901 | -0.031528 | 0.13272 | -0.06622 | 0.14469 | -0.42861 | -0.097228 | -0.019173 | -0.067414 | 0.3612 | 0.098845 | -0.090255 | 123.0304 | 122.9669 | 123.1778 | 66.7342 | -123.1974 | 122.9359 | 123.132 | 122.9429 | 66.724 | -123.4618
2348.7969 | 123.2208 | -66.7282 | 56.3599 | -0.0029761 | -0.02894 | -0.00017946 | 0.053081 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055895 | 0.038421 | 0.056385 | -66.729 | 0.005985 | -66.7643 | 56.3159 | 56.2433 | 56.4496 | -66.9016 | -66.7565 | -0.00422 | -66.7819 | 56.2077 | 56.3992 | 56.2513 | -67.1522 | -0.17341 | -0.043927 | -0.000746 | -0.036108 | 0.1373 | -0.11657 | 0.089757 | -0.42403 | -0.15216 | -0.028332 | -0.05368 | 0.37035 | 0.039334 | -0.10856 | 123.0441 | 122.9715 | 123.1778 | 66.7342 | -123.2615 | 122.9359 | 123.1274 | 122.9795 | 66.724 | -123.5121
2349.7969 | 123.175 | -66.7374 | 56.369 | -0.0029761 | -0.029154 | -0.00082046 | 0.053081 | -0.0073736 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.056108 | 0.037993 | 0.056171 | -66.729 | 0.001407 | -66.7689 | 56.3114 | 56.2341 | 56.4405 | -66.897 | -66.752 | -0.00422 | -66.791 | 56.2169 | 56.3992 | 56.2284 | -67.1477 | -0.15967 | -0.057661 | 0.00841 | -0.03153 | 0.12814 | -0.13489 | 0.071444 | -0.4103 | -0.15216 | -0.014597 | -0.053681 | 0.35662 | 0.030178 | -0.14061 | 123.0487 | 122.9715 | 123.1778 | 66.7388 | -123.2661 | 122.9542 | 123.1366 | 122.9658 | 66.7331 | -123.5167
2350.7969 | 123.1888 | -66.7419 | 56.3416 | 0.0046549 | -0.029154 | -0.00082046 | 0.053295 | -0.0075872 | 0.062503 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055681 | 0.038421 | 0.056385 | -66.7244 | 0.001407 | -66.7597 | 56.3114 | 56.2616 | 56.4496 | -66.897 | -66.7474 | -0.00422 | -66.7819 | 56.2169 | 56.3946 | 56.2284 | -67.1477 | -0.1551 | -0.030195 | 0.017566 | -0.017797 | 0.1373 | -0.079948 | 0.10807 | -0.40572 | -0.12469 | -0.005442 | -0.039947 | 0.36578 | 0.053065 | -0.11314 | 123.0533 | 123.0035 | 123.1916 | 66.7434 | -123.2386 | 122.9588 | 123.1366 | 122.9704 | 66.7377 | -123.4892
2351.7969 | 123.1842 | -66.7603 | 56.3461 | -0.010607 | -0.029154 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055681 | 0.038634 | 0.056385 | -66.7381 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.445 | -66.897 | -66.7474 | 0.000359 | -66.7865 | 56.2214 | 56.3992 | 56.233 | -67.1614 | -0.13679 | -0.039351 | 0.022142 | -0.004064 | 0.13272 | -0.10742 | 0.098911 | -0.40115 | -0.12469 | 0.012869 | -0.026215 | 0.37493 | 0.053067 | -0.11314 | 123.067 | 122.999 | 123.2053 | 66.7617 | -123.2432 | 122.9817 | 123.1595 | 122.9932 | 66.7606 | -123.5075
2352.8594 | 123.3307 | -66.687 | 56.3049 | 0.0046549 | -0.029367 | -0.00060686 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055895 | 0.037993 | 0.056171 | -66.729 | 0.001407 | -66.7643 | 56.3114 | 56.2524 | 56.445 | -66.8879 | -66.7565 | 0.004938 | -66.7956 | 56.2123 | 56.3946 | 56.2238 | -67.1522 | -0.20087 | 0.006426 | -0.041944 | -0.077306 | 0.12356 | -0.052485 | 0.14011 | -0.46523 | -0.092651 | -0.06953 | -0.10861 | 0.35662 | 0.089686 | -0.0811 | 122.9984 | 122.9395 | 123.1321 | 66.6884 | -123.1928 | 122.8993 | 123.0816 | 122.9108 | 66.6919 | -123.4572
2353.7969 | 123.1796 | -66.7511 | 56.3507 | 0.012286 | -0.029154 | -0.00039306 | 0.053081 | -0.0075872 | 0.062289 | 0.0077831 | -0.0032665 | -0.00098273 | 0.055681 | 0.038207 | 0.056385 | -66.729 | 0.010564 | -66.7552 | 56.3159 | 56.2479 | 56.4496 | -66.8879 | -66.7474 | -0.00422 | -66.7819 | 56.2077 | 56.3992 | 56.2376 | -67.1477 | -0.13678 | -0.034772 | 0.022143 | -0.004062 | 0.13272 | -0.10284 | 0.098912 | -0.39657 | -0.14301 | 0.003714 | -0.030791 | 0.36578 | 0.048489 | -0.11314 | 123.067 | 122.999 | 123.2007 | 66.7617 | -123.2386 | 122.9588 | 123.1503 | 122.9887 | 66.7469 | -123.4984
2354.7969 | 123.2071 | -66.7465 | 56.3416 | 0.0046549 | -0.029154 | -0.00060686 | 0.053295 | -0.0075872 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055895 | 0.038207 | 0.056171 | -66.729 | 0.010564 | -66.7597 | 56.3114 | 56.2341 | 56.4542 | -66.8879 | -66.752 | -0.00422 | -66.7773 | 56.2123 | 56.3946 | 56.2238 | -67.1477 | -0.14136 | -0.030195 | 0.017565 | -0.013219 | 0.12814 | -0.10742 | 0.11265 | -0.40114 | -0.12927 | -0.005442 | -0.03079 | 0.37036 | 0.053065 | -0.11772 | 123.0579 | 122.9807 | 123.2007 | 66.7571 | -123.2294 | 122.9588 | 123.1411 | 122.9704 | 66.7423 | -123.4892
2355.8594 | 123.143 | -66.7374 | 56.3461 | -0.0029761 | -0.028726 | -0.00017946 | 0.053081 | -0.0075872 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.038421 | 0.056385 | -66.7381 | 0.001407 | -66.7643 | 56.3068 | 56.2387 | 56.4496 | -66.8879 | -66.752 | 0.000359 | -66.7773 | 56.2123 | 56.4038 | 56.233 | -67.1614 | -0.15052 | -0.039351 | -0.000746 | -0.026952 | 0.12356 | -0.10742 | 0.10349 | -0.42404 | -0.13385 | -0.014597 | -0.039945 | 0.38409 | 0.057645 | -0.11314 | 123.0441 | 122.9761 | 123.187 | 66.7388 | -123.234 | 122.9496 | 123.1411 | 122.9704 | 66.7377 | -123.5075
2356.7969 | 123.2162 | -66.7648 | 56.3324 | 0.0046549 | -0.02894 | -0.00060686 | 0.052867 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.056108 | 0.038634 | 0.056385 | -66.7381 | 0.005985 | -66.7643 | 56.3159 | 56.2524 | 56.4496 | -66.8925 | -66.7474 | -0.00422 | -66.791 | 56.2123 | 56.3992 | 56.2055 | -67.1568 | -0.12763 | -0.016461 | 0.02672 | 0.000514 | 0.12814 | -0.07995 | 0.11722 | -0.39199 | -0.12012 | 0.017447 | -0.026215 | 0.36578 | 0.0668 | -0.12688 | 123.0808 | 123.0173 | 123.2145 | 66.7708 | -123.2249 | 122.9771 | 123.164 | 122.9703 | 66.7606 | -123.4892
2357.7969 | 123.1934 | -66.7557 | 56.3416 | -0.0029761 | -0.02894 | -0.00039306 | 0.053081 | -0.0075872 | 0.061862 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055895 | 0.038421 | 0.056599 | -66.7335 | 0.005985 | -66.7689 | 56.3159 | 56.2433 | 56.4496 | -66.9016 | -66.752 | 0.000359 | -66.7865 | 56.2169 | 56.3992 | 56.233 | -67.1522 | -0.14594 | -0.025617 | 0.022142 | -0.01322 | 0.13272 | -0.098264 | 0.10807 | -0.39657 | -0.12469 | 0.003713 | -0.030793 | 0.36577 | 0.057644 | -0.10856 | 123.0716 | 122.999 | 123.2053 | 66.7617 | -123.2432 | 122.9725 | 123.1549 | 122.9887 | 66.756 | -123.4938
2358.8594 | 123.1705 | -66.7282 | 56.3553 | 0.0046549 | -0.029367 | -0.00039306 | 0.053295 | -0.0078008 | 0.062076 | 0.0077831 | -0.0034801 | -0.00034193 | 0.056108 | 0.038207 | 0.056385 | -66.729 | 0.001407 | -66.7643 | 56.3114 | 56.2524 | 56.4496 | -66.897 | -66.7474 | -0.008798 | -66.7865 | 56.2123 | 56.3992 | 56.2376 | -67.1568 | -0.16883 | -0.043928 | -0.000746 | -0.036108 | 0.13272 | -0.10284 | 0.094334 | -0.42861 | -0.14301 | -0.019175 | -0.058259 | 0.37035 | 0.043911 | -0.11772 | 123.0396 | 122.9807 | 123.1778 | 66.7296 | -123.2523 | 122.9405 | 123.1274 | 122.9658 | 66.7194 | -123.5121
2359.7969 | 123.1842 | -66.7236 | 56.3553 | 0.0046549 | -0.029367 | -0.00039306 | 0.052867 | -0.0075872 | 0.062289 | 0.0077831 | -0.0032665 | -0.00076913 | 0.055895 | 0.038207 | 0.056171 | -66.729 | 0.010564 | -66.7552 | 56.3114 | 56.2433 | 56.4542 | -66.9016 | -66.7428 | -0.00422 | -66.7865 | 56.2169 | 56.4038 | 56.265 | -67.1568 | -0.17799 | -0.043928 | -0.005323 | -0.031528 | 0.14646 | -0.112 | 0.098912 | -0.43319 | -0.13843 | -0.019173 | -0.062836 | 0.37035 | 0.048489 | -0.090246 | 123.035 | 122.9669 | 123.1778 | 66.7342 | -123.2569 | 122.9405 | 123.1274 | 122.9887 | 66.7194 | -123.5121
2360.8594 | 123.2529 | -66.7099 | 56.3507 | 0.0046549 | -0.02894 | -0.00060686 | 0.053295 | -0.0073736 | 0.062076 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055895 | 0.038421 | 0.056385 | -66.729 | 0.005985 | -66.7643 | 56.3068 | 56.2433 | 56.445 | -66.8879 | -66.7428 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.2238 | -67.1568 | -0.17798 | -0.043929 | -0.019056 | -0.054418 | 0.12356 | -0.10742 | 0.094333 | -0.44692 | -0.13385 | -0.032906 | -0.081147 | 0.36578 | 0.053067 | -0.12688 | 123.0167 | 122.9532 | 123.1549 | 66.7159 | -123.2386 | 122.9268 | 123.1137 | 122.9337 | 66.7103 | -123.5075
2361.7969 | 123.2025 | -66.7694 | 56.3324 | -0.0029761 | -0.029581 | -0.00017946 | 0.053295 | -0.0075872 | 0.062717 | 0.00015261 | -0.0036937 | -0.00098273 | 0.055467 | 0.038634 | 0.056812 | -66.729 | -0.003172 | -66.7781 | 56.3159 | 56.257 | 56.4542 | -66.897 | -66.7474 | -0.00422 | -66.791 | 56.2169 | 56.4084 | 56.2147 | -67.1477 | -0.12763 | -0.016461 | 0.040453 | -0.008644 | 0.11899 | -0.075371 | 0.1218 | -0.37826 | -0.11554 | 0.022024 | -0.021638 | 0.35662 | 0.075957 | -0.11772 | 123.0853 | 123.0264 | 123.2236 | 66.7662 | -123.2294 | 122.9863 | 123.1778 | 122.9841 | 66.7652 | -123.4801
2362.7969 | 123.143 | -66.7557 | 56.3278 | -0.010607 | -0.029154 | -0.00060686 | 0.052867 | -0.0071598 | 0.062289 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055467 | 0.038421 | 0.056385 | -66.7244 | 0.005985 | -66.7506 | 56.3068 | 56.2433 | 56.4496 | -66.897 | -66.7428 | -0.00422 | -66.7865 | 56.2123 | 56.4084 | 56.2238 | -67.1431 | -0.14136 | -0.021041 | 0.031299 | 0.005093 | 0.14646 | -0.084531 | 0.1218 | -0.38741 | -0.11554 | 0.01287 | -0.030793 | 0.35662 | 0.080534 | -0.10399 | 123.0625 | 122.999 | 123.2053 | 66.7617 | -123.2249 | 122.968 | 123.164 | 122.9795 | 66.7515 | -123.4709
2363.7969 | 123.23 | -66.7419 | 56.3416 | -0.0029761 | -0.029367 | -0.00060686 | 0.052867 | -0.0073736 | 0.062076 | 0.0077831 | -0.0030529 | -0.00076913 | 0.055467 | 0.038634 | 0.056385 | -66.7335 | 0.005985 | -66.7643 | 56.3159 | 56.2387 | 56.4542 | -66.8879 | -66.752 | 0.000359 | -66.7865 | 56.2169 | 56.4038 | 56.2238 | -67.1568 | -0.14594 | -0.025617 | 0.008409 | -0.022375 | 0.12356 | -0.10284 | 0.11265 | -0.41488 | -0.12469 | -0.01002 | -0.044526 | 0.37035 | 0.062222 | -0.11772 | 123.0579 | 122.9807 | 123.1961 | 66.7479 | -123.2294 | 122.9588 | 123.1457 | 122.9658 | 66.7423 | -123.4984
2364.7969 | 123.1476 | -66.774 | 56.3141 | 0.0046549 | -0.029154 | -0.00039306 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056108 | 0.038634 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3159 | 56.2341 | 56.4405 | -66.8879 | -66.752 | -0.00422 | -66.8002 | 56.2123 | 56.3992 | 56.2101 | -67.1568 | -0.11389 | 0.001849 | 0.040453 | 0.014247 | 0.12814 | -0.079956 | 0.12638 | -0.38284 | -0.10181 | 0.022024 | -0.026218 | 0.35662 | 0.08511 | -0.10399 | 123.0899 | 123.0081 | 123.2144 | 66.78 | -123.202 | 122.9863 | 123.1732 | 122.9841 | 66.7698 | -123.4709
2365.8594 | 123.2208 | -66.7191 | 56.3507 | 0.0046549 | -0.029367 | -0.00082046 | 0.053081 | -0.0075872 | 0.062289 | -0.0074779 | -0.0036937 | -0.00076913 | 0.055681 | 0.038634 | 0.056385 | -66.7381 | 0.001407 | -66.7735 | 56.3159 | 56.2433 | 56.445 | -66.9016 | -66.7565 | -0.00422 | -66.7865 | 56.2123 | 56.4038 | 56.233 | -67.1568 | -0.18256 | -0.034772 | -0.019057 | -0.054419 | 0.12815 | -0.10742 | 0.094333 | -0.43777 | -0.13843 | -0.037487 | -0.067414 | 0.37035 | 0.053067 | -0.11772 | 123.035 | 122.9623 | 123.1641 | 66.7205 | -123.2523 | 122.9313 | 123.1228 | 122.952 | 66.7148 | -123.5075
2366.7969 | 123.1705 | -66.7511 | 56.3507 | -0.0029761 | -0.029367 | -0.00082046 | 0.053081 | -0.0075872 | 0.062717 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055895 | 0.038421 | 0.056385 | -66.729 | 0.010564 | -66.7689 | 56.3114 | 56.2341 | 56.4405 | -66.8879 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.4129 | 56.2376 | -67.1568 | -0.13678 | -0.03935 | 0.022143 | -0.017797 | 0.11899 | -0.11658 | 0.089755 | -0.40572 | -0.13843 | -0.000864 | -0.039948 | 0.36578 | 0.062224 | -0.11314 | 123.0625 | 122.9852 | 123.1916 | 66.7617 | -123.2386 | 122.9634 | 123.164 | 122.9887 | 66.7469 | -123.5075
2367.7969 | 123.1613 | -66.7648 | 56.3553 | -0.0029761 | -0.029367 | -0.00060686 | 0.053081 | -0.0075872 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.038207 | 0.055958 | -66.729 | 0.010564 | -66.7689 | 56.3114 | 56.2524 | 56.4496 | -66.8879 | -66.7565 | 0.000359 | -66.7865 | 56.2169 | 56.4084 | 56.233 | -67.1522 | -0.12305 | -0.043928 | 0.035876 | -0.004064 | 0.11899 | -0.10284 | 0.094334 | -0.38741 | -0.13843 | 0.00829 | -0.021637 | 0.36577 | 0.053068 | -0.1223 | 123.0762 | 123.0173 | 123.2145 | 66.7754 | -123.2432 | 122.9817 | 123.1732 | 122.9978 | 66.7652 | -123.5075
2368.8594 | 123.1384 | -66.7923 | 56.3278 | 0.0046549 | -0.029581 | -0.00039306 | 0.052654 | -0.0078008 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.039062 | 0.056599 | -66.7335 | 0.005985 | -66.7781 | 56.3114 | 56.2433 | 56.4496 | -66.8925 | -66.752 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.2238 | -67.1522 | -0.10016 | -0.016462 | 0.058763 | 0.014244 | 0.11441 | -0.084531 | 0.1218 | -0.35995 | -0.11096 | 0.040334 | 0.00125 | 0.3612 | 0.075955 | -0.10399 | 123.1037 | 123.0356 | 123.2419 | 66.7983 | -123.2203 | 123.0092 | 123.1961 | 123.0161 | 66.7927 | -123.4801
2369.7969 | 123.175 | -66.7648 | 56.337 | 0.0046549 | -0.029367 | -0.00039306 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0032665 | -0.00098273 | 0.055895 | 0.038207 | 0.056599 | -66.7244 | 0.010564 | -66.7781 | 56.3114 | 56.2433 | 56.4542 | -66.897 | -66.752 | 0.000359 | -66.7819 | 56.2077 | 56.3992 | 56.2559 | -67.1522 | -0.13221 | -0.025617 | 0.040455 | -0.013221 | 0.11899 | -0.093686 | 0.11722 | -0.38741 | -0.12927 | 0.012869 | -0.017058 | 0.37035 | 0.062222 | -0.081092 | 123.0762 | 123.0081 | 123.219 | 66.7754 | -123.234 | 122.9725 | 123.164 | 123.0207 | 66.7652 | -123.4892
2370.7969 | 123.2483 | -66.7419 | 56.3232 | 0.0046549 | -0.029367 | -0.00060686 | 0.052867 | -0.0071598 | 0.06293 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.038207 | 0.056171 | -66.729 | 0.015142 | -66.7689 | 56.3068 | 56.257 | 56.4542 | -66.9016 | -66.7565 | -0.00422 | -66.7865 | 56.2169 | 56.4084 | 56.2605 | -67.1568 | -0.15968 | -0.016463 | 0.012987 | -0.026953 | 0.13272 | -0.066216 | 0.13096 | -0.41488 | -0.10638 | -0.014599 | -0.044526 | 0.37035 | 0.085112 | -0.062781 | 123.0487 | 122.999 | 123.1961 | 66.7571 | -123.2249 | 122.9588 | 123.1503 | 123.0024 | 66.7377 | -123.4801
2371.7969 | 123.1842 | -66.774 | 56.3461 | 0.0046549 | -0.029367 | -0.00039306 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055467 | 0.038634 | 0.056385 | -66.7427 | 0.005985 | -66.7735 | 56.3114 | 56.257 | 56.4542 | -66.8879 | -66.752 | 0.000359 | -66.7819 | 56.2214 | 56.4038 | 56.233 | -67.1568 | -0.11389 | -0.034772 | 0.031296 | 0.000513 | 0.11441 | -0.089104 | 0.10807 | -0.38284 | -0.12469 | 0.022024 | -0.007903 | 0.37493 | 0.057645 | -0.11314 | 123.0853 | 123.031 | 123.2282 | 66.78 | -123.234 | 122.9954 | 123.1778 | 123.007 | 66.7743 | -123.503
2372.7969 | 123.1888 | -66.7877 | 56.3004 | -0.0029761 | -0.029581 | -0.00060686 | 0.052867 | -0.0075872 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055895 | 0.038421 | 0.056385 | -66.7198 | 0.005985 | -66.7735 | 56.3114 | 56.2296 | 56.4496 | -66.897 | -66.7565 | 0.000359 | -66.791 | 56.2169 | 56.3992 | 56.2009 | -67.1614 | -0.10932 | 0.011004 | 0.067921 | 0.014246 | 0.12357 | -0.070802 | 0.14927 | -0.37368 | -0.083495 | 0.031178 | -0.003327 | 0.37035 | 0.098843 | -0.099415 | 123.0991 | 123.0173 | 123.2373 | 66.7937 | -123.1974 | 123.0046 | 123.1869 | 122.9887 | 66.7881 | -123.4618
2373.7969 | 123.1979 | -66.7786 | 56.3049 | -0.0029761 | -0.029367 | -0.00060686 | 0.053295 | -0.0075872 | 0.062717 | -0.0074779 | -0.0030529 | -0.00076913 | 0.055681 | 0.038634 | 0.056599 | -66.729 | 0.005985 | -66.7643 | 56.3205 | 56.2387 | 56.4542 | -66.8879 | -66.7565 | -0.00422 | -66.7865 | 56.2123 | 56.4038 | 56.233 | -67.1568 | -0.10932 | 0.015582 | 0.049608 | 0.014246 | 0.12356 | -0.066222 | 0.14927 | -0.37826 | -0.092651 | 0.022022 | -0.007905 | 0.37035 | 0.098843 | -0.071942 | 123.0991 | 123.0173 | 123.2328 | 66.7845 | -123.1928 | 122.9908 | 123.1823 | 123.0116 | 66.7743 | -123.4618
2374.7969 | 123.3307 | -66.7328 | 56.3278 | -0.0029761 | -0.029367 | -0.00060686 | 0.053295 | -0.0075872 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055681 | 0.038634 | 0.056385 | -66.7381 | 0.001407 | -66.7689 | 56.3159 | 56.2479 | 56.445 | -66.8925 | -66.752 | -0.00422 | -66.7865 | 56.2077 | 56.4038 | 56.233 | -67.1568 | -0.15967 | -0.011884 | -0.005324 | -0.036108 | 0.12356 | -0.079952 | 0.11722 | -0.42404 | -0.12012 | -0.019175 | -0.053681 | 0.37035 | 0.075955 | -0.09483 | 123.0487 | 122.9807 | 123.1778 | 66.7342 | -123.2203 | 122.9405 | 123.1366 | 122.9658 | 66.7286 | -123.4846
2375.8594 | 123.2025 | -66.7465 | 56.3416 | 0.0046549 | -0.029581 | -0.00017946 | 0.052654 | -0.0078008 | 0.062503 | -0.015108 | -0.0032665 | -0.00076913 | 0.055895 | 0.038421 | 0.056171 | -66.7244 | 0.005985 | -66.7643 | 56.3114 | 56.2524 | 56.4588 | -66.897 | -66.7565 | 0.000359 | -66.7865 | 56.2169 | 56.4084 | 56.2513 | -67.1522 | -0.15052 | -0.030195 | 0.022144 | -0.017797 | 0.13272 | -0.089106 | 0.11722 | -0.40572 | -0.12469 | -0.010021 | -0.039948 | 0.36577 | 0.066801 | -0.090249 | 123.0579 | 122.999 | 123.2053 | 66.7525 | -123.2386 | 122.9634 | 123.1549 | 122.9978 | 66.7469 | -123.4938
2376.7969 | 123.2895 | -66.7191 | 56.2912 | 0.0046549 | -0.029581 | -0.00060686 | 0.053295 | -0.0078008 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.038848 | 0.056171 | -66.729 | 0.005985 | -66.7643 | 56.3159 | 56.2341 | 56.4496 | -66.8879 | -66.752 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.233 | -67.1477 | -0.16883 | 0.024737 | -0.009901 | -0.045263 | 0.12356 | -0.057068 | 0.15842 | -0.42861 | -0.07434 | -0.032908 | -0.071992 | 0.35662 | 0.11258 | -0.058209 | 123.035 | 122.9532 | 123.1687 | 66.725 | -123.1791 | 122.9359 | 123.1228 | 122.952 | 66.7194 | -123.4389
2377.7969 | 123.23 | -66.7786 | 56.337 | -0.010607 | -0.029367 | -0.00060686 | 0.052654 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055895 | 0.038848 | 0.056599 | -66.729 | 0.005985 | -66.7689 | 56.3068 | 56.2479 | 56.4496 | -66.897 | -66.752 | -0.00422 | -66.791 | 56.2123 | 56.4038 | 56.2193 | -67.1568 | -0.11848 | -0.030196 | 0.049608 | 0.009668 | 0.12814 | -0.089107 | 0.11265 | -0.37826 | -0.12469 | 0.026601 | -0.012483 | 0.36578 | 0.0668 | -0.11772 | 123.0853 | 123.0264 | 123.2282 | 66.7845 | -123.234 | 122.9908 | 123.1823 | 122.9978 | 66.7743 | -123.4938
2378.8594 | 123.2071 | -66.7694 | 56.369 | 0.0046549 | -0.029581 | -0.00060686 | 0.053295 | -0.0075872 | 0.062503 | 0.0077831 | -0.0036937 | -0.00076913 | 0.055895 | 0.038634 | 0.056385 | -66.729 | 0.001407 | -66.7643 | 56.3068 | 56.2433 | 56.4542 | -66.897 | -66.7565 | 0.000359 | -66.7819 | 56.2169 | 56.4084 | 56.2055 | -67.1477 | -0.12763 | -0.06224 | 0.040453 | 0.005091 | 0.13272 | -0.12573 | 0.085179 | -0.37826 | -0.15216 | 0.012867 | -0.012481 | 0.36578 | 0.039335 | -0.1635 | 123.0762 | 123.0127 | 123.2236 | 66.7708 | -123.2661 | 122.9863 | 123.1778 | 122.9749 | 66.7698 | -123.5167
2379.7969 | 123.1888 | -66.7603 | 56.3461 | -0.010607 | -0.029581 | -0.00039306 | 0.053295 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.055895 | 0.039062 | 0.056599 | -66.729 | 0.015142 | -66.7643 | 56.3114 | 56.257 | 56.4542 | -66.897 | -66.752 | 0.000359 | -66.7865 | 56.2123 | 56.4038 | 56.2284 | -67.1522 | -0.13679 | -0.034772 | 0.031298 | -0.004064 | 0.13272 | -0.089104 | 0.10807 | -0.39199 | -0.13385 | 0.008291 | -0.026215 | 0.36577 | 0.057645 | -0.11772 | 123.0716 | 123.0173 | 123.2145 | 66.7754 | -123.2432 | 122.9725 | 123.164 | 122.9887 | 66.7606 | -123.4984
2380.7969 | 123.2346 | -66.7236 | 56.3187 | 0.0046549 | -0.029367 | -0.00060686 | 0.053081 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.038848 | 0.056171 | -66.729 | 0.001407 | -66.7735 | 56.3114 | 56.2341 | 56.4405 | -66.897 | -66.7611 | -0.00422 | -66.7865 | 56.2169 | 56.4084 | 56.2376 | -67.1477 | -0.17341 | -0.007307 | -0.005323 | -0.049841 | 0.12357 | -0.084534 | 0.1218 | -0.42403 | -0.10181 | -0.037488 | -0.062836 | 0.3612 | 0.089689 | -0.081097 | 123.035 | 122.9578 | 123.1641 | 66.725 | -123.2157 | 122.9405 | 123.132 | 122.9612 | 66.7194 | -123.4663
2381.8594 | 123.2208 | -66.7557 | 56.3553 | 0.0046549 | -0.029581 | -0.00039306 | 0.053508 | -0.0078008 | 0.062717 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055681 | 0.038848 | 0.056385 | -66.7335 | 0.005985 | -66.7689 | 56.3068 | 56.257 | 56.4542 | -66.8925 | -66.7565 | -0.00422 | -66.7819 | 56.226 | 56.4038 | 56.2467 | -67.1568 | -0.13679 | -0.048507 | 0.022142 | -0.01322 | 0.12356 | -0.09826 | 0.098912 | -0.40115 | -0.12927 | -0.000866 | -0.026214 | 0.37493 | 0.048489 | -0.10856 | 123.0625 | 123.0127 | 123.2099 | 66.7617 | -123.2477 | 122.9817 | 123.1595 | 123.0024 | 66.7515 | -123.5121
2382.7969 | 123.2391 | -66.7236 | 56.337 | 0.0046549 | -0.029367 | -0.00082046 | 0.053722 | -0.0075872 | 0.062289 | 0.015414 | -0.0032665 | -0.00034193 | 0.055895 | 0.038634 | 0.056385 | -66.729 | 0.005985 | -66.7689 | 56.3022 | 56.2524 | 56.445 | -66.897 | -66.7474 | -0.00422 | -66.7819 | 56.2214 | 56.4038 | 56.2238 | -67.1568 | -0.17341 | -0.034774 | -0.005323 | -0.045263 | 0.12814 | -0.084528 | 0.10807 | -0.43319 | -0.11554 | -0.023752 | -0.058257 | 0.37493 | 0.0668 | -0.11314 | 123.0258 | 122.9761 | 123.1687 | 66.7296 | -123.234 | 122.9451 | 123.1274 | 122.9475 | 66.7194 | -123.4938
2383.7969 | 123.2986 | -66.7053 | 56.3278 | 0.0046549 | -0.029581 | -0.00082046 | 0.053081 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055467 | 0.038634 | 0.056171 | -66.7335 | 0.001407 | -66.7643 | 56.3068 | 56.2433 | 56.4542 | -66.897 | -66.7611 | -0.00422 | -66.791 | 56.2123 | 56.4038 | 56.2605 | -67.1522 | -0.19172 | -0.021041 | -0.028212 | -0.058996 | 0.13272 | -0.084531 | 0.12638 | -0.44692 | -0.11554 | -0.055799 | -0.085725 | 0.3612 | 0.075955 | -0.067359 | 123.0121 | 122.9486 | 123.1595 | 66.7067 | -123.2249 | 122.9176 | 123.1091 | 122.9658 | 66.7011 | -123.4801
2384.7969 | 123.2071 | -66.7282 | 56.3599 | -0.010607 | -0.029367 | -0.00017946 | 0.053295 | -0.0075872 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055895 | 0.039062 | 0.056599 | -66.7244 | 0.005985 | -66.7597 | 56.3022 | 56.2479 | 56.4496 | -66.8833 | -66.752 | 0.000359 | -66.7865 | 56.226 | 56.4084 | 56.2284 | -67.1477 | -0.15509 | -0.057662 | 0.003833 | -0.03153 | 0.12356 | -0.112 | 0.089757 | -0.41946 | -0.13385 | -0.023753 | -0.058259 | 0.3612 | 0.048491 | -0.13145 | 123.0304 | 122.9761 | 123.1778 | 66.7342 | -123.2432 | 122.9542 | 123.1366 | 122.9566 | 66.7286 | -123.5075
2385.7969 | 123.2666 | -66.7053 | 56.2912 | -0.0029761 | -0.029367 | -0.00039306 | 0.052867 | -0.0075872 | 0.062503 | -0.015108 | -0.0032665 | -0.00055553 | 0.055467 | 0.038634 | 0.056385 | -66.7335 | 0.001407 | -66.7597 | 56.3114 | 56.2433 | 56.4496 | -66.8925 | -66.752 | -0.008798 | -66.791 | 56.2123 | 56.4084 | 56.2238 | -67.1522 | -0.18714 | 0.020159 | -0.028212 | -0.054418 | 0.13272 | -0.04791 | 0.15842 | -0.44692 | -0.078918 | -0.046641 | -0.085725 | 0.3612 | 0.11716 | -0.067367 | 123.0167 | 122.9486 | 123.1549 | 66.7067 | -123.1837 | 122.9176 | 123.1137 | 122.9292 | 66.6965 | -123.4434
2386.8594 | 123.2849 | -66.7053 | 56.3095 | -0.010607 | -0.029581 | -0.00039306 | 0.052867 | -0.0075872 | 0.062717 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055895 | 0.038207 | 0.056385 | -66.7335 | 0.005985 | -66.7552 | 56.3159 | 56.2524 | 56.4496 | -66.8925 | -66.7565 | -0.00422 | -66.7865 | 56.2214 | 56.4129 | 56.2193 | -67.1522 | -0.18714 | 0.006427 | -0.028212 | -0.049839 | 0.1373 | -0.057062 | 0.14011 | -0.44692 | -0.088071 | -0.05122 | -0.081147 | 0.36577 | 0.10342 | -0.090255 | 123.0213 | 122.9578 | 123.1549 | 66.7113 | -123.202 | 122.9268 | 123.1183 | 122.9246 | 66.7011 | -123.4618
2387.7969 | 123.2437 | -66.7328 | 56.3187 | -0.0029761 | -0.029795 | -0.00060686 | 0.053508 | -0.0078008 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055681 | 0.038848 | 0.056171 | -66.7335 | 0.005985 | -66.7735 | 56.2976 | 56.2341 | 56.4496 | -66.8879 | -66.7565 | -0.013377 | -66.7956 | 56.2214 | 56.4084 | 56.2284 | -67.1614 | -0.15509 | -0.021042 | -0.000746 | -0.040686 | 0.11441 | -0.084534 | 0.13096 | -0.42861 | -0.097227 | -0.023754 | -0.062838 | 0.36578 | 0.089689 | -0.090254 | 123.0304 | 122.9669 | 123.1824 | 66.7388 | -123.2065 | 122.9542 | 123.1411 | 122.9612 | 66.7194 | -123.4801
2388.8594 | 123.2483 | -66.7374 | 56.3049 | -0.010607 | -0.029581 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055254 | 0.038848 | 0.056599 | -66.729 | 0.005985 | -66.7643 | 56.3159 | 56.2524 | 56.4588 | -66.8925 | -66.7565 | -0.00422 | -66.7865 | 56.2214 | 56.4038 | 56.2284 | -67.1614 | -0.1551 | 0.011004 | 0.00841 | -0.026952 | 0.12814 | -0.052485 | 0.15384 | -0.42404 | -0.083494 | -0.019176 | -0.049103 | 0.37493 | 0.098843 | -0.076521 | 123.0533 | 122.9898 | 123.1961 | 66.7434 | -123.1974 | 122.9588 | 123.1411 | 122.9658 | 66.7331 | -123.4663
2389.7969 | 123.2208 | -66.7374 | 56.3049 | -0.0029761 | -0.029581 | -0.00039306 | 0.053081 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.056322 | 0.038421 | 0.056385 | -66.729 | 0.010564 | -66.7643 | 56.3068 | 56.2387 | 56.4496 | -66.8879 | -66.752 | 0.004938 | -66.7865 | 56.2123 | 56.4129 | 56.233 | -67.1522 | -0.15052 | 0.001847 | 0.00841 | -0.026952 | 0.12356 | -0.066222 | 0.14469 | -0.41488 | -0.092651 | -0.014597 | -0.049103 | 0.36577 | 0.108 | -0.071942 | 123.0441 | 122.9761 | 123.187 | 66.7479 | -123.1928 | 122.9496 | 123.1503 | 122.9704 | 66.7423 | -123.4572
2390.7969 | 123.3124 | -66.6733 | 56.3278 | 0.0046549 | -0.029795 | -0.00039306 | 0.053081 | -0.0078008 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055681 | 0.038848 | 0.056171 | -66.7244 | -0.003172 | -66.7689 | 56.3068 | 56.2524 | 56.445 | -66.8833 | -66.7474 | 0.000359 | -66.7865 | 56.2169 | 56.4084 | 56.233 | -67.1522 | -0.21002 | -0.021041 | -0.051098 | -0.095617 | 0.11441 | -0.075373 | 0.11722 | -0.47897 | -0.11096 | -0.074106 | -0.11319 | 0.36577 | 0.080534 | -0.09483 | 122.9801 | 122.9257 | 123.1183 | 66.6701 | -123.2111 | 122.8901 | 123.0816 | 122.9063 | 66.6736 | -123.4801
2391.8594 | 123.2483 | -66.7374 | 56.3141 | 0.0046549 | -0.029795 | -0.00039306 | 0.053295 | -0.0078008 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055681 | 0.039062 | 0.056385 | -66.7381 | 0.010564 | -66.7597 | 56.3068 | 56.2479 | 56.445 | -66.897 | -66.7565 | 0.000359 | -66.7865 | 56.2169 | 56.4038 | 56.2147 | -67.1568 | -0.15967 | -0.007308 | -0.000746 | -0.022374 | 0.1373 | -0.066219 | 0.13095 | -0.41946 | -0.097228 | -0.019176 | -0.049103 | 0.37035 | 0.089688 | -0.099412 | 123.0441 | 122.9852 | 123.1824 | 66.7479 | -123.2111 | 122.9542 | 123.1411 | 122.952 | 66.7377 | -123.4709
2392.7969 | 123.2254 | -66.7648 | 56.3278 | 0.0046549 | -0.029795 | -0.00017946 | 0.053081 | -0.0078008 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.039062 | 0.056385 | -66.729 | 0.005985 | -66.7735 | 56.3159 | 56.2387 | 56.4542 | -66.8925 | -66.7611 | -0.00422 | -66.7819 | 56.2214 | 56.3992 | 56.2238 | -67.1522 | -0.12763 | -0.011884 | 0.035876 | -0.008642 | 0.11899 | -0.08911 | 0.12638 | -0.38741 | -0.10638 | 0.003711 | -0.017058 | 0.37035 | 0.071377 | -0.10399 | 123.0808 | 123.0035 | 123.219 | 66.7708 | -123.2203 | 122.9863 | 123.164 | 122.9887 | 66.7606 | -123.4801
2393.8594 | 123.2849 | -66.7145 | 56.2958 | -0.0029761 | -0.029581 | -0.00060686 | 0.053081 | -0.0073736 | 0.062289 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055467 | 0.038848 | 0.056385 | -66.7381 | 0.015142 | -66.7689 | 56.3114 | 56.257 | 56.4496 | -66.897 | -66.752 | -0.00422 | -66.7865 | 56.2214 | 56.4038 | 56.2147 | -67.1568 | -0.18256 | 0.015582 | -0.023634 | -0.054418 | 0.12814 | -0.03875 | 0.15384 | -0.44235 | -0.074338 | -0.037485 | -0.071991 | 0.37035 | 0.108 | -0.081101 | 123.0258 | 122.9715 | 123.1641 | 66.7296 | -123.1928 | 122.9359 | 123.1183 | 122.9292 | 66.7103 | -123.4526
2394.7969 | 123.2986 | -66.687 | 56.337 | -0.0029761 | -0.029367 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055467 | 0.039062 | 0.055958 | -66.729 | 0.005985 | -66.7552 | 56.3114 | 56.2387 | 56.4542 | -66.897 | -66.752 | 0.000359 | -66.791 | 56.2169 | 56.4129 | 56.2238 | -67.1614 | -0.21003 | -0.025617 | -0.041944 | -0.068149 | 0.14188 | -0.098265 | 0.11722 | -0.47439 | -0.12012 | -0.064951 | -0.10404 | 0.37035 | 0.075957 | -0.11314 | 122.9984 | 122.9257 | 123.1412 | 66.693 | -123.234 | 122.9039 | 123.0999 | 122.9108 | 66.6874 | -123.4984
2395.8594 | 123.1796 | -66.7557 | 56.3187 | 0.0046549 | -0.029795 | -0.00060686 | 0.053295 | -0.0078008 | 0.062503 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055681 | 0.038848 | 0.056171 | -66.729 | 0.001407 | -66.7689 | 56.3159 | 56.2387 | 56.4496 | -66.8879 | -66.7474 | 0.000359 | -66.7819 | 56.2123 | 56.4084 | 56.2238 | -67.1568 | -0.13221 | -0.002729 | 0.02672 | -0.01322 | 0.11899 | -0.079955 | 0.13096 | -0.40115 | -0.10638 | 0.008291 | -0.026214 | 0.37493 | 0.089689 | -0.094833 | 123.0716 | 122.9944 | 123.2053 | 66.7571 | -123.2065 | 122.968 | 123.164 | 122.9795 | 66.756 | -123.4755
2396.7969 | 123.2437 | -66.7099 | 56.3644 | 0.012286 | -0.029795 | 3.4136e-05 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.038848 | 0.056385 | -66.729 | 0.001407 | -66.7689 | 56.3159 | 56.2387 | 56.4542 | -66.897 | -66.752 | 0.000359 | -66.7865 | 56.2214 | 56.3992 | 56.2284 | -67.1568 | -0.18714 | -0.048505 | -0.019056 | -0.058996 | 0.12814 | -0.12573 | 0.089757 | -0.44692 | -0.143 | -0.042063 | -0.076569 | 0.37035 | 0.034756 | -0.13603 | 123.0258 | 122.9486 | 123.1641 | 66.7113 | -123.2615 | 122.9313 | 123.1091 | 122.9383 | 66.7103 | -123.5213
2397.7969 | 123.23 | -66.7419 | 56.3461 | -0.0029761 | -0.029581 | -0.00017946 | 0.053081 | -0.0073736 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055895 | 0.038848 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3159 | 56.2433 | 56.445 | -66.9016 | -66.752 | -0.00422 | -66.7819 | 56.2169 | 56.4038 | 56.2238 | -67.1568 | -0.15968 | -0.030194 | 0.008409 | -0.017797 | 0.14188 | -0.10284 | 0.098911 | -0.41488 | -0.12927 | -0.01002 | -0.039947 | 0.37493 | 0.057645 | -0.1223 | 123.0579 | 122.9852 | 123.187 | 66.7434 | -123.2477 | 122.9588 | 123.1457 | 122.9658 | 66.7377 | -123.503
2398.8594 | 123.262 | -66.7282 | 56.3095 | 0.0046549 | -0.029581 | -0.00039306 | 0.053295 | -0.0075872 | 0.062289 | -0.0074779 | -0.0032665 | -0.00034193 | 0.055895 | 0.038634 | 0.056171 | -66.729 | 0.005985 | -66.7643 | 56.3068 | 56.2433 | 56.4542 | -66.8879 | -66.752 | -0.00422 | -66.7865 | 56.2214 | 56.4038 | 56.2284 | -67.1568 | -0.15967 | -0.00273 | -0.000746 | -0.036108 | 0.12356 | -0.06622 | 0.14469 | -0.42861 | -0.088071 | -0.023753 | -0.058259 | 0.37035 | 0.094266 | -0.081098 | 123.035 | 122.9715 | 123.1824 | 66.7342 | -123.1974 | 122.9496 | 123.132 | 122.9566 | 66.724 | -123.4663
2399.7969 | 123.2758 | -66.7145 | 56.3187 | 0.012286 | -0.029581 | -0.00060686 | 0.053081 | -0.0078008 | 0.062503 | 0.0077831 | -0.0034801 | -0.00055553 | 0.056108 | 0.038848 | 0.056385 | -66.7381 | 0.001407 | -66.7552 | 56.3022 | 56.2479 | 56.4496 | -66.8925 | -66.7428 | -0.00422 | -66.7865 | 56.2169 | 56.4129 | 56.2193 | -67.1477 | -0.17798 | -0.016464 | -0.023634 | -0.040683 | 0.1373 | -0.070797 | 0.13096 | -0.43319 | -0.10181 | -0.028328 | -0.071991 | 0.3612 | 0.094267 | -0.099411 | 123.0167 | 122.9623 | 123.1641 | 66.7159 | -123.2111 | 122.9313 | 123.1274 | 122.9337 | 66.7103 | -123.4663
2400.7969 | 123.1842 | -66.7328 | 56.3644 | -0.0029761 | -0.029367 | 3.4136e-05 | 0.053081 | -0.0075872 | 0.062076 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.039062 | 0.056599 | -66.7335 | 0.001407 | -66.7597 | 56.3068 | 56.17 | 56.4221 | -66.8833 | -66.7382 | -0.00422 | -66.791 | 56.2214 | 56.4038 | 55.9491 | -67.1568 | -0.15051 | -0.057662 | -0.000746 | -0.026952 | 0.12356 | -0.19441 | 0.057707 | -0.42404 | -0.143 | -0.005439 | -0.058259 | 0.36578 | 0.039334 | -0.41533 | 123.0396 | 122.9028 | 123.1549 | 66.7342 | -123.2477 | 122.9542 | 123.1366 | 122.6819 | 66.7286 | -123.5213
2401.8594 | 123.175 | -66.7328 | 56.3644 | 0.0046549 | -0.029367 | -0.00039306 | 0.053295 | -0.0073736 | 0.061862 | -0.0074779 | -0.0028393 | -0.00012813 | 0.055895 | 0.038848 | 0.056171 | -66.7381 | 0.005985 | -66.7552 | 56.3068 | 56.0372 | 56.3489 | -66.7505 | -66.7336 | -0.008798 | -66.7865 | 56.2214 | 56.3992 | 55.9537 | -67.1568 | -0.017726 | -0.057662 | -0.005324 | -0.022373 | -0.004647 | -0.3272 | -0.015551 | -0.42404 | -0.143 | -0.000861 | -0.053681 | 0.37035 | 0.034756 | -0.41075 | 123.0396 | 122.77 | 123.0817 | 66.7388 | -123.115 | 122.9542 | 123.132 | 122.6865 | 66.724 | -123.5213
2402.7969 | 123.1705 | -66.7511 | 56.3141 | -0.0029761 | -0.029367 | -0.00060686 | 0.052867 | -0.0073736 | 0.061648 | -0.015108 | -0.0028393 | -0.00012813 | 0.055681 | 0.038421 | 0.055958 | -66.7335 | 0.001407 | -66.7506 | 56.3114 | 56.0372 | 56.358 | -66.7001 | -66.7245 | 0.004938 | -66.7773 | 56.2077 | 56.4038 | 55.9583 | -67.1522 | 0.050953 | -0.002729 | 0.017565 | 0.000516 | -0.050437 | -0.27685 | 0.043961 | -0.40114 | -0.10639 | 0.026608 | -0.026212 | 0.37493 | 0.089688 | -0.35581 | 123.0625 | 122.7883 | 123.1091 | 66.7525 | -123.0142 | 122.9588 | 123.1549 | 122.7094 | 66.756 | -123.4663
2403.7969 | 123.2071 | -66.7007 | 56.3507 | -0.0029761 | -0.029367 | -0.00039306 | 0.053081 | -0.0073736 | 0.061435 | 0.023044 | -0.0028393 | -0.00034193 | 0.055895 | 0.038848 | 0.055958 | -66.7335 | -0.007751 | -66.7552 | 56.3159 | 56.0693 | 56.3443 | -66.8696 | -66.7336 | -0.00422 | -66.7865 | 56.2169 | 56.4038 | 55.9629 | -67.1568 | -0.16882 | -0.034772 | -0.032789 | -0.054416 | 0.11441 | -0.28142 | -0.006396 | -0.45608 | -0.13385 | -0.032904 | -0.085724 | 0.37035 | 0.053067 | -0.38786 | 123.0167 | 122.77 | 123.0451 | 66.693 | -123.2203 | 122.9176 | 123.1045 | 122.6636 | 66.6965 | -123.5075
2404.7969 | 123.1613 | -66.7557 | 56.369 | -0.0029761 | -0.029154 | -0.00039306 | 0.053295 | -0.0071598 | 0.061648 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055895 | 0.038421 | 0.055958 | -66.7244 | 0.001407 | -66.7506 | 56.3114 | 56.0739 | 56.3672 | -66.8879 | -66.7382 | -0.008798 | -66.791 | 56.226 | 56.4084 | 55.9537 | -67.1614 | -0.13221 | -0.057661 | 0.031299 | 0.005093 | 0.1373 | -0.29515 | -0.001814 | -0.40573 | -0.143 | 0.017449 | -0.035371 | 0.37035 | 0.039335 | -0.41532 | 123.067 | 122.8295 | 123.1229 | 66.7571 | -123.2569 | 122.9817 | 123.164 | 122.7094 | 66.7469 | -123.5304
2405.7969 | 123.2071 | -66.7465 | 56.3782 | 0.0046549 | -0.029581 | -0.00082046 | 0.053295 | -0.0078008 | 0.062503 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055467 | 0.038848 | 0.056385 | -66.7335 | 0.001407 | -66.7552 | 56.3068 | 56.1471 | 56.4221 | -66.8879 | -66.7474 | 0.004938 | -66.7819 | 56.226 | 56.4084 | 55.9216 | -67.1477 | -0.14136 | -0.071395 | 0.012987 | -0.00864 | 0.13272 | -0.23104 | 0.043974 | -0.40114 | -0.15216 | -0.000864 | -0.035369 | 0.36578 | 0.03018 | -0.45653 | 123.0533 | 122.8937 | 123.1687 | 66.7479 | -123.2661 | 122.9725 | 123.1549 | 122.6682 | 66.7515 | -123.5258
2406.8594 | 123.2162 | -66.7419 | 56.3644 | 0.0046549 | -0.029795 | -0.00039306 | 0.053081 | -0.0078008 | 0.062717 | 0.015414 | -0.0036937 | -0.00076913 | 0.055681 | 0.038848 | 0.056599 | -66.7427 | 0.0243 | -66.8101 | 56.3709 | 56.3578 | 56.5046 | -66.9611 | -66.784 | 0.004938 | -66.7865 | 56.2169 | 56.4038 | 56.3017 | -67.166 | -0.2192 | 0.006436 | -0.000748 | -0.068158 | 0.15104 | -0.006679 | 0.14012 | -0.42404 | -0.14758 | -0.042071 | -0.044526 | 0.37951 | 0.039334 | -0.062772 | 123.1128 | 123.0997 | 123.2465 | 66.7662 | -123.3256 | 122.9588 | 123.1457 | 123.0436 | 66.7469 | -123.5304
2407.7969 | 123.1979 | -66.7557 | 56.3232 | -0.010607 | -0.029367 | -0.00060686 | 0.053508 | -0.0075872 | 0.062289 | -0.0074779 | -0.0030529 | -0.00034193 | 0.055681 | 0.039062 | 0.056171 | -66.7381 | 0.019721 | -66.7781 | 56.3434 | 56.344 | 56.4908 | -66.9474 | -66.7428 | 0.009516 | -66.791 | 56.226 | 56.4084 | 56.352 | -67.1614 | -0.19173 | 0.020164 | 0.017564 | -0.022377 | 0.16935 | 0.020783 | 0.16759 | -0.40573 | -0.097226 | 0.01287 | -0.035371 | 0.37035 | 0.085112 | 0.028791 | 123.0991 | 123.0997 | 123.2465 | 66.7754 | -123.2706 | 122.9817 | 123.164 | 123.1077 | 66.7652 | -123.4846
2408.7969 | 123.2071 | -66.7648 | 56.3278 | -0.018238 | -0.029367 | -0.00039306 | 0.053295 | -0.0078008 | 0.062076 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055681 | 0.038634 | 0.056171 | -66.7381 | 0.010564 | -66.7552 | 56.3297 | 56.3257 | 56.4679 | -66.9291 | -66.7291 | 0.000359 | -66.7865 | 56.2123 | 56.4129 | 56.3383 | -67.1522 | -0.16426 | 0.001851 | 0.02672 | 0.009671 | 0.17393 | -0.00211 | 0.14011 | -0.38741 | -0.11554 | 0.035762 | -0.021637 | 0.36577 | 0.085112 | 0.010477 | 123.0945 | 123.0905 | 123.2328 | 66.7754 | -123.2569 | 122.9771 | 123.1778 | 123.1031 | 66.7652 | -123.4801
2409.7969 | 123.1796 | -66.7648 | 56.3507 | -0.0029761 | -0.029367 | -0.00060686 | 0.053508 | -0.0073736 | 0.061862 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055467 | 0.038634 | 0.055958 | -66.7427 | 0.010564 | -66.7552 | 56.3159 | 56.2433 | 56.4588 | -66.9154 | -66.7336 | 0.000359 | -66.7865 | 56.2169 | 56.4084 | 56.3246 | -67.1568 | -0.15052 | -0.034772 | 0.022141 | 0.009671 | 0.1602 | -0.10742 | 0.10807 | -0.39199 | -0.13385 | 0.031183 | -0.021637 | 0.37035 | 0.057646 | -0.026146 | 123.0808 | 123.0081 | 123.2236 | 66.7754 | -123.2661 | 122.9817 | 123.1732 | 123.0894 | 66.7652 | -123.5075
2410.8594 | 123.0835 | -66.7374 | 56.3553 | -0.0029761 | -0.029367 | -0.00039306 | 0.052867 | -0.0071598 | 0.061648 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055467 | 0.038848 | 0.056171 | -66.7381 | 0.001407 | -66.7643 | 56.3251 | 56.2341 | 56.4542 | -66.81 | -66.7291 | -0.008798 | -66.791 | 56.2077 | 56.4084 | 56.0819 | -67.1568 | -0.072674 | -0.030193 | -0.000746 | -0.026952 | 0.045722 | -0.12116 | 0.098912 | -0.41946 | -0.14758 | 0.008296 | -0.053681 | 0.36578 | 0.053068 | -0.27339 | 123.0625 | 122.9715 | 123.1916 | 66.7388 | -123.1653 | 122.9451 | 123.1457 | 122.8193 | 66.7286 | -123.5121
2411.7969 | 123.1705 | -66.7694 | 56.3461 | 0.0046549 | -0.029581 | -0.00039306 | 0.053722 | -0.0071598 | 0.061648 | -0.0074779 | -0.0030529 | -0.00012813 | 0.055467 | 0.038848 | 0.056385 | -66.7198 | 0.005985 | -66.7552 | 56.3159 | 56.2387 | 56.4542 | -66.9016 | -66.7382 | 0.000359 | -66.791 | 56.2123 | 56.4038 | 56.2055 | -67.1568 | -0.13221 | -0.030194 | 0.04961 | 0.014248 | 0.14646 | -0.10742 | 0.10807 | -0.38741 | -0.13385 | 0.031182 | -0.021638 | 0.36578 | 0.057645 | -0.14061 | 123.0853 | 123.0081 | 123.2236 | 66.7754 | -123.2477 | 122.9817 | 123.1732 | 122.9749 | 66.7698 | -123.503
2412.7969 | 123.1979 | -66.7465 | 56.3187 | -0.0029761 | -0.029581 | -0.00060686 | 0.053508 | -0.0078008 | 0.062503 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055681 | 0.039062 | 0.056171 | -66.729 | 0.005985 | -66.7552 | 56.3114 | 56.2433 | 56.4542 | -66.9108 | -66.7428 | 0.000359 | -66.7865 | 56.226 | 56.4084 | 56.2101 | -67.1568 | -0.16426 | -0.007307 | 0.017565 | -0.00864 | 0.15562 | -0.075376 | 0.13553 | -0.4103 | -0.092649 | 0.003715 | -0.039948 | 0.37035 | 0.089689 | -0.10857 | 123.0579 | 122.9898 | 123.2007 | 66.7525 | -123.2294 | 122.9725 | 123.1549 | 122.9566 | 66.7469 | -123.4755
2413.8594 | 123.2849 | -66.7236 | 56.3095 | 0.0046549 | -0.030008 | -0.00039306 | 0.053508 | -0.0073736 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.039062 | 0.055958 | -66.7335 | 0.001407 | -66.7597 | 56.2976 | 56.2524 | 56.445 | -66.897 | -66.7565 | -0.00422 | -66.7956 | 56.2123 | 56.4084 | 56.2376 | -67.1477 | -0.17341 | -0.011886 | -0.009901 | -0.036107 | 0.1373 | -0.057062 | 0.13553 | -0.42403 | -0.097228 | -0.032909 | -0.071993 | 0.35204 | 0.098845 | -0.071941 | 123.0213 | 122.9761 | 123.1687 | 66.725 | -123.2065 | 122.9359 | 123.132 | 122.9612 | 66.7194 | -123.4572
2414.7969 | 123.1888 | -66.7511 | 56.3416 | -0.010607 | -0.029581 | -0.00060686 | 0.053081 | -0.0073736 | 0.061862 | 0.0077831 | -0.0030529 | -0.00055553 | 0.055681 | 0.039275 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3205 | 56.2524 | 56.4588 | -66.8925 | -66.7428 | 0.000359 | -66.7865 | 56.2123 | 56.4129 | 56.2101 | -67.1568 | -0.14136 | -0.021039 | 0.017565 | -0.008641 | 0.13272 | -0.089106 | 0.11722 | -0.40572 | -0.12927 | 0.008293 | -0.03537 | 0.37035 | 0.071379 | -0.13146 | 123.0716 | 123.0035 | 123.2099 | 66.7571 | -123.234 | 122.9634 | 123.164 | 122.9612 | 66.7515 | -123.4984
2415.7969 | 123.2117 | -66.7511 | 56.3187 | -0.0029761 | -0.029581 | -0.00039306 | 0.052867 | -0.0069462 | 0.061862 | 0.00015261 | -0.0030529 | -0.00012813 | 0.055467 | 0.038848 | 0.055958 | -66.729 | 0.001407 | -66.7643 | 56.3068 | 56.2296 | 56.4588 | -66.897 | -66.7336 | 0.000359 | -66.791 | 56.2169 | 56.4038 | 56.2147 | -67.1477 | -0.14594 | -0.011886 | 0.022143 | -0.013219 | 0.13272 | -0.089113 | 0.14011 | -0.39657 | -0.10181 | 0.01745 | -0.039948 | 0.35662 | 0.08511 | -0.10399 | 123.0579 | 122.9807 | 123.2099 | 66.7525 | -123.2157 | 122.968 | 123.1549 | 122.9658 | 66.7515 | -123.4663
2416.7969 | 123.1201 | -66.774 | 56.3187 | 0.0046549 | -0.030008 | -0.00060686 | 0.053081 | -0.0073736 | 0.062717 | -0.0074779 | -0.0036937 | -0.00076913 | 0.055895 | 0.039062 | 0.056385 | -66.7335 | 0.0243 | -66.8055 | 56.38 | 56.2387 | 56.4771 | -66.9016 | -66.7749 | 0.009516 | -66.791 | 56.2214 | 56.4038 | 56.1964 | -67.1614 | -0.12763 | 0.061369 | 0.040453 | -0.031535 | 0.096097 | -0.079955 | 0.15843 | -0.38741 | -0.097227 | -0.00087 | -0.01706 | 0.37035 | 0.08511 | -0.1223 | 123.154 | 123.0127 | 123.2511 | 66.7983 | -123.2203 | 122.9954 | 123.1778 | 122.9703 | 66.7835 | -123.4801
2417.7969 | 123.1979 | -66.7374 | 56.3278 | -0.0029761 | -0.029581 | -0.00060686 | 0.053295 | -0.0075872 | 0.062289 | 0.0077831 | -0.0030529 | -0.00034193 | 0.056108 | 0.038848 | 0.056385 | -66.7244 | 0.019721 | -66.8009 | 56.3663 | 56.3761 | 56.5137 | -66.9337 | -66.7657 | 0.009516 | -66.7865 | 56.2123 | 56.4038 | 56.0911 | -67.166 | -0.19631 | 0.038478 | 0.012989 | -0.063578 | 0.13273 | 0.048258 | 0.1859 | -0.42862 | -0.11554 | -0.028333 | -0.049103 | 0.37951 | 0.075955 | -0.23677 | 123.1037 | 123.1134 | 123.2511 | 66.7571 | -123.2615 | 122.9496 | 123.1411 | 122.8284 | 66.7469 | -123.4938
2418.8594 | 123.2758 | -66.7099 | 56.3416 | 0.0046549 | -0.029795 | -0.00039306 | 0.053508 | -0.0073736 | 0.062289 | 0.023044 | -0.0032665 | -0.00034193 | 0.055467 | 0.039275 | 0.056171 | -66.7335 | 0.015142 | -66.7918 | 56.3571 | 56.3303 | 56.5 | -66.8741 | -66.752 | 0.004938 | -66.7819 | 56.2214 | 56.4084 | 56.059 | -67.1614 | -0.16424 | 0.015589 | -0.023634 | -0.081888 | 0.082357 | -0.011264 | 0.15843 | -0.4515 | -0.12011 | -0.042063 | -0.07199 | 0.37951 | 0.066801 | -0.28255 | 123.067 | 123.0402 | 123.2099 | 66.725 | -123.2157 | 122.9313 | 123.1183 | 122.7689 | 66.7148 | -123.503
2419.7969 | 123.2254 | -66.7374 | 56.3599 | -0.0029761 | -0.029367 | -0.00039306 | 0.052654 | -0.0073736 | 0.061862 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055467 | 0.039062 | 0.056385 | -66.7335 | 0.010564 | -66.7781 | 56.348 | 56.3074 | 56.4908 | -66.9108 | -66.7474 | 0.009516 | -66.7956 | 56.2123 | 56.4038 | 56.0544 | -67.1614 | -0.17341 | -0.011878 | 0.003832 | -0.040687 | 0.13272 | -0.052469 | 0.13096 | -0.42404 | -0.14758 | -0.010019 | -0.05826 | 0.36578 | 0.043912 | -0.30544 | 123.0854 | 123.0448 | 123.2282 | 66.7479 | -123.2706 | 122.9496 | 123.1411 | 122.7918 | 66.7469 | -123.5213
2420.7969 | 123.1522 | -66.7969 | 56.337 | 0.0046549 | -0.029367 | -0.00060686 | 0.052867 | -0.0073736 | 0.061862 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055895 | 0.038848 | 0.056171 | -66.7244 | 0.019721 | -66.7735 | 56.348 | 56.2341 | 56.4817 | -66.8879 | -66.7428 | 0.004938 | -66.7865 | 56.2214 | 56.3992 | 55.9171 | -67.1568 | -0.091007 | 0.01101 | 0.072498 | 0.023401 | 0.11441 | -0.10284 | 0.14469 | -0.35995 | -0.11554 | 0.054069 | 0.010406 | 0.37035 | 0.062222 | -0.41991 | 123.1449 | 123.031 | 123.2785 | 66.8166 | -123.2249 | 123.0183 | 123.1961 | 122.7139 | 66.8018 | -123.4938
2421.8594 | 123.2849 | -66.7099 | 56.369 | -0.0029761 | -0.029795 | -0.00060686 | 0.052867 | -0.0073736 | 0.062076 | -0.0074779 | -0.0026255 | -0.00034193 | 0.055895 | 0.038848 | 0.055744 | -66.729 | 0.010564 | -66.7689 | 56.348 | 56.3028 | 56.4817 | -66.897 | -66.7336 | 0.000359 | -66.7865 | 56.2169 | 56.4038 | 55.9674 | -67.166 | -0.18714 | -0.021034 | -0.019056 | -0.058996 | 0.12814 | -0.066204 | 0.11265 | -0.45608 | -0.15216 | -0.023749 | -0.076569 | 0.37951 | 0.034756 | -0.40159 | 123.0579 | 123.0127 | 123.1916 | 66.7205 | -123.2661 | 122.9268 | 123.1137 | 122.6773 | 66.7103 | -123.535
2422.7969 | 123.2666 | -66.7603 | 56.3004 | -0.0029761 | -0.02894 | -0.00017946 | 0.053081 | -0.0073736 | 0.061862 | 0.00015261 | -0.0028393 | -0.00055553 | 0.055467 | 0.038848 | 0.055958 | -66.729 | 0.005985 | -66.7643 | 56.3388 | 56.3303 | 56.4771 | -66.9108 | -66.7336 | 0.004938 | -66.7865 | 56.2214 | 56.4038 | 56.0178 | -67.1568 | -0.15052 | 0.038474 | 0.031298 | -0.004064 | 0.14646 | 0.029935 | 0.17674 | -0.39657 | -0.078916 | 0.026605 | -0.026215 | 0.37035 | 0.10342 | -0.28256 | 123.0991 | 123.0905 | 123.2373 | 66.7662 | -123.2111 | 122.9817 | 123.164 | 122.778 | 66.7652 | -123.4572
2423.7969 | 123.1888 | -66.7877 | 56.3324 | -0.010607 | -0.029581 | -0.00039306 | 0.053081 | -0.0073736 | 0.062076 | 0.00015261 | -0.0026255 | -0.00055553 | 0.055681 | 0.039062 | 0.056385 | -66.7427 | 0.019721 | -66.7597 | 56.3342 | 56.3074 | 56.4679 | -66.9154 | -66.7291 | -0.00422 | -66.7819 | 56.2169 | 56.4038 | 56.0773 | -67.1522 | -0.12764 | 0.001853 | 0.045029 | 0.02798 | 0.15562 | -0.025003 | 0.13554 | -0.36452 | -0.11554 | 0.05865 | 0.00583 | 0.37035 | 0.071378 | -0.25508 | 123.122 | 123.0951 | 123.2557 | 66.8074 | -123.2478 | 123.0046 | 123.1915 | 122.865 | 66.7835 | -123.4846
2424.7969 | 123.3078 | -66.7374 | 56.2775 | -0.0029761 | -0.029367 | -0.00017946 | 0.053295 | -0.0071598 | 0.061862 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055681 | 0.039062 | 0.055744 | -66.729 | 0.010564 | -66.7643 | 56.3251 | 56.2662 | 56.4771 | -66.8925 | -66.7291 | 0.000359 | -66.791 | 56.2214 | 56.3992 | 56.0224 | -67.1614 | -0.1551 | 0.047627 | 0.00841 | -0.026952 | 0.12814 | -0.011282 | 0.19963 | -0.42404 | -0.056028 | 0.008296 | -0.053681 | 0.37035 | 0.12173 | -0.25509 | 123.0625 | 123.0035 | 123.2145 | 66.7479 | -123.1699 | 122.9588 | 123.1366 | 122.7597 | 66.7377 | -123.4389
2425.7969 | 123.1979 | -66.774 | 56.3232 | 0.0046549 | -0.029367 | -0.00017946 | 0.053295 | -0.0075872 | 0.061862 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055467 | 0.039062 | 0.055958 | -66.729 | 0.005985 | -66.7506 | 56.3297 | 56.2616 | 56.4679 | -66.9062 | -66.7382 | -0.008798 | -66.8002 | 56.2214 | 56.4084 | 56.0178 | -67.1614 | -0.13221 | 0.006429 | 0.045031 | 0.023404 | 0.15561 | -0.061637 | 0.14469 | -0.38741 | -0.1018 | 0.03576 | -0.026218 | 0.3612 | 0.085112 | -0.30545 | 123.1037 | 123.0356 | 123.2419 | 66.78 | -123.2294 | 122.9954 | 123.1823 | 122.7918 | 66.7652 | -123.4846
2426.7969 | 123.2986 | -66.7282 | 56.2775 | -0.010607 | -0.029581 | -0.00039306 | 0.052654 | -0.0073736 | 0.061221 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055681 | 0.038848 | 0.055958 | -66.7244 | 0.010564 | -66.7506 | 56.3159 | 56.2479 | 56.4542 | -66.897 | -66.7336 | -0.00422 | -66.7956 | 56.2169 | 56.4129 | 56.0086 | -67.1568 | -0.16883 | 0.03847 | 0.003833 | -0.022373 | 0.14646 | -0.029598 | 0.17673 | -0.42861 | -0.060607 | -0.005439 | -0.067416 | 0.3612 | 0.13547 | -0.26883 | 123.0441 | 122.9761 | 123.1824 | 66.7388 | -123.1745 | 122.9451 | 123.1411 | 122.7368 | 66.724 | -123.4343
2427.7969 | 123.1613 | -66.7694 | 56.3416 | -0.018238 | -0.029581 | -0.00017946 | 0.053081 | -0.0078008 | 0.061862 | 0.00015261 | -0.0030529 | 8.5466e-05 | 0.055467 | 0.039062 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3114 | 56.1929 | 56.4496 | -66.897 | -66.7336 | 0.004938 | -66.791 | 56.2169 | 56.4038 | 55.9537 | -67.1568 | -0.12763 | -0.030195 | 0.035875 | 0.009669 | 0.1373 | -0.14863 | 0.10807 | -0.38741 | -0.12469 | 0.03576 | -0.021638 | 0.36578 | 0.062222 | -0.38786 | 123.0808 | 122.9623 | 123.219 | 66.7754 | -123.2386 | 122.9863 | 123.1732 | 122.7231 | 66.7743 | -123.4984
2428.7969 | 123.2941 | -66.7328 | 56.3095 | -0.0029761 | -0.029154 | -0.00082046 | 0.053081 | -0.0073736 | 0.062076 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055681 | 0.038848 | 0.056171 | -66.7335 | -0.003172 | -66.746 | 56.3068 | 56.2067 | 56.4496 | -66.897 | -66.7382 | -0.00422 | -66.7956 | 56.226 | 56.4084 | 55.9949 | -67.1568 | -0.16425 | -0.00273 | -0.000746 | -0.013217 | 0.15104 | -0.10285 | 0.14011 | -0.42404 | -0.083493 | -0.005439 | -0.062838 | 0.3612 | 0.098845 | -0.31461 | 123.0396 | 122.9394 | 123.1824 | 66.7296 | -123.2065 | 122.9588 | 123.1411 | 122.7277 | 66.7286 | -123.4663
2429.8594 | 123.175 | -66.7831 | 56.3736 | -0.0029761 | -0.029795 | -0.00060686 | 0.053081 | -0.0075872 | 0.061648 | -0.0074779 | -0.0028393 | -0.00012813 | 0.055681 | 0.038634 | 0.056171 | -66.7244 | 0.001407 | -66.7506 | 56.3114 | 56.2204 | 56.4588 | -66.9062 | -66.7336 | -0.00422 | -66.7865 | 56.226 | 56.4038 | 56.0636 | -67.166 | -0.12306 | -0.062238 | 0.058765 | 0.032559 | 0.15561 | -0.1532 | 0.085181 | -0.38284 | -0.14758 | 0.049493 | -0.003327 | 0.37951 | 0.030179 | -0.31001 | 123.0945 | 123.0035 | 123.2419 | 66.7845 | -123.2798 | 123.0092 | 123.1869 | 122.8467 | 66.7789 | -123.5396
2430.7969 | 123.2712 | -66.7419 | 56.3004 | 0.0046549 | -0.029367 | -0.00017946 | 0.053081 | -0.0075872 | 0.061648 | 0.0077831 | -0.0030529 | 8.5466e-05 | 0.055467 | 0.039062 | 0.055531 | -66.7335 | 0.001407 | -66.7506 | 56.3114 | 56.2204 | 56.4496 | -66.9016 | -66.7291 | -0.00422 | -66.791 | 56.2214 | 56.4038 | 56.1689 | -67.1568 | -0.15968 | 0.011004 | 0.008409 | -0.00864 | 0.15104 | -0.079959 | 0.14927 | -0.41488 | -0.078916 | 0.012873 | -0.049104 | 0.36578 | 0.10342 | -0.13146 | 123.0533 | 122.9623 | 123.1916 | 66.7434 | -123.202 | 122.9634 | 123.1457 | 122.9108 | 66.7377 | -123.4572
2431.7969 | 123.2895 | -66.7282 | 56.2912 | 0.0046549 | -0.029795 | -0.00060686 | 0.053081 | -0.0075872 | 0.061648 | -0.0074779 | -0.0028393 | -0.00012813 | 0.055254 | 0.038848 | 0.056171 | -66.7335 | 0.001407 | -66.7597 | 56.3114 | 56.2067 | 56.4496 | -66.9016 | -66.7291 | 0.000359 | -66.7865 | 56.2214 | 56.3992 | 56.0407 | -67.1614 | -0.17341 | 0.020159 | -0.005324 | -0.03153 | 0.14188 | -0.084541 | 0.15842 | -0.43319 | -0.069761 | -0.00086 | -0.058259 | 0.37493 | 0.108 | -0.25051 | 123.0396 | 122.9349 | 123.1778 | 66.7296 | -123.1928 | 122.9496 | 123.1274 | 122.7689 | 66.7286 | -123.4526
2432.7969 | 123.2391 | -66.7191 | 56.3232 | -0.0029761 | -0.029367 | -0.00039306 | 0.053081 | -0.0073736 | 0.062076 | -0.0074779 | -0.0028393 | -0.00034193 | 0.055467 | 0.038848 | 0.056385 | -66.729 | -0.007751 | -66.7597 | 56.3114 | 56.1197 | 56.4542 | -66.8879 | -66.7245 | -0.013377 | -66.791 | 56.2214 | 56.4038 | 55.8392 | -67.1568 | -0.16883 | -0.011884 | -0.009901 | -0.040685 | 0.12814 | -0.20358 | 0.13096 | -0.43777 | -0.1018 | -0.005436 | -0.071992 | 0.36578 | 0.080533 | -0.48401 | 123.0304 | 122.8387 | 123.1733 | 66.7113 | -123.2111 | 122.9405 | 123.1228 | 122.5583 | 66.7057 | -123.4801
2433.7969 | 123.2437 | -66.7419 | 56.2912 | -0.010607 | -0.029154 | -0.00017946 | 0.053295 | -0.0071598 | 0.061648 | -0.015108 | -0.0028393 | 8.5466e-05 | 0.055681 | 0.039062 | 0.056385 | -66.7335 | 0.005985 | -66.7597 | 56.3114 | 56.2341 | 56.4588 | -66.9062 | -66.7291 | -0.00422 | -66.7865 | 56.2214 | 56.4129 | 56.0132 | -67.1522 | -0.16425 | 0.020159 | 0.008409 | -0.017797 | 0.14646 | -0.057068 | 0.16758 | -0.4103 | -0.069761 | 0.012873 | -0.044526 | 0.36577 | 0.12173 | -0.27798 | 123.0533 | 122.9761 | 123.2007 | 66.7479 | -123.1974 | 122.9634 | 123.1549 | 122.7552 | 66.7377 | -123.4434
2434.8594 | 123.1934 | -66.7328 | 56.3416 | -0.010607 | -0.029581 | -0.00039306 | 0.053295 | -0.0073736 | 0.061862 | 0.00015261 | -0.0030529 | -0.00034193 | 0.05504 | 0.039062 | 0.055958 | -66.729 | 0.005985 | -66.7506 | 56.3251 | 56.2845 | 56.4679 | -66.9108 | -66.7199 | -0.013377 | -66.7819 | 56.2169 | 56.3946 | 56.178 | -67.1614 | -0.17799 | -0.01646 | 0.003832 | -0.017795 | 0.16019 | -0.057054 | 0.12638 | -0.42861 | -0.12469 | 0.012876 | -0.049102 | 0.37951 | 0.053065 | -0.16351 | 123.0579 | 123.0173 | 123.2007 | 66.7388 | -123.2523 | 122.9496 | 123.1274 | 122.9108 | 66.7194 | -123.503
2435.7969 | 123.3124 | -66.7374 | 56.3004 | -0.010607 | -0.029795 | -0.00082046 | 0.052867 | -0.0069462 | 0.061648 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055467 | 0.039062 | 0.055958 | -66.7335 | 0.001407 | -66.7506 | 56.3251 | 56.2937 | 56.4588 | -66.9062 | -66.7336 | -0.008798 | -66.7865 | 56.2214 | 56.4038 | 56.0956 | -67.1522 | -0.16883 | 0.024739 | 0.003832 | -0.013217 | 0.15561 | -0.006697 | 0.15842 | -0.41488 | -0.078916 | 0.003717 | -0.049103 | 0.36577 | 0.10342 | -0.20472 | 123.0625 | 123.031 | 123.1961 | 66.7388 | -123.2066 | 122.9588 | 123.1411 | 122.833 | 66.7286 | -123.4526
2436.7969 | 123.2117 | -66.7007 | 56.3141 | 0.012286 | -0.029581 | -0.00060686 | 0.053295 | -0.0071598 | 0.061648 | -0.0074779 | -0.0030529 | 8.5466e-05 | 0.055467 | 0.039062 | 0.056171 | -66.7335 | 0.001407 | -66.7552 | 56.3205 | 56.2982 | 56.4679 | -66.9062 | -66.7336 | -0.00422 | -66.7819 | 56.2214 | 56.4084 | 56.1506 | -67.166 | -0.20545 | 0.006427 | -0.032789 | -0.054416 | 0.15104 | -0.015851 | 0.15385 | -0.46524 | -0.092649 | -0.032904 | -0.081145 | 0.38409 | 0.094267 | -0.16351 | 123.0213 | 122.999 | 123.1687 | 66.7022 | -123.2203 | 122.9222 | 123.1091 | 122.8513 | 66.6965 | -123.4801
2437.7969 | 123.2712 | -66.7374 | 56.3141 | -0.0029761 | -0.029367 | -0.00017946 | 0.053295 | -0.0071598 | 0.061435 | -0.0074779 | -0.0030529 | -0.00012813 | 0.055895 | 0.039275 | 0.056171 | -66.729 | 0.001407 | -66.7597 | 56.3297 | 56.3349 | 56.4634 | -66.9199 | -66.7199 | 0.000359 | -66.7956 | 56.2169 | 56.4038 | 56.0819 | -67.1614 | -0.18257 | 0.015584 | 0.00841 | -0.022374 | 0.1602 | 0.020781 | 0.14927 | -0.42404 | -0.097228 | 0.017454 | -0.05826 | 0.36578 | 0.089688 | -0.23219 | 123.067 | 123.0722 | 123.2007 | 66.7388 | -123.234 | 122.9542 | 123.1411 | 122.8193 | 66.7377 | -123.4755
2438.7969 | 123.2483 | -66.7282 | 56.3187 | -0.0029761 | -0.029154 | -0.00017946 | 0.053295 | -0.0073736 | 0.061862 | 0.00015261 | -0.0026255 | -0.00012813 | 0.055254 | 0.039062 | 0.056171 | -66.7244 | 0.005985 | -66.7735 | 56.3297 | 56.3303 | 56.4771 | -66.9154 | -66.7291 | -0.00422 | -66.7865 | 56.226 | 56.4038 | 56.1597 | -67.1614 | -0.18715 | 0.011006 | 0.003833 | -0.045264 | 0.14188 | 0.011624 | 0.15843 | -0.43319 | -0.092649 | -0.00086 | -0.058259 | 0.37493 | 0.08511 | -0.15893 | 123.0579 | 123.0585 | 123.2053 | 66.7342 | -123.234 | 122.9542 | 123.132 | 122.8879 | 66.724 | -123.4801
2439.7969 | 123.2803 | -66.7236 | 56.3187 | -0.010607 | -0.029367 | -0.00017946 | 0.053295 | -0.0075872 | 0.061862 | -0.0074779 | -0.0032665 | 8.5466e-05 | 0.055681 | 0.039062 | 0.056171 | -66.7244 | 0.005985 | -66.7689 | 56.3342 | 56.3349 | 56.4725 | -66.9337 | -66.7428 | -0.00422 | -66.7819 | 56.226 | 56.4038 | 56.3108 | -67.1568 | -0.21004 | 0.015585 | -0.000744 | -0.045263 | 0.16478 | 0.016203 | 0.15385 | -0.43319 | -0.092649 | -0.019173 | -0.058257 | 0.37493 | 0.08511 | -0.007839 | 123.0579 | 123.0585 | 123.1961 | 66.7296 | -123.2523 | 122.9496 | 123.1274 | 123.0345 | 66.7194 | -123.4755
2440.8594 | 123.2849 | -66.7236 | 56.3095 | -0.010607 | -0.029367 | -0.00039306 | 0.053508 | -0.0073736 | 0.061648 | -0.015108 | -0.0030529 | 8.5466e-05 | 0.055467 | 0.039062 | 0.056171 | -66.7335 | 0.001407 | -66.7781 | 56.3342 | 56.3349 | 56.4725 | -66.9337 | -66.7291 | 0.000359 | -66.7865 | 56.2214 | 56.4084 | 56.1139 | -67.1522 | -0.21004 | 0.024741 | -0.009901 | -0.05442 | 0.15562 | 0.025359 | 0.163 | -0.42861 | -0.088071 | -0.005437 | -0.062836 | 0.36577 | 0.098845 | -0.19556 | 123.0579 | 123.0585 | 123.1961 | 66.725 | -123.2432 | 122.9451 | 123.132 | 122.8376 | 66.724 | -123.4618
2441.7969 | 123.3032 | -66.7328 | 56.2912 | 0.012286 | -0.029367 | -0.00017946 | 0.053081 | -0.0073736 | 0.061648 | -0.015108 | -0.0028393 | -0.00034193 | 0.055681 | 0.039275 | 0.055958 | -66.729 | 0.005985 | -66.7689 | 56.348 | 56.344 | 56.4817 | -66.9382 | -66.7382 | -0.013377 | -66.791 | 56.2214 | 56.4084 | 56.2971 | -67.166 | -0.20546 | 0.056786 | 0.003832 | -0.036108 | 0.16935 | 0.052826 | 0.19047 | -0.43319 | -0.069761 | -0.005439 | -0.058259 | 0.37493 | 0.11716 | 0.005891 | 123.0808 | 123.0768 | 123.2145 | 66.7388 | -123.2294 | 122.9542 | 123.1411 | 123.0299 | 66.7194 | -123.4572
2442.8594 | 123.2437 | -66.7236 | 56.3232 | 0.012286 | -0.029367 | -0.00017946 | 0.053081 | -0.0071598 | 0.061648 | -0.0074779 | -0.0030529 | -0.00034193 | 0.05504 | 0.038848 | 0.055744 | -66.729 | 0.005985 | -66.7826 | 56.3526 | 56.3486 | 56.4908 | -66.9382 | -66.7428 | 0.000359 | -66.791 | 56.2214 | 56.4129 | 56.2971 | -67.1614 | -0.21462 | 0.029321 | -0.005323 | -0.058998 | 0.15562 | 0.025362 | 0.16759 | -0.43777 | -0.1018 | -0.019173 | -0.067414 | 0.37035 | 0.08969 | -0.026152 | 123.0762 | 123.0722 | 123.2145 | 66.7296 | -123.2615 | 122.9451 | 123.1366 | 123.0207 | 66.724 | -123.4846
2443.7969 | 123.23 | -66.7282 | 56.3141 | -0.0029761 | -0.029154 | -0.00039306 | 0.053295 | -0.0075872 | 0.061648 | -0.0074779 | -0.0030529 | -0.00034193 | 0.055681 | 0.038848 | 0.055958 | -66.729 | 0.015142 | -66.7826 | 56.3526 | 56.3486 | 56.4862 | -66.952 | -66.7428 | 0.000359 | -66.7865 | 56.2123 | 56.4129 | 56.32 | -67.1614 | -0.22378 | 0.038476 | -0.000746 | -0.054421 | 0.16936 | 0.034517 | 0.17216 | -0.43319 | -0.10181 | -0.014596 | -0.058259 | 0.37493 | 0.098845 | 0.005896 | 123.0808 | 123.0768 | 123.2145 | 66.7434 | -123.2661 | 122.9405 | 123.1411 | 123.0482 | 66.7286 | -123.4755
2444.7969 | 123.2758 | -66.7145 | 56.3461 | 0.0046549 | -0.029367 | -0.00039306 | 0.053295 | -0.0073736 | 0.061862 | 0.0077831 | -0.0032665 | -0.00012813 | 0.055681 | 0.039275 | 0.055958 | -66.7335 | 0.005985 | -66.7826 | 56.3526 | 56.3623 | 56.5 | -66.952 | -66.7474 | 0.004938 | -66.791 | 56.2169 | 56.4038 | 56.2421 | -67.166 | -0.23751 | 0.006433 | -0.019056 | -0.068153 | 0.16936 | 0.016211 | 0.15385 | -0.4515 | -0.12927 | -0.032907 | -0.076569 | 0.37493 | 0.057645 | -0.10398 | 123.067 | 123.0768 | 123.2145 | 66.7205 | -123.2981 | 122.9313 | 123.1183 | 122.9566 | 66.7194 | -123.5121
2445.7969 | 123.2483 | -66.7236 | 56.3095 | -0.0029761 | -0.029367 | -0.00060686 | 0.053081 | -0.0073736 | 0.062289 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055681 | 0.038848 | 0.055958 | -66.7335 | 0.005985 | -66.7872 | 56.3571 | 56.3532 | 56.5046 | -66.9566 | -66.752 | -0.008798 | -66.7865 | 56.2214 | 56.4084 | 56.2971 | -67.1522 | -0.23293 | 0.047633 | -0.009901 | -0.063576 | 0.16936 | 0.043674 | 0.19505 | -0.42861 | -0.088071 | -0.02833 | -0.062836 | 0.36577 | 0.098845 | -0.012419 | 123.0808 | 123.0768 | 123.2282 | 66.7296 | -123.2661 | 122.9451 | 123.132 | 123.0207 | 66.7148 | -123.4618
2446.8594 | 123.2574 | -66.7557 | 56.3004 | 0.0046549 | -0.029795 | -0.00039306 | 0.053081 | -0.0075872 | 0.062503 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055467 | 0.039275 | 0.055958 | -66.7244 | 0.015142 | -66.8009 | 56.3663 | 56.3715 | 56.5091 | -66.9611 | -66.7657 | 0.004938 | -66.791 | 56.2169 | 56.3992 | 56.352 | -67.1568 | -0.20547 | 0.065944 | 0.031299 | -0.045268 | 0.1602 | 0.071145 | 0.20879 | -0.40115 | -0.083495 | -0.010023 | -0.035371 | 0.36578 | 0.098843 | 0.051679 | 123.122 | 123.1272 | 123.2648 | 66.7708 | -123.2615 | 122.9725 | 123.1549 | 123.1077 | 66.7606 | -123.4572
2447.7969 | 123.2849 | -66.7236 | 56.2958 | -0.0029761 | -0.029795 | -0.00039306 | 0.053081 | -0.0071598 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055681 | 0.039062 | 0.056171 | -66.7335 | 0.015142 | -66.8055 | 56.3709 | 56.3669 | 56.5137 | -66.9657 | -66.7657 | 0.000359 | -66.791 | 56.2169 | 56.3992 | 56.3658 | -67.1568 | -0.24209 | 0.075101 | -0.009901 | -0.081889 | 0.1602 | 0.071144 | 0.21794 | -0.43319 | -0.078917 | -0.042066 | -0.067414 | 0.36578 | 0.10342 | 0.069993 | 123.0945 | 123.0906 | 123.2374 | 66.7388 | -123.2615 | 122.9405 | 123.1228 | 123.0894 | 66.724 | -123.4526
2448.7969 | 123.2803 | -66.7236 | 56.3141 | 0.0046549 | -0.030222 | -0.00082046 | 0.053081 | -0.0075872 | 0.062503 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055681 | 0.039062 | 0.055958 | -66.729 | 0.005985 | -66.8055 | 56.3709 | 56.3761 | 56.5091 | -66.9657 | -66.7657 | 0.004938 | -66.7819 | 56.226 | 56.4129 | 56.3658 | -67.1568 | -0.24209 | 0.05679 | -0.005323 | -0.081889 | 0.1602 | 0.061991 | 0.19505 | -0.43319 | -0.088071 | -0.042066 | -0.058257 | 0.37493 | 0.098845 | 0.051682 | 123.0945 | 123.0997 | 123.2328 | 66.7296 | -123.2798 | 122.9496 | 123.1366 | 123.0894 | 66.7286 | -123.4709
2449.8594 | 123.175 | -66.7831 | 56.3324 | -0.0029761 | -0.030222 | -0.00060686 | 0.052654 | -0.0078008 | 0.062717 | 0.0077831 | -0.0036937 | -0.00034193 | 0.055895 | 0.039275 | 0.056385 | -66.7335 | 0.015142 | -66.8009 | 56.3755 | 56.3807 | 56.5183 | -66.9703 | -66.7749 | 0.004938 | -66.7865 | 56.226 | 56.4084 | 56.32 | -67.1614 | -0.18716 | 0.043058 | 0.049608 | -0.017802 | 0.16936 | 0.04826 | 0.1859 | -0.37826 | -0.10638 | 0.008285 | -0.003327 | 0.37493 | 0.075957 | -0.012414 | 123.1586 | 123.1638 | 123.3014 | 66.7983 | -123.3027 | 123.0092 | 123.1915 | 123.1031 | 66.7881 | -123.4938
2450.7969 | 123.3078 | -66.6962 | 56.3324 | 0.012286 | -0.030222 | -0.00039306 | 0.052867 | -0.0078008 | 0.062503 | 0.015414 | -0.0039075 | -0.00076913 | 0.056108 | 0.039703 | 0.056385 | -66.729 | 0.010564 | -66.8101 | 56.3846 | 56.3807 | 56.5183 | -66.952 | -66.7794 | 0.000359 | -66.791 | 56.2169 | 56.4084 | 56.2009 | -67.1477 | -0.25582 | 0.052215 | -0.032789 | -0.11393 | 0.14189 | 0.04826 | 0.1859 | -0.4515 | -0.11554 | -0.083269 | -0.09488 | 0.35662 | 0.075957 | -0.13146 | 123.0808 | 123.0768 | 123.2145 | 66.7067 | -123.2844 | 122.913 | 123.1045 | 122.8971 | 66.6965 | -123.4801
2451.8594 | 123.23 | -66.7282 | 56.3416 | 0.0046549 | -0.030436 | -0.00039306 | 0.052867 | -0.0078008 | 0.063358 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055895 | 0.039489 | 0.056385 | -66.7335 | 0.005985 | -66.8147 | 56.3663 | 56.257 | 56.4496 | -66.9016 | -66.7794 | -0.013377 | -66.7865 | 56.226 | 56.4084 | 56.1826 | -67.1614 | -0.17341 | 0.024745 | -0.005324 | -0.086469 | 0.08694 | -0.084527 | 0.10807 | -0.43319 | -0.11554 | -0.051226 | -0.058259 | 0.37493 | 0.066801 | -0.15893 | 123.0945 | 122.9852 | 123.1778 | 66.7342 | -123.2432 | 122.9542 | 123.1366 | 122.9108 | 66.7148 | -123.503
2452.7969 | 123.2666 | -66.7053 | 56.3324 | -0.0029761 | -0.029795 | -0.00082046 | 0.053295 | -0.0075872 | 0.061648 | 0.0077831 | -0.0030529 | -0.00055553 | 0.055467 | 0.039275 | 0.055531 | -66.7335 | -0.007751 | -66.7872 | 56.3068 | 56.2433 | 56.4496 | -66.8925 | -66.7749 | -0.013377 | -66.791 | 56.2169 | 56.4129 | 56.2193 | -67.1568 | -0.18714 | -0.025618 | -0.028212 | -0.081887 | 0.10525 | -0.089108 | 0.11722 | -0.4515 | -0.11554 | -0.069535 | -0.085725 | 0.36578 | 0.080535 | -0.11314 | 123.0121 | 122.9486 | 123.1549 | 66.6976 | -123.2249 | 122.9222 | 123.1183 | 122.9246 | 66.6919 | -123.4892
2453.7969 | 123.2758 | -66.7282 | 56.3416 | 0.0046549 | -0.029367 | -0.00039306 | 0.053081 | -0.0073736 | 0.061648 | 0.0077831 | -0.0028393 | -0.00055553 | 0.055681 | 0.039489 | 0.055958 | -66.7427 | 0.001407 | -66.7597 | 56.3251 | 56.2479 | 56.4496 | -66.9062 | -66.7291 | -0.00422 | -66.7819 | 56.2214 | 56.4084 | 56.2238 | -67.1614 | -0.17799 | -0.01646 | -0.014481 | -0.03153 | 0.14646 | -0.093685 | 0.10807 | -0.43319 | -0.12011 | -0.00086 | -0.05368 | 0.37951 | 0.066801 | -0.11772 | 123.0533 | 122.9761 | 123.1778 | 66.7296 | -123.2478 | 122.9496 | 123.1366 | 122.952 | 66.724 | -123.503
2454.7969 | 123.2803 | -66.7099 | 56.3461 | 0.0046549 | -0.029581 | -0.00039306 | 0.053081 | -0.0071598 | 0.061648 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055467 | 0.039489 | 0.056171 | -66.7335 | 0.001407 | -66.7643 | 56.3159 | 56.2479 | 56.4496 | -66.8879 | -66.7336 | -0.008798 | -66.791 | 56.2169 | 56.4084 | 56.2147 | -67.1614 | -0.17798 | -0.030194 | -0.023634 | -0.054418 | 0.12356 | -0.098262 | 0.10349 | -0.4515 | -0.12927 | -0.023749 | -0.081147 | 0.37035 | 0.062224 | -0.13146 | 123.0258 | 122.9578 | 123.1595 | 66.7113 | -123.234 | 122.9268 | 123.1183 | 122.9246 | 66.7011 | -123.5075
2455.7969 | 123.2529 | -66.7191 | 56.337 | 0.0046549 | -0.029581 | -0.00060686 | 0.053081 | -0.0075872 | 0.061862 | 0.00015261 | -0.0026255 | 0.00029907 | 0.055467 | 0.039703 | 0.056385 | -66.7335 | 0.001407 | -66.7597 | 56.3159 | 56.2433 | 56.4542 | -66.8925 | -66.7382 | 0.000359 | -66.791 | 56.226 | 56.4084 | 56.2284 | -67.1568 | -0.17341 | -0.021039 | -0.014479 | -0.040685 | 0.13272 | -0.093686 | 0.11722 | -0.43777 | -0.11096 | -0.019172 | -0.071992 | 0.36578 | 0.071379 | -0.10856 | 123.035 | 122.9623 | 123.1733 | 66.7205 | -123.2294 | 122.9451 | 123.1274 | 122.9475 | 66.7194 | -123.4938
2456.8594 | 123.262 | -66.7099 | 56.3278 | 0.0046549 | -0.029367 | -0.00039306 | 0.053081 | -0.0075872 | 0.062076 | -0.0074779 | -0.0030529 | 8.5466e-05 | 0.055895 | 0.039062 | 0.055958 | -66.7335 | 0.005985 | -66.7552 | 56.3114 | 56.2433 | 56.4542 | -66.9016 | -66.7336 | -0.008798 | -66.8002 | 56.2214 | 56.4129 | 56.2284 | -67.166 | -0.19172 | -0.016462 | -0.023634 | -0.045261 | 0.14646 | -0.084531 | 0.12638 | -0.45608 | -0.10638 | -0.023749 | -0.090305 | 0.36578 | 0.085112 | -0.099409 | 123.0213 | 122.9532 | 123.1641 | 66.7159 | -123.2294 | 122.9313 | 123.1228 | 122.9383 | 66.7011 | -123.4938
2457.7969 | 123.2758 | -66.7419 | 56.3416 | 0.0046549 | -0.030008 | -0.00039306 | 0.053081 | -0.0078008 | 0.061862 | -0.0074779 | -0.0032665 | -0.00034193 | 0.055681 | 0.039275 | 0.056171 | -66.7335 | -0.012329 | -66.7597 | 56.3159 | 56.2479 | 56.4496 | -66.8925 | -66.7382 | -0.008798 | -66.791 | 56.226 | 56.4129 | 56.233 | -67.166 | -0.15052 | -0.025617 | 0.008409 | -0.017797 | 0.13272 | -0.093685 | 0.10807 | -0.42404 | -0.11554 | 0.003716 | -0.049104 | 0.37493 | 0.071379 | -0.10856 | 123.0579 | 122.9898 | 123.1916 | 66.7296 | -123.234 | 122.968 | 123.1549 | 122.9749 | 66.7331 | -123.5075
2458.7969 | 123.2758 | -66.7099 | 56.3416 | 0.0046549 | -0.030222 | -0.00082046 | 0.053295 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055681 | 0.039489 | 0.056385 | -66.7335 | 0.001407 | -66.7643 | 56.3159 | 56.257 | 56.445 | -66.8879 | -66.752 | -0.008798 | -66.7865 | 56.2214 | 56.4175 | 56.2376 | -67.1568 | -0.17798 | -0.025617 | -0.023634 | -0.054418 | 0.12356 | -0.084527 | 0.10349 | -0.44692 | -0.12011 | -0.042063 | -0.076569 | 0.37035 | 0.075958 | -0.10398 | 123.0258 | 122.9669 | 123.1549 | 66.7113 | -123.2294 | 122.9313 | 123.1274 | 122.9475 | 66.7011 | -123.4984
2459.7969 | 123.3124 | -66.7145 | 56.3141 | 0.0046549 | -0.029795 | -0.00082046 | 0.053508 | -0.0075872 | 0.062503 | 0.015414 | -0.0039075 | -0.00076913 | 0.055467 | 0.039489 | 0.056171 | -66.7335 | -0.003172 | -66.7643 | 56.3114 | 56.2616 | 56.4542 | -66.9016 | -66.7565 | -0.013377 | -66.791 | 56.2169 | 56.4175 | 56.2284 | -67.1614 | -0.18714 | -0.002729 | -0.019056 | -0.04984 | 0.1373 | -0.052482 | 0.14011 | -0.44692 | -0.097228 | -0.042064 | -0.076569 | 0.37035 | 0.10342 | -0.085676 | 123.0258 | 122.9761 | 123.1687 | 66.7113 | -123.2157 | 122.9313 | 123.132 | 122.9429 | 66.7011 | -123.4755
2460.7969 | 123.2391 | -66.7099 | 56.3599 | -0.010607 | -0.030008 | -0.00082046 | 0.053295 | -0.0075872 | 0.062289 | 0.0077831 | -0.0036937 | -0.00012813 | 0.055467 | 0.039703 | 0.055958 | -66.7335 | -0.007751 | -66.7643 | 56.3114 | 56.2708 | 56.4588 | -66.897 | -66.7474 | -0.008798 | -66.8002 | 56.2123 | 56.4084 | 56.2376 | -67.1522 | -0.18714 | -0.048505 | -0.023634 | -0.054418 | 0.13272 | -0.0891 | 0.098914 | -0.44234 | -0.14758 | -0.037485 | -0.090305 | 0.35204 | 0.048491 | -0.12229 | 123.0213 | 122.9807 | 123.1687 | 66.7021 | -123.2569 | 122.9222 | 123.1183 | 122.9475 | 66.7011 | -123.5121
2461.8594 | 123.2758 | -66.7236 | 56.3049 | 0.0046549 | -0.030222 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055467 | 0.039489 | 0.055744 | -66.7335 | -0.003172 | -66.7552 | 56.3159 | 56.2479 | 56.4496 | -66.897 | -66.752 | -0.00422 | -66.7773 | 56.2123 | 56.4129 | 56.2513 | -67.1568 | -0.17341 | 0.011004 | -0.009901 | -0.031528 | 0.14188 | -0.057064 | 0.14469 | -0.43319 | -0.092651 | -0.02833 | -0.053678 | 0.37951 | 0.108 | -0.053628 | 123.0396 | 122.9715 | 123.1733 | 66.7205 | -123.202 | 122.9359 | 123.1366 | 122.9749 | 66.7194 | -123.4618
2462.7969 | 123.262 | -66.7099 | 56.3553 | 0.0046549 | -0.030222 | -0.00039306 | 0.052867 | -0.0073736 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.039703 | 0.056385 | -66.729 | -0.003172 | -66.7643 | 56.3159 | 56.2524 | 56.4542 | -66.9016 | -66.7474 | -0.013377 | -66.791 | 56.2169 | 56.4175 | 56.2605 | -67.1614 | -0.19172 | -0.03935 | -0.019056 | -0.054418 | 0.1373 | -0.10284 | 0.098912 | -0.4515 | -0.13843 | -0.037485 | -0.081147 | 0.37035 | 0.062225 | -0.094825 | 123.0258 | 122.9623 | 123.1641 | 66.7067 | -123.2569 | 122.9268 | 123.1274 | 122.9704 | 66.6965 | -123.5167
2463.7969 | 123.2666 | -66.7191 | 56.3232 | -0.0029761 | -0.030222 | -0.00060686 | 0.053508 | -0.0075872 | 0.062076 | 0.0077831 | -0.0030529 | -0.00034193 | 0.055681 | 0.039703 | 0.056171 | -66.7335 | -0.012329 | -66.7643 | 56.3114 | 56.2616 | 56.4588 | -66.9016 | -66.7565 | -0.008798 | -66.791 | 56.226 | 56.4129 | 56.2376 | -67.1568 | -0.18256 | -0.011884 | -0.014479 | -0.045263 | 0.1373 | -0.061637 | 0.13553 | -0.43777 | -0.097226 | -0.037487 | -0.071992 | 0.36578 | 0.08969 | -0.085674 | 123.0304 | 122.9807 | 123.1778 | 66.7067 | -123.2249 | 122.9451 | 123.132 | 122.9566 | 66.7103 | -123.4801
2464.8594 | 123.3032 | -66.7053 | 56.2866 | -0.010607 | -0.030008 | -0.00017946 | 0.053081 | -0.0075872 | 0.062076 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.039062 | 0.055958 | -66.729 | -0.003172 | -66.7597 | 56.3114 | 56.2296 | 56.4588 | -66.9108 | -66.7382 | -0.008798 | -66.7865 | 56.2169 | 56.4038 | 56.2376 | -67.1522 | -0.20546 | 0.024737 | -0.023634 | -0.054418 | 0.15104 | -0.057069 | 0.17216 | -0.44692 | -0.069762 | -0.032905 | -0.081147 | 0.36577 | 0.11715 | -0.049053 | 123.0167 | 122.9349 | 123.1641 | 66.7021 | -123.1974 | 122.9222 | 123.1091 | 122.9429 | 66.6965 | -123.4389
2465.7969 | 123.2574 | -66.7053 | 56.3507 | 0.0046549 | -0.030222 | -0.00082046 | 0.053508 | -0.0075872 | 0.061862 | 0.015414 | -0.0032665 | -0.00055553 | 0.055681 | 0.039703 | 0.056171 | -66.7335 | -0.003172 | -66.7552 | 56.3159 | 56.2387 | 56.4634 | -66.9016 | -66.7382 | -0.008798 | -66.791 | 56.226 | 56.4129 | 56.2605 | -67.1614 | -0.1963 | -0.034772 | -0.028212 | -0.049839 | 0.14646 | -0.112 | 0.11265 | -0.45608 | -0.12469 | -0.032905 | -0.085725 | 0.37035 | 0.062224 | -0.090247 | 123.0213 | 122.944 | 123.1687 | 66.7021 | -123.2523 | 122.9313 | 123.1183 | 122.9658 | 66.6965 | -123.5121
2466.7969 | 123.1659 | -66.7603 | 56.369 | -0.0029761 | -0.029795 | -0.00060686 | 0.053081 | -0.0075872 | 0.062076 | 0.015414 | -0.0034801 | -0.00055553 | 0.055681 | 0.039489 | 0.056171 | -66.7335 | -0.007751 | -66.7643 | 56.3205 | 56.2387 | 56.4542 | -66.9016 | -66.7382 | 0.000359 | -66.7819 | 56.2214 | 56.4084 | 56.2605 | -67.1522 | -0.14136 | -0.048505 | 0.02672 | -0.004064 | 0.1373 | -0.13031 | 0.085179 | -0.39199 | -0.14758 | 0.022027 | -0.021636 | 0.37035 | 0.039335 | -0.10856 | 123.0808 | 122.999 | 123.2145 | 66.7525 | -123.2706 | 122.9817 | 123.1686 | 123.0207 | 66.7606 | -123.5213
2467.8594 | 123.317 | -66.6962 | 56.3324 | -0.0029761 | -0.030222 | -0.00039306 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055467 | 0.039275 | 0.055744 | -66.729 | -0.003172 | -66.7597 | 56.3068 | 56.2387 | 56.4588 | -66.897 | -66.7291 | -0.017956 | -66.7956 | 56.2214 | 56.4129 | 56.2513 | -67.1614 | -0.20087 | -0.025618 | -0.032789 | -0.063573 | 0.1373 | -0.093687 | 0.12638 | -0.46523 | -0.11096 | -0.032903 | -0.099459 | 0.36578 | 0.080535 | -0.081093 | 123.0029 | 122.9349 | 123.1549 | 66.693 | -123.2294 | 122.9176 | 123.1091 | 122.9475 | 66.6782 | -123.4938
2468.7969 | 123.1613 | -66.7236 | 56.3553 | 0.0046549 | -0.030222 | -0.00060686 | 0.053508 | -0.0078008 | 0.062076 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055467 | 0.039489 | 0.055744 | -66.729 | 0.010564 | -66.7506 | 56.3068 | 56.2341 | 56.4634 | -66.897 | -66.7336 | -0.013377 | -66.7865 | 56.2214 | 56.4129 | 56.2513 | -67.1614 | -0.17341 | -0.048507 | -0.005323 | -0.02695 | 0.14646 | -0.12116 | 0.10807 | -0.43777 | -0.13385 | -0.010016 | -0.062836 | 0.37493 | 0.057646 | -0.10398 | 123.0304 | 122.9578 | 123.187 | 66.7342 | -123.2523 | 122.9451 | 123.1366 | 122.9749 | 66.7103 | -123.5167
2469.7969 | 123.1155 | -66.7511 | 56.3965 | 0.0046549 | -0.030222 | -0.00039306 | 0.053508 | -0.0073736 | 0.061862 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055467 | 0.039489 | 0.055744 | -66.729 | -0.007751 | -66.7597 | 56.3159 | 56.2387 | 56.4588 | -66.897 | -66.7382 | -0.013377 | -66.7865 | 56.226 | 56.4084 | 56.2696 | -67.1614 | -0.14594 | -0.080548 | 0.022143 | -0.008641 | 0.1373 | -0.15777 | 0.062293 | -0.4103 | -0.17047 | 0.012872 | -0.03537 | 0.37493 | 0.01187 | -0.12687 | 123.067 | 122.9898 | 123.2099 | 66.7433 | -123.2935 | 122.9771 | 123.1595 | 123.0207 | 66.7377 | -123.5579
2470.8594 | 123.2346 | -66.7419 | 56.3278 | 0.0046549 | -0.030008 | -0.00060686 | 0.053295 | -0.0075872 | 0.061862 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055467 | 0.039703 | 0.055958 | -66.7381 | -0.007751 | -66.7689 | 56.3114 | 56.2341 | 56.4634 | -66.897 | -66.7428 | -0.008798 | -66.7956 | 56.2214 | 56.4129 | 56.233 | -67.1614 | -0.1551 | -0.016462 | 0.003831 | -0.026953 | 0.12814 | -0.093689 | 0.13554 | -0.41946 | -0.10638 | -0.000863 | -0.053683 | 0.36578 | 0.085112 | -0.09483 | 123.0533 | 122.9761 | 123.2053 | 66.7342 | -123.2249 | 122.9634 | 123.1549 | 122.9749 | 66.7331 | -123.4892
2471.7969 | 123.1705 | -66.7511 | 56.3599 | -0.010607 | -0.030222 | -0.00060686 | 0.053081 | -0.0073736 | 0.062076 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055681 | 0.039916 | 0.056385 | -66.729 | -0.003172 | -66.7597 | 56.3159 | 56.2341 | 56.4634 | -66.897 | -66.7336 | -0.013377 | -66.7865 | 56.2214 | 56.4129 | 56.2605 | -67.166 | -0.14594 | -0.043927 | 0.022143 | -0.008641 | 0.1373 | -0.12573 | 0.10349 | -0.41488 | -0.13842 | 0.01745 | -0.03537 | 0.37951 | 0.053069 | -0.099402 | 123.067 | 122.9852 | 123.2145 | 66.7479 | -123.2569 | 122.9725 | 123.164 | 123.0116 | 66.7377 | -123.5258
2472.8594 | 123.1934 | -66.7465 | 56.3599 | 0.0046549 | -0.030008 | -0.00017946 | 0.053508 | -0.0073736 | 0.061862 | 0.015414 | -0.0028393 | -0.00034193 | 0.055895 | 0.039703 | 0.056171 | -66.729 | -0.007751 | -66.7597 | 56.3159 | 56.2341 | 56.4634 | -66.8879 | -66.7382 | -0.013377 | -66.791 | 56.226 | 56.4129 | 56.2467 | -67.166 | -0.14136 | -0.043927 | 0.017565 | -0.013219 | 0.12814 | -0.12573 | 0.10349 | -0.41946 | -0.13385 | 0.008294 | -0.044526 | 0.37493 | 0.053069 | -0.11314 | 123.0625 | 122.9807 | 123.2099 | 66.7388 | -123.2477 | 122.9725 | 123.1595 | 122.9932 | 66.7331 | -123.5258
2473.7969 | 123.2162 | -66.7099 | 56.3644 | 0.0046549 | -0.030008 | -0.00082046 | 0.053295 | -0.0075872 | 0.061435 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055254 | 0.039489 | 0.055958 | -66.729 | 0.001407 | -66.7643 | 56.3205 | 56.2433 | 56.4542 | -66.8879 | -66.7382 | -0.013377 | -66.8002 | 56.226 | 56.4129 | 56.2559 | -67.1614 | -0.17798 | -0.043927 | -0.019056 | -0.054418 | 0.12356 | -0.12115 | 0.089757 | -0.4515 | -0.13842 | -0.028327 | -0.090305 | 0.3612 | 0.048491 | -0.10856 | 123.0304 | 122.9532 | 123.1641 | 66.7113 | -123.2523 | 122.9359 | 123.1228 | 122.9658 | 66.6965 | -123.5258
2474.7969 | 123.23 | -66.7374 | 56.337 | -0.0029761 | -0.030008 | -0.00060686 | 0.053295 | -0.0073736 | 0.061862 | -0.0074779 | -0.0030529 | 8.5466e-05 | 0.055895 | 0.039703 | 0.055958 | -66.7381 | -0.012329 | -66.7643 | 56.3159 | 56.2341 | 56.4542 | -66.8925 | -66.7291 | -0.013377 | -66.791 | 56.2123 | 56.4129 | 56.2696 | -67.166 | -0.1551 | -0.021039 | -0.000746 | -0.026952 | 0.12814 | -0.10284 | 0.11722 | -0.42862 | -0.12469 | 0.008296 | -0.053681 | 0.37493 | 0.075957 | -0.067357 | 123.0533 | 122.9715 | 123.1916 | 66.725 | -123.2294 | 122.9496 | 123.1503 | 123.007 | 66.724 | -123.503
2475.8594 | 123.2529 | -66.7511 | 56.3004 | -0.0029761 | -0.030008 | -0.00017946 | 0.053508 | -0.0073736 | 0.061648 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055681 | 0.039489 | 0.055958 | -66.7335 | -0.003172 | -66.7643 | 56.3114 | 56.225 | 56.4588 | -66.897 | -66.7291 | -0.013377 | -66.791 | 56.226 | 56.4129 | 56.2559 | -67.1568 | -0.14594 | 0.011004 | 0.017565 | -0.013219 | 0.13272 | -0.075381 | 0.15842 | -0.40572 | -0.074338 | 0.022029 | -0.039948 | 0.36578 | 0.11258 | -0.044471 | 123.0625 | 122.9761 | 123.2099 | 66.7479 | -123.1974 | 122.9771 | 123.164 | 123.007 | 66.7377 | -123.4572
2476.7969 | 123.2071 | -66.7328 | 56.3553 | -0.0029761 | -0.030008 | -0.00039306 | 0.053508 | -0.0075872 | 0.061862 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055467 | 0.039703 | 0.055958 | -66.729 | -0.007751 | -66.7643 | 56.3114 | 56.2433 | 56.4542 | -66.9062 | -66.7382 | -0.013377 | -66.791 | 56.226 | 56.4038 | 56.265 | -67.1568 | -0.17341 | -0.043928 | 0.003832 | -0.03153 | 0.14188 | -0.112 | 0.098912 | -0.42404 | -0.12927 | -0.005439 | -0.058259 | 0.36578 | 0.048489 | -0.090246 | 123.0441 | 122.9761 | 123.187 | 66.725 | -123.2615 | 122.9588 | 123.1366 | 122.9978 | 66.7194 | -123.5121
2477.7969 | 123.2025 | -66.7374 | 56.3782 | 0.0046549 | -0.030008 | -0.00039306 | 0.053081 | -0.0078008 | 0.061862 | 0.0077831 | -0.0028393 | -0.00076913 | 0.055254 | 0.039703 | 0.056171 | -66.7335 | -0.007751 | -66.7643 | 56.3205 | 56.2524 | 56.4588 | -66.9062 | -66.7336 | -0.008798 | -66.7956 | 56.2123 | 56.4129 | 56.2421 | -67.1614 | -0.16883 | -0.05766 | 0.003832 | -0.026952 | 0.14188 | -0.12573 | 0.080603 | -0.42404 | -0.16589 | 0.003717 | -0.05826 | 0.36578 | 0.034758 | -0.13603 | 123.0579 | 122.9898 | 123.1961 | 66.7296 | -123.2844 | 122.9496 | 123.1503 | 122.9795 | 66.7286 | -123.5396
2478.8594 | 123.3444 | -66.7053 | 56.3278 | -0.0029761 | -0.030008 | -0.00060686 | 0.053508 | -0.0078008 | 0.061648 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055467 | 0.039489 | 0.055744 | -66.7335 | -0.007751 | -66.7689 | 56.3159 | 56.2296 | 56.4588 | -66.9016 | -66.7291 | -0.013377 | -66.7956 | 56.226 | 56.4129 | 56.265 | -67.1568 | -0.1963 | -0.011884 | -0.028212 | -0.063574 | 0.13272 | -0.098268 | 0.13096 | -0.4515 | -0.1018 | -0.023748 | -0.090304 | 0.3612 | 0.085112 | -0.06278 | 123.0213 | 122.9349 | 123.1641 | 66.6976 | -123.2294 | 122.9313 | 123.1183 | 122.9704 | 66.6919 | -123.4846
2479.7969 | 123.1659 | -66.7374 | 56.3553 | -0.010607 | -0.030008 | -0.00039306 | 0.053295 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.039275 | 0.056171 | -66.729 | -0.003172 | -66.7552 | 56.3114 | 56.2341 | 56.4588 | -66.9016 | -66.7382 | -0.013377 | -66.791 | 56.2214 | 56.4129 | 56.233 | -67.1614 | -0.16425 | -0.043928 | 0.00841 | -0.017795 | 0.14646 | -0.12116 | 0.10349 | -0.42404 | -0.13385 | -0.000861 | -0.053681 | 0.37035 | 0.057646 | -0.1223 | 123.0487 | 122.9715 | 123.1961 | 66.7342 | -123.2569 | 122.9588 | 123.1503 | 122.9704 | 66.724 | -123.5167
2480.7969 | 123.2346 | -66.7419 | 56.3553 | 0.0046549 | -0.030008 | -0.00082046 | 0.053295 | -0.0073736 | 0.062076 | 0.00015261 | -0.0030529 | -0.00012813 | 0.055681 | 0.039703 | 0.055531 | -66.729 | -0.007751 | -66.7643 | 56.3205 | 56.2433 | 56.4542 | -66.9108 | -66.7428 | -0.008798 | -66.7865 | 56.2123 | 56.4129 | 56.265 | -67.1568 | -0.16883 | -0.034772 | 0.012987 | -0.022375 | 0.14646 | -0.112 | 0.098912 | -0.41488 | -0.14301 | -0.000863 | -0.044526 | 0.37035 | 0.057646 | -0.090246 | 123.0625 | 122.9852 | 123.1961 | 66.7342 | -123.2661 | 122.9542 | 123.1549 | 123.007 | 66.7331 | -123.5121
2481.7969 | 123.175 | -66.7694 | 56.337 | -0.010607 | -0.030008 | -0.00039306 | 0.053508 | -0.0073736 | 0.061862 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.039489 | 0.056171 | -66.729 | -0.007751 | -66.7597 | 56.3159 | 56.2479 | 56.4588 | -66.8925 | -66.7382 | -0.013377 | -66.791 | 56.226 | 56.4129 | 56.265 | -67.1614 | -0.12305 | -0.021039 | 0.040453 | 0.009669 | 0.13272 | -0.089107 | 0.1218 | -0.39199 | -0.11096 | 0.031182 | -0.021638 | 0.37035 | 0.075957 | -0.071935 | 123.0853 | 123.0173 | 123.2282 | 66.7617 | -123.2294 | 122.9954 | 123.1823 | 123.0344 | 66.756 | -123.4984
2482.7969 | 123.2162 | -66.7282 | 56.337 | 0.0046549 | -0.030649 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0028393 | -0.00034193 | 0.055681 | 0.039916 | 0.055958 | -66.729 | -0.007751 | -66.7689 | 56.3205 | 56.2387 | 56.4634 | -66.9016 | -66.7336 | -0.008798 | -66.791 | 56.2169 | 56.4084 | 56.2605 | -67.1614 | -0.17341 | -0.016461 | -0.000746 | -0.040686 | 0.13272 | -0.098265 | 0.12638 | -0.43319 | -0.12012 | -0.005439 | -0.062837 | 0.37035 | 0.071379 | -0.076514 | 123.0487 | 122.9669 | 123.1916 | 66.7205 | -123.2386 | 122.9451 | 123.1366 | 122.9887 | 66.7194 | -123.4984
2483.8594 | 123.2758 | -66.7191 | 56.3278 | 0.0046549 | -0.030436 | -0.00039306 | 0.053508 | -0.0075872 | 0.061862 | 0.015414 | -0.0030529 | -0.00012813 | 0.055681 | 0.039703 | 0.056171 | -66.7381 | -0.003172 | -66.7643 | 56.3159 | 56.2433 | 56.4588 | -66.897 | -66.7428 | -0.013377 | -66.7865 | 56.2214 | 56.4175 | 56.2284 | -67.1568 | -0.17799 | -0.011884 | -0.019057 | -0.045263 | 0.13272 | -0.084531 | 0.13096 | -0.43777 | -0.10638 | -0.023751 | -0.067414 | 0.37035 | 0.089691 | -0.099409 | 123.035 | 122.9623 | 123.1778 | 66.7159 | -123.2249 | 122.9405 | 123.1366 | 122.9475 | 66.7057 | -123.4846
2484.7969 | 123.1979 | -66.774 | 56.3599 | 0.0046549 | -0.030008 | -0.00039306 | 0.053295 | -0.0075872 | 0.062076 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.039489 | 0.056171 | -66.7335 | -0.003172 | -66.7643 | 56.3159 | 56.2662 | 56.4634 | -66.897 | -66.7474 | -0.008798 | -66.7819 | 56.226 | 56.4038 | 56.2513 | -67.166 | -0.12305 | -0.043927 | 0.040453 | 0.009669 | 0.13272 | -0.093679 | 0.10349 | -0.39199 | -0.13385 | 0.026602 | -0.007903 | 0.38409 | 0.043912 | -0.10856 | 123.0899 | 123.0402 | 123.2373 | 66.7708 | -123.2569 | 123 | 123.1778 | 123.0253 | 66.7652 | -123.5258
2485.8594 | 123.2483 | -66.7603 | 56.3049 | 0.0046549 | -0.030436 | -0.00060686 | 0.053722 | -0.0075872 | 0.061862 | 0.00015261 | -0.0030529 | -0.00055553 | 0.055681 | 0.039703 | 0.055958 | -66.729 | -0.007751 | -66.7643 | 56.3114 | 56.257 | 56.4588 | -66.8925 | -66.7336 | -0.013377 | -66.7865 | 56.226 | 56.4084 | 56.2513 | -67.1568 | -0.13221 | 0.006426 | 0.031298 | -0.004064 | 0.12814 | -0.047906 | 0.15384 | -0.39657 | -0.078916 | 0.026605 | -0.026215 | 0.37035 | 0.10342 | -0.053628 | 123.0716 | 123.0173 | 123.219 | 66.7525 | -123.1974 | 122.9863 | 123.1686 | 123.0116 | 66.7469 | -123.4618
2486.7969 | 123.143 | -66.7557 | 56.3736 | -0.0029761 | -0.030436 | -0.00039306 | 0.053081 | -0.0078008 | 0.062289 | 0.0077831 | -0.0032665 | -0.00012813 | 0.055681 | 0.039489 | 0.056171 | -66.7381 | 0.001407 | -66.7597 | 56.3205 | 56.2616 | 56.4542 | -66.897 | -66.7474 | -0.008798 | -66.791 | 56.2214 | 56.4175 | 56.2513 | -67.1614 | -0.14136 | -0.053082 | 0.017564 | -0.004064 | 0.1373 | -0.11199 | 0.080602 | -0.40573 | -0.15216 | 0.008291 | -0.035371 | 0.37035 | 0.043915 | -0.12229 | 123.0762 | 123.0173 | 123.2099 | 66.7571 | -123.2706 | 122.9771 | 123.1732 | 123.007 | 66.7469 | -123.535
2487.7969 | 123.2391 | -66.7557 | 56.3507 | -0.0029761 | -0.030008 | -0.00039306 | 0.053295 | -0.0078008 | 0.062076 | 0.00015261 | -0.0032665 | -0.00012813 | 0.055681 | 0.039703 | 0.055958 | -66.729 | -0.007751 | -66.7689 | 56.3159 | 56.2616 | 56.4588 | -66.897 | -66.7474 | -0.017956 | -66.7819 | 56.226 | 56.4175 | 56.2605 | -67.1614 | -0.14136 | -0.034772 | 0.02672 | -0.01322 | 0.12814 | -0.089103 | 0.10807 | -0.40573 | -0.12469 | 0.008291 | -0.026214 | 0.37951 | 0.066803 | -0.090247 | 123.0716 | 123.0173 | 123.2145 | 66.7479 | -123.2477 | 122.9817 | 123.1732 | 123.0161 | 66.7377 | -123.5121
2488.7969 | 123.2758 | -66.7099 | 56.3049 | 0.0046549 | -0.030222 | -0.00060686 | 0.053295 | -0.0073736 | 0.062289 | 0.00015261 | -0.0030529 | -0.00034193 | 0.055681 | 0.039489 | 0.056385 | -66.729 | -0.007751 | -66.7643 | 56.3159 | 56.2662 | 56.4542 | -66.897 | -66.7428 | -0.008798 | -66.791 | 56.2169 | 56.4175 | 56.2238 | -67.166 | -0.18714 | 0.011004 | -0.019056 | -0.054418 | 0.13272 | -0.038748 | 0.14927 | -0.45608 | -0.088073 | -0.032906 | -0.081147 | 0.37493 | 0.11258 | -0.0811 | 123.0258 | 122.9761 | 123.1641 | 66.7021 | -123.202 | 122.9268 | 123.1274 | 122.9337 | 66.7011 | -123.4709
2489.7969 | 123.2346 | -66.7328 | 56.3324 | -0.0029761 | -0.030222 | -0.00060686 | 0.053081 | -0.0075872 | 0.061862 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.039916 | 0.056599 | -66.7335 | -0.003172 | -66.7689 | 56.3205 | 56.2662 | 56.4634 | -66.9062 | -66.752 | -0.022535 | -66.791 | 56.2214 | 56.4129 | 56.2513 | -67.1614 | -0.17341 | -0.011883 | -0.000746 | -0.036108 | 0.1373 | -0.066213 | 0.13096 | -0.42861 | -0.11096 | -0.019175 | -0.058259 | 0.37035 | 0.080535 | -0.081093 | 123.0533 | 122.999 | 123.1961 | 66.7296 | -123.2386 | 122.9542 | 123.1457 | 122.9841 | 66.7103 | -123.4938
2490.7969 | 123.1705 | -66.7603 | 56.3324 | 0.012286 | -0.030649 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.039489 | 0.056171 | -66.7381 | -0.012329 | -66.7689 | 56.3159 | 56.257 | 56.4588 | -66.9016 | -66.752 | -0.008798 | -66.791 | 56.2169 | 56.4084 | 56.2513 | -67.1614 | -0.14136 | -0.016461 | 0.022142 | -0.008642 | 0.13272 | -0.075371 | 0.12638 | -0.40115 | -0.11554 | 0.008291 | -0.030793 | 0.37035 | 0.075957 | -0.081093 | 123.0762 | 123.0173 | 123.219 | 66.7479 | -123.234 | 122.9771 | 123.1686 | 123.0116 | 66.7515 | -123.4938
2491.7969 | 123.175 | -66.7786 | 56.3324 | -0.0029761 | -0.030436 | -0.00039306 | 0.052867 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055895 | 0.040344 | 0.055958 | -66.729 | -0.007751 | -66.7689 | 56.3159 | 56.2616 | 56.4634 | -66.9016 | -66.7428 | -0.008798 | -66.791 | 56.2214 | 56.4129 | 56.2605 | -67.166 | -0.12305 | -0.016461 | 0.049608 | 0.009668 | 0.13272 | -0.070792 | 0.13096 | -0.38742 | -0.11096 | 0.035758 | -0.012483 | 0.37493 | 0.080535 | -0.071936 | 123.0945 | 123.0402 | 123.2419 | 66.7708 | -123.234 | 123 | 123.1915 | 123.039 | 66.7698 | -123.4984
2492.7969 | 123.1934 | -66.7465 | 56.3141 | -0.018238 | -0.030222 | -0.00060686 | 0.053081 | -0.0075872 | 0.062076 | 0.00015261 | -0.0039075 | -0.00034193 | 0.055254 | 0.039703 | 0.055958 | -66.7381 | -0.007751 | -66.7643 | 56.3114 | 56.257 | 56.4588 | -66.897 | -66.7474 | -0.013377 | -66.7819 | 56.226 | 56.4129 | 56.2513 | -67.1614 | -0.15052 | -0.002729 | 0.008409 | -0.017797 | 0.13272 | -0.057061 | 0.14469 | -0.41488 | -0.088071 | -0.000864 | -0.035369 | 0.37951 | 0.098845 | -0.062783 | 123.0579 | 123.0035 | 123.2053 | 66.7388 | -123.2111 | 122.9725 | 123.1595 | 122.9978 | 66.7331 | -123.4755
2493.7969 | 123.2895 | -66.7328 | 56.3324 | -0.010607 | -0.030008 | -0.00060686 | 0.053295 | -0.0078008 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055895 | 0.039703 | 0.055958 | -66.7335 | -0.021486 | -66.7643 | 56.3114 | 56.257 | 56.4588 | -66.897 | -66.7428 | -0.017956 | -66.791 | 56.2306 | 56.4129 | 56.265 | -67.1568 | -0.16425 | -0.021039 | -0.000746 | -0.03153 | 0.13272 | -0.075371 | 0.12638 | -0.42404 | -0.1018 | -0.010018 | -0.058259 | 0.36578 | 0.080535 | -0.067357 | 123.0441 | 122.9898 | 123.1916 | 66.7113 | -123.2294 | 122.9634 | 123.1457 | 122.9978 | 66.7148 | -123.4892
2494.8594 | 123.2574 | -66.7236 | 56.2912 | 0.0046549 | -0.030649 | -0.00039306 | 0.053508 | -0.0078008 | 0.062503 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055467 | 0.04013 | 0.055958 | -66.7244 | -0.012329 | -66.7597 | 56.3159 | 56.2662 | 56.4588 | -66.9016 | -66.7382 | -0.017956 | -66.7819 | 56.2214 | 56.4084 | 56.2605 | -67.1614 | -0.17799 | 0.024737 | -0.000744 | -0.036107 | 0.14188 | -0.025015 | 0.16758 | -0.43777 | -0.069761 | -0.014594 | -0.058257 | 0.37951 | 0.11716 | -0.030738 | 123.0396 | 122.9898 | 123.1824 | 66.7113 | -123.1928 | 122.9451 | 123.132 | 122.9841 | 66.7057 | -123.4526
2495.7969 | 123.2208 | -66.7603 | 56.3644 | -0.0029761 | -0.030436 | -0.00082046 | 0.053081 | -0.0078008 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.05504 | 0.039703 | 0.055958 | -66.7335 | -0.012329 | -66.7597 | 56.3205 | 56.2708 | 56.4634 | -66.9016 | -66.7474 | -0.008798 | -66.7865 | 56.2306 | 56.4175 | 56.2742 | -67.166 | -0.14136 | -0.043927 | 0.02672 | 0.000514 | 0.14188 | -0.093678 | 0.098915 | -0.40573 | -0.13385 | 0.012869 | -0.026215 | 0.37951 | 0.05307 | -0.090244 | 123.0808 | 123.031 | 123.2236 | 66.7479 | -123.2661 | 122.9908 | 123.1778 | 123.0345 | 66.7515 | -123.5304
2496.7969 | 123.2986 | -66.7419 | 56.3095 | 0.0046549 | -0.030436 | -0.00082046 | 0.053508 | -0.0078008 | 0.062076 | 0.00015261 | -0.0030529 | -0.00076913 | 0.055467 | 0.039916 | 0.056171 | -66.7427 | -0.012329 | -66.7689 | 56.3159 | 56.2616 | 56.4588 | -66.8925 | -66.7428 | -0.013377 | -66.791 | 56.2214 | 56.4084 | 56.2559 | -67.1751 | -0.15052 | 0.006427 | -0.000748 | -0.026953 | 0.12356 | -0.047904 | 0.14927 | -0.43319 | -0.088071 | -0.000863 | -0.049104 | 0.38409 | 0.098845 | -0.053626 | 123.0579 | 123.0035 | 123.2007 | 66.7296 | -123.202 | 122.9634 | 123.1503 | 122.9978 | 66.7286 | -123.4846
2497.7969 | 123.2117 | -66.7648 | 56.3278 | -0.0029761 | -0.030649 | -0.00082046 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055467 | 0.039916 | 0.056171 | -66.729 | -0.003172 | -66.7643 | 56.3205 | 56.2524 | 56.4588 | -66.8925 | -66.7474 | -0.013377 | -66.7956 | 56.2214 | 56.4129 | 56.2605 | -67.166 | -0.12763 | -0.007306 | 0.035876 | 0.000514 | 0.12814 | -0.075373 | 0.13096 | -0.40115 | -0.10638 | 0.017447 | -0.030794 | 0.37036 | 0.085112 | -0.067359 | 123.0853 | 123.0173 | 123.2236 | 66.7617 | -123.2203 | 122.9863 | 123.1778 | 123.0253 | 66.7515 | -123.4938
2498.8125 | 123.1934 | -66.7328 | 56.3644 | -0.010607 | -0.030649 | -0.00039306 | 0.053081 | -0.0078008 | 0.062076 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055254 | 0.039916 | 0.055744 | -66.7335 | -0.007751 | -66.7643 | 56.3114 | 56.2524 | 56.4634 | -66.897 | -66.7474 | -0.017956 | -66.7819 | 56.226 | 56.4084 | 56.265 | -67.166 | -0.16425 | -0.053083 | -0.000746 | -0.03153 | 0.13272 | -0.11199 | 0.098915 | -0.43319 | -0.13842 | -0.014597 | -0.049102 | 0.38409 | 0.043913 | -0.099401 | 123.0441 | 122.9852 | 123.1961 | 66.725 | -123.2615 | 122.9588 | 123.1411 | 122.9978 | 66.7148 | -123.5304
2499.7969 | 123.2483 | -66.7465 | 56.2958 | -0.0029761 | -0.030436 | -0.00082046 | 0.052867 | -0.0078008 | 0.062503 | -0.015108 | -0.0032665 | -0.00076913 | 0.055681 | 0.039703 | 0.056171 | -66.729 | -0.012329 | -66.7597 | 56.3205 | 56.2524 | 56.4542 | -66.897 | -66.7474 | -0.013377 | -66.7865 | 56.226 | 56.4038 | 56.2284 | -67.1568 | -0.15052 | 0.024738 | 0.017565 | -0.013219 | 0.1373 | -0.043329 | 0.15842 | -0.4103 | -0.06976 | -0.000864 | -0.039948 | 0.37035 | 0.108 | -0.067365 | 123.067 | 122.999 | 123.2007 | 66.7342 | -123.1928 | 122.9725 | 123.1503 | 122.9749 | 66.7331 | -123.4526
2500.8594 | 123.143 | -66.7603 | 56.3416 | -0.0029761 | -0.030649 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.039916 | 0.056171 | -66.7381 | -0.012329 | -66.7552 | 56.3205 | 56.2524 | 56.4588 | -66.9062 | -66.7565 | -0.008798 | -66.791 | 56.2169 | 56.4038 | 56.2605 | -67.1706 | -0.14594 | -0.021039 | 0.022142 | 0.005093 | 0.15104 | -0.089106 | 0.11722 | -0.41031 | -0.12469 | 0.003712 | -0.030793 | 0.37951 | 0.062222 | -0.081092 | 123.0808 | 123.0127 | 123.219 | 66.7479 | -123.2478 | 122.9771 | 123.164 | 123.0207 | 66.7515 | -123.5121
2501.7969 | 123.2803 | -66.7328 | 56.2912 | 0.0046549 | -0.030863 | -0.00039306 | 0.053081 | -0.0082282 | 0.062503 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055467 | 0.04013 | 0.056385 | -66.7427 | -0.012329 | -66.7643 | 56.3205 | 56.2662 | 56.4588 | -66.8925 | -66.7474 | -0.017956 | -66.791 | 56.2214 | 56.4038 | 56.265 | -67.166 | -0.15967 | 0.029315 | -0.009903 | -0.03153 | 0.12814 | -0.025015 | 0.16758 | -0.43319 | -0.069761 | -0.014597 | -0.058259 | 0.37493 | 0.11258 | -0.026159 | 123.0533 | 122.999 | 123.1916 | 66.7205 | -123.1837 | 122.9542 | 123.1366 | 122.9978 | 66.7148 | -123.4572
2502.8594 | 123.1659 | -66.7648 | 56.369 | 0.0046549 | -0.030436 | -0.00060686 | 0.053508 | -0.0075872 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.055681 | 0.039916 | 0.056171 | -66.729 | -0.012329 | -66.7689 | 56.3205 | 56.2616 | 56.4542 | -66.897 | -66.7565 | -0.013377 | -66.7956 | 56.2214 | 56.4084 | 56.2513 | -67.1568 | -0.13221 | -0.048505 | 0.035876 | -0.004064 | 0.12814 | -0.10741 | 0.085179 | -0.39199 | -0.14758 | 0.00829 | -0.030794 | 0.3612 | 0.039335 | -0.11772 | 123.0853 | 123.0264 | 123.219 | 66.7525 | -123.2661 | 122.9863 | 123.1732 | 123.0161 | 66.7515 | -123.5258
2503.7969 | 123.2941 | -66.7099 | 56.3599 | 0.0046549 | -0.030649 | -0.00039306 | 0.053081 | -0.0080146 | 0.062503 | 0.015414 | -0.0034801 | -0.00055553 | 0.055895 | 0.039489 | 0.056171 | -66.7381 | -0.012329 | -66.7643 | 56.3159 | 56.2616 | 56.4588 | -66.9016 | -66.7474 | -0.017956 | -66.7865 | 56.226 | 56.4084 | 56.2513 | -67.166 | -0.19172 | -0.043927 | -0.028212 | -0.054418 | 0.1373 | -0.098258 | 0.098914 | -0.45608 | -0.13385 | -0.037485 | -0.076569 | 0.37951 | 0.048491 | -0.10856 | 123.0258 | 122.9715 | 123.1687 | 66.6976 | -123.2615 | 122.9359 | 123.1183 | 122.9612 | 66.6919 | -123.5258
2504.8594 | 123.2346 | -66.7374 | 56.3049 | -0.0029761 | -0.030649 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055895 | 0.039703 | 0.055744 | -66.7244 | -0.007751 | -66.7689 | 56.3114 | 56.2662 | 56.4634 | -66.897 | -66.752 | -0.013377 | -66.7956 | 56.2169 | 56.4084 | 56.2605 | -67.166 | -0.15967 | 0.006426 | 0.012989 | -0.03153 | 0.12814 | -0.038748 | 0.15842 | -0.42862 | -0.088073 | -0.014597 | -0.05826 | 0.37036 | 0.10342 | -0.044471 | 123.0487 | 123.0035 | 123.2007 | 66.7296 | -123.202 | 122.9542 | 123.1457 | 122.9978 | 66.724 | -123.4709
2505.7969 | 123.23 | -66.7236 | 56.3232 | -0.0029761 | -0.030649 | -0.00082046 | 0.053081 | -0.0080146 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.039916 | 0.056385 | -66.7335 | -0.016908 | -66.7735 | 56.3159 | 56.2662 | 56.4588 | -66.8879 | -66.752 | -0.013377 | -66.7956 | 56.2214 | 56.4084 | 56.2559 | -67.166 | -0.16425 | -0.007306 | -0.009901 | -0.049841 | 0.11441 | -0.057058 | 0.13553 | -0.44235 | -0.1018 | -0.02833 | -0.071993 | 0.37036 | 0.085112 | -0.067359 | 123.0396 | 122.9898 | 123.1824 | 66.7067 | -123.2111 | 122.9451 | 123.132 | 122.9795 | 66.7103 | -123.4892
2506.7969 | 123.2849 | -66.7007 | 56.3324 | 0.0046549 | -0.030649 | -0.00039306 | 0.053295 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055254 | 0.040344 | 0.055958 | -66.7335 | -0.012329 | -66.7643 | 56.3205 | 56.2616 | 56.4588 | -66.9016 | -66.752 | -0.022535 | -66.7819 | 56.2214 | 56.4129 | 56.233 | -67.1568 | -0.20087 | -0.011883 | -0.032789 | -0.063573 | 0.1373 | -0.070792 | 0.12638 | -0.45608 | -0.11096 | -0.051218 | -0.081145 | 0.37493 | 0.080535 | -0.099407 | 123.0213 | 122.9624 | 123.1595 | 66.6884 | -123.234 | 122.9222 | 123.1137 | 122.9337 | 66.6782 | -123.4892
2507.7969 | 123.2391 | -66.7374 | 56.3461 | 0.0046549 | -0.030436 | -0.00060686 | 0.053508 | -0.0080146 | 0.062503 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055895 | 0.039916 | 0.055744 | -66.7381 | -0.012329 | -66.7597 | 56.3159 | 56.2616 | 56.4588 | -66.9016 | -66.7474 | -0.022535 | -66.791 | 56.2169 | 56.4084 | 56.2421 | -67.166 | -0.16425 | -0.030194 | -0.000746 | -0.022374 | 0.14188 | -0.084525 | 0.11265 | -0.42862 | -0.12927 | -0.010019 | -0.053681 | 0.37493 | 0.062224 | -0.10398 | 123.0533 | 122.999 | 123.1961 | 66.725 | -123.2477 | 122.9542 | 123.1457 | 122.9795 | 66.7148 | -123.5121
2508.8594 | 123.1934 | -66.7419 | 56.3828 | 0.0046549 | -0.030222 | -0.00060686 | 0.053081 | -0.0078008 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.039916 | 0.056171 | -66.7381 | -0.016908 | -66.7597 | 56.3114 | 56.2662 | 56.4542 | -66.897 | -66.7474 | -0.017956 | -66.791 | 56.2214 | 56.4175 | 56.2421 | -67.166 | -0.1551 | -0.071393 | 0.003831 | -0.017797 | 0.1373 | -0.11657 | 0.071447 | -0.42404 | -0.16131 | -0.005442 | -0.049104 | 0.37493 | 0.03476 | -0.1406 | 123.0533 | 123.0081 | 123.1961 | 66.725 | -123.2798 | 122.9634 | 123.1595 | 122.9841 | 66.724 | -123.5487
2509.7969 | 123.2529 | -66.7282 | 56.3095 | 0.012286 | -0.030863 | -0.00039306 | 0.053295 | -0.0075872 | 0.062717 | -0.0074779 | -0.0034801 | -0.00098273 | 0.055895 | 0.04013 | 0.056171 | -66.729 | -0.016908 | -66.7643 | 56.3114 | 56.2524 | 56.4588 | -66.8879 | -66.752 | -0.017956 | -66.7865 | 56.2214 | 56.4084 | 56.2284 | -67.1614 | -0.15967 | 0.001849 | -0.000746 | -0.036108 | 0.12356 | -0.057062 | 0.14927 | -0.43319 | -0.088071 | -0.023753 | -0.058259 | 0.37493 | 0.098845 | -0.081098 | 123.0396 | 122.9807 | 123.187 | 66.7113 | -123.1974 | 122.9496 | 123.1366 | 122.9566 | 66.7103 | -123.4709
2510.7969 | 123.2346 | -66.7191 | 56.3736 | -0.0029761 | -0.030863 | -0.00039306 | 0.053295 | -0.0078008 | 0.062717 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055681 | 0.04013 | 0.056171 | -66.7335 | -0.016908 | -66.7506 | 56.3205 | 56.2662 | 56.4679 | -66.897 | -66.752 | -0.022535 | -66.7819 | 56.2306 | 56.4129 | 56.2238 | -67.1614 | -0.17799 | -0.053082 | -0.014479 | -0.031528 | 0.14646 | -0.10741 | 0.094338 | -0.44235 | -0.143 | -0.032908 | -0.062835 | 0.37951 | 0.039336 | -0.14976 | 123.0396 | 122.9852 | 123.187 | 66.7021 | -123.2706 | 122.9496 | 123.132 | 122.9429 | 66.6965 | -123.535
2511.7969 | 123.3307 | -66.7145 | 56.3461 | 0.0046549 | -0.030649 | -0.00039306 | 0.053295 | -0.0078008 | 0.062289 | -0.0074779 | -0.0034801 | -0.00012813 | 0.055467 | 0.04013 | 0.056171 | -66.7244 | -0.016908 | -66.7689 | 56.3159 | 56.2616 | 56.4679 | -66.8879 | -66.7474 | -0.017956 | -66.791 | 56.2169 | 56.4038 | 56.2421 | -67.166 | -0.1734 | -0.030194 | -0.009899 | -0.054418 | 0.11899 | -0.084525 | 0.1218 | -0.4515 | -0.12927 | -0.032907 | -0.076569 | 0.37493 | 0.057645 | -0.10398 | 123.0304 | 122.9761 | 123.1824 | 66.6976 | -123.234 | 122.9313 | 123.1183 | 122.9566 | 66.6965 | -123.5121
2512.8594 | 123.1613 | -66.7282 | 56.3599 | 0.0046549 | -0.030649 | -0.00060686 | 0.052867 | -0.0080146 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055681 | 0.04013 | 0.056385 | -66.7335 | -0.016908 | -66.7597 | 56.3114 | 56.2616 | 56.4634 | -66.897 | -66.7474 | -0.027113 | -66.7819 | 56.2214 | 56.4129 | 56.2421 | -67.166 | -0.16883 | -0.048505 | -0.005324 | -0.03153 | 0.1373 | -0.098258 | 0.10349 | -0.43777 | -0.13842 | -0.019175 | -0.05368 | 0.38409 | 0.053069 | -0.11772 | 123.0396 | 122.9898 | 123.1916 | 66.7113 | -123.2569 | 122.9496 | 123.1411 | 122.9704 | 66.7011 | -123.5258
2513.7969 | 123.2849 | -66.6916 | 56.3095 | 0.0046549 | -0.031077 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055467 | 0.04013 | 0.056171 | -66.7381 | -0.012329 | -66.7689 | 56.3205 | 56.257 | 56.4634 | -66.897 | -66.7428 | -0.022535 | -66.791 | 56.2169 | 56.4129 | 56.2376 | -67.166 | -0.20545 | 0.011005 | -0.046523 | -0.077307 | 0.12814 | -0.052483 | 0.15385 | -0.47439 | -0.09265 | -0.051217 | -0.099458 | 0.37493 | 0.10342 | -0.071941 | 123.0121 | 122.9486 | 123.1549 | 66.6793 | -123.2065 | 122.9084 | 123.1045 | 122.9292 | 66.6691 | -123.4755
2514.7969 | 123.2025 | -66.7282 | 56.3873 | 0.0046549 | -0.030863 | -0.00082046 | 0.052867 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055681 | 0.039703 | 0.056385 | -66.729 | -0.003172 | -66.7597 | 56.3159 | 56.2616 | 56.4588 | -66.8925 | -66.752 | -0.013377 | -66.7865 | 56.2214 | 56.4084 | 56.2376 | -67.1614 | -0.16425 | -0.071393 | -0.000746 | -0.03153 | 0.13272 | -0.12572 | 0.071448 | -0.43319 | -0.16589 | -0.023753 | -0.058259 | 0.37493 | 0.021025 | -0.14976 | 123.0441 | 122.9898 | 123.187 | 66.725 | -123.2798 | 122.9496 | 123.1366 | 122.9658 | 66.7148 | -123.5487
2515.7969 | 123.2529 | -66.7145 | 56.3187 | 0.012286 | -0.030863 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.039916 | 0.056171 | -66.7381 | -0.012329 | -66.7597 | 56.3159 | 56.257 | 56.4588 | -66.897 | -66.752 | -0.022535 | -66.7865 | 56.226 | 56.4129 | 56.2193 | -67.1568 | -0.18256 | -0.002729 | -0.023634 | -0.045262 | 0.1373 | -0.061639 | 0.14011 | -0.44235 | -0.092649 | -0.037485 | -0.071991 | 0.37035 | 0.094267 | -0.099411 | 123.0304 | 122.9715 | 123.1733 | 66.7021 | -123.2157 | 122.9405 | 123.1274 | 122.9337 | 66.6919 | -123.4755
2516.8594 | 123.3078 | -66.7145 | 56.3095 | 0.012286 | -0.030649 | -0.00060686 | 0.053508 | -0.0078008 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055681 | 0.039916 | 0.055958 | -66.729 | -0.016908 | -66.7643 | 56.3205 | 56.2662 | 56.4634 | -66.897 | -66.7565 | -0.017956 | -66.791 | 56.226 | 56.4084 | 56.2376 | -67.166 | -0.18256 | 0.011005 | -0.014478 | -0.04984 | 0.13272 | -0.043325 | 0.15385 | -0.4515 | -0.083493 | -0.042064 | -0.076569 | 0.37493 | 0.098845 | -0.071941 | 123.035 | 122.9807 | 123.1778 | 66.6976 | -123.2065 | 122.9405 | 123.1228 | 122.952 | 66.6965 | -123.4755
2517.7969 | 123.2162 | -66.7236 | 56.3507 | -0.0029761 | -0.031077 | -0.00039306 | 0.053081 | -0.0078008 | 0.062503 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055467 | 0.040344 | 0.056171 | -66.7198 | -0.016908 | -66.7597 | 56.3114 | 56.257 | 56.4588 | -66.897 | -66.7611 | -0.017956 | -66.7865 | 56.2214 | 56.4129 | 56.2376 | -67.166 | -0.17341 | -0.03935 | 0.003834 | -0.036107 | 0.1373 | -0.093682 | 0.10807 | -0.44235 | -0.12927 | -0.037488 | -0.062836 | 0.37951 | 0.062224 | -0.11314 | 123.035 | 122.9807 | 123.1824 | 66.7067 | -123.2477 | 122.9451 | 123.1366 | 122.9612 | 66.7057 | -123.5167
2518.7969 | 123.2025 | -66.7374 | 56.337 | -0.0029761 | -0.030863 | -0.00039306 | 0.053295 | -0.0078008 | 0.062717 | 0.015414 | -0.0036937 | -0.00055553 | 0.055681 | 0.040344 | 0.056171 | -66.729 | -0.012329 | -66.7735 | 56.3205 | 56.2616 | 56.4542 | -66.9062 | -66.7565 | -0.008798 | -66.7956 | 56.2123 | 56.4129 | 56.2421 | -67.166 | -0.16883 | -0.016461 | 0.00841 | -0.036108 | 0.13272 | -0.07537 | 0.11722 | -0.42862 | -0.12469 | -0.019176 | -0.05826 | 0.37036 | 0.075957 | -0.094828 | 123.0579 | 122.999 | 123.1916 | 66.725 | -123.2432 | 122.9496 | 123.1503 | 122.9795 | 66.7286 | -123.503
2519.8594 | 123.175 | -66.7328 | 56.369 | 0.0046549 | -0.030863 | -0.00082046 | 0.053295 | -0.0075872 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055895 | 0.040344 | 0.056171 | -66.7244 | -0.016908 | -66.7826 | 56.3297 | 56.2891 | 56.4725 | -66.9108 | -66.7657 | -0.013377 | -66.7819 | 56.226 | 56.4084 | 56.2513 | -67.1614 | -0.17799 | -0.039348 | 0.008411 | -0.049843 | 0.12815 | -0.079941 | 0.10349 | -0.42861 | -0.143 | -0.032911 | -0.049102 | 0.37951 | 0.039335 | -0.11772 | 123.0625 | 123.0219 | 123.2053 | 66.7159 | -123.2798 | 122.9588 | 123.1411 | 122.9841 | 66.7194 | -123.5304
2520.7969 | 123.2391 | -66.7374 | 56.3599 | -0.010607 | -0.031077 | -0.00060686 | 0.052867 | -0.0078008 | 0.062717 | 0.00015261 | -0.0039075 | -0.00076913 | 0.055681 | 0.040344 | 0.056385 | -66.7335 | -0.012329 | -66.7826 | 56.3342 | 56.2799 | 56.4725 | -66.9062 | -66.7611 | -0.013377 | -66.7819 | 56.226 | 56.4084 | 56.2467 | -67.166 | -0.16883 | -0.025613 | 0.003832 | -0.045265 | 0.12357 | -0.079942 | 0.11265 | -0.42862 | -0.13385 | -0.023755 | -0.044524 | 0.38409 | 0.048491 | -0.11314 | 123.0716 | 123.0173 | 123.2099 | 66.725 | -123.2661 | 122.9634 | 123.1457 | 122.9841 | 66.724 | -123.5258
2521.8594 | 123.2208 | -66.7465 | 56.3507 | 0.012286 | -0.031504 | -0.00082046 | 0.052654 | -0.0080146 | 0.062076 | 0.015414 | -0.0032665 | -0.00076913 | 0.055467 | 0.039916 | 0.056171 | -66.7335 | -0.012329 | -66.7964 | 56.3388 | 56.2753 | 56.4862 | -66.9062 | -66.7657 | -0.022535 | -66.7819 | 56.2214 | 56.4038 | 56.2376 | -67.166 | -0.15968 | -0.01188 | 0.012987 | -0.049845 | 0.10983 | -0.075366 | 0.13554 | -0.41946 | -0.12927 | -0.019178 | -0.035369 | 0.38409 | 0.053067 | -0.11314 | 123.0853 | 123.0219 | 123.2328 | 66.7342 | -123.2569 | 122.968 | 123.1503 | 122.9841 | 66.724 | -123.5167
2522.7969 | 123.2162 | -66.7603 | 56.3232 | -0.010607 | -0.03129 | -0.00039306 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0036937 | -0.00098273 | 0.055681 | 0.040557 | 0.056171 | -66.7335 | -0.003172 | -66.7781 | 56.3434 | 56.3166 | 56.4862 | -66.9291 | -66.7611 | -0.013377 | -66.7956 | 56.2214 | 56.4038 | 56.2834 | -67.1568 | -0.16884 | 0.020164 | 0.02672 | -0.017799 | 0.15104 | -0.00669 | 0.16301 | -0.39657 | -0.1018 | -0.000867 | -0.035372 | 0.3612 | 0.080533 | -0.039888 | 123.1037 | 123.0768 | 123.2465 | 66.7571 | -123.2523 | 122.9817 | 123.164 | 123.0436 | 66.7469 | -123.4801
2523.8594 | 123.2895 | -66.7374 | 56.3232 | -0.010607 | -0.03129 | -0.00060686 | 0.053508 | -0.0078008 | 0.062717 | -0.0074779 | -0.0030529 | -0.00055553 | 0.055467 | 0.04013 | 0.055744 | -66.7381 | -0.016908 | -66.7689 | 56.3159 | 56.2616 | 56.4679 | -66.9016 | -66.752 | -0.013377 | -66.7865 | 56.2169 | 56.4084 | 56.2605 | -67.1614 | -0.16425 | -0.007306 | -0.000746 | -0.03153 | 0.13272 | -0.061637 | 0.14469 | -0.42404 | -0.10638 | -0.014597 | -0.049103 | 0.37493 | 0.085112 | -0.062781 | 123.0533 | 122.999 | 123.2053 | 66.7205 | -123.2249 | 122.9542 | 123.1457 | 122.9978 | 66.724 | -123.4846
2524.7969 | 123.1567 | -66.7831 | 56.3644 | -0.0029761 | -0.030649 | -0.00060686 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055254 | 0.040344 | 0.055958 | -66.7381 | -0.012329 | -66.7735 | 56.3251 | 56.2662 | 56.4634 | -66.897 | -66.752 | -0.017956 | -66.7865 | 56.2169 | 56.4084 | 56.2238 | -67.166 | -0.1139 | -0.039348 | 0.04503 | 0.009668 | 0.12357 | -0.098257 | 0.098915 | -0.38284 | -0.14758 | 0.031179 | -0.003327 | 0.37951 | 0.043913 | -0.14061 | 123.1082 | 123.0493 | 123.2465 | 66.7708 | -123.2615 | 123 | 123.1915 | 123.007 | 66.7652 | -123.5304
2525.8594 | 123.1979 | -66.7603 | 56.3507 | 0.0046549 | -0.030863 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055254 | 0.040557 | 0.055958 | -66.7335 | -0.026065 | -66.7643 | 56.3159 | 56.257 | 56.4542 | -66.897 | -66.7611 | -0.013377 | -66.791 | 56.2169 | 56.4175 | 56.2238 | -67.1568 | -0.13679 | -0.034772 | 0.02672 | -0.004064 | 0.13272 | -0.093682 | 0.10349 | -0.39657 | -0.13385 | -0.000867 | -0.030793 | 0.36578 | 0.066803 | -0.12688 | 123.0762 | 123.0173 | 123.2145 | 66.7342 | -123.2477 | 122.9771 | 123.1778 | 122.9841 | 66.7469 | -123.5075
2526.7969 | 123.2208 | -66.7694 | 56.3278 | -0.018238 | -0.031077 | -0.00082046 | 0.053081 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055467 | 0.04013 | 0.055958 | -66.7335 | -0.007751 | -66.7597 | 56.3205 | 56.257 | 56.4588 | -66.897 | -66.7565 | -0.017956 | -66.7956 | 56.2214 | 56.4084 | 56.233 | -67.1614 | -0.12763 | -0.007306 | 0.035875 | 0.009669 | 0.1373 | -0.070794 | 0.13096 | -0.39199 | -0.10638 | 0.012867 | -0.026217 | 0.36578 | 0.080534 | -0.09483 | 123.0899 | 123.0264 | 123.2282 | 66.7617 | -123.2249 | 122.9908 | 123.1778 | 123.0024 | 66.7515 | -123.4892
2527.7969 | 123.175 | -66.8015 | 56.3461 | -0.0029761 | -0.031077 | -0.00082046 | 0.052867 | -0.0073736 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.040344 | 0.056171 | -66.729 | -0.016908 | -66.7735 | 56.3159 | 56.2433 | 56.4634 | -66.9062 | -66.7657 | -0.031692 | -66.7865 | 56.2214 | 56.4129 | 56.2284 | -67.1614 | -0.10475 | -0.030194 | 0.072497 | 0.027979 | 0.13272 | -0.10284 | 0.11723 | -0.35995 | -0.12469 | 0.035754 | 0.014984 | 0.37493 | 0.066802 | -0.11772 | 123.1174 | 123.0447 | 123.2648 | 66.7845 | -123.2523 | 123.0229 | 123.2144 | 123.0299 | 66.7698 | -123.5075
2528.7969 | 123.2208 | -66.7511 | 56.3049 | -0.010607 | -0.030863 | -0.00082046 | 0.053295 | -0.0075872 | 0.062289 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055681 | 0.040344 | 0.055744 | -66.7335 | -0.012329 | -66.7689 | 56.3159 | 56.2524 | 56.4588 | -66.897 | -66.7611 | -0.022535 | -66.7865 | 56.2214 | 56.4129 | 56.2101 | -67.166 | -0.14594 | 0.011004 | 0.017565 | -0.017797 | 0.12814 | -0.052485 | 0.15384 | -0.41488 | -0.083494 | -0.010022 | -0.03537 | 0.37951 | 0.108 | -0.094835 | 123.067 | 123.0035 | 123.2099 | 66.7388 | -123.202 | 122.9725 | 123.164 | 122.9612 | 66.7286 | -123.4709
2529.7969 | 123.2025 | -66.7465 | 56.3232 | 0.0046549 | -0.030863 | -0.00060686 | 0.052654 | -0.0078008 | 0.062717 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055681 | 0.04013 | 0.056171 | -66.7244 | -0.012329 | -66.7735 | 56.3159 | 56.2662 | 56.4588 | -66.9108 | -66.7565 | -0.017956 | -66.791 | 56.2169 | 56.4129 | 56.2605 | -67.166 | -0.16426 | -0.007306 | 0.022144 | -0.026953 | 0.1373 | -0.057058 | 0.13553 | -0.41946 | -0.10638 | -0.010021 | -0.044526 | 0.37493 | 0.08969 | -0.062781 | 123.0625 | 123.0127 | 123.2053 | 66.7342 | -123.234 | 122.9634 | 123.1595 | 123.007 | 66.7286 | -123.4892
2530.7969 | 123.2941 | -66.7236 | 56.3004 | -0.018238 | -0.030649 | -0.00060686 | 0.052867 | -0.0075872 | 0.062717 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055895 | 0.04013 | 0.056171 | -66.729 | -0.016908 | -66.7643 | 56.3159 | 56.2708 | 56.4588 | -66.9062 | -66.752 | -0.027113 | -66.7956 | 56.226 | 56.4175 | 56.2467 | -67.1614 | -0.18256 | 0.015582 | -0.005323 | -0.040685 | 0.14188 | -0.029591 | 0.15842 | -0.43777 | -0.074338 | -0.02833 | -0.071993 | 0.36578 | 0.11716 | -0.053629 | 123.0396 | 122.9944 | 123.1824 | 66.7067 | -123.2066 | 122.9496 | 123.1411 | 122.9704 | 66.6965 | -123.4618
2531.8594 | 123.1796 | -66.7465 | 56.369 | 0.0046549 | -0.031077 | -0.00082046 | 0.053081 | -0.0078008 | 0.062717 | -0.0074779 | -0.0032665 | -0.00034193 | 0.055467 | 0.040344 | 0.055958 | -66.729 | -0.016908 | -66.7826 | 56.3159 | 56.2524 | 56.4588 | -66.897 | -66.752 | -0.017956 | -66.7865 | 56.226 | 56.4175 | 56.2101 | -67.1568 | -0.15052 | -0.053083 | 0.017565 | -0.03611 | 0.11441 | -0.11657 | 0.089758 | -0.4103 | -0.143 | -0.005442 | -0.039948 | 0.37035 | 0.048492 | -0.15892 | 123.0625 | 122.999 | 123.2053 | 66.7296 | -123.2661 | 122.9725 | 123.164 | 122.9566 | 66.7286 | -123.5258
2532.7969 | 123.2758 | -66.7465 | 56.282 | -0.0029761 | -0.030649 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.040344 | 0.056171 | -66.7335 | -0.012329 | -66.7597 | 56.3114 | 56.2524 | 56.4634 | -66.9016 | -66.7611 | -0.022535 | -66.791 | 56.2214 | 56.4129 | 56.2467 | -67.166 | -0.1551 | 0.029315 | 0.012987 | -0.013219 | 0.14188 | -0.029596 | 0.18131 | -0.41946 | -0.060605 | -0.0146 | -0.044526 | 0.37493 | 0.13089 | -0.035318 | 123.0579 | 122.999 | 123.2099 | 66.7342 | -123.1837 | 122.968 | 123.1595 | 122.9932 | 66.724 | -123.448
2533.8594 | 123.1888 | -66.7236 | 56.3599 | -0.0029761 | -0.030649 | -0.00039306 | 0.052867 | -0.0080146 | 0.062717 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.040344 | 0.055958 | -66.729 | -0.021486 | -66.7735 | 56.3114 | 56.2708 | 56.4634 | -66.9016 | -66.752 | -0.022535 | -66.7865 | 56.2214 | 56.4129 | 56.2376 | -67.1614 | -0.17799 | -0.048505 | -0.005323 | -0.049841 | 0.12815 | -0.0891 | 0.10349 | -0.43777 | -0.13842 | -0.02833 | -0.062836 | 0.37493 | 0.053069 | -0.12229 | 123.035 | 122.9944 | 123.187 | 66.7021 | -123.2615 | 122.9451 | 123.1366 | 122.9612 | 66.7011 | -123.5213
2534.7969 | 123.3032 | -66.7374 | 56.3187 | -0.0029761 | -0.030863 | -0.00060686 | 0.053295 | -0.0075872 | 0.062289 | -0.0074779 | -0.0034801 | -0.00034193 | 0.055467 | 0.040344 | 0.056385 | -66.7335 | -0.021486 | -66.7689 | 56.3159 | 56.2616 | 56.4679 | -66.9016 | -66.752 | -0.022535 | -66.7956 | 56.2214 | 56.4084 | 56.2467 | -67.1706 | -0.16425 | -0.002729 | 0.003832 | -0.03153 | 0.13272 | -0.05706 | 0.14927 | -0.43319 | -0.097227 | -0.014597 | -0.05826 | 0.37493 | 0.089689 | -0.07194 | 123.0533 | 122.999 | 123.2053 | 66.7159 | -123.2203 | 122.9588 | 123.1457 | 122.9841 | 66.7148 | -123.4892
2535.7969 | 123.349 | -66.7557 | 56.2729 | -0.0029761 | -0.030863 | -0.00060686 | 0.053295 | -0.0078008 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055681 | 0.040344 | 0.056599 | -66.7335 | -0.012329 | -66.7643 | 56.3068 | 56.2296 | 56.4588 | -66.8925 | -66.7565 | -0.022535 | -66.7865 | 56.2306 | 56.4129 | 56.233 | -67.1614 | -0.13679 | 0.033891 | 0.022142 | -0.008642 | 0.12814 | -0.043336 | 0.18589 | -0.40573 | -0.042293 | -0.000866 | -0.030793 | 0.37493 | 0.14004 | -0.039898 | 123.0625 | 122.9852 | 123.2145 | 66.7433 | -123.1653 | 122.9863 | 123.1686 | 122.9887 | 66.7331 | -123.4343
2536.8594 | 123.2986 | -66.7282 | 56.2775 | -0.0029761 | -0.03129 | -0.00082046 | 0.053295 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055467 | 0.040771 | 0.055958 | -66.729 | -0.016908 | -66.7643 | 56.3159 | 56.2662 | 56.4634 | -66.897 | -66.752 | -0.027113 | -66.7956 | 56.226 | 56.4084 | 56.2238 | -67.166 | -0.16883 | 0.03847 | -0.000746 | -0.036108 | 0.13272 | -0.011282 | 0.18589 | -0.43777 | -0.05145 | -0.023753 | -0.067416 | 0.37036 | 0.13089 | -0.053634 | 123.0441 | 122.9944 | 123.1916 | 66.7113 | -123.1745 | 122.9542 | 123.1366 | 122.952 | 66.7011 | -123.4434
2537.7969 | 123.2666 | -66.7328 | 56.3095 | -0.0029761 | -0.03129 | -0.00039306 | 0.053081 | -0.0078008 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055467 | 0.040344 | 0.055744 | -66.7381 | -0.021486 | -66.7781 | 56.3114 | 56.2433 | 56.4542 | -66.897 | -66.7611 | -0.022535 | -66.791 | 56.2214 | 56.4175 | 56.2238 | -67.166 | -0.16425 | 0.001849 | -0.005324 | -0.045265 | 0.11899 | -0.06622 | 0.14469 | -0.43319 | -0.088071 | -0.028333 | -0.058259 | 0.37493 | 0.108 | -0.085677 | 123.0441 | 122.9761 | 123.187 | 66.7113 | -123.2065 | 122.9542 | 123.1503 | 122.9566 | 66.7103 | -123.4755
2538.8594 | 123.2666 | -66.7328 | 56.3004 | -0.0029761 | -0.031077 | -0.00060686 | 0.053508 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.040344 | 0.056171 | -66.7381 | -0.016908 | -66.7689 | 56.3205 | 56.2662 | 56.4588 | -66.9062 | -66.7565 | -0.017956 | -66.7819 | 56.2306 | 56.4129 | 56.2605 | -67.1614 | -0.17341 | 0.02016 | -0.005324 | -0.036108 | 0.1373 | -0.03417 | 0.15842 | -0.42861 | -0.069759 | -0.023754 | -0.049102 | 0.37951 | 0.11258 | -0.039893 | 123.0533 | 122.999 | 123.1916 | 66.7159 | -123.2066 | 122.9634 | 123.1457 | 122.9932 | 66.7148 | -123.4618
2539.7969 | 123.2346 | -66.7282 | 56.3278 | -0.0029761 | -0.03129 | -0.00082046 | 0.053508 | -0.0075872 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055467 | 0.040771 | 0.055744 | -66.7335 | -0.016908 | -66.7689 | 56.3159 | 56.2524 | 56.4634 | -66.897 | -66.7565 | -0.031692 | -66.7865 | 56.226 | 56.4129 | 56.2605 | -67.1706 | -0.16883 | -0.011884 | -0.005324 | -0.040686 | 0.12814 | -0.075373 | 0.13554 | -0.44235 | -0.1018 | -0.028332 | -0.058259 | 0.38409 | 0.085112 | -0.067359 | 123.0441 | 122.9807 | 123.1916 | 66.7113 | -123.2249 | 122.9542 | 123.1411 | 122.9887 | 66.6965 | -123.4984
2540.8594 | 123.2071 | -66.7511 | 56.369 | 0.0046549 | -0.03129 | -0.00082046 | 0.052867 | -0.0080146 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055681 | 0.040344 | 0.055958 | -66.7244 | -0.012329 | -66.7643 | 56.3205 | 56.2616 | 56.4679 | -66.9062 | -66.7565 | -0.017956 | -66.791 | 56.2306 | 56.4129 | 56.233 | -67.1706 | -0.1551 | -0.048505 | 0.026722 | -0.013219 | 0.14188 | -0.10741 | 0.098915 | -0.41946 | -0.13842 | -0.005443 | -0.039948 | 0.37951 | 0.043913 | -0.13603 | 123.0716 | 123.0127 | 123.219 | 66.7388 | -123.2752 | 122.9817 | 123.164 | 122.9841 | 66.7331 | -123.5396
2541.7969 | 123.2346 | -66.7557 | 56.3141 | 0.012286 | -0.031077 | -0.00060686 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055895 | 0.040557 | 0.055744 | -66.7381 | -0.021486 | -66.7735 | 56.3068 | 56.2524 | 56.4588 | -66.9062 | -66.752 | -0.022535 | -66.7865 | 56.226 | 56.4129 | 56.2284 | -67.1568 | -0.15052 | -0.007308 | 0.017564 | -0.017798 | 0.13272 | -0.06164 | 0.14469 | -0.40115 | -0.088071 | 0.003713 | -0.030793 | 0.37035 | 0.098845 | -0.085676 | 123.0625 | 123.0081 | 123.2145 | 66.7342 | -123.2203 | 122.9817 | 123.1686 | 122.9841 | 66.7331 | -123.4709
2542.7969 | 123.2941 | -66.7282 | 56.337 | -0.0029761 | -0.03129 | -0.00039306 | 0.053295 | -0.0075872 | 0.062503 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055467 | 0.039916 | 0.056171 | -66.7335 | -0.012329 | -66.7552 | 56.3114 | 56.257 | 56.4634 | -66.8925 | -66.7565 | -0.022535 | -66.791 | 56.226 | 56.4129 | 56.2467 | -67.1614 | -0.16425 | -0.025617 | -0.005324 | -0.026951 | 0.1373 | -0.079949 | 0.12638 | -0.43319 | -0.11096 | -0.028332 | -0.062837 | 0.37035 | 0.075957 | -0.09025 | 123.0396 | 122.9852 | 123.1916 | 66.7159 | -123.2294 | 122.9542 | 123.1411 | 122.9749 | 66.7057 | -123.4984
2543.7969 | 123.3215 | -66.7236 | 56.337 | 0.012286 | -0.031077 | -0.00082046 | 0.053081 | -0.0080146 | 0.062289 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055681 | 0.04013 | 0.055958 | -66.729 | -0.016908 | -66.7643 | 56.3159 | 56.2524 | 56.4634 | -66.897 | -66.7565 | -0.022535 | -66.7865 | 56.2123 | 56.4129 | 56.2421 | -67.166 | -0.17341 | -0.021039 | -0.005323 | -0.040685 | 0.13272 | -0.084528 | 0.12638 | -0.44235 | -0.12469 | -0.032909 | -0.062836 | 0.37951 | 0.075957 | -0.094828 | 123.0396 | 122.9761 | 123.187 | 66.7067 | -123.234 | 122.9359 | 123.1366 | 122.9658 | 66.7011 | -123.503
2544.8594 | 123.3124 | -66.7236 | 56.3141 | -0.018238 | -0.030863 | -0.00039306 | 0.053295 | -0.0073736 | 0.062503 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055254 | 0.040771 | 0.055958 | -66.7381 | -0.026065 | -66.7643 | 56.3114 | 56.2708 | 56.4634 | -66.8925 | -66.752 | -0.022535 | -66.7865 | 56.2306 | 56.4084 | 56.2238 | -67.1706 | -0.16883 | -0.002729 | -0.014479 | -0.040685 | 0.12814 | -0.043324 | 0.14927 | -0.44693 | -0.083492 | -0.02833 | -0.062836 | 0.38409 | 0.094267 | -0.090255 | 123.035 | 122.9944 | 123.187 | 66.6976 | -123.2065 | 122.9542 | 123.132 | 122.9475 | 66.7011 | -123.4846
2545.7969 | 123.2895 | -66.7374 | 56.3324 | 0.0046549 | -0.030863 | -0.00060686 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055681 | 0.040557 | 0.055744 | -66.7335 | -0.012329 | -66.7689 | 56.3159 | 56.2524 | 56.4634 | -66.9016 | -66.7565 | -0.027113 | -66.7865 | 56.226 | 56.4084 | 56.2284 | -67.1614 | -0.16425 | -0.016461 | 0.003832 | -0.03153 | 0.13272 | -0.07995 | 0.13096 | -0.42404 | -0.10638 | -0.019176 | -0.049103 | 0.37493 | 0.075957 | -0.10399 | 123.0533 | 122.9898 | 123.2007 | 66.725 | -123.234 | 122.9634 | 123.1457 | 122.9658 | 66.7103 | -123.4938
2546.7969 | 123.2849 | -66.7053 | 56.3507 | -0.0029761 | -0.03129 | -0.00060686 | 0.053081 | -0.0080146 | 0.062717 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.040344 | 0.055958 | -66.729 | -0.021486 | -66.7643 | 56.3205 | 56.2708 | 56.4634 | -66.9016 | -66.752 | -0.027113 | -66.7956 | 56.2214 | 56.4129 | 56.2193 | -67.1568 | -0.1963 | -0.030194 | -0.023634 | -0.058996 | 0.1373 | -0.079945 | 0.11265 | -0.4515 | -0.12927 | -0.046641 | -0.090304 | 0.3612 | 0.062224 | -0.13145 | 123.0258 | 122.9761 | 123.1687 | 66.6838 | -123.2523 | 122.9268 | 123.1183 | 122.9246 | 66.6782 | -123.5075
2547.7969 | 123.3307 | -66.7282 | 56.3324 | -0.010607 | -0.031077 | -0.00039306 | 0.053295 | -0.0078008 | 0.062503 | 0.0077831 | -0.0034801 | -0.00055553 | 0.05504 | 0.040344 | 0.055744 | -66.729 | -0.026065 | -66.7643 | 56.3205 | 56.2616 | 56.4588 | -66.8879 | -66.7474 | -0.022535 | -66.7819 | 56.226 | 56.4175 | 56.2467 | -67.1614 | -0.15967 | -0.011883 | -0.000746 | -0.036108 | 0.12356 | -0.070792 | 0.12638 | -0.43319 | -0.10638 | -0.019175 | -0.05368 | 0.37951 | 0.085114 | -0.085672 | 123.0487 | 122.9898 | 123.187 | 66.7021 | -123.2203 | 122.9542 | 123.1457 | 122.9749 | 66.7057 | -123.4938
2548.7969 | 123.2574 | -66.7145 | 56.3507 | -0.010607 | -0.031077 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055467 | 0.04013 | 0.056171 | -66.7335 | -0.016908 | -66.7597 | 56.3159 | 56.2662 | 56.4679 | -66.897 | -66.752 | -0.022535 | -66.791 | 56.226 | 56.4084 | 56.2513 | -67.1614 | -0.18256 | -0.034772 | -0.019056 | -0.045262 | 0.1373 | -0.084524 | 0.11723 | -0.44692 | -0.12469 | -0.037485 | -0.076569 | 0.37035 | 0.057646 | -0.099404 | 123.0304 | 122.9807 | 123.1824 | 66.6976 | -123.2477 | 122.9405 | 123.1228 | 122.9658 | 66.6919 | -123.5121
2549.8594 | 123.1613 | -66.7786 | 56.3324 | -0.0029761 | -0.03129 | -0.00082046 | 0.053295 | -0.0080146 | 0.062503 | -0.015108 | -0.0034801 | -0.00034193 | 0.055467 | 0.040344 | 0.055958 | -66.7381 | -0.026065 | -66.7597 | 56.3159 | 56.2662 | 56.4679 | -66.9016 | -66.7428 | -0.027113 | -66.7956 | 56.2214 | 56.4129 | 56.2513 | -67.166 | -0.12305 | -0.016461 | 0.040452 | 0.018824 | 0.14188 | -0.066213 | 0.13554 | -0.38742 | -0.11096 | 0.035758 | -0.017062 | 0.37036 | 0.080535 | -0.081093 | 123.0945 | 123.0447 | 123.2465 | 66.7525 | -123.234 | 123 | 123.1915 | 123.0299 | 66.7515 | -123.4984
2550.7969 | 123.1842 | -66.7603 | 56.3644 | -0.010607 | -0.031077 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.015414 | -0.0036937 | -0.00034193 | 0.055681 | 0.040557 | 0.055958 | -66.7381 | -0.012329 | -66.7689 | 56.3205 | 56.2616 | 56.4588 | -66.897 | -66.7474 | -0.027113 | -66.791 | 56.2169 | 56.4038 | 56.2696 | -67.1614 | -0.13679 | -0.043927 | 0.022142 | -0.008642 | 0.12814 | -0.10284 | 0.094336 | -0.40115 | -0.14758 | 0.012869 | -0.030793 | 0.37035 | 0.039334 | -0.094823 | 123.0808 | 123.0219 | 123.219 | 66.7479 | -123.2615 | 122.9771 | 123.164 | 123.0299 | 66.7331 | -123.5258
2551.7969 | 123.3124 | -66.7099 | 56.3324 | -0.010607 | -0.030863 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.015414 | -0.0034801 | -0.00055553 | 0.055467 | 0.040557 | 0.055744 | -66.729 | -0.026065 | -66.7689 | 56.3205 | 56.2616 | 56.4634 | -66.897 | -66.7474 | -0.031692 | -66.7865 | 56.2214 | 56.4129 | 56.2376 | -67.1614 | -0.18714 | -0.011883 | -0.019056 | -0.058996 | 0.12814 | -0.070792 | 0.13096 | -0.4515 | -0.11096 | -0.037485 | -0.076569 | 0.37493 | 0.080535 | -0.094829 | 123.0304 | 122.9715 | 123.1733 | 66.6838 | -123.2294 | 122.9313 | 123.1228 | 122.9475 | 66.6782 | -123.4938
2552.7969 | 123.1796 | -66.7603 | 56.3965 | -0.0029761 | -0.031504 | -0.00039306 | 0.053081 | -0.0078008 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.04013 | 0.055958 | -66.7335 | -0.016908 | -66.7689 | 56.3159 | 56.257 | 56.4634 | -66.897 | -66.7428 | -0.031692 | -66.7865 | 56.2214 | 56.4038 | 56.2559 | -67.1614 | -0.13679 | -0.080548 | 0.02672 | -0.008642 | 0.12814 | -0.13946 | 0.066872 | -0.40115 | -0.17505 | 0.017448 | -0.026215 | 0.37493 | 0.007291 | -0.1406 | 123.0762 | 123.0173 | 123.2236 | 66.7433 | -123.2935 | 122.9817 | 123.164 | 123.0161 | 66.7286 | -123.5579
2553.7969 | 123.2712 | -66.7099 | 56.3324 | 0.012286 | -0.03129 | -0.00082046 | 0.053508 | -0.0080146 | 0.062503 | 0.023044 | -0.0034801 | -0.00012813 | 0.055467 | 0.040344 | 0.056171 | -66.729 | -0.026065 | -66.7689 | 56.3205 | 56.2753 | 56.4634 | -66.9016 | -66.7565 | -0.022535 | -66.7865 | 56.226 | 56.4175 | 56.2376 | -67.1614 | -0.19172 | -0.011883 | -0.019056 | -0.058996 | 0.13272 | -0.057055 | 0.13096 | -0.4515 | -0.10638 | -0.046642 | -0.076569 | 0.37493 | 0.085114 | -0.094829 | 123.0304 | 122.9852 | 123.1733 | 66.6838 | -123.234 | 122.9359 | 123.1274 | 122.9475 | 66.6874 | -123.4938
2554.8594 | 123.2666 | -66.7145 | 56.3141 | -0.0029761 | -0.031077 | -0.00060686 | 0.053722 | -0.0075872 | 0.062076 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.040557 | 0.055531 | -66.7381 | -0.021486 | -66.7643 | 56.3114 | 56.2708 | 56.4679 | -66.897 | -66.752 | -0.031692 | -66.7819 | 56.2214 | 56.4175 | 56.2421 | -67.166 | -0.18256 | -0.002729 | -0.023634 | -0.04984 | 0.13272 | -0.043324 | 0.15385 | -0.4515 | -0.092649 | -0.037485 | -0.067412 | 0.38409 | 0.10342 | -0.07194 | 123.0258 | 122.9852 | 123.1824 | 66.693 | -123.2111 | 122.9359 | 123.132 | 122.9566 | 66.6828 | -123.4801
2555.7969 | 123.381 | -66.6733 | 56.3873 | -0.0029761 | -0.031077 | -0.00082046 | 0.053081 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055254 | 0.040985 | 0.055744 | -66.729 | -0.021486 | -66.7689 | 56.3159 | 56.2708 | 56.4679 | -66.9016 | -66.752 | -0.027113 | -66.7865 | 56.2306 | 56.4175 | 56.2238 | -67.1614 | -0.22834 | -0.071393 | -0.055677 | -0.095617 | 0.13272 | -0.11657 | 0.080605 | -0.48812 | -0.15673 | -0.078684 | -0.11319 | 0.37493 | 0.030182 | -0.1635 | 122.9892 | 122.944 | 123.1412 | 66.6518 | -123.2889 | 122.9039 | 123.0908 | 122.8971 | 66.6462 | -123.5487
2556.7969 | 123.175 | -66.7374 | 56.3644 | -0.0029761 | -0.03129 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | 0.0077831 | -0.0036937 | -0.00034193 | 0.055254 | 0.040344 | 0.055958 | -66.7335 | -0.026065 | -66.7689 | 56.3205 | 56.2524 | 56.4634 | -66.9062 | -66.7565 | -0.022535 | -66.7865 | 56.2214 | 56.4175 | 56.2376 | -67.166 | -0.16883 | -0.043927 | 0.003832 | -0.03153 | 0.1373 | -0.11199 | 0.098915 | -0.42862 | -0.143 | -0.019176 | -0.049103 | 0.37951 | 0.05307 | -0.12687 | 123.0579 | 122.9898 | 123.2007 | 66.7113 | -123.2706 | 122.9588 | 123.1549 | 122.9749 | 66.7148 | -123.5304
2557.7969 | 123.2254 | -66.7236 | 56.3507 | -0.010607 | -0.031504 | -0.00060686 | 0.053081 | -0.0075872 | 0.062717 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055254 | 0.040344 | 0.056171 | -66.7335 | -0.026065 | -66.7689 | 56.3205 | 56.2616 | 56.4679 | -66.9016 | -66.752 | -0.022535 | -66.791 | 56.226 | 56.4221 | 56.2193 | -67.166 | -0.17799 | -0.030194 | -0.009901 | -0.045263 | 0.13272 | -0.089103 | 0.11723 | -0.44235 | -0.12469 | -0.02833 | -0.067414 | 0.37493 | 0.071382 | -0.13145 | 123.0441 | 122.9852 | 123.1916 | 66.6976 | -123.2523 | 122.9496 | 123.1457 | 122.9429 | 66.7011 | -123.5167
2558.8594 | 123.3032 | -66.6962 | 56.3232 | -0.0029761 | -0.031504 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.015414 | -0.0032665 | -0.00055553 | 0.055895 | 0.040771 | 0.055958 | -66.7335 | -0.021486 | -66.7597 | 56.3205 | 56.2662 | 56.4634 | -66.897 | -66.7565 | -0.027113 | -66.7956 | 56.2306 | 56.4221 | 56.2284 | -67.1614 | -0.20087 | -0.002728 | -0.037367 | -0.063573 | 0.1373 | -0.057058 | 0.14011 | -0.46523 | -0.092647 | -0.060375 | -0.099459 | 0.36578 | 0.098848 | -0.094831 | 123.0167 | 122.9624 | 123.1595 | 66.6747 | -123.2203 | 122.9268 | 123.1183 | 122.9246 | 66.6691 | -123.4846
2559.7969 | 123.2162 | -66.7191 | 56.3828 | 0.0046549 | -0.031077 | -0.00039306 | 0.053081 | -0.0078008 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055254 | 0.040771 | 0.055958 | -66.7335 | -0.021486 | -66.7597 | 56.3114 | 56.2524 | 56.4679 | -66.9062 | -66.7565 | -0.027113 | -66.7865 | 56.2214 | 56.4175 | 56.2467 | -67.1614 | -0.18714 | -0.071393 | -0.014479 | -0.040685 | 0.14646 | -0.1303 | 0.085183 | -0.44235 | -0.16131 | -0.037487 | -0.067414 | 0.37493 | 0.03476 | -0.13603 | 123.0304 | 122.9715 | 123.187 | 66.6976 | -123.2889 | 122.9405 | 123.1366 | 122.9658 | 66.6919 | -123.5442
2560.7969 | 123.2254 | -66.7603 | 56.3416 | -0.0029761 | -0.031504 | -0.00082046 | 0.052867 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055681 | 0.040557 | 0.055958 | -66.7335 | -0.021486 | -66.7597 | 56.3159 | 56.257 | 56.4634 | -66.9016 | -66.752 | -0.027113 | -66.7865 | 56.226 | 56.4175 | 56.2788 | -67.166 | -0.14136 | -0.025617 | 0.02672 | 0.000514 | 0.14188 | -0.084527 | 0.1218 | -0.40573 | -0.11554 | 0.008291 | -0.026215 | 0.37951 | 0.075958 | -0.062777 | 123.0762 | 123.0173 | 123.2236 | 66.7388 | -123.2432 | 122.9863 | 123.1778 | 123.039 | 66.7331 | -123.5075
2561.8594 | 123.2986 | -66.7145 | 56.3049 | 0.012286 | -0.03129 | -0.00060686 | 0.053081 | -0.0078008 | 0.062503 | 0.015414 | -0.0032665 | -0.00034193 | 0.055681 | 0.040557 | 0.055958 | -66.7335 | -0.030644 | -66.7643 | 56.3159 | 56.2708 | 56.4725 | -66.9016 | -66.752 | -0.031692 | -66.7865 | 56.2214 | 56.4038 | 56.2147 | -67.1614 | -0.18714 | 0.011004 | -0.019056 | -0.04984 | 0.1373 | -0.034169 | 0.16758 | -0.44692 | -0.083494 | -0.037485 | -0.071991 | 0.37493 | 0.098843 | -0.090257 | 123.0304 | 122.9852 | 123.187 | 66.6838 | -123.2066 | 122.9359 | 123.1183 | 122.9292 | 66.6828 | -123.4663
2562.7969 | 123.2208 | -66.7465 | 56.369 | -0.010607 | -0.031504 | -0.00060686 | 0.052867 | -0.0082282 | 0.06293 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.040557 | 0.055958 | -66.729 | -0.021486 | -66.7689 | 56.3205 | 56.2662 | 56.4634 | -66.897 | -66.7611 | -0.031692 | -66.7865 | 56.2306 | 56.4038 | 56.2467 | -67.1614 | -0.15052 | -0.048505 | 0.017565 | -0.022375 | 0.12814 | -0.10283 | 0.094337 | -0.41488 | -0.13842 | -0.0146 | -0.039948 | 0.37493 | 0.034756 | -0.12229 | 123.067 | 123.0127 | 123.2099 | 66.725 | -123.2661 | 122.9771 | 123.1503 | 122.9932 | 66.7148 | -123.5304
2563.8594 | 123.2895 | -66.7191 | 56.3324 | -0.010607 | -0.031504 | -0.00039306 | 0.052867 | -0.0080146 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055254 | 0.040557 | 0.056171 | -66.7335 | -0.030644 | -66.7735 | 56.3068 | 56.257 | 56.4588 | -66.897 | -66.7565 | -0.027113 | -66.791 | 56.2306 | 56.4129 | 56.2513 | -67.1706 | -0.17799 | -0.025618 | -0.014479 | -0.054419 | 0.12357 | -0.075371 | 0.12638 | -0.4515 | -0.1018 | -0.037487 | -0.071992 | 0.37951 | 0.080535 | -0.081093 | 123.0258 | 122.9761 | 123.1778 | 66.6884 | -123.2294 | 122.9496 | 123.132 | 122.9704 | 66.6919 | -123.503
2564.7969 | 123.1934 | -66.7694 | 56.3461 | 0.0046549 | -0.031504 | -0.00082046 | 0.053081 | -0.0078008 | 0.062076 | 0.015414 | -0.0034801 | -0.00012813 | 0.055681 | 0.040344 | 0.055958 | -66.7244 | -0.026065 | -66.7597 | 56.3297 | 56.2616 | 56.4679 | -66.9016 | -66.7611 | -0.027113 | -66.791 | 56.2169 | 56.4129 | 56.2788 | -67.1568 | -0.13221 | -0.016459 | 0.045032 | 0.009669 | 0.14188 | -0.084525 | 0.1218 | -0.38741 | -0.12927 | 0.008288 | -0.021638 | 0.36578 | 0.066802 | -0.067354 | 123.0991 | 123.031 | 123.2373 | 66.7433 | -123.2477 | 122.9863 | 123.1823 | 123.0482 | 66.7423 | -123.503
2565.7969 | 123.2437 | -66.7603 | 56.3461 | -0.010607 | -0.03129 | -0.00039306 | 0.052867 | -0.0080146 | 0.062503 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055467 | 0.040771 | 0.055958 | -66.729 | -0.030644 | -66.7643 | 56.3205 | 56.2753 | 56.4679 | -66.9016 | -66.7565 | -0.027113 | -66.791 | 56.226 | 56.4221 | 56.2513 | -67.166 | -0.14136 | -0.025616 | 0.031298 | -0.004064 | 0.1373 | -0.070788 | 0.1218 | -0.40573 | -0.12011 | 0.003712 | -0.030793 | 0.37493 | 0.07596 | -0.094826 | 123.0808 | 123.0356 | 123.2282 | 66.7296 | -123.2477 | 122.9863 | 123.1823 | 123.0116 | 66.7331 | -123.5121
2566.7969 | 123.1659 | -66.7648 | 56.3278 | -0.0029761 | -0.031504 | -0.00060686 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055254 | 0.040985 | 0.055958 | -66.7335 | -0.026065 | -66.7689 | 56.3205 | 56.2616 | 56.4679 | -66.897 | -66.752 | -0.027113 | -66.7865 | 56.226 | 56.4084 | 56.2467 | -67.1751 | -0.13221 | -0.007306 | 0.031298 | -0.004064 | 0.12814 | -0.066215 | 0.14011 | -0.41031 | -0.1018 | 0.012869 | -0.021637 | 0.38867 | 0.080534 | -0.081095 | 123.0853 | 123.0264 | 123.2328 | 66.7388 | -123.2249 | 122.9908 | 123.1732 | 123.0116 | 66.7377 | -123.503
2567.7969 | 123.2025 | -66.7648 | 56.3507 | 0.012286 | -0.031718 | -0.00039306 | 0.053081 | -0.0078008 | 0.062717 | -0.0074779 | -0.0034801 | -0.00034193 | 0.055467 | 0.040771 | 0.055744 | -66.7381 | -0.026065 | -66.7597 | 56.3159 | 56.2616 | 56.4725 | -66.9016 | -66.7565 | -0.027113 | -66.7865 | 56.2306 | 56.4221 | 56.233 | -67.1568 | -0.13679 | -0.034772 | 0.02672 | 0.005092 | 0.14188 | -0.089103 | 0.12181 | -0.39199 | -0.12011 | 0.00829 | -0.021637 | 0.37035 | 0.071382 | -0.11772 | 123.0808 | 123.0264 | 123.2373 | 66.7388 | -123.2523 | 122.9954 | 123.1869 | 122.9978 | 66.7377 | -123.5075
2568.8594 | 123.1979 | -66.7557 | 56.3599 | -0.010607 | -0.031931 | -0.00082046 | 0.053508 | -0.0082282 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055254 | 0.040985 | 0.056171 | -66.7335 | -0.026065 | -66.7689 | 56.3159 | 56.2616 | 56.4679 | -66.9062 | -66.7565 | -0.031692 | -66.7865 | 56.2214 | 56.4175 | 56.2421 | -67.1706 | -0.15052 | -0.043927 | 0.022142 | -0.01322 | 0.1373 | -0.098258 | 0.10807 | -0.41488 | -0.13842 | -0.000866 | -0.030793 | 0.38409 | 0.057648 | -0.11772 | 123.0716 | 123.0173 | 123.2236 | 66.7296 | -123.2661 | 122.9771 | 123.1732 | 122.9978 | 66.724 | -123.5304
2569.7969 | 123.1979 | -66.7374 | 56.3278 | 0.0046549 | -0.03129 | -0.00039306 | 0.053081 | -0.0078008 | 0.062503 | 0.015414 | -0.0032665 | -0.00034193 | 0.055467 | 0.040557 | 0.056171 | -66.7335 | -0.026065 | -66.7689 | 56.3159 | 56.2616 | 56.4771 | -66.9016 | -66.7565 | -0.027113 | -66.7865 | 56.2352 | 56.4175 | 56.2421 | -67.166 | -0.16425 | -0.011884 | 0.003832 | -0.03153 | 0.13272 | -0.066215 | 0.14927 | -0.42862 | -0.092647 | -0.019176 | -0.049103 | 0.37951 | 0.089691 | -0.085673 | 123.0533 | 122.999 | 123.2145 | 66.7113 | -123.2294 | 122.9725 | 123.1549 | 122.9795 | 66.7103 | -123.4938
2570.7969 | 123.2208 | -66.7465 | 56.3187 | -0.010607 | -0.031504 | -0.00060686 | 0.053081 | -0.0080146 | 0.062717 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055681 | 0.040557 | 0.055744 | -66.729 | -0.021486 | -66.7735 | 56.3159 | 56.2708 | 56.4588 | -66.9062 | -66.7565 | -0.031692 | -66.7865 | 56.226 | 56.4175 | 56.2284 | -67.1568 | -0.15968 | -0.002729 | 0.017565 | -0.026953 | 0.13272 | -0.047902 | 0.14011 | -0.4103 | -0.092649 | -0.010021 | -0.039948 | 0.37035 | 0.098846 | -0.090254 | 123.0625 | 123.0173 | 123.2053 | 66.725 | -123.2249 | 122.9725 | 123.164 | 122.9749 | 66.7148 | -123.4755
2571.8594 | 123.1842 | -66.7282 | 56.369 | 0.0046549 | -0.031504 | -0.00082046 | 0.053295 | -0.0080146 | 0.062717 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055681 | 0.040985 | 0.055744 | -66.7335 | -0.021486 | -66.7643 | 56.3251 | 56.2708 | 56.4679 | -66.9016 | -66.7565 | -0.027113 | -66.7956 | 56.2306 | 56.4129 | 56.2513 | -67.166 | -0.17341 | -0.043926 | -0.005324 | -0.036108 | 0.1373 | -0.098256 | 0.098915 | -0.43777 | -0.13842 | -0.028332 | -0.067416 | 0.37036 | 0.043913 | -0.11772 | 123.0533 | 122.999 | 123.1961 | 66.7067 | -123.2706 | 122.9588 | 123.1411 | 122.9795 | 66.7011 | -123.535
2572.7969 | 123.2941 | -66.7465 | 56.2958 | 0.0046549 | -0.031504 | -0.0010343 | 0.053295 | -0.0080146 | 0.062289 | -0.0074779 | -0.0036937 | -0.00076913 | 0.055467 | 0.040344 | 0.055958 | -66.7335 | -0.026065 | -66.7597 | 56.3159 | 56.2479 | 56.4634 | -66.8925 | -66.7565 | -0.027113 | -66.7865 | 56.226 | 56.4221 | 56.2376 | -67.1614 | -0.14594 | 0.02016 | 0.012987 | -0.013219 | 0.13272 | -0.047908 | 0.16758 | -0.41488 | -0.06976 | -0.010021 | -0.039948 | 0.37493 | 0.12631 | -0.058208 | 123.0625 | 122.9944 | 123.2099 | 66.7205 | -123.1882 | 122.9725 | 123.1686 | 122.9841 | 66.7194 | -123.4572
2573.7969 | 123.1979 | -66.7557 | 56.3232 | -0.010607 | -0.031504 | -0.00017946 | 0.053295 | -0.0082282 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055681 | 0.040771 | 0.055744 | -66.7335 | -0.026065 | -66.7643 | 56.3159 | 56.2662 | 56.4634 | -66.897 | -66.752 | -0.031692 | -66.791 | 56.226 | 56.4175 | 56.2513 | -67.1614 | -0.14136 | -0.007306 | 0.022142 | -0.008642 | 0.13272 | -0.057058 | 0.14011 | -0.40573 | -0.097226 | 0.003713 | -0.035371 | 0.37035 | 0.094269 | -0.071938 | 123.0716 | 123.0219 | 123.219 | 66.7296 | -123.2203 | 122.9817 | 123.1732 | 123.007 | 66.724 | -123.4846
2574.7969 | 123.2895 | -66.7282 | 56.2729 | 0.0046549 | -0.031504 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.040557 | 0.055744 | -66.729 | -0.026065 | -66.7689 | 56.3205 | 56.2616 | 56.4634 | -66.9016 | -66.752 | -0.031692 | -66.7865 | 56.2352 | 56.4129 | 56.265 | -67.166 | -0.17341 | 0.047626 | -0.000746 | -0.040686 | 0.13272 | -0.011283 | 0.19047 | -0.43777 | -0.037715 | -0.023753 | -0.058259 | 0.37951 | 0.14004 | -0.007848 | 123.0487 | 122.9898 | 123.1916 | 66.7021 | -123.1745 | 122.9634 | 123.1411 | 122.9933 | 66.6965 | -123.4389
2575.7969 | 123.2437 | -66.7282 | 56.3004 | -0.0029761 | -0.031718 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00076913 | 0.055467 | 0.040344 | 0.055958 | -66.729 | -0.026065 | -66.7689 | 56.3251 | 56.2799 | 56.4634 | -66.897 | -66.7565 | -0.031692 | -66.791 | 56.226 | 56.4221 | 56.233 | -67.1614 | -0.16883 | 0.024739 | -0.000746 | -0.040686 | 0.12814 | -0.020433 | 0.163 | -0.43319 | -0.074338 | -0.028332 | -0.062837 | 0.37035 | 0.12174 | -0.067364 | 123.0533 | 123.0081 | 123.1916 | 66.7021 | -123.1974 | 122.9542 | 123.1503 | 122.9612 | 66.6965 | -123.4618
2576.7969 | 123.2712 | -66.7282 | 56.3141 | 0.0046549 | -0.031931 | -0.00060686 | 0.052867 | -0.0075872 | 0.062503 | 0.0077831 | -0.0032665 | -0.00034193 | 0.055254 | 0.040771 | 0.055958 | -66.7381 | -0.021486 | -66.7643 | 56.3159 | 56.2662 | 56.4634 | -66.9062 | -66.7565 | -0.027113 | -66.791 | 56.226 | 56.4129 | 56.2788 | -67.166 | -0.17799 | 0.001849 | -0.009902 | -0.036108 | 0.14188 | -0.047903 | 0.14927 | -0.43777 | -0.088071 | -0.028332 | -0.062837 | 0.37493 | 0.098845 | -0.035311 | 123.0441 | 122.9944 | 123.1916 | 66.7067 | -123.2203 | 122.9542 | 123.1411 | 123.007 | 66.7011 | -123.4801
2577.7969 | 123.3032 | -66.7282 | 56.3095 | -0.010607 | -0.03129 | -0.00060686 | 0.053295 | -0.0080146 | 0.062289 | -0.0074779 | -0.0034801 | -0.00012813 | 0.055254 | 0.040557 | 0.056171 | -66.7335 | -0.026065 | -66.7597 | 56.3205 | 56.2479 | 56.4634 | -66.8925 | -66.7474 | -0.027113 | -66.791 | 56.226 | 56.4129 | 56.2376 | -67.1568 | -0.16425 | 0.011005 | -0.005324 | -0.03153 | 0.13272 | -0.061641 | 0.15385 | -0.42861 | -0.083493 | -0.019175 | -0.062837 | 0.36578 | 0.10342 | -0.071941 | 123.0487 | 122.9761 | 123.1916 | 66.7021 | -123.202 | 122.9542 | 123.1411 | 122.9658 | 66.7011 | -123.4663
2578.8594 | 123.2025 | -66.7877 | 56.3599 | -0.018238 | -0.031504 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | -0.0074779 | -0.0036937 | -0.00012813 | 0.055254 | 0.040771 | 0.055958 | -66.7244 | -0.026065 | -66.7643 | 56.3205 | 56.2662 | 56.4817 | -66.9016 | -66.7565 | -0.022535 | -66.7819 | 56.2214 | 56.4175 | 56.2559 | -67.1614 | -0.1139 | -0.039349 | 0.063343 | 0.023402 | 0.1373 | -0.093679 | 0.12181 | -0.37368 | -0.13842 | 0.031178 | 0.00583 | 0.37951 | 0.057648 | -0.10398 | 123.1082 | 123.0539 | 123.2694 | 66.7617 | -123.2615 | 123.0092 | 123.2052 | 123.0436 | 66.7652 | -123.5213
2579.7969 | 123.2986 | -66.7511 | 56.3049 | -0.0029761 | -0.03129 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.041198 | 0.055744 | -66.7381 | -0.026065 | -66.7735 | 56.3159 | 56.257 | 56.4634 | -66.9016 | -66.7565 | -0.031692 | -66.7865 | 56.2306 | 56.4084 | 56.2513 | -67.1568 | -0.15052 | 0.011004 | 0.012987 | -0.022375 | 0.12815 | -0.047906 | 0.15842 | -0.40572 | -0.074337 | -0.005443 | -0.03537 | 0.37035 | 0.10342 | -0.053628 | 123.067 | 123.0081 | 123.2145 | 66.725 | -123.2066 | 122.9817 | 123.1595 | 123.0024 | 66.7194 | -123.4618
2580.7969 | 123.262 | -66.7465 | 56.3232 | 0.012286 | -0.031718 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055895 | 0.040557 | 0.056171 | -66.7427 | -0.030644 | -66.7643 | 56.3205 | 56.2616 | 56.4634 | -66.8925 | -66.7565 | -0.036271 | -66.7819 | 56.226 | 56.4129 | 56.2421 | -67.1614 | -0.14594 | -0.002728 | 0.00383 | -0.017797 | 0.12814 | -0.061637 | 0.14011 | -0.41488 | -0.097226 | -0.010021 | -0.035369 | 0.37951 | 0.08969 | -0.081095 | 123.067 | 123.0081 | 123.2099 | 66.7159 | -123.2157 | 122.9725 | 123.1595 | 122.9887 | 66.7103 | -123.4846
2581.8594 | 123.23 | -66.7099 | 56.3278 | -0.0029761 | -0.031718 | -0.00060686 | 0.053508 | -0.0078008 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055467 | 0.040985 | 0.055744 | -66.729 | -0.021486 | -66.7689 | 56.3159 | 56.2616 | 56.4679 | -66.9016 | -66.7474 | -0.031692 | -66.791 | 56.2214 | 56.4175 | 56.2467 | -67.1614 | -0.19172 | -0.011884 | -0.019056 | -0.058996 | 0.13272 | -0.066215 | 0.14011 | -0.4515 | -0.10638 | -0.037485 | -0.081147 | 0.37035 | 0.089691 | -0.081095 | 123.0258 | 122.9715 | 123.1778 | 66.6884 | -123.2294 | 122.9313 | 123.1274 | 122.9566 | 66.6782 | -123.4892
2582.7969 | 123.3032 | -66.7282 | 56.3278 | 0.0046549 | -0.031504 | -0.0012479 | 0.053295 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.040985 | 0.055958 | -66.7381 | -0.030644 | -66.7735 | 56.3068 | 56.2616 | 56.4634 | -66.9016 | -66.7611 | -0.031692 | -66.791 | 56.2306 | 56.4129 | 56.2284 | -67.166 | -0.17341 | -0.021041 | -0.009902 | -0.045264 | 0.12815 | -0.066215 | 0.13554 | -0.43777 | -0.097225 | -0.032911 | -0.062837 | 0.37493 | 0.085112 | -0.099409 | 123.035 | 122.9898 | 123.1916 | 66.6976 | -123.2294 | 122.9588 | 123.1411 | 122.9566 | 66.6965 | -123.4938
2583.7969 | 123.3032 | -66.7145 | 56.3095 | 0.012286 | -0.031718 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055681 | 0.041198 | 0.055958 | -66.7335 | -0.030644 | -66.7689 | 56.3205 | 56.2616 | 56.4679 | -66.9062 | -66.7611 | -0.040849 | -66.7819 | 56.2306 | 56.4175 | 56.2376 | -67.1706 | -0.19172 | 0.011005 | -0.019056 | -0.054418 | 0.1373 | -0.047904 | 0.15843 | -0.45608 | -0.078914 | -0.046643 | -0.067412 | 0.38867 | 0.108 | -0.071941 | 123.035 | 122.9761 | 123.1824 | 66.6838 | -123.2157 | 122.9451 | 123.132 | 122.952 | 66.6736 | -123.4801
2584.8594 | 123.2849 | -66.7145 | 56.3416 | -0.0029761 | -0.031718 | -0.0010343 | 0.053508 | -0.0078008 | 0.062076 | 0.015414 | -0.0036937 | -0.00055553 | 0.055467 | 0.040344 | 0.055958 | -66.7335 | -0.030644 | -66.7781 | 56.3159 | 56.2616 | 56.4588 | -66.9016 | -66.752 | -0.031692 | -66.7865 | 56.226 | 56.4129 | 56.233 | -67.1614 | -0.18714 | -0.025617 | -0.019056 | -0.063575 | 0.12357 | -0.079948 | 0.11722 | -0.44692 | -0.11554 | -0.037485 | -0.071991 | 0.37493 | 0.071379 | -0.10856 | 123.0304 | 122.9761 | 123.1733 | 66.6838 | -123.2432 | 122.9405 | 123.1274 | 122.9475 | 66.6828 | -123.503
2585.7969 | 123.2758 | -66.7374 | 56.3095 | 0.0046549 | -0.031718 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.040771 | 0.055531 | -66.7335 | -0.030644 | -66.7781 | 56.3251 | 56.257 | 56.4679 | -66.897 | -66.752 | -0.036271 | -66.7819 | 56.226 | 56.4129 | 56.2467 | -67.166 | -0.15967 | 0.015584 | 0.003832 | -0.040687 | 0.11899 | -0.052483 | 0.15843 | -0.42862 | -0.083493 | -0.014597 | -0.044524 | 0.38409 | 0.10342 | -0.062784 | 123.0625 | 122.9944 | 123.2053 | 66.7067 | -123.2065 | 122.9634 | 123.1503 | 122.9841 | 66.7011 | -123.4755
2586.7969 | 123.2895 | -66.7099 | 56.3324 | -0.010607 | -0.031504 | -0.00082046 | 0.052867 | -0.0078008 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.040771 | 0.056171 | -66.7381 | -0.026065 | -66.7735 | 56.3159 | 56.257 | 56.4679 | -66.897 | -66.752 | -0.031692 | -66.7819 | 56.2306 | 56.4129 | 56.2284 | -67.1706 | -0.18714 | -0.016461 | -0.028212 | -0.063574 | 0.12357 | -0.075371 | 0.13554 | -0.46066 | -0.1018 | -0.042063 | -0.07199 | 0.38867 | 0.080535 | -0.10399 | 123.0258 | 122.9669 | 123.1778 | 66.6838 | -123.2294 | 122.9405 | 123.1228 | 122.9383 | 66.6782 | -123.503
2587.7969 | 123.2391 | -66.7374 | 56.337 | 0.0046549 | -0.031718 | -0.00039306 | 0.053722 | -0.0078008 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.040771 | 0.056171 | -66.7427 | -0.030644 | -66.7781 | 56.3251 | 56.2479 | 56.4679 | -66.9016 | -66.7565 | -0.031692 | -66.7865 | 56.2306 | 56.4129 | 56.2421 | -67.166 | -0.16425 | -0.011882 | -0.005325 | -0.040687 | 0.12357 | -0.089107 | 0.13096 | -0.42862 | -0.10638 | -0.019176 | -0.049103 | 0.37951 | 0.075957 | -0.094828 | 123.0625 | 122.9852 | 123.2053 | 66.7067 | -123.2386 | 122.968 | 123.1503 | 122.9795 | 66.7057 | -123.503
2588.7969 | 123.2574 | -66.7053 | 56.3416 | -0.010607 | -0.031931 | -0.00017946 | 0.052867 | -0.0080146 | 0.062289 | 0.0077831 | -0.0036937 | -0.00034193 | 0.055254 | 0.041198 | 0.055958 | -66.7335 | -0.035222 | -66.7689 | 56.3114 | 56.2616 | 56.4634 | -66.9016 | -66.7565 | -0.031692 | -66.791 | 56.226 | 56.4221 | 56.2238 | -67.1706 | -0.1963 | -0.030195 | -0.028212 | -0.063574 | 0.13272 | -0.079948 | 0.1218 | -0.46524 | -0.11554 | -0.05122 | -0.085725 | 0.37951 | 0.080537 | -0.11772 | 123.0167 | 122.9669 | 123.1687 | 66.6701 | -123.2432 | 122.9313 | 123.1274 | 122.9292 | 66.6736 | -123.5121
2589.8594 | 123.1842 | -66.7465 | 56.3873 | -0.0029761 | -0.031718 | -0.00039306 | 0.053081 | -0.0078008 | 0.062717 | -0.015108 | -0.0036937 | -0.00076913 | 0.05504 | 0.040771 | 0.055958 | -66.729 | -0.021486 | -66.7689 | 56.3159 | 56.2662 | 56.4725 | -66.9062 | -66.7565 | -0.031692 | -66.7865 | 56.2214 | 56.4175 | 56.2284 | -67.1614 | -0.15968 | -0.071393 | 0.017565 | -0.022375 | 0.1373 | -0.12114 | 0.085184 | -0.41488 | -0.16589 | -0.010021 | -0.039948 | 0.37493 | 0.030182 | -0.15892 | 123.0625 | 123.0127 | 123.219 | 66.725 | -123.2935 | 122.968 | 123.164 | 122.9749 | 66.7148 | -123.5487
2590.7969 | 123.2986 | -66.7236 | 56.3324 | -0.010607 | -0.031931 | -0.00082046 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055467 | 0.040985 | 0.055744 | -66.729 | -0.030644 | -66.7689 | 56.3159 | 56.2662 | 56.4634 | -66.897 | -66.7565 | -0.031692 | -66.7865 | 56.2214 | 56.4175 | 56.233 | -67.166 | -0.17341 | -0.016461 | -0.005323 | -0.045263 | 0.12814 | -0.066213 | 0.13096 | -0.44235 | -0.11096 | -0.032909 | -0.062836 | 0.37951 | 0.085114 | -0.099407 | 123.0396 | 122.9898 | 123.187 | 66.693 | -123.2294 | 122.9451 | 123.1411 | 122.9566 | 66.6919 | -123.4984
2591.8594 | 123.3032 | -66.7236 | 56.3278 | -0.0029761 | -0.031931 | -0.00039306 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.040771 | 0.055744 | -66.7381 | -0.026065 | -66.7689 | 56.3159 | 56.2616 | 56.4634 | -66.9062 | -66.7565 | -0.036271 | -66.7956 | 56.2306 | 56.4175 | 56.2284 | -67.1614 | -0.18256 | -0.011884 | -0.014479 | -0.045263 | 0.1373 | -0.066215 | 0.13554 | -0.43777 | -0.097225 | -0.032909 | -0.071993 | 0.36578 | 0.089691 | -0.099409 | 123.0396 | 122.9852 | 123.187 | 66.6976 | -123.234 | 122.9542 | 123.1411 | 122.952 | 66.6874 | -123.4892
2592.7969 | 123.2895 | -66.7007 | 56.3324 | -0.0029761 | -0.031931 | -0.00082046 | 0.053722 | -0.0078008 | 0.06293 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.040985 | 0.055744 | -66.7335 | -0.035222 | -66.7643 | 56.3159 | 56.2479 | 56.4588 | -66.9016 | -66.7611 | -0.031692 | -66.7865 | 56.226 | 56.4175 | 56.2421 | -67.1751 | -0.20087 | -0.016461 | -0.032789 | -0.063573 | 0.1373 | -0.084529 | 0.12638 | -0.47439 | -0.10638 | -0.060376 | -0.085724 | 0.38867 | 0.085114 | -0.09025 | 123.0167 | 122.9486 | 123.1595 | 66.6655 | -123.234 | 122.9268 | 123.1183 | 122.9429 | 66.6691 | -123.5075
2593.7969 | 123.3032 | -66.7191 | 56.3324 | -0.0029761 | -0.031931 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055254 | 0.041198 | 0.056171 | -66.729 | -0.030644 | -66.7735 | 56.3159 | 56.2662 | 56.4725 | -66.897 | -66.7565 | -0.040849 | -66.791 | 56.2214 | 56.4084 | 56.2467 | -67.166 | -0.17799 | -0.016461 | -0.009901 | -0.054419 | 0.12357 | -0.066213 | 0.14012 | -0.44693 | -0.11096 | -0.037487 | -0.071992 | 0.37493 | 0.075957 | -0.085672 | 123.035 | 122.9852 | 123.1916 | 66.6884 | -123.2294 | 122.9405 | 123.1274 | 122.9658 | 66.6782 | -123.4984
2594.8594 | 123.2849 | -66.7007 | 56.3278 | -0.0029761 | -0.031931 | -0.00039306 | 0.053295 | -0.0080146 | 0.062289 | -0.0074779 | -0.0032665 | -0.00076913 | 0.055681 | 0.040771 | 0.056171 | -66.729 | -0.026065 | -66.7689 | 56.3114 | 56.257 | 56.4634 | -66.9062 | -66.752 | -0.031692 | -66.7865 | 56.226 | 56.4084 | 56.2147 | -67.1706 | -0.20545 | -0.016462 | -0.028211 | -0.068151 | 0.1373 | -0.070794 | 0.13554 | -0.46981 | -0.1018 | -0.051218 | -0.085724 | 0.38409 | 0.080534 | -0.11315 | 123.0121 | 122.9578 | 123.1641 | 66.6747 | -123.234 | 122.9268 | 123.1091 | 122.9154 | 66.6691 | -123.4984
2595.7969 | 123.2437 | -66.7191 | 56.3232 | 0.012286 | -0.031718 | -0.00039306 | 0.053295 | -0.0078008 | 0.062503 | 0.015414 | -0.0034801 | -0.00076913 | 0.055467 | 0.040771 | 0.055958 | -66.7335 | -0.030644 | -66.7735 | 56.3159 | 56.2708 | 56.4679 | -66.897 | -66.7611 | -0.036271 | -66.7819 | 56.226 | 56.4084 | 56.2193 | -67.1706 | -0.17799 | -0.007306 | -0.014479 | -0.054419 | 0.12357 | -0.052479 | 0.14469 | -0.4515 | -0.097226 | -0.042066 | -0.062835 | 0.38867 | 0.085112 | -0.10399 | 123.035 | 122.9898 | 123.187 | 66.6884 | -123.2203 | 122.9451 | 123.1274 | 122.9383 | 66.6828 | -123.4938
2596.8594 | 123.2712 | -66.7557 | 56.2866 | -0.0029761 | -0.031718 | -0.00039306 | 0.052867 | -0.0082282 | 0.062076 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.041412 | 0.056171 | -66.7473 | -0.030644 | -66.7689 | 56.3159 | 56.2524 | 56.4588 | -66.8925 | -66.7657 | -0.031692 | -66.7865 | 56.2306 | 56.4129 | 56.2055 | -67.1614 | -0.13679 | 0.029315 | 0.008407 | -0.01322 | 0.12356 | -0.034174 | 0.17216 | -0.40573 | -0.056026 | -0.010023 | -0.030793 | 0.37493 | 0.12631 | -0.081103 | 123.0716 | 123.0081 | 123.2145 | 66.725 | -123.1791 | 122.9863 | 123.1686 | 122.9612 | 66.724 | -123.448
2597.7969 | 123.2986 | -66.7145 | 56.3324 | -0.010607 | -0.031931 | -0.00082046 | 0.053508 | -0.0080146 | 0.06293 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055681 | 0.041198 | 0.055958 | -66.7381 | -0.030644 | -66.7689 | 56.3159 | 56.257 | 56.4725 | -66.897 | -66.7565 | -0.036271 | -66.791 | 56.226 | 56.4129 | 56.2421 | -67.1614 | -0.18256 | -0.016461 | -0.023634 | -0.054418 | 0.12814 | -0.075371 | 0.14012 | -0.44692 | -0.10638 | -0.042064 | -0.076569 | 0.37035 | 0.080535 | -0.09025 | 123.0304 | 122.9715 | 123.187 | 66.6838 | -123.2294 | 122.9405 | 123.1274 | 122.9566 | 66.6782 | -123.4938
2598.8594 | 123.2849 | -66.7145 | 56.3232 | 0.0046549 | -0.032145 | -0.00060686 | 0.053295 | -0.0080146 | 0.062717 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055467 | 0.040985 | 0.055744 | -66.7244 | -0.026065 | -66.7689 | 56.3251 | 56.257 | 56.4725 | -66.897 | -66.752 | -0.040849 | -66.7865 | 56.2214 | 56.4038 | 56.2421 | -67.1614 | -0.18256 | 0.001851 | -0.009899 | -0.054418 | 0.12814 | -0.066216 | 0.14927 | -0.44692 | -0.1018 | -0.037485 | -0.071991 | 0.37493 | 0.080533 | -0.081095 | 123.0396 | 122.9715 | 123.187 | 66.6884 | -123.2203 | 122.9359 | 123.1183 | 122.9566 | 66.6736 | -123.4846
2599.7969 | 123.1979 | -66.7419 | 56.3416 | -0.010607 | -0.031931 | -0.00060686 | 0.052654 | -0.0080146 | 0.062289 | -0.0074779 | -0.0039075 | -0.00076913 | 0.055467 | 0.040771 | 0.055744 | -66.7381 | -0.030644 | -66.7735 | 56.3205 | 56.2616 | 56.4588 | -66.9016 | -66.7611 | -0.031692 | -66.791 | 56.226 | 56.4129 | 56.2376 | -67.166 | -0.15968 | -0.021039 | 0.003831 | -0.031531 | 0.12815 | -0.079948 | 0.11722 | -0.42404 | -0.11554 | -0.019178 | -0.049104 | 0.37493 | 0.071379 | -0.10398 | 123.0625 | 123.0035 | 123.2007 | 66.7113 | -123.2432 | 122.968 | 123.1549 | 122.9795 | 66.7103 | -123.5075
2600.7969 | 123.1979 | -66.7557 | 56.3736 | -0.0029761 | -0.031931 | -0.00082046 | 0.052867 | -0.0084418 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055254 | 0.041198 | 0.056171 | -66.7381 | -0.026065 | -66.7643 | 56.3159 | 56.2662 | 56.4725 | -66.9062 | -66.7565 | -0.031692 | -66.7819 | 56.2306 | 56.4129 | 56.2467 | -67.166 | -0.15052 | -0.05766 | 0.017564 | -0.008642 | 0.14188 | -0.10741 | 0.098917 | -0.41031 | -0.143 | -0.000866 | -0.026214 | 0.38409 | 0.039336 | -0.12687 | 123.0716 | 123.0219 | 123.2282 | 66.7296 | -123.2798 | 122.9863 | 123.1686 | 123.0024 | 66.724 | -123.5396
2601.7969 | 123.2849 | -66.7191 | 56.3049 | 0.0046549 | -0.031504 | -0.00082046 | 0.053081 | -0.0078008 | 0.062503 | 0.015414 | -0.0036937 | -0.00076913 | 0.055467 | 0.040771 | 0.055744 | -66.7335 | -0.035222 | -66.7643 | 56.3205 | 56.2662 | 56.4679 | -66.897 | -66.752 | -0.031692 | -66.8002 | 56.2306 | 56.4129 | 56.2421 | -67.166 | -0.17799 | 0.015582 | -0.014479 | -0.045263 | 0.13272 | -0.038748 | 0.163 | -0.44693 | -0.074337 | -0.032908 | -0.08115 | 0.36578 | 0.108 | -0.062785 | 123.0396 | 122.9852 | 123.187 | 66.6838 | -123.202 | 122.9496 | 123.132 | 122.9612 | 66.6874 | -123.4709
2602.7969 | 123.1934 | -66.7465 | 56.4011 | -0.0029761 | -0.031931 | -0.0010343 | 0.053081 | -0.0078008 | 0.062289 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055467 | 0.040771 | 0.055958 | -66.7335 | -0.039801 | -66.7689 | 56.3205 | 56.2616 | 56.4725 | -66.9062 | -66.7565 | -0.036271 | -66.791 | 56.2306 | 56.4175 | 56.2467 | -67.166 | -0.15968 | -0.080548 | 0.012987 | -0.022375 | 0.1373 | -0.13946 | 0.071451 | -0.41946 | -0.17047 | -0.010021 | -0.044526 | 0.37493 | 0.016449 | -0.15434 | 123.067 | 123.0081 | 123.219 | 66.7067 | -123.3073 | 122.9771 | 123.164 | 122.9932 | 66.7103 | -123.567
2603.8594 | 123.2986 | -66.7007 | 56.3187 | -0.0029761 | -0.032145 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.041198 | 0.056171 | -66.7335 | -0.030644 | -66.7643 | 56.3251 | 56.2616 | 56.4771 | -66.9016 | -66.7565 | -0.036271 | -66.7819 | 56.2306 | 56.4175 | 56.2513 | -67.166 | -0.20087 | 0.006428 | -0.032789 | -0.063573 | 0.1373 | -0.05706 | 0.15843 | -0.46524 | -0.08807 | -0.055797 | -0.081145 | 0.38409 | 0.098846 | -0.067361 | 123.0258 | 122.9624 | 123.1778 | 66.6701 | -123.2203 | 122.9313 | 123.1183 | 122.952 | 66.6645 | -123.4846
2604.7969 | 123.2208 | -66.7511 | 56.3461 | -0.0029761 | -0.031931 | -0.00082046 | 0.052867 | -0.0084418 | 0.062076 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055467 | 0.040985 | 0.056171 | -66.7381 | -0.035222 | -66.7689 | 56.3251 | 56.2662 | 56.4679 | -66.9016 | -66.7565 | -0.040849 | -66.7865 | 56.226 | 56.4175 | 56.2421 | -67.166 | -0.15052 | -0.021037 | 0.012987 | -0.017797 | 0.13272 | -0.079946 | 0.1218 | -0.41488 | -0.12011 | -0.005443 | -0.03537 | 0.37951 | 0.071381 | -0.10398 | 123.0762 | 123.0173 | 123.219 | 66.7159 | -123.2477 | 122.9771 | 123.1686 | 122.9932 | 66.7103 | -123.5121
2605.7969 | 123.3078 | -66.7236 | 56.337 | 0.0046549 | -0.031931 | -0.00060686 | 0.053295 | -0.0080146 | 0.062717 | 0.0077831 | -0.0034801 | -0.00098273 | 0.055681 | 0.040771 | 0.056171 | -66.7381 | -0.035222 | -66.7597 | 56.3251 | 56.2524 | 56.4634 | -66.9016 | -66.7565 | -0.036271 | -66.791 | 56.2352 | 56.4129 | 56.2421 | -67.1706 | -0.17799 | -0.011882 | -0.014479 | -0.036107 | 0.14188 | -0.084528 | 0.12638 | -0.44693 | -0.1018 | -0.032909 | -0.067414 | 0.37951 | 0.075957 | -0.094828 | 123.0487 | 122.9761 | 123.187 | 66.6884 | -123.2386 | 122.9588 | 123.1366 | 122.9658 | 66.6874 | -123.5075
2606.7969 | 123.175 | -66.7557 | 56.3736 | 0.0046549 | -0.031931 | -0.0010343 | 0.053295 | -0.0082282 | 0.062076 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055467 | 0.040985 | 0.056171 | -66.729 | -0.030644 | -66.7689 | 56.3205 | 56.2524 | 56.4679 | -66.9016 | -66.7611 | -0.040849 | -66.791 | 56.2306 | 56.4129 | 56.2742 | -67.166 | -0.14594 | -0.053082 | 0.02672 | -0.01322 | 0.13272 | -0.12115 | 0.094338 | -0.41031 | -0.143 | -0.005445 | -0.035371 | 0.37493 | 0.039336 | -0.099399 | 123.0762 | 123.0081 | 123.2236 | 66.725 | -123.2752 | 122.9863 | 123.1686 | 123.0299 | 66.7148 | -123.5396
2607.7969 | 123.2254 | -66.7236 | 56.3461 | 0.0046549 | -0.031718 | -0.00060686 | 0.052867 | -0.0082282 | 0.062717 | 0.015414 | -0.0032665 | -0.00076913 | 0.055254 | 0.040985 | 0.055744 | -66.7335 | -0.039801 | -66.7689 | 56.3114 | 56.2616 | 56.4679 | -66.9108 | -66.752 | -0.040849 | -66.7819 | 56.2214 | 56.4084 | 56.2421 | -67.166 | -0.18714 | -0.034772 | -0.009901 | -0.045263 | 0.14188 | -0.084525 | 0.1218 | -0.44235 | -0.12469 | -0.02833 | -0.058257 | 0.38409 | 0.062224 | -0.10398 | 123.035 | 122.9852 | 123.1916 | 66.6838 | -123.2569 | 122.9451 | 123.132 | 122.9658 | 66.6828 | -123.5121
2608.8594 | 123.2941 | -66.6916 | 56.337 | 0.0046549 | -0.031718 | -0.00060686 | 0.053295 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.055254 | 0.041412 | 0.055744 | -66.7335 | -0.039801 | -66.7689 | 56.3205 | 56.2662 | 56.4679 | -66.9016 | -66.7611 | -0.040849 | -66.791 | 56.226 | 56.4175 | 56.2467 | -67.1614 | -0.21003 | -0.016461 | -0.041945 | -0.077307 | 0.13272 | -0.070791 | 0.13096 | -0.46981 | -0.11096 | -0.069532 | -0.099458 | 0.37035 | 0.080536 | -0.09025 | 123.0121 | 122.9578 | 123.1595 | 66.6518 | -123.2386 | 122.9176 | 123.1091 | 122.9383 | 66.6507 | -123.4984
2609.7969 | 123.1934 | -66.7419 | 56.3644 | -0.0029761 | -0.031931 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.055254 | 0.041198 | 0.056171 | -66.7381 | -0.030644 | -66.7781 | 56.3205 | 56.2662 | 56.4634 | -66.9016 | -66.7657 | -0.040849 | -66.7819 | 56.2306 | 56.4129 | 56.2559 | -67.166 | -0.15968 | -0.043927 | 0.003831 | -0.03611 | 0.12357 | -0.098257 | 0.098915 | -0.42404 | -0.13385 | -0.023756 | -0.039947 | 0.38409 | 0.048491 | -0.10856 | 123.0625 | 123.0081 | 123.2053 | 66.7113 | -123.2661 | 122.9725 | 123.1549 | 122.9978 | 66.7011 | -123.5304
2610.7969 | 123.2437 | -66.7603 | 56.3553 | -0.010607 | -0.031931 | -0.00039306 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0034801 | -0.00098273 | 0.055681 | 0.041198 | 0.055958 | -66.7335 | -0.035222 | -66.7735 | 56.3159 | 56.2616 | 56.4725 | -66.9154 | -66.7565 | -0.040849 | -66.791 | 56.2306 | 56.4221 | 56.2421 | -67.166 | -0.1551 | -0.03935 | 0.02672 | -0.01322 | 0.14188 | -0.093681 | 0.11723 | -0.40573 | -0.12469 | 0.003712 | -0.030793 | 0.37493 | 0.066804 | -0.11314 | 123.0762 | 123.0219 | 123.2328 | 66.725 | -123.2706 | 122.9908 | 123.1823 | 123.0024 | 66.7194 | -123.5213
2611.8594 | 123.2895 | -66.6962 | 56.337 | -0.0029761 | -0.031931 | -0.00060686 | 0.053081 | -0.0080146 | 0.062717 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055254 | 0.040771 | 0.055958 | -66.7381 | -0.035222 | -66.7735 | 56.3251 | 56.2616 | 56.4725 | -66.9062 | -66.7474 | -0.040849 | -66.7865 | 56.2306 | 56.4129 | 56.2421 | -67.166 | -0.21003 | -0.011882 | -0.041945 | -0.077307 | 0.13272 | -0.07537 | 0.13554 | -0.46981 | -0.10638 | -0.051218 | -0.090302 | 0.37951 | 0.075957 | -0.094828 | 123.0213 | 122.9578 | 123.1687 | 66.6609 | -123.2432 | 122.9268 | 123.1091 | 122.9383 | 66.6553 | -123.503
2612.7969 | 123.175 | -66.7374 | 56.3736 | 0.012286 | -0.031931 | -0.00082046 | 0.053295 | -0.0082282 | 0.062717 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055467 | 0.040771 | 0.055958 | -66.729 | -0.030644 | -66.7597 | 56.3205 | 56.2662 | 56.4725 | -66.9016 | -66.7474 | -0.031692 | -66.791 | 56.226 | 56.4175 | 56.2421 | -67.166 | -0.16425 | -0.053082 | 0.00841 | -0.022374 | 0.14188 | -0.10741 | 0.098917 | -0.42862 | -0.14758 | -0.010019 | -0.053681 | 0.37493 | 0.043915 | -0.13145 | 123.0579 | 123.0035 | 123.2099 | 66.7067 | -123.2752 | 122.9634 | 123.1549 | 122.9795 | 66.7057 | -123.5396
2613.7969 | 123.1659 | -66.7557 | 56.3599 | 0.0046549 | -0.031718 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.040985 | 0.055958 | -66.729 | -0.035222 | -66.7643 | 56.3205 | 56.2708 | 56.4725 | -66.9062 | -66.7474 | -0.036271 | -66.791 | 56.226 | 56.4175 | 56.2742 | -67.1706 | -0.15052 | -0.039349 | 0.02672 | -0.008642 | 0.14188 | -0.0891 | 0.11265 | -0.41488 | -0.13385 | 0.008291 | -0.035371 | 0.37951 | 0.057648 | -0.085666 | 123.0762 | 123.0264 | 123.2282 | 66.7205 | -123.2661 | 122.9817 | 123.1732 | 123.0299 | 66.7194 | -123.5304
2614.8594 | 123.1979 | -66.7465 | 56.3507 | 0.0046549 | -0.031931 | -0.00039306 | 0.052654 | -0.0082282 | 0.062717 | 0.023044 | -0.0036937 | -0.00076913 | 0.055467 | 0.041412 | 0.056171 | -66.729 | -0.039801 | -66.7689 | 56.3205 | 56.2662 | 56.4725 | -66.9108 | -66.7611 | -0.045428 | -66.7956 | 56.2306 | 56.4175 | 56.2742 | -67.166 | -0.16426 | -0.030194 | 0.017565 | -0.022375 | 0.14188 | -0.084524 | 0.12181 | -0.41946 | -0.12011 | -0.0146 | -0.049105 | 0.37036 | 0.066803 | -0.076511 | 123.067 | 123.0127 | 123.219 | 66.7067 | -123.2615 | 122.9771 | 123.164 | 123.0207 | 66.7011 | -123.5167
2615.7969 | 123.2391 | -66.7694 | 56.3736 | -0.0029761 | -0.032145 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.040985 | 0.055744 | -66.7381 | -0.039801 | -66.7735 | 56.3251 | 56.2616 | 56.4771 | -66.897 | -66.7565 | -0.040849 | -66.791 | 56.2352 | 56.4221 | 56.2467 | -67.1614 | -0.12763 | -0.048503 | 0.031297 | -0.004065 | 0.12357 | -0.11199 | 0.1035 | -0.39199 | -0.13842 | 0.012867 | -0.021638 | 0.37035 | 0.048494 | -0.12687 | 123.0945 | 123.031 | 123.2465 | 66.7296 | -123.2706 | 123.0046 | 123.1915 | 123.0161 | 66.7286 | -123.535
2616.7969 | 123.1979 | -66.7511 | 56.337 | -0.0029761 | -0.031931 | -0.00082046 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0032665 | -0.00055553 | 0.055254 | 0.041198 | 0.055744 | -66.7381 | -0.030644 | -66.7689 | 56.3251 | 56.257 | 56.4725 | -66.9016 | -66.7611 | -0.045428 | -66.7819 | 56.2352 | 56.4084 | 56.2376 | -67.1614 | -0.15052 | -0.011882 | 0.012987 | -0.017797 | 0.13272 | -0.079949 | 0.13554 | -0.4103 | -0.1018 | -0.010022 | -0.030791 | 0.37951 | 0.071379 | -0.099407 | 123.0762 | 123.0081 | 123.2236 | 66.7205 | -123.2386 | 122.9863 | 123.1595 | 122.9887 | 66.7057 | -123.4984
2617.8594 | 123.2208 | -66.7419 | 56.3965 | 0.012286 | -0.032145 | -0.00060686 | 0.053081 | -0.0078008 | 0.062717 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055467 | 0.040985 | 0.056171 | -66.7335 | -0.044379 | -66.7689 | 56.3297 | 56.2616 | 56.4725 | -66.9062 | -66.7611 | -0.040849 | -66.7865 | 56.2306 | 56.4129 | 56.2513 | -67.1614 | -0.16425 | -0.066813 | 0.008409 | -0.026953 | 0.1373 | -0.13488 | 0.076029 | -0.41946 | -0.16589 | -0.019178 | -0.044526 | 0.37493 | 0.016448 | -0.14518 | 123.0716 | 123.0035 | 123.2145 | 66.6976 | -123.3027 | 122.9725 | 123.1549 | 122.9932 | 66.7011 | -123.5579
2618.7969 | 123.2208 | -66.7419 | 56.337 | 0.0046549 | -0.032145 | -0.00039306 | 0.052867 | -0.0082282 | 0.062289 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.041198 | 0.056385 | -66.7335 | -0.035222 | -66.7781 | 56.3251 | 56.2753 | 56.4817 | -66.9062 | -66.7565 | -0.031692 | -66.791 | 56.226 | 56.4129 | 56.2376 | -67.1568 | -0.16425 | -0.011882 | 0.008409 | -0.03611 | 0.12815 | -0.061633 | 0.14469 | -0.41488 | -0.11096 | -0.014599 | -0.049104 | 0.36578 | 0.075957 | -0.099407 | 123.067 | 123.0173 | 123.2236 | 66.7067 | -123.2432 | 122.968 | 123.1549 | 122.9795 | 66.7103 | -123.4938
2619.7969 | 123.2208 | -66.7603 | 56.3599 | -0.0029761 | -0.032359 | -0.00060686 | 0.052654 | -0.0078008 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.041198 | 0.056171 | -66.7244 | -0.035222 | -66.7735 | 56.3297 | 56.2616 | 56.4725 | -66.9062 | -66.7611 | -0.040849 | -66.791 | 56.2306 | 56.4175 | 56.2605 | -67.166 | -0.14594 | -0.030192 | 0.035877 | -0.01322 | 0.13272 | -0.098258 | 0.11265 | -0.40573 | -0.12927 | -0.000867 | -0.030793 | 0.37493 | 0.057648 | -0.099402 | 123.0899 | 123.0219 | 123.2328 | 66.725 | -123.2661 | 122.9908 | 123.1778 | 123.0207 | 66.7194 | -123.5258
2620.7969 | 123.2208 | -66.7694 | 56.3553 | -0.010607 | -0.032359 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | -0.0074779 | -0.0039075 | -0.00034193 | 0.055467 | 0.041198 | 0.055958 | -66.7335 | -0.030644 | -66.7689 | 56.3205 | 56.2524 | 56.4771 | -66.9062 | -66.7565 | -0.050007 | -66.7865 | 56.226 | 56.4129 | 56.2421 | -67.1706 | -0.13679 | -0.034772 | 0.035875 | 0.000513 | 0.1373 | -0.10284 | 0.12181 | -0.40115 | -0.12927 | 0.012867 | -0.01706 | 0.38409 | 0.057646 | -0.11314 | 123.0899 | 123.0219 | 123.2465 | 66.7388 | -123.2615 | 122.9954 | 123.1823 | 123.0116 | 66.7194 | -123.5258
2621.7969 | 123.1934 | -66.7603 | 56.3553 | -0.010607 | -0.032145 | -0.00039306 | 0.053081 | -0.0082282 | 0.062717 | 0.015414 | -0.0041211 | -0.00076913 | 0.05504 | 0.040985 | 0.055958 | -66.7335 | -0.035222 | -66.7643 | 56.3205 | 56.2845 | 56.4679 | -66.897 | -66.752 | -0.050007 | -66.791 | 56.2306 | 56.4175 | 56.2284 | -67.1614 | -0.13679 | -0.034772 | 0.02672 | -0.004064 | 0.13272 | -0.070787 | 0.11265 | -0.40115 | -0.12469 | 0.008291 | -0.030793 | 0.37035 | 0.062225 | -0.12687 | 123.0808 | 123.0448 | 123.2282 | 66.725 | -123.2523 | 122.9908 | 123.1778 | 122.9887 | 66.7102 | -123.5167
2622.7969 | 123.1659 | -66.7877 | 56.3232 | -0.0029761 | -0.031931 | -0.00082046 | 0.053081 | -0.0080146 | 0.062076 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055681 | 0.040985 | 0.056171 | -66.7381 | -0.035222 | -66.7689 | 56.3251 | 56.2662 | 56.4725 | -66.9062 | -66.7657 | -0.040849 | -66.7865 | 56.2214 | 56.4221 | 56.2467 | -67.1614 | -0.11848 | 0.001851 | 0.049608 | 0.018824 | 0.1373 | -0.057058 | 0.14927 | -0.37368 | -0.1018 | 0.022021 | 0.001251 | 0.37493 | 0.098848 | -0.076517 | 123.1128 | 123.0539 | 123.2602 | 66.7525 | -123.2294 | 123.0092 | 123.2098 | 123.0344 | 66.7469 | -123.4846
2623.8594 | 123.2391 | -66.7328 | 56.3324 | 0.0046549 | -0.032359 | -0.00060686 | 0.052867 | -0.0075872 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.041412 | 0.056171 | -66.729 | -0.048958 | -66.7781 | 56.3205 | 56.2662 | 56.4725 | -66.9108 | -66.7565 | -0.045428 | -66.7956 | 56.226 | 56.4175 | 56.2559 | -67.166 | -0.17799 | -0.011883 | 0.003832 | -0.045265 | 0.13272 | -0.066213 | 0.14012 | -0.43319 | -0.10638 | -0.023754 | -0.062838 | 0.37036 | 0.085114 | -0.076514 | 123.0533 | 122.999 | 123.2053 | 66.6838 | -123.2432 | 122.9588 | 123.1503 | 122.9887 | 66.6874 | -123.4984
2624.7969 | 123.1659 | -66.7603 | 56.3461 | -0.0029761 | -0.031931 | -0.00082046 | 0.053295 | -0.0078008 | 0.062076 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055467 | 0.041198 | 0.056171 | -66.7381 | -0.035222 | -66.7643 | 56.3205 | 56.257 | 56.4679 | -66.9016 | -66.752 | -0.045428 | -66.7956 | 56.2306 | 56.4221 | 56.265 | -67.166 | -0.14136 | -0.025616 | 0.022142 | -0.004064 | 0.1373 | -0.089104 | 0.1218 | -0.40573 | -0.11554 | 0.008291 | -0.035372 | 0.37036 | 0.07596 | -0.08109 | 123.0808 | 123.0173 | 123.2282 | 66.725 | -123.2477 | 122.9908 | 123.1823 | 123.0253 | 66.7148 | -123.5121
2625.7969 | 123.1567 | -66.7694 | 56.3507 | -0.0029761 | -0.032145 | -0.00060686 | 0.052654 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.05504 | 0.040985 | 0.055958 | -66.7381 | -0.044379 | -66.7689 | 56.3297 | 56.257 | 56.4679 | -66.9016 | -66.7565 | -0.045428 | -66.791 | 56.2306 | 56.4175 | 56.2238 | -67.166 | -0.13221 | -0.021037 | 0.031297 | 0.000513 | 0.13272 | -0.093682 | 0.11723 | -0.39657 | -0.12011 | 0.012867 | -0.021638 | 0.37493 | 0.066803 | -0.12688 | 123.0991 | 123.0264 | 123.2373 | 66.725 | -123.2523 | 123 | 123.1869 | 122.9932 | 66.724 | -123.5167
2626.8594 | 123.2117 | -66.7557 | 56.3324 | -0.010607 | -0.032359 | -0.00060686 | 0.053081 | -0.0082282 | 0.062289 | -0.015108 | -0.0039075 | -0.00076913 | 0.055254 | 0.041412 | 0.055958 | -66.7335 | -0.035222 | -66.7735 | 56.3205 | 56.2753 | 56.4679 | -66.9108 | -66.7611 | -0.045428 | -66.7865 | 56.2352 | 56.4175 | 56.2467 | -67.166 | -0.1551 | -0.011883 | 0.022142 | -0.017798 | 0.1373 | -0.057055 | 0.13554 | -0.41031 | -0.097224 | -0.005445 | -0.030793 | 0.37951 | 0.085114 | -0.085672 | 123.0762 | 123.031 | 123.2236 | 66.7205 | -123.2432 | 122.9908 | 123.1732 | 123.0024 | 66.7102 | -123.4984
2627.7969 | 123.2208 | -66.7694 | 56.3095 | -0.0029761 | -0.031931 | -0.00039306 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0036937 | -0.00012813 | 0.055467 | 0.041412 | 0.055744 | -66.729 | -0.035222 | -66.7643 | 56.3159 | 56.2616 | 56.4725 | -66.9016 | -66.7565 | -0.040849 | -66.7865 | 56.2214 | 56.4129 | 56.2605 | -67.166 | -0.13221 | 0.006427 | 0.040453 | 0.005091 | 0.1373 | -0.047904 | 0.163 | -0.39657 | -0.088071 | 0.012867 | -0.01706 | 0.37951 | 0.10342 | -0.049048 | 123.0853 | 123.031 | 123.2419 | 66.7342 | -123.2111 | 122.9908 | 123.1823 | 123.0299 | 66.7286 | -123.4755
2628.8594 | 123.1613 | -66.7511 | 56.3507 | -0.0029761 | -0.032359 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.055254 | 0.040771 | 0.056171 | -66.729 | -0.035222 | -66.7735 | 56.3205 | 56.2616 | 56.4817 | -66.9016 | -66.7474 | -0.045428 | -66.7819 | 56.2214 | 56.4175 | 56.2559 | -67.1568 | -0.15052 | -0.030194 | 0.022143 | -0.022375 | 0.12815 | -0.089103 | 0.13096 | -0.40572 | -0.12927 | 0.003714 | -0.030791 | 0.37493 | 0.066803 | -0.094825 | 123.0716 | 123.0127 | 123.2328 | 66.7159 | -123.2523 | 122.9725 | 123.1686 | 123.007 | 66.7057 | -123.5075
2629.7969 | 123.2895 | -66.7465 | 56.3004 | 0.0046549 | -0.032145 | -0.00060686 | 0.052867 | -0.0080146 | 0.062717 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055254 | 0.041412 | 0.055744 | -66.7335 | -0.035222 | -66.7689 | 56.3205 | 56.2616 | 56.4725 | -66.9016 | -66.7565 | -0.040849 | -66.791 | 56.226 | 56.4221 | 56.2284 | -67.166 | -0.1551 | 0.02016 | 0.012987 | -0.022375 | 0.13272 | -0.038749 | 0.17216 | -0.41946 | -0.074338 | -0.010021 | -0.044526 | 0.37493 | 0.12174 | -0.071943 | 123.067 | 123.0081 | 123.219 | 66.7113 | -123.202 | 122.9725 | 123.1686 | 122.9749 | 66.7057 | -123.4663
2630.7969 | 123.262 | -66.7557 | 56.3004 | 0.0046549 | -0.032145 | -0.00060686 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.041198 | 0.056171 | -66.7335 | -0.039801 | -66.7689 | 56.3205 | 56.2662 | 56.4725 | -66.897 | -66.7565 | -0.040849 | -66.7956 | 56.2214 | 56.4175 | 56.233 | -67.166 | -0.14136 | 0.02016 | 0.022142 | -0.01322 | 0.12814 | -0.03417 | 0.17216 | -0.41031 | -0.078916 | -0.000866 | -0.03995 | 0.37036 | 0.11716 | -0.067364 | 123.0762 | 123.0219 | 123.2282 | 66.7159 | -123.1974 | 122.9771 | 123.1732 | 122.9887 | 66.7148 | -123.4663
2631.7969 | 123.2941 | -66.7099 | 56.2912 | -0.010607 | -0.032145 | -0.0010343 | 0.053081 | -0.0078008 | 0.062503 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055681 | 0.041198 | 0.056171 | -66.7335 | -0.039801 | -66.7689 | 56.3251 | 56.257 | 56.4771 | -66.897 | -66.752 | -0.036271 | -66.791 | 56.2169 | 56.4084 | 56.2193 | -67.166 | -0.18714 | 0.033894 | -0.023634 | -0.058996 | 0.12814 | -0.034173 | 0.18589 | -0.45608 | -0.07434 | -0.042063 | -0.081147 | 0.37493 | 0.11716 | -0.071945 | 123.035 | 122.9669 | 123.187 | 66.6701 | -123.1882 | 122.9268 | 123.1183 | 122.9292 | 66.6736 | -123.4572
2632.8594 | 123.2849 | -66.7236 | 56.2866 | -0.0029761 | -0.032145 | -0.00039306 | 0.053081 | -0.0080146 | 0.062289 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055467 | 0.041626 | 0.055744 | -66.7381 | -0.044379 | -66.7735 | 56.3205 | 56.2662 | 56.4725 | -66.9016 | -66.7611 | -0.040849 | -66.791 | 56.2352 | 56.4175 | 56.265 | -67.166 | -0.17799 | 0.033893 | -0.014479 | -0.049841 | 0.12815 | -0.020437 | 0.18589 | -0.44235 | -0.051448 | -0.037488 | -0.067414 | 0.37493 | 0.13089 | -0.021581 | 123.0441 | 122.9898 | 123.1961 | 66.6793 | -123.1882 | 122.9588 | 123.1411 | 122.9887 | 66.6828 | -123.4526
2633.7969 | 123.3078 | -66.7419 | 56.3095 | 0.012286 | -0.032145 | -0.0010343 | 0.053081 | -0.0080146 | 0.062717 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055254 | 0.041626 | 0.055958 | -66.7335 | -0.035222 | -66.7735 | 56.3205 | 56.2616 | 56.4771 | -66.897 | -66.7657 | -0.040849 | -66.7819 | 56.2214 | 56.4175 | 56.233 | -67.1614 | -0.1551 | 0.011005 | 0.008409 | -0.031531 | 0.12357 | -0.047904 | 0.16758 | -0.41946 | -0.088071 | -0.023756 | -0.039947 | 0.37951 | 0.108 | -0.076519 | 123.0625 | 123.0035 | 123.219 | 66.7067 | -123.2065 | 122.9634 | 123.1595 | 122.9749 | 66.7011 | -123.4709
2634.7969 | 123.2758 | -66.7099 | 56.3324 | -0.0029761 | -0.031931 | -0.00060686 | 0.053081 | -0.0078008 | 0.062289 | 0.00015261 | -0.0039075 | -0.00076913 | 0.055467 | 0.041412 | 0.055958 | -66.7381 | -0.048958 | -66.7689 | 56.3251 | 56.2708 | 56.4725 | -66.9062 | -66.7565 | -0.050007 | -66.7865 | 56.2306 | 56.4175 | 56.2513 | -67.1614 | -0.1963 | -0.007304 | -0.028212 | -0.058996 | 0.1373 | -0.061634 | 0.14012 | -0.4515 | -0.1018 | -0.046642 | -0.076569 | 0.37493 | 0.085114 | -0.081093 | 123.035 | 122.9807 | 123.1824 | 66.6609 | -123.2386 | 122.9405 | 123.1274 | 122.9612 | 66.6599 | -123.4938
2635.7969 | 123.262 | -66.7328 | 56.3141 | -0.0029761 | -0.032145 | -0.00082046 | 0.053295 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055681 | 0.041198 | 0.055744 | -66.7335 | -0.039801 | -66.7735 | 56.3159 | 56.2662 | 56.4725 | -66.9108 | -66.752 | -0.040849 | -66.7956 | 56.2214 | 56.4129 | 56.2421 | -67.1614 | -0.17799 | 0.001849 | -0.000746 | -0.040686 | 0.1373 | -0.047903 | 0.15843 | -0.42861 | -0.092649 | -0.019175 | -0.062838 | 0.36578 | 0.098845 | -0.07194 | 123.0487 | 122.999 | 123.2053 | 66.693 | -123.2249 | 122.9542 | 123.1457 | 122.9749 | 66.6919 | -123.4755
2636.7969 | 123.2986 | -66.7236 | 56.337 | 0.0046549 | -0.032359 | -0.00060686 | 0.053508 | -0.0082282 | 0.062717 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055254 | 0.041198 | 0.055958 | -66.7381 | -0.044379 | -66.7689 | 56.3251 | 56.2708 | 56.4725 | -66.9016 | -66.7565 | -0.054586 | -66.7819 | 56.2306 | 56.4175 | 56.2605 | -67.166 | -0.17799 | -0.011882 | -0.014479 | -0.045263 | 0.13272 | -0.066212 | 0.13554 | -0.44235 | -0.10638 | -0.032909 | -0.058257 | 0.38409 | 0.080536 | -0.076514 | 123.0487 | 122.9944 | 123.1961 | 66.6793 | -123.2386 | 122.9542 | 123.1411 | 122.9841 | 66.669 | -123.503
2637.7969 | 123.2437 | -66.7236 | 56.337 | -0.0029761 | -0.032145 | -0.00082046 | 0.053081 | -0.0078008 | 0.062503 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055467 | 0.041412 | 0.056171 | -66.7427 | -0.039801 | -66.7826 | 56.3251 | 56.257 | 56.4679 | -66.9016 | -66.7611 | -0.050007 | -66.791 | 56.2306 | 56.4175 | 56.2605 | -67.1614 | -0.17799 | -0.011882 | -0.019058 | -0.058998 | 0.11899 | -0.079949 | 0.13096 | -0.43777 | -0.10638 | -0.037488 | -0.067414 | 0.37035 | 0.080536 | -0.076514 | 123.0487 | 122.9807 | 123.1916 | 66.6838 | -123.2386 | 122.9542 | 123.1411 | 122.9841 | 66.6736 | -123.4984
2638.8594 | 123.3582 | -66.7007 | 56.2958 | -0.0029761 | -0.032359 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.041198 | 0.055744 | -66.7381 | -0.035222 | -66.7735 | 56.3205 | 56.257 | 56.4679 | -66.897 | -66.7565 | -0.050007 | -66.7956 | 56.226 | 56.4175 | 56.2193 | -67.166 | -0.1963 | 0.024738 | -0.037367 | -0.072729 | 0.12357 | -0.03875 | 0.17216 | -0.46524 | -0.06976 | -0.055797 | -0.094881 | 0.37036 | 0.12174 | -0.076522 | 123.0213 | 122.9578 | 123.1687 | 66.6655 | -123.1928 | 122.9268 | 123.1183 | 122.92 | 66.6507 | -123.4618
2639.7969 | 123.2666 | -66.7191 | 56.3324 | 0.0046549 | -0.032145 | -0.00060686 | 0.053295 | -0.0078008 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055467 | 0.041198 | 0.055744 | -66.7427 | -0.039801 | -66.7781 | 56.3205 | 56.2708 | 56.4679 | -66.9016 | -66.7611 | -0.054586 | -66.7865 | 56.2306 | 56.4175 | 56.233 | -67.1706 | -0.18256 | -0.011883 | -0.023636 | -0.058998 | 0.12357 | -0.061634 | 0.13554 | -0.4515 | -0.1018 | -0.042066 | -0.067414 | 0.38409 | 0.085114 | -0.099407 | 123.0396 | 122.9898 | 123.187 | 66.6793 | -123.234 | 122.9496 | 123.1366 | 122.952 | 66.6645 | -123.503
2640.7969 | 123.3032 | -66.6962 | 56.3599 | -0.0029761 | -0.032145 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0032665 | -0.00076913 | 0.055467 | 0.041626 | 0.055958 | -66.7381 | -0.048958 | -66.7735 | 56.3251 | 56.2708 | 56.4771 | -66.897 | -66.7611 | -0.050007 | -66.7865 | 56.226 | 56.4221 | 56.2421 | -67.166 | -0.20087 | -0.03477 | -0.041945 | -0.077307 | 0.12357 | -0.0891 | 0.11723 | -0.46981 | -0.13385 | -0.064954 | -0.090302 | 0.37951 | 0.062227 | -0.11772 | 123.0213 | 122.9669 | 123.1733 | 66.6472 | -123.2569 | 122.9222 | 123.1183 | 122.9383 | 66.6462 | -123.5258
2641.7969 | 123.3261 | -66.687 | 56.3416 | 0.0046549 | -0.032359 | -0.0010343 | 0.053081 | -0.0080146 | 0.062717 | -0.0074779 | -0.0039075 | -0.00055553 | 0.055254 | 0.041198 | 0.055958 | -66.7244 | -0.044379 | -66.7735 | 56.3251 | 56.2616 | 56.4679 | -66.9062 | -66.752 | -0.045428 | -66.7956 | 56.2306 | 56.4175 | 56.2513 | -67.1706 | -0.21919 | -0.01646 | -0.037365 | -0.086462 | 0.13272 | -0.079948 | 0.12638 | -0.48355 | -0.11096 | -0.064951 | -0.10861 | 0.37493 | 0.075958 | -0.090249 | 123.0121 | 122.9486 | 123.1549 | 66.6426 | -123.2478 | 122.9176 | 123.1045 | 122.9383 | 66.6416 | -123.5121
2642.8594 | 123.3261 | -66.7145 | 56.3324 | -0.0029761 | -0.032359 | -0.00082046 | 0.053295 | -0.0078008 | 0.062717 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.041412 | 0.055744 | -66.7381 | -0.039801 | -66.7735 | 56.3159 | 56.2662 | 56.4771 | -66.9062 | -66.7611 | -0.045428 | -66.7865 | 56.2306 | 56.4129 | 56.2513 | -67.166 | -0.19172 | -0.016461 | -0.023634 | -0.058996 | 0.13272 | -0.066213 | 0.14469 | -0.4515 | -0.1018 | -0.046643 | -0.071991 | 0.37951 | 0.080535 | -0.081093 | 123.0304 | 122.9807 | 123.1916 | 66.6747 | -123.2386 | 122.9451 | 123.1274 | 122.9658 | 66.669 | -123.4984
2643.7969 | 123.3032 | -66.687 | 56.3416 | -0.0029761 | -0.031931 | -0.0010343 | 0.053081 | -0.0082282 | 0.062289 | 0.015414 | -0.0036937 | -0.00076913 | 0.055467 | 0.041412 | 0.055744 | -66.7381 | -0.039801 | -66.7826 | 56.3159 | 56.2616 | 56.4771 | -66.9062 | -66.7565 | -0.050007 | -66.791 | 56.2306 | 56.4129 | 56.2467 | -67.1706 | -0.21919 | -0.025617 | -0.0511 | -0.095619 | 0.12357 | -0.079948 | 0.13554 | -0.48355 | -0.11096 | -0.06953 | -0.10404 | 0.37951 | 0.071379 | -0.094828 | 123.0029 | 122.9486 | 123.1641 | 66.6472 | -123.2478 | 122.9176 | 123.0999 | 122.9337 | 66.637 | -123.5121
2644.8594 | 123.3261 | -66.6916 | 56.3461 | 0.0046549 | -0.032359 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.041198 | 0.055958 | -66.7381 | -0.048958 | -66.7689 | 56.3159 | 56.2662 | 56.4679 | -66.9016 | -66.7565 | -0.040849 | -66.791 | 56.226 | 56.4221 | 56.2421 | -67.166 | -0.21003 | -0.030194 | -0.046523 | -0.077307 | 0.13272 | -0.079946 | 0.1218 | -0.47439 | -0.12011 | -0.064953 | -0.099458 | 0.37493 | 0.07596 | -0.10398 | 123.0075 | 122.9578 | 123.1595 | 66.6426 | -123.2477 | 122.9176 | 123.1137 | 122.9337 | 66.6507 | -123.5121
2645.7969 | 123.2986 | -66.6733 | 56.3278 | -0.0029761 | -0.032359 | -0.00060686 | 0.053295 | -0.0080146 | 0.062289 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055467 | 0.041412 | 0.055744 | -66.729 | -0.044379 | -66.7735 | 56.3251 | 56.2616 | 56.4679 | -66.9016 | -66.7611 | -0.045428 | -66.7865 | 56.226 | 56.4267 | 56.2467 | -67.166 | -0.22834 | -0.002727 | -0.055677 | -0.10019 | 0.12815 | -0.066215 | 0.14011 | -0.4927 | -0.1018 | -0.087842 | -0.11319 | 0.37951 | 0.098848 | -0.081095 | 122.9984 | 122.9349 | 123.1412 | 66.6289 | -123.2294 | 122.8993 | 123.0999 | 122.92 | 66.6279 | -123.4938
2646.8594 | 123.2391 | -66.7374 | 56.3232 | 0.012286 | -0.032572 | -0.00060686 | 0.053081 | -0.0082282 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.041198 | 0.056171 | -66.7335 | -0.048958 | -66.7735 | 56.3159 | 56.2708 | 56.4771 | -66.897 | -66.7565 | -0.050007 | -66.7956 | 56.2352 | 56.4175 | 56.2467 | -67.1614 | -0.15967 | -0.007306 | 0.003832 | -0.036108 | 0.12357 | -0.052479 | 0.15385 | -0.42404 | -0.088069 | -0.019176 | -0.05826 | 0.36578 | 0.094269 | -0.076517 | 123.0533 | 123.0081 | 123.2145 | 66.6884 | -123.2203 | 122.9725 | 123.1549 | 122.9841 | 66.6874 | -123.4846
2647.7969 | 123.2666 | -66.7236 | 56.3324 | 0.0046549 | -0.031931 | -0.00082046 | 0.053295 | -0.0078008 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055254 | 0.041198 | 0.055744 | -66.7381 | -0.048958 | -66.7735 | 56.3159 | 56.2524 | 56.4725 | -66.897 | -66.752 | -0.045428 | -66.791 | 56.2214 | 56.4175 | 56.2467 | -67.1706 | -0.17341 | -0.016461 | -0.014479 | -0.049841 | 0.12357 | -0.07995 | 0.14012 | -0.44693 | -0.11096 | -0.02833 | -0.067414 | 0.37951 | 0.085114 | -0.085672 | 123.0396 | 122.9761 | 123.1961 | 66.6747 | -123.2294 | 122.9451 | 123.1411 | 122.9704 | 66.6782 | -123.503
2648.7969 | 123.1979 | -66.7648 | 56.3599 | 0.0046549 | -0.032145 | -0.00039306 | 0.052867 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055254 | 0.040985 | 0.056385 | -66.729 | -0.044379 | -66.7689 | 56.3159 | 56.2662 | 56.4679 | -66.9016 | -66.7565 | -0.045428 | -66.7819 | 56.2306 | 56.4175 | 56.2284 | -67.1706 | -0.13679 | -0.043927 | 0.035876 | -0.004064 | 0.13272 | -0.093679 | 0.10807 | -0.40573 | -0.12927 | 0.00829 | -0.017058 | 0.38867 | 0.057648 | -0.13145 | 123.0808 | 123.031 | 123.2328 | 66.7205 | -123.2615 | 122.9954 | 123.1823 | 122.9932 | 66.7194 | -123.5304
2649.7969 | 123.1842 | -66.7557 | 56.3782 | -0.0029761 | -0.032359 | -0.00082046 | 0.053081 | -0.0084418 | 0.062717 | -0.0074779 | -0.0034801 | -0.00034193 | 0.05504 | 0.041412 | 0.055958 | -66.7381 | -0.044379 | -66.7689 | 56.3205 | 56.2662 | 56.4679 | -66.897 | -66.7565 | -0.050007 | -66.7819 | 56.2214 | 56.4129 | 56.2559 | -67.166 | -0.14136 | -0.05766 | 0.017564 | -0.01322 | 0.12814 | -0.11199 | 0.08976 | -0.41031 | -0.15674 | -0.000866 | -0.026214 | 0.38409 | 0.034758 | -0.12229 | 123.0762 | 123.0219 | 123.2236 | 66.7113 | -123.2752 | 122.9771 | 123.1686 | 123.0116 | 66.7057 | -123.5442
2650.7969 | 123.2483 | -66.7465 | 56.3599 | 0.0046549 | -0.032359 | -0.00082046 | 0.052867 | -0.0080146 | 0.062289 | 0.015414 | -0.0036937 | -0.00055553 | 0.055254 | 0.041412 | 0.055744 | -66.7381 | -0.039801 | -66.7735 | 56.3251 | 56.2616 | 56.4725 | -66.9016 | -66.7611 | -0.036271 | -66.791 | 56.2352 | 56.4221 | 56.2513 | -67.166 | -0.1551 | -0.03477 | 0.008409 | -0.026953 | 0.12815 | -0.098258 | 0.11265 | -0.41946 | -0.12469 | -0.0146 | -0.044526 | 0.37493 | 0.062227 | -0.10856 | 123.0716 | 123.0081 | 123.219 | 66.7067 | -123.2615 | 122.9817 | 123.1686 | 122.9978 | 66.7103 | -123.5258
2651.8594 | 123.2025 | -66.7191 | 56.3736 | 0.0046549 | -0.032572 | -0.00082046 | 0.052867 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.042053 | 0.055531 | -66.729 | -0.044379 | -66.7689 | 56.3251 | 56.2753 | 56.4679 | -66.9016 | -66.7611 | -0.050007 | -66.791 | 56.226 | 56.4175 | 56.2467 | -67.166 | -0.18256 | -0.048503 | -0.009901 | -0.049841 | 0.13272 | -0.098254 | 0.094338 | -0.44693 | -0.14758 | -0.042066 | -0.071992 | 0.37493 | 0.043915 | -0.12687 | 123.0441 | 122.9944 | 123.187 | 66.6747 | -123.2752 | 122.9451 | 123.1366 | 122.9658 | 66.669 | -123.5396
2652.7969 | 123.2117 | -66.7648 | 56.3553 | 0.012286 | -0.032359 | -0.00060686 | 0.053081 | -0.0084418 | 0.062289 | 0.00015261 | -0.0039075 | -0.00076913 | 0.055467 | 0.041626 | 0.055958 | -66.7335 | -0.048958 | -66.7735 | 56.3205 | 56.257 | 56.4725 | -66.9062 | -66.7611 | -0.040849 | -66.7865 | 56.2214 | 56.4221 | 56.2559 | -67.1706 | -0.14137 | -0.034772 | 0.031298 | -0.008642 | 0.13272 | -0.09826 | 0.11723 | -0.40573 | -0.13385 | 0.003711 | -0.021637 | 0.38409 | 0.066804 | -0.099403 | 123.0853 | 123.0219 | 123.2373 | 66.7159 | -123.2615 | 122.9863 | 123.1869 | 123.0207 | 66.724 | -123.5258
2653.8594 | 123.3078 | -66.7145 | 56.3141 | -0.0029761 | -0.032145 | -0.00082046 | 0.053295 | -0.0080146 | 0.062717 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.041626 | 0.055744 | -66.7335 | -0.048958 | -66.7735 | 56.3205 | 56.2616 | 56.4679 | -66.8925 | -66.7657 | -0.050007 | -66.7865 | 56.2306 | 56.4221 | 56.2559 | -67.166 | -0.17798 | 0.006427 | -0.019056 | -0.058996 | 0.11899 | -0.052482 | 0.15385 | -0.4515 | -0.083492 | -0.051221 | -0.071991 | 0.37951 | 0.108 | -0.058204 | 123.035 | 122.9761 | 123.1824 | 66.6655 | -123.2065 | 122.9451 | 123.1366 | 122.9704 | 66.6645 | -123.4801
2654.7969 | 123.2254 | -66.7419 | 56.3644 | 0.0046549 | -0.032359 | -0.0010343 | 0.052867 | -0.0078008 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.041626 | 0.055958 | -66.7335 | -0.044379 | -66.7735 | 56.3205 | 56.2708 | 56.4817 | -66.9016 | -66.7611 | -0.050007 | -66.7865 | 56.2352 | 56.4129 | 56.2513 | -67.1614 | -0.15968 | -0.043927 | 0.008409 | -0.031531 | 0.12815 | -0.093678 | 0.11723 | -0.41946 | -0.12927 | -0.019178 | -0.044526 | 0.37493 | 0.048491 | -0.11314 | 123.0625 | 123.0127 | 123.2236 | 66.6976 | -123.2661 | 122.9771 | 123.1549 | 122.9932 | 66.6919 | -123.5258
2655.7969 | 123.2208 | -66.7374 | 56.3507 | -0.0029761 | -0.031931 | -0.00082046 | 0.052867 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055254 | 0.041412 | 0.055744 | -66.7427 | -0.048958 | -66.7735 | 56.3159 | 56.2799 | 56.4725 | -66.9108 | -66.7611 | -0.050007 | -66.791 | 56.2352 | 56.4129 | 56.265 | -67.1706 | -0.17341 | -0.034772 | -0.005325 | -0.036108 | 0.1373 | -0.070787 | 0.12181 | -0.43319 | -0.11553 | -0.023755 | -0.053681 | 0.37951 | 0.062224 | -0.085668 | 123.0533 | 123.0173 | 123.2099 | 66.6884 | -123.2615 | 122.9725 | 123.1503 | 123.0024 | 66.6874 | -123.5213
2656.7969 | 123.1796 | -66.7465 | 56.337 | -0.010607 | -0.032572 | -0.0012479 | 0.053081 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055254 | 0.041412 | 0.055744 | -66.7244 | -0.048958 | -66.7735 | 56.3297 | 56.2662 | 56.4771 | -66.9062 | -66.7565 | -0.050007 | -66.791 | 56.2352 | 56.4129 | 56.2421 | -67.1751 | -0.15968 | -0.007304 | 0.022144 | -0.026953 | 0.13272 | -0.070791 | 0.14012 | -0.42862 | -0.1018 | -0.010021 | -0.044526 | 0.38409 | 0.075957 | -0.094828 | 123.0762 | 123.0127 | 123.2236 | 66.6976 | -123.2432 | 122.9817 | 123.1595 | 122.9887 | 66.6965 | -123.5121
2657.7969 | 123.2117 | -66.7419 | 56.3461 | -0.0029761 | -0.032572 | -0.0010343 | 0.053081 | -0.0080146 | 0.062503 | 0.015414 | -0.0036937 | -0.00076913 | 0.055254 | 0.041412 | 0.055958 | -66.7335 | -0.044379 | -66.7643 | 56.3205 | 56.2662 | 56.4725 | -66.9016 | -66.752 | -0.054586 | -66.7956 | 56.226 | 56.4221 | 56.2559 | -67.1706 | -0.15968 | -0.025616 | 0.008409 | -0.022375 | 0.1373 | -0.079946 | 0.12638 | -0.42862 | -0.12011 | -0.01002 | -0.053683 | 0.37493 | 0.07596 | -0.090247 | 123.0625 | 123.0081 | 123.2145 | 66.6976 | -123.2477 | 122.968 | 123.164 | 122.9978 | 66.6874 | -123.5167
2658.8594 | 123.2117 | -66.7603 | 56.3736 | -0.0029761 | -0.032572 | -0.00060686 | 0.052867 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055467 | 0.041412 | 0.056171 | -66.729 | -0.053537 | -66.7689 | 56.3251 | 56.2662 | 56.4862 | -66.9016 | -66.7565 | -0.045428 | -66.791 | 56.2214 | 56.4175 | 56.2421 | -67.166 | -0.14136 | -0.048503 | 0.031298 | -0.008642 | 0.13272 | -0.10741 | 0.11265 | -0.40573 | -0.15216 | 0.003712 | -0.030793 | 0.37493 | 0.043915 | -0.13145 | 123.0853 | 123.0264 | 123.2465 | 66.7067 | -123.2752 | 122.9817 | 123.1778 | 123.0024 | 66.7148 | -123.5396
2659.7969 | 123.2208 | -66.7236 | 56.3461 | -0.0029761 | -0.032572 | -0.00060686 | 0.052867 | -0.0075872 | 0.06293 | 0.015414 | -0.0039075 | -0.00076913 | 0.055254 | 0.041626 | 0.056171 | -66.7244 | -0.044379 | -66.7735 | 56.3251 | 56.2708 | 56.4725 | -66.9108 | -66.752 | -0.050007 | -66.7865 | 56.2306 | 56.4129 | 56.2513 | -67.1614 | -0.18714 | -0.021037 | -0.000744 | -0.049841 | 0.1373 | -0.075367 | 0.12638 | -0.43777 | -0.11554 | -0.02833 | -0.062836 | 0.37493 | 0.066802 | -0.094826 | 123.0487 | 122.9944 | 123.1961 | 66.6793 | -123.2569 | 122.9542 | 123.1366 | 122.9749 | 66.6736 | -123.5075
2660.7969 | 123.1934 | -66.7648 | 56.337 | -0.0029761 | -0.032572 | -0.00060686 | 0.052867 | -0.0084418 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.05504 | 0.041626 | 0.055744 | -66.7381 | -0.044379 | -66.7781 | 56.3205 | 56.2662 | 56.4771 | -66.9108 | -66.7565 | -0.054586 | -66.8002 | 56.226 | 56.4221 | 56.2605 | -67.166 | -0.14594 | -0.016461 | 0.02672 | -0.013221 | 0.13272 | -0.070791 | 0.14012 | -0.40115 | -0.11096 | 0.00829 | -0.035373 | 0.36578 | 0.085115 | -0.076514 | 123.0853 | 123.031 | 123.2419 | 66.7205 | -123.2478 | 122.9908 | 123.1869 | 123.0253 | 66.7102 | -123.503
2661.8594 | 123.1842 | -66.7694 | 56.3416 | 0.0046549 | -0.032359 | -0.00060686 | 0.052867 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055254 | 0.041626 | 0.056171 | -66.7335 | -0.048958 | -66.7781 | 56.3251 | 56.2799 | 56.4771 | -66.9062 | -66.7611 | -0.050007 | -66.7819 | 56.2352 | 56.4221 | 56.265 | -67.166 | -0.13679 | -0.01646 | 0.035875 | -0.008644 | 0.12815 | -0.061632 | 0.13554 | -0.39657 | -0.10638 | 0.008288 | -0.012481 | 0.38409 | 0.080537 | -0.076513 | 123.0945 | 123.0493 | 123.2465 | 66.7205 | -123.2478 | 123.0046 | 123.1915 | 123.0344 | 66.7194 | -123.5075
2662.7969 | 123.2391 | -66.7557 | 56.3095 | -0.0029761 | -0.032786 | -0.00082046 | 0.052867 | -0.0082282 | 0.062289 | 0.015414 | -0.0039075 | -0.00055553 | 0.055467 | 0.041626 | 0.055744 | -66.7335 | -0.044379 | -66.7735 | 56.3251 | 56.2662 | 56.4817 | -66.9062 | -66.752 | -0.050007 | -66.7819 | 56.2306 | 56.4129 | 56.2513 | -67.1751 | -0.15052 | 0.015584 | 0.022142 | -0.017798 | 0.13272 | -0.043325 | 0.17216 | -0.41946 | -0.078914 | 0.003713 | -0.026214 | 0.39325 | 0.10342 | -0.058205 | 123.0808 | 123.0219 | 123.2373 | 66.7113 | -123.2157 | 122.9863 | 123.1686 | 123.007 | 66.7057 | -123.4846
2663.7969 | 123.1705 | -66.7648 | 56.3324 | -0.0029761 | -0.032786 | -0.00082046 | 0.052867 | -0.0078008 | 0.062289 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055467 | 0.041839 | 0.055958 | -66.7335 | -0.048958 | -66.7781 | 56.3251 | 56.2708 | 56.4679 | -66.897 | -66.7474 | -0.045428 | -66.791 | 56.2306 | 56.4221 | 56.233 | -67.1614 | -0.13221 | -0.007304 | 0.031298 | -0.013221 | 0.11899 | -0.061634 | 0.13554 | -0.39657 | -0.1018 | 0.017447 | -0.026215 | 0.37035 | 0.089693 | -0.099407 | 123.0899 | 123.0356 | 123.2328 | 66.7159 | -123.2294 | 122.9954 | 123.1869 | 122.9978 | 66.7194 | -123.4938
2664.8594 | 123.1934 | -66.7603 | 56.3599 | -0.018238 | -0.032572 | -0.00060686 | 0.053295 | -0.0082282 | 0.062289 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055254 | 0.041412 | 0.055958 | -66.729 | -0.044379 | -66.7689 | 56.3251 | 56.2616 | 56.4725 | -66.9016 | -66.7565 | -0.054586 | -66.7865 | 56.2352 | 56.4221 | 56.2376 | -67.1706 | -0.14136 | -0.03477 | 0.031298 | -0.008642 | 0.13272 | -0.098258 | 0.11265 | -0.41031 | -0.12469 | 0.003712 | -0.026215 | 0.38409 | 0.062227 | -0.12229 | 123.0853 | 123.0219 | 123.2328 | 66.7159 | -123.2615 | 122.9954 | 123.1823 | 122.9978 | 66.7057 | -123.5304
2665.7969 | 123.175 | -66.7877 | 56.3278 | 0.0046549 | -0.032786 | -0.0010343 | 0.053081 | -0.0080146 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.054826 | 0.041412 | 0.055744 | -66.7335 | -0.044379 | -66.7826 | 56.3205 | 56.2616 | 56.4817 | -66.9016 | -66.7611 | -0.050007 | -66.791 | 56.2306 | 56.4221 | 56.265 | -67.1797 | -0.1139 | -0.007306 | 0.054186 | 0.005089 | 0.11899 | -0.066215 | 0.15385 | -0.392 | -0.097225 | 0.026599 | -0.003327 | 0.38867 | 0.09427 | -0.06278 | 123.1082 | 123.0493 | 123.2694 | 66.7433 | -123.2294 | 123.0183 | 123.2098 | 123.0528 | 66.7377 | -123.5075
2666.7969 | 123.3032 | -66.7191 | 56.3187 | 0.0046549 | -0.032572 | -0.00082046 | 0.053295 | -0.0082282 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055254 | 0.041412 | 0.056171 | -66.7335 | -0.048958 | -66.7735 | 56.3159 | 56.257 | 56.4771 | -66.9016 | -66.7565 | -0.045428 | -66.791 | 56.2352 | 56.4221 | 56.2513 | -67.1706 | -0.18256 | -0.002729 | -0.014479 | -0.054419 | 0.12815 | -0.061639 | 0.15843 | -0.4515 | -0.083492 | -0.037487 | -0.071992 | 0.37951 | 0.10342 | -0.067361 | 123.035 | 122.9761 | 123.1961 | 66.6701 | -123.2203 | 122.9542 | 123.1411 | 122.9704 | 66.6736 | -123.4892
2667.8594 | 123.1613 | -66.774 | 56.3736 | 0.0046549 | -0.032572 | -0.00082046 | 0.052867 | -0.0082282 | 0.062289 | 0.0077831 | -0.0036937 | -0.00055553 | 0.05504 | 0.041626 | 0.055958 | -66.7335 | -0.053537 | -66.7735 | 56.3297 | 56.257 | 56.4725 | -66.9016 | -66.7565 | -0.050007 | -66.7865 | 56.2306 | 56.4129 | 56.2421 | -67.166 | -0.12763 | -0.043925 | 0.040453 | 0.000513 | 0.12815 | -0.11657 | 0.098917 | -0.39199 | -0.143 | 0.017445 | -0.012482 | 0.37951 | 0.039336 | -0.13145 | 123.1037 | 123.031 | 123.2465 | 66.7204 | -123.2752 | 123.0046 | 123.1869 | 123.0161 | 66.724 | -123.5396
2668.7969 | 123.3032 | -66.7191 | 56.2912 | 0.0046549 | -0.032786 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | 0.00015261 | -0.0032665 | -0.00034193 | 0.055467 | 0.041626 | 0.055744 | -66.729 | -0.058115 | -66.7735 | 56.3251 | 56.2662 | 56.4771 | -66.9016 | -66.7565 | -0.059164 | -66.791 | 56.2306 | 56.4221 | 56.2467 | -67.1706 | -0.18256 | 0.033894 | -0.009901 | -0.054419 | 0.12815 | -0.025015 | 0.18589 | -0.4515 | -0.060604 | -0.037487 | -0.071992 | 0.37951 | 0.13089 | -0.044474 | 123.0441 | 122.9852 | 123.1961 | 66.6609 | -123.1928 | 122.9496 | 123.1411 | 122.9658 | 66.6599 | -123.4618
2669.7969 | 123.2849 | -66.7191 | 56.2912 | 0.019917 | -0.032572 | -0.00082046 | 0.053508 | -0.0082282 | 0.062717 | -0.0074779 | -0.0032665 | -0.00055553 | 0.055254 | 0.041626 | 0.056171 | -66.7335 | -0.053537 | -66.7781 | 56.3159 | 56.2753 | 56.4725 | -66.897 | -66.752 | -0.054586 | -66.791 | 56.226 | 56.4221 | 56.2513 | -67.166 | -0.17799 | 0.024737 | -0.014479 | -0.058998 | 0.11899 | -0.015857 | 0.18131 | -0.44693 | -0.065183 | -0.032908 | -0.071992 | 0.37493 | 0.13089 | -0.039895 | 123.035 | 122.9944 | 123.1916 | 66.6655 | -123.1882 | 122.9451 | 123.1411 | 122.9704 | 66.6645 | -123.4572
2670.8594 | 123.3078 | -66.7603 | 56.3049 | -0.010607 | -0.033 | -0.00060686 | 0.053081 | -0.0080146 | 0.062289 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055254 | 0.041412 | 0.055958 | -66.7381 | -0.053537 | -66.7826 | 56.3159 | 56.2662 | 56.4771 | -66.9062 | -66.752 | -0.050007 | -66.7956 | 56.2306 | 56.4221 | 56.2467 | -67.1614 | -0.14594 | 0.011004 | 0.022142 | -0.022377 | 0.12357 | -0.038748 | 0.17216 | -0.40115 | -0.074337 | 0.008291 | -0.035372 | 0.36578 | 0.11716 | -0.058207 | 123.0762 | 123.0264 | 123.2373 | 66.7067 | -123.2111 | 122.9908 | 123.1823 | 123.007 | 66.7102 | -123.4663
2671.7969 | 123.3124 | -66.7374 | 56.3004 | -0.0029761 | -0.032145 | -0.00060686 | 0.053081 | -0.0084418 | 0.062289 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055467 | 0.041412 | 0.055958 | -66.7335 | -0.048958 | -66.7781 | 56.3159 | 56.257 | 56.4771 | -66.8925 | -66.7565 | -0.054586 | -66.7865 | 56.226 | 56.4221 | 56.2421 | -67.1706 | -0.1551 | 0.015582 | 0.003832 | -0.040687 | 0.11441 | -0.043328 | 0.17674 | -0.43319 | -0.074338 | -0.019176 | -0.049103 | 0.38409 | 0.12174 | -0.058207 | 123.0533 | 122.9944 | 123.2145 | 66.6884 | -123.1928 | 122.9634 | 123.1595 | 122.9795 | 66.6828 | -123.4709
2672.7969 | 123.2437 | -66.7419 | 56.337 | -0.0029761 | -0.032786 | -0.00060686 | 0.053295 | -0.0078008 | 0.062717 | 0.00015261 | -0.0034801 | -0.00034193 | 0.05504 | 0.041839 | 0.055744 | -66.7335 | -0.053537 | -66.7735 | 56.3251 | 56.2662 | 56.4771 | -66.9016 | -66.7474 | -0.054586 | -66.791 | 56.2306 | 56.4175 | 56.2605 | -67.1706 | -0.15968 | -0.011882 | 0.008409 | -0.031531 | 0.12815 | -0.070791 | 0.14012 | -0.42862 | -0.10638 | -0.005442 | -0.049104 | 0.37951 | 0.080536 | -0.076514 | 123.067 | 123.0081 | 123.219 | 66.6884 | -123.2386 | 122.9725 | 123.1595 | 123.0024 | 66.6874 | -123.5075
2673.8594 | 123.1384 | -66.7694 | 56.3461 | 0.0046549 | -0.032786 | -0.0010343 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.041626 | 0.055531 | -66.7335 | -0.053537 | -66.7781 | 56.3205 | 56.2662 | 56.4725 | -66.9016 | -66.7657 | -0.050007 | -66.7865 | 56.226 | 56.4221 | 56.2513 | -67.1706 | -0.13221 | -0.025616 | 0.035875 | -0.008644 | 0.12357 | -0.079946 | 0.12638 | -0.40115 | -0.12011 | 0.00371 | -0.01706 | 0.38409 | 0.07596 | -0.094826 | 123.0899 | 123.0356 | 123.2419 | 66.7159 | -123.2477 | 122.9954 | 123.1915 | 123.0207 | 66.7194 | -123.5167
2674.7969 | 123.2529 | -66.7328 | 56.3507 | 0.0046549 | -0.032786 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.041626 | 0.055744 | -66.7335 | -0.044379 | -66.7826 | 56.3205 | 56.2753 | 56.4771 | -66.8787 | -66.7474 | -0.054586 | -66.7819 | 56.2306 | 56.4267 | 56.2193 | -67.1706 | -0.14594 | -0.030194 | -0.000746 | -0.049843 | 0.096093 | -0.075366 | 0.12638 | -0.43777 | -0.12011 | -0.014597 | -0.049102 | 0.38867 | 0.07596 | -0.13145 | 123.0533 | 123.0081 | 123.2099 | 66.6884 | -123.2294 | 122.9634 | 123.1595 | 122.952 | 66.6782 | -123.5213
2675.8594 | 123.1934 | -66.7694 | 56.3736 | -0.010607 | -0.032786 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055681 | 0.041839 | 0.056171 | -66.7335 | -0.048958 | -66.7735 | 56.3205 | 56.2799 | 56.4725 | -66.9016 | -66.7565 | -0.050007 | -66.791 | 56.226 | 56.4175 | 56.2376 | -67.166 | -0.13221 | -0.053082 | 0.035875 | -0.004065 | 0.12815 | -0.093675 | 0.098917 | -0.39657 | -0.14758 | 0.012867 | -0.021638 | 0.37493 | 0.043915 | -0.13603 | 123.0899 | 123.0493 | 123.2419 | 66.7205 | -123.2752 | 122.9954 | 123.1869 | 123.007 | 66.7194 | -123.5396
2676.7969 | 123.3124 | -66.7282 | 56.3416 | 0.0046549 | -0.032786 | -0.00082046 | 0.053508 | -0.0075872 | 0.062717 | -0.0074779 | -0.0034801 | -0.00076913 | 0.055254 | 0.041839 | 0.055317 | -66.7335 | -0.044379 | -66.7735 | 56.3205 | 56.257 | 56.4771 | -66.9062 | -66.7565 | -0.050007 | -66.7956 | 56.2306 | 56.4175 | 56.2513 | -67.1706 | -0.17799 | -0.021039 | -0.005324 | -0.045264 | 0.13272 | -0.084527 | 0.13554 | -0.44235 | -0.11096 | -0.028332 | -0.067416 | 0.37493 | 0.075958 | -0.090249 | 123.0487 | 122.9852 | 123.2053 | 66.6838 | -123.2478 | 122.9588 | 123.1457 | 122.9795 | 66.6782 | -123.5121
2677.7969 | 123.2758 | -66.7236 | 56.3187 | -0.0029761 | -0.032572 | -0.00060686 | 0.053081 | -0.0078008 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055467 | 0.041839 | 0.055744 | -66.7335 | -0.058115 | -66.7781 | 56.3251 | 56.2708 | 56.4725 | -66.9016 | -66.7611 | -0.059164 | -66.7865 | 56.2306 | 56.4221 | 56.2559 | -67.166 | -0.17799 | 0.006428 | -0.009901 | -0.05442 | 0.12357 | -0.047902 | 0.15385 | -0.44235 | -0.08807 | -0.037488 | -0.062836 | 0.37951 | 0.10342 | -0.062782 | 123.0487 | 122.9944 | 123.1961 | 66.6655 | -123.2203 | 122.9542 | 123.1457 | 122.9795 | 66.6645 | -123.4846
2678.8594 | 123.2483 | -66.7328 | 56.3461 | -0.0029761 | -0.032572 | -0.0010343 | 0.053081 | -0.0080146 | 0.062717 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055467 | 0.041412 | 0.055744 | -66.7335 | -0.053537 | -66.7826 | 56.3205 | 56.257 | 56.4634 | -66.9016 | -66.7474 | -0.050007 | -66.791 | 56.2306 | 56.4129 | 56.2605 | -67.1706 | -0.16883 | -0.025616 | -0.000746 | -0.049843 | 0.11899 | -0.089104 | 0.11723 | -0.43777 | -0.11554 | -0.014597 | -0.058259 | 0.37951 | 0.066802 | -0.085669 | 123.0533 | 122.9898 | 123.1961 | 66.6793 | -123.2477 | 122.9634 | 123.1457 | 122.9932 | 66.6828 | -123.5167
2679.7969 | 123.2574 | -66.7053 | 56.337 | -0.0029761 | -0.032572 | -0.00060686 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055467 | 0.041626 | 0.056171 | -66.7427 | -0.053537 | -66.7872 | 56.3251 | 56.2708 | 56.4771 | -66.897 | -66.7565 | -0.050007 | -66.7956 | 56.2306 | 56.4221 | 56.2193 | -67.166 | -0.19172 | -0.011882 | -0.037369 | -0.081887 | 0.10983 | -0.066212 | 0.14012 | -0.46066 | -0.10638 | -0.05122 | -0.090304 | 0.37036 | 0.085115 | -0.11772 | 123.0304 | 122.9761 | 123.1824 | 66.6518 | -123.234 | 122.9359 | 123.1274 | 122.9246 | 66.6553 | -123.503
2680.7969 | 123.2117 | -66.7419 | 56.3553 | 0.0046549 | -0.032572 | -0.00039306 | 0.052867 | -0.0080146 | 0.062503 | 0.0077831 | -0.0032665 | -0.00055553 | 0.055254 | 0.041839 | 0.055958 | -66.729 | -0.048958 | -66.7781 | 56.3251 | 56.2799 | 56.4725 | -66.9016 | -66.752 | -0.059164 | -66.791 | 56.2306 | 56.4129 | 56.2559 | -67.166 | -0.15968 | -0.030193 | 0.012987 | -0.03611 | 0.12357 | -0.075365 | 0.11723 | -0.42404 | -0.12469 | -0.01002 | -0.049104 | 0.37493 | 0.057646 | -0.099403 | 123.067 | 123.0219 | 123.2145 | 66.693 | -123.2569 | 122.9725 | 123.1549 | 122.9978 | 66.6828 | -123.5213
2681.8594 | 123.262 | -66.7236 | 56.3095 | -0.010607 | -0.032786 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.053537 | -66.7826 | 56.3159 | 56.2616 | 56.4771 | -66.897 | -66.7565 | -0.054586 | -66.791 | 56.2306 | 56.4084 | 56.233 | -67.1797 | -0.17341 | 0.006427 | -0.009901 | -0.058998 | 0.11441 | -0.047904 | 0.16758 | -0.45608 | -0.078914 | -0.032909 | -0.067414 | 0.38867 | 0.098845 | -0.076519 | 123.0396 | 122.9852 | 123.2007 | 66.6701 | -123.2065 | 122.9542 | 123.132 | 122.9566 | 66.669 | -123.4892
2682.7969 | 123.1934 | -66.7511 | 56.3919 | -0.010607 | -0.032786 | -0.00060686 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.055467 | 0.042053 | 0.055744 | -66.7244 | -0.053537 | -66.7826 | 56.3205 | 56.2753 | 56.4771 | -66.9016 | -66.7565 | -0.054586 | -66.7865 | 56.2306 | 56.4129 | 56.2559 | -67.1751 | -0.15052 | -0.071393 | 0.026722 | -0.031532 | 0.11899 | -0.11657 | 0.085184 | -0.42404 | -0.16131 | -0.005443 | -0.03537 | 0.38867 | 0.021025 | -0.13602 | 123.0716 | 123.0264 | 123.2282 | 66.6976 | -123.2935 | 122.9817 | 123.164 | 123.007 | 66.6965 | -123.567
2683.7969 | 123.2941 | -66.7145 | 56.3599 | 0.0046549 | -0.032786 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | 0.0077831 | -0.0034801 | -0.00034193 | 0.05504 | 0.041839 | 0.055744 | -66.729 | -0.053537 | -66.7781 | 56.3159 | 56.2662 | 56.4679 | -66.9016 | -66.7565 | -0.059164 | -66.7865 | 56.226 | 56.4175 | 56.2376 | -67.1706 | -0.18714 | -0.043927 | -0.014478 | -0.063575 | 0.12357 | -0.093679 | 0.10807 | -0.45608 | -0.13385 | -0.042064 | -0.071991 | 0.38409 | 0.057648 | -0.12229 | 123.0304 | 122.9807 | 123.1824 | 66.6609 | -123.2615 | 122.9405 | 123.132 | 122.952 | 66.6553 | -123.5304
2684.7969 | 123.1293 | -66.7465 | 56.369 | 0.012286 | -0.032786 | -0.00060686 | 0.053081 | -0.0082282 | 0.062717 | 0.015414 | -0.0039075 | -0.00098273 | 0.055467 | 0.042053 | 0.055317 | -66.7335 | -0.048958 | -66.7872 | 56.3205 | 56.2753 | 56.4771 | -66.9108 | -66.7657 | -0.054586 | -66.791 | 56.2352 | 56.4221 | 56.2513 | -67.1706 | -0.16426 | -0.048505 | 0.012987 | -0.040688 | 0.12357 | -0.093677 | 0.10807 | -0.42404 | -0.13385 | -0.019178 | -0.044526 | 0.37951 | 0.053071 | -0.11772 | 123.067 | 123.0219 | 123.2236 | 66.6976 | -123.2798 | 122.9817 | 123.1686 | 122.9978 | 66.6919 | -123.5396
2685.7969 | 123.2025 | -66.7465 | 56.3416 | -0.0029761 | -0.032786 | -0.00060686 | 0.053081 | -0.0084418 | 0.062503 | -0.022739 | -0.0039075 | -0.00055553 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.053537 | -66.7781 | 56.3251 | 56.2616 | 56.4862 | -66.9016 | -66.7565 | -0.059164 | -66.791 | 56.2306 | 56.4129 | 56.2605 | -67.1706 | -0.1551 | -0.01646 | 0.012987 | -0.031532 | 0.12357 | -0.079948 | 0.1447 | -0.42404 | -0.11096 | -0.010021 | -0.044526 | 0.37951 | 0.071379 | -0.081092 | 123.0716 | 123.0081 | 123.2328 | 66.693 | -123.2432 | 122.9771 | 123.1595 | 123.007 | 66.6874 | -123.5121
2686.8594 | 123.2117 | -66.7694 | 56.3599 | -0.0029761 | -0.032786 | -0.00039306 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055681 | 0.042053 | 0.055958 | -66.7335 | -0.058115 | -66.7735 | 56.3297 | 56.2845 | 56.4771 | -66.9016 | -66.7565 | -0.059164 | -66.791 | 56.2306 | 56.4221 | 56.2605 | -67.166 | -0.13221 | -0.030192 | 0.035875 | -0.004065 | 0.12815 | -0.075364 | 0.11723 | -0.39657 | -0.12927 | 0.012867 | -0.021638 | 0.37493 | 0.062227 | -0.099402 | 123.0991 | 123.0539 | 123.2465 | 66.7113 | -123.2615 | 123 | 123.1915 | 123.0299 | 66.7102 | -123.5258
2687.7969 | 123.2025 | -66.7557 | 56.3461 | 0.0046549 | -0.032572 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | 0.0077831 | -0.0032665 | -0.00012813 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.058115 | -66.7735 | 56.3251 | 56.2662 | 56.4817 | -66.9016 | -66.7565 | -0.063743 | -66.7819 | 56.2352 | 56.4221 | 56.2559 | -67.1706 | -0.14594 | -0.021037 | 0.022142 | -0.017798 | 0.12815 | -0.079946 | 0.13554 | -0.41488 | -0.11096 | -0.000866 | -0.026214 | 0.38867 | 0.07596 | -0.090247 | 123.0808 | 123.0219 | 123.2373 | 66.6976 | -123.2477 | 122.9908 | 123.1778 | 123.0116 | 66.6919 | -123.5167
2688.8594 | 123.2986 | -66.7145 | 56.3416 | 0.0046549 | -0.033 | -0.0010343 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.041839 | 0.055744 | -66.7335 | -0.053537 | -66.7781 | 56.3205 | 56.257 | 56.4725 | -66.9016 | -66.752 | -0.063743 | -66.8002 | 56.2306 | 56.4221 | 56.2376 | -67.166 | -0.18714 | -0.021039 | -0.019056 | -0.063575 | 0.12357 | -0.084527 | 0.13096 | -0.4515 | -0.11096 | -0.037485 | -0.085727 | 0.36578 | 0.080537 | -0.10398 | 123.035 | 122.9715 | 123.187 | 66.6609 | -123.2432 | 122.9451 | 123.1366 | 122.952 | 66.6507 | -123.5075
2689.7969 | 123.1934 | -66.7328 | 56.3599 | 0.0046549 | -0.032786 | -0.00060686 | 0.052867 | -0.0084418 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.05504 | 0.041626 | 0.056171 | -66.7335 | -0.053537 | -66.7781 | 56.3297 | 56.2662 | 56.4771 | -66.9062 | -66.7565 | -0.063743 | -66.7865 | 56.2306 | 56.4175 | 56.2513 | -67.1751 | -0.17341 | -0.030192 | -0.000746 | -0.045265 | 0.12815 | -0.093679 | 0.11723 | -0.44235 | -0.12927 | -0.023754 | -0.053681 | 0.38867 | 0.057648 | -0.10856 | 123.0625 | 122.999 | 123.2099 | 66.6793 | -123.2661 | 122.9634 | 123.1503 | 122.9841 | 66.669 | -123.535
2690.7969 | 123.2666 | -66.7328 | 56.3049 | -0.010607 | -0.032786 | -0.00060686 | 0.053722 | -0.0078008 | 0.062503 | -0.015108 | -0.0036937 | -0.00034193 | 0.055467 | 0.042053 | 0.055958 | -66.7381 | -0.058115 | -66.7689 | 56.3205 | 56.2753 | 56.4725 | -66.9016 | -66.7565 | -0.059164 | -66.7865 | 56.2306 | 56.4267 | 56.2467 | -67.166 | -0.16883 | 0.015582 | -0.005324 | -0.036108 | 0.13272 | -0.02959 | 0.16758 | -0.43319 | -0.074337 | -0.023754 | -0.053681 | 0.37951 | 0.12174 | -0.058207 | 123.0533 | 123.0081 | 123.2053 | 66.6747 | -123.2066 | 122.9634 | 123.1595 | 122.9795 | 66.6736 | -123.4709
2691.7969 | 123.2437 | -66.7511 | 56.3782 | -0.0029761 | -0.032786 | -0.00060686 | 0.053508 | -0.0080146 | 0.062503 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055254 | 0.042267 | 0.055744 | -66.729 | -0.053537 | -66.7781 | 56.3251 | 56.2708 | 56.4771 | -66.9108 | -66.7611 | -0.059164 | -66.791 | 56.2306 | 56.4221 | 56.2742 | -67.1751 | -0.15968 | -0.053081 | 0.022143 | -0.026954 | 0.13272 | -0.10741 | 0.098917 | -0.42404 | -0.14758 | -0.010022 | -0.039948 | 0.38409 | 0.043916 | -0.10398 | 123.0762 | 123.0219 | 123.2282 | 66.6976 | -123.289 | 122.9817 | 123.1732 | 123.0253 | 66.6919 | -123.5533
2692.7969 | 123.1934 | -66.7648 | 56.337 | -0.010607 | -0.032786 | -0.00060686 | 0.052867 | -0.0082282 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055467 | 0.041839 | 0.055744 | -66.7381 | -0.053537 | -66.7826 | 56.3251 | 56.2891 | 56.4817 | -66.9062 | -66.7611 | -0.059164 | -66.7865 | 56.2306 | 56.4221 | 56.2788 | -67.1706 | -0.14137 | -0.011882 | 0.02672 | -0.017799 | 0.12357 | -0.047897 | 0.14469 | -0.40573 | -0.10638 | 0.003711 | -0.021637 | 0.38409 | 0.085115 | -0.058199 | 123.0899 | 123.0539 | 123.2465 | 66.7113 | -123.2432 | 122.9954 | 123.1869 | 123.0436 | 66.7057 | -123.5075
2693.7969 | 123.23 | -66.7603 | 56.3736 | 0.0046549 | -0.032786 | -0.0010343 | 0.053295 | -0.0082282 | 0.062717 | 0.0077831 | -0.0034801 | -0.00055553 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.062694 | -66.7735 | 56.3159 | 56.2616 | 56.4817 | -66.9108 | -66.752 | -0.063743 | -66.791 | 56.226 | 56.4221 | 56.2513 | -67.1706 | -0.15052 | -0.05766 | 0.02672 | -0.01322 | 0.1373 | -0.11199 | 0.10807 | -0.41031 | -0.14758 | 0.008291 | -0.030793 | 0.37951 | 0.048494 | -0.12229 | 123.0762 | 123.0219 | 123.2419 | 66.6976 | -123.2844 | 122.9863 | 123.1823 | 123.0116 | 66.6965 | -123.5442
2694.7969 | 123.1567 | -66.7511 | 56.3553 | -0.010607 | -0.032572 | -0.0010343 | 0.053295 | -0.0082282 | 0.062717 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055254 | 0.042053 | 0.055531 | -66.729 | -0.048958 | -66.7689 | 56.3251 | 56.2708 | 56.4817 | -66.9062 | -66.7565 | -0.054586 | -66.7865 | 56.2352 | 56.4221 | 56.2559 | -67.1706 | -0.1551 | -0.030193 | 0.022143 | -0.017797 | 0.1373 | -0.084523 | 0.12638 | -0.41946 | -0.12011 | -0.005443 | -0.03537 | 0.38409 | 0.066804 | -0.099403 | 123.0762 | 123.0219 | 123.2328 | 66.7021 | -123.2615 | 122.9863 | 123.1732 | 123.007 | 66.6965 | -123.5258
2695.7969 | 123.2574 | -66.7236 | 56.3187 | -0.018238 | -0.033213 | -0.0010343 | 0.053295 | -0.0082282 | 0.06293 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055467 | 0.041626 | 0.055744 | -66.7335 | -0.053537 | -66.7735 | 56.3159 | 56.2662 | 56.4725 | -66.897 | -66.7565 | -0.054586 | -66.7865 | 56.2352 | 56.4312 | 56.2559 | -67.1706 | -0.17341 | -0.002729 | -0.009901 | -0.049841 | 0.12357 | -0.052481 | 0.15385 | -0.44693 | -0.083492 | -0.032909 | -0.062836 | 0.38409 | 0.11258 | -0.062782 | 123.0396 | 122.9898 | 123.1961 | 66.6701 | -123.2157 | 122.9588 | 123.1549 | 122.9795 | 66.669 | -123.4892
2696.7969 | 123.2071 | -66.7831 | 56.3416 | -0.0029761 | -0.032786 | -0.00039306 | 0.053295 | -0.0082282 | 0.062717 | -0.0074779 | -0.0034801 | -0.00034193 | 0.055467 | 0.042053 | 0.055744 | -66.7244 | -0.053537 | -66.7689 | 56.3297 | 56.2799 | 56.4817 | -66.9016 | -66.7611 | -0.059164 | -66.7819 | 56.2306 | 56.4267 | 56.2284 | -67.1751 | -0.11848 | -0.011882 | 0.058765 | 0.014246 | 0.13272 | -0.061632 | 0.14012 | -0.392 | -0.11096 | 0.022021 | 0.001252 | 0.39325 | 0.085115 | -0.11314 | 123.1128 | 123.0631 | 123.2648 | 66.7296 | -123.2432 | 123.0137 | 123.2098 | 123.0116 | 66.724 | -123.5167
2697.7969 | 123.1522 | -66.774 | 56.3553 | -0.0029761 | -0.033 | -0.00082046 | 0.053295 | -0.0084418 | 0.063144 | 0.0077831 | -0.0039075 | -0.00076913 | 0.05504 | 0.042267 | 0.055958 | -66.7198 | -0.053537 | -66.7735 | 56.3297 | 56.2616 | 56.4817 | -66.9062 | -66.7474 | -0.063743 | -66.7865 | 56.2306 | 56.4267 | 56.2788 | -67.1751 | -0.13221 | -0.025615 | 0.054188 | 0.000513 | 0.13272 | -0.093681 | 0.12638 | -0.40115 | -0.12469 | 0.026602 | -0.012482 | 0.38867 | 0.071382 | -0.07651 | 123.1037 | 123.0356 | 123.2557 | 66.7204 | -123.2615 | 123.0046 | 123.2007 | 123.0528 | 66.7102 | -123.5304
2698.7969 | 123.2071 | -66.7786 | 56.3187 | -0.0029761 | -0.032572 | -0.00082046 | 0.053295 | -0.0082282 | 0.062503 | -0.015108 | -0.0039075 | -0.00055553 | 0.05504 | 0.041839 | 0.055958 | -66.7381 | -0.053537 | -66.7735 | 56.3297 | 56.2799 | 56.4862 | -66.9016 | -66.7657 | -0.063743 | -66.7819 | 56.2352 | 56.4175 | 56.2467 | -67.1706 | -0.12305 | 0.011006 | 0.040452 | 0.00509 | 0.12815 | -0.038744 | 0.16758 | -0.392 | -0.083492 | 0.012865 | -0.003326 | 0.38867 | 0.098846 | -0.07194 | 123.1082 | 123.0585 | 123.2648 | 66.725 | -123.2203 | 123.0137 | 123.1961 | 123.0253 | 66.7148 | -123.4892
2699.7969 | 123.1613 | -66.7465 | 56.337 | -0.010607 | -0.032786 | -0.00082046 | 0.053295 | -0.0080146 | 0.062289 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055467 | 0.042053 | 0.055744 | -66.7335 | -0.058115 | -66.7735 | 56.3251 | 56.2753 | 56.4817 | -66.9062 | -66.7611 | -0.059164 | -66.7865 | 56.2306 | 56.4221 | 56.2559 | -67.166 | -0.15968 | -0.011882 | 0.012987 | -0.026953 | 0.13272 | -0.061633 | 0.14469 | -0.41946 | -0.10638 | -0.0146 | -0.039948 | 0.37951 | 0.085115 | -0.081092 | 123.0716 | 123.0219 | 123.2282 | 66.6884 | -123.2432 | 122.9771 | 123.1686 | 123.0024 | 66.6874 | -123.503
2700.7969 | 123.3124 | -66.7419 | 56.282 | -0.018238 | -0.033213 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | -0.015108 | -0.0036937 | -0.00055553 | 0.055254 | 0.042053 | 0.055958 | -66.729 | -0.048958 | -66.7826 | 56.3205 | 56.2616 | 56.4679 | -66.9016 | -66.752 | -0.054586 | -66.791 | 56.2306 | 56.4221 | 56.2467 | -67.1706 | -0.15968 | 0.038471 | 0.012987 | -0.040688 | 0.11899 | -0.020438 | 0.18589 | -0.42862 | -0.051448 | -0.01002 | -0.049104 | 0.37951 | 0.14005 | -0.035318 | 123.0625 | 123.0035 | 123.2099 | 66.693 | -123.1837 | 122.9725 | 123.164 | 122.9887 | 66.6874 | -123.4526
2701.8594 | 123.1796 | -66.7694 | 56.3461 | 0.012286 | -0.032786 | -0.0010343 | 0.052867 | -0.0084418 | 0.062717 | -0.0074779 | -0.0039075 | -0.00098273 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.062694 | -66.7735 | 56.3205 | 56.2708 | 56.4725 | -66.9016 | -66.7565 | -0.063743 | -66.791 | 56.2306 | 56.4221 | 56.2376 | -67.166 | -0.13221 | -0.025616 | 0.035875 | -0.004065 | 0.12815 | -0.075367 | 0.12638 | -0.39657 | -0.11554 | 0.012867 | -0.021638 | 0.37493 | 0.07596 | -0.10856 | 123.0899 | 123.0402 | 123.2419 | 66.7067 | -123.2477 | 123 | 123.1915 | 123.007 | 66.7057 | -123.5121
2702.7969 | 123.2666 | -66.7419 | 56.3049 | -0.0029761 | -0.032572 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | -0.015108 | -0.0039075 | -0.00076913 | 0.055254 | 0.042053 | 0.055958 | -66.729 | -0.062694 | -66.7735 | 56.3251 | 56.2662 | 56.4725 | -66.897 | -66.752 | -0.059164 | -66.7865 | 56.2398 | 56.4221 | 56.2513 | -67.1706 | -0.1551 | 0.020161 | 0.012987 | -0.031531 | 0.12357 | -0.038748 | 0.16758 | -0.42862 | -0.065181 | -0.01002 | -0.044526 | 0.38409 | 0.11716 | -0.053628 | 123.067 | 123.0081 | 123.2145 | 66.6792 | -123.202 | 122.9817 | 123.164 | 122.9932 | 66.6828 | -123.4755
2703.7969 | 123.2208 | -66.7603 | 56.3416 | -0.018238 | -0.033 | -0.00082046 | 0.053295 | -0.0082282 | 0.062289 | 0.00015261 | -0.0034801 | -0.00055553 | 0.055254 | 0.041839 | 0.055744 | -66.7335 | -0.058115 | -66.7735 | 56.3297 | 56.2662 | 56.4771 | -66.897 | -66.752 | -0.068322 | -66.791 | 56.226 | 56.4175 | 56.2421 | -67.1797 | -0.13679 | -0.011882 | 0.02672 | -0.01322 | 0.12357 | -0.075369 | 0.13554 | -0.41946 | -0.11554 | 0.008291 | -0.030793 | 0.38867 | 0.075958 | -0.099406 | 123.0899 | 123.0264 | 123.2373 | 66.7021 | -123.2386 | 122.9863 | 123.1778 | 123.0024 | 66.6919 | -123.5213
2704.7969 | 123.3215 | -66.7236 | 56.3324 | 0.0046549 | -0.032786 | -0.0010343 | 0.053295 | -0.0084418 | 0.062289 | 0.0077831 | -0.0039075 | -0.00012813 | 0.055467 | 0.041839 | 0.055531 | -66.7335 | -0.058115 | -66.7689 | 56.3251 | 56.2616 | 56.4817 | -66.9016 | -66.7611 | -0.059164 | -66.7865 | 56.2352 | 56.4175 | 56.233 | -67.1751 | -0.17799 | -0.007304 | -0.009901 | -0.045263 | 0.13272 | -0.070792 | 0.14927 | -0.4515 | -0.097224 | -0.037488 | -0.062836 | 0.38867 | 0.085114 | -0.099407 | 123.0487 | 122.9852 | 123.2053 | 66.6655 | -123.234 | 122.9588 | 123.1411 | 122.9566 | 66.6645 | -123.5075
2705.8594 | 123.2803 | -66.7374 | 56.3416 | -0.010607 | -0.033 | -0.0010343 | 0.053508 | -0.0080146 | 0.062503 | -0.015108 | -0.0036937 | -0.00034193 | 0.055254 | 0.041839 | 0.055958 | -66.7335 | -0.058115 | -66.7735 | 56.3205 | 56.2616 | 56.4862 | -66.9062 | -66.7611 | -0.063743 | -66.7956 | 56.2398 | 56.4221 | 56.2559 | -67.166 | -0.16883 | -0.021039 | 0.003832 | -0.036108 | 0.13272 | -0.079948 | 0.1447 | -0.42862 | -0.1018 | -0.023755 | -0.05826 | 0.37036 | 0.080537 | -0.08567 | 123.0579 | 122.999 | 123.2236 | 66.6793 | -123.2478 | 122.9771 | 123.1595 | 122.9932 | 66.6736 | -123.5075
2706.7969 | 123.2849 | -66.7145 | 56.3324 | -0.010607 | -0.032786 | -0.00060686 | 0.052867 | -0.0084418 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.042053 | 0.055744 | -66.7335 | -0.067272 | -66.7781 | 56.3205 | 56.2662 | 56.4817 | -66.9016 | -66.7565 | -0.063743 | -66.7865 | 56.2352 | 56.4221 | 56.2193 | -67.1751 | -0.18714 | -0.011883 | -0.019056 | -0.063575 | 0.12357 | -0.066213 | 0.14927 | -0.46066 | -0.097224 | -0.042064 | -0.071991 | 0.38867 | 0.089693 | -0.11314 | 123.035 | 122.9807 | 123.1961 | 66.6472 | -123.234 | 122.9497 | 123.1366 | 122.9337 | 66.6507 | -123.5075
2707.8594 | 123.1934 | -66.7328 | 56.3324 | -0.0029761 | -0.033 | -0.0010343 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.042267 | 0.055744 | -66.7381 | -0.053537 | -66.7735 | 56.3297 | 56.2799 | 56.4817 | -66.897 | -66.7565 | -0.059164 | -66.7956 | 56.2443 | 56.4129 | 56.2467 | -67.1751 | -0.16425 | -0.002726 | -0.005324 | -0.040686 | 0.12357 | -0.052476 | 0.14927 | -0.44235 | -0.088067 | -0.023754 | -0.062838 | 0.37951 | 0.080535 | -0.085672 | 123.0625 | 123.0127 | 123.2145 | 66.6793 | -123.2294 | 122.9771 | 123.1457 | 122.9795 | 66.6736 | -123.5075
2708.7969 | 123.2666 | -66.7328 | 56.2912 | -0.010607 | -0.033 | -0.00060686 | 0.053295 | -0.0082282 | 0.062503 | -0.015108 | -0.0041211 | -0.00034193 | 0.055254 | 0.04248 | 0.055744 | -66.7335 | -0.062694 | -66.7689 | 56.3159 | 56.2616 | 56.4725 | -66.9016 | -66.7611 | -0.068322 | -66.7865 | 56.2352 | 56.4175 | 56.2559 | -67.1706 | -0.16883 | 0.024737 | -0.000746 | -0.036108 | 0.13272 | -0.029594 | 0.18131 | -0.43777 | -0.056026 | -0.028333 | -0.053681 | 0.38409 | 0.12631 | -0.035316 | 123.0487 | 122.9944 | 123.2053 | 66.6701 | -123.1928 | 122.968 | 123.1503 | 122.9887 | 66.6645 | -123.4618
2709.7969 | 123.2758 | -66.7191 | 56.3141 | -0.0029761 | -0.032572 | -0.00060686 | 0.053295 | -0.0082282 | 0.062717 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055254 | 0.042267 | 0.055958 | -66.729 | -0.062694 | -66.7781 | 56.3159 | 56.2662 | 56.4771 | -66.9062 | -66.7565 | -0.063743 | -66.7865 | 56.2306 | 56.4175 | 56.265 | -67.166 | -0.18714 | 0.001849 | -0.009901 | -0.058998 | 0.12815 | -0.047903 | 0.163 | -0.44693 | -0.083492 | -0.037487 | -0.067414 | 0.37951 | 0.10342 | -0.049047 | 123.035 | 122.9852 | 123.1961 | 66.6564 | -123.2203 | 122.9496 | 123.1366 | 122.9841 | 66.6553 | -123.4801
2710.7969 | 123.2666 | -66.7236 | 56.3095 | -0.0029761 | -0.032786 | -0.0010343 | 0.053295 | -0.0082282 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055467 | 0.042267 | 0.055531 | -66.7381 | -0.067272 | -66.7826 | 56.3205 | 56.2662 | 56.4725 | -66.9016 | -66.7611 | -0.068322 | -66.791 | 56.2352 | 56.4221 | 56.2559 | -67.1706 | -0.17799 | 0.011005 | -0.014479 | -0.058998 | 0.11899 | -0.043325 | 0.163 | -0.44693 | -0.074336 | -0.037488 | -0.067414 | 0.37951 | 0.11258 | -0.053626 | 123.0441 | 122.9898 | 123.1961 | 66.6564 | -123.2111 | 122.9588 | 123.1457 | 122.9795 | 66.6553 | -123.4801
2711.8594 | 123.2071 | -66.7694 | 56.3232 | 0.012286 | -0.032786 | -0.00060686 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0034801 | -0.00034193 | 0.05504 | 0.042053 | 0.055317 | -66.7335 | -0.067272 | -66.7735 | 56.3251 | 56.2616 | 56.4771 | -66.8925 | -66.7565 | -0.059164 | -66.791 | 56.2398 | 56.4312 | 56.2559 | -67.1751 | -0.12305 | 0.001851 | 0.035875 | -0.004065 | 0.11899 | -0.061637 | 0.15385 | -0.40573 | -0.083491 | 0.012867 | -0.021638 | 0.38409 | 0.108 | -0.067359 | 123.0945 | 123.031 | 123.2465 | 66.7021 | -123.2157 | 123.0092 | 123.2007 | 123.0253 | 66.7102 | -123.4984
2712.7969 | 123.2666 | -66.7145 | 56.3461 | -0.0029761 | -0.032786 | -0.00039306 | 0.053508 | -0.0082282 | 0.062717 | -0.0074779 | -0.0036937 | -0.00076913 | 0.05504 | 0.042053 | 0.055531 | -66.7244 | -0.067272 | -66.7735 | 56.3297 | 56.257 | 56.4771 | -66.897 | -66.7611 | -0.0729 | -66.7865 | 56.2352 | 56.4312 | 56.2421 | -67.1706 | -0.18256 | -0.016459 | -0.009899 | -0.058996 | 0.12357 | -0.089104 | 0.13096 | -0.45608 | -0.11096 | -0.046643 | -0.071991 | 0.38409 | 0.085117 | -0.10398 | 123.0441 | 122.9715 | 123.1916 | 66.6472 | -123.2432 | 122.9497 | 123.1457 | 122.9566 | 66.6416 | -123.5167
2713.7969 | 123.2391 | -66.7419 | 56.3416 | 0.0046549 | -0.033 | -0.00060686 | 0.053295 | -0.0078008 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055254 | 0.042053 | 0.055744 | -66.7381 | -0.067272 | -66.7826 | 56.3205 | 56.2616 | 56.4771 | -66.897 | -66.7611 | -0.063743 | -66.791 | 56.2306 | 56.4267 | 56.2238 | -67.1706 | -0.1551 | -0.021039 | 0.003831 | -0.040688 | 0.11441 | -0.079948 | 0.13554 | -0.42862 | -0.11096 | -0.019178 | -0.049104 | 0.37951 | 0.085115 | -0.11772 | 123.0625 | 123.0035 | 123.219 | 66.6747 | -123.2386 | 122.9725 | 123.1686 | 122.9658 | 66.6782 | -123.5121
2714.7969 | 123.2758 | -66.7328 | 56.3278 | -0.010607 | -0.032572 | -0.00082046 | 0.053295 | -0.0078008 | 0.062289 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.04248 | 0.055531 | -66.7335 | -0.058115 | -66.7781 | 56.3205 | 56.2708 | 56.4817 | -66.9062 | -66.7565 | -0.063743 | -66.791 | 56.2398 | 56.4267 | 56.2605 | -67.1751 | -0.17341 | -0.007306 | -0.000746 | -0.045265 | 0.12815 | -0.057057 | 0.15385 | -0.44235 | -0.088069 | -0.023754 | -0.058259 | 0.38409 | 0.098848 | -0.067359 | 123.0533 | 123.0036 | 123.2145 | 66.6747 | -123.234 | 122.9725 | 123.1595 | 122.9932 | 66.669 | -123.503
2715.7969 | 123.2712 | -66.7236 | 56.3278 | -0.0029761 | -0.033 | -0.0010343 | 0.053508 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00055553 | 0.054826 | 0.042053 | 0.055531 | -66.7335 | -0.058115 | -66.7781 | 56.3159 | 56.257 | 56.4725 | -66.8925 | -66.7611 | -0.0729 | -66.7819 | 56.2306 | 56.4221 | 56.2193 | -67.1751 | -0.16883 | -0.011884 | -0.009901 | -0.05442 | 0.11441 | -0.070794 | 0.14469 | -0.4515 | -0.097225 | -0.037488 | -0.058257 | 0.39325 | 0.09427 | -0.10857 | 123.0396 | 122.9807 | 123.1961 | 66.6655 | -123.2203 | 122.9542 | 123.1457 | 122.9429 | 66.6507 | -123.503
2716.7969 | 123.2712 | -66.7374 | 56.3232 | -0.0029761 | -0.033 | -0.00060686 | 0.053722 | -0.0082282 | 0.062503 | 0.015414 | -0.0039075 | -0.00055553 | 0.055254 | 0.042053 | 0.055744 | -66.729 | -0.062694 | -66.7735 | 56.3205 | 56.2616 | 56.4679 | -66.897 | -66.7565 | -0.082058 | -66.7956 | 56.2306 | 56.4175 | 56.233 | -67.1751 | -0.15967 | -0.002728 | 0.00841 | -0.036108 | 0.12357 | -0.061637 | 0.14469 | -0.43777 | -0.092647 | -0.019176 | -0.05826 | 0.37951 | 0.094269 | -0.090252 | 123.0579 | 122.999 | 123.2053 | 66.6747 | -123.2203 | 122.968 | 123.1549 | 122.9704 | 66.6553 | -123.4984
2717.7969 | 123.3032 | -66.7328 | 56.3461 | -0.0029761 | -0.033 | -0.00082046 | 0.053722 | -0.0084418 | 0.062289 | 0.00015261 | -0.0034801 | -0.00034193 | 0.05504 | 0.042053 | 0.055531 | -66.7381 | -0.067272 | -66.7781 | 56.3251 | 56.2616 | 56.4771 | -66.9062 | -66.7611 | -0.068322 | -66.791 | 56.2352 | 56.4175 | 56.2376 | -67.1751 | -0.17341 | -0.021037 | -0.005324 | -0.045265 | 0.12815 | -0.084525 | 0.13096 | -0.44235 | -0.11096 | -0.028333 | -0.058259 | 0.38409 | 0.071381 | -0.10856 | 123.0579 | 122.9944 | 123.2099 | 66.6655 | -123.2523 | 122.968 | 123.1503 | 122.9704 | 66.6645 | -123.5213
2718.7969 | 123.3261 | -66.6916 | 56.3507 | -0.010607 | -0.033213 | -0.00082046 | 0.053081 | -0.0084418 | 0.062503 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055254 | 0.042267 | 0.055531 | -66.7381 | -0.062694 | -66.7689 | 56.3205 | 56.257 | 56.4679 | -66.9062 | -66.7611 | -0.068322 | -66.7956 | 56.226 | 56.4221 | 56.2605 | -67.1706 | -0.21461 | -0.030194 | -0.046523 | -0.077307 | 0.1373 | -0.093682 | 0.11723 | -0.47897 | -0.12469 | -0.069532 | -0.10404 | 0.37493 | 0.071382 | -0.090247 | 123.0121 | 122.9486 | 123.1595 | 66.6289 | -123.2569 | 122.9176 | 123.1137 | 122.952 | 66.6233 | -123.5213
2719.8594 | 123.2025 | -66.7557 | 56.3461 | -0.0029761 | -0.033213 | -0.0010343 | 0.053081 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.042694 | 0.055958 | -66.7335 | -0.058115 | -66.7781 | 56.3251 | 56.2616 | 56.4862 | -66.9062 | -66.7565 | -0.059164 | -66.7865 | 56.2352 | 56.4175 | 56.2559 | -67.1751 | -0.15052 | -0.021037 | 0.022142 | -0.022377 | 0.12815 | -0.084525 | 0.14012 | -0.41946 | -0.11096 | -0.000866 | -0.030793 | 0.38867 | 0.071381 | -0.090247 | 123.0808 | 123.0173 | 123.2419 | 66.6976 | -123.2523 | 122.9908 | 123.1732 | 123.0116 | 66.6965 | -123.5213
2720.7969 | 123.3353 | -66.7145 | 56.3416 | 0.0046549 | -0.033641 | -0.00082046 | 0.053295 | -0.0082282 | 0.062717 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.042053 | 0.055958 | -66.7381 | -0.062694 | -66.7735 | 56.3251 | 56.257 | 56.4771 | -66.9062 | -66.7611 | -0.063743 | -66.791 | 56.2352 | 56.4175 | 56.2467 | -67.1706 | -0.19172 | -0.01646 | -0.023634 | -0.058996 | 0.13272 | -0.084527 | 0.13554 | -0.45608 | -0.10638 | -0.046643 | -0.076569 | 0.37951 | 0.075958 | -0.094828 | 123.0396 | 122.9715 | 123.1916 | 66.6518 | -123.2478 | 122.9497 | 123.132 | 122.9612 | 66.6507 | -123.5121
2721.7969 | 123.2849 | -66.7191 | 56.3232 | -0.010607 | -0.033213 | -0.0012479 | 0.053295 | -0.0082282 | 0.062503 | -0.0074779 | -0.0041211 | -0.00055553 | 0.055467 | 0.042267 | 0.055317 | -66.7335 | -0.067272 | -66.7689 | 56.3251 | 56.2524 | 56.4771 | -66.8879 | -66.7611 | -0.068322 | -66.7956 | 56.226 | 56.4175 | 56.2376 | -67.1751 | -0.16883 | 0.001851 | -0.014479 | -0.049841 | 0.11899 | -0.070795 | 0.15385 | -0.45608 | -0.097226 | -0.042066 | -0.076571 | 0.37951 | 0.094269 | -0.085674 | 123.0441 | 122.9715 | 123.1961 | 66.6518 | -123.2111 | 122.9451 | 123.1366 | 122.9566 | 66.6507 | -123.4984
2722.7969 | 123.2986 | -66.6824 | 56.3461 | 0.0046549 | -0.033 | -0.0010343 | 0.053295 | -0.0080146 | 0.062503 | 0.00015261 | -0.0036937 | -0.00098273 | 0.055254 | 0.04248 | 0.055744 | -66.729 | -0.067272 | -66.7826 | 56.3297 | 56.2845 | 56.4862 | -66.8925 | -66.752 | -0.068322 | -66.791 | 56.226 | 56.4175 | 56.2284 | -67.1706 | -0.21003 | -0.016459 | -0.046522 | -0.1002 | 0.10983 | -0.061631 | 0.14012 | -0.48813 | -0.12011 | -0.069529 | -0.10861 | 0.37951 | 0.071381 | -0.11772 | 123.0121 | 122.9669 | 123.1687 | 66.6152 | -123.2386 | 122.9085 | 123.0999 | 122.9108 | 66.6141 | -123.5167
2723.8594 | 123.262 | -66.7328 | 56.3278 | -0.0029761 | -0.033 | -0.00082046 | 0.053508 | -0.0084418 | 0.062717 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.042267 | 0.055744 | -66.7335 | -0.058115 | -66.7781 | 56.3251 | 56.257 | 56.4771 | -66.9016 | -66.7657 | -0.068322 | -66.7865 | 56.2352 | 56.4221 | 56.2376 | -67.166 | -0.16883 | -0.002727 | -0.000746 | -0.045265 | 0.12357 | -0.070794 | 0.14927 | -0.43319 | -0.092647 | -0.032911 | -0.053681 | 0.37951 | 0.09427 | -0.090252 | 123.0579 | 122.9898 | 123.2099 | 66.6747 | -123.2294 | 122.968 | 123.1549 | 122.9704 | 66.6645 | -123.4938
2724.7969 | 123.2895 | -66.7282 | 56.3828 | 0.0046549 | -0.033427 | -0.00082046 | 0.053508 | -0.0082282 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.05504 | 0.042267 | 0.055958 | -66.729 | -0.062694 | -66.7826 | 56.3251 | 56.2616 | 56.4771 | -66.9016 | -66.7749 | -0.068322 | -66.7819 | 56.2352 | 56.4312 | 56.2421 | -67.1706 | -0.17341 | -0.057658 | -0.000746 | -0.054421 | 0.11899 | -0.12115 | 0.09434 | -0.44235 | -0.14758 | -0.046647 | -0.05368 | 0.38867 | 0.048496 | -0.1406 | 123.0533 | 122.9898 | 123.2053 | 66.6655 | -123.2844 | 122.9634 | 123.1595 | 122.9704 | 66.6599 | -123.5533
2725.7969 | 123.3032 | -66.6916 | 56.3553 | 0.0046549 | -0.033 | -0.00082046 | 0.053295 | -0.0084418 | 0.062503 | -0.0074779 | -0.0039075 | -0.00055553 | 0.055254 | 0.042267 | 0.055531 | -66.7335 | -0.067272 | -66.7735 | 56.3205 | 56.257 | 56.4862 | -66.9016 | -66.7611 | -0.068322 | -66.791 | 56.2306 | 56.4221 | 56.2421 | -67.1751 | -0.21003 | -0.034772 | -0.041945 | -0.081885 | 0.12815 | -0.09826 | 0.13096 | -0.48355 | -0.12469 | -0.069532 | -0.099458 | 0.38409 | 0.066804 | -0.11314 | 123.0121 | 122.9486 | 123.1778 | 66.6243 | -123.2569 | 122.9222 | 123.1137 | 122.9337 | 66.6233 | -123.5304
2726.8594 | 123.3353 | -66.7282 | 56.3141 | 0.0046549 | -0.033213 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00098273 | 0.054826 | 0.042053 | 0.055317 | -66.7335 | -0.067272 | -66.7735 | 56.3251 | 56.2662 | 56.4817 | -66.9016 | -66.7611 | -0.068322 | -66.791 | 56.2306 | 56.4312 | 56.2605 | -67.1706 | -0.17341 | 0.011006 | -0.005324 | -0.045264 | 0.12815 | -0.047903 | 0.16758 | -0.44235 | -0.083492 | -0.032911 | -0.062837 | 0.37951 | 0.11716 | -0.053626 | 123.0533 | 122.9944 | 123.2099 | 66.6609 | -123.2157 | 122.9588 | 123.1595 | 122.9887 | 66.6599 | -123.4846
2727.7969 | 123.2986 | -66.6916 | 56.3324 | -0.010607 | -0.033213 | -0.00082046 | 0.053295 | -0.0080146 | 0.062289 | 0.0077831 | -0.0034801 | -0.00076913 | 0.05504 | 0.042053 | 0.055958 | -66.729 | -0.067272 | -66.7964 | 56.3251 | 56.2799 | 56.4771 | -66.9062 | -66.7565 | -0.068322 | -66.7956 | 56.2306 | 56.4221 | 56.2559 | -67.166 | -0.21461 | -0.007304 | -0.037367 | -0.10478 | 0.10983 | -0.052476 | 0.14469 | -0.47439 | -0.1018 | -0.064953 | -0.10404 | 0.37036 | 0.089693 | -0.076514 | 123.0167 | 122.9715 | 123.1687 | 66.6243 | -123.2386 | 122.9222 | 123.1137 | 122.9475 | 66.6233 | -123.4984
2728.8594 | 123.262 | -66.7191 | 56.3324 | 0.0046549 | -0.033213 | -0.00060686 | 0.053722 | -0.0082282 | 0.062717 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055467 | 0.04248 | 0.055958 | -66.7381 | -0.062694 | -66.7781 | 56.3251 | 56.257 | 56.4862 | -66.897 | -66.7565 | -0.068322 | -66.791 | 56.2352 | 56.4221 | 56.2467 | -67.1751 | -0.17799 | -0.007304 | -0.019057 | -0.058998 | 0.11899 | -0.075371 | 0.15385 | -0.45608 | -0.097224 | -0.037487 | -0.071992 | 0.38409 | 0.089693 | -0.085672 | 123.0441 | 122.9761 | 123.2053 | 66.6564 | -123.2294 | 122.9542 | 123.1411 | 122.9658 | 66.6507 | -123.5075
2729.7969 | 123.317 | -66.7191 | 56.3232 | 0.012286 | -0.033213 | -0.0014615 | 0.053936 | -0.0082282 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.042267 | 0.055958 | -66.7335 | -0.067272 | -66.7781 | 56.3251 | 56.2616 | 56.4771 | -66.9016 | -66.7611 | -0.0729 | -66.791 | 56.2352 | 56.4312 | 56.2467 | -67.1751 | -0.18256 | 0.001851 | -0.014479 | -0.058998 | 0.12357 | -0.061637 | 0.15385 | -0.45608 | -0.088069 | -0.042066 | -0.071992 | 0.38409 | 0.108 | -0.076517 | 123.0441 | 122.9807 | 123.1961 | 66.6518 | -123.2249 | 122.9542 | 123.1503 | 122.9658 | 66.6462 | -123.4984
2730.7969 | 123.1979 | -66.7236 | 56.4239 | 0.012286 | -0.033427 | -0.0010343 | 0.052654 | -0.0080146 | 0.062503 | 0.015414 | -0.0036937 | -0.00076913 | 0.055467 | 0.042694 | 0.055531 | -66.7335 | -0.071851 | -66.7826 | 56.3251 | 56.2753 | 56.4771 | -66.897 | -66.752 | -0.068322 | -66.791 | 56.2306 | 56.4267 | 56.2421 | -67.1706 | -0.17341 | -0.098857 | -0.009901 | -0.058998 | 0.11441 | -0.14861 | 0.053141 | -0.44693 | -0.19335 | -0.02833 | -0.067414 | 0.37951 | 0.002718 | -0.1818 | 123.0487 | 122.999 | 123.2007 | 66.6518 | -123.321 | 122.9542 | 123.1503 | 122.9658 | 66.6553 | -123.5945
2731.7969 | 123.2803 | -66.7282 | 56.3324 | 0.0046549 | -0.033 | -0.0012479 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055467 | 0.041839 | 0.055744 | -66.729 | -0.058115 | -66.7826 | 56.3297 | 56.2616 | 56.4817 | -66.8925 | -66.7611 | -0.0729 | -66.7865 | 56.2352 | 56.4129 | 56.2284 | -67.1706 | -0.16425 | -0.002726 | -0.000746 | -0.054421 | 0.10983 | -0.070792 | 0.14927 | -0.44235 | -0.097224 | -0.032911 | -0.058259 | 0.38409 | 0.080535 | -0.10399 | 123.0579 | 122.9898 | 123.2099 | 66.6701 | -123.2249 | 122.9634 | 123.1411 | 122.9566 | 66.6553 | -123.503
2732.8594 | 123.262 | -66.7099 | 56.3187 | -0.010607 | -0.033213 | -0.00060686 | 0.053722 | -0.0082282 | 0.062717 | 0.00015261 | -0.0034801 | -0.00076913 | 0.055254 | 0.042053 | 0.055958 | -66.7335 | -0.062694 | -66.7781 | 56.3205 | 56.2524 | 56.4771 | -66.897 | -66.7611 | -0.063743 | -66.8002 | 56.2306 | 56.4221 | 56.2193 | -67.1797 | -0.18714 | 0.001849 | -0.023634 | -0.068153 | 0.11899 | -0.066218 | 0.15843 | -0.46982 | -0.08807 | -0.051221 | -0.090305 | 0.37951 | 0.10342 | -0.099411 | 123.0304 | 122.9623 | 123.187 | 66.6472 | -123.2157 | 122.9405 | 123.132 | 122.9292 | 66.6462 | -123.4984
2733.7969 | 123.3078 | -66.6916 | 56.3553 | -0.0029761 | -0.033 | -0.00082046 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.042053 | 0.055531 | -66.7335 | -0.067272 | -66.7918 | 56.3251 | 56.2708 | 56.4771 | -66.897 | -66.7657 | -0.063743 | -66.7865 | 56.2306 | 56.4312 | 56.2467 | -67.1751 | -0.20545 | -0.030193 | -0.041945 | -0.1002 | 0.10525 | -0.084523 | 0.12181 | -0.48355 | -0.12469 | -0.07411 | -0.09488 | 0.38867 | 0.075961 | -0.10856 | 123.0167 | 122.9624 | 123.1687 | 66.6243 | -123.2523 | 122.9222 | 123.1228 | 122.9383 | 66.6278 | -123.5304
2734.8594 | 123.3124 | -66.7328 | 56.3095 | -0.010607 | -0.033213 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | -0.0074779 | -0.0036937 | -0.00055553 | 0.05504 | 0.042267 | 0.055744 | -66.7335 | -0.067272 | -66.7826 | 56.3251 | 56.2753 | 56.4817 | -66.897 | -66.7657 | -0.068322 | -66.791 | 56.2352 | 56.4221 | 56.2467 | -67.1706 | -0.16425 | 0.015584 | -0.000746 | -0.049843 | 0.11441 | -0.034167 | 0.17216 | -0.43777 | -0.074336 | -0.032911 | -0.058259 | 0.37951 | 0.11258 | -0.062784 | 123.0579 | 123.0081 | 123.2145 | 66.6655 | -123.2065 | 122.968 | 123.1549 | 122.9795 | 66.6645 | -123.4801
2735.7969 | 123.2849 | -66.7419 | 56.369 | -0.010607 | -0.033213 | -0.00082046 | 0.053508 | -0.0086556 | 0.06293 | 0.00015261 | -0.0039075 | -0.00034193 | 0.055254 | 0.04248 | 0.055958 | -66.729 | -0.071851 | -66.7826 | 56.3342 | 56.257 | 56.4817 | -66.9016 | -66.7565 | -0.0729 | -66.791 | 56.2352 | 56.4267 | 56.233 | -67.166 | -0.15968 | -0.034769 | 0.012987 | -0.040688 | 0.11899 | -0.11199 | 0.11265 | -0.42404 | -0.13385 | -0.014599 | -0.049104 | 0.37493 | 0.057649 | -0.13603 | 123.0762 | 122.999 | 123.2236 | 66.6701 | -123.2706 | 122.9771 | 123.1686 | 122.9749 | 66.669 | -123.535
2736.8594 | 123.175 | -66.7191 | 56.3919 | -0.0029761 | -0.033213 | -0.00060686 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.055254 | 0.042053 | 0.055317 | -66.7335 | -0.071851 | -66.7872 | 56.3251 | 56.2616 | 56.4679 | -66.9016 | -66.7611 | -0.0729 | -66.791 | 56.2352 | 56.4175 | 56.2376 | -67.1843 | -0.18256 | -0.066814 | -0.014479 | -0.068154 | 0.11441 | -0.1303 | 0.076027 | -0.46524 | -0.15673 | -0.042066 | -0.071992 | 0.39325 | 0.025604 | -0.15434 | 123.0441 | 122.9807 | 123.187 | 66.6472 | -123.2935 | 122.9542 | 123.1366 | 122.9566 | 66.6462 | -123.5762
2737.7969 | 123.1659 | -66.7511 | 56.3736 | -0.0029761 | -0.033427 | -0.00082046 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00034193 | 0.055467 | 0.04248 | 0.055744 | -66.7427 | -0.071851 | -66.7872 | 56.3205 | 56.2662 | 56.4817 | -66.9108 | -66.752 | -0.077479 | -66.791 | 56.226 | 56.4175 | 56.2559 | -67.1751 | -0.15968 | -0.053082 | 0.008408 | -0.03611 | 0.12357 | -0.10741 | 0.10807 | -0.42404 | -0.14758 | -0.000864 | -0.039948 | 0.38409 | 0.043915 | -0.11771 | 123.0716 | 123.0173 | 123.2328 | 66.6792 | -123.2844 | 122.9771 | 123.1686 | 123.007 | 66.6736 | -123.5487
2738.7969 | 123.2437 | -66.7419 | 56.3736 | -0.0029761 | -0.033427 | -0.00082046 | 0.053295 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00012813 | 0.055467 | 0.04248 | 0.055744 | -66.729 | -0.067272 | -66.7918 | 56.3297 | 56.257 | 56.4771 | -66.9016 | -66.752 | -0.0729 | -66.7956 | 56.226 | 56.4221 | 56.233 | -67.166 | -0.15968 | -0.043925 | 0.012987 | -0.049845 | 0.10983 | -0.11657 | 0.1035 | -0.42404 | -0.14758 | -0.01002 | -0.053683 | 0.37036 | 0.048494 | -0.14061 | 123.0716 | 122.999 | 123.219 | 66.6747 | -123.2752 | 122.968 | 123.164 | 122.9749 | 66.669 | -123.5396
2739.8594 | 123.2895 | -66.7236 | 56.3049 | -0.0029761 | -0.033427 | -0.0012479 | 0.053295 | -0.0082282 | 0.062717 | -0.0074779 | -0.0036937 | -0.00055553 | 0.055254 | 0.04248 | 0.055531 | -66.7427 | -0.067272 | -66.7872 | 56.3205 | 56.257 | 56.4771 | -66.897 | -66.7565 | -0.0729 | -66.791 | 56.2352 | 56.4221 | 56.2376 | -67.1797 | -0.17341 | 0.015582 | -0.019058 | -0.063576 | 0.10983 | -0.047906 | 0.17216 | -0.45608 | -0.069759 | -0.032909 | -0.067414 | 0.38867 | 0.11716 | -0.067364 | 123.0441 | 122.9807 | 123.2007 | 66.6564 | -123.202 | 122.9588 | 123.1457 | 122.9612 | 66.6507 | -123.4846
2740.7969 | 123.23 | -66.7419 | 56.3599 | -0.0029761 | -0.033 | -0.0012479 | 0.052867 | -0.0082282 | 0.062289 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.04248 | 0.055958 | -66.7427 | -0.067272 | -66.7872 | 56.3297 | 56.2616 | 56.4771 | -66.9016 | -66.752 | -0.068322 | -66.7819 | 56.2352 | 56.4267 | 56.2193 | -67.1751 | -0.15968 | -0.030192 | -0.000748 | -0.045266 | 0.11441 | -0.098258 | 0.11723 | -0.43319 | -0.12469 | -0.01002 | -0.039947 | 0.39325 | 0.066805 | -0.14061 | 123.0716 | 123.0035 | 123.219 | 66.6747 | -123.2615 | 122.9771 | 123.1686 | 122.9612 | 66.6736 | -123.535
2741.8594 | 123.2254 | -66.7419 | 56.3782 | 0.0046549 | -0.033 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.015414 | -0.0036937 | -0.00055553 | 0.05504 | 0.04248 | 0.055958 | -66.729 | -0.07643 | -66.7918 | 56.3159 | 56.2616 | 56.4817 | -66.9062 | -66.7565 | -0.0729 | -66.791 | 56.226 | 56.4267 | 56.2605 | -67.1751 | -0.16425 | -0.062238 | 0.012987 | -0.049845 | 0.11441 | -0.11657 | 0.1035 | -0.43319 | -0.15216 | -0.014599 | -0.049104 | 0.38409 | 0.048494 | -0.11771 | 123.0579 | 123.0035 | 123.2236 | 66.6655 | -123.2844 | 122.968 | 123.1686 | 123.0024 | 66.669 | -123.5533
2742.7969 | 123.1979 | -66.7465 | 56.3553 | -0.0029761 | -0.033213 | -0.0014615 | 0.053081 | -0.0084418 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.042694 | 0.055531 | -66.729 | -0.071851 | -66.7781 | 56.3297 | 56.2753 | 56.4817 | -66.9062 | -66.7611 | -0.077479 | -66.7865 | 56.2352 | 56.4221 | 56.2284 | -67.1751 | -0.15968 | -0.025615 | 0.017565 | -0.031532 | 0.12815 | -0.079944 | 0.12638 | -0.42862 | -0.12011 | -0.0146 | -0.039948 | 0.38867 | 0.066804 | -0.12687 | 123.0762 | 123.0219 | 123.2282 | 66.6747 | -123.2615 | 122.9817 | 123.1686 | 122.9749 | 66.669 | -123.5304
2743.8438 | 123.2529 | -66.7557 | 56.3187 | 0.0046549 | -0.032786 | -0.0014615 | 0.053508 | -0.0082282 | 0.062289 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055254 | 0.04248 | 0.055531 | -66.7427 | -0.067272 | -66.7826 | 56.3205 | 56.2753 | 56.4817 | -66.897 | -66.7611 | -0.068322 | -66.791 | 56.2443 | 56.4221 | 56.2284 | -67.1706 | -0.14136 | 0.001849 | 0.012985 | -0.026955 | 0.11441 | -0.043323 | 0.163 | -0.41488 | -0.074335 | -0.005445 | -0.035371 | 0.37951 | 0.10342 | -0.090254 | 123.0762 | 123.031 | 123.2373 | 66.6884 | -123.2157 | 123 | 123.1778 | 122.9841 | 66.6874 | -123.4892
2744.7969 | 123.1934 | -66.7465 | 56.3507 | -0.010607 | -0.033213 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0041211 | -0.00076913 | 0.055254 | 0.042267 | 0.055744 | -66.729 | -0.067272 | -66.7781 | 56.3297 | 56.2524 | 56.4862 | -66.9108 | -66.7611 | -0.0729 | -66.7819 | 56.2306 | 56.4221 | 56.233 | -67.1706 | -0.16426 | -0.021037 | 0.017565 | -0.031532 | 0.13272 | -0.098261 | 0.13554 | -0.42404 | -0.12011 | -0.0146 | -0.035369 | 0.38867 | 0.071382 | -0.11772 | 123.0762 | 122.999 | 123.2328 | 66.6792 | -123.2615 | 122.9771 | 123.1686 | 122.9795 | 66.6736 | -123.5213
2745.7969 | 123.2437 | -66.7328 | 56.337 | -0.0029761 | -0.033427 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0032665 | -0.00055553 | 0.05504 | 0.042267 | 0.055958 | -66.729 | -0.067272 | -66.7735 | 56.3297 | 56.2753 | 56.4817 | -66.9062 | -66.7611 | -0.068322 | -66.7865 | 56.2352 | 56.4175 | 56.233 | -67.1751 | -0.17341 | -0.007304 | 0.003832 | -0.040686 | 0.13272 | -0.061633 | 0.14469 | -0.44235 | -0.1018 | -0.028333 | -0.053681 | 0.38867 | 0.080536 | -0.10399 | 123.0625 | 123.0081 | 123.2145 | 66.6655 | -123.2432 | 122.968 | 123.1503 | 122.9658 | 66.6645 | -123.5121
2746.8594 | 123.1842 | -66.7557 | 56.3736 | 0.012286 | -0.033213 | -0.00082046 | 0.053295 | -0.0080146 | 0.06293 | 0.015414 | -0.0043347 | -0.00055553 | 0.055254 | 0.042267 | 0.055958 | -66.729 | -0.067272 | -66.7781 | 56.3251 | 56.2753 | 56.4817 | -66.9016 | -66.7565 | -0.0729 | -66.791 | 56.2306 | 56.4221 | 56.2284 | -67.1751 | -0.14594 | -0.048503 | 0.02672 | -0.022377 | 0.12357 | -0.098254 | 0.10807 | -0.41946 | -0.143 | -0.000866 | -0.035371 | 0.38409 | 0.048494 | -0.14518 | 123.0808 | 123.031 | 123.2373 | 66.6884 | -123.2752 | 122.9863 | 123.1778 | 122.9841 | 66.6828 | -123.5487
2747.7969 | 123.2254 | -66.7328 | 56.3599 | 0.0046549 | -0.033213 | -0.0010343 | 0.053081 | -0.0080146 | 0.06293 | 0.0077831 | -0.0036937 | -0.00055553 | 0.05504 | 0.042694 | 0.055531 | -66.7335 | -0.07643 | -66.7918 | 56.3297 | 56.2753 | 56.4862 | -66.897 | -66.7611 | -0.068322 | -66.7865 | 56.2352 | 56.4221 | 56.2559 | -67.1797 | -0.16425 | -0.030192 | -0.000746 | -0.059 | 0.10525 | -0.084521 | 0.12639 | -0.44693 | -0.12469 | -0.028333 | -0.053681 | 0.39325 | 0.062227 | -0.10398 | 123.0625 | 123.0081 | 123.219 | 66.6564 | -123.2569 | 122.968 | 123.1549 | 122.9887 | 66.6645 | -123.5396
2748.8594 | 123.2529 | -66.7007 | 56.3461 | 0.012286 | -0.033213 | -0.00082046 | 0.053295 | -0.0082282 | 0.062503 | 0.015414 | -0.0039075 | -0.00055553 | 0.05504 | 0.04248 | 0.055744 | -66.729 | -0.071851 | -66.7781 | 56.3297 | 56.2662 | 56.4862 | -66.9016 | -66.7611 | -0.0729 | -66.8002 | 56.2352 | 56.4267 | 56.2421 | -67.1751 | -0.20087 | -0.016459 | -0.028211 | -0.077308 | 0.12357 | -0.079946 | 0.14012 | -0.47439 | -0.11096 | -0.060376 | -0.09946 | 0.37493 | 0.080538 | -0.10398 | 123.0304 | 122.9669 | 123.187 | 66.6289 | -123.2477 | 122.9359 | 123.1274 | 122.9429 | 66.6278 | -123.5213
2749.7969 | 123.2025 | -66.7236 | 56.3461 | 0.0046549 | -0.033213 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00055553 | 0.055254 | 0.042908 | 0.055744 | -66.7335 | -0.071851 | -66.7781 | 56.3297 | 56.2753 | 56.4817 | -66.9062 | -66.7657 | -0.077479 | -66.7819 | 56.2352 | 56.4175 | 56.2513 | -67.1706 | -0.18256 | -0.016459 | -0.009901 | -0.05442 | 0.12815 | -0.070788 | 0.13554 | -0.44693 | -0.11096 | -0.042066 | -0.058257 | 0.38867 | 0.071381 | -0.094826 | 123.0533 | 122.999 | 123.2053 | 66.6518 | -123.2523 | 122.9588 | 123.1411 | 122.9749 | 66.6462 | -123.5167
2750.7969 | 123.2346 | -66.7648 | 56.3278 | 0.0046549 | -0.033 | -0.0012479 | 0.053081 | -0.0084418 | 0.06293 | 0.00015261 | -0.0034801 | -0.00034193 | 0.055467 | 0.042694 | 0.055744 | -66.7381 | -0.067272 | -66.7872 | 56.3388 | 56.2662 | 56.4817 | -66.9062 | -66.7611 | -0.082058 | -66.791 | 56.2352 | 56.4267 | 56.2284 | -67.1706 | -0.14137 | 0.011008 | 0.02672 | -0.022377 | 0.11899 | -0.061636 | 0.15385 | -0.40573 | -0.092647 | 0.003711 | -0.026215 | 0.37951 | 0.098848 | -0.099409 | 123.1037 | 123.031 | 123.2465 | 66.6976 | -123.234 | 123 | 123.1915 | 122.9932 | 66.6828 | -123.4984
2751.7969 | 123.1659 | -66.7786 | 56.369 | 0.0046549 | -0.033213 | -0.0012479 | 0.052654 | -0.0082282 | 0.062717 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.042267 | 0.055317 | -66.7335 | -0.071851 | -66.7826 | 56.3342 | 56.2753 | 56.4862 | -66.9016 | -66.7703 | -0.0729 | -66.7865 | 56.2306 | 56.4267 | 56.2513 | -67.1706 | -0.12305 | -0.034769 | 0.04503 | -0.004067 | 0.11899 | -0.093677 | 0.11723 | -0.392 | -0.13842 | 0.008286 | -0.007905 | 0.38409 | 0.057649 | -0.11772 | 123.1128 | 123.0539 | 123.2648 | 66.7067 | -123.2706 | 123.0092 | 123.2052 | 123.0299 | 66.7057 | -123.5396
2752.7969 | 123.2346 | -66.7603 | 56.3416 | -0.0029761 | -0.032786 | -0.00060686 | 0.053508 | -0.0084418 | 0.06293 | 0.0077831 | -0.0032665 | -0.00055553 | 0.05504 | 0.04248 | 0.055744 | -66.7381 | -0.067272 | -66.7781 | 56.3297 | 56.2708 | 56.4771 | -66.8925 | -66.7565 | -0.0729 | -66.791 | 56.2352 | 56.4267 | 56.2376 | -67.1797 | -0.13221 | -0.011882 | 0.022142 | -0.017799 | 0.11441 | -0.07079 | 0.13554 | -0.41946 | -0.10638 | 0.003712 | -0.030793 | 0.38867 | 0.085115 | -0.10398 | 123.0899 | 123.031 | 123.2373 | 66.693 | -123.234 | 122.9954 | 123.1869 | 122.9978 | 66.6874 | -123.5213
2753.8594 | 123.175 | -66.7648 | 56.3507 | 0.012286 | -0.033641 | -0.00082046 | 0.053081 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.04248 | 0.055744 | -66.7381 | -0.07643 | -66.7781 | 56.3297 | 56.2708 | 56.4817 | -66.9062 | -66.7565 | -0.077479 | -66.7865 | 56.2352 | 56.4267 | 56.2513 | -67.1751 | -0.14137 | -0.021037 | 0.02672 | -0.013221 | 0.12815 | -0.079945 | 0.13096 | -0.41031 | -0.11553 | 0.00829 | -0.021637 | 0.38867 | 0.07596 | -0.099404 | 123.0945 | 123.0356 | 123.2465 | 66.6884 | -123.2569 | 123 | 123.1915 | 123.0161 | 66.6874 | -123.5258
2754.7969 | 123.2483 | -66.7603 | 56.3232 | -0.0029761 | -0.033213 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.055254 | 0.042053 | 0.055744 | -66.729 | -0.07643 | -66.7689 | 56.3251 | 56.2662 | 56.4817 | -66.9062 | -66.7657 | -0.068322 | -66.7956 | 56.2398 | 56.4221 | 56.2559 | -67.1751 | -0.14594 | 0.001851 | 0.031298 | -0.008642 | 0.1373 | -0.057058 | 0.15843 | -0.41488 | -0.083491 | -0.005445 | -0.035372 | 0.37951 | 0.098848 | -0.067359 | 123.0853 | 123.0264 | 123.2419 | 66.6838 | -123.2294 | 123 | 123.1823 | 123.0161 | 66.6919 | -123.4984
2755.7969 | 123.1567 | -66.7786 | 56.3324 | -0.010607 | -0.033213 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | -0.0074779 | -0.0036937 | -0.00055553 | 0.05504 | 0.04248 | 0.055958 | -66.729 | -0.07643 | -66.7781 | 56.3297 | 56.2708 | 56.4862 | -66.9108 | -66.7657 | -0.082058 | -66.791 | 56.2352 | 56.4175 | 56.2467 | -67.1751 | -0.13221 | -0.002726 | 0.049608 | 0.000511 | 0.13272 | -0.061634 | 0.15385 | -0.39657 | -0.097224 | 0.012865 | -0.012483 | 0.38409 | 0.085114 | -0.085672 | 123.1082 | 123.0493 | 123.2648 | 66.7021 | -123.2432 | 123.0137 | 123.1961 | 123.0253 | 66.6965 | -123.5075
2756.7969 | 123.2986 | -66.7648 | 56.3141 | -0.010607 | -0.033427 | -0.00082046 | 0.053295 | -0.0084418 | 0.062289 | -0.0074779 | -0.0036937 | -0.00055553 | 0.054826 | 0.042694 | 0.055531 | -66.7381 | -0.067272 | -66.7781 | 56.3251 | 56.257 | 56.4817 | -66.9016 | -66.7657 | -0.0729 | -66.7956 | 56.2306 | 56.4267 | 56.2238 | -67.1751 | -0.13679 | 0.011006 | 0.02672 | -0.013221 | 0.12357 | -0.057061 | 0.16758 | -0.41031 | -0.083492 | -0.000867 | -0.030794 | 0.37951 | 0.11258 | -0.090255 | 123.0899 | 123.0219 | 123.2465 | 66.6976 | -123.2157 | 122.9954 | 123.1915 | 122.9887 | 66.6919 | -123.4892
2757.7969 | 123.1018 | -66.7969 | 56.3004 | 0.0046549 | -0.033427 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | -0.0074779 | -0.0039075 | -0.00055553 | 0.055254 | 0.04248 | 0.055744 | -66.7381 | -0.067272 | -66.7781 | 56.3297 | 56.2708 | 56.4817 | -66.9108 | -66.7565 | -0.082058 | -66.8002 | 56.2443 | 56.4267 | 56.2513 | -67.1751 | -0.1139 | 0.029317 | 0.058763 | 0.018822 | 0.13272 | -0.029591 | 0.18132 | -0.37826 | -0.056024 | 0.040333 | -0.00333 | 0.37493 | 0.12631 | -0.04905 | 123.1265 | 123.0676 | 123.2785 | 66.7296 | -123.2111 | 123.0412 | 123.2235 | 123.0482 | 66.7148 | -123.4755
2758.8594 | 123.2162 | -66.7603 | 56.3507 | -0.0029761 | -0.033427 | -0.00082046 | 0.053081 | -0.0080146 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.05504 | 0.04248 | 0.055531 | -66.7335 | -0.071851 | -66.7735 | 56.3297 | 56.2799 | 56.4817 | -66.9062 | -66.7611 | -0.077479 | -66.791 | 56.2306 | 56.4312 | 56.233 | -67.1706 | -0.14594 | -0.021037 | 0.02672 | -0.01322 | 0.13272 | -0.070787 | 0.13096 | -0.41031 | -0.12011 | -0.000867 | -0.030793 | 0.37951 | 0.080539 | -0.11772 | 123.0899 | 123.0402 | 123.2419 | 66.6884 | -123.2569 | 122.9908 | 123.1915 | 122.9932 | 66.6828 | -123.5213
2759.7969 | 123.2117 | -66.7374 | 56.3278 | -0.0029761 | -0.033427 | -0.00060686 | 0.053295 | -0.0082282 | 0.062076 | -0.0074779 | -0.0039075 | -0.00098273 | 0.05504 | 0.042908 | 0.055744 | -66.7335 | -0.07643 | -66.7781 | 56.3251 | 56.257 | 56.4725 | -66.9016 | -66.7611 | -0.077479 | -66.7819 | 56.2352 | 56.4221 | 56.2284 | -67.166 | -0.16425 | -0.002727 | 0.003832 | -0.040687 | 0.12357 | -0.070794 | 0.14469 | -0.42862 | -0.092647 | -0.023755 | -0.044524 | 0.38409 | 0.09427 | -0.099409 | 123.0625 | 122.9944 | 123.2099 | 66.6609 | -123.2294 | 122.9725 | 123.1595 | 122.9658 | 66.6599 | -123.4938
2760.7969 | 123.2941 | -66.7191 | 56.3141 | -0.0029761 | -0.033213 | -0.00060686 | 0.053081 | -0.0084418 | 0.062503 | 0.00015261 | -0.0039075 | -0.00012813 | 0.05504 | 0.04248 | 0.055531 | -66.7335 | -0.071851 | -66.7918 | 56.3297 | 56.2753 | 56.4817 | -66.9108 | -66.7611 | -0.086637 | -66.791 | 56.2306 | 56.4221 | 56.2376 | -67.166 | -0.19172 | 0.015584 | -0.014479 | -0.072733 | 0.11899 | -0.038745 | 0.16758 | -0.44693 | -0.083492 | -0.042066 | -0.071992 | 0.37493 | 0.108 | -0.076519 | 123.0487 | 122.9944 | 123.2007 | 66.6472 | -123.2249 | 122.9496 | 123.1411 | 122.9566 | 66.6324 | -123.4801
2761.8594 | 123.175 | -66.7603 | 56.3782 | -0.010607 | -0.033427 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055254 | 0.042053 | 0.055744 | -66.729 | -0.07643 | -66.7781 | 56.3297 | 56.2753 | 56.4817 | -66.9016 | -66.7565 | -0.077479 | -66.7865 | 56.2352 | 56.4267 | 56.2421 | -67.1843 | -0.14136 | -0.048503 | 0.031298 | -0.017799 | 0.12357 | -0.10283 | 0.1035 | -0.42404 | -0.143 | 0.003712 | -0.026215 | 0.39783 | 0.048494 | -0.13603 | 123.0899 | 123.0356 | 123.2419 | 66.6838 | -123.2798 | 122.9954 | 123.1869 | 123.0024 | 66.6828 | -123.5625
2762.7969 | 123.2666 | -66.7419 | 56.3232 | -0.010607 | -0.033213 | -0.00060686 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0043347 | -0.00076913 | 0.05504 | 0.04248 | 0.055744 | -66.7335 | -0.071851 | -66.7826 | 56.3251 | 56.2662 | 56.4725 | -66.9016 | -66.7611 | -0.077479 | -66.7865 | 56.2306 | 56.4312 | 56.2559 | -67.1751 | -0.15968 | 0.001851 | 0.008409 | -0.040688 | 0.11899 | -0.057058 | 0.14927 | -0.43319 | -0.092647 | -0.019178 | -0.044526 | 0.38867 | 0.108 | -0.067359 | 123.067 | 123.0081 | 123.2145 | 66.6701 | -123.2249 | 122.9725 | 123.1732 | 122.9978 | 66.6645 | -123.4984
2763.7969 | 123.2895 | -66.7328 | 56.3232 | -0.010607 | -0.033854 | -0.0010343 | 0.053508 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055254 | 0.042694 | 0.055744 | -66.7335 | -0.07643 | -66.7872 | 56.3251 | 56.2524 | 56.4725 | -66.897 | -66.7611 | -0.0729 | -66.7956 | 56.2352 | 56.4267 | 56.2421 | -67.1751 | -0.16425 | 0.001851 | -0.000746 | -0.054421 | 0.10983 | -0.070795 | 0.14927 | -0.44235 | -0.088069 | -0.028333 | -0.062838 | 0.37951 | 0.10343 | -0.081095 | 123.0579 | 122.9852 | 123.2053 | 66.6564 | -123.2203 | 122.968 | 123.1595 | 122.9749 | 66.6599 | -123.4984
2764.8594 | 123.2025 | -66.7557 | 56.3736 | -0.0029761 | -0.033641 | -0.0010343 | 0.053081 | -0.0084418 | 0.062503 | -0.0074779 | -0.0034801 | -0.00076913 | 0.05504 | 0.042694 | 0.055744 | -66.7244 | -0.081008 | -66.7872 | 56.3297 | 56.2616 | 56.4817 | -66.9062 | -66.7565 | -0.077479 | -66.7819 | 56.2398 | 56.4267 | 56.2193 | -67.1797 | -0.15052 | -0.043925 | 0.031299 | -0.031533 | 0.11899 | -0.11199 | 0.10807 | -0.42404 | -0.13385 | -0.000866 | -0.026214 | 0.39783 | 0.053072 | -0.15434 | 123.0853 | 123.0173 | 123.2373 | 66.6747 | -123.2798 | 122.9954 | 123.1823 | 122.9749 | 66.6782 | -123.5533
2765.7969 | 123.3032 | -66.7328 | 56.3141 | -0.0029761 | -0.034068 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | -0.0074779 | -0.0041211 | -0.00034193 | 0.05504 | 0.042694 | 0.055744 | -66.7381 | -0.071851 | -66.7918 | 56.3251 | 56.2753 | 56.4817 | -66.897 | -66.7749 | -0.086637 | -66.791 | 56.2352 | 56.4267 | 56.233 | -67.1706 | -0.16425 | 0.011006 | -0.005324 | -0.059 | 0.10525 | -0.038745 | 0.16758 | -0.43777 | -0.078914 | -0.042069 | -0.058259 | 0.37951 | 0.11258 | -0.081097 | 123.0579 | 123.0081 | 123.2145 | 66.6609 | -123.2111 | 122.968 | 123.1595 | 122.9658 | 66.6462 | -123.4846
2766.8594 | 123.175 | -66.7648 | 56.282 | -0.0029761 | -0.033427 | -0.0010343 | 0.052867 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.055254 | 0.042694 | 0.055958 | -66.729 | -0.07643 | -66.8009 | 56.3297 | 56.2708 | 56.4771 | -66.9062 | -66.7657 | -0.077479 | -66.7956 | 56.2398 | 56.4312 | 56.2513 | -67.1751 | -0.14137 | 0.047628 | 0.035876 | -0.036112 | 0.10525 | -0.01128 | 0.19505 | -0.41031 | -0.042292 | -0.000867 | -0.030794 | 0.37951 | 0.1492 | -0.030739 | 123.0945 | 123.0356 | 123.2419 | 66.6884 | -123.1882 | 123.0046 | 123.1961 | 123.0161 | 66.6874 | -123.4572
2767.7969 | 123.2803 | -66.7282 | 56.3278 | 0.0046549 | -0.033641 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0041211 | -0.00076913 | 0.055467 | 0.042694 | 0.055531 | -66.7381 | -0.07643 | -66.8055 | 56.3297 | 56.2662 | 56.4817 | -66.897 | -66.7611 | -0.082058 | -66.7956 | 56.2443 | 56.4267 | 56.233 | -67.166 | -0.16883 | 0.001851 | -0.009902 | -0.077312 | 0.091518 | -0.061636 | 0.15385 | -0.43777 | -0.08349 | -0.032911 | -0.067416 | 0.37036 | 0.098848 | -0.09483 | 123.0579 | 122.9944 | 123.2099 | 66.6518 | -123.2249 | 122.9725 | 123.1549 | 122.9612 | 66.6462 | -123.4938
2768.7969 | 123.2895 | -66.7328 | 56.3324 | -0.0029761 | -0.033427 | -0.00060686 | 0.053295 | -0.0084418 | 0.062717 | 0.0077831 | -0.0036937 | -0.00034193 | 0.055254 | 0.042694 | 0.055958 | -66.7244 | -0.07643 | -66.8055 | 56.3251 | 56.2524 | 56.4862 | -66.897 | -66.7611 | -0.077479 | -66.791 | 56.2352 | 56.4312 | 56.2376 | -67.1797 | -0.16425 | -0.007304 | 0.008411 | -0.072734 | 0.091518 | -0.07995 | 0.15385 | -0.44693 | -0.097224 | -0.028333 | -0.058259 | 0.38867 | 0.09885 | -0.094829 | 123.0579 | 122.9852 | 123.219 | 66.6564 | -123.2294 | 122.968 | 123.164 | 122.9704 | 66.6553 | -123.5121
2769.7969 | 123.2529 | -66.7236 | 56.3278 | 0.012286 | -0.033427 | -0.00082046 | 0.053508 | -0.0080146 | 0.062717 | -0.0074779 | -0.0039075 | -0.00034193 | 0.055254 | 0.04248 | 0.055531 | -66.7381 | -0.07643 | -66.7918 | 56.3205 | 56.2616 | 56.4817 | -66.9062 | -66.7703 | -0.077479 | -66.7865 | 56.2352 | 56.4312 | 56.2238 | -67.1751 | -0.18256 | -0.007306 | -0.014479 | -0.068155 | 0.11441 | -0.066215 | 0.15385 | -0.4515 | -0.092647 | -0.046645 | -0.062836 | 0.38867 | 0.10343 | -0.10399 | 123.0441 | 122.9852 | 123.2053 | 66.6472 | -123.234 | 122.9588 | 123.1549 | 122.9475 | 66.6462 | -123.503
2770.7969 | 123.2574 | -66.7236 | 56.3416 | -0.010607 | -0.033641 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0041211 | -0.00055553 | 0.055467 | 0.042694 | 0.055958 | -66.7381 | -0.07643 | -66.7918 | 56.3251 | 56.2616 | 56.4817 | -66.9016 | -66.7611 | -0.082058 | -66.791 | 56.2352 | 56.4175 | 56.265 | -67.1751 | -0.17799 | -0.01646 | -0.014479 | -0.068155 | 0.10983 | -0.079948 | 0.14012 | -0.4515 | -0.10638 | -0.037488 | -0.067414 | 0.38409 | 0.075958 | -0.076513 | 123.0487 | 122.9852 | 123.2053 | 66.6472 | -123.2432 | 122.9588 | 123.1411 | 122.9887 | 66.6416 | -123.5167
2771.8594 | 123.2986 | -66.7374 | 56.3416 | 0.0046549 | -0.034068 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | -0.0074779 | -0.0036937 | -0.00076913 | 0.055254 | 0.042694 | 0.055958 | -66.729 | -0.081008 | -66.8101 | 56.3297 | 56.2662 | 56.4771 | -66.9016 | -66.7611 | -0.082058 | -66.8002 | 56.2352 | 56.4312 | 56.233 | -67.1797 | -0.16425 | -0.011882 | 0.00841 | -0.072735 | 0.091518 | -0.075369 | 0.13554 | -0.44235 | -0.10638 | -0.023755 | -0.062839 | 0.37951 | 0.089694 | -0.10856 | 123.067 | 123.0035 | 123.2145 | 66.6564 | -123.2432 | 122.9725 | 123.1686 | 122.9704 | 66.6553 | -123.5213
2772.7969 | 123.2986 | -66.7053 | 56.3278 | 0.0046549 | -0.033427 | -0.0010343 | 0.053508 | -0.0082282 | 0.062717 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055254 | 0.042694 | 0.055744 | -66.7381 | -0.07643 | -66.7872 | 56.3251 | 56.2662 | 56.4771 | -66.9016 | -66.7703 | -0.077479 | -66.791 | 56.2398 | 56.4312 | 56.2284 | -67.1706 | -0.1963 | -0.002727 | -0.03279 | -0.081887 | 0.11441 | -0.061636 | 0.14927 | -0.46524 | -0.088069 | -0.064956 | -0.085725 | 0.37951 | 0.10343 | -0.099409 | 123.0304 | 122.9715 | 123.1824 | 66.6289 | -123.2294 | 122.9451 | 123.1366 | 122.9337 | 66.6278 | -123.4984
2773.7969 | 123.2849 | -66.7328 | 56.337 | 0.0046549 | -0.033854 | -0.00082046 | 0.053722 | -0.0082282 | 0.062717 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054826 | 0.042053 | 0.055744 | -66.7427 | -0.085587 | -66.8009 | 56.3342 | 56.2524 | 56.4725 | -66.9016 | -66.7657 | -0.082058 | -66.8002 | 56.2398 | 56.4267 | 56.2238 | -67.1751 | -0.16883 | -0.002725 | -0.009903 | -0.068156 | 0.10067 | -0.084528 | 0.13554 | -0.44235 | -0.097224 | -0.032911 | -0.067417 | 0.37493 | 0.089693 | -0.11314 | 123.067 | 122.9852 | 123.2053 | 66.6472 | -123.2386 | 122.9725 | 123.1595 | 122.9566 | 66.6507 | -123.5121
2774.8594 | 123.262 | -66.7465 | 56.3507 | 0.0046549 | -0.033641 | -0.00082046 | 0.053295 | -0.0084418 | 0.062289 | -0.0074779 | -0.0039075 | -0.00055553 | 0.05504 | 0.04248 | 0.055744 | -66.7381 | -0.07643 | -66.8009 | 56.3342 | 56.2662 | 56.4862 | -66.9016 | -66.7611 | -0.082058 | -66.8002 | 56.2398 | 56.4358 | 56.233 | -67.1751 | -0.1551 | -0.016458 | 0.008409 | -0.054423 | 0.10067 | -0.084524 | 0.13554 | -0.42862 | -0.11096 | -0.0146 | -0.053684 | 0.37493 | 0.085117 | -0.11772 | 123.0808 | 123.0127 | 123.2328 | 66.6701 | -123.2523 | 122.9863 | 123.1823 | 122.9795 | 66.6645 | -123.5258
2775.7969 | 123.2666 | -66.7191 | 56.3187 | -0.010607 | -0.033427 | -0.00082046 | 0.053722 | -0.0082282 | 0.062717 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.042694 | 0.055958 | -66.7335 | -0.081008 | -66.7826 | 56.3205 | 56.257 | 56.4817 | -66.9062 | -66.7703 | -0.077479 | -66.7819 | 56.2352 | 56.4312 | 56.2101 | -67.1706 | -0.18714 | 0.001849 | -0.014479 | -0.063576 | 0.12357 | -0.061639 | 0.163 | -0.4515 | -0.083492 | -0.051223 | -0.062835 | 0.38867 | 0.11258 | -0.10857 | 123.0396 | 122.9761 | 123.2007 | 66.638 | -123.2249 | 122.9542 | 123.1503 | 122.9292 | 66.6416 | -123.4892
2776.7969 | 123.2483 | -66.7465 | 56.3553 | -0.0029761 | -0.033641 | -0.00060686 | 0.053295 | -0.0082282 | 0.062503 | -0.015108 | -0.0039075 | -0.00055553 | 0.054826 | 0.042694 | 0.055744 | -66.7335 | -0.085587 | -66.7964 | 56.3251 | 56.2708 | 56.4862 | -66.9016 | -66.7657 | -0.082058 | -66.7956 | 56.2306 | 56.4267 | 56.233 | -67.1751 | -0.1551 | -0.030193 | 0.012987 | -0.049845 | 0.10525 | -0.084523 | 0.13096 | -0.42862 | -0.12469 | -0.019178 | -0.049105 | 0.37951 | 0.071382 | -0.1223 | 123.0716 | 123.0173 | 123.2328 | 66.6609 | -123.2569 | 122.9771 | 123.1732 | 122.9795 | 66.6645 | -123.5304
2777.7969 | 123.2346 | -66.7145 | 56.3232 | -0.0029761 | -0.033641 | -0.00082046 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055467 | 0.042694 | 0.055531 | -66.7381 | -0.07643 | -66.7918 | 56.3251 | 56.2662 | 56.4817 | -66.9062 | -66.7611 | -0.082058 | -66.7956 | 56.2306 | 56.4267 | 56.2513 | -67.166 | -0.19172 | 0.001851 | -0.023634 | -0.07731 | 0.11441 | -0.057058 | 0.15843 | -0.4515 | -0.092647 | -0.046643 | -0.081148 | 0.37036 | 0.10343 | -0.071938 | 123.0396 | 122.9807 | 123.1961 | 66.638 | -123.2294 | 122.9451 | 123.1411 | 122.9658 | 66.6324 | -123.4892
2778.7969 | 123.3032 | -66.7053 | 56.3644 | -0.0029761 | -0.034068 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0034801 | -0.00076913 | 0.055254 | 0.042694 | 0.055744 | -66.7335 | -0.07643 | -66.7872 | 56.3342 | 56.2799 | 56.4817 | -66.9016 | -66.7565 | -0.086637 | -66.7865 | 56.2398 | 56.4175 | 56.2376 | -67.1751 | -0.1963 | -0.030191 | -0.028212 | -0.081887 | 0.11441 | -0.08452 | 0.11723 | -0.46982 | -0.12469 | -0.05122 | -0.081147 | 0.38867 | 0.05307 | -0.12687 | 123.0396 | 122.9852 | 123.187 | 66.6289 | -123.2661 | 122.9451 | 123.1228 | 122.9429 | 66.6187 | -123.5396
2779.7969 | 123.2941 | -66.7191 | 56.3553 | 0.0046549 | -0.033854 | -0.0010343 | 0.053508 | -0.0080146 | 0.062503 | 0.0077831 | -0.0041211 | -0.00034193 | 0.05504 | 0.042267 | 0.055744 | -66.7381 | -0.07643 | -66.7735 | 56.3297 | 56.2708 | 56.4862 | -66.9062 | -66.7657 | -0.077479 | -66.791 | 56.2398 | 56.4221 | 56.2467 | -67.1797 | -0.18714 | -0.025615 | -0.019057 | -0.054419 | 0.13272 | -0.084523 | 0.13096 | -0.46066 | -0.11554 | -0.046644 | -0.071992 | 0.38867 | 0.066804 | -0.10856 | 123.0487 | 122.9898 | 123.2053 | 66.6426 | -123.2615 | 122.9588 | 123.1411 | 122.9658 | 66.6416 | -123.535
2780.7969 | 123.2712 | -66.7191 | 56.3507 | -0.010607 | -0.033427 | -0.00082046 | 0.053295 | -0.0082282 | 0.062289 | 0.015414 | -0.0039075 | -0.00076913 | 0.054826 | 0.04248 | 0.055744 | -66.7381 | -0.071851 | -66.7964 | 56.3205 | 56.2616 | 56.4862 | -66.9108 | -66.7611 | -0.086637 | -66.791 | 56.2306 | 56.4312 | 56.2605 | -67.1706 | -0.19172 | -0.030194 | -0.019057 | -0.077311 | 0.11441 | -0.089103 | 0.13554 | -0.4515 | -0.12011 | -0.042066 | -0.071992 | 0.37951 | 0.080539 | -0.090247 | 123.0396 | 122.9807 | 123.2053 | 66.6472 | -123.2615 | 122.9496 | 123.1503 | 122.9795 | 66.6324 | -123.5213
2781.8594 | 123.1888 | -66.7282 | 56.3553 | 0.0046549 | -0.034068 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0039075 | -0.00076913 | 0.05504 | 0.042694 | 0.055531 | -66.7335 | -0.081008 | -66.7781 | 56.3297 | 56.2662 | 56.4862 | -66.9016 | -66.7657 | -0.082058 | -66.7865 | 56.2352 | 56.4267 | 56.2513 | -67.1797 | -0.17341 | -0.025615 | -0.005324 | -0.049843 | 0.12357 | -0.089102 | 0.13096 | -0.45151 | -0.12011 | -0.037489 | -0.058259 | 0.39325 | 0.071382 | -0.10398 | 123.0579 | 122.9944 | 123.2145 | 66.6472 | -123.2569 | 122.9634 | 123.1549 | 122.9795 | 66.6462 | -123.535
2782.7969 | 123.2483 | -66.7236 | 56.3553 | -0.0029761 | -0.033641 | -0.00082046 | 0.053295 | -0.0084418 | 0.062289 | 0.0077831 | -0.0036937 | -0.00076913 | 0.055254 | 0.042908 | 0.055744 | -66.7381 | -0.07643 | -66.7781 | 56.3342 | 56.2753 | 56.4817 | -66.9016 | -66.7611 | -0.082058 | -66.8002 | 56.226 | 56.4267 | 56.2559 | -67.1706 | -0.17799 | -0.021036 | -0.014479 | -0.05442 | 0.12357 | -0.079944 | 0.12638 | -0.44693 | -0.12927 | -0.037488 | -0.076572 | 0.37035 | 0.071382 | -0.099403 | 123.0579 | 122.999 | 123.2053 | 66.6472 | -123.2569 | 122.9496 | 123.1503 | 122.9795 | 66.6416 | -123.5258
2783.7969 | 123.3078 | -66.7145 | 56.3461 | 0.012286 | -0.033641 | -0.00082046 | 0.053295 | -0.0080146 | 0.062289 | 0.00015261 | -0.0036937 | 8.5466e-05 | 0.055467 | 0.042694 | 0.055744 | -66.7335 | -0.085587 | -66.7826 | 56.3297 | 56.2799 | 56.4908 | -66.9108 | -66.7703 | -0.082058 | -66.791 | 56.2352 | 56.4175 | 56.2696 | -67.1843 | -0.1963 | -0.016459 | -0.019056 | -0.068153 | 0.12815 | -0.066209 | 0.1447 | -0.46982 | -0.11096 | -0.0558 | -0.076569 | 0.39325 | 0.071381 | -0.076512 | 123.0441 | 122.9944 | 123.2053 | 66.6289 | -123.2569 | 122.9497 | 123.132 | 122.9841 | 66.6324 | -123.5304
2784.8594 | 123.2574 | -66.7236 | 56.3278 | 0.0046549 | -0.033641 | -0.00082046 | 0.053508 | -0.0080146 | 0.062503 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.042694 | 0.055531 | -66.7335 | -0.081008 | -66.7781 | 56.3251 | 56.2845 | 56.4817 | -66.9062 | -66.7657 | -0.086637 | -66.7865 | 56.226 | 56.4267 | 56.265 | -67.1797 | -0.18256 | -0.002727 | -0.009901 | -0.05442 | 0.12815 | -0.043321 | 0.15385 | -0.45608 | -0.1018 | -0.042066 | -0.062836 | 0.39325 | 0.098848 | -0.06278 | 123.0487 | 123.0081 | 123.2053 | 66.6426 | -123.234 | 122.9496 | 123.1503 | 122.9887 | 66.637 | -123.5075
2785.7969 | 123.23 | -66.7191 | 56.3782 | -0.010607 | -0.033641 | -0.0010343 | 0.053081 | -0.0082282 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.054826 | 0.042908 | 0.055531 | -66.7335 | -0.07643 | -66.7872 | 56.3205 | 56.2708 | 56.4862 | -66.9016 | -66.7611 | -0.0729 | -66.7956 | 56.2352 | 56.4221 | 56.2696 | -67.1751 | -0.18256 | -0.05766 | -0.014479 | -0.068154 | 0.11441 | -0.10741 | 0.10807 | -0.45608 | -0.143 | -0.042066 | -0.076571 | 0.37951 | 0.043916 | -0.10856 | 123.0396 | 122.9898 | 123.2053 | 66.6426 | -123.2798 | 122.9542 | 123.1411 | 122.9887 | 66.6462 | -123.5533
2786.7969 | 123.2071 | -66.7603 | 56.3507 | -0.010607 | -0.033854 | -0.00082046 | 0.053295 | -0.0082282 | 0.062289 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.042694 | 0.055531 | -66.729 | -0.081008 | -66.7735 | 56.3251 | 56.2662 | 56.4817 | -66.9016 | -66.7565 | -0.082058 | -66.7865 | 56.2306 | 56.4267 | 56.2559 | -67.1797 | -0.14136 | -0.025615 | 0.031298 | -0.01322 | 0.12815 | -0.084524 | 0.13096 | -0.41946 | -0.12011 | 0.003712 | -0.026215 | 0.39325 | 0.07596 | -0.094825 | 123.0853 | 123.0264 | 123.2419 | 66.6792 | -123.2523 | 122.9908 | 123.1869 | 123.0161 | 66.6782 | -123.5304
2787.8594 | 123.2529 | -66.7603 | 56.3187 | -0.018238 | -0.033641 | -0.00082046 | 0.053722 | -0.0084418 | 0.062289 | -0.0074779 | -0.0036937 | -0.00034193 | 0.055254 | 0.042908 | 0.055744 | -66.7335 | -0.07643 | -66.7781 | 56.3251 | 56.2845 | 56.4954 | -66.897 | -66.7611 | -0.082058 | -66.8002 | 56.2306 | 56.4221 | 56.2376 | -67.1751 | -0.13679 | 0.006428 | 0.02672 | -0.017799 | 0.11899 | -0.034166 | 0.17674 | -0.41488 | -0.08807 | -0.000867 | -0.039951 | 0.37493 | 0.10342 | -0.081097 | 123.0853 | 123.0448 | 123.2557 | 66.6838 | -123.2157 | 122.9908 | 123.1823 | 122.9978 | 66.6782 | -123.4938
2788.7969 | 123.23 | -66.7236 | 56.3782 | -0.010607 | -0.033427 | -0.0010343 | 0.053081 | -0.0082282 | 0.062289 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.042908 | 0.055531 | -66.7335 | -0.081008 | -66.7735 | 56.3297 | 56.2753 | 56.4908 | -66.9108 | -66.7565 | -0.086637 | -66.7956 | 56.2398 | 56.4267 | 56.2421 | -67.1751 | -0.18714 | -0.048503 | -0.009901 | -0.049841 | 0.1373 | -0.10283 | 0.11265 | -0.4515 | -0.13842 | -0.032909 | -0.071993 | 0.37951 | 0.048494 | -0.13603 | 123.0533 | 122.999 | 123.2145 | 66.6426 | -123.289 | 122.9634 | 123.1503 | 122.9658 | 66.637 | -123.5533
2789.7969 | 123.1934 | -66.7511 | 56.3461 | -0.0029761 | -0.033427 | -0.0010343 | 0.053508 | -0.0082282 | 0.062289 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.042694 | 0.055744 | -66.7335 | -0.085587 | -66.7735 | 56.3342 | 56.2845 | 56.4908 | -66.9016 | -66.7565 | -0.082058 | -66.791 | 56.2398 | 56.4358 | 56.2513 | -67.1706 | -0.15052 | -0.01188 | 0.017565 | -0.022375 | 0.12815 | -0.061631 | 0.1447 | -0.41946 | -0.10638 | -0.005443 | -0.039948 | 0.37951 | 0.089695 | -0.094826 | 123.0853 | 123.0356 | 123.2419 | 66.6655 | -123.2477 | 122.9908 | 123.1869 | 123.0024 | 66.669 | -123.5167
2790.7969 | 123.1979 | -66.7282 | 56.3599 | 0.019917 | -0.033641 | -0.00082046 | 0.053295 | -0.0084418 | 0.062717 | -0.0074779 | -0.0039075 | -0.00034193 | 0.055467 | 0.042694 | 0.055744 | -66.7381 | -0.07643 | -66.7872 | 56.3297 | 56.2799 | 56.4817 | -66.9108 | -66.7474 | -0.082058 | -66.791 | 56.2398 | 56.4267 | 56.265 | -67.1797 | -0.18257 | -0.030192 | -0.009902 | -0.058999 | 0.12357 | -0.079942 | 0.12181 | -0.45151 | -0.12011 | -0.019175 | -0.062837 | 0.38867 | 0.066805 | -0.094823 | 123.0579 | 123.0081 | 123.2099 | 66.6518 | -123.2706 | 122.968 | 123.1549 | 122.9933 | 66.6462 | -123.5396
2791.7969 | 123.2025 | -66.7923 | 56.3278 | -0.0029761 | -0.033854 | -0.0010343 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.042908 | 0.055958 | -66.7381 | -0.081008 | -66.7735 | 56.3297 | 56.2616 | 56.4817 | -66.9062 | -66.7611 | -0.077479 | -66.7956 | 56.2398 | 56.4267 | 56.2376 | -67.1706 | -0.1139 | 0.001851 | 0.054185 | 0.018823 | 0.13272 | -0.066215 | 0.15385 | -0.37826 | -0.088069 | 0.031176 | -0.003329 | 0.37493 | 0.098848 | -0.090252 | 123.122 | 123.0539 | 123.274 | 66.7113 | -123.234 | 123.032 | 123.219 | 123.0299 | 66.7148 | -123.4984
2792.8594 | 123.3215 | -66.6962 | 56.337 | 0.0046549 | -0.033854 | -0.0012479 | 0.053295 | -0.0082282 | 0.062717 | 0.015414 | -0.0039075 | -0.00055553 | 0.05504 | 0.04248 | 0.055958 | -66.7381 | -0.090166 | -66.7872 | 56.3205 | 56.2708 | 56.4771 | -66.9062 | -66.7657 | -0.082058 | -66.791 | 56.2398 | 56.4267 | 56.2559 | -67.1751 | -0.21003 | -0.016461 | -0.041945 | -0.091042 | 0.11899 | -0.066212 | 0.14012 | -0.47897 | -0.097224 | -0.069532 | -0.09488 | 0.38409 | 0.089693 | -0.081092 | 123.0167 | 122.9669 | 123.1733 | 66.606 | -123.2432 | 122.9359 | 123.1228 | 122.952 | 66.6141 | -123.5121
2793.7969 | 123.2117 | -66.7328 | 56.3828 | 0.0046549 | -0.033854 | -0.0012479 | 0.053295 | -0.0080146 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.05504 | 0.042908 | 0.055744 | -66.7335 | -0.081008 | -66.7872 | 56.3251 | 56.2799 | 56.4771 | -66.9108 | -66.7657 | -0.082058 | -66.791 | 56.2352 | 56.4312 | 56.2513 | -67.1751 | -0.17799 | -0.057658 | -0.000746 | -0.054421 | 0.12357 | -0.10283 | 0.09434 | -0.44235 | -0.14758 | -0.032911 | -0.058259 | 0.38409 | 0.048496 | -0.13145 | 123.0579 | 123.0127 | 123.2099 | 66.6518 | -123.2935 | 122.968 | 123.164 | 122.9841 | 66.6507 | -123.5579
2794.8594 | 123.2574 | -66.7191 | 56.3278 | -0.0029761 | -0.034068 | -0.0010343 | 0.053508 | -0.0086556 | 0.062717 | 0.015414 | -0.0039075 | -0.00034193 | 0.055254 | 0.042908 | 0.055744 | -66.7381 | -0.085587 | -66.7918 | 56.3205 | 56.2662 | 56.4771 | -66.897 | -66.7565 | -0.086637 | -66.7865 | 56.2306 | 56.4175 | 56.2467 | -67.1751 | -0.17799 | -0.007306 | -0.019057 | -0.072733 | 0.10525 | -0.061636 | 0.14927 | -0.45608 | -0.097225 | -0.037487 | -0.067414 | 0.38867 | 0.089691 | -0.081095 | 123.0396 | 122.9852 | 123.1961 | 66.6335 | -123.2249 | 122.9496 | 123.1366 | 122.9658 | 66.6324 | -123.503
2795.7969 | 123.2071 | -66.7419 | 56.369 | -0.0029761 | -0.033854 | -0.00082046 | 0.053295 | -0.0084418 | 0.062717 | 0.0077831 | -0.0041211 | -0.00098273 | 0.05504 | 0.042908 | 0.055744 | -66.7427 | -0.081008 | -66.7918 | 56.3251 | 56.257 | 56.4725 | -66.897 | -66.7611 | -0.077479 | -66.7865 | 56.2398 | 56.4312 | 56.2513 | -67.166 | -0.1551 | -0.043926 | -0.000748 | -0.049845 | 0.10525 | -0.11199 | 0.10349 | -0.42404 | -0.12927 | -0.019178 | -0.044526 | 0.37951 | 0.062228 | -0.11772 | 123.067 | 122.999 | 123.2145 | 66.6609 | -123.2661 | 122.9817 | 123.1732 | 122.9932 | 66.6645 | -123.535
2796.7969 | 123.2483 | -66.7328 | 56.3873 | 0.0046549 | -0.034068 | -0.0012479 | 0.052867 | -0.0084418 | 0.062503 | 0.015414 | -0.0039075 | -0.00055553 | 0.055254 | 0.043121 | 0.055958 | -66.7335 | -0.081008 | -66.8055 | 56.3251 | 56.2524 | 56.4862 | -66.897 | -66.7611 | -0.086637 | -66.7819 | 56.2352 | 56.4312 | 56.2101 | -67.1751 | -0.16425 | -0.062236 | -0.000746 | -0.072734 | 0.091518 | -0.13488 | 0.09892 | -0.44235 | -0.15216 | -0.028333 | -0.049102 | 0.39325 | 0.043918 | -0.17723 | 123.0579 | 122.9852 | 123.219 | 66.6518 | -123.2844 | 122.968 | 123.164 | 122.9429 | 66.6462 | -123.5625
2797.8594 | 123.3215 | -66.7557 | 56.337 | 0.0046549 | -0.033854 | -0.0010343 | 0.053295 | -0.0078008 | 0.062289 | 0.015414 | -0.0039075 | -0.00034193 | 0.055467 | 0.043121 | 0.055531 | -66.7335 | -0.07643 | -66.7964 | 56.3297 | 56.2479 | 56.4771 | -66.897 | -66.7611 | -0.086637 | -66.791 | 56.2443 | 56.4221 | 56.2055 | -67.1797 | -0.14136 | -0.007304 | 0.022142 | -0.04069 | 0.10067 | -0.089107 | 0.14012 | -0.42404 | -0.092645 | -0.005445 | -0.035371 | 0.38867 | 0.085115 | -0.13146 | 123.0853 | 123.0035 | 123.2328 | 66.6792 | -123.234 | 123 | 123.1778 | 122.9612 | 66.669 | -123.5167
2798.7969 | 123.2071 | -66.7603 | 56.3553 | 0.0046549 | -0.033854 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055467 | 0.042908 | 0.055531 | -66.7381 | -0.085587 | -66.7872 | 56.3251 | 56.2708 | 56.4908 | -66.9062 | -66.7565 | -0.086637 | -66.791 | 56.2398 | 56.4312 | 56.2284 | -67.1797 | -0.14594 | -0.030193 | 0.022142 | -0.026955 | 0.11899 | -0.084523 | 0.13554 | -0.41946 | -0.11554 | 0.003712 | -0.030793 | 0.38867 | 0.075961 | -0.12687 | 123.0853 | 123.031 | 123.2511 | 66.6747 | -123.2615 | 123 | 123.1915 | 122.9887 | 66.6736 | -123.535
2799.8594 | 123.3353 | -66.7099 | 56.3324 | 0.0046549 | -0.033854 | -0.00060686 | 0.053081 | -0.0078008 | 0.06293 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.04248 | 0.055744 | -66.7381 | -0.085587 | -66.7918 | 56.3297 | 56.2616 | 56.4771 | -66.9062 | -66.7657 | -0.086637 | -66.7865 | 56.2398 | 56.4267 | 56.2193 | -67.1797 | -0.1963 | -0.002726 | -0.028212 | -0.081888 | 0.11441 | -0.070792 | 0.14469 | -0.46982 | -0.092646 | -0.055799 | -0.076569 | 0.39325 | 0.094271 | -0.11314 | 123.0396 | 122.9715 | 123.187 | 66.6243 | -123.2386 | 122.9497 | 123.1366 | 122.9292 | 66.6233 | -123.5121
2800.7969 | 123.175 | -66.7557 | 56.3553 | -0.0029761 | -0.034068 | -0.0010343 | 0.052867 | -0.0084418 | 0.062503 | -0.0074779 | -0.0039075 | -0.00098273 | 0.055254 | 0.042908 | 0.055744 | -66.729 | -0.081008 | -66.7964 | 56.3297 | 56.2799 | 56.4862 | -66.9154 | -66.7611 | -0.086637 | -66.791 | 56.2352 | 56.4312 | 56.265 | -67.1751 | -0.15968 | -0.025615 | 0.02672 | -0.04069 | 0.11899 | -0.075365 | 0.13096 | -0.41946 | -0.12011 | -0.005445 | -0.035371 | 0.38409 | 0.075961 | -0.090246 | 123.0853 | 123.0356 | 123.2419 | 66.6747 | -123.2706 | 122.9908 | 123.1869 | 123.0207 | 66.669 | -123.5304
2801.8594 | 123.3078 | -66.7236 | 56.2775 | -0.0029761 | -0.033854 | -0.00082046 | 0.053295 | -0.0086556 | 0.062503 | 0.00015261 | -0.0036937 | -0.00034193 | 0.055254 | 0.043121 | 0.055958 | -66.7335 | -0.07643 | -66.8055 | 56.3251 | 56.2662 | 56.4771 | -66.9062 | -66.7611 | -0.086637 | -66.7956 | 56.2398 | 56.4267 | 56.2284 | -67.1751 | -0.18256 | 0.047627 | -0.009901 | -0.081889 | 0.10068 | -0.011282 | 0.19963 | -0.4515 | -0.037715 | -0.037488 | -0.071993 | 0.37951 | 0.1492 | -0.049055 | 123.0487 | 122.9898 | 123.2007 | 66.6472 | -123.1837 | 122.9634 | 123.1503 | 122.952 | 66.637 | -123.4526
2802.7969 | 123.1659 | -66.7877 | 56.3553 | -0.0029761 | -0.034282 | -0.0012479 | 0.053081 | -0.0086556 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.042908 | 0.055958 | -66.7335 | -0.07643 | -66.8009 | 56.3297 | 56.2616 | 56.4954 | -66.9062 | -66.7565 | -0.086637 | -66.791 | 56.2398 | 56.4267 | 56.2467 | -67.1706 | -0.11848 | -0.025615 | 0.054186 | -0.013224 | 0.10525 | -0.093681 | 0.14012 | -0.38284 | -0.11554 | 0.031178 | -0.003327 | 0.37951 | 0.071382 | -0.10856 | 123.1174 | 123.0493 | 123.2831 | 66.7113 | -123.2615 | 123.0275 | 123.2144 | 123.0344 | 66.7011 | -123.5258
2803.7969 | 123.2025 | -66.774 | 56.3461 | -0.0029761 | -0.033854 | -0.00060686 | 0.053508 | -0.0084418 | 0.062717 | -0.0074779 | -0.0039075 | -0.00076913 | 0.055254 | 0.042694 | 0.055958 | -66.7335 | -0.090166 | -66.7964 | 56.3342 | 56.2616 | 56.4862 | -66.9062 | -66.7611 | -0.086637 | -66.7819 | 56.2398 | 56.4221 | 56.2513 | -67.1797 | -0.13221 | -0.01188 | 0.040453 | -0.022379 | 0.10983 | -0.084525 | 0.14012 | -0.40573 | -0.10638 | 0.012866 | -0.007903 | 0.39783 | 0.07596 | -0.094826 | 123.1082 | 123.0356 | 123.2602 | 66.6838 | -123.2523 | 123.0137 | 123.1961 | 123.0253 | 66.6874 | -123.5258
2804.7969 | 123.1659 | -66.774 | 56.3461 | 0.0046549 | -0.034282 | -0.0010343 | 0.052867 | -0.0084418 | 0.062503 | -0.0074779 | -0.0039075 | -0.00034193 | 0.055254 | 0.04248 | 0.055531 | -66.7335 | -0.090166 | -66.7964 | 56.3297 | 56.2753 | 56.4817 | -66.8833 | -66.7611 | -0.082058 | -66.8048 | 56.2352 | 56.4312 | 56.2467 | -67.1843 | -0.10932 | -0.016459 | 0.040453 | -0.022379 | 0.086937 | -0.070788 | 0.13554 | -0.41031 | -0.11096 | 0.012866 | -0.030796 | 0.37951 | 0.085117 | -0.099405 | 123.1037 | 123.0493 | 123.2557 | 66.6838 | -123.2294 | 123.0092 | 123.2052 | 123.0207 | 66.6919 | -123.5304
2805.7969 | 123.2208 | -66.7511 | 56.337 | 0.0046549 | -0.034068 | -0.0010343 | 0.053081 | -0.0086556 | 0.062503 | -0.0074779 | -0.0036937 | -0.00055553 | 0.05504 | 0.043121 | 0.055744 | -66.7427 | -0.085587 | -66.7918 | 56.3297 | 56.2616 | 56.4908 | -66.9062 | -66.7611 | -0.082058 | -66.7956 | 56.2352 | 56.4221 | 56.2513 | -67.1797 | -0.1551 | -0.007304 | 0.008408 | -0.040689 | 0.11441 | -0.07537 | 0.15385 | -0.42862 | -0.1018 | -0.010022 | -0.044527 | 0.38409 | 0.085115 | -0.085671 | 123.0808 | 123.0127 | 123.2419 | 66.6655 | -123.2432 | 122.9863 | 123.1732 | 123.0024 | 66.669 | -123.5167
2806.8594 | 123.2346 | -66.774 | 56.3049 | -0.0029761 | -0.034068 | -0.0012479 | 0.052867 | -0.0080146 | 0.062503 | -0.0074779 | -0.0039075 | -0.00076913 | 0.054826 | 0.043121 | 0.055317 | -66.7335 | -0.085587 | -66.8009 | 56.3251 | 56.2662 | 56.4725 | -66.9016 | -66.7657 | -0.091215 | -66.7956 | 56.2352 | 56.4221 | 56.2284 | -67.1797 | -0.12763 | 0.020161 | 0.040453 | -0.026957 | 0.10067 | -0.038748 | 0.16758 | -0.40573 | -0.069759 | 0.008288 | -0.021639 | 0.38409 | 0.11716 | -0.076521 | 123.0991 | 123.0402 | 123.2465 | 66.6884 | -123.2066 | 123.0092 | 123.1961 | 123.0024 | 66.6828 | -123.4846
2807.7969 | 123.1705 | -66.7603 | 56.337 | -0.010607 | -0.033641 | -0.0012479 | 0.052867 | -0.0082282 | 0.062503 | -0.0074779 | -0.0034801 | -0.00055553 | 0.055254 | 0.042694 | 0.055744 | -66.7335 | -0.085587 | -66.8009 | 56.3342 | 56.2616 | 56.4908 | -66.897 | -66.7657 | -0.086637 | -66.791 | 56.2306 | 56.4312 | 56.233 | -67.1751 | -0.13679 | -0.002725 | 0.02672 | -0.04069 | 0.096096 | -0.07537 | 0.15385 | -0.41488 | -0.10638 | -0.005445 | -0.030793 | 0.38409 | 0.094272 | -0.10399 | 123.0945 | 123.0219 | 123.2511 | 66.6747 | -123.234 | 122.9908 | 123.1915 | 122.9932 | 66.6736 | -123.5121
2808.7969 | 123.2666 | -66.7648 | 56.3187 | 0.0046549 | -0.034068 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0036937 | -0.00076913 | 0.05504 | 0.043335 | 0.055744 | -66.7335 | -0.085587 | -66.7964 | 56.3297 | 56.2616 | 56.4862 | -66.9062 | -66.7657 | -0.082058 | -66.7956 | 56.2352 | 56.4221 | 56.2238 | -67.1751 | -0.14137 | 0.011006 | 0.031298 | -0.031534 | 0.10983 | -0.05706 | 0.16758 | -0.41031 | -0.083492 | -0.000867 | -0.030794 | 0.37951 | 0.10342 | -0.094833 | 123.0945 | 123.0264 | 123.2511 | 66.6792 | -123.2249 | 123 | 123.1869 | 122.9887 | 66.6828 | -123.4938
2809.7969 | 123.1476 | -66.7831 | 56.3644 | -0.0029761 | -0.034068 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.055254 | 0.042908 | 0.055744 | -66.7335 | -0.081008 | -66.7918 | 56.3251 | 56.2799 | 56.4862 | -66.9062 | -66.7657 | -0.082058 | -66.791 | 56.2352 | 56.4267 | 56.2559 | -67.166 | -0.12306 | -0.039348 | 0.049608 | -0.008646 | 0.11441 | -0.08452 | 0.12181 | -0.38284 | -0.12927 | 0.017443 | -0.007905 | 0.37493 | 0.062227 | -0.10856 | 123.1082 | 123.0631 | 123.2694 | 66.7021 | -123.2706 | 123.0183 | 123.2098 | 123.039 | 66.7011 | -123.5304
2810.7969 | 123.2849 | -66.7557 | 56.3095 | -0.0029761 | -0.034282 | -0.0010343 | 0.053295 | -0.0082282 | 0.062289 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054826 | 0.042694 | 0.055531 | -66.729 | -0.085587 | -66.7964 | 56.3342 | 56.2662 | 56.4725 | -66.9062 | -66.7611 | -0.091215 | -66.791 | 56.2398 | 56.4267 | 56.2193 | -67.1751 | -0.15052 | 0.024741 | 0.02672 | -0.04069 | 0.10983 | -0.043325 | 0.163 | -0.41946 | -0.069758 | -0.005445 | -0.035371 | 0.38409 | 0.11716 | -0.090255 | 123.0899 | 123.0219 | 123.2282 | 66.6701 | -123.2157 | 122.9954 | 123.1823 | 122.9749 | 66.6645 | -123.4846
2811.8594 | 123.2117 | -66.7511 | 56.3736 | 0.0046549 | -0.033854 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.043335 | 0.055744 | -66.7381 | -0.085587 | -66.7964 | 56.3297 | 56.2753 | 56.4862 | -66.9016 | -66.7611 | -0.091215 | -66.791 | 56.2398 | 56.4267 | 56.2513 | -67.1797 | -0.15052 | -0.043925 | 0.012987 | -0.045267 | 0.10525 | -0.098254 | 0.11265 | -0.42862 | -0.13385 | -0.010022 | -0.039948 | 0.38867 | 0.053072 | -0.12229 | 123.0808 | 123.0264 | 123.2373 | 66.6655 | -123.2752 | 122.9908 | 123.1778 | 123.0024 | 66.6599 | -123.5533
2812.7969 | 123.3124 | -66.7374 | 56.3187 | -0.010607 | -0.034068 | -0.0010343 | 0.053081 | -0.0086556 | 0.062503 | 0.00015261 | -0.0041211 | -0.00034193 | 0.05504 | 0.042908 | 0.055744 | -66.7381 | -0.085587 | -66.7872 | 56.3251 | 56.2616 | 56.4771 | -66.9016 | -66.7611 | -0.077479 | -66.791 | 56.2352 | 56.4267 | 56.2467 | -67.1751 | -0.16425 | 0.006428 | -0.000746 | -0.049843 | 0.11441 | -0.05706 | 0.15843 | -0.43777 | -0.083492 | -0.023755 | -0.053681 | 0.38409 | 0.108 | -0.07194 | 123.0625 | 122.999 | 123.2145 | 66.6518 | -123.2203 | 122.9725 | 123.164 | 122.9841 | 66.6599 | -123.4938
2813.7969 | 123.2803 | -66.7648 | 56.3232 | -0.010607 | -0.034495 | -0.00060686 | 0.052867 | -0.0082282 | 0.062503 | -0.015108 | -0.0039075 | -0.00076913 | 0.05504 | 0.042908 | 0.055531 | -66.7335 | -0.081008 | -66.7826 | 56.3297 | 56.2708 | 56.4817 | -66.9062 | -66.7611 | -0.091215 | -66.8002 | 56.2352 | 56.4267 | 56.2193 | -67.1706 | -0.14137 | 0.006429 | 0.031298 | -0.017799 | 0.12357 | -0.052479 | 0.15843 | -0.40573 | -0.088069 | 0.003711 | -0.035373 | 0.37035 | 0.10343 | -0.10399 | 123.0945 | 123.0356 | 123.2465 | 66.6838 | -123.2294 | 123 | 123.1915 | 122.9841 | 66.6736 | -123.4938
2814.8594 | 123.2574 | -66.7328 | 56.337 | -0.0029761 | -0.034068 | -0.0010343 | 0.053295 | -0.0080146 | 0.062717 | 0.0077831 | -0.0039075 | -0.00034193 | 0.054826 | 0.043121 | 0.055744 | -66.7335 | -0.085587 | -66.7826 | 56.3251 | 56.2753 | 56.4771 | -66.9062 | -66.7749 | -0.082058 | -66.7956 | 56.2398 | 56.4267 | 56.2284 | -67.1751 | -0.17341 | -0.011882 | -0.000746 | -0.049843 | 0.12357 | -0.061633 | 0.14012 | -0.44235 | -0.097224 | -0.042069 | -0.062838 | 0.37951 | 0.089693 | -0.10856 | 123.0579 | 123.0081 | 123.2099 | 66.6472 | -123.2432 | 122.9725 | 123.1595 | 122.9612 | 66.6507 | -123.5121
2815.7969 | 123.3032 | -66.7282 | 56.3141 | -0.010607 | -0.033854 | -0.00082046 | 0.053081 | -0.0086556 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.055254 | 0.042908 | 0.055958 | -66.729 | -0.081008 | -66.7872 | 56.3297 | 56.2616 | 56.4908 | -66.9062 | -66.7565 | -0.086637 | -66.7865 | 56.2352 | 56.4267 | 56.2284 | -67.1751 | -0.17799 | 0.015584 | -0.000746 | -0.058999 | 0.11899 | -0.052482 | 0.17674 | -0.44693 | -0.078914 | -0.028332 | -0.058259 | 0.38867 | 0.11258 | -0.085676 | 123.0579 | 122.9898 | 123.219 | 66.6472 | -123.2203 | 122.9634 | 123.1549 | 122.9566 | 66.6416 | -123.4892
2816.7969 | 123.2529 | -66.7465 | 56.3416 | -0.0029761 | -0.034068 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00012813 | 0.054826 | 0.043121 | 0.055744 | -66.7335 | -0.085587 | -66.7918 | 56.3342 | 56.2662 | 56.4817 | -66.9016 | -66.7657 | -0.082058 | -66.8002 | 56.2352 | 56.4267 | 56.2513 | -67.1797 | -0.1551 | -0.007303 | 0.012987 | -0.045267 | 0.10983 | -0.075369 | 0.14012 | -0.4332 | -0.10638 | -0.019178 | -0.053684 | 0.37951 | 0.085115 | -0.090249 | 123.0808 | 123.0127 | 123.2282 | 66.6609 | -123.2432 | 122.9817 | 123.1732 | 122.9978 | 66.6645 | -123.5213
2817.8594 | 123.2208 | -66.7877 | 56.3324 | -0.010607 | -0.034068 | -0.0010343 | 0.052867 | -0.0084418 | 0.06293 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.042694 | 0.055317 | -66.7335 | -0.085587 | -66.7918 | 56.3205 | 56.2708 | 56.4862 | -66.897 | -66.7611 | -0.095794 | -66.7956 | 56.2398 | 56.4358 | 56.233 | -67.1751 | -0.10932 | -0.011883 | 0.054186 | -0.004068 | 0.10525 | -0.061634 | 0.15385 | -0.38742 | -0.092646 | 0.026599 | -0.007906 | 0.37951 | 0.10343 | -0.099407 | 123.1082 | 123.0585 | 123.274 | 66.7021 | -123.2294 | 123.0275 | 123.2235 | 123.0207 | 66.6919 | -123.5075
2818.7969 | 123.2803 | -66.7419 | 56.3141 | 0.0046549 | -0.034282 | -0.0010343 | 0.053295 | -0.0082282 | 0.062289 | -0.015108 | -0.0039075 | -0.00034193 | 0.054826 | 0.043121 | 0.055744 | -66.7335 | -0.081008 | -66.7964 | 56.3251 | 56.2616 | 56.4908 | -66.897 | -66.7657 | -0.091215 | -66.7956 | 56.2306 | 56.4267 | 56.2513 | -67.1797 | -0.1551 | 0.011006 | 0.008409 | -0.054423 | 0.10067 | -0.052482 | 0.17674 | -0.43777 | -0.083492 | -0.023756 | -0.053683 | 0.38409 | 0.11258 | -0.062783 | 123.067 | 123.0035 | 123.2328 | 66.6609 | -123.2111 | 122.9725 | 123.1686 | 122.9932 | 66.6507 | -123.4938
2819.7969 | 123.2666 | -66.7191 | 56.3049 | 0.0046549 | -0.034068 | -0.0012479 | 0.053295 | -0.0084418 | 0.062717 | 0.00015261 | -0.0039075 | -0.00098273 | 0.055254 | 0.042908 | 0.055531 | -66.7335 | -0.090166 | -66.7964 | 56.3297 | 56.2708 | 56.4908 | -66.9016 | -66.7703 | -0.082058 | -66.791 | 56.2398 | 56.4267 | 56.2467 | -67.1751 | -0.18256 | 0.024739 | -0.014479 | -0.077311 | 0.10525 | -0.034169 | 0.1859 | -0.45608 | -0.065181 | -0.051223 | -0.071992 | 0.38409 | 0.12174 | -0.058207 | 123.0487 | 122.9898 | 123.2099 | 66.6289 | -123.2066 | 122.9588 | 123.1457 | 122.9658 | 66.637 | -123.4801
2820.8594 | 123.3215 | -66.7374 | 56.3141 | -0.0029761 | -0.034282 | -0.00082046 | 0.053508 | -0.0082282 | 0.062717 | 0.0077831 | -0.0039075 | -0.00076913 | 0.054826 | 0.042694 | 0.055531 | -66.7427 | -0.094744 | -66.7964 | 56.3297 | 56.2616 | 56.4862 | -66.9016 | -66.7657 | -0.086637 | -66.8002 | 56.2306 | 56.4267 | 56.233 | -67.1797 | -0.16425 | 0.015584 | -0.005325 | -0.059 | 0.10525 | -0.052482 | 0.17216 | -0.44235 | -0.083492 | -0.028333 | -0.062839 | 0.37951 | 0.11258 | -0.081097 | 123.067 | 122.999 | 123.2236 | 66.6426 | -123.2157 | 122.968 | 123.164 | 122.9704 | 66.6507 | -123.4938
2821.7969 | 123.2666 | -66.7465 | 56.3049 | 0.0046549 | -0.034068 | -0.00082046 | 0.053508 | -0.0086556 | 0.062717 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055467 | 0.043121 | 0.055744 | -66.7335 | -0.090166 | -66.8009 | 56.3251 | 56.2662 | 56.4908 | -66.8925 | -66.7703 | -0.091215 | -66.791 | 56.2306 | 56.4267 | 56.2467 | -67.1706 | -0.14594 | 0.020161 | 0.012987 | -0.054423 | 0.091517 | -0.038748 | 0.1859 | -0.42404 | -0.074337 | -0.023757 | -0.044526 | 0.37951 | 0.12174 | -0.058207 | 123.0716 | 123.0127 | 123.2373 | 66.6564 | -123.1974 | 122.9771 | 123.1732 | 122.9932 | 66.6553 | -123.4755
2822.7969 | 123.3124 | -66.7191 | 56.3232 | 0.0046549 | -0.034282 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | -0.0074779 | -0.0041211 | -0.00098273 | 0.05504 | 0.043121 | 0.055531 | -66.729 | -0.090166 | -66.7964 | 56.3297 | 56.2799 | 56.4862 | -66.9062 | -66.7565 | -0.082058 | -66.7865 | 56.2398 | 56.4267 | 56.2376 | -67.1706 | -0.18714 | 0.006429 | -0.009901 | -0.077311 | 0.10983 | -0.043321 | 0.16301 | -0.4515 | -0.083491 | -0.037487 | -0.067414 | 0.38409 | 0.10343 | -0.085674 | 123.0487 | 122.999 | 123.2053 | 66.6289 | -123.2294 | 122.9588 | 123.1457 | 122.9566 | 66.637 | -123.4938
2823.7969 | 123.2849 | -66.7374 | 56.3324 | 0.0046549 | -0.034068 | -0.00082046 | 0.053508 | -0.0084418 | 0.062717 | 0.00015261 | -0.0039075 | -0.00034193 | 0.055254 | 0.043121 | 0.055531 | -66.729 | -0.085587 | -66.7826 | 56.3205 | 56.2662 | 56.4908 | -66.9062 | -66.7657 | -0.095794 | -66.791 | 56.2443 | 56.4312 | 56.2467 | -67.1797 | -0.16883 | -0.011883 | 0.00841 | -0.045265 | 0.12357 | -0.066213 | 0.15843 | -0.44235 | -0.088067 | -0.028333 | -0.053681 | 0.38867 | 0.09885 | -0.085672 | 123.0579 | 123.0035 | 123.2282 | 66.6518 | -123.2386 | 122.9817 | 123.1686 | 122.9841 | 66.6416 | -123.5121
2824.7969 | 123.3124 | -66.7007 | 56.3507 | -0.0029761 | -0.034282 | -0.0010343 | 0.052867 | -0.0080146 | 0.062717 | 0.015414 | -0.0039075 | -0.00034193 | 0.055254 | 0.043335 | 0.055531 | -66.7335 | -0.081008 | -66.7964 | 56.3297 | 56.2753 | 56.4771 | -66.9016 | -66.7565 | -0.095794 | -66.7956 | 56.2398 | 56.4312 | 56.2193 | -67.1751 | -0.20087 | -0.021037 | -0.032789 | -0.095621 | 0.10525 | -0.075366 | 0.12638 | -0.47439 | -0.11096 | -0.055797 | -0.094881 | 0.37951 | 0.080539 | -0.13145 | 123.0304 | 122.9761 | 123.1778 | 66.6197 | -123.2523 | 122.9405 | 123.132 | 122.92 | 66.605 | -123.5258
2825.7969 | 123.262 | -66.7328 | 56.3644 | -0.010607 | -0.034282 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0034801 | -0.00055553 | 0.05504 | 0.042908 | 0.055744 | -66.729 | -0.081008 | -66.8009 | 56.3297 | 56.2799 | 56.4908 | -66.9062 | -66.7611 | -0.086637 | -66.791 | 56.2306 | 56.4312 | 56.2467 | -67.1751 | -0.17341 | -0.03477 | 0.003832 | -0.068156 | 0.10525 | -0.08452 | 0.12639 | -0.44235 | -0.13385 | -0.028333 | -0.058259 | 0.38409 | 0.066806 | -0.11772 | 123.0625 | 123.0127 | 123.2236 | 66.6518 | -123.2706 | 122.9634 | 123.164 | 122.9795 | 66.6462 | -123.5396
2826.875 | 123.1613 | -66.7648 | 56.3553 | -0.0029761 | -0.034068 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | -0.0074779 | -0.0039075 | -0.00098273 | 0.055254 | 0.043335 | 0.055531 | -66.7335 | -0.090166 | -66.7872 | 56.3342 | 56.2616 | 56.4862 | -66.9016 | -66.7611 | -0.091215 | -66.791 | 56.2398 | 56.4312 | 56.2376 | -67.1706 | -0.13679 | -0.021036 | 0.031298 | -0.022377 | 0.11441 | -0.093681 | 0.13096 | -0.40573 | -0.11554 | 0.003711 | -0.026215 | 0.37951 | 0.075961 | -0.11772 | 123.0991 | 123.0264 | 123.2511 | 66.6747 | -123.2569 | 123.0046 | 123.1961 | 123.0024 | 66.6736 | -123.5258
2827.7969 | 123.3032 | -66.7191 | 56.3095 | 0.0046549 | -0.034282 | -0.0012479 | 0.053295 | -0.0082282 | 0.062717 | -0.0074779 | -0.0039075 | -0.00076913 | 0.055254 | 0.043121 | 0.055531 | -66.7381 | -0.085587 | -66.7918 | 56.3297 | 56.257 | 56.4862 | -66.9016 | -66.7611 | -0.091215 | -66.7865 | 56.2489 | 56.4312 | 56.233 | -67.1751 | -0.18256 | 0.020162 | -0.019057 | -0.072733 | 0.10983 | -0.052483 | 0.17674 | -0.45608 | -0.060601 | -0.042066 | -0.067414 | 0.38867 | 0.12174 | -0.076519 | 123.0487 | 122.9761 | 123.2053 | 66.6335 | -123.2111 | 122.968 | 123.1503 | 122.952 | 66.6278 | -123.4846
2829.2969 | 123.1934 | -66.7694 | 56.3461 | -0.0029761 | -0.034282 | -0.00082046 | 0.053295 | -0.0080146 | 0.06293 | 0.00015261 | -0.0041211 | -0.00055553 | 0.055254 | 0.043549 | 0.055531 | -66.7335 | -0.081008 | -66.7826 | 56.3388 | 56.2708 | 56.4862 | -66.897 | -66.7611 | -0.091215 | -66.7819 | 56.2489 | 56.4358 | 56.2238 | -67.1935 | -0.12763 | -0.007302 | 0.035875 | -0.013222 | 0.11441 | -0.075367 | 0.14012 | -0.42405 | -0.097222 | 0.008288 | -0.012481 | 0.41156 | 0.089695 | -0.1223 | 123.1082 | 123.0402 | 123.2557 | 66.6884 | -123.2432 | 123.0183 | 123.2052 | 122.9932 | 66.6782 | -123.5396
2829.8906 | 123.3032 | -66.7145 | 56.3416 | 0.0046549 | -0.034495 | -0.0010343 | 0.053295 | -0.0082282 | 0.062717 | -0.0074779 | -0.0041211 | -0.00055553 | 0.05504 | 0.043549 | 0.055744 | -66.729 | -0.085587 | -66.7872 | 56.3251 | 56.2753 | 56.4817 | -66.9199 | -66.7611 | -0.095794 | -66.791 | 56.2398 | 56.4312 | 56.233 | -67.1751 | -0.20546 | -0.01646 | -0.014478 | -0.072731 | 0.13273 | -0.066211 | 0.14012 | -0.46066 | -0.1018 | -0.046643 | -0.076569 | 0.38409 | 0.089694 | -0.10856 | 123.0396 | 122.9898 | 123.1961 | 66.6289 | -123.2615 | 122.9542 | 123.1457 | 122.9475 | 66.6187 | -123.5167
2830.7969 | 123.2574 | -66.7236 | 56.3416 | 0.0046549 | -0.033854 | -0.0010343 | 0.053081 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.043335 | 0.055317 | -66.7381 | -0.094744 | -66.7918 | 56.3251 | 56.2753 | 56.4771 | -66.9016 | -66.7657 | -0.10037 | -66.7865 | 56.2352 | 56.4358 | 56.2467 | -67.1751 | -0.17799 | -0.01646 | -0.014479 | -0.068155 | 0.10983 | -0.066211 | 0.13554 | -0.4515 | -0.10638 | -0.042066 | -0.062836 | 0.38867 | 0.094272 | -0.094828 | 123.0487 | 122.999 | 123.2007 | 66.6289 | -123.2432 | 122.9588 | 123.1595 | 122.9704 | 66.6233 | -123.5167
2831.7969 | 123.3398 | -66.7053 | 56.3644 | 0.0046549 | -0.034282 | -0.0010343 | 0.053295 | -0.0082282 | 0.06293 | 0.015414 | -0.0039075 | -0.00098273 | 0.05504 | 0.042908 | 0.055531 | -66.729 | -0.085587 | -66.7964 | 56.3251 | 56.2616 | 56.4862 | -66.9108 | -66.7611 | -0.086637 | -66.7865 | 56.2398 | 56.4267 | 56.2513 | -67.1797 | -0.20546 | -0.039348 | -0.023634 | -0.091044 | 0.11441 | -0.10284 | 0.12181 | -0.4744 | -0.12469 | -0.055799 | -0.081147 | 0.39325 | 0.062227 | -0.11314 | 123.0304 | 122.9669 | 123.1916 | 66.6197 | -123.2752 | 122.9451 | 123.132 | 122.9566 | 66.6187 | -123.5442
2832.7969 | 123.2162 | -66.7465 | 56.3736 | -0.0029761 | -0.034495 | -0.00082046 | 0.053081 | -0.0084418 | 0.06293 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.043121 | 0.055744 | -66.7335 | -0.085587 | -66.7872 | 56.3297 | 56.2708 | 56.4817 | -66.8833 | -66.7611 | -0.10037 | -66.791 | 56.2352 | 56.4312 | 56.2284 | -67.1797 | -0.13678 | -0.043925 | 0.012987 | -0.040688 | 0.096094 | -0.10283 | 0.10807 | -0.4332 | -0.13842 | -0.0146 | -0.044526 | 0.38867 | 0.057651 | -0.14518 | 123.0762 | 123.0173 | 123.2282 | 66.6609 | -123.2569 | 122.9817 | 123.1778 | 122.9749 | 66.6461 | -123.5533
2833.7969 | 123.2666 | -66.7099 | 56.3736 | 0.0046549 | -0.034282 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.05504 | 0.043121 | 0.055744 | -66.7381 | -0.094744 | -66.7964 | 56.3342 | 56.2479 | 56.4817 | -66.9016 | -66.7657 | -0.091215 | -66.7865 | 56.2306 | 56.4312 | 56.2467 | -67.1751 | -0.19172 | -0.039346 | -0.028212 | -0.086466 | 0.10525 | -0.12573 | 0.10807 | -0.46524 | -0.143 | -0.055799 | -0.076569 | 0.38867 | 0.057651 | -0.12687 | 123.0442 | 122.9578 | 123.1916 | 66.6152 | -123.2752 | 122.9405 | 123.1411 | 122.9566 | 66.6187 | -123.5487
2834.7969 | 123.1934 | -66.7648 | 56.3965 | -0.010607 | -0.034282 | -0.0012479 | 0.052867 | -0.0080146 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.043121 | 0.055103 | -66.7381 | -0.090166 | -66.7964 | 56.3205 | 56.2753 | 56.4771 | -66.9108 | -66.7611 | -0.091215 | -66.7956 | 56.2398 | 56.4312 | 56.2284 | -67.1797 | -0.14594 | -0.07597 | 0.02672 | -0.031534 | 0.11441 | -0.12114 | 0.080607 | -0.41488 | -0.15673 | 0.003711 | -0.030794 | 0.38409 | 0.034763 | -0.16807 | 123.0853 | 123.0402 | 123.2419 | 66.6747 | -123.3073 | 123.0046 | 123.1961 | 122.9932 | 66.6736 | -123.5762
2835.7969 | 123.2162 | -66.7328 | 56.3599 | 0.0046549 | -0.034495 | -0.0010343 | 0.053081 | -0.0084418 | 0.062717 | 0.015414 | -0.0039075 | -0.00055553 | 0.054826 | 0.043335 | 0.055531 | -66.7335 | -0.1039 | -66.8009 | 56.3297 | 56.2799 | 56.4908 | -66.9108 | -66.7657 | -0.091215 | -66.7956 | 56.2398 | 56.4312 | 56.2559 | -67.1797 | -0.17799 | -0.030192 | -0.000746 | -0.068156 | 0.10983 | -0.079942 | 0.13096 | -0.44693 | -0.12011 | -0.032911 | -0.062838 | 0.38409 | 0.071384 | -0.10398 | 123.0625 | 123.0127 | 123.2236 | 66.6289 | -123.2706 | 122.9725 | 123.164 | 122.9887 | 66.6416 | -123.5396
2836.7969 | 123.23 | -66.7465 | 56.3782 | 0.0046549 | -0.034068 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00076913 | 0.055467 | 0.043335 | 0.055531 | -66.7335 | -0.090166 | -66.7964 | 56.3297 | 56.2708 | 56.4817 | -66.9108 | -66.7611 | -0.095794 | -66.791 | 56.2352 | 56.4358 | 56.233 | -67.1797 | -0.16426 | -0.048503 | 0.012987 | -0.049845 | 0.11441 | -0.10741 | 0.1035 | -0.4332 | -0.143 | -0.0146 | -0.044526 | 0.38867 | 0.057651 | -0.14518 | 123.0762 | 123.0173 | 123.2282 | 66.6564 | -123.289 | 122.9817 | 123.1823 | 122.9795 | 66.6507 | -123.5579
2837.7969 | 123.1842 | -66.7511 | 56.3644 | 0.0046549 | -0.034495 | -0.00082046 | 0.053081 | -0.0086556 | 0.062717 | 0.0077831 | -0.0039075 | -0.00012813 | 0.05504 | 0.042908 | 0.055317 | -66.7381 | -0.094744 | -66.7964 | 56.3251 | 56.2662 | 56.4862 | -66.9108 | -66.7611 | -0.095794 | -66.7865 | 56.2443 | 56.4312 | 56.2376 | -67.1843 | -0.15968 | -0.039348 | 0.012987 | -0.045267 | 0.11441 | -0.098257 | 0.12181 | -0.4332 | -0.12011 | -0.010022 | -0.03537 | 0.39783 | 0.066806 | -0.12687 | 123.0762 | 123.0173 | 123.2373 | 66.6564 | -123.2752 | 122.9954 | 123.1823 | 122.9887 | 66.6553 | -123.5487
2838.7969 | 123.2254 | -66.7557 | 56.3461 | 0.0046549 | -0.034282 | -0.00082046 | 0.052867 | -0.0084418 | 0.06293 | 0.0077831 | -0.0041211 | -0.00055553 | 0.055254 | 0.043549 | 0.055744 | -66.729 | -0.094744 | -66.7918 | 56.3297 | 56.2753 | 56.4954 | -66.9062 | -66.7611 | -0.095794 | -66.7956 | 56.2352 | 56.4358 | 56.2376 | -67.1751 | -0.15052 | -0.016459 | 0.02672 | -0.036112 | 0.11441 | -0.070788 | 0.14928 | -0.41946 | -0.11096 | -0.005445 | -0.03995 | 0.37951 | 0.089695 | -0.10856 | 123.0853 | 123.031 | 123.2511 | 66.6609 | -123.2523 | 122.9908 | 123.1915 | 122.9932 | 66.6599 | -123.5213
2839.7969 | 123.2071 | -66.7694 | 56.3828 | 0.0046549 | -0.034282 | -0.0014615 | 0.053081 | -0.0086556 | 0.062076 | 0.0077831 | -0.0043347 | -0.00055553 | 0.055254 | 0.043335 | 0.055531 | -66.7335 | -0.090166 | -66.7826 | 56.3251 | 56.2799 | 56.4862 | -66.9108 | -66.7565 | -0.091215 | -66.791 | 56.2352 | 56.4312 | 56.2559 | -67.1797 | -0.14137 | -0.057658 | 0.035875 | -0.013222 | 0.12815 | -0.10283 | 0.1035 | -0.41031 | -0.14758 | 0.012867 | -0.021638 | 0.38867 | 0.048496 | -0.12687 | 123.0945 | 123.0493 | 123.2557 | 66.6792 | -123.2935 | 123.0046 | 123.2007 | 123.0253 | 66.6782 | -123.5625
2840.7969 | 123.2346 | -66.7236 | 56.3324 | -0.0029761 | -0.034495 | -0.0012479 | 0.053081 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.043335 | 0.055744 | -66.7335 | -0.090166 | -66.7826 | 56.3297 | 56.2662 | 56.4817 | -66.9154 | -66.7611 | -0.10037 | -66.7956 | 56.2398 | 56.4267 | 56.2376 | -67.1751 | -0.19172 | -0.002726 | -0.009901 | -0.058998 | 0.13273 | -0.066213 | 0.14927 | -0.4515 | -0.092646 | -0.037488 | -0.071993 | 0.37951 | 0.094271 | -0.094829 | 123.0533 | 122.9898 | 123.2053 | 66.6335 | -123.2478 | 122.9634 | 123.1503 | 122.9612 | 66.6233 | -123.5075
2841.7969 | 123.2254 | -66.7419 | 56.3736 | 0.0046549 | -0.034495 | -0.00082046 | 0.053295 | -0.0086556 | 0.062503 | 0.00015261 | -0.0041211 | -0.00076913 | 0.05504 | 0.043335 | 0.055744 | -66.7381 | -0.094744 | -66.7964 | 56.3342 | 56.2662 | 56.4817 | -66.9062 | -66.7657 | -0.095794 | -66.7819 | 56.2352 | 56.4358 | 56.2376 | -67.1843 | -0.16425 | -0.039346 | 0.003831 | -0.054423 | 0.10983 | -0.10741 | 0.10807 | -0.44235 | -0.13842 | -0.023756 | -0.039947 | 0.40241 | 0.062229 | -0.13603 | 123.0762 | 123.0081 | 123.2236 | 66.6472 | -123.2798 | 122.9771 | 123.1778 | 122.9795 | 66.6461 | -123.5579
2842.7969 | 123.1888 | -66.7511 | 56.3507 | -0.010607 | -0.034495 | -0.00082046 | 0.053508 | -0.0088692 | 0.062717 | -0.0074779 | -0.0041211 | -0.00055553 | 0.055254 | 0.043121 | 0.055103 | -66.7381 | -0.081008 | -66.7872 | 56.3342 | 56.2708 | 56.4908 | -66.9199 | -66.7657 | -0.091215 | -66.7956 | 56.2352 | 56.4312 | 56.2467 | -67.1751 | -0.16884 | -0.016458 | 0.012987 | -0.03611 | 0.13273 | -0.079945 | 0.14012 | -0.42404 | -0.11553 | -0.0146 | -0.044527 | 0.37951 | 0.080539 | -0.10398 | 123.0853 | 123.0219 | 123.2419 | 66.6701 | -123.2706 | 122.9863 | 123.1823 | 122.9978 | 66.6599 | -123.5258
2843.7969 | 123.2208 | -66.7419 | 56.3736 | 0.0046549 | -0.034282 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | -0.0074779 | -0.0034801 | -0.00055553 | 0.054826 | 0.043549 | 0.055744 | -66.7381 | -0.094744 | -66.7918 | 56.3342 | 56.2662 | 56.4908 | -66.9199 | -66.7657 | -0.10037 | -66.791 | 56.2443 | 56.4221 | 56.2513 | -67.1843 | -0.17799 | -0.039346 | 0.003831 | -0.049845 | 0.12815 | -0.10741 | 0.11723 | -0.44235 | -0.12927 | -0.023756 | -0.049104 | 0.39325 | 0.048494 | -0.12229 | 123.0762 | 123.0081 | 123.2328 | 66.6472 | -123.2935 | 122.9863 | 123.164 | 122.9932 | 66.6416 | -123.5579
2844.7969 | 123.2071 | -66.7603 | 56.3507 | -0.0029761 | -0.034495 | -0.00082046 | 0.053081 | -0.0086556 | 0.062503 | -0.0074779 | -0.0036937 | -0.00076913 | 0.05504 | 0.043335 | 0.055531 | -66.729 | -0.094744 | -66.8009 | 56.3297 | 56.2845 | 56.4862 | -66.9016 | -66.7703 | -0.091215 | -66.7865 | 56.2398 | 56.4267 | 56.2467 | -67.1843 | -0.14136 | -0.021037 | 0.031298 | -0.04069 | 0.10067 | -0.066209 | 0.13554 | -0.42404 | -0.11096 | -0.010024 | -0.026215 | 0.39783 | 0.07596 | -0.10398 | 123.0899 | 123.0448 | 123.2465 | 66.6655 | -123.2523 | 123 | 123.1869 | 123.007 | 66.669 | -123.535
2845.7969 | 123.2254 | -66.7511 | 56.3278 | 0.0046549 | -0.034709 | -0.0010343 | 0.053081 | -0.0086556 | 0.062503 | -0.0074779 | -0.0039075 | -0.00055553 | 0.05504 | 0.043549 | 0.055531 | -66.729 | -0.094744 | -66.7964 | 56.3297 | 56.2616 | 56.4817 | -66.9062 | -66.7657 | -0.095794 | -66.791 | 56.2352 | 56.4312 | 56.2238 | -67.1797 | -0.1551 | 0.001851 | 0.022143 | -0.045267 | 0.10983 | -0.066215 | 0.15385 | -0.42862 | -0.092647 | -0.0146 | -0.039948 | 0.38867 | 0.10343 | -0.10399 | 123.0808 | 123.0127 | 123.2328 | 66.6564 | -123.234 | 122.9863 | 123.1823 | 122.9749 | 66.6553 | -123.5075
2846.7969 | 123.1522 | -66.774 | 56.3644 | -0.010607 | -0.034282 | -0.0012479 | 0.052867 | -0.0084418 | 0.062503 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.043549 | 0.055531 | -66.729 | -0.090166 | -66.8009 | 56.3251 | 56.2662 | 56.4862 | -66.9062 | -66.7565 | -0.10037 | -66.791 | 56.2443 | 56.4358 | 56.2467 | -67.1843 | -0.13221 | -0.039348 | 0.045031 | -0.026957 | 0.10525 | -0.098257 | 0.12181 | -0.41031 | -0.12011 | 0.017445 | -0.01706 | 0.39325 | 0.071384 | -0.11772 | 123.0991 | 123.0402 | 123.2602 | 66.6838 | -123.2706 | 123.0183 | 123.2098 | 123.0207 | 66.6736 | -123.5487
2847.7969 | 123.1888 | -66.7831 | 56.3416 | 0.0046549 | -0.034495 | -0.0014615 | 0.052867 | -0.0084418 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.043121 | 0.055744 | -66.729 | -0.094744 | -66.7964 | 56.3342 | 56.2753 | 56.4908 | -66.9154 | -66.7657 | -0.095794 | -66.7956 | 56.2443 | 56.4267 | 56.2284 | -67.1797 | -0.13221 | -0.007303 | 0.054186 | -0.013224 | 0.11899 | -0.066211 | 0.14927 | -0.39657 | -0.097223 | 0.017443 | -0.012484 | 0.38409 | 0.085115 | -0.11314 | 123.1174 | 123.0585 | 123.274 | 66.6884 | -123.2569 | 123.0275 | 123.2098 | 123.0116 | 66.6873 | -123.5213
2848.7969 | 123.2117 | -66.7603 | 56.3187 | -0.0029761 | -0.034068 | -0.00082046 | 0.052654 | -0.0084418 | 0.062076 | -0.0074779 | -0.0036937 | -0.00012813 | 0.055254 | 0.043121 | 0.055531 | -66.7335 | -0.085587 | -66.7872 | 56.3342 | 56.2753 | 56.5 | -66.9062 | -66.7565 | -0.095794 | -66.791 | 56.2398 | 56.4312 | 56.2467 | -67.1751 | -0.14594 | 0.015585 | 0.02672 | -0.026955 | 0.11899 | -0.043323 | 0.18132 | -0.41488 | -0.078914 | 0.003712 | -0.030793 | 0.38409 | 0.11258 | -0.07194 | 123.0945 | 123.0356 | 123.2602 | 66.6747 | -123.2249 | 123 | 123.1915 | 123.007 | 66.6645 | -123.4938
2849.7969 | 123.1796 | -66.7511 | 56.3553 | 0.0046549 | -0.034068 | -0.00082046 | 0.053081 | -0.0080146 | 0.062717 | -0.0074779 | -0.0039075 | -0.00034193 | 0.05504 | 0.043121 | 0.05489 | -66.7335 | -0.099323 | -66.7964 | 56.3297 | 56.2616 | 56.4862 | -66.9062 | -66.7611 | -0.095794 | -66.7956 | 56.2443 | 56.4358 | 56.2193 | -67.1889 | -0.1551 | -0.025615 | 0.017565 | -0.045267 | 0.10983 | -0.093681 | 0.13096 | -0.43778 | -0.11096 | -0.010022 | -0.044527 | 0.39325 | 0.080539 | -0.13603 | 123.0808 | 123.0127 | 123.2373 | 66.6518 | -123.2615 | 122.9954 | 123.1869 | 122.9704 | 66.6553 | -123.5442
2850.7969 | 123.2574 | -66.7511 | 56.3232 | -0.0029761 | -0.034495 | -0.0010343 | 0.053081 | -0.0080146 | 0.062289 | -0.015108 | -0.0039075 | -0.00034193 | 0.055467 | 0.043335 | 0.055531 | -66.7335 | -0.085587 | -66.7918 | 56.3297 | 56.2616 | 56.4862 | -66.9016 | -66.7611 | -0.095794 | -66.7865 | 56.2352 | 56.4312 | 56.2193 | -67.1797 | -0.15052 | 0.006429 | 0.017565 | -0.040689 | 0.10983 | -0.061637 | 0.16301 | -0.42862 | -0.088069 | -0.010022 | -0.03537 | 0.39325 | 0.108 | -0.10399 | 123.0808 | 123.0127 | 123.2373 | 66.6655 | -123.2249 | 122.9863 | 123.1823 | 122.9704 | 66.6553 | -123.503
2851.7969 | 123.1796 | -66.7877 | 56.337 | 0.0046549 | -0.034495 | -0.0010343 | 0.053081 | -0.0084418 | 0.062717 | 0.00015261 | -0.0039075 | -0.00034193 | 0.05504 | 0.043335 | 0.055317 | -66.7381 | -0.090166 | -66.7918 | 56.3159 | 56.2524 | 56.4908 | -66.9062 | -66.7611 | -0.091215 | -66.791 | 56.2398 | 56.4312 | 56.2513 | -67.1797 | -0.11848 | -0.021039 | 0.049608 | -0.004068 | 0.11441 | -0.084528 | 0.15385 | -0.392 | -0.097224 | 0.026599 | -0.003327 | 0.38867 | 0.094272 | -0.085671 | 123.1037 | 123.0402 | 123.2785 | 66.6976 | -123.2432 | 123.0275 | 123.219 | 123.039 | 66.6965 | -123.5167
2852.7969 | 123.3032 | -66.7328 | 56.3232 | 0.0046549 | -0.034709 | -0.0010343 | 0.052867 | -0.0084418 | 0.06293 | 0.00015261 | -0.0039075 | -0.00012813 | 0.05504 | 0.043121 | 0.055317 | -66.729 | -0.090166 | -66.8009 | 56.3342 | 56.2708 | 56.4862 | -66.897 | -66.7565 | -0.10037 | -66.7956 | 56.2398 | 56.4358 | 56.2467 | -67.1843 | -0.16425 | 0.011008 | 0.003832 | -0.068156 | 0.096096 | -0.052479 | 0.16301 | -0.45151 | -0.083491 | -0.023754 | -0.062838 | 0.38867 | 0.11258 | -0.076517 | 123.067 | 123.0036 | 123.219 | 66.6426 | -123.2203 | 122.9725 | 123.1686 | 122.9795 | 66.6324 | -123.5075
2853.7969 | 123.1384 | -66.7511 | 56.3416 | -0.010607 | -0.034709 | -0.0010343 | 0.053295 | -0.0082282 | 0.062503 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054826 | 0.043549 | 0.055103 | -66.7335 | -0.090166 | -66.7826 | 56.3388 | 56.257 | 56.4954 | -66.9108 | -66.7703 | -0.095794 | -66.7865 | 56.2398 | 56.4267 | 56.2284 | -67.1751 | -0.15968 | -0.002725 | 0.017565 | -0.031532 | 0.12815 | -0.084527 | 0.15385 | -0.42404 | -0.1018 | -0.019179 | -0.03537 | 0.38867 | 0.085115 | -0.11314 | 123.0899 | 123.0081 | 123.2465 | 66.6609 | -123.2523 | 122.9908 | 123.1778 | 122.9795 | 66.6553 | -123.5167
2854.7969 | 123.2941 | -66.7145 | 56.3232 | -0.010607 | -0.034495 | -0.00060686 | 0.052867 | -0.0080146 | 0.062503 | -0.015108 | -0.0041211 | -0.00055553 | 0.055254 | 0.043335 | 0.055744 | -66.7335 | -0.090166 | -66.8009 | 56.3342 | 56.2708 | 56.4954 | -66.9062 | -66.7611 | -0.095794 | -66.791 | 56.2443 | 56.4267 | 56.2467 | -67.1889 | -0.19172 | 0.011008 | -0.019056 | -0.086466 | 0.10525 | -0.052479 | 0.17216 | -0.4744 | -0.078912 | -0.046643 | -0.076569 | 0.39783 | 0.10343 | -0.076517 | 123.0487 | 122.9852 | 123.2099 | 66.6243 | -123.2294 | 122.9588 | 123.1411 | 122.9612 | 66.6187 | -123.5121
2855.7969 | 123.2666 | -66.7282 | 56.3278 | 0.012286 | -0.034923 | -0.0010343 | 0.052654 | -0.0082282 | 0.062503 | -0.015108 | -0.0041211 | -0.00055553 | 0.055254 | 0.043335 | 0.055531 | -66.729 | -0.090166 | -66.7964 | 56.3342 | 56.2616 | 56.4862 | -66.897 | -66.7611 | -0.10037 | -66.7956 | 56.2398 | 56.4312 | 56.2376 | -67.1797 | -0.16883 | 0.00643 | -0.000746 | -0.068156 | 0.10067 | -0.066215 | 0.15843 | -0.45151 | -0.088069 | -0.032911 | -0.067416 | 0.38409 | 0.10343 | -0.090252 | 123.0625 | 122.9898 | 123.2145 | 66.638 | -123.2249 | 122.968 | 123.1595 | 122.9658 | 66.6278 | -123.5075
2856.7969 | 123.262 | -66.7328 | 56.3187 | 0.0046549 | -0.034495 | -0.00082046 | 0.052867 | -0.0080146 | 0.062717 | 0.00015261 | -0.0041211 | -0.00076913 | 0.055254 | 0.043335 | 0.055531 | -66.7335 | -0.085587 | -66.7964 | 56.3251 | 56.2708 | 56.4908 | -66.9062 | -66.7565 | -0.10037 | -66.791 | 56.2352 | 56.4312 | 56.2788 | -67.1843 | -0.17341 | 0.006428 | -0.000746 | -0.063578 | 0.10983 | -0.047902 | 0.17216 | -0.45151 | -0.083492 | -0.023754 | -0.058259 | 0.39325 | 0.11258 | -0.039889 | 123.0579 | 123.0036 | 123.2236 | 66.6472 | -123.2249 | 122.968 | 123.164 | 123.0116 | 66.6324 | -123.503
2857.7969 | 123.3032 | -66.7053 | 56.2866 | -0.010607 | -0.034495 | -0.0012479 | 0.053295 | -0.0082282 | 0.062289 | 0.00015261 | -0.0043347 | -0.00055553 | 0.055254 | 0.043549 | 0.055744 | -66.7335 | -0.090166 | -66.7918 | 56.3251 | 56.2799 | 56.4908 | -66.9062 | -66.7657 | -0.10037 | -66.791 | 56.2398 | 56.4267 | 56.2467 | -67.1706 | -0.20088 | 0.038472 | -0.028212 | -0.086466 | 0.11441 | -0.0067 | 0.20421 | -0.46524 | -0.04687 | -0.060377 | -0.085725 | 0.37951 | 0.14005 | -0.039896 | 123.0304 | 122.9852 | 123.1961 | 66.6152 | -123.1928 | 122.9451 | 123.132 | 122.952 | 66.6049 | -123.4572
2858.8594 | 123.3124 | -66.7511 | 56.2958 | -0.0029761 | -0.034709 | -0.00082046 | 0.053081 | -0.0082282 | 0.062503 | -0.0074779 | -0.0036937 | -0.00076913 | 0.05504 | 0.043549 | 0.055744 | -66.7335 | -0.094744 | -66.8009 | 56.3251 | 56.2753 | 56.4908 | -66.9016 | -66.7611 | -0.095794 | -66.7956 | 56.2443 | 56.4267 | 56.2376 | -67.1751 | -0.15052 | 0.029317 | 0.017565 | -0.049845 | 0.10067 | -0.020434 | 0.19505 | -0.42404 | -0.051446 | -0.010022 | -0.044527 | 0.37951 | 0.13089 | -0.058208 | 123.0762 | 123.0264 | 123.2419 | 66.6564 | -123.1974 | 122.9954 | 123.1778 | 122.9887 | 66.6553 | -123.4709
2859.7969 | 123.3124 | -66.7236 | 56.3232 | -0.0029761 | -0.034282 | -0.00060686 | 0.053508 | -0.0084418 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.043549 | 0.055744 | -66.729 | -0.099323 | -66.7918 | 56.3297 | 56.2753 | 56.4862 | -66.9062 | -66.7657 | -0.10037 | -66.791 | 56.2352 | 56.4312 | 56.2421 | -67.1797 | -0.18256 | 0.006429 | -0.005323 | -0.068155 | 0.11441 | -0.0479 | 0.16301 | -0.45608 | -0.088069 | -0.042066 | -0.067414 | 0.38867 | 0.108 | -0.081095 | 123.0533 | 122.999 | 123.2099 | 66.6243 | -123.2294 | 122.9588 | 123.1549 | 122.9658 | 66.6233 | -123.503
2860.7969 | 123.2666 | -66.7236 | 56.337 | -0.0029761 | -0.034495 | -0.00082046 | 0.052867 | -0.0084418 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.054826 | 0.043762 | 0.055531 | -66.7335 | -0.090166 | -66.7964 | 56.3251 | 56.2662 | 56.4862 | -66.9062 | -66.7657 | -0.10037 | -66.791 | 56.2398 | 56.4404 | 56.2238 | -67.1843 | -0.18256 | -0.011882 | -0.009901 | -0.072733 | 0.10983 | -0.070791 | 0.14927 | -0.46066 | -0.097224 | -0.042066 | -0.067414 | 0.39325 | 0.10343 | -0.11314 | 123.0487 | 122.9898 | 123.2099 | 66.6335 | -123.2432 | 122.9634 | 123.164 | 122.9475 | 66.6233 | -123.5213
2861.7969 | 123.2849 | -66.7374 | 56.337 | -0.0029761 | -0.034709 | -0.00082046 | 0.052867 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00034193 | 0.055254 | 0.043549 | 0.055531 | -66.7335 | -0.099323 | -66.7964 | 56.3251 | 56.2662 | 56.4817 | -66.9062 | -66.7657 | -0.10037 | -66.791 | 56.2306 | 56.4404 | 56.2513 | -67.1797 | -0.16883 | -0.011882 | 0.003832 | -0.059 | 0.10983 | -0.070791 | 0.14469 | -0.44235 | -0.10638 | -0.028333 | -0.053681 | 0.38867 | 0.10343 | -0.085671 | 123.0625 | 123.0035 | 123.219 | 66.638 | -123.2432 | 122.968 | 123.1778 | 122.9887 | 66.637 | -123.5167
2862.7969 | 123.2391 | -66.7282 | 56.3599 | -0.0029761 | -0.034495 | -0.0010343 | 0.052867 | -0.0082282 | 0.062503 | 0.0077831 | -0.0036937 | -0.00034193 | 0.05504 | 0.043549 | 0.055958 | -66.729 | -0.090166 | -66.7872 | 56.3297 | 56.2753 | 56.4862 | -66.9062 | -66.7611 | -0.095794 | -66.7956 | 56.2398 | 56.4358 | 56.2238 | -67.1797 | -0.17799 | -0.030192 | -0.000746 | -0.058999 | 0.11899 | -0.084521 | 0.12639 | -0.45151 | -0.12011 | -0.032911 | -0.067416 | 0.38409 | 0.075962 | -0.13603 | 123.0579 | 123.0036 | 123.2145 | 66.638 | -123.2661 | 122.968 | 123.164 | 122.952 | 66.6324 | -123.5396
2863.7969 | 123.2574 | -66.7603 | 56.3278 | -0.0029761 | -0.035136 | -0.0012479 | 0.053081 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00055553 | 0.055254 | 0.043335 | 0.055531 | -66.7335 | -0.094744 | -66.7918 | 56.3251 | 56.2753 | 56.4862 | -66.9016 | -66.7611 | -0.10037 | -66.7956 | 56.2489 | 56.4358 | 56.2605 | -67.1797 | -0.14136 | -0.002727 | 0.02672 | -0.031534 | 0.10983 | -0.052478 | 0.15843 | -0.41946 | -0.078912 | -0.000867 | -0.035372 | 0.38409 | 0.108 | -0.067359 | 123.0853 | 123.0356 | 123.2465 | 66.6655 | -123.2294 | 123.0092 | 123.1961 | 123.0207 | 66.6599 | -123.5075
2864.7969 | 123.3444 | -66.6962 | 56.3461 | -0.0029761 | -0.034495 | -0.00082046 | 0.053295 | -0.0082282 | 0.062717 | 0.023044 | -0.0039075 | -0.00076913 | 0.05504 | 0.043335 | 0.055744 | -66.7244 | -0.094744 | -66.7964 | 56.3388 | 56.2799 | 56.4954 | -66.9062 | -66.7611 | -0.10495 | -66.7865 | 56.2352 | 56.4267 | 56.2513 | -67.1797 | -0.21003 | -0.007302 | -0.02821 | -0.1002 | 0.10983 | -0.066209 | 0.14928 | -0.48355 | -0.11096 | -0.064954 | -0.090302 | 0.39325 | 0.080538 | -0.094826 | 123.035 | 122.9761 | 123.1916 | 66.6014 | -123.2523 | 122.9313 | 123.1228 | 122.9475 | 66.5912 | -123.5258
2865.7969 | 123.3032 | -66.7236 | 56.3553 | -0.0029761 | -0.034709 | -0.0010343 | 0.053508 | -0.0082282 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.05504 | 0.043549 | 0.055317 | -66.7427 | -0.099323 | -66.7826 | 56.3251 | 56.2616 | 56.4817 | -66.9062 | -66.7657 | -0.10953 | -66.7819 | 56.2443 | 56.4358 | 56.2376 | -67.1843 | -0.18256 | -0.030193 | -0.019058 | -0.058998 | 0.12357 | -0.093681 | 0.12638 | -0.46066 | -0.11096 | -0.042066 | -0.058257 | 0.40241 | 0.080539 | -0.11772 | 123.0487 | 122.9852 | 123.2053 | 66.6243 | -123.2615 | 122.968 | 123.1595 | 122.9612 | 66.6141 | -123.5396
2866.7969 | 123.3261 | -66.6779 | 56.3416 | -0.0029761 | -0.034068 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00055553 | 0.055254 | 0.043335 | 0.055531 | -66.7381 | -0.1039 | -66.7964 | 56.3388 | 56.2708 | 56.4862 | -66.9108 | -66.7749 | -0.10495 | -66.791 | 56.2398 | 56.4267 | 56.2284 | -67.1751 | -0.23292 | -0.002725 | -0.060256 | -0.11851 | 0.11441 | -0.07079 | 0.1447 | -0.49728 | -0.1018 | -0.097001 | -0.11319 | 0.38409 | 0.085115 | -0.11314 | 123.0167 | 122.9486 | 123.1641 | 66.574 | -123.2523 | 122.9176 | 123.1045 | 122.9063 | 66.5729 | -123.5167
2867.7969 | 123.1888 | -66.7191 | 56.3919 | 0.0046549 | -0.035136 | -0.0010343 | 0.052867 | -0.0086556 | 0.062503 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.043549 | 0.055317 | -66.7335 | -0.1039 | -66.7964 | 56.3297 | 56.2753 | 56.4908 | -66.9016 | -66.7611 | -0.10037 | -66.791 | 56.2398 | 56.4267 | 56.2467 | -67.1889 | -0.18256 | -0.062236 | -0.014479 | -0.077311 | 0.10525 | -0.11657 | 0.09892 | -0.46982 | -0.15216 | -0.042066 | -0.071992 | 0.39783 | 0.034761 | -0.14518 | 123.0487 | 122.9944 | 123.2099 | 66.6152 | -123.2935 | 122.9588 | 123.1457 | 122.9658 | 66.6187 | -123.5808
2868.7969 | 123.2803 | -66.7236 | 56.3553 | -0.010607 | -0.034709 | -0.0012479 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0036937 | -0.00098273 | 0.05504 | 0.043335 | 0.055531 | -66.7381 | -0.10848 | -66.7964 | 56.3342 | 56.2845 | 56.4908 | -66.897 | -66.7657 | -0.10037 | -66.791 | 56.2352 | 56.4221 | 56.2467 | -67.1797 | -0.17341 | -0.021036 | -0.014479 | -0.072733 | 0.10067 | -0.070787 | 0.13554 | -0.45608 | -0.12011 | -0.042066 | -0.067414 | 0.38867 | 0.066804 | -0.10856 | 123.0579 | 123.0081 | 123.2145 | 66.6152 | -123.2523 | 122.9588 | 123.1457 | 122.9704 | 66.6233 | -123.535
2869.7969 | 123.3307 | -66.6824 | 56.3278 | -0.010607 | -0.034495 | -0.0012479 | 0.053508 | -0.0080146 | 0.062717 | 0.0077831 | -0.0039075 | -0.00076913 | 0.055254 | 0.043549 | 0.055744 | -66.7381 | -0.1039 | -66.8009 | 56.3342 | 56.2524 | 56.4908 | -66.9062 | -66.7703 | -0.10495 | -66.7956 | 56.2398 | 56.4358 | 56.2193 | -67.1889 | -0.22376 | 0.00643 | -0.055678 | -0.11851 | 0.10525 | -0.075373 | 0.16301 | -0.50644 | -0.088069 | -0.087844 | -0.11319 | 0.39325 | 0.108 | -0.10857 | 123.0167 | 122.9349 | 123.1733 | 66.5785 | -123.234 | 122.9222 | 123.1183 | 122.9017 | 66.5775 | -123.5167
2870.7969 | 123.2025 | -66.7328 | 56.3919 | -0.0029761 | -0.034495 | -0.0010343 | 0.052654 | -0.0084418 | 0.062503 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.043549 | 0.055744 | -66.7335 | -0.099323 | -66.7872 | 56.3342 | 56.2662 | 56.5 | -66.9062 | -66.7657 | -0.10037 | -66.7865 | 56.2443 | 56.4312 | 56.2421 | -67.1889 | -0.17341 | -0.057657 | -0.000746 | -0.054421 | 0.11899 | -0.12572 | 0.10808 | -0.45609 | -0.14758 | -0.032911 | -0.053681 | 0.40241 | 0.03934 | -0.14976 | 123.067 | 122.999 | 123.2328 | 66.6335 | -123.2981 | 122.9771 | 123.164 | 122.9749 | 66.6324 | -123.5808
2871.7969 | 123.3444 | -66.7053 | 56.3141 | -0.0029761 | -0.034709 | -0.00082046 | 0.053295 | -0.0084418 | 0.062289 | 0.00015261 | -0.0036937 | -0.00076913 | 0.055254 | 0.043976 | 0.055317 | -66.7335 | -0.099323 | -66.7918 | 56.3251 | 56.2708 | 56.4862 | -66.9108 | -66.7657 | -0.095794 | -66.791 | 56.2443 | 56.4267 | 56.2238 | -67.1843 | -0.20546 | 0.011006 | -0.028212 | -0.086466 | 0.11899 | -0.043324 | 0.17216 | -0.47897 | -0.069757 | -0.060377 | -0.085725 | 0.39325 | 0.11258 | -0.090255 | 123.0304 | 122.9761 | 123.1916 | 66.606 | -123.2249 | 122.9497 | 123.132 | 122.9292 | 66.6095 | -123.4984
2872.7969 | 123.23 | -66.7511 | 56.3507 | -0.010607 | -0.034709 | -0.0010343 | 0.053295 | -0.0084418 | 0.06293 | 0.00015261 | -0.0041211 | -0.00055553 | 0.05504 | 0.043549 | 0.055531 | -66.7381 | -0.094744 | -66.7872 | 56.3251 | 56.2845 | 56.4862 | -66.9108 | -66.7611 | -0.10037 | -66.791 | 56.2443 | 56.4312 | 56.2513 | -67.1797 | -0.15968 | -0.025615 | 0.012987 | -0.03611 | 0.12357 | -0.066209 | 0.13554 | -0.42862 | -0.10638 | -0.010022 | -0.039948 | 0.38867 | 0.080539 | -0.099404 | 123.0762 | 123.0356 | 123.2373 | 66.6564 | -123.2615 | 122.9954 | 123.1823 | 123.0024 | 66.6507 | -123.5304
2873.7969 | 123.3124 | -66.7191 | 56.3416 | 0.0046549 | -0.034709 | -0.0010343 | 0.053295 | -0.0082282 | 0.062717 | 0.0077831 | -0.0043347 | -0.00034193 | 0.05504 | 0.043549 | 0.055531 | -66.7335 | -0.1039 | -66.7918 | 56.3297 | 56.2753 | 56.4817 | -66.9108 | -66.7703 | -0.11869 | -66.791 | 56.2398 | 56.4312 | 56.2513 | -67.1843 | -0.19172 | -0.011882 | -0.014479 | -0.072733 | 0.11899 | -0.066211 | 0.14012 | -0.46524 | -0.1018 | -0.051223 | -0.071992 | 0.39325 | 0.089694 | -0.090249 | 123.0487 | 122.9944 | 123.2007 | 66.6152 | -123.2523 | 122.9588 | 123.1503 | 122.9704 | 66.6004 | -123.5258
2874.7969 | 123.1934 | -66.7648 | 56.3553 | 0.0046549 | -0.034923 | -0.0010343 | 0.053081 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.043762 | 0.055531 | -66.7335 | -0.1039 | -66.7872 | 56.3342 | 56.2799 | 56.4908 | -66.9108 | -66.7657 | -0.10037 | -66.7956 | 56.2352 | 56.4312 | 56.2513 | -67.1843 | -0.14594 | -0.021036 | 0.031298 | -0.022377 | 0.12357 | -0.075365 | 0.13554 | -0.41946 | -0.12011 | -0.000867 | -0.030794 | 0.38867 | 0.075961 | -0.10398 | 123.0991 | 123.0448 | 123.2557 | 66.6609 | -123.2661 | 123 | 123.1961 | 123.0161 | 66.6645 | -123.5396
2875.7969 | 123.1659 | -66.7465 | 56.3965 | -0.0029761 | -0.034495 | -0.0012479 | 0.053081 | -0.0082282 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.043549 | 0.055531 | -66.7335 | -0.099323 | -66.7872 | 56.3297 | 56.2753 | 56.4908 | -66.9062 | -66.7611 | -0.10495 | -66.7865 | 56.2398 | 56.4221 | 56.2467 | -67.1843 | -0.15968 | -0.066813 | 0.012987 | -0.040688 | 0.11899 | -0.12114 | 0.094343 | -0.43778 | -0.15673 | -0.0146 | -0.039948 | 0.39783 | 0.025606 | -0.14976 | 123.0762 | 123.0219 | 123.2373 | 66.6472 | -123.3027 | 122.9863 | 123.1686 | 122.9932 | 66.6416 | -123.5808
2876.7969 | 123.2254 | -66.7511 | 56.3416 | 0.0046549 | -0.034709 | -0.00060686 | 0.053081 | -0.0084418 | 0.062717 | 0.0077831 | -0.0039075 | -0.00055553 | 0.055254 | 0.043762 | 0.055317 | -66.7381 | -0.094744 | -66.8009 | 56.3342 | 56.2799 | 56.4908 | -66.9108 | -66.7611 | -0.10037 | -66.791 | 56.2398 | 56.4358 | 56.2376 | -67.1751 | -0.15968 | -0.007303 | 0.012987 | -0.049845 | 0.10983 | -0.061632 | 0.14927 | -0.42404 | -0.1018 | -0.010022 | -0.039948 | 0.38409 | 0.094272 | -0.10398 | 123.0853 | 123.031 | 123.2419 | 66.6564 | -123.2523 | 122.9908 | 123.1869 | 122.9887 | 66.6507 | -123.5167
2877.7969 | 123.2529 | -66.7557 | 56.2866 | -0.018238 | -0.034709 | -0.0010343 | 0.053081 | -0.0084418 | 0.062503 | -0.0074779 | -0.0039075 | -0.00034193 | 0.054826 | 0.043762 | 0.055531 | -66.7473 | -0.1039 | -66.7918 | 56.3297 | 56.2662 | 56.4771 | -66.9108 | -66.7565 | -0.10495 | -66.791 | 56.2443 | 56.4312 | 56.2238 | -67.1797 | -0.1551 | 0.04305 | 0.008407 | -0.036112 | 0.11899 | -0.020437 | 0.19047 | -0.42404 | -0.042291 | -0.000866 | -0.035371 | 0.38867 | 0.14463 | -0.062789 | 123.0853 | 123.0219 | 123.2328 | 66.6518 | -123.1974 | 123 | 123.1869 | 122.9795 | 66.6507 | -123.4663
2878.7969 | 123.2437 | -66.7557 | 56.3553 | 0.0046549 | -0.034709 | -0.0010343 | 0.052867 | -0.0082282 | 0.062289 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.043549 | 0.055531 | -66.7381 | -0.099323 | -66.7826 | 56.3342 | 56.2708 | 56.4817 | -66.9062 | -66.7657 | -0.10037 | -66.791 | 56.2398 | 56.4312 | 56.2467 | -67.1797 | -0.15052 | -0.021036 | 0.017564 | -0.026955 | 0.12357 | -0.084523 | 0.12638 | -0.42404 | -0.11554 | -0.010023 | -0.035371 | 0.38867 | 0.075961 | -0.10856 | 123.0899 | 123.0264 | 123.2373 | 66.6564 | -123.2615 | 122.9954 | 123.1869 | 123.0024 | 66.6553 | -123.535
2879.7969 | 123.175 | -66.7603 | 56.369 | 0.0046549 | -0.034923 | -0.00082046 | 0.053295 | -0.0082282 | 0.062503 | 0.015414 | -0.0041211 | -0.00098273 | 0.05504 | 0.043762 | 0.055103 | -66.7381 | -0.094744 | -66.7964 | 56.3342 | 56.2845 | 56.4908 | -66.9154 | -66.7565 | -0.095794 | -66.7865 | 56.2443 | 56.4312 | 56.2513 | -67.1797 | -0.1551 | -0.034769 | 0.022142 | -0.036112 | 0.11899 | -0.08452 | 0.12181 | -0.41946 | -0.12469 | 0.003712 | -0.026215 | 0.39325 | 0.062228 | -0.11772 | 123.0945 | 123.0448 | 123.2511 | 66.6655 | -123.2844 | 123.0046 | 123.1915 | 123.0116 | 66.6645 | -123.5487
2880.8594 | 123.2071 | -66.7557 | 56.3507 | 0.0046549 | -0.034709 | -0.0010343 | 0.052654 | -0.0084418 | 0.062503 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054826 | 0.04419 | 0.055317 | -66.7335 | -0.099323 | -66.8009 | 56.3342 | 56.2662 | 56.4908 | -66.9154 | -66.7611 | -0.095794 | -66.8002 | 56.2489 | 56.4267 | 56.2376 | -67.1843 | -0.15968 | -0.016458 | 0.022142 | -0.045268 | 0.11441 | -0.084524 | 0.14012 | -0.42862 | -0.1018 | -0.005445 | -0.044529 | 0.38409 | 0.07596 | -0.11314 | 123.0899 | 123.0219 | 123.2465 | 66.6564 | -123.2661 | 123.0046 | 123.1823 | 122.9932 | 66.6599 | -123.535
2881.7969 | 123.2254 | -66.7465 | 56.3553 | 0.0046549 | -0.034923 | -0.0014615 | 0.053081 | -0.0080146 | 0.062503 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.043762 | 0.055531 | -66.729 | -0.099323 | -66.7918 | 56.3342 | 56.2937 | 56.4908 | -66.9108 | -66.7565 | -0.10953 | -66.7865 | 56.2398 | 56.4312 | 56.2284 | -67.1889 | -0.16426 | -0.021036 | 0.017565 | -0.045267 | 0.11899 | -0.061629 | 0.13554 | -0.44235 | -0.11554 | -0.010021 | -0.039948 | 0.40241 | 0.075961 | -0.12687 | 123.0808 | 123.0402 | 123.2373 | 66.6472 | -123.2661 | 122.9863 | 123.1778 | 122.9749 | 66.637 | -123.5442
2882.7969 | 123.2574 | -66.7236 | 56.3095 | 0.0046549 | -0.034709 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | 0.015414 | -0.0039075 | -0.00055553 | 0.055254 | 0.043549 | 0.055531 | -66.7335 | -0.099323 | -66.7918 | 56.3297 | 56.2662 | 56.4908 | -66.9016 | -66.7657 | -0.10037 | -66.8002 | 56.2398 | 56.4358 | 56.2376 | -67.1797 | -0.17799 | 0.020162 | -0.009901 | -0.068155 | 0.10983 | -0.043325 | 0.18132 | -0.45608 | -0.069758 | -0.042066 | -0.076572 | 0.37951 | 0.12632 | -0.071941 | 123.0533 | 122.9898 | 123.2145 | 66.6243 | -123.2111 | 122.9634 | 123.1595 | 122.9612 | 66.6233 | -123.4892
2883.7969 | 123.2346 | -66.7465 | 56.3599 | 0.0046549 | -0.034709 | -0.0012479 | 0.052867 | -0.0086556 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.05504 | 0.043549 | 0.055531 | -66.7381 | -0.094744 | -66.7918 | 56.3297 | 56.2799 | 56.4954 | -66.9108 | -66.7657 | -0.091215 | -66.791 | 56.2398 | 56.4312 | 56.233 | -67.1797 | -0.16426 | -0.030192 | 0.008409 | -0.045267 | 0.11899 | -0.079942 | 0.13554 | -0.4332 | -0.12011 | -0.019178 | -0.044526 | 0.38867 | 0.071384 | -0.12687 | 123.0762 | 123.0264 | 123.2419 | 66.6518 | -123.2706 | 122.9863 | 123.1778 | 122.9795 | 66.6553 | -123.5396
2884.7969 | 123.1979 | -66.7969 | 56.337 | -0.010607 | -0.035136 | -0.0010343 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0045483 | -0.00076913 | 0.05504 | 0.043762 | 0.055317 | -66.729 | -0.1039 | -66.7872 | 56.3297 | 56.2891 | 56.4954 | -66.9108 | -66.7565 | -0.10037 | -66.791 | 56.2489 | 56.4358 | 56.2513 | -67.1797 | -0.1139 | -0.007304 | 0.067919 | 0.009666 | 0.12357 | -0.047897 | 0.15843 | -0.38284 | -0.088067 | 0.040333 | 0.005828 | 0.38867 | 0.09885 | -0.085671 | 123.1265 | 123.086 | 123.2923 | 66.693 | -123.2478 | 123.0458 | 123.2327 | 123.0482 | 66.6965 | -123.5167
2885.7969 | 123.2391 | -66.7786 | 56.3324 | -0.010607 | -0.034709 | -0.0010343 | 0.053081 | -0.0084418 | 0.062503 | 0.0077831 | -0.0034801 | -0.00034193 | 0.054826 | 0.043549 | 0.055531 | -66.7381 | -0.090166 | -66.7781 | 56.3342 | 56.2937 | 56.4954 | -66.9108 | -66.7565 | -0.10037 | -66.791 | 56.2398 | 56.4312 | 56.2421 | -67.1797 | -0.13221 | 0.001853 | 0.040452 | 0.000511 | 0.13272 | -0.03874 | 0.16301 | -0.40115 | -0.092646 | 0.022022 | -0.012483 | 0.38867 | 0.09885 | -0.09025 | 123.1128 | 123.0722 | 123.274 | 66.6884 | -123.2432 | 123.0183 | 123.2098 | 123.0207 | 66.6782 | -123.5121
2886.7969 | 123.2025 | -66.7786 | 56.337 | -0.0029761 | -0.034709 | -0.0010343 | 0.053295 | -0.0086556 | 0.062289 | -0.0074779 | -0.0039075 | -0.00055553 | 0.054826 | 0.043335 | 0.055531 | -66.729 | -0.094744 | -66.7826 | 56.3297 | 56.2616 | 56.4817 | -66.9062 | -66.7657 | -0.095794 | -66.791 | 56.2489 | 56.4358 | 56.2376 | -67.1843 | -0.12763 | -0.007304 | 0.049608 | -0.004067 | 0.12357 | -0.07537 | 0.14469 | -0.40573 | -0.088067 | 0.012865 | -0.012483 | 0.39325 | 0.09885 | -0.099407 | 123.1082 | 123.0402 | 123.2602 | 66.6838 | -123.2432 | 123.0275 | 123.2144 | 123.0161 | 66.6828 | -123.5213
2887.7969 | 123.2758 | -66.7374 | 56.3095 | -0.0029761 | -0.034709 | -0.0010343 | 0.052867 | -0.0084418 | 0.062717 | 0.00015261 | -0.0036937 | -0.00055553 | 0.054826 | 0.043762 | 0.055317 | -66.7335 | -0.099323 | -66.7918 | 56.3342 | 56.2616 | 56.4908 | -66.9016 | -66.7611 | -0.095794 | -66.7865 | 56.2489 | 56.4312 | 56.2559 | -67.1889 | -0.16425 | 0.024741 | 0.003832 | -0.054422 | 0.10983 | -0.047904 | 0.18132 | -0.45151 | -0.060601 | -0.023755 | -0.049103 | 0.40241 | 0.12174 | -0.053626 | 123.0716 | 122.999 | 123.2282 | 66.638 | -123.2111 | 122.9863 | 123.1686 | 122.9932 | 66.6416 | -123.4984
2888.7969 | 123.2254 | -66.774 | 56.3416 | -0.010607 | -0.034495 | -0.0010343 | 0.052654 | -0.0084418 | 0.062717 | 0.0077831 | -0.0041211 | -0.00098273 | 0.055254 | 0.043762 | 0.055744 | -66.7335 | -0.094744 | -66.7872 | 56.3342 | 56.2708 | 56.4908 | -66.9016 | -66.7565 | -0.095794 | -66.7956 | 56.2443 | 56.4267 | 56.2284 | -67.1797 | -0.12763 | -0.007303 | 0.040453 | -0.013222 | 0.11441 | -0.07079 | 0.14927 | -0.40573 | -0.097223 | 0.017445 | -0.021639 | 0.38409 | 0.085115 | -0.11314 | 123.1082 | 123.0448 | 123.2648 | 66.6792 | -123.2432 | 123.0183 | 123.2007 | 123.0024 | 66.6782 | -123.5213
2889.7969 | 123.1705 | -66.7831 | 56.3644 | -0.010607 | -0.035136 | -0.0012479 | 0.052867 | -0.0084418 | 0.062503 | 0.00015261 | -0.0041211 | -0.00012813 | 0.05504 | 0.043549 | 0.055317 | -66.7381 | -0.094744 | -66.7872 | 56.3297 | 56.2708 | 56.4862 | -66.9108 | -66.7565 | -0.095794 | -66.7865 | 56.2489 | 56.4312 | 56.2467 | -67.1797 | -0.12763 | -0.03477 | 0.04503 | -0.004067 | 0.12357 | -0.093678 | 0.12181 | -0.39657 | -0.11553 | 0.0266 | -0.003327 | 0.39325 | 0.066806 | -0.11772 | 123.1128 | 123.0539 | 123.2694 | 66.6884 | -123.2752 | 123.032 | 123.2144 | 123.0299 | 66.6873 | -123.5442
2890.7969 | 123.2529 | -66.774 | 56.3324 | -0.0029761 | -0.035136 | -0.0010343 | 0.052867 | -0.0084418 | 0.062289 | -0.0074779 | -0.0039075 | -0.00055553 | 0.054613 | 0.043762 | 0.055531 | -66.7335 | -0.094744 | -66.7918 | 56.3342 | 56.2708 | 56.4862 | -66.9108 | -66.7611 | -0.10037 | -66.7865 | 56.2352 | 56.4358 | 56.2559 | -67.1797 | -0.13679 | 0.001853 | 0.040453 | -0.017801 | 0.11899 | -0.061634 | 0.15385 | -0.40573 | -0.097224 | 0.012866 | -0.012482 | 0.39325 | 0.10343 | -0.076514 | 123.1082 | 123.0448 | 123.2602 | 66.6792 | -123.2432 | 123.0092 | 123.2098 | 123.0299 | 66.6736 | -123.5121
2891.8594 | 123.2666 | -66.7419 | 56.3644 | -0.0029761 | -0.034923 | -0.0012479 | 0.053081 | -0.0084418 | 0.062717 | 0.015414 | -0.0043347 | -0.00055553 | 0.055254 | 0.043549 | 0.055317 | -66.7427 | -0.1039 | -66.7964 | 56.3342 | 56.2937 | 56.4908 | -66.9062 | -66.7611 | -0.10037 | -66.791 | 56.2398 | 56.4358 | 56.2421 | -67.1797 | -0.16425 | -0.030191 | -0.000748 | -0.054423 | 0.10983 | -0.070784 | 0.12639 | -0.43777 | -0.12469 | -0.019178 | -0.049104 | 0.38867 | 0.071384 | -0.12229 | 123.0762 | 123.0356 | 123.2328 | 66.638 | -123.2706 | 122.9817 | 123.1778 | 122.9841 | 66.6416 | -123.5442
2892.7969 | 123.3032 | -66.7465 | 56.2958 | -0.0029761 | -0.034709 | -0.0014615 | 0.053295 | -0.0082282 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.05504 | 0.043976 | 0.055958 | -66.7335 | -0.090166 | -66.7964 | 56.3297 | 56.2891 | 56.4954 | -66.9062 | -66.7611 | -0.10037 | -66.7956 | 56.2443 | 56.4312 | 56.233 | -67.1843 | -0.15968 | 0.033895 | 0.012987 | -0.049845 | 0.10983 | -0.006698 | 0.19963 | -0.43778 | -0.051446 | -0.0146 | -0.049105 | 0.38867 | 0.13547 | -0.062786 | 123.0762 | 123.0356 | 123.2419 | 66.6564 | -123.202 | 122.9909 | 123.1778 | 122.9795 | 66.6461 | -123.4801
2893.7969 | 123.1888 | -66.7831 | 56.3599 | -0.0029761 | -0.034923 | -0.00082046 | 0.053081 | -0.0082282 | 0.062717 | 0.0077831 | -0.0041211 | -0.00055553 | 0.055254 | 0.043976 | 0.055744 | -66.729 | -0.094744 | -66.7964 | 56.3342 | 56.2708 | 56.4908 | -66.9062 | -66.7657 | -0.10495 | -66.7956 | 56.2352 | 56.4358 | 56.2376 | -67.1751 | -0.12306 | -0.025613 | 0.054186 | -0.013224 | 0.10983 | -0.0891 | 0.13096 | -0.392 | -0.12469 | 0.017443 | -0.012484 | 0.37951 | 0.075962 | -0.12229 | 123.1174 | 123.0539 | 123.274 | 66.6884 | -123.2661 | 123.0183 | 123.219 | 123.0207 | 66.6782 | -123.535
2894.7969 | 123.2895 | -66.7419 | 56.3141 | -0.0029761 | -0.034923 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0041211 | -0.00055553 | 0.055254 | 0.043762 | 0.055744 | -66.7381 | -0.094744 | -66.7918 | 56.3342 | 56.2662 | 56.4908 | -66.9108 | -66.7657 | -0.10495 | -66.791 | 56.2398 | 56.4312 | 56.2605 | -67.1797 | -0.16883 | 0.020163 | 0.003831 | -0.049845 | 0.11899 | -0.047903 | 0.17674 | -0.43777 | -0.074336 | -0.023756 | -0.049104 | 0.38867 | 0.11716 | -0.053626 | 123.0762 | 123.0081 | 123.2328 | 66.6472 | -123.2249 | 122.9817 | 123.1732 | 123.0024 | 66.637 | -123.4938
2895.7969 | 123.2666 | -66.7694 | 56.3324 | -0.0029761 | -0.034923 | -0.0012479 | 0.053081 | -0.0086556 | 0.062717 | 0.0077831 | -0.0041211 | -0.00076913 | 0.05504 | 0.043762 | 0.055531 | -66.7381 | -0.099323 | -66.7964 | 56.3251 | 56.257 | 56.4908 | -66.9108 | -66.7657 | -0.10037 | -66.7865 | 56.2398 | 56.4312 | 56.2284 | -67.1843 | -0.14137 | -0.007304 | 0.031297 | -0.026957 | 0.11441 | -0.075371 | 0.15843 | -0.41489 | -0.092646 | 0.00371 | -0.01706 | 0.39783 | 0.09885 | -0.10399 | 123.0945 | 123.0264 | 123.2602 | 66.6701 | -123.2432 | 123.0092 | 123.2007 | 122.9978 | 66.669 | -123.5167
2896.7969 | 123.3215 | -66.7328 | 56.3049 | -0.018238 | -0.034495 | -0.0012479 | 0.053081 | -0.0082282 | 0.062503 | -0.0074779 | -0.0041211 | -0.00055553 | 0.05504 | 0.043549 | 0.055317 | -66.7381 | -0.1039 | -66.7918 | 56.3297 | 56.2753 | 56.4862 | -66.9062 | -66.7611 | -0.10495 | -66.791 | 56.2535 | 56.4404 | 56.233 | -67.1889 | -0.17341 | 0.024739 | -0.005324 | -0.059 | 0.11441 | -0.02959 | 0.18132 | -0.45609 | -0.051445 | -0.028333 | -0.058259 | 0.39783 | 0.13547 | -0.071942 | 123.0625 | 123.0081 | 123.219 | 66.6289 | -123.2111 | 122.9863 | 123.1732 | 122.9658 | 66.6278 | -123.4938
2897.7969 | 123.2941 | -66.7511 | 56.3095 | -0.0029761 | -0.034282 | -0.0010343 | 0.053295 | -0.0082282 | 0.062289 | 0.00015261 | -0.0041211 | -0.00055553 | 0.05504 | 0.043762 | 0.055531 | -66.7381 | -0.10848 | -66.7826 | 56.3297 | 56.2799 | 56.4862 | -66.9062 | -66.7611 | -0.10495 | -66.791 | 56.2535 | 56.4358 | 56.2467 | -67.1751 | -0.1551 | 0.020162 | 0.012987 | -0.031532 | 0.12357 | -0.029588 | 0.17674 | -0.42404 | -0.056022 | -0.010022 | -0.039948 | 0.38409 | 0.12632 | -0.062784 | 123.0808 | 123.031 | 123.2373 | 66.6426 | -123.2157 | 123.0046 | 123.1869 | 122.9978 | 66.6461 | -123.4846
2898.8594 | 123.1979 | -66.7419 | 56.3599 | -0.0029761 | -0.034709 | -0.0010343 | 0.053081 | -0.0086556 | 0.062717 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054826 | 0.043762 | 0.055317 | -66.7473 | -0.094744 | -66.7918 | 56.3342 | 56.2616 | 56.4862 | -66.9108 | -66.7565 | -0.10037 | -66.7819 | 56.2535 | 56.4404 | 56.233 | -67.1843 | -0.16883 | -0.025613 | -0.005326 | -0.049845 | 0.11899 | -0.098258 | 0.12639 | -0.44235 | -0.10638 | -0.014599 | -0.039947 | 0.40241 | 0.080541 | -0.12687 | 123.0762 | 123.0035 | 123.2282 | 66.6472 | -123.2706 | 122.9954 | 123.1823 | 122.9749 | 66.6416 | -123.5442
2899.7969 | 123.2941 | -66.7099 | 56.2958 | -0.0029761 | -0.034709 | -0.0010343 | 0.053081 | -0.0082282 | 0.06293 | -0.0074779 | -0.0041211 | -0.00055553 | 0.055254 | 0.043762 | 0.055317 | -66.7335 | -0.099323 | -66.8009 | 56.3342 | 56.2662 | 56.4817 | -66.9062 | -66.7657 | -0.10495 | -66.7956 | 56.2489 | 56.4358 | 56.2284 | -67.1843 | -0.1963 | 0.038474 | -0.023634 | -0.091044 | 0.10525 | -0.029592 | 0.18589 | -0.4744 | -0.046868 | -0.055799 | -0.085726 | 0.38867 | 0.14005 | -0.067365 | 123.0442 | 122.9761 | 123.1916 | 66.6106 | -123.202 | 122.9588 | 123.1457 | 122.9383 | 66.6049 | -123.4801
2900.7969 | 123.262 | -66.7374 | 56.3599 | -0.010607 | -0.034495 | -0.00082046 | 0.053295 | -0.0086556 | 0.062717 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.043976 | 0.055531 | -66.7381 | -0.1039 | -66.7872 | 56.3297 | 56.2753 | 56.4908 | -66.9154 | -66.7611 | -0.10037 | -66.8002 | 56.2581 | 56.4358 | 56.2467 | -67.1797 | -0.17799 | -0.030192 | -0.000746 | -0.049843 | 0.12815 | -0.084521 | 0.13096 | -0.44235 | -0.1018 | -0.023755 | -0.062839 | 0.37951 | 0.075962 | -0.11314 | 123.067 | 123.0127 | 123.2282 | 66.6335 | -123.2752 | 122.9954 | 123.1732 | 122.9841 | 66.637 | -123.5396
2901.7969 | 123.3124 | -66.7282 | 56.3187 | 0.012286 | -0.034709 | -0.00082046 | 0.053295 | -0.0084418 | 0.062717 | -0.0074779 | -0.0039075 | -0.00055553 | 0.05504 | 0.043762 | 0.055317 | -66.7381 | -0.099323 | -66.8009 | 56.3342 | 56.2753 | 56.5 | -66.9062 | -66.7611 | -0.10495 | -66.791 | 56.2489 | 56.4404 | 56.2421 | -67.1889 | -0.17799 | 0.015585 | -0.009902 | -0.072734 | 0.10525 | -0.043323 | 0.18132 | -0.46066 | -0.069757 | -0.032911 | -0.062837 | 0.39783 | 0.12174 | -0.076518 | 123.0625 | 123.0036 | 123.2282 | 66.6289 | -123.2249 | 122.9771 | 123.1686 | 122.9704 | 66.6233 | -123.5075
2902.7969 | 123.23 | -66.7419 | 56.3507 | 0.0046549 | -0.035136 | -0.0014615 | 0.053081 | -0.0086556 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.04419 | 0.055317 | -66.7381 | -0.1039 | -66.7872 | 56.3342 | 56.2708 | 56.4817 | -66.9154 | -66.7657 | -0.10037 | -66.791 | 56.2489 | 56.4312 | 56.2376 | -67.1843 | -0.17341 | -0.016458 | 0.003831 | -0.045266 | 0.12815 | -0.079945 | 0.13096 | -0.44235 | -0.1018 | -0.023756 | -0.049104 | 0.39325 | 0.080539 | -0.11314 | 123.0762 | 123.0127 | 123.2236 | 66.638 | -123.2661 | 122.9909 | 123.1732 | 122.9795 | 66.6416 | -123.535
2903.7969 | 123.2986 | -66.7374 | 56.3095 | -0.010607 | -0.035136 | -0.0012479 | 0.053081 | -0.0086556 | 0.062717 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054826 | 0.043976 | 0.055531 | -66.7381 | -0.099323 | -66.8009 | 56.3342 | 56.2753 | 56.4862 | -66.9108 | -66.7657 | -0.10037 | -66.7956 | 56.2489 | 56.4358 | 56.2605 | -67.1889 | -0.17341 | 0.024741 | -0.000746 | -0.063578 | 0.10983 | -0.034167 | 0.17674 | -0.45151 | -0.060601 | -0.028333 | -0.05826 | 0.39325 | 0.12632 | -0.049048 | 123.0716 | 123.0127 | 123.2236 | 66.638 | -123.2203 | 122.9863 | 123.1732 | 122.9978 | 66.637 | -123.4984
2904.7969 | 123.2758 | -66.6962 | 56.3553 | 0.0046549 | -0.034923 | -0.0010343 | 0.053081 | -0.0086556 | 0.062289 | 0.0077831 | -0.0041211 | -0.00034193 | 0.05504 | 0.043976 | 0.055531 | -66.7427 | -0.099323 | -66.7918 | 56.3388 | 56.2753 | 56.5 | -66.9062 | -66.7611 | -0.10495 | -66.791 | 56.2535 | 56.4358 | 56.2421 | -67.1935 | -0.21003 | -0.016458 | -0.046524 | -0.095621 | 0.11441 | -0.079944 | 0.1447 | -0.49729 | -0.1018 | -0.064954 | -0.09488 | 0.40241 | 0.080539 | -0.11314 | 123.035 | 122.9715 | 123.1962 | 66.5968 | -123.2615 | 122.9497 | 123.132 | 122.9383 | 66.5912 | -123.5487
2905.8594 | 123.23 | -66.7374 | 56.3324 | -0.0029761 | -0.034923 | -0.00082046 | 0.053081 | -0.0082282 | 0.062289 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.043762 | 0.055103 | -66.7335 | -0.099323 | -66.8009 | 56.3342 | 56.2662 | 56.4908 | -66.9062 | -66.7611 | -0.10495 | -66.7865 | 56.2443 | 56.4312 | 56.2605 | -67.1889 | -0.16883 | 0.001853 | 0.003832 | -0.063578 | 0.10525 | -0.066213 | 0.15843 | -0.45151 | -0.088067 | -0.023755 | -0.049103 | 0.40241 | 0.09885 | -0.071936 | 123.0716 | 123.0035 | 123.2282 | 66.638 | -123.2386 | 122.9817 | 123.1686 | 122.9978 | 66.6324 | -123.5213
2906.7969 | 123.3215 | -66.7282 | 56.3324 | -0.018238 | -0.034923 | -0.0010343 | 0.053081 | -0.0084418 | 0.062289 | 0.00015261 | -0.0041211 | -0.00076913 | 0.055254 | 0.04419 | 0.055317 | -66.7381 | -0.1039 | -66.8009 | 56.3342 | 56.2708 | 56.4862 | -66.9108 | -66.7657 | -0.10495 | -66.791 | 56.2535 | 56.4312 | 56.2284 | -67.1797 | -0.18257 | 0.001853 | -0.009902 | -0.072734 | 0.10983 | -0.061634 | 0.15385 | -0.45151 | -0.07891 | -0.037489 | -0.062837 | 0.38867 | 0.09885 | -0.10399 | 123.0625 | 122.999 | 123.2145 | 66.6243 | -123.2432 | 122.9817 | 123.1595 | 122.9566 | 66.6233 | -123.5121
2907.7969 | 123.262 | -66.7511 | 56.3187 | -0.0029761 | -0.034923 | -0.00082046 | 0.053081 | -0.0084418 | 0.06293 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054826 | 0.043762 | 0.055744 | -66.7427 | -0.1039 | -66.7964 | 56.3297 | 56.2524 | 56.4908 | -66.9062 | -66.7657 | -0.10037 | -66.8002 | 56.2581 | 56.4267 | 56.2147 | -67.1889 | -0.1551 | 0.011006 | 0.008408 | -0.045267 | 0.10983 | -0.066218 | 0.17216 | -0.43778 | -0.0606 | -0.0146 | -0.049106 | 0.38867 | 0.108 | -0.10399 | 123.0808 | 123.0035 | 123.2419 | 66.6472 | -123.2249 | 123.0092 | 123.1778 | 122.9658 | 66.6507 | -123.5075
2908.7969 | 123.2803 | -66.687 | 56.369 | -0.0029761 | -0.035136 | -0.0012479 | 0.053295 | -0.0084418 | 0.062289 | 0.00015261 | -0.0036937 | -0.00055553 | 0.054613 | 0.043976 | 0.055744 | -66.7427 | -0.1039 | -66.7964 | 56.3297 | 56.2662 | 56.4908 | -66.9062 | -66.7657 | -0.10495 | -66.7956 | 56.2489 | 56.4358 | 56.2513 | -67.1797 | -0.21919 | -0.039348 | -0.055679 | -0.10935 | 0.10983 | -0.10283 | 0.12181 | -0.49271 | -0.12011 | -0.078687 | -0.10861 | 0.38409 | 0.066806 | -0.11772 | 123.0167 | 122.9532 | 123.1778 | 66.5831 | -123.2752 | 122.9359 | 123.1228 | 122.9383 | 66.5821 | -123.5487
2909.7969 | 123.2529 | -66.7374 | 56.3507 | -0.0029761 | -0.03535 | -0.0010343 | 0.053295 | -0.0084418 | 0.062717 | 0.00015261 | -0.0036937 | -0.00012813 | 0.05504 | 0.04419 | 0.055317 | -66.7381 | -0.099323 | -66.7918 | 56.3388 | 56.2616 | 56.4954 | -66.9016 | -66.7611 | -0.10495 | -66.7865 | 56.2581 | 56.4358 | 56.2421 | -67.1889 | -0.16425 | -0.01188 | -0.000746 | -0.054422 | 0.10983 | -0.089103 | 0.1447 | -0.45151 | -0.092643 | -0.023755 | -0.049103 | 0.40241 | 0.085117 | -0.10856 | 123.0762 | 122.999 | 123.2328 | 66.638 | -123.2523 | 122.9954 | 123.1732 | 122.9795 | 66.6324 | -123.5396
2910.7969 | 123.3307 | -66.6824 | 56.3507 | -0.0029761 | -0.035136 | -0.00082046 | 0.053508 | -0.0084418 | 0.062717 | 0.0077831 | -0.0041211 | -0.00034193 | 0.055254 | 0.04419 | 0.055531 | -66.7427 | -0.1039 | -66.7826 | 56.3342 | 56.2753 | 56.4862 | -66.9062 | -66.7611 | -0.10495 | -66.8002 | 56.2581 | 56.4358 | 56.2559 | -67.1843 | -0.22376 | -0.016458 | -0.060257 | -0.1002 | 0.12357 | -0.075366 | 0.13554 | -0.50186 | -0.092643 | -0.078687 | -0.11777 | 0.38409 | 0.085117 | -0.094825 | 123.0167 | 122.9578 | 123.1687 | 66.5785 | -123.2569 | 122.9405 | 123.1183 | 122.9383 | 66.5775 | -123.535
2911.7969 | 123.2712 | -66.7145 | 56.337 | -0.0029761 | -0.034923 | -0.00082046 | 0.053295 | -0.0086556 | 0.062503 | 0.0077831 | -0.0039075 | -0.00034193 | 0.05504 | 0.04419 | 0.055103 | -66.7335 | -0.099323 | -66.7872 | 56.3297 | 56.2799 | 56.4954 | -66.9062 | -66.7703 | -0.10495 | -66.791 | 56.2581 | 56.4312 | 56.2421 | -67.1889 | -0.19172 | -0.007304 | -0.019056 | -0.072731 | 0.11899 | -0.057054 | 0.15843 | -0.4744 | -0.07891 | -0.0558 | -0.076569 | 0.39783 | 0.094272 | -0.094828 | 123.0441 | 122.9944 | 123.2099 | 66.6152 | -123.2432 | 122.9725 | 123.1457 | 122.9566 | 66.6095 | -123.5258
2912.7969 | 123.3307 | -66.7099 | 56.3599 | -0.0029761 | -0.035136 | -0.00082046 | 0.053508 | -0.0082282 | 0.062503 | -0.0074779 | -0.0039075 | -0.00034193 | 0.055254 | 0.044403 | 0.055317 | -66.7381 | -0.1039 | -66.7918 | 56.3342 | 56.2708 | 56.4954 | -66.9016 | -66.7611 | -0.10953 | -66.791 | 56.2581 | 56.4404 | 56.265 | -67.1889 | -0.19172 | -0.025613 | -0.028212 | -0.081888 | 0.10983 | -0.0891 | 0.13554 | -0.47897 | -0.1018 | -0.051221 | -0.081147 | 0.39783 | 0.080541 | -0.094823 | 123.0442 | 122.9807 | 123.2053 | 66.606 | -123.2615 | 122.968 | 123.1503 | 122.9749 | 66.6004 | -123.5487
2913.7969 | 123.317 | -66.7374 | 56.3416 | -0.010607 | -0.034923 | -0.00082046 | 0.053081 | -0.0084418 | 0.062289 | 0.015414 | -0.0039075 | -0.00034193 | 0.054826 | 0.04419 | 0.055531 | -66.7335 | -0.10848 | -66.7826 | 56.3342 | 56.2937 | 56.5 | -66.9016 | -66.7657 | -0.10953 | -66.7956 | 56.2489 | 56.4312 | 56.265 | -67.1889 | -0.16425 | -0.007303 | 0.003832 | -0.045265 | 0.11899 | -0.047896 | 0.15843 | -0.45151 | -0.092645 | -0.028333 | -0.05826 | 0.39325 | 0.089694 | -0.076513 | 123.0716 | 123.031 | 123.2373 | 66.6289 | -123.2432 | 122.9863 | 123.1686 | 123.0024 | 66.6278 | -123.5304
2914.7969 | 123.3124 | -66.7053 | 56.3461 | -0.0029761 | -0.035136 | -0.00082046 | 0.052867 | -0.0084418 | 0.062503 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054826 | 0.043976 | 0.055744 | -66.7381 | -0.1039 | -66.7826 | 56.3388 | 56.2753 | 56.4908 | -66.9154 | -66.7657 | -0.10495 | -66.7956 | 56.2535 | 56.4312 | 56.2376 | -67.1797 | -0.21003 | -0.007302 | -0.03279 | -0.077309 | 0.13273 | -0.070788 | 0.1447 | -0.4744 | -0.092643 | -0.060377 | -0.090304 | 0.38409 | 0.085117 | -0.10856 | 123.0442 | 122.9807 | 123.1961 | 66.6014 | -123.2615 | 122.9588 | 123.1366 | 122.9429 | 66.6004 | -123.5258
2915.7969 | 123.2803 | -66.7053 | 56.3461 | 0.0046549 | -0.03535 | -0.0010343 | 0.053295 | -0.0088692 | 0.062717 | 0.015414 | -0.0041211 | -0.00034193 | 0.054399 | 0.043976 | 0.055103 | -66.7335 | -0.1039 | -66.7781 | 56.3388 | 56.2891 | 56.4954 | -66.9062 | -66.7611 | -0.10953 | -66.7956 | 56.2581 | 56.4358 | 56.2238 | -67.1843 | -0.20088 | -0.007302 | -0.028212 | -0.072731 | 0.12815 | -0.057052 | 0.14928 | -0.47897 | -0.088065 | -0.055799 | -0.090304 | 0.38867 | 0.089695 | -0.1223 | 123.0442 | 122.9944 | 123.2007 | 66.6014 | -123.2523 | 122.9634 | 123.1411 | 122.9292 | 66.5958 | -123.5304
2916.7969 | 123.2803 | -66.7099 | 56.3782 | 0.0046549 | -0.035136 | -0.0012479 | 0.053081 | -0.0086556 | 0.062717 | 0.00015261 | -0.0041211 | -0.00076913 | 0.05504 | 0.043976 | 0.055744 | -66.7381 | -0.099323 | -66.8009 | 56.3342 | 56.2845 | 56.4954 | -66.9154 | -66.7657 | -0.10953 | -66.791 | 56.2535 | 56.4358 | 56.2559 | -67.1889 | -0.20546 | -0.043924 | -0.028212 | -0.091044 | 0.11441 | -0.093675 | 0.11723 | -0.47897 | -0.12469 | -0.055799 | -0.081147 | 0.39783 | 0.057651 | -0.12229 | 123.0442 | 122.9944 | 123.2053 | 66.6106 | -123.2935 | 122.9634 | 123.1457 | 122.9658 | 66.6004 | -123.567
2917.7969 | 123.3353 | -66.7282 | 56.3416 | 0.0046549 | -0.035136 | -0.0012479 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054613 | 0.043976 | 0.055317 | -66.7335 | -0.1039 | -66.7964 | 56.3342 | 56.2662 | 56.4908 | -66.9108 | -66.7611 | -0.11411 | -66.791 | 56.2489 | 56.4404 | 56.2605 | -67.1889 | -0.18257 | -0.007303 | -0.005324 | -0.068156 | 0.11441 | -0.075369 | 0.14927 | -0.46066 | -0.092645 | -0.032911 | -0.062837 | 0.39783 | 0.098851 | -0.081092 | 123.0625 | 122.9944 | 123.219 | 66.6243 | -123.2523 | 122.9771 | 123.1686 | 122.9887 | 66.6141 | -123.5304
2918.7969 | 123.2529 | -66.7007 | 56.3782 | -0.0029761 | -0.034923 | -0.0010343 | 0.052654 | -0.0084418 | 0.062076 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.044403 | 0.055744 | -66.7427 | -0.1039 | -66.7918 | 56.3342 | 56.2708 | 56.4908 | -66.9062 | -66.7657 | -0.10495 | -66.7956 | 56.2489 | 56.4312 | 56.2421 | -67.1797 | -0.20545 | -0.043924 | -0.041946 | -0.091043 | 0.11441 | -0.10741 | 0.11265 | -0.47897 | -0.12927 | -0.064954 | -0.094881 | 0.38409 | 0.053073 | -0.13603 | 123.035 | 122.9715 | 123.1916 | 66.5968 | -123.2844 | 122.9497 | 123.132 | 122.9429 | 66.5958 | -123.5579
2919.7969 | 123.3582 | -66.687 | 56.3324 | 0.0046549 | -0.035136 | -0.0012479 | 0.053295 | -0.0082282 | 0.062503 | 0.0077831 | -0.0036937 | -0.00055553 | 0.055254 | 0.043762 | 0.055317 | -66.7335 | -0.10848 | -66.7964 | 56.3342 | 56.2891 | 56.4954 | -66.9016 | -66.7657 | -0.10495 | -66.8002 | 56.2535 | 56.4358 | 56.2421 | -67.1889 | -0.21461 | 0.001853 | -0.046522 | -0.10935 | 0.10525 | -0.043319 | 0.16301 | -0.50186 | -0.07891 | -0.078687 | -0.11319 | 0.38867 | 0.10343 | -0.09025 | 123.0213 | 122.9761 | 123.1824 | 66.5785 | -123.234 | 122.9405 | 123.1228 | 122.9292 | 66.5821 | -123.5213
2920.7969 | 123.1888 | -66.7603 | 56.3782 | 0.012286 | -0.035136 | -0.00082046 | 0.052867 | -0.0086556 | 0.062289 | 0.00015261 | -0.0039075 | -0.00012813 | 0.055254 | 0.043762 | 0.055531 | -66.7335 | -0.10848 | -66.7918 | 56.3388 | 56.2753 | 56.4954 | -66.9062 | -66.7657 | -0.10953 | -66.791 | 56.2535 | 56.4312 | 56.2421 | -67.1935 | -0.14594 | -0.039346 | 0.02672 | -0.031534 | 0.11441 | -0.10283 | 0.11723 | -0.4332 | -0.12469 | -0.005445 | -0.030793 | 0.40241 | 0.053073 | -0.13603 | 123.0991 | 123.0356 | 123.2557 | 66.6518 | -123.2844 | 123.0137 | 123.1915 | 123.0024 | 66.6507 | -123.5716
2921.7969 | 123.3444 | -66.7191 | 56.3553 | 0.0046549 | -0.034923 | -0.0010343 | 0.053081 | -0.0084418 | 0.062503 | 0.00015261 | -0.0036937 | -0.00076913 | 0.05504 | 0.043976 | 0.055317 | -66.7427 | -0.10848 | -66.7918 | 56.3251 | 56.2708 | 56.4908 | -66.9062 | -66.7611 | -0.11411 | -66.8002 | 56.2581 | 56.445 | 56.2513 | -67.1935 | -0.18714 | -0.030193 | -0.023636 | -0.072733 | 0.11441 | -0.084523 | 0.13554 | -0.4744 | -0.097221 | -0.042066 | -0.08115 | 0.39325 | 0.089697 | -0.10398 | 123.0441 | 122.9898 | 123.2099 | 66.6106 | -123.2615 | 122.9771 | 123.164 | 122.9704 | 66.6049 | -123.5487
2922.7969 | 123.2208 | -66.7191 | 56.3828 | -0.0029761 | -0.034709 | -0.0010343 | 0.052867 | -0.0084418 | 0.062503 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054826 | 0.043976 | 0.055531 | -66.7381 | -0.1039 | -66.7964 | 56.3297 | 56.2616 | 56.4954 | -66.9108 | -66.7657 | -0.10953 | -66.7865 | 56.2535 | 56.4358 | 56.2421 | -67.1889 | -0.19172 | -0.05308 | -0.019057 | -0.077311 | 0.11441 | -0.12115 | 0.11266 | -0.46982 | -0.12926 | -0.046644 | -0.067414 | 0.40241 | 0.053074 | -0.1406 | 123.0487 | 122.9807 | 123.2145 | 66.6152 | -123.2935 | 122.9725 | 123.1549 | 122.9612 | 66.6095 | -123.5716
2923.7969 | 123.2758 | -66.6916 | 56.3644 | -0.0029761 | -0.035136 | -0.0012479 | 0.052867 | -0.0082282 | 0.062503 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.043549 | 0.055317 | -66.7381 | -0.1039 | -66.7964 | 56.3297 | 56.2708 | 56.4908 | -66.9062 | -66.7657 | -0.10953 | -66.791 | 56.2535 | 56.4404 | 56.2376 | -67.1797 | -0.21461 | -0.03477 | -0.046523 | -0.10478 | 0.10983 | -0.093678 | 0.12639 | -0.48813 | -0.11095 | -0.07411 | -0.099458 | 0.38867 | 0.075963 | -0.12687 | 123.0213 | 122.9624 | 123.1824 | 66.5877 | -123.2706 | 122.9451 | 123.132 | 122.9292 | 66.5821 | -123.5442
2924.7969 | 123.1934 | -66.7419 | 56.3644 | 0.012286 | -0.03535 | -0.0012479 | 0.053081 | -0.0084418 | 0.062289 | 0.00015261 | -0.0043347 | -0.00055553 | 0.055467 | 0.04419 | 0.055744 | -66.7381 | -0.1039 | -66.7964 | 56.3388 | 56.2708 | 56.4954 | -66.9062 | -66.7611 | -0.10495 | -66.7956 | 56.2581 | 56.4358 | 56.2467 | -67.1797 | -0.16425 | -0.025613 | 0.003831 | -0.054423 | 0.10983 | -0.093678 | 0.13097 | -0.43777 | -0.10638 | -0.019178 | -0.053683 | 0.38409 | 0.071384 | -0.11772 | 123.0808 | 123.0127 | 123.2373 | 66.638 | -123.2706 | 123 | 123.1778 | 122.9887 | 66.637 | -123.5442
2925.7969 | 123.2849 | -66.7145 | 56.3828 | -0.0029761 | -0.03535 | -0.0010343 | 0.052867 | -0.0086556 | 0.062289 | 0.0077831 | -0.0041211 | -0.00098273 | 0.05504 | 0.044403 | 0.055317 | -66.7335 | -0.1039 | -66.7964 | 56.3297 | 56.2799 | 56.4954 | -66.9108 | -66.7611 | -0.10495 | -66.8048 | 56.2489 | 56.4312 | 56.2559 | -67.1843 | -0.1963 | -0.05308 | -0.019056 | -0.081888 | 0.11441 | -0.10283 | 0.11266 | -0.46982 | -0.13384 | -0.046643 | -0.090305 | 0.37951 | 0.048496 | -0.12687 | 123.0441 | 122.9944 | 123.2099 | 66.6106 | -123.2935 | 122.9634 | 123.1457 | 122.9704 | 66.6095 | -123.567
2926.7969 | 123.1796 | -66.7145 | 56.3553 | -0.010607 | -0.035136 | -0.00082046 | 0.052867 | -0.0084418 | 0.062717 | -0.0074779 | -0.0036937 | -0.00076913 | 0.054826 | 0.04419 | 0.055317 | -66.7381 | -0.094744 | -66.8009 | 56.3388 | 56.2753 | 56.4908 | -66.9108 | -66.7611 | -0.10953 | -66.791 | 56.2398 | 56.4312 | 56.2284 | -67.1843 | -0.1963 | -0.016458 | -0.023634 | -0.086466 | 0.10983 | -0.079944 | 0.13554 | -0.46982 | -0.11554 | -0.046643 | -0.076569 | 0.39325 | 0.075961 | -0.12687 | 123.0533 | 122.9898 | 123.2053 | 66.6197 | -123.2661 | 122.9542 | 123.1457 | 122.9429 | 66.6049 | -123.5396
2927.7969 | 123.2117 | -66.7282 | 56.3644 | 0.0046549 | -0.034923 | -0.0012479 | 0.053081 | -0.0086556 | 0.062289 | -0.0074779 | -0.0043347 | -0.00055553 | 0.05504 | 0.043976 | 0.055531 | -66.7381 | -0.094744 | -66.7964 | 56.3297 | 56.2799 | 56.4954 | -66.9108 | -66.7657 | -0.10953 | -66.791 | 56.2581 | 56.4358 | 56.2284 | -67.1797 | -0.18257 | -0.03477 | -0.009902 | -0.068156 | 0.11441 | -0.08452 | 0.13097 | -0.45151 | -0.10638 | -0.037489 | -0.062837 | 0.38867 | 0.071384 | -0.13603 | 123.0579 | 123.0081 | 123.2236 | 66.6335 | -123.2752 | 122.9863 | 123.164 | 122.9566 | 66.6187 | -123.5442
2928.7969 | 123.2254 | -66.7557 | 56.3782 | -0.0029761 | -0.035136 | -0.0010343 | 0.053081 | -0.0084418 | 0.062503 | 0.015414 | -0.0043347 | -0.00076913 | 0.05504 | 0.043976 | 0.055531 | -66.7335 | -0.1039 | -66.7964 | 56.3297 | 56.2662 | 56.4954 | -66.9062 | -66.7657 | -0.10953 | -66.791 | 56.2581 | 56.4267 | 56.233 | -67.1889 | -0.15052 | -0.048503 | 0.022142 | -0.04069 | 0.10983 | -0.11199 | 0.11723 | -0.4332 | -0.12011 | -0.010023 | -0.035371 | 0.39783 | 0.048494 | -0.14518 | 123.0853 | 123.0219 | 123.2511 | 66.6518 | -123.2844 | 123.0137 | 123.1823 | 122.9887 | 66.6461 | -123.567
2929.7969 | 123.1934 | -66.7831 | 56.3599 | -0.0029761 | -0.034923 | -0.0010343 | 0.053081 | -0.0086556 | 0.062717 | 0.00015261 | -0.0039075 | -0.00055553 | 0.055254 | 0.043976 | 0.055317 | -66.7335 | -0.10848 | -66.7872 | 56.3251 | 56.2845 | 56.4954 | -66.9108 | -66.7657 | -0.10495 | -66.791 | 56.2581 | 56.4267 | 56.233 | -67.1843 | -0.12763 | -0.03477 | 0.049608 | -0.004067 | 0.12357 | -0.075364 | 0.13554 | -0.40115 | -0.1018 | 0.017443 | -0.007905 | 0.39325 | 0.066805 | -0.12687 | 123.1082 | 123.0676 | 123.2785 | 66.6747 | -123.2706 | 123.0412 | 123.2098 | 123.0161 | 66.6782 | -123.5442
2930.7969 | 123.2346 | -66.7374 | 56.3507 | -0.0029761 | -0.03535 | -0.0012479 | 0.053295 | -0.0086556 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.043976 | 0.055531 | -66.729 | -0.099323 | -66.7918 | 56.3342 | 56.2753 | 56.5 | -66.9108 | -66.7657 | -0.10495 | -66.8002 | 56.2489 | 56.4404 | 56.2238 | -67.1843 | -0.17341 | -0.016458 | 0.00841 | -0.054422 | 0.11899 | -0.075366 | 0.14928 | -0.44693 | -0.1018 | -0.028333 | -0.062839 | 0.38409 | 0.089696 | -0.12688 | 123.0716 | 123.0127 | 123.2373 | 66.638 | -123.2615 | 122.9863 | 123.1778 | 122.9612 | 66.6324 | -123.535
2931.7969 | 123.1934 | -66.7328 | 56.3828 | -0.0029761 | -0.035136 | -0.0012479 | 0.053081 | -0.0086556 | 0.062289 | -0.0074779 | -0.0041211 | -0.00076913 | 0.05504 | 0.04419 | 0.055103 | -66.7427 | -0.1039 | -66.7918 | 56.3342 | 56.2845 | 56.4954 | -66.9062 | -66.7611 | -0.10495 | -66.7865 | 56.2535 | 56.4312 | 56.2467 | -67.1889 | -0.17341 | -0.048501 | -0.009903 | -0.059 | 0.11441 | -0.098252 | 0.11266 | -0.45609 | -0.12926 | -0.028333 | -0.053681 | 0.40241 | 0.048496 | -0.13603 | 123.067 | 123.0173 | 123.2282 | 66.6289 | -123.2889 | 122.9863 | 123.164 | 122.9795 | 66.6278 | -123.5716
2932.7969 | 123.2391 | -66.7557 | 56.3324 | 0.0046549 | -0.035564 | -0.0014615 | 0.053081 | -0.0088692 | 0.062503 | 0.00015261 | -0.0039075 | -0.00055553 | 0.054826 | 0.04419 | 0.055531 | -66.7381 | -0.1039 | -66.7826 | 56.3342 | 56.2662 | 56.5 | -66.9062 | -66.7657 | -0.10495 | -66.791 | 56.2626 | 56.4358 | 56.233 | -67.1797 | -0.15052 | 0.001853 | 0.017564 | -0.026955 | 0.12357 | -0.066213 | 0.16759 | -0.42404 | -0.069753 | -0.010023 | -0.035371 | 0.38867 | 0.10343 | -0.099407 | 123.0899 | 123.0219 | 123.2557 | 66.6518 | -123.2386 | 123.0183 | 123.1915 | 122.9887 | 66.6507 | -123.5121
2933.7969 | 123.2346 | -66.7511 | 56.3599 | -0.0029761 | -0.03535 | -0.0012479 | 0.053295 | -0.0088692 | 0.062503 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.044403 | 0.055531 | -66.7335 | -0.10848 | -66.7826 | 56.3342 | 56.2753 | 56.5046 | -66.9108 | -66.7703 | -0.10953 | -66.7956 | 56.2535 | 56.4358 | 56.2559 | -67.1843 | -0.15968 | -0.025613 | 0.017565 | -0.031532 | 0.12815 | -0.084521 | 0.1447 | -0.4332 | -0.10638 | -0.019179 | -0.044527 | 0.38867 | 0.075962 | -0.10398 | 123.0853 | 123.0264 | 123.2557 | 66.6426 | -123.2706 | 123.0046 | 123.1869 | 123.007 | 66.6416 | -123.5442
2934.7969 | 123.1934 | -66.7694 | 56.3553 | -0.010607 | -0.03535 | -0.0012479 | 0.052867 | -0.0082282 | 0.062289 | 0.0077831 | -0.0043347 | -0.00055553 | 0.05504 | 0.04419 | 0.05489 | -66.7335 | -0.1039 | -66.7918 | 56.3297 | 56.2845 | 56.5046 | -66.9062 | -66.7611 | -0.10495 | -66.7865 | 56.2535 | 56.4358 | 56.2605 | -67.1889 | -0.13679 | -0.025615 | 0.035875 | -0.022379 | 0.11441 | -0.070787 | 0.14928 | -0.41947 | -0.1018 | 0.008288 | -0.01706 | 0.40241 | 0.080539 | -0.094825 | 123.0991 | 123.0539 | 123.274 | 66.6655 | -123.2615 | 123.0229 | 123.2052 | 123.0299 | 66.6645 | -123.5442
2935.7969 | 123.2346 | -66.7648 | 56.3461 | 0.0046549 | -0.03535 | -0.0010343 | 0.053081 | -0.0086556 | 0.062503 | -0.0074779 | -0.0043347 | -0.00012813 | 0.05504 | 0.04419 | 0.055744 | -66.729 | -0.1039 | -66.7826 | 56.3342 | 56.2799 | 56.5 | -66.9108 | -66.7657 | -0.11869 | -66.7956 | 56.2535 | 56.4312 | 56.2696 | -67.1889 | -0.14594 | -0.01188 | 0.035876 | -0.017799 | 0.12815 | -0.066209 | 0.15385 | -0.42404 | -0.092643 | -0.000867 | -0.030794 | 0.39325 | 0.085117 | -0.076512 | 123.0991 | 123.0448 | 123.2648 | 66.6609 | -123.2569 | 123.0183 | 123.1961 | 123.0344 | 66.6461 | -123.535
2936.7969 | 123.175 | -66.7557 | 56.3324 | -0.0029761 | -0.03535 | -0.0010343 | 0.053081 | -0.0086556 | 0.062289 | -0.015108 | -0.0039075 | -0.00076913 | 0.05504 | 0.043976 | 0.055531 | -66.7381 | -0.1039 | -66.7918 | 56.3342 | 56.2799 | 56.5 | -66.9108 | -66.7657 | -0.10495 | -66.791 | 56.2581 | 56.4312 | 56.2559 | -67.1843 | -0.1551 | 0.001853 | 0.017564 | -0.036112 | 0.11899 | -0.052476 | 0.16759 | -0.42862 | -0.074332 | -0.010023 | -0.035371 | 0.39325 | 0.09885 | -0.076514 | 123.0899 | 123.0356 | 123.2557 | 66.6518 | -123.2432 | 123.0137 | 123.1869 | 123.0116 | 66.6507 | -123.5167
2937.7969 | 123.2391 | -66.7465 | 56.3507 | -0.010607 | -0.035564 | -0.0012479 | 0.053081 | -0.0088692 | 0.062717 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.044403 | 0.055317 | -66.7335 | -0.11306 | -66.7964 | 56.3388 | 56.2708 | 56.4908 | -66.9062 | -66.7565 | -0.10953 | -66.791 | 56.2535 | 56.4404 | 56.2696 | -67.1889 | -0.15968 | -0.01188 | 0.012987 | -0.049845 | 0.10983 | -0.079945 | 0.14012 | -0.44235 | -0.097221 | -0.010021 | -0.044526 | 0.39783 | 0.089696 | -0.08109 | 123.0853 | 123.0173 | 123.2373 | 66.6335 | -123.2569 | 123 | 123.1869 | 123.0161 | 66.637 | -123.5396
2938.7969 | 123.1842 | -66.7786 | 56.3324 | -0.0029761 | -0.03535 | -0.00082046 | 0.052654 | -0.0084418 | 0.06293 | 0.0077831 | -0.0041211 | -0.00098273 | 0.05504 | 0.043976 | 0.055317 | -66.7335 | -0.1039 | -66.7872 | 56.3297 | 56.2708 | 56.4908 | -66.9154 | -66.7703 | -0.10953 | -66.791 | 56.2535 | 56.4312 | 56.233 | -67.1935 | -0.13679 | -0.002726 | 0.04503 | -0.008645 | 0.12815 | -0.061634 | 0.15843 | -0.41489 | -0.07891 | 0.008286 | -0.012483 | 0.40241 | 0.09885 | -0.099407 | 123.1082 | 123.0493 | 123.2694 | 66.6747 | -123.2478 | 123.0321 | 123.2098 | 123.0116 | 66.669 | -123.5259
2939.7969 | 123.1934 | -66.7557 | 56.3461 | -0.010607 | -0.03535 | -0.0012479 | 0.053081 | -0.0086556 | 0.062503 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.044403 | 0.055103 | -66.7381 | -0.10848 | -66.7918 | 56.3342 | 56.2753 | 56.4954 | -66.9154 | -66.7657 | -0.10495 | -66.7956 | 56.2535 | 56.445 | 56.2605 | -67.1889 | -0.15968 | -0.01188 | 0.017564 | -0.036112 | 0.12357 | -0.070788 | 0.14928 | -0.4332 | -0.092643 | -0.010023 | -0.03995 | 0.39325 | 0.098853 | -0.085669 | 123.0899 | 123.031 | 123.2511 | 66.6472 | -123.2615 | 123.0092 | 123.2007 | 123.0161 | 66.6507 | -123.535
2940.7969 | 123.2712 | -66.7374 | 56.3049 | -0.0029761 | -0.035564 | -0.0010343 | 0.053295 | -0.0086556 | 0.062076 | 0.0077831 | -0.0043347 | -0.00055553 | 0.05504 | 0.04419 | 0.055103 | -66.7335 | -0.10848 | -66.7826 | 56.3342 | 56.2616 | 56.4862 | -66.9062 | -66.7657 | -0.10953 | -66.791 | 56.2581 | 56.4404 | 56.2467 | -67.1889 | -0.16883 | 0.029318 | 0.003832 | -0.045265 | 0.12357 | -0.043327 | 0.18132 | -0.45151 | -0.046867 | -0.028333 | -0.053681 | 0.39783 | 0.13547 | -0.058207 | 123.0716 | 122.999 | 123.2236 | 66.6289 | -123.2111 | 122.9954 | 123.1778 | 122.9841 | 66.6278 | -123.4938
2941.7969 | 123.1842 | -66.7923 | 56.3461 | -0.0029761 | -0.035564 | -0.0010343 | 0.053081 | -0.0086556 | 0.062503 | 0.0077831 | -0.0041211 | -0.00034193 | 0.05504 | 0.044403 | 0.055317 | -66.729 | -0.1039 | -66.7918 | 56.3388 | 56.2753 | 56.4954 | -66.9154 | -66.7703 | -0.10953 | -66.7956 | 56.2535 | 56.445 | 56.2559 | -67.1843 | -0.12306 | -0.007302 | 0.063341 | 0.000509 | 0.12357 | -0.070788 | 0.14928 | -0.392 | -0.092643 | 0.022019 | -0.003329 | 0.38867 | 0.098853 | -0.090247 | 123.1311 | 123.0676 | 123.2877 | 66.6884 | -123.2615 | 123.0458 | 123.2373 | 123.0482 | 66.6828 | -123.5304
2942.7969 | 123.2346 | -66.7419 | 56.3232 | -0.0029761 | -0.03535 | -0.0010343 | 0.053295 | -0.0084418 | 0.062289 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.043976 | 0.055531 | -66.7381 | -0.1039 | -66.7826 | 56.3388 | 56.2799 | 56.4954 | -66.9108 | -66.7565 | -0.10953 | -66.791 | 56.2581 | 56.4404 | 56.2605 | -67.1889 | -0.16883 | 0.015586 | 0.003831 | -0.040688 | 0.12815 | -0.043321 | 0.17216 | -0.44693 | -0.065177 | -0.014599 | -0.049104 | 0.39783 | 0.11716 | -0.062781 | 123.0808 | 123.0219 | 123.2373 | 66.638 | -123.234 | 123 | 123.1823 | 123.0024 | 66.6324 | -123.5121
2943.7969 | 123.2025 | -66.7557 | 56.3461 | -0.010607 | -0.03535 | -0.0010343 | 0.053081 | -0.0084418 | 0.062289 | 0.00015261 | -0.0036937 | -0.00034193 | 0.054613 | 0.043976 | 0.055531 | -66.7335 | -0.099323 | -66.7781 | 56.3388 | 56.2799 | 56.4954 | -66.9062 | -66.7657 | -0.10953 | -66.7956 | 56.2535 | 56.4358 | 56.2467 | -67.1843 | -0.15052 | -0.007302 | 0.022142 | -0.022377 | 0.12815 | -0.066209 | 0.14928 | -0.42862 | -0.092643 | -0.010023 | -0.03995 | 0.38867 | 0.089695 | -0.099405 | 123.0945 | 123.0356 | 123.2511 | 66.6564 | -123.2523 | 123.0092 | 123.1915 | 123.0024 | 66.6461 | -123.5304
2944.7969 | 123.2803 | -66.7511 | 56.25 | 0.0046549 | -0.03535 | -0.0012479 | 0.053295 | -0.0086556 | 0.062289 | 0.0077831 | -0.0036937 | -0.00034193 | 0.054826 | 0.043976 | 0.055531 | -66.7381 | -0.1039 | -66.7872 | 56.3342 | 56.3028 | 56.4908 | -66.9062 | -66.7611 | -0.10495 | -66.7956 | 56.2535 | 56.4358 | 56.2696 | -67.1889 | -0.1551 | 0.08425 | 0.012987 | -0.03611 | 0.11899 | 0.052815 | 0.24083 | -0.43778 | 0.003487 | -0.010022 | -0.044527 | 0.39325 | 0.18583 | 0.019618 | 123.0853 | 123.0539 | 123.2419 | 66.6472 | -123.1562 | 123.0046 | 123.1869 | 123.0207 | 66.6461 | -123.4389
2945.7969 | 123.2254 | -66.7786 | 56.3461 | -0.010607 | -0.035564 | -0.0010343 | 0.053508 | -0.0090828 | 0.062289 | -0.0074779 | -0.0039075 | -0.00055553 | 0.05504 | 0.04419 | 0.055103 | -66.7381 | -0.099323 | -66.7826 | 56.3342 | 56.2845 | 56.5 | -66.9108 | -66.7611 | -0.10037 | -66.791 | 56.2489 | 56.445 | 56.2421 | -67.1935 | -0.13221 | -0.01188 | 0.040452 | -0.004067 | 0.12815 | -0.061631 | 0.15385 | -0.41489 | -0.097222 | 0.017443 | -0.012483 | 0.40241 | 0.098853 | -0.10398 | 123.1128 | 123.0631 | 123.2785 | 66.6792 | -123.2569 | 123.0275 | 123.2235 | 123.0207 | 66.6782 | -123.5396
2946.7969 | 123.2986 | -66.7191 | 56.3095 | -0.010607 | -0.035564 | -0.0012479 | 0.052867 | -0.0086556 | 0.062076 | 0.00015261 | -0.0039075 | -0.00034193 | 0.05504 | 0.044403 | 0.055317 | -66.7381 | -0.10848 | -66.7735 | 56.3297 | 56.2708 | 56.4954 | -66.9062 | -66.7657 | -0.10953 | -66.7865 | 56.2581 | 56.4358 | 56.2513 | -67.1889 | -0.18714 | 0.020162 | -0.019057 | -0.054419 | 0.13272 | -0.038746 | 0.1859 | -0.46982 | -0.051444 | -0.046644 | -0.067414 | 0.40241 | 0.12632 | -0.058205 | 123.0487 | 122.9898 | 123.2145 | 66.6106 | -123.2157 | 122.9771 | 123.1549 | 122.9704 | 66.6095 | -123.4984
2947.8594 | 123.262 | -66.7419 | 56.3232 | -0.0029761 | -0.034923 | -0.0010343 | 0.053508 | -0.0086556 | 0.062289 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054399 | 0.04419 | 0.055103 | -66.7335 | -0.10848 | -66.7918 | 56.3297 | 56.2799 | 56.4908 | -66.9108 | -66.7657 | -0.10953 | -66.7956 | 56.2535 | 56.4404 | 56.2559 | -67.1797 | -0.16883 | 0.006429 | 0.008409 | -0.049845 | 0.11899 | -0.043321 | 0.16759 | -0.43777 | -0.069755 | -0.023756 | -0.053683 | 0.38409 | 0.11716 | -0.067359 | 123.0716 | 123.0219 | 123.2328 | 66.6335 | -123.234 | 122.9954 | 123.1823 | 122.9978 | 66.6324 | -123.503
2948.7969 | 123.3124 | -66.7282 | 56.3187 | -0.010607 | -0.03535 | -0.0010343 | 0.053081 | -0.0084418 | 0.062717 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054826 | 0.044403 | 0.055317 | -66.7381 | -0.099323 | -66.7918 | 56.3388 | 56.2616 | 56.4908 | -66.9108 | -66.7611 | -0.11869 | -66.7956 | 56.2581 | 56.4358 | 56.2238 | -67.1843 | -0.18257 | 0.020163 | -0.009902 | -0.063578 | 0.11899 | -0.05706 | 0.17216 | -0.45609 | -0.0606 | -0.032911 | -0.067416 | 0.38867 | 0.11716 | -0.094833 | 123.067 | 122.9898 | 123.219 | 66.6289 | -123.2294 | 122.9863 | 123.164 | 122.952 | 66.6095 | -123.503
2949.7969 | 123.2712 | -66.7786 | 56.3141 | 0.0046549 | -0.035564 | -0.0012479 | 0.052867 | -0.0084418 | 0.062289 | 0.00015261 | -0.0045483 | -0.00034193 | 0.054826 | 0.04419 | 0.055317 | -66.7427 | -0.1039 | -66.7826 | 56.3342 | 56.2799 | 56.5 | -66.9062 | -66.7565 | -0.10953 | -66.7956 | 56.2535 | 56.4404 | 56.2284 | -67.1889 | -0.12763 | 0.020163 | 0.035873 | -0.004067 | 0.12357 | -0.034166 | 0.1859 | -0.41031 | -0.0606 | 0.022022 | -0.017062 | 0.39325 | 0.12632 | -0.085676 | 123.1128 | 123.0585 | 123.2785 | 66.6747 | -123.2203 | 123.0321 | 123.219 | 123.007 | 66.669 | -123.503
2950.7969 | 123.262 | -66.7236 | 56.3507 | -0.0029761 | -0.035136 | -0.0010343 | 0.052867 | -0.0084418 | 0.061862 | 0.00015261 | -0.0039075 | -0.00034193 | 0.054826 | 0.04419 | 0.055317 | -66.7335 | -0.1039 | -66.7918 | 56.3251 | 56.2662 | 56.4954 | -66.9016 | -66.7611 | -0.10953 | -66.8002 | 56.2535 | 56.4358 | 56.2467 | -67.1935 | -0.17799 | -0.025615 | -0.009901 | -0.068155 | 0.10983 | -0.084524 | 0.1447 | -0.46982 | -0.097221 | -0.037488 | -0.076572 | 0.39325 | 0.085117 | -0.10398 | 123.0487 | 122.9898 | 123.219 | 66.6197 | -123.2523 | 122.9771 | 123.1595 | 122.9704 | 66.6141 | -123.5442
2951.7969 | 123.2895 | -66.6962 | 56.3049 | 0.0046549 | -0.035564 | -0.0012479 | 0.052867 | -0.0084418 | 0.062076 | -0.015108 | -0.0041211 | -0.00034193 | 0.05504 | 0.043976 | 0.055317 | -66.729 | -0.1039 | -66.7918 | 56.3388 | 56.2845 | 56.5 | -66.9154 | -66.7657 | -0.10953 | -66.791 | 56.2581 | 56.4358 | 56.2467 | -67.1935 | -0.21919 | 0.033896 | -0.032789 | -0.095621 | 0.12357 | -0.020433 | 0.19505 | -0.49729 | -0.046867 | -0.069532 | -0.09488 | 0.40241 | 0.13089 | -0.058207 | 123.035 | 122.9807 | 123.1962 | 66.5923 | -123.2203 | 122.9542 | 123.132 | 122.9429 | 66.5866 | -123.4984
2952.7969 | 123.2758 | -66.7236 | 56.3599 | -0.010607 | -0.035777 | -0.0010343 | 0.053295 | -0.0084418 | 0.062503 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.044403 | 0.055531 | -66.7335 | -0.099323 | -66.7918 | 56.3342 | 56.2662 | 56.4954 | -66.9062 | -66.7657 | -0.10953 | -66.7956 | 56.2535 | 56.4358 | 56.233 | -67.1889 | -0.18256 | -0.025613 | -0.009901 | -0.068155 | 0.11441 | -0.093679 | 0.13554 | -0.46524 | -0.10638 | -0.042066 | -0.071993 | 0.39325 | 0.075962 | -0.12687 | 123.0579 | 122.9898 | 123.219 | 66.6243 | -123.2661 | 122.9771 | 123.1595 | 122.9566 | 66.6141 | -123.5487
2953.7969 | 123.2986 | -66.7328 | 56.3278 | -0.010607 | -0.035991 | -0.0012479 | 0.053295 | -0.0088692 | 0.06293 | 0.00015261 | -0.0043347 | -0.00076913 | 0.05504 | 0.044403 | 0.055317 | -66.7381 | -0.10848 | -66.7964 | 56.3251 | 56.2891 | 56.4954 | -66.9108 | -66.7565 | -0.10495 | -66.791 | 56.2489 | 56.4404 | 56.2193 | -67.1889 | -0.17799 | -0.002727 | -0.005324 | -0.063578 | 0.11441 | -0.038742 | 0.16759 | -0.45609 | -0.078912 | -0.023754 | -0.058259 | 0.39783 | 0.11258 | -0.10857 | 123.0579 | 123.0219 | 123.2282 | 66.6243 | -123.2386 | 122.9817 | 123.1732 | 122.952 | 66.6278 | -123.5167
2954.7969 | 123.2712 | -66.7282 | 56.369 | -0.0029761 | -0.035777 | -0.0014615 | 0.053508 | -0.0088692 | 0.062076 | 0.00015261 | -0.0039075 | -0.00034193 | 0.05504 | 0.04419 | 0.055317 | -66.7427 | -0.10848 | -66.7918 | 56.3251 | 56.2799 | 56.5046 | -66.9062 | -66.7657 | -0.11411 | -66.7956 | 56.2626 | 56.4404 | 56.2421 | -67.1935 | -0.17799 | -0.043926 | -0.014481 | -0.063578 | 0.11441 | -0.089098 | 0.13554 | -0.46524 | -0.10637 | -0.037489 | -0.067416 | 0.39783 | 0.071385 | -0.12687 | 123.0533 | 123.0081 | 123.2328 | 66.6197 | -123.2752 | 122.9909 | 123.1686 | 122.9704 | 66.6141 | -123.5625
2955.7969 | 123.2941 | -66.7191 | 56.3187 | -0.0029761 | -0.03535 | -0.0012479 | 0.053081 | -0.0086556 | 0.062076 | 0.015414 | -0.0039075 | -0.00076913 | 0.054826 | 0.044617 | 0.055317 | -66.7381 | -0.1039 | -66.7872 | 56.3342 | 56.2799 | 56.5 | -66.9108 | -66.7657 | -0.10495 | -66.791 | 56.2535 | 56.4358 | 56.2238 | -67.1935 | -0.19172 | 0.015585 | -0.019057 | -0.068154 | 0.12357 | -0.038744 | 0.18132 | -0.4744 | -0.065178 | -0.046644 | -0.071992 | 0.40241 | 0.11716 | -0.094833 | 123.0533 | 122.999 | 123.219 | 66.6152 | -123.2294 | 122.9725 | 123.1549 | 122.9429 | 66.6141 | -123.5121
2956.7969 | 123.2254 | -66.7145 | 56.3507 | 0.0046549 | -0.035136 | -0.0014615 | 0.053081 | -0.0086556 | 0.062717 | 0.0077831 | -0.0039075 | -0.00098273 | 0.055254 | 0.04419 | 0.055744 | -66.6832 | -0.10848 | -66.7872 | 56.3434 | 56.2662 | 56.5 | -66.8879 | -66.7657 | -0.10953 | -66.7956 | 56.2489 | 56.4312 | 56.2284 | -67.1843 | -0.1734 | -0.007302 | 0.031306 | -0.072731 | 0.10067 | -0.084524 | 0.14928 | -0.46982 | -0.1018 | -0.051221 | -0.081148 | 0.38867 | 0.080539 | -0.1223 | 123.0579 | 122.9807 | 123.2145 | 66.606 | -123.2386 | 122.9634 | 123.1457 | 122.9429 | 66.6049 | -123.535
2957.7969 | 123.2712 | -66.7191 | 56.2958 | -0.0029761 | -0.035136 | -0.0014615 | 0.053295 | -0.0088692 | 0.062717 | 0.00015261 | -0.0043347 | -0.00098273 | 0.054826 | 0.044403 | 0.055531 | -66.6923 | -0.10848 | -66.7964 | 56.3297 | 56.2708 | 56.4862 | -66.8879 | -66.7749 | -0.10495 | -66.7956 | 56.2535 | 56.4404 | 56.2421 | -67.1889 | -0.16883 | 0.033895 | 0.026727 | -0.077311 | 0.091516 | -0.025013 | 0.19047 | -0.46982 | -0.042289 | -0.055802 | -0.076571 | 0.39325 | 0.14463 | -0.053629 | 123.0487 | 122.9898 | 123.2053 | 66.6106 | -123.1837 | 122.9725 | 123.1595 | 122.9612 | 66.6141 | -123.4847
2958.7969 | 123.3078 | -67.5659 | 55.5267 | 0.0046549 | 0.032384 | -0.0014615 | 0.052867 | -0.0084418 | 0.12981 | 0.0077831 | -0.0041211 | -0.00076913 | 0.05504 | 0.044403 | 0.055531 | 55.3629 | -0.10848 | -67.6296 | 55.4644 | 55.4145 | 55.6255 | -67.7487 | -67.6173 | -0.12327 | -67.6427 | 55.4065 | 55.5842 | 55.3631 | -68.0451 | -0.1828 | -0.062377 | 122.9288 | -0.063695 | 0.11911 | -0.11223 | 0.098738 | -0.4792 | -0.12027 | -0.051422 | -0.076769 | 0.40243 | 0.057472 | -0.16368 | 123.0303 | 122.9804 | 123.1914 | 67.4574 | -123.2755 | 122.9724 | 123.1501 | 122.929 | 67.4427 | -123.5718
2959.7969 | 123.2574 | -67.598 | 55.4672 | -0.010607 | 0.032171 | -0.0014615 | 0.053508 | -0.0086556 | 0.13002 | 0.0077831 | -0.0043347 | -0.00034193 | 0.05504 | 0.044403 | 0.05489 | 55.3904 | -0.11306 | -67.6388 | 55.4689 | 55.4053 | 55.6346 | -67.7487 | -67.6082 | -0.10953 | -67.6427 | 55.3927 | 55.5796 | 55.3722 | -68.0451 | -0.15076 | 0.00171 | 122.9883 | -0.040809 | 0.10995 | -0.061878 | 0.1674 | -0.44715 | -0.074494 | -0.010221 | -0.044726 | 0.40243 | 0.1124 | -0.095012 | 123.0669 | 123.0033 | 123.2326 | 67.4849 | -123.2159 | 122.9907 | 123.1776 | 122.9702 | 67.4884 | -123.5123
2960.7969 | 123.317 | -67.5568 | 55.4947 | -0.0029761 | 0.032598 | -0.0014615 | 0.053081 | -0.0086556 | 0.13002 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.04419 | 0.055531 | 55.395 | -0.11764 | -67.6296 | 55.4644 | 55.4053 | 55.6255 | -67.7533 | -67.6265 | -0.11869 | -67.6381 | 55.3927 | 55.575 | 55.3905 | -68.0451 | -0.19654 | -0.030334 | 122.9517 | -0.07285 | 0.12369 | -0.089344 | 0.13078 | -0.48835 | -0.10196 | -0.069734 | -0.081346 | 0.407 | 0.080358 | -0.10416 | 123.0211 | 122.9621 | 123.1822 | 67.4391 | -123.248 | 122.9495 | 123.1318 | 122.9473 | 67.4381 | -123.5398
2961.8594 | 123.2712 | -67.6025 | 55.4764 | -0.0029761 | 0.031957 | -0.0012479 | 0.053508 | -0.0082282 | 0.13002 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.04419 | 0.055317 | 55.4133 | -0.10848 | -67.6342 | 55.4689 | 55.4099 | 55.6209 | -67.7487 | -67.6036 | -0.11869 | -67.6381 | 55.3927 | 55.5842 | 55.3951 | -68.0405 | -0.14618 | -0.007445 | 123.0158 | -0.031652 | 0.11453 | -0.066454 | 0.14451 | -0.438 | -0.083649 | -0.001064 | -0.03557 | 0.40243 | 0.10783 | -0.081274 | 123.0715 | 123.0125 | 123.2234 | 67.4941 | -123.2251 | 122.9953 | 123.1867 | 122.9976 | 67.4839 | -123.5169
2962.7969 | 123.2986 | -67.5522 | 55.4672 | 0.012286 | 0.032171 | -0.0012479 | 0.053081 | -0.0082282 | 0.13002 | -0.015108 | -0.0041211 | -0.00055553 | 0.054826 | 0.044403 | 0.055531 | 55.3858 | -0.10848 | -67.6342 | 55.4644 | 55.4053 | 55.63 | -67.7533 | -67.6128 | -0.11411 | -67.6381 | 55.3927 | 55.5705 | 55.3951 | -68.0405 | -0.20111 | -0.002868 | 122.938 | -0.082006 | 0.11911 | -0.061878 | 0.16283 | -0.48835 | -0.074494 | -0.060576 | -0.085924 | 0.40243 | 0.10325 | -0.072119 | 123.0165 | 122.9575 | 123.1822 | 67.4437 | -123.2205 | 122.9449 | 123.1227 | 122.9473 | 67.4381 | -123.5078
2963.7969 | 123.2574 | -67.5522 | 55.4764 | -0.0029761 | 0.031743 | -0.0010343 | 0.052867 | -0.0086556 | 0.12981 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.044617 | 0.055103 | 55.4179 | -0.10848 | -67.6296 | 55.4598 | 55.4053 | 55.6346 | -67.7487 | -67.6128 | -0.11869 | -67.6473 | 55.3882 | 55.575 | 55.3768 | -68.036 | -0.19654 | -0.016601 | 122.97 | -0.077428 | 0.11911 | -0.071033 | 0.15825 | -0.48377 | -0.088228 | -0.060576 | -0.095081 | 0.38869 | 0.098669 | -0.099588 | 123.012 | 122.9575 | 123.1868 | 67.4437 | -123.2251 | 122.9403 | 123.1272 | 122.929 | 67.4335 | -123.5123
2964.7969 | 123.2986 | -67.5568 | 55.5038 | 0.0046549 | 0.031743 | -0.0014615 | 0.053081 | -0.0088692 | 0.12938 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.044403 | 0.055317 | 55.4179 | -0.11306 | -67.6342 | 55.4735 | 55.3962 | 55.63 | -67.7487 | -67.6128 | -0.12327 | -67.6427 | 55.3973 | 55.5842 | 55.3722 | -68.0451 | -0.19196 | -0.030332 | 122.9746 | -0.077428 | 0.11453 | -0.10766 | 0.1262 | -0.48835 | -0.10654 | -0.055998 | -0.085924 | 0.40243 | 0.08036 | -0.13163 | 123.0303 | 122.953 | 123.1868 | 67.4437 | -123.2526 | 122.9541 | 123.141 | 122.929 | 67.4335 | -123.549
2965.7969 | 123.3215 | -67.543 | 55.4764 | 0.0046549 | 0.031957 | -0.0010343 | 0.052867 | -0.0084418 | 0.12981 | 0.00015261 | -0.0036937 | -0.00055553 | 0.05504 | 0.04419 | 0.055317 | 55.4133 | -0.11764 | -67.625 | 55.4644 | 55.4099 | 55.63 | -67.7487 | -67.6082 | -0.11411 | -67.6335 | 55.3882 | 55.5796 | 55.3676 | -68.0405 | -0.20569 | -0.012023 | 122.9563 | -0.082005 | 0.12369 | -0.066454 | 0.15367 | -0.49751 | -0.088228 | -0.065152 | -0.0905 | 0.40701 | 0.10325 | -0.10874 | 123.0074 | 122.953 | 123.1731 | 67.4254 | -123.2251 | 122.9312 | 123.1227 | 122.9107 | 67.4289 | -123.5169
2966.7969 | 123.2666 | -67.5613 | 55.4855 | 0.0046549 | 0.031743 | -0.0014615 | 0.053081 | -0.0086556 | 0.12981 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.04419 | 0.055317 | 55.4224 | -0.11306 | -67.625 | 55.4598 | 55.4145 | 55.6209 | -67.7487 | -67.6082 | -0.11411 | -67.6335 | 55.3836 | 55.5705 | 55.3722 | -68.036 | -0.18738 | -0.025757 | 122.9838 | -0.063695 | 0.12369 | -0.071031 | 0.13536 | -0.47462 | -0.10196 | -0.046842 | -0.07219 | 0.40243 | 0.084934 | -0.11332 | 123.0211 | 122.9758 | 123.1822 | 67.4483 | -123.2343 | 122.9449 | 123.1318 | 122.9336 | 67.4472 | -123.5215
2967.7969 | 123.2849 | -67.5568 | 55.4581 | -0.0029761 | 0.031316 | -0.0018889 | 0.053081 | -0.0088692 | 0.12959 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054826 | 0.044403 | 0.055317 | 55.4316 | -0.11306 | -67.6433 | 55.4552 | 55.4099 | 55.63 | -67.7441 | -67.6082 | -0.11869 | -67.6335 | 55.3882 | 55.5705 | 55.3859 | -68.0405 | -0.18738 | -0.00287 | 122.9884 | -0.086585 | 0.10079 | -0.048144 | 0.17198 | -0.48377 | -0.069918 | -0.051419 | -0.076767 | 0.40701 | 0.1124 | -0.072121 | 123.012 | 122.9667 | 123.1868 | 67.4437 | -123.2022 | 122.9449 | 123.1272 | 122.9427 | 67.4381 | -123.4986
2968.7969 | 123.1888 | -67.5842 | 55.5222 | -0.010607 | 0.031957 | -0.0014615 | 0.053295 | -0.0084418 | 0.12959 | 0.015414 | -0.0041211 | -0.00055553 | 0.054613 | 0.044403 | 0.055317 | 55.4316 | -0.11306 | -67.6388 | 55.4552 | 55.4053 | 55.6255 | -67.7487 | -67.6082 | -0.11411 | -67.629 | 55.3927 | 55.575 | 55.3768 | -68.0405 | -0.16449 | -0.066957 | 123.0158 | -0.054541 | 0.10995 | -0.11681 | 0.10331 | -0.45631 | -0.12943 | -0.023953 | -0.044722 | 0.41158 | 0.052892 | -0.14537 | 123.0394 | 122.9896 | 123.2097 | 67.4712 | -123.2709 | 122.977 | 123.1593 | 122.961 | 67.4701 | -123.5627
2969.7969 | 123.317 | -67.5476 | 55.4718 | 0.0046549 | 0.031957 | -0.0012479 | 0.053081 | -0.0086556 | 0.12959 | 0.00015261 | -0.0041211 | -0.00034193 | 0.05504 | 0.044831 | 0.055531 | 55.427 | -0.10848 | -67.6342 | 55.4689 | 55.4145 | 55.63 | -67.7396 | -67.6082 | -0.11411 | -67.6381 | 55.3927 | 55.575 | 55.3676 | -68.0405 | -0.19196 | -0.002868 | 122.9746 | -0.086584 | 0.10537 | -0.057298 | 0.15825 | -0.49293 | -0.079072 | -0.060575 | -0.090502 | 0.40243 | 0.10325 | -0.10417 | 123.0165 | 122.9621 | 123.1777 | 67.4391 | -123.2114 | 122.9403 | 123.1227 | 122.9152 | 67.4335 | -123.5123
2970.7969 | 123.1705 | -67.5568 | 55.513 | -0.0029761 | 0.031957 | -0.0014615 | 0.053081 | -0.0084418 | 0.12959 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.044617 | 0.055103 | 55.4362 | -0.11306 | -67.6342 | 55.4552 | 55.4008 | 55.6255 | -67.7441 | -67.6082 | -0.10495 | -67.6381 | 55.3882 | 55.575 | 55.3768 | -68.036 | -0.18738 | -0.057801 | 122.9929 | -0.077428 | 0.10995 | -0.11223 | 0.11247 | -0.47919 | -0.12485 | -0.051419 | -0.081346 | 0.39785 | 0.062048 | -0.13621 | 123.012 | 122.9575 | 123.1822 | 67.4437 | -123.2571 | 122.9449 | 123.1318 | 122.9336 | 67.4518 | -123.549
2971.7969 | 123.2437 | -67.5522 | 55.4993 | -0.010607 | 0.031743 | -0.0012479 | 0.053081 | -0.0088692 | 0.12981 | -0.0074779 | -0.0036937 | -0.00055553 | 0.05504 | 0.044403 | 0.055103 | 55.4362 | -0.11764 | -67.625 | 55.4598 | 55.387 | 55.63 | -67.7396 | -67.599 | -0.11411 | -67.6335 | 55.3882 | 55.5705 | 55.3722 | -68.0314 | -0.18738 | -0.03949 | 122.9884 | -0.07285 | 0.11453 | -0.11224 | 0.13078 | -0.47919 | -0.11112 | -0.04684 | -0.081345 | 0.39785 | 0.071201 | -0.12706 | 123.012 | 122.9392 | 123.1822 | 67.4345 | -123.2388 | 122.9403 | 123.1227 | 122.9244 | 67.4381 | -123.5306
2972.7969 | 123.1796 | -67.6025 | 55.5038 | -0.0029761 | 0.03153 | -0.0016753 | 0.052867 | -0.0088692 | 0.12959 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054826 | 0.044831 | 0.055103 | 55.4453 | -0.11764 | -67.6296 | 55.4598 | 55.4008 | 55.6255 | -67.7441 | -67.5944 | -0.11411 | -67.629 | 55.3882 | 55.5705 | 55.3859 | -68.036 | -0.1416 | -0.044067 | 123.0479 | -0.027074 | 0.11453 | -0.10308 | 0.12163 | -0.43342 | -0.11569 | 0.008093 | -0.026412 | 0.407 | 0.066624 | -0.1179 | 123.0623 | 123.0033 | 123.228 | 67.4849 | -123.248 | 122.9907 | 123.173 | 122.9885 | 67.4884 | -123.5398
2973.7969 | 123.2208 | -67.5613 | 55.5038 | 0.0046549 | 0.03153 | -0.0016753 | 0.052867 | -0.0086556 | 0.12938 | -0.0074779 | -0.0041211 | -0.00055553 | 0.05504 | 0.044831 | 0.055744 | 55.4362 | -0.11764 | -67.625 | 55.4598 | 55.4008 | 55.6255 | -67.7441 | -67.599 | -0.11869 | -67.6244 | 55.3836 | 55.5705 | 55.3539 | -68.0451 | -0.1828 | -0.044067 | 122.9975 | -0.063695 | 0.11911 | -0.10308 | 0.12163 | -0.48377 | -0.12027 | -0.037685 | -0.063032 | 0.42074 | 0.066624 | -0.14995 | 123.0211 | 122.9621 | 123.1868 | 67.4437 | -123.248 | 122.9449 | 123.1318 | 122.9152 | 67.4427 | -123.549
2974.7969 | 123.2071 | -67.5934 | 55.4855 | -0.010607 | 0.03153 | -0.0014615 | 0.052654 | -0.0088692 | 0.12938 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.044403 | 0.055317 | 55.4453 | -0.11764 | -67.6388 | 55.4644 | 55.3916 | 55.63 | -67.7304 | -67.599 | -0.10953 | -67.6244 | 55.3882 | 55.5659 | 55.3722 | -68.0405 | -0.13702 | -0.021179 | 123.0387 | -0.045386 | 0.091634 | -0.093926 | 0.14451 | -0.44715 | -0.097384 | -0.005641 | -0.030988 | 0.41616 | 0.080356 | -0.11332 | 123.0577 | 122.985 | 123.2234 | 67.4757 | -123.2159 | 122.9815 | 123.1593 | 122.9656 | 67.4839 | -123.5261
2975.7969 | 123.23 | -67.5751 | 55.4993 | -0.0029761 | 0.031316 | -0.0014615 | 0.052867 | -0.0084418 | 0.12895 | 0.0077831 | -0.0039075 | -0.00076913 | 0.054613 | 0.044617 | 0.055317 | 55.4407 | -0.11306 | -67.6296 | 55.4552 | 55.3962 | 55.6209 | -67.7441 | -67.599 | -0.11411 | -67.6335 | 55.379 | 55.575 | 55.3859 | -68.0314 | -0.16907 | -0.044069 | 123.0158 | -0.05454 | 0.11453 | -0.10308 | 0.12163 | -0.4563 | -0.12027 | -0.023952 | -0.058457 | 0.39785 | 0.07578 | -0.11332 | 123.0303 | 122.9713 | 123.196 | 67.462 | -123.2434 | 122.9541 | 123.1501 | 122.961 | 67.461 | -123.5306
2976.7969 | 123.2117 | -67.5934 | 55.4947 | -0.0029761 | 0.031102 | -0.0014615 | 0.052654 | -0.0082282 | 0.12959 | 0.00015261 | -0.0045483 | -0.00098273 | 0.05504 | 0.044403 | 0.05489 | 55.4453 | -0.10848 | -67.625 | 55.4644 | 55.4008 | 55.6209 | -67.7533 | -67.6036 | -0.11869 | -67.629 | 55.3882 | 55.5659 | 55.3814 | -68.0314 | -0.15991 | -0.030334 | 123.0387 | -0.031651 | 0.12826 | -0.093923 | 0.1262 | -0.43799 | -0.10654 | -0.010219 | -0.035567 | 0.40243 | 0.071201 | -0.11332 | 123.0577 | 122.9942 | 123.2143 | 67.4849 | -123.248 | 122.9815 | 123.1593 | 122.9748 | 67.4747 | -123.5261
2977.8594 | 123.2391 | -67.5705 | 55.4672 | 0.012286 | 0.031316 | -0.0010343 | 0.053508 | -0.0084418 | 0.12917 | 0.00015261 | -0.0039075 | -0.00034193 | 0.054613 | 0.044617 | 0.055317 | 55.4407 | -0.11764 | -67.6296 | 55.4552 | 55.4008 | 55.6255 | -67.7441 | -67.599 | -0.11869 | -67.6244 | 55.3927 | 55.575 | 55.3722 | -68.036 | -0.17364 | -0.012025 | 123.0112 | -0.059117 | 0.11453 | -0.066457 | 0.15825 | -0.46546 | -0.074494 | -0.028529 | -0.053876 | 0.41158 | 0.10782 | -0.095012 | 123.0257 | 122.9713 | 123.196 | 67.4529 | -123.2114 | 122.9632 | 123.1455 | 122.9427 | 67.4518 | -123.5032
2978.7969 | 123.2117 | -67.5797 | 55.4855 | 0.012286 | 0.031316 | -0.0012479 | 0.052654 | -0.0084418 | 0.12938 | 0.0077831 | -0.0043347 | -0.00098273 | 0.054613 | 0.044617 | 0.055317 | 55.4407 | -0.11764 | -67.6342 | 55.4598 | 55.4053 | 55.6209 | -67.7396 | -67.5944 | -0.11869 | -67.6244 | 55.3882 | 55.5705 | 55.3539 | -68.0314 | -0.15991 | -0.025757 | 123.0204 | -0.05454 | 0.10537 | -0.080189 | 0.13536 | -0.45173 | -0.097384 | -0.014795 | -0.044721 | 0.40701 | 0.084934 | -0.13164 | 123.0394 | 122.985 | 123.2005 | 67.462 | -123.2251 | 122.9678 | 123.1501 | 122.9335 | 67.461 | -123.5169
2979.7969 | 123.1842 | -67.5797 | 55.5084 | -0.0029761 | 0.031316 | -0.0012479 | 0.052654 | -0.0084418 | 0.12895 | -0.0074779 | -0.0043347 | -0.00034193 | 0.055467 | 0.044403 | 0.055317 | 55.4407 | -0.11764 | -67.6113 | 55.4689 | 55.4008 | 55.6255 | -67.7441 | -67.6036 | -0.11411 | -67.6244 | 55.3836 | 55.5705 | 55.3814 | -68.0314 | -0.16449 | -0.039489 | 123.0204 | -0.031649 | 0.13284 | -0.10766 | 0.11705 | -0.45173 | -0.12485 | -0.023952 | -0.044721 | 0.40701 | 0.062046 | -0.12705 | 123.0486 | 122.9804 | 123.2051 | 67.462 | -123.2526 | 122.9632 | 123.1501 | 122.961 | 67.4655 | -123.5398
2980.7969 | 123.2346 | -67.5842 | 55.481 | -0.0029761 | 0.031316 | -0.0014615 | 0.052867 | -0.0086556 | 0.12895 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054613 | 0.044403 | 0.055317 | 55.4453 | -0.11306 | -67.6113 | 55.4598 | 55.4008 | 55.6209 | -67.7396 | -67.6036 | -0.11869 | -67.6244 | 55.3927 | 55.575 | 55.3814 | -68.0314 | -0.15533 | -0.021179 | 123.0296 | -0.027071 | 0.12826 | -0.08019 | 0.13994 | -0.44715 | -0.088227 | -0.019374 | -0.040143 | 0.40701 | 0.094091 | -0.099587 | 123.044 | 122.985 | 123.2051 | 67.4712 | -123.2205 | 122.977 | 123.1593 | 122.9656 | 67.4655 | -123.5123
2981.7969 | 123.2071 | -67.5888 | 55.4947 | -0.0029761 | 0.031102 | -0.00082046 | 0.053081 | -0.0084418 | 0.12938 | 0.0077831 | -0.0036937 | -0.00055553 | 0.054613 | 0.044617 | 0.055317 | 55.4362 | -0.10848 | -67.6205 | 55.4598 | 55.4008 | 55.6209 | -67.735 | -67.599 | -0.11411 | -67.629 | 55.3836 | 55.5659 | 55.3768 | -68.0314 | -0.14618 | -0.034912 | 123.025 | -0.03165 | 0.11453 | -0.093923 | 0.1262 | -0.44257 | -0.11112 | -0.010219 | -0.040145 | 0.40243 | 0.071201 | -0.1179 | 123.0486 | 122.9896 | 123.2097 | 67.4803 | -123.2297 | 122.9724 | 123.1547 | 122.9656 | 67.4747 | -123.5261
2982.7969 | 123.1888 | -67.5842 | 55.481 | 0.0046549 | 0.031102 | -0.0016753 | 0.053081 | -0.0086556 | 0.12917 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054613 | 0.04419 | 0.055317 | 55.4407 | -0.11306 | -67.625 | 55.4644 | 55.4099 | 55.63 | -67.7487 | -67.6036 | -0.11869 | -67.6244 | 55.3882 | 55.5613 | 55.3676 | -68.0314 | -0.16449 | -0.016601 | 123.025 | -0.040806 | 0.12369 | -0.071032 | 0.14909 | -0.44715 | -0.092806 | -0.019374 | -0.040143 | 0.40701 | 0.080355 | -0.11332 | 123.0486 | 122.9942 | 123.2143 | 67.4712 | -123.2297 | 122.9724 | 123.1455 | 122.9519 | 67.4655 | -123.5123
2983.7969 | 123.262 | -67.5705 | 55.4489 | -0.010607 | 0.030889 | -0.0014615 | 0.052867 | -0.0086556 | 0.12938 | -0.0074779 | -0.0041211 | -0.00076913 | 0.054826 | 0.044617 | 0.055103 | 55.4453 | -0.1039 | -67.6159 | 55.4598 | 55.3962 | 55.6255 | -67.735 | -67.599 | -0.11411 | -67.629 | 55.3882 | 55.5659 | 55.3768 | -68.0314 | -0.16449 | 0.010864 | 123.0158 | -0.045382 | 0.11911 | -0.052726 | 0.17656 | -0.46088 | -0.060763 | -0.028529 | -0.058455 | 0.40243 | 0.11698 | -0.072123 | 123.0303 | 122.9667 | 123.196 | 67.4666 | -123.1839 | 122.9586 | 123.1364 | 122.9473 | 67.4564 | -123.4803
2984.7969 | 123.2712 | -67.5842 | 55.4077 | -0.0029761 | 0.031102 | -0.0014615 | 0.052654 | -0.0086556 | 0.12895 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054826 | 0.044831 | 0.055317 | 55.4407 | -0.11306 | -67.625 | 55.4552 | 55.3916 | 55.6163 | -67.735 | -67.6036 | -0.11411 | -67.6335 | 55.3836 | 55.5567 | 55.3859 | -68.0268 | -0.15075 | 0.047484 | 123.025 | -0.040806 | 0.10995 | -0.016106 | 0.2086 | -0.44257 | -0.024142 | -0.019374 | -0.049301 | 0.39327 | 0.14902 | -0.021767 | 123.0394 | 122.9758 | 123.2005 | 67.4712 | -123.1427 | 122.9678 | 123.141 | 122.9702 | 67.4701 | -123.4345
2985.7969 | 123.175 | -67.5934 | 55.4901 | -0.010607 | 0.031102 | -0.0016753 | 0.052867 | -0.0084418 | 0.12917 | -0.0074779 | -0.0039075 | -0.00055553 | 0.054613 | 0.044617 | 0.055531 | 55.4407 | -0.11306 | -67.625 | 55.4552 | 55.4053 | 55.6255 | -67.7396 | -67.6082 | -0.12784 | -67.6244 | 55.3882 | 55.5613 | 55.3859 | -68.0268 | -0.14618 | -0.034913 | 123.0341 | -0.031651 | 0.11453 | -0.084766 | 0.13536 | -0.43341 | -0.10196 | -0.014798 | -0.030988 | 0.40243 | 0.0712 | -0.10416 | 123.0486 | 122.9987 | 123.2189 | 67.4803 | -123.2297 | 122.9815 | 123.1547 | 122.9793 | 67.4655 | -123.5169
2986.7969 | 123.1888 | -67.5842 | 55.4718 | 0.012286 | 0.031102 | -0.0016753 | 0.052867 | -0.0086556 | 0.12917 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.044831 | 0.055317 | 55.4453 | -0.11306 | -67.6205 | 55.4598 | 55.4008 | 55.6117 | -67.7441 | -67.6036 | -0.11411 | -67.6198 | 55.3836 | 55.5659 | 55.3676 | -68.0314 | -0.15991 | -0.012024 | 123.0296 | -0.036227 | 0.12368 | -0.071035 | 0.13993 | -0.44715 | -0.088229 | -0.019374 | -0.035565 | 0.41158 | 0.094089 | -0.10417 | 123.044 | 122.985 | 123.196 | 67.4712 | -123.2159 | 122.9678 | 123.1501 | 122.9519 | 67.4701 | -123.5032
2987.8594 | 123.2437 | -67.5385 | 55.4672 | -0.0029761 | 0.031102 | -0.0016753 | 0.053081 | -0.0088692 | 0.12874 | 0.00015261 | -0.0039075 | -0.00055553 | 0.054826 | 0.044831 | 0.05489 | 55.4362 | -0.11306 | -67.625 | 55.4552 | 55.3825 | 55.6255 | -67.7304 | -67.5944 | -0.11411 | -67.629 | 55.379 | 55.5613 | 55.3814 | -68.036 | -0.19195 | -0.012025 | 122.9746 | -0.086583 | 0.10537 | -0.084773 | 0.15825 | -0.4975 | -0.08823 | -0.055994 | -0.090499 | 0.407 | 0.094088 | -0.085854 | 122.9937 | 122.9209 | 123.1639 | 67.4254 | -123.1976 | 122.9174 | 123.0998 | 122.9198 | 67.4243 | -123.5032
2988.7969 | 123.2391 | -67.5705 | 55.4489 | 0.012286 | 0.030675 | -0.0014615 | 0.053081 | -0.0088692 | 0.12917 | 0.00015261 | -0.0041211 | -0.00076913 | 0.05504 | 0.044831 | 0.055317 | 55.4362 | -0.11764 | -67.6296 | 55.4552 | 55.3916 | 55.6255 | -67.735 | -67.599 | -0.11869 | -67.629 | 55.3882 | 55.5659 | 55.3676 | -68.036 | -0.16449 | 0.006285 | 123.0067 | -0.059117 | 0.10537 | -0.057305 | 0.17656 | -0.46546 | -0.060763 | -0.028529 | -0.058455 | 0.407 | 0.11698 | -0.08128 | 123.0257 | 122.9621 | 123.196 | 67.4529 | -123.1839 | 122.9586 | 123.1364 | 122.9381 | 67.4518 | -123.4849
2989.7969 | 123.2437 | -67.5751 | 55.4443 | -0.0029761 | 0.030889 | -0.0012479 | 0.053081 | -0.0086556 | 0.12917 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.044617 | 0.055531 | 55.4407 | -0.11306 | -67.625 | 55.4552 | 55.3916 | 55.6209 | -67.735 | -67.599 | -0.12784 | -67.6244 | 55.3836 | 55.5613 | 55.3859 | -68.036 | -0.15991 | 0.010863 | 123.0158 | -0.049962 | 0.10995 | -0.052727 | 0.17656 | -0.46088 | -0.060763 | -0.023952 | -0.049299 | 0.41158 | 0.11698 | -0.058388 | 123.0303 | 122.9667 | 123.196 | 67.462 | -123.1793 | 122.9586 | 123.1364 | 122.961 | 67.4472 | -123.4803
2990.7969 | 123.1613 | -67.5934 | 55.5038 | 0.0046549 | 0.030675 | -0.0014615 | 0.053081 | -0.0082282 | 0.12874 | 0.015414 | -0.0039075 | -0.00034193 | 0.054613 | 0.044831 | 0.055317 | 55.4407 | -0.10848 | -67.6205 | 55.4598 | 55.3962 | 55.6255 | -67.7487 | -67.5944 | -0.11869 | -67.6244 | 55.3744 | 55.5522 | 55.3585 | -68.0222 | -0.15534 | -0.044067 | 123.0341 | -0.027072 | 0.12826 | -0.10766 | 0.12163 | -0.42884 | -0.12943 | -0.001062 | -0.030988 | 0.39785 | 0.04831 | -0.14537 | 123.0532 | 122.9896 | 123.2189 | 67.4849 | -123.2526 | 122.9678 | 123.1455 | 122.9519 | 67.4747 | -123.5261
2991.7969 | 123.1705 | -67.5842 | 55.4947 | 0.0046549 | 0.030889 | -0.0014615 | 0.052867 | -0.0086556 | 0.12895 | 0.0077831 | -0.0039075 | -0.00098273 | 0.054826 | 0.044831 | 0.055103 | 55.4407 | -0.12222 | -67.6342 | 55.4552 | 55.3916 | 55.6163 | -67.7487 | -67.599 | -0.11411 | -67.6335 | 55.379 | 55.5613 | 55.3814 | -68.0222 | -0.16449 | -0.039491 | 123.025 | -0.049962 | 0.11453 | -0.10308 | 0.12162 | -0.43799 | -0.1157 | -0.014796 | -0.049301 | 0.38869 | 0.066622 | -0.11332 | 123.0394 | 122.9758 | 123.2005 | 67.462 | -123.2434 | 122.9632 | 123.1455 | 122.9656 | 67.4701 | -123.5169
2992.7969 | 123.2071 | -67.6163 | 55.426 | -0.0029761 | 0.030675 | -0.0012479 | 0.052867 | -0.0088692 | 0.12874 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.044403 | 0.055317 | 55.4407 | -0.11306 | -67.6296 | 55.4598 | 55.3825 | 55.6255 | -67.735 | -67.599 | -0.12327 | -67.629 | 55.379 | 55.5567 | 55.3402 | -68.0268 | -0.11871 | 0.033753 | 123.057 | -0.013341 | 0.10537 | -0.043574 | 0.19945 | -0.41053 | -0.047031 | 0.017247 | -0.012679 | 0.39785 | 0.13071 | -0.085863 | 123.076 | 122.9987 | 123.2417 | 67.5032 | -123.161 | 122.9953 | 123.173 | 122.9564 | 67.493 | -123.4528
2993.7969 | 123.2346 | -67.5476 | 55.4398 | 0.0046549 | 0.030889 | -0.0016753 | 0.053295 | -0.0088692 | 0.12917 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054399 | 0.044831 | 0.055744 | 55.4407 | -0.11306 | -67.625 | 55.4506 | 55.4053 | 55.6209 | -67.735 | -67.5944 | -0.10495 | -67.6244 | 55.379 | 55.5567 | 55.3768 | -68.036 | -0.18738 | 0.010863 | 122.9884 | -0.077428 | 0.10995 | -0.034412 | 0.18114 | -0.48835 | -0.060764 | -0.046839 | -0.076765 | 0.41158 | 0.11698 | -0.062967 | 122.9982 | 122.953 | 123.1685 | 67.4345 | -123.1747 | 122.9266 | 123.1043 | 122.9244 | 67.4427 | -123.4757
2994.7969 | 123.2162 | -67.5659 | 55.5084 | -0.0029761 | 0.030889 | -0.0012479 | 0.052867 | -0.0086556 | 0.12852 | -0.0074779 | -0.0039075 | -0.00076913 | 0.054613 | 0.045044 | 0.055317 | 55.4362 | -0.10848 | -67.625 | 55.446 | 55.3825 | 55.6255 | -67.735 | -67.5944 | -0.11411 | -67.629 | 55.3882 | 55.5567 | 55.3585 | -68.036 | -0.16907 | -0.062381 | 123.0021 | -0.059117 | 0.10995 | -0.12597 | 0.11705 | -0.47004 | -0.12027 | -0.028528 | -0.063033 | 0.407 | 0.048311 | -0.14995 | 123.012 | 122.9484 | 123.1914 | 67.4574 | -123.2434 | 122.9541 | 123.1227 | 122.9244 | 67.4518 | -123.5444
2995.7969 | 123.1613 | -67.5888 | 55.481 | -0.010607 | 0.030889 | -0.0014615 | 0.052867 | -0.0088692 | 0.12895 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.045044 | 0.055103 | 55.4499 | -0.11306 | -67.625 | 55.4552 | 55.3825 | 55.6209 | -67.7304 | -67.5944 | -0.11411 | -67.629 | 55.3744 | 55.5613 | 55.3585 | -68.0268 | -0.1416 | -0.025758 | 123.0387 | -0.036229 | 0.10537 | -0.098506 | 0.13994 | -0.43799 | -0.10654 | -0.00564 | -0.040145 | 0.39785 | 0.080355 | -0.12248 | 123.044 | 122.9713 | 123.2097 | 67.4757 | -123.2114 | 122.9632 | 123.1501 | 122.9473 | 67.4747 | -123.5078
2996.7969 | 123.1842 | -67.6071 | 55.4535 | -0.010607 | 0.030675 | -0.0014615 | 0.053081 | -0.0084418 | 0.12852 | -0.0074779 | -0.0039075 | -0.00076913 | 0.054613 | 0.044617 | 0.055103 | 55.4453 | -0.11306 | -67.625 | 55.4369 | 55.3916 | 55.6255 | -67.735 | -67.599 | -0.11411 | -67.6335 | 55.3882 | 55.5522 | 55.3768 | -68.0268 | -0.12787 | -0.016605 | 123.0524 | -0.017918 | 0.10995 | -0.061882 | 0.17198 | -0.41968 | -0.06534 | 0.008092 | -0.026413 | 0.39327 | 0.098664 | -0.0767 | 123.044 | 122.9987 | 123.2326 | 67.4941 | -123.1885 | 122.9953 | 123.1593 | 122.9839 | 67.493 | -123.4803
2997.7969 | 123.1796 | -67.6163 | 55.4901 | -0.0029761 | 0.030248 | -0.0016753 | 0.053295 | -0.0086556 | 0.12852 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.044831 | 0.055317 | 55.4316 | -0.12222 | -67.625 | 55.4552 | 55.3916 | 55.6209 | -67.735 | -67.599 | -0.11869 | -67.6244 | 55.3836 | 55.5705 | 55.3585 | -68.036 | -0.11871 | -0.034913 | 123.0479 | -0.008763 | 0.10995 | -0.098503 | 0.13078 | -0.41968 | -0.10654 | 0.017247 | -0.0081 | 0.41158 | 0.080357 | -0.13164 | 123.0715 | 123.0079 | 123.2372 | 67.4941 | -123.2251 | 122.9998 | 123.1867 | 122.9747 | 67.4976 | -123.5261
2998.7969 | 123.1796 | -67.5385 | 55.4718 | 0.0046549 | 0.030675 | -0.0012479 | 0.053081 | -0.0084418 | 0.12852 | 0.00015261 | -0.0039075 | -0.00034193 | 0.05504 | 0.044617 | 0.055103 | 55.4407 | -0.11306 | -67.625 | 55.4506 | 55.4053 | 55.6209 | -67.7304 | -67.5944 | -0.12784 | -67.6244 | 55.3744 | 55.5613 | 55.3676 | -68.036 | -0.19195 | -0.021181 | 122.9792 | -0.086583 | 0.10537 | -0.066456 | 0.14909 | -0.4975 | -0.097386 | -0.055994 | -0.08592 | 0.41158 | 0.08951 | -0.10417 | 122.9891 | 122.9438 | 123.1593 | 67.4254 | -123.2022 | 122.9129 | 123.0998 | 122.9061 | 67.4106 | -123.5078
2999.8125 | 123.2162 | -67.6071 | 55.481 | -0.0029761 | 0.030675 | -0.0014615 | 0.053081 | -0.0086556 | 0.12831 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054613 | 0.044403 | 0.055103 | 55.4362 | -0.1039 | -67.6159 | 55.4552 | 55.387 | 55.6163 | -67.735 | -67.599 | -0.11869 | -67.6198 | 55.379 | 55.5659 | 55.3585 | -68.0268 | -0.12787 | -0.025758 | 123.0433 | -0.008761 | 0.11911 | -0.093927 | 0.13536 | -0.41968 | -0.10196 | 0.008092 | -0.012677 | 0.407 | 0.084934 | -0.12248 | 123.0623 | 122.9941 | 123.2234 | 67.5032 | -123.2159 | 122.9861 | 123.173 | 122.9656 | 67.4884 | -123.5078
3000.7969 | 123.2483 | -67.5613 | 55.426 | -0.010607 | 0.030461 | -0.0012479 | 0.053081 | -0.0082282 | 0.12831 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054613 | 0.04419 | 0.055103 | 55.4362 | -0.11306 | -67.6159 | 55.4506 | 55.3825 | 55.6117 | -67.7304 | -67.5899 | -0.11411 | -67.6244 | 55.379 | 55.5705 | 55.3585 | -68.0314 | -0.16906 | 0.024596 | 122.9975 | -0.054538 | 0.11453 | -0.043574 | 0.18571 | -0.47004 | -0.047031 | -0.028527 | -0.063032 | 0.40701 | 0.14444 | -0.067549 | 123.012 | 122.9438 | 123.1731 | 67.4483 | -123.1564 | 122.9403 | 123.1318 | 122.9198 | 67.4472 | -123.4574
3001.7969 | 123.2574 | -67.5659 | 55.4398 | -0.0029761 | 0.030248 | -0.0012479 | 0.053081 | -0.0086556 | 0.12852 | 0.00015261 | -0.0043347 | -0.00098273 | 0.054613 | 0.044403 | 0.055317 | 55.4407 | -0.11764 | -67.6296 | 55.4506 | 55.387 | 55.6209 | -67.735 | -67.5944 | -0.11411 | -67.629 | 55.379 | 55.5613 | 55.3493 | -68.036 | -0.16907 | 0.010863 | 123.0067 | -0.063695 | 0.10537 | -0.052728 | 0.18114 | -0.47004 | -0.060764 | -0.028528 | -0.063033 | 0.407 | 0.12155 | -0.090439 | 123.0165 | 122.9529 | 123.1868 | 67.4483 | -123.1747 | 122.9449 | 123.1272 | 122.9152 | 67.4518 | -123.4757
3002.7969 | 123.2666 | -67.5476 | 55.4947 | -0.010607 | 0.030034 | -0.0014615 | 0.053295 | -0.0086556 | 0.12852 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.044831 | 0.055531 | 55.4453 | -0.11764 | -67.625 | 55.446 | 55.3916 | 55.6163 | -67.735 | -67.5899 | -0.13242 | -67.6244 | 55.379 | 55.5567 | 55.3539 | -68.036 | -0.18738 | -0.048648 | 122.9929 | -0.077428 | 0.10995 | -0.10308 | 0.12162 | -0.48835 | -0.1157 | -0.04226 | -0.076765 | 0.41158 | 0.062044 | -0.14079 | 122.9936 | 122.9392 | 123.1639 | 67.43 | -123.2297 | 122.9266 | 123.1043 | 122.9015 | 67.4152 | -123.5306
3003.7969 | 123.143 | -67.6346 | 55.4901 | -0.0029761 | 0.030461 | -0.0016753 | 0.052867 | -0.0088692 | 0.12852 | 0.00015261 | -0.0043347 | -0.00076913 | 0.05504 | 0.044831 | 0.055317 | 55.4362 | -0.10848 | -67.625 | 55.4552 | 55.4008 | 55.6209 | -67.7441 | -67.5944 | -0.11411 | -67.6152 | 55.3836 | 55.5705 | 55.3768 | -68.0268 | -0.10956 | -0.034913 | 123.0708 | 0.009548 | 0.11911 | -0.089345 | 0.13078 | -0.39221 | -0.10654 | 0.040137 | 0.019368 | 0.41158 | 0.080357 | -0.11332 | 123.0898 | 123.0354 | 123.2555 | 67.5261 | -123.2343 | 123.0182 | 123.2051 | 123.0114 | 67.5205 | -123.5169
3004.8125 | 123.2391 | -67.5613 | 55.4581 | 0.0046549 | 0.030248 | -0.0012479 | 0.052654 | -0.0088692 | 0.12852 | 0.00015261 | -0.0039075 | -0.0011965 | 0.054613 | 0.044831 | 0.055317 | 55.4362 | -0.11306 | -67.625 | 55.4552 | 55.3779 | 55.6026 | -67.7304 | -67.599 | -0.11869 | -67.6244 | 55.3882 | 55.5613 | 55.3493 | -68.036 | -0.16906 | -0.00287 | 122.9975 | -0.063695 | 0.10537 | -0.080197 | 0.14451 | -0.47462 | -0.069918 | -0.037685 | -0.063032 | 0.41158 | 0.10324 | -0.10875 | 123.0165 | 122.9392 | 123.1639 | 67.4483 | -123.1885 | 122.9495 | 123.1227 | 122.9107 | 67.4427 | -123.494
3005.7969 | 123.2941 | -67.5568 | 55.4581 | 0.0046549 | 0.030461 | -0.0016753 | 0.053295 | -0.0084418 | 0.12874 | 0.0077831 | -0.0041211 | -0.00034193 | 0.05504 | 0.045044 | 0.055531 | 55.4453 | -0.11306 | -67.6388 | 55.4552 | 55.3962 | 55.6072 | -67.7304 | -67.5944 | -0.11869 | -67.6198 | 55.379 | 55.5613 | 55.3493 | -68.036 | -0.17364 | -0.00287 | 123.0021 | -0.082007 | 0.091634 | -0.061881 | 0.14909 | -0.47919 | -0.079075 | -0.037683 | -0.063031 | 0.41616 | 0.10324 | -0.10875 | 123.012 | 122.953 | 123.1639 | 67.4437 | -123.1885 | 122.9358 | 123.1181 | 122.9061 | 67.4381 | -123.494
3006.7969 | 123.2666 | -67.5476 | 55.4718 | 0.0046549 | 0.030034 | -0.0014615 | 0.053295 | -0.0086556 | 0.12852 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054826 | 0.044831 | 0.055531 | 55.4453 | -0.11764 | -67.6296 | 55.446 | 55.387 | 55.6209 | -67.7396 | -67.5944 | -0.11411 | -67.6244 | 55.3836 | 55.5659 | 55.3814 | -68.0268 | -0.19196 | -0.02576 | 122.9929 | -0.082006 | 0.10995 | -0.084772 | 0.14909 | -0.47919 | -0.088229 | -0.046839 | -0.076765 | 0.40243 | 0.094089 | -0.090432 | 122.9936 | 122.9346 | 123.1685 | 67.43 | -123.2114 | 122.9312 | 123.1135 | 122.929 | 67.4335 | -123.4986
3007.7969 | 123.2483 | -67.5613 | 55.4855 | -0.010607 | 0.030461 | -0.0014615 | 0.053295 | -0.0086556 | 0.12831 | 0.00015261 | -0.0041211 | -0.00098273 | 0.054826 | 0.045044 | 0.055317 | 55.4362 | -0.11306 | -67.6296 | 55.446 | 55.3962 | 55.6163 | -67.7304 | -67.5899 | -0.11869 | -67.6244 | 55.3836 | 55.5613 | 55.3859 | -68.0268 | -0.16906 | -0.039493 | 122.9975 | -0.068273 | 0.10079 | -0.089347 | 0.13078 | -0.46546 | -0.10196 | -0.028527 | -0.063032 | 0.40243 | 0.075777 | -0.099587 | 123.0074 | 122.9575 | 123.1777 | 67.4483 | -123.2159 | 122.9449 | 123.1227 | 122.9473 | 67.4427 | -123.5123
3008.7969 | 123.2941 | -67.543 | 55.4855 | 0.0046549 | 0.030248 | -0.0014615 | 0.053081 | -0.0084418 | 0.12831 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054826 | 0.044617 | 0.055317 | 55.4362 | -0.11306 | -67.625 | 55.4552 | 55.3779 | 55.6209 | -67.735 | -67.6036 | -0.11869 | -67.6106 | 55.3744 | 55.5522 | 55.3722 | -68.0222 | -0.19195 | -0.030336 | 122.9792 | -0.082005 | 0.10995 | -0.10766 | 0.13536 | -0.47919 | -0.11112 | -0.060573 | -0.067606 | 0.41158 | 0.06662 | -0.11332 | 122.9982 | 122.9209 | 123.1639 | 67.43 | -123.2205 | 122.9174 | 123.0952 | 122.9152 | 67.4243 | -123.5078
3009.8125 | 123.2758 | -67.5476 | 55.4626 | -0.0029761 | 0.02982 | -0.0010343 | 0.053081 | -0.0088692 | 0.12831 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054826 | 0.044403 | 0.055103 | 55.4362 | -0.11306 | -67.625 | 55.4506 | 55.387 | 55.6163 | -67.7304 | -67.6036 | -0.11869 | -67.6198 | 55.3698 | 55.5567 | 55.3722 | -68.036 | -0.1828 | -0.012025 | 122.9838 | -0.077428 | 0.10537 | -0.075616 | 0.15367 | -0.48835 | -0.092809 | -0.055996 | -0.072187 | 0.41616 | 0.094088 | -0.090434 | 122.9982 | 122.9346 | 123.1639 | 67.4345 | -123.193 | 122.9174 | 123.1043 | 122.9198 | 67.4289 | -123.4986
3010.875 | 123.143 | -67.6163 | 55.4855 | -0.010607 | 0.030248 | -0.0010343 | 0.052867 | -0.0086556 | 0.12831 | -0.0074779 | -0.0041211 | -0.00098273 | 0.054613 | 0.044403 | 0.055317 | 55.4407 | -0.11306 | -67.625 | 55.4598 | 55.3916 | 55.6209 | -67.735 | -67.5899 | -0.12327 | -67.6244 | 55.3744 | 55.5613 | 55.3676 | -68.0222 | -0.11871 | -0.025757 | 123.057 | -0.008763 | 0.10995 | -0.093926 | 0.13536 | -0.40595 | -0.11112 | 0.026405 | -0.0081 | 0.39785 | 0.075777 | -0.1179 | 123.076 | 123.0079 | 123.2372 | 67.5032 | -123.2205 | 122.9907 | 123.1776 | 122.9839 | 67.493 | -123.5078
3011.7969 | 123.2986 | -67.543 | 55.4306 | -0.0029761 | 0.030034 | -0.0014615 | 0.053081 | -0.0084418 | 0.12874 | 0.023044 | -0.0036937 | -0.00034193 | 0.054399 | 0.044617 | 0.055103 | 55.4453 | -0.11764 | -67.6159 | 55.4415 | 55.3962 | 55.6117 | -67.7304 | -67.5853 | -0.13242 | -67.6244 | 55.3607 | 55.5659 | 55.3402 | -68.0268 | -0.18737 | 0.010861 | 122.9884 | -0.072848 | 0.11453 | -0.034415 | 0.18113 | -0.48377 | -0.069923 | -0.042259 | -0.081342 | 0.40243 | 0.13529 | -0.090441 | 122.9845 | 122.9392 | 123.1548 | 67.4254 | -123.161 | 122.9037 | 123.1089 | 122.8832 | 67.4106 | -123.4574
3012.7969 | 123.1613 | -67.5751 | 55.5038 | 0.0046549 | 0.030034 | -0.0014615 | 0.052867 | -0.0086556 | 0.12852 | 0.0077831 | -0.0039075 | -0.00076913 | 0.054613 | 0.045044 | 0.055531 | 55.4407 | -0.11306 | -67.625 | 55.4552 | 55.3916 | 55.6163 | -67.7396 | -67.5853 | -0.11869 | -67.6244 | 55.3698 | 55.5567 | 55.3539 | -68.0268 | -0.16449 | -0.048646 | 123.0158 | -0.049962 | 0.11453 | -0.11224 | 0.11247 | -0.45172 | -0.13401 | -0.010216 | -0.049299 | 0.40243 | 0.052889 | -0.14995 | 123.0303 | 122.9667 | 123.1914 | 67.462 | -123.2434 | 122.9449 | 123.1318 | 122.929 | 67.4564 | -123.5306
3013.7969 | 123.2666 | -67.5247 | 55.4718 | -0.0029761 | 0.030034 | -0.0012479 | 0.053295 | -0.0086556 | 0.1281 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.044831 | 0.055317 | 55.4407 | -0.11764 | -67.6342 | 55.4598 | 55.3825 | 55.6117 | -67.7304 | -67.6036 | -0.12327 | -67.629 | 55.379 | 55.5522 | 55.3676 | -68.0268 | -0.20568 | -0.012024 | 122.9655 | -0.10947 | 0.096213 | -0.089351 | 0.13993 | -0.50208 | -0.092808 | -0.078884 | -0.10423 | 0.39785 | 0.080353 | -0.10417 | 122.9845 | 122.9072 | 123.1365 | 67.4071 | -123.2022 | 122.9037 | 123.0769 | 122.8924 | 67.4015 | -123.4986
3014.8125 | 123.2346 | -67.5751 | 55.4398 | -0.0029761 | 0.02982 | -0.0016753 | 0.053081 | -0.0086556 | 0.1281 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054613 | 0.045044 | 0.055317 | 55.4362 | -0.11764 | -67.6205 | 55.446 | 55.3916 | 55.6209 | -67.7304 | -67.599 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3493 | -68.0268 | -0.15533 | 0.006284 | 123.0112 | -0.045383 | 0.10995 | -0.048149 | 0.18114 | -0.45172 | -0.074499 | -0.023952 | -0.044721 | 0.407 | 0.11698 | -0.090439 | 123.0211 | 122.9667 | 123.196 | 67.4574 | -123.1702 | 122.9403 | 123.1318 | 122.9244 | 67.4564 | -123.4666
3015.7969 | 123.2712 | -67.5385 | 55.4672 | 0.0046549 | 0.030034 | -0.0012479 | 0.052867 | -0.0086556 | 0.1281 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054826 | 0.044831 | 0.055103 | 55.4362 | -0.12222 | -67.6159 | 55.446 | 55.3962 | 55.6163 | -67.735 | -67.5853 | -0.11869 | -67.6198 | 55.3607 | 55.5567 | 55.3585 | -68.0314 | -0.19653 | -0.021182 | 122.9746 | -0.077426 | 0.11911 | -0.071036 | 0.14909 | -0.49292 | -0.10654 | -0.046837 | -0.081342 | 0.41158 | 0.08951 | -0.10875 | 122.9845 | 122.9346 | 123.1548 | 67.4162 | -123.2022 | 122.8991 | 123.0952 | 122.8969 | 67.4198 | -123.4986
3016.7969 | 123.1384 | -67.5659 | 55.513 | 0.0046549 | 0.02982 | -0.0012479 | 0.053081 | -0.0082282 | 0.1281 | 0.023044 | -0.0039075 | -0.00076913 | 0.054613 | 0.044831 | 0.055103 | 55.4362 | -0.11764 | -67.625 | 55.4552 | 55.3916 | 55.6117 | -67.735 | -67.6036 | -0.11869 | -67.6244 | 55.3698 | 55.5522 | 55.3676 | -68.036 | -0.16907 | -0.057801 | 123.0021 | -0.059117 | 0.10995 | -0.12139 | 0.098735 | -0.47004 | -0.14316 | -0.037685 | -0.058454 | 0.41158 | 0.039155 | -0.14537 | 123.0211 | 122.9575 | 123.1777 | 67.4483 | -123.248 | 122.9358 | 123.1181 | 122.9336 | 67.4472 | -123.549
3017.7969 | 123.2895 | -67.5613 | 55.4398 | 0.0046549 | 0.030034 | -0.0014615 | 0.053081 | -0.0086556 | 0.12874 | 0.00015261 | -0.0043347 | -0.00098273 | 0.055254 | 0.045044 | 0.055317 | 55.4453 | -0.11764 | -67.6205 | 55.446 | 55.3962 | 55.63 | -67.735 | -67.5944 | -0.11869 | -67.6198 | 55.3698 | 55.5567 | 55.3539 | -68.0314 | -0.17364 | 0.006284 | 123.0067 | -0.059116 | 0.11453 | -0.04357 | 0.19029 | -0.47004 | -0.069921 | -0.033106 | -0.058454 | 0.41158 | 0.11698 | -0.08586 | 123.0074 | 122.9575 | 123.1914 | 67.4437 | -123.1747 | 122.9312 | 123.1181 | 122.9152 | 67.4427 | -123.4711
3018.7969 | 123.2529 | -67.5339 | 55.481 | -0.0029761 | 0.02982 | -0.0014615 | 0.053081 | -0.0086556 | 0.12852 | 0.0077831 | -0.0045483 | -0.00034193 | 0.05504 | 0.044831 | 0.055103 | 55.4407 | -0.11764 | -67.6113 | 55.4506 | 55.3916 | 55.6072 | -67.7304 | -67.5899 | -0.12784 | -67.6152 | 55.3698 | 55.5613 | 55.3997 | -68.0314 | -0.19653 | -0.030336 | 122.9746 | -0.077425 | 0.1191 | -0.089348 | 0.1262 | -0.4975 | -0.11112 | -0.055992 | -0.08134 | 0.41616 | 0.080355 | -0.081273 | 122.9845 | 122.9255 | 123.141 | 67.4162 | -123.2114 | 122.9037 | 123.0952 | 122.9336 | 67.406 | -123.5123
3019.8125 | 123.2346 | -67.5613 | 55.4581 | 0.0046549 | 0.029607 | -0.0012479 | 0.052867 | -0.0088692 | 0.12852 | 0.0077831 | -0.0039075 | -0.00055553 | 0.05504 | 0.044617 | 0.055103 | 55.4362 | -0.11306 | -67.6205 | 55.4552 | 55.4053 | 55.6255 | -67.7258 | -67.5944 | -0.11869 | -67.6244 | 55.3744 | 55.5567 | 55.3585 | -68.0314 | -0.16448 | -0.00287 | 122.9975 | -0.059116 | 0.10537 | -0.052723 | 0.1674 | -0.47004 | -0.083653 | -0.033106 | -0.063032 | 0.40701 | 0.098665 | -0.099593 | 123.0165 | 122.9667 | 123.1868 | 67.4483 | -123.1839 | 122.9358 | 123.1181 | 122.9198 | 67.4427 | -123.4894
3020.7969 | 123.1888 | -67.5934 | 55.4672 | -0.0029761 | 0.02982 | -0.0016753 | 0.052867 | -0.0084418 | 0.1281 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054826 | 0.045044 | 0.055317 | 55.4407 | -0.11306 | -67.6113 | 55.446 | 55.4008 | 55.6209 | -67.7396 | -67.5899 | -0.11869 | -67.6244 | 55.3607 | 55.5613 | 55.3722 | -68.0222 | -0.14618 | -0.021182 | 123.0341 | -0.017916 | 0.12826 | -0.066457 | 0.15367 | -0.42884 | -0.10654 | 0.003517 | -0.030988 | 0.39785 | 0.094088 | -0.095012 | 123.0394 | 122.9942 | 123.2143 | 67.4803 | -123.2068 | 122.9541 | 123.1547 | 122.9656 | 67.4747 | -123.4894
3021.7969 | 123.1888 | -67.5797 | 55.481 | 0.012286 | 0.029607 | -0.0014615 | 0.053295 | -0.0088692 | 0.12788 | 0.0077831 | -0.0039075 | -0.00098273 | 0.054826 | 0.045258 | 0.05489 | 55.4362 | -0.11306 | -67.6067 | 55.4552 | 55.4053 | 55.6255 | -67.7258 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3859 | -68.0268 | -0.14617 | -0.025758 | 123.0158 | -0.027071 | 0.1191 | -0.075611 | 0.14451 | -0.44715 | -0.1157 | -0.010216 | -0.040143 | 0.407 | 0.075777 | -0.095009 | 123.0349 | 122.985 | 123.2051 | 67.4666 | -123.2068 | 122.9449 | 123.1364 | 122.9656 | 67.461 | -123.5078
3022.7969 | 123.143 | -67.6071 | 55.5176 | 0.0046549 | 0.030248 | -0.0014615 | 0.052654 | -0.0086556 | 0.12831 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054826 | 0.045044 | 0.055103 | 55.4362 | -0.10848 | -67.6113 | 55.446 | 55.3916 | 55.6117 | -67.7258 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3493 | -68.0222 | -0.11871 | -0.071536 | 123.0433 | -0.004183 | 0.11453 | -0.12597 | 0.094157 | -0.4151 | -0.15232 | 0.01725 | -0.012677 | 0.40243 | 0.039156 | -0.16826 | 123.0532 | 122.9987 | 123.2189 | 67.4986 | -123.2434 | 122.9724 | 123.1639 | 122.9564 | 67.4884 | -123.5398
3023.7969 | 123.1384 | -67.5522 | 55.513 | 0.0046549 | 0.030461 | -0.0014615 | 0.053081 | -0.0088692 | 0.1281 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.044831 | 0.055317 | 55.4407 | -0.12222 | -67.6159 | 55.446 | 55.4008 | 55.6209 | -67.7396 | -67.5944 | -0.12327 | -67.6152 | 55.3653 | 55.5567 | 55.3676 | -68.0268 | -0.18738 | -0.066958 | 122.9929 | -0.063693 | 0.12368 | -0.11223 | 0.10789 | -0.47461 | -0.14774 | -0.042261 | -0.06303 | 0.41158 | 0.043734 | -0.14537 | 122.9982 | 122.953 | 123.1731 | 67.43 | -123.2526 | 122.9174 | 123.1089 | 122.9198 | 67.4289 | -123.5398
3024.7969 | 123.2346 | -67.6163 | 55.4169 | -0.0029761 | 0.030461 | -0.0014615 | 0.052654 | -0.0088692 | 0.1281 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054613 | 0.045044 | 0.055103 | 55.4316 | -0.11764 | -67.6113 | 55.4506 | 55.4099 | 55.6209 | -67.7304 | -67.5944 | -0.12327 | -67.6244 | 55.3698 | 55.5567 | 55.3676 | -68.0268 | -0.11413 | 0.033751 | 123.0479 | 0.004972 | 0.1191 | -0.006945 | 0.20402 | -0.41053 | -0.047033 | 0.021826 | -0.0081 | 0.40243 | 0.13986 | -0.049236 | 123.0669 | 123.0262 | 123.2372 | 67.4986 | -123.1473 | 122.9861 | 123.173 | 122.9839 | 67.493 | -123.4437
3025.7969 | 123.1247 | -67.5842 | 55.5176 | 0.0046549 | 0.02982 | -0.0012479 | 0.052654 | -0.0088692 | 0.12831 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.044831 | 0.055317 | 55.4316 | -0.11764 | -67.6113 | 55.4552 | 55.3962 | 55.6163 | -67.735 | -67.5944 | -0.12327 | -67.6198 | 55.3744 | 55.5659 | 55.3768 | -68.0268 | -0.15075 | -0.062379 | 123.0158 | -0.027071 | 0.12368 | -0.12139 | 0.098736 | -0.44257 | -0.14316 | -0.010217 | -0.035565 | 0.407 | 0.048313 | -0.14079 | 123.0394 | 122.9804 | 123.2005 | 67.4666 | -123.2526 | 122.9586 | 123.1501 | 122.961 | 67.461 | -123.5444
3026.8594 | 123.1476 | -67.598 | 55.4626 | 0.0046549 | 0.029607 | -0.0014615 | 0.053295 | -0.0086556 | 0.12831 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054613 | 0.044831 | 0.055317 | 55.4407 | -0.11306 | -67.6159 | 55.4506 | 55.4008 | 55.6163 | -67.7396 | -67.5853 | -0.12327 | -67.6198 | 55.3698 | 55.5567 | 55.3814 | -68.0268 | -0.1416 | -0.012025 | 123.0387 | -0.017917 | 0.12368 | -0.061879 | 0.15367 | -0.42884 | -0.092809 | 0.012672 | -0.021833 | 0.407 | 0.094088 | -0.081276 | 123.0486 | 122.9987 | 123.2143 | 67.4849 | -123.2022 | 122.9678 | 123.1547 | 122.9793 | 67.4747 | -123.4894
3027.7969 | 123.1842 | -67.5659 | 55.4855 | -0.0029761 | 0.02982 | -0.0014615 | 0.053081 | -0.0082282 | 0.1281 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.045044 | 0.055317 | 55.4407 | -0.12222 | -67.6159 | 55.4552 | 55.4053 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6152 | 55.3653 | 55.5659 | 55.3768 | -68.0314 | -0.16449 | -0.030336 | 123.0067 | -0.04996 | 0.11453 | -0.080189 | 0.13078 | -0.46546 | -0.12028 | -0.023949 | -0.049297 | 0.41616 | 0.080356 | -0.10874 | 123.0211 | 122.9713 | 123.1822 | 67.4437 | -123.2159 | 122.9312 | 123.1318 | 122.9427 | 67.4427 | -123.5169
3028.7969 | 123.143 | -67.6071 | 55.4489 | -0.0029761 | 0.02982 | -0.0018889 | 0.053295 | -0.0086556 | 0.12788 | 0.00015261 | -0.0041211 | -0.00076913 | 0.05504 | 0.044617 | 0.055103 | 55.4407 | -0.11306 | -67.6113 | 55.446 | 55.3916 | 55.6163 | -67.7396 | -67.5899 | -0.11411 | -67.6198 | 55.3653 | 55.5613 | 55.3402 | -68.0268 | -0.13245 | -0.002872 | 123.0479 | -0.004183 | 0.12826 | -0.057305 | 0.1674 | -0.41968 | -0.083655 | 0.01725 | -0.012677 | 0.407 | 0.1124 | -0.10875 | 123.0532 | 122.9987 | 123.2234 | 67.4941 | -123.1885 | 122.9724 | 123.1684 | 122.9473 | 67.493 | -123.4757
3029.7969 | 123.2712 | -67.5659 | 55.4398 | 0.0046549 | 0.029393 | -0.0014615 | 0.052867 | -0.0088692 | 0.12788 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054826 | 0.045258 | 0.05489 | 55.4407 | -0.11764 | -67.625 | 55.446 | 55.387 | 55.6163 | -67.7396 | -67.5853 | -0.11869 | -67.6244 | 55.3653 | 55.5522 | 55.3631 | -68.0314 | -0.17364 | 0.006284 | 123.0067 | -0.059117 | 0.11453 | -0.052728 | 0.17656 | -0.46546 | -0.074499 | -0.019371 | -0.058454 | 0.40701 | 0.1124 | -0.076703 | 123.012 | 122.9529 | 123.1822 | 67.4483 | -123.1793 | 122.9312 | 123.1181 | 122.929 | 67.4472 | -123.4711
3030.7969 | 123.143 | -67.6025 | 55.4855 | -0.0029761 | 0.02982 | -0.0014615 | 0.052867 | -0.0088692 | 0.12788 | -0.0074779 | -0.0043347 | -0.00098273 | 0.054613 | 0.045258 | 0.055531 | 55.4316 | -0.11764 | -67.6159 | 55.4552 | 55.3962 | 55.6163 | -67.735 | -67.5899 | -0.11869 | -67.6335 | 55.3653 | 55.5613 | 55.3768 | -68.0222 | -0.13244 | -0.030336 | 123.0341 | -0.013339 | 0.11911 | -0.089347 | 0.13078 | -0.41968 | -0.12028 | 0.012672 | -0.030991 | 0.38869 | 0.075777 | -0.10874 | 123.0577 | 122.9987 | 123.2189 | 67.4849 | -123.2205 | 122.9678 | 123.1639 | 122.9793 | 67.4839 | -123.5078
3031.7969 | 123.1522 | -67.5797 | 55.5176 | -0.010607 | 0.02982 | -0.0014615 | 0.052867 | -0.0086556 | 0.1281 | 0.0077831 | -0.0045483 | -0.00076913 | 0.054826 | 0.045258 | 0.055103 | 55.4362 | -0.11764 | -67.625 | 55.4552 | 55.4008 | 55.6117 | -67.7396 | -67.5899 | -0.11411 | -67.6198 | 55.3698 | 55.5567 | 55.3631 | -68.036 | -0.15991 | -0.062379 | 123.0158 | -0.045384 | 0.11453 | -0.11681 | 0.094157 | -0.45631 | -0.14774 | -0.010216 | -0.040143 | 0.41616 | 0.039156 | -0.15452 | 123.0349 | 122.9804 | 123.1914 | 67.462 | -123.2571 | 122.9495 | 123.1364 | 122.9427 | 67.4655 | -123.5535
3032.7969 | 123.1705 | -67.5797 | 55.481 | -0.010607 | 0.029607 | -0.0012479 | 0.053081 | -0.0086556 | 0.1281 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054826 | 0.045258 | 0.055317 | 55.4362 | -0.11764 | -67.6205 | 55.4506 | 55.3962 | 55.6209 | -67.7396 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3585 | -68.0268 | -0.15991 | -0.030336 | 123.0158 | -0.040805 | 0.11911 | -0.084769 | 0.13994 | -0.44715 | -0.1157 | -0.010216 | -0.040143 | 0.407 | 0.075777 | -0.12248 | 123.0303 | 122.9758 | 123.2005 | 67.462 | -123.2205 | 122.9449 | 123.1364 | 122.9381 | 67.461 | -123.5078
3033.7969 | 123.1613 | -67.5842 | 55.4947 | -0.010607 | 0.02982 | -0.0014615 | 0.052867 | -0.0090828 | 0.12767 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.045044 | 0.055317 | 55.4362 | -0.11306 | -67.6159 | 55.4598 | 55.3916 | 55.6163 | -67.7396 | -67.5899 | -0.11869 | -67.6198 | 55.3744 | 55.5567 | 55.3676 | -68.0314 | -0.15533 | -0.034912 | 123.0204 | -0.031649 | 0.12368 | -0.10308 | 0.12162 | -0.44715 | -0.12027 | -0.005638 | -0.035565 | 0.41158 | 0.062044 | -0.12706 | 123.044 | 122.9758 | 123.2005 | 67.4712 | -123.2343 | 122.9586 | 123.141 | 122.9519 | 67.4655 | -123.5261
3034.7969 | 123.23 | -67.543 | 55.4352 | -0.0029761 | 0.029607 | -0.0014615 | 0.053081 | -0.0084418 | 0.1281 | -0.0074779 | -0.0041211 | -0.00098273 | 0.054826 | 0.045044 | 0.055317 | 55.4316 | -0.12222 | -67.6296 | 55.4506 | 55.3825 | 55.6209 | -67.735 | -67.5853 | -0.11869 | -67.629 | 55.3653 | 55.5522 | 55.3631 | -68.0314 | -0.19195 | 0.01544 | 122.9746 | -0.086583 | 0.10537 | -0.05273 | 0.18571 | -0.48835 | -0.069922 | -0.042259 | -0.085921 | 0.40243 | 0.11697 | -0.072126 | 122.9937 | 122.9255 | 123.1639 | 67.4208 | -123.1702 | 122.9083 | 123.0952 | 122.9061 | 67.4243 | -123.4666
3035.7969 | 123.1796 | -67.5888 | 55.4947 | -0.010607 | 0.02982 | -0.0016753 | 0.052867 | -0.0084418 | 0.12831 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045258 | 0.055317 | 55.4316 | -0.10848 | -67.6296 | 55.4598 | 55.4053 | 55.6209 | -67.7304 | -67.5944 | -0.11411 | -67.6244 | 55.3744 | 55.5613 | 55.3722 | -68.0222 | -0.1416 | -0.034912 | 123.0204 | -0.040807 | 0.10079 | -0.089344 | 0.1262 | -0.43341 | -0.12027 | -0.00564 | -0.035566 | 0.39785 | 0.066622 | -0.12248 | 123.0486 | 122.9942 | 123.2097 | 67.4803 | -123.2251 | 122.9632 | 123.1501 | 122.961 | 67.4747 | -123.5169
3036.7969 | 123.1979 | -67.5934 | 55.4626 | -0.0029761 | 0.029179 | -0.0014615 | 0.053081 | -0.0088692 | 0.12788 | -0.0074779 | -0.0039075 | -0.00055553 | 0.054399 | 0.044617 | 0.055103 | 55.4362 | -0.11764 | -67.6342 | 55.4552 | 55.387 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6244 | 55.3698 | 55.5659 | 55.3356 | -68.036 | -0.13702 | -0.007447 | 123.0296 | -0.040807 | 0.096213 | -0.075616 | 0.15367 | -0.44257 | -0.092809 | 0.003517 | -0.030988 | 0.41158 | 0.10325 | -0.12706 | 123.0486 | 122.9804 | 123.2097 | 67.4757 | -123.193 | 122.9632 | 123.1593 | 122.929 | 67.4701 | -123.4986
3037.7969 | 123.1338 | -67.5934 | 55.4672 | -0.010607 | 0.029607 | -0.0016753 | 0.052867 | -0.0084418 | 0.12788 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.045044 | 0.05489 | 55.4316 | -0.11306 | -67.6342 | 55.4506 | 55.3825 | 55.6072 | -67.735 | -67.599 | -0.11869 | -67.6198 | 55.3698 | 55.5613 | 55.3631 | -68.0268 | -0.1416 | -0.016603 | 123.025 | -0.040807 | 0.10079 | -0.084773 | 0.13993 | -0.43341 | -0.097387 | -0.005641 | -0.02641 | 0.407 | 0.094088 | -0.10417 | 123.044 | 122.9758 | 123.2005 | 67.4803 | -123.2022 | 122.9632 | 123.1547 | 122.9564 | 67.4747 | -123.494
3038.7969 | 123.111 | -67.6025 | 55.481 | -0.010607 | 0.029607 | -0.0016753 | 0.052867 | -0.0088692 | 0.12746 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054399 | 0.045044 | 0.055531 | 55.4316 | -0.11764 | -67.6296 | 55.4506 | 55.387 | 55.6209 | -67.7396 | -67.5899 | -0.12327 | -67.6198 | 55.3653 | 55.5613 | 55.3676 | -68.0268 | -0.13702 | -0.030336 | 123.0341 | -0.027074 | 0.10995 | -0.093927 | 0.13994 | -0.42426 | -0.1157 | 0.012672 | -0.017255 | 0.407 | 0.080355 | -0.11332 | 123.0532 | 122.9896 | 123.2234 | 67.4849 | -123.2205 | 122.9678 | 123.1639 | 122.9702 | 67.4793 | -123.5078
3039.7969 | 123.2758 | -67.5613 | 55.426 | 0.0046549 | 0.029393 | -0.0014615 | 0.053081 | -0.0084418 | 0.12831 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045044 | 0.055317 | 55.4316 | -0.12222 | -67.625 | 55.4415 | 55.387 | 55.6117 | -67.7304 | -67.5899 | -0.11869 | -67.6152 | 55.3744 | 55.5613 | 55.3585 | -68.0268 | -0.16906 | 0.015439 | 122.9929 | -0.063695 | 0.10537 | -0.038995 | 0.18571 | -0.46546 | -0.051609 | -0.028527 | -0.053875 | 0.41158 | 0.13529 | -0.067549 | 123.0028 | 122.9484 | 123.1731 | 67.4391 | -123.1564 | 122.9358 | 123.1227 | 122.9198 | 67.4427 | -123.4528
3040.7969 | 123.1705 | -67.5934 | 55.4581 | -0.0029761 | 0.02982 | -0.0014615 | 0.052867 | -0.0088692 | 0.12831 | -0.0074779 | -0.0041211 | -0.00076913 | 0.054613 | 0.045258 | 0.055317 | 55.4407 | -0.11764 | -67.6159 | 55.4506 | 55.3916 | 55.6117 | -67.735 | -67.5944 | -0.11411 | -67.6198 | 55.3653 | 55.5659 | 55.3768 | -68.0268 | -0.1416 | -0.007448 | 123.0341 | -0.022494 | 0.11911 | -0.06646 | 0.15367 | -0.43341 | -0.09281 | -0.001062 | -0.02641 | 0.407 | 0.10782 | -0.081278 | 123.044 | 122.985 | 123.2051 | 67.4757 | -123.1931 | 122.9586 | 123.1593 | 122.9702 | 67.4793 | -123.4849
3041.7969 | 123.1659 | -67.598 | 55.4672 | -0.010607 | 0.029179 | -0.0014615 | 0.052654 | -0.0086556 | 0.1281 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054399 | 0.045258 | 0.055317 | 55.4407 | -0.12222 | -67.6296 | 55.4552 | 55.4008 | 55.6163 | -67.735 | -67.5807 | -0.11869 | -67.6198 | 55.3653 | 55.5659 | 55.3402 | -68.0268 | -0.13702 | -0.012025 | 123.0387 | -0.031652 | 0.10537 | -0.066457 | 0.14909 | -0.42884 | -0.10196 | 0.017251 | -0.021833 | 0.407 | 0.098667 | -0.12706 | 123.0532 | 122.9987 | 123.2143 | 67.4757 | -123.2022 | 122.9632 | 123.1639 | 122.9381 | 67.4793 | -123.494
3042.7969 | 123.2071 | -67.5797 | 55.4489 | -0.018238 | 0.029179 | -0.0014615 | 0.053295 | -0.0088692 | 0.1281 | -0.0074779 | -0.0043347 | -0.00076913 | 0.054826 | 0.045044 | 0.055531 | 55.4316 | -0.12222 | -67.625 | 55.4506 | 55.4008 | 55.6163 | -67.7304 | -67.5899 | -0.11411 | -67.6152 | 55.3698 | 55.5659 | 55.3768 | -68.0268 | -0.15075 | 0.001707 | 123.0112 | -0.045384 | 0.10537 | -0.048147 | 0.1674 | -0.44715 | -0.079077 | -0.010216 | -0.035564 | 0.41158 | 0.11698 | -0.072123 | 123.0303 | 122.9804 | 123.196 | 67.4574 | -123.1793 | 122.9495 | 123.1455 | 122.9564 | 67.4655 | -123.4757
3043.7969 | 123.1567 | -67.5934 | 55.4535 | -0.0029761 | 0.028966 | -0.0016753 | 0.052654 | -0.0084418 | 0.12724 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054399 | 0.045472 | 0.055317 | 55.4316 | -0.11306 | -67.6205 | 55.4598 | 55.387 | 55.6072 | -67.7304 | -67.5899 | -0.11869 | -67.6244 | 55.3653 | 55.5613 | 55.3493 | -68.0222 | -0.13702 | 0.006287 | 123.025 | -0.027072 | 0.10995 | -0.066461 | 0.15367 | -0.42884 | -0.088232 | 0.003517 | -0.030988 | 0.39785 | 0.10782 | -0.10417 | 123.0532 | 122.9804 | 123.2005 | 67.4803 | -123.1839 | 122.9586 | 123.1547 | 122.9427 | 67.4747 | -123.4757
3044.7969 | 123.2574 | -67.5476 | 55.4855 | -0.010607 | 0.029607 | -0.0012479 | 0.052867 | -0.0086556 | 0.12746 | 0.015414 | -0.0045483 | -0.00055553 | 0.054826 | 0.044831 | 0.055103 | 55.4316 | -0.11306 | -67.625 | 55.4552 | 55.4008 | 55.6209 | -67.7304 | -67.5899 | -0.12327 | -67.6244 | 55.3653 | 55.5613 | 55.3631 | -68.0268 | -0.1828 | -0.030336 | 122.9792 | -0.077428 | 0.10537 | -0.084768 | 0.13536 | -0.47919 | -0.12028 | -0.04226 | -0.076765 | 0.40243 | 0.075777 | -0.12248 | 123.0028 | 122.9484 | 123.1685 | 67.4345 | -123.2159 | 122.9129 | 123.1089 | 122.9107 | 67.4243 | -123.5123
3045.7969 | 123.1522 | -67.598 | 55.4581 | 0.0046549 | 0.028966 | -0.0016753 | 0.053081 | -0.0086556 | 0.1281 | 0.015414 | -0.0045483 | -0.00076913 | 0.054826 | 0.045258 | 0.055531 | 55.4316 | -0.11306 | -67.6205 | 55.4506 | 55.387 | 55.6163 | -67.7304 | -67.599 | -0.12327 | -67.6152 | 55.3698 | 55.5613 | 55.3768 | -68.0268 | -0.13244 | -0.007448 | 123.0296 | -0.022495 | 0.10995 | -0.071039 | 0.15825 | -0.42884 | -0.088232 | -0.001064 | -0.017254 | 0.41158 | 0.10324 | -0.081278 | 123.0486 | 122.985 | 123.2143 | 67.4849 | -123.1885 | 122.9678 | 123.1593 | 122.9748 | 67.4747 | -123.4849
3046.7969 | 123.2849 | -67.5705 | 55.4352 | -0.010607 | 0.029179 | -0.0014615 | 0.052654 | -0.0086556 | 0.12788 | 0.00015261 | -0.0039075 | -0.00076913 | 0.05504 | 0.045258 | 0.055317 | 55.427 | -0.11764 | -67.6113 | 55.4552 | 55.4008 | 55.6163 | -67.7304 | -67.5853 | -0.11869 | -67.629 | 55.3607 | 55.5567 | 55.3447 | -68.0268 | -0.15991 | 0.020018 | 122.9975 | -0.040804 | 0.1191 | -0.034414 | 0.18113 | -0.4563 | -0.074501 | -0.014793 | -0.058455 | 0.39785 | 0.12155 | -0.09044 | 123.0257 | 122.9713 | 123.1868 | 67.4529 | -123.1656 | 122.9312 | 123.1272 | 122.9152 | 67.4518 | -123.462
3047.7969 | 123.1796 | -67.598 | 55.4764 | 0.0046549 | 0.029393 | -0.0014615 | 0.052867 | -0.0088692 | 0.12746 | -0.015108 | -0.0043347 | -0.00055553 | 0.055254 | 0.045472 | 0.055317 | 55.4362 | -0.11764 | -67.6159 | 55.4506 | 55.387 | 55.6209 | -67.7304 | -67.5899 | -0.12327 | -67.6244 | 55.3698 | 55.5613 | 55.3493 | -68.0314 | -0.13244 | -0.025758 | 123.0341 | -0.017917 | 0.11453 | -0.089349 | 0.14451 | -0.43342 | -0.10654 | 0.008094 | -0.026411 | 0.40701 | 0.084933 | -0.12706 | 123.0486 | 122.985 | 123.2189 | 67.4803 | -123.2068 | 122.9678 | 123.1593 | 122.9473 | 67.4747 | -123.5078
3048.7969 | 123.2437 | -67.5659 | 55.4352 | -0.0029761 | 0.029607 | -0.0016753 | 0.053295 | -0.0086556 | 0.12746 | -0.0074779 | -0.0043347 | -0.00098273 | 0.054399 | 0.045472 | 0.055317 | 55.4362 | -0.11764 | -67.6067 | 55.446 | 55.3916 | 55.6209 | -67.7396 | -67.5853 | -0.12327 | -67.6198 | 55.3698 | 55.5613 | 55.3676 | -68.0268 | -0.17364 | 0.010861 | 123.0021 | -0.040804 | 0.13284 | -0.043572 | 0.18571 | -0.46088 | -0.065344 | -0.019371 | -0.053876 | 0.407 | 0.12613 | -0.067547 | 123.012 | 122.9575 | 123.1868 | 67.4483 | -123.1747 | 122.9358 | 123.1272 | 122.9336 | 67.4427 | -123.462
3049.7969 | 123.2025 | -67.5705 | 55.4947 | -0.0029761 | 0.029179 | -0.0012479 | 0.053081 | -0.0086556 | 0.12788 | 0.00015261 | -0.0039075 | -0.00076913 | 0.054826 | 0.044831 | 0.055317 | 55.4362 | -0.11764 | -67.6113 | 55.4552 | 55.3916 | 55.6117 | -67.7167 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5522 | 55.3722 | -68.036 | -0.14617 | -0.039491 | 123.0067 | -0.040804 | 0.10537 | -0.10308 | 0.11705 | -0.46546 | -0.12943 | -0.019371 | -0.049298 | 0.41616 | 0.057465 | -0.12248 | 123.0257 | 122.9621 | 123.1822 | 67.4529 | -123.2114 | 122.9358 | 123.1227 | 122.9427 | 67.4518 | -123.5306
3050.7969 | 123.262 | -67.543 | 55.4581 | -0.0029761 | 0.029179 | -0.0016753 | 0.053081 | -0.0088692 | 0.12746 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054613 | 0.045044 | 0.055317 | 55.4362 | -0.12222 | -67.6021 | 55.446 | 55.3916 | 55.6117 | -67.7304 | -67.5944 | -0.12327 | -67.6244 | 55.3653 | 55.5567 | 55.3493 | -68.0314 | -0.18737 | -0.012027 | 122.9792 | -0.059113 | 0.12826 | -0.06646 | 0.15367 | -0.48835 | -0.09281 | -0.051416 | -0.081342 | 0.40701 | 0.098665 | -0.10875 | 122.9891 | 122.9346 | 123.1548 | 67.4208 | -123.1885 | 122.9083 | 123.0998 | 122.8923 | 67.4198 | -123.4894
3051.7969 | 123.2483 | -67.5568 | 55.4123 | -0.018238 | 0.029393 | -0.0018889 | 0.053081 | -0.0084418 | 0.12788 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054613 | 0.045258 | 0.05489 | 55.4362 | -0.12222 | -67.6067 | 55.4506 | 55.3916 | 55.6163 | -67.7258 | -67.5899 | -0.11869 | -67.6198 | 55.3607 | 55.5567 | 55.3676 | -68.0314 | -0.16906 | 0.038329 | 122.9929 | -0.049959 | 0.1191 | -0.020683 | 0.20402 | -0.47461 | -0.051612 | -0.033104 | -0.063031 | 0.41158 | 0.14444 | -0.044658 | 123.0074 | 122.9484 | 123.1731 | 67.4345 | -123.1381 | 122.9174 | 123.1135 | 122.9244 | 67.4381 | -123.4437
3052.7969 | 123.2254 | -67.598 | 55.4672 | -0.010607 | 0.029607 | -0.0014615 | 0.052867 | -0.0084418 | 0.12788 | -0.0074779 | -0.0043347 | -0.00034193 | 0.054399 | 0.045044 | 0.05489 | 55.4362 | -0.11306 | -67.6205 | 55.446 | 55.3962 | 55.6117 | -67.7304 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3539 | -68.0314 | -0.13244 | -0.021182 | 123.0341 | -0.022495 | 0.10995 | -0.071036 | 0.14451 | -0.43342 | -0.10196 | 0.008094 | -0.021833 | 0.41158 | 0.08951 | -0.11333 | 123.044 | 122.9941 | 123.2097 | 67.4849 | -123.1976 | 122.9632 | 123.1547 | 122.9519 | 67.4793 | -123.4986
3053.7969 | 123.2254 | -67.5476 | 55.4535 | -0.010607 | 0.029179 | -0.0012479 | 0.052867 | -0.0084418 | 0.12767 | 0.0077831 | -0.0041211 | -0.00076913 | 0.05504 | 0.045258 | 0.055103 | 55.4316 | -0.12222 | -67.6113 | 55.4415 | 55.3779 | 55.6117 | -67.7212 | -67.5899 | -0.11869 | -67.6106 | 55.3698 | 55.5705 | 55.3631 | -68.0314 | -0.17364 | -0.012027 | 122.9792 | -0.063693 | 0.10995 | -0.075619 | 0.15824 | -0.48377 | -0.083654 | -0.04226 | -0.063029 | 0.42074 | 0.11698 | -0.090436 | 122.9891 | 122.9255 | 123.1593 | 67.4254 | -123.1747 | 122.9174 | 123.1181 | 122.9107 | 67.4289 | -123.4849
3054.8125 | 123.1567 | -67.5842 | 55.5176 | -0.0029761 | 0.028752 | -0.0014615 | 0.052867 | -0.0086556 | 0.1281 | 0.015414 | -0.0043347 | -0.00098273 | 0.054613 | 0.045258 | 0.055103 | 55.4316 | -0.11764 | -67.6159 | 55.4506 | 55.4008 | 55.6163 | -67.7304 | -67.5853 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3539 | -68.036 | -0.14617 | -0.066957 | 123.0158 | -0.031649 | 0.11453 | -0.11681 | 0.098736 | -0.45173 | -0.15232 | -0.00106 | -0.035565 | 0.41616 | 0.039156 | -0.16368 | 123.0348 | 122.985 | 123.2005 | 67.4666 | -123.248 | 122.9495 | 123.141 | 122.9381 | 67.4655 | -123.5535
3055.7969 | 123.2071 | -67.5613 | 55.4352 | -0.0029761 | 0.029179 | -0.0014615 | 0.052867 | -0.0088692 | 0.12788 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.045044 | 0.055103 | 55.4362 | -0.11764 | -67.6159 | 55.4506 | 55.3962 | 55.6163 | -67.7258 | -67.5899 | -0.11869 | -67.6061 | 55.3653 | 55.5659 | 55.3585 | -68.0268 | -0.16448 | 0.01544 | 122.9975 | -0.054538 | 0.10995 | -0.038993 | 0.18113 | -0.46546 | -0.069922 | -0.028527 | -0.044718 | 0.42074 | 0.13071 | -0.076705 | 123.012 | 122.9575 | 123.1777 | 67.4437 | -123.161 | 122.9266 | 123.1272 | 122.9198 | 67.4427 | -123.462
3056.7969 | 123.2483 | -67.5568 | 55.4626 | -0.010607 | 0.028966 | -0.0012479 | 0.053081 | -0.0084418 | 0.1281 | 0.00015261 | -0.0039075 | -0.00055553 | 0.05504 | 0.045258 | 0.055317 | 55.4362 | -0.11764 | -67.6205 | 55.4506 | 55.3916 | 55.6209 | -67.735 | -67.5944 | -0.12784 | -67.6244 | 55.3698 | 55.5567 | 55.3539 | -68.0314 | -0.17822 | -0.012025 | 122.9929 | -0.063693 | 0.11453 | -0.071037 | 0.15825 | -0.47461 | -0.092809 | -0.037683 | -0.067609 | 0.40701 | 0.094088 | -0.10875 | 123.0074 | 122.9484 | 123.1777 | 67.4391 | -123.1976 | 122.9266 | 123.1135 | 122.9107 | 67.4289 | -123.494
3057.7969 | 123.2437 | -67.5568 | 55.4443 | -0.0029761 | 0.029179 | -0.0016753 | 0.053081 | -0.0086556 | 0.12788 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054826 | 0.045258 | 0.05489 | 55.4362 | -0.12222 | -67.6067 | 55.446 | 55.3962 | 55.6209 | -67.7258 | -67.5853 | -0.11411 | -67.6061 | 55.3653 | 55.5613 | 55.3402 | -68.0268 | -0.16906 | 0.001706 | 122.9929 | -0.049959 | 0.1191 | -0.048148 | 0.17656 | -0.47003 | -0.079077 | -0.028526 | -0.049295 | 0.42074 | 0.11698 | -0.10417 | 123.0028 | 122.953 | 123.1777 | 67.4345 | -123.1702 | 122.922 | 123.1181 | 122.8969 | 67.4427 | -123.4711
3058.7969 | 123.1155 | -67.598 | 55.5267 | 0.012286 | 0.028966 | -0.0014615 | 0.052654 | -0.0088692 | 0.12767 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054613 | 0.045472 | 0.055103 | 55.4316 | -0.11764 | -67.6113 | 55.4552 | 55.3962 | 55.6163 | -67.7304 | -67.5853 | -0.12784 | -67.6244 | 55.3653 | 55.5567 | 55.3631 | -68.036 | -0.13244 | -0.071534 | 123.0296 | -0.013339 | 0.1191 | -0.13054 | 0.089581 | -0.438 | -0.16147 | 0.012672 | -0.026411 | 0.41158 | 0.030001 | -0.16368 | 123.0532 | 122.9941 | 123.2143 | 67.4803 | -123.2571 | 122.9632 | 123.1547 | 122.961 | 67.4701 | -123.5627
3059.7969 | 123.2071 | -67.5659 | 55.4855 | 0.0046549 | 0.029179 | -0.0016753 | 0.053081 | -0.0086556 | 0.12724 | 0.00015261 | -0.0036937 | -0.00034193 | 0.054613 | 0.045472 | 0.055103 | 55.4362 | -0.11764 | -67.6205 | 55.446 | 55.3916 | 55.6117 | -67.7212 | -67.5944 | -0.12327 | -67.6198 | 55.3698 | 55.5522 | 55.3539 | -68.0268 | -0.15533 | -0.039493 | 123.0021 | -0.054538 | 0.10079 | -0.093926 | 0.1262 | -0.46088 | -0.1157 | -0.028528 | -0.053876 | 0.407 | 0.06662 | -0.13164 | 123.012 | 122.9575 | 123.1777 | 67.4483 | -123.2068 | 122.9358 | 123.1181 | 122.9198 | 67.4427 | -123.5123
3060.7969 | 123.2849 | -67.5476 | 55.4718 | 0.0046549 | 0.029179 | -0.0016753 | 0.053295 | -0.0086556 | 0.12746 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.045044 | 0.055103 | 55.4362 | -0.11764 | -67.6159 | 55.446 | 55.3962 | 55.6117 | -67.735 | -67.5944 | -0.12327 | -67.6198 | 55.3653 | 55.5659 | 55.3676 | -68.0314 | -0.18738 | -0.02576 | 122.9838 | -0.068271 | 0.11911 | -0.075614 | 0.13993 | -0.48377 | -0.10654 | -0.046839 | -0.072187 | 0.41158 | 0.094089 | -0.10417 | 122.9936 | 122.9438 | 123.1593 | 67.43 | -123.2068 | 122.9129 | 123.1135 | 122.9152 | 67.4243 | -123.5032
3061.7969 | 123.2574 | -67.5476 | 55.4718 | 0.0046549 | 0.028966 | -0.0014615 | 0.052867 | -0.0086556 | 0.12746 | 0.0077831 | -0.0045483 | -0.00055553 | 0.054613 | 0.045258 | 0.055103 | 55.4362 | -0.11764 | -67.6067 | 55.4415 | 55.3916 | 55.6117 | -67.7212 | -67.5899 | -0.11869 | -67.6244 | 55.3744 | 55.5567 | 55.3631 | -68.0222 | -0.17364 | -0.030338 | 122.9838 | -0.059115 | 0.11452 | -0.080193 | 0.13993 | -0.47461 | -0.097386 | -0.04226 | -0.076765 | 0.39785 | 0.084932 | -0.10875 | 122.9891 | 122.9392 | 123.1593 | 67.43 | -123.193 | 122.922 | 123.1043 | 122.9107 | 67.4289 | -123.494
3062.7969 | 123.2666 | -67.5293 | 55.4672 | 0.0046549 | 0.028966 | -0.0012479 | 0.052867 | -0.0090828 | 0.12767 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054399 | 0.045258 | 0.055103 | 55.4316 | -0.11764 | -67.6205 | 55.446 | 55.3779 | 55.6163 | -67.7304 | -67.5853 | -0.12327 | -67.6244 | 55.3607 | 55.5613 | 55.3722 | -68.0222 | -0.20111 | -0.021182 | 122.9609 | -0.091159 | 0.10995 | -0.089352 | 0.14909 | -0.49292 | -0.10654 | -0.055992 | -0.095075 | 0.39785 | 0.094088 | -0.095012 | 122.9753 | 122.9072 | 123.1456 | 67.4117 | -123.1976 | 122.89 | 123.0906 | 122.9015 | 67.406 | -123.4894
3063.7969 | 123.2483 | -67.543 | 55.4672 | -0.0029761 | 0.028966 | -0.0014615 | 0.053081 | -0.0084418 | 0.12746 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.045472 | 0.055103 | 55.4407 | -0.12222 | -67.6205 | 55.4506 | 55.3779 | 55.6209 | -67.7258 | -67.5899 | -0.11411 | -67.6152 | 55.3698 | 55.5567 | 55.3539 | -68.036 | -0.18279 | -0.016603 | 122.9838 | -0.077426 | 0.10537 | -0.089352 | 0.15367 | -0.49293 | -0.097387 | -0.046837 | -0.072185 | 0.42074 | 0.08951 | -0.11333 | 122.9937 | 122.9209 | 123.1639 | 67.4208 | -123.193 | 122.9129 | 123.0998 | 122.8969 | 67.4289 | -123.5032
3064.7969 | 123.1796 | -67.6025 | 55.4947 | -0.0029761 | 0.028966 | -0.0012479 | 0.052867 | -0.0086556 | 0.12746 | 0.00015261 | -0.0041211 | -0.00055553 | 0.05504 | 0.045044 | 0.055103 | 55.4362 | -0.11764 | -67.625 | 55.446 | 55.3962 | 55.6163 | -67.7396 | -67.5944 | -0.12327 | -67.6198 | 55.3653 | 55.5659 | 55.3905 | -68.0314 | -0.13702 | -0.048648 | 123.0387 | -0.022496 | 0.11453 | -0.098502 | 0.12162 | -0.42884 | -0.12943 | 0.008093 | -0.017255 | 0.41158 | 0.071201 | -0.10416 | 123.0486 | 122.9987 | 123.2189 | 67.4849 | -123.2343 | 122.9678 | 123.1684 | 122.9931 | 67.4793 | -123.5261
3065.7969 | 123.2529 | -67.543 | 55.4443 | -0.0029761 | 0.028966 | -0.0014615 | 0.053081 | -0.0088692 | 0.12724 | 0.0077831 | -0.0039075 | -0.00034193 | 0.054826 | 0.045258 | 0.05489 | 55.4407 | -0.11764 | -67.625 | 55.4506 | 55.387 | 55.6117 | -67.735 | -67.5853 | -0.11869 | -67.6152 | 55.3698 | 55.5613 | 55.3447 | -68.036 | -0.19195 | 0.006285 | 122.9838 | -0.082005 | 0.10995 | -0.057306 | 0.1674 | -0.49293 | -0.074499 | -0.042259 | -0.072185 | 0.42074 | 0.11698 | -0.099595 | 122.9937 | 122.9301 | 123.1548 | 67.4254 | -123.1793 | 122.9129 | 123.1043 | 122.8878 | 67.4243 | -123.4803
3066.7969 | 123.2071 | -67.5476 | 55.4993 | 0.012286 | 0.028752 | -0.0016753 | 0.053081 | -0.0088692 | 0.12746 | 0.00015261 | -0.0043347 | -0.00055553 | 0.05504 | 0.045258 | 0.055531 | 55.4407 | -0.12222 | -67.625 | 55.446 | 55.4008 | 55.6072 | -67.7304 | -67.5807 | -0.12327 | -67.6198 | 55.3653 | 55.5613 | 55.3402 | -68.0268 | -0.1828 | -0.053226 | 122.9884 | -0.077428 | 0.10537 | -0.098501 | 0.10789 | -0.47919 | -0.13401 | -0.033103 | -0.072187 | 0.407 | 0.062044 | -0.15911 | 122.9936 | 122.9484 | 123.1548 | 67.4254 | -123.2297 | 122.9129 | 123.1089 | 122.8878 | 67.4243 | -123.5261
3067.7969 | 123.2391 | -67.543 | 55.4626 | 0.0046549 | 0.028966 | -0.0014615 | 0.053295 | -0.0086556 | 0.12767 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054399 | 0.045258 | 0.055103 | 55.4453 | -0.11764 | -67.6159 | 55.4506 | 55.3962 | 55.6163 | -67.735 | -67.5853 | -0.11411 | -67.6152 | 55.3653 | 55.5613 | 55.3768 | -68.0222 | -0.19195 | -0.012025 | 122.9884 | -0.072848 | 0.11911 | -0.066458 | 0.15367 | -0.47919 | -0.097387 | -0.042259 | -0.072185 | 0.407 | 0.098666 | -0.085855 | 122.9937 | 122.9392 | 123.1593 | 67.4254 | -123.1976 | 122.9083 | 123.1043 | 122.9198 | 67.4289 | -123.4849
3068.7969 | 123.143 | -67.5247 | 55.4993 | -0.0029761 | 0.028752 | -0.0014615 | 0.052867 | -0.0086556 | 0.12767 | 0.015414 | -0.0041211 | -0.00076913 | 0.055254 | 0.045685 | 0.054676 | 55.4316 | -0.11306 | -67.6067 | 55.4506 | 55.3962 | 55.6163 | -67.7304 | -67.5853 | -0.12327 | -67.6152 | 55.3607 | 55.5522 | 55.3722 | -68.0222 | -0.20568 | -0.048647 | 122.9563 | -0.082003 | 0.12368 | -0.10308 | 0.11705 | -0.4975 | -0.13859 | -0.06057 | -0.090496 | 0.407 | 0.052887 | -0.12706 | 122.9753 | 122.9209 | 123.141 | 67.4117 | -123.2297 | 122.8854 | 123.0769 | 122.8969 | 67.4015 | -123.5215
3069.7969 | 123.1567 | -67.5797 | 55.4626 | -0.010607 | 0.028966 | -0.0016753 | 0.053295 | -0.0088692 | 0.12767 | 0.00015261 | -0.0039075 | -0.00034193 | 0.054826 | 0.045472 | 0.055103 | 55.4316 | -0.11306 | -67.6205 | 55.4506 | 55.3962 | 55.6072 | -67.7396 | -67.5761 | -0.11869 | -67.6152 | 55.3698 | 55.5613 | 55.3585 | -68.0268 | -0.15991 | -0.012025 | 123.0112 | -0.040805 | 0.11911 | -0.066458 | 0.14451 | -0.44715 | -0.092809 | 0.00352 | -0.035564 | 0.41158 | 0.098666 | -0.10417 | 123.0303 | 122.9758 | 123.1868 | 67.4666 | -123.2022 | 122.9495 | 123.141 | 122.9381 | 67.461 | -123.4894
3070.7969 | 123.1613 | -67.5613 | 55.4993 | 0.0046549 | 0.028752 | -0.0016753 | 0.052867 | -0.0090828 | 0.12767 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054613 | 0.045258 | 0.055317 | 55.4316 | -0.11764 | -67.6159 | 55.4415 | 55.4008 | 55.6072 | -67.735 | -67.5899 | -0.12327 | -67.6198 | 55.3698 | 55.5613 | 55.3631 | -68.0314 | -0.17364 | -0.057804 | 122.9929 | -0.054538 | 0.11911 | -0.098501 | 0.10789 | -0.47004 | -0.12943 | -0.028527 | -0.058454 | 0.41158 | 0.062044 | -0.13621 | 123.0028 | 122.9621 | 123.1685 | 67.4437 | -123.2343 | 122.9312 | 123.1227 | 122.9244 | 67.4381 | -123.5306
3071.7969 | 123.2254 | -67.5568 | 55.4901 | -0.0029761 | 0.028966 | -0.0010343 | 0.052867 | -0.0088692 | 0.12746 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054826 | 0.045258 | 0.055317 | 55.4362 | -0.11764 | -67.625 | 55.4506 | 55.3916 | 55.6026 | -67.7258 | -67.5899 | -0.12327 | -67.629 | 55.3744 | 55.5567 | 55.3585 | -68.0268 | -0.16906 | -0.039491 | 122.9929 | -0.068272 | 0.10079 | -0.098503 | 0.11247 | -0.47003 | -0.1157 | -0.033104 | -0.072188 | 0.39785 | 0.066622 | -0.13164 | 123.0074 | 122.9484 | 123.1593 | 67.4391 | -123.2159 | 122.9312 | 123.1135 | 122.9152 | 67.4335 | -123.5169
3072.8594 | 123.1201 | -67.5751 | 55.4535 | -0.0029761 | 0.028538 | -0.0012479 | 0.052867 | -0.0086556 | 0.12767 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054613 | 0.045044 | 0.055103 | 55.4362 | -0.11306 | -67.6159 | 55.446 | 55.4008 | 55.6209 | -67.7396 | -67.5853 | -0.12327 | -67.6198 | 55.3607 | 55.5567 | 55.3768 | -68.0268 | -0.16449 | -0.007449 | 123.0112 | -0.040805 | 0.12368 | -0.052724 | 0.1674 | -0.45172 | -0.092811 | -0.010216 | -0.044721 | 0.407 | 0.10324 | -0.0767 | 123.0211 | 122.9758 | 123.196 | 67.462 | -123.1931 | 122.9358 | 123.1318 | 122.9519 | 67.4518 | -123.4803
3073.7969 | 123.2071 | -67.5568 | 55.4855 | -0.010607 | 0.029179 | -0.0012479 | 0.052654 | -0.0088692 | 0.12724 | 0.0077831 | -0.0045483 | -0.00055553 | 0.054613 | 0.045472 | 0.055317 | 55.4316 | -0.11306 | -67.6113 | 55.446 | 55.3916 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6152 | 55.3698 | 55.5613 | 55.3585 | -68.0268 | -0.17364 | -0.039493 | 122.9884 | -0.054537 | 0.1191 | -0.093926 | 0.13078 | -0.47003 | -0.1157 | -0.033104 | -0.058452 | 0.41158 | 0.075777 | -0.12706 | 123.0028 | 122.9484 | 123.1731 | 67.4437 | -123.2159 | 122.9266 | 123.1181 | 122.9152 | 67.4335 | -123.5123
3074.7969 | 123.2986 | -67.5476 | 55.4398 | -0.0029761 | 0.028966 | -0.0014615 | 0.053295 | -0.0088692 | 0.12767 | -0.0074779 | -0.0045483 | -0.00055553 | 0.054613 | 0.045258 | 0.055103 | 55.427 | -0.11306 | -67.6159 | 55.446 | 55.3962 | 55.6117 | -67.7258 | -67.5899 | -0.11869 | -67.6244 | 55.3698 | 55.5613 | 55.3631 | -68.0222 | -0.17822 | 0.006284 | 122.9746 | -0.068271 | 0.10995 | -0.04357 | 0.17198 | -0.47461 | -0.069921 | -0.04226 | -0.076765 | 0.39785 | 0.12155 | -0.076703 | 122.9936 | 122.9438 | 123.1593 | 67.4345 | -123.1656 | 122.9174 | 123.1089 | 122.9107 | 67.4289 | -123.462
3075.7969 | 123.1567 | -67.5568 | 55.4855 | -0.0029761 | 0.028538 | -0.0014615 | 0.053081 | -0.0084418 | 0.12724 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.045472 | 0.055317 | 55.4316 | -0.11764 | -67.6159 | 55.4506 | 55.3962 | 55.6209 | -67.735 | -67.599 | -0.12327 | -67.6152 | 55.3561 | 55.5567 | 55.3676 | -68.0268 | -0.17822 | -0.034914 | 122.9884 | -0.059115 | 0.11911 | -0.089347 | 0.13536 | -0.47003 | -0.12943 | -0.042262 | -0.058452 | 0.41158 | 0.071199 | -0.1179 | 123.0074 | 122.953 | 123.1777 | 67.4391 | -123.2205 | 122.9129 | 123.1135 | 122.9244 | 67.4335 | -123.5123
3076.7969 | 123.1522 | -67.5934 | 55.4993 | -0.010607 | 0.028752 | -0.0016753 | 0.052867 | -0.0086556 | 0.12746 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.045472 | 0.055103 | 55.4316 | -0.11764 | -67.6113 | 55.4506 | 55.3962 | 55.6163 | -67.7258 | -67.5899 | -0.12327 | -67.6198 | 55.3607 | 55.5567 | 55.3585 | -68.0268 | -0.13244 | -0.048647 | 123.025 | -0.017916 | 0.11453 | -0.10308 | 0.11705 | -0.43341 | -0.13859 | 0.003517 | -0.02641 | 0.407 | 0.057466 | -0.14079 | 123.044 | 122.9896 | 123.2097 | 67.4757 | -123.2251 | 122.9541 | 123.1501 | 122.9519 | 67.4701 | -123.5261
3077.7969 | 123.0881 | -67.5613 | 55.5084 | 0.012286 | 0.028752 | -0.0012479 | 0.052867 | -0.0088692 | 0.12724 | 0.0077831 | -0.0043347 | -0.00076913 | 0.05504 | 0.045685 | 0.055103 | 55.4362 | -0.11764 | -67.6159 | 55.4506 | 55.4053 | 55.6255 | -67.7304 | -67.5944 | -0.11869 | -67.6106 | 55.3607 | 55.5567 | 55.3631 | -68.0222 | -0.16906 | -0.057802 | 122.9975 | -0.054538 | 0.11453 | -0.10308 | 0.11705 | -0.46088 | -0.14774 | -0.033106 | -0.049296 | 0.41158 | 0.048311 | -0.14537 | 123.012 | 122.9667 | 123.1868 | 67.4437 | -123.2388 | 122.922 | 123.1181 | 122.9244 | 67.4427 | -123.5306
3078.7969 | 123.1522 | -67.6025 | 55.4718 | -0.0029761 | 0.028752 | -0.0018889 | 0.053081 | -0.0084418 | 0.12746 | -0.0074779 | -0.0043347 | -0.00055553 | 0.054826 | 0.045258 | 0.05489 | 55.4362 | -0.10848 | -67.6113 | 55.4552 | 55.3825 | 55.6209 | -67.735 | -67.5899 | -0.12327 | -67.6152 | 55.3653 | 55.5613 | 55.3676 | -68.036 | -0.13244 | -0.016603 | 123.0387 | -0.008761 | 0.12368 | -0.089351 | 0.14909 | -0.43342 | -0.10654 | 0.012672 | -0.012676 | 0.42074 | 0.08951 | -0.10417 | 123.0577 | 122.985 | 123.2234 | 67.4941 | -123.2068 | 122.9678 | 123.1639 | 122.9702 | 67.4793 | -123.5078
3079.7969 | 123.1796 | -67.5888 | 55.5038 | 0.0046549 | 0.028752 | -0.0016753 | 0.052654 | -0.0086556 | 0.12724 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054613 | 0.045472 | 0.055317 | 55.4362 | -0.11764 | -67.6159 | 55.4506 | 55.3825 | 55.6163 | -67.7396 | -67.5899 | -0.11411 | -67.6152 | 55.3653 | 55.5567 | 55.3539 | -68.0268 | -0.15076 | -0.053224 | 123.025 | -0.027072 | 0.12368 | -0.12139 | 0.11247 | -0.43799 | -0.13859 | -0.001061 | -0.026409 | 0.41158 | 0.052889 | -0.14995 | 123.0394 | 122.9713 | 123.2051 | 67.4712 | -123.2434 | 122.9541 | 123.1455 | 122.9427 | 67.4747 | -123.5306
3080.7969 | 123.1567 | -67.5797 | 55.481 | 0.0046549 | 0.028752 | -0.0016753 | 0.05244 | -0.0084418 | 0.12703 | 0.015414 | -0.0041211 | -0.00076913 | 0.054826 | 0.045258 | 0.055103 | 55.4316 | -0.12222 | -67.6205 | 55.4552 | 55.4008 | 55.6163 | -67.7396 | -67.5944 | -0.11869 | -67.6152 | 55.3698 | 55.5567 | 55.3539 | -68.0314 | -0.15991 | -0.025758 | 123.0112 | -0.040805 | 0.11911 | -0.08019 | 0.13536 | -0.45173 | -0.11112 | -0.014795 | -0.035564 | 0.41616 | 0.075777 | -0.12706 | 123.0349 | 122.9804 | 123.196 | 67.4574 | -123.2205 | 122.9495 | 123.1364 | 122.9335 | 67.461 | -123.5123
3081.7969 | 123.1705 | -67.5613 | 55.5038 | 0.0046549 | 0.028538 | -0.0014615 | 0.05244 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00076913 | 0.05504 | 0.045472 | 0.055103 | 55.4362 | -0.11764 | -67.6205 | 55.446 | 55.3962 | 55.6209 | -67.7441 | -67.5899 | -0.11869 | -67.6152 | 55.3653 | 55.5613 | 55.3676 | -68.036 | -0.1828 | -0.057803 | 122.9975 | -0.059116 | 0.12368 | -0.10766 | 0.11705 | -0.47462 | -0.13859 | -0.028527 | -0.053875 | 0.42074 | 0.057467 | -0.13621 | 123.0074 | 122.9575 | 123.1822 | 67.4437 | -123.248 | 122.9266 | 123.1227 | 122.929 | 67.4427 | -123.5398
3082.7969 | 123.1476 | -67.5888 | 55.4535 | 0.012286 | 0.028752 | -0.0016753 | 0.052654 | -0.0088692 | 0.12767 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.045685 | 0.055103 | 55.427 | -0.11306 | -67.6205 | 55.4506 | 55.3825 | 55.6163 | -67.7304 | -67.5899 | -0.12784 | -67.6244 | 55.3653 | 55.5522 | 55.3631 | -68.036 | -0.1416 | -0.00287 | 123.0158 | -0.03165 | 0.10995 | -0.07104 | 0.16282 | -0.44715 | -0.088232 | -0.001061 | -0.035566 | 0.41158 | 0.098664 | -0.090436 | 123.0394 | 122.9713 | 123.2051 | 67.4757 | -123.1839 | 122.9541 | 123.141 | 122.9519 | 67.461 | -123.4894
3083.7969 | 123.1796 | -67.5751 | 55.4764 | -0.010607 | 0.028538 | -0.0016753 | 0.05244 | -0.0084418 | 0.12746 | 0.00015261 | -0.0043347 | -0.00012813 | 0.054826 | 0.045472 | 0.055317 | 55.4362 | -0.11764 | -67.625 | 55.446 | 55.3962 | 55.6163 | -67.735 | -67.5853 | -0.12327 | -67.6198 | 55.3653 | 55.5613 | 55.3676 | -68.0268 | -0.15991 | -0.030337 | 123.0112 | -0.049962 | 0.10995 | -0.080191 | 0.13994 | -0.45172 | -0.11112 | -0.010216 | -0.044721 | 0.407 | 0.084933 | -0.10874 | 123.0211 | 122.9713 | 123.1914 | 67.4574 | -123.2114 | 122.9403 | 123.1364 | 122.9427 | 67.4518 | -123.5032
3084.7969 | 123.2162 | -67.5659 | 55.4352 | -0.0029761 | 0.028752 | -0.0016753 | 0.053295 | -0.0088692 | 0.12746 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.045472 | 0.05489 | 55.4407 | -0.11764 | -67.6205 | 55.4598 | 55.3962 | 55.6163 | -67.7258 | -67.5853 | -0.12327 | -67.6152 | 55.3515 | 55.5522 | 55.3493 | -68.0268 | -0.15991 | 0.024597 | 123.0067 | -0.054538 | 0.10537 | -0.038993 | 0.18113 | -0.46088 | -0.083658 | -0.019371 | -0.049297 | 0.41158 | 0.11697 | -0.085862 | 123.0257 | 122.9621 | 123.1822 | 67.4483 | -123.161 | 122.9174 | 123.1181 | 122.9152 | 67.4427 | -123.462
3085.7969 | 123.1705 | -67.5568 | 55.4855 | -0.0029761 | 0.028325 | -0.0014615 | 0.05244 | -0.0086556 | 0.12746 | 0.0077831 | -0.0045483 | -0.00076913 | 0.054613 | 0.045258 | 0.055317 | 55.4362 | -0.11764 | -67.625 | 55.4552 | 55.387 | 55.6163 | -67.7396 | -67.599 | -0.11411 | -67.6152 | 55.3653 | 55.5613 | 55.3722 | -68.0268 | -0.1828 | -0.030336 | 122.9929 | -0.068272 | 0.11453 | -0.098505 | 0.13078 | -0.47003 | -0.12028 | -0.042262 | -0.058452 | 0.41158 | 0.075777 | -0.11332 | 123.012 | 122.9438 | 123.1731 | 67.4391 | -123.2251 | 122.922 | 123.1181 | 122.929 | 67.4427 | -123.5123
3086.7969 | 123.1384 | -67.598 | 55.4626 | -0.0029761 | 0.028538 | -0.0012479 | 0.053081 | -0.0086556 | 0.12703 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054613 | 0.045685 | 0.055317 | 55.427 | -0.12222 | -67.6067 | 55.4552 | 55.3962 | 55.6163 | -67.7304 | -67.5944 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3676 | -68.0314 | -0.13244 | -0.007447 | 123.025 | -0.008761 | 0.12368 | -0.066458 | 0.15367 | -0.43342 | -0.097387 | 0.003515 | -0.021833 | 0.41158 | 0.094088 | -0.095012 | 123.0532 | 122.9941 | 123.2143 | 67.4757 | -123.193 | 122.9632 | 123.1547 | 122.9656 | 67.4793 | -123.494
3087.7969 | 123.1338 | -67.5888 | 55.4855 | -0.0029761 | 0.028538 | -0.0016753 | 0.053081 | -0.0088692 | 0.12724 | -0.0074779 | -0.0043347 | -0.00055553 | 0.054613 | 0.045472 | 0.055317 | 55.4362 | -0.11764 | -67.6205 | 55.4552 | 55.387 | 55.6117 | -67.7304 | -67.5899 | -0.11869 | -67.6198 | 55.3698 | 55.5567 | 55.3768 | -68.0268 | -0.1416 | -0.030336 | 123.025 | -0.03165 | 0.10995 | -0.098505 | 0.1262 | -0.43799 | -0.1157 | -0.001061 | -0.030988 | 0.407 | 0.071199 | -0.10874 | 123.044 | 122.9758 | 123.2005 | 67.4712 | -123.2159 | 122.9586 | 123.1455 | 122.9656 | 67.4701 | -123.5123
3088.7969 | 123.2483 | -67.5797 | 55.4489 | -0.0029761 | 0.028325 | -0.0012479 | 0.052654 | -0.0088692 | 0.12703 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054826 | 0.045472 | 0.055103 | 55.4362 | -0.11764 | -67.6205 | 55.4506 | 55.4008 | 55.6026 | -67.7258 | -67.5899 | -0.11411 | -67.6106 | 55.3653 | 55.5613 | 55.3493 | -68.0268 | -0.14617 | 0.001707 | 123.0158 | -0.040805 | 0.10537 | -0.048147 | 0.15366 | -0.44715 | -0.083655 | -0.010216 | -0.030985 | 0.41616 | 0.1124 | -0.099595 | 123.0303 | 122.9804 | 123.1822 | 67.462 | -123.1747 | 122.9449 | 123.141 | 122.929 | 67.4655 | -123.4757
3089.7969 | 123.2117 | -67.5568 | 55.4718 | 0.0046549 | 0.028325 | -0.0016753 | 0.053081 | -0.0088692 | 0.12724 | 0.015414 | -0.0041211 | -0.00055553 | 0.054613 | 0.045472 | 0.055317 | 55.427 | -0.11764 | -67.6159 | 55.446 | 55.3825 | 55.6072 | -67.7258 | -67.5899 | -0.12327 | -67.6152 | 55.3653 | 55.5659 | 55.3585 | -68.0314 | -0.16906 | -0.02576 | 122.9838 | -0.059115 | 0.10995 | -0.089351 | 0.13536 | -0.47461 | -0.10654 | -0.033104 | -0.058452 | 0.41616 | 0.094089 | -0.11333 | 123.0028 | 122.9392 | 123.1639 | 67.4391 | -123.1976 | 122.922 | 123.1227 | 122.9152 | 67.4335 | -123.5032
3090.7969 | 123.2162 | -67.5842 | 55.4443 | -0.0029761 | 0.028325 | -0.0014615 | 0.052867 | -0.0084418 | 0.12724 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054613 | 0.045258 | 0.055103 | 55.4316 | -0.11764 | -67.6067 | 55.446 | 55.4053 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6198 | 55.3561 | 55.5613 | 55.3722 | -68.0268 | -0.14617 | 0.001706 | 123.0158 | -0.022493 | 0.12368 | -0.03899 | 0.17198 | -0.44257 | -0.088234 | -0.005638 | -0.035565 | 0.407 | 0.11698 | -0.072124 | 123.0303 | 122.9896 | 123.2005 | 67.4666 | -123.1747 | 122.9403 | 123.1455 | 122.9564 | 67.461 | -123.4711
3091.7969 | 123.1522 | -67.5888 | 55.4718 | 0.0046549 | 0.028325 | -0.0012479 | 0.052654 | -0.0086556 | 0.12703 | -0.015108 | -0.0043347 | -0.00055553 | 0.054613 | 0.045685 | 0.055317 | 55.4407 | -0.11306 | -67.6159 | 55.446 | 55.3916 | 55.6163 | -67.7304 | -67.5853 | -0.11869 | -67.6152 | 55.3653 | 55.5567 | 55.3859 | -68.0268 | -0.1416 | -0.02576 | 123.0296 | -0.027072 | 0.11453 | -0.080193 | 0.14451 | -0.43799 | -0.10654 | 0.003517 | -0.026409 | 0.41158 | 0.084932 | -0.085854 | 123.0348 | 122.9804 | 123.2051 | 67.4757 | -123.2022 | 122.9541 | 123.1455 | 122.9748 | 67.4701 | -123.4986
3092.8594 | 123.2071 | -67.5705 | 55.4489 | -0.0029761 | 0.028111 | -0.0016753 | 0.053295 | -0.0086556 | 0.12767 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054185 | 0.045685 | 0.055317 | 55.4316 | -0.11306 | -67.6205 | 55.446 | 55.3916 | 55.6117 | -67.7304 | -67.5807 | -0.11869 | -67.6106 | 55.3561 | 55.5522 | 55.3539 | -68.0268 | -0.15991 | -0.002872 | 123.0021 | -0.04996 | 0.10995 | -0.057305 | 0.16282 | -0.4563 | -0.092812 | -0.010214 | -0.04014 | 0.41616 | 0.10324 | -0.095016 | 123.0165 | 122.9621 | 123.1822 | 67.4574 | -123.1793 | 122.9266 | 123.1227 | 122.9244 | 67.4518 | -123.4757
3093.7969 | 123.2895 | -67.5659 | 55.426 | -0.010607 | 0.028752 | -0.0014615 | 0.052654 | -0.0086556 | 0.12724 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054613 | 0.045258 | 0.055317 | 55.4362 | -0.1039 | -67.6113 | 55.4506 | 55.3962 | 55.6209 | -67.7304 | -67.5899 | -0.13242 | -67.6152 | 55.3607 | 55.5476 | 55.3722 | -68.0268 | -0.16449 | 0.024596 | 123.0021 | -0.045382 | 0.1191 | -0.029837 | 0.19487 | -0.46088 | -0.065345 | -0.023949 | -0.049297 | 0.41158 | 0.12155 | -0.053813 | 123.0165 | 122.9621 | 123.1868 | 67.462 | -123.1564 | 122.9266 | 123.1135 | 122.9381 | 67.4335 | -123.4528
3094.8125 | 123.143 | -67.5842 | 55.4947 | -0.0029761 | 0.028325 | -0.0014615 | 0.052654 | -0.0086556 | 0.12724 | -0.0074779 | -0.0045483 | -0.00076913 | 0.054613 | 0.045472 | 0.055103 | 55.4316 | -0.11764 | -67.6067 | 55.4552 | 55.3962 | 55.6163 | -67.7304 | -67.5807 | -0.11411 | -67.6198 | 55.3653 | 55.5567 | 55.3722 | -68.0268 | -0.14617 | -0.039491 | 123.0158 | -0.022493 | 0.12368 | -0.098502 | 0.12162 | -0.44257 | -0.12943 | 0.003519 | -0.035565 | 0.407 | 0.062044 | -0.12248 | 123.0394 | 122.9804 | 123.2005 | 67.4666 | -123.2251 | 122.9495 | 123.141 | 122.9564 | 67.4701 | -123.5215
3095.7969 | 123.2666 | -67.5568 | 55.4306 | -0.010607 | 0.028538 | -0.0010343 | 0.052654 | -0.0084418 | 0.12724 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045258 | 0.055317 | 55.4407 | -0.11764 | -67.6159 | 55.446 | 55.3916 | 55.6163 | -67.7258 | -67.5853 | -0.12327 | -67.6198 | 55.3653 | 55.5567 | 55.3722 | -68.0268 | -0.16906 | 0.015439 | 122.9975 | -0.059115 | 0.10995 | -0.038994 | 0.18571 | -0.47003 | -0.065344 | -0.028526 | -0.063031 | 0.407 | 0.12613 | -0.058391 | 123.0028 | 122.9484 | 123.1731 | 67.4391 | -123.1564 | 122.922 | 123.1135 | 122.929 | 67.4335 | -123.4574
3096.8594 | 123.2666 | -67.5476 | 55.4398 | -0.010607 | 0.028111 | -0.0012479 | 0.052654 | -0.0086556 | 0.12724 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.045258 | 0.05489 | 55.4362 | -0.11306 | -67.6113 | 55.4506 | 55.3825 | 55.6209 | -67.7258 | -67.5944 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3676 | -68.0222 | -0.17822 | 0.010863 | 122.9838 | -0.063693 | 0.11453 | -0.057307 | 0.18114 | -0.47461 | -0.074499 | -0.046839 | -0.072187 | 0.40243 | 0.11698 | -0.072124 | 122.9982 | 122.9301 | 123.1685 | 67.4345 | -123.1656 | 122.9129 | 123.1043 | 122.9152 | 67.4289 | -123.462
3097.7969 | 123.262 | -67.5613 | 55.4398 | -0.0029761 | 0.028538 | -0.0012479 | 0.053081 | -0.0086556 | 0.12703 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054826 | 0.045258 | 0.055103 | 55.4316 | -0.11764 | -67.6021 | 55.4415 | 55.3916 | 55.6117 | -67.7258 | -67.5899 | -0.11869 | -67.6106 | 55.3698 | 55.5567 | 55.3631 | -68.0314 | -0.16448 | 0.001706 | 122.9929 | -0.040803 | 0.12368 | -0.048149 | 0.17198 | -0.47004 | -0.069921 | -0.028527 | -0.049296 | 0.42074 | 0.11698 | -0.076703 | 123.0028 | 122.9529 | 123.1731 | 67.4437 | -123.1656 | 122.9312 | 123.1181 | 122.9244 | 67.4427 | -123.4711
3098.7969 | 123.2346 | -67.5613 | 55.481 | -0.0029761 | 0.028111 | -0.0014615 | 0.053081 | -0.0088692 | 0.12724 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054399 | 0.045258 | 0.055103 | 55.4362 | -0.12222 | -67.5884 | 55.4415 | 55.387 | 55.6117 | -67.735 | -67.5853 | -0.12327 | -67.6198 | 55.3653 | 55.5613 | 55.3447 | -68.0268 | -0.17364 | -0.039493 | 122.9975 | -0.027068 | 0.14657 | -0.093927 | 0.13078 | -0.46546 | -0.1157 | -0.023949 | -0.058454 | 0.407 | 0.080355 | -0.13622 | 123.0028 | 122.9484 | 123.1731 | 67.4391 | -123.2159 | 122.9266 | 123.1227 | 122.9061 | 67.4381 | -123.5078
3099.8125 | 123.2483 | -67.543 | 55.4169 | 0.0046549 | 0.028325 | -0.0014615 | 0.053295 | -0.0084418 | 0.12703 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054826 | 0.045472 | 0.05489 | 55.4316 | -0.11306 | -67.6021 | 55.446 | 55.387 | 55.6163 | -67.7304 | -67.5853 | -0.11869 | -67.6198 | 55.3698 | 55.5567 | 55.3722 | -68.0222 | -0.18737 | 0.029172 | 122.9746 | -0.059113 | 0.12826 | -0.02984 | 0.19944 | -0.47919 | -0.047033 | -0.042259 | -0.076764 | 0.40243 | 0.13986 | -0.044658 | 122.9891 | 122.9301 | 123.1593 | 67.43 | -123.1473 | 122.9129 | 123.0998 | 122.9152 | 67.4243 | -123.4391
3100.7969 | 123.262 | -67.5568 | 55.4626 | -0.0029761 | 0.028538 | -0.0012479 | 0.053295 | -0.0084418 | 0.12703 | 0.015414 | -0.0043347 | -0.00034193 | 0.054826 | 0.045258 | 0.05489 | 55.4316 | -0.12222 | -67.5976 | 55.4415 | 55.4053 | 55.6163 | -67.7258 | -67.5853 | -0.12327 | -67.6152 | 55.3653 | 55.5659 | 55.4043 | -68.036 | -0.16906 | -0.021182 | 122.9884 | -0.040802 | 0.12826 | -0.0573 | 0.15367 | -0.47919 | -0.097387 | -0.028526 | -0.058452 | 0.42074 | 0.10325 | -0.058383 | 122.9982 | 122.9621 | 123.1731 | 67.4345 | -123.1885 | 122.922 | 123.1227 | 122.961 | 67.4335 | -123.4986
3101.7969 | 123.2574 | -67.5339 | 55.4764 | 0.0046549 | 0.028325 | -0.0012479 | 0.052867 | -0.0088692 | 0.12724 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.045685 | 0.055103 | 55.4362 | -0.10848 | -67.6021 | 55.446 | 55.387 | 55.6163 | -67.7304 | -67.5899 | -0.12784 | -67.6198 | 55.3653 | 55.5613 | 55.3814 | -68.0314 | -0.19653 | -0.030337 | 122.97 | -0.068268 | 0.12826 | -0.089349 | 0.13994 | -0.4975 | -0.11112 | -0.055992 | -0.085919 | 0.41158 | 0.084933 | -0.095009 | 122.9799 | 122.9209 | 123.1502 | 67.4254 | -123.2068 | 122.8991 | 123.0952 | 122.9152 | 67.406 | -123.5078
3102.7969 | 123.2346 | -67.5476 | 55.4764 | -0.0029761 | 0.028111 | -0.0016753 | 0.053081 | -0.0086556 | 0.12682 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054826 | 0.045899 | 0.05489 | 55.427 | -0.12222 | -67.6113 | 55.4506 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.12327 | -67.6106 | 55.3698 | 55.5659 | 55.3585 | -68.036 | -0.17822 | -0.025758 | 122.9746 | -0.063693 | 0.11453 | -0.080191 | 0.14451 | -0.48835 | -0.10654 | -0.033103 | -0.063029 | 0.42532 | 0.089512 | -0.1179 | 122.9982 | 122.9438 | 123.1685 | 67.4254 | -123.2022 | 122.9174 | 123.1135 | 122.9061 | 67.4243 | -123.5123
3103.7969 | 123.2483 | -67.5568 | 55.4672 | -0.010607 | 0.028325 | -0.0016753 | 0.053081 | -0.0086556 | 0.12703 | 0.015414 | -0.0041211 | -0.00076913 | 0.054399 | 0.045472 | 0.055103 | 55.4362 | -0.11306 | -67.6067 | 55.446 | 55.4053 | 55.63 | -67.7258 | -67.5853 | -0.12327 | -67.6198 | 55.3698 | 55.5659 | 55.3585 | -68.0314 | -0.16906 | -0.021182 | 122.9929 | -0.049959 | 0.1191 | -0.061878 | 0.16283 | -0.47461 | -0.097387 | -0.028526 | -0.063031 | 0.41158 | 0.098667 | -0.10875 | 123.0028 | 122.9621 | 123.1868 | 67.4437 | -123.193 | 122.9266 | 123.1227 | 122.9152 | 67.4335 | -123.4986
3104.8125 | 123.2346 | -67.5659 | 55.4581 | -0.0029761 | 0.028111 | -0.0016753 | 0.052867 | -0.0086556 | 0.12724 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054826 | 0.045472 | 0.05489 | 55.4362 | -0.11764 | -67.6021 | 55.4506 | 55.3962 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6152 | 55.3653 | 55.5659 | 55.3676 | -68.036 | -0.16449 | -0.007448 | 123.0021 | -0.036225 | 0.12826 | -0.061881 | 0.15825 | -0.47004 | -0.09281 | -0.023949 | -0.049297 | 0.42074 | 0.10782 | -0.090435 | 123.0165 | 122.9621 | 123.1822 | 67.4483 | -123.1885 | 122.9312 | 123.1318 | 122.9336 | 67.4427 | -123.494
3105.7969 | 123.262 | -67.5476 | 55.4718 | 0.0046549 | 0.028325 | -0.0012479 | 0.053081 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00055553 | 0.05504 | 0.045472 | 0.055103 | 55.4316 | -0.11764 | -67.6067 | 55.446 | 55.3962 | 55.6163 | -67.7304 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5522 | 55.3676 | -68.0268 | -0.1828 | -0.02576 | 122.9792 | -0.059115 | 0.12368 | -0.075614 | 0.14451 | -0.47919 | -0.10654 | -0.04226 | -0.072187 | 0.407 | 0.080353 | -0.10417 | 122.9936 | 122.9438 | 123.1639 | 67.43 | -123.2022 | 122.9129 | 123.0998 | 122.9152 | 67.4289 | -123.4986
3106.7969 | 123.2071 | -67.5293 | 55.4901 | -0.0029761 | 0.027897 | -0.0012479 | 0.053081 | -0.0086556 | 0.12682 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054399 | 0.046113 | 0.055317 | 55.4362 | -0.11764 | -67.6159 | 55.4598 | 55.3962 | 55.6209 | -67.7258 | -67.5853 | -0.11869 | -67.6198 | 55.3653 | 55.5613 | 55.3722 | -68.0268 | -0.19653 | -0.030334 | 122.9655 | -0.086581 | 0.10995 | -0.093924 | 0.13078 | -0.4975 | -0.12485 | -0.055992 | -0.090497 | 0.407 | 0.0712 | -0.1179 | 122.9891 | 122.9255 | 123.1502 | 67.4117 | -123.2159 | 122.8946 | 123.0906 | 122.9015 | 67.4106 | -123.5169
3107.7969 | 123.2529 | -67.5247 | 55.4626 | 0.012286 | 0.028325 | -0.0012479 | 0.053081 | -0.0086556 | 0.12703 | 0.015414 | -0.0041211 | -0.00034193 | 0.054613 | 0.045899 | 0.055103 | 55.427 | -0.11764 | -67.6205 | 55.4552 | 55.3825 | 55.6209 | -67.7304 | -67.5853 | -0.11411 | -67.6152 | 55.3653 | 55.5613 | 55.3768 | -68.0222 | -0.20568 | -0.007447 | 122.9517 | -0.095737 | 0.10995 | -0.080195 | 0.15825 | -0.4975 | -0.097387 | -0.06057 | -0.090496 | 0.407 | 0.098666 | -0.085855 | 122.9799 | 122.9072 | 123.1456 | 67.4071 | -123.193 | 122.89 | 123.086 | 122.9015 | 67.4106 | -123.4849
3108.8594 | 123.1842 | -67.5613 | 55.4855 | 0.012286 | 0.028111 | -0.0014615 | 0.052867 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045685 | 0.05489 | 55.4407 | -0.11764 | -67.6159 | 55.446 | 55.4008 | 55.6163 | -67.7258 | -67.5853 | -0.11869 | -67.6244 | 55.3607 | 55.5613 | 55.3539 | -68.0314 | -0.16448 | -0.039493 | 123.0021 | -0.054538 | 0.10995 | -0.084768 | 0.13078 | -0.47004 | -0.12485 | -0.023949 | -0.063032 | 0.40701 | 0.075777 | -0.13164 | 123.0074 | 122.9621 | 123.1777 | 67.4437 | -123.2114 | 122.922 | 123.1227 | 122.9152 | 67.4427 | -123.5169
3109.8125 | 123.2529 | -67.543 | 55.4581 | -0.0029761 | 0.028111 | -0.0016753 | 0.053081 | -0.0086556 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045472 | 0.05489 | 55.4407 | -0.11764 | -67.6021 | 55.4506 | 55.4053 | 55.6163 | -67.7304 | -67.5853 | -0.12327 | -67.6152 | 55.3653 | 55.5522 | 55.3859 | -68.0268 | -0.18737 | -0.007448 | 122.9838 | -0.059113 | 0.12826 | -0.052723 | 0.15825 | -0.48377 | -0.09281 | -0.042259 | -0.072185 | 0.41158 | 0.094086 | -0.072121 | 122.9937 | 122.9484 | 123.1593 | 67.4254 | -123.1885 | 122.9083 | 123.0952 | 122.929 | 67.4198 | -123.4849
3110.7969 | 123.1567 | -67.5659 | 55.4993 | -0.0029761 | 0.027897 | -0.0012479 | 0.052654 | -0.0088692 | 0.12724 | 0.015414 | -0.0041211 | -0.00098273 | 0.054826 | 0.045472 | 0.055103 | 55.4316 | -0.11764 | -67.6067 | 55.446 | 55.3962 | 55.6209 | -67.7304 | -67.5899 | -0.11869 | -67.6152 | 55.3653 | 55.5613 | 55.3585 | -68.0268 | -0.16449 | -0.053226 | 122.9975 | -0.040804 | 0.12368 | -0.10308 | 0.12163 | -0.46088 | -0.13401 | -0.023949 | -0.049297 | 0.41158 | 0.062044 | -0.14079 | 123.012 | 122.9621 | 123.1868 | 67.4483 | -123.2297 | 122.9312 | 123.1272 | 122.9244 | 67.4472 | -123.5261
3111.7969 | 123.1247 | -67.5659 | 55.513 | 0.0046549 | 0.027897 | -0.0012479 | 0.052654 | -0.0086556 | 0.12703 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054826 | 0.045685 | 0.055317 | 55.4362 | -0.12222 | -67.6067 | 55.4415 | 55.4008 | 55.6163 | -67.735 | -67.5853 | -0.11869 | -67.6152 | 55.3698 | 55.5613 | 55.3814 | -68.0268 | -0.16907 | -0.071536 | 123.0021 | -0.040804 | 0.12826 | -0.11223 | 0.10331 | -0.46088 | -0.14316 | -0.019371 | -0.049297 | 0.41158 | 0.048312 | -0.13163 | 123.0074 | 122.9667 | 123.1822 | 67.4437 | -123.248 | 122.9358 | 123.1272 | 122.9473 | 67.4472 | -123.5398
3112.7969 | 123.175 | -67.5797 | 55.4672 | 0.0046549 | 0.027897 | -0.0014615 | 0.05244 | -0.0086556 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045685 | 0.055317 | 55.4316 | -0.11306 | -67.6067 | 55.4506 | 55.3962 | 55.6209 | -67.735 | -67.5853 | -0.12327 | -67.6106 | 55.3698 | 55.5522 | 55.3722 | -68.0268 | -0.15533 | -0.016603 | 123.0112 | -0.027071 | 0.12826 | -0.071036 | 0.15367 | -0.44715 | -0.097387 | -0.005638 | -0.030985 | 0.41616 | 0.084931 | -0.095012 | 123.0303 | 122.9758 | 123.2005 | 67.4666 | -123.2022 | 122.9495 | 123.1318 | 122.9519 | 67.4564 | -123.494
3113.7969 | 123.1842 | -67.5888 | 55.4764 | -0.0029761 | 0.028111 | -0.0014615 | 0.052654 | -0.0088692 | 0.12682 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.045472 | 0.055103 | 55.427 | -0.11764 | -67.6067 | 55.4506 | 55.4008 | 55.6209 | -67.7304 | -67.5899 | -0.11411 | -67.6152 | 55.3698 | 55.5567 | 55.3768 | -68.0268 | -0.1416 | -0.025758 | 123.0158 | -0.017916 | 0.12368 | -0.075612 | 0.14451 | -0.43799 | -0.10654 | -0.001061 | -0.026409 | 0.41158 | 0.080355 | -0.099588 | 123.0394 | 122.9896 | 123.2097 | 67.4712 | -123.2068 | 122.9586 | 123.1455 | 122.9656 | 67.4747 | -123.5032
3114.8125 | 123.1659 | -67.5568 | 55.4901 | -0.0029761 | 0.027897 | -0.0012479 | 0.052654 | -0.0088692 | 0.12703 | 0.00015261 | -0.0045483 | -0.00012813 | 0.054613 | 0.045685 | 0.05489 | 55.4362 | -0.11764 | -67.6067 | 55.446 | 55.3962 | 55.6255 | -67.7304 | -67.5807 | -0.11869 | -67.6152 | 55.3653 | 55.5567 | 55.3814 | -68.0268 | -0.17364 | -0.04407 | 122.9929 | -0.049959 | 0.12368 | -0.093924 | 0.13536 | -0.47003 | -0.12485 | -0.023947 | -0.058452 | 0.41158 | 0.066622 | -0.10874 | 123.0028 | 122.953 | 123.1822 | 67.4391 | -123.2205 | 122.922 | 123.1135 | 122.9381 | 67.4381 | -123.5169
3115.7969 | 123.1613 | -67.5934 | 55.4535 | -0.018238 | 0.027897 | -0.0012479 | 0.053081 | -0.0088692 | 0.12703 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.045472 | 0.055103 | 55.4362 | -0.11764 | -67.6205 | 55.4552 | 55.4008 | 55.6209 | -67.7441 | -67.5899 | -0.11869 | -67.6106 | 55.3653 | 55.5613 | 55.3951 | -68.0268 | -0.15076 | 0.001708 | 123.0296 | -0.027072 | 0.12368 | -0.052724 | 0.1674 | -0.43341 | -0.088232 | 0.003517 | -0.017252 | 0.41616 | 0.10782 | -0.058386 | 123.0486 | 122.9942 | 123.2143 | 67.4757 | -123.1976 | 122.9586 | 123.1547 | 122.9885 | 67.4747 | -123.4803
3116.7969 | 123.1018 | -67.6071 | 55.4535 | -0.0029761 | 0.028325 | -0.0018889 | 0.052654 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054613 | 0.045685 | 0.055103 | 55.4316 | -0.10848 | -67.6067 | 55.446 | 55.4008 | 55.6209 | -67.735 | -67.5807 | -0.12327 | -67.6152 | 55.3698 | 55.5613 | 55.3631 | -68.0268 | -0.12787 | -0.007449 | 123.0387 | 0.000395 | 0.12826 | -0.052724 | 0.1674 | -0.41968 | -0.083654 | 0.026407 | -0.008098 | 0.41158 | 0.10782 | -0.090436 | 123.0532 | 123.0079 | 123.228 | 67.4986 | -123.1885 | 122.977 | 123.1684 | 122.9702 | 67.4839 | -123.4803
3117.7969 | 123.1018 | -67.5797 | 55.4901 | -0.0029761 | 0.027897 | -0.0014615 | 0.052867 | -0.0086556 | 0.12682 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.046113 | 0.05489 | 55.4362 | -0.11764 | -67.6205 | 55.4598 | 55.3916 | 55.63 | -67.7396 | -67.5853 | -0.11869 | -67.6106 | 55.3698 | 55.5567 | 55.3768 | -68.0314 | -0.15991 | -0.030334 | 123.0158 | -0.040805 | 0.11911 | -0.098503 | 0.13994 | -0.45173 | -0.12028 | -0.005638 | -0.030985 | 0.42074 | 0.066622 | -0.11332 | 123.0394 | 122.9713 | 123.2097 | 67.462 | -123.2297 | 122.9495 | 123.1364 | 122.9564 | 67.461 | -123.5215
3118.7969 | 123.23 | -67.5613 | 55.4123 | 0.012286 | 0.027684 | -0.0016753 | 0.052654 | -0.0086556 | 0.12724 | -0.0074779 | -0.0041211 | -0.00076913 | 0.054613 | 0.045899 | 0.05489 | 55.427 | -0.12222 | -67.6067 | 55.446 | 55.4008 | 55.6163 | -67.735 | -67.5853 | -0.11869 | -67.6152 | 55.3698 | 55.5567 | 55.3585 | -68.0314 | -0.17364 | 0.03375 | 122.9884 | -0.045382 | 0.12826 | -0.011525 | 0.20402 | -0.47004 | -0.042455 | -0.023949 | -0.053875 | 0.41616 | 0.14444 | -0.053816 | 123.0074 | 122.9621 | 123.1777 | 67.4391 | -123.1473 | 122.9312 | 123.1181 | 122.9198 | 67.4427 | -123.4437
3119.7969 | 123.2758 | -67.5385 | 55.4398 | 0.0046549 | 0.027897 | -0.0018889 | 0.052867 | -0.0088692 | 0.12703 | 0.015414 | -0.0043347 | -0.00034193 | 0.054399 | 0.045899 | 0.055317 | 55.4224 | -0.11764 | -67.6159 | 55.446 | 55.3779 | 55.6117 | -67.7304 | -67.5944 | -0.11869 | -67.6152 | 55.3607 | 55.5522 | 55.3676 | -68.0314 | -0.19195 | 0.006284 | 122.9609 | -0.077426 | 0.11453 | -0.061886 | 0.17198 | -0.49292 | -0.079078 | -0.055994 | -0.076763 | 0.41616 | 0.1124 | -0.072124 | 122.9845 | 122.9163 | 123.1502 | 67.4208 | -123.1702 | 122.8991 | 123.0906 | 122.9061 | 67.4198 | -123.4711
3120.7969 | 123.1338 | -67.6071 | 55.4764 | -0.0029761 | 0.027684 | -0.0012479 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.045899 | 0.055103 | 55.4362 | -0.11764 | -67.6159 | 55.446 | 55.3825 | 55.6209 | -67.735 | -67.5807 | -0.11411 | -67.6244 | 55.3698 | 55.5567 | 55.3631 | -68.0314 | -0.12787 | -0.030337 | 123.0433 | -0.008761 | 0.11911 | -0.093928 | 0.14451 | -0.42426 | -0.10654 | 0.026407 | -0.017255 | 0.40701 | 0.080355 | -0.11332 | 123.0532 | 122.9896 | 123.228 | 67.4895 | -123.2114 | 122.977 | 123.1639 | 122.9702 | 67.493 | -123.5078
3121.7969 | 123.1384 | -67.6025 | 55.4398 | -0.0029761 | 0.02747 | -0.0014615 | 0.052867 | -0.0088692 | 0.12703 | -0.015108 | -0.0043347 | -0.00055553 | 0.054399 | 0.045685 | 0.055317 | 55.4316 | -0.11764 | -67.6159 | 55.446 | 55.4099 | 55.6209 | -67.7396 | -67.5853 | -0.11869 | -67.6106 | 55.3698 | 55.5659 | 55.3905 | -68.0314 | -0.13702 | 0.006284 | 123.0341 | -0.013339 | 0.12368 | -0.029833 | 0.18114 | -0.42884 | -0.069921 | 0.01725 | -0.008097 | 0.42074 | 0.12613 | -0.049231 | 123.0486 | 123.0125 | 123.2234 | 67.4849 | -123.1793 | 122.9724 | 123.1684 | 122.9931 | 67.4839 | -123.4711
3122.7969 | 123.1934 | -67.6025 | 55.4535 | 0.0046549 | 0.027897 | -0.0014615 | 0.052654 | -0.0086556 | 0.12703 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054826 | 0.045258 | 0.054676 | 55.4316 | -0.11764 | -67.6113 | 55.446 | 55.3916 | 55.6209 | -67.7304 | -67.5853 | -0.12327 | -67.6198 | 55.3698 | 55.5613 | 55.3631 | -68.0176 | -0.12786 | -0.007449 | 123.0341 | -0.008761 | 0.1191 | -0.061882 | 0.1674 | -0.4151 | -0.083654 | 0.01725 | -0.017255 | 0.39785 | 0.10782 | -0.090436 | 123.0486 | 122.9941 | 123.2234 | 67.4849 | -123.1839 | 122.9724 | 123.1639 | 122.9656 | 67.4793 | -123.4711
3123.7969 | 123.0927 | -67.6117 | 55.4672 | -0.0029761 | 0.027684 | -0.0016753 | 0.052867 | -0.0086556 | 0.12703 | -0.015108 | -0.0045483 | -0.00034193 | 0.054399 | 0.046113 | 0.055103 | 55.4362 | -0.12222 | -67.6159 | 55.4415 | 55.3962 | 55.6072 | -67.7396 | -67.5853 | -0.11869 | -67.6106 | 55.3607 | 55.5567 | 55.3722 | -68.0222 | -0.12787 | -0.02576 | 123.0479 | -0.004184 | 0.12368 | -0.071036 | 0.13993 | -0.41053 | -0.10654 | 0.026405 | 0.001058 | 0.41158 | 0.08951 | -0.095012 | 123.0532 | 123.0079 | 123.2189 | 67.4895 | -123.2068 | 122.9724 | 123.1684 | 122.9839 | 67.493 | -123.4894
3124.7969 | 123.262 | -67.5476 | 55.4535 | -0.0029761 | 0.027897 | -0.0012479 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054399 | 0.045685 | 0.05489 | 55.4316 | -0.11764 | -67.6113 | 55.446 | 55.3916 | 55.6117 | -67.735 | -67.5853 | -0.11869 | -67.6198 | 55.3653 | 55.5522 | 55.3814 | -68.0268 | -0.18738 | -0.007449 | 122.9792 | -0.063693 | 0.12368 | -0.061882 | 0.15824 | -0.47919 | -0.088232 | -0.037682 | -0.072187 | 0.407 | 0.098664 | -0.072121 | 122.9936 | 122.9392 | 123.1593 | 67.43 | -123.1885 | 122.9129 | 123.0998 | 122.929 | 67.4289 | -123.4803
3125.7969 | 123.2254 | -67.5613 | 55.426 | -0.010607 | 0.027684 | -0.0012479 | 0.052654 | -0.0086556 | 0.12682 | -0.0074779 | -0.0045483 | -0.00055553 | 0.054613 | 0.045899 | 0.05489 | 55.4316 | -0.12222 | -67.6159 | 55.446 | 55.3916 | 55.6209 | -67.735 | -67.5807 | -0.11411 | -67.6152 | 55.3653 | 55.5613 | 55.3722 | -68.0222 | -0.17364 | 0.020017 | 122.9929 | -0.054538 | 0.11911 | -0.034416 | 0.19487 | -0.46088 | -0.060766 | -0.01937 | -0.053875 | 0.407 | 0.13529 | -0.053813 | 123.0074 | 122.9529 | 123.1822 | 67.4391 | -123.161 | 122.9266 | 123.1227 | 122.9336 | 67.4472 | -123.4482
3126.7969 | 123.2208 | -67.5705 | 55.4581 | -0.0029761 | 0.027684 | -0.0016753 | 0.052867 | -0.0084418 | 0.12682 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054826 | 0.045899 | 0.05489 | 55.4316 | -0.11306 | -67.5976 | 55.446 | 55.387 | 55.6117 | -67.7258 | -67.5807 | -0.11869 | -67.6198 | 55.3607 | 55.5522 | 55.3356 | -68.0314 | -0.15533 | -0.012027 | 123.0021 | -0.027069 | 0.12826 | -0.071039 | 0.15367 | -0.46088 | -0.097389 | -0.010214 | -0.049298 | 0.41158 | 0.094086 | -0.12249 | 123.0165 | 122.9575 | 123.1822 | 67.4574 | -123.1839 | 122.9312 | 123.1227 | 122.9061 | 67.4518 | -123.4894
3127.7969 | 123.1934 | -67.5613 | 55.4489 | -0.010607 | 0.027897 | -0.0012479 | 0.052867 | -0.0090828 | 0.12703 | -0.0074779 | -0.0043347 | -0.00098273 | 0.054399 | 0.045899 | 0.05489 | 55.4407 | -0.11764 | -67.6067 | 55.446 | 55.3916 | 55.6209 | -67.7304 | -67.5807 | -0.12327 | -67.6152 | 55.3698 | 55.5522 | 55.3768 | -68.0268 | -0.16906 | -0.002872 | 123.0021 | -0.045382 | 0.12368 | -0.057305 | 0.17198 | -0.46546 | -0.079077 | -0.01937 | -0.053875 | 0.41158 | 0.10324 | -0.072123 | 123.0074 | 122.9529 | 123.1822 | 67.4437 | -123.1793 | 122.9312 | 123.1135 | 122.9381 | 67.4381 | -123.4757
3128.7969 | 123.1934 | -67.5613 | 55.4398 | 0.0046549 | 0.027897 | -0.0016753 | 0.052654 | -0.0088692 | 0.12724 | 0.00015261 | -0.0045483 | -0.00034193 | 0.054613 | 0.045685 | 0.05489 | 55.427 | -0.11306 | -67.6113 | 55.4506 | 55.387 | 55.6117 | -67.7121 | -67.5853 | -0.11411 | -67.6152 | 55.3607 | 55.5522 | 55.3631 | -68.036 | -0.15075 | 0.010863 | 122.9884 | -0.04996 | 0.10079 | -0.052728 | 0.17198 | -0.47462 | -0.079078 | -0.023949 | -0.053875 | 0.42074 | 0.1124 | -0.076703 | 123.012 | 122.9484 | 123.1731 | 67.4483 | -123.1518 | 122.922 | 123.1135 | 122.9244 | 67.4472 | -123.4757
3129.7969 | 123.2391 | -67.5293 | 55.4764 | 0.0046549 | 0.02747 | -0.0014615 | 0.052867 | -0.0086556 | 0.12746 | 0.00015261 | -0.0045483 | -0.00076913 | 0.054185 | 0.045899 | 0.05489 | 55.4316 | -0.12222 | -67.6021 | 55.4506 | 55.3962 | 55.6117 | -67.7258 | -67.5853 | -0.11411 | -67.6106 | 55.3653 | 55.5613 | 55.3814 | -68.0222 | -0.19653 | -0.025758 | 122.9609 | -0.072846 | 0.12368 | -0.080191 | 0.13536 | -0.49292 | -0.11112 | -0.055992 | -0.081339 | 0.41158 | 0.084933 | -0.095009 | 122.9799 | 122.9255 | 123.141 | 67.4071 | -123.2022 | 122.8946 | 123.0906 | 122.9107 | 67.4152 | -123.4986
3130.7969 | 123.2483 | -67.5659 | 55.426 | 0.0046549 | 0.028111 | -0.0012479 | 0.053081 | -0.0084418 | 0.12682 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054613 | 0.045472 | 0.05489 | 55.4316 | -0.11764 | -67.6113 | 55.4369 | 55.3916 | 55.6163 | -67.7396 | -67.5899 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.3814 | -68.0314 | -0.17364 | 0.010861 | 122.9975 | -0.045382 | 0.12826 | -0.034416 | 0.19029 | -0.46546 | -0.060766 | -0.023949 | -0.044718 | 0.42074 | 0.13071 | -0.044655 | 123.0028 | 122.9575 | 123.1822 | 67.4483 | -123.1656 | 122.9312 | 123.1227 | 122.9473 | 67.4518 | -123.4574
3131.7969 | 123.2437 | -67.5705 | 55.4306 | -0.0029761 | 0.02747 | -0.0014615 | 0.053081 | -0.0088692 | 0.12682 | -0.0074779 | -0.0041211 | -0.00076913 | 0.054826 | 0.045899 | 0.05489 | 55.4407 | -0.11764 | -67.6113 | 55.446 | 55.3962 | 55.6163 | -67.7304 | -67.5807 | -0.12327 | -67.6152 | 55.3698 | 55.5567 | 55.3676 | -68.0314 | -0.15991 | 0.015439 | 123.0112 | -0.040804 | 0.1191 | -0.034415 | 0.18571 | -0.46088 | -0.060766 | -0.010214 | -0.044719 | 0.41616 | 0.12613 | -0.062969 | 123.0165 | 122.9667 | 123.1868 | 67.4529 | -123.161 | 122.9403 | 123.1272 | 122.9381 | 67.4472 | -123.462
3132.7969 | 123.2483 | -67.5659 | 55.4535 | -0.010607 | 0.027897 | -0.0012479 | 0.053295 | -0.0086556 | 0.12724 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054399 | 0.046113 | 0.055103 | 55.4316 | -0.11764 | -67.6113 | 55.4506 | 55.4099 | 55.6163 | -67.7304 | -67.5807 | -0.12327 | -67.6198 | 55.3607 | 55.5567 | 55.3676 | -68.0222 | -0.16449 | -0.00287 | 122.9975 | -0.045382 | 0.1191 | -0.043566 | 0.16282 | -0.4563 | -0.092811 | -0.014792 | -0.053876 | 0.40243 | 0.10324 | -0.085857 | 123.0165 | 122.9758 | 123.1822 | 67.4483 | -123.1839 | 122.9266 | 123.1227 | 122.9336 | 67.4427 | -123.4757
3133.7969 | 123.1979 | -67.5522 | 55.4855 | -0.010607 | 0.027897 | -0.0016753 | 0.052654 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054399 | 0.045685 | 0.05489 | 55.427 | -0.11306 | -67.6067 | 55.446 | 55.4053 | 55.6163 | -67.735 | -67.5899 | -0.11411 | -67.6152 | 55.3653 | 55.5613 | 55.3768 | -68.0268 | -0.1828 | -0.039493 | 122.9792 | -0.054537 | 0.12826 | -0.080189 | 0.13078 | -0.47461 | -0.12028 | -0.037682 | -0.06303 | 0.41158 | 0.075777 | -0.10874 | 122.9982 | 122.9575 | 123.1685 | 67.4391 | -123.2205 | 122.9174 | 123.1135 | 122.929 | 67.4381 | -123.5123
3134.7969 | 123.2117 | -67.5293 | 55.4901 | 0.0046549 | 0.027897 | -0.0018889 | 0.053081 | -0.0088692 | 0.12682 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054185 | 0.045685 | 0.055103 | 55.4362 | -0.12222 | -67.6067 | 55.4506 | 55.3916 | 55.6209 | -67.735 | -67.5899 | -0.12327 | -67.6198 | 55.3653 | 55.5567 | 55.3814 | -68.0314 | -0.20569 | -0.039491 | 122.9655 | -0.077425 | 0.12826 | -0.098503 | 0.13078 | -0.50208 | -0.12485 | -0.06057 | -0.090497 | 0.41158 | 0.066622 | -0.10874 | 122.9799 | 122.9209 | 123.1502 | 67.4071 | -123.2251 | 122.8946 | 123.086 | 122.9107 | 67.406 | -123.5215
3135.7969 | 123.2254 | -67.5797 | 55.4535 | -0.0029761 | 0.027684 | -0.0016753 | 0.052867 | -0.0086556 | 0.12703 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054399 | 0.045899 | 0.055103 | 55.4316 | -0.12222 | -67.6021 | 55.4506 | 55.4099 | 55.6255 | -67.7212 | -67.5853 | -0.11869 | -67.6061 | 55.3561 | 55.5567 | 55.3585 | -68.0176 | -0.14159 | -0.00287 | 123.0112 | -0.022492 | 0.1191 | -0.043566 | 0.17198 | -0.43799 | -0.097389 | -0.005638 | -0.026407 | 0.41158 | 0.10324 | -0.095015 | 123.0303 | 122.9896 | 123.2051 | 67.4574 | -123.1747 | 122.9358 | 123.1364 | 122.9381 | 67.461 | -123.4711
3136.7969 | 123.1979 | -67.5522 | 55.4626 | -0.010607 | 0.02747 | -0.0018889 | 0.053081 | -0.0086556 | 0.12682 | 0.015414 | -0.0041211 | -0.00034193 | 0.054185 | 0.045899 | 0.055103 | 55.4362 | -0.11764 | -67.6067 | 55.446 | 55.3825 | 55.6163 | -67.7258 | -67.5807 | -0.12327 | -67.6152 | 55.3607 | 55.5522 | 55.3722 | -68.0314 | -0.17364 | -0.016604 | 122.9884 | -0.054537 | 0.1191 | -0.080195 | 0.15367 | -0.47919 | -0.10197 | -0.028525 | -0.06303 | 0.41616 | 0.089509 | -0.090434 | 122.9982 | 122.9346 | 123.1685 | 67.4345 | -123.1885 | 122.9129 | 123.1043 | 122.9244 | 67.4289 | -123.494
3137.7969 | 123.1979 | -67.5522 | 55.4443 | -0.010607 | 0.027684 | -0.0014615 | 0.052867 | -0.0086556 | 0.12682 | -0.0074779 | -0.0043347 | -0.00055553 | 0.054185 | 0.046113 | 0.05489 | 55.427 | -0.11764 | -67.6021 | 55.4506 | 55.3916 | 55.6163 | -67.7304 | -67.5761 | -0.11411 | -67.6152 | 55.3653 | 55.5659 | 55.3631 | -68.0314 | -0.17822 | 0.006285 | 122.9792 | -0.049958 | 0.12826 | -0.052727 | 0.17198 | -0.47919 | -0.079077 | -0.023946 | -0.06303 | 0.41616 | 0.12156 | -0.081281 | 123.0028 | 122.9438 | 123.1685 | 67.4345 | -123.1747 | 122.9174 | 123.1181 | 122.9152 | 67.4381 | -123.4757
3138.7969 | 123.2391 | -67.5476 | 55.4764 | 0.0046549 | 0.027897 | -0.0016753 | 0.053081 | -0.0084418 | 0.12703 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054826 | 0.045685 | 0.055103 | 55.4316 | -0.12222 | -67.5976 | 55.446 | 55.387 | 55.6209 | -67.735 | -67.5853 | -0.11869 | -67.6198 | 55.3653 | 55.5522 | 55.3814 | -68.0314 | -0.18738 | -0.030337 | 122.9792 | -0.049958 | 0.13742 | -0.089349 | 0.14451 | -0.48377 | -0.11112 | -0.037682 | -0.072187 | 0.41158 | 0.075776 | -0.095009 | 122.9936 | 122.9346 | 123.1685 | 67.4254 | -123.2114 | 122.9129 | 123.0998 | 122.929 | 67.4289 | -123.5078
3139.7969 | 123.1934 | -67.5339 | 55.4855 | -0.0029761 | 0.027684 | -0.0012479 | 0.052654 | -0.0086556 | 0.12703 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054399 | 0.046113 | 0.05489 | 55.4316 | -0.11764 | -67.6113 | 55.446 | 55.4053 | 55.6163 | -67.7258 | -67.5853 | -0.11869 | -67.6061 | 55.3653 | 55.5476 | 55.3859 | -68.0268 | -0.19195 | -0.039493 | 122.9655 | -0.077425 | 0.11453 | -0.080189 | 0.13078 | -0.49292 | -0.12028 | -0.051414 | -0.072183 | 0.42074 | 0.062041 | -0.099587 | 122.9799 | 122.9392 | 123.1502 | 67.4162 | -123.2114 | 122.8991 | 123.0815 | 122.9198 | 67.4152 | -123.5123
3140.7969 | 123.2666 | -67.5018 | 55.4306 | -0.0029761 | 0.027684 | -0.0014615 | 0.053081 | -0.0088692 | 0.1266 | 0.015414 | -0.0041211 | -0.00076913 | 0.054399 | 0.045899 | 0.055317 | 55.427 | -0.11764 | -67.5976 | 55.446 | 55.4053 | 55.6163 | -67.735 | -67.5807 | -0.11869 | -67.6061 | 55.3561 | 55.5567 | 55.3676 | -68.0222 | -0.23315 | 0.015439 | 122.9288 | -0.095734 | 0.13742 | -0.025257 | 0.18571 | -0.52039 | -0.074501 | -0.078879 | -0.10423 | 0.41616 | 0.12613 | -0.062969 | 122.9479 | 122.9072 | 123.1181 | 67.3842 | -123.1656 | 122.8579 | 123.0586 | 122.8695 | 67.3831 | -123.4528
3141.7969 | 123.2025 | -67.5568 | 55.4581 | 0.0046549 | 0.02747 | -0.0018889 | 0.052867 | -0.0088692 | 0.12639 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054185 | 0.045685 | 0.05489 | 55.4362 | -0.11764 | -67.6021 | 55.446 | 55.3916 | 55.6209 | -67.7258 | -67.5899 | -0.12784 | -67.6198 | 55.3607 | 55.5522 | 55.3768 | -68.0314 | -0.16906 | -0.012027 | 122.9929 | -0.04538 | 0.12368 | -0.06646 | 0.16282 | -0.47461 | -0.097389 | -0.033104 | -0.063031 | 0.41158 | 0.094086 | -0.081278 | 123.0028 | 122.9484 | 123.1777 | 67.4391 | -123.1839 | 122.9174 | 123.1089 | 122.9336 | 67.4289 | -123.4894
3142.7969 | 123.1476 | -67.5842 | 55.513 | 0.0046549 | 0.02747 | -0.0016753 | 0.053081 | -0.0086556 | 0.12703 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054613 | 0.045899 | 0.05489 | 55.427 | -0.11764 | -67.6021 | 55.446 | 55.3962 | 55.6163 | -67.7258 | -67.5853 | -0.11869 | -67.6152 | 55.3653 | 55.5659 | 55.3585 | -68.0314 | -0.1416 | -0.066958 | 123.0112 | -0.017914 | 0.12368 | -0.11681 | 0.10331 | -0.44715 | -0.14774 | -0.00106 | -0.030986 | 0.41616 | 0.052891 | -0.15452 | 123.0303 | 122.9804 | 123.2005 | 67.4666 | -123.2388 | 122.9495 | 123.1501 | 122.9427 | 67.4655 | -123.5444
3143.7969 | 123.2162 | -67.5751 | 55.4581 | 0.012286 | 0.027897 | -0.0016753 | 0.052867 | -0.0088692 | 0.12703 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054613 | 0.045899 | 0.05489 | 55.4362 | -0.11764 | -67.593 | 55.4415 | 55.3916 | 55.6163 | -67.7258 | -67.5899 | -0.11411 | -67.6152 | 55.3607 | 55.5659 | 55.3905 | -68.0314 | -0.15075 | -0.016605 | 123.0112 | -0.017914 | 0.13284 | -0.06646 | 0.15825 | -0.4563 | -0.097389 | -0.014794 | -0.040142 | 0.41616 | 0.10782 | -0.067542 | 123.0165 | 122.9667 | 123.1914 | 67.4574 | -123.1839 | 122.9358 | 123.141 | 122.9656 | 67.461 | -123.4894
3144.7969 | 123.1567 | -67.5705 | 55.5176 | -0.0029761 | 0.027256 | -0.0012479 | 0.05244 | -0.0086556 | 0.12682 | -0.0074779 | -0.0043347 | -0.00034193 | 0.054613 | 0.045899 | 0.055103 | 55.4362 | -0.11764 | -67.5976 | 55.4506 | 55.3916 | 55.6209 | -67.735 | -67.5899 | -0.10953 | -67.6106 | 55.3653 | 55.5567 | 55.3814 | -68.036 | -0.16449 | -0.066957 | 123.0067 | -0.027069 | 0.13742 | -0.12597 | 0.10332 | -0.46546 | -0.15232 | -0.019371 | -0.04014 | 0.42532 | 0.039156 | -0.13621 | 123.0211 | 122.9621 | 123.1914 | 67.4529 | -123.2526 | 122.9358 | 123.1272 | 122.9519 | 67.461 | -123.5535
3145.7969 | 123.2574 | -67.5293 | 55.4581 | 0.0046549 | 0.027256 | -0.0016753 | 0.053295 | -0.0086556 | 0.12682 | 0.00015261 | -0.0045483 | -0.00076913 | 0.054826 | 0.045899 | 0.05489 | 55.4362 | -0.12222 | -67.6021 | 55.4369 | 55.4008 | 55.6117 | -67.7304 | -67.5944 | -0.10495 | -67.6198 | 55.3653 | 55.5567 | 55.3722 | -68.0268 | -0.20111 | -0.021183 | 122.9655 | -0.072846 | 0.12826 | -0.057302 | 0.15367 | -0.4975 | -0.09281 | -0.065149 | -0.090497 | 0.407 | 0.098665 | -0.085857 | 122.9662 | 122.9301 | 123.141 | 67.4071 | -123.1885 | 122.8946 | 123.086 | 122.9015 | 67.4243 | -123.4849
3146.7969 | 123.143 | -67.5751 | 55.4993 | 0.0046549 | 0.027256 | -0.0014615 | 0.052654 | -0.0086556 | 0.12703 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054399 | 0.045899 | 0.05489 | 55.4407 | -0.11764 | -67.6021 | 55.4506 | 55.4053 | 55.6163 | -67.7396 | -67.5807 | -0.11869 | -67.6106 | 55.3561 | 55.5522 | 55.3585 | -68.0268 | -0.16449 | -0.048647 | 123.0158 | -0.02707 | 0.13742 | -0.093922 | 0.11705 | -0.45172 | -0.14317 | -0.005637 | -0.035563 | 0.41616 | 0.052887 | -0.14079 | 123.0257 | 122.9804 | 123.1914 | 67.4574 | -123.2388 | 122.9312 | 123.1272 | 122.9335 | 67.4564 | -123.5261
3147.7969 | 123.2803 | -67.5156 | 55.4535 | -0.0029761 | 0.027256 | -0.0014615 | 0.053081 | -0.0090828 | 0.12682 | 0.00015261 | -0.0045483 | -0.00034193 | 0.054613 | 0.045685 | 0.055103 | 55.4407 | -0.11306 | -67.6067 | 55.446 | 55.4008 | 55.6209 | -67.7212 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5567 | 55.3493 | -68.0222 | -0.20568 | -0.007449 | 122.9563 | -0.091158 | 0.11452 | -0.052724 | 0.1674 | -0.50666 | -0.088232 | -0.074303 | -0.10423 | 0.40243 | 0.10324 | -0.10417 | 122.9616 | 122.9163 | 123.1365 | 67.4025 | -123.1747 | 122.8808 | 123.0723 | 122.8649 | 67.3969 | -123.4757
3148.7969 | 123.2025 | -67.5339 | 55.481 | 0.0046549 | 0.027256 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054613 | 0.046113 | 0.055103 | 55.4316 | -0.12222 | -67.5976 | 55.446 | 55.3962 | 55.6163 | -67.7258 | -67.5853 | -0.11869 | -67.6106 | 55.3607 | 55.5613 | 55.3539 | -68.0222 | -0.19195 | -0.034915 | 122.9655 | -0.06369 | 0.12826 | -0.084769 | 0.13536 | -0.48835 | -0.12028 | -0.051414 | -0.076761 | 0.41158 | 0.080355 | -0.12706 | 122.9799 | 122.9301 | 123.1502 | 67.4117 | -123.2068 | 122.8946 | 123.0952 | 122.8878 | 67.4152 | -123.5032
3149.7969 | 123.1155 | -67.5842 | 55.5038 | 0.012286 | 0.027256 | -0.0012479 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054826 | 0.045899 | 0.055103 | 55.427 | -0.11764 | -67.6021 | 55.4415 | 55.3962 | 55.6163 | -67.7396 | -67.5853 | -0.11411 | -67.6152 | 55.3515 | 55.5613 | 55.3493 | -68.0222 | -0.15533 | -0.062381 | 123.0112 | -0.017914 | 0.13742 | -0.10766 | 0.11247 | -0.43799 | -0.15232 | -0.00106 | -0.030986 | 0.407 | 0.057467 | -0.15453 | 123.0257 | 122.9804 | 123.2005 | 67.4666 | -123.2434 | 122.9358 | 123.1455 | 122.9335 | 67.4701 | -123.5261
3150.7969 | 123.1613 | -67.5797 | 55.4718 | 0.0046549 | 0.02747 | -0.0018889 | 0.05244 | -0.0086556 | 0.1266 | -0.0074779 | -0.0047619 | -0.00012813 | 0.054185 | 0.045899 | 0.055103 | 55.4316 | -0.11764 | -67.6113 | 55.4552 | 55.4053 | 55.63 | -67.7304 | -67.5899 | -0.11869 | -67.6061 | 55.3607 | 55.5522 | 55.3768 | -68.0176 | -0.15075 | -0.016603 | 123.0112 | -0.031649 | 0.1191 | -0.066456 | 0.15825 | -0.43799 | -0.11112 | -0.010216 | -0.026407 | 0.41158 | 0.080353 | -0.095011 | 123.0349 | 122.985 | 123.2097 | 67.462 | -123.2022 | 122.9403 | 123.1318 | 122.9564 | 67.461 | -123.4894
3151.7969 | 123.23 | -67.5156 | 55.481 | -0.0029761 | 0.02747 | -0.0016753 | 0.053081 | -0.0086556 | 0.1266 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054399 | 0.046113 | 0.055103 | 55.4362 | -0.11764 | -67.6067 | 55.446 | 55.3962 | 55.6255 | -67.7258 | -67.5853 | -0.12327 | -67.6106 | 55.3653 | 55.5567 | 55.3585 | -68.0222 | -0.21026 | -0.034915 | 122.9517 | -0.091158 | 0.1191 | -0.084769 | 0.14451 | -0.50666 | -0.1157 | -0.069725 | -0.095072 | 0.41158 | 0.075777 | -0.12248 | 122.9616 | 122.9118 | 123.141 | 67.3979 | -123.2068 | 122.8808 | 123.0723 | 122.874 | 67.3923 | -123.5032
3152.8594 | 123.2346 | -67.5568 | 55.4535 | -0.0029761 | 0.027256 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | -0.0041211 | -0.00055553 | 0.05504 | 0.045899 | 0.055103 | 55.4362 | -0.12222 | -67.6021 | 55.4369 | 55.4053 | 55.6209 | -67.7258 | -67.5899 | -0.11869 | -67.6106 | 55.3698 | 55.5522 | 55.3676 | -68.0222 | -0.16906 | -0.016605 | 122.9929 | -0.04538 | 0.12368 | -0.048145 | 0.1674 | -0.46546 | -0.083654 | -0.033104 | -0.053873 | 0.41158 | 0.098664 | -0.085857 | 122.9936 | 122.9621 | 123.1777 | 67.4345 | -123.1793 | 122.9266 | 123.1089 | 122.9244 | 67.4381 | -123.4757
3153.7969 | 123.1247 | -67.5705 | 55.4855 | -0.0029761 | 0.027256 | -0.0014615 | 0.052654 | -0.0086556 | 0.12682 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054399 | 0.046113 | 0.055103 | 55.4224 | -0.11764 | -67.6021 | 55.446 | 55.3962 | 55.6117 | -67.735 | -67.5807 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.3768 | -68.0268 | -0.16449 | -0.039493 | 122.9929 | -0.031647 | 0.13284 | -0.089347 | 0.1262 | -0.4563 | -0.12028 | -0.010214 | -0.04014 | 0.41616 | 0.071199 | -0.10874 | 123.0165 | 122.9667 | 123.1822 | 67.4529 | -123.2205 | 122.9358 | 123.1272 | 122.9473 | 67.4564 | -123.5123
3154.7969 | 123.2208 | -67.5522 | 55.4306 | 0.0046549 | 0.027042 | -0.0012479 | 0.053081 | -0.0086556 | 0.1266 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054399 | 0.046326 | 0.055103 | 55.4362 | -0.12222 | -67.5976 | 55.446 | 55.387 | 55.6209 | -67.7304 | -67.5853 | -0.11869 | -67.6198 | 55.3698 | 55.5522 | 55.3722 | -68.0268 | -0.17822 | 0.015439 | 122.9884 | -0.04538 | 0.13284 | -0.043573 | 0.19029 | -0.47461 | -0.060766 | -0.033104 | -0.067609 | 0.407 | 0.12155 | -0.058391 | 122.9982 | 122.9392 | 123.1731 | 67.43 | -123.161 | 122.922 | 123.1043 | 122.9244 | 67.4335 | -123.4574
3155.7969 | 123.111 | -67.5888 | 55.4993 | 0.0046549 | 0.027897 | -0.0014615 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054613 | 0.046113 | 0.055103 | 55.4407 | -0.11764 | -67.5976 | 55.4506 | 55.4008 | 55.6209 | -67.7212 | -67.5761 | -0.11411 | -67.6198 | 55.3607 | 55.5613 | 55.3814 | -68.0314 | -0.13244 | -0.048647 | 123.0296 | -0.008759 | 0.12368 | -0.098501 | 0.12163 | -0.44257 | -0.13859 | 0.012675 | -0.030988 | 0.41158 | 0.062044 | -0.1179 | 123.0394 | 122.9896 | 123.2097 | 67.4712 | -123.2205 | 122.9495 | 123.1501 | 122.9702 | 67.4747 | -123.5306
3156.7969 | 123.1934 | -67.5705 | 55.481 | -0.010607 | 0.027684 | -0.0014615 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | -0.0045483 | -0.00034193 | 0.054399 | 0.045899 | 0.055103 | 55.4316 | -0.11764 | -67.5976 | 55.446 | 55.4053 | 55.6209 | -67.7304 | -67.5899 | -0.11869 | -67.6106 | 55.3561 | 55.5476 | 55.3859 | -68.0222 | -0.15991 | -0.034915 | 123.0021 | -0.027069 | 0.13284 | -0.075611 | 0.13994 | -0.45172 | -0.12485 | -0.019371 | -0.04014 | 0.41158 | 0.066619 | -0.095009 | 123.0165 | 122.9758 | 123.1914 | 67.4529 | -123.2114 | 122.9266 | 123.1181 | 122.9564 | 67.4518 | -123.5032
3157.7969 | 123.1522 | -67.598 | 55.4901 | 0.012286 | 0.027042 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.00015261 | -0.0045483 | -0.00076913 | 0.054399 | 0.046113 | 0.05489 | 55.4362 | -0.11764 | -67.5976 | 55.446 | 55.3962 | 55.63 | -67.7304 | -67.5853 | -0.11869 | -67.6106 | 55.3607 | 55.5522 | 55.3631 | -68.0222 | -0.13244 | -0.04407 | 123.0341 | 0.000396 | 0.13284 | -0.093924 | 0.13994 | -0.42426 | -0.12943 | 0.012672 | -0.012675 | 0.41158 | 0.062043 | -0.12706 | 123.044 | 122.9941 | 123.228 | 67.4803 | -123.2205 | 122.9586 | 123.1501 | 122.961 | 67.4793 | -123.5123
3158.7969 | 123.1247 | -67.5934 | 55.4489 | -0.010607 | 0.027256 | -0.0014615 | 0.05244 | -0.0090828 | 0.12703 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054613 | 0.046113 | 0.055103 | 55.4407 | -0.11306 | -67.6113 | 55.446 | 55.387 | 55.6255 | -67.735 | -67.5853 | -0.11869 | -67.6152 | 55.3653 | 55.5522 | 55.3676 | -68.0176 | -0.1416 | -0.002872 | 123.0341 | -0.017916 | 0.12368 | -0.061884 | 0.17656 | -0.42426 | -0.083655 | 0.008095 | -0.021831 | 0.40243 | 0.10324 | -0.08128 | 123.0394 | 122.9804 | 123.2189 | 67.4803 | -123.1839 | 122.9586 | 123.1455 | 122.961 | 67.4747 | -123.4666
3159.7969 | 123.1476 | -67.6025 | 55.4581 | -0.010607 | 0.02747 | -0.0012479 | 0.05244 | -0.0086556 | 0.12639 | -0.0074779 | -0.0043347 | -0.00076913 | 0.054613 | 0.045899 | 0.05489 | 55.4362 | -0.11764 | -67.6159 | 55.446 | 55.3962 | 55.6209 | -67.7258 | -67.5853 | -0.11411 | -67.6152 | 55.3653 | 55.5522 | 55.3859 | -68.0222 | -0.12329 | -0.012027 | 123.0387 | -0.013339 | 0.10995 | -0.061881 | 0.16282 | -0.41968 | -0.09281 | 0.01725 | -0.012676 | 0.407 | 0.094086 | -0.072121 | 123.0486 | 122.9987 | 123.2234 | 67.4849 | -123.1839 | 122.9678 | 123.1547 | 122.9885 | 67.4884 | -123.4803
3160.7969 | 123.1476 | -67.5705 | 55.4718 | -0.0029761 | 0.02747 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.00015261 | -0.0039075 | -0.00098273 | 0.054399 | 0.045899 | 0.055103 | 55.4407 | -0.11306 | -67.6113 | 55.4506 | 55.3962 | 55.6255 | -67.7304 | -67.5807 | -0.11869 | -67.6152 | 55.3653 | 55.5613 | 55.3631 | -68.0314 | -0.15991 | -0.021181 | 123.0112 | -0.040804 | 0.1191 | -0.075614 | 0.15367 | -0.46088 | -0.10654 | -0.010214 | -0.044719 | 0.41616 | 0.08951 | -0.10875 | 123.0211 | 122.9667 | 123.196 | 67.4574 | -123.2022 | 122.9358 | 123.1318 | 122.9336 | 67.4518 | -123.5032
3161.7969 | 123.2025 | -67.5705 | 55.4672 | -0.0029761 | 0.027256 | -0.0016753 | 0.052867 | -0.0086556 | 0.12724 | 0.0077831 | -0.0043347 | -0.00076913 | 0.054613 | 0.046113 | 0.055103 | 55.4316 | -0.11764 | -67.6159 | 55.4506 | 55.3962 | 55.6255 | -67.7304 | -67.5807 | -0.11869 | -67.6061 | 55.3653 | 55.5522 | 55.3631 | -68.0222 | -0.15991 | -0.016603 | 123.0021 | -0.045382 | 0.11453 | -0.071036 | 0.15825 | -0.45172 | -0.10196 | -0.010214 | -0.035562 | 0.41616 | 0.084931 | -0.10417 | 123.0211 | 122.9667 | 123.196 | 67.4529 | -123.1976 | 122.9358 | 123.1227 | 122.9336 | 67.4518 | -123.4894
3162.7969 | 123.1384 | -67.6117 | 55.4581 | -0.0029761 | 0.027256 | -0.0012479 | 0.05244 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054185 | 0.045899 | 0.054676 | 55.4362 | -0.11306 | -67.6159 | 55.4415 | 55.3962 | 55.6072 | -67.7304 | -67.5899 | -0.12327 | -67.6152 | 55.3607 | 55.5567 | 55.3493 | -68.0222 | -0.11871 | -0.016605 | 123.0479 | -0.004184 | 0.11453 | -0.061881 | 0.14909 | -0.41053 | -0.097389 | 0.021827 | -0.003521 | 0.407 | 0.098665 | -0.10875 | 123.0532 | 123.0079 | 123.2189 | 67.4986 | -123.1885 | 122.9724 | 123.1684 | 122.961 | 67.4884 | -123.4803
3163.7969 | 123.1567 | -67.5934 | 55.4626 | 0.012286 | 0.027042 | -0.0010343 | 0.052867 | -0.0088692 | 0.1266 | -0.0074779 | -0.0043347 | -0.00098273 | 0.054399 | 0.045899 | 0.054676 | 55.4362 | -0.11764 | -67.6113 | 55.446 | 55.3916 | 55.6209 | -67.735 | -67.5807 | -0.11869 | -67.6106 | 55.3607 | 55.5567 | 55.3539 | -68.0176 | -0.1416 | -0.016604 | 123.0296 | -0.017916 | 0.12368 | -0.071037 | 0.15825 | -0.42426 | -0.10197 | 0.012674 | -0.017252 | 0.407 | 0.094088 | -0.10875 | 123.0394 | 122.985 | 123.2143 | 67.4757 | -123.1976 | 122.9541 | 123.1501 | 122.9473 | 67.4747 | -123.4803
3164.7969 | 123.2437 | -67.5476 | 55.426 | -0.010607 | 0.02747 | -0.0014615 | 0.053081 | -0.0086556 | 0.1266 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054399 | 0.045685 | 0.054676 | 55.4316 | -0.11764 | -67.6067 | 55.446 | 55.4008 | 55.6209 | -67.735 | -67.5899 | -0.11869 | -67.6198 | 55.3653 | 55.5522 | 55.3768 | -68.0222 | -0.18738 | 0.020017 | 122.9792 | -0.059115 | 0.12826 | -0.025258 | 0.19487 | -0.47461 | -0.060766 | -0.04226 | -0.072187 | 0.40243 | 0.12613 | -0.049234 | 122.9936 | 122.9484 | 123.1685 | 67.43 | -123.161 | 122.9129 | 123.0998 | 122.9244 | 67.4289 | -123.4482
3165.7969 | 123.1338 | -67.5522 | 55.4672 | -0.010607 | 0.027684 | -0.0016753 | 0.052867 | -0.0086556 | 0.12682 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.045899 | 0.055531 | 55.4362 | -0.11764 | -67.6205 | 55.4506 | 55.3962 | 55.6209 | -67.735 | -67.5853 | -0.12327 | -67.6106 | 55.3653 | 55.5522 | 55.3585 | -68.0268 | -0.1828 | -0.016603 | 122.9884 | -0.068271 | 0.11453 | -0.071036 | 0.15367 | -0.47461 | -0.10196 | -0.033104 | -0.058451 | 0.41616 | 0.084931 | -0.10875 | 123.0028 | 122.9484 | 123.1731 | 67.4345 | -123.2022 | 122.9174 | 123.1043 | 122.9107 | 67.4289 | -123.494
3166.7969 | 123.2712 | -67.543 | 55.4214 | -0.0029761 | 0.02747 | -0.0014615 | 0.052654 | -0.0088692 | 0.12682 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054613 | 0.045899 | 0.055103 | 55.4316 | -0.12222 | -67.6067 | 55.4369 | 55.4053 | 55.6163 | -67.7212 | -67.5853 | -0.10953 | -67.6152 | 55.3607 | 55.5567 | 55.3768 | -68.0222 | -0.17822 | 0.015438 | 122.9746 | -0.063692 | 0.11452 | -0.016102 | 0.19487 | -0.47919 | -0.060768 | -0.042259 | -0.072185 | 0.407 | 0.13529 | -0.044657 | 122.9799 | 122.9484 | 123.1593 | 67.4208 | -123.1427 | 122.9037 | 123.0998 | 122.9198 | 67.4335 | -123.4437
3167.7969 | 123.1567 | -67.5842 | 55.426 | -0.0029761 | 0.027256 | -0.0014615 | 0.052654 | -0.0092964 | 0.1266 | -0.0074779 | -0.0043347 | -0.00055553 | 0.054185 | 0.046113 | 0.05489 | 55.4407 | -0.12222 | -67.5976 | 55.4506 | 55.3916 | 55.6255 | -67.7304 | -67.5761 | -0.11869 | -67.6106 | 55.3607 | 55.5522 | 55.3631 | -68.0268 | -0.14617 | 0.024596 | 123.025 | -0.013336 | 0.13284 | -0.034416 | 0.19945 | -0.44257 | -0.065345 | 0.008098 | -0.026407 | 0.41616 | 0.12613 | -0.06297 | 123.0348 | 122.9758 | 123.2097 | 67.462 | -123.1564 | 122.9449 | 123.1364 | 122.9473 | 67.4655 | -123.4528
3168.7969 | 123.1247 | -67.5888 | 55.481 | -0.010607 | 0.027256 | -0.0012479 | 0.052867 | -0.0090828 | 0.12703 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054399 | 0.045685 | 0.055103 | 55.427 | -0.12222 | -67.6021 | 55.4415 | 55.4008 | 55.63 | -67.7212 | -67.5853 | -0.11411 | -67.6061 | 55.3653 | 55.5613 | 55.3585 | -68.0222 | -0.13244 | -0.039493 | 123.0158 | -0.013337 | 0.1191 | -0.08019 | 0.14909 | -0.43341 | -0.1157 | 0.003517 | -0.017252 | 0.41616 | 0.080355 | -0.12248 | 123.0303 | 122.9896 | 123.2189 | 67.4666 | -123.2022 | 122.9541 | 123.1501 | 122.9473 | 67.4747 | -123.5032
3169.8594 | 123.1522 | -67.6163 | 55.4443 | -0.0029761 | 0.027256 | -0.0012479 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | -0.0039075 | -0.00012813 | 0.054399 | 0.046326 | 0.05489 | 55.4362 | -0.11764 | -67.6021 | 55.4552 | 55.387 | 55.6209 | -67.7304 | -67.5853 | -0.11411 | -67.6061 | 55.3698 | 55.5522 | 55.3768 | -68.0222 | -0.11413 | 0.010863 | 123.0524 | 0.014129 | 0.12826 | -0.057306 | 0.17656 | -0.40595 | -0.074499 | 0.030983 | 0.010214 | 0.41616 | 0.10782 | -0.067545 | 123.0715 | 123.0033 | 123.2372 | 67.4986 | -123.1747 | 122.9861 | 123.1684 | 122.9931 | 67.5022 | -123.4666
3170.7969 | 123.2208 | -67.5705 | 55.426 | -0.0029761 | 0.027256 | -0.0016753 | 0.052867 | -0.0090828 | 0.1266 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054399 | 0.046113 | 0.054676 | 55.4362 | -0.11764 | -67.6067 | 55.446 | 55.387 | 55.6209 | -67.7258 | -67.5807 | -0.11869 | -67.6152 | 55.3607 | 55.5613 | 55.3356 | -68.0176 | -0.15533 | 0.020017 | 123.0067 | -0.036226 | 0.1191 | -0.038995 | 0.19487 | -0.44714 | -0.065345 | -0.010214 | -0.044719 | 0.40243 | 0.13529 | -0.090442 | 123.0165 | 122.9575 | 123.1914 | 67.4529 | -123.1518 | 122.9312 | 123.1318 | 122.9061 | 67.4518 | -123.4437
3171.7969 | 123.1247 | -67.5842 | 55.4855 | 0.012286 | 0.027042 | -0.0014615 | 0.052654 | -0.0088692 | 0.12682 | -0.0074779 | -0.0039075 | -0.00055553 | 0.054185 | 0.046326 | 0.054676 | 55.4316 | -0.10848 | -67.5976 | 55.4506 | 55.3916 | 55.6255 | -67.735 | -67.5761 | -0.10953 | -67.6061 | 55.3653 | 55.5659 | 55.3722 | -68.0268 | -0.15075 | -0.034914 | 123.0158 | -0.013336 | 0.13742 | -0.093926 | 0.13994 | -0.44257 | -0.12028 | 0.008098 | -0.021829 | 0.42074 | 0.080356 | -0.11332 | 123.0348 | 122.9758 | 123.2097 | 67.4757 | -123.2205 | 122.9495 | 123.1501 | 122.9564 | 67.4747 | -123.5123
3172.7969 | 123.2346 | -67.5705 | 55.4077 | 0.0046549 | 0.027042 | -0.0010343 | 0.052654 | -0.0086556 | 0.12682 | 0.00015261 | -0.0043347 | -0.00034193 | 0.053972 | 0.046113 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.4415 | 55.3825 | 55.6163 | -67.7304 | -67.5899 | -0.12327 | -67.6152 | 55.3607 | 55.5476 | 55.3447 | -68.0268 | -0.15991 | 0.033749 | 122.9975 | -0.027069 | 0.13284 | -0.025264 | 0.2086 | -0.4563 | -0.047035 | -0.019371 | -0.044719 | 0.41158 | 0.13986 | -0.062974 | 123.012 | 122.9529 | 123.1868 | 67.4574 | -123.1381 | 122.9312 | 123.1181 | 122.9152 | 67.4472 | -123.4345
3173.7969 | 123.2071 | -67.5751 | 55.4398 | -0.0029761 | 0.02747 | -0.0014615 | 0.052867 | -0.0088692 | 0.1266 | -0.0074779 | -0.0043347 | -0.00076913 | 0.054613 | 0.04654 | 0.054676 | 55.4362 | -0.11306 | -67.6021 | 55.4506 | 55.387 | 55.6209 | -67.7258 | -67.5853 | -0.12327 | -67.6152 | 55.3607 | 55.5476 | 55.3722 | -68.0176 | -0.15075 | 0.010863 | 123.0112 | -0.02707 | 0.12368 | -0.052728 | 0.18114 | -0.44257 | -0.079078 | -0.010216 | -0.040142 | 0.40243 | 0.10782 | -0.067546 | 123.0257 | 122.9621 | 123.196 | 67.462 | -123.1656 | 122.9358 | 123.1226 | 122.9473 | 67.4518 | -123.4574
3174.7969 | 123.2117 | -67.5659 | 55.4306 | -0.010607 | 0.02747 | -0.0016753 | 0.052867 | -0.0088692 | 0.12703 | 0.0077831 | -0.0041211 | -0.00098273 | 0.054185 | 0.046113 | 0.055103 | 55.4362 | -0.11306 | -67.6067 | 55.4506 | 55.3962 | 55.6255 | -67.735 | -67.5853 | -0.11869 | -67.6152 | 55.3607 | 55.5567 | 55.3676 | -68.0176 | -0.16907 | 0.020018 | 123.0021 | -0.040804 | 0.12826 | -0.034415 | 0.19487 | -0.45172 | -0.069923 | -0.019371 | -0.049297 | 0.40243 | 0.12613 | -0.062969 | 123.0165 | 122.9621 | 123.1914 | 67.4529 | -123.1656 | 122.9266 | 123.1227 | 122.9336 | 67.4472 | -123.4482
3175.7969 | 123.2529 | -67.5385 | 55.4306 | -0.010607 | 0.02747 | -0.0012479 | 0.052654 | -0.0086556 | 0.12682 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054826 | 0.046113 | 0.05489 | 55.4316 | -0.12222 | -67.6067 | 55.446 | 55.3962 | 55.6163 | -67.735 | -67.5807 | -0.12327 | -67.6106 | 55.3607 | 55.5522 | 55.3631 | -68.0314 | -0.19653 | 0.015439 | 122.97 | -0.06827 | 0.12826 | -0.034415 | 0.18571 | -0.49292 | -0.069923 | -0.042258 | -0.072184 | 0.42074 | 0.12155 | -0.067548 | 122.9845 | 122.9346 | 123.1548 | 67.4162 | -123.1656 | 122.8991 | 123.0906 | 122.9015 | 67.4152 | -123.462
3176.7969 | 123.2483 | -67.5522 | 55.4489 | -0.0029761 | 0.02747 | -0.0014615 | 0.052867 | -0.0088692 | 0.1266 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054613 | 0.046113 | 0.055103 | 55.4316 | -0.11764 | -67.5976 | 55.4415 | 55.3962 | 55.6209 | -67.7167 | -67.5807 | -0.10953 | -67.6152 | 55.3561 | 55.5567 | 55.3356 | -68.0268 | -0.16448 | -0.00745 | 122.9838 | -0.04538 | 0.1191 | -0.052726 | 0.17198 | -0.47461 | -0.092812 | -0.028525 | -0.06303 | 0.41158 | 0.10782 | -0.11333 | 122.9936 | 122.9484 | 123.1731 | 67.4345 | -123.1656 | 122.9083 | 123.1089 | 122.8878 | 67.4427 | -123.4757
3177.7969 | 123.23 | -67.5613 | 55.426 | -0.0029761 | 0.027256 | -0.0014615 | 0.052654 | -0.0086556 | 0.12682 | -0.0074779 | -0.0043347 | -0.00098273 | 0.054613 | 0.046326 | 0.054676 | 55.427 | -0.10848 | -67.6067 | 55.4506 | 55.387 | 55.6209 | -67.7258 | -67.5807 | -0.11411 | -67.6106 | 55.3561 | 55.5567 | 55.3951 | -68.0222 | -0.16448 | 0.024596 | 122.9884 | -0.045382 | 0.1191 | -0.038995 | 0.19487 | -0.46088 | -0.069923 | -0.01937 | -0.049296 | 0.41158 | 0.13071 | -0.03092 | 123.012 | 122.9484 | 123.1822 | 67.4529 | -123.1518 | 122.9174 | 123.1181 | 122.9564 | 67.4472 | -123.4482
3178.7969 | 123.2391 | -67.5476 | 55.4672 | -0.0029761 | 0.027042 | -0.0016753 | 0.052867 | -0.0088692 | 0.12703 | 0.00015261 | -0.0041211 | -0.00012813 | 0.054613 | 0.046326 | 0.055103 | 55.4224 | -0.11764 | -67.6113 | 55.446 | 55.3962 | 55.6163 | -67.7258 | -67.5807 | -0.11411 | -67.6152 | 55.3607 | 55.5613 | 55.3493 | -68.0176 | -0.17822 | -0.021182 | 122.97 | -0.063693 | 0.11453 | -0.071036 | 0.14909 | -0.47003 | -0.10654 | -0.033103 | -0.067608 | 0.40243 | 0.094088 | -0.11791 | 122.9936 | 122.9438 | 123.1639 | 67.43 | -123.193 | 122.9083 | 123.1089 | 122.8969 | 67.4335 | -123.4849
3179.7969 | 123.2483 | -67.5522 | 55.4443 | -0.010607 | 0.027042 | -0.0016753 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | -0.0043347 | -0.00034193 | 0.054613 | 0.045685 | 0.055103 | 55.427 | -0.11306 | -67.6067 | 55.4415 | 55.3825 | 55.6255 | -67.7304 | -67.5807 | -0.11869 | -67.6152 | 55.3607 | 55.5613 | 55.3676 | -68.0222 | -0.17822 | -0.002872 | 122.9792 | -0.054537 | 0.12368 | -0.061885 | 0.18113 | -0.47004 | -0.083656 | -0.028525 | -0.06303 | 0.407 | 0.11698 | -0.076702 | 122.9936 | 122.9346 | 123.1777 | 67.4391 | -123.1747 | 122.9129 | 123.1135 | 122.9198 | 67.4335 | -123.4666
3180.7969 | 123.1842 | -67.5568 | 55.4489 | -0.0029761 | 0.026829 | -0.0012479 | 0.052867 | -0.0088692 | 0.12682 | -0.0074779 | -0.0045483 | -0.00055553 | 0.053972 | 0.045899 | 0.055317 | 55.4316 | -0.11764 | -67.5976 | 55.4506 | 55.3825 | 55.6163 | -67.7167 | -67.5807 | -0.11869 | -67.6106 | 55.3653 | 55.5522 | 55.3539 | -68.0268 | -0.1599 | 0.001707 | 122.9884 | -0.040802 | 0.1191 | -0.066463 | 0.1674 | -0.47003 | -0.083655 | -0.023947 | -0.053873 | 0.41616 | 0.10324 | -0.095016 | 123.0074 | 122.9392 | 123.1731 | 67.4391 | -123.1656 | 122.922 | 123.1089 | 122.9107 | 67.4381 | -123.4757
3181.7969 | 123.2483 | -67.5201 | 55.4169 | -0.0029761 | 0.027042 | -0.0014615 | 0.05244 | -0.0084418 | 0.12682 | -0.0074779 | -0.0043347 | -0.00034193 | 0.054613 | 0.046113 | 0.055103 | 55.427 | -0.11764 | -67.6113 | 55.4552 | 55.387 | 55.6163 | -67.7167 | -67.5853 | -0.11869 | -67.6106 | 55.3653 | 55.5567 | 55.3814 | -68.0268 | -0.19652 | 0.038329 | 122.9472 | -0.091158 | 0.10537 | -0.02984 | 0.19944 | -0.50666 | -0.051611 | -0.065147 | -0.090494 | 0.41616 | 0.13986 | -0.0355 | 122.9753 | 122.9072 | 123.1365 | 67.4025 | -123.1335 | 122.8854 | 123.0769 | 122.9015 | 67.4015 | -123.4437
3182.7969 | 123.1979 | -67.5751 | 55.4398 | -0.0029761 | 0.026829 | -0.0016753 | 0.052867 | -0.0086556 | 0.12682 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054399 | 0.046326 | 0.055103 | 55.4316 | -0.10848 | -67.6067 | 55.4415 | 55.3962 | 55.6163 | -67.735 | -67.5807 | -0.11869 | -67.6061 | 55.3698 | 55.5522 | 55.3859 | -68.0176 | -0.15991 | 0.001706 | 123.0067 | -0.031649 | 0.12826 | -0.04357 | 0.17656 | -0.44257 | -0.069921 | -0.005637 | -0.030985 | 0.41158 | 0.1124 | -0.05381 | 123.0165 | 122.9713 | 123.1914 | 67.4666 | -123.1747 | 122.9449 | 123.1272 | 122.961 | 67.4564 | -123.4574
3183.7969 | 123.2117 | -67.5659 | 55.4626 | -0.0029761 | 0.027256 | -0.0014615 | 0.052867 | -0.0086556 | 0.12682 | 0.00015261 | -0.0041211 | -0.00076913 | 0.054399 | 0.046326 | 0.05489 | 55.427 | -0.12222 | -67.6021 | 55.4415 | 55.4008 | 55.6209 | -67.7304 | -67.5807 | -0.11411 | -67.6061 | 55.3607 | 55.5522 | 55.3493 | -68.0222 | -0.16449 | -0.021182 | 122.9929 | -0.036225 | 0.12826 | -0.061879 | 0.15825 | -0.4563 | -0.10197 | -0.014792 | -0.04014 | 0.41616 | 0.089509 | -0.11333 | 123.0074 | 122.9667 | 123.1868 | 67.4437 | -123.193 | 122.9266 | 123.1181 | 122.9152 | 67.4518 | -123.4849
3184.7969 | 123.2803 | -67.511 | 55.4443 | 0.0046549 | 0.027042 | -0.0012479 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054185 | 0.046326 | 0.054676 | 55.427 | -0.12222 | -67.5976 | 55.4506 | 55.3962 | 55.6163 | -67.735 | -67.5807 | -0.11411 | -67.6152 | 55.3607 | 55.5613 | 55.3585 | -68.0222 | -0.224 | 0.006285 | 122.938 | -0.086579 | 0.13742 | -0.048148 | 0.17198 | -0.51123 | -0.083656 | -0.069724 | -0.10423 | 0.407 | 0.11698 | -0.08586 | 122.9616 | 122.9072 | 123.1273 | 67.3888 | -123.1793 | 122.8717 | 123.0723 | 122.8695 | 67.3969 | -123.4666
3185.7969 | 123.23 | -67.5385 | 55.4672 | -0.0029761 | 0.027256 | -0.0014615 | 0.052867 | -0.0090828 | 0.12682 | 0.0077831 | -0.0045483 | -0.00034193 | 0.054399 | 0.046113 | 0.05489 | 55.4316 | -0.11764 | -67.6021 | 55.4415 | 55.3962 | 55.6163 | -67.7212 | -67.5807 | -0.11411 | -67.6152 | 55.3698 | 55.5567 | 55.3768 | -68.0222 | -0.18279 | -0.02576 | 122.97 | -0.063691 | 0.1191 | -0.071036 | 0.14909 | -0.48377 | -0.097387 | -0.042258 | -0.076763 | 0.407 | 0.08951 | -0.090433 | 122.9799 | 122.9346 | 123.1548 | 67.4208 | -123.1885 | 122.9083 | 123.0952 | 122.9152 | 67.4243 | -123.4894
3186.7969 | 123.175 | -67.5476 | 55.4626 | 0.0046549 | 0.02747 | -0.0016753 | 0.053081 | -0.0088692 | 0.12682 | 0.00015261 | -0.0045483 | -0.00055553 | 0.054613 | 0.046326 | 0.055103 | 55.4362 | -0.11306 | -67.6021 | 55.446 | 55.3962 | 55.6209 | -67.7212 | -67.5853 | -0.11869 | -67.6106 | 55.3653 | 55.5567 | 55.3768 | -68.0222 | -0.17364 | -0.016604 | 122.9838 | -0.054536 | 0.1191 | -0.066458 | 0.15825 | -0.47461 | -0.097387 | -0.037682 | -0.063029 | 0.41158 | 0.094088 | -0.085855 | 122.9936 | 122.9438 | 123.1685 | 67.4345 | -123.1839 | 122.9129 | 123.1043 | 122.9244 | 67.4289 | -123.4849
3187.7969 | 123.2483 | -67.5339 | 55.4398 | -0.010607 | 0.027042 | -0.0014615 | 0.052654 | -0.0088692 | 0.12682 | 0.0077831 | -0.0043347 | -0.00034193 | 0.054399 | 0.046113 | 0.05489 | 55.427 | -0.11764 | -67.6021 | 55.4506 | 55.3962 | 55.6209 | -67.7212 | -67.5853 | -0.11869 | -67.6198 | 55.3698 | 55.5567 | 55.3768 | -68.0222 | -0.18737 | 0.010863 | 122.9609 | -0.068268 | 0.1191 | -0.04357 | 0.18114 | -0.48835 | -0.069921 | -0.051414 | -0.085919 | 0.40243 | 0.11698 | -0.062967 | 122.9845 | 122.9301 | 123.1548 | 67.4162 | -123.161 | 122.9037 | 123.0906 | 122.9107 | 67.4152 | -123.462
3188.7969 | 123.2758 | -67.511 | 55.4901 | 0.012286 | 0.027042 | -0.0014615 | 0.053081 | -0.0090828 | 0.12682 | 0.0077831 | -0.0045483 | -0.00055553 | 0.054613 | 0.046113 | 0.055103 | 55.427 | -0.12222 | -67.6021 | 55.446 | 55.3962 | 55.6255 | -67.7258 | -67.5853 | -0.11869 | -67.6152 | 55.3653 | 55.5522 | 55.3859 | -68.0268 | -0.21484 | -0.04407 | 122.938 | -0.091157 | 0.12368 | -0.093924 | 0.13536 | -0.51581 | -0.12485 | -0.074303 | -0.10423 | 0.41158 | 0.062043 | -0.10416 | 122.957 | 122.9072 | 123.1365 | 67.3888 | -123.2159 | 122.8762 | 123.0631 | 122.8969 | 67.3923 | -123.5169
3189.7969 | 123.1979 | -67.5476 | 55.4443 | -0.010607 | 0.026829 | -0.0016753 | 0.053081 | -0.0088692 | 0.12639 | -0.0074779 | -0.0039075 | -0.00034193 | 0.054613 | 0.046113 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.4506 | 55.3916 | 55.6163 | -67.7304 | -67.5807 | -0.11869 | -67.6106 | 55.3561 | 55.5522 | 55.3997 | -68.0222 | -0.1828 | 0.006285 | 122.9746 | -0.049958 | 0.13284 | -0.052727 | 0.17198 | -0.47461 | -0.088234 | -0.033103 | -0.063029 | 0.41158 | 0.10782 | -0.044652 | 122.9982 | 122.9392 | 123.1639 | 67.4345 | -123.1747 | 122.9037 | 123.0998 | 122.9473 | 67.4289 | -123.4666
3190.7969 | 123.2803 | -67.5201 | 55.4581 | -0.0029761 | 0.026829 | -0.0014615 | 0.053295 | -0.0088692 | 0.12639 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054399 | 0.046113 | 0.05489 | 55.4362 | -0.11306 | -67.593 | 55.4506 | 55.4099 | 55.6209 | -67.7304 | -67.5899 | -0.11869 | -67.6152 | 55.3653 | 55.5522 | 55.3676 | -68.0176 | -0.21026 | -0.007448 | 122.9563 | -0.072845 | 0.13742 | -0.048144 | 0.16282 | -0.4975 | -0.09281 | -0.069725 | -0.095073 | 0.40243 | 0.094086 | -0.090435 | 122.9708 | 122.9301 | 123.141 | 67.4071 | -123.1885 | 122.8854 | 123.0723 | 122.8878 | 67.4015 | -123.4757
3191.7969 | 123.2529 | -67.5476 | 55.4581 | 0.0046549 | 0.027042 | -0.0014615 | 0.052867 | -0.0086556 | 0.12682 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054613 | 0.046326 | 0.054676 | 55.4224 | -0.11306 | -67.6067 | 55.446 | 55.387 | 55.6209 | -67.7304 | -67.5807 | -0.11869 | -67.6152 | 55.3698 | 55.5522 | 55.3631 | -68.0268 | -0.1828 | -0.012027 | 122.97 | -0.059115 | 0.12368 | -0.071039 | 0.16282 | -0.47919 | -0.088232 | -0.033103 | -0.067608 | 0.41158 | 0.094086 | -0.095014 | 122.9936 | 122.9346 | 123.1685 | 67.4345 | -123.1885 | 122.9174 | 123.0998 | 122.9107 | 67.4289 | -123.4849
3192.8594 | 123.1934 | -67.5476 | 55.4535 | -0.010607 | 0.027042 | -0.0014615 | 0.052654 | -0.0086556 | 0.1266 | -0.0074779 | -0.0043347 | -0.00055553 | 0.054613 | 0.045899 | 0.054676 | 55.427 | -0.12222 | -67.5976 | 55.4415 | 55.4008 | 55.6209 | -67.7258 | -67.5761 | -0.11869 | -67.6152 | 55.3607 | 55.5522 | 55.3585 | -68.0131 | -0.17822 | -0.012027 | 122.9746 | -0.049958 | 0.12826 | -0.052724 | 0.1674 | -0.46546 | -0.092811 | -0.028524 | -0.067608 | 0.39785 | 0.098664 | -0.095015 | 122.9891 | 122.9484 | 123.1685 | 67.4254 | -123.1793 | 122.9083 | 123.0998 | 122.9061 | 67.4289 | -123.4666
3193.7969 | 123.1979 | -67.543 | 55.4443 | -0.0029761 | 0.026401 | -0.0014615 | 0.053508 | -0.0086556 | 0.12703 | 0.015414 | -0.0041211 | -0.00076913 | 0.054399 | 0.046754 | 0.055103 | 55.4362 | -0.11306 | -67.5976 | 55.4369 | 55.4053 | 55.6209 | -67.7258 | -67.5807 | -0.11869 | -67.6106 | 55.3607 | 55.5522 | 55.3676 | -68.0222 | -0.18279 | -0.00745 | 122.9792 | -0.054535 | 0.12826 | -0.03899 | 0.17656 | -0.47919 | -0.083656 | -0.03768 | -0.067606 | 0.41158 | 0.10782 | -0.076702 | 122.9799 | 122.9484 | 123.1639 | 67.43 | -123.1702 | 122.9037 | 123.0952 | 122.9107 | 67.4243 | -123.4666
3194.7969 | 123.2346 | -67.5247 | 55.481 | 0.0046549 | 0.027042 | -0.0014615 | 0.052867 | -0.0084418 | 0.1266 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.046326 | 0.055103 | 55.4316 | -0.11764 | -67.5976 | 55.446 | 55.387 | 55.6209 | -67.7212 | -67.5807 | -0.11411 | -67.6061 | 55.3653 | 55.5476 | 55.3722 | -68.0268 | -0.19653 | -0.034915 | 122.9563 | -0.072846 | 0.12368 | -0.093927 | 0.13994 | -0.50208 | -0.1157 | -0.055991 | -0.081339 | 0.42074 | 0.066619 | -0.10874 | 122.9708 | 122.9117 | 123.1456 | 67.4071 | -123.2022 | 122.89 | 123.0723 | 122.8969 | 67.4106 | -123.5078
3195.7969 | 123.262 | -67.5476 | 55.4535 | 0.012286 | 0.027042 | -0.0012479 | 0.052654 | -0.0088692 | 0.12682 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054399 | 0.046326 | 0.05489 | 55.4316 | -0.11764 | -67.5884 | 55.446 | 55.3825 | 55.6163 | -67.7304 | -67.5853 | -0.12327 | -67.6106 | 55.3607 | 55.5567 | 55.3814 | -68.0222 | -0.1828 | -0.007449 | 122.9792 | -0.040801 | 0.142 | -0.07104 | 0.16282 | -0.47461 | -0.092811 | -0.037682 | -0.063029 | 0.41158 | 0.10324 | -0.072121 | 122.9936 | 122.9301 | 123.1639 | 67.43 | -123.1839 | 122.9083 | 123.1043 | 122.929 | 67.4243 | -123.4757
3196.7969 | 123.2758 | -67.5201 | 55.4855 | 0.0046549 | 0.027042 | -0.0012479 | 0.052867 | -0.0088692 | 0.1266 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054399 | 0.04654 | 0.05489 | 55.4179 | -0.11764 | -67.593 | 55.446 | 55.387 | 55.6255 | -67.7304 | -67.5761 | -0.11869 | -67.6152 | 55.3653 | 55.5567 | 55.3402 | -68.0131 | -0.21026 | -0.039493 | 122.938 | -0.072845 | 0.13742 | -0.098505 | 0.13994 | -0.49292 | -0.12028 | -0.055989 | -0.095073 | 0.39785 | 0.071199 | -0.14537 | 122.9662 | 122.9072 | 123.1456 | 67.4025 | -123.2159 | 122.8854 | 123.0769 | 122.8603 | 67.4015 | -123.4986
3197.7969 | 123.2437 | -67.5385 | 55.4489 | -0.0029761 | 0.027256 | -0.0016753 | 0.053295 | -0.0090828 | 0.1266 | 0.00015261 | -0.0041211 | -0.00034193 | 0.054185 | 0.046113 | 0.05489 | 55.427 | -0.11306 | -67.6021 | 55.446 | 55.3733 | 55.6255 | -67.7258 | -67.5853 | -0.11411 | -67.6152 | 55.3607 | 55.5522 | 55.3493 | -68.0222 | -0.18737 | -0.002872 | 122.9655 | -0.063691 | 0.12368 | -0.075621 | 0.17656 | -0.48377 | -0.088234 | -0.046837 | -0.076763 | 0.407 | 0.10324 | -0.099595 | 122.9845 | 122.9117 | 123.1639 | 67.4254 | -123.1747 | 122.8991 | 123.0906 | 122.8878 | 67.4243 | -123.4711
3198.7969 | 123.2529 | -67.5201 | 55.4489 | 0.0046549 | 0.026829 | -0.0012479 | 0.052867 | -0.0090828 | 0.1266 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054399 | 0.046113 | 0.055103 | 55.4316 | -0.10848 | -67.5976 | 55.446 | 55.387 | 55.6163 | -67.7258 | -67.5807 | -0.11869 | -67.6106 | 55.3653 | 55.5476 | 55.3585 | -68.0268 | -0.20568 | -0.002872 | 122.9517 | -0.077423 | 0.12826 | -0.061884 | 0.1674 | -0.50666 | -0.083655 | -0.060568 | -0.090494 | 0.41616 | 0.098662 | -0.090438 | 122.9662 | 122.9072 | 123.1365 | 67.4117 | -123.1747 | 122.8854 | 123.0677 | 122.8786 | 67.4015 | -123.4757
3199.7969 | 123.1338 | -67.5613 | 55.481 | -0.0029761 | 0.027042 | -0.0016753 | 0.053081 | -0.0090828 | 0.12639 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054399 | 0.04654 | 0.05489 | 55.427 | -0.11764 | -67.6159 | 55.446 | 55.3962 | 55.6209 | -67.7304 | -67.5807 | -0.11869 | -67.6106 | 55.3561 | 55.5522 | 55.3859 | -68.0268 | -0.16906 | -0.034915 | 122.9884 | -0.054538 | 0.11453 | -0.084769 | 0.13994 | -0.46546 | -0.12485 | -0.01937 | -0.049296 | 0.41616 | 0.071198 | -0.095009 | 123.0074 | 122.9575 | 123.1822 | 67.4437 | -123.2114 | 122.9174 | 123.1135 | 122.9473 | 67.4427 | -123.5078
3200.7969 | 123.2025 | -67.5476 | 55.4718 | 0.0046549 | 0.026829 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054399 | 0.046326 | 0.055103 | 55.427 | -0.11306 | -67.6021 | 55.446 | 55.3916 | 55.6209 | -67.7258 | -67.5807 | -0.11869 | -67.6106 | 55.3653 | 55.5567 | 55.3585 | -68.0268 | -0.17822 | -0.02576 | 122.9746 | -0.054536 | 0.12368 | -0.080193 | 0.14909 | -0.47919 | -0.10654 | -0.033103 | -0.063029 | 0.41616 | 0.084932 | -0.11333 | 122.9936 | 122.9392 | 123.1685 | 67.4345 | -123.1976 | 122.9129 | 123.1043 | 122.9061 | 67.4289 | -123.4986
3201.7969 | 123.2529 | -67.5385 | 55.4718 | -0.0029761 | 0.027256 | -0.0014615 | 0.053295 | -0.0086556 | 0.1266 | 0.015414 | -0.0039075 | -0.00076913 | 0.054399 | 0.046326 | 0.055103 | 55.4316 | -0.11306 | -67.5976 | 55.446 | 55.3916 | 55.6163 | -67.7258 | -67.5899 | -0.11869 | -67.6061 | 55.3653 | 55.5613 | 55.3585 | -68.0131 | -0.18737 | -0.02576 | 122.97 | -0.059113 | 0.12826 | -0.080193 | 0.14451 | -0.47461 | -0.10654 | -0.051415 | -0.067606 | 0.407 | 0.08951 | -0.11333 | 122.9845 | 122.9301 | 123.1548 | 67.4254 | -123.1976 | 122.9037 | 123.0998 | 122.8969 | 67.4198 | -123.4849
3202.7969 | 123.2529 | -67.5705 | 55.4352 | 0.0046549 | 0.027256 | -0.0014615 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | -0.0043347 | -0.00098273 | 0.054185 | 0.04654 | 0.055103 | 55.4316 | -0.12222 | -67.593 | 55.4415 | 55.387 | 55.6209 | -67.7258 | -67.5899 | -0.11869 | -67.6106 | 55.3653 | 55.5476 | 55.3859 | -68.0176 | -0.15533 | 0.006283 | 123.0021 | -0.022491 | 0.13284 | -0.048151 | 0.18571 | -0.44714 | -0.069922 | -0.019371 | -0.04014 | 0.407 | 0.11239 | -0.049233 | 123.012 | 122.9575 | 123.1914 | 67.4483 | -123.161 | 122.9358 | 123.1181 | 122.9564 | 67.4518 | -123.4528
3203.7969 | 123.2483 | -67.5568 | 55.4443 | 0.0046549 | 0.027042 | -0.0018889 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | -0.0045483 | -0.00034193 | 0.054399 | 0.046754 | 0.055103 | 55.4316 | -0.11764 | -67.5976 | 55.446 | 55.4008 | 55.6072 | -67.7304 | -67.5761 | -0.11411 | -67.6061 | 55.3561 | 55.5567 | 55.3722 | -68.0176 | -0.17364 | 0.001706 | 122.9884 | -0.040802 | 0.13284 | -0.043569 | 0.16282 | -0.46088 | -0.088234 | -0.019368 | -0.049295 | 0.41158 | 0.1124 | -0.072124 | 123.0028 | 122.9575 | 123.1639 | 67.4391 | -123.1747 | 122.9129 | 123.1135 | 122.929 | 67.4427 | -123.462
3204.7969 | 123.1796 | -67.543 | 55.4993 | -0.0029761 | 0.027042 | -0.0014615 | 0.052654 | -0.0088692 | 0.12703 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054826 | 0.04654 | 0.055103 | 55.4316 | -0.10848 | -67.593 | 55.4506 | 55.4008 | 55.6209 | -67.7304 | -67.5807 | -0.10953 | -67.6152 | 55.3607 | 55.5613 | 55.3722 | -68.0176 | -0.18737 | -0.048647 | 122.9746 | -0.049957 | 0.13742 | -0.098501 | 0.12163 | -0.47461 | -0.13859 | -0.03768 | -0.072185 | 0.40243 | 0.062044 | -0.12706 | 122.9937 | 122.9438 | 123.1639 | 67.4346 | -123.2297 | 122.9037 | 123.1043 | 122.9152 | 67.4335 | -123.5169
3205.7969 | 123.2712 | -67.5293 | 55.4489 | -0.0029761 | 0.027042 | -0.0014615 | 0.052867 | -0.0086556 | 0.12703 | 0.00015261 | -0.0043347 | -0.00034193 | 0.054185 | 0.046326 | 0.05489 | 55.4316 | -0.11306 | -67.5976 | 55.4415 | 55.4053 | 55.6209 | -67.7304 | -67.5807 | -0.11411 | -67.6152 | 55.3653 | 55.5567 | 55.3905 | -68.0222 | -0.20111 | -0.00745 | 122.9609 | -0.068268 | 0.13284 | -0.043568 | 0.17198 | -0.49292 | -0.083655 | -0.051413 | -0.085918 | 0.407 | 0.10782 | -0.058387 | 122.9708 | 122.9346 | 123.1502 | 67.4162 | -123.1793 | 122.8946 | 123.086 | 122.9198 | 67.4152 | -123.4711
3206.7969 | 123.2162 | -67.543 | 55.4718 | 0.0046549 | 0.026829 | -0.0016753 | 0.052654 | -0.0090828 | 0.12703 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054185 | 0.04654 | 0.05489 | 55.427 | -0.11306 | -67.5976 | 55.446 | 55.4008 | 55.6255 | -67.7304 | -67.5807 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.3722 | -68.0268 | -0.18737 | -0.02576 | 122.97 | -0.054535 | 0.13284 | -0.071035 | 0.15367 | -0.48377 | -0.10654 | -0.03768 | -0.067606 | 0.41616 | 0.084932 | -0.09959 | 122.9891 | 122.9438 | 123.1685 | 67.43 | -123.2022 | 122.9083 | 123.0998 | 122.9152 | 67.4289 | -123.4986
3207.7969 | 123.1796 | -67.543 | 55.4764 | 0.0046549 | 0.026401 | -0.0014615 | 0.052654 | -0.0090828 | 0.1266 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.04654 | 0.055103 | 55.427 | -0.11306 | -67.5976 | 55.446 | 55.4053 | 55.6163 | -67.7304 | -67.5807 | -0.12327 | -67.6061 | 55.3653 | 55.5567 | 55.3768 | -68.0176 | -0.18737 | -0.030337 | 122.97 | -0.054535 | 0.13284 | -0.071033 | 0.13994 | -0.47461 | -0.11112 | -0.03768 | -0.063028 | 0.41158 | 0.080355 | -0.099588 | 122.9891 | 122.9484 | 123.1593 | 67.43 | -123.2068 | 122.9083 | 123.0998 | 122.9198 | 67.4198 | -123.494
3208.7969 | 123.1567 | -67.5613 | 55.4901 | 0.0046549 | 0.027042 | -0.0018889 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054826 | 0.046754 | 0.054676 | 55.4224 | -0.10848 | -67.5976 | 55.446 | 55.3916 | 55.6255 | -67.7304 | -67.5899 | -0.11869 | -67.6061 | 55.3653 | 55.5613 | 55.3768 | -68.0222 | -0.16906 | -0.04407 | 122.9838 | -0.036225 | 0.13284 | -0.098503 | 0.13536 | -0.46088 | -0.12485 | -0.028527 | -0.044718 | 0.41616 | 0.0712 | -0.11332 | 123.0074 | 122.9529 | 123.1868 | 67.4529 | -123.2205 | 122.9266 | 123.1227 | 122.9381 | 67.4427 | -123.5123
3209.7969 | 123.1613 | -67.5293 | 55.4672 | 0.0046549 | 0.026829 | -0.0016753 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | -0.0039075 | -0.00055553 | 0.054399 | 0.046326 | 0.055317 | 55.4316 | -0.12222 | -67.593 | 55.446 | 55.3962 | 55.6163 | -67.735 | -67.5807 | -0.11869 | -67.6015 | 55.3653 | 55.5522 | 55.3493 | -68.0222 | -0.20569 | -0.021182 | 122.9609 | -0.06369 | 0.142 | -0.071036 | 0.14909 | -0.49292 | -0.10196 | -0.051413 | -0.072182 | 0.42074 | 0.084931 | -0.11791 | 122.9753 | 122.9255 | 123.1456 | 67.4071 | -123.2022 | 122.8946 | 123.0815 | 122.8786 | 67.4106 | -123.4894
3210.7969 | 123.1201 | -67.5797 | 55.4718 | -0.010607 | 0.027042 | -0.0014615 | 0.052654 | -0.0088692 | 0.12682 | -0.0074779 | -0.0041211 | -0.00098273 | 0.054185 | 0.04654 | 0.05489 | 55.427 | -0.10848 | -67.5976 | 55.4506 | 55.4099 | 55.6209 | -67.7258 | -67.5807 | -0.11869 | -67.6198 | 55.3607 | 55.5567 | 55.3859 | -68.0222 | -0.14617 | -0.021181 | 123.0067 | -0.017914 | 0.12826 | -0.061877 | 0.14909 | -0.44257 | -0.11112 | -0.001059 | -0.040143 | 0.40243 | 0.084932 | -0.085854 | 123.0303 | 122.9896 | 123.2005 | 67.4712 | -123.1976 | 122.9403 | 123.1364 | 122.9656 | 67.461 | -123.494
3211.7969 | 123.1201 | -67.5842 | 55.5176 | 0.0046549 | 0.027042 | -0.0014615 | 0.052867 | -0.0088692 | 0.12682 | 0.00015261 | -0.0041211 | -0.00055553 | 0.054399 | 0.046754 | 0.05489 | 55.4316 | -0.11306 | -67.6021 | 55.4506 | 55.4053 | 55.6209 | -67.7258 | -67.5807 | -0.11411 | -67.6015 | 55.3607 | 55.5522 | 55.3631 | -68.0268 | -0.1416 | -0.066957 | 123.0158 | -0.017914 | 0.12368 | -0.11223 | 0.10332 | -0.44257 | -0.1569 | 0.003519 | -0.01725 | 0.42532 | 0.034577 | -0.15452 | 123.0348 | 122.9896 | 123.2051 | 67.4712 | -123.2434 | 122.9449 | 123.1364 | 122.9473 | 67.4701 | -123.5444
3212.7969 | 123.1567 | -67.5705 | 55.4855 | 0.0046549 | 0.026188 | -0.0012479 | 0.052654 | -0.0090828 | 0.12682 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054613 | 0.046754 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.446 | 55.4053 | 55.6209 | -67.7212 | -67.5761 | -0.11869 | -67.6015 | 55.3653 | 55.5567 | 55.3859 | -68.0222 | -0.15075 | -0.039493 | 122.9975 | -0.027069 | 0.12368 | -0.080189 | 0.13536 | -0.45172 | -0.12028 | -0.005635 | -0.030983 | 0.42074 | 0.071199 | -0.099587 | 123.0165 | 122.9758 | 123.1914 | 67.4574 | -123.2068 | 122.9358 | 123.1272 | 122.9564 | 67.4518 | -123.5078
3213.7969 | 123.1522 | -67.5385 | 55.4764 | 0.012286 | 0.018282 | 0.0068719 | 0.052867 | -0.0088692 | 0.12682 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054185 | 0.046326 | 0.055103 | 55.4316 | -0.11764 | -67.593 | 55.4506 | 55.4008 | 55.6209 | -67.7258 | -67.5853 | -0.10953 | -67.6106 | 55.3698 | 55.5476 | 55.3585 | -68.0222 | -0.18737 | -0.025758 | 122.97 | -0.054535 | 0.13284 | -0.075612 | 0.14451 | -0.48377 | -0.10654 | -0.046837 | -0.072184 | 0.41158 | 0.071197 | -0.1179 | 122.9891 | 122.9392 | 123.1593 | 67.4208 | -123.2022 | 122.9083 | 123.086 | 122.8969 | 67.4289 | -123.4986
3214.7969 | 123.1155 | -67.6163 | 55.4626 | 0.012286 | 0.01529 | 0.0096497 | 0.052867 | -0.0086556 | 0.1266 | 0.00015261 | -0.0047619 | -0.00076913 | 0.054185 | 0.046326 | 0.05489 | 55.4316 | -0.11306 | -67.6067 | 55.4415 | 55.3916 | 55.6209 | -67.7258 | -67.5853 | -0.11869 | -67.6061 | 55.3653 | 55.5522 | 55.3814 | -68.0222 | -0.10955 | -0.021182 | 123.0479 | 0.00955 | 0.1191 | -0.071037 | 0.15825 | -0.40595 | -0.097387 | 0.030983 | 0.010214 | 0.41616 | 0.089509 | -0.081276 | 123.0577 | 123.0079 | 123.2372 | 67.5032 | -123.1885 | 122.9815 | 123.1684 | 122.9976 | 67.4976 | -123.4849
3215.7969 | 123.2437 | -67.5476 | 55.4306 | -0.0029761 | 0.01059 | 0.01371 | 0.052867 | -0.0090828 | 0.12682 | 0.00015261 | -0.0043347 | -0.00076913 | 0.054399 | 0.046326 | 0.05489 | 55.4316 | -0.11764 | -67.5884 | 55.4369 | 55.3962 | 55.6255 | -67.7304 | -67.5761 | -0.11869 | -67.6152 | 55.3698 | 55.5659 | 55.3676 | -68.0268 | -0.1828 | 0.006283 | 122.9792 | -0.040801 | 0.142 | -0.034415 | 0.19487 | -0.47919 | -0.060766 | -0.028524 | -0.067608 | 0.41158 | 0.13529 | -0.062969 | 122.9845 | 122.9438 | 123.1731 | 67.43 | -123.161 | 122.9174 | 123.1135 | 122.9152 | 67.4289 | -123.4574
3216.7969 | 123.143 | -67.5842 | 55.4993 | 0.012286 | 0.0050342 | 0.019479 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | -0.0041211 | -0.00055553 | 0.054399 | 0.046754 | 0.054676 | 55.4316 | -0.12222 | -67.5976 | 55.4506 | 55.4191 | 55.6255 | -67.735 | -67.5807 | -0.11869 | -67.6152 | 55.3653 | 55.5567 | 55.3814 | -68.0222 | -0.15075 | -0.048647 | 123.0158 | -0.013336 | 0.13742 | -0.080185 | 0.1262 | -0.43799 | -0.13401 | 0.003519 | -0.030986 | 0.407 | 0.057466 | -0.1179 | 123.0348 | 123.0033 | 123.2097 | 67.462 | -123.2343 | 122.9495 | 123.141 | 122.9656 | 67.4655 | -123.5215
3217.7969 | 123.1613 | -67.5613 | 55.4947 | -0.0029761 | 0.0003334 | 0.023753 | 0.052867 | -0.0086556 | 0.12639 | 0.0077831 | -0.0045483 | -0.00034193 | 0.054185 | 0.04654 | 0.05489 | 55.427 | -0.11764 | -67.5884 | 55.4506 | 55.4053 | 55.6209 | -67.7304 | -67.5807 | -0.11869 | -67.6106 | 55.3561 | 55.5567 | 55.3814 | -68.0268 | -0.16906 | -0.044069 | 122.9884 | -0.027068 | 0.142 | -0.089344 | 0.1262 | -0.46546 | -0.13859 | -0.01937 | -0.049296 | 0.41616 | 0.062044 | -0.11332 | 123.012 | 122.9667 | 123.1822 | 67.4437 | -123.2251 | 122.9174 | 123.1181 | 122.9427 | 67.4427 | -123.5215
3218.7969 | 123.1522 | -67.5751 | 55.4855 | -0.0029761 | -0.0015898 | 0.025889 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | -0.0041211 | -0.00076913 | 0.054613 | 0.04654 | 0.054676 | 55.4316 | -0.11764 | -67.5976 | 55.4506 | 55.3962 | 55.63 | -67.7258 | -67.5716 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.3722 | -68.0176 | -0.15075 | -0.034914 | 123.0067 | -0.022492 | 0.12826 | -0.089347 | 0.14451 | -0.44257 | -0.12028 | 0.003521 | -0.035563 | 0.407 | 0.071199 | -0.11332 | 123.0257 | 122.9713 | 123.2051 | 67.4574 | -123.2114 | 122.9403 | 123.1318 | 122.9473 | 67.461 | -123.5032
3219.7969 | 123.1247 | -67.6117 | 55.4535 | 0.0046549 | -0.0024444 | 0.02653 | 0.052867 | -0.0086556 | 0.12639 | 0.00015261 | -0.0039075 | -0.00098273 | 0.054185 | 0.046754 | 0.055103 | 55.4316 | -0.11306 | -67.5976 | 55.446 | 55.4053 | 55.6209 | -67.7304 | -67.5807 | -0.11411 | -67.6061 | 55.3698 | 55.5613 | 55.3859 | -68.0268 | -0.11871 | -0.007449 | 123.0433 | 0.014129 | 0.13284 | -0.048145 | 0.1674 | -0.4151 | -0.083654 | 0.030984 | 0.005636 | 0.42074 | 0.10782 | -0.067543 | 123.0577 | 123.017 | 123.2326 | 67.4986 | -123.1839 | 122.9815 | 123.173 | 122.9976 | 67.4976 | -123.4803
3220.7969 | 123.1888 | -67.5797 | 55.4306 | -0.0029761 | -0.0028718 | 0.027171 | 0.053081 | -0.0086556 | 0.12682 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054185 | 0.046754 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.446 | 55.3962 | 55.6163 | -67.7258 | -67.5807 | -0.11411 | -67.6106 | 55.3607 | 55.5613 | 55.3814 | -68.0268 | -0.14617 | 0.015439 | 123.0067 | -0.017914 | 0.12826 | -0.034415 | 0.18571 | -0.44715 | -0.069923 | -0.001059 | -0.030985 | 0.41616 | 0.13071 | -0.049233 | 123.0257 | 122.9758 | 123.196 | 67.4666 | -123.1564 | 122.9403 | 123.141 | 122.961 | 67.4655 | -123.4574
3221.7969 | 123.0927 | -67.5522 | 55.5222 | -0.0029761 | -0.003299 | 0.027812 | 0.053081 | -0.0090828 | 0.1266 | 0.0077831 | -0.0043347 | -0.00034193 | 0.054613 | 0.046754 | 0.054676 | 55.4224 | -0.11764 | -67.593 | 55.446 | 55.4008 | 55.6255 | -67.7304 | -67.5807 | -0.10953 | -67.6152 | 55.3607 | 55.5522 | 55.3768 | -68.0222 | -0.17822 | -0.076114 | 122.9746 | -0.040802 | 0.13742 | -0.12139 | 0.10331 | -0.47004 | -0.16148 | -0.028525 | -0.06303 | 0.407 | 0.029999 | -0.14537 | 122.9982 | 122.953 | 123.1777 | 67.4345 | -123.2526 | 122.9129 | 123.1043 | 122.929 | 67.4427 | -123.5444
3222.8594 | 123.1659 | -67.5613 | 55.5084 | -0.0029761 | -0.0037264 | 0.027812 | 0.052867 | -0.0088692 | 0.12682 | 0.015414 | -0.0043347 | -0.00034193 | 0.054613 | 0.046754 | 0.05489 | 55.4407 | -0.11306 | -67.593 | 55.4552 | 55.4053 | 55.6255 | -67.7396 | -67.5853 | -0.11411 | -67.6106 | 55.3698 | 55.5567 | 55.3676 | -68.0268 | -0.17822 | -0.053224 | 123.0021 | -0.031647 | 0.14658 | -0.10308 | 0.11705 | -0.46546 | -0.13859 | -0.023949 | -0.049296 | 0.41616 | 0.048311 | -0.14079 | 123.0165 | 122.9667 | 123.1868 | 67.4483 | -123.248 | 122.9312 | 123.1181 | 122.929 | 67.4472 | -123.5352
3223.7969 | 123.1934 | -67.5568 | 55.513 | 0.012286 | -0.0037264 | 0.028453 | 0.05244 | -0.0090828 | 0.12682 | -0.0074779 | -0.0045483 | -0.00055553 | 0.054399 | 0.046754 | 0.055103 | 55.4316 | -0.11764 | -67.5976 | 55.4552 | 55.387 | 55.63 | -67.7304 | -67.5807 | -0.11411 | -67.6106 | 55.3607 | 55.5567 | 55.3951 | -68.0176 | -0.17364 | -0.057801 | 122.9884 | -0.040802 | 0.13284 | -0.12597 | 0.11705 | -0.46088 | -0.15232 | -0.023947 | -0.053873 | 0.407 | 0.043734 | -0.11789 | 123.012 | 122.9438 | 123.1868 | 67.4391 | -123.2434 | 122.9174 | 123.1135 | 122.9519 | 67.4427 | -123.5306
3224.7969 | 123.2162 | -67.5842 | 55.4077 | -0.010607 | -0.0041538 | 0.028026 | 0.052654 | -0.0088692 | 0.12682 | -0.0074779 | -0.0041211 | -0.00034193 | 0.054613 | 0.046967 | 0.05489 | 55.4362 | -0.12222 | -67.5976 | 55.4415 | 55.3916 | 55.6163 | -67.7212 | -67.5807 | -0.11411 | -67.6198 | 55.3607 | 55.5613 | 55.3676 | -68.0176 | -0.13702 | 0.033749 | 123.0204 | -0.013336 | 0.12368 | -0.016106 | 0.2086 | -0.43341 | -0.047035 | 0.003519 | -0.035565 | 0.39785 | 0.1536 | -0.040081 | 123.0257 | 122.9758 | 123.2005 | 67.462 | -123.129 | 122.9449 | 123.1455 | 122.9519 | 67.4701 | -123.4254
3225.7969 | 123.2346 | -67.5522 | 55.4306 | -0.0029761 | -0.0039402 | 0.028453 | 0.052867 | -0.0090828 | 0.1266 | 0.0077831 | -0.0041211 | -0.00034193 | 0.054613 | 0.046754 | 0.054462 | 55.4362 | -0.11306 | -67.6021 | 55.4369 | 55.3962 | 55.6209 | -67.7304 | -67.5853 | -0.10495 | -67.6106 | 55.3607 | 55.5613 | 55.3585 | -68.0222 | -0.17822 | 0.006283 | 122.9884 | -0.049958 | 0.12826 | -0.034415 | 0.19029 | -0.47004 | -0.069923 | -0.033104 | -0.058451 | 0.41158 | 0.13071 | -0.072127 | 122.9891 | 122.9484 | 123.1731 | 67.4391 | -123.161 | 122.9129 | 123.1135 | 122.9107 | 67.4472 | -123.4528
3226.7969 | 123.1522 | -67.5842 | 55.4901 | -0.0029761 | -0.0039402 | 0.028026 | 0.052654 | -0.0086556 | 0.1266 | 0.00015261 | -0.0043347 | -0.00055553 | 0.054613 | 0.046754 | 0.054676 | 55.4316 | -0.11764 | -67.6159 | 55.4506 | 55.3962 | 55.63 | -67.7396 | -67.5853 | -0.10495 | -67.6152 | 55.3607 | 55.5613 | 55.3722 | -68.0222 | -0.15533 | -0.039491 | 123.0158 | -0.031649 | 0.12368 | -0.093924 | 0.13994 | -0.43799 | -0.12943 | -0.00106 | -0.030986 | 0.407 | 0.0712 | -0.1179 | 123.0348 | 122.9804 | 123.2143 | 67.4666 | -123.2297 | 122.9449 | 123.1455 | 122.9564 | 67.4793 | -123.5123
3227.7969 | 123.1293 | -67.5659 | 55.481 | -0.010607 | -0.0041538 | 0.028667 | 0.052654 | -0.0086556 | 0.1266 | 0.0077831 | -0.0043347 | -0.00055553 | 0.054185 | 0.04654 | 0.055103 | 55.427 | -0.11306 | -67.6113 | 55.4506 | 55.3916 | 55.6255 | -67.7258 | -67.5853 | -0.10953 | -67.6106 | 55.3561 | 55.5567 | 55.3722 | -68.0222 | -0.15991 | -0.030336 | 122.9929 | -0.045382 | 0.11453 | -0.089348 | 0.14451 | -0.4563 | -0.12485 | -0.019371 | -0.044718 | 0.41158 | 0.075777 | -0.10874 | 123.0165 | 122.9575 | 123.1914 | 67.4529 | -123.2068 | 122.922 | 123.1227 | 122.9381 | 67.4564 | -123.5032
3228.7969 | 123.1384 | -67.5842 | 55.4718 | -0.0029761 | -0.0043674 | 0.028667 | 0.053081 | -0.0088692 | 0.12639 | 0.015414 | -0.0043347 | -0.00076913 | 0.054613 | 0.04654 | 0.05489 | 55.427 | -0.11306 | -67.5976 | 55.4552 | 55.4053 | 55.6255 | -67.7304 | -67.5761 | -0.10953 | -67.6106 | 55.3515 | 55.5522 | 55.3722 | -68.0176 | -0.14617 | -0.016603 | 123.0112 | -0.013336 | 0.13284 | -0.066456 | 0.15367 | -0.43341 | -0.12028 | 0.008098 | -0.026407 | 0.407 | 0.080353 | -0.09959 | 123.0394 | 122.9896 | 123.2097 | 67.4712 | -123.2022 | 122.9358 | 123.1364 | 122.9564 | 67.4747 | -123.4894
3229.7969 | 123.1613 | -67.6163 | 55.4306 | -0.0029761 | -0.0045812 | 0.028453 | 0.052867 | -0.0090828 | 0.12639 | -0.0074779 | -0.0043347 | -0.00034193 | 0.054185 | 0.046754 | 0.05489 | 55.4362 | -0.11764 | -67.5976 | 55.446 | 55.3962 | 55.6209 | -67.7304 | -67.5853 | -0.10953 | -67.6106 | 55.3607 | 55.5567 | 55.3631 | -68.0176 | -0.11413 | 0.015439 | 123.0524 | 0.018707 | 0.13284 | -0.034415 | 0.19029 | -0.40137 | -0.069923 | 0.030983 | 0.005636 | 0.407 | 0.12613 | -0.067548 | 123.0623 | 123.0125 | 123.2372 | 67.4986 | -123.161 | 122.977 | 123.173 | 122.9793 | 67.5067 | -123.4482
3230.7969 | 123.1338 | -67.6025 | 55.4581 | -0.010607 | -0.0047948 | 0.02824 | 0.052867 | -0.0090828 | 0.12639 | -0.0074779 | -0.0041211 | -0.00055553 | 0.054399 | 0.046326 | 0.055103 | 55.4362 | -0.11306 | -67.6067 | 55.446 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.10953 | -67.6106 | 55.3698 | 55.5613 | 55.3585 | -68.0268 | -0.12329 | -0.012027 | 123.0387 | -0.004183 | 0.1191 | -0.061881 | 0.16282 | -0.42426 | -0.088232 | 0.021829 | -0.008097 | 0.41616 | 0.10324 | -0.099593 | 123.0486 | 122.9987 | 123.2234 | 67.4895 | -123.1839 | 122.9724 | 123.1639 | 122.961 | 67.493 | -123.4849
3231.7969 | 123.175 | -67.5705 | 55.4535 | -0.0029761 | -0.0045812 | 0.028453 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | -0.0043347 | -0.00012813 | 0.054185 | 0.046967 | 0.055103 | 55.4362 | -0.11306 | -67.6067 | 55.4552 | 55.3962 | 55.63 | -67.7258 | -67.5807 | -0.11869 | -67.6152 | 55.3607 | 55.5613 | 55.3631 | -68.0131 | -0.15533 | 0.001708 | 123.0067 | -0.036226 | 0.1191 | -0.057303 | 0.17656 | -0.44257 | -0.092811 | -0.010214 | -0.044719 | 0.39785 | 0.10782 | -0.090436 | 123.0257 | 122.9667 | 123.2005 | 67.4574 | -123.1793 | 122.9312 | 123.1318 | 122.9336 | 67.4518 | -123.4666
3232.7969 | 123.143 | -67.598 | 55.4626 | 0.0046549 | -0.0045812 | 0.028881 | 0.052654 | -0.0092964 | 0.12682 | 0.0077831 | -0.0045483 | -0.00034193 | 0.054185 | 0.04654 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.4506 | 55.3962 | 55.6255 | -67.7304 | -67.5807 | -0.10495 | -67.6061 | 55.3607 | 55.5659 | 55.3493 | -68.0222 | -0.13244 | -0.012025 | 123.025 | 0.000396 | 0.13284 | -0.066458 | 0.16282 | -0.42426 | -0.10197 | 0.017251 | -0.008097 | 0.41616 | 0.10325 | -0.11333 | 123.0486 | 122.9941 | 123.2234 | 67.4849 | -123.193 | 122.9586 | 123.1639 | 122.9473 | 67.493 | -123.4849
3233.7969 | 123.175 | -67.5888 | 55.4626 | -0.0029761 | -0.0050084 | 0.028881 | 0.052654 | -0.0090828 | 0.12639 | 0.00015261 | -0.0043347 | -0.00034193 | 0.053972 | 0.046967 | 0.055317 | 55.4362 | -0.12222 | -67.5976 | 55.4506 | 55.3962 | 55.6255 | -67.7258 | -67.5853 | -0.11411 | -67.6061 | 55.3607 | 55.5613 | 55.3585 | -68.0222 | -0.13702 | -0.012025 | 123.025 | -0.008759 | 0.12826 | -0.066458 | 0.16282 | -0.43341 | -0.10197 | 0.003517 | -0.017252 | 0.41616 | 0.098666 | -0.10417 | 123.0394 | 122.985 | 123.2143 | 67.4666 | -123.1885 | 122.9495 | 123.1501 | 122.9473 | 67.4747 | -123.4849
3234.7969 | 123.2254 | -67.5613 | 55.4077 | -0.0029761 | -0.0045812 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | 0.0077831 | -0.0043347 | -0.00076913 | 0.053972 | 0.046754 | 0.05489 | 55.427 | -0.11764 | -67.6021 | 55.446 | 55.4008 | 55.6209 | -67.7167 | -67.5853 | -0.10495 | -67.6106 | 55.3561 | 55.5613 | 55.3539 | -68.0176 | -0.15533 | 0.038327 | 122.9884 | -0.040803 | 0.11452 | -0.006948 | 0.21318 | -0.4563 | -0.051613 | -0.023949 | -0.049296 | 0.407 | 0.1536 | -0.053817 | 123.0074 | 122.9621 | 123.1822 | 67.4437 | -123.1244 | 122.9174 | 123.1227 | 122.9152 | 67.4564 | -123.4254
3235.7969 | 123.2574 | -67.5522 | 55.4489 | -0.0029761 | -0.0045812 | 0.028453 | 0.052654 | -0.0090828 | 0.1266 | -0.0074779 | 0.0027153 | -0.00055553 | 0.047349 | 0.04654 | 0.055103 | 55.4316 | -0.11306 | -67.6067 | 55.446 | 55.3962 | 55.6255 | -67.7212 | -67.5853 | -0.11869 | -67.6106 | 55.3561 | 55.5567 | 55.3539 | -68.0222 | -0.16906 | -0.002872 | 122.9838 | -0.054537 | 0.11452 | -0.052726 | 0.17656 | -0.47004 | -0.092812 | -0.033104 | -0.058451 | 0.41158 | 0.10782 | -0.095016 | 122.9982 | 122.9484 | 123.1777 | 67.4391 | -123.1702 | 122.9083 | 123.1089 | 122.9061 | 67.4335 | -123.4711
3236.7969 | 123.1476 | -67.5705 | 55.4352 | -0.010607 | -0.0043674 | 0.029094 | 0.052867 | -0.0088692 | 0.1266 | -0.0074779 | 0.017456 | -0.00098273 | 0.032393 | 0.046754 | 0.054676 | 55.427 | -0.11306 | -67.6067 | 55.4415 | 55.3962 | 55.6255 | -67.7212 | -67.5853 | -0.10953 | -67.6061 | 55.3561 | 55.5567 | 55.3722 | -68.0176 | -0.15075 | 0.006283 | 122.9975 | -0.036226 | 0.11452 | -0.038993 | 0.19029 | -0.44714 | -0.079079 | -0.014793 | -0.035562 | 0.41158 | 0.12155 | -0.062969 | 123.012 | 122.9667 | 123.196 | 67.4574 | -123.1564 | 122.9266 | 123.1272 | 122.9427 | 67.461 | -123.4528
3237.7969 | 123.1842 | -67.5842 | 55.4718 | 0.0046549 | -0.0047948 | 0.028667 | 0.05244 | -0.0090828 | 0.12703 | -0.0074779 | 0.022584 | -0.00055553 | 0.027266 | 0.046754 | 0.055103 | 55.427 | -0.11764 | -67.6067 | 55.4506 | 55.3962 | 55.6255 | -67.7304 | -67.5761 | -0.11869 | -67.6061 | 55.3607 | 55.5613 | 55.3631 | -68.0176 | -0.14617 | -0.021181 | 123.0112 | -0.022493 | 0.12368 | -0.075614 | 0.15367 | -0.43341 | -0.11112 | 0.008098 | -0.021829 | 0.41158 | 0.08951 | -0.10875 | 123.0348 | 122.9804 | 123.2097 | 67.4666 | -123.2022 | 122.9449 | 123.1455 | 122.9473 | 67.4655 | -123.4894
3238.7969 | 123.2162 | -67.5751 | 55.426 | -0.0029761 | -0.0047948 | 0.028881 | 0.052867 | -0.0090828 | 0.1266 | -0.0074779 | 0.024079 | -0.00055553 | 0.02577 | 0.046326 | 0.055317 | 55.4316 | -0.10848 | -67.5976 | 55.4552 | 55.3779 | 55.6163 | -67.7212 | -67.5853 | -0.10495 | -67.6061 | 55.3653 | 55.5613 | 55.3585 | -68.0222 | -0.14617 | 0.029174 | 123.0067 | -0.022492 | 0.12368 | -0.048153 | 0.19029 | -0.44715 | -0.060766 | -0.010216 | -0.030985 | 0.41616 | 0.13529 | -0.067549 | 123.0303 | 122.9529 | 123.1914 | 67.4666 | -123.1473 | 122.9403 | 123.1364 | 122.9335 | 67.4701 | -123.4482
3239.7969 | 123.23 | -67.5842 | 55.4352 | -0.010607 | -0.0047948 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | -0.0074779 | 0.022797 | 0.0032903 | 0.022993 | 0.046967 | 0.05489 | 55.427 | -0.1039 | -67.593 | 55.4415 | 55.3962 | 55.6255 | -67.7258 | -67.5807 | -0.10953 | -67.6152 | 55.3607 | 55.5613 | 55.3722 | -68.0176 | -0.1416 | 0.006283 | 123.0112 | -0.008758 | 0.13284 | -0.038993 | 0.19029 | -0.43341 | -0.074501 | 0.003519 | -0.030986 | 0.40243 | 0.12613 | -0.062969 | 123.0257 | 122.9804 | 123.2097 | 67.4803 | -123.161 | 122.9449 | 123.1455 | 122.9564 | 67.4747 | -123.4528
3240.7969 | 123.2391 | -67.5568 | 55.4214 | -0.010607 | -0.0050084 | 0.029094 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | 0.021943 | 0.0062815 | 0.021497 | 0.046967 | 0.054676 | 55.4362 | -0.10848 | -67.593 | 55.4415 | 55.3916 | 55.6255 | -67.7304 | -67.5807 | -0.10495 | -67.6061 | 55.3607 | 55.5613 | 55.3539 | -68.0268 | -0.17364 | 0.020016 | 122.9929 | -0.036224 | 0.13742 | -0.029839 | 0.20402 | -0.47003 | -0.060768 | -0.023947 | -0.049295 | 0.42074 | 0.13986 | -0.06755 | 122.9982 | 122.9484 | 123.1822 | 67.4483 | -123.1519 | 122.9174 | 123.1181 | 122.9107 | 67.4518 | -123.4482
3241.7969 | 123.2117 | -67.5293 | 55.4489 | -0.0029761 | -0.0050084 | 0.029094 | 0.053081 | -0.0090828 | 0.12682 | -0.0074779 | 0.020447 | 0.0090591 | 0.019574 | 0.046326 | 0.054676 | 55.427 | -0.11306 | -67.5976 | 55.4415 | 55.3962 | 55.6255 | -67.7212 | -67.5853 | -0.10953 | -67.6061 | 55.3698 | 55.5522 | 55.3676 | -68.0176 | -0.19195 | -0.00745 | 122.9563 | -0.068268 | 0.12368 | -0.052726 | 0.17656 | -0.48834 | -0.079077 | -0.055992 | -0.076761 | 0.41158 | 0.10324 | -0.08128 | 122.9708 | 122.9255 | 123.1548 | 67.4162 | -123.1702 | 122.8991 | 123.0815 | 122.8969 | 67.4198 | -123.4666
3242.7969 | 123.2254 | -67.5522 | 55.4581 | 0.0046549 | -0.0047948 | 0.029308 | 0.053081 | -0.0092964 | 0.1266 | 0.00015261 | 0.019593 | 0.011837 | 0.018506 | 0.046967 | 0.055103 | 55.4316 | -0.10848 | -67.593 | 55.4369 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.11869 | -67.6061 | 55.3653 | 55.5613 | 55.3951 | -68.0222 | -0.17364 | -0.021183 | 122.9838 | -0.040802 | 0.13284 | -0.061881 | 0.16282 | -0.47004 | -0.09281 | -0.028525 | -0.053873 | 0.41616 | 0.10324 | -0.062964 | 122.9891 | 122.9484 | 123.1731 | 67.4437 | -123.1839 | 122.9174 | 123.1135 | 122.9473 | 67.4335 | -123.4803
3243.7969 | 123.2162 | -67.5659 | 55.4581 | -0.0029761 | -0.0050084 | 0.029308 | 0.052654 | -0.0086556 | 0.12639 | -0.0074779 | 0.018738 | 0.012691 | 0.017652 | 0.04654 | 0.055103 | 55.427 | -0.11306 | -67.5884 | 55.4415 | 55.4145 | 55.6209 | -67.7258 | -67.5853 | -0.11411 | -67.6061 | 55.3607 | 55.5613 | 55.3676 | -68.0176 | -0.15991 | -0.016605 | 122.9929 | -0.02249 | 0.13742 | -0.043565 | 0.16282 | -0.45172 | -0.097389 | -0.019371 | -0.04014 | 0.41158 | 0.10324 | -0.090435 | 123.0074 | 122.9804 | 123.1868 | 67.4529 | -123.1839 | 122.9266 | 123.1272 | 122.9336 | 67.4518 | -123.4757
3244.7969 | 123.2346 | -67.5659 | 55.4672 | -0.0029761 | -0.0047948 | 0.028881 | 0.052867 | -0.0090828 | 0.1266 | 0.00015261 | 0.018524 | 0.014401 | 0.016583 | 0.046754 | 0.054676 | 55.4362 | -0.11764 | -67.593 | 55.446 | 55.3962 | 55.6255 | -67.7167 | -67.5807 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.3676 | -68.0222 | -0.15075 | -0.021182 | 123.0021 | -0.027069 | 0.12368 | -0.071036 | 0.15825 | -0.4563 | -0.10196 | -0.014792 | -0.044718 | 0.41158 | 0.08951 | -0.09959 | 123.012 | 122.9621 | 123.1914 | 67.4483 | -123.1839 | 122.9312 | 123.1227 | 122.9336 | 67.4518 | -123.4894
3245.7969 | 123.2437 | -67.5705 | 55.426 | -0.0029761 | -0.0047948 | 0.029094 | 0.052654 | -0.0084418 | 0.1266 | 0.00015261 | 0.01767 | 0.015896 | 0.016156 | 0.046754 | 0.054676 | 55.4316 | -0.11306 | -67.5976 | 55.4415 | 55.4008 | 55.6346 | -67.7258 | -67.5853 | -0.11869 | -67.6061 | 55.3607 | 55.5567 | 55.3676 | -68.0268 | -0.15533 | 0.015439 | 123.0021 | -0.027069 | 0.12826 | -0.025258 | 0.2086 | -0.4563 | -0.065345 | -0.014793 | -0.035562 | 0.42074 | 0.13071 | -0.058391 | 123.012 | 122.9713 | 123.2051 | 67.4574 | -123.1518 | 122.9312 | 123.1272 | 122.9381 | 67.4518 | -123.4528
3246.7969 | 123.2483 | -67.5201 | 55.4443 | 0.012286 | -0.0047948 | 0.029094 | 0.052654 | -0.0086556 | 0.12682 | 0.0077831 | 0.01767 | 0.016751 | 0.015301 | 0.04654 | 0.055103 | 55.427 | -0.11306 | -67.5976 | 55.4415 | 55.3962 | 55.6255 | -67.7258 | -67.5807 | -0.10953 | -67.6106 | 55.3607 | 55.5567 | 55.3905 | -68.0222 | -0.20568 | -0.002872 | 122.9472 | -0.077423 | 0.12826 | -0.048148 | 0.18113 | -0.50208 | -0.083656 | -0.060568 | -0.090494 | 0.41158 | 0.1124 | -0.053809 | 122.9616 | 122.9163 | 123.1456 | 67.4071 | -123.1702 | 122.8808 | 123.0769 | 122.9107 | 67.4106 | -123.4666
3247.7969 | 123.2071 | -67.5705 | 55.4764 | 0.012286 | -0.0050084 | 0.028667 | 0.052867 | -0.0090828 | 0.1266 | 0.015414 | 0.017243 | 0.016751 | 0.015301 | 0.046754 | 0.05489 | 55.427 | -0.11306 | -67.5976 | 55.4415 | 55.387 | 55.6209 | -67.7167 | -67.5807 | -0.10953 | -67.6106 | 55.3653 | 55.5567 | 55.3722 | -68.0222 | -0.14617 | -0.034915 | 122.9975 | -0.027069 | 0.1191 | -0.089349 | 0.14451 | -0.45172 | -0.11112 | -0.010214 | -0.04014 | 0.41158 | 0.080355 | -0.10417 | 123.012 | 122.9575 | 123.1914 | 67.4574 | -123.193 | 122.9358 | 123.1272 | 122.9427 | 67.461 | -123.4986
3248.7969 | 123.2437 | -67.511 | 55.4443 | -0.0029761 | -0.0045812 | 0.029094 | 0.053081 | -0.0090828 | 0.12639 | 0.0077831 | 0.017243 | 0.017178 | 0.014874 | 0.046754 | 0.054676 | 55.427 | -0.10848 | -67.5976 | 55.446 | 55.3962 | 55.6117 | -67.7258 | -67.5899 | -0.11869 | -67.6106 | 55.3653 | 55.5522 | 55.3722 | -68.0222 | -0.21484 | 0.001706 | 122.938 | -0.086579 | 0.12826 | -0.048148 | 0.1674 | -0.51123 | -0.079077 | -0.078881 | -0.09965 | 0.41158 | 0.10782 | -0.072124 | 122.957 | 122.9072 | 123.1227 | 67.4025 | -123.1702 | 122.8762 | 123.0631 | 122.8832 | 67.3923 | -123.4666
3249.7969 | 123.1705 | -67.543 | 55.4764 | 0.0046549 | -0.0050084 | 0.028881 | 0.05244 | -0.0086556 | 0.12682 | 0.0077831 | 0.017029 | 0.017392 | 0.014874 | 0.046754 | 0.05489 | 55.4316 | -0.11764 | -67.5976 | 55.4506 | 55.3962 | 55.6209 | -67.7304 | -67.5807 | -0.11411 | -67.6061 | 55.3607 | 55.5567 | 55.3722 | -68.0176 | -0.18737 | -0.025758 | 122.9746 | -0.054535 | 0.13284 | -0.080191 | 0.14451 | -0.47461 | -0.1157 | -0.03768 | -0.063028 | 0.41158 | 0.080355 | -0.10417 | 122.9937 | 122.9392 | 123.1639 | 67.4254 | -123.2068 | 122.9037 | 123.0998 | 122.9152 | 67.4289 | -123.494
3250.7969 | 123.23 | -67.5293 | 55.4718 | 0.0046549 | -0.0047948 | 0.028453 | 0.052867 | -0.0086556 | 0.12639 | 0.0077831 | 0.017243 | 0.018033 | 0.014447 | 0.046967 | 0.05489 | 55.4316 | -0.11306 | -67.6021 | 55.446 | 55.3962 | 55.6255 | -67.7212 | -67.5807 | -0.10953 | -67.6061 | 55.3561 | 55.5567 | 55.3676 | -68.0268 | -0.19195 | -0.02576 | 122.9609 | -0.072846 | 0.1191 | -0.075614 | 0.15367 | -0.4975 | -0.1157 | -0.051413 | -0.076761 | 0.42074 | 0.084932 | -0.10417 | 122.9753 | 122.9255 | 123.1548 | 67.4162 | -123.193 | 122.8854 | 123.086 | 122.8969 | 67.4198 | -123.4986
3251.7969 | 123.1796 | -67.5613 | 55.4306 | -0.0029761 | -0.0047948 | 0.029094 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | 0.017456 | 0.018033 | 0.014447 | 0.047181 | 0.05489 | 55.4316 | -0.11306 | -67.5976 | 55.446 | 55.3916 | 55.63 | -67.7304 | -67.5807 | -0.11869 | -67.6015 | 55.3561 | 55.5659 | 55.3722 | -68.0222 | -0.16906 | 0.015439 | 122.9929 | -0.036225 | 0.13284 | -0.038994 | 0.19945 | -0.46088 | -0.074501 | -0.01937 | -0.040139 | 0.42074 | 0.13529 | -0.058391 | 123.0074 | 122.9529 | 123.1914 | 67.4483 | -123.161 | 122.9174 | 123.1272 | 122.9336 | 67.4427 | -123.4528
3252.7969 | 123.2712 | -67.5339 | 55.4489 | 0.0046549 | -0.0052222 | 0.029094 | 0.053295 | -0.0086556 | 0.12703 | 0.015414 | 0.017029 | 0.018674 | 0.014019 | 0.046967 | 0.054676 | 55.4316 | -0.11764 | -67.593 | 55.446 | 55.3962 | 55.63 | -67.7258 | -67.5807 | -0.11411 | -67.6061 | 55.3607 | 55.5567 | 55.3905 | -68.0222 | -0.19195 | -0.002872 | 122.9655 | -0.059112 | 0.13284 | -0.052726 | 0.18114 | -0.48835 | -0.088234 | -0.046835 | -0.072183 | 0.41616 | 0.10782 | -0.058387 | 122.9799 | 122.9301 | 123.1639 | 67.4162 | -123.1747 | 122.8946 | 123.0906 | 122.9244 | 67.4198 | -123.4711
3253.7969 | 123.23 | -67.5247 | 55.4443 | 0.012286 | -0.0052222 | 0.028881 | 0.052867 | -0.0086556 | 0.1266 | 0.0077831 | 0.017029 | 0.01846 | 0.014233 | 0.046967 | 0.055103 | 55.4362 | -0.11306 | -67.5976 | 55.4506 | 55.3916 | 55.6209 | -67.7212 | -67.5807 | -0.10495 | -67.6106 | 55.3607 | 55.5613 | 55.3905 | -68.0268 | -0.19653 | 0.006285 | 122.9609 | -0.072846 | 0.12368 | -0.052727 | 0.17656 | -0.50208 | -0.083656 | -0.055991 | -0.085917 | 0.41616 | 0.11698 | -0.053809 | 122.9753 | 122.9163 | 123.1456 | 67.4117 | -123.1656 | 122.8854 | 123.086 | 122.9152 | 67.4198 | -123.4711
3254.7969 | 123.2529 | -67.5247 | 55.4489 | -0.0029761 | -0.0054358 | 0.028881 | 0.052867 | -0.0090828 | 0.12639 | 0.015414 | 0.017029 | 0.018674 | 0.013806 | 0.046967 | 0.054676 | 55.427 | -0.11306 | -67.593 | 55.446 | 55.4053 | 55.6255 | -67.7304 | -67.5853 | -0.10495 | -67.6061 | 55.3653 | 55.5476 | 55.3859 | -68.0176 | -0.20568 | -0.002872 | 122.9517 | -0.068268 | 0.13742 | -0.043568 | 0.17656 | -0.49292 | -0.083655 | -0.06057 | -0.081339 | 0.41158 | 0.098662 | -0.062966 | 122.9708 | 122.9301 | 123.1502 | 67.4117 | -123.1793 | 122.89 | 123.0723 | 122.9107 | 67.4198 | -123.4666
3255.7969 | 123.2437 | -67.5247 | 55.4626 | -0.0029761 | -0.0052222 | 0.028667 | 0.052867 | -0.0086556 | 0.12682 | 0.0077831 | 0.016602 | 0.018674 | 0.013592 | 0.046754 | 0.054676 | 55.4224 | -0.11306 | -67.593 | 55.4506 | 55.4008 | 55.6255 | -67.7212 | -67.5761 | -0.11411 | -67.6106 | 55.3653 | 55.5522 | 55.3768 | -68.0176 | -0.19653 | -0.012025 | 122.9472 | -0.068268 | 0.12826 | -0.061879 | 0.16282 | -0.49292 | -0.097387 | -0.051412 | -0.085917 | 0.407 | 0.089509 | -0.085855 | 122.9753 | 122.9255 | 123.1502 | 67.4117 | -123.1839 | 122.89 | 123.0769 | 122.9015 | 67.4106 | -123.4803
3256.7969 | 123.2162 | -67.5385 | 55.4626 | -0.0029761 | -0.0052222 | 0.028667 | 0.05244 | -0.0088692 | 0.1266 | 0.0077831 | 0.017029 | 0.018887 | 0.013592 | 0.046967 | 0.054676 | 55.4224 | -0.11306 | -67.593 | 55.446 | 55.3916 | 55.6209 | -67.7304 | -67.5716 | -0.11411 | -67.6015 | 55.3607 | 55.5613 | 55.3631 | -68.0176 | -0.19195 | -0.016604 | 122.9609 | -0.054535 | 0.13742 | -0.071037 | 0.15825 | -0.47919 | -0.10197 | -0.0331 | -0.063027 | 0.41616 | 0.098666 | -0.099591 | 122.9845 | 122.9301 | 123.1593 | 67.4254 | -123.193 | 122.8991 | 123.0998 | 122.9015 | 67.4243 | -123.4803
3257.7969 | 123.2346 | -67.5476 | 55.4352 | -0.0029761 | -0.0054358 | 0.028667 | 0.052867 | -0.0090828 | 0.12703 | 0.015414 | 0.016815 | 0.018887 | 0.013806 | 0.047181 | 0.054462 | 55.427 | -0.11306 | -67.5976 | 55.446 | 55.3825 | 55.6117 | -67.7258 | -67.5807 | -0.10953 | -67.6061 | 55.3698 | 55.5522 | 55.3814 | -68.0268 | -0.17822 | 0.010861 | 122.9746 | -0.049958 | 0.12826 | -0.05273 | 0.17655 | -0.47919 | -0.065344 | -0.033103 | -0.058451 | 0.42074 | 0.11697 | -0.053811 | 122.9936 | 122.9301 | 123.1593 | 67.4345 | -123.161 | 122.9174 | 123.0998 | 122.929 | 67.4381 | -123.462
3258.7969 | 123.2437 | -67.5247 | 55.4764 | -0.0029761 | -0.0052222 | 0.029094 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | 0.016815 | 0.018887 | 0.013165 | 0.046967 | 0.05489 | 55.4362 | -0.11306 | -67.593 | 55.4506 | 55.3962 | 55.6209 | -67.7304 | -67.5807 | -0.10953 | -67.6106 | 55.3653 | 55.5659 | 55.3859 | -68.0222 | -0.20568 | -0.025758 | 122.9609 | -0.068268 | 0.13742 | -0.080191 | 0.14451 | -0.4975 | -0.11112 | -0.055991 | -0.085917 | 0.41158 | 0.089512 | -0.090431 | 122.9753 | 122.9209 | 123.1456 | 67.4117 | -123.2068 | 122.89 | 123.0906 | 122.9107 | 67.4152 | -123.4986
3259.7969 | 123.2346 | -67.5201 | 55.481 | -0.0029761 | -0.0052222 | 0.028881 | 0.052867 | -0.0092964 | 0.12682 | 0.0077831 | 0.016602 | 0.018887 | 0.013592 | 0.046967 | 0.054676 | 55.4316 | -0.11306 | -67.5976 | 55.4415 | 55.4008 | 55.6209 | -67.7304 | -67.5807 | -0.11411 | -67.6015 | 55.3561 | 55.5522 | 55.3631 | -68.0222 | -0.21026 | -0.039493 | 122.9517 | -0.077423 | 0.13284 | -0.08019 | 0.13994 | -0.50208 | -0.12485 | -0.060568 | -0.081337 | 0.42074 | 0.071198 | -0.1179 | 122.9616 | 122.9209 | 123.141 | 67.4071 | -123.2114 | 122.8762 | 123.0723 | 122.8832 | 67.406 | -123.5032
3260.8594 | 123.2574 | -67.5293 | 55.4306 | -0.0029761 | -0.0054358 | 0.028881 | 0.052867 | -0.0088692 | 0.1266 | 0.00015261 | 0.017029 | 0.019101 | 0.013379 | 0.046967 | 0.05489 | 55.4316 | -0.10848 | -67.5976 | 55.446 | 55.4008 | 55.6255 | -67.735 | -67.5807 | -0.11411 | -67.6015 | 55.3607 | 55.5567 | 55.3722 | -68.0222 | -0.20569 | 0.015439 | 122.9609 | -0.068268 | 0.13742 | -0.029836 | 0.19487 | -0.49292 | -0.069923 | -0.051413 | -0.072182 | 0.42074 | 0.12613 | -0.058391 | 122.9753 | 122.9301 | 123.1548 | 67.4208 | -123.1656 | 122.89 | 123.086 | 122.9015 | 67.4152 | -123.4528
3261.7969 | 123.2208 | -67.5247 | 55.4764 | -0.0029761 | -0.0050084 | 0.029094 | 0.052867 | -0.0090828 | 0.12682 | 0.0077831 | 0.016388 | 0.019315 | 0.013165 | 0.046967 | 0.05489 | 55.4362 | -0.10848 | -67.593 | 55.446 | 55.4008 | 55.6209 | -67.7304 | -67.5761 | -0.11411 | -67.6015 | 55.3653 | 55.5567 | 55.3859 | -68.0222 | -0.20568 | -0.030337 | 122.9609 | -0.068268 | 0.13742 | -0.075612 | 0.14451 | -0.4975 | -0.11112 | -0.051412 | -0.07676 | 0.42074 | 0.080355 | -0.090431 | 122.9708 | 122.9255 | 123.1456 | 67.4162 | -123.2068 | 122.89 | 123.0815 | 122.9107 | 67.4106 | -123.4986
3262.7969 | 123.1064 | -67.5705 | 55.4855 | -0.010607 | -0.0050084 | 0.029094 | 0.052654 | -0.0092964 | 0.12682 | 0.00015261 | 0.017029 | 0.019101 | 0.013379 | 0.046754 | 0.054676 | 55.4316 | -0.1039 | -67.593 | 55.4415 | 55.4053 | 55.63 | -67.7304 | -67.5853 | -0.10495 | -67.6015 | 55.3653 | 55.5522 | 55.3859 | -68.0176 | -0.15991 | -0.044071 | 123.0021 | -0.022491 | 0.13742 | -0.080189 | 0.14451 | -0.44714 | -0.12028 | -0.014793 | -0.030983 | 0.41616 | 0.06662 | -0.099587 | 123.012 | 122.9758 | 123.2005 | 67.4666 | -123.2159 | 122.9358 | 123.1227 | 122.9564 | 67.4655 | -123.5032
3263.7969 | 123.1293 | -67.5751 | 55.4718 | 0.012286 | -0.0052222 | 0.028881 | 0.05244 | -0.0088692 | 0.12639 | -0.0074779 | 0.016815 | 0.019101 | 0.013379 | 0.04654 | 0.054676 | 55.427 | -0.10848 | -67.5976 | 55.446 | 55.3962 | 55.6117 | -67.7258 | -67.5807 | -0.10953 | -67.6015 | 55.3607 | 55.5567 | 55.3585 | -68.0222 | -0.15075 | -0.02576 | 123.0021 | -0.022492 | 0.12826 | -0.075614 | 0.13993 | -0.44715 | -0.11112 | -0.005637 | -0.026406 | 0.42074 | 0.084932 | -0.11333 | 123.0211 | 122.9713 | 123.1868 | 67.4666 | -123.1976 | 122.9358 | 123.1318 | 122.9335 | 67.4655 | -123.494
3264.7969 | 123.1567 | -67.5293 | 55.4855 | 0.0046549 | -0.0054358 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | 0.0077831 | 0.016602 | 0.019101 | 0.013592 | 0.04654 | 0.054676 | 55.4316 | -0.10848 | -67.5976 | 55.4506 | 55.4099 | 55.63 | -67.7258 | -67.5807 | -0.11411 | -67.6106 | 55.3653 | 55.5567 | 55.4043 | -68.0176 | -0.19653 | -0.034914 | 122.9609 | -0.068268 | 0.12826 | -0.07561 | 0.14451 | -0.48834 | -0.12028 | -0.051413 | -0.081339 | 0.407 | 0.071199 | -0.081272 | 122.9799 | 122.9392 | 123.1593 | 67.4208 | -123.2114 | 122.8946 | 123.086 | 122.9336 | 67.4152 | -123.5032
3265.7969 | 123.1842 | -67.5385 | 55.4672 | 0.0046549 | -0.0052222 | 0.028881 | 0.053081 | -0.0090828 | 0.12639 | -0.0074779 | 0.016602 | 0.019315 | 0.013165 | 0.047181 | 0.05489 | 55.4316 | -0.11306 | -67.6113 | 55.446 | 55.4053 | 55.6255 | -67.7212 | -67.5807 | -0.11411 | -67.6061 | 55.3653 | 55.5613 | 55.3814 | -68.0268 | -0.18279 | -0.021182 | 122.97 | -0.072848 | 0.10995 | -0.061878 | 0.15825 | -0.48835 | -0.10196 | -0.042258 | -0.067606 | 0.42074 | 0.094088 | -0.085854 | 122.9845 | 122.9438 | 123.1639 | 67.4254 | -123.1885 | 122.9037 | 123.0998 | 122.9198 | 67.4243 | -123.494
3266.7969 | 123.1567 | -67.5751 | 55.4855 | 0.012286 | -0.0050084 | 0.029094 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | 0.016602 | 0.019101 | 0.013592 | 0.047395 | 0.054676 | 55.4316 | -0.11306 | -67.6021 | 55.446 | 55.4008 | 55.63 | -67.7304 | -67.5761 | -0.10953 | -67.6061 | 55.3607 | 55.5659 | 55.3631 | -68.0268 | -0.15533 | -0.039493 | 123.0067 | -0.02707 | 0.12826 | -0.084768 | 0.14451 | -0.45172 | -0.12485 | -0.001058 | -0.030985 | 0.42074 | 0.080356 | -0.12248 | 123.0211 | 122.9758 | 123.2051 | 67.462 | -123.2159 | 122.9358 | 123.141 | 122.9381 | 67.4655 | -123.5123
3267.7969 | 123.2071 | -67.5568 | 55.4626 | 0.012286 | -0.0054358 | 0.028881 | 0.052867 | -0.0088692 | 0.1266 | 0.0077831 | 0.017029 | 0.019315 | 0.013379 | 0.046754 | 0.05489 | 55.4316 | -0.1039 | -67.593 | 55.4506 | 55.4008 | 55.6209 | -67.7212 | -67.5853 | -0.10953 | -67.6152 | 55.3607 | 55.5659 | 55.3768 | -68.0176 | -0.16448 | -0.012025 | 122.9884 | -0.036224 | 0.12826 | -0.061879 | 0.15825 | -0.46088 | -0.10197 | -0.028526 | -0.058452 | 0.40243 | 0.10325 | -0.085855 | 123.0074 | 122.9575 | 123.1777 | 67.4529 | -123.1839 | 122.9174 | 123.1227 | 122.9336 | 67.4472 | -123.4803
3268.7969 | 123.1247 | -67.5842 | 55.4947 | -0.0029761 | -0.0054358 | 0.028667 | 0.052654 | -0.0090828 | 0.1266 | 0.00015261 | 0.016815 | 0.019101 | 0.013379 | 0.046967 | 0.05489 | 55.4316 | -0.11306 | -67.5976 | 55.4506 | 55.4145 | 55.6209 | -67.7258 | -67.5807 | -0.10953 | -67.6061 | 55.3653 | 55.5659 | 55.3768 | -68.0131 | -0.1416 | -0.044069 | 123.0158 | -0.013336 | 0.12826 | -0.080186 | 0.1262 | -0.42883 | -0.12943 | 0.003519 | -0.021829 | 0.407 | 0.071201 | -0.1179 | 123.0348 | 122.9987 | 123.2051 | 67.4712 | -123.2205 | 122.9495 | 123.1501 | 122.961 | 67.4747 | -123.5078
3269.7969 | 123.1201 | -67.5751 | 55.481 | -0.0029761 | -0.0052222 | 0.028881 | 0.053081 | -0.0086556 | 0.1266 | 0.00015261 | 0.016602 | 0.019315 | 0.013379 | 0.046967 | 0.054676 | 55.4316 | -0.11306 | -67.6067 | 55.4415 | 55.3962 | 55.6209 | -67.7304 | -67.5807 | -0.10953 | -67.6015 | 55.3607 | 55.5522 | 55.3814 | -68.0268 | -0.15533 | -0.039493 | 123.0067 | -0.031649 | 0.12368 | -0.084769 | 0.13994 | -0.45172 | -0.12028 | -0.005637 | -0.026406 | 0.42532 | 0.071198 | -0.099587 | 123.0165 | 122.9713 | 123.196 | 67.462 | -123.2114 | 122.9358 | 123.1272 | 122.9564 | 67.4655 | -123.5078
3270.7969 | 123.1705 | -67.5751 | 55.4718 | -0.010607 | -0.0056496 | 0.029094 | 0.052654 | -0.0090828 | 0.12639 | 0.00015261 | 0.016815 | 0.019315 | 0.013592 | 0.047395 | 0.054676 | 55.4224 | -0.10848 | -67.5976 | 55.4506 | 55.4008 | 55.6255 | -67.7304 | -67.5807 | -0.10953 | -67.6015 | 55.3607 | 55.5613 | 55.3768 | -68.0176 | -0.15533 | -0.021181 | 122.9975 | -0.022492 | 0.13284 | -0.071035 | 0.15367 | -0.44257 | -0.11112 | -0.005637 | -0.026406 | 0.41616 | 0.08951 | -0.095011 | 123.0257 | 122.9758 | 123.2005 | 67.4666 | -123.2022 | 122.9358 | 123.1364 | 122.9519 | 67.4655 | -123.4894
3271.7969 | 123.2071 | -67.543 | 55.481 | 0.019917 | -0.0052222 | 0.029094 | 0.053081 | -0.0090828 | 0.12682 | 0.0077831 | 0.016388 | 0.019101 | 0.013165 | 0.046754 | 0.054462 | 55.427 | -0.10848 | -67.5976 | 55.446 | 55.4053 | 55.63 | -67.7304 | -67.5761 | -0.11869 | -67.6061 | 55.3698 | 55.5613 | 55.3814 | -68.0176 | -0.18737 | -0.034915 | 122.97 | -0.054535 | 0.13284 | -0.075611 | 0.14909 | -0.47461 | -0.11112 | -0.033101 | -0.063028 | 0.41158 | 0.080355 | -0.099587 | 122.9891 | 122.9484 | 123.1731 | 67.4346 | -123.2114 | 122.9129 | 123.1043 | 122.9244 | 67.4243 | -123.4986
3272.7969 | 123.1567 | -67.5705 | 55.4901 | -0.010607 | -0.0052222 | 0.029522 | 0.052654 | -0.0090828 | 0.1266 | -0.0074779 | 0.016602 | 0.019528 | 0.013379 | 0.047181 | 0.054676 | 55.4316 | -0.1039 | -67.6021 | 55.446 | 55.3962 | 55.6255 | -67.7304 | -67.5807 | -0.11411 | -67.6061 | 55.3561 | 55.5522 | 55.3768 | -68.0176 | -0.15991 | -0.04407 | 123.0021 | -0.031647 | 0.12826 | -0.093924 | 0.13536 | -0.44714 | -0.13401 | -0.010214 | -0.035562 | 0.41158 | 0.062043 | -0.11332 | 123.0165 | 122.9667 | 123.196 | 67.4666 | -123.2205 | 122.9266 | 123.1227 | 122.9473 | 67.4564 | -123.5078
3273.7969 | 123.1384 | -67.5705 | 55.481 | -0.0029761 | -0.0056496 | 0.029308 | 0.052654 | -0.0088692 | 0.12682 | 0.0077831 | 0.016815 | 0.019315 | 0.013379 | 0.046967 | 0.054676 | 55.4407 | -0.11306 | -67.6067 | 55.4415 | 55.4008 | 55.6209 | -67.7258 | -67.5807 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3814 | -68.0268 | -0.15533 | -0.039493 | 123.0112 | -0.036226 | 0.1191 | -0.08019 | 0.13994 | -0.4563 | -0.12028 | -0.010214 | -0.04014 | 0.41616 | 0.080355 | -0.099587 | 123.012 | 122.9713 | 123.1914 | 67.4574 | -123.2068 | 122.9312 | 123.1318 | 122.9519 | 67.461 | -123.5078
3274.7969 | 123.1842 | -67.5568 | 55.4672 | -0.010607 | -0.0054358 | 0.028881 | 0.052654 | -0.0088692 | 0.1266 | 0.0077831 | 0.016388 | 0.019315 | 0.012951 | 0.047181 | 0.05489 | 55.4362 | -0.11306 | -67.5976 | 55.446 | 55.3962 | 55.6163 | -67.7258 | -67.5807 | -0.10495 | -67.6106 | 55.3607 | 55.5567 | 55.3814 | -68.0176 | -0.16906 | -0.021182 | 122.9929 | -0.040802 | 0.12826 | -0.071036 | 0.14909 | -0.46088 | -0.10654 | -0.023947 | -0.053873 | 0.407 | 0.08951 | -0.085854 | 123.0028 | 122.953 | 123.1731 | 67.4437 | -123.193 | 122.9174 | 123.1135 | 122.9381 | 67.4518 | -123.4849
3275.8594 | 123.2071 | -67.5659 | 55.4214 | -0.010607 | -0.0058632 | 0.029308 | 0.052867 | -0.0090828 | 0.1266 | 0.0077831 | 0.016602 | 0.019528 | 0.013165 | 0.046967 | 0.054676 | 55.4316 | -0.1039 | -67.6113 | 55.446 | 55.3962 | 55.6209 | -67.7212 | -67.5761 | -0.11411 | -67.5969 | 55.3653 | 55.5567 | 55.3539 | -68.0268 | -0.15533 | 0.024594 | 122.9975 | -0.045382 | 0.10995 | -0.02526 | 0.19945 | -0.46088 | -0.056189 | -0.010213 | -0.030982 | 0.4299 | 0.13529 | -0.06755 | 123.012 | 122.9621 | 123.1868 | 67.462 | -123.1427 | 122.9312 | 123.1227 | 122.9198 | 67.4518 | -123.4482
3276.7969 | 123.1384 | -67.6163 | 55.4626 | -0.0029761 | -0.0056496 | 0.029094 | 0.052654 | -0.0088692 | 0.1266 | -0.015108 | 0.016388 | 0.019101 | 0.013379 | 0.046754 | 0.05489 | 55.4224 | -0.1039 | -67.5976 | 55.4506 | 55.387 | 55.6209 | -67.7258 | -67.5853 | -0.10495 | -67.6061 | 55.3653 | 55.5613 | 55.3493 | -68.0176 | -0.10955 | -0.012025 | 123.0387 | 0.018707 | 0.12826 | -0.075616 | 0.15825 | -0.40137 | -0.097387 | 0.030983 | 0.010214 | 0.41158 | 0.098666 | -0.11333 | 123.0669 | 123.0033 | 123.2372 | 67.5124 | -123.1885 | 122.9815 | 123.1776 | 122.9656 | 67.5113 | -123.4803
3277.7969 | 123.0972 | -67.5659 | 55.4993 | 0.0046549 | -0.0056496 | 0.029094 | 0.052226 | -0.0090828 | 0.12682 | 0.0077831 | 0.016602 | 0.019528 | 0.013165 | 0.046967 | 0.054462 | 55.4316 | -0.11764 | -67.593 | 55.4369 | 55.3916 | 55.63 | -67.7212 | -67.5807 | -0.10953 | -67.6061 | 55.3698 | 55.5613 | 55.3768 | -68.0268 | -0.15533 | -0.062382 | 122.9975 | -0.027069 | 0.12826 | -0.10766 | 0.13078 | -0.46088 | -0.12943 | -0.014792 | -0.04014 | 0.42074 | 0.062044 | -0.12248 | 123.0028 | 122.9575 | 123.196 | 67.4483 | -123.2205 | 122.9358 | 123.1272 | 122.9427 | 67.4564 | -123.5261
3278.7969 | 123.1567 | -67.5797 | 55.4718 | 0.0046549 | -0.0052222 | 0.029094 | 0.053081 | -0.0092964 | 0.12682 | 0.00015261 | 0.016602 | 0.019742 | 0.013379 | 0.047395 | 0.055103 | 55.4316 | -0.11306 | -67.6067 | 55.4506 | 55.4008 | 55.63 | -67.7258 | -67.5807 | -0.11869 | -67.6061 | 55.3607 | 55.5567 | 55.3768 | -68.0222 | -0.14617 | -0.021181 | 123.0112 | -0.027071 | 0.1191 | -0.071035 | 0.15825 | -0.44257 | -0.11112 | -0.001059 | -0.026407 | 0.41616 | 0.084932 | -0.095011 | 123.0303 | 122.9804 | 123.2097 | 67.4666 | -123.1976 | 122.9403 | 123.1364 | 122.9564 | 67.461 | -123.494
3279.7969 | 123.1384 | -67.5613 | 55.4672 | 0.0046549 | -0.0052222 | 0.029308 | 0.053081 | -0.0090828 | 0.1266 | -0.015108 | 0.016602 | 0.019742 | 0.012951 | 0.046967 | 0.054462 | 55.4316 | -0.1039 | -67.593 | 55.446 | 55.3916 | 55.6255 | -67.7304 | -67.5853 | -0.11411 | -67.6106 | 55.3561 | 55.5567 | 55.3676 | -68.0176 | -0.16906 | -0.021182 | 122.9929 | -0.031647 | 0.13742 | -0.075615 | 0.15825 | -0.4563 | -0.11112 | -0.023949 | -0.049296 | 0.407 | 0.08951 | -0.09959 | 123.0074 | 122.9529 | 123.1868 | 67.4574 | -123.1976 | 122.9174 | 123.1181 | 122.929 | 67.4472 | -123.4849
3280.7969 | 123.0972 | -67.5797 | 55.4855 | 0.0046549 | -0.0054358 | 0.028667 | 0.05244 | -0.0090828 | 0.1266 | 0.00015261 | 0.016602 | 0.019528 | 0.013165 | 0.047181 | 0.05489 | 55.427 | -0.1039 | -67.6021 | 55.4506 | 55.3779 | 55.63 | -67.7304 | -67.5761 | -0.11411 | -67.6061 | 55.3607 | 55.5613 | 55.3722 | -68.0176 | -0.15075 | -0.034914 | 123.0067 | -0.022492 | 0.12826 | -0.10766 | 0.14451 | -0.43799 | -0.12485 | 0.00352 | -0.026407 | 0.41158 | 0.075777 | -0.11332 | 123.0303 | 122.9575 | 123.2097 | 67.4758 | -123.2159 | 122.9403 | 123.141 | 122.9519 | 67.4655 | -123.5032
3281.7969 | 123.175 | -67.5705 | 55.4764 | 0.0046549 | -0.0050084 | 0.029094 | 0.052226 | -0.0088692 | 0.12703 | -0.0074779 | 0.016602 | 0.019315 | 0.013379 | 0.047608 | 0.054676 | 55.4316 | -0.10848 | -67.5976 | 55.4415 | 55.4053 | 55.6255 | -67.7304 | -67.5853 | -0.10953 | -67.6015 | 55.3607 | 55.5567 | 55.3631 | -68.0176 | -0.15991 | -0.034915 | 123.0021 | -0.027069 | 0.13284 | -0.071033 | 0.14909 | -0.44714 | -0.1157 | -0.014793 | -0.030983 | 0.41616 | 0.080355 | -0.11332 | 123.012 | 122.9758 | 123.196 | 67.462 | -123.2068 | 122.9312 | 123.1272 | 122.9336 | 67.461 | -123.494
3282.7969 | 123.1018 | -67.6071 | 55.4489 | -0.0029761 | -0.0054358 | 0.028881 | 0.052226 | -0.0090828 | 0.12682 | 0.00015261 | 0.016602 | 0.019315 | 0.013592 | 0.047181 | 0.054462 | 55.4316 | -0.1039 | -67.593 | 55.4415 | 55.4053 | 55.63 | -67.7258 | -67.5761 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3447 | -68.0176 | -0.11871 | -0.00745 | 123.0387 | 0.01413 | 0.13284 | -0.043568 | 0.18114 | -0.41052 | -0.088234 | 0.030986 | -0.003519 | 0.407 | 0.1124 | -0.10417 | 123.0486 | 123.0125 | 123.2372 | 67.5032 | -123.1747 | 122.9678 | 123.1684 | 122.9519 | 67.4976 | -123.4666
3283.7969 | 123.1842 | -67.5705 | 55.4718 | -0.0029761 | -0.0056496 | 0.029094 | 0.05244 | -0.0090828 | 0.12682 | 0.00015261 | 0.016388 | 0.019528 | 0.012951 | 0.047181 | 0.054676 | 55.4362 | -0.10848 | -67.6067 | 55.4506 | 55.387 | 55.6346 | -67.7304 | -67.5807 | -0.10495 | -67.6106 | 55.3653 | 55.5613 | 55.3676 | -68.0222 | -0.15991 | -0.021181 | 123.0067 | -0.036226 | 0.12368 | -0.084772 | 0.16283 | -0.45172 | -0.10654 | -0.010214 | -0.04014 | 0.41158 | 0.08951 | -0.10417 | 123.0211 | 122.9575 | 123.2051 | 67.462 | -123.2022 | 122.9358 | 123.1318 | 122.9381 | 67.4655 | -123.494
3284.7969 | 123.1293 | -67.598 | 55.4535 | -0.0029761 | -0.0058632 | 0.028881 | 0.05244 | -0.0090828 | 0.1266 | -0.015108 | 0.016815 | 0.019315 | 0.013165 | 0.046967 | 0.05489 | 55.4316 | -0.10848 | -67.5976 | 55.446 | 55.3825 | 55.6117 | -67.7212 | -67.5716 | -0.10953 | -67.6061 | 55.3561 | 55.5567 | 55.3676 | -68.0176 | -0.12328 | -0.007449 | 123.0296 | 0.000396 | 0.12368 | -0.07104 | 0.15824 | -0.41968 | -0.097389 | 0.026409 | -0.008097 | 0.41158 | 0.10324 | -0.085857 | 123.044 | 122.9804 | 123.2097 | 67.4895 | -123.1747 | 122.9541 | 123.1547 | 122.9656 | 67.4884 | -123.4711
3285.7969 | 123.175 | -67.5751 | 55.4718 | -0.0029761 | -0.0054358 | 0.028881 | 0.053081 | -0.0090828 | 0.1266 | 0.00015261 | 0.016388 | 0.019528 | 0.013165 | 0.046967 | 0.054676 | 55.427 | -0.1039 | -67.6067 | 55.446 | 55.3916 | 55.6255 | -67.7258 | -67.5761 | -0.10953 | -67.6152 | 55.3698 | 55.5613 | 55.3447 | -68.0314 | -0.15075 | -0.02576 | 123.0021 | -0.031649 | 0.1191 | -0.080193 | 0.15367 | -0.4563 | -0.10196 | -0.001058 | -0.040142 | 0.41616 | 0.08951 | -0.12706 | 123.0211 | 122.9667 | 123.2005 | 67.4712 | -123.1976 | 122.9449 | 123.1364 | 122.9198 | 67.4655 | -123.5032
3286.7969 | 123.1613 | -67.598 | 55.4489 | -0.010607 | -0.0056496 | 0.028881 | 0.05244 | -0.0088692 | 0.12682 | -0.0074779 | 0.016815 | 0.019315 | 0.013165 | 0.047181 | 0.054676 | 55.427 | -0.099323 | -67.6067 | 55.446 | 55.3825 | 55.6255 | -67.7258 | -67.5716 | -0.10495 | -67.6106 | 55.3561 | 55.5613 | 55.3585 | -68.0176 | -0.12786 | -0.002872 | 123.025 | -0.008761 | 0.1191 | -0.066463 | 0.17656 | -0.41968 | -0.092812 | 0.026409 | -0.012675 | 0.407 | 0.1124 | -0.090438 | 123.044 | 122.9804 | 123.2234 | 67.4986 | -123.1747 | 122.9541 | 123.1593 | 122.9564 | 67.493 | -123.4666
3287.7969 | 123.1018 | -67.5888 | 55.4672 | -0.0029761 | -0.0056496 | 0.028667 | 0.052867 | -0.0088692 | 0.12639 | -0.0074779 | 0.016388 | 0.019315 | 0.013379 | 0.046967 | 0.054676 | 55.427 | -0.10848 | -67.6021 | 55.4598 | 55.4008 | 55.6209 | -67.7258 | -67.5716 | -0.10953 | -67.6061 | 55.3607 | 55.5659 | 55.3859 | -68.0268 | -0.13702 | -0.007446 | 123.0158 | -0.013337 | 0.12368 | -0.066457 | 0.15367 | -0.43799 | -0.10654 | 0.017254 | -0.017252 | 0.42074 | 0.098667 | -0.081276 | 123.0486 | 122.9896 | 123.2097 | 67.4803 | -123.193 | 122.9495 | 123.1547 | 122.9748 | 67.4793 | -123.494
3288.7969 | 123.1613 | -67.5797 | 55.4489 | -0.0029761 | -0.0056496 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | 0.00015261 | 0.016815 | 0.019528 | 0.013165 | 0.047181 | 0.054676 | 55.4316 | -0.1039 | -67.6067 | 55.446 | 55.3962 | 55.6255 | -67.7167 | -67.5807 | -0.10495 | -67.6061 | 55.3607 | 55.5613 | 55.3402 | -68.0176 | -0.13702 | -0.002872 | 123.0112 | -0.027071 | 0.10994 | -0.052726 | 0.17656 | -0.43799 | -0.088234 | -0.001059 | -0.026407 | 0.41158 | 0.1124 | -0.10875 | 123.0257 | 122.9758 | 123.2051 | 67.4758 | -123.1656 | 122.9403 | 123.141 | 122.9198 | 67.4747 | -123.4666
3289.7969 | 123.1293 | -67.5934 | 55.4626 | -0.0029761 | -0.0056496 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | -0.0074779 | 0.016602 | 0.019742 | 0.012951 | 0.047181 | 0.05489 | 55.4224 | -0.10848 | -67.6021 | 55.4506 | 55.4008 | 55.6255 | -67.735 | -67.5807 | -0.10953 | -67.6061 | 55.3653 | 55.5567 | 55.3951 | -68.0314 | -0.1416 | -0.012025 | 123.0158 | -0.008759 | 0.13284 | -0.061879 | 0.16282 | -0.43799 | -0.097387 | 0.012674 | -0.012674 | 0.42532 | 0.094088 | -0.067541 | 123.044 | 122.9942 | 123.2189 | 67.4849 | -123.1976 | 122.9586 | 123.1501 | 122.9885 | 67.4839 | -123.494
3290.7969 | 123.2162 | -67.5293 | 55.426 | -0.0029761 | -0.0058632 | 0.029094 | 0.052867 | -0.0092964 | 0.12639 | -0.0074779 | 0.016602 | 0.019742 | 0.013165 | 0.047181 | 0.054676 | 55.4362 | -0.1039 | -67.6021 | 55.446 | 55.3962 | 55.6209 | -67.7212 | -67.5807 | -0.10495 | -67.6061 | 55.3698 | 55.5705 | 55.3585 | -68.0222 | -0.19195 | 0.020017 | 122.9655 | -0.072846 | 0.1191 | -0.029837 | 0.19487 | -0.49292 | -0.056188 | -0.051413 | -0.076761 | 0.41616 | 0.14444 | -0.067549 | 122.9753 | 122.9255 | 123.1502 | 67.4254 | -123.1473 | 122.8991 | 123.0998 | 122.8878 | 67.4243 | -123.4482
3291.7969 | 123.1064 | -67.598 | 55.4764 | -0.0029761 | -0.0056496 | 0.029094 | 0.052654 | -0.0090828 | 0.12639 | -0.0074779 | 0.016815 | 0.019742 | 0.012951 | 0.047608 | 0.05489 | 55.427 | -0.099323 | -67.6113 | 55.4415 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.10953 | -67.6061 | 55.3607 | 55.5522 | 55.3631 | -68.0222 | -0.12786 | -0.034915 | 123.025 | -0.013339 | 0.11453 | -0.080191 | 0.14451 | -0.42426 | -0.1157 | 0.017251 | -0.008097 | 0.41616 | 0.075776 | -0.11332 | 123.0394 | 122.9941 | 123.2189 | 67.4986 | -123.2022 | 122.9586 | 123.1501 | 122.961 | 67.4884 | -123.4986
3292.7969 | 123.2574 | -67.543 | 55.426 | -0.0029761 | -0.0058632 | 0.029094 | 0.052867 | -0.0090828 | 0.12682 | 0.00015261 | 0.016388 | 0.019528 | 0.013165 | 0.046967 | 0.05489 | 55.427 | -0.099323 | -67.6067 | 55.446 | 55.3916 | 55.6163 | -67.7212 | -67.5853 | -0.10495 | -67.6061 | 55.3653 | 55.5567 | 55.3768 | -68.0176 | -0.17822 | 0.020017 | 122.97 | -0.063692 | 0.11452 | -0.034416 | 0.19029 | -0.47461 | -0.060766 | -0.042259 | -0.063028 | 0.41158 | 0.13071 | -0.049234 | 122.9891 | 122.9346 | 123.1593 | 67.4437 | -123.1473 | 122.9083 | 123.0998 | 122.9198 | 67.4381 | -123.4437
3293.7969 | 123.175 | -67.5751 | 55.4443 | -0.0029761 | -0.0056496 | 0.029094 | 0.052654 | -0.0092964 | 0.1266 | 0.00015261 | 0.016815 | 0.019528 | 0.013165 | 0.047395 | 0.05489 | 55.4316 | -0.10848 | -67.5976 | 55.4415 | 55.3916 | 55.6255 | -67.7304 | -67.5761 | -0.10495 | -67.6106 | 55.3698 | 55.5567 | 55.3722 | -68.0131 | -0.15533 | -0.002872 | 123.0067 | -0.022492 | 0.13284 | -0.052727 | 0.18113 | -0.43799 | -0.074499 | -0.001058 | -0.035563 | 0.40243 | 0.1124 | -0.072124 | 123.0165 | 122.9667 | 123.2005 | 67.4666 | -123.1747 | 122.9449 | 123.1318 | 122.9473 | 67.4701 | -123.4574
3294.7969 | 123.2162 | -67.543 | 55.4398 | 0.0046549 | -0.0054358 | 0.029094 | 0.052867 | -0.0090828 | 0.12682 | 0.00015261 | 0.016602 | 0.019528 | 0.013379 | 0.047608 | 0.054676 | 55.4224 | -0.11306 | -67.593 | 55.446 | 55.3916 | 55.6209 | -67.7304 | -67.5761 | -0.10495 | -67.6152 | 55.3607 | 55.5613 | 55.3722 | -68.0176 | -0.18737 | 0.006284 | 122.9655 | -0.049957 | 0.13742 | -0.048149 | 0.18114 | -0.47461 | -0.079078 | -0.033101 | -0.072185 | 0.40243 | 0.12155 | -0.067546 | 122.9891 | 122.9346 | 123.1639 | 67.43 | -123.1702 | 122.9037 | 123.1043 | 122.9152 | 67.4381 | -123.4574
3295.8594 | 123.0423 | -67.6117 | 55.4443 | -0.010607 | -0.0054358 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | 0.00015261 | 0.016388 | 0.019742 | 0.013165 | 0.047181 | 0.054676 | 55.427 | -0.099323 | -67.5884 | 55.446 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.11411 | -67.6061 | 55.3607 | 55.5567 | 55.3722 | -68.0176 | -0.11413 | 0.001706 | 123.0387 | 0.023286 | 0.13742 | -0.048148 | 0.17656 | -0.40595 | -0.083656 | 0.030984 | 0.005636 | 0.41158 | 0.1124 | -0.072124 | 123.0577 | 123.0079 | 123.2326 | 67.5124 | -123.1702 | 122.9724 | 123.1684 | 122.9839 | 67.4976 | -123.462
3296.7969 | 123.2254 | -67.5751 | 55.4352 | -0.0029761 | -0.0056496 | 0.028881 | 0.052654 | -0.0092964 | 0.1266 | 0.0077831 | 0.016602 | 0.019742 | 0.013165 | 0.047395 | 0.05489 | 55.4316 | -0.10848 | -67.593 | 55.4552 | 55.387 | 55.63 | -67.7304 | -67.5807 | -0.10495 | -67.6106 | 55.3653 | 55.5613 | 55.3585 | -68.0176 | -0.15533 | 0.020018 | 123.0067 | -0.017914 | 0.13742 | -0.048151 | 0.19487 | -0.44257 | -0.069922 | -0.005637 | -0.035563 | 0.407 | 0.12613 | -0.076705 | 123.0303 | 122.9621 | 123.2051 | 67.4666 | -123.1656 | 122.9403 | 123.1364 | 122.9335 | 67.4701 | -123.4528
3297.7969 | 123.2712 | -67.543 | 55.4626 | -0.0029761 | -0.0056496 | 0.029094 | 0.052867 | -0.0090828 | 0.12682 | 0.015414 | 0.017029 | 0.019315 | 0.013165 | 0.047181 | 0.054676 | 55.427 | -0.1039 | -67.593 | 55.4415 | 55.4053 | 55.6163 | -67.7258 | -67.5807 | -0.095794 | -67.6061 | 55.3698 | 55.5567 | 55.3676 | -68.0222 | -0.18279 | -0.021182 | 122.97 | -0.049957 | 0.13284 | -0.0573 | 0.15367 | -0.47919 | -0.092809 | -0.03768 | -0.063028 | 0.41616 | 0.094088 | -0.095012 | 122.9845 | 122.9484 | 123.1593 | 67.4391 | -123.1885 | 122.9129 | 123.0998 | 122.9107 | 67.4472 | -123.4849
3298.7969 | 123.1888 | -67.5797 | 55.4398 | -0.010607 | -0.0054358 | 0.029094 | 0.052867 | -0.0088692 | 0.1266 | 0.00015261 | 0.016602 | 0.019956 | 0.012951 | 0.047395 | 0.054462 | 55.4224 | -0.10848 | -67.5976 | 55.446 | 55.4008 | 55.6209 | -67.7304 | -67.5761 | -0.10495 | -67.6152 | 55.3653 | 55.5522 | 55.3951 | -68.0268 | -0.15075 | 0.006284 | 123.0021 | -0.017914 | 0.13284 | -0.038991 | 0.18114 | -0.44715 | -0.074499 | 0.00352 | -0.035564 | 0.41158 | 0.1124 | -0.044653 | 123.0257 | 122.9804 | 123.2005 | 67.4712 | -123.1702 | 122.9449 | 123.1318 | 122.9748 | 67.4747 | -123.4666
3299.8594 | 123.0927 | -67.6117 | 55.4855 | -0.010607 | -0.0056496 | 0.029094 | 0.052867 | -0.0092964 | 0.12682 | 0.015414 | 0.016602 | 0.019528 | 0.012951 | 0.047395 | 0.054676 | 55.4316 | -0.1039 | -67.6067 | 55.4415 | 55.4053 | 55.63 | -67.7304 | -67.5807 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3722 | -68.0131 | -0.11871 | -0.044071 | 123.0433 | 0.004972 | 0.12368 | -0.080189 | 0.14451 | -0.40137 | -0.12485 | 0.030984 | 0.001058 | 0.40243 | 0.075777 | -0.11332 | 123.0532 | 123.017 | 123.2417 | 67.5078 | -123.2159 | 122.9724 | 123.173 | 122.9839 | 67.5022 | -123.4986
3300.7969 | 123.2071 | -67.5705 | 55.4581 | -0.0029761 | -0.0054358 | 0.029094 | 0.052867 | -0.0088692 | 0.1266 | 0.00015261 | 0.016388 | 0.019528 | 0.013165 | 0.047395 | 0.054676 | 55.4224 | -0.099323 | -67.6067 | 55.4506 | 55.3962 | 55.6209 | -67.7258 | -67.5807 | -0.10495 | -67.6061 | 55.3607 | 55.5522 | 55.3722 | -68.0176 | -0.15533 | -0.007448 | 122.9929 | -0.036226 | 0.1191 | -0.061881 | 0.16282 | -0.44714 | -0.097389 | -0.010214 | -0.035562 | 0.41158 | 0.094086 | -0.085857 | 123.0211 | 122.9667 | 123.1914 | 67.4712 | -123.1839 | 122.9312 | 123.1227 | 122.9427 | 67.4655 | -123.4757
3301.7969 | 123.2162 | -67.5613 | 55.4214 | -0.010607 | -0.0058632 | 0.028667 | 0.052654 | -0.0088692 | 0.1266 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.046967 | 0.054676 | 55.4224 | -0.1039 | -67.6021 | 55.4415 | 55.4191 | 55.6209 | -67.7212 | -67.5761 | -0.10953 | -67.5969 | 55.3653 | 55.5613 | 55.3722 | -68.0131 | -0.15991 | 0.020016 | 122.9838 | -0.040803 | 0.1191 | -0.002365 | 0.19945 | -0.45172 | -0.056189 | -0.014791 | -0.03556 | 0.41616 | 0.13986 | -0.049236 | 123.0028 | 122.9804 | 123.1822 | 67.4574 | -123.1427 | 122.9266 | 123.1227 | 122.9336 | 67.4518 | -123.4345
3302.7969 | 123.1796 | -67.5522 | 55.4352 | -0.010607 | -0.0056496 | 0.028881 | 0.053081 | -0.0090828 | 0.12682 | 0.0077831 | 0.016815 | 0.019742 | 0.013165 | 0.047395 | 0.05489 | 55.4224 | -0.099323 | -67.6021 | 55.446 | 55.3916 | 55.6255 | -67.7212 | -67.5853 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3676 | -68.0131 | -0.16906 | 0.010861 | 122.9746 | -0.049958 | 0.1191 | -0.043572 | 0.19029 | -0.46088 | -0.074501 | -0.033104 | -0.058451 | 0.40243 | 0.12613 | -0.067547 | 122.9982 | 122.9438 | 123.1777 | 67.4529 | -123.1564 | 122.9129 | 123.1135 | 122.9198 | 67.4427 | -123.4482
3303.7969 | 123.1888 | -67.5476 | 55.4489 | -0.0029761 | -0.0056496 | 0.029094 | 0.052867 | -0.0090828 | 0.12682 | -0.0074779 | 0.016602 | 0.019528 | 0.012951 | 0.047395 | 0.054676 | 55.427 | -0.099323 | -67.5976 | 55.4415 | 55.4008 | 55.6209 | -67.7212 | -67.5807 | -0.10953 | -67.6061 | 55.3698 | 55.5567 | 55.3585 | -68.0222 | -0.17364 | -0.00745 | 122.9746 | -0.049958 | 0.12368 | -0.048147 | 0.17198 | -0.47461 | -0.079077 | -0.033103 | -0.058451 | 0.41616 | 0.10782 | -0.090438 | 122.9891 | 122.9484 | 123.1685 | 67.4483 | -123.1702 | 122.9174 | 123.1043 | 122.9061 | 67.4381 | -123.4711
3304.7969 | 123.2483 | -67.5247 | 55.4718 | 0.0046549 | -0.0058632 | 0.029094 | 0.052867 | -0.0092964 | 0.12682 | 0.0077831 | 0.016602 | 0.019315 | 0.013165 | 0.047395 | 0.054676 | 55.4316 | -0.10848 | -67.5976 | 55.446 | 55.4145 | 55.6255 | -67.7258 | -67.5807 | -0.10037 | -67.6061 | 55.3653 | 55.5613 | 55.3585 | -68.0222 | -0.20111 | -0.02576 | 122.9563 | -0.072846 | 0.12826 | -0.057298 | 0.15367 | -0.4975 | -0.10654 | -0.055991 | -0.081339 | 0.41616 | 0.08951 | -0.11333 | 122.9708 | 122.9392 | 123.1502 | 67.4162 | -123.1976 | 122.89 | 123.086 | 122.8832 | 67.4243 | -123.494
3305.7969 | 123.1796 | -67.5659 | 55.4398 | 0.0046549 | -0.0058632 | 0.028667 | 0.05244 | -0.0086556 | 0.12639 | 0.00015261 | 0.016602 | 0.019315 | 0.012738 | 0.047608 | 0.054462 | 55.427 | -0.1039 | -67.6113 | 55.446 | 55.4008 | 55.6209 | -67.7304 | -67.5761 | -0.10953 | -67.6061 | 55.3653 | 55.5613 | 55.3859 | -68.0222 | -0.16449 | 0.006284 | 122.9929 | -0.045382 | 0.1191 | -0.038991 | 0.18114 | -0.4563 | -0.074499 | -0.010213 | -0.04014 | 0.41616 | 0.12155 | -0.05381 | 123.012 | 122.9667 | 123.1868 | 67.462 | -123.1702 | 122.9312 | 123.1272 | 122.9519 | 67.4564 | -123.462
3306.7969 | 123.2208 | -67.5476 | 55.4443 | -0.0029761 | -0.0056496 | 0.029308 | 0.052867 | -0.0092964 | 0.1266 | -0.0074779 | 0.016602 | 0.019315 | 0.012738 | 0.047395 | 0.054676 | 55.4362 | -0.094744 | -67.6113 | 55.4415 | 55.4053 | 55.6209 | -67.7258 | -67.5899 | -0.11411 | -67.6015 | 55.3607 | 55.5567 | 55.3768 | -68.0222 | -0.17822 | -0.002872 | 122.9838 | -0.063693 | 0.11453 | -0.03899 | 0.17656 | -0.47461 | -0.083656 | -0.04226 | -0.053872 | 0.42074 | 0.1124 | -0.067545 | 122.9891 | 122.953 | 123.1685 | 67.4529 | -123.1702 | 122.9083 | 123.1043 | 122.9244 | 67.4335 | -123.4666
3307.7969 | 123.1842 | -67.5568 | 55.4535 | 0.012286 | -0.0056496 | 0.028881 | 0.052867 | -0.0090828 | 0.1266 | -0.015108 | 0.016602 | 0.019315 | 0.012951 | 0.047608 | 0.05489 | 55.427 | -0.1039 | -67.5976 | 55.446 | 55.387 | 55.6072 | -67.7212 | -67.5853 | -0.10953 | -67.6106 | 55.3607 | 55.5567 | 55.3676 | -68.0268 | -0.16448 | -0.007449 | 122.9838 | -0.040802 | 0.12368 | -0.066461 | 0.15367 | -0.47003 | -0.092811 | -0.028526 | -0.053873 | 0.41616 | 0.10324 | -0.085857 | 123.0028 | 122.9438 | 123.1639 | 67.4529 | -123.1747 | 122.9174 | 123.1135 | 122.9244 | 67.4472 | -123.4803
3308.7969 | 123.262 | -67.5385 | 55.4626 | -0.010607 | -0.0058632 | 0.029308 | 0.052654 | -0.0090828 | 0.1266 | -0.0074779 | 0.016602 | 0.019742 | 0.012951 | 0.047395 | 0.054462 | 55.4224 | -0.1039 | -67.6021 | 55.4415 | 55.4053 | 55.6209 | -67.7212 | -67.5807 | -0.10953 | -67.6061 | 55.3607 | 55.5613 | 55.3676 | -68.0176 | -0.18279 | -0.021182 | 122.9609 | -0.063691 | 0.1191 | -0.0573 | 0.15825 | -0.47919 | -0.10197 | -0.042258 | -0.067606 | 0.41158 | 0.098666 | -0.095012 | 122.9799 | 122.9438 | 123.1593 | 67.4346 | -123.1839 | 122.8991 | 123.0998 | 122.9061 | 67.4289 | -123.4803
3309.7969 | 123.1979 | -67.543 | 55.4581 | 0.0046549 | -0.0058632 | 0.028881 | 0.053081 | -0.0090828 | 0.12703 | 0.00015261 | 0.016602 | 0.019528 | 0.012951 | 0.047395 | 0.054462 | 55.4224 | -0.1039 | -67.6113 | 55.446 | 55.4008 | 55.6255 | -67.7258 | -67.5807 | -0.10495 | -67.6106 | 55.3607 | 55.5567 | 55.3447 | -68.0176 | -0.18279 | -0.012027 | 122.9655 | -0.06827 | 0.11453 | -0.057302 | 0.1674 | -0.47461 | -0.097389 | -0.03768 | -0.067606 | 0.407 | 0.098665 | -0.11333 | 122.9891 | 122.9438 | 123.1685 | 67.4391 | -123.1839 | 122.9037 | 123.0998 | 122.8878 | 67.4381 | -123.4757
3310.7969 | 123.2071 | -67.5064 | 55.4718 | -0.0029761 | -0.0058632 | 0.029094 | 0.052867 | -0.0095102 | 0.12639 | 0.015414 | 0.016815 | 0.019742 | 0.012951 | 0.047608 | 0.054676 | 55.4224 | -0.099323 | -67.6067 | 55.4415 | 55.3962 | 55.63 | -67.7304 | -67.5853 | -0.10953 | -67.6152 | 55.3698 | 55.5567 | 55.3676 | -68.0085 | -0.22399 | -0.030338 | 122.9288 | -0.10031 | 0.12368 | -0.075614 | 0.15825 | -0.50207 | -0.10196 | -0.07888 | -0.10881 | 0.39327 | 0.084932 | -0.10417 | 122.9479 | 122.9026 | 123.1365 | 67.4071 | -123.2022 | 122.8762 | 123.0631 | 122.874 | 67.3969 | -123.4803
3311.8594 | 123.2803 | -67.5247 | 55.4489 | -0.0029761 | -0.0056496 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | 0.0077831 | 0.016602 | 0.019956 | 0.013165 | 0.047395 | 0.05489 | 55.4224 | -0.099323 | -67.6021 | 55.4415 | 55.4053 | 55.6255 | -67.7258 | -67.5761 | -0.10037 | -67.6061 | 55.3607 | 55.5567 | 55.3493 | -68.0222 | -0.20111 | -0.00745 | 122.9472 | -0.077424 | 0.12368 | -0.043568 | 0.17656 | -0.4975 | -0.088234 | -0.051412 | -0.081339 | 0.41616 | 0.10782 | -0.099595 | 122.9662 | 122.9301 | 123.1502 | 67.4254 | -123.1747 | 122.8854 | 123.0815 | 122.874 | 67.4243 | -123.4711
3312.7969 | 123.1338 | -67.5064 | 55.4718 | -0.0029761 | -0.0054358 | 0.028881 | 0.053081 | -0.0090828 | 0.12639 | 0.0077831 | 0.016602 | 0.019528 | 0.013165 | 0.047181 | 0.054462 | 55.4224 | -0.1039 | -67.5976 | 55.4415 | 55.387 | 55.6255 | -67.7167 | -67.5761 | -0.10495 | -67.6106 | 55.3653 | 55.5613 | 55.3768 | -68.0222 | -0.21026 | -0.030338 | 122.9288 | -0.091156 | 0.1191 | -0.084772 | 0.15367 | -0.51581 | -0.10654 | -0.069722 | -0.10423 | 0.41158 | 0.08951 | -0.095011 | 122.9479 | 122.8934 | 123.1319 | 67.4025 | -123.1885 | 122.8717 | 123.0677 | 122.8832 | 67.4015 | -123.494
3313.7969 | 123.2803 | -67.5293 | 55.4443 | -0.0029761 | -0.0056496 | 0.028881 | 0.052867 | -0.0092964 | 0.12724 | 0.00015261 | 0.016815 | 0.019528 | 0.013165 | 0.047395 | 0.054462 | 55.4224 | -0.10848 | -67.6021 | 55.4369 | 55.3962 | 55.63 | -67.7258 | -67.5807 | -0.10953 | -67.6015 | 55.3653 | 55.5613 | 55.3447 | -68.0176 | -0.19653 | -0.00745 | 122.9517 | -0.072846 | 0.12368 | -0.048148 | 0.18571 | -0.48834 | -0.079077 | -0.051413 | -0.072182 | 0.41616 | 0.11698 | -0.099595 | 122.9662 | 122.9255 | 123.1593 | 67.4208 | -123.1702 | 122.8946 | 123.0906 | 122.874 | 67.4198 | -123.462
3314.7969 | 123.1705 | -67.5247 | 55.4764 | 0.0046549 | -0.0058632 | 0.029094 | 0.052867 | -0.0086556 | 0.12703 | 0.00015261 | 0.016815 | 0.019742 | 0.012951 | 0.047395 | 0.054676 | 55.427 | -0.099323 | -67.5976 | 55.4506 | 55.3916 | 55.6209 | -67.7212 | -67.5761 | -0.11411 | -67.6106 | 55.3561 | 55.5613 | 55.3768 | -68.0176 | -0.19653 | -0.025758 | 122.9517 | -0.072846 | 0.12368 | -0.08477 | 0.14451 | -0.49292 | -0.12028 | -0.051412 | -0.085917 | 0.407 | 0.084933 | -0.099588 | 122.9753 | 122.9163 | 123.1456 | 67.4254 | -123.1976 | 122.8808 | 123.086 | 122.9015 | 67.4106 | -123.494
3315.7969 | 123.2712 | -67.5201 | 55.4581 | -0.0029761 | -0.0056496 | 0.029308 | 0.052654 | -0.0092964 | 0.1266 | 0.00015261 | 0.017029 | 0.019528 | 0.012951 | 0.047608 | 0.05489 | 55.427 | -0.099323 | -67.5976 | 55.4415 | 55.3916 | 55.6209 | -67.7258 | -67.5807 | -0.11411 | -67.6106 | 55.3607 | 55.5659 | 55.3585 | -68.0176 | -0.20568 | -0.016605 | 122.9472 | -0.077423 | 0.12826 | -0.06646 | 0.16282 | -0.4975 | -0.097389 | -0.060568 | -0.090494 | 0.407 | 0.10782 | -0.099593 | 122.9616 | 122.9118 | 123.141 | 67.4208 | -123.1839 | 122.8808 | 123.086 | 122.8786 | 67.406 | -123.4757
3316.7969 | 123.1155 | -67.5751 | 55.4993 | -0.0029761 | -0.0060768 | 0.029308 | 0.052867 | -0.0090828 | 0.1266 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.047608 | 0.054676 | 55.4316 | -0.1039 | -67.6021 | 55.4506 | 55.4099 | 55.6255 | -67.7396 | -67.5761 | -0.10953 | -67.6106 | 55.3653 | 55.5567 | 55.3768 | -68.0176 | -0.16449 | -0.048647 | 123.0067 | -0.02707 | 0.13742 | -0.089343 | 0.1262 | -0.44257 | -0.13401 | -0.001058 | -0.035563 | 0.407 | 0.057466 | -0.12248 | 123.0257 | 122.985 | 123.2005 | 67.4712 | -123.2388 | 122.9403 | 123.1318 | 122.9519 | 67.4655 | -123.5169
3317.7969 | 123.2391 | -67.5018 | 55.4581 | -0.010607 | -0.0058632 | 0.029094 | 0.053081 | -0.0090828 | 0.1266 | 0.0077831 | 0.016602 | 0.019742 | 0.013165 | 0.047395 | 0.054462 | 55.427 | -0.1039 | -67.5976 | 55.446 | 55.4008 | 55.6255 | -67.7258 | -67.5761 | -0.10495 | -67.6015 | 55.3653 | 55.5567 | 55.3951 | -68.0131 | -0.22399 | -0.012027 | 122.9288 | -0.095734 | 0.12826 | -0.057302 | 0.1674 | -0.51123 | -0.09281 | -0.0743 | -0.099648 | 0.41158 | 0.098665 | -0.062964 | 122.9479 | 122.9026 | 123.1273 | 67.3979 | -123.1839 | 122.8671 | 123.0586 | 122.8969 | 67.3969 | -123.4711
3318.7969 | 123.1201 | -67.5842 | 55.4993 | -0.0029761 | -0.0058632 | 0.029094 | 0.053081 | -0.0090828 | 0.12639 | 0.0077831 | 0.016815 | 0.019742 | 0.013165 | 0.046967 | 0.054676 | 55.4316 | -0.099323 | -67.5884 | 55.446 | 55.4145 | 55.6255 | -67.7258 | -67.5716 | -0.10953 | -67.6106 | 55.3653 | 55.5613 | 55.3814 | -68.0131 | -0.1416 | -0.053226 | 123.0158 | -0.004179 | 0.13742 | -0.084764 | 0.1262 | -0.42883 | -0.13401 | 0.012677 | -0.026407 | 0.40243 | 0.062044 | -0.1179 | 123.0303 | 122.9987 | 123.2097 | 67.4849 | -123.2251 | 122.9495 | 123.1455 | 122.9656 | 67.4747 | -123.5123
3319.7969 | 123.2483 | -67.5293 | 55.4443 | -0.0029761 | -0.0056496 | 0.028881 | 0.053081 | -0.0088692 | 0.1266 | 0.0077831 | 0.016815 | 0.019742 | 0.012951 | 0.047395 | 0.054676 | 55.427 | -0.1039 | -67.593 | 55.4415 | 55.4099 | 55.6255 | -67.7258 | -67.5761 | -0.10495 | -67.6061 | 55.3607 | 55.5613 | 55.3814 | -68.0222 | -0.19653 | -0.002872 | 122.9563 | -0.06369 | 0.13284 | -0.034411 | 0.18113 | -0.49292 | -0.083656 | -0.046834 | -0.076761 | 0.41616 | 0.11698 | -0.062966 | 122.9708 | 122.9392 | 123.1548 | 67.4254 | -123.1702 | 122.89 | 123.0906 | 122.9107 | 67.4243 | -123.4666
3320.7969 | 123.1293 | -67.5705 | 55.481 | 0.0046549 | -0.0056496 | 0.029094 | 0.052654 | -0.0090828 | 0.12682 | 0.00015261 | 0.017029 | 0.019956 | 0.012738 | 0.047608 | 0.054676 | 55.4316 | -0.099323 | -67.593 | 55.4415 | 55.4099 | 55.63 | -67.7258 | -67.5853 | -0.10953 | -67.6061 | 55.3561 | 55.5613 | 55.3905 | -68.0176 | -0.15533 | -0.039493 | 123.0021 | -0.022491 | 0.13284 | -0.071032 | 0.14909 | -0.44714 | -0.12485 | -0.014793 | -0.035562 | 0.41158 | 0.080355 | -0.09043 | 123.012 | 122.9804 | 123.2005 | 67.4712 | -123.2068 | 122.9266 | 123.1318 | 122.961 | 67.461 | -123.4986
3321.7969 | 123.2666 | -67.5201 | 55.4352 | 0.0046549 | -0.0058632 | 0.028667 | 0.052867 | -0.0088692 | 0.12596 | 0.0077831 | 0.016602 | 0.019528 | 0.013165 | 0.047608 | 0.054676 | 55.4316 | -0.099323 | -67.5976 | 55.4369 | 55.387 | 55.63 | -67.7212 | -67.5899 | -0.10495 | -67.6106 | 55.3653 | 55.5613 | 55.3676 | -68.0176 | -0.2011 | 0.001705 | 122.9517 | -0.077423 | 0.12368 | -0.048151 | 0.19487 | -0.4975 | -0.069922 | -0.069725 | -0.090494 | 0.407 | 0.12613 | -0.067547 | 122.957 | 122.9072 | 123.1502 | 67.4208 | -123.1564 | 122.8854 | 123.0815 | 122.8878 | 67.4152 | -123.4528
3322.7969 | 123.1384 | -67.5613 | 55.4718 | 0.0046549 | -0.0056496 | 0.028453 | 0.052654 | -0.0090828 | 0.1266 | -0.0074779 | 0.017029 | 0.019742 | 0.012738 | 0.047181 | 0.054462 | 55.427 | -0.099323 | -67.5884 | 55.446 | 55.3916 | 55.6346 | -67.7304 | -67.5716 | -0.10953 | -67.6106 | 55.3653 | 55.5659 | 55.3905 | -68.0176 | -0.16906 | -0.02576 | 122.9884 | -0.027068 | 0.142 | -0.080193 | 0.16283 | -0.4563 | -0.10654 | -0.010212 | -0.049296 | 0.407 | 0.094089 | -0.081275 | 123.0074 | 122.9529 | 123.196 | 67.462 | -123.2022 | 122.9266 | 123.1272 | 122.9519 | 67.4518 | -123.4894
3323.7969 | 123.2758 | -67.5156 | 55.4718 | 0.0046549 | -0.0060768 | 0.029308 | 0.052654 | -0.0090828 | 0.12682 | 0.00015261 | 0.016602 | 0.019528 | 0.013165 | 0.047395 | 0.054462 | 55.4316 | -0.1039 | -67.5884 | 55.4415 | 55.4053 | 55.6209 | -67.7258 | -67.5807 | -0.11411 | -67.6152 | 55.3607 | 55.5659 | 55.3814 | -68.0131 | -0.21026 | -0.030338 | 122.9472 | -0.072844 | 0.13742 | -0.066456 | 0.14909 | -0.4975 | -0.11112 | -0.065146 | -0.099651 | 0.39785 | 0.094089 | -0.090432 | 122.957 | 122.9209 | 123.1365 | 67.4117 | -123.1976 | 122.8762 | 123.0815 | 122.8969 | 67.4015 | -123.4849
3324.7969 | 123.143 | -67.5888 | 55.4764 | -0.010607 | -0.0062906 | 0.029308 | 0.053081 | -0.0090828 | 0.12617 | 0.00015261 | 0.016388 | 0.019528 | 0.012951 | 0.047395 | 0.054676 | 55.427 | -0.094744 | -67.593 | 55.446 | 55.4008 | 55.63 | -67.7304 | -67.5807 | -0.10953 | -67.5969 | 55.3607 | 55.5567 | 55.3859 | -68.0222 | -0.1416 | -0.030337 | 123.0158 | -0.004181 | 0.13742 | -0.075612 | 0.15367 | -0.43341 | -0.1157 | 0.008096 | -0.008094 | 0.42532 | 0.080355 | -0.090431 | 123.0348 | 122.9896 | 123.2189 | 67.4941 | -123.2068 | 122.9495 | 123.1455 | 122.9748 | 67.4793 | -123.4986
3325.7969 | 123.262 | -67.5156 | 55.4764 | -0.010607 | -0.0062906 | 0.029308 | 0.052867 | -0.0090828 | 0.12639 | 0.0077831 | 0.016602 | 0.019742 | 0.013165 | 0.047181 | 0.054462 | 55.4224 | -0.099323 | -67.593 | 55.446 | 55.4008 | 55.63 | -67.7304 | -67.5807 | -0.10953 | -67.6061 | 55.3653 | 55.5567 | 55.3722 | -68.0085 | -0.21484 | -0.030337 | 122.938 | -0.077423 | 0.13742 | -0.075612 | 0.15367 | -0.49292 | -0.11112 | -0.065146 | -0.090494 | 0.40242 | 0.080355 | -0.10417 | 122.9616 | 122.9163 | 123.1456 | 67.4162 | -123.2068 | 122.8808 | 123.0723 | 122.8878 | 67.406 | -123.4849
3326.7969 | 123.1842 | -67.5522 | 55.4352 | -0.0029761 | -0.0056496 | 0.029094 | 0.052867 | -0.0090828 | 0.1266 | 0.0077831 | 0.016388 | 0.019528 | 0.013165 | 0.047395 | 0.05489 | 55.427 | -0.090166 | -67.593 | 55.4415 | 55.4008 | 55.6209 | -67.7304 | -67.5807 | -0.10495 | -67.6061 | 55.3653 | 55.5567 | 55.3676 | -68.0131 | -0.17822 | 0.006283 | 122.9792 | -0.040802 | 0.13742 | -0.034414 | 0.18571 | -0.46088 | -0.069922 | -0.028525 | -0.053873 | 0.407 | 0.12155 | -0.067547 | 122.9936 | 122.953 | 123.1731 | 67.462 | -123.1656 | 122.9174 | 123.1089 | 122.9198 | 67.4472 | -123.4482
3327.7969 | 123.1796 | -67.5385 | 55.4718 | 0.0046549 | -0.0060768 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | 0.00015261 | 0.017029 | 0.019742 | 0.013165 | 0.047822 | 0.054462 | 55.4316 | -0.090166 | -67.593 | 55.4415 | 55.4099 | 55.6346 | -67.735 | -67.5716 | -0.10037 | -67.6061 | 55.3653 | 55.5613 | 55.4088 | -68.0222 | -0.19653 | -0.030338 | 122.97 | -0.054535 | 0.142 | -0.061877 | 0.16283 | -0.48377 | -0.10654 | -0.0331 | -0.067606 | 0.41616 | 0.08951 | -0.062961 | 122.9799 | 122.9484 | 123.1731 | 67.4483 | -123.2068 | 122.9037 | 123.0998 | 122.9473 | 67.4381 | -123.494
3328.7969 | 123.0743 | -67.5476 | 55.5222 | -0.0029761 | -0.0060768 | 0.028881 | 0.052654 | -0.0090828 | 0.12639 | 0.0077831 | 0.016602 | 0.019742 | 0.012951 | 0.047395 | 0.05489 | 55.427 | -0.085587 | -67.5976 | 55.446 | 55.4328 | 55.63 | -67.7304 | -67.5761 | -0.10953 | -67.6061 | 55.3653 | 55.5567 | 55.3814 | -68.0131 | -0.1828 | -0.076114 | 122.9746 | -0.049958 | 0.13284 | -0.089337 | 0.10789 | -0.46546 | -0.1569 | -0.028524 | -0.058451 | 0.407 | 0.034578 | -0.14079 | 122.9936 | 122.9804 | 123.1777 | 67.462 | -123.2526 | 122.9129 | 123.1043 | 122.929 | 67.4381 | -123.5352
3329.7969 | 123.2346 | -67.5293 | 55.4535 | 0.012286 | -0.0058632 | 0.029308 | 0.052867 | -0.0090828 | 0.12682 | 0.015414 | 0.016602 | 0.019315 | 0.012951 | 0.047608 | 0.05489 | 55.4316 | -0.099323 | -67.593 | 55.4552 | 55.3962 | 55.6209 | -67.7212 | -67.5807 | -0.11869 | -67.6015 | 55.3653 | 55.5613 | 55.3631 | -68.0222 | -0.19195 | 0.001708 | 122.9609 | -0.06369 | 0.12826 | -0.057303 | 0.1674 | -0.49292 | -0.088232 | -0.051413 | -0.072182 | 0.42074 | 0.10782 | -0.090436 | 122.9845 | 122.9255 | 123.1502 | 67.43 | -123.1747 | 122.8946 | 123.0906 | 122.8924 | 67.4106 | -123.4757
3330.7969 | 123.1155 | -67.5705 | 55.4901 | 0.0046549 | -0.0060768 | 0.028881 | 0.052654 | -0.0092964 | 0.1266 | 0.0077831 | 0.016602 | 0.019742 | 0.013379 | 0.047395 | 0.054676 | 55.4224 | -0.094744 | -67.5976 | 55.446 | 55.4008 | 55.6163 | -67.735 | -67.5807 | -0.10495 | -67.6015 | 55.3607 | 55.5613 | 55.3905 | -68.0131 | -0.16449 | -0.04407 | 122.9929 | -0.027069 | 0.13742 | -0.089345 | 0.1262 | -0.44257 | -0.12943 | -0.010214 | -0.030983 | 0.41158 | 0.0712 | -0.099585 | 123.0165 | 122.9713 | 123.1868 | 67.4758 | -123.2251 | 122.9312 | 123.1318 | 122.961 | 67.4655 | -123.5032
3331.7969 | 123.1247 | -67.5934 | 55.4718 | 0.012286 | -0.0060768 | 0.029094 | 0.052654 | -0.0090828 | 0.12682 | -0.0074779 | 0.016388 | 0.019956 | 0.013165 | 0.047395 | 0.05489 | 55.4224 | -0.099323 | -67.6067 | 55.4552 | 55.4053 | 55.63 | -67.7304 | -67.5807 | -0.10495 | -67.6015 | 55.3653 | 55.5613 | 55.3722 | -68.0222 | -0.13702 | -0.016603 | 123.0158 | -0.013338 | 0.12368 | -0.066456 | 0.15825 | -0.42884 | -0.10654 | 0.012674 | -0.008095 | 0.42074 | 0.08951 | -0.09959 | 123.0486 | 122.9987 | 123.2234 | 67.4941 | -123.2022 | 122.9586 | 123.1547 | 122.9656 | 67.4884 | -123.494
3332.7969 | 123.1979 | -67.5339 | 55.5176 | -0.0029761 | -0.0058632 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | -0.015108 | 0.016388 | 0.019956 | 0.012951 | 0.047608 | 0.054676 | 55.427 | -0.099323 | -67.5976 | 55.446 | 55.4008 | 55.6209 | -67.7258 | -67.5716 | -0.10495 | -67.6061 | 55.3653 | 55.5613 | 55.3722 | -68.0176 | -0.19195 | -0.071536 | 122.9609 | -0.06369 | 0.12826 | -0.11681 | 0.10332 | -0.48377 | -0.15232 | -0.037677 | -0.072183 | 0.41158 | 0.043734 | -0.14537 | 122.9799 | 122.9346 | 123.1548 | 67.4346 | -123.2434 | 122.8991 | 123.0952 | 122.9061 | 67.4289 | -123.5352
3333.7969 | 123.2162 | -67.5201 | 55.4581 | -0.0029761 | -0.0060768 | 0.028667 | 0.052654 | -0.0090828 | 0.12682 | 0.00015261 | 0.016388 | 0.019528 | 0.012524 | 0.047822 | 0.054676 | 55.427 | -0.094744 | -67.6113 | 55.446 | 55.4145 | 55.6209 | -67.7212 | -67.5807 | -0.10953 | -67.6106 | 55.3653 | 55.5522 | 55.3631 | -68.0268 | -0.2011 | -0.012027 | 122.9472 | -0.091158 | 0.10995 | -0.043565 | 0.16282 | -0.50666 | -0.09281 | -0.060568 | -0.090494 | 0.41616 | 0.094086 | -0.095014 | 122.9662 | 122.9346 | 123.141 | 67.4254 | -123.1793 | 122.8854 | 123.0723 | 122.8832 | 67.4106 | -123.4849
3334.7969 | 123.1659 | -67.5659 | 55.481 | 0.0046549 | -0.0060768 | 0.028881 | 0.052867 | -0.0088692 | 0.12682 | 0.0077831 | 0.017029 | 0.019742 | 0.013379 | 0.047608 | 0.054676 | 55.4179 | -0.094744 | -67.6021 | 55.4415 | 55.4053 | 55.6255 | -67.7258 | -67.5807 | -0.10037 | -67.6061 | 55.3561 | 55.5567 | 55.3859 | -68.0176 | -0.15991 | -0.039493 | 122.9838 | -0.036225 | 0.12368 | -0.075611 | 0.14451 | -0.45172 | -0.12485 | -0.014792 | -0.04014 | 0.41158 | 0.075777 | -0.095009 | 123.0074 | 122.9713 | 123.1914 | 67.4712 | -123.2068 | 122.922 | 123.1227 | 122.9519 | 67.4655 | -123.4986
3335.7969 | 123.1247 | -67.5385 | 55.4993 | -0.0029761 | -0.0060768 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | 0.00015261 | 0.016602 | 0.019956 | 0.012738 | 0.047608 | 0.055103 | 55.427 | -0.085587 | -67.5976 | 55.446 | 55.3825 | 55.6209 | -67.7304 | -67.5807 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3859 | -68.0176 | -0.19195 | -0.053226 | 122.9655 | -0.059113 | 0.13284 | -0.11682 | 0.12163 | -0.47919 | -0.13859 | -0.042258 | -0.072184 | 0.407 | 0.062044 | -0.11332 | 122.9845 | 122.9209 | 123.1593 | 67.4529 | -123.2297 | 122.8991 | 123.0998 | 122.9244 | 67.4289 | -123.5169
3336.7969 | 123.2254 | -67.5705 | 55.4031 | -0.0029761 | -0.0060768 | 0.029094 | 0.05244 | -0.0092964 | 0.12682 | 0.00015261 | 0.016815 | 0.019528 | 0.012951 | 0.047608 | 0.05489 | 55.427 | -0.081008 | -67.5976 | 55.4415 | 55.3962 | 55.6209 | -67.7212 | -67.5807 | -0.10953 | -67.6106 | 55.3561 | 55.5567 | 55.3493 | -68.0222 | -0.15075 | 0.038327 | 122.9975 | -0.027069 | 0.12368 | -0.006949 | 0.21776 | -0.45172 | -0.047035 | -0.010214 | -0.04014 | 0.41158 | 0.1536 | -0.053818 | 123.012 | 122.9667 | 123.1914 | 67.4895 | -123.1244 | 122.9266 | 123.1272 | 122.9198 | 67.461 | -123.4254
3337.7969 | 123.1155 | -67.5659 | 55.4855 | -0.0029761 | -0.0058632 | 0.029094 | 0.05244 | -0.0090828 | 0.1266 | 0.0077831 | 0.016602 | 0.019956 | 0.013165 | 0.047608 | 0.054676 | 55.4224 | -0.090166 | -67.5976 | 55.4506 | 55.3962 | 55.63 | -67.735 | -67.5761 | -0.10037 | -67.6106 | 55.3607 | 55.5476 | 55.3768 | -68.0222 | -0.16907 | -0.034914 | 122.9884 | -0.031647 | 0.13742 | -0.089347 | 0.14451 | -0.4563 | -0.12485 | -0.010213 | -0.044718 | 0.41158 | 0.062041 | -0.10874 | 123.0165 | 122.9621 | 123.196 | 67.4758 | -123.2205 | 122.9266 | 123.1135 | 122.9427 | 67.4655 | -123.5078
3338.7969 | 123.1705 | -67.5842 | 55.4947 | -0.0029761 | -0.0060768 | 0.028667 | 0.052226 | -0.0090828 | 0.1266 | 0.00015261 | 0.016602 | 0.019315 | 0.012951 | 0.047395 | 0.054676 | 55.427 | -0.090166 | -67.6159 | 55.4506 | 55.4053 | 55.6346 | -67.7304 | -67.5807 | -0.10037 | -67.6061 | 55.3653 | 55.5522 | 55.3814 | -68.0222 | -0.14617 | -0.044069 | 123.0112 | -0.031649 | 0.11453 | -0.089344 | 0.13994 | -0.43799 | -0.12943 | 0.003519 | -0.021829 | 0.41616 | 0.057465 | -0.11332 | 123.0348 | 122.9896 | 123.2189 | 67.4941 | -123.2251 | 122.9495 | 123.1364 | 122.9656 | 67.4839 | -123.5169
3339.7969 | 123.0331 | -67.5751 | 55.4947 | 0.012286 | -0.0062906 | 0.029094 | 0.052654 | -0.0095102 | 0.12682 | 0.00015261 | 0.016602 | 0.019528 | 0.012951 | 0.047395 | 0.054462 | 55.427 | -0.094744 | -67.593 | 55.446 | 55.387 | 55.6255 | -67.7304 | -67.5853 | -0.095794 | -67.6061 | 55.3607 | 55.5567 | 55.3768 | -68.0268 | -0.15533 | -0.048648 | 123.0021 | -0.017914 | 0.13742 | -0.10766 | 0.13078 | -0.45172 | -0.13401 | -0.010216 | -0.030985 | 0.42074 | 0.062044 | -0.1179 | 123.0211 | 122.9621 | 123.2005 | 67.4803 | -123.2251 | 122.9358 | 123.1318 | 122.9519 | 67.4793 | -123.5215
3340.7969 | 123.1384 | -67.5385 | 55.4581 | -0.0029761 | -0.0062906 | 0.029308 | 0.052867 | -0.0092964 | 0.12682 | 0.015414 | 0.016388 | 0.019528 | 0.012951 | 0.047822 | 0.054462 | 55.427 | -0.090166 | -67.6067 | 55.446 | 55.387 | 55.6209 | -67.735 | -67.5853 | -0.10037 | -67.5969 | 55.3607 | 55.5567 | 55.331 | -68.0222 | -0.19653 | -0.012027 | 122.9655 | -0.06827 | 0.12826 | -0.071039 | 0.16282 | -0.48377 | -0.097389 | -0.046837 | -0.058448 | 0.42532 | 0.098665 | -0.12706 | 122.9845 | 122.9255 | 123.1593 | 67.4483 | -123.1931 | 122.8991 | 123.0952 | 122.8695 | 67.4381 | -123.4803
3341.7969 | 123.1705 | -67.5888 | 55.4535 | -0.018238 | -0.0062906 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | 0.00015261 | 0.016388 | 0.019742 | 0.012951 | 0.047608 | 0.054676 | 55.4316 | -0.085587 | -67.6067 | 55.4415 | 55.4008 | 55.6209 | -67.7258 | -67.5761 | -0.10953 | -67.6106 | 55.3607 | 55.5613 | 55.3859 | -68.0176 | -0.13702 | -0.012027 | 123.0204 | -0.017916 | 0.1191 | -0.052724 | 0.1674 | -0.42883 | -0.092811 | 0.012675 | -0.02183 | 0.407 | 0.10782 | -0.067543 | 123.0303 | 122.9896 | 123.2097 | 67.5032 | -123.1793 | 122.9495 | 123.1501 | 122.9748 | 67.4793 | -123.4711
3342.7969 | 123.1338 | -67.598 | 55.4581 | 0.0046549 | -0.0062906 | 0.028881 | 0.052654 | -0.0090828 | 0.12682 | 0.0077831 | 0.016602 | 0.019742 | 0.012738 | 0.04825 | 0.054462 | 55.4316 | -0.090166 | -67.6021 | 55.4415 | 55.4099 | 55.63 | -67.7258 | -67.5853 | -0.095794 | -67.6015 | 55.3607 | 55.5522 | 55.3539 | -68.0176 | -0.12786 | -0.016605 | 123.0296 | -0.004182 | 0.12368 | -0.048144 | 0.17198 | -0.41968 | -0.097389 | 0.012672 | -0.003518 | 0.41616 | 0.094086 | -0.10417 | 123.0394 | 123.0079 | 123.228 | 67.5078 | -123.1839 | 122.9586 | 123.1501 | 122.9519 | 67.5022 | -123.4757
3343.7969 | 123.1567 | -67.5613 | 55.4535 | -0.0029761 | -0.0058632 | 0.028667 | 0.052867 | -0.0090828 | 0.1266 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.047822 | 0.054676 | 55.427 | -0.090166 | -67.6021 | 55.4506 | 55.4099 | 55.63 | -67.7304 | -67.5807 | -0.10037 | -67.6015 | 55.3561 | 55.5613 | 55.3631 | -68.0085 | -0.16906 | -0.00287 | 122.9884 | -0.040803 | 0.12826 | -0.043566 | 0.17656 | -0.44714 | -0.097389 | -0.01937 | -0.040139 | 0.407 | 0.10782 | -0.090436 | 123.012 | 122.9713 | 123.1914 | 67.4712 | -123.1839 | 122.9174 | 123.1227 | 122.9244 | 67.461 | -123.462
3344.7969 | 123.0881 | -67.9413 | 55.0735 | -0.0029761 | -0.0060768 | 0.028881 | 0.052654 | -0.0092964 | 0.12617 | 0.00015261 | 0.016388 | 0.019315 | 0.012951 | 0.047822 | 0.054462 | 55.0836 | 49.9952 | -67.9501 | 55.0935 | 55.0528 | 55.2729 | -68.0692 | -67.9333 | -0.10037 | -67.9449 | 55.0219 | 55.2133 | 55.0197 | -68.3702 | -0.12796 | 0.01996 | 123.0249 | -0.008809 | 0.11915 | -0.020778 | 0.19937 | -0.42893 | -0.051675 | 0.008014 | -0.003598 | 0.42533 | 0.13979 | -0.053887 | 123.0348 | 122.9941 | 123.2142 | 117.9365 | -123.1428 | 122.9632 | 123.1546 | 122.9609 | 67.8409 | -123.4438
3345.7969 | 123.1522 | -67.9047 | 55.1193 | -0.0029761 | -0.0060768 | 0.029308 | 0.05244 | -0.0095102 | 0.1266 | 0.00015261 | 0.016602 | 0.019742 | 0.012738 | 0.047395 | 0.054676 | 55.0791 | 50.3202 | -67.9638 | 55.0981 | 55.0573 | 55.2821 | -68.0784 | -67.9287 | -0.10953 | -67.954 | 55.0173 | 55.2088 | 55.0105 | -68.3702 | -0.17374 | -0.021239 | 122.9837 | -0.059164 | 0.11458 | -0.061976 | 0.16275 | -0.46555 | -0.10203 | -0.024029 | -0.049377 | 0.41617 | 0.089436 | -0.10882 | 123.0027 | 122.962 | 123.1867 | 118.2249 | -123.1977 | 122.922 | 123.1134 | 122.9152 | 67.7951 | -123.4895
3346.7969 | 123.1979 | -67.9001 | 55.069 | -0.0029761 | -0.0060768 | 0.029094 | 0.052654 | -0.0090828 | 0.1266 | 0.00015261 | 0.016388 | 0.020169 | 0.013165 | 0.048036 | 0.054462 | 55.0699 | 50.6407 | -67.9547 | 55.0844 | 55.0528 | 55.2729 | -68.0738 | -67.9333 | -0.10495 | -67.954 | 55.0173 | 55.2042 | 55.0151 | -68.3702 | -0.17374 | 0.01538 | 122.97 | -0.054586 | 0.11915 | -0.016201 | 0.20395 | -0.47012 | -0.051677 | -0.033185 | -0.053955 | 0.41617 | 0.13521 | -0.053889 | 122.9844 | 122.9529 | 123.173 | 118.5408 | -123.1428 | 122.9174 | 123.1043 | 122.9152 | 67.7951 | -123.4392
3347.8594 | 123.1567 | -67.9367 | 55.1331 | 0.0046549 | -0.0060768 | 0.029522 | 0.052654 | -0.0090828 | 0.12703 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.047822 | 0.054676 | 55.0745 | 50.6591 | -67.9638 | 55.0889 | 55.0436 | 55.2683 | -68.0876 | -67.9378 | -0.10953 | -67.954 | 55.0036 | 55.2042 | 55.0288 | -68.3702 | -0.15085 | -0.044129 | 123.0112 | -0.02712 | 0.12373 | -0.089446 | 0.13528 | -0.4335 | -0.1295 | -0.001142 | -0.017333 | 0.41617 | 0.071124 | -0.10424 | 123.0256 | 122.9803 | 123.205 | 118.5958 | -123.2206 | 122.9403 | 123.1409 | 122.9655 | 67.8272 | -123.5033
3348.7969 | 123.111 | -67.9596 | 55.1102 | -0.0029761 | -0.0060768 | 0.029308 | 0.052654 | -0.0090828 | 0.1266 | 0.00015261 | 0.016388 | 0.019528 | 0.012951 | 0.047608 | 0.054676 | 55.0745 | 50.6865 | -67.9592 | 55.0981 | 55.0619 | 55.2775 | -68.0784 | -67.9287 | -0.10495 | -67.9495 | 55.0036 | 55.2042 | 55.0242 | -68.3748 | -0.11881 | -0.012083 | 123.0341 | 0.000346 | 0.11915 | -0.048241 | 0.16733 | -0.41519 | -0.10661 | 0.030903 | 0.010134 | 0.42533 | 0.094013 | -0.085929 | 123.0577 | 123.0215 | 123.2371 | 118.6461 | -123.1886 | 122.9632 | 123.1638 | 122.9838 | 67.8546 | -123.485
3349.7969 | 123.1201 | -67.9184 | 55.0964 | 0.0046549 | -0.0060768 | 0.028667 | 0.05244 | -0.0090828 | 0.12682 | 0.015414 | 0.017029 | 0.019742 | 0.012524 | 0.047395 | 0.054676 | 55.0745 | 50.5629 | -67.9592 | 55.0981 | 55.0436 | 55.2683 | -68.083 | -67.9241 | -0.10953 | -67.9495 | 55.0173 | 55.2088 | 55.0242 | -68.3702 | -0.16459 | 0.001649 | 122.9929 | -0.040853 | 0.12373 | -0.052825 | 0.1719 | -0.45181 | -0.079143 | -0.005717 | -0.031065 | 0.42075 | 0.11232 | -0.072197 | 123.0165 | 122.962 | 123.1867 | 118.4813 | -123.1794 | 122.9357 | 123.1272 | 122.9426 | 67.8089 | -123.4666
3350.7969 | 123.143 | -67.9642 | 55.101 | 0.012286 | -0.0067178 | 0.029308 | 0.052654 | -0.0088692 | 0.12682 | 0.0077831 | 0.016602 | 0.019528 | 0.012951 | 0.047822 | 0.05489 | 55.0791 | 49.9997 | -67.9455 | 55.1027 | 55.0482 | 55.2775 | -68.0784 | -67.9241 | -0.10495 | -67.954 | 55.0173 | 55.2133 | 55.0334 | -68.3702 | -0.11423 | 0.00165 | 123.0432 | 0.018658 | 0.13289 | -0.052823 | 0.17648 | -0.40604 | -0.08372 | 0.040059 | 0.010132 | 0.41617 | 0.11232 | -0.067617 | 123.0668 | 123.0124 | 123.2417 | 117.9639 | -123.1794 | 122.9815 | 123.1775 | 122.9976 | 67.8592 | -123.4712
3351.7969 | 123.2117 | -67.9047 | 55.0735 | 0.0046549 | -0.0058632 | 0.028667 | 0.052867 | -0.0090828 | 0.12639 | 0.0077831 | 0.016388 | 0.019528 | 0.012951 | 0.047822 | 0.054676 | 55.0836 | 50.4805 | -67.9501 | 55.0981 | 55.0619 | 55.2775 | -68.0784 | -67.9333 | -0.10495 | -67.9586 | 55.0173 | 55.2042 | 55.0242 | -68.3656 | -0.17374 | 0.024538 | 122.9883 | -0.04543 | 0.12831 | -0.01162 | 0.20395 | -0.46097 | -0.056254 | -0.028607 | -0.053955 | 0.40701 | 0.13063 | -0.049308 | 123.0027 | 122.9666 | 123.1822 | 118.3852 | -123.1519 | 122.922 | 123.1088 | 122.9289 | 67.7997 | -123.4392
3352.7969 | 123.1659 | -67.9367 | 55.1056 | -0.0029761 | -0.0060768 | 0.029094 | 0.052226 | -0.0090828 | 0.12682 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.047608 | 0.054676 | 55.0745 | 51.0895 | -67.9592 | 55.0889 | 55.0482 | 55.2638 | -68.0784 | -67.9287 | -0.10953 | -67.954 | 55.0081 | 55.1996 | 55.0288 | -68.3702 | -0.14169 | -0.016663 | 123.0112 | -0.022542 | 0.11915 | -0.057401 | 0.15817 | -0.4335 | -0.097455 | 0.008015 | -0.017333 | 0.41617 | 0.094012 | -0.076774 | 123.0256 | 122.9849 | 123.2005 | 119.0262 | -123.184 | 122.9448 | 123.1363 | 122.9655 | 67.8272 | -123.4758
3353.7969 | 123.1567 | -67.923 | 55.1102 | -0.0029761 | -0.0060768 | 0.029094 | 0.052654 | -0.0092964 | 0.12682 | 0.00015261 | 0.016602 | 0.019528 | 0.012738 | 0.047608 | 0.05489 | 55.0653 | 51.4695 | -67.9592 | 55.0889 | 55.0436 | 55.2683 | -68.0876 | -67.9424 | -0.10953 | -67.9586 | 55.0036 | 55.1996 | 55.0197 | -68.3748 | -0.16459 | -0.02124 | 122.9883 | -0.036275 | 0.12831 | -0.066557 | 0.15817 | -0.45182 | -0.10661 | -0.019454 | -0.035644 | 0.41617 | 0.089435 | -0.090508 | 123.0119 | 122.9666 | 123.1913 | 119.3925 | -123.1977 | 122.9265 | 123.1226 | 122.9426 | 67.8134 | -123.485
3354.7969 | 123.0652 | -68.0008 | 55.0415 | -0.010607 | -0.0062906 | 0.029094 | 0.052654 | -0.0088692 | 0.12639 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.048036 | 0.054676 | 55.0424 | 55.2697 | -67.9913 | 55.0569 | 55.0253 | 55.2409 | -68.1105 | -67.9699 | -0.10495 | -67.9998 | 54.9761 | 55.1721 | 54.9693 | -68.4068 | -0.10966 | 0.015375 | 123.0432 | 0.009496 | 0.11916 | -0.016209 | 0.19937 | -0.40605 | -0.065417 | 0.030893 | 0.000966 | 0.40701 | 0.13063 | -0.072209 | 123.0577 | 123.0261 | 123.2417 | 123.2705 | -123.152 | 122.9769 | 123.1729 | 122.9701 | 67.8958 | -123.4483
3355.7969 | 123.1201 | -67.9688 | 55.0781 | 0.0046549 | -0.0062906 | 0.029522 | 0.052867 | -0.0090828 | 0.1266 | 0.00015261 | 0.016388 | 0.019742 | 0.012951 | 0.048036 | 0.05489 | 55.0424 | 55.288 | -67.9913 | 55.0615 | 55.0161 | 55.2454 | -68.1196 | -67.9607 | -0.10953 | -67.9815 | 54.9807 | 55.1721 | 54.9922 | -68.4023 | -0.15086 | -0.016667 | 123.0112 | -0.022547 | 0.12832 | -0.061988 | 0.16732 | -0.43351 | -0.09746 | 0.008007 | -0.012762 | 0.42075 | 0.094006 | -0.085937 | 123.0302 | 122.9849 | 123.2142 | 123.2568 | -123.1977 | 122.9494 | 123.1409 | 122.9609 | 67.8592 | -123.4804
3356.7969 | 123.1934 | -67.9596 | 55.0598 | -0.010607 | -0.0062906 | 0.029094 | 0.052654 | -0.0090828 | 0.12682 | 0.00015261 | 0.016602 | 0.019101 | 0.012738 | 0.047822 | 0.054676 | 55.0378 | 55.2835 | -67.9867 | 55.0569 | 55.0207 | 55.2363 | -68.115 | -67.9607 | -0.10953 | -67.9815 | 54.9807 | 55.1767 | 55.0151 | -68.4068 | -0.15544 | -0.002935 | 122.9974 | -0.027124 | 0.12832 | -0.039098 | 0.17648 | -0.44725 | -0.079149 | -0.001148 | -0.021917 | 0.42533 | 0.1169 | -0.044733 | 123.0165 | 122.9803 | 123.1959 | 123.243 | -123.1748 | 122.9403 | 123.1363 | 122.9747 | 67.8501 | -123.4667
3357.7969 | 123.0972 | -67.9596 | 55.101 | -0.0029761 | -0.0058632 | 0.029094 | 0.052867 | -0.0090828 | 0.1266 | -0.0074779 | 0.016388 | 0.019956 | 0.012738 | 0.047822 | 0.054676 | 55.0424 | 55.2835 | -67.9821 | 55.066 | 55.0024 | 55.2409 | -68.115 | -67.9653 | -0.10037 | -67.9815 | 54.9807 | 55.1767 | 54.9922 | -68.4023 | -0.15544 | -0.034977 | 123.002 | -0.022546 | 0.13289 | -0.098612 | 0.13986 | -0.44267 | -0.12035 | -0.005726 | -0.021917 | 0.42075 | 0.075697 | -0.10883 | 123.0256 | 122.962 | 123.2005 | 123.243 | -123.216 | 122.9403 | 123.1363 | 122.9518 | 67.8592 | -123.5033
3358.7969 | 123.2391 | -67.9504 | 55.0415 | -0.010607 | -0.0062906 | 0.028881 | 0.052654 | -0.0086556 | 0.12682 | 0.015414 | 0.016602 | 0.019528 | 0.012951 | 0.047822 | 0.054676 | 55.0424 | 55.288 | -67.9776 | 55.0569 | 55.0207 | 55.2363 | -68.115 | -67.9699 | -0.10495 | -67.9907 | 54.9807 | 55.1767 | 54.9693 | -68.4068 | -0.16459 | 0.015375 | 122.9929 | -0.027123 | 0.13747 | -0.020788 | 0.19479 | -0.4564 | -0.060839 | -0.019461 | -0.04023 | 0.41617 | 0.13521 | -0.072209 | 123.0073 | 122.9712 | 123.1867 | 123.2385 | -123.1565 | 122.9311 | 123.1271 | 122.9197 | 67.8455 | -123.4483
3359.7969 | 123.1338 | -67.9688 | 55.1056 | -0.010607 | -0.0060768 | 0.029094 | 0.052867 | -0.0090828 | 0.1266 | -0.0074779 | 0.016602 | 0.019742 | 0.012951 | 0.047608 | 0.054462 | 55.047 | 55.2926 | -68.0142 | 55.1164 | 55.126 | 55.2867 | -68.17 | -67.9653 | -0.11869 | -67.9907 | 54.9852 | 55.1767 | 55.1158 | -68.4023 | -0.20123 | 0.010807 | 123.0158 | -0.045439 | 0.15579 | 0.020441 | 0.18106 | -0.43351 | -0.12035 | 0.003429 | -0.021919 | 0.41159 | 0.071119 | 0.01022 | 123.0851 | 123.0948 | 123.2554 | 123.2614 | -123.2756 | 122.954 | 123.1455 | 123.0846 | 67.8501 | -123.5079
3360.7969 | 123.1659 | -67.9642 | 55.0598 | 0.0046549 | -0.0054358 | 0.028667 | 0.052867 | -0.0088692 | 0.12596 | -0.0074779 | 0.016602 | 0.019315 | 0.013165 | 0.047608 | 0.054249 | 55.0424 | 55.2606 | -67.9776 | 55.0569 | 54.8376 | 55.1676 | -68.1013 | -67.9378 | -0.10495 | -67.9952 | 54.9715 | 55.1676 | 54.7312 | -68.4023 | -0.13712 | -0.002935 | 123.0066 | -0.01339 | 0.12373 | -0.22226 | 0.1078 | -0.43809 | -0.088306 | 0.026323 | -0.031076 | 0.40701 | 0.10774 | -0.32861 | 123.0211 | 122.8017 | 123.1318 | 123.2247 | -123.1611 | 122.9357 | 123.1317 | 122.6954 | 67.8592 | -123.4621
3361.7969 | 123.1293 | -67.9688 | 55.0873 | 0.0046549 | -0.0056496 | 0.029094 | 0.053081 | -0.0090828 | 0.12596 | 0.00015261 | 0.016602 | 0.019742 | 0.013165 | 0.047395 | 0.054676 | 55.0424 | 55.2743 | -67.9776 | 55.0569 | 54.8833 | 55.1905 | -68.0967 | -67.9424 | -0.11411 | -67.9907 | 54.9715 | 55.1767 | 54.7358 | -68.4023 | -0.12797 | -0.030401 | 123.0112 | -0.008812 | 0.11916 | -0.20393 | 0.10322 | -0.43351 | -0.11577 | 0.026322 | -0.021919 | 0.41159 | 0.08943 | -0.35149 | 123.0256 | 122.8521 | 123.1593 | 123.243 | -123.184 | 122.9403 | 123.1455 | 122.7045 | 67.8546 | -123.4895
3362.7969 | 123.2483 | -67.9642 | 55.0461 | -0.0029761 | -0.0056496 | 0.028667 | 0.05244 | -0.0090828 | 0.12596 | -0.0074779 | 0.016174 | 0.019528 | 0.013165 | 0.047395 | 0.054249 | 55.0424 | 55.256 | -67.9684 | 55.0706 | 54.8559 | 55.1997 | -68.1059 | -67.9378 | -0.10495 | -67.9907 | 54.9761 | 55.1767 | 54.7358 | -68.4068 | -0.1417 | 0.024533 | 123.0066 | -0.004234 | 0.13747 | -0.19021 | 0.15358 | -0.44267 | -0.069995 | 0.026323 | -0.026497 | 0.41617 | 0.13063 | -0.31029 | 123.0348 | 122.82 | 123.1638 | 123.2202 | -123.152 | 122.9403 | 123.1409 | 122.7 | 67.8592 | -123.4529
3363.7969 | 123.0881 | -67.9962 | 55.0873 | -0.018238 | -0.0056496 | 0.029094 | 0.052867 | -0.0086556 | 0.12617 | -0.0074779 | 0.016815 | 0.019528 | 0.013165 | 0.047608 | 0.054462 | 55.0424 | 55.2606 | -67.973 | 55.0569 | 54.8559 | 55.1951 | -68.1013 | -67.9424 | -0.10495 | -67.9907 | 54.9807 | 55.1721 | 54.7541 | -68.4068 | -0.10508 | -0.030401 | 123.0386 | 0.023232 | 0.12831 | -0.23141 | 0.1078 | -0.41062 | -0.10661 | 0.053788 | 0.005547 | 0.41617 | 0.084851 | -0.33318 | 123.0531 | 122.8521 | 123.1913 | 123.2568 | -123.1886 | 122.9769 | 123.1683 | 122.7503 | 67.8913 | -123.4941
3364.7969 | 123.2254 | -67.9367 | 55.0415 | -0.018238 | -0.0054358 | 0.028881 | 0.05244 | -0.0086556 | 0.12596 | 0.00015261 | 0.016815 | 0.019742 | 0.013379 | 0.047822 | 0.054249 | 55.047 | 55.2697 | -67.973 | 55.0615 | 54.8742 | 55.218 | -68.1013 | -67.947 | -0.10495 | -67.9815 | 54.9807 | 55.1721 | 54.7449 | -68.4068 | -0.16459 | 0.019954 | 122.9837 | -0.036277 | 0.12831 | -0.16731 | 0.17647 | -0.47013 | -0.060839 | -0.0103 | -0.044805 | 0.42533 | 0.13063 | -0.29656 | 122.9982 | 122.8109 | 123.1547 | 123.2064 | -123.1428 | 122.9174 | 123.1088 | 122.6817 | 67.8318 | -123.4483
3365.7969 | 123.1567 | -67.9642 | 55.0552 | -0.0029761 | -0.0058632 | 0.028667 | 0.052226 | -0.0088692 | 0.12596 | -0.0074779 | 0.016388 | 0.019528 | 0.013379 | 0.047608 | 0.054249 | 55.0516 | 55.2651 | -67.9821 | 55.0477 | 54.8467 | 55.1401 | -68.0464 | -67.947 | -0.10495 | -67.9907 | 54.9761 | 55.1721 | 54.7221 | -68.4068 | -0.082178 | -0.007514 | 123.0158 | -0.017969 | 0.064209 | -0.20852 | 0.084902 | -0.44267 | -0.07915 | 0.017165 | -0.026497 | 0.41617 | 0.11689 | -0.33319 | 123.0119 | 122.8109 | 123.1043 | 123.2293 | -123.1016 | 122.9403 | 123.1363 | 122.6862 | 67.8592 | -123.4621
3366.7969 | 123.2346 | -67.9367 | 55.0461 | -0.0029761 | -0.0060768 | 0.029308 | 0.052654 | -0.0090828 | 0.12639 | -0.0074779 | 0.016815 | 0.019956 | 0.013165 | 0.047822 | 0.054676 | 55.0378 | 55.2743 | -67.973 | 55.0523 | 54.9291 | 55.2042 | -68.0372 | -67.947 | -0.13242 | -67.8625 | 54.9807 | 55.1767 | 54.7816 | -68.329 | -0.10049 | 0.006219 | 122.9746 | -0.036277 | 0.064208 | -0.11694 | 0.15816 | -0.39229 | -0.065417 | -0.0103 | 0.074242 | 0.46653 | 0.13063 | -0.26451 | 122.989 | 122.8658 | 123.1409 | 123.211 | -123.0833 | 122.9174 | 123.1134 | 122.7183 | 67.8043 | -123.3751
3367.8594 | 123.1659 | -67.9413 | 55.1056 | -0.0029761 | -0.0058632 | 0.029094 | 0.052867 | -0.0092964 | 0.1266 | 0.00015261 | 0.016388 | 0.019956 | 0.013379 | 0.048036 | 0.054462 | 55.0424 | 55.288 | -68.0096 | 55.1027 | 55.126 | 55.2867 | -68.1654 | -67.9607 | -0.11411 | -67.9724 | 54.9807 | 55.1767 | 55.0838 | -68.3977 | -0.22412 | -0.002928 | 122.9837 | -0.068326 | 0.15579 | 0.020441 | 0.18106 | -0.4564 | -0.12493 | -0.019459 | -0.03107 | 0.42533 | 0.071119 | -0.021831 | 123.0439 | 123.0673 | 123.2279 | 123.2293 | -123.271 | 122.9219 | 123.118 | 123.025 | 67.8272 | -123.5033
3368.7969 | 123.2117 | -67.955 | 55.0369 | -0.010607 | -0.0054358 | 0.028667 | 0.053081 | -0.0086556 | 0.12596 | 0.00015261 | 0.016602 | 0.019956 | 0.012951 | 0.047822 | 0.054676 | 55.0378 | 55.2743 | -67.9776 | 55.0798 | 55.0986 | 55.2638 | -68.1425 | -67.9378 | -0.11869 | -67.9632 | 54.9898 | 55.1767 | 55.0883 | -68.4068 | -0.18749 | 0.042845 | 122.9929 | -0.022545 | 0.16494 | 0.061632 | 0.22684 | -0.45182 | -0.047104 | 0.017168 | -0.00818 | 0.44364 | 0.13978 | 0.051413 | 123.0348 | 123.0536 | 123.2188 | 123.2293 | -123.1794 | 122.9448 | 123.1317 | 123.0434 | 67.8363 | -123.4438
3369.7969 | 123.1338 | -67.9871 | 55.0735 | -0.018238 | -0.0060768 | 0.028667 | 0.053081 | -0.0090828 | 0.12639 | 0.00015261 | 0.016602 | 0.019956 | 0.012951 | 0.047395 | 0.054676 | 55.0378 | 55.2606 | -67.9638 | 55.0615 | 55.0116 | 55.2454 | -68.1242 | -67.9424 | -0.12327 | -67.9678 | 54.9807 | 55.1859 | 55.0792 | -68.4068 | -0.13713 | -0.012089 | 123.0249 | 0.023234 | 0.16036 | -0.061989 | 0.1719 | -0.41978 | -0.092882 | 0.044633 | 0.019285 | 0.43906 | 0.11232 | 0.005635 | 123.0485 | 122.9986 | 123.2325 | 123.2476 | -123.1977 | 122.9677 | 123.1729 | 123.0662 | 67.8638 | -123.4804
3370.7969 | 123.2346 | -67.9092 | 55.0278 | 0.0046549 | -0.0058632 | 0.029094 | 0.053081 | -0.0086556 | 0.12617 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.048036 | 0.054676 | 55.0424 | 55.2743 | -67.9867 | 55.0615 | 55.0024 | 55.2409 | -67.996 | -67.9378 | -0.10953 | -67.9586 | 54.9761 | 55.1721 | 54.7495 | -68.4068 | -0.086741 | 0.033687 | 122.9517 | -0.077478 | 0.009263 | -0.02537 | 0.2131 | -0.4976 | -0.051684 | -0.028608 | -0.049377 | 0.44822 | 0.14436 | -0.27825 | 122.9707 | 122.9116 | 123.1501 | 123.1835 | -123.0238 | 122.8853 | 123.0814 | 122.6588 | 67.7997 | -123.4346
3371.7969 | 123.2208 | -67.955 | 55.0552 | -0.0029761 | -0.0056496 | 0.028881 | 0.053081 | -0.0088692 | 0.12575 | -0.0074779 | 0.016602 | 0.019742 | 0.012951 | 0.047822 | 0.054676 | 55.047 | 55.2651 | -67.9821 | 55.0615 | 54.9932 | 55.2409 | -68.1105 | -67.9424 | -0.10953 | -67.9586 | 54.9807 | 55.1767 | 54.896 | -68.4068 | -0.15544 | 0.006221 | 123.002 | -0.027124 | 0.12831 | -0.061994 | 0.18563 | -0.45182 | -0.074572 | 0.012589 | -0.003601 | 0.44822 | 0.12147 | -0.1592 | 123.0165 | 122.9483 | 123.1959 | 123.2202 | -123.1657 | 122.9357 | 123.1317 | 122.8511 | 67.8455 | -123.4621
3372.7969 | 123.1934 | -67.9459 | 55.0232 | 0.0046549 | -0.0062906 | 0.028881 | 0.052654 | -0.0088692 | 0.12639 | 0.00015261 | 0.016602 | 0.019956 | 0.012951 | 0.047822 | 0.054676 | 55.0424 | 55.2743 | -67.9821 | 55.0615 | 54.9841 | 55.2363 | -68.1105 | -67.9562 | -0.11869 | -67.954 | 54.9761 | 55.163 | 54.9647 | -68.4023 | -0.16459 | 0.038265 | 122.9883 | -0.036279 | 0.12831 | -0.039108 | 0.2131 | -0.4564 | -0.047106 | -0.010302 | -0.008178 | 0.44822 | 0.13978 | -0.058476 | 123.0073 | 122.9299 | 123.1822 | 123.2202 | -123.1336 | 122.9219 | 123.1088 | 122.9106 | 67.8272 | -123.4255
3373.7969 | 123.1201 | -67.9733 | 55.069 | -0.0029761 | -0.0060768 | 0.029094 | 0.052654 | -0.0095102 | 0.12639 | 0.00015261 | 0.016815 | 0.019528 | 0.013165 | 0.048036 | 0.054676 | 55.0333 | 55.2926 | -67.9867 | 55.066 | 55.007 | 55.2363 | -68.1059 | -67.9607 | -0.11411 | -67.9586 | 54.9852 | 55.1767 | 54.9739 | -68.4114 | -0.13255 | -0.002934 | 123.0066 | -0.013391 | 0.11916 | -0.06199 | 0.16732 | -0.43809 | -0.083726 | 0.012585 | 0.01471 | 0.4528 | 0.10774 | -0.095096 | 123.0394 | 122.9803 | 123.2096 | 123.2659 | -123.1748 | 122.9586 | 123.15 | 122.9472 | 67.8592 | -123.4804
3374.7969 | 123.23 | -67.9459 | 55.0507 | -0.010607 | -0.0058632 | 0.028881 | 0.052867 | -0.0088692 | 0.12639 | -0.0074779 | 0.016815 | 0.019956 | 0.012738 | 0.048036 | 0.054462 | 55.0378 | 55.2697 | -67.9776 | 55.0569 | 54.9841 | 55.2317 | -68.1059 | -67.9333 | -0.10495 | -67.9495 | 54.9807 | 55.1676 | 54.9281 | -68.4023 | -0.16001 | 0.00622 | 122.9837 | -0.0317 | 0.12831 | -0.066574 | 0.18105 | -0.4564 | -0.069994 | 0.012592 | -0.003599 | 0.4528 | 0.11689 | -0.12257 | 123.0027 | 122.9299 | 123.1776 | 123.2156 | -123.1565 | 122.9265 | 123.1134 | 122.874 | 67.8409 | -123.4529
3375.7969 | 123.2254 | -67.9596 | 55.0644 | -0.025869 | -0.0065042 | 0.029094 | 0.052654 | -0.0092964 | 0.12703 | 0.00015261 | 0.016388 | 0.019956 | 0.012524 | 0.04825 | 0.05489 | 55.0424 | 55.3109 | -68.0233 | 55.121 | 55.0436 | 55.2912 | -68.1242 | -67.9882 | -0.12327 | -67.9449 | 54.9715 | 55.163 | 54.9144 | -68.4023 | -0.1646 | 0.056585 | 123.002 | -0.06375 | 0.10085 | -0.020781 | 0.22684 | -0.44267 | -0.092884 | -0.02862 | 0.014713 | 0.45738 | 0.098582 | -0.15004 | 123.0806 | 123.0032 | 123.2508 | 123.2705 | -123.1886 | 122.9311 | 123.1226 | 122.8739 | 67.8363 | -123.4667
3376.7969 | 123.2254 | -67.955 | 55.0507 | -0.010607 | -0.0067178 | 0.029308 | 0.052654 | -0.0086556 | 0.1266 | 0.00015261 | 0.016602 | 0.019742 | 0.013165 | 0.047822 | 0.054676 | 55.0378 | 55.2972 | -68.0188 | 55.1164 | 55.1215 | 55.2912 | -68.1379 | -67.9699 | -0.12784 | -67.9357 | 54.9761 | 55.1721 | 54.8319 | -68.4068 | -0.18291 | 0.065739 | 122.9929 | -0.06375 | 0.11916 | 0.070794 | 0.24057 | -0.45182 | -0.074572 | -0.014883 | 0.019292 | 0.47111 | 0.12147 | -0.21872 | 123.0714 | 123.0765 | 123.2463 | 123.2522 | -123.1886 | 122.9311 | 123.1271 | 122.787 | 67.8272 | -123.4575
3377.8125 | 123.1476 | -67.9596 | 55.0781 | -0.0029761 | -0.0054358 | 0.029094 | 0.052654 | -0.0088692 | 0.12617 | 0.00015261 | 0.016388 | 0.019528 | 0.013165 | 0.047822 | 0.054676 | 55.0424 | 55.2926 | -68.0096 | 55.1072 | 55.1077 | 55.2775 | -67.996 | -67.9653 | -0.15074 | -67.8533 | 54.9807 | 55.1676 | 54.8274 | -68.2924 | -0.036387 | 0.029117 | 123.002 | -0.050015 | -0.013628 | 0.029591 | 0.19937 | -0.33278 | -0.09746 | -0.005726 | 0.10629 | 0.43906 | 0.089427 | -0.25077 | 123.0668 | 123.0673 | 123.2371 | 123.2522 | -123.0741 | 122.9403 | 123.1271 | 122.787 | 67.8089 | -123.3705
3378.7969 | 123.1888 | -67.9504 | 55.0598 | -0.0029761 | -0.0056496 | 0.028667 | 0.052654 | -0.0086556 | 0.12617 | 0.00015261 | 0.016815 | 0.019956 | 0.013379 | 0.047822 | 0.054676 | 55.0287 | 55.2789 | -67.9959 | 55.0889 | 54.9703 | 55.2683 | -67.7625 | -67.9516 | -0.17363 | -67.7846 | 54.9807 | 55.163 | 54.7862 | -68.1321 | 0.18798 | 0.029114 | 122.9791 | -0.045436 | -0.23342 | -0.089466 | 0.20853 | -0.18167 | -0.079149 | -0.001146 | 0.16581 | 0.34748 | 0.10316 | -0.27366 | 123.0394 | 122.9208 | 123.2188 | 123.2293 | -122.8223 | 122.9311 | 123.1134 | 122.7366 | 67.7768 | -123.1919
3379.7969 | 123.2071 | -67.9184 | 55.0552 | -0.0029761 | -0.0056496 | 0.028881 | 0.05244 | -0.0090828 | 0.12617 | 0.0077831 | 0.016388 | 0.019528 | 0.012951 | 0.04825 | 0.054462 | 55.0378 | 55.2743 | -67.9913 | 55.0889 | 54.9658 | 55.2592 | -68.115 | -67.9424 | -0.12784 | -67.9632 | 54.9807 | 55.163 | 54.8274 | -68.4114 | -0.19664 | 0.033691 | 122.9562 | -0.072901 | 0.12374 | -0.089468 | 0.20395 | -0.49302 | -0.074572 | -0.024032 | -0.044801 | 0.44822 | 0.10774 | -0.22788 | 123.0073 | 122.8842 | 123.1776 | 123.1927 | -123.1703 | 122.8991 | 123.0814 | 122.7458 | 67.7906 | -123.4667
3380.7969 | 123.2071 | -67.9367 | 55.0735 | -0.010607 | -0.0058632 | 0.028881 | 0.053081 | -0.0088692 | 0.12617 | 0.00015261 | 0.016602 | 0.019742 | 0.012951 | 0.04825 | 0.054249 | 55.0378 | 55.2743 | -67.9821 | 55.0844 | 55.0986 | 55.2638 | -68.1288 | -67.9424 | -0.13242 | -67.9586 | 54.9807 | 55.1721 | 54.8411 | -68.4023 | -0.19206 | 0.010803 | 122.9746 | -0.045434 | 0.14663 | 0.025011 | 0.19022 | -0.46555 | -0.092882 | -0.005721 | -0.021911 | 0.44364 | 0.098584 | -0.23245 | 123.0211 | 123.0353 | 123.2005 | 123.211 | -123.2023 | 122.9174 | 123.1088 | 122.7778 | 67.8043 | -123.4758
3381.7969 | 123.1796 | -67.9321 | 55.0644 | -0.010607 | -0.0058632 | 0.028881 | 0.052867 | -0.0090828 | 0.12617 | -0.015108 | 0.016602 | 0.019742 | 0.012951 | 0.048036 | 0.054676 | 55.0287 | 55.2651 | -67.9821 | 55.0752 | 55.0436 | 55.2592 | -68.1242 | -67.9424 | -0.13242 | -67.954 | 54.9852 | 55.1676 | 54.7816 | -68.3977 | -0.19206 | 0.010801 | 122.9608 | -0.050012 | 0.14205 | -0.020781 | 0.19479 | -0.46555 | -0.079148 | -0.010299 | -0.021911 | 0.44364 | 0.10316 | -0.28282 | 123.0073 | 122.9757 | 123.1913 | 123.1973 | -123.1886 | 122.9174 | 123.0997 | 122.7137 | 67.7997 | -123.4621
3382.7969 | 123.1796 | -67.9321 | 55.0644 | -0.0029761 | -0.0058632 | 0.02824 | 0.052867 | -0.0088692 | 0.12575 | 0.00015261 | 0.016815 | 0.019742 | 0.013165 | 0.047822 | 0.054676 | 55.0424 | 55.2651 | -67.9776 | 55.0706 | 55.0528 | 55.2546 | -68.1059 | -67.9424 | -0.12784 | -67.9586 | 54.9807 | 55.1676 | 54.8411 | -68.4114 | -0.17375 | 0.006223 | 122.9746 | -0.045433 | 0.12831 | -0.011623 | 0.19021 | -0.47929 | -0.083727 | -0.010299 | -0.026489 | 0.4528 | 0.10316 | -0.2233 | 123.0027 | 122.9849 | 123.1867 | 123.1973 | -123.1703 | 122.9128 | 123.0997 | 122.7732 | 67.8043 | -123.4758
3383.7969 | 123.2437 | -64.444 | 58.5251 | -0.0029761 | -0.072102 | 0.024607 | -0.0043998 | -0.0092964 | 0.012292 | 0.0077831 | 0.016388 | 0.019528 | 0.013165 | 0.047608 | 0.054249 | 0.25286 | 0.39975 | -0.39298 | 0.61527 | 0.60936 | 0.89743 | -0.30116 | -64.4855 | -0.095794 | -64.4925 | 58.4466 | 58.6519 | 58.2705 | -64.9224 | 64.1428 | -57.9098 | 64.6968 | 64.051 | -0.091824 | -57.9157 | -57.6276 | -0.47839 | -0.078499 | -0.041532 | -0.048565 | 0.42982 | 0.12678 | -0.25462 | 65.0592 | 65.0533 | 65.3414 | 64.8437 | -58.8262 | 122.8906 | 123.0958 | 122.7144 | 64.3482 | -123.4474
3384.7969 | -150 | -53.8834 | 58.4564 | -0.010607 | -0.072957 | 0.02418 | -0.004827 | -0.0092964 | 0.011437 | -0.04563 | 0.016815 | 0.02252 | 0.016583 | 0.057437 | 0.044848 | -0.026423 | 0.10671 | -0.026723 | 0.30394 | 0.35294 | 0.58151 | 1.6724 | -64.1741 | -1.6571 | -55.0421 | 58.41 | 58.281 | 58.124 | -55.6274 | 55.5557 | -58.1525 | 53.8569 | 53.8566 | -1.6991 | -58.1035 | -57.8749 | -1.744 | -0.046463 | -10.2908 | -1.1587 | 0.58528 | -0.17542 | -0.33247 | 54.1873 | 54.2363 | 54.4649 | 53.9901 | -56.7841 | 112.2933 | 112.1644 | 112.0073 | 52.2262 | -114.0838
3385.7969 | -150 | -49.0448 | 58.2413 | -0.010607 | -0.072743 | 0.023966 | -0.0046134 | -0.0092964 | 0.011437 | 0.00015261 | 0.018311 | 0.02487 | 0.020429 | 0.065984 | 0.038866 | -0.049315 | 0.0884 | -0.031301 | 0.25358 | 0.33004 | 0.55862 | 2.3958 | -64.0459 | -2.5317 | -47.0019 | 58.3504 | 58.2077 | 57.8309 | -46.7307 | 51.4406 | -57.9877 | 48.9955 | 49.0135 | -2.4271 | -57.9112 | -57.6827 | 2.3141 | 0.10917 | -15.0011 | 2.0429 | -0.27114 | -0.033527 | -0.41035 | 49.2984 | 49.3748 | 49.6034 | 49.1332 | -55.8454 | 107.3952 | 107.2525 | 106.8757 | 46.5131 | -104.972
3386.7969 | 122.6074 | -45.7809 | 57.6508 | -0.0029761 | -0.072529 | 0.024394 | -0.0050408 | -0.0097238 | 0.011437 | 0.0077831 | 0.01767 | 0.023374 | 0.020215 | 0.06513 | 0.039507 | -0.03558 | 0.092979 | -0.022144 | 0.16201 | 0.32088 | 0.57693 | 2.3546 | -64.165 | -2.2295 | -49.2729 | 58.3642 | 58.2947 | 58.0507 | -48.4661 | 48.1356 | -57.4887 | 45.7454 | 45.7588 | -2.3768 | -57.3299 | -57.0738 | -2.6851 | 0.71342 | -18.384 | -3.492 | -0.80681 | 0.64398 | 0.39994 | 45.943 | 46.1018 | 46.3579 | 45.8739 | -55.2961 | 104.1451 | 104.0757 | 103.8316 | 43.5515 | -106.1168
3387.7969 | 122.7768 | -60.1685 | 57.7972 | -0.010607 | -0.072743 | 0.023539 | -0.0056818 | -0.0090828 | 0.011224 | 0.00015261 | 0.017884 | 0.023801 | 0.019147 | 0.066839 | 0.040575 | -0.044736 | 0.092979 | -0.022144 | 0.17117 | 0.32546 | 0.57235 | 2.0158 | -64.2245 | -2.0601 | -49.9414 | 58.3688 | 58.368 | 57.8263 | -50.3114 | 62.1842 | -57.6261 | 60.1237 | 60.1463 | -2.0379 | -57.4718 | -57.2249 | 9.8571 | 0.57151 | -4.0561 | 10.2271 | 0.36996 | 0.57075 | 0.029102 | 60.3396 | 60.4939 | 60.7408 | 60.2614 | -55.7815 | 118.5372 | 118.5365 | 117.9948 | 58.1084 | -108.1086
3388.7969 | 107.4417 | -48.2254 | 55.426 | -0.0029761 | -0.072957 | 0.02418 | -0.004827 | -0.0099374 | 0.011437 | 0.0077831 | 0.017884 | 0.023374 | 0.019147 | 0.065343 | 0.041002 | -0.040158 | 0.083821 | -0.012988 | 0.20321 | -0.072904 | 0.55862 | 1.9105 | -64.2611 | -1.8723 | -50.4496 | 58.3733 | 58.4 | 57.8492 | -51.1355 | 50.1359 | -55.2228 | 48.1852 | 48.2124 | -1.9234 | -55.4989 | -54.8674 | -2.9101 | 2.9473 | -16.0357 | -2.2242 | 0.68591 | 2.974 | 2.4232 | 48.4286 | 48.1525 | 48.784 | 48.3092 | -53.5156 | 106.5987 | 106.6254 | 106.0746 | 46.3531 | -106.5616
3389.7969 | 123.0286 | -53.7094 | 57.9025 | -0.010607 | -0.072957 | 0.023539 | -0.0046134 | -0.0092964 | 0.01101 | -0.0074779 | 0.017029 | 0.022733 | 0.017438 | 0.062779 | 0.042711 | -0.06305 | 0.083821 | -0.012988 | 0.19864 | -0.10496 | 0.54946 | 1.8235 | -64.3573 | -1.7716 | -53.6044 | 58.4054 | 58.4 | 57.8584 | -53.4021 | 55.5329 | -57.7039 | 53.6464 | 53.6964 | -1.8364 | -58.0075 | -57.3531 | 0.30736 | 0.50285 | -10.6479 | 0.10505 | -0.20231 | 0.49752 | -0.044134 | 53.908 | 53.6045 | 54.2589 | 53.7932 | -56.0791 | 112.1148 | 112.1095 | 111.5678 | 51.9378 | -111.3046
3390.7969 | 122.6944 | -56.369 | 58.1955 | -0.0029761 | -0.071461 | 0.023753 | -0.004827 | -0.0095102 | 0.013147 | 0.00015261 | 0.017029 | 0.021665 | 0.017011 | 0.061284 | 0.042498 | -0.053893 | 0.0884 | -0.026723 | 0.20779 | -0.11869 | 0.55404 | 1.4526 | -64.3893 | -1.5518 | -54.8131 | 58.4237 | 58.4458 | 57.9133 | -55.0275 | 57.8216 | -57.9877 | 56.3151 | 56.3423 | -1.4793 | -58.3142 | -57.6415 | 1.3415 | 0.2282 | -8.0203 | 1.5559 | 0.21439 | 0.25034 | -0.28216 | 56.5768 | 56.2503 | 56.9231 | 56.4574 | -56.7429 | 114.7927 | 114.8149 | 114.2824 | 54.8172 | -113.223
3391.7969 | 122.905 | -63.4598 | 58.8638 | 0.0046549 | -0.071033 | 0.023753 | -0.0050408 | -0.0090828 | 0.012933 | -0.0074779 | 0.016815 | 0.020383 | 0.014233 | 0.052309 | 0.054035 | -0.03558 | 0.097557 | -0.012988 | 0.20321 | -0.11869 | 0.55862 | 0.051416 | -64.4855 | -0.28352 | -62.0979 | 58.4649 | 58.6473 | 58.0782 | -63.9242 | 63.5112 | -58.6606 | 63.4242 | 63.4468 | -0.064404 | -58.9825 | -58.3052 | -0.4644 | -0.39893 | -1.0257 | 1.3619 | 1.8263 | -0.21654 | -0.78566 | 63.663 | 63.3411 | 64.0184 | 63.5573 | -58.8124 | 121.9247 | 122.1071 | 121.5379 | 63.1763 | -122.788
3392.7969 | 122.7768 | -65.2725 | 56.9183 | -0.0029761 | -0.071247 | 0.023539 | -0.004827 | -0.0097238 | 0.013147 | -0.0074779 | 0.041811 | 0.045381 | 0.041153 | 0.12902 | 0.054035 | -0.040158 | 0.092979 | -0.012988 | 0.1849 | -0.10496 | 0.5632 | 0.088047 | -65.3463 | 0.74669 | 41.9121 | 57.6041 | 57.8002 | 57.2174 | -65.7694 | 65.3606 | -56.7334 | 65.2324 | 65.2595 | -0.10103 | -57.0233 | -56.3551 | -0.49692 | 0.68581 | -0.073777 | 107.1846 | 107.6815 | 0.88191 | 0.29905 | 65.4574 | 65.1676 | 65.8357 | 65.3655 | -56.8303 | 122.8767 | 123.0728 | 122.4899 | 66.0192 | -122.6878
3393.875 | 97.76 | -55.4443 | 57.7927 | 0.0046549 | -0.071461 | 0.023753 | -0.0046134 | -0.0097238 | 0.012933 | 0.00015261 | 0.044375 | 0.047731 | 0.043503 | 0.13607 | 0.054249 | -0.044736 | 0.092979 | -0.008409 | 0.19406 | -0.11411 | 0.55404 | 0.088047 | -65.4058 | 0.84742 | 51.5091 | 57.5263 | 57.7316 | 57.1396 | -65.8519 | 55.5324 | -57.5986 | 55.3996 | 55.4359 | -0.096456 | -57.9068 | -57.2386 | -10.4075 | -0.26636 | -9.9615 | 106.9534 | 117.3609 | -0.061094 | -0.65311 | 55.6384 | 55.3302 | 55.9984 | 55.5373 | -57.7046 | 112.9706 | 113.1759 | 112.5839 | 56.2918 | -123.6445
3394.7969 | 122.8088 | -65.3549 | 57.1106 | 0.0046549 | -0.071247 | 0.023966 | -0.004827 | -0.0097238 | 0.012933 | 0.0077831 | 0.044588 | 0.047731 | 0.043717 | 0.13607 | 0.054462 | -0.044736 | 0.092979 | -0.022144 | 0.20321 | -0.11869 | 0.55404 | 0.1201 | -65.4104 | 0.86116 | 51.651 | 57.5217 | 57.7316 | 57.1487 | -65.8564 | 65.475 | -56.9074 | 65.3102 | 65.3328 | -0.14224 | -57.2293 | -56.5566 | -0.50152 | 0.41113 | -0.055482 | 117.0059 | 117.5075 | 0.62097 | 0.038114 | 65.5581 | 65.2362 | 65.909 | 65.4479 | -56.9905 | 122.8766 | 123.0865 | 122.5036 | 66.2161 | -122.967
3395.7969 | 122.8043 | -65.3641 | 57.6324 | 0.0046549 | -0.071461 | 0.023753 | -0.004827 | -0.0097238 | 0.013147 | -0.0074779 | 0.044161 | 0.047945 | 0.043503 | 0.13628 | 0.053821 | -0.03558 | 0.092979 | -0.017566 | 0.20321 | -0.13243 | 0.55404 | 0.097205 | -65.415 | 0.87947 | 51.9715 | 57.5217 | 57.727 | 57.1487 | -65.8564 | 65.4613 | -57.4292 | 65.3285 | 65.3465 | -0.11477 | -57.7649 | -57.0784 | -0.49236 | -0.11072 | -0.050905 | 117.3356 | 117.828 | 0.094545 | -0.48374 | 65.5673 | 65.2316 | 65.9181 | 65.4571 | -57.5352 | 122.8858 | 123.0911 | 122.5128 | 66.2435 | -123.4889
3396.7969 | 122.4609 | -65.007 | 57.6508 | 0.0046549 | -0.071674 | 0.023966 | -0.004827 | -0.0097238 | 0.012933 | 0.0077831 | 0.044802 | 0.047945 | 0.043503 | 0.13586 | 0.054462 | -0.031001 | 0.083821 | -0.017566 | 0.20779 | -0.10038 | 0.55404 | 0.088047 | -65.4058 | 0.81079 | 51.9212 | 57.5309 | 57.727 | 57.1396 | -65.8564 | 65.0951 | -57.443 | 64.976 | 64.9895 | -0.10561 | -57.7511 | -57.0967 | -0.84942 | -0.11987 | -0.3988 | 116.9282 | 117.7776 | 0.076234 | -0.5112 | 65.2148 | 64.9066 | 65.5611 | 65.0908 | -57.5627 | 122.5379 | 122.734 | 122.1466 | 65.8178 | -123.5072
3397.7969 | 122.937 | -65.3915 | 57.6599 | -0.0029761 | -0.071247 | 0.023539 | -0.004827 | -0.0095102 | 0.012933 | -0.0074779 | 0.044161 | 0.047518 | 0.043717 | 0.13564 | 0.054249 | -0.040158 | 0.079243 | -0.012988 | 0.19406 | 0.023254 | 0.55862 | 0.07431 | -65.4196 | 0.81995 | 51.7746 | 57.5263 | 57.7224 | 57.3685 | -65.8519 | 65.4659 | -57.4659 | 65.3514 | 65.3786 | -0.087298 | -57.6367 | -57.1013 | -0.46032 | -0.1336 | -0.028018 | 117.1662 | 117.6265 | 0.062501 | -0.29143 | 65.5856 | 65.4148 | 65.9502 | 65.4708 | -57.5856 | 122.9179 | 123.114 | 122.76 | 66.2115 | -123.5118
3398.7969 | 122.7219 | -65.1947 | 57.6462 | 0.0046549 | -0.071674 | 0.023325 | -0.0046134 | -0.0095102 | 0.012933 | 0.00015261 | 0.044375 | 0.047731 | 0.043717 | 0.13586 | 0.054462 | -0.044736 | 0.0884 | -0.017566 | 0.21695 | 0.023254 | 0.54946 | 0.046837 | -65.4104 | 0.82453 | 52.0311 | 57.5263 | 57.727 | 57.4417 | -65.8519 | 65.2415 | -57.4292 | 65.15 | 65.1771 | -0.064403 | -57.6229 | -57.0967 | -0.65716 | -0.11987 | -0.2157 | 117.2258 | 117.8829 | 0.080812 | -0.20444 | 65.4117 | 65.218 | 65.7442 | 65.2831 | -57.5993 | 122.721 | 122.9217 | 122.6364 | 66.0192 | -123.498
3399.7969 | 122.9645 | -65.3412 | 57.6324 | -0.0029761 | -0.071674 | 0.023753 | -0.0050408 | -0.0092964 | 0.012933 | -0.0074779 | 0.044161 | 0.047518 | 0.043289 | 0.13586 | 0.054035 | -0.044736 | 0.0884 | -0.017566 | 0.23069 | 0.064464 | 0.54488 | 0.092626 | -65.4241 | 0.83826 | 51.8433 | 57.5309 | 57.7178 | 57.4967 | -65.8564 | 65.4338 | -57.4018 | 65.2965 | 65.3236 | -0.11019 | -57.568 | -57.0876 | -0.51525 | -0.10156 | -0.08295 | 117.1845 | 117.6998 | 0.085388 | -0.13576 | 65.5719 | 65.4057 | 65.8861 | 65.4296 | -57.5398 | 122.8721 | 123.059 | 122.8379 | 66.1795 | -123.4889
3400.7969 | 122.731 | -64.9704 | 57.6645 | 0.012286 | -0.071033 | 0.023753 | -0.0046134 | -0.0095102 | 0.012719 | 0.0077831 | 0.043947 | 0.047731 | 0.043503 | 0.13543 | 0.054249 | -0.044736 | 0.092979 | -0.008409 | 0.23069 | 0.032411 | 0.54946 | -0.044742 | -65.4196 | 0.852 | 51.8708 | 57.5263 | 57.7224 | 57.5928 | -65.8564 | 64.9257 | -57.4338 | 64.9257 | 64.962 | 0.036333 | -57.6321 | -57.115 | -0.88604 | -0.13818 | -0.44916 | 116.8412 | 117.7272 | 0.057923 | -0.071655 | 65.2011 | 65.0028 | 65.5199 | 65.0634 | -57.7092 | 122.4967 | 122.6928 | 122.5632 | 65.8224 | -123.5209
3401.7969 | 123.2849 | -65.3641 | 57.637 | -0.0029761 | -0.071674 | 0.023753 | -0.004827 | -0.0095102 | 0.013147 | 0.0077831 | 0.044161 | 0.047731 | 0.043076 | 0.13543 | 0.054249 | -0.040158 | 0.092979 | -0.012988 | 0.23526 | 0.15604 | 0.54488 | -0.044742 | -65.4196 | 0.852 | 51.7426 | 57.5355 | 57.727 | 57.6524 | -65.861 | 65.3193 | -57.4018 | 65.3239 | 65.3511 | 0.031754 | -57.481 | -57.0921 | -0.49694 | -0.10156 | -0.055484 | 117.1067 | 117.6036 | 0.089967 | 0.015332 | 65.5993 | 65.5201 | 65.909 | 65.4571 | -57.6818 | 122.8995 | 123.0911 | 123.0164 | 66.2161 | -123.498
3402.7969 | 123.056 | -65.2771 | 57.6462 | -0.0029761 | -0.071461 | 0.023325 | -0.004827 | -0.0099374 | 0.012719 | 0.00015261 | 0.043947 | 0.047945 | 0.043503 | 0.13543 | 0.054035 | -0.044736 | 0.0884 | -0.017566 | 0.24442 | 0.23846 | 0.5403 | -0.063057 | -65.4333 | 0.85658 | 51.6373 | 57.5309 | 57.727 | 57.6661 | -65.861 | 65.214 | -57.4018 | 65.2324 | 65.2595 | 0.045491 | -57.4077 | -57.1059 | -0.58392 | -0.11529 | -0.15619 | 116.9144 | 117.4983 | 0.080812 | 0.019913 | 65.5215 | 65.5156 | 65.8174 | 65.3655 | -57.7092 | 122.808 | 123.0041 | 122.9432 | 66.1337 | -123.5072
3403.7969 | 123.2025 | -65.3687 | 57.6279 | 0.0046549 | -0.071674 | 0.023112 | -0.0050408 | -0.0097238 | 0.012506 | -0.0074779 | 0.044588 | 0.047945 | 0.043503 | 0.13543 | 0.054035 | -0.049315 | 0.092979 | -0.003831 | 0.25358 | 0.25678 | 0.54488 | -0.067636 | -65.4287 | 0.86574 | 51.6693 | 57.5263 | 57.727 | 57.6661 | -65.8564 | 65.301 | -57.3743 | 65.3193 | 65.3648 | 0.063805 | -57.3711 | -57.083 | -0.48779 | -0.10156 | -0.060064 | 117.038 | 117.5258 | 0.099122 | 0.038223 | 65.6222 | 65.6254 | 65.9135 | 65.4616 | -57.6955 | 122.895 | 123.0956 | 123.0347 | 66.2344 | -123.4843
3404.7969 | 123.0103 | -65.2954 | 57.6874 | 0.019917 | -0.072102 | 0.023112 | -0.0050408 | -0.010151 | 0.012078 | 0.0077831 | 0.044802 | 0.047731 | 0.043289 | 0.13543 | 0.054249 | -0.040158 | 0.10214 | -0.003831 | 0.25358 | 0.27509 | 0.54946 | -0.081373 | -65.4379 | 0.87489 | 51.7655 | 57.54 | 57.7224 | 57.6752 | -65.8564 | 65.214 | -57.4338 | 65.2553 | 65.2916 | 0.077542 | -57.4123 | -57.1379 | -0.56103 | -0.14733 | -0.14246 | 117.0609 | 117.6219 | 0.035035 | -0.012129 | 65.549 | 65.5705 | 65.8449 | 65.3975 | -57.7688 | 122.8355 | 123.0178 | 122.9707 | 66.1703 | -123.5438
3405.7969 | 123.2895 | -65.3778 | 57.6553 | -0.010607 | -0.072102 | 0.023753 | -0.0050408 | -0.0097238 | 0.012078 | -0.0074779 | 0.044588 | 0.047945 | 0.043289 | 0.13543 | 0.054676 | -0.040158 | 0.092979 | -0.008409 | 0.249 | 0.19267 | 0.54946 | -0.081373 | -65.4425 | 0.87489 | 51.8067 | 57.5172 | 57.7178 | 57.6478 | -65.8519 | 65.2964 | -57.4063 | 65.3376 | 65.3694 | 0.072964 | -57.4627 | -57.1059 | -0.47405 | -0.13818 | -0.064644 | 117.1845 | 117.6586 | 0.0625 | -0.007556 | 65.6268 | 65.5705 | 65.9273 | 65.4708 | -57.7367 | 122.895 | 123.0956 | 123.0256 | 66.2527 | -123.5072
3406.7969 | 123.0148 | -65.3778 | 57.5592 | 0.0046549 | -0.072316 | 0.023325 | -0.004827 | -0.010151 | 0.012078 | 0.015414 | 0.044588 | 0.048158 | 0.043076 | 0.13543 | 0.055103 | -0.040158 | 0.097557 | -0.003831 | 0.25816 | 0.15604 | 0.54946 | -0.085952 | -65.447 | 0.87947 | 51.8387 | 57.5309 | 57.7224 | 57.6249 | -65.861 | 65.2919 | -57.301 | 65.3376 | 65.374 | 0.082121 | -57.4032 | -57.0097 | -0.48321 | -0.028317 | -0.069223 | 117.2166 | 117.6998 | 0.16321 | 0.065681 | 65.636 | 65.5339 | 65.9273 | 65.4754 | -57.6452 | 122.9087 | 123.1002 | 123.0027 | 66.2573 | -123.4202
3407.7969 | 123.1979 | -65.3549 | 57.6324 | -0.0029761 | -0.072529 | 0.023539 | -0.0043998 | -0.010151 | 0.011865 | 0.00015261 | 0.044802 | 0.048158 | 0.043503 | 0.13543 | 0.05489 | -0.03558 | 0.092979 | 0.000747 | 0.21695 | 0.12399 | 0.55404 | -0.081373 | -65.4562 | 0.88405 | 51.7426 | 57.5309 | 57.7178 | 57.4967 | -65.8564 | 65.2735 | -57.4155 | 65.3193 | 65.3557 | 0.08212 | -57.5085 | -57.0784 | -0.50152 | -0.10156 | -0.10127 | 117.0975 | 117.599 | 0.085388 | -0.13576 | 65.5719 | 65.4789 | 65.909 | 65.4479 | -57.7138 | 122.8858 | 123.0728 | 122.8516 | 66.239 | -123.4889
3408.7969 | 123.0194 | -65.4236 | 57.6828 | -0.0029761 | -0.071888 | 0.022898 | -0.0043998 | -0.0099374 | 0.012719 | 0.015414 | 0.044161 | 0.047731 | 0.043076 | 0.13521 | 0.054249 | -0.040158 | 0.092979 | -0.012988 | 0.20321 | 0.12857 | 0.54488 | -0.090531 | -65.4516 | 0.90236 | 51.8067 | 57.5355 | 57.7224 | 57.5242 | -65.8564 | 65.3331 | -57.4796 | 65.3834 | 65.4106 | 0.077543 | -57.5542 | -57.1379 | -0.43285 | -0.14733 | -0.028026 | 117.2303 | 117.6631 | 0.039613 | -0.15864 | 65.6268 | 65.5522 | 65.9685 | 65.5166 | -57.7733 | 122.9591 | 123.146 | 122.9477 | 66.3259 | -123.5392
3409.7969 | 123.1476 | -65.4099 | 57.6508 | -0.0029761 | -0.071461 | 0.023325 | -0.004827 | -0.0095102 | 0.012933 | 0.00015261 | 0.044161 | 0.047518 | 0.043289 | 0.13479 | 0.054462 | -0.040158 | 0.0884 | -0.008409 | 0.20321 | 0.11483 | 0.5403 | -0.081373 | -65.415 | 0.84742 | 51.7609 | 57.5309 | 57.727 | 57.4829 | -65.861 | 65.3285 | -57.4475 | 65.3697 | 65.4014 | 0.072964 | -57.5359 | -57.1105 | -0.45117 | -0.11987 | -0.005129 | 117.1708 | 117.6219 | 0.076234 | -0.16781 | 65.6131 | 65.5247 | 65.9502 | 65.4983 | -57.7321 | 122.9407 | 123.1368 | 122.8928 | 66.2573 | -123.5118
3410.7969 | 123.0881 | -65.4053 | 57.6736 | -0.0029761 | -0.071674 | 0.023325 | -0.004186 | -0.0095102 | 0.012719 | -0.0074779 | 0.043947 | 0.047731 | 0.043076 | 0.13457 | 0.054462 | -0.049315 | 0.097557 | -0.003831 | 0.17574 | 0.12857 | 0.54488 | -0.090531 | -65.4058 | 0.84742 | 51.5594 | 57.5263 | 57.7224 | 57.515 | -65.8564 | 65.3147 | -57.4979 | 65.356 | 65.4014 | 0.0867 | -57.5451 | -57.1288 | -0.45117 | -0.14734 | -0.00055 | 116.9647 | 117.4159 | 0.048768 | -0.15865 | 65.581 | 65.5338 | 65.9502 | 65.5028 | -57.7642 | 122.9316 | 123.1277 | 122.9203 | 66.2527 | -123.5301
3411.7969 | 123.1705 | -65.4373 | 57.6736 | 0.012286 | -0.071247 | 0.022684 | -0.004827 | -0.0099374 | 0.012933 | 0.015414 | 0.043947 | 0.047731 | 0.043503 | 0.13479 | 0.054249 | -0.040158 | 0.0884 | -0.008409 | 0.19406 | 0.13773 | 0.54488 | -0.099689 | -65.415 | 0.84742 | 51.5732 | 57.5309 | 57.727 | 57.5287 | -65.8564 | 65.3376 | -57.4796 | 65.3972 | 65.4289 | 0.09128 | -57.5359 | -57.1288 | -0.41912 | -0.14276 | 0.022337 | 117.0105 | 117.4296 | 0.053346 | -0.14491 | 65.6314 | 65.575 | 65.9822 | 65.5257 | -57.7733 | 122.9682 | 123.1643 | 122.9661 | 66.2847 | -123.5301
3412.7969 | 122.9095 | -65.4465 | 57.5455 | -0.0029761 | -0.071461 | 0.023112 | -0.0046134 | -0.0097238 | 0.012506 | 0.00015261 | 0.044161 | 0.047518 | 0.043076 | 0.13457 | 0.054462 | -0.040158 | 0.0884 | -0.008409 | 0.19864 | 0.14231 | 0.5403 | -0.09511 | -65.415 | 0.86116 | 51.5778 | 57.5309 | 57.7224 | 57.5287 | -65.8564 | 65.3514 | -57.3468 | 65.4063 | 65.4381 | 0.086701 | -57.4032 | -57.0052 | -0.40997 | -0.014584 | 0.031492 | 117.0242 | 117.4342 | 0.17694 | -0.016737 | 65.6451 | 65.5888 | 65.9868 | 65.5349 | -57.6406 | 122.9774 | 123.1689 | 122.9752 | 66.3076 | -123.4019
3413.7969 | 123.1613 | -65.4236 | 57.6599 | -0.0029761 | -0.071674 | 0.022898 | -0.0046134 | -0.0097238 | 0.012292 | 0.0077831 | 0.044161 | 0.048158 | 0.043289 | 0.13479 | 0.054462 | -0.044736 | 0.092979 | -0.003831 | 0.19406 | 0.13315 | 0.5403 | -0.099689 | -65.4287 | 0.87489 | 51.6327 | 57.5263 | 57.7224 | 57.5562 | -65.861 | 65.3239 | -57.4659 | 65.3788 | 65.4198 | 0.095858 | -57.5268 | -57.1196 | -0.43743 | -0.1336 | -0.005132 | 117.0563 | 117.4937 | 0.062501 | -0.10371 | 65.6176 | 65.5567 | 65.9639 | 65.5166 | -57.7596 | 122.9499 | 123.146 | 122.9798 | 66.2985 | -123.5209
3414.7969 | 123.0148 | -65.4327 | 57.637 | -0.0029761 | -0.072102 | 0.022898 | -0.0043998 | -0.0097238 | 0.012292 | 0.00015261 | 0.044375 | 0.047945 | 0.043289 | 0.135 | 0.054249 | -0.040158 | 0.092979 | -0.012988 | 0.20321 | 0.11941 | 0.54488 | -0.10885 | -65.4333 | 0.87031 | 51.5732 | 57.5355 | 57.727 | 57.547 | -65.861 | 65.3239 | -57.4338 | 65.3926 | 65.4198 | 0.095859 | -57.5176 | -57.0921 | -0.42828 | -0.10156 | -0.000556 | 117.0059 | 117.4342 | 0.089967 | -0.089976 | 65.636 | 65.5521 | 65.9776 | 65.5257 | -57.7459 | 122.9682 | 123.1597 | 122.9798 | 66.3031 | -123.498
3415.7969 | 123.1293 | -65.4465 | 57.6874 | -0.010607 | -0.072316 | 0.023539 | -0.004827 | -0.010151 | 0.012506 | 0.0077831 | 0.044375 | 0.047945 | 0.042862 | 0.13521 | 0.054462 | -0.049315 | 0.097557 | -0.012988 | 0.15743 | 0.11941 | 0.54488 | -0.118 | -65.4379 | 0.88405 | 51.6235 | 57.5263 | 57.7316 | 57.5379 | -65.8564 | 65.3285 | -57.5299 | 65.3972 | 65.4335 | 0.10502 | -57.568 | -57.1425 | -0.40997 | -0.16107 | 0.008598 | 117.07 | 117.48 | 0.044192 | -0.14949 | 65.6039 | 65.5659 | 65.9914 | 65.544 | -57.8054 | 122.9728 | 123.178 | 122.9844 | 66.3305 | -123.5438
3416.8594 | 123.1522 | -65.4282 | 57.6599 | 0.0046549 | -0.072102 | 0.023112 | -0.0043998 | -0.0099374 | 0.012078 | -0.0074779 | 0.044161 | 0.047731 | 0.043076 | 0.13479 | 0.054249 | -0.03558 | 0.092979 | -0.008409 | 0.19406 | 0.11025 | 0.53573 | -0.12258 | -65.4333 | 0.88405 | 51.5823 | 57.5263 | 57.7224 | 57.547 | -65.8564 | 65.3056 | -57.4659 | 65.3926 | 65.4198 | 0.11417 | -57.5497 | -57.1242 | -0.42828 | -0.1336 | -0.005133 | 117.0105 | 117.4388 | 0.062501 | -0.11286 | 65.6222 | 65.5384 | 65.9639 | 65.5211 | -57.7825 | 122.9545 | 123.1506 | 122.9752 | 66.3122 | -123.5164
3417.7969 | 123.1705 | -65.4282 | 57.6599 | 0.0046549 | -0.072102 | 0.023112 | -0.0050408 | -0.0097238 | 0.012506 | 0.00015261 | 0.044375 | 0.047731 | 0.043076 | 0.13457 | 0.05489 | -0.03558 | 0.0884 | -0.008409 | 0.17117 | 0.11941 | 0.54946 | -0.13174 | -65.4287 | 0.87031 | 51.2939 | 57.5263 | 57.727 | 57.5516 | -65.8564 | 65.2964 | -57.4887 | 65.3926 | 65.4198 | 0.12333 | -57.5405 | -57.1105 | -0.42828 | -0.1336 | -0.000554 | 116.722 | 117.1503 | 0.067079 | -0.10828 | 65.5993 | 65.5476 | 65.9776 | 65.5166 | -57.7917 | 122.9545 | 123.1552 | 122.9798 | 66.2985 | -123.5164
3418.7969 | 122.9874 | -65.4236 | 57.6736 | -0.018238 | -0.071888 | 0.023112 | -0.004827 | -0.0099374 | 0.012292 | 0.015414 | 0.044161 | 0.047731 | 0.042862 | 0.13457 | 0.054462 | -0.049315 | 0.0884 | -0.003831 | 0.19406 | 0.11483 | 0.53573 | -0.12258 | -65.4287 | 0.86574 | 51.39 | 57.5355 | 57.7316 | 57.5562 | -65.861 | 65.301 | -57.4796 | 65.3743 | 65.4198 | 0.11875 | -57.5588 | -57.1379 | -0.43743 | -0.13818 | -0.005132 | 116.8136 | 117.2511 | 0.057925 | -0.11744 | 65.6176 | 65.5384 | 65.9593 | 65.512 | -57.7962 | 122.9591 | 123.1552 | 122.9798 | 66.2893 | -123.5347
3419.7969 | 123.056 | -65.4144 | 57.6508 | 0.0046549 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012506 | -0.0074779 | 0.044161 | 0.047518 | 0.042862 | 0.13457 | 0.054462 | -0.040158 | 0.092979 | -0.008409 | 0.20779 | 0.12857 | 0.54488 | -0.118 | -65.4241 | 0.86116 | 51.4679 | 57.54 | 57.727 | 57.5516 | -65.8519 | 65.2964 | -57.443 | 65.3743 | 65.406 | 0.10959 | -57.5222 | -57.1059 | -0.43743 | -0.11071 | -0.009708 | 116.8823 | 117.3197 | 0.076234 | -0.09913 | 65.6222 | 65.543 | 65.9593 | 65.5074 | -57.7688 | 122.9545 | 123.1414 | 122.9661 | 66.2756 | -123.5026
3420.7969 | 122.937 | -65.4282 | 57.6462 | -0.010607 | -0.071888 | 0.023112 | -0.0050408 | -0.010151 | 0.012719 | 0.0077831 | 0.043947 | 0.047518 | 0.043076 | 0.13436 | 0.054462 | -0.044736 | 0.0884 | -0.003831 | 0.19406 | 0.12857 | 0.54946 | -0.10427 | -65.4287 | 0.86116 | 51.5823 | 57.5263 | 57.727 | 57.5654 | -65.861 | 65.3239 | -57.4521 | 65.3834 | 65.4243 | 0.10044 | -57.5176 | -57.0967 | -0.43286 | -0.11987 | -0.000554 | 117.0105 | 117.4434 | 0.080812 | -0.080816 | 65.6222 | 65.5567 | 65.9776 | 65.5166 | -57.7504 | 122.9545 | 123.1552 | 122.9935 | 66.2893 | -123.5072
3421.7969 | 123.1567 | -65.4282 | 57.6874 | 0.0046549 | -0.071888 | 0.023112 | -0.004827 | -0.0095102 | 0.012506 | -0.015108 | 0.043947 | 0.047304 | 0.043076 | 0.13393 | 0.054035 | -0.044736 | 0.092979 | -0.003831 | 0.19406 | 0.11941 | 0.54488 | -0.118 | -65.4196 | 0.86116 | 51.216 | 57.5309 | 57.727 | 57.5562 | -65.8519 | 65.3102 | -57.4933 | 65.3834 | 65.4243 | 0.11417 | -57.568 | -57.1425 | -0.4237 | -0.15649 | 0.008603 | 116.6442 | 117.0679 | 0.039613 | -0.13117 | 65.6222 | 65.5476 | 65.973 | 65.5211 | -57.8054 | 122.959 | 123.1552 | 122.9844 | 66.2893 | -123.5392
3422.7969 | 123.1247 | -65.419 | 57.6599 | 0.0046549 | -0.071674 | 0.023325 | -0.004827 | -0.0099374 | 0.012506 | -0.0074779 | 0.04352 | 0.047304 | 0.043076 | 0.13436 | 0.054676 | -0.044736 | 0.092979 | -0.008409 | 0.20321 | 0.12857 | 0.53573 | -0.12258 | -65.4104 | 0.86574 | 51.0421 | 57.5355 | 57.7361 | 57.5654 | -65.8519 | 65.2964 | -57.4567 | 65.3743 | 65.4106 | 0.11417 | -57.5313 | -57.1242 | -0.43285 | -0.12445 | 0.008605 | 116.4611 | 116.8939 | 0.076236 | -0.094549 | 65.6222 | 65.5476 | 65.9547 | 65.512 | -57.7825 | 122.9545 | 123.1552 | 122.9844 | 66.2847 | -123.5118
3423.7969 | 123.0972 | -65.4373 | 57.6416 | -0.010607 | -0.071674 | 0.023112 | -0.0050408 | -0.0095102 | 0.013147 | 0.00015261 | 0.043734 | 0.047518 | 0.042862 | 0.13351 | 0.054462 | -0.044736 | 0.097557 | -0.008409 | 0.19406 | 0.12399 | 0.53115 | -0.118 | -65.4058 | 0.86574 | 50.6986 | 57.5355 | 57.7361 | 57.5654 | -65.8519 | 65.3193 | -57.4475 | 65.3926 | 65.4289 | 0.10959 | -57.5176 | -57.1105 | -0.41454 | -0.10614 | 0.031494 | 116.136 | 116.5505 | 0.094546 | -0.076239 | 65.6314 | 65.5613 | 65.9685 | 65.5349 | -57.7596 | 122.9728 | 123.1735 | 123.0027 | 66.3031 | -123.4935
3424.7969 | 123.0927 | -65.4236 | 57.6462 | -0.0029761 | -0.071461 | 0.023112 | -0.004827 | -0.0099374 | 0.012933 | 0.00015261 | 0.043093 | 0.04709 | 0.042435 | 0.13351 | 0.054249 | -0.049315 | 0.092979 | -0.008409 | 0.20321 | 0.11941 | 0.53573 | -0.12258 | -65.4104 | 0.86116 | 50.2682 | 57.54 | 57.7407 | 57.5608 | -65.8427 | 65.301 | -57.443 | 65.3743 | 65.4152 | 0.11417 | -57.5268 | -57.1105 | -0.41912 | -0.10613 | 0.013183 | 115.6918 | 116.111 | 0.094548 | -0.085395 | 65.6268 | 65.543 | 65.9593 | 65.5166 | -57.7688 | 122.9636 | 123.1643 | 122.9844 | 66.2847 | -123.4889
3425.7969 | 123.1934 | -65.3915 | 57.6599 | -0.010607 | -0.071674 | 0.023112 | -0.0050408 | -0.0095102 | 0.012719 | 0.0077831 | 0.04352 | 0.04709 | 0.043076 | 0.13372 | 0.054462 | -0.044736 | 0.10214 | 0.000747 | 0.19864 | 0.12857 | 0.54488 | -0.12258 | -65.4058 | 0.87031 | 50.8406 | 57.5355 | 57.7361 | 57.547 | -65.8519 | 65.269 | -57.4613 | 65.3468 | 65.3923 | 0.12333 | -57.5313 | -57.115 | -0.46032 | -0.12445 | -0.014282 | 116.2321 | 116.6924 | 0.076236 | -0.11286 | 65.5902 | 65.5201 | 65.9364 | 65.4937 | -57.7825 | 122.927 | 123.1277 | 122.9386 | 66.2619 | -123.5118
3426.7969 | 123.1659 | -65.4419 | 57.6233 | -0.0029761 | -0.071888 | 0.023112 | -0.0050408 | -0.0099374 | 0.012933 | 0.0077831 | 0.044161 | 0.047304 | 0.043289 | 0.13457 | 0.054249 | -0.044736 | 0.092979 | -0.003831 | 0.1849 | 0.12399 | 0.53573 | -0.12716 | -65.4196 | 0.88863 | 52.0082 | 57.5263 | 57.7316 | 57.5242 | -65.8656 | 65.3147 | -57.4384 | 65.3972 | 65.4381 | 0.12333 | -57.4993 | -57.0876 | -0.4237 | -0.096982 | 0.022336 | 117.4501 | 117.8738 | 0.10828 | -0.099136 | 65.6268 | 65.5659 | 65.9776 | 65.5349 | -57.7505 | 122.9682 | 123.1735 | 122.966 | 66.3305 | -123.4889
3427.7969 | 123.1613 | -65.4419 | 57.637 | -0.0029761 | -0.071461 | 0.022898 | -0.0050408 | -0.0099374 | 0.012506 | 0.00015261 | 0.044375 | 0.047731 | 0.043076 | 0.13521 | 0.054249 | -0.040158 | 0.0884 | -0.003831 | 0.19864 | 0.12399 | 0.54946 | -0.13632 | -65.4287 | 0.90236 | 53.0109 | 57.5172 | 57.7224 | 57.5242 | -65.8702 | 65.3056 | -57.4384 | 65.4017 | 65.4381 | 0.13249 | -57.513 | -57.0876 | -0.42828 | -0.11987 | 0.013179 | 118.4528 | 118.8811 | 0.085389 | -0.11287 | 65.6405 | 65.5659 | 65.9914 | 65.5303 | -57.7733 | 122.959 | 123.1643 | 122.966 | 66.3443 | -123.5072
3428.7969 | 123.1476 | -65.4648 | 57.6508 | -0.018238 | -0.071674 | 0.023325 | -0.0052544 | -0.0097238 | 0.01336 | -0.0074779 | 0.044375 | 0.047731 | 0.043076 | 0.13521 | 0.054462 | -0.031001 | 0.092979 | -0.008409 | 0.18948 | 0.12857 | 0.5403 | -0.118 | -65.4241 | 0.90236 | 52.9331 | 57.5263 | 57.7178 | 57.5287 | -65.8656 | 65.3468 | -57.4613 | 65.4338 | 65.4564 | 0.10959 | -57.5222 | -57.1105 | -0.40081 | -0.12445 | 0.040646 | 118.3978 | 118.7987 | 0.067077 | -0.12202 | 65.6543 | 65.5934 | 66.0051 | 65.5578 | -57.7688 | 122.9911 | 123.1826 | 122.9935 | 66.3671 | -123.5164
3429.7969 | 123.2025 | -65.4419 | 57.6233 | -0.0029761 | -0.071247 | 0.022898 | -0.0052544 | -0.0099374 | 0.013147 | 0.0077831 | 0.043947 | 0.047945 | 0.043289 | 0.13479 | 0.054249 | -0.049315 | 0.0884 | -0.008409 | 0.19406 | 0.13315 | 0.53573 | -0.12258 | -65.4241 | 0.90694 | 52.8781 | 57.5172 | 57.7133 | 57.5333 | -65.8702 | 65.3193 | -57.4292 | 65.3926 | 65.4335 | 0.11417 | -57.4901 | -57.0876 | -0.42828 | -0.10614 | 0.017758 | 118.32 | 118.7483 | 0.089964 | -0.089978 | 65.636 | 65.575 | 65.9776 | 65.5303 | -57.7459 | 122.959 | 123.1551 | 122.9752 | 66.3488 | -123.4935
3430.7969 | 123.143 | -65.4556 | 57.6279 | -0.010607 | -0.071674 | 0.023112 | -0.0050408 | -0.0097238 | 0.012719 | 0.00015261 | 0.043947 | 0.047518 | 0.043076 | 0.135 | 0.054462 | -0.03558 | 0.097557 | -0.008409 | 0.19406 | 0.12399 | 0.53573 | -0.12716 | -65.4241 | 0.90694 | 52.8827 | 57.5309 | 57.7224 | 57.5242 | -65.8656 | 65.3285 | -57.4338 | 65.42 | 65.4472 | 0.11875 | -57.5039 | -57.0921 | -0.40997 | -0.096982 | 0.03149 | 118.3383 | 118.7483 | 0.094544 | -0.10371 | 65.6497 | 65.5796 | 65.9914 | 65.5532 | -57.755 | 122.9865 | 123.178 | 122.9798 | 66.3626 | -123.4935
3431.7969 | 123.1384 | -65.4694 | 57.6187 | -0.010607 | -0.071461 | 0.02247 | -0.0052544 | -0.0099374 | 0.012933 | 0.00015261 | 0.043734 | 0.047518 | 0.043289 | 0.13479 | 0.054249 | -0.049315 | 0.097557 | -0.008409 | 0.1849 | 0.13315 | 0.5403 | -0.12258 | -65.4104 | 0.90694 | 52.8598 | 57.5263 | 57.7178 | 57.5608 | -65.8702 | 65.3468 | -57.4338 | 65.42 | 65.461 | 0.11417 | -57.4856 | -57.0784 | -0.40082 | -0.092404 | 0.058959 | 118.3292 | 118.73 | 0.099121 | -0.057929 | 65.6543 | 65.6025 | 66.0097 | 65.5669 | -57.7413 | 122.9957 | 123.1872 | 123.0301 | 66.3763 | -123.4889
3432.8594 | 123.1796 | -65.4282 | 57.6782 | -0.010607 | -0.071674 | 0.023112 | -0.0050408 | -0.0099374 | 0.01336 | 0.0077831 | 0.043947 | 0.047304 | 0.043289 | 0.13521 | 0.054676 | -0.044736 | 0.092979 | -0.003831 | 0.19406 | 0.12399 | 0.53573 | -0.13174 | -65.4196 | 0.91152 | 52.7774 | 57.5217 | 57.7133 | 57.547 | -65.8656 | 65.2964 | -57.4842 | 65.3834 | 65.4243 | 0.12791 | -57.5542 | -57.1425 | -0.43743 | -0.15649 | 0.008603 | 118.2055 | 118.643 | 0.035032 | -0.13118 | 65.6222 | 65.5522 | 65.9639 | 65.5211 | -57.81 | 122.9499 | 123.1414 | 122.9752 | 66.3397 | -123.5438
3433.7969 | 123.1476 | -65.4602 | 57.6187 | -0.010607 | -0.071247 | 0.023112 | -0.0050408 | -0.0097238 | 0.012933 | 0.00015261 | 0.043947 | 0.047518 | 0.043076 | 0.135 | 0.054462 | -0.049315 | 0.092979 | -0.003831 | 0.1849 | 0.13315 | 0.53115 | -0.12258 | -65.4196 | 0.9161 | 52.9147 | 57.5172 | 57.7178 | 57.547 | -65.8656 | 65.3376 | -57.4338 | 65.4109 | 65.4564 | 0.11875 | -57.4856 | -57.0876 | -0.40539 | -0.10156 | 0.040646 | 118.3749 | 118.7803 | 0.099121 | -0.071665 | 65.6451 | 65.5934 | 65.9914 | 65.5532 | -57.7413 | 122.9774 | 123.178 | 123.0073 | 66.3763 | -123.4843
3434.7969 | 123.2071 | -65.4465 | 57.6141 | -0.010607 | -0.071461 | 0.022684 | -0.0052544 | -0.0095102 | 0.013147 | -0.0074779 | 0.044161 | 0.047518 | 0.043289 | 0.135 | 0.054035 | -0.044736 | 0.0884 | -0.008409 | 0.19864 | 0.12399 | 0.53573 | -0.10885 | -65.415 | 0.9161 | 52.8232 | 57.5217 | 57.7133 | 57.5287 | -65.861 | 65.3376 | -57.4155 | 65.4017 | 65.4381 | 0.10044 | -57.4901 | -57.0784 | -0.41455 | -0.092406 | 0.031492 | 118.2696 | 118.6842 | 0.099119 | -0.085402 | 65.6451 | 65.5705 | 65.9822 | 65.5349 | -57.723 | 122.9682 | 123.1597 | 122.9752 | 66.3626 | -123.4752
3435.7969 | 123.1522 | -65.4694 | 57.637 | -0.0029761 | -0.071461 | 0.023112 | -0.0050408 | -0.0099374 | 0.012506 | 0.0077831 | 0.044161 | 0.047304 | 0.043076 | 0.135 | 0.054249 | -0.040158 | 0.097557 | 0.000747 | 0.19864 | 0.13773 | 0.53573 | -0.12258 | -65.4287 | 0.92068 | 52.8369 | 57.5263 | 57.727 | 57.5516 | -65.8656 | 65.3468 | -57.4384 | 65.4292 | 65.4701 | 0.12333 | -57.4993 | -57.1013 | -0.39624 | -0.11071 | 0.040644 | 118.3063 | 118.7025 | 0.089967 | -0.085397 | 65.668 | 65.6071 | 66.0051 | 65.5669 | -57.7596 | 122.9957 | 123.1964 | 123.021 | 66.39 | -123.5026
3436.7969 | 123.1705 | -65.4648 | 57.6279 | -0.010607 | -0.071888 | 0.022684 | -0.004827 | -0.0097238 | 0.012719 | 0.00015261 | 0.044161 | 0.047304 | 0.043076 | 0.13521 | 0.054249 | -0.053893 | 0.0884 | 0.005325 | 0.18948 | 0.12399 | 0.53115 | -0.118 | -65.4287 | 0.92526 | 52.7774 | 57.5172 | 57.7178 | 57.5379 | -65.8656 | 65.3468 | -57.4384 | 65.4109 | 65.4701 | 0.12333 | -57.5039 | -57.0967 | -0.40081 | -0.11072 | 0.036067 | 118.2422 | 118.643 | 0.089965 | -0.089978 | 65.6543 | 65.5888 | 65.9959 | 65.5532 | -57.7459 | 122.9819 | 123.1826 | 123.0027 | 66.39 | -123.4935
3437.7969 | 123.1293 | -65.4694 | 57.6599 | -0.010607 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012719 | -0.0074779 | 0.044161 | 0.047518 | 0.043076 | 0.13457 | 0.054676 | -0.044736 | 0.0884 | -0.003831 | 0.19864 | 0.11483 | 0.53573 | -0.11342 | -65.4196 | 0.92068 | 52.7133 | 57.5263 | 57.7224 | 57.5379 | -65.8656 | 65.3559 | -57.4613 | 65.4246 | 65.4655 | 0.10959 | -57.5451 | -57.1242 | -0.39624 | -0.1336 | 0.049801 | 118.1826 | 118.5789 | 0.062501 | -0.12202 | 65.668 | 65.5842 | 66.0051 | 65.5578 | -57.7733 | 122.9957 | 123.1918 | 123.0073 | 66.39 | -123.5255
3438.7969 | 123.2117 | -65.4419 | 57.6141 | -0.0029761 | -0.071888 | 0.022898 | -0.004827 | -0.0097238 | 0.012933 | -0.0074779 | 0.044375 | 0.047304 | 0.043076 | 0.13457 | 0.054462 | -0.044736 | 0.083821 | -0.003831 | 0.19406 | 0.13315 | 0.53573 | -0.11342 | -65.4196 | 0.92068 | 52.7453 | 57.5263 | 57.7224 | 57.5699 | -65.8656 | 65.3285 | -57.4201 | 65.3972 | 65.4381 | 0.10959 | -57.481 | -57.0784 | -0.4237 | -0.087827 | 0.022336 | 118.1872 | 118.6109 | 0.10828 | -0.044194 | 65.636 | 65.575 | 65.9776 | 65.5257 | -57.7276 | 122.9682 | 123.1643 | 123.0118 | 66.3626 | -123.4797
3439.7969 | 123.1476 | -65.4648 | 57.6187 | -0.0029761 | -0.072102 | 0.022684 | -0.004827 | -0.0099374 | 0.012719 | 0.00015261 | 0.044375 | 0.047304 | 0.043076 | 0.13479 | 0.054676 | -0.044736 | 0.092979 | -0.008409 | 0.18948 | 0.12857 | 0.53573 | -0.118 | -65.4379 | 0.92526 | 52.8323 | 57.5126 | 57.7224 | 57.5425 | -65.8656 | 65.3468 | -57.4292 | 65.42 | 65.4564 | 0.10959 | -57.4901 | -57.083 | -0.40081 | -0.10614 | 0.026909 | 118.2971 | 118.6979 | 0.1037 | -0.076243 | 65.6543 | 65.5934 | 66.0005 | 65.5578 | -57.7367 | 122.9774 | 123.1872 | 123.0073 | 66.39 | -123.4843
3440.7969 | 123.2803 | -65.4144 | 57.605 | -0.0029761 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012506 | -0.0074779 | 0.043947 | 0.047731 | 0.042862 | 0.135 | 0.054035 | -0.040158 | 0.092979 | -0.003831 | 0.16659 | 0.11483 | 0.53573 | -0.10885 | -65.4425 | 0.92526 | 52.869 | 57.5217 | 57.7224 | 57.5287 | -65.8702 | 65.3056 | -57.4384 | 65.3743 | 65.4106 | 0.10502 | -57.4901 | -57.0693 | -0.45575 | -0.08325 | -0.028023 | 118.2834 | 118.7391 | 0.11743 | -0.076246 | 65.581 | 65.5293 | 65.9502 | 65.5074 | -57.7138 | 122.9362 | 123.1368 | 122.9432 | 66.3397 | -123.4752
3441.7969 | 123.2254 | -65.4099 | 57.5958 | -0.0029761 | -0.072102 | 0.022898 | -0.004827 | -0.0099374 | 0.012506 | 0.00015261 | 0.044588 | 0.047304 | 0.043289 | 0.13457 | 0.054249 | -0.049315 | 0.092979 | -0.012988 | 0.19406 | 0.11483 | 0.53115 | -0.11342 | -65.4287 | 0.92526 | 52.8415 | 57.5217 | 57.7178 | 57.5333 | -65.8748 | 65.2964 | -57.4018 | 65.3605 | 65.3969 | 0.10044 | -57.481 | -57.0647 | -0.4649 | -0.074095 | -0.018865 | 118.2513 | 118.7162 | 0.12201 | -0.062512 | 65.6039 | 65.5247 | 65.941 | 65.5028 | -57.7092 | 122.9316 | 123.1277 | 122.9432 | 66.3351 | -123.4706
3442.7969 | 123.2346 | -65.4419 | 57.6279 | -0.0029761 | -0.072102 | 0.023112 | -0.0050408 | -0.0092964 | 0.012506 | -0.0074779 | 0.044375 | 0.047731 | 0.042862 | 0.135 | 0.054035 | -0.044736 | 0.083821 | -0.003831 | 0.19406 | 0.11483 | 0.53573 | -0.10885 | -65.447 | 0.93899 | 53.1025 | 57.5126 | 57.7224 | 57.5379 | -65.8748 | 65.333 | -57.4338 | 65.3972 | 65.4381 | 0.10502 | -57.513 | -57.0921 | -0.43286 | -0.1153 | -0.005136 | 118.5444 | 118.9772 | 0.094544 | -0.089978 | 65.636 | 65.5567 | 65.9776 | 65.5257 | -57.7367 | 122.9545 | 123.1643 | 122.9798 | 66.3809 | -123.5026
3443.7969 | 123.143 | -65.4694 | 57.6462 | -0.010607 | -0.072529 | 0.022898 | -0.0054682 | -0.0097238 | 0.012506 | 0.00015261 | 0.044375 | 0.047731 | 0.043289 | 0.13521 | 0.054462 | -0.049315 | 0.0884 | 0.000747 | 0.19406 | 0.11941 | 0.53573 | -0.10427 | -65.4425 | 0.93899 | 53.249 | 57.5263 | 57.7224 | 57.5379 | -65.8748 | 65.3651 | -57.4521 | 65.42 | 65.4701 | 0.10501 | -57.5268 | -57.1105 | -0.40539 | -0.11987 | 0.026908 | 118.7183 | 119.1237 | 0.076234 | -0.10829 | 65.6634 | 65.5888 | 66.0051 | 65.5578 | -57.7504 | 122.9957 | 123.1918 | 123.0073 | 66.4084 | -123.5209
3444.7969 | 123.262 | -65.3961 | 57.605 | -0.010607 | -0.072102 | 0.023112 | -0.004827 | -0.0095102 | 0.012078 | 0.00015261 | 0.043947 | 0.047304 | 0.043076 | 0.13479 | 0.054462 | -0.044736 | 0.0884 | -0.012988 | 0.18032 | 0.12399 | 0.53115 | -0.11342 | -65.447 | 0.93899 | 53.0887 | 57.5217 | 57.7133 | 57.5516 | -65.861 | 65.2827 | -57.4247 | 65.3514 | 65.3831 | 0.10044 | -57.481 | -57.0738 | -0.4649 | -0.08325 | -0.050913 | 118.4849 | 118.9498 | 0.10827 | -0.053353 | 65.5764 | 65.5201 | 65.9273 | 65.4845 | -57.7184 | 122.9178 | 123.1094 | 122.9477 | 66.3351 | -123.466
3445.7969 | 123.1934 | -65.4648 | 57.6233 | -0.0029761 | -0.071888 | 0.022684 | -0.0050408 | -0.0095102 | 0.012506 | -0.0074779 | 0.044588 | 0.047518 | 0.043289 | 0.135 | 0.054462 | -0.040158 | 0.083821 | 0.000747 | 0.19406 | 0.11025 | 0.53573 | -0.118 | -65.4379 | 0.95273 | 53.4779 | 57.5217 | 57.7133 | 57.5425 | -65.8748 | 65.3468 | -57.4292 | 65.4246 | 65.4655 | 0.11875 | -57.513 | -57.0876 | -0.40997 | -0.10156 | 0.026909 | 118.9427 | 119.3527 | 0.089964 | -0.080821 | 65.6588 | 65.575 | 66.0005 | 65.5486 | -57.7413 | 122.9865 | 123.178 | 123.0073 | 66.4175 | -123.498
3446.7969 | 123.2712 | -65.4236 | 57.6004 | -0.010607 | -0.071674 | 0.022684 | -0.0050408 | -0.0095102 | 0.012292 | 0.00015261 | 0.044161 | 0.047518 | 0.043076 | 0.135 | 0.054249 | -0.03558 | 0.092979 | -0.008409 | 0.16659 | 0.11941 | 0.5403 | -0.11342 | -65.4425 | 0.96189 | 53.4505 | 57.5126 | 57.7178 | 57.5379 | -65.8793 | 65.3102 | -57.4338 | 65.388 | 65.4152 | 0.10502 | -57.481 | -57.0601 | -0.45575 | -0.08783 | -0.018868 | 118.874 | 119.3298 | 0.11743 | -0.062512 | 65.5902 | 65.543 | 65.9639 | 65.5166 | -57.7138 | 122.9362 | 123.1414 | 122.9615 | 66.3855 | -123.4797
3447.7969 | 123.1522 | -65.4282 | 57.6508 | -0.0029761 | -0.072102 | 0.023112 | -0.0052544 | -0.0097238 | 0.012506 | 0.0077831 | 0.044375 | 0.04709 | 0.043076 | 0.135 | 0.054249 | -0.044736 | 0.092979 | -0.012988 | 0.18948 | 0.11941 | 0.5403 | -0.10885 | -65.4425 | 0.95731 | 53.4413 | 57.5172 | 57.7133 | 57.5333 | -65.8793 | 65.3193 | -57.4613 | 65.3834 | 65.4152 | 0.095859 | -57.5313 | -57.1105 | -0.45117 | -0.1336 | -0.01429 | 118.8695 | 119.3206 | 0.062498 | -0.11744 | 65.6176 | 65.5476 | 65.9685 | 65.5211 | -57.7596 | 122.9453 | 123.1414 | 122.9615 | 66.3855 | -123.5301
3448.7969 | 123.2208 | -65.4144 | 57.6004 | -0.0029761 | -0.071888 | 0.023112 | -0.0050408 | -0.0097238 | 0.012292 | -0.0074779 | 0.043947 | 0.04709 | 0.043289 | 0.135 | 0.054676 | -0.044736 | 0.083821 | -0.003831 | 0.19406 | 0.11483 | 0.53573 | -0.10885 | -65.4425 | 0.95731 | 53.194 | 57.5172 | 57.7224 | 57.5425 | -65.8793 | 65.3056 | -57.4063 | 65.3697 | 65.4106 | 0.10502 | -57.4856 | -57.0647 | -0.4649 | -0.083251 | -0.028023 | 118.6085 | 119.0734 | 0.12201 | -0.057933 | 65.6085 | 65.5293 | 65.9502 | 65.4982 | -57.7092 | 122.9316 | 123.1368 | 122.9569 | 66.3717 | -123.4797
3449.7969 | 123.2391 | -65.4236 | 57.6187 | -0.0029761 | -0.071674 | 0.023112 | -0.004827 | -0.0095102 | 0.012506 | 0.00015261 | 0.044161 | 0.04709 | 0.043076 | 0.13457 | 0.054462 | -0.031001 | 0.092979 | 0.005325 | 0.19406 | 0.11483 | 0.52657 | -0.10427 | -65.447 | 0.95731 | 53.2307 | 57.5217 | 57.7087 | 57.5608 | -65.8702 | 65.3193 | -57.4247 | 65.3926 | 65.4289 | 0.10959 | -57.5039 | -57.0921 | -0.44659 | -0.096983 | -0.023447 | 118.6543 | 119.1009 | 0.089964 | -0.057929 | 65.6176 | 65.5384 | 65.9502 | 65.5166 | -57.723 | 122.9453 | 123.1323 | 122.9844 | 66.3809 | -123.4889
3450.7969 | 123.2346 | -65.3961 | 57.6004 | -0.0029761 | -0.071888 | 0.023112 | -0.0052544 | -0.0095102 | 0.012933 | -0.0074779 | 0.044375 | 0.047304 | 0.043289 | 0.13479 | 0.054035 | -0.049315 | 0.0884 | 0.000747 | 0.20321 | 0.11025 | 0.53573 | -0.10427 | -65.4425 | 0.95731 | 53.2765 | 57.5172 | 57.7133 | 57.5379 | -65.8793 | 65.2918 | -57.3972 | 65.3468 | 65.3969 | 0.10501 | -57.4901 | -57.0647 | -0.48322 | -0.083251 | -0.046334 | 118.6726 | 119.1558 | 0.11285 | -0.062512 | 65.5993 | 65.5064 | 65.9318 | 65.4845 | -57.7047 | 122.9133 | 123.1094 | 122.934 | 66.3534 | -123.4797
3451.7969 | 123.2346 | -65.4282 | 57.5546 | -0.010607 | -0.071888 | 0.023325 | -0.0052544 | -0.0099374 | 0.012506 | -0.0074779 | 0.044161 | 0.047518 | 0.043076 | 0.13436 | 0.054676 | -0.044736 | 0.092979 | -0.008409 | 0.1849 | 0.11025 | 0.53115 | -0.099689 | -65.447 | 0.95731 | 53.1803 | 57.5217 | 57.7178 | 57.5379 | -65.8702 | 65.3285 | -57.3697 | 65.3834 | 65.4198 | 0.09128 | -57.4444 | -57.0235 | -0.44201 | -0.032896 | -0.018869 | 118.6085 | 119.0505 | 0.16321 | -0.016735 | 65.6131 | 65.5384 | 65.9593 | 65.5211 | -57.6543 | 122.9499 | 123.146 | 122.9661 | 66.3855 | -123.4248
3452.7969 | 123.143 | -65.4419 | 57.6782 | -0.0029761 | -0.071888 | 0.022898 | -0.004827 | -0.0099374 | 0.012292 | 0.00015261 | 0.043734 | 0.047304 | 0.043076 | 0.13479 | 0.054249 | -0.040158 | 0.092979 | -0.012988 | 0.18948 | 0.11025 | 0.53115 | -0.10427 | -65.447 | 0.97562 | 53.1757 | 57.5309 | 57.7178 | 57.5333 | -65.8656 | 65.3376 | -57.4887 | 65.4017 | 65.4289 | 0.09128 | -57.568 | -57.1471 | -0.4237 | -0.14734 | -0.005136 | 118.6176 | 119.0413 | 0.039611 | -0.14491 | 65.6314 | 65.5521 | 65.973 | 65.5349 | -57.7825 | 122.9728 | 123.1597 | 122.9752 | 66.4175 | -123.5438
3453.7969 | 123.2437 | -65.419 | 57.5821 | -0.0029761 | -0.071674 | 0.022684 | -0.004827 | -0.0097238 | 0.012078 | 0.00015261 | 0.043734 | 0.047518 | 0.042862 | 0.13479 | 0.054462 | -0.044736 | 0.083821 | -0.008409 | 0.18032 | 0.11025 | 0.52657 | -0.10427 | -65.4379 | 0.9802 | 53.2673 | 57.5172 | 57.7133 | 57.5425 | -65.8748 | 65.3147 | -57.4018 | 65.3743 | 65.4106 | 0.095859 | -57.4718 | -57.0555 | -0.45575 | -0.06494 | -0.018868 | 118.6863 | 119.1421 | 0.13116 | -0.039622 | 65.5993 | 65.5293 | 65.9456 | 65.5028 | -57.6864 | 122.9362 | 123.1323 | 122.9615 | 66.3992 | -123.4568
3454.7969 | 123.2346 | -65.4099 | 57.6279 | -0.0029761 | -0.071888 | 0.022684 | -0.0050408 | -0.010151 | 0.012719 | 0.00015261 | 0.044161 | 0.047518 | 0.043076 | 0.13479 | 0.054462 | -0.044736 | 0.092979 | -0.008409 | 0.18032 | 0.1011 | 0.53115 | -0.099689 | -65.4425 | 0.9802 | 53.3131 | 57.5263 | 57.7178 | 57.5104 | -65.8702 | 65.3102 | -57.4475 | 65.3651 | 65.4014 | 0.09128 | -57.5268 | -57.0967 | -0.46032 | -0.10156 | -0.032601 | 118.7229 | 119.1833 | 0.089965 | -0.11745 | 65.5902 | 65.5109 | 65.941 | 65.5028 | -57.7276 | 122.9362 | 123.1277 | 122.9203 | 66.3901 | -123.498
3455.7969 | 123.2483 | -65.419 | 57.5958 | -0.010607 | -0.071888 | 0.022684 | -0.0050408 | -0.0097238 | 0.012506 | 0.00015261 | 0.043947 | 0.047518 | 0.043076 | 0.13457 | 0.054249 | -0.044736 | 0.097557 | -0.003831 | 0.18948 | 0.1011 | 0.53115 | -0.10427 | -65.4379 | 0.97562 | 53.2032 | 57.5172 | 57.7224 | 57.5242 | -65.8748 | 65.3147 | -57.4063 | 65.3743 | 65.4152 | 0.10044 | -57.4947 | -57.0647 | -0.45575 | -0.078673 | -0.018868 | 118.6222 | 119.078 | 0.12659 | -0.07167 | 65.6085 | 65.5201 | 65.9502 | 65.5166 | -57.7001 | 122.9362 | 123.1414 | 122.9432 | 66.3946 | -123.4706
3456.7969 | 123.2391 | -65.4373 | 57.6187 | -0.0029761 | -0.072316 | 0.022898 | -0.004827 | -0.0097238 | 0.011865 | -0.0074779 | 0.044375 | 0.047518 | 0.042862 | 0.13479 | 0.054462 | -0.044736 | 0.0884 | -0.008409 | 0.18948 | 0.10567 | 0.53573 | -0.11342 | -65.447 | 0.99852 | 53.4321 | 57.5172 | 57.7133 | 57.547 | -65.8885 | 65.3239 | -57.4292 | 65.3926 | 65.4289 | 0.10502 | -57.513 | -57.083 | -0.45117 | -0.10156 | -0.009714 | 118.8695 | 119.3206 | 0.094542 | -0.071665 | 65.6268 | 65.543 | 65.973 | 65.5257 | -57.7321 | 122.9545 | 123.1506 | 122.9844 | 66.4358 | -123.5072
3457.7969 | 123.1934 | -65.4099 | 57.6462 | 0.0046549 | -0.071674 | 0.023112 | -0.0046134 | -0.0097238 | 0.012506 | -0.0074779 | 0.044588 | 0.047945 | 0.042648 | 0.13457 | 0.054249 | -0.044736 | 0.0884 | 0.000747 | 0.16659 | 0.10567 | 0.53115 | -0.118 | -65.4425 | 1.0031 | 53.3955 | 57.5126 | 57.7133 | 57.5425 | -65.8793 | 65.2918 | -57.4796 | 65.3651 | 65.4106 | 0.11875 | -57.5405 | -57.115 | -0.46948 | -0.13361 | -0.032601 | 118.8054 | 119.2748 | 0.067076 | -0.10371 | 65.5764 | 65.5155 | 65.941 | 65.4983 | -57.7642 | 122.9224 | 123.1231 | 122.9523 | 66.4129 | -123.5255
3458.7969 | 123.2391 | -65.4282 | 57.637 | -0.0029761 | -0.072102 | 0.023112 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.044375 | 0.047731 | 0.042648 | 0.135 | 0.054462 | -0.049315 | 0.0884 | -0.003831 | 0.19406 | 0.10567 | 0.53573 | -0.099689 | -65.4562 | 0.99394 | 53.3543 | 57.5172 | 57.7178 | 57.515 | -65.8702 | 65.3285 | -57.443 | 65.3788 | 65.4243 | 0.095858 | -57.5313 | -57.1013 | -0.44201 | -0.11987 | -0.028026 | 118.7825 | 119.2245 | 0.08081 | -0.12203 | 65.6222 | 65.5338 | 65.9639 | 65.5166 | -57.7367 | 122.9453 | 123.146 | 122.9432 | 66.4221 | -123.5072
3459.7969 | 123.1888 | -65.419 | 57.6187 | 0.0046549 | -0.072102 | 0.023112 | -0.0050408 | -0.0097238 | 0.012078 | 0.00015261 | 0.044375 | 0.047945 | 0.042221 | 0.13457 | 0.054249 | -0.044736 | 0.092979 | -0.012988 | 0.17574 | 0.11941 | 0.53115 | -0.09511 | -65.4516 | 1.0123 | 53.194 | 57.5217 | 57.7178 | 57.5242 | -65.8748 | 65.3239 | -57.443 | 65.3743 | 65.406 | 0.082122 | -57.4993 | -57.0876 | -0.45575 | -0.096983 | -0.032604 | 118.6131 | 119.0688 | 0.099121 | -0.094558 | 65.5947 | 65.5384 | 65.9502 | 65.512 | -57.7138 | 122.9407 | 123.1368 | 122.9432 | 66.4313 | -123.4935
3460.7969 | 123.262 | -65.3915 | 57.605 | -0.0029761 | -0.072316 | 0.023112 | -0.0052544 | -0.0097238 | 0.012078 | 0.015414 | 0.044375 | 0.047731 | 0.042435 | 0.13479 | 0.054462 | -0.044736 | 0.0884 | -0.003831 | 0.18948 | 0.10567 | 0.53573 | -0.09511 | -65.447 | 1.0214 | 53.4459 | 57.5126 | 57.7041 | 57.5287 | -65.8748 | 65.2964 | -57.4155 | 65.3468 | 65.3877 | 0.091279 | -57.4993 | -57.0693 | -0.48321 | -0.092407 | -0.05549 | 118.8374 | 119.3206 | 0.099118 | -0.076246 | 65.581 | 65.4972 | 65.9273 | 65.4799 | -57.7001 | 122.9041 | 123.0956 | 122.9203 | 66.413 | -123.4797
3461.7969 | 123.23 | -65.4419 | 57.5912 | 0.0046549 | -0.072102 | 0.023112 | -0.0052544 | -0.0095102 | 0.012078 | 0.0077831 | 0.044588 | 0.048158 | 0.042435 | 0.13479 | 0.05489 | -0.044736 | 0.097557 | -0.008409 | 0.18032 | 0.1011 | 0.53573 | -0.099689 | -65.4516 | 1.0306 | 53.6153 | 57.5217 | 57.7178 | 57.5287 | -65.8793 | 65.3422 | -57.4109 | 65.3972 | 65.4335 | 0.09128 | -57.4902 | -57.0555 | -0.43744 | -0.069518 | -0.009715 | 119.0572 | 119.4946 | 0.12659 | -0.062514 | 65.6222 | 65.543 | 65.9776 | 65.5395 | -57.6909 | 122.9636 | 123.1597 | 122.9706 | 66.4725 | -123.4706
3462.7969 | 123.1522 | -65.4327 | 57.6691 | -0.0029761 | -0.072102 | 0.023325 | -0.0052544 | -0.0097238 | 0.011651 | 0.015414 | 0.044588 | 0.047945 | 0.042221 | 0.13479 | 0.054249 | -0.040158 | 0.092979 | -0.008409 | 0.17574 | 0.11025 | 0.43957 | -0.099689 | -65.4516 | 1.026 | 53.3864 | 57.5263 | 57.7133 | 57.5242 | -65.8748 | 65.3331 | -57.4933 | 65.3926 | 65.4243 | 0.09128 | -57.5588 | -57.2295 | -0.44201 | -0.14276 | -0.018871 | 118.8191 | 119.2611 | 0.044188 | -0.14491 | 65.6085 | 65.543 | 65.8723 | 65.5257 | -57.7688 | 122.959 | 123.146 | 122.9569 | 66.4587 | -123.5438
3463.7969 | 123.2712 | -65.3961 | 57.5912 | -0.0029761 | -0.072102 | 0.023112 | -0.0050408 | -0.0097238 | 0.012292 | -0.015108 | 0.044161 | 0.047731 | 0.042648 | 0.13457 | 0.054676 | -0.049315 | 0.0884 | 0.000747 | 0.1849 | 0.11483 | 0.42126 | -0.10427 | -65.4516 | 1.0306 | 53.4505 | 57.5126 | 57.7133 | 57.5196 | -65.8793 | 65.2918 | -57.4063 | 65.3468 | 65.3969 | 0.10501 | -57.4764 | -57.17 | -0.48322 | -0.078675 | -0.055492 | 118.8466 | 119.3298 | 0.12201 | -0.071671 | 65.581 | 65.511 | 65.8174 | 65.4845 | -57.6955 | 122.9087 | 123.1094 | 122.9157 | 66.4267 | -123.4706
3464.7969 | 123.2437 | -65.387 | 57.6141 | 0.0046549 | -0.072316 | 0.023325 | -0.0052544 | -0.0097238 | 0.012078 | 0.015414 | 0.044375 | 0.047945 | 0.042435 | 0.13479 | 0.054462 | -0.053893 | 0.047193 | -0.008409 | 0.17574 | 0.11025 | 0.41668 | -0.10885 | -65.4516 | 1.0351 | 53.455 | 57.5172 | 57.7178 | 57.5287 | -65.8656 | 65.2781 | -57.4384 | 65.3331 | 65.3786 | 0.10044 | -57.5039 | -57.1975 | -0.47863 | -0.096984 | -0.064647 | 118.842 | 119.3206 | 0.1037 | -0.085402 | 65.5627 | 65.4972 | 65.8036 | 65.4342 | -57.723 | 122.9041 | 123.1048 | 122.9157 | 66.4221 | -123.4797
3465.7969 | 123.2117 | -65.4236 | 57.6187 | -0.010607 | -0.072316 | 0.022898 | -0.0052544 | -0.0097238 | 0.012292 | -0.0074779 | 0.044375 | 0.047945 | 0.042648 | 0.13479 | 0.054676 | -0.040158 | 0.051771 | 0.000747 | 0.1849 | 0.10567 | 0.43042 | -0.09511 | -65.4516 | 1.0443 | 53.5878 | 57.5172 | 57.7133 | 57.5242 | -65.8748 | 65.3285 | -57.4338 | 65.3834 | 65.4243 | 0.095857 | -57.513 | -57.1883 | -0.45117 | -0.10156 | -0.028026 | 119.0114 | 119.4626 | 0.094542 | -0.094558 | 65.6085 | 65.5293 | 65.854 | 65.4754 | -57.7138 | 122.9407 | 123.1368 | 122.9477 | 66.4679 | -123.4935
3466.7969 | 123.2803 | -65.4236 | 57.6416 | 0.012286 | -0.072529 | 0.023325 | -0.0052544 | -0.0097238 | 0.012292 | 0.00015261 | 0.044375 | 0.048158 | 0.042648 | 0.135 | 0.054676 | -0.044736 | 0.051771 | -0.003831 | 0.1849 | 0.11025 | 0.4121 | -0.10427 | -65.4562 | 1.0443 | 53.7435 | 57.5217 | 57.7178 | 57.5013 | -65.8793 | 65.3193 | -57.4567 | 65.3788 | 65.4198 | 0.10044 | -57.5313 | -57.2295 | -0.45575 | -0.11987 | -0.032604 | 119.1671 | 119.6228 | 0.076232 | -0.14034 | 65.6085 | 65.5338 | 65.8357 | 65.4754 | -57.7459 | 122.9453 | 123.1414 | 122.9248 | 66.4679 | -123.5209
3467.7969 | 123.2025 | -65.419 | 57.6828 | -0.0029761 | -0.072102 | 0.022684 | -0.0046134 | -0.010151 | 0.012292 | 0.00015261 | 0.044588 | 0.048158 | 0.042435 | 0.135 | 0.054462 | -0.040158 | 0.060928 | 0.000747 | 0.1849 | 0.10567 | 0.41668 | -0.10885 | -65.4562 | 1.0535 | 53.8305 | 57.5172 | 57.7133 | 57.5379 | -65.8748 | 65.3102 | -57.4979 | 65.3788 | 65.4198 | 0.10959 | -57.5771 | -57.2661 | -0.45575 | -0.16565 | -0.037182 | 119.2495 | 119.7052 | 0.030455 | -0.14491 | 65.6039 | 65.5247 | 65.8357 | 65.4799 | -57.7916 | 122.9362 | 123.1323 | 122.9569 | 66.4725 | -123.5576
3468.7969 | 123.2666 | -65.4053 | 57.6233 | -0.0029761 | -0.072529 | 0.023325 | -0.0050408 | -0.0099374 | 0.012078 | 0.0077831 | 0.044161 | 0.047731 | 0.042221 | 0.13457 | 0.054249 | -0.044736 | 0.051771 | -0.008409 | 0.17574 | 0.1011 | 0.42584 | -0.099689 | -65.4562 | 1.0443 | 53.4138 | 57.5217 | 57.7224 | 57.5562 | -65.8748 | 65.3056 | -57.4475 | 65.3605 | 65.3969 | 0.09128 | -57.5222 | -57.1975 | -0.46948 | -0.10156 | -0.050915 | 118.8191 | 119.2886 | 0.099122 | -0.067085 | 65.581 | 65.5064 | 65.8311 | 65.457 | -57.723 | 122.927 | 123.1277 | 122.9615 | 66.4496 | -123.498
3469.7969 | 123.2346 | -65.4099 | 57.5958 | -0.010607 | -0.072102 | 0.023325 | -0.0050408 | -0.0099374 | 0.012078 | -0.0074779 | 0.044161 | 0.047518 | 0.042221 | 0.13436 | 0.054462 | -0.044736 | 0.05635 | -0.012988 | 0.17574 | 0.11025 | 0.4121 | -0.099689 | -65.447 | 1.0443 | 53.4642 | 57.5263 | 57.7178 | 57.5333 | -65.8839 | 65.3102 | -57.4201 | 65.3651 | 65.3969 | 0.086701 | -57.4856 | -57.1837 | -0.47406 | -0.069516 | -0.03718 | 118.874 | 119.3481 | 0.12201 | -0.062512 | 65.5856 | 65.5201 | 65.822 | 65.4662 | -57.6955 | 122.9362 | 123.1277 | 122.9432 | 66.4542 | -123.4797
3470.7969 | 123.2758 | -65.3824 | 57.6462 | 0.0046549 | -0.072316 | 0.022898 | -0.0050408 | -0.010151 | 0.012078 | 0.00015261 | 0.044375 | 0.048158 | 0.042221 | 0.13479 | 0.054676 | -0.044736 | 0.051771 | -0.012988 | 0.18948 | 0.11025 | 0.42126 | -0.090531 | -65.4653 | 1.0489 | 53.5787 | 57.5172 | 57.7133 | 57.5562 | -65.8748 | 65.2919 | -57.4567 | 65.3376 | 65.3694 | 0.077543 | -57.5359 | -57.2249 | -0.49237 | -0.12903 | -0.082961 | 118.961 | 119.4534 | 0.067076 | -0.089973 | 65.5719 | 65.4926 | 65.8036 | 65.4342 | -57.7367 | 122.8995 | 123.0956 | 122.9386 | 66.4313 | -123.5209
3471.7969 | 123.2254 | -65.4144 | 57.6096 | -0.010607 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012292 | -0.0074779 | 0.044588 | 0.047731 | 0.042435 | 0.135 | 0.054462 | -0.040158 | 0.051771 | -0.003831 | 0.18948 | 0.11941 | 0.42126 | -0.099689 | -65.4516 | 1.0535 | 53.5558 | 57.5217 | 57.7178 | 57.5379 | -65.8793 | 65.3147 | -57.4201 | 65.3743 | 65.4106 | 0.095858 | -57.4901 | -57.1883 | -0.4649 | -0.087828 | -0.037181 | 118.9702 | 119.4351 | 0.10828 | -0.071667 | 65.6039 | 65.5338 | 65.8357 | 65.4662 | -57.7092 | 122.9362 | 123.1323 | 122.9523 | 66.4679 | -123.4889
3472.7969 | 123.1979 | -65.4144 | 57.6462 | -0.010607 | -0.072102 | 0.022898 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.044375 | 0.047518 | 0.042007 | 0.13436 | 0.054676 | -0.03558 | 0.05635 | -0.003831 | 0.19406 | 0.11025 | 0.42126 | -0.118 | -65.4516 | 1.058 | 53.4047 | 57.5217 | 57.7133 | 57.5425 | -65.8748 | 65.2964 | -57.4521 | 65.3788 | 65.4106 | 0.11417 | -57.5359 | -57.2249 | -0.46032 | -0.12445 | -0.037181 | 118.8191 | 119.2794 | 0.067076 | -0.10371 | 65.6085 | 65.5247 | 65.8357 | 65.4708 | -57.7642 | 122.9362 | 123.1277 | 122.9569 | 66.4725 | -123.5209
3473.7969 | 123.2208 | -65.4419 | 57.6141 | -0.0029761 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012078 | 0.0077831 | 0.044161 | 0.047518 | 0.042007 | 0.13457 | 0.054676 | -0.049315 | 0.047193 | -0.008409 | 0.18948 | 0.11025 | 0.42126 | -0.09511 | -65.447 | 1.058 | 53.4276 | 57.5172 | 57.7178 | 57.5333 | -65.8656 | 65.3468 | -57.4247 | 65.3926 | 65.4335 | 0.086701 | -57.5039 | -57.1929 | -0.4237 | -0.096984 | -0.005136 | 118.8695 | 119.2932 | 0.1037 | -0.080823 | 65.6314 | 65.5521 | 65.8632 | 65.4891 | -57.7092 | 122.959 | 123.1597 | 122.9752 | 66.4999 | -123.4797
3474.7969 | 123.2803 | -65.4053 | 57.6279 | 0.0046549 | -0.072102 | 0.022898 | -0.004827 | -0.0097238 | 0.012292 | 0.00015261 | 0.044375 | 0.047731 | 0.041794 | 0.13457 | 0.054676 | -0.044736 | 0.05635 | -0.008409 | 0.16201 | 0.1011 | 0.41668 | -0.10427 | -65.4516 | 1.058 | 53.5466 | 57.5217 | 57.7178 | 57.5196 | -65.8793 | 65.301 | -57.4659 | 65.3605 | 65.3969 | 0.095859 | -57.5268 | -57.2112 | -0.47406 | -0.10614 | -0.046337 | 118.9519 | 119.4259 | 0.089965 | -0.10829 | 65.5673 | 65.5064 | 65.822 | 65.4616 | -57.7321 | 122.927 | 123.1231 | 122.9248 | 66.4633 | -123.5072
3475.7969 | 123.2346 | -65.4007 | 57.6279 | 0.0046549 | -0.072102 | 0.023112 | -0.0050408 | -0.0099374 | 0.012292 | 0.0077831 | 0.044588 | 0.047945 | 0.042007 | 0.13457 | 0.054249 | -0.03558 | 0.047193 | -0.003831 | 0.18948 | 0.10567 | 0.42126 | -0.10427 | -65.447 | 1.058 | 53.4642 | 57.5126 | 57.7133 | 57.5379 | -65.8793 | 65.2964 | -57.4384 | 65.3651 | 65.3969 | 0.10044 | -57.5222 | -57.2066 | -0.47864 | -0.1153 | -0.046335 | 118.8649 | 119.3435 | 0.085386 | -0.089978 | 65.5902 | 65.5064 | 65.822 | 65.4479 | -57.7321 | 122.9133 | 123.114 | 122.9386 | 66.4587 | -123.5072
3476.7969 | 123.2666 | -65.4007 | 57.6324 | 0.012286 | -0.072102 | 0.022898 | -0.0052544 | -0.0099374 | 0.012078 | 0.00015261 | 0.044375 | 0.047731 | 0.042007 | 0.13436 | 0.054462 | -0.044736 | 0.05635 | -0.003831 | 0.19406 | 0.11941 | 0.4121 | -0.099689 | -65.4516 | 1.0718 | 53.5878 | 57.5217 | 57.7087 | 57.547 | -65.8793 | 65.301 | -57.4384 | 65.356 | 65.3969 | 0.095858 | -57.513 | -57.2203 | -0.47864 | -0.11072 | -0.050914 | 118.9885 | 119.4671 | 0.076231 | -0.085398 | 65.5948 | 65.5201 | 65.8128 | 65.457 | -57.7321 | 122.9224 | 123.1094 | 122.9477 | 66.4725 | -123.5118
3477.7969 | 123.2529 | -65.4373 | 57.6416 | 0.0046549 | -0.072102 | 0.023112 | -0.0050408 | -0.0099374 | 0.011865 | 0.00015261 | 0.044161 | 0.047518 | 0.042435 | 0.13436 | 0.054462 | -0.044736 | 0.047193 | -0.012988 | 0.19406 | 0.10567 | 0.42126 | -0.099689 | -65.4516 | 1.0764 | 53.597 | 57.5217 | 57.7041 | 57.5196 | -65.8748 | 65.3376 | -57.4475 | 65.3926 | 65.4243 | 0.086701 | -57.5359 | -57.2203 | -0.43744 | -0.11987 | -0.014293 | 119.0343 | 119.4717 | 0.062496 | -0.12203 | 65.6314 | 65.543 | 65.8586 | 65.4845 | -57.7413 | 122.959 | 123.1414 | 122.9569 | 66.5137 | -123.5164
3478.8594 | 123.2712 | -65.3915 | 57.6096 | -0.010607 | -0.072316 | 0.022898 | -0.0052544 | -0.010151 | 0.012506 | 0.0077831 | 0.044375 | 0.047518 | 0.042007 | 0.13436 | 0.054462 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.1011 | 0.41668 | -0.09511 | -65.4562 | 1.0718 | 53.6244 | 57.5126 | 57.7087 | 57.5196 | -65.8793 | 65.2964 | -57.4338 | 65.3514 | 65.3877 | 0.091279 | -57.5085 | -57.1929 | -0.48779 | -0.096985 | -0.064647 | 119.016 | 119.5038 | 0.099119 | -0.089981 | 65.5673 | 65.4926 | 65.8082 | 65.4479 | -57.7047 | 122.9041 | 123.1002 | 122.9111 | 66.4633 | -123.4889
3479.7969 | 123.2483 | -65.4373 | 57.6096 | 0.0046549 | -0.072102 | 0.023112 | -0.004827 | -0.010151 | 0.011865 | 0.0077831 | 0.044802 | 0.047518 | 0.042007 | 0.13457 | 0.054035 | -0.044736 | 0.042614 | -0.008409 | 0.18032 | 0.11025 | 0.41668 | -0.09511 | -65.447 | 1.0809 | 53.6428 | 57.5263 | 57.7087 | 57.547 | -65.8793 | 65.3422 | -57.4292 | 65.3926 | 65.4289 | 0.086701 | -57.4993 | -57.1929 | -0.44202 | -0.083249 | -0.009714 | 119.0801 | 119.5221 | 0.099119 | -0.06251 | 65.6176 | 65.5476 | 65.854 | 65.4799 | -57.7047 | 122.9636 | 123.146 | 122.9844 | 66.5183 | -123.4889
3480.7969 | 123.2803 | -65.3824 | 57.6324 | -0.010607 | -0.072316 | 0.023112 | -0.0052544 | -0.0099374 | 0.012292 | 0.0077831 | 0.044161 | 0.047518 | 0.041794 | 0.13372 | 0.054462 | -0.053893 | 0.060928 | -0.008409 | 0.19406 | 0.11941 | 0.42126 | -0.099689 | -65.4425 | 1.0855 | 53.4138 | 57.5217 | 57.7133 | 57.5425 | -65.8748 | 65.2827 | -57.4384 | 65.3285 | 65.374 | 0.09128 | -57.513 | -57.2112 | -0.49237 | -0.11072 | -0.060067 | 118.7962 | 119.2886 | 0.080809 | -0.089976 | 65.5764 | 65.5018 | 65.8036 | 65.4433 | -57.7321 | 122.9041 | 123.0956 | 122.9249 | 66.4679 | -123.5072
3481.7969 | 123.2895 | -65.3732 | 57.605 | 0.0046549 | -0.071888 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.00015261 | 0.043947 | 0.047731 | 0.042007 | 0.13372 | 0.054249 | -0.049315 | 0.051771 | -0.003831 | 0.18948 | 0.11025 | 0.41668 | -0.11342 | -65.4425 | 1.0855 | 53.5283 | 57.5217 | 57.7133 | 57.5608 | -65.8793 | 65.2598 | -57.4155 | 65.3239 | 65.3694 | 0.10959 | -57.4947 | -57.1883 | -0.5061 | -0.08325 | -0.069222 | 118.9015 | 119.4076 | 0.10827 | -0.044196 | 65.5627 | 65.4835 | 65.7899 | 65.425 | -57.7184 | 122.895 | 123.0865 | 122.934 | 66.4587 | -123.4843
3482.7969 | 123.262 | -65.387 | 57.6004 | -0.0029761 | -0.072102 | 0.02247 | -0.0050408 | -0.010151 | 0.012506 | 0.0077831 | 0.043947 | 0.047518 | 0.042221 | 0.13436 | 0.054462 | -0.044736 | 0.051771 | -0.003831 | 0.17574 | 0.1011 | 0.42584 | -0.10427 | -65.4516 | 1.0855 | 53.5466 | 57.5172 | 57.7087 | 57.5425 | -65.8793 | 65.2827 | -57.4247 | 65.3422 | 65.3831 | 0.10044 | -57.4993 | -57.1746 | -0.49237 | -0.083251 | -0.064647 | 118.9336 | 119.4259 | 0.10827 | -0.057933 | 65.5627 | 65.4881 | 65.8128 | 65.4387 | -57.7047 | 122.9041 | 123.0956 | 122.9294 | 66.4725 | -123.4797
3483.7969 | 123.317 | -65.4053 | 57.6508 | -0.0029761 | -0.072102 | 0.022898 | -0.004827 | -0.010151 | 0.012292 | 0.00015261 | 0.043947 | 0.047518 | 0.041794 | 0.13457 | 0.054462 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.11483 | 0.42584 | -0.099689 | -65.447 | 1.0947 | 53.3543 | 57.5217 | 57.7224 | 57.5333 | -65.8748 | 65.3056 | -57.4659 | 65.356 | 65.4014 | 0.095858 | -57.5359 | -57.2249 | -0.46948 | -0.12903 | -0.041758 | 118.7596 | 119.2291 | 0.071656 | -0.11744 | 65.5902 | 65.5201 | 65.8311 | 65.457 | -57.7504 | 122.927 | 123.1277 | 122.9386 | 66.4999 | -123.5255
3484.7969 | 123.2529 | -65.419 | 57.6279 | 0.0046549 | -0.072102 | 0.022898 | -0.0050408 | -0.0097238 | 0.012292 | 0.0077831 | 0.043947 | 0.047518 | 0.041794 | 0.13436 | 0.054462 | -0.044736 | 0.051771 | -0.012988 | 0.16659 | 0.11025 | 0.42584 | -0.10427 | -65.4425 | 1.0901 | 53.3268 | 57.5172 | 57.7178 | 57.5379 | -65.8793 | 65.3147 | -57.4613 | 65.3743 | 65.406 | 0.09128 | -57.5176 | -57.202 | -0.46033 | -0.11072 | -0.023446 | 118.7458 | 119.2062 | 0.089965 | -0.089978 | 65.5856 | 65.5293 | 65.8448 | 65.4708 | -57.7321 | 122.9362 | 123.1368 | 122.9569 | 66.5091 | -123.5072
3485.7969 | 123.2437 | -65.4144 | 57.6324 | 0.0046549 | -0.072102 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.015414 | 0.043947 | 0.047518 | 0.041794 | 0.13436 | 0.054462 | -0.044736 | 0.047193 | -0.003831 | 0.19406 | 0.11025 | 0.42126 | -0.09511 | -65.4562 | 1.0947 | 53.3177 | 57.5172 | 57.7178 | 57.5379 | -65.8793 | 65.3193 | -57.4384 | 65.3697 | 65.4106 | 0.091279 | -57.5222 | -57.2112 | -0.4649 | -0.11529 | -0.041759 | 118.7321 | 119.197 | 0.085388 | -0.094555 | 65.6085 | 65.5247 | 65.8357 | 65.4616 | -57.7276 | 122.9316 | 123.1323 | 122.9523 | 66.5091 | -123.5118
3486.7969 | 123.2254 | -65.3961 | 57.637 | 0.0046549 | -0.072102 | 0.023112 | -0.0050408 | -0.0097238 | 0.012292 | 0.015414 | 0.044161 | 0.047518 | 0.042007 | 0.13393 | 0.054462 | -0.044736 | 0.051771 | 0.000747 | 0.18948 | 0.10567 | 0.4121 | -0.10885 | -65.4516 | 1.0992 | 53.2948 | 57.5217 | 57.7224 | 57.5425 | -65.8702 | 65.2873 | -57.4475 | 65.3514 | 65.3969 | 0.10959 | -57.5313 | -57.2249 | -0.47406 | -0.11529 | -0.055492 | 118.6909 | 119.165 | 0.085389 | -0.094554 | 65.5856 | 65.5018 | 65.8082 | 65.4479 | -57.7459 | 122.9178 | 123.1185 | 122.9386 | 66.4954 | -123.5072
3487.7969 | 123.2895 | -65.419 | 57.5867 | -0.0029761 | -0.072316 | 0.022684 | -0.0052544 | -0.010151 | 0.012292 | 0.0077831 | 0.043947 | 0.047731 | 0.041794 | 0.13351 | 0.054462 | -0.040158 | 0.051771 | -0.003831 | 0.16659 | 0.11483 | 0.43042 | -0.12258 | -65.4516 | 1.1038 | 53.2994 | 57.5217 | 57.7087 | 57.5516 | -65.8702 | 65.2964 | -57.4201 | 65.3788 | 65.4152 | 0.11875 | -57.4718 | -57.1563 | -0.45117 | -0.06494 | -0.032604 | 118.7184 | 119.1695 | 0.12201 | -0.035043 | 65.5856 | 65.5338 | 65.8494 | 65.4708 | -57.7093 | 122.9407 | 123.1277 | 122.9706 | 66.5228 | -123.4568
3488.7969 | 123.2391 | -65.4144 | 57.6553 | -0.0029761 | -0.072316 | 0.022684 | -0.0050408 | -0.0099374 | 0.012719 | 0.00015261 | 0.043734 | 0.047304 | 0.041794 | 0.13393 | 0.054249 | -0.049315 | 0.05635 | -0.008409 | 0.18948 | 0.10567 | 0.41668 | -0.099689 | -65.447 | 1.0901 | 53.2124 | 57.5172 | 57.7133 | 57.5333 | -65.8748 | 65.3147 | -57.4659 | 65.3651 | 65.406 | 0.09128 | -57.5497 | -57.2387 | -0.46032 | -0.13818 | -0.032602 | 118.6268 | 119.0871 | 0.057921 | -0.12202 | 65.6039 | 65.5201 | 65.8311 | 65.4708 | -57.755 | 122.9316 | 123.1277 | 122.9477 | 66.5045 | -123.5301
3489.7969 | 123.2986 | -65.4099 | 57.5821 | 0.0046549 | -0.072316 | 0.022684 | -0.0050408 | -0.0097238 | 0.012292 | 0.00015261 | 0.043947 | 0.047304 | 0.042007 | 0.13393 | 0.054462 | -0.044736 | 0.05635 | -0.003831 | 0.18948 | 0.11025 | 0.42584 | -0.10427 | -65.447 | 1.1038 | 53.3589 | 57.5172 | 57.7087 | 57.5562 | -65.8748 | 65.3056 | -57.3926 | 65.3651 | 65.406 | 0.10044 | -57.4718 | -57.1563 | -0.4649 | -0.06494 | -0.03718 | 118.7687 | 119.2336 | 0.12658 | -0.025886 | 65.5993 | 65.5201 | 65.8357 | 65.4662 | -57.6864 | 122.927 | 123.1185 | 122.9661 | 66.5137 | -123.4568
3490.7969 | 123.2895 | -65.419 | 57.5912 | 0.0046549 | -0.071888 | 0.023112 | -0.0046134 | -0.0095102 | 0.011865 | -0.0074779 | 0.04352 | 0.047518 | 0.04158 | 0.13351 | 0.054249 | -0.040158 | 0.047193 | -0.012988 | 0.1849 | 0.11483 | 0.42584 | -0.099689 | -65.447 | 1.1038 | 53.1986 | 57.5309 | 57.7178 | 57.5654 | -65.8839 | 65.3193 | -57.4063 | 65.3788 | 65.406 | 0.086701 | -57.4764 | -57.1654 | -0.46491 | -0.060361 | -0.028025 | 118.6176 | 119.0825 | 0.12659 | -0.025885 | 65.6039 | 65.5338 | 65.8448 | 65.4662 | -57.6909 | 122.9499 | 123.1368 | 122.9844 | 66.5228 | -123.4752
3491.7969 | 123.2529 | -65.4053 | 57.6141 | -0.0029761 | -0.071888 | 0.022898 | -0.0052544 | -0.0097238 | 0.012078 | -0.0074779 | 0.043947 | 0.047518 | 0.042007 | 0.13372 | 0.054462 | -0.053893 | 0.051771 | -0.012988 | 0.18032 | 0.11483 | 0.43042 | -0.10885 | -65.4516 | 1.0992 | 53.2032 | 57.5263 | 57.7178 | 57.5196 | -65.8748 | 65.2964 | -57.4338 | 65.3514 | 65.3923 | 0.095859 | -57.4993 | -57.1837 | -0.46948 | -0.087827 | -0.046337 | 118.6085 | 119.078 | 0.1037 | -0.094559 | 65.5856 | 65.5201 | 65.8357 | 65.457 | -57.723 | 122.9316 | 123.1231 | 122.9248 | 66.5045 | -123.4889
3492.7969 | 123.2162 | -65.3915 | 57.6462 | -0.0029761 | -0.072102 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.00015261 | 0.043947 | 0.047731 | 0.041794 | 0.13351 | 0.054676 | -0.044736 | 0.051771 | -0.008409 | 0.17117 | 0.11941 | 0.42584 | -0.10427 | -65.4562 | 1.1176 | 53.1849 | 57.5217 | 57.727 | 57.5379 | -65.8748 | 65.2873 | -57.475 | 65.3468 | 65.3831 | 0.095859 | -57.5268 | -57.2203 | -0.48321 | -0.12445 | -0.064647 | 118.5764 | 119.0596 | 0.080812 | -0.10829 | 65.5627 | 65.511 | 65.8174 | 65.4433 | -57.7504 | 122.9133 | 123.1185 | 122.9294 | 66.5091 | -123.5209
3493.7969 | 123.2758 | -65.419 | 57.605 | 0.0046549 | -0.072316 | 0.022898 | -0.0052544 | -0.0099374 | 0.012078 | 0.00015261 | 0.043734 | 0.04709 | 0.042007 | 0.13372 | 0.054462 | -0.049315 | 0.060928 | 0.000747 | 0.17574 | 0.11483 | 0.42584 | -0.10427 | -65.4562 | 1.1267 | 53.1025 | 57.5263 | 57.7178 | 57.5425 | -65.8748 | 65.3147 | -57.4292 | 65.3697 | 65.4198 | 0.10501 | -57.4901 | -57.1791 | -0.45575 | -0.078671 | -0.037182 | 118.5215 | 118.9772 | 0.11285 | -0.06251 | 65.5947 | 65.5338 | 65.8448 | 65.4799 | -57.7092 | 122.9453 | 123.1368 | 122.9615 | 66.5457 | -123.4797
3494.7969 | 123.1613 | -65.419 | 57.6599 | -0.0029761 | -0.071888 | 0.022684 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.044161 | 0.047945 | 0.04158 | 0.13372 | 0.054249 | -0.044736 | 0.051771 | 0.000747 | 0.19406 | 0.11025 | 0.42584 | -0.10427 | -65.4425 | 1.1176 | 53.0842 | 57.5172 | 57.7224 | 57.5608 | -65.8748 | 65.3147 | -57.4659 | 65.3743 | 65.4198 | 0.10501 | -57.5497 | -57.2341 | -0.45575 | -0.14276 | -0.023446 | 118.5032 | 118.9589 | 0.062501 | -0.099128 | 65.6131 | 65.5293 | 65.8448 | 65.4708 | -57.7642 | 122.9362 | 123.1414 | 122.9798 | 66.5366 | -123.5347
3495.7969 | 123.2712 | -65.3824 | 57.6416 | 0.012286 | -0.072102 | 0.022898 | -0.0052544 | -0.0099374 | 0.012292 | 0.00015261 | 0.044161 | 0.047731 | 0.041794 | 0.13372 | 0.054676 | -0.044736 | 0.047193 | -0.008409 | 0.18948 | 0.10567 | 0.4121 | -0.099689 | -65.4425 | 1.1267 | 53.1299 | 57.5263 | 57.7133 | 57.5333 | -65.8748 | 65.2827 | -57.4521 | 65.3376 | 65.374 | 0.09128 | -57.5359 | -57.2295 | -0.49237 | -0.11529 | -0.060067 | 118.5123 | 119.0047 | 0.071653 | -0.10829 | 65.5719 | 65.4881 | 65.7945 | 65.4296 | -57.7413 | 122.9087 | 123.0956 | 122.9157 | 66.5091 | -123.5164
3496.7969 | 123.143 | -65.451 | 57.6553 | -0.0029761 | -0.072316 | 0.022898 | -0.0052544 | -0.0099374 | 0.012292 | -0.0074779 | 0.043947 | 0.047304 | 0.04158 | 0.13372 | 0.054676 | -0.040158 | 0.051771 | -0.008409 | 0.16659 | 0.10567 | 0.4121 | -0.099689 | -65.4425 | 1.1313 | 52.9926 | 57.5217 | 57.7178 | 57.5196 | -65.8702 | 65.3514 | -57.4887 | 65.4109 | 65.4426 | 0.09128 | -57.5497 | -57.2432 | -0.41913 | -0.1336 | 0.008598 | 118.4436 | 118.8628 | 0.0625 | -0.13576 | 65.6176 | 65.5567 | 65.8632 | 65.5028 | -57.755 | 122.9728 | 123.1689 | 122.9706 | 66.5823 | -123.5255
3497.7969 | 123.2529 | -65.3778 | 57.6416 | -0.010607 | -0.072529 | 0.02247 | -0.0050408 | -0.010151 | 0.011865 | 0.00015261 | 0.043947 | 0.04709 | 0.04158 | 0.13351 | 0.054676 | -0.049315 | 0.051771 | 0.000747 | 0.18948 | 0.10567 | 0.42126 | -0.099689 | -65.4516 | 1.1359 | 52.9422 | 57.5309 | 57.7178 | 57.5242 | -65.8793 | 65.2781 | -57.4521 | 65.3285 | 65.3786 | 0.10044 | -57.5359 | -57.2203 | -0.50153 | -0.11071 | -0.073802 | 118.32 | 118.8215 | 0.076232 | -0.11745 | 65.5673 | 65.4835 | 65.7991 | 65.4296 | -57.7413 | 122.9087 | 123.0956 | 122.902 | 66.5137 | -123.5209
3498.8594 | 123.1613 | -65.3961 | 57.6599 | -0.010607 | -0.072316 | 0.022898 | -0.004827 | -0.0099374 | 0.011865 | 0.00015261 | 0.043947 | 0.047731 | 0.042221 | 0.13329 | 0.054462 | -0.044736 | 0.05635 | -0.008409 | 0.18948 | 0.11483 | 0.42126 | -0.10427 | -65.4562 | 1.1405 | 53.162 | 57.5172 | 57.7133 | 57.547 | -65.8793 | 65.2918 | -57.4704 | 65.3514 | 65.3877 | 0.095859 | -57.5451 | -57.2387 | -0.48322 | -0.14276 | -0.06007 | 118.5581 | 119.0413 | 0.053343 | -0.11286 | 65.5856 | 65.511 | 65.8174 | 65.4525 | -57.7642 | 122.9133 | 123.1094 | 122.9432 | 66.5366 | -123.5392
3499.7969 | 123.2666 | -65.3961 | 57.637 | -0.0029761 | -0.072529 | 0.023112 | -0.0050408 | -0.0097238 | 0.012292 | 0.00015261 | 0.043947 | 0.047518 | 0.041794 | 0.13393 | 0.054462 | -0.044736 | 0.05635 | -0.008409 | 0.18032 | 0.10567 | 0.4121 | -0.09511 | -65.447 | 1.1496 | 52.9926 | 57.5309 | 57.7224 | 57.5242 | -65.8748 | 65.301 | -57.4567 | 65.3514 | 65.3877 | 0.086701 | -57.5313 | -57.2249 | -0.47864 | -0.10614 | -0.050913 | 118.3887 | 118.8673 | 0.085389 | -0.11287 | 65.5764 | 65.5018 | 65.8082 | 65.4525 | -57.7321 | 122.927 | 123.1185 | 122.9203 | 66.5457 | -123.5118
3500.7969 | 123.0927 | -65.3915 | 57.7057 | -0.0029761 | -0.072316 | 0.022898 | -0.0050408 | -0.010365 | 0.012292 | 0.0077831 | 0.044161 | 0.047304 | 0.042007 | 0.13329 | 0.054249 | -0.040158 | 0.05635 | 0.000747 | 0.18032 | 0.10567 | 0.41668 | -0.10885 | -65.447 | 1.1496 | 52.869 | 57.5309 | 57.7178 | 57.5425 | -65.8748 | 65.2827 | -57.5254 | 65.3514 | 65.3923 | 0.10959 | -57.6 | -57.289 | -0.48321 | -0.1748 | -0.05549 | 118.2605 | 118.7437 | 0.012146 | -0.16322 | 65.5719 | 65.4972 | 65.8082 | 65.4479 | -57.8145 | 122.9224 | 123.1094 | 122.934 | 66.5412 | -123.5804
3501.7969 | 123.1705 | -65.4007 | 57.6736 | 0.012286 | -0.072102 | 0.023112 | -0.0050408 | -0.0099374 | 0.012292 | -0.0074779 | 0.043947 | 0.047304 | 0.041794 | 0.13329 | 0.054249 | -0.044736 | 0.051771 | -0.003831 | 0.18948 | 0.11025 | 0.43042 | -0.099689 | -65.4425 | 1.1496 | 52.7362 | 57.5172 | 57.7224 | 57.5425 | -65.8656 | 65.301 | -57.4842 | 65.356 | 65.3969 | 0.095858 | -57.5634 | -57.2432 | -0.4649 | -0.15649 | -0.041756 | 118.1369 | 118.6018 | 0.048768 | -0.13117 | 65.5902 | 65.5109 | 65.8311 | 65.4525 | -57.7733 | 122.9178 | 123.1231 | 122.9432 | 66.5503 | -123.5392
3502.8594 | 123.1796 | -65.4602 | 57.6508 | 0.0046549 | -0.072316 | 0.022898 | -0.0050408 | -0.0099374 | 0.012078 | 0.015414 | 0.043947 | 0.047304 | 0.041794 | 0.13286 | 0.054676 | -0.049315 | 0.051771 | 0.000747 | 0.19406 | 0.11483 | 0.42126 | -0.10427 | -65.4516 | 1.1496 | 52.8827 | 57.5217 | 57.7178 | 57.5608 | -65.8748 | 65.3559 | -57.4567 | 65.4109 | 65.461 | 0.10501 | -57.5359 | -57.2295 | -0.41455 | -0.12903 | 0.008595 | 118.3429 | 118.7574 | 0.067077 | -0.089973 | 65.6543 | 65.575 | 65.8815 | 65.512 | -57.755 | 122.9819 | 123.178 | 123.021 | 66.6098 | -123.5255
3503.7969 | 123.2346 | -65.4144 | 57.6553 | -0.0029761 | -0.072316 | 0.022898 | -0.0050408 | -0.010151 | 0.012078 | 0.00015261 | 0.043947 | 0.04709 | 0.04158 | 0.13351 | 0.054462 | -0.049315 | 0.05635 | -0.008409 | 0.18948 | 0.11483 | 0.41668 | -0.10427 | -65.4516 | 1.1588 | 52.8323 | 57.5309 | 57.727 | 57.5562 | -65.8748 | 65.3102 | -57.4659 | 65.3651 | 65.406 | 0.095859 | -57.5405 | -57.2387 | -0.46032 | -0.12445 | -0.037181 | 118.2468 | 118.7071 | 0.071657 | -0.099128 | 65.6039 | 65.5293 | 65.8311 | 65.4708 | -57.7596 | 122.9453 | 123.1414 | 122.9706 | 66.5732 | -123.5301
3504.7969 | 123.143 | -65.4373 | 57.6691 | 0.0046549 | -0.072529 | 0.023112 | -0.0050408 | -0.0099374 | 0.012506 | 0.015414 | 0.04352 | 0.04709 | 0.04158 | 0.13329 | 0.054676 | -0.040158 | 0.051771 | -0.008409 | 0.1849 | 0.11483 | 0.4121 | -0.10885 | -65.447 | 1.1542 | 52.9376 | 57.5309 | 57.7133 | 57.5242 | -65.8748 | 65.3285 | -57.4842 | 65.3972 | 65.4289 | 0.10044 | -57.5542 | -57.257 | -0.43744 | -0.13818 | -0.009714 | 118.375 | 118.8124 | 0.044188 | -0.14491 | 65.6222 | 65.5521 | 65.8494 | 65.4891 | -57.7779 | 122.9682 | 123.1506 | 122.9615 | 66.5915 | -123.5438
3505.7969 | 123.1567 | -65.4419 | 57.6828 | 0.0046549 | -0.072316 | 0.02247 | -0.004827 | -0.0097238 | 0.012292 | 0.00015261 | 0.043947 | 0.047518 | 0.04158 | 0.13329 | 0.054249 | -0.044736 | 0.051771 | -0.008409 | 0.18948 | 0.10567 | 0.4121 | -0.099689 | -65.447 | 1.1679 | 53.1162 | 57.5172 | 57.7178 | 57.5425 | -65.8702 | 65.3422 | -57.4933 | 65.3972 | 65.4335 | 0.09128 | -57.5771 | -57.2707 | -0.42828 | -0.16565 | -0.005136 | 118.5581 | 118.9864 | 0.035034 | -0.14033 | 65.6314 | 65.5476 | 65.854 | 65.4937 | -57.7825 | 122.959 | 123.1597 | 122.9844 | 66.6098 | -123.553
3506.7969 | 123.2025 | -65.4373 | 57.6553 | 0.012286 | -0.072102 | 0.022684 | -0.004827 | -0.0099374 | 0.011865 | 0.0077831 | 0.043947 | 0.04709 | 0.041366 | 0.13351 | 0.054035 | -0.040158 | 0.047193 | -0.003831 | 0.18948 | 0.11025 | 0.4121 | -0.099689 | -65.447 | 1.1588 | 52.9285 | 57.5263 | 57.7178 | 57.5287 | -65.8793 | 65.3376 | -57.4659 | 65.3972 | 65.4335 | 0.095858 | -57.5451 | -57.2432 | -0.44202 | -0.12903 | -0.009714 | 118.3658 | 118.8078 | 0.0625 | -0.1266 | 65.6268 | 65.5476 | 65.8494 | 65.4845 | -57.755 | 122.9636 | 123.1552 | 122.9661 | 66.5961 | -123.5347
3507.7969 | 123.175 | -65.4465 | 57.6599 | -0.0029761 | -0.072529 | 0.02247 | -0.004827 | -0.0097238 | 0.012292 | -0.0074779 | 0.043947 | 0.04709 | 0.041794 | 0.13308 | 0.054035 | -0.040158 | 0.047193 | -0.003831 | 0.18032 | 0.10567 | 0.42126 | -0.10427 | -65.4379 | 1.1634 | 52.695 | 57.5263 | 57.7316 | 57.5425 | -65.8793 | 65.3422 | -57.4796 | 65.4063 | 65.4426 | 0.10044 | -57.5542 | -57.2387 | -0.43286 | -0.1336 | 0.008598 | 118.1414 | 118.5743 | 0.071658 | -0.11744 | 65.6268 | 65.5521 | 65.8677 | 65.4937 | -57.7642 | 122.9728 | 123.178 | 122.9889 | 66.6098 | -123.5392
3508.7969 | 123.1705 | -65.4785 | 57.6416 | -0.0029761 | -0.072529 | 0.022684 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.043734 | 0.046877 | 0.04158 | 0.13286 | 0.054462 | -0.040158 | 0.051771 | 0.000747 | 0.19406 | 0.11483 | 0.4121 | -0.10885 | -65.447 | 1.1725 | 52.6125 | 57.5355 | 57.7224 | 57.547 | -65.8748 | 65.3697 | -57.4475 | 65.4384 | 65.4793 | 0.10959 | -57.5268 | -57.2295 | -0.39624 | -0.10614 | 0.031485 | 118.0911 | 118.4873 | 0.080811 | -0.094554 | 65.6726 | 65.5933 | 65.8906 | 65.5303 | -57.7504 | 123.014 | 123.2009 | 123.0256 | 66.651 | -123.5164
3509.7969 | 123.1705 | -65.4373 | 57.6462 | -0.0029761 | -0.072529 | 0.02247 | -0.0050408 | -0.0099374 | 0.012292 | 0.0077831 | 0.044161 | 0.047304 | 0.04158 | 0.13308 | 0.054249 | -0.044736 | 0.060928 | -0.008409 | 0.1849 | 0.11025 | 0.42584 | -0.10427 | -65.4379 | 1.1771 | 52.7499 | 57.5263 | 57.7133 | 57.5242 | -65.8702 | 65.333 | -57.4613 | 65.3926 | 65.4289 | 0.095859 | -57.5359 | -57.2203 | -0.43286 | -0.11987 | -0.000557 | 118.1872 | 118.6201 | 0.067076 | -0.12202 | 65.6222 | 65.5476 | 65.8632 | 65.4982 | -57.7504 | 122.9636 | 123.1506 | 122.9615 | 66.6144 | -123.5164
3510.7969 | 123.2025 | -65.4099 | 57.6324 | -0.0029761 | -0.072743 | 0.023325 | -0.004827 | -0.0099374 | 0.012506 | 0.00015261 | 0.043734 | 0.04709 | 0.042007 | 0.13329 | 0.054462 | -0.044736 | 0.060928 | 0.000747 | 0.1849 | 0.11025 | 0.42126 | -0.099689 | -65.447 | 1.1817 | 52.7728 | 57.5309 | 57.7224 | 57.5287 | -65.8702 | 65.3102 | -57.4475 | 65.3651 | 65.4106 | 0.10044 | -57.5222 | -57.2112 | -0.46032 | -0.10156 | -0.03718 | 118.1827 | 118.643 | 0.089967 | -0.10371 | 65.5948 | 65.5201 | 65.8311 | 65.4708 | -57.7321 | 122.9407 | 123.1323 | 122.9386 | 66.5915 | -123.5026
3511.7969 | 123.1567 | -65.451 | 57.6645 | 0.012286 | -0.072102 | 0.022898 | -0.004827 | -0.0099374 | 0.012078 | 0.00015261 | 0.043734 | 0.047304 | 0.04158 | 0.13308 | 0.054462 | -0.044736 | 0.047193 | -0.003831 | 0.17574 | 0.10567 | 0.42584 | -0.099689 | -65.4562 | 1.1817 | 52.6354 | 57.5263 | 57.727 | 57.5242 | -65.8793 | 65.3514 | -57.4887 | 65.4063 | 65.4472 | 0.095858 | -57.5588 | -57.2387 | -0.42828 | -0.13818 | -0.005138 | 118.0865 | 118.5148 | 0.062501 | -0.14034 | 65.6268 | 65.5567 | 65.8769 | 65.4982 | -57.7642 | 122.9774 | 123.178 | 122.9752 | 66.6327 | -123.5438
3512.7969 | 123.1522 | -65.4282 | 57.637 | -0.0029761 | -0.072743 | 0.022898 | -0.0043998 | -0.010365 | 0.012078 | -0.0074779 | 0.043734 | 0.04709 | 0.04158 | 0.13286 | 0.054462 | -0.049315 | 0.051771 | -0.008409 | 0.19406 | 0.11941 | 0.4121 | -0.09511 | -65.4425 | 1.1862 | 52.4706 | 57.5309 | 57.7224 | 57.5425 | -65.8656 | 65.3331 | -57.443 | 65.3788 | 65.4198 | 0.086701 | -57.5176 | -57.2249 | -0.43743 | -0.10614 | -0.01429 | 117.8988 | 118.3362 | 0.085389 | -0.094554 | 65.6222 | 65.5476 | 65.8403 | 65.4799 | -57.7321 | 122.959 | 123.1506 | 122.9706 | 66.6144 | -123.5026
3513.7969 | 123.2162 | -65.4099 | 57.6462 | -0.018238 | -0.072529 | 0.022684 | -0.004827 | -0.010365 | 0.011865 | 0.00015261 | 0.04352 | 0.046877 | 0.041794 | 0.13265 | 0.054462 | -0.044736 | 0.060928 | -0.003831 | 0.1849 | 0.1011 | 0.41668 | -0.099689 | -65.4379 | 1.1771 | 52.2783 | 57.5355 | 57.7224 | 57.5516 | -65.8748 | 65.3102 | -57.4613 | 65.3651 | 65.406 | 0.095858 | -57.5451 | -57.2295 | -0.4649 | -0.11071 | -0.028023 | 117.6882 | 118.1531 | 0.076234 | -0.094552 | 65.5948 | 65.5109 | 65.8265 | 65.4708 | -57.7459 | 122.9453 | 123.1323 | 122.9615 | 66.5869 | -123.5209
3514.8594 | 123.1659 | -65.4327 | 57.6645 | -0.0029761 | -0.072743 | 0.022684 | -0.0046134 | -0.0099374 | 0.012078 | 0.015414 | 0.04352 | 0.047304 | 0.04158 | 0.13308 | 0.054462 | -0.044736 | 0.047193 | -0.008409 | 0.19406 | 0.10567 | 0.43042 | -0.099689 | -65.4516 | 1.1954 | 52.5027 | 57.5217 | 57.7224 | 57.5562 | -65.8656 | 65.3331 | -57.4704 | 65.388 | 65.4243 | 0.09128 | -57.5588 | -57.2341 | -0.43286 | -0.14276 | -0.018871 | 117.9354 | 118.3683 | 0.057923 | -0.10828 | 65.6268 | 65.5384 | 65.8632 | 65.4799 | -57.7642 | 122.9545 | 123.1552 | 122.9889 | 66.6281 | -123.5301
3515.7969 | 123.1842 | -65.4419 | 57.637 | -0.010607 | -0.072529 | 0.023112 | -0.004827 | -0.0099374 | 0.012078 | 0.00015261 | 0.043734 | 0.047518 | 0.04158 | 0.13308 | 0.054462 | -0.03558 | 0.05635 | -0.008409 | 0.18032 | 0.10567 | 0.435 | -0.10427 | -65.447 | 1.1908 | 52.6767 | 57.5217 | 57.7133 | 57.547 | -65.8748 | 65.3376 | -57.4567 | 65.4063 | 65.4335 | 0.095859 | -57.5313 | -57.202 | -0.43286 | -0.11529 | -0.005136 | 118.1185 | 118.5514 | 0.076231 | -0.089976 | 65.6222 | 65.5476 | 65.8769 | 65.4982 | -57.7413 | 122.9636 | 123.1551 | 122.9889 | 66.6327 | -123.5118
3516.7969 | 123.1934 | -65.4602 | 57.6233 | -0.0029761 | -0.072743 | 0.022684 | -0.0056818 | -0.0097238 | 0.011865 | -0.0074779 | 0.04352 | 0.046663 | 0.04158 | 0.13351 | 0.054249 | -0.040158 | 0.05635 | -0.003831 | 0.18948 | 0.10567 | 0.42126 | -0.099689 | -65.4425 | 1.2 | 52.5576 | 57.5309 | 57.7224 | 57.5516 | -65.8793 | 65.3605 | -57.4338 | 65.42 | 65.4564 | 0.095858 | -57.5176 | -57.202 | -0.41913 | -0.092404 | 0.017753 | 118.0178 | 118.4369 | 0.099122 | -0.071664 | 65.6497 | 65.5659 | 65.8815 | 65.5166 | -57.723 | 122.9911 | 123.1826 | 123.0118 | 66.6602 | -123.5026
3517.7969 | 123.1842 | -65.4327 | 57.6462 | 0.0046549 | -0.072316 | 0.022684 | -0.004827 | -0.010365 | 0.012292 | 0.0077831 | 0.043947 | 0.04709 | 0.04158 | 0.13286 | 0.054249 | -0.044736 | 0.05635 | -0.003831 | 0.19406 | 0.11025 | 0.42126 | -0.090531 | -65.4379 | 1.2 | 52.521 | 57.5263 | 57.727 | 57.5333 | -65.8748 | 65.3422 | -57.4521 | 65.388 | 65.4289 | 0.0867 | -57.5359 | -57.2249 | -0.44201 | -0.11987 | -0.005135 | 117.9537 | 118.3957 | 0.080812 | -0.11287 | 65.6268 | 65.543 | 65.854 | 65.4891 | -57.7367 | 122.959 | 123.1597 | 122.9661 | 66.6327 | -123.5209
3518.7969 | 123.1934 | -65.4282 | 57.637 | 0.0046549 | -0.072529 | 0.022898 | -0.004827 | -0.0099374 | 0.012292 | -0.0074779 | 0.043734 | 0.04709 | 0.04158 | 0.13286 | 0.054249 | -0.040158 | 0.047193 | -0.003831 | 0.18948 | 0.10567 | 0.40295 | -0.10427 | -65.4425 | 1.2 | 52.4431 | 57.5309 | 57.7224 | 57.5562 | -65.8793 | 65.3239 | -57.4475 | 65.388 | 65.4243 | 0.10044 | -57.5313 | -57.2341 | -0.45117 | -0.10614 | -0.01429 | 117.8713 | 118.3225 | 0.085389 | -0.080818 | 65.6176 | 65.5338 | 65.8311 | 65.4754 | -57.7413 | 122.959 | 123.1506 | 122.9844 | 66.6281 | -123.5164
3519.7969 | 123.2162 | -65.4144 | 57.6691 | 0.0046549 | -0.072316 | 0.022684 | -0.0046134 | -0.0099374 | 0.012506 | 0.00015261 | 0.043307 | 0.046877 | 0.041366 | 0.13244 | 0.054462 | -0.044736 | 0.065507 | 0.000747 | 0.1849 | 0.1011 | 0.41668 | -0.099689 | -65.447 | 1.2 | 52.2691 | 57.5263 | 57.7361 | 57.5333 | -65.8702 | 65.3147 | -57.4842 | 65.3697 | 65.4152 | 0.10044 | -57.568 | -57.2524 | -0.45575 | -0.14276 | -0.032602 | 117.6836 | 118.1393 | 0.067081 | -0.13575 | 65.5993 | 65.5155 | 65.8311 | 65.4799 | -57.7688 | 122.9407 | 123.1506 | 122.9477 | 66.6144 | -123.5392
3520.7969 | 123.1476 | -65.4327 | 57.6416 | 0.0046549 | -0.072743 | 0.022684 | -0.0050408 | -0.010151 | 0.012506 | 0.00015261 | 0.04352 | 0.04709 | 0.04158 | 0.13244 | 0.054462 | -0.049315 | 0.051771 | -0.003831 | 0.18948 | 0.10567 | 0.42126 | -0.099689 | -65.4379 | 1.1954 | 52.1364 | 57.5309 | 57.7316 | 57.5562 | -65.8702 | 65.3331 | -57.4521 | 65.3834 | 65.4289 | 0.095858 | -57.5359 | -57.2203 | -0.43744 | -0.11071 | -0.005135 | 117.5691 | 118.0065 | 0.089968 | -0.085396 | 65.6222 | 65.5384 | 65.854 | 65.4845 | -57.7413 | 122.9636 | 123.1643 | 122.9889 | 66.6281 | -123.5118
3521.7969 | 123.1842 | -65.4419 | 57.6233 | -0.0029761 | -0.072529 | 0.023112 | -0.0050408 | -0.010151 | 0.012506 | 0.015414 | 0.043734 | 0.047304 | 0.041366 | 0.13286 | 0.054462 | -0.044736 | 0.05635 | 0.000747 | 0.17117 | 0.096516 | 0.42126 | -0.099689 | -65.447 | 1.2091 | 52.4111 | 57.5309 | 57.7224 | 57.5425 | -65.8656 | 65.3422 | -57.4521 | 65.3972 | 65.4426 | 0.10044 | -57.5268 | -57.202 | -0.4237 | -0.092404 | -0.005136 | 117.853 | 118.2767 | 0.099122 | -0.080821 | 65.6131 | 65.5384 | 65.8632 | 65.4982 | -57.723 | 122.9728 | 123.1643 | 122.9844 | 66.651 | -123.4889
3522.7969 | 123.1705 | -65.4694 | 57.6416 | -0.0029761 | -0.072316 | 0.022898 | -0.0050408 | -0.0095102 | 0.012292 | 0.00015261 | 0.043947 | 0.046877 | 0.04158 | 0.13308 | 0.054462 | -0.03558 | 0.060928 | -0.003831 | 0.17574 | 0.10567 | 0.42126 | -0.099689 | -65.4425 | 1.2183 | 52.6309 | 57.5309 | 57.7316 | 57.547 | -65.8748 | 65.3697 | -57.4659 | 65.4338 | 65.4655 | 0.095858 | -57.5359 | -57.2203 | -0.40539 | -0.11071 | 0.026908 | 118.1002 | 118.5056 | 0.089968 | -0.094554 | 65.6451 | 65.575 | 65.8906 | 65.5303 | -57.7413 | 123.0002 | 123.2009 | 123.0164 | 66.6877 | -123.5164
3523.7969 | 123.1338 | -65.4602 | 57.637 | -0.0029761 | -0.072743 | 0.022898 | -0.0046134 | -0.010151 | 0.012292 | -0.0074779 | 0.04352 | 0.04709 | 0.041366 | 0.13308 | 0.054249 | -0.03558 | 0.05635 | 0.000747 | 0.19864 | 0.096516 | 0.41668 | -0.09511 | -65.4562 | 1.2137 | 52.5622 | 57.5355 | 57.727 | 57.5425 | -65.8793 | 65.3651 | -57.4384 | 65.4246 | 65.461 | 0.095857 | -57.5405 | -57.2203 | -0.41913 | -0.10156 | 0.004017 | 118.0224 | 118.4415 | 0.089967 | -0.094554 | 65.6588 | 65.5567 | 65.8769 | 65.5166 | -57.7321 | 122.9957 | 123.1872 | 123.0027 | 66.6739 | -123.5164
3524.7969 | 123.1338 | -65.451 | 57.6141 | -0.0029761 | -0.072743 | 0.022684 | -0.004827 | -0.0099374 | 0.011865 | 0.0077831 | 0.043307 | 0.04709 | 0.041366 | 0.13308 | 0.054249 | -0.03558 | 0.051771 | -0.012988 | 0.1849 | 0.10567 | 0.40295 | -0.09511 | -65.4516 | 1.2229 | 52.7087 | 57.54 | 57.7316 | 57.547 | -65.8748 | 65.3559 | -57.4292 | 65.4155 | 65.4381 | 0.082122 | -57.5085 | -57.2112 | -0.4237 | -0.074092 | -0.00056 | 118.1598 | 118.5835 | 0.11743 | -0.067088 | 65.636 | 65.5567 | 65.854 | 65.5028 | -57.7092 | 122.9911 | 123.1826 | 122.9981 | 66.6739 | -123.4889
3525.7969 | 123.1888 | -65.4556 | 57.6599 | -0.010607 | -0.072957 | 0.022684 | -0.0050408 | -0.010365 | 0.012078 | -0.015108 | 0.043734 | 0.047304 | 0.04158 | 0.13265 | 0.054462 | -0.040158 | 0.05635 | -0.003831 | 0.18948 | 0.10567 | 0.39837 | -0.090531 | -65.447 | 1.2275 | 52.4935 | 57.5309 | 57.7316 | 57.5379 | -65.8702 | 65.3651 | -57.4704 | 65.4155 | 65.4518 | 0.0867 | -57.5542 | -57.2615 | -0.41455 | -0.12902 | 0.008596 | 117.9491 | 118.3637 | 0.071658 | -0.12202 | 65.6451 | 65.5613 | 65.854 | 65.512 | -57.7504 | 122.9865 | 123.1872 | 122.9935 | 66.6831 | -123.5301
3526.7969 | 123.1888 | -65.4556 | 57.6462 | -0.0029761 | -0.072743 | 0.023325 | -0.004827 | -0.0099374 | 0.012292 | -0.0074779 | 0.043947 | 0.047304 | 0.04158 | 0.13329 | 0.054249 | -0.040158 | 0.05635 | -0.008409 | 0.1849 | 0.11483 | 0.4121 | -0.090531 | -65.4516 | 1.2275 | 52.4615 | 57.5309 | 57.7361 | 57.547 | -65.8748 | 65.3651 | -57.4613 | 65.4155 | 65.4472 | 0.082122 | -57.5313 | -57.2341 | -0.41913 | -0.11529 | 0.004017 | 117.9171 | 118.3362 | 0.089969 | -0.099131 | 65.6405 | 65.5705 | 65.8677 | 65.512 | -57.7367 | 122.9865 | 123.1918 | 123.0027 | 66.6831 | -123.5209
3527.7969 | 123.175 | -65.451 | 57.6462 | -0.0029761 | -0.072529 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.04352 | 0.04709 | 0.04158 | 0.13265 | 0.054676 | -0.03558 | 0.060928 | -0.012988 | 0.18948 | 0.10567 | 0.41668 | -0.099689 | -65.4516 | 1.232 | 52.521 | 57.5355 | 57.7224 | 57.5608 | -65.8748 | 65.3514 | -57.4567 | 65.4155 | 65.4381 | 0.086701 | -57.5405 | -57.2295 | -0.4237 | -0.11071 | -0.00056 | 117.972 | 118.3957 | 0.076234 | -0.085395 | 65.6405 | 65.5567 | 65.8677 | 65.512 | -57.7459 | 122.9865 | 123.1735 | 123.0118 | 66.6831 | -123.5209
3528.7969 | 123.2758 | -65.4007 | 57.6324 | 0.0046549 | -0.072529 | 0.02247 | -0.0050408 | -0.0099374 | 0.012292 | 0.00015261 | 0.04352 | 0.04709 | 0.041366 | 0.13286 | 0.054676 | -0.044736 | 0.05635 | -0.003831 | 0.18948 | 0.1011 | 0.40295 | -0.09511 | -65.447 | 1.2229 | 52.4386 | 57.5263 | 57.727 | 57.5425 | -65.8748 | 65.3056 | -57.443 | 65.356 | 65.3969 | 0.091279 | -57.5314 | -57.2295 | -0.47406 | -0.10614 | -0.046335 | 117.8393 | 118.3133 | 0.094545 | -0.089976 | 65.5902 | 65.5018 | 65.8036 | 65.457 | -57.7276 | 122.927 | 123.1277 | 122.9432 | 66.6236 | -123.5072
3529.7969 | 123.1613 | -65.4556 | 57.6508 | -0.0029761 | -0.072743 | 0.022898 | -0.0052544 | -0.010151 | 0.012292 | 0.00015261 | 0.043307 | 0.04709 | 0.041366 | 0.13265 | 0.054676 | -0.031001 | 0.051771 | -0.003831 | 0.17574 | 0.096516 | 0.41668 | -0.099689 | -65.4425 | 1.2458 | 52.3882 | 57.5309 | 57.727 | 57.5333 | -65.8748 | 65.3559 | -57.475 | 65.4246 | 65.4518 | 0.095858 | -57.5542 | -57.2341 | -0.41913 | -0.11987 | 0.013175 | 117.8438 | 118.2629 | 0.076234 | -0.11744 | 65.6314 | 65.5521 | 65.8723 | 65.5074 | -57.7504 | 122.9865 | 123.1826 | 122.9889 | 66.7014 | -123.5255
3530.7969 | 123.2895 | -65.4327 | 57.5867 | -0.010607 | -0.072743 | 0.022684 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.043947 | 0.047518 | 0.04158 | 0.13329 | 0.054462 | -0.040158 | 0.051771 | -0.008409 | 0.17117 | 0.10567 | 0.40753 | -0.099689 | -65.4516 | 1.2549 | 53.2215 | 57.5263 | 57.727 | 57.5379 | -65.8793 | 65.3331 | -57.4155 | 65.3926 | 65.4243 | 0.09128 | -57.481 | -57.1791 | -0.44659 | -0.060361 | -0.018871 | 118.6543 | 119.1009 | 0.14032 | -0.048779 | 65.6039 | 65.5384 | 65.8403 | 65.4845 | -57.6864 | 122.959 | 123.1597 | 122.9706 | 66.6877 | -123.466
3531.7969 | 123.143 | -65.4694 | 57.6233 | 0.0046549 | -0.072957 | 0.022684 | -0.0046134 | -0.010151 | 0.012292 | 0.00015261 | 0.043734 | 0.047304 | 0.04158 | 0.13286 | 0.054249 | -0.040158 | 0.047193 | -0.008409 | 0.1849 | 0.10567 | 0.40295 | -0.09511 | -65.4516 | 1.2595 | 52.7499 | 57.5263 | 57.7224 | 57.5379 | -65.8748 | 65.3742 | -57.4384 | 65.4292 | 65.461 | 0.086701 | -57.5176 | -57.2203 | -0.40539 | -0.096982 | 0.01775 | 118.2193 | 118.6247 | 0.099122 | -0.0854 | 65.6543 | 65.575 | 65.8723 | 65.5166 | -57.7184 | 122.9957 | 123.1918 | 123.0073 | 66.7289 | -123.498
3532.7969 | 123.262 | -65.4144 | 57.605 | -0.018238 | -0.072529 | 0.022684 | -0.0050408 | -0.0097238 | 0.012078 | 0.0077831 | 0.043734 | 0.046663 | 0.041153 | 0.13265 | 0.054676 | -0.044736 | 0.051771 | -0.012988 | 0.17574 | 0.10567 | 0.39837 | -0.09511 | -65.447 | 1.2595 | 52.521 | 57.5355 | 57.7316 | 57.5196 | -65.8656 | 65.3193 | -57.4292 | 65.3697 | 65.4014 | 0.082122 | -57.4993 | -57.2066 | -0.45117 | -0.069514 | -0.032602 | 117.9354 | 118.3866 | 0.12659 | -0.085403 | 65.5902 | 65.5201 | 65.8128 | 65.4662 | -57.7001 | 122.9499 | 123.146 | 122.934 | 66.6739 | -123.4706
3533.7969 | 123.2025 | -65.4327 | 57.6279 | -0.0029761 | -0.072957 | 0.022898 | -0.004827 | -0.010151 | 0.011865 | -0.0074779 | 0.04352 | 0.047304 | 0.041366 | 0.13222 | 0.054249 | -0.040158 | 0.047193 | -0.003831 | 0.1849 | 0.11025 | 0.41668 | -0.099689 | -65.447 | 1.2641 | 52.4569 | 57.5309 | 57.7224 | 57.5379 | -65.8702 | 65.3331 | -57.443 | 65.3926 | 65.4289 | 0.095858 | -57.5176 | -57.2112 | -0.43744 | -0.096982 | -0.014292 | 117.8896 | 118.327 | 0.094544 | -0.089978 | 65.6176 | 65.543 | 65.8494 | 65.4799 | -57.7276 | 122.9636 | 123.1552 | 122.9706 | 66.6968 | -123.498
3534.7969 | 123.2758 | -65.419 | 57.6096 | -0.010607 | -0.072529 | 0.022898 | -0.004827 | -0.0097238 | 0.012292 | -0.0074779 | 0.04352 | 0.047304 | 0.041153 | 0.13286 | 0.054462 | -0.040158 | 0.051771 | -0.003831 | 0.18032 | 0.1011 | 0.40295 | -0.090531 | -65.4516 | 1.2732 | 52.7224 | 57.5309 | 57.727 | 57.515 | -65.8793 | 65.3285 | -57.4292 | 65.3788 | 65.4152 | 0.0867 | -57.5085 | -57.2066 | -0.46033 | -0.078671 | -0.032604 | 118.1414 | 118.6018 | 0.11743 | -0.09456 | 65.5993 | 65.5201 | 65.822 | 65.4708 | -57.7001 | 122.9499 | 123.146 | 122.934 | 66.6922 | -123.4889
3535.7969 | 123.2941 | -65.4053 | 57.605 | 0.012286 | -0.072529 | 0.022684 | -0.004827 | -0.010151 | 0.012078 | 0.0077831 | 0.043947 | 0.047304 | 0.04158 | 0.13308 | 0.054249 | -0.044736 | 0.05635 | 0.000747 | 0.1849 | 0.096516 | 0.42126 | -0.09511 | -65.447 | 1.2687 | 52.7545 | 57.5355 | 57.7178 | 57.5425 | -65.8748 | 65.3102 | -57.4201 | 65.3605 | 65.406 | 0.095857 | -57.5085 | -57.1837 | -0.46948 | -0.069514 | -0.041758 | 118.1598 | 118.6292 | 0.11285 | -0.06251 | 65.5902 | 65.5018 | 65.8265 | 65.4616 | -57.7001 | 122.9407 | 123.1231 | 122.9477 | 66.6739 | -123.4797
3536.7969 | 123.2437 | -65.4144 | 57.6233 | -0.010607 | -0.072316 | 0.022898 | -0.0046134 | -0.0097238 | 0.012292 | -0.0074779 | 0.043734 | 0.04709 | 0.04158 | 0.13308 | 0.054676 | -0.044736 | 0.047193 | -0.003831 | 0.18032 | 0.1011 | 0.40295 | -0.09511 | -65.447 | 1.2778 | 52.8781 | 57.5263 | 57.727 | 57.5333 | -65.8793 | 65.3193 | -57.443 | 65.3697 | 65.4106 | 0.091279 | -57.5222 | -57.2203 | -0.4649 | -0.096982 | -0.032602 | 118.2925 | 118.7574 | 0.1037 | -0.089978 | 65.5948 | 65.5155 | 65.8174 | 65.4616 | -57.7184 | 122.9407 | 123.1414 | 122.9477 | 66.6922 | -123.5026
3537.7969 | 123.2758 | -65.4236 | 57.5958 | -0.0029761 | -0.072957 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.00015261 | 0.04352 | 0.04709 | 0.041366 | 0.13308 | 0.054676 | -0.044736 | 0.047193 | 0.000747 | 0.17574 | 0.096516 | 0.40753 | -0.09511 | -65.4562 | 1.287 | 52.8644 | 57.5309 | 57.727 | 57.5379 | -65.8748 | 65.3285 | -57.4201 | 65.3788 | 65.4243 | 0.095857 | -57.4993 | -57.1883 | -0.45117 | -0.064938 | -0.032604 | 118.288 | 118.7391 | 0.13117 | -0.057934 | 65.5993 | 65.5201 | 65.8311 | 65.4708 | -57.6909 | 122.9545 | 123.1506 | 122.9615 | 66.7106 | -123.4706
3538.7969 | 123.2483 | -65.4236 | 57.6279 | -0.0029761 | -0.072743 | 0.022898 | -0.0050408 | -0.010365 | 0.012078 | 0.00015261 | 0.04352 | 0.04709 | 0.04158 | 0.13286 | 0.054462 | -0.044736 | 0.047193 | -0.008409 | 0.17117 | 0.11025 | 0.42126 | -0.09511 | -65.4425 | 1.2778 | 52.8735 | 57.5172 | 57.727 | 57.5425 | -65.8839 | 65.3285 | -57.4567 | 65.3788 | 65.4152 | 0.086701 | -57.5176 | -57.2066 | -0.46033 | -0.11072 | -0.018868 | 118.2971 | 118.7574 | 0.099122 | -0.085399 | 65.5948 | 65.5338 | 65.8448 | 65.4708 | -57.723 | 122.9407 | 123.1506 | 122.9661 | 66.7014 | -123.5118
3539.7969 | 123.2712 | -65.4053 | 57.6141 | 0.0046549 | -0.072957 | 0.022684 | -0.0050408 | -0.010151 | 0.012292 | -0.0074779 | 0.043947 | 0.047304 | 0.04158 | 0.13308 | 0.054249 | -0.040158 | 0.051771 | 0.000747 | 0.1849 | 0.10567 | 0.4121 | -0.099689 | -65.447 | 1.2961 | 53.0063 | 57.5263 | 57.727 | 57.5379 | -65.8748 | 65.3056 | -57.4292 | 65.3651 | 65.406 | 0.10044 | -57.5085 | -57.202 | -0.46948 | -0.087827 | -0.041758 | 118.4116 | 118.8811 | 0.11285 | -0.076245 | 65.5902 | 65.5109 | 65.8174 | 65.457 | -57.7138 | 122.9316 | 123.1323 | 122.9432 | 66.7014 | -123.4889
3540.7969 | 123.2437 | -65.419 | 57.6187 | -0.010607 | -0.072743 | 0.02247 | -0.0052544 | -0.0099374 | 0.012506 | 0.0077831 | 0.043734 | 0.046877 | 0.04158 | 0.13308 | 0.054249 | -0.044736 | 0.047193 | -0.008409 | 0.18948 | 0.11025 | 0.41668 | -0.090531 | -65.4516 | 1.287 | 52.8964 | 57.5263 | 57.727 | 57.5654 | -65.8748 | 65.3285 | -57.4292 | 65.3743 | 65.4106 | 0.082122 | -57.5085 | -57.202 | -0.45575 | -0.092404 | -0.032604 | 118.3154 | 118.7712 | 0.10828 | -0.05335 | 65.6085 | 65.5293 | 65.8357 | 65.4662 | -57.7092 | 122.9453 | 123.146 | 122.9844 | 66.706 | -123.4935
3541.7969 | 123.2437 | -65.3961 | 57.6233 | -0.010607 | -0.072957 | 0.022898 | -0.0052544 | -0.010151 | 0.012292 | -0.0074779 | 0.043734 | 0.04709 | 0.040939 | 0.13308 | 0.054249 | -0.040158 | 0.05635 | -0.017566 | 0.18032 | 0.10567 | 0.40753 | -0.099689 | -65.4516 | 1.2961 | 52.8049 | 57.5309 | 57.7224 | 57.547 | -65.8793 | 65.2964 | -57.443 | 65.356 | 65.3786 | 0.082123 | -57.5176 | -57.2158 | -0.48322 | -0.092404 | -0.055492 | 118.201 | 118.6842 | 0.099122 | -0.076243 | 65.5764 | 65.5018 | 65.8036 | 65.4525 | -57.723 | 122.927 | 123.1185 | 122.9432 | 66.6923 | -123.5026
3542.7969 | 123.2803 | -65.3961 | 57.6508 | 0.0046549 | -0.07317 | 0.022898 | -0.004827 | -0.010151 | 0.012292 | 0.0077831 | 0.04352 | 0.04709 | 0.041153 | 0.13286 | 0.054676 | -0.044736 | 0.05635 | -0.008409 | 0.17117 | 0.1011 | 0.39837 | -0.090531 | -65.4516 | 1.3007 | 52.8461 | 57.5309 | 57.727 | 57.5333 | -65.8748 | 65.3056 | -57.4796 | 65.3514 | 65.3877 | 0.082122 | -57.5497 | -57.2524 | -0.47864 | -0.11987 | -0.055492 | 118.2422 | 118.7208 | 0.076234 | -0.11744 | 65.5673 | 65.4972 | 65.7945 | 65.4525 | -57.7413 | 122.927 | 123.1231 | 122.9294 | 66.6968 | -123.5255
3543.7969 | 123.3444 | -65.419 | 57.6233 | 0.0046549 | -0.072743 | 0.022684 | -0.0046134 | -0.0097238 | 0.011865 | 0.00015261 | 0.04352 | 0.04709 | 0.041366 | 0.13308 | 0.054035 | -0.049315 | 0.05635 | -0.003831 | 0.18948 | 0.096516 | 0.4121 | -0.099689 | -65.4562 | 1.2961 | 52.8415 | 57.5355 | 57.7316 | 57.5287 | -65.8839 | 65.3193 | -57.4338 | 65.3697 | 65.4152 | 0.095858 | -57.5268 | -57.2112 | -0.46491 | -0.087825 | -0.037182 | 118.2605 | 118.7254 | 0.10828 | -0.094557 | 65.6085 | 65.5155 | 65.8311 | 65.4754 | -57.723 | 122.9545 | 123.1506 | 122.9477 | 66.7151 | -123.5072
3544.7969 | 123.3124 | -65.3915 | 57.6324 | 0.0046549 | -0.072957 | 0.022684 | -0.0050408 | -0.010578 | 0.012292 | 0.00015261 | 0.043734 | 0.047304 | 0.041153 | 0.13329 | 0.054462 | -0.040158 | 0.047193 | -0.008409 | 0.1849 | 0.11025 | 0.42126 | -0.10427 | -65.447 | 1.3053 | 52.8827 | 57.5263 | 57.7224 | 57.5425 | -65.8793 | 65.2873 | -57.4475 | 65.3514 | 65.3831 | 0.095859 | -57.5222 | -57.2112 | -0.48779 | -0.10614 | -0.05549 | 118.2742 | 118.762 | 0.089967 | -0.089976 | 65.5764 | 65.5018 | 65.8128 | 65.4387 | -57.7367 | 122.9179 | 123.114 | 122.934 | 66.6968 | -123.5118
3545.7969 | 123.2346 | -65.4099 | 57.6187 | -0.010607 | -0.072529 | 0.023112 | -0.0052544 | -0.0097238 | 0.012078 | 0.00015261 | 0.04352 | 0.04709 | 0.04158 | 0.13265 | 0.054462 | -0.040158 | 0.05635 | 0.005325 | 0.16659 | 0.10567 | 0.4121 | -0.09511 | -65.447 | 1.3053 | 52.7865 | 57.5309 | 57.7224 | 57.5425 | -65.8793 | 65.3147 | -57.4521 | 65.3697 | 65.4152 | 0.10043 | -57.513 | -57.2066 | -0.46948 | -0.087826 | -0.03718 | 118.1964 | 118.6659 | 0.1037 | -0.076243 | 65.5764 | 65.5155 | 65.822 | 65.4662 | -57.7138 | 122.9407 | 123.1323 | 122.9523 | 66.7151 | -123.498
3546.7969 | 123.2941 | -65.4007 | 57.6462 | -0.018238 | -0.07317 | 0.022898 | -0.0050408 | -0.010365 | 0.012078 | 0.015414 | 0.04352 | 0.04709 | 0.041366 | 0.13265 | 0.054462 | -0.049315 | 0.051771 | -0.008409 | 0.17117 | 0.1011 | 0.40753 | -0.090531 | -65.447 | 1.3099 | 52.7316 | 57.5309 | 57.727 | 57.547 | -65.8748 | 65.3102 | -57.475 | 65.3514 | 65.3923 | 0.082122 | -57.5451 | -57.2387 | -0.47406 | -0.11529 | -0.046335 | 118.1323 | 118.6063 | 0.080812 | -0.099131 | 65.5719 | 65.5018 | 65.8082 | 65.4525 | -57.7367 | 122.9316 | 123.1277 | 122.9477 | 66.7106 | -123.5209
3547.7969 | 123.2758 | -65.4053 | 57.6324 | -0.0029761 | -0.072957 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.0077831 | 0.043734 | 0.04709 | 0.041153 | 0.13308 | 0.054676 | -0.049315 | 0.05635 | -0.012988 | 0.18948 | 0.1011 | 0.39379 | -0.09511 | -65.447 | 1.3144 | 52.6721 | 57.5355 | 57.7316 | 57.5333 | -65.8748 | 65.3102 | -57.443 | 65.356 | 65.3923 | 0.082122 | -57.5314 | -57.2387 | -0.46948 | -0.09698 | -0.041758 | 118.0773 | 118.5468 | 0.099124 | -0.099133 | 65.5948 | 65.5064 | 65.7991 | 65.4616 | -57.7276 | 122.9407 | 123.1368 | 122.9386 | 66.7197 | -123.5072
3548.7969 | 123.2574 | -65.3687 | 57.6691 | 0.0046549 | -0.072743 | 0.023112 | -0.0050408 | -0.010151 | 0.011865 | 0.00015261 | 0.043734 | 0.046877 | 0.041153 | 0.13265 | 0.054249 | -0.044736 | 0.051771 | -0.017566 | 0.17117 | 0.096516 | 0.42126 | -0.090531 | -65.447 | 1.319 | 52.9056 | 57.5355 | 57.727 | 57.5287 | -65.8793 | 65.2781 | -57.4979 | 65.3239 | 65.3511 | 0.072965 | -57.5726 | -57.2478 | -0.51068 | -0.1336 | -0.078379 | 118.2742 | 118.7849 | 0.057924 | -0.14033 | 65.5398 | 65.4652 | 65.7899 | 65.4204 | -57.7596 | 122.9041 | 123.0956 | 122.8974 | 66.6877 | -123.5484
3549.7969 | 123.175 | -65.4327 | 57.6828 | 0.0046549 | -0.072957 | 0.022898 | -0.0046134 | -0.010365 | 0.012078 | 0.00015261 | 0.043734 | 0.046877 | 0.04158 | 0.13308 | 0.054462 | -0.03558 | 0.051771 | -0.008409 | 0.19406 | 0.11025 | 0.42584 | -0.099689 | -65.4516 | 1.3282 | 53.0704 | 57.5263 | 57.7224 | 57.5608 | -65.8839 | 65.3331 | -57.4887 | 65.3972 | 65.4243 | 0.09128 | -57.5725 | -57.257 | -0.45117 | -0.15649 | -0.018871 | 118.5032 | 118.9543 | 0.039613 | -0.12202 | 65.6268 | 65.543 | 65.8586 | 65.4845 | -57.7825 | 122.959 | 123.1552 | 122.9935 | 66.7609 | -123.5667
3550.7969 | 123.1613 | -65.4373 | 57.6508 | 0.0046549 | -0.07317 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.043307 | 0.04709 | 0.04158 | 0.13308 | 0.054676 | -0.044736 | 0.05635 | 0.000747 | 0.1849 | 0.096516 | 0.40753 | -0.099689 | -65.4516 | 1.3328 | 53.1391 | 57.5263 | 57.7133 | 57.5333 | -65.8839 | 65.3376 | -57.4659 | 65.3926 | 65.4381 | 0.10044 | -57.5542 | -57.2432 | -0.4466 | -0.12445 | -0.014293 | 118.5764 | 119.023 | 0.062498 | -0.11744 | 65.6222 | 65.5338 | 65.8448 | 65.4937 | -57.7504 | 122.9636 | 123.1506 | 122.9706 | 66.7701 | -123.5347
3551.7969 | 123.317 | -65.4236 | 57.6096 | -0.0029761 | -0.07317 | 0.022898 | -0.0050408 | -0.010151 | 0.012078 | 0.00015261 | 0.043734 | 0.047304 | 0.041366 | 0.13308 | 0.054462 | -0.040158 | 0.051771 | -0.003831 | 0.18032 | 0.096516 | 0.42126 | -0.090531 | -65.4562 | 1.3328 | 53.2627 | 57.5263 | 57.7224 | 57.515 | -65.8885 | 65.3331 | -57.4292 | 65.3834 | 65.4198 | 0.0867 | -57.513 | -57.1883 | -0.46491 | -0.083249 | -0.032604 | 118.6863 | 119.1512 | 0.11286 | -0.09456 | 65.6039 | 65.5201 | 65.8448 | 65.4754 | -57.7001 | 122.9499 | 123.146 | 122.9386 | 66.7563 | -123.498
3552.7969 | 123.2117 | -65.4327 | 57.6416 | -0.0029761 | -0.072743 | 0.022684 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | 0.043734 | 0.047304 | 0.041366 | 0.13351 | 0.054462 | -0.040158 | 0.051771 | -0.008409 | 0.17574 | 0.11025 | 0.39837 | -0.10885 | -65.4562 | 1.3328 | 53.2673 | 57.5217 | 57.727 | 57.5425 | -65.8885 | 65.3239 | -57.4659 | 65.3926 | 65.4243 | 0.10044 | -57.5313 | -57.2432 | -0.45575 | -0.11987 | -0.023449 | 118.7 | 119.1558 | 0.085389 | -0.099132 | 65.6085 | 65.543 | 65.8311 | 65.4845 | -57.7504 | 122.9545 | 123.1597 | 122.9752 | 66.7655 | -123.5301
3553.7969 | 123.262 | -65.4007 | 57.6508 | -0.0029761 | -0.072743 | 0.022684 | -0.004827 | -0.0097238 | 0.012078 | 0.0077831 | 0.043734 | 0.04709 | 0.041366 | 0.13329 | 0.054249 | -0.044736 | 0.051771 | -0.012988 | 0.16659 | 0.11483 | 0.4121 | -0.09511 | -65.4516 | 1.3328 | 53.162 | 57.5263 | 57.727 | 57.5745 | -65.8793 | 65.3056 | -57.4842 | 65.356 | 65.3877 | 0.082122 | -57.5359 | -57.2387 | -0.47864 | -0.12445 | -0.050914 | 118.5627 | 119.0413 | 0.076234 | -0.076237 | 65.5673 | 65.5155 | 65.8128 | 65.4525 | -57.7459 | 122.927 | 123.1277 | 122.9752 | 66.7335 | -123.5301
3554.7969 | 123.1842 | -65.4648 | 57.6462 | 0.0046549 | -0.072957 | 0.022684 | -0.004827 | -0.0099374 | 0.012292 | 0.0077831 | 0.043734 | 0.046877 | 0.041153 | 0.13308 | 0.054249 | -0.03558 | 0.05635 | -0.008409 | 0.18032 | 0.10567 | 0.42126 | -0.099689 | -65.4608 | 1.3373 | 53.1162 | 57.5355 | 57.7224 | 57.547 | -65.8839 | 65.3651 | -57.4659 | 65.4292 | 65.4564 | 0.09128 | -57.5405 | -57.2249 | -0.41913 | -0.11071 | 0.004016 | 118.581 | 119.0001 | 0.076234 | -0.099131 | 65.6451 | 65.5705 | 65.886 | 65.5211 | -57.7459 | 123.0002 | 123.1872 | 123.0118 | 66.8021 | -123.5301
3555.7969 | 123.2529 | -65.419 | 57.6462 | 0.0046549 | -0.072957 | 0.022898 | -0.004827 | -0.0099374 | 0.012078 | 0.0077831 | 0.043734 | 0.04709 | 0.041366 | 0.13308 | 0.054249 | -0.040158 | 0.051771 | -0.003831 | 0.1849 | 0.11025 | 0.42126 | -0.099689 | -65.4516 | 1.3282 | 53.1895 | 57.5355 | 57.7224 | 57.5333 | -65.8839 | 65.3193 | -57.4613 | 65.3788 | 65.4152 | 0.095858 | -57.5359 | -57.2249 | -0.46491 | -0.11071 | -0.032604 | 118.6085 | 119.0734 | 0.076234 | -0.11287 | 65.6039 | 65.5293 | 65.8403 | 65.4708 | -57.7459 | 122.9545 | 123.1414 | 122.9523 | 66.7472 | -123.5301
3556.7969 | 123.2162 | -65.4282 | 57.6462 | -0.0029761 | -0.072957 | 0.022257 | -0.0050408 | -0.0099374 | 0.011865 | 0.00015261 | 0.043307 | 0.046877 | 0.041153 | 0.13308 | 0.054249 | -0.044736 | 0.05635 | 0.005325 | 0.17574 | 0.10567 | 0.42126 | -0.10885 | -65.4608 | 1.3465 | 53.2124 | 57.5263 | 57.7133 | 57.5333 | -65.8839 | 65.3193 | -57.4704 | 65.3834 | 65.4335 | 0.11417 | -57.5405 | -57.2249 | -0.45575 | -0.11987 | -0.032605 | 118.6405 | 119.0963 | 0.067076 | -0.11287 | 65.6039 | 65.5338 | 65.8494 | 65.4845 | -57.755 | 122.9545 | 123.1414 | 122.9615 | 66.7747 | -123.5301
3557.7969 | 123.0789 | -65.4327 | 57.6736 | 0.0046549 | -0.072743 | 0.022684 | -0.0046134 | -0.0099374 | 0.012292 | -0.015108 | 0.043307 | 0.046877 | 0.041366 | 0.13286 | 0.054249 | -0.044736 | 0.051771 | 0.000747 | 0.17574 | 0.1011 | 0.41668 | -0.11342 | -65.4516 | 1.3557 | 53.3314 | 57.5263 | 57.7178 | 57.5516 | -65.8839 | 65.3193 | -57.4979 | 65.388 | 65.4335 | 0.11417 | -57.5725 | -57.257 | -0.45117 | -0.14734 | -0.018871 | 118.7641 | 119.2153 | 0.044189 | -0.12202 | 65.6085 | 65.5338 | 65.8494 | 65.4845 | -57.7871 | 122.959 | 123.1506 | 122.9844 | 66.7884 | -123.5576
3558.8594 | 123.1659 | -65.4556 | 57.6462 | -0.0029761 | -0.072529 | 0.022684 | -0.004827 | -0.010151 | 0.012506 | 0.00015261 | 0.043947 | 0.046663 | 0.041794 | 0.13308 | 0.054462 | -0.040158 | 0.05635 | -0.003831 | 0.19864 | 0.11025 | 0.4121 | -0.099689 | -65.4562 | 1.3557 | 53.4459 | 57.5263 | 57.7133 | 57.5516 | -65.8839 | 65.3559 | -57.4475 | 65.4155 | 65.4518 | 0.095858 | -57.5359 | -57.2341 | -0.42828 | -0.11987 | -0.000561 | 118.9015 | 119.3298 | 0.067076 | -0.094552 | 65.6543 | 65.5659 | 65.8677 | 65.512 | -57.7459 | 122.9819 | 123.1689 | 123.0073 | 66.8113 | -123.5301
3559.7969 | 123.1842 | -65.451 | 57.6508 | 0.0046549 | -0.072529 | 0.022684 | -0.0050408 | -0.010151 | 0.012506 | 0.015414 | 0.04352 | 0.04709 | 0.041153 | 0.13329 | 0.054462 | -0.040158 | 0.047193 | -0.003831 | 0.18032 | 0.11025 | 0.39837 | -0.118 | -65.447 | 1.3511 | 53.3543 | 57.5309 | 57.7133 | 57.5425 | -65.8793 | 65.333 | -57.4704 | 65.4109 | 65.4472 | 0.11417 | -57.5405 | -57.2524 | -0.42828 | -0.11987 | 0.004019 | 118.8053 | 119.2336 | 0.062498 | -0.10829 | 65.6314 | 65.5613 | 65.8494 | 65.4982 | -57.7688 | 122.9819 | 123.1643 | 122.9935 | 66.8021 | -123.5301
3560.7969 | 123.2071 | -65.4373 | 57.6279 | 0.0046549 | -0.072529 | 0.022898 | -0.004827 | -0.0097238 | 0.012506 | -0.0074779 | 0.043734 | 0.047304 | 0.041153 | 0.13286 | 0.054035 | -0.044736 | 0.047193 | -0.003831 | 0.1849 | 0.096516 | 0.42584 | -0.10427 | -65.4516 | 1.3602 | 53.281 | 57.5263 | 57.727 | 57.5516 | -65.8839 | 65.333 | -57.443 | 65.3926 | 65.4335 | 0.10044 | -57.5314 | -57.202 | -0.4466 | -0.10156 | -0.014293 | 118.7184 | 119.165 | 0.099122 | -0.076242 | 65.6222 | 65.5338 | 65.8632 | 65.4845 | -57.7321 | 122.9636 | 123.1643 | 122.9889 | 66.7976 | -123.5118
3561.7969 | 123.1613 | -65.4465 | 57.6324 | 0.0046549 | -0.072957 | 0.022684 | -0.004827 | -0.010365 | 0.012078 | 0.00015261 | 0.04352 | 0.047304 | 0.041366 | 0.13308 | 0.054462 | -0.03558 | 0.05635 | 0.000747 | 0.18032 | 0.10567 | 0.40295 | -0.09511 | -65.4516 | 1.3602 | 53.3177 | 57.5126 | 57.7224 | 57.5425 | -65.8748 | 65.3514 | -57.4521 | 65.4109 | 65.4472 | 0.095857 | -57.5268 | -57.2295 | -0.42828 | -0.11987 | -0.005138 | 118.7641 | 119.1924 | 0.089967 | -0.089976 | 65.6268 | 65.5521 | 65.8494 | 65.5028 | -57.7276 | 122.959 | 123.1689 | 122.9889 | 66.8067 | -123.5072
3562.7969 | 123.1842 | -65.4602 | 57.6233 | -0.0029761 | -0.072529 | 0.02247 | -0.004827 | -0.0099374 | 0.012078 | 0.015414 | 0.043307 | 0.04709 | 0.041794 | 0.13308 | 0.054462 | -0.044736 | 0.05635 | -0.008409 | 0.18948 | 0.10567 | 0.42126 | -0.10885 | -65.4653 | 1.3648 | 53.423 | 57.5126 | 57.7178 | 57.5058 | -65.8931 | 65.3514 | -57.4338 | 65.4155 | 65.4518 | 0.10044 | -57.5176 | -57.202 | -0.43286 | -0.11072 | -0.005141 | 118.8832 | 119.316 | 0.094543 | -0.11745 | 65.6497 | 65.5659 | 65.8815 | 65.5166 | -57.7321 | 122.9728 | 123.178 | 122.966 | 66.825 | -123.5164
3563.7969 | 123.2574 | -65.419 | 57.5821 | -0.010607 | -0.072529 | 0.02247 | -0.0050408 | -0.0097238 | 0.012078 | 0.0077831 | 0.04352 | 0.046877 | 0.041153 | 0.13308 | 0.054035 | -0.03558 | 0.047193 | -0.003831 | 0.18032 | 0.096516 | 0.40753 | -0.09511 | -65.4516 | 1.374 | 53.716 | 57.5263 | 57.7133 | 57.5379 | -65.8839 | 65.3239 | -57.4018 | 65.3834 | 65.4152 | 0.091279 | -57.4856 | -57.1746 | -0.46491 | -0.055783 | -0.032604 | 119.135 | 119.5999 | 0.13116 | -0.044201 | 65.5993 | 65.5155 | 65.8265 | 65.4662 | -57.6772 | 122.9453 | 123.1323 | 122.9569 | 66.793 | -123.466
3564.7969 | 123.1476 | -65.451 | 57.6416 | 0.0046549 | -0.07317 | 0.022898 | -0.004827 | -0.010151 | 0.012078 | 0.00015261 | 0.043734 | 0.046663 | 0.041366 | 0.13351 | 0.054462 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.11483 | 0.42584 | -0.099689 | -65.4608 | 1.3786 | 53.7526 | 57.5263 | 57.7178 | 57.5287 | -65.8839 | 65.3514 | -57.4567 | 65.4017 | 65.4472 | 0.095858 | -57.5268 | -57.2158 | -0.43286 | -0.11529 | -0.009717 | 119.2037 | 119.6366 | 0.076232 | -0.11287 | 65.636 | 65.5659 | 65.8769 | 65.5028 | -57.7413 | 122.9774 | 123.1689 | 122.9798 | 66.8296 | -123.5255
3565.7969 | 123.1888 | -65.4602 | 57.6462 | -0.010607 | -0.072957 | 0.02247 | -0.0050408 | -0.0099374 | 0.011865 | 0.0077831 | 0.04352 | 0.047304 | 0.041366 | 0.13329 | 0.054249 | -0.03558 | 0.047193 | -0.008409 | 0.19406 | 0.11025 | 0.40295 | -0.09511 | -65.4653 | 1.3831 | 53.6931 | 57.5263 | 57.7133 | 57.5242 | -65.8885 | 65.3651 | -57.4521 | 65.4246 | 65.4518 | 0.086701 | -57.5359 | -57.2432 | -0.42829 | -0.11987 | -0.005141 | 119.1533 | 119.5816 | 0.067076 | -0.12202 | 65.6543 | 65.5705 | 65.8632 | 65.5074 | -57.7413 | 122.9865 | 123.1735 | 122.9844 | 66.8433 | -123.5347
3566.7969 | 123.2162 | -65.4419 | 57.637 | -0.010607 | -0.072743 | 0.022898 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.04352 | 0.046877 | 0.041153 | 0.13308 | 0.054249 | -0.044736 | 0.042614 | -0.008409 | 0.16659 | 0.1011 | 0.41668 | -0.090531 | -65.4608 | 1.3831 | 53.5558 | 57.5263 | 57.727 | 57.515 | -65.8793 | 65.3514 | -57.4704 | 65.3972 | 65.4335 | 0.082122 | -57.5359 | -57.2203 | -0.43744 | -0.11071 | -0.018872 | 118.9977 | 119.4351 | 0.089967 | -0.12203 | 65.6085 | 65.543 | 65.8586 | 65.4845 | -57.7276 | 122.9682 | 123.1689 | 122.9569 | 66.825 | -123.5164
3567.7969 | 123.2025 | -65.4556 | 57.6324 | 0.0046549 | -0.072957 | 0.022684 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.044161 | 0.047518 | 0.041366 | 0.13351 | 0.054462 | -0.031001 | 0.05635 | -0.012988 | 0.17117 | 0.1011 | 0.435 | -0.09511 | -65.4562 | 1.3877 | 53.4733 | 57.5172 | 57.7178 | 57.5516 | -65.8793 | 65.3605 | -57.4613 | 65.4246 | 65.4426 | 0.082122 | -57.5314 | -57.1974 | -0.42371 | -0.11529 | -0.000561 | 118.929 | 119.3527 | 0.085388 | -0.080819 | 65.6268 | 65.5567 | 65.8906 | 65.512 | -57.7276 | 122.9728 | 123.1735 | 123.0073 | 66.8433 | -123.5118
3568.7969 | 123.2162 | -65.4007 | 57.6141 | -0.0029761 | -0.072957 | 0.022684 | -0.0052544 | -0.010151 | 0.012719 | 0.0077831 | 0.04352 | 0.047304 | 0.041153 | 0.13308 | 0.054035 | -0.03558 | 0.051771 | -0.003831 | 0.16201 | 0.1011 | 0.39837 | -0.09511 | -65.4608 | 1.3877 | 53.3726 | 57.5263 | 57.7224 | 57.547 | -65.8839 | 65.3056 | -57.4521 | 65.3651 | 65.3969 | 0.091279 | -57.513 | -57.2158 | -0.48322 | -0.087827 | -0.060071 | 118.7733 | 119.2565 | 0.10828 | -0.067088 | 65.5627 | 65.5018 | 65.7991 | 65.4525 | -57.7092 | 122.927 | 123.1231 | 122.9477 | 66.7884 | -123.498
3569.7969 | 123.2071 | -65.4373 | 57.637 | 0.0046549 | -0.072743 | 0.022684 | -0.0050408 | -0.0099374 | 0.011865 | 0.00015261 | 0.04352 | 0.046877 | 0.04158 | 0.13308 | 0.054249 | -0.040158 | 0.051771 | -0.008409 | 0.18032 | 0.1011 | 0.41668 | -0.10427 | -65.4562 | 1.4014 | 53.4001 | 57.5217 | 57.7178 | 57.515 | -65.8839 | 65.333 | -57.4567 | 65.3972 | 65.4289 | 0.095859 | -57.5359 | -57.2203 | -0.4466 | -0.11529 | -0.018871 | 118.8374 | 119.284 | 0.08081 | -0.12203 | 65.6176 | 65.5384 | 65.854 | 65.4891 | -57.7413 | 122.959 | 123.1552 | 122.9523 | 66.8388 | -123.5209
3570.7969 | 123.2529 | -65.4465 | 57.5958 | -0.0029761 | -0.072957 | 0.022898 | -0.0050408 | -0.010151 | 0.012292 | -0.0074779 | 0.043734 | 0.04709 | 0.041153 | 0.13329 | 0.054462 | -0.049315 | 0.047193 | -0.003831 | 0.18032 | 0.1011 | 0.4121 | -0.090531 | -65.4608 | 1.406 | 53.4367 | 57.5263 | 57.7178 | 57.5379 | -65.8839 | 65.3559 | -57.4155 | 65.3972 | 65.4426 | 0.0867 | -57.4947 | -57.1837 | -0.43744 | -0.069516 | -0.014295 | 118.8832 | 119.3206 | 0.12201 | -0.057934 | 65.6268 | 65.5476 | 65.8586 | 65.4937 | -57.6864 | 122.9728 | 123.1643 | 122.9844 | 66.8525 | -123.4797
3571.7969 | 123.1796 | -65.4648 | 57.6416 | -0.018238 | -0.07317 | 0.022684 | -0.0052544 | -0.010365 | 0.011865 | 0.0077831 | 0.043307 | 0.04709 | 0.041153 | 0.13329 | 0.054462 | -0.03558 | 0.05635 | -0.003831 | 0.18032 | 0.10567 | 0.41668 | -0.090531 | -65.4608 | 1.4106 | 53.5146 | 57.5217 | 57.7224 | 57.5242 | -65.8885 | 65.3743 | -57.4613 | 65.4292 | 65.461 | 0.0867 | -57.5359 | -57.2249 | -0.42371 | -0.11987 | 0.004016 | 118.9793 | 119.403 | 0.080811 | -0.11745 | 65.6451 | 65.5705 | 65.8815 | 65.5211 | -57.7321 | 122.9865 | 123.1872 | 122.9889 | 66.8754 | -123.5301
3572.7969 | 123.1659 | -65.4556 | 57.6508 | -0.010607 | -0.07317 | 0.022684 | -0.0050408 | -0.0099374 | 0.011651 | 0.00015261 | 0.043947 | 0.04709 | 0.041366 | 0.13286 | 0.054462 | -0.044736 | 0.05635 | 0.005325 | 0.19406 | 0.10567 | 0.40753 | -0.10427 | -65.4608 | 1.406 | 53.5924 | 57.5217 | 57.7224 | 57.5379 | -65.8931 | 65.3514 | -57.4567 | 65.4109 | 65.461 | 0.10959 | -57.5451 | -57.2432 | -0.43744 | -0.12903 | -0.00514 | 119.048 | 119.4855 | 0.071656 | -0.11287 | 65.6497 | 65.5613 | 65.8632 | 65.512 | -57.755 | 122.9774 | 123.178 | 122.9935 | 66.8617 | -123.5438
3573.7969 | 123.2666 | -65.4236 | 57.5958 | -0.010607 | -0.072957 | 0.02247 | -0.0052544 | -0.0099374 | 0.012506 | -0.0074779 | 0.04352 | 0.047304 | 0.041366 | 0.13286 | 0.054035 | -0.044736 | 0.051771 | 0.000747 | 0.1849 | 0.096516 | 0.40753 | -0.085952 | -65.4608 | 1.4106 | 53.7801 | 57.5263 | 57.727 | 57.5287 | -65.8885 | 65.3376 | -57.4109 | 65.3788 | 65.4243 | 0.086699 | -57.4993 | -57.1883 | -0.46491 | -0.069516 | -0.037183 | 119.2037 | 119.6686 | 0.13117 | -0.067091 | 65.6085 | 65.5201 | 65.8311 | 65.4754 | -57.6818 | 122.9499 | 123.1506 | 122.9523 | 66.8342 | -123.4843
3574.7969 | 123.1567 | -65.451 | 57.637 | -0.010607 | -0.072743 | 0.02247 | -0.0046134 | -0.0097238 | 0.012292 | -0.0074779 | 0.043734 | 0.046877 | 0.041366 | 0.13329 | 0.054035 | -0.044736 | 0.051771 | 0.000747 | 0.17117 | 0.10567 | 0.4121 | -0.099689 | -65.4562 | 1.4106 | 53.8534 | 57.5172 | 57.7133 | 57.547 | -65.8839 | 65.3514 | -57.4659 | 65.4063 | 65.4518 | 0.10044 | -57.5313 | -57.2249 | -0.43286 | -0.11987 | -0.005138 | 119.3044 | 119.7373 | 0.076231 | -0.089976 | 65.6222 | 65.5567 | 65.8632 | 65.5028 | -57.7367 | 122.9682 | 123.1643 | 122.9981 | 66.8617 | -123.5209
3575.8594 | 123.2117 | -65.4602 | 57.637 | 0.0046549 | -0.07317 | 0.022684 | -0.004827 | -0.0099374 | 0.011651 | 0.00015261 | 0.04352 | 0.046877 | 0.041366 | 0.13329 | 0.054462 | -0.044736 | 0.047193 | 0.000747 | 0.18032 | 0.10567 | 0.41668 | -0.09511 | -65.4562 | 1.4198 | 53.8717 | 57.5217 | 57.7178 | 57.5333 | -65.8885 | 65.3651 | -57.4567 | 65.4155 | 65.461 | 0.095857 | -57.5313 | -57.2203 | -0.42829 | -0.11529 | 0.004017 | 119.3319 | 119.7602 | 0.08081 | -0.10371 | 65.6405 | 65.5659 | 65.8769 | 65.5074 | -57.7321 | 122.9819 | 123.178 | 122.9935 | 66.88 | -123.5255
3576.7969 | 123.1705 | -65.4739 | 57.6279 | -0.0029761 | -0.072957 | 0.02247 | -0.0050408 | -0.0099374 | 0.012078 | 0.00015261 | 0.04352 | 0.04709 | 0.041366 | 0.13308 | 0.054249 | -0.040158 | 0.051771 | -0.003831 | 0.18948 | 0.1011 | 0.41668 | -0.09511 | -65.4562 | 1.4198 | 53.7526 | 57.5309 | 57.727 | 57.5333 | -65.8839 | 65.3788 | -57.4384 | 65.4338 | 65.4701 | 0.091279 | -57.5268 | -57.2112 | -0.40997 | -0.096982 | 0.01775 | 119.2266 | 119.6366 | 0.099122 | -0.094556 | 65.6634 | 65.575 | 65.8906 | 65.5257 | -57.723 | 123.0048 | 123.2009 | 123.0073 | 66.8937 | -123.5118
3577.7969 | 123.1613 | -65.4419 | 57.6416 | -0.0029761 | -0.07317 | 0.022043 | -0.0046134 | -0.010151 | 0.012078 | -0.0074779 | 0.043734 | 0.046877 | 0.04158 | 0.13308 | 0.054462 | -0.040158 | 0.051771 | -0.003831 | 0.1849 | 0.1011 | 0.4121 | -0.09511 | -65.4562 | 1.4198 | 53.7343 | 57.5263 | 57.7224 | 57.5196 | -65.8885 | 65.3468 | -57.4567 | 65.4017 | 65.4381 | 0.091279 | -57.5405 | -57.2295 | -0.4466 | -0.11529 | -0.014293 | 119.1762 | 119.6228 | 0.080811 | -0.12203 | 65.6268 | 65.543 | 65.854 | 65.4937 | -57.7367 | 122.9682 | 123.1643 | 122.9615 | 66.8617 | -123.5301
3578.7969 | 123.2758 | -65.4144 | 57.5958 | -0.010607 | -0.072743 | 0.02247 | -0.0056818 | -0.010151 | 0.012506 | 0.0077831 | 0.043734 | 0.04709 | 0.041153 | 0.13329 | 0.054035 | -0.040158 | 0.047193 | 0.000747 | 0.1849 | 0.1011 | 0.4121 | -0.090531 | -65.4562 | 1.4198 | 53.7389 | 57.5309 | 57.7178 | 57.5333 | -65.8931 | 65.3239 | -57.4109 | 65.3743 | 65.4152 | 0.091278 | -57.4947 | -57.1837 | -0.47864 | -0.064938 | -0.041759 | 119.1533 | 119.632 | 0.12201 | -0.062512 | 65.5993 | 65.5155 | 65.8265 | 65.4616 | -57.6864 | 122.9453 | 123.1323 | 122.9477 | 66.8342 | -123.4889
3579.7969 | 123.2483 | -65.451 | 57.6233 | -0.0029761 | -0.07317 | 0.02247 | -0.004827 | -0.010365 | 0.012292 | 0.0077831 | 0.043734 | 0.046877 | 0.041153 | 0.13308 | 0.054249 | -0.040158 | 0.05635 | 0.000747 | 0.1849 | 0.11025 | 0.4121 | -0.09511 | -65.4562 | 1.4381 | 53.8076 | 57.5263 | 57.7178 | 57.5333 | -65.8885 | 65.3559 | -57.4384 | 65.4109 | 65.4518 | 0.095857 | -57.513 | -57.2112 | -0.43744 | -0.096982 | -0.005138 | 119.2586 | 119.6961 | 0.094543 | -0.089978 | 65.636 | 65.5613 | 65.8632 | 65.5074 | -57.7184 | 122.9774 | 123.1689 | 122.9844 | 66.8891 | -123.5118
3580.7969 | 123.1476 | -65.4785 | 57.637 | -0.010607 | -0.072743 | 0.022684 | -0.004827 | -0.0097238 | 0.012078 | -0.0074779 | 0.043307 | 0.046877 | 0.041153 | 0.13308 | 0.054035 | -0.040158 | 0.05635 | 0.005325 | 0.18032 | 0.11483 | 0.4121 | -0.099689 | -65.4562 | 1.4335 | 53.8488 | 57.5172 | 57.7224 | 57.5379 | -65.8839 | 65.3788 | -57.4567 | 65.4384 | 65.4838 | 0.10501 | -57.5222 | -57.2249 | -0.4054 | -0.11987 | 0.022328 | 119.3273 | 119.7327 | 0.085389 | -0.099133 | 65.6588 | 65.5933 | 65.8906 | 65.5349 | -57.7367 | 122.9957 | 123.2009 | 123.0164 | 66.912 | -123.5209
3581.7969 | 123.1796 | -65.4739 | 57.6324 | -0.0029761 | -0.072957 | 0.022257 | -0.0046134 | -0.010151 | 0.012292 | 0.00015261 | 0.04352 | 0.046663 | 0.040939 | 0.13351 | 0.054035 | -0.040158 | 0.060928 | 0.000747 | 0.18948 | 0.11483 | 0.42584 | -0.099689 | -65.4562 | 1.4289 | 53.7343 | 57.5263 | 57.7178 | 57.547 | -65.8885 | 65.3742 | -57.443 | 65.4338 | 65.4747 | 0.10044 | -57.5176 | -57.2066 | -0.41455 | -0.10614 | 0.01775 | 119.2083 | 119.6228 | 0.085388 | -0.085398 | 65.6634 | 65.5888 | 65.8998 | 65.5349 | -57.7321 | 123.0002 | 123.1918 | 123.021 | 66.9029 | -123.5209
3582.7969 | 123.1842 | -65.4556 | 57.637 | -0.0029761 | -0.07317 | 0.022898 | -0.004827 | -0.0099374 | 0.012078 | 0.0077831 | 0.043307 | 0.04709 | 0.041153 | 0.13265 | 0.054249 | -0.040158 | 0.051771 | -0.003831 | 0.19406 | 0.1011 | 0.42126 | -0.099689 | -65.4516 | 1.4289 | 53.6428 | 57.5172 | 57.7178 | 57.547 | -65.8931 | 65.3559 | -57.443 | 65.4155 | 65.4518 | 0.095858 | -57.5359 | -57.2158 | -0.43744 | -0.11987 | 0.004017 | 119.0984 | 119.5358 | 0.08081 | -0.089976 | 65.6497 | 65.5567 | 65.8769 | 65.5074 | -57.7367 | 122.9728 | 123.1735 | 123.0027 | 66.8845 | -123.5301
3583.7969 | 123.2666 | -65.4373 | 57.6233 | -0.0029761 | -0.072957 | 0.022684 | -0.0052544 | -0.010365 | 0.012292 | 0.00015261 | 0.04352 | 0.046663 | 0.041153 | 0.13308 | 0.054462 | -0.040158 | 0.051771 | 0.000747 | 0.18032 | 0.091937 | 0.42126 | -0.099689 | -65.4608 | 1.4335 | 53.6519 | 57.5263 | 57.7178 | 57.5425 | -65.8839 | 65.3376 | -57.443 | 65.3972 | 65.4381 | 0.10044 | -57.5314 | -57.202 | -0.4466 | -0.096982 | -0.02345 | 119.0892 | 119.5358 | 0.094543 | -0.080821 | 65.6176 | 65.5293 | 65.8586 | 65.4891 | -57.723 | 122.9636 | 123.1552 | 122.9798 | 66.8708 | -123.5072
3584.7969 | 123.1796 | -65.4556 | 57.6187 | -0.0029761 | -0.07317 | 0.022684 | -0.0052544 | -0.010151 | 0.012078 | 0.00015261 | 0.043093 | 0.04709 | 0.041366 | 0.13308 | 0.054462 | -0.040158 | 0.05635 | -0.008409 | 0.1849 | 0.10567 | 0.40753 | -0.09511 | -65.4562 | 1.4381 | 53.6473 | 57.5263 | 57.727 | 57.547 | -65.8931 | 65.3605 | -57.4338 | 65.4155 | 65.4472 | 0.086701 | -57.513 | -57.2112 | -0.43744 | -0.092404 | -0.000561 | 119.103 | 119.5404 | 0.10828 | -0.071665 | 65.6405 | 65.5613 | 65.8632 | 65.512 | -57.7138 | 122.9819 | 123.1826 | 123.0027 | 66.8937 | -123.5118
3585.7969 | 123.175 | -65.4602 | 57.6462 | 0.0046549 | -0.07317 | 0.022684 | -0.0052544 | -0.010151 | 0.012506 | 0.00015261 | 0.04352 | 0.04709 | 0.041366 | 0.13308 | 0.054249 | -0.044736 | 0.047193 | -0.003831 | 0.1849 | 0.1011 | 0.40753 | -0.09511 | -65.4516 | 1.4381 | 53.6336 | 57.5217 | 57.7178 | 57.5242 | -65.8931 | 65.3651 | -57.4613 | 65.4155 | 65.4564 | 0.091279 | -57.5451 | -57.2387 | -0.43286 | -0.12445 | 0.008595 | 119.0938 | 119.5267 | 0.071655 | -0.12202 | 65.6451 | 65.5613 | 65.8677 | 65.5074 | -57.7413 | 122.9819 | 123.178 | 122.9844 | 66.8983 | -123.5392
3586.7969 | 123.1705 | -65.4877 | 57.6096 | -0.0029761 | -0.073384 | 0.022898 | -0.004827 | -0.0099374 | 0.012292 | -0.0074779 | 0.043947 | 0.047304 | 0.041153 | 0.13329 | 0.054462 | -0.040158 | 0.060928 | -0.008409 | 0.18032 | 0.11025 | 0.4121 | -0.09511 | -65.4562 | 1.4518 | 53.7069 | 57.5217 | 57.7178 | 57.5196 | -65.8885 | 65.3926 | -57.4292 | 65.4475 | 65.4793 | 0.086701 | -57.4993 | -57.1975 | -0.40082 | -0.087828 | 0.031483 | 119.1945 | 119.5954 | 0.10828 | -0.089981 | 65.668 | 65.5979 | 65.8998 | 65.5486 | -57.7047 | 123.0094 | 123.2055 | 123.0072 | 66.9395 | -123.498
3587.7969 | 123.1888 | -65.4465 | 57.6096 | 0.0046549 | -0.073384 | 0.022684 | -0.0050408 | -0.0099374 | 0.011865 | -0.0074779 | 0.04352 | 0.046877 | 0.041366 | 0.13329 | 0.054249 | -0.040158 | 0.05635 | 0.000747 | 0.15743 | 0.091937 | 0.4121 | -0.10427 | -65.4516 | 1.4472 | 53.6885 | 57.5217 | 57.7224 | 57.515 | -65.8885 | 65.3422 | -57.4521 | 65.4063 | 65.4472 | 0.10501 | -57.5176 | -57.1975 | -0.44202 | -0.087828 | -0.005138 | 119.135 | 119.577 | 0.11286 | -0.09456 | 65.6039 | 65.5384 | 65.8586 | 65.5028 | -57.7138 | 122.9682 | 123.1689 | 122.9615 | 66.8937 | -123.498
3588.8125 | 123.1659 | -65.451 | 57.6416 | 0.0046549 | -0.07317 | 0.022257 | -0.0050408 | -0.0099374 | 0.012078 | 0.00015261 | 0.043734 | 0.04709 | 0.04158 | 0.13308 | 0.054035 | -0.044736 | 0.047193 | -0.008409 | 0.17117 | 0.1011 | 0.40753 | -0.10885 | -65.4562 | 1.4564 | 53.8351 | 57.5263 | 57.7133 | 57.5425 | -65.8885 | 65.3422 | -57.4704 | 65.4063 | 65.4426 | 0.10044 | -57.5405 | -57.2341 | -0.43744 | -0.11529 | -0.005138 | 119.2861 | 119.7236 | 0.071653 | -0.099132 | 65.6222 | 65.5521 | 65.8586 | 65.4982 | -57.7504 | 122.9774 | 123.1643 | 122.9935 | 66.9074 | -123.5301
3589.7969 | 123.1567 | -65.4602 | 57.6096 | 0.0046549 | -0.072957 | 0.022684 | -0.004827 | -0.010151 | 0.011651 | 0.0077831 | 0.043307 | 0.047304 | 0.041153 | 0.13329 | 0.054676 | -0.040158 | 0.051771 | -0.008409 | 0.18948 | 0.096516 | 0.4121 | -0.09511 | -65.4608 | 1.4564 | 54.0091 | 57.5263 | 57.7224 | 57.5242 | -65.8885 | 65.3651 | -57.4201 | 65.42 | 65.4518 | 0.086701 | -57.513 | -57.1975 | -0.42829 | -0.083249 | -0.000562 | 119.4693 | 119.8975 | 0.11286 | -0.085403 | 65.6497 | 65.5567 | 65.8723 | 65.512 | -57.7047 | 122.9865 | 123.1826 | 122.9844 | 66.9166 | -123.498
3590.7969 | 123.175 | -65.4922 | 57.6187 | -0.0029761 | -0.073384 | 0.022684 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.043734 | 0.046877 | 0.041366 | 0.13329 | 0.054035 | -0.044736 | 0.060928 | 0.000747 | 0.17574 | 0.10567 | 0.39837 | -0.09511 | -65.4562 | 1.4564 | 53.9999 | 57.5263 | 57.7224 | 57.5333 | -65.8931 | 65.3971 | -57.443 | 65.4475 | 65.493 | 0.095857 | -57.513 | -57.2203 | -0.40082 | -0.092404 | 0.036061 | 119.4921 | 119.893 | 0.1037 | -0.0854 | 65.668 | 65.5979 | 65.8906 | 65.5532 | -57.7138 | 123.0186 | 123.2147 | 123.0256 | 66.9486 | -123.5118
3591.7969 | 123.1293 | -65.4922 | 57.637 | -0.010607 | -0.07317 | 0.022684 | -0.004827 | -0.010151 | 0.012292 | -0.015108 | 0.04352 | 0.046663 | 0.041366 | 0.13329 | 0.054249 | -0.040158 | 0.05635 | 0.000747 | 0.18032 | 0.1011 | 0.4121 | -0.09511 | -65.4608 | 1.4655 | 54.0503 | 57.5172 | 57.7133 | 57.547 | -65.8885 | 65.3971 | -57.4567 | 65.4521 | 65.493 | 0.095857 | -57.5359 | -57.2249 | -0.39624 | -0.11987 | 0.031482 | 119.5425 | 119.9388 | 0.076231 | -0.089976 | 65.6726 | 65.5933 | 65.9044 | 65.5486 | -57.7321 | 123.0094 | 123.2055 | 123.0393 | 66.9578 | -123.5255
3592.7969 | 123.1659 | -65.4739 | 57.6279 | -0.018238 | -0.072957 | 0.02247 | -0.0046134 | -0.010365 | 0.012292 | 0.00015261 | 0.043947 | 0.046877 | 0.040939 | 0.13286 | 0.054462 | -0.049315 | 0.05635 | -0.008409 | 0.1849 | 0.10567 | 0.4121 | -0.090531 | -65.4562 | 1.4747 | 54.064 | 57.5217 | 57.7224 | 57.5333 | -65.8839 | 65.3834 | -57.443 | 65.4246 | 65.4655 | 0.082122 | -57.5222 | -57.2158 | -0.40997 | -0.10614 | 0.01775 | 119.5379 | 119.9479 | 0.094544 | -0.094556 | 65.6588 | 65.5796 | 65.886 | 65.5303 | -57.7184 | 122.9957 | 123.1964 | 123.0073 | 66.9486 | -123.5118
3593.7969 | 123.2208 | -65.4465 | 57.637 | -0.010607 | -0.07317 | 0.02247 | -0.0046134 | -0.010365 | 0.011865 | -0.0074779 | 0.043734 | 0.04709 | 0.041366 | 0.13329 | 0.054249 | -0.049315 | 0.05635 | 0.000747 | 0.17574 | 0.1011 | 0.4121 | -0.09511 | -65.4653 | 1.4701 | 54.0686 | 57.5172 | 57.7178 | 57.5425 | -65.8976 | 65.3514 | -57.4613 | 65.3972 | 65.4472 | 0.095857 | -57.5359 | -57.2249 | -0.45118 | -0.11987 | -0.018874 | 119.5151 | 119.9662 | 0.08081 | -0.094554 | 65.6222 | 65.5476 | 65.8586 | 65.5028 | -57.7321 | 122.9636 | 123.1643 | 122.9889 | 66.9166 | -123.5347
3594.7969 | 123.175 | -65.4739 | 57.6416 | -0.0029761 | -0.07317 | 0.022898 | -0.004827 | -0.010365 | 0.012078 | 0.00015261 | 0.043734 | 0.04709 | 0.041366 | 0.13329 | 0.054249 | -0.049315 | 0.060928 | -0.003831 | 0.17574 | 0.1011 | 0.4121 | -0.09511 | -65.4608 | 1.4793 | 54.0777 | 57.5217 | 57.7178 | 57.5287 | -65.8885 | 65.3788 | -57.4659 | 65.4246 | 65.4701 | 0.091279 | -57.5405 | -57.2295 | -0.41455 | -0.11987 | 0.013171 | 119.5517 | 119.9662 | 0.076232 | -0.11287 | 65.6497 | 65.575 | 65.886 | 65.5349 | -57.7367 | 122.9957 | 123.1918 | 123.0027 | 66.9532 | -123.5301
3595.7969 | 123.175 | -65.4648 | 57.6187 | -0.0029761 | -0.073384 | 0.02247 | -0.004827 | -0.010151 | 0.012078 | -0.0074779 | 0.043307 | 0.04709 | 0.041153 | 0.13308 | 0.054035 | -0.040158 | 0.051771 | 0.000747 | 0.17117 | 0.1011 | 0.42126 | -0.09511 | -65.4608 | 1.4839 | 54.0869 | 57.5172 | 57.7178 | 57.547 | -65.8931 | 65.3697 | -57.4475 | 65.4246 | 65.4655 | 0.095857 | -57.5176 | -57.1975 | -0.42829 | -0.10156 | 0.004016 | 119.5517 | 119.98 | 0.099121 | -0.071665 | 65.6359 | 65.5659 | 65.886 | 65.5166 | -57.7138 | 122.9819 | 123.1826 | 123.0118 | 66.9486 | -123.5118
3596.8594 | 123.262 | -65.4053 | 57.6279 | -0.0029761 | -0.072957 | 0.022257 | -0.0050408 | -0.0097238 | 0.012292 | 0.00015261 | 0.043307 | 0.046663 | 0.041153 | 0.13329 | 0.054462 | -0.044736 | 0.051771 | -0.003831 | 0.18032 | 0.10567 | 0.40753 | -0.09511 | -65.4653 | 1.4839 | 54.0869 | 57.5217 | 57.7087 | 57.5562 | -65.8931 | 65.3102 | -57.4475 | 65.3605 | 65.4014 | 0.091279 | -57.5222 | -57.2203 | -0.4878 | -0.10614 | -0.060073 | 119.4922 | 119.98 | 0.080808 | -0.071663 | 65.5856 | 65.5109 | 65.8128 | 65.457 | -57.723 | 122.927 | 123.1139 | 122.9615 | 66.8891 | -123.5209
3597.7969 | 123.1705 | -66.4627 | 56.6574 | 0.0046549 | -0.072743 | 0.022898 | -0.004827 | -0.0099374 | 0.012078 | 0.0077831 | 0.066593 | 0.068456 | 0.062731 | 0.13329 | 0.12048 | -0.040158 | 0.05635 | -0.008409 | 0.1849 | 0.11025 | 0.41668 | -0.10427 | 51.8458 | 1.4747 | 53.2398 | 56.5602 | 56.7517 | 56.5672 | -66.8455 | 66.3584 | -56.4725 | 66.4226 | 66.4543 | 0.095859 | -56.5472 | -56.2407 | -0.38276 | -0.097164 | 118.3085 | 119.7025 | 120.0853 | 0.094339 | -0.090182 | 66.6476 | 66.573 | 66.8794 | 66.5191 | -56.7617 | 123.023 | 123.2145 | 123.0299 | 67.9374 | -123.5029
3598.7969 | 123.2483 | -66.4398 | 56.5979 | -0.0029761 | -0.073384 | 0.022684 | -0.0052544 | -0.010151 | 0.012292 | 0.00015261 | 0.06702 | 0.069311 | 0.063586 | 0.13308 | 0.1224 | -0.044736 | 0.047193 | -0.008409 | 0.17117 | 0.091937 | 0.40753 | -0.099689 | 56.4428 | 1.4564 | 53.1757 | 56.5282 | 56.7289 | 56.526 | -66.8638 | 66.3401 | -56.4267 | 66.3951 | 66.4314 | 0.09128 | -56.506 | -56.1904 | -0.42396 | -0.069703 | 122.8826 | 119.6155 | 120.0395 | 0.13096 | -0.07188 | 66.611 | 66.5318 | 66.8473 | 66.487 | -56.6976 | 122.968 | 123.1687 | 122.9658 | 67.8962 | -123.4617
3599.7969 | 123.2071 | -66.4215 | 56.6345 | 0.0046549 | -0.07317 | 0.022684 | -0.004827 | -0.010151 | 0.012506 | 0.00015261 | 0.066807 | 0.068883 | 0.063586 | 0.13308 | 0.12219 | -0.040158 | 0.051771 | -0.003831 | 0.18948 | 0.10567 | 0.4121 | -0.10885 | 56.4611 | 1.461 | 53.2261 | 56.5282 | 56.7243 | 56.5352 | -66.8546 | 66.3127 | -56.445 | 66.3814 | 66.4177 | 0.10502 | -56.5288 | -56.2224 | -0.43311 | -0.10632 | 122.8826 | 119.6476 | 120.0807 | 0.089756 | -0.099344 | 66.611 | 66.5272 | 66.8336 | 66.4733 | -56.7434 | 122.9497 | 123.1458 | 122.9567 | 67.8825 | -123.4891
3600.7969 | 123.1476 | -66.4536 | 56.6437 | -0.0029761 | -0.07317 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | 0.00015261 | 0.066807 | 0.069097 | 0.063586 | 0.13329 | 0.1224 | -0.040158 | 0.051771 | 0.000747 | 0.18948 | 0.10567 | 0.4121 | -0.099689 | 56.4565 | 1.4701 | 53.3177 | 56.5282 | 56.7243 | 56.5581 | -66.8638 | 66.3539 | -56.4542 | 66.4134 | 66.4543 | 0.10044 | -56.538 | -56.2316 | -0.41023 | -0.11548 | 122.9101 | 119.7712 | 120.1814 | 0.0806 | -0.085607 | 66.643 | 66.5592 | 66.8657 | 66.5053 | -56.7434 | 122.9817 | 123.1778 | 123.0116 | 67.9237 | -123.5075
3601.7969 | 123.1522 | -66.4444 | 56.6299 | -0.010607 | -0.07317 | 0.022684 | -0.0052544 | -0.010365 | 0.012292 | -0.0074779 | 0.06702 | 0.069097 | 0.063586 | 0.13329 | 0.12262 | -0.044736 | 0.05635 | 0.005325 | 0.17574 | 0.1011 | 0.41668 | -0.09511 | 56.4474 | 1.461 | 53.3177 | 56.5236 | 56.7197 | 56.5443 | -66.8638 | 66.3493 | -56.4542 | 66.3997 | 66.4497 | 0.10043 | -56.5288 | -56.2133 | -0.41938 | -0.10633 | 122.8918 | 119.7621 | 120.1814 | 0.089755 | -0.085609 | 66.6201 | 66.5455 | 66.8611 | 66.5007 | -56.7251 | 122.968 | 123.1641 | 122.9887 | 67.9054 | -123.4937
3602.7969 | 123.1705 | -66.4398 | 56.6299 | -0.018238 | -0.072957 | 0.022684 | -0.0050408 | -0.0099374 | 0.012292 | -0.0074779 | 0.06702 | 0.069311 | 0.063372 | 0.13308 | 0.12219 | -0.044736 | 0.05635 | 0.000747 | 0.16659 | 0.11025 | 0.40753 | -0.09511 | 56.4428 | 1.4701 | 53.249 | 56.5236 | 56.7243 | 56.5352 | -66.8546 | 66.3447 | -56.4634 | 66.3951 | 66.4406 | 0.095857 | -56.5197 | -56.2224 | -0.4148 | -0.10633 | 122.8826 | 119.6888 | 120.1036 | 0.094333 | -0.094767 | 66.6064 | 66.5501 | 66.8473 | 66.4962 | -56.7251 | 122.9634 | 123.1641 | 122.975 | 67.9099 | -123.4846
3603.7969 | 123.1659 | -66.4398 | 56.6528 | -0.0029761 | -0.07317 | 0.02247 | -0.0050408 | -0.010365 | 0.012292 | 0.00015261 | 0.066807 | 0.069311 | 0.063372 | 0.13329 | 0.1224 | -0.03558 | 0.065507 | -0.003831 | 0.18032 | 0.10567 | 0.4121 | -0.10427 | 56.4886 | 1.4793 | 53.281 | 56.519 | 56.7289 | 56.5352 | -66.8546 | 66.3356 | -56.4725 | 66.4042 | 66.436 | 0.10044 | -56.5472 | -56.2407 | -0.4148 | -0.13379 | 122.9284 | 119.7209 | 120.1357 | 0.076024 | -0.11765 | 66.6201 | 66.5455 | 66.8519 | 66.5053 | -56.7571 | 122.9589 | 123.1687 | 122.975 | 67.9191 | -123.5075
3604.7969 | 123.1934 | -66.4261 | 56.6116 | 0.0046549 | -0.073598 | 0.022684 | -0.0050408 | -0.010151 | 0.012506 | -0.015108 | 0.066807 | 0.069311 | 0.063159 | 0.13308 | 0.12219 | -0.044736 | 0.051771 | -0.003831 | 0.15743 | 0.096516 | 0.4121 | -0.085952 | 56.4977 | 1.4747 | 53.1849 | 56.5236 | 56.7197 | 56.5443 | -66.8592 | 66.3401 | -56.4542 | 66.3813 | 66.4223 | 0.082121 | -56.5151 | -56.1995 | -0.43311 | -0.088015 | 122.9238 | 119.611 | 120.0441 | 0.10807 | -0.067298 | 66.5835 | 66.5226 | 66.8382 | 66.4779 | -56.6976 | 122.9497 | 123.1458 | 122.9704 | 67.9008 | -123.4708
3605.7969 | 123.1659 | -66.4398 | 56.6345 | -0.0029761 | -0.07317 | 0.022898 | -0.0050408 | -0.0099374 | 0.012292 | 0.00015261 | 0.066593 | 0.069524 | 0.063372 | 0.13308 | 0.1224 | -0.044736 | 0.051771 | -0.003831 | 0.17574 | 0.10567 | 0.4121 | -0.090531 | 56.4886 | 1.4839 | 53.1254 | 56.5236 | 56.7243 | 56.526 | -66.8592 | 66.3493 | -56.4588 | 66.3951 | 66.436 | 0.0867 | -56.5288 | -56.2224 | -0.41938 | -0.1109 | 122.9284 | 119.5652 | 119.9846 | 0.089756 | -0.1085 | 66.6156 | 66.5455 | 66.8519 | 66.4916 | -56.7251 | 122.9634 | 123.1641 | 122.9658 | 67.9237 | -123.4937
3606.7969 | 123.2071 | -66.4169 | 56.6162 | -0.010607 | -0.073384 | 0.022684 | -0.0043998 | -0.010151 | 0.012078 | -0.0074779 | 0.06702 | 0.068883 | 0.063372 | 0.13286 | 0.12262 | -0.044736 | 0.05635 | 0.005325 | 0.1849 | 0.1011 | 0.40753 | -0.099689 | 56.5115 | 1.4793 | 52.9651 | 56.5236 | 56.7243 | 56.5214 | -66.85 | 66.3172 | -56.4313 | 66.3722 | 66.4223 | 0.10501 | -56.5151 | -56.2087 | -0.43311 | -0.092593 | 122.9284 | 119.382 | 119.8152 | 0.10807 | -0.094769 | 66.6018 | 66.518 | 66.8245 | 66.4733 | -56.7159 | 122.9405 | 123.1412 | 122.9384 | 67.8962 | -123.4663
3607.7969 | 123.1567 | -66.4261 | 56.6299 | 0.0046549 | -0.073384 | 0.02247 | -0.004827 | -0.010151 | 0.012292 | 0.00015261 | 0.066807 | 0.069097 | 0.062945 | 0.13308 | 0.12219 | -0.049315 | 0.051771 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.09511 | 56.5023 | 1.4747 | 52.9972 | 56.5236 | 56.7197 | 56.5077 | -66.8592 | 66.331 | -56.4542 | 66.3768 | 66.4223 | 0.091279 | -56.5288 | -56.2224 | -0.43311 | -0.10633 | 122.9284 | 119.4232 | 119.8564 | 0.089755 | -0.12224 | 66.6018 | 66.5272 | 66.8336 | 66.4779 | -56.7251 | 122.9497 | 123.1458 | 122.9338 | 67.9008 | -123.4891
3608.7969 | 123.1888 | -66.4352 | 56.6162 | 0.0046549 | -0.07317 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.066807 | 0.06867 | 0.063372 | 0.13329 | 0.12219 | -0.031001 | 0.047193 | -0.003831 | 0.17117 | 0.1011 | 0.40753 | -0.09511 | 56.5023 | 1.4793 | 52.8873 | 56.5236 | 56.7197 | 56.5214 | -66.8546 | 66.3401 | -56.445 | 66.4042 | 66.4314 | 0.091279 | -56.5151 | -56.2087 | -0.41938 | -0.092593 | 122.9376 | 119.3225 | 119.7419 | 0.10349 | -0.094769 | 66.6064 | 66.5363 | 66.8428 | 66.4824 | -56.7113 | 122.9589 | 123.1549 | 122.9567 | 67.9145 | -123.4708
3609.7969 | 123.1934 | -66.4398 | 56.6071 | -0.0029761 | -0.07317 | 0.022257 | -0.0052544 | -0.0099374 | 0.012078 | 0.0077831 | 0.066807 | 0.069311 | 0.062945 | 0.13308 | 0.1224 | -0.049315 | 0.051771 | -0.003831 | 0.17574 | 0.091937 | 0.40295 | -0.085952 | 56.5023 | 1.493 | 52.9422 | 56.519 | 56.7243 | 56.5169 | -66.8546 | 66.3539 | -56.4313 | 66.3905 | 66.436 | 0.082121 | -56.5151 | -56.2041 | -0.4148 | -0.088016 | 122.9421 | 119.382 | 119.7968 | 0.11722 | -0.090193 | 66.6156 | 66.5318 | 66.8428 | 66.4916 | -56.693 | 122.9589 | 123.1641 | 122.9567 | 67.9328 | -123.4617
3610.7969 | 123.175 | -66.4352 | 56.6254 | -0.010607 | -0.073384 | 0.022257 | -0.004827 | -0.010365 | 0.011865 | -0.0074779 | 0.066593 | 0.069311 | 0.063372 | 0.13329 | 0.12219 | -0.049315 | 0.047193 | 0.000747 | 0.1849 | 0.096516 | 0.40295 | -0.099689 | 56.5023 | 1.4976 | 53.2078 | 56.5236 | 56.7243 | 56.5214 | -66.8546 | 66.3356 | -56.4405 | 66.3859 | 66.436 | 0.10044 | -56.5288 | -56.2224 | -0.41938 | -0.10175 | 122.9376 | 119.643 | 120.0624 | 0.098911 | -0.10392 | 66.6201 | 66.5318 | 66.8382 | 66.4824 | -56.7251 | 122.9589 | 123.1595 | 122.9567 | 67.9328 | -123.48
3611.8594 | 123.1567 | -66.4536 | 56.6528 | 0.0046549 | -0.073598 | 0.02247 | -0.004827 | -0.010365 | 0.012078 | -0.0074779 | 0.06702 | 0.069311 | 0.062945 | 0.13329 | 0.12198 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.11025 | 0.40753 | -0.090531 | 56.5023 | 1.5068 | 53.1986 | 56.5282 | 56.7151 | 56.5214 | -66.85 | 66.363 | -56.4679 | 66.4042 | 66.4497 | 0.0867 | -56.5426 | -56.2453 | -0.39649 | -0.12463 | 122.9559 | 119.6522 | 120.0487 | 0.062288 | -0.13139 | 66.6385 | 66.5638 | 66.8611 | 66.5053 | -56.7434 | 122.9817 | 123.1687 | 122.975 | 67.9603 | -123.5029
3612.7969 | 123.2391 | -66.4261 | 56.5933 | -0.0029761 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012506 | -0.0074779 | 0.066593 | 0.068883 | 0.063586 | 0.13329 | 0.12219 | -0.044736 | 0.047193 | -0.003831 | 0.1849 | 0.1011 | 0.40753 | -0.09511 | 56.4977 | 1.5068 | 53.1757 | 56.5236 | 56.7151 | 56.5398 | -66.8546 | 66.331 | -56.4084 | 66.3813 | 66.4223 | 0.091279 | -56.4922 | -56.1858 | -0.42853 | -0.069705 | 122.9238 | 119.6018 | 120.0304 | 0.1218 | -0.053567 | 66.611 | 66.5272 | 66.8336 | 66.4733 | -56.6884 | 122.9497 | 123.1412 | 122.9658 | 67.9328 | -123.4479
3613.7969 | 123.0972 | -66.449 | 56.6437 | -0.0029761 | -0.073384 | 0.02247 | -0.0046134 | -0.010151 | 0.012078 | -0.0074779 | 0.06702 | 0.069097 | 0.063372 | 0.13351 | 0.12219 | -0.044736 | 0.05635 | 0.005325 | 0.18948 | 0.1011 | 0.41668 | -0.09511 | 56.5023 | 1.5068 | 53.1437 | 56.5145 | 56.7151 | 56.5306 | -66.8546 | 66.3539 | -56.4542 | 66.4042 | 66.4543 | 0.10043 | -56.5426 | -56.227 | -0.40565 | -0.12922 | 122.9513 | 119.5927 | 119.9983 | 0.071443 | -0.11308 | 66.6385 | 66.5501 | 66.8657 | 66.5053 | -56.7388 | 122.9634 | 123.1641 | 122.9796 | 67.9557 | -123.4983
3614.7969 | 123.1659 | -66.4398 | 56.6162 | -0.018238 | -0.073384 | 0.022898 | -0.0046134 | -0.0099374 | 0.012078 | 0.00015261 | 0.067234 | 0.068883 | 0.063159 | 0.13286 | 0.12219 | -0.049315 | 0.05635 | -0.003831 | 0.19406 | 0.10567 | 0.40295 | -0.090531 | 56.5023 | 1.5113 | 53.162 | 56.519 | 56.7105 | 56.5123 | -66.8455 | 66.3493 | -56.4222 | 66.3905 | 66.436 | 0.0867 | -56.5105 | -56.2133 | -0.40565 | -0.097171 | 122.9421 | 119.6018 | 120.0075 | 0.09433 | -0.10393 | 66.6339 | 66.5455 | 66.8428 | 66.4962 | -56.7067 | 122.9589 | 123.1504 | 122.9521 | 67.9512 | -123.4617
3615.7969 | 123.2208 | -66.4307 | 56.6437 | -0.010607 | -0.073384 | 0.02247 | -0.004827 | -0.0099374 | 0.012292 | -0.0074779 | 0.066807 | 0.068883 | 0.063586 | 0.13308 | 0.12219 | -0.040158 | 0.051771 | -0.003831 | 0.18032 | 0.096516 | 0.4121 | -0.10427 | 56.5069 | 1.5068 | 53.0521 | 56.5236 | 56.7014 | 56.5214 | -66.85 | 66.3264 | -56.4634 | 66.3905 | 66.4268 | 0.10044 | -56.5472 | -56.2316 | -0.41938 | -0.12006 | 122.9376 | 119.4828 | 119.9021 | 0.057707 | -0.12223 | 66.611 | 66.5272 | 66.8428 | 66.4824 | -56.7479 | 122.9543 | 123.132 | 122.9521 | 67.9374 | -123.4937
3616.7969 | 123.2391 | -66.4215 | 56.5979 | -0.0029761 | -0.07317 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.066807 | 0.069311 | 0.063159 | 0.13286 | 0.12198 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.10567 | 0.41668 | -0.09511 | 56.5069 | 1.5022 | 52.956 | 56.5145 | 56.7197 | 56.526 | -66.8546 | 66.3264 | -56.4222 | 66.3814 | 66.4177 | 0.091279 | -56.4922 | -56.1812 | -0.43311 | -0.083439 | 122.9284 | 119.3775 | 119.8106 | 0.1218 | -0.07188 | 66.5973 | 66.5272 | 66.8382 | 66.4779 | -56.693 | 122.936 | 123.1412 | 122.9475 | 67.9237 | -123.4525
3617.7969 | 123.175 | -66.4261 | 56.6116 | -0.0029761 | -0.07317 | 0.022257 | -0.0050408 | -0.010365 | 0.012292 | -0.0074779 | 0.066379 | 0.069097 | 0.062945 | 0.13308 | 0.12198 | -0.044736 | 0.047193 | 0.000747 | 0.18032 | 0.1011 | 0.4121 | -0.090531 | 56.5115 | 1.5068 | 52.8873 | 56.519 | 56.7151 | 56.5398 | -66.85 | 66.3356 | -56.4313 | 66.3813 | 66.4268 | 0.091278 | -56.5105 | -56.1995 | -0.42396 | -0.092593 | 122.9376 | 119.3134 | 119.7373 | 0.10349 | -0.071877 | 66.6064 | 66.5272 | 66.8382 | 66.4733 | -56.7022 | 122.9451 | 123.1412 | 122.9658 | 67.9328 | -123.4617
3618.7969 | 123.2162 | -66.3986 | 56.5933 | -0.0029761 | -0.07317 | 0.02247 | -0.004827 | -0.010151 | 0.012292 | -0.0074779 | 0.066807 | 0.069097 | 0.062945 | 0.13308 | 0.12176 | -0.044736 | 0.05635 | -0.003831 | 0.1849 | 0.1011 | 0.40753 | -0.090531 | 56.5069 | 1.4976 | 52.8369 | 56.5236 | 56.7105 | 56.5031 | -66.8546 | 66.3081 | -56.4084 | 66.3539 | 66.3948 | 0.0867 | -56.4922 | -56.1858 | -0.456 | -0.069705 | 122.9055 | 119.2355 | 119.6915 | 0.11722 | -0.090196 | 66.5835 | 66.4997 | 66.8061 | 66.455 | -56.6839 | 122.9222 | 123.1092 | 122.9017 | 67.8962 | -123.4479
3619.7969 | 123.2529 | -66.394 | 56.575 | -0.010607 | -0.073384 | 0.022043 | -0.0052544 | -0.0099374 | 0.012078 | 0.00015261 | 0.066593 | 0.068883 | 0.062518 | 0.13286 | 0.12176 | -0.03558 | 0.05635 | 0.000747 | 0.18948 | 0.096516 | 0.40753 | -0.085952 | 56.5069 | 1.5068 | 52.869 | 56.5236 | 56.7151 | 56.5398 | -66.8546 | 66.3081 | -56.3855 | 66.3585 | 66.3948 | 0.086699 | -56.4785 | -56.1675 | -0.46058 | -0.051394 | 122.9009 | 119.263 | 119.7236 | 0.14011 | -0.035256 | 66.5835 | 66.4906 | 66.8016 | 66.4504 | -56.661 | 122.9177 | 123.1092 | 122.9338 | 67.9008 | -123.4296
3620.7969 | 123.2254 | -66.4032 | 56.6025 | -0.010607 | -0.073384 | 0.022043 | -0.0050408 | -0.010578 | 0.012506 | 0.00015261 | 0.066807 | 0.068883 | 0.063159 | 0.13286 | 0.12155 | -0.03558 | 0.05635 | -0.008409 | 0.17117 | 0.1011 | 0.40295 | -0.09511 | 56.5023 | 1.5022 | 52.9285 | 56.5099 | 56.7105 | 56.5306 | -66.8455 | 66.3081 | -56.4313 | 66.3676 | 66.3948 | 0.086701 | -56.5014 | -56.1995 | -0.44227 | -0.092595 | 122.9055 | 119.3317 | 119.7739 | 0.10806 | -0.071879 | 66.5744 | 66.5043 | 66.8061 | 66.4595 | -56.6976 | 122.9131 | 123.1137 | 122.9338 | 67.9054 | -123.4479
3621.7969 | 123.1522 | -66.4352 | 56.6528 | 0.0046549 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066593 | 0.069311 | 0.062945 | 0.13286 | 0.12176 | -0.040158 | 0.05635 | -0.003831 | 0.18032 | 0.11025 | 0.41668 | -0.099689 | 56.4977 | 1.5113 | 52.8644 | 56.5236 | 56.7151 | 56.5169 | -66.85 | 66.3356 | -56.4725 | 66.3951 | 66.4314 | 0.095858 | -56.5426 | -56.2361 | -0.4148 | -0.12921 | 122.933 | 119.2996 | 119.7144 | 0.062288 | -0.13597 | 66.6156 | 66.5455 | 66.8519 | 66.4916 | -56.7525 | 122.9589 | 123.1504 | 122.9521 | 67.9466 | -123.5029
3622.7969 | 123.2346 | -66.4032 | 56.6071 | -0.0029761 | -0.073598 | 0.022684 | -0.004827 | -0.0097238 | 0.012292 | 0.00015261 | 0.066166 | 0.069097 | 0.063159 | 0.13308 | 0.12198 | -0.044736 | 0.05635 | -0.008409 | 0.17117 | 0.10567 | 0.40295 | -0.090531 | 56.5069 | 1.5159 | 52.8003 | 56.5236 | 56.7151 | 56.5306 | -66.85 | 66.3127 | -56.4359 | 66.3585 | 66.3948 | 0.082122 | -56.5014 | -56.2041 | -0.44684 | -0.083438 | 122.9101 | 119.2035 | 119.6503 | 0.10806 | -0.076457 | 66.5744 | 66.5089 | 66.8061 | 66.4595 | -56.6976 | 122.9268 | 123.1183 | 122.9338 | 67.9191 | -123.4571
3623.7969 | 123.2162 | -66.4307 | 56.6437 | -0.018238 | -0.073384 | 0.022684 | -0.0050408 | -0.010365 | 0.011651 | -0.0074779 | 0.066379 | 0.069097 | 0.063159 | 0.13265 | 0.12155 | -0.040158 | 0.05635 | -0.003831 | 0.1849 | 0.11025 | 0.40295 | -0.09511 | 56.5069 | 1.5113 | 52.7545 | 56.519 | 56.7105 | 56.526 | -66.8455 | 66.3356 | -56.4588 | 66.3905 | 66.4268 | 0.091279 | -56.5334 | -56.2407 | -0.4148 | -0.12464 | 122.9376 | 119.1852 | 119.6 | 0.066864 | -0.11766 | 66.6156 | 66.5409 | 66.8336 | 66.487 | -56.7388 | 122.9497 | 123.1412 | 122.9567 | 67.942 | -123.4891
3624.7969 | 123.2162 | -66.3712 | 56.6254 | -0.010607 | -0.073598 | 0.02247 | -0.0052544 | -0.010365 | 0.011865 | 0.00015261 | 0.066379 | 0.068883 | 0.062518 | 0.13286 | 0.12112 | -0.040158 | 0.047193 | -0.003831 | 0.18948 | 0.1011 | 0.4121 | -0.090531 | 56.5023 | 1.5113 | 52.7316 | 56.519 | 56.7105 | 56.5214 | -66.85 | 66.2806 | -56.4359 | 66.331 | 66.3673 | 0.0867 | -56.5243 | -56.2133 | -0.47889 | -0.10633 | 122.8735 | 119.1028 | 119.5816 | 0.085175 | -0.10392 | 66.5606 | 66.4723 | 66.7833 | 66.4183 | -56.7159 | 122.8902 | 123.0817 | 122.8926 | 67.8825 | -123.4754
3625.7969 | 123.2346 | -66.4307 | 56.6208 | -0.010607 | -0.073384 | 0.022684 | -0.0052544 | -0.010365 | 0.011651 | 0.0077831 | 0.066807 | 0.06867 | 0.062731 | 0.13244 | 0.12198 | -0.044736 | 0.05635 | -0.008409 | 0.17117 | 0.1011 | 0.40295 | -0.090531 | 56.5115 | 1.5342 | 52.7133 | 56.519 | 56.7197 | 56.526 | -66.8455 | 66.3401 | -56.4496 | 66.3859 | 66.4223 | 0.082122 | -56.5197 | -56.2178 | -0.4148 | -0.10175 | 122.9421 | 119.1439 | 119.5587 | 0.09891 | -0.094769 | 66.6018 | 66.5318 | 66.8336 | 66.487 | -56.7113 | 122.9497 | 123.1504 | 122.9567 | 67.9649 | -123.4663
3626.7969 | 123.2162 | -66.394 | 56.6071 | -0.0029761 | -0.073811 | 0.02247 | -0.0043998 | -0.010151 | 0.012292 | 0.00015261 | 0.066379 | 0.069097 | 0.062945 | 0.13286 | 0.12219 | -0.040158 | 0.060928 | -0.003831 | 0.18032 | 0.096516 | 0.4121 | -0.090531 | 56.5023 | 1.5205 | 52.7545 | 56.5145 | 56.7151 | 56.5306 | -66.85 | 66.3035 | -56.4267 | 66.3539 | 66.3902 | 0.0867 | -56.5105 | -56.195 | -0.456 | -0.092595 | 122.8964 | 119.1485 | 119.6045 | 0.10806 | -0.076457 | 66.5744 | 66.4906 | 66.8061 | 66.455 | -56.6976 | 122.9085 | 123.1092 | 122.9246 | 67.9145 | -123.4571
3627.7969 | 123.2483 | -66.4169 | 56.6071 | 0.0046549 | -0.073384 | 0.022684 | -0.0050408 | -0.010365 | 0.011865 | 0.00015261 | 0.066379 | 0.069097 | 0.062731 | 0.13265 | 0.12198 | -0.044736 | 0.051771 | -0.003831 | 0.18032 | 0.096516 | 0.41668 | -0.099689 | 56.5069 | 1.5251 | 52.7041 | 56.5145 | 56.7151 | 56.5169 | -66.85 | 66.3172 | -56.4267 | 66.3722 | 66.4131 | 0.095858 | -56.5105 | -56.1904 | -0.43311 | -0.092595 | 122.9238 | 119.1211 | 119.5542 | 0.10806 | -0.090193 | 66.5973 | 66.5134 | 66.8336 | 66.4687 | -56.7067 | 122.9314 | 123.1321 | 122.9338 | 67.942 | -123.4571
3628.7969 | 123.2071 | -66.3849 | 56.6208 | -0.0029761 | -0.073598 | 0.02247 | -0.0050408 | -0.0099374 | 0.012292 | -0.0074779 | 0.066379 | 0.068883 | 0.062731 | 0.13265 | 0.12176 | -0.040158 | 0.051771 | 0.000747 | 0.1849 | 0.10567 | 0.40753 | -0.09511 | 56.5069 | 1.5251 | 52.695 | 56.5145 | 56.7105 | 56.5352 | -66.8455 | 66.2898 | -56.4359 | 66.3447 | 66.3856 | 0.095857 | -56.5151 | -56.2133 | -0.46058 | -0.10633 | 122.8918 | 119.0799 | 119.5404 | 0.089752 | -0.085612 | 66.5698 | 66.4906 | 66.7924 | 66.4367 | -56.7159 | 122.8993 | 123.0954 | 122.9201 | 67.91 | -123.4663
3629.7969 | 123.2117 | -66.3895 | 56.6025 | -0.010607 | -0.073598 | 0.022257 | -0.004827 | -0.0099374 | 0.012078 | 0.00015261 | 0.066807 | 0.069311 | 0.063159 | 0.13308 | 0.12155 | -0.040158 | 0.047193 | 0.000747 | 0.18032 | 0.091937 | 0.40753 | -0.090531 | 56.4977 | 1.548 | 53.6382 | 56.5145 | 56.706 | 56.5077 | -66.85 | 66.2989 | -56.4222 | 66.3493 | 66.3902 | 0.091278 | -56.5105 | -56.195 | -0.46058 | -0.088017 | 122.8872 | 120.0276 | 120.4882 | 0.10348 | -0.094772 | 66.5698 | 66.4814 | 66.797 | 66.4367 | -56.693 | 122.9039 | 123.0954 | 122.8972 | 67.9374 | -123.4525
3630.7969 | 123.2117 | -66.3849 | 56.6162 | -0.0029761 | -0.07317 | 0.022898 | -0.0050408 | -0.010365 | 0.012292 | 0.00015261 | 0.066807 | 0.069311 | 0.062945 | 0.13393 | 0.12155 | -0.044736 | 0.051771 | 0.000747 | 0.18032 | 0.1011 | 0.4121 | -0.09511 | 56.4886 | 1.5525 | 54.1876 | 56.5053 | 56.6968 | 56.526 | -66.8592 | 66.2898 | -56.4359 | 66.3402 | 66.3856 | 0.095857 | -56.5151 | -56.2041 | -0.47431 | -0.11091 | 122.8735 | 120.5725 | 121.0468 | 0.080595 | -0.090191 | 66.5652 | 66.486 | 66.797 | 66.4367 | -56.7113 | 122.8902 | 123.0817 | 122.9109 | 67.9374 | -123.4754
3631.7969 | 123.1934 | -66.4124 | 56.5933 | -0.0029761 | -0.07317 | 0.022684 | -0.004827 | -0.010151 | 0.012078 | 0.00015261 | 0.066807 | 0.069097 | 0.063586 | 0.13351 | 0.12155 | -0.040158 | 0.051771 | -0.008409 | 0.18032 | 0.10567 | 0.4121 | -0.09511 | 56.484 | 1.5663 | 54.3296 | 56.5053 | 56.6922 | 56.526 | -66.85 | 66.3172 | -56.413 | 66.3722 | 66.4039 | 0.086701 | -56.4876 | -56.1812 | -0.43769 | -0.088019 | 122.8964 | 120.7419 | 121.1796 | 0.098904 | -0.067303 | 66.5927 | 66.518 | 66.8245 | 66.4641 | -56.6884 | 122.9177 | 123.1046 | 122.9384 | 67.9786 | -123.4434
3632.7969 | 123.2391 | -66.4032 | 56.6162 | 0.0046549 | -0.073811 | 0.022257 | -0.0046134 | -0.010151 | 0.011865 | 0.00015261 | 0.06702 | 0.069311 | 0.062945 | 0.13415 | 0.12198 | -0.03558 | 0.05635 | -0.003831 | 0.1849 | 0.11025 | 0.40753 | -0.09511 | 56.4932 | 1.5663 | 54.3021 | 56.5007 | 56.706 | 56.5077 | -66.8592 | 66.3081 | -56.4313 | 66.3676 | 66.3994 | 0.091279 | -56.506 | -56.2087 | -0.456 | -0.11548 | 122.8964 | 120.7053 | 121.1613 | 0.089752 | -0.10851 | 66.5881 | 66.5135 | 66.8107 | 66.4595 | -56.7113 | 122.9039 | 123.1092 | 122.9109 | 67.9695 | -123.4754
3633.7969 | 123.1888 | -66.3849 | 56.6254 | -0.0029761 | -0.07317 | 0.022684 | -0.0054682 | -0.010365 | 0.012078 | -0.0074779 | 0.06702 | 0.069311 | 0.062945 | 0.13351 | 0.12176 | -0.044736 | 0.05635 | -0.003831 | 0.18032 | 0.11025 | 0.39837 | -0.09511 | 56.4977 | 1.5663 | 54.1189 | 56.5007 | 56.7014 | 56.5443 | -66.8592 | 66.2898 | -56.445 | 66.3402 | 66.3811 | 0.091279 | -56.5151 | -56.227 | -0.47431 | -0.12464 | 122.8826 | 120.5038 | 120.9781 | 0.076018 | -0.081031 | 66.5652 | 66.4951 | 66.7833 | 66.4412 | -56.7205 | 122.8856 | 123.0863 | 122.9292 | 67.9512 | -123.4846
3634.7969 | 123.1659 | -66.4261 | 56.6345 | -0.0029761 | -0.073598 | 0.022257 | -0.0050408 | -0.010151 | 0.011865 | -0.0074779 | 0.066593 | 0.069097 | 0.063159 | 0.13393 | 0.12155 | -0.049315 | 0.051771 | -0.003831 | 0.18032 | 0.10567 | 0.4121 | -0.085952 | 56.4886 | 1.5709 | 54.1968 | 56.5053 | 56.706 | 56.5031 | -66.8546 | 66.3401 | -56.4542 | 66.3768 | 66.4223 | 0.082121 | -56.5288 | -56.2224 | -0.42853 | -0.12922 | 122.9147 | 120.6229 | 121.0514 | 0.071442 | -0.13139 | 66.6064 | 66.5318 | 66.8382 | 66.4779 | -56.7205 | 122.9314 | 123.132 | 122.9292 | 67.9969 | -123.4891
3635.8594 | 123.1705 | -66.4536 | 56.6345 | -0.0029761 | -0.073384 | 0.022257 | -0.0050408 | -0.0099374 | 0.012292 | -0.0074779 | 0.066593 | 0.069311 | 0.063159 | 0.13415 | 0.12198 | -0.044736 | 0.05635 | 0.000747 | 0.1849 | 0.1011 | 0.4121 | -0.085952 | 56.4932 | 1.5663 | 54.0869 | 56.5099 | 56.706 | 56.5123 | -66.8546 | 66.3676 | -56.4496 | 66.4088 | 66.4543 | 0.086699 | -56.5334 | -56.2224 | -0.40107 | -0.12464 | 122.9467 | 120.5404 | 120.9415 | 0.071442 | -0.12224 | 66.6385 | 66.5546 | 66.8657 | 66.5099 | -56.7205 | 122.9634 | 123.1595 | 122.9658 | 68.0198 | -123.4891
3636.7969 | 123.1888 | -66.3986 | 56.6025 | -0.0029761 | -0.073384 | 0.02247 | -0.0052544 | -0.010365 | 0.011865 | 0.0077831 | 0.066593 | 0.069524 | 0.063159 | 0.13351 | 0.12112 | -0.049315 | 0.060928 | 0.000747 | 0.18032 | 0.11483 | 0.4121 | -0.09511 | 56.4886 | 1.5709 | 53.9495 | 56.5145 | 56.6968 | 56.526 | -66.8592 | 66.3035 | -56.4222 | 66.3493 | 66.3994 | 0.095857 | -56.4876 | -56.1904 | -0.46058 | -0.088017 | 122.8872 | 120.3482 | 120.8087 | 0.094328 | -0.076458 | 66.5789 | 66.5135 | 66.8107 | 66.4595 | -56.6976 | 122.9131 | 123.0954 | 122.9246 | 67.9695 | -123.4617
3637.7969 | 123.1934 | -66.4124 | 56.6025 | -0.0029761 | -0.073384 | 0.02247 | -0.0052544 | -0.010151 | 0.012292 | 0.00015261 | 0.066379 | 0.068883 | 0.063372 | 0.13351 | 0.12091 | -0.044736 | 0.05635 | 0.005325 | 0.1849 | 0.096516 | 0.39837 | -0.085952 | 56.4932 | 1.5663 | 53.6702 | 56.5099 | 56.7151 | 56.5398 | -66.8546 | 66.3264 | -56.4176 | 66.3676 | 66.4177 | 0.091277 | -56.506 | -56.2041 | -0.44227 | -0.092595 | 122.9055 | 120.0826 | 120.5249 | 0.11264 | -0.062722 | 66.5973 | 66.5089 | 66.8107 | 66.4687 | -56.6884 | 122.9222 | 123.1275 | 122.9521 | 67.9786 | -123.4571
3638.7969 | 123.2574 | -66.3757 | 56.6254 | -0.0029761 | -0.073384 | 0.022043 | -0.0046134 | -0.010365 | 0.011651 | -0.0074779 | 0.066379 | 0.069097 | 0.063159 | 0.13329 | 0.12155 | -0.03558 | 0.051771 | 0.000747 | 0.17117 | 0.10567 | 0.40753 | -0.09511 | 56.4932 | 1.5754 | 53.6428 | 56.5099 | 56.7151 | 56.5214 | -66.85 | 66.2806 | -56.4542 | 66.3402 | 66.3765 | 0.095857 | -56.5197 | -56.2178 | -0.47431 | -0.11548 | 122.8689 | 120.0185 | 120.4928 | 0.089754 | -0.10392 | 66.5469 | 66.4814 | 66.7833 | 66.4275 | -56.7205 | 122.8856 | 123.0909 | 122.8972 | 67.9512 | -123.4754
3639.7969 | 123.2162 | -66.3895 | 56.6162 | -0.010607 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066379 | 0.068883 | 0.063159 | 0.13351 | 0.12134 | -0.044736 | 0.05635 | -0.008409 | 0.18948 | 0.11025 | 0.42126 | -0.090531 | 56.4977 | 1.5663 | 53.7343 | 56.5053 | 56.7151 | 56.5169 | -66.85 | 66.2989 | -56.4267 | 66.3447 | 66.3811 | 0.082122 | -56.506 | -56.1949 | -0.46058 | -0.11091 | 122.8872 | 120.1238 | 120.5844 | 0.098909 | -0.099348 | 66.5789 | 66.4997 | 66.8107 | 66.4458 | -56.7067 | 122.8948 | 123.1046 | 122.9063 | 67.9557 | -123.4663
3640.7969 | 123.2941 | -66.3803 | 56.6208 | -0.0029761 | -0.073384 | 0.02247 | -0.0046134 | -0.010365 | 0.012292 | -0.0074779 | 0.066593 | 0.069311 | 0.062731 | 0.13329 | 0.12134 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.096516 | 0.40753 | -0.09511 | 56.5023 | 1.5663 | 53.7893 | 56.5053 | 56.706 | 56.4985 | -66.8546 | 66.2852 | -56.4359 | 66.331 | 66.3765 | 0.091279 | -56.5243 | -56.2133 | -0.47431 | -0.11548 | 122.8826 | 120.1696 | 120.6439 | 0.085174 | -0.12224 | 66.5652 | 66.4768 | 66.7878 | 66.4321 | -56.7159 | 122.8856 | 123.0863 | 122.8789 | 67.9466 | -123.4754
3641.7969 | 123.2208 | -66.3895 | 56.6208 | 0.0046549 | -0.07317 | 0.022684 | -0.0050408 | -0.010578 | 0.012078 | 0.0077831 | 0.066379 | 0.069311 | 0.063159 | 0.13393 | 0.12155 | -0.040158 | 0.047193 | -0.008409 | 0.15743 | 0.1011 | 0.42126 | -0.09511 | 56.4886 | 1.58 | 53.9816 | 56.5007 | 56.6968 | 56.5077 | -66.8546 | 66.2944 | -56.4634 | 66.3493 | 66.3811 | 0.086701 | -56.5197 | -56.1995 | -0.46516 | -0.12006 | 122.8781 | 120.371 | 120.8362 | 0.076017 | -0.11308 | 66.5469 | 66.4906 | 66.8107 | 66.4367 | -56.7159 | 122.8902 | 123.0863 | 122.8972 | 67.9695 | -123.4754
3642.7969 | 123.262 | -66.362 | 56.6437 | 0.0046549 | -0.073384 | 0.022257 | -0.0050408 | -0.010365 | 0.012506 | -0.0074779 | 0.066593 | 0.069311 | 0.062945 | 0.13351 | 0.12155 | -0.058472 | 0.05635 | -0.003831 | 0.15743 | 0.096516 | 0.41668 | -0.090531 | 56.4886 | 1.5754 | 54.0182 | 56.5007 | 56.6968 | 56.5123 | -66.8592 | 66.2715 | -56.4862 | 66.3035 | 66.3582 | 0.0867 | -56.5472 | -56.227 | -0.4972 | -0.14295 | 122.8506 | 120.3802 | 120.8774 | 0.053129 | -0.13139 | 66.5194 | 66.4585 | 66.7787 | 66.4183 | -56.7342 | 122.8627 | 123.0588 | 122.8743 | 67.9374 | -123.5029
3643.7969 | 123.2391 | -66.3849 | 56.6116 | 0.012286 | -0.073598 | 0.02247 | -0.0050408 | -0.0099374 | 0.012078 | 0.0077831 | 0.066593 | 0.068883 | 0.062731 | 0.13393 | 0.12155 | -0.03558 | 0.060928 | -0.008409 | 0.17117 | 0.096516 | 0.40753 | -0.09511 | 56.4886 | 1.5754 | 54.0136 | 56.5053 | 56.7014 | 56.5306 | -66.8546 | 66.2898 | -56.4405 | 66.3493 | 66.3765 | 0.086701 | -56.5151 | -56.2041 | -0.46973 | -0.10633 | 122.8735 | 120.3985 | 120.8683 | 0.089751 | -0.081034 | 66.5561 | 66.4814 | 66.7924 | 66.4458 | -56.7067 | 122.8902 | 123.0863 | 122.9155 | 67.9603 | -123.4663
3644.7969 | 123.2574 | -66.4124 | 56.6299 | 0.0046549 | -0.073384 | 0.022684 | -0.0050408 | -0.010578 | 0.011865 | 0.00015261 | 0.066379 | 0.069097 | 0.062731 | 0.13372 | 0.12134 | -0.040158 | 0.051771 | -0.003831 | 0.15743 | 0.096516 | 0.39837 | -0.10427 | 56.4977 | 1.5892 | 54.0091 | 56.5053 | 56.7014 | 56.5306 | -66.8592 | 66.3081 | -56.4725 | 66.3722 | 66.4085 | 0.10044 | -56.5334 | -56.2316 | -0.44685 | -0.12464 | 122.9101 | 120.4214 | 120.8683 | 0.07144 | -0.099345 | 66.5698 | 66.5089 | 66.8107 | 66.4641 | -56.7342 | 122.9177 | 123.1137 | 122.943 | 68.0015 | -123.4891
3645.7969 | 123.2529 | -66.3986 | 56.6071 | -0.0029761 | -0.073384 | 0.02247 | -0.0050408 | -0.010365 | 0.012078 | 0.0077831 | 0.066593 | 0.06867 | 0.062945 | 0.13351 | 0.12155 | -0.040158 | 0.051771 | 0.000747 | 0.1849 | 0.11025 | 0.41668 | -0.10427 | 56.484 | 1.58 | 54.0091 | 56.5053 | 56.7014 | 56.5352 | -66.85 | 66.2944 | -56.4222 | 66.3585 | 66.3994 | 0.10501 | -56.4968 | -56.1904 | -0.45142 | -0.10175 | 122.8826 | 120.4077 | 120.8591 | 0.094328 | -0.071879 | 66.5835 | 66.5089 | 66.8153 | 66.4504 | -56.7113 | 122.9039 | 123.1 | 122.9338 | 67.9786 | -123.4571
3646.7969 | 123.2025 | -66.3757 | 56.6299 | 0.0046549 | -0.073384 | 0.02247 | -0.004827 | -0.010365 | 0.012292 | 0.00015261 | 0.066807 | 0.069097 | 0.063159 | 0.13372 | 0.12134 | -0.03558 | 0.051771 | -0.012988 | 0.16201 | 0.1011 | 0.40753 | -0.09511 | 56.4794 | 1.6029 | 54.5081 | 56.5053 | 56.6968 | 56.5352 | -66.85 | 66.2806 | -56.4679 | 66.3402 | 66.3627 | 0.082122 | -56.5288 | -56.2224 | -0.47431 | -0.12464 | 122.8552 | 120.8839 | 121.3582 | 0.066862 | -0.094767 | 66.5377 | 66.4768 | 66.7833 | 66.4275 | -56.7251 | 122.881 | 123.0725 | 122.9109 | 67.9786 | -123.48
3647.7969 | 123.2391 | -66.3986 | 56.5979 | 0.0046549 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | 0.0077831 | 0.066807 | 0.069097 | 0.063159 | 0.13415 | 0.12134 | -0.049315 | 0.060928 | 0.000747 | 0.17117 | 0.1011 | 0.40295 | -0.09511 | 56.4932 | 1.6029 | 54.3113 | 56.5099 | 56.7014 | 56.5123 | -66.8592 | 66.3035 | -56.4267 | 66.3493 | 66.3994 | 0.095857 | -56.4968 | -56.195 | -0.46058 | -0.088017 | 122.8918 | 120.7099 | 121.1705 | 0.10348 | -0.085616 | 66.5698 | 66.4997 | 66.8016 | 66.4595 | -56.693 | 122.9085 | 123.1 | 122.9109 | 68.0015 | -123.4571
3648.7969 | 123.1522 | -66.449 | 56.6574 | -0.010607 | -0.073384 | 0.022898 | -0.004827 | -0.010151 | 0.012292 | 0.0077831 | 0.066593 | 0.069311 | 0.063159 | 0.13372 | 0.12112 | -0.03558 | 0.051771 | -0.003831 | 0.19406 | 0.10567 | 0.39379 | -0.09511 | 56.4886 | 1.5983 | 54.5448 | 56.5007 | 56.7014 | 56.5169 | -66.8546 | 66.3539 | -56.4634 | 66.4134 | 66.4451 | 0.091279 | -56.5517 | -56.2636 | -0.40565 | -0.15668 | 122.9376 | 120.9937 | 121.3994 | 0.043974 | -0.14055 | 66.643 | 66.5546 | 66.8428 | 66.5007 | -56.7525 | 122.9497 | 123.1504 | 122.9658 | 68.0473 | -123.512
3649.7969 | 123.2483 | -66.3803 | 56.5933 | 0.0046549 | -0.072957 | 0.02247 | -0.0052544 | -0.010151 | 0.012078 | 0.00015261 | 0.066593 | 0.069311 | 0.063159 | 0.13393 | 0.12112 | -0.049315 | 0.051771 | -0.003831 | 0.17574 | 0.1011 | 0.4121 | -0.090531 | 56.4932 | 1.6075 | 54.705 | 56.5007 | 56.6876 | 56.4848 | -66.8638 | 66.2898 | -56.4176 | 66.331 | 66.3765 | 0.0867 | -56.4922 | -56.1812 | -0.48347 | -0.092597 | 122.8735 | 121.0853 | 121.5688 | 0.094325 | -0.10851 | 66.5561 | 66.4814 | 66.7924 | 66.4321 | -56.6839 | 122.881 | 123.068 | 122.8651 | 67.9878 | -123.4571
3650.7969 | 123.1796 | -66.4032 | 56.6299 | 0.0046549 | -0.073384 | 0.022043 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066593 | 0.069097 | 0.062945 | 0.13415 | 0.12112 | -0.044736 | 0.051771 | 0.000747 | 0.18948 | 0.1011 | 0.40295 | -0.09511 | 56.4886 | 1.6075 | 54.4578 | 56.5007 | 56.6922 | 56.5077 | -66.8592 | 66.3081 | -56.4405 | 66.3585 | 66.4039 | 0.095857 | -56.5288 | -56.227 | -0.456 | -0.12922 | 122.8918 | 120.861 | 121.317 | 0.062283 | -0.12224 | 66.5927 | 66.5043 | 66.8061 | 66.455 | -56.7251 | 122.9039 | 123.0954 | 122.9109 | 68.0107 | -123.4891
3651.7969 | 123.2666 | -66.3849 | 56.6299 | 0.012286 | -0.07317 | 0.02247 | -0.0052544 | -0.010365 | 0.012078 | 0.015414 | 0.066593 | 0.069097 | 0.062731 | 0.13351 | 0.12155 | -0.03558 | 0.05635 | -0.003831 | 0.18948 | 0.096516 | 0.40753 | -0.090531 | 56.4932 | 1.6121 | 54.4623 | 56.4961 | 56.6968 | 56.4848 | -66.8546 | 66.2944 | -56.4405 | 66.3493 | 66.3811 | 0.0867 | -56.5334 | -56.2224 | -0.46973 | -0.1338 | 122.8781 | 120.8472 | 121.317 | 0.066862 | -0.14513 | 66.5744 | 66.4814 | 66.7924 | 66.4412 | -56.7205 | 122.881 | 123.0817 | 122.8697 | 67.997 | -123.4846
3652.7969 | 123.111 | -66.4261 | 56.662 | -0.010607 | -0.073384 | 0.022257 | -0.0052544 | -0.010365 | 0.012506 | 0.00015261 | 0.066379 | 0.069097 | 0.063159 | 0.13415 | 0.12134 | -0.040158 | 0.051771 | 0.000747 | 0.18948 | 0.11025 | 0.40753 | -0.11342 | 56.4932 | 1.6075 | 54.4166 | 56.4961 | 56.7014 | 56.5214 | -66.8546 | 66.3127 | -56.4725 | 66.3859 | 66.4268 | 0.11417 | -56.5517 | -56.2545 | -0.42853 | -0.16584 | 122.9193 | 120.8426 | 121.2712 | 0.039397 | -0.14055 | 66.6156 | 66.5363 | 66.8336 | 66.4779 | -56.7754 | 122.9222 | 123.1275 | 122.9475 | 68.0336 | -123.5166
3653.7969 | 123.2483 | -66.3849 | 56.6025 | 0.0046549 | -0.073384 | 0.022898 | -0.004827 | -0.010151 | 0.012078 | 0.00015261 | 0.066593 | 0.068883 | 0.062945 | 0.13372 | 0.12112 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.10567 | 0.4121 | -0.09511 | 56.4932 | 1.6166 | 54.4395 | 56.5053 | 56.6968 | 56.5123 | -66.8592 | 66.2898 | -56.4176 | 66.3356 | 66.3811 | 0.091279 | -56.4968 | -56.1904 | -0.47431 | -0.097174 | 122.8781 | 120.8243 | 121.2987 | 0.094328 | -0.090194 | 66.5698 | 66.4906 | 66.797 | 66.4367 | -56.6976 | 122.8902 | 123.0817 | 122.8972 | 68.0015 | -123.4617
3654.7969 | 123.1796 | -66.3986 | 56.6437 | -0.0029761 | -0.073384 | 0.022257 | -0.0052544 | -0.010151 | 0.012078 | 0.0077831 | 0.066593 | 0.069311 | 0.062945 | 0.13372 | 0.12091 | -0.044736 | 0.060928 | -0.003831 | 0.1849 | 0.11025 | 0.4121 | -0.09511 | 56.4932 | 1.6121 | 54.3113 | 56.5053 | 56.7014 | 56.5214 | -66.8546 | 66.3035 | -56.4588 | 66.3539 | 66.3948 | 0.091279 | -56.5334 | -56.2316 | -0.456 | -0.13837 | 122.8918 | 120.7099 | 121.1659 | 0.057707 | -0.12223 | 66.5835 | 66.5089 | 66.8107 | 66.4595 | -56.7388 | 122.9039 | 123.1 | 122.9201 | 68.0107 | -123.4983
3655.7969 | 123.2346 | -66.3666 | 56.5933 | 0.0046549 | -0.07317 | 0.02247 | -0.0052544 | -0.010365 | 0.012292 | 0.0077831 | 0.066593 | 0.068883 | 0.062731 | 0.13393 | 0.12112 | -0.040158 | 0.051771 | 0.000747 | 0.18032 | 0.096516 | 0.40753 | -0.099689 | 56.4886 | 1.6212 | 54.4211 | 56.5007 | 56.6922 | 56.5352 | -66.8546 | 66.2669 | -56.413 | 66.3264 | 66.3673 | 0.10044 | -56.4968 | -56.1858 | -0.48804 | -0.092597 | 122.8552 | 120.7877 | 121.2758 | 0.098904 | -0.058146 | 66.5469 | 66.4631 | 66.7741 | 66.4183 | -56.693 | 122.8673 | 123.0588 | 122.9018 | 67.9878 | -123.4479
3656.7969 | 123.1384 | -66.4398 | 56.6528 | 0.0046549 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.066593 | 0.069097 | 0.062945 | 0.13393 | 0.12134 | -0.040158 | 0.060928 | 0.000747 | 0.1849 | 0.11025 | 0.39837 | -0.09511 | 56.4886 | 1.6212 | 54.3891 | 56.4961 | 56.6968 | 56.4985 | -66.8638 | 66.3447 | -56.4679 | 66.3997 | 66.4406 | 0.095857 | -56.5426 | -56.2545 | -0.42396 | -0.15668 | 122.9284 | 120.8289 | 121.2529 | 0.043974 | -0.15428 | 66.6247 | 66.5501 | 66.8382 | 66.5007 | -56.7479 | 122.936 | 123.1366 | 122.9384 | 68.061 | -123.5166
3657.7969 | 123.143 | -66.4398 | 56.662 | 0.012286 | -0.073598 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | 0.0077831 | 0.066379 | 0.069097 | 0.063159 | 0.13393 | 0.12134 | -0.040158 | 0.05635 | -0.008409 | 0.1849 | 0.10567 | 0.40753 | -0.099689 | 56.4886 | 1.6212 | 54.3479 | 56.5007 | 56.706 | 56.494 | -66.85 | 66.3401 | -56.4771 | 66.3997 | 66.4314 | 0.09128 | -56.5563 | -56.2545 | -0.41022 | -0.16126 | 122.9284 | 120.7877 | 121.1979 | 0.043976 | -0.16802 | 66.6247 | 66.5455 | 66.8473 | 66.4962 | -56.7617 | 122.9405 | 123.1458 | 122.9338 | 68.061 | -123.512
3658.7969 | 123.1796 | -66.4261 | 56.5979 | -0.0029761 | -0.073598 | 0.022257 | -0.0052544 | -0.010151 | 0.012078 | 0.015414 | 0.066807 | 0.068883 | 0.062945 | 0.13351 | 0.12069 | -0.044736 | 0.060928 | -0.003831 | 0.17117 | 0.1011 | 0.40753 | -0.10427 | 56.4886 | 1.6304 | 54.3616 | 56.4961 | 56.7014 | 56.5123 | -66.8546 | 66.3218 | -56.4267 | 66.3813 | 66.4223 | 0.10044 | -56.4968 | -56.1904 | -0.42853 | -0.10175 | 122.9147 | 120.7877 | 121.2162 | 0.10348 | -0.085616 | 66.5973 | 66.5272 | 66.8336 | 66.487 | -56.7022 | 122.9222 | 123.1275 | 122.9384 | 68.0565 | -123.4525
3659.7969 | 123.111 | -66.449 | 56.6299 | 0.0046549 | -0.073598 | 0.022684 | -0.0046134 | -0.010578 | 0.012292 | 0.00015261 | 0.066593 | 0.06867 | 0.062945 | 0.13372 | 0.12112 | -0.049315 | 0.060928 | -0.003831 | 0.16659 | 0.11025 | 0.4121 | -0.09511 | 56.4977 | 1.6212 | 54.325 | 56.4961 | 56.6922 | 56.5123 | -66.8592 | 66.3539 | -56.4634 | 66.3997 | 66.4451 | 0.091279 | -56.5197 | -56.2178 | -0.41022 | -0.1338 | 122.9467 | 120.774 | 121.1842 | 0.062283 | -0.11766 | 66.6156 | 66.5592 | 66.8611 | 66.5099 | -56.7251 | 122.9451 | 123.1412 | 122.9613 | 68.0702 | -123.4891
3660.7969 | 123.1522 | -66.4215 | 56.6391 | 0.0046549 | -0.073598 | 0.022257 | -0.004827 | -0.010578 | 0.011651 | 0.0077831 | 0.066807 | 0.069097 | 0.062731 | 0.13372 | 0.12112 | -0.03558 | 0.060928 | -0.003831 | 0.17574 | 0.10567 | 0.41668 | -0.09511 | 56.4886 | 1.6212 | 54.238 | 56.5053 | 56.6968 | 56.5169 | -66.8546 | 66.3264 | -56.4634 | 66.3859 | 66.4177 | 0.091279 | -56.5334 | -56.2224 | -0.43311 | -0.13379 | 122.9101 | 120.6595 | 121.0926 | 0.057707 | -0.12224 | 66.5973 | 66.5272 | 66.8382 | 66.4824 | -56.7342 | 122.9268 | 123.1183 | 122.9384 | 68.0427 | -123.4937
3661.7969 | 123.175 | -66.3986 | 56.6116 | 0.012286 | -0.073598 | 0.022257 | -0.004827 | -0.010151 | 0.011865 | 0.0077831 | 0.066166 | 0.06867 | 0.062945 | 0.13393 | 0.12112 | -0.044736 | 0.051771 | 0.000747 | 0.16659 | 0.1011 | 0.4121 | -0.099689 | 56.4886 | 1.6395 | 54.2334 | 56.5053 | 56.6922 | 56.5214 | -66.8546 | 66.2989 | -56.445 | 66.3539 | 66.3994 | 0.10044 | -56.5105 | -56.1995 | -0.456 | -0.10633 | 122.8872 | 120.632 | 121.088 | 0.080594 | -0.090191 | 66.5652 | 66.4997 | 66.8107 | 66.4504 | -56.7113 | 122.9039 | 123.0908 | 122.9201 | 68.0382 | -123.4663
3662.7969 | 123.1247 | -66.4307 | 56.6391 | -0.0029761 | -0.073384 | 0.02247 | -0.004827 | -0.010151 | 0.012078 | -0.0074779 | 0.066379 | 0.06867 | 0.062731 | 0.13393 | 0.12112 | -0.040158 | 0.05635 | -0.003831 | 0.1849 | 0.11941 | 0.41668 | -0.09511 | 56.4932 | 1.6258 | 54.2563 | 56.5053 | 56.6968 | 56.5352 | -66.8592 | 66.3356 | -56.4542 | 66.3905 | 66.4268 | 0.091279 | -56.5197 | -56.2224 | -0.42854 | -0.13379 | 122.9238 | 120.687 | 121.1155 | 0.057707 | -0.10392 | 66.6156 | 66.5501 | 66.8473 | 66.487 | -56.7342 | 122.936 | 123.1275 | 122.9658 | 68.0565 | -123.4983
3663.7969 | 123.111 | -66.4215 | 56.6299 | -0.010607 | -0.073811 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066593 | 0.06867 | 0.062518 | 0.13351 | 0.12112 | -0.044736 | 0.051771 | 0.000747 | 0.15285 | 0.10567 | 0.40753 | -0.099689 | 56.4932 | 1.635 | 54.2471 | 56.4961 | 56.7014 | 56.5169 | -66.8592 | 66.3218 | -56.4771 | 66.3768 | 66.4223 | 0.10044 | -56.5243 | -56.2224 | -0.43769 | -0.1338 | 122.9147 | 120.6687 | 121.1063 | 0.07144 | -0.11308 | 66.5744 | 66.5272 | 66.829 | 66.4733 | -56.7296 | 122.9177 | 123.1229 | 122.9384 | 68.0565 | -123.4891
3664.7969 | 123.1567 | -66.4078 | 56.6483 | 0.0046549 | -0.073384 | 0.02247 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066379 | 0.068883 | 0.062731 | 0.13372 | 0.12069 | -0.044736 | 0.05635 | -0.003831 | 0.18032 | 0.10567 | 0.4121 | -0.10427 | 56.4932 | 1.6395 | 54.3021 | 56.4961 | 56.6876 | 56.5169 | -66.8592 | 66.3035 | -56.4679 | 66.363 | 66.4039 | 0.10044 | -56.5426 | -56.2362 | -0.45142 | -0.15211 | 122.9009 | 120.7099 | 121.1613 | 0.039394 | -0.13139 | 66.5881 | 66.5134 | 66.8199 | 66.4641 | -56.7525 | 122.9039 | 123.0954 | 122.9246 | 68.0473 | -123.5075
3665.7969 | 123.1293 | -66.4169 | 56.6299 | 0.0046549 | -0.073598 | 0.02247 | -0.0050408 | -0.010151 | 0.011651 | 0.0077831 | 0.066379 | 0.069097 | 0.062731 | 0.13393 | 0.12112 | -0.03558 | 0.051771 | -0.003831 | 0.17574 | 0.11025 | 0.4121 | -0.09511 | 56.4886 | 1.6487 | 54.3113 | 56.5053 | 56.6968 | 56.5123 | -66.8592 | 66.3218 | -56.4542 | 66.3814 | 66.4131 | 0.091279 | -56.5197 | -56.2178 | -0.44227 | -0.12464 | 122.9055 | 120.7282 | 121.1705 | 0.066862 | -0.11766 | 66.5927 | 66.5272 | 66.829 | 66.4687 | -56.7251 | 122.9222 | 123.1137 | 122.9292 | 68.0656 | -123.4891
3666.7969 | 123.0789 | -66.4261 | 56.5887 | -0.0029761 | -0.073811 | 0.022257 | -0.0050408 | -0.010151 | 0.011865 | -0.0074779 | 0.066593 | 0.068883 | 0.062518 | 0.13372 | 0.12112 | -0.044736 | 0.05635 | -0.008409 | 0.18032 | 0.10567 | 0.39837 | -0.09511 | 56.484 | 1.6533 | 54.2975 | 56.5053 | 56.7014 | 56.5306 | -66.8592 | 66.331 | -56.4084 | 66.3813 | 66.4177 | 0.086701 | -56.4831 | -56.1904 | -0.43311 | -0.083441 | 122.9101 | 120.7236 | 121.1567 | 0.11264 | -0.058146 | 66.6064 | 66.5318 | 66.8245 | 66.4824 | -56.6839 | 122.9314 | 123.1275 | 122.9567 | 68.0794 | -123.4479
3667.7969 | 123.1338 | -66.4032 | 56.6254 | -0.010607 | -0.073811 | 0.022257 | -0.0054682 | -0.010578 | 0.011651 | 0.00015261 | 0.066807 | 0.068883 | 0.062945 | 0.13351 | 0.12091 | -0.044736 | 0.060928 | -0.008409 | 0.1849 | 0.11483 | 0.40295 | -0.099689 | 56.4886 | 1.6533 | 54.2929 | 56.5007 | 56.6968 | 56.5352 | -66.85 | 66.3035 | -56.4405 | 66.3585 | 66.3948 | 0.09128 | -56.5105 | -56.2224 | -0.44684 | -0.12464 | 122.8918 | 120.6961 | 121.143 | 0.07144 | -0.090189 | 66.5881 | 66.518 | 66.8061 | 66.4641 | -56.7251 | 122.9039 | 123.1 | 122.9384 | 68.0565 | -123.4754
3668.7969 | 123.175 | -66.4307 | 56.6162 | 0.0046549 | -0.073811 | 0.022684 | -0.0050408 | -0.010151 | 0.011651 | 0.00015261 | 0.066593 | 0.069097 | 0.062945 | 0.13351 | 0.12112 | -0.040158 | 0.047193 | -0.008409 | 0.18948 | 0.11025 | 0.4121 | -0.099689 | 56.4932 | 1.6487 | 54.3067 | 56.5053 | 56.6922 | 56.5077 | -66.8546 | 66.331 | -56.4267 | 66.3905 | 66.4223 | 0.09128 | -56.506 | -56.2041 | -0.42396 | -0.11091 | 122.9238 | 120.7373 | 121.1613 | 0.076016 | -0.10851 | 66.6201 | 66.5409 | 66.8428 | 66.4779 | -56.7159 | 122.936 | 123.1229 | 122.9384 | 68.0794 | -123.4708
3669.7969 | 123.0331 | -66.4398 | 56.6391 | -0.010607 | -0.073384 | 0.02247 | -0.0050408 | -0.010578 | 0.012078 | 0.0077831 | 0.066593 | 0.06867 | 0.062731 | 0.13372 | 0.12112 | -0.053893 | 0.060928 | -0.008409 | 0.17574 | 0.11025 | 0.40295 | -0.090531 | 56.4932 | 1.6579 | 54.3158 | 56.5053 | 56.7014 | 56.5077 | -66.8546 | 66.3493 | -56.4634 | 66.3859 | 66.4314 | 0.082122 | -56.5288 | -56.2362 | -0.4148 | -0.13379 | 122.933 | 120.7556 | 121.1704 | 0.062285 | -0.13139 | 66.6156 | 66.5501 | 66.8428 | 66.5007 | -56.7296 | 122.9451 | 123.1412 | 122.9475 | 68.0977 | -123.4937
3670.8594 | 123.1338 | -66.4215 | 56.6391 | 0.012286 | -0.073811 | 0.022684 | -0.0046134 | -0.010151 | 0.012292 | 0.00015261 | 0.066593 | 0.069097 | 0.062945 | 0.13393 | 0.12091 | -0.040158 | 0.060928 | -0.008409 | 0.17117 | 0.096516 | 0.40295 | -0.090531 | 56.4932 | 1.667 | 54.3067 | 56.4916 | 56.6968 | 56.5077 | -66.8546 | 66.331 | -56.4679 | 66.3814 | 66.4131 | 0.082122 | -56.5426 | -56.2362 | -0.43311 | -0.14753 | 122.9147 | 120.7282 | 121.1613 | 0.057707 | -0.13139 | 66.5927 | 66.518 | 66.8245 | 66.4824 | -56.7296 | 122.9131 | 123.1183 | 122.9292 | 68.0885 | -123.4937
3671.7969 | 123.143 | -66.4215 | 56.6345 | 0.0046549 | -0.073384 | 0.022257 | -0.0050408 | -0.010365 | 0.011651 | 0.0077831 | 0.066166 | 0.068883 | 0.062945 | 0.13393 | 0.12091 | -0.040158 | 0.051771 | -0.008409 | 0.17574 | 0.096516 | 0.4121 | -0.09511 | 56.4886 | 1.6579 | 54.3296 | 56.4961 | 56.6968 | 56.5077 | -66.8592 | 66.3264 | -56.4588 | 66.3814 | 66.4131 | 0.086701 | -56.538 | -56.2224 | -0.43769 | -0.13837 | 122.9101 | 120.7511 | 121.1888 | 0.062285 | -0.12682 | 66.5973 | 66.518 | 66.8336 | 66.4733 | -56.7296 | 122.9177 | 123.1183 | 122.9292 | 68.0794 | -123.4937
3672.7969 | 123.1522 | -66.4398 | 56.6071 | -0.0029761 | -0.073598 | 0.022043 | -0.0046134 | -0.010151 | 0.012078 | -0.015108 | 0.066379 | 0.06867 | 0.063159 | 0.13415 | 0.12112 | -0.040158 | 0.05635 | 0.000747 | 0.17574 | 0.10567 | 0.39379 | -0.099689 | 56.4932 | 1.6624 | 54.3158 | 56.5007 | 56.7014 | 56.5214 | -66.8638 | 66.3401 | -56.4313 | 66.3997 | 66.4406 | 0.10044 | -56.5014 | -56.2133 | -0.42396 | -0.10633 | 122.933 | 120.7556 | 121.1796 | 0.094328 | -0.085614 | 66.6156 | 66.5455 | 66.8336 | 66.4962 | -56.7067 | 122.9405 | 123.1412 | 122.9613 | 68.1022 | -123.4708
3673.7969 | 123.1567 | -66.4352 | 56.6162 | 0.0046549 | -0.074025 | 0.022043 | -0.004827 | -0.010365 | 0.011651 | 0.00015261 | 0.066593 | 0.068883 | 0.062945 | 0.13351 | 0.12091 | -0.040158 | 0.060928 | -0.008409 | 0.16201 | 0.11025 | 0.4121 | -0.09511 | 56.4977 | 1.6716 | 54.3021 | 56.4961 | 56.706 | 56.5169 | -66.8546 | 66.3401 | -56.4542 | 66.3951 | 66.4268 | 0.086701 | -56.506 | -56.2041 | -0.41938 | -0.12006 | 122.933 | 120.7373 | 121.1567 | 0.089752 | -0.099348 | 66.5973 | 66.5455 | 66.8473 | 66.4962 | -56.7113 | 122.9314 | 123.1412 | 122.9521 | 68.1068 | -123.4708
3674.7969 | 123.1201 | -66.4307 | 56.6208 | -0.0029761 | -0.073598 | 0.022684 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | 0.066379 | 0.068883 | 0.062731 | 0.13351 | 0.12112 | -0.044736 | 0.060928 | -0.012988 | 0.19864 | 0.1011 | 0.4121 | -0.10885 | 56.4886 | 1.6624 | 54.3067 | 56.5007 | 56.7105 | 56.5169 | -66.8592 | 66.3218 | -56.4222 | 66.3859 | 66.4177 | 0.095859 | -56.5197 | -56.2087 | -0.42854 | -0.12006 | 122.9193 | 120.7373 | 121.1659 | 0.089752 | -0.10393 | 66.6293 | 66.5318 | 66.8428 | 66.4916 | -56.7296 | 122.9314 | 123.1412 | 122.9475 | 68.0931 | -123.48
3675.7969 | 123.1476 | -66.4215 | 56.6208 | -0.0029761 | -0.073598 | 0.02247 | -0.004827 | -0.010365 | 0.012078 | -0.0074779 | 0.066379 | 0.068883 | 0.062731 | 0.13393 | 0.12091 | -0.044736 | 0.05635 | 0.000747 | 0.18948 | 0.10567 | 0.39837 | -0.09511 | 56.484 | 1.6762 | 54.3067 | 56.4916 | 56.7014 | 56.5352 | -66.8546 | 66.3264 | -56.4313 | 66.3768 | 66.4223 | 0.095857 | -56.5151 | -56.2224 | -0.43311 | -0.12922 | 122.9055 | 120.7282 | 121.1613 | 0.080595 | -0.085612 | 66.611 | 66.5272 | 66.8199 | 66.4779 | -56.7159 | 122.9131 | 123.1229 | 122.9567 | 68.0977 | -123.4754
3676.7969 | 123.1476 | -66.4169 | 56.6071 | -0.010607 | -0.074239 | 0.022257 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | 0.066166 | 0.069097 | 0.062518 | 0.13351 | 0.12091 | -0.040158 | 0.060928 | -0.008409 | 0.16201 | 0.11025 | 0.41668 | -0.09511 | 56.5069 | 1.6762 | 54.3067 | 56.5007 | 56.6968 | 56.5306 | -66.85 | 66.3218 | -56.445 | 66.3768 | 66.4085 | 0.086701 | -56.4968 | -56.1904 | -0.43311 | -0.10633 | 122.9238 | 120.7236 | 121.1567 | 0.08975 | -0.076457 | 66.5789 | 66.5272 | 66.8336 | 66.4779 | -56.7022 | 122.9177 | 123.1137 | 122.9475 | 68.0931 | -123.4571
3677.7969 | 123.1522 | -66.4307 | 56.5933 | -0.0029761 | -0.073811 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.066593 | 0.06867 | 0.062731 | 0.13372 | 0.12069 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.090531 | 56.4977 | 1.6716 | 54.3525 | 56.4961 | 56.6968 | 56.526 | -66.8592 | 66.3401 | -56.4176 | 66.3905 | 66.4268 | 0.0867 | -56.4922 | -56.1858 | -0.42854 | -0.097176 | 122.9284 | 120.7831 | 121.2117 | 0.10348 | -0.067303 | 66.6064 | 66.5318 | 66.8382 | 66.487 | -56.6839 | 122.9268 | 123.1275 | 122.9567 | 68.1023 | -123.4525
3678.7969 | 123.1018 | -66.449 | 56.6071 | 0.0046549 | -0.073811 | 0.022257 | -0.004827 | -0.010578 | 0.012078 | 0.0077831 | 0.066593 | 0.06867 | 0.062731 | 0.13372 | 0.12069 | -0.040158 | 0.060928 | 0.000747 | 0.17574 | 0.091937 | 0.40295 | -0.09511 | 56.4886 | 1.6762 | 54.3341 | 56.4961 | 56.7014 | 56.494 | -66.8546 | 66.3539 | -56.4313 | 66.4088 | 66.4497 | 0.095857 | -56.5151 | -56.2041 | -0.40565 | -0.11091 | 122.9376 | 120.7831 | 121.1888 | 0.094328 | -0.11309 | 66.6247 | 66.5409 | 66.8519 | 66.5099 | -56.7022 | 122.9451 | 123.1504 | 122.9429 | 68.1251 | -123.4617
3679.7969 | 123.1613 | -66.4261 | 56.5979 | -0.010607 | -0.073598 | 0.022684 | -0.0050408 | -0.010151 | 0.011651 | 0.00015261 | 0.066379 | 0.068883 | 0.062731 | 0.13372 | 0.12091 | -0.044736 | 0.060928 | -0.003831 | 0.1849 | 0.10567 | 0.4121 | -0.09511 | 56.4932 | 1.6716 | 54.27 | 56.4961 | 56.7014 | 56.526 | -66.8546 | 66.331 | -56.413 | 66.3813 | 66.4223 | 0.091279 | -56.4922 | -56.1858 | -0.42853 | -0.10175 | 122.9193 | 120.6961 | 121.1247 | 0.10348 | -0.07188 | 66.611 | 66.5318 | 66.8382 | 66.487 | -56.693 | 122.9222 | 123.1275 | 122.9521 | 68.0977 | -123.4525
3680.7969 | 123.1293 | -66.4398 | 56.6071 | -0.0029761 | -0.073598 | 0.022257 | -0.0050408 | -0.010365 | 0.012292 | -0.0074779 | 0.066166 | 0.068883 | 0.062945 | 0.13393 | 0.12069 | -0.040158 | 0.05635 | 0.000747 | 0.17574 | 0.091937 | 0.41668 | -0.099689 | 56.4886 | 1.6762 | 54.2838 | 56.5007 | 56.6968 | 56.494 | -66.8546 | 66.3401 | -56.4313 | 66.3997 | 66.4406 | 0.10044 | -56.5151 | -56.1904 | -0.4148 | -0.10633 | 122.9284 | 120.7236 | 121.1384 | 0.08975 | -0.11309 | 66.6156 | 66.5318 | 66.8565 | 66.4962 | -56.7067 | 122.9405 | 123.1366 | 122.9338 | 68.116 | -123.4617
3681.7969 | 123.1705 | -66.4398 | 56.6162 | 0.012286 | -0.073384 | 0.022684 | -0.0052544 | -0.010151 | 0.012292 | 0.00015261 | 0.066593 | 0.068456 | 0.062518 | 0.13372 | 0.12112 | -0.040158 | 0.05635 | 0.000747 | 0.1849 | 0.1011 | 0.40753 | -0.09511 | 56.4932 | 1.6716 | 54.2884 | 56.4961 | 56.7014 | 56.526 | -66.8592 | 66.3447 | -56.4313 | 66.3997 | 66.4406 | 0.095857 | -56.5151 | -56.2087 | -0.41938 | -0.12006 | 122.933 | 120.7282 | 121.1476 | 0.085173 | -0.090191 | 66.6247 | 66.5409 | 66.8473 | 66.4962 | -56.7113 | 122.936 | 123.1412 | 122.9658 | 68.1114 | -123.4754
3682.7969 | 123.1338 | -66.4352 | 56.6025 | -0.010607 | -0.073384 | 0.022257 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | 0.066379 | 0.06867 | 0.062731 | 0.13351 | 0.12069 | -0.049315 | 0.05635 | 0.000747 | 0.17117 | 0.1011 | 0.40295 | -0.090531 | 56.4932 | 1.6762 | 54.2334 | 56.5053 | 56.7014 | 56.5214 | -66.8546 | 66.3447 | -56.4313 | 66.3859 | 66.436 | 0.091278 | -56.5014 | -56.1995 | -0.41938 | -0.097174 | 122.9284 | 120.6687 | 121.088 | 0.098906 | -0.081036 | 66.6064 | 66.5363 | 66.8382 | 66.4916 | -56.693 | 122.9405 | 123.1366 | 122.9567 | 68.1114 | -123.4571
3683.7969 | 123.1796 | -66.4352 | 56.6162 | 0.0046549 | -0.073598 | 0.022257 | -0.004827 | -0.010578 | 0.012292 | 0.00015261 | 0.066379 | 0.068242 | 0.062518 | 0.13351 | 0.12091 | -0.044736 | 0.060928 | -0.003831 | 0.17117 | 0.1011 | 0.41668 | -0.090531 | 56.4977 | 1.6762 | 54.238 | 56.5053 | 56.6968 | 56.5214 | -66.8546 | 66.3447 | -56.445 | 66.3905 | 66.4314 | 0.0867 | -56.5151 | -56.1995 | -0.41938 | -0.11091 | 122.933 | 120.6732 | 121.0926 | 0.080595 | -0.094769 | 66.6064 | 66.5363 | 66.8519 | 66.4962 | -56.7067 | 122.9405 | 123.132 | 122.9567 | 68.1114 | -123.4708
3684.7969 | 123.2117 | -66.3986 | 56.5933 | 0.0046549 | -0.073384 | 0.022043 | -0.0050408 | -0.010365 | 0.011865 | 0.0077831 | 0.066379 | 0.06867 | 0.062731 | 0.13351 | 0.12069 | -0.040158 | 0.051771 | -0.003831 | 0.18032 | 0.10567 | 0.39837 | -0.090531 | 56.4886 | 1.6716 | 54.2197 | 56.5007 | 56.6968 | 56.5077 | -66.8546 | 66.3081 | -56.413 | 66.3585 | 66.3948 | 0.0867 | -56.4876 | -56.195 | -0.456 | -0.092597 | 122.8872 | 120.6183 | 121.0743 | 0.10348 | -0.085617 | 66.5789 | 66.5043 | 66.797 | 66.4504 | -56.6839 | 122.8993 | 123.0954 | 122.9063 | 68.0702 | -123.4479
3685.7969 | 123.1064 | -66.4398 | 56.6345 | -0.010607 | -0.073598 | 0.02247 | -0.0050408 | -0.010365 | 0.011651 | -0.0074779 | 0.066593 | 0.068242 | 0.062518 | 0.13372 | 0.12069 | -0.03558 | 0.060928 | -0.008409 | 0.17574 | 0.10567 | 0.4121 | -0.090531 | 56.4977 | 1.6807 | 54.2151 | 56.4961 | 56.6922 | 56.5077 | -66.8592 | 66.3493 | -56.4588 | 66.4042 | 66.4314 | 0.082122 | -56.5288 | -56.2224 | -0.41938 | -0.13837 | 122.9376 | 120.6549 | 121.0743 | 0.057706 | -0.12682 | 66.6156 | 66.5455 | 66.8519 | 66.5007 | -56.7251 | 122.936 | 123.132 | 122.9475 | 68.1206 | -123.4937
3686.7969 | 123.1522 | -66.4444 | 56.6025 | -0.010607 | -0.074025 | 0.02247 | -0.0050408 | -0.010578 | 0.012078 | 0.00015261 | 0.066379 | 0.068456 | 0.062304 | 0.13351 | 0.12091 | -0.044736 | 0.060928 | -0.003831 | 0.1849 | 0.096516 | 0.40295 | -0.090531 | 56.4886 | 1.6762 | 54.2151 | 56.5007 | 56.7014 | 56.5214 | -66.8546 | 66.3539 | -56.4176 | 66.3997 | 66.4406 | 0.0867 | -56.506 | -56.1995 | -0.41022 | -0.10175 | 122.933 | 120.6595 | 121.0697 | 0.098906 | -0.081036 | 66.6293 | 66.5409 | 66.8473 | 66.5053 | -56.693 | 122.9451 | 123.1458 | 122.9658 | 68.1206 | -123.4571
3687.7969 | 123.1018 | -66.4581 | 56.6162 | -0.0029761 | -0.074025 | 0.022257 | -0.0050408 | -0.010792 | 0.011865 | -0.0074779 | 0.066379 | 0.06867 | 0.062945 | 0.13351 | 0.12069 | -0.044736 | 0.051771 | 0.000747 | 0.18032 | 0.1011 | 0.41668 | -0.09511 | 56.4977 | 1.6899 | 54.2243 | 56.5007 | 56.6968 | 56.5031 | -66.8638 | 66.363 | -56.4359 | 66.4134 | 66.4589 | 0.095857 | -56.5151 | -56.1995 | -0.40565 | -0.11548 | 122.9559 | 120.6824 | 121.088 | 0.080595 | -0.11308 | 66.6385 | 66.5592 | 66.8748 | 66.5099 | -56.7113 | 122.9589 | 123.1549 | 122.9613 | 68.148 | -123.48
3688.7969 | 123.1934 | -66.4444 | 56.5842 | -0.0029761 | -0.073811 | 0.02247 | -0.0050408 | -0.0099374 | 0.011651 | -0.0074779 | 0.066593 | 0.068456 | 0.062731 | 0.13351 | 0.12091 | -0.040158 | 0.060928 | -0.008409 | 0.1849 | 0.10567 | 0.40295 | -0.090531 | 56.4932 | 1.6991 | 54.2426 | 56.4961 | 56.6968 | 56.5306 | -66.8592 | 66.3539 | -56.3993 | 66.4042 | 66.436 | 0.082122 | -56.4785 | -56.1812 | -0.4148 | -0.08802 | 122.9376 | 120.687 | 121.1018 | 0.11264 | -0.053568 | 66.6293 | 66.5501 | 66.8473 | 66.5053 | -56.6747 | 122.9405 | 123.1412 | 122.975 | 68.1435 | -123.4434
3689.7969 | 123.2254 | -66.4078 | 56.6162 | -0.0029761 | -0.074025 | 0.02247 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | 0.066379 | 0.06867 | 0.062731 | 0.13351 | 0.12069 | -0.040158 | 0.051771 | -0.003831 | 0.16659 | 0.096516 | 0.40753 | -0.09511 | 56.4932 | 1.6945 | 54.2243 | 56.5053 | 56.6968 | 56.5214 | -66.8638 | 66.3127 | -56.4496 | 66.3676 | 66.4039 | 0.091279 | -56.5197 | -56.2087 | -0.456 | -0.11091 | 122.9009 | 120.632 | 121.088 | 0.080595 | -0.094769 | 66.5744 | 66.5043 | 66.8153 | 66.4595 | -56.7113 | 122.9131 | 123.1046 | 122.9292 | 68.1023 | -123.48
3690.7969 | 123.1247 | -61.4594 | 61.6287 | -0.0029761 | -0.074025 | 0.022257 | -0.0050408 | -0.010151 | 0.011865 | 0.00015261 | -0.043003 | 0.02081 | 0.017438 | 0.05466 | 0.0068176 | -0.040158 | 0.060928 | -0.003831 | 0.17574 | 0.096516 | 0.40295 | -0.09511 | 0.083464 | 0.064461 | 0.039802 | 0.24933 | 0.44867 | 0.40609 | -0.51672 | 61.3642 | -61.453 | 61.4192 | 61.4555 | 0.091279 | -61.5322 | -61.2258 | 60.9426 | -61.3794 | 61.5428 | 61.4992 | 0.55652 | -61.18 | -61.2226 | 61.6351 | 61.5559 | 61.8623 | 61.5203 | -61.7238 | 61.7087 | 61.908 | 61.8654 | 61.5238 | -62.1454
3691.7969 | 123.1201 | -61.4685 | 61.6104 | -0.010607 | -0.073811 | 0.022257 | -0.0052544 | -0.010365 | 0.011865 | 0.0077831 | -0.043217 | 0.020597 | 0.017438 | 0.054232 | 0.006604 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.096516 | 0.40295 | -0.090531 | 0.010205 | 0.078197 | -0.028879 | 0.18524 | 0.37542 | 0.35115 | -0.42972 | 61.378 | -61.4255 | 61.4192 | 61.4647 | 0.0867 | -61.5139 | -61.2075 | 61.0388 | -61.4252 | 61.4787 | 61.4396 | 0.40084 | -61.235 | -61.2593 | 61.6534 | 61.565 | 61.8715 | 61.5203 | -61.7009 | 61.6537 | 61.8439 | 61.8197 | 61.5467 | -62.0401
3692.8594 | 123.1613 | -61.4502 | 61.6379 | -0.010607 | -0.073598 | 0.02247 | -0.0052544 | -0.010151 | 0.011651 | 0.00015261 | -0.043431 | 0.021024 | 0.017011 | 0.054019 | 0.006604 | -0.040158 | 0.05635 | -0.003831 | 0.16659 | 0.12399 | 0.42126 | -0.09511 | 0.010205 | 0.078197 | -0.038036 | 0.17608 | 0.37542 | 0.34657 | -0.42514 | 61.3551 | -61.4713 | 61.41 | 61.4464 | 0.091279 | -61.5139 | -61.2166 | 61.0251 | -61.4618 | 61.4604 | 61.4122 | 0.3871 | -61.2625 | -61.2913 | 61.6168 | 61.5742 | 61.8715 | 61.5065 | -61.733 | 61.6263 | 61.8256 | 61.7968 | 61.5284 | -62.063
3693.7969 | 123.1522 | -61.4594 | 61.5967 | -0.0029761 | -0.073598 | 0.02247 | -0.004827 | -0.010151 | 0.011865 | -0.015108 | -0.043217 | 0.020597 | 0.016797 | 0.054232 | 0.006604 | -0.044736 | 0.060928 | -0.003831 | 0.17117 | 0.096516 | 0.40295 | -0.085952 | 0.010205 | 0.046146 | -0.038036 | 0.17608 | 0.37084 | 0.35115 | -0.41598 | 61.3734 | -61.4255 | 61.4146 | 61.4555 | 0.082121 | -61.5002 | -61.1937 | 61.0434 | -61.4206 | 61.4696 | 61.4213 | 0.37795 | -61.2258 | -61.2455 | 61.6305 | 61.5559 | 61.8623 | 61.5203 | -61.6826 | 61.6354 | 61.8302 | 61.8105 | 61.5055 | -62.0127
3694.7969 | 123.2529 | -61.4319 | 61.5829 | -0.0029761 | -0.073598 | 0.022043 | -0.0052544 | -0.010365 | 0.011865 | 0.00015261 | -0.043003 | 0.020169 | 0.017224 | 0.054232 | 0.0063904 | -0.044736 | 0.051771 | -0.003831 | 0.1849 | 0.096516 | 0.40753 | -0.090531 | -0.003531 | 0.046146 | -0.038036 | 0.17608 | 0.37084 | 0.35115 | -0.41141 | 61.3414 | -61.398 | 61.3871 | 61.4281 | 0.0867 | -61.4864 | -61.1754 | 61.0205 | -61.4069 | 61.4284 | 61.3938 | 0.37337 | -61.2121 | -61.2318 | 61.6168 | 61.5284 | 61.8394 | 61.4837 | -61.6735 | 61.608 | 61.8027 | 61.783 | 61.478 | -61.9944
3695.7969 | 123.1567 | -61.4777 | 61.615 | -0.0029761 | -0.073598 | 0.02247 | -0.004827 | -0.0099374 | 0.012078 | 0.00015261 | -0.043217 | 0.020597 | 0.017224 | 0.054446 | 0.0063904 | -0.040158 | 0.051771 | -0.003831 | 0.13912 | 0.096516 | 0.40295 | -0.09511 | 0.005626 | 0.050725 | -0.033458 | 0.16692 | 0.36168 | 0.33741 | -0.42514 | 61.3826 | -61.4759 | 61.4375 | 61.4738 | 0.091279 | -61.5185 | -61.212 | 61.0525 | -61.4481 | 61.4833 | 61.4442 | 0.39168 | -61.2533 | -61.2776 | 61.6168 | 61.5742 | 61.8806 | 61.5294 | -61.7101 | 61.6446 | 61.8393 | 61.8151 | 61.5284 | -62.0401
3696.7969 | 123.2712 | -61.4594 | 61.5829 | -0.0029761 | -0.073598 | 0.022043 | -0.0052544 | -0.010151 | 0.012078 | 0.0077831 | -0.043431 | 0.020597 | 0.017011 | 0.054232 | 0.0061766 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.10567 | 0.41668 | -0.090531 | 0.001048 | 0.036989 | -0.042615 | 0.1715 | 0.36626 | 0.33741 | -0.41598 | 61.3688 | -61.4072 | 61.4192 | 61.4555 | 0.0867 | -61.4773 | -61.1663 | 61.0434 | -61.4114 | 61.4604 | 61.4167 | 0.37337 | -61.2167 | -61.2455 | 61.6351 | 61.565 | 61.876 | 61.5157 | -61.6735 | 61.6308 | 61.8256 | 61.7968 | 61.4963 | -61.9989
3697.7969 | 123.1979 | -61.4822 | 61.6058 | -0.0029761 | -0.073384 | 0.02247 | -0.0052544 | -0.010365 | 0.011865 | -0.0074779 | -0.043003 | 0.020383 | 0.017011 | 0.05466 | 0.0063904 | -0.049315 | 0.060928 | -0.003831 | 0.16659 | 0.096516 | 0.41668 | -0.09511 | -0.003531 | 0.046146 | -0.038036 | 0.17608 | 0.36168 | 0.33741 | -0.41141 | 61.3871 | -61.4392 | 61.4329 | 61.4784 | 0.091279 | -61.5093 | -61.1892 | 61.0708 | -61.4298 | 61.4787 | 61.4442 | 0.37337 | -61.2442 | -61.2684 | 61.6488 | 61.5788 | 61.8989 | 61.5432 | -61.7009 | 61.6583 | 61.8439 | 61.8196 | 61.5284 | -62.0172
3698.7969 | 123.2986 | -61.4319 | 61.6104 | -0.0029761 | -0.073598 | 0.022043 | -0.0054682 | -0.010578 | 0.012292 | 0.00015261 | -0.043217 | 0.02081 | 0.016797 | 0.054232 | 0.0061766 | -0.040158 | 0.05635 | 0.000747 | 0.14827 | 0.1011 | 0.40295 | -0.081373 | 0.001048 | 0.041567 | -0.042615 | 0.1715 | 0.36626 | -0.10214 | -0.41141 | 61.3505 | -61.4621 | 61.3917 | 61.4326 | 0.08212 | -61.5093 | -61.2075 | 61.0205 | -61.4389 | 61.4329 | 61.3893 | 0.36879 | -61.2442 | -61.7125 | 61.5802 | 61.533 | 61.8348 | 61.4882 | -61.6918 | 61.6034 | 61.7981 | 61.3297 | 61.4735 | -62.0218
3699.7969 | 123.2529 | -61.4319 | 61.647 | -0.0029761 | -0.073811 | 0.02247 | -0.004827 | -0.010151 | 0.012292 | 0.00015261 | -0.043431 | 0.020597 | 0.016797 | 0.05466 | 0.0063904 | -0.040158 | 0.065507 | -0.003831 | 0.18032 | 0.1011 | 0.40753 | -0.09511 | -0.00811 | 0.03241 | -0.042615 | 0.16692 | 0.35252 | -0.0884 | -0.41598 | 61.3368 | -61.4667 | 61.3917 | 61.4281 | 0.091279 | -61.5459 | -61.2395 | 61.0159 | -61.4801 | 61.4238 | 61.3893 | 0.37337 | -61.2945 | -61.7354 | 61.6122 | 61.533 | 61.8394 | 61.4974 | -61.7421 | 61.5988 | 61.7844 | 61.3435 | 61.4643 | -62.063
3700.7969 | 123.2529 | -61.4319 | 61.6104 | -0.0029761 | -0.073598 | 0.022257 | -0.0050408 | -0.010365 | 0.011865 | 0.00015261 | -0.043003 | 0.020597 | 0.017011 | 0.054232 | 0.0063904 | -0.040158 | 0.05635 | -0.003831 | 0.18032 | 0.096516 | 0.39837 | -0.085952 | 0.005626 | 0.041567 | -0.047194 | 0.1715 | 0.36168 | -0.10214 | -0.40225 | 61.3459 | -61.4301 | 61.3917 | 61.4281 | 0.082121 | -61.5139 | -61.212 | 61.0296 | -61.4389 | 61.4375 | 61.3847 | 0.35505 | -61.2487 | -61.7125 | 61.6122 | 61.5284 | 61.8303 | 61.4882 | -61.6964 | 61.6034 | 61.7936 | 61.3297 | 61.4735 | -62.0127
3701.7969 | 123.3032 | -61.4639 | 61.6241 | -0.010607 | -0.073598 | 0.022257 | -0.0050408 | -0.0099374 | 0.012078 | 0.00015261 | -0.043217 | 0.021024 | 0.017011 | 0.054232 | 0.0068176 | -0.044736 | 0.05635 | -0.012988 | 0.16201 | 0.096516 | 0.39837 | -0.09511 | 0.001048 | 0.041567 | -0.042615 | 0.16692 | 0.36168 | -0.10671 | -0.40683 | 61.3688 | -61.4621 | 61.4192 | 61.4509 | 0.082122 | -61.5276 | -61.2258 | 61.0571 | -61.4572 | 61.465 | 61.4213 | 0.36421 | -61.2625 | -61.7309 | 61.6259 | 61.5604 | 61.8623 | 61.5203 | -61.7193 | 61.6308 | 61.8256 | 61.3572 | 61.5055 | -62.031
3702.7969 | 123.2437 | -61.4548 | 61.6287 | -0.010607 | -0.073598 | 0.022257 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | -0.043217 | 0.020383 | 0.017224 | 0.054446 | 0.006604 | -0.044736 | 0.065507 | -0.003831 | 0.15743 | 0.10567 | 0.40753 | -0.090531 | 0.001048 | 0.046146 | -0.047194 | 0.15776 | 0.36168 | -0.10671 | -0.40683 | 61.3642 | -61.4713 | 61.41 | 61.4509 | 0.0867 | -61.523 | -61.2212 | 61.0479 | -61.471 | 61.4558 | 61.4076 | 0.35963 | -61.267 | -61.7354 | 61.6122 | 61.5604 | 61.8623 | 61.5203 | -61.7193 | 61.6125 | 61.8165 | 61.3481 | 61.5009 | -62.0355
3703.8594 | 123.1659 | -61.4822 | 61.6425 | 0.0046549 | -0.073811 | 0.022257 | -0.0046134 | -0.010792 | 0.011865 | -0.0074779 | -0.043003 | 0.020597 | 0.017224 | 0.054446 | 0.0063904 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.096516 | 0.41668 | -0.09511 | -0.00811 | 0.041567 | -0.033458 | 0.15318 | 0.35252 | -0.10214 | -0.40225 | 61.3871 | -61.4667 | 61.4421 | 61.4784 | 0.091279 | -61.5459 | -61.2258 | 61.08 | -61.4893 | 61.4741 | 61.4488 | 0.36879 | -61.2899 | -61.7446 | 61.658 | 61.5788 | 61.8989 | 61.5386 | -61.7376 | 61.6354 | 61.8348 | 61.3801 | 61.5238 | -62.0447
3704.7969 | 123.2162 | -61.4822 | 61.6837 | -0.0029761 | -0.073598 | 0.02247 | -0.0050408 | -0.010578 | 0.011865 | 0.00015261 | -0.04279 | 0.020597 | 0.017011 | 0.054446 | 0.0068176 | -0.040158 | 0.060928 | -0.003831 | 0.16659 | 0.1011 | 0.4121 | -0.099689 | 0.001048 | 0.046146 | -0.038036 | 0.16692 | 0.36168 | -0.10214 | -0.40225 | 61.3826 | -61.5171 | 61.4421 | 61.4784 | 0.095858 | -61.5826 | -61.2716 | 61.08 | -61.5167 | 61.4833 | 61.4442 | 0.36421 | -61.322 | -61.7858 | 61.6488 | 61.5833 | 61.8943 | 61.5432 | -61.7833 | 61.6492 | 61.8439 | 61.3801 | 61.5284 | -62.0859
3705.7969 | 123.3124 | -61.4182 | 61.6013 | -0.0029761 | -0.073811 | 0.022257 | -0.0052544 | -0.010578 | 0.012078 | -0.0074779 | -0.043217 | 0.02081 | 0.017224 | 0.05466 | 0.0063904 | -0.049315 | 0.060928 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.085952 | -0.003531 | 0.041567 | -0.038036 | 0.16234 | 0.35252 | -0.10671 | -0.40225 | 61.3322 | -61.4255 | 61.3688 | 61.4143 | 0.082121 | -61.5002 | -61.1937 | 61.0159 | -61.4389 | 61.4146 | 61.3801 | 0.36421 | -61.2487 | -61.708 | 61.5939 | 61.5192 | 61.8257 | 61.4791 | -61.6872 | 61.5805 | 61.7707 | 61.3114 | 61.4597 | -62.0035
3706.7969 | 123.2712 | -61.4594 | 61.6104 | -0.0029761 | -0.073811 | 0.022257 | -0.004827 | -0.010578 | 0.012078 | 0.00015261 | -0.043003 | 0.020383 | 0.017224 | 0.054446 | 0.006604 | -0.044736 | 0.065507 | -0.008409 | 0.16659 | 0.096516 | 0.40295 | -0.090531 | -0.00811 | 0.041567 | -0.042615 | 0.16234 | 0.35252 | -0.11587 | -0.39767 | 61.3688 | -61.4438 | 61.4146 | 61.4509 | 0.082122 | -61.5139 | -61.2075 | 61.0617 | -61.4481 | 61.4512 | 61.4167 | 0.35505 | -61.2579 | -61.7263 | 61.6259 | 61.5559 | 61.8623 | 61.5249 | -61.7009 | 61.6217 | 61.8119 | 61.3435 | 61.5009 | -62.0081
3707.7969 | 123.2666 | -61.441 | 61.6241 | -0.0029761 | -0.073811 | 0.021829 | -0.0050408 | -0.010578 | 0.012078 | 0.00015261 | -0.043217 | 0.02081 | 0.017224 | 0.054446 | 0.006604 | -0.044736 | 0.060928 | 0.000747 | 0.17117 | 0.096516 | 0.42126 | -0.09511 | -0.003531 | 0.03241 | -0.047194 | 0.16234 | 0.3571 | -0.10671 | -0.40225 | 61.3459 | -61.453 | 61.3963 | 61.4418 | 0.095857 | -61.5276 | -61.2029 | 61.0388 | -61.4618 | 61.4375 | 61.3938 | 0.35505 | -61.267 | -61.7309 | 61.6122 | 61.5376 | 61.8623 | 61.502 | -61.7193 | 61.6034 | 61.7981 | 61.3343 | 61.4734 | -62.0264
3708.875 | 123.2941 | -61.5097 | 61.6745 | -0.0029761 | -0.073811 | 0.021829 | -0.0052544 | -0.010151 | 0.012292 | -0.0074779 | -0.043217 | 0.020597 | 0.017438 | 0.054232 | 0.006604 | -0.049315 | 0.05635 | 0.000747 | 0.13454 | 0.10567 | 0.40295 | -0.099689 | 0.001048 | 0.046146 | -0.042615 | 0.16692 | 0.3571 | -0.11129 | -0.40225 | 61.41 | -61.54 | 61.4604 | 61.5105 | 0.10044 | -61.5688 | -61.2716 | 61.1075 | -61.5076 | 61.5108 | 61.4671 | 0.35963 | -61.3174 | -61.7858 | 61.6442 | 61.6154 | 61.9127 | 61.5661 | -61.7742 | 61.6766 | 61.8668 | 61.3984 | 61.5559 | -62.0767
3709.7969 | 123.2574 | -61.4594 | 61.6928 | 0.012286 | -0.073598 | 0.022257 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | -0.043003 | 0.02081 | 0.017011 | 0.054446 | 0.0061766 | -0.044736 | 0.05635 | -0.003831 | 0.18032 | 0.1011 | 0.39837 | -0.099689 | 0.005626 | 0.036989 | -0.038036 | 0.16692 | 0.3571 | -0.11129 | -0.39767 | 61.3597 | -61.5125 | 61.4146 | 61.4555 | 0.095858 | -61.5917 | -61.2944 | 61.0617 | -61.5259 | 61.465 | 61.4213 | 0.35963 | -61.3357 | -61.8041 | 61.6397 | 61.5604 | 61.8577 | 61.5157 | -61.7925 | 61.6263 | 61.8165 | 61.3481 | 61.4963 | -62.0905
3710.7969 | 123.2712 | -61.4594 | 61.6333 | -0.0029761 | -0.073811 | 0.02247 | -0.004827 | -0.010365 | 0.011651 | 0.00015261 | -0.042362 | 0.020597 | 0.017011 | 0.054232 | 0.0063904 | -0.040158 | 0.051771 | -0.003831 | 0.16201 | 0.1011 | 0.38921 | -0.09511 | 0.001048 | 0.036989 | -0.051772 | 0.16234 | 0.35252 | -0.10671 | -0.40225 | 61.3642 | -61.4713 | 61.4192 | 61.4555 | 0.091279 | -61.5322 | -61.2441 | 61.0571 | -61.471 | 61.4604 | 61.4076 | 0.35048 | -61.2808 | -61.74 | 61.6214 | 61.5604 | 61.8486 | 61.5111 | -61.7284 | 61.6217 | 61.8119 | 61.3526 | 61.4963 | -62.0355
3711.7969 | 123.2986 | -61.4731 | 61.615 | -0.0029761 | -0.073598 | 0.022043 | -0.0050408 | -0.010365 | 0.012078 | -0.0074779 | -0.042362 | 0.020597 | 0.017011 | 0.054446 | 0.006604 | -0.044736 | 0.051771 | -0.008409 | 0.1849 | 0.096516 | 0.40295 | -0.090531 | 0.001048 | 0.046146 | -0.051772 | 0.15776 | 0.35252 | -0.11129 | -0.40225 | 61.3826 | -61.4301 | 61.4283 | 61.4647 | 0.082122 | -61.5185 | -61.212 | 61.0708 | -61.4572 | 61.4741 | 61.4213 | 0.35048 | -61.2625 | -61.7263 | 61.658 | 61.5696 | 61.876 | 61.5249 | -61.7055 | 61.6308 | 61.8256 | 61.3618 | 61.5192 | -62.0172
3712.7969 | 123.3124 | -61.4502 | 61.615 | 0.0046549 | -0.073598 | 0.022043 | -0.0052544 | -0.010365 | 0.012078 | -0.015108 | -0.042362 | 0.020597 | 0.017438 | 0.054232 | 0.0063904 | -0.049315 | 0.065507 | 0.000747 | 0.17117 | 0.1011 | 0.39837 | -0.090531 | 0.010205 | 0.041567 | -0.042615 | 0.16234 | 0.35252 | -0.10671 | -0.40225 | 61.3597 | -61.4438 | 61.4009 | 61.4509 | 0.091278 | -61.5139 | -61.2166 | 61.0479 | -61.4526 | 61.4604 | 61.4076 | 0.35963 | -61.2625 | -61.7217 | 61.6214 | 61.5513 | 61.8486 | 61.5157 | -61.7055 | 61.6125 | 61.8027 | 61.3435 | 61.4918 | -62.0172
3713.7969 | 123.3124 | -61.4639 | 61.6562 | -0.010607 | -0.073598 | 0.022257 | -0.0054682 | -0.010151 | 0.011865 | 0.00015261 | -0.042149 | 0.020597 | 0.017011 | 0.054446 | 0.006604 | -0.044736 | 0.060928 | 0.005325 | 0.17117 | 0.11025 | 0.40295 | -0.090531 | 0.005626 | 0.036989 | -0.042615 | 0.16234 | 0.35252 | -0.11587 | -0.40683 | 61.3734 | -61.485 | 61.4192 | 61.4693 | 0.095856 | -61.5459 | -61.2532 | 61.0571 | -61.4938 | 61.4696 | 61.4213 | 0.36421 | -61.3037 | -61.7721 | 61.6351 | 61.5742 | 61.8669 | 61.5249 | -61.7467 | 61.6263 | 61.8165 | 61.3481 | 61.5009 | -62.063
3714.7969 | 123.3261 | -61.4273 | 61.6608 | 0.012286 | -0.073811 | 0.022257 | -0.004827 | -0.010578 | 0.012078 | -0.0074779 | -0.042362 | 0.020597 | 0.017652 | 0.05466 | 0.0063904 | -0.040158 | 0.051771 | -0.003831 | 0.1849 | 0.10567 | 0.39837 | -0.09511 | 0.001048 | 0.03241 | -0.047194 | 0.16234 | 0.36168 | -0.10671 | -0.39767 | 61.3322 | -61.4759 | 61.3871 | 61.4235 | 0.091279 | -61.5551 | -61.2624 | 61.0296 | -61.4984 | 61.4284 | 61.3801 | 0.35047 | -61.2991 | -61.7675 | 61.6122 | 61.533 | 61.8257 | 61.4791 | -61.7559 | 61.5896 | 61.789 | 61.3206 | 61.4597 | -62.0584
3715.7969 | 123.3582 | -61.4365 | 61.6333 | 0.0046549 | -0.073811 | 0.022257 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | -0.042149 | 0.020169 | 0.017438 | 0.054446 | 0.0068176 | -0.049315 | 0.05635 | -0.008409 | 0.16201 | 0.091937 | 0.41668 | -0.090531 | -0.00811 | 0.041567 | -0.038036 | 0.16234 | 0.34794 | -0.11129 | -0.39767 | 61.3459 | -61.4713 | 61.3871 | 61.4281 | 0.082122 | -61.5414 | -61.2166 | 61.0388 | -61.471 | 61.4284 | 61.3984 | 0.35963 | -61.2854 | -61.7446 | 61.5985 | 61.5284 | 61.8531 | 61.4928 | -61.7238 | 61.5988 | 61.7844 | 61.3252 | 61.478 | -62.031
3716.7969 | 123.3627 | -61.4182 | 61.6379 | -0.0029761 | -0.073811 | 0.022257 | -0.0052544 | -0.010151 | 0.011651 | 0.00015261 | -0.042576 | 0.02081 | 0.017652 | 0.054019 | 0.006604 | -0.053893 | 0.051771 | -0.003831 | 0.17117 | 0.10567 | 0.40753 | -0.09511 | 0.005626 | 0.036989 | -0.042615 | 0.16692 | 0.3571 | -0.10671 | -0.40225 | 61.323 | -61.4667 | 61.3643 | 61.4143 | 0.091279 | -61.5322 | -61.2304 | 61.0159 | -61.471 | 61.4238 | 61.3755 | 0.35963 | -61.2808 | -61.7446 | 61.5893 | 61.5238 | 61.8257 | 61.4699 | -61.733 | 61.5851 | 61.7753 | 61.3114 | 61.4551 | -62.0401
3717.7969 | 123.3124 | -61.4685 | 61.6196 | 0.0046549 | -0.073811 | 0.02247 | -0.0050408 | -0.010578 | 0.012292 | 0.00015261 | -0.042576 | 0.02081 | 0.017865 | 0.054446 | 0.006604 | -0.044736 | 0.060928 | -0.008409 | 0.17574 | 0.091937 | 0.41668 | -0.081373 | -0.003531 | 0.03241 | -0.038036 | 0.16234 | 0.3571 | -0.11587 | -0.38851 | 61.3871 | -61.4438 | 61.4238 | 61.4601 | 0.072964 | -61.5276 | -61.2029 | 61.08 | -61.4572 | 61.465 | 61.4305 | 0.35047 | -61.2625 | -61.7354 | 61.6442 | 61.5604 | 61.8852 | 61.5294 | -61.7009 | 61.6308 | 61.8256 | 61.3526 | 61.5009 | -62.0081
3718.7969 | 123.3398 | -61.4594 | 61.6745 | -0.010607 | -0.073598 | 0.022043 | -0.0052544 | -0.010365 | 0.011865 | 0.0077831 | -0.04279 | 0.020597 | 0.018079 | 0.054446 | 0.006604 | -0.044736 | 0.05635 | -0.008409 | 0.17117 | 0.10567 | 0.4121 | -0.09511 | 0.010205 | 0.041567 | -0.047194 | 0.15776 | 0.34337 | -0.12045 | -0.39309 | 61.3642 | -61.5033 | 61.4146 | 61.4509 | 0.086701 | -61.5688 | -61.2624 | 61.0663 | -61.5167 | 61.4696 | 61.4122 | 0.3459 | -61.3311 | -61.795 | 61.6305 | 61.565 | 61.8715 | 61.5157 | -61.7696 | 61.6171 | 61.8027 | 61.3389 | 61.5009 | -62.0676
3719.7969 | 123.3627 | -61.4456 | 61.6699 | -0.0029761 | -0.074025 | 0.021829 | -0.0052544 | -0.010151 | 0.011865 | 0.00015261 | -0.042576 | 0.02081 | 0.017224 | 0.05466 | 0.0063904 | -0.049315 | 0.05635 | -0.012988 | 0.16201 | 0.096516 | 0.41668 | -0.09511 | 0.001048 | 0.050725 | -0.042615 | 0.15318 | 0.3571 | -0.11587 | -0.39767 | 61.3505 | -61.5079 | 61.3963 | 61.4326 | 0.082122 | -61.5734 | -61.2532 | 61.048 | -61.5167 | 61.4467 | 61.403 | 0.35505 | -61.3128 | -61.7858 | 61.6076 | 61.5421 | 61.8623 | 61.502 | -61.765 | 61.5988 | 61.8027 | 61.3297 | 61.4963 | -62.0676
3720.7969 | 123.2758 | -61.4822 | 61.6745 | 0.0046549 | -0.073811 | 0.022257 | -0.0050408 | -0.010365 | 0.012078 | 0.00015261 | -0.042576 | 0.020383 | 0.017224 | 0.054232 | 0.0063904 | -0.044736 | 0.051771 | -0.003831 | 0.1849 | 0.10567 | 0.4121 | -0.09511 | 0.005626 | 0.041567 | -0.042615 | 0.16234 | 0.34794 | -0.11129 | -0.39309 | 61.3871 | -61.4896 | 61.4375 | 61.4784 | 0.091279 | -61.5688 | -61.2624 | 61.0891 | -61.5122 | 61.4879 | 61.4396 | 0.35047 | -61.3266 | -61.7858 | 61.6671 | 61.5879 | 61.8943 | 61.534 | -61.7696 | 61.6446 | 61.8302 | 61.3709 | 61.5238 | -62.0676
3721.7969 | 123.3444 | -61.4182 | 61.6608 | 0.0046549 | -0.073811 | 0.022257 | -0.0050408 | -0.010151 | 0.012292 | -0.0074779 | -0.042576 | 0.021024 | 0.017652 | 0.054446 | 0.006604 | -0.040158 | 0.051771 | -0.003831 | 0.1849 | 0.10567 | 0.42126 | -0.081373 | 0.005626 | 0.046146 | -0.038036 | 0.16234 | 0.35252 | -0.11129 | -0.39309 | 61.3368 | -61.4759 | 61.378 | 61.4143 | 0.077542 | -61.5551 | -61.2395 | 61.0251 | -61.4984 | 61.4238 | 61.3801 | 0.35505 | -61.3082 | -61.7721 | 61.6031 | 61.5238 | 61.8394 | 61.4699 | -61.7421 | 61.5805 | 61.7707 | 61.3069 | 61.4643 | -62.0539
3722.7969 | 123.2483 | -61.4822 | 61.7065 | 0.0046549 | -0.073384 | 0.02247 | -0.004827 | -0.010151 | 0.011651 | 0.0077831 | -0.042576 | 0.02081 | 0.017438 | 0.054873 | 0.0061766 | -0.044736 | 0.051771 | -0.008409 | 0.17574 | 0.096516 | 0.40295 | -0.09511 | -0.003531 | 0.050725 | -0.042615 | 0.15318 | 0.33879 | -0.10671 | -0.39309 | 61.3871 | -61.5308 | 61.4375 | 61.4738 | 0.086701 | -61.61 | -61.3036 | 61.0891 | -61.5534 | 61.4787 | 61.4396 | 0.35047 | -61.3678 | -61.8133 | 61.658 | 61.5788 | 61.8852 | 61.534 | -61.8017 | 61.6354 | 61.821 | 61.3755 | 61.533 | -62.0996
3723.7969 | 123.3673 | -61.4502 | 61.6379 | 0.019917 | -0.073811 | 0.022257 | -0.0052544 | -0.010365 | 0.011865 | -0.0074779 | -0.042576 | 0.02081 | 0.017652 | 0.05466 | 0.006604 | -0.040158 | 0.051771 | -0.003831 | 0.16201 | 0.10567 | 0.39837 | -0.090531 | 0.005626 | 0.041567 | -0.047194 | 0.15776 | 0.34794 | -0.10671 | -0.38851 | 61.3597 | -61.4759 | 61.41 | 61.4464 | 0.0867 | -61.5322 | -61.2395 | 61.0617 | -61.4801 | 61.4558 | 61.403 | 0.34132 | -61.2899 | -61.7446 | 61.6122 | 61.5559 | 61.8486 | 61.502 | -61.7284 | 61.608 | 61.7981 | 61.3435 | 61.4918 | -62.0264
3724.7969 | 123.3215 | -61.4822 | 61.6745 | -0.010607 | -0.074239 | 0.021829 | -0.004827 | -0.010578 | 0.011651 | 0.00015261 | -0.042576 | 0.02081 | 0.017652 | 0.054446 | 0.0063904 | -0.044736 | 0.051771 | -0.008409 | 0.17117 | 0.091937 | 0.40753 | -0.09511 | -0.003531 | 0.046146 | -0.042615 | 0.16234 | 0.34337 | -0.11129 | -0.39309 | 61.3871 | -61.5033 | 61.4375 | 61.4738 | 0.086701 | -61.5826 | -61.267 | 61.0891 | -61.5122 | 61.4787 | 61.4396 | 0.35047 | -61.3311 | -61.7858 | 61.6534 | 61.5742 | 61.8898 | 61.534 | -61.7696 | 61.6446 | 61.8256 | 61.3709 | 61.5284 | -62.0676
3725.7969 | 123.2529 | -61.4456 | 61.6974 | 0.0046549 | -0.073384 | 0.022043 | -0.0054682 | -0.010365 | 0.011651 | 0.0077831 | -0.042576 | 0.020597 | 0.018079 | 0.054446 | 0.006604 | -0.040158 | 0.05635 | -0.008409 | 0.1849 | 0.10567 | 0.40295 | -0.099689 | 0.005626 | 0.041567 | -0.042615 | 0.15318 | 0.34337 | -0.11587 | -0.39767 | 61.3459 | -61.5125 | 61.4055 | 61.4372 | 0.09128 | -61.5917 | -61.2944 | 61.048 | -61.5442 | 61.4512 | 61.403 | 0.35505 | -61.354 | -61.8133 | 61.6305 | 61.5513 | 61.8486 | 61.502 | -61.7971 | 61.5988 | 61.789 | 61.3297 | 61.4872 | -62.0951
3726.7969 | 123.2574 | -61.5005 | 61.6928 | 0.012286 | -0.073384 | 0.021829 | -0.004827 | -0.010578 | 0.011865 | 0.0077831 | -0.042362 | 0.02081 | 0.017438 | 0.054446 | 0.0068176 | -0.044736 | 0.065507 | 0.000747 | 0.15285 | 0.096516 | 0.40295 | -0.090531 | 0.001048 | 0.036989 | -0.047194 | 0.16234 | 0.34337 | -0.10671 | -0.38851 | 61.41 | -61.54 | 61.4558 | 61.5013 | 0.091278 | -61.5963 | -61.2899 | 61.112 | -61.5305 | 61.5016 | 61.4534 | 0.34132 | -61.3494 | -61.7995 | 61.6534 | 61.5971 | 61.9035 | 61.5661 | -61.7833 | 61.6629 | 61.8439 | 61.3938 | 61.5375 | -62.0813
3727.7969 | 123.3444 | -61.4685 | 61.6562 | 0.0046549 | -0.074025 | 0.022257 | -0.004827 | -0.010578 | 0.012078 | 0.0077831 | -0.04279 | 0.02081 | 0.017652 | 0.05466 | 0.0063904 | -0.044736 | 0.051771 | -0.008409 | 0.17117 | 0.1011 | 0.4121 | -0.099689 | -0.00811 | 0.041567 | -0.042615 | 0.15776 | 0.33879 | -0.11587 | -0.39767 | 61.3688 | -61.485 | 61.4238 | 61.4601 | 0.09128 | -61.5551 | -61.2441 | 61.0708 | -61.4984 | 61.4604 | 61.4259 | 0.35505 | -61.3174 | -61.7721 | 61.6397 | 61.5696 | 61.8806 | 61.5203 | -61.7559 | 61.6263 | 61.8073 | 61.3526 | 61.5101 | -62.0539
3728.7969 | 123.1979 | -61.4822 | 61.7157 | -0.010607 | -0.074025 | 0.022257 | -0.004827 | -0.010365 | 0.011651 | 0.00015261 | -0.042362 | 0.020597 | 0.017438 | 0.05466 | 0.0068176 | -0.044736 | 0.05635 | -0.008409 | 0.15743 | 0.091937 | 0.41668 | -0.090531 | 0.001048 | 0.046146 | -0.042615 | 0.15776 | 0.34794 | -0.11587 | -0.38851 | 61.3917 | -61.5583 | 61.4375 | 61.4738 | 0.082122 | -61.6238 | -61.299 | 61.0937 | -61.5579 | 61.4833 | 61.4396 | 0.3459 | -61.3678 | -61.8316 | 61.6397 | 61.5742 | 61.8989 | 61.5386 | -61.8062 | 61.64 | 61.8302 | 61.3664 | 61.5284 | -62.1042
3729.7969 | 123.262 | -61.4914 | 61.6974 | -0.0029761 | -0.074025 | 0.022257 | -0.0052544 | -0.010151 | 0.011651 | 0.015414 | -0.042149 | 0.02081 | 0.017652 | 0.054873 | 0.0061766 | -0.040158 | 0.060928 | -0.008409 | 0.17117 | 0.1011 | 0.40753 | -0.090531 | 0.001048 | 0.036989 | -0.042615 | 0.15776 | 0.33879 | -0.11129 | -0.38851 | 61.4009 | -61.5262 | 61.4512 | 61.483 | 0.082122 | -61.5963 | -61.2899 | 61.1029 | -61.5396 | 61.4924 | 61.4488 | 0.3459 | -61.3586 | -61.8087 | 61.6626 | 61.5925 | 61.8989 | 61.5523 | -61.7879 | 61.6492 | 61.8302 | 61.3801 | 61.5284 | -62.0859
3730.9531 | 123.3994 | -61.4548 | 61.647 | 0.0046549 | -0.073811 | 0.022257 | -0.0052544 | -0.010365 | 0.011651 | 0.00015261 | -0.042362 | 0.020383 | 0.017652 | 0.054446 | 0.0061766 | -0.044736 | 0.060928 | 0.000747 | 0.15743 | 0.1011 | 0.40295 | -0.09511 | 0.005626 | 0.046146 | -0.042615 | 0.16234 | 0.35252 | -0.12045 | -0.38851 | 61.3597 | -61.4896 | 61.41 | 61.4555 | 0.095857 | -61.5459 | -61.2441 | 61.0663 | -61.4847 | 61.4604 | 61.4122 | 0.3459 | -61.2945 | -61.7675 | 61.6122 | 61.5559 | 61.8577 | 61.5157 | -61.7421 | 61.6171 | 61.8073 | 61.3343 | 61.5009 | -62.0355
3731.7969 | 123.3856 | -61.4594 | 61.6608 | 0.0046549 | -0.073811 | 0.021829 | -0.0050408 | -0.010578 | 0.012292 | 0.0077831 | -0.042576 | 0.020383 | 0.017438 | 0.054873 | 0.0068176 | -0.049315 | 0.060928 | -0.003831 | 0.16659 | 0.091937 | 0.39837 | -0.09511 | -0.003531 | 0.041567 | -0.042615 | 0.15776 | 0.34794 | -0.12045 | -0.39309 | 61.3642 | -61.4942 | 61.41 | 61.4555 | 0.091279 | -61.5688 | -61.2624 | 61.0663 | -61.503 | 61.4558 | 61.4167 | 0.35047 | -61.3128 | -61.7812 | 61.6259 | 61.5513 | 61.8577 | 61.5203 | -61.7559 | 61.6171 | 61.8073 | 61.3389 | 61.5009 | -62.0539
3732.7969 | 123.2758 | -61.496 | 61.6974 | -0.0029761 | -0.074025 | 0.022043 | -0.0052544 | -0.010578 | 0.011651 | 0.0077831 | -0.042576 | 0.02081 | 0.017438 | 0.05466 | 0.006604 | -0.03558 | 0.051771 | 0.000747 | 0.15743 | 0.10567 | 0.40295 | -0.085952 | 0.001048 | 0.036989 | -0.042615 | 0.16234 | 0.33879 | -0.10671 | -0.38851 | 61.41 | -61.54 | 61.4604 | 61.4967 | 0.086699 | -61.5917 | -61.2944 | 61.1075 | -61.535 | 61.497 | 61.4534 | 0.3459 | -61.3586 | -61.8041 | 61.6534 | 61.6016 | 61.8989 | 61.5477 | -61.7833 | 61.6583 | 61.8348 | 61.3893 | 61.533 | -62.0859
3733.7969 | 123.3536 | -61.4685 | 61.6791 | -0.0029761 | -0.073598 | 0.022043 | -0.0050408 | -0.010578 | 0.011651 | 0.00015261 | -0.042576 | 0.021024 | 0.017865 | 0.05466 | 0.0063904 | -0.03558 | 0.05635 | -0.008409 | 0.16659 | 0.1011 | 0.40753 | -0.090531 | 0.001048 | 0.041567 | -0.042615 | 0.15776 | 0.34337 | -0.11587 | -0.40225 | 61.378 | -61.5125 | 61.4329 | 61.4601 | 0.082122 | -61.578 | -61.2716 | 61.0663 | -61.5213 | 61.4696 | 61.4259 | 0.35963 | -61.3357 | -61.7949 | 61.6351 | 61.5696 | 61.876 | 61.5249 | -61.7696 | 61.6263 | 61.8119 | 61.3526 | 61.5101 | -62.0813
3734.7969 | 123.2666 | -61.4822 | 61.7065 | -0.0029761 | -0.073811 | 0.022257 | -0.004827 | -0.010578 | 0.011651 | 0.0077831 | -0.042362 | 0.020383 | 0.017652 | 0.054873 | 0.0068176 | -0.044736 | 0.051771 | -0.003831 | 0.16201 | 0.096516 | 0.39379 | -0.090531 | -0.003531 | 0.046146 | -0.047194 | 0.14861 | 0.34337 | -0.11587 | -0.38851 | 61.3917 | -61.5445 | 61.4375 | 61.4784 | 0.0867 | -61.61 | -61.3128 | 61.0937 | -61.5579 | 61.4787 | 61.435 | 0.34132 | -61.3632 | -61.8224 | 61.6442 | 61.5788 | 61.876 | 61.534 | -61.7971 | 61.6308 | 61.8256 | 61.3664 | 61.5284 | -62.0951
3735.7969 | 123.2712 | -61.5005 | 61.6608 | 0.0046549 | -0.074025 | 0.022043 | -0.0052544 | -0.010365 | 0.011437 | 0.00015261 | -0.042362 | 0.020169 | 0.017438 | 0.054873 | 0.0063904 | -0.044736 | 0.051771 | -0.008409 | 0.13912 | 0.096516 | 0.39837 | -0.090531 | 0.001048 | 0.046146 | -0.038036 | 0.15318 | 0.34337 | -0.11587 | -0.38851 | 61.41 | -61.5217 | 61.4558 | 61.4921 | 0.082122 | -61.5643 | -61.2624 | 61.112 | -61.5076 | 61.5016 | 61.4625 | 0.35047 | -61.3174 | -61.7766 | 61.6397 | 61.5971 | 61.8989 | 61.5523 | -61.7513 | 61.6537 | 61.8439 | 61.3847 | 61.5467 | -62.0493
3736.7969 | 123.2941 | -61.496 | 61.6882 | -0.0029761 | -0.073598 | 0.022257 | -0.0054682 | -0.010578 | 0.012078 | 0.0077831 | -0.04279 | 0.020383 | 0.017652 | 0.05466 | 0.0061766 | -0.040158 | 0.060928 | -0.008409 | 0.16659 | 0.10567 | 0.4121 | -0.090531 | 0.001048 | 0.046146 | -0.038036 | 0.14861 | 0.34337 | -0.11587 | -0.38851 | 61.4054 | -61.5216 | 61.4558 | 61.4876 | 0.082122 | -61.5826 | -61.2761 | 61.1075 | -61.5396 | 61.497 | 61.4579 | 0.35047 | -61.3449 | -61.8041 | 61.6626 | 61.6016 | 61.9081 | 61.5569 | -61.7788 | 61.6446 | 61.8393 | 61.3801 | 61.5421 | -62.0767
3737.7969 | 123.2529 | -61.496 | 61.6928 | -0.0029761 | -0.073598 | 0.022043 | -0.0050408 | -0.010365 | 0.012078 | 0.00015261 | -0.042576 | 0.020597 | 0.017865 | 0.054446 | 0.0063904 | -0.044736 | 0.05635 | -0.008409 | 0.17574 | 0.1011 | 0.40753 | -0.099689 | 0.001048 | 0.041567 | -0.033458 | 0.15318 | 0.34794 | -0.11587 | -0.38851 | 61.3963 | -61.5171 | 61.4512 | 61.4876 | 0.09128 | -61.5917 | -61.2853 | 61.1075 | -61.5396 | 61.497 | 61.4625 | 0.35505 | -61.3449 | -61.8087 | 61.6717 | 61.5971 | 61.9035 | 61.5523 | -61.7925 | 61.6492 | 61.8439 | 61.3801 | 61.5375 | -62.0813
3738.7969 | 123.2803 | -61.496 | 61.7111 | -0.010607 | -0.073598 | 0.022684 | -0.004827 | -0.010151 | 0.012292 | -0.0074779 | -0.042149 | 0.020383 | 0.017652 | 0.05466 | 0.0063904 | -0.049315 | 0.051771 | -0.008409 | 0.17574 | 0.10567 | 0.40753 | -0.099689 | 0.001048 | 0.041567 | -0.038036 | 0.14861 | 0.33879 | -0.11129 | -0.38851 | 61.3963 | -61.5354 | 61.4467 | 61.4876 | 0.09128 | -61.6054 | -61.3036 | 61.1075 | -61.5625 | 61.497 | 61.4579 | 0.35047 | -61.3723 | -61.8224 | 61.6717 | 61.6016 | 61.9035 | 61.5477 | -61.8108 | 61.6446 | 61.8348 | 61.3847 | 61.5375 | -62.0996
3739.7969 | 123.2849 | -61.528 | 61.702 | -0.010607 | -0.073598 | 0.022043 | -0.0052544 | -0.010578 | 0.011651 | 0.00015261 | -0.042576 | 0.020597 | 0.017438 | 0.054873 | 0.0063904 | -0.049315 | 0.051771 | -0.003831 | 0.1849 | 0.1011 | 0.39837 | -0.09511 | 0.010205 | 0.046146 | -0.051772 | 0.16234 | 0.34337 | -0.11129 | -0.38851 | 61.4329 | -61.5171 | 61.4787 | 61.5242 | 0.091279 | -61.6009 | -61.3036 | 61.1395 | -61.5396 | 61.5382 | 61.4762 | 0.33674 | -61.3586 | -61.8133 | 61.7129 | 61.6291 | 61.9264 | 61.5798 | -61.7971 | 61.6904 | 61.8714 | 61.4167 | 61.5742 | -62.0905
3740.7969 | 123.3124 | -61.5189 | 61.702 | -0.0029761 | -0.074239 | 0.022043 | -0.0050408 | -0.010578 | 0.012292 | 0.0077831 | -0.042576 | 0.021238 | 0.017652 | 0.05466 | 0.0068176 | -0.040158 | 0.060928 | -0.008409 | 0.1849 | 0.11025 | 0.40295 | -0.099689 | 0.001048 | 0.046146 | -0.042615 | 0.15318 | 0.33879 | -0.11587 | -0.38851 | 61.4192 | -61.5171 | 61.4787 | 61.5105 | 0.09128 | -61.5917 | -61.299 | 61.1303 | -61.5488 | 61.5199 | 61.4762 | 0.3459 | -61.3632 | -61.8178 | 61.7038 | 61.6291 | 61.9218 | 61.5798 | -61.8017 | 61.672 | 61.8576 | 61.403 | 61.565 | -62.0905
3741.7969 | 123.3032 | -61.5189 | 61.6974 | 0.0046549 | -0.073811 | 0.022257 | -0.0050408 | -0.010578 | 0.012078 | 0.0077831 | -0.042576 | 0.020383 | 0.017438 | 0.05466 | 0.006604 | -0.040158 | 0.060928 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.09511 | -0.003531 | 0.041567 | -0.038036 | 0.15318 | 0.34337 | -0.11587 | -0.38393 | 61.4237 | -61.5216 | 61.4787 | 61.515 | 0.091279 | -61.5963 | -61.2899 | 61.1349 | -61.5442 | 61.5153 | 61.4808 | 0.3459 | -61.354 | -61.8133 | 61.6946 | 61.62 | 61.9264 | 61.5798 | -61.7925 | 61.672 | 61.8622 | 61.403 | 61.5604 | -62.0813
3742.7969 | 123.3078 | -61.5097 | 61.6928 | -0.0029761 | -0.074239 | 0.022043 | -0.0050408 | -0.010151 | 0.012078 | -0.0074779 | -0.042362 | 0.020597 | 0.017865 | 0.05466 | 0.006604 | -0.044736 | 0.065507 | 0.000747 | 0.16659 | 0.11025 | 0.41668 | -0.099689 | 0.005626 | 0.041567 | -0.038036 | 0.15776 | 0.34337 | -0.11129 | -0.37935 | 61.41 | -61.5262 | 61.465 | 61.5105 | 0.10044 | -61.5826 | -61.2761 | 61.1304 | -61.535 | 61.5153 | 61.4717 | 0.34132 | -61.3494 | -61.8041 | 61.6763 | 61.62 | 61.9264 | 61.5752 | -61.7925 | 61.6675 | 61.8531 | 61.3984 | 61.5513 | -62.0722
3743.8594 | 123.2574 | -61.5005 | 61.6791 | -0.0029761 | -0.074239 | 0.022257 | -0.0050408 | -0.010365 | 0.011865 | 0.00015261 | -0.043003 | 0.02081 | 0.017652 | 0.05466 | 0.006604 | -0.040158 | 0.05635 | -0.003831 | 0.17117 | 0.096516 | 0.40295 | -0.090531 | 0.001048 | 0.050725 | -0.038036 | 0.14861 | 0.34337 | -0.11587 | -0.39309 | 61.41 | -61.5079 | 61.4604 | 61.4967 | 0.0867 | -61.5826 | -61.2761 | 61.1075 | -61.5305 | 61.5016 | 61.4625 | 0.35505 | -61.3357 | -61.7949 | 61.6717 | 61.5971 | 61.9035 | 61.5569 | -61.7696 | 61.6492 | 61.8439 | 61.3847 | 61.5513 | -62.0722
3744.7969 | 123.3124 | -61.5097 | 61.6653 | -0.0029761 | -0.074025 | 0.02247 | -0.0052544 | -0.010151 | 0.011651 | 0.00015261 | -0.041935 | 0.020383 | 0.017865 | 0.05466 | 0.006604 | -0.049315 | 0.060928 | -0.003831 | 0.17574 | 0.11025 | 0.41668 | -0.09511 | 0.005626 | 0.050725 | -0.038036 | 0.15776 | 0.34337 | -0.12045 | -0.37935 | 61.4146 | -61.4896 | 61.4604 | 61.5059 | 0.091279 | -61.5551 | -61.2487 | 61.1304 | -61.5076 | 61.5153 | 61.4717 | 0.34132 | -61.322 | -61.7858 | 61.6854 | 61.62 | 61.9264 | 61.5706 | -61.7605 | 61.6675 | 61.8531 | 61.3893 | 61.5604 | -62.0447
3745.7969 | 123.3261 | -61.5097 | 61.6837 | -0.0029761 | -0.074025 | 0.02247 | -0.0052544 | -0.010151 | 0.012078 | 0.00015261 | -0.042362 | 0.020597 | 0.017438 | 0.05466 | 0.0063904 | -0.040158 | 0.060928 | -0.012988 | 0.17574 | 0.1011 | 0.41668 | -0.09511 | -0.00811 | 0.041567 | -0.042615 | 0.15776 | 0.32963 | -0.11587 | -0.38393 | 61.4146 | -61.5079 | 61.4695 | 61.4967 | 0.082122 | -61.5826 | -61.267 | 61.1258 | -61.5259 | 61.5016 | 61.4671 | 0.34132 | -61.354 | -61.7995 | 61.6854 | 61.6108 | 61.9264 | 61.5706 | -61.7788 | 61.6675 | 61.8393 | 61.3938 | 61.5513 | -62.0676
3746.7969 | 123.2986 | -61.5326 | 61.6882 | -0.025869 | -0.073811 | 0.022043 | -0.0052544 | -0.010365 | 0.012078 | 0.00015261 | -0.042576 | 0.020383 | 0.017652 | 0.05466 | 0.0063904 | -0.03558 | 0.060928 | -0.008409 | 0.18948 | 0.096516 | 0.41668 | -0.099689 | 0.005626 | 0.046146 | -0.038036 | 0.15318 | 0.34337 | -0.10671 | -0.38851 | 61.4329 | -61.4988 | 61.497 | 61.5242 | 0.09128 | -61.5917 | -61.2715 | 61.1441 | -61.535 | 61.5382 | 61.4946 | 0.35047 | -61.3449 | -61.7949 | 61.7221 | 61.6291 | 61.9493 | 61.5935 | -61.7879 | 61.6858 | 61.876 | 61.4259 | 61.5787 | -62.0767
3747.7969 | 123.2895 | -61.528 | 61.6699 | 0.012286 | -0.074239 | 0.021829 | -0.0052544 | -0.010151 | 0.011865 | 0.0077831 | -0.042362 | 0.020597 | 0.017652 | 0.055087 | 0.0063904 | -0.040158 | 0.05635 | -0.008409 | 0.18032 | 0.096516 | 0.40295 | -0.09511 | 0.001048 | 0.046146 | -0.038036 | 0.15776 | 0.33421 | -0.11129 | -0.38851 | 61.4329 | -61.4896 | 61.4879 | 61.5196 | 0.086701 | -61.5734 | -61.267 | 61.1395 | -61.5122 | 61.5291 | 61.49 | 0.35047 | -61.3357 | -61.7812 | 61.7083 | 61.6245 | 61.931 | 61.5844 | -61.765 | 61.6858 | 61.8622 | 61.4167 | 61.5742 | -62.0584
3748.7969 | 123.2803 | -61.5051 | 61.6837 | 0.0046549 | -0.074025 | 0.022043 | -0.0050408 | -0.010578 | 0.011865 | 0.0077831 | -0.042576 | 0.020597 | 0.017438 | 0.054873 | 0.0063904 | -0.03558 | 0.051771 | -0.003831 | 0.18032 | 0.1011 | 0.4121 | -0.090531 | 0.001048 | 0.03241 | -0.047194 | 0.15318 | 0.34337 | -0.11587 | -0.38851 | 61.4146 | -61.5033 | 61.4695 | 61.5013 | 0.0867 | -61.5826 | -61.2716 | 61.1166 | -61.5305 | 61.5062 | 61.4579 | 0.34132 | -61.3403 | -61.7995 | 61.6855 | 61.6062 | 61.9172 | 61.5569 | -61.7742 | 61.6583 | 61.8485 | 61.3893 | 61.5375 | -62.0722
3749.7969 | 123.3124 | -61.4868 | 61.6837 | -0.010607 | -0.074239 | 0.022257 | -0.0046134 | -0.010578 | 0.012078 | 0.015414 | -0.043003 | 0.020383 | 0.017438 | 0.05466 | 0.006604 | -0.040158 | 0.060928 | -0.003831 | 0.17117 | 0.10567 | 0.40295 | -0.090531 | 0.001048 | 0.041567 | -0.042615 | 0.15318 | 0.33421 | -0.11587 | -0.38851 | 61.3963 | -61.5125 | 61.4467 | 61.483 | 0.0867 | -61.578 | -61.2807 | 61.0983 | -61.5305 | 61.4879 | 61.4442 | 0.3459 | -61.3494 | -61.7995 | 61.658 | 61.5925 | 61.8898 | 61.5477 | -61.7742 | 61.64 | 61.821 | 61.3709 | 61.5284 | -62.0722
3750.7969 | 123.2803 | -61.5097 | 61.6791 | -0.0029761 | -0.074025 | 0.021829 | -0.004827 | -0.010792 | 0.012078 | 0.00015261 | -0.042576 | 0.020597 | 0.017438 | 0.054446 | 0.0061766 | -0.040158 | 0.065507 | -0.008409 | 0.16659 | 0.096516 | 0.40295 | -0.090531 | 0.001048 | 0.036989 | -0.047194 | 0.15776 | 0.34337 | -0.12045 | -0.37935 | 61.4192 | -61.5125 | 61.4695 | 61.5013 | 0.082122 | -61.5826 | -61.2761 | 61.1304 | -61.5213 | 61.5108 | 61.4625 | 0.33216 | -61.3357 | -61.7995 | 61.6763 | 61.6062 | 61.9127 | 61.5752 | -61.7696 | 61.6675 | 61.8531 | 61.3893 | 61.5467 | -62.0584
3751.7969 | 123.3353 | -61.5143 | 61.6928 | -0.010607 | -0.074025 | 0.022257 | -0.004827 | -0.010365 | 0.011437 | 0.0077831 | -0.042362 | 0.020597 | 0.017652 | 0.054873 | 0.0061766 | -0.03558 | 0.05635 | -0.008409 | 0.16659 | 0.096516 | 0.38921 | -0.090531 | 0.001048 | 0.03241 | -0.047194 | 0.15318 | 0.33879 | -0.0884 | -0.38851 | 61.4238 | -61.5262 | 61.4787 | 61.5059 | 0.082122 | -61.5963 | -61.3036 | 61.1258 | -61.5396 | 61.5153 | 61.4671 | 0.34132 | -61.354 | -61.7812 | 61.6809 | 61.6108 | 61.9035 | 61.5706 | -61.7833 | 61.6675 | 61.8531 | 61.4259 | 61.5467 | -62.0813
3752.7969 | 123.262 | -61.5234 | 61.6791 | -0.0029761 | -0.073811 | 0.022257 | -0.0050408 | -0.010365 | 0.011865 | -0.0074779 | -0.042362 | 0.020383 | 0.017652 | 0.05466 | 0.006604 | -0.040158 | 0.060928 | -0.003831 | 0.17117 | 0.096516 | 0.40753 | -0.090531 | 0.005626 | 0.041567 | -0.042615 | 0.15318 | 0.33879 | -0.097557 | -0.38393 | 61.4329 | -61.5079 | 61.4833 | 61.5196 | 0.0867 | -61.5826 | -61.2716 | 61.1395 | -61.5259 | 61.5291 | 61.4808 | 0.34132 | -61.3403 | -61.7766 | 61.6946 | 61.62 | 61.931 | 61.5844 | -61.7696 | 61.6766 | 61.8622 | 61.4259 | 61.565 | -62.063
3753.7969 | 123.2849 | -61.5143 | 61.6791 | -0.010607 | -0.074239 | 0.021829 | -0.0052544 | -0.010365 | 0.011865 | 0.00015261 | -0.04279 | 0.020597 | 0.017652 | 0.05466 | 0.0063904 | -0.03558 | 0.05635 | -0.008409 | 0.17117 | 0.096516 | 0.39837 | -0.09511 | 0.010205 | 0.046146 | -0.042615 | 0.14861 | 0.34337 | -0.11587 | -0.38393 | 61.4192 | -61.5079 | 61.4787 | 61.5059 | 0.086701 | -61.5826 | -61.2807 | 61.1303 | -61.5305 | 61.5245 | 61.4717 | 0.34132 | -61.3357 | -61.7949 | 61.6854 | 61.6108 | 61.9126 | 61.5706 | -61.7742 | 61.6629 | 61.8576 | 61.3984 | 61.5604 | -62.063
3754.7969 | 123.262 | -61.5143 | 61.6837 | -0.0029761 | -0.074239 | 0.021616 | -0.0050408 | -0.010151 | 0.012292 | 0.0077831 | -0.042362 | 0.021024 | 0.017224 | 0.054873 | 0.0061766 | -0.049315 | 0.05635 | -0.008409 | 0.17117 | 0.1011 | 0.39837 | -0.09511 | -0.017267 | 0.046146 | -0.038036 | 0.15776 | 0.34794 | -0.11587 | -0.38393 | 61.4192 | -61.5125 | 61.465 | 61.5059 | 0.086701 | -61.5826 | -61.2853 | 61.1303 | -61.5259 | 61.497 | 61.4762 | 0.3459 | -61.3357 | -61.7995 | 61.6854 | 61.6154 | 61.9126 | 61.5706 | -61.7788 | 61.672 | 61.8622 | 61.3984 | 61.5604 | -62.0676
3755.7969 | 123.262 | -61.5326 | 61.6837 | -0.010607 | -0.073811 | 0.021829 | -0.004827 | -0.010578 | 0.012078 | 0.00015261 | -0.042362 | 0.02081 | 0.017438 | 0.054873 | 0.0061766 | -0.031001 | 0.051771 | 0.000747 | 0.17574 | 0.10567 | 0.40753 | -0.10427 | -0.017267 | 0.036989 | -0.038036 | 0.15776 | 0.33421 | -0.11587 | -0.37935 | 61.4283 | -61.5079 | 61.5016 | 61.5333 | 0.10501 | -61.578 | -61.2761 | 61.1532 | -61.5259 | 61.5153 | 61.4946 | 0.34132 | -61.3494 | -61.7995 | 61.7083 | 61.6383 | 61.9401 | 61.5844 | -61.7879 | 61.6904 | 61.8668 | 61.4167 | 61.5696 | -62.063
3756.7969 | 123.317 | -61.5143 | 61.6745 | -0.025869 | -0.074239 | 0.021829 | -0.0050408 | -0.010578 | 0.012292 | 0.00015261 | -0.042576 | 0.020383 | 0.017438 | 0.054873 | 0.0063904 | -0.044736 | 0.05635 | -0.012988 | 0.17117 | 0.1011 | 0.40295 | -0.081373 | -0.012689 | 0.041567 | -0.038036 | 0.15318 | 0.33879 | -0.11587 | -0.37935 | 61.4329 | -61.5033 | 61.4695 | 61.5013 | 0.068385 | -61.5734 | -61.2716 | 61.1349 | -61.5213 | 61.5016 | 61.4762 | 0.34132 | -61.3357 | -61.7904 | 61.6854 | 61.6154 | 61.9172 | 61.5706 | -61.7559 | 61.6675 | 61.8531 | 61.3984 | 61.5558 | -62.0539
3757.7969 | 123.3032 | -61.5372 | 61.702 | -0.0029761 | -0.074025 | 0.02247 | -0.0050408 | -0.010151 | 0.011865 | 0.00015261 | -0.041935 | 0.020383 | 0.017438 | 0.054873 | 0.0061766 | -0.044736 | 0.05635 | -0.008409 | 0.17117 | 0.10567 | 0.41668 | -0.099689 | -0.012689 | 0.046146 | -0.033458 | 0.15776 | 0.33879 | -0.11587 | -0.38393 | 61.4375 | -61.5308 | 61.4924 | 61.5288 | 0.09128 | -61.5963 | -61.2853 | 61.1532 | -61.5442 | 61.5245 | 61.5037 | 0.35047 | -61.3632 | -61.8178 | 61.7083 | 61.6428 | 61.9539 | 61.5935 | -61.8017 | 61.6949 | 61.876 | 61.4213 | 61.5833 | -62.0859
3758.7969 | 123.3032 | -61.5372 | 61.6882 | -0.025869 | -0.074239 | 0.022684 | -0.0050408 | -0.010578 | 0.011651 | -0.0074779 | -0.042362 | 0.02081 | 0.017652 | 0.055087 | 0.006604 | -0.03558 | 0.060928 | 0.000747 | 0.1849 | 0.1011 | 0.39379 | -0.090531 | -0.026425 | 0.036989 | -0.038036 | 0.15318 | 0.33421 | -0.11129 | -0.37935 | 61.4466 | -61.5033 | 61.5016 | 61.5379 | 0.091278 | -61.5871 | -61.2944 | 61.1578 | -61.535 | 61.5107 | 61.4991 | 0.34132 | -61.354 | -61.7995 | 61.7221 | 61.6383 | 61.931 | 61.5981 | -61.7788 | 61.6904 | 61.8714 | 61.4259 | 61.5742 | -62.0676
3759.7969 | 123.2941 | -61.5189 | 61.6837 | -0.0029761 | -0.074239 | 0.02247 | -0.004827 | -0.010151 | 0.011437 | 0.00015261 | -0.042362 | 0.020383 | 0.017652 | 0.055087 | 0.006604 | -0.049315 | 0.060928 | -0.008409 | 0.16659 | 0.096516 | 0.40295 | -0.090531 | -0.012689 | 0.041567 | -0.042615 | 0.16234 | 0.33879 | -0.11129 | -0.37477 | 61.4283 | -61.5171 | 61.4695 | 61.5105 | 0.082122 | -61.5871 | -61.2807 | 61.1441 | -61.5213 | 61.5062 | 61.4762 | 0.33216 | -61.3449 | -61.7949 | 61.6854 | 61.6154 | 61.9218 | 61.5798 | -61.7742 | 61.6812 | 61.8576 | 61.4076 | 61.5604 | -62.0584
3760.7969 | 123.4085 | -61.4868 | 61.6699 | -0.018238 | -0.074239 | 0.022257 | -0.0050408 | -0.010365 | 0.011651 | 0.00015261 | -0.042576 | 0.020597 | 0.017438 | 0.055087 | 0.006604 | -0.049315 | 0.047193 | -0.008409 | 0.16659 | 0.091937 | 0.39837 | -0.085952 | -0.017267 | 0.046146 | -0.047194 | 0.14861 | 0.34337 | -0.11587 | -0.38393 | 61.4009 | -61.5033 | 61.4375 | 61.4784 | 0.077543 | -61.578 | -61.2716 | 61.1029 | -61.5213 | 61.4695 | 61.4396 | 0.33674 | -61.3266 | -61.7858 | 61.6534 | 61.5788 | 61.8852 | 61.534 | -61.7559 | 61.6354 | 61.8302 | 61.3709 | 61.533 | -62.0539
3761.7969 | 123.3444 | -61.5189 | 61.6928 | -0.010607 | -0.074239 | 0.022043 | -0.0052544 | -0.010365 | 0.011865 | 0.00015261 | -0.042362 | 0.020597 | 0.017652 | 0.054873 | 0.0068176 | -0.040158 | 0.051771 | -0.008409 | 0.18032 | 0.1011 | 0.39837 | -0.090531 | -0.021846 | 0.046146 | -0.038036 | 0.15318 | 0.32963 | -0.11587 | -0.38393 | 61.4283 | -61.5125 | 61.4787 | 61.5105 | 0.082122 | -61.5917 | -61.2944 | 61.1349 | -61.5396 | 61.497 | 61.4808 | 0.3459 | -61.3632 | -61.8087 | 61.6992 | 61.62 | 61.9172 | 61.5706 | -61.7833 | 61.672 | 61.8485 | 61.403 | 61.565 | -62.0767
3762.7969 | 123.4085 | -61.4777 | 61.6653 | -0.0029761 | -0.074025 | 0.022043 | -0.0052544 | -0.010578 | 0.011865 | 0.00015261 | -0.042149 | 0.020383 | 0.017438 | 0.05466 | 0.0061766 | -0.044736 | 0.051771 | -0.003831 | 0.14369 | 0.096516 | 0.40753 | -0.085952 | -0.017267 | 0.046146 | -0.042615 | 0.14861 | 0.33879 | -0.11587 | -0.38851 | 61.3917 | -61.5216 | 61.4329 | 61.4738 | 0.082121 | -61.5688 | -61.2578 | 61.0891 | -61.5167 | 61.4604 | 61.435 | 0.3459 | -61.3266 | -61.7812 | 61.6214 | 61.5742 | 61.8852 | 61.5294 | -61.7513 | 61.6263 | 61.8164 | 61.3618 | 61.5238 | -62.0539
3763.7969 | 123.436 | -61.4822 | 61.6882 | -0.0029761 | -0.074025 | 0.022257 | -0.004827 | -0.010578 | 0.011865 | 0.00015261 | -0.04279 | 0.02081 | 0.017438 | 0.054873 | 0.0063904 | -0.040158 | 0.05635 | 0.000747 | 0.13912 | 0.10567 | 0.4121 | -0.09511 | -0.012689 | 0.041567 | -0.042615 | 0.14861 | 0.33879 | -0.11129 | -0.38393 | 61.3871 | -61.5491 | 61.4421 | 61.483 | 0.095857 | -61.5826 | -61.2761 | 61.0983 | -61.5396 | 61.4695 | 61.4396 | 0.34132 | -61.3494 | -61.7995 | 61.6214 | 61.5879 | 61.8943 | 61.5386 | -61.7833 | 61.6308 | 61.821 | 61.3709 | 61.5238 | -62.0722
3764.7969 | 123.3902 | -61.4731 | 61.6562 | 0.0046549 | -0.074025 | 0.022043 | -0.0052544 | -0.010151 | 0.011865 | -0.0074779 | -0.042149 | 0.02081 | 0.017652 | 0.054873 | 0.006604 | -0.044736 | 0.05635 | -0.008409 | 0.18032 | 0.10567 | 0.39379 | -0.09511 | -0.017267 | 0.041567 | -0.042615 | 0.15318 | 0.33879 | -0.11587 | -0.37935 | 61.378 | -61.4759 | 61.4283 | 61.4647 | 0.086701 | -61.5505 | -61.2624 | 61.0937 | -61.503 | 61.4558 | 61.4305 | 0.33674 | -61.3174 | -61.7721 | 61.6534 | 61.5788 | 61.8669 | 61.5294 | -61.7513 | 61.6263 | 61.8119 | 61.3572 | 61.5147 | -62.0355
3765.7969 | 123.3353 | -61.4914 | 61.6653 | -0.0029761 | -0.073811 | 0.02247 | -0.0052544 | -0.010578 | 0.011865 | 0.00015261 | -0.042576 | 0.020597 | 0.017652 | 0.05466 | 0.0063904 | -0.040158 | 0.05635 | 0.000747 | 0.16659 | 0.1011 | 0.4121 | -0.085952 | -0.012689 | 0.041567 | -0.038036 | 0.15318 | 0.34337 | -0.11587 | -0.37935 | 61.4054 | -61.4988 | 61.4512 | 61.4921 | 0.086699 | -61.5642 | -61.2532 | 61.112 | -61.5122 | 61.4787 | 61.4534 | 0.34132 | -61.322 | -61.7812 | 61.658 | 61.5925 | 61.9035 | 61.5477 | -61.7513 | 61.6446 | 61.8348 | 61.3755 | 61.533 | -62.0447
3766.7969 | 123.3627 | -61.496 | 61.7065 | -0.0029761 | -0.073598 | 0.022043 | -0.0052544 | -0.010578 | 0.011865 | 0.00015261 | -0.042362 | 0.021024 | 0.017438 | 0.054873 | 0.006604 | -0.044736 | 0.05635 | -0.003831 | 0.16659 | 0.087359 | 0.40753 | -0.085952 | -0.021846 | 0.036989 | -0.042615 | 0.14861 | 0.32963 | -0.10671 | -0.37477 | 61.41 | -61.54 | 61.4512 | 61.4921 | 0.082121 | -61.6192 | -61.299 | 61.1212 | -61.5579 | 61.4741 | 61.4534 | 0.33216 | -61.3769 | -61.8133 | 61.6626 | 61.5833 | 61.9035 | 61.5523 | -61.7925 | 61.6446 | 61.8256 | 61.3893 | 61.533 | -62.0813
3767.7969 | 123.3994 | -61.5051 | 61.6562 | -0.018238 | -0.074025 | 0.022257 | -0.0050408 | -0.010365 | 0.011865 | 0.00015261 | -0.042576 | 0.02081 | 0.017652 | 0.055087 | 0.0063904 | -0.044736 | 0.047193 | -0.003831 | 0.13912 | 0.11025 | 0.40753 | -0.085952 | -0.021846 | 0.036989 | -0.038036 | 0.15318 | 0.34337 | -0.10671 | -0.38393 | 61.4192 | -61.5171 | 61.4604 | 61.5013 | 0.082121 | -61.5459 | -61.2487 | 61.1212 | -61.503 | 61.4833 | 61.4671 | 0.3459 | -61.3128 | -61.7629 | 61.6442 | 61.6154 | 61.9127 | 61.5523 | -61.7421 | 61.6583 | 61.8485 | 61.3984 | 61.5421 | -62.0401
3768.7969 | 123.3856 | -61.4822 | 61.6562 | -0.0029761 | -0.074025 | 0.022043 | -0.0050408 | -0.010365 | 0.012078 | 0.0077831 | -0.04279 | 0.021024 | 0.017438 | 0.054873 | 0.0061766 | -0.044736 | 0.05635 | 0.000747 | 0.16201 | 0.1011 | 0.4121 | -0.090531 | -0.021846 | 0.036989 | -0.038036 | 0.15318 | 0.33879 | -0.12045 | -0.38393 | 61.3917 | -61.4942 | 61.4375 | 61.483 | 0.091278 | -61.5551 | -61.2441 | 61.0983 | -61.503 | 61.4604 | 61.4442 | 0.3459 | -61.3174 | -61.7766 | 61.6442 | 61.5833 | 61.8943 | 61.5386 | -61.7467 | 61.6354 | 61.821 | 61.3618 | 61.5192 | -62.0401
3769.7969 | 123.3673 | -61.4868 | 61.6699 | 0.0046549 | -0.074025 | 0.021829 | -0.0054682 | -0.010365 | 0.012292 | 0.0077831 | -0.042362 | 0.020597 | 0.017224 | 0.055087 | 0.006604 | -0.044736 | 0.051771 | -0.008409 | 0.17574 | 0.096516 | 0.39837 | -0.090531 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.33879 | -0.11587 | -0.37477 | 61.3963 | -61.4942 | 61.4421 | 61.4784 | 0.082122 | -61.5734 | -61.2716 | 61.112 | -61.5213 | 61.4695 | 61.4442 | 0.33216 | -61.3311 | -61.7858 | 61.6626 | 61.5833 | 61.8852 | 61.5386 | -61.7605 | 61.6354 | 61.8256 | 61.3709 | 61.5284 | -62.0447
3770.7969 | 123.4131 | -61.4822 | 61.6928 | -0.0029761 | -0.074025 | 0.022257 | -0.004827 | -0.010365 | 0.011865 | 0.00015261 | -0.042576 | 0.02081 | 0.017438 | 0.055301 | 0.006604 | -0.044736 | 0.060928 | -0.008409 | 0.17574 | 0.10567 | 0.40753 | -0.081373 | -0.012689 | 0.041567 | -0.047194 | 0.15318 | 0.34794 | -0.11129 | -0.37935 | 61.4009 | -61.5171 | 61.4375 | 61.4738 | 0.072964 | -61.5871 | -61.2853 | 61.1029 | -61.5396 | 61.4695 | 61.435 | 0.33216 | -61.3449 | -61.8041 | 61.658 | 61.5879 | 61.8898 | 61.5432 | -61.7742 | 61.6354 | 61.8302 | 61.3709 | 61.5238 | -62.0722
3771.7969 | 123.3719 | -61.4777 | 61.6745 | 0.012286 | -0.074025 | 0.022043 | -0.0052544 | -0.010151 | 0.011651 | 0.0077831 | -0.042149 | 0.020383 | 0.017438 | 0.054873 | 0.006604 | -0.044736 | 0.051771 | 0.000747 | 0.18032 | 0.096516 | 0.39837 | -0.090531 | -0.012689 | 0.041567 | -0.038036 | 0.14861 | 0.34337 | -0.12045 | -0.38393 | 61.3871 | -61.4942 | 61.4329 | 61.4784 | 0.091278 | -61.578 | -61.2761 | 61.0937 | -61.5259 | 61.465 | 61.4396 | 0.3459 | -61.3311 | -61.795 | 61.658 | 61.5742 | 61.876 | 61.5294 | -61.765 | 61.6263 | 61.821 | 61.3572 | 61.5192 | -62.0584
3772.7969 | 123.4039 | -61.4822 | 61.702 | -0.0029761 | -0.074452 | 0.022257 | -0.0054682 | -0.010365 | 0.011865 | 0.0077831 | -0.042576 | 0.020597 | 0.017652 | 0.055087 | 0.0061766 | -0.053893 | 0.051771 | -0.003831 | 0.17117 | 0.087359 | 0.39837 | -0.090531 | -0.026425 | 0.041567 | -0.033458 | 0.14861 | 0.34794 | -0.11129 | -0.38851 | 61.3917 | -61.5308 | 61.4283 | 61.4784 | 0.0867 | -61.6146 | -61.3036 | 61.0937 | -61.5534 | 61.4558 | 61.4488 | 0.35505 | -61.354 | -61.8133 | 61.6534 | 61.5696 | 61.8806 | 61.534 | -61.7925 | 61.6308 | 61.8302 | 61.3709 | 61.5238 | -62.0905
3773.7969 | 123.3902 | -61.496 | 61.7065 | 0.0046549 | -0.074025 | 0.022257 | -0.0054682 | -0.010151 | 0.011865 | -0.0074779 | -0.042576 | 0.02081 | 0.017224 | 0.055087 | 0.0061766 | -0.044736 | 0.05635 | 0.000747 | 0.18032 | 0.096516 | 0.40295 | -0.090531 | -0.021846 | 0.036989 | -0.042615 | 0.15776 | 0.34794 | -0.11587 | -0.38851 | 61.4054 | -61.5262 | 61.4512 | 61.4967 | 0.091278 | -61.61 | -61.3036 | 61.1075 | -61.5488 | 61.4741 | 61.4534 | 0.3459 | -61.3586 | -61.8224 | 61.6763 | 61.5925 | 61.8989 | 61.5523 | -61.7971 | 61.6537 | 61.8439 | 61.3801 | 61.533 | -62.0951
3774.7969 | 123.4406 | -61.4639 | 61.6974 | -0.010607 | -0.074452 | 0.022257 | -0.0050408 | -0.010365 | 0.012078 | 0.0077831 | -0.042576 | 0.02081 | 0.017652 | 0.055087 | 0.006604 | -0.053893 | 0.05635 | -0.003831 | 0.18032 | 0.096516 | 0.39837 | -0.09511 | -0.017267 | 0.046146 | -0.033458 | 0.15318 | 0.34337 | -0.11129 | -0.37935 | 61.3688 | -61.5171 | 61.41 | 61.4601 | 0.091279 | -61.6009 | -61.299 | 61.0846 | -61.5442 | 61.4467 | 61.4305 | 0.3459 | -61.354 | -61.8087 | 61.6443 | 61.5604 | 61.8623 | 61.5203 | -61.7925 | 61.6171 | 61.8073 | 61.3526 | 61.5101 | -62.0767
3775.7969 | 123.3627 | -61.5143 | 61.6974 | -0.0029761 | -0.074239 | 0.022043 | -0.0052544 | -0.010578 | 0.011651 | -0.015108 | -0.042362 | 0.020597 | 0.017652 | 0.054873 | 0.0063904 | -0.049315 | 0.070086 | -0.008409 | 0.1849 | 0.1011 | 0.39379 | -0.085952 | -0.021846 | 0.041567 | -0.038036 | 0.14861 | 0.33879 | -0.11587 | -0.37935 | 61.4283 | -61.5125 | 61.465 | 61.5059 | 0.077543 | -61.5963 | -61.3036 | 61.1349 | -61.5488 | 61.4924 | 61.4762 | 0.34132 | -61.3586 | -61.8133 | 61.6992 | 61.6154 | 61.9081 | 61.5844 | -61.7833 | 61.6629 | 61.8531 | 61.3984 | 61.5558 | -62.0767
3776.7969 | 123.3994 | -61.5097 | 61.6974 | 0.0046549 | -0.074239 | 0.022257 | -0.0050408 | -0.010365 | 0.012078 | 0.0077831 | -0.042362 | 0.020383 | 0.017652 | 0.054873 | 0.0061766 | -0.049315 | 0.05635 | -0.003831 | 0.17117 | 0.10567 | 0.40753 | -0.09511 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.35252 | -0.11587 | -0.38393 | 61.4146 | -61.5262 | 61.4604 | 61.5059 | 0.091279 | -61.5917 | -61.2899 | 61.1258 | -61.5488 | 61.4924 | 61.4671 | 0.34132 | -61.3449 | -61.8133 | 61.6809 | 61.6154 | 61.9172 | 61.5661 | -61.7925 | 61.6583 | 61.8622 | 61.3938 | 61.5513 | -62.0813
3777.7969 | 123.4268 | -61.4685 | 61.6653 | 0.0046549 | -0.074025 | 0.022043 | -0.0052544 | -0.010578 | 0.012506 | -0.0074779 | -0.042362 | 0.020597 | 0.017652 | 0.054873 | 0.0063904 | -0.053893 | 0.060928 | -0.008409 | 0.16201 | 0.096516 | 0.40295 | -0.090531 | -0.021846 | 0.046146 | -0.047194 | 0.14861 | 0.33879 | -0.11587 | -0.37935 | 61.378 | -61.5033 | 61.4146 | 61.4601 | 0.082122 | -61.5688 | -61.2624 | 61.0892 | -61.5167 | 61.4467 | 61.4213 | 0.33216 | -61.3266 | -61.7812 | 61.6305 | 61.565 | 61.8715 | 61.5294 | -61.7559 | 61.6171 | 61.8073 | 61.3526 | 61.5147 | -62.0447
3778.7969 | 123.3994 | -61.5005 | 61.6837 | 0.0046549 | -0.073811 | 0.022043 | -0.0052544 | -0.010365 | 0.012078 | 0.0077831 | -0.042576 | 0.020383 | 0.017224 | 0.055087 | 0.0063904 | -0.040158 | 0.05635 | 0.000747 | 0.17574 | 0.096516 | 0.40295 | -0.099689 | -0.017267 | 0.036989 | -0.042615 | 0.14861 | 0.34337 | -0.11587 | -0.37477 | 61.4009 | -61.5079 | 61.4604 | 61.5013 | 0.10044 | -61.5871 | -61.2807 | 61.1258 | -61.535 | 61.4833 | 61.4579 | 0.33216 | -61.3403 | -61.7995 | 61.6763 | 61.5971 | 61.9035 | 61.5569 | -61.7833 | 61.6492 | 61.8439 | 61.3847 | 61.5375 | -62.0584
3779.7969 | 123.4222 | -61.4777 | 61.702 | -0.0029761 | -0.074025 | 0.022043 | -0.0050408 | -0.010151 | 0.012292 | 0.00015261 | -0.042149 | 0.020383 | 0.017438 | 0.05466 | 0.006604 | -0.040158 | 0.05635 | -0.003831 | 0.18032 | 0.11025 | 0.41668 | -0.085952 | -0.017267 | 0.036989 | -0.047194 | 0.14861 | 0.34337 | -0.10671 | -0.37477 | 61.3917 | -61.5216 | 61.4375 | 61.4738 | 0.082121 | -61.5917 | -61.2853 | 61.1029 | -61.5534 | 61.4604 | 61.4305 | 0.32758 | -61.3586 | -61.8087 | 61.658 | 61.5879 | 61.8943 | 61.534 | -61.7879 | 61.6263 | 61.821 | 61.3709 | 61.5146 | -62.0767
3780.7969 | 123.3398 | -61.5509 | 61.702 | -0.010607 | -0.074239 | 0.022043 | -0.0052544 | -0.010365 | 0.012078 | -0.0074779 | -0.042362 | 0.020597 | 0.017438 | 0.055087 | 0.0063904 | -0.044736 | 0.05635 | -0.008409 | 0.16659 | 0.10567 | 0.4121 | -0.081373 | -0.012689 | 0.041567 | -0.042615 | 0.14403 | 0.34337 | -0.11587 | -0.37935 | 61.4695 | -61.5354 | 61.5062 | 61.5425 | 0.072964 | -61.5963 | -61.2899 | 61.1715 | -61.5579 | 61.5382 | 61.5083 | 0.33674 | -61.3586 | -61.8178 | 61.7175 | 61.6566 | 61.963 | 61.6073 | -61.7833 | 61.6949 | 61.8943 | 61.435 | 61.5925 | -62.0813
3781.7969 | 123.4085 | -61.5005 | 61.702 | 0.0046549 | -0.074239 | 0.022043 | -0.0050408 | -0.0099374 | 0.011651 | 0.00015261 | -0.042149 | 0.020597 | 0.017438 | 0.055087 | 0.0061766 | -0.044736 | 0.05635 | 0.005325 | 0.15285 | 0.10567 | 0.39379 | -0.090531 | -0.00811 | 0.041567 | -0.042615 | 0.14861 | 0.33879 | -0.11587 | -0.37935 | 61.41 | -61.5491 | 61.4558 | 61.5059 | 0.095856 | -61.5963 | -61.3082 | 61.1212 | -61.5534 | 61.4924 | 61.4579 | 0.33674 | -61.3632 | -61.8178 | 61.6534 | 61.6062 | 61.8943 | 61.5569 | -61.7925 | 61.6492 | 61.8393 | 61.3847 | 61.5421 | -62.0813
3782.7969 | 123.2162 | -61.5189 | 61.7386 | -0.0029761 | -0.073811 | 0.021829 | -0.0050408 | -0.010578 | 0.011865 | -0.0074779 | -0.042576 | 0.020597 | 0.017652 | 0.055087 | 0.0063904 | -0.044736 | 0.05635 | 0.000747 | 0.18032 | 0.1011 | 0.38463 | -0.099689 | -0.017267 | 0.041567 | -0.042615 | 0.14403 | 0.33879 | -0.11129 | -0.37935 | 61.4192 | -61.5583 | 61.4741 | 61.5196 | 0.10044 | -61.6375 | -61.354 | 61.1395 | -61.5946 | 61.5016 | 61.4762 | 0.33674 | -61.3998 | -61.8499 | 61.6992 | 61.62 | 61.9035 | 61.5752 | -61.8383 | 61.6629 | 61.8576 | 61.4076 | 61.5604 | -62.1179
3783.7969 | 123.4039 | -61.5097 | 61.7111 | -0.0029761 | -0.074239 | 0.022043 | -0.0052544 | -0.010365 | 0.012078 | 0.0077831 | -0.042362 | 0.021024 | 0.017438 | 0.054873 | 0.006604 | -0.049315 | 0.05635 | -0.008409 | 0.17117 | 0.096516 | 0.39837 | -0.090531 | -0.017267 | 0.046146 | -0.042615 | 0.15318 | 0.34337 | -0.11587 | -0.37935 | 61.4192 | -61.54 | 61.4604 | 61.5013 | 0.082122 | -61.6146 | -61.3128 | 61.1304 | -61.5579 | 61.4924 | 61.4671 | 0.33674 | -61.3678 | -61.827 | 61.6809 | 61.6062 | 61.9081 | 61.5661 | -61.8017 | 61.6629 | 61.8531 | 61.3938 | 61.5559 | -62.0905
3784.7969 | 123.317 | -61.5326 | 61.7065 | -0.0029761 | -0.074239 | 0.022043 | -0.0050408 | -0.010365 | 0.011651 | 0.015414 | -0.042149 | 0.02081 | 0.017438 | 0.054873 | 0.0063904 | -0.040158 | 0.05635 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.099689 | -0.017267 | 0.041567 | -0.056351 | 0.15776 | 0.33879 | -0.11129 | -0.37477 | 61.4329 | -61.5308 | 61.4924 | 61.5288 | 0.095858 | -61.6054 | -61.299 | 61.1578 | -61.5488 | 61.5153 | 61.4762 | 0.31842 | -61.3678 | -61.8178 | 61.7083 | 61.6337 | 61.9401 | 61.5889 | -61.8062 | 61.6904 | 61.8714 | 61.4213 | 61.5742 | -62.0813
3785.7969 | 123.2803 | -61.5555 | 61.7203 | -0.010607 | -0.074025 | 0.021829 | -0.0052544 | -0.010578 | 0.012292 | -0.0074779 | -0.042149 | 0.02081 | 0.017438 | 0.055301 | 0.0063904 | -0.040158 | 0.05635 | -0.003831 | 0.1849 | 0.096516 | 0.4121 | -0.09511 | -0.017267 | 0.046146 | -0.038036 | 0.14861 | 0.33879 | -0.11129 | -0.37477 | 61.4604 | -61.5354 | 61.5153 | 61.5517 | 0.091279 | -61.6238 | -61.3082 | 61.1807 | -61.5717 | 61.5382 | 61.5174 | 0.33674 | -61.3815 | -61.8316 | 61.7404 | 61.652 | 61.9676 | 61.6118 | -61.8154 | 61.7041 | 61.8943 | 61.4442 | 61.6016 | -62.0951
3786.7969 | 123.3032 | -61.5189 | 61.7294 | 0.0046549 | -0.074239 | 0.022257 | -0.0052544 | -0.010365 | 0.011865 | 0.00015261 | -0.042362 | 0.020597 | 0.017224 | 0.055087 | 0.0063904 | -0.049315 | 0.060928 | -0.003831 | 0.18032 | 0.096516 | 0.40753 | -0.09511 | -0.012689 | 0.046146 | -0.038036 | 0.15318 | 0.33421 | -0.11129 | -0.37935 | 61.4237 | -61.5491 | 61.4695 | 61.515 | 0.091279 | -61.6329 | -61.3219 | 61.1395 | -61.5762 | 61.5062 | 61.4808 | 0.34132 | -61.3952 | -61.8407 | 61.6992 | 61.6154 | 61.9264 | 61.5798 | -61.8245 | 61.672 | 61.8531 | 61.4076 | 61.565 | -62.1088
3787.7969 | 123.349 | -61.5189 | 61.7065 | 0.012286 | -0.074239 | 0.022043 | -0.0054682 | -0.010365 | 0.011865 | 0.00015261 | -0.042362 | 0.02081 | 0.017438 | 0.055087 | 0.0061766 | -0.040158 | 0.051771 | 0.000747 | 0.18948 | 0.1011 | 0.40295 | -0.090531 | -0.012689 | 0.036989 | -0.033458 | 0.15318 | 0.34337 | -0.11129 | -0.37935 | 61.4283 | -61.5171 | 61.4787 | 61.5196 | 0.091278 | -61.6054 | -61.3036 | 61.1395 | -61.5534 | 61.5062 | 61.4854 | 0.3459 | -61.3632 | -61.8178 | 61.7083 | 61.62 | 61.9218 | 61.5706 | -61.7971 | 61.672 | 61.8622 | 61.4076 | 61.5558 | -62.0859
3788.7969 | 123.3536 | -61.5097 | 61.7294 | 0.0046549 | -0.074025 | 0.022257 | -0.004827 | -0.010365 | 0.012078 | 0.015414 | -0.042149 | 0.020383 | 0.017438 | 0.055087 | 0.0063904 | -0.044736 | 0.051771 | -0.012988 | 0.18032 | 0.091937 | 0.39837 | -0.09511 | -0.017267 | 0.041567 | -0.038036 | 0.14403 | 0.34337 | -0.11129 | -0.37935 | 61.4146 | -61.5491 | 61.465 | 61.4967 | 0.082122 | -61.6375 | -61.3311 | 61.1304 | -61.5854 | 61.4924 | 61.4717 | 0.34132 | -61.3861 | -61.8407 | 61.69 | 61.6016 | 61.9081 | 61.5615 | -61.8245 | 61.6537 | 61.8531 | 61.3984 | 61.5513 | -62.1088
3789.7969 | 123.2986 | -61.5509 | 61.7065 | 0.0046549 | -0.074025 | 0.021829 | -0.0052544 | -0.010578 | 0.012292 | -0.0074779 | -0.042149 | 0.02081 | 0.017438 | 0.055301 | 0.0063904 | -0.03558 | 0.060928 | -0.008409 | 0.18948 | 0.10567 | 0.42126 | -0.099689 | -0.021846 | 0.036989 | -0.042615 | 0.14403 | 0.33421 | -0.11129 | -0.37477 | 61.4512 | -61.5171 | 61.5153 | 61.5425 | 0.09128 | -61.6009 | -61.2853 | 61.1761 | -61.5625 | 61.5291 | 61.5083 | 0.33216 | -61.3723 | -61.8178 | 61.7404 | 61.6566 | 61.9722 | 61.6118 | -61.8062 | 61.6949 | 61.8851 | 61.4396 | 61.5879 | -62.0813
3790.7969 | 123.4222 | -61.5097 | 61.6333 | -0.0029761 | -0.074025 | 0.022257 | -0.004827 | -0.010365 | 0.012506 | 0.00015261 | -0.042149 | 0.020597 | 0.017438 | 0.055087 | 0.0063904 | -0.040158 | 0.051771 | 0.000747 | 0.1849 | 0.096516 | 0.41668 | -0.099689 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.34794 | -0.11129 | -0.37477 | 61.41 | -61.4484 | 61.4695 | 61.5105 | 0.10044 | -61.5368 | -61.2166 | 61.1349 | -61.4847 | 61.4924 | 61.4671 | 0.33216 | -61.2854 | -61.7446 | 61.6946 | 61.6062 | 61.9264 | 61.5615 | -61.733 | 61.6583 | 61.8576 | 61.3984 | 61.5513 | -62.0081
3791.7969 | 123.3307 | -61.5234 | 61.734 | 0.0046549 | -0.074452 | 0.022043 | -0.0052544 | -0.010365 | 0.011865 | -0.0074779 | -0.04279 | 0.020597 | 0.017438 | 0.055087 | 0.0063904 | -0.040158 | 0.051771 | -0.003831 | 0.18032 | 0.096516 | 0.41668 | -0.099689 | -0.021846 | 0.036989 | -0.042615 | 0.15318 | 0.32963 | -0.11587 | -0.37935 | 61.4237 | -61.5537 | 61.4833 | 61.5196 | 0.095858 | -61.6375 | -61.3173 | 61.1441 | -61.5808 | 61.5016 | 61.4808 | 0.33674 | -61.4044 | -61.8499 | 61.7038 | 61.62 | 61.9401 | 61.5752 | -61.8337 | 61.6766 | 61.8531 | 61.4076 | 61.5604 | -62.1134
3792.7969 | 123.3582 | -61.5234 | 61.6974 | 0.012286 | -0.074452 | 0.022043 | -0.0052544 | -0.010365 | 0.012292 | -0.0074779 | -0.042576 | 0.020597 | 0.017652 | 0.055087 | 0.006604 | -0.044736 | 0.05635 | 0.000747 | 0.17574 | 0.1011 | 0.42126 | -0.099689 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.34337 | -0.11587 | -0.37477 | 61.4237 | -61.5216 | 61.4787 | 61.5242 | 0.10044 | -61.5963 | -61.2761 | 61.1487 | -61.5488 | 61.5062 | 61.4808 | 0.33216 | -61.354 | -61.8133 | 61.6992 | 61.6245 | 61.9447 | 61.5798 | -61.7971 | 61.672 | 61.8668 | 61.4076 | 61.565 | -62.0722
3793.7969 | 123.3398 | -61.5463 | 61.7386 | 0.0046549 | -0.073811 | 0.021829 | -0.0052544 | -0.010578 | 0.012078 | 0.023044 | -0.042362 | 0.020597 | 0.017224 | 0.055301 | 0.0061766 | -0.03558 | 0.060928 | -0.003831 | 0.1849 | 0.10567 | 0.4121 | -0.09511 | -0.026425 | 0.041567 | -0.042615 | 0.15318 | 0.33421 | -0.10671 | -0.37935 | 61.4512 | -61.5537 | 61.5107 | 61.5425 | 0.091279 | -61.6329 | -61.3265 | 61.167 | -61.5854 | 61.5199 | 61.5037 | 0.33674 | -61.4044 | -61.8453 | 61.7312 | 61.652 | 61.9584 | 61.6073 | -61.8337 | 61.6995 | 61.8805 | 61.4396 | 61.5879 | -62.1179
3794.7969 | 123.3582 | -61.5463 | 61.6974 | 0.0046549 | -0.074025 | 0.022257 | -0.004827 | -0.010578 | 0.011651 | 0.00015261 | -0.042576 | 0.020597 | 0.017865 | 0.054873 | 0.0063904 | -0.040158 | 0.065507 | -0.003831 | 0.17117 | 0.1011 | 0.42126 | -0.099689 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.33421 | -0.11587 | -0.37935 | 61.4466 | -61.5262 | 61.5062 | 61.5425 | 0.095858 | -61.5963 | -61.2761 | 61.167 | -61.5488 | 61.5291 | 61.5037 | 0.33674 | -61.3632 | -61.8133 | 61.7175 | 61.6474 | 61.9676 | 61.6118 | -61.7971 | 61.6949 | 61.8805 | 61.4305 | 61.5879 | -62.0767
3795.7969 | 123.4085 | -61.5051 | 61.6699 | -0.0029761 | -0.074239 | 0.022257 | -0.0050408 | -0.0099374 | 0.011865 | -0.0074779 | -0.042149 | 0.021024 | 0.017224 | 0.054873 | 0.0068176 | -0.049315 | 0.05635 | -0.008409 | 0.17574 | 0.10567 | 0.40295 | -0.09511 | -0.021846 | 0.046146 | -0.038036 | 0.14861 | 0.33879 | -0.11587 | -0.37935 | 61.41 | -61.4942 | 61.4558 | 61.4967 | 0.086701 | -61.5642 | -61.267 | 61.1258 | -61.5213 | 61.4833 | 61.4671 | 0.34132 | -61.3311 | -61.7858 | 61.6809 | 61.6108 | 61.9081 | 61.5615 | -61.765 | 61.6537 | 61.8439 | 61.3893 | 61.5513 | -62.0493
3796.7969 | 123.3261 | -61.5784 | 61.734 | 0.0046549 | -0.074452 | 0.022257 | -0.004827 | -0.010365 | 0.011651 | 0.00015261 | -0.042362 | 0.02081 | 0.017438 | 0.055087 | 0.0063904 | -0.044736 | 0.05635 | 0.005325 | 0.18032 | 0.1011 | 0.40753 | -0.090531 | -0.012689 | 0.046146 | -0.047194 | 0.14403 | 0.33421 | -0.097557 | -0.37935 | 61.4878 | -61.5537 | 61.5336 | 61.5837 | 0.095856 | -61.6329 | -61.3265 | 61.199 | -61.59 | 61.5657 | 61.5312 | 0.33216 | -61.3998 | -61.8316 | 61.7587 | 61.6795 | 61.9859 | 61.6347 | -61.8245 | 61.7224 | 61.9126 | 61.4808 | 61.6245 | -62.1134
3797.7969 | 123.3536 | -61.5143 | 61.7065 | -0.0029761 | -0.074452 | 0.021829 | -0.0050408 | -0.010792 | 0.012078 | -0.0074779 | -0.042362 | 0.02081 | 0.017652 | 0.055301 | 0.0061766 | -0.03558 | 0.060928 | -0.008409 | 0.17574 | 0.1011 | 0.41668 | -0.09511 | -0.012689 | 0.036989 | -0.042615 | 0.15318 | 0.34794 | -0.11129 | -0.37477 | 61.4192 | -61.5308 | 61.4787 | 61.5059 | 0.086701 | -61.6054 | -61.2899 | 61.1395 | -61.5534 | 61.5016 | 61.4717 | 0.33216 | -61.3586 | -61.8178 | 61.69 | 61.6154 | 61.931 | 61.5752 | -61.8017 | 61.6675 | 61.8622 | 61.403 | 61.5513 | -62.0813
3798.7969 | 123.2941 | -61.5555 | 61.7065 | -0.010607 | -0.074239 | 0.022257 | -0.0050408 | -0.010578 | 0.012078 | -0.0074779 | -0.042362 | 0.02081 | 0.017652 | 0.054873 | 0.0063904 | -0.049315 | 0.05635 | -0.003831 | 0.18948 | 0.1011 | 0.4121 | -0.09511 | -0.017267 | 0.041567 | -0.051772 | 0.15776 | 0.33421 | -0.11129 | -0.37477 | 61.4604 | -61.5171 | 61.5062 | 61.5517 | 0.091279 | -61.6054 | -61.2944 | 61.1807 | -61.5488 | 61.5382 | 61.5037 | 0.323 | -61.3723 | -61.8178 | 61.745 | 61.6566 | 61.9676 | 61.6118 | -61.8017 | 61.7132 | 61.8897 | 61.4442 | 61.597 | -62.0813
3799.7969 | 123.3627 | -61.528 | 61.7294 | -0.0029761 | -0.074239 | 0.022257 | -0.0052544 | -0.010365 | 0.011865 | 0.0077831 | -0.042362 | 0.020597 | 0.017011 | 0.055514 | 0.0061766 | -0.03558 | 0.05635 | -0.003831 | 0.17574 | 0.096516 | 0.38921 | -0.09511 | -0.017267 | 0.036989 | -0.038036 | 0.15318 | 0.33421 | -0.10671 | -0.37935 | 61.4329 | -61.5537 | 61.4924 | 61.5242 | 0.091279 | -61.6329 | -61.3402 | 61.1487 | -61.5762 | 61.5107 | 61.49 | 0.34132 | -61.3952 | -61.8361 | 61.7038 | 61.6245 | 61.9172 | 61.5844 | -61.8245 | 61.6812 | 61.8622 | 61.4213 | 61.565 | -62.1088
3800.7969 | 123.4085 | -61.4777 | 61.7203 | 0.0046549 | -0.074452 | 0.022257 | -0.0052544 | -0.010578 | 0.012078 | 0.0077831 | -0.042362 | 0.020383 | 0.017224 | 0.055087 | 0.006604 | -0.044736 | 0.060928 | -0.012988 | 0.17574 | 0.096516 | 0.4121 | -0.090531 | -0.012689 | 0.041567 | -0.051772 | 0.14861 | 0.33879 | -0.12503 | -0.37477 | 61.3871 | -61.5445 | 61.4329 | 61.4647 | 0.077543 | -61.6238 | -61.3082 | 61.1029 | -61.5717 | 61.465 | 61.4259 | 0.323 | -61.3815 | -61.8453 | 61.6534 | 61.5742 | 61.8898 | 61.5386 | -61.8108 | 61.6263 | 61.8164 | 61.3526 | 61.5192 | -62.0951
3801.7969 | 123.3307 | -61.5189 | 61.7065 | -0.0029761 | -0.074239 | 0.022257 | -0.0052544 | -0.010578 | 0.011651 | 0.0077831 | -0.042362 | 0.020383 | 0.017438 | 0.055301 | 0.0063904 | -0.053893 | 0.05635 | -0.008409 | 0.18032 | 0.1011 | 0.40295 | -0.099689 | -0.021846 | 0.041567 | -0.042615 | 0.14861 | 0.33879 | -0.11587 | -0.37935 | 61.4192 | -61.5262 | 61.465 | 61.5105 | 0.09128 | -61.6054 | -61.3036 | 61.1395 | -61.5579 | 61.497 | 61.4762 | 0.33674 | -61.3678 | -61.8224 | 61.6992 | 61.62 | 61.9218 | 61.5752 | -61.8062 | 61.6675 | 61.8576 | 61.403 | 61.5604 | -62.0859
3802.7969 | 123.4177 | -61.4868 | 61.6653 | -0.010607 | -0.074239 | 0.022043 | -0.0050408 | -0.010578 | 0.011865 | 0.0077831 | -0.042576 | 0.020597 | 0.017011 | 0.055301 | 0.0063904 | -0.049315 | 0.047193 | -0.008409 | 0.18948 | 0.096516 | 0.40753 | -0.090531 | -0.012689 | 0.046146 | -0.038036 | 0.14861 | 0.33879 | -0.11129 | -0.37477 | 61.3963 | -61.4759 | 61.4375 | 61.4784 | 0.082122 | -61.5688 | -61.2578 | 61.112 | -61.5167 | 61.4741 | 61.4488 | 0.33674 | -61.3266 | -61.7766 | 61.6763 | 61.5833 | 61.8943 | 61.534 | -61.7559 | 61.6354 | 61.8256 | 61.3755 | 61.533 | -62.0401
3803.7969 | 123.3673 | -61.5463 | 61.6928 | 0.0046549 | -0.074239 | 0.021829 | -0.0050408 | -0.010578 | 0.011651 | -0.015108 | -0.042362 | 0.020597 | 0.017224 | 0.055087 | 0.006604 | -0.044736 | 0.051771 | -0.003831 | 0.17574 | 0.1011 | 0.40753 | -0.085952 | -0.017267 | 0.041567 | -0.042615 | 0.14861 | 0.33421 | -0.11129 | -0.3702 | 61.4604 | -61.5171 | 61.5016 | 61.5425 | 0.082121 | -61.5917 | -61.2853 | 61.1761 | -61.5442 | 61.5291 | 61.5037 | 0.32758 | -61.3586 | -61.8041 | 61.7221 | 61.6474 | 61.9539 | 61.5981 | -61.7788 | 61.6949 | 61.8805 | 61.435 | 61.5879 | -62.063
3804.7969 | 123.436 | -61.5143 | 61.6837 | -0.0029761 | -0.074025 | 0.022257 | -0.0050408 | -0.010578 | 0.011865 | 0.00015261 | -0.041935 | 0.02081 | 0.017652 | 0.055301 | 0.006604 | -0.049315 | 0.05635 | 0.005325 | 0.15743 | 0.10567 | 0.40295 | -0.090531 | -0.021846 | 0.041567 | -0.038036 | 0.15318 | 0.32963 | -0.11129 | -0.38393 | 61.4238 | -61.5262 | 61.465 | 61.5196 | 0.095856 | -61.578 | -61.2807 | 61.1303 | -61.5305 | 61.4924 | 61.4762 | 0.3459 | -61.354 | -61.7949 | 61.6717 | 61.62 | 61.9172 | 61.5706 | -61.7742 | 61.6675 | 61.8439 | 61.403 | 61.5558 | -62.0676
3805.7969 | 123.317 | -61.5326 | 61.7294 | -0.010607 | -0.074025 | 0.022257 | -0.0052544 | -0.010578 | 0.012078 | 0.00015261 | -0.042576 | 0.02081 | 0.017438 | 0.055087 | 0.0063904 | -0.049315 | 0.060928 | -0.003831 | 0.14369 | 0.10567 | 0.39837 | -0.090531 | -0.012689 | 0.046146 | -0.038036 | 0.14861 | 0.33879 | -0.11587 | -0.3702 | 61.4421 | -61.5857 | 61.4833 | 61.5288 | 0.0867 | -61.6238 | -61.3311 | 61.1624 | -61.5808 | 61.5199 | 61.4946 | 0.33216 | -61.3906 | -61.8453 | 61.6763 | 61.6383 | 61.931 | 61.5935 | -61.82 | 61.6812 | 61.8714 | 61.4167 | 61.5787 | -62.0996
3806.7969 | 123.4222 | -61.5097 | 61.6882 | -0.0029761 | -0.074666 | 0.022043 | -0.0054682 | -0.010578 | 0.011651 | 0.00015261 | -0.042149 | 0.02081 | 0.017438 | 0.054873 | 0.0061766 | -0.053893 | 0.051771 | -0.008409 | 0.16201 | 0.087359 | 0.40295 | -0.085952 | -0.017267 | 0.041567 | -0.038036 | 0.15318 | 0.33879 | -0.12503 | -0.37935 | 61.4238 | -61.5262 | 61.4558 | 61.5013 | 0.077543 | -61.6009 | -61.2853 | 61.1304 | -61.535 | 61.4924 | 61.4717 | 0.34132 | -61.3494 | -61.8133 | 61.6717 | 61.5971 | 61.9127 | 61.5615 | -61.7742 | 61.6629 | 61.8485 | 61.3847 | 61.5513 | -62.0676
3807.7969 | 123.4085 | -61.5189 | 61.7203 | -0.010607 | -0.074666 | 0.022257 | -0.0050408 | -0.010365 | 0.011865 | -0.0074779 | -0.042149 | 0.020169 | 0.017011 | 0.055087 | 0.0061766 | -0.040158 | 0.060928 | -0.003831 | 0.18032 | 0.091937 | 0.39379 | -0.081373 | -0.012689 | 0.046146 | -0.038036 | 0.14403 | 0.34337 | -0.12045 | -0.37477 | 61.4375 | -61.54 | 61.4787 | 61.515 | 0.077542 | -61.6283 | -61.3265 | 61.1441 | -61.5762 | 61.5062 | 61.4808 | 0.33674 | -61.3769 | -61.8407 | 61.6992 | 61.6108 | 61.9126 | 61.5798 | -61.8016 | 61.6629 | 61.8622 | 61.3984 | 61.565 | -62.0951
3808.7969 | 123.4177 | -61.5051 | 61.6837 | -0.0029761 | -0.074239 | 0.022257 | -0.0050408 | -0.010578 | 0.011865 | 0.0077831 | -0.042149 | 0.020383 | 0.017865 | 0.055514 | 0.006604 | -0.03558 | 0.060928 | -0.008409 | 0.18032 | 0.096516 | 0.40753 | -0.090531 | -0.017267 | 0.03241 | -0.042615 | 0.14861 | 0.33879 | -0.047193 | -0.37935 | 61.4146 | -61.5033 | 61.4695 | 61.4967 | 0.082122 | -61.5871 | -61.2761 | 61.1258 | -61.535 | 61.4879 | 61.4625 | 0.33674 | -61.3449 | -61.7308 | 61.6855 | 61.6016 | 61.9127 | 61.5661 | -61.7742 | 61.6537 | 61.8439 | 61.4579 | 61.5375 | -62.063
3809.7969 | 123.4451 | -61.4822 | 61.6699 | 0.0046549 | -0.074025 | 0.02247 | -0.0046134 | -0.010365 | 0.011437 | 0.00015261 | -0.042149 | 0.020597 | 0.017224 | 0.054873 | 0.006604 | -0.044736 | 0.051771 | -0.003831 | 0.18032 | 0.091937 | 0.40295 | -0.090531 | -0.021846 | 0.041567 | -0.038036 | 0.15318 | 0.34337 | -0.070086 | -0.38393 | 61.3917 | -61.4896 | 61.4375 | 61.4784 | 0.0867 | -61.578 | -61.267 | 61.0983 | -61.5167 | 61.4604 | 61.4442 | 0.3459 | -61.3266 | -61.74 | 61.6626 | 61.5742 | 61.8852 | 61.534 | -61.7605 | 61.6354 | 61.8256 | 61.4122 | 61.5238 | -62.0539
3810.7969 | 123.4085 | -61.4914 | 61.6882 | -0.010607 | -0.074666 | 0.022043 | -0.004827 | -0.010151 | 0.011651 | 0.00015261 | -0.042576 | 0.02081 | 0.017224 | 0.055514 | 0.006604 | -0.044736 | 0.051771 | -0.003831 | 0.16659 | 0.096516 | 0.39837 | -0.090531 | -0.021846 | 0.046146 | -0.047194 | 0.14403 | 0.33879 | -0.065507 | -0.37935 | 61.4009 | -61.5216 | 61.4467 | 61.4876 | 0.0867 | -61.5917 | -61.2899 | 61.112 | -61.5442 | 61.4695 | 61.4442 | 0.33216 | -61.3494 | -61.7537 | 61.658 | 61.5879 | 61.8898 | 61.5432 | -61.7788 | 61.6354 | 61.8302 | 61.4259 | 61.5375 | -62.0676
3811.8594 | 123.3536 | -61.5189 | 61.7432 | 0.0046549 | -0.07488 | 0.022043 | -0.0052544 | -0.010578 | 0.012078 | -0.0074779 | -0.042576 | 0.020383 | 0.017224 | 0.055301 | 0.0063904 | -0.040158 | 0.060928 | 0.000747 | 0.18032 | 0.091937 | 0.40753 | -0.085952 | -0.012689 | 0.046146 | -0.038036 | 0.14861 | 0.34337 | -0.047193 | -0.37477 | 61.4329 | -61.5628 | 61.4787 | 61.5196 | 0.086699 | -61.6512 | -61.3356 | 61.1441 | -61.5946 | 61.5062 | 61.4808 | 0.33674 | -61.3998 | -61.7904 | 61.6992 | 61.6108 | 61.9264 | 61.5798 | -61.8291 | 61.6675 | 61.8622 | 61.4717 | 61.565 | -62.1179
3812.7969 | 123.4085 | -61.5051 | 61.6791 | 0.0046549 | -0.074452 | 0.022043 | -0.0052544 | -0.010365 | 0.011437 | 0.0077831 | -0.042149 | 0.020597 | 0.017438 | 0.054873 | 0.005963 | -0.044736 | 0.05635 | -0.008409 | 0.15743 | 0.096516 | 0.40295 | -0.081373 | -0.017267 | 0.041567 | -0.042615 | 0.15318 | 0.33421 | -0.12045 | -0.3702 | 61.4238 | -61.5216 | 61.4604 | 61.4967 | 0.072964 | -61.5826 | -61.2761 | 61.1349 | -61.5259 | 61.4879 | 61.4625 | 0.32758 | -61.3449 | -61.7995 | 61.6626 | 61.6016 | 61.9081 | 61.5615 | -61.7604 | 61.6583 | 61.8393 | 61.3847 | 61.5467 | -62.0493
3813.7969 | 123.4543 | -61.5051 | 61.7157 | 0.0046549 | -0.074452 | 0.022043 | -0.0052544 | -0.011006 | 0.011651 | -0.0074779 | -0.041935 | 0.02081 | 0.017652 | 0.054873 | 0.006604 | -0.03558 | 0.051771 | -0.003831 | 0.16659 | 0.091937 | 0.39379 | -0.081373 | -0.012689 | 0.050725 | -0.033458 | 0.14861 | 0.33879 | -0.12045 | -0.37477 | 61.4238 | -61.5491 | 61.4695 | 61.5013 | 0.077542 | -61.6238 | -61.3219 | 61.1304 | -61.5671 | 61.4924 | 61.4717 | 0.34132 | -61.3769 | -61.8361 | 61.6717 | 61.5971 | 61.8989 | 61.5569 | -61.7971 | 61.6537 | 61.8439 | 61.3847 | 61.5559 | -62.0905
3814.7969 | 123.468 | -61.4639 | 61.6928 | 0.012286 | -0.074666 | 0.022043 | -0.0052544 | -0.010578 | 0.011651 | 0.0077831 | -0.042362 | 0.020597 | 0.017438 | 0.055301 | 0.0063904 | -0.044736 | 0.051771 | -0.012988 | 0.16659 | 0.10567 | 0.38921 | -0.085952 | -0.021846 | 0.036989 | -0.042615 | 0.14861 | 0.33421 | -0.12045 | -0.37477 | 61.378 | -61.5262 | 61.4192 | 61.4509 | 0.072964 | -61.5871 | -61.3036 | 61.0892 | -61.5442 | 61.4421 | 61.4213 | 0.33216 | -61.3586 | -61.8133 | 61.6305 | 61.5696 | 61.8531 | 61.5157 | -61.7788 | 61.6125 | 61.7981 | 61.3435 | 61.5009 | -62.0676
3815.7969 | 123.4085 | -61.496 | 61.7065 | 0.0046549 | -0.074452 | 0.022257 | -0.0050408 | -0.010792 | 0.011865 | 0.0077831 | -0.042149 | 0.020383 | 0.017224 | 0.055087 | 0.0063904 | -0.044736 | 0.05635 | -0.012988 | 0.18032 | 0.096516 | 0.39837 | -0.090531 | -0.012689 | 0.041567 | -0.047194 | 0.15318 | 0.34337 | -0.11587 | -0.38393 | 61.4054 | -61.5262 | 61.4512 | 61.483 | 0.077543 | -61.61 | -61.3082 | 61.112 | -61.5534 | 61.4833 | 61.4488 | 0.33674 | -61.3632 | -61.8224 | 61.6763 | 61.5925 | 61.8943 | 61.5523 | -61.7971 | 61.6492 | 61.8393 | 61.3801 | 61.5375 | -62.0905
3816.7969 | 123.3444 | -61.5143 | 61.7432 | -0.0029761 | -0.074025 | 0.022043 | -0.0050408 | -0.010792 | 0.012078 | -0.0074779 | -0.042362 | 0.020383 | 0.017438 | 0.055087 | 0.006604 | -0.040158 | 0.05635 | -0.003831 | 0.1849 | 0.1011 | 0.39837 | -0.09511 | -0.017267 | 0.046146 | -0.042615 | 0.14861 | 0.33421 | -0.11587 | -0.37477 | 61.4192 | -61.5583 | 61.4741 | 61.5105 | 0.091279 | -61.6421 | -61.3448 | 61.1395 | -61.5946 | 61.497 | 61.4717 | 0.33216 | -61.409 | -61.859 | 61.6992 | 61.6154 | 61.9126 | 61.5706 | -61.8383 | 61.6629 | 61.8485 | 61.3984 | 61.5604 | -62.1179
3817.7969 | 123.4451 | -61.5143 | 61.6882 | -0.010607 | -0.074239 | 0.022257 | -0.0054682 | -0.010792 | 0.012078 | 0.00015261 | -0.042576 | 0.020597 | 0.017438 | 0.055087 | 0.006604 | -0.040158 | 0.05635 | -0.008409 | 0.17574 | 0.096516 | 0.4121 | -0.090531 | -0.017267 | 0.046146 | -0.042615 | 0.15318 | 0.35252 | -0.11587 | -0.37477 | 61.4238 | -61.5125 | 61.4741 | 61.5059 | 0.082122 | -61.5917 | -61.2761 | 61.1395 | -61.535 | 61.497 | 61.4717 | 0.33216 | -61.3357 | -61.8041 | 61.69 | 61.6108 | 61.9264 | 61.5706 | -61.7788 | 61.6675 | 61.8668 | 61.3984 | 61.5604 | -62.063
3818.7969 | 123.4726 | -61.4868 | 61.6974 | 0.0046549 | -0.074666 | 0.022257 | -0.0050408 | -0.010365 | 0.012078 | 0.0077831 | -0.042362 | 0.020597 | 0.017224 | 0.055301 | 0.006604 | -0.049315 | 0.051771 | 0.000747 | 0.16659 | 0.096516 | 0.40753 | -0.090531 | -0.021846 | 0.036989 | -0.038036 | 0.15318 | 0.33879 | -0.11587 | -0.37477 | 61.3963 | -61.5308 | 61.4375 | 61.4876 | 0.091278 | -61.6009 | -61.2899 | 61.112 | -61.5442 | 61.465 | 61.4488 | 0.33674 | -61.3586 | -61.8133 | 61.6534 | 61.5833 | 61.8943 | 61.5386 | -61.7879 | 61.64 | 61.8256 | 61.3709 | 61.5238 | -62.0722
3819.7969 | 123.436 | -61.5143 | 61.6837 | -0.010607 | -0.074452 | 0.021616 | -0.0054682 | -0.010578 | 0.012292 | 0.0077831 | -0.042149 | 0.020383 | 0.017865 | 0.054873 | 0.0061766 | -0.040158 | 0.05635 | -0.003831 | 0.16659 | 0.091937 | 0.40753 | -0.085952 | -0.00811 | 0.036989 | -0.047194 | 0.15318 | 0.33879 | -0.11129 | -0.38393 | 61.4283 | -61.5171 | 61.4741 | 61.5105 | 0.082121 | -61.5917 | -61.2761 | 61.1303 | -61.5305 | 61.5062 | 61.4671 | 0.33674 | -61.3449 | -61.7949 | 61.6809 | 61.6062 | 61.9218 | 61.5706 | -61.7696 | 61.6675 | 61.8531 | 61.403 | 61.5513 | -62.0676
3820.7969 | 123.4634 | -61.4822 | 61.7294 | -0.0029761 | -0.073598 | 0.021616 | -0.004827 | -0.010151 | 0.012506 | 0.0077831 | -0.041935 | 0.020597 | 0.017438 | 0.054873 | 0.006604 | -0.040158 | 0.051771 | 0.000747 | 0.18032 | -0.086641 | 0.39379 | 0.069732 | -0.017267 | 0.046146 | -0.051772 | 0.14403 | 0.33421 | -0.17081 | -0.37935 | 61.552 | -61.5491 | 61.4421 | 61.483 | -0.068985 | -61.8161 | -61.3356 | 61.1029 | -61.5854 | 61.465 | 61.4305 | 0.32758 | -61.3952 | -61.9002 | 61.6626 | 61.3956 | 61.876 | 61.534 | -61.6597 | 61.6263 | 61.8164 | 61.3114 | 61.5284 | -62.1088

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.9177 | 22.5133 | 22.4556 | 22.5919
0.0823 | 22.5087 | 22.4611 | 22.5925
1.0823 | 22.5092 | 22.4659 | 22.5911
2.0823 | 22.5159 | 22.4609 | 22.5956
3.0823 | 22.7708 | 22.4623 | 22.5894
4.0823 | 23.6548 | 22.4542 | 22.5971
5.0823 | 25.2735 | 22.4658 | 22.5991
6.0823 | 27.5384 | 22.4765 | 22.6162
7.0823 | 30.3895 | 22.4819 | 22.6476
8.0823 | 33.6728 | 22.5078 | 22.6787
9.0823 | 37.3277 | 22.5314 | 22.7267
10.0823 | 41.324 | 22.5742 | 22.7761
11.0823 | 45.5851 | 22.6138 | 22.8498
12.0823 | 50.1069 | 22.6734 | 22.9243
13.0823 | 54.7779 | 22.735 | 23.0215
14.0823 | 59.6612 | 22.8143 | 23.1504
15.0823 | 64.7225 | 22.8932 | 23.3024
16.0823 | 69.9206 | 22.9896 | 23.4643
17.0823 | 75.2204 | 23.1036 | 23.6343
18.0823 | 80.658 | 23.2191 | 23.8104
19.0823 | 86.1918 | 23.3478 | 24.0145
20.0823 | 91.7338 | 23.5053 | 24.226
21.0823 | 97.4752 | 23.6601 | 24.4535
22.0823 | 103.2871 | 23.8504 | 24.7191
23.0823 | 109.1702 | 24.039 | 25.0054
24.0823 | 115.0568 | 24.255 | 25.306
25.0823 | 121.0755 | 24.4869 | 25.6239
26.0823 | 127.0657 | 24.7347 | 25.9604
27.0823 | 133.062 | 25.0099 | 26.3371
28.0823 | 139.0727 | 25.3073 | 26.7306
29.0823 | 144.9935 | 25.6248 | 27.1225
30.0823 | 150.9681 | 25.9658 | 27.5116
31.0823 | 156.9599 | 26.3475 | 27.9281
32.0823 | 162.9242 | 26.7267 | 28.3822
33.0823 | 168.7361 | 27.144 | 28.8518
34.0823 | 174.6101 | 27.5467 | 29.3659
35.0823 | 180.6196 | 28.0001 | 29.8929
36.0823 | 186.651 | 28.4737 | 30.4513
37.0823 | 192.7142 | 28.9695 | 31.0329
38.0823 | 198.7632 | 29.4982 | 31.6296
39.0823 | 204.6281 | 30.0415 | 32.2363
40.0823 | 210.4965 | 30.6064 | 32.8858
41.0823 | 216.1848 | 31.1845 | 33.5648
42.0823 | 221.8321 | 31.8074 | 34.2647
43.0823 | 227.7044 | 32.4805 | 35.0074
44.0823 | 233.4721 | 33.1456 | 35.7627
45.0823 | 239.2689 | 33.8264 | 36.5599
46.0823 | 245.1802 | 34.5357 | 37.3871
47.0823 | 251.0335 | 35.2596 | 38.2756
48.0823 | 256.6918 | 36.0085 | 39.1594
49.0823 | 262.4677 | 36.7929 | 40.039
50.0823 | 268.2213 | 37.6058 | 40.9579
51.0823 | 273.9513 | 38.4442 | 41.9375
52.0823 | 279.6804 | 39.2977 | 42.9614
53.0823 | 285.2646 | 40.1681 | 43.9934
54.0823 | 290.3964 | 41.063 | 45.0431
55.0823 | 295.0251 | 41.9934 | 46.1067
56.0823 | 299.3683 | 42.9248 | 47.1588
57.0823 | 303.1794 | 43.8588 | 48.2526
58.0823 | 306.9404 | 44.7925 | 49.3338
59.0823 | 310.7107 | 45.7638 | 50.4176
60.0823 | 314.2627 | 46.7545 | 51.5189
61.0823 | 317.5609 | 47.752 | 52.6081
62.0823 | 320.7073 | 48.7486 | 53.6962
63.0823 | 323.5034 | 49.7598 | 54.7938
64.0823 | 325.8617 | 50.7869 | 55.8948
65.0823 | 328.0127 | 51.7957 | 56.9988
66.0823 | 329.9282 | 52.7865 | 58.0662
67.0823 | 331.5356 | 53.7912 | 59.1369
68.0823 | 332.8844 | 54.7727 | 60.1722
69.0823 | 333.9195 | 55.7478 | 61.2038
70.0823 | 334.7757 | 56.6955 | 62.1923
71.0823 | 335.354 | 57.6508 | 63.1719
72.0823 | 335.8572 | 58.5654 | 64.1218
73.0823 | 336.1759 | 59.4757 | 65.0427
74.0823 | 336.3398 | 60.3941 | 65.9525
75.0823 | 336.498 | 61.3105 | 66.839
76.0823 | 336.5886 | 62.192 | 67.707
77.0979 | 336.635 | 63.0694 | 68.552
78.0823 | 336.6406 | 63.9228 | 69.38
79.0823 | 336.5499 | 64.762 | 70.199
80.0823 | 336.1113 | 65.5602 | 71.0003
81.0823 | 335.73 | 66.3687 | 71.76
82.0823 | 335.5089 | 67.2008 | 72.5252
83.0823 | 335.1897 | 67.999 | 73.2881
84.0823 | 334.8874 | 68.768 | 74.0058
85.0823 | 334.5478 | 69.5493 | 74.7366
86.0823 | 334.0046 | 70.324 | 75.4442
87.0823 | 333.5724 | 71.0796 | 76.1641
88.0823 | 333.1951 | 71.8221 | 76.8653
89.0823 | 332.8477 | 72.5913 | 77.5626
90.0823 | 332.4313 | 73.3602 | 78.2394
91.0823 | 331.9145 | 74.1032 | 78.9028
92.0823 | 331.3955 | 74.8379 | 79.5722
93.0823 | 331.0015 | 75.5389 | 80.2459
94.0823 | 330.585 | 76.2531 | 80.882
95.0823 | 330.18 | 76.9857 | 81.5134
96.0823 | 329.7285 | 77.7181 | 82.1361
97.0823 | 329.2325 | 78.4189 | 82.7492
98.0823 | 328.7292 | 79.1223 | 83.3614
99.0823 | 328.3001 | 79.8196 | 83.9794
100.0823 | 327.8642 | 80.5084 | 84.5956
101.0823 | 327.3708 | 81.1768 | 85.208
102.0979 | 327.0108 | 81.8457 | 85.8225
103.0823 | 326.6054 | 82.5049 | 86.4301
104.0823 | 326.2313 | 83.1618 | 87.0202
105.0823 | 325.7978 | 83.8032 | 87.6012
106.0823 | 325.5588 | 84.4142 | 88.1797
107.0979 | 325.2608 | 85.049 | 88.7691
108.0823 | 325.0002 | 85.6722 | 89.3574
109.0823 | 324.9017 | 86.3093 | 89.9533
110.0823 | 324.7865 | 86.9299 | 90.5319
111.0823 | 324.6638 | 87.541 | 91.1038
112.0823 | 324.6004 | 88.1472 | 91.6776
113.0823 | 324.6757 | 88.7574 | 92.2612
114.0823 | 324.6188 | 89.3659 | 92.8288
115.0823 | 324.6322 | 89.9603 | 93.3851
116.0823 | 324.762 | 90.5463 | 93.9387
117.0979 | 324.8289 | 91.1547 | 94.5169
118.0823 | 324.9273 | 91.7708 | 95.103
119.0823 | 325.1472 | 92.3727 | 95.685
120.0823 | 325.4001 | 92.9668 | 96.2581
121.0823 | 325.5114 | 93.5708 | 96.8593
122.0823 | 325.7639 | 94.1661 | 97.4515
123.0979 | 325.9988 | 94.7778 | 98.0616
124.0823 | 326.2877 | 95.3869 | 98.6895
125.0823 | 326.6565 | 96.0117 | 99.3169
126.0823 | 326.9393 | 96.6347 | 99.9263
127.0979 | 327.1685 | 97.2444 | 100.5116
128.0823 | 327.3897 | 97.8562 | 101.0928
129.0823 | 327.7558 | 98.4852 | 101.6688
130.0823 | 327.9994 | 99.0886 | 102.248
131.0823 | 328.3632 | 99.7069 | 102.8393
132.0979 | 328.7372 | 100.3064 | 103.4253
133.0979 | 329.1373 | 100.9162 | 104.0072
134.0823 | 329.4162 | 101.5284 | 104.6014
135.0979 | 329.7815 | 102.1422 | 105.1987
136.0823 | 330.068 | 102.7746 | 105.8112
137.0979 | 330.2472 | 103.4048 | 106.4435
138.0823 | 330.3714 | 104.0339 | 107.0604
139.0823 | 330.5793 | 104.6441 | 107.668
140.0823 | 330.7307 | 105.2691 | 108.2783
141.0823 | 330.9138 | 105.8887 | 108.8987
142.0979 | 331.1771 | 106.5174 | 109.5134
143.0823 | 331.182 | 107.1274 | 110.1152
144.0823 | 331.2497 | 107.7438 | 110.7269
145.0823 | 331.2576 | 108.3665 | 111.3103
146.0823 | 331.2427 | 108.9838 | 111.8683
147.0979 | 331.2754 | 109.5983 | 112.4379
148.0823 | 331.4039 | 110.181 | 112.9927
149.0823 | 331.4849 | 110.7607 | 113.5425
150.0823 | 331.5333 | 111.3349 | 114.0745
151.0823 | 331.6338 | 111.9202 | 114.6117
152.0823 | 331.6996 | 112.5032 | 115.1619
153.0823 | 331.6672 | 113.0872 | 115.7382
154.0823 | 331.7722 | 113.692 | 116.3203
155.0823 | 331.9042 | 114.2778 | 116.887
156.0823 | 331.928 | 114.8924 | 117.4881
157.0823 | 331.9825 | 115.506 | 118.075
158.0823 | 331.8997 | 116.0969 | 118.6389
159.0823 | 331.9878 | 116.6826 | 119.1973
160.0823 | 332.0432 | 117.2549 | 119.7325
161.0823 | 332.0849 | 117.8466 | 120.2635
162.0823 | 332.094 | 118.4186 | 120.8044
163.0823 | 331.998 | 118.9971 | 121.3534
164.0823 | 331.9639 | 119.5774 | 121.9233
165.0823 | 332.0002 | 120.1611 | 122.4972
166.0823 | 331.935 | 120.7361 | 123.077
167.0823 | 331.9694 | 121.2974 | 123.6478
168.0823 | 331.9345 | 121.8658 | 124.2181
169.0823 | 331.8215 | 122.4428 | 124.785
170.0823 | 331.8264 | 123.008 | 125.3321
171.0823 | 331.7802 | 123.5819 | 125.8621
172.0823 | 331.6805 | 124.1596 | 126.3835
173.0823 | 331.6329 | 124.7159 | 126.9305
174.0823 | 331.6056 | 125.2834 | 127.4803
175.0823 | 331.5587 | 125.8468 | 128.0339
176.0823 | 331.3613 | 126.4189 | 128.5615
177.0823 | 331.2432 | 126.9782 | 129.0974
178.0823 | 331.3305 | 127.5491 | 129.6524
179.0823 | 331.3922 | 128.1143 | 130.1975
180.0823 | 331.2999 | 128.6748 | 130.7523
181.0823 | 331.2722 | 129.2254 | 131.3057
182.0823 | 331.3479 | 129.7672 | 131.8337
183.0823 | 331.2838 | 130.3173 | 132.3478
184.0823 | 331.1401 | 130.8656 | 132.87
185.0823 | 331.1761 | 131.3806 | 133.3853
186.0823 | 331.201 | 131.9168 | 133.8987
187.0823 | 331.0772 | 132.4599 | 134.4121
188.0823 | 331.0427 | 133.008 | 134.9507
189.0823 | 330.9647 | 133.5482 | 135.4779
190.0823 | 330.9009 | 134.072 | 135.9696
191.0823 | 330.9315 | 134.5981 | 136.4325
192.0823 | 330.9936 | 135.1041 | 136.9161
193.0823 | 331.0413 | 135.6082 | 137.4193
194.0823 | 331.0808 | 136.1147 | 137.9123
195.0823 | 331.051 | 136.6208 | 138.4023
196.0823 | 330.9904 | 137.136 | 138.8929
197.0823 | 330.9022 | 137.6646 | 139.3737
198.0823 | 330.8387 | 138.1762 | 139.8448
199.0823 | 330.7315 | 138.6737 | 140.3265
200.0823 | 330.7148 | 139.191 | 140.8169
201.0823 | 330.7782 | 139.6998 | 141.2889
202.0823 | 330.7359 | 140.194 | 141.7225
203.0823 | 330.6369 | 140.7033 | 142.1827
204.0823 | 330.5668 | 141.2 | 142.6236
205.0823 | 330.5083 | 141.6457 | 143.0281
206.0823 | 330.5422 | 142.1249 | 143.4266
207.0823 | 330.5888 | 142.5931 | 143.8593
208.0823 | 330.6618 | 143.0916 | 144.3302
209.0823 | 330.6728 | 143.5852 | 144.8017
210.0823 | 330.7024 | 144.0706 | 145.2786
211.0823 | 330.7058 | 144.5769 | 145.7558
212.0823 | 330.7315 | 145.0771 | 146.2373
213.0823 | 330.74 | 145.5772 | 146.7476
214.0823 | 330.8761 | 146.0696 | 147.2328
215.0823 | 331.0251 | 146.5768 | 147.7209
216.0823 | 331.0065 | 147.0605 | 148.1905
217.0823 | 331.135 | 147.5375 | 148.6386
218.0823 | 331.2941 | 148.0331 | 149.1143
219.0823 | 331.2821 | 148.5257 | 149.5928
220.0823 | 331.2178 | 149.0001 | 150.0876
221.0823 | 331.3035 | 149.4821 | 150.5644
222.0823 | 331.2758 | 149.9634 | 151.0545
223.0823 | 331.292 | 150.4362 | 151.4872
224.0823 | 331.3159 | 150.9069 | 151.9188
225.0823 | 331.2458 | 151.3801 | 152.3745
226.0823 | 331.2033 | 151.8562 | 152.8379
227.0823 | 331.2549 | 152.3357 | 153.2653
228.0823 | 331.2953 | 152.7916 | 153.7043
229.0823 | 331.2374 | 153.2634 | 154.1436
230.0823 | 331.195 | 153.739 | 154.6001
231.0823 | 331.1969 | 154.2134 | 155.0236
232.0823 | 331.2427 | 154.6883 | 155.4548
233.0823 | 331.2552 | 155.1212 | 155.8853
234.0823 | 331.1658 | 155.5799 | 156.2976
235.0823 | 331.206 | 156.0266 | 156.7264
236.0823 | 331.346 | 156.4791 | 157.1735
237.0823 | 331.3329 | 156.9422 | 157.6409
238.0823 | 331.3082 | 157.3902 | 158.1112
239.0823 | 331.3066 | 157.8564 | 158.5991
240.0823 | 331.2744 | 158.3047 | 159.0749
241.0823 | 331.2695 | 158.7606 | 159.5562
242.0823 | 331.2766 | 159.2051 | 160.0225
243.0823 | 331.1773 | 159.6559 | 160.4813
244.0823 | 331.2611 | 160.1127 | 160.9383
245.0823 | 331.2693 | 160.5624 | 161.3674
246.0823 | 331.2964 | 160.9912 | 161.7649
247.0823 | 331.221 | 161.4429 | 162.1713
248.0823 | 331.2511 | 161.8843 | 162.5819
249.0823 | 331.1675 | 162.3156 | 163.0022
250.0823 | 331.0706 | 162.7679 | 163.4324
251.0823 | 331.0518 | 163.2093 | 163.8706
252.0823 | 331.0741 | 163.6425 | 164.3009
253.0823 | 331.1034 | 164.0741 | 164.6969
254.0823 | 331.0716 | 164.4967 | 165.0562
255.0823 | 331.1117 | 164.9237 | 165.4268
256.0823 | 331.0925 | 165.3464 | 165.8371
257.0823 | 331.0072 | 165.762 | 166.243
258.0823 | 330.873 | 166.2138 | 166.6505
259.0823 | 330.8193 | 166.638 | 167.0627
260.0823 | 330.7209 | 167.0379 | 167.467
261.0823 | 330.6061 | 167.4749 | 167.8637
262.0823 | 330.6908 | 167.8707 | 168.2117
263.0979 | 330.6335 | 168.27 | 168.5399
264.0823 | 330.5526 | 168.6802 | 168.8812
265.0823 | 330.489 | 169.0757 | 169.227
266.0823 | 330.4537 | 169.4586 | 169.6062
267.0823 | 330.3853 | 169.841 | 170.0012
268.0823 | 330.2663 | 170.2372 | 170.4054
269.0823 | 330.3207 | 170.6352 | 170.7626
270.0823 | 330.3561 | 171.0111 | 171.1478
271.0823 | 330.3776 | 171.4101 | 171.5302
272.0823 | 330.3745 | 171.8131 | 171.8891
273.0823 | 330.4073 | 172.215 | 172.258
274.0823 | 330.3791 | 172.5998 | 172.5946
275.0823 | 330.523 | 172.9937 | 172.9549
276.0823 | 330.589 | 173.3722 | 173.3155
277.0823 | 330.566 | 173.7654 | 173.6556
278.0823 | 330.5139 | 174.1461 | 173.9562
279.0823 | 330.4575 | 174.5013 | 174.2198
280.0823 | 330.4519 | 174.8721 | 174.5644
281.0823 | 330.539 | 175.2492 | 174.9386
282.0823 | 330.5821 | 175.649 | 175.3461
283.0823 | 330.7127 | 176.0554 | 175.7535
284.0823 | 330.7421 | 176.4369 | 176.1338
285.0823 | 330.7146 | 176.8302 | 176.482
286.0823 | 330.6433 | 177.1941 | 176.8517
287.0823 | 330.5997 | 177.5984 | 177.2309
288.0823 | 330.6317 | 177.9766 | 177.5688
289.0823 | 330.6527 | 178.3656 | 177.9447
290.0823 | 330.7131 | 178.7471 | 178.3468
291.0823 | 330.815 | 179.1399 | 178.7413
292.0823 | 330.8994 | 179.5234 | 179.0725
293.0979 | 330.899 | 179.9003 | 179.4101
294.0823 | 330.8171 | 180.2811 | 179.7652
295.0823 | 330.8178 | 180.6591 | 180.1549
296.0823 | 330.8048 | 181.0381 | 180.536
297.0823 | 330.7845 | 181.4222 | 180.8844
298.0823 | 330.8278 | 181.7953 | 181.2649
299.0823 | 330.706 | 182.1707 | 181.6274
300.0823 | 330.6932 | 182.5402 | 181.9934
301.0823 | 330.7978 | 182.9113 | 182.3284
302.0823 | 330.8245 | 183.2861 | 182.667
303.0823 | 330.8294 | 183.6513 | 183.0012
304.0823 | 330.7241 | 184.0178 | 183.357
305.0823 | 330.7388 | 184.3552 | 183.7144
306.0823 | 330.6495 | 184.71 | 184.0731
307.0979 | 330.6274 | 185.0343 | 184.3614
308.0823 | 330.5042 | 185.3925 | 184.6611
309.0823 | 330.4364 | 185.7285 | 184.9814
310.0823 | 330.3859 | 186.0787 | 185.3261
311.0823 | 330.2874 | 186.4538 | 185.6743
312.0823 | 330.1353 | 186.7767 | 186.0139
313.0823 | 330.151 | 187.1394 | 186.3445
314.0823 | 330.1913 | 187.4922 | 186.64
315.0823 | 330.3013 | 187.837 | 186.9246
316.0823 | 330.3892 | 188.1965 | 187.2348
317.0823 | 330.3678 | 188.5428 | 187.5685
318.0823 | 330.2438 | 188.895 | 187.9212
319.0823 | 330.1084 | 189.2485 | 188.2673
320.0823 | 330.1531 | 189.5904 | 188.6158
321.0823 | 330.1506 | 189.9383 | 188.9847
322.0979 | 330.1902 | 190.2743 | 189.3503
323.0823 | 330.0246 | 190.6293 | 189.6519
324.0823 | 329.9499 | 190.9576 | 189.9776
325.0823 | 329.9558 | 191.2991 | 190.2874
326.0823 | 329.9374 | 191.6402 | 190.5834
327.0979 | 329.9545 | 191.9847 | 190.9144
328.0823 | 329.9954 | 192.307 | 191.1823
329.0823 | 330.0228 | 192.6399 | 191.4315
330.0823 | 330.0323 | 192.9577 | 191.7253
331.0823 | 330.0824 | 193.2953 | 192.0388
332.0823 | 330.1694 | 193.6226 | 192.3722
333.0823 | 330.1251 | 193.9568 | 192.7057
334.0823 | 330.1923 | 194.2742 | 193.0475
335.0823 | 330.0604 | 194.6202 | 193.3644
336.0823 | 329.8926 | 194.9532 | 193.6827
337.0979 | 329.9772 | 195.3058 | 194.0251
338.0823 | 329.9633 | 195.6304 | 194.3565
339.0823 | 330.0258 | 195.9464 | 194.6888
340.0823 | 329.9898 | 196.2788 | 195.0184
341.0823 | 329.9672 | 196.596 | 195.3598
342.0823 | 329.9702 | 196.9116 | 195.6661
343.0823 | 329.9922 | 197.2201 | 195.963
344.0823 | 329.9875 | 197.5241 | 196.2853
345.0823 | 330.0305 | 197.8349 | 196.6018
346.0823 | 330.09 | 198.1522 | 196.9083
347.0823 | 330.0865 | 198.4583 | 197.1703
348.0823 | 330.0942 | 198.7609 | 197.3988
349.0823 | 329.9978 | 199.0644 | 197.6021
350.0823 | 329.9675 | 199.3736 | 197.8616
351.0823 | 330.0985 | 199.68 | 198.1493
352.0979 | 330.1441 | 199.9954 | 198.4268
353.0979 | 330.1024 | 200.2897 | 198.6802
354.0823 | 329.9407 | 200.5969 | 198.9265
355.0823 | 329.8777 | 200.8953 | 199.1276
356.0823 | 329.7726 | 201.2112 | 199.3728
357.0823 | 329.7276 | 201.5184 | 199.662
358.0823 | 329.6924 | 201.8167 | 199.9793
359.0823 | 329.738 | 202.1182 | 200.2809
360.0823 | 329.678 | 202.4177 | 200.6031
361.0823 | 329.6529 | 202.718 | 200.9205
362.0979 | 329.6685 | 203.0155 | 201.2341
363.0823 | 329.7091 | 203.3203 | 201.4866
364.0823 | 329.6305 | 203.6181 | 201.7783
365.0823 | 329.6241 | 203.9008 | 202.0892
366.0823 | 329.6394 | 204.193 | 202.3816
367.0979 | 329.6972 | 204.4822 | 202.6673
368.0823 | 329.6642 | 204.7702 | 202.975
369.0823 | 329.62 | 205.0772 | 203.279
370.0823 | 329.6651 | 205.3719 | 203.6037
371.0979 | 329.6936 | 205.6749 | 203.8879
372.0823 | 329.635 | 205.9639 | 204.1752
373.0823 | 329.7236 | 206.1929 | 204.4743
374.0823 | 329.9137 | 206.4807 | 204.7713
375.0823 | 329.9778 | 206.7654 | 205.0418
376.0823 | 329.9306 | 207.0465 | 205.3093
377.0823 | 329.8264 | 207.3405 | 205.5666
378.0823 | 329.8658 | 207.6247 | 205.8374
379.0823 | 329.8977 | 207.8782 | 206.1222
380.0823 | 329.9232 | 208.1516 | 206.4072
381.0823 | 329.8899 | 208.4315 | 206.7134
382.0823 | 329.8589 | 208.7051 | 206.9536
383.0823 | 329.8707 | 208.9736 | 207.2089
384.0823 | 329.8541 | 209.2416 | 207.4756
385.0823 | 329.7746 | 209.5314 | 207.7542
386.0823 | 329.6707 | 209.8023 | 208.048
387.0823 | 329.721 | 210.0706 | 208.3315
388.0823 | 329.7216 | 210.3453 | 208.6156
389.0823 | 329.7258 | 210.6159 | 208.892
390.0823 | 329.678 | 210.8905 | 209.172
391.0823 | 329.6571 | 211.1474 | 209.4572
392.0823 | 329.5626 | 211.414 | 209.7238
393.0823 | 329.5909 | 211.6819 | 209.9814
394.0823 | 329.6202 | 211.9502 | 210.2408
395.0823 | 329.7071 | 212.2038 | 210.4877
396.0823 | 329.8197 | 212.4463 | 210.7588
397.0823 | 329.8225 | 212.7255 | 211.033
398.0823 | 329.8234 | 212.9781 | 211.3002
399.0823 | 329.6787 | 213.2413 | 211.5591
400.0823 | 329.6747 | 213.4848 | 211.8219
401.0823 | 329.7325 | 213.7351 | 212.1035
402.0823 | 329.7104 | 213.9823 | 212.3628
403.0823 | 329.7746 | 214.232 | 212.6173
404.0823 | 329.7284 | 214.4703 | 212.8526
405.0823 | 329.7265 | 214.7357 | 213.103
406.0823 | 329.7194 | 214.9789 | 213.3249
407.0823 | 329.8072 | 215.2182 | 213.561
408.0823 | 329.8375 | 215.467 | 213.7973
409.0823 | 329.8716 | 215.699 | 214.0145
410.0823 | 329.8414 | 215.9347 | 214.2132
411.0823 | 329.8493 | 216.1748 | 214.4145
412.0823 | 329.8115 | 216.4044 | 214.5881
413.0823 | 329.8114 | 216.6406 | 214.7672
414.0823 | 329.7614 | 216.8936 | 214.9435
415.0823 | 329.7946 | 217.1284 | 215.1146
416.0823 | 329.8177 | 217.3818 | 215.2453
417.0823 | 329.8177 | 217.606 | 215.3972
418.0823 | 329.7744 | 217.8605 | 215.5965
419.0823 | 329.7369 | 218.1077 | 215.8083
420.0823 | 329.649 | 218.3407 | 216.0266
421.0823 | 329.6328 | 218.5766 | 216.2604
422.0823 | 329.707 | 218.8123 | 216.5037
423.0823 | 329.7477 | 219.0424 | 216.7465
424.0823 | 329.751 | 219.2577 | 216.9686
425.0823 | 329.7845 | 219.4905 | 217.2043
426.0823 | 329.7637 | 219.6884 | 217.427
427.0823 | 329.6567 | 219.9297 | 217.6374
428.0823 | 329.6382 | 220.1608 | 217.8363
429.0823 | 329.6582 | 220.393 | 217.994
430.0823 | 329.649 | 220.6009 | 218.1475
431.0823 | 329.5705 | 220.8464 | 218.349
432.0823 | 329.5166 | 221.0599 | 218.5327
433.0823 | 329.4244 | 221.2929 | 218.7109
434.0823 | 329.409 | 221.5093 | 218.8655
435.0823 | 329.5249 | 221.7184 | 219.024
436.0823 | 329.5926 | 221.9534 | 219.2054
437.0823 | 329.6525 | 222.1725 | 219.4019
438.0823 | 329.7086 | 222.3819 | 219.5899
439.0823 | 329.6473 | 222.6186 | 219.7867
440.0823 | 329.6086 | 222.8435 | 220.0023
441.0823 | 329.5574 | 223.0702 | 220.2276
442.0823 | 329.5514 | 223.2976 | 220.4597
443.0823 | 329.5157 | 223.5109 | 220.6873
444.0823 | 329.5171 | 223.7456 | 220.9312
445.0823 | 329.513 | 223.9656 | 221.1752
446.0823 | 329.4433 | 224.197 | 221.3954
447.0823 | 329.3591 | 224.4087 | 221.6387
448.0823 | 329.3428 | 224.6464 | 221.8965
449.0823 | 329.4147 | 224.8636 | 222.1289
450.0823 | 329.5096 | 225.0641 | 222.3666
451.0823 | 329.6057 | 225.2655 | 222.5846
452.0823 | 329.6669 | 225.4777 | 222.8185
453.0823 | 329.7074 | 225.6806 | 223.0342
454.0823 | 329.7606 | 225.8838 | 223.2473
455.0823 | 329.7099 | 226.0839 | 223.4505
456.0823 | 329.8448 | 226.3022 | 223.654
457.0823 | 329.8334 | 226.4948 | 223.8506
458.0823 | 329.7631 | 226.6922 | 224.0639
459.0823 | 329.7066 | 226.9029 | 224.2883
460.0823 | 329.7174 | 227.1217 | 224.4817
461.0823 | 329.6894 | 227.3167 | 224.6357
462.0823 | 329.7562 | 227.5144 | 224.7819
463.0823 | 329.78 | 227.7147 | 224.9339
464.0823 | 329.7964 | 227.9014 | 225.0698
465.0823 | 329.8473 | 228.0918 | 225.2084
466.0823 | 329.9182 | 228.2986 | 225.3649
467.0823 | 329.8634 | 228.4985 | 225.5542
468.0823 | 329.781 | 228.6959 | 225.7402
469.0823 | 329.6693 | 228.8805 | 225.9267
470.0823 | 329.6805 | 229.0842 | 226.1
471.0823 | 329.7892 | 229.2595 | 226.2613
472.0823 | 329.8166 | 229.4534 | 226.4256
473.0979 | 329.8254 | 229.6411 | 226.574
474.0823 | 329.8259 | 229.8187 | 226.7476
475.0823 | 329.7857 | 230.0183 | 226.9171
476.0823 | 329.748 | 230.1906 | 227.0885
477.0823 | 329.6886 | 230.3621 | 227.2592
478.0823 | 329.6298 | 230.5304 | 227.4596
479.0823 | 329.6163 | 230.7138 | 227.6672
480.0823 | 329.522 | 230.9002 | 227.8751
481.0823 | 329.4679 | 231.0857 | 228.0789
482.0823 | 329.4574 | 231.2607 | 228.2763
483.0823 | 329.3892 | 231.4498 | 228.4736
484.0823 | 329.372 | 231.6373 | 228.6746
485.0823 | 329.316 | 231.82 | 228.8308
486.0823 | 329.3125 | 231.9802 | 228.9649
487.0823 | 329.3085 | 232.1501 | 229.0896
488.0823 | 329.3228 | 232.3105 | 229.2266
489.0823 | 329.2107 | 232.4856 | 229.3193
490.0823 | 329.2878 | 232.6317 | 229.441
491.0823 | 329.3191 | 232.8007 | 229.5871
492.0823 | 329.308 | 232.9659 | 229.7409
493.0823 | 329.301 | 233.1213 | 229.8913
494.0823 | 329.3369 | 233.2675 | 230.0318
495.0823 | 329.3884 | 233.398 | 230.1589
496.0823 | 329.4274 | 233.5345 | 230.3038
497.0823 | 329.4211 | 233.6886 | 230.4083
498.0823 | 329.3349 | 233.8291 | 230.4908
499.0823 | 329.3963 | 233.9599 | 230.6043
500.0823 | 329.402 | 234.1096 | 230.6795
501.0823 | 329.4425 | 234.2577 | 230.7704
502.0979 | 329.4089 | 234.3994 | 230.8649
503.0979 | 329.3947 | 234.546 | 231.0049
504.0823 | 329.411 | 234.6984 | 231.1707
505.0823 | 329.3481 | 234.8383 | 231.3371
506.0823 | 329.3197 | 235.0147 | 231.51
507.0823 | 329.3381 | 235.1588 | 231.6513
508.0823 | 329.3077 | 235.3261 | 231.8221
509.0823 | 329.3042 | 235.4767 | 231.984
510.0823 | 329.19 | 235.6314 | 232.1432
511.0823 | 329.1007 | 235.7983 | 232.2907
512.0823 | 329.1068 | 235.9458 | 232.4542
513.0823 | 329.2132 | 236.1192 | 232.6019
514.0823 | 329.3669 | 236.2817 | 232.75
515.0979 | 329.3092 | 236.4418 | 232.856
516.0823 | 329.1966 | 236.5945 | 232.9598
517.0823 | 329.2013 | 236.7475 | 233.0812
518.0823 | 329.1998 | 236.9165 | 233.2412
519.0823 | 329.1259 | 237.0664 | 233.4039
520.0823 | 328.9916 | 237.2167 | 233.5556
521.0979 | 328.9616 | 237.3714 | 233.7086
522.0979 | 329.0225 | 237.5241 | 233.8382
523.0823 | 329.0537 | 237.6643 | 233.9661
524.0823 | 329.0551 | 237.8161 | 234.1195
525.0823 | 329.0692 | 237.9616 | 234.2888
526.0823 | 329.1016 | 238.105 | 234.4481
527.0979 | 329.1422 | 238.2526 | 234.6292
528.0823 | 329.0415 | 238.3205 | 234.806
529.0979 | 328.9628 | 238.474 | 234.9833
530.0823 | 328.9015 | 238.6282 | 235.1691
531.0823 | 328.8515 | 238.7924 | 235.2987
532.0979 | 328.8753 | 238.9401 | 235.4276
533.0979 | 328.7894 | 239.0904 | 235.5788
534.0823 | 328.6426 | 239.2287 | 235.7253
535.0823 | 328.5774 | 239.3728 | 235.8774
536.0823 | 328.6748 | 239.5108 | 236
537.0823 | 328.6572 | 239.6562 | 236.1308
538.0823 | 328.5809 | 239.79 | 236.2634
539.0823 | 328.5882 | 239.9375 | 236.4106
540.0823 | 328.5664 | 240.07 | 236.5015
541.0823 | 328.5683 | 240.2143 | 236.5723
542.0979 | 328.6339 | 240.3292 | 236.6604
543.0823 | 328.5821 | 240.4546 | 236.7263
544.0823 | 328.6383 | 240.5747 | 236.8064
545.0823 | 328.7043 | 240.6988 | 236.885
546.0823 | 328.701 | 240.8237 | 236.9671
547.0979 | 328.6438 | 240.9338 | 237.0514
548.0823 | 328.5795 | 241.0308 | 237.137
549.0823 | 328.5762 | 241.1406 | 237.2562
550.0823 | 328.5231 | 241.2552 | 237.3934
551.0823 | 328.4791 | 241.3724 | 237.544
552.0823 | 328.4549 | 241.5111 | 237.6839
553.0823 | 328.4923 | 241.6269 | 237.7994
554.0823 | 328.5407 | 241.7641 | 237.9194
555.0823 | 328.6544 | 241.8835 | 238.0246
556.0823 | 328.7588 | 241.9966 | 238.1292
557.0979 | 328.8699 | 242.1205 | 238.2481
558.0823 | 328.8398 | 242.2495 | 238.3738
559.0823 | 328.8315 | 242.3884 | 238.515
560.0823 | 328.8096 | 242.5056 | 238.6457
561.0823 | 328.8032 | 242.6194 | 238.7891
562.0823 | 328.7857 | 242.7437 | 238.911
563.0979 | 328.8157 | 242.8668 | 239.0416
564.0823 | 328.7818 | 242.9809 | 239.1882
565.0823 | 328.758 | 243.1085 | 239.3398
566.0823 | 328.6761 | 243.2247 | 239.4998
567.0823 | 328.7189 | 243.3583 | 239.6442
568.0823 | 328.7879 | 243.4814 | 239.7859
569.0823 | 328.8342 | 243.5941 | 239.9077
570.0823 | 328.7605 | 243.7224 | 240.0404
571.0823 | 328.6485 | 243.8419 | 240.151
572.0979 | 328.6064 | 243.9721 | 240.2528
573.0823 | 328.5839 | 244.0891 | 240.3637
574.0823 | 328.5116 | 244.2106 | 240.4797
575.0823 | 328.5507 | 244.3279 | 240.6084
576.0823 | 328.5831 | 244.4419 | 240.7223
577.0823 | 328.585 | 244.5593 | 240.8057
578.0823 | 328.5579 | 244.6751 | 240.8534
579.0823 | 328.5932 | 244.7761 | 240.9236
580.0823 | 328.5966 | 244.9123 | 241.0266
581.0823 | 328.6019 | 245.0237 | 241.1534
582.0979 | 328.5598 | 245.1306 | 241.2904
583.0823 | 328.5843 | 245.2285 | 241.3586
584.0823 | 328.4439 | 245.3244 | 241.4421
585.0823 | 328.2976 | 245.4438 | 241.5424
586.0823 | 328.3103 | 245.5551 | 241.6396
587.0823 | 328.3641 | 245.6639 | 241.7471
588.0823 | 328.3546 | 245.7669 | 241.8708
589.0823 | 328.3976 | 245.9003 | 242.003
590.0823 | 328.4671 | 246.0235 | 242.138
591.0823 | 328.3201 | 246.1308 | 242.2636
592.0823 | 328.3097 | 246.2288 | 242.3057
593.0823 | 328.3627 | 246.3411 | 242.3123
594.0823 | 328.426 | 246.4408 | 242.3572
595.0823 | 328.5023 | 246.5413 | 242.3941
596.0823 | 328.484 | 246.6292 | 242.4539
597.0823 | 328.5396 | 246.7552 | 242.5285
598.0823 | 328.5854 | 246.8414 | 242.614
599.0823 | 328.5916 | 246.951 | 242.688
600.0823 | 328.5078 | 247.0582 | 242.7745
601.0823 | 328.5697 | 247.1591 | 242.8713
602.0823 | 328.5686 | 247.259 | 242.9792
603.0823 | 328.5423 | 247.3751 | 243.1095
604.0823 | 328.5558 | 247.4788 | 243.2382
605.0823 | 328.5725 | 247.5653 | 243.3583
606.0823 | 328.5748 | 247.6456 | 243.4334
607.0823 | 328.5887 | 247.7454 | 243.5192
608.0823 | 328.4934 | 247.8398 | 243.6072
609.0823 | 328.5186 | 247.9355 | 243.7071
610.0823 | 328.5852 | 248.034 | 243.8063
611.0823 | 328.5629 | 248.1224 | 243.9188
612.0823 | 328.5809 | 248.2169 | 244.0218
613.0823 | 328.5535 | 248.3303 | 244.1456
614.0823 | 328.4914 | 248.4161 | 244.2735
615.0823 | 328.3402 | 248.5312 | 244.4098
616.0823 | 328.3936 | 248.6352 | 244.5448
617.0823 | 328.4042 | 248.7241 | 244.67
618.0823 | 328.419 | 248.8406 | 244.763
619.0823 | 328.4082 | 248.9429 | 244.8398
620.0823 | 328.4494 | 249.0481 | 244.9055
621.0823 | 328.3868 | 249.1434 | 244.9533
622.0823 | 328.2447 | 249.2365 | 245.0327
623.0823 | 328.2544 | 249.3301 | 245.1185
624.0823 | 328.3277 | 249.4288 | 245.2181
625.0823 | 328.4194 | 249.5209 | 245.3089
626.0823 | 328.4712 | 249.6106 | 245.4081
627.0823 | 328.3671 | 249.7161 | 245.4895
628.0823 | 328.3813 | 249.8044 | 245.5386
629.0823 | 328.3115 | 249.8987 | 245.596
630.0823 | 328.3121 | 249.9865 | 245.6868
631.0823 | 328.3787 | 250.0772 | 245.7776
632.0823 | 328.4043 | 250.15 | 245.8549
633.0823 | 328.439 | 250.2292 | 245.9485
634.0823 | 328.4535 | 250.3214 | 246.0418
635.0823 | 328.3936 | 250.4043 | 246.1327
636.0823 | 328.3947 | 250.4921 | 246.2399
637.0823 | 328.4759 | 250.5095 | 246.3598
638.0823 | 328.5182 | 250.5941 | 246.4746
639.0823 | 328.4916 | 250.6929 | 246.5783
640.0823 | 328.4651 | 250.7723 | 246.6748
641.0823 | 328.4003 | 250.8607 | 246.7727
642.0823 | 328.3515 | 250.9468 | 246.8667
643.0823 | 328.4009 | 251.05 | 246.9757
644.0823 | 328.4371 | 251.1409 | 247.0738
645.0823 | 328.41 | 251.2265 | 247.1725
646.0823 | 328.3444 | 251.3168 | 247.2844
647.0823 | 328.3508 | 251.4004 | 247.4007
648.0823 | 328.3574 | 251.4814 | 247.5063
649.0823 | 328.3623 | 251.5568 | 247.588
650.0823 | 328.2963 | 251.6362 | 247.6738
651.0823 | 328.2762 | 251.7167 | 247.7489
652.0823 | 328.3626 | 251.8111 | 247.8011
653.0823 | 328.316 | 251.8982 | 247.8845
654.0823 | 328.2637 | 251.9807 | 247.9634
655.0823 | 328.2207 | 252.0606 | 248.0412
656.0823 | 328.3199 | 252.1337 | 248.1001
657.0823 | 328.3808 | 252.1945 | 248.1376
658.0823 | 328.384 | 252.2635 | 248.1774
659.0823 | 328.2174 | 252.335 | 248.2617
660.0823 | 328.2472 | 252.4097 | 248.3431
661.0823 | 328.3661 | 252.4929 | 248.4375
662.0823 | 328.4384 | 252.5627 | 248.5339
663.0823 | 328.4142 | 252.6553 | 248.6307
664.0823 | 328.3027 | 252.7258 | 248.7274
665.0823 | 328.2188 | 252.8083 | 248.7983
666.0823 | 328.215 | 252.8736 | 248.8497
667.0823 | 328.2719 | 252.9539 | 248.9087
668.0823 | 328.2865 | 253.0261 | 248.9709
669.0823 | 328.2722 | 253.1114 | 249.0491
670.0823 | 328.2202 | 253.1797 | 249.1211
671.0823 | 328.2806 | 253.2438 | 249.1944
672.0823 | 328.2778 | 253.312 | 249.2783
673.0823 | 328.3165 | 253.3864 | 249.3749
674.0823 | 328.2638 | 253.4573 | 249.4789
675.0823 | 328.2581 | 253.5292 | 249.5789
676.0823 | 328.3235 | 253.6198 | 249.6782
677.0823 | 328.3387 | 253.688 | 249.772
678.0823 | 328.4627 | 253.7657 | 249.8652
679.0823 | 328.5015 | 253.7994 | 249.9381
680.0823 | 328.5259 | 253.8863 | 250.0058
681.0823 | 328.5077 | 253.9478 | 250.0785
682.0823 | 328.4542 | 254.017 | 250.1579
683.0823 | 328.4366 | 254.0889 | 250.2452
684.0823 | 328.4105 | 254.1548 | 250.3426
685.0823 | 328.4966 | 254.2332 | 250.4437
686.0823 | 328.4962 | 254.2868 | 250.5328
687.0823 | 328.5252 | 254.3675 | 250.5927
688.0823 | 328.5589 | 254.4277 | 250.6423
689.0979 | 328.4658 | 254.5013 | 250.6857
690.0823 | 328.4273 | 254.5505 | 250.7341
691.0823 | 328.4724 | 254.5942 | 250.7837
692.0979 | 328.4355 | 254.6537 | 250.8405
693.0823 | 328.3782 | 254.7029 | 250.9105
694.0823 | 328.3248 | 254.7811 | 250.9812
695.0823 | 328.3096 | 254.8431 | 251.0598
696.0823 | 328.2651 | 254.9033 | 251.144
697.0823 | 328.2516 | 254.9805 | 251.2282
698.0823 | 328.2293 | 255.042 | 251.3045
699.0823 | 328.2281 | 255.1114 | 251.3762
700.0823 | 328.2446 | 255.1744 | 251.4257
701.0823 | 328.0892 | 255.239 | 251.4693
702.0823 | 328.0961 | 255.3117 | 251.5339
703.0823 | 328.0917 | 255.3758 | 251.5801
704.0823 | 328.0095 | 255.4463 | 251.6291
705.0823 | 328.0612 | 255.4946 | 251.6745
706.0823 | 327.9793 | 255.5766 | 251.7163
707.0979 | 328.0656 | 255.6571 | 251.782
708.0823 | 328.1077 | 255.7106 | 251.8198
709.0823 | 328.1261 | 255.7895 | 251.8691
710.0823 | 328.0849 | 255.8474 | 251.9458
711.0823 | 328.0435 | 255.9202 | 252.0173
712.0979 | 328.0048 | 255.9902 | 252.0441
713.0823 | 327.9611 | 256.0504 | 252.0812
714.0823 | 327.8471 | 256.1091 | 252.1128
715.0823 | 327.8621 | 256.1763 | 252.1764
716.0823 | 327.8822 | 256.2314 | 252.2696
717.0823 | 327.8891 | 256.3038 | 252.3425
718.0823 | 327.9055 | 256.3572 | 252.4209
719.0823 | 327.9078 | 256.4372 | 252.498
720.0823 | 327.7918 | 256.4848 | 252.5352
721.0823 | 327.8469 | 256.5512 | 252.5574
722.0979 | 327.8215 | 256.6086 | 252.5956
723.0823 | 327.7719 | 256.6755 | 252.6423
724.0823 | 327.6383 | 256.7297 | 252.6796
725.0823 | 327.6002 | 256.7769 | 252.7054
726.0823 | 327.6683 | 256.717 | 252.7429
727.0823 | 327.7367 | 256.8056 | 252.7586
728.0823 | 327.8113 | 256.8628 | 252.7705
729.0823 | 327.8366 | 256.9177 | 252.7875
730.0979 | 327.8353 | 256.981 | 252.8174
731.0823 | 327.7933 | 257.0407 | 252.8432
732.0823 | 327.6448 | 257.0851 | 252.8507
733.0823 | 327.7007 | 257.1541 | 252.8111
734.0823 | 327.7308 | 257.1962 | 252.7779
735.0823 | 327.814 | 257.2399 | 252.7848
736.0823 | 327.9 | 257.2675 | 252.8034
737.0823 | 327.9709 | 257.347 | 252.8556
738.0823 | 328.1256 | 257.4041 | 252.9098
739.0979 | 328.2166 | 257.4397 | 252.9656
740.0823 | 328.2127 | 257.5123 | 253.0305
741.0823 | 328.0895 | 257.5676 | 253.1137
742.0823 | 328.0946 | 257.6224 | 253.2078
743.0823 | 328.1644 | 257.6648 | 253.2589
744.0823 | 328.2561 | 257.7364 | 253.3337
745.0823 | 328.2941 | 257.787 | 253.4017
746.0823 | 328.278 | 257.8425 | 253.4547
747.0979 | 328.1912 | 257.9019 | 253.5175
748.0823 | 328.1359 | 257.9576 | 253.574
749.0823 | 328.0439 | 258.005 | 253.6305
750.0823 | 327.977 | 258.0545 | 253.6918
751.0823 | 327.9915 | 258.1041 | 253.7508
752.0979 | 328.048 | 258.1511 | 253.8227
753.0823 | 328.037 | 258.2201 | 253.8947
754.0823 | 328.0507 | 258.2724 | 253.974
755.0823 | 328.0633 | 258.3247 | 254.0534
756.0979 | 328.1419 | 258.3807 | 254.1149
757.0823 | 328.1789 | 258.423 | 254.1615
758.0823 | 328.2325 | 258.4624 | 254.211
759.0823 | 328.2209 | 258.5128 | 254.2582
760.0823 | 328.292 | 258.5578 | 254.3005
761.0823 | 328.3339 | 258.6246 | 254.3012
762.0979 | 328.2721 | 258.6758 | 254.3403
763.0823 | 328.2971 | 258.7494 | 254.4157
764.0823 | 328.4024 | 258.8068 | 254.4961
765.0823 | 328.5272 | 258.8702 | 254.5578
766.0979 | 328.5889 | 258.9157 | 254.6162
767.0979 | 328.5128 | 258.9724 | 254.6634
768.0823 | 328.4851 | 259.0198 | 254.6969
769.0823 | 328.582 | 259.0656 | 254.7327
770.0823 | 328.5821 | 259.1189 | 254.7564
771.0823 | 328.4854 | 259.1734 | 254.801
772.0823 | 328.4803 | 259.2284 | 254.8661
773.0823 | 328.6191 | 259.279 | 254.9136
774.0823 | 328.7339 | 259.3381 | 254.9466
775.0823 | 328.5876 | 259.3933 | 254.9854
776.0823 | 328.4715 | 259.4575 | 255.0248
777.0823 | 328.3436 | 259.5001 | 255.0819
778.0823 | 328.3941 | 259.5514 | 255.1479
779.0823 | 328.4298 | 259.6107 | 255.201
780.0823 | 328.3793 | 259.6551 | 255.2428
781.0823 | 328.2988 | 259.7117 | 255.2904
782.0823 | 328.2236 | 259.7637 | 255.339
783.0823 | 328.1678 | 259.8173 | 255.3794
784.0823 | 328.0817 | 259.8552 | 255.4218
785.0823 | 327.9389 | 259.8932 | 255.4678
786.0823 | 327.8836 | 259.9268 | 255.5086
787.0823 | 327.8302 | 259.9562 | 255.5275
788.0823 | 327.8338 | 259.9957 | 255.579
789.0823 | 327.7911 | 260.0412 | 255.6239
790.0979 | 327.8494 | 260.0846 | 255.6879
791.0823 | 327.8386 | 260.1193 | 255.7483
792.0823 | 327.8607 | 260.1577 | 255.8003
793.0823 | 327.9282 | 260.1916 | 255.8509
794.0823 | 327.9228 | 260.2208 | 255.892
795.0823 | 327.9551 | 260.2586 | 255.9223
796.0823 | 328.0385 | 260.2841 | 255.9655
797.0823 | 327.9861 | 260.3323 | 256.0206
798.0823 | 327.9473 | 260.3762 | 256.0754
799.0823 | 327.9371 | 260.4101 | 256.1133
800.0823 | 327.9917 | 260.4602 | 256.1486
801.0823 | 327.902 | 260.5016 | 256.1821
802.0823 | 327.8558 | 260.5432 | 256.1914
803.0823 | 327.8797 | 260.5749 | 256.209
804.0823 | 327.9297 | 260.6232 | 256.2384
805.0823 | 327.869 | 260.6676 | 256.2641
806.0823 | 327.8096 | 260.7086 | 256.3132
807.0823 | 327.7793 | 260.7379 | 256.3838
808.0823 | 327.7623 | 260.7944 | 256.4502
809.0823 | 327.7052 | 260.8191 | 256.503
810.0823 | 327.7165 | 260.8594 | 256.5506
811.0823 | 327.7965 | 260.8938 | 256.5865
812.0823 | 327.8114 | 260.9347 | 256.6242
813.0823 | 327.8672 | 260.9839 | 256.6671
814.0823 | 327.8195 | 261.0224 | 256.7081
815.0823 | 327.7485 | 261.07 | 256.7434
816.0823 | 327.7545 | 261.1089 | 256.7545
817.0823 | 327.8301 | 261.1671 | 256.7911
818.0823 | 327.7973 | 261.2193 | 256.8551
819.0823 | 327.7876 | 261.2603 | 256.9106
820.0823 | 327.8453 | 261.2944 | 256.9509
821.0823 | 327.8446 | 261.3456 | 256.9931
822.0823 | 327.8995 | 261.3877 | 257.0322
823.0823 | 327.9197 | 261.4254 | 257.0684
824.0823 | 327.9337 | 261.4612 | 257.1052
825.0823 | 327.8515 | 261.4959 | 257.128
826.0823 | 327.751 | 261.5335 | 257.1562
827.0823 | 327.8644 | 261.5788 | 257.2062
828.0823 | 327.9337 | 261.6011 | 257.2585
829.0823 | 327.8896 | 261.6426 | 257.3246
830.0823 | 327.9526 | 261.6708 | 257.3824
831.0823 | 327.9412 | 261.7145 | 257.4352
832.0823 | 327.9974 | 261.7482 | 257.502
833.0823 | 328.0741 | 261.7711 | 257.5555
834.0823 | 328.1775 | 261.8186 | 257.6097
835.0823 | 328.314 | 261.8745 | 257.6726
836.0823 | 328.3554 | 261.9137 | 257.7213
837.0823 | 328.3337 | 261.9612 | 257.7717
838.0823 | 328.3517 | 262.0083 | 257.824
839.0823 | 328.276 | 262.046 | 257.8796
840.0823 | 328.2422 | 262.1012 | 257.9218
841.0823 | 328.287 | 262.1476 | 257.9541
842.0823 | 328.3319 | 262.179 | 258.0133
843.0823 | 328.4166 | 262.2194 | 258.054
844.0823 | 328.5001 | 262.2467 | 258.1015
845.0823 | 328.3774 | 262.3096 | 258.1577
846.0823 | 328.3451 | 262.3378 | 258.192
847.0823 | 328.3774 | 262.3762 | 258.2443
848.0823 | 328.3342 | 262.4142 | 258.3044
849.0823 | 328.4389 | 262.4323 | 258.3689
850.0979 | 328.4911 | 262.4763 | 258.3845
851.0823 | 328.4561 | 262.494 | 258.3976
852.0823 | 328.467 | 262.4888 | 258.3964
853.0823 | 328.4284 | 262.4756 | 258.4067
854.0823 | 328.4412 | 262.4866 | 258.4213
855.0823 | 328.3881 | 262.5042 | 258.4387
856.0823 | 328.3533 | 262.5078 | 258.4482
857.0823 | 328.3183 | 262.5065 | 258.4106
858.0823 | 328.4022 | 262.5589 | 258.4414
859.0979 | 328.4426 | 262.589 | 258.4678
860.0823 | 328.4388 | 262.6346 | 258.5324
861.0823 | 328.4877 | 262.6677 | 258.6021
862.0823 | 328.4291 | 262.7055 | 258.6646
863.0823 | 328.448 | 262.7545 | 258.7207
864.0823 | 328.465 | 262.7929 | 258.7777
865.0823 | 328.444 | 262.8389 | 258.8201
866.0823 | 328.4543 | 262.8769 | 258.8749
867.0823 | 328.3911 | 262.9112 | 258.9294
868.0823 | 328.3636 | 262.9548 | 258.9607
869.0823 | 328.4519 | 262.9832 | 258.9852
870.0979 | 328.4252 | 263.017 | 258.9902
871.0823 | 328.4869 | 263.0487 | 259.0136
872.0979 | 328.4912 | 263.0947 | 259.0403
873.0823 | 328.5054 | 263.13 | 259.064
874.0823 | 328.4169 | 263.163 | 259.1003
875.0823 | 328.3708 | 263.2126 | 259.1185
876.0979 | 328.3116 | 263.2472 | 259.1361
877.0823 | 328.2441 | 263.2997 | 259.1382
878.0823 | 328.2548 | 263.3315 | 259.1567
879.0979 | 328.2626 | 263.3721 | 259.1748
880.0823 | 328.1626 | 263.4167 | 259.2122
881.0823 | 328.1226 | 263.4687 | 259.2578
882.0823 | 328.0309 | 263.5017 | 259.2815
883.0823 | 328.022 | 263.5283 | 259.2917
884.0823 | 328.0368 | 263.5715 | 259.3063
885.0823 | 328.0041 | 263.6118 | 259.3053
886.0823 | 327.8325 | 263.65 | 259.3186
887.0979 | 327.7795 | 263.6792 | 259.3325
888.0823 | 327.7574 | 263.7116 | 259.3474
889.0823 | 327.7538 | 263.7538 | 259.3759
890.0823 | 327.8165 | 263.7885 | 259.3978
891.0979 | 327.8742 | 263.8003 | 259.409
892.0823 | 327.8573 | 263.8181 | 259.4328
893.0823 | 327.8579 | 263.8648 | 259.4628
894.0823 | 327.8342 | 263.8962 | 259.4903
895.0823 | 327.7615 | 263.9391 | 259.5251
896.0823 | 327.7398 | 263.9759 | 259.5723
897.0823 | 327.7968 | 264.0174 | 259.6145
898.0823 | 327.9252 | 264.0519 | 259.661
899.0823 | 328.019 | 264.0875 | 259.7014
900.0823 | 328.1015 | 264.1152 | 259.7361
901.0823 | 328.145 | 264.1464 | 259.7655
902.0823 | 328.1203 | 264.1744 | 259.7772
903.0823 | 328.1115 | 264.204 | 259.8034
904.0823 | 328.0934 | 264.2207 | 259.8157
905.0823 | 328.0466 | 264.2444 | 259.82
906.0823 | 327.943 | 264.2894 | 259.8429
907.0823 | 327.9301 | 264.3274 | 259.8217
908.0823 | 327.8755 | 264.3767 | 259.8134
909.0823 | 327.8623 | 264.4197 | 259.8371
910.0823 | 327.8946 | 264.451 | 259.8617
911.0823 | 327.8411 | 264.4918 | 259.8879
912.0979 | 327.8492 | 264.5368 | 259.9299
913.0823 | 327.7832 | 264.5522 | 259.9645
914.0823 | 327.772 | 264.5752 | 259.9675
915.0979 | 327.6355 | 264.5946 | 259.8939
916.0823 | 327.5782 | 264.6287 | 259.8681
917.0823 | 327.5403 | 264.6587 | 259.8855
918.0823 | 327.5363 | 264.6886 | 259.933
919.0823 | 327.6026 | 264.7187 | 259.9763
920.0823 | 327.5541 | 264.7428 | 260.0214
921.0823 | 327.5512 | 264.7577 | 260.0399
922.0823 | 327.5571 | 264.788 | 260.0329
923.0823 | 327.6008 | 264.8064 | 260.0214
924.0823 | 327.709 | 264.8472 | 260.0473
925.0823 | 327.752 | 264.8789 | 260.0777
926.0823 | 327.7296 | 264.9043 | 260.1244
927.0979 | 327.7883 | 264.9118 | 260.1639
928.0823 | 327.8329 | 264.9378 | 260.2145
929.0823 | 327.7979 | 264.9627 | 260.271
930.0823 | 327.6887 | 264.9743 | 260.3174
931.0823 | 327.7305 | 265.0052 | 260.3418
932.0979 | 327.7072 | 265.0191 | 260.3539
933.0823 | 327.7114 | 265.0332 | 260.3311
934.0823 | 327.7287 | 265.056 | 260.3453
935.0823 | 327.7653 | 265.0773 | 260.369
936.0823 | 327.7005 | 265.1076 | 260.4015
937.0823 | 327.7149 | 265.1418 | 260.4519
938.0823 | 327.7164 | 265.1763 | 260.4979
939.0823 | 327.7748 | 265.2066 | 260.5136
940.0823 | 327.836 | 265.2218 | 260.5113
941.0823 | 327.8496 | 265.2471 | 260.5132
942.0979 | 327.8697 | 265.2447 | 260.5227
943.0823 | 327.8865 | 265.248 | 260.5435
944.0823 | 327.9568 | 265.2712 | 260.5563
945.0823 | 327.9821 | 265.3033 | 260.5902
946.0823 | 328.0365 | 265.3311 | 260.628
947.0823 | 328.1055 | 265.3546 | 260.6819
948.0823 | 328.1303 | 265.3996 | 260.7193
949.0823 | 328.0765 | 265.4416 | 260.7537
950.0823 | 328.0598 | 265.4846 | 260.7996
951.0823 | 327.935 | 265.5176 | 260.8532
952.0823 | 327.8382 | 265.5363 | 260.9039
953.0823 | 327.8261 | 265.5793 | 260.9377
954.0823 | 327.8755 | 265.6004 | 260.9751
955.0823 | 327.945 | 265.6252 | 261.0126
956.0823 | 327.9294 | 265.6573 | 261.0544
957.0979 | 327.8974 | 265.6688 | 261.092
958.0823 | 327.9891 | 265.7122 | 261.1509
959.0823 | 328.0298 | 265.7612 | 261.2042
960.0823 | 328.0884 | 265.7955 | 261.2405
961.0823 | 328.1491 | 265.8383 | 261.2481
962.0823 | 328.182 | 265.8718 | 261.2948
963.0823 | 328.2697 | 265.9214 | 261.3267
964.0823 | 328.3126 | 265.9513 | 261.3536
965.0823 | 328.3102 | 265.9851 | 261.3872
966.0823 | 328.3879 | 266.0239 | 261.4208
967.0979 | 328.4121 | 266.0575 | 261.4676
968.0823 | 328.4372 | 266.0892 | 261.4822
969.0823 | 328.4063 | 266.1297 | 261.5095
970.0979 | 328.4498 | 266.1523 | 261.5229
971.0823 | 328.5279 | 266.1926 | 261.5544
972.0979 | 328.5385 | 266.2233 | 261.583
973.0823 | 328.5021 | 266.2379 | 261.5904
974.0823 | 328.3649 | 266.2636 | 261.5527
975.0823 | 328.2359 | 266.2799 | 261.5106
976.0823 | 328.1666 | 266.2851 | 261.4974
977.0823 | 328.1935 | 266.3002 | 261.4903
978.0823 | 328.272 | 266.321 | 261.4822
979.0823 | 328.3018 | 266.3314 | 261.4862
980.0823 | 328.3118 | 266.3722 | 261.5123
981.0823 | 328.2657 | 266.3927 | 261.5368
982.0823 | 328.1581 | 266.4013 | 261.5539
983.0823 | 328.0197 | 266.4193 | 261.5595
984.0823 | 327.997 | 266.4398 | 261.5792
985.0823 | 327.9395 | 266.4536 | 261.6077
986.0823 | 327.8388 | 266.4716 | 261.6362
987.0823 | 327.7294 | 266.4711 | 261.6577
988.0823 | 327.702 | 266.4643 | 261.6931
989.0823 | 327.6947 | 266.4644 | 261.7263
990.0823 | 327.6689 | 266.4711 | 261.7667
991.0823 | 327.6481 | 266.4651 | 261.8036
992.0823 | 327.6877 | 266.5157 | 261.8316
993.0823 | 327.6867 | 266.5362 | 261.8767
994.0823 | 327.7123 | 266.5526 | 261.9076
995.0823 | 327.647 | 266.5645 | 261.9436
996.0823 | 327.5682 | 266.5968 | 261.9577
997.0823 | 327.6959 | 266.6387 | 261.9962
998.0823 | 327.7502 | 266.681 | 262.0439
999.0823 | 327.8049 | 266.7168 | 262.0913
1000.0823 | 327.712 | 266.744 | 262.1174
1001.0823 | 327.6905 | 266.8089 | 262.1688
1002.0823 | 327.6241 | 266.8468 | 262.2087
1003.0823 | 327.602 | 266.8862 | 262.2393
1004.0823 | 327.5888 | 266.9179 | 262.2333
1005.0823 | 327.5868 | 266.9382 | 262.2214
1006.0823 | 327.5148 | 266.9584 | 262.2069
1007.0823 | 327.4617 | 266.9729 | 262.1937
1008.0823 | 327.478 | 266.9916 | 262.2131
1009.0823 | 327.4688 | 266.9997 | 262.2196
1010.0823 | 327.526 | 266.9939 | 262.2512
1011.0823 | 327.6359 | 267.0179 | 262.2964
1012.0979 | 327.5459 | 267.0275 | 262.3385
1013.0823 | 327.522 | 267.0523 | 262.3553
1014.0823 | 327.5134 | 267.0665 | 262.3619
1015.0823 | 327.3912 | 267.0982 | 262.3671
1016.0823 | 327.3518 | 267.1216 | 262.383
1017.0823 | 327.3488 | 267.1571 | 262.4193
1018.0823 | 327.3974 | 267.1836 | 262.4454
1019.0823 | 327.3558 | 267.2147 | 262.4861
1020.0823 | 327.3752 | 267.2467 | 262.543
1021.0823 | 327.4117 | 267.2732 | 262.6017
1022.0823 | 327.4458 | 267.2978 | 262.6369
1023.0823 | 327.4918 | 267.3265 | 262.6609
1024.0823 | 327.4966 | 267.3559 | 262.6739
1025.0823 | 327.4249 | 267.3758 | 262.6969
1026.0823 | 327.4948 | 267.41 | 262.714
1027.0823 | 327.5993 | 267.4217 | 262.7148
1028.0823 | 327.6139 | 267.3963 | 262.7227
1029.0823 | 327.5621 | 267.4024 | 262.7303
1030.0823 | 327.5263 | 267.4244 | 262.7336
1031.0823 | 327.5379 | 267.467 | 262.7471
1032.0823 | 327.6013 | 267.4969 | 262.7806
1033.0823 | 327.7041 | 267.5032 | 262.8058
1034.0823 | 327.7357 | 267.5442 | 262.8325
1035.0823 | 327.8348 | 267.5151 | 262.8537
1036.0823 | 327.7037 | 267.531 | 262.8861
1037.0823 | 327.688 | 267.5389 | 262.9307
1038.0823 | 327.6621 | 267.5506 | 262.9539
1039.0823 | 327.7355 | 267.54 | 262.967
1040.0823 | 327.7045 | 267.5668 | 262.968
1041.0823 | 327.6483 | 267.5783 | 262.9935
1042.0823 | 327.5844 | 267.6047 | 263.0209
1043.0823 | 327.5529 | 267.6317 | 263.0541
1044.0823 | 327.5075 | 267.6174 | 263.0789
1045.0823 | 327.5645 | 267.6344 | 263.0959
1046.0823 | 327.6234 | 267.6611 | 263.068
1047.0823 | 327.6257 | 267.6844 | 263.0502
1048.0823 | 327.6582 | 267.712 | 263.0108
1049.0823 | 327.7352 | 267.757 | 262.9799
1050.0823 | 327.7644 | 267.7876 | 262.9752
1051.0823 | 327.7429 | 267.8248 | 262.9837
1052.0823 | 327.6581 | 267.8403 | 263.0023
1053.0823 | 327.627 | 267.878 | 263.0244
1054.0823 | 327.5711 | 267.9017 | 263.0668
1055.0823 | 327.4692 | 267.9495 | 263.1283
1056.0823 | 327.4779 | 267.985 | 263.1564
1057.0823 | 327.4064 | 268.0018 | 263.1426
1058.0823 | 327.3915 | 268.0155 | 263.0777
1059.0823 | 327.3433 | 268.0438 | 263.0534
1060.0823 | 327.3194 | 268.0591 | 263.0282
1061.0823 | 327.3105 | 268.0933 | 263.0431
1062.0823 | 327.2752 | 268.0942 | 263.0355
1063.0823 | 327.2083 | 268.1346 | 263.0383
1064.0823 | 327.1953 | 268.1674 | 263.0742
1065.0823 | 327.1215 | 268.2044 | 263.1089
1066.0823 | 327.0867 | 268.2264 | 263.1385
1067.0823 | 327.0866 | 268.2511 | 263.1493
1068.0823 | 327.1778 | 268.2729 | 263.1699
1069.0823 | 327.1722 | 268.2931 | 263.182
1070.0823 | 327.1129 | 268.3012 | 263.1901
1071.0823 | 327.2184 | 268.3071 | 263.174
1072.0823 | 327.3813 | 268.3137 | 263.1767
1073.0823 | 327.4526 | 268.3296 | 263.2078
1074.0823 | 327.4523 | 268.3344 | 263.2383
1075.0823 | 327.474 | 268.3363 | 263.2887
1076.0823 | 327.5272 | 268.3543 | 263.3387
1077.0979 | 327.63 | 268.3791 | 263.3634
1078.0823 | 327.6523 | 268.4087 | 263.4075
1079.0823 | 327.7786 | 268.4141 | 263.4346
1080.0823 | 327.9158 | 268.4549 | 263.4379
1081.0823 | 327.9922 | 268.4791 | 263.4596
1082.0979 | 327.952 | 268.5005 | 263.4976
1083.0823 | 327.8938 | 268.5308 | 263.5065
1084.0823 | 327.9096 | 268.5254 | 263.5414
1085.0823 | 327.9431 | 268.517 | 263.5871
1086.0823 | 327.9752 | 268.5194 | 263.6243
1087.0823 | 328.0452 | 268.5352 | 263.6531
1088.0823 | 328.0126 | 268.5308 | 263.6693
1089.0823 | 328.0503 | 268.5483 | 263.6708
1090.0979 | 328.0249 | 268.5637 | 263.6764
1091.0979 | 327.9541 | 268.5845 | 263.6643
1092.0979 | 327.8676 | 268.6282 | 263.6657
1093.0979 | 327.9024 | 268.6695 | 263.6954
1094.0823 | 327.9836 | 268.7029 | 263.7163
1095.0979 | 327.9564 | 268.7327 | 263.7361
1096.0979 | 327.9021 | 268.7462 | 263.7496
1097.0979 | 327.9166 | 268.7568 | 263.7601
1098.0823 | 327.8677 | 268.7651 | 263.7833
1099.0823 | 327.8464 | 268.7633 | 263.8059
1100.0823 | 327.9124 | 268.77 | 263.826
1101.0823 | 327.9682 | 268.7764 | 263.8534
1102.0823 | 327.9548 | 268.7951 | 263.8779
1103.0823 | 327.9697 | 268.8083 | 263.8977
1104.0823 | 327.913 | 268.8295 | 263.908
1105.0823 | 327.9104 | 268.8481 | 263.9437
1106.0823 | 327.9279 | 268.8813 | 263.983
1107.0823 | 327.9082 | 268.9099 | 263.9869
1108.0823 | 328.0146 | 268.9453 | 264.0026
1109.0823 | 328.0376 | 268.9746 | 264.0341
1110.0823 | 327.9855 | 268.9721 | 264.0736
1111.0823 | 328.0163 | 269.0011 | 264.1203
1112.0823 | 328.0631 | 269.0105 | 264.1647
1113.0823 | 328.0172 | 269.0281 | 264.2029
1114.0823 | 327.9456 | 269.0397 | 264.235
1115.0979 | 327.9487 | 269.0492 | 264.2383
1116.0823 | 327.9176 | 269.0504 | 264.2308
1117.0823 | 327.8765 | 269.1081 | 264.2578
1118.0823 | 327.8295 | 269.1371 | 264.2684
1119.0823 | 327.9398 | 269.1468 | 264.2766
1120.0823 | 328.0314 | 269.1561 | 264.2677
1121.0979 | 328.082 | 269.163 | 264.2672
1122.0979 | 328.0536 | 269.1681 | 264.2704
1123.0823 | 328.0063 | 269.1853 | 264.276
1124.0823 | 328.0276 | 269.2016 | 264.3012
1125.0979 | 328.0212 | 269.2049 | 264.3161
1126.0823 | 327.9922 | 269.2065 | 264.3243
1127.0823 | 327.9715 | 269.2106 | 264.3155
1128.0823 | 327.9935 | 269.2061 | 264.3122
1129.0823 | 327.9544 | 269.214 | 264.2515
1130.0823 | 327.916 | 269.2162 | 264.2219
1131.0823 | 327.9381 | 269.2251 | 264.2156
1132.0979 | 328.0669 | 269.2247 | 264.228
1133.0979 | 328.0932 | 269.2326 | 264.2504
1134.0823 | 328.0287 | 269.2464 | 264.2692
1135.0823 | 327.9848 | 269.2857 | 264.2931
1136.0823 | 327.9025 | 269.3253 | 264.3232
1137.0823 | 327.7869 | 269.3671 | 264.3435
1138.0823 | 327.6382 | 269.4072 | 264.3522
1139.0823 | 327.5445 | 269.4098 | 264.2895
1140.0823 | 327.5076 | 269.3999 | 264.2075
1141.0823 | 327.3 | 269.3967 | 264.1286
1142.0823 | 327.3241 | 269.4005 | 264.0797
1143.0823 | 327.3979 | 269.4243 | 264.0474
1144.0823 | 327.3459 | 269.438 | 264.0406
1145.0823 | 327.4483 | 269.4641 | 264.046
1146.0823 | 327.4127 | 269.4781 | 264.0472
1147.0979 | 327.4073 | 269.4943 | 264.055
1148.0823 | 327.5284 | 269.515 | 264.084
1149.0979 | 327.5982 | 269.5303 | 264.1196
1150.0979 | 327.5979 | 269.558 | 264.1683
1151.0823 | 327.5156 | 269.5926 | 264.1978
1152.0979 | 327.5941 | 269.6171 | 264.2338
1153.0823 | 327.5257 | 269.6482 | 264.2681
1154.0979 | 327.5463 | 269.6832 | 264.2866
1155.0823 | 327.5206 | 269.7174 | 264.2318
1156.0823 | 327.523 | 269.7497 | 264.2103
1157.0823 | 327.5596 | 269.7767 | 264.2359
1158.0823 | 327.5315 | 269.8023 | 264.2495
1159.0823 | 327.6067 | 269.8408 | 264.2569
1160.0823 | 327.6258 | 269.8469 | 264.2479
1161.0823 | 327.6022 | 269.8643 | 264.2555
1162.0823 | 327.632 | 269.8765 | 264.2635
1163.0823 | 327.6799 | 269.8933 | 264.2794
1164.0823 | 327.6874 | 269.9033 | 264.3295
1165.0823 | 327.7759 | 269.9013 | 264.3616
1166.0823 | 327.8595 | 269.8963 | 264.3939
1167.0823 | 327.8795 | 269.9053 | 264.3996
1168.0823 | 327.9517 | 269.8856 | 264.4216
1169.0823 | 327.9842 | 269.906 | 264.4497
1170.0823 | 327.9658 | 269.9285 | 264.4674
1171.0823 | 327.9089 | 269.9333 | 264.5053
1172.0823 | 327.9062 | 269.954 | 264.5083
1173.0823 | 327.9251 | 269.9526 | 264.5249
1174.0823 | 327.9436 | 269.9855 | 264.5663
1175.0823 | 327.9206 | 270.0185 | 264.6247
1176.0823 | 327.9583 | 270.0457 | 264.6989
1177.0823 | 328.0199 | 270.0723 | 264.7538
1178.0823 | 328.0859 | 270.1014 | 264.8184
1179.0823 | 328.0069 | 270.1261 | 264.84
1180.0823 | 327.9149 | 270.1605 | 264.8547
1181.0823 | 327.9979 | 270.1946 | 264.8761
1182.0823 | 328.049 | 270.2203 | 264.8566
1183.0823 | 328.0328 | 270.2403 | 264.841
1184.0823 | 327.9555 | 270.2737 | 264.8453
1185.0823 | 327.9506 | 270.2878 | 264.8642
1186.0823 | 327.8718 | 270.2869 | 264.8898
1187.0979 | 327.8309 | 270.2983 | 264.9274
1188.0823 | 327.8327 | 270.3019 | 264.9718
1189.0823 | 327.7736 | 270.3075 | 264.9948
1190.0823 | 327.7457 | 270.3152 | 265.0147
1191.0823 | 327.8055 | 270.3015 | 265.0287
1192.0823 | 327.73 | 270.2799 | 265.0287
1193.0823 | 327.6912 | 270.2741 | 265.0691
1194.0823 | 327.6828 | 270.2423 | 265.1138
1195.0823 | 327.6699 | 270.2463 | 265.1459
1196.0823 | 327.7452 | 270.2544 | 265.1658
1197.0823 | 327.7891 | 270.2805 | 265.1729
1198.0823 | 327.8299 | 270.311 | 265.2023
1199.0823 | 327.8622 | 270.3197 | 265.2091
1200.0823 | 327.8618 | 270.2803 | 265.182
1201.0823 | 327.9517 | 270.2276 | 265.1758
1202.0823 | 328.056 | 270.1986 | 265.2012
1203.0823 | 328.1893 | 270.1991 | 265.2446
1204.0823 | 328.1096 | 270.209 | 265.2669
1205.0823 | 328.1063 | 270.2283 | 265.284
1206.0823 | 328.171 | 270.2584 | 265.336
1207.0823 | 328.1823 | 270.2553 | 265.3646
1208.0823 | 328.1547 | 270.2586 | 265.3973
1209.0823 | 328.0595 | 270.2565 | 265.4378
1210.0979 | 328.0658 | 270.256 | 265.4805
1211.0823 | 328.194 | 270.2444 | 265.5108
1212.0823 | 328.2257 | 270.2396 | 265.5248
1213.0823 | 328.2878 | 270.2415 | 265.5545
1214.0823 | 328.3543 | 270.2403 | 265.5588
1215.0823 | 328.3774 | 270.2482 | 265.5586
1216.0823 | 328.4074 | 270.2478 | 265.5722
1217.0823 | 328.4938 | 270.2537 | 265.5937
1218.0823 | 328.5845 | 270.2736 | 265.6024
1219.0823 | 328.5281 | 270.3175 | 265.6348
1220.0823 | 328.5825 | 270.3473 | 265.664
1221.0823 | 328.692 | 270.3892 | 265.6794
1222.0823 | 328.705 | 270.4249 | 265.67
1223.0823 | 328.7275 | 270.4656 | 265.6688
1224.0823 | 328.7156 | 270.5009 | 265.6701
1225.0823 | 328.7795 | 270.5254 | 265.6858
1226.0823 | 328.7396 | 270.5495 | 265.6764
1227.0823 | 328.6996 | 270.5772 | 265.6928
1228.0823 | 328.5839 | 270.608 | 265.7118
1229.0823 | 328.6221 | 270.6315 | 265.7421
1230.0823 | 328.589 | 270.6541 | 265.7626
1231.0823 | 328.5599 | 270.669 | 265.7855
1232.0823 | 328.4865 | 270.6778 | 265.8008
1233.0823 | 328.3572 | 270.699 | 265.8284
1234.0823 | 328.147 | 270.7138 | 265.8634
1235.0823 | 328.0207 | 270.7424 | 265.8751
1236.0823 | 327.966 | 270.7632 | 265.8906
1237.0823 | 327.859 | 270.7706 | 265.9104
1238.0823 | 327.7899 | 270.7535 | 265.914
1239.0979 | 327.7555 | 270.7447 | 265.9192
1240.0823 | 327.6604 | 270.7321 | 265.927
1241.0823 | 327.5668 | 270.7335 | 265.9414
1242.0979 | 327.5083 | 270.7296 | 265.9473
1243.0823 | 327.4702 | 270.7218 | 265.976
1244.0823 | 327.4249 | 270.7047 | 266.0037
1245.0823 | 327.4118 | 270.696 | 266.0185
1246.0823 | 327.4075 | 270.6992 | 266.0124
1247.0823 | 327.4342 | 270.7194 | 266.0261
1248.0823 | 327.4651 | 270.7466 | 266.0576
1249.0823 | 327.48 | 270.7901 | 266.1037
1250.0823 | 327.4778 | 270.8279 | 266.1316
1251.0823 | 327.4568 | 270.8579 | 266.1244
1252.0823 | 327.4353 | 270.8879 | 266.0843
1253.0823 | 327.4271 | 270.9155 | 266.0838
1254.0823 | 327.4631 | 270.9534 | 266.0803
1255.0823 | 327.4281 | 271.0087 | 266.096
1256.0823 | 327.3469 | 271.0228 | 266.1177
1257.0979 | 327.3605 | 271.0583 | 266.1353
1258.0823 | 327.3986 | 271.0654 | 266.1257
1259.0823 | 327.4463 | 271.0825 | 266.1267
1260.0823 | 327.4042 | 271.1014 | 266.1417
1261.0823 | 327.4063 | 271.1144 | 266.1456
1262.0823 | 327.48 | 271.1252 | 266.0759
1263.0823 | 327.5307 | 271.1476 | 266.038
1264.0823 | 327.6037 | 271.1555 | 266.0451
1265.0979 | 327.7067 | 271.1818 | 266.0634
1266.0823 | 327.7054 | 271.1849 | 266.0653
1267.0823 | 327.7156 | 271.2016 | 266.0781
1268.0823 | 327.6754 | 271.209 | 266.1009
1269.0823 | 327.6391 | 271.2138 | 266.136
1270.0823 | 327.6382 | 271.2399 | 266.1829
1271.0823 | 327.6663 | 271.2618 | 266.2249
1272.0979 | 327.6536 | 271.2688 | 266.2556
1273.0823 | 327.6513 | 271.2789 | 266.2609
1274.0823 | 327.7464 | 271.2874 | 266.2384
1275.0823 | 327.6719 | 271.2961 | 266.2243
1276.0823 | 327.6505 | 271.3177 | 266.2516
1277.0823 | 327.695 | 271.3374 | 266.2837
1278.0823 | 327.7543 | 271.3523 | 266.3037
1279.0823 | 327.7242 | 271.381 | 266.3299
1280.0823 | 327.6406 | 271.4182 | 266.3494
1281.0823 | 327.6011 | 271.4594 | 266.3763
1282.0823 | 327.5797 | 271.4889 | 266.3525
1283.0823 | 327.6157 | 271.5109 | 266.3107
1284.0823 | 327.612 | 271.5302 | 266.2935
1285.0823 | 327.682 | 271.5323 | 266.3143
1286.0823 | 327.697 | 271.536 | 266.3394
1287.0823 | 327.6795 | 271.5265 | 266.3823
1288.0823 | 327.7255 | 271.5386 | 266.4254
1289.0823 | 327.7843 | 271.5168 | 266.4767
1290.0823 | 327.748 | 271.4887 | 266.5173
1291.0823 | 327.7223 | 271.4324 | 266.572
1292.0823 | 327.816 | 271.3919 | 266.6338
1293.0823 | 327.9293 | 271.3478 | 266.6709
1294.0823 | 327.9625 | 271.3093 | 266.6875
1295.0823 | 327.9434 | 271.3007 | 266.7095
1296.0823 | 327.9868 | 271.2881 | 266.7152
1297.0979 | 328.0142 | 271.2886 | 266.7325
1298.0823 | 328.0826 | 271.3065 | 266.7541
1299.0823 | 328.0503 | 271.3233 | 266.7875
1300.0823 | 327.9693 | 271.3466 | 266.7874
1301.0823 | 327.9002 | 271.3679 | 266.7495
1302.0979 | 327.8919 | 271.3694 | 266.6968
1303.0823 | 327.845 | 271.3547 | 266.6145
1304.0823 | 327.805 | 271.3425 | 266.5102
1305.0823 | 327.7116 | 271.3475 | 266.437
1306.0823 | 327.7783 | 271.3532 | 266.3849
1307.0823 | 327.7905 | 271.3587 | 266.3558
1308.0823 | 327.7754 | 271.3586 | 266.3603
1309.0823 | 327.7223 | 271.3863 | 266.3911
1310.0823 | 327.6787 | 271.3762 | 266.3933
1311.0823 | 327.6519 | 271.409 | 266.3899
1312.0979 | 327.5929 | 271.4254 | 266.4189
1313.0823 | 327.5146 | 271.4432 | 266.4344
1314.0823 | 327.5065 | 271.465 | 266.4462
1315.0823 | 327.4954 | 271.4942 | 266.4613
1316.0823 | 327.5922 | 271.5008 | 266.5033
1317.0979 | 327.6372 | 271.5078 | 266.5613
1318.0823 | 327.5579 | 271.5264 | 266.6214
1319.0823 | 327.4508 | 271.5335 | 266.6388
1320.0823 | 327.3753 | 271.5614 | 266.6709
1321.0823 | 327.3893 | 271.5852 | 266.7114
1322.0823 | 327.4513 | 271.6096 | 266.7581
1323.0823 | 327.414 | 271.6194 | 266.7758
1324.0823 | 327.413 | 271.6132 | 266.7847
1325.0823 | 327.3539 | 271.629 | 266.7943
1326.0823 | 327.3712 | 271.6386 | 266.8079
1327.0823 | 327.3936 | 271.6418 | 266.8156
1328.0823 | 327.3775 | 271.6367 | 266.8265
1329.0823 | 327.4235 | 271.6512 | 266.8496
1330.0979 | 327.4098 | 271.6766 | 266.8679
1331.0823 | 327.4649 | 271.6844 | 266.8741
1332.0823 | 327.5706 | 271.695 | 266.8819
1333.0823 | 327.5767 | 271.7171 | 266.9217
1334.0823 | 327.5889 | 271.755 | 266.9532
1335.0823 | 327.5907 | 271.793 | 266.9778
1336.0823 | 327.5233 | 271.8242 | 267.0151
1337.0823 | 327.4783 | 271.8367 | 267.0584
1338.0823 | 327.3725 | 271.82 | 267.0542
1339.0823 | 327.3897 | 271.8113 | 267.0732
1340.0823 | 327.5091 | 271.8112 | 267.1015
1341.0823 | 327.6517 | 271.8244 | 267.1422
1342.0823 | 327.7434 | 271.8568 | 267.1681
1343.0823 | 327.7452 | 271.8715 | 267.1973
1344.0823 | 327.762 | 271.8974 | 267.2109
1345.0823 | 327.8281 | 271.9311 | 267.2144
1346.0823 | 327.7747 | 271.9542 | 267.2504
1347.0823 | 327.76 | 271.979 | 267.2803
1348.0823 | 327.7385 | 271.9819 | 267.293
1349.0823 | 327.7405 | 271.9824 | 267.318
1350.0823 | 327.7145 | 271.9793 | 267.3235
1351.0823 | 327.6698 | 271.9751 | 267.3179
1352.0823 | 327.5812 | 271.9522 | 267.329
1353.0823 | 327.5887 | 271.944 | 267.3393
1354.0823 | 327.5499 | 271.9149 | 267.3515
1355.0823 | 327.6234 | 271.9276 | 267.3525
1356.0823 | 327.6729 | 271.9475 | 267.3473
1357.0823 | 327.672 | 271.9443 | 267.3306
1358.0823 | 327.7603 | 271.9515 | 267.3015
1359.0823 | 327.7776 | 271.9707 | 267.2722
1360.0823 | 327.7207 | 271.9781 | 267.2245
1361.0823 | 327.7349 | 271.9834 | 267.1847
1362.0823 | 327.7173 | 271.9591 | 267.1496
1363.0823 | 327.7374 | 271.9764 | 267.1115
1364.0823 | 327.6487 | 271.9867 | 267.0768
1365.0823 | 327.6149 | 271.9661 | 267.0504
1366.0823 | 327.6335 | 271.9663 | 267.0359
1367.0823 | 327.5694 | 271.9651 | 267.0361
1368.0823 | 327.4845 | 271.9663 | 267.0448
1369.0823 | 327.4361 | 271.9633 | 267.055
1370.0823 | 327.4901 | 271.9488 | 267.0561
1371.0823 | 327.4061 | 271.952 | 267.0745
1372.0979 | 327.3739 | 271.9357 | 267.1173
1373.0823 | 327.2818 | 271.9602 | 267.1824
1374.0823 | 327.2121 | 271.9872 | 267.2329
1375.0823 | 327.0538 | 271.989 | 267.2415
1376.0823 | 327.0607 | 272.0017 | 267.2409
1377.0823 | 327.1185 | 272.0063 | 267.2542
1378.0823 | 327.1403 | 272.0003 | 267.2766
1379.0823 | 327.3059 | 271.9953 | 267.3114
1380.0823 | 327.3342 | 271.9826 | 267.3233
1381.0823 | 327.3472 | 271.9619 | 267.3298
1382.0823 | 327.3264 | 271.9512 | 267.3566
1383.0823 | 327.382 | 271.9738 | 267.3872
1384.0823 | 327.3917 | 271.9971 | 267.4191
1385.0823 | 327.4043 | 272.0135 | 267.4435
1386.0823 | 327.4052 | 272.0089 | 267.4619
1387.0823 | 327.4303 | 272.0283 | 267.49
1388.0823 | 327.4652 | 272.0335 | 267.4947
1389.0823 | 327.4885 | 272.0299 | 267.5053
1390.0823 | 327.4914 | 272.0551 | 267.5138
1391.0823 | 327.457 | 272.0574 | 267.5047
1392.0823 | 327.542 | 272.0535 | 267.4861
1393.0823 | 327.5853 | 272.0868 | 267.4624
1394.0823 | 327.6866 | 272.113 | 267.4496
1395.0823 | 327.7702 | 272.1346 | 267.447
1396.0823 | 327.7978 | 272.1555 | 267.4733
1397.0823 | 327.8477 | 272.1742 | 267.4939
1398.0823 | 327.8523 | 272.182 | 267.5094
1399.0823 | 327.8179 | 272.2007 | 267.533
1400.0823 | 327.8423 | 272.2267 | 267.56
1401.0823 | 327.8713 | 272.2511 | 267.5581
1402.0823 | 327.9644 | 272.2672 | 267.5622
1403.0823 | 327.9851 | 272.3097 | 267.5936
1404.0979 | 327.9165 | 272.3218 | 267.6122
1405.0823 | 327.9184 | 272.3334 | 267.6299
1406.0823 | 327.8058 | 272.3364 | 267.6637
1407.0823 | 327.7818 | 272.3446 | 267.686
1408.0823 | 327.7979 | 272.3664 | 267.7142
1409.0823 | 327.8594 | 272.3776 | 267.7459
1410.0823 | 327.7613 | 272.3693 | 267.7588
1411.0823 | 327.7299 | 272.3639 | 267.7812
1412.0823 | 327.8435 | 272.3774 | 267.82
1413.0823 | 327.8628 | 272.385 | 267.8175
1414.0823 | 327.8993 | 272.3862 | 267.8237
1415.0823 | 327.8928 | 272.3601 | 267.8448
1416.0823 | 327.9417 | 272.3483 | 267.8618
1417.0823 | 327.9316 | 272.3129 | 267.8885
1418.0823 | 327.9911 | 272.2893 | 267.9091
1419.0823 | 328.0057 | 272.2892 | 267.9111
1420.0823 | 328.0807 | 272.2673 | 267.9001
1421.0823 | 328.1801 | 272.2484 | 267.8785
1422.0823 | 328.1743 | 272.2572 | 267.8487
1423.0823 | 328.1717 | 272.2543 | 267.8535
1424.0823 | 328.1509 | 272.2707 | 267.8442
1425.0823 | 328.1385 | 272.2852 | 267.8607
1426.0823 | 328.1313 | 272.2979 | 267.8315
1427.0823 | 328.1016 | 272.3102 | 267.8209
1428.0823 | 328.1081 | 272.3192 | 267.8331
1429.0823 | 328.0673 | 272.3303 | 267.8252
1430.0823 | 328.0264 | 272.3385 | 267.8412
1431.0823 | 327.9722 | 272.376 | 267.8632
1432.0823 | 327.8859 | 272.3639 | 267.9147
1433.0823 | 327.8166 | 272.3554 | 267.9501
1434.0979 | 327.7931 | 272.341 | 268.0074
1435.0823 | 327.7845 | 272.3346 | 268.0373
1436.0823 | 327.7429 | 272.3239 | 268.0594
1437.0979 | 327.7245 | 272.3229 | 268.0887
1438.0823 | 327.6728 | 272.3357 | 268.1234
1439.0823 | 327.6479 | 272.3607 | 268.121
1440.0823 | 327.6578 | 272.3815 | 268.0878
1441.0823 | 327.6464 | 272.3922 | 268.0282
1442.0823 | 327.623 | 272.4238 | 268.0161
1443.0823 | 327.5734 | 272.4189 | 268.0054
1444.0823 | 327.5545 | 272.4241 | 268.0027
1445.0823 | 327.5335 | 272.4296 | 267.994
1446.0823 | 327.5967 | 272.4596 | 268.0194
1447.0823 | 327.5481 | 272.4749 | 268.0165
1448.0823 | 327.5204 | 272.4663 | 268.0314
1449.0823 | 327.5323 | 272.4939 | 268.021
1450.0979 | 327.5261 | 272.4914 | 268.0075
1451.0823 | 327.5035 | 272.5157 | 268.0104
1452.0823 | 327.56 | 272.5122 | 268.0125
1453.0823 | 327.574 | 272.5106 | 268.0235
1454.0823 | 327.6378 | 272.5043 | 268.0264
1455.0823 | 327.7085 | 272.4934 | 268.0351
1456.0823 | 327.8028 | 272.4912 | 268.0445
1457.0823 | 327.8475 | 272.4757 | 268.0022
1458.0823 | 327.9281 | 272.4708 | 267.9685
1459.0823 | 327.9806 | 272.4771 | 267.9522
1460.0823 | 327.9657 | 272.4858 | 267.962
1461.0823 | 327.9777 | 272.515 | 267.972
1462.0979 | 328.0127 | 272.537 | 267.9725
1463.0823 | 328.1194 | 272.5406 | 267.9429
1464.0979 | 328.1027 | 272.5555 | 267.9434
1465.0823 | 328.1607 | 272.5851 | 267.9594
1466.0823 | 328.1769 | 272.6252 | 267.9853
1467.0979 | 328.1852 | 272.6471 | 268.0267
1468.0823 | 328.1055 | 272.6719 | 268.0384
1469.0823 | 328.1295 | 272.6922 | 268.0597
1470.0823 | 328.1422 | 272.7142 | 268.0506
1471.0823 | 328.1755 | 272.7306 | 268.0188
1472.0823 | 328.2022 | 272.7645 | 267.9785
1473.0823 | 328.2443 | 272.7768 | 267.9932
1474.0823 | 328.2672 | 272.7943 | 268.0007
1475.0979 | 328.2 | 272.8076 | 268.0252
1476.0823 | 328.2524 | 272.8281 | 268.0702
1477.0979 | 328.286 | 272.8599 | 268.1126
1478.0823 | 328.2511 | 272.8768 | 268.1527
1479.0979 | 328.1974 | 272.8742 | 268.1795
1480.0823 | 328.1822 | 272.8574 | 268.1962
1481.0823 | 328.138 | 272.8373 | 268.2012
1482.0979 | 328.0808 | 272.8171 | 268.1832
1483.0823 | 328.0603 | 272.8046 | 268.1642
1484.0979 | 327.9886 | 272.7671 | 268.1488
1485.0823 | 327.9368 | 272.7925 | 268.1592
1486.0823 | 327.9545 | 272.7868 | 268.1887
1487.0823 | 327.9791 | 272.7919 | 268.212
1488.0823 | 328.045 | 272.8011 | 268.234
1489.0979 | 327.9778 | 272.8174 | 268.2322
1490.0823 | 327.9298 | 272.8141 | 268.2459
1491.0823 | 327.8912 | 272.8247 | 268.2667
1492.0979 | 327.8829 | 272.8065 | 268.2758
1493.0823 | 327.7732 | 272.8014 | 268.2755
1494.0979 | 327.7551 | 272.7817 | 268.2795
1495.0823 | 327.8129 | 272.7562 | 268.2991
1496.0823 | 327.8178 | 272.7425 | 268.3048
1497.0823 | 327.8149 | 272.7421 | 268.2927
1498.0823 | 327.7743 | 272.7338 | 268.2971
1499.0823 | 327.8086 | 272.7232 | 268.2737
1500.0823 | 327.8076 | 272.7422 | 268.2574
1501.0823 | 327.8733 | 272.7468 | 268.2473
1502.0823 | 327.9686 | 272.7722 | 268.243
1503.0823 | 328.0524 | 272.7835 | 268.2145
1504.0979 | 328.0472 | 272.8074 | 268.2059
1505.0823 | 328.044 | 272.8224 | 268.1909
1506.0823 | 328.0247 | 272.8391 | 268.2055
1507.0823 | 327.977 | 272.8407 | 268.2073
1508.0823 | 327.9505 | 272.8482 | 268.2098
1509.0823 | 328.1061 | 272.8679 | 268.2273
1510.0979 | 328.1452 | 272.8861 | 268.2631
1511.0823 | 328.1955 | 272.9235 | 268.2738
1512.0823 | 328.1234 | 272.9322 | 268.2623
1513.0823 | 328.1186 | 272.9214 | 268.2694
1514.0823 | 328.0566 | 272.9271 | 268.2725
1515.0823 | 328.0192 | 272.905 | 268.2515
1516.0823 | 327.9491 | 272.8813 | 268.2461
1517.0823 | 327.9647 | 272.8662 | 268.2496
1518.0823 | 328.0016 | 272.8548 | 268.2659
1519.0823 | 328.0135 | 272.8485 | 268.3001
1520.0823 | 328.0596 | 272.8446 | 268.3227
1521.0823 | 327.9862 | 272.8463 | 268.3312
1522.0823 | 327.8587 | 272.8559 | 268.3299
1523.0823 | 327.8924 | 272.8395 | 268.3121
1524.0979 | 327.8822 | 272.8235 | 268.3009
1525.0823 | 327.922 | 272.788 | 268.2816
1526.0823 | 327.9153 | 272.7729 | 268.2738
1527.0823 | 327.9536 | 272.7504 | 268.2802
1528.0823 | 327.905 | 272.7229 | 268.2869
1529.0823 | 327.8964 | 272.703 | 268.2765
1530.0823 | 327.9367 | 272.691 | 268.2749
1531.0823 | 327.9104 | 272.6914 | 268.2838
1532.0823 | 327.8715 | 272.7068 | 268.2724
1533.0823 | 327.7913 | 272.7291 | 268.2748
1534.0823 | 327.7754 | 272.7493 | 268.2617
1535.0823 | 327.8124 | 272.7807 | 268.2724
1536.0823 | 327.8583 | 272.8055 | 268.2891
1537.0823 | 327.8575 | 272.8353 | 268.2988
1538.0823 | 327.7636 | 272.8514 | 268.2851
1539.0823 | 327.7958 | 272.8881 | 268.2986
1540.0823 | 327.7859 | 272.9067 | 268.2731
1541.0823 | 327.6792 | 272.9217 | 268.2783
1542.0823 | 327.5687 | 272.9292 | 268.2572
1543.0823 | 327.5435 | 272.9382 | 268.2599
1544.0823 | 327.5472 | 272.9168 | 268.278
1545.0823 | 327.5053 | 272.9036 | 268.299
1546.0823 | 327.4325 | 272.9052 | 268.3202
1547.0823 | 327.3845 | 272.9018 | 268.3519
1548.0823 | 327.4304 | 272.925 | 268.3656
1549.0823 | 327.3984 | 272.9435 | 268.3706
1550.0823 | 327.377 | 272.9533 | 268.393
1551.0823 | 327.3646 | 272.951 | 268.4189
1552.0823 | 327.3148 | 272.9368 | 268.4253
1553.0823 | 327.3455 | 272.9342 | 268.4398
1554.0823 | 327.3615 | 272.9155 | 268.4415
1555.0823 | 327.4237 | 272.9037 | 268.4485
1556.0823 | 327.4365 | 272.8905 | 268.4658
1557.0823 | 327.4169 | 272.9024 | 268.4754
1558.0823 | 327.5144 | 272.899 | 268.4962
1559.0823 | 327.5945 | 272.9055 | 268.5248
1560.0823 | 327.7247 | 272.9043 | 268.5592
1561.0823 | 327.7835 | 272.8968 | 268.5987
1562.0823 | 327.9642 | 272.8966 | 268.632
1563.0823 | 328.1015 | 272.9165 | 268.678
1564.0823 | 328.1883 | 272.9435 | 268.6701
1565.0823 | 328.1463 | 272.943 | 268.676
1566.0823 | 328.219 | 272.9726 | 268.6798
1567.0823 | 328.2493 | 272.9806 | 268.6929
1568.0823 | 328.2126 | 273.0007 | 268.697
1569.0823 | 328.2151 | 273.0118 | 268.6809
1570.0979 | 328.2267 | 273.0451 | 268.6989
1571.0823 | 328.2423 | 273.0675 | 268.7124
1572.0823 | 328.2974 | 273.0899 | 268.7293
1573.0823 | 328.3112 | 273.1253 | 268.7728
1574.0823 | 328.274 | 273.1445 | 268.7912
1575.0823 | 328.2641 | 273.1794 | 268.8346
1576.0823 | 328.2113 | 273.1665 | 268.8599
1577.0823 | 328.1265 | 273.1368 | 268.8722
1578.0823 | 328.1078 | 273.1087 | 268.8741
1579.0823 | 328.0291 | 273.0677 | 268.8854
1580.0823 | 327.9788 | 273.0495 | 268.9113
1581.0823 | 328.0134 | 273.0348 | 268.9164
1582.0823 | 327.9833 | 273.0363 | 268.9272
1583.0823 | 327.9676 | 273.0352 | 268.9228
1584.0823 | 327.927 | 273.0447 | 268.907
1585.0823 | 327.9638 | 273.049 | 268.8975
1586.0823 | 327.9407 | 273.0607 | 268.8721
1587.0823 | 327.9378 | 273.0839 | 268.8227
1588.0823 | 327.9184 | 273.0997 | 268.8222
1589.0823 | 327.9072 | 273.1314 | 268.8342
1590.0823 | 327.8572 | 273.1334 | 268.8304
1591.0823 | 327.8429 | 273.1428 | 268.8049
1592.0823 | 327.7642 | 273.1345 | 268.7803
1593.0823 | 327.6681 | 273.1237 | 268.7783
1594.0823 | 327.5412 | 273.1242 | 268.7795
1595.0823 | 327.4662 | 273.1231 | 268.7914
1596.0823 | 327.4159 | 273.1256 | 268.8107
1597.0823 | 327.5107 | 273.1701 | 268.8395
1598.0823 | 327.5498 | 273.1764 | 268.8197
1599.0823 | 327.5656 | 273.1827 | 268.7367
1600.0823 | 327.6287 | 273.1908 | 268.6075
1601.0823 | 327.6066 | 273.2031 | 268.5367
1602.0979 | 327.6292 | 273.2193 | 268.5059
1603.0979 | 327.626 | 273.2335 | 268.5081
1604.0823 | 327.5961 | 273.2483 | 268.4994
1605.0823 | 327.6074 | 273.282 | 268.5206
1606.0823 | 327.6285 | 273.2925 | 268.5442
1607.0823 | 327.5969 | 273.3007 | 268.5854
1608.0823 | 327.5897 | 273.3106 | 268.6172
1609.0979 | 327.619 | 273.3262 | 268.6045
1610.0823 | 327.6151 | 273.3155 | 268.5662
1611.0823 | 327.5708 | 273.2979 | 268.5465
1612.0823 | 327.5412 | 273.2787 | 268.5192
1613.0823 | 327.5723 | 273.2812 | 268.5073
1614.0979 | 327.6065 | 273.2865 | 268.49
1615.0823 | 327.6376 | 273.2756 | 268.5132
1616.0823 | 327.627 | 273.2772 | 268.5244
1617.0823 | 327.623 | 273.2767 | 268.5321
1618.0823 | 327.6751 | 273.263 | 268.5281
1619.0823 | 327.6887 | 273.2766 | 268.5371
1620.0823 | 327.7015 | 273.282 | 268.5746
1621.0823 | 327.7434 | 273.2697 | 268.6272
1622.0823 | 327.7433 | 273.26 | 268.6457
1623.0979 | 327.7138 | 273.2672 | 268.6547
1624.0823 | 327.8285 | 273.2565 | 268.6603
1625.0823 | 327.8433 | 273.2683 | 268.6337
1626.0823 | 327.96 | 273.2669 | 268.6337
1627.0979 | 328.0273 | 273.2799 | 268.626
1628.0823 | 327.9686 | 273.2822 | 268.6399
1629.0979 | 327.9874 | 273.302 | 268.6705
1630.0979 | 327.9797 | 273.2942 | 268.7137
1631.0823 | 327.9285 | 273.2808 | 268.7068
1632.0979 | 327.9356 | 273.2618 | 268.6912
1633.0979 | 327.947 | 273.239 | 268.7028
1634.0823 | 327.9802 | 273.1959 | 268.7437
1635.0823 | 328.0374 | 273.1496 | 268.7821
1636.0823 | 328.0385 | 273.112 | 268.8262
1637.0823 | 328.0398 | 273.0803 | 268.8535
1638.0823 | 328.0788 | 273.0375 | 268.862
1639.0823 | 328.1317 | 272.9842 | 268.8685
1640.0823 | 328.1537 | 272.9614 | 268.8738
1641.0823 | 328.1293 | 272.9408 | 268.8937
1642.0979 | 328.0861 | 272.9202 | 268.913
1643.0823 | 328.1332 | 272.8868 | 268.9466
1644.0979 | 328.1017 | 272.8928 | 268.9709
1645.0823 | 328.1139 | 272.8922 | 268.9657
1646.0823 | 328.0933 | 272.9184 | 268.9673
1647.0979 | 328.0531 | 272.9378 | 268.9858
1648.0823 | 328.0526 | 272.9877 | 268.9978
1649.0823 | 328.0926 | 272.9962 | 269.0112
1650.2385 | 328.1077 | 273.0195 | 269.0283
1651.0823 | 328.1122 | 273.0292 | 269.032
1652.0823 | 328.1657 | 273.0468 | 269.045
1653.0823 | 328.2147 | 273.0801 | 269.0606
1654.1604 | 328.2171 | 273.1178 | 269.0682
1655.0823 | 328.1856 | 273.1296 | 269.0691
1656.1292 | 328.2499 | 273.1595 | 269.0666
1657.0979 | 328.2953 | 273.1395 | 269.0045
1658.1917 | 328.3283 | 273.1288 | 268.9465
1659.0823 | 328.2693 | 273.1261 | 268.9232
1660.0823 | 328.2552 | 273.1094 | 268.9108
1661.0823 | 328.2079 | 273.0788 | 268.9192
1662.0823 | 328.1904 | 273.0434 | 268.958
1663.0823 | 328.2222 | 273.0462 | 268.9557
1664.0823 | 328.2168 | 273.0474 | 268.892
1665.0823 | 328.2199 | 273.0614 | 268.876
1666.0823 | 328.2104 | 273.0824 | 268.8608
1667.0823 | 328.2151 | 273.0682 | 268.8623
1668.0823 | 328.199 | 273.0702 | 268.8544
1669.0823 | 328.2633 | 273.0803 | 268.8626
1670.0823 | 328.1966 | 273.0526 | 268.8546
1671.0823 | 328.1144 | 273.0419 | 268.8425
1672.0979 | 328.0942 | 273.0287 | 268.8367
1673.0823 | 328.0851 | 272.9845 | 268.8116
1674.0823 | 328.0851 | 272.9581 | 268.8207
1675.0823 | 328.0891 | 272.9522 | 268.8471
1676.0823 | 328.0656 | 272.9345 | 268.8601
1677.0823 | 328.141 | 272.9686 | 268.8663
1678.0823 | 328.0571 | 272.9753 | 268.848
1679.0823 | 328.0308 | 272.9993 | 268.8599
1680.0823 | 328.0211 | 273.0079 | 268.8899
1681.0823 | 328.0536 | 273.0222 | 268.9084
1682.0823 | 328.1133 | 273.0127 | 268.9156
1683.0823 | 328.1054 | 272.9997 | 268.9436
1684.0823 | 328.111 | 273.0121 | 268.9834
1685.0823 | 328.086 | 273.0287 | 269.0173
1686.0823 | 327.996 | 273.04 | 269.0398
1687.0823 | 327.9944 | 273.0533 | 269.0534
1688.0823 | 328.0168 | 273.0435 | 269.0784
1689.0823 | 328.0142 | 273.048 | 269.0964
1690.0823 | 328.0098 | 273.0353 | 269.1007
1691.0823 | 328.052 | 273.0336 | 269.119
1692.0823 | 328.1052 | 273.0187 | 269.1392
1693.0823 | 328.1833 | 273.0117 | 269.1645
1694.0823 | 328.187 | 272.9901 | 269.1868
1695.0823 | 328.2282 | 272.9571 | 269.176
1696.0823 | 328.2822 | 272.9373 | 269.1463
1697.0823 | 328.3025 | 272.9321 | 269.1255
1698.0823 | 328.287 | 272.9112 | 269.1172
1699.0823 | 328.3277 | 272.8998 | 269.1209
1700.0823 | 328.3708 | 272.8949 | 269.1097
1701.0823 | 328.4484 | 272.907 | 269.122
1702.0823 | 328.4293 | 272.9267 | 269.1502
1703.0823 | 328.3793 | 272.9382 | 269.1472
1704.0823 | 328.4103 | 272.9658 | 269.1846
1705.0823 | 328.4083 | 272.9978 | 269.2043
1706.0823 | 328.4641 | 273.0556 | 269.219
1707.0823 | 328.4273 | 273.0771 | 269.2456
1708.0823 | 328.5288 | 273.1108 | 269.2819
1709.0823 | 328.6151 | 273.1526 | 269.2996
1710.0823 | 328.6494 | 273.1831 | 269.2778
1711.0823 | 328.6879 | 273.1958 | 269.2233
1712.0823 | 328.7132 | 273.2073 | 269.172
1713.0823 | 328.6461 | 273.2002 | 269.1323
1714.0823 | 328.5636 | 273.215 | 269.0523
1715.0823 | 328.5924 | 273.2545 | 269.0052
1716.0823 | 328.6199 | 273.2499 | 268.9736
1717.0823 | 328.6071 | 273.2533 | 268.9482
1718.0823 | 328.6036 | 273.2491 | 268.8869
1719.0823 | 328.7011 | 273.1899 | 268.765
1720.0823 | 328.7468 | 273.1443 | 268.725
1721.0823 | 328.7253 | 273.1376 | 268.7415
1722.0823 | 328.6398 | 273.1385 | 268.7431
1723.0823 | 328.5753 | 273.1493 | 268.7458
1724.0823 | 328.5774 | 273.1623 | 268.7423
1725.0823 | 328.5124 | 273.1557 | 268.7636
1726.0823 | 328.4275 | 273.1753 | 268.774
1727.0823 | 328.36 | 273.1858 | 268.7931
1728.0823 | 328.3026 | 273.1875 | 268.8131
1729.0823 | 328.3896 | 273.163 | 268.8505
1730.0823 | 328.2509 | 273.1401 | 268.8594
1731.0823 | 328.1715 | 273.1384 | 268.8898
1732.0823 | 328.1281 | 273.1611 | 268.944
1733.0823 | 328.1139 | 273.1688 | 268.9836
1734.0823 | 328.0657 | 273.1947 | 269.0102
1735.0823 | 328.0091 | 273.1882 | 269.0028
1736.0823 | 328.0055 | 273.2099 | 268.9911
1737.0823 | 328.0173 | 273.2327 | 268.9868
1738.0823 | 328.1256 | 273.2432 | 268.9765
1739.0823 | 328.1913 | 273.2362 | 268.9643
1740.0823 | 328.1507 | 273.2271 | 268.9708
1741.0823 | 328.2139 | 273.2436 | 268.972
1742.0823 | 328.2487 | 273.2654 | 269.0033
1743.0823 | 328.269 | 273.2852 | 269.0094
1744.0823 | 328.2455 | 273.3085 | 268.9875
1745.0823 | 328.2841 | 273.3167 | 268.9964
1746.0823 | 328.2846 | 273.312 | 268.9891
1747.0823 | 328.2734 | 273.3036 | 268.9797
1748.0823 | 328.3001 | 273.3053 | 268.9926
1749.0823 | 328.2722 | 273.316 | 269.0212
1750.0823 | 328.2909 | 273.3278 | 269.0512
1751.0823 | 328.2999 | 273.3365 | 269.0809
1752.0979 | 328.3196 | 273.3515 | 269.1015
1753.0823 | 328.383 | 273.3645 | 269.118
1754.0823 | 328.4004 | 273.3878 | 269.1232
1755.0823 | 328.4391 | 273.3981 | 269.1114
1756.0823 | 328.488 | 273.426 | 269.1151
1757.0823 | 328.4235 | 273.4418 | 269.1272
1758.0823 | 328.3343 | 273.4613 | 269.1617
1759.0823 | 328.3067 | 273.4985 | 269.1904
1760.0823 | 328.3311 | 273.5039 | 269.2241
1761.0823 | 328.3847 | 273.5056 | 269.2493
1762.0823 | 328.3785 | 273.5045 | 269.2278
1763.0823 | 328.3204 | 273.5089 | 269.2029
1764.0823 | 328.3189 | 273.5035 | 269.1781
1765.0823 | 328.2936 | 273.4949 | 269.1825
1766.0823 | 328.2481 | 273.4974 | 269.1908
1767.0979 | 328.1653 | 273.4896 | 269.1875
1768.0823 | 328.2026 | 273.4826 | 269.201
1769.0823 | 328.1834 | 273.4746 | 269.1916
1770.0823 | 328.0999 | 273.4894 | 269.1849
1771.0823 | 328.0983 | 273.5077 | 269.2124
1772.0823 | 328.1031 | 273.4877 | 269.2103
1773.0823 | 328.1104 | 273.4731 | 269.2119
1774.0823 | 328.1771 | 273.4642 | 269.24
1775.0823 | 328.2472 | 273.4804 | 269.2806
1776.0823 | 328.2608 | 273.4876 | 269.2734
1777.0823 | 328.1463 | 273.4853 | 269.2453
1778.0823 | 328.1156 | 273.4842 | 269.2212
1779.0823 | 328.0446 | 273.4915 | 269.2143
1780.0823 | 327.9834 | 273.4948 | 269.2485
1781.0823 | 327.9307 | 273.5109 | 269.2565
1782.0823 | 327.9193 | 273.4803 | 269.2242
1783.0823 | 327.8677 | 273.4443 | 269.173
1784.0823 | 327.8684 | 273.4112 | 269.162
1785.0823 | 327.8068 | 273.3977 | 269.1704
1786.0823 | 327.7547 | 273.3925 | 269.1663
1787.0823 | 327.7352 | 273.3757 | 269.135
1788.0823 | 327.8088 | 273.381 | 269.1154
1789.0823 | 327.7083 | 273.3647 | 269.0884
1790.0823 | 327.6065 | 273.3572 | 269.0739
1791.0823 | 327.6192 | 273.3339 | 269.0817
1792.0979 | 327.5326 | 273.3069 | 269.0901
1793.0823 | 327.581 | 273.2856 | 269.105
1794.0823 | 327.5248 | 273.2726 | 269.1292
1795.0823 | 327.497 | 273.2429 | 269.1537
1796.0823 | 327.5122 | 273.225 | 269.16
1797.0979 | 327.4877 | 273.225 | 269.1543
1798.0823 | 327.4539 | 273.2058 | 269.1367
1799.0823 | 327.4964 | 273.2179 | 269.1015
1800.0823 | 327.4882 | 273.2098 | 269.0774
1801.0823 | 327.4946 | 273.2171 | 269.0706
1802.0823 | 327.5002 | 273.2418 | 269.0942
1803.0823 | 327.501 | 273.2526 | 269.0584
1804.0823 | 327.5288 | 273.27 | 269.0085
1805.0823 | 327.5571 | 273.2803 | 268.9601
1806.0823 | 327.6219 | 273.2945 | 268.9399
1807.0979 | 327.5738 | 273.327 | 268.938
1808.0823 | 327.5296 | 273.3379 | 268.951
1809.0823 | 327.474 | 273.3692 | 268.9721
1810.0823 | 327.4784 | 273.3806 | 268.9813
1811.0823 | 327.4404 | 273.3942 | 268.9912
1812.0979 | 327.5213 | 273.3984 | 269.0026
1813.0823 | 327.4848 | 273.41 | 269.021
1814.0823 | 327.447 | 273.4176 | 269.027
1815.0823 | 327.321 | 273.39 | 269.0349
1816.0823 | 327.3435 | 273.3615 | 269.0101
1817.0823 | 327.3557 | 273.3487 | 269.0009
1818.0823 | 327.467 | 273.3502 | 269.0285
1819.0823 | 327.4855 | 273.3459 | 269.0489
1820.0823 | 327.5592 | 273.3306 | 269.088
1821.0823 | 327.6059 | 273.336 | 269.1141
1822.0979 | 327.6143 | 273.3439 | 269.1141
1823.0823 | 327.574 | 273.3398 | 269.1146
1824.0979 | 327.636 | 273.3398 | 269.1177
1825.0823 | 327.6538 | 273.338 | 269.1231
1826.0823 | 327.7782 | 273.3544 | 269.1353
1827.0979 | 327.8599 | 273.3833 | 269.1615
1828.0823 | 327.853 | 273.4176 | 269.1945
1829.0823 | 327.8203 | 273.4402 | 269.2319
1830.0823 | 327.793 | 273.471 | 269.2368
1831.0979 | 327.8028 | 273.4982 | 269.2827
1832.0823 | 327.8451 | 273.5232 | 269.3126
1833.0823 | 327.8563 | 273.5423 | 269.3219
1834.0823 | 327.8812 | 273.5318 | 269.2847
1835.0823 | 327.8928 | 273.5422 | 269.2532
1836.0823 | 327.9295 | 273.5411 | 269.2405
1837.0979 | 327.9009 | 273.532 | 269.2481
1838.0823 | 327.8854 | 273.522 | 269.2553
1839.0823 | 327.9146 | 273.5474 | 269.263
1840.0823 | 327.9171 | 273.5696 | 269.2609
1841.0823 | 327.9266 | 273.5807 | 269.2538
1842.0823 | 327.8804 | 273.5803 | 269.2497
1843.0823 | 327.8991 | 273.5839 | 269.258
1844.0823 | 327.8748 | 273.5899 | 269.2531
1845.0823 | 327.7856 | 273.588 | 269.246
1846.0823 | 327.826 | 273.5633 | 269.2592
1847.0823 | 327.84 | 273.567 | 269.2353
1848.0823 | 327.7936 | 273.5415 | 269.1943
1849.0823 | 327.7124 | 273.5284 | 269.1698
1850.0823 | 327.7173 | 273.4894 | 269.1687
1851.0823 | 327.8152 | 273.4844 | 269.1862
1852.0823 | 327.8413 | 273.4886 | 269.1955
1853.0823 | 327.8985 | 273.4764 | 269.2006
1854.0823 | 327.9779 | 273.4863 | 269.1558
1855.0823 | 328.0357 | 273.4787 | 269.0837
1856.0823 | 327.9685 | 273.48 | 269.0553
1857.0823 | 327.9041 | 273.4707 | 269.0338
1858.0823 | 327.8769 | 273.484 | 269.0176
1859.0823 | 327.7979 | 273.4851 | 269.041
1860.0823 | 327.8414 | 273.5083 | 269.0469
1861.0823 | 327.8437 | 273.519 | 269.0574
1862.0823 | 327.83 | 273.494 | 269.0779
1863.0823 | 327.8372 | 273.4969 | 269.0898
1864.0823 | 327.8865 | 273.4769 | 269.094
1865.0823 | 327.9031 | 273.4686 | 269.1096
1866.0823 | 327.9542 | 273.4732 | 269.0887
1867.0823 | 328.0169 | 273.4671 | 269.0674
1868.0823 | 327.9982 | 273.4642 | 269.0783
1869.0823 | 327.9927 | 273.4601 | 269.0899
1870.0823 | 327.9824 | 273.4707 | 269.0026
1871.0823 | 327.9957 | 273.4722 | 268.9662
1872.0823 | 327.9996 | 273.4401 | 268.9627
1873.0823 | 327.9844 | 273.416 | 268.9965
1874.0823 | 328.0451 | 273.3703 | 269.0407
1875.0823 | 328.136 | 273.3367 | 269.0817
1876.0823 | 328.0423 | 273.3268 | 269.1197
1877.0979 | 328.013 | 273.2985 | 269.1359
1878.0823 | 328.0294 | 273.2815 | 269.1665
1879.0823 | 328.1172 | 273.238 | 269.2037
1880.0823 | 328.0836 | 273.2091 | 269.2415
1881.0823 | 328.108 | 273.1997 | 269.2772
1882.0823 | 328.1325 | 273.2084 | 269.2845
1883.0823 | 328.1312 | 273.2198 | 269.2804
1884.0823 | 328.0957 | 273.2227 | 269.2975
1885.0823 | 328.1445 | 273.2358 | 269.3258
1886.0823 | 328.1062 | 273.2502 | 269.3492
1887.0823 | 328.0694 | 273.2812 | 269.3507
1888.0823 | 328.1573 | 273.3 | 269.3693
1889.0823 | 328.1759 | 273.3064 | 269.3864
1890.0823 | 328.2337 | 273.3208 | 269.3836
1891.0823 | 328.3394 | 273.3192 | 269.3594
1892.0823 | 328.4111 | 273.3359 | 269.3418
1893.0823 | 328.3041 | 273.33 | 269.3347
1894.0823 | 328.1917 | 273.3141 | 269.326
1895.0823 | 328.2305 | 273.2847 | 269.2856
1896.0823 | 328.2539 | 273.2903 | 269.2674
1897.0823 | 328.2003 | 273.2903 | 269.2628
1898.0823 | 328.1808 | 273.3176 | 269.2441
1899.0823 | 328.1624 | 273.3316 | 269.2428
1900.0823 | 328.1865 | 273.3598 | 269.2443
1901.0823 | 328.2007 | 273.3632 | 269.247
1902.0823 | 328.2242 | 273.3654 | 269.261
1903.0823 | 328.343 | 273.3517 | 269.2641
1904.0823 | 328.3882 | 273.3559 | 269.2553
1905.0823 | 328.431 | 273.3601 | 269.2683
1906.0823 | 328.4492 | 273.3668 | 269.2587
1907.0823 | 328.3963 | 273.3644 | 269.2467
1908.0823 | 328.3927 | 273.3574 | 269.2269
1909.0823 | 328.4323 | 273.3433 | 269.2179
1910.0823 | 328.4108 | 273.3633 | 269.2238
1911.0823 | 328.3694 | 273.3676 | 269.2556
1912.0823 | 328.3448 | 273.3891 | 269.2709
1913.0823 | 328.3421 | 273.4104 | 269.2866
1914.0823 | 328.2737 | 273.4489 | 269.3224
1915.0823 | 328.3165 | 273.4771 | 269.3448
1916.0823 | 328.2551 | 273.5053 | 269.333
1917.0979 | 328.2379 | 273.5219 | 269.3473
1918.0823 | 328.3168 | 273.5434 | 269.356
1919.0823 | 328.3314 | 273.5463 | 269.3765
1920.0823 | 328.273 | 273.5485 | 269.3835
1921.0823 | 328.271 | 273.5765 | 269.3581
1922.0823 | 328.3835 | 273.5977 | 269.2965
1923.0823 | 328.3304 | 273.6057 | 269.2084
1924.0823 | 328.3056 | 273.6018 | 269.1706
1925.0823 | 328.2224 | 273.6119 | 269.1755
1926.0823 | 328.1145 | 273.5958 | 269.1866
1927.0823 | 328.1644 | 273.5784 | 269.2159
1928.0823 | 328.2128 | 273.5875 | 269.2095
1929.0823 | 328.1595 | 273.59 | 269.2534
1930.0823 | 328.0874 | 273.6139 | 269.3015
1931.0823 | 328.0803 | 273.6286 | 269.3477
1932.0979 | 328.0212 | 273.6509 | 269.3596
1933.0823 | 327.9908 | 273.6644 | 269.3847
1934.0823 | 328.0702 | 273.677 | 269.4088
1935.0823 | 328.0569 | 273.6536 | 269.4432
1936.0823 | 328.0785 | 273.6582 | 269.4469
1937.0823 | 328.1865 | 273.6457 | 269.4444
1938.0823 | 328.1373 | 273.6451 | 269.4482
1939.0823 | 328.026 | 273.6507 | 269.4443
1940.0823 | 327.8826 | 273.6385 | 269.3853
1941.0823 | 327.9406 | 273.644 | 269.3168
1942.0823 | 327.9208 | 273.6507 | 269.3103
1943.0823 | 327.9057 | 273.6623 | 269.3212
1944.0823 | 327.8627 | 273.6675 | 269.319
1945.0823 | 327.8693 | 273.6719 | 269.3099
1946.0823 | 327.9041 | 273.6583 | 269.312
1947.0823 | 327.9134 | 273.653 | 269.3205
1948.0823 | 327.9943 | 273.6458 | 269.3324
1949.0823 | 327.9948 | 273.625 | 269.3418
1950.0823 | 327.9953 | 273.5934 | 269.3584
1951.0823 | 327.8891 | 273.5679 | 269.3778
1952.0823 | 327.8034 | 273.5432 | 269.3858
1953.0823 | 327.7927 | 273.5228 | 269.3831
1954.0979 | 327.9019 | 273.502 | 269.3833
1955.0823 | 327.9338 | 273.5003 | 269.3815
1956.0823 | 328.0573 | 273.5152 | 269.3958
1957.0979 | 328.0892 | 273.5145 | 269.429
1958.0979 | 328.1348 | 273.5103 | 269.4276
1959.0823 | 328.1682 | 273.5149 | 269.422
1960.0823 | 328.1155 | 273.5305 | 269.392
1961.0823 | 328.0925 | 273.5476 | 269.378
1962.0979 | 328.0858 | 273.5301 | 269.3758
1963.0823 | 328.0811 | 273.4843 | 269.3703
1964.0979 | 328.1116 | 273.4371 | 269.3428
1965.0823 | 328.1582 | 273.4216 | 269.3041
1966.0823 | 328.2243 | 273.3921 | 269.2639
1967.0823 | 328.2257 | 273.3889 | 269.2646
1968.0823 | 328.2291 | 273.3961 | 269.3006
1969.0823 | 328.1996 | 273.403 | 269.292
1970.0823 | 328.2132 | 273.3833 | 269.2541
1971.0823 | 328.3599 | 273.3505 | 269.2619
1972.0979 | 328.4227 | 273.3171 | 269.2994
1973.0823 | 328.5251 | 273.3026 | 269.3091
1974.0823 | 328.5534 | 273.3239 | 269.3299
1975.0823 | 328.5212 | 273.3487 | 269.3558
1976.0823 | 328.5183 | 273.3546 | 269.3605
1977.0979 | 328.5831 | 273.3774 | 269.3315
1978.0823 | 328.5764 | 273.3917 | 269.3281
1979.0823 | 328.5141 | 273.3808 | 269.3132
1980.0979 | 328.552 | 273.402 | 269.3114
1981.0823 | 328.5936 | 273.4122 | 269.3025
1982.0823 | 328.5526 | 273.4276 | 269.3097
1983.0823 | 328.4769 | 273.4386 | 269.3349
1984.0823 | 328.4688 | 273.461 | 269.348
1985.0823 | 328.4895 | 273.4849 | 269.3628
1986.0823 | 328.4314 | 273.4911 | 269.3817
1987.0979 | 328.477 | 273.4726 | 269.4064
1988.0823 | 328.4694 | 273.4448 | 269.3957
1989.0823 | 328.4416 | 273.4043 | 269.38
1990.0823 | 328.4096 | 273.3709 | 269.3943
1991.0823 | 328.3879 | 273.3614 | 269.3598
1992.0823 | 328.4358 | 273.3343 | 269.3321
1993.0823 | 328.5289 | 273.3201 | 269.2996
1994.0823 | 328.5918 | 273.3138 | 269.2671
1995.0823 | 328.6769 | 273.3101 | 269.2764
1996.0823 | 328.6616 | 273.2903 | 269.3012
1997.0823 | 328.5869 | 273.3005 | 269.3077
1998.0823 | 328.6276 | 273.3021 | 269.2916
1999.0823 | 328.576 | 273.3053 | 269.2858
2000.0823 | 328.6122 | 273.2961 | 269.2847
2001.0823 | 328.5818 | 273.3023 | 269.2941
2002.0823 | 328.5708 | 273.2795 | 269.3206
2003.0823 | 328.5055 | 273.2802 | 269.3441
2004.0823 | 328.4005 | 273.2888 | 269.3777
2005.0823 | 328.376 | 273.2756 | 269.4247
2006.0823 | 328.2853 | 273.3043 | 269.4637
2007.0823 | 328.2184 | 273.3148 | 269.4637
2008.0823 | 328.1604 | 273.3095 | 269.4865
2009.0823 | 328.2154 | 273.33 | 269.5341
2010.0823 | 328.1697 | 273.3545 | 269.5704
2011.0823 | 328.0683 | 273.3879 | 269.6032
2012.0823 | 328.0743 | 273.3988 | 269.6216
2013.0823 | 328.1433 | 273.4109 | 269.6304
2014.0823 | 328.1055 | 273.4131 | 269.655
2015.0823 | 328.106 | 273.4282 | 269.6462
2016.0823 | 328.1293 | 273.4319 | 269.6501
2017.0823 | 328.2166 | 273.4588 | 269.6584
2018.0823 | 328.1905 | 273.4636 | 269.6867
2019.0823 | 328.1715 | 273.4384 | 269.6943
2020.0823 | 328.312 | 273.4324 | 269.7046
2021.0823 | 328.3435 | 273.4473 | 269.6927
2022.0823 | 328.2865 | 273.4589 | 269.6739
2023.0823 | 328.3214 | 273.4545 | 269.6751
2024.0823 | 328.335 | 273.4624 | 269.6555
2025.0823 | 328.3604 | 273.4527 | 269.6405
2026.0823 | 328.2922 | 273.4632 | 269.6474
2027.0823 | 328.2399 | 273.4694 | 269.6691
2028.0823 | 328.2982 | 273.4871 | 269.6877
2029.0823 | 328.317 | 273.4926 | 269.7174
2030.0823 | 328.3118 | 273.5175 | 269.6956
2031.0823 | 328.2529 | 273.5269 | 269.6434
2032.0823 | 328.3424 | 273.5705 | 269.6543
2033.0823 | 328.385 | 273.5861 | 269.6678
2034.0823 | 328.4241 | 273.6059 | 269.6662
2035.0823 | 328.4492 | 273.5992 | 269.687
2036.0823 | 328.409 | 273.6045 | 269.7108
2037.0823 | 328.3281 | 273.6084 | 269.7441
2038.0823 | 328.3759 | 273.6457 | 269.7535
2039.0823 | 328.3899 | 273.658 | 269.7342
2040.0823 | 328.3496 | 273.7123 | 269.7162
2041.0823 | 328.3142 | 273.747 | 269.7045
2042.0823 | 328.3261 | 273.7575 | 269.7101
2043.0823 | 328.4152 | 273.7746 | 269.7157
2044.0823 | 328.4342 | 273.7963 | 269.7241
2045.0823 | 328.3885 | 273.8204 | 269.7522
2046.0823 | 328.438 | 273.828 | 269.7443
2047.0823 | 328.4607 | 273.8184 | 269.7556
2048.0823 | 328.4955 | 273.7954 | 269.7755
2049.0823 | 328.4636 | 273.7946 | 269.7975
2050.0823 | 328.5142 | 273.7936 | 269.8084
2051.0823 | 328.4932 | 273.7848 | 269.8182
2052.0823 | 328.4921 | 273.7913 | 269.7733
2053.0823 | 328.4073 | 273.7863 | 269.7334
2054.0823 | 328.248 | 273.7944 | 269.7022
2055.0823 | 328.1367 | 273.7943 | 269.7025
2056.0823 | 328.2012 | 273.7937 | 269.7081
2057.0823 | 328.1877 | 273.8 | 269.7141
2058.0823 | 328.2218 | 273.7989 | 269.6879
2059.0823 | 328.3028 | 273.7871 | 269.7058
2060.0979 | 328.4038 | 273.7587 | 269.7211
2061.0823 | 328.488 | 273.6986 | 269.7195
2062.0823 | 328.4384 | 273.6752 | 269.744
2063.0823 | 328.3807 | 273.6699 | 269.7592
2064.0823 | 328.3907 | 273.674 | 269.7777
2065.0823 | 328.3984 | 273.6863 | 269.7884
2066.0823 | 328.4653 | 273.6937 | 269.7911
2067.0823 | 328.5341 | 273.709 | 269.7869
2068.0823 | 328.526 | 273.7166 | 269.7982
2069.0823 | 328.553 | 273.7346 | 269.8119
2070.0823 | 328.5443 | 273.7342 | 269.8147
2071.0823 | 328.6231 | 273.7149 | 269.8443
2072.0823 | 328.7645 | 273.7319 | 269.8594
2073.0823 | 328.7412 | 273.7439 | 269.8835
2074.0823 | 328.6486 | 273.7616 | 269.9408
2075.0823 | 328.5581 | 273.7895 | 269.9809
2076.0823 | 328.5417 | 273.8022 | 270.0056
2077.0979 | 328.4619 | 273.8047 | 270.0249
2078.0823 | 328.5192 | 273.7799 | 270.03
2079.0823 | 328.5425 | 273.7571 | 270.0168
2080.0823 | 328.6031 | 273.7321 | 270.0059
2081.0979 | 328.5304 | 273.7382 | 270.0087
2082.0979 | 328.4847 | 273.7227 | 269.996
2083.0823 | 328.4714 | 273.7344 | 269.9819
2084.0823 | 328.3903 | 273.7319 | 269.9436
2085.0823 | 328.3765 | 273.7308 | 269.9132
2086.0823 | 328.3932 | 273.7413 | 269.9279
2087.0979 | 328.3392 | 273.7568 | 269.9267
2088.0823 | 328.3035 | 273.775 | 269.9093
2089.0823 | 328.2798 | 273.78 | 269.8066
2090.0823 | 328.3023 | 273.8045 | 269.7365
2091.0823 | 328.3197 | 273.8445 | 269.7324
2092.0823 | 328.2983 | 273.8862 | 269.7274
2093.0823 | 328.2882 | 273.9161 | 269.718
2094.0979 | 328.2985 | 273.918 | 269.7281
2095.0823 | 328.2904 | 273.9393 | 269.7522
2096.0823 | 328.2368 | 273.9613 | 269.7496
2097.0979 | 328.1719 | 273.9633 | 269.7391
2098.0823 | 328.0538 | 273.9554 | 269.7502
2099.0823 | 327.9201 | 273.9237 | 269.7808
2100.0823 | 327.9152 | 273.9084 | 269.8178
2101.0823 | 327.8188 | 273.8897 | 269.8496
2102.0823 | 327.7334 | 273.8484 | 269.8696
2103.0823 | 327.7285 | 273.8364 | 269.8671
2104.0823 | 327.6631 | 273.8196 | 269.8502
2105.0823 | 327.719 | 273.7986 | 269.8355
2106.0823 | 327.7924 | 273.782 | 269.8193
2107.0823 | 327.9228 | 273.7775 | 269.8011
2108.0979 | 328.0127 | 273.7452 | 269.7999
2109.0823 | 328.0329 | 273.7286 | 269.8233
2110.0823 | 327.9851 | 273.7145 | 269.8436
2111.0823 | 327.8888 | 273.7296 | 269.8548
2112.0823 | 327.9199 | 273.7308 | 269.862
2113.0823 | 327.9625 | 273.728 | 269.8834
2114.0823 | 327.9406 | 273.7127 | 269.8771
2115.0823 | 327.9572 | 273.7265 | 269.8661
2116.0823 | 327.9715 | 273.7032 | 269.8718
2117.0823 | 328.0303 | 273.7271 | 269.8907
2118.0823 | 328.0689 | 273.7442 | 269.9175
2119.0823 | 328.0808 | 273.7406 | 269.8933
2120.0823 | 328.035 | 273.7397 | 269.8812
2121.0823 | 328.0014 | 273.7396 | 269.8846
2122.0979 | 328.0059 | 273.7581 | 269.895
2123.0823 | 328.1038 | 273.7598 | 269.8955
2124.0823 | 328.0992 | 273.7701 | 269.9112
2125.0823 | 328.166 | 273.7674 | 269.9271
2126.0823 | 328.1542 | 273.7553 | 269.9322
2127.0979 | 328.1973 | 273.7581 | 269.8892
2128.0823 | 328.2425 | 273.7577 | 269.8752
2129.0823 | 328.159 | 273.7642 | 269.8673
2130.0823 | 328.162 | 273.757 | 269.8611
2131.0823 | 328.2855 | 273.7687 | 269.8388
2132.0823 | 328.3334 | 273.7864 | 269.7972
2133.0823 | 328.4272 | 273.8036 | 269.764
2134.0823 | 328.4957 | 273.8169 | 269.7504
2135.0823 | 328.5397 | 273.8399 | 269.7506
2136.0823 | 328.5529 | 273.8565 | 269.7644
2137.0979 | 328.4952 | 273.8702 | 269.771
2138.0823 | 328.4763 | 273.904 | 269.7834
2139.0823 | 328.374 | 273.9255 | 269.8128
2140.0823 | 328.3139 | 273.922 | 269.8247
2141.0823 | 328.2236 | 273.9136 | 269.8542
2142.0979 | 328.1891 | 273.8822 | 269.8711
2143.0823 | 328.2482 | 273.8381 | 269.9118
2144.0823 | 328.2804 | 273.7983 | 269.9292
2145.0823 | 328.3085 | 273.7461 | 269.9511
2146.0823 | 328.274 | 273.6988 | 269.9326
2147.0823 | 328.3023 | 273.6676 | 269.9285
2148.0823 | 328.4113 | 273.6624 | 269.9049
2149.0823 | 328.4941 | 273.6625 | 269.8955
2150.0823 | 328.4898 | 273.6406 | 269.8989
2151.0823 | 328.5125 | 273.6277 | 269.892
2152.0823 | 328.5355 | 273.5946 | 269.8852
2153.0823 | 328.5829 | 273.595 | 269.8648
2154.0823 | 328.5768 | 273.6026 | 269.8513
2155.0823 | 328.6007 | 273.6131 | 269.8597
2156.0823 | 328.6406 | 273.6318 | 269.8854
2157.0823 | 328.5803 | 273.6402 | 269.8752
2158.0823 | 328.552 | 273.6327 | 269.8647
2159.0823 | 328.5612 | 273.6379 | 269.8758
2160.0823 | 328.6369 | 273.6406 | 269.8847
2161.0823 | 328.7361 | 273.6237 | 269.8908
2162.0823 | 328.7886 | 273.575 | 269.8655
2163.0823 | 328.8244 | 273.5114 | 269.856
2164.0823 | 328.8051 | 273.4703 | 269.8718
2165.0823 | 328.7627 | 273.452 | 269.886
2166.0823 | 328.733 | 273.4413 | 269.8533
2167.0823 | 328.7541 | 273.4287 | 269.8039
2168.0823 | 328.8205 | 273.4346 | 269.7668
2169.0823 | 328.8955 | 273.4362 | 269.753
2170.0823 | 328.8855 | 273.4737 | 269.7306
2171.0823 | 328.8417 | 273.499 | 269.7403
2172.0823 | 328.7898 | 273.5367 | 269.7555
2173.0823 | 328.8167 | 273.5622 | 269.7901
2174.0823 | 328.866 | 273.611 | 269.8243
2175.0823 | 328.7166 | 273.6226 | 269.8429
2176.0823 | 328.6303 | 273.6696 | 269.8582
2177.0823 | 328.5689 | 273.6656 | 269.8726
2178.0823 | 328.6182 | 273.6541 | 269.8815
2179.0823 | 328.6378 | 273.6542 | 269.9023
2180.0823 | 328.6177 | 273.6373 | 269.9114
2181.0823 | 328.6958 | 273.6152 | 269.8953
2182.0823 | 328.7869 | 273.5934 | 269.8642
2183.0823 | 328.7764 | 273.5612 | 269.8461
2184.0823 | 328.7749 | 273.5473 | 269.8441
2185.0823 | 328.7042 | 273.5635 | 269.8542
2186.0823 | 328.7011 | 273.5917 | 269.8283
2187.0823 | 328.6591 | 273.6148 | 269.8268
2188.0823 | 328.614 | 273.6394 | 269.8065
2189.0823 | 328.6194 | 273.6672 | 269.8262
2190.0823 | 328.6079 | 273.6895 | 269.8695
2191.0823 | 328.5315 | 273.7194 | 269.9183
2192.0823 | 328.6062 | 273.7244 | 269.961
2193.0823 | 328.6841 | 273.7223 | 269.9677
2194.0823 | 328.6735 | 273.7396 | 269.9634
2195.0979 | 328.659 | 273.7402 | 269.9826
2196.0823 | 328.631 | 273.7635 | 269.9927
2197.0823 | 328.6554 | 273.768 | 270.0044
2198.0823 | 328.6206 | 273.7564 | 270.0063
2199.0823 | 328.543 | 273.7769 | 270.005
2200.0823 | 328.4409 | 273.7921 | 270.0213
2201.0823 | 328.4592 | 273.8111 | 270.0093
2202.0823 | 328.4392 | 273.8004 | 270.005
2203.0823 | 328.3565 | 273.794 | 269.9875
2204.0823 | 328.2706 | 273.7863 | 269.9544
2205.0823 | 328.3403 | 273.7895 | 269.9452
2206.0823 | 328.4515 | 273.7926 | 269.9416
2207.0823 | 328.4885 | 273.7932 | 269.9673
2208.0823 | 328.4602 | 273.7925 | 269.9659
2209.0823 | 328.4237 | 273.7829 | 269.9381
2210.0823 | 328.4212 | 273.7873 | 269.9216
2211.0823 | 328.4531 | 273.8062 | 269.9029
2212.0823 | 328.4834 | 273.7894 | 269.8959
2213.0823 | 328.4031 | 273.7852 | 269.8731
2214.0823 | 328.3054 | 273.8003 | 269.8656
2215.0823 | 328.2455 | 273.8045 | 269.8561
2216.0823 | 328.0758 | 273.8025 | 269.8654
2217.0823 | 328.0649 | 273.8078 | 269.8785
2218.0823 | 328.0404 | 273.7925 | 269.9015
2219.0823 | 327.9948 | 273.7639 | 269.9217
2220.0823 | 327.9554 | 273.7483 | 269.9265
2221.0823 | 327.9973 | 273.7337 | 269.9407
2222.0823 | 327.9163 | 273.7401 | 269.929
2223.0823 | 328.0104 | 273.7372 | 269.9052
2224.0823 | 327.9655 | 273.739 | 269.9031
2225.0823 | 327.9148 | 273.7476 | 269.9237
2226.0823 | 327.9058 | 273.7734 | 269.9561
2227.0823 | 327.9119 | 273.792 | 269.9883
2228.0823 | 327.9477 | 273.798 | 270.0015
2229.0823 | 327.8547 | 273.8304 | 269.9838
2230.0823 | 327.8232 | 273.8296 | 269.9796
2231.0823 | 327.722 | 273.8488 | 269.9802
2232.0823 | 327.7226 | 273.8472 | 269.9851
2233.0823 | 327.7021 | 273.8204 | 269.9923
2234.0823 | 327.711 | 273.8157 | 270.0026
2235.0823 | 327.7917 | 273.8039 | 270.038
2236.0823 | 327.9025 | 273.8011 | 270.0517
2237.0823 | 327.9393 | 273.8005 | 270.0782
2238.0823 | 327.917 | 273.787 | 270.0771
2239.0823 | 327.8811 | 273.7757 | 270.0775
2240.0823 | 327.8477 | 273.7701 | 270.0945
2241.0823 | 327.8751 | 273.7792 | 270.0964
2242.0823 | 327.8491 | 273.8005 | 270.1246
2243.0823 | 327.8834 | 273.7987 | 270.1459
2244.0823 | 328.0303 | 273.7948 | 270.1624
2245.0823 | 328.2063 | 273.8023 | 270.1813
2246.0823 | 328.2597 | 273.8263 | 270.2012
2247.0823 | 328.2652 | 273.8454 | 270.2113
2248.0823 | 328.2583 | 273.8813 | 270.2316
2249.0823 | 328.2592 | 273.8861 | 270.2418
2250.0823 | 328.3331 | 273.9071 | 270.2466
2251.0823 | 328.3871 | 273.9013 | 270.2284
2252.0823 | 328.4747 | 273.8903 | 270.2076
2253.0823 | 328.5357 | 273.8764 | 270.1835
2254.0823 | 328.4931 | 273.8755 | 270.1435
2255.0823 | 328.4138 | 273.8704 | 270.1277
2256.0823 | 328.4199 | 273.8818 | 270.137
2257.0823 | 328.4967 | 273.9033 | 270.1257
2258.0823 | 328.4678 | 273.8943 | 270.1144
2259.0823 | 328.4021 | 273.8943 | 270.1237
2260.0823 | 328.3425 | 273.9086 | 270.1605
2261.0823 | 328.343 | 273.922 | 270.1945
2262.0979 | 328.4521 | 273.9282 | 270.2203
2263.0979 | 328.4403 | 273.9536 | 270.2389
2264.0823 | 328.3601 | 273.9778 | 270.2427
2265.0823 | 328.33 | 274.004 | 270.2483
2266.0823 | 328.3308 | 274.0302 | 270.2466
2267.0823 | 328.3776 | 274.0734 | 270.2508
2268.0823 | 328.2824 | 274.09 | 270.2725
2269.0823 | 328.2489 | 274.0964 | 270.2912
2270.0823 | 328.1221 | 274.0913 | 270.271
2271.0823 | 328.0814 | 274.0976 | 270.2625
2272.0823 | 328.0258 | 274.0816 | 270.2541
2273.0823 | 327.9595 | 274.0912 | 270.2558
2274.0823 | 327.8999 | 274.0959 | 270.2633
2275.0823 | 327.8615 | 274.0865 | 270.2774
2276.0823 | 327.7276 | 274.0831 | 270.2501
2277.0823 | 327.6915 | 274.0774 | 270.225
2278.0823 | 327.6998 | 274.0853 | 270.221
2279.0823 | 327.7549 | 274.0831 | 270.1917
2280.0823 | 327.7768 | 274.1114 | 270.19
2281.0823 | 327.7823 | 274.1145 | 270.1992
2282.0823 | 327.7933 | 274.1278 | 270.1918
2283.0823 | 327.7193 | 274.1149 | 270.1715
2284.0823 | 327.6815 | 274.1051 | 270.1491
2285.0823 | 327.6662 | 274.0928 | 270.1067
2286.0823 | 327.6131 | 274.0689 | 270.0963
2287.0979 | 327.5351 | 274.0533 | 270.0592
2288.0823 | 327.5514 | 274.0434 | 270.0358
2289.0823 | 327.5222 | 273.9873 | 270.0075
2290.0823 | 327.5005 | 273.9962 | 269.9965
2291.0823 | 327.5235 | 274.0064 | 270.0411
2292.0979 | 327.5214 | 274.015 | 270.0688
2293.0823 | 327.4968 | 274.0341 | 270.0611
2294.0823 | 327.5315 | 274.0536 | 270.0518
2295.0823 | 327.5561 | 274.0239 | 270.0502
2296.0823 | 327.5201 | 274.0053 | 270.0595
2297.0823 | 327.5643 | 273.9862 | 270.069
2298.0823 | 327.5299 | 273.9948 | 270.0751
2299.0823 | 327.5823 | 273.9977 | 270.0933
2300.0823 | 327.4776 | 273.9918 | 270.125
2301.0823 | 327.4824 | 273.9892 | 270.1358
2302.0979 | 327.546 | 273.9868 | 270.1196
2303.0823 | 327.5717 | 273.9937 | 270.1045
2304.0823 | 327.5782 | 273.9775 | 270.0626
2305.0823 | 327.6025 | 273.9374 | 270.024
2306.0823 | 327.5477 | 273.913 | 270.0167
2307.0979 | 327.5801 | 273.8899 | 270.0305
2308.0823 | 327.5978 | 273.8858 | 270.0308
2309.0823 | 327.5657 | 273.8876 | 270.0447
2310.0823 | 327.4571 | 273.8892 | 270.0716
2311.0823 | 327.4252 | 273.858 | 270.0899
2312.0823 | 327.5176 | 273.8388 | 270.094
2313.0823 | 327.5215 | 273.8378 | 270.069
2314.0823 | 327.4874 | 273.807 | 270.012
2315.0823 | 327.6073 | 273.8049 | 269.9853
2316.0823 | 327.6024 | 273.7899 | 269.9707
2317.0823 | 327.4092 | 273.766 | 269.9761
2318.0823 | 327.404 | 273.7515 | 269.9523
2319.0823 | 327.3834 | 273.7131 | 269.9418
2320.0823 | 327.34 | 273.7019 | 269.9326
2321.0823 | 327.4383 | 273.6711 | 269.9206
2322.0823 | 327.4631 | 273.6573 | 269.9147
2323.0823 | 327.3781 | 273.6417 | 269.9251
2324.0823 | 327.3278 | 273.6332 | 269.936
2325.0823 | 327.3491 | 273.6382 | 269.9523
2326.0823 | 327.4189 | 273.6609 | 269.9448
2327.0823 | 327.4977 | 273.6846 | 269.9372
2328.0823 | 327.5556 | 273.7133 | 269.9424
2329.0823 | 327.5437 | 273.7287 | 269.9599
2330.0823 | 327.5589 | 273.753 | 269.9724
2331.0823 | 327.5608 | 273.7281 | 269.8914
2332.0823 | 327.5893 | 273.7381 | 269.8596
2333.0823 | 327.5529 | 273.754 | 269.8631
2334.0823 | 327.6235 | 273.7829 | 269.8468
2335.0979 | 327.6889 | 273.7985 | 269.8337
2336.0823 | 327.7519 | 273.8083 | 269.857
2337.0823 | 327.8023 | 273.8235 | 269.8944
2338.0823 | 327.8704 | 273.8274 | 269.9293
2339.0823 | 327.942 | 273.8225 | 269.9679
2340.0823 | 328.0116 | 273.8108 | 269.9624
2341.0823 | 328.0547 | 273.7955 | 269.9604
2342.0823 | 328.1121 | 273.7994 | 269.9652
2343.0823 | 328.2157 | 273.7976 | 269.9483
2344.0823 | 328.208 | 273.7883 | 269.9282
2345.0823 | 328.2538 | 273.7258 | 269.9324
2346.0823 | 328.2616 | 273.6752 | 269.9422
2347.0823 | 328.2864 | 273.6124 | 269.9369
2348.0823 | 328.2232 | 273.5811 | 269.9332
2349.0823 | 328.2717 | 273.5589 | 269.9301
2350.0823 | 328.2544 | 273.5894 | 269.9618
2351.0823 | 328.227 | 273.5948 | 269.9311
2352.0823 | 328.1438 | 273.6016 | 269.8993
2353.0823 | 328.1019 | 273.6347 | 269.8999
2354.0823 | 328.2079 | 273.6405 | 269.9211
2355.0823 | 328.2122 | 273.6542 | 269.9455
2356.0823 | 328.2991 | 273.6612 | 269.9842
2357.0823 | 328.3838 | 273.6595 | 270.0074
2358.0823 | 328.2715 | 273.6711 | 270.0007
2359.0823 | 328.2774 | 273.6844 | 269.9891
2360.0823 | 328.1973 | 273.6891 | 269.994
2361.0823 | 328.1631 | 273.7081 | 269.9897
2362.0823 | 328.0203 | 273.7451 | 270.0029
2363.0823 | 327.9984 | 273.7708 | 270.0331
2364.0823 | 328.0528 | 273.7905 | 270.0479
2365.0979 | 328.1095 | 273.8031 | 270.0365
2366.0823 | 328.1487 | 273.8274 | 270.0325
2367.0823 | 328.226 | 273.8701 | 270.0401
2368.0823 | 328.2015 | 273.868 | 270.0459
2369.0823 | 328.1098 | 273.8613 | 270.062
2370.0823 | 328.073 | 273.8436 | 270.0787
2371.0823 | 328.0655 | 273.8411 | 270.072
2372.0823 | 328.0795 | 273.822 | 270.0629
2373.0823 | 328.0491 | 273.8129 | 270.0531
2374.0823 | 328.0703 | 273.8242 | 270.0453
2375.0823 | 328.1317 | 273.8446 | 270.0539
2376.0823 | 328.2011 | 273.8581 | 270.0812
2377.0823 | 328.172 | 273.8721 | 270.0782
2378.0823 | 328.1482 | 273.8701 | 270.0615
2379.0823 | 328.1431 | 273.8689 | 270.0275
2380.0823 | 328.2087 | 273.8385 | 270.0011
2381.0823 | 328.2576 | 273.8336 | 269.9913
2382.0823 | 328.2723 | 273.8488 | 269.9818
2383.0823 | 328.2605 | 273.8406 | 269.9481
2384.0823 | 328.3166 | 273.8479 | 269.9342
2385.0823 | 328.3392 | 273.8396 | 269.9091
2386.0823 | 328.3787 | 273.8595 | 269.9139
2387.0823 | 328.3203 | 273.8557 | 269.9082
2388.0823 | 328.2894 | 273.86 | 269.9093
2389.0823 | 328.2781 | 273.8593 | 269.8914
2390.0823 | 328.3253 | 273.8496 | 269.8766
2391.0823 | 328.3444 | 273.8602 | 269.8532
2392.0823 | 328.3226 | 273.8566 | 269.8015
2393.0823 | 328.3618 | 273.8528 | 269.7614
2394.0823 | 328.3841 | 273.8636 | 269.7476
2395.0823 | 328.4479 | 273.8802 | 269.7549
2396.0823 | 328.4736 | 273.8786 | 269.8001
2397.0823 | 328.4092 | 273.8414 | 269.8484
2398.0823 | 328.368 | 273.8114 | 269.8881
2399.0823 | 328.4325 | 273.7665 | 269.8861
2400.0823 | 328.4367 | 273.7004 | 269.8814
2401.0823 | 328.3884 | 273.6971 | 269.9023
2402.0823 | 328.3506 | 273.7042 | 269.9263
2403.0823 | 328.9495 | 273.7042 | 269.9553
2404.0823 | 330.2857 | 273.7262 | 269.9665
2405.0823 | 332.2875 | 273.7771 | 270.004
2406.0823 | 334.736 | 273.8497 | 270.0964
2407.0823 | 337.5785 | 273.9365 | 270.2028
2408.0823 | 340.6843 | 274.065 | 270.3535
2409.0823 | 343.749 | 274.1881 | 270.5662
2410.0823 | 346.8488 | 274.3533 | 270.8102
2411.0823 | 349.6985 | 274.5372 | 271.0625
2412.0979 | 352.3217 | 274.7513 | 271.3294
2413.0823 | 354.5671 | 274.9807 | 271.5933
2414.0823 | 356.5039 | 275.2245 | 271.8426
2415.0823 | 358.0373 | 275.4882 | 272.1108
2416.0823 | 359.3136 | 275.7415 | 272.3526
2417.0979 | 360.3964 | 276.0163 | 272.6003
2418.0823 | 361.231 | 276.2757 | 272.8226
2419.0823 | 361.8897 | 276.52 | 273.0478
2420.0823 | 362.3506 | 276.7687 | 273.229
2421.0823 | 362.7038 | 276.9939 | 273.402
2422.0823 | 362.9413 | 277.1966 | 273.5721
2423.0823 | 362.9994 | 277.4073 | 273.7687
2424.0823 | 362.9539 | 277.6239 | 273.9824
2425.0979 | 362.8474 | 277.8282 | 274.1584
2426.0823 | 362.7304 | 278.0332 | 274.3425
2427.0979 | 362.6095 | 278.2246 | 274.5314
2428.0823 | 362.4135 | 278.3938 | 274.7127
2429.0823 | 362.1799 | 278.5482 | 274.8849
2430.0823 | 361.8756 | 278.7123 | 274.949
2431.0823 | 361.5767 | 278.8818 | 275.0673
2432.0823 | 361.1792 | 279.0369 | 275.1279
2433.0823 | 360.7067 | 279.1942 | 275.2077
2434.0823 | 360.3308 | 279.3598 | 275.3162
2435.0823 | 360.0311 | 279.586 | 275.4284
2436.0823 | 359.6467 | 279.7037 | 275.5389
2437.0823 | 359.2282 | 279.829 | 275.663
2438.0979 | 358.7333 | 279.9485 | 275.7939
2439.0823 | 358.236 | 280.0585 | 275.909
2440.0823 | 357.8034 | 280.1637 | 276.031
2441.0823 | 357.3605 | 280.2695 | 276.1584
2442.0823 | 356.8777 | 280.3821 | 276.2941
2443.0823 | 356.3633 | 280.4847 | 276.4129
2444.0823 | 355.9367 | 280.5704 | 276.5136
2445.0823 | 355.3711 | 280.6813 | 276.5942
2446.0823 | 354.8914 | 280.7727 | 276.6826
2447.0823 | 354.3647 | 280.8669 | 276.7542
2448.0979 | 353.8692 | 280.9645 | 276.8408
2449.0823 | 353.334 | 281.0293 | 276.9262
2450.0823 | 352.8521 | 281.0819 | 277.0016
2451.0823 | 352.443 | 281.1147 | 277.0748
2452.0979 | 352.0029 | 281.1745 | 277.1533
2453.0823 | 351.5713 | 281.2117 | 277.1914
2454.0823 | 351.0915 | 281.2695 | 277.2389
2455.0823 | 350.6454 | 281.3157 | 277.2813
2456.0823 | 350.2077 | 281.3589 | 277.3296
2457.0979 | 349.8107 | 281.3913 | 277.418
2458.0823 | 349.3872 | 281.4248 | 277.4863
2459.0823 | 349.0306 | 281.4636 | 277.5261
2460.0823 | 348.6649 | 281.5131 | 277.5704
2461.0823 | 348.3909 | 281.5487 | 277.6094
2462.0823 | 348.1035 | 281.573 | 277.6189
2463.0823 | 347.8556 | 281.5741 | 277.6365
2464.0823 | 347.6776 | 281.6174 | 277.6634
2465.0823 | 347.4832 | 281.6448 | 277.7085
2466.0823 | 347.3174 | 281.6803 | 277.7401
2467.0979 | 347.2025 | 281.7312 | 277.7795
2468.0823 | 347.0941 | 281.7416 | 277.8273
2469.0823 | 347.0567 | 281.7532 | 277.8783
2470.0823 | 347.0097 | 281.7711 | 277.9187
2471.0823 | 347.0914 | 281.7939 | 277.916
2472.0823 | 347.2427 | 281.8396 | 277.9247
2473.0823 | 347.3224 | 281.8978 | 277.9392
2474.0823 | 347.5231 | 281.942 | 277.9728
2475.0823 | 347.7065 | 281.9973 | 278.0305
2476.0823 | 347.9542 | 282.0257 | 278.093
2477.0823 | 348.1572 | 282.0661 | 278.1358
2478.0823 | 348.2828 | 282.093 | 278.2121
2479.0823 | 348.4469 | 282.1218 | 278.292
2480.0823 | 348.5607 | 282.1888 | 278.3714
2481.0823 | 348.8683 | 282.2582 | 278.4597
2482.0823 | 348.9898 | 282.294 | 278.5003
2483.0823 | 349.1629 | 282.3696 | 278.5462
2484.0823 | 349.3899 | 282.4576 | 278.6415
2485.0823 | 349.4784 | 282.5137 | 278.7146
2486.0823 | 349.6663 | 282.5647 | 278.7916
2487.0823 | 349.8643 | 282.6185 | 278.8608
2488.0823 | 350.0976 | 282.7042 | 278.9349
2489.0823 | 350.221 | 282.7862 | 279.0373
2490.0823 | 350.4061 | 282.8632 | 279.1093
2491.0823 | 350.548 | 282.9442 | 279.1926
2492.0823 | 350.7224 | 283.0454 | 279.287
2493.0823 | 350.8253 | 283.1319 | 279.3773
2494.0823 | 350.9875 | 283.2036 | 279.483
2495.0823 | 351.1049 | 283.2643 | 279.5738
2496.0823 | 351.1765 | 283.3312 | 279.6809
2497.0823 | 351.1344 | 283.4141 | 279.7791
2498.0823 | 351.137 | 283.4883 | 279.8619
2499.0823 | 351.1688 | 283.5658 | 279.9301
2500.0823 | 351.1788 | 283.6531 | 280.0092
2501.0823 | 351.2302 | 283.7239 | 280.1009
2502.0823 | 351.2589 | 283.7846 | 280.1475
2503.0823 | 351.3489 | 283.8656 | 280.2006
2504.0823 | 351.3664 | 283.9423 | 280.2626
2505.0823 | 351.3416 | 284.0213 | 280.3035
2506.0823 | 351.3783 | 284.0704 | 280.3752
2507.0823 | 351.4672 | 284.156 | 280.4445
2508.0823 | 351.4979 | 284.2257 | 280.5041
2509.0823 | 351.5508 | 284.291 | 280.5389
2510.0823 | 351.5823 | 284.3805 | 280.5859
2511.0823 | 351.5773 | 284.4407 | 280.6492
2512.0823 | 351.6387 | 284.523 | 280.7442
2513.0823 | 351.6027 | 284.5656 | 280.8055
2514.0823 | 351.7258 | 284.6018 | 280.8654
2515.0823 | 351.7384 | 284.6627 | 280.9232
2516.0823 | 351.6961 | 284.7154 | 281.0012
2517.0823 | 351.7276 | 284.7849 | 281.0837
2518.0823 | 351.768 | 284.8546 | 281.1753
2519.0823 | 351.8301 | 284.905 | 281.2386
2520.0823 | 351.7948 | 284.9486 | 281.2196
2521.0823 | 351.9124 | 284.9939 | 281.2336
2522.0823 | 351.9029 | 285.0403 | 281.2854
2523.0823 | 351.7744 | 285.0987 | 281.3385
2524.0823 | 351.7787 | 285.1678 | 281.3879
2525.0823 | 351.9366 | 285.2186 | 281.437
2526.0823 | 351.9947 | 285.2895 | 281.5081
2527.0823 | 351.9636 | 285.3583 | 281.6316
2528.0823 | 351.9905 | 285.4445 | 281.7135
2529.0823 | 352.0074 | 285.5038 | 281.7725
2530.0823 | 351.9716 | 285.5797 | 281.8175
2531.0823 | 351.8983 | 285.6316 | 281.8916
2532.0823 | 351.7992 | 285.6796 | 281.9446
2533.0823 | 351.78 | 285.7205 | 281.9479
2534.0823 | 351.7568 | 285.7816 | 281.9734
2535.0823 | 351.6625 | 285.8368 | 281.997
2536.0823 | 351.589 | 285.8925 | 282.0115
2537.0823 | 351.5903 | 285.9635 | 282.0301
2538.0823 | 351.5693 | 285.9873 | 282.0185
2539.0823 | 351.5547 | 286.0156 | 282.0035
2540.0823 | 351.5734 | 286.0532 | 282.0197
2541.0823 | 351.4848 | 286.1127 | 282.0707
2542.0823 | 351.4647 | 286.1718 | 282.1072
2543.0823 | 351.548 | 286.2403 | 282.1713
2544.0823 | 351.5268 | 286.3063 | 282.1939
2545.0979 | 351.5468 | 286.3453 | 282.2215
2546.0823 | 351.5542 | 286.379 | 282.2555
2547.0823 | 351.4719 | 286.4312 | 282.2648
2548.0823 | 351.5136 | 286.479 | 282.2948
2549.0823 | 351.4741 | 286.5389 | 282.3816
2550.0823 | 351.4168 | 286.5916 | 282.4619
2551.0823 | 351.3857 | 286.6475 | 282.5087
2552.0823 | 351.4312 | 286.6981 | 282.5749
2553.0823 | 351.5142 | 286.7656 | 282.6242
2554.0823 | 351.6465 | 286.7982 | 282.6564
2555.0823 | 351.7291 | 286.87 | 282.7123
2556.0823 | 351.7681 | 286.9002 | 282.6308
2557.0823 | 351.7618 | 286.9298 | 282.5874
2558.0823 | 351.7586 | 286.97 | 282.6202
2559.0823 | 351.8802 | 287.0099 | 282.678
2560.0823 | 351.9084 | 287.0549 | 282.7378
2561.0823 | 351.8994 | 287.1142 | 282.8191
2562.0979 | 351.8719 | 287.1683 | 282.8885
2563.0823 | 351.9317 | 287.2326 | 282.9982
2564.0823 | 352.0129 | 287.2873 | 283.1061
2565.0823 | 351.9646 | 287.3234 | 283.1783
2566.0823 | 351.8318 | 287.3704 | 283.2643
2567.0823 | 351.8461 | 287.44 | 283.3141
2568.0823 | 351.9203 | 287.4784 | 283.3771
2569.0823 | 351.9404 | 287.5211 | 283.4418
2570.0979 | 351.9079 | 287.538 | 283.5046
2571.0823 | 351.8145 | 287.5915 | 283.5637
2572.0823 | 351.8622 | 287.6412 | 283.6447
2573.0823 | 351.7624 | 287.683 | 283.6902
2574.0979 | 351.705 | 287.7344 | 283.7329
2575.0823 | 351.7187 | 287.7945 | 283.807
2576.0823 | 351.7542 | 287.8442 | 283.8381
2577.0979 | 351.8482 | 287.8848 | 283.8463
2578.0823 | 351.9334 | 287.9062 | 283.9032
2579.0823 | 351.8767 | 287.9052 | 283.962
2580.0979 | 351.9394 | 287.8988 | 284.0202
2581.0823 | 352.145 | 287.8829 | 284.0818
2582.0979 | 352.2927 | 287.8599 | 284.1322
2583.0823 | 352.3338 | 287.8501 | 284.1532
2584.0823 | 352.4237 | 287.8409 | 284.1646
2585.0979 | 352.3908 | 287.8559 | 284.2153
2586.0823 | 352.3488 | 287.8583 | 284.2759
2587.0823 | 352.4256 | 287.8598 | 284.3424
2588.0823 | 352.4069 | 287.88 | 284.3841
2589.0823 | 352.4203 | 287.9116 | 284.4299
2590.0823 | 352.4029 | 287.9482 | 284.4733
2591.0823 | 352.4016 | 287.9843 | 284.5124
2592.0979 | 352.3947 | 288.0507 | 284.5622
2593.0823 | 352.4194 | 288.0978 | 284.6096
2594.0823 | 352.3269 | 288.1764 | 284.6682
2595.0823 | 352.2411 | 288.2497 | 284.7254
2596.0979 | 352.214 | 288.3408 | 284.7827
2597.0823 | 352.2186 | 288.4198 | 284.8106
2598.0823 | 352.1916 | 288.4956 | 284.8572
2599.0823 | 352.1875 | 288.6024 | 284.8763
2600.0823 | 352.1811 | 288.667 | 284.8817
2601.0823 | 352.1841 | 288.74 | 284.8844
2602.0823 | 352.167 | 288.7992 | 284.924
2603.0823 | 352.0693 | 288.8742 | 284.9947
2604.0979 | 352.0493 | 288.9213 | 285.0054
2605.0979 | 352.0762 | 288.9896 | 285.0324
2606.0823 | 352.0585 | 289.0754 | 285.064
2607.0979 | 352.0867 | 289.1277 | 285.1013
2608.0823 | 352.0514 | 289.1876 | 285.1186
2609.0823 | 351.9466 | 289.2135 | 285.1229
2610.0823 | 351.9119 | 289.2299 | 285.1442
2611.0823 | 351.9237 | 289.2548 | 285.196
2612.0823 | 351.8789 | 289.2781 | 285.261
2613.0823 | 351.7737 | 289.324 | 285.3407
2614.0823 | 351.6959 | 289.3546 | 285.3782
2615.0823 | 351.6726 | 289.3892 | 285.4432
2616.0823 | 351.6479 | 289.4253 | 285.4793
2617.0979 | 351.6709 | 289.4673 | 285.4586
2618.0823 | 351.6154 | 289.503 | 285.4083
2619.0823 | 351.6034 | 289.533 | 285.3983
2620.0823 | 351.5378 | 289.5534 | 285.416
2621.0823 | 351.4907 | 289.5651 | 285.4575
2622.0823 | 351.5055 | 289.5775 | 285.4883
2623.0823 | 351.535 | 289.5985 | 285.507
2624.0823 | 351.5379 | 289.6019 | 285.4249
2625.0823 | 351.529 | 289.6379 | 285.3635
2626.0823 | 351.514 | 289.6492 | 285.3723
2627.0823 | 351.55 | 289.6903 | 285.4204
2628.0823 | 351.6161 | 289.7317 | 285.4836
2629.0823 | 351.6794 | 289.7794 | 285.5263
2630.0823 | 351.6014 | 289.8403 | 285.5822
2631.0823 | 351.5071 | 289.8745 | 285.6403
2632.0823 | 351.5294 | 289.8812 | 285.691
2633.0823 | 351.6003 | 289.917 | 285.749
2634.0823 | 351.5517 | 289.9644 | 285.7946
2635.0823 | 351.6375 | 290.0037 | 285.8014
2636.0823 | 351.5966 | 290.0285 | 285.7823
2637.0823 | 351.5472 | 290.0081 | 285.7577
2638.0823 | 351.4966 | 289.992 | 285.7737
2639.0823 | 351.4421 | 290.0159 | 285.8383
2640.0823 | 351.4112 | 290.0324 | 285.9067
2641.0823 | 351.4648 | 290.0527 | 285.8816
2642.0823 | 351.5588 | 290.0899 | 285.8928
2643.0823 | 351.5556 | 290.1277 | 285.9073
2644.0823 | 351.4935 | 290.1823 | 285.9525
2645.0823 | 351.441 | 290.2373 | 286.0155
2646.0823 | 351.3965 | 290.2807 | 286.0659
2647.0823 | 351.334 | 290.3121 | 286.1177
2648.0823 | 351.3056 | 290.3485 | 286.1654
2649.0823 | 351.2798 | 290.4033 | 286.2271
2650.0823 | 351.2615 | 290.4454 | 286.3133
2651.0823 | 351.1422 | 290.493 | 286.3747
2652.0823 | 351.0886 | 290.5359 | 286.4262
2653.0823 | 351.0545 | 290.5914 | 286.4806
2654.0823 | 350.9916 | 290.6519 | 286.5188
2655.0823 | 351.0145 | 290.6917 | 286.5247
2656.0823 | 351.0364 | 290.7305 | 286.5321
2657.0823 | 351.0831 | 290.7656 | 286.5578
2658.0823 | 351.1179 | 290.8081 | 286.5745
2659.0823 | 351.0447 | 290.83 | 286.5971
2660.0823 | 351.0201 | 290.8339 | 286.6162
2661.0823 | 351.0443 | 290.8666 | 286.6069
2662.0823 | 351.0294 | 290.8932 | 286.6266
2663.0823 | 351.0154 | 290.9375 | 286.6726
2664.0823 | 351.053 | 290.9595 | 286.7319
2665.0823 | 351.0972 | 290.9845 | 286.7992
2666.0823 | 350.998 | 291.0135 | 286.8352
2667.0823 | 351.0188 | 291.0339 | 286.912
2668.0823 | 351.0823 | 291.0453 | 286.9877
2669.0823 | 351.1241 | 291.0449 | 287.0591
2670.0823 | 351.1583 | 291.0671 | 287.1247
2671.0823 | 351.2121 | 291.0669 | 287.1562
2672.0823 | 351.2488 | 291.0628 | 287.1784
2673.0823 | 351.1946 | 291.0695 | 287.1877
2674.0823 | 351.1887 | 291.0852 | 287.1754
2675.0823 | 351.2093 | 291.1009 | 287.126
2676.0823 | 351.3191 | 291.1047 | 287.0667
2677.0823 | 351.3493 | 291.1291 | 287.0489
2678.0823 | 351.3693 | 291.1672 | 287.0614
2679.0823 | 351.4238 | 291.1834 | 287.0962
2680.0823 | 351.3969 | 291.2014 | 287.1268
2681.0823 | 351.2813 | 291.2218 | 287.1235
2682.0979 | 351.1512 | 291.2408 | 287.0949
2683.0823 | 351.0842 | 291.2747 | 287.069
2684.0823 | 351.063 | 291.3231 | 286.994
2685.0823 | 350.9936 | 291.3536 | 286.8706
2686.0823 | 350.9488 | 291.394 | 286.7937
2687.0823 | 350.8518 | 291.4084 | 286.7753
2688.0823 | 350.7506 | 291.458 | 286.7767
2689.0823 | 350.6533 | 291.4909 | 286.7877
2690.0823 | 350.6201 | 291.533 | 286.8294
2691.0823 | 350.6606 | 291.5903 | 286.9176
2692.0979 | 350.661 | 291.6303 | 286.9851
2693.0823 | 350.6801 | 291.648 | 287.0486
2694.0979 | 350.7814 | 291.6472 | 287.1019
2695.0823 | 350.8788 | 291.6561 | 287.1621
2696.0823 | 350.892 | 291.6489 | 287.2197
2697.0823 | 350.9612 | 291.6455 | 287.2743
2698.0823 | 350.957 | 291.6432 | 287.3194
2699.0823 | 350.9283 | 291.6159 | 287.3706
2700.0823 | 350.9307 | 291.6247 | 287.4431
2701.0823 | 350.9941 | 291.6317 | 287.4911
2702.0979 | 350.9986 | 291.6508 | 287.4703
2703.0823 | 351.0894 | 291.6873 | 287.4837
2704.0823 | 351.2057 | 291.7071 | 287.5243
2705.0823 | 351.2301 | 291.7268 | 287.5394
2706.0823 | 351.2321 | 291.7577 | 287.5708
2707.0823 | 351.2203 | 291.8054 | 287.6253
2708.0823 | 351.172 | 291.8373 | 287.6737
2709.0823 | 351.144 | 291.8572 | 287.7116
2710.0823 | 351.2113 | 291.8976 | 287.6844
2711.0823 | 351.3315 | 291.9276 | 287.65
2712.0823 | 351.3454 | 291.9512 | 287.584
2713.0823 | 351.327 | 291.9783 | 287.5172
2714.0823 | 351.3962 | 292.0105 | 287.5106
2715.0823 | 351.4116 | 292.0435 | 287.5522
2716.0823 | 351.3386 | 292.0847 | 287.5431
2717.0823 | 351.2935 | 292.112 | 287.548
2718.0823 | 351.2517 | 292.1477 | 287.5625
2719.0823 | 351.1506 | 292.1752 | 287.6217
2720.0979 | 351.1104 | 292.1923 | 287.6878
2721.0823 | 351.0296 | 292.2174 | 287.7644
2722.0823 | 350.9316 | 292.2254 | 287.7963
2723.0823 | 350.8642 | 292.2227 | 287.8524
2724.0823 | 350.9769 | 292.2259 | 287.8961
2725.0823 | 351.0042 | 292.2446 | 287.9534
2726.0823 | 351.0512 | 292.2768 | 287.9711
2727.0979 | 351.105 | 292.2975 | 288.0141
2728.0823 | 351.1393 | 292.3058 | 288.0812
2729.0823 | 351.1172 | 292.3604 | 288.1502
2730.0823 | 351.1446 | 292.3931 | 288.1961
2731.0823 | 351.208 | 292.45 | 288.2348
2732.0979 | 351.2098 | 292.517 | 288.305
2733.0823 | 351.2076 | 292.5543 | 288.3622
2734.0823 | 351.2626 | 292.5968 | 288.3674
2735.0823 | 351.3105 | 292.6188 | 288.3265
2736.0979 | 351.277 | 292.6392 | 288.3184
2737.0823 | 351.3012 | 292.6577 | 288.3117
2738.0823 | 351.2628 | 292.6616 | 288.3322
2739.0823 | 351.2136 | 292.6824 | 288.3799
2740.0823 | 351.1965 | 292.7161 | 288.4771
2741.0823 | 351.1713 | 292.7422 | 288.5841
2742.0979 | 351.144 | 292.7459 | 288.6315
2743.0823 | 351.2095 | 292.7489 | 288.6486
2744.0823 | 351.2343 | 292.7732 | 288.6971
2745.0823 | 351.1461 | 292.7783 | 288.6916
2746.0823 | 351.1837 | 292.8013 | 288.6885
2747.0979 | 351.1339 | 292.7868 | 288.6919
2748.0823 | 350.9325 | 292.7933 | 288.6957
2749.0823 | 350.7704 | 292.8013 | 288.6675
2750.0823 | 350.7185 | 292.8004 | 288.6851
2751.0823 | 350.6866 | 292.8272 | 288.7592
2752.0823 | 350.5974 | 292.8345 | 288.8287
2753.0823 | 350.5851 | 292.8458 | 288.886
2754.0823 | 350.5598 | 292.8407 | 288.9616
2755.0823 | 350.6372 | 292.8588 | 289.0325
2756.0823 | 350.5869 | 292.8583 | 289.1065
2757.0979 | 350.5411 | 292.8621 | 289.1159
2758.0823 | 350.6559 | 292.8613 | 289.0525
2759.0823 | 350.781 | 292.8815 | 289.0346
2760.0823 | 350.7641 | 292.9097 | 289.033
2761.0823 | 350.7801 | 292.9356 | 289.0316
2762.0823 | 350.887 | 292.9751 | 289.0492
2763.0823 | 350.9303 | 292.9985 | 289.0689
2764.0823 | 350.9561 | 293.0188 | 289.0597
2765.0823 | 351.0023 | 293.061 | 289.0571
2766.0823 | 350.9459 | 293.0773 | 289.0603
2767.0823 | 350.9149 | 293.1217 | 289.0514
2768.0823 | 350.9317 | 293.1319 | 289.0247
2769.0823 | 350.9538 | 293.1563 | 289.0083
2770.0823 | 351.0539 | 293.1734 | 289.0049
2771.0823 | 351.1062 | 293.2018 | 289.0654
2772.0823 | 351.0988 | 293.204 | 289.0951
2773.0823 | 351.1294 | 293.2057 | 289.1361
2774.0823 | 351.185 | 293.1966 | 289.145
2775.0823 | 351.1846 | 293.1994 | 289.1812
2776.0823 | 351.1534 | 293.208 | 289.2374
2777.0823 | 351.1614 | 293.2396 | 289.3111
2778.0823 | 351.1476 | 293.2388 | 289.3527
2779.0823 | 351.0826 | 293.2364 | 289.3935
2780.0823 | 351.0786 | 293.2399 | 289.4217
2781.0823 | 351.1272 | 293.2709 | 289.4899
2782.0823 | 351.1793 | 293.2857 | 289.538
2783.0823 | 351.192 | 293.2954 | 289.4195
2784.0823 | 351.2234 | 293.3169 | 289.3232
2785.0823 | 351.1697 | 293.3619 | 289.2853
2786.0823 | 351.1779 | 293.3989 | 289.3161
2787.0823 | 351.1993 | 293.4342 | 289.3571
2788.0823 | 351.1989 | 293.464 | 289.3162
2789.0823 | 351.2181 | 293.5047 | 289.3231
2790.0823 | 351.376 | 293.5467 | 289.3518
2791.0823 | 351.4421 | 293.5778 | 289.3992
2792.0823 | 351.5066 | 293.6008 | 289.4341
2793.0823 | 351.6601 | 293.6288 | 289.4746
2794.0823 | 351.6834 | 293.6768 | 289.515
2795.0823 | 351.6659 | 293.711 | 289.5595
2796.0823 | 351.6997 | 293.7192 | 289.5935
2797.0823 | 351.7363 | 293.7332 | 289.6223
2798.0823 | 351.7879 | 293.7468 | 289.6373
2799.0823 | 351.8244 | 293.757 | 289.6235
2800.0823 | 351.7952 | 293.7729 | 289.6117
2801.0823 | 351.8417 | 293.81 | 289.6313
2802.0823 | 351.9757 | 293.8453 | 289.6344
2803.0823 | 352.0543 | 293.885 | 289.6233
2804.0823 | 352.0739 | 293.9175 | 289.6305
2805.0823 | 352.1406 | 293.9712 | 289.6986
2806.0823 | 352.0399 | 294.001 | 289.7761
2807.0823 | 351.9407 | 294.0606 | 289.8512
2808.0823 | 351.8132 | 294.0897 | 289.9177
2809.0823 | 351.7575 | 294.0957 | 289.9466
2810.0823 | 351.8174 | 294.0937 | 289.9519
2811.0823 | 351.7537 | 294.0801 | 289.9921
2812.0823 | 351.6985 | 294.0508 | 290.0096
2813.0823 | 351.6572 | 294.0127 | 290.031
2814.0823 | 351.7405 | 293.9766 | 290.0766
2815.0823 | 351.7582 | 293.9398 | 290.0811
2816.0823 | 351.7319 | 293.9093 | 290.0646
2817.0823 | 351.7418 | 293.8941 | 290.0298
2818.0823 | 351.7102 | 293.892 | 290.0364
2819.0823 | 351.8121 | 293.8673 | 290.0546
2820.0823 | 351.8235 | 293.8522 | 290.061
2821.0823 | 351.8446 | 293.8333 | 290.0695
2822.0823 | 351.7441 | 293.8074 | 290.0742
2823.0823 | 351.7161 | 293.7977 | 290.1035
2824.0823 | 351.7765 | 293.8163 | 290.1625
2825.0823 | 351.7607 | 293.8466 | 290.2464
2826.0823 | 351.793 | 293.8845 | 290.2923
2827.0823 | 351.7693 | 293.9024 | 290.3282
2828.0823 | 351.8279 | 293.9312 | 290.351
2829.0823 | 351.8866 | 293.9781 | 290.3735
2830.0823 | 351.8536 | 294.0189 | 290.3472
2831.0823 | 351.8021 | 294.0419 | 290.2982
2832.0823 | 351.6712 | 294.0924 | 290.2961
2833.0823 | 351.6958 | 294.1217 | 290.2722
2834.0823 | 351.7312 | 294.1655 | 290.2729
2835.0823 | 351.7382 | 294.2029 | 290.2605
2836.0823 | 351.7325 | 294.2384 | 290.2762
2837.0823 | 351.7915 | 294.2354 | 290.2824
2838.0823 | 351.7831 | 294.2272 | 290.2904
2839.0823 | 351.7654 | 294.2414 | 290.2605
2840.0823 | 351.7583 | 294.2704 | 290.2137
2841.0823 | 351.6522 | 294.2691 | 290.2001
2842.0823 | 351.5946 | 294.2758 | 290.1583
2843.0823 | 351.614 | 294.2832 | 290.1027
2844.0823 | 351.6821 | 294.277 | 290.099
2845.0823 | 351.7239 | 294.2711 | 290.0953
2846.0823 | 351.7974 | 294.278 | 290.0862
2847.0823 | 351.7711 | 294.2694 | 290.115
2848.0823 | 351.6872 | 294.2365 | 290.1135
2849.0823 | 351.7106 | 294.2179 | 290.1384
2850.0823 | 351.6571 | 294.2334 | 290.1846
2851.0823 | 351.5231 | 294.2483 | 290.2155
2852.0979 | 351.5011 | 294.2669 | 290.2796
2853.0823 | 351.368 | 294.2754 | 290.3673
2854.0823 | 351.3451 | 294.268 | 290.4053
2855.0823 | 351.3874 | 294.2628 | 290.3835
2856.0823 | 351.2822 | 294.2628 | 290.3881
2857.0823 | 351.147 | 294.263 | 290.4054
2858.0823 | 351.1686 | 294.2711 | 290.4334
2859.0823 | 351.2087 | 294.2883 | 290.4494
2860.0823 | 351.1988 | 294.3031 | 290.4342
2861.0823 | 351.2586 | 294.3104 | 290.4641
2862.0823 | 351.2002 | 294.315 | 290.5186
2863.0823 | 351.1582 | 294.3503 | 290.5443
2864.0823 | 351.247 | 294.3731 | 290.5539
2865.0823 | 351.1819 | 294.4175 | 290.5319
2866.0823 | 351.1743 | 294.4439 | 290.5348
2867.0979 | 351.1814 | 294.4765 | 290.5601
2868.0823 | 351.2692 | 294.4964 | 290.4794
2869.0823 | 351.4183 | 294.5225 | 290.3948
2870.0823 | 351.4788 | 294.5571 | 290.3265
2871.0823 | 351.4763 | 294.59 | 290.3211
2872.0823 | 351.4405 | 294.6315 | 290.3383
2873.0823 | 351.4925 | 294.67 | 290.4193
2874.0823 | 351.4814 | 294.7154 | 290.473
2875.0823 | 351.4071 | 294.738 | 290.4565
2876.0823 | 351.3016 | 294.7771 | 290.455
2877.0823 | 351.2716 | 294.7983 | 290.4236
2878.0823 | 351.3173 | 294.8156 | 290.387
2879.0823 | 351.267 | 294.8245 | 290.403
2880.0823 | 351.2166 | 294.8496 | 290.4738
2881.0823 | 351.2472 | 294.86 | 290.5468
2882.0823 | 351.3671 | 294.8841 | 290.5765
2883.0823 | 351.3667 | 294.8816 | 290.5638
2884.0823 | 351.3319 | 294.8919 | 290.5886
2885.0823 | 351.2932 | 294.8603 | 290.6449
2886.0823 | 351.2327 | 294.8335 | 290.664
2887.0823 | 351.1184 | 294.828 | 290.6767
2888.0823 | 351.0994 | 294.8119 | 290.711
2889.0823 | 351.1672 | 294.7912 | 290.7567
2890.0823 | 351.1973 | 294.781 | 290.8066
2891.0823 | 351.1967 | 294.7613 | 290.8497
2892.0979 | 351.1467 | 294.7449 | 290.8914
2893.0823 | 351.1255 | 294.7541 | 290.9346
2894.0823 | 351.2043 | 294.7621 | 290.9061
2895.0823 | 351.3043 | 294.7686 | 290.8835
2896.0823 | 351.2519 | 294.7339 | 290.8611
2897.0979 | 351.1237 | 294.7197 | 290.853
2898.0823 | 351.1958 | 294.7169 | 290.8729
2899.0823 | 351.2409 | 294.7292 | 290.908
2900.0823 | 351.2087 | 294.7434 | 290.9293
2901.0823 | 351.119 | 294.7818 | 290.9726
2902.0823 | 351.1398 | 294.8161 | 290.9285
2903.0823 | 351.2115 | 294.8405 | 290.9047
2904.0823 | 351.2825 | 294.8714 | 290.8799
2905.0823 | 351.3551 | 294.8805 | 290.8269
2906.0823 | 351.3814 | 294.9 | 290.7796
2907.0979 | 351.3607 | 294.8977 | 290.771
2908.0823 | 351.3889 | 294.8972 | 290.7562
2909.0823 | 351.3697 | 294.9009 | 290.7869
2910.0823 | 351.3604 | 294.9293 | 290.8195
2911.0823 | 351.292 | 294.9568 | 290.8212
2912.0979 | 351.2131 | 294.9744 | 290.8494
2913.0823 | 351.2602 | 294.9832 | 290.9071
2914.0823 | 351.2761 | 295.0032 | 290.9369
2915.0823 | 351.2872 | 294.9906 | 290.9704
2916.0823 | 351.378 | 294.9781 | 291.0017
2917.0823 | 351.3335 | 294.939 | 291.018
2918.0823 | 351.3189 | 294.9342 | 291.0273
2919.0823 | 351.2928 | 294.9309 | 291.0763
2920.0823 | 351.2636 | 294.9299 | 291.1076
2921.0823 | 351.1837 | 294.9509 | 291.1291
2922.0823 | 351.1793 | 294.9841 | 291.1446
2923.0823 | 351.1731 | 295.0287 | 291.1922
2924.0823 | 351.1212 | 295.0356 | 291.2367
2925.0823 | 351.0948 | 295.0625 | 291.2695
2926.0823 | 351.176 | 295.1061 | 291.2556
2927.0979 | 351.2502 | 295.1301 | 291.241
2928.0823 | 351.2239 | 295.1612 | 291.2582
2929.0823 | 351.223 | 295.1618 | 291.2708
2930.0823 | 351.226 | 295.1553 | 291.3049
2931.0823 | 351.2302 | 295.1496 | 291.3079
2932.0823 | 351.0812 | 295.1536 | 291.3182
2933.0823 | 350.9949 | 295.1662 | 291.3515
2934.0823 | 350.9374 | 295.1758 | 291.3871
2935.0823 | 350.9259 | 295.1572 | 291.4049
2936.0823 | 350.9079 | 295.1472 | 291.4076
2937.0823 | 351.0074 | 295.1323 | 291.4203
2938.0823 | 351.1155 | 295.1234 | 291.434
2939.0823 | 351.2303 | 295.1129 | 291.4701
2940.0823 | 351.2878 | 295.1208 | 291.4889
2941.0823 | 351.2323 | 295.1256 | 291.4853
2942.0823 | 351.1922 | 295.1253 | 291.4864
2943.0823 | 351.1767 | 295.1207 | 291.4615
2944.0823 | 351.101 | 295.1354 | 291.4423
2945.0823 | 351.0577 | 295.1386 | 291.4672
2946.0823 | 350.9442 | 295.145 | 291.4591
2947.0823 | 350.9688 | 295.1683 | 291.4568
2948.0823 | 351.0584 | 295.1955 | 291.5069
2949.0823 | 351.1031 | 295.2402 | 291.5441
2950.0823 | 351.1031 | 295.2881 | 291.6076
2951.0823 | 351.1333 | 295.3161 | 291.6611
2952.0823 | 351.2635 | 295.332 | 291.701
2953.0823 | 351.3714 | 295.336 | 291.7408
2954.0823 | 351.468 | 295.3498 | 291.7483
2955.0823 | 351.5312 | 295.3528 | 291.7657
2956.0823 | 351.4922 | 295.3581 | 291.7592
2957.0823 | 351.4543 | 295.3556 | 291.7422
2958.0823 | 351.4646 | 295.3628 | 291.7263
2959.0823 | 351.5746 | 295.371 | 291.7055
2960.0823 | 351.5389 | 295.3828 | 291.6391
2961.0823 | 351.5217 | 295.4013 | 291.6304
2962.0823 | 351.534 | 295.4298 | 291.6456
2963.0823 | 351.467 | 295.4435 | 291.6616
2964.0823 | 351.3975 | 295.4567 | 291.6547
2965.0823 | 351.3916 | 295.4593 | 291.6151
2966.0823 | 351.3834 | 295.4732 | 291.5835
2967.0823 | 351.4264 | 295.5001 | 291.5379
2968.0823 | 351.4689 | 295.5293 | 291.5537
2969.0823 | 351.5324 | 295.543 | 291.5757
2970.0823 | 351.5207 | 295.5862 | 291.5888
2971.0823 | 351.4833 | 295.5938 | 291.5699
2972.0823 | 351.4634 | 295.6315 | 291.5504
2973.0823 | 351.4425 | 295.6221 | 291.5438
2974.0823 | 351.5413 | 295.6295 | 291.5341
2975.0823 | 351.5796 | 295.6302 | 291.5491
2976.0823 | 351.4992 | 295.618 | 291.5653
2977.0823 | 351.3706 | 295.613 | 291.5734
2978.0823 | 351.2858 | 295.5918 | 291.5423
2979.0823 | 351.2527 | 295.5979 | 291.4898
2980.0823 | 351.3122 | 295.6158 | 291.4663
2981.0823 | 351.3426 | 295.6278 | 291.4678
2982.0823 | 351.3226 | 295.648 | 291.4239
2983.0823 | 351.4293 | 295.652 | 291.4259
2984.0823 | 351.3908 | 295.6667 | 291.4341
2985.0823 | 351.4081 | 295.6815 | 291.4765
2986.0823 | 351.3834 | 295.7136 | 291.4877
2987.0823 | 351.4135 | 295.7574 | 291.506
2988.0823 | 351.3953 | 295.7798 | 291.5649
2989.0823 | 351.3672 | 295.8076 | 291.6186
2990.0823 | 351.3198 | 295.8219 | 291.6424
2991.0823 | 351.3268 | 295.8334 | 291.6513
2992.0823 | 351.3309 | 295.8619 | 291.6502
2993.0823 | 351.3616 | 295.8865 | 291.6778
2994.0823 | 351.4458 | 295.9197 | 291.7145
2995.0823 | 351.3885 | 295.9343 | 291.7039
2996.0823 | 351.3707 | 295.9666 | 291.731
2997.0823 | 351.3108 | 295.9737 | 291.7683
2998.0823 | 351.2508 | 295.9927 | 291.803
2999.0823 | 351.2787 | 295.9848 | 291.8622
3000.0823 | 351.2408 | 295.9612 | 291.8974
3001.0823 | 351.2121 | 295.9704 | 291.8725
3002.0979 | 351.1642 | 295.9764 | 291.8848
3003.0823 | 351.0932 | 295.9756 | 291.91
3004.0823 | 351.0739 | 295.9714 | 291.8449
3005.0823 | 351.0942 | 295.9443 | 291.7813
3006.0823 | 351.131 | 295.944 | 291.745
3007.0823 | 351.1443 | 295.9551 | 291.7216
3008.0823 | 351.191 | 295.9749 | 291.7287
3009.0823 | 351.199 | 295.9722 | 291.7753
3010.0823 | 351.1835 | 295.9807 | 291.8346
3011.0823 | 351.2023 | 295.9914 | 291.8859
3012.0823 | 351.3259 | 296.0026 | 291.9278
3013.0823 | 351.3178 | 296.0105 | 291.9537
3014.0823 | 351.212 | 295.9944 | 291.9846
3015.0823 | 351.1737 | 296.0107 | 292.0487
3016.0823 | 351.2489 | 296.0129 | 292.0882
3017.0979 | 351.101 | 296.0138 | 292.0795
3018.0823 | 350.9409 | 296.0348 | 292.1261
3019.0823 | 350.8458 | 296.0647 | 292.1196
3020.0823 | 350.8382 | 296.0712 | 292.137
3021.0823 | 350.8473 | 296.0705 | 292.1738
3022.0979 | 350.8444 | 296.0793 | 292.1855
3023.0823 | 350.9221 | 296.0881 | 292.1664
3024.0823 | 350.9086 | 296.1025 | 292.1826
3025.0823 | 350.945 | 296.0849 | 292.2178
3026.0823 | 350.9623 | 296.0853 | 292.2085
3027.0823 | 350.899 | 296.0789 | 292.1998
3028.0823 | 350.8931 | 296.0983 | 292.189
3029.0823 | 350.797 | 296.122 | 292.1512
3030.0823 | 350.7378 | 296.1307 | 292.1267
3031.0823 | 350.6933 | 296.151 | 292.1299
3032.0979 | 350.6765 | 296.1738 | 292.0794
3033.0823 | 350.6324 | 296.1887 | 292.0231
3034.0823 | 350.567 | 296.1974 | 292.0011
3035.0823 | 350.6406 | 296.2013 | 291.9875
3036.0823 | 350.77 | 296.2129 | 291.9873
3037.0823 | 350.7494 | 296.2407 | 292.0103
3038.0823 | 350.7622 | 296.2651 | 292.0269
3039.0823 | 350.7529 | 296.286 | 292.0651
3040.0823 | 350.6969 | 296.2984 | 292.0993
3041.0823 | 350.6686 | 296.2818 | 292.1378
3042.0823 | 350.7209 | 296.2885 | 292.1539
3043.0823 | 350.7518 | 296.2898 | 292.1714
3044.0823 | 350.8658 | 296.2863 | 292.1817
3045.0823 | 350.867 | 296.28 | 292.1601
3046.0823 | 350.8472 | 296.2795 | 292.1087
3047.0979 | 350.8747 | 296.2977 | 292.09
3048.0823 | 350.8105 | 296.3053 | 292.0554
3049.0823 | 350.853 | 296.2964 | 292.0578
3050.0823 | 350.791 | 296.298 | 292.0799
3051.0823 | 350.7202 | 296.3127 | 292.1166
3052.0823 | 350.6952 | 296.2842 | 292.1478
3053.0823 | 350.7144 | 296.2949 | 292.1658
3054.0823 | 350.7267 | 296.2843 | 292.1915
3055.0823 | 350.701 | 296.2729 | 292.2269
3056.0823 | 350.6927 | 296.2528 | 292.2148
3057.0979 | 350.7068 | 296.2382 | 292.1838
3058.0823 | 350.7609 | 296.2337 | 292.1537
3059.0823 | 350.7434 | 296.2171 | 292.1597
3060.0823 | 350.7262 | 296.1934 | 292.1701
3061.0979 | 350.6773 | 296.2032 | 292.1734
3062.0979 | 350.6659 | 296.2169 | 292.1908
3063.0823 | 350.7279 | 296.2223 | 292.2267
3064.0823 | 350.7133 | 296.2406 | 292.2635
3065.0823 | 350.7133 | 296.2433 | 292.304
3066.0823 | 350.7135 | 296.2446 | 292.3473
3067.0823 | 350.666 | 296.2341 | 292.381
3068.0823 | 350.678 | 296.2184 | 292.3877
3069.0823 | 350.7013 | 296.2205 | 292.3665
3070.0823 | 350.6391 | 296.2279 | 292.355
3071.0823 | 350.7101 | 296.2265 | 292.3676
3072.0823 | 350.6433 | 296.2246 | 292.3985
3073.0823 | 350.6398 | 296.2002 | 292.4541
3074.0823 | 350.7347 | 296.1674 | 292.4637
3075.0823 | 350.7694 | 296.179 | 292.478
3076.0823 | 350.872 | 296.1716 | 292.4134
3077.0823 | 350.8094 | 296.1693 | 292.3768
3078.0823 | 350.8789 | 296.1402 | 292.298
3079.0823 | 350.8705 | 296.1092 | 292.2705
3080.0823 | 350.8443 | 296.092 | 292.2322
3081.0823 | 350.8562 | 296.0732 | 292.2245
3082.0823 | 350.7856 | 296.0667 | 292.2346
3083.0823 | 350.7744 | 296.0499 | 292.2473
3084.0823 | 350.8523 | 296.0505 | 292.2638
3085.0823 | 350.9437 | 296.0643 | 292.3051
3086.0823 | 350.9915 | 296.0772 | 292.3655
3087.0823 | 351.0411 | 296.081 | 292.4071
3088.0823 | 351.1414 | 296.1026 | 292.4359
3089.0823 | 351.1708 | 296.1192 | 292.4518
3090.0823 | 351.1199 | 296.1247 | 292.4633
3091.0823 | 351.1591 | 296.1422 | 292.4053
3092.0823 | 351.0878 | 296.1588 | 292.3181
3093.0823 | 351.1133 | 296.1582 | 292.2405
3094.0823 | 351.1473 | 296.164 | 292.1884
3095.0823 | 351.0779 | 296.1594 | 292.2062
3096.0823 | 351.0521 | 296.172 | 292.2421
3097.0823 | 351.0545 | 296.1814 | 292.2455
3098.0823 | 351.0904 | 296.1854 | 292.2547
3099.0823 | 351.1764 | 296.1806 | 292.2887
3100.0823 | 351.1634 | 296.1847 | 292.2843
3101.0823 | 351.0974 | 296.1962 | 292.3075
3102.0823 | 351.0067 | 296.209 | 292.3239
3103.0823 | 351.0812 | 296.2059 | 292.3094
3104.0823 | 351.0964 | 296.2167 | 292.2928
3105.0823 | 351.061 | 296.2325 | 292.272
3106.0823 | 351.0204 | 296.2607 | 292.2931
3107.0823 | 351.0579 | 296.265 | 292.29
3108.0823 | 351.1157 | 296.2947 | 292.2879
3109.0823 | 351.0419 | 296.3091 | 292.3118
3110.0823 | 351.0116 | 296.3395 | 292.3224
3111.0823 | 351.0212 | 296.3697 | 292.3367
3112.0823 | 351.0203 | 296.3817 | 292.3107
3113.0823 | 350.9752 | 296.3969 | 292.2883
3114.0823 | 351.0151 | 296.4108 | 292.2909
3115.0823 | 351.0389 | 296.4148 | 292.2345
3116.0823 | 351.0601 | 296.4304 | 292.1694
3117.0823 | 351.108 | 296.4413 | 292.1494
3118.0823 | 351.1227 | 296.4368 | 292.1361
3119.0823 | 351.123 | 296.4544 | 292.1609
3120.0979 | 351.1905 | 296.4585 | 292.2021
3121.0823 | 351.2054 | 296.4723 | 292.2365
3122.0823 | 351.0811 | 296.4889 | 292.311
3123.0823 | 351.0324 | 296.5039 | 292.3252
3124.0823 | 350.9425 | 296.5263 | 292.3355
3125.0823 | 350.8679 | 296.5243 | 292.3121
3126.0823 | 350.902 | 296.544 | 292.2534
3127.0823 | 350.9483 | 296.5346 | 292.1852
3128.0823 | 350.863 | 296.5363 | 292.1203
3129.0823 | 350.7259 | 296.5127 | 292.1082
3130.0823 | 350.7604 | 296.5159 | 292.0929
3131.0823 | 350.7814 | 296.4945 | 292.1152
3132.0823 | 350.7281 | 296.4665 | 292.1024
3133.0823 | 350.7131 | 296.4613 | 292.0786
3134.0823 | 350.7739 | 296.4481 | 292.1002
3135.0823 | 350.7767 | 296.4237 | 292.1288
3136.0823 | 350.8064 | 296.4062 | 292.1565
3137.0823 | 350.8673 | 296.3804 | 292.2008
3138.0823 | 350.9624 | 296.3729 | 292.2555
3139.0823 | 350.9306 | 296.3798 | 292.3254
3140.0823 | 350.9107 | 296.3779 | 292.3922
3141.0823 | 350.958 | 296.3863 | 292.4126
3142.0823 | 350.9503 | 296.3953 | 292.3614
3143.0823 | 350.9571 | 296.4042 | 292.2984
3144.0823 | 350.9049 | 296.4154 | 292.2854
3145.0823 | 351.0378 | 296.4283 | 292.2999
3146.0823 | 351.0893 | 296.4415 | 292.2991
3147.0823 | 351.0876 | 296.406 | 292.3002
3148.0823 | 351.1425 | 296.3915 | 292.2978
3149.0823 | 351.2286 | 296.3776 | 292.3077
3150.0823 | 351.1693 | 296.3753 | 292.334
3151.0823 | 351.1312 | 296.3749 | 292.346
3152.0823 | 351.229 | 296.3878 | 292.3493
3153.0823 | 351.341 | 296.3866 | 292.358
3154.0823 | 351.2536 | 296.3927 | 292.3651
3155.0823 | 351.3655 | 296.4005 | 292.3884
3156.0823 | 351.3857 | 296.4255 | 292.4131
3157.0823 | 351.4247 | 296.4369 | 292.4501
3158.0823 | 351.432 | 296.4154 | 292.4595
3159.0823 | 351.4808 | 296.3974 | 292.5021
3160.0823 | 351.4984 | 296.3917 | 292.5513
3161.0823 | 351.5388 | 296.3953 | 292.5945
3162.0823 | 351.5244 | 296.3605 | 292.6526
3163.0823 | 351.4821 | 296.3518 | 292.6968
3164.0823 | 351.442 | 296.3438 | 292.7358
3165.0823 | 351.4312 | 296.3436 | 292.775
3166.0823 | 351.3618 | 296.3156 | 292.8122
3167.0979 | 351.3915 | 296.3019 | 292.8666
3168.0823 | 351.3438 | 296.3063 | 292.8983
3169.0823 | 351.3375 | 296.3034 | 292.9015
3170.0823 | 351.2753 | 296.2998 | 292.9174
3171.0823 | 351.275 | 296.2745 | 292.9191
3172.0823 | 351.2571 | 296.2983 | 292.9248
3173.0823 | 351.2758 | 296.3031 | 292.8733
3174.0823 | 351.3247 | 296.303 | 292.8056
3175.0823 | 351.3057 | 296.2998 | 292.7976
3176.0823 | 351.355 | 296.2843 | 292.7713
3177.0823 | 351.3914 | 296.2771 | 292.7504
3178.0823 | 351.3101 | 296.2702 | 292.7336
3179.0823 | 351.1384 | 296.2762 | 292.6877
3180.0823 | 351.0651 | 296.2838 | 292.691
3181.0823 | 351.0184 | 296.2915 | 292.6062
3182.0979 | 351.0545 | 296.3158 | 292.5816
3183.0979 | 351.0546 | 296.3438 | 292.6159
3184.0823 | 351.0381 | 296.3451 | 292.6462
3185.0823 | 351.0825 | 296.3423 | 292.6434
3186.0823 | 351.0685 | 296.3732 | 292.6476
3187.0979 | 351.0283 | 296.3924 | 292.6682
3188.0823 | 350.9397 | 296.3933 | 292.732
3189.0979 | 350.8904 | 296.4283 | 292.7588
3190.0823 | 350.7948 | 296.438 | 292.7438
3191.0823 | 350.8227 | 296.4258 | 292.6745
3192.0823 | 350.7618 | 296.3976 | 292.6517
3193.0823 | 350.7203 | 296.3761 | 292.6568
3194.0823 | 350.7397 | 296.3627 | 292.6551
3195.0823 | 350.7054 | 296.3486 | 292.6808
3196.0823 | 350.7358 | 296.3299 | 292.7205
3197.0979 | 350.7658 | 296.3436 | 292.7073
3198.0823 | 350.7068 | 296.3522 | 292.5918
3199.0823 | 350.6634 | 296.3393 | 292.5106
3200.0979 | 350.6808 | 296.3411 | 292.4097
3201.0823 | 350.6449 | 296.3285 | 292.3813
3202.0823 | 350.6079 | 296.3401 | 292.4074
3203.0823 | 350.5143 | 296.3608 | 292.4673
3204.0823 | 350.4326 | 296.3677 | 292.5053
3205.0823 | 350.3026 | 296.3751 | 292.5162
3206.0823 | 350.2729 | 296.3717 | 292.5274
3207.0823 | 350.28 | 296.3838 | 292.5102
3208.0823 | 350.3457 | 296.392 | 292.4697
3209.0823 | 350.4383 | 296.3834 | 292.3431
3210.0823 | 350.4651 | 296.3912 | 292.274
3211.0823 | 350.5095 | 296.4181 | 292.2357
3212.0823 | 350.563 | 296.4228 | 292.1842
3213.0823 | 350.5193 | 296.4534 | 292.1966
3214.0823 | 350.5794 | 296.4705 | 292.2303
3215.0823 | 350.5693 | 296.4925 | 292.281
3216.0823 | 350.599 | 296.5032 | 292.3274
3217.0823 | 350.6174 | 296.5241 | 292.3128
3218.0823 | 350.6961 | 296.5293 | 292.3268
3219.0823 | 350.8117 | 296.5493 | 292.3462
3220.0823 | 350.8138 | 296.5606 | 292.3787
3221.0823 | 350.9105 | 296.5795 | 292.3684
3222.0823 | 350.9277 | 296.5925 | 292.3545
3223.0823 | 350.9745 | 296.5943 | 292.3125
3224.0823 | 350.9469 | 296.6051 | 292.3217
3225.0823 | 350.9935 | 296.6026 | 292.3209
3226.0823 | 351.0293 | 296.6116 | 292.3334
3227.0823 | 351.1271 | 296.6167 | 292.3451
3228.0823 | 351.1761 | 296.6219 | 292.3935
3229.0823 | 351.2226 | 296.6217 | 292.4175
3230.0823 | 351.2527 | 296.6175 | 292.4419
3231.0823 | 351.3128 | 296.6369 | 292.3999
3232.0823 | 351.3726 | 296.6407 | 292.4153
3233.0823 | 351.2879 | 296.6429 | 292.4378
3234.0823 | 351.204 | 296.6424 | 292.4728
3235.0823 | 351.19 | 296.6407 | 292.4854
3236.0823 | 351.243 | 296.6439 | 292.4981
3237.0823 | 351.3719 | 296.641 | 292.5171
3238.0823 | 351.4181 | 296.6215 | 292.5586
3239.0823 | 351.3334 | 296.6094 | 292.5405
3240.0823 | 351.3554 | 296.6119 | 292.5167
3241.0823 | 351.3213 | 296.6231 | 292.5303
3242.0823 | 351.35 | 296.6362 | 292.5499
3243.0823 | 351.2928 | 296.6385 | 292.5927
3244.0823 | 351.2921 | 296.6494 | 292.588
3245.0823 | 351.1963 | 296.6627 | 292.5573
3246.0823 | 351.1143 | 296.6943 | 292.6267
3247.0823 | 351.1428 | 296.7032 | 292.6746
3248.0823 | 351.1324 | 296.733 | 292.6871
3249.0823 | 351.0675 | 296.7394 | 292.6922
3250.0823 | 351.0039 | 296.7573 | 292.6769
3251.0823 | 350.9795 | 296.7643 | 292.7016
3252.0823 | 350.9407 | 296.7499 | 292.7255
3253.0823 | 350.9143 | 296.7431 | 292.7207
3254.0823 | 350.9428 | 296.7386 | 292.7047
3255.0823 | 350.9221 | 296.7103 | 292.6815
3256.0823 | 350.9171 | 296.6638 | 292.6871
3257.0823 | 350.9867 | 296.6217 | 292.6306
3258.0823 | 351.0265 | 296.5576 | 292.5555
3259.0823 | 351.0174 | 296.5161 | 292.4139
3260.0823 | 351.0598 | 296.4997 | 292.3212
3261.0823 | 351.0307 | 296.5082 | 292.3428
3262.0823 | 350.9898 | 296.4817 | 292.3912
3263.0823 | 351.0286 | 296.4303 | 292.4075
3264.0823 | 351.1082 | 296.403 | 292.4014
3265.0823 | 351.1838 | 296.396 | 292.3992
3266.0823 | 351.2358 | 296.3864 | 292.4115
3267.0823 | 351.2429 | 296.3727 | 292.4133
3268.0823 | 351.1897 | 296.3287 | 292.3932
3269.0823 | 351.2054 | 296.2903 | 292.3969
3270.0823 | 351.2876 | 296.2378 | 292.4343
3271.0823 | 351.3777 | 296.2306 | 292.5133
3272.0823 | 351.5018 | 296.247 | 292.565
3273.0823 | 351.5117 | 296.2498 | 292.5824
3274.0823 | 351.5445 | 296.2413 | 292.5988
3275.0823 | 351.5768 | 296.2469 | 292.5784
3276.0823 | 351.5003 | 296.2593 | 292.5952
3277.0823 | 351.3916 | 296.2763 | 292.6158
3278.0823 | 351.4014 | 296.2772 | 292.6262
3279.0823 | 351.5752 | 296.2636 | 292.6146
3280.0823 | 351.6654 | 296.253 | 292.6495
3281.0823 | 351.7137 | 296.2463 | 292.6928
3282.0823 | 351.6032 | 296.2614 | 292.7551
3283.0823 | 351.4855 | 296.2816 | 292.7971
3284.0823 | 351.397 | 296.2988 | 292.8491
3285.0823 | 351.351 | 296.3017 | 292.8672
3286.0823 | 351.3205 | 296.3024 | 292.8658
3287.0823 | 351.2495 | 296.3093 | 292.8512
3288.0823 | 351.2052 | 296.3487 | 292.8634
3289.0823 | 351.1745 | 296.3849 | 292.9194
3290.0823 | 351.1105 | 296.4346 | 292.9521
3291.0823 | 351.2063 | 296.4852 | 292.9723
3292.0979 | 351.2351 | 296.5223 | 292.9608
3293.0823 | 351.1481 | 296.5361 | 292.9159
3294.0823 | 351.1842 | 296.5789 | 292.8457
3295.0823 | 351.1675 | 296.6003 | 292.8478
3296.0823 | 351.1599 | 296.6321 | 292.8672
3297.0823 | 351.1008 | 296.6505 | 292.9202
3298.0823 | 350.9773 | 296.6694 | 292.9236
3299.0823 | 350.895 | 296.7067 | 292.9318
3300.0979 | 350.8555 | 296.728 | 292.9295
3301.0823 | 350.95 | 296.7349 | 292.9205
3302.0823 | 350.9729 | 296.7347 | 292.9218
3303.0823 | 350.9426 | 296.7471 | 292.9056
3304.0823 | 350.9286 | 296.7573 | 292.9354
3305.0823 | 350.8343 | 296.7856 | 292.9762
3306.0823 | 350.794 | 296.7938 | 293.0167
3307.0979 | 350.8148 | 296.7925 | 293.0126
3308.0823 | 350.8109 | 296.8054 | 293.0032
3309.0823 | 350.9303 | 296.8071 | 292.9912
3310.0979 | 350.9388 | 296.8194 | 292.9403
3311.0823 | 350.912 | 296.8262 | 292.8623
3312.0823 | 350.8638 | 296.8197 | 292.8067
3313.0979 | 350.8755 | 296.8232 | 292.795
3314.0823 | 350.9299 | 296.8415 | 292.7001
3315.0823 | 350.8579 | 296.8491 | 292.6095
3316.0823 | 350.8602 | 296.8511 | 292.5723
3317.0823 | 350.8491 | 296.8014 | 292.5315
3318.0823 | 350.867 | 296.7753 | 292.4466
3319.0979 | 350.8611 | 296.7399 | 292.3854
3320.0823 | 350.7995 | 296.7039 | 292.379
3321.0979 | 350.772 | 296.6797 | 292.4366
3322.0823 | 350.7734 | 296.6667 | 292.4981
3323.0823 | 350.8389 | 296.6657 | 292.575
3324.0823 | 350.9226 | 296.6682 | 292.6506
3325.0823 | 350.9908 | 296.6652 | 292.6942
3326.0823 | 351.02 | 296.6677 | 292.7123
3327.0823 | 351.0207 | 296.6734 | 292.6838
3328.0823 | 351.1836 | 296.6855 | 292.6774
3329.0823 | 351.2565 | 296.7043 | 292.7119
3330.0979 | 351.2806 | 296.7321 | 292.7515
3331.0823 | 351.2635 | 296.748 | 292.8004
3332.0979 | 351.3764 | 296.7447 | 292.8192
3333.0823 | 351.4717 | 296.7367 | 292.7893
3334.0823 | 351.6505 | 296.7279 | 292.7841
3335.0823 | 351.6776 | 296.6898 | 292.7262
3336.0823 | 351.644 | 296.6731 | 292.7014
3337.0979 | 351.6376 | 296.6556 | 292.7035
3338.0823 | 351.6327 | 296.6435 | 292.717
3339.0823 | 351.6699 | 296.6297 | 292.7392
3340.0823 | 351.7374 | 296.6174 | 292.7517
3341.0823 | 351.7668 | 296.596 | 292.7856
3342.0823 | 351.7304 | 296.5941 | 292.7482
3343.0823 | 351.7483 | 296.6021 | 292.7244
3344.0823 | 351.6531 | 296.6118 | 292.7265
3345.0823 | 351.6629 | 296.5981 | 292.5996
3346.0823 | 351.5805 | 296.5839 | 292.4938
3347.0979 | 351.514 | 296.5595 | 292.3413
3348.0823 | 351.5342 | 296.5491 | 292.2788
3349.0823 | 351.582 | 296.5656 | 292.3152
3350.0823 | 351.5637 | 296.5811 | 292.3762
3351.0823 | 351.5688 | 296.62 | 292.4557
3352.0979 | 351.439 | 296.6553 | 292.5141
3353.0823 | 351.4415 | 296.6706 | 292.549
3354.0823 | 351.375 | 296.6662 | 292.5453
3355.0823 | 351.327 | 296.6819 | 292.5373
3356.0979 | 351.2948 | 296.6661 | 292.491
3357.0823 | 351.2196 | 296.6351 | 292.4696
3358.0823 | 351.1851 | 296.6122 | 292.4841
3359.0823 | 351.2009 | 296.6019 | 292.5091
3360.0823 | 351.2788 | 296.572 | 292.5316
3361.0823 | 351.2808 | 296.5726 | 292.5608
3362.0823 | 351.5411 | 296.5798 | 292.5829
3363.0823 | 352.6518 | 296.6016 | 292.6473
3364.0823 | 354.4286 | 296.6247 | 292.7597
3365.0823 | 356.7663 | 296.6977 | 292.9112
3366.0823 | 359.5874 | 296.7985 | 293.1046
3367.0823 | 362.7992 | 296.9033 | 293.3283
3368.0823 | 366.2335 | 297.0352 | 293.5431
3369.0823 | 369.6968 | 297.2095 | 293.8436
3370.0823 | 372.9887 | 297.422 | 294.2109
3371.0823 | 376.1153 | 297.6571 | 294.5776
3372.0823 | 378.8154 | 297.9124 | 294.8327
3373.0823 | 381.1121 | 298.1756 | 295.0213
3374.0823 | 383.1541 | 298.4418 | 295.3509
3375.0823 | 384.8847 | 298.7362 | 295.7026
3376.0823 | 386.3166 | 299.0113 | 295.9849
3377.0823 | 387.2878 | 299.2794 | 296.3094
3378.0823 | 388.1246 | 299.5826 | 296.6491
3379.0823 | 388.8223 | 299.855 | 297.0046
3380.0823 | 389.2354 | 300.1524 | 297.3365
3381.0823 | 389.4534 | 300.4401 | 297.6355
3382.0823 | 389.4745 | 300.7139 | 297.9386
3383.0823 | 389.478 | 300.984 | 298.2266
3384.0823 | 389.4228 | 301.286 | 298.4773
3385.0823 | 389.1703 | 301.5606 | 298.6702
3386.0823 | 388.8661 | 301.791 | 298.8486
3387.0823 | 388.4751 | 302.0167 | 299.0699
3388.0823 | 388.1751 | 302.2184 | 299.2905
3389.0823 | 387.9276 | 302.3857 | 299.4952
3390.0823 | 387.5406 | 302.5747 | 299.6702
3391.0823 | 387.0895 | 302.7454 | 299.8635
3392.0823 | 386.7128 | 302.9254 | 300.053
3393.0823 | 386.2468 | 303.1021 | 300.1856
3394.0823 | 385.8336 | 303.263 | 300.3218
3395.0823 | 385.2946 | 303.3944 | 300.4729
3396.0823 | 384.7371 | 303.5098 | 300.6135
3397.0823 | 384.3264 | 303.6362 | 300.7577
3398.0823 | 383.8471 | 303.7486 | 300.9162
3399.0823 | 383.3439 | 303.8407 | 301.0618
3400.0823 | 382.7588 | 303.9235 | 301.1739
3401.0823 | 382.2082 | 303.9918 | 301.2581
3402.0823 | 381.5699 | 304.0738 | 301.3696
3403.0823 | 380.994 | 304.1626 | 301.4773
3404.0823 | 380.4903 | 304.2495 | 301.5572
3405.0823 | 380.0316 | 304.3337 | 301.61
3406.0823 | 379.557 | 304.435 | 301.6808
3407.0823 | 378.9323 | 304.5141 | 301.7709
3408.0823 | 378.4065 | 304.5905 | 301.8713
3409.0823 | 377.8355 | 304.6936 | 301.8952
3410.0823 | 377.3549 | 304.7652 | 301.8995
3411.0823 | 376.8362 | 304.8628 | 301.899
3412.0823 | 376.3256 | 304.9231 | 301.9107
3413.0823 | 375.8484 | 304.9944 | 301.9123
3414.0823 | 375.4407 | 305.0694 | 301.9203
3415.0823 | 374.9978 | 305.1341 | 301.9361
3416.0979 | 374.6144 | 305.2113 | 301.9269
3417.0823 | 374.3209 | 305.2547 | 301.9237
3418.0823 | 374.008 | 305.29 | 301.9273
3419.0823 | 373.7113 | 305.3235 | 301.8925
3420.0823 | 373.4468 | 305.3748 | 301.8979
3421.0823 | 373.2926 | 305.4028 | 301.9376
3422.0823 | 373.145 | 305.4554 | 301.9602
3423.0823 | 372.9419 | 305.5072 | 302.0017
3424.0823 | 372.8097 | 305.5686 | 302.0965
3425.0823 | 372.6822 | 305.6411 | 302.1786
3426.0823 | 372.6244 | 305.6915 | 302.1931
3427.0823 | 372.6086 | 305.7303 | 302.2202
3428.0823 | 372.6304 | 305.7509 | 302.2763
3429.0823 | 372.7998 | 305.7674 | 302.3622
3430.0823 | 373.024 | 305.7924 | 302.5074
3431.0823 | 373.1971 | 305.8323 | 302.6053
3432.0823 | 373.4249 | 305.8634 | 302.6581
3433.0823 | 373.6119 | 305.9158 | 302.7126
3434.0823 | 373.7991 | 305.9674 | 302.7814
3435.0823 | 373.9428 | 306.0263 | 302.8521
3436.0823 | 374.0777 | 306.1118 | 302.9649
3437.0823 | 374.2344 | 306.1856 | 303.0599
3438.0823 | 374.4513 | 306.2579 | 303.1624
3439.0823 | 374.6677 | 306.3297 | 303.2645
3440.0823 | 374.8534 | 306.3806 | 303.3473
3441.0823 | 375.0215 | 306.4547 | 303.4635
3442.0979 | 375.2259 | 306.52 | 303.5902
3443.0823 | 375.4523 | 306.5678 | 303.6959
3444.0823 | 375.6086 | 306.6335 | 303.7821
3445.0823 | 375.6909 | 306.7287 | 303.8487
3446.0979 | 375.8206 | 306.8129 | 303.9335
3447.0823 | 375.9643 | 306.9137 | 304.0332
3448.0823 | 376.1564 | 307.0155 | 304.1309
3449.0823 | 376.3094 | 307.1229 | 304.2256
3450.0823 | 376.44 | 307.2362 | 304.3309
3451.0823 | 376.5043 | 307.346 | 304.4606
3452.0823 | 376.5461 | 307.47 | 304.6121
3453.0823 | 376.5594 | 307.5906 | 304.7252
3454.0823 | 376.677 | 307.7024 | 304.8322
3455.0823 | 376.7224 | 307.8077 | 304.9542
3456.0823 | 376.7951 | 307.8963 | 305.0415
3457.0979 | 376.9502 | 308.0137 | 305.1174
3458.0823 | 377.1169 | 308.1218 | 305.2123
3459.0823 | 377.0882 | 308.2237 | 305.2653
3460.0979 | 377.0326 | 308.3319 | 305.3107
3461.0823 | 377.1071 | 308.4289 | 305.3541
3462.0979 | 377.1776 | 308.5207 | 305.4005
3463.0823 | 377.3032 | 308.6207 | 305.4457
3464.0823 | 377.2369 | 308.7145 | 305.5154
3465.0823 | 377.245 | 308.7948 | 305.5689
3466.0823 | 377.3089 | 308.856 | 305.6449
3467.0979 | 377.2531 | 308.9326 | 305.7176
3468.0823 | 377.1859 | 309.0118 | 305.7822
3469.0823 | 377.0438 | 309.1029 | 305.8482
3470.0823 | 376.9643 | 309.1952 | 305.9355
3471.0823 | 376.8266 | 309.2818 | 306.0178
3472.0979 | 376.8322 | 309.3695 | 306.0879
3473.0823 | 376.8255 | 309.4314 | 306.1802
3474.0823 | 376.696 | 309.526 | 306.2891
3475.0823 | 376.651 | 309.611 | 306.3613
3476.0979 | 376.6862 | 309.6722 | 306.4635
3477.0823 | 376.6621 | 309.7447 | 306.5127
3478.0823 | 376.7326 | 309.8197 | 306.629
3479.0823 | 376.7091 | 309.8604 | 306.7391
3480.0823 | 376.6579 | 309.9349 | 306.7887
3481.0823 | 376.669 | 309.9823 | 306.8559
3482.0823 | 376.6145 | 310.0544 | 306.9347
3483.0823 | 376.567 | 310.129 | 307.0125
3484.0823 | 376.4851 | 310.2067 | 307.0699
3485.0823 | 376.5165 | 310.2801 | 307.1342
3486.0823 | 376.5573 | 310.3534 | 307.2069
3487.0979 | 376.5593 | 310.4387 | 307.2634
3488.0823 | 376.5427 | 310.4973 | 307.288
3489.0823 | 376.6687 | 310.5538 | 307.348
3490.0823 | 376.6603 | 310.6313 | 307.3615
3491.0823 | 376.754 | 310.7011 | 307.4041
3492.0823 | 376.8416 | 310.7698 | 307.4652
3493.0823 | 376.9421 | 310.7771 | 307.5472
3494.0823 | 377.0356 | 310.7894 | 307.6536
3495.0823 | 377.0385 | 310.8084 | 307.7204
3496.0823 | 377.1255 | 310.8391 | 307.7766
3497.0823 | 377.2573 | 310.866 | 307.8145
3498.0823 | 377.2623 | 310.9429 | 307.8671
3499.0823 | 377.2405 | 311.0041 | 307.9727
3500.0823 | 377.2093 | 311.0832 | 308.084
3501.0823 | 377.2125 | 311.1255 | 308.1591
3502.0823 | 377.1 | 311.1551 | 308.184
3503.0823 | 377.0656 | 311.2052 | 308.2493
3504.0823 | 377.0918 | 311.2543 | 308.314
3505.0823 | 377.1138 | 311.3145 | 308.3662
3506.0979 | 377.0737 | 311.3771 | 308.3823
3507.0823 | 377.2307 | 311.4582 | 308.3905
3508.0823 | 377.2514 | 311.5423 | 308.4441
3509.0823 | 377.2724 | 311.6478 | 308.5322
3510.0823 | 377.2124 | 311.7395 | 308.5705
3511.0823 | 377.2347 | 311.8108 | 308.617
3512.0823 | 377.2667 | 311.8753 | 308.7038
3513.0823 | 377.279 | 311.9296 | 308.8252
3514.0823 | 377.2884 | 312.0035 | 308.9223
3515.0823 | 377.2315 | 312.0657 | 308.9719
3516.0823 | 377.1828 | 312.1361 | 309.0197
3517.0823 | 377.2075 | 312.2199 | 309.0225
3518.0823 | 377.2237 | 312.2924 | 309.0513
3519.0823 | 377.2362 | 312.3618 | 309.0553
3520.0823 | 377.2592 | 312.4113 | 309.0782
3521.0823 | 377.2146 | 312.4542 | 309.0833
3522.0823 | 377.2193 | 312.5048 | 309.0775
3523.0823 | 377.1965 | 312.5726 | 309.1307
3524.0823 | 377.1873 | 312.6279 | 309.1226
3525.0823 | 377.1811 | 312.6793 | 309.1443
3526.0823 | 377.2619 | 312.7522 | 309.1554
3527.0823 | 377.3082 | 312.8241 | 309.2337
3528.0823 | 377.3412 | 312.8854 | 309.3459
3529.0823 | 377.3767 | 312.9498 | 309.4908
3530.0823 | 377.3564 | 312.9992 | 309.5807
3531.0823 | 377.4212 | 313.0887 | 309.6501
3532.0823 | 377.4284 | 313.1538 | 309.6684
3533.0823 | 377.3536 | 313.2191 | 309.7065
3534.0823 | 377.1791 | 313.264 | 309.7297
3535.0823 | 377.1396 | 313.3199 | 309.7883
3536.0979 | 377.1368 | 313.3592 | 309.8632
3537.0823 | 376.9833 | 313.3997 | 309.9364
3538.0823 | 376.9919 | 313.4153 | 309.9974
3539.0823 | 376.9523 | 313.4315 | 310.018
3540.0823 | 376.9406 | 313.4751 | 310.008
3541.0823 | 376.9292 | 313.4893 | 309.9542
3542.0823 | 376.9477 | 313.5187 | 309.9252
3543.0823 | 376.8919 | 313.5421 | 309.9412
3544.0823 | 376.809 | 313.5769 | 310.0101
3545.0823 | 376.6812 | 313.6286 | 310.0884
3546.0823 | 376.6505 | 313.6807 | 310.1372
3547.0823 | 376.6025 | 313.7047 | 310.1691
3548.0823 | 376.54 | 313.7424 | 310.183
3549.0823 | 376.458 | 313.7734 | 310.1975
3550.0823 | 376.4968 | 313.7896 | 310.2364
3551.0823 | 376.4985 | 313.8716 | 310.2873
3552.0823 | 376.4881 | 313.8972 | 310.3348
3553.0823 | 376.5415 | 313.9646 | 310.3607
3554.0823 | 376.5416 | 314.0091 | 310.4028
3555.0823 | 376.5415 | 314.0485 | 310.4383
3556.0823 | 376.6366 | 314.1226 | 310.4757
3557.0979 | 376.7191 | 314.1938 | 310.529
3558.0823 | 376.8547 | 314.2711 | 310.5953
3559.0823 | 376.9322 | 314.3319 | 310.6429
3560.0823 | 376.8257 | 314.4095 | 310.6907
3561.0979 | 376.8611 | 314.4698 | 310.7229
3562.0823 | 376.8646 | 314.5298 | 310.7311
3563.0823 | 376.8535 | 314.5899 | 310.7493
3564.0823 | 376.794 | 314.6486 | 310.8041
3565.0823 | 376.8627 | 314.6861 | 310.9031
3566.0979 | 376.9159 | 314.7176 | 311.0171
3567.0979 | 377.0647 | 314.728 | 311.1391
3568.0823 | 377.0158 | 314.7497 | 311.1916
3569.0823 | 376.8481 | 314.7558 | 311.2692
3570.0823 | 376.8191 | 314.7688 | 311.3439
3571.0823 | 376.8366 | 314.7996 | 311.4199
3572.0823 | 376.8397 | 314.8178 | 311.4693
3573.0823 | 376.7815 | 314.8603 | 311.4942
3574.0823 | 376.6794 | 314.9233 | 311.5177
3575.0823 | 376.5854 | 314.9713 | 311.4888
3576.0823 | 376.7001 | 315.004 | 311.4168
3577.0823 | 376.7336 | 315.0495 | 311.3772
3578.0823 | 376.7013 | 315.11 | 311.3896
3579.0823 | 376.7251 | 315.1574 | 311.4274
3580.0823 | 376.7053 | 315.1953 | 311.4482
3581.0823 | 376.5959 | 315.2339 | 311.5277
3582.0979 | 376.5195 | 315.2613 | 311.5847
3583.0823 | 376.5071 | 315.3223 | 311.6407
3584.0979 | 376.4955 | 315.3703 | 311.6873
3585.0823 | 376.5954 | 315.4095 | 311.7252
3586.0823 | 376.6826 | 315.4305 | 311.771
3587.0823 | 376.8045 | 315.4558 | 311.8151
3588.0823 | 376.8621 | 315.4554 | 311.8806
3589.0823 | 376.9014 | 315.4855 | 311.8522
3590.0823 | 376.8782 | 315.4848 | 311.7924
3591.0823 | 376.8358 | 315.4832 | 311.7272
3592.0823 | 376.7332 | 315.4978 | 311.7091
3593.0823 | 376.7051 | 315.5366 | 311.7533
3594.0823 | 376.663 | 315.5589 | 311.7798
3595.0823 | 376.7273 | 315.614 | 311.8187
3596.0979 | 376.8149 | 315.6816 | 311.9104
3597.0979 | 376.8591 | 315.7349 | 312.0271
3598.0823 | 376.8477 | 315.7688 | 312.0995
3599.0823 | 376.8817 | 315.8002 | 312.1344
3600.0823 | 376.8349 | 315.8436 | 312.1545
3601.0823 | 376.7503 | 315.8967 | 312.1812
3602.0823 | 376.7101 | 315.9367 | 312.1979
3603.0823 | 376.7837 | 315.9903 | 312.2186
3604.0823 | 376.8425 | 316.0215 | 312.2447
3605.0823 | 376.8459 | 316.0602 | 312.2894
3606.0823 | 376.9095 | 316.0848 | 312.3429
3607.0979 | 376.916 | 316.1115 | 312.3866
3608.0823 | 376.9262 | 316.1132 | 312.3957
3609.0823 | 376.9695 | 316.1144 | 312.4554
3610.0823 | 376.9568 | 316.0982 | 312.4866
3611.0823 | 376.9526 | 316.1066 | 312.529
3612.0979 | 376.947 | 316.1416 | 312.6164
3613.0823 | 376.8818 | 316.1755 | 312.6873
3614.0823 | 376.9397 | 316.2357 | 312.7544
3615.0823 | 376.8545 | 316.2926 | 312.8219
3616.0823 | 376.7932 | 316.3455 | 312.8492
3617.0823 | 376.7606 | 316.4038 | 312.8482
3618.0823 | 376.8626 | 316.4298 | 312.7842
3619.0823 | 376.9071 | 316.4283 | 312.7597
3620.0823 | 377.0071 | 316.4674 | 312.8087
3621.0823 | 377.0652 | 316.5114 | 312.8417
3622.0979 | 376.9265 | 316.5518 | 312.8688
3623.0823 | 376.866 | 316.5956 | 312.8591
3624.0823 | 376.8842 | 316.6273 | 312.8443
3625.0823 | 376.8869 | 316.6578 | 312.8587
3626.0979 | 376.8824 | 316.6859 | 312.9176
3627.0979 | 376.8162 | 316.7382 | 312.9698
3628.0823 | 376.7273 | 316.7923 | 313.0404
3629.0823 | 376.655 | 316.8501 | 313.0707
3630.0823 | 376.6875 | 316.8804 | 313.0933
3631.0823 | 376.6703 | 316.93 | 313.0902
3632.0823 | 376.6893 | 316.9701 | 313.0414
3633.0823 | 376.7162 | 317.0186 | 313.0787
3634.0823 | 376.6944 | 317.0625 | 313.1449
3635.0823 | 376.6946 | 317.1067 | 313.2132
3636.0823 | 376.7102 | 317.1604 | 313.2089
3637.0823 | 376.5993 | 317.2031 | 313.2611
3638.0823 | 376.6188 | 317.233 | 313.2859
3639.0823 | 376.6937 | 317.2504 | 313.3054
3640.0823 | 376.7113 | 317.2529 | 313.2573
3641.0823 | 376.7648 | 317.2386 | 313.2414
3642.0823 | 376.7408 | 317.2532 | 313.3044
3643.0823 | 376.6579 | 317.2836 | 313.3942
3644.0823 | 376.6722 | 317.3229 | 313.4938
3645.0823 | 376.7029 | 317.3613 | 313.6209
3646.0823 | 376.6693 | 317.405 | 313.7209
3647.0823 | 376.6376 | 317.4419 | 313.7958
3648.0823 | 376.6724 | 317.4686 | 313.8801
3649.0823 | 376.7763 | 317.5251 | 313.9249
3650.0823 | 376.7568 | 317.5902 | 313.9639
3651.0823 | 376.6285 | 317.641 | 314.0212
3652.0823 | 376.6029 | 317.6868 | 314.0854
3653.0823 | 376.6377 | 317.7169 | 314.1655
3654.0823 | 376.6212 | 317.7586 | 314.2189
3655.0823 | 376.5469 | 317.803 | 314.2338
3656.0823 | 376.5855 | 317.8519 | 314.2681
3657.0823 | 376.5811 | 317.8671 | 314.3198
3658.0823 | 376.6124 | 317.8939 | 314.3821
3659.0823 | 376.621 | 317.9306 | 314.3613
3660.0823 | 376.7309 | 317.9549 | 314.3751
3661.0823 | 376.7112 | 317.985 | 314.3933
3662.0823 | 376.7506 | 317.9686 | 314.3876
3663.0823 | 376.7693 | 317.9726 | 314.4306
3664.0823 | 376.7628 | 317.9716 | 314.486
3665.0823 | 376.7972 | 317.9982 | 314.5174
3666.0823 | 376.9091 | 318.0311 | 314.5517
3667.0979 | 377.0435 | 318.065 | 314.5632
3668.0823 | 377.0507 | 318.097 | 314.6003
3669.0823 | 377.028 | 318.1229 | 314.655
3670.0823 | 377.0634 | 318.1364 | 314.7116
3671.0979 | 377.0493 | 318.1592 | 314.7377
3672.0823 | 377.0034 | 318.1837 | 314.7782
3673.0823 | 377.115 | 318.2143 | 314.8066
3674.0823 | 377.1014 | 318.2568 | 314.7865
3675.0823 | 377.1212 | 318.2847 | 314.7854
3676.0823 | 377.0997 | 318.3254 | 314.8222
3677.0823 | 377.0702 | 318.3563 | 314.882
3678.0823 | 377.0576 | 318.4093 | 314.9248
3679.0823 | 376.9786 | 318.4469 | 314.9908
3680.0823 | 376.8838 | 318.4851 | 315.0439
3681.0823 | 376.8552 | 318.4999 | 315.0853
3682.0823 | 376.8432 | 318.5129 | 315.0724
3683.0823 | 376.8461 | 318.5146 | 315.1163
3684.0823 | 376.8295 | 318.5371 | 315.1745
3685.0823 | 376.7974 | 318.5578 | 315.2127
3686.0979 | 376.8081 | 318.5741 | 315.231
3687.0823 | 376.8069 | 318.5682 | 315.2444
3688.0823 | 376.7498 | 318.5733 | 315.2579
3689.0823 | 376.687 | 318.5639 | 315.2765
3690.0823 | 376.7581 | 318.5716 | 315.3135
3691.0823 | 376.8251 | 318.6092 | 315.332
3692.0823 | 376.8981 | 318.5911 | 315.3542
3693.0823 | 376.9201 | 318.6005 | 315.3723
3694.0823 | 376.9523 | 318.6277 | 315.4458
3695.0823 | 376.9972 | 318.6408 | 315.5005
3696.0823 | 376.9304 | 318.6661 | 315.5053
3697.0823 | 376.8143 | 318.6831 | 315.4994
3698.0823 | 376.8139 | 318.7272 | 315.5077
3699.0823 | 376.8416 | 318.7592 | 315.5288
3700.0823 | 376.8472 | 318.7905 | 315.5427
3701.0823 | 376.9152 | 318.8173 | 315.5081
3702.0823 | 376.8462 | 318.8625 | 315.5129
3703.0823 | 376.8896 | 318.9009 | 315.5574
3704.0823 | 376.9296 | 318.9428 | 315.5895
3705.0823 | 376.9472 | 318.9939 | 315.637
3706.0823 | 376.8818 | 319.037 | 315.693
3707.0823 | 376.9132 | 319.0523 | 315.7539
3708.0823 | 376.9511 | 319.0903 | 315.7447
3709.0823 | 377.0078 | 319.1236 | 315.7368
3710.0823 | 377.1122 | 319.1521 | 315.7832
3711.0823 | 377.0581 | 319.1808 | 315.8097
3712.0823 | 376.9675 | 319.2021 | 315.8039
3713.0823 | 376.8928 | 319.213 | 315.8119
3714.0823 | 376.8697 | 319.2352 | 315.8268
3715.0823 | 376.8737 | 319.2589 | 315.8175
3716.0823 | 376.8471 | 319.2958 | 315.8162
3717.0979 | 376.9301 | 319.3289 | 315.8118
3718.0823 | 376.9146 | 319.3677 | 315.8285
3719.0823 | 376.9706 | 319.4014 | 315.8488
3720.0823 | 376.9804 | 319.4527 | 315.7663
3721.0823 | 376.8921 | 319.4716 | 315.6064
3722.0823 | 376.9065 | 319.5045 | 315.5501
3723.0823 | 376.9208 | 319.5342 | 315.5792
3724.0823 | 376.9017 | 319.5979 | 315.6533
3725.0823 | 376.9195 | 319.6356 | 315.7318
3726.0823 | 376.9212 | 319.6631 | 315.7802
3727.0823 | 376.9189 | 319.7028 | 315.8765
3728.0823 | 376.9405 | 319.736 | 315.9328
3729.0823 | 376.931 | 319.7726 | 315.9768
3730.0823 | 376.955 | 319.7974 | 315.9925
3731.0979 | 376.9225 | 319.8245 | 316.0121
3732.0979 | 376.924 | 319.8369 | 316.033
3733.0823 | 376.857 | 319.8848 | 316.0474
3734.0823 | 376.7775 | 319.9179 | 316.0891
3735.0823 | 376.7591 | 319.9567 | 316.121
3736.0823 | 376.8038 | 319.9919 | 316.0834
3737.0979 | 376.7736 | 320.013 | 316.0518
3738.0823 | 376.7042 | 320.0334 | 316.0627
3739.0823 | 376.6506 | 320.0405 | 316.0585
3740.0823 | 376.7061 | 320.0686 | 316.094
3741.0823 | 376.7465 | 320.0837 | 316.1487
3742.0823 | 376.7765 | 320.1132 | 316.1538
3743.0823 | 376.7055 | 320.1286 | 316.1678
3744.0823 | 376.7754 | 320.1337 | 316.1619
3745.0823 | 376.7935 | 320.1339 | 316.1445
3746.0823 | 376.8052 | 320.1192 | 316.1985
3747.0979 | 376.7775 | 320.1173 | 316.2578
3748.0823 | 376.7335 | 320.1165 | 316.2212
3749.0823 | 376.7285 | 320.142 | 316.197
3750.0823 | 376.7943 | 320.1512 | 316.2094
3751.0823 | 376.7186 | 320.1565 | 316.1792
3752.0823 | 376.6437 | 320.1572 | 316.2053
3753.0823 | 376.6528 | 320.167 | 316.2571
3754.0823 | 376.7331 | 320.1925 | 316.3129
3755.0823 | 376.7224 | 320.209 | 316.387
3756.0823 | 376.7385 | 320.216 | 316.4197
3757.0823 | 376.7222 | 320.2199 | 316.4596
3758.0823 | 376.7976 | 320.2284 | 316.467
3759.0823 | 376.8135 | 320.2464 | 316.5072
3760.0823 | 376.72 | 320.2631 | 316.4795
3761.0823 | 376.6139 | 320.2722 | 316.4325
3762.0979 | 376.5638 | 320.2935 | 316.3326
3763.0823 | 376.4447 | 320.3236 | 316.3279
3764.0823 | 376.4024 | 320.3461 | 316.3436
3765.0823 | 376.4339 | 320.3333 | 316.3832
3766.0823 | 376.4445 | 320.3309 | 316.4372
3767.0823 | 376.3246 | 320.3235 | 316.4895
3768.0979 | 376.2239 | 320.3245 | 316.5291
3769.0823 | 376.2098 | 320.3273 | 316.5201
3770.0823 | 376.2278 | 320.3378 | 316.5288
3771.0823 | 376.3161 | 320.3588 | 316.5091
3772.0823 | 376.3355 | 320.3564 | 316.4421
3773.0823 | 376.3325 | 320.3461 | 316.4249
3774.0823 | 376.2713 | 320.3227 | 316.4359
3775.0823 | 376.3173 | 320.3267 | 316.4655
3776.0823 | 376.4286 | 320.3253 | 316.493
3777.0823 | 376.4517 | 320.3208 | 316.4768
3778.0823 | 376.4406 | 320.3229 | 316.4456
3779.0823 | 376.4875 | 320.2852 | 316.429
3780.0823 | 376.4029 | 320.2587 | 316.443
3781.0823 | 376.343 | 320.238 | 316.4672
3782.0823 | 376.3159 | 320.217 | 316.5181
3783.0823 | 376.4369 | 320.2189 | 316.561
3784.0823 | 376.4886 | 320.2275 | 316.5781
3785.0823 | 376.3706 | 320.2516 | 316.5845
3786.0823 | 376.3412 | 320.2957 | 316.6289
3787.0823 | 376.4574 | 320.3261 | 316.6327
3788.0823 | 376.4799 | 320.3478 | 316.6524
3789.0823 | 376.4429 | 320.3828 | 316.6774
3790.0823 | 376.3358 | 320.416 | 316.6575
3791.0823 | 376.3786 | 320.4483 | 316.6101
3792.0823 | 376.4302 | 320.4923 | 316.503
3793.0823 | 376.5096 | 320.5064 | 316.4015
3794.0823 | 376.4835 | 320.5588 | 316.3843
3795.0823 | 376.4904 | 320.5856 | 316.4154
3796.0823 | 376.4915 | 320.6282 | 316.4913
3797.0823 | 376.5355 | 320.682 | 316.5738
3798.0823 | 376.5893 | 320.6946 | 316.6544
3799.0823 | 376.6795 | 320.6979 | 316.6957
3800.0823 | 376.7727 | 320.6949 | 316.6865
3801.0823 | 376.8495 | 320.7005 | 316.6734
3802.0823 | 376.9166 | 320.722 | 316.7313
3803.0823 | 376.9052 | 320.7224 | 316.8087
3804.0823 | 376.8829 | 320.7536 | 316.8839
3805.0823 | 376.8898 | 320.7735 | 316.9212
3806.0823 | 376.9318 | 320.7696 | 316.9915
3807.0823 | 377.0189 | 320.763 | 317.0433
3808.0823 | 377.0414 | 320.7738 | 317.0752
3809.0823 | 377.1048 | 320.7177 | 317.1228
3810.0823 | 377.1608 | 320.6633 | 317.1672
3811.0823 | 377.0851 | 320.5859 | 317.1796
3812.0823 | 377.0508 | 320.5395 | 317.1881
3813.0823 | 377.0227 | 320.5093 | 317.1949
3814.0823 | 377.0079 | 320.4549 | 317.2101
3815.0823 | 376.9445 | 320.4091 | 317.2164
3816.0823 | 376.8965 | 320.3708 | 317.2652
3817.0823 | 376.8844 | 320.3409 | 317.227
3818.0823 | 376.8313 | 320.3461 | 317.1855
3819.0823 | 376.7873 | 320.3418 | 317.191
3820.0979 | 376.7865 | 320.3534 | 317.1999