## Test Conditions
DESIREE-FIRE Test Number 29 - Circuit Simulator Data Only
Test Date: | 2009-07-29
DCSim DAQ Start Time | 11:38
DCSim Time for Synchronization | 11:47
Heat Source Synchronization | 5:25 | minutes:seconds
Heat Source DAQ Start Time | 11:42
Heat Source Start Time | 11:49
DCSim Offset | 0:11 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 641 | seconds
Heat Source Offset | 0:07 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 418 | seconds
Heat Source Stop Time | 13:26
Test Duration | 1:37 | minutes:seconds
| 5820 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | Tefzel/Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | Tefzel/Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.23438 | 123.2025 | -60.8551 | 61.9766 | -0.24818 | -0.0039434 | 0.0019013 | 0.0028476 | 0.0663 | -0.00052335 | 0.068906 | -60.9421 | 61.9034 | -60.9741 | -61.0062 | 61.9537 | 0.14648 | -0.036621 | 0.21057 | 61.9354 | -61.0474 | -0.11902 | -0.073243 | -0.086975 | -0.15106 | -0.022889 | -0.19226 | -0.041199 | 0.032043 | 60.8185 | 61.0657 | 122.8088 | 122.7585 | -0.086975 | 122.7905 | 61.0016 | -0.19226 | 122.7585 | -0.086975 | 61.0016 | 122.8088 | 122.7905 | -122.9507 | -123.024
0.76562 | 123.1796 | -60.878 | 61.9675 | 0.056992 | -0.0026618 | 0.00061946 | -0.00014316 | 0.065018 | -0.0026595 | 0.067197 | -61.0245 | 61.9171 | -61.0062 | -61.0886 | 61.8805 | 0.091553 | -0.064087 | 0.13733 | 61.8896 | -61.0474 | -0.12817 | -0.050354 | -0.14648 | -0.21057 | -0.086975 | -0.16937 | -0.07782 | -0.01831 | 60.8139 | 61.0153 | 122.7585 | 122.7951 | -0.14648 | 122.7676 | 60.9695 | -0.16937 | 122.7951 | -0.14648 | 60.9695 | 122.7585 | 122.7676 | -122.9736 | -123.0148
1.7656 | 123.1796 | -60.8963 | 61.9812 | 0.049362 | -0.0039434 | -0.0015167 | 0.00071144 | 0.065018 | -0.0022323 | 0.068693 | -61.0336 | 61.9034 | -61.0062 | -61.0931 | 61.8622 | 0.086975 | -0.050354 | 0.12817 | 61.9034 | -61.0565 | -0.10986 | -0.07782 | -0.13733 | -0.19684 | -0.11902 | -0.16022 | -0.07782 | -0.027465 | 60.8459 | 61.0245 | 122.7585 | 122.7997 | -0.13733 | 122.7997 | 60.9833 | -0.16022 | 122.7997 | -0.13733 | 60.9833 | 122.7585 | 122.7997 | -122.9874 | -123.0377
2.7812 | 123.0881 | -60.91 | 62.0224 | 0.10277 | -0.003089 | 0.0010467 | 0.0015658 | 0.064591 | -0.00073695 | 0.068479 | -60.9192 | 61.9675 | -61.0199 | -61.0977 | 61.8347 | 0.064087 | 0.10986 | 0.11444 | 61.94 | -61.1023 | -0.10986 | -0.054932 | -0.009155 | -0.18768 | -0.18768 | -0.19226 | -0.082398 | 0.10071 | 61.0199 | 61.0245 | 122.7448 | 122.8775 | -0.009155 | 122.85 | 60.9741 | -0.19226 | 122.8775 | -0.009155 | 60.9741 | 122.7448 | 122.85 | -123.0423 | -123.1247
3.7656 | 123.1888 | -60.9055 | 61.9583 | -0.034561 | -0.003089 | 0.0012605 | 0.00049764 | 0.064805 | -0.0024459 | 0.068265 | -61.0245 | 61.8988 | -61.0199 | -61.0703 | 61.8622 | 0.10529 | -0.07782 | 0.16479 | 61.9217 | -61.0428 | -0.11444 | -0.059509 | -0.11902 | -0.16479 | -0.09613 | -0.13733 | -0.036621 | -0.004578 | 60.8276 | 61.0703 | 122.7676 | 122.8043 | -0.11902 | 122.8271 | 61.0107 | -0.13733 | 122.8043 | -0.11902 | 61.0107 | 122.7676 | 122.8271 | -122.9782 | -123.0011
4.7656 | 123.2117 | -60.8688 | 61.9766 | -0.04982 | -0.0045844 | -2.1336e-05 | 0.00071144 | 0.063523 | -0.0020187 | 0.067838 | -60.9879 | 61.9034 | -60.9924 | -61.0428 | 61.9263 | 0.15564 | -0.086975 | 0.20599 | 61.8942 | -61.0336 | -0.1236 | -0.073243 | -0.11902 | -0.17395 | -0.050354 | -0.1648 | -0.082398 | 0.004578 | 60.7819 | 61.0748 | 122.7951 | 122.7722 | -0.11902 | 122.7631 | 61.0245 | -0.1648 | 122.7722 | -0.11902 | 61.0245 | 122.7951 | 122.7631 | -122.9691 | -123.0103
5.7656 | 123.2208 | -60.8643 | 61.9858 | -0.019302 | -0.0037298 | 0.00061946 | 0.001993 | 0.066087 | -0.0030869 | 0.066984 | -60.997 | 61.9125 | -61.0016 | -61.0611 | 61.9034 | 0.13275 | -0.064087 | 0.17395 | 61.9217 | -61.0107 | -0.13733 | -0.073242 | -0.13275 | -0.19684 | -0.082398 | -0.14648 | -0.064087 | 0.004578 | 60.8002 | 61.0382 | 122.7676 | 122.7768 | -0.13275 | 122.7859 | 60.997 | -0.14648 | 122.7768 | -0.13275 | 60.997 | 122.7676 | 122.7859 | -122.9874 | -122.9965
6.7656 | 123.2162 | -60.8917 | 61.9629 | -0.057449 | -0.005866 | -0.0032257 | -0.0012112 | 0.063737 | -0.0022323 | 0.069547 | -61.0245 | 61.9217 | -60.997 | -61.0703 | 61.8896 | 0.09613 | -0.050354 | 0.15106 | 61.8805 | -61.0428 | -0.10528 | -0.041199 | -0.13275 | -0.17853 | -0.073243 | -0.15106 | -0.082398 | -0.027466 | 60.8414 | 61.0428 | 122.7814 | 122.8134 | -0.13275 | 122.7722 | 60.9879 | -0.15106 | 122.8134 | -0.13275 | 60.9879 | 122.7814 | 122.7722 | -122.9599 | -123.0057
7.7812 | 123.0698 | -60.9375 | 61.972 | 0.064621 | -0.003089 | -0.00023494 | 0.0069064 | 0.066941 | -0.0013779 | 0.067411 | -61.0336 | 62.0132 | -60.997 | -61.1252 | 61.8027 | -0.009155 | 0.018311 | 0.004578 | 61.9492 | -61.116 | -0.059509 | 0.041199 | -0.09613 | -0.18768 | -0.16937 | -0.17853 | -0.022888 | -0.036621 | 60.9558 | 60.9421 | 122.7402 | 122.9507 | -0.09613 | 122.8867 | 60.9283 | -0.17853 | 122.9507 | -0.09613 | 60.9283 | 122.7402 | 122.8867 | -122.9691 | -123.0881
8.7656 | 123.1613 | -60.8917 | 61.94 | 0.14092 | -0.0050116 | 0.0010467 | 0.00049764 | 0.066727 | -0.0033005 | 0.070188 | -61.0474 | 61.908 | -61.0336 | -61.116 | 61.853 | 0.032043 | -0.064087 | 0.068665 | 61.9171 | -61.0474 | -0.14191 | -0.032043 | -0.15564 | -0.2243 | -0.086975 | -0.15564 | -0.022888 | -0.013733 | 60.8276 | 60.9604 | 122.7448 | 122.7997 | -0.15564 | 122.8088 | 60.9238 | -0.15564 | 122.7997 | -0.15564 | 60.9238 | 122.7448 | 122.8088 | -122.9736 | -122.9874
9.7656 | 123.1842 | -60.8963 | 61.972 | 0.13329 | -0.0039434 | -0.0025847 | -0.00057036 | 0.066087 | -0.00073695 | 0.069547 | -61.0382 | 61.8988 | -61.0291 | -61.1206 | 61.8484 | 0.050354 | -0.041199 | 0.068665 | 61.9263 | -61.0657 | -0.13275 | -0.073242 | -0.14191 | -0.2243 | -0.1236 | -0.16937 | -0.045776 | -0.009155 | 60.8551 | 60.965 | 122.7448 | 122.7951 | -0.14191 | 122.8226 | 60.9467 | -0.16937 | 122.7951 | -0.14191 | 60.9467 | 122.7448 | 122.8226 | -123.0011 | -123.0377
10.7656 | 123.1659 | -60.91 | 61.9858 | 0.13329 | -0.0022346 | -0.0051483 | -0.00099756 | 0.063309 | 0.00011745 | 0.069333 | -61.0565 | 61.9171 | -61.0153 | -61.1206 | 61.8347 | 0.041199 | -0.07782 | 0.059509 | 61.8942 | -61.0794 | -0.10529 | -0.068665 | -0.14648 | -0.21057 | -0.15106 | -0.16937 | -0.091553 | -0.041199 | 60.8322 | 60.9695 | 122.7448 | 122.8271 | -0.14648 | 122.8043 | 60.9512 | -0.16937 | 122.8271 | -0.14648 | 60.9512 | 122.7448 | 122.8043 | -123.0011 | -123.0652
11.7656 | 123.1705 | -60.9009 | 61.9766 | 0.11803 | -0.0028754 | 0.0046783 | -0.00035676 | 0.063309 | -0.0035141 | 0.068693 | -61.0565 | 61.9034 | -61.0016 | -61.1023 | 61.8484 | 0.064087 | -0.054932 | 0.10071 | 61.9034 | -61.0382 | -0.10071 | -0.073243 | -0.15564 | -0.20142 | -0.12817 | -0.13733 | -0.073243 | -0.054932 | 60.8459 | 61.0016 | 122.7493 | 122.8043 | -0.15564 | 122.8043 | 60.965 | -0.13733 | 122.8043 | -0.15564 | 60.965 | 122.7493 | 122.8043 | -122.9782 | -123.0148
12.7812 | 123.143 | -60.8963 | 62.0178 | -0.095596 | -0.0020208 | 0.0040375 | 0.00712 | 0.063737 | -0.0058639 | 0.068693 | -61.0153 | 62.0316 | -60.9924 | -61.084 | 61.853 | 0.082397 | 0.086975 | 0.09613 | 61.94 | -61.0886 | -0.096131 | 0.013733 | -0.11902 | -0.18768 | -0.1648 | -0.19226 | -0.07782 | -0.022888 | 60.9833 | 60.9924 | 122.7493 | 122.9279 | -0.11902 | 122.8363 | 60.9787 | -0.19226 | 122.9279 | -0.11902 | 60.9787 | 122.7493 | 122.8363 | -123.0103 | -123.1064
13.7656 | 123.1613 | -60.8871 | 61.9675 | 0.12566 | -0.0041572 | 0.00083306 | -0.00035676 | 0.065873 | -0.00073695 | 0.070402 | -61.0611 | 61.8805 | -61.0199 | -61.1252 | 61.8393 | 0.050354 | -0.059509 | 0.068665 | 61.9263 | -61.0382 | -0.13275 | -0.086975 | -0.17395 | -0.23804 | -0.12817 | -0.15106 | -0.041198 | -0.041199 | 60.8276 | 60.9558 | 122.7264 | 122.7676 | -0.17395 | 122.8134 | 60.9375 | -0.15106 | 122.7676 | -0.17395 | 60.9375 | 122.7264 | 122.8134 | -122.9874 | -123.0057
14.7656 | 123.1705 | -60.9055 | 61.9263 | 0.20195 | -0.003089 | 0.00083306 | 0.00092504 | 0.065446 | -0.0035141 | 0.069761 | -61.0153 | 61.8988 | -61.0336 | -61.1023 | 61.8713 | 0.059509 | -0.16479 | 0.073242 | 61.8851 | -61.0611 | -0.12817 | -0.027466 | -0.10986 | -0.19684 | -0.054932 | -0.15564 | -0.041199 | 0.01831 | 60.7407 | 60.9787 | 122.7768 | 122.8043 | -0.10986 | 122.7905 | 60.965 | -0.15564 | 122.8043 | -0.10986 | 60.965 | 122.7768 | 122.7905 | -122.9599 | -122.9874
15.7656 | 123.23 | -60.8643 | 61.972 | 0.25536 | -0.0028754 | 0.0016877 | 0.002634 | 0.066941 | -0.0030869 | 0.068906 | -61.0016 | 61.9034 | -61.0336 | -61.0794 | 61.8713 | 0.068665 | -0.16937 | 0.082397 | 61.8713 | -61.0611 | -0.16937 | -0.068665 | -0.13733 | -0.21515 | -0.10071 | -0.19684 | -0.10071 | 0.032043 | 60.6949 | 60.9467 | 122.7356 | 122.7676 | -0.13733 | 122.7356 | 60.9329 | -0.19684 | 122.7676 | -0.13733 | 60.9329 | 122.7356 | 122.7356 | -123.0057 | -123.0331
16.7656 | 123.1476 | -60.9192 | 61.9308 | 0.10277 | -0.0015936 | 0.0012605 | 0.0022066 | 0.066727 | -0.0022323 | 0.068052 | -61.0336 | 61.908 | -61.0291 | -61.1069 | 61.8484 | 0.054932 | -0.12817 | 0.059509 | 61.8805 | -61.0703 | -0.10986 | -0.022888 | -0.11444 | -0.18768 | -0.082397 | -0.15106 | -0.050354 | -0.004577 | 60.791 | 60.9787 | 122.7676 | 122.8271 | -0.11444 | 122.7997 | 60.9741 | -0.15106 | 122.8271 | -0.11444 | 60.9741 | 122.7676 | 122.7997 | -122.9599 | -123.0011
17.7656 | 123.1705 | -60.8917 | 61.9629 | 0.23247 | -0.0026618 | 0.00061946 | 0.002634 | 0.065446 | -0.0011643 | 0.067411 | -61.0062 | 61.8851 | -60.997 | -61.116 | 61.8622 | 0.068665 | -0.16937 | 0.073242 | 61.8988 | -61.0657 | -0.10528 | -0.07782 | -0.11444 | -0.2243 | -0.10071 | -0.17395 | -0.064087 | -0.009156 | 60.7224 | 60.965 | 122.7539 | 122.7768 | -0.11444 | 122.7905 | 60.9604 | -0.17395 | 122.7768 | -0.11444 | 60.9604 | 122.7539 | 122.7905 | -122.9599 | -123.0286
18.7656 | 123.1476 | -60.9055 | 61.9629 | 0.18669 | -0.0035162 | -0.0027985 | 0.00028404 | 0.063523 | -0.0030869 | 0.069974 | -61.0428 | 61.8942 | -61.0062 | -61.1252 | 61.8484 | 0.036621 | -0.09613 | 0.059509 | 61.9217 | -61.0703 | -0.10071 | -0.068665 | -0.13733 | -0.21973 | -0.11444 | -0.16479 | -0.041199 | -0.036621 | 60.8093 | 60.965 | 122.7539 | 122.7997 | -0.13733 | 122.8271 | 60.9421 | -0.16479 | 122.7997 | -0.13733 | 60.9421 | 122.7539 | 122.8271 | -122.9691 | -123.0331
19.7656 | 123.1659 | -60.8963 | 61.9629 | 0.26299 | -0.0033026 | 0.0010467 | 0.0030612 | 0.065018 | -0.0035141 | 0.068906 | -61.0107 | 61.8942 | -61.0107 | -61.1069 | 61.8622 | 0.041199 | -0.1236 | 0.064087 | 61.8851 | -61.0519 | -0.11444 | -0.068665 | -0.11444 | -0.21057 | -0.10071 | -0.15564 | -0.07782 | 0 | 60.7727 | 60.9604 | 122.7585 | 122.7905 | -0.11444 | 122.7814 | 60.9375 | -0.15564 | 122.7905 | -0.11444 | 60.9375 | 122.7585 | 122.7814 | -122.9736 | -123.0148
20.7656 | 123.1934 | -60.91 | 61.9583 | 0.20195 | -0.0041572 | 0.0040375 | 0.00092504 | 0.063523 | -0.0028731 | 0.068052 | -60.9741 | 61.8759 | -61.0107 | -61.0931 | 61.853 | 0.036621 | -0.16479 | 0.086975 | 61.8805 | -61.0703 | -0.10071 | -0.082397 | -0.064087 | -0.18311 | -0.10529 | -0.16022 | -0.07782 | 0.036621 | 60.7452 | 60.997 | 122.7631 | 122.7859 | -0.064087 | 122.7905 | 60.9467 | -0.16022 | 122.7859 | -0.064087 | 60.9467 | 122.7631 | 122.7905 | -122.9691 | -123.0286
21.7656 | 123.2117 | -60.878 | 61.9263 | 0.27061 | -0.0033026 | -0.00066214 | 0.0030612 | 0.064378 | -0.0047957 | 0.06912 | -60.9833 | 61.8805 | -61.0107 | -61.0703 | 61.8851 | 0.064087 | -0.18768 | 0.091553 | 61.8988 | -61.0611 | -0.13275 | -0.045777 | -0.10528 | -0.19226 | -0.041199 | -0.1831 | -0.027466 | 0.027466 | 60.6903 | 60.9695 | 122.7631 | 122.7585 | -0.10528 | 122.7768 | 60.9421 | -0.1831 | 122.7585 | -0.10528 | 60.9421 | 122.7631 | 122.7768 | -122.937 | -122.9874
22.7656 | 123.1888 | -60.8826 | 61.94 | 0.2401 | -0.0037298 | 0.0025421 | 0.0039156 | 0.067155 | -0.0035141 | 0.068265 | -60.9833 | 61.9263 | -61.0107 | -61.0748 | 61.8759 | 0.073242 | -0.17395 | 0.07782 | 61.8484 | -61.084 | -0.12817 | -0.013732 | -0.10071 | -0.19226 | -0.064086 | -0.20142 | -0.091552 | 0.027466 | 60.7086 | 60.9604 | 122.7585 | 122.8088 | -0.10071 | 122.731 | 60.9558 | -0.20142 | 122.8088 | -0.10071 | 60.9558 | 122.7585 | 122.731 | -122.9507 | -123.024
23.7656 | 123.2254 | -60.9009 | 61.9354 | 0.27061 | -0.0011664 | -0.0015167 | 0.00092504 | 0.068009 | -0.0030869 | 0.070188 | -60.9924 | 61.8851 | -60.997 | -61.0794 | 61.8896 | 0.054932 | -0.16937 | 0.082397 | 61.8713 | -61.084 | -0.09613 | -0.050354 | -0.091553 | -0.17853 | -0.045777 | -0.1831 | -0.064087 | 0.004577 | 60.7315 | 60.9833 | 122.7905 | 122.786 | -0.091553 | 122.7722 | 60.9558 | -0.1831 | 122.786 | -0.091553 | 60.9558 | 122.7905 | 122.7722 | -122.9324 | -123.0194
24.7656 | 123.1934 | -60.8963 | 61.9308 | 0.27824 | -0.0037298 | 0.0031831 | 0.0022066 | 0.064378 | -0.00073695 | 0.067838 | -60.9879 | 61.9446 | -61.0062 | -61.0794 | 61.8805 | 0.054932 | -0.17395 | 0.086975 | 61.8942 | -61.1023 | -0.10986 | 0.013733 | -0.091553 | -0.18311 | -0.050354 | -0.20599 | -0.036621 | 0.018311 | 60.7224 | 60.9833 | 122.7768 | 122.8409 | -0.091553 | 122.7905 | 60.9512 | -0.20599 | 122.8409 | -0.091553 | 60.9512 | 122.7768 | 122.7905 | -122.937 | -123.0331
25.7656 | 123.175 | -60.9238 | 61.9263 | 0.2401 | -0.003089 | 0.00040586 | 0.00071144 | 0.065873 | -0.0045821 | 0.069974 | -61.0062 | 61.9217 | -61.0199 | -61.0931 | 61.9354 | 0.11902 | -0.15564 | 0.068665 | 61.8851 | -61.0794 | -0.09613 | -0.004578 | -0.082398 | -0.16937 | 0.009155 | -0.15564 | -0.041199 | 0.013732 | 60.7681 | 60.9924 | 122.8592 | 122.8455 | -0.082398 | 122.8088 | 61.0428 | -0.15564 | 122.8455 | -0.082398 | 61.0428 | 122.8592 | 122.8088 | -122.9462 | -123.0057
26.7656 | 123.2071 | -60.8917 | 61.94 | 0.23247 | -0.004798 | -0.00023494 | 0.0013522 | 0.064805 | -0.0030869 | 0.068693 | -60.9924 | 61.9171 | -61.0062 | -61.0703 | 61.8851 | 0.064087 | -0.16479 | 0.082397 | 61.8896 | -61.0519 | -0.11444 | -0.022888 | -0.10071 | -0.17853 | -0.054931 | -0.16022 | -0.050354 | 0.013733 | 60.7269 | 60.9741 | 122.7768 | 122.8088 | -0.10071 | 122.7814 | 60.9558 | -0.16022 | 122.8088 | -0.10071 | 60.9558 | 122.7768 | 122.7814 | -122.9462 | -122.9919
27.7656 | 123.1842 | -60.9238 | 61.9308 | 0.22484 | -0.0024482 | 0.0021149 | 0.0028476 | 0.068436 | -0.0013779 | 0.068265 | -60.997 | 61.9263 | -61.0336 | -61.084 | 61.8805 | 0.064087 | -0.16937 | 0.091553 | 61.8942 | -61.0703 | -0.10986 | -0.004577 | -0.073242 | -0.16022 | -0.050354 | -0.14648 | -0.036621 | 0.036621 | 60.7544 | 61.0153 | 122.8043 | 122.85 | -0.073242 | 122.818 | 60.9879 | -0.14648 | 122.85 | -0.073242 | 60.9879 | 122.8043 | 122.818 | -122.9645 | -123.0011
28.7656 | 123.1934 | -60.8871 | 61.9629 | 0.23247 | -0.0015936 | 0.0036103 | 0.003702 | 0.066941 | -0.0011643 | 0.07147 | -61.0245 | 61.9492 | -61.0382 | -61.0886 | 61.8622 | 0.050354 | -0.16479 | 0.068665 | 61.8942 | -61.0657 | -0.15106 | -0.013733 | -0.13733 | -0.20142 | -0.10071 | -0.17853 | -0.068665 | 0.013733 | 60.7224 | 60.9558 | 122.7493 | 122.8363 | -0.13733 | 122.7814 | 60.9375 | -0.17853 | 122.8363 | -0.13733 | 60.9375 | 122.7493 | 122.7814 | -123.0011 | -123.0286
29.7656 | 123.175 | -60.8917 | 61.9492 | 0.25536 | -0.0028754 | 0.0014741 | 0.0032748 | 0.065873 | -0.0020187 | 0.070402 | -61.0245 | 61.9537 | -61.0199 | -61.0931 | 61.853 | 0.054932 | -0.15106 | 0.073242 | 61.8988 | -61.0748 | -0.12817 | 0.004577 | -0.13275 | -0.20142 | -0.096131 | -0.1831 | -0.050354 | -0.004578 | 60.7407 | 60.965 | 122.7448 | 122.8455 | -0.13275 | 122.7905 | 60.9467 | -0.1831 | 122.8455 | -0.13275 | 60.9467 | 122.7448 | 122.7905 | -122.9691 | -123.024
30.7656 | 123.1979 | -60.8963 | 61.9492 | 0.24773 | -0.0033026 | 0.00083306 | 0.0022066 | 0.068436 | -0.0022323 | 0.067624 | -60.9879 | 61.908 | -60.997 | -61.0931 | 61.8805 | 0.041199 | -0.16937 | 0.082397 | 61.8988 | -61.0703 | -0.10071 | -0.041199 | -0.091553 | -0.19684 | -0.068665 | -0.17395 | -0.050354 | 0.009155 | 60.7269 | 60.9787 | 122.7768 | 122.8043 | -0.091553 | 122.7951 | 60.9375 | -0.17395 | 122.8043 | -0.091553 | 60.9375 | 122.7768 | 122.7951 | -122.9462 | -123.0194
31.7656 | 123.2254 | -60.9055 | 61.9446 | 0.24773 | -0.0054388 | 0.0046783 | 0.0017794 | 0.065659 | -0.00073695 | 0.066556 | -61.0016 | 61.9171 | -61.0016 | -61.0748 | 61.8942 | 0.059509 | -0.17395 | 0.073242 | 61.8942 | -61.1069 | -0.09613 | -0.027466 | -0.09613 | -0.16937 | -0.050354 | -0.20142 | -0.050354 | 0 | 60.7315 | 60.9787 | 122.7997 | 122.8226 | -0.09613 | 122.7997 | 60.965 | -0.20142 | 122.8226 | -0.09613 | 60.965 | 122.7997 | 122.7997 | -122.9462 | -123.0515
32.7656 | 123.1888 | -60.878 | 61.9308 | 0.23247 | -0.0041572 | 0.00019226 | 0.0011386 | 0.065232 | -0.00052335 | 0.068265 | -61.0062 | 61.8851 | -61.0107 | -61.0886 | 61.8484 | 0.054932 | -0.15106 | 0.16022 | 61.908 | -61.084 | -0.13275 | -0.045776 | -0.12817 | -0.21057 | -0.082397 | -0.20599 | -0.022888 | 0.004577 | 60.7269 | 61.0382 | 122.7264 | 122.7631 | -0.12817 | 122.7859 | 60.9329 | -0.20599 | 122.7631 | -0.12817 | 60.9329 | 122.7264 | 122.7859 | -122.9416 | -123.0148
33.7656 | 123.2254 | -60.878 | 61.9446 | 0.23247 | -0.0039434 | -0.0040801 | 0.0015658 | 0.064805 | -0.0026595 | 0.068265 | -60.997 | 61.9263 | -61.0245 | -61.0886 | 61.8713 | 0.064087 | -0.16022 | 0.091553 | 61.8942 | -61.0931 | -0.14648 | -0.01831 | -0.11902 | -0.21057 | -0.073242 | -0.21515 | -0.050354 | 0.027466 | 60.7178 | 60.9695 | 122.7493 | 122.8043 | -0.11902 | 122.7722 | 60.9421 | -0.21515 | 122.8043 | -0.11902 | 60.9421 | 122.7493 | 122.7722 | -122.9691 | -123.0377
34.7656 | 123.2071 | -60.8871 | 61.9537 | 0.21721 | -0.0041572 | 0.00061946 | 0.0022066 | 0.067795 | -0.0028731 | 0.068906 | -61.0062 | 61.9446 | -61.0199 | -61.0931 | 61.8805 | 0.064087 | -0.15106 | 0.082397 | 61.8668 | -61.0794 | -0.13275 | -0.009155 | -0.11902 | -0.20599 | -0.073242 | -0.19226 | -0.086975 | 0.013732 | 60.7361 | 60.9695 | 122.7676 | 122.8317 | -0.11902 | 122.7539 | 60.9512 | -0.19226 | 122.8317 | -0.11902 | 60.9512 | 122.7676 | 122.7539 | -122.9736 | -123.0331
35.7656 | 123.2117 | -60.8871 | 61.9354 | 0.2401 | -0.0015936 | 0.0012605 | 0.0024202 | 0.066941 | -0.0024459 | 0.069547 | -61.0062 | 61.908 | -61.0428 | -61.0931 | 61.8759 | 0.059509 | -0.17853 | 0.064087 | 61.9034 | -61.0474 | -0.15564 | -0.027466 | -0.11902 | -0.20599 | -0.059509 | -0.16022 | -0.032044 | 0.036621 | 60.7086 | 60.9512 | 122.7631 | 122.7951 | -0.11902 | 122.7905 | 60.9467 | -0.16022 | 122.7951 | -0.11902 | 60.9467 | 122.7631 | 122.7905 | -122.9782 | -122.9828
36.7656 | 123.2254 | -60.91 | 61.94 | 0.22484 | -0.0018072 | 0.0014741 | 0.0032748 | 0.066514 | -0.00095055 | 0.067838 | -61.0107 | 61.9446 | -61.0336 | -61.084 | 61.8713 | 0.050354 | -0.14648 | 0.068665 | 61.8942 | -61.1023 | -0.1236 | 0.004578 | -0.10071 | -0.17395 | -0.068664 | -0.19226 | -0.045776 | 0.022888 | 60.7636 | 60.9787 | 122.7814 | 122.8546 | -0.10071 | 122.8043 | 60.9604 | -0.19226 | 122.8546 | -0.10071 | 60.9604 | 122.7814 | 122.8043 | -122.9736 | -123.0423
37.7656 | 123.2162 | -60.8963 | 61.9446 | 0.27824 | -0.0026618 | 0.00019226 | 0.0022066 | 0.067155 | -0.0020187 | 0.068052 | -60.9924 | 61.9217 | -61.0245 | -61.0748 | 61.8805 | 0.050354 | -0.17395 | 0.07782 | 61.8896 | -61.0748 | -0.12817 | -0.022888 | -0.096131 | -0.17853 | -0.064087 | -0.17853 | -0.054932 | 0.032043 | 60.7224 | 60.9741 | 122.7768 | 122.818 | -0.096131 | 122.7859 | 60.9467 | -0.17853 | 122.818 | -0.096131 | 60.9467 | 122.7768 | 122.7859 | -122.9691 | -123.0194
38.7656 | 123.1979 | -60.8917 | 61.9446 | 0.22484 | -0.0026618 | 0.00040586 | 0.001993 | 0.064591 | -0.0011643 | 0.06912 | -60.997 | 61.9308 | -61.0016 | -61.0794 | 61.8759 | 0.054932 | -0.16479 | 0.07782 | 61.8851 | -61.084 | -0.10986 | -0.013733 | -0.10528 | -0.18768 | -0.068664 | -0.19226 | -0.059509 | 0.004578 | 60.7269 | 60.9695 | 122.7676 | 122.8226 | -0.10528 | 122.7768 | 60.9467 | -0.19226 | 122.8226 | -0.10528 | 60.9467 | 122.7676 | 122.7768 | -122.9462 | -123.0286
39.7656 | 123.1659 | -60.9009 | 61.9492 | 0.23247 | -0.0050116 | 0.00061946 | 0.001993 | 0.065446 | -0.0013779 | 0.068479 | -61.0107 | 61.94 | -61.0199 | -61.0931 | 61.8668 | 0.064087 | -0.12817 | 0.14648 | 61.9034 | -61.0886 | -0.11902 | -0.009156 | -0.10986 | -0.19226 | -0.082398 | -0.18768 | -0.045777 | 0.009155 | 60.7727 | 61.0474 | 122.7676 | 122.8409 | -0.10986 | 122.8043 | 60.965 | -0.18768 | 122.8409 | -0.10986 | 60.965 | 122.7676 | 122.8043 | -122.9691 | -123.0377
40.7656 | 123.2025 | -60.8871 | 61.9217 | 0.20958 | -0.003089 | 0.0016877 | 0.00092504 | 0.067155 | -0.0015915 | 0.069333 | -60.9879 | 61.8988 | -61.0107 | -61.084 | 61.8713 | 0.054932 | -0.16937 | 0.09613 | 61.8668 | -61.0611 | -0.1236 | -0.022888 | -0.10071 | -0.19684 | -0.050354 | -0.17395 | -0.054932 | 0.022888 | 60.7178 | 60.9833 | 122.7585 | 122.7859 | -0.10071 | 122.7539 | 60.9421 | -0.17395 | 122.7859 | -0.10071 | 60.9421 | 122.7585 | 122.7539 | -122.9324 | -122.9828
41.7656 | 123.2254 | -60.9009 | 61.9583 | 0.23247 | -0.0035162 | 0.0025421 | 0.0024202 | 0.065446 | -0.0018051 | 0.069974 | -60.997 | 61.9217 | -61.0153 | -61.084 | 61.8668 | 0.050354 | -0.17853 | 0.091553 | 61.9034 | -61.0794 | -0.11444 | -0.036621 | -0.09613 | -0.1831 | -0.091553 | -0.17853 | -0.054932 | 0.018311 | 60.7224 | 60.9924 | 122.7676 | 122.8226 | -0.09613 | 122.8043 | 60.9512 | -0.17853 | 122.8226 | -0.09613 | 60.9512 | 122.7676 | 122.8043 | -122.9736 | -123.0377
42.7656 | 123.23 | -60.8963 | 61.9354 | 0.2401 | -0.0028754 | 0.00061946 | 0.0041292 | 0.067155 | -0.0022323 | 0.068906 | -61.0245 | 61.908 | -61.0336 | -61.084 | 61.853 | 0.041199 | -0.14191 | 0.068665 | 61.8851 | -61.0794 | -0.13733 | -0.027466 | -0.12817 | -0.18768 | -0.082398 | -0.18311 | -0.050354 | 0.009155 | 60.7544 | 60.965 | 122.7493 | 122.8043 | -0.12817 | 122.7814 | 60.9375 | -0.18311 | 122.8043 | -0.12817 | 60.9375 | 122.7493 | 122.7814 | -122.9691 | -123.0148
43.7656 | 123.1979 | -60.9238 | 61.9263 | 0.27061 | -0.0011664 | 0.0019013 | 0.001993 | 0.069718 | -0.0030869 | 0.068052 | -61.0291 | 61.9308 | -61.0245 | -61.1114 | 61.8393 | 0.036621 | -0.13275 | 0.054932 | 61.9171 | -61.084 | -0.10071 | 0.004577 | -0.10529 | -0.18768 | -0.086976 | -0.16022 | -0.009156 | -0.004578 | 60.791 | 60.9787 | 122.7631 | 122.8546 | -0.10529 | 122.8409 | 60.9604 | -0.16022 | 122.8546 | -0.10529 | 60.9604 | 122.7631 | 122.8409 | -122.9507 | -123.0103
44.7656 | 123.1934 | -60.9192 | 61.9308 | 0.27061 | -0.00052559 | -0.0017303 | 0.0028476 | 0.066514 | -0.0022323 | 0.068479 | -60.9833 | 61.9308 | -61.0291 | -61.0886 | 61.8713 | 0.073242 | -0.18768 | 0.082397 | 61.8759 | -61.0931 | -0.10986 | 0 | -0.064087 | -0.16937 | -0.059509 | -0.17395 | -0.054931 | 0.045777 | 60.7315 | 61.0016 | 122.7905 | 122.85 | -0.064087 | 122.7951 | 60.9924 | -0.17395 | 122.85 | -0.064087 | 60.9924 | 122.7905 | 122.7951 | -122.9599 | -123.024
45.7656 | 123.2071 | -60.8917 | 61.9583 | 0.27061 | -0.0026618 | 0.0012605 | 0.00071144 | 0.066941 | -0.0024459 | 0.06912 | -60.997 | 61.9354 | -61.0245 | -61.084 | 61.8713 | 0.059509 | -0.17853 | 0.082397 | 61.8942 | -61.084 | -0.13275 | -0.022888 | -0.10528 | -0.19226 | -0.086975 | -0.19226 | -0.064087 | 0.027466 | 60.7132 | 60.9741 | 122.7631 | 122.8271 | -0.10528 | 122.786 | 60.9512 | -0.19226 | 122.8271 | -0.10528 | 60.9512 | 122.7631 | 122.786 | -122.9828 | -123.0423
46.7656 | 123.1934 | -60.8917 | 61.9492 | 0.22484 | -0.0041572 | -0.0053619 | 0.0011386 | 0.064805 | -0.0020187 | 0.068693 | -61.0062 | 61.94 | -61.0336 | -61.0748 | 61.8713 | 0.068665 | -0.15106 | 0.082397 | 61.8759 | -61.1023 | -0.14191 | -0.009156 | -0.11444 | -0.1831 | -0.07782 | -0.21057 | -0.073242 | 0.027465 | 60.7407 | 60.9741 | 122.7631 | 122.8317 | -0.11444 | 122.7676 | 60.9604 | -0.21057 | 122.8317 | -0.11444 | 60.9604 | 122.7631 | 122.7676 | -122.9828 | -123.0515
47.7656 | 123.1979 | -60.8963 | 61.9675 | 0.24773 | -0.0015936 | -0.0010895 | -0.00078396 | 0.064805 | -0.0011643 | 0.068693 | -61.0062 | 61.9354 | -61.0428 | -61.084 | 61.8896 | 0.054932 | -0.17853 | 0.082397 | 61.8805 | -61.0886 | -0.14648 | -0.032043 | -0.10986 | -0.18768 | -0.07782 | -0.19226 | -0.086975 | 0.036621 | 60.7178 | 60.9787 | 122.7859 | 122.8317 | -0.10986 | 122.7768 | 60.9512 | -0.19226 | 122.8317 | -0.10986 | 60.9512 | 122.7859 | 122.7768 | -123.0103 | -123.056
48.7656 | 123.2162 | -60.91 | 61.94 | 0.24773 | -0.0022346 | 0.0021149 | 0.00028404 | 0.063737 | -0.00052335 | 0.069333 | -60.9879 | 61.9263 | -61.0336 | -61.0703 | 61.8622 | 0.054932 | -0.17395 | 0.091553 | 61.8942 | -61.0611 | -0.1236 | -0.013732 | -0.07782 | -0.16022 | -0.077819 | -0.15106 | -0.045776 | 0.045776 | 60.7361 | 61.0016 | 122.7722 | 122.8363 | -0.07782 | 122.8043 | 60.965 | -0.15106 | 122.8363 | -0.07782 | 60.965 | 122.7722 | 122.8043 | -122.9736 | -123.0011
49.7656 | 123.2025 | -60.8917 | 61.9354 | 0.27824 | -0.0035162 | 0.00061946 | 0.0028476 | 0.066941 | -0.0024459 | 0.067838 | -61.0382 | 61.9766 | -61.0474 | -61.1023 | 61.8484 | 0.032043 | -0.13275 | 0.050354 | 61.908 | -61.0931 | -0.15564 | 0.041199 | -0.14648 | -0.21057 | -0.086975 | -0.20142 | -0.027466 | 0.009155 | 60.759 | 60.9421 | 122.7402 | 122.8683 | -0.14648 | 122.7997 | 60.9238 | -0.20142 | 122.8683 | -0.14648 | 60.9238 | 122.7402 | 122.7997 | -122.9828 | -123.0286
50.7656 | 123.1979 | -60.91 | 61.9263 | 0.25536 | -0.003089 | 0.0025421 | 0.001993 | 0.065232 | -0.0028731 | 0.067197 | -60.997 | 61.9263 | -61.0245 | -61.0886 | 61.8805 | 0.068665 | -0.16937 | 0.10071 | 61.9171 | -61.0794 | -0.11444 | 0 | -0.086975 | -0.17853 | -0.045777 | -0.16937 | -0.009156 | 0.027466 | 60.7407 | 61.0107 | 122.7905 | 122.8363 | -0.086975 | 122.8271 | 60.9787 | -0.16937 | 122.8363 | -0.086975 | 60.9787 | 122.7905 | 122.8271 | -122.9507 | -123.0057
51.7656 | 123.2117 | -60.8963 | 61.9537 | 0.2401 | -0.0011664 | 0.0012605 | 0.001993 | 0.067795 | -0.0020187 | 0.067838 | -60.997 | 61.9492 | -61.0153 | -61.0886 | 61.8668 | 0.059509 | -0.17853 | 0.086975 | 61.908 | -61.0794 | -0.11902 | -0.004577 | -0.10071 | -0.19226 | -0.086975 | -0.18311 | -0.045776 | 0.018311 | 60.7178 | 60.9833 | 122.7631 | 122.8455 | -0.10071 | 122.8043 | 60.9558 | -0.18311 | 122.8455 | -0.10071 | 60.9558 | 122.7631 | 122.8043 | -122.9691 | -123.0331
52.7656 | 123.1979 | -60.9009 | 61.9537 | 0.27061 | -0.0035162 | -0.00023494 | 0.0022066 | 0.066941 | -0.00095055 | 0.069761 | -61.0153 | 61.9354 | -61.0107 | -61.0977 | 61.8668 | 0.045776 | -0.15106 | 0.064087 | 61.8759 | -61.0931 | -0.10986 | -0.01831 | -0.11444 | -0.19684 | -0.086975 | -0.19226 | -0.077819 | -0.004578 | 60.7498 | 60.965 | 122.7676 | 122.8363 | -0.11444 | 122.7768 | 60.9467 | -0.19226 | 122.8363 | -0.11444 | 60.9467 | 122.7676 | 122.7768 | -122.9645 | -123.0469
53.7656 | 123.2071 | -60.9009 | 61.9446 | 0.26299 | -0.00052559 | 0.0042511 | 0.0024202 | 0.063737 | -0.0018051 | 0.067838 | -61.0016 | 61.9217 | -61.0428 | -61.0748 | 61.8759 | 0.059509 | -0.17395 | 0.091553 | 61.8896 | -61.0794 | -0.14191 | -0.022888 | -0.10071 | -0.17395 | -0.068664 | -0.17853 | -0.054932 | 0.041199 | 60.7269 | 60.9924 | 122.7768 | 122.8226 | -0.10071 | 122.7905 | 60.9604 | -0.17853 | 122.8226 | -0.10071 | 60.9604 | 122.7768 | 122.7905 | -122.9874 | -123.024
54.7656 | 123.2025 | -60.9009 | 61.9583 | 0.30113 | -0.003089 | 0.00040586 | 0.001993 | 0.066514 | -0.0013779 | 0.068052 | -60.997 | 61.9446 | -61.0245 | -61.0931 | 61.8896 | 0.059509 | -0.17853 | 0.086975 | 61.8576 | -61.0886 | -0.1236 | -0.013733 | -0.09613 | -0.19226 | -0.068665 | -0.18768 | -0.10071 | 0.027466 | 60.7224 | 60.9879 | 122.7905 | 122.8455 | -0.09613 | 122.7585 | 60.9604 | -0.18768 | 122.8455 | -0.09613 | 60.9604 | 122.7905 | 122.7585 | -122.9828 | -123.0469
55.7656 | 123.1934 | -60.9055 | 61.9446 | 0.23247 | -0.003089 | 0.0027557 | 0.0015658 | 0.065232 | -0.0015915 | 0.06912 | -60.9741 | 61.94 | -61.0336 | -61.0931 | 61.8576 | 0.059509 | -0.17395 | 0.082397 | 61.9263 | -61.0794 | -0.12817 | -0.004578 | -0.068664 | -0.18768 | -0.086975 | -0.17395 | -0.01831 | 0.059509 | 60.7315 | 60.9879 | 122.7631 | 122.8455 | -0.068664 | 122.8317 | 60.965 | -0.17395 | 122.8455 | -0.068664 | 60.965 | 122.7631 | 122.8317 | -122.9782 | -123.024
56.7656 | 123.1567 | -60.9146 | 61.9537 | 0.25536 | -0.0026618 | 0.0048921 | 0.0041292 | 0.066941 | -0.0018051 | 0.070829 | -61.1206 | 61.9949 | -61.0657 | -61.1481 | 61.7661 | -0.027466 | -0.068665 | 0.004578 | 61.9217 | -61.116 | -0.15106 | 0.041199 | -0.20599 | -0.23346 | -0.18768 | -0.20142 | -0.032043 | -0.054931 | 60.8459 | 60.9192 | 122.6807 | 122.9095 | -0.20599 | 122.8363 | 60.8871 | -0.20142 | 122.9095 | -0.20599 | 60.8871 | 122.6807 | 122.8363 | -123.0194 | -123.0698
57.7656 | 123.2071 | -60.878 | 61.9263 | 0.27061 | -0.0022346 | -0.0015167 | 0.0030612 | 0.067582 | -0.00095055 | 0.067197 | -61.0062 | 61.9492 | -61.0336 | -61.1069 | 61.8668 | 0.054932 | -0.16022 | 0.059509 | 61.908 | -61.1069 | -0.15564 | 0.022888 | -0.12817 | -0.22888 | -0.05951 | -0.22888 | -0.018311 | 0.027465 | 60.7178 | 60.9375 | 122.7448 | 122.8271 | -0.12817 | 122.7859 | 60.9329 | -0.22888 | 122.8271 | -0.12817 | 60.9329 | 122.7448 | 122.7859 | -122.9599 | -123.0331
58.7656 | 123.2117 | -60.8917 | 61.9583 | 0.1104 | -0.0039434 | -0.0015167 | 0.00092504 | 0.067155 | -0.00073695 | 0.068052 | -60.8734 | 61.9766 | -61.0291 | -61.0748 | 61.8393 | 0.018311 | -0.14191 | 0.059509 | 61.908 | -61.0886 | -0.13733 | 0.018311 | 0.018311 | -0.1831 | -0.11902 | -0.19684 | -0.050354 | 0.15564 | 60.7498 | 60.9512 | 122.731 | 122.8683 | 0.018311 | 122.7997 | 60.91 | -0.19684 | 122.8683 | 0.018311 | 60.91 | 122.731 | 122.7997 | -122.9874 | -123.0469
59.7656 | 123.1384 | -60.9329 | 61.908 | 0.27824 | -0.0018072 | 0.0012605 | 0.003702 | 0.069291 | -0.0033005 | 0.070188 | -61.0474 | 61.9675 | -61.0474 | -61.1343 | 61.8439 | 0.027466 | -0.13275 | 0.032043 | 61.8988 | -61.1023 | -0.11444 | 0.059509 | -0.11444 | -0.20142 | -0.064087 | -0.16937 | -0.009155 | 0 | 60.8002 | 60.965 | 122.7768 | 122.9004 | -0.11444 | 122.8317 | 60.9604 | -0.16937 | 122.9004 | -0.11444 | 60.9604 | 122.7768 | 122.8317 | -122.9553 | -123.0103
60.7656 | 123.2025 | -60.91 | 61.9492 | -0.56862 | -0.0039434 | -0.0013031 | -0.00014316 | 0.066941 | -0.0011643 | 0.068693 | -60.91 | 61.9675 | -61.0153 | -61.0931 | 61.8576 | 0.059509 | -0.17395 | 0.086975 | 61.9034 | -61.0794 | -0.10529 | 0.01831 | 0 | -0.18311 | -0.091553 | -0.16937 | -0.045777 | 0.10529 | 60.7361 | 60.997 | 122.7676 | 122.8775 | 0 | 122.8134 | 60.9695 | -0.16937 | 122.8775 | 0 | 60.9695 | 122.7676 | 122.8134 | -122.9645 | -123.0286
61.7656 | 123.2529 | -60.8871 | 61.9446 | 0.23247 | -0.0039434 | 0.00061946 | 0.001993 | 0.065873 | -0.0011643 | 0.069974 | -61.0016 | 61.9492 | -61.0336 | -61.1023 | 61.8622 | 0.059509 | -0.37079 | -0.10071 | 61.8713 | -61.1343 | -0.14648 | 0.004578 | -0.11444 | -0.21515 | -0.082397 | -0.24719 | -0.073242 | 0.032043 | 60.5164 | 60.7864 | 122.7493 | 122.8363 | -0.11444 | 122.7585 | 60.9467 | -0.24719 | 122.8363 | -0.11444 | 60.9467 | 122.7493 | 122.7585 | -122.9782 | -123.0789
62.7656 | 123.1155 | -60.9192 | 61.9629 | 0.23247 | -0.00031179 | 0.0048921 | 0.0030612 | 0.067795 | -0.00052335 | 0.068052 | -61.0565 | 62.0178 | -61.0748 | -61.1755 | 61.7798 | -0.022888 | -0.050354 | -0.027466 | 61.9263 | -61.1069 | -0.15564 | 0.054931 | -0.13733 | -0.25635 | -0.18311 | -0.18768 | -0.036621 | 0.01831 | 60.8688 | 60.8917 | 122.699 | 122.937 | -0.13733 | 122.8455 | 60.8963 | -0.18768 | 122.937 | -0.13733 | 60.8963 | 122.699 | 122.8455 | -123.0377 | -123.0698
63.7656 | 123.111 | -60.9329 | 61.9629 | 0.2401 | -0.0011664 | 0.0036103 | 0.0015658 | 0.067582 | -0.0020187 | 0.070615 | -61.0703 | 62.0087 | -61.0657 | -61.1893 | 61.7706 | -0.054932 | -0.018311 | -0.013733 | 61.9492 | -61.1298 | -0.13275 | 0.045776 | -0.13733 | -0.25635 | -0.19226 | -0.19684 | -0.013733 | -0.004577 | 60.9146 | 60.9192 | 122.7036 | 122.9416 | -0.13733 | 122.8821 | 60.878 | -0.19684 | 122.9416 | -0.13733 | 60.878 | 122.7036 | 122.8821 | -123.0286 | -123.0927
64.7656 | 123.1567 | -60.9146 | 61.9766 | 0.28587 | -0.0015936 | -0.0021575 | 0.0017794 | 0.0663 | 0.00011745 | 0.069547 | -61.0611 | 61.9949 | -61.0657 | -61.1526 | 61.821 | 0.004578 | -0.091553 | 0.009155 | 61.9308 | -61.116 | -0.15106 | 0.01831 | -0.14648 | -0.23804 | -0.15564 | -0.20142 | -0.045777 | 0.004578 | 60.8231 | 60.9238 | 122.7356 | 122.9095 | -0.14648 | 122.8455 | 60.9192 | -0.20142 | 122.9095 | -0.14648 | 60.9192 | 122.7356 | 122.8455 | -123.0423 | -123.0927
65.7656 | 123.1201 | -60.9421 | 61.9583 | 0.27061 | -0.00052559 | 0.0019013 | 0.00049764 | 0.066941 | -0.0013779 | 0.070402 | -61.0703 | 62.0087 | -61.0703 | -61.1755 | 61.7935 | -0.013733 | -0.054932 | -0.009155 | 61.9629 | -61.1069 | -0.12817 | 0.050354 | -0.12817 | -0.23346 | -0.16479 | -0.16479 | 0.004578 | 0 | 60.8871 | 60.9329 | 122.7356 | 122.9507 | -0.12817 | 122.905 | 60.9283 | -0.16479 | 122.9507 | -0.12817 | 60.9283 | 122.7356 | 122.905 | -123.0286 | -123.0652
66.7656 | 123.1842 | -60.8963 | 61.9354 | 0.26299 | -0.00073919 | 0.0019013 | 0.0011386 | 0.067368 | -0.00030975 | 0.068052 | -61.0336 | 61.9995 | -61.0611 | -61.1252 | 61.8393 | 0.054932 | -0.17395 | 0.050354 | 61.908 | -61.1206 | -0.16479 | 0.064087 | -0.13733 | -0.22888 | -0.096131 | -0.2243 | -0.027466 | 0.027466 | 60.7224 | 60.9467 | 122.7356 | 122.8958 | -0.13733 | 122.8043 | 60.9512 | -0.2243 | 122.8958 | -0.13733 | 60.9512 | 122.7356 | 122.8043 | -122.9965 | -123.056
67.7656 | 123.1522 | -60.9329 | 61.9308 | 0.28587 | -0.00095279 | -0.0023711 | 0.00092504 | 0.067155 | -0.0013779 | 0.070829 | -61.0657 | 61.9995 | -61.0703 | -61.1481 | 61.8164 | -0.009155 | -0.091553 | 0.018311 | 61.94 | -61.0794 | -0.13733 | 0.068665 | -0.13275 | -0.21515 | -0.11444 | -0.14649 | 0.009155 | 0.004577 | 60.8414 | 60.9512 | 122.7493 | 122.9324 | -0.13275 | 122.8729 | 60.9238 | -0.14649 | 122.9324 | -0.13275 | 60.9238 | 122.7493 | 122.8729 | -123.0011 | -123.0103
68.7656 | 123.1293 | -60.9238 | 61.9492 | -0.16426 | -0.00031179 | 0.0014741 | 0.001993 | 0.069077 | -0.0028731 | 0.069974 | -61.0474 | 62.0041 | -61.0519 | -61.1893 | 61.7935 | -0.018311 | -0.054932 | -0.009155 | 61.9537 | -61.1252 | -0.12817 | 0.054931 | -0.1236 | -0.2655 | -0.15564 | -0.20142 | 0.004577 | 0.004578 | 60.8688 | 60.9146 | 122.7173 | 122.9279 | -0.1236 | 122.8775 | 60.9055 | -0.20142 | 122.9279 | -0.1236 | 60.9055 | 122.7173 | 122.8775 | -123.0011 | -123.0743
69.7656 | 123.0743 | -60.9283 | 61.9858 | 0.15617 | 0.00032901 | -0.0025847 | 0.0032748 | 0.067582 | -0.0018051 | 0.068693 | -61.084 | 62.027 | -61.0611 | -61.1893 | 61.7569 | -0.050354 | 0.022888 | -0.045776 | 61.9858 | -61.1389 | -0.13275 | 0.041199 | -0.15564 | -0.26093 | -0.22888 | -0.21057 | 0 | -0.022888 | 60.9512 | 60.8826 | 122.6852 | 122.9553 | -0.15564 | 122.9141 | 60.878 | -0.21057 | 122.9553 | -0.15564 | 60.878 | 122.6852 | 122.9141 | -123.0469 | -123.1247
70.7656 | 123.0652 | -60.9375 | 61.9995 | 0.14092 | -0.0033026 | 0.0031831 | 0.0024202 | 0.069291 | -0.00073695 | 0.068265 | -61.0748 | 62.0453 | -61.0565 | -61.2167 | 61.7432 | -0.064087 | 0.045776 | -0.036621 | 61.972 | -61.1206 | -0.11902 | 0.045776 | -0.13733 | -0.27924 | -0.25635 | -0.1831 | -0.027466 | -0.01831 | 60.9833 | 60.9009 | 122.6807 | 122.9828 | -0.13733 | 122.9095 | 60.8734 | -0.1831 | 122.9828 | -0.13733 | 60.8734 | 122.6807 | 122.9095 | -123.056 | -123.1201
71.7656 | 123.0927 | -60.9558 | 61.9812 | 0.20195 | -0.0015936 | -0.0019439 | 0.0028476 | 0.067155 | -0.0026595 | 0.06912 | -61.084 | 62.027 | -61.0565 | -61.2167 | 61.7615 | -0.045776 | 0.022888 | -0.045776 | 61.9766 | -61.1526 | -0.10071 | 0.045777 | -0.12817 | -0.26093 | -0.21973 | -0.19684 | -0.004577 | -0.027465 | 60.9787 | 60.91 | 122.7173 | 122.9828 | -0.12817 | 122.9324 | 60.91 | -0.19684 | 122.9828 | -0.12817 | 60.91 | 122.7173 | 122.9324 | -123.0377 | -123.1338
72.7656 | 123.1155 | -60.965 | 61.9629 | 0.14092 | -0.00052559 | 0.0029693 | 0.00071144 | 0.0663 | -0.0015915 | 0.069333 | -61.1114 | 62.0453 | -61.0703 | -61.2213 | 61.7432 | -0.041199 | 0.022888 | -0.036621 | 61.9354 | -61.1572 | -0.10529 | 0.082397 | -0.14648 | -0.25635 | -0.21973 | -0.19226 | -0.027466 | -0.041199 | 60.9879 | 60.9283 | 122.7081 | 123.0103 | -0.14648 | 122.9004 | 60.9238 | -0.19226 | 123.0103 | -0.14648 | 60.9238 | 122.7081 | 122.9004 | -123.0331 | -123.1201
73.7656 | 123.0835 | -60.9421 | 61.9766 | 0.17143 | -0.0011664 | 0.00040586 | 0.0034884 | 0.067155 | -0.0011643 | 0.068906 | -61.1069 | 62.0453 | -61.0703 | -61.203 | 61.7844 | -0.050354 | 0.013733 | -0.041199 | 61.9308 | -61.1618 | -0.12817 | 0.068664 | -0.16479 | -0.26093 | -0.19226 | -0.21973 | -0.045777 | -0.036622 | 60.9558 | 60.9009 | 122.7264 | 122.9874 | -0.16479 | 122.8729 | 60.8917 | -0.21973 | 122.9874 | -0.16479 | 60.8917 | 122.7264 | 122.8729 | -123.0469 | -123.1384
74.7656 | 123.0743 | -60.965 | 61.9766 | 0.17143 | -0.0024482 | 0.0012605 | 0.0030612 | 0.069077 | 0.0013993 | 0.068906 | -61.0886 | 62.0407 | -61.084 | -61.2122 | 61.7706 | -0.045776 | 0.022888 | -0.045776 | 61.94 | -61.1526 | -0.11902 | 0.064086 | -0.1236 | -0.24719 | -0.20599 | -0.18768 | -0.036622 | -0.004578 | 60.9879 | 60.9192 | 122.7356 | 123.0057 | -0.1236 | 122.905 | 60.9192 | -0.18768 | 123.0057 | -0.1236 | 60.9192 | 122.7356 | 122.905 | -123.0606 | -123.1293
75.7656 | 123.0743 | -60.9375 | 61.972 | 0.21721 | -0.00073919 | -0.0010895 | 0.0034884 | 0.067155 | -0.00095055 | 0.067411 | -61.0977 | 62.0453 | -61.0519 | -61.2305 | 61.7432 | -0.036621 | 0.022888 | -0.036621 | 61.9537 | -61.1526 | -0.11444 | 0.073242 | -0.16022 | -0.29297 | -0.22888 | -0.21515 | -0.018311 | -0.045776 | 60.9604 | 60.9009 | 122.6807 | 122.9828 | -0.16022 | 122.8912 | 60.9009 | -0.21515 | 122.9828 | -0.16022 | 60.9009 | 122.6807 | 122.8912 | -123.024 | -123.1247
76.7656 | 123.0789 | -60.9055 | 61.9995 | 0.072251 | -0.0011664 | 0.0019013 | 0.0024202 | 0.069932 | -0.0011643 | 0.068052 | -61.0382 | 62.0499 | -61.0382 | -61.1526 | 61.8073 | -0.068665 | 0.054932 | 0.041199 | 61.9629 | -61.1389 | -0.13275 | 0.050354 | -0.13275 | -0.24719 | -0.19226 | -0.23346 | -0.036621 | 0 | 60.9604 | 60.9467 | 122.7127 | 122.9553 | -0.13275 | 122.8683 | 60.8368 | -0.23346 | 122.9553 | -0.13275 | 60.8368 | 122.7127 | 122.8683 | -123.0377 | -123.1384
77.7656 | 123.0927 | -60.8963 | 61.9995 | 0.056992 | -0.0018072 | 0.0029693 | 0.0047702 | 0.068223 | -9.6146e-05 | 0.068479 | -61.0291 | 62.059 | -61.0153 | -61.1343 | 61.821 | 0.032043 | 0.022888 | 0.064087 | 61.9354 | -61.1435 | -0.11902 | 0.059509 | -0.13275 | -0.23804 | -0.17853 | -0.24719 | -0.064087 | -0.013733 | 60.9192 | 60.9604 | 122.7173 | 122.9553 | -0.13275 | 122.8317 | 60.9283 | -0.24719 | 122.9553 | -0.13275 | 60.9283 | 122.7173 | 122.8317 | -123.0148 | -123.143
78.7656 | 123.0927 | -60.9146 | 61.9949 | 0.026474 | -0.0022346 | 0.0016877 | 0.00049764 | 0.067155 | -0.0020187 | 0.067197 | -61.0565 | 62.0682 | -61.0428 | -61.1801 | 61.7889 | -0.009155 | 0.041199 | 0.018311 | 61.9354 | -61.1343 | -0.12817 | 0.073242 | -0.14191 | -0.2655 | -0.20599 | -0.21973 | -0.059509 | -0.013733 | 60.9558 | 60.9329 | 122.7036 | 122.9828 | -0.14191 | 122.85 | 60.9055 | -0.21973 | 122.9828 | -0.14191 | 60.9055 | 122.7036 | 122.85 | -123.0377 | -123.1293
80.0938 | 123.1293 | -60.9055 | 61.9766 | -0.072708 | -0.0018072 | 0.00061946 | 0.0013522 | 0.067795 | -0.0011643 | 0.068906 | -61.0245 | 62.0361 | -61.0062 | -61.1206 | 61.8576 | 0.086975 | 0.054932 | 0.11444 | 61.9583 | -61.1252 | -0.10071 | 0.059509 | -0.11902 | -0.21515 | -0.11902 | -0.21973 | -0.018311 | -0.01831 | 60.9604 | 61.0199 | 122.7631 | 122.9416 | -0.11902 | 122.8638 | 60.9924 | -0.21973 | 122.9416 | -0.11902 | 60.9924 | 122.7631 | 122.8638 | -122.9828 | -123.1018
80.7656 | 123.056 | -60.9329 | 62.0178 | 0.064621 | -9.819e-05 | 0.0014741 | 0.001993 | 0.066727 | -0.00095055 | 0.067838 | -61.084 | 62.0544 | -61.0657 | -61.2259 | 61.7569 | -0.045776 | 0.041199 | -0.036621 | 61.9766 | -61.1526 | -0.13275 | 0.036621 | -0.15106 | -0.29297 | -0.26093 | -0.21973 | -0.041198 | -0.01831 | 60.9741 | 60.8963 | 122.6898 | 122.9874 | -0.15106 | 122.9095 | 60.8871 | -0.21973 | 122.9874 | -0.15106 | 60.8871 | 122.6898 | 122.9095 | -123.0835 | -123.1705
81.7656 | 123.0606 | -60.9238 | 61.9675 | 0.14854 | -0.00095279 | 0.0038239 | 0.0024202 | 0.067795 | -0.0013779 | 0.071256 | -61.0565 | 62.0728 | -61.0565 | -61.203 | 61.7706 | -0.013733 | 0.054932 | -0.027466 | 61.9904 | -61.1572 | -0.13275 | 0.10529 | -0.13275 | -0.27924 | -0.19684 | -0.23346 | 0.022888 | 0 | 60.9787 | 60.8963 | 122.6944 | 122.9965 | -0.13275 | 122.9141 | 60.91 | -0.23346 | 122.9965 | -0.13275 | 60.91 | 122.6944 | 122.9141 | -123.024 | -123.1247
82.7656 | 123.0789 | -60.9283 | 61.9949 | 0.011215 | -0.00138 | 0.00040586 | -0.00057036 | 0.068223 | -0.0018051 | 0.069974 | -61.0519 | 62.0682 | -61.0519 | -61.1664 | 61.7844 | -0.013733 | 0.036621 | 0.027466 | 61.9858 | -61.1481 | -0.1236 | 0.073242 | -0.1236 | -0.23804 | -0.21057 | -0.21973 | -0.009155 | 0 | 60.965 | 60.9558 | 122.7127 | 122.9965 | -0.1236 | 122.9141 | 60.9146 | -0.21973 | 122.9965 | -0.1236 | 60.9146 | 122.7127 | 122.9141 | -123.0469 | -123.143
83.7812 | 123.1659 | -60.9146 | 61.972 | 0.22484 | -0.004798 | 0.00019226 | -0.0039884 | 0.066514 | 0.00097205 | 0.068693 | -61.0565 | 61.908 | -61.0428 | -61.1572 | 61.8439 | 0.036621 | -0.082397 | 0.086975 | 61.9354 | -61.0794 | -0.12817 | -0.064087 | -0.14191 | -0.24262 | -0.12817 | -0.1648 | -0.036621 | -0.013733 | 60.8322 | 61.0016 | 122.7585 | 122.8226 | -0.14191 | 122.85 | 60.9512 | -0.1648 | 122.8226 | -0.14191 | 60.9512 | 122.7585 | 122.85 | -123.0148 | -123.0515
84.7656 | 123.111 | -60.9192 | 61.9949 | -0.080337 | -0.0024482 | 0.0021149 | 0.0045566 | 0.069504 | -0.00095055 | 0.06912 | -60.997 | 62.0407 | -61.0336 | -61.1252 | 61.8347 | 0.073242 | 0.022888 | 0.10529 | 61.9995 | -61.1298 | -0.11444 | 0.045776 | -0.07782 | -0.20599 | -0.16022 | -0.21057 | 0.004578 | 0.036621 | 60.9421 | 61.0245 | 122.7539 | 122.9599 | -0.07782 | 122.9187 | 60.9924 | -0.21057 | 122.9599 | -0.07782 | 60.9924 | 122.7539 | 122.9187 | -123.0286 | -123.1247
85.7656 | 123.1018 | -60.91 | 61.9904 | 0.056992 | -0.0011664 | 0.00061946 | 0.004343 | 0.069932 | -0.0020187 | 0.070188 | -61.0107 | 62.0407 | -61.0382 | -61.1298 | 61.8027 | 0.027466 | 0.027466 | -0.068665 | 61.972 | -61.1298 | -0.12817 | 0.050354 | -0.10071 | -0.21973 | -0.18768 | -0.21973 | -0.01831 | 0.027466 | 60.9375 | 60.8414 | 122.7127 | 122.9507 | -0.10071 | 122.8821 | 60.9375 | -0.21973 | 122.9507 | -0.10071 | 60.9375 | 122.7127 | 122.8821 | -123.0286 | -123.1201
86.7656 | 123.1064 | -60.91 | 61.9904 | 0.034104 | -0.0015936 | -0.0025847 | 0.0039156 | 0.067795 | -0.0013779 | 0.070829 | -61.0153 | 62.0453 | -61.0153 | -61.1252 | 61.8301 | 0.054932 | 0.032043 | 0.07782 | 61.9675 | -61.1435 | -0.10529 | 0.054932 | -0.10529 | -0.21515 | -0.16022 | -0.23346 | -0.022888 | 0 | 60.9421 | 60.9879 | 122.7402 | 122.9553 | -0.10529 | 122.8775 | 60.965 | -0.23346 | 122.9553 | -0.10529 | 60.965 | 122.7402 | 122.8775 | -123.0057 | -123.1338
87.7656 | 123.0835 | -60.9055 | 61.972 | 0.011215 | -0.00052559 | 0.0010467 | 0.0034884 | 0.068864 | -0.00073695 | 0.071042 | -61.0199 | 62.027 | -61.0153 | -61.171 | 61.7889 | 0 | 0.064087 | 0.036621 | 61.9766 | -61.1298 | -0.10986 | 0.054932 | -0.11444 | -0.2655 | -0.18311 | -0.2243 | 0.004578 | -0.004577 | 60.9695 | 60.9421 | 122.6944 | 122.9324 | -0.11444 | 122.8821 | 60.9055 | -0.2243 | 122.9324 | -0.11444 | 60.9055 | 122.6944 | 122.8821 | -122.9874 | -123.1018
88.7812 | 123.1979 | -60.9192 | 61.9263 | 0.20958 | -0.0022346 | -0.0017303 | -0.002493 | 0.068864 | -0.0011643 | 0.068693 | -61.0153 | 61.9675 | -61.0519 | -61.1069 | 61.853 | 0.054932 | -0.17395 | 0.07782 | 61.9171 | -61.1023 | -0.13275 | 0.041198 | -0.096131 | -0.18768 | -0.073243 | -0.18311 | -0.009156 | 0.036621 | 60.7452 | 60.997 | 122.7722 | 122.8867 | -0.096131 | 122.8363 | 60.9741 | -0.18311 | 122.8867 | -0.096131 | 60.9741 | 122.7722 | 122.8363 | -122.9782 | -123.0286
89.7656 | 123.1018 | -60.9146 | 61.9904 | 0.026474 | -0.0018072 | -0.00066214 | 0.0011386 | 0.066087 | -0.0013779 | 0.069547 | -61.0107 | 62.0361 | -61.0428 | -61.1114 | 61.8347 | 0.050354 | 0.027466 | 0.064087 | 61.9583 | -61.1343 | -0.12817 | 0.045777 | -0.09613 | -0.19684 | -0.15564 | -0.21973 | -0.032043 | 0.032044 | 60.9421 | 60.9787 | 122.7493 | 122.9507 | -0.09613 | 122.8729 | 60.965 | -0.21973 | 122.9507 | -0.09613 | 60.965 | 122.7493 | 122.8729 | -123.0331 | -123.1247
90.7656 | 123.1293 | -60.8917 | 62.0132 | -0.04219 | -0.00073919 | 0.0016877 | 0.0011386 | 0.067368 | -0.0024459 | 0.067411 | -60.997 | 62.0453 | -61.0336 | -61.1252 | 61.8484 | 0.086975 | 0.059509 | 0.11444 | 61.9812 | -61.1343 | -0.14191 | 0.032043 | -0.10528 | -0.23346 | -0.16479 | -0.24261 | -0.032044 | 0.036621 | 60.9512 | 61.0062 | 122.7402 | 122.937 | -0.10528 | 122.8729 | 60.9787 | -0.24261 | 122.937 | -0.10528 | 60.9787 | 122.7402 | 122.8729 | -123.0469 | -123.1476
91.7656 | 123.1247 | -60.8963 | 61.9858 | -0.080337 | -0.00138 | 0.00083306 | 0.002634 | 0.06865 | -0.0018051 | 0.068265 | -61.0062 | 62.0407 | -61.0245 | -61.116 | 61.8576 | 0.086975 | 0.068665 | 0.1236 | 62.0087 | -61.1206 | -0.12817 | 0.054931 | -0.10986 | -0.21973 | -0.12817 | -0.2243 | 0.022888 | 0.01831 | 60.965 | 61.0199 | 122.7539 | 122.937 | -0.10986 | 122.905 | 60.9833 | -0.2243 | 122.937 | -0.10986 | 60.9833 | 122.7539 | 122.905 | -123.0103 | -123.1064
92.7656 | 123.1293 | -60.9146 | 61.9904 | -0.095596 | -0.00052559 | 0.0053193 | 0.00071144 | 0.067795 | -0.0013779 | 0.070615 | -61.0291 | 62.0544 | -61.0428 | -61.116 | 61.8347 | 0.054932 | 0.045776 | 0.09613 | 61.9675 | -61.1298 | -0.12817 | 0.064087 | -0.11444 | -0.20142 | -0.15564 | -0.21515 | -0.022888 | 0.013733 | 60.9604 | 61.0107 | 122.7493 | 122.9691 | -0.11444 | 122.8821 | 60.9695 | -0.21515 | 122.9691 | -0.11444 | 60.9695 | 122.7493 | 122.8821 | -123.0331 | -123.1201
93.7812 | 123.0927 | -60.9192 | 61.9858 | 2.9943 | -0.00073919 | -0.0030121 | -0.0012112 | 0.070145 | -0.0013779 | 0.068479 | -61.0199 | 62.0132 | -61.0657 | -61.1801 | 61.7706 | -0.041199 | -0.027466 | -0.018311 | 61.9812 | -61.1252 | -0.14648 | 0.027466 | -0.10071 | -0.26093 | -0.21515 | -0.20599 | -0.004578 | 0.045777 | 60.8917 | 60.9009 | 122.6898 | 122.9324 | -0.10071 | 122.9004 | 60.878 | -0.20599 | 122.9324 | -0.10071 | 60.878 | 122.6898 | 122.9004 | -123.0515 | -123.111
94.7656 | 123.1064 | -60.9238 | 61.972 | -0.065079 | -0.00138 | -0.0015167 | 0.0022066 | 0.068436 | -0.0018051 | 0.068479 | -61.0016 | 62.0544 | -61.0382 | -61.116 | 61.8439 | 0.073242 | 0.022888 | 0.10071 | 61.9766 | -61.1389 | -0.11444 | 0.082397 | -0.07782 | -0.19226 | -0.12817 | -0.21515 | 0.004578 | 0.036621 | 60.9467 | 61.0245 | 122.7676 | 122.9782 | -0.07782 | 122.9004 | 60.997 | -0.21515 | 122.9782 | -0.07782 | 60.997 | 122.7676 | 122.9004 | -123.0103 | -123.111
95.7656 | 123.1247 | -60.9329 | 61.9904 | -0.019302 | -0.0020208 | 0.0033967 | 0.00049764 | 0.068009 | 0.00011745 | 0.068265 | -61.0062 | 62.0499 | -61.0199 | -61.1023 | 61.8347 | 0.068665 | 0.032043 | 0.10986 | 61.9995 | -61.1526 | -0.086975 | 0.05951 | -0.073243 | -0.16937 | -0.15564 | -0.21973 | 0.009156 | 0.013732 | 60.965 | 61.0428 | 122.7676 | 122.9828 | -0.073243 | 122.9324 | 61.0016 | -0.21973 | 122.9828 | -0.073243 | 61.0016 | 122.7676 | 122.9324 | -123.0103 | -123.143
96.7656 | 123.1476 | -60.9192 | 61.9858 | -0.04219 | 0.00011541 | 0.0016877 | 0.0015658 | 0.069077 | -0.0011643 | 0.071042 | -60.997 | 62.0499 | -61.0519 | -61.116 | 61.8668 | 0.073242 | 0.041199 | 0.09613 | 62.0041 | -61.116 | -0.13275 | 0.064087 | -0.07782 | -0.19684 | -0.11902 | -0.19684 | 0.01831 | 0.054932 | 60.9604 | 61.0153 | 122.7859 | 122.9691 | -0.07782 | 122.9233 | 60.9924 | -0.19684 | 122.9691 | -0.07782 | 60.9924 | 122.7859 | 122.9233 | -123.0377 | -123.1018
97.7656 | 123.1247 | -60.9146 | 62.0224 | -0.17952 | -0.0028754 | 0.00019226 | -0.00014316 | 0.067155 | -0.00052335 | 0.070188 | -61.0519 | 62.0499 | -61.0428 | -61.1526 | 61.821 | 0.064087 | 0.14648 | 0.09613 | 61.9858 | -61.1252 | -0.12817 | 0.027466 | -0.13733 | -0.23804 | -0.20142 | -0.21057 | -0.036621 | -0.009155 | 61.0611 | 61.0107 | 122.7356 | 122.9645 | -0.13733 | 122.9004 | 60.9787 | -0.21057 | 122.9645 | -0.13733 | 60.9787 | 122.7356 | 122.9004 | -123.0652 | -123.1476
98.7656 | 123.0835 | -60.9329 | 62.0041 | -2.0564 | -0.0020208 | -0.00023494 | -0.00035676 | 0.067795 | -0.0018051 | 0.069333 | -61.1023 | 62.0819 | -61.0336 | -61.1664 | 61.7889 | 0.054932 | 0.15564 | 0.10529 | 62.0041 | -61.116 | -0.10071 | 0.07782 | -0.16937 | -0.23346 | -0.21515 | -0.18311 | 0 | -0.068665 | 61.0886 | 61.0382 | 122.7219 | 123.0148 | -0.16937 | 122.937 | 60.9879 | -0.18311 | 123.0148 | -0.16937 | 60.9879 | 122.7219 | 122.937 | -123.0377 | -123.1201
99.7656 | 123.111 | -60.8963 | 62.0407 | -0.149 | -0.003089 | 0.00019226 | -0.00099756 | 0.068436 | -0.0011643 | 0.06677 | -61.0382 | 62.0453 | -61.0382 | -61.1618 | 61.8256 | 0.059509 | 0.13275 | 0.10986 | 62.0178 | -61.1023 | -0.14191 | 0.004578 | -0.14191 | -0.2655 | -0.21515 | -0.20599 | -0.022888 | 0 | 61.0291 | 61.0062 | 122.7219 | 122.9416 | -0.14191 | 122.9141 | 60.9558 | -0.20599 | 122.9416 | -0.14191 | 60.9558 | 122.7219 | 122.9141 | -123.0789 | -123.143
100.7656 | 123.0835 | -60.9146 | 62.027 | 0.026474 | -0.0024482 | 0.0040375 | 0.0015658 | 0.067795 | 0.0011857 | 0.070188 | -61.0703 | 62.0224 | -61.0748 | -61.1755 | 61.7981 | 0.045776 | 0.14191 | 0.082397 | 62.0224 | -61.0977 | -0.16022 | -0.004578 | -0.15564 | -0.26093 | -0.22888 | -0.18311 | -0.004578 | 0.004578 | 61.0565 | 60.997 | 122.7127 | 122.937 | -0.15564 | 122.937 | 60.9604 | -0.18311 | 122.937 | -0.15564 | 60.9604 | 122.7127 | 122.937 | -123.1018 | -123.1247
101.7656 | 123.111 | -60.9238 | 62.0087 | -0.15663 | -0.0015936 | -0.0021575 | 0.00049764 | 0.067795 | -0.0030869 | 0.068906 | -61.0519 | 62.0178 | -61.0199 | -61.1298 | 61.8256 | 0.059509 | 0.13275 | 0.10529 | 62.0041 | -61.1114 | -0.09613 | 0.009155 | -0.12817 | -0.20599 | -0.18311 | -0.18768 | -0.004578 | -0.032044 | 61.0565 | 61.0291 | 122.7493 | 122.9416 | -0.12817 | 122.9279 | 60.9833 | -0.18768 | 122.9416 | -0.12817 | 60.9833 | 122.7493 | 122.9279 | -123.0286 | -123.1201
102.7656 | 123.111 | -60.9009 | 62.0316 | -0.19478 | -0.0018072 | -0.0025847 | -0.00035676 | 0.066087 | -0.00030975 | 0.067838 | -61.0565 | 62.0361 | -61.0565 | -61.1526 | 61.7981 | 0.064087 | 0.13733 | 0.09613 | 62.0361 | -61.0886 | -0.15564 | 0.004578 | -0.15564 | -0.25177 | -0.23346 | -0.18768 | 0.004578 | 0 | 61.0382 | 60.997 | 122.699 | 122.937 | -0.15564 | 122.937 | 60.965 | -0.18768 | 122.937 | -0.15564 | 60.965 | 122.699 | 122.937 | -123.0881 | -123.1201
103.7656 | 123.0881 | -60.9055 | 62.027 | -0.15663 | -0.0022346 | -0.0030121 | -0.0012112 | 0.066514 | -0.0026595 | 0.071042 | -60.9375 | 62.0819 | -61.0245 | -61.1847 | 61.7981 | 0.036621 | 0.13733 | 0.09613 | 62.0178 | -61.1023 | -0.11902 | 0.054931 | -0.032043 | -0.27923 | -0.22888 | -0.19684 | -0.009156 | 0.086975 | 61.0428 | 61.0016 | 122.7036 | 122.9874 | -0.032043 | 122.9233 | 60.9421 | -0.19684 | 122.9874 | -0.032043 | 60.9421 | 122.7036 | 122.9233 | -123.0515 | -123.1293
104.7656 | 123.1247 | -60.8643 | 62.0178 | -0.14137 | -0.0035162 | -0.0036529 | -0.0033476 | 0.064164 | -0.0018051 | 0.06912 | -60.997 | 62.0041 | -61.0519 | -61.0886 | 61.8759 | 0.13275 | 0.064087 | 0.1831 | 61.9949 | -61.0657 | -0.18768 | -0.013733 | -0.13275 | -0.2243 | -0.14191 | -0.20142 | -0.022888 | 0.054932 | 60.9283 | 61.0474 | 122.7402 | 122.8683 | -0.13275 | 122.8592 | 60.997 | -0.20142 | 122.8683 | -0.13275 | 60.997 | 122.7402 | 122.8592 | -123.0698 | -123.0835
105.7656 | 123.1796 | -60.878 | 62.0041 | -0.14137 | -0.0062934 | 0.00061946 | -0.0018522 | 0.065446 | -0.0039413 | 0.07147 | -60.9879 | 61.9675 | -60.9879 | -61.0611 | 61.9034 | 0.14191 | 0.022888 | 0.21057 | 61.9492 | -61.0748 | -0.10986 | -0.036621 | -0.10986 | -0.1831 | -0.10071 | -0.19684 | -0.054931 | 0 | 60.9009 | 61.0886 | 122.7814 | 122.8455 | -0.10986 | 122.8271 | 61.0199 | -0.19684 | 122.8455 | -0.10986 | 61.0199 | 122.7814 | 122.8271 | -122.9919 | -123.0789
106.7656 | 123.1064 | -60.9009 | 62.0087 | -0.16426 | -0.0037298 | 0.0012605 | -0.0012112 | 0.064164 | -0.0020187 | 0.066556 | -60.9924 | 61.9766 | -61.0062 | -61.1023 | 61.8759 | 0.11902 | 0.082397 | 0.16937 | 61.972 | -61.084 | -0.10529 | -0.032043 | -0.091553 | -0.20142 | -0.13275 | -0.1831 | -0.036621 | 0.013733 | 60.9833 | 61.0703 | 122.7768 | 122.8775 | -0.091553 | 122.8729 | 61.0199 | -0.1831 | 122.8775 | -0.091553 | 61.0199 | 122.7768 | 122.8729 | -123.0148 | -123.0927
107.7656 | 123.1522 | -60.8734 | 62.0224 | -0.15663 | -0.0033026 | -0.0021575 | -0.0022794 | 0.064164 | 0.00011745 | 0.069333 | -60.9833 | 61.972 | -60.9924 | -61.0748 | 61.8896 | 0.14191 | 0.018311 | 0.20142 | 61.94 | -61.0657 | -0.11902 | -0.050354 | -0.10986 | -0.20142 | -0.13275 | -0.19226 | -0.082398 | 0.009156 | 60.8917 | 61.0748 | 122.7631 | 122.8455 | -0.10986 | 122.8134 | 61.0153 | -0.19226 | 122.8455 | -0.10986 | 61.0153 | 122.7631 | 122.8134 | -123.0148 | -123.0881
108.7656 | 123.1522 | -60.8871 | 62.0132 | -0.2253 | -0.0039434 | -0.0019439 | -0.0012112 | 0.063737 | -0.0015915 | 0.066984 | -61.0016 | 61.972 | -61.0382 | -61.0931 | 61.853 | 0.10071 | 0.086975 | 0.16937 | 61.9812 | -61.0794 | -0.15106 | -0.041199 | -0.11444 | -0.20599 | -0.16022 | -0.19226 | -0.032044 | 0.036621 | 60.9741 | 61.0565 | 122.7402 | 122.8592 | -0.11444 | 122.8683 | 60.9879 | -0.19226 | 122.8592 | -0.11444 | 60.9879 | 122.7402 | 122.8683 | -123.0515 | -123.0927
109.7656 | 123.175 | -60.8963 | 62.0087 | -0.149 | -0.0054388 | -0.0027985 | -0.0020658 | 0.064591 | -0.0024459 | 0.070188 | -60.9741 | 61.9537 | -61.0291 | -61.0703 | 61.8896 | 0.12817 | 0.027466 | 0.20599 | 61.9949 | -61.0611 | -0.13275 | -0.054932 | -0.07782 | -0.17395 | -0.11902 | -0.16479 | -0.013733 | 0.054932 | 60.9238 | 61.1023 | 122.7859 | 122.85 | -0.07782 | 122.8912 | 61.0245 | -0.16479 | 122.85 | -0.07782 | 61.0245 | 122.7859 | 122.8912 | -123.0377 | -123.0698
110.7656 | 123.1979 | -60.878 | 62.0178 | -0.080337 | -0.0045844 | -0.0045075 | -0.00057036 | 0.06395 | -0.0047957 | 0.069761 | -60.9741 | 61.9492 | -61.0153 | -61.0428 | 61.9034 | 0.14648 | -0.009155 | 0.21515 | 61.9446 | -61.0519 | -0.13733 | -0.068664 | -0.09613 | -0.16479 | -0.11444 | -0.17395 | -0.073242 | 0.041199 | 60.8688 | 61.0931 | 122.7814 | 122.8271 | -0.09613 | 122.8226 | 61.0245 | -0.17395 | 122.8271 | -0.09613 | 61.0245 | 122.7814 | 122.8226 | -123.0331 | -123.0698
111.7656 | 123.23 | -60.8688 | 61.9629 | -0.057449 | -0.0045844 | -0.0013031 | -0.0022794 | 0.063309 | -0.0018051 | 0.068052 | -61.0016 | 61.9308 | -61.0336 | -61.0428 | 61.908 | 0.15564 | -0.068665 | 0.21973 | 61.9034 | -61.0382 | -0.1648 | -0.032044 | -0.13275 | -0.17395 | -0.054932 | -0.16937 | -0.05951 | 0.032043 | 60.8002 | 61.0886 | 122.7768 | 122.7997 | -0.13275 | 122.7722 | 61.0245 | -0.16937 | 122.7997 | -0.13275 | 61.0245 | 122.7768 | 122.7722 | -122.9965 | -123.0011
112.7656 | 123.2071 | -60.8826 | 61.9949 | 0.011215 | -0.003089 | -0.0010895 | -0.0012112 | 0.063309 | -0.00095055 | 0.067197 | -61.0245 | 61.94 | -61.0153 | -61.0611 | 61.8805 | 0.12817 | -0.07782 | 0.17853 | 61.9217 | -61.084 | -0.13275 | -0.054932 | -0.14191 | -0.17853 | -0.11444 | -0.20142 | -0.073242 | -0.009155 | 60.8047 | 61.0611 | 122.7631 | 122.8226 | -0.14191 | 122.8043 | 61.0107 | -0.20142 | 122.8226 | -0.14191 | 61.0107 | 122.7631 | 122.8043 | -123.0103 | -123.0789
113.7656 | 123.2346 | -60.8688 | 62.0041 | -0.17189 | -0.0043708 | -0.0032257 | 0.00049764 | 0.063309 | -0.0030869 | 0.068479 | -60.9558 | 61.9171 | -61.0153 | -61.0199 | 61.9537 | 0.14648 | -0.045776 | 0.2243 | 61.9446 | -61.0565 | -0.14649 | -0.086975 | -0.086976 | -0.15106 | -0.050354 | -0.18768 | -0.059509 | 0.059509 | 60.8231 | 61.0931 | 122.8226 | 122.7859 | -0.086976 | 122.8134 | 61.0153 | -0.18768 | 122.7859 | -0.086976 | 61.0153 | 122.8226 | 122.8134 | -123.0194 | -123.0606
114.7656 | 123.2346 | -60.8643 | 61.9904 | -0.065079 | -0.0060798 | -0.0013031 | 0.00049764 | 0.063309 | -0.0022323 | 0.068479 | -60.9558 | 61.9263 | -61.0153 | -61.0336 | 61.9217 | 0.15106 | -0.073242 | 0.21973 | 61.9629 | -61.0199 | -0.15106 | -0.064086 | -0.091553 | -0.16937 | -0.068664 | -0.15564 | -0.027465 | 0.059509 | 60.791 | 61.084 | 122.7859 | 122.7905 | -0.091553 | 122.8271 | 61.0153 | -0.15564 | 122.7905 | -0.091553 | 61.0153 | 122.7859 | 122.8271 | -123.0057 | -123.0103
115.7656 | 123.2391 | -60.8826 | 61.9583 | -0.10323 | -0.0045844 | -0.0047211 | 0.0011386 | 0.06395 | -0.0028731 | 0.068265 | -60.7269 | 61.972 | -60.9833 | -61.0199 | 61.853 | 0.14191 | -0.07782 | 0.23804 | 61.9446 | -61.0474 | -0.10071 | 0.013733 | 0.15564 | -0.13733 | -0.10529 | -0.16479 | -0.013733 | 0.25635 | 60.8047 | 61.1206 | 122.7356 | 122.8546 | 0.15564 | 122.8271 | 61.0245 | -0.16479 | 122.8546 | 0.15564 | 61.0245 | 122.7356 | 122.8271 | -122.9416 | -123.0057
116.7656 | 123.1842 | -60.8871 | 61.9766 | -0.11085 | -0.0039434 | -0.0034393 | 0.00092504 | 0.063309 | -0.0047957 | 0.067197 | -60.9512 | 61.9492 | -60.997 | -61.0336 | 61.9766 | 0.42114 | 0.009155 | 0 | 61.9766 | -61.0382 | -0.10986 | -0.027466 | -0.064087 | -0.14648 | 0 | -0.15106 | 0 | 0.045776 | 60.8963 | 60.8871 | 122.8638 | 122.8363 | -0.064087 | 122.8638 | 61.3083 | -0.15106 | 122.8363 | -0.064087 | 61.3083 | 122.8638 | 122.8638 | -122.9736 | -123.0148
117.7656 | 123.2117 | -60.878 | 61.9812 | -0.026932 | -0.0050116 | 0.00019226 | 0.0015658 | 0.062882 | -0.0028731 | 0.069761 | -60.9558 | 61.9217 | -61.0245 | -61.0153 | 61.9263 | 0.16479 | -0.041199 | 0.21973 | 61.9492 | -61.0428 | -0.14648 | -0.059509 | -0.07782 | -0.13733 | -0.054931 | -0.16479 | -0.032043 | 0.068664 | 60.8368 | 61.0977 | 122.8043 | 122.7997 | -0.07782 | 122.8271 | 61.0428 | -0.16479 | 122.7997 | -0.07782 | 61.0428 | 122.8043 | 122.8271 | -123.0057 | -123.024
118.7656 | 123.1888 | -60.8871 | 61.9766 | 0.041733 | -0.0035162 | -0.0055755 | 0.0024202 | 0.063737 | -0.0015915 | 0.067197 | -61.0199 | 61.9263 | -61.0291 | -61.0931 | 61.8805 | 0.10071 | -0.059509 | 0.14648 | 61.8851 | -61.0565 | -0.14191 | -0.050354 | -0.13275 | -0.20599 | -0.096131 | -0.16937 | -0.091553 | 0.009156 | 60.8276 | 61.0336 | 122.7676 | 122.8134 | -0.13275 | 122.7722 | 60.9879 | -0.16937 | 122.8134 | -0.13275 | 60.9879 | 122.7676 | 122.7722 | -123.0057 | -123.0331
119.7656 | 123.2346 | -60.8871 | 61.9629 | -0.019302 | -0.0043708 | 0.0029693 | -0.0012112 | 0.063309 | -0.0020187 | 0.068906 | -60.9787 | 61.9171 | -61.0291 | -61.0428 | 61.9263 | 0.15106 | -0.059509 | 0.21057 | 61.9354 | -61.0474 | -0.14191 | -0.045777 | -0.091553 | -0.15564 | -0.036621 | -0.16022 | -0.027466 | 0.050354 | 60.8276 | 61.0977 | 122.8134 | 122.8043 | -0.091553 | 122.8226 | 61.0382 | -0.16022 | 122.8043 | -0.091553 | 61.0382 | 122.8134 | 122.8226 | -122.9919 | -123.0103
120.7656 | 123.23 | -60.8597 | 61.9812 | -0.04219 | -0.0045844 | -0.0034393 | 7.0444e-05 | 0.063523 | -0.00073695 | 0.069333 | -61.0016 | 61.9308 | -61.0153 | -61.0565 | 61.8896 | 0.13733 | -0.059509 | 0.20142 | 61.9217 | -61.0703 | -0.15564 | -0.050354 | -0.14191 | -0.19684 | -0.091553 | -0.21057 | -0.059509 | 0.013733 | 60.8002 | 61.0611 | 122.7493 | 122.7905 | -0.14191 | 122.7814 | 60.997 | -0.21057 | 122.7905 | -0.14191 | 60.997 | 122.7493 | 122.7814 | -122.9965 | -123.0515
121.7656 | 123.2117 | -60.878 | 61.972 | 0.011215 | -0.003089 | -0.0013031 | -0.00014316 | 0.062669 | -0.0028731 | 0.066129 | -61.0016 | 61.94 | -61.0336 | -61.0794 | 61.8942 | 0.11444 | -0.064087 | 0.16937 | 61.9492 | -61.0611 | -0.15564 | -0.032044 | -0.1236 | -0.20142 | -0.07782 | -0.1831 | -0.022888 | 0.032043 | 60.8139 | 61.0474 | 122.7722 | 122.818 | -0.1236 | 122.8271 | 60.9924 | -0.1831 | 122.818 | -0.1236 | 60.9924 | 122.7722 | 122.8271 | -123.0057 | -123.0331
122.7656 | 123.2483 | -60.8917 | 61.972 | -0.072708 | -0.0015936 | -0.0036529 | 0.00071144 | 0.063096 | -0.0026595 | 0.069974 | -60.9741 | 61.9034 | -61.0107 | -60.997 | 61.9354 | 0.16479 | -0.086975 | 0.21973 | 61.9263 | -61.0519 | -0.11902 | -0.068665 | -0.082397 | -0.10528 | -0.036621 | -0.16022 | -0.045776 | 0.036621 | 60.8047 | 61.1115 | 122.8271 | 122.7951 | -0.082397 | 122.818 | 61.0565 | -0.16022 | 122.7951 | -0.082397 | 61.0565 | 122.8271 | 122.818 | -122.9828 | -123.024
123.7656 | 123.2117 | -60.8505 | 61.9766 | -0.034561 | -0.0035162 | -0.0010895 | 0.00028404 | 0.060532 | -0.0024459 | 0.068265 | -60.997 | 61.908 | -61.0291 | -61.0291 | 61.9308 | 0.14648 | -0.068665 | 0.21515 | 61.9034 | -61.0519 | -0.17853 | -0.068665 | -0.14648 | -0.17853 | -0.045777 | -0.20142 | -0.073243 | 0.032044 | 60.7819 | 61.0657 | 122.7814 | 122.7585 | -0.14648 | 122.7539 | 60.997 | -0.20142 | 122.7585 | -0.14648 | 60.997 | 122.7814 | 122.7539 | -123.0057 | -123.0286
124.7656 | 123.2117 | -60.878 | 61.9858 | -0.04982 | -0.0035162 | -0.0047211 | -0.0012112 | 0.063096 | -9.6146e-05 | 0.068265 | -61.0107 | 61.8942 | -61.0153 | -61.0519 | 61.9171 | 0.14191 | -0.082397 | 0.19226 | 61.94 | -61.0611 | -0.13733 | -0.091553 | -0.13275 | -0.17395 | -0.068665 | -0.1831 | -0.045777 | 0.004578 | 60.7956 | 61.0703 | 122.7951 | 122.7722 | -0.13275 | 122.818 | 61.0199 | -0.1831 | 122.7722 | -0.13275 | 61.0199 | 122.7951 | 122.818 | -123.0011 | -123.0469
125.7656 | 123.1659 | -60.8734 | 61.9812 | -0.072708 | -0.0060798 | -0.0032257 | 0.0015658 | 0.064378 | -0.0028731 | 0.068693 | -61.0565 | 61.9171 | -61.0565 | -61.1023 | 61.8622 | 0.054932 | -0.064087 | 0.10071 | 61.9446 | -61.0794 | -0.18311 | -0.064087 | -0.18311 | -0.22888 | -0.11902 | -0.20599 | -0.036621 | 0 | 60.8093 | 60.9741 | 122.7356 | 122.7905 | -0.18311 | 122.818 | 60.9283 | -0.20599 | 122.7905 | -0.18311 | 60.9283 | 122.7356 | 122.818 | -123.0377 | -123.0606
126.7656 | 123.1934 | -60.8826 | 61.9812 | -0.034561 | -0.003089 | 0.0012605 | 0.0024202 | 0.06395 | -0.0037277 | 0.070402 | -61.0291 | 61.9171 | -61.0199 | -61.0657 | 61.8896 | 0.11902 | -0.068665 | 0.16022 | 61.8896 | -61.0611 | -0.13733 | -0.064087 | -0.14648 | -0.18311 | -0.091553 | -0.17853 | -0.091553 | -0.009156 | 60.8139 | 61.0428 | 122.7722 | 122.7997 | -0.14648 | 122.7722 | 61.0016 | -0.17853 | 122.7997 | -0.14648 | 61.0016 | 122.7722 | 122.7722 | -123.0011 | -123.0423
127.7656 | 123.2117 | -60.8597 | 61.9812 | -0.034561 | -0.006507 | 0.00040586 | 7.0444e-05 | 0.060105 | -0.0028731 | 0.069547 | -61.0382 | 61.9263 | -61.0153 | -61.0565 | 61.8896 | 0.09613 | -0.054932 | 0.13275 | 61.9034 | -61.0657 | -0.15564 | -0.054931 | -0.17853 | -0.19684 | -0.091553 | -0.20599 | -0.07782 | -0.022888 | 60.8047 | 60.9924 | 122.7493 | 122.7859 | -0.17853 | 122.7631 | 60.9558 | -0.20599 | 122.7859 | -0.17853 | 60.9558 | 122.7493 | 122.7631 | -122.9965 | -123.0469
128.7656 | 123.2162 | -60.8643 | 61.972 | -0.080337 | -0.0056524 | -0.0017303 | 0.00028404 | 0.064378 | -0.0020187 | 0.067624 | -60.9924 | 61.9217 | -61.0291 | -61.0199 | 61.9125 | 0.14648 | -0.073242 | 0.19684 | 61.9263 | -61.0382 | -0.16479 | -0.050354 | -0.12817 | -0.15564 | -0.059509 | -0.17395 | -0.045776 | 0.036621 | 60.791 | 61.0611 | 122.7768 | 122.7859 | -0.12817 | 122.7905 | 61.0107 | -0.17395 | 122.7859 | -0.12817 | 61.0107 | 122.7768 | 122.7905 | -123.0011 | -123.0103
129.7656 | 123.2117 | -60.8643 | 61.9675 | -0.011673 | -0.0062934 | -0.0021575 | 0.0017794 | 0.062882 | -0.0039413 | 0.069761 | -61.0016 | 61.9171 | -61.0153 | -61.0428 | 61.9125 | 0.13733 | -0.068665 | 0.1831 | 61.908 | -61.0336 | -0.15106 | -0.050354 | -0.13733 | -0.17853 | -0.054931 | -0.16937 | -0.059509 | 0.013733 | 60.7956 | 61.0474 | 122.7768 | 122.7814 | -0.13733 | 122.7722 | 61.0016 | -0.16937 | 122.7814 | -0.13733 | 61.0016 | 122.7768 | 122.7722 | -122.9828 | -123.0011
130.7656 | 123.1934 | -60.8643 | 61.9766 | -0.034561 | -0.0035162 | -0.0042937 | -0.00078396 | 0.064164 | -0.0039413 | 0.067624 | -61.0107 | 61.9263 | -61.0382 | -61.0657 | 61.8988 | 0.10986 | -0.041199 | 0.16479 | 61.9217 | -61.0657 | -0.17395 | -0.050354 | -0.14648 | -0.20142 | -0.07782 | -0.20142 | -0.054932 | 0.027466 | 60.8231 | 61.0291 | 122.7631 | 122.7905 | -0.14648 | 122.7859 | 60.9741 | -0.20142 | 122.7905 | -0.14648 | 60.9741 | 122.7631 | 122.7859 | -123.0148 | -123.0423
131.7656 | 123.175 | -60.8505 | 61.9858 | 0.0035856 | -0.0067206 | -0.0019439 | 0.0022066 | 0.061814 | -0.0028731 | 0.067838 | -61.0428 | 61.9171 | -61.0382 | -61.084 | 61.8896 | 0.10529 | -0.059509 | 0.14191 | 61.9125 | -61.0565 | -0.18768 | -0.068665 | -0.19226 | -0.23346 | -0.096131 | -0.20599 | -0.073242 | -0.004578 | 60.791 | 60.9924 | 122.7402 | 122.7676 | -0.19226 | 122.7631 | 60.9558 | -0.20599 | 122.7676 | -0.19226 | 60.9558 | 122.7402 | 122.7631 | -123.024 | -123.0423
132.7656 | 123.1338 | -60.9009 | 61.9629 | 0.1104 | -0.0035162 | -0.0027985 | 0.0013522 | 0.063096 | -0.0018051 | 0.064847 | -61.0519 | 61.9263 | -61.0336 | -60.9604 | 61.8713 | 0.004578 | -0.064087 | 0.050354 | 61.9171 | -61.0428 | -0.13275 | -0.036621 | -0.15106 | -0.059509 | -0.091553 | -0.14191 | -0.045777 | -0.018311 | 60.8368 | 60.9512 | 122.7722 | 122.8271 | -0.15106 | 122.818 | 60.9055 | -0.14191 | 122.8271 | -0.15106 | 60.9055 | 122.7722 | 122.818 | -122.9965 | -123.0057
133.7656 | 123.1888 | -60.8963 | 61.9812 | 0.1104 | -0.0060798 | -0.0021575 | -0.00035676 | 0.062455 | -0.0013779 | 0.067624 | -61.0336 | 61.9308 | -61.0291 | -61.1069 | 61.8622 | 0.07782 | -0.045776 | 0.10986 | 61.9034 | -61.0611 | -0.13275 | -0.050354 | -0.13733 | -0.21057 | -0.11902 | -0.16479 | -0.07782 | -0.004577 | 60.8505 | 61.0062 | 122.7585 | 122.8271 | -0.13733 | 122.7997 | 60.9741 | -0.16479 | 122.8271 | -0.13733 | 60.9741 | 122.7585 | 122.7997 | -123.0103 | -123.0423
134.7656 | 123.1979 | -60.8826 | 61.9904 | 0.14092 | -0.007575 | -0.0015167 | 0.0011386 | 0.063096 | -0.0047957 | 0.068906 | -61.0519 | 61.9125 | -61.0336 | -61.0977 | 61.8484 | 0.059509 | -0.054932 | 0.10529 | 61.9446 | -61.0611 | -0.15106 | -0.077819 | -0.16937 | -0.21515 | -0.14191 | -0.17853 | -0.045776 | -0.018311 | 60.8276 | 60.9879 | 122.731 | 122.7951 | -0.16937 | 122.8271 | 60.9421 | -0.17853 | 122.7951 | -0.16937 | 60.9421 | 122.731 | 122.8271 | -123.024 | -123.0515
135.7656 | 123.1888 | -60.8734 | 61.9766 | -0.04982 | -0.006507 | -0.00087594 | 0.00028404 | 0.063096 | -0.0026595 | 0.067624 | -61.0245 | 61.9492 | -61.0382 | -61.0657 | 61.8805 | 0.10986 | -0.068665 | 0.14648 | 61.908 | -61.0657 | -0.16479 | -0.027466 | -0.15106 | -0.19226 | -0.096131 | -0.19226 | -0.068665 | 0.013733 | 60.8047 | 61.0199 | 122.7539 | 122.8226 | -0.15106 | 122.7814 | 60.9833 | -0.19226 | 122.8226 | -0.15106 | 60.9833 | 122.7539 | 122.7814 | -123.0148 | -123.0423
136.7656 | 123.175 | -60.8826 | 61.9766 | 0.0035856 | -0.0024482 | -0.0032257 | 0.00049764 | 0.062028 | -0.0020187 | 0.069547 | -61.0245 | 61.9034 | -61.0291 | -61.0748 | 61.8805 | 0.10071 | -0.050354 | 0.12817 | 61.908 | -61.0565 | -0.14648 | -0.073243 | -0.14191 | -0.19226 | -0.096131 | -0.17395 | -0.068665 | 0.004578 | 60.8322 | 61.0107 | 122.7631 | 122.7859 | -0.14191 | 122.7905 | 60.9833 | -0.17395 | 122.7859 | -0.14191 | 60.9833 | 122.7631 | 122.7905 | -123.0057 | -123.0331
137.7656 | 123.175 | -60.8917 | 61.9812 | 0.049362 | -0.0041572 | -0.0038665 | -0.00035676 | 0.062241 | -0.0041549 | 0.069547 | -61.0428 | 61.9263 | -61.0291 | -61.0977 | 61.8805 | 0.082397 | -0.064087 | 0.10529 | 61.9034 | -61.0519 | -0.13733 | -0.054931 | -0.15106 | -0.20599 | -0.10071 | -0.16022 | -0.07782 | -0.013733 | 60.8276 | 60.997 | 122.7722 | 122.818 | -0.15106 | 122.7951 | 60.9741 | -0.16022 | 122.818 | -0.15106 | 60.9741 | 122.7722 | 122.7951 | -123.0103 | -123.0331
138.7656 | 123.143 | -60.9329 | 61.9583 | 0.15617 | -0.0041572 | -0.0045075 | 0.00028404 | 0.065446 | -0.0028731 | 0.069761 | -61.0428 | 61.9354 | -61.0382 | -61.1114 | 61.8256 | 0.045776 | -0.068665 | 0.064087 | 61.908 | -61.0565 | -0.10529 | -0.022888 | -0.10986 | -0.17853 | -0.13275 | -0.1236 | -0.050354 | -0.004578 | 60.8643 | 60.997 | 122.7585 | 122.8683 | -0.10986 | 122.8409 | 60.9787 | -0.1236 | 122.8683 | -0.10986 | 60.9787 | 122.7585 | 122.8409 | -122.9965 | -123.0148
139.7656 | 123.1567 | -60.8963 | 61.9629 | 0.1638 | -0.0043708 | -0.0032257 | -0.00014316 | 0.062455 | -0.0020187 | 0.066984 | -61.0382 | 61.908 | -61.0153 | -61.1114 | 61.853 | 0.036621 | -0.082397 | 0.064087 | 61.8668 | -61.0611 | -0.11902 | -0.054932 | -0.14191 | -0.21515 | -0.10986 | -0.16479 | -0.096131 | -0.022888 | 60.8139 | 60.9604 | 122.7493 | 122.8043 | -0.14191 | 122.7631 | 60.9329 | -0.16479 | 122.8043 | -0.14191 | 60.9329 | 122.7493 | 122.7631 | -122.9782 | -123.024
140.7656 | 123.1659 | -60.8643 | 61.9675 | 0.14092 | -0.004798 | -0.0045075 | 0.00028404 | 0.065018 | -0.0020187 | 0.068906 | -61.0428 | 61.9171 | -61.0336 | -61.1069 | 61.8622 | 0.041199 | -0.054932 | 0.059509 | 61.9354 | -61.0199 | -0.16937 | -0.050354 | -0.17853 | -0.24262 | -0.10528 | -0.15564 | -0.032043 | -0.009156 | 60.8093 | 60.9238 | 122.7264 | 122.7814 | -0.17853 | 122.7997 | 60.9055 | -0.15564 | 122.7814 | -0.17853 | 60.9055 | 122.7264 | 122.7997 | -123.0011 | -122.9874
141.7656 | 123.1888 | -60.8871 | 61.9675 | 0.011215 | -0.0037298 | -0.0049347 | -0.00078396 | 0.062455 | -0.0024459 | 0.069547 | -61.0611 | 61.9263 | -61.0382 | -61.0931 | 61.8439 | 0.068665 | -0.050354 | 0.11444 | 61.8988 | -61.0565 | -0.15106 | -0.041198 | -0.17395 | -0.20599 | -0.1236 | -0.16937 | -0.068664 | -0.022888 | 60.8368 | 61.0016 | 122.731 | 122.8134 | -0.17395 | 122.7859 | 60.9558 | -0.16937 | 122.8134 | -0.17395 | 60.9558 | 122.731 | 122.7859 | -123.0057 | -123.024
142.7656 | 123.1613 | -60.8826 | 61.9583 | 0.095139 | -0.0026618 | -0.0027985 | 0.0015658 | 0.064378 | -0.0020187 | 0.071256 | -60.9604 | 61.9492 | -61.0062 | -61.0886 | 61.8484 | 0.050354 | -0.045776 | 0.09613 | 61.94 | -61.0428 | -0.1236 | -0.009155 | -0.07782 | -0.20599 | -0.10986 | -0.16022 | -0.018311 | 0.045777 | 60.8368 | 60.9787 | 122.731 | 122.8317 | -0.07782 | 122.8226 | 60.9329 | -0.16022 | 122.8317 | -0.07782 | 60.9329 | 122.731 | 122.8226 | -122.9645 | -123.0011
143.7656 | 123.1476 | -60.878 | 61.9583 | 0.13329 | -0.0041572 | -0.0040801 | 0.00092504 | 0.061173 | -0.0018051 | 0.066343 | -61.0565 | 61.9492 | -61.0291 | -61.116 | 61.8301 | 0.064087 | 0.022888 | 0.086975 | 61.9217 | -61.0611 | -0.15106 | -0.009155 | -0.17853 | -0.23804 | -0.12817 | -0.1831 | -0.036621 | -0.027466 | 60.9009 | 60.965 | 122.7081 | 122.8271 | -0.17853 | 122.7997 | 60.9421 | -0.1831 | 122.8271 | -0.17853 | 60.9421 | 122.7081 | 122.7997 | -122.9874 | -123.0194
144.7656 | 123.1567 | -60.8963 | 61.972 | 0.095139 | -0.0041572 | 0.00019226 | 0.0013522 | 0.062455 | -0.00052335 | 0.069761 | -61.0657 | 61.9125 | -61.0336 | -61.1298 | 61.8347 | 0.054932 | -0.059509 | 0.086975 | 61.8988 | -61.0886 | -0.13733 | -0.059509 | -0.16937 | -0.23346 | -0.13733 | -0.19226 | -0.073242 | -0.032044 | 60.8368 | 60.9833 | 122.731 | 122.8088 | -0.16937 | 122.7951 | 60.9512 | -0.19226 | 122.8088 | -0.16937 | 60.9512 | 122.731 | 122.7951 | -123.0057 | -123.0606
145.7656 | 123.1934 | -60.8963 | 61.9629 | 0.20958 | -0.0028754 | -0.0025847 | 0.002634 | 0.063309 | -0.0026595 | 0.069974 | -61.0062 | 61.8851 | -61.0382 | -61.0931 | 61.8484 | 0.045776 | -0.14191 | 0.082397 | 61.9034 | -61.084 | -0.14191 | -0.07782 | -0.10986 | -0.19684 | -0.11444 | -0.18768 | -0.05951 | 0.032043 | 60.7544 | 60.9787 | 122.7448 | 122.7814 | -0.10986 | 122.7997 | 60.9421 | -0.18768 | 122.7814 | -0.10986 | 60.9421 | 122.7448 | 122.7997 | -123.0011 | -123.0469
146.7656 | 123.1888 | -60.8917 | 61.9537 | 0.20195 | -0.0024482 | -0.0040801 | -0.00035676 | 0.064805 | -0.0039413 | 0.068052 | -60.9924 | 61.9125 | -61.0062 | -61.084 | 61.8759 | 0.064087 | -0.15106 | 0.086975 | 61.9034 | -61.0382 | -0.11444 | -0.041198 | -0.10071 | -0.19226 | -0.077819 | -0.14648 | -0.050354 | 0.013733 | 60.7407 | 60.9787 | 122.7676 | 122.8043 | -0.10071 | 122.7951 | 60.9558 | -0.14648 | 122.8043 | -0.10071 | 60.9558 | 122.7676 | 122.7951 | -122.9599 | -122.9919
147.7656 | 123.1476 | -60.9055 | 61.9446 | 0.20958 | -0.0060798 | -0.0042937 | 0.00028404 | 0.06395 | -0.0030869 | 0.068052 | -61.0291 | 61.9171 | -61.0428 | -61.0931 | 61.8301 | 0.036621 | -0.10529 | 0.068665 | 61.8759 | -61.0748 | -0.13733 | -0.027466 | -0.1236 | -0.18768 | -0.11444 | -0.16937 | -0.068664 | 0.013733 | 60.8002 | 60.9741 | 122.7356 | 122.8226 | -0.1236 | 122.7814 | 60.9421 | -0.16937 | 122.8226 | -0.1236 | 60.9421 | 122.7356 | 122.7814 | -122.9874 | -123.0194
148.7656 | 123.1613 | -60.8826 | 61.9629 | 0.20958 | -0.003089 | -0.0042937 | 0.0030612 | 0.063096 | -0.0028731 | 0.070402 | -61.0245 | 61.908 | -61.0428 | -61.0977 | 61.8484 | 0.032043 | -0.14648 | 0.07782 | 61.8759 | -61.0428 | -0.16022 | -0.054932 | -0.14191 | -0.21515 | -0.11444 | -0.16022 | -0.086975 | 0.018311 | 60.7361 | 60.9604 | 122.731 | 122.7905 | -0.14191 | 122.7585 | 60.9146 | -0.16022 | 122.7905 | -0.14191 | 60.9146 | 122.731 | 122.7585 | -123.0057 | -123.0057
149.7656 | 123.1567 | -60.9009 | 61.9675 | 0.15617 | -0.0039434 | -0.0019439 | 0.00092504 | 0.062241 | -0.0022323 | 0.068479 | -61.0382 | 61.9217 | -61.0519 | -61.116 | 61.8439 | 0.045776 | -0.07782 | 0.064087 | 61.9171 | -61.0611 | -0.15106 | -0.045776 | -0.13733 | -0.21515 | -0.1236 | -0.16022 | -0.050354 | 0.013733 | 60.8231 | 60.965 | 122.7448 | 122.8226 | -0.13733 | 122.818 | 60.9467 | -0.16022 | 122.8226 | -0.13733 | 60.9467 | 122.7448 | 122.818 | -123.0194 | -123.0286
150.7656 | 123.1979 | -60.8688 | 61.9446 | -0.04982 | -0.004798 | 0.0014741 | -0.0012112 | 0.062028 | -0.0028731 | 0.068906 | -60.997 | 61.9125 | -61.0199 | -61.0519 | 61.9217 | 0.14191 | -0.073242 | 0.20142 | 61.9125 | -61.0382 | -0.15106 | -0.032043 | -0.12817 | -0.18311 | -0.022888 | -0.16937 | -0.032043 | 0.022888 | 60.7956 | 61.0703 | 122.7905 | 122.7814 | -0.12817 | 122.7814 | 61.0107 | -0.16937 | 122.7814 | -0.12817 | 61.0107 | 122.7905 | 122.7814 | -122.9645 | -122.9828
151.7656 | 123.1705 | -60.8826 | 61.9583 | 0.20958 | -0.0035162 | -0.0019439 | 0.00028404 | 0.062241 | -0.0028731 | 0.069547 | -61.0291 | 61.9125 | -61.0428 | -61.1069 | 61.8347 | 0.032043 | -0.11444 | 0.07782 | 61.8851 | -61.0611 | -0.16022 | -0.045776 | -0.14648 | -0.22431 | -0.1236 | -0.17853 | -0.073242 | 0.013733 | 60.7681 | 60.9604 | 122.7173 | 122.7951 | -0.14648 | 122.7676 | 60.9146 | -0.17853 | 122.7951 | -0.14648 | 60.9146 | 122.7173 | 122.7676 | -123.0011 | -123.0194
152.7656 | 123.2071 | -60.878 | 61.9492 | 0.2401 | -0.0041572 | -0.00066214 | 0.005411 | 0.065446 | -0.0050095 | 0.070188 | -60.9833 | 61.8942 | -61.0245 | -61.0153 | 61.8942 | 0.07782 | -0.15106 | 0.09613 | 61.8896 | -61.0519 | -0.14648 | -0.054932 | -0.10528 | -0.13733 | -0.054932 | -0.17395 | -0.05951 | 0.041199 | 60.7269 | 60.9741 | 122.7722 | 122.7722 | -0.10528 | 122.7676 | 60.9558 | -0.17395 | 122.7722 | -0.10528 | 60.9558 | 122.7722 | 122.7676 | -122.9736 | -123.0011
153.7656 | 123.2483 | -60.9009 | 61.9446 | 0.31639 | -0.0041572 | -0.0038665 | 0.001993 | 0.065018 | -0.0033005 | 0.067197 | -60.9879 | 61.8896 | -61.0474 | -61.0611 | 61.8805 | 0.064087 | -0.17853 | 0.086975 | 61.8851 | -61.0886 | -0.14648 | -0.054932 | -0.086975 | -0.16022 | -0.064087 | -0.18768 | -0.059509 | 0.059509 | 60.7224 | 60.9879 | 122.7814 | 122.7905 | -0.086975 | 122.786 | 60.965 | -0.18768 | 122.7905 | -0.086975 | 60.965 | 122.7814 | 122.786 | -122.9919 | -123.0331
154.7656 | 123.2025 | -60.8917 | 61.9537 | 0.14854 | -0.0037298 | -0.0010895 | 0.0045566 | 0.065232 | -0.0024459 | 0.067838 | -61.0062 | 61.94 | -61.0245 | -61.0703 | 61.8805 | 0.064087 | -0.16937 | 0.09613 | 61.8713 | -61.0794 | -0.13275 | -0.013733 | -0.11444 | -0.17853 | -0.073242 | -0.18768 | -0.082397 | 0.01831 | 60.7224 | 60.9879 | 122.7722 | 122.8317 | -0.11444 | 122.7631 | 60.9558 | -0.18768 | 122.8317 | -0.11444 | 60.9558 | 122.7722 | 122.7631 | -122.9782 | -123.0331
155.7656 | 123.2208 | -60.8826 | 61.9583 | 0.25536 | -0.0052252 | -0.00087594 | 0.0022066 | 0.065873 | -9.6146e-05 | 0.069333 | -61.1572 | 61.9354 | -61.0611 | -61.0428 | 61.8713 | 0.073242 | -0.16937 | 0.086975 | 61.8759 | -61.0748 | -0.17853 | -0.022888 | -0.27466 | -0.16022 | -0.086975 | -0.19226 | -0.082397 | -0.096131 | 60.7132 | 60.9695 | 122.7539 | 122.818 | -0.27466 | 122.7585 | 60.9558 | -0.19226 | 122.818 | -0.27466 | 60.9558 | 122.7539 | 122.7585 | -123.0194 | -123.0331
156.7656 | 123.175 | -60.8963 | 61.9492 | 0.20195 | -0.0037298 | -0.0019439 | 0.00092504 | 0.0663 | -0.0022323 | 0.070402 | -61.0016 | 61.9217 | -61.0291 | -61.0886 | 61.8622 | 0.050354 | -0.14191 | 0.091553 | 61.9125 | -61.0611 | -0.13275 | -0.027466 | -0.10529 | -0.19226 | -0.086975 | -0.16479 | -0.036621 | 0.027466 | 60.7544 | 60.9879 | 122.7585 | 122.818 | -0.10529 | 122.8088 | 60.9467 | -0.16479 | 122.818 | -0.10529 | 60.9467 | 122.7585 | 122.8088 | -122.9782 | -123.0103
157.7656 | 123.2162 | -60.8826 | 61.9583 | 0.31639 | -0.0024482 | -0.00066214 | 0.0013522 | 0.066941 | -0.0035141 | 0.068906 | -61.0062 | 61.9308 | -61.0428 | -61.0703 | 61.8805 | 0.054932 | -0.16479 | 0.10071 | 61.8942 | -61.0886 | -0.16022 | -0.027466 | -0.1236 | -0.18768 | -0.07782 | -0.20599 | -0.064087 | 0.036621 | 60.7178 | 60.9833 | 122.7631 | 122.8134 | -0.1236 | 122.7768 | 60.9375 | -0.20599 | 122.8134 | -0.1236 | 60.9375 | 122.7631 | 122.7768 | -123.0011 | -123.0469
158.7656 | 123.2208 | -60.8826 | 61.9354 | 1.2624 | -0.0041572 | 0.0029693 | 0.0039156 | 0.064378 | -0.0024459 | 0.070402 | -60.9192 | 61.9492 | -61.0291 | -61.0428 | 61.8759 | 0.054932 | -0.16937 | 0.07782 | 61.8759 | -61.084 | -0.14648 | 0.013733 | -0.036621 | -0.16022 | -0.059509 | -0.20142 | -0.059509 | 0.10986 | 60.7132 | 60.9604 | 122.7585 | 122.8317 | -0.036621 | 122.7585 | 60.9375 | -0.20142 | 122.8317 | -0.036621 | 60.9375 | 122.7585 | 122.7585 | -122.9645 | -123.0194
159.7656 | 123.2162 | -60.8871 | 61.94 | 0.24773 | -0.0033026 | 0.0012605 | 0.0051974 | 0.0663 | -0.0011643 | 0.068693 | -61.0199 | 61.9629 | -61.0611 | -61.1114 | 61.8393 | 0.041199 | -0.14648 | 0.073242 | 61.8851 | -61.0931 | -0.17395 | 0.022889 | -0.13275 | -0.2243 | -0.10071 | -0.20599 | -0.054931 | 0.041199 | 60.7407 | 60.9604 | 122.7264 | 122.85 | -0.13275 | 122.7722 | 60.9283 | -0.20599 | 122.85 | -0.13275 | 60.9283 | 122.7264 | 122.7722 | -123.0011 | -123.0331
160.7656 | 123.175 | -60.8917 | 61.9537 | 0.28587 | -0.0018072 | -0.0032257 | 0.003702 | 0.064378 | -0.0022323 | 0.070188 | -61.0519 | 62.0087 | -61.0794 | -61.1206 | 61.8256 | 0.018311 | -0.11902 | 0.032043 | 61.9034 | -61.084 | -0.18768 | 0.054932 | -0.16022 | -0.22888 | -0.12817 | -0.19226 | -0.050354 | 0.027466 | 60.7727 | 60.9238 | 122.7173 | 122.9004 | -0.16022 | 122.7951 | 60.91 | -0.19226 | 122.9004 | -0.16022 | 60.91 | 122.7173 | 122.7951 | -123.0331 | -123.0377
161.7656 | 123.2071 | -60.8917 | 61.94 | 0.2401 | -0.003089 | -0.0025847 | 0.003702 | 0.066514 | -0.0022323 | 0.068265 | -60.9924 | 61.9675 | -61.0519 | -61.0794 | 61.8668 | 0.054932 | -0.16479 | 0.086975 | 61.9171 | -61.084 | -0.16022 | 0.027466 | -0.10071 | -0.18768 | -0.073242 | -0.19226 | -0.022888 | 0.059509 | 60.7269 | 60.9787 | 122.7585 | 122.8592 | -0.10071 | 122.8088 | 60.9467 | -0.19226 | 122.8592 | -0.10071 | 60.9467 | 122.7585 | 122.8088 | -122.9919 | -123.024
162.7656 | 123.2117 | -60.9055 | 61.9675 | 0.22484 | -0.00031179 | 0.0010467 | 0.0045566 | 0.068009 | -0.0033005 | 0.070188 | -61.0199 | 61.9766 | -61.0794 | -61.0748 | 61.8622 | 0.054932 | -0.16022 | 0.082397 | 61.9034 | -61.1206 | -0.17395 | 0.009156 | -0.11444 | -0.16937 | -0.10528 | -0.21515 | -0.064087 | 0.05951 | 60.7452 | 60.9879 | 122.7676 | 122.8821 | -0.11444 | 122.8088 | 60.9604 | -0.21515 | 122.8821 | -0.11444 | 60.9604 | 122.7676 | 122.8088 | -123.0469 | -123.0881
163.7656 | 123.2208 | -60.8597 | 61.9446 | 0.25536 | -0.0020208 | 0.0023285 | 0.00028404 | 0.065446 | -0.0018051 | 0.069974 | -60.997 | 61.9537 | -61.0474 | -61.2671 | 61.8301 | 0.10071 | -0.091553 | 0.13733 | 61.8942 | -61.0611 | -0.18768 | 0.009155 | -0.13733 | -0.40741 | -0.11444 | -0.20142 | -0.050354 | 0.050354 | 60.7681 | 60.997 | 122.6898 | 122.8134 | -0.13733 | 122.7539 | 60.9604 | -0.20142 | 122.8134 | -0.13733 | 60.9604 | 122.6898 | 122.7539 | -122.9919 | -123.0057
164.7656 | 123.2025 | -60.8826 | 61.9263 | 0.20195 | -0.0045844 | -0.0036529 | 0.0011386 | 0.065018 | -0.0033005 | 0.06912 | -60.997 | 61.9446 | -61.0336 | -61.0931 | 61.8713 | 0.059509 | -0.16479 | 0.086975 | 61.8805 | -61.0931 | -0.15106 | 0.01831 | -0.11444 | -0.21057 | -0.054932 | -0.21057 | -0.045777 | 0.036621 | 60.7178 | 60.9695 | 122.7539 | 122.8271 | -0.11444 | 122.7631 | 60.9421 | -0.21057 | 122.8271 | -0.11444 | 60.9421 | 122.7539 | 122.7631 | -122.9599 | -123.0194
165.7656 | 123.1842 | -60.8963 | 61.9492 | 0.25536 | -0.0022346 | 0.0023285 | 0.00071144 | 0.065873 | -0.0013779 | 0.071256 | -61.0016 | 61.9492 | -61.0428 | -61.0886 | 61.8576 | 0.064087 | -0.18768 | 0.082397 | 61.8805 | -61.116 | -0.14648 | 0 | -0.10529 | -0.19226 | -0.091553 | -0.21973 | -0.068665 | 0.041199 | 60.7086 | 60.9787 | 122.7539 | 122.8455 | -0.10529 | 122.7768 | 60.9604 | -0.21973 | 122.8455 | -0.10529 | 60.9604 | 122.7539 | 122.7768 | -122.9919 | -123.0652
166.7656 | 123.1247 | -60.9146 | 61.9675 | 0.2401 | -0.00031179 | -0.00087594 | 0.0051974 | 0.0663 | 0.00033105 | 0.069547 | -61.084 | 61.9766 | -61.0703 | -61.1526 | 61.7889 | -0.013733 | -0.068665 | -0.009155 | 61.908 | -61.1298 | -0.15564 | 0.009156 | -0.16937 | -0.23804 | -0.17853 | -0.21515 | -0.059509 | -0.013733 | 60.8459 | 60.9055 | 122.7036 | 122.8912 | -0.16937 | 122.8226 | 60.9009 | -0.21515 | 122.8912 | -0.16937 | 60.9009 | 122.7036 | 122.8226 | -123.0377 | -123.0972
167.7656 | 123.0743 | -60.9192 | 61.9812 | 0.17143 | -0.00052559 | -0.00023494 | 0.0041292 | 0.067795 | -0.00052335 | 0.068906 | -61.0886 | 62.0224 | -61.0794 | -61.1618 | 61.7798 | -0.036621 | -0.050354 | -0.027466 | 61.9308 | -61.116 | -0.16022 | 0.041199 | -0.16937 | -0.24261 | -0.20142 | -0.19684 | -0.050354 | -0.009155 | 60.8688 | 60.8917 | 122.699 | 122.9416 | -0.16937 | 122.85 | 60.8826 | -0.19684 | 122.9416 | -0.16937 | 60.8826 | 122.699 | 122.85 | -123.0606 | -123.0972
168.7656 | 123.1934 | -60.8917 | 61.9629 | 0.27824 | -0.0024482 | -0.00023494 | 0.0030612 | 0.065659 | -0.0024459 | 0.067411 | -61.0519 | 61.9812 | -61.0519 | -61.1252 | 61.8439 | 0.009155 | -0.1236 | 0.068665 | 61.908 | -61.1114 | -0.16022 | 0.01831 | -0.16022 | -0.23346 | -0.11902 | -0.21973 | -0.054932 | 0 | 60.7681 | 60.9604 | 122.7356 | 122.8729 | -0.16022 | 122.7997 | 60.9009 | -0.21973 | 122.8729 | -0.16022 | 60.9009 | 122.7356 | 122.7997 | -123.0148 | -123.0743
169.7656 | 123.1613 | -60.9192 | 61.9812 | 0.25536 | -0.0011664 | 0.0010467 | 0.0032748 | 0.067155 | -0.00073695 | 0.070188 | -61.0565 | 62.027 | -61.0611 | -61.1252 | 61.8164 | 0.009155 | -0.10071 | 0.027466 | 61.9034 | -61.1298 | -0.14191 | 0.045777 | -0.13733 | -0.20599 | -0.16479 | -0.21057 | -0.07782 | 0.004577 | 60.8185 | 60.9467 | 122.7356 | 122.9462 | -0.13733 | 122.8226 | 60.9283 | -0.21057 | 122.9462 | -0.13733 | 60.9283 | 122.7356 | 122.8226 | -123.0423 | -123.111
170.7656 | 123.2208 | -60.8963 | 61.9583 | 0.20195 | -0.0018072 | -0.0010895 | 0.0024202 | 0.066941 | -0.0018051 | 0.069974 | -61.0153 | 61.9949 | -61.0291 | -61.1069 | 61.8668 | 0.073242 | -0.17395 | 0.07782 | 61.908 | -61.1023 | -0.13275 | 0.036621 | -0.11902 | -0.21057 | -0.091553 | -0.20599 | -0.050354 | 0.013733 | 60.7224 | 60.9741 | 122.7631 | 122.8912 | -0.11902 | 122.8043 | 60.9695 | -0.20599 | 122.8912 | -0.11902 | 60.9695 | 122.7631 | 122.8043 | -122.9874 | -123.0606
171.7656 | 123.1888 | -60.8871 | 61.9308 | 0.24773 | -0.0018072 | 0.0042511 | 0.0015658 | 0.068436 | -0.0020187 | 0.06912 | -61.0062 | 61.9766 | -61.0382 | -61.116 | 61.8484 | 0.054932 | -0.15564 | 0.082397 | 61.9171 | -61.1206 | -0.15106 | 0.045777 | -0.11902 | -0.22888 | -0.082397 | -0.23346 | -0.013733 | 0.032043 | 60.7315 | 60.9695 | 122.7356 | 122.8638 | -0.11902 | 122.8043 | 60.9421 | -0.23346 | 122.8638 | -0.11902 | 60.9421 | 122.7356 | 122.8043 | -122.9691 | -123.0515
172.7656 | 123.1842 | -60.9055 | 61.9629 | 0.2401 | -0.0028754 | -2.1336e-05 | 0.0030612 | 0.065232 | -0.00052335 | 0.070402 | -61.0291 | 61.9858 | -61.0657 | -61.116 | 61.8393 | 0.050354 | -0.1831 | 0.050354 | 61.9171 | -61.0977 | -0.16022 | 0.022888 | -0.1236 | -0.21057 | -0.1236 | -0.19226 | -0.045777 | 0.036621 | 60.7224 | 60.9558 | 122.7448 | 122.8912 | -0.1236 | 122.8226 | 60.9558 | -0.19226 | 122.8912 | -0.1236 | 60.9558 | 122.7448 | 122.8226 | -123.0286 | -123.0606
173.7656 | 123.0881 | -60.9512 | 61.9629 | 0.087509 | -0.00138 | 0.0010467 | 0.00092504 | 0.067368 | -0.0022323 | 0.071042 | -61.1023 | 62.0132 | -61.0657 | -61.1847 | 61.7798 | -0.027466 | -0.009155 | -0.022888 | 61.9492 | -61.1389 | -0.11444 | 0.050354 | -0.15106 | -0.23346 | -0.18311 | -0.18768 | -0.013733 | -0.036621 | 60.9421 | 60.9283 | 122.731 | 122.9645 | -0.15106 | 122.9004 | 60.9238 | -0.18768 | 122.9645 | -0.15106 | 60.9238 | 122.731 | 122.9004 | -123.0286 | -123.1018
174.7656 | 123.0972 | -60.91 | 61.9812 | -1.507 | -0.0060798 | 0.0027557 | 0.0030612 | 0.066727 | -0.0011643 | 0.069761 | -61.0565 | 62.0361 | -61.0565 | -61.1938 | 61.7615 | -0.041199 | -0.009155 | -0.018311 | 61.9537 | -61.1114 | -0.14648 | 0.054932 | -0.14648 | -0.28381 | -0.21973 | -0.20142 | -0.027466 | 0 | 60.9009 | 60.8917 | 122.6715 | 122.9462 | -0.14648 | 122.8638 | 60.8688 | -0.20142 | 122.9462 | -0.14648 | 60.8688 | 122.6715 | 122.8638 | -123.0377 | -123.0927
175.7656 | 123.1522 | -60.9283 | 61.9537 | 0.23247 | -0.0020208 | -0.00044854 | 0.0017794 | 0.069291 | -0.0015915 | 0.067624 | -61.0565 | 62.0132 | -61.0519 | -61.171 | 61.8027 | -0.018311 | -0.07782 | 0.013733 | 61.9537 | -61.1298 | -0.1236 | 0.05951 | -0.12817 | -0.24261 | -0.15106 | -0.20142 | 0 | -0.004578 | 60.8505 | 60.9421 | 122.731 | 122.9416 | -0.12817 | 122.8821 | 60.91 | -0.20142 | 122.9416 | -0.12817 | 60.91 | 122.731 | 122.8821 | -123.0057 | -123.0835
176.7656 | 123.1522 | -60.9421 | 61.972 | 0.23247 | -9.819e-05 | 0.0016877 | 0.0024202 | 0.068009 | -0.0022323 | 0.068479 | -61.0794 | 62.0361 | -61.0748 | -61.1755 | 61.7844 | -0.018311 | -0.068665 | -0.004578 | 61.9492 | -61.116 | -0.13275 | 0.064087 | -0.13733 | -0.23346 | -0.18768 | -0.17395 | -0.022888 | -0.004578 | 60.8734 | 60.9375 | 122.7264 | 122.9782 | -0.13733 | 122.8912 | 60.9238 | -0.17395 | 122.9782 | -0.13733 | 60.9238 | 122.7264 | 122.8912 | -123.0469 | -123.0881
177.7656 | 123.1659 | -60.8734 | 61.9766 | 0.25536 | -0.0020208 | 0.0019013 | 0.0013522 | 0.066727 | -0.0024459 | 0.069333 | -61.0291 | 62.0041 | -61.0611 | -61.1206 | 61.8393 | 0.032043 | -0.14648 | 0.073242 | 61.9217 | -61.0794 | -0.18768 | 0.027465 | -0.15564 | -0.24719 | -0.13733 | -0.20599 | -0.054932 | 0.032043 | 60.7269 | 60.9467 | 122.7127 | 122.8775 | -0.15564 | 122.7951 | 60.9055 | -0.20599 | 122.8775 | -0.15564 | 60.9055 | 122.7127 | 122.7951 | -123.0377 | -123.056
178.7656 | 123.1705 | -60.8917 | 61.9446 | 0.2401 | -0.0022346 | -0.00044854 | 0.00049764 | 0.068223 | -0.00052335 | 0.069333 | -61.0428 | 61.9812 | -61.0428 | -61.1252 | 61.821 | 0.027466 | -0.12817 | 0.045776 | 61.9308 | -61.1114 | -0.15106 | 0.036621 | -0.15106 | -0.23346 | -0.1236 | -0.21973 | -0.013733 | 0 | 60.7636 | 60.9375 | 122.7127 | 122.8729 | -0.15106 | 122.8226 | 60.9192 | -0.21973 | 122.8729 | -0.15106 | 60.9192 | 122.7127 | 122.8226 | -122.9874 | -123.056
179.7812 | 123.175 | -60.8688 | 61.9675 | -0.04219 | -0.0022346 | -0.00023494 | -0.0044156 | 0.06395 | -0.0041549 | 0.068906 | -61.0107 | 61.9537 | -61.0245 | -61.0428 | 61.94 | 0.16022 | -0.059509 | 0.22888 | 61.9492 | -61.0748 | -0.15564 | -0.013733 | -0.14191 | -0.17395 | -0.027466 | -0.20599 | -0.01831 | 0.013733 | 60.8093 | 61.0977 | 122.8088 | 122.8226 | -0.14191 | 122.818 | 61.0291 | -0.20599 | 122.8226 | -0.14191 | 61.0291 | 122.8088 | 122.818 | -122.9919 | -123.0423
180.7656 | 123.0652 | -60.9192 | 61.9812 | 0.17143 | -0.0015936 | 0.00061946 | 0.0028476 | 0.064591 | -0.0024459 | 0.068906 | -61.0519 | 62.0316 | -61.0703 | -61.1618 | 61.7752 | -0.064087 | 0.059509 | 0.013733 | 61.972 | -61.1526 | -0.15106 | 0.050354 | -0.13275 | -0.24261 | -0.20599 | -0.23346 | -0.009155 | 0.01831 | 60.9787 | 60.9329 | 122.6944 | 122.9507 | -0.13275 | 122.8912 | 60.8551 | -0.23346 | 122.9507 | -0.13275 | 60.8551 | 122.6944 | 122.8912 | -123.0515 | -123.1338
181.7656 | 123.1018 | -60.9329 | 62.0041 | 0.22484 | -0.0022346 | -0.0010895 | 0.002634 | 0.067368 | -0.0030869 | 0.068906 | -61.0931 | 62.0224 | -61.084 | -61.203 | 61.6425 | -0.26093 | 0.045776 | 0.15564 | 61.972 | -61.1481 | -0.15106 | 0.018311 | -0.16022 | -0.27008 | -0.36163 | -0.21515 | -0.032043 | -0.009156 | 60.9787 | 61.0886 | 122.5754 | 122.9553 | -0.16022 | 122.905 | 60.672 | -0.21515 | 122.9553 | -0.16022 | 60.672 | 122.5754 | 122.905 | -123.0881 | -123.1522
182.7656 | 123.1201 | -60.9283 | 61.9675 | 0.20195 | -0.00073919 | -0.0010895 | 0.0062656 | 0.066514 | -0.0026595 | 0.069974 | -61.0703 | 62.0178 | -61.0703 | -61.1755 | 61.7798 | -0.041199 | -0.041199 | -0.009155 | 61.9354 | -61.1481 | -0.14191 | 0.050354 | -0.14191 | -0.24719 | -0.18768 | -0.21973 | -0.032043 | 0 | 60.8871 | 60.9192 | 122.7081 | 122.9462 | -0.14191 | 122.8638 | 60.8871 | -0.21973 | 122.9462 | -0.14191 | 60.8871 | 122.7081 | 122.8638 | -123.0377 | -123.1155
183.7656 | 123.0972 | -60.9421 | 61.9949 | 0.20195 | -0.00073919 | -0.0015167 | 0.0024202 | 0.067368 | -0.0020187 | 0.06912 | -61.0748 | 62.0407 | -61.0886 | -61.1801 | 61.7798 | -0.032043 | -0.013733 | -0.022888 | 61.9629 | -61.1298 | -0.14648 | 0.045776 | -0.13275 | -0.23804 | -0.21515 | -0.18768 | -0.032043 | 0.013733 | 60.9283 | 60.9192 | 122.7219 | 122.9828 | -0.13275 | 122.905 | 60.91 | -0.18768 | 122.9828 | -0.13275 | 60.91 | 122.7219 | 122.905 | -123.0835 | -123.1247
184.7812 | 123.2071 | -60.8963 | 61.9858 | -0.0040434 | -0.0028754 | -0.0036529 | -0.0048428 | 0.063309 | -0.0020187 | 0.069761 | -61.0657 | 61.9583 | -61.0336 | -61.1114 | 61.8622 | 0.091553 | -0.041199 | 0.16022 | 61.9354 | -61.0703 | -0.13733 | -0.027466 | -0.16937 | -0.21515 | -0.1236 | -0.17395 | -0.050354 | -0.032044 | 60.8551 | 61.0565 | 122.7585 | 122.8546 | -0.16937 | 122.8317 | 60.9879 | -0.17395 | 122.8546 | -0.16937 | 60.9879 | 122.7585 | 122.8317 | -123.0194 | -123.056
185.7656 | 123.143 | -60.91 | 61.9446 | 0.27061 | -0.0045844 | -0.0025847 | 0.001993 | 0.065873 | -0.0013779 | 0.069761 | -61.0519 | 62.0178 | -61.0611 | -61.1618 | 61.8164 | -0.004578 | -0.10071 | 0.027466 | 61.9171 | -61.171 | -0.15106 | 0.073242 | -0.14191 | -0.25177 | -0.12817 | -0.26093 | -0.027466 | 0.009155 | 60.8093 | 60.9375 | 122.7264 | 122.9279 | -0.14191 | 122.8271 | 60.9055 | -0.26093 | 122.9279 | -0.14191 | 60.9055 | 122.7264 | 122.8271 | -123.0057 | -123.1155
186.7656 | 123.1155 | -60.9238 | 61.9446 | 0.2401 | -0.00031179 | -0.00023494 | 0.0013522 | 0.065018 | -0.0028731 | 0.070829 | -61.0657 | 61.9949 | -61.084 | -61.1572 | 61.7981 | -0.009155 | -0.07782 | 0.013733 | 61.9537 | -61.1389 | -0.16022 | 0.050354 | -0.14191 | -0.23346 | -0.14648 | -0.21515 | 0.009155 | 0.01831 | 60.8459 | 60.9375 | 122.7219 | 122.9187 | -0.14191 | 122.8775 | 60.9146 | -0.21515 | 122.9187 | -0.14191 | 60.9146 | 122.7219 | 122.8775 | -123.0286 | -123.0835
187.7656 | 123.0606 | -60.9421 | 61.9858 | 0.23247 | 0.00011541 | -0.00023494 | 0.005411 | 0.06395 | -0.0037277 | 0.069333 | -61.0794 | 62.0407 | -61.0931 | -61.1481 | 61.7981 | -0.050354 | 0.059509 | -0.004578 | 61.9812 | -61.1206 | -0.15106 | 0.054931 | -0.13733 | -0.20599 | -0.18768 | -0.17853 | -0.004578 | 0.013733 | 61.0016 | 60.9375 | 122.7402 | 122.9828 | -0.13733 | 122.9233 | 60.8917 | -0.17853 | 122.9828 | -0.13733 | 60.8917 | 122.7402 | 122.9233 | -123.0789 | -123.1064
188.7656 | 123.0835 | -60.9421 | 61.9949 | 0.19432 | 0.00054261 | 0.0023285 | 0.004343 | 0.067155 | -0.0020187 | 0.070829 | -61.0886 | 62.027 | -61.0611 | -61.1526 | 61.4594 | -0.32044 | 0.23804 | 0.050354 | 61.94 | -61.1435 | -0.11902 | 0.032044 | -0.14648 | -0.21057 | -0.53558 | -0.20142 | -0.054932 | -0.027466 | 61.1801 | 60.9924 | 122.4014 | 122.9691 | -0.14648 | 122.8821 | 60.6216 | -0.20142 | 122.9691 | -0.14648 | 60.6216 | 122.4014 | 122.8821 | -123.056 | -123.1384
189.7812 | 123.1659 | -60.91 | 61.9675 | 0.69023 | -0.0028754 | -0.0027985 | -0.0037748 | 0.0663 | -0.0041549 | 0.068906 | -61.0245 | 61.9492 | -61.0428 | -61.1298 | 61.8439 | 0.064087 | -0.041199 | 0.10986 | 61.9492 | -61.084 | -0.13275 | -0.01831 | -0.11444 | -0.21973 | -0.1236 | -0.17395 | -0.01831 | 0.018311 | 60.8688 | 61.0199 | 122.7539 | 122.8592 | -0.11444 | 122.8592 | 60.9741 | -0.17395 | 122.8592 | -0.11444 | 60.9741 | 122.7539 | 122.8592 | -123.0103 | -123.0515
190.7656 | 123.1842 | -60.8871 | 61.9446 | 0.26299 | -0.0033026 | -0.0027985 | 0.0017794 | 0.066727 | -0.0022323 | 0.068052 | -61.0245 | 61.9949 | -61.0519 | -61.1206 | 61.8301 | 0.022888 | -0.16479 | 0.07782 | 61.94 | -61.0977 | -0.16479 | 0.050354 | -0.13733 | -0.23346 | -0.11444 | -0.21057 | -0.004578 | 0.027466 | 60.7224 | 60.965 | 122.7173 | 122.8821 | -0.13733 | 122.8271 | 60.91 | -0.21057 | 122.8821 | -0.13733 | 60.91 | 122.7173 | 122.8271 | -122.9965 | -123.0423
191.7656 | 123.1934 | -60.9009 | 61.9537 | 0.25536 | -0.0035162 | 0.00061946 | 0.001993 | 0.066514 | -0.0030869 | 0.06677 | -61.0291 | 62.0041 | -61.0474 | -61.116 | 61.8256 | 0.022888 | -0.1236 | 0.059509 | 61.9171 | -61.1206 | -0.14648 | 0.050354 | -0.12817 | -0.21515 | -0.12817 | -0.21973 | -0.036621 | 0.01831 | 60.7773 | 60.9604 | 122.7264 | 122.905 | -0.12817 | 122.818 | 60.9238 | -0.21973 | 122.905 | -0.12817 | 60.9238 | 122.7264 | 122.818 | -123.0011 | -123.0743
192.7656 | 123.1659 | -60.9283 | 61.9583 | 0.26299 | 0.0018244 | 0.0023285 | 0.0030612 | 0.066727 | -0.0013779 | 0.069333 | -61.0382 | 61.9812 | -61.0565 | -61.1343 | 61.8256 | 0 | -0.1236 | 0.041199 | 61.9171 | -61.1298 | -0.12817 | 0.022888 | -0.10986 | -0.20599 | -0.13275 | -0.20142 | -0.041199 | 0.018311 | 60.8047 | 60.9695 | 122.7539 | 122.9095 | -0.10986 | 122.8455 | 60.9283 | -0.20142 | 122.9095 | -0.10986 | 60.9283 | 122.7539 | 122.8455 | -123.0148 | -123.0881
193.7656 | 123.1613 | -60.9329 | 61.9537 | 0.2401 | -0.0028754 | -0.0019439 | 0.001993 | 0.066941 | -0.00073695 | 0.067411 | -61.0519 | 61.9904 | -61.0611 | -61.1435 | 61.8118 | -0.009155 | -0.091553 | 0.022888 | 61.9263 | -61.1389 | -0.12817 | 0.036621 | -0.11902 | -0.21057 | -0.14191 | -0.20599 | -0.027465 | 0.009155 | 60.8414 | 60.9558 | 122.7448 | 122.9233 | -0.11902 | 122.8592 | 60.9238 | -0.20599 | 122.9233 | -0.11902 | 60.9238 | 122.7448 | 122.8592 | -123.0148 | -123.0927
194.7812 | 123.2162 | -60.8826 | 61.9446 | 0.095139 | -0.0035162 | -0.00087594 | 7.0444e-05 | 0.064591 | -0.0011643 | 0.068265 | -60.997 | 61.9812 | -61.0062 | -61.1069 | 61.8622 | 0.041199 | -0.16022 | 0.10986 | 61.9263 | -61.0794 | -0.1236 | 0.036621 | -0.11444 | -0.22431 | -0.082397 | -0.19684 | -0.01831 | 0.009156 | 60.7224 | 60.9924 | 122.7448 | 122.8638 | -0.11444 | 122.8088 | 60.9238 | -0.19684 | 122.8638 | -0.11444 | 60.9238 | 122.7448 | 122.8088 | -122.9507 | -123.024
195.7656 | 123.0881 | -60.8871 | 62.0178 | 0.23247 | -0.003089 | 0.0012605 | 0.003702 | 0.066941 | -0.0011643 | 0.068693 | -61.0794 | 62.0316 | -61.0886 | -61.1984 | 61.5234 | -0.30212 | 0.23804 | 0.07782 | 61.94 | -61.1526 | -0.20142 | 0.013733 | -0.19226 | -0.31128 | -0.49439 | -0.2655 | -0.07782 | 0.009155 | 61.1252 | 60.965 | 122.4106 | 122.9187 | -0.19226 | 122.8271 | 60.585 | -0.2655 | 122.9187 | -0.19226 | 60.585 | 122.4106 | 122.8271 | -123.1064 | -123.1705
196.7656 | 123.0927 | -60.9192 | 61.9904 | 0.24773 | -0.00138 | 0.0016877 | 0.0024202 | 0.068223 | -0.0022323 | 0.070402 | -61.0794 | 62.0407 | -61.0794 | -61.171 | 61.7523 | -0.032043 | -0.041199 | -0.032043 | 61.9675 | -61.1389 | -0.16022 | 0.050354 | -0.16022 | -0.25177 | -0.23804 | -0.21973 | -0.022888 | 0 | 60.878 | 60.8871 | 122.6715 | 122.9599 | -0.16022 | 122.8867 | 60.8871 | -0.21973 | 122.9599 | -0.16022 | 60.8871 | 122.6715 | 122.8867 | -123.0698 | -123.1293
197.7656 | 123.1613 | -60.8963 | 61.9537 | 0.25536 | -0.0033026 | -0.0023711 | -0.00057036 | 0.066514 | -0.0013779 | 0.070402 | -61.0565 | 62.0224 | -61.0565 | -61.1389 | 61.8118 | 0.009155 | -0.11902 | 0.036621 | 61.9354 | -61.1206 | -0.16022 | 0.068665 | -0.16022 | -0.24262 | -0.14191 | -0.2243 | -0.01831 | 0 | 60.7773 | 60.9329 | 122.7081 | 122.9187 | -0.16022 | 122.8317 | 60.9055 | -0.2243 | 122.9187 | -0.16022 | 60.9055 | 122.7081 | 122.8317 | -123.0103 | -123.0743
198.7656 | 123.1705 | -60.8963 | 61.9263 | 0.25536 | 0.00011541 | -0.0010895 | -0.00014316 | 0.06865 | -0.0033005 | 0.070615 | -61.0657 | 62.0087 | -61.0931 | -61.1481 | 61.8164 | -0.004578 | -0.09613 | 0.009155 | 61.9492 | -61.1343 | -0.19684 | 0.082397 | -0.16937 | -0.25177 | -0.10986 | -0.23804 | 0.022888 | 0.027466 | 60.8002 | 60.9055 | 122.7127 | 122.905 | -0.16937 | 122.8455 | 60.8917 | -0.23804 | 122.905 | -0.16937 | 60.8917 | 122.7127 | 122.8455 | -123.0194 | -123.0606
199.7656 | 123.1247 | -60.8963 | 61.9629 | 0.24773 | -0.00073919 | -0.00066214 | 0.00028404 | 0.067368 | -0.00095055 | 0.068265 | -61.0703 | 62.0224 | -61.0794 | -61.1755 | 61.7935 | -0.018311 | -0.064087 | -0.013733 | 61.94 | -61.1481 | -0.18311 | 0.059509 | -0.17395 | -0.27924 | -0.16937 | -0.25177 | -0.022889 | 0.009156 | 60.8322 | 60.8826 | 122.6898 | 122.9187 | -0.17395 | 122.8363 | 60.878 | -0.25177 | 122.9187 | -0.17395 | 60.878 | 122.6898 | 122.8363 | -123.0423 | -123.111
200.7656 | 123.1247 | -60.9512 | 61.972 | 0.20958 | 0.00075621 | 0.00083306 | 0.001993 | 0.067582 | -0.00030975 | 0.06912 | -61.0886 | 62.0316 | -61.0748 | -61.1984 | 61.7798 | -0.036621 | -0.045776 | -0.009155 | 61.9446 | -61.1572 | -0.1236 | 0.059509 | -0.13733 | -0.24719 | -0.19226 | -0.20599 | -0.027466 | -0.013733 | 60.9055 | 60.9421 | 122.731 | 122.9828 | -0.13733 | 122.8958 | 60.9146 | -0.20599 | 122.9828 | -0.13733 | 60.9146 | 122.731 | 122.8958 | -123.0469 | -123.1293
201.7656 | 123.0881 | -60.9329 | 61.9904 | 0.15617 | -0.0015936 | -0.00044854 | 0.0034884 | 0.069291 | -0.0024459 | 0.069974 | -61.0931 | 62.0499 | -61.1023 | -61.2213 | 61.7477 | -0.045776 | 0.009155 | -0.041199 | 61.9766 | -61.1618 | -0.16937 | 0.05951 | -0.16022 | -0.28839 | -0.24261 | -0.22888 | -0.013732 | 0.009155 | 60.9421 | 60.8917 | 122.6807 | 122.9828 | -0.16022 | 122.9095 | 60.8871 | -0.22888 | 122.9828 | -0.16022 | 60.8871 | 122.6807 | 122.9095 | -123.0927 | -123.1522
202.7656 | 123.1018 | -60.9375 | 61.972 | 0.21721 | -9.819e-05 | -0.0017303 | 0.0032748 | 0.066941 | -0.0035141 | 0.069547 | -61.084 | 62.0407 | -61.0611 | -61.1755 | 61.7935 | -0.032043 | 0.045776 | 0 | 61.9904 | -61.1435 | -0.1236 | 0.068664 | -0.14648 | -0.23804 | -0.17853 | -0.20599 | 0.01831 | -0.022888 | 60.9833 | 60.9375 | 122.731 | 122.9782 | -0.14648 | 122.9279 | 60.9055 | -0.20599 | 122.9782 | -0.14648 | 60.9055 | 122.731 | 122.9279 | -123.0331 | -123.1155
203.7656 | 123.0423 | -60.9558 | 61.9537 | 0.21721 | -0.0028754 | 0.0029693 | 0.001993 | 0.067368 | -0.00095055 | 0.068479 | -61.0794 | 62.0728 | -61.0794 | -61.2076 | 61.7523 | -0.050354 | 0.018311 | -0.032043 | 61.9858 | -61.1664 | -0.1236 | 0.11902 | -0.1236 | -0.25177 | -0.20142 | -0.21057 | 0.032044 | 0 | 60.9741 | 60.9238 | 122.7081 | 123.0286 | -0.1236 | 122.9416 | 60.9055 | -0.21057 | 123.0286 | -0.1236 | 60.9055 | 122.7081 | 122.9416 | -123.0331 | -123.1201
204.7656 | 123.0743 | -60.9421 | 61.9904 | 0.30113 | -0.0020208 | -0.0060027 | 0.0032748 | 0.069291 | -0.0030869 | 0.070188 | -61.0657 | 62.0728 | -61.0703 | -61.1984 | 61.7615 | -0.045776 | -0.013733 | -0.004578 | 61.9858 | -61.1481 | -0.12817 | 0.082398 | -0.1236 | -0.25635 | -0.22888 | -0.20599 | -0.004577 | 0.004577 | 60.9283 | 60.9375 | 122.7036 | 123.0148 | -0.1236 | 122.9279 | 60.8963 | -0.20599 | 123.0148 | -0.1236 | 60.8963 | 122.7036 | 122.9279 | -123.0606 | -123.1384
205.7656 | 123.0423 | -60.9467 | 62.0132 | 0.21721 | -0.0026618 | 0.0021149 | -0.00099756 | 0.065659 | -0.00052335 | 0.067411 | -61.0886 | 62.0544 | -61.0703 | -61.1572 | 61.7569 | -0.054932 | 0.041199 | -0.009155 | 61.9766 | -61.1526 | -0.1236 | 0.041198 | -0.14191 | -0.21057 | -0.25635 | -0.20599 | -0.036621 | -0.018311 | 60.9879 | 60.9375 | 122.7036 | 123.0011 | -0.14191 | 122.9233 | 60.8917 | -0.20599 | 123.0011 | -0.14191 | 60.8917 | 122.7036 | 122.9233 | -123.0835 | -123.1659
206.7656 | 123.1567 | -60.9558 | 61.9949 | 0.21721 | -0.0015936 | 0.0021149 | 0.0028476 | 0.066941 | -0.0011643 | 0.069974 | -61.0748 | 62.0544 | -61.0748 | -61.1938 | 61.7523 | -0.041199 | 0.018311 | -0.1236 | 61.9537 | -61.1755 | -0.11902 | 0.059509 | -0.11902 | -0.23804 | -0.24262 | -0.21973 | -0.041199 | 0 | 60.9741 | 60.8322 | 122.7081 | 123.0103 | -0.11902 | 122.9095 | 60.9146 | -0.21973 | 123.0103 | -0.11902 | 60.9146 | 122.7081 | 122.9095 | -123.0698 | -123.1705
207.7812 | 123.2025 | -60.9192 | 61.9354 | 0.25536 | -0.0020208 | -0.0013031 | 0.00049764 | 0.069077 | -0.00052335 | 0.070402 | -61.0565 | 62.0041 | -61.0748 | -61.1252 | 61.8164 | 0.013733 | -0.1236 | 0.054932 | 61.9354 | -61.1206 | -0.15564 | 0.068664 | -0.13733 | -0.20599 | -0.11902 | -0.20142 | 0 | 0.01831 | 60.7956 | 60.9741 | 122.7356 | 122.9233 | -0.13733 | 122.8546 | 60.9329 | -0.20142 | 122.9233 | -0.13733 | 60.9329 | 122.7356 | 122.8546 | -123.0103 | -123.056
208.7656 | 123.1064 | -60.8917 | 61.9858 | 0.064621 | -0.0026618 | -0.0023711 | 0.0034884 | 0.066514 | -0.0020187 | 0.068052 | -61.0382 | 62.0636 | -61.0565 | -61.1481 | 61.7798 | 0.022888 | 0.022888 | 0.050354 | 61.9858 | -61.1252 | -0.16479 | 0.07782 | -0.14648 | -0.25635 | -0.20599 | -0.23346 | 0 | 0.018311 | 60.9146 | 60.9421 | 122.6715 | 122.9553 | -0.14648 | 122.8775 | 60.9146 | -0.23346 | 122.9553 | -0.14648 | 60.9146 | 122.6715 | 122.8775 | -123.0423 | -123.111
209.7656 | 123.0743 | -60.9238 | 61.9995 | 0.11803 | -0.0011664 | -0.00066214 | 0.001993 | 0.068436 | -0.00073695 | 0.06912 | -61.0611 | 62.0544 | -61.0748 | -61.171 | 61.7706 | -0.018311 | 0.050354 | 0.013733 | 62.0041 | -61.1618 | -0.15106 | 0.054931 | -0.13733 | -0.24719 | -0.22888 | -0.23804 | 0.004577 | 0.013733 | 60.9741 | 60.9375 | 122.6944 | 122.9782 | -0.13733 | 122.9279 | 60.9055 | -0.23804 | 122.9782 | -0.13733 | 60.9055 | 122.6944 | 122.9279 | -123.0743 | -123.1613
210.7656 | 123.0835 | -60.9283 | 61.9995 | 0.095139 | -0.0033026 | 0.0016877 | 0.0041292 | 0.068009 | -0.0018051 | 0.070188 | -61.0519 | 62.059 | -61.0794 | -61.1664 | 61.7889 | 0 | 0.041199 | 0.022888 | 61.9812 | -61.1618 | -0.15106 | 0.059509 | -0.1236 | -0.23804 | -0.21057 | -0.23346 | -0.018311 | 0.027466 | 60.9695 | 60.9512 | 122.7173 | 122.9874 | -0.1236 | 122.9095 | 60.9283 | -0.23346 | 122.9874 | -0.1236 | 60.9283 | 122.7173 | 122.9095 | -123.0789 | -123.1613
211.7656 | 123.0606 | -60.9375 | 61.9904 | 0.27824 | -0.00073919 | 0.0029693 | 0.002634 | 0.068436 | -0.0011643 | 0.070188 | -61.0886 | 62.0728 | -61.0611 | -61.2167 | 61.7477 | -0.045776 | 0.054932 | -0.041199 | 61.9858 | -61.1481 | -0.1236 | 0.082398 | -0.15106 | -0.27924 | -0.24261 | -0.21057 | -0.004577 | -0.027466 | 60.9924 | 60.8963 | 122.6852 | 123.0103 | -0.15106 | 122.9233 | 60.8917 | -0.21057 | 123.0103 | -0.15106 | 60.8917 | 122.6852 | 122.9233 | -123.0515 | -123.1384
212.7656 | 123.0698 | -60.9421 | 61.9949 | 0.14092 | -0.0018072 | 0.0019013 | 0.00092504 | 0.067155 | -0.0020187 | 0.067624 | -61.0794 | 62.1002 | -61.0886 | -61.1755 | 61.7661 | -0.036621 | 0.045776 | -0.032043 | 61.9904 | -61.171 | -0.14648 | 0.10529 | -0.13733 | -0.23346 | -0.22888 | -0.22888 | -0.004578 | 0.009155 | 60.9879 | 60.91 | 122.7081 | 123.0423 | -0.13733 | 122.9324 | 60.9055 | -0.22888 | 123.0423 | -0.13733 | 60.9055 | 122.7081 | 122.9324 | -123.0835 | -123.1659
213.7656 | 123.0789 | -60.9329 | 62.0132 | 0.026474 | -0.00095279 | 0.0025421 | 0.002634 | 0.069291 | -0.0022323 | 0.069547 | -61.0519 | 62.0636 | -61.0519 | -61.1755 | 61.7844 | -0.018311 | 0.045776 | 0 | 62.0041 | -61.1481 | -0.11902 | 0.050354 | -0.11902 | -0.24262 | -0.22888 | -0.21515 | -0.009156 | 0 | 60.9787 | 60.9329 | 122.7173 | 122.9965 | -0.11902 | 122.937 | 60.9146 | -0.21515 | 122.9965 | -0.11902 | 60.9146 | 122.7173 | 122.937 | -123.0652 | -123.1613
214.7656 | 123.0927 | -60.9192 | 62.0178 | -0.0040434 | -0.003089 | -0.0027985 | 0.0024202 | 0.068009 | -0.00052335 | 0.070615 | -61.0291 | 62.0407 | -61.0611 | -61.1206 | 61.8393 | 0.045776 | 0.041199 | 0.10071 | 61.9583 | -61.1298 | -0.14191 | 0.022888 | -0.10986 | -0.20142 | -0.17853 | -0.21057 | -0.059509 | 0.032043 | 60.9604 | 61.0199 | 122.7585 | 122.9599 | -0.10986 | 122.8775 | 60.965 | -0.21057 | 122.9599 | -0.10986 | 60.965 | 122.7585 | 122.8775 | -123.0789 | -123.1476
215.7656 | 123.1247 | -60.9238 | 61.9812 | -0.019302 | -0.0018072 | -0.0013031 | 0.002634 | 0.06865 | -0.0015915 | 0.06912 | -61.0016 | 62.0544 | -61.0428 | -61.116 | 61.8439 | 0.013733 | -0.027466 | 0.10071 | 61.9812 | -61.1481 | -0.11902 | 0.073242 | -0.07782 | -0.19226 | -0.13733 | -0.2243 | 0 | 0.041199 | 60.8963 | 61.0245 | 122.7676 | 122.9782 | -0.07782 | 122.905 | 60.9375 | -0.2243 | 122.9782 | -0.07782 | 60.9375 | 122.7676 | 122.905 | -123.024 | -123.1293
216.7656 | 123.0972 | -60.9055 | 61.9949 | 0.026474 | -0.00073919 | 0.00040586 | 0.002634 | 0.06865 | -0.0022323 | 0.06912 | -61.0291 | 62.0499 | -61.0519 | -61.1343 | 61.821 | 0.054932 | 0.036621 | 0.059509 | 61.9995 | -61.1252 | -0.14648 | 0.054932 | -0.1236 | -0.22888 | -0.17395 | -0.21973 | 0.004578 | 0.022888 | 60.9421 | 60.965 | 122.7264 | 122.9553 | -0.1236 | 122.905 | 60.9604 | -0.21973 | 122.9553 | -0.1236 | 60.9604 | 122.7264 | 122.905 | -123.0469 | -123.1201
217.7656 | 123.1293 | -60.9238 | 62.0224 | -0.04219 | 0.00075621 | 0.00040586 | -0.00014316 | 0.06865 | -0.0022323 | 0.068052 | -61.0107 | 62.0636 | -61.0428 | -61.1206 | 61.8164 | 0.068665 | 0.032043 | 0.086975 | 61.9995 | -61.1389 | -0.11902 | 0.041199 | -0.086975 | -0.19684 | -0.20599 | -0.21515 | -0.022888 | 0.032044 | 60.9558 | 61.0107 | 122.7402 | 122.9874 | -0.086975 | 122.9233 | 60.9924 | -0.21515 | 122.9874 | -0.086975 | 60.9924 | 122.7402 | 122.9233 | -123.0652 | -123.1613
218.7656 | 123.1155 | -60.9375 | 62.027 | 0.064621 | -0.00138 | 0.00061946 | 0.002634 | 0.069718 | -0.0011643 | 0.069547 | -61.0474 | 62.0682 | -61.0519 | -61.1618 | 61.7935 | 0.004578 | 0.041199 | 0.032043 | 61.9858 | -61.1664 | -0.11444 | 0.041198 | -0.10986 | -0.2243 | -0.23346 | -0.22888 | -0.041199 | 0.004578 | 60.9787 | 60.9695 | 122.731 | 123.0057 | -0.10986 | 122.9233 | 60.9421 | -0.22888 | 123.0057 | -0.10986 | 60.9421 | 122.731 | 122.9233 | -123.0789 | -123.1934
219.7656 | 123.0881 | -60.9329 | 62.0087 | 0.0035856 | -0.00052559 | 0.0029693 | 7.0444e-05 | 0.069718 | -0.00095055 | 0.068906 | -61.0199 | 62.0316 | -61.0611 | -61.1526 | 61.8027 | 0.013733 | 0.022888 | 0.059509 | 61.9995 | -61.1481 | -0.12817 | 0.022888 | -0.086975 | -0.21973 | -0.20599 | -0.21515 | -0.009155 | 0.041199 | 60.9558 | 60.9924 | 122.7356 | 122.9645 | -0.086975 | 122.9324 | 60.9467 | -0.21515 | 122.9645 | -0.086975 | 60.9467 | 122.7356 | 122.9324 | -123.0698 | -123.1567
220.7656 | 123.111 | -60.9055 | 61.9995 | 0.011215 | -0.0041572 | 0.0016877 | 0.002634 | 0.06865 | -0.0011643 | 0.068693 | -61.0153 | 62.1002 | -61.0474 | -61.1481 | 61.821 | 0.027466 | 0.032043 | 0.068665 | 61.9675 | -61.1435 | -0.14191 | 0.10071 | -0.10986 | -0.24261 | -0.17853 | -0.23804 | -0.032044 | 0.032043 | 60.9375 | 60.9741 | 122.7264 | 123.0057 | -0.10986 | 122.8729 | 60.9329 | -0.23804 | 123.0057 | -0.10986 | 60.9329 | 122.7264 | 122.8729 | -123.0469 | -123.143
221.7656 | 123.143 | -60.91 | 61.9904 | -0.0040434 | -0.00138 | 0.00019226 | -0.00057036 | 0.068009 | -0.00030975 | 0.069333 | -61.0107 | 62.0728 | -61.0519 | -61.1298 | 61.8393 | 0.086975 | 0.045776 | 0.1236 | 62.0361 | -61.1298 | -0.14191 | 0.082398 | -0.10071 | -0.21973 | -0.15106 | -0.21973 | 0.045777 | 0.041199 | 60.9558 | 61.0336 | 122.7493 | 122.9828 | -0.10071 | 122.9462 | 60.997 | -0.21973 | 122.9828 | -0.10071 | 60.997 | 122.7493 | 122.9462 | -123.0423 | -123.1201
222.7656 | 123.1247 | -60.9283 | 61.9995 | -0.065079 | -0.0015936 | 0.0031831 | 0.0015658 | 0.066941 | 0.00011745 | 0.069761 | -61.0016 | 62.0819 | -61.0519 | -61.1252 | 61.8301 | 0.086975 | 0.068665 | 0.13275 | 61.9812 | -61.1435 | -0.1236 | 0.082397 | -0.073242 | -0.19684 | -0.16937 | -0.21515 | -0.018311 | 0.050354 | 60.997 | 61.0611 | 122.7585 | 123.0103 | -0.073242 | 122.9095 | 61.0153 | -0.21515 | 123.0103 | -0.073242 | 61.0153 | 122.7585 | 122.9095 | -123.0515 | -123.143
223.7656 | 123.1155 | -60.8963 | 61.9675 | -0.011673 | -0.00095279 | -2.1336e-05 | 0.0017794 | 0.067795 | -0.0028731 | 0.067197 | -61.0153 | 62.0773 | -61.0611 | -61.0931 | 61.8439 | 0.059509 | 0.022888 | 0.11902 | 61.9995 | -61.1435 | -0.16479 | 0.10986 | -0.11902 | -0.19684 | -0.1236 | -0.24719 | 0.032044 | 0.045776 | 60.9192 | 61.0153 | 122.7402 | 122.9736 | -0.11902 | 122.8958 | 60.9558 | -0.24719 | 122.9736 | -0.11902 | 60.9558 | 122.7402 | 122.8958 | -123.0286 | -123.111
224.7656 | 123.1567 | -60.9375 | 61.9949 | -0.034561 | 0.00032901 | 0.00061946 | 0.00049764 | 0.069291 | -0.0024459 | 0.068052 | -61.0107 | 62.0728 | -61.0748 | -61.1252 | 61.853 | 0.086975 | 0.036621 | -0.064087 | 61.972 | -61.1343 | -0.13733 | 0.07782 | -0.073242 | -0.18768 | -0.14191 | -0.19684 | -0.022888 | 0.064087 | 60.9741 | 60.8734 | 122.7905 | 123.0103 | -0.073242 | 122.9095 | 61.0245 | -0.19684 | 123.0103 | -0.073242 | 61.0245 | 122.7905 | 122.9095 | -123.0698 | -123.1293
225.7656 | 123.111 | -60.9146 | 61.9904 | 0.072251 | -0.00138 | -0.0027985 | 0.001993 | 0.068436 | -9.6146e-05 | 0.068906 | -61.0107 | 62.0499 | -61.0474 | -61.1389 | 61.8164 | 0.050354 | 0.027466 | 0.086975 | 62.0041 | -61.1435 | -0.13275 | 0.05951 | -0.09613 | -0.2243 | -0.17395 | -0.22888 | 0.013733 | 0.036621 | 60.9421 | 61.0016 | 122.731 | 122.9645 | -0.09613 | 122.9187 | 60.965 | -0.22888 | 122.9645 | -0.09613 | 60.965 | 122.731 | 122.9187 | -123.0377 | -123.1338
226.7656 | 123.1384 | -60.8963 | 61.9995 | -0.36262 | -0.0026618 | -0.0013031 | 0.003702 | 0.068436 | -0.0020187 | 0.066984 | -61.0107 | 62.0682 | -61.0474 | -61.116 | 61.8256 | 0.073242 | 0.036621 | 0.10071 | 62.0132 | -61.1481 | -0.15106 | 0.068664 | -0.11444 | -0.21973 | -0.17395 | -0.25177 | 0.013733 | 0.036621 | 60.9329 | 60.997 | 122.7219 | 122.9645 | -0.11444 | 122.9095 | 60.9695 | -0.25177 | 122.9645 | -0.11444 | 60.9695 | 122.7219 | 122.9095 | -123.0469 | -123.1476
227.7656 | 123.1476 | -60.9146 | 62.0087 | -0.011673 | -0.00052559 | -0.0017303 | 0.0022066 | 0.067368 | 0.0020401 | 0.069547 | -61.0062 | 62.0728 | -61.0611 | -61.1801 | 61.8484 | 0.086975 | 0.059509 | 0.1236 | 62.0178 | -61.1343 | -0.14648 | 0.064087 | -0.091553 | -0.2655 | -0.16022 | -0.21973 | 0.009155 | 0.054931 | 60.9741 | 61.0382 | 122.7631 | 122.9874 | -0.091553 | 122.9324 | 61.0016 | -0.21973 | 122.9874 | -0.091553 | 61.0016 | 122.7631 | 122.9324 | -123.0698 | -123.143
228.7656 | 123.1201 | -60.9238 | 62.0041 | -0.16426 | -0.00073919 | -0.0023711 | 0.00092504 | 0.068223 | -0.0013779 | 0.06912 | -61.0336 | 62.0819 | -61.0428 | -61.1252 | 61.8301 | 0.082397 | 0.073242 | 0.13733 | 61.9949 | -61.1526 | -0.11902 | 0.07782 | -0.10986 | -0.20142 | -0.17395 | -0.22888 | -0.009155 | 0.009156 | 60.997 | 61.0611 | 122.7539 | 123.0057 | -0.10986 | 122.9187 | 61.0062 | -0.22888 | 123.0057 | -0.10986 | 61.0062 | 122.7539 | 122.9187 | -123.0469 | -123.1567
229.7656 | 123.1293 | -60.9192 | 62.0178 | -0.11848 | -0.0035162 | 0.0010467 | 0.00092504 | 0.066941 | -0.0030869 | 0.069974 | -61.0428 | 62.0956 | -61.0657 | -61.1343 | 61.8393 | 0.07782 | 0.10071 | 0.1236 | 61.9995 | -61.1435 | -0.14648 | 0.07782 | -0.1236 | -0.21515 | -0.17853 | -0.2243 | -0.01831 | 0.022888 | 61.0199 | 61.0428 | 122.7585 | 123.0148 | -0.1236 | 122.9187 | 60.997 | -0.2243 | 123.0148 | -0.1236 | 60.997 | 122.7585 | 122.9187 | -123.0835 | -123.1613
230.7656 | 123.143 | -60.9055 | 62.027 | -0.087967 | -0.0041572 | 0.0025421 | 0.0013522 | 0.066941 | -9.6146e-05 | 0.069547 | -61.0107 | 62.0682 | -61.0611 | -61.1298 | 61.8301 | 0.073242 | 0.050354 | 0.12817 | 61.9766 | -61.1343 | -0.15564 | 0.041198 | -0.10529 | -0.2243 | -0.19684 | -0.22888 | -0.050354 | 0.050354 | 60.9558 | 61.0336 | 122.7356 | 122.9736 | -0.10529 | 122.8821 | 60.9787 | -0.22888 | 122.9736 | -0.10529 | 60.9787 | 122.7356 | 122.8821 | -123.0881 | -123.1613
231.7656 | 123.111 | -60.8826 | 62.0178 | -0.11085 | -0.003089 | -0.0021575 | 0.0039156 | 0.068009 | -0.00052335 | 0.068693 | -61.0153 | 62.0636 | -61.0519 | -61.1252 | 61.8622 | 0.09613 | 0.073242 | 0.11902 | 61.9904 | -61.1206 | -0.16937 | 0.045777 | -0.13275 | -0.24262 | -0.15564 | -0.23804 | -0.027466 | 0.036621 | 60.9558 | 61.0016 | 122.7448 | 122.9462 | -0.13275 | 122.8729 | 60.9787 | -0.23804 | 122.9462 | -0.13275 | 60.9787 | 122.7448 | 122.8729 | -123.0698 | -123.1384
232.7656 | 123.0469 | -60.9283 | 61.9949 | -0.034561 | -0.0037298 | -0.0010895 | 0.0022066 | 0.065446 | -0.0018051 | 0.068693 | -61.0153 | 62.0636 | -61.0748 | -61.1206 | 61.8393 | 0.064087 | 0.036621 | 0.10529 | 61.9629 | -61.1481 | -0.14648 | 0.068665 | -0.086975 | -0.19226 | -0.15564 | -0.21973 | -0.032043 | 0.059509 | 60.965 | 61.0336 | 122.7676 | 122.9919 | -0.086975 | 122.8912 | 60.9924 | -0.21973 | 122.9919 | -0.086975 | 60.9924 | 122.7676 | 122.8912 | -123.0698 | -123.143
233.7656 | 123.1522 | -60.8963 | 61.9812 | -0.04982 | -0.0033026 | 0.0021149 | 0.0017794 | 0.068223 | -0.00030975 | 0.070402 | -61.0062 | 62.0773 | -61.0428 | -61.0977 | 61.8393 | 0.073242 | 0.045776 | 0.13275 | 62.0132 | -61.1435 | -0.14648 | 0.096131 | -0.10986 | -0.20142 | -0.14191 | -0.24719 | 0.032044 | 0.036621 | 60.9421 | 61.0291 | 122.7356 | 122.9736 | -0.10986 | 122.9095 | 60.9695 | -0.24719 | 122.9736 | -0.10986 | 60.9695 | 122.7356 | 122.9095 | -123.024 | -123.1247
234.7656 | 123.1293 | -60.9009 | 61.9995 | -0.17952 | -0.00095279 | 0.00019226 | 0.00071144 | 0.066727 | 0.0011857 | 0.068906 | -61.0062 | 62.059 | -61.0519 | -61.0977 | 61.8347 | 0.073242 | 0.068665 | 0.13733 | 61.9812 | -61.1618 | -0.15106 | 0.059509 | -0.10529 | -0.19684 | -0.1648 | -0.26092 | -0.018311 | 0.045776 | 60.9695 | 61.0382 | 122.7356 | 122.9599 | -0.10529 | 122.8821 | 60.9741 | -0.26092 | 122.9599 | -0.10529 | 60.9741 | 122.7356 | 122.8821 | -123.0515 | -123.1613
235.7656 | 123.1064 | -60.9055 | 62.0178 | -0.15663 | -0.00052559 | -0.0030121 | 0.00092504 | 0.067155 | -0.0015915 | 0.07147 | -61.0565 | 62.0682 | -61.0657 | -61.1481 | 61.8073 | 0.059509 | 0.13733 | 0.11444 | 62.0407 | -61.1298 | -0.16022 | 0.050354 | -0.15106 | -0.24261 | -0.21057 | -0.2243 | 0.022888 | 0.009155 | 61.0428 | 61.0199 | 122.7127 | 122.9736 | -0.15106 | 122.9462 | 60.965 | -0.2243 | 122.9736 | -0.15106 | 60.965 | 122.7127 | 122.9462 | -123.0835 | -123.1476
236.7656 | 123.1018 | -60.9055 | 62.0178 | -0.18715 | 0.00032901 | 0.0016877 | -0.00035676 | 0.066087 | -0.00030975 | 0.06912 | -61.0657 | 62.0819 | -61.0565 | -61.1618 | 61.8027 | 0.064087 | 0.13275 | 0.10529 | 61.9995 | -61.1618 | -0.15106 | 0.064087 | -0.16022 | -0.25635 | -0.21515 | -0.25635 | -0.01831 | -0.009155 | 61.0382 | 61.0107 | 122.7081 | 122.9874 | -0.16022 | 122.905 | 60.9695 | -0.25635 | 122.9874 | -0.16022 | 60.9695 | 122.7081 | 122.905 | -123.0743 | -123.1796
237.7656 | 123.1247 | -60.8963 | 62.0087 | -0.15663 | -0.0011664 | -0.0034393 | 0.0015658 | 0.067368 | 0.00011745 | 0.067624 | -61.0336 | 62.0819 | -61.0611 | -61.116 | 61.8347 | 0.07782 | 0.091553 | 0.1236 | 62.0178 | -61.1206 | -0.16479 | 0.073242 | -0.13733 | -0.21973 | -0.17395 | -0.2243 | 0.009155 | 0.027466 | 60.9879 | 61.0199 | 122.731 | 122.9782 | -0.13733 | 122.9141 | 60.9741 | -0.2243 | 122.9782 | -0.13733 | 60.9741 | 122.731 | 122.9141 | -123.0698 | -123.1293
238.7656 | 123.111 | -60.9009 | 62.027 | -0.12611 | 0.00054261 | -0.0038665 | 7.0444e-05 | 0.066941 | -0.0015915 | 0.068265 | -61.0291 | 62.0773 | -61.0565 | -61.1343 | 61.8256 | 0.073242 | 0.10071 | 0.13733 | 62.027 | -61.1526 | -0.15564 | 0.050354 | -0.12817 | -0.23346 | -0.20142 | -0.25177 | 0 | 0.027466 | 61.0016 | 61.0382 | 122.7264 | 122.9782 | -0.12817 | 122.9279 | 60.9741 | -0.25177 | 122.9782 | -0.12817 | 60.9741 | 122.7264 | 122.9279 | -123.0835 | -123.1796
239.7656 | 123.1293 | -60.8963 | 61.9904 | -0.072708 | -0.0020208 | -0.0021575 | 0.0015658 | 0.066087 | -0.00073695 | 0.068052 | -61.0016 | 62.0773 | -61.0565 | -61.1206 | 61.8256 | 0.082397 | 0.054932 | 0.1236 | 62.0041 | -61.1572 | -0.16022 | 0.086976 | -0.10529 | -0.2243 | -0.16479 | -0.26093 | 0.013733 | 0.054932 | 60.9512 | 61.0199 | 122.7219 | 122.9736 | -0.10529 | 122.9004 | 60.9787 | -0.26093 | 122.9736 | -0.10529 | 60.9787 | 122.7219 | 122.9004 | -123.0469 | -123.1476
240.7656 | 123.1338 | -60.9009 | 62.0087 | -0.072708 | -0.0011664 | -0.0057891 | 0.00092504 | 0.064378 | -0.0013779 | 0.069547 | -61.0153 | 62.0728 | -61.0657 | -61.1114 | 61.853 | 0.068665 | 0.050354 | 0.13275 | 61.9904 | -61.1481 | -0.16479 | 0.064087 | -0.11444 | -0.21057 | -0.15564 | -0.24719 | -0.018311 | 0.050354 | 60.9512 | 61.0336 | 122.7539 | 122.9736 | -0.11444 | 122.8912 | 60.9695 | -0.24719 | 122.9736 | -0.11444 | 60.9695 | 122.7539 | 122.8912 | -123.0743 | -123.1567
241.7656 | 123.1338 | -60.878 | 61.9812 | -0.087967 | -0.00073919 | 0.0025421 | -0.00078396 | 0.067155 | -0.0026595 | 0.069547 | -61.0291 | 62.0361 | -61.0611 | -61.1069 | 61.8347 | 0.07782 | 0.068665 | 0.13275 | 62.0041 | -61.1206 | -0.1831 | 0.054932 | -0.15106 | -0.22888 | -0.14648 | -0.24261 | 0.022888 | 0.032043 | 60.9467 | 61.0107 | 122.7127 | 122.9141 | -0.15106 | 122.8821 | 60.9558 | -0.24261 | 122.9141 | -0.15106 | 60.9558 | 122.7127 | 122.8821 | -123.0423 | -123.1018
242.7656 | 123.0743 | -60.9055 | 62.027 | -0.17189 | -0.0015936 | -0.0010895 | -0.00014316 | 0.067582 | 0.00075845 | 0.068052 | -61.0474 | 62.0819 | -61.0886 | -61.1618 | 61.7981 | 0.054932 | 0.14191 | 0.10071 | 62.0087 | -61.1343 | -0.18311 | 0.054931 | -0.14191 | -0.25635 | -0.22888 | -0.22888 | -0.018311 | 0.041199 | 61.0474 | 61.0062 | 122.7036 | 122.9874 | -0.14191 | 122.9141 | 60.9604 | -0.22888 | 122.9874 | -0.14191 | 60.9604 | 122.7036 | 122.9141 | -123.1155 | -123.1613
243.7656 | 123.0881 | -60.9238 | 62.0041 | 0.087509 | -0.0028754 | 0.0012605 | 0.00092504 | 0.066514 | -0.0011643 | 0.069547 | -61.0931 | 62.0728 | -61.0748 | -61.1526 | 61.8164 | 0.036621 | 0.14191 | 0.082397 | 62.027 | -61.1343 | -0.15106 | 0.068665 | -0.16937 | -0.22888 | -0.18768 | -0.21057 | 0.022889 | -0.018311 | 61.0657 | 61.0062 | 122.7402 | 122.9965 | -0.16937 | 122.9507 | 60.9604 | -0.21057 | 122.9965 | -0.16937 | 60.9604 | 122.7402 | 122.9507 | -123.0789 | -123.1384
244.7656 | 123.1247 | -60.91 | 61.9949 | -0.11085 | -0.0035162 | 0.00019226 | 0.0022066 | 0.066727 | -9.6146e-05 | 0.06912 | -61.0382 | 62.0773 | -61.0428 | -61.1298 | 61.8256 | 0.064087 | 0.10529 | 0.12817 | 62.027 | -61.1435 | -0.13275 | 0.082398 | -0.12817 | -0.21973 | -0.16937 | -0.23346 | 0.032044 | 0.004578 | 61.0153 | 61.0382 | 122.7356 | 122.9874 | -0.12817 | 122.937 | 60.9741 | -0.23346 | 122.9874 | -0.12817 | 60.9741 | 122.7356 | 122.937 | -123.0377 | -123.1384
245.7656 | 123.1201 | -60.9055 | 62.0224 | -0.14137 | -0.0022346 | 0.0012605 | 0.0024202 | 0.065873 | -0.0015915 | 0.068479 | -61.0336 | 62.0682 | -61.0519 | -61.1252 | 61.8301 | 0.068665 | 0.13275 | 0.11902 | 62.027 | -61.1252 | -0.14648 | 0.045776 | -0.12817 | -0.21973 | -0.19226 | -0.21973 | 0.004578 | 0.018311 | 61.0382 | 61.0245 | 122.7356 | 122.9736 | -0.12817 | 122.9324 | 60.9741 | -0.21973 | 122.9736 | -0.12817 | 60.9741 | 122.7356 | 122.9324 | -123.0743 | -123.1476
246.7656 | 123.1338 | -60.9192 | 62.0087 | -0.065079 | -0.0011664 | -2.1336e-05 | 0.0013522 | 0.066514 | -0.0018051 | 0.06912 | -61.0062 | 62.0819 | -61.0519 | -61.116 | 61.8393 | 0.082397 | 0.050354 | 0.12817 | 61.9858 | -61.1389 | -0.13275 | 0.073242 | -0.086976 | -0.19684 | -0.16937 | -0.21973 | -0.022888 | 0.045776 | 60.9695 | 61.0474 | 122.7585 | 123.0011 | -0.086976 | 122.905 | 61.0016 | -0.21973 | 123.0011 | -0.086976 | 61.0016 | 122.7585 | 122.905 | -123.0606 | -123.1476
247.7656 | 123.143 | -60.9055 | 62.0224 | -0.087967 | -0.0020208 | 0.0014741 | 0.0022066 | 0.068223 | -0.0030869 | 0.067838 | -61.0245 | 62.059 | -61.0565 | -61.0931 | 61.8301 | 0.082397 | 0.086975 | 0.13275 | 61.9766 | -61.1252 | -0.15106 | 0.036621 | -0.11902 | -0.18768 | -0.19226 | -0.21973 | -0.045776 | 0.032044 | 60.9924 | 61.0382 | 122.7356 | 122.9645 | -0.11902 | 122.8821 | 60.9879 | -0.21973 | 122.9645 | -0.11902 | 60.9879 | 122.7356 | 122.8821 | -123.0789 | -123.1476
248.7656 | 123.1384 | -60.91 | 62.0224 | -0.057449 | -0.0026618 | 0.00019226 | 0.0011386 | 0.068009 | -0.0015915 | 0.068265 | -61.0291 | 62.1048 | -61.084 | -61.1069 | 61.8347 | 0.082397 | 0.086975 | 0.11902 | 61.9858 | -61.1526 | -0.17395 | 0.082397 | -0.11902 | -0.19684 | -0.18768 | -0.24261 | -0.036621 | 0.054931 | 60.997 | 61.0291 | 122.7448 | 123.0148 | -0.11902 | 122.8958 | 60.9924 | -0.24261 | 123.0148 | -0.11902 | 60.9924 | 122.7448 | 122.8958 | -123.1064 | -123.175
249.7656 | 123.0881 | -60.9009 | 62.0224 | -0.17952 | -0.003089 | -0.0062163 | 0.00092504 | 0.068009 | -0.0011643 | 0.069761 | -61.0428 | 62.0911 | -61.0382 | -61.1801 | 61.7935 | 0.041199 | 0.16022 | 0.10529 | 62.027 | -61.1343 | -0.13733 | 0.068664 | -0.14191 | -0.27924 | -0.22888 | -0.23346 | 0.004578 | -0.004578 | 61.0611 | 61.0062 | 122.6944 | 122.9919 | -0.14191 | 122.9279 | 60.9421 | -0.23346 | 122.9919 | -0.14191 | 60.9421 | 122.6944 | 122.9279 | -123.0606 | -123.1567
250.7656 | 123.1155 | -60.91 | 62.0041 | -0.16426 | -0.0022346 | -0.0015167 | -0.0033476 | 0.066514 | -0.00052335 | 0.067411 | -61.0565 | 62.0728 | -61.0703 | -60.9924 | 61.8027 | -0.013733 | 0.086975 | 0.059509 | 62.027 | -61.1298 | -0.16022 | 0.068665 | -0.14648 | -0.082398 | -0.20142 | -0.21973 | 0.022889 | 0.013732 | 60.997 | 60.9695 | 122.7127 | 122.9828 | -0.14648 | 122.937 | 60.8963 | -0.21973 | 122.9828 | -0.14648 | 60.8963 | 122.7127 | 122.937 | -123.0743 | -123.1338
251.7656 | 123.111 | -60.9055 | 62.0224 | -0.087967 | -0.0020208 | -0.0021575 | 0.00028404 | 0.065659 | -0.0020187 | 0.068906 | -61.0611 | 62.0728 | -61.0794 | -61.1435 | 61.8073 | 0.064087 | 0.13733 | 0.09613 | 62.027 | -61.1298 | -0.17395 | 0.050354 | -0.15564 | -0.23804 | -0.21515 | -0.2243 | 0.004578 | 0.018311 | 61.0428 | 61.0016 | 122.7127 | 122.9782 | -0.15564 | 122.9324 | 60.9695 | -0.2243 | 122.9782 | -0.15564 | 60.9695 | 122.7127 | 122.9324 | -123.1018 | -123.1522
252.7656 | 123.0972 | -60.9192 | 62.0041 | -0.11085 | -0.00095279 | 0.0012605 | 0.0017794 | 0.066087 | -0.0028731 | 0.068052 | -61.0611 | 62.0453 | -61.0748 | -61.1618 | 61.7935 | 0.054932 | 0.14191 | 0.09613 | 61.9904 | -61.1206 | -0.15564 | 0.041199 | -0.14191 | -0.24261 | -0.21057 | -0.20142 | -0.013733 | 0.013733 | 61.0611 | 61.0153 | 122.7127 | 122.9645 | -0.14191 | 122.9095 | 60.9741 | -0.20142 | 122.9645 | -0.14191 | 60.9741 | 122.7127 | 122.9095 | -123.0789 | -123.1247
253.7656 | 123.1247 | -60.91 | 61.9949 | -0.14137 | -0.0011664 | -2.1336e-05 | 0.00092504 | 0.066941 | -0.0018051 | 0.069547 | -61.0291 | 62.0819 | -61.0703 | -61.1206 | 61.8393 | 0.086975 | 0.09613 | 0.13275 | 62.0041 | -61.1343 | -0.16022 | 0.086975 | -0.11902 | -0.21057 | -0.15564 | -0.2243 | 0.009155 | 0.041198 | 61.0062 | 61.0428 | 122.7493 | 122.9919 | -0.11902 | 122.9141 | 60.997 | -0.2243 | 122.9919 | -0.11902 | 60.997 | 122.7493 | 122.9141 | -123.0652 | -123.1293
254.7656 | 123.1293 | -60.91 | 62.0316 | -0.11848 | -0.0026618 | 0.00019226 | 0.0024202 | 0.064805 | -0.00095055 | 0.070402 | -61.0565 | 62.0865 | -61.0748 | -61.1389 | 61.821 | 0.050354 | 0.13275 | 0.11902 | 62.0178 | -61.1206 | -0.16479 | 0.054932 | -0.14648 | -0.22888 | -0.21057 | -0.21057 | -0.013733 | 0.01831 | 61.0428 | 61.0291 | 122.731 | 122.9965 | -0.14648 | 122.9279 | 60.9604 | -0.21057 | 122.9965 | -0.14648 | 60.9604 | 122.731 | 122.9279 | -123.1064 | -123.1522
255.7656 | 123.1247 | -60.9192 | 62.0316 | -0.149 | -0.0026618 | -0.0019439 | 0.00028404 | 0.066087 | -0.0022323 | 0.069761 | -61.0703 | 62.0682 | -61.0657 | -61.1343 | 61.8073 | 0.059509 | 0.13733 | 0.10071 | 61.9995 | -61.116 | -0.14648 | 0.036621 | -0.15106 | -0.21515 | -0.2243 | -0.19684 | -0.032043 | -0.004577 | 61.0565 | 61.0199 | 122.7264 | 122.9874 | -0.15106 | 122.9187 | 60.9787 | -0.19684 | 122.9874 | -0.15106 | 60.9787 | 122.7264 | 122.9187 | -123.0972 | -123.1476
256.7656 | 123.1064 | -60.9009 | 62.0361 | -0.18715 | -0.0028754 | -0.00087594 | -0.002493 | 0.064805 | -0.0022323 | 0.068479 | -61.0657 | 62.059 | -61.0703 | -61.1481 | 61.8301 | 0.045776 | 0.15564 | 0.10986 | 61.9904 | -61.1298 | -0.16937 | 0.022888 | -0.16479 | -0.24719 | -0.20599 | -0.22888 | -0.045777 | 0.004577 | 61.0565 | 61.0107 | 122.731 | 122.9599 | -0.16479 | 122.8912 | 60.9467 | -0.22888 | 122.9599 | -0.16479 | 60.9467 | 122.731 | 122.8912 | -123.1064 | -123.1659
257.7656 | 123.111 | -60.9055 | 62.0178 | -0.21004 | -0.0020208 | -0.0025847 | 0.00092504 | 0.068864 | -0.0022323 | 0.06912 | -61.0153 | 62.1048 | -61.0474 | -61.1572 | 61.7752 | 0.041199 | 0.16022 | 0.10071 | 62.0224 | -61.1389 | -0.14191 | 0.086975 | -0.10986 | -0.25177 | -0.24261 | -0.23346 | 0.004578 | 0.032043 | 61.0657 | 61.0062 | 122.6807 | 123.0103 | -0.10986 | 122.9279 | 60.9467 | -0.23346 | 123.0103 | -0.10986 | 60.9467 | 122.6807 | 122.9279 | -123.0652 | -123.1567
258.7656 | 123.0789 | -60.91 | 62.0132 | -0.17189 | -0.0028754 | -0.0025847 | -0.00099756 | 0.064378 | -0.0020187 | 0.066984 | -61.0794 | 62.0499 | -61.0519 | -60.9833 | 61.908 | 0.013733 | 0.07782 | 0.050354 | 62.027 | -61.1343 | -0.14191 | 0.036621 | -0.16937 | -0.073242 | -0.10529 | -0.2243 | 0.013733 | -0.027466 | 60.9879 | 60.9604 | 122.818 | 122.9599 | -0.16937 | 122.937 | 60.9238 | -0.2243 | 122.9599 | -0.16937 | 60.9238 | 122.818 | 122.937 | -123.0652 | -123.1476
259.7656 | 123.1064 | -60.9146 | 62.0361 | -0.15663 | -0.0015936 | -0.0023711 | -0.00035676 | 0.066087 | -0.00030975 | 0.068052 | -61.0611 | 62.0453 | -61.0748 | -61.1664 | 61.8073 | 0.050354 | 0.17395 | 0.10986 | 62.0316 | -61.116 | -0.16022 | 0.009155 | -0.14648 | -0.25177 | -0.22888 | -0.20142 | -0.004578 | 0.013733 | 61.0886 | 61.0245 | 122.7219 | 122.9599 | -0.14648 | 122.9462 | 60.965 | -0.20142 | 122.9599 | -0.14648 | 60.965 | 122.7219 | 122.9462 | -123.111 | -123.1522
260.7656 | 123.0789 | -60.9009 | 62.0132 | -0.080337 | -0.0022346 | -2.1336e-05 | -0.00057036 | 0.063309 | -9.6146e-05 | 0.069761 | -61.0428 | 62.0636 | -61.0748 | -61.1435 | 61.8073 | 0.054932 | 0.12817 | 0.09613 | 62.0087 | -61.116 | -0.17395 | 0.050354 | -0.14191 | -0.24261 | -0.20599 | -0.21515 | -0.004578 | 0.032043 | 61.0291 | 60.997 | 122.7081 | 122.9645 | -0.14191 | 122.9095 | 60.9558 | -0.21515 | 122.9645 | -0.14191 | 60.9558 | 122.7081 | 122.9095 | -123.0881 | -123.1293
261.7656 | 123.0881 | -60.91 | 62.0407 | -2.27 | -0.0024482 | -0.0027985 | -0.00078396 | 0.06395 | -0.0039413 | 0.06912 | -61.0886 | 62.0499 | -61.0474 | -61.1526 | 61.7798 | 0.068665 | 0.16022 | 0.1236 | 62.0132 | -61.1435 | -0.13733 | 0.009156 | -0.17853 | -0.24261 | -0.26093 | -0.23346 | -0.027465 | -0.041199 | 61.0703 | 61.0336 | 122.6898 | 122.9599 | -0.17853 | 122.9233 | 60.9787 | -0.23346 | 122.9599 | -0.17853 | 60.9787 | 122.6898 | 122.9233 | -123.0881 | -123.1842
262.7656 | 123.0698 | -60.9283 | 62.0224 | -0.20241 | -0.0011664 | -0.0010895 | -0.0012112 | 0.066087 | -0.0022323 | 0.068479 | -61.0565 | 62.0407 | -61.0611 | -61.1435 | 61.7111 | -0.036621 | 0.1236 | 0.091553 | 61.9904 | -61.1252 | -0.13275 | 0.01831 | -0.12817 | -0.21515 | -0.31128 | -0.19684 | -0.032044 | 0.004577 | 61.0519 | 61.0199 | 122.6395 | 122.9691 | -0.12817 | 122.9187 | 60.8917 | -0.19684 | 122.9691 | -0.12817 | 60.8917 | 122.6395 | 122.9187 | -123.0835 | -123.1476
263.7656 | 123.1064 | -60.9055 | 62.027 | -0.21767 | -0.0035162 | -0.0036529 | -0.0020658 | 0.066087 | 0.00075845 | 0.069761 | -61.0107 | 62.0224 | -61.0565 | -61.1023 | 61.8393 | 0.086975 | 0.11902 | 0.14191 | 62.0132 | -61.084 | -0.15106 | -0.004578 | -0.10529 | -0.19684 | -0.18768 | -0.17853 | -0.013733 | 0.045777 | 61.0245 | 61.0474 | 122.7448 | 122.9279 | -0.10529 | 122.9187 | 60.9924 | -0.17853 | 122.9279 | -0.10529 | 60.9924 | 122.7448 | 122.9187 | -123.0835 | -123.111
264.7656 | 123.1064 | -60.9009 | 62.0453 | -0.15663 | -0.0041572 | -0.0047211 | 0.00071144 | 0.063096 | -0.00073695 | 0.067411 | -61.0519 | 62.0316 | -61.0657 | -61.1664 | 61.8118 | 0.059509 | 0.17395 | 0.13275 | 62.0178 | -61.0886 | -0.16479 | -0.013733 | -0.15106 | -0.2655 | -0.23346 | -0.18768 | -0.027466 | 0.013733 | 61.0748 | 61.0336 | 122.7127 | 122.9324 | -0.15106 | 122.9187 | 60.9604 | -0.18768 | 122.9324 | -0.15106 | 60.9604 | 122.7127 | 122.9187 | -123.111 | -123.1338
265.7656 | 123.0927 | -60.9055 | 62.0407 | -0.12611 | -0.0041572 | -0.0040801 | -0.0018522 | 0.063309 | -0.0020187 | 0.068906 | -61.0565 | 62.0178 | -61.084 | -61.1481 | 61.8073 | 0.045776 | 0.16022 | 0.12817 | 62.0132 | -61.1114 | -0.17853 | -0.022888 | -0.15106 | -0.24261 | -0.23346 | -0.20599 | -0.027465 | 0.027465 | 61.0657 | 61.0336 | 122.7127 | 122.9233 | -0.15106 | 122.9187 | 60.9512 | -0.20599 | 122.9233 | -0.15106 | 60.9512 | 122.7127 | 122.9187 | -123.1247 | -123.1522
266.7656 | 123.111 | -60.8917 | 62.0178 | -0.18715 | -0.0041572 | -0.0038665 | -0.0018522 | 0.065018 | -0.0011643 | 0.068052 | -61.0565 | 62.0178 | -61.0565 | -61.1572 | 61.8118 | 0.059509 | 0.13275 | 0.11902 | 61.9766 | -61.1252 | -0.16479 | 0 | -0.16479 | -0.2655 | -0.20599 | -0.23346 | -0.041198 | 0 | 61.0245 | 61.0107 | 122.7036 | 122.9095 | -0.16479 | 122.8683 | 60.9512 | -0.23346 | 122.9095 | -0.16479 | 60.9512 | 122.7036 | 122.8683 | -123.0743 | -123.143
267.7656 | 123.0423 | -60.878 | 62.0361 | -0.21004 | -0.0037298 | -0.0015167 | 0.00092504 | 0.063309 | -0.0015915 | 0.067838 | -61.0657 | 62.0499 | -61.0703 | -61.1481 | 61.7981 | 0.068665 | 0.15106 | 0.21973 | 61.9995 | -61.0565 | -0.19226 | 0.013733 | -0.18768 | -0.27008 | -0.23804 | -0.17853 | -0.036621 | 0.004577 | 61.0291 | 61.0977 | 122.6761 | 122.9279 | -0.18768 | 122.8775 | 60.9467 | -0.17853 | 122.9279 | -0.18768 | 60.9467 | 122.6761 | 122.8775 | -123.1064 | -123.0927
268.7656 | 123.0972 | -60.8963 | 62.0224 | -0.16426 | -0.0026618 | -0.0036529 | 0.0030612 | 0.065232 | 0.00033105 | 0.068906 | -61.0611 | 62.0407 | -61.0565 | -61.1389 | 61.8118 | 0.050354 | 0.16022 | 0.11444 | 62.0224 | -61.1206 | -0.16022 | 0.01831 | -0.16479 | -0.24262 | -0.21057 | -0.2243 | 0 | -0.004577 | 61.0565 | 61.0107 | 122.7081 | 122.937 | -0.16479 | 122.9187 | 60.9467 | -0.2243 | 122.937 | -0.16479 | 60.9467 | 122.7081 | 122.9187 | -123.0789 | -123.143
269.7656 | 123.0606 | -60.9009 | 62.0361 | -0.17952 | -0.0037298 | -0.0036529 | 7.0444e-05 | 0.062669 | -0.0033005 | 0.069761 | -61.0519 | 62.0361 | -61.0886 | -61.1435 | 61.8027 | 0.050354 | 0.14648 | 0.11444 | 62.0178 | -61.1206 | -0.18768 | 0 | -0.15106 | -0.24261 | -0.23346 | -0.21973 | -0.018311 | 0.036621 | 61.0474 | 61.0153 | 122.7036 | 122.937 | -0.15106 | 122.9187 | 60.9512 | -0.21973 | 122.937 | -0.15106 | 60.9512 | 122.7036 | 122.9187 | -123.1247 | -123.1567
270.7812 | 123.1796 | -60.91 | 61.9492 | 0.28587 | -0.0024482 | -0.00087594 | 0.0030612 | 0.065018 | -0.0013779 | 0.070402 | -61.0382 | 61.9949 | -61.0519 | -61.1206 | 61.8484 | 0.022888 | -0.17395 | 0.050354 | 61.9125 | -61.1298 | -0.14191 | 0.045776 | -0.12817 | -0.21057 | -0.10071 | -0.21973 | -0.036621 | 0.013733 | 60.7361 | 60.9604 | 122.7585 | 122.905 | -0.12817 | 122.8226 | 60.9329 | -0.21973 | 122.905 | -0.12817 | 60.9329 | 122.7585 | 122.8226 | -123.0011 | -123.0789
271.7656 | 123.0927 | -60.9009 | 62.0178 | -0.17189 | -0.0054388 | -0.0077117 | -0.00035676 | 0.062241 | -0.0043685 | 0.069547 | -61.0336 | 62.0361 | -61.0519 | -61.1389 | 61.8301 | 0.073242 | 0.12817 | 0.1236 | 61.9858 | -61.084 | -0.15106 | 0.018311 | -0.13275 | -0.23804 | -0.18768 | -0.1831 | -0.032043 | 0.018311 | 61.0291 | 61.0245 | 122.731 | 122.937 | -0.13275 | 122.8867 | 60.9741 | -0.1831 | 122.937 | -0.13275 | 60.9741 | 122.731 | 122.8867 | -123.0698 | -123.1018
272.7656 | 123.1064 | -60.8643 | 62.0178 | -0.17952 | -0.0018072 | -0.0038665 | -0.00099756 | 0.062455 | 0.00011745 | 0.069761 | -61.0336 | 61.9995 | -61.0565 | -61.1298 | 61.8347 | 0.064087 | 0.13733 | 0.14648 | 61.9675 | -61.1069 | -0.19226 | -0.01831 | -0.16937 | -0.2655 | -0.18311 | -0.24262 | -0.050354 | 0.022889 | 61.0016 | 61.0107 | 122.699 | 122.8638 | -0.16937 | 122.8317 | 60.9283 | -0.24262 | 122.8638 | -0.16937 | 60.9283 | 122.699 | 122.8317 | -123.0743 | -123.1247
273.7656 | 123.1659 | -60.9055 | 62.059 | -0.16426 | -0.00138 | 0.0014741 | 0.0039156 | 0.066514 | -0.0037277 | 0.068693 | -61.0657 | 62.0499 | -61.084 | -61.1389 | 61.8073 | 0.041199 | 0.14648 | 0.10071 | 62.0041 | -61.1252 | -0.17853 | -0.009155 | -0.16022 | -0.23346 | -0.25177 | -0.21973 | -0.054932 | 0.01831 | 61.0519 | 61.0062 | 122.7127 | 122.9553 | -0.16022 | 122.9095 | 60.9467 | -0.21973 | 122.9553 | -0.16022 | 60.9467 | 122.7127 | 122.9095 | -123.143 | -123.1842
274.7656 | 123.0835 | -60.9146 | 62.027 | -0.21004 | -0.0028754 | -0.0021575 | 0.002634 | 0.063309 | -0.0043685 | 0.06912 | -61.0657 | 62.0361 | -61.0703 | -61.1481 | 61.821 | 0.045776 | 0.16022 | 0.10986 | 62.0087 | -61.1252 | -0.15564 | 0.009155 | -0.15106 | -0.23346 | -0.20599 | -0.21057 | -0.018311 | 0.004577 | 61.0748 | 61.0245 | 122.7356 | 122.9507 | -0.15106 | 122.9233 | 60.9604 | -0.21057 | 122.9507 | -0.15106 | 60.9604 | 122.7356 | 122.9233 | -123.0972 | -123.1522
275.7812 | 123.0698 | -60.9467 | 62.0087 | 0.11803 | -0.0022346 | 0.0019013 | 0.003702 | 0.066941 | -0.0030869 | 0.06912 | -61.0336 | 62.0544 | -61.0474 | -61.1481 | 61.7661 | -0.041199 | 0.032043 | -0.032043 | 61.9904 | -61.1526 | -0.10071 | 0.045776 | -0.086975 | -0.20142 | -0.24262 | -0.20599 | -0.018311 | 0.013733 | 60.9787 | 60.9146 | 122.7127 | 123.0011 | -0.086975 | 122.937 | 60.9055 | -0.20599 | 123.0011 | -0.086975 | 60.9055 | 122.7127 | 122.937 | -123.056 | -123.1613
276.7656 | 123.0789 | -60.9146 | 61.9995 | -0.23293 | -0.0024482 | -0.00044854 | 0.00071144 | 0.062455 | -0.0013779 | 0.067411 | -61.0703 | 62.027 | -61.084 | -61.1481 | 61.8256 | 0.073242 | 0.13733 | 0.11444 | 62.0132 | -61.0977 | -0.16937 | 0.027466 | -0.15564 | -0.23346 | -0.17395 | -0.18311 | 0.013733 | 0.013733 | 61.0519 | 61.0291 | 122.7402 | 122.9416 | -0.15564 | 122.9279 | 60.9879 | -0.18311 | 122.9416 | -0.15564 | 60.9879 | 122.7402 | 122.9279 | -123.0835 | -123.0972
277.7656 | 123.1522 | -60.8826 | 62.0178 | -0.17189 | -0.0022346 | -0.00066214 | -0.0012112 | 0.062669 | -0.00030975 | 0.067197 | -61.0016 | 61.9949 | -61.0611 | -61.0611 | 61.8896 | 0.12817 | 0.018311 | 0.21515 | 61.9995 | -61.0794 | -0.17853 | -0.022888 | -0.11902 | -0.17853 | -0.12817 | -0.19684 | -0.01831 | 0.059509 | 60.9009 | 61.0977 | 122.7722 | 122.8775 | -0.11902 | 122.8821 | 61.0107 | -0.19684 | 122.8775 | -0.11902 | 61.0107 | 122.7722 | 122.8821 | -123.0789 | -123.0972
278.7656 | 123.0652 | -60.91 | 62.0407 | -0.17189 | -0.0037298 | -0.0038665 | -0.00057036 | 0.063096 | -0.0020187 | 0.068052 | -61.0382 | 62.0224 | -61.0748 | -61.084 | 61.8164 | 0.050354 | 0.15564 | 0.1236 | 61.9949 | -61.1069 | -0.16479 | -0.01831 | -0.12817 | -0.17395 | -0.2243 | -0.19684 | -0.045776 | 0.036621 | 61.0657 | 61.0336 | 122.7264 | 122.9324 | -0.12817 | 122.905 | 60.9604 | -0.19684 | 122.9324 | -0.12817 | 60.9604 | 122.7264 | 122.905 | -123.1155 | -123.1476
279.7656 | 123.0972 | -60.8963 | 62.0132 | -0.20241 | -0.0037298 | -0.00066214 | 0.00049764 | 0.06395 | -0.0024459 | 0.069333 | -61.0382 | 62.0041 | -61.0565 | -61.1114 | 61.8256 | 0.082397 | 0.13733 | 0.15564 | 61.9949 | -61.1069 | -0.16022 | -0.009156 | -0.14191 | -0.21515 | -0.18768 | -0.21057 | -0.018311 | 0.018311 | 61.0336 | 61.0519 | 122.7219 | 122.9004 | -0.14191 | 122.8912 | 60.9787 | -0.21057 | 122.9004 | -0.14191 | 60.9787 | 122.7219 | 122.8912 | -123.0698 | -123.1201
280.7812 | 123.143 | -60.9146 | 61.9583 | 0.28587 | -0.0041572 | -0.0034393 | 0.0045566 | 0.066087 | -0.00030975 | 0.068265 | -61.0611 | 62.0087 | -61.0794 | -61.1572 | 61.8073 | -0.022888 | -0.091553 | 0.018311 | 61.9446 | -61.1618 | -0.1648 | 0.050354 | -0.14648 | -0.24262 | -0.15106 | -0.24719 | -0.013733 | 0.018311 | 60.8231 | 60.9329 | 122.7219 | 122.9233 | -0.14648 | 122.8592 | 60.8917 | -0.24719 | 122.9233 | -0.14648 | 60.8917 | 122.7219 | 122.8592 | -123.0377 | -123.1201
281.7656 | 123.0881 | -60.9009 | 62.0316 | -0.18715 | -0.0033026 | -0.0053619 | -0.00057036 | 0.064164 | -0.00030975 | 0.066556 | -61.0611 | 62.0453 | -61.0657 | -61.1298 | 61.8164 | 0.064087 | 0.16022 | 0.10986 | 62.0224 | -61.1114 | -0.16479 | 0.013733 | -0.16022 | -0.22888 | -0.21515 | -0.21057 | -0.009155 | 0.004578 | 61.0611 | 61.0107 | 122.7173 | 122.9462 | -0.16022 | 122.9233 | 60.965 | -0.21057 | 122.9462 | -0.16022 | 60.965 | 122.7173 | 122.9233 | -123.0972 | -123.143
282.7656 | 123.0652 | -60.8917 | 62.027 | -0.15663 | -0.0028754 | -0.0025847 | 0.001993 | 0.06395 | -0.0020187 | 0.06912 | -61.0703 | 62.059 | -61.0794 | -61.1435 | 61.8073 | 0.050354 | 0.15564 | 0.11444 | 61.9858 | -61.1069 | -0.18768 | 0.032043 | -0.17853 | -0.25177 | -0.21973 | -0.21515 | -0.041199 | 0.009156 | 61.0474 | 61.0062 | 122.699 | 122.9507 | -0.17853 | 122.8775 | 60.9421 | -0.21515 | 122.9507 | -0.17853 | 60.9421 | 122.699 | 122.8775 | -123.1064 | -123.1339
283.7656 | 123.1567 | -60.9009 | 62.0041 | -0.17189 | -0.0050116 | -0.0027985 | 7.0444e-05 | 0.064378 | -0.0024459 | 0.069974 | -60.9879 | 61.9812 | -61.0382 | -61.0657 | 61.8851 | 0.11902 | 0.050354 | 0.20599 | 61.972 | -61.0931 | -0.13733 | -0.022888 | -0.086975 | -0.16479 | -0.11902 | -0.19226 | -0.032043 | 0.050354 | 60.9512 | 61.1069 | 122.786 | 122.8821 | -0.086975 | 122.8729 | 61.0199 | -0.19226 | 122.8821 | -0.086975 | 61.0199 | 122.786 | 122.8729 | -123.0423 | -123.0972
284.7656 | 123.1247 | -60.878 | 62.027 | -0.16426 | -0.0018072 | -0.0019439 | -0.00057036 | 0.062028 | -0.0037277 | 0.069974 | -60.9924 | 61.9858 | -61.0382 | -61.0657 | 61.908 | 0.14191 | 0.036621 | 0.21515 | 61.9583 | -61.0748 | -0.16022 | -0.041199 | -0.11444 | -0.18768 | -0.11902 | -0.19684 | -0.068665 | 0.045776 | 60.9146 | 61.0931 | 122.7859 | 122.8638 | -0.11444 | 122.8363 | 61.0199 | -0.19684 | 122.8638 | -0.11444 | 61.0199 | 122.7859 | 122.8363 | -123.0652 | -123.1018
285.7812 | 123.0515 | -60.9238 | 61.9904 | 0.13329 | -0.0024482 | 0.0012605 | 0.0041292 | 0.066087 | -0.0024459 | 0.069761 | -61.084 | 62.0407 | -61.1206 | -61.2167 | 61.7386 | -0.036621 | 0.009155 | -0.032043 | 61.9675 | -61.1114 | -0.19684 | 0.050354 | -0.16022 | -0.29297 | -0.25177 | -0.18768 | -0.022888 | 0.036621 | 60.9329 | 60.8917 | 122.6624 | 122.9645 | -0.16022 | 122.8912 | 60.8871 | -0.18768 | 122.9645 | -0.16022 | 60.8871 | 122.6624 | 122.8912 | -123.111 | -123.1018
286.7656 | 123.0927 | -60.8871 | 62.0453 | -0.17189 | -0.0033026 | -0.0045075 | -0.00099756 | 0.065873 | -0.00095055 | 0.070402 | -61.0199 | 62.0132 | -61.0519 | -61.1252 | 61.8393 | 0.082397 | 0.10986 | 0.16937 | 62.0087 | -61.0611 | -0.16479 | -0.032043 | -0.13275 | -0.23804 | -0.20599 | -0.17395 | -0.036621 | 0.032044 | 60.997 | 61.0565 | 122.7264 | 122.9004 | -0.13275 | 122.8958 | 60.9695 | -0.17395 | 122.9004 | -0.13275 | 60.9695 | 122.7264 | 122.8958 | -123.0972 | -123.1064
287.7656 | 123.1613 | -60.9009 | 62.0773 | -0.17952 | -0.0045844 | -0.00066214 | -0.00078396 | 0.065232 | -0.0020187 | 0.067838 | -61.0519 | 62.059 | -61.0611 | -61.1389 | 61.8073 | 0.064087 | 0.15564 | 0.10529 | 62.0041 | -61.1069 | -0.16022 | -0.018311 | -0.15106 | -0.23804 | -0.27008 | -0.20599 | -0.073243 | 0.009155 | 61.0565 | 61.0062 | 122.7081 | 122.9599 | -0.15106 | 122.905 | 60.965 | -0.20599 | 122.9599 | -0.15106 | 60.965 | 122.7081 | 122.905 | -123.1384 | -123.1842
288.7656 | 123.0789 | -60.9238 | 62.0407 | -0.16426 | -0.0033026 | -0.0051483 | -0.00014316 | 0.065018 | -0.0026595 | 0.067411 | -61.0657 | 62.0041 | -61.0565 | -61.1252 | 61.7981 | 0.054932 | 0.16022 | 0.10986 | 62.0041 | -61.1069 | -0.13275 | -0.036621 | -0.14191 | -0.20142 | -0.24261 | -0.18311 | -0.036621 | -0.009155 | 61.084 | 61.0336 | 122.7219 | 122.9279 | -0.14191 | 122.9279 | 60.9787 | -0.18311 | 122.9279 | -0.14191 | 60.9787 | 122.7219 | 122.9279 | -123.0972 | -123.1476
289.7656 | 123.0789 | -60.9055 | 62.0224 | -0.095596 | -0.0024482 | -0.0051483 | 0.0017794 | 0.064805 | -0.0013779 | 0.068906 | -61.0657 | 62.0407 | -61.0519 | -61.1343 | 61.8301 | 0.059509 | 0.15564 | 0.13275 | 62.0041 | -61.0931 | -0.14648 | 0.01831 | -0.16022 | -0.22888 | -0.19226 | -0.18768 | -0.018311 | -0.013733 | 61.0611 | 61.0382 | 122.7356 | 122.9462 | -0.16022 | 122.9095 | 60.965 | -0.18768 | 122.9462 | -0.16022 | 60.965 | 122.7356 | 122.9095 | -123.0743 | -123.1155
290.7656 | 123.1705 | -60.8826 | 61.9766 | -0.11848 | -0.0035162 | -0.0025847 | 0.0017794 | 0.063523 | -0.0039413 | 0.068052 | -60.9924 | 61.972 | -61.0336 | -61.0657 | 61.908 | 0.15564 | 0.022888 | 0.2243 | 61.9629 | -61.0886 | -0.15106 | -0.004578 | -0.10986 | -0.18311 | -0.068665 | -0.20599 | -0.013733 | 0.041198 | 60.9055 | 61.1069 | 122.7905 | 122.8546 | -0.10986 | 122.8455 | 61.0382 | -0.20599 | 122.8546 | -0.10986 | 61.0382 | 122.7905 | 122.8455 | -123.0103 | -123.0652
291.7656 | 123.1567 | -60.8551 | 61.9949 | -0.19478 | -0.0056524 | -0.0053619 | 7.0444e-05 | 0.064164 | -0.0050095 | 0.068265 | -60.9741 | 61.9949 | -61.0474 | -61.0474 | 61.9125 | 0.15106 | -0.004578 | 0.2243 | 61.9629 | -61.0382 | -0.19226 | 0 | -0.11902 | -0.19226 | -0.082397 | -0.1831 | -0.032043 | 0.073242 | 60.8505 | 61.0794 | 122.7676 | 122.85 | -0.11902 | 122.818 | 61.0062 | -0.1831 | 122.85 | -0.11902 | 61.0062 | 122.7676 | 122.818 | -123.0423 | -123.0331
292.7656 | 123.1064 | -60.8917 | 62.0224 | -0.20241 | -0.0037298 | 0.0023285 | 7.0444e-05 | 0.06096 | -0.0026595 | 0.069333 | -61.0062 | 61.9858 | -61.0291 | -61.0886 | 61.8713 | 0.10986 | 0.086975 | 0.16479 | 61.9583 | -61.1069 | -0.13733 | -0.036621 | -0.11444 | -0.19684 | -0.15106 | -0.21515 | -0.064087 | 0.022888 | 60.9787 | 61.0565 | 122.7631 | 122.8775 | -0.11444 | 122.85 | 61.0016 | -0.21515 | 122.8775 | -0.11444 | 61.0016 | 122.7631 | 122.85 | -123.0515 | -123.1293
293.7656 | 123.1613 | -60.8597 | 62.0041 | -0.21004 | -0.0043708 | -0.0027985 | 0.0011386 | 0.061814 | 0.00033105 | 0.068479 | -60.9879 | 61.9904 | -61.0291 | -61.0565 | 61.8851 | 0.14191 | 0.073242 | 0.20142 | 61.9858 | -61.0794 | -0.16937 | -0.013733 | -0.12817 | -0.19684 | -0.11902 | -0.21973 | -0.01831 | 0.041199 | 60.9329 | 61.0611 | 122.7448 | 122.85 | -0.12817 | 122.8455 | 61.0016 | -0.21973 | 122.85 | -0.12817 | 61.0016 | 122.7448 | 122.8455 | -123.0331 | -123.0835
294.7656 | 123.1064 | -60.9055 | 62.0132 | -0.11085 | -0.0028754 | -0.0032257 | 0.0017794 | 0.063737 | -0.0030869 | 0.066984 | -61.0703 | 62.027 | -61.0657 | -61.1252 | 61.8118 | 0.073242 | 0.14191 | 0.12817 | 62.0132 | -61.1114 | -0.16022 | 0.013733 | -0.16479 | -0.21973 | -0.20142 | -0.20599 | 0 | -0.004577 | 61.0474 | 61.0336 | 122.7173 | 122.9324 | -0.16479 | 122.9187 | 60.9787 | -0.20599 | 122.9324 | -0.16479 | 60.9787 | 122.7173 | 122.9187 | -123.0789 | -123.1247
295.7656 | 123.1064 | -60.91 | 62.027 | -0.149 | -0.0033026 | -0.0025847 | 0.0015658 | 0.062882 | -0.0018051 | 0.06677 | -61.0199 | 62.0087 | -61.0611 | -61.116 | 61.8484 | 0.091553 | 0.11902 | 0.14191 | 62.0087 | -61.0886 | -0.15106 | -0.018311 | -0.10986 | -0.20599 | -0.17853 | -0.17853 | -0.018311 | 0.041199 | 61.0291 | 61.0519 | 122.7585 | 122.9187 | -0.10986 | 122.9187 | 61.0016 | -0.17853 | 122.9187 | -0.10986 | 61.0016 | 122.7585 | 122.9187 | -123.0881 | -123.1155
296.7656 | 123.1064 | -60.9192 | 61.9904 | -0.17952 | -0.0067206 | -0.00087594 | 0.00071144 | 0.065018 | -0.0047957 | 0.068693 | -61.0016 | 61.9904 | -61.0474 | -61.0931 | 61.853 | 0.10071 | 0.091553 | 0.16022 | 61.9904 | -61.0657 | -0.12817 | 0 | -0.082398 | -0.17395 | -0.13733 | -0.14648 | 0 | 0.045776 | 61.0107 | 61.0794 | 122.7722 | 122.9095 | -0.082398 | 122.9095 | 61.0199 | -0.14648 | 122.9095 | -0.082398 | 61.0199 | 122.7722 | 122.9095 | -123.0377 | -123.056
297.7656 | 123.175 | -60.8871 | 61.9995 | 0.71312 | -0.0041572 | -0.00044854 | 0.00092504 | 0.063309 | -0.0018051 | 0.068052 | -61.0016 | 61.9812 | -61.0657 | -61.0153 | 61.9263 | 0.15564 | -0.027466 | 0.23346 | 61.9446 | -61.0291 | -0.17853 | -0.018311 | -0.11444 | -0.12817 | -0.073242 | -0.14191 | -0.054932 | 0.064087 | 60.8597 | 61.1206 | 122.8134 | 122.8683 | -0.11444 | 122.8317 | 61.0428 | -0.14191 | 122.8683 | -0.11444 | 61.0428 | 122.8134 | 122.8317 | -123.0652 | -123.0286
298.7656 | 123.175 | -60.8871 | 61.9583 | -0.15663 | -0.0060798 | 0.00019226 | 0.0017794 | 0.060319 | -0.0050095 | 0.068693 | -61.0748 | 62.0087 | -61.0107 | -61.0245 | 61.8942 | 0.11902 | -0.045776 | 0.21515 | 61.9354 | -61.0565 | -0.1236 | 0.050354 | -0.18768 | -0.13733 | -0.064087 | -0.16937 | -0.022888 | -0.064087 | 60.8414 | 61.1023 | 122.7814 | 122.8958 | -0.18768 | 122.8226 | 61.0062 | -0.16937 | 122.8958 | -0.18768 | 61.0062 | 122.7814 | 122.8226 | -122.9691 | -123.0148
299.7656 | 123.1476 | -60.878 | 61.9949 | -0.149 | -0.0024482 | 0.00019226 | 0.00092504 | 0.062882 | -0.0018051 | 0.069333 | -60.9787 | 62.0041 | -61.0428 | -61.0565 | 61.8942 | 0.1236 | 0.032043 | 0.21973 | 61.9766 | -61.0703 | -0.16479 | 0.009155 | -0.10071 | -0.17853 | -0.10071 | -0.19226 | -0.01831 | 0.064087 | 60.91 | 61.0977 | 122.7722 | 122.8821 | -0.10071 | 122.8546 | 61.0016 | -0.19226 | 122.8821 | -0.10071 | 61.0016 | 122.7722 | 122.8546 | -123.0377 | -123.0652
300.7656 | 123.1567 | -60.8551 | 62.0224 | -0.080337 | -0.004798 | -0.0068573 | 0.00049764 | 0.063096 | -0.0026595 | 0.069761 | -60.9833 | 61.9537 | -61.0428 | -61.0474 | 61.8988 | 0.13275 | 0.022888 | 0.21973 | 61.9446 | -61.084 | -0.18768 | -0.068665 | -0.12817 | -0.19226 | -0.1236 | -0.22888 | -0.07782 | 0.05951 | 60.878 | 61.0748 | 122.7539 | 122.8088 | -0.12817 | 122.7997 | 60.9879 | -0.22888 | 122.8088 | -0.12817 | 60.9879 | 122.7539 | 122.7997 | -123.0652 | -123.1064
301.7656 | 123.0881 | -60.8963 | 62.0132 | -0.18715 | -0.0026618 | -0.0034393 | 0.00028404 | 0.06395 | -0.0022323 | 0.069547 | -61.0062 | 61.9995 | -61.0519 | -61.1252 | 61.853 | 0.07782 | 0.091553 | 0.14191 | 61.9904 | -61.0931 | -0.15564 | -0.013733 | -0.10986 | -0.22888 | -0.16022 | -0.19684 | -0.022889 | 0.045776 | 60.9879 | 61.0382 | 122.7493 | 122.8958 | -0.10986 | 122.8867 | 60.9741 | -0.19684 | 122.8958 | -0.10986 | 60.9741 | 122.7493 | 122.8867 | -123.0652 | -123.1064
302.7656 | 123.1338 | -60.8826 | 62.0087 | -0.18715 | -0.0041572 | -0.0021575 | 0.0024202 | 0.064164 | -0.0037277 | 0.068906 | -60.9924 | 62.0087 | -61.0336 | -61.0931 | 61.853 | 0.11444 | 0.091553 | 0.18768 | 61.9858 | -61.0794 | -0.15106 | 0 | -0.10986 | -0.21057 | -0.15564 | -0.19684 | -0.022888 | 0.041198 | 60.9741 | 61.0703 | 122.7356 | 122.8912 | -0.10986 | 122.8683 | 60.997 | -0.19684 | 122.8912 | -0.10986 | 60.997 | 122.7356 | 122.8683 | -123.0423 | -123.0881
303.7656 | 123.1384 | -60.8871 | 61.9949 | -0.17952 | -0.0050116 | -0.0010895 | 0.00049764 | 0.063523 | -0.0028731 | 0.068265 | -61.0016 | 61.9675 | -61.0291 | -61.0703 | 61.8851 | 0.1236 | 0.07782 | 0.17853 | 61.9675 | -61.0565 | -0.14191 | -0.027466 | -0.11444 | -0.1831 | -0.10986 | -0.16937 | -0.027466 | 0.027466 | 60.965 | 61.0657 | 122.7722 | 122.8546 | -0.11444 | 122.8546 | 61.0107 | -0.16937 | 122.8546 | -0.11444 | 61.0107 | 122.7722 | 122.8546 | -123.024 | -123.0515
304.7656 | 123.1888 | -60.8963 | 62.0041 | -0.12611 | -0.0028754 | -0.0040801 | -0.004202 | 0.062882 | -0.0033005 | 0.069761 | -60.9695 | 61.9537 | -61.0199 | -61.0382 | 61.8713 | 0.11444 | -0.036621 | 0.19684 | 61.94 | -61.0474 | -0.1236 | -0.050354 | -0.073242 | -0.14191 | -0.13275 | -0.15106 | -0.064087 | 0.050354 | 60.8597 | 61.0931 | 122.7676 | 122.85 | -0.073242 | 122.8363 | 61.0107 | -0.15106 | 122.85 | -0.073242 | 61.0107 | 122.7676 | 122.8363 | -123.024 | -123.0515
305.7656 | 123.2025 | -60.8871 | 61.9904 | -0.10323 | -0.0045844 | -0.0062163 | 7.0444e-05 | 0.063523 | 0.00033105 | 0.06677 | -60.9558 | 61.9537 | -61.0107 | -61.1206 | 62.1048 | 0.42114 | -0.2243 | 0.07782 | 61.9446 | -61.0748 | -0.1236 | -0.036621 | -0.068665 | -0.23346 | 0.11444 | -0.18768 | -0.045776 | 0.054931 | 60.6628 | 60.965 | 122.9919 | 122.8409 | -0.068665 | 122.8317 | 61.3083 | -0.18768 | 122.8409 | -0.068665 | 61.3083 | 122.9919 | 122.8317 | -123.0011 | -123.0652
306.7656 | 123.175 | -60.8643 | 62.0361 | -0.13374 | -0.0056524 | -0.0045075 | 0.001993 | 0.061173 | -0.0026595 | 0.068693 | -60.9787 | 61.9629 | -61.0428 | -61.0474 | 61.9034 | 0.14648 | 0.027466 | 0.23804 | 61.94 | -61.0519 | -0.17853 | -0.073242 | -0.11444 | -0.1831 | -0.13275 | -0.18768 | -0.096131 | 0.064087 | 60.8917 | 61.1023 | 122.7676 | 122.8271 | -0.11444 | 122.8043 | 61.0107 | -0.18768 | 122.8271 | -0.11444 | 61.0107 | 122.7676 | 122.8043 | -123.0789 | -123.0881
307.7656 | 123.0881 | -60.9009 | 62.0453 | -0.17189 | -0.004798 | -0.0047211 | 0.0022066 | 0.063096 | -0.0026595 | 0.065916 | -61.0062 | 61.9995 | -61.0748 | -61.1023 | 61.821 | 0.086975 | 0.082397 | 0.14648 | 61.9766 | -61.084 | -0.17395 | -0.045776 | -0.10529 | -0.20142 | -0.2243 | -0.1831 | -0.068664 | 0.068664 | 60.9833 | 61.0474 | 122.7219 | 122.9004 | -0.10529 | 122.8775 | 60.9879 | -0.1831 | 122.9004 | -0.10529 | 60.9879 | 122.7219 | 122.8775 | -123.1201 | -123.1293
308.7656 | 123.1018 | -60.9009 | 62.0224 | -0.17189 | -0.0028754 | -0.0036529 | 0.004343 | 0.062669 | -0.0050095 | 0.068052 | -61.0107 | 61.9949 | -61.0657 | -61.084 | 61.8484 | 0.082397 | 0.10529 | 0.16937 | 61.9858 | -61.1023 | -0.16479 | -0.027466 | -0.10986 | -0.1831 | -0.17395 | -0.20142 | -0.036621 | 0.054932 | 61.0062 | 61.0703 | 122.7493 | 122.8958 | -0.10986 | 122.8867 | 60.9833 | -0.20142 | 122.8958 | -0.10986 | 60.9833 | 122.7493 | 122.8867 | -123.0881 | -123.1247
309.7656 | 123.1522 | -60.8826 | 62.0224 | -0.23293 | -0.0056524 | -0.00023494 | 0.00071144 | 0.064805 | -0.0022323 | 0.066984 | -60.9833 | 61.9949 | -61.0474 | -61.0748 | 61.8713 | 0.10529 | 0.068665 | 0.17395 | 61.9766 | -61.0748 | -0.16479 | -0.027466 | -0.10071 | -0.19226 | -0.15106 | -0.19226 | -0.045776 | 0.064087 | 60.9512 | 61.0565 | 122.7539 | 122.8775 | -0.10071 | 122.8592 | 60.9879 | -0.19226 | 122.8775 | -0.10071 | 60.9879 | 122.7539 | 122.8592 | -123.0698 | -123.0972
310.7656 | 123.175 | -60.8871 | 62.0132 | -0.21004 | -0.0026618 | -0.0045075 | 0.0013522 | 0.064164 | -0.0054367 | 0.068479 | -60.997 | 61.9904 | -61.0474 | -61.084 | 61.8713 | 0.11444 | 0.064087 | 0.18768 | 61.9858 | -61.0886 | -0.16022 | -0.022889 | -0.10986 | -0.19684 | -0.14191 | -0.20142 | -0.027466 | 0.050354 | 60.9512 | 61.0748 | 122.7585 | 122.8775 | -0.10986 | 122.8729 | 61.0016 | -0.20142 | 122.8775 | -0.10986 | 61.0016 | 122.7585 | 122.8729 | -123.0606 | -123.1018
311.7656 | 123.1934 | -60.8871 | 61.9949 | -0.095596 | -0.0062934 | -0.0047211 | -0.00099756 | 0.068864 | -0.0047957 | 0.067624 | -60.9695 | 61.9766 | -61.0199 | -61.1343 | 61.7386 | 0.1236 | -0.09613 | 0.22888 | 61.9492 | -61.0565 | -0.13275 | -0.01831 | -0.082397 | -0.24719 | -0.25635 | -0.16937 | -0.045776 | 0.050354 | 60.791 | 61.116 | 122.6257 | 122.8638 | -0.082397 | 122.8363 | 61.0107 | -0.16937 | 122.8638 | -0.082397 | 61.0107 | 122.6257 | 122.8363 | -123.0148 | -123.0515
312.7656 | 123.2391 | -60.8505 | 61.9766 | -0.11085 | -0.0050116 | -0.0051483 | 0.00049764 | 0.064164 | -0.0041549 | 0.066984 | -60.965 | 61.9629 | -61.0245 | -61.0382 | 61.9125 | 0.036621 | 0.37079 | 0.41199 | 62.0132 | -61.0291 | -0.17395 | -0.013733 | -0.11444 | -0.18768 | -0.064087 | -0.17853 | 0.036621 | 0.059509 | 61.2213 | 61.2625 | 122.7631 | 122.8134 | -0.11444 | 122.8638 | 60.8871 | -0.17853 | 122.8134 | -0.11444 | 60.8871 | 122.7631 | 122.8638 | -123.0011 | -123.0057
313.7656 | 123.1613 | -60.8734 | 62.0132 | -0.15663 | -0.0039434 | -0.0042937 | -0.00057036 | 0.064378 | -0.0035141 | 0.069974 | -60.9787 | 61.972 | -61.0474 | -61.0382 | 61.9034 | 0.14648 | 0.004578 | 0.2243 | 61.94 | -61.0519 | -0.17395 | -0.041199 | -0.10529 | -0.16479 | -0.10986 | -0.17853 | -0.073243 | 0.068664 | 60.878 | 61.0977 | 122.7768 | 122.8455 | -0.10529 | 122.8134 | 61.0199 | -0.17853 | 122.8455 | -0.10529 | 61.0199 | 122.7768 | 122.8134 | -123.0606 | -123.0652
314.7656 | 123.175 | -60.8643 | 62.0224 | 0.40794 | -0.0033026 | -0.0053619 | -0.00099756 | 0.061173 | -0.0018051 | 0.06912 | -60.9695 | 61.9537 | -61.0245 | -61.0382 | 61.9125 | 0.15106 | -0.013733 | 0.22888 | 61.9446 | -61.084 | -0.16022 | -0.068665 | -0.10529 | -0.17395 | -0.10986 | -0.21973 | -0.07782 | 0.054932 | 60.8505 | 61.0931 | 122.7768 | 122.818 | -0.10529 | 122.8088 | 61.0153 | -0.21973 | 122.818 | -0.10529 | 61.0153 | 122.7768 | 122.8088 | -123.0469 | -123.1064
315.7656 | 123.1247 | -60.9055 | 62.0178 | -0.21767 | -0.0054388 | -0.0030121 | 0.001993 | 0.06395 | -0.0026595 | 0.068479 | -61.0016 | 61.9858 | -61.0519 | -61.084 | 61.8759 | 0.11444 | 0.091553 | 0.17853 | 61.9629 | -61.0657 | -0.14648 | -0.032043 | -0.09613 | -0.17853 | -0.14191 | -0.16022 | -0.054931 | 0.050354 | 60.997 | 61.084 | 122.7814 | 122.8912 | -0.09613 | 122.8683 | 61.0199 | -0.16022 | 122.8912 | -0.09613 | 61.0199 | 122.7814 | 122.8683 | -123.0698 | -123.0835
316.7656 | 123.143 | -60.8917 | 62.0041 | -0.18715 | -0.0054388 | -0.0047211 | 0.0013522 | 0.060319 | -0.0020187 | 0.067624 | -60.997 | 61.9949 | -61.0428 | -61.0657 | 61.8896 | 0.1236 | 0.054932 | 0.18768 | 61.9492 | -61.0886 | -0.15106 | -0.009155 | -0.10528 | -0.17395 | -0.11444 | -0.19684 | -0.054931 | 0.045777 | 60.9467 | 61.0794 | 122.7814 | 122.8867 | -0.10528 | 122.8409 | 61.0153 | -0.19684 | 122.8867 | -0.10528 | 61.0153 | 122.7814 | 122.8409 | -123.0469 | -123.0927
317.7656 | 123.143 | -60.8871 | 62.0087 | -0.15663 | -0.0056524 | -0.00023494 | 0.0011386 | 0.06395 | -0.0043685 | 0.067624 | -60.9787 | 61.972 | -61.0611 | -61.0703 | 61.8942 | 0.13733 | 0.041199 | 0.21515 | 61.9766 | -61.0428 | -0.17395 | -0.036621 | -0.091553 | -0.1831 | -0.11444 | -0.15564 | -0.032043 | 0.082397 | 60.9283 | 61.1023 | 122.7814 | 122.8592 | -0.091553 | 122.8638 | 61.0245 | -0.15564 | 122.8592 | -0.091553 | 61.0245 | 122.7814 | 122.8638 | -123.0698 | -123.0515
318.7656 | 123.2071 | -60.8551 | 62.0132 | -0.13374 | -0.0041572 | -0.0023711 | 0.00028404 | 0.064378 | -0.0045821 | 0.06912 | -60.9604 | 61.9629 | -61.0336 | -61.0245 | 61.9125 | 0.16479 | -0.036621 | 0.26093 | 61.94 | -61.0703 | -0.17853 | -0.050354 | -0.10529 | -0.16937 | -0.10071 | -0.21515 | -0.073243 | 0.073242 | 60.8185 | 61.116 | 122.7676 | 122.818 | -0.10529 | 122.7951 | 61.0199 | -0.21515 | 122.818 | -0.10529 | 61.0199 | 122.7676 | 122.7951 | -123.0469 | -123.0835
319.7656 | 123.1842 | -60.8734 | 62.0178 | 0.34691 | -0.0035162 | -0.0021575 | 0.0015658 | 0.063737 | -0.0065047 | 0.067197 | -60.9833 | 61.9537 | -61.0519 | -61.0428 | 61.9263 | 0.15564 | -0.018311 | 0.2243 | 61.9354 | -61.0428 | -0.17853 | -0.064087 | -0.10986 | -0.16937 | -0.091552 | -0.16937 | -0.082397 | 0.068665 | 60.8551 | 61.0977 | 122.7997 | 122.8271 | -0.10986 | 122.8088 | 61.0291 | -0.16937 | 122.8271 | -0.10986 | 61.0291 | 122.7997 | 122.8088 | -123.0698 | -123.0606
320.7656 | 123.175 | -60.8505 | 61.9766 | -0.95009 | -0.0086432 | -0.0013031 | 0.00092504 | 0.062882 | -0.0041549 | 0.067411 | -60.8414 | 61.9995 | -61.0428 | -61.0657 | 61.908 | 0.14191 | -0.009155 | 0.24261 | 61.9537 | -61.0565 | -0.19226 | 0.022888 | 0.009155 | -0.21515 | -0.068665 | -0.20599 | -0.022889 | 0.20142 | 60.8414 | 61.0931 | 122.7585 | 122.85 | 0.009155 | 122.8043 | 60.9924 | -0.20599 | 122.85 | 0.009155 | 60.9924 | 122.7585 | 122.8043 | -123.0194 | -123.0331
321.7656 | 123.1842 | -60.8643 | 61.9583 | -0.12611 | -0.0045844 | -0.0040801 | 0.0011386 | 0.062241 | -0.0080001 | 0.068693 | -60.9604 | 61.9583 | -61.0291 | -60.8917 | 61.702 | 0.018311 | -0.07782 | 0.18768 | 61.9354 | -61.0703 | -0.16479 | 0 | -0.09613 | -0.027466 | -0.25635 | -0.20599 | -0.022888 | 0.068665 | 60.7864 | 61.0519 | 122.5662 | 122.8226 | -0.09613 | 122.7997 | 60.8826 | -0.20599 | 122.8226 | -0.09613 | 60.8826 | 122.5662 | 122.7997 | -122.9874 | -123.0286
322.7656 | 123.1613 | -60.8597 | 62.0041 | -0.11848 | -0.0067206 | -0.0021575 | 0.0034884 | 0.062455 | -0.0045821 | 0.06912 | -60.9787 | 61.972 | -61.0336 | -61.0382 | 61.9034 | 0.14191 | 0.027466 | 0.21515 | 61.9446 | -61.0703 | -0.17395 | -0.032043 | -0.11902 | -0.17853 | -0.10071 | -0.21057 | -0.059509 | 0.054931 | 60.8871 | 61.0748 | 122.7631 | 122.8317 | -0.11902 | 122.8043 | 61.0016 | -0.21057 | 122.8317 | -0.11902 | 61.0016 | 122.7631 | 122.8043 | -123.0377 | -123.0743
323.7656 | 123.1705 | -60.8643 | 62.0224 | 0.026474 | -0.0041572 | -0.0051483 | 0.0032748 | 0.063523 | -0.0024459 | 0.06912 | -60.997 | 61.9629 | -61.0474 | -61.0382 | 61.9171 | 0.14648 | -0.013733 | 0.21515 | 61.94 | -61.0657 | -0.1831 | -0.059509 | -0.13275 | -0.17395 | -0.10529 | -0.20142 | -0.082398 | 0.050354 | 60.8505 | 61.0794 | 122.7814 | 122.8271 | -0.13275 | 122.8043 | 61.0107 | -0.20142 | 122.8271 | -0.13275 | 61.0107 | 122.7814 | 122.8043 | -123.0698 | -123.0881
324.7656 | 123.1979 | -60.8688 | 61.9904 | -0.10323 | -0.005866 | 0.0023285 | 0.0030612 | 0.062669 | -0.0037277 | 0.070402 | -60.8963 | 61.9858 | -61.0245 | -61.0245 | 61.8622 | 0.11902 | -0.045776 | 0.21515 | 61.9171 | -61.0474 | -0.15564 | -0.004577 | -0.027466 | -0.15564 | -0.12817 | -0.17853 | -0.073242 | 0.12817 | 60.8231 | 61.084 | 122.731 | 122.8546 | -0.027466 | 122.7859 | 60.9879 | -0.17853 | 122.8546 | -0.027466 | 60.9879 | 122.731 | 122.7859 | -123.0148 | -123.0377
325.7656 | 123.2071 | -60.8643 | 61.9858 | -0.026932 | -0.0054388 | -0.0055755 | -0.00035676 | 0.06096 | -0.0033005 | 0.06912 | -60.9787 | 61.9583 | -61.0382 | -61.0291 | 61.8942 | 0.14648 | -0.054932 | 0.25635 | 61.9446 | -61.0291 | -0.17395 | -0.027466 | -0.11444 | -0.16479 | -0.091553 | -0.16479 | -0.041199 | 0.059509 | 60.8093 | 61.1206 | 122.7585 | 122.8226 | -0.11444 | 122.8088 | 61.0107 | -0.16479 | 122.8226 | -0.11444 | 61.0107 | 122.7585 | 122.8088 | -123.024 | -123.0148
326.7656 | 123.23 | -60.8551 | 61.9858 | -0.11085 | -0.0052252 | -0.0057891 | 0.00092504 | 0.062882 | -0.0045821 | 0.070188 | -60.9512 | 61.9446 | -61.0291 | -61.0291 | 61.9217 | 0.15564 | -0.041199 | 0.26093 | 61.9354 | -61.0382 | -0.17395 | -0.041199 | -0.09613 | -0.17395 | -0.064087 | -0.1831 | -0.050354 | 0.07782 | 60.8139 | 61.116 | 122.7768 | 122.7997 | -0.09613 | 122.7905 | 61.0107 | -0.1831 | 122.7997 | -0.09613 | 61.0107 | 122.7768 | 122.7905 | -123.0148 | -123.024
327.7656 | 123.23 | -60.8551 | 61.9995 | -0.04219 | -0.0028754 | -0.0030121 | -0.00078396 | 0.06096 | -0.0028731 | 0.068479 | -60.9741 | 61.9492 | -61.0474 | -61.0245 | 61.9217 | 0.17853 | -0.07782 | 0.24261 | 61.9354 | -61.0382 | -0.19226 | -0.050354 | -0.11902 | -0.16937 | -0.07782 | -0.1831 | -0.064087 | 0.073242 | 60.7773 | 61.0977 | 122.7768 | 122.8043 | -0.11902 | 122.7905 | 61.0336 | -0.1831 | 122.8043 | -0.11902 | 61.0336 | 122.7768 | 122.7905 | -123.0469 | -123.0377
328.7656 | 123.1979 | -60.8505 | 61.9766 | -0.11085 | -0.0039434 | -0.0053619 | -0.0020658 | 0.063523 | -0.0020187 | 0.068479 | -60.9604 | 61.94 | -61.0611 | -61.0062 | 61.7157 | 0.31586 | 0.15106 | 0.018311 | 61.9812 | -61.0336 | -0.21057 | -0.036622 | -0.10986 | -0.15564 | -0.26093 | -0.18311 | 0.004577 | 0.10071 | 61.0016 | 60.8688 | 122.5662 | 122.7905 | -0.10986 | 122.8317 | 61.1664 | -0.18311 | 122.7905 | -0.10986 | 61.1664 | 122.5662 | 122.8317 | -123.0377 | -123.0103
329.7656 | 123.1979 | -60.878 | 61.9812 | -0.20241 | -0.0041572 | -0.0017303 | 0.0024202 | 0.064378 | -0.0045821 | 0.067624 | -60.9467 | 61.9446 | -61.0428 | -61.0245 | 61.9125 | 0.16937 | -0.018311 | 0.23804 | 61.9492 | -61.0519 | -0.16479 | -0.036621 | -0.068664 | -0.14648 | -0.068664 | -0.17395 | -0.032043 | 0.096131 | 60.8597 | 61.116 | 122.7905 | 122.8226 | -0.068664 | 122.8271 | 61.0474 | -0.17395 | 122.8226 | -0.068664 | 61.0474 | 122.7905 | 122.8271 | -123.024 | -123.0331
330.7656 | 123.23 | -60.8459 | 61.9766 | -0.14137 | -0.0039434 | -0.0010895 | 0.0013522 | 0.059464 | -0.0058639 | 0.067624 | -60.965 | 61.9583 | -61.0291 | -60.997 | 61.9446 | 0.16937 | -0.07782 | 0.23804 | 61.9583 | -61.0291 | -0.18311 | -0.018311 | -0.11902 | -0.15106 | -0.032044 | -0.18311 | -0.018311 | 0.064087 | 60.7681 | 61.084 | 122.7905 | 122.8043 | -0.11902 | 122.8043 | 61.0153 | -0.18311 | 122.8043 | -0.11902 | 61.0153 | 122.7905 | 122.8043 | -123.0057 | -123.0057
331.7656 | 123.2254 | -60.8688 | 61.9858 | -0.13374 | -0.0054388 | -0.0047211 | 0.001993 | 0.060105 | -0.0024459 | 0.06912 | -60.9741 | 61.9446 | -61.0519 | -61.0336 | 61.9171 | 0.17395 | -0.073242 | 0.22888 | 61.9446 | -61.0199 | -0.18311 | -0.041199 | -0.10529 | -0.1648 | -0.068665 | -0.15106 | -0.041199 | 0.07782 | 60.7956 | 61.0977 | 122.7859 | 122.8134 | -0.10529 | 122.8134 | 61.0428 | -0.15106 | 122.8134 | -0.10529 | 61.0428 | 122.7859 | 122.8134 | -123.0377 | -123.0057
332.7656 | 123.1613 | -60.8871 | 61.972 | 0.041733 | -0.0043708 | -0.0066437 | 0.00092504 | 0.062241 | -0.0011643 | 0.070188 | -61.0245 | 61.9537 | -61.0382 | -61.0977 | 61.8668 | 0.082397 | -0.068665 | 0.13275 | 61.9125 | -61.0703 | -0.15106 | -0.018311 | -0.13733 | -0.21057 | -0.10529 | -0.1831 | -0.059509 | 0.013733 | 60.8185 | 61.0199 | 122.7539 | 122.8409 | -0.13733 | 122.7997 | 60.9695 | -0.1831 | 122.8409 | -0.13733 | 60.9695 | 122.7539 | 122.7997 | -123.0103 | -123.0423
333.7656 | 123.1567 | -60.8734 | 61.9995 | 0.049362 | -0.0041572 | -0.0019439 | 0.00092504 | 0.059678 | -0.0026595 | 0.067197 | -61.0519 | 61.9537 | -61.0657 | -61.116 | 61.8576 | 0.045776 | -0.064087 | 0.13275 | 61.9263 | -61.084 | -0.19226 | -0.045777 | -0.17853 | -0.24262 | -0.14191 | -0.21057 | -0.073242 | 0.013733 | 60.8093 | 61.0062 | 122.731 | 122.8271 | -0.17853 | 122.7997 | 60.9192 | -0.21057 | 122.8271 | -0.17853 | 60.9192 | 122.731 | 122.7997 | -123.0652 | -123.0835
334.7656 | 123.2254 | -60.8688 | 61.9949 | -0.019302 | -0.0043708 | -0.0019439 | -0.00099756 | 0.062455 | -0.00095055 | 0.068479 | -61.0153 | 61.9537 | -61.0794 | -61.0703 | 61.8759 | 0.10529 | -0.059509 | 0.17853 | 61.9492 | -61.0474 | -0.21057 | -0.041199 | -0.14649 | -0.20142 | -0.11902 | -0.17853 | -0.045776 | 0.064087 | 60.8093 | 61.0474 | 122.7448 | 122.8226 | -0.14649 | 122.818 | 60.9741 | -0.17853 | 122.8226 | -0.14649 | 60.9741 | 122.7448 | 122.818 | -123.0743 | -123.0423
335.7656 | 123.1842 | -60.878 | 61.9904 | 0.049362 | -0.0043708 | -0.0040801 | -0.001425 | 0.060319 | -0.0013779 | 0.069761 | -61.0062 | 61.9354 | -61.0245 | -61.0703 | 61.8851 | 0.10071 | -0.050354 | 0.18768 | 61.9171 | -61.0703 | -0.14648 | -0.054931 | -0.12817 | -0.19226 | -0.10528 | -0.19226 | -0.073242 | 0.01831 | 60.8276 | 61.0657 | 122.7631 | 122.8134 | -0.12817 | 122.7951 | 60.9787 | -0.19226 | 122.8134 | -0.12817 | 60.9787 | 122.7631 | 122.7951 | -123.0148 | -123.0606
336.7656 | 123.2208 | -60.8276 | 61.9583 | -0.057449 | -0.005866 | -0.0021575 | 7.0444e-05 | 0.062455 | -0.0024459 | 0.06677 | -60.9879 | 61.9263 | -61.0519 | -61.0153 | 61.9308 | 0.15106 | -0.07782 | 0.21515 | 61.9354 | -61.0565 | -0.2243 | -0.032043 | -0.16022 | -0.18768 | -0.027466 | -0.22888 | -0.022888 | 0.064087 | 60.7498 | 61.0428 | 122.7585 | 122.7539 | -0.16022 | 122.7631 | 60.9787 | -0.22888 | 122.7539 | -0.16022 | 60.9787 | 122.7585 | 122.7631 | -123.0103 | -123.0148
337.7656 | 123.2254 | -60.8597 | 61.9766 | -0.026932 | -0.0052252 | -0.0032257 | 0.0017794 | 0.06395 | -0.0024459 | 0.067838 | -60.9879 | 61.9446 | -61.0245 | -61.0107 | 61.8988 | 0.16022 | -0.07782 | 0.23346 | 61.9492 | -61.0428 | -0.1648 | -0.032044 | -0.12817 | -0.15106 | -0.07782 | -0.18311 | -0.027466 | 0.036621 | 60.7819 | 61.0931 | 122.7585 | 122.8043 | -0.12817 | 122.8088 | 61.0199 | -0.18311 | 122.8043 | -0.12817 | 61.0199 | 122.7585 | 122.8088 | -123.0011 | -123.0194
338.7656 | 123.2025 | -60.8551 | 61.972 | -0.019302 | -0.004798 | -0.0051483 | 0.0013522 | 0.062669 | -0.0037277 | 0.068265 | -60.9879 | 61.9263 | -61.0382 | -61.0428 | 61.9171 | 0.14648 | -0.059509 | 0.20599 | 61.94 | -61.0519 | -0.1831 | -0.045776 | -0.13275 | -0.18768 | -0.054932 | -0.19684 | -0.032044 | 0.050354 | 60.7956 | 61.0611 | 122.7722 | 122.7814 | -0.13275 | 122.7951 | 61.0016 | -0.19684 | 122.7814 | -0.13275 | 61.0016 | 122.7722 | 122.7951 | -123.0103 | -123.024
339.7656 | 123.1567 | -60.8871 | 61.9812 | 0.072251 | -0.0073614 | -0.0047211 | 0.00028404 | 0.059891 | -0.0024459 | 0.070402 | -61.0474 | 61.9308 | -61.0657 | -61.0886 | 61.8576 | 0.073242 | -0.064087 | 0.1236 | 61.9492 | -61.0657 | -0.17853 | -0.050354 | -0.16022 | -0.20142 | -0.1236 | -0.17853 | -0.032043 | 0.018311 | 60.8231 | 61.0107 | 122.7448 | 122.818 | -0.16022 | 122.8363 | 60.9604 | -0.17853 | 122.818 | -0.16022 | 60.9604 | 122.7448 | 122.8363 | -123.0469 | -123.0469
340.7656 | 123.2025 | -60.8505 | 61.9812 | -0.072708 | -0.0039434 | -0.0023711 | 0.001993 | 0.0616 | -0.0024459 | 0.070402 | -61.0016 | 61.9583 | -61.0382 | -61.0382 | 61.9034 | 0.13275 | -0.086975 | 0.20142 | 61.9308 | -61.0428 | -0.18768 | -0.022888 | -0.15106 | -0.18768 | -0.07782 | -0.19226 | -0.050354 | 0.036621 | 60.7635 | 61.0519 | 122.7539 | 122.8088 | -0.15106 | 122.7814 | 60.9833 | -0.19226 | 122.8088 | -0.15106 | 60.9833 | 122.7539 | 122.7814 | -123.0194 | -123.024
341.7656 | 123.2162 | -60.8643 | 62.0453 | -0.11085 | -0.0043708 | -0.0049347 | -0.00078396 | 0.06395 | -0.0043685 | 0.068479 | -60.965 | 61.9263 | -61.0291 | -61.0153 | 61.9354 | 0.16022 | -0.045776 | 0.23804 | 61.9308 | -61.0657 | -0.16479 | -0.11902 | -0.10071 | -0.15106 | -0.10986 | -0.20142 | -0.11444 | 0.064087 | 60.8185 | 61.1023 | 122.7997 | 122.7905 | -0.10071 | 122.7951 | 61.0245 | -0.20142 | 122.7905 | -0.10071 | 61.0245 | 122.7997 | 122.7951 | -123.0743 | -123.111
342.7656 | 123.23 | -60.8368 | 62.0041 | -0.11085 | -0.004798 | -0.0055755 | 0.001993 | 0.065446 | -0.0041549 | 0.070402 | -60.9421 | 61.9583 | -61.0519 | -61.0153 | 61.9308 | 0.15564 | -0.036621 | 0.24719 | 61.9354 | -61.0336 | -0.21515 | -0.045776 | -0.10529 | -0.17853 | -0.073242 | -0.19684 | -0.068664 | 0.10986 | 60.8002 | 61.084 | 122.7676 | 122.7951 | -0.10529 | 122.7722 | 60.9924 | -0.19684 | 122.7951 | -0.10529 | 60.9924 | 122.7676 | 122.7722 | -123.056 | -123.0377
343.7656 | 123.2117 | -60.8276 | 62.0132 | -0.04982 | -0.005866 | -0.0042937 | 0.0015658 | 0.062882 | -0.0045821 | 0.067624 | -60.9558 | 61.9812 | -61.0565 | -61.0153 | 61.9354 | 0.16479 | -0.045776 | 0.25635 | 61.9446 | -61.0336 | -0.22888 | -0.032044 | -0.12817 | -0.18768 | -0.07782 | -0.20599 | -0.068665 | 0.10071 | 60.7819 | 61.084 | 122.7631 | 122.8088 | -0.12817 | 122.7722 | 60.9924 | -0.20599 | 122.8088 | -0.12817 | 60.9924 | 122.7631 | 122.7722 | -123.0698 | -123.0469
344.7656 | 123.2391 | -60.8643 | 62.0361 | -0.13374 | -0.0073614 | -0.0021575 | 0.00028404 | 0.063523 | -0.0054367 | 0.069333 | -60.965 | 61.9675 | -61.0565 | -61.0153 | 61.9308 | 0.16479 | -0.032043 | 0.24719 | 61.9354 | -61.0519 | -0.19226 | -0.068665 | -0.10071 | -0.15106 | -0.10529 | -0.18768 | -0.10071 | 0.091553 | 60.8322 | 61.1114 | 122.7951 | 122.8317 | -0.10071 | 122.7997 | 61.0291 | -0.18768 | 122.8317 | -0.10071 | 61.0291 | 122.7951 | 122.7997 | -123.0927 | -123.0881
345.7656 | 123.3078 | -60.8368 | 62.0636 | -0.12611 | -0.0054388 | -0.0051483 | 0.001993 | 0.060746 | -0.0030869 | 0.068479 | -60.9421 | 61.9354 | -61.0428 | -61.0291 | 61.9217 | 0.16937 | -0.050354 | 0.25635 | 61.9308 | -61.0474 | -0.20599 | -0.12817 | -0.10529 | -0.19226 | -0.14191 | -0.21057 | -0.13275 | 0.10071 | 60.7864 | 61.0931 | 122.7585 | 122.7722 | -0.10529 | 122.7676 | 61.0062 | -0.21057 | 122.7722 | -0.10529 | 61.0062 | 122.7585 | 122.7676 | -123.1064 | -123.111
346.7656 | 123.2162 | -60.8643 | 61.9858 | -0.019302 | -0.0054388 | -0.0055755 | -0.00099756 | 0.060746 | -0.0039413 | 0.068052 | -61.0016 | 61.9537 | -61.0519 | -61.0519 | 61.908 | 0.15106 | -0.07782 | 0.21515 | 61.9354 | -61.0519 | -0.18768 | -0.032044 | -0.13733 | -0.18768 | -0.07782 | -0.18768 | -0.050354 | 0.050354 | 60.7864 | 61.0794 | 122.7722 | 122.818 | -0.13733 | 122.7997 | 61.0153 | -0.18768 | 122.818 | -0.13733 | 61.0153 | 122.7722 | 122.7997 | -123.0377 | -123.0377
347.7656 | 123.2208 | -60.8597 | 61.9766 | -0.13374 | -0.0011664 | -0.0010895 | -0.00057036 | 0.062028 | -0.00052335 | 0.071256 | -60.9787 | 61.972 | -61.0382 | -61.0199 | 61.9217 | 0.050354 | 0.36163 | 0.42114 | 61.972 | -61.0336 | -0.17853 | -0.004578 | -0.11902 | -0.16022 | -0.054932 | -0.17395 | -0.004578 | 0.059509 | 61.2213 | 61.2808 | 122.7814 | 122.8317 | -0.11902 | 122.8317 | 60.91 | -0.17395 | 122.8317 | -0.11902 | 60.91 | 122.7814 | 122.8317 | -123.0148 | -123.0103
348.7656 | 123.23 | -60.8505 | 61.9812 | -0.10323 | -0.0060798 | -0.0032257 | 0.00071144 | 0.063737 | -0.0047957 | 0.064847 | -60.9604 | 61.9537 | -61.0474 | -60.8322 | 62.1918 | 0.29297 | -0.23804 | 0.2243 | 61.9308 | -61.0519 | -0.19684 | -0.027466 | -0.10986 | 0.018311 | 0.21057 | -0.20142 | -0.050354 | 0.086975 | 60.6125 | 61.0748 | 123.0423 | 122.8043 | -0.10986 | 122.7814 | 61.1435 | -0.20142 | 122.8043 | -0.10986 | 61.1435 | 123.0423 | 122.7814 | -123.0286 | -123.0331
349.7656 | 123.1476 | -60.878 | 61.9995 | -0.14137 | -0.004798 | -0.0010895 | 0.0041292 | 0.062669 | -0.0026595 | 0.067838 | -60.9741 | 61.9904 | -61.0519 | -61.0519 | 61.8851 | 0.13275 | 0.054932 | 0.20142 | 61.9537 | -61.0519 | -0.17395 | -0.009156 | -0.09613 | -0.17395 | -0.11444 | -0.17395 | -0.045777 | 0.07782 | 60.9329 | 61.0794 | 122.7631 | 122.8683 | -0.09613 | 122.8317 | 61.0107 | -0.17395 | 122.8683 | -0.09613 | 61.0107 | 122.7631 | 122.8317 | -123.0515 | -123.0515
350.7656 | 123.1201 | -60.8734 | 62.0361 | -0.095596 | -0.0037298 | -0.0017303 | 0.0077608 | 0.064805 | -0.0052231 | 0.068052 | -61.0291 | 62.0316 | -61.0703 | -61.1023 | 61.8393 | 0.07782 | 0.10986 | 0.11902 | 61.9995 | -61.0794 | -0.19684 | -0.004578 | -0.15564 | -0.22888 | -0.19684 | -0.20599 | -0.036621 | 0.041198 | 60.9833 | 60.9924 | 122.7127 | 122.905 | -0.15564 | 122.8729 | 60.9512 | -0.20599 | 122.905 | -0.15564 | 60.9512 | 122.7127 | 122.8729 | -123.1064 | -123.1155
351.7656 | 123.1018 | -60.9009 | 61.9949 | -0.18715 | -0.0056524 | -0.0034393 | 0.0011386 | 0.064378 | -0.0041549 | 0.070615 | -61.0016 | 61.9858 | -61.0428 | -61.084 | 61.8713 | 0.11902 | 0.07782 | 0.17395 | 61.9812 | -61.0519 | -0.14191 | -0.009155 | -0.10071 | -0.1831 | -0.1236 | -0.15106 | -0.013733 | 0.041199 | 60.9787 | 61.0748 | 122.7722 | 122.8867 | -0.10071 | 122.8821 | 61.0199 | -0.15106 | 122.8867 | -0.10071 | 61.0199 | 122.7722 | 122.8821 | -123.0377 | -123.0469
352.7656 | 123.1842 | -60.8688 | 61.9949 | 0.026474 | -0.0043708 | 0.00019226 | 0.00028404 | 0.064378 | -0.0035141 | 0.066984 | -60.9879 | 61.972 | -61.0382 | -61.0382 | 61.9125 | 0.17395 | -0.013733 | 0.23346 | 61.9263 | -61.0245 | -0.16937 | -0.022888 | -0.11902 | -0.16937 | -0.082397 | -0.15564 | -0.068664 | 0.050354 | 60.8551 | 61.1023 | 122.7814 | 122.8409 | -0.11902 | 122.7951 | 61.0428 | -0.15564 | 122.8409 | -0.11902 | 61.0428 | 122.7814 | 122.7951 | -123.0331 | -123.0194
353.7656 | 123.1705 | -60.878 | 62.0087 | -0.087967 | -0.003089 | 0.0014741 | -0.001425 | 0.063309 | -0.0039413 | 0.069974 | -60.9879 | 61.9949 | -61.0474 | -61.0336 | 61.9125 | 0.15564 | 0.013733 | 0.21057 | 61.94 | -61.0886 | -0.16937 | -0.013733 | -0.10986 | -0.15564 | -0.09613 | -0.21057 | -0.068665 | 0.059509 | 60.8917 | 61.0886 | 122.7905 | 122.8729 | -0.10986 | 122.818 | 61.0336 | -0.21057 | 122.8729 | -0.10986 | 61.0336 | 122.7905 | 122.818 | -123.056 | -123.0972
354.7656 | 123.1018 | -60.9192 | 62.0224 | -0.21767 | -0.0035162 | -0.0015167 | 0.001993 | 0.062241 | -0.0037277 | 0.067838 | -61.0382 | 62.0132 | -61.084 | -61.1252 | 61.8301 | 0.073242 | 0.13275 | 0.12817 | 61.9812 | -61.0931 | -0.16479 | -0.009155 | -0.11902 | -0.20599 | -0.19226 | -0.17395 | -0.041199 | 0.045776 | 61.0519 | 61.0474 | 122.7493 | 122.9324 | -0.11902 | 122.9004 | 60.9924 | -0.17395 | 122.9324 | -0.11902 | 60.9924 | 122.7493 | 122.9004 | -123.1064 | -123.1155
355.7656 | 123.0743 | -60.9055 | 62.0224 | -0.43892 | -0.0033026 | -0.0036529 | 0.0034884 | 0.062241 | -0.0030869 | 0.069547 | -61.0336 | 62.0316 | -61.0931 | -61.1206 | 61.8347 | 0.073242 | 0.14648 | 0.13733 | 61.9949 | -61.0977 | -0.18768 | 0.009155 | -0.12817 | -0.21515 | -0.18768 | -0.19226 | -0.027466 | 0.05951 | 61.0519 | 61.0428 | 122.7402 | 122.937 | -0.12817 | 122.9004 | 60.9787 | -0.19226 | 122.937 | -0.12817 | 60.9787 | 122.7402 | 122.9004 | -123.1155 | -123.1201
356.7812 | 123.1384 | -60.9741 | 61.9949 | 0.20195 | -0.00073919 | 0.00040586 | 0.0075472 | 0.064805 | -0.0033005 | 0.068693 | -61.0657 | 62.0316 | -61.0977 | -61.1893 | 61.7569 | -0.050354 | 0.018311 | -0.050354 | 61.94 | -61.1389 | -0.1236 | 0.036621 | -0.091553 | -0.21515 | -0.23804 | -0.1648 | -0.054932 | 0.032043 | 60.9924 | 60.9238 | 122.731 | 123.0057 | -0.091553 | 122.9141 | 60.9238 | -0.1648 | 123.0057 | -0.091553 | 60.9238 | 122.731 | 122.9141 | -123.0927 | -123.1338
357.7656 | 123.0972 | -60.9055 | 62.0407 | -0.11848 | -0.0026618 | -0.0017303 | 0.0032748 | 0.064378 | -0.0043685 | 0.068052 | -61.0474 | 62.0636 | -61.0931 | -61.1298 | 61.8073 | 0.059509 | 0.14648 | 0.10986 | 61.972 | -61.1023 | -0.18768 | 0.022889 | -0.14191 | -0.2243 | -0.23346 | -0.19684 | -0.068664 | 0.045777 | 61.0519 | 61.0153 | 122.7127 | 122.9691 | -0.14191 | 122.8775 | 60.965 | -0.19684 | 122.9691 | -0.14191 | 60.965 | 122.7127 | 122.8775 | -123.1338 | -123.143
358.7656 | 123.0927 | -60.9192 | 61.9949 | -0.20241 | -0.0033026 | -0.0055755 | 0.002634 | 0.066087 | -0.0030869 | 0.068265 | -61.0428 | 62.0728 | -61.0977 | -61.116 | 61.8164 | 0.064087 | 0.13733 | 0.10529 | 62.0178 | -61.1023 | -0.17853 | 0.07782 | -0.1236 | -0.19684 | -0.17853 | -0.18311 | 0.022888 | 0.054931 | 61.0565 | 61.0245 | 122.7356 | 122.9919 | -0.1236 | 122.937 | 60.9833 | -0.18311 | 122.9919 | -0.1236 | 60.9833 | 122.7356 | 122.937 | -123.0927 | -123.0972
359.7656 | 123.0927 | -60.878 | 62.0499 | -0.23293 | -0.0033026 | -0.0034393 | 0.0024202 | 0.063523 | -0.0039413 | 0.070615 | -61.0748 | 62.0911 | -61.0657 | -61.1481 | 61.821 | 0.068665 | 0.16022 | 0.10986 | 61.9995 | -61.1389 | -0.18768 | 0.041198 | -0.19684 | -0.27008 | -0.22888 | -0.26093 | -0.050354 | -0.009155 | 61.0382 | 60.9879 | 122.699 | 122.9691 | -0.19684 | 122.8775 | 60.9467 | -0.26093 | 122.9691 | -0.19684 | 60.9467 | 122.699 | 122.8775 | -123.1155 | -123.1888
360.7656 | 123.0881 | -60.9283 | 61.9995 | -0.17952 | -0.0033026 | -0.00087594 | 0.0022066 | 0.065018 | -0.0037277 | 0.069761 | -61.0565 | 62.0728 | -61.0886 | -61.1526 | 61.8484 | 0.22888 | 0.18768 | 0 | 62.0041 | -61.116 | -0.16022 | 0.073242 | -0.12817 | -0.2243 | -0.15106 | -0.18768 | 0.004577 | 0.032043 | 61.116 | 60.9283 | 122.7768 | 123.0011 | -0.12817 | 122.9324 | 61.1572 | -0.18768 | 123.0011 | -0.12817 | 61.1572 | 122.7768 | 122.9324 | -123.0881 | -123.1155
361.7812 | 123.1338 | -60.8917 | 61.9537 | 0.27061 | -0.0024482 | 0.0012605 | 0.0015658 | 0.065018 | -0.0020187 | 0.068479 | -61.0611 | 62.0132 | -61.1069 | -61.1389 | 61.821 | 0.018311 | -0.12817 | 0.064087 | 61.9217 | -61.1298 | -0.21515 | 0.05951 | -0.16937 | -0.24719 | -0.13275 | -0.23804 | -0.032043 | 0.045777 | 60.7636 | 60.9558 | 122.7127 | 122.905 | -0.16937 | 122.8134 | 60.91 | -0.23804 | 122.905 | -0.16937 | 60.91 | 122.7127 | 122.8134 | -123.0606 | -123.0835
362.7656 | 123.1064 | -60.8871 | 62.0178 | -0.11848 | -0.0039434 | -0.0027985 | 0.0030612 | 0.065232 | -0.0024459 | 0.067411 | -61.0428 | 62.1002 | -61.0565 | -61.116 | 61.821 | 0.082397 | 0.13733 | 0.13275 | 62.0041 | -61.1069 | -0.16937 | 0.082398 | -0.15564 | -0.22888 | -0.19684 | -0.21973 | -0.013733 | 0.013733 | 61.0245 | 61.0199 | 122.7081 | 122.9874 | -0.15564 | 122.8912 | 60.9695 | -0.21973 | 122.9874 | -0.15564 | 60.9695 | 122.7081 | 122.8912 | -123.0743 | -123.1247
363.7656 | 123.1201 | -60.8963 | 62.0041 | -0.057449 | -0.0043708 | -0.0032257 | 0.0058382 | 0.066727 | -0.0043685 | 0.069547 | -61.0062 | 62.0636 | -61.0703 | -61.0931 | 61.853 | 0.082397 | 0.054932 | 0.10986 | 62.0087 | -61.1023 | -0.17395 | 0.05951 | -0.10986 | -0.19684 | -0.15106 | -0.20599 | 0.004578 | 0.064086 | 60.9512 | 61.0062 | 122.7493 | 122.9599 | -0.10986 | 122.905 | 60.9787 | -0.20599 | 122.9599 | -0.10986 | 60.9787 | 122.7493 | 122.905 | -123.0743 | -123.1064
364.7656 | 123.1293 | -60.8963 | 61.9949 | -0.057449 | -0.00052559 | -0.0023711 | 0.0051974 | 0.066727 | -0.0013779 | 0.069974 | -60.9924 | 62.0728 | -61.0565 | -61.084 | 61.8439 | 0.09613 | 0.054932 | 0.15564 | 61.9949 | -61.116 | -0.16022 | 0.07782 | -0.096131 | -0.18768 | -0.15106 | -0.21973 | 0 | 0.064087 | 60.9512 | 61.0519 | 122.7402 | 122.9691 | -0.096131 | 122.8912 | 60.9924 | -0.21973 | 122.9691 | -0.096131 | 60.9924 | 122.7402 | 122.8912 | -123.0515 | -123.111
365.7656 | 123.1476 | -60.9192 | 62.0087 | -0.057449 | -0.00073919 | -0.0010895 | 0.0039156 | 0.067582 | -0.0024459 | 0.068479 | -60.997 | 62.0728 | -61.0748 | -61.0977 | 61.8439 | 0.073242 | 0.064087 | 0.13275 | 62.0041 | -61.1252 | -0.15564 | 0.064087 | -0.07782 | -0.17853 | -0.1648 | -0.20599 | -0.004578 | 0.07782 | 60.9833 | 61.0519 | 122.7631 | 122.9919 | -0.07782 | 122.9233 | 60.9924 | -0.20599 | 122.9919 | -0.07782 | 60.9924 | 122.7631 | 122.9233 | -123.0835 | -123.1338
366.7812 | 123.1705 | -60.9009 | 61.9308 | 0.21721 | -0.0035162 | -0.0034393 | -0.0022794 | 0.066727 | -0.00073695 | 0.070615 | -61.0336 | 61.972 | -61.0748 | -61.1252 | 61.8713 | 0.064087 | -0.14648 | 0.09613 | 61.9263 | -61.1069 | -0.17395 | 0.041199 | -0.13275 | -0.2243 | -0.059509 | -0.20599 | -0.004577 | 0.041199 | 60.7544 | 60.997 | 122.7722 | 122.8729 | -0.13275 | 122.8271 | 60.965 | -0.20599 | 122.8729 | -0.13275 | 60.965 | 122.7722 | 122.8271 | -123.0057 | -123.0377
367.7656 | 123.0927 | -60.9055 | 61.9904 | -0.15663 | -0.0033026 | -0.0034393 | 0.0049838 | 0.065446 | -0.0028731 | 0.06912 | -61.0291 | 62.1002 | -61.084 | -61.1252 | 61.8256 | 0.082397 | 0.09613 | 0.13733 | 61.9766 | -61.1343 | -0.17853 | 0.10986 | -0.1236 | -0.21973 | -0.16479 | -0.22888 | -0.013732 | 0.054931 | 61.0016 | 61.0428 | 122.731 | 123.0057 | -0.1236 | 122.8821 | 60.9879 | -0.22888 | 123.0057 | -0.1236 | 60.9879 | 122.731 | 122.8821 | -123.0743 | -123.1247
368.7656 | 123.0972 | -60.878 | 61.9995 | -0.04219 | -0.00138 | 0.0033967 | 0.0032748 | 0.066087 | -0.0035141 | 0.067411 | -61.0016 | 62.0911 | -61.0977 | -61.1069 | 61.8484 | 0.086975 | 0.050354 | 0.13733 | 61.9812 | -61.1481 | -0.21973 | 0.091552 | -0.1236 | -0.22888 | -0.15106 | -0.27008 | -0.018311 | 0.09613 | 60.9283 | 61.0153 | 122.7264 | 122.9691 | -0.1236 | 122.8592 | 60.965 | -0.27008 | 122.9691 | -0.1236 | 60.965 | 122.7264 | 122.8592 | -123.0972 | -123.1476
369.7656 | 123.0972 | -60.9192 | 61.9995 | 0.026474 | -0.0024482 | -0.00044854 | 0.002634 | 0.065659 | -0.00095055 | 0.06912 | -60.9879 | 62.0865 | -61.0748 | -61.1069 | 61.8622 | 0.082397 | 0.041199 | 0.14191 | 62.0087 | -61.1114 | -0.15564 | 0.086975 | -0.068665 | -0.18768 | -0.13733 | -0.19226 | 0.009155 | 0.086975 | 60.9604 | 61.0611 | 122.7814 | 123.0057 | -0.068665 | 122.9279 | 61.0016 | -0.19226 | 123.0057 | -0.068665 | 61.0016 | 122.7814 | 122.9279 | -123.0743 | -123.111
370.7656 | 123.1064 | -60.9238 | 61.9995 | -0.080337 | -0.0018072 | -0.0025847 | 0.0024202 | 0.068223 | -0.0018051 | 0.068479 | -61.0107 | 62.0773 | -61.0657 | -61.1343 | 61.8164 | 0.059509 | 0.041199 | 0.09613 | 61.9766 | -61.1481 | -0.14191 | 0.07782 | -0.086975 | -0.21057 | -0.18311 | -0.2243 | -0.022888 | 0.054932 | 60.965 | 61.0199 | 122.7402 | 123.0011 | -0.086975 | 122.9004 | 60.9833 | -0.2243 | 123.0011 | -0.086975 | 60.9833 | 122.7402 | 122.9004 | -123.0652 | -123.1476
371.7812 | 123.175 | -60.878 | 61.9766 | 0.27061 | -0.0026618 | -0.0055755 | -0.0044156 | 0.064805 | -0.0022323 | 0.068479 | -61.0519 | 62.0224 | -61.0474 | -61.1389 | 61.8347 | 0.041199 | -0.064087 | 0.10529 | 61.94 | -61.1114 | -0.16937 | 0.045776 | -0.17395 | -0.26093 | -0.14191 | -0.23346 | -0.036622 | -0.004578 | 60.8139 | 60.9833 | 122.7127 | 122.9004 | -0.17395 | 122.818 | 60.9192 | -0.23346 | 122.9004 | -0.17395 | 60.9192 | 122.7127 | 122.818 | -123.024 | -123.0881
372.7656 | 123.0972 | -60.9192 | 61.9995 | 0.0035856 | -0.0015936 | 0.00040586 | 0.0024202 | 0.066727 | -0.0022323 | 0.067624 | -61.0016 | 62.0773 | -61.0931 | -61.1435 | 61.8027 | 0.027466 | 0.022888 | 0.086975 | 62.0224 | -61.1481 | -0.17395 | 0.07782 | -0.082398 | -0.2243 | -0.19684 | -0.22888 | 0.022888 | 0.091553 | 60.9421 | 61.0062 | 122.7219 | 122.9965 | -0.082398 | 122.9416 | 60.9467 | -0.22888 | 122.9965 | -0.082398 | 60.9467 | 122.7219 | 122.9416 | -123.0927 | -123.1476
373.7656 | 123.111 | -60.8871 | 62.0087 | 0.0035856 | -0.0024482 | 0.0025421 | 0.0032748 | 0.068436 | -0.0026595 | 0.069974 | -60.9924 | 62.0865 | -61.1023 | -61.0977 | 61.8301 | 0.082397 | 0.041199 | 0.13733 | 62.0041 | -61.1343 | -0.21515 | 0.07782 | -0.10529 | -0.21057 | -0.17853 | -0.24719 | -0.004578 | 0.10986 | 60.9283 | 61.0245 | 122.7173 | 122.9736 | -0.10529 | 122.8912 | 60.9695 | -0.24719 | 122.9736 | -0.10529 | 60.9695 | 122.7173 | 122.8912 | -123.111 | -123.143
374.7656 | 123.1293 | -60.9055 | 61.9949 | -0.087967 | 0.00011541 | 0.0038239 | 0.001993 | 0.066727 | -0.00052335 | 0.069761 | -61.0016 | 62.0865 | -61.0977 | -61.1023 | 61.8393 | 0.086975 | 0.050354 | 0.14648 | 61.9904 | -61.1526 | -0.19226 | 0.091553 | -0.09613 | -0.19684 | -0.15564 | -0.24719 | -0.004578 | 0.09613 | 60.9558 | 61.0519 | 122.7448 | 122.9919 | -0.09613 | 122.8958 | 60.9924 | -0.24719 | 122.9919 | -0.09613 | 60.9924 | 122.7448 | 122.8958 | -123.0927 | -123.1476
375.7656 | 123.0881 | -60.9055 | 61.9904 | -0.072708 | -0.0020208 | -0.00023494 | 0.0039156 | 0.066727 | -0.00073695 | 0.067624 | -61.0062 | 62.0636 | -61.0611 | -61.116 | 61.8118 | 0.050354 | 0.036621 | 0.091553 | 62.0087 | -61.1481 | -0.15564 | 0.073243 | -0.10071 | -0.21057 | -0.17853 | -0.24261 | 0.018311 | 0.054931 | 60.9421 | 60.997 | 122.7173 | 122.9691 | -0.10071 | 122.9141 | 60.9558 | -0.24261 | 122.9691 | -0.10071 | 60.9558 | 122.7173 | 122.9141 | -123.0515 | -123.1384
376.7656 | 123.0515 | -60.9329 | 61.9812 | 0.1104 | -0.0026618 | -0.0010895 | 0.0022066 | 0.066727 | -0.0028731 | 0.068265 | -61.0519 | 62.0956 | -61.0886 | -61.1893 | 61.7661 | -0.032043 | 0.036621 | 0.018311 | 62.0041 | -61.1526 | -0.15564 | 0.11444 | -0.11902 | -0.25635 | -0.21515 | -0.21973 | 0.022888 | 0.036621 | 60.9695 | 60.9512 | 122.699 | 123.0286 | -0.11902 | 122.937 | 60.9009 | -0.21973 | 123.0286 | -0.11902 | 60.9009 | 122.699 | 122.937 | -123.0698 | -123.1338
377.7656 | 123.0743 | -60.9375 | 61.9949 | 0.12566 | -0.00031179 | 0.0025421 | 0.0024202 | 0.066727 | -0.00052335 | 0.071042 | -61.0565 | 62.1002 | -61.084 | -61.1801 | 61.7798 | -0.004578 | 0.036621 | 0.022888 | 61.9949 | -61.1526 | -0.14648 | 0.10529 | -0.11902 | -0.24262 | -0.21515 | -0.21515 | 0 | 0.027465 | 60.9741 | 60.9604 | 122.7173 | 123.0377 | -0.11902 | 122.9324 | 60.9329 | -0.21515 | 123.0377 | -0.11902 | 60.9329 | 122.7173 | 122.9324 | -123.0789 | -123.1476
378.7656 | 123.1018 | -60.9009 | 62.0041 | 0.064621 | 0.00032901 | 0.0016877 | 0.0041292 | 0.065659 | -0.00030975 | 0.069974 | -61.0519 | 62.0956 | -61.0886 | -61.1755 | 61.7569 | -0.009155 | 0.050354 | 0.022888 | 61.9995 | -61.1526 | -0.18768 | 0.091553 | -0.15106 | -0.27466 | -0.24719 | -0.25177 | -0.004577 | 0.036621 | 60.9512 | 60.9238 | 122.6578 | 122.9965 | -0.15106 | 122.9004 | 60.8917 | -0.25177 | 122.9965 | -0.15106 | 60.8917 | 122.6578 | 122.9004 | -123.0927 | -123.1567
379.7656 | 123.0835 | -60.9055 | 61.9995 | 0.10277 | -0.00073919 | -0.00066214 | 0.0013522 | 0.068223 | -0.0018051 | 0.069547 | -61.0336 | 62.0819 | -61.084 | -61.1664 | 61.7798 | -0.009155 | 0.041199 | 0.036621 | 62.0041 | -61.1572 | -0.17853 | 0.082397 | -0.12817 | -0.26093 | -0.21973 | -0.25177 | 0.004577 | 0.050354 | 60.9467 | 60.9421 | 122.6852 | 122.9874 | -0.12817 | 122.9095 | 60.8963 | -0.25177 | 122.9874 | -0.12817 | 60.8963 | 122.6852 | 122.9095 | -123.0835 | -123.1567
380.7656 | 123.1567 | -60.9055 | 62.0361 | -0.0040434 | -9.819e-05 | -0.0019439 | 0.0017794 | 0.066941 | -0.0035141 | 0.070188 | -61.0062 | 62.0865 | -61.0886 | -61.1252 | 61.8164 | 0.059509 | 0.036621 | 0.13275 | 61.9904 | -61.1801 | -0.18311 | 0.050354 | -0.10071 | -0.21973 | -0.21973 | -0.27466 | -0.045777 | 0.082397 | 60.9421 | 61.0382 | 122.7219 | 122.9919 | -0.10071 | 122.8958 | 60.965 | -0.27466 | 122.9919 | -0.10071 | 60.965 | 122.7219 | 122.8958 | -123.1247 | -123.2162
381.7656 | 123.1018 | -60.9009 | 62.0224 | -0.019302 | -0.00073919 | 0.0012605 | 0.0041292 | 0.065018 | -0.0026595 | 0.069974 | -60.997 | 62.0819 | -61.0519 | -61.1069 | 61.7981 | 0.07782 | 0.027466 | 0.11902 | 62.0224 | -61.1481 | -0.15106 | 0.059509 | -0.09613 | -0.20599 | -0.2243 | -0.24719 | 0 | 0.054932 | 60.9283 | 61.0199 | 122.699 | 122.9828 | -0.09613 | 122.9233 | 60.9787 | -0.24719 | 122.9828 | -0.09613 | 60.9787 | 122.699 | 122.9233 | -123.0743 | -123.1705
382.7656 | 123.0652 | -60.9283 | 61.9995 | 0.064621 | -9.819e-05 | 0.0016877 | 0.0034884 | 0.065659 | -0.0022323 | 0.069974 | -61.0382 | 62.0956 | -61.0931 | -61.171 | 61.7889 | 0.004578 | 0.032043 | 0.064087 | 61.9995 | -61.171 | -0.16479 | 0.09613 | -0.10986 | -0.24261 | -0.21057 | -0.24261 | 0 | 0.054932 | 60.9604 | 60.9924 | 122.7173 | 123.024 | -0.10986 | 122.9279 | 60.9329 | -0.24261 | 123.024 | -0.10986 | 60.9329 | 122.7173 | 122.9279 | -123.0927 | -123.1705
383.7656 | 123.0835 | -60.9283 | 62.0132 | 0.018845 | -0.00031179 | -0.0017303 | 0.00071144 | 0.069077 | -0.0045821 | 0.069547 | -61.0245 | 62.0682 | -61.0886 | -61.1618 | 61.7935 | 0.022888 | 0.036621 | 0.064087 | 62.0132 | -61.1526 | -0.16022 | 0.054931 | -0.09613 | -0.23346 | -0.21973 | -0.2243 | 0 | 0.064087 | 60.965 | 60.9924 | 122.7219 | 122.9965 | -0.09613 | 122.9416 | 60.9512 | -0.2243 | 122.9965 | -0.09613 | 60.9512 | 122.7219 | 122.9416 | -123.1018 | -123.1659
384.7656 | 123.0835 | -60.9329 | 61.9904 | 0.14092 | -0.0041572 | 0.00019226 | 0.0011386 | 0.066941 | -0.0028731 | 0.071683 | -61.0703 | 62.1048 | -61.0748 | -61.1984 | 61.7477 | -0.045776 | 0.045776 | -0.018311 | 62.0178 | -61.1938 | -0.14191 | 0.11444 | -0.13733 | -0.2655 | -0.24261 | -0.26093 | 0.027466 | 0.004578 | 60.9787 | 60.9146 | 122.6807 | 123.0377 | -0.13733 | 122.9507 | 60.8871 | -0.26093 | 123.0377 | -0.13733 | 60.8871 | 122.6807 | 122.9507 | -123.0652 | -123.1842
385.7656 | 123.0789 | -60.9238 | 61.9766 | 0.12566 | -0.00138 | -0.0036529 | 0.0015658 | 0.066514 | -0.0024459 | 0.067838 | -61.0474 | 62.0911 | -61.1023 | -61.203 | 61.7386 | -0.059509 | 0.045776 | 0.004578 | 62.0316 | -61.1847 | -0.17853 | 0.11444 | -0.1236 | -0.27924 | -0.23804 | -0.26093 | 0.054931 | 0.054932 | 60.9695 | 60.9283 | 122.6624 | 123.0148 | -0.1236 | 122.9553 | 60.8643 | -0.26093 | 123.0148 | -0.1236 | 60.8643 | 122.6624 | 122.9553 | -123.0789 | -123.1613
386.7656 | 123.0606 | -60.9375 | 62.0132 | 0.072251 | -0.0026618 | -0.0019439 | 0.0022066 | 0.067582 | -0.0035141 | 0.068052 | -61.0657 | 62.0819 | -61.0748 | -61.1938 | 61.7523 | -0.022888 | 0.045776 | 0.013733 | 62.0087 | -61.1618 | -0.13733 | 0.068664 | -0.12817 | -0.25635 | -0.26093 | -0.2243 | -0.004578 | 0.009155 | 60.9833 | 60.9512 | 122.6898 | 123.0194 | -0.12817 | 122.9462 | 60.9146 | -0.2243 | 123.0194 | -0.12817 | 60.9146 | 122.6898 | 122.9462 | -123.0881 | -123.175
387.7656 | 123.0515 | -60.9192 | 62.0041 | 0.095139 | -0.0011664 | -0.0015167 | 0.0013522 | 0.066941 | -0.0035141 | 0.068479 | -61.0519 | 62.0911 | -61.1069 | -61.1893 | 61.7752 | -0.013733 | 0.041199 | 0.027466 | 62.0087 | -61.1801 | -0.18768 | 0.086975 | -0.13275 | -0.27008 | -0.22888 | -0.26093 | 0.004578 | 0.054932 | 60.9604 | 60.9467 | 122.6944 | 123.0103 | -0.13275 | 122.9279 | 60.9055 | -0.26093 | 123.0103 | -0.13275 | 60.9055 | 122.6944 | 122.9279 | -123.111 | -123.1842
388.7656 | 123.1018 | -60.8871 | 62.027 | 0.24773 | -0.0022346 | 0.00040586 | 0.0017794 | 0.06865 | -0.0026595 | 0.06912 | -60.9879 | 62.0728 | -61.0886 | -61.1252 | 61.8164 | 0.054932 | 0.036621 | 0.086975 | 62.0132 | -61.1618 | -0.20142 | 0.045776 | -0.10071 | -0.23804 | -0.21057 | -0.27466 | -0.013733 | 0.10071 | 60.9238 | 60.9741 | 122.7036 | 122.9599 | -0.10071 | 122.9004 | 60.9421 | -0.27466 | 122.9599 | -0.10071 | 60.9421 | 122.7036 | 122.9004 | -123.1155 | -123.1888
389.7656 | 123.0652 | -60.91 | 62.0224 | 0.1104 | -0.00073919 | -0.0045075 | 0.0017794 | 0.066727 | -0.0028731 | 0.068265 | -61.0428 | 62.0728 | -61.0886 | -61.171 | 61.7798 | -0.004578 | 0.036621 | 0.036621 | 62.0544 | -61.1664 | -0.17853 | 0.050354 | -0.13275 | -0.26093 | -0.24262 | -0.25635 | 0.032043 | 0.045776 | 60.9467 | 60.9467 | 122.6898 | 122.9828 | -0.13275 | 122.9645 | 60.9055 | -0.25635 | 122.9828 | -0.13275 | 60.9055 | 122.6898 | 122.9645 | -123.111 | -123.1888
390.7656 | 123.0835 | -60.9238 | 62.0132 | 0.20195 | -0.0026618 | -0.00044854 | 0.0011386 | 0.068223 | -0.00052335 | 0.068906 | -61.0886 | 62.0911 | -61.1252 | -61.2213 | 61.734 | -0.050354 | 0.004578 | -0.013733 | 62.0087 | -61.1801 | -0.20142 | 0.077819 | -0.1648 | -0.29755 | -0.27924 | -0.25635 | -0.004578 | 0.036621 | 60.9283 | 60.91 | 122.6578 | 123.0148 | -0.1648 | 122.9324 | 60.8734 | -0.25635 | 123.0148 | -0.1648 | 60.8734 | 122.6578 | 122.9324 | -123.1384 | -123.1934
391.7656 | 123.056 | -60.9329 | 61.9904 | 0.20195 | -0.0022346 | 0.0010467 | 0.001993 | 0.067582 | -0.0033005 | 0.069761 | -61.0794 | 62.1094 | -61.116 | -61.2259 | 61.7477 | -0.054932 | 0.064087 | -0.036621 | 62.0178 | -61.1755 | -0.18311 | 0.11902 | -0.14649 | -0.29297 | -0.24261 | -0.24262 | 0.027466 | 0.036621 | 60.997 | 60.8963 | 122.6807 | 123.0423 | -0.14649 | 122.9507 | 60.878 | -0.24262 | 123.0423 | -0.14649 | 60.878 | 122.6807 | 122.9507 | -123.1064 | -123.1659
392.7656 | 123.0743 | -60.9329 | 62.0087 | 0.14092 | -0.0018072 | -0.0015167 | 0.0045566 | 0.066087 | -0.0026595 | 0.070402 | -61.084 | 62.0773 | -61.1252 | -61.2259 | 61.7432 | -0.054932 | 0.041199 | -0.027466 | 62.0224 | -61.1984 | -0.19226 | 0.068665 | -0.15106 | -0.29297 | -0.2655 | -0.2655 | 0.013733 | 0.041199 | 60.9741 | 60.9055 | 122.6761 | 123.0103 | -0.15106 | 122.9553 | 60.878 | -0.2655 | 123.0103 | -0.15106 | 60.878 | 122.6761 | 122.9553 | -123.1338 | -123.2071
393.7656 | 123.0515 | -60.9055 | 61.9858 | 0.1104 | -0.0028754 | -0.00066214 | 0.0030612 | 0.069504 | -0.0030869 | 0.069761 | -61.0748 | 62.0773 | -61.1069 | -61.1893 | 61.7477 | -0.050354 | 0.036621 | 0.009155 | 61.9949 | -61.1572 | -0.20142 | 0.091553 | -0.16937 | -0.28381 | -0.23804 | -0.25177 | 0.009155 | 0.032044 | 60.9421 | 60.9146 | 122.6532 | 122.9828 | -0.16937 | 122.9004 | 60.8551 | -0.25177 | 122.9828 | -0.16937 | 60.8551 | 122.6532 | 122.9004 | -123.0927 | -123.143
394.7656 | 123.111 | -60.9238 | 61.9949 | 0.0035856 | -0.0022346 | -0.0023711 | 0.0032748 | 0.068223 | -0.0018051 | 0.068052 | -61.0107 | 62.059 | -61.0931 | -61.1435 | 61.8164 | 0.036621 | 0.036621 | 0.082397 | 62.0041 | -61.1755 | -0.16937 | 0.064087 | -0.086975 | -0.21973 | -0.17853 | -0.25177 | 0.009155 | 0.082398 | 60.9604 | 61.0062 | 122.7402 | 122.9828 | -0.086975 | 122.9279 | 60.9604 | -0.25177 | 122.9828 | -0.086975 | 60.9604 | 122.7402 | 122.9279 | -123.0881 | -123.1705
395.7656 | 123.0743 | -60.9375 | 62.0178 | 0.072251 | -0.0022346 | 0.00019226 | 0.0030612 | 0.069504 | -0.0018051 | 0.071256 | -61.0519 | 62.1002 | -61.084 | -61.1984 | 61.7661 | -0.036621 | 0.045776 | 0.013733 | 62.027 | -61.1801 | -0.14648 | 0.082398 | -0.11444 | -0.26093 | -0.25177 | -0.24262 | 0.009156 | 0.032043 | 60.9833 | 60.9512 | 122.7036 | 123.0377 | -0.11444 | 122.9645 | 60.9009 | -0.24262 | 123.0377 | -0.11444 | 60.9009 | 122.7036 | 122.9645 | -123.1018 | -123.1979
396.7656 | 123.0789 | -60.9192 | 61.9949 | 0.087509 | -0.0015936 | -2.1336e-05 | 0.0030612 | 0.068223 | 0.00097205 | 0.06912 | -61.0428 | 62.0911 | -61.1069 | -61.1801 | 61.7798 | -0.027466 | 0.036621 | 0.027466 | 62.0132 | -61.1664 | -0.18768 | 0.09613 | -0.1236 | -0.26093 | -0.21515 | -0.24719 | 0.018311 | 0.064087 | 60.9558 | 60.9467 | 122.699 | 123.0103 | -0.1236 | 122.9324 | 60.8917 | -0.24719 | 123.0103 | -0.1236 | 60.8917 | 122.699 | 122.9324 | -123.1018 | -123.1613
397.7656 | 123.0743 | -60.9467 | 61.9904 | 0.20195 | -0.0022346 | -0.0019439 | 0.0022066 | 0.067795 | -0.0033005 | 0.068906 | -61.0794 | 62.0636 | -61.1343 | -61.2305 | 61.7111 | -0.041199 | 0.022888 | -0.013733 | 62.0316 | -61.1755 | -0.18768 | 0.073243 | -0.13275 | -0.28381 | -0.27923 | -0.22888 | 0.041199 | 0.054931 | 60.9695 | 60.9329 | 122.6578 | 123.0103 | -0.13275 | 122.9782 | 60.9055 | -0.22888 | 123.0103 | -0.13275 | 60.9055 | 122.6578 | 122.9782 | -123.1247 | -123.1659
398.7656 | 123.0331 | -60.9283 | 61.9995 | 0.12566 | -0.00138 | -0.00023494 | 0.0041292 | 0.065873 | -0.0052231 | 0.067838 | -61.0748 | 62.0819 | -61.1206 | -61.2305 | 61.734 | -0.064087 | 0.050354 | -0.032043 | 61.9858 | -61.2076 | -0.19226 | 0.082397 | -0.14648 | -0.30212 | -0.2655 | -0.27924 | -0.013733 | 0.045776 | 60.9787 | 60.8963 | 122.6624 | 123.0103 | -0.14648 | 122.9141 | 60.8643 | -0.27924 | 123.0103 | -0.14648 | 60.8643 | 122.6624 | 122.9141 | -123.1201 | -123.2071
399.7656 | 123.056 | -60.9467 | 61.9949 | 0.041733 | -0.003089 | -0.0015167 | 0.0049838 | 0.067368 | -0.0018051 | 0.069974 | -61.0794 | 62.0728 | -61.1069 | -61.2122 | 61.7386 | -0.059509 | 0.041199 | -0.013733 | 62.0316 | -61.1801 | -0.16022 | 0.07782 | -0.13275 | -0.2655 | -0.25635 | -0.23346 | 0.036621 | 0.027466 | 60.9879 | 60.9329 | 122.6852 | 123.0194 | -0.13275 | 122.9782 | 60.8871 | -0.23346 | 123.0194 | -0.13275 | 60.8871 | 122.6852 | 122.9782 | -123.1018 | -123.175
400.7656 | 123.0698 | -60.9192 | 62.0132 | 0.1104 | -0.0011664 | -0.0034393 | 0.0013522 | 0.066514 | -0.00095055 | 0.070615 | -61.0703 | 62.0819 | -61.1023 | -61.2122 | 61.7477 | -0.027466 | 0.041199 | -0.009155 | 62.0132 | -61.1755 | -0.18311 | 0.068664 | -0.15106 | -0.29297 | -0.2655 | -0.25635 | 0 | 0.032044 | 60.9604 | 60.91 | 122.6669 | 123.0011 | -0.15106 | 122.9324 | 60.8917 | -0.25635 | 123.0011 | -0.15106 | 60.8917 | 122.6669 | 122.9324 | -123.1155 | -123.1888
401.7656 | 123.1064 | -60.9375 | 62.0041 | -0.034561 | -0.00052559 | -2.1336e-05 | 0.001993 | 0.068436 | -0.0052231 | 0.071256 | -61.0016 | 62.0773 | -61.0794 | -61.1389 | 61.8073 | 0.041199 | 0.027466 | 0.091553 | 62.0132 | -61.1572 | -0.14191 | 0.073243 | -0.064087 | -0.20142 | -0.19684 | -0.21973 | 0.009156 | 0.07782 | 60.965 | 61.0291 | 122.7448 | 123.0148 | -0.064087 | 122.9507 | 60.9787 | -0.21973 | 123.0148 | -0.064087 | 60.9787 | 122.7448 | 122.9507 | -123.0835 | -123.1613
402.7656 | 123.1155 | -60.8917 | 62.0087 | 0.018845 | -0.00095279 | -0.0021575 | 0.0022066 | 0.066514 | -0.0035141 | 0.069761 | -61.0199 | 62.0773 | -61.084 | -61.1252 | 61.8393 | 0.032043 | 0.027466 | 0.10071 | 62.0041 | -61.1755 | -0.19226 | 0.068665 | -0.12817 | -0.23346 | -0.16937 | -0.28381 | -0.004578 | 0.064087 | 60.9192 | 60.9924 | 122.731 | 122.9691 | -0.12817 | 122.8958 | 60.9238 | -0.28381 | 122.9691 | -0.12817 | 60.9238 | 122.731 | 122.8958 | -123.0927 | -123.1842
403.7656 | 123.0881 | -60.9283 | 61.9949 | 0.07988 | -0.0035162 | -0.0019439 | 0.0028476 | 0.066941 | -0.0026595 | 0.068906 | -61.0245 | 62.0911 | -61.1069 | -61.1664 | 61.7752 | -0.022888 | 0.018311 | 0.045776 | 62.0132 | -61.1847 | -0.17853 | 0.09613 | -0.09613 | -0.23804 | -0.21973 | -0.25635 | 0.018311 | 0.082398 | 60.9467 | 60.9741 | 122.7036 | 123.0194 | -0.09613 | 122.9416 | 60.9055 | -0.25635 | 123.0194 | -0.09613 | 60.9055 | 122.7036 | 122.9416 | -123.1018 | -123.1796
404.7656 | 123.0515 | -60.9283 | 61.9812 | 0.20958 | -0.0020208 | -0.00087594 | 0.002634 | 0.066727 | -0.0020187 | 0.069547 | -61.0794 | 62.0911 | -61.1343 | -61.2259 | 61.734 | -0.059509 | 0.032043 | -0.032043 | 62.0087 | -61.203 | -0.20599 | 0.10986 | -0.15106 | -0.29755 | -0.24719 | -0.27466 | 0.027466 | 0.054931 | 60.9604 | 60.8963 | 122.6624 | 123.0194 | -0.15106 | 122.937 | 60.8688 | -0.27466 | 123.0194 | -0.15106 | 60.8688 | 122.6624 | 122.937 | -123.1155 | -123.1842
405.7656 | 123.056 | -60.9375 | 62.0087 | 0.12566 | -0.00052559 | -0.0027985 | 0.0024202 | 0.067582 | 0.00011745 | 0.068693 | -61.0794 | 62.0682 | -61.1114 | -61.2259 | 61.7615 | -0.036621 | 0.032043 | -0.027466 | 61.9949 | -61.1984 | -0.17395 | 0.059509 | -0.14191 | -0.28839 | -0.24719 | -0.26093 | -0.013733 | 0.032043 | 60.9695 | 60.91 | 122.699 | 123.0057 | -0.14191 | 122.9324 | 60.9009 | -0.26093 | 123.0057 | -0.14191 | 60.9009 | 122.699 | 122.9324 | -123.1201 | -123.2071
406.7656 | 123.0835 | -60.9283 | 62.0132 | 0.11803 | -0.0011664 | 0.0033967 | 0.0024202 | 0.068009 | -0.00095055 | 0.072111 | -61.0703 | 62.0956 | -61.0886 | -61.2076 | 61.7523 | -0.045776 | 0.032043 | -0.013733 | 62.0132 | -61.1755 | -0.16022 | 0.082397 | -0.14191 | -0.27924 | -0.26093 | -0.24719 | 0 | 0.018311 | 60.9604 | 60.9146 | 122.6807 | 123.024 | -0.14191 | 122.9416 | 60.8826 | -0.24719 | 123.024 | -0.14191 | 60.8826 | 122.6807 | 122.9416 | -123.1018 | -123.1888
407.7656 | 123.0515 | -60.9283 | 61.9949 | 0.12566 | -0.0026618 | -0.0038665 | 0.003702 | 0.066514 | -9.6146e-05 | 0.067838 | -61.0611 | 62.0956 | -61.0886 | -61.1847 | 61.7432 | -0.045776 | 0.041199 | 0.013733 | 61.9995 | -61.1755 | -0.16022 | 0.10071 | -0.13275 | -0.25635 | -0.25177 | -0.24719 | 0.004578 | 0.027466 | 60.9695 | 60.9421 | 122.6715 | 123.024 | -0.13275 | 122.9279 | 60.8826 | -0.24719 | 123.024 | -0.13275 | 60.8826 | 122.6715 | 122.9279 | -123.0835 | -123.1705
408.7656 | 123.1018 | -60.9192 | 62.0087 | -0.0040434 | -0.00031179 | 0.0019013 | 0.0015658 | 0.067155 | -0.00095055 | 0.070188 | -61.0107 | 62.0682 | -61.0794 | -61.1343 | 61.8027 | 0.036621 | 0.041199 | 0.07782 | 62.0087 | -61.1572 | -0.16022 | 0.059509 | -0.091553 | -0.21515 | -0.20599 | -0.23804 | 0 | 0.068665 | 60.9604 | 60.997 | 122.7219 | 122.9874 | -0.091553 | 122.9279 | 60.9558 | -0.23804 | 122.9874 | -0.091553 | 60.9558 | 122.7219 | 122.9279 | -123.0881 | -123.1659
409.7656 | 123.1018 | -60.9375 | 62.0132 | 0.064621 | -0.0018072 | -0.0021575 | 0.0039156 | 0.068009 | -0.0043685 | 0.06912 | -61.0382 | 62.0956 | -61.084 | -61.1893 | 61.7661 | -0.018311 | 0.054932 | 0.018311 | 62.0407 | -61.1572 | -0.14648 | 0.082397 | -0.10071 | -0.25177 | -0.24719 | -0.21973 | 0.027465 | 0.045776 | 60.9924 | 60.9558 | 122.7036 | 123.0331 | -0.10071 | 122.9782 | 60.9192 | -0.21973 | 123.0331 | -0.10071 | 60.9192 | 122.7036 | 122.9782 | -123.0972 | -123.1705
410.7656 | 123.0698 | -60.965 | 62.0224 | 0.14092 | -0.0015936 | 0.00061946 | 0.0030612 | 0.066941 | -0.0024459 | 0.071042 | -61.0428 | 62.1094 | -61.1069 | -61.1893 | 61.7706 | -0.027466 | 0.045776 | 0.027466 | 62.0178 | -61.171 | -0.14191 | 0.086975 | -0.07782 | -0.2243 | -0.25177 | -0.20599 | -0.004578 | 0.064087 | 61.0107 | 60.9924 | 122.7356 | 123.0743 | -0.07782 | 122.9828 | 60.9375 | -0.20599 | 123.0743 | -0.07782 | 60.9375 | 122.7356 | 122.9828 | -123.1293 | -123.1934
411.7656 | 123.0743 | -60.9146 | 61.9812 | 0.14092 | -0.00031179 | 0.0010467 | 0.00071144 | 0.068223 | -0.0011643 | 0.069333 | -61.0931 | 62.0865 | -61.1206 | -61.2213 | 61.7432 | -0.041199 | 0.013733 | -0.022888 | 62.0041 | -61.171 | -0.20599 | 0.10529 | -0.17853 | -0.3067 | -0.23804 | -0.25635 | 0.022888 | 0.027465 | 60.9283 | 60.8917 | 122.6578 | 123.0011 | -0.17853 | 122.9187 | 60.8734 | -0.25635 | 123.0011 | -0.17853 | 60.8734 | 122.6578 | 122.9187 | -123.1018 | -123.1522
412.7656 | 123.0743 | -60.9329 | 61.972 | 0.10277 | -0.00095279 | -0.0060027 | 0.0030612 | 0.065873 | -0.00095055 | 0.070402 | -61.0703 | 62.0819 | -61.1069 | -61.2122 | 61.7477 | -0.045776 | 0.009155 | -0.018311 | 61.9949 | -61.1847 | -0.17395 | 0.10986 | -0.13733 | -0.27924 | -0.2243 | -0.25177 | 0.022888 | 0.036622 | 60.9421 | 60.9146 | 122.6807 | 123.0148 | -0.13733 | 122.9279 | 60.8871 | -0.25177 | 123.0148 | -0.13733 | 60.8871 | 122.6807 | 122.9279 | -123.0789 | -123.1567
413.7656 | 123.0927 | -60.9238 | 62.0041 | 0.13329 | -0.0018072 | -0.0023711 | 0.0028476 | 0.067795 | -0.0011643 | 0.069547 | -61.1069 | 62.0636 | -61.0931 | -61.2305 | 61.7249 | -0.036621 | 0.032043 | -0.022888 | 62.0361 | -61.171 | -0.16937 | 0.05951 | -0.18311 | -0.3067 | -0.27923 | -0.24719 | 0.032044 | -0.013733 | 60.9558 | 60.9009 | 122.6486 | 122.9874 | -0.18311 | 122.9599 | 60.8871 | -0.24719 | 122.9874 | -0.18311 | 60.8871 | 122.6486 | 122.9599 | -123.0972 | -123.175
414.7656 | 123.0881 | -60.9375 | 61.9812 | 0.19432 | -0.0015936 | -0.0010895 | 0.0013522 | 0.067368 | -0.0020187 | 0.070402 | -61.1023 | 62.0819 | -61.1206 | -61.2213 | 61.734 | -0.041199 | 0.018311 | -0.018311 | 62.0087 | -61.1938 | -0.1831 | 0.10071 | -0.16479 | -0.28381 | -0.24719 | -0.25635 | 0.027466 | 0.01831 | 60.9558 | 60.9192 | 122.6715 | 123.0194 | -0.16479 | 122.9462 | 60.8963 | -0.25635 | 123.0194 | -0.16479 | 60.8963 | 122.6715 | 122.9462 | -123.1018 | -123.175
415.7656 | 123.0972 | -60.9329 | 62.0132 | 0.10277 | -0.0024482 | -0.00087594 | 0.0032748 | 0.067368 | -9.6146e-05 | 0.068265 | -61.0245 | 62.0728 | -61.1114 | -61.1618 | 61.7752 | 0.004578 | 0.032043 | 0.036621 | 62.0544 | -61.1801 | -0.17853 | 0.059509 | -0.091553 | -0.22888 | -0.23804 | -0.24719 | 0.041198 | 0.086975 | 60.965 | 60.9695 | 122.7081 | 123.0057 | -0.091553 | 122.9874 | 60.9375 | -0.24719 | 123.0057 | -0.091553 | 60.9375 | 122.7081 | 122.9874 | -123.1247 | -123.1934
416.7656 | 123.0698 | -60.9421 | 62.0132 | 0.17906 | -0.0050116 | 0.0010467 | 0.001993 | 0.067155 | -0.0013779 | 0.068906 | -61.0977 | 62.0636 | -61.0977 | -61.2396 | 61.734 | -0.054932 | 0.027466 | -0.018311 | 62.0132 | -61.1847 | -0.15564 | 0.050354 | -0.15564 | -0.29755 | -0.27924 | -0.24261 | 0 | 0 | 60.9695 | 60.9238 | 122.6761 | 123.0057 | -0.15564 | 122.9553 | 60.8871 | -0.24261 | 123.0057 | -0.15564 | 60.8871 | 122.6761 | 122.9553 | -123.111 | -123.1979
417.7656 | 123.0469 | -60.9283 | 61.9995 | 0.14092 | -0.00073919 | -0.0042937 | 0.0034884 | 0.066941 | -0.0011643 | 0.068693 | -61.0886 | 62.1048 | -61.1114 | -61.235 | 61.7157 | -0.054932 | 0.013733 | -0.013733 | 61.9949 | -61.1755 | -0.1831 | 0.10528 | -0.16022 | -0.3067 | -0.28381 | -0.24719 | -0.004578 | 0.022888 | 60.9421 | 60.9146 | 122.644 | 123.0331 | -0.16022 | 122.9233 | 60.8734 | -0.24719 | 123.0331 | -0.16022 | 60.8734 | 122.644 | 122.9233 | -123.111 | -123.175
418.7656 | 123.0927 | -60.9283 | 61.9766 | 0.30876 | -0.0015936 | -0.00087594 | 0.003702 | 0.067368 | -0.00095055 | 0.068906 | -61.0428 | 62.0728 | -61.0931 | -61.2167 | 61.7615 | -0.050354 | -0.004578 | -0.009155 | 61.9949 | -61.1801 | -0.16479 | 0.09613 | -0.11444 | -0.28839 | -0.21515 | -0.25177 | 0.01831 | 0.050354 | 60.9238 | 60.9192 | 122.6898 | 123.0011 | -0.11444 | 122.9233 | 60.878 | -0.25177 | 123.0011 | -0.11444 | 60.878 | 122.6898 | 122.9233 | -123.0698 | -123.1567
419.7656 | 123.0835 | -60.9146 | 62.0041 | -1.6215 | -0.00052559 | -2.1336e-05 | 0.00092504 | 0.066727 | -0.0013779 | 0.069547 | -61.0565 | 62.0773 | -61.0977 | -61.2305 | 61.7386 | -0.045776 | 0 | -0.009155 | 61.9949 | -61.203 | -0.18311 | 0.073243 | -0.14191 | -0.31586 | -0.2655 | -0.28839 | -0.009155 | 0.041198 | 60.9146 | 60.9055 | 122.6532 | 122.9919 | -0.14191 | 122.9095 | 60.8688 | -0.28839 | 122.9919 | -0.14191 | 60.8688 | 122.6532 | 122.9095 | -123.1018 | -123.2071
420.7656 | 123.1155 | -60.9238 | 61.9812 | -0.26344 | -0.0026618 | -0.0027985 | 0.0015658 | 0.064805 | -0.0013779 | 0.070829 | -61.0565 | 62.0911 | -61.0977 | -61.2167 | 61.7386 | -0.041199 | -0.009155 | -0.013733 | 61.9949 | -61.1664 | -0.17395 | 0.10986 | -0.13275 | -0.29297 | -0.24262 | -0.24262 | 0.013733 | 0.041198 | 60.9146 | 60.91 | 122.6624 | 123.0148 | -0.13275 | 122.9187 | 60.8826 | -0.24262 | 123.0148 | -0.13275 | 60.8826 | 122.6624 | 122.9187 | -123.0789 | -123.1476
421.7656 | 123.0743 | -60.9192 | 61.9675 | 0.12566 | -0.00138 | 0.0036103 | 0.0028476 | 0.0663 | -0.0018051 | 0.069333 | -61.0886 | 62.0682 | -61.1206 | -61.2259 | 61.7432 | -0.068665 | 0.022888 | -0.013733 | 62.027 | -61.1618 | -0.20142 | 0.10071 | -0.16937 | -0.3067 | -0.2243 | -0.24261 | 0.05951 | 0.032043 | 60.9421 | 60.9055 | 122.6624 | 122.9874 | -0.16937 | 122.9462 | 60.8505 | -0.24261 | 122.9874 | -0.16937 | 60.8505 | 122.6624 | 122.9462 | -123.0881 | -123.1293
422.7656 | 123.0789 | -60.9283 | 62.0041 | 0.1638 | -0.0024482 | -0.0034393 | 0.0028476 | 0.0663 | -9.6146e-05 | 0.06912 | -61.0977 | 62.0865 | -61.116 | -61.2259 | 61.7294 | -0.073242 | 0.022888 | -0.022888 | 61.9995 | -61.171 | -0.18768 | 0.082398 | -0.16937 | -0.29755 | -0.27466 | -0.24261 | -0.004577 | 0.018311 | 60.9512 | 60.9055 | 122.6578 | 123.0148 | -0.16937 | 122.9279 | 60.8551 | -0.24261 | 123.0148 | -0.16937 | 60.8551 | 122.6578 | 122.9279 | -123.1201 | -123.175
423.7812 | 123.175 | -60.9055 | 61.9492 | 0.27824 | -0.0054388 | -0.0017303 | -0.0050566 | 0.0663 | -0.0011643 | 0.07147 | -61.0291 | 61.9583 | -61.0931 | -61.1114 | 61.8576 | 0.041199 | -0.16022 | 0.10986 | 61.9629 | -61.1069 | -0.18768 | 0.009155 | -0.1236 | -0.20599 | -0.091553 | -0.20142 | 0.013733 | 0.064087 | 60.7452 | 61.0153 | 122.7631 | 122.8638 | -0.1236 | 122.8683 | 60.9467 | -0.20142 | 122.8638 | -0.1236 | 60.9467 | 122.7631 | 122.8683 | -123.0423 | -123.056
424.7656 | 123.1522 | -60.9055 | 61.9766 | 0.25536 | -0.0011664 | -0.00066214 | 0.001993 | 0.066941 | -0.0037277 | 0.068906 | -61.0428 | 62.0453 | -61.1023 | -61.1572 | 61.8073 | 0.004578 | -0.1236 | 0.041199 | 61.9904 | -61.1298 | -0.19684 | 0.068664 | -0.13733 | -0.25177 | -0.16937 | -0.2243 | 0.013732 | 0.059509 | 60.7819 | 60.9467 | 122.7127 | 122.9507 | -0.13733 | 122.8958 | 60.91 | -0.2243 | 122.9507 | -0.13733 | 60.91 | 122.7127 | 122.8958 | -123.0789 | -123.1064
425.7656 | 123.175 | -60.8917 | 61.972 | 0.25536 | -0.0024482 | -0.00023494 | 0.00092504 | 0.0663 | -0.00030975 | 0.068693 | -61.0336 | 62.0407 | -61.1114 | -61.1389 | 61.8164 | 0.004578 | -0.13733 | 0.050354 | 61.9629 | -61.1114 | -0.21973 | 0.068664 | -0.14191 | -0.24719 | -0.15564 | -0.21973 | -0.009155 | 0.07782 | 60.7544 | 60.9421 | 122.7081 | 122.9324 | -0.14191 | 122.8546 | 60.8963 | -0.21973 | 122.9324 | -0.14191 | 60.8963 | 122.7081 | 122.8546 | -123.0835 | -123.0835
426.7656 | 123.1705 | -60.91 | 61.9766 | 0.20958 | -0.0045844 | -0.0017303 | -0.0044156 | 0.065018 | -0.0011643 | 0.06912 | -61.0199 | 61.9766 | -61.0794 | -61.1481 | 61.8256 | 0.032043 | -0.10986 | 0.091553 | 62.0041 | -61.1343 | -0.16937 | 0 | -0.10986 | -0.23804 | -0.15106 | -0.2243 | 0.027465 | 0.05951 | 60.8002 | 61.0016 | 122.7356 | 122.8867 | -0.10986 | 122.9141 | 60.9421 | -0.2243 | 122.8867 | -0.10986 | 60.9421 | 122.7356 | 122.9141 | -123.056 | -123.111
427.7656 | 123.1842 | -60.8963 | 61.94 | 0.28587 | -0.0022346 | -0.0036529 | 0.0045566 | 0.066727 | -0.0015915 | 0.067838 | -61.0382 | 62.0132 | -61.084 | -61.1389 | 61.8073 | -0.004578 | -0.13275 | 0.050354 | 61.9583 | -61.1664 | -0.18768 | 0.073243 | -0.14191 | -0.24262 | -0.13275 | -0.27008 | 0.018311 | 0.045776 | 60.7636 | 60.9467 | 122.7036 | 122.9095 | -0.14191 | 122.8546 | 60.8917 | -0.27008 | 122.9095 | -0.14191 | 60.8917 | 122.7036 | 122.8546 | -123.024 | -123.1064
428.7812 | 123.2071 | -60.878 | 61.9904 | -0.026932 | -0.0041572 | -0.0045075 | -0.0029202 | 0.062882 | -0.0050095 | 0.069547 | -61.0428 | 61.9675 | -61.0703 | -61.0977 | 61.8759 | 0.09613 | -0.036621 | 0.18768 | 61.9812 | -61.084 | -0.19226 | -0.022888 | -0.16479 | -0.21973 | -0.11444 | -0.20599 | -0.009155 | 0.027465 | 60.8414 | 61.0657 | 122.7539 | 122.8455 | -0.16479 | 122.8592 | 60.9741 | -0.20599 | 122.8455 | -0.16479 | 60.9741 | 122.7539 | 122.8592 | -123.0606 | -123.0743
429.7656 | 123.1155 | -60.9283 | 61.9812 | 0.23247 | -0.0022346 | -0.0017303 | 0.0028476 | 0.06395 | -0.0022323 | 0.069974 | -61.0657 | 62.0453 | -61.0886 | -61.1801 | 61.7615 | -0.050354 | -0.022888 | -0.009155 | 61.9904 | -61.1847 | -0.16022 | 0.064087 | -0.13733 | -0.25177 | -0.21973 | -0.25635 | 0.009155 | 0.022888 | 60.9055 | 60.9192 | 122.6898 | 122.9736 | -0.13733 | 122.9187 | 60.878 | -0.25635 | 122.9736 | -0.13733 | 60.878 | 122.6898 | 122.9187 | -123.0698 | -123.1659
430.7656 | 123.1934 | -60.9009 | 61.972 | 0.25536 | -0.0033026 | -2.1336e-05 | 0.001993 | 0.064591 | -0.0028731 | 0.069333 | -61.0336 | 62.0224 | -61.0977 | -61.1069 | 61.821 | 0.018311 | -0.14648 | 0.041199 | 61.9675 | -61.1389 | -0.19684 | 0.050354 | -0.13275 | -0.20599 | -0.15106 | -0.23804 | -0.004578 | 0.064087 | 60.7544 | 60.9421 | 122.7219 | 122.9233 | -0.13275 | 122.8683 | 60.9192 | -0.23804 | 122.9233 | -0.13275 | 60.9192 | 122.7219 | 122.8683 | -123.0698 | -123.111
431.7656 | 123.1796 | -60.9055 | 61.9354 | 0.25536 | -0.0024482 | 0.0012605 | 0.003702 | 0.065659 | -0.0020187 | 0.067624 | -61.0336 | 61.9995 | -61.1023 | -61.1206 | 61.8118 | 0.013733 | -0.14191 | 0.036621 | 61.9492 | -61.1389 | -0.19684 | 0.064087 | -0.12817 | -0.21515 | -0.1236 | -0.23346 | 0.013733 | 0.068665 | 60.7635 | 60.9421 | 122.7173 | 122.905 | -0.12817 | 122.8546 | 60.9192 | -0.23346 | 122.905 | -0.12817 | 60.9192 | 122.7173 | 122.8546 | -123.0377 | -123.0743
432.7656 | 123.1934 | -60.8917 | 61.9995 | 0.28587 | -0.0018072 | -0.0053619 | 0.00092504 | 0.065873 | -0.0011643 | 0.066984 | -60.9833 | 61.9537 | -61.0794 | -61.0794 | 61.8576 | 0.10529 | -0.43488 | 0.14191 | 61.9263 | -61.1435 | -0.18768 | -0.045777 | -0.091552 | -0.18768 | -0.14191 | -0.25177 | -0.073242 | 0.096131 | 60.4568 | 61.0336 | 122.7493 | 122.8455 | -0.091552 | 122.818 | 60.997 | -0.25177 | 122.8455 | -0.091552 | 60.997 | 122.7493 | 122.818 | -123.0789 | -123.143
433.7969 | 123.2117 | -60.8551 | 61.9446 | 1.9643 | -0.004798 | -0.00066214 | 0.0011386 | 0.066087 | -0.0035141 | 0.068906 | -60.9421 | 61.9492 | -61.084 | -61.0794 | 61.8622 | 0.064087 | -0.19684 | 0.10529 | 61.94 | -61.1023 | -0.22888 | 0.004578 | -0.086975 | -0.2243 | -0.082397 | -0.24719 | -0.004578 | 0.14191 | 60.6583 | 60.9604 | 122.7173 | 122.8043 | -0.086975 | 122.7951 | 60.9192 | -0.24719 | 122.8043 | -0.086975 | 60.9192 | 122.7173 | 122.7951 | -123.0286 | -123.0469
434.7656 | 123.1888 | -60.8643 | 61.9812 | 0.23247 | -0.0026618 | -0.0019439 | 0.0015658 | 0.0663 | -0.0030869 | 0.068265 | -60.9787 | 61.9629 | -61.0977 | -61.0886 | 61.734 | -0.13275 | -0.13275 | 0.22888 | 61.9308 | -61.116 | -0.23346 | -0.01831 | -0.11444 | -0.2243 | -0.24719 | -0.25177 | -0.050354 | 0.11902 | 60.7315 | 61.0931 | 122.5983 | 122.8271 | -0.11444 | 122.7951 | 60.7315 | -0.25177 | 122.8271 | -0.11444 | 60.7315 | 122.5983 | 122.7951 | -123.0789 | -123.0972
435.7656 | 123.1796 | -60.8917 | 61.972 | 0.28587 | -0.0028754 | 0.0025421 | 0.0049838 | 0.065018 | -0.0024459 | 0.069333 | -61.0062 | 62.0041 | -61.0931 | -61.1069 | 61.821 | 0.022888 | -0.15106 | 0.07782 | 61.9492 | -61.1298 | -0.20142 | 0.032043 | -0.11444 | -0.21515 | -0.15106 | -0.23804 | -0.022888 | 0.086975 | 60.7407 | 60.9695 | 122.7127 | 122.8958 | -0.11444 | 122.8409 | 60.9146 | -0.23804 | 122.8958 | -0.11444 | 60.9146 | 122.7127 | 122.8409 | -123.0652 | -123.1018
436.7812 | 123.2071 | -60.8505 | 61.9995 | -0.072708 | -0.0071478 | -0.0042937 | -0.0027066 | 0.065659 | -0.0024459 | 0.067624 | -60.9741 | 61.972 | -61.0474 | -61.0245 | 61.94 | 0.16022 | -0.050354 | 0.24719 | 61.9812 | -61.0611 | -0.19684 | -0.027466 | -0.1236 | -0.17395 | -0.05951 | -0.21057 | -0.018311 | 0.073242 | 60.8002 | 61.0977 | 122.7905 | 122.8226 | -0.1236 | 122.8317 | 61.0107 | -0.21057 | 122.8226 | -0.1236 | 61.0107 | 122.7905 | 122.8317 | -123.0469 | -123.0606
437.7656 | 123.1979 | -60.878 | 61.9629 | 0.24773 | -0.003089 | -0.0013031 | 0.0013522 | 0.064378 | -0.0030869 | 0.070188 | -60.9879 | 61.9492 | -61.0794 | -61.2579 | 61.8439 | 0.11444 | -0.11902 | 0.15564 | 61.9354 | -61.1343 | -0.20142 | -0.013733 | -0.10986 | -0.37994 | -0.11902 | -0.25635 | -0.027466 | 0.091553 | 60.759 | 61.0336 | 122.7219 | 122.8271 | -0.10986 | 122.8134 | 60.9924 | -0.25635 | 122.8271 | -0.10986 | 60.9924 | 122.7219 | 122.8134 | -123.0423 | -123.0972
438.7812 | 123.0881 | -60.9055 | 62.0453 | -0.15663 | -0.0037298 | -0.0017303 | 0.00049764 | 0.06096 | -0.0015915 | 0.067197 | -61.0565 | 62.0773 | -61.0703 | -61.1389 | 61.7889 | 0.045776 | 0.14648 | 0.12817 | 62.0361 | -61.116 | -0.16479 | 0.032044 | -0.15106 | -0.23346 | -0.25635 | -0.21057 | -0.009155 | 0.013732 | 61.0519 | 61.0336 | 122.6944 | 122.9828 | -0.15106 | 122.9416 | 60.9512 | -0.21057 | 122.9828 | -0.15106 | 60.9512 | 122.6944 | 122.9416 | -123.1155 | -123.1613
439.7656 | 123.1522 | -60.8734 | 61.9446 | 0.21721 | -0.0024482 | -2.1336e-05 | 0.00028404 | 0.064164 | -0.0039413 | 0.068693 | -60.997 | 61.9537 | -61.1023 | -61.0886 | 61.8439 | 0.045776 | -0.16022 | 0.086975 | 61.9537 | -61.1023 | -0.22888 | 0.009155 | -0.1236 | -0.21515 | -0.10071 | -0.22888 | 0.009155 | 0.10529 | 60.7132 | 60.9604 | 122.7173 | 122.8271 | -0.1236 | 122.8271 | 60.9192 | -0.22888 | 122.8271 | -0.1236 | 60.9192 | 122.7173 | 122.8271 | -123.0469 | -123.0469
440.7656 | 123.1613 | -60.8917 | 61.9675 | 0.19432 | -0.004798 | -0.0023711 | -0.00014316 | 0.062241 | -0.00095055 | 0.071256 | -61.0062 | 61.9537 | -61.0931 | -61.0886 | 61.8484 | 0.045776 | -0.17395 | 0.10071 | 61.9537 | -61.1069 | -0.20142 | -0.013733 | -0.11444 | -0.19684 | -0.11902 | -0.21515 | -0.013733 | 0.086975 | 60.7178 | 60.9924 | 122.7402 | 122.8455 | -0.11444 | 122.8455 | 60.9375 | -0.21515 | 122.8455 | -0.11444 | 60.9375 | 122.7402 | 122.8455 | -123.0606 | -123.0743
441.7656 | 123.175 | -60.878 | 61.9537 | 0.23247 | -0.0039434 | -0.0049347 | 7.0444e-05 | 0.064164 | -0.0033005 | 0.069333 | -60.9924 | 61.9446 | -61.0748 | -61.1023 | 61.8256 | 0.064087 | -0.16479 | 0.10529 | 61.9308 | -61.0931 | -0.19684 | -0.009155 | -0.11444 | -0.2243 | -0.12817 | -0.21515 | -0.022888 | 0.082397 | 60.7132 | 60.9833 | 122.7036 | 122.8226 | -0.11444 | 122.8088 | 60.9421 | -0.21515 | 122.8226 | -0.11444 | 60.9421 | 122.7036 | 122.8088 | -123.0286 | -123.0469
442.7656 | 123.1979 | -60.8871 | 61.9446 | 0.25536 | -0.0045844 | -0.0045075 | 0.0047702 | 0.062241 | -0.0011643 | 0.070188 | -60.9879 | 61.9537 | -61.0748 | -61.084 | 61.8759 | 0.068665 | -0.17853 | 0.09613 | 61.9308 | -61.1114 | -0.18768 | 0.009155 | -0.10071 | -0.19684 | -0.068664 | -0.2243 | -0.013733 | 0.086975 | 60.7086 | 60.9833 | 122.7631 | 122.8409 | -0.10071 | 122.818 | 60.9558 | -0.2243 | 122.8409 | -0.10071 | 60.9558 | 122.7631 | 122.818 | -123.0194 | -123.056
443.7812 | 123.1293 | -60.878 | 62.0087 | -0.0040434 | -0.0022346 | -0.0019439 | 0.0049838 | 0.064378 | -0.0018051 | 0.06677 | -60.9695 | 62.0773 | -61.0886 | -61.0794 | 61.8347 | 0.064087 | 0.045776 | 0.12817 | 61.9904 | -61.1526 | -0.21057 | 0.068665 | -0.091552 | -0.20142 | -0.17395 | -0.27466 | -0.018311 | 0.11902 | 60.9238 | 61.0062 | 122.7127 | 122.9553 | -0.091552 | 122.8683 | 60.9421 | -0.27466 | 122.9553 | -0.091552 | 60.9421 | 122.7127 | 122.8683 | -123.0972 | -123.1613
444.7656 | 123.1705 | -60.8871 | 61.9446 | 0.25536 | -0.0054388 | -0.0036529 | -0.001425 | 0.065873 | -0.0030869 | 0.068479 | -60.997 | 61.9629 | -61.0886 | -61.0886 | 61.8668 | 0.045776 | -0.16022 | 0.10529 | 61.9308 | -61.1114 | -0.20142 | 0.018311 | -0.10986 | -0.20142 | -0.07782 | -0.2243 | -0.013733 | 0.091553 | 60.7269 | 60.9924 | 122.7539 | 122.85 | -0.10986 | 122.818 | 60.9329 | -0.2243 | 122.85 | -0.10986 | 60.9329 | 122.7539 | 122.818 | -123.0331 | -123.056
445.7656 | 123.1934 | -60.878 | 61.9446 | 0.19432 | -0.004798 | -0.0019439 | -0.00035676 | 0.064164 | -0.0024459 | 0.066343 | -61.0153 | 61.9629 | -61.084 | -61.0794 | 61.8622 | 0.045776 | -0.16937 | 0.11902 | 61.9217 | -61.0977 | -0.20599 | 0.018311 | -0.13733 | -0.20142 | -0.082397 | -0.21973 | -0.022888 | 0.068664 | 60.7086 | 60.997 | 122.7402 | 122.8409 | -0.13733 | 122.7997 | 60.9238 | -0.21973 | 122.8409 | -0.13733 | 60.9238 | 122.7402 | 122.7997 | -123.0286 | -123.0423
446.7656 | 123.1613 | -60.8734 | 61.9812 | 0.20195 | -0.0033026 | -0.0036529 | -0.00014316 | 0.063096 | -0.0060775 | 0.068052 | -61.0199 | 61.9125 | -61.0931 | -61.1389 | 61.8256 | 0.027466 | -0.11444 | 0.082397 | 61.9583 | -61.0886 | -0.21973 | -0.068664 | -0.14648 | -0.2655 | -0.15564 | -0.21515 | -0.022888 | 0.073243 | 60.759 | 60.9558 | 122.699 | 122.7859 | -0.14648 | 122.8317 | 60.9009 | -0.21515 | 122.7859 | -0.14648 | 60.9009 | 122.699 | 122.8317 | -123.0743 | -123.0698
447.7812 | 123.175 | -60.8871 | 62.0224 | -0.15663 | -0.0045844 | -0.0013031 | 7.0444e-05 | 0.062241 | -0.0043685 | 0.067624 | -60.9879 | 61.9995 | -61.0428 | -61.0565 | 61.8896 | 0.14191 | 0.027466 | 0.21973 | 61.9675 | -61.0657 | -0.15564 | -0.022888 | -0.10071 | -0.16937 | -0.13275 | -0.17853 | -0.054932 | 0.054932 | 60.9146 | 61.1069 | 122.7768 | 122.8867 | -0.10071 | 122.8546 | 61.0291 | -0.17853 | 122.8867 | -0.10071 | 61.0291 | 122.7768 | 122.8546 | -123.0652 | -123.0881
448.7812 | 123.0835 | -60.9329 | 61.9812 | 0.19432 | -0.00095279 | 0.0010467 | 0.0049838 | 0.065873 | -0.0011643 | 0.067411 | -61.0657 | 62.0453 | -61.1114 | -61.171 | 61.7615 | -0.041199 | -0.022888 | -0.013733 | 61.9812 | -61.1618 | -0.17853 | 0.064087 | -0.13275 | -0.23804 | -0.21973 | -0.22888 | 0 | 0.045776 | 60.91 | 60.9192 | 122.6944 | 122.9782 | -0.13275 | 122.9141 | 60.8917 | -0.22888 | 122.9782 | -0.13275 | 60.8917 | 122.6944 | 122.9141 | -123.0927 | -123.143
449.7656 | 123.1934 | -60.8871 | 61.972 | 0.087509 | -0.0054388 | 0.00061946 | 0.001993 | 0.066727 | -0.0039413 | 0.068906 | -60.9833 | 61.9446 | -61.0611 | -61.0748 | 61.8622 | 0.059509 | -0.17853 | 0.1236 | 61.9583 | -61.0794 | -0.17395 | -0.027466 | -0.09613 | -0.18768 | -0.10986 | -0.19226 | -0.013733 | 0.07782 | 60.7086 | 61.0107 | 122.7493 | 122.8317 | -0.09613 | 122.8455 | 60.9467 | -0.19226 | 122.8317 | -0.09613 | 60.9467 | 122.7493 | 122.8455 | -123.0331 | -123.0515
450.7812 | 123.1659 | -60.878 | 62.0178 | 0.072251 | -0.0043708 | -0.0060027 | -0.00099756 | 0.062241 | -0.0050095 | 0.069547 | -61.0703 | 61.9492 | -61.0886 | -61.1481 | 61.8256 | 0.032043 | -0.064087 | 0.091553 | 61.9675 | -61.0657 | -0.21057 | -0.068664 | -0.19226 | -0.27008 | -0.19226 | -0.18768 | -0.050354 | 0.018311 | 60.8139 | 60.9695 | 122.7036 | 122.8271 | -0.19226 | 122.8455 | 60.91 | -0.18768 | 122.8271 | -0.19226 | 60.91 | 122.7036 | 122.8455 | -123.1064 | -123.0835
451.7812 | 123.2071 | -60.8597 | 61.972 | -0.072708 | -0.006507 | -0.00087594 | 0.00092504 | 0.0616 | -0.0037277 | 0.068052 | -60.997 | 61.9492 | -61.0519 | -61.0611 | 61.8942 | 0.14191 | -0.064087 | 0.22888 | 61.9446 | -61.0748 | -0.19226 | -0.022888 | -0.13733 | -0.20142 | -0.07782 | -0.21515 | -0.027466 | 0.054932 | 60.7956 | 61.0886 | 122.7539 | 122.8088 | -0.13733 | 122.8043 | 61.0016 | -0.21515 | 122.8088 | -0.13733 | 61.0016 | 122.7539 | 122.8043 | -123.024 | -123.0469
452.7812 | 123.1018 | -60.878 | 62.0361 | -0.13374 | -0.0024482 | -0.0010895 | 0.0077608 | 0.064164 | -0.0035141 | 0.068052 | -61.0245 | 62.0773 | -61.0977 | -61.1252 | 61.8164 | 0.059509 | 0.1236 | 0.13275 | 62.0316 | -61.1252 | -0.21973 | 0.041199 | -0.14648 | -0.24719 | -0.21973 | -0.24719 | -0.004578 | 0.073242 | 61.0016 | 61.0107 | 122.6944 | 122.9553 | -0.14648 | 122.9095 | 60.9375 | -0.24719 | 122.9553 | -0.14648 | 60.9375 | 122.6944 | 122.9095 | -123.1338 | -123.1613
453.7969 | 123.1659 | -60.9055 | 61.9766 | 0.095139 | -0.0037298 | -0.010275 | -0.002493 | 0.062028 | -0.0028731 | 0.069974 | -61.0794 | 61.9675 | -61.0748 | -61.0336 | 61.908 | 0.086975 | -0.082397 | 0.11444 | 61.9675 | -61.0794 | -0.16937 | -0.009156 | -0.17395 | -0.12817 | -0.068665 | -0.17395 | -0.009156 | -0.004578 | 60.8231 | 61.0199 | 122.8134 | 122.8729 | -0.17395 | 122.8729 | 60.9924 | -0.17395 | 122.8729 | -0.17395 | 60.9924 | 122.8134 | 122.8729 | -123.0515 | -123.056
454.7656 | 123.2025 | -60.8551 | 61.9858 | -0.095596 | -0.006507 | -0.0042937 | 0.0022066 | 0.061387 | -0.0056503 | 0.06912 | -60.9558 | 61.972 | -61.0611 | -61.0107 | 61.9537 | 0.14191 | -0.050354 | 0.24261 | 61.9537 | -61.0565 | -0.20599 | -0.013733 | -0.10071 | -0.15564 | -0.032044 | -0.20142 | -0.032044 | 0.10529 | 60.8047 | 61.0977 | 122.8088 | 122.8271 | -0.10071 | 122.8088 | 60.997 | -0.20142 | 122.8271 | -0.10071 | 60.997 | 122.8088 | 122.8088 | -123.0469 | -123.0423
455.7812 | 123.1888 | -60.8597 | 62.0178 | -0.11085 | -0.0045844 | 0.00040586 | 0.0032748 | 0.06096 | -0.0033005 | 0.070402 | -60.9741 | 61.9766 | -61.0428 | -61.0428 | 61.8805 | 0.15564 | 0.027466 | 0.22888 | 61.9446 | -61.0977 | -0.18311 | -0.041198 | -0.11444 | -0.18311 | -0.13733 | -0.23804 | -0.073242 | 0.068665 | 60.8871 | 61.0886 | 122.7402 | 122.8363 | -0.11444 | 122.8043 | 61.0153 | -0.23804 | 122.8363 | -0.11444 | 61.0153 | 122.7402 | 122.8043 | -123.0606 | -123.1155
456.7812 | 123.1705 | -60.8734 | 62.027 | -0.12611 | -0.0039434 | -0.0013031 | 0.0017794 | 0.059678 | -0.0041549 | 0.067411 | -60.9695 | 61.9949 | -61.0657 | -61.0703 | 61.8988 | 0.15564 | 0.022888 | 0.23346 | 61.9766 | -61.0565 | -0.19226 | -0.032044 | -0.09613 | -0.19684 | -0.12817 | -0.18311 | -0.050354 | 0.096131 | 60.8963 | 61.1069 | 122.7722 | 122.8683 | -0.09613 | 122.85 | 61.0291 | -0.18311 | 122.8683 | -0.09613 | 61.0291 | 122.7722 | 122.85 | -123.0927 | -123.0835
457.7812 | 123.0881 | -60.9055 | 62.0041 | 0.087509 | -0.00052559 | 0.0016877 | 0.0069064 | 0.064378 | -0.0045821 | 0.065916 | -61.0245 | 62.0544 | -61.1069 | -61.116 | 61.7798 | -0.004578 | 0.018311 | 0.032043 | 62.0041 | -61.1526 | -0.20142 | 0.050354 | -0.11902 | -0.21057 | -0.2243 | -0.24719 | 0 | 0.082398 | 60.9238 | 60.9375 | 122.6852 | 122.9599 | -0.11902 | 122.9095 | 60.9009 | -0.24719 | 122.9599 | -0.11902 | 60.9009 | 122.6852 | 122.9095 | -123.111 | -123.1567
458.7969 | 123.1522 | -60.8551 | 61.9904 | -0.20241 | -0.0041572 | -0.0047211 | 0.0011386 | 0.063096 | -0.0024459 | 0.068052 | -60.9879 | 61.9995 | -61.0657 | -61.0565 | 61.8622 | 0.11902 | 0.054932 | 0.18768 | 61.9995 | -61.0657 | -0.21057 | 0.009156 | -0.13275 | -0.20142 | -0.12817 | -0.21057 | 0.009156 | 0.07782 | 60.91 | 61.0428 | 122.7173 | 122.8546 | -0.13275 | 122.8546 | 60.9741 | -0.21057 | 122.8546 | -0.13275 | 60.9741 | 122.7173 | 122.8546 | -123.056 | -123.056
459.7812 | 123.1613 | -60.8597 | 62.0087 | -0.087967 | -0.0056524 | -0.0040801 | -0.00014316 | 0.061387 | -0.0060775 | 0.06912 | -61.0016 | 61.9904 | -61.0519 | -61.0382 | 61.8988 | 0.13275 | 0.032043 | 0.23804 | 61.9995 | -61.0565 | -0.19226 | -0.018311 | -0.14191 | -0.17853 | -0.10986 | -0.19684 | -0.009155 | 0.050354 | 60.8917 | 61.0977 | 122.7585 | 122.85 | -0.14191 | 122.8592 | 60.9924 | -0.19684 | 122.85 | -0.14191 | 60.9924 | 122.7585 | 122.8592 | -123.0606 | -123.0652
460.7812 | 123.0881 | -60.8917 | 62.0361 | -0.17952 | -0.003089 | -0.0049347 | 0.0024202 | 0.063737 | -0.0043685 | 0.068906 | -61.0336 | 62.0316 | -61.084 | -61.1252 | 61.8301 | 0.064087 | 0.13733 | 0.13275 | 62.0224 | -61.0977 | -0.19226 | -0.004578 | -0.14191 | -0.23346 | -0.20599 | -0.20599 | -0.013733 | 0.050354 | 61.0291 | 61.0245 | 122.7219 | 122.9233 | -0.14191 | 122.9141 | 60.9558 | -0.20599 | 122.9233 | -0.14191 | 60.9558 | 122.7219 | 122.9141 | -123.1201 | -123.1338
461.7812 | 123.111 | -60.8917 | 62.0361 | -0.12611 | -0.0022346 | -0.0070709 | 0.005411 | 0.064591 | -0.0035141 | 0.069333 | -61.0245 | 62.0819 | -61.0794 | -61.1023 | 61.821 | 0.073242 | 0.10071 | 0.12817 | 62.0041 | -61.1252 | -0.18768 | 0.045776 | -0.13275 | -0.21057 | -0.21515 | -0.23346 | -0.032044 | 0.054932 | 60.9924 | 61.0199 | 122.7127 | 122.9736 | -0.13275 | 122.8958 | 60.965 | -0.23346 | 122.9736 | -0.13275 | 60.965 | 122.7127 | 122.8958 | -123.1155 | -123.1613
462.7812 | 123.1064 | -60.91 | 61.9904 | 0.23247 | -0.0020208 | -0.0025847 | 0.0058382 | 0.065659 | -0.0028731 | 0.067624 | -61.0565 | 62.0361 | -61.1069 | -61.1847 | 61.7706 | -0.041199 | -0.050354 | 0.004578 | 61.9492 | -61.1755 | -0.19684 | 0.045777 | -0.14648 | -0.27466 | -0.21973 | -0.2655 | -0.041198 | 0.050354 | 60.8597 | 60.9146 | 122.6807 | 122.9462 | -0.14648 | 122.8592 | 60.8688 | -0.2655 | 122.9462 | -0.14648 | 60.8688 | 122.6807 | 122.8592 | -123.0972 | -123.1659
463.7969 | 123.1247 | -60.9055 | 62.027 | -0.12611 | -0.0035162 | -0.0042937 | 0.004343 | 0.06395 | -0.0022323 | 0.067624 | -61.0016 | 62.1002 | -61.0748 | -61.0977 | 61.8347 | 0.07782 | 0.068665 | 0.12817 | 61.9949 | -61.1114 | -0.16937 | 0.073242 | -0.09613 | -0.19226 | -0.19226 | -0.20599 | -0.032044 | 0.073242 | 60.9741 | 61.0336 | 122.7402 | 123.0057 | -0.09613 | 122.9004 | 60.9833 | -0.20599 | 123.0057 | -0.09613 | 60.9833 | 122.7402 | 122.9004 | -123.1018 | -123.1384
464.7812 | 123.0835 | -60.9055 | 62.0361 | -1.5528 | -0.0033026 | 0.0023285 | 0.0034884 | 0.065232 | -0.0011643 | 0.067838 | -61.1023 | 62.114 | -61.0977 | -61.1481 | 61.7935 | 0.064087 | 0.14648 | 0.13733 | 62.0132 | -61.116 | -0.19226 | 0.07782 | -0.19684 | -0.24261 | -0.24262 | -0.21057 | -0.022888 | -0.004578 | 61.0519 | 61.0428 | 122.699 | 123.0194 | -0.19684 | 122.9187 | 60.9695 | -0.21057 | 123.0194 | -0.19684 | 60.9695 | 122.699 | 122.9187 | -123.1338 | -123.1522
465.7812 | 123.0606 | -60.9375 | 62.0132 | 0.056992 | -0.00073919 | -0.00023494 | 0.003702 | 0.067155 | -0.0018051 | 0.070615 | -61.0519 | 62.0911 | -61.0931 | -61.1755 | 61.7935 | -0.022888 | 0.032043 | 0.009155 | 61.9904 | -61.1481 | -0.15564 | 0.077819 | -0.11444 | -0.23804 | -0.21973 | -0.21057 | -0.022889 | 0.041199 | 60.9695 | 60.9467 | 122.731 | 123.0286 | -0.11444 | 122.9279 | 60.9146 | -0.21057 | 123.0286 | -0.11444 | 60.9146 | 122.731 | 122.9279 | -123.1064 | -123.1613
466.7812 | 123.0881 | -60.91 | 62.0041 | 0.1638 | -0.00073919 | -0.0021575 | 0.0034884 | 0.067582 | -0.0030869 | 0.069974 | -61.0291 | 62.0865 | -61.1114 | -61.1847 | 61.7752 | -0.027466 | 0.036621 | 0.022888 | 61.9949 | -61.1481 | -0.20142 | 0.082398 | -0.11902 | -0.27466 | -0.22888 | -0.23804 | -0.009155 | 0.082397 | 60.9467 | 60.9329 | 122.6852 | 122.9965 | -0.11902 | 122.905 | 60.8826 | -0.23804 | 122.9965 | -0.11902 | 60.8826 | 122.6852 | 122.905 | -123.1155 | -123.1522
467.7812 | 123.1613 | -60.9238 | 61.9446 | 0.19432 | -0.00138 | -0.0040801 | -0.0037748 | 0.066087 | -0.00052335 | 0.069547 | -61.0565 | 62.0041 | -61.0657 | -61.1435 | 61.8301 | 0.054932 | -0.082397 | 0.09613 | 61.9766 | -61.0931 | -0.14191 | 0.059509 | -0.13275 | -0.21973 | -0.11444 | -0.16937 | 0.032044 | 0.009155 | 60.8414 | 61.0199 | 122.7539 | 122.9279 | -0.13275 | 122.9004 | 60.9787 | -0.16937 | 122.9279 | -0.13275 | 60.9787 | 122.7539 | 122.9004 | -123.0103 | -123.0377
468.7969 | 123.0606 | -60.9329 | 62.0224 | -0.17952 | -0.0024482 | -0.0032257 | 0.0024202 | 0.063737 | -0.00095055 | 0.070615 | -61.0748 | 62.0773 | -61.0977 | -61.1481 | 61.8027 | 0.054932 | 0.16479 | 0.11444 | 61.9995 | -61.1069 | -0.1648 | 0.054932 | -0.14191 | -0.21515 | -0.21973 | -0.17395 | -0.022888 | 0.022888 | 61.0977 | 61.0474 | 122.7356 | 123.0103 | -0.14191 | 122.9324 | 60.9879 | -0.17395 | 123.0103 | -0.14191 | 60.9879 | 122.7356 | 122.9324 | -123.1201 | -123.1293
469.7812 | 123.1796 | -60.878 | 61.9675 | 0.2401 | -0.0039434 | -0.0027985 | -0.00014316 | 0.065873 | -0.0026595 | 0.068693 | -61.0016 | 61.9766 | -61.0519 | -60.997 | 61.9583 | 0.10071 | -0.15106 | 0.13733 | 61.9308 | -61.116 | -0.17395 | 0.009156 | -0.1236 | -0.11902 | -0.009155 | -0.23804 | -0.036621 | 0.050354 | 60.7269 | 61.0153 | 122.8363 | 122.8546 | -0.1236 | 122.8088 | 60.9787 | -0.23804 | 122.8546 | -0.1236 | 60.9787 | 122.8363 | 122.8088 | -123.0194 | -123.0835
470.7812 | 123.1064 | -60.8963 | 62.027 | -0.14137 | -0.0024482 | -0.0021575 | 0.0049838 | 0.064805 | -0.0037277 | 0.067197 | -61.0199 | 62.0773 | -61.0703 | -61.116 | 61.8439 | 0.091553 | 0.086975 | 0.13733 | 61.9904 | -61.1206 | -0.17395 | 0.050354 | -0.1236 | -0.21973 | -0.18311 | -0.2243 | -0.036622 | 0.050354 | 60.9833 | 61.0336 | 122.7402 | 122.9736 | -0.1236 | 122.8867 | 60.9879 | -0.2243 | 122.9736 | -0.1236 | 60.9879 | 122.7402 | 122.8867 | -123.0972 | -123.1476
471.7812 | 123.0972 | -60.9146 | 62.0132 | 0.13329 | -0.0011664 | -0.0034393 | 0.0047702 | 0.066941 | -0.0018051 | 0.068693 | -61.0657 | 62.0728 | -61.0748 | -61.1755 | 61.7844 | -0.027466 | 0.036621 | 0.027466 | 62.0132 | -61.1481 | -0.16022 | 0.059509 | -0.15106 | -0.26093 | -0.22888 | -0.23346 | 0 | 0.009155 | 60.9512 | 60.9421 | 122.699 | 122.9874 | -0.15106 | 122.9279 | 60.8871 | -0.23346 | 122.9874 | -0.15106 | 60.8871 | 122.699 | 122.9279 | -123.0881 | -123.1613
472.7812 | 123.1064 | -60.9146 | 61.9949 | 0.041733 | 0.00011541 | -2.1336e-05 | 0.0032748 | 0.067155 | -0.0018051 | 0.069333 | -60.997 | 62.0911 | -61.0977 | -61.1252 | 61.8027 | 0.054932 | 0.045776 | 0.086975 | 62.0224 | -61.1114 | -0.18311 | 0.09613 | -0.082397 | -0.21057 | -0.19226 | -0.19684 | 0.027466 | 0.10071 | 60.9604 | 61.0016 | 122.7173 | 123.0057 | -0.082397 | 122.937 | 60.9695 | -0.19684 | 123.0057 | -0.082397 | 60.9695 | 122.7173 | 122.937 | -123.0927 | -123.1064
473.7969 | 123.0972 | -60.9283 | 61.9766 | 0.18669 | -0.00095279 | -0.0025847 | 0.004343 | 0.066941 | -0.0035141 | 0.069974 | -61.084 | 62.0544 | -61.1389 | -61.1755 | 61.8118 | -0.009155 | 0.018311 | 0.022888 | 61.9904 | -61.1664 | -0.21057 | 0.077819 | -0.15564 | -0.24719 | -0.16479 | -0.23804 | 0.013732 | 0.054932 | 60.9467 | 60.9512 | 122.7402 | 122.9828 | -0.15564 | 122.9187 | 60.9192 | -0.23804 | 122.9828 | -0.15564 | 60.9192 | 122.7402 | 122.9187 | -123.1155 | -123.143
474.7812 | 123.0927 | -60.9421 | 61.9812 | 0.23247 | -0.0024482 | -0.0034393 | 0.0028476 | 0.066514 | 0.00011745 | 0.070615 | -61.0703 | 62.0544 | -61.1206 | -61.1847 | 61.7661 | -0.022888 | -0.059509 | 0.013733 | 61.9629 | -61.1343 | -0.17853 | 0.073242 | -0.12817 | -0.24261 | -0.21515 | -0.19226 | -0.01831 | 0.050354 | 60.8826 | 60.9558 | 122.7081 | 122.9965 | -0.12817 | 122.905 | 60.9192 | -0.19226 | 122.9965 | -0.12817 | 60.9192 | 122.7081 | 122.905 | -123.1018 | -123.1155
475.7812 | 123.1842 | -60.8826 | 61.9629 | 0.2401 | -0.0043708 | -0.0049347 | -0.0044156 | 0.06395 | -0.0011643 | 0.069974 | -61.0199 | 61.9675 | -61.0794 | -61.116 | 61.8347 | 0.036621 | -0.13275 | 0.10071 | 61.9446 | -61.1069 | -0.19684 | 0.004577 | -0.13733 | -0.23346 | -0.12817 | -0.22431 | -0.018311 | 0.05951 | 60.7498 | 60.9833 | 122.7173 | 122.85 | -0.13733 | 122.8271 | 60.9192 | -0.22431 | 122.85 | -0.13733 | 60.9192 | 122.7173 | 122.8271 | -123.0423 | -123.0698
476.7812 | 123.1934 | -60.8871 | 61.972 | 0.26299 | -0.0022346 | -0.0027985 | 0.0011386 | 0.066941 | -0.0020187 | 0.067838 | -61.0062 | 61.9354 | -61.0886 | -61.1801 | 61.972 | 0.12817 | -0.11902 | 0.16022 | 61.9583 | -61.0794 | -0.20142 | -0.036621 | -0.11902 | -0.29297 | 0 | -0.19226 | -0.013733 | 0.082397 | 60.7681 | 61.0474 | 122.8592 | 122.8226 | -0.11902 | 122.8455 | 61.0153 | -0.19226 | 122.8226 | -0.11902 | 61.0153 | 122.8592 | 122.8455 | -123.0606 | -123.0515
477.7812 | 123.1338 | -60.9146 | 61.9858 | 0.15617 | -0.0039434 | -0.0055755 | -0.00099756 | 0.063523 | -0.0028731 | 0.068906 | -61.0611 | 61.9675 | -61.084 | -61.1389 | 61.8164 | 0.032043 | -0.068665 | 0.09613 | 61.9629 | -61.0977 | -0.16937 | -0.018311 | -0.14648 | -0.2243 | -0.16937 | -0.18311 | -0.022888 | 0.022888 | 60.8459 | 61.0107 | 122.731 | 122.8821 | -0.14648 | 122.8775 | 60.9467 | -0.18311 | 122.8821 | -0.14648 | 60.9467 | 122.731 | 122.8775 | -123.0698 | -123.0835
478.7969 | 123.024 | -60.878 | 62.059 | -0.18715 | -0.0033026 | -0.0032257 | 0.004343 | 0.062455 | -0.0024459 | 0.068265 | -61.0565 | 62.0499 | -61.0748 | -61.1389 | 61.7844 | 0.050354 | 0.14648 | 0.12817 | 62.0453 | -61.0977 | -0.19684 | -0.009155 | -0.17853 | -0.26093 | -0.27466 | -0.21973 | -0.013733 | 0.01831 | 61.0245 | 61.0062 | 122.6624 | 122.9279 | -0.17853 | 122.9233 | 60.9283 | -0.21973 | 122.9279 | -0.17853 | 60.9283 | 122.6624 | 122.9233 | -123.1338 | -123.1567
479.7812 | 123.1979 | -60.8551 | 61.9995 | 0.011215 | -0.0060798 | -0.0064301 | -0.002493 | 0.060746 | -0.0020187 | 0.068693 | -61.0016 | 61.9583 | -61.0657 | -61.084 | 61.8988 | 0.12817 | -0.059509 | 0.20142 | 61.9949 | -61.084 | -0.21057 | -0.041199 | -0.14648 | -0.22888 | -0.10071 | -0.22888 | -0.004578 | 0.064087 | 60.7956 | 61.0565 | 122.7539 | 122.8134 | -0.14648 | 122.85 | 60.9833 | -0.22888 | 122.8134 | -0.14648 | 60.9833 | 122.7539 | 122.85 | -123.0652 | -123.0835
480.7812 | 123.1522 | -60.9055 | 61.9858 | 0.095139 | -0.004798 | -0.0053619 | -0.00014316 | 0.064164 | -0.0028731 | 0.067411 | -61.0474 | 61.9629 | -61.0748 | -61.1389 | 61.8164 | 0.032043 | -0.07782 | 0.11902 | 61.9583 | -61.0977 | -0.16937 | -0.022888 | -0.14191 | -0.23346 | -0.16937 | -0.19226 | -0.027466 | 0.027466 | 60.8276 | 61.0245 | 122.7219 | 122.8683 | -0.14191 | 122.8638 | 60.9375 | -0.19226 | 122.8683 | -0.14191 | 60.9375 | 122.7219 | 122.8638 | -123.0606 | -123.0835
481.7812 | 123.1796 | -60.8505 | 61.9858 | -0.026932 | -0.0054388 | -0.0070709 | 0.0015658 | 0.061814 | -0.0047957 | 0.068052 | -60.9741 | 61.9949 | -61.0657 | -61.0428 | 61.8759 | 0.14191 | -0.004578 | 0.24261 | 61.9583 | -61.0657 | -0.21515 | 0.009155 | -0.1236 | -0.19226 | -0.10986 | -0.21515 | -0.027466 | 0.091553 | 60.8459 | 61.0931 | 122.7264 | 122.8455 | -0.1236 | 122.8088 | 60.9924 | -0.21515 | 122.8455 | -0.1236 | 60.9924 | 122.7264 | 122.8088 | -123.0515 | -123.0515
482.7812 | 123.2208 | -60.8459 | 61.9949 | -0.065079 | -0.0073614 | -0.0072845 | 0.00049764 | 0.06395 | -0.0030869 | 0.069547 | -60.9421 | 61.9766 | -61.0382 | -61.0336 | 61.8988 | 0.15564 | -0.041199 | 0.25635 | 61.9675 | -61.0382 | -0.19226 | -0.01831 | -0.096131 | -0.18768 | -0.09613 | -0.19226 | -0.027466 | 0.09613 | 60.8047 | 61.1023 | 122.7448 | 122.8226 | -0.096131 | 122.8134 | 61.0016 | -0.19226 | 122.8226 | -0.096131 | 61.0016 | 122.7448 | 122.8134 | -123.0331 | -123.0331
483.7969 | 123.0927 | -60.9192 | 62.0361 | -0.14137 | -0.0015936 | -0.0030121 | 0.0060518 | 0.063309 | -0.0039413 | 0.068265 | -61.0199 | 62.0865 | -61.0931 | -61.1114 | 61.8027 | 0.050354 | 0.13275 | 0.1236 | 62.0316 | -61.1252 | -0.17395 | 0.050354 | -0.10071 | -0.19226 | -0.23346 | -0.20599 | -0.004578 | 0.073243 | 61.0519 | 61.0428 | 122.7219 | 123.0057 | -0.10071 | 122.9507 | 60.9695 | -0.20599 | 123.0057 | -0.10071 | 60.9695 | 122.7219 | 122.9507 | -123.1293 | -123.1613
484.7812 | 123.111 | -60.8917 | 62.0316 | -0.04982 | -0.00138 | -0.0019439 | 0.0034884 | 0.064164 | -0.0026595 | 0.066343 | -61.0199 | 62.0819 | -61.0703 | -61.1298 | 61.8027 | 0.041199 | 0.14191 | 0.1236 | 62.0544 | -61.1069 | -0.17853 | 0.050354 | -0.12817 | -0.23804 | -0.22888 | -0.21515 | 0.022888 | 0.050354 | 61.0336 | 61.0153 | 122.6944 | 122.9736 | -0.12817 | 122.9462 | 60.9329 | -0.21515 | 122.9736 | -0.12817 | 60.9329 | 122.6944 | 122.9462 | -123.1018 | -123.1384
485.7812 | 123.1064 | -60.8963 | 61.9995 | 0.19432 | -0.0037298 | -0.0038665 | 0.0066928 | 0.070145 | -0.0020187 | 0.069547 | -61.0703 | 62.0544 | -61.1069 | -61.0062 | 61.8027 | -0.022888 | 0.022888 | -0.004578 | 62.0178 | -61.1206 | -0.21057 | 0.054931 | -0.17395 | -0.10986 | -0.19684 | -0.2243 | 0.01831 | 0.036622 | 60.9192 | 60.8917 | 122.699 | 122.9507 | -0.17395 | 122.9141 | 60.8734 | -0.2243 | 122.9507 | -0.17395 | 60.8734 | 122.699 | 122.9141 | -123.1064 | -123.1201
486.7812 | 123.0789 | -60.9192 | 61.9949 | 0.011215 | -0.0024482 | -0.0017303 | 0.0045566 | 0.067155 | -0.00073695 | 0.069547 | -61.0153 | 62.0865 | -61.1069 | -61.1343 | 61.7935 | 0.009155 | 0.018311 | 0.064087 | 62.0041 | -61.1435 | -0.18768 | 0.091553 | -0.096131 | -0.21515 | -0.20142 | -0.2243 | 0.009155 | 0.091553 | 60.9375 | 60.9833 | 122.7127 | 123.0057 | -0.096131 | 122.9233 | 60.9283 | -0.2243 | 123.0057 | -0.096131 | 60.9283 | 122.7127 | 122.9233 | -123.1018 | -123.1384
487.7812 | 123.1705 | -60.9009 | 61.9812 | 0.20195 | -0.0039434 | -0.0032257 | -0.0027066 | 0.064591 | -0.0028731 | 0.068479 | -61.0428 | 61.9308 | -61.1023 | -61.1389 | 61.8393 | 0.018311 | -0.10986 | 0.09613 | 61.94 | -61.0931 | -0.20142 | -0.050354 | -0.14191 | -0.23804 | -0.14191 | -0.19226 | -0.041199 | 0.059509 | 60.791 | 60.997 | 122.7402 | 122.8317 | -0.14191 | 122.8409 | 60.9192 | -0.19226 | 122.8317 | -0.14191 | 60.9192 | 122.7402 | 122.8409 | -123.0835 | -123.0743
488.7812 | 123.2025 | -60.8871 | 61.9537 | 0.24773 | -0.0041572 | 0.00061946 | 0.0032748 | 0.064805 | -0.0030869 | 0.068265 | -60.9833 | 61.9675 | -61.1114 | -61.0794 | 61.8439 | 0.045776 | -0.17853 | 0.10071 | 61.94 | -61.116 | -0.2243 | 0.013733 | -0.09613 | -0.19226 | -0.10986 | -0.22888 | -0.013733 | 0.12817 | 60.7086 | 60.9879 | 122.731 | 122.8546 | -0.09613 | 122.8271 | 60.9329 | -0.22888 | 122.8546 | -0.09613 | 60.9329 | 122.731 | 122.8271 | -123.0652 | -123.0698
489.7812 | 123.0972 | -60.9238 | 61.9949 | 0.064621 | -0.00031179 | -0.0010895 | 0.0058382 | 0.0663 | -0.0035141 | 0.067197 | -61.0199 | 62.0453 | -61.0931 | -61.1389 | 61.7844 | 0.022888 | 0.022888 | 0.041199 | 61.9995 | -61.1526 | -0.16937 | 0.050354 | -0.09613 | -0.21515 | -0.21057 | -0.22888 | 0.004578 | 0.073243 | 60.9467 | 60.965 | 122.7081 | 122.9691 | -0.09613 | 122.9233 | 60.9467 | -0.22888 | 122.9691 | -0.09613 | 60.9467 | 122.7081 | 122.9233 | -123.0881 | -123.1476
490.7812 | 123.0789 | -60.91 | 61.9949 | 0.1104 | -0.0011664 | -0.00087594 | 0.0034884 | 0.065446 | -0.0030869 | 0.069974 | -61.0107 | 62.0773 | -61.0931 | -61.1481 | 61.7889 | 0.009155 | 0.018311 | 0.059509 | 61.9904 | -61.1572 | -0.18311 | 0.082398 | -0.10071 | -0.23804 | -0.20599 | -0.24719 | -0.004578 | 0.082398 | 60.9283 | 60.9695 | 122.699 | 122.9874 | -0.10071 | 122.9004 | 60.9192 | -0.24719 | 122.9874 | -0.10071 | 60.9192 | 122.699 | 122.9004 | -123.0881 | -123.1522
491.7812 | 123.1659 | -60.9192 | 61.972 | 0.26299 | -0.00095279 | -0.0036529 | 0.0030612 | 0.0663 | -0.00073695 | 0.070188 | -61.0428 | 62.0316 | -61.1114 | -61.1618 | 61.8118 | -0.004578 | -0.09613 | 0.032043 | 61.9858 | -61.1298 | -0.19226 | 0.059509 | -0.1236 | -0.24261 | -0.16022 | -0.21057 | 0.013733 | 0.068664 | 60.8231 | 60.9512 | 122.731 | 122.9507 | -0.1236 | 122.905 | 60.9146 | -0.21057 | 122.9507 | -0.1236 | 60.9146 | 122.731 | 122.905 | -123.0835 | -123.1018
492.7812 | 123.143 | -60.91 | 62.0224 | -0.13374 | -0.00052559 | -0.0038665 | 0.0024202 | 0.065659 | 0.00054465 | 0.067624 | -61.0611 | 62.1094 | -61.0931 | -61.1252 | 61.8118 | 0.068665 | 0.1236 | 0.11902 | 62.0407 | -61.1252 | -0.18311 | 0.086975 | -0.15106 | -0.21515 | -0.21057 | -0.21515 | 0.01831 | 0.032044 | 61.0336 | 61.0291 | 122.7219 | 123.0194 | -0.15106 | 122.9507 | 60.9787 | -0.21515 | 123.0194 | -0.15106 | 60.9787 | 122.7219 | 122.9507 | -123.1155 | -123.1476
493.7812 | 123.1613 | -60.9146 | 61.9766 | 0.26299 | -0.0022346 | -0.0036529 | 0.0011386 | 0.065232 | -0.0026595 | 0.068052 | -61.0565 | 62.0453 | -61.1069 | -61.1526 | 61.7981 | -0.013733 | -0.09613 | 0.022888 | 61.9858 | -61.1206 | -0.19226 | 0.068664 | -0.14191 | -0.23804 | -0.17853 | -0.20599 | 0.009155 | 0.050354 | 60.8185 | 60.9375 | 122.7127 | 122.9599 | -0.14191 | 122.9004 | 60.9009 | -0.20599 | 122.9599 | -0.14191 | 60.9009 | 122.7127 | 122.9004 | -123.0835 | -123.0972
494.7812 | 123.0515 | -60.9329 | 62.0041 | 0.14854 | -0.0033026 | -0.0045075 | 0.0041292 | 0.066087 | -0.0060775 | 0.070402 | -61.0474 | 62.0956 | -61.0977 | -61.2076 | 61.7477 | -0.041199 | 0.032043 | 0 | 61.9904 | -61.1801 | -0.1648 | 0.091553 | -0.11444 | -0.27466 | -0.25635 | -0.24719 | -0.013733 | 0.050354 | 60.965 | 60.9329 | 122.6807 | 123.0286 | -0.11444 | 122.9233 | 60.8917 | -0.24719 | 123.0286 | -0.11444 | 60.8917 | 122.6807 | 122.9233 | -123.1018 | -123.1842
495.7812 | 123.1522 | -60.8826 | 61.9583 | 0.13329 | -0.0069342 | -0.0055755 | -0.0035612 | 0.06395 | -0.0022323 | 0.071042 | -61.0703 | 61.972 | -61.0931 | -61.1572 | 61.8439 | 0.050354 | -0.07782 | 0.082397 | 61.9629 | -61.1252 | -0.21057 | 0.013733 | -0.18768 | -0.27466 | -0.11444 | -0.24262 | 0.004578 | 0.022889 | 60.8047 | 60.965 | 122.7264 | 122.8546 | -0.18768 | 122.8455 | 60.9329 | -0.24262 | 122.8546 | -0.18768 | 60.9329 | 122.7264 | 122.8455 | -123.0515 | -123.0835
496.7812 | 123.1659 | -60.8963 | 61.9537 | 0.20195 | -0.0050116 | -0.0030121 | -0.0020658 | 0.064164 | -0.00030975 | 0.067411 | -61.0199 | 61.9583 | -61.0977 | -61.1298 | 61.8347 | 0.032043 | -0.11444 | 0.11444 | 61.9583 | -61.0748 | -0.20142 | 0.004578 | -0.1236 | -0.23346 | -0.11902 | -0.17853 | 0.004578 | 0.07782 | 60.7819 | 61.0107 | 122.731 | 122.8546 | -0.1236 | 122.8546 | 60.9283 | -0.17853 | 122.8546 | -0.1236 | 60.9283 | 122.731 | 122.8546 | -123.0515 | -123.0286
497.7812 | 123.1934 | -60.8826 | 61.9217 | 0.41557 | -0.0020208 | -0.0060027 | 0.002634 | 0.065659 | -0.0035141 | 0.068693 | -60.9924 | 61.9766 | -61.0657 | -61.0931 | 61.8393 | 0.050354 | -0.1831 | 0.091553 | 61.9583 | -61.1252 | -0.18311 | 0.054932 | -0.10986 | -0.21057 | -0.082398 | -0.24262 | 0.036621 | 0.073242 | 60.6995 | 60.9741 | 122.7219 | 122.8592 | -0.10986 | 122.8409 | 60.9329 | -0.24262 | 122.8592 | -0.10986 | 60.9329 | 122.7219 | 122.8409 | -122.9874 | -123.0469
498.7812 | 123.1476 | -60.8963 | 61.9629 | 0.1638 | -0.004798 | -0.0040801 | -0.0016386 | 0.063096 | -0.0033005 | 0.070188 | -61.0611 | 61.972 | -61.0977 | -61.1481 | 61.821 | 0.027466 | -0.068665 | 0.10071 | 61.9675 | -61.0931 | -0.20142 | 0.009155 | -0.16479 | -0.25177 | -0.14191 | -0.19684 | 0.004577 | 0.036621 | 60.8276 | 60.997 | 122.7173 | 122.8683 | -0.16479 | 122.8638 | 60.9238 | -0.19684 | 122.8683 | -0.16479 | 60.9238 | 122.7173 | 122.8638 | -123.0606 | -123.056
499.7812 | 123.1979 | -60.8826 | 61.9492 | 0.15617 | -0.0026618 | -0.0042937 | 0.0028476 | 0.065659 | -0.0028731 | 0.068052 | -61.0382 | 61.9629 | -61.1298 | -61.1069 | 61.8393 | 0.036621 | -0.16479 | 0.10071 | 61.9171 | -61.1114 | -0.24719 | 0.013733 | -0.15564 | -0.22431 | -0.10986 | -0.22888 | -0.032044 | 0.091553 | 60.7178 | 60.9833 | 122.7219 | 122.8455 | -0.15564 | 122.7997 | 60.9192 | -0.22888 | 122.8455 | -0.15564 | 60.9192 | 122.7219 | 122.7997 | -123.0789 | -123.0606
500.7812 | 123.1522 | -60.8643 | 61.9537 | 0.2401 | -0.004798 | -0.0049347 | -0.00035676 | 0.065873 | -0.0054367 | 0.067838 | -61.0336 | 61.9583 | -61.0977 | -61.1389 | 61.821 | 0.036621 | -0.13275 | 0.11444 | 61.9492 | -61.1069 | -0.23346 | 0.004578 | -0.16937 | -0.27466 | -0.13275 | -0.24262 | -0.004577 | 0.064087 | 60.7315 | 60.9787 | 122.6852 | 122.8226 | -0.16937 | 122.8134 | 60.9009 | -0.24262 | 122.8226 | -0.16937 | 60.9009 | 122.6852 | 122.8134 | -123.0515 | -123.0606
501.7812 | 123.2117 | -60.878 | 61.9537 | 0.24773 | -0.005866 | 0.0021149 | 0.0017794 | 0.064164 | -0.0050095 | 0.067411 | -61.0336 | 61.9537 | -61.0794 | -61.0703 | 61.8668 | 0.064087 | -0.15564 | 0.12817 | 61.9263 | -61.1114 | -0.20142 | 0 | -0.15564 | -0.19226 | -0.086975 | -0.23346 | -0.027465 | 0.045777 | 60.7224 | 61.0062 | 122.7448 | 122.8317 | -0.15564 | 122.8043 | 60.9421 | -0.23346 | 122.8317 | -0.15564 | 60.9421 | 122.7448 | 122.8043 | -123.0331 | -123.0652
502.7812 | 123.0423 | -60.91 | 62.0041 | 0.13329 | -0.0043708 | -0.0025847 | 0.0073336 | 0.063737 | -0.0035141 | 0.068265 | -61.0382 | 62.0819 | -61.084 | -61.1801 | 61.7569 | -0.045776 | 0.022888 | -0.009155 | 61.9904 | -61.1847 | -0.17395 | 0.07782 | -0.12817 | -0.27008 | -0.24719 | -0.27466 | -0.013733 | 0.045776 | 60.9329 | 60.9009 | 122.6669 | 122.9919 | -0.12817 | 122.9004 | 60.8643 | -0.27466 | 122.9919 | -0.12817 | 60.8643 | 122.6669 | 122.9004 | -123.0881 | -123.1888
503.7812 | 123.143 | -60.8871 | 61.972 | 0.18669 | -0.0041572 | -0.0066437 | -0.00014316 | 0.065873 | -0.0026595 | 0.069974 | -60.997 | 61.9766 | -61.0931 | -61.1252 | 61.8393 | 0.041199 | -0.15106 | 0.10529 | 61.9766 | -61.0977 | -0.20599 | 0.004578 | -0.10986 | -0.23804 | -0.13275 | -0.21057 | 0.004578 | 0.096131 | 60.7361 | 60.9924 | 122.7264 | 122.8638 | -0.10986 | 122.8638 | 60.9283 | -0.21057 | 122.8638 | -0.10986 | 60.9283 | 122.7264 | 122.8638 | -123.0652 | -123.0698
504.7812 | 123.1934 | -60.8643 | 61.9675 | 0.23247 | -0.0037298 | 0.0016877 | 0.0024202 | 0.065018 | -0.0037277 | 0.068906 | -60.9833 | 61.9812 | -61.0794 | -61.0153 | 61.8896 | 0.064087 | -0.13275 | 0.13733 | 61.9629 | -61.1114 | -0.21515 | 0.013733 | -0.11902 | -0.15106 | -0.07782 | -0.24719 | -0.004577 | 0.096131 | 60.7315 | 61.0016 | 122.7539 | 122.8455 | -0.11902 | 122.8271 | 60.9283 | -0.24719 | 122.8455 | -0.11902 | 60.9283 | 122.7539 | 122.8271 | -123.0469 | -123.0789
505.7812 | 123.0881 | -60.9329 | 61.9904 | 0.19432 | -0.0011664 | -0.0057891 | 0.0047702 | 0.063523 | -0.0039413 | 0.068479 | -61.0565 | 62.027 | -61.116 | -61.1618 | 61.7615 | -0.045776 | -0.045776 | -0.004578 | 61.9766 | -61.171 | -0.18311 | 0.036622 | -0.1236 | -0.22888 | -0.22888 | -0.23804 | -0.013732 | 0.059509 | 60.8871 | 60.9283 | 122.6944 | 122.9599 | -0.1236 | 122.9095 | 60.8871 | -0.23804 | 122.9599 | -0.1236 | 60.8871 | 122.6944 | 122.9095 | -123.1064 | -123.1613
506.7812 | 123.0469 | -60.9283 | 61.9354 | 0.21721 | -0.0039434 | -0.0032257 | 0.0032748 | 0.064591 | -0.0028731 | 0.070615 | -61.0931 | 62.059 | -61.1343 | -61.1801 | 61.7523 | -0.054932 | 0 | -0.013733 | 61.9858 | -61.1572 | -0.20599 | 0.1236 | -0.16479 | -0.25177 | -0.18311 | -0.22888 | 0.050354 | 0.041198 | 60.9283 | 60.9146 | 122.6807 | 122.9874 | -0.16479 | 122.9141 | 60.8734 | -0.22888 | 122.9874 | -0.16479 | 60.8734 | 122.6807 | 122.9141 | -123.0698 | -123.0927
507.7812 | 123.1979 | -60.91 | 61.9492 | 0.20958 | -0.0028754 | -0.0057891 | -0.0012112 | 0.065446 | -0.0020187 | 0.068052 | -61.0153 | 61.9904 | -61.0931 | -61.1206 | 61.8668 | 0.041199 | -0.16022 | 0.10529 | 61.9492 | -61.1069 | -0.18311 | 0.041198 | -0.10529 | -0.21057 | -0.082398 | -0.19684 | 0 | 0.07782 | 60.7498 | 61.0153 | 122.7768 | 122.9004 | -0.10529 | 122.8592 | 60.9512 | -0.19684 | 122.9004 | -0.10529 | 60.9512 | 122.7768 | 122.8592 | -123.0423 | -123.056
508.7812 | 123.1705 | -60.878 | 61.9858 | 0.011215 | -0.0054388 | -0.0083527 | -0.0037748 | 0.063737 | -0.0035141 | 0.069547 | -61.0245 | 61.9675 | -61.0794 | -61.084 | 61.8713 | 0.11902 | -0.064087 | 0.17395 | 61.9583 | -61.116 | -0.20142 | -0.018311 | -0.14648 | -0.20599 | -0.11444 | -0.23804 | -0.027466 | 0.054932 | 60.8139 | 61.0519 | 122.7493 | 122.8455 | -0.14648 | 122.8363 | 60.997 | -0.23804 | 122.8455 | -0.14648 | 60.997 | 122.7493 | 122.8363 | -123.0652 | -123.1018
509.7812 | 123.1384 | -60.8826 | 61.9766 | 0.1638 | -0.0067206 | -0.0036529 | -0.001425 | 0.061173 | -0.0015915 | 0.070402 | -61.0657 | 61.9583 | -61.0931 | -61.1298 | 61.8164 | 0.018311 | -0.086975 | 0.091553 | 61.94 | -61.1069 | -0.21057 | -0.018311 | -0.18311 | -0.24719 | -0.16022 | -0.22431 | -0.036622 | 0.027466 | 60.7956 | 60.9741 | 122.699 | 122.8409 | -0.18311 | 122.8226 | 60.9009 | -0.22431 | 122.8409 | -0.18311 | 60.9009 | 122.699 | 122.8226 | -123.0698 | -123.0835
510.7812 | 123.0972 | -60.9283 | 61.9995 | 0.27061 | -0.0037298 | -0.00023494 | 0.004343 | 0.064805 | -0.0045821 | 0.068479 | -61.0336 | 62.0819 | -61.0886 | -61.1755 | 61.7615 | -0.054932 | -0.022888 | 0.013733 | 61.9812 | -61.1755 | -0.16022 | 0.082397 | -0.10529 | -0.24719 | -0.23804 | -0.24719 | -0.018311 | 0.054932 | 60.9055 | 60.9421 | 122.6898 | 123.0103 | -0.10529 | 122.9095 | 60.8734 | -0.24719 | 123.0103 | -0.10529 | 60.8734 | 122.6898 | 122.9095 | -123.0881 | -123.175
511.7812 | 123.1796 | -60.8551 | 61.9675 | 0.034104 | -0.0039434 | -0.0027985 | -0.0033476 | 0.062241 | -0.0037277 | 0.06912 | -61.0474 | 61.972 | -61.1114 | -61.0931 | 61.8668 | 0.086975 | -0.059509 | 0.15106 | 61.9629 | -61.0794 | -0.25635 | 0.004578 | -0.19226 | -0.23804 | -0.10071 | -0.2243 | -0.004577 | 0.064087 | 60.7956 | 61.0062 | 122.7219 | 122.8271 | -0.19226 | 122.818 | 60.9421 | -0.2243 | 122.8271 | -0.19226 | 60.9421 | 122.7219 | 122.818 | -123.0789 | -123.0469
512.7812 | 123.1476 | -60.8963 | 61.9812 | 0.27061 | -0.00095279 | 0.0010467 | 0.0051974 | 0.065232 | -0.0039413 | 0.06912 | -61.0336 | 61.9949 | -61.1069 | -61.1526 | 61.7844 | -0.027466 | -0.10071 | 0.032043 | 61.9766 | -61.1252 | -0.21057 | 0.013733 | -0.13733 | -0.25635 | -0.19684 | -0.22888 | -0.004577 | 0.073243 | 60.7956 | 60.9283 | 122.6807 | 122.8912 | -0.13733 | 122.8729 | 60.8688 | -0.22888 | 122.8912 | -0.13733 | 60.8688 | 122.6807 | 122.8729 | -123.0881 | -123.1064
513.7812 | 123.175 | -60.8871 | 61.9812 | 0.14854 | -0.0041572 | -0.0032257 | -0.00099756 | 0.062882 | -0.0026595 | 0.066343 | -61.0611 | 61.9675 | -61.1023 | -61.1252 | 61.821 | 0.032043 | -0.068665 | 0.091553 | 61.9446 | -61.1114 | -0.21515 | -0.013733 | -0.17395 | -0.23804 | -0.16022 | -0.2243 | -0.036621 | 0.041199 | 60.8185 | 60.9787 | 122.7081 | 122.8546 | -0.17395 | 122.8317 | 60.9192 | -0.2243 | 122.8546 | -0.17395 | 60.9192 | 122.7081 | 122.8317 | -123.0835 | -123.0927
514.7812 | 123.0972 | -60.91 | 62.027 | 0.27824 | -0.003089 | -0.0017303 | 0.008829 | 0.065446 | -0.0035141 | 0.069974 | -61.0748 | 62.0773 | -61.1069 | -61.116 | 61.8027 | -0.027466 | -0.004578 | 0.041199 | 61.9949 | -61.1526 | -0.19684 | 0.050354 | -0.16479 | -0.20599 | -0.22431 | -0.24261 | -0.032044 | 0.032044 | 60.9055 | 60.9512 | 122.7127 | 122.9874 | -0.16479 | 122.905 | 60.8826 | -0.24261 | 122.9874 | -0.16479 | 60.8826 | 122.7127 | 122.905 | -123.1339 | -123.1796
515.7812 | 123.175 | -60.878 | 61.9583 | 0.20195 | -0.003089 | -0.0015167 | 0.0022066 | 0.064164 | -0.0050095 | 0.070188 | -61.0107 | 61.9766 | -61.0748 | -61.1206 | 61.8484 | 0.032043 | -0.14191 | 0.10071 | 61.9308 | -61.116 | -0.19684 | 0.018311 | -0.13275 | -0.24261 | -0.10986 | -0.23804 | -0.027466 | 0.064087 | 60.7361 | 60.9787 | 122.7264 | 122.8546 | -0.13275 | 122.8088 | 60.91 | -0.23804 | 122.8546 | -0.13275 | 60.91 | 122.7264 | 122.8088 | -123.0331 | -123.0743
516.7812 | 123.1979 | -60.878 | 61.9675 | 0.25536 | -0.0056524 | -0.0045075 | 0.002634 | 0.065446 | -0.0052231 | 0.067411 | -60.9924 | 61.9675 | -61.0748 | -61.0016 | 61.9583 | 0.11902 | -0.15564 | 0.14191 | 61.9583 | -61.084 | -0.19684 | 0 | -0.11444 | -0.1236 | -0.009155 | -0.20599 | -0.009155 | 0.082397 | 60.7224 | 61.0199 | 122.8363 | 122.8455 | -0.11444 | 122.8363 | 60.997 | -0.20599 | 122.8455 | -0.11444 | 60.997 | 122.8363 | 122.8363 | -123.0423 | -123.0515
517.7812 | 123.1613 | -60.8826 | 61.9949 | 0.072251 | -0.0028754 | -0.0021575 | -0.00078396 | 0.063096 | -0.0013779 | 0.069761 | -61.0428 | 61.9629 | -61.1023 | -61.1206 | 61.8027 | 0.027466 | -0.082397 | 0.091553 | 61.9629 | -61.116 | -0.21973 | -0.032043 | -0.16022 | -0.23804 | -0.19226 | -0.23346 | -0.032043 | 0.059509 | 60.8002 | 60.9741 | 122.6852 | 122.8455 | -0.16022 | 122.8455 | 60.91 | -0.23346 | 122.8455 | -0.16022 | 60.91 | 122.6852 | 122.8455 | -123.0972 | -123.111
518.7812 | 123.143 | -60.8963 | 61.9995 | 0.072251 | -0.0022346 | -0.0072845 | -0.0012112 | 0.062882 | -0.0028731 | 0.070402 | -61.0565 | 61.9904 | -61.084 | -61.1618 | 61.8576 | 0.032043 | -0.064087 | 0.10986 | 61.9446 | -61.116 | -0.18768 | -0.009156 | -0.16022 | -0.2655 | -0.14191 | -0.21973 | -0.054932 | 0.027465 | 60.8322 | 61.0062 | 122.7539 | 122.8867 | -0.16022 | 122.8409 | 60.9283 | -0.21973 | 122.8867 | -0.16022 | 60.9283 | 122.7539 | 122.8409 | -123.0835 | -123.1155
519.7812 | 123.1476 | -60.9146 | 61.9537 | 0.27061 | -0.0037298 | -0.0019439 | 0.0066928 | 0.062241 | -0.0041549 | 0.069333 | -60.9879 | 61.9812 | -61.0703 | -61.0657 | 61.8622 | 0.036621 | -0.19684 | 0.11444 | 61.908 | -61.1114 | -0.15564 | 0.027466 | -0.073242 | -0.15106 | -0.091552 | -0.19684 | -0.045776 | 0.082397 | 60.7178 | 61.0291 | 122.7768 | 122.8958 | -0.073242 | 122.8226 | 60.9512 | -0.19684 | 122.8958 | -0.073242 | 60.9512 | 122.7768 | 122.8226 | -123.024 | -123.0652
520.7812 | 123.1659 | -60.8963 | 61.972 | 0.27824 | -0.0028754 | 0.00019226 | 0.003702 | 0.06395 | -0.0024459 | 0.069547 | -61.0245 | 61.9858 | -61.0886 | -61.116 | 61.8118 | 0.018311 | -0.14191 | 0.07782 | 61.9629 | -61.116 | -0.19226 | 0.013733 | -0.12817 | -0.21973 | -0.16022 | -0.21973 | -0.009155 | 0.064087 | 60.7544 | 60.9741 | 122.7081 | 122.8821 | -0.12817 | 122.8592 | 60.9146 | -0.21973 | 122.8821 | -0.12817 | 60.9146 | 122.7081 | 122.8592 | -123.0606 | -123.0881
521.7812 | 123.1796 | -60.9146 | 61.9446 | 0.26299 | -0.0052252 | -0.0027985 | 0.0030612 | 0.064378 | -0.0015915 | 0.070615 | -60.9879 | 61.9766 | -61.0886 | -61.084 | 61.8668 | 0.041199 | -0.19226 | 0.11902 | 61.9171 | -61.116 | -0.17395 | 0.032044 | -0.073242 | -0.16937 | -0.07782 | -0.20142 | -0.027466 | 0.10071 | 60.7224 | 61.0336 | 122.7814 | 122.8912 | -0.073242 | 122.8317 | 60.9558 | -0.20142 | 122.8912 | -0.073242 | 60.9558 | 122.7814 | 122.8317 | -123.0331 | -123.0606
522.7812 | 123.175 | -60.878 | 61.9812 | 0.20195 | -0.003089 | -0.0066437 | -0.00099756 | 0.063096 | -0.00030975 | 0.069547 | -61.0565 | 61.9629 | -61.0886 | -61.1526 | 61.8118 | 0.022888 | -0.091553 | 0.09613 | 61.9171 | -61.1206 | -0.21057 | -0.01831 | -0.17853 | -0.27466 | -0.16937 | -0.24261 | -0.064087 | 0.032043 | 60.7864 | 60.9741 | 122.6898 | 122.8409 | -0.17853 | 122.7951 | 60.9009 | -0.24261 | 122.8409 | -0.17853 | 60.9009 | 122.6898 | 122.7951 | -123.0698 | -123.1018
523.7812 | 123.1888 | -60.8597 | 61.9904 | -0.13374 | -0.0033026 | -0.0094207 | 0.0032748 | 0.060746 | -0.0035141 | 0.069974 | -61.0336 | 62.0178 | -61.0474 | -61.0199 | 61.9217 | 0.1236 | -0.068665 | 0.22888 | 61.9446 | -61.1023 | -0.18768 | 0.027466 | -0.17395 | -0.16022 | -0.068664 | -0.24262 | -0.045776 | 0.013733 | 60.791 | 61.0886 | 122.7814 | 122.8775 | -0.17395 | 122.8043 | 60.9833 | -0.24262 | 122.8775 | -0.17395 | 60.9833 | 122.7814 | 122.8043 | -123.0377 | -123.0927
524.7812 | 123.1796 | -60.8963 | 61.9537 | 0.27824 | -0.0052252 | -0.0036529 | 0.0022066 | 0.060105 | -0.0045821 | 0.06912 | -60.997 | 61.9949 | -61.1023 | -61.0886 | 61.8347 | 0.050354 | -0.16937 | 0.10529 | 61.908 | -61.1298 | -0.20599 | 0.041199 | -0.10071 | -0.19226 | -0.11902 | -0.23346 | -0.045776 | 0.10529 | 60.7269 | 61.0016 | 122.731 | 122.8912 | -0.10071 | 122.8043 | 60.9467 | -0.23346 | 122.8912 | -0.10071 | 60.9467 | 122.731 | 122.8043 | -123.056 | -123.0835
525.7812 | 123.1476 | -60.8917 | 61.9812 | 0.087509 | -0.0054388 | -0.0023711 | 0.0015658 | 0.061814 | -0.0033005 | 0.070402 | -61.0519 | 61.9858 | -61.1023 | -61.1298 | 61.8164 | 0.054932 | 0.068665 | 0.1236 | 61.9675 | -61.0703 | -0.21057 | 0.004578 | -0.16022 | -0.23804 | -0.16479 | -0.17853 | -0.013733 | 0.050354 | 60.9604 | 61.0153 | 122.7081 | 122.8775 | -0.16022 | 122.8592 | 60.9467 | -0.17853 | 122.8775 | -0.16022 | 60.9467 | 122.7081 | 122.8592 | -123.0835 | -123.0515
526.7812 | 123.2071 | -60.8597 | 61.972 | 0.2935 | -0.0054388 | -0.0032257 | 0.0045566 | 0.059891 | -0.0041549 | 0.066984 | -60.9833 | 61.9583 | -61.0794 | -61.0748 | 61.853 | 0.050354 | -0.21515 | 0.11444 | 61.9354 | -61.1252 | -0.21973 | -0.013733 | -0.1236 | -0.21515 | -0.11902 | -0.2655 | -0.036621 | 0.096131 | 60.6445 | 60.9741 | 122.7127 | 122.818 | -0.1236 | 122.7951 | 60.91 | -0.2655 | 122.818 | -0.1236 | 60.91 | 122.7127 | 122.7951 | -123.0515 | -123.0972
527.7812 | 123.175 | -60.8826 | 61.9446 | 0.2401 | -0.0050116 | -0.00066214 | 0.002634 | 0.064164 | -0.00030975 | 0.067411 | -61.0062 | 61.9583 | -61.0703 | -61.0931 | 61.8301 | 0.059509 | -0.16022 | 0.11444 | 61.9125 | -61.0931 | -0.18768 | 0.013733 | -0.1236 | -0.21057 | -0.11444 | -0.21057 | -0.032043 | 0.064086 | 60.7224 | 60.997 | 122.7127 | 122.8409 | -0.1236 | 122.7951 | 60.9421 | -0.21057 | 122.8409 | -0.1236 | 60.9421 | 122.7127 | 122.7951 | -123.0148 | -123.0377
528.7812 | 123.2025 | -60.8826 | 62.0087 | -0.15663 | -0.004798 | -0.0049347 | -0.0029202 | 0.060105 | -0.0035141 | 0.069974 | -60.9695 | 61.9995 | -61.0474 | -61.116 | 61.8759 | 0.10529 | -0.022888 | 0.20142 | 61.9446 | -61.0931 | -0.16479 | -0.009155 | -0.086975 | -0.23346 | -0.13275 | -0.21057 | -0.064087 | 0.07782 | 60.8597 | 61.084 | 122.7585 | 122.8821 | -0.086975 | 122.8271 | 60.9879 | -0.21057 | 122.8821 | -0.086975 | 60.9879 | 122.7585 | 122.8271 | -123.056 | -123.1018
529.7812 | 123.1705 | -60.8826 | 61.9812 | 0.064621 | -0.004798 | -0.0083527 | 0.00028404 | 0.062028 | -0.0047957 | 0.066984 | -61.0565 | 61.9949 | -61.0931 | -61.1298 | 61.821 | 0.050354 | 0.086975 | 0.13275 | 61.9812 | -61.0657 | -0.21057 | 0.013733 | -0.17395 | -0.24719 | -0.16022 | -0.18311 | 0 | 0.036621 | 60.9695 | 61.0153 | 122.7036 | 122.8775 | -0.17395 | 122.8638 | 60.9329 | -0.18311 | 122.8775 | -0.17395 | 60.9329 | 122.7036 | 122.8638 | -123.0743 | -123.0469
530.7812 | 123.1338 | -60.8734 | 61.9904 | 0.041733 | -0.0043708 | -0.0060027 | 0.00028404 | 0.060319 | -0.0028731 | 0.068479 | -61.0519 | 61.9858 | -61.0794 | -61.1252 | 61.8805 | 0.11444 | -0.064087 | 0.11444 | 61.9583 | -61.1023 | -0.20599 | -0.004577 | -0.17853 | -0.25177 | -0.10986 | -0.22888 | -0.032043 | 0.027466 | 60.8093 | 60.9879 | 122.7539 | 122.8592 | -0.17853 | 122.8317 | 60.9879 | -0.22888 | 122.8592 | -0.17853 | 60.9879 | 122.7539 | 122.8317 | -123.0698 | -123.0927
531.7812 | 123.1796 | -60.9009 | 61.9812 | 0.07988 | -0.005866 | -0.0051483 | 0.00049764 | 0.062669 | -0.0041549 | 0.068479 | -61.0291 | 61.9583 | -61.1114 | -61.0794 | 61.94 | 0.10071 | -0.082397 | 0.13275 | 61.9583 | -61.1069 | -0.21057 | -0.022888 | -0.12817 | -0.17853 | -0.041199 | -0.20599 | -0.022888 | 0.082397 | 60.8185 | 61.0336 | 122.8409 | 122.8592 | -0.12817 | 122.8592 | 61.0016 | -0.20599 | 122.8592 | -0.12817 | 61.0016 | 122.8409 | 122.8592 | -123.0927 | -123.0881
532.7812 | 123.2025 | -60.8231 | 61.9904 | -0.16426 | -0.0052252 | -0.0051483 | 0.00092504 | 0.062882 | -0.0041549 | 0.067838 | -60.9604 | 61.9583 | -61.0519 | -61.0062 | 61.9171 | 0.16479 | -0.082397 | 0.26093 | 61.9858 | -61.0611 | -0.22888 | -0.032043 | -0.13733 | -0.18311 | -0.073242 | -0.23804 | -0.004577 | 0.091553 | 60.7407 | 61.084 | 122.7402 | 122.7814 | -0.13733 | 122.8088 | 60.9879 | -0.23804 | 122.7814 | -0.13733 | 60.9879 | 122.7402 | 122.8088 | -123.0423 | -123.0515
533.7969 | 123.1384 | -60.8734 | 61.9812 | 0.11803 | -0.004798 | -0.0036529 | 0.0015658 | 0.062241 | -0.0028731 | 0.06912 | -61.0474 | 61.9583 | -61.1114 | -61.1114 | 61.8164 | 0.041199 | -0.086975 | 0.091553 | 61.972 | -61.0794 | -0.23804 | -0.022888 | -0.17395 | -0.23804 | -0.16479 | -0.20599 | -0.009155 | 0.064087 | 60.7864 | 60.965 | 122.6898 | 122.8317 | -0.17395 | 122.8455 | 60.9146 | -0.20599 | 122.8317 | -0.17395 | 60.9146 | 122.6898 | 122.8455 | -123.0927 | -123.0606
534.7812 | 123.2346 | -60.8917 | 61.972 | 0.24773 | -0.0022346 | -0.0049347 | 0.0045566 | 0.063523 | -0.0037277 | 0.068693 | -60.9741 | 61.972 | -61.0931 | -61.0748 | 61.853 | 0.054932 | -0.20599 | -0.059509 | 61.8942 | -61.1481 | -0.20142 | 0 | -0.082397 | -0.1831 | -0.11902 | -0.25635 | -0.07782 | 0.11902 | 60.6857 | 60.8322 | 122.7448 | 122.8638 | -0.082397 | 122.786 | 60.9467 | -0.25635 | 122.8638 | -0.082397 | 60.9467 | 122.7448 | 122.786 | -123.0652 | -123.1201
535.7812 | 123.2254 | -60.8826 | 61.9766 | -0.072708 | -0.0054388 | -0.0068573 | 0.0015658 | 0.062028 | -0.0033005 | 0.069547 | -60.9558 | 61.9675 | -61.0657 | -61.0062 | 61.9308 | 0.15106 | -0.050354 | 0.24719 | 61.9537 | -61.0931 | -0.18311 | -0.009156 | -0.073243 | -0.1236 | -0.045777 | -0.21057 | -0.022889 | 0.10986 | 60.8322 | 61.1298 | 122.8134 | 122.85 | -0.073243 | 122.8363 | 61.0336 | -0.21057 | 122.85 | -0.073243 | 61.0336 | 122.8134 | 122.8363 | -123.0423 | -123.0698
536.7812 | 123.143 | -60.8551 | 61.9995 | 0.064621 | -0.0037298 | -0.0042937 | 0.00028404 | 0.058396 | -0.0039413 | 0.068906 | -60.9512 | 62.0041 | -61.0703 | -61.1069 | 61.8439 | 0.059509 | -0.073242 | 0.1236 | 61.94 | -61.1114 | -0.21515 | 0.004577 | -0.09613 | -0.25177 | -0.15564 | -0.25635 | -0.05951 | 0.11902 | 60.7819 | 60.9787 | 122.699 | 122.8592 | -0.09613 | 122.7951 | 60.9146 | -0.25635 | 122.8592 | -0.09613 | 60.9146 | 122.699 | 122.7951 | -123.0698 | -123.111
537.7812 | 123.1659 | -60.878 | 61.972 | 0.17906 | -0.0024482 | -0.0047211 | 0.0028476 | 0.063096 | -0.0024459 | 0.069547 | -61.0153 | 61.9537 | -61.0886 | -61.0794 | 61.8576 | 0.045776 | -0.16022 | 0.10986 | 61.9217 | -61.1206 | -0.21057 | -0.018311 | -0.13733 | -0.20142 | -0.11444 | -0.24261 | -0.050354 | 0.073242 | 60.7178 | 60.9879 | 122.7356 | 122.8317 | -0.13733 | 122.7997 | 60.9238 | -0.24261 | 122.8317 | -0.13733 | 60.9238 | 122.7356 | 122.7997 | -123.0606 | -123.0927
538.7812 | 123.1338 | -60.9055 | 62.0499 | 0.018845 | -0.0018072 | -0.0038665 | 0.0056246 | 0.062669 | -0.0026595 | 0.070402 | -60.9741 | 62.0819 | -61.0794 | -61.0474 | 61.7889 | -0.027466 | 0.027466 | 0.10529 | 61.9492 | -61.1435 | -0.17395 | 0.032043 | -0.068664 | -0.14191 | -0.26093 | -0.23804 | -0.10071 | 0.10529 | 60.9329 | 61.0107 | 122.6944 | 122.9874 | -0.068664 | 122.8546 | 60.878 | -0.23804 | 122.9874 | -0.068664 | 60.878 | 122.6944 | 122.8546 | -123.1293 | -123.1934
539.7812 | 123.1613 | -60.9009 | 62.0178 | 0.67497 | -0.0037298 | -0.0062163 | -0.0027066 | 0.063523 | -0.0030869 | 0.06912 | -61.0199 | 61.9858 | -61.0977 | -61.116 | 61.8301 | 0.045776 | -0.068665 | 0.14191 | 61.9812 | -61.0611 | -0.19684 | -0.032043 | -0.11902 | -0.21515 | -0.18768 | -0.16022 | -0.036621 | 0.07782 | 60.8322 | 61.0428 | 122.731 | 122.8867 | -0.11902 | 122.8821 | 60.9467 | -0.16022 | 122.8867 | -0.11902 | 60.9467 | 122.731 | 122.8821 | -123.1155 | -123.0789
540.7812 | 123.1522 | -60.8871 | 61.9766 | 0.20958 | -0.0037298 | -0.0034393 | 0.0030612 | 0.065232 | -0.0033005 | 0.068906 | -61.0107 | 61.9537 | -61.0886 | -61.0977 | 61.8347 | 0.022888 | -0.15106 | 0.10529 | 61.9125 | -61.116 | -0.20142 | -0.022889 | -0.1236 | -0.21057 | -0.14191 | -0.22888 | -0.064087 | 0.07782 | 60.7361 | 60.9924 | 122.7219 | 122.8409 | -0.1236 | 122.7997 | 60.91 | -0.22888 | 122.8409 | -0.1236 | 60.91 | 122.7219 | 122.7997 | -123.0652 | -123.0927
541.7812 | 123.2071 | -60.8551 | 61.9583 | -0.0040434 | -0.0071478 | -0.0064301 | -0.001425 | 0.062455 | -0.0022323 | 0.069974 | -60.997 | 61.9858 | -61.0703 | -61.0428 | 61.8942 | 0.12817 | -0.064087 | 0.20599 | 61.9583 | -61.0931 | -0.21515 | 0.027466 | -0.14191 | -0.18768 | -0.064087 | -0.23804 | 0 | 0.073242 | 60.791 | 61.0611 | 122.7493 | 122.8409 | -0.14191 | 122.8134 | 60.9833 | -0.23804 | 122.8409 | -0.14191 | 60.9833 | 122.7493 | 122.8134 | -123.0286 | -123.0515
542.7812 | 123.1979 | -60.8871 | 61.972 | 0.2401 | -0.0024482 | -0.00087594 | 0.0034884 | 0.061814 | -0.0039413 | 0.070829 | -61.0931 | 61.9583 | -61.0794 | -61.0657 | 61.8713 | 0.073242 | -0.1831 | 0.10529 | 61.9171 | -61.1206 | -0.19226 | -0.013733 | -0.20599 | -0.17853 | -0.10071 | -0.23346 | -0.054932 | -0.013733 | 60.704 | 60.9924 | 122.7585 | 122.8455 | -0.20599 | 122.8043 | 60.9604 | -0.23346 | 122.8455 | -0.20599 | 60.9604 | 122.7585 | 122.8043 | -123.0515 | -123.0927
543.7812 | 123.0927 | -60.9238 | 62.0178 | 0.041733 | -0.00073919 | 0.00083306 | 0.0081882 | 0.064378 | -0.0037277 | 0.067838 | -60.997 | 62.0865 | -61.0748 | -61.1252 | 61.7889 | -0.009155 | 0.018311 | 0.041199 | 61.9812 | -61.1618 | -0.15106 | 0.068665 | -0.073242 | -0.20142 | -0.22888 | -0.23804 | -0.036621 | 0.07782 | 60.9421 | 60.965 | 122.7127 | 123.0103 | -0.073242 | 122.905 | 60.9146 | -0.23804 | 123.0103 | -0.073242 | 60.9146 | 122.7127 | 122.905 | -123.0927 | -123.1796
544.7812 | 123.1567 | -60.9009 | 61.9995 | 0.018845 | -0.0037298 | -0.0047211 | -0.003134 | 0.062882 | -0.0018051 | 0.067838 | -61.0519 | 61.9537 | -61.1023 | -61.1114 | 61.853 | 0.07782 | -0.050354 | 0.16479 | 61.9537 | -61.0611 | -0.20142 | -0.045777 | -0.15106 | -0.21057 | -0.14649 | -0.16022 | -0.045777 | 0.050354 | 60.8505 | 61.0657 | 122.7539 | 122.8546 | -0.15106 | 122.8546 | 60.9787 | -0.16022 | 122.8546 | -0.15106 | 60.9787 | 122.7539 | 122.8546 | -123.1018 | -123.0606
545.7812 | 123.1705 | -60.8688 | 62.0087 | -0.14137 | -0.005866 | -0.0032257 | 0.0015658 | 0.063096 | -0.0045821 | 0.067411 | -60.9741 | 62.027 | -61.0794 | -61.0519 | 61.908 | 0.13275 | 0.041199 | 0.2243 | 61.9492 | -61.084 | -0.21057 | 0.018311 | -0.10529 | -0.18311 | -0.10071 | -0.21515 | -0.059509 | 0.10529 | 60.91 | 61.0931 | 122.7768 | 122.8958 | -0.10529 | 122.818 | 61.0016 | -0.21515 | 122.8958 | -0.10529 | 61.0016 | 122.7768 | 122.818 | -123.0881 | -123.0927
546.7812 | 123.1705 | -60.8734 | 62.027 | -0.16426 | -0.0052252 | -0.0064301 | 0.0024202 | 0.061387 | -0.0037277 | 0.06912 | -60.9741 | 61.9995 | -61.1023 | -61.0565 | 61.8896 | 0.13733 | 0.059509 | 0.21973 | 61.9904 | -61.084 | -0.22888 | -0.027466 | -0.10071 | -0.18311 | -0.13733 | -0.21057 | -0.036622 | 0.12817 | 60.9329 | 61.0931 | 122.7631 | 122.8729 | -0.10071 | 122.8638 | 61.0107 | -0.21057 | 122.8729 | -0.10071 | 61.0107 | 122.7631 | 122.8638 | -123.1293 | -123.111
547.7812 | 123.175 | -60.8734 | 61.9858 | -0.0040434 | -0.0067206 | -0.0027985 | -0.0016386 | 0.062028 | -0.0024459 | 0.067624 | -61.0245 | 61.9583 | -61.0931 | -61.0794 | 61.8759 | 0.10986 | -0.050354 | 0.15564 | 61.9583 | -61.084 | -0.21973 | -0.027466 | -0.15106 | -0.20599 | -0.10986 | -0.21057 | -0.027466 | 0.068665 | 60.8231 | 61.0291 | 122.7493 | 122.8317 | -0.15106 | 122.8317 | 60.9833 | -0.21057 | 122.8317 | -0.15106 | 60.9833 | 122.7493 | 122.8317 | -123.0789 | -123.0698
548.7812 | 123.0698 | -60.9192 | 62.0132 | 0.12566 | -0.0018072 | -0.0042937 | 0.0069064 | 0.062669 | -0.0030869 | 0.068052 | -61.0474 | 62.059 | -61.1298 | -61.1755 | 61.7615 | -0.050354 | 0.054932 | -0.018311 | 61.9812 | -61.1481 | -0.21057 | 0.045776 | -0.12817 | -0.25635 | -0.25177 | -0.22888 | -0.032044 | 0.082398 | 60.9741 | 60.9009 | 122.6807 | 122.9782 | -0.12817 | 122.9004 | 60.8688 | -0.22888 | 122.9782 | -0.12817 | 60.8688 | 122.6807 | 122.9004 | -123.143 | -123.1613
549.7812 | 123.1201 | -60.8826 | 62.0316 | -0.0040434 | -0.0041572 | -0.0045075 | 0.0079744 | 0.065232 | -0.0041549 | 0.068693 | -60.9787 | 62.0636 | -61.0886 | -61.0794 | 61.8439 | 0.068665 | -0.032043 | 0 | 61.9812 | -61.1252 | -0.20599 | 0.032044 | -0.096131 | -0.19684 | -0.18768 | -0.24262 | -0.050354 | 0.10986 | 60.8505 | 60.8826 | 122.7264 | 122.9462 | -0.096131 | 122.8638 | 60.9512 | -0.24262 | 122.9462 | -0.096131 | 60.9512 | 122.7264 | 122.8638 | -123.1201 | -123.1567
550.7812 | 123.2071 | -60.878 | 61.9949 | 0.011215 | -0.0050116 | -0.0038665 | -0.0020658 | 0.063737 | -0.0039413 | 0.070615 | -61.0199 | 61.9904 | -61.0931 | -61.0703 | 61.8942 | 0.1236 | -0.059509 | 0.21057 | 61.9766 | -61.0748 | -0.21515 | -0.004578 | -0.14191 | -0.19226 | -0.10071 | -0.19684 | -0.01831 | 0.073243 | 60.8185 | 61.0886 | 122.7722 | 122.8683 | -0.14191 | 122.8546 | 61.0016 | -0.19684 | 122.8683 | -0.14191 | 61.0016 | 122.7722 | 122.8546 | -123.0881 | -123.0698
551.7812 | 123.1705 | -60.8688 | 61.9812 | -0.30159 | -0.0041572 | -0.0013031 | -0.00057036 | 0.061814 | -0.0043685 | 0.068052 | -60.9695 | 62.0132 | -61.0794 | -61.0611 | 61.908 | 0.16022 | 0.013733 | 0.23346 | 61.9675 | -61.084 | -0.21057 | 0.032044 | -0.10071 | -0.19226 | -0.073242 | -0.21515 | -0.013733 | 0.10986 | 60.8826 | 61.1023 | 122.7768 | 122.8821 | -0.10071 | 122.8363 | 61.0291 | -0.21515 | 122.8821 | -0.10071 | 61.0291 | 122.7768 | 122.8363 | -123.0606 | -123.0652
552.7812 | 123.1796 | -60.8597 | 62.0132 | -0.15663 | -0.0050116 | -0.0081389 | 0.00071144 | 0.06096 | -0.0033005 | 0.068052 | -60.9604 | 61.9995 | -61.0611 | -61.0336 | 61.908 | 0.16479 | -0.050354 | 0.2655 | 61.9629 | -61.0657 | -0.20142 | -0.013733 | -0.10071 | -0.17395 | -0.10529 | -0.20599 | -0.050354 | 0.10071 | 60.8093 | 61.1252 | 122.7676 | 122.8592 | -0.10071 | 122.8226 | 61.0245 | -0.20599 | 122.8592 | -0.10071 | 61.0245 | 122.7676 | 122.8226 | -123.0743 | -123.0789
553.7812 | 123.1018 | -60.9192 | 62.0132 | -0.12611 | -0.00031179 | -0.0051483 | 0.0075472 | 0.065659 | -0.0020187 | 0.070615 | -61.0565 | 62.0728 | -61.0977 | -61.1618 | 61.7615 | -0.027466 | -0.009155 | -0.004578 | 61.9766 | -61.1618 | -0.17853 | 0.059509 | -0.13733 | -0.24261 | -0.25177 | -0.24261 | -0.036621 | 0.041198 | 60.91 | 60.9146 | 122.6807 | 122.9919 | -0.13733 | 122.8958 | 60.8917 | -0.24261 | 122.9919 | -0.13733 | 60.8917 | 122.6807 | 122.8958 | -123.111 | -123.175
554.7812 | 123.2071 | -60.8871 | 61.9812 | 0.026474 | -0.0050116 | -0.0077117 | -0.0020658 | 0.062455 | -0.0024459 | 0.070188 | -61.0565 | 61.9812 | -61.1206 | -61.1114 | 61.8622 | 0.07782 | -0.064087 | 0.16022 | 61.9629 | -61.084 | -0.23346 | 0 | -0.16937 | -0.2243 | -0.11902 | -0.19684 | -0.01831 | 0.064086 | 60.8231 | 61.0474 | 122.7493 | 122.8683 | -0.16937 | 122.85 | 60.965 | -0.19684 | 122.8683 | -0.16937 | 60.965 | 122.7493 | 122.85 | -123.1018 | -123.0652
555.7812 | 123.1796 | -60.8459 | 62.0407 | -0.19478 | -0.0041572 | -0.0010895 | -0.00014316 | 0.05861 | -0.0062911 | 0.068479 | -60.9604 | 62.0132 | -61.0611 | -61.0657 | 61.8713 | 0.13275 | 0.050354 | 0.21515 | 61.972 | -61.0977 | -0.21515 | -0.027465 | -0.11444 | -0.21973 | -0.16937 | -0.25177 | -0.068664 | 0.10071 | 60.8963 | 61.0611 | 122.7173 | 122.8592 | -0.11444 | 122.818 | 60.9787 | -0.25177 | 122.8592 | -0.11444 | 60.9787 | 122.7173 | 122.818 | -123.1018 | -123.1384
556.7812 | 123.1705 | -60.9421 | 62.0132 | 0.21721 | 0.00054261 | -0.0030121 | 0.0062656 | 0.062669 | -0.0026595 | 0.068906 | -61.0611 | 62.0819 | -61.116 | -61.1801 | 61.7569 | -0.050354 | -0.009155 | -0.19684 | 61.94 | -61.1664 | -0.17395 | 0.068664 | -0.11902 | -0.23804 | -0.25635 | -0.2243 | -0.073243 | 0.054932 | 60.9329 | 60.7452 | 122.699 | 123.024 | -0.11902 | 122.8821 | 60.8917 | -0.2243 | 123.024 | -0.11902 | 60.8917 | 122.699 | 122.8821 | -123.1293 | -123.1796
557.7812 | 123.0835 | -60.9055 | 62.0178 | -0.149 | -0.0041572 | -0.0036529 | 0.002634 | 0.06395 | -0.0037277 | 0.068479 | -61.0428 | 62.0773 | -61.1252 | -61.1298 | 61.8027 | 0.064087 | 0.12817 | 0.13275 | 62.027 | -61.1206 | -0.21973 | 0.05951 | -0.13733 | -0.2243 | -0.21515 | -0.21515 | 0.009156 | 0.082397 | 61.0336 | 61.0382 | 122.7081 | 122.9828 | -0.13733 | 122.9324 | 60.9695 | -0.21515 | 122.9828 | -0.13733 | 60.9695 | 122.7081 | 122.9324 | -123.143 | -123.1384
558.7812 | 123.1796 | -60.8643 | 61.9949 | -0.24055 | -0.0035162 | -0.00044854 | -0.0012112 | 0.0663 | -0.0045821 | 0.068479 | -61.0016 | 61.9766 | -61.0794 | -61.0565 | 61.908 | 0.15106 | -0.022888 | 0.23804 | 62.0224 | -61.0703 | -0.21515 | -0.01831 | -0.13733 | -0.19226 | -0.086975 | -0.20599 | 0.027466 | 0.07782 | 60.8414 | 61.1023 | 122.7722 | 122.8409 | -0.13733 | 122.8867 | 61.0153 | -0.20599 | 122.8409 | -0.13733 | 61.0153 | 122.7722 | 122.8867 | -123.0743 | -123.0652
559.7812 | 123.1293 | -60.9329 | 62.0041 | -0.034561 | -0.0037298 | -0.0019439 | 0.0045566 | 0.065659 | -0.0028731 | 0.066343 | -60.9741 | 62.0956 | -61.0794 | -61.084 | 61.7752 | 0.045776 | 0.022888 | 0.1236 | 62.0041 | -61.116 | -0.14649 | 0.091553 | -0.041199 | -0.15106 | -0.22888 | -0.18311 | 0 | 0.10529 | 60.9558 | 61.0565 | 122.7081 | 123.0286 | -0.041199 | 122.937 | 60.9787 | -0.18311 | 123.0286 | -0.041199 | 60.9787 | 122.7081 | 122.937 | -123.0835 | -123.1201
560.7812 | 123.1613 | -60.8551 | 62.0041 | -0.11085 | -0.007575 | -0.0045075 | -0.0022794 | 0.063737 | -0.0041549 | 0.06912 | -60.9924 | 61.9949 | -61.0794 | -61.0474 | 61.908 | 0.14648 | 0.018311 | 0.24261 | 62.0087 | -61.0565 | -0.2243 | -0.009155 | -0.13733 | -0.19226 | -0.09613 | -0.20142 | 0.004578 | 0.086975 | 60.8734 | 61.0977 | 122.7631 | 122.85 | -0.13733 | 122.8638 | 61.0016 | -0.20142 | 122.85 | -0.13733 | 61.0016 | 122.7631 | 122.8638 | -123.0835 | -123.0606
561.7812 | 123.0652 | -60.9283 | 62.0178 | 0.1104 | -0.0018072 | -0.0040801 | 0.0073336 | 0.066514 | -0.0043685 | 0.069333 | -61.0245 | 62.0956 | -61.0748 | -61.1481 | 61.7706 | 0 | 0.045776 | 0.045776 | 62.0132 | -61.1435 | -0.14648 | 0.07782 | -0.09613 | -0.21973 | -0.24719 | -0.21515 | -0.004577 | 0.050354 | 60.9741 | 60.9741 | 122.699 | 123.024 | -0.09613 | 122.9416 | 60.9283 | -0.21515 | 123.024 | -0.09613 | 60.9283 | 122.699 | 122.9416 | -123.0927 | -123.1613
562.7812 | 123.0469 | -60.91 | 62.0361 | -0.24818 | -0.0039434 | -0.0040801 | -0.00035676 | 0.063309 | -0.0022323 | 0.068052 | -61.0565 | 62.0499 | -61.0977 | -61.1481 | 61.8256 | 0.068665 | 0.14191 | 0.14648 | 62.0178 | -61.1023 | -0.18768 | 0.013733 | -0.14648 | -0.23804 | -0.21057 | -0.19226 | -0.018311 | 0.041198 | 61.0519 | 61.0565 | 122.7356 | 122.9599 | -0.14648 | 122.9279 | 60.9787 | -0.19226 | 122.9599 | -0.14648 | 60.9787 | 122.7356 | 122.9279 | -123.1338 | -123.1384
563.7969 | 123.1155 | -60.8963 | 62.0224 | -0.17952 | -0.004798 | -0.0049347 | 0.0017794 | 0.063737 | -0.0030869 | 0.070188 | -61.0153 | 62.0407 | -61.0931 | -61.0977 | 61.8393 | 0.10986 | 0.10071 | 0.17395 | 62.0041 | -61.1023 | -0.19684 | 0.01831 | -0.11902 | -0.20142 | -0.18311 | -0.20599 | -0.018311 | 0.07782 | 60.997 | 61.0703 | 122.7356 | 122.937 | -0.11902 | 122.9004 | 61.0062 | -0.20599 | 122.937 | -0.11902 | 61.0062 | 122.7356 | 122.9004 | -123.1155 | -123.1247
564.7812 | 123.1476 | -60.8643 | 62.0361 | -0.17189 | -0.006507 | -0.00044854 | -0.00057036 | 0.063737 | -0.0037277 | 0.068052 | -61.0016 | 62.0132 | -61.0703 | -61.084 | 61.8713 | 0.11902 | 0.07782 | 0.21515 | 61.9904 | -61.1069 | -0.20599 | -0.022888 | -0.13733 | -0.21973 | -0.16479 | -0.24262 | -0.045777 | 0.068664 | 60.9421 | 61.0794 | 122.7356 | 122.8775 | -0.13733 | 122.8546 | 60.9833 | -0.24262 | 122.8775 | -0.13733 | 60.9833 | 122.7356 | 122.8546 | -123.1064 | -123.143
565.7812 | 123.1064 | -60.91 | 62.0132 | -0.080337 | -0.0052252 | -0.0030121 | 0.0066928 | 0.064591 | -0.0035141 | 0.067838 | -61.0062 | 62.0728 | -61.084 | -61.0977 | 61.8256 | 0.07782 | 0.073242 | 0.15564 | 62.0132 | -61.1389 | -0.17395 | 0.059509 | -0.096131 | -0.18768 | -0.18768 | -0.22888 | 0 | 0.077819 | 60.9833 | 61.0657 | 122.7356 | 122.9828 | -0.096131 | 122.9233 | 60.9879 | -0.22888 | 122.9828 | -0.096131 | 60.9879 | 122.7356 | 122.9233 | -123.0972 | -123.1522
566.7812 | 123.0652 | -60.8871 | 62.0453 | -0.15663 | -0.0011664 | -2.1336e-05 | 0.001993 | 0.063096 | -0.0028731 | 0.06912 | -61.0565 | 62.0636 | -61.0977 | -61.1526 | 61.8027 | 0.073242 | 0.17395 | 0.1236 | 62.0499 | -61.0977 | -0.21057 | 0.018311 | -0.16937 | -0.2655 | -0.24262 | -0.21057 | 0.004578 | 0.041198 | 61.0611 | 61.0107 | 122.6898 | 122.9507 | -0.16937 | 122.937 | 60.9604 | -0.21057 | 122.9507 | -0.16937 | 60.9604 | 122.6898 | 122.937 | -123.143 | -123.143
567.7812 | 123.0972 | -60.91 | 62.027 | -0.15663 | -0.0028754 | -0.0032257 | 0.0028476 | 0.066087 | -0.0028731 | 0.068906 | -61.0474 | 62.0956 | -61.0886 | -61.1206 | 61.7981 | 0.068665 | 0.13275 | 0.11902 | 62.0453 | -61.116 | -0.17853 | 0.068664 | -0.13733 | -0.21057 | -0.22888 | -0.20599 | 0.01831 | 0.041199 | 61.0428 | 61.0291 | 122.7081 | 123.0057 | -0.13733 | 122.9553 | 60.9787 | -0.20599 | 123.0057 | -0.13733 | 60.9787 | 122.7081 | 122.9553 | -123.1155 | -123.143
568.7812 | 123.0927 | -60.91 | 62.0407 | -0.087967 | -0.0020208 | 0.0016877 | 0.0034884 | 0.064805 | -0.0043685 | 0.069761 | -61.0336 | 62.1094 | -61.0794 | -61.1343 | 61.7889 | 0.064087 | 0.14648 | 0.1236 | 62.0224 | -61.1206 | -0.16937 | 0.068665 | -0.1236 | -0.2243 | -0.25177 | -0.21057 | -0.01831 | 0.045777 | 61.0565 | 61.0336 | 122.699 | 123.0194 | -0.1236 | 122.9324 | 60.9741 | -0.21057 | 123.0194 | -0.1236 | 60.9741 | 122.699 | 122.9324 | -123.1201 | -123.1613
569.7812 | 123.1476 | -60.8917 | 62.027 | -0.15663 | -0.0041572 | -0.0047211 | 0.00028404 | 0.065018 | -0.0028731 | 0.069974 | -61.0107 | 62.027 | -61.0977 | -61.1206 | 61.8439 | 0.10071 | 0.11444 | 0.16937 | 62.0087 | -61.0977 | -0.20599 | 0 | -0.11902 | -0.22888 | -0.18311 | -0.20599 | -0.018311 | 0.086975 | 61.0062 | 61.0611 | 122.7356 | 122.9187 | -0.11902 | 122.9004 | 60.9924 | -0.20599 | 122.9187 | -0.11902 | 60.9924 | 122.7356 | 122.9004 | -123.1247 | -123.1247
570.7812 | 123.0881 | -60.8734 | 62.0407 | -0.19478 | -0.0062934 | -0.0049347 | 0.0017794 | 0.062455 | -0.0043685 | 0.069974 | -61.0336 | 62.027 | -61.0931 | -61.1252 | 61.821 | 0.091553 | 0.11902 | 0.18768 | 62.0316 | -61.0977 | -0.21973 | -0.013732 | -0.16022 | -0.25177 | -0.21973 | -0.2243 | -0.009155 | 0.05951 | 60.9924 | 61.0611 | 122.6944 | 122.9004 | -0.16022 | 122.905 | 60.965 | -0.2243 | 122.9004 | -0.16022 | 60.965 | 122.6944 | 122.905 | -123.1338 | -123.1384
571.7812 | 123.1338 | -60.8917 | 62.0453 | -0.04219 | -0.0018072 | 0.00019226 | 0.0051974 | 0.0663 | -0.0062911 | 0.066984 | -60.9833 | 62.0636 | -61.0748 | -61.0977 | 61.8164 | 0.073242 | 0.054932 | 0.14648 | 62.0224 | -61.1298 | -0.1831 | 0.018311 | -0.091552 | -0.20599 | -0.22888 | -0.23804 | -0.022888 | 0.091553 | 60.9467 | 61.0382 | 122.7081 | 122.9553 | -0.091552 | 122.9141 | 60.965 | -0.23804 | 122.9553 | -0.091552 | 60.965 | 122.7081 | 122.9141 | -123.1201 | -123.175
572.7812 | 123.1018 | -60.91 | 62.0499 | -0.10323 | -0.0033026 | -0.0032257 | 0.0032748 | 0.0663 | -0.0033005 | 0.067624 | -61.0291 | 62.0728 | -61.0977 | -61.1343 | 61.821 | 0.064087 | 0.13275 | 0.14191 | 62.0316 | -61.1023 | -0.18768 | 0.022888 | -0.11902 | -0.2243 | -0.22888 | -0.19226 | -0.018311 | 0.068664 | 61.0428 | 61.0519 | 122.731 | 122.9828 | -0.11902 | 122.9416 | 60.9741 | -0.19226 | 122.9828 | -0.11902 | 60.9741 | 122.731 | 122.9416 | -123.1476 | -123.1522
573.7812 | 123.0789 | -60.9329 | 62.0087 | -0.31685 | -0.0033026 | -0.0062163 | 0.001993 | 0.066087 | -0.0024459 | 0.070402 | -61.0565 | 62.0682 | -61.1023 | -61.1847 | 61.7752 | -0.032043 | -0.009155 | 0.009155 | 61.9949 | -61.1526 | -0.16937 | 0.059509 | -0.1236 | -0.25177 | -0.23346 | -0.21973 | -0.013733 | 0.045776 | 60.9238 | 60.9421 | 122.7081 | 123.0011 | -0.1236 | 122.9279 | 60.9009 | -0.21973 | 123.0011 | -0.1236 | 60.9009 | 122.7081 | 122.9279 | -123.111 | -123.1613
574.7812 | 123.1567 | -60.9055 | 62.0178 | -0.13374 | -0.0033026 | -0.0049347 | -0.0016386 | 0.066087 | -0.0039413 | 0.067838 | -60.9833 | 62.0087 | -61.0657 | -61.0748 | 61.8896 | 0.15106 | 0.036621 | 0.24261 | 61.9995 | -61.0748 | -0.16022 | -0.009155 | -0.077819 | -0.16937 | -0.12817 | -0.16937 | -0.01831 | 0.082398 | 60.9421 | 61.1481 | 122.7951 | 122.9141 | -0.077819 | 122.905 | 61.0565 | -0.16937 | 122.9141 | -0.077819 | 61.0565 | 122.7951 | 122.905 | -123.0835 | -123.0927
575.7812 | 123.0927 | -60.8871 | 62.0316 | -0.11085 | -0.0024482 | -0.0019439 | 0.0058382 | 0.065018 | -0.0026595 | 0.066556 | -61.0153 | 62.1231 | -61.1023 | -61.1298 | 61.8164 | 0.054932 | 0.11444 | 0.14191 | 62.0361 | -61.1298 | -0.21515 | 0.091553 | -0.12817 | -0.24262 | -0.21515 | -0.24262 | 0.004578 | 0.086975 | 61.0016 | 61.0291 | 122.7036 | 123.0103 | -0.12817 | 122.9233 | 60.9421 | -0.24262 | 123.0103 | -0.12817 | 60.9421 | 122.7036 | 122.9233 | -123.1338 | -123.1613
576.7812 | 123.1018 | -60.9055 | 62.0224 | -0.057449 | -0.003089 | -0.0036529 | 0.0041292 | 0.0663 | -0.0024459 | 0.068265 | -60.997 | 62.0956 | -61.1023 | -61.1069 | 61.8484 | 0.073242 | 0.036621 | 0.13275 | 61.9949 | -61.1435 | -0.19684 | 0.073242 | -0.091552 | -0.20142 | -0.17395 | -0.23804 | -0.027466 | 0.10529 | 60.9421 | 61.0382 | 122.7539 | 123.0011 | -0.091552 | 122.9004 | 60.9787 | -0.23804 | 123.0011 | -0.091552 | 60.9787 | 122.7539 | 122.9004 | -123.1247 | -123.1659
577.7812 | 123.1155 | -60.9375 | 61.9629 | 0.21721 | -0.0022346 | -0.0015167 | 0.0034884 | 0.0663 | -0.0020187 | 0.068479 | -61.0977 | 62.0728 | -61.1252 | -61.1893 | 61.7386 | -0.059509 | 0.013733 | -0.009155 | 62.0087 | -61.1298 | -0.18768 | 0.10986 | -0.16022 | -0.25177 | -0.22431 | -0.19226 | 0.045776 | 0.027466 | 60.9512 | 60.9283 | 122.6761 | 123.0103 | -0.16022 | 122.9462 | 60.878 | -0.19226 | 123.0103 | -0.16022 | 60.878 | 122.6761 | 122.9462 | -123.0881 | -123.0927
578.7812 | 123.1476 | -60.9375 | 61.9858 | 0.19432 | -0.0011664 | -0.0032257 | 0.0024202 | 0.065446 | -0.00073695 | 0.069333 | -61.0794 | 62.1048 | -61.1526 | -61.1893 | 61.7615 | -0.054932 | 0.013733 | -0.041199 | 62.0041 | -61.1572 | -0.21515 | 0.11902 | -0.14191 | -0.25177 | -0.2243 | -0.21973 | 0.01831 | 0.073242 | 60.9512 | 60.8963 | 122.699 | 123.0423 | -0.14191 | 122.9416 | 60.8826 | -0.21973 | 123.0423 | -0.14191 | 60.8826 | 122.699 | 122.9416 | -123.1384 | -123.143
579.7812 | 123.0927 | -60.9055 | 62.0132 | 0.041733 | -0.0028754 | -0.00066214 | 0.0039156 | 0.067368 | -0.0035141 | 0.068265 | -61.0062 | 62.0773 | -61.1023 | -61.1252 | 61.8073 | 0.041199 | 0.022888 | 0.091553 | 62.0453 | -61.1389 | -0.19684 | 0.064087 | -0.10071 | -0.21973 | -0.20599 | -0.23346 | 0.032043 | 0.09613 | 60.9283 | 60.997 | 122.7127 | 122.9828 | -0.10071 | 122.9507 | 60.9467 | -0.23346 | 122.9828 | -0.10071 | 60.9467 | 122.7127 | 122.9507 | -123.1155 | -123.1522
580.7812 | 123.1018 | -60.9009 | 61.9904 | -0.065079 | -0.0043708 | -0.0019439 | 0.0030612 | 0.068009 | -0.0018051 | 0.068052 | -60.997 | 62.0911 | -61.0977 | -61.0886 | 61.8439 | 0.07782 | 0.027466 | 0.13733 | 62.0361 | -61.116 | -0.19684 | 0.10071 | -0.09613 | -0.18768 | -0.14648 | -0.21515 | 0.045777 | 0.10071 | 60.9283 | 61.0382 | 122.7448 | 122.9919 | -0.09613 | 122.937 | 60.9787 | -0.21515 | 122.9919 | -0.09613 | 60.9787 | 122.7448 | 122.937 | -123.0881 | -123.1064
581.7812 | 123.111 | -60.9055 | 61.9904 | 0.24773 | -0.0020208 | -0.0049347 | 0.00092504 | 0.066514 | -0.0028731 | 0.070188 | -61.0611 | 62.059 | -61.1298 | -61.171 | 61.7935 | -0.041199 | -0.073242 | 0.027466 | 61.9995 | -61.1435 | -0.2243 | 0.068665 | -0.15564 | -0.2655 | -0.19684 | -0.23804 | 0.009156 | 0.068665 | 60.8322 | 60.9329 | 122.699 | 122.9645 | -0.15564 | 122.905 | 60.8643 | -0.23804 | 122.9645 | -0.15564 | 60.8643 | 122.699 | 122.905 | -123.1201 | -123.1338
582.7812 | 123.111 | -60.9009 | 62.0224 | -0.10323 | -0.0024482 | -0.0015167 | -0.00057036 | 0.064378 | -0.0039413 | 0.067838 | -61.0565 | 62.0682 | -61.0931 | -61.171 | 61.8073 | 0.068665 | 0.13275 | 0.11444 | 62.0316 | -61.1343 | -0.19226 | 0.045776 | -0.15564 | -0.27008 | -0.21515 | -0.23346 | 0.009155 | 0.036621 | 61.0336 | 61.0153 | 122.7081 | 122.9691 | -0.15564 | 122.9324 | 60.9695 | -0.23346 | 122.9691 | -0.15564 | 60.9695 | 122.7081 | 122.9324 | -123.1155 | -123.1567
583.7812 | 123.143 | -60.9009 | 61.9629 | 0.27824 | -0.0043708 | -2.1336e-05 | 0.00049764 | 0.065873 | -0.0013779 | 0.070402 | -61.0611 | 62.0499 | -61.116 | -61.1526 | 61.8027 | -0.013733 | -0.086975 | 0.045776 | 61.9766 | -61.1389 | -0.21515 | 0.086975 | -0.16022 | -0.25177 | -0.16022 | -0.23804 | 0.013733 | 0.054932 | 60.8139 | 60.9467 | 122.7036 | 122.9507 | -0.16022 | 122.8775 | 60.8871 | -0.23804 | 122.9507 | -0.16022 | 60.8871 | 122.7036 | 122.8775 | -123.0789 | -123.1018
584.7812 | 123.0789 | -60.9009 | 61.9949 | 0.13329 | -0.0024482 | 0.00061946 | 0.0034884 | 0.0663 | -0.0022323 | 0.067411 | -61.0382 | 62.0911 | -61.1069 | -61.1618 | 61.7615 | -0.013733 | 0.027466 | 0.064087 | 62.0316 | -61.1481 | -0.20599 | 0.09613 | -0.13733 | -0.26092 | -0.23346 | -0.24719 | 0.036621 | 0.068665 | 60.9283 | 60.965 | 122.6624 | 122.9919 | -0.13733 | 122.9324 | 60.8871 | -0.24719 | 122.9919 | -0.13733 | 60.8871 | 122.6624 | 122.9324 | -123.1018 | -123.143
585.7812 | 123.175 | -60.9192 | 61.9537 | 0.25536 | -0.0035162 | 0.00061946 | 0.0011386 | 0.065873 | -0.0022323 | 0.068479 | -61.0428 | 62.0178 | -61.1252 | -61.1343 | 61.821 | 0.009155 | -0.14191 | 0.082397 | 61.9904 | -61.1252 | -0.20599 | 0.064087 | -0.1236 | -0.21515 | -0.13275 | -0.20599 | 0.036621 | 0.082397 | 60.7773 | 61.0016 | 122.7402 | 122.937 | -0.1236 | 122.9095 | 60.9283 | -0.20599 | 122.937 | -0.1236 | 60.9283 | 122.7402 | 122.9095 | -123.0789 | -123.0789
586.7812 | 123.143 | -60.9192 | 62.027 | -0.04982 | -0.0028754 | -0.0034393 | 0.0030612 | 0.067582 | -0.00073695 | 0.067838 | -60.9879 | 62.0865 | -61.084 | -61.0977 | 61.8393 | 0.091553 | 0.045776 | 0.16022 | 62.0407 | -61.1206 | -0.16479 | 0.059509 | -0.068665 | -0.17853 | -0.18768 | -0.20142 | 0.013732 | 0.09613 | 60.965 | 61.0794 | 122.7585 | 123.0057 | -0.068665 | 122.9599 | 61.0107 | -0.20142 | 123.0057 | -0.068665 | 61.0107 | 122.7585 | 122.9599 | -123.111 | -123.1476
587.7812 | 123.0194 | -60.9604 | 61.9949 | 0.20195 | -0.0033026 | -0.0060027 | 0.002634 | 0.064591 | -0.0033005 | 0.068479 | -61.1023 | 62.0773 | -61.1206 | -61.2076 | 61.7386 | -0.050354 | 0.004578 | -0.022888 | 62.0544 | -61.1526 | -0.16022 | 0.082398 | -0.14191 | -0.24719 | -0.25635 | -0.19226 | 0.059509 | 0.01831 | 60.965 | 60.9375 | 122.699 | 123.0377 | -0.14191 | 123.0148 | 60.91 | -0.19226 | 123.0377 | -0.14191 | 60.91 | 122.699 | 123.0148 | -123.1155 | -123.1476
588.7812 | 123.1476 | -60.9421 | 61.9675 | 0.20195 | -0.0028754 | -0.0030121 | 0.001993 | 0.066087 | -0.0035141 | 0.06912 | -61.0657 | 62.0728 | -61.1114 | -61.1801 | 61.7706 | -0.036621 | -0.059509 | 0.013733 | 62.0132 | -61.1572 | -0.16937 | 0.10529 | -0.1236 | -0.23804 | -0.19684 | -0.21515 | 0.045777 | 0.045776 | 60.8826 | 60.9558 | 122.7127 | 123.0148 | -0.1236 | 122.9553 | 60.9055 | -0.21515 | 123.0148 | -0.1236 | 60.9055 | 122.7127 | 122.9553 | -123.0789 | -123.1247
589.7812 | 123.1888 | -60.8963 | 61.9492 | 0.3698 | -0.0052252 | 0.0010467 | 0.00028404 | 0.065232 | -0.0026595 | 0.067624 | -61.0245 | 61.9904 | -61.1023 | -61.1023 | 61.8484 | 0.041199 | -0.17395 | 0.10986 | 61.9583 | -61.1343 | -0.20599 | 0.041198 | -0.12817 | -0.20599 | -0.10071 | -0.23804 | 0.009155 | 0.07782 | 60.7224 | 61.0062 | 122.7448 | 122.8867 | -0.12817 | 122.8546 | 60.9375 | -0.23804 | 122.8867 | -0.12817 | 60.9375 | 122.7448 | 122.8546 | -123.0515 | -123.0835
590.7812 | 123.0972 | -60.9055 | 62.0132 | 0.026474 | -0.0022346 | 0.0016877 | 0.0045566 | 0.066727 | -0.0024459 | 0.068479 | -61.0107 | 62.114 | -61.0977 | -61.1481 | 61.7752 | 0.009155 | 0.027466 | 0.068665 | 62.0087 | -61.1481 | -0.19226 | 0.10071 | -0.10529 | -0.24261 | -0.23804 | -0.24261 | -0.004578 | 0.086975 | 60.9329 | 60.9741 | 122.6807 | 123.0194 | -0.10529 | 122.9141 | 60.9146 | -0.24261 | 123.0194 | -0.10529 | 60.9146 | 122.6807 | 122.9141 | -123.111 | -123.1613
591.7812 | 123.0881 | -60.9604 | 62.0041 | 1.9262 | -0.0018072 | -0.0049347 | 0.0022066 | 0.065018 | -0.0011643 | 0.068693 | -60.9055 | 62.1048 | -61.1298 | -61.1847 | 61.7706 | -0.050354 | -0.009155 | -0.018311 | 62.0041 | -61.1847 | -0.16937 | 0.10071 | 0.054931 | -0.2243 | -0.23346 | -0.2243 | 0 | 0.2243 | 60.9512 | 60.9421 | 122.731 | 123.0652 | 0.054931 | 122.9645 | 60.91 | -0.2243 | 123.0652 | 0.054931 | 60.91 | 122.731 | 122.9645 | -123.1338 | -123.1888
592.7812 | 123.0789 | -60.9192 | 61.9766 | -0.011673 | -0.0011664 | -0.0034393 | 0.0028476 | 0.064805 | -0.0011643 | 0.071042 | -61.0977 | 62.1002 | -61.1206 | -61.1984 | 61.7294 | -0.041199 | -0.013733 | 0.004578 | 61.9904 | -61.1664 | -0.20142 | 0.1236 | -0.17853 | -0.27924 | -0.24719 | -0.24719 | 0.013732 | 0.022888 | 60.9055 | 60.9238 | 122.6486 | 123.0194 | -0.17853 | 122.9095 | 60.878 | -0.24719 | 123.0194 | -0.17853 | 60.878 | 122.6486 | 122.9095 | -123.0972 | -123.143
593.7812 | 123.1613 | -60.8963 | 61.9812 | 0.1638 | -0.0054388 | -0.0049347 | -0.0048428 | 0.064591 | -0.0024459 | 0.069547 | -61.0611 | 61.9904 | -61.1069 | -61.1526 | 61.8118 | 0.018311 | -0.082397 | 0.09613 | 61.9904 | -61.1298 | -0.21057 | 0.009155 | -0.16479 | -0.25635 | -0.16937 | -0.23346 | 0.009155 | 0.045777 | 60.8139 | 60.9924 | 122.7081 | 122.8867 | -0.16479 | 122.8867 | 60.9146 | -0.23346 | 122.8867 | -0.16479 | 60.9146 | 122.7081 | 122.8867 | -123.0881 | -123.111
594.7812 | 123.2391 | -60.8734 | 61.9858 | 0.22484 | -0.0015936 | -2.1336e-05 | -0.00035676 | 0.06395 | -0.0033005 | 0.068265 | -60.9833 | 61.9675 | -61.1023 | -61.0931 | 61.9675 | 0.004578 | -0.3479 | 0.21515 | 61.9446 | -61.1343 | -0.22888 | -0.018311 | -0.10986 | -0.21973 | -0.018311 | -0.26093 | -0.041199 | 0.11902 | 60.5255 | 61.0886 | 122.8409 | 122.8409 | -0.10986 | 122.818 | 60.878 | -0.26093 | 122.8409 | -0.10986 | 60.878 | 122.8409 | 122.818 | -123.0881 | -123.1201
595.7812 | 123.1064 | -60.9375 | 61.972 | 0.19432 | -0.0043708 | 0.00019226 | 0.0039156 | 0.063737 | -0.0026595 | 0.069761 | -61.0657 | 62.0453 | -61.1252 | -61.1847 | 61.7706 | -0.036621 | -0.054932 | 0.022888 | 62.0087 | -61.1618 | -0.18768 | 0.073242 | -0.12817 | -0.24719 | -0.20142 | -0.2243 | 0.036621 | 0.059509 | 60.8826 | 60.9604 | 122.7081 | 122.9828 | -0.12817 | 122.9462 | 60.9009 | -0.2243 | 122.9828 | -0.12817 | 60.9009 | 122.7081 | 122.9462 | -123.0972 | -123.1338
596.7812 | 123.1338 | -60.9009 | 61.9858 | 0.26299 | -0.0035162 | -0.0062163 | 0.0051974 | 0.064805 | -0.0035141 | 0.07147 | -61.0565 | 62.0361 | -61.0931 | -61.1481 | 61.7661 | -0.018311 | -0.09613 | 0.041199 | 61.9675 | -61.1389 | -0.19226 | 0.050354 | -0.15564 | -0.24719 | -0.21973 | -0.23804 | -0.018311 | 0.036621 | 60.8047 | 60.9421 | 122.6669 | 122.937 | -0.15564 | 122.8683 | 60.8826 | -0.23804 | 122.937 | -0.15564 | 60.8826 | 122.6669 | 122.8683 | -123.0789 | -123.1247
597.7812 | 123.111 | -60.8871 | 61.9812 | 0.11803 | -0.004798 | -0.0051483 | -0.0029202 | 0.06395 | -0.0030869 | 0.068906 | -61.0657 | 61.9766 | -61.1343 | -61.1389 | 61.7935 | 0.041199 | -0.054932 | 0.10529 | 61.9949 | -61.1023 | -0.24719 | -0.004577 | -0.17853 | -0.25177 | -0.18768 | -0.21515 | 0.013733 | 0.068664 | 60.8322 | 60.9924 | 122.6807 | 122.8638 | -0.17853 | 122.8821 | 60.9283 | -0.21515 | 122.8638 | -0.17853 | 60.9283 | 122.6807 | 122.8821 | -123.1155 | -123.0835
598.7812 | 123.1476 | -60.8963 | 61.972 | 0.095139 | -0.0028754 | -0.0051483 | -0.0027066 | 0.0616 | -0.0028731 | 0.067624 | -61.0611 | 61.9904 | -61.0794 | -61.1481 | 61.8576 | 0.13275 | -0.082397 | 0.11902 | 62.0087 | -61.0931 | -0.18311 | 0.01831 | -0.16479 | -0.25177 | -0.11444 | -0.19684 | 0.036621 | 0.018311 | 60.8139 | 61.0153 | 122.7539 | 122.8867 | -0.16479 | 122.905 | 61.0291 | -0.19684 | 122.8867 | -0.16479 | 61.0291 | 122.7539 | 122.905 | -123.0515 | -123.0652
599.7812 | 123.1338 | -60.9009 | 61.9812 | 0.19432 | -0.0011664 | -0.0047211 | 0.0024202 | 0.06096 | -0.0037277 | 0.069761 | -61.0153 | 61.9537 | -61.0977 | -61.1114 | 61.8256 | 0.036621 | -0.14191 | 0.10986 | 61.9583 | -61.1389 | -0.19684 | -0.027466 | -0.11444 | -0.21057 | -0.15564 | -0.23804 | -0.022888 | 0.082397 | 60.759 | 61.0107 | 122.7264 | 122.8546 | -0.11444 | 122.8592 | 60.9375 | -0.23804 | 122.8546 | -0.11444 | 60.9375 | 122.7264 | 122.8592 | -123.0789 | -123.1201
600.7812 | 123.2117 | -60.9146 | 61.9537 | 0.25536 | -0.0039434 | -0.0049347 | 0.004343 | 0.063096 | -0.0024459 | 0.069974 | -60.9879 | 61.9858 | -61.0886 | -61.0428 | 61.8439 | 0.054932 | -0.15564 | 0.14191 | 61.9354 | -61.116 | -0.17395 | 0.032044 | -0.073242 | -0.12817 | -0.10986 | -0.20142 | -0.01831 | 0.10071 | 60.759 | 61.0565 | 122.7585 | 122.9004 | -0.073242 | 122.85 | 60.9695 | -0.20142 | 122.9004 | -0.073242 | 60.9695 | 122.7585 | 122.85 | -123.0423 | -123.0698
601.7812 | 123.1796 | -60.878 | 61.9629 | -0.0040434 | -0.0039434 | -0.0049347 | -0.00057036 | 0.061387 | -0.0039413 | 0.067624 | -61.0382 | 61.9629 | -61.0977 | -61.1206 | 61.8347 | 0.086975 | -0.068665 | 0.14648 | 61.9995 | -61.1252 | -0.21973 | 0 | -0.16022 | -0.24261 | -0.12817 | -0.24719 | 0.036621 | 0.059509 | 60.8093 | 61.0245 | 122.7127 | 122.8409 | -0.16022 | 122.8775 | 60.965 | -0.24719 | 122.8409 | -0.16022 | 60.965 | 122.7127 | 122.8775 | -123.0606 | -123.0881
602.7812 | 123.1338 | -60.8963 | 61.9766 | 0.20958 | -0.0052252 | -0.0072845 | 0.00028404 | 0.062241 | -0.0039413 | 0.069333 | -61.0153 | 61.9675 | -61.116 | -61.1298 | 61.8073 | 0.018311 | -0.10529 | 0.086975 | 61.9629 | -61.1069 | -0.21973 | -0.009156 | -0.11902 | -0.23346 | -0.16937 | -0.21057 | -0.013733 | 0.10071 | 60.791 | 60.9833 | 122.7036 | 122.8638 | -0.11902 | 122.8592 | 60.9146 | -0.21057 | 122.8638 | -0.11902 | 60.9146 | 122.7036 | 122.8592 | -123.0927 | -123.0835
603.7812 | 123.1934 | -60.8459 | 62.0087 | -0.04982 | -0.0045844 | -0.0066437 | 0.00028404 | 0.060532 | -0.0026595 | 0.066556 | -60.965 | 61.9949 | -61.0611 | -61.0107 | 61.908 | 0.14191 | -0.10529 | 0.2655 | 61.9492 | -61.1069 | -0.21515 | -0.013733 | -0.11902 | -0.16479 | -0.10071 | -0.26093 | -0.059509 | 0.09613 | 60.7407 | 61.1115 | 122.7539 | 122.8409 | -0.11902 | 122.7951 | 60.9879 | -0.26093 | 122.8409 | -0.11902 | 60.9879 | 122.7539 | 122.7951 | -123.0698 | -123.1155
604.7812 | 123.1842 | -60.9009 | 61.9766 | 0.1104 | -0.0035162 | -0.00023494 | 0.00071144 | 0.059891 | -0.0041549 | 0.067411 | -61.0474 | 61.9675 | -61.1069 | -61.1298 | 61.821 | 0.009155 | -0.091553 | 0.09613 | 61.9308 | -61.1114 | -0.20599 | -0.009156 | -0.14648 | -0.22888 | -0.15564 | -0.21057 | -0.045777 | 0.05951 | 60.8093 | 60.997 | 122.7219 | 122.8683 | -0.14648 | 122.8317 | 60.91 | -0.21057 | 122.8683 | -0.14648 | 60.91 | 122.7219 | 122.8317 | -123.0835 | -123.0881
605.7812 | 123.2254 | -60.8551 | 61.9858 | -0.04982 | -0.007575 | -0.0060027 | 0.0017794 | 0.061173 | -0.0043685 | 0.070188 | -60.9879 | 61.9812 | -61.0886 | -61.0565 | 61.8851 | 0.11902 | -0.082397 | 0.2243 | 61.9675 | -61.1069 | -0.23346 | -0.004578 | -0.13275 | -0.20142 | -0.10071 | -0.25177 | -0.018311 | 0.10071 | 60.7727 | 61.0794 | 122.7402 | 122.8363 | -0.13275 | 122.8226 | 60.9741 | -0.25177 | 122.8363 | -0.13275 | 60.9741 | 122.7402 | 122.8226 | -123.0743 | -123.0927
606.7812 | 123.2208 | -60.8459 | 61.9949 | -0.04982 | -0.0069342 | -0.0038665 | -0.00035676 | 0.059251 | -0.0020187 | 0.068265 | -60.9787 | 61.9583 | -61.084 | -61.0291 | 61.9171 | 0.14648 | -0.073242 | 0.23346 | 61.9492 | -61.0794 | -0.23804 | -0.036621 | -0.13275 | -0.18311 | -0.07782 | -0.23346 | -0.045776 | 0.10529 | 60.7727 | 61.0794 | 122.7631 | 122.8043 | -0.13275 | 122.7951 | 60.9924 | -0.23346 | 122.8043 | -0.13275 | 60.9924 | 122.7631 | 122.7951 | -123.0789 | -123.0743
607.7812 | 123.2071 | -60.8734 | 62.0132 | -0.011673 | -0.007575 | -0.0034393 | 0.0017794 | 0.059891 | -0.0035141 | 0.069333 | -61.0245 | 61.9675 | -61.1069 | -61.0703 | 61.853 | 0.086975 | -0.068665 | 0.16479 | 61.9675 | -61.1114 | -0.23346 | -0.045777 | -0.15106 | -0.19684 | -0.16022 | -0.23804 | -0.045777 | 0.082398 | 60.8047 | 61.0382 | 122.7264 | 122.8409 | -0.15106 | 122.8409 | 60.9604 | -0.23804 | 122.8409 | -0.15106 | 60.9604 | 122.7264 | 122.8409 | -123.1201 | -123.1247
608.7812 | 123.1613 | -60.878 | 61.972 | 0.23247 | -0.0033026 | -0.0019439 | 0.0041292 | 0.062882 | -0.0041549 | 0.067838 | -60.9787 | 61.9904 | -61.0931 | -61.0794 | 61.8347 | 0.036621 | -0.16479 | 0.10986 | 61.9492 | -61.1252 | -0.21515 | 0.01831 | -0.10071 | -0.20142 | -0.13733 | -0.24719 | -0.022888 | 0.11444 | 60.7132 | 60.9879 | 122.7127 | 122.8683 | -0.10071 | 122.8271 | 60.9146 | -0.24719 | 122.8683 | -0.10071 | 60.9146 | 122.7127 | 122.8271 | -123.0652 | -123.0972
609.7812 | 123.2346 | -60.8597 | 61.9904 | -0.14137 | -0.0054388 | -0.0047211 | 0.00071144 | 0.062028 | -0.0033005 | 0.068052 | -60.9558 | 61.972 | -61.0703 | -61.0245 | 61.9034 | 0.14191 | -0.068665 | 0.25635 | 61.972 | -61.1069 | -0.21057 | -0.01831 | -0.096131 | -0.1648 | -0.086975 | -0.24719 | -0.01831 | 0.11444 | 60.791 | 61.116 | 122.7631 | 122.8317 | -0.096131 | 122.8317 | 61.0016 | -0.24719 | 122.8317 | -0.096131 | 61.0016 | 122.7631 | 122.8317 | -123.0606 | -123.0972
610.7812 | 123.2025 | -60.878 | 61.9858 | 0.034104 | -0.005866 | -0.0057891 | 0.00049764 | 0.060532 | -0.0028731 | 0.068906 | -61.0016 | 61.9995 | -61.0886 | -61.0428 | 61.8805 | 0.1236 | -0.07782 | 0.21515 | 61.9766 | -61.0794 | -0.21057 | 0.013733 | -0.1236 | -0.16479 | -0.10529 | -0.20142 | -0.009155 | 0.086975 | 60.8002 | 61.0931 | 122.7585 | 122.8775 | -0.1236 | 122.8546 | 61.0016 | -0.20142 | 122.8775 | -0.1236 | 61.0016 | 122.7585 | 122.8546 | -123.0743 | -123.0652
611.7812 | 123.2941 | -60.8276 | 62.0316 | -0.080337 | -0.0062934 | -0.0017303 | 0.0011386 | 0.061814 | -0.0028731 | 0.06912 | -60.9604 | 61.9904 | -61.0794 | -61.0245 | 61.9125 | 0.16022 | -0.045776 | 0.24719 | 61.9629 | -61.0657 | -0.25177 | -0.041199 | -0.13275 | -0.19684 | -0.11902 | -0.23804 | -0.068664 | 0.11902 | 60.7819 | 61.0748 | 122.7402 | 122.818 | -0.13275 | 122.7905 | 60.9879 | -0.23804 | 122.818 | -0.13275 | 60.9879 | 122.7402 | 122.7905 | -123.111 | -123.0972
612.7812 | 123.175 | -60.878 | 61.972 | 0.041733 | -0.005866 | -0.010916 | 0.00028404 | 0.061387 | -0.0054367 | 0.067838 | -61.0199 | 61.9858 | -61.116 | -61.0977 | 61.8484 | 0.068665 | -0.059509 | 0.16479 | 61.9766 | -61.0794 | -0.23804 | 0.013733 | -0.14191 | -0.21973 | -0.1236 | -0.20142 | 0.004578 | 0.096131 | 60.8185 | 61.0428 | 122.7264 | 122.8638 | -0.14191 | 122.8546 | 60.9467 | -0.20142 | 122.8638 | -0.14191 | 60.9467 | 122.7264 | 122.8546 | -123.0881 | -123.0515
613.7812 | 123.143 | -60.9055 | 62.0041 | -0.10323 | -0.0035162 | -0.0045075 | 0.0073336 | 0.062882 | -0.0037277 | 0.068906 | -60.997 | 62.0316 | -61.1114 | -61.0703 | 61.8393 | 0.073242 | 0 | 0.14191 | 61.9766 | -61.1206 | -0.20599 | 0.027466 | -0.091552 | -0.16479 | -0.16479 | -0.21515 | -0.027465 | 0.11444 | 60.9055 | 61.0474 | 122.7448 | 122.937 | -0.091552 | 122.8821 | 60.9787 | -0.21515 | 122.937 | -0.091552 | 60.9787 | 122.7448 | 122.8821 | -123.1155 | -123.1247
614.7812 | 123.143 | -60.8505 | 62.0361 | -0.14137 | -0.0039434 | -0.0072845 | 0.0011386 | 0.063096 | -0.0037277 | 0.067411 | -60.9741 | 62.0316 | -61.0794 | -61.0519 | 61.8759 | 0.12817 | 0.045776 | 0.21057 | 61.9995 | -61.0931 | -0.22888 | -0.004578 | -0.1236 | -0.20142 | -0.16022 | -0.24262 | -0.036621 | 0.10529 | 60.8963 | 61.0611 | 122.7264 | 122.8821 | -0.1236 | 122.85 | 60.9787 | -0.24262 | 122.8821 | -0.1236 | 60.9787 | 122.7264 | 122.85 | -123.1155 | -123.1293
615.7812 | 123.2071 | -60.8551 | 62.0178 | 0.041733 | -0.0050116 | -0.0074981 | -0.0027066 | 0.062882 | -0.0024459 | 0.068479 | -61.0336 | 61.9904 | -61.1023 | -61.0748 | 61.8622 | 0.07782 | -0.059509 | 0.16937 | 61.9675 | -61.0565 | -0.24719 | -0.027466 | -0.17853 | -0.21973 | -0.15564 | -0.20142 | -0.050354 | 0.068665 | 60.7956 | 61.0245 | 122.7173 | 122.8455 | -0.17853 | 122.8226 | 60.9329 | -0.20142 | 122.8455 | -0.17853 | 60.9329 | 122.7173 | 122.8226 | -123.1201 | -123.0743
616.7812 | 123.0789 | -60.8963 | 62.027 | -0.17189 | -0.0037298 | -0.0057891 | 0.0032748 | 0.0616 | -0.0047957 | 0.068479 | -61.0336 | 62.0453 | -61.1069 | -61.1206 | 61.8118 | 0.059509 | 0.11902 | 0.13733 | 62.0453 | -61.1298 | -0.21057 | 0.01831 | -0.13733 | -0.2243 | -0.21515 | -0.23346 | 0.01831 | 0.073243 | 61.0153 | 61.0336 | 122.7081 | 122.9416 | -0.13733 | 122.9416 | 60.9558 | -0.23346 | 122.9416 | -0.13733 | 60.9558 | 122.7081 | 122.9416 | -123.1339 | -123.1567
617.7812 | 123.1842 | -60.878 | 62.0224 | -0.16426 | -0.0060798 | -0.0032257 | 0.0024202 | 0.062028 | -0.0018051 | 0.06912 | -60.9833 | 62.0041 | -61.0382 | -61.0199 | 61.8942 | 0.1236 | -0.059509 | 0.2243 | 61.972 | -61.0794 | -0.16022 | -0.018311 | -0.10528 | -0.14191 | -0.12817 | -0.20142 | -0.050354 | 0.054932 | 60.8185 | 61.1023 | 122.7722 | 122.8821 | -0.10528 | 122.85 | 61.0016 | -0.20142 | 122.8821 | -0.10528 | 61.0016 | 122.7722 | 122.85 | -123.0606 | -123.1018
618.7812 | 123.2162 | -60.8505 | 62.0361 | -0.149 | -0.005866 | -0.0077117 | 0.002634 | 0.063523 | -0.0041549 | 0.066984 | -60.8688 | 62.027 | -61.0519 | -61.0107 | 61.8851 | 0.11444 | -0.064087 | 0.23804 | 61.9766 | -61.0611 | -0.20142 | -0.009155 | -0.01831 | -0.16022 | -0.15106 | -0.21057 | -0.059509 | 0.18311 | 60.7864 | 61.0886 | 122.7356 | 122.8775 | -0.01831 | 122.8271 | 60.965 | -0.21057 | 122.8775 | -0.01831 | 60.965 | 122.7356 | 122.8271 | -123.0881 | -123.0972
619.7812 | 123.1842 | -60.8414 | 62.0132 | -1.446 | -0.0067206 | -0.0034393 | 0.001993 | 0.062028 | -0.0035141 | 0.070402 | -60.8643 | 62.0407 | -61.0703 | -61.0611 | 61.9308 | 0.14191 | -0.004578 | 0.25635 | 61.9675 | -61.0565 | -0.22888 | 0.027465 | -0.022888 | -0.21973 | -0.082398 | -0.21515 | -0.045777 | 0.20599 | 60.8368 | 61.0977 | 122.7722 | 122.8821 | -0.022888 | 122.8088 | 60.9833 | -0.21515 | 122.8821 | -0.022888 | 60.9833 | 122.7722 | 122.8088 | -123.0835 | -123.0698
620.7812 | 123.2391 | -60.8459 | 61.9858 | -0.026932 | -0.0073614 | -0.0066437 | 0.0013522 | 0.062028 | -0.0037277 | 0.068693 | -60.9467 | 61.9766 | -61.0703 | -61.0062 | 61.9308 | 0.16022 | -0.068665 | 0.2655 | 61.9812 | -61.0428 | -0.2243 | -0.009155 | -0.10071 | -0.16022 | -0.054932 | -0.19684 | -0.004578 | 0.1236 | 60.7773 | 61.1115 | 122.7768 | 122.8226 | -0.10071 | 122.8271 | 61.0062 | -0.19684 | 122.8226 | -0.10071 | 61.0062 | 122.7768 | 122.8271 | -123.056 | -123.0286
621.7812 | 123.0835 | -60.8963 | 62.0224 | -0.18715 | -0.0033026 | -0.0057891 | 0.0056246 | 0.061173 | -0.0052231 | 0.068265 | -61.0519 | 62.059 | -61.1114 | -61.1298 | 61.7935 | 0.073242 | 0.14648 | 0.15106 | 62.0132 | -61.1023 | -0.21515 | 0.036621 | -0.15564 | -0.23346 | -0.22888 | -0.20599 | -0.009155 | 0.059509 | 61.0428 | 61.0474 | 122.6898 | 122.9553 | -0.15564 | 122.9095 | 60.9695 | -0.20599 | 122.9553 | -0.15564 | 60.9695 | 122.6898 | 122.9095 | -123.1338 | -123.1247
622.7812 | 123.0743 | -60.8917 | 62.0544 | -0.19478 | -0.0039434 | -0.0051483 | 0.003702 | 0.062882 | -0.0047957 | 0.068906 | -61.0428 | 62.0819 | -61.1252 | -61.1343 | 61.7981 | 0.059509 | 0.16479 | 0.13733 | 62.0361 | -61.0931 | -0.23346 | 0.027466 | -0.15106 | -0.24261 | -0.25635 | -0.20142 | -0.01831 | 0.082397 | 61.0565 | 61.0291 | 122.6898 | 122.9736 | -0.15106 | 122.9279 | 60.9512 | -0.20142 | 122.9736 | -0.15106 | 60.9512 | 122.6898 | 122.9279 | -123.1796 | -123.1476
623.7812 | 123.1064 | -60.8917 | 62.0132 | -0.10323 | -0.003089 | -0.0064301 | 0.0060518 | 0.063737 | -0.0026595 | 0.068906 | -61.0016 | 62.0453 | -61.1114 | -61.0794 | 61.8256 | 0.059509 | 0.022888 | 0.11902 | 62.0132 | -61.1023 | -0.21973 | 0.032043 | -0.10986 | -0.18768 | -0.18768 | -0.21057 | 0 | 0.10986 | 60.9146 | 61.0107 | 122.7173 | 122.937 | -0.10986 | 122.905 | 60.9512 | -0.21057 | 122.937 | -0.10986 | 60.9512 | 122.7173 | 122.905 | -123.1247 | -123.1155
624.7812 | 123.0881 | -60.9009 | 62.0178 | -0.087967 | -0.0020208 | -0.0064301 | 0.0049838 | 0.063523 | -0.0020187 | 0.068052 | -61.0291 | 62.1048 | -61.084 | -61.116 | 61.8118 | 0.054932 | 0.13733 | 0.13733 | 62.0041 | -61.1343 | -0.1831 | 0.086975 | -0.12817 | -0.21515 | -0.20599 | -0.23346 | -0.013733 | 0.054931 | 61.0382 | 61.0382 | 122.7127 | 123.0057 | -0.12817 | 122.905 | 60.9558 | -0.23346 | 123.0057 | -0.12817 | 60.9558 | 122.7127 | 122.905 | -123.1018 | -123.1522
625.7812 | 123.0927 | -60.8871 | 62.0361 | -0.18715 | -0.0067206 | -0.0092071 | 0.0017794 | 0.062669 | -0.0037277 | 0.069974 | -61.0748 | 62.0865 | -61.116 | -61.1298 | 61.8164 | 0.041199 | 0.15106 | 0.13275 | 62.0499 | -61.1069 | -0.22888 | 0.050354 | -0.18768 | -0.24262 | -0.21973 | -0.21973 | 0.013733 | 0.041199 | 61.0382 | 61.0199 | 122.7036 | 122.9736 | -0.18768 | 122.937 | 60.9283 | -0.21973 | 122.9736 | -0.18768 | 60.9283 | 122.7036 | 122.937 | -123.1522 | -123.143
626.7812 | 123.0835 | -60.9055 | 62.0453 | -0.16426 | -0.0018072 | -0.0017303 | 0.0015658 | 0.065232 | -0.0030869 | 0.067197 | -61.0611 | 62.0636 | -61.1023 | -61.1526 | 61.8164 | 0.073242 | 0.16022 | 0.13733 | 62.027 | -61.1252 | -0.19684 | 0.018311 | -0.15564 | -0.24719 | -0.22888 | -0.21973 | -0.01831 | 0.041199 | 61.0657 | 61.0428 | 122.7219 | 122.9691 | -0.15564 | 122.9324 | 60.9787 | -0.21973 | 122.9691 | -0.15564 | 60.9787 | 122.7219 | 122.9324 | -123.1476 | -123.1705
627.7812 | 123.0331 | -60.9329 | 62.0087 | 0.13329 | -0.004798 | 0.0029693 | 0.0066928 | 0.0663 | -0.0037277 | 0.068479 | -61.0748 | 62.1048 | -61.0931 | -61.1938 | 61.7386 | -0.041199 | 0.050354 | -0.018311 | 61.9949 | -61.1664 | -0.16022 | 0.09613 | -0.14191 | -0.26093 | -0.27008 | -0.23346 | -0.013733 | 0.018311 | 60.9833 | 60.9146 | 122.6715 | 123.0377 | -0.14191 | 122.9279 | 60.8917 | -0.23346 | 123.0377 | -0.14191 | 60.8917 | 122.6715 | 122.9279 | -123.1018 | -123.175
628.7656 | 123.1018 | -60.8826 | 61.9949 | 0.064621 | -0.0043708 | -0.0049347 | 0.0034884 | 0.067368 | -0.0056503 | 0.068906 | -61.0291 | 62.0132 | -61.1252 | -61.1069 | 61.8301 | 0.032043 | 0.018311 | 0.086975 | 62.0178 | -61.0886 | -0.24262 | 0.018311 | -0.14648 | -0.22431 | -0.16479 | -0.20599 | 0.022888 | 0.09613 | 60.9009 | 60.9695 | 122.7127 | 122.8958 | -0.14648 | 122.9004 | 60.9146 | -0.20599 | 122.8958 | -0.14648 | 60.9146 | 122.7127 | 122.9004 | -123.1201 | -123.0835
629.7812 | 123.0652 | -60.9283 | 61.9995 | 0.11803 | -0.0020208 | -0.0053619 | 0.004343 | 0.066087 | -0.0037277 | 0.069547 | -61.084 | 62.0636 | -61.1069 | -61.1984 | 61.7294 | -0.064087 | 0.045776 | -0.022888 | 62.027 | -61.1618 | -0.17853 | 0.064087 | -0.15564 | -0.27008 | -0.27008 | -0.23346 | 0.027466 | 0.022889 | 60.9741 | 60.9055 | 122.6578 | 122.9919 | -0.15564 | 122.9553 | 60.8643 | -0.23346 | 122.9919 | -0.15564 | 60.8643 | 122.6578 | 122.9553 | -123.1064 | -123.1613
630.7812 | 123.0789 | -60.91 | 62.0224 | -0.17952 | -0.0022346 | -0.0032257 | -0.00078396 | 0.063523 | -0.0045821 | 0.068906 | -61.0748 | 62.0911 | -61.1023 | -61.1481 | 61.9125 | 0.24261 | 0.11902 | 0.022888 | 62.0407 | -61.1481 | -0.19226 | 0.068664 | -0.16479 | -0.23804 | -0.10986 | -0.23804 | 0.01831 | 0.027466 | 61.0291 | 60.9329 | 122.8226 | 123.0011 | -0.16479 | 122.9507 | 61.1526 | -0.23804 | 123.0011 | -0.16479 | 61.1526 | 122.8226 | 122.9507 | -123.1247 | -123.1705
631.7812 | 123.1247 | -60.9009 | 62.027 | -0.04982 | -0.0028754 | -0.0021575 | 0.0045566 | 0.067155 | -0.0039413 | 0.069547 | -60.9879 | 62.1094 | -61.1069 | -61.0886 | 61.8576 | 0.086975 | 0.064087 | 0.13733 | 62.0132 | -61.116 | -0.20599 | 0.082397 | -0.086975 | -0.18768 | -0.16937 | -0.21515 | -0.013733 | 0.11902 | 60.965 | 61.0382 | 122.7585 | 123.0103 | -0.086975 | 122.9141 | 60.9879 | -0.21515 | 123.0103 | -0.086975 | 60.9879 | 122.7585 | 122.9141 | -123.1339 | -123.143
632.7812 | 123.0698 | -60.8871 | 62.0407 | -0.17189 | -0.0041572 | -0.0062163 | -0.00078396 | 0.064591 | -0.0035141 | 0.068906 | -61.0428 | 62.0636 | -61.0977 | -61.1389 | 61.821 | 0.064087 | 0.14191 | 0.15106 | 62.0407 | -61.0886 | -0.21057 | 0.022889 | -0.15564 | -0.25177 | -0.21973 | -0.20142 | 0 | 0.054931 | 61.0291 | 61.0382 | 122.7081 | 122.9507 | -0.15564 | 122.9279 | 60.9512 | -0.20142 | 122.9507 | -0.15564 | 60.9512 | 122.7081 | 122.9279 | -123.1384 | -123.1293
633.7812 | 123.0652 | -60.9283 | 61.9812 | 0.21721 | -0.00052559 | -0.00066214 | 0.0049838 | 0.064805 | -0.0020187 | 0.070402 | -61.0886 | 62.0499 | -61.1572 | -61.2122 | 61.7432 | -0.068665 | 0.013733 | 0.009155 | 61.9904 | -61.1389 | -0.22888 | 0.068665 | -0.16022 | -0.28381 | -0.23804 | -0.21057 | 0.009155 | 0.068665 | 60.9421 | 60.9375 | 122.6715 | 122.9782 | -0.16022 | 122.9187 | 60.8597 | -0.21057 | 122.9782 | -0.16022 | 60.8597 | 122.6715 | 122.9187 | -123.1384 | -123.1201
634.7812 | 123.1384 | -60.91 | 61.9949 | 0.23247 | -0.00052559 | -0.0027985 | 0.003702 | 0.066727 | -0.00030975 | 0.068479 | -61.0748 | 62.0636 | -61.1343 | -61.1755 | 61.7615 | -0.018311 | -0.059509 | 0.022888 | 61.9629 | -61.1298 | -0.2243 | 0.068665 | -0.16479 | -0.2655 | -0.23346 | -0.21973 | -0.032043 | 0.059509 | 60.8505 | 60.9329 | 122.6715 | 122.9736 | -0.16479 | 122.8729 | 60.8917 | -0.21973 | 122.9736 | -0.16479 | 60.8917 | 122.6715 | 122.8729 | -123.1293 | -123.1247
635.7812 | 123.0927 | -60.8688 | 62.0361 | -0.17189 | -0.004798 | -0.0053619 | -0.00078396 | 0.064164 | -0.0030869 | 0.068906 | -61.0107 | 62.0407 | -61.084 | -61.0977 | 61.8484 | 0.10529 | 0.10071 | 0.19226 | 62.027 | -61.1023 | -0.21515 | 0.004577 | -0.14191 | -0.22888 | -0.18768 | -0.23346 | -0.009155 | 0.073242 | 60.9695 | 61.0611 | 122.7173 | 122.9095 | -0.14191 | 122.8958 | 60.9741 | -0.23346 | 122.9095 | -0.14191 | 60.9741 | 122.7173 | 122.8958 | -123.1201 | -123.1384
636.7812 | 123.1201 | -60.8917 | 62.0132 | -0.11848 | -0.0011664 | -0.0055755 | 0.0024202 | 0.062241 | -0.0024459 | 0.06912 | -61.0565 | 62.1094 | -61.1023 | -61.1389 | 61.8118 | 0.054932 | 0.13733 | 0.13733 | 62.0316 | -61.1252 | -0.21057 | 0.09613 | -0.16479 | -0.24719 | -0.20142 | -0.23346 | 0.01831 | 0.045776 | 61.0291 | 61.0291 | 122.7036 | 123.0011 | -0.16479 | 122.9233 | 60.9467 | -0.23346 | 123.0011 | -0.16479 | 60.9467 | 122.7036 | 122.9233 | -123.1155 | -123.1384
637.7812 | 123.0743 | -60.91 | 61.9904 | 0.034104 | -0.00031179 | -0.0049347 | 0.0073336 | 0.066087 | -0.0020187 | 0.069547 | -61.0245 | 62.0956 | -61.1069 | -61.1435 | 61.7798 | 0 | 0.059509 | 0.064087 | 62.0178 | -61.1481 | -0.19684 | 0.10529 | -0.11444 | -0.23346 | -0.21057 | -0.23804 | 0.027466 | 0.082398 | 60.9695 | 60.9741 | 122.6898 | 123.0057 | -0.11444 | 122.9279 | 60.91 | -0.23804 | 123.0057 | -0.11444 | 60.91 | 122.6898 | 122.9279 | -123.0972 | -123.1384
638.7656 | 123.1338 | -60.8963 | 61.972 | 0.2935 | -0.0043708 | -2.1336e-05 | -0.00057036 | 0.067155 | -0.0020187 | 0.068479 | -61.0657 | 62.0224 | -61.1435 | -61.1618 | 61.7889 | -0.013733 | -0.086975 | 0.054932 | 61.9812 | -61.1114 | -0.24719 | 0.050354 | -0.16937 | -0.2655 | -0.18311 | -0.21515 | 0.009155 | 0.07782 | 60.8093 | 60.9512 | 122.6852 | 122.9187 | -0.16937 | 122.8775 | 60.8826 | -0.21515 | 122.9187 | -0.16937 | 60.8826 | 122.6852 | 122.8775 | -123.1155 | -123.0835
639.7812 | 123.1705 | -60.8643 | 61.9812 | 0.10277 | -0.0028754 | -0.0045075 | -0.00078396 | 0.065018 | -0.0020187 | 0.065916 | -61.0428 | 62.0499 | -61.0565 | -61.1618 | 61.8256 | 0.045776 | -0.036621 | 0.13733 | 61.9949 | -61.1114 | -0.19226 | 0.068665 | -0.17853 | -0.29755 | -0.15564 | -0.24719 | 0.013733 | 0.013733 | 60.8276 | 61.0016 | 122.6898 | 122.9141 | -0.17853 | 122.8592 | 60.91 | -0.24719 | 122.9141 | -0.17853 | 60.91 | 122.6898 | 122.8592 | -123.0377 | -123.0927
640.7812 | 123.111 | -60.8963 | 62.0087 | -0.13374 | -0.0043708 | -0.00044854 | 0.0049838 | 0.063737 | -0.0026595 | 0.068052 | -61.0199 | 62.0956 | -61.1252 | -61.1069 | 61.821 | 0.07782 | 0.082397 | 0.13275 | 62.0316 | -61.116 | -0.22888 | 0.086975 | -0.1236 | -0.21057 | -0.18768 | -0.21973 | 0.022888 | 0.10529 | 60.9787 | 61.0291 | 122.7173 | 122.9919 | -0.1236 | 122.9279 | 60.9741 | -0.21973 | 122.9919 | -0.1236 | 60.9741 | 122.7173 | 122.9279 | -123.1338 | -123.1247
641.7812 | 123.0606 | -60.9146 | 62.0087 | 0.23247 | -0.0018072 | -0.0047211 | 0.0041292 | 0.065018 | -0.0028731 | 0.069974 | -61.0703 | 62.0773 | -61.1298 | -61.4365 | 61.6013 | 0.036621 | 0.045776 | 0.064087 | 62.0407 | -61.1343 | -0.21515 | 0.068665 | -0.15564 | -0.52185 | -0.40741 | -0.21973 | 0.032043 | 0.05951 | 60.9604 | 60.9787 | 122.5159 | 122.9919 | -0.15564 | 122.9553 | 60.9512 | -0.21973 | 122.9919 | -0.15564 | 60.9512 | 122.5159 | 122.9553 | -123.1384 | -123.143
642.7812 | 123.0652 | -60.9146 | 61.9949 | 0.11803 | -0.0018072 | -0.0064301 | 0.0039156 | 0.065873 | -0.0037277 | 0.067624 | -61.0703 | 62.0636 | -61.1206 | -61.1938 | 61.7477 | -0.059509 | 0.050354 | -0.013733 | 62.0407 | -61.1618 | -0.20599 | 0.068665 | -0.15564 | -0.27924 | -0.24719 | -0.24719 | 0.045776 | 0.050354 | 60.965 | 60.9009 | 122.6624 | 122.9782 | -0.15564 | 122.9553 | 60.8551 | -0.24719 | 122.9782 | -0.15564 | 60.8551 | 122.6624 | 122.9553 | -123.1155 | -123.1567
643.7656 | 123.0469 | -60.91 | 62.0132 | 0.1638 | -0.0026618 | -0.0083527 | 0.0051974 | 0.066514 | -0.0041549 | 0.070615 | -61.0565 | 62.059 | -61.1343 | -61.1984 | 61.7432 | -0.045776 | 0.036621 | -0.004578 | 62.0316 | -61.1435 | -0.2243 | 0.045776 | -0.14648 | -0.28839 | -0.27008 | -0.23346 | 0.01831 | 0.077819 | 60.9467 | 60.9055 | 122.6532 | 122.9691 | -0.14648 | 122.9416 | 60.8643 | -0.23346 | 122.9691 | -0.14648 | 60.8643 | 122.6532 | 122.9416 | -123.1476 | -123.1567
644.7812 | 123.1064 | -60.9055 | 62.0224 | 0.049362 | -0.0024482 | 0.0010467 | 0.004343 | 0.066941 | -0.0058639 | 0.068479 | -61.0428 | 62.0453 | -61.1343 | -61.1252 | 61.8118 | 0.045776 | 0.045776 | 0.13275 | 62.0087 | -61.1252 | -0.22888 | 0.022888 | -0.13733 | -0.21973 | -0.21057 | -0.21973 | -0.013733 | 0.091552 | 60.9512 | 61.0382 | 122.7173 | 122.9507 | -0.13733 | 122.9141 | 60.9512 | -0.21973 | 122.9507 | -0.13733 | 60.9512 | 122.7173 | 122.9141 | -123.1567 | -123.1476
645.7812 | 123.0743 | -60.9146 | 61.9858 | 0.072251 | -0.003089 | -0.0023711 | 7.0444e-05 | 0.066087 | -0.0024459 | 0.069333 | -61.0748 | 62.0636 | -61.1435 | -61.1938 | 61.7615 | -0.027466 | -0.009155 | 0.013733 | 61.972 | -61.1801 | -0.22888 | 0.07782 | -0.16022 | -0.27924 | -0.2243 | -0.2655 | -0.013733 | 0.068665 | 60.9055 | 60.9283 | 122.6761 | 122.9782 | -0.16022 | 122.8867 | 60.8871 | -0.2655 | 122.9782 | -0.16022 | 60.8871 | 122.6761 | 122.8867 | -123.1293 | -123.1659
646.7812 | 123.0835 | -60.9192 | 61.9904 | 0.24773 | -0.0020208 | -0.0045075 | 0.0017794 | 0.065659 | -0.0024459 | 0.06912 | -61.0794 | 62.0544 | -61.1481 | -61.1893 | 61.7569 | -0.036621 | -0.027466 | 0.009155 | 62.0178 | -61.1481 | -0.22888 | 0.064087 | -0.16022 | -0.27008 | -0.23346 | -0.22888 | 0.027466 | 0.068664 | 60.8917 | 60.9283 | 122.6761 | 122.9736 | -0.16022 | 122.937 | 60.8826 | -0.22888 | 122.9736 | -0.16022 | 60.8826 | 122.6761 | 122.937 | -123.1384 | -123.1384
647.7812 | 123.1888 | -60.8963 | 61.9537 | 0.30113 | -0.0041572 | -0.0047211 | -0.00099756 | 0.066514 | -0.0030869 | 0.067624 | -61.0199 | 62.027 | -61.1023 | -61.1572 | 61.8347 | 0.050354 | -0.15106 | 0.10986 | 61.9675 | -61.1343 | -0.20599 | 0.073243 | -0.1236 | -0.26093 | -0.11902 | -0.23804 | 0.013733 | 0.082398 | 60.7452 | 61.0062 | 122.731 | 122.9233 | -0.1236 | 122.8638 | 60.9467 | -0.23804 | 122.9233 | -0.1236 | 60.9467 | 122.731 | 122.8638 | -123.056 | -123.0881
648.7656 | 123.0652 | -60.9238 | 61.9949 | 0.17143 | -0.0015936 | -0.0036529 | 0.002634 | 0.065446 | -0.0041549 | 0.068479 | -61.0977 | 62.0728 | -61.1343 | -61.2076 | 61.7477 | -0.064087 | 0 | -0.004578 | 62.027 | -61.1572 | -0.21057 | 0.07782 | -0.17395 | -0.28381 | -0.24719 | -0.23346 | 0.032044 | 0.036621 | 60.9238 | 60.9192 | 122.6715 | 122.9965 | -0.17395 | 122.9507 | 60.8597 | -0.23346 | 122.9965 | -0.17395 | 60.8597 | 122.6715 | 122.9507 | -123.1293 | -123.1522
649.7812 | 123.1064 | -60.9146 | 61.9675 | 0.25536 | -0.0018072 | 0.00061946 | 0.003702 | 0.064591 | 0.00033105 | 0.070829 | -61.0748 | 62.0544 | -61.1435 | -61.1801 | 61.7615 | -0.027466 | -0.068665 | 0.027466 | 61.9675 | -61.171 | -0.22888 | 0.086975 | -0.16022 | -0.2655 | -0.20599 | -0.25635 | 0 | 0.068665 | 60.8459 | 60.9421 | 122.6761 | 122.9691 | -0.16022 | 122.8821 | 60.8871 | -0.25635 | 122.9691 | -0.16022 | 60.8871 | 122.6761 | 122.8821 | -123.111 | -123.1384
650.7812 | 123.1705 | -60.9009 | 61.9766 | 0.2935 | -0.0020208 | -0.0021575 | 0.0017794 | 0.06395 | -0.0039413 | 0.070615 | -61.0748 | 62.0682 | -61.1298 | -61.1801 | 61.7706 | -0.022888 | -0.091553 | 0.027466 | 61.9766 | -61.1893 | -0.22888 | 0.091552 | -0.17395 | -0.27924 | -0.20599 | -0.28839 | 0 | 0.054932 | 60.8093 | 60.9283 | 122.6715 | 122.9691 | -0.17395 | 122.8775 | 60.878 | -0.28839 | 122.9691 | -0.17395 | 60.878 | 122.6715 | 122.8775 | -123.1064 | -123.1659
651.7812 | 123.2025 | -60.8963 | 61.9446 | 0.23247 | -0.0043708 | 0.0016877 | -0.00057036 | 0.065659 | -0.0015915 | 0.06912 | -60.9879 | 61.9858 | -61.0931 | -61.1023 | 61.8484 | 0.045776 | -0.17853 | 0.10986 | 61.972 | -61.1389 | -0.19684 | 0.041199 | -0.091553 | -0.20599 | -0.09613 | -0.24262 | 0.027466 | 0.10529 | 60.7178 | 61.0062 | 122.7448 | 122.8821 | -0.091553 | 122.8683 | 60.9421 | -0.24262 | 122.8821 | -0.091553 | 60.9421 | 122.7448 | 122.8683 | -123.0377 | -123.0835
652.7656 | 123.2117 | -60.8963 | 61.972 | 0.35454 | -0.0039434 | -0.0025847 | 0.0022066 | 0.065018 | -0.0015915 | 0.06912 | -61.0107 | 62.0453 | -61.1069 | -61.1069 | 61.8347 | 0.032043 | -0.17853 | 0.11444 | 61.9537 | -61.1618 | -0.21057 | 0.073242 | -0.11444 | -0.21057 | -0.13733 | -0.2655 | -0.018311 | 0.096131 | 60.7178 | 61.0107 | 122.731 | 122.9416 | -0.11444 | 122.85 | 60.9283 | -0.2655 | 122.9416 | -0.11444 | 60.9283 | 122.731 | 122.85 | -123.0789 | -123.1338
653.7812 | 123.1613 | -60.8963 | 61.9812 | 0.17143 | -0.0028754 | -0.0038665 | -0.0016386 | 0.062669 | -0.0018051 | 0.068906 | -61.0428 | 62.0407 | -61.084 | -61.1298 | 61.8118 | 0.027466 | -0.10529 | 0.091553 | 61.9812 | -61.1526 | -0.18768 | 0.059509 | -0.14648 | -0.23346 | -0.16937 | -0.25635 | 0 | 0.041198 | 60.791 | 60.9879 | 122.7081 | 122.937 | -0.14648 | 122.8775 | 60.9238 | -0.25635 | 122.937 | -0.14648 | 60.9238 | 122.7081 | 122.8775 | -123.0652 | -123.1338
654.7812 | 123.1705 | -60.8963 | 61.9629 | 0.18669 | -0.0037298 | -0.0079253 | -0.00014316 | 0.064805 | -0.0041549 | 0.06677 | -61.0153 | 62.0224 | -61.1069 | -61.0794 | 61.8256 | 0.032043 | -0.16479 | 0.1236 | 61.9446 | -61.1526 | -0.21057 | 0.059509 | -0.11902 | -0.18311 | -0.13733 | -0.25635 | -0.018311 | 0.091553 | 60.7315 | 61.0199 | 122.7219 | 122.9187 | -0.11902 | 122.8409 | 60.9283 | -0.25635 | 122.9187 | -0.11902 | 60.9283 | 122.7219 | 122.8409 | -123.0698 | -123.1155
655.7812 | 123.1705 | -60.8963 | 61.9629 | 0.21721 | -0.0028754 | -0.0040801 | 0.00092504 | 0.063737 | -0.0028731 | 0.070829 | -60.9879 | 62.027 | -61.0931 | -61.1023 | 61.8347 | 0.036621 | -0.15564 | 0.11902 | 61.972 | -61.1572 | -0.19684 | 0.064087 | -0.091553 | -0.20599 | -0.12817 | -0.26093 | 0.009155 | 0.10529 | 60.7407 | 61.0153 | 122.731 | 122.9233 | -0.091553 | 122.8683 | 60.9329 | -0.26093 | 122.9233 | -0.091553 | 60.9329 | 122.731 | 122.8683 | -123.056 | -123.1201
656.7656 | 123.1705 | -60.91 | 61.9766 | 0.095139 | 0.00054261 | -0.0060027 | 7.0444e-05 | 0.062241 | -0.0018051 | 0.069974 | -61.0291 | 62.0407 | -61.1023 | -61.1252 | 61.9034 | 0.14191 | -0.082397 | 0.11444 | 62.0041 | -61.1114 | -0.19226 | 0.064086 | -0.11902 | -0.21515 | -0.073243 | -0.20142 | 0.027465 | 0.073242 | 60.8276 | 61.0245 | 122.8134 | 122.9507 | -0.11902 | 122.9141 | 61.0519 | -0.20142 | 122.9507 | -0.11902 | 61.0519 | 122.8134 | 122.9141 | -123.0789 | -123.0881
657.7656 | 123.1613 | -60.9192 | 61.9766 | 0.095139 | -0.0045844 | -0.0079253 | -0.001425 | 0.060105 | -0.0030869 | 0.069333 | -61.0474 | 62.0407 | -61.084 | -61.1526 | 61.8347 | 0.050354 | -0.07782 | 0.13733 | 61.9629 | -61.1389 | -0.16479 | 0.064086 | -0.12817 | -0.23346 | -0.14191 | -0.21973 | -0.013733 | 0.036621 | 60.8414 | 61.0565 | 122.7539 | 122.9599 | -0.12817 | 122.8821 | 60.9695 | -0.21973 | 122.9599 | -0.12817 | 60.9695 | 122.7539 | 122.8821 | -123.0606 | -123.1155
658.7812 | 123.2025 | -60.8871 | 61.9812 | 0.30113 | -0.0028754 | -0.0025847 | 0.003702 | 0.064164 | -0.0011643 | 0.068693 | -60.8963 | 62.0178 | -61.1023 | -61.0657 | 61.8393 | 0.045776 | -0.18768 | 0.11444 | 61.9354 | -61.1526 | -0.21515 | 0.036621 | -0.009155 | -0.17853 | -0.14191 | -0.2655 | -0.045776 | 0.20599 | 60.6995 | 61.0016 | 122.7264 | 122.905 | -0.009155 | 122.8226 | 60.9329 | -0.2655 | 122.905 | -0.009155 | 60.9329 | 122.7264 | 122.8226 | -123.0835 | -123.1338
659.7812 | 123.1888 | -60.8734 | 61.9766 | 0.049362 | -0.0035162 | -0.0023711 | -0.0022794 | 0.059891 | -0.0013779 | 0.068265 | -61.0428 | 62.0224 | -61.1023 | -61.0931 | 61.8301 | 0.054932 | -0.064087 | 0.16022 | 61.9583 | -61.1481 | -0.22888 | 0.045776 | -0.16937 | -0.21973 | -0.14648 | -0.27466 | -0.018311 | 0.059509 | 60.8093 | 61.0336 | 122.7036 | 122.8958 | -0.16937 | 122.8317 | 60.9283 | -0.27466 | 122.8958 | -0.16937 | 60.9283 | 122.7036 | 122.8317 | -123.0789 | -123.1247
660.7656 | 123.2025 | -60.8826 | 61.972 | 0.36217 | -0.0024482 | -0.0023711 | 0.0056246 | 0.065232 | -0.0024459 | 0.065916 | -60.965 | 62.0316 | -61.1023 | -61.0703 | 61.8301 | 0.032043 | -0.19226 | 0.10529 | 61.9583 | -61.1343 | -0.21973 | 0.059509 | -0.082398 | -0.18768 | -0.14191 | -0.25177 | -0.013733 | 0.13733 | 60.6903 | 60.9879 | 122.7127 | 122.9141 | -0.082398 | 122.8409 | 60.9146 | -0.25177 | 122.9141 | -0.082398 | 60.9146 | 122.7127 | 122.8409 | -123.0743 | -123.1064
661.7656 | 123.1293 | -60.8459 | 61.9858 | -0.11848 | -0.0056524 | -0.0013031 | -0.00014316 | 0.063309 | -0.0035141 | 0.069761 | -60.9467 | 62.0361 | -61.0748 | -61.0245 | 61.9125 | 0.16479 | -0.041199 | 0.40283 | 62.0178 | -61.1206 | -0.22888 | 0.050354 | -0.10071 | -0.17853 | -0.073242 | -0.27466 | 0.032043 | 0.12817 | 60.8047 | 61.2488 | 122.7585 | 122.8821 | -0.10071 | 122.8638 | 61.0107 | -0.27466 | 122.8821 | -0.10071 | 61.0107 | 122.7585 | 122.8638 | -123.0606 | -123.1064
662.7656 | 123.1659 | -60.8871 | 61.9766 | 0.19432 | -0.0050116 | -0.0049347 | 0.0022066 | 0.062241 | -0.0011643 | 0.068693 | -61.0153 | 62.0407 | -61.0977 | -61.1114 | 61.8027 | 0.032043 | -0.10986 | 0.09613 | 61.9583 | -61.1481 | -0.21057 | 0.064086 | -0.12817 | -0.2243 | -0.17395 | -0.26093 | -0.018311 | 0.082397 | 60.7773 | 60.9833 | 122.6898 | 122.9279 | -0.12817 | 122.8455 | 60.9192 | -0.26093 | 122.9279 | -0.12817 | 60.9192 | 122.6898 | 122.8455 | -123.0743 | -123.1247
663.7656 | 123.1796 | -60.91 | 61.9354 | 0.22484 | -0.0028754 | 0.0010467 | 0.003702 | 0.063096 | -0.0039413 | 0.067411 | -60.9787 | 62.027 | -61.1023 | -61.0611 | 61.853 | 0.045776 | -0.20599 | 0.11444 | 61.9354 | -61.1435 | -0.19226 | 0.091553 | -0.068665 | -0.15106 | -0.082398 | -0.23346 | 0 | 0.1236 | 60.704 | 61.0245 | 122.7631 | 122.937 | -0.068665 | 122.8455 | 60.9558 | -0.23346 | 122.937 | -0.068665 | 60.9558 | 122.7631 | 122.8455 | -123.0377 | -123.0789
664.7656 | 123.175 | -60.8871 | 61.972 | 0.2401 | -0.0045844 | -0.0030121 | 0.0013522 | 0.06395 | -0.0020187 | 0.070615 | -61.0107 | 62.0087 | -61.0977 | -61.0931 | 61.8301 | 0.041199 | -0.16022 | 0.10986 | 61.9308 | -61.1664 | -0.21057 | 0.036621 | -0.1236 | -0.20599 | -0.14191 | -0.27924 | -0.041199 | 0.086975 | 60.7269 | 60.997 | 122.7173 | 122.8958 | -0.1236 | 122.818 | 60.9283 | -0.27924 | 122.8958 | -0.1236 | 60.9283 | 122.7173 | 122.818 | -123.0698 | -123.1384
665.7656 | 123.1979 | -60.8826 | 61.9904 | -0.019302 | -0.0039434 | -0.0017303 | -0.0012112 | 0.062241 | -0.00052335 | 0.069333 | -61.0016 | 62.0407 | -61.1114 | -61.0428 | 61.8759 | 0.11444 | -0.07782 | 0.21057 | 61.9766 | -61.1343 | -0.22888 | 0.050354 | -0.11902 | -0.16022 | -0.11444 | -0.25177 | -0.013732 | 0.10986 | 60.8047 | 61.0931 | 122.7585 | 122.9233 | -0.11902 | 122.8592 | 60.997 | -0.25177 | 122.9233 | -0.11902 | 60.997 | 122.7585 | 122.8592 | -123.1018 | -123.1247
666.7656 | 123.2117 | -60.8597 | 61.9949 | -0.026932 | -0.0024482 | -0.0032257 | -0.00035676 | 0.061387 | 0.00011745 | 0.068479 | -60.9787 | 62.0316 | -61.0886 | -61.0428 | 61.8668 | 0.14191 | -0.064087 | 0.23346 | 61.9766 | -61.116 | -0.22888 | 0.036621 | -0.11902 | -0.18311 | -0.12817 | -0.25635 | -0.01831 | 0.10986 | 60.7956 | 61.0931 | 122.7264 | 122.8912 | -0.11902 | 122.8363 | 61.0016 | -0.25635 | 122.8912 | -0.11902 | 61.0016 | 122.7264 | 122.8363 | -123.0835 | -123.111
667.7656 | 123.0835 | -60.8826 | 62.0407 | -0.21004 | -0.0045844 | -0.0045075 | 0.0034884 | 0.060532 | -0.0026595 | 0.06912 | -61.0336 | 62.0728 | -61.1023 | -61.1252 | 61.8027 | 0.041199 | 0.13275 | 0.15106 | 62.0499 | -61.1481 | -0.21973 | 0.032044 | -0.15106 | -0.24262 | -0.23804 | -0.2655 | 0.009156 | 0.068665 | 61.0153 | 61.0336 | 122.6852 | 122.9553 | -0.15106 | 122.9324 | 60.9238 | -0.2655 | 122.9553 | -0.15106 | 60.9238 | 122.6852 | 122.9324 | -123.143 | -123.1888
668.7656 | 123.1613 | -60.8917 | 61.9492 | 0.2401 | -0.005866 | -0.0060027 | 0.0013522 | 0.063309 | -0.0037277 | 0.068265 | -60.997 | 62.027 | -61.1069 | -61.084 | 61.8439 | 0.032043 | -0.15106 | 0.10986 | 61.9583 | -61.116 | -0.21515 | 0.07782 | -0.10528 | -0.19226 | -0.10529 | -0.2243 | 0.009155 | 0.10986 | 60.7407 | 61.0016 | 122.7356 | 122.9187 | -0.10528 | 122.85 | 60.9238 | -0.2243 | 122.9187 | -0.10528 | 60.9238 | 122.7356 | 122.85 | -123.056 | -123.0652
669.7656 | 123.1476 | -60.9055 | 61.9583 | 0.23247 | -0.0043708 | -0.0083527 | 0.0024202 | 0.063309 | 0.00011745 | 0.070829 | -61.0107 | 62.0041 | -61.1298 | -61.1114 | 61.8347 | 0.018311 | -0.14191 | 0.10071 | 61.9308 | -61.1389 | -0.2243 | 0.045776 | -0.10529 | -0.20599 | -0.1236 | -0.23346 | -0.027466 | 0.11902 | 60.7635 | 61.0062 | 122.7402 | 122.9095 | -0.10529 | 122.8363 | 60.9238 | -0.23346 | 122.9095 | -0.10529 | 60.9238 | 122.7402 | 122.8363 | -123.0881 | -123.0972
670.7656 | 123.1522 | -60.91 | 62.0087 | 0.17906 | -0.0050116 | -0.0042937 | 0.00092504 | 0.061173 | -9.6146e-05 | 0.068906 | -61.0291 | 62.0224 | -61.1069 | -61.1252 | 61.8164 | 0.032043 | -0.11444 | 0.09613 | 61.94 | -61.1481 | -0.19684 | 0.013733 | -0.11902 | -0.21515 | -0.19226 | -0.23804 | -0.068665 | 0.07782 | 60.7956 | 61.0062 | 122.7264 | 122.9324 | -0.11902 | 122.85 | 60.9421 | -0.23804 | 122.9324 | -0.11902 | 60.9421 | 122.7264 | 122.85 | -123.1155 | -123.1567
671.7656 | 123.1705 | -60.8917 | 61.9949 | 0.049362 | -0.0035162 | -0.0077117 | -0.001425 | 0.06395 | -0.0024459 | 0.069974 | -61.0474 | 62.0316 | -61.0977 | -60.9879 | 61.8713 | 0.059509 | -0.050354 | 0.10986 | 61.9766 | -61.116 | -0.20599 | 0.036621 | -0.15564 | -0.09613 | -0.1236 | -0.2243 | -0.01831 | 0.050354 | 60.8414 | 61.0016 | 122.7631 | 122.9233 | -0.15564 | 122.8683 | 60.9512 | -0.2243 | 122.9233 | -0.15564 | 60.9512 | 122.7631 | 122.8683 | -123.0927 | -123.111
672.7656 | 123.1888 | -60.878 | 61.9675 | -0.087967 | -0.0054388 | -0.0040801 | 0.003702 | 0.061814 | -0.0024459 | 0.068906 | -60.9512 | 61.9949 | -61.1023 | -61.084 | 61.8484 | 0.027466 | -0.16937 | 0.11902 | 61.9446 | -61.1252 | -0.2243 | 0.027466 | -0.073242 | -0.20599 | -0.11902 | -0.24719 | -0.022888 | 0.15106 | 60.7086 | 60.997 | 122.7264 | 122.8729 | -0.073242 | 122.8226 | 60.9055 | -0.24719 | 122.8729 | -0.073242 | 60.9055 | 122.7264 | 122.8226 | -123.0698 | -123.0927
673.7656 | 123.2162 | -60.8643 | 61.9858 | 0.018845 | -0.005866 | -0.0045075 | -0.00099756 | 0.06096 | -0.0030869 | 0.067838 | -61.0153 | 61.9995 | -61.1343 | -61.0474 | 61.8942 | 0.1236 | -0.073242 | 0.2243 | 61.9766 | -61.0977 | -0.27008 | 0.013733 | -0.15106 | -0.1831 | -0.091553 | -0.23346 | -0.009155 | 0.11902 | 60.791 | 61.0886 | 122.7585 | 122.8638 | -0.15106 | 122.8409 | 60.9879 | -0.23346 | 122.8638 | -0.15106 | 60.9879 | 122.7585 | 122.8409 | -123.1201 | -123.0835
674.7656 | 123.2208 | -60.8734 | 61.9858 | -0.04982 | -0.0050116 | -0.0053619 | -0.0016386 | 0.062455 | -0.0035141 | 0.069333 | -60.9741 | 61.9858 | -61.0703 | -61.0382 | 61.9125 | 0.14191 | -0.064087 | 0.23346 | 61.9949 | -61.0794 | -0.19684 | 0 | -0.10071 | -0.16479 | -0.073242 | -0.20599 | 0.009155 | 0.09613 | 60.8093 | 61.1069 | 122.7859 | 122.8592 | -0.10071 | 122.8683 | 61.0153 | -0.20599 | 122.8592 | -0.10071 | 61.0153 | 122.7859 | 122.8683 | -123.056 | -123.0652
675.7656 | 123.0927 | -60.8688 | 62.0224 | -0.15663 | -0.004798 | -0.0030121 | 0.0049838 | 0.062241 | -0.0056503 | 0.067624 | -61.0428 | 62.0316 | -61.1069 | -61.1252 | 61.8027 | 0.054932 | 0.15106 | 0.1236 | 62.0544 | -61.1114 | -0.23804 | 0.009155 | -0.17395 | -0.25635 | -0.21973 | -0.24262 | 0.032043 | 0.064087 | 61.0199 | 60.9924 | 122.6715 | 122.9004 | -0.17395 | 122.9233 | 60.9238 | -0.24262 | 122.9004 | -0.17395 | 60.9238 | 122.6715 | 122.9233 | -123.1293 | -123.1338
676.7656 | 123.1522 | -60.8917 | 62.0041 | 0.072251 | -0.0050116 | -0.0068573 | -0.00035676 | 0.062669 | -0.0043685 | 0.068479 | -61.0336 | 61.9812 | -61.0886 | -61.1252 | 61.821 | 0.036621 | -0.07782 | 0.10986 | 61.9858 | -61.084 | -0.19684 | -0.022888 | -0.14191 | -0.23346 | -0.1831 | -0.19226 | -0.01831 | 0.054932 | 60.8139 | 61.0016 | 122.7127 | 122.8729 | -0.14191 | 122.8775 | 60.9283 | -0.19226 | 122.8729 | -0.14191 | 60.9283 | 122.7127 | 122.8775 | -123.0927 | -123.0881
677.7812 | 123.1934 | -60.8734 | 61.9949 | 0.018845 | -0.004798 | -0.0062163 | -0.00014316 | 0.063737 | -0.0056503 | 0.06912 | -61.0291 | 61.9904 | -61.0886 | -61.084 | 61.8439 | 0.073242 | -0.059509 | 0.16937 | 61.972 | -61.0657 | -0.21515 | -0.004578 | -0.15564 | -0.21057 | -0.15106 | -0.19226 | -0.022888 | 0.059509 | 60.8139 | 61.0428 | 122.7173 | 122.8638 | -0.15564 | 122.8455 | 60.9467 | -0.19226 | 122.8638 | -0.15564 | 60.9467 | 122.7173 | 122.8455 | -123.0835 | -123.0606
678.7656 | 123.1522 | -60.8871 | 61.9858 | 0.17906 | -0.0050116 | -0.0062163 | 0.0032748 | 0.062455 | -0.0045821 | 0.068693 | -61.0428 | 61.9858 | -61.1114 | -61.1252 | 61.8301 | 0.018311 | -0.11444 | 0.086975 | 61.9354 | -61.1389 | -0.2243 | 0 | -0.15564 | -0.23804 | -0.15564 | -0.25177 | -0.050354 | 0.068664 | 60.7727 | 60.9741 | 122.7173 | 122.8729 | -0.15564 | 122.8226 | 60.9055 | -0.25177 | 122.8729 | -0.15564 | 60.9055 | 122.7173 | 122.8226 | -123.0972 | -123.1247
679.7812 | 123.1796 | -60.878 | 62.0132 | -0.49995 | -0.00138 | -0.0036529 | 0.00092504 | 0.063096 | -0.0054367 | 0.066343 | -61.1114 | 61.9766 | -61.0886 | -61.0519 | 61.8942 | 0.16479 | -0.036621 | 0.24719 | 61.9812 | -61.0611 | -0.21057 | -0.036621 | -0.23346 | -0.17395 | -0.11902 | -0.1831 | -0.032044 | -0.022888 | 60.8414 | 61.1252 | 122.7722 | 122.8546 | -0.23346 | 122.8592 | 61.0428 | -0.1831 | 122.8546 | -0.23346 | 61.0428 | 122.7722 | 122.8592 | -123.1018 | -123.0743
680.7812 | 123.1888 | -60.8505 | 61.9949 | 0.34691 | -0.0043708 | -0.0057891 | 0.0017794 | 0.063096 | -0.0047957 | 0.067197 | -60.9833 | 61.9812 | -61.0748 | -61.0382 | 61.9034 | 0.13275 | -0.027466 | 0.23804 | 61.9583 | -61.0657 | -0.2243 | -0.013733 | -0.13275 | -0.18768 | -0.091553 | -0.21515 | -0.036621 | 0.091553 | 60.8231 | 61.0886 | 122.7539 | 122.8317 | -0.13275 | 122.8088 | 60.9833 | -0.21515 | 122.8317 | -0.13275 | 60.9833 | 122.7539 | 122.8088 | -123.0698 | -123.0606
681.7812 | 123.1338 | -60.8963 | 62.0361 | -0.14137 | -0.003089 | -0.0045075 | 0.0081882 | 0.062241 | -0.0045821 | 0.06912 | -61.0245 | 62.0316 | -61.1252 | -61.116 | 61.8164 | 0.064087 | 0.12817 | 0.14191 | 62.0041 | -61.0977 | -0.22888 | -0.004578 | -0.12817 | -0.21973 | -0.21973 | -0.20142 | -0.032044 | 0.10071 | 61.0245 | 61.0382 | 122.7127 | 122.9279 | -0.12817 | 122.9004 | 60.9604 | -0.20142 | 122.9279 | -0.12817 | 60.9604 | 122.7127 | 122.9004 | -123.1613 | -123.1338
682.7812 | 123.0972 | -60.9009 | 62.0453 | -0.17189 | -0.0050116 | 0.0027557 | 0.004343 | 0.063309 | -0.0037277 | 0.069547 | -61.0611 | 62.0728 | -61.1252 | -61.1481 | 61.7798 | 0.045776 | 0.13275 | 0.11902 | 62.0453 | -61.1023 | -0.2243 | 0.027466 | -0.16022 | -0.24719 | -0.2655 | -0.20142 | 0 | 0.064087 | 61.0336 | 61.0199 | 122.6807 | 122.9736 | -0.16022 | 122.9462 | 60.9467 | -0.20142 | 122.9736 | -0.16022 | 60.9467 | 122.6807 | 122.9462 | -123.1705 | -123.1476
683.7656 | 123.2025 | -60.8414 | 61.9949 | -0.034561 | -0.0054388 | -0.0060027 | -0.0016386 | 0.064164 | -0.0035141 | 0.068693 | -60.9879 | 61.9812 | -61.0886 | -61.0291 | 61.9171 | 0.14648 | -0.064087 | 0.24261 | 61.9858 | -61.0428 | -0.24719 | -0.013733 | -0.14648 | -0.18768 | -0.07782 | -0.20142 | -0.009155 | 0.10071 | 60.7773 | 61.084 | 122.7585 | 122.8226 | -0.14648 | 122.8271 | 60.9879 | -0.20142 | 122.8226 | -0.14648 | 60.9879 | 122.7585 | 122.8271 | -123.0835 | -123.0377
684.7656 | 123.2071 | -60.8688 | 61.9949 | -0.0040434 | -0.005866 | -0.0057891 | -0.00057036 | 0.061387 | -0.0045821 | 0.070615 | -60.9879 | 61.9675 | -61.1023 | -61.0886 | 61.8759 | 0.10986 | -0.059509 | 0.16937 | 61.9766 | -61.0703 | -0.23346 | -0.027466 | -0.11902 | -0.21973 | -0.11902 | -0.20142 | -0.01831 | 0.11444 | 60.8093 | 61.0382 | 122.7448 | 122.8363 | -0.11902 | 122.8455 | 60.9787 | -0.20142 | 122.8363 | -0.11902 | 60.9787 | 122.7448 | 122.8455 | -123.0972 | -123.0652
685.7656 | 123.1842 | -60.8643 | 61.9812 | -0.0040434 | -0.0054388 | -0.0047211 | -0.00014316 | 0.062669 | -0.0052231 | 0.068265 | -61.0062 | 61.9583 | -61.1023 | -61.0748 | 61.8805 | 0.11902 | -0.050354 | 0.21515 | 61.9858 | -61.0794 | -0.23804 | -0.022888 | -0.14191 | -0.21057 | -0.10071 | -0.21515 | 0.004578 | 0.09613 | 60.8139 | 61.0794 | 122.7448 | 122.8226 | -0.14191 | 122.85 | 60.9833 | -0.21515 | 122.8226 | -0.14191 | 60.9833 | 122.7448 | 122.85 | -123.0835 | -123.0606
686.7656 | 123.1247 | -60.8276 | 62.0499 | -0.11848 | -0.0060798 | -0.0034393 | 0.0013522 | 0.06096 | -0.0052231 | 0.069761 | -60.965 | 61.972 | -61.0748 | -61.0199 | 61.9034 | 0.17395 | -0.027466 | 0.33417 | 62.0132 | -61.0657 | -0.24719 | -0.07782 | -0.13733 | -0.19226 | -0.14648 | -0.23804 | -0.036621 | 0.10986 | 60.8002 | 61.1618 | 122.731 | 122.7997 | -0.13733 | 122.8409 | 61.0016 | -0.23804 | 122.7997 | -0.13733 | 61.0016 | 122.731 | 122.8409 | -123.1247 | -123.1155
687.7812 | 123.1476 | -60.8826 | 62.0132 | -0.14137 | -0.0039434 | -0.0036529 | 0.00092504 | 0.061387 | -0.0047957 | 0.067624 | -60.9741 | 62.0132 | -61.0886 | -61.0565 | 61.8805 | 0.14648 | 0.041199 | 0.22888 | 62.0132 | -61.0748 | -0.20599 | 0 | -0.091553 | -0.17395 | -0.13275 | -0.19226 | 0 | 0.11444 | 60.9238 | 61.1114 | 122.7631 | 122.8958 | -0.091553 | 122.8958 | 61.0291 | -0.19226 | 122.8958 | -0.091553 | 61.0291 | 122.7631 | 122.8958 | -123.1018 | -123.0881
688.7812 | 123.1338 | -60.9055 | 62.0453 | -0.14137 | -0.007575 | -0.0045075 | 0.0011386 | 0.062669 | -0.0073593 | 0.06912 | -60.9833 | 62.027 | -61.0886 | -61.0611 | 61.853 | 0.11444 | 0.068665 | 0.19684 | 62.0041 | -61.0794 | -0.18311 | -0.01831 | -0.077819 | -0.15564 | -0.19226 | -0.17395 | -0.041199 | 0.10529 | 60.9741 | 61.1023 | 122.7585 | 122.9324 | -0.077819 | 122.9095 | 61.0199 | -0.17395 | 122.9324 | -0.077819 | 61.0199 | 122.7585 | 122.9095 | -123.1338 | -123.1247
689.7812 | 123.1155 | -60.8917 | 62.0224 | -0.080337 | -0.0071478 | -0.0047211 | 0.0069064 | 0.062669 | -0.0067185 | 0.06912 | -60.997 | 62.027 | -61.1114 | -61.0703 | 61.8301 | 0.073242 | 0.054932 | 0.14191 | 62.027 | -61.0794 | -0.21973 | 0.004578 | -0.10528 | -0.17853 | -0.19226 | -0.18768 | 0.004578 | 0.11444 | 60.9467 | 61.0336 | 122.7219 | 122.9187 | -0.10528 | 122.9187 | 60.965 | -0.18768 | 122.9187 | -0.10528 | 60.965 | 122.7219 | 122.9187 | -123.1338 | -123.1018
690.7812 | 123.0881 | -60.9055 | 62.0087 | -0.13374 | -0.0043708 | -0.0010895 | 0.0032748 | 0.062669 | -0.0050095 | 0.068479 | -61.0153 | 62.0407 | -61.1114 | -61.1023 | 61.821 | 0.068665 | 0.11444 | 0.15564 | 62.027 | -61.0886 | -0.20599 | 0.032043 | -0.10986 | -0.19684 | -0.18768 | -0.18311 | 0.018311 | 0.09613 | 61.0199 | 61.0611 | 122.7264 | 122.9462 | -0.10986 | 122.9324 | 60.9741 | -0.18311 | 122.9462 | -0.10986 | 60.9741 | 122.7264 | 122.9324 | -123.1201 | -123.0972
691.7656 | 123.2391 | -60.8551 | 61.9995 | -0.04219 | -0.0020208 | -0.0040801 | -0.001425 | 0.062028 | -0.0045821 | 0.069547 | -60.9787 | 61.9812 | -61.0748 | -61.0199 | 61.9217 | 0.15106 | -0.068665 | 0.25177 | 61.972 | -61.0428 | -0.21973 | -0.018311 | -0.1236 | -0.16479 | -0.07782 | -0.18768 | -0.027466 | 0.09613 | 60.7864 | 61.1069 | 122.7768 | 122.8363 | -0.1236 | 122.8271 | 61.0062 | -0.18768 | 122.8363 | -0.1236 | 61.0062 | 122.7768 | 122.8271 | -123.0743 | -123.0423
692.7656 | 123.1476 | -60.91 | 62.0361 | -0.17189 | -0.0062934 | -0.0062163 | 0.00071144 | 0.062241 | -0.0065047 | 0.071256 | -61.0016 | 62.0132 | -61.0703 | -61.0886 | 61.8622 | 0.10529 | 0.09613 | 0.16937 | 62.0087 | -61.0931 | -0.16022 | -0.022888 | -0.091553 | -0.17853 | -0.17395 | -0.18311 | -0.027466 | 0.068664 | 61.0062 | 61.0794 | 122.7722 | 122.9233 | -0.091553 | 122.9187 | 61.0153 | -0.18311 | 122.9233 | -0.091553 | 61.0153 | 122.7722 | 122.9187 | -123.1064 | -123.1293
693.7656 | 123.1247 | -60.8963 | 62.0407 | -0.17952 | -0.004798 | -0.0049347 | 0.0030612 | 0.062455 | -0.0056503 | 0.068479 | -61.0107 | 62.027 | -61.0703 | -61.116 | 61.8439 | 0.11444 | 0.13275 | 0.16022 | 62.0453 | -61.1069 | -0.17395 | -0.013732 | -0.11444 | -0.21973 | -0.19684 | -0.21057 | 0.004578 | 0.059509 | 61.0291 | 61.0565 | 122.7402 | 122.9233 | -0.11444 | 122.9416 | 61.0107 | -0.21057 | 122.9233 | -0.11444 | 61.0107 | 122.7402 | 122.9416 | -123.111 | -123.1476
694.7656 | 123.0789 | -60.9009 | 62.0544 | -0.21767 | -0.0033026 | -0.0068573 | 0.0030612 | 0.063309 | -0.0030869 | 0.069974 | -61.0153 | 62.1094 | -61.0794 | -61.1572 | 61.7661 | 0.045776 | 0.11902 | 0.10986 | 62.0682 | -61.1206 | -0.17853 | 0.054932 | -0.11444 | -0.25635 | -0.28839 | -0.21973 | 0.013733 | 0.064087 | 61.0199 | 61.0107 | 122.6669 | 123.0103 | -0.11444 | 122.9691 | 60.9467 | -0.21973 | 123.0103 | -0.11444 | 60.9467 | 122.6669 | 122.9691 | -123.1338 | -123.175
695.7656 | 123.0743 | -60.9055 | 62.0499 | 0.0035856 | -0.0028754 | -0.0040801 | 0.003702 | 0.064378 | -0.0020187 | 0.067411 | -61.0519 | 62.0682 | -61.1069 | -61.1298 | 61.8118 | 0.041199 | 0.12817 | 0.13275 | 62.0316 | -61.1389 | -0.20142 | 0.01831 | -0.14648 | -0.2243 | -0.23804 | -0.23346 | -0.018311 | 0.054932 | 61.0336 | 61.0382 | 122.7173 | 122.9736 | -0.14648 | 122.937 | 60.9467 | -0.23346 | 122.9736 | -0.14648 | 60.9467 | 122.7173 | 122.937 | -123.1567 | -123.1888
696.7656 | 123.1155 | -60.8826 | 62.027 | -0.12611 | -0.00095279 | -0.0034393 | 0.0032748 | 0.064378 | -0.0052231 | 0.068052 | -61.0428 | 62.0911 | -61.1389 | -61.1206 | 61.8118 | 0.086975 | 0.13733 | 0.13275 | 62.0407 | -61.1252 | -0.25635 | 0.064086 | -0.16022 | -0.23804 | -0.21515 | -0.24262 | 0.013732 | 0.09613 | 61.0199 | 61.0153 | 122.6944 | 122.9736 | -0.16022 | 122.9233 | 60.9695 | -0.24262 | 122.9736 | -0.16022 | 60.9695 | 122.6944 | 122.9233 | -123.1659 | -123.1522
697.7656 | 123.1247 | -60.8963 | 62.0132 | -0.11848 | -0.0050116 | -0.0017303 | 0.002634 | 0.064805 | -0.0037277 | 0.06912 | -61.0245 | 62.1002 | -61.116 | -61.1069 | 61.821 | 0.082397 | 0.1236 | 0.13733 | 62.0224 | -61.1389 | -0.21973 | 0.086975 | -0.12817 | -0.21057 | -0.19226 | -0.24262 | 0.009155 | 0.091553 | 61.0199 | 61.0336 | 122.7173 | 122.9965 | -0.12817 | 122.9187 | 60.9787 | -0.24262 | 122.9965 | -0.12817 | 60.9787 | 122.7173 | 122.9187 | -123.1293 | -123.1522
698.7656 | 123.0927 | -60.91 | 62.0224 | -1.4155 | -0.0045844 | -0.0040801 | 0.0024202 | 0.06395 | -0.0018051 | 0.068906 | -61.0336 | 62.1368 | -61.0977 | -61.1481 | 61.7706 | 0.059509 | 0.15564 | 0.1236 | 62.0453 | -61.1526 | -0.18768 | 0.11444 | -0.1236 | -0.23804 | -0.25177 | -0.24261 | 0.022888 | 0.064087 | 61.0657 | 61.0336 | 122.6807 | 123.0469 | -0.1236 | 122.9553 | 60.9695 | -0.24261 | 123.0469 | -0.1236 | 60.9695 | 122.6807 | 122.9553 | -123.1201 | -123.175
699.7656 | 123.1064 | -60.8871 | 62.0178 | -0.11085 | 0.00075621 | -0.0051483 | 0.0041292 | 0.064805 | -0.0033005 | 0.067838 | -61.0062 | 62.1094 | -61.1023 | -61.0977 | 61.8439 | 0.091553 | 0.086975 | 0.14191 | 62.0316 | -61.1206 | -0.21515 | 0.091553 | -0.11902 | -0.21057 | -0.17395 | -0.23346 | 0.013733 | 0.09613 | 60.9741 | 61.0291 | 122.731 | 122.9965 | -0.11902 | 122.9187 | 60.9787 | -0.23346 | 122.9965 | -0.11902 | 60.9787 | 122.731 | 122.9187 | -123.1201 | -123.1384
700.7656 | 123.1201 | -60.8871 | 61.9995 | -0.11848 | -0.0024482 | -0.0057891 | 0.0047702 | 0.065232 | -0.00052335 | 0.068479 | -60.9879 | 62.1094 | -61.0886 | -61.0886 | 61.8393 | 0.086975 | 0.032043 | 0.15106 | 62.0041 | -61.1389 | -0.20142 | 0.10986 | -0.10071 | -0.20142 | -0.16022 | -0.25177 | 0.004577 | 0.10071 | 60.9192 | 61.0382 | 122.7264 | 122.9965 | -0.10071 | 122.8912 | 60.9741 | -0.25177 | 122.9965 | -0.10071 | 60.9741 | 122.7264 | 122.8912 | -123.0881 | -123.1384
701.7656 | 123.0927 | -60.9238 | 61.9949 | 0.8886 | -0.0024482 | -0.0060027 | 0.004343 | 0.065659 | -0.0020187 | 0.06912 | -60.9467 | 62.0911 | -61.1206 | -61.0886 | 61.8439 | 0.07782 | 0.013733 | 0.11444 | 62.0132 | -61.1435 | -0.19684 | 0.09613 | -0.022888 | -0.1648 | -0.15106 | -0.21973 | 0.018311 | 0.17395 | 60.9375 | 61.0382 | 122.7676 | 123.0148 | -0.022888 | 122.937 | 61.0016 | -0.21973 | 123.0148 | -0.022888 | 61.0016 | 122.7676 | 122.937 | -123.1155 | -123.1384
702.7656 | 123.0972 | -60.8917 | 61.9904 | -0.0040434 | -0.0039434 | -0.0030121 | 0.0058382 | 0.065659 | -0.0020187 | 0.068265 | -60.997 | 62.1231 | -61.1206 | -61.1252 | 61.821 | 0.050354 | 0.022888 | 0.11902 | 61.9949 | -61.171 | -0.22888 | 0.13275 | -0.10528 | -0.23346 | -0.16937 | -0.27923 | 0.004578 | 0.1236 | 60.9146 | 61.0107 | 122.7127 | 123.0148 | -0.10528 | 122.8867 | 60.9421 | -0.27923 | 123.0148 | -0.10528 | 60.9421 | 122.7127 | 122.8867 | -123.111 | -123.1613
703.7656 | 123.0972 | -60.9146 | 61.9995 | -0.011673 | -0.0022346 | -0.00066214 | 0.0028476 | 0.066941 | -0.0028731 | 0.067624 | -61.0153 | 62.1002 | -61.1206 | -61.1298 | 61.8027 | 0.032043 | 0.022888 | 0.082397 | 62.0178 | -61.1618 | -0.20599 | 0.10071 | -0.10071 | -0.21515 | -0.19684 | -0.24719 | 0.01831 | 0.10528 | 60.9375 | 60.997 | 122.7173 | 123.0148 | -0.10071 | 122.9324 | 60.9467 | -0.24719 | 123.0148 | -0.10071 | 60.9467 | 122.7173 | 122.9324 | -123.1201 | -123.1613
704.7656 | 123.0881 | -60.91 | 61.9858 | 0.087509 | -0.0020208 | -0.0023711 | 0.0030612 | 0.065446 | -0.0020187 | 0.068479 | -61.0245 | 62.1231 | -61.1114 | -61.1435 | 61.7935 | 0.009155 | 0.032043 | 0.073242 | 62.027 | -61.171 | -0.20142 | 0.13733 | -0.11444 | -0.23346 | -0.19226 | -0.26093 | 0.041199 | 0.086975 | 60.9421 | 60.9833 | 122.7036 | 123.0331 | -0.11444 | 122.937 | 60.9192 | -0.26093 | 123.0331 | -0.11444 | 60.9192 | 122.7036 | 122.937 | -123.0972 | -123.1567
705.7656 | 123.1293 | -60.8734 | 62.0041 | 0.53001 | -0.0026618 | -0.00087594 | 0.0030612 | 0.066514 | -0.0015915 | 0.070402 | -61.0016 | 62.114 | -61.1298 | -61.1206 | 61.853 | 0.064087 | 0.027466 | 0.11902 | 62.0087 | -61.1572 | -0.25635 | 0.10986 | -0.12817 | -0.24719 | -0.15106 | -0.28381 | 0.004578 | 0.12817 | 60.9009 | 60.9924 | 122.7264 | 122.9874 | -0.12817 | 122.8821 | 60.9375 | -0.28381 | 122.9874 | -0.12817 | 60.9375 | 122.7264 | 122.8821 | -123.1338 | -123.1613
706.7656 | 123.0789 | -60.9238 | 61.9949 | 0.10277 | -0.00138 | -0.0019439 | 0.0017794 | 0.067155 | -0.0020187 | 0.069333 | -61.0519 | 62.1277 | -61.1298 | -61.1618 | 61.7752 | -0.013733 | 0.041199 | 0.036621 | 62.0316 | -61.1526 | -0.20599 | 0.13275 | -0.12817 | -0.23804 | -0.21973 | -0.22888 | 0.036621 | 0.07782 | 60.965 | 60.9604 | 122.699 | 123.0515 | -0.12817 | 122.9553 | 60.91 | -0.22888 | 123.0515 | -0.12817 | 60.91 | 122.699 | 122.9553 | -123.1247 | -123.1476
707.7656 | 123.0881 | -60.9055 | 62.027 | 0.18669 | -0.0015936 | -0.0034393 | 0.0022066 | 0.066514 | -0.0011643 | 0.069974 | -61.0886 | 62.114 | -61.1435 | -61.203 | 61.6745 | -0.26093 | 0.013733 | 0.1831 | 61.9812 | -61.1801 | -0.23804 | 0.086975 | -0.18311 | -0.29755 | -0.35248 | -0.27466 | -0.045777 | 0.054932 | 60.9192 | 61.0886 | 122.58 | 123.0194 | -0.18311 | 122.8867 | 60.6445 | -0.27466 | 123.0194 | -0.18311 | 60.6445 | 122.58 | 122.8867 | -123.1705 | -123.2071
708.7656 | 123.0515 | -60.8917 | 61.9904 | 0.19432 | -0.00138 | -0.0032257 | 0.00092504 | 0.066727 | -0.0013779 | 0.06912 | -61.0062 | 62.0773 | -61.1618 | -61.1893 | 61.734 | 0 | 0.032043 | 0.022888 | 62.0316 | -61.1526 | -0.27008 | 0.086976 | -0.11444 | -0.29755 | -0.25635 | -0.26092 | 0.041199 | 0.15564 | 60.9238 | 60.9146 | 122.6257 | 122.9691 | -0.11444 | 122.9233 | 60.8917 | -0.26092 | 122.9691 | -0.11444 | 60.8917 | 122.6257 | 122.9233 | -123.1522 | -123.143
709.7656 | 123.0835 | -60.9375 | 62.0132 | -0.12611 | -0.00138 | -0.0032257 | -0.00035676 | 0.066087 | -0.0020187 | 0.069333 | -61.0748 | 62.1094 | -61.1023 | -61.2122 | 61.7569 | -0.041199 | -0.009155 | 0.013733 | 62.0407 | -61.1893 | -0.16479 | 0.09613 | -0.13733 | -0.27466 | -0.25635 | -0.25177 | 0.027465 | 0.027466 | 60.9283 | 60.9512 | 122.6944 | 123.0469 | -0.13733 | 122.9782 | 60.8963 | -0.25177 | 123.0469 | -0.13733 | 60.8963 | 122.6944 | 122.9782 | -123.1155 | -123.2025
710.7656 | 123.1201 | -60.9146 | 61.9766 | 0.12566 | -0.0024482 | -0.0049347 | 0.0022066 | 0.065873 | -0.0026595 | 0.070829 | -61.0977 | 62.1002 | -61.1343 | -61.1984 | 61.7706 | -0.036621 | -0.013733 | 0.004578 | 61.9949 | -61.1618 | -0.21973 | 0.1236 | -0.18311 | -0.28381 | -0.20599 | -0.24719 | 0.01831 | 0.036621 | 60.9009 | 60.9192 | 122.6852 | 123.0148 | -0.18311 | 122.9095 | 60.878 | -0.24719 | 123.0148 | -0.18311 | 60.878 | 122.6852 | 122.9095 | -123.111 | -123.1384
711.7656 | 123.0606 | -60.9512 | 61.9949 | 0.20195 | -0.0028754 | -0.0010895 | 0.0017794 | 0.064591 | -0.0013779 | 0.069761 | -61.1069 | 62.0911 | -61.1481 | -61.2076 | 61.7523 | -0.059509 | 0.018311 | -0.009155 | 61.9812 | -61.171 | -0.19684 | 0.09613 | -0.15564 | -0.25635 | -0.24262 | -0.21973 | -0.013733 | 0.041198 | 60.9695 | 60.9421 | 122.7036 | 123.0423 | -0.15564 | 122.9324 | 60.8917 | -0.21973 | 123.0423 | -0.15564 | 60.8917 | 122.7036 | 122.9324 | -123.143 | -123.1659
712.7656 | 123.0835 | -60.9375 | 62.0224 | 0.18669 | -0.0020208 | -0.0017303 | 0.001993 | 0.064378 | -0.0022323 | 0.069333 | -61.0794 | 62.1094 | -61.1526 | -61.2122 | 61.734 | 0.054932 | -0.38452 | -0.17853 | 61.9537 | -61.2122 | -0.21515 | 0.086975 | -0.14191 | -0.27466 | -0.28839 | -0.27466 | -0.068665 | 0.073242 | 60.553 | 60.759 | 122.6715 | 123.0469 | -0.14191 | 122.8912 | 60.9924 | -0.27466 | 123.0469 | -0.14191 | 60.9924 | 122.6715 | 122.8912 | -123.175 | -123.2346
713.7656 | 123.1247 | -60.9146 | 61.9812 | 0.24773 | -0.0015936 | 0.0036103 | 0.002634 | 0.066727 | 0.00054465 | 0.070188 | -61.0794 | 62.1048 | -61.116 | -61.171 | 61.7706 | -0.027466 | -0.07782 | 0.032043 | 61.972 | -61.1938 | -0.20142 | 0.1236 | -0.1648 | -0.25635 | -0.21057 | -0.27924 | -0.009155 | 0.036621 | 60.8368 | 60.9467 | 122.6852 | 123.0194 | -0.1648 | 122.8867 | 60.8871 | -0.27924 | 123.0194 | -0.1648 | 60.8871 | 122.6852 | 122.8867 | -123.0972 | -123.175
714.7656 | 123.1522 | -60.9238 | 61.9904 | 0.27824 | -0.00073919 | -0.0057891 | -0.00014316 | 0.064591 | -0.0028731 | 0.070402 | -61.0748 | 62.0911 | -61.1389 | -61.1618 | 61.7935 | -0.022888 | -0.10071 | 0.054932 | 61.9904 | -61.171 | -0.21515 | 0.10071 | -0.15106 | -0.23804 | -0.19684 | -0.24719 | 0 | 0.064087 | 60.8231 | 60.9787 | 122.7173 | 123.0148 | -0.15106 | 122.9141 | 60.9009 | -0.24719 | 123.0148 | -0.15106 | 60.9009 | 122.7173 | 122.9141 | -123.1293 | -123.1613
715.7812 | 123.0606 | -60.8963 | 62.0224 | -0.072708 | -0.0043708 | -0.0023711 | 0.00092504 | 0.062669 | -0.0011643 | 0.071256 | -61.0794 | 62.1048 | -61.1206 | -61.1755 | 61.7981 | 0.059509 | 0.14191 | 0.15106 | 62.0361 | -61.1343 | -0.2243 | 0.082397 | -0.18311 | -0.27924 | -0.2243 | -0.23804 | 0.013733 | 0.041198 | 61.0382 | 61.0474 | 122.6944 | 123.0011 | -0.18311 | 122.9324 | 60.9558 | -0.23804 | 123.0011 | -0.18311 | 60.9558 | 122.6944 | 122.9324 | -123.143 | -123.1567
716.7656 | 123.23 | -60.9146 | 61.9766 | 0.26299 | -0.0043708 | -0.0047211 | 0.00092504 | 0.064591 | -0.0024459 | 0.068265 | -60.997 | 61.9858 | -61.0977 | -61.1023 | 61.8393 | 0.054932 | -0.18768 | -0.032043 | 61.9583 | -61.1435 | -0.18311 | 0.009155 | -0.082397 | -0.18768 | -0.13733 | -0.22888 | -0.018311 | 0.10071 | 60.7269 | 60.8826 | 122.7539 | 122.9004 | -0.082397 | 122.8729 | 60.9695 | -0.22888 | 122.9004 | -0.082397 | 60.9695 | 122.7539 | 122.8729 | -123.0743 | -123.1201
717.7656 | 123.1659 | -60.8688 | 61.9675 | 0.23247 | -0.0033026 | -0.0032257 | 0.0024202 | 0.066087 | -0.0047957 | 0.068906 | -60.997 | 62.0041 | -61.1069 | -61.0245 | 61.8896 | 0.059509 | -0.13733 | 0.14191 | 61.9766 | -61.1206 | -0.23804 | 0.036621 | -0.12817 | -0.15564 | -0.07782 | -0.25177 | 0.009156 | 0.10986 | 60.7315 | 61.0107 | 122.7585 | 122.8729 | -0.12817 | 122.8455 | 60.9283 | -0.25177 | 122.8729 | -0.12817 | 60.9283 | 122.7585 | 122.8455 | -123.0743 | -123.0881
718.7656 | 123.2254 | -60.9009 | 61.972 | 0.27824 | -0.0039434 | -0.0010895 | 0.0015658 | 0.063523 | -0.00073695 | 0.069547 | -60.9833 | 61.9949 | -61.1206 | -61.1023 | 61.8256 | 0.036621 | -0.19226 | 0.10071 | 61.9675 | -61.1389 | -0.21973 | 0.022888 | -0.082397 | -0.20142 | -0.14648 | -0.23804 | -0.004578 | 0.13733 | 60.7086 | 61.0016 | 122.7264 | 122.8958 | -0.082397 | 122.8683 | 60.9375 | -0.23804 | 122.8958 | -0.082397 | 60.9375 | 122.7264 | 122.8683 | -123.0927 | -123.111
719.7656 | 123.2071 | -60.9009 | 61.9812 | 0.28587 | -0.0022346 | -0.0023711 | 0.0024202 | 0.065659 | -9.6146e-05 | 0.067624 | -60.997 | 61.9904 | -61.1114 | -61.1069 | 61.8439 | 0.050354 | -0.18768 | 0.11444 | 61.9492 | -61.1526 | -0.21057 | 0.009155 | -0.09613 | -0.20599 | -0.13733 | -0.25177 | -0.032043 | 0.11444 | 60.7132 | 61.0153 | 122.7448 | 122.8912 | -0.09613 | 122.85 | 60.9512 | -0.25177 | 122.8912 | -0.09613 | 60.9512 | 122.7448 | 122.85 | -123.0927 | -123.1338
720.7812 | 123.1796 | -60.8643 | 61.9904 | 0.026474 | -0.006507 | -0.0055755 | -0.0020658 | 0.062241 | -0.0018051 | 0.068265 | -61.0519 | 62.0087 | -61.0931 | -61.1023 | 61.853 | 0.091553 | -0.073242 | 0.19226 | 61.9766 | -61.1114 | -0.22888 | 0.018311 | -0.18768 | -0.23804 | -0.13733 | -0.24719 | -0.013732 | 0.041199 | 60.791 | 61.0565 | 122.7173 | 122.8729 | -0.18768 | 122.8409 | 60.9558 | -0.24719 | 122.8729 | -0.18768 | 60.9558 | 122.7173 | 122.8409 | -123.0835 | -123.1018
721.7656 | 123.1613 | -60.8826 | 61.9766 | 0.14092 | -0.0033026 | -0.0055755 | 0.00092504 | 0.0616 | -0.0035141 | 0.069333 | -61.0519 | 61.9766 | -61.1069 | -61.1343 | 61.8073 | 0.022888 | -0.091553 | 0.11444 | 62.0041 | -61.0931 | -0.22431 | 0 | -0.16937 | -0.25177 | -0.16937 | -0.21057 | 0.027465 | 0.054932 | 60.791 | 60.997 | 122.6898 | 122.8592 | -0.16937 | 122.8867 | 60.9055 | -0.21057 | 122.8592 | -0.16937 | 60.9055 | 122.6898 | 122.8867 | -123.0835 | -123.0698
722.7656 | 123.143 | -60.8871 | 61.9995 | 0.1104 | -0.007575 | -0.0057891 | 7.0444e-05 | 0.064378 | -0.0030869 | 0.069333 | -61.0382 | 61.972 | -61.1252 | -61.1572 | 61.8164 | 0.018311 | -0.091553 | 0.10071 | 62.0087 | -61.1252 | -0.23804 | -0.027466 | -0.15106 | -0.27008 | -0.18311 | -0.23804 | 0.009155 | 0.086975 | 60.7956 | 60.9879 | 122.7036 | 122.8592 | -0.15106 | 122.8958 | 60.9055 | -0.23804 | 122.8592 | -0.15106 | 60.9055 | 122.7036 | 122.8958 | -123.1247 | -123.1247
723.7656 | 123.1384 | -60.8826 | 61.9812 | 0.10277 | -0.0039434 | -0.0068573 | 0.00028404 | 0.062455 | -0.0028731 | 0.06912 | -61.0382 | 61.972 | -61.1114 | -61.1252 | 61.8027 | 0.022888 | -0.068665 | 0.11902 | 62.0132 | -61.116 | -0.22888 | -0.009155 | -0.15564 | -0.24262 | -0.17853 | -0.23346 | 0.032044 | 0.073242 | 60.8139 | 61.0016 | 122.6852 | 122.8546 | -0.15564 | 122.8958 | 60.9055 | -0.23346 | 122.8546 | -0.15564 | 60.9055 | 122.6852 | 122.8958 | -123.0927 | -123.0972
724.7656 | 123.1384 | -60.878 | 61.9904 | 0.056992 | -0.0054388 | -0.0066437 | 0.00028404 | 0.062028 | -0.0056503 | 0.069974 | -61.0519 | 61.9904 | -61.1023 | -61.1343 | 61.8027 | 0.022888 | -0.073242 | 0.11902 | 61.9995 | -61.116 | -0.2243 | 0 | -0.17395 | -0.25635 | -0.18768 | -0.23804 | 0.009156 | 0.050354 | 60.8047 | 60.997 | 122.6807 | 122.8683 | -0.17395 | 122.8775 | 60.9009 | -0.23804 | 122.8683 | -0.17395 | 60.9009 | 122.6807 | 122.8775 | -123.0927 | -123.1064
725.7812 | 123.1293 | -60.8871 | 62.0361 | -0.17189 | -0.0056524 | -0.0055755 | 0.0022066 | 0.060532 | -0.0052231 | 0.068479 | -60.997 | 62.0132 | -61.0931 | -61.0565 | 61.8759 | 0.11444 | 0.036621 | 0.23346 | 62.0087 | -61.1114 | -0.20599 | -0.022888 | -0.10986 | -0.16937 | -0.16022 | -0.2243 | -0.027466 | 0.096131 | 60.9238 | 61.1206 | 122.7631 | 122.9004 | -0.10986 | 122.8958 | 61.0016 | -0.2243 | 122.9004 | -0.10986 | 61.0016 | 122.7631 | 122.8958 | -123.1293 | -123.1476
726.7656 | 123.1567 | -60.8734 | 61.9904 | 0.10277 | -0.0067206 | -0.0070709 | -0.0012112 | 0.062455 | -0.0024459 | 0.06912 | -61.0519 | 61.972 | -61.1252 | -61.1389 | 61.8027 | 0.022888 | -0.10529 | 0.09613 | 61.9629 | -61.1298 | -0.25177 | -0.01831 | -0.17853 | -0.2655 | -0.18768 | -0.25635 | -0.027465 | 0.073242 | 60.7681 | 60.9695 | 122.6761 | 122.8455 | -0.17853 | 122.8363 | 60.8963 | -0.25635 | 122.8455 | -0.17853 | 60.8963 | 122.6761 | 122.8363 | -123.1155 | -123.1201
727.7656 | 123.1979 | -60.8917 | 62.0178 | 0.095139 | -0.0060798 | -0.0057891 | -0.00057036 | 0.06096 | -0.0047957 | 0.066129 | -61.0474 | 61.9812 | -61.084 | -61.116 | 61.7935 | 0.032043 | -0.07782 | 0.14191 | 61.9949 | -61.1206 | -0.19226 | -0.036621 | -0.15564 | -0.2243 | -0.2243 | -0.22888 | -0.022888 | 0.036621 | 60.8139 | 61.0336 | 122.6852 | 122.8729 | -0.15564 | 122.8867 | 60.9238 | -0.22888 | 122.8729 | -0.15564 | 60.9238 | 122.6852 | 122.8867 | -123.1018 | -123.1384
728.7656 | 123.2208 | -60.878 | 62.0087 | -0.019302 | -0.0080024 | -0.0083527 | -0.00035676 | 0.060746 | -0.0033005 | 0.067197 | -61.0153 | 61.9675 | -61.1069 | -61.0748 | 61.8713 | 0.091553 | -0.07782 | 0.18768 | 61.9858 | -61.0931 | -0.22888 | -0.041199 | -0.13733 | -0.19684 | -0.13733 | -0.21515 | -0.022888 | 0.091553 | 60.8002 | 61.0657 | 122.7493 | 122.8455 | -0.13733 | 122.8638 | 60.9695 | -0.21515 | 122.8455 | -0.13733 | 60.9695 | 122.7493 | 122.8638 | -123.1155 | -123.1018
729.7656 | 123.1934 | -60.8826 | 61.9995 | -0.026932 | -0.0060798 | -0.01113 | 0.001993 | 0.060532 | -0.0026595 | 0.069333 | -60.9924 | 61.972 | -61.116 | -61.0703 | 61.8622 | 0.10071 | -0.082397 | 0.21057 | 61.9995 | -61.0703 | -0.23346 | -0.027466 | -0.10986 | -0.18768 | -0.13733 | -0.18768 | 0 | 0.1236 | 60.8002 | 61.0931 | 122.7448 | 122.8546 | -0.10986 | 122.8821 | 60.9833 | -0.18768 | 122.8546 | -0.10986 | 60.9833 | 122.7448 | 122.8821 | -123.1155 | -123.0698
730.7812 | 123.1018 | -60.8826 | 62.0087 | 0.026474 | -0.0028754 | -0.0019439 | 0.0092562 | 0.063523 | -0.00052335 | 0.070615 | -60.9558 | 62.0636 | -61.1023 | -61.0886 | 61.8256 | 0.041199 | 0.036621 | 0.12817 | 62.0224 | -61.1481 | -0.21973 | 0.054932 | -0.073243 | -0.20599 | -0.18311 | -0.2655 | 0.013733 | 0.14648 | 60.9192 | 61.0107 | 122.7081 | 122.9462 | -0.073243 | 122.905 | 60.9238 | -0.2655 | 122.9462 | -0.073243 | 60.9238 | 122.7081 | 122.905 | -123.111 | -123.1567
731.7656 | 123.1934 | -60.8597 | 61.9858 | -0.026932 | -0.0062934 | -0.0060027 | 0.00028404 | 0.0616 | -0.0026595 | 0.068052 | -60.997 | 61.9812 | -61.0931 | -61.0611 | 61.8988 | 0.1236 | -0.07782 | 0.22888 | 62.0224 | -61.0565 | -0.23346 | -0.004578 | -0.13733 | -0.20142 | -0.086975 | -0.19684 | 0.036621 | 0.096131 | 60.7819 | 61.0886 | 122.7585 | 122.8409 | -0.13733 | 122.8821 | 60.9833 | -0.19684 | 122.8409 | -0.13733 | 60.9833 | 122.7585 | 122.8821 | -123.0789 | -123.0423
732.7656 | 123.1522 | -60.8917 | 62.0087 | 0.13329 | -0.0069342 | -0.0092071 | -0.0020658 | 0.062028 | -0.0052231 | 0.069761 | -61.0291 | 61.9675 | -61.1389 | -61.0886 | 61.8439 | 0.050354 | -0.07782 | 0.15106 | 61.9949 | -61.0977 | -0.24719 | -0.041199 | -0.13733 | -0.19684 | -0.1648 | -0.20599 | -0.013733 | 0.10986 | 60.8139 | 61.0428 | 122.7356 | 122.8592 | -0.13733 | 122.8867 | 60.9421 | -0.20599 | 122.8592 | -0.13733 | 60.9421 | 122.7356 | 122.8867 | -123.1476 | -123.1064
733.7656 | 123.1934 | -60.8871 | 61.9949 | 0.10277 | -0.0054388 | -0.0047211 | 0.0011386 | 0.061814 | -0.0052231 | 0.06912 | -61.0336 | 61.9812 | -61.116 | -61.1069 | 61.8393 | 0.068665 | -0.059509 | 0.15106 | 62.0087 | -61.0748 | -0.22888 | -0.013733 | -0.14648 | -0.21973 | -0.15564 | -0.18768 | 0.013733 | 0.082398 | 60.8276 | 61.0382 | 122.7264 | 122.8683 | -0.14648 | 122.8958 | 60.9558 | -0.18768 | 122.8683 | -0.14648 | 60.9558 | 122.7264 | 122.8958 | -123.111 | -123.0698
734.7656 | 123.2254 | -60.8368 | 61.9995 | -0.0040434 | -0.0041572 | -0.0040801 | 0.00028404 | 0.063096 | -0.0058639 | 0.066984 | -60.9695 | 61.9766 | -61.1023 | -61.0336 | 61.8851 | 0.13733 | -0.064087 | 0.24261 | 62.0087 | -61.0657 | -0.2655 | -0.022888 | -0.13275 | -0.19684 | -0.11444 | -0.22888 | 0.009155 | 0.13275 | 60.7727 | 61.0794 | 122.7219 | 122.8134 | -0.13275 | 122.8455 | 60.9741 | -0.22888 | 122.8134 | -0.13275 | 60.9741 | 122.7219 | 122.8455 | -123.1018 | -123.0652
735.7656 | 123.0377 | -60.9283 | 62.0132 | 0.21721 | -0.0024482 | -0.0053619 | 0.0073336 | 0.063523 | -0.0058639 | 0.067624 | -61.0748 | 62.0316 | -61.1526 | -61.1755 | 61.734 | -0.064087 | 0.022888 | -0.013733 | 62.0407 | -61.1252 | -0.2243 | 0.01831 | -0.14648 | -0.24719 | -0.27924 | -0.19684 | 0.027465 | 0.07782 | 60.9512 | 60.9146 | 122.6624 | 122.9599 | -0.14648 | 122.9691 | 60.8643 | -0.19684 | 122.9599 | -0.14648 | 60.8643 | 122.6624 | 122.9691 | -123.1659 | -123.1384
736.7656 | 123.2162 | -60.8871 | 61.9858 | -0.17952 | -0.004798 | -0.0036529 | 0.00028404 | 0.063737 | -0.0045821 | 0.067197 | -60.9695 | 61.9904 | -61.0703 | -60.7773 | 62.1231 | 0.1236 | -0.13733 | 0.19684 | 61.9812 | -61.084 | -0.1831 | 0.004577 | -0.082397 | 0.10986 | 0.13733 | -0.19684 | -0.004578 | 0.10071 | 60.7498 | 61.084 | 123.0103 | 122.8775 | -0.082397 | 122.8683 | 61.0107 | -0.19684 | 122.8775 | -0.082397 | 61.0107 | 123.0103 | 122.8683 | -123.056 | -123.0698
737.7656 | 123.1934 | -60.8688 | 61.9858 | -0.15663 | -0.0041572 | -0.0027985 | 0.00049764 | 0.060319 | -0.0022323 | 0.067838 | -60.9604 | 61.9904 | -61.0794 | -61.1252 | 61.8988 | 0.14648 | -0.045776 | 0.2243 | 61.9583 | -61.0657 | -0.21057 | 0.004577 | -0.091553 | -0.25635 | -0.086975 | -0.19684 | -0.027466 | 0.11902 | 60.8231 | 61.0931 | 122.7676 | 122.8592 | -0.091553 | 122.8271 | 61.0153 | -0.19684 | 122.8592 | -0.091553 | 61.0153 | 122.7676 | 122.8271 | -123.0652 | -123.0515
738.7656 | 123.2025 | -60.8551 | 62.0132 | -0.11848 | -0.006507 | -0.0049347 | -0.00014316 | 0.063523 | -0.0052231 | 0.06912 | -60.9695 | 61.9995 | -61.0748 | -61.0611 | 61.853 | 0.13733 | -0.07782 | 0.21515 | 61.9629 | -61.1023 | -0.21973 | -0.013733 | -0.11444 | -0.20599 | -0.16022 | -0.24719 | -0.050354 | 0.10529 | 60.7773 | 61.0703 | 122.7081 | 122.8546 | -0.11444 | 122.818 | 60.9924 | -0.24719 | 122.8546 | -0.11444 | 60.9924 | 122.7081 | 122.818 | -123.0881 | -123.1155
739.7656 | 123.2254 | -60.8505 | 61.9858 | 0.018845 | -0.0039434 | -0.0062163 | 7.0444e-05 | 0.060746 | -0.0060775 | 0.068052 | -60.9512 | 61.9858 | -61.084 | -61.0199 | 61.9263 | 0.16022 | -0.059509 | 0.25635 | 62.0316 | -61.0474 | -0.23346 | 0 | -0.10071 | -0.16937 | -0.059509 | -0.19684 | 0.045776 | 0.13275 | 60.791 | 61.1069 | 122.7768 | 122.8363 | -0.10071 | 122.8821 | 61.0107 | -0.19684 | 122.8363 | -0.10071 | 61.0107 | 122.7768 | 122.8821 | -123.0698 | -123.0331
740.7656 | 123.2346 | -60.8414 | 62.0132 | -0.11085 | -0.0056524 | -0.0055755 | -0.00035676 | 0.063737 | -0.0045821 | 0.071256 | -60.9558 | 61.9766 | -61.0794 | -60.9924 | 61.9308 | 0.16479 | -0.07782 | 0.2655 | 61.9904 | -61.084 | -0.23804 | -0.036621 | -0.11444 | -0.15106 | -0.082398 | -0.24261 | -0.022889 | 0.1236 | 60.7635 | 61.1069 | 122.7722 | 122.818 | -0.11444 | 122.8317 | 61.0062 | -0.24261 | 122.818 | -0.11444 | 61.0062 | 122.7722 | 122.8317 | -123.0927 | -123.0972
741.7656 | 123.1659 | -60.8643 | 61.9995 | -0.24055 | -0.005866 | -0.0062163 | 0.0028476 | 0.062028 | -0.0013779 | 0.070188 | -61.0611 | 61.9949 | -61.1023 | -61.0382 | 61.908 | 0.17395 | -0.018311 | 0.26093 | 61.9766 | -61.1023 | -0.23804 | -0.004578 | -0.19684 | -0.17395 | -0.091553 | -0.23804 | -0.022888 | 0.041199 | 60.8459 | 61.1252 | 122.7722 | 122.8592 | -0.19684 | 122.8409 | 61.0382 | -0.23804 | 122.8592 | -0.19684 | 61.0382 | 122.7722 | 122.8409 | -123.1018 | -123.1018
742.7656 | 123.1384 | -60.878 | 62.0453 | -0.25581 | -0.0054388 | -0.0060027 | 0.0015658 | 0.062882 | -0.0039413 | 0.067624 | -60.9879 | 62.0407 | -61.0794 | -61.0886 | 61.8622 | 0.091553 | 0.09613 | 0.18768 | 62.0453 | -61.0794 | -0.20142 | -0.004578 | -0.10986 | -0.21057 | -0.1831 | -0.20142 | 0 | 0.091553 | 60.9741 | 61.0657 | 122.7402 | 122.9187 | -0.10986 | 122.9233 | 60.9695 | -0.20142 | 122.9187 | -0.10986 | 60.9695 | 122.7402 | 122.9233 | -123.1247 | -123.1247
743.7656 | 123.1064 | -60.8734 | 62.0499 | -0.17189 | -0.0041572 | -0.0021575 | 0.001993 | 0.060105 | -0.0047957 | 0.068265 | -61.0016 | 62.0407 | -61.084 | -61.0703 | 61.8484 | 0.082397 | 0.091553 | 0.17853 | 62.0132 | -61.1023 | -0.21057 | -0.009156 | -0.12817 | -0.19684 | -0.20142 | -0.22888 | -0.036621 | 0.082397 | 60.965 | 61.0519 | 122.7219 | 122.9141 | -0.12817 | 122.8867 | 60.9558 | -0.22888 | 122.9141 | -0.12817 | 60.9558 | 122.7219 | 122.8867 | -123.1338 | -123.1522
744.7656 | 123.1018 | -60.8688 | 62.0407 | -0.18715 | -0.0050116 | -0.0023711 | 0.0047702 | 0.062028 | -0.0039413 | 0.069333 | -61.0107 | 62.0453 | -61.0886 | -61.1069 | 61.8347 | 0.082397 | 0.10986 | 0.1831 | 62.0041 | -61.1069 | -0.21973 | 0.004578 | -0.14191 | -0.23804 | -0.20599 | -0.23804 | -0.036621 | 0.07782 | 60.9787 | 61.0519 | 122.7036 | 122.9141 | -0.14191 | 122.8729 | 60.9512 | -0.23804 | 122.9141 | -0.14191 | 60.9512 | 122.7036 | 122.8729 | -123.1293 | -123.1476
745.7656 | 123.0972 | -60.8734 | 62.0316 | -0.17189 | -0.0050116 | -0.0034393 | 0.0022066 | 0.061814 | -0.0026595 | 0.069547 | -61.0199 | 62.0407 | -61.1023 | -61.1069 | 61.8439 | 0.091553 | 0.11902 | 0.16479 | 62.0361 | -61.0931 | -0.22888 | 0.009155 | -0.14648 | -0.23346 | -0.18768 | -0.21973 | 0.004578 | 0.082398 | 60.9924 | 61.0382 | 122.7173 | 122.9141 | -0.14648 | 122.9095 | 60.965 | -0.21973 | 122.9141 | -0.14648 | 60.965 | 122.7173 | 122.9095 | -123.1338 | -123.1247
746.7656 | 123.1888 | -60.8597 | 62.0041 | -0.15663 | -0.005866 | -0.0064301 | 0.00049764 | 0.063523 | -0.0020187 | 0.068265 | -60.9695 | 62.0178 | -61.084 | -61.0336 | 61.8805 | 0.15106 | 0.013733 | 0.24719 | 61.9766 | -61.0794 | -0.2243 | 0.013733 | -0.10986 | -0.17395 | -0.1236 | -0.21973 | -0.027465 | 0.11444 | 60.8734 | 61.1069 | 122.7402 | 122.8775 | -0.10986 | 122.8363 | 61.0107 | -0.21973 | 122.8775 | -0.10986 | 61.0107 | 122.7402 | 122.8363 | -123.0881 | -123.0835
747.7656 | 123.1476 | -60.8871 | 62.0041 | -0.11848 | -0.0060798 | -0.0055755 | 0.002634 | 0.062669 | -0.0041549 | 0.069547 | -60.9695 | 62.027 | -61.0931 | -61.0565 | 61.8851 | 0.15564 | 0.018311 | 0.22888 | 61.9949 | -61.084 | -0.20599 | 0.022889 | -0.082397 | -0.16937 | -0.11902 | -0.19684 | -0.009155 | 0.1236 | 60.9055 | 61.116 | 122.7722 | 122.9141 | -0.082397 | 122.8821 | 61.0428 | -0.19684 | 122.9141 | -0.082397 | 61.0428 | 122.7722 | 122.8821 | -123.0972 | -123.0881
748.7656 | 123.0835 | -60.8917 | 62.0499 | -0.46181 | -0.0039434 | -0.0083527 | 0.0013522 | 0.063096 | -0.0033005 | 0.068906 | -61.0428 | 62.0407 | -61.1114 | -61.1343 | 61.8256 | 0.054932 | 0.13733 | 0.14191 | 62.059 | -61.116 | -0.21973 | -0.009156 | -0.15106 | -0.24261 | -0.2243 | -0.2243 | 0.009155 | 0.068664 | 61.0291 | 61.0336 | 122.7173 | 122.9324 | -0.15106 | 122.9507 | 60.9467 | -0.2243 | 122.9324 | -0.15106 | 60.9467 | 122.7173 | 122.9507 | -123.1613 | -123.1659
749.7656 | 123.0789 | -60.9055 | 62.0453 | 0.85045 | -0.0033026 | -0.0045075 | 0.005411 | 0.063309 | -0.0041549 | 0.069761 | -61.0931 | 62.0865 | -61.1114 | -61.1343 | 61.8164 | 0.054932 | 0.15106 | 0.13733 | 62.0224 | -61.1343 | -0.20599 | 0.041199 | -0.18768 | -0.22888 | -0.22888 | -0.22888 | -0.022888 | 0.01831 | 61.0565 | 61.0428 | 122.7219 | 122.9919 | -0.18768 | 122.9279 | 60.9604 | -0.22888 | 122.9919 | -0.18768 | 60.9604 | 122.7219 | 122.9279 | -123.1567 | -123.1796
750.7656 | 123.1064 | -60.8963 | 62.0224 | -0.057449 | -0.0035162 | -0.0060027 | 0.0058382 | 0.062241 | -0.0037277 | 0.068693 | -61.0611 | 62.0911 | -61.1298 | -61.1298 | 61.8073 | 0.059509 | 0.12817 | 0.13275 | 62.0499 | -61.1252 | -0.23346 | 0.068664 | -0.16479 | -0.23346 | -0.21515 | -0.22888 | 0.027466 | 0.068665 | 61.0245 | 61.0291 | 122.7036 | 122.9874 | -0.16479 | 122.9462 | 60.9558 | -0.22888 | 122.9874 | -0.16479 | 60.9558 | 122.7036 | 122.9462 | -123.1522 | -123.1476
751.7656 | 123.1018 | -60.9238 | 62.0453 | -0.10323 | -0.0041572 | -0.0034393 | 0.0028476 | 0.063523 | -0.0033005 | 0.069547 | -61.0382 | 62.0956 | -61.1481 | -61.1389 | 61.8118 | 0.064087 | 0.13275 | 0.13275 | 61.9995 | -61.1618 | -0.2243 | 0.050354 | -0.11444 | -0.21515 | -0.23346 | -0.23804 | -0.045776 | 0.10986 | 61.0565 | 61.0565 | 122.7356 | 123.0194 | -0.11444 | 122.9233 | 60.9879 | -0.23804 | 123.0194 | -0.11444 | 60.9879 | 122.7356 | 122.9233 | -123.1934 | -123.2071
752.7656 | 123.1064 | -60.9055 | 62.0453 | -0.17952 | -0.0035162 | -0.0081389 | 0.0030612 | 0.065446 | -0.0030869 | 0.067197 | -61.0519 | 62.0956 | -61.116 | -61.1343 | 61.8118 | 0.068665 | 0.11444 | 0.13733 | 62.0407 | -61.1206 | -0.21057 | 0.050354 | -0.14648 | -0.22888 | -0.23346 | -0.21515 | -0.004578 | 0.064087 | 61.0199 | 61.0428 | 122.7173 | 123.0011 | -0.14648 | 122.9462 | 60.9741 | -0.21515 | 123.0011 | -0.14648 | 60.9741 | 122.7173 | 122.9462 | -123.1613 | -123.1659
753.7656 | 123.0652 | -60.8688 | 62.027 | -0.21004 | -0.0028754 | 0.00083306 | 0.0017794 | 0.062882 | -0.0035141 | 0.068906 | -61.0474 | 62.1094 | -61.1023 | -61.1435 | 61.8027 | 0.064087 | 0.15564 | 0.13733 | 62.059 | -61.1435 | -0.23346 | 0.082397 | -0.17853 | -0.27466 | -0.22431 | -0.27466 | 0.032043 | 0.054932 | 61.0245 | 61.0062 | 122.6715 | 122.9782 | -0.17853 | 122.9279 | 60.9329 | -0.27466 | 122.9782 | -0.17853 | 60.9329 | 122.6715 | 122.9279 | -123.1293 | -123.1705
754.7656 | 123.0652 | -60.9055 | 62.0361 | -0.19478 | -0.0026618 | -0.0045075 | 0.002634 | 0.063737 | -0.0039413 | 0.070188 | -61.0565 | 62.0911 | -61.1114 | -61.1435 | 62.0361 | 0.21057 | 0.018311 | 0.068665 | 62.0636 | -61.1526 | -0.20599 | 0.054931 | -0.15106 | -0.23804 | 0 | -0.24719 | 0.027466 | 0.054931 | 60.9238 | 60.9741 | 122.9416 | 122.9965 | -0.15106 | 122.9691 | 61.116 | -0.24719 | 122.9965 | -0.15106 | 61.116 | 122.9416 | 122.9691 | -123.1476 | -123.1888
755.7656 | 123.1155 | -60.8963 | 62.0361 | -0.14137 | -0.00073919 | -0.0055755 | 0.0041292 | 0.065018 | -0.0039413 | 0.069547 | -61.0153 | 62.1231 | -61.1298 | -61.1206 | 61.8256 | 0.07782 | 0.12817 | 0.14648 | 62.0453 | -61.1435 | -0.23346 | 0.086975 | -0.11902 | -0.2243 | -0.21057 | -0.24719 | 0.009155 | 0.11444 | 61.0245 | 61.0428 | 122.7219 | 123.0194 | -0.11902 | 122.9416 | 60.9741 | -0.24719 | 123.0194 | -0.11902 | 60.9741 | 122.7219 | 122.9416 | -123.1659 | -123.1796
756.7656 | 123.1338 | -60.8826 | 62.0087 | -0.087967 | -0.0035162 | 0.00040586 | 0.005411 | 0.064378 | -0.0022323 | 0.068906 | -61.0062 | 62.1094 | -61.1023 | -61.1023 | 61.8393 | 0.086975 | 0.045776 | 0.14191 | 62.0224 | -61.1618 | -0.21973 | 0.10071 | -0.1236 | -0.21973 | -0.16937 | -0.27924 | 0.013733 | 0.09613 | 60.9283 | 61.0245 | 122.7219 | 122.9919 | -0.1236 | 122.905 | 60.9695 | -0.27924 | 122.9919 | -0.1236 | 60.9695 | 122.7219 | 122.905 | -123.111 | -123.1705
757.7656 | 123.1384 | -60.91 | 62.027 | -0.034561 | -0.00052559 | -2.1336e-05 | 0.0041292 | 0.065446 | -0.0026595 | 0.06912 | -61.0016 | 62.1185 | -61.1114 | -61.0977 | 61.8393 | 0.091553 | 0.036621 | 0.15564 | 62.0224 | -61.1298 | -0.20142 | 0.091552 | -0.091553 | -0.18768 | -0.18768 | -0.21973 | -0.004578 | 0.10986 | 60.9467 | 61.0657 | 122.7493 | 123.0286 | -0.091553 | 122.9324 | 61.0016 | -0.21973 | 123.0286 | -0.091553 | 61.0016 | 122.7493 | 122.9324 | -123.1384 | -123.1567
758.7656 | 123.1293 | -60.9009 | 62.027 | -0.072708 | -0.0028754 | 0.0010467 | 0.0028476 | 0.066727 | -0.0026595 | 0.070829 | -60.9833 | 62.1002 | -61.116 | -61.0931 | 61.853 | 0.082397 | 0.036621 | 0.15106 | 62.0224 | -61.1526 | -0.21515 | 0.073242 | -0.082397 | -0.19226 | -0.17395 | -0.25177 | -0.004578 | 0.13275 | 60.9375 | 61.0519 | 122.7539 | 123.0011 | -0.082397 | 122.9233 | 60.9833 | -0.25177 | 123.0011 | -0.082397 | 60.9833 | 122.7539 | 122.9233 | -123.143 | -123.1796
759.7656 | 123.1293 | -60.8963 | 62.0178 | 0.0035856 | -0.0033026 | -0.0030121 | 0.0041292 | 0.065232 | -0.0024459 | 0.068906 | -60.9833 | 62.1231 | -61.0977 | -61.0977 | 61.8393 | 0.082397 | 0.050354 | 0.15106 | 62.027 | -61.171 | -0.20142 | 0.10529 | -0.086975 | -0.20142 | -0.17853 | -0.27466 | 0.009156 | 0.11444 | 60.9467 | 61.0474 | 122.7356 | 123.0194 | -0.086975 | 122.9233 | 60.9787 | -0.27466 | 123.0194 | -0.086975 | 60.9787 | 122.7356 | 122.9233 | -123.1155 | -123.1888
760.7656 | 123.1155 | -60.91 | 62.0499 | -0.14137 | -0.0056524 | -0.0042937 | 0.0030612 | 0.064591 | -0.0033005 | 0.071256 | -61.0291 | 62.1643 | -61.1435 | -61.1252 | 61.8301 | 0.091553 | 0.10529 | 0.16479 | 62.0224 | -61.1572 | -0.23346 | 0.11444 | -0.11902 | -0.21515 | -0.21973 | -0.24719 | -0.027466 | 0.11444 | 61.0153 | 61.0748 | 122.7402 | 123.0743 | -0.11902 | 122.9324 | 61.0016 | -0.24719 | 123.0743 | -0.11902 | 61.0016 | 122.7402 | 122.9324 | -123.1934 | -123.2071
761.7656 | 123.1201 | -60.8826 | 62.0316 | -0.04982 | -0.00138 | 0.0072419 | 0.0032748 | 0.064164 | -0.0022323 | 0.070402 | -60.997 | 62.1185 | -61.1298 | -61.0931 | 61.8484 | 0.091553 | 0.045776 | 0.15106 | 62.0316 | -61.1572 | -0.24719 | 0.086975 | -0.11444 | -0.21057 | -0.1831 | -0.27466 | 0 | 0.13275 | 60.9283 | 61.0336 | 122.731 | 123.0011 | -0.11444 | 122.9141 | 60.9741 | -0.27466 | 123.0011 | -0.11444 | 60.9741 | 122.731 | 122.9141 | -123.1613 | -123.1888
762.7656 | 123.1247 | -60.9009 | 61.9812 | -0.04219 | 0.00032901 | -0.0021575 | 0.0017794 | 0.064164 | -0.0033005 | 0.070188 | -61.0016 | 62.1414 | -61.1206 | -61.1206 | 61.8347 | 0.086975 | 0.054932 | 0.15564 | 62.0087 | -61.1801 | -0.21973 | 0.16022 | -0.10071 | -0.21973 | -0.14648 | -0.27924 | 0.027466 | 0.11902 | 60.9558 | 61.0565 | 122.7356 | 123.0423 | -0.10071 | 122.9095 | 60.9879 | -0.27924 | 123.0423 | -0.10071 | 60.9879 | 122.7356 | 122.9095 | -123.1018 | -123.1613
763.7656 | 123.1018 | -60.91 | 62.0041 | 0.064621 | -9.819e-05 | -0.0010895 | 0.003702 | 0.066514 | -0.0024459 | 0.068906 | -61.0062 | 62.114 | -61.1114 | -61.1252 | 61.7981 | 0.036621 | 0.022888 | 0.10986 | 62.0224 | -61.1984 | -0.20142 | 0.10986 | -0.096131 | -0.21515 | -0.20599 | -0.28839 | 0.018311 | 0.10528 | 60.9329 | 61.0199 | 122.7081 | 123.024 | -0.096131 | 122.9324 | 60.9467 | -0.28839 | 123.024 | -0.096131 | 60.9467 | 122.7081 | 122.9324 | -123.1155 | -123.2025
764.7656 | 123.1018 | -60.9009 | 61.9949 | 0.011215 | -0.00073919 | -0.0023711 | 0.0028476 | 0.066087 | -0.0035141 | 0.068693 | -61.0062 | 62.1185 | -61.116 | -61.1435 | 61.8073 | 0.041199 | 0.045776 | 0.10529 | 62.0682 | -61.1664 | -0.21515 | 0.1236 | -0.10529 | -0.24261 | -0.18768 | -0.2655 | 0.073242 | 0.10986 | 60.9467 | 61.0062 | 122.7081 | 123.0194 | -0.10529 | 122.9691 | 60.9421 | -0.2655 | 123.0194 | -0.10529 | 60.9421 | 122.7081 | 122.9691 | -123.111 | -123.1613
765.7656 | 123.111 | -60.8963 | 62.0224 | 0.041733 | -0.0033026 | -0.0042937 | 0.0030612 | 0.065659 | -0.0022323 | 0.068052 | -61.0062 | 62.1231 | -61.1069 | -61.1435 | 61.8027 | 0.045776 | 0.027466 | 0.09613 | 62.0453 | -61.1618 | -0.21057 | 0.10071 | -0.10986 | -0.24719 | -0.21973 | -0.2655 | 0.022888 | 0.10071 | 60.9238 | 60.9924 | 122.699 | 123.0194 | -0.10986 | 122.9416 | 60.9421 | -0.2655 | 123.0194 | -0.10986 | 60.9421 | 122.699 | 122.9416 | -123.1293 | -123.1842
766.7656 | 123.1201 | -60.91 | 61.9995 | 0.0035856 | -0.00095279 | -0.00066214 | 0.0034884 | 0.065446 | -0.0022323 | 0.06677 | -61.0153 | 62.1094 | -61.1435 | -61.1298 | 61.8027 | 0.036621 | 0.036621 | 0.10529 | 62.0361 | -61.1664 | -0.23346 | 0.10986 | -0.10529 | -0.21973 | -0.19684 | -0.25635 | 0.036621 | 0.12817 | 60.9467 | 61.0153 | 122.7127 | 123.0194 | -0.10529 | 122.9462 | 60.9467 | -0.25635 | 123.0194 | -0.10529 | 60.9467 | 122.7127 | 122.9462 | -123.143 | -123.1659
767.7656 | 123.1476 | -60.9238 | 62.0316 | -0.04219 | 0.00054261 | -0.0049347 | 0.0041292 | 0.064378 | -0.0024459 | 0.066556 | -61.0016 | 62.1323 | -61.1023 | -61.1069 | 61.8256 | 0.07782 | 0.032043 | 0.15106 | 62.0224 | -61.1893 | -0.17853 | 0.10071 | -0.07782 | -0.18311 | -0.20599 | -0.2655 | -0.009155 | 0.10071 | 60.9558 | 61.0748 | 122.7493 | 123.056 | -0.07782 | 122.9462 | 61.0016 | -0.2655 | 123.056 | -0.07782 | 61.0016 | 122.7493 | 122.9462 | -123.1338 | -123.2208
768.7656 | 123.1201 | -60.9009 | 62.0132 | 0.064621 | -0.0035162 | -0.0077117 | 0.00092504 | 0.068009 | -0.0035141 | 0.068693 | -61.0199 | 62.1002 | -61.1206 | -61.1435 | 61.8027 | 0.036621 | 0.018311 | 0.091553 | 62.0453 | -61.1801 | -0.21973 | 0.086975 | -0.11902 | -0.24261 | -0.21057 | -0.27924 | 0.032043 | 0.10071 | 60.9192 | 60.9924 | 122.7036 | 123.0011 | -0.11902 | 122.9462 | 60.9375 | -0.27924 | 123.0011 | -0.11902 | 60.9375 | 122.7036 | 122.9462 | -123.1338 | -123.1934
769.7656 | 123.0972 | -60.8826 | 61.9766 | 0.0035856 | -0.0028754 | -0.0034393 | 0.0032748 | 0.066941 | -0.0015915 | 0.070188 | -61.0291 | 62.1368 | -61.1298 | -61.1252 | 61.821 | 0.050354 | 0.022888 | 0.10071 | 62.0178 | -61.1847 | -0.24719 | 0.16022 | -0.14648 | -0.24262 | -0.15564 | -0.30212 | 0.041198 | 0.10071 | 60.9055 | 60.9833 | 122.7036 | 123.0194 | -0.14648 | 122.9004 | 60.9329 | -0.30212 | 123.0194 | -0.14648 | 60.9329 | 122.7036 | 122.9004 | -123.1064 | -123.1613
770.7656 | 123.0606 | -60.9421 | 62.027 | 0.1104 | 0.00011541 | -0.0027985 | 0.0028476 | 0.068009 | -0.0015915 | 0.070402 | -61.0519 | 62.1231 | -61.1389 | -61.2076 | 61.7477 | -0.050354 | 0.036621 | 0.022888 | 62.0407 | -61.1938 | -0.19684 | 0.09613 | -0.10986 | -0.2655 | -0.27924 | -0.25177 | 0.013732 | 0.086975 | 60.9787 | 60.965 | 122.6898 | 123.0652 | -0.10986 | 122.9828 | 60.8917 | -0.25177 | 123.0652 | -0.10986 | 60.8917 | 122.6898 | 122.9828 | -123.1659 | -123.2208
771.7656 | 123.0469 | -60.9192 | 62.027 | 0.20958 | -0.0039434 | -0.0027985 | 0.0039156 | 0.065659 | -0.0035141 | 0.069547 | -61.0519 | 62.1185 | -61.1298 | -61.2076 | 61.7432 | -0.032043 | 0.036621 | 0.004578 | 62.0453 | -61.2122 | -0.21057 | 0.091552 | -0.13275 | -0.28839 | -0.28381 | -0.29297 | 0.01831 | 0.07782 | 60.9558 | 60.9238 | 122.6624 | 123.0377 | -0.13275 | 122.9645 | 60.8871 | -0.29297 | 123.0377 | -0.13275 | 60.8871 | 122.6624 | 122.9645 | -123.1567 | -123.2391
772.7656 | 123.0789 | -60.9467 | 62.0041 | 0.15617 | -0.00138 | -0.0030121 | 0.0017794 | 0.067155 | -0.0022323 | 0.069333 | -61.0474 | 62.146 | -61.1389 | -61.2167 | 61.7249 | -0.050354 | 0.050354 | 0.018311 | 62.0361 | -61.1984 | -0.19226 | 0.14191 | -0.10071 | -0.27008 | -0.27923 | -0.25177 | 0.032044 | 0.091553 | 60.997 | 60.965 | 122.6715 | 123.0927 | -0.10071 | 122.9828 | 60.8963 | -0.25177 | 123.0927 | -0.10071 | 60.8963 | 122.6715 | 122.9828 | -123.143 | -123.2025
773.7656 | 123.1018 | -60.9055 | 62.0178 | 0.072251 | -0.0022346 | -0.0025847 | 0.0032748 | 0.065232 | -0.0035141 | 0.070402 | -61.0336 | 62.1277 | -61.1298 | -61.1435 | 61.7935 | 0.032043 | 0.022888 | 0.086975 | 62.0178 | -61.1893 | -0.2243 | 0.10986 | -0.12817 | -0.23804 | -0.2243 | -0.28381 | 0 | 0.096131 | 60.9283 | 60.9924 | 122.699 | 123.0331 | -0.12817 | 122.9233 | 60.9375 | -0.28381 | 123.0331 | -0.12817 | 60.9375 | 122.699 | 122.9233 | -123.1476 | -123.2071
774.7656 | 123.1155 | -60.8963 | 62.027 | 0.034104 | -0.00031179 | -0.00023494 | 0.0028476 | 0.066514 | -0.0035141 | 0.070402 | -61.0016 | 62.1048 | -61.1435 | -61.1618 | 61.7889 | 0.009155 | 0.027466 | 0.082397 | 62.0407 | -61.1893 | -0.24719 | 0.077819 | -0.10529 | -0.2655 | -0.23804 | -0.29297 | 0.013732 | 0.14191 | 60.9238 | 60.9787 | 122.6852 | 123.0011 | -0.10529 | 122.937 | 60.9055 | -0.29297 | 123.0011 | -0.10529 | 60.9055 | 122.6852 | 122.937 | -123.1705 | -123.2162
775.7656 | 123.0698 | -60.9329 | 61.9995 | 0.13329 | -0.00073919 | 0.00083306 | 0.002634 | 0.065018 | -0.0018051 | 0.068265 | -61.0748 | 62.1368 | -61.1343 | -61.2076 | 61.7386 | -0.054932 | 0.032043 | 0.027466 | 62.0316 | -61.203 | -0.20142 | 0.13733 | -0.14191 | -0.27466 | -0.26093 | -0.27008 | 0.032043 | 0.059509 | 60.965 | 60.9604 | 122.6715 | 123.0698 | -0.14191 | 122.9645 | 60.878 | -0.27008 | 123.0698 | -0.14191 | 60.878 | 122.6715 | 122.9645 | -123.1338 | -123.2025
776.7656 | 123.0698 | -60.9283 | 62.0178 | 0.13329 | -0.00073919 | -0.0030121 | 0.0017794 | 0.067368 | -0.00052335 | 0.067624 | -61.0565 | 62.1185 | -61.1389 | -61.2122 | 61.7432 | -0.036621 | 0.027466 | 0.013733 | 62.0407 | -61.2259 | -0.21057 | 0.10071 | -0.12817 | -0.28381 | -0.27466 | -0.29755 | 0.022888 | 0.082397 | 60.9558 | 60.9421 | 122.6715 | 123.0469 | -0.12817 | 122.9691 | 60.8917 | -0.29755 | 123.0469 | -0.12817 | 60.8917 | 122.6715 | 122.9691 | -123.1567 | -123.2437
777.7656 | 123.0881 | -60.9055 | 61.9904 | 0.2401 | -0.0026618 | -0.0010895 | 0.001993 | 0.063309 | -0.0011643 | 0.068265 | -61.2991 | 62.0544 | -61.1801 | -61.1938 | 61.7752 | -0.036621 | 0.018311 | -0.009155 | 62.0453 | -61.2167 | -0.27466 | 0.064087 | -0.39368 | -0.28839 | -0.21515 | -0.31128 | 0.054932 | -0.11902 | 60.9238 | 60.8963 | 122.6807 | 122.9599 | -0.39368 | 122.9507 | 60.8688 | -0.31128 | 122.9599 | -0.39368 | 60.8688 | 122.6807 | 122.9507 | -123.1705 | -123.2071
778.7656 | 123.1018 | -60.9375 | 61.9904 | -1.6901 | -0.003089 | -0.0010895 | 0.00092504 | 0.0663 | -0.0018051 | 0.068693 | -61.0474 | 62.1094 | -61.1481 | -61.2076 | 61.7157 | -0.054932 | 0 | 0.013733 | 62.059 | -61.1801 | -0.21057 | 0.11902 | -0.10986 | -0.27008 | -0.27466 | -0.24262 | 0.068665 | 0.10071 | 60.9375 | 60.9512 | 122.6532 | 123.0469 | -0.10986 | 122.9965 | 60.8826 | -0.24262 | 123.0469 | -0.10986 | 60.8826 | 122.6532 | 122.9965 | -123.1384 | -123.1705
779.7656 | 123.0652 | -60.9146 | 61.9812 | -0.25581 | -0.003089 | -0.0049347 | 0.0028476 | 0.065232 | -0.0013779 | 0.06912 | -61.0931 | 62.114 | -61.1389 | -61.2167 | 61.7386 | -0.054932 | -0.027466 | 0.013733 | 62.0407 | -61.1893 | -0.2243 | 0.13275 | -0.17853 | -0.30212 | -0.24262 | -0.27466 | 0.059509 | 0.045776 | 60.8871 | 60.9283 | 122.6532 | 123.0286 | -0.17853 | 122.9553 | 60.8597 | -0.27466 | 123.0286 | -0.17853 | 60.8597 | 122.6532 | 122.9553 | -123.1201 | -123.1705
780.7656 | 123.0789 | -60.9146 | 62.0132 | 0.15617 | -0.0028754 | -0.0032257 | 0.0030612 | 0.067155 | -0.0026595 | 0.070188 | -61.0794 | 62.1048 | -61.1572 | -61.2259 | 61.7111 | -0.059509 | 0.013733 | -0.004578 | 62.0499 | -61.1801 | -0.24262 | 0.091552 | -0.1648 | -0.31128 | -0.30212 | -0.2655 | 0.036621 | 0.07782 | 60.9283 | 60.91 | 122.6257 | 123.0194 | -0.1648 | 122.9645 | 60.8551 | -0.2655 | 123.0194 | -0.1648 | 60.8551 | 122.6257 | 122.9645 | -123.1705 | -123.1934
781.7656 | 123.056 | -60.9192 | 62.0132 | 0.17143 | -0.0020208 | 0.0033967 | 0.0017794 | 0.065659 | -0.0018051 | 0.068693 | -61.084 | 62.1094 | -61.1572 | -61.2122 | 61.7386 | -0.054932 | 0.009155 | -0.018311 | 62.0544 | -61.203 | -0.23804 | 0.09613 | -0.16479 | -0.29297 | -0.27466 | -0.28381 | 0.041198 | 0.073243 | 60.9283 | 60.9009 | 122.6578 | 123.0286 | -0.16479 | 122.9736 | 60.8643 | -0.28381 | 123.0286 | -0.16479 | 60.8643 | 122.6578 | 122.9736 | -123.1705 | -123.2162
782.7656 | 123.1064 | -60.9238 | 61.9995 | 0.20958 | -0.0024482 | -0.0038665 | 0.003702 | 0.065873 | -0.0033005 | 0.070188 | -61.0886 | 62.1094 | -61.1618 | -61.1938 | 61.7569 | -0.050354 | -0.032043 | 0.013733 | 62.0178 | -61.2076 | -0.23804 | 0.10986 | -0.1648 | -0.27008 | -0.24262 | -0.28381 | 0.01831 | 0.073242 | 60.8917 | 60.9375 | 122.6807 | 123.0331 | -0.1648 | 122.9416 | 60.8734 | -0.28381 | 123.0331 | -0.1648 | 60.8734 | 122.6807 | 122.9416 | -123.1613 | -123.2071
783.7656 | 123.1155 | -60.9238 | 61.972 | 0.23247 | -0.0039434 | -0.0055755 | 0.0011386 | 0.064805 | 0.00054465 | 0.068693 | -61.0748 | 62.114 | -61.1664 | -61.1847 | 61.7523 | -0.022888 | -0.064087 | 0.018311 | 62.027 | -61.1938 | -0.24262 | 0.14191 | -0.15106 | -0.26093 | -0.21973 | -0.27008 | 0.054932 | 0.091553 | 60.8597 | 60.9421 | 122.6761 | 123.0377 | -0.15106 | 122.9507 | 60.9009 | -0.27008 | 123.0377 | -0.15106 | 60.9009 | 122.6761 | 122.9507 | -123.1384 | -123.1659
784.7656 | 123.1934 | -60.878 | 61.9812 | 0.22484 | -0.00031179 | -0.0034393 | 0.0024202 | 0.063309 | -0.0035141 | 0.069547 | -61.0336 | 62.0361 | -61.1343 | -61.1206 | 61.8484 | 0.032043 | -0.1831 | 0.10071 | 61.9812 | -61.1481 | -0.25635 | 0.054932 | -0.15564 | -0.24261 | -0.13275 | -0.27008 | 0 | 0.10071 | 60.6949 | 60.9787 | 122.7264 | 122.9141 | -0.15564 | 122.8592 | 60.91 | -0.27008 | 122.9141 | -0.15564 | 60.91 | 122.7264 | 122.8592 | -123.1155 | -123.1293
785.7656 | 123.1705 | -60.878 | 62.0041 | 0.1104 | -0.0024482 | -0.0045075 | -0.0039884 | 0.063523 | -0.0018051 | 0.068693 | -61.0657 | 62.0224 | -61.1389 | -61.1664 | 61.8118 | 0.027466 | -0.07782 | 0.10986 | 61.9858 | -61.1526 | -0.26093 | 0.018311 | -0.18768 | -0.28839 | -0.19226 | -0.27466 | -0.01831 | 0.073242 | 60.8002 | 60.9879 | 122.6898 | 122.9004 | -0.18768 | 122.8638 | 60.9055 | -0.27466 | 122.9004 | -0.18768 | 60.9055 | 122.6898 | 122.8638 | -123.143 | -123.1567
786.7656 | 123.175 | -60.8734 | 61.9537 | 0.20958 | -0.0052252 | -0.0057891 | 0.002634 | 0.064378 | -0.0024459 | 0.068693 | -60.9833 | 62.0041 | -61.1069 | -61.1069 | 61.8256 | 0.045776 | -0.19684 | 0.11902 | 61.9904 | -61.1435 | -0.23346 | 0.050354 | -0.10986 | -0.23346 | -0.12817 | -0.27008 | 0.036621 | 0.1236 | 60.6766 | 60.9924 | 122.699 | 122.8775 | -0.10986 | 122.8638 | 60.9192 | -0.27008 | 122.8775 | -0.10986 | 60.9192 | 122.699 | 122.8638 | -123.0606 | -123.0972
787.7656 | 123.143 | -60.8963 | 62.0087 | 0.27061 | -0.0041572 | -0.0021575 | 0.0022066 | 0.06395 | -0.0033005 | 0.066343 | -61.0611 | 62.0499 | -61.1664 | -61.1664 | 61.7752 | -0.022888 | -0.10529 | 0.045776 | 61.9766 | -61.1389 | -0.27008 | 0.041199 | -0.16479 | -0.27008 | -0.23346 | -0.24262 | -0.032043 | 0.10529 | 60.791 | 60.9421 | 122.6715 | 122.9462 | -0.16479 | 122.8729 | 60.8734 | -0.24262 | 122.9462 | -0.16479 | 60.8734 | 122.6715 | 122.8729 | -123.175 | -123.1476
788.7656 | 123.1567 | -60.9055 | 61.9537 | 0.31639 | -0.0015936 | -0.0049347 | 0.0024202 | 0.062455 | -0.0035141 | 0.067197 | -61.0474 | 62.0361 | -61.1572 | -61.1389 | 61.7889 | -0.009155 | -0.14191 | 0.082397 | 61.9766 | -61.1664 | -0.25177 | 0.082398 | -0.14191 | -0.23346 | -0.1648 | -0.26093 | 0.022889 | 0.10986 | 60.7635 | 60.9879 | 122.6944 | 122.9416 | -0.14191 | 122.8821 | 60.8963 | -0.26093 | 122.9416 | -0.14191 | 60.8963 | 122.6944 | 122.8821 | -123.111 | -123.1201
789.7656 | 123.1659 | -60.8734 | 61.9217 | 0.26299 | -0.0039434 | -0.0042937 | 0.001993 | 0.065446 | -0.0041549 | 0.067411 | -60.9741 | 61.9949 | -61.1023 | -61.0977 | 61.8484 | 0.041199 | -0.20142 | 0.12817 | 61.9537 | -61.171 | -0.22888 | 0.073242 | -0.10071 | -0.2243 | -0.073242 | -0.29755 | 0.032043 | 0.12817 | 60.672 | 61.0016 | 122.7219 | 122.8683 | -0.10071 | 122.8271 | 60.9146 | -0.29755 | 122.8683 | -0.10071 | 60.9146 | 122.7219 | 122.8271 | -123.024 | -123.0927
790.7656 | 123.1705 | -60.878 | 61.9995 | 0.20195 | -0.0037298 | -0.0038665 | -0.002493 | 0.062882 | -0.0020187 | 0.070188 | -61.0016 | 62.0041 | -61.1343 | -61.1023 | 61.8301 | 0.036621 | -0.17395 | 0.13275 | 61.9812 | -61.1298 | -0.25635 | 0.004577 | -0.1236 | -0.2243 | -0.16937 | -0.25177 | -0.018311 | 0.13275 | 60.704 | 61.0107 | 122.7081 | 122.8821 | -0.1236 | 122.8592 | 60.9146 | -0.25177 | 122.8821 | -0.1236 | 60.9146 | 122.7081 | 122.8592 | -123.1338 | -123.1293
791.7656 | 123.1842 | -60.8688 | 61.9949 | 0.23247 | -0.0043708 | -0.0070709 | 7.0444e-05 | 0.062028 | -0.0041549 | 0.068906 | -61.0062 | 62.0132 | -61.1252 | -61.1069 | 61.853 | 0.027466 | -0.16022 | 0.10986 | 61.9583 | -61.1481 | -0.25635 | 0.018311 | -0.13733 | -0.23804 | -0.14191 | -0.27924 | -0.036621 | 0.11902 | 60.7086 | 60.9787 | 122.7219 | 122.8821 | -0.13733 | 122.8271 | 60.8963 | -0.27924 | 122.8821 | -0.13733 | 60.8963 | 122.7219 | 122.8271 | -123.1201 | -123.143
792.7656 | 123.1522 | -60.8734 | 61.9812 | 0.20958 | -0.0052252 | -0.0045075 | 0.0011386 | 0.063737 | -0.0035141 | 0.069974 | -61.0016 | 61.9812 | -61.1206 | -61.116 | 61.8347 | 0.036621 | -0.15564 | 0.11902 | 61.9904 | -61.1526 | -0.24719 | 0 | -0.12817 | -0.24262 | -0.14648 | -0.27924 | 0.009155 | 0.11902 | 60.7178 | 60.9924 | 122.7081 | 122.8546 | -0.12817 | 122.8638 | 60.91 | -0.27924 | 122.8546 | -0.12817 | 60.91 | 122.7081 | 122.8638 | -123.1018 | -123.1338
793.7656 | 123.175 | -60.8734 | 61.9949 | 0.17906 | -0.0056524 | -0.0055755 | -0.00057036 | 0.060746 | -0.0039413 | 0.067838 | -61.0062 | 61.9766 | -61.1343 | -61.1023 | 61.821 | 0.022888 | -0.15564 | 0.10529 | 61.9995 | -61.116 | -0.26093 | -0.01831 | -0.13275 | -0.22888 | -0.17395 | -0.24262 | 0.004578 | 0.12817 | 60.7178 | 60.9787 | 122.6944 | 122.85 | -0.13275 | 122.8729 | 60.8963 | -0.24262 | 122.85 | -0.13275 | 60.8963 | 122.6944 | 122.8729 | -123.1293 | -123.111
794.7656 | 123.1934 | -60.878 | 61.9583 | 0.25536 | -0.0060798 | -0.0038665 | 0.001993 | 0.063309 | -0.0045821 | 0.068052 | -60.8826 | 61.9766 | -61.1343 | -61.0565 | 61.853 | 0.054932 | -0.15564 | 0.15106 | 61.9629 | -61.1389 | -0.25635 | 0.018311 | -0.004577 | -0.17853 | -0.10529 | -0.26093 | 0.004578 | 0.25177 | 60.7224 | 61.0291 | 122.731 | 122.8546 | -0.004577 | 122.8409 | 60.9329 | -0.26093 | 122.8546 | -0.004577 | 60.9329 | 122.731 | 122.8409 | -123.0927 | -123.0972
795.7656 | 123.2117 | -60.8963 | 61.972 | 0.25536 | -0.004798 | -0.0032257 | 0.0034884 | 0.061387 | -0.0022323 | 0.068693 | -61.0748 | 61.9583 | -61.1435 | -61.0657 | 61.8622 | 0.054932 | -0.20142 | 0.11902 | 61.9766 | -61.1298 | -0.24719 | -0.013733 | -0.17853 | -0.16937 | -0.10986 | -0.23346 | 0.004578 | 0.068665 | 60.6949 | 61.0153 | 122.7585 | 122.8546 | -0.17853 | 122.8729 | 60.9512 | -0.23346 | 122.8546 | -0.17853 | 60.9512 | 122.7585 | 122.8729 | -123.1155 | -123.1018
796.7656 | 123.1476 | -60.8597 | 61.9812 | 0.20958 | -0.0054388 | -0.0062163 | 0.00028404 | 0.064378 | -0.0030869 | 0.068265 | -61.0016 | 61.972 | -61.1206 | -61.1252 | 61.8073 | 0.018311 | -0.13733 | 0.09613 | 61.9766 | -61.116 | -0.26093 | -0.009155 | -0.14191 | -0.2655 | -0.17395 | -0.25635 | -0.004577 | 0.11902 | 60.7224 | 60.9558 | 122.6669 | 122.8317 | -0.14191 | 122.8363 | 60.878 | -0.25635 | 122.8317 | -0.14191 | 60.878 | 122.6669 | 122.8363 | -123.1018 | -123.0972
797.7656 | 123.1659 | -60.8826 | 62.0041 | 0.1104 | -0.0045844 | -0.0055755 | -0.0018522 | 0.060746 | -0.0030869 | 0.068906 | -61.0474 | 61.9949 | -61.1298 | -61.1252 | 61.8164 | 0.027466 | -0.10071 | 0.11444 | 62.0087 | -61.0931 | -0.24719 | -0.009155 | -0.16479 | -0.24262 | -0.18768 | -0.21057 | 0.004578 | 0.082398 | 60.7819 | 60.997 | 122.699 | 122.8775 | -0.16479 | 122.8912 | 60.91 | -0.21057 | 122.8775 | -0.16479 | 60.91 | 122.699 | 122.8912 | -123.1338 | -123.0972
798.7656 | 123.1567 | -60.8688 | 61.9949 | 0.17143 | -0.0077888 | -0.0089935 | -0.00078396 | 0.060319 | -0.0047957 | 0.068693 | -61.0428 | 61.9583 | -61.1069 | -61.116 | 61.821 | 0.018311 | -0.082397 | 0.10529 | 62.0041 | -61.1389 | -0.23804 | -0.036621 | -0.17395 | -0.24719 | -0.17395 | -0.27008 | 0.009155 | 0.064087 | 60.7864 | 60.9741 | 122.6898 | 122.8271 | -0.17395 | 122.8729 | 60.8871 | -0.27008 | 122.8271 | -0.17395 | 60.8871 | 122.6898 | 122.8729 | -123.1018 | -123.1338
799.7656 | 123.1659 | -60.8871 | 61.9858 | 0.1104 | -0.0035162 | -0.0094207 | 0.0011386 | 0.061173 | -0.0033005 | 0.070829 | -61.0611 | 61.9812 | -61.1206 | -61.1298 | 61.7981 | 0.022888 | -0.082397 | 0.10071 | 61.972 | -61.116 | -0.23346 | -0.004578 | -0.17395 | -0.24262 | -0.18768 | -0.22888 | -0.013733 | 0.059509 | 60.8047 | 60.9879 | 122.6852 | 122.8683 | -0.17395 | 122.8592 | 60.91 | -0.22888 | 122.8683 | -0.17395 | 60.91 | 122.6852 | 122.8592 | -123.1064 | -123.1018
800.7656 | 123.1613 | -60.878 | 61.9812 | 0.18669 | -0.0050116 | -0.0057891 | 0.00071144 | 0.059891 | -0.0028731 | 0.068479 | -61.0291 | 61.972 | -61.1343 | -61.116 | 61.821 | 0.027466 | -0.07782 | 0.10986 | 61.9675 | -61.1069 | -0.25635 | -0.009155 | -0.15106 | -0.23804 | -0.16022 | -0.22888 | -0.013733 | 0.10529 | 60.8002 | 60.9879 | 122.699 | 122.85 | -0.15106 | 122.8455 | 60.9055 | -0.22888 | 122.85 | -0.15106 | 60.9055 | 122.699 | 122.8455 | -123.1155 | -123.0881
801.7656 | 123.1888 | -60.878 | 61.9949 | 0.20195 | -0.0054388 | -0.0064301 | 0.0041292 | 0.061387 | -0.0028731 | 0.06912 | -61.0245 | 61.9675 | -61.1069 | -61.1114 | 61.8256 | 0.022888 | -0.11902 | 0.09613 | 61.9995 | -61.1252 | -0.22888 | -0.027466 | -0.14648 | -0.23346 | -0.16937 | -0.24719 | 0.004578 | 0.082398 | 60.759 | 60.9741 | 122.7036 | 122.8455 | -0.14648 | 122.8775 | 60.9009 | -0.24719 | 122.8455 | -0.14648 | 60.9009 | 122.7036 | 122.8775 | -123.1018 | -123.1201
802.7656 | 123.1613 | -60.8597 | 62.0041 | 0.23247 | -0.0062934 | -0.0034393 | -0.00014316 | 0.060532 | -0.0045821 | 0.069974 | -61.0291 | 61.9675 | -61.1023 | -61.1206 | 61.7981 | 0.013733 | -0.13275 | 0.10529 | 61.9949 | -61.1069 | -0.24262 | -0.036621 | -0.16937 | -0.26093 | -0.20599 | -0.24719 | -0.009155 | 0.073242 | 60.7269 | 60.965 | 122.6578 | 122.8271 | -0.16937 | 122.8546 | 60.8734 | -0.24719 | 122.8271 | -0.16937 | 60.8734 | 122.6578 | 122.8546 | -123.1064 | -123.111
803.7656 | 123.1613 | -60.8871 | 62.0132 | 0.07988 | -0.0071478 | -0.011557 | -0.00014316 | 0.059891 | -0.0047957 | 0.068052 | -61.0382 | 61.972 | -61.1343 | -61.1069 | 61.8073 | 0.027466 | -0.082397 | 0.10986 | 61.9766 | -61.1069 | -0.24719 | -0.041199 | -0.15106 | -0.21973 | -0.20599 | -0.21973 | -0.036621 | 0.09613 | 60.8047 | 60.997 | 122.6944 | 122.8592 | -0.15106 | 122.8638 | 60.9146 | -0.21973 | 122.8592 | -0.15106 | 60.9146 | 122.6944 | 122.8638 | -123.1476 | -123.1201
804.7656 | 123.1705 | -60.8551 | 61.9904 | 0.10277 | -0.0050116 | -0.0072845 | -0.00035676 | 0.060746 | -0.0039413 | 0.069761 | -61.0336 | 61.9995 | -61.1298 | -61.1023 | 61.8347 | 0.073242 | -0.073242 | 0.15564 | 62.0041 | -61.116 | -0.27466 | 0.009156 | -0.17853 | -0.24719 | -0.15564 | -0.26093 | 0.013733 | 0.096131 | 60.7819 | 61.0107 | 122.6898 | 122.8546 | -0.17853 | 122.8592 | 60.9283 | -0.26093 | 122.8546 | -0.17853 | 60.9283 | 122.6898 | 122.8592 | -123.1201 | -123.1064
805.7656 | 123.175 | -60.878 | 61.9858 | 0.10277 | -0.0026618 | -0.0060027 | 0.00071144 | 0.062455 | -0.0041549 | 0.071042 | -61.0245 | 61.9858 | -61.0977 | -61.0931 | 61.8393 | 0.059509 | -0.068665 | 0.14648 | 61.9949 | -61.0886 | -0.21973 | 0 | -0.14648 | -0.21515 | -0.14648 | -0.21057 | 0.009155 | 0.073242 | 60.8093 | 61.0245 | 122.7173 | 122.8638 | -0.14648 | 122.8729 | 60.9375 | -0.21057 | 122.8638 | -0.14648 | 60.9375 | 122.7173 | 122.8729 | -123.0835 | -123.0743
806.7812 | 123.0881 | -60.8826 | 62.0316 | -0.16426 | -0.0033026 | -0.0027985 | 0.0073336 | 0.062882 | -0.0047957 | 0.067838 | -61.0245 | 62.0682 | -61.116 | -61.1435 | 61.7798 | 0.022888 | 0.10071 | 0.11444 | 62.0407 | -61.1526 | -0.23346 | 0.036621 | -0.14191 | -0.26093 | -0.25177 | -0.27008 | 0.009155 | 0.091553 | 60.9833 | 60.997 | 122.6624 | 122.9507 | -0.14191 | 122.9233 | 60.9055 | -0.27008 | 122.9507 | -0.14191 | 60.9055 | 122.6624 | 122.9233 | -123.1476 | -123.1842
807.7656 | 123.1796 | -60.8917 | 62.0041 | 0.034104 | -0.0073614 | -0.0013031 | -0.0020658 | 0.062241 | -0.0041549 | 0.068479 | -61.0336 | 61.9812 | -61.1343 | -61.0886 | 61.8347 | 0.07782 | -0.073242 | 0.15564 | 61.9812 | -61.0703 | -0.24261 | -0.022888 | -0.14191 | -0.19684 | -0.16937 | -0.17853 | -0.022888 | 0.10071 | 60.8185 | 61.0474 | 122.7264 | 122.8729 | -0.14191 | 122.8729 | 60.9695 | -0.17853 | 122.8729 | -0.14191 | 60.9695 | 122.7264 | 122.8729 | -123.1384 | -123.0743
808.7656 | 123.1705 | -60.8826 | 61.9858 | 0.14854 | -0.0060798 | -0.0064301 | -0.0018522 | 0.062241 | -0.0030869 | 0.068693 | -61.0382 | 61.9812 | -61.1114 | -61.1114 | 61.8118 | 0.032043 | -0.082397 | 0.11444 | 61.9995 | -61.116 | -0.22888 | -0.004578 | -0.15564 | -0.22888 | -0.17395 | -0.23346 | 0.013733 | 0.073242 | 60.8002 | 60.997 | 122.6944 | 122.8638 | -0.15564 | 122.8821 | 60.9146 | -0.23346 | 122.8638 | -0.15564 | 60.9146 | 122.6944 | 122.8821 | -123.0972 | -123.1018
809.7656 | 123.1705 | -60.878 | 61.9995 | 0.018845 | -0.0067206 | -0.0038665 | 0.0013522 | 0.062455 | -0.0056503 | 0.068479 | -61.0428 | 61.94 | -61.1069 | -61.0977 | 61.8347 | 0.073242 | -0.064087 | 0.16479 | 61.9995 | -61.084 | -0.22888 | -0.05951 | -0.16479 | -0.21973 | -0.1648 | -0.20599 | 0 | 0.064087 | 60.8139 | 61.0428 | 122.7127 | 122.818 | -0.16479 | 122.8775 | 60.9512 | -0.20599 | 122.818 | -0.16479 | 60.9512 | 122.7127 | 122.8775 | -123.1064 | -123.0835
810.7656 | 123.1796 | -60.8505 | 62.0041 | 0.1638 | -0.0054388 | -0.0042937 | -0.0022794 | 0.061173 | -0.0041549 | 0.070188 | -61.0382 | 61.9949 | -61.1298 | -61.0977 | 61.8484 | 0.059509 | -0.082397 | 0.14191 | 62.0087 | -61.0931 | -0.27924 | -0.009155 | -0.18768 | -0.24719 | -0.15564 | -0.24262 | 0.004578 | 0.091553 | 60.7681 | 60.9924 | 122.699 | 122.8455 | -0.18768 | 122.8592 | 60.91 | -0.24262 | 122.8455 | -0.18768 | 60.91 | 122.699 | 122.8592 | -123.1338 | -123.0972
811.7812 | 123.1201 | -60.91 | 62.0316 | -0.04219 | -0.0045844 | -0.0030121 | 0.0092562 | 0.063096 | -0.0030869 | 0.070188 | -60.9604 | 62.0865 | -61.116 | -61.0428 | 61.821 | 0.082397 | 0.050354 | 0.15106 | 62.0316 | -61.1298 | -0.20599 | 0.054932 | -0.050354 | -0.13275 | -0.21057 | -0.21973 | 0 | 0.15564 | 60.9604 | 61.0611 | 122.731 | 122.9965 | -0.050354 | 122.9416 | 60.9924 | -0.21973 | 122.9965 | -0.050354 | 60.9924 | 122.731 | 122.9416 | -123.1476 | -123.1613
812.7656 | 123.1888 | -60.878 | 61.9812 | 0.049362 | -0.0045844 | -0.0045075 | -0.0022794 | 0.062241 | -0.0052231 | 0.069333 | -61.0245 | 61.9995 | -61.0931 | -61.0748 | 61.8896 | 0.12817 | -0.082397 | 0.2243 | 61.9537 | -61.0886 | -0.21515 | 0.018311 | -0.14648 | -0.19684 | -0.091553 | -0.21057 | -0.027466 | 0.068665 | 60.7956 | 61.1023 | 122.7676 | 122.8775 | -0.14648 | 122.8317 | 61.0062 | -0.21057 | 122.8775 | -0.14648 | 61.0062 | 122.7676 | 122.8317 | -123.0743 | -123.0698
813.7656 | 123.1979 | -60.8688 | 61.9949 | -0.057449 | -0.0069342 | -0.0066437 | -0.00035676 | 0.06096 | -0.0047957 | 0.069974 | -60.997 | 62.0132 | -61.084 | -61.0428 | 61.8942 | 0.11902 | -0.073242 | 0.20599 | 61.9858 | -61.0931 | -0.21515 | 0.018311 | -0.12817 | -0.17395 | -0.10071 | -0.22431 | -0.009155 | 0.086975 | 60.7956 | 61.0748 | 122.7631 | 122.8821 | -0.12817 | 122.8546 | 60.9879 | -0.22431 | 122.8821 | -0.12817 | 60.9879 | 122.7631 | 122.8546 | -123.0789 | -123.0881
814.7656 | 123.2071 | -60.8597 | 62.0132 | -0.0040434 | -0.0086432 | -0.0036529 | -0.00035676 | 0.062669 | -0.0041549 | 0.067838 | -60.9924 | 61.9675 | -61.1023 | -61.0519 | 61.9034 | 0.1236 | -0.068665 | 0.21515 | 61.9949 | -61.084 | -0.24262 | -0.045777 | -0.13275 | -0.19226 | -0.10986 | -0.2243 | -0.018311 | 0.10986 | 60.791 | 61.0748 | 122.7631 | 122.8271 | -0.13275 | 122.8546 | 60.9833 | -0.2243 | 122.8271 | -0.13275 | 60.9833 | 122.7631 | 122.8546 | -123.1155 | -123.0972
815.7656 | 123.175 | -60.8826 | 61.9766 | -0.4084 | -0.005866 | -0.0064301 | -0.00035676 | 0.0616 | -0.0054367 | 0.06912 | -61.0657 | 61.9766 | -61.1114 | -61.1023 | 61.8347 | 0.054932 | -0.068665 | 0.11902 | 61.9812 | -61.0931 | -0.22888 | 0 | -0.18311 | -0.21973 | -0.14191 | -0.21057 | 0.004577 | 0.045776 | 60.8139 | 61.0016 | 122.7173 | 122.8592 | -0.18311 | 122.8638 | 60.9375 | -0.21057 | 122.8592 | -0.18311 | 60.9375 | 122.7173 | 122.8638 | -123.0881 | -123.0698
816.7812 | 123.1201 | -60.8963 | 62.0041 | -0.019302 | -0.0026618 | -0.0042937 | 0.0086154 | 0.062241 | -0.0052231 | 0.068693 | -60.965 | 62.0865 | -61.0886 | -61.0657 | 61.8347 | 0.054932 | 0 | -0.009155 | 62.0041 | -61.1526 | -0.19226 | 0.082398 | -0.068665 | -0.16937 | -0.16937 | -0.25635 | 0 | 0.1236 | 60.8963 | 60.8871 | 122.731 | 122.9828 | -0.068665 | 122.9004 | 60.9512 | -0.25635 | 122.9828 | -0.068665 | 60.9512 | 122.731 | 122.9004 | -123.0927 | -123.1567
817.7656 | 123.1796 | -60.8688 | 61.9812 | -0.04219 | -0.0054388 | -0.0089935 | -0.001425 | 0.062241 | -0.0035141 | 0.067624 | -61.0199 | 62.0041 | -61.116 | -61.0703 | 61.8942 | 0.10529 | -0.059509 | 0.17853 | 62.0178 | -61.0474 | -0.24719 | 0.022888 | -0.15106 | -0.20142 | -0.086975 | -0.17853 | 0.036621 | 0.096131 | 60.8093 | 61.0474 | 122.7631 | 122.8729 | -0.15106 | 122.8867 | 60.9741 | -0.17853 | 122.8729 | -0.15106 | 60.9741 | 122.7631 | 122.8867 | -123.0972 | -123.0286
818.7656 | 123.2117 | -60.8368 | 62.0132 | -0.04219 | -0.0071478 | -0.0034393 | 0.00092504 | 0.060746 | -0.0033005 | 0.067838 | -60.9741 | 61.972 | -61.0794 | -61.0153 | 61.9217 | 0.1831 | -0.064087 | 0.26093 | 61.9995 | -61.0748 | -0.24262 | -0.041199 | -0.13733 | -0.17853 | -0.091553 | -0.23804 | -0.013733 | 0.10529 | 60.7727 | 61.0977 | 122.7585 | 122.8088 | -0.13733 | 122.8363 | 61.0199 | -0.23804 | 122.8088 | -0.13733 | 61.0199 | 122.7585 | 122.8363 | -123.0927 | -123.0881
819.7656 | 123.1979 | -60.8734 | 62.0087 | 0.034104 | -0.0056524 | -0.0070709 | -0.001425 | 0.061173 | -0.0050095 | 0.068265 | -61.0107 | 61.9583 | -61.116 | -61.0748 | 61.8713 | 0.10529 | -0.059509 | 0.19226 | 61.9766 | -61.0886 | -0.24262 | -0.050354 | -0.13733 | -0.20142 | -0.13733 | -0.21515 | -0.032043 | 0.10529 | 60.8139 | 61.0657 | 122.7448 | 122.8317 | -0.13733 | 122.85 | 60.9787 | -0.21515 | 122.8317 | -0.13733 | 60.9787 | 122.7448 | 122.85 | -123.1247 | -123.0972
820.7656 | 123.23 | -60.8459 | 61.9858 | -0.11085 | -0.0080024 | -0.0055755 | 7.0444e-05 | 0.061387 | -0.0041549 | 0.067411 | -60.9741 | 61.9904 | -61.0886 | -61.0199 | 61.9171 | 0.16022 | -0.07782 | 0.27466 | 61.9446 | -61.0565 | -0.24262 | 0.004577 | -0.12817 | -0.17395 | -0.068665 | -0.21057 | -0.041199 | 0.11444 | 60.7681 | 61.1206 | 122.7631 | 122.8363 | -0.12817 | 122.7905 | 61.0062 | -0.21057 | 122.8363 | -0.12817 | 61.0062 | 122.7631 | 122.7905 | -123.0743 | -123.0423
821.7656 | 123.1155 | -60.8734 | 62.0087 | 0.026474 | -0.003089 | -0.0040801 | 0.0090426 | 0.063523 | -0.0045821 | 0.068052 | -61.0748 | 62.0041 | -61.1664 | -61.0886 | 61.8073 | 0.036621 | 0.022888 | 0.13275 | 62.0316 | -61.1069 | -0.29297 | -0.004578 | -0.20142 | -0.21515 | -0.20142 | -0.23346 | 0.022888 | 0.091553 | 60.8963 | 61.0062 | 122.6807 | 122.8775 | -0.20142 | 122.905 | 60.91 | -0.23346 | 122.8775 | -0.20142 | 60.91 | 122.6807 | 122.905 | -123.175 | -123.1155
822.7656 | 123.2071 | -60.8643 | 61.9949 | 0.10277 | -0.0052252 | -0.0066437 | -0.0018522 | 0.062455 | -0.0033005 | 0.068265 | -61.0199 | 61.9858 | -61.1252 | -61.0977 | 61.8851 | 0.09613 | -0.054932 | 0.17395 | 61.9949 | -61.0886 | -0.26093 | -0.009155 | -0.15564 | -0.23346 | -0.10986 | -0.2243 | 0 | 0.10529 | 60.8093 | 61.0382 | 122.7493 | 122.85 | -0.15564 | 122.8592 | 60.9604 | -0.2243 | 122.85 | -0.15564 | 60.9604 | 122.7493 | 122.8592 | -123.1201 | -123.0835
823.7656 | 123.2346 | -60.8505 | 62.0041 | -0.04982 | -0.0062934 | -0.0053619 | -0.00057036 | 0.06096 | -0.0060775 | 0.068265 | -60.9741 | 62.0041 | -61.0886 | -61.0245 | 61.908 | 0.16937 | -0.073242 | 0.27466 | 61.9812 | -61.0565 | -0.23804 | 0 | -0.1236 | -0.17395 | -0.09613 | -0.20599 | -0.022888 | 0.11444 | 60.7773 | 61.1252 | 122.7585 | 122.8546 | -0.1236 | 122.8317 | 61.0199 | -0.20599 | 122.8546 | -0.1236 | 61.0199 | 122.7585 | 122.8317 | -123.0927 | -123.0606
824.7656 | 123.2391 | -60.8597 | 62.0361 | -0.11085 | -0.007575 | -0.0081389 | 0.0022066 | 0.060532 | -0.0037277 | 0.069974 | -60.9467 | 61.9675 | -61.0794 | -61.0291 | 61.9171 | 0.15564 | -0.073242 | 0.26093 | 61.9904 | -61.0657 | -0.21973 | -0.068665 | -0.086975 | -0.16937 | -0.11902 | -0.20599 | -0.045777 | 0.13275 | 60.7864 | 61.1206 | 122.7768 | 122.8271 | -0.086975 | 122.85 | 61.0153 | -0.20599 | 122.8271 | -0.086975 | 61.0153 | 122.7768 | 122.85 | -123.1155 | -123.1018
825.7656 | 123.175 | -60.8505 | 62.0224 | -0.11848 | -0.009284 | -0.0092071 | 0.0015658 | 0.061814 | -0.0050095 | 0.068265 | -60.7452 | 62.0407 | -61.0474 | -61.0474 | 61.8759 | 0.14191 | -0.059509 | 0.27924 | 61.9812 | -61.0565 | -0.19684 | 0.01831 | 0.10529 | -0.19684 | -0.14648 | -0.20599 | -0.041199 | 0.30212 | 60.791 | 61.1298 | 122.7264 | 122.8912 | 0.10529 | 122.8317 | 60.9924 | -0.20599 | 122.8912 | 0.10529 | 60.9924 | 122.7264 | 122.8317 | -123.0698 | -123.0789
826.7656 | 123.1842 | -60.8551 | 62.0132 | -0.12611 | -0.003089 | -0.0085663 | 0.00049764 | 0.062028 | -0.0060775 | 0.070188 | -60.7315 | 62.0499 | -61.0657 | -61.0474 | 61.8942 | 0.14648 | -0.050354 | 0.27924 | 61.9766 | -61.0886 | -0.21057 | 0.036621 | 0.1236 | -0.19226 | -0.11902 | -0.23346 | -0.036621 | 0.33417 | 60.8047 | 61.1343 | 122.7493 | 122.905 | 0.1236 | 122.8317 | 61.0016 | -0.23346 | 122.905 | 0.1236 | 61.0016 | 122.7493 | 122.8317 | -123.0789 | -123.1018
827.7656 | 123.1888 | -60.8551 | 62.0041 | -0.13374 | -0.0086432 | -0.0072845 | 0.0015658 | 0.060746 | -0.0041549 | 0.067411 | -60.7864 | 62.0636 | -61.0611 | -61.0565 | 61.8896 | 0.13733 | -0.004578 | 0.2655 | 61.9766 | -61.0657 | -0.20599 | 0.05951 | 0.068665 | -0.20142 | -0.11444 | -0.21057 | -0.027465 | 0.27466 | 60.8505 | 61.1206 | 122.7448 | 122.9187 | 0.068665 | 122.8317 | 60.9924 | -0.21057 | 122.9187 | 0.068665 | 60.9924 | 122.7448 | 122.8317 | -123.0652 | -123.0698
828.7656 | 123.1796 | -60.8551 | 62.027 | -0.17189 | -0.0084296 | -0.0079253 | 0.003702 | 0.0616 | -0.0056503 | 0.069547 | -60.8368 | 62.0316 | -61.0748 | -61.0565 | 61.9125 | 0.15106 | -0.009155 | 0.27008 | 61.9858 | -61.084 | -0.21973 | 0.004577 | 0.018311 | -0.20142 | -0.11444 | -0.22888 | -0.041199 | 0.23804 | 60.8459 | 61.1252 | 122.7676 | 122.8867 | 0.018311 | 122.8409 | 61.0062 | -0.22888 | 122.8867 | 0.018311 | 61.0062 | 122.7676 | 122.8409 | -123.1018 | -123.111
829.7656 | 123.2483 | -60.8734 | 61.9995 | -0.026932 | -0.0045844 | -0.0042937 | 0.00049764 | 0.058823 | -0.0018051 | 0.066556 | -60.9695 | 62.0087 | -61.0977 | -61.0153 | 61.9171 | 0.17395 | -0.068665 | 0.27924 | 61.9537 | -61.0794 | -0.2243 | 0.009155 | -0.09613 | -0.14191 | -0.082398 | -0.20599 | -0.045777 | 0.12817 | 60.8047 | 61.1526 | 122.7905 | 122.8821 | -0.09613 | 122.8271 | 61.0474 | -0.20599 | 122.8821 | -0.09613 | 61.0474 | 122.7905 | 122.8271 | -123.0972 | -123.0789
830.7656 | 123.1979 | -60.8505 | 62.0316 | -1.3544 | -0.005866 | -0.011771 | 0.002634 | 0.06096 | -0.0035141 | 0.06912 | -60.9238 | 62.0544 | -61.0886 | -61.0611 | 61.8942 | 0.12817 | -0.004578 | 0.25635 | 61.972 | -61.1023 | -0.23804 | 0.022888 | -0.073242 | -0.21057 | -0.13733 | -0.25177 | -0.059509 | 0.1648 | 60.8459 | 61.1069 | 122.7448 | 122.905 | -0.073242 | 122.8226 | 60.9787 | -0.25177 | 122.905 | -0.073242 | 60.9787 | 122.7448 | 122.8226 | -123.1201 | -123.1338
831.7656 | 123.1247 | -60.8963 | 62.0453 | -0.19478 | -0.005866 | -0.0023711 | 0.0017794 | 0.063309 | -0.0052231 | 0.067838 | -60.997 | 62.0361 | -61.0931 | -61.0657 | 61.8576 | 0.11902 | 0.07782 | 0.20599 | 62.0178 | -61.0886 | -0.19684 | -0.009155 | -0.10071 | -0.16937 | -0.18768 | -0.19226 | -0.027466 | 0.096131 | 60.9741 | 61.1023 | 122.7539 | 122.9324 | -0.10071 | 122.9141 | 61.0153 | -0.19226 | 122.9324 | -0.10071 | 61.0153 | 122.7539 | 122.9141 | -123.1384 | -123.1338
832.7656 | 123.1201 | -60.8871 | 62.0499 | -0.21767 | -0.006507 | -0.0049347 | 0.0045566 | 0.062028 | -0.0043685 | 0.068693 | -60.9741 | 62.0499 | -61.0977 | -61.0794 | 61.853 | 0.10071 | 0.068665 | 0.19684 | 62.0316 | -61.1206 | -0.21057 | 0 | -0.086975 | -0.19226 | -0.19684 | -0.23346 | -0.018311 | 0.1236 | 60.9558 | 61.084 | 122.7402 | 122.937 | -0.086975 | 122.9187 | 60.9879 | -0.23346 | 122.937 | -0.086975 | 60.9879 | 122.7402 | 122.9187 | -123.1476 | -123.1705
833.7656 | 123.111 | -60.8505 | 62.0453 | -0.21767 | -0.0052252 | -0.0040801 | 0.0013522 | 0.059678 | -0.0028731 | 0.067197 | -60.9741 | 62.027 | -61.1023 | -61.0657 | 61.8668 | 0.11902 | 0.082397 | 0.21057 | 62.0132 | -61.0886 | -0.25177 | -0.01831 | -0.1236 | -0.21515 | -0.17853 | -0.23804 | -0.032043 | 0.12817 | 60.9329 | 61.0611 | 122.7173 | 122.8775 | -0.1236 | 122.8638 | 60.9695 | -0.23804 | 122.8775 | -0.1236 | 60.9695 | 122.7173 | 122.8638 | -123.1476 | -123.1338
834.7656 | 123.1338 | -60.8643 | 62.0453 | -0.19478 | -0.007575 | -0.0042937 | 0.0028476 | 0.06395 | -0.0052231 | 0.067838 | -60.9833 | 62.0316 | -61.1023 | -61.0565 | 61.8576 | 0.10986 | 0.073242 | 0.21515 | 62.0316 | -61.084 | -0.23804 | -0.013733 | -0.11902 | -0.19226 | -0.18768 | -0.21973 | -0.013733 | 0.11902 | 60.9375 | 61.0794 | 122.7219 | 122.8958 | -0.11902 | 122.8958 | 60.9741 | -0.21973 | 122.8958 | -0.11902 | 60.9741 | 122.7219 | 122.8958 | -123.1476 | -123.1293
835.7656 | 123.1201 | -60.8734 | 62.0132 | -0.17189 | -0.0060798 | -0.0042937 | 0.0030612 | 0.062882 | -0.0035141 | 0.068265 | -60.9833 | 62.0407 | -61.116 | -61.0657 | 61.8576 | 0.10986 | 0.073242 | 0.21973 | 62.0316 | -61.0703 | -0.24262 | 0.027465 | -0.10986 | -0.19226 | -0.15564 | -0.19684 | 0.01831 | 0.13275 | 60.9467 | 61.0931 | 122.731 | 122.9141 | -0.10986 | 122.905 | 60.9833 | -0.19684 | 122.9141 | -0.10986 | 60.9833 | 122.731 | 122.905 | -123.1293 | -123.0835
836.7656 | 123.23 | -60.8643 | 62.0041 | -0.080337 | -0.0033026 | -0.0036529 | -0.0016386 | 0.06096 | -0.0039413 | 0.068052 | -60.9604 | 61.9858 | -61.1069 | -61.0062 | 61.9354 | 0.1831 | -0.086975 | 0.27466 | 62.0132 | -61.0474 | -0.24262 | -0.01831 | -0.09613 | -0.14191 | -0.068664 | -0.1831 | 0.009156 | 0.14648 | 60.7773 | 61.1389 | 122.7997 | 122.85 | -0.09613 | 122.8775 | 61.0474 | -0.1831 | 122.85 | -0.09613 | 61.0474 | 122.7997 | 122.8775 | -123.111 | -123.0515
837.7656 | 123.1018 | -60.8597 | 62.0361 | -0.21767 | -0.004798 | -0.0053619 | 0.002634 | 0.062241 | -0.0058639 | 0.068906 | -60.9924 | 61.9949 | -61.0931 | -61.0657 | 61.8393 | 0.10986 | 0.082397 | 0.20142 | 62.0224 | -61.0794 | -0.23346 | -0.041199 | -0.13275 | -0.20599 | -0.19684 | -0.21973 | -0.013733 | 0.10071 | 60.9421 | 61.0611 | 122.699 | 122.8546 | -0.13275 | 122.8821 | 60.9695 | -0.21973 | 122.8546 | -0.13275 | 60.9695 | 122.699 | 122.8821 | -123.1293 | -123.1155
838.7656 | 123.111 | -60.8643 | 62.027 | -0.20241 | -0.004798 | -0.0057891 | 0.001993 | 0.063523 | -0.0037277 | 0.068693 | -60.9879 | 62.027 | -61.116 | -61.0794 | 61.8576 | 0.10986 | 0.091553 | 0.21057 | 62.027 | -61.0886 | -0.25177 | 0 | -0.1236 | -0.21515 | -0.16937 | -0.2243 | 0 | 0.12817 | 60.9558 | 61.0748 | 122.7219 | 122.8912 | -0.1236 | 122.8912 | 60.9741 | -0.2243 | 122.8912 | -0.1236 | 60.9741 | 122.7219 | 122.8912 | -123.143 | -123.1155
839.7656 | 123.0698 | -60.8917 | 62.0682 | -0.23293 | -0.0028754 | -0.0055755 | 0.0051974 | 0.065232 | -0.0030869 | 0.068479 | -61.0474 | 62.0773 | -61.1069 | -61.1252 | 61.8073 | 0.068665 | 0.15106 | 0.14191 | 62.0544 | -61.0931 | -0.21515 | 0.009156 | -0.15564 | -0.23346 | -0.26093 | -0.20142 | -0.013733 | 0.05951 | 61.0428 | 61.0336 | 122.699 | 122.9691 | -0.15564 | 122.9462 | 60.9604 | -0.20142 | 122.9691 | -0.15564 | 60.9604 | 122.699 | 122.9462 | -123.175 | -123.1613
840.7656 | 123.0606 | -60.91 | 62.0407 | -0.20241 | -0.0043708 | -0.0055755 | 0.0049838 | 0.064805 | -0.0047957 | 0.067411 | -61.0245 | 62.114 | -61.1343 | -61.116 | 61.7935 | 0.059509 | 0.14648 | 0.14648 | 62.0636 | -61.1252 | -0.2243 | 0.073243 | -0.11444 | -0.20599 | -0.24719 | -0.21515 | 0.022889 | 0.10986 | 61.0565 | 61.0565 | 122.7036 | 123.024 | -0.11444 | 122.9736 | 60.9695 | -0.21515 | 123.024 | -0.11444 | 60.9695 | 122.7036 | 122.9736 | -123.175 | -123.1659
841.7656 | 123.1018 | -60.8963 | 62.0499 | -0.17952 | -0.0043708 | -0.0068573 | 0.0015658 | 0.063737 | -0.0062911 | 0.069761 | -61.0428 | 62.0773 | -61.1206 | -61.1526 | 61.8301 | 0.050354 | 0.16479 | 0.14648 | 62.0773 | -61.1298 | -0.2243 | 0.027466 | -0.14648 | -0.25635 | -0.21973 | -0.23346 | 0.027466 | 0.077819 | 61.0611 | 61.0428 | 122.7264 | 122.9736 | -0.14648 | 122.9736 | 60.9467 | -0.23346 | 122.9736 | -0.14648 | 60.9467 | 122.7264 | 122.9736 | -123.1705 | -123.1796
842.7656 | 123.1338 | -60.8643 | 62.027 | -0.20241 | -0.0043708 | -0.0040801 | 0.0013522 | 0.062669 | -0.0050095 | 0.068265 | -60.9879 | 62.0407 | -61.0977 | -61.0931 | 61.8668 | 0.1236 | 0.059509 | 0.21973 | 62.0178 | -61.0931 | -0.23346 | 0.013732 | -0.1236 | -0.22888 | -0.16022 | -0.22888 | -0.009156 | 0.10986 | 60.9238 | 61.084 | 122.731 | 122.905 | -0.1236 | 122.8821 | 60.9879 | -0.22888 | 122.905 | -0.1236 | 60.9879 | 122.731 | 122.8821 | -123.1247 | -123.1201
843.7656 | 123.1293 | -60.878 | 62.0407 | -0.24818 | -0.0067206 | -0.0072845 | 0.001993 | 0.063737 | -0.0054367 | 0.068906 | -60.997 | 62.0407 | -61.1069 | -61.0886 | 61.853 | 0.10529 | 0.068665 | 0.21057 | 62.0224 | -61.1252 | -0.22888 | 0 | -0.11902 | -0.21057 | -0.18768 | -0.24719 | -0.01831 | 0.10986 | 60.9467 | 61.0886 | 122.731 | 122.9187 | -0.11902 | 122.9004 | 60.9833 | -0.24719 | 122.9187 | -0.11902 | 60.9833 | 122.731 | 122.9004 | -123.1476 | -123.1659
844.7656 | 123.0698 | -60.9192 | 62.0499 | -0.21004 | -0.0041572 | -0.0060027 | 0.004343 | 0.062028 | -0.0058639 | 0.068052 | -61.0428 | 62.0865 | -61.1114 | -61.1298 | 61.7981 | 0.059509 | 0.15564 | 0.14191 | 62.0636 | -61.1252 | -0.19226 | 0.036621 | -0.1236 | -0.21057 | -0.25177 | -0.20599 | 0.013733 | 0.068664 | 61.0748 | 61.0611 | 122.7173 | 123.0057 | -0.1236 | 122.9828 | 60.9787 | -0.20599 | 123.0057 | -0.1236 | 60.9787 | 122.7173 | 122.9828 | -123.1613 | -123.175
845.7656 | 123.0743 | -60.9192 | 62.0636 | -0.17189 | -0.0041572 | -0.0055755 | 0.0058382 | 0.063096 | -0.0018051 | 0.069974 | -61.0519 | 62.1185 | -61.1389 | -61.1252 | 61.8073 | 0.054932 | 0.12817 | 0.13733 | 62.0132 | -61.1435 | -0.21973 | 0.054931 | -0.13275 | -0.20599 | -0.25635 | -0.2243 | -0.050354 | 0.086975 | 61.0474 | 61.0565 | 122.7264 | 123.0377 | -0.13275 | 122.9324 | 60.9741 | -0.2243 | 123.0377 | -0.13275 | 60.9741 | 122.7264 | 122.9324 | -123.2025 | -123.2071
846.7656 | 123.0835 | -60.9146 | 62.0499 | -0.14137 | -0.00095279 | -0.0051483 | 0.0022066 | 0.064591 | -0.0043685 | 0.06912 | -61.0428 | 62.1094 | -61.1023 | -61.1343 | 61.8073 | 0.059509 | 0.1236 | 0.13733 | 62.0544 | -61.1298 | -0.18768 | 0.059509 | -0.12817 | -0.21973 | -0.24262 | -0.21515 | 0.004577 | 0.059509 | 61.0382 | 61.0519 | 122.7219 | 123.024 | -0.12817 | 122.9691 | 60.9741 | -0.21515 | 123.024 | -0.12817 | 60.9741 | 122.7219 | 122.9691 | -123.1522 | -123.1796
847.7656 | 123.1064 | -60.9055 | 62.0407 | -0.10323 | -0.0035162 | -0.0062163 | 0.002634 | 0.064591 | -0.0054367 | 0.068052 | -61.0336 | 62.1048 | -61.1252 | -61.1389 | 61.8027 | 0.068665 | 0.13733 | 0.14648 | 62.0544 | -61.1298 | -0.21973 | 0.064087 | -0.12817 | -0.23346 | -0.23804 | -0.2243 | 0.013733 | 0.091553 | 61.0428 | 61.0519 | 122.7081 | 123.0103 | -0.12817 | 122.9599 | 60.9741 | -0.2243 | 123.0103 | -0.12817 | 60.9741 | 122.7081 | 122.9599 | -123.1659 | -123.1705
848.7656 | 123.1018 | -60.9009 | 62.027 | -0.10323 | -0.0028754 | -0.0055755 | 0.0017794 | 0.062669 | -0.0024459 | 0.071256 | -61.0611 | 62.1185 | -61.1298 | -61.1252 | 61.7981 | 0.045776 | 0.13275 | 0.14191 | 62.0499 | -61.1435 | -0.22888 | 0.091552 | -0.16022 | -0.2243 | -0.22888 | -0.24261 | 0.022888 | 0.068665 | 61.0336 | 61.0428 | 122.699 | 123.0194 | -0.16022 | 122.9507 | 60.9467 | -0.24261 | 123.0194 | -0.16022 | 60.9467 | 122.699 | 122.9507 | -123.1567 | -123.1705
849.7656 | 123.0927 | -60.8826 | 62.059 | -0.26344 | -0.0050116 | -0.0013031 | 0.0017794 | 0.0616 | -0.0018051 | 0.067624 | -61.0611 | 62.146 | -61.116 | -61.1481 | 61.8027 | 0.068665 | 0.15106 | 0.14191 | 62.0407 | -61.1298 | -0.23346 | 0.086975 | -0.17853 | -0.2655 | -0.25635 | -0.24719 | -0.018311 | 0.054932 | 61.0336 | 61.0245 | 122.6852 | 123.0286 | -0.17853 | 122.9233 | 60.9512 | -0.24719 | 123.0286 | -0.17853 | 60.9512 | 122.6852 | 122.9233 | -123.175 | -123.1888
850.7656 | 123.0286 | -60.8917 | 62.059 | -0.21004 | -0.0039434 | -0.0023711 | 0.0024202 | 0.062669 | -0.0020187 | 0.068693 | -61.0519 | 62.1277 | -61.1343 | -61.1526 | 61.7935 | 0.059509 | 0.16022 | 0.16022 | 62.0773 | -61.1298 | -0.24261 | 0.068665 | -0.16022 | -0.26092 | -0.2655 | -0.23804 | 0.018311 | 0.082397 | 61.0519 | 61.0519 | 122.6852 | 123.0194 | -0.16022 | 122.9691 | 60.9512 | -0.23804 | 123.0194 | -0.16022 | 60.9512 | 122.6852 | 122.9691 | -123.1934 | -123.1888
851.7656 | 123.1155 | -60.878 | 62.0361 | -0.15663 | -0.0020208 | -0.00087594 | 0.0030612 | 0.062669 | -0.0035141 | 0.067411 | -61.0336 | 62.114 | -61.1206 | -61.1481 | 61.8118 | 0.059509 | 0.13275 | 0.17395 | 62.0636 | -61.1206 | -0.24261 | 0.07782 | -0.15564 | -0.27008 | -0.2243 | -0.24261 | 0.027466 | 0.086975 | 61.0107 | 61.0519 | 122.6898 | 122.9919 | -0.15564 | 122.9416 | 60.9375 | -0.24261 | 122.9919 | -0.15564 | 60.9375 | 122.6898 | 122.9416 | -123.1567 | -123.1567
852.7656 | 123.1155 | -60.8963 | 62.0224 | -0.072708 | -0.0045844 | -0.0045075 | 0.0034884 | 0.065873 | -0.0037277 | 0.06912 | -60.9879 | 62.1231 | -61.116 | -61.1023 | 61.8256 | 0.07782 | 0.054932 | 0.16022 | 62.0453 | -61.1298 | -0.21973 | 0.10071 | -0.091553 | -0.20599 | -0.19684 | -0.23346 | 0.022888 | 0.12817 | 60.9512 | 61.0565 | 122.7219 | 123.0194 | -0.091553 | 122.9416 | 60.9741 | -0.23346 | 123.0194 | -0.091553 | 60.9741 | 122.7219 | 122.9416 | -123.1384 | -123.1522
853.7656 | 123.111 | -60.8871 | 62.0361 | -0.04219 | -0.0041572 | -0.0049347 | 0.0045566 | 0.066727 | -0.0045821 | 0.066129 | -60.9833 | 62.0911 | -61.1069 | -61.0931 | 61.8301 | 0.07782 | 0.050354 | 0.15106 | 62.0407 | -61.1343 | -0.21973 | 0.054931 | -0.09613 | -0.20599 | -0.20599 | -0.24719 | 0.004577 | 0.1236 | 60.9375 | 61.0382 | 122.7173 | 122.9782 | -0.09613 | 122.9279 | 60.965 | -0.24719 | 122.9782 | -0.09613 | 60.965 | 122.7173 | 122.9279 | -123.143 | -123.1705
854.7656 | 123.1293 | -60.8734 | 62.0178 | -0.095596 | -0.00052559 | -0.0042937 | 0.0051974 | 0.065446 | -0.0054367 | 0.069974 | -60.9787 | 62.1231 | -61.1206 | -61.1069 | 61.821 | 0.091553 | 0.059509 | 0.17395 | 62.0728 | -61.1481 | -0.24719 | 0.10529 | -0.10529 | -0.23346 | -0.19684 | -0.27466 | 0.054932 | 0.14191 | 60.9329 | 61.0474 | 122.6944 | 122.9965 | -0.10529 | 122.9462 | 60.965 | -0.27466 | 122.9965 | -0.10529 | 60.965 | 122.6944 | 122.9462 | -123.1384 | -123.1659
855.7656 | 123.1201 | -60.8917 | 62.0087 | -0.10323 | -0.00031179 | -0.0042937 | 0.003702 | 0.064591 | -0.0022323 | 0.068693 | -61.0062 | 62.1185 | -61.0977 | -61.1206 | 61.8347 | 0.086975 | 0.064087 | 0.14191 | 62.0407 | -61.1206 | -0.20599 | 0.10986 | -0.11444 | -0.22888 | -0.17395 | -0.22888 | 0.032043 | 0.091552 | 60.9558 | 61.0336 | 122.7264 | 123.0103 | -0.11444 | 122.9324 | 60.9787 | -0.22888 | 123.0103 | -0.11444 | 60.9787 | 122.7264 | 122.9324 | -123.1064 | -123.1293
856.7656 | 123.0927 | -60.8917 | 62.0361 | -0.15663 | -0.003089 | -0.0038665 | 0.0024202 | 0.067155 | -0.0033005 | 0.068479 | -61.0199 | 62.1414 | -61.1252 | -61.1481 | 61.8301 | 0.064087 | 0.13733 | 0.15106 | 62.059 | -61.1526 | -0.23346 | 0.10529 | -0.12817 | -0.25635 | -0.20599 | -0.26092 | 0.022888 | 0.10529 | 61.0291 | 61.0428 | 122.7219 | 123.0331 | -0.12817 | 122.9507 | 60.9558 | -0.26092 | 123.0331 | -0.12817 | 60.9558 | 122.7219 | 122.9507 | -123.1613 | -123.1888
857.7656 | 123.1155 | -60.8871 | 62.0453 | -0.16426 | -0.0020208 | -0.0060027 | 0.001993 | 0.066087 | -0.00073695 | 0.068906 | -61.0336 | 62.1185 | -61.1206 | -61.1389 | 61.8256 | 0.068665 | 0.11902 | 0.15106 | 62.0636 | -61.1435 | -0.23346 | 0.073242 | -0.14648 | -0.25177 | -0.21973 | -0.25635 | 0.018311 | 0.086975 | 61.0062 | 61.0382 | 122.7127 | 123.0057 | -0.14648 | 122.9507 | 60.9558 | -0.25635 | 123.0057 | -0.14648 | 60.9558 | 122.7127 | 122.9507 | -123.1659 | -123.1888
858.7656 | 123.1338 | -60.8963 | 62.0178 | -0.072708 | -0.0041572 | -0.0036529 | 0.0022066 | 0.065446 | -0.0037277 | 0.067624 | -60.997 | 62.1277 | -61.1435 | -61.1252 | 61.8347 | 0.07782 | 0.045776 | 0.14648 | 62.0407 | -61.1206 | -0.24719 | 0.10986 | -0.10071 | -0.22888 | -0.18311 | -0.2243 | 0.022888 | 0.14648 | 60.9421 | 61.0428 | 122.731 | 123.024 | -0.10071 | 122.937 | 60.9741 | -0.2243 | 123.024 | -0.10071 | 60.9741 | 122.731 | 122.937 | -123.1613 | -123.1384
859.7812 | 123.0789 | -60.9192 | 62.0132 | 0.12566 | -0.003089 | -0.0021575 | 0.0047702 | 0.066727 | -0.0022323 | 0.068906 | -61.0336 | 62.1048 | -61.1664 | -61.1618 | 61.7844 | 0.004578 | 0.022888 | 0.059509 | 62.027 | -61.1984 | -0.24719 | 0.091552 | -0.11444 | -0.24261 | -0.22888 | -0.27924 | 0.013733 | 0.13275 | 60.9421 | 60.9787 | 122.7036 | 123.024 | -0.11444 | 122.9462 | 60.9238 | -0.27924 | 123.024 | -0.11444 | 60.9238 | 122.7036 | 122.9462 | -123.1796 | -123.2117
860.7656 | 123.1064 | -60.9146 | 62.0041 | 0.034104 | -0.0033026 | 0.0031831 | 0.0011386 | 0.06395 | -0.0037277 | 0.067838 | -61.0657 | 62.114 | -61.1481 | -61.1252 | 61.8027 | 0.059509 | 0.032043 | 0.15106 | 62.027 | -61.1893 | -0.23346 | 0.10986 | -0.15106 | -0.21057 | -0.20142 | -0.27466 | 0.022889 | 0.082397 | 60.9467 | 61.0657 | 122.7173 | 123.0286 | -0.15106 | 122.9416 | 60.9741 | -0.27466 | 123.0286 | -0.15106 | 60.9741 | 122.7173 | 122.9416 | -123.1522 | -123.1934
861.7656 | 123.111 | -60.8963 | 62.0132 | 0.0035856 | -0.0022346 | -0.0055755 | 0.0032748 | 0.066087 | -0.0028731 | 0.070188 | -61.0519 | 62.0956 | -61.1389 | -61.116 | 61.8164 | 0.036621 | 0.041199 | 0.14191 | 62.027 | -61.171 | -0.24262 | 0.082397 | -0.15564 | -0.21973 | -0.19684 | -0.27466 | 0.013733 | 0.086975 | 60.9375 | 61.0382 | 122.7127 | 122.9919 | -0.15564 | 122.9233 | 60.9329 | -0.27466 | 122.9919 | -0.15564 | 60.9329 | 122.7127 | 122.9233 | -123.1522 | -123.1842
862.7656 | 123.1201 | -60.8871 | 62.027 | -0.026932 | -0.0018072 | 0.00019226 | 0.0032748 | 0.065232 | -0.0035141 | 0.068479 | -61.0291 | 62.1231 | -61.1526 | -61.1252 | 61.8164 | 0.07782 | 0.032043 | 0.13733 | 62.027 | -61.1847 | -0.2655 | 0.09613 | -0.14191 | -0.23804 | -0.21057 | -0.29755 | 0 | 0.1236 | 60.9192 | 61.0245 | 122.7036 | 123.0103 | -0.14191 | 122.9141 | 60.965 | -0.29755 | 123.0103 | -0.14191 | 60.965 | 122.7036 | 122.9141 | -123.1796 | -123.2117
863.7656 | 123.1247 | -60.8688 | 62.027 | -0.17952 | -0.0022346 | -0.0021575 | 0.0015658 | 0.064805 | -0.0022323 | 0.066984 | -60.9924 | 62.1552 | -61.1298 | -61.116 | 61.8256 | 0.068665 | 0.073242 | 0.16479 | 62.0453 | -61.1481 | -0.26093 | 0.12817 | -0.1236 | -0.24719 | -0.20142 | -0.27924 | 0.01831 | 0.13733 | 60.9421 | 61.0336 | 122.6944 | 123.024 | -0.1236 | 122.9141 | 60.9375 | -0.27924 | 123.024 | -0.1236 | 60.9375 | 122.6944 | 122.9141 | -123.1567 | -123.175
864.7656 | 123.1155 | -60.9055 | 62.0132 | -0.095596 | -0.0033026 | -0.0053619 | 0.002634 | 0.06395 | -0.0013779 | 0.069761 | -60.9924 | 62.146 | -61.1252 | -61.1023 | 61.8347 | 0.082397 | 0.054932 | 0.15106 | 62.0499 | -61.1572 | -0.21973 | 0.13275 | -0.086975 | -0.19684 | -0.17853 | -0.25177 | 0.036621 | 0.13275 | 60.9604 | 61.0565 | 122.7402 | 123.0515 | -0.086975 | 122.9553 | 60.9879 | -0.25177 | 123.0515 | -0.086975 | 60.9879 | 122.7402 | 122.9553 | -123.1384 | -123.1705
865.7656 | 123.1155 | -60.91 | 62.0178 | 0.95726 | -0.0024482 | -0.0036529 | 0.003702 | 0.064591 | -0.0050095 | 0.068693 | -60.9512 | 62.1277 | -61.1252 | -61.1206 | 61.821 | 0.054932 | 0.027466 | 0.13733 | 62.059 | -61.1801 | -0.21515 | 0.10986 | -0.041199 | -0.21057 | -0.19684 | -0.27008 | 0.041199 | 0.17395 | 60.9375 | 61.0474 | 122.731 | 123.0377 | -0.041199 | 122.9691 | 60.965 | -0.27008 | 123.0377 | -0.041199 | 60.965 | 122.731 | 122.9691 | -123.143 | -123.1979
866.7656 | 123.0972 | -60.9238 | 62.0132 | 0.034104 | -0.0039434 | -0.0040801 | 0.004343 | 0.065659 | -0.0026595 | 0.068906 | -61.0245 | 62.1048 | -61.1481 | -61.1618 | 61.7981 | 0 | 0.036621 | 0.073242 | 62.0682 | -61.1847 | -0.2243 | 0.091552 | -0.10071 | -0.23804 | -0.21515 | -0.26093 | 0.054931 | 0.1236 | 60.9604 | 60.997 | 122.7219 | 123.0286 | -0.10071 | 122.9919 | 60.9238 | -0.26093 | 123.0286 | -0.10071 | 60.9238 | 122.7219 | 122.9919 | -123.1613 | -123.1979
867.7812 | 123.0515 | -60.9283 | 61.9812 | 0.17906 | -0.0018072 | -0.00087594 | 0.0011386 | 0.064591 | -0.0026595 | 0.06912 | -61.0977 | 62.1185 | -61.1435 | -61.2213 | 61.7249 | -0.054932 | 0.009155 | 0.018311 | 62.0544 | -61.1893 | -0.21515 | 0.13733 | -0.16937 | -0.29297 | -0.25635 | -0.26093 | 0.073242 | 0.045777 | 60.9375 | 60.9467 | 122.6532 | 123.0469 | -0.16937 | 122.9828 | 60.8734 | -0.26093 | 123.0469 | -0.16937 | 60.8734 | 122.6532 | 122.9828 | -123.1247 | -123.1705
868.7656 | 123.056 | -60.8917 | 62.027 | 0.11803 | -0.0024482 | -0.0030121 | 0.0017794 | 0.065659 | -0.0030869 | 0.068265 | -61.0291 | 62.1323 | -61.1481 | -61.1618 | 61.7706 | -0.004578 | 0.036621 | 0.054932 | 62.059 | -61.1847 | -0.25635 | 0.10529 | -0.13733 | -0.27008 | -0.25635 | -0.29297 | 0.032043 | 0.11902 | 60.9283 | 60.9467 | 122.6624 | 123.024 | -0.13733 | 122.9507 | 60.8871 | -0.29297 | 123.024 | -0.13733 | 60.8871 | 122.6624 | 122.9507 | -123.175 | -123.2117
869.7656 | 123.1155 | -60.9329 | 61.9766 | 0.27824 | -0.0026618 | -0.0021575 | 0.0017794 | 0.065659 | -0.0011643 | 0.069547 | -61.0703 | 62.1002 | -61.1618 | -61.2076 | 61.7661 | -0.022888 | -0.082397 | 0.036621 | 62.059 | -61.1893 | -0.22888 | 0.1236 | -0.13733 | -0.27466 | -0.21057 | -0.25635 | 0.082397 | 0.091553 | 60.8505 | 60.9695 | 122.699 | 123.0331 | -0.13733 | 122.9919 | 60.91 | -0.25635 | 123.0331 | -0.13733 | 60.91 | 122.699 | 122.9919 | -123.1384 | -123.1659
870.7656 | 123.1201 | -60.8963 | 62.0041 | -0.0040434 | -0.0020208 | -0.0019439 | 0.0030612 | 0.066941 | -0.0030869 | 0.06912 | -60.9833 | 62.1277 | -61.116 | -61.1023 | 61.8027 | 0.068665 | 0.018311 | 0.14648 | 62.0682 | -61.1893 | -0.21973 | 0.1236 | -0.086975 | -0.20599 | -0.20142 | -0.29297 | 0.064087 | 0.13275 | 60.9146 | 61.0428 | 122.699 | 123.024 | -0.086975 | 122.9645 | 60.965 | -0.29297 | 123.024 | -0.086975 | 60.965 | 122.699 | 122.9645 | -123.1201 | -123.1934
871.7656 | 123.1201 | -60.9055 | 61.9995 | 0.018845 | -0.0039434 | -0.0025847 | 0.0051974 | 0.066727 | 0.00054465 | 0.069547 | -60.9924 | 62.1094 | -61.1435 | -61.171 | 61.8073 | 0.064087 | 0.041199 | 0.17853 | 62.0728 | -61.1801 | -0.23804 | 0.10986 | -0.086975 | -0.2655 | -0.19226 | -0.27466 | 0.073242 | 0.15106 | 60.9467 | 61.084 | 122.7127 | 123.0148 | -0.086975 | 122.9782 | 60.9695 | -0.27466 | 123.0148 | -0.086975 | 60.9695 | 122.7127 | 122.9782 | -123.143 | -123.1796
872.7656 | 123.0972 | -60.9192 | 62.0132 | 0.049362 | -0.0039434 | -0.00066214 | 0.0047702 | 0.067155 | -0.0043685 | 0.068052 | -61.0016 | 62.1323 | -61.1389 | -61.1526 | 61.7706 | 0.004578 | 0.018311 | 0.10071 | 62.0636 | -61.171 | -0.21973 | 0.11902 | -0.082398 | -0.23346 | -0.24262 | -0.25177 | 0.050354 | 0.13733 | 60.9375 | 61.0199 | 122.6898 | 123.0515 | -0.082398 | 122.9828 | 60.9238 | -0.25177 | 123.0515 | -0.082398 | 60.9238 | 122.6898 | 122.9828 | -123.1522 | -123.1842
873.7656 | 123.0652 | -60.9283 | 62.0041 | 0.1104 | -0.0026618 | -0.0070709 | 0.0045566 | 0.066514 | -0.0018051 | 0.071683 | -61.0794 | 62.1185 | -61.1755 | -61.203 | 61.7203 | -0.045776 | 0.045776 | 0.004578 | 62.0544 | -61.203 | -0.24719 | 0.11444 | -0.15106 | -0.27466 | -0.28381 | -0.27466 | 0.050354 | 0.09613 | 60.9741 | 60.9329 | 122.6486 | 123.0469 | -0.15106 | 122.9828 | 60.8826 | -0.27466 | 123.0469 | -0.15106 | 60.8826 | 122.6486 | 122.9828 | -123.1796 | -123.2071
874.7656 | 123.0377 | -60.9329 | 61.9995 | 0.14854 | -0.0035162 | -0.0017303 | 0.0049838 | 0.067368 | -0.0020187 | 0.069333 | -61.0748 | 62.1414 | -61.1526 | -61.2259 | 61.7249 | -0.059509 | 0.050354 | 0.018311 | 62.0499 | -61.2213 | -0.21973 | 0.14191 | -0.14191 | -0.29297 | -0.27466 | -0.28839 | 0.050354 | 0.07782 | 60.9833 | 60.9512 | 122.6578 | 123.0743 | -0.14191 | 122.9828 | 60.8734 | -0.28839 | 123.0743 | -0.14191 | 60.8734 | 122.6578 | 122.9828 | -123.1522 | -123.2208
875.7656 | 123.0743 | -60.9375 | 62.0178 | 0.12566 | -0.0033026 | -0.0053619 | 0.004343 | 0.066514 | -0.0043685 | 0.068479 | -61.0474 | 62.114 | -61.171 | -61.1938 | 61.7386 | -0.045776 | 0.018311 | 0.018311 | 62.0728 | -61.1984 | -0.23346 | 0.096131 | -0.10986 | -0.25635 | -0.27924 | -0.26093 | 0.054932 | 0.1236 | 60.9558 | 60.9558 | 122.6761 | 123.0515 | -0.10986 | 123.0103 | 60.8917 | -0.26093 | 123.0515 | -0.10986 | 60.8917 | 122.6761 | 123.0103 | -123.1888 | -123.2162
876.7656 | 123.0515 | -60.91 | 61.9995 | 0.13329 | -0.0022346 | -0.0085663 | 0.0041292 | 0.066514 | -0.0024459 | 0.069333 | -61.0565 | 62.1323 | -61.1526 | -61.1984 | 61.7432 | -0.054932 | 0.041199 | 0.018311 | 62.0499 | -61.2122 | -0.24261 | 0.13275 | -0.14648 | -0.28839 | -0.25635 | -0.30212 | 0.050354 | 0.09613 | 60.9512 | 60.9283 | 122.6532 | 123.0423 | -0.14648 | 122.9599 | 60.8551 | -0.30212 | 123.0423 | -0.14648 | 60.8551 | 122.6532 | 122.9599 | -123.1522 | -123.2117
877.7656 | 123.0881 | -60.91 | 62.0224 | 0.018845 | -0.0035162 | -0.0036529 | 0.004343 | 0.067582 | -0.0045821 | 0.06912 | -61.0016 | 62.1323 | -61.1298 | -61.1526 | 61.7798 | 0.022888 | 0.013733 | 0.07782 | 62.0682 | -61.1938 | -0.21973 | 0.10986 | -0.091553 | -0.24261 | -0.24262 | -0.28381 | 0.045776 | 0.12817 | 60.9238 | 60.9879 | 122.6898 | 123.0423 | -0.091553 | 122.9782 | 60.9329 | -0.28381 | 123.0423 | -0.091553 | 60.9329 | 122.6898 | 122.9782 | -123.1522 | -123.2162
878.7656 | 123.0743 | -60.91 | 62.027 | 0.011215 | -0.0018072 | -0.00087594 | 0.004343 | 0.067155 | -0.0030869 | 0.067838 | -60.997 | 62.1094 | -61.1252 | -61.1526 | 61.7935 | 0.018311 | 0.027466 | 0.07782 | 62.059 | -61.1801 | -0.21515 | 0.082397 | -0.086975 | -0.24261 | -0.23346 | -0.27008 | 0.032043 | 0.12817 | 60.9375 | 60.9879 | 122.7036 | 123.0194 | -0.086975 | 122.9691 | 60.9283 | -0.27008 | 123.0194 | -0.086975 | 60.9283 | 122.7036 | 122.9691 | -123.1522 | -123.2071
879.7656 | 123.0698 | -60.9009 | 62.0132 | 0.17143 | -0.0024482 | -0.0038665 | 0.0039156 | 0.067155 | -0.0026595 | 0.070615 | -61.0611 | 62.1277 | -61.1435 | -61.203 | 61.7569 | -0.045776 | 0.036621 | 0 | 62.0682 | -61.1893 | -0.24261 | 0.11444 | -0.16022 | -0.30212 | -0.25635 | -0.28839 | 0.054931 | 0.082398 | 60.9375 | 60.9009 | 122.6578 | 123.0286 | -0.16022 | 122.9691 | 60.8551 | -0.28839 | 123.0286 | -0.16022 | 60.8551 | 122.6578 | 122.9691 | -123.1567 | -123.2025
880.7656 | 123.0835 | -60.9055 | 62.0316 | 0.20958 | -0.0026618 | -0.0021575 | 0.0045566 | 0.065659 | -0.0047957 | 0.070402 | -61.0657 | 62.1002 | -61.1572 | -61.2396 | 61.496 | -0.29755 | 0.21515 | 0.14191 | 62.0544 | -61.203 | -0.25177 | 0.068665 | -0.16022 | -0.33417 | -0.53558 | -0.29755 | 0.022888 | 0.091553 | 61.1206 | 61.0474 | 122.4014 | 123.0057 | -0.16022 | 122.9599 | 60.6079 | -0.29755 | 123.0057 | -0.16022 | 60.6079 | 122.4014 | 122.9599 | -123.1888 | -123.2346
881.7656 | 123.1247 | -60.9283 | 62.0224 | 0.20195 | -0.0022346 | -0.0036529 | 0.0013522 | 0.066727 | -0.0015915 | 0.069547 | -61.084 | 62.1048 | -61.1755 | -61.203 | 61.7386 | -0.26093 | -0.059509 | 0.21057 | 62.0224 | -61.2213 | -0.24719 | 0.082397 | -0.15564 | -0.27466 | -0.28381 | -0.29297 | 0 | 0.091553 | 60.8688 | 61.1389 | 122.6669 | 123.0331 | -0.15564 | 122.9507 | 60.6674 | -0.29297 | 123.0331 | -0.15564 | 60.6674 | 122.6669 | 122.9507 | -123.1979 | -123.2437
882.7656 | 123.0423 | -60.9283 | 62.0132 | 0.21721 | -0.0035162 | -0.0060027 | 0.0032748 | 0.065659 | -0.0024459 | 0.068265 | -61.0748 | 62.114 | -61.171 | -61.2625 | 61.4319 | -0.32044 | 0.22888 | 0.045776 | 62.0407 | -61.1938 | -0.24261 | 0.10071 | -0.14648 | -0.33417 | -0.58136 | -0.2655 | 0.027465 | 0.09613 | 61.1572 | 60.9741 | 122.3602 | 123.0423 | -0.14648 | 122.9691 | 60.6079 | -0.2655 | 123.0423 | -0.14648 | 60.6079 | 122.3602 | 122.9691 | -123.1842 | -123.2071
883.7656 | 123.0606 | -60.9146 | 62.0178 | 0.26299 | -0.0035162 | -0.0057891 | 0.0051974 | 0.0663 | -0.0020187 | 0.068479 | -61.0703 | 62.0956 | -61.1572 | -61.4227 | 61.4914 | -0.10986 | 0.15564 | 0.050354 | 62.0819 | -61.1755 | -0.24262 | 0.07782 | -0.15564 | -0.50812 | -0.52643 | -0.26093 | 0.064087 | 0.086976 | 61.0703 | 60.965 | 122.406 | 123.0103 | -0.15564 | 122.9965 | 60.8047 | -0.26093 | 123.0103 | -0.15564 | 60.8047 | 122.406 | 122.9965 | -123.175 | -123.1934
884.7656 | 123.0515 | -60.91 | 62.0224 | 0.14092 | -0.0018072 | -0.0047211 | 0.0017794 | 0.066514 | -0.0041549 | 0.06912 | -61.0657 | 62.1368 | -61.1389 | -61.2076 | 61.7203 | -0.041199 | 0.050354 | 0.027466 | 62.0819 | -61.203 | -0.22888 | 0.11444 | -0.15564 | -0.29755 | -0.30212 | -0.29297 | 0.059509 | 0.073242 | 60.9604 | 60.9375 | 122.6303 | 123.0469 | -0.15564 | 122.9919 | 60.8688 | -0.29297 | 123.0469 | -0.15564 | 60.8688 | 122.6303 | 122.9919 | -123.1613 | -123.2254
885.7656 | 123.0377 | -60.9283 | 62.0041 | 0.1638 | -0.00138 | -0.0077117 | 0.0032748 | 0.065873 | -0.0045821 | 0.068693 | -61.0657 | 62.1368 | -61.1481 | -61.1984 | 61.7203 | -0.054932 | 0.036621 | 0.013733 | 62.0636 | -61.2076 | -0.21973 | 0.13275 | -0.13733 | -0.27008 | -0.28381 | -0.27924 | 0.05951 | 0.082397 | 60.965 | 60.9421 | 122.6486 | 123.0652 | -0.13733 | 122.9919 | 60.8734 | -0.27924 | 123.0652 | -0.13733 | 60.8734 | 122.6486 | 122.9919 | -123.1522 | -123.2117
886.7656 | 123.0743 | -60.9009 | 62.0132 | 0.22484 | -0.0020208 | -0.00044854 | 0.0022066 | 0.066941 | -0.0035141 | 0.070188 | -60.965 | 62.1094 | -61.1664 | -61.2076 | 61.734 | -0.013733 | 0.009155 | 0.022888 | 62.0682 | -61.1984 | -0.2655 | 0.09613 | -0.064087 | -0.3067 | -0.27924 | -0.29755 | 0.054931 | 0.20142 | 60.91 | 60.9238 | 122.6349 | 123.0103 | -0.064087 | 122.9691 | 60.8871 | -0.29755 | 123.0103 | -0.064087 | 60.8871 | 122.6349 | 122.9691 | -123.1796 | -123.2117
887.7656 | 123.1613 | -60.91 | 61.9812 | 0.27824 | -0.005866 | -0.00044854 | -0.00035676 | 0.064805 | -0.0022323 | 0.070188 | -61.0428 | 62.0773 | -61.1618 | -61.1572 | 61.7844 | -0.013733 | -0.11902 | 0.064087 | 62.027 | -61.171 | -0.25177 | 0.096131 | -0.13275 | -0.24719 | -0.19684 | -0.26093 | 0.045777 | 0.11902 | 60.791 | 60.9741 | 122.6944 | 122.9874 | -0.13275 | 122.937 | 60.8963 | -0.26093 | 122.9874 | -0.13275 | 60.8963 | 122.6944 | 122.937 | -123.143 | -123.1522
888.7656 | 123.1613 | -60.878 | 61.9995 | 0.26299 | -0.0024482 | -0.0047211 | 0.0011386 | 0.065446 | -0.0024459 | 0.068693 | -61.0474 | 62.0682 | -61.1481 | -61.1526 | 61.8073 | 0 | -0.1236 | 0.07782 | 62.0178 | -61.1572 | -0.27008 | 0.068664 | -0.16937 | -0.27466 | -0.19226 | -0.27924 | 0.01831 | 0.10071 | 60.7544 | 60.9558 | 122.6852 | 122.9462 | -0.16937 | 122.8958 | 60.878 | -0.27924 | 122.9462 | -0.16937 | 60.878 | 122.6852 | 122.8958 | -123.1476 | -123.1567
889.7656 | 123.1796 | -60.9009 | 61.972 | 0.25536 | -0.0037298 | -0.0045075 | 0.0030612 | 0.065446 | -0.0024459 | 0.068906 | -61.0336 | 62.0544 | -61.1343 | -61.1389 | 61.821 | 0.018311 | -0.13275 | 0.09613 | 62.0316 | -61.1572 | -0.23346 | 0.082397 | -0.13275 | -0.23804 | -0.15106 | -0.25635 | 0.059509 | 0.10071 | 60.7681 | 60.997 | 122.7219 | 122.9553 | -0.13275 | 122.9324 | 60.9192 | -0.25635 | 122.9553 | -0.13275 | 60.9192 | 122.7219 | 122.9324 | -123.1064 | -123.1293
890.7656 | 123.1888 | -60.8871 | 61.9675 | 0.23247 | -0.003089 | 0.0014741 | 0.0024202 | 0.065232 | -0.0033005 | 0.068906 | -61.0153 | 62.0316 | -61.1389 | -61.0977 | 61.8073 | -0.018311 | -0.14191 | 0.12817 | 62.0316 | -61.1389 | -0.25177 | 0.064087 | -0.12817 | -0.21057 | -0.16022 | -0.25177 | 0.064087 | 0.1236 | 60.7452 | 61.0153 | 122.6944 | 122.9187 | -0.12817 | 122.9187 | 60.8688 | -0.25177 | 122.9187 | -0.12817 | 60.8688 | 122.6944 | 122.9187 | -123.1064 | -123.1064
891.7656 | 123.1155 | -60.9421 | 61.9995 | 0.20958 | -0.0018072 | -0.0042937 | 0.001993 | 0.064805 | -0.0037277 | 0.069547 | -61.0748 | 62.0773 | -61.1618 | -61.1755 | 61.7569 | -0.041199 | -0.07782 | 0.036621 | 62.027 | -61.1801 | -0.21973 | 0.07782 | -0.13275 | -0.23346 | -0.24262 | -0.23804 | 0.027466 | 0.086975 | 60.8643 | 60.9787 | 122.699 | 123.0194 | -0.13275 | 122.9691 | 60.9009 | -0.23804 | 123.0194 | -0.13275 | 60.9009 | 122.699 | 122.9691 | -123.1613 | -123.1796
892.7812 | 123.1979 | -60.878 | 62.0087 | 0.018845 | -0.004798 | -0.0057891 | -0.0048428 | 0.063523 | -0.0033005 | 0.069547 | -61.0245 | 62.0178 | -61.1389 | -61.0657 | 61.8759 | 0.12817 | -0.07782 | 0.21973 | 62.0316 | -61.1069 | -0.26093 | 0.009155 | -0.14648 | -0.18768 | -0.13275 | -0.22888 | 0.022888 | 0.11444 | 60.8002 | 61.0977 | 122.7539 | 122.8958 | -0.14648 | 122.9095 | 61.0062 | -0.22888 | 122.8958 | -0.14648 | 61.0062 | 122.7539 | 122.9095 | -123.1476 | -123.1155
893.7656 | 123.1842 | -60.8734 | 61.972 | 0.27824 | -0.0045844 | -0.0053619 | 0.0030612 | 0.062669 | -0.0024459 | 0.068693 | -60.9787 | 62.0544 | -61.1481 | -61.1114 | 61.8347 | 0.036621 | -0.21057 | 0.11902 | 61.9904 | -61.1481 | -0.27466 | 0.082397 | -0.10529 | -0.23804 | -0.13733 | -0.27466 | 0.01831 | 0.16937 | 60.6628 | 60.9924 | 122.7081 | 122.9279 | -0.10529 | 122.8638 | 60.91 | -0.27466 | 122.9279 | -0.10529 | 60.91 | 122.7081 | 122.8638 | -123.1201 | -123.1201
894.7656 | 123.1934 | -60.8917 | 61.9766 | 0.20958 | -0.0045844 | -0.0036529 | 0.00092504 | 0.063096 | -0.0052231 | 0.067411 | -61.0107 | 62.0178 | -61.1252 | -61.1069 | 61.8256 | 0.032043 | -0.16022 | 0.13275 | 61.9812 | -61.1664 | -0.23346 | 0.041198 | -0.11902 | -0.21515 | -0.15106 | -0.27466 | 0.004577 | 0.11444 | 60.7315 | 61.0245 | 122.7173 | 122.9095 | -0.11902 | 122.8729 | 60.9238 | -0.27466 | 122.9095 | -0.11902 | 60.9238 | 122.7173 | 122.8729 | -123.1018 | -123.143
895.7656 | 123.1934 | -60.8917 | 61.9812 | 0.26299 | -0.004798 | -0.0032257 | 0.0017794 | 0.061387 | -0.0020187 | 0.068265 | -60.9924 | 62.0041 | -61.1389 | -61.1023 | 61.8393 | 0.045776 | -0.19226 | 0.1236 | 61.9812 | -61.1389 | -0.24719 | 0.022888 | -0.10071 | -0.21057 | -0.14191 | -0.24719 | 0 | 0.14648 | 60.6995 | 61.0153 | 122.731 | 122.8958 | -0.10071 | 122.8729 | 60.9375 | -0.24719 | 122.8958 | -0.10071 | 60.9375 | 122.731 | 122.8729 | -123.1201 | -123.1201
896.7656 | 123.175 | -60.8643 | 61.9812 | 0.20958 | -0.0041572 | -0.0021575 | 7.0444e-05 | 0.060532 | -0.0037277 | 0.069761 | -61.0016 | 61.9995 | -61.1206 | -61.1114 | 61.8164 | 0.036621 | -0.16479 | 0.13275 | 61.972 | -61.1664 | -0.25635 | 0.018311 | -0.13733 | -0.24719 | -0.16479 | -0.30212 | -0.009155 | 0.11902 | 60.6995 | 60.997 | 122.6807 | 122.8638 | -0.13733 | 122.8363 | 60.9009 | -0.30212 | 122.8638 | -0.13733 | 60.9009 | 122.6807 | 122.8363 | -123.1018 | -123.1476
897.7812 | 123.0927 | -60.8963 | 62.0407 | -0.21004 | -0.004798 | -0.0066437 | 0.0041292 | 0.060319 | -0.0045821 | 0.06677 | -61.0199 | 62.0911 | -61.1206 | -61.1298 | 61.7798 | 0.045776 | 0.1236 | 0.14191 | 62.0865 | -61.1343 | -0.2243 | 0.050354 | -0.1236 | -0.23346 | -0.26093 | -0.23804 | 0.045777 | 0.10071 | 61.0199 | 61.0382 | 122.6761 | 122.9874 | -0.1236 | 122.9828 | 60.9421 | -0.23804 | 122.9874 | -0.1236 | 60.9421 | 122.6761 | 122.9828 | -123.1613 | -123.175
898.7656 | 123.1934 | -60.8414 | 62.0041 | 0.25536 | -0.003089 | -0.0066437 | 0.0047702 | 0.064164 | -0.0047957 | 0.068265 | -60.9924 | 61.9904 | -61.116 | -61.0199 | 61.8759 | 0.059509 | -0.17395 | 0.14648 | 62.0087 | -61.1069 | -0.27466 | -0.013733 | -0.15106 | -0.17853 | -0.12817 | -0.2655 | 0.004578 | 0.1236 | 60.6674 | 60.9879 | 122.7173 | 122.8317 | -0.15106 | 122.85 | 60.9009 | -0.2655 | 122.8317 | -0.15106 | 60.9009 | 122.7173 | 122.85 | -123.1201 | -123.111
899.7656 | 123.1522 | -60.8826 | 61.9675 | 0.22484 | -0.0056524 | -0.0051483 | 0.0011386 | 0.061387 | -0.0039413 | 0.068265 | -61.0153 | 61.972 | -61.116 | -61.1252 | 61.8164 | 0.009155 | -0.14191 | 0.11444 | 62.0087 | -61.1481 | -0.23346 | 0.004578 | -0.13275 | -0.24262 | -0.15106 | -0.2655 | 0.041199 | 0.10071 | 60.7407 | 60.997 | 122.699 | 122.8546 | -0.13275 | 122.8912 | 60.8917 | -0.2655 | 122.8546 | -0.13275 | 60.8917 | 122.699 | 122.8912 | -123.0835 | -123.1155
900.7656 | 123.1476 | -60.8871 | 61.9904 | 0.20958 | -0.0033026 | -0.0064301 | 0.0017794 | 0.062241 | -0.0033005 | 0.068052 | -61.0153 | 61.9858 | -61.1252 | -61.1298 | 61.8301 | 0.036621 | -0.15564 | 0.1236 | 61.9812 | -61.1343 | -0.23804 | -0.004577 | -0.12817 | -0.24262 | -0.16022 | -0.24719 | -0.009155 | 0.10986 | 60.7315 | 61.0107 | 122.7173 | 122.8729 | -0.12817 | 122.8683 | 60.9238 | -0.24719 | 122.8729 | -0.12817 | 60.9238 | 122.7173 | 122.8683 | -123.1155 | -123.1247
901.7656 | 123.1384 | -60.878 | 62.0041 | 0.12566 | -0.0056524 | -0.0062163 | 0.00028404 | 0.061814 | -0.0024459 | 0.071042 | -61.0474 | 61.9949 | -61.1206 | -61.1343 | 61.8301 | 0.009155 | -0.091553 | 0.10071 | 62.0041 | -61.1298 | -0.24261 | -0.009155 | -0.16937 | -0.25635 | -0.17395 | -0.25177 | 0 | 0.073242 | 60.7864 | 60.9787 | 122.7081 | 122.8729 | -0.16937 | 122.8821 | 60.8871 | -0.25177 | 122.8729 | -0.16937 | 60.8871 | 122.7081 | 122.8821 | -123.1247 | -123.1338
902.7812 | 123.0743 | -60.9055 | 62.0544 | -0.17189 | -0.0039434 | -0.0038665 | 0.002634 | 0.06096 | -0.0033005 | 0.06912 | -61.0519 | 62.0865 | -61.1023 | -61.203 | 61.7386 | 0.036621 | 0.10986 | 0.12817 | 62.0453 | -61.1664 | -0.19684 | 0.032044 | -0.14648 | -0.29755 | -0.31586 | -0.26093 | -0.009155 | 0.050354 | 61.0153 | 61.0336 | 122.644 | 122.9919 | -0.14648 | 122.9507 | 60.9421 | -0.26093 | 122.9919 | -0.14648 | 60.9421 | 122.644 | 122.9507 | -123.1567 | -123.2208
903.7656 | 123.1476 | -60.8871 | 62.0087 | 0.1104 | -0.0077888 | -0.0074981 | 0.00028404 | 0.060532 | -0.0041549 | 0.069974 | -61.0519 | 62.0041 | -61.1206 | -61.1389 | 61.8118 | 0.022888 | -0.07782 | 0.10529 | 61.9949 | -61.1114 | -0.23346 | -0.004578 | -0.16479 | -0.25177 | -0.19684 | -0.2243 | -0.013733 | 0.068664 | 60.8093 | 60.9924 | 122.699 | 122.8912 | -0.16479 | 122.8821 | 60.91 | -0.2243 | 122.8912 | -0.16479 | 60.91 | 122.699 | 122.8821 | -123.1293 | -123.1201
904.7656 | 123.1293 | -60.8551 | 62.0087 | 0.14854 | -0.0062934 | -0.0070709 | -0.00035676 | 0.059891 | -0.0026595 | 0.067838 | -61.0657 | 61.9904 | -61.1069 | -61.1343 | 61.821 | 0.018311 | -0.068665 | 0.1236 | 61.9904 | -61.1252 | -0.25177 | -0.018311 | -0.21057 | -0.27923 | -0.18768 | -0.27008 | -0.018311 | 0.041199 | 60.7864 | 60.9787 | 122.6761 | 122.8455 | -0.21057 | 122.8455 | 60.8734 | -0.27008 | 122.8455 | -0.21057 | 60.8734 | 122.6761 | 122.8455 | -123.1155 | -123.1338
905.7656 | 123.1293 | -60.8917 | 61.9904 | 0.21721 | -0.0069342 | -0.0027985 | 0.00028404 | 0.060746 | -0.0028731 | 0.069974 | -61.0382 | 61.9949 | -61.1252 | -61.1252 | 61.821 | 0.027466 | -0.13275 | 0.1236 | 61.9675 | -61.1069 | -0.23346 | 0.004578 | -0.14648 | -0.23346 | -0.16937 | -0.21515 | -0.022888 | 0.086975 | 60.759 | 61.0153 | 122.7127 | 122.8867 | -0.14648 | 122.8592 | 60.9192 | -0.21515 | 122.8867 | -0.14648 | 60.9192 | 122.7127 | 122.8592 | -123.1155 | -123.0972
906.7656 | 123.1201 | -60.878 | 62.0361 | 0.14854 | -0.0062934 | -0.0074981 | 0.00028404 | 0.05861 | -0.0026595 | 0.068693 | -61.0382 | 61.9949 | -61.1252 | -61.1343 | 61.8164 | 0.022888 | -0.073242 | 0.12817 | 61.9858 | -61.1069 | -0.24719 | -0.041199 | -0.16022 | -0.25635 | -0.21973 | -0.22888 | -0.050354 | 0.086975 | 60.8047 | 61.0062 | 122.6944 | 122.8729 | -0.16022 | 122.8638 | 60.9009 | -0.22888 | 122.8729 | -0.16022 | 60.9009 | 122.6944 | 122.8638 | -123.1613 | -123.143
907.7656 | 123.1659 | -60.878 | 61.9812 | 0.034104 | -0.0069342 | -0.0096343 | 0.002634 | 0.0616 | -0.0033005 | 0.067197 | -61.0336 | 62.0178 | -61.1298 | -61.1023 | 61.8393 | 0.064087 | -0.068665 | 0.17853 | 62.0224 | -61.1114 | -0.25177 | 0.036621 | -0.15564 | -0.2243 | -0.14191 | -0.23346 | 0.041199 | 0.096131 | 60.8093 | 61.0565 | 122.7173 | 122.8958 | -0.15564 | 122.9004 | 60.9421 | -0.23346 | 122.8958 | -0.15564 | 60.9421 | 122.7173 | 122.9004 | -123.111 | -123.0927
908.7656 | 123.175 | -60.8826 | 61.9995 | 0.026474 | -0.0054388 | -0.0081389 | -0.00099756 | 0.060319 | -0.0062911 | 0.06677 | -61.0382 | 61.9766 | -61.1206 | -61.0931 | 61.8301 | 0.059509 | -0.07782 | 0.16022 | 62.0041 | -61.0977 | -0.23804 | -0.022888 | -0.15564 | -0.21057 | -0.16937 | -0.21515 | 0.004577 | 0.082397 | 60.8047 | 61.0428 | 122.7127 | 122.8592 | -0.15564 | 122.8867 | 60.9421 | -0.21515 | 122.8592 | -0.15564 | 60.9421 | 122.7127 | 122.8867 | -123.1201 | -123.0972
909.7656 | 123.1979 | -60.878 | 61.9949 | 0.064621 | -0.0060798 | -0.0049347 | 0.00049764 | 0.062882 | -0.0050095 | 0.068052 | -61.0199 | 61.972 | -61.1252 | -61.0977 | 61.8393 | 0.054932 | -0.073242 | 0.16937 | 62.0316 | -61.084 | -0.24719 | -0.022888 | -0.14191 | -0.21973 | -0.15564 | -0.20599 | 0.036621 | 0.10529 | 60.8047 | 61.0474 | 122.7173 | 122.85 | -0.14191 | 122.9095 | 60.9329 | -0.20599 | 122.85 | -0.14191 | 60.9329 | 122.7173 | 122.9095 | -123.1201 | -123.0789
910.7656 | 123.1613 | -60.8826 | 62.0132 | 0.034104 | -0.0062934 | -0.0057891 | 0.0017794 | 0.060105 | -9.6146e-05 | 0.068479 | -61.0336 | 61.9858 | -61.116 | -61.1069 | 61.853 | 0.054932 | -0.068665 | 0.17395 | 61.9995 | -61.1069 | -0.23346 | -0.027466 | -0.15106 | -0.22431 | -0.16022 | -0.22431 | -0.013733 | 0.082398 | 60.8139 | 61.0565 | 122.7356 | 122.8683 | -0.15106 | 122.8821 | 60.9375 | -0.22431 | 122.8683 | -0.15106 | 60.9375 | 122.7356 | 122.8821 | -123.1293 | -123.1201
911.7656 | 123.1522 | -60.8917 | 61.9904 | 0.056992 | -0.0060798 | -0.0042937 | -0.0012112 | 0.062455 | -0.0047957 | 0.066984 | -61.0382 | 61.9858 | -61.1298 | -61.1252 | 61.8164 | 0.027466 | -0.082397 | 0.1236 | 61.9995 | -61.1023 | -0.23804 | -0.004577 | -0.14648 | -0.23346 | -0.17395 | -0.21057 | 0.009156 | 0.091553 | 60.8093 | 61.0153 | 122.7081 | 122.8775 | -0.14648 | 122.8912 | 60.9192 | -0.21057 | 122.8775 | -0.14648 | 60.9192 | 122.7081 | 122.8912 | -123.1201 | -123.0927
912.7656 | 123.1522 | -60.8734 | 61.972 | 0.14092 | -0.0062934 | -0.0079253 | 0.0013522 | 0.061173 | -0.0052231 | 0.066984 | -61.0519 | 61.9904 | -61.1298 | -61.116 | 61.8073 | 0.027466 | -0.082397 | 0.11902 | 61.9812 | -61.1114 | -0.25635 | 0.01831 | -0.17853 | -0.24262 | -0.16479 | -0.23804 | 0.009155 | 0.07782 | 60.791 | 60.9924 | 122.6807 | 122.8638 | -0.17853 | 122.8546 | 60.9009 | -0.23804 | 122.8638 | -0.17853 | 60.9009 | 122.6807 | 122.8546 | -123.1018 | -123.0835
913.7656 | 123.1979 | -60.8505 | 62.0087 | 0.072251 | -0.0069342 | -0.0066437 | 0.0024202 | 0.059891 | -0.0056503 | 0.068265 | -61.0291 | 61.9812 | -61.1114 | -61.0931 | 61.8347 | 0.059509 | -0.064087 | 0.15564 | 62.0178 | -61.0977 | -0.26093 | -0.027466 | -0.17853 | -0.24262 | -0.17395 | -0.24719 | 0.009155 | 0.082397 | 60.7864 | 61.0062 | 122.6852 | 122.8317 | -0.17853 | 122.8683 | 60.91 | -0.24719 | 122.8317 | -0.17853 | 60.91 | 122.6852 | 122.8683 | -123.1201 | -123.1064
914.7656 | 123.2025 | -60.8414 | 61.9812 | -0.0040434 | -0.0037298 | -0.0045075 | 0.0024202 | 0.058823 | -0.0028731 | 0.069333 | -60.9879 | 61.9995 | -61.1206 | -61.0245 | 61.8759 | 0.11444 | -0.07782 | 0.24719 | 61.9858 | -61.0931 | -0.27923 | 0.018311 | -0.14648 | -0.18311 | -0.10529 | -0.25177 | 0.004578 | 0.13275 | 60.7635 | 61.0886 | 122.7173 | 122.8409 | -0.14648 | 122.8271 | 60.9558 | -0.25177 | 122.8409 | -0.14648 | 60.9558 | 122.7173 | 122.8271 | -123.1018 | -123.0743
915.7656 | 123.2025 | -60.8734 | 62.0041 | -0.034561 | -0.0067206 | -0.0098479 | 0.00028404 | 0.059251 | -0.0033005 | 0.069547 | -60.9924 | 62.0132 | -61.116 | -61.0428 | 61.8851 | 0.11902 | -0.082397 | 0.23346 | 61.9766 | -61.0886 | -0.24262 | 0.009156 | -0.11902 | -0.16937 | -0.11902 | -0.21515 | -0.027465 | 0.1236 | 60.791 | 61.1069 | 122.7585 | 122.8867 | -0.11902 | 122.85 | 60.9924 | -0.21515 | 122.8867 | -0.11902 | 60.9924 | 122.7585 | 122.85 | -123.1201 | -123.0927
916.7656 | 123.2071 | -60.8505 | 61.9858 | 0.026474 | -0.007575 | -0.010275 | 0.00028404 | 0.059891 | -0.0058639 | 0.067624 | -61.0016 | 61.9812 | -61.1114 | -61.0565 | 61.9034 | 0.11902 | -0.10071 | 0.21973 | 61.9446 | -61.1023 | -0.26093 | -0.004578 | -0.15106 | -0.20599 | -0.082398 | -0.25177 | -0.041199 | 0.10986 | 60.7498 | 61.0703 | 122.7539 | 122.8317 | -0.15106 | 122.7951 | 60.9695 | -0.25177 | 122.8317 | -0.15106 | 60.9695 | 122.7539 | 122.7951 | -123.0972 | -123.0881
917.7656 | 123.2117 | -60.8688 | 61.9995 | -0.011673 | -0.004798 | -0.0098479 | 0.00092504 | 0.061814 | -0.0037277 | 0.068265 | -61.0107 | 61.9904 | -61.1069 | -61.0336 | 61.8713 | 0.1236 | -0.082397 | 0.23346 | 62.0041 | -61.0611 | -0.23804 | -0.009156 | -0.14191 | -0.1648 | -0.12817 | -0.19226 | 0.004577 | 0.096131 | 60.7864 | 61.1023 | 122.7402 | 122.8592 | -0.14191 | 122.8729 | 60.9924 | -0.19226 | 122.8592 | -0.14191 | 60.9924 | 122.7402 | 122.8729 | -123.1064 | -123.0606
918.7656 | 123.1705 | -60.878 | 61.9995 | -0.095596 | -0.0067206 | -0.0051483 | 0.00071144 | 0.06096 | -0.0056503 | 0.06912 | -61.0611 | 61.9949 | -61.1343 | -61.1114 | 61.8439 | 0.050354 | -0.068665 | 0.15106 | 61.9995 | -61.0748 | -0.25635 | -0.004578 | -0.1831 | -0.23346 | -0.15564 | -0.19684 | 0 | 0.073242 | 60.8093 | 61.0291 | 122.7219 | 122.8729 | -0.1831 | 122.8775 | 60.9283 | -0.19684 | 122.8729 | -0.1831 | 60.9283 | 122.7219 | 122.8775 | -123.1338 | -123.0743
919.7656 | 123.175 | -60.9055 | 61.9904 | 0.24773 | -0.005866 | -0.0053619 | 0.00092504 | 0.0616 | -0.0026595 | 0.067624 | -61.0153 | 62.0087 | -61.0931 | -61.1069 | 61.821 | 0.050354 | -0.068665 | 0.13733 | 62.0224 | -61.0611 | -0.18768 | 0.018311 | -0.10986 | -0.20142 | -0.16937 | -0.15564 | 0.032044 | 0.07782 | 60.8368 | 61.0428 | 122.7264 | 122.9141 | -0.10986 | 122.9279 | 60.9558 | -0.15564 | 122.9141 | -0.10986 | 60.9558 | 122.7264 | 122.9279 | -123.0835 | -123.0515
920.7656 | 123.2025 | -60.8734 | 62.0087 | 0.011215 | -0.0071478 | -0.0085663 | -0.00057036 | 0.059678 | -0.0026595 | 0.067624 | -61.0107 | 62.0407 | -61.0886 | -61.0519 | 61.8713 | 0.10986 | -0.091553 | 0.21515 | 61.9858 | -61.0748 | -0.21515 | 0.032043 | -0.13733 | -0.17853 | -0.13733 | -0.20142 | -0.022888 | 0.07782 | 60.7819 | 61.0886 | 122.7448 | 122.9141 | -0.13733 | 122.8592 | 60.9833 | -0.20142 | 122.9141 | -0.13733 | 60.9833 | 122.7448 | 122.8592 | -123.0972 | -123.0835
921.7656 | 123.2025 | -60.8368 | 62.0224 | -0.080337 | -0.0052252 | -0.0087799 | 0.0013522 | 0.061173 | -0.0033005 | 0.068693 | -60.9512 | 61.9995 | -61.1023 | -60.997 | 61.9034 | 0.16937 | -0.054932 | 0.25635 | 61.9812 | -61.0794 | -0.2655 | -0.022888 | -0.11444 | -0.16022 | -0.11902 | -0.24262 | -0.041199 | 0.15106 | 60.7819 | 61.0931 | 122.7402 | 122.8363 | -0.11444 | 122.818 | 61.0062 | -0.24262 | 122.8363 | -0.11444 | 61.0062 | 122.7402 | 122.818 | -123.1247 | -123.1018
922.7656 | 123.1842 | -60.8414 | 62.0178 | -0.057449 | -0.0050116 | -0.012412 | 0.0015658 | 0.060532 | -0.0030869 | 0.068693 | -60.9512 | 61.9858 | -61.0886 | -61.0016 | 61.9308 | 0.13733 | -0.059509 | 0.2655 | 61.9858 | -61.0931 | -0.24719 | -0.032043 | -0.10986 | -0.16022 | -0.086975 | -0.25177 | -0.032043 | 0.13733 | 60.7819 | 61.1069 | 122.7722 | 122.8271 | -0.10986 | 122.8271 | 60.9787 | -0.25177 | 122.8271 | -0.10986 | 60.9787 | 122.7722 | 122.8271 | -123.1064 | -123.111
923.7656 | 123.2208 | -60.8414 | 62.0087 | -0.11848 | -0.0062934 | -0.0070709 | -0.00099756 | 0.059678 | -0.0045821 | 0.066129 | -60.9604 | 61.9995 | -61.0931 | -60.997 | 61.9171 | 0.15564 | -0.027466 | 0.2655 | 62.0087 | -61.0611 | -0.25177 | -0.009155 | -0.11902 | -0.15564 | -0.091553 | -0.21973 | 0 | 0.13275 | 60.8139 | 61.1069 | 122.7585 | 122.8409 | -0.11902 | 122.85 | 60.997 | -0.21973 | 122.8409 | -0.11902 | 60.997 | 122.7585 | 122.85 | -123.1018 | -123.0698
924.7656 | 123.2025 | -60.8459 | 61.9995 | -0.13374 | -0.0067206 | -0.0034393 | 0.0011386 | 0.060105 | -0.0043685 | 0.067197 | -60.965 | 61.9995 | -61.116 | -61.0107 | 61.9263 | 0.16022 | -0.054932 | 0.2655 | 61.9904 | -61.0703 | -0.27008 | 0 | -0.11902 | -0.16479 | -0.073242 | -0.2243 | -0.009156 | 0.15106 | 60.791 | 61.1115 | 122.7722 | 122.8455 | -0.11902 | 122.8363 | 61.0062 | -0.2243 | 122.8455 | -0.11902 | 61.0062 | 122.7722 | 122.8363 | -123.1155 | -123.0698
925.7656 | 123.1934 | -60.8826 | 61.9812 | -0.026932 | -0.0056524 | -0.0070709 | -0.0020658 | 0.06096 | -0.0039413 | 0.069974 | -60.997 | 61.9949 | -61.1298 | -61.0565 | 61.8851 | 0.10986 | -0.07782 | 0.20599 | 61.9766 | -61.0748 | -0.24719 | 0.013733 | -0.11444 | -0.17395 | -0.09613 | -0.19226 | -0.004577 | 0.13275 | 60.8047 | 61.0886 | 122.7676 | 122.8775 | -0.11444 | 122.8592 | 60.9924 | -0.19226 | 122.8775 | -0.11444 | 60.9924 | 122.7676 | 122.8592 | -123.111 | -123.056
926.7656 | 123.2208 | -60.8414 | 61.9766 | -0.026932 | -0.0080024 | -0.0038665 | 0.00049764 | 0.059678 | -0.0035141 | 0.068052 | -61.0107 | 61.9904 | -61.116 | -61.0611 | 61.8713 | 0.11444 | -0.07782 | 0.20599 | 61.9675 | -61.0794 | -0.27466 | 0.013732 | -0.16937 | -0.21973 | -0.10529 | -0.23804 | -0.009156 | 0.10529 | 60.7635 | 61.0474 | 122.7127 | 122.8317 | -0.16937 | 122.8088 | 60.9558 | -0.23804 | 122.8317 | -0.16937 | 60.9558 | 122.7127 | 122.8088 | -123.0927 | -123.056
927.7656 | 123.2162 | -60.8368 | 61.9904 | -0.04982 | -0.009284 | -0.0060027 | 7.0444e-05 | 0.059464 | -0.0047957 | 0.067197 | -60.9695 | 61.9949 | -61.1252 | -61.0016 | 61.94 | 0.17853 | -0.059509 | 0.27466 | 61.9949 | -61.0565 | -0.28839 | 0.004578 | -0.13275 | -0.16479 | -0.050354 | -0.21973 | 0.004578 | 0.15564 | 60.7773 | 61.1115 | 122.7768 | 122.8317 | -0.13275 | 122.8317 | 61.0153 | -0.21973 | 122.8317 | -0.13275 | 61.0153 | 122.7768 | 122.8317 | -123.1155 | -123.0469
928.7656 | 123.1888 | -60.8643 | 62.0087 | -0.15663 | -0.010993 | -0.010703 | 0.0028476 | 0.062455 | -0.0028731 | 0.067197 | -60.7269 | 62.0773 | -61.0886 | -61.0474 | 61.8759 | 0.14191 | -0.050354 | 0.2655 | 61.9766 | -61.084 | -0.2243 | 0.068665 | 0.13733 | -0.1831 | -0.13275 | -0.21973 | -0.032043 | 0.36163 | 60.8139 | 61.1298 | 122.7402 | 122.9416 | 0.13733 | 122.8409 | 61.0062 | -0.21973 | 122.9416 | 0.13733 | 61.0062 | 122.7402 | 122.8409 | -123.0972 | -123.0927
929.7656 | 123.1979 | -60.8734 | 62.0087 | -0.13374 | -0.0054388 | -0.0055755 | 0.0049838 | 0.061387 | -0.0056503 | 0.06912 | -60.9787 | 62.0087 | -61.0931 | -61.0611 | 61.9171 | 0.16022 | -0.086975 | 0.25635 | 61.9858 | -61.084 | -0.21973 | 0 | -0.10529 | -0.18768 | -0.091553 | -0.21057 | -0.022888 | 0.11444 | 60.7864 | 61.1298 | 122.7905 | 122.8821 | -0.10529 | 122.8592 | 61.0336 | -0.21057 | 122.8821 | -0.10529 | 61.0336 | 122.7905 | 122.8592 | -123.1018 | -123.0927
930.7656 | 123.23 | -60.8643 | 62.0087 | -0.15663 | -0.006507 | -0.0045075 | 0.00092504 | 0.060105 | -0.0039413 | 0.070188 | -60.9741 | 61.9995 | -61.0931 | -61.2213 | 61.821 | 0.13275 | -0.07782 | 0.27466 | 61.9812 | -61.0657 | -0.22888 | -0.009155 | -0.10986 | -0.35706 | -0.18768 | -0.20142 | -0.027466 | 0.11902 | 60.7864 | 61.1389 | 122.6852 | 122.8638 | -0.10986 | 122.8455 | 60.997 | -0.20142 | 122.8638 | -0.10986 | 60.997 | 122.6852 | 122.8455 | -123.1018 | -123.0743
931.7656 | 123.1888 | -60.8688 | 61.9949 | -0.15663 | -0.0069342 | -0.0070709 | 0.0030612 | 0.060105 | -0.0035141 | 0.067411 | -60.9741 | 62.0132 | -61.1023 | -61.0062 | 61.9766 | 0.35248 | -0.050354 | 0.082397 | 62.0178 | -61.0565 | -0.23346 | 0.018311 | -0.10529 | -0.13733 | -0.01831 | -0.18768 | 0.022888 | 0.12817 | 60.8185 | 60.9512 | 122.8455 | 122.8821 | -0.10529 | 122.8867 | 61.2213 | -0.18768 | 122.8821 | -0.10529 | 61.2213 | 122.8455 | 122.8867 | -123.0972 | -123.0515
932.7656 | 123.2346 | -60.8276 | 62.0087 | -0.080337 | -0.0054388 | -0.0055755 | 0.0015658 | 0.059891 | -0.0045821 | 0.069974 | -60.997 | 61.9904 | -61.0931 | -61.0382 | 61.9171 | 0.16022 | -0.07782 | 0.25635 | 61.972 | -61.1114 | -0.2655 | -0.018311 | -0.16937 | -0.21057 | -0.091553 | -0.28381 | -0.036621 | 0.096131 | 60.7498 | 61.084 | 122.7448 | 122.818 | -0.16937 | 122.7997 | 60.9879 | -0.28381 | 122.818 | -0.16937 | 60.9879 | 122.7448 | 122.7997 | -123.1018 | -123.1201
933.7656 | 123.2346 | -60.8551 | 61.9904 | -0.019302 | -0.0084296 | -0.0083527 | 0.00092504 | 0.061173 | -0.0035141 | 0.069547 | -60.997 | 61.9904 | -61.1114 | -61.0291 | 61.908 | 0.13275 | -0.07782 | 0.26093 | 61.9995 | -61.0931 | -0.25635 | 0 | -0.14191 | -0.17395 | -0.082397 | -0.23804 | 0.009156 | 0.11444 | 60.7773 | 61.116 | 122.7631 | 122.8455 | -0.14191 | 122.8546 | 60.9879 | -0.23804 | 122.8455 | -0.14191 | 60.9879 | 122.7631 | 122.8546 | -123.1018 | -123.0835
934.7656 | 123.2025 | -60.8688 | 62.0041 | -0.026932 | -0.0067206 | -0.0064301 | 0.0015658 | 0.060105 | -0.0043685 | 0.067411 | -60.9467 | 62.0041 | -61.1023 | -61.0062 | 61.9125 | 0.16479 | -0.036621 | 0.26093 | 61.9949 | -61.0703 | -0.23346 | 0 | -0.07782 | -0.13733 | -0.091552 | -0.20142 | -0.009155 | 0.15564 | 60.8322 | 61.1298 | 122.7814 | 122.8729 | -0.07782 | 122.8638 | 61.0336 | -0.20142 | 122.8729 | -0.07782 | 61.0336 | 122.7814 | 122.8638 | -123.1064 | -123.0743
935.7656 | 123.1934 | -60.8643 | 62.0041 | 0.12566 | -0.0056524 | -0.0077117 | 7.0444e-05 | 0.060105 | -0.0039413 | 0.068052 | -60.9879 | 62.0132 | -61.0977 | -61.0291 | 61.908 | 0.15106 | -0.022888 | 0.25177 | 61.9904 | -61.0886 | -0.23346 | 0.009156 | -0.1236 | -0.16479 | -0.09613 | -0.2243 | -0.013733 | 0.10986 | 60.8414 | 61.116 | 122.7722 | 122.8775 | -0.1236 | 122.8546 | 61.0153 | -0.2243 | 122.8775 | -0.1236 | 61.0153 | 122.7722 | 122.8546 | -123.1018 | -123.0927
936.7656 | 123.1842 | -60.878 | 62.0087 | -0.10323 | -0.0043708 | -0.0040801 | 0.0017794 | 0.059251 | -0.0045821 | 0.069333 | -61.0153 | 62.0087 | -61.1206 | -61.0291 | 61.8896 | 0.13733 | -0.027466 | 0.27008 | 61.9904 | -61.0748 | -0.24261 | 0 | -0.13733 | -0.15106 | -0.11902 | -0.19684 | -0.018311 | 0.10528 | 60.8505 | 61.1481 | 122.7676 | 122.8867 | -0.13733 | 122.8683 | 61.0153 | -0.19684 | 122.8867 | -0.13733 | 61.0153 | 122.7676 | 122.8683 | -123.1293 | -123.0835
937.7656 | 123.0835 | -60.8963 | 62.0499 | -0.15663 | -0.0052252 | -0.0096343 | 0.0079744 | 0.062882 | -0.0067185 | 0.068906 | -61.1664 | 62.0956 | -61.1343 | -61.1526 | 61.7889 | 0.045776 | 0.14648 | 0.11444 | 62.0361 | -61.1023 | -0.23804 | 0.045776 | -0.27008 | -0.25635 | -0.26093 | -0.20599 | -0.013733 | -0.032044 | 61.0428 | 61.0107 | 122.6852 | 122.9919 | -0.27008 | 122.9324 | 60.9421 | -0.20599 | 122.9919 | -0.27008 | 60.9421 | 122.6852 | 122.9324 | -123.1842 | -123.1522
938.7656 | 123.1934 | -60.8688 | 61.9949 | -0.13374 | -0.0069342 | -0.0015167 | 0.001993 | 0.060532 | -0.0047957 | 0.068265 | -61.116 | 62.0041 | -61.0794 | -61.0565 | 61.9171 | 0.14191 | -0.073242 | 0.25177 | 62.0041 | -61.0382 | -0.21057 | 0.009155 | -0.24719 | -0.18768 | -0.07782 | -0.16937 | 0.009155 | -0.036621 | 60.7956 | 61.1206 | 122.7859 | 122.8729 | -0.24719 | 122.8729 | 61.0107 | -0.16937 | 122.8729 | -0.24719 | 61.0107 | 122.7859 | 122.8729 | -123.0743 | -123.0331
939.7656 | 123.2162 | -60.8231 | 61.9858 | -0.080337 | -0.0067206 | -0.0074981 | -0.001425 | 0.06395 | -0.0062911 | 0.067838 | -60.9879 | 62.0041 | -61.116 | -61.0245 | 61.9263 | 0.16479 | -0.073242 | 0.27008 | 61.9995 | -61.0336 | -0.29297 | 0.01831 | -0.16479 | -0.20142 | -0.059509 | -0.21057 | 0.013733 | 0.12817 | 60.7498 | 61.0931 | 122.7493 | 122.8271 | -0.16479 | 122.8226 | 60.9879 | -0.21057 | 122.8271 | -0.16479 | 60.9879 | 122.7493 | 122.8226 | -123.1018 | -123.0194
940.7656 | 123.2071 | -60.8871 | 61.9904 | -0.13374 | -0.0056524 | -0.0055755 | 0.00049764 | 0.059678 | -0.0033005 | 0.068479 | -60.9695 | 62.0087 | -61.0794 | -61.1206 | 62.0956 | 0.39368 | -0.20599 | 0.09613 | 61.9858 | -61.0611 | -0.19226 | 0.018311 | -0.082397 | -0.23346 | 0.10529 | -0.17395 | -0.004577 | 0.10986 | 60.6812 | 60.9833 | 122.9828 | 122.8958 | -0.082397 | 122.8729 | 61.2808 | -0.17395 | 122.8958 | -0.082397 | 61.2808 | 122.9828 | 122.8729 | -123.0698 | -123.0515
941.7656 | 123.1476 | -60.8505 | 61.9812 | -0.13374 | -0.006507 | -0.0068573 | -0.00035676 | 0.059891 | -0.0052231 | 0.069974 | -60.9741 | 61.9995 | -61.116 | -61.0245 | 61.9217 | 0.15564 | 0.086975 | 0.59509 | 62.0224 | -61.0703 | -0.2655 | 0.018311 | -0.1236 | -0.17395 | -0.059509 | -0.21973 | 0.041199 | 0.14191 | 60.9375 | 61.4456 | 122.7722 | 122.85 | -0.1236 | 122.8729 | 61.0062 | -0.21973 | 122.85 | -0.1236 | 61.0062 | 122.7722 | 122.8729 | -123.0972 | -123.0515
942.7656 | 123.1613 | -60.9055 | 62.0361 | -0.10323 | -0.0062934 | -0.0085663 | 0.002634 | 0.059678 | -0.0047957 | 0.069974 | -60.9787 | 62.0316 | -61.0977 | -61.0336 | 61.8805 | 0.14648 | 0.018311 | 0.25177 | 62.027 | -61.084 | -0.19226 | -0.004578 | -0.073242 | -0.12817 | -0.15564 | -0.17853 | -0.009155 | 0.11902 | 60.9238 | 61.1572 | 122.7859 | 122.937 | -0.073242 | 122.9324 | 61.0519 | -0.17853 | 122.937 | -0.073242 | 61.0519 | 122.7859 | 122.9324 | -123.1338 | -123.1201
943.7656 | 123.143 | -60.8597 | 62.0178 | -0.33211 | -0.006507 | -0.0051483 | 0.0032748 | 0.062241 | -0.0050095 | 0.066984 | -60.965 | 62.027 | -61.0977 | -61.0291 | 61.8896 | 0.14648 | 0.004578 | 0.25635 | 61.9995 | -61.0794 | -0.23804 | 0.009156 | -0.10529 | -0.16937 | -0.12817 | -0.21973 | -0.01831 | 0.13275 | 60.8643 | 61.116 | 122.7493 | 122.8867 | -0.10529 | 122.8592 | 61.0062 | -0.21973 | 122.8867 | -0.10529 | 61.0062 | 122.7493 | 122.8592 | -123.1155 | -123.0972
944.7656 | 123.2025 | -60.8734 | 62.027 | 0.15617 | -0.0071478 | -0.0025847 | 0.0022066 | 0.059464 | -0.0062911 | 0.068052 | -60.9833 | 62.0041 | -61.1114 | -61.0382 | 61.8851 | 0.14648 | -0.013733 | 0.25635 | 61.9812 | -61.0657 | -0.23804 | -0.022889 | -0.10986 | -0.16479 | -0.14191 | -0.19226 | -0.045777 | 0.12817 | 60.8597 | 61.1298 | 122.7585 | 122.8775 | -0.10986 | 122.8546 | 61.0199 | -0.19226 | 122.8775 | -0.10986 | 61.0199 | 122.7585 | 122.8546 | -123.1384 | -123.0927
945.7656 | 123.1934 | -60.8505 | 62.0132 | 0.41557 | -0.006507 | -0.0049347 | 0.0022066 | 0.06096 | -0.0047957 | 0.066343 | -60.9512 | 61.9858 | -61.1023 | -61.0428 | 61.8942 | 0.12817 | -0.009155 | 0.25635 | 62.0087 | -61.0794 | -0.25177 | -0.027466 | -0.10071 | -0.19226 | -0.11902 | -0.22888 | -0.004578 | 0.15106 | 60.8414 | 61.1069 | 122.7448 | 122.8363 | -0.10071 | 122.8592 | 60.9787 | -0.22888 | 122.8363 | -0.10071 | 60.9787 | 122.7448 | 122.8592 | -123.1155 | -123.0927
946.7656 | 123.2391 | -60.8459 | 62.0041 | -0.095596 | -0.006507 | -0.0085663 | 0.00092504 | 0.061173 | -0.0030869 | 0.068265 | -60.9604 | 61.9995 | -61.1114 | -61.0107 | 61.9171 | 0.1831 | -0.068665 | 0.27008 | 61.9766 | -61.0748 | -0.2655 | -0.004577 | -0.11444 | -0.16479 | -0.086975 | -0.22888 | -0.027465 | 0.15106 | 60.7773 | 61.116 | 122.7631 | 122.8455 | -0.11444 | 122.8226 | 61.0291 | -0.22888 | 122.8455 | -0.11444 | 61.0291 | 122.7631 | 122.8226 | -123.1155 | -123.0789
947.7656 | 123.2391 | -60.8505 | 62.0132 | -0.019302 | -0.0062934 | -0.0038665 | 0.00092504 | 0.060319 | -0.0043685 | 0.06677 | -60.9787 | 62.0041 | -61.0886 | -61.0245 | 61.9171 | 0.16022 | -0.073242 | 0.27924 | 61.9995 | -61.0748 | -0.23804 | -0.009156 | -0.12817 | -0.17395 | -0.096131 | -0.2243 | -0.013733 | 0.10986 | 60.7773 | 61.1298 | 122.7676 | 122.8546 | -0.12817 | 122.85 | 61.0107 | -0.2243 | 122.8546 | -0.12817 | 61.0107 | 122.7676 | 122.85 | -123.1018 | -123.0881
948.7656 | 123.1842 | -60.8505 | 62.0224 | -0.11848 | -0.0069342 | -0.0053619 | 0.0028476 | 0.056473 | -0.0052231 | 0.070615 | -60.9604 | 62.0041 | -61.1252 | -61.2259 | 61.853 | 0.14191 | -0.068665 | 0.27466 | 61.9629 | -61.1069 | -0.27466 | -0.018311 | -0.10986 | -0.37537 | -0.16937 | -0.25635 | -0.059509 | 0.16479 | 60.7819 | 61.1252 | 122.7036 | 122.8546 | -0.10986 | 122.8134 | 60.9924 | -0.25635 | 122.8546 | -0.10986 | 60.9924 | 122.7036 | 122.8134 | -123.1476 | -123.1293
949.7656 | 123.1476 | -60.8688 | 62.027 | -0.20241 | -0.006507 | -0.011557 | 0.0028476 | 0.060319 | -0.0030869 | 0.068052 | -60.9695 | 62.0316 | -61.084 | -61.0382 | 61.8713 | 0.12817 | 0.027466 | 0.24261 | 62.0132 | -61.0748 | -0.21515 | 0.004577 | -0.10071 | -0.16937 | -0.15564 | -0.20599 | -0.013733 | 0.11444 | 60.8963 | 61.1114 | 122.7402 | 122.9004 | -0.10071 | 122.8821 | 60.997 | -0.20599 | 122.9004 | -0.10071 | 60.997 | 122.7402 | 122.8821 | -123.111 | -123.1018
950.7656 | 123.1476 | -60.8688 | 62.0499 | -0.14137 | -0.006507 | -0.0034393 | 0.001993 | 0.061387 | -0.0047957 | 0.067411 | -60.9787 | 62.027 | -61.1069 | -61.0428 | 61.8988 | 0.13275 | 0.022888 | 0.25177 | 62.0361 | -61.084 | -0.23804 | -0.022888 | -0.10986 | -0.17395 | -0.15106 | -0.21515 | -0.013733 | 0.12817 | 60.8917 | 61.1206 | 122.7676 | 122.8958 | -0.10986 | 122.905 | 61.0016 | -0.21515 | 122.8958 | -0.10986 | 61.0016 | 122.7676 | 122.905 | -123.1567 | -123.1338
951.7656 | 123.1842 | -60.8551 | 62.0316 | -0.11848 | -0.0062934 | -0.0064301 | 0.0028476 | 0.060746 | -0.0056503 | 0.066984 | -60.9787 | 62.0132 | -61.1298 | -61.0382 | 61.8759 | 0.14648 | 0 | 0.25177 | 62.0087 | -61.0931 | -0.27466 | -0.01831 | -0.1236 | -0.1831 | -0.15564 | -0.23804 | -0.022888 | 0.15106 | 60.8551 | 61.1069 | 122.731 | 122.8683 | -0.1236 | 122.8638 | 61.0016 | -0.23804 | 122.8683 | -0.1236 | 61.0016 | 122.731 | 122.8638 | -123.1613 | -123.1247
952.7656 | 123.1659 | -60.8597 | 62.0407 | -0.19478 | -0.0073614 | -0.0098479 | 0.001993 | 0.062882 | -0.0039413 | 0.06912 | -60.9741 | 62.0132 | -61.0931 | -61.0382 | 61.8896 | 0.13733 | -0.018311 | 0.25177 | 62.027 | -61.0703 | -0.23346 | -0.027465 | -0.11444 | -0.17853 | -0.15106 | -0.21057 | -0.013732 | 0.11902 | 60.8414 | 61.1114 | 122.7493 | 122.8729 | -0.11444 | 122.8867 | 60.997 | -0.21057 | 122.8729 | -0.11444 | 60.997 | 122.7493 | 122.8867 | -123.1338 | -123.111
953.7656 | 123.2208 | -60.8688 | 62.0132 | -0.10323 | -0.0056524 | -0.0081389 | 0.0032748 | 0.060319 | -0.0045821 | 0.068052 | -60.9604 | 62.0132 | -61.1343 | -61.0153 | 61.9034 | 0.15106 | -0.041199 | 0.27924 | 61.9858 | -61.0748 | -0.2655 | 0 | -0.091553 | -0.14649 | -0.10986 | -0.20599 | -0.027466 | 0.17395 | 60.8276 | 61.1481 | 122.7722 | 122.8821 | -0.091553 | 122.8546 | 61.0199 | -0.20599 | 122.8821 | -0.091553 | 61.0199 | 122.7722 | 122.8546 | -123.1476 | -123.0881
954.7656 | 123.2162 | -60.8459 | 61.9995 | -0.04982 | -0.007575 | -0.012839 | 0.0024202 | 0.059678 | -0.0043685 | 0.070188 | -60.9695 | 62.0316 | -61.116 | -61.0336 | 61.8851 | 0.16022 | -0.054932 | 0.26093 | 61.9995 | -61.0931 | -0.27008 | 0.032043 | -0.1236 | -0.18768 | -0.11444 | -0.24719 | 0 | 0.14648 | 60.791 | 61.1069 | 122.731 | 122.8775 | -0.1236 | 122.8455 | 61.0062 | -0.24719 | 122.8775 | -0.1236 | 61.0062 | 122.731 | 122.8455 | -123.1155 | -123.0927
955.7656 | 123.1659 | -60.8505 | 62.0407 | -0.15663 | -0.0043708 | -0.0081389 | 0.0028476 | 0.058823 | -0.0035141 | 0.067838 | -60.9695 | 62.0316 | -61.1298 | -61.0382 | 61.8896 | 0.13733 | -0.018311 | 0.26093 | 61.9858 | -61.1069 | -0.27924 | -0.009155 | -0.11902 | -0.18768 | -0.15106 | -0.25635 | -0.054931 | 0.16022 | 60.8322 | 61.1114 | 122.7402 | 122.8821 | -0.11902 | 122.8363 | 60.9879 | -0.25635 | 122.8821 | -0.11902 | 60.9879 | 122.7402 | 122.8363 | -123.1705 | -123.1476
956.7656 | 123.0972 | -60.8917 | 62.0407 | -0.18715 | -0.004798 | -0.0047211 | 0.003702 | 0.060105 | -0.0056503 | 0.069333 | -61.0016 | 62.0544 | -61.116 | -61.0886 | 61.8301 | 0.082397 | 0.10071 | 0.19684 | 62.059 | -61.1252 | -0.2243 | 0.013733 | -0.10986 | -0.19684 | -0.21057 | -0.23346 | 0.018311 | 0.11444 | 60.9924 | 61.0886 | 122.7219 | 122.9462 | -0.10986 | 122.9507 | 60.9741 | -0.23346 | 122.9462 | -0.10986 | 60.9741 | 122.7219 | 122.9507 | -123.1567 | -123.1659
957.7656 | 123.1018 | -60.9009 | 62.0453 | -0.19478 | -0.0050116 | -0.0077117 | 0.0034884 | 0.0616 | -0.0062911 | 0.067838 | -60.997 | 62.0544 | -61.1114 | -61.1114 | 61.8439 | 0.10071 | 0.086975 | 0.17853 | 62.0682 | -61.1206 | -0.21057 | 0.009155 | -0.09613 | -0.21057 | -0.20142 | -0.21973 | 0.022888 | 0.11444 | 60.9879 | 61.0794 | 122.7448 | 122.9553 | -0.09613 | 122.9691 | 61.0016 | -0.21973 | 122.9553 | -0.09613 | 61.0016 | 122.7448 | 122.9691 | -123.1567 | -123.1659
958.7656 | 123.0972 | -60.8917 | 62.0361 | -0.20241 | -0.0050116 | -0.0053619 | 0.0032748 | 0.062028 | -0.0065047 | 0.068693 | -60.9924 | 62.0407 | -61.116 | -61.0886 | 61.8393 | 0.10071 | 0.11902 | 0.16479 | 62.0773 | -61.1069 | -0.2243 | 0.004577 | -0.10071 | -0.19684 | -0.19684 | -0.21515 | 0.041199 | 0.1236 | 61.0107 | 61.0565 | 122.731 | 122.9324 | -0.10071 | 122.9691 | 60.9924 | -0.21515 | 122.9324 | -0.10071 | 60.9924 | 122.731 | 122.9691 | -123.1522 | -123.143
959.7656 | 123.0927 | -60.8734 | 62.059 | -0.17189 | -0.0054388 | -0.0060027 | 0.004343 | 0.059891 | -0.0052231 | 0.069761 | -61.0107 | 62.0407 | -61.1206 | -61.0977 | 61.8256 | 0.073242 | 0.091553 | 0.17853 | 62.0407 | -61.116 | -0.24719 | -0.018311 | -0.13733 | -0.2243 | -0.23346 | -0.24262 | -0.018311 | 0.10986 | 60.965 | 61.0519 | 122.699 | 122.9141 | -0.13733 | 122.9141 | 60.9467 | -0.24262 | 122.9141 | -0.13733 | 60.9467 | 122.699 | 122.9141 | -123.1796 | -123.175
960.7656 | 123.1796 | -60.8505 | 62.0407 | -0.080337 | -0.004798 | -0.010062 | 0.0015658 | 0.061814 | -0.0035141 | 0.067197 | -60.9695 | 62.0316 | -61.084 | -61.0428 | 61.8896 | 0.13733 | -0.018311 | 0.25177 | 61.9995 | -61.0794 | -0.23346 | -0.009155 | -0.11902 | -0.19226 | -0.15106 | -0.22888 | -0.041198 | 0.11444 | 60.8322 | 61.1023 | 122.7402 | 122.8821 | -0.11902 | 122.85 | 60.9879 | -0.22888 | 122.8821 | -0.11902 | 60.9879 | 122.7402 | 122.85 | -123.1247 | -123.1201
961.7656 | 123.1842 | -60.8551 | 62.0178 | -0.16426 | -0.0084296 | -0.0057891 | 0.00049764 | 0.063096 | -0.0035141 | 0.068265 | -60.9467 | 62.0224 | -61.1023 | -61.0474 | 61.9125 | 0.13733 | -0.013733 | 0.26093 | 62.0132 | -61.1069 | -0.24719 | 0.004578 | -0.091552 | -0.19226 | -0.10529 | -0.25177 | -0.004577 | 0.15564 | 60.8414 | 61.116 | 122.7676 | 122.8775 | -0.091552 | 122.8683 | 60.9924 | -0.25177 | 122.8775 | -0.091552 | 60.9924 | 122.7676 | 122.8683 | -123.1201 | -123.1247
962.7656 | 123.1293 | -60.878 | 62.0361 | -0.19478 | -0.0041572 | -0.0077117 | 0.001993 | 0.061814 | -0.0058639 | 0.069333 | -61.0062 | 62.0499 | -61.1069 | -61.0748 | 61.8439 | 0.091553 | 0.086975 | 0.19226 | 62.027 | -61.0931 | -0.22888 | 0.013733 | -0.12817 | -0.19684 | -0.19226 | -0.21515 | -0.009155 | 0.10071 | 60.965 | 61.0703 | 122.7219 | 122.9279 | -0.12817 | 122.905 | 60.9695 | -0.21515 | 122.9279 | -0.12817 | 60.9695 | 122.7219 | 122.905 | -123.143 | -123.1293
963.7656 | 123.0743 | -60.8963 | 62.0453 | -0.16426 | -0.0039434 | -0.0066437 | 0.004343 | 0.05861 | -0.0035141 | 0.068693 | -61.0519 | 62.0911 | -61.1435 | -61.1343 | 61.8073 | 0.064087 | 0.15106 | 0.14648 | 62.0361 | -61.1389 | -0.24719 | 0.045776 | -0.15564 | -0.23804 | -0.23804 | -0.24262 | -0.009155 | 0.091553 | 61.0474 | 61.0428 | 122.7036 | 122.9874 | -0.15564 | 122.9324 | 60.9604 | -0.24262 | 122.9874 | -0.15564 | 60.9604 | 122.7036 | 122.9324 | -123.1888 | -123.1842
964.7656 | 123.0469 | -60.9192 | 62.059 | -0.17189 | -0.0067206 | -0.0030121 | 0.0034884 | 0.062669 | -0.0037277 | 0.067411 | -61.0519 | 62.1002 | -61.1526 | -61.1298 | 61.8073 | 0.054932 | 0.15564 | 0.15564 | 62.0819 | -61.1206 | -0.23346 | 0.041199 | -0.13275 | -0.21057 | -0.25177 | -0.20142 | 0.022888 | 0.10071 | 61.0748 | 61.0748 | 122.7264 | 123.0194 | -0.13275 | 123.0011 | 60.9741 | -0.20142 | 123.0194 | -0.13275 | 60.9741 | 122.7264 | 123.0011 | -123.2117 | -123.1796
965.7656 | 123.0652 | -60.9055 | 62.027 | -0.034561 | -0.0033026 | -0.010275 | 0.0022066 | 0.061814 | -0.0047957 | 0.068906 | -61.0519 | 62.114 | -61.1298 | -61.1389 | 61.8118 | 0.059509 | 0.14648 | 0.16937 | 62.059 | -61.1298 | -0.2243 | 0.086975 | -0.14648 | -0.23346 | -0.21515 | -0.2243 | 0.032043 | 0.07782 | 61.0519 | 61.0748 | 122.7173 | 123.0194 | -0.14648 | 122.9645 | 60.965 | -0.2243 | 123.0194 | -0.14648 | 60.965 | 122.7173 | 122.9645 | -123.1567 | -123.1567
966.7656 | 123.1064 | -60.8917 | 62.0682 | -0.13374 | -0.0052252 | -0.0040801 | 0.0017794 | 0.0616 | -0.0054367 | 0.067197 | -61.0611 | 62.0911 | -61.1206 | -61.1389 | 61.7981 | 0.07782 | 0.14191 | 0.16937 | 62.0682 | -61.1435 | -0.22888 | 0.022888 | -0.16937 | -0.24719 | -0.27008 | -0.25177 | 0 | 0.059509 | 61.0336 | 61.0611 | 122.6898 | 122.9828 | -0.16937 | 122.9599 | 60.9695 | -0.25177 | 122.9828 | -0.16937 | 60.9695 | 122.6898 | 122.9599 | -123.1888 | -123.2117
967.7656 | 123.1567 | -60.878 | 62.027 | -0.095596 | -0.0056524 | -0.0051483 | 0.002634 | 0.063737 | -0.0045821 | 0.067197 | -60.9833 | 62.0224 | -61.0931 | -61.0474 | 61.8988 | 0.13275 | 0.018311 | 0.24719 | 62.0178 | -61.0931 | -0.21515 | -0.004578 | -0.10528 | -0.16937 | -0.12817 | -0.21515 | -0.009156 | 0.10986 | 60.8963 | 61.1252 | 122.7768 | 122.9004 | -0.10528 | 122.8958 | 61.0107 | -0.21515 | 122.9004 | -0.10528 | 61.0107 | 122.7768 | 122.8958 | -123.1201 | -123.1201
968.7656 | 123.0881 | -60.8917 | 62.059 | -0.14137 | -0.005866 | -0.0042937 | 0.001993 | 0.059891 | -0.0037277 | 0.066556 | -61.0153 | 62.0865 | -61.1343 | -61.1069 | 61.8118 | 0.082397 | 0.086975 | 0.20142 | 62.0316 | -61.1023 | -0.24261 | 0.027466 | -0.1236 | -0.21515 | -0.24719 | -0.21057 | -0.027466 | 0.11902 | 60.9787 | 61.0931 | 122.7036 | 122.9782 | -0.1236 | 122.9233 | 60.9741 | -0.21057 | 122.9782 | -0.1236 | 60.9741 | 122.7036 | 122.9233 | -123.1934 | -123.1613
969.7656 | 123.1018 | -60.8734 | 62.0361 | -0.21767 | -0.0056524 | -0.0034393 | 0.0024202 | 0.059464 | -0.0037277 | 0.068265 | -60.9924 | 62.0682 | -61.1343 | -61.0931 | 61.8484 | 0.091553 | 0.10071 | 0.20599 | 62.0316 | -61.1343 | -0.26093 | 0.032043 | -0.11902 | -0.21973 | -0.18768 | -0.26093 | -0.004578 | 0.14191 | 60.9741 | 61.0794 | 122.7219 | 122.9416 | -0.11902 | 122.905 | 60.965 | -0.26093 | 122.9416 | -0.11902 | 60.965 | 122.7219 | 122.905 | -123.1705 | -123.1705
970.7656 | 123.0835 | -60.8963 | 62.059 | -0.15663 | -0.0056524 | -0.0070709 | 0.0015658 | 0.0616 | -0.0050095 | 0.066984 | -61.0428 | 62.1002 | -61.1481 | -61.1481 | 61.7935 | 0.073242 | 0.16479 | 0.16022 | 62.059 | -61.1206 | -0.25177 | 0.041199 | -0.14648 | -0.25177 | -0.2655 | -0.2243 | 0 | 0.10529 | 61.0611 | 61.0565 | 122.6898 | 122.9965 | -0.14648 | 122.9553 | 60.9695 | -0.2243 | 122.9965 | -0.14648 | 60.9695 | 122.6898 | 122.9553 | -123.2071 | -123.1796
971.7656 | 123.0743 | -60.8963 | 62.0544 | -0.36262 | -0.0062934 | -0.0068573 | 0.0039156 | 0.059678 | -0.0028731 | 0.067838 | -61.0519 | 62.0911 | -61.1206 | -61.1343 | 61.821 | 0.045776 | 0.13733 | 0.16479 | 62.0453 | -61.1526 | -0.2243 | 0.036621 | -0.15564 | -0.23804 | -0.23346 | -0.25635 | -0.009155 | 0.068664 | 61.0336 | 61.0611 | 122.7173 | 122.9874 | -0.15564 | 122.9416 | 60.9421 | -0.25635 | 122.9874 | -0.15564 | 60.9421 | 122.7173 | 122.9416 | -123.175 | -123.2071
972.7656 | 123.1018 | -60.9238 | 62.0499 | -0.16426 | -0.0041572 | -0.0087799 | 0.0030612 | 0.059678 | -0.0050095 | 0.067411 | -61.0336 | 62.0773 | -61.1069 | -61.1435 | 61.7752 | 0.064087 | 0.1236 | 0.16022 | 62.0499 | -61.0977 | -0.18311 | 0.027466 | -0.10986 | -0.21973 | -0.27466 | -0.17395 | 0 | 0.073243 | 61.0474 | 61.084 | 122.699 | 123.0011 | -0.10986 | 122.9736 | 60.9879 | -0.17395 | 123.0011 | -0.10986 | 60.9879 | 122.699 | 122.9736 | -123.1567 | -123.1476
973.7656 | 123.0927 | -60.8871 | 62.0453 | -0.14137 | -0.0067206 | -0.0047211 | 0.0011386 | 0.062241 | -0.0041549 | 0.06912 | -61.0107 | 62.059 | -61.1206 | -61.116 | 61.8301 | 0.086975 | 0.091553 | 0.17853 | 62.059 | -61.1252 | -0.23346 | 0.013733 | -0.1236 | -0.22888 | -0.21515 | -0.23804 | 0.013733 | 0.10986 | 60.9787 | 61.0657 | 122.7173 | 122.9462 | -0.1236 | 122.9462 | 60.9741 | -0.23804 | 122.9462 | -0.1236 | 60.9741 | 122.7173 | 122.9462 | -123.1659 | -123.1705
974.7656 | 123.2071 | -60.8826 | 62.0087 | 0.23247 | -0.0050116 | -0.0081389 | 0.0030612 | 0.060532 | -0.0039413 | 0.066129 | -60.965 | 62.0132 | -61.1114 | -61.0382 | 61.8942 | 0.13733 | -0.013733 | 0.26093 | 62.0178 | -61.0977 | -0.22888 | 0.004578 | -0.082398 | -0.15564 | -0.11444 | -0.21515 | 0.009155 | 0.14648 | 60.8688 | 61.1435 | 122.7768 | 122.8958 | -0.082398 | 122.9004 | 61.0199 | -0.21515 | 122.8958 | -0.082398 | 61.0199 | 122.7768 | 122.9004 | -123.1201 | -123.1064
975.7656 | 123.1247 | -60.8871 | 62.0453 | -0.18715 | -0.0060798 | -0.0094207 | 0.0017794 | 0.0616 | -0.0050095 | 0.068906 | -60.9833 | 62.0407 | -61.1069 | -61.0703 | 61.8622 | 0.13275 | 0.054932 | 0.21973 | 62.0361 | -61.0931 | -0.21973 | -0.004578 | -0.09613 | -0.1831 | -0.1831 | -0.20599 | -0.009155 | 0.1236 | 60.9421 | 61.1069 | 122.7493 | 122.9279 | -0.09613 | 122.9233 | 61.0199 | -0.20599 | 122.9279 | -0.09613 | 61.0199 | 122.7493 | 122.9233 | -123.1522 | -123.1384
976.7656 | 123.0698 | -60.8917 | 62.0453 | -0.026932 | -0.0067206 | -0.0055755 | 0.002634 | 0.061387 | -0.0050095 | 0.067838 | -60.9924 | 62.0865 | -61.0977 | -61.1252 | 61.8073 | 0.059509 | 0.15106 | 0.16022 | 62.059 | -61.1252 | -0.20599 | 0.041199 | -0.10071 | -0.23346 | -0.23804 | -0.23346 | 0.013733 | 0.10529 | 61.0428 | 61.0519 | 122.699 | 122.9782 | -0.10071 | 122.9507 | 60.9512 | -0.23346 | 122.9782 | -0.10071 | 60.9512 | 122.699 | 122.9507 | -123.143 | -123.1705
977.7656 | 123.1018 | -60.8917 | 62.0316 | -0.18715 | -0.0060798 | -0.0053619 | 0.0011386 | 0.0616 | -0.0039413 | 0.070188 | -61.0382 | 62.0819 | -61.1343 | -61.1298 | 61.7844 | 0.054932 | 0.12817 | 0.15564 | 62.0773 | -61.1389 | -0.24261 | 0.050354 | -0.14648 | -0.23804 | -0.24719 | -0.24719 | 0.045777 | 0.09613 | 61.0199 | 61.0474 | 122.6761 | 122.9736 | -0.14648 | 122.9691 | 60.9467 | -0.24719 | 122.9736 | -0.14648 | 60.9467 | 122.6761 | 122.9691 | -123.1659 | -123.1705
978.7812 | 123.0423 | -60.9375 | 62.0178 | 0.24773 | -0.003089 | -0.0064301 | 0.0056246 | 0.062455 | -0.0028731 | 0.068265 | -61.0565 | 62.1231 | -61.1618 | -61.1801 | 61.7477 | -0.064087 | 0.041199 | -0.004578 | 62.0316 | -61.1618 | -0.2243 | 0.10529 | -0.11902 | -0.24262 | -0.27008 | -0.2243 | 0.013733 | 0.10528 | 60.9787 | 60.9329 | 122.6852 | 123.0606 | -0.11902 | 122.9691 | 60.8734 | -0.2243 | 123.0606 | -0.11902 | 60.8734 | 122.6852 | 122.9691 | -123.1796 | -123.1796
979.7656 | 123.111 | -60.8826 | 62.0132 | -0.15663 | -0.0045844 | -0.0062163 | -0.00035676 | 0.063737 | -0.0050095 | 0.068906 | -60.9879 | 62.0224 | -61.1114 | -61.0931 | 61.8484 | 0.091553 | 0.10529 | 0.19226 | 62.0544 | -61.1069 | -0.22888 | 0.009155 | -0.10529 | -0.21057 | -0.16479 | -0.22431 | 0.041198 | 0.1236 | 60.9879 | 61.0748 | 122.731 | 122.905 | -0.10529 | 122.937 | 60.9741 | -0.22431 | 122.905 | -0.10529 | 60.9741 | 122.731 | 122.937 | -123.1247 | -123.1201
980.7656 | 123.1979 | -60.8597 | 62.0041 | 1.8423 | -0.0054388 | -0.0068573 | 0.00028404 | 0.062028 | -0.0047957 | 0.068052 | -61.0062 | 62.0178 | -61.1114 | -61.0336 | 61.9263 | 0.15564 | -0.041199 | 0.27008 | 62.0041 | -61.0977 | -0.25177 | 0.013733 | -0.14649 | -0.17395 | -0.077819 | -0.23804 | 0 | 0.10528 | 60.8185 | 61.1298 | 122.7859 | 122.8775 | -0.14649 | 122.8638 | 61.0153 | -0.23804 | 122.8775 | -0.14649 | 61.0153 | 122.7859 | 122.8638 | -123.1155 | -123.1018
981.7656 | 123.1979 | -60.8643 | 61.9949 | -0.14137 | -0.0043708 | -0.0042937 | 0.0015658 | 0.065659 | -0.0052231 | 0.068265 | -60.9695 | 62.0041 | -61.0886 | -61.0886 | 61.8896 | 0.1831 | -0.09613 | 0.24261 | 62.0132 | -61.0794 | -0.2243 | 0.009155 | -0.10529 | -0.2243 | -0.10529 | -0.21515 | 0.018311 | 0.11902 | 60.7681 | 61.1069 | 122.7539 | 122.8683 | -0.10529 | 122.8775 | 61.0474 | -0.21515 | 122.8683 | -0.10529 | 61.0474 | 122.7539 | 122.8775 | -123.0835 | -123.0743
982.7656 | 123.1476 | -60.878 | 62.0316 | -0.17189 | -0.0050116 | -0.0064301 | 0.00028404 | 0.062669 | -0.0058639 | 0.069547 | -60.9695 | 62.0453 | -61.1023 | -61.0565 | 61.8896 | 0.13275 | 0.027466 | 0.24719 | 62.0132 | -61.084 | -0.2243 | 0.013733 | -0.091552 | -0.17853 | -0.14191 | -0.20599 | -0.01831 | 0.13275 | 60.9055 | 61.1252 | 122.7676 | 122.9233 | -0.091552 | 122.8912 | 61.0107 | -0.20599 | 122.9233 | -0.091552 | 61.0107 | 122.7676 | 122.8912 | -123.1338 | -123.1155
983.7812 | 123.0881 | -60.9283 | 62.0087 | 0.1104 | -0.0028754 | -0.0060027 | 0.0064792 | 0.065018 | -0.0041549 | 0.067624 | -60.9924 | 62.114 | -61.1435 | -61.1389 | 61.7615 | -0.018311 | 0.009155 | 0.050354 | 62.0361 | -61.1572 | -0.21515 | 0.10529 | -0.064087 | -0.21057 | -0.24719 | -0.22888 | 0.027466 | 0.15106 | 60.9375 | 60.9787 | 122.6898 | 123.0423 | -0.064087 | 122.9645 | 60.91 | -0.22888 | 123.0423 | -0.064087 | 60.91 | 122.6898 | 122.9645 | -123.1522 | -123.1659
984.7656 | 123.0881 | -60.8871 | 62.059 | -0.21004 | -0.0045844 | -0.0089935 | -0.00035676 | 0.062669 | -0.0045821 | 0.068052 | -61.0245 | 62.0544 | -61.1298 | -61.1114 | 61.8301 | 0.07782 | 0.11444 | 0.1831 | 62.059 | -61.0977 | -0.24262 | -0.004578 | -0.13733 | -0.2243 | -0.22888 | -0.21057 | 0 | 0.10529 | 61.0016 | 61.0703 | 122.7173 | 122.9416 | -0.13733 | 122.9462 | 60.965 | -0.21057 | 122.9416 | -0.13733 | 60.965 | 122.7173 | 122.9462 | -123.1888 | -123.1567
985.7656 | 123.1247 | -60.8917 | 62.0544 | -0.19478 | -0.0060798 | -0.0083527 | 0.0022066 | 0.061173 | -0.0041549 | 0.070188 | -61.0016 | 62.0636 | -61.1389 | -61.084 | 61.8393 | 0.1236 | 0.068665 | 0.21057 | 62.059 | -61.1114 | -0.24719 | 0.009156 | -0.10986 | -0.19226 | -0.21515 | -0.21973 | 0.004578 | 0.13733 | 60.9604 | 61.1023 | 122.731 | 122.9553 | -0.10986 | 122.9507 | 61.0153 | -0.21973 | 122.9553 | -0.10986 | 61.0153 | 122.731 | 122.9507 | -123.1934 | -123.1659
986.7656 | 123.1201 | -60.878 | 62.0453 | -0.18715 | -0.0062934 | -0.0072845 | 0.0011386 | 0.062241 | -0.0022323 | 0.068052 | -61.0062 | 62.0499 | -61.1298 | -61.0703 | 61.8668 | 0.1236 | 0.059509 | 0.23346 | 62.0132 | -61.116 | -0.25177 | 0.004578 | -0.12817 | -0.19226 | -0.17853 | -0.23804 | -0.032043 | 0.1236 | 60.9375 | 61.1115 | 122.7448 | 122.9279 | -0.12817 | 122.8912 | 61.0016 | -0.23804 | 122.9279 | -0.12817 | 61.0016 | 122.7448 | 122.8912 | -123.175 | -123.1613
987.7656 | 123.1796 | -60.8597 | 61.9904 | -0.14137 | -0.005866 | -0.0079253 | -0.00035676 | 0.059891 | -0.0099227 | 0.067197 | -60.965 | 62.027 | -61.1023 | -60.8368 | 61.8439 | -0.022888 | -0.045776 | 0.20142 | 61.9812 | -61.1023 | -0.24262 | 0.036622 | -0.10529 | 0.022888 | -0.14648 | -0.24262 | -0.009155 | 0.13733 | 60.8139 | 61.0611 | 122.7036 | 122.8867 | -0.10529 | 122.8409 | 60.8368 | -0.24262 | 122.8867 | -0.10529 | 60.8368 | 122.7036 | 122.8409 | -123.0927 | -123.0927
988.7812 | 123.1842 | -60.9192 | 61.9629 | 0.27061 | -0.0026618 | -0.0064301 | 0.0060518 | 0.064591 | -0.00073695 | 0.068693 | -61.0382 | 62.0407 | -61.1252 | -61.1206 | 61.7889 | 0 | -0.14648 | 0.091553 | 62.0041 | -61.1389 | -0.20599 | 0.077819 | -0.11902 | -0.20142 | -0.17395 | -0.21973 | 0.041198 | 0.086975 | 60.7727 | 61.0107 | 122.7081 | 122.9599 | -0.11902 | 122.9233 | 60.9192 | -0.21973 | 122.9599 | -0.11902 | 60.9192 | 122.7081 | 122.9233 | -123.0881 | -123.1018
989.7656 | 123.1934 | -60.8597 | 62.0132 | -0.04982 | -0.0056524 | -0.0079253 | -0.00078396 | 0.059678 | -0.0041549 | 0.068052 | -60.9741 | 62.0224 | -61.1389 | -61.0657 | 61.8988 | 0.12817 | -0.018311 | 0.25177 | 61.9995 | -61.1114 | -0.27924 | 0.009155 | -0.11444 | -0.20599 | -0.11444 | -0.25177 | -0.013733 | 0.1648 | 60.8414 | 61.1114 | 122.7585 | 122.8821 | -0.11444 | 122.8592 | 60.9879 | -0.25177 | 122.8821 | -0.11444 | 60.9879 | 122.7585 | 122.8592 | -123.1522 | -123.1247
990.7656 | 123.111 | -60.8963 | 62.0682 | -0.20241 | -0.0054388 | -0.0064301 | 0.0028476 | 0.060532 | -0.0052231 | 0.067411 | -61.0016 | 62.0773 | -61.1114 | -61.0977 | 61.8439 | 0.10529 | 0.086975 | 0.20142 | 62.059 | -61.116 | -0.21515 | 0.009156 | -0.10529 | -0.20142 | -0.2243 | -0.21973 | -0.009155 | 0.10986 | 60.9833 | 61.0977 | 122.7402 | 122.9736 | -0.10529 | 122.9553 | 61.0016 | -0.21973 | 122.9736 | -0.10529 | 61.0016 | 122.7402 | 122.9553 | -123.1796 | -123.1842
991.7812 | 123.0927 | -60.9009 | 62.0544 | -0.087967 | -0.0033026 | -0.0072845 | 0.0024202 | 0.061173 | -0.0058639 | 0.069547 | -61.0519 | 62.1048 | -61.1343 | -61.1526 | 61.8118 | 0.041199 | 0.16479 | 0.16937 | 62.0453 | -61.1069 | -0.23346 | 0.050354 | -0.15106 | -0.25177 | -0.24261 | -0.20599 | -0.009155 | 0.082397 | 61.0657 | 61.0703 | 122.7127 | 123.0057 | -0.15106 | 122.9462 | 60.9421 | -0.20599 | 123.0057 | -0.15106 | 60.9421 | 122.7127 | 122.9462 | -123.1888 | -123.1613
992.7656 | 123.1522 | -60.8734 | 62.0316 | -0.16426 | -0.004798 | -0.0062163 | 0.0028476 | 0.062028 | -0.0039413 | 0.06677 | -60.9833 | 62.0544 | -61.116 | -61.0794 | 61.8805 | 0.13275 | 0.050354 | 0.23804 | 62.0728 | -61.0977 | -0.24262 | 0.022888 | -0.10986 | -0.20599 | -0.15106 | -0.2243 | 0.041199 | 0.13275 | 60.9238 | 61.1114 | 122.7539 | 122.9279 | -0.10986 | 122.9462 | 61.0062 | -0.2243 | 122.9279 | -0.10986 | 61.0062 | 122.7539 | 122.9462 | -123.1476 | -123.1293
993.7656 | 123.1293 | -60.8963 | 61.9858 | 0.25536 | -0.0045844 | -0.0070709 | 0.0051974 | 0.061814 | -0.0045821 | 0.069761 | -61.0519 | 62.0407 | -61.1572 | -61.1389 | 61.7889 | -0.004578 | -0.10071 | 0.059509 | 61.9949 | -61.171 | -0.26093 | 0.054931 | -0.15564 | -0.24262 | -0.19684 | -0.27466 | 0.009155 | 0.10529 | 60.7956 | 60.9558 | 122.6852 | 122.937 | -0.15564 | 122.8912 | 60.8917 | -0.27466 | 122.937 | -0.15564 | 60.8917 | 122.6852 | 122.8912 | -123.143 | -123.1567
994.7656 | 123.2162 | -60.8505 | 61.9858 | -0.12611 | -0.006507 | -0.0049347 | -0.0016386 | 0.061387 | -0.0060775 | 0.066556 | -60.9558 | 62.0087 | -61.1114 | -61.0245 | 61.908 | 0.16022 | -0.045776 | 0.27924 | 62.0224 | -61.1069 | -0.26093 | 0.022888 | -0.10529 | -0.17395 | -0.07782 | -0.25635 | 0.036621 | 0.15564 | 60.8047 | 61.1298 | 122.7585 | 122.8592 | -0.10529 | 122.8729 | 61.0107 | -0.25635 | 122.8592 | -0.10529 | 61.0107 | 122.7585 | 122.8729 | -123.0972 | -123.0927
995.7656 | 123.23 | -60.8643 | 61.9995 | -0.13374 | -0.0062934 | -0.0030121 | 0.00028404 | 0.062241 | -0.0043685 | 0.069333 | -60.9512 | 61.9949 | -61.1206 | -61.0382 | 61.8988 | 0.15564 | -0.050354 | 0.2655 | 62.0316 | -61.0886 | -0.25635 | -0.004578 | -0.086975 | -0.17395 | -0.10071 | -0.2243 | 0.032043 | 0.16937 | 60.8139 | 61.1298 | 122.7631 | 122.8592 | -0.086975 | 122.8958 | 61.0199 | -0.2243 | 122.8592 | -0.086975 | 61.0199 | 122.7631 | 122.8958 | -123.1201 | -123.0881
996.7656 | 123.1888 | -60.8459 | 62.0224 | -0.40077 | -0.006507 | -0.0074981 | 0.00071144 | 0.062669 | -0.0058639 | 0.067624 | -61.0199 | 62.0453 | -61.1206 | -61.0336 | 61.8851 | 0.13733 | -0.018311 | 0.25635 | 62.0132 | -61.0931 | -0.27466 | 0.022888 | -0.17395 | -0.18768 | -0.13733 | -0.24719 | -0.009155 | 0.10071 | 60.8276 | 61.1023 | 122.731 | 122.8912 | -0.17395 | 122.8592 | 60.9833 | -0.24719 | 122.8912 | -0.17395 | 60.9833 | 122.731 | 122.8592 | -123.143 | -123.1155
997.7656 | 123.111 | -60.8688 | 62.0636 | -0.19478 | -0.007575 | -0.0070709 | 0.003702 | 0.061173 | -0.0037277 | 0.067197 | -61.0062 | 62.0361 | -61.1343 | -61.0886 | 61.8347 | 0.091553 | 0.086975 | 0.20599 | 62.059 | -61.0886 | -0.2655 | -0.027466 | -0.13733 | -0.21973 | -0.22888 | -0.21973 | -0.004578 | 0.12817 | 60.9558 | 61.0748 | 122.7036 | 122.905 | -0.13733 | 122.9279 | 60.9604 | -0.21973 | 122.905 | -0.13733 | 60.9604 | 122.7036 | 122.9279 | -123.1979 | -123.1522
998.7656 | 123.0789 | -60.8734 | 62.027 | -0.2253 | -0.0043708 | -0.0051483 | 0.0028476 | 0.061173 | -0.0058639 | 0.068479 | -60.997 | 62.0499 | -61.0931 | -61.084 | 61.8484 | 0.10986 | 0.09613 | 0.21057 | 62.0453 | -61.1206 | -0.21973 | 0.022888 | -0.1236 | -0.21057 | -0.17853 | -0.24719 | 0.01831 | 0.096131 | 60.9695 | 61.084 | 122.7219 | 122.9233 | -0.1236 | 122.9187 | 60.9833 | -0.24719 | 122.9233 | -0.1236 | 60.9833 | 122.7219 | 122.9187 | -123.1201 | -123.1476
999.7656 | 123.1018 | -60.8917 | 62.0407 | -0.17189 | -0.0056524 | -0.00087594 | 0.0022066 | 0.062241 | -0.0054367 | 0.067624 | -61.0062 | 62.0361 | -61.1298 | -61.0794 | 61.8576 | 0.09613 | 0.082397 | 0.21057 | 62.0728 | -61.1206 | -0.23804 | -0.004577 | -0.11444 | -0.18768 | -0.1831 | -0.22888 | 0.032044 | 0.1236 | 60.9741 | 61.1023 | 122.7493 | 122.9279 | -0.11444 | 122.9645 | 60.9879 | -0.22888 | 122.9279 | -0.11444 | 60.9879 | 122.7493 | 122.9645 | -123.1705 | -123.1613
1000.7656 | 123.143 | -60.8643 | 62.0636 | -0.18715 | -0.0037298 | -0.0057891 | 0.0015658 | 0.063309 | -0.0054367 | 0.067624 | -60.9879 | 62.0453 | -61.084 | -61.0703 | 61.8393 | 0.10529 | 0.073242 | 0.2243 | 62.0453 | -61.1206 | -0.21973 | -0.018311 | -0.1236 | -0.20599 | -0.22431 | -0.25635 | -0.018311 | 0.09613 | 60.9375 | 61.0886 | 122.7036 | 122.9095 | -0.1236 | 122.9095 | 60.9695 | -0.25635 | 122.9095 | -0.1236 | 60.9695 | 122.7036 | 122.9095 | -123.1476 | -123.1842
1001.7656 | 123.1979 | -60.8459 | 62.0178 | -0.17189 | -0.0090704 | -0.0060027 | 0.002634 | 0.062669 | -0.0052231 | 0.066343 | -60.6903 | 62.0682 | -61.1114 | -61.0703 | 61.8851 | 0.13275 | -0.022888 | 0.27924 | 62.0453 | -61.0794 | -0.2655 | 0.050354 | 0.15564 | -0.2243 | -0.13275 | -0.23346 | 0.027466 | 0.42114 | 60.8231 | 61.1252 | 122.731 | 122.9141 | 0.15564 | 122.8912 | 60.9787 | -0.23346 | 122.9141 | 0.15564 | 60.9787 | 122.731 | 122.8912 | -123.1293 | -123.0972
1002.7656 | 123.2254 | -60.8688 | 62.0087 | -2.6057 | -0.004798 | -0.0040801 | 0.0013522 | 0.061387 | -0.0043685 | 0.068479 | -61.0794 | 62.0316 | -61.0931 | -61.0382 | 61.8942 | 0.13733 | -0.027466 | 0.2655 | 62.027 | -61.1069 | -0.22431 | 0.022888 | -0.21057 | -0.16937 | -0.11444 | -0.23804 | 0.018311 | 0.013733 | 60.8414 | 61.1343 | 122.7631 | 122.9004 | -0.21057 | 122.8958 | 61.0062 | -0.23804 | 122.9004 | -0.21057 | 61.0062 | 122.7631 | 122.8958 | -123.1018 | -123.1155
1003.7656 | 123.143 | -60.8734 | 62.0361 | -0.23293 | -0.0073614 | -0.010275 | 0.0049838 | 0.059891 | -0.0050095 | 0.068479 | -60.9924 | 62.0407 | -61.1023 | -61.0794 | 61.8576 | 0.10986 | 0.073242 | 0.20599 | 62.0682 | -61.0794 | -0.22888 | 0.004577 | -0.11902 | -0.20599 | -0.17853 | -0.20599 | 0.032043 | 0.10986 | 60.9467 | 61.0794 | 122.731 | 122.9141 | -0.11902 | 122.9416 | 60.9833 | -0.20599 | 122.9141 | -0.11902 | 60.9833 | 122.731 | 122.9416 | -123.1384 | -123.1155
1004.7656 | 123.056 | -60.9146 | 62.0132 | -0.21004 | -0.0052252 | -0.0053619 | 0.0045566 | 0.061814 | -0.0052231 | 0.068479 | -61.0519 | 62.1048 | -61.1252 | -61.1252 | 61.7981 | 0.050354 | 0.16022 | 0.14191 | 62.0865 | -61.1435 | -0.21057 | 0.091552 | -0.13733 | -0.21057 | -0.21515 | -0.22888 | 0.073242 | 0.073242 | 61.0748 | 61.0565 | 122.7127 | 123.0194 | -0.13733 | 123.0011 | 60.965 | -0.22888 | 123.0194 | -0.13733 | 60.965 | 122.7127 | 123.0011 | -123.1384 | -123.1567
1005.7656 | 123.0606 | -60.9055 | 62.027 | -0.15663 | -0.0043708 | -0.00044854 | 0.0049838 | 0.061387 | -0.0045821 | 0.066984 | -61.0428 | 62.1002 | -61.1526 | -61.1206 | 61.8073 | 0.054932 | 0.13733 | 0.14191 | 62.059 | -61.1343 | -0.24719 | 0.073242 | -0.13733 | -0.21515 | -0.21973 | -0.22888 | 0.032043 | 0.10986 | 61.0428 | 61.0474 | 122.7127 | 123.0057 | -0.13733 | 122.9645 | 60.9604 | -0.22888 | 123.0057 | -0.13733 | 60.9604 | 122.7127 | 122.9645 | -123.1796 | -123.1613
1006.7656 | 123.0606 | -60.9192 | 62.059 | -0.18715 | -0.0045844 | -0.0085663 | 0.0034884 | 0.062241 | -0.0045821 | 0.069761 | -61.0519 | 62.0956 | -61.1206 | -61.1298 | 61.8027 | 0.054932 | 0.14648 | 0.15106 | 62.0819 | -61.1206 | -0.20142 | 0.036621 | -0.13275 | -0.21057 | -0.25635 | -0.20142 | 0.022888 | 0.068664 | 61.0657 | 61.0703 | 122.7219 | 123.0148 | -0.13275 | 123.0011 | 60.9741 | -0.20142 | 123.0148 | -0.13275 | 60.9741 | 122.7219 | 123.0011 | -123.1796 | -123.1796
1007.7656 | 123.0972 | -60.8917 | 62.0544 | -0.21004 | -0.003089 | -0.0051483 | 0.0022066 | 0.062455 | -0.0052231 | 0.067624 | -61.0428 | 62.1048 | -61.1343 | -61.1298 | 61.7935 | 0.059509 | 0.14648 | 0.13275 | 62.1048 | -61.1343 | -0.24261 | 0.050354 | -0.15106 | -0.23804 | -0.26093 | -0.24261 | 0.050354 | 0.091552 | 61.0382 | 61.0245 | 122.6852 | 122.9965 | -0.15106 | 122.9965 | 60.9512 | -0.24261 | 122.9965 | -0.15106 | 60.9512 | 122.6852 | 122.9965 | -123.1888 | -123.1888
1008.7656 | 123.1018 | -60.9055 | 62.0407 | -0.17952 | -0.0052252 | -0.0066437 | 0.00092504 | 0.060532 | -0.0020187 | 0.066129 | -60.997 | 62.0773 | -61.1298 | -61.1114 | 61.8393 | 0.10071 | 0.10071 | 0.19684 | 62.059 | -61.1298 | -0.2243 | 0.036622 | -0.091552 | -0.20599 | -0.20142 | -0.2243 | 0.018311 | 0.13275 | 61.0062 | 61.1023 | 122.7448 | 122.9828 | -0.091552 | 122.9645 | 61.0062 | -0.2243 | 122.9828 | -0.091552 | 61.0062 | 122.7448 | 122.9645 | -123.1705 | -123.1705
1009.7656 | 123.1155 | -60.8826 | 62.027 | -0.23293 | -0.0033026 | -0.0025847 | 0.0011386 | 0.060532 | -0.00095055 | 0.067838 | -61.0153 | 62.0773 | -61.1206 | -61.084 | 61.8576 | 0.10529 | 0.10529 | 0.19684 | 62.0407 | -61.1252 | -0.23804 | 0.050354 | -0.13275 | -0.20142 | -0.16937 | -0.24262 | 0.013732 | 0.10528 | 60.9879 | 61.0794 | 122.7402 | 122.9599 | -0.13275 | 122.9233 | 60.9879 | -0.24262 | 122.9599 | -0.13275 | 60.9879 | 122.7402 | 122.9233 | -123.1476 | -123.1522
1010.7656 | 123.0972 | -60.878 | 62.0407 | -0.18715 | -0.0060798 | -0.0085663 | 0.002634 | 0.060319 | -0.0033005 | 0.070402 | -61.0474 | 62.1048 | -61.1389 | -61.1481 | 61.8027 | 0.054932 | 0.14648 | 0.14191 | 62.0956 | -61.1298 | -0.26093 | 0.064087 | -0.16937 | -0.27008 | -0.23804 | -0.25177 | 0.054932 | 0.091553 | 61.0245 | 61.0199 | 122.6807 | 122.9828 | -0.16937 | 122.9736 | 60.9329 | -0.25177 | 122.9828 | -0.16937 | 60.9329 | 122.6807 | 122.9736 | -123.1796 | -123.1705
1011.7656 | 123.0972 | -60.9009 | 62.0453 | -0.12611 | -0.0035162 | -0.0051483 | 0.004343 | 0.065018 | -0.0028731 | 0.068265 | -61.0245 | 62.1323 | -61.1298 | -61.1298 | 61.7981 | 0.059509 | 0.12817 | 0.15106 | 62.059 | -61.1481 | -0.22888 | 0.086975 | -0.1236 | -0.22888 | -0.24719 | -0.24719 | 0.013733 | 0.10529 | 61.0291 | 61.0519 | 122.699 | 123.0331 | -0.1236 | 122.9599 | 60.9604 | -0.24719 | 123.0331 | -0.1236 | 60.9604 | 122.699 | 122.9599 | -123.175 | -123.1934
1012.7656 | 123.0972 | -60.8917 | 62.0544 | -0.17189 | -0.0043708 | -0.0077117 | 0.0032748 | 0.064591 | -0.00073695 | 0.068052 | -61.0199 | 62.1094 | -61.1389 | -61.1389 | 61.8347 | 0.054932 | 0.13275 | 0.14648 | 62.0956 | -61.1252 | -0.24719 | 0.054932 | -0.12817 | -0.24719 | -0.21973 | -0.23346 | 0.041199 | 0.11902 | 61.0245 | 61.0382 | 122.7264 | 123.0011 | -0.12817 | 122.9874 | 60.9467 | -0.23346 | 123.0011 | -0.12817 | 60.9467 | 122.7264 | 122.9874 | -123.1934 | -123.1796
1013.7656 | 123.0835 | -60.9009 | 62.0682 | -0.12611 | -0.0024482 | -0.0079253 | 0.001993 | 0.062241 | -0.0041549 | 0.065488 | -61.0245 | 62.1323 | -61.1618 | -61.1526 | 61.7935 | 0.059509 | 0.1236 | 0.16022 | 62.0819 | -61.1481 | -0.26092 | 0.064087 | -0.1236 | -0.25177 | -0.27466 | -0.24719 | 0.013733 | 0.13733 | 61.0245 | 61.0611 | 122.6944 | 123.0331 | -0.1236 | 122.9828 | 60.9604 | -0.24719 | 123.0331 | -0.1236 | 60.9604 | 122.6944 | 122.9828 | -123.23 | -123.2162
1014.7656 | 123.111 | -60.9192 | 62.0316 | -0.019302 | -0.0033026 | -0.0060027 | 0.0030612 | 0.065873 | -0.0052231 | 0.067197 | -61.0428 | 62.1048 | -61.1572 | -61.1343 | 61.7889 | 0.045776 | 0.12817 | 0.14648 | 62.0819 | -61.1343 | -0.23804 | 0.073242 | -0.1236 | -0.21515 | -0.24262 | -0.21515 | 0.050354 | 0.11444 | 61.0474 | 61.0657 | 122.7081 | 123.024 | -0.1236 | 123.0011 | 60.965 | -0.21515 | 123.024 | -0.1236 | 60.965 | 122.7081 | 123.0011 | -123.1888 | -123.1659
1015.7656 | 123.0606 | -60.8826 | 62.0361 | -0.13374 | -0.0020208 | -0.0081389 | 0.0028476 | 0.06096 | -0.0020187 | 0.06912 | -61.0565 | 62.1323 | -61.116 | -61.1481 | 61.821 | 0.050354 | 0.15106 | 0.16479 | 62.0728 | -61.1801 | -0.23346 | 0.09613 | -0.17395 | -0.2655 | -0.21515 | -0.29755 | 0.036621 | 0.059509 | 61.0336 | 61.0474 | 122.7036 | 123.0148 | -0.17395 | 122.9553 | 60.9329 | -0.29755 | 123.0148 | -0.17395 | 60.9329 | 122.7036 | 122.9553 | -123.1522 | -123.2162
1016.7656 | 123.0698 | -60.9009 | 62.0682 | -0.2787 | -0.0037298 | -0.0057891 | 0.0011386 | 0.062028 | -0.0039413 | 0.069547 | -61.0474 | 62.1094 | -61.1206 | -61.1298 | 61.8073 | 0.068665 | 0.14648 | 0.15106 | 62.0819 | -61.1252 | -0.21973 | 0.041199 | -0.14648 | -0.22888 | -0.26093 | -0.2243 | 0.013733 | 0.073242 | 61.0474 | 61.0519 | 122.7081 | 123.0103 | -0.14648 | 122.9828 | 60.9695 | -0.2243 | 123.0103 | -0.14648 | 60.9695 | 122.7081 | 122.9828 | -123.1888 | -123.1934
1017.7656 | 123.1064 | -60.9055 | 62.0499 | 0.041733 | -0.0037298 | -0.0045075 | 0.0047702 | 0.06395 | -0.0035141 | 0.068479 | -61.0703 | 62.1048 | -61.1481 | -61.1252 | 61.8164 | 0.073242 | 0.14191 | 0.13275 | 62.0407 | -61.1389 | -0.24261 | 0.054931 | -0.16479 | -0.21973 | -0.23346 | -0.23346 | -0.009156 | 0.07782 | 61.0474 | 61.0382 | 122.7219 | 123.0103 | -0.16479 | 122.9462 | 60.9787 | -0.23346 | 123.0103 | -0.16479 | 60.9787 | 122.7219 | 122.9462 | -123.1979 | -123.1888
1018.7656 | 123.1293 | -60.8963 | 62.0178 | -0.17952 | -0.0035162 | -0.0062163 | 0.0032748 | 0.063523 | -0.0037277 | 0.06677 | -61.0153 | 62.1597 | -61.1343 | -61.0977 | 61.8347 | 0.073242 | 0.07782 | 0.16479 | 62.0682 | -61.1252 | -0.23804 | 0.14191 | -0.11902 | -0.20142 | -0.18311 | -0.22888 | 0.050354 | 0.11902 | 60.9741 | 61.0611 | 122.731 | 123.056 | -0.11902 | 122.9645 | 60.9695 | -0.22888 | 123.056 | -0.11902 | 60.9695 | 122.731 | 122.9645 | -123.1522 | -123.143
1019.7656 | 123.1064 | -60.9055 | 62.0499 | -0.15663 | -0.0033026 | -0.0057891 | 0.005411 | 0.0663 | -0.0033005 | 0.069547 | -61.0245 | 62.1643 | -61.1252 | -61.1023 | 61.821 | 0.07782 | 0.10529 | 0.17395 | 62.0499 | -61.1572 | -0.21973 | 0.11444 | -0.11902 | -0.19684 | -0.22888 | -0.25177 | 0 | 0.10071 | 61.0107 | 61.0794 | 122.7264 | 123.0698 | -0.11902 | 122.9553 | 60.9833 | -0.25177 | 123.0698 | -0.11902 | 60.9833 | 122.7264 | 122.9553 | -123.175 | -123.2071
1020.7656 | 123.143 | -60.8963 | 62.0453 | -0.14137 | -0.0073614 | -0.0034393 | 0.0049838 | 0.065018 | -0.0037277 | 0.068906 | -61.0199 | 62.1597 | -61.1526 | -61.1114 | 61.8347 | 0.082397 | 0.091553 | 0.16937 | 62.0499 | -61.1801 | -0.25635 | 0.11444 | -0.1236 | -0.21515 | -0.21057 | -0.28381 | 0.004578 | 0.13275 | 60.9879 | 61.0657 | 122.731 | 123.056 | -0.1236 | 122.9462 | 60.9787 | -0.28381 | 123.056 | -0.1236 | 60.9787 | 122.731 | 122.9462 | -123.1979 | -123.2254
1021.7656 | 123.1018 | -60.8826 | 62.0407 | -0.14137 | -0.0033026 | -0.0062163 | 0.004343 | 0.063523 | -0.0035141 | 0.06912 | -61.0153 | 62.1414 | -61.1298 | -61.116 | 61.8301 | 0.086975 | 0.10071 | 0.17853 | 62.0544 | -61.1618 | -0.24719 | 0.10071 | -0.13275 | -0.23346 | -0.21057 | -0.27924 | 0.013733 | 0.11444 | 60.9833 | 61.0611 | 122.7127 | 123.024 | -0.13275 | 122.937 | 60.9695 | -0.27924 | 123.024 | -0.13275 | 60.9695 | 122.7127 | 122.937 | -123.1705 | -123.2025
1022.7656 | 123.0743 | -60.9055 | 62.0499 | -0.17189 | -0.0037298 | -0.0070709 | 0.0013522 | 0.062028 | -0.0037277 | 0.068265 | -60.8688 | 62.1643 | -61.1069 | -61.1618 | 61.7844 | 0.050354 | 0.14648 | 0.15106 | 62.0819 | -61.1481 | -0.20142 | 0.11444 | 0.036622 | -0.25635 | -0.2655 | -0.24261 | 0.032043 | 0.23804 | 61.0519 | 61.0565 | 122.6898 | 123.0698 | 0.036622 | 122.9874 | 60.9558 | -0.24261 | 123.0698 | 0.036622 | 60.9558 | 122.6898 | 122.9874 | -123.1567 | -123.1979
1023.7656 | 123.0743 | -60.9055 | 62.0407 | -0.19478 | -0.0039434 | -0.0051483 | 0.0028476 | 0.065232 | -0.0043685 | 0.068906 | -61.1298 | 62.1506 | -61.1298 | -61.1664 | 61.7752 | 0.041199 | 0.13733 | 0.11902 | 62.0682 | -61.171 | -0.2243 | 0.10986 | -0.2243 | -0.26093 | -0.2655 | -0.2655 | 0.027466 | 0 | 61.0428 | 61.0245 | 122.6807 | 123.056 | -0.2243 | 122.9736 | 60.9467 | -0.2655 | 123.056 | -0.2243 | 60.9467 | 122.6807 | 122.9736 | -123.1705 | -123.2117
1024.7656 | 123.1064 | -60.9055 | 62.059 | -0.17189 | -0.0041572 | -0.0038665 | 0.0022066 | 0.063309 | -0.0050095 | 0.068906 | -61.0336 | 62.1231 | -61.1389 | -61.1389 | 61.8256 | 0.064087 | 0.10529 | 0.16937 | 62.0956 | -61.1481 | -0.23346 | 0.064087 | -0.12817 | -0.23346 | -0.23346 | -0.24261 | 0.036621 | 0.10529 | 61.0107 | 61.0748 | 122.731 | 123.0286 | -0.12817 | 123.0011 | 60.9695 | -0.24261 | 123.0286 | -0.12817 | 60.9695 | 122.731 | 123.0011 | -123.1979 | -123.2071
1025.7812 | 123.1201 | -60.9283 | 62.027 | -0.44655 | -0.0018072 | -0.0027985 | 0.0056246 | 0.065018 | -0.0037277 | 0.069761 | -61.0153 | 62.1185 | -61.1618 | -61.1069 | 61.8118 | 0.064087 | 0.009155 | 0.14191 | 62.059 | -61.1618 | -0.23346 | 0.091552 | -0.086975 | -0.17853 | -0.21515 | -0.23346 | 0.032043 | 0.14648 | 60.9375 | 61.0703 | 122.7402 | 123.0469 | -0.086975 | 122.9874 | 60.9924 | -0.23346 | 123.0469 | -0.086975 | 60.9924 | 122.7402 | 122.9874 | -123.1888 | -123.1888
1026.7656 | 123.1522 | -60.8826 | 62.0316 | -0.087967 | -0.00031179 | -0.0023711 | 0.0024202 | 0.068436 | -0.0039413 | 0.070188 | -60.997 | 62.1323 | -61.1252 | -61.1069 | 61.853 | 0.07782 | 0.054932 | 0.16022 | 62.0682 | -61.1801 | -0.24262 | 0.10071 | -0.11444 | -0.22431 | -0.17853 | -0.29755 | 0.036621 | 0.12817 | 60.9375 | 61.0428 | 122.7356 | 123.0148 | -0.11444 | 122.9507 | 60.9604 | -0.29755 | 123.0148 | -0.11444 | 60.9604 | 122.7356 | 122.9507 | -123.1567 | -123.2117
1027.7656 | 123.1293 | -60.9146 | 62.0453 | -0.087967 | -0.0035162 | -0.0010895 | 0.004343 | 0.064805 | -0.0024459 | 0.069761 | -61.0016 | 62.1323 | -61.1298 | -61.0977 | 61.8301 | 0.064087 | 0.054932 | 0.16937 | 62.0865 | -61.1572 | -0.21515 | 0.086975 | -0.086975 | -0.18311 | -0.21515 | -0.24262 | 0.041199 | 0.12817 | 60.9695 | 61.084 | 122.7448 | 123.0469 | -0.086975 | 123.0011 | 60.9787 | -0.24262 | 123.0469 | -0.086975 | 60.9787 | 122.7448 | 123.0011 | -123.175 | -123.2025
1028.7656 | 123.1247 | -60.9192 | 62.0316 | -0.065079 | -0.0028754 | -0.0057891 | 0.0030612 | 0.066941 | -0.0054367 | 0.06912 | -60.9879 | 62.146 | -61.1389 | -61.1114 | 61.8347 | 0.07782 | 0.050354 | 0.16937 | 62.0773 | -61.1481 | -0.21973 | 0.11444 | -0.068665 | -0.19226 | -0.19684 | -0.22888 | 0.045777 | 0.15106 | 60.9695 | 61.0886 | 122.7539 | 123.0652 | -0.068665 | 122.9965 | 60.997 | -0.22888 | 123.0652 | -0.068665 | 60.997 | 122.7539 | 122.9965 | -123.1705 | -123.1796
1029.7656 | 123.1064 | -60.8917 | 62.0453 | -0.14137 | -0.003089 | 0.00040586 | -0.00014316 | 0.066514 | -0.0047957 | 0.068906 | -61.0474 | 62.1414 | -61.1435 | -61.1298 | 61.8118 | 0.068665 | 0.11902 | 0.16479 | 62.1048 | -61.1664 | -0.25177 | 0.09613 | -0.15564 | -0.23804 | -0.23346 | -0.27466 | 0.059509 | 0.096131 | 61.0107 | 61.0565 | 122.7036 | 123.0331 | -0.15564 | 122.9965 | 60.9604 | -0.27466 | 123.0331 | -0.15564 | 60.9604 | 122.7036 | 122.9965 | -123.1888 | -123.2117
1030.7656 | 123.0927 | -60.9055 | 62.0224 | -0.11848 | -0.0041572 | -0.0025847 | 0.002634 | 0.062669 | -0.0054367 | 0.069333 | -61.0519 | 62.1414 | -61.1481 | -61.1572 | 61.8073 | 0.054932 | 0.13275 | 0.14191 | 62.0819 | -61.1572 | -0.24261 | 0.11902 | -0.14648 | -0.25177 | -0.21515 | -0.25177 | 0.059509 | 0.09613 | 61.0382 | 61.0474 | 122.7127 | 123.0469 | -0.14648 | 122.9874 | 60.9604 | -0.25177 | 123.0469 | -0.14648 | 60.9604 | 122.7127 | 122.9874 | -123.1705 | -123.1796
1031.7656 | 123.1293 | -60.8871 | 62.0041 | -0.080337 | -0.0035162 | -0.0030121 | 0.0034884 | 0.065446 | -0.0037277 | 0.068052 | -61.0107 | 62.1323 | -61.1389 | -61.1069 | 61.8301 | 0.082397 | 0.059509 | 0.17853 | 62.0499 | -61.1893 | -0.25177 | 0.12817 | -0.1236 | -0.21973 | -0.17395 | -0.30212 | 0.045777 | 0.12817 | 60.9467 | 61.0657 | 122.7173 | 123.0194 | -0.1236 | 122.937 | 60.9695 | -0.30212 | 123.0194 | -0.1236 | 60.9695 | 122.7173 | 122.937 | -123.143 | -123.1934
1032.7656 | 123.0835 | -60.9146 | 62.027 | -0.026932 | -0.003089 | -0.0057891 | 0.003702 | 0.066087 | -0.00052335 | 0.069974 | -60.9833 | 62.1185 | -61.1572 | -61.1069 | 61.8256 | 0.064087 | 0.036621 | 0.15106 | 62.0682 | -61.171 | -0.24262 | 0.091552 | -0.068664 | -0.19226 | -0.20142 | -0.25635 | 0.041198 | 0.17395 | 60.9512 | 61.0657 | 122.7402 | 123.0331 | -0.068664 | 122.9828 | 60.9787 | -0.25635 | 123.0331 | -0.068664 | 60.9787 | 122.7402 | 122.9828 | -123.1842 | -123.1979
1033.7656 | 123.143 | -60.9192 | 62.0407 | -0.019302 | -0.0035162 | -0.0055755 | 0.003702 | 0.066087 | -0.0035141 | 0.069761 | -60.9924 | 62.1323 | -61.1481 | -61.0931 | 61.8164 | 0.059509 | 0.032043 | 0.16479 | 62.0773 | -61.1938 | -0.22888 | 0.091553 | -0.073243 | -0.17395 | -0.2243 | -0.27466 | 0.036622 | 0.15564 | 60.9512 | 61.084 | 122.7356 | 123.0515 | -0.073243 | 122.9965 | 60.9787 | -0.27466 | 123.0515 | -0.073243 | 60.9787 | 122.7356 | 122.9965 | -123.1888 | -123.2346
1034.7656 | 123.143 | -60.8871 | 62.0316 | -0.04219 | -0.0028754 | 0.00083306 | 0.0058382 | 0.0663 | -0.0033005 | 0.070188 | -60.9787 | 62.1506 | -61.1206 | -61.0931 | 61.8439 | 0.082397 | 0.018311 | 0.14648 | 62.0728 | -61.1801 | -0.23346 | 0.11902 | -0.091553 | -0.20599 | -0.18768 | -0.29297 | 0.041199 | 0.14191 | 60.9055 | 61.0336 | 122.731 | 123.0377 | -0.091553 | 122.9599 | 60.9695 | -0.29297 | 123.0377 | -0.091553 | 60.9695 | 122.731 | 122.9599 | -123.1522 | -123.2117
1035.7656 | 123.1384 | -60.9146 | 62.0178 | -0.04219 | -0.0015936 | -0.0055755 | 0.002634 | 0.064591 | -0.0020187 | 0.067624 | -60.9741 | 62.1277 | -61.1481 | -61.0977 | 61.8301 | 0.059509 | 0.036621 | 0.16937 | 62.0956 | -61.1526 | -0.23346 | 0.10986 | -0.059509 | -0.18311 | -0.18768 | -0.23804 | 0.07782 | 0.17395 | 60.9512 | 61.084 | 122.7448 | 123.0423 | -0.059509 | 123.0103 | 60.9741 | -0.23804 | 123.0423 | -0.059509 | 60.9741 | 122.7448 | 123.0103 | -123.1659 | -123.1705
1036.7656 | 123.1338 | -60.8963 | 62.0361 | -0.149 | -0.0037298 | -0.0068573 | 0.0017794 | 0.065873 | -0.0026595 | 0.069333 | -61.0062 | 62.1643 | -61.1343 | -61.1114 | 61.8301 | 0.07782 | 0.10529 | 0.16022 | 62.1048 | -61.1664 | -0.23804 | 0.12817 | -0.10986 | -0.21515 | -0.20599 | -0.27008 | 0.068664 | 0.12817 | 61.0016 | 61.0565 | 122.7264 | 123.0606 | -0.10986 | 123.0011 | 60.9741 | -0.27008 | 123.0606 | -0.10986 | 60.9741 | 122.7264 | 123.0011 | -123.1705 | -123.2025
1037.7656 | 123.1293 | -60.8871 | 62.0132 | -0.057449 | -0.00138 | -0.0040801 | 0.0047702 | 0.065232 | -0.0020187 | 0.067411 | -61.0062 | 62.1094 | -61.1435 | -61.0931 | 61.8301 | 0.082397 | 0.041199 | 0.16937 | 62.0316 | -61.2076 | -0.25635 | 0.09613 | -0.11902 | -0.20599 | -0.18311 | -0.32043 | 0.01831 | 0.13733 | 60.9283 | 61.0565 | 122.7173 | 122.9965 | -0.11902 | 122.9187 | 60.9695 | -0.32043 | 122.9965 | -0.11902 | 60.9695 | 122.7173 | 122.9187 | -123.1567 | -123.2208
1038.7656 | 123.1293 | -60.8917 | 62.0087 | 0.026474 | 0.00075621 | -0.0081389 | 0.0041292 | 0.067368 | -0.0020187 | 0.069761 | -61.0336 | 62.1185 | -61.1618 | -61.1481 | 61.8256 | 0.054932 | 0.036621 | 0.14191 | 62.059 | -61.1755 | -0.27008 | 0.10986 | -0.14191 | -0.25635 | -0.18311 | -0.28381 | 0.050354 | 0.12817 | 60.9283 | 61.0336 | 122.7173 | 123.0103 | -0.14191 | 122.9507 | 60.9467 | -0.28381 | 123.0103 | -0.14191 | 60.9467 | 122.7173 | 122.9507 | -123.1705 | -123.1842
1039.7656 | 123.1018 | -60.9009 | 62.0407 | 0.011215 | -0.00052559 | -0.0030121 | 0.001993 | 0.065873 | -0.0075729 | 0.070615 | -60.9833 | 62.1506 | -61.1389 | -61.1023 | 61.8164 | 0.059509 | 0.013733 | 0.15106 | 62.0773 | -61.1847 | -0.23804 | 0.10986 | -0.082397 | -0.20142 | -0.2243 | -0.28381 | 0.036622 | 0.15564 | 60.9146 | 61.0519 | 122.7173 | 123.0515 | -0.082397 | 122.9782 | 60.9604 | -0.28381 | 123.0515 | -0.082397 | 60.9604 | 122.7173 | 122.9782 | -123.1796 | -123.2254
1040.7656 | 123.1201 | -60.9055 | 62.0178 | -0.04982 | -0.0050116 | -0.0025847 | 0.0011386 | 0.064805 | 0.00097205 | 0.06912 | -60.9833 | 62.1597 | -61.1206 | -61.1481 | 61.8393 | 0.064087 | 0.054932 | 0.16479 | 62.0865 | -61.1847 | -0.21515 | 0.14191 | -0.077819 | -0.24261 | -0.17853 | -0.27923 | 0.068665 | 0.13733 | 60.9604 | 61.0703 | 122.7448 | 123.0652 | -0.077819 | 122.9919 | 60.9695 | -0.27923 | 123.0652 | -0.077819 | 60.9695 | 122.7448 | 122.9919 | -123.1384 | -123.2025
1041.7656 | 123.1064 | -60.91 | 62.027 | -0.04219 | -0.00138 | -0.0042937 | 0.005411 | 0.065446 | -0.0037277 | 0.070402 | -60.997 | 62.1277 | -61.1343 | -61.1252 | 61.8622 | -0.013733 | 0.036621 | 0.16479 | 62.0361 | -61.1847 | -0.2243 | 0.10071 | -0.086975 | -0.21515 | -0.16479 | -0.27466 | 0.009155 | 0.13733 | 60.9467 | 61.0748 | 122.7722 | 123.0377 | -0.086975 | 122.9462 | 60.8963 | -0.27466 | 123.0377 | -0.086975 | 60.8963 | 122.7722 | 122.9462 | -123.1613 | -123.2117
1042.7656 | 123.0927 | -60.8917 | 62.0224 | -0.04982 | -0.0024482 | -0.0036529 | 0.002634 | 0.067155 | -0.0052231 | 0.06912 | -60.9879 | 62.1414 | -61.1526 | -61.116 | 61.821 | 0.073242 | 0.009155 | 0.15564 | 62.0728 | -61.1618 | -0.26092 | 0.11902 | -0.09613 | -0.2243 | -0.20142 | -0.27008 | 0.050354 | 0.16479 | 60.9009 | 61.0474 | 122.7127 | 123.0331 | -0.09613 | 122.9645 | 60.965 | -0.27008 | 123.0331 | -0.09613 | 60.965 | 122.7127 | 122.9645 | -123.175 | -123.1842
1043.7656 | 123.1201 | -60.8917 | 62.0316 | -0.14137 | -0.0011664 | -0.0042937 | 0.0034884 | 0.064805 | -0.0054367 | 0.067411 | -61.0291 | 62.1368 | -61.1618 | -61.116 | 61.8118 | 0.068665 | 0.086975 | 0.16479 | 62.1185 | -61.1664 | -0.27008 | 0.10529 | -0.13733 | -0.2243 | -0.21973 | -0.27466 | 0.086975 | 0.13275 | 60.9787 | 61.0565 | 122.7036 | 123.0286 | -0.13733 | 123.0103 | 60.9604 | -0.27466 | 123.0286 | -0.13733 | 60.9604 | 122.7036 | 123.0103 | -123.1934 | -123.1979
1044.7656 | 123.1338 | -60.9055 | 62.0407 | -0.057449 | -0.0024482 | -0.0042937 | 0.0011386 | 0.065232 | -0.0018051 | 0.07147 | -60.9833 | 62.1643 | -61.1343 | -61.1298 | 61.821 | 0.07782 | 0.041199 | 0.16479 | 62.0728 | -61.1893 | -0.22888 | 0.1236 | -0.077819 | -0.2243 | -0.21973 | -0.28381 | 0.032044 | 0.15106 | 60.9467 | 61.0703 | 122.7264 | 123.0698 | -0.077819 | 122.9782 | 60.9833 | -0.28381 | 123.0698 | -0.077819 | 60.9833 | 122.7264 | 122.9782 | -123.175 | -123.23
1045.7656 | 123.1018 | -60.9055 | 62.0132 | -0.33974 | -0.0015936 | -0.00023494 | 0.0056246 | 0.064378 | -0.0013779 | 0.068693 | -60.9833 | 62.146 | -61.1343 | -61.1298 | 61.7981 | 0.022888 | 0.022888 | 0.1236 | 62.0407 | -61.2076 | -0.22888 | 0.13275 | -0.077819 | -0.2243 | -0.21515 | -0.30212 | 0.027465 | 0.15106 | 60.9283 | 61.0291 | 122.7036 | 123.0515 | -0.077819 | 122.9462 | 60.9283 | -0.30212 | 123.0515 | -0.077819 | 60.9283 | 122.7036 | 122.9462 | -123.1476 | -123.2208
1046.7656 | 123.1338 | -60.878 | 62.0178 | 1.2853 | -0.0043708 | -0.0030121 | 0.0049838 | 0.064591 | -0.0045821 | 0.069333 | -60.9741 | 62.0865 | -61.1572 | -61.1298 | 61.8164 | 0.050354 | 0.022888 | 0.16022 | 62.1048 | -61.1984 | -0.27924 | 0.068665 | -0.09613 | -0.25177 | -0.20142 | -0.32043 | 0.086975 | 0.18311 | 60.9009 | 61.0382 | 122.6944 | 122.9645 | -0.09613 | 122.9828 | 60.9283 | -0.32043 | 122.9645 | -0.09613 | 60.9283 | 122.6944 | 122.9828 | -123.175 | -123.2162
1047.7656 | 123.1064 | -60.8871 | 62.0132 | 0.011215 | -0.0054388 | -0.0042937 | 0.0039156 | 0.064805 | -0.0020187 | 0.069761 | -60.9833 | 62.1414 | -61.1618 | -61.1114 | 61.8164 | 0.054932 | 0.022888 | 0.14648 | 62.0911 | -61.1801 | -0.27466 | 0.12817 | -0.09613 | -0.2243 | -0.19684 | -0.29297 | 0.077819 | 0.17853 | 60.91 | 61.0336 | 122.7036 | 123.0286 | -0.09613 | 122.9782 | 60.9421 | -0.29297 | 123.0286 | -0.09613 | 60.9421 | 122.7036 | 122.9782 | -123.175 | -123.1934
1048.7656 | 123.1064 | -60.9009 | 62.0407 | 0.018845 | -0.0028754 | -0.0034393 | 0.0015658 | 0.066087 | -0.0011643 | 0.066984 | -60.9924 | 62.1552 | -61.1252 | -61.1069 | 61.7935 | 0.041199 | 0.032043 | 0.14191 | 62.0911 | -61.1938 | -0.2243 | 0.11444 | -0.091553 | -0.20599 | -0.24719 | -0.29297 | 0.050354 | 0.13275 | 60.9329 | 61.0428 | 122.6944 | 123.056 | -0.091553 | 122.9919 | 60.9421 | -0.29297 | 123.056 | -0.091553 | 60.9421 | 122.6944 | 122.9919 | -123.1659 | -123.2346
1049.7656 | 123.1293 | -60.8871 | 62.0499 | -0.087967 | -0.0026618 | -2.1336e-05 | 0.003702 | 0.062455 | -0.0035141 | 0.070188 | -61.0107 | 62.1552 | -61.1435 | -61.1298 | 61.8256 | 0.07782 | 0.082397 | 0.16479 | 62.059 | -61.1755 | -0.25635 | 0.10528 | -0.1236 | -0.24262 | -0.2243 | -0.28839 | 0.009155 | 0.13275 | 60.9695 | 61.0519 | 122.7127 | 123.0423 | -0.1236 | 122.9462 | 60.965 | -0.28839 | 123.0423 | -0.1236 | 60.965 | 122.7127 | 122.9462 | -123.1934 | -123.2254
1050.7656 | 123.1293 | -60.9055 | 62.0178 | -0.10323 | -0.004798 | -0.0040801 | 0.0034884 | 0.066727 | -0.0043685 | 0.06912 | -61.0062 | 62.146 | -61.1389 | -61.1114 | 61.8301 | 0.073242 | 0.082397 | 0.16479 | 62.0865 | -61.1664 | -0.23346 | 0.12817 | -0.10071 | -0.20599 | -0.18768 | -0.26093 | 0.068665 | 0.13275 | 60.9879 | 61.0703 | 122.7356 | 123.0515 | -0.10071 | 122.9919 | 60.9787 | -0.26093 | 123.0515 | -0.10071 | 60.9787 | 122.7356 | 122.9919 | -123.1567 | -123.1842
1051.7656 | 123.1064 | -60.9055 | 62.0132 | -0.065079 | -0.0026618 | -0.0066437 | 0.003702 | 0.065659 | -0.0022323 | 0.06912 | -61.0016 | 62.1323 | -61.1481 | -61.0977 | 61.8256 | 0.064087 | 0.022888 | 0.16479 | 62.0499 | -61.1893 | -0.24261 | 0.11902 | -0.09613 | -0.19226 | -0.18768 | -0.28381 | 0.036621 | 0.14648 | 60.9283 | 61.0703 | 122.731 | 123.0377 | -0.09613 | 122.9553 | 60.9695 | -0.28381 | 123.0377 | -0.09613 | 60.9695 | 122.731 | 122.9553 | -123.1613 | -123.2025
1052.7656 | 123.1293 | -60.9009 | 61.9904 | 0.018845 | -0.0024482 | -0.0032257 | 0.0051974 | 0.064591 | -0.0041549 | 0.070402 | -61.0062 | 62.1414 | -61.1114 | -61.1298 | 61.8073 | 0.022888 | 0.018311 | 0.1236 | 62.0682 | -61.1893 | -0.21057 | 0.15106 | -0.10529 | -0.22888 | -0.1831 | -0.28839 | 0.07782 | 0.10528 | 60.9192 | 61.0245 | 122.7081 | 123.0423 | -0.10529 | 122.9691 | 60.9238 | -0.28839 | 123.0423 | -0.10529 | 60.9238 | 122.7081 | 122.9691 | -123.1018 | -123.1796
1053.7656 | 123.0835 | -60.9009 | 62.0224 | -0.30159 | -0.0028754 | -0.0085663 | 0.002634 | 0.066941 | -0.0028731 | 0.069547 | -61.0153 | 62.1323 | -61.1481 | -61.1252 | 61.7981 | 0.050354 | 0.022888 | 0.1236 | 62.0865 | -61.1801 | -0.24719 | 0.10986 | -0.11444 | -0.2243 | -0.2243 | -0.27924 | 0.064087 | 0.13275 | 60.9238 | 61.0245 | 122.699 | 123.0331 | -0.11444 | 122.9874 | 60.9512 | -0.27924 | 123.0331 | -0.11444 | 60.9512 | 122.699 | 122.9874 | -123.1705 | -123.2025
1054.7656 | 123.1247 | -60.8826 | 62.0224 | -0.011673 | -0.0018072 | -0.0015167 | 0.003702 | 0.067155 | -0.0041549 | 0.066556 | -61.0474 | 62.1048 | -61.1343 | -61.1252 | 61.8073 | 0.059509 | 0.032043 | 0.14191 | 62.0865 | -61.171 | -0.25177 | 0.082397 | -0.16479 | -0.24262 | -0.21515 | -0.28839 | 0.064087 | 0.086975 | 60.9146 | 61.0245 | 122.6898 | 122.9874 | -0.16479 | 122.9691 | 60.9421 | -0.28839 | 122.9874 | -0.16479 | 60.9421 | 122.6898 | 122.9691 | -123.1567 | -123.1934
1055.7656 | 123.1338 | -60.9146 | 62.0316 | 0.041733 | -0.0035162 | -0.0027985 | 0.003702 | 0.066514 | -0.0030869 | 0.06912 | -60.9924 | 62.1368 | -61.1664 | -61.0977 | 61.8347 | 0.041199 | 0.013733 | 0.14191 | 62.1002 | -61.1755 | -0.25177 | 0.10529 | -0.07782 | -0.18311 | -0.19684 | -0.26093 | 0.068665 | 0.17395 | 60.9283 | 61.0565 | 122.7493 | 123.0515 | -0.07782 | 123.0148 | 60.9558 | -0.26093 | 123.0515 | -0.07782 | 60.9558 | 122.7493 | 123.0148 | -123.1979 | -123.2071
1056.7656 | 123.1522 | -60.878 | 62.0499 | -0.080337 | -0.0028754 | -0.0060027 | 0.005411 | 0.0663 | -0.0052231 | 0.070188 | -60.9924 | 62.1231 | -61.1435 | -61.1206 | 61.8073 | 0.068665 | 0.064087 | 0.17395 | 62.0911 | -61.1618 | -0.2655 | 0.073242 | -0.11444 | -0.24261 | -0.24262 | -0.28381 | 0.041198 | 0.15106 | 60.9421 | 61.0519 | 122.6852 | 123.0011 | -0.11444 | 122.9691 | 60.9467 | -0.28381 | 123.0011 | -0.11444 | 60.9467 | 122.6852 | 122.9691 | -123.1934 | -123.2117
1057.7656 | 123.1338 | -60.8734 | 62.0178 | -0.10323 | -0.0026618 | -0.0030121 | 0.0024202 | 0.065873 | -0.0035141 | 0.067624 | -60.9879 | 62.1414 | -61.1435 | -61.1069 | 61.8393 | 0.082397 | 0.059509 | 0.16022 | 62.1094 | -61.1801 | -0.27008 | 0.1236 | -0.11444 | -0.23346 | -0.17853 | -0.3067 | 0.091553 | 0.15564 | 60.9329 | 61.0336 | 122.7127 | 123.0148 | -0.11444 | 122.9828 | 60.9558 | -0.3067 | 123.0148 | -0.11444 | 60.9558 | 122.7127 | 122.9828 | -123.1613 | -123.1979
1058.7656 | 123.0972 | -60.91 | 62.0224 | -0.080337 | -0.0011664 | -0.0077117 | 0.005411 | 0.063737 | -0.0015915 | 0.070188 | -60.9879 | 62.1414 | -61.1618 | -61.116 | 61.8164 | 0.068665 | 0.022888 | 0.15564 | 62.0911 | -61.1847 | -0.25177 | 0.11902 | -0.07782 | -0.20599 | -0.20599 | -0.27466 | 0.068664 | 0.17395 | 60.9329 | 61.0657 | 122.7264 | 123.0515 | -0.07782 | 123.0011 | 60.9787 | -0.27466 | 123.0515 | -0.07782 | 60.9787 | 122.7264 | 123.0011 | -123.1842 | -123.2071
1059.7656 | 123.0698 | -60.9146 | 61.9949 | 0.041733 | -0.00052559 | -0.0030121 | 0.0060518 | 0.062669 | -0.0028731 | 0.068052 | -61.0153 | 62.1552 | -61.1618 | -61.1252 | 61.8027 | 0.018311 | 0.013733 | 0.11444 | 62.0499 | -61.1893 | -0.24719 | 0.16022 | -0.10071 | -0.21057 | -0.19226 | -0.27466 | 0.054932 | 0.14648 | 60.9283 | 61.0291 | 122.7173 | 123.0698 | -0.10071 | 122.9645 | 60.9329 | -0.27466 | 123.0698 | -0.10071 | 60.9329 | 122.7173 | 122.9645 | -123.1567 | -123.1842
1060.7656 | 123.111 | -60.9055 | 62.0178 | -0.019302 | -0.0024482 | -0.0060027 | 0.0056246 | 0.065659 | -0.0039413 | 0.068906 | -60.997 | 62.1368 | -61.1526 | -61.1298 | 61.8027 | 0.027466 | 0.032043 | 0.11902 | 62.0636 | -61.1938 | -0.24719 | 0.11902 | -0.091552 | -0.2243 | -0.21515 | -0.28839 | 0.045777 | 0.15564 | 60.9375 | 61.0245 | 122.7081 | 123.0423 | -0.091552 | 122.9691 | 60.9329 | -0.28839 | 123.0423 | -0.091552 | 60.9329 | 122.7081 | 122.9691 | -123.1705 | -123.2117
1061.7656 | 123.1155 | -60.8917 | 62.027 | 0.11803 | -0.0028754 | -0.0017303 | 0.0058382 | 0.0663 | -0.0043685 | 0.068693 | -60.9833 | 62.1368 | -61.1435 | -61.1343 | 61.7935 | 0.041199 | 0.032043 | 0.11902 | 62.0956 | -61.1847 | -0.25177 | 0.10986 | -0.091552 | -0.24261 | -0.23346 | -0.29297 | 0.068664 | 0.16022 | 60.9238 | 61.0107 | 122.6852 | 123.0286 | -0.091552 | 122.9874 | 60.9329 | -0.29297 | 123.0286 | -0.091552 | 60.9329 | 122.6852 | 122.9874 | -123.1705 | -123.2117
1062.7656 | 123.1338 | -60.8963 | 62.0361 | -0.33974 | -0.00073919 | -0.0038665 | 0.005411 | 0.0663 | -0.0047957 | 0.068906 | -60.9879 | 62.1185 | -61.1526 | -61.1114 | 61.7935 | 0.050354 | 0.027466 | 0.13275 | 62.0773 | -61.171 | -0.25635 | 0.082397 | -0.091553 | -0.21515 | -0.24262 | -0.27466 | 0.041199 | 0.16479 | 60.9238 | 61.0291 | 122.6898 | 123.0148 | -0.091553 | 122.9736 | 60.9467 | -0.27466 | 123.0148 | -0.091553 | 60.9467 | 122.6898 | 122.9736 | -123.1888 | -123.2071
1063.7656 | 123.1567 | -60.8734 | 62.0132 | 0.011215 | -0.0028754 | -0.0049347 | 0.0045566 | 0.065232 | -0.0039413 | 0.070188 | -60.9924 | 62.1689 | -61.1526 | -61.116 | 61.8256 | 0.07782 | 0.050354 | 0.16022 | 62.0728 | -61.1847 | -0.27924 | 0.15564 | -0.11902 | -0.24262 | -0.18768 | -0.31128 | 0.059509 | 0.16022 | 60.9238 | 61.0336 | 122.699 | 123.0423 | -0.11902 | 122.9462 | 60.9512 | -0.31128 | 123.0423 | -0.11902 | 60.9512 | 122.699 | 122.9462 | -123.1659 | -123.1979
1064.7656 | 123.1384 | -60.9055 | 62.0178 | -0.0040434 | -0.0026618 | -0.0055755 | 0.0041292 | 0.066514 | -0.0043685 | 0.066984 | -60.9879 | 62.1552 | -61.1435 | -61.1206 | 61.8484 | 0.086975 | 0.050354 | 0.17395 | 62.1048 | -61.1847 | -0.23804 | 0.13733 | -0.082397 | -0.21515 | -0.16937 | -0.27923 | 0.086975 | 0.15564 | 60.9558 | 61.0794 | 122.7539 | 123.0606 | -0.082397 | 123.0103 | 60.9924 | -0.27923 | 123.0606 | -0.082397 | 60.9924 | 122.7539 | 123.0103 | -123.1613 | -123.2025
1065.7656 | 123.1155 | -60.9283 | 62.0361 | -0.04982 | -0.0056524 | -0.0049347 | 0.005411 | 0.066514 | -0.0030869 | 0.069974 | -60.9787 | 62.1323 | -61.1572 | -61.1801 | 61.6974 | 0.009155 | 0.041199 | 0.14191 | 62.1002 | -61.1893 | -0.22888 | 0.09613 | -0.050354 | -0.25177 | -0.33875 | -0.26093 | 0.064087 | 0.17853 | 60.9695 | 61.0703 | 122.6257 | 123.0606 | -0.050354 | 123.0286 | 60.9375 | -0.26093 | 123.0606 | -0.050354 | 60.9375 | 122.6257 | 123.0286 | -123.1934 | -123.2254
1066.7656 | 123.0743 | -60.8917 | 61.9995 | -0.034561 | -0.0020208 | -0.0051483 | 0.0047702 | 0.066941 | -0.00073695 | 0.069761 | -61.0016 | 62.1323 | -61.1389 | -61.1435 | 61.7752 | 0.013733 | 0.018311 | 0.086975 | 62.0819 | -61.1938 | -0.24719 | 0.13275 | -0.10986 | -0.25177 | -0.2243 | -0.30212 | 0.082397 | 0.13733 | 60.91 | 60.9787 | 122.6669 | 123.024 | -0.10986 | 122.9736 | 60.9055 | -0.30212 | 123.024 | -0.10986 | 60.9055 | 122.6669 | 122.9736 | -123.1384 | -123.1934
1067.7656 | 123.0927 | -60.9146 | 62.0316 | 0.018845 | -0.0043708 | -0.00066214 | 0.004343 | 0.065018 | -0.0026595 | 0.069333 | -60.9833 | 62.146 | -61.1572 | -61.1526 | 61.7981 | 0.032043 | 0.027466 | 0.11444 | 62.0911 | -61.1938 | -0.24262 | 0.11444 | -0.068664 | -0.23804 | -0.23346 | -0.27924 | 0.059509 | 0.17395 | 60.9421 | 61.0291 | 122.7127 | 123.0606 | -0.068664 | 123.0057 | 60.9467 | -0.27924 | 123.0606 | -0.068664 | 60.9467 | 122.7127 | 123.0057 | -123.1888 | -123.2254
1068.7656 | 123.111 | -60.8871 | 62.0316 | 0.1104 | -0.0033026 | -0.0034393 | 0.0049838 | 0.065659 | -0.0043685 | 0.069974 | -61.0153 | 62.1185 | -61.1664 | -61.1298 | 61.8027 | 0.041199 | 0.041199 | 0.12817 | 62.0956 | -61.1938 | -0.27924 | 0.086975 | -0.12817 | -0.24262 | -0.22888 | -0.3067 | 0.064087 | 0.15106 | 60.9283 | 61.0153 | 122.6898 | 123.0057 | -0.12817 | 122.9828 | 60.9283 | -0.3067 | 123.0057 | -0.12817 | 60.9283 | 122.6898 | 122.9828 | -123.1979 | -123.2254
1069.7812 | 123.1796 | -60.878 | 62.0132 | 0.19432 | -0.0050116 | -0.0060027 | -0.0027066 | 0.063309 | -0.0015915 | 0.071897 | -61.0565 | 62.0087 | -61.1572 | -61.171 | 61.8347 | 0.018311 | -0.10071 | 0.11444 | 62.0132 | -61.1481 | -0.27924 | -0.004578 | -0.17853 | -0.29297 | -0.17853 | -0.27008 | 0 | 0.10071 | 60.7773 | 60.9924 | 122.7127 | 122.8867 | -0.17853 | 122.8912 | 60.8963 | -0.27008 | 122.8867 | -0.17853 | 60.8963 | 122.7127 | 122.8912 | -123.1705 | -123.1613
1070.7656 | 123.1338 | -60.9009 | 62.0453 | -0.080337 | -0.0035162 | -0.0030121 | 0.0047702 | 0.063096 | -0.0039413 | 0.070188 | -60.9879 | 62.1323 | -61.1206 | -61.1114 | 61.8073 | 0.07782 | 0.054932 | 0.16479 | 62.0773 | -61.1893 | -0.21973 | 0.086975 | -0.086975 | -0.21057 | -0.23804 | -0.28839 | 0.032044 | 0.13275 | 60.9558 | 61.0657 | 122.7081 | 123.0331 | -0.086975 | 122.9782 | 60.9787 | -0.28839 | 123.0331 | -0.086975 | 60.9787 | 122.7081 | 122.9782 | -123.1659 | -123.2346
1071.7656 | 123.1338 | -60.8963 | 62.0224 | -0.11085 | -0.0035162 | -0.0047211 | 0.0024202 | 0.065659 | -0.0035141 | 0.068265 | -60.9924 | 62.1643 | -61.1252 | -61.1206 | 61.8073 | 0.064087 | 0.064087 | 0.16022 | 62.059 | -61.203 | -0.22888 | 0.14191 | -0.096131 | -0.2243 | -0.21515 | -0.3067 | 0.036621 | 0.13275 | 60.9604 | 61.0565 | 122.7036 | 123.0606 | -0.096131 | 122.9553 | 60.9604 | -0.3067 | 123.0606 | -0.096131 | 60.9604 | 122.7036 | 122.9553 | -123.1476 | -123.2254
1072.7656 | 123.1476 | -60.91 | 62.0361 | -0.04219 | -0.0037298 | -0.0015167 | 0.005411 | 0.065659 | -0.0043685 | 0.071256 | -60.9833 | 62.1323 | -61.171 | -61.1252 | 61.8118 | 0.054932 | 0.032043 | 0.16937 | 62.0682 | -61.1938 | -0.26093 | 0.09613 | -0.073242 | -0.21515 | -0.2243 | -0.28381 | 0.032043 | 0.18768 | 60.9421 | 61.0794 | 122.7219 | 123.0423 | -0.073242 | 122.9782 | 60.965 | -0.28381 | 123.0423 | -0.073242 | 60.965 | 122.7219 | 122.9782 | -123.2071 | -123.23
1073.7656 | 123.0972 | -60.9283 | 62.0407 | 0.011215 | -0.003089 | -0.0032257 | 0.0056246 | 0.066087 | -0.0030869 | 0.070829 | -60.9833 | 62.1414 | -61.1389 | -61.1298 | 61.8027 | 0.032043 | 0.022888 | 0.11902 | 62.0728 | -61.1984 | -0.21057 | 0.10071 | -0.054931 | -0.20142 | -0.23804 | -0.27008 | 0.032044 | 0.15564 | 60.9512 | 61.0474 | 122.731 | 123.0698 | -0.054931 | 123.0011 | 60.9604 | -0.27008 | 123.0698 | -0.054931 | 60.9604 | 122.731 | 123.0011 | -123.1796 | -123.2391
1074.7812 | 123.23 | -60.9055 | 61.9446 | 0.22484 | -0.0043708 | -0.0032257 | 7.0444e-05 | 0.064805 | -0.0028731 | 0.068693 | -60.997 | 62.0316 | -61.1664 | -61.0977 | 61.8576 | 0.036621 | -0.17853 | 0.13275 | 62.0178 | -61.1572 | -0.26093 | 0.086975 | -0.091552 | -0.19226 | -0.086975 | -0.25177 | 0.073242 | 0.16937 | 60.7269 | 61.0382 | 122.7631 | 122.937 | -0.091552 | 122.9233 | 60.9421 | -0.25177 | 122.937 | -0.091552 | 60.9421 | 122.7631 | 122.9233 | -123.111 | -123.1018
1075.7656 | 123.1064 | -60.878 | 62.0224 | 0.026474 | -0.0024482 | -0.0034393 | 0.0073336 | 0.065873 | -0.0069321 | 0.069761 | -60.9833 | 62.1323 | -61.1389 | -61.1343 | 61.821 | 0.082397 | 0.022888 | 0.13733 | 62.1185 | -61.1801 | -0.26093 | 0.10986 | -0.10528 | -0.25635 | -0.20142 | -0.30212 | 0.09613 | 0.15564 | 60.9009 | 61.0153 | 122.699 | 123.0103 | -0.10528 | 122.9965 | 60.9604 | -0.30212 | 123.0103 | -0.10528 | 60.9604 | 122.699 | 122.9965 | -123.1613 | -123.2025
1076.7656 | 123.1201 | -60.8917 | 62.027 | -0.04219 | -0.0015936 | -0.0034393 | 0.0022066 | 0.065446 | -0.0028731 | 0.069333 | -60.9833 | 62.146 | -61.1435 | -61.1069 | 61.8256 | 0.059509 | -0.068665 | 0.045776 | 62.1002 | -61.1847 | -0.25177 | 0.11902 | -0.091552 | -0.21515 | -0.20142 | -0.29297 | 0.073242 | 0.16022 | 60.8231 | 60.9375 | 122.7173 | 123.0377 | -0.091552 | 122.9919 | 60.9512 | -0.29297 | 123.0377 | -0.091552 | 60.9512 | 122.7173 | 122.9919 | -123.1705 | -123.2117
1077.7656 | 123.1155 | -60.8871 | 62.027 | -0.14137 | 0.00011541 | -0.0062163 | 0.00071144 | 0.065018 | -0.0024459 | 0.070402 | -61.0245 | 62.146 | -61.1481 | -61.116 | 61.821 | 0.068665 | 0.073242 | 0.17853 | 62.0636 | -61.1893 | -0.26093 | 0.11902 | -0.13733 | -0.22888 | -0.20599 | -0.30212 | 0.036621 | 0.1236 | 60.9604 | 61.0657 | 122.7081 | 123.0331 | -0.13733 | 122.9507 | 60.9558 | -0.30212 | 123.0331 | -0.13733 | 60.9558 | 122.7081 | 122.9507 | -123.175 | -123.2162
1078.7656 | 123.143 | -60.8871 | 62.0361 | -0.149 | -0.0052252 | -0.0064301 | 0.0041292 | 0.064805 | -0.0035141 | 0.068479 | -61.0199 | 62.1506 | -61.1572 | -61.116 | 61.8164 | 0.082397 | 0.09613 | 0.16479 | 62.0911 | -61.171 | -0.27008 | 0.11444 | -0.13275 | -0.22888 | -0.21973 | -0.28381 | 0.054931 | 0.13733 | 60.9833 | 61.0519 | 122.7036 | 123.0377 | -0.13275 | 122.9782 | 60.9695 | -0.28381 | 123.0377 | -0.13275 | 60.9695 | 122.7036 | 122.9782 | -123.1934 | -123.2071
1079.7812 | 123.1842 | -60.9009 | 61.9583 | 0.23247 | -0.0041572 | -0.0027985 | -0.00014316 | 0.065232 | -0.0030869 | 0.068265 | -61.0428 | 62.0682 | -61.1664 | -61.1618 | 61.8118 | 0 | -0.13275 | 0.091553 | 62.0041 | -61.1847 | -0.2655 | 0.10986 | -0.14191 | -0.26092 | -0.14648 | -0.28381 | 0.045776 | 0.1236 | 60.7681 | 60.9924 | 122.7127 | 122.9691 | -0.14191 | 122.905 | 60.9009 | -0.28381 | 122.9691 | -0.14191 | 60.9009 | 122.7127 | 122.905 | -123.1247 | -123.143
1080.7656 | 123.1201 | -60.8871 | 62.027 | 0.018845 | -0.0020208 | -0.0013031 | 0.0047702 | 0.068436 | -0.0020187 | 0.067624 | -60.9879 | 62.1323 | -61.1435 | -61.1114 | 61.8073 | 0.018311 | 0.032043 | 0.12817 | 62.0453 | -61.1801 | -0.25635 | 0.10529 | -0.10071 | -0.2243 | -0.21973 | -0.29297 | 0.01831 | 0.15564 | 60.9192 | 61.0153 | 122.6944 | 123.0194 | -0.10071 | 122.9324 | 60.9055 | -0.29297 | 123.0194 | -0.10071 | 60.9055 | 122.6944 | 122.9324 | -123.1705 | -123.2071
1081.7656 | 123.1293 | -60.9146 | 62.0407 | -0.04219 | -0.0033026 | -0.0057891 | 0.0049838 | 0.064378 | -0.00073695 | 0.068265 | -60.9879 | 62.146 | -61.1526 | -61.116 | 61.8073 | 0.068665 | -0.009155 | -0.018311 | 62.0224 | -61.1893 | -0.23804 | 0.10529 | -0.073242 | -0.20142 | -0.23346 | -0.27466 | -0.01831 | 0.16479 | 60.9055 | 60.8963 | 122.7219 | 123.0606 | -0.073242 | 122.937 | 60.9833 | -0.27466 | 123.0606 | -0.073242 | 60.9833 | 122.7219 | 122.937 | -123.1934 | -123.23
1082.7656 | 123.1155 | -60.9009 | 62.0407 | -0.026932 | -0.0028754 | -0.0066437 | 0.002634 | 0.064164 | -0.0033005 | 0.068479 | -60.997 | 62.1323 | -61.1435 | -61.116 | 61.8118 | 0.064087 | 0.022888 | 0.16937 | 62.0773 | -61.1618 | -0.24261 | 0.091553 | -0.09613 | -0.21515 | -0.22888 | -0.26092 | 0.036622 | 0.14648 | 60.9238 | 61.0703 | 122.7127 | 123.0331 | -0.09613 | 122.9782 | 60.965 | -0.26092 | 123.0331 | -0.09613 | 60.965 | 122.7127 | 122.9782 | -123.1842 | -123.2025
1083.7656 | 123.1247 | -60.8917 | 62.0132 | -0.034561 | -0.0035162 | -0.0047211 | 0.0024202 | 0.066514 | -0.0033005 | 0.068479 | -60.9787 | 62.1323 | -61.1572 | -61.1206 | 61.8301 | 0.068665 | 0.045776 | 0.17395 | 62.0819 | -61.1755 | -0.2655 | 0.11902 | -0.086975 | -0.22888 | -0.18311 | -0.28381 | 0.068664 | 0.17853 | 60.9375 | 61.0657 | 122.7219 | 123.024 | -0.086975 | 122.9736 | 60.9604 | -0.28381 | 123.024 | -0.086975 | 60.9604 | 122.7219 | 122.9736 | -123.1705 | -123.1888
1084.7812 | 123.1705 | -60.91 | 61.9446 | 0.23247 | -0.0024482 | -0.00087594 | -0.0018522 | 0.064378 | -0.0013779 | 0.068479 | -61.0062 | 62.0682 | -61.1389 | -61.1252 | 61.8484 | 0.036621 | -0.16022 | 0.14191 | 62.027 | -61.1664 | -0.22888 | 0.1236 | -0.096131 | -0.21515 | -0.09613 | -0.25635 | 0.082398 | 0.13275 | 60.7498 | 61.0519 | 122.7585 | 122.9782 | -0.096131 | 122.937 | 60.9467 | -0.25635 | 122.9782 | -0.096131 | 60.9467 | 122.7585 | 122.937 | -123.0835 | -123.111
1085.7656 | 123.0927 | -60.9009 | 62.0499 | -0.13374 | -0.0026618 | -0.0081389 | 0.0051974 | 0.065018 | -0.0043685 | 0.070188 | -61.0382 | 62.1552 | -61.1572 | -61.116 | 61.8027 | 0.050354 | 0.10529 | 0.15106 | 62.1094 | -61.1893 | -0.25635 | 0.10528 | -0.13733 | -0.21515 | -0.24719 | -0.28839 | 0.059509 | 0.11902 | 61.0062 | 61.0519 | 122.7036 | 123.056 | -0.13733 | 123.0103 | 60.9512 | -0.28839 | 123.056 | -0.13733 | 60.9512 | 122.7036 | 123.0103 | -123.2071 | -123.2391
1086.7656 | 123.1293 | -60.9009 | 62.0361 | -0.080337 | -0.0028754 | -0.0060027 | 0.0049838 | 0.065232 | -0.0039413 | 0.066984 | -60.9833 | 62.1323 | -61.1389 | -61.1069 | 61.8256 | 0.073242 | 0.036621 | 0.16479 | 62.0911 | -61.1938 | -0.23804 | 0.09613 | -0.082397 | -0.20599 | -0.21057 | -0.29297 | 0.054931 | 0.15564 | 60.9375 | 61.0657 | 122.7264 | 123.0331 | -0.082397 | 122.9919 | 60.9741 | -0.29297 | 123.0331 | -0.082397 | 60.9741 | 122.7264 | 122.9919 | -123.175 | -123.23
1087.7656 | 123.1384 | -60.8963 | 62.0407 | 0.0035856 | -0.00138 | -0.0038665 | 0.0051974 | 0.066727 | -0.0015915 | 0.069974 | -60.9924 | 62.1323 | -61.1481 | -61.1847 | 61.7203 | 0.022888 | 0.036621 | 0.14191 | 62.0544 | -61.1893 | -0.25177 | 0.091553 | -0.096131 | -0.28839 | -0.32043 | -0.29297 | 0.013733 | 0.15564 | 60.9329 | 61.0382 | 122.6166 | 123.0286 | -0.096131 | 122.9507 | 60.9192 | -0.29297 | 123.0286 | -0.096131 | 60.9192 | 122.6166 | 122.9507 | -123.1888 | -123.23
1088.7656 | 123.1338 | -60.9146 | 62.027 | -0.011673 | -0.0033026 | -0.0034393 | 0.0034884 | 0.065018 | -0.0033005 | 0.067838 | -60.9833 | 62.1277 | -61.1389 | -61.1023 | 61.821 | 0.068665 | 0.027466 | 0.07782 | 62.0728 | -61.171 | -0.2243 | 0.10071 | -0.068664 | -0.18768 | -0.20599 | -0.25635 | 0.045776 | 0.15564 | 60.9421 | 60.9924 | 122.7356 | 123.0423 | -0.068664 | 122.9874 | 60.9833 | -0.25635 | 123.0423 | -0.068664 | 60.9833 | 122.7356 | 122.9874 | -123.1659 | -123.1979
1089.7656 | 123.1247 | -60.91 | 62.0224 | -0.095596 | -0.0024482 | -0.0053619 | 0.0039156 | 0.065659 | -0.0015915 | 0.069974 | -61.0016 | 62.1689 | -61.1481 | -61.1252 | 61.8347 | 0.050354 | 0.009155 | 0.15106 | 62.0682 | -61.1847 | -0.23804 | 0.14648 | -0.091553 | -0.21515 | -0.18768 | -0.27466 | 0.045776 | 0.14648 | 60.9192 | 61.0611 | 122.7448 | 123.0789 | -0.091553 | 122.9782 | 60.9604 | -0.27466 | 123.0789 | -0.091553 | 60.9604 | 122.7448 | 122.9782 | -123.1705 | -123.2071
1090.7656 | 123.1293 | -60.8963 | 62.0361 | -0.04982 | -0.0033026 | -0.0051483 | 0.0039156 | 0.065659 | -0.0050095 | 0.068693 | -61.0153 | 62.1368 | -61.1435 | -61.1069 | 61.8256 | 0.064087 | 0.022888 | 0.16022 | 62.0407 | -61.1938 | -0.24719 | 0.10071 | -0.11902 | -0.21057 | -0.21057 | -0.29755 | 0.004577 | 0.12817 | 60.9192 | 61.0565 | 122.7219 | 123.0331 | -0.11902 | 122.937 | 60.9604 | -0.29755 | 123.0331 | -0.11902 | 60.9604 | 122.7219 | 122.937 | -123.1796 | -123.23
1091.7656 | 123.1018 | -60.91 | 62.0224 | -0.14137 | -0.0060798 | -0.0098479 | 0.0028476 | 0.062455 | -0.0030869 | 0.068479 | -61.0245 | 62.1826 | -61.1526 | -61.1206 | 61.8393 | 0.073242 | 0.09613 | 0.17395 | 62.0911 | -61.171 | -0.24261 | 0.16022 | -0.11444 | -0.21057 | -0.18311 | -0.26093 | 0.068664 | 0.12817 | 61.0062 | 61.084 | 122.7493 | 123.0927 | -0.11444 | 123.0011 | 60.9833 | -0.26093 | 123.0927 | -0.11444 | 60.9833 | 122.7493 | 123.0011 | -123.175 | -123.1934
1092.7656 | 123.1064 | -60.8963 | 62.0407 | -0.17189 | -0.0020208 | -0.0010895 | 0.0030612 | 0.064164 | -0.0011643 | 0.068906 | -61.0153 | 62.1735 | -61.171 | -61.116 | 61.8256 | 0.064087 | 0.086975 | 0.16022 | 62.0911 | -61.1664 | -0.27466 | 0.13275 | -0.11902 | -0.21973 | -0.21515 | -0.27008 | 0.050354 | 0.15564 | 60.9833 | 61.0565 | 122.7219 | 123.0698 | -0.11902 | 122.9874 | 60.9604 | -0.27008 | 123.0698 | -0.11902 | 60.9604 | 122.7219 | 122.9874 | -123.2117 | -123.2071
1093.7656 | 123.1201 | -60.8963 | 62.0499 | -0.04219 | -0.0033026 | -0.0038665 | 0.0032748 | 0.064805 | -0.00052335 | 0.066984 | -60.997 | 62.178 | -61.1389 | -61.0931 | 61.8301 | 0.073242 | 0.036621 | 0.16937 | 62.0499 | -61.1847 | -0.24262 | 0.12817 | -0.10071 | -0.19684 | -0.21973 | -0.28839 | 0 | 0.14191 | 60.9329 | 61.0657 | 122.7264 | 123.0743 | -0.10071 | 122.9462 | 60.9695 | -0.28839 | 123.0743 | -0.10071 | 60.9695 | 122.7264 | 122.9462 | -123.1888 | -123.2346
1094.7656 | 123.1338 | -60.9055 | 62.027 | 0.0035856 | -0.0018072 | -0.0051483 | 0.003702 | 0.0663 | -0.0020187 | 0.070829 | -60.997 | 62.146 | -61.1572 | -61.1343 | 61.8118 | 0.036621 | 0.027466 | 0.11902 | 62.0819 | -61.1847 | -0.25177 | 0.11902 | -0.091552 | -0.22888 | -0.21515 | -0.27923 | 0.054931 | 0.16022 | 60.9329 | 61.0245 | 122.7173 | 123.0515 | -0.091552 | 122.9874 | 60.9421 | -0.27923 | 123.0515 | -0.091552 | 60.9421 | 122.7173 | 122.9874 | -123.1842 | -123.2117
1095.7656 | 123.1155 | -60.9192 | 62.0224 | 0.17906 | -0.0018072 | -0.0030121 | 0.0039156 | 0.064805 | -0.0047957 | 0.067411 | -60.9787 | 62.1323 | -61.116 | -61.1252 | 61.8164 | 0.036621 | 0.022888 | 0.1236 | 62.0819 | -61.1847 | -0.19684 | 0.10986 | -0.05951 | -0.20599 | -0.20599 | -0.2655 | 0.059509 | 0.13733 | 60.9421 | 61.0428 | 122.7356 | 123.0515 | -0.05951 | 123.0011 | 60.9558 | -0.2655 | 123.0515 | -0.05951 | 60.9558 | 122.7356 | 123.0011 | -123.1384 | -123.2071
1096.7656 | 123.1155 | -60.91 | 62.0178 | -0.36262 | -0.0028754 | -0.0034393 | 0.0049838 | 0.067368 | -0.0039413 | 0.069974 | -61.0153 | 62.1094 | -61.116 | -61.116 | 61.8073 | 0.050354 | 0.013733 | 0.12817 | 62.0773 | -61.1755 | -0.20599 | 0.091553 | -0.10529 | -0.20599 | -0.21057 | -0.2655 | 0.05951 | 0.10071 | 60.9238 | 61.0382 | 122.7173 | 123.0194 | -0.10529 | 122.9874 | 60.9604 | -0.2655 | 123.0194 | -0.10529 | 60.9604 | 122.7173 | 122.9874 | -123.1338 | -123.1934
1097.7656 | 123.1247 | -60.9146 | 62.0178 | 0.11803 | -0.0035162 | -0.0047211 | 0.0028476 | 0.064378 | -0.0028731 | 0.067624 | -60.9833 | 62.1368 | -61.1618 | -61.1206 | 61.8118 | 0.064087 | 0.027466 | 0.11902 | 62.059 | -61.1938 | -0.24719 | 0.11902 | -0.068664 | -0.20599 | -0.20599 | -0.27924 | 0.041199 | 0.17853 | 60.9421 | 61.0336 | 122.7264 | 123.0515 | -0.068664 | 122.9736 | 60.9787 | -0.27924 | 123.0515 | -0.068664 | 60.9787 | 122.7264 | 122.9736 | -123.1796 | -123.2117
1098.7656 | 123.1338 | -60.9009 | 62.0316 | -0.10323 | -0.0024482 | -0.0040801 | 0.0049838 | 0.064591 | -0.0047957 | 0.068906 | -60.997 | 62.1368 | -61.1572 | -61.1252 | 61.8301 | 0.07782 | 0.041199 | 0.17395 | 62.114 | -61.1618 | -0.25635 | 0.10529 | -0.09613 | -0.2243 | -0.20142 | -0.26092 | 0.082398 | 0.16022 | 60.9421 | 61.0748 | 122.731 | 123.0377 | -0.09613 | 123.0148 | 60.9787 | -0.26092 | 123.0377 | -0.09613 | 60.9787 | 122.731 | 123.0148 | -123.1888 | -123.1934
1099.7656 | 123.1018 | -60.9009 | 62.0316 | -0.04219 | 0.0016108 | -0.0032257 | 0.0017794 | 0.065232 | -0.0024459 | 0.067838 | -61.0748 | 62.1277 | -61.1572 | -61.1389 | 61.7981 | 0.059509 | 0.022888 | 0.14191 | 62.0728 | -61.1893 | -0.25635 | 0.096131 | -0.17395 | -0.23804 | -0.23346 | -0.28839 | 0.041199 | 0.082398 | 60.9238 | 61.0428 | 122.699 | 123.0286 | -0.17395 | 122.9736 | 60.9604 | -0.28839 | 123.0286 | -0.17395 | 60.9604 | 122.699 | 122.9736 | -123.1888 | -123.2208
1100.7656 | 123.0743 | -60.9146 | 62.0132 | 0.07988 | -0.0035162 | -0.0057891 | 0.0058382 | 0.065446 | -0.0013779 | 0.069974 | -61.0199 | 62.146 | -61.171 | -61.1618 | 61.7752 | -0.027466 | 0.036621 | 0.059509 | 62.0773 | -61.2122 | -0.25635 | 0.13275 | -0.10529 | -0.24719 | -0.23804 | -0.29755 | 0.064087 | 0.15106 | 60.9512 | 60.9741 | 122.6898 | 123.0606 | -0.10529 | 122.9919 | 60.8871 | -0.29755 | 123.0606 | -0.10529 | 60.8871 | 122.6898 | 122.9919 | -123.1842 | -123.2254
1101.7656 | 123.0698 | -60.9238 | 62.0316 | 0.087509 | -0.004798 | -0.0045075 | 0.0049838 | 0.064591 | -0.0015915 | 0.069333 | -61.0245 | 62.178 | -61.1572 | -61.1847 | 61.7752 | -0.018311 | 0.022888 | 0.064087 | 62.0453 | -61.2122 | -0.23346 | 0.14649 | -0.10071 | -0.26093 | -0.25635 | -0.28839 | 0.013733 | 0.13275 | 60.9467 | 60.9879 | 122.699 | 123.1018 | -0.10071 | 122.9691 | 60.9055 | -0.28839 | 123.1018 | -0.10071 | 60.9055 | 122.699 | 122.9691 | -123.1888 | -123.2437
1102.7656 | 123.0743 | -60.9283 | 62.0178 | 0.17143 | -0.0041572 | -0.0068573 | 0.0041292 | 0.065873 | -0.00095055 | 0.068906 | -61.0886 | 62.1414 | -61.1847 | -61.235 | 61.7157 | -0.054932 | 0.009155 | 0.013733 | 62.0544 | -61.2305 | -0.25635 | 0.1236 | -0.16022 | -0.3067 | -0.30212 | -0.30212 | 0.036621 | 0.09613 | 60.9375 | 60.9421 | 122.644 | 123.0698 | -0.16022 | 122.9828 | 60.8734 | -0.30212 | 123.0698 | -0.16022 | 60.8734 | 122.644 | 122.9828 | -123.2025 | -123.2483
1103.7656 | 123.0972 | -60.9238 | 61.9995 | 0.11803 | -0.003089 | -0.0019439 | 0.0030612 | 0.065232 | -0.0011643 | 0.067838 | -61.0291 | 62.1277 | -61.1572 | -61.1801 | 61.7706 | -0.022888 | 0.045776 | 0.064087 | 62.0728 | -61.203 | -0.23346 | 0.12817 | -0.10529 | -0.25635 | -0.22888 | -0.27924 | 0.073242 | 0.12817 | 60.9695 | 60.9879 | 122.6944 | 123.0515 | -0.10529 | 122.9965 | 60.9009 | -0.27924 | 123.0515 | -0.10529 | 60.9009 | 122.6944 | 122.9965 | -123.1567 | -123.2025
1104.7656 | 123.0652 | -60.9283 | 62.027 | 0.12566 | -0.0033026 | -0.0070709 | 0.0056246 | 0.064591 | -0.0037277 | 0.068265 | -61.0336 | 62.1368 | -61.1526 | -61.1801 | 61.7798 | -0.013733 | 0.036621 | 0.045776 | 62.0819 | -61.1893 | -0.2243 | 0.10986 | -0.10529 | -0.25177 | -0.24719 | -0.26093 | 0.054931 | 0.11902 | 60.965 | 60.9741 | 122.7081 | 123.0652 | -0.10529 | 123.0103 | 60.9146 | -0.26093 | 123.0652 | -0.10529 | 60.9146 | 122.7081 | 123.0103 | -123.1796 | -123.2162
1105.7656 | 123.1018 | -60.9055 | 62.0453 | 0.1104 | -0.0024482 | -0.0057891 | 0.0028476 | 0.066087 | -0.0024459 | 0.069333 | -60.9695 | 62.1506 | -61.1618 | -61.1252 | 61.7981 | 0.045776 | 0.027466 | 0.14191 | 62.0728 | -61.1938 | -0.25635 | 0.10529 | -0.064086 | -0.21973 | -0.24719 | -0.28839 | 0.027466 | 0.19226 | 60.9329 | 61.0474 | 122.7036 | 123.056 | -0.064086 | 122.9782 | 60.9512 | -0.28839 | 123.056 | -0.064086 | 60.9512 | 122.7036 | 122.9782 | -123.2071 | -123.2391
1106.7656 | 123.1247 | -60.91 | 62.0224 | -0.34737 | -0.0024482 | -0.0019439 | 0.0045566 | 0.062455 | -0.0024459 | 0.068052 | -60.9787 | 62.146 | -61.1618 | -61.1252 | 61.7889 | 0.032043 | 0.036621 | 0.14191 | 62.0728 | -61.1984 | -0.25177 | 0.1236 | -0.068665 | -0.21515 | -0.23346 | -0.28839 | 0.050354 | 0.1831 | 60.9467 | 61.0519 | 122.699 | 123.056 | -0.068665 | 122.9828 | 60.9421 | -0.28839 | 123.056 | -0.068665 | 60.9421 | 122.699 | 122.9828 | -123.1842 | -123.2208
1107.7656 | 123.0835 | -60.9192 | 62.0132 | 0.17143 | -0.0022346 | -0.0021575 | 0.0028476 | 0.063523 | -0.00030975 | 0.068479 | -61.1069 | 62.1414 | -61.1618 | -61.1984 | 61.7203 | -0.068665 | -0.009155 | 0.018311 | 62.0453 | -61.2305 | -0.24261 | 0.12817 | -0.18768 | -0.27924 | -0.29297 | -0.31128 | 0.032043 | 0.054931 | 60.91 | 60.9375 | 122.6395 | 123.0606 | -0.18768 | 122.9645 | 60.8505 | -0.31128 | 123.0606 | -0.18768 | 60.8505 | 122.6395 | 122.9645 | -123.175 | -123.2437
1108.7656 | 123.0881 | -60.9329 | 62.0087 | 0.24773 | -0.0024482 | -0.00087594 | 0.0049838 | 0.065018 | -0.0030869 | 0.068906 | -61.0703 | 62.146 | -61.171 | -61.2122 | 61.7432 | -0.073242 | 0.004578 | 0.004578 | 62.0773 | -61.2167 | -0.23804 | 0.13733 | -0.13733 | -0.27924 | -0.2655 | -0.28381 | 0.068665 | 0.10071 | 60.9375 | 60.9375 | 122.6761 | 123.0789 | -0.13733 | 123.0103 | 60.8597 | -0.28381 | 123.0789 | -0.13733 | 60.8597 | 122.6761 | 123.0103 | -123.1796 | -123.2254
1109.7656 | 123.0698 | -60.91 | 62.0087 | 0.17143 | -0.0024482 | -0.0053619 | 0.0049838 | 0.064591 | -0.0020187 | 0.069761 | -61.0977 | 62.1368 | -61.1664 | -61.203 | 61.7432 | -0.059509 | 0.004578 | 0.004578 | 62.0773 | -61.2076 | -0.25635 | 0.12817 | -0.18768 | -0.29297 | -0.2655 | -0.29755 | 0.068665 | 0.068665 | 60.9146 | 60.9146 | 122.6532 | 123.0469 | -0.18768 | 122.9874 | 60.8505 | -0.29755 | 123.0469 | -0.18768 | 60.8505 | 122.6532 | 122.9874 | -123.175 | -123.2162
1110.7656 | 123.0927 | -60.9055 | 62.0132 | 0.21721 | -0.0028754 | -0.0040801 | 0.0028476 | 0.065659 | -0.0011643 | 0.069761 | -61.0794 | 62.114 | -61.171 | -61.1984 | 61.7477 | -0.054932 | 0.013733 | 0.009155 | 62.0819 | -61.1938 | -0.2655 | 0.10071 | -0.17395 | -0.29297 | -0.2655 | -0.28839 | 0.068664 | 0.091552 | 60.9192 | 60.9146 | 122.6532 | 123.0194 | -0.17395 | 122.9874 | 60.8505 | -0.28839 | 123.0194 | -0.17395 | 60.8505 | 122.6532 | 122.9874 | -123.1842 | -123.2071
1111.7656 | 123.0743 | -60.9192 | 62.027 | 0.15617 | -0.00095279 | -0.0027985 | 0.005411 | 0.065446 | -0.0037277 | 0.069333 | -61.0931 | 62.146 | -61.1938 | -61.203 | 61.7203 | -0.045776 | 0 | 0.009155 | 62.0773 | -61.2259 | -0.27466 | 0.11902 | -0.17395 | -0.28381 | -0.3067 | -0.3067 | 0.050354 | 0.10071 | 60.9192 | 60.9283 | 122.6395 | 123.0652 | -0.17395 | 122.9965 | 60.8734 | -0.3067 | 123.0652 | -0.17395 | 60.8734 | 122.6395 | 122.9965 | -123.2208 | -123.2529
1112.7656 | 123.0835 | -60.9146 | 62.0087 | 0.095139 | -0.0039434 | -0.0049347 | 0.005411 | 0.06395 | -0.0043685 | 0.068479 | -61.0336 | 62.1368 | -61.171 | -61.1801 | 61.7569 | 0 | 0.027466 | 0.068665 | 62.059 | -61.2167 | -0.25635 | 0.12817 | -0.11902 | -0.2655 | -0.25177 | -0.30212 | 0.050354 | 0.13733 | 60.9421 | 60.9833 | 122.6715 | 123.0515 | -0.11902 | 122.9736 | 60.9146 | -0.30212 | 123.0515 | -0.11902 | 60.9146 | 122.6715 | 122.9736 | -123.1796 | -123.2254
1113.7656 | 123.0789 | -60.9329 | 62.0224 | 0.13329 | -0.0020208 | -0.0042937 | 0.002634 | 0.065873 | -0.0041549 | 0.067624 | -61.084 | 62.146 | -61.1938 | -61.2259 | 61.7249 | -0.050354 | 0.018311 | 0 | 62.059 | -61.2213 | -0.26093 | 0.1236 | -0.15106 | -0.29297 | -0.29755 | -0.28839 | 0.036621 | 0.10986 | 60.9512 | 60.9329 | 122.6578 | 123.0789 | -0.15106 | 122.9919 | 60.8826 | -0.28839 | 123.0789 | -0.15106 | 60.8826 | 122.6578 | 122.9919 | -123.2162 | -123.2437
1114.7656 | 123.0927 | -60.9238 | 62.0361 | -0.026932 | -0.0035162 | -0.0049347 | 0.0041292 | 0.065659 | -0.0024459 | 0.067197 | -61.0382 | 62.1643 | -61.1801 | -61.2213 | 61.7432 | -0.054932 | -0.004578 | 0.022888 | 62.0636 | -61.2076 | -0.25635 | 0.12817 | -0.11444 | -0.29755 | -0.29297 | -0.28381 | 0.027466 | 0.14191 | 60.9192 | 60.9467 | 122.6669 | 123.0881 | -0.11444 | 122.9874 | 60.8688 | -0.28381 | 123.0881 | -0.11444 | 60.8688 | 122.6669 | 122.9874 | -123.2162 | -123.2437
1115.7656 | 123.1201 | -60.9421 | 62.027 | 0.59105 | -0.0054388 | -0.0053619 | 0.0032748 | 0.064164 | -0.0013779 | 0.068052 | -60.9009 | 62.1414 | -61.1572 | -61.2076 | 61.7477 | -0.068665 | -0.004578 | 0.018311 | 62.0544 | -61.2167 | -0.21515 | 0.11444 | 0.041199 | -0.2655 | -0.27924 | -0.27466 | 0.027465 | 0.25635 | 60.9375 | 60.9604 | 122.6898 | 123.0835 | 0.041199 | 122.9965 | 60.8734 | -0.27466 | 123.0835 | 0.041199 | 60.8734 | 122.6898 | 122.9965 | -123.1842 | -123.2437
1116.7656 | 123.1064 | -60.9283 | 62.0132 | 0.20195 | 0.00096981 | -0.00087594 | 0.0024202 | 0.065446 | -0.0018051 | 0.070402 | -61.3495 | 62.0911 | -61.1984 | -61.171 | 61.7477 | -0.050354 | -0.013733 | 0 | 62.0636 | -61.2076 | -0.27008 | 0.077819 | -0.42114 | -0.24261 | -0.2655 | -0.27924 | 0.050354 | -0.15106 | 60.9146 | 60.9283 | 122.6761 | 123.0194 | -0.42114 | 122.9919 | 60.878 | -0.27924 | 123.0194 | -0.42114 | 60.878 | 122.6761 | 122.9919 | -123.2117 | -123.2208
1117.7656 | 123.0927 | -60.91 | 61.9949 | 0.21721 | -0.0052252 | -0.0023711 | 0.00092504 | 0.063737 | -0.0056503 | 0.069333 | -60.9467 | 62.1185 | -61.203 | -61.1801 | 61.7065 | -0.041199 | 0.018311 | 0.036621 | 62.0911 | -61.203 | -0.29297 | 0.1236 | -0.036621 | -0.27008 | -0.28839 | -0.29297 | 0.09613 | 0.25635 | 60.9283 | 60.9467 | 122.6166 | 123.0286 | -0.036621 | 123.0011 | 60.8688 | -0.29297 | 123.0286 | -0.036621 | 60.8688 | 122.6166 | 123.0011 | -123.1979 | -123.1979
1118.7656 | 123.0469 | -60.9421 | 62.0224 | 0.095139 | -0.003089 | -0.0049347 | 0.0064792 | 0.065873 | -0.0022323 | 0.066129 | -61.0703 | 62.1414 | -61.171 | -61.203 | 61.7294 | -0.068665 | 0.032043 | 0.009155 | 62.0682 | -61.2213 | -0.22888 | 0.11902 | -0.12817 | -0.26093 | -0.29297 | -0.27923 | 0.045776 | 0.10071 | 60.9741 | 60.9512 | 122.6715 | 123.0835 | -0.12817 | 123.0103 | 60.8734 | -0.27923 | 123.0835 | -0.12817 | 60.8734 | 122.6715 | 123.0103 | -123.1934 | -123.2437
1119.7656 | 123.0927 | -60.9421 | 62.0087 | 0.12566 | -0.0026618 | -0.0074981 | 0.0034884 | 0.06395 | -0.0033005 | 0.06677 | -61.0611 | 62.1597 | -61.171 | -61.1984 | 61.7386 | -0.045776 | 0.032043 | 0.027466 | 62.0728 | -61.2122 | -0.22888 | 0.15106 | -0.11902 | -0.25635 | -0.27008 | -0.27008 | 0.064087 | 0.10986 | 60.9741 | 60.9695 | 122.6807 | 123.1018 | -0.11902 | 123.0148 | 60.8963 | -0.27008 | 123.1018 | -0.11902 | 60.8963 | 122.6807 | 123.0148 | -123.1796 | -123.2208
1120.7656 | 123.0789 | -60.9192 | 62.0316 | 0.20958 | -0.003089 | -0.0047211 | 0.0030612 | 0.066087 | -0.0033005 | 0.068265 | -61.0703 | 62.1277 | -61.1847 | -61.2488 | 61.4456 | -0.32044 | 0.24261 | 0.041199 | 62.0773 | -61.203 | -0.2655 | 0.096131 | -0.15106 | -0.32959 | -0.58594 | -0.28381 | 0.045777 | 0.11444 | 61.1618 | 60.9604 | 122.3648 | 123.0469 | -0.15106 | 122.9965 | 60.5988 | -0.28381 | 123.0469 | -0.15106 | 60.5988 | 122.3648 | 122.9965 | -123.2162 | -123.2346
1121.7656 | 123.111 | -60.9329 | 62.027 | 0.23247 | -0.0033026 | -0.0027985 | 0.0013522 | 0.065018 | -0.0020187 | 0.068052 | -61.0611 | 62.1094 | -61.1618 | -61.1984 | 61.7706 | -0.059509 | -0.050354 | 0.036621 | 62.0453 | -61.1984 | -0.22888 | 0.082397 | -0.12817 | -0.2655 | -0.25635 | -0.2655 | 0.01831 | 0.10071 | 60.8826 | 60.9695 | 122.7036 | 123.0423 | -0.12817 | 122.9782 | 60.8734 | -0.2655 | 123.0423 | -0.12817 | 60.8734 | 122.7036 | 122.9782 | -123.1888 | -123.2254
1122.7656 | 123.1018 | -60.9146 | 61.9995 | 0.21721 | -0.0018072 | -0.0072845 | 0.0015658 | 0.064805 | 0.00011745 | 0.069761 | -61.0565 | 62.1048 | -61.1755 | -61.203 | 61.734 | -0.032043 | -0.059509 | 0.027466 | 62.0407 | -61.1984 | -0.26093 | 0.10528 | -0.14191 | -0.28839 | -0.2655 | -0.28381 | 0.041198 | 0.11902 | 60.8551 | 60.9421 | 122.6486 | 123.0194 | -0.14191 | 122.9553 | 60.8826 | -0.28381 | 123.0194 | -0.14191 | 60.8826 | 122.6486 | 122.9553 | -123.175 | -123.1979
1123.7656 | 123.143 | -60.9192 | 61.9858 | 0.22484 | -0.0024482 | -0.0053619 | 0.0028476 | 0.065659 | -0.0013779 | 0.068052 | -61.0565 | 62.1185 | -61.1801 | -61.1847 | 61.7569 | -0.054932 | -0.041199 | 0.022888 | 62.0682 | -61.203 | -0.26093 | 0.13275 | -0.13733 | -0.2655 | -0.22888 | -0.28381 | 0.082397 | 0.1236 | 60.878 | 60.9421 | 122.6761 | 123.0377 | -0.13733 | 122.9874 | 60.8643 | -0.28381 | 123.0377 | -0.13733 | 60.8643 | 122.6761 | 122.9874 | -123.1659 | -123.1888
1124.7656 | 123.111 | -60.9192 | 61.9858 | 0.20195 | -0.0033026 | -0.0070709 | 0.0030612 | 0.065446 | -0.0018051 | 0.068479 | -61.0657 | 62.1277 | -61.1664 | -61.1893 | 61.7477 | -0.050354 | -0.022888 | 0.022888 | 62.0636 | -61.2122 | -0.24719 | 0.14191 | -0.14648 | -0.27008 | -0.23804 | -0.29297 | 0.07782 | 0.10071 | 60.8963 | 60.9421 | 122.6669 | 123.0469 | -0.14648 | 122.9828 | 60.8688 | -0.29297 | 123.0469 | -0.14648 | 60.8688 | 122.6669 | 122.9828 | -123.1522 | -123.1979
1125.7656 | 123.0789 | -60.9192 | 62.0178 | 0.20958 | -0.0035162 | -0.0060027 | 0.0032748 | 0.066514 | -0.0033005 | 0.067838 | -61.0748 | 62.1277 | -61.171 | -61.2076 | 61.7477 | -0.050354 | -0.004578 | 0.004578 | 62.1002 | -61.1938 | -0.25177 | 0.10986 | -0.15564 | -0.28839 | -0.27008 | -0.27466 | 0.082398 | 0.09613 | 60.9146 | 60.9238 | 122.6669 | 123.0469 | -0.15564 | 123.0194 | 60.8688 | -0.27466 | 123.0469 | -0.15564 | 60.8688 | 122.6669 | 123.0194 | -123.1888 | -123.2117
1126.7656 | 123.0881 | -60.9192 | 61.9995 | 0.19432 | -0.0026618 | -0.0038665 | 0.004343 | 0.066514 | -0.0035141 | 0.066984 | -61.0748 | 62.1231 | -61.1847 | -61.1893 | 61.734 | -0.073242 | 0.013733 | 0.013733 | 62.0636 | -61.203 | -0.2655 | 0.1236 | -0.15564 | -0.27008 | -0.2655 | -0.28381 | 0.064087 | 0.10986 | 60.9329 | 60.9329 | 122.6532 | 123.0423 | -0.15564 | 122.9828 | 60.8459 | -0.28381 | 123.0423 | -0.15564 | 60.8459 | 122.6532 | 122.9828 | -123.1842 | -123.2025
1127.7656 | 123.111 | -60.9192 | 62.0224 | 0.18669 | -0.0028754 | -0.0038665 | 0.0024202 | 0.065659 | -0.00073695 | 0.069974 | -61.0657 | 62.1414 | -61.1893 | -61.1893 | 61.734 | -0.032043 | -0.022888 | 0.027466 | 62.0636 | -61.1984 | -0.27008 | 0.11902 | -0.14648 | -0.27008 | -0.28839 | -0.27924 | 0.041199 | 0.1236 | 60.8963 | 60.9467 | 122.6532 | 123.0606 | -0.14648 | 122.9828 | 60.8871 | -0.27924 | 123.0606 | -0.14648 | 60.8871 | 122.6532 | 122.9828 | -123.2117 | -123.2208
1128.7656 | 123.1476 | -60.9467 | 61.9675 | 0.30113 | -0.0045844 | -0.0027985 | 0.0015658 | 0.065659 | -0.0033005 | 0.069761 | -61.0382 | 62.0728 | -61.1526 | -61.1389 | 61.8118 | 0.004578 | -0.12817 | 0.09613 | 62.0224 | -61.1847 | -0.20599 | 0.10529 | -0.091553 | -0.19226 | -0.15564 | -0.23804 | 0.054932 | 0.11444 | 60.8185 | 61.0428 | 122.7585 | 123.0194 | -0.091553 | 122.9691 | 60.9512 | -0.23804 | 123.0194 | -0.091553 | 60.9512 | 122.7585 | 122.9691 | -123.1201 | -123.1522
1129.7656 | 123.1842 | -60.8871 | 61.9766 | 0.21721 | -0.0056524 | -0.0062163 | 0.002634 | 0.065659 | -0.0045821 | 0.069333 | -61.0199 | 62.0819 | -61.1526 | -61.1481 | 61.8027 | 0.013733 | -0.14191 | 0.10529 | 62.0316 | -61.1618 | -0.2655 | 0.10529 | -0.13275 | -0.26093 | -0.17395 | -0.27466 | 0.054931 | 0.13275 | 60.7452 | 60.9924 | 122.6898 | 122.9691 | -0.13275 | 122.9187 | 60.9009 | -0.27466 | 122.9691 | -0.13275 | 60.9009 | 122.6898 | 122.9187 | -123.1293 | -123.1384
1130.7656 | 123.1842 | -60.8963 | 62.0041 | 0.2935 | -0.0028754 | -0.0038665 | 0.0022066 | 0.06395 | -0.0024459 | 0.06912 | -61.0336 | 62.0911 | -61.171 | -61.1206 | 61.8118 | 0.009155 | -0.14648 | 0.10986 | 62.0499 | -61.171 | -0.27466 | 0.086975 | -0.13733 | -0.2243 | -0.19226 | -0.27466 | 0.045777 | 0.13733 | 60.7498 | 61.0062 | 122.7081 | 122.9874 | -0.13733 | 122.9462 | 60.9055 | -0.27466 | 122.9874 | -0.13733 | 60.9055 | 122.7081 | 122.9462 | -123.175 | -123.175
1131.7656 | 123.1796 | -60.8826 | 61.9858 | 0.23247 | -0.0020208 | -0.0055755 | 0.00071144 | 0.066941 | -0.0024459 | 0.069333 | -61.0199 | 62.0773 | -61.171 | -61.1435 | 61.8118 | 0.018311 | -0.13275 | 0.10986 | 62.0407 | -61.1893 | -0.28839 | 0.091553 | -0.13733 | -0.26093 | -0.17395 | -0.3067 | 0.054931 | 0.15106 | 60.7498 | 60.9924 | 122.6944 | 122.9599 | -0.13733 | 122.9233 | 60.9009 | -0.3067 | 122.9599 | -0.13733 | 60.9009 | 122.6944 | 122.9233 | -123.1567 | -123.175
1132.7656 | 123.1018 | -60.8826 | 62.0087 | 0.18669 | -0.0039434 | -0.0032257 | 0.003702 | 0.065232 | -0.0041549 | 0.069333 | -61.0886 | 62.1048 | -61.1755 | -61.171 | 61.7477 | -0.036621 | -0.045776 | 0.027466 | 62.0728 | -61.1984 | -0.29297 | 0.09613 | -0.20599 | -0.28839 | -0.26093 | -0.31586 | 0.064087 | 0.086975 | 60.8368 | 60.91 | 122.6303 | 122.9874 | -0.20599 | 122.9553 | 60.8459 | -0.31586 | 122.9874 | -0.20599 | 60.8459 | 122.6303 | 122.9553 | -123.1842 | -123.2071
1133.7656 | 123.1064 | -60.9009 | 62.0316 | 0.1104 | -0.0026618 | -0.0083527 | 0.0039156 | 0.06395 | -0.0030869 | 0.06912 | -61.0703 | 62.1094 | -61.1801 | -61.1847 | 61.7523 | -0.045776 | -0.036621 | 0.032043 | 62.0956 | -61.2076 | -0.27924 | 0.07782 | -0.16937 | -0.28381 | -0.27924 | -0.3067 | 0.064087 | 0.10986 | 60.8643 | 60.9329 | 122.6532 | 123.0103 | -0.16937 | 122.9965 | 60.8551 | -0.3067 | 123.0103 | -0.16937 | 60.8551 | 122.6532 | 122.9965 | -123.2117 | -123.2391
1134.7656 | 123.175 | -60.8826 | 61.9629 | 0.30876 | -0.0020208 | -0.0051483 | 0.00092504 | 0.065659 | -0.0033005 | 0.070615 | -61.0474 | 62.0773 | -61.1481 | -61.1252 | 61.8301 | 0.009155 | -0.15106 | 0.09613 | 62.0224 | -61.1801 | -0.2655 | 0.11444 | -0.16479 | -0.24262 | -0.13275 | -0.29755 | 0.059509 | 0.10071 | 60.7315 | 60.9787 | 122.7127 | 122.9599 | -0.16479 | 122.905 | 60.8917 | -0.29755 | 122.9599 | -0.16479 | 60.8917 | 122.7127 | 122.905 | -123.111 | -123.143
1135.7656 | 123.2483 | -60.8826 | 61.9949 | 0.27061 | -0.005866 | -0.0060027 | 0.0017794 | 0.065232 | -0.0039413 | 0.06677 | -60.997 | 62.0407 | -61.1343 | -61.1023 | 61.8393 | 0.050354 | -0.39368 | -0.032043 | 61.9583 | -61.1847 | -0.25177 | 0.045776 | -0.11444 | -0.21973 | -0.15564 | -0.30212 | -0.036621 | 0.13733 | 60.4889 | 60.8505 | 122.7219 | 122.9233 | -0.11444 | 122.8409 | 60.9329 | -0.30212 | 122.9233 | -0.11444 | 60.9329 | 122.7219 | 122.8409 | -123.1293 | -123.1796
1136.7656 | 123.2117 | -60.8597 | 62.0132 | 0.26299 | -0.0052252 | -0.0034393 | 0.0022066 | 0.061387 | -0.0052231 | 0.068479 | -60.9879 | 62.027 | -61.1481 | -61.0931 | 62.0132 | 0.009155 | -0.37537 | 0.24261 | 61.94 | -61.1938 | -0.28839 | 0.013733 | -0.12817 | -0.23346 | 0 | -0.33417 | -0.073243 | 0.16022 | 60.4843 | 61.1023 | 122.8729 | 122.8867 | -0.12817 | 122.7997 | 60.8688 | -0.33417 | 122.8867 | -0.12817 | 60.8688 | 122.8729 | 122.7997 | -123.1613 | -123.2071
1137.7656 | 123.2071 | -60.8643 | 61.9675 | 0.28587 | -0.0041572 | -0.0055755 | 0.00071144 | 0.063737 | -0.0035141 | 0.070402 | -60.9879 | 62.027 | -61.1526 | -61.0977 | 61.94 | -0.073242 | -0.29755 | 0.24719 | 61.972 | -61.1664 | -0.28839 | 0.05951 | -0.1236 | -0.23346 | -0.027466 | -0.30212 | 0.004578 | 0.16479 | 60.5667 | 61.1114 | 122.8043 | 122.8912 | -0.1236 | 122.8363 | 60.791 | -0.30212 | 122.8912 | -0.1236 | 60.791 | 122.8043 | 122.8363 | -123.1201 | -123.1338
1138.7656 | 123.2346 | -60.8734 | 61.9629 | 0.27824 | -0.0037298 | -0.0055755 | -0.00014316 | 0.063737 | -0.0022323 | 0.068052 | -60.997 | 62.0224 | -61.1526 | -61.0977 | 61.8027 | -0.11444 | -0.19684 | 0.2655 | 62.0041 | -61.1618 | -0.27924 | 0.059509 | -0.1236 | -0.2243 | -0.16022 | -0.28839 | 0.041198 | 0.15564 | 60.6766 | 61.1389 | 122.6761 | 122.8958 | -0.1236 | 122.8775 | 60.759 | -0.28839 | 122.8958 | -0.1236 | 60.759 | 122.6761 | 122.8775 | -123.1155 | -123.1247
1139.7656 | 123.2208 | -60.8734 | 61.972 | 0.2401 | -0.0045844 | -0.0070709 | 0.0047702 | 0.0663 | -0.0054367 | 0.067838 | -61.0107 | 62.0361 | -61.1801 | -61.116 | 61.8073 | 0.018311 | -0.16022 | 0.11902 | 62.0178 | -61.1252 | -0.3067 | 0.064087 | -0.13733 | -0.24262 | -0.16479 | -0.25177 | 0.045776 | 0.16937 | 60.7132 | 60.9924 | 122.6807 | 122.9095 | -0.13733 | 122.8912 | 60.8917 | -0.25177 | 122.9095 | -0.13733 | 60.8917 | 122.6807 | 122.8912 | -123.1522 | -123.0972
1140.7656 | 123.2117 | -60.8688 | 61.9812 | 0.28587 | -0.0024482 | -0.0057891 | 0.0034884 | 0.063737 | -0.0047957 | 0.069333 | -61.0245 | 62.0544 | -61.1618 | -61.1206 | 61.8073 | 0.009155 | -0.15106 | 0.10986 | 62.0087 | -61.1618 | -0.29297 | 0.073242 | -0.15564 | -0.25177 | -0.17395 | -0.29297 | 0.027466 | 0.13733 | 60.7178 | 60.9787 | 122.6761 | 122.9233 | -0.15564 | 122.8775 | 60.878 | -0.29297 | 122.9233 | -0.15564 | 60.878 | 122.6761 | 122.8775 | -123.143 | -123.143
1141.7656 | 123.1796 | -60.8505 | 61.9904 | 0.21721 | -0.0037298 | -0.0089935 | 0.0017794 | 0.063096 | -0.0026595 | 0.069333 | -61.0062 | 62.0132 | -61.1526 | -61.116 | 61.8301 | 0.032043 | -0.16479 | 0.13275 | 62.0087 | -61.1435 | -0.30212 | 0.022889 | -0.15564 | -0.2655 | -0.16022 | -0.29297 | 0.018311 | 0.14648 | 60.6857 | 60.9833 | 122.6807 | 122.8638 | -0.15564 | 122.8592 | 60.8826 | -0.29297 | 122.8638 | -0.15564 | 60.8826 | 122.6807 | 122.8592 | -123.143 | -123.1338
1142.7656 | 123.1567 | -60.878 | 61.9675 | 0.23247 | -0.0041572 | -0.0051483 | 0.0011386 | 0.061814 | -0.0030869 | 0.069761 | -61.0107 | 62.0041 | -61.1526 | -61.1206 | 61.8164 | 0.022888 | -0.16937 | 0.13733 | 61.9949 | -61.171 | -0.27466 | 0.036621 | -0.13275 | -0.24261 | -0.15106 | -0.29297 | 0.027466 | 0.14191 | 60.7086 | 61.0153 | 122.6944 | 122.8821 | -0.13275 | 122.8729 | 60.9009 | -0.29297 | 122.8821 | -0.13275 | 60.9009 | 122.6944 | 122.8729 | -123.1201 | -123.1384
1143.7656 | 123.1613 | -60.8871 | 61.9904 | 0.2401 | -0.0043708 | -0.010489 | 0.0011386 | 0.059464 | -0.0026595 | 0.068265 | -61.0153 | 62.0041 | -61.1526 | -61.1114 | 61.8301 | 0.027466 | -0.15106 | 0.13733 | 61.9675 | -61.1435 | -0.2655 | 0.013733 | -0.12817 | -0.2243 | -0.16022 | -0.25635 | -0.022888 | 0.13733 | 60.7361 | 61.0245 | 122.7173 | 122.8912 | -0.12817 | 122.8546 | 60.9146 | -0.25635 | 122.8912 | -0.12817 | 60.9146 | 122.7173 | 122.8546 | -123.143 | -123.1338
1144.7656 | 123.1888 | -60.8734 | 61.9766 | 0.19432 | -0.005866 | -0.0087799 | 7.0444e-05 | 0.062241 | -0.0041549 | 0.06677 | -61.0062 | 62.0087 | -61.1435 | -61.1114 | 61.8073 | 0.022888 | -0.16022 | 0.13275 | 61.9904 | -61.1664 | -0.27008 | 0.032043 | -0.13275 | -0.23804 | -0.16937 | -0.29297 | 0.013732 | 0.13733 | 60.7132 | 61.0062 | 122.6807 | 122.8821 | -0.13275 | 122.8638 | 60.8963 | -0.29297 | 122.8821 | -0.13275 | 60.8963 | 122.6807 | 122.8638 | -123.1201 | -123.143
1145.7812 | 123.2071 | -60.8597 | 61.9949 | -0.026932 | -0.0069342 | -0.0089935 | -0.00014316 | 0.06096 | -0.0056503 | 0.06912 | -61.0153 | 62.0041 | -61.1435 | -61.0703 | 61.8668 | 0.10071 | -0.068665 | 0.2243 | 62.0316 | -61.1114 | -0.28381 | 0.009155 | -0.15564 | -0.21057 | -0.12817 | -0.25177 | 0.036621 | 0.12817 | 60.791 | 61.084 | 122.7264 | 122.8638 | -0.15564 | 122.8912 | 60.9604 | -0.25177 | 122.8638 | -0.15564 | 60.9604 | 122.7264 | 122.8912 | -123.1384 | -123.1064
1146.7656 | 123.1979 | -60.8597 | 62.0041 | 0.24773 | -0.0056524 | -0.0055755 | 0.0045566 | 0.062241 | -0.0028731 | 0.069974 | -60.9741 | 62.0224 | -61.1343 | -61.2488 | 61.7889 | 0.07782 | -0.13733 | 0.18768 | 62.027 | -61.1343 | -0.27466 | 0.018311 | -0.11444 | -0.3891 | -0.21515 | -0.27466 | 0.022889 | 0.16022 | 60.7224 | 61.0474 | 122.6486 | 122.8821 | -0.11444 | 122.8867 | 60.9375 | -0.27466 | 122.8821 | -0.11444 | 60.9375 | 122.6486 | 122.8867 | -123.1384 | -123.1384
1147.7656 | 123.2117 | -60.8597 | 61.9858 | 0.22484 | -0.005866 | -0.0074981 | 0.0047702 | 0.061814 | -0.0058639 | 0.069333 | -60.9695 | 61.9904 | -61.1343 | -61.0565 | 61.6196 | -0.10986 | -0.068665 | 0.20599 | 62.0316 | -61.1069 | -0.27466 | 0.004577 | -0.10986 | -0.19684 | -0.36621 | -0.24719 | 0.045776 | 0.16479 | 60.791 | 61.0657 | 122.4792 | 122.85 | -0.10986 | 122.8912 | 60.7498 | -0.24719 | 122.85 | -0.10986 | 60.7498 | 122.4792 | 122.8912 | -123.1201 | -123.0927
1148.7656 | 123.1979 | -60.8871 | 61.9812 | 0.22484 | -0.006507 | -0.0032257 | 0.0028476 | 0.061387 | -0.0033005 | 0.068479 | -61.0062 | 62.027 | -61.1206 | -61.1023 | 61.8347 | 0.036621 | -0.16937 | 0.12817 | 61.9858 | -61.1526 | -0.23346 | 0.045777 | -0.11902 | -0.21515 | -0.14648 | -0.2655 | 0.004578 | 0.11444 | 60.7178 | 61.0153 | 122.7219 | 122.9141 | -0.11902 | 122.8729 | 60.9238 | -0.2655 | 122.9141 | -0.11902 | 60.9238 | 122.7219 | 122.8729 | -123.1018 | -123.1338
1149.7656 | 123.1659 | -60.8688 | 61.9995 | 0.18669 | -0.004798 | -0.0030121 | 0.0024202 | 0.0616 | -0.0037277 | 0.068052 | -61.0519 | 61.9858 | -61.1389 | -61.1343 | 61.8118 | 0.013733 | -0.091553 | 0.1236 | 62.0087 | -61.1252 | -0.27008 | -0.013733 | -0.18311 | -0.2655 | -0.18768 | -0.25635 | 0.009155 | 0.086975 | 60.7773 | 60.9924 | 122.6807 | 122.8546 | -0.18311 | 122.8775 | 60.8826 | -0.25635 | 122.8546 | -0.18311 | 60.8826 | 122.6807 | 122.8775 | -123.1384 | -123.1247
1150.7656 | 123.1705 | -60.8917 | 62.0041 | 0.17143 | -0.008216 | -0.0083527 | 0.0013522 | 0.062241 | -0.0054367 | 0.068265 | -61.0336 | 62.0041 | -61.171 | -61.1252 | 61.8118 | 0.018311 | -0.091553 | 0.13275 | 62.027 | -61.1389 | -0.27923 | 0 | -0.14191 | -0.23346 | -0.19226 | -0.24719 | 0.022889 | 0.13733 | 60.8002 | 61.0245 | 122.7036 | 122.8958 | -0.14191 | 122.9187 | 60.91 | -0.24719 | 122.8958 | -0.14191 | 60.91 | 122.7036 | 122.9187 | -123.175 | -123.143
1151.7656 | 123.1705 | -60.8734 | 61.9949 | 0.1638 | -0.0067206 | -0.0070709 | 0.0015658 | 0.058182 | -0.0050095 | 0.068052 | -61.0474 | 62.0132 | -61.1481 | -61.1298 | 61.8118 | 0.032043 | -0.082397 | 0.13275 | 62.0041 | -61.1481 | -0.27466 | 0.018311 | -0.17395 | -0.25635 | -0.1831 | -0.27466 | 0.009155 | 0.10071 | 60.791 | 61.0062 | 122.6852 | 122.8867 | -0.17395 | 122.8775 | 60.9055 | -0.27466 | 122.8867 | -0.17395 | 60.9055 | 122.6852 | 122.8775 | -123.143 | -123.143
1152.7656 | 123.1567 | -60.878 | 62.0132 | 0.19432 | -0.0069342 | -0.0081389 | 0.0015658 | 0.060532 | -0.0030869 | 0.065702 | -61.0382 | 62.0087 | -61.1526 | -61.1252 | 61.8073 | 0.004578 | -0.10071 | 0.12817 | 62.0041 | -61.1389 | -0.27466 | -0.004578 | -0.16022 | -0.24719 | -0.20599 | -0.26093 | -0.009156 | 0.11444 | 60.7773 | 61.0062 | 122.6852 | 122.8867 | -0.16022 | 122.8821 | 60.8826 | -0.26093 | 122.8867 | -0.16022 | 60.8826 | 122.6852 | 122.8821 | -123.1659 | -123.1522
1153.7656 | 123.1979 | -60.9009 | 61.9583 | 0.24773 | -0.0050116 | -0.0098479 | 0.0056246 | 0.059251 | -0.0037277 | 0.068052 | -60.9879 | 62.0224 | -61.1481 | -61.0748 | 61.8301 | 0.041199 | -0.17853 | 0.14191 | 61.9858 | -61.1435 | -0.24719 | 0.064087 | -0.086975 | -0.17395 | -0.12817 | -0.24261 | 0.027466 | 0.16022 | 60.7224 | 61.0428 | 122.731 | 122.9233 | -0.086975 | 122.8867 | 60.9421 | -0.24261 | 122.9233 | -0.086975 | 60.9421 | 122.731 | 122.8867 | -123.1064 | -123.1018
1154.7656 | 123.1888 | -60.878 | 61.9629 | 0.1104 | -0.0041572 | -0.0077117 | 0.004343 | 0.063096 | -0.0033005 | 0.067624 | -60.9741 | 61.9904 | -61.1572 | -61.0611 | 61.8622 | 0.045776 | -0.16022 | 0.12817 | 61.9995 | -61.1114 | -0.27924 | 0.027465 | -0.09613 | -0.1831 | -0.10071 | -0.23346 | 0.036621 | 0.18311 | 60.7178 | 61.0062 | 122.7402 | 122.8683 | -0.09613 | 122.8775 | 60.9238 | -0.23346 | 122.8683 | -0.09613 | 60.9238 | 122.7402 | 122.8775 | -123.1201 | -123.0743
1155.7812 | 123.175 | -60.8688 | 62.0224 | -0.16426 | -0.0050116 | -0.0096343 | 0.0045566 | 0.059464 | -0.0058639 | 0.067838 | -60.9741 | 62.0544 | -61.1206 | -61.0474 | 61.8896 | 0.12817 | 0.013733 | 0.25177 | 62.0316 | -61.1343 | -0.25177 | 0.032043 | -0.10529 | -0.17853 | -0.13275 | -0.2655 | 0.009155 | 0.14648 | 60.8826 | 61.1206 | 122.7585 | 122.9233 | -0.10529 | 122.9004 | 60.997 | -0.2655 | 122.9233 | -0.10529 | 60.997 | 122.7585 | 122.9004 | -123.143 | -123.1567
1156.7656 | 123.1567 | -60.9009 | 61.9675 | 0.2401 | -0.0054388 | -0.0062163 | 0.001993 | 0.061173 | -0.0033005 | 0.066556 | -60.997 | 62.0087 | -61.1435 | -61.1069 | 61.8301 | 0.032043 | -0.16022 | 0.1236 | 61.9949 | -61.1435 | -0.24261 | 0.041199 | -0.09613 | -0.20599 | -0.13733 | -0.24261 | 0.027466 | 0.14648 | 60.7407 | 61.0245 | 122.731 | 122.9095 | -0.09613 | 122.8958 | 60.9329 | -0.24261 | 122.9095 | -0.09613 | 60.9329 | 122.731 | 122.8958 | -123.111 | -123.111
1157.7656 | 123.1522 | -60.8963 | 62.0132 | 0.15617 | -0.0060798 | -0.0085663 | 0.0022066 | 0.060532 | -0.0033005 | 0.068052 | -61.0519 | 61.9904 | -61.1389 | -61.1298 | 61.8256 | 0.022888 | -0.091553 | 0.11444 | 61.9995 | -61.1343 | -0.24262 | -0.022889 | -0.15564 | -0.23346 | -0.18768 | -0.23804 | -0.013733 | 0.086975 | 60.8047 | 61.0107 | 122.7219 | 122.8867 | -0.15564 | 122.8958 | 60.9192 | -0.23804 | 122.8867 | -0.15564 | 60.9192 | 122.7219 | 122.8958 | -123.1522 | -123.1476
1158.7656 | 123.175 | -60.8734 | 61.9995 | 0.17143 | -0.0054388 | -0.0064301 | 0.0013522 | 0.061387 | -0.0043685 | 0.06912 | -61.0382 | 62.0178 | -61.1526 | -61.1114 | 61.8073 | 0.018311 | -0.10071 | 0.1236 | 62.0178 | -61.1206 | -0.27924 | 0.01831 | -0.16479 | -0.23804 | -0.19226 | -0.24719 | 0.01831 | 0.11444 | 60.7727 | 60.997 | 122.6807 | 122.8912 | -0.16479 | 122.8912 | 60.8917 | -0.24719 | 122.8912 | -0.16479 | 60.8917 | 122.6807 | 122.8912 | -123.1522 | -123.1201
1159.7656 | 123.1613 | -60.8734 | 62.0178 | 0.22484 | -0.0069342 | -0.0053619 | 0.0017794 | 0.059037 | -0.0037277 | 0.068479 | -61.0428 | 62.0087 | -61.1435 | -61.1069 | 61.8118 | 0.022888 | -0.11902 | 0.11444 | 61.9949 | -61.1343 | -0.27008 | -0.009155 | -0.16937 | -0.23346 | -0.20599 | -0.26093 | -0.022888 | 0.10071 | 60.7544 | 60.9879 | 122.6852 | 122.8821 | -0.16937 | 122.8683 | 60.8963 | -0.26093 | 122.8821 | -0.16937 | 60.8963 | 122.6852 | 122.8683 | -123.1613 | -123.1522
1160.7812 | 123.0881 | -60.9009 | 62.059 | -0.18715 | -0.0026618 | -0.0068573 | 0.0079744 | 0.060532 | -0.0054367 | 0.068479 | -61.0382 | 62.1231 | -61.1572 | -60.9879 | 61.702 | -0.018311 | 0.10529 | 0.10986 | 62.0682 | -61.1938 | -0.25635 | 0.064087 | -0.13733 | -0.086975 | -0.35706 | -0.29297 | 0.009155 | 0.11902 | 61.0062 | 61.0107 | 122.6028 | 123.024 | -0.13733 | 122.9691 | 60.8826 | -0.29297 | 123.024 | -0.13733 | 60.8826 | 122.6028 | 122.9691 | -123.2162 | -123.2529
1161.7656 | 123.1476 | -60.8871 | 61.9949 | 0.14854 | -0.0062934 | -0.0068573 | 0.001993 | 0.061814 | -0.0026595 | 0.068906 | -61.0062 | 62.0087 | -61.1481 | -61.116 | 61.8256 | 0.022888 | -0.13733 | 0.12817 | 61.9949 | -61.1435 | -0.26093 | 0.013733 | -0.11902 | -0.22888 | -0.16937 | -0.25635 | 0 | 0.14191 | 60.7498 | 61.0153 | 122.7127 | 122.8958 | -0.11902 | 122.8821 | 60.91 | -0.25635 | 122.8958 | -0.11902 | 60.91 | 122.7127 | 122.8821 | -123.143 | -123.1384
1162.7656 | 123.1476 | -60.8871 | 62.0087 | 0.17143 | -0.0073614 | -0.0068573 | 0.0011386 | 0.062455 | -0.0037277 | 0.06912 | -61.0474 | 61.9949 | -61.1435 | -61.1252 | 61.821 | 0.018311 | -0.09613 | 0.1236 | 62.0316 | -61.116 | -0.25635 | -0.013733 | -0.16022 | -0.23804 | -0.18768 | -0.22888 | 0.022888 | 0.096131 | 60.791 | 61.0107 | 122.7081 | 122.8821 | -0.16022 | 122.9187 | 60.9055 | -0.22888 | 122.8821 | -0.16022 | 60.9055 | 122.7081 | 122.9187 | -123.1522 | -123.1247
1163.7656 | 123.1293 | -60.8826 | 62.0132 | 0.17143 | -0.0045844 | -0.0081389 | 0.0013522 | 0.060746 | -0.0045821 | 0.067838 | -61.0382 | 62.0224 | -61.1435 | -61.1206 | 61.8118 | 0.022888 | -0.086975 | 0.11444 | 61.9949 | -61.1572 | -0.26093 | 0.009155 | -0.15564 | -0.23804 | -0.20142 | -0.27466 | -0.018311 | 0.10529 | 60.7956 | 60.997 | 122.6944 | 122.905 | -0.15564 | 122.8775 | 60.9055 | -0.27466 | 122.905 | -0.15564 | 60.9055 | 122.6944 | 122.8775 | -123.1567 | -123.1705
1164.7656 | 123.1796 | -60.8917 | 61.9995 | 0.15617 | -0.0060798 | -0.0068573 | 0.0034884 | 0.062241 | -0.0062911 | 0.068052 | -61.0199 | 61.9812 | -61.1526 | -61.1114 | 61.821 | 0.027466 | -0.11444 | 0.10529 | 62.0316 | -61.1252 | -0.26092 | -0.018311 | -0.12817 | -0.21973 | -0.17853 | -0.23346 | 0.032043 | 0.13275 | 60.7773 | 60.997 | 122.7127 | 122.8729 | -0.12817 | 122.9233 | 60.9192 | -0.23346 | 122.8729 | -0.12817 | 60.9192 | 122.7127 | 122.9233 | -123.1522 | -123.1247
1165.7812 | 123.1338 | -60.8322 | 62.0224 | -0.13374 | -0.0050116 | -0.0077117 | -0.00035676 | 0.061173 | -0.0050095 | 0.06677 | -60.9787 | 62.0132 | -61.1069 | -61.0062 | 61.8988 | 0.16022 | -0.036621 | 0.33417 | 62.027 | -61.0794 | -0.27466 | -0.009155 | -0.14648 | -0.17395 | -0.1236 | -0.24719 | 0.004578 | 0.12817 | 60.7956 | 61.1664 | 122.731 | 122.8455 | -0.14648 | 122.8592 | 60.9924 | -0.24719 | 122.8455 | -0.14648 | 60.9924 | 122.731 | 122.8592 | -123.1293 | -123.1018
1166.7656 | 123.1888 | -60.8734 | 61.9812 | 0.21721 | -0.0073614 | -0.0074981 | 0.00071144 | 0.06096 | -0.0037277 | 0.069974 | -61.0062 | 62.0178 | -61.1343 | -61.084 | 61.821 | 0.036621 | -0.14648 | 0.1236 | 61.9675 | -61.1206 | -0.26093 | 0.036621 | -0.13275 | -0.21057 | -0.16022 | -0.24719 | -0.013733 | 0.12817 | 60.7269 | 60.997 | 122.6944 | 122.8912 | -0.13275 | 122.8409 | 60.91 | -0.24719 | 122.8912 | -0.13275 | 60.91 | 122.6944 | 122.8409 | -123.1155 | -123.1018
1167.7656 | 123.2162 | -60.8414 | 61.9812 | 0.26299 | -0.0054388 | -0.0030121 | 0.0069064 | 0.062455 | -0.0054367 | 0.068479 | -60.9787 | 61.9949 | -61.1389 | -61.0474 | 61.6928 | -0.1236 | -0.07782 | 0.23346 | 61.9858 | -61.116 | -0.29755 | 0.013733 | -0.13733 | -0.20599 | -0.28839 | -0.27466 | 0.004578 | 0.16022 | 60.7635 | 61.0748 | 122.5342 | 122.8363 | -0.13733 | 122.8271 | 60.7178 | -0.27466 | 122.8363 | -0.13733 | 60.7178 | 122.5342 | 122.8271 | -123.1201 | -123.0972
1168.7656 | 123.2162 | -60.8871 | 61.9675 | 0.2401 | -0.0043708 | -0.0047211 | 0.0047702 | 0.061173 | -0.0030869 | 0.067838 | -60.9741 | 62.0178 | -61.1435 | -61.0565 | 61.8668 | 0.064087 | -0.19684 | 0.13275 | 61.972 | -61.1343 | -0.25635 | 0.050354 | -0.086975 | -0.16937 | -0.10071 | -0.24719 | 0.004578 | 0.16937 | 60.6903 | 61.0199 | 122.7539 | 122.905 | -0.086975 | 122.8592 | 60.9512 | -0.24719 | 122.905 | -0.086975 | 60.9512 | 122.7539 | 122.8592 | -123.111 | -123.1018
1169.7656 | 123.1522 | -60.8826 | 62.0087 | 0.19432 | -0.0073614 | -0.0089935 | -0.00057036 | 0.06096 | -0.0028731 | 0.068052 | -61.0382 | 62.0087 | -61.1389 | -61.1069 | 61.8256 | 0.032043 | -0.10986 | 0.12817 | 62.0132 | -61.1298 | -0.25635 | 0 | -0.15564 | -0.22431 | -0.18311 | -0.24719 | 0.004578 | 0.10071 | 60.7727 | 61.0107 | 122.7081 | 122.8912 | -0.15564 | 122.8958 | 60.9146 | -0.24719 | 122.8912 | -0.15564 | 60.9146 | 122.7081 | 122.8958 | -123.1476 | -123.1384
1170.7812 | 123.1659 | -60.8826 | 62.0132 | -0.011673 | -0.0067206 | -0.0092071 | 0.0011386 | 0.060105 | -0.0024459 | 0.068693 | -61.0245 | 62.0453 | -61.1481 | -61.0931 | 61.8393 | 0.064087 | -0.073242 | 0.15564 | 62.0453 | -61.084 | -0.2655 | 0.032043 | -0.14191 | -0.21057 | -0.17395 | -0.20142 | 0.032043 | 0.1236 | 60.8093 | 61.0382 | 122.7219 | 122.9279 | -0.14191 | 122.9279 | 60.9467 | -0.20142 | 122.9279 | -0.14191 | 60.9467 | 122.7219 | 122.9279 | -123.1613 | -123.0972
1171.7656 | 123.1476 | -60.8597 | 61.9858 | 0.22484 | -0.0039434 | -0.0025847 | 0.0030612 | 0.060105 | -0.0033005 | 0.067197 | -61.0153 | 62.0041 | -61.1572 | -61.0977 | 61.8256 | 0.050354 | -0.16022 | 0.12817 | 61.9766 | -61.1572 | -0.29755 | 0.01831 | -0.15564 | -0.23804 | -0.16022 | -0.29755 | -0.009155 | 0.14191 | 60.6995 | 60.9879 | 122.6852 | 122.8638 | -0.15564 | 122.8363 | 60.91 | -0.29755 | 122.8638 | -0.15564 | 60.91 | 122.6852 | 122.8363 | -123.143 | -123.143
1172.7656 | 123.175 | -60.8688 | 61.9904 | 0.22484 | -0.006507 | -0.0040801 | 0.001993 | 0.061387 | -0.0060775 | 0.069761 | -60.9787 | 62.0132 | -61.1481 | -61.0748 | 61.8393 | 0.032043 | -0.16022 | 0.13275 | 61.9812 | -61.1206 | -0.27924 | 0.022889 | -0.10986 | -0.20599 | -0.15106 | -0.25177 | -0.009155 | 0.16937 | 60.7086 | 61.0016 | 122.7081 | 122.8821 | -0.10986 | 122.85 | 60.9009 | -0.25177 | 122.8821 | -0.10986 | 60.9009 | 122.7081 | 122.85 | -123.1384 | -123.111
1173.7656 | 123.1796 | -60.8871 | 61.9858 | 0.24773 | -0.0060798 | -0.0057891 | 0.0032748 | 0.062241 | -0.0062911 | 0.06677 | -61.0062 | 62.0087 | -61.1252 | -61.084 | 61.8393 | 0.036621 | -0.16937 | 0.12817 | 61.9949 | -61.1526 | -0.23804 | 0.022888 | -0.11902 | -0.19684 | -0.14648 | -0.2655 | 0.009155 | 0.11902 | 60.7178 | 61.0153 | 122.7264 | 122.8958 | -0.11902 | 122.8821 | 60.9238 | -0.2655 | 122.8958 | -0.11902 | 60.9238 | 122.7264 | 122.8821 | -123.111 | -123.1384
1174.7656 | 123.1979 | -60.8826 | 61.9675 | 0.21721 | -0.0052252 | -0.0049347 | 0.0062656 | 0.062882 | -0.0037277 | 0.068052 | -60.9695 | 62.0132 | -61.1298 | -61.0657 | 61.8393 | 0.050354 | -0.20142 | 0.13275 | 61.9675 | -61.1298 | -0.24719 | 0.045777 | -0.086975 | -0.18311 | -0.12817 | -0.24719 | 0 | 0.16022 | 60.6812 | 61.0153 | 122.7219 | 122.8958 | -0.086975 | 122.85 | 60.9329 | -0.24719 | 122.8958 | -0.086975 | 60.9329 | 122.7219 | 122.85 | -123.0972 | -123.0972
1175.7656 | 123.2025 | -60.8826 | 61.972 | 0.3698 | -0.005866 | -0.0070709 | 0.0028476 | 0.062241 | -0.0041549 | 0.068906 | -60.8963 | 62.0132 | -61.1618 | -61.0748 | 61.853 | 0.022888 | -0.19684 | 0.14191 | 61.9263 | -61.1526 | -0.27924 | 0.041199 | -0.013733 | -0.19226 | -0.11902 | -0.27008 | -0.045776 | 0.2655 | 60.6857 | 61.0245 | 122.7356 | 122.8958 | -0.013733 | 122.8088 | 60.9055 | -0.27008 | 122.8958 | -0.013733 | 60.9055 | 122.7356 | 122.8088 | -123.1338 | -123.1247
1176.7656 | 123.1659 | -60.9009 | 61.9949 | 0.20195 | -0.006507 | -0.010489 | 0.00092504 | 0.06096 | -0.0011643 | 0.068479 | -61.0062 | 62.0087 | -61.1526 | -61.0886 | 61.8393 | 0.041199 | -0.16022 | 0.1236 | 61.9766 | -61.1343 | -0.25177 | 0.013733 | -0.10529 | -0.18768 | -0.15564 | -0.23346 | -0.01831 | 0.14648 | 60.7407 | 61.0245 | 122.7402 | 122.9095 | -0.10529 | 122.8775 | 60.9421 | -0.23346 | 122.9095 | -0.10529 | 60.9421 | 122.7402 | 122.8775 | -123.1476 | -123.1293
1177.7656 | 123.1842 | -60.8963 | 61.972 | 0.23247 | -0.0039434 | -0.0072845 | 0.0030612 | 0.062455 | -0.0047957 | 0.06912 | -61.0107 | 62.0316 | -61.1481 | -61.0977 | 61.853 | 0.054932 | -0.16022 | 0.13733 | 61.9675 | -61.1572 | -0.25177 | 0.059509 | -0.11444 | -0.20142 | -0.11902 | -0.26093 | -0.004578 | 0.13733 | 60.7361 | 61.0336 | 122.7493 | 122.9279 | -0.11444 | 122.8638 | 60.9512 | -0.26093 | 122.9279 | -0.11444 | 60.9512 | 122.7493 | 122.8638 | -123.1201 | -123.1293
1178.7656 | 123.175 | -60.8871 | 61.9766 | 0.27061 | -0.0060798 | -0.0049347 | 0.004343 | 0.062669 | -0.0018051 | 0.067624 | -60.9879 | 62.0178 | -61.1618 | -61.0748 | 61.8393 | 0.054932 | -0.16022 | 0.13733 | 61.9949 | -61.116 | -0.27466 | 0.041198 | -0.10071 | -0.18768 | -0.13733 | -0.22888 | 0.01831 | 0.17395 | 60.7269 | 61.0245 | 122.7264 | 122.905 | -0.10071 | 122.8821 | 60.9421 | -0.22888 | 122.905 | -0.10071 | 60.9421 | 122.7264 | 122.8821 | -123.1384 | -123.0927
1179.7656 | 123.1842 | -60.8826 | 61.9904 | 0.11803 | -0.0056524 | -0.0066437 | 0.003702 | 0.062455 | -0.0035141 | 0.068906 | -60.997 | 62.0041 | -61.1343 | -61.0611 | 61.8576 | 0.068665 | -0.18768 | 0.15564 | 61.9766 | -61.1435 | -0.25177 | 0.013733 | -0.11444 | -0.17853 | -0.13275 | -0.26093 | -0.013732 | 0.13733 | 60.6949 | 61.0382 | 122.7402 | 122.8867 | -0.11444 | 122.8592 | 60.9512 | -0.26093 | 122.8867 | -0.11444 | 60.9512 | 122.7402 | 122.8592 | -123.1247 | -123.1338
1180.7656 | 123.1979 | -60.8826 | 61.9858 | -0.39314 | -0.0043708 | -0.0021575 | 0.002634 | 0.065232 | -0.0052231 | 0.069761 | -60.9283 | 62.027 | -61.1389 | -61.0611 | 61.8393 | 0.036621 | -0.18768 | 0.1236 | 61.9766 | -61.1435 | -0.25635 | 0.041199 | -0.045777 | -0.17853 | -0.14648 | -0.26093 | -0.009155 | 0.21057 | 60.6949 | 61.0062 | 122.7219 | 122.9095 | -0.045777 | 122.8592 | 60.9192 | -0.26093 | 122.9095 | -0.045777 | 60.9192 | 122.7219 | 122.8592 | -123.1247 | -123.1293
1181.7656 | 123.1842 | -60.8551 | 61.9675 | 0.21721 | -0.0050116 | -0.0051483 | 0.0056246 | 0.062241 | -0.0043685 | 0.068265 | -60.9741 | 62.0316 | -61.171 | -61.0565 | 61.8484 | 0.045776 | -0.17395 | 0.11902 | 62.0041 | -61.1298 | -0.31586 | 0.064087 | -0.11902 | -0.20142 | -0.11902 | -0.27466 | 0.036621 | 0.19684 | 60.6812 | 60.9741 | 122.7036 | 122.8867 | -0.11902 | 122.8592 | 60.9009 | -0.27466 | 122.8867 | -0.11902 | 60.9009 | 122.7036 | 122.8592 | -123.1384 | -123.0972
1182.7656 | 123.2162 | -60.8597 | 61.9904 | 0.24773 | -0.0037298 | -0.0027985 | 0.0032748 | 0.062028 | -0.0058639 | 0.06912 | -60.997 | 62.0407 | -61.1435 | -61.0703 | 61.8393 | 0.1236 | -0.44403 | 0.13733 | 61.9629 | -61.1389 | -0.28381 | 0.050354 | -0.13733 | -0.21057 | -0.15106 | -0.27924 | -0.027465 | 0.14648 | 60.4156 | 60.997 | 122.699 | 122.9004 | -0.13733 | 122.8226 | 60.9833 | -0.27924 | 122.9004 | -0.13733 | 60.9833 | 122.699 | 122.8226 | -123.1338 | -123.1293
1183.7656 | 123.1796 | -60.8734 | 61.9904 | 0.21721 | -0.007575 | -0.0096343 | 0.001993 | 0.062455 | -0.0052231 | 0.068693 | -61.0062 | 62.0178 | -61.1435 | -61.0748 | 61.853 | 0.041199 | -0.16022 | 0.14191 | 61.9858 | -61.1435 | -0.27008 | 0.027466 | -0.13275 | -0.20142 | -0.13733 | -0.27008 | -0.004577 | 0.13733 | 60.7132 | 61.0153 | 122.7264 | 122.8912 | -0.13275 | 122.8592 | 60.9146 | -0.27008 | 122.8912 | -0.13275 | 60.9146 | 122.7264 | 122.8592 | -123.1338 | -123.1338
1184.7656 | 123.1934 | -60.8917 | 61.9904 | 0.25536 | -0.0043708 | -0.0015167 | 0.0022066 | 0.062455 | -0.0054367 | 0.069333 | -60.9879 | 62.027 | -61.1389 | -61.0794 | 61.853 | 0.045776 | -0.1831 | 0.15106 | 61.9858 | -61.1114 | -0.24719 | 0.036622 | -0.09613 | -0.18768 | -0.13733 | -0.21973 | -0.004577 | 0.15106 | 60.7086 | 61.0428 | 122.7448 | 122.9187 | -0.09613 | 122.8775 | 60.9375 | -0.21973 | 122.9187 | -0.09613 | 60.9375 | 122.7448 | 122.8775 | -123.1293 | -123.1018
1185.7656 | 123.2162 | -60.8826 | 61.9858 | 0.10277 | -0.0037298 | -0.0057891 | 0.0030612 | 0.063309 | -0.0056503 | 0.068693 | -60.9009 | 62.027 | -61.1572 | -61.0794 | 61.8576 | 0.041199 | -0.19684 | 0.15106 | 61.9858 | -61.1252 | -0.27466 | 0.041199 | -0.018311 | -0.19684 | -0.12817 | -0.24262 | 0 | 0.25635 | 60.6857 | 61.0336 | 122.7402 | 122.9095 | -0.018311 | 122.8683 | 60.9238 | -0.24262 | 122.9095 | -0.018311 | 60.9238 | 122.7402 | 122.8683 | -123.143 | -123.111
1186.7656 | 123.23 | -60.8551 | 61.9812 | 0.26299 | -0.0056524 | -0.0042937 | 0.0051974 | 0.066514 | -0.0052231 | 0.066984 | -60.9833 | 62.0224 | -61.1343 | -60.9787 | 61.9492 | 0.10529 | -0.16479 | 0.1831 | 61.9766 | -61.1206 | -0.27923 | 0.041199 | -0.12817 | -0.1236 | -0.032043 | -0.2655 | -0.004577 | 0.15106 | 60.6903 | 61.0382 | 122.8043 | 122.8775 | -0.12817 | 122.8317 | 60.9604 | -0.2655 | 122.8775 | -0.12817 | 60.9604 | 122.8043 | 122.8317 | -123.1155 | -123.1018
1187.7656 | 123.1934 | -60.8826 | 61.9858 | 0.27824 | -0.0033026 | -0.0062163 | 0.0081882 | 0.064164 | -0.0030869 | 0.068693 | -61.0199 | 62.059 | -61.1801 | -61.1114 | 61.8301 | 0.027466 | -0.1236 | 0.073242 | 61.9812 | -61.1618 | -0.29755 | 0.073242 | -0.13733 | -0.22888 | -0.15564 | -0.27924 | -0.004578 | 0.16022 | 60.759 | 60.9558 | 122.7127 | 122.9416 | -0.13733 | 122.8638 | 60.91 | -0.27924 | 122.9416 | -0.13733 | 60.91 | 122.7127 | 122.8638 | -123.1659 | -123.1476
1188.7656 | 123.1796 | -60.8917 | 61.9858 | 0.26299 | -0.0028754 | -0.0055755 | 0.0045566 | 0.06395 | -0.0035141 | 0.067197 | -61.0291 | 62.0728 | -61.1664 | -61.116 | 61.7889 | -0.004578 | -0.12817 | 0.086975 | 61.9949 | -61.1526 | -0.27466 | 0.086975 | -0.13733 | -0.2243 | -0.19684 | -0.26092 | 0.009155 | 0.13733 | 60.7636 | 60.9787 | 122.6807 | 122.9645 | -0.13733 | 122.8867 | 60.8871 | -0.26092 | 122.9645 | -0.13733 | 60.8871 | 122.6807 | 122.8867 | -123.1522 | -123.1384
1189.7656 | 123.1888 | -60.8734 | 61.9812 | 0.22484 | -0.0050116 | -0.0013031 | 0.00092504 | 0.065018 | -0.0052231 | 0.068479 | -60.9833 | 62.027 | -61.1572 | -61.0794 | 61.853 | 0.059509 | -0.18768 | 0.12817 | 61.972 | -61.1526 | -0.28381 | 0.045777 | -0.10986 | -0.20599 | -0.12817 | -0.27924 | -0.009155 | 0.17395 | 60.6857 | 61.0016 | 122.7264 | 122.9004 | -0.10986 | 122.8455 | 60.9329 | -0.27924 | 122.9004 | -0.10986 | 60.9329 | 122.7264 | 122.8455 | -123.1384 | -123.1338
1190.7656 | 123.2025 | -60.8643 | 61.9949 | 0.24773 | -0.0041572 | -0.0042937 | 0.0062656 | 0.066941 | -0.0056503 | 0.066984 | -60.9833 | 61.9995 | -61.1389 | -60.9879 | 61.908 | 0.082397 | -0.16937 | 0.16022 | 62.0316 | -61.0977 | -0.27466 | 0.004578 | -0.11902 | -0.1236 | -0.086975 | -0.23346 | 0.036621 | 0.15564 | 60.6949 | 61.0245 | 122.7722 | 122.8638 | -0.11902 | 122.8958 | 60.9467 | -0.23346 | 122.8638 | -0.11902 | 60.9467 | 122.7722 | 122.8958 | -123.1338 | -123.0927
1191.7656 | 123.175 | -60.9055 | 61.9446 | 0.24773 | -0.0060798 | -0.0047211 | 0.0041292 | 0.06395 | -0.0022323 | 0.06912 | -60.9741 | 62.0407 | -61.1526 | -61.0703 | 61.8713 | 0.041199 | -0.19226 | 0.15564 | 61.9904 | -61.1435 | -0.24719 | 0.09613 | -0.068664 | -0.16479 | -0.073242 | -0.23804 | 0.045776 | 0.17853 | 60.7132 | 61.0611 | 122.7768 | 122.9462 | -0.068664 | 122.8958 | 60.9467 | -0.23804 | 122.9462 | -0.068664 | 60.9467 | 122.7768 | 122.8958 | -123.0972 | -123.0881
1192.7656 | 123.2117 | -60.8826 | 61.9949 | 0.2401 | -0.0062934 | -0.0083527 | 0.0032748 | 0.063523 | -0.0039413 | 0.06677 | -60.9879 | 62.0407 | -61.1526 | -61.0703 | 61.8347 | 0.059509 | -0.19684 | 0.14648 | 61.9766 | -61.1298 | -0.27008 | 0.045776 | -0.10529 | -0.18768 | -0.16022 | -0.24719 | -0.01831 | 0.16479 | 60.6857 | 61.0291 | 122.7173 | 122.9233 | -0.10529 | 122.8592 | 60.9421 | -0.24719 | 122.9233 | -0.10529 | 60.9421 | 122.7173 | 122.8592 | -123.1476 | -123.1247
1193.7656 | 123.2071 | -60.9009 | 61.9904 | 0.21721 | -0.00073919 | -0.0057891 | 0.0060518 | 0.064164 | -0.0020187 | 0.069761 | -60.9787 | 62.0361 | -61.1526 | -61.0794 | 61.8576 | 0.054932 | -0.17853 | 0.13275 | 61.9904 | -61.1481 | -0.25177 | 0.045777 | -0.07782 | -0.17853 | -0.13275 | -0.24719 | 0 | 0.17395 | 60.7224 | 61.0336 | 122.7585 | 122.937 | -0.07782 | 122.8912 | 60.9558 | -0.24719 | 122.937 | -0.07782 | 60.9558 | 122.7585 | 122.8912 | -123.143 | -123.1384
1194.7656 | 123.1522 | -60.9192 | 62.0316 | 0.22484 | -0.0037298 | -0.0042937 | 0.0049838 | 0.0663 | -0.0015915 | 0.070615 | -61.0519 | 62.1094 | -61.1526 | -61.1618 | 61.7706 | -0.036621 | -0.091553 | 0.041199 | 62.0178 | -61.1664 | -0.23346 | 0.07782 | -0.13275 | -0.24261 | -0.26093 | -0.24719 | -0.013733 | 0.10071 | 60.8276 | 60.9604 | 122.6898 | 123.0286 | -0.13275 | 122.937 | 60.8826 | -0.24719 | 123.0286 | -0.13275 | 60.8826 | 122.6898 | 122.937 | -123.1842 | -123.1979
1195.7656 | 123.1293 | -60.9009 | 62.0087 | 0.25536 | -0.00138 | -0.0064301 | 0.0028476 | 0.063737 | -0.0011643 | 0.067838 | -61.0748 | 62.114 | -61.1801 | -61.1664 | 61.7661 | -0.050354 | -0.050354 | 0.050354 | 62.0316 | -61.1893 | -0.27924 | 0.10529 | -0.17395 | -0.2655 | -0.24262 | -0.28839 | 0.022888 | 0.10529 | 60.8505 | 60.9512 | 122.6669 | 123.0148 | -0.17395 | 122.9324 | 60.8505 | -0.28839 | 123.0148 | -0.17395 | 60.8505 | 122.6669 | 122.9324 | -123.1888 | -123.1979
1196.7656 | 123.1796 | -60.8917 | 61.9629 | 0.27824 | -0.0035162 | -0.0025847 | 0.0060518 | 0.065018 | -0.0041549 | 0.06912 | -61.0245 | 62.0728 | -61.171 | -61.116 | 61.8301 | 0.032043 | -0.16937 | 0.082397 | 62.0041 | -61.1618 | -0.27923 | 0.10986 | -0.13275 | -0.2243 | -0.13275 | -0.27008 | 0.041198 | 0.14648 | 60.7224 | 60.9741 | 122.7219 | 122.9645 | -0.13275 | 122.8958 | 60.9238 | -0.27008 | 122.9645 | -0.13275 | 60.9238 | 122.7219 | 122.8958 | -123.1338 | -123.1247
1197.7656 | 123.2025 | -60.8597 | 61.9858 | 0.26299 | -0.0035162 | -0.0032257 | 0.0022066 | 0.062669 | -0.0043685 | 0.06677 | -60.9879 | 62.0499 | -61.1618 | -61.0977 | 61.8576 | 0.050354 | -0.1831 | 0.13733 | 61.9766 | -61.1664 | -0.30212 | 0.064087 | -0.12817 | -0.23804 | -0.12817 | -0.3067 | -0.009155 | 0.17395 | 60.6766 | 60.997 | 122.7173 | 122.9095 | -0.12817 | 122.8363 | 60.91 | -0.3067 | 122.9095 | -0.12817 | 60.91 | 122.7173 | 122.8363 | -123.1476 | -123.1522
1198.7656 | 123.2025 | -60.8871 | 61.9675 | 0.26299 | -0.0043708 | -0.0032257 | 0.0022066 | 0.062241 | -0.0039413 | 0.070402 | -60.9924 | 62.059 | -61.1298 | -61.0794 | 61.8439 | 0.036621 | -0.20599 | 0.12817 | 61.9675 | -61.1481 | -0.24262 | 0.091553 | -0.10529 | -0.19226 | -0.1236 | -0.26093 | 0 | 0.13733 | 60.6812 | 61.0153 | 122.731 | 122.9462 | -0.10529 | 122.8546 | 60.9238 | -0.26093 | 122.9462 | -0.10529 | 60.9238 | 122.731 | 122.8546 | -123.0972 | -123.1155
1199.7656 | 123.2071 | -60.878 | 61.9812 | 0.40794 | -0.00138 | -0.00066214 | 0.0056246 | 0.063096 | -0.0041549 | 0.068906 | -60.9833 | 62.0499 | -61.1389 | -61.084 | 61.8484 | 0.050354 | -0.1831 | 0.15106 | 61.9812 | -61.1847 | -0.26093 | 0.068665 | -0.10528 | -0.20599 | -0.13275 | -0.3067 | 0 | 0.15564 | 60.6949 | 61.0291 | 122.7264 | 122.9279 | -0.10528 | 122.8592 | 60.9283 | -0.3067 | 122.9279 | -0.10528 | 60.9283 | 122.7264 | 122.8592 | -123.1201 | -123.1659
1200.7656 | 123.2162 | -60.8826 | 61.9858 | 0.45372 | -0.0052252 | -0.0051483 | 0.0056246 | 0.061387 | -0.0024459 | 0.069547 | -61.0016 | 62.0499 | -61.171 | -61.0931 | 61.8484 | 0.036621 | -0.17395 | 0.14191 | 61.9995 | -61.171 | -0.28839 | 0.064087 | -0.11902 | -0.21057 | -0.13733 | -0.28839 | 0.013733 | 0.16937 | 60.7086 | 61.0245 | 122.731 | 122.9324 | -0.11902 | 122.8821 | 60.9192 | -0.28839 | 122.9324 | -0.11902 | 60.9192 | 122.731 | 122.8821 | -123.1567 | -123.1567
1201.7656 | 123.1338 | -60.9055 | 62.0132 | 0.20195 | -0.0026618 | -0.0085663 | 0.0047702 | 0.06395 | -0.0028731 | 0.069333 | -61.0657 | 62.0956 | -61.1664 | -61.1755 | 61.7706 | -0.032043 | -0.068665 | 0.050354 | 62.027 | -61.2122 | -0.26093 | 0.082397 | -0.16022 | -0.27008 | -0.24262 | -0.3067 | 0.013733 | 0.10071 | 60.8368 | 60.9558 | 122.6761 | 123.0011 | -0.16022 | 122.9324 | 60.8734 | -0.3067 | 123.0011 | -0.16022 | 60.8734 | 122.6761 | 122.9324 | -123.1796 | -123.2254
1202.7656 | 123.1247 | -60.9146 | 61.9766 | 0.25536 | -0.0039434 | -0.0068573 | 0.004343 | 0.063523 | -0.0026595 | 0.068693 | -61.0565 | 62.1277 | -61.1984 | -61.1755 | 61.7706 | -0.041199 | -0.036621 | 0.027466 | 62.0407 | -61.1801 | -0.28381 | 0.15106 | -0.14191 | -0.26093 | -0.20599 | -0.2655 | 0.064086 | 0.14191 | 60.878 | 60.9421 | 122.6852 | 123.0423 | -0.14191 | 122.9553 | 60.8734 | -0.2655 | 123.0423 | -0.14191 | 60.8734 | 122.6852 | 122.9553 | -123.175 | -123.1567
1203.7656 | 123.2071 | -60.8963 | 61.972 | 0.2401 | -0.003089 | -0.0060027 | 0.0034884 | 0.063523 | -0.0020187 | 0.070402 | -61.0245 | 62.0636 | -61.1481 | -61.1114 | 61.8164 | 0.032043 | -0.13733 | 0.10071 | 62.0178 | -61.1847 | -0.25177 | 0.091553 | -0.12817 | -0.21515 | -0.15564 | -0.28839 | 0.045776 | 0.1236 | 60.759 | 60.997 | 122.7127 | 122.9599 | -0.12817 | 122.9141 | 60.9283 | -0.28839 | 122.9599 | -0.12817 | 60.9283 | 122.7127 | 122.9141 | -123.1201 | -123.1567
1204.7656 | 123.175 | -60.8871 | 61.9949 | 0.28587 | -0.0050116 | -0.0019439 | 0.0013522 | 0.063737 | -0.0033005 | 0.068906 | -60.9924 | 62.0682 | -61.1572 | -61.0886 | 61.853 | 0.036621 | -0.18768 | 0.14648 | 62.0041 | -61.1526 | -0.27008 | 0.073242 | -0.10529 | -0.20142 | -0.14191 | -0.2655 | 0.009155 | 0.16479 | 60.6995 | 61.0336 | 122.7402 | 122.9553 | -0.10529 | 122.8912 | 60.9238 | -0.2655 | 122.9553 | -0.10529 | 60.9238 | 122.7402 | 122.8912 | -123.1522 | -123.1476
1205.7656 | 123.2025 | -60.8871 | 61.9583 | 0.30113 | -0.0039434 | -0.0042937 | 0.0034884 | 0.062882 | -0.0020187 | 0.06912 | -60.9924 | 62.0316 | -61.1389 | -61.0886 | 61.8622 | 0.045776 | -0.18768 | 0.13275 | 61.9949 | -61.1664 | -0.25177 | 0.073242 | -0.10529 | -0.20142 | -0.09613 | -0.27924 | 0.036621 | 0.14648 | 60.6995 | 61.0199 | 122.7493 | 122.9187 | -0.10529 | 122.8821 | 60.9329 | -0.27924 | 122.9187 | -0.10529 | 60.9329 | 122.7493 | 122.8821 | -123.0972 | -123.1247
1206.7656 | 123.1796 | -60.8871 | 61.9904 | 0.21721 | -0.0026618 | -0.0062163 | 0.0034884 | 0.065232 | -0.0069321 | 0.068693 | -60.9695 | 62.0316 | -61.1526 | -61.0886 | 61.8484 | 0.050354 | -0.1831 | 0.14191 | 62.0178 | -61.1618 | -0.2655 | 0.041199 | -0.082397 | -0.20142 | -0.14191 | -0.27466 | 0.027466 | 0.18311 | 60.704 | 61.0291 | 122.7356 | 122.9187 | -0.082397 | 122.905 | 60.9375 | -0.27466 | 122.9187 | -0.082397 | 60.9375 | 122.7356 | 122.905 | -123.143 | -123.1522
1207.7656 | 123.2208 | -60.8643 | 61.9537 | 0.25536 | -0.0043708 | -0.0049347 | 0.0032748 | 0.064164 | -0.0037277 | 0.069761 | -60.997 | 62.0407 | -61.1526 | -61.084 | 61.8347 | 0.036621 | -0.19226 | 0.13275 | 61.9904 | -61.1435 | -0.28839 | 0.086975 | -0.13275 | -0.21973 | -0.11902 | -0.27924 | 0.036621 | 0.15564 | 60.672 | 60.997 | 122.699 | 122.905 | -0.13275 | 122.8546 | 60.9009 | -0.27924 | 122.905 | -0.13275 | 60.9009 | 122.699 | 122.8546 | -123.1064 | -123.0972
1208.7656 | 123.1155 | -60.91 | 62.0132 | 0.24773 | -0.0024482 | -0.0042937 | 0.0069064 | 0.063096 | -0.0037277 | 0.068265 | -61.0611 | 62.0956 | -61.1755 | -61.1526 | 61.7844 | -0.032043 | -0.082397 | 0.045776 | 61.9995 | -61.1801 | -0.2655 | 0.082397 | -0.15106 | -0.24261 | -0.22888 | -0.27008 | -0.013733 | 0.11444 | 60.8276 | 60.9558 | 122.6944 | 123.0057 | -0.15106 | 122.9095 | 60.878 | -0.27008 | 123.0057 | -0.15106 | 60.878 | 122.6944 | 122.9095 | -123.1888 | -123.1934
1209.7656 | 123.1155 | -60.9055 | 61.9949 | 0.2935 | -0.0018072 | -0.0070709 | 0.0060518 | 0.064805 | -0.0037277 | 0.068906 | -61.0703 | 62.1002 | -61.1664 | -61.171 | 61.7844 | -0.036621 | -0.073242 | 0.041199 | 62.027 | -61.1755 | -0.26093 | 0.10529 | -0.16479 | -0.2655 | -0.21057 | -0.27008 | 0.032044 | 0.096131 | 60.8322 | 60.9467 | 122.6898 | 123.0057 | -0.16479 | 122.9324 | 60.8688 | -0.27008 | 123.0057 | -0.16479 | 60.8688 | 122.6898 | 122.9324 | -123.1613 | -123.1705
1210.7656 | 123.2117 | -60.878 | 61.972 | 0.25536 | -0.0039434 | -0.0066437 | -0.00057036 | 0.064164 | -0.0043685 | 0.067411 | -60.9146 | 62.0361 | -61.1847 | -61.0657 | 61.8713 | 0.054932 | -0.17395 | 0.15564 | 62.0087 | -61.1481 | -0.3067 | 0.064087 | -0.036621 | -0.18768 | -0.10071 | -0.27008 | 0.036621 | 0.27008 | 60.704 | 61.0336 | 122.7493 | 122.9141 | -0.036621 | 122.8867 | 60.9329 | -0.27008 | 122.9141 | -0.036621 | 60.9329 | 122.7493 | 122.8867 | -123.1567 | -123.1201
1211.7656 | 123.2208 | -60.8734 | 61.9812 | 0.25536 | -0.0054388 | -0.0066437 | 0.00049764 | 0.061814 | -0.0020187 | 0.069761 | -61.0016 | 62.0407 | -61.1526 | -61.0794 | 61.8622 | 0.073242 | -0.16022 | 0.15106 | 62.0178 | -61.1664 | -0.27924 | 0.059509 | -0.12817 | -0.20599 | -0.11902 | -0.29297 | 0.036621 | 0.15106 | 60.7132 | 61.0245 | 122.7356 | 122.9141 | -0.12817 | 122.8912 | 60.9467 | -0.29297 | 122.9141 | -0.12817 | 60.9467 | 122.7356 | 122.8912 | -123.1338 | -123.1476
1212.7656 | 123.2025 | -60.878 | 61.9858 | 0.2401 | -0.0054388 | -0.0023711 | 0.0041292 | 0.062882 | -0.0039413 | 0.068693 | -60.9833 | 62.0453 | -61.1481 | -61.0062 | 61.8942 | 0.073242 | -0.14191 | 0.17395 | 61.9949 | -61.1481 | -0.27008 | 0.059509 | -0.10528 | -0.12817 | -0.091553 | -0.27008 | 0.009155 | 0.1648 | 60.7361 | 61.0519 | 122.7722 | 122.9233 | -0.10528 | 122.8729 | 60.9512 | -0.27008 | 122.9233 | -0.10528 | 60.9512 | 122.7722 | 122.8729 | -123.1338 | -123.1338
1213.7656 | 123.2162 | -60.8734 | 61.9812 | 0.25536 | -0.0050116 | -0.0068573 | 0.0028476 | 0.063737 | -0.0028731 | 0.067838 | -60.9787 | 62.0178 | -61.1618 | -60.9879 | 61.9217 | 0.082397 | -0.16022 | 0.17853 | 62.0132 | -61.1298 | -0.28839 | 0.036621 | -0.10529 | -0.11444 | -0.059509 | -0.25635 | 0.032044 | 0.1831 | 60.7132 | 61.0519 | 122.7951 | 122.8912 | -0.10529 | 122.8867 | 60.9558 | -0.25635 | 122.8912 | -0.10529 | 60.9558 | 122.7951 | 122.8867 | -123.143 | -123.111
1214.7656 | 123.2117 | -60.878 | 62.0178 | 0.27824 | -0.0033026 | -0.0042937 | 0.0039156 | 0.065446 | -0.0050095 | 0.070402 | -60.9879 | 62.027 | -61.1526 | -60.9833 | 61.9034 | 0.050354 | -0.15106 | 0.17395 | 62.0178 | -61.1343 | -0.27466 | 0.009156 | -0.10986 | -0.10528 | -0.11444 | -0.25635 | 0 | 0.16479 | 60.7269 | 61.0519 | 122.7814 | 122.905 | -0.10986 | 122.8958 | 60.9283 | -0.25635 | 122.905 | -0.10986 | 60.9283 | 122.7814 | 122.8958 | -123.1705 | -123.1522
1215.7656 | 123.2346 | -60.8917 | 61.9995 | 0.2401 | -0.005866 | -0.0066437 | 0.0066928 | 0.063737 | -0.0037277 | 0.06677 | -61.0016 | 62.0361 | -61.1618 | -61.0977 | 61.8256 | 0.032043 | -0.17853 | 0.13733 | 62.0087 | -61.1389 | -0.27008 | 0.036621 | -0.10986 | -0.20599 | -0.17395 | -0.24719 | 0.009155 | 0.16022 | 60.7132 | 61.0291 | 122.7173 | 122.9279 | -0.10986 | 122.9004 | 60.9238 | -0.24719 | 122.9279 | -0.10986 | 60.9238 | 122.7173 | 122.9004 | -123.1613 | -123.1384
1216.7656 | 123.1934 | -60.8871 | 61.972 | 0.23247 | -0.0028754 | -0.0053619 | 0.0034884 | 0.065446 | -0.0037277 | 0.068906 | -60.9833 | 62.0407 | -61.1847 | -61.0977 | 61.8393 | 0.032043 | -0.1831 | 0.12817 | 62.0178 | -61.1481 | -0.29755 | 0.068664 | -0.09613 | -0.21057 | -0.13275 | -0.26093 | 0.045776 | 0.20142 | 60.704 | 61.0153 | 122.7264 | 122.9279 | -0.09613 | 122.905 | 60.9192 | -0.26093 | 122.9279 | -0.09613 | 60.9192 | 122.7264 | 122.905 | -123.1567 | -123.1201
1217.7656 | 123.1613 | -60.91 | 61.9675 | 0.21721 | -0.005866 | -0.0070709 | 0.00028404 | 0.062455 | -0.0035141 | 0.068906 | -61.0199 | 62.0361 | -61.171 | -61.1252 | 61.8393 | 0.018311 | -0.14648 | 0.14648 | 62.0316 | -61.1343 | -0.26093 | 0.068665 | -0.10986 | -0.21515 | -0.12817 | -0.2243 | 0.064087 | 0.15106 | 60.7636 | 61.0565 | 122.7493 | 122.9462 | -0.10986 | 122.9416 | 60.9283 | -0.2243 | 122.9462 | -0.10986 | 60.9283 | 122.7493 | 122.9416 | -123.1384 | -123.1018
1218.7656 | 123.1613 | -60.9009 | 61.9949 | 0.21721 | -0.0050116 | -0.0094207 | 0.0015658 | 0.062455 | -0.0060775 | 0.070829 | -60.997 | 61.9995 | -61.1526 | -61.1206 | 61.8256 | 0.022888 | -0.15106 | 0.13275 | 62.0224 | -61.1343 | -0.25177 | 0.004578 | -0.09613 | -0.21973 | -0.16937 | -0.23346 | 0.027466 | 0.15564 | 60.7498 | 61.0336 | 122.7264 | 122.9004 | -0.09613 | 122.9233 | 60.9238 | -0.23346 | 122.9004 | -0.09613 | 60.9238 | 122.7264 | 122.9233 | -123.1476 | -123.1293
1219.7656 | 123.1659 | -60.8734 | 61.9675 | 0.21721 | -0.0056524 | -0.0079253 | 0.0024202 | 0.0616 | -0.0028731 | 0.068479 | -61.0107 | 62.0361 | -61.1618 | -61.1023 | 61.8164 | 0.004578 | -0.15564 | 0.13275 | 62.0087 | -61.1298 | -0.28839 | 0.068665 | -0.13733 | -0.22888 | -0.15106 | -0.25635 | 0.041199 | 0.15106 | 60.7178 | 61.0062 | 122.6898 | 122.9095 | -0.13733 | 122.8821 | 60.878 | -0.25635 | 122.9095 | -0.13733 | 60.878 | 122.6898 | 122.8821 | -123.1293 | -123.0972
1220.7656 | 123.1567 | -60.8734 | 61.9904 | 0.20195 | -0.0050116 | -0.0064301 | 0.002634 | 0.059251 | -0.0050095 | 0.067838 | -61.0016 | 62.0224 | -61.1481 | -61.1252 | 61.821 | 0.018311 | -0.14191 | 0.13733 | 61.9995 | -61.1755 | -0.27466 | 0.032044 | -0.12817 | -0.25177 | -0.16937 | -0.30212 | 0.009156 | 0.14648 | 60.7315 | 61.0107 | 122.6944 | 122.8958 | -0.12817 | 122.8729 | 60.8917 | -0.30212 | 122.8958 | -0.12817 | 60.8917 | 122.6944 | 122.8729 | -123.1384 | -123.1659
1221.7656 | 123.1659 | -60.8734 | 61.9949 | 0.20958 | -0.006507 | -0.0092071 | 0.0017794 | 0.062241 | -0.0030869 | 0.068052 | -61.0062 | 62.0041 | -61.171 | -61.1252 | 61.8118 | 0.032043 | -0.12817 | 0.1236 | 61.972 | -61.1664 | -0.29755 | 0.009155 | -0.13275 | -0.25177 | -0.1831 | -0.29297 | -0.022888 | 0.16479 | 60.7452 | 60.997 | 122.6852 | 122.8775 | -0.13275 | 122.8455 | 60.9055 | -0.29297 | 122.8775 | -0.13275 | 60.9055 | 122.6852 | 122.8455 | -123.1659 | -123.1613
1222.7656 | 123.1979 | -60.8597 | 61.9904 | 0.25536 | -0.0045844 | -0.0055755 | 0.0013522 | 0.059464 | -0.0041549 | 0.066984 | -60.8871 | 62.027 | -61.171 | -61.0565 | 61.8668 | 0.054932 | -0.16479 | 0.16022 | 61.9904 | -61.1526 | -0.31128 | 0.036622 | -0.027466 | -0.19684 | -0.1236 | -0.29297 | 0 | 0.28381 | 60.6949 | 61.0199 | 122.7264 | 122.8867 | -0.027466 | 122.85 | 60.9146 | -0.29297 | 122.8867 | -0.027466 | 60.9146 | 122.7264 | 122.85 | -123.1613 | -123.143
1223.7656 | 123.2025 | -60.8597 | 61.9949 | 0.27824 | -0.0033026 | -0.0096343 | 0.0045566 | 0.062028 | -0.0073593 | 0.06912 | -60.9879 | 62.0132 | -61.1572 | -61.0565 | 61.8622 | 0.064087 | -0.16022 | 0.16937 | 62.0316 | -61.1206 | -0.29755 | 0.018311 | -0.12817 | -0.19684 | -0.13275 | -0.26093 | 0.036621 | 0.16937 | 60.6995 | 61.0291 | 122.7219 | 122.8729 | -0.12817 | 122.8912 | 60.9238 | -0.26093 | 122.8729 | -0.12817 | 60.9238 | 122.7219 | 122.8912 | -123.1522 | -123.1155
1224.7656 | 123.1476 | -60.878 | 62.0087 | 0.17906 | -0.0054388 | -0.0096343 | -0.0012112 | 0.060105 | -0.0039413 | 0.069974 | -61.0519 | 62.0087 | -61.116 | -61.1298 | 61.8164 | 0.018311 | -0.073242 | 0.12817 | 62.0087 | -61.1252 | -0.23804 | 0 | -0.17395 | -0.25177 | -0.19226 | -0.24719 | 0 | 0.064087 | 60.8047 | 61.0062 | 122.6944 | 122.8867 | -0.17395 | 122.8867 | 60.8963 | -0.24719 | 122.8867 | -0.17395 | 60.8963 | 122.6944 | 122.8867 | -123.1247 | -123.1338
1225.7656 | 123.175 | -60.8871 | 61.9812 | 0.17143 | -0.0060798 | -0.0074981 | -0.00014316 | 0.061173 | -0.0030869 | 0.070402 | -61.0382 | 61.9995 | -61.1481 | -61.1252 | 61.8164 | 0.027466 | -0.09613 | 0.13275 | 62.0132 | -61.1389 | -0.26093 | 0.018311 | -0.15106 | -0.23804 | -0.16479 | -0.25177 | 0.032044 | 0.10986 | 60.791 | 61.0199 | 122.7036 | 122.8867 | -0.15106 | 122.9004 | 60.9146 | -0.25177 | 122.8867 | -0.15106 | 60.9146 | 122.7036 | 122.9004 | -123.1293 | -123.1201
1226.7656 | 123.1522 | -60.8871 | 62.0041 | 0.17906 | -0.0045844 | -0.0072845 | 0.001993 | 0.061173 | -0.0039413 | 0.067411 | -61.0428 | 62.0132 | -61.1435 | -61.1069 | 61.8301 | 0.018311 | -0.10071 | 0.13733 | 62.027 | -61.116 | -0.25635 | 0.009156 | -0.15564 | -0.21973 | -0.17395 | -0.22888 | 0.022889 | 0.10071 | 60.7864 | 61.0245 | 122.7173 | 122.9004 | -0.15564 | 122.9141 | 60.9055 | -0.22888 | 122.9004 | -0.15564 | 60.9055 | 122.7173 | 122.9141 | -123.1476 | -123.1201
1227.7656 | 123.1796 | -60.8963 | 62.0132 | 0.19432 | -0.0056524 | -0.0068573 | 0.0017794 | 0.061173 | -0.0035141 | 0.068906 | -61.0519 | 62.0316 | -61.1572 | -61.1435 | 61.8118 | 0.022888 | -0.086975 | 0.12817 | 62.027 | -61.1298 | -0.26093 | 0.01831 | -0.15564 | -0.24719 | -0.20142 | -0.23346 | 0.013733 | 0.10529 | 60.8093 | 61.0245 | 122.7081 | 122.9279 | -0.15564 | 122.9233 | 60.9192 | -0.23346 | 122.9279 | -0.15564 | 60.9192 | 122.7081 | 122.9233 | -123.1705 | -123.143
1228.7656 | 123.143 | -60.8826 | 62.0132 | 0.17906 | -0.0062934 | -0.0040801 | 0.0024202 | 0.062455 | -0.0041549 | 0.06912 | -61.0428 | 62.0224 | -61.1435 | -61.1069 | 61.8118 | 0.022888 | -0.1236 | 0.1236 | 61.9995 | -61.1206 | -0.26093 | 0.009155 | -0.16022 | -0.22431 | -0.20142 | -0.23804 | -0.013733 | 0.10071 | 60.759 | 61.0062 | 122.6944 | 122.905 | -0.16022 | 122.8821 | 60.9055 | -0.23804 | 122.905 | -0.16022 | 60.9055 | 122.6944 | 122.8821 | -123.1567 | -123.1338
1229.7656 | 123.1796 | -60.8597 | 61.9537 | 0.2401 | -0.0050116 | -0.0081389 | 0.0034884 | 0.059891 | -0.0050095 | 0.065275 | -60.997 | 62.0178 | -61.1343 | -61.0657 | 61.8393 | 0.022888 | -0.17853 | 0.15106 | 61.9812 | -61.1572 | -0.27466 | 0.064087 | -0.13733 | -0.20599 | -0.11444 | -0.29755 | 0.027466 | 0.13733 | 60.6812 | 61.0107 | 122.699 | 122.8775 | -0.13733 | 122.8409 | 60.8826 | -0.29755 | 122.8775 | -0.13733 | 60.8826 | 122.699 | 122.8409 | -123.0881 | -123.111
1230.7656 | 123.175 | -60.8688 | 61.9583 | 0.30113 | -0.0067206 | -0.0053619 | 0.0039156 | 0.059891 | -0.0022323 | 0.067838 | -60.9741 | 62.0224 | -61.1206 | -61.0931 | 61.8393 | 0.045776 | -0.17395 | 0.15564 | 61.9904 | -61.1755 | -0.25177 | 0.064087 | -0.10529 | -0.22431 | -0.11902 | -0.3067 | 0.032043 | 0.14648 | 60.6949 | 61.0245 | 122.7081 | 122.8912 | -0.10529 | 122.8592 | 60.9146 | -0.3067 | 122.8912 | -0.10529 | 60.9146 | 122.7081 | 122.8592 | -123.0789 | -123.1338
1231.7656 | 123.175 | -60.878 | 62.0224 | 0.11803 | -0.0069342 | -0.0025847 | 0.0013522 | 0.059891 | -0.0054367 | 0.066984 | -61.0519 | 62.0178 | -61.1526 | -61.1206 | 61.8393 | 0.009155 | -0.068665 | 0.1236 | 61.9949 | -61.116 | -0.27466 | -0.004578 | -0.17395 | -0.24261 | -0.18311 | -0.23804 | -0.027466 | 0.10071 | 60.8093 | 61.0016 | 122.7173 | 122.8958 | -0.17395 | 122.8729 | 60.8871 | -0.23804 | 122.8958 | -0.17395 | 60.8871 | 122.7173 | 122.8729 | -123.175 | -123.1384
1232.7656 | 123.1567 | -60.8871 | 61.9949 | 0.14092 | -0.0054388 | -0.010489 | 0.0030612 | 0.059678 | -0.0041549 | 0.06912 | -61.0519 | 62.0224 | -61.1389 | -61.1298 | 61.8301 | 0.032043 | -0.07782 | 0.11444 | 62.0087 | -61.1435 | -0.25177 | 0.027466 | -0.16479 | -0.24262 | -0.16479 | -0.25635 | 0.013733 | 0.086975 | 60.8093 | 61.0016 | 122.7173 | 122.9095 | -0.16479 | 122.8958 | 60.9192 | -0.25635 | 122.9095 | -0.16479 | 60.9192 | 122.7173 | 122.8958 | -123.1338 | -123.1384
1233.7656 | 123.1796 | -60.878 | 62.027 | 0.1104 | -0.0056524 | -0.0042937 | 7.0444e-05 | 0.060532 | -0.0037277 | 0.068906 | -61.0474 | 61.9995 | -61.1389 | -61.1298 | 61.8164 | 0.022888 | -0.082397 | 0.12817 | 62.0361 | -61.1252 | -0.26093 | -0.027466 | -0.16937 | -0.25177 | -0.21057 | -0.24719 | 0.009155 | 0.091553 | 60.7956 | 61.0062 | 122.6944 | 122.8775 | -0.16937 | 122.9141 | 60.9009 | -0.24719 | 122.8775 | -0.16937 | 60.9009 | 122.6944 | 122.9141 | -123.1659 | -123.1522
1234.7656 | 123.1659 | -60.8871 | 62.0041 | 0.17143 | -0.0020208 | -0.0055755 | 0.0030612 | 0.061814 | -0.0011643 | 0.068052 | -61.0474 | 62.0316 | -61.1435 | -61.1298 | 61.821 | 0.018311 | -0.10071 | 0.11444 | 62.0178 | -61.1389 | -0.25635 | 0.027466 | -0.16022 | -0.24262 | -0.1831 | -0.25177 | 0.013733 | 0.096131 | 60.7864 | 61.0016 | 122.7081 | 122.9187 | -0.16022 | 122.905 | 60.9055 | -0.25177 | 122.9187 | -0.16022 | 60.9055 | 122.7081 | 122.905 | -123.1476 | -123.143
1235.7656 | 123.1613 | -60.8917 | 61.9995 | 0.14854 | -0.0084296 | -0.0060027 | 0.0028476 | 0.061814 | -0.0047957 | 0.067411 | -61.0245 | 62.0132 | -61.1572 | -61.1069 | 61.8164 | 0.027466 | -0.091553 | 0.13733 | 62.0224 | -61.1114 | -0.2655 | 0.013733 | -0.13275 | -0.21515 | -0.18311 | -0.21973 | 0.022888 | 0.13275 | 60.8002 | 61.0291 | 122.7081 | 122.905 | -0.13275 | 122.9141 | 60.9192 | -0.21973 | 122.905 | -0.13275 | 60.9192 | 122.7081 | 122.9141 | -123.1567 | -123.111
1236.7656 | 123.1705 | -60.878 | 61.972 | 0.21721 | -0.0052252 | -0.0045075 | 0.0017794 | 0.062028 | -0.0052231 | 0.06912 | -60.997 | 61.9812 | -61.1481 | -61.0886 | 61.8393 | 0.050354 | -0.17395 | 0.14191 | 61.9858 | -61.1526 | -0.27008 | 0.009155 | -0.11902 | -0.21057 | -0.13275 | -0.27466 | 0.013733 | 0.15106 | 60.704 | 61.0199 | 122.7173 | 122.8592 | -0.11902 | 122.8638 | 60.9283 | -0.27466 | 122.8592 | -0.11902 | 60.9283 | 122.7173 | 122.8638 | -123.1201 | -123.1247
1237.7656 | 123.2208 | -60.8734 | 61.9812 | 0.26299 | -0.0073614 | -0.0057891 | 0.0022066 | 0.059251 | -0.0054367 | 0.069333 | -60.9879 | 62.0178 | -61.1481 | -61.0886 | 61.8439 | 0.041199 | -0.1831 | 0.14191 | 61.9904 | -61.0931 | -0.27466 | 0.036621 | -0.11444 | -0.21515 | -0.13733 | -0.21973 | 0.009155 | 0.16022 | 60.6903 | 61.0153 | 122.7173 | 122.8912 | -0.11444 | 122.8638 | 60.9146 | -0.21973 | 122.8912 | -0.11444 | 60.9146 | 122.7173 | 122.8638 | -123.1293 | -123.0743
1238.7656 | 123.1338 | -60.8871 | 62.0178 | 0.072251 | -0.0067206 | -0.0064301 | 0.001993 | 0.059678 | -0.0026595 | 0.071256 | -61.0565 | 62.0178 | -61.1572 | -61.1114 | 61.8256 | 0.027466 | -0.086975 | 0.1236 | 62.0361 | -61.1114 | -0.27008 | 0 | -0.16937 | -0.2243 | -0.19226 | -0.2243 | 0.018311 | 0.10071 | 60.8002 | 61.0107 | 122.7127 | 122.905 | -0.16937 | 122.9233 | 60.9146 | -0.2243 | 122.905 | -0.16937 | 60.9146 | 122.7127 | 122.9233 | -123.175 | -123.1293
1239.7656 | 123.1476 | -60.8826 | 62.0132 | 0.1104 | -0.0045844 | -0.0072845 | 0.0013522 | 0.05861 | -0.0043685 | 0.068693 | -61.0428 | 61.9904 | -61.1572 | -61.1206 | 61.821 | 0.018311 | -0.073242 | 0.13275 | 62.0087 | -61.1069 | -0.27466 | -0.022889 | -0.16022 | -0.23804 | -0.19226 | -0.22431 | -0.004578 | 0.11444 | 60.8093 | 61.0153 | 122.7036 | 122.8729 | -0.16022 | 122.8912 | 60.9009 | -0.22431 | 122.8729 | -0.16022 | 60.9009 | 122.7036 | 122.8912 | -123.1705 | -123.1201
1240.7656 | 123.143 | -60.8826 | 61.9995 | 0.12566 | -0.0045844 | -0.010703 | -0.00035676 | 0.058396 | -0.0043685 | 0.06912 | -61.0474 | 62.0178 | -61.1343 | -61.1114 | 61.821 | 0.018311 | -0.086975 | 0.1236 | 61.972 | -61.1343 | -0.25177 | 0.01831 | -0.16479 | -0.22888 | -0.17853 | -0.25177 | -0.027466 | 0.086975 | 60.7956 | 61.0062 | 122.7036 | 122.9004 | -0.16479 | 122.8546 | 60.9009 | -0.25177 | 122.9004 | -0.16479 | 60.9009 | 122.7036 | 122.8546 | -123.1338 | -123.1338
1241.7656 | 123.1476 | -60.8963 | 61.9995 | 0.14092 | -0.0060798 | -0.0072845 | 0.0013522 | 0.059037 | -0.0024459 | 0.067411 | -61.0474 | 62.0178 | -61.1572 | -61.1114 | 61.8073 | 0.041199 | -0.09613 | 0.13275 | 61.9995 | -61.1298 | -0.26093 | 0.01831 | -0.15106 | -0.21515 | -0.19226 | -0.23346 | 0 | 0.10986 | 60.8002 | 61.0291 | 122.7036 | 122.9141 | -0.15106 | 122.8958 | 60.9375 | -0.23346 | 122.9141 | -0.15106 | 60.9375 | 122.7036 | 122.8958 | -123.1567 | -123.1293
1242.7656 | 123.1705 | -60.878 | 62.0132 | 0.17143 | -0.0077888 | -0.0085663 | 7.0444e-05 | 0.062028 | -0.0030869 | 0.066984 | -61.0382 | 62.0087 | -61.1618 | -61.1206 | 61.8073 | 0.045776 | -0.082397 | 0.13733 | 62.027 | -61.1023 | -0.28381 | -0.004578 | -0.16022 | -0.24261 | -0.20599 | -0.2243 | 0.013733 | 0.1236 | 60.7956 | 61.0153 | 122.6852 | 122.8867 | -0.16022 | 122.905 | 60.9238 | -0.2243 | 122.8867 | -0.16022 | 60.9238 | 122.6852 | 122.905 | -123.175 | -123.1155
1243.7656 | 123.1934 | -60.8597 | 61.9675 | 0.20195 | -0.0067206 | -0.010703 | 0.0041292 | 0.061387 | -0.0067185 | 0.068479 | -60.9879 | 62.0041 | -61.1618 | -61.084 | 61.8393 | 0.036621 | -0.16022 | 0.15106 | 61.9858 | -61.1206 | -0.30212 | 0.036621 | -0.12817 | -0.2243 | -0.12817 | -0.26093 | 0.018311 | 0.17395 | 60.6995 | 61.0107 | 122.699 | 122.8638 | -0.12817 | 122.8455 | 60.8963 | -0.26093 | 122.8638 | -0.12817 | 60.8963 | 122.699 | 122.8455 | -123.1293 | -123.0881
1244.7656 | 123.1796 | -60.878 | 61.972 | 0.18669 | -0.0060798 | -0.0062163 | 0.0028476 | 0.059037 | -0.0054367 | 0.068906 | -61.0382 | 61.9904 | -61.1618 | -61.1114 | 61.8301 | 0.018311 | -0.11444 | 0.1236 | 62.0087 | -61.1206 | -0.28381 | 0.01831 | -0.16022 | -0.23346 | -0.14191 | -0.24261 | 0.036621 | 0.1236 | 60.7636 | 61.0016 | 122.7081 | 122.8683 | -0.16022 | 122.8867 | 60.8963 | -0.24261 | 122.8683 | -0.16022 | 60.8963 | 122.7081 | 122.8867 | -123.1338 | -123.0927
1245.7656 | 123.1613 | -60.8963 | 61.9949 | 0.095139 | -0.0062934 | -0.0092071 | 0.0011386 | 0.059251 | -0.0022323 | 0.067197 | -61.0428 | 62.027 | -61.1664 | -61.1206 | 61.8301 | 0.009155 | -0.068665 | 0.1236 | 62.0178 | -61.1435 | -0.27008 | 0.032044 | -0.14648 | -0.2243 | -0.16479 | -0.24719 | 0.022888 | 0.1236 | 60.8276 | 61.0199 | 122.7264 | 122.9233 | -0.14648 | 122.9141 | 60.9055 | -0.24719 | 122.9233 | -0.14648 | 60.9055 | 122.7264 | 122.9141 | -123.1613 | -123.1384
1246.7812 | 123.1018 | -60.8917 | 62.0499 | -0.15663 | -0.0022346 | -0.010703 | 0.0077608 | 0.061387 | -0.0058639 | 0.068265 | -61.0199 | 62.1231 | -61.1481 | -61.1069 | 61.8118 | 0.045776 | 0.12817 | 0.16022 | 62.0636 | -61.1572 | -0.25635 | 0.073242 | -0.12817 | -0.21515 | -0.23804 | -0.2655 | 0.013733 | 0.12817 | 61.0199 | 61.0519 | 122.7036 | 123.0148 | -0.12817 | 122.9553 | 60.9375 | -0.2655 | 123.0148 | -0.12817 | 60.9375 | 122.7036 | 122.9553 | -123.1979 | -123.2071
1247.7656 | 123.143 | -60.8643 | 61.9949 | 0.07988 | -0.0071478 | -0.0092071 | 7.0444e-05 | 0.062028 | -0.0039413 | 0.068693 | -61.0565 | 61.9904 | -61.171 | -61.1206 | 61.8256 | 0.036621 | -0.091553 | 0.1236 | 62.0178 | -61.1023 | -0.3067 | -0.004578 | -0.19226 | -0.25635 | -0.16937 | -0.23804 | 0.022888 | 0.11444 | 60.7727 | 60.9879 | 122.6898 | 122.8546 | -0.19226 | 122.8821 | 60.9009 | -0.23804 | 122.8546 | -0.19226 | 60.9009 | 122.6898 | 122.8821 | -123.1659 | -123.0972
1248.7656 | 123.1522 | -60.878 | 61.9995 | 0.056992 | -0.0039434 | -0.010275 | -0.0016386 | 0.061173 | -0.0073593 | 0.06677 | -61.0519 | 61.9949 | -61.1526 | -61.1206 | 61.821 | 0.022888 | -0.086975 | 0.11444 | 62.0361 | -61.0977 | -0.27466 | -0.004578 | -0.17395 | -0.24261 | -0.17853 | -0.21973 | 0.036621 | 0.10071 | 60.791 | 60.9924 | 122.699 | 122.8729 | -0.17395 | 122.9141 | 60.9009 | -0.21973 | 122.8729 | -0.17395 | 60.9009 | 122.699 | 122.9141 | -123.1522 | -123.0972
1249.7656 | 123.175 | -60.8963 | 61.9583 | 0.17143 | -0.0054388 | -0.0040801 | 0.0013522 | 0.062455 | -0.0037277 | 0.069547 | -61.0062 | 61.9904 | -61.1572 | -61.0886 | 61.8347 | 0.045776 | -0.15106 | 0.13275 | 61.9812 | -61.1252 | -0.26093 | 0.032043 | -0.10986 | -0.19226 | -0.1236 | -0.22888 | 0.022888 | 0.15106 | 60.7452 | 61.0291 | 122.731 | 122.8867 | -0.10986 | 122.8775 | 60.9421 | -0.22888 | 122.8867 | -0.10986 | 60.9421 | 122.731 | 122.8775 | -123.1155 | -123.0835
1250.7656 | 123.1934 | -60.8871 | 61.9858 | 0.27061 | -0.0069342 | -0.0079253 | 0.002634 | 0.062241 | -0.0054367 | 0.069761 | -61.0016 | 61.9949 | -61.1664 | -61.084 | 61.8576 | 0.045776 | -0.17395 | 0.13275 | 62.0041 | -61.1252 | -0.27924 | 0.009155 | -0.11444 | -0.19684 | -0.12817 | -0.23804 | 0.01831 | 0.16479 | 60.7132 | 61.0199 | 122.7448 | 122.8821 | -0.11444 | 122.8912 | 60.9329 | -0.23804 | 122.8821 | -0.11444 | 60.9329 | 122.7448 | 122.8912 | -123.1522 | -123.111
1251.7812 | 123.1888 | -60.8643 | 62.0087 | -0.17189 | -0.0043708 | -0.0094207 | 0.0047702 | 0.060319 | -0.0060775 | 0.067197 | -60.9695 | 62.0544 | -61.116 | -61.0519 | 61.8805 | 0.13733 | 0.036621 | 0.25177 | 62.0544 | -61.1252 | -0.25177 | 0.045776 | -0.10529 | -0.18768 | -0.12817 | -0.26093 | 0.045776 | 0.14648 | 60.9009 | 61.116 | 122.7448 | 122.9187 | -0.10529 | 122.9187 | 61.0016 | -0.26093 | 122.9187 | -0.10529 | 61.0016 | 122.7448 | 122.9187 | -123.1247 | -123.1338
1252.7656 | 123.1522 | -60.9009 | 62.0132 | 0.11803 | -0.0062934 | -0.0045075 | -0.00099756 | 0.060746 | -0.0037277 | 0.067197 | -61.0474 | 62.0224 | -61.1526 | -61.1252 | 61.821 | 0.027466 | -0.073242 | 0.10529 | 62.0224 | -61.116 | -0.25177 | 0.009155 | -0.14648 | -0.2243 | -0.19226 | -0.21515 | 0.009155 | 0.10529 | 60.8276 | 61.0062 | 122.7219 | 122.9233 | -0.14648 | 122.9233 | 60.9283 | -0.21515 | 122.9233 | -0.14648 | 60.9283 | 122.7219 | 122.9233 | -123.1659 | -123.1293
1253.7656 | 123.1842 | -60.8871 | 61.9812 | 0.13329 | -0.007575 | -0.0030121 | 0.00092504 | 0.059891 | -0.0045821 | 0.067197 | -61.0382 | 62.027 | -61.1664 | -61.1252 | 61.8301 | 0.027466 | -0.068665 | 0.13733 | 61.9949 | -61.1389 | -0.27924 | 0.045777 | -0.15106 | -0.23804 | -0.15106 | -0.25177 | 0.013733 | 0.12817 | 60.8185 | 61.0245 | 122.7173 | 122.9141 | -0.15106 | 122.8821 | 60.9146 | -0.25177 | 122.9141 | -0.15106 | 60.9146 | 122.7173 | 122.8821 | -123.1476 | -123.1201
1254.7656 | 123.1705 | -60.8917 | 61.9949 | 0.11803 | -0.0071478 | -0.0083527 | -0.00014316 | 0.059891 | -0.0067185 | 0.068479 | -61.0428 | 62.0178 | -61.171 | -61.1252 | 61.8164 | 0.022888 | -0.091553 | 0.13733 | 62.0407 | -61.1023 | -0.27923 | 0.022888 | -0.15106 | -0.23346 | -0.17853 | -0.21057 | 0.045776 | 0.12817 | 60.8002 | 61.0291 | 122.7081 | 122.9095 | -0.15106 | 122.9324 | 60.9146 | -0.21057 | 122.9095 | -0.15106 | 60.9146 | 122.7081 | 122.9324 | -123.1659 | -123.0972
1255.7656 | 123.1705 | -60.8734 | 61.9904 | 0.14854 | -0.006507 | -0.0053619 | -0.00099756 | 0.060532 | -0.0039413 | 0.067624 | -61.0474 | 62.0132 | -61.1298 | -61.1206 | 61.8301 | 0.032043 | -0.10529 | 0.1236 | 62.0087 | -61.1343 | -0.25635 | 0.022889 | -0.17395 | -0.24719 | -0.16022 | -0.26093 | 0.018311 | 0.082398 | 60.7681 | 60.997 | 122.7036 | 122.8867 | -0.17395 | 122.8821 | 60.9055 | -0.26093 | 122.8867 | -0.17395 | 60.9055 | 122.7036 | 122.8821 | -123.1201 | -123.1247
1256.7812 | 123.0881 | -60.878 | 62.0636 | -1.24 | -0.00138 | -0.0030121 | 0.0058382 | 0.063309 | -0.0050095 | 0.066556 | -61.1114 | 62.1506 | -61.1755 | -61.1206 | 61.7844 | 0.050354 | 0.13733 | 0.15564 | 62.1002 | -61.1618 | -0.29755 | 0.086975 | -0.23346 | -0.24261 | -0.27924 | -0.28381 | 0.036621 | 0.064087 | 61.0153 | 61.0336 | 122.6624 | 123.0286 | -0.23346 | 122.9782 | 60.9283 | -0.28381 | 123.0286 | -0.23346 | 60.9283 | 122.6624 | 122.9782 | -123.2391 | -123.2254
1257.7656 | 123.2162 | -60.8871 | 61.9995 | -0.39314 | -0.0056524 | -0.0068573 | 0.0047702 | 0.0616 | -0.0052231 | 0.066984 | -60.9833 | 62.0224 | -61.1664 | -61.0794 | 61.8576 | 0.050354 | -0.18768 | 0.14191 | 61.972 | -61.116 | -0.27924 | 0.022888 | -0.09613 | -0.19226 | -0.14191 | -0.22888 | -0.027466 | 0.18311 | 60.6995 | 61.0291 | 122.7448 | 122.9095 | -0.09613 | 122.8592 | 60.9375 | -0.22888 | 122.9095 | -0.09613 | 60.9375 | 122.7448 | 122.8592 | -123.1659 | -123.1155
1258.7656 | 123.175 | -60.8688 | 61.9904 | 0.22484 | -0.0052252 | -0.0055755 | 0.0022066 | 0.062669 | -0.0039413 | 0.070615 | -61.0062 | 62.0178 | -61.1526 | -61.1023 | 61.8439 | 0.036621 | -0.15106 | 0.13733 | 62.0041 | -61.116 | -0.28381 | 0.027466 | -0.13733 | -0.23346 | -0.14648 | -0.24719 | 0.013733 | 0.14648 | 60.7178 | 61.0062 | 122.7127 | 122.8867 | -0.13733 | 122.8729 | 60.9055 | -0.24719 | 122.8867 | -0.13733 | 60.9055 | 122.7127 | 122.8729 | -123.143 | -123.1064
1259.7656 | 123.1476 | -60.8871 | 61.9995 | 0.14854 | -0.0073614 | -0.0051483 | 0.0017794 | 0.06096 | -0.0047957 | 0.068693 | -61.0474 | 62.0132 | -61.1389 | -61.1298 | 61.821 | 0.022888 | -0.07782 | 0.12817 | 62.0178 | -61.1298 | -0.25177 | 0.013733 | -0.16022 | -0.24262 | -0.17853 | -0.24262 | 0.01831 | 0.091553 | 60.8093 | 61.0153 | 122.7081 | 122.9004 | -0.16022 | 122.905 | 60.91 | -0.24262 | 122.9004 | -0.16022 | 60.91 | 122.7081 | 122.905 | -123.1384 | -123.1293
1260.7656 | 123.1476 | -60.8688 | 61.9812 | 0.18669 | -0.0045844 | -0.0057891 | 0.0017794 | 0.061814 | -0.0045821 | 0.067838 | -61.0245 | 62.0316 | -61.1526 | -61.116 | 61.8164 | 0.013733 | -0.11902 | 0.10986 | 62.0132 | -61.1298 | -0.28381 | 0.050354 | -0.15564 | -0.24719 | -0.16479 | -0.26093 | 0.032044 | 0.12817 | 60.7498 | 60.9787 | 122.6852 | 122.9004 | -0.15564 | 122.8821 | 60.8826 | -0.26093 | 122.9004 | -0.15564 | 60.8826 | 122.6852 | 122.8821 | -123.1338 | -123.111
1261.7812 | 123.0743 | -60.8871 | 62.0682 | -0.17952 | -0.004798 | -0.0038665 | 0.0047702 | 0.059678 | -0.0069321 | 0.067838 | -61.0519 | 62.0911 | -61.1618 | -60.965 | 61.9217 | 0.009155 | 0.073242 | 0.10986 | 62.0407 | -61.1343 | -0.27466 | 0.022888 | -0.16479 | -0.07782 | -0.14648 | -0.24719 | -0.027466 | 0.10986 | 60.9604 | 60.997 | 122.8088 | 122.9782 | -0.16479 | 122.9279 | 60.8963 | -0.24719 | 122.9782 | -0.16479 | 60.8963 | 122.8088 | 122.9279 | -123.23 | -123.2025
1262.7656 | 123.1613 | -60.8963 | 61.9949 | 0.22484 | -0.0035162 | -0.0074981 | 0.0022066 | 0.063096 | -0.0028731 | 0.067838 | -61.0153 | 62.0132 | -61.1755 | -61.1023 | 61.8439 | 0.045776 | -0.14648 | 0.14191 | 61.9995 | -61.1343 | -0.27924 | 0.018311 | -0.11902 | -0.20599 | -0.15106 | -0.23804 | 0.004578 | 0.16022 | 60.7498 | 61.0382 | 122.7402 | 122.9095 | -0.11902 | 122.8958 | 60.9421 | -0.23804 | 122.9095 | -0.11902 | 60.9421 | 122.7402 | 122.8958 | -123.1705 | -123.1293
1263.7656 | 123.1613 | -60.9009 | 61.9492 | 0.28587 | -0.0056524 | -0.0042937 | 0.0041292 | 0.062669 | -0.0050095 | 0.068906 | -60.9833 | 62.0316 | -61.1298 | -61.0748 | 61.8668 | 0.054932 | -0.19684 | 0.14648 | 61.9858 | -61.1435 | -0.22888 | 0.082397 | -0.082397 | -0.17395 | -0.082398 | -0.24261 | 0.036621 | 0.14649 | 60.704 | 61.0474 | 122.7676 | 122.9324 | -0.082397 | 122.8867 | 60.9558 | -0.24261 | 122.9324 | -0.082397 | 60.9558 | 122.7676 | 122.8867 | -123.0789 | -123.0927
1264.7656 | 123.1888 | -60.8688 | 61.9858 | 0.23247 | -0.005866 | -0.010062 | 0.004343 | 0.063523 | -0.0065047 | 0.068265 | -60.9741 | 62.0453 | -61.1481 | -61.0794 | 61.8622 | 0.041199 | -0.18768 | 0.12817 | 61.9949 | -61.116 | -0.27924 | 0.059509 | -0.10529 | -0.21057 | -0.1236 | -0.24719 | 0.009155 | 0.17395 | 60.6812 | 60.997 | 122.731 | 122.9141 | -0.10529 | 122.8638 | 60.91 | -0.24719 | 122.9141 | -0.10529 | 60.91 | 122.731 | 122.8638 | -123.1338 | -123.1018
1265.7656 | 123.2025 | -60.878 | 61.9904 | 0.26299 | -0.0056524 | -0.0015167 | 0.0011386 | 0.060746 | -0.0065047 | 0.068052 | -61.1114 | 62.0316 | -61.1481 | -61.0428 | 61.8668 | 0.054932 | -0.17853 | 0.15564 | 61.9949 | -61.1343 | -0.27008 | 0.041199 | -0.23346 | -0.16479 | -0.1236 | -0.25635 | 0.004578 | 0.036621 | 60.6995 | 61.0336 | 122.7448 | 122.9095 | -0.23346 | 122.8729 | 60.9329 | -0.25635 | 122.9095 | -0.23346 | 60.9329 | 122.7448 | 122.8729 | -123.1384 | -123.1247
1266.7656 | 123.1888 | -60.8551 | 61.9766 | 0.21721 | -0.0052252 | -0.0081389 | 0.0028476 | 0.06395 | -0.0037277 | 0.069333 | -61.0016 | 62.0224 | -61.1572 | -61.0931 | 61.8622 | 0.050354 | -0.15106 | 0.13733 | 62.0224 | -61.1206 | -0.30212 | 0.045776 | -0.14648 | -0.23804 | -0.11444 | -0.2655 | 0.045776 | 0.15564 | 60.704 | 60.9924 | 122.7173 | 122.8775 | -0.14648 | 122.8775 | 60.9055 | -0.2655 | 122.8775 | -0.14648 | 60.9055 | 122.7173 | 122.8775 | -123.1339 | -123.0972
1267.7656 | 123.2254 | -60.8688 | 61.9858 | 0.18669 | -0.0050116 | -0.0068573 | 0.0045566 | 0.063096 | -0.0060775 | 0.065488 | -60.9879 | 62.0178 | -61.1389 | -61.0931 | 61.8668 | 0.064087 | -0.16937 | 0.14191 | 62.0041 | -61.1481 | -0.27008 | 0.032043 | -0.11902 | -0.22431 | -0.11902 | -0.27924 | 0.01831 | 0.15106 | 60.6995 | 61.0107 | 122.7356 | 122.8867 | -0.11902 | 122.8729 | 60.9329 | -0.27924 | 122.8867 | -0.11902 | 60.9329 | 122.7356 | 122.8729 | -123.1247 | -123.1338
1268.7656 | 123.2025 | -60.878 | 61.9675 | 0.26299 | -0.0039434 | -0.0025847 | 0.0049838 | 0.0616 | -0.0062911 | 0.068906 | -60.9924 | 62.0132 | -61.1801 | -61.0474 | 61.8668 | 0.068665 | -0.16479 | 0.16937 | 62.0224 | -61.1114 | -0.30212 | 0.045777 | -0.11444 | -0.16937 | -0.10071 | -0.23346 | 0.054932 | 0.18768 | 60.7132 | 61.0474 | 122.7448 | 122.8912 | -0.11444 | 122.9004 | 60.9467 | -0.23346 | 122.8912 | -0.11444 | 60.9467 | 122.7448 | 122.9004 | -123.1476 | -123.0789
1269.7656 | 123.1842 | -60.9055 | 61.9446 | 0.25536 | -0.0039434 | -0.0087799 | 0.0039156 | 0.062241 | -0.0067185 | 0.067197 | -60.9833 | 62.0224 | -61.1801 | -61.0611 | 61.8484 | 0.045776 | -0.19226 | 0.16022 | 61.972 | -61.1481 | -0.27466 | 0.07782 | -0.077819 | -0.15564 | -0.09613 | -0.24261 | 0.027466 | 0.19684 | 60.7132 | 61.0657 | 122.7539 | 122.9279 | -0.077819 | 122.8775 | 60.9512 | -0.24261 | 122.9279 | -0.077819 | 60.9512 | 122.7539 | 122.8775 | -123.1247 | -123.0927
1270.7656 | 123.1567 | -60.91 | 62.0132 | 0.24773 | -0.0060798 | -0.0077117 | 0.0049838 | 0.059678 | -0.0052231 | 0.069333 | -61.0428 | 62.0636 | -61.1664 | -61.1298 | 61.8027 | -0.013733 | -0.12817 | 0.073242 | 62.0316 | -61.1801 | -0.25635 | 0.050354 | -0.13275 | -0.21973 | -0.21057 | -0.27008 | 0.01831 | 0.1236 | 60.7819 | 60.9833 | 122.7127 | 122.9736 | -0.13275 | 122.9416 | 60.8963 | -0.27008 | 122.9736 | -0.13275 | 60.8963 | 122.7127 | 122.9416 | -123.1796 | -123.1934
1271.7656 | 123.1384 | -60.9055 | 62.0087 | 0.24773 | -0.0039434 | -0.0027985 | 0.004343 | 0.062455 | -0.0028731 | 0.066984 | -61.0703 | 62.0911 | -61.1755 | -61.1618 | 61.7752 | -0.027466 | -0.10071 | 0.054932 | 62.0453 | -61.1618 | -0.27008 | 0.082397 | -0.16479 | -0.25635 | -0.23346 | -0.25635 | 0.036621 | 0.10529 | 60.8047 | 60.9604 | 122.6807 | 122.9965 | -0.16479 | 122.9507 | 60.878 | -0.25635 | 122.9965 | -0.16479 | 60.878 | 122.6807 | 122.9507 | -123.1842 | -123.1705
1272.7656 | 123.1979 | -60.8688 | 61.9812 | 0.21721 | -0.0054388 | -0.0053619 | 0.0032748 | 0.062882 | -0.0015915 | 0.070615 | -61.0016 | 62.0407 | -61.1664 | -61.1801 | 61.9583 | 0.1236 | -0.14648 | 0.19226 | 62.0087 | -61.1252 | -0.29755 | 0.059509 | -0.13275 | -0.31128 | -0.022888 | -0.25635 | 0.027466 | 0.16479 | 60.7224 | 61.0611 | 122.8271 | 122.9095 | -0.13275 | 122.8775 | 60.9924 | -0.25635 | 122.9095 | -0.13275 | 60.9924 | 122.8271 | 122.8775 | -123.1476 | -123.1064
1273.7656 | 123.1796 | -60.8963 | 61.9583 | 0.24773 | -0.0054388 | -0.0070709 | 0.0041292 | 0.060746 | -0.0026595 | 0.067838 | -60.997 | 62.0132 | -61.171 | -61.0977 | 61.8622 | 0.041199 | -0.20142 | 0.15564 | 61.9675 | -61.1664 | -0.27466 | 0.054932 | -0.10071 | -0.20142 | -0.09613 | -0.27008 | 0.009155 | 0.17395 | 60.6949 | 61.0519 | 122.7585 | 122.9095 | -0.10071 | 122.8638 | 60.9375 | -0.27008 | 122.9095 | -0.10071 | 60.9375 | 122.7585 | 122.8638 | -123.1293 | -123.1247
1274.7656 | 123.2117 | -60.878 | 61.9629 | 0.23247 | -0.0026618 | -0.0096343 | 0.0047702 | 0.063523 | -0.0043685 | 0.069761 | -60.9787 | 62.0316 | -61.1847 | -61.0977 | 61.8576 | 0.036621 | -0.1831 | 0.16022 | 62.0041 | -61.1389 | -0.3067 | 0.068664 | -0.10071 | -0.21973 | -0.10529 | -0.26093 | 0.041198 | 0.20599 | 60.6949 | 61.0382 | 122.7356 | 122.9095 | -0.10071 | 122.8821 | 60.9146 | -0.26093 | 122.9095 | -0.10071 | 60.9146 | 122.7356 | 122.8821 | -123.1476 | -123.1018
1275.7656 | 123.1934 | -60.8963 | 61.9949 | 0.15617 | -0.004798 | -0.0023711 | 0.003702 | 0.062028 | -0.0060775 | 0.06912 | -60.9879 | 62.0636 | -61.1664 | -61.084 | 61.8484 | 0.050354 | -0.19684 | 0.12817 | 61.9675 | -61.1526 | -0.27008 | 0.068665 | -0.091553 | -0.18768 | -0.14648 | -0.25635 | -0.027466 | 0.17853 | 60.6995 | 61.0245 | 122.7448 | 122.9599 | -0.091553 | 122.8638 | 60.9467 | -0.25635 | 122.9599 | -0.091553 | 60.9467 | 122.7448 | 122.8638 | -123.1613 | -123.1476
1276.7656 | 123.1888 | -60.8643 | 61.9766 | 0.22484 | -0.0028754 | -0.0062163 | 0.0030612 | 0.064591 | -0.0058639 | 0.069974 | -60.9695 | 62.0316 | -61.1481 | -61.084 | 61.8439 | 0.050354 | -0.17395 | 0.13733 | 62.0041 | -61.1023 | -0.28381 | 0.054931 | -0.10529 | -0.21973 | -0.13275 | -0.23804 | 0.027465 | 0.17853 | 60.6903 | 61.0016 | 122.7081 | 122.8958 | -0.10529 | 122.8683 | 60.9146 | -0.23804 | 122.8958 | -0.10529 | 60.9146 | 122.7081 | 122.8683 | -123.1247 | -123.0789
1277.7656 | 123.1338 | -60.9146 | 62.0224 | 0.2401 | -0.0028754 | -0.0040801 | 0.0030612 | 0.063309 | -0.0043685 | 0.066343 | -61.0611 | 62.1094 | -61.1755 | -61.171 | 61.7615 | -0.036621 | -0.086975 | 0.045776 | 62.0224 | -61.1893 | -0.26093 | 0.086975 | -0.14648 | -0.25635 | -0.26093 | -0.27466 | 0 | 0.11444 | 60.8276 | 60.9604 | 122.6761 | 123.024 | -0.14648 | 122.937 | 60.878 | -0.27466 | 123.024 | -0.14648 | 60.878 | 122.6761 | 122.937 | -123.1979 | -123.2117
1278.7656 | 123.0881 | -60.9192 | 62.0041 | 0.20195 | -0.00052559 | -0.0013031 | 0.0064792 | 0.063523 | -0.0069321 | 0.068479 | -61.0382 | 62.1231 | -61.1801 | -61.1755 | 61.7661 | -0.045776 | -0.054932 | 0.032043 | 62.0407 | -61.1893 | -0.26093 | 0.11902 | -0.11902 | -0.25635 | -0.23804 | -0.27008 | 0.036621 | 0.14191 | 60.8643 | 60.9512 | 122.6852 | 123.0423 | -0.11902 | 122.9599 | 60.8734 | -0.27008 | 123.0423 | -0.11902 | 60.8734 | 122.6852 | 122.9599 | -123.1842 | -123.1934
1279.7656 | 123.2666 | -60.8826 | 61.9675 | 0.28587 | -0.0041572 | -0.0079253 | -0.0012112 | 0.063096 | -0.0041549 | 0.070615 | -60.9833 | 62.0407 | -61.1801 | -61.0886 | 61.8622 | 0.032043 | -0.18768 | 0.064087 | 62.0041 | -61.171 | -0.29755 | 0.073242 | -0.10071 | -0.20599 | -0.10528 | -0.28839 | 0.036621 | 0.19684 | 60.6949 | 60.9467 | 122.7448 | 122.9233 | -0.10071 | 122.8867 | 60.9146 | -0.28839 | 122.9233 | -0.10071 | 60.9146 | 122.7448 | 122.8867 | -123.1476 | -123.1384
1280.7656 | 123.2071 | -60.8734 | 61.9766 | 0.27824 | -0.0024482 | -0.0089935 | 0.0030612 | 0.06395 | -0.0050095 | 0.069547 | -60.997 | 62.0544 | -61.1481 | -61.0931 | 61.8484 | 0.054932 | -0.1831 | 0.15106 | 61.9766 | -61.1801 | -0.27466 | 0.077819 | -0.1236 | -0.21973 | -0.12817 | -0.3067 | 0 | 0.15106 | 60.6903 | 61.0245 | 122.7219 | 122.9279 | -0.1236 | 122.85 | 60.9283 | -0.3067 | 122.9279 | -0.1236 | 60.9283 | 122.7219 | 122.85 | -123.1247 | -123.1567
1281.7656 | 123.2117 | -60.8734 | 61.9812 | 0.25536 | -0.0043708 | -0.0064301 | 0.0022066 | 0.064805 | -0.0045821 | 0.067411 | -60.9879 | 62.0636 | -61.171 | -61.1023 | 61.853 | 0.045776 | -0.18768 | 0.14648 | 61.9995 | -61.1572 | -0.29755 | 0.082398 | -0.11444 | -0.22888 | -0.12817 | -0.28381 | 0.018311 | 0.18311 | 60.6857 | 61.0199 | 122.7264 | 122.937 | -0.11444 | 122.8729 | 60.9192 | -0.28381 | 122.937 | -0.11444 | 60.9192 | 122.7264 | 122.8729 | -123.1522 | -123.1384
1282.7656 | 123.1979 | -60.878 | 61.9949 | 0.27824 | -0.0028754 | -0.0047211 | 0.0030612 | 0.063309 | -0.0028731 | 0.068693 | -60.9741 | 62.0499 | -61.1664 | -61.0886 | 61.8439 | 0.050354 | -0.18768 | 0.13275 | 61.9904 | -61.1572 | -0.28839 | 0.054932 | -0.09613 | -0.21057 | -0.15106 | -0.27924 | -0.004578 | 0.19226 | 60.6903 | 61.0107 | 122.7219 | 122.9279 | -0.09613 | 122.8683 | 60.9283 | -0.27924 | 122.9279 | -0.09613 | 60.9283 | 122.7219 | 122.8683 | -123.1613 | -123.1522
1283.7656 | 123.2208 | -60.8871 | 61.972 | 0.40794 | -0.003089 | -0.0047211 | 0.00712 | 0.062455 | -0.0043685 | 0.068052 | -60.9787 | 62.0728 | -61.1801 | -61.0977 | 61.8439 | 0.050354 | -0.1831 | 0.11444 | 62.0087 | -61.1572 | -0.29297 | 0.10071 | -0.091553 | -0.21057 | -0.12817 | -0.27008 | 0.036621 | 0.20142 | 60.704 | 61.0016 | 122.731 | 122.9599 | -0.091553 | 122.8958 | 60.9375 | -0.27008 | 122.9599 | -0.091553 | 60.9375 | 122.731 | 122.8958 | -123.1522 | -123.1293
1284.7656 | 123.1338 | -60.9283 | 62.0041 | 0.19432 | -0.0028754 | -0.0062163 | 0.0032748 | 0.063096 | -0.0067185 | 0.068906 | -61.0565 | 62.0956 | -61.171 | -61.171 | 61.7661 | -0.045776 | -0.059509 | 0.045776 | 62.0544 | -61.1664 | -0.24261 | 0.091553 | -0.12817 | -0.24261 | -0.23804 | -0.23804 | 0.050354 | 0.11444 | 60.8688 | 60.9741 | 122.6944 | 123.024 | -0.12817 | 122.9828 | 60.8826 | -0.23804 | 123.024 | -0.12817 | 60.8826 | 122.6944 | 122.9828 | -123.175 | -123.1705
1285.7656 | 123.1018 | -60.9009 | 62.0132 | 0.3698 | -0.003089 | -0.0032257 | 0.0060518 | 0.06395 | -0.0052231 | 0.068265 | -61.0657 | 62.1231 | -61.1801 | -61.1801 | 61.7615 | -0.045776 | -0.041199 | 0.022888 | 62.0773 | -61.1755 | -0.27924 | 0.10986 | -0.16479 | -0.27924 | -0.25177 | -0.27466 | 0.064087 | 0.11444 | 60.8597 | 60.9238 | 122.6624 | 123.024 | -0.16479 | 122.9782 | 60.8551 | -0.27466 | 123.024 | -0.16479 | 60.8551 | 122.6624 | 122.9782 | -123.1934 | -123.1888
1286.7656 | 123.2025 | -60.8871 | 61.94 | 0.26299 | -0.004798 | -0.0064301 | 0.0017794 | 0.063096 | -0.0041549 | 0.065916 | -60.9879 | 62.0682 | -61.1755 | -61.0931 | 61.8576 | 0.045776 | -0.18768 | 0.14648 | 61.9995 | -61.171 | -0.28839 | 0.12817 | -0.10071 | -0.20599 | -0.082397 | -0.28381 | 0.05951 | 0.18768 | 60.6995 | 61.0336 | 122.7448 | 122.9553 | -0.10071 | 122.8867 | 60.9329 | -0.28381 | 122.9553 | -0.10071 | 60.9329 | 122.7448 | 122.8867 | -123.1155 | -123.111
1287.7656 | 123.1934 | -60.8826 | 61.9949 | 0.25536 | -0.0045844 | -0.0042937 | 0.0028476 | 0.064378 | -0.0039413 | 0.066984 | -60.9741 | 62.0636 | -61.1526 | -61.0977 | 61.8439 | 0.050354 | -0.19684 | 0.12817 | 62.0087 | -61.1801 | -0.27008 | 0.068665 | -0.091553 | -0.21515 | -0.15106 | -0.29755 | 0.013733 | 0.17853 | 60.6857 | 61.0107 | 122.7264 | 122.9462 | -0.091553 | 122.8912 | 60.9329 | -0.29755 | 122.9462 | -0.091553 | 60.9329 | 122.7264 | 122.8912 | -123.1476 | -123.175
1288.7656 | 123.1934 | -60.8963 | 61.9995 | 0.22484 | -0.0024482 | -0.0062163 | 0.002634 | 0.06395 | -0.0011643 | 0.068265 | -60.997 | 62.0544 | -61.1893 | -61.1023 | 61.8347 | 0.022888 | -0.16022 | 0.1236 | 62.0041 | -61.1755 | -0.29297 | 0.054931 | -0.10071 | -0.20599 | -0.1648 | -0.27924 | 0.004577 | 0.19226 | 60.7361 | 61.0199 | 122.731 | 122.9507 | -0.10071 | 122.9004 | 60.9192 | -0.27924 | 122.9507 | -0.10071 | 60.9192 | 122.731 | 122.9004 | -123.1888 | -123.175
1289.7656 | 123.1796 | -60.91 | 62.0087 | 0.17906 | -0.0052252 | -0.0081389 | -0.00057036 | 0.059678 | -0.0026595 | 0.067197 | -61.0519 | 62.0636 | -61.1343 | -61.1435 | 61.8256 | 0.022888 | -0.091553 | 0.11444 | 62.0178 | -61.1526 | -0.2243 | 0.054932 | -0.14191 | -0.23346 | -0.18311 | -0.24261 | 0.009155 | 0.082397 | 60.8185 | 61.0245 | 122.7356 | 122.9736 | -0.14191 | 122.9279 | 60.9329 | -0.24261 | 122.9736 | -0.14191 | 60.9329 | 122.7356 | 122.9279 | -123.143 | -123.1613
1290.7812 | 123.1934 | -60.8597 | 61.9995 | 0.19432 | -0.0062934 | -0.0051483 | 0.0041292 | 0.062882 | -0.0037277 | 0.068265 | -61.0291 | 62.0361 | -61.1618 | -61.0977 | 61.8439 | 0.041199 | -0.16937 | 0.13733 | 61.9949 | -61.1664 | -0.30212 | 0.036621 | -0.16937 | -0.23804 | -0.15564 | -0.3067 | -0.004578 | 0.13275 | 60.6903 | 60.997 | 122.7036 | 122.8958 | -0.16937 | 122.8546 | 60.9009 | -0.3067 | 122.8958 | -0.16937 | 60.9009 | 122.7036 | 122.8546 | -123.1613 | -123.1659
1291.7656 | 123.1155 | -60.8963 | 62.0361 | 0.18669 | -0.0011664 | -0.0062163 | 0.010752 | 0.063523 | -0.0041549 | 0.067411 | -61.0611 | 62.1231 | -61.1801 | -61.116 | 61.7523 | -0.009155 | -0.018311 | 0.07782 | 62.0682 | -61.1893 | -0.28381 | 0.086975 | -0.16479 | -0.21973 | -0.28381 | -0.29297 | 0.032043 | 0.11902 | 60.878 | 60.9741 | 122.6486 | 123.0194 | -0.16479 | 122.9645 | 60.8871 | -0.29297 | 123.0194 | -0.16479 | 60.8871 | 122.6486 | 122.9645 | -123.2162 | -123.2254
1292.7656 | 122.9919 | -60.9512 | 61.9629 | 0.21721 | -0.0033026 | -0.0057891 | 0.0045566 | 0.062882 | -0.0041549 | 0.067838 | -61.0703 | 62.1506 | -61.1801 | -61.1847 | 61.7477 | -0.068665 | 0.009155 | 0 | 62.0407 | -61.203 | -0.22888 | 0.18768 | -0.11902 | -0.23346 | -0.21515 | -0.25177 | 0.077819 | 0.10986 | 60.9604 | 60.9512 | 122.699 | 123.1018 | -0.11902 | 122.9919 | 60.8826 | -0.25177 | 123.1018 | -0.11902 | 60.8826 | 122.699 | 122.9919 | -123.143 | -123.1659
1293.7656 | 123.1934 | -60.8963 | 61.9904 | 0.27061 | -0.0026618 | -0.0038665 | 0.0013522 | 0.065659 | -0.0033005 | 0.070402 | -61.0336 | 62.1002 | -61.171 | -61.1343 | 61.8027 | -0.013733 | -0.14191 | 0.091553 | 62.027 | -61.1801 | -0.27466 | 0.10986 | -0.13733 | -0.23804 | -0.18768 | -0.28381 | 0.036622 | 0.13733 | 60.7544 | 60.9879 | 122.699 | 122.9965 | -0.13733 | 122.9233 | 60.8826 | -0.28381 | 122.9965 | -0.13733 | 60.8826 | 122.699 | 122.9233 | -123.1613 | -123.1705
1294.7656 | 123.1384 | -60.8917 | 61.9858 | 0.28587 | -0.0011664 | -0.0055755 | 0.0047702 | 0.064591 | -0.0054367 | 0.068693 | -61.0565 | 62.1094 | -61.1664 | -61.1618 | 61.7889 | -0.013733 | -0.10071 | 0.068665 | 62.0499 | -61.1618 | -0.27466 | 0.1236 | -0.16479 | -0.27008 | -0.19684 | -0.27008 | 0.064087 | 0.10986 | 60.791 | 60.9604 | 122.6807 | 123.0011 | -0.16479 | 122.9416 | 60.878 | -0.27008 | 123.0011 | -0.16479 | 60.878 | 122.6807 | 122.9416 | -123.1522 | -123.1476
1295.7656 | 123.1338 | -60.9146 | 61.9949 | 0.19432 | -0.0041572 | -0.0083527 | 0.004343 | 0.063737 | -0.0037277 | 0.069761 | -61.0382 | 62.114 | -61.1618 | -61.1618 | 61.7752 | -0.054932 | -0.054932 | 0.027466 | 62.0407 | -61.203 | -0.24719 | 0.11902 | -0.1236 | -0.24719 | -0.21973 | -0.28839 | 0.045776 | 0.1236 | 60.8597 | 60.9421 | 122.6898 | 123.0286 | -0.1236 | 122.9553 | 60.8597 | -0.28839 | 123.0286 | -0.1236 | 60.8597 | 122.6898 | 122.9553 | -123.1567 | -123.1979
1296.7656 | 123.0972 | -60.91 | 62.027 | -0.29396 | -0.003089 | -0.0040801 | 0.0034884 | 0.066514 | -0.0047957 | 0.068906 | -61.0565 | 62.1323 | -61.171 | -61.1801 | 61.7386 | -0.036621 | -0.022888 | 0.032043 | 62.0453 | -61.1893 | -0.26093 | 0.10529 | -0.14648 | -0.27008 | -0.28839 | -0.27924 | 0.01831 | 0.11444 | 60.8871 | 60.9421 | 122.6486 | 123.0423 | -0.14648 | 122.9553 | 60.8734 | -0.27924 | 123.0423 | -0.14648 | 60.8734 | 122.6486 | 122.9553 | -123.1979 | -123.2162
1297.7656 | 123.0881 | -60.9238 | 62.027 | 0.20958 | -0.0024482 | -0.0085663 | 0.005411 | 0.06096 | -0.0024459 | 0.067411 | -61.0657 | 62.1597 | -61.1893 | -61.1481 | 61.7889 | -0.064087 | 0.050354 | 0.041199 | 62.1048 | -61.2167 | -0.2655 | 0.13275 | -0.14191 | -0.2243 | -0.23804 | -0.29297 | 0.077819 | 0.1236 | 60.9741 | 60.965 | 122.7127 | 123.0835 | -0.14191 | 123.0286 | 60.8597 | -0.29297 | 123.0835 | -0.14191 | 60.8597 | 122.7127 | 123.0286 | -123.2162 | -123.2437
1298.7656 | 123.0789 | -60.9009 | 62.0224 | 0.17143 | -0.0022346 | -0.0032257 | 0.0069064 | 0.0663 | -0.0026595 | 0.066984 | -61.0428 | 62.1506 | -61.1618 | -61.171 | 61.7706 | -0.013733 | 0.032043 | 0.050354 | 62.059 | -61.235 | -0.26092 | 0.12817 | -0.14191 | -0.27008 | -0.25177 | -0.33417 | 0.036621 | 0.11902 | 60.9329 | 60.9512 | 122.6715 | 123.0515 | -0.14191 | 122.9599 | 60.8871 | -0.33417 | 123.0515 | -0.14191 | 60.8871 | 122.6715 | 122.9599 | -123.1842 | -123.2574
1299.7656 | 123.056 | -60.9329 | 62.0178 | 0.10277 | -0.0026618 | -0.0057891 | 0.0030612 | 0.067368 | -0.0041549 | 0.067624 | -61.0794 | 62.1643 | -61.1938 | -61.2167 | 61.7294 | -0.07782 | 0.036621 | 0.027466 | 62.0682 | -61.2259 | -0.26093 | 0.14648 | -0.14649 | -0.28381 | -0.28839 | -0.29297 | 0.050354 | 0.11444 | 60.9695 | 60.9604 | 122.6624 | 123.0972 | -0.14649 | 123.0011 | 60.8551 | -0.29297 | 123.0972 | -0.14649 | 60.8551 | 122.6624 | 123.0011 | -123.2117 | -123.2437
1300.7656 | 123.0789 | -60.9329 | 62.0407 | 0.17906 | -0.0033026 | -0.0070709 | 0.0041292 | 0.065873 | -0.0024459 | 0.068479 | -61.0703 | 62.146 | -61.1938 | -61.2167 | 61.7661 | -0.07782 | -0.33417 | 0.14648 | 61.9995 | -61.2396 | -0.26093 | 0.10529 | -0.13733 | -0.28381 | -0.27466 | -0.3067 | -0.041198 | 0.1236 | 60.5988 | 61.0794 | 122.699 | 123.0789 | -0.13733 | 122.9324 | 60.8551 | -0.3067 | 123.0789 | -0.13733 | 60.8551 | 122.699 | 122.9324 | -123.2346 | -123.2803
1301.7656 | 123.056 | -60.9558 | 62.0041 | 0.19432 | -0.00095279 | -0.0027985 | 0.0056246 | 0.063309 | -0.0028731 | 0.06912 | -61.0703 | 62.1552 | -61.1755 | -61.2122 | 61.7157 | -0.041199 | 0.022888 | 0.004578 | 62.059 | -61.2259 | -0.21973 | 0.15106 | -0.11444 | -0.25635 | -0.28839 | -0.27008 | 0.054932 | 0.10529 | 60.9787 | 60.9604 | 122.6715 | 123.111 | -0.11444 | 123.0148 | 60.9146 | -0.27008 | 123.111 | -0.11444 | 60.9146 | 122.6715 | 123.0148 | -123.1796 | -123.23
1302.7656 | 123.1705 | -60.8871 | 61.9766 | 0.25536 | -0.003089 | -0.0077117 | 0.001993 | 0.062455 | -0.0020187 | 0.068479 | -61.0291 | 62.0819 | -61.1984 | -61.0977 | 61.8027 | -0.022888 | -0.14191 | 0.1236 | 62.0224 | -61.1664 | -0.31128 | 0.10529 | -0.14191 | -0.21057 | -0.17395 | -0.27924 | 0.045776 | 0.16937 | 60.7452 | 61.0107 | 122.6898 | 122.9691 | -0.14191 | 122.9095 | 60.8643 | -0.27924 | 122.9691 | -0.14191 | 60.8643 | 122.6898 | 122.9095 | -123.175 | -123.143
1303.7656 | 123.0927 | -60.9421 | 62.059 | 0.056992 | -0.0026618 | -0.00087594 | 0.0064792 | 0.066514 | -0.0033005 | 0.066556 | -61.0291 | 62.1552 | -61.203 | -61.171 | 61.7706 | -0.013733 | 0.036621 | 0.064087 | 62.0911 | -61.2167 | -0.26093 | 0.09613 | -0.086975 | -0.22888 | -0.28839 | -0.27466 | 0.032043 | 0.17395 | 60.9787 | 61.0062 | 122.7127 | 123.0972 | -0.086975 | 123.0331 | 60.9283 | -0.27466 | 123.0972 | -0.086975 | 60.9283 | 122.7127 | 123.0331 | -123.262 | -123.2758
1304.7656 | 123.0881 | -60.9192 | 62.0178 | 0.049362 | -0.0026618 | -0.0034393 | 0.0047702 | 0.065659 | -0.0011643 | 0.068265 | -61.0153 | 62.146 | -61.1526 | -61.1618 | 61.7981 | 0.004578 | 0.045776 | 0.10071 | 62.0453 | -61.2534 | -0.23346 | 0.12817 | -0.096131 | -0.24261 | -0.21973 | -0.33417 | 0.027466 | 0.13733 | 60.965 | 61.0199 | 122.7173 | 123.0652 | -0.096131 | 122.9645 | 60.9238 | -0.33417 | 123.0652 | -0.096131 | 60.9238 | 122.7173 | 122.9645 | -123.1705 | -123.2712
1305.7656 | 123.1201 | -60.91 | 62.027 | -0.04982 | -0.0022346 | -0.0057891 | 0.0015658 | 0.065446 | -0.0018051 | 0.068479 | -60.9787 | 62.1552 | -61.171 | -61.1023 | 61.8301 | 0.068665 | 0.041199 | 0.16937 | 62.1002 | -61.2076 | -0.26093 | 0.12817 | -0.068665 | -0.19226 | -0.19684 | -0.29755 | 0.073242 | 0.19226 | 60.9512 | 61.0794 | 122.7402 | 123.0652 | -0.068665 | 123.0103 | 60.9787 | -0.29755 | 123.0652 | -0.068665 | 60.9787 | 122.7402 | 123.0103 | -123.1979 | -123.2346
1306.7656 | 123.1476 | -60.878 | 62.027 | 0.0035856 | -9.819e-05 | -0.0057891 | 0.0032748 | 0.062455 | -0.0039413 | 0.069761 | -60.997 | 62.1323 | -61.171 | -61.1298 | 61.8164 | 0.041199 | 0.036621 | 0.16022 | 62.0728 | -61.203 | -0.29297 | 0.10529 | -0.11902 | -0.25177 | -0.21057 | -0.32501 | 0.045776 | 0.17395 | 60.9146 | 61.0382 | 122.6944 | 123.0103 | -0.11902 | 122.9507 | 60.9192 | -0.32501 | 123.0103 | -0.11902 | 60.9192 | 122.6944 | 122.9507 | -123.1979 | -123.23
1307.7656 | 123.1155 | -60.9329 | 62.0453 | 0.011215 | -0.0026618 | -0.0021575 | 0.0041292 | 0.065446 | -0.0024459 | 0.068265 | -61.0107 | 62.1597 | -61.1572 | -61.1481 | 61.7935 | 0.009155 | 0.027466 | 0.10529 | 62.1002 | -61.1847 | -0.22431 | 0.11444 | -0.07782 | -0.21515 | -0.25177 | -0.25177 | 0.054932 | 0.14648 | 60.9604 | 61.0382 | 122.7264 | 123.0927 | -0.07782 | 123.0331 | 60.9421 | -0.25177 | 123.0927 | -0.07782 | 60.9421 | 122.7264 | 123.0331 | -123.2025 | -123.23
1308.7656 | 123.1155 | -60.91 | 62.0361 | -0.19478 | -0.0028754 | -0.0034393 | 0.00712 | 0.0663 | -0.0018051 | 0.06912 | -60.9741 | 62.1552 | -61.1664 | -61.116 | 61.8118 | 0.036621 | 0.027466 | 0.13275 | 62.114 | -61.1847 | -0.25635 | 0.11902 | -0.064087 | -0.20599 | -0.2243 | -0.27466 | 0.07782 | 0.19226 | 60.9375 | 61.0428 | 122.7219 | 123.0652 | -0.064087 | 123.024 | 60.9467 | -0.27466 | 123.0652 | -0.064087 | 60.9467 | 122.7219 | 123.024 | -123.2025 | -123.2208
1309.7656 | 123.1476 | -60.8963 | 62.0544 | -0.04219 | -0.0043708 | -0.0021575 | 0.0039156 | 0.065659 | -0.0030869 | 0.068052 | -60.9924 | 62.146 | -61.1389 | -61.1206 | 61.8851 | -0.027466 | 0.054932 | 0.17853 | 62.0819 | -61.1847 | -0.24262 | 0.091553 | -0.096131 | -0.2243 | -0.16937 | -0.28839 | 0.027466 | 0.14648 | 60.9512 | 61.0748 | 122.7814 | 123.0423 | -0.096131 | 122.9782 | 60.8688 | -0.28839 | 123.0423 | -0.096131 | 60.8688 | 122.7814 | 122.9782 | -123.1934 | -123.2391
1310.7656 | 123.1384 | -60.8917 | 62.0316 | 0.018845 | -0.0039434 | -0.0057891 | 0.0041292 | 0.065018 | -0.0050095 | 0.067624 | -60.9924 | 62.1643 | -61.1343 | -61.1069 | 61.8393 | 0.07782 | 0.041199 | 0.17853 | 62.0865 | -61.1938 | -0.24261 | 0.13275 | -0.10071 | -0.21515 | -0.19226 | -0.30212 | 0.054932 | 0.14191 | 60.9329 | 61.0703 | 122.731 | 123.056 | -0.10071 | 122.9782 | 60.9695 | -0.30212 | 123.056 | -0.10071 | 60.9695 | 122.731 | 122.9782 | -123.1659 | -123.2254
1311.7656 | 123.1384 | -60.8917 | 62.027 | -0.087967 | -0.0022346 | -0.0036529 | 0.0028476 | 0.064164 | -0.0052231 | 0.070188 | -60.997 | 62.1826 | -61.1618 | -61.1298 | 61.8256 | 0.086975 | 0.068665 | 0.17395 | 62.114 | -61.2167 | -0.27008 | 0.15564 | -0.10528 | -0.23804 | -0.20142 | -0.32501 | 0.086975 | 0.16479 | 60.9604 | 61.0657 | 122.7173 | 123.0743 | -0.10528 | 123.0057 | 60.9787 | -0.32501 | 123.0743 | -0.10528 | 60.9787 | 122.7173 | 123.0057 | -123.1888 | -123.2437
1312.7656 | 123.1293 | -60.9055 | 62.0316 | -0.11848 | -0.0037298 | -0.0047211 | 0.00071144 | 0.066514 | -0.0039413 | 0.068693 | -60.9924 | 62.1735 | -61.1526 | -61.1252 | 61.8301 | 0.07782 | 0.073242 | 0.17395 | 62.1231 | -61.1938 | -0.24719 | 0.14191 | -0.086975 | -0.21973 | -0.20142 | -0.28839 | 0.091553 | 0.16022 | 60.9787 | 61.0794 | 122.7356 | 123.0789 | -0.086975 | 123.0286 | 60.9833 | -0.28839 | 123.0789 | -0.086975 | 60.9833 | 122.7356 | 123.0286 | -123.1842 | -123.2254
1313.7656 | 123.1155 | -60.8963 | 62.0636 | -0.10323 | -0.00073919 | -0.0072845 | 0.00092504 | 0.064164 | -0.0062911 | 0.068693 | -61.0199 | 62.1918 | -61.1572 | -61.1481 | 61.8118 | 0.073242 | 0.12817 | 0.16479 | 62.1094 | -61.171 | -0.26093 | 0.12817 | -0.1236 | -0.25177 | -0.25177 | -0.27466 | 0.045776 | 0.13733 | 61.0245 | 61.0611 | 122.7081 | 123.0881 | -0.1236 | 123.0057 | 60.9695 | -0.27466 | 123.0881 | -0.1236 | 60.9695 | 122.7081 | 123.0057 | -123.2208 | -123.2346
1314.7656 | 123.1293 | -60.8963 | 62.0224 | -0.10323 | -0.0035162 | -0.0047211 | 0.0039156 | 0.062882 | -0.0033005 | 0.065916 | -61.0016 | 62.1506 | -61.1435 | -61.116 | 61.8164 | 0.064087 | 0.09613 | 0.18768 | 62.0956 | -61.203 | -0.24719 | 0.12817 | -0.10529 | -0.21973 | -0.20599 | -0.3067 | 0.073242 | 0.14191 | 60.9924 | 61.084 | 122.7127 | 123.0469 | -0.10529 | 122.9919 | 60.9604 | -0.3067 | 123.0469 | -0.10529 | 60.9604 | 122.7127 | 122.9919 | -123.1659 | -123.2254
1315.7656 | 123.1201 | -60.9009 | 62.0499 | -0.15663 | -0.0041572 | -0.0045075 | 0.0045566 | 0.065232 | -0.0024459 | 0.068479 | -61.0107 | 62.1689 | -61.171 | -61.1252 | 61.8118 | 0.082397 | 0.086975 | 0.17395 | 62.1185 | -61.1847 | -0.27008 | 0.11902 | -0.10986 | -0.2243 | -0.23804 | -0.28381 | 0.068664 | 0.16022 | 60.9879 | 61.0748 | 122.7127 | 123.0698 | -0.10986 | 123.0194 | 60.9833 | -0.28381 | 123.0698 | -0.10986 | 60.9833 | 122.7127 | 123.0194 | -123.2208 | -123.2346
1316.7656 | 123.1338 | -60.8826 | 62.0728 | -0.095596 | -0.0035162 | -0.0066437 | 0.0030612 | 0.06395 | -0.0013779 | 0.069333 | -61.0428 | 62.1643 | -61.1664 | -61.1526 | 61.8118 | 0.050354 | 0.14191 | 0.16479 | 62.1094 | -61.1893 | -0.28381 | 0.091553 | -0.16022 | -0.27008 | -0.26093 | -0.3067 | 0.036621 | 0.1236 | 61.0245 | 61.0474 | 122.6944 | 123.0469 | -0.16022 | 122.9919 | 60.9329 | -0.3067 | 123.0469 | -0.16022 | 60.9329 | 122.6944 | 122.9919 | -123.2391 | -123.262
1317.7656 | 123.111 | -60.8963 | 62.0773 | 0.026474 | -0.0033026 | -0.0077117 | 0.0028476 | 0.063309 | -0.0043685 | 0.067411 | -61.0611 | 62.1552 | -61.1618 | -61.1664 | 61.7844 | 0.036621 | 0.13733 | 0.15564 | 62.1277 | -61.1755 | -0.2655 | 0.077819 | -0.16479 | -0.27008 | -0.29297 | -0.27924 | 0.050354 | 0.10071 | 61.0336 | 61.0519 | 122.6807 | 123.0515 | -0.16479 | 123.024 | 60.9329 | -0.27924 | 123.0515 | -0.16479 | 60.9329 | 122.6807 | 123.024 | -123.2391 | -123.2529
1318.7656 | 123.0972 | -60.9055 | 62.0636 | -0.13374 | -0.0054388 | -0.0045075 | -0.0018522 | 0.063309 | -0.0054367 | 0.068906 | -61.0565 | 62.1323 | -61.1481 | -61.1664 | 61.8073 | 0.059509 | 0.15106 | 0.17395 | 62.1002 | -61.1938 | -0.24261 | 0.068664 | -0.15106 | -0.26093 | -0.25635 | -0.28839 | 0.036621 | 0.091552 | 61.0565 | 61.0794 | 122.7127 | 123.0377 | -0.15106 | 123.0057 | 60.965 | -0.28839 | 123.0377 | -0.15106 | 60.965 | 122.7127 | 123.0057 | -123.2117 | -123.2574
1319.7656 | 123.111 | -60.9009 | 62.0728 | -0.2253 | -0.005866 | -0.0070709 | -0.0029202 | 0.062028 | -0.0030869 | 0.069333 | -61.0107 | 62.1048 | -61.171 | -61.1252 | 61.8256 | 0.073242 | 0.10529 | 0.19226 | 62.1048 | -61.1801 | -0.27008 | 0.032043 | -0.10986 | -0.2243 | -0.24719 | -0.27924 | 0.032043 | 0.16022 | 61.0062 | 61.0931 | 122.7264 | 123.0057 | -0.10986 | 123.0057 | 60.9741 | -0.27924 | 123.0057 | -0.10986 | 60.9741 | 122.7264 | 123.0057 | -123.2437 | -123.2529
1320.7656 | 123.1293 | -60.9055 | 62.0682 | -0.26344 | -0.0060798 | -0.0081389 | 0.001993 | 0.062028 | -0.0028731 | 0.068479 | -61.0611 | 62.114 | -61.1526 | -61.1618 | 61.8027 | 0.059509 | 0.15106 | 0.16479 | 62.1094 | -61.1847 | -0.24719 | 0.045777 | -0.15564 | -0.25635 | -0.2655 | -0.27923 | 0.041199 | 0.091553 | 61.0565 | 61.0703 | 122.7081 | 123.0194 | -0.15564 | 123.0148 | 60.965 | -0.27923 | 123.0194 | -0.15564 | 60.965 | 122.7081 | 123.0148 | -123.2208 | -123.2529
1321.7656 | 123.0972 | -60.91 | 62.0636 | -0.17952 | -0.004798 | -0.0077117 | 0.00071144 | 0.060105 | -0.0045821 | 0.068906 | -61.0519 | 62.1323 | -61.1572 | -61.171 | 61.6425 | 0.07782 | 0.33875 | 0.050354 | 62.1368 | -61.1618 | -0.24719 | 0.068664 | -0.14191 | -0.26093 | -0.42114 | -0.25177 | 0.073242 | 0.10529 | 61.2488 | 60.9604 | 122.5525 | 123.0423 | -0.14191 | 123.0469 | 60.9879 | -0.25177 | 123.0423 | -0.14191 | 60.9879 | 122.5525 | 123.0469 | -123.2208 | -123.2254
1322.7656 | 123.1018 | -60.9009 | 62.0728 | -0.16426 | -0.0039434 | -0.0079253 | -0.00057036 | 0.06096 | -0.0035141 | 0.069547 | -61.0428 | 62.1231 | -61.1664 | -61.1572 | 61.7935 | 0.059509 | 0.13275 | 0.16022 | 62.146 | -61.1755 | -0.2655 | 0.050354 | -0.14191 | -0.25635 | -0.27924 | -0.27466 | 0.073242 | 0.1236 | 61.0336 | 61.0611 | 122.6944 | 123.024 | -0.14191 | 123.0469 | 60.9604 | -0.27466 | 123.024 | -0.14191 | 60.9604 | 122.6944 | 123.0469 | -123.2391 | -123.2483
1323.7656 | 123.0743 | -60.9009 | 62.0453 | -0.30159 | -0.0035162 | -0.0083527 | 0.0022066 | 0.060746 | -0.0033005 | 0.06912 | -61.0474 | 62.1048 | -61.1847 | -61.1389 | 61.7981 | 0.054932 | 0.13275 | 0.17853 | 62.1094 | -61.1572 | -0.28381 | 0.059509 | -0.14648 | -0.23804 | -0.24719 | -0.25635 | 0.064087 | 0.13733 | 61.0336 | 61.0794 | 122.699 | 123.0057 | -0.14648 | 123.0103 | 60.9558 | -0.25635 | 123.0057 | -0.14648 | 60.9558 | 122.699 | 123.0103 | -123.23 | -123.2025
1324.7656 | 123.0972 | -60.9009 | 62.0728 | -0.15663 | -0.0060798 | -0.0055755 | 0.00092504 | 0.062028 | -0.0035141 | 0.066984 | -61.0382 | 62.0911 | -61.1526 | -61.1206 | 61.8301 | 0.073242 | 0.11444 | 0.20142 | 62.1094 | -61.1893 | -0.25177 | 0.01831 | -0.13733 | -0.21973 | -0.24262 | -0.28839 | 0.036621 | 0.11444 | 61.0153 | 61.1023 | 122.731 | 122.9919 | -0.13733 | 123.0103 | 60.9741 | -0.28839 | 122.9919 | -0.13733 | 60.9741 | 122.731 | 123.0103 | -123.2254 | -123.262
1325.7656 | 123.2071 | -60.8551 | 62.0224 | -0.33974 | -0.008216 | -0.014761 | -0.0018522 | 0.062455 | -0.0037277 | 0.066556 | -60.9879 | 62.0361 | -61.1389 | -61.0428 | 61.8851 | 0.16022 | -0.032043 | 0.29297 | 62.0682 | -61.1206 | -0.28381 | 0.013733 | -0.13275 | -0.18768 | -0.13733 | -0.2655 | 0.045776 | 0.15106 | 60.8231 | 61.1481 | 122.7402 | 122.8912 | -0.13275 | 122.9233 | 61.0153 | -0.2655 | 122.8912 | -0.13275 | 61.0153 | 122.7402 | 122.9233 | -123.1613 | -123.143
1326.7656 | 123.2117 | -60.8688 | 62.027 | -0.095596 | -0.0062934 | -0.010916 | 0.00049764 | 0.061173 | -0.0041549 | 0.070188 | -60.9787 | 62.059 | -61.1114 | -61.1023 | 61.8759 | 0.17395 | -0.091553 | 0.2655 | 62.0407 | -61.1435 | -0.24262 | 0.032043 | -0.10986 | -0.23346 | -0.15106 | -0.27466 | 0.013732 | 0.13275 | 60.7773 | 61.1343 | 122.7448 | 122.9279 | -0.10986 | 122.9095 | 61.0428 | -0.27466 | 122.9279 | -0.10986 | 61.0428 | 122.7448 | 122.9095 | -123.1384 | -123.1705
1327.7656 | 123.1567 | -60.8688 | 62.0453 | -0.12611 | -0.0080024 | -0.0040801 | -0.0020658 | 0.062241 | -0.0062911 | 0.066556 | -60.9879 | 62.0728 | -61.1435 | -61.0703 | 61.8668 | 0.11902 | 0.041199 | 0.25177 | 62.0682 | -61.1206 | -0.27466 | 0.027466 | -0.11902 | -0.20142 | -0.17853 | -0.25177 | 0.022888 | 0.15564 | 60.91 | 61.1206 | 122.7356 | 122.9416 | -0.11902 | 122.937 | 60.9879 | -0.25177 | 122.9416 | -0.11902 | 60.9879 | 122.7356 | 122.937 | -123.1888 | -123.1659
1328.7656 | 123.1064 | -60.8917 | 62.0773 | -0.18715 | -0.0054388 | -0.010703 | 0.002634 | 0.060532 | -0.0041549 | 0.06912 | -61.0245 | 62.0865 | -61.1481 | -61.1298 | 61.8027 | 0.068665 | 0.13275 | 0.17853 | 62.1002 | -61.1572 | -0.25635 | 0.009155 | -0.13275 | -0.23804 | -0.27466 | -0.2655 | 0.022888 | 0.1236 | 61.0245 | 61.0703 | 122.6944 | 122.9782 | -0.13275 | 122.9919 | 60.9604 | -0.2655 | 122.9782 | -0.13275 | 60.9604 | 122.6944 | 122.9919 | -123.2254 | -123.2346
1329.7656 | 123.1522 | -60.8826 | 62.0682 | -0.17189 | -0.0050116 | -0.010703 | 0.0028476 | 0.060532 | -0.0065047 | 0.068052 | -61.0016 | 62.0636 | -61.1481 | -61.084 | 61.8164 | 0.086975 | 0.09613 | 0.21973 | 62.1048 | -61.1298 | -0.2655 | -0.004577 | -0.11902 | -0.20142 | -0.25177 | -0.24719 | 0.036621 | 0.14648 | 60.9787 | 61.1023 | 122.699 | 122.9462 | -0.11902 | 122.9874 | 60.9695 | -0.24719 | 122.9462 | -0.11902 | 60.9695 | 122.699 | 122.9874 | -123.2162 | -123.1979
1330.7656 | 123.1384 | -60.8917 | 62.0224 | -0.20241 | -0.0045844 | -0.010703 | 0.003702 | 0.060319 | -0.0039413 | 0.06912 | -60.9833 | 62.0773 | -61.1572 | -61.1023 | 61.853 | 0.086975 | 0.059509 | 0.22888 | 62.0636 | -61.1526 | -0.2655 | 0.054932 | -0.091552 | -0.21057 | -0.16937 | -0.26092 | 0.041199 | 0.17395 | 60.9512 | 61.1206 | 122.7448 | 122.9691 | -0.091552 | 122.9553 | 60.9787 | -0.26092 | 122.9691 | -0.091552 | 60.9787 | 122.7448 | 122.9553 | -123.1796 | -123.175
1331.7656 | 123.143 | -60.878 | 62.0544 | -0.19478 | -0.0052252 | -0.0087799 | 0.003702 | 0.060105 | -0.0039413 | 0.063566 | -60.9833 | 62.0636 | -61.1343 | -61.0794 | 61.8622 | 0.11444 | 0.041199 | 0.24261 | 62.0728 | -61.1526 | -0.25635 | 0.009156 | -0.10528 | -0.20142 | -0.19226 | -0.27466 | 0.018311 | 0.15106 | 60.9192 | 61.1206 | 122.7402 | 122.9416 | -0.10528 | 122.9507 | 60.9924 | -0.27466 | 122.9416 | -0.10528 | 60.9924 | 122.7402 | 122.9507 | -123.1888 | -123.2071
1332.7812 | 123.1384 | -60.8917 | 62.0316 | -0.065079 | -0.0039434 | -0.0060027 | 0.0062656 | 0.062669 | -0.0056503 | 0.067624 | -60.9741 | 62.1231 | -61.1435 | -61.0886 | 61.8301 | 0.050354 | 0.032043 | 0.17853 | 62.0728 | -61.1938 | -0.25177 | 0.091553 | -0.082397 | -0.19684 | -0.20142 | -0.30212 | 0.041199 | 0.16937 | 60.9238 | 61.0703 | 122.7219 | 123.0148 | -0.082397 | 122.9645 | 60.9421 | -0.30212 | 123.0148 | -0.082397 | 60.9421 | 122.7219 | 122.9645 | -123.175 | -123.2254
1333.7656 | 123.1155 | -60.8459 | 62.0041 | -0.13374 | -0.0054388 | -0.0074981 | -0.0016386 | 0.061173 | -0.0028731 | 0.068479 | -60.9924 | 62.0453 | -61.1481 | -61.0382 | 61.9125 | 0.14648 | -0.036621 | 0.57678 | 62.0956 | -61.0657 | -0.30212 | 0.041199 | -0.14648 | -0.19226 | -0.091552 | -0.21973 | 0.091553 | 0.15564 | 60.8093 | 61.4227 | 122.7585 | 122.8912 | -0.14648 | 122.9416 | 60.9924 | -0.21973 | 122.8912 | -0.14648 | 60.9924 | 122.7585 | 122.9416 | -123.1522 | -123.0698
1334.7656 | 123.1842 | -60.8643 | 62.027 | -0.095596 | -0.0069342 | -0.0066437 | 7.0444e-05 | 0.060105 | -0.0050095 | 0.069974 | -60.9741 | 62.0361 | -61.1618 | -61.0565 | 61.9034 | 0.14191 | -0.004578 | 0.27008 | 62.059 | -61.1114 | -0.29755 | 0.009155 | -0.10986 | -0.19226 | -0.1236 | -0.24719 | 0.032043 | 0.18768 | 60.8597 | 61.1343 | 122.7676 | 122.9004 | -0.10986 | 122.9233 | 61.0062 | -0.24719 | 122.9004 | -0.10986 | 61.0062 | 122.7676 | 122.9233 | -123.1888 | -123.1384
1335.7656 | 123.0835 | -60.8871 | 62.0728 | -0.17189 | -0.0060798 | -0.0051483 | 0.0013522 | 0.060105 | -0.0056503 | 0.06677 | -60.9924 | 62.114 | -61.1389 | -61.1114 | 61.8118 | 0.073242 | 0.073242 | 0.19226 | 62.0956 | -61.171 | -0.25177 | 0.041199 | -0.10529 | -0.2243 | -0.26093 | -0.28381 | 0.022888 | 0.14648 | 60.9604 | 61.0794 | 122.699 | 123.0011 | -0.10529 | 122.9828 | 60.9604 | -0.28381 | 123.0011 | -0.10529 | 60.9604 | 122.699 | 122.9828 | -123.2117 | -123.2437
1336.7656 | 123.0972 | -60.8917 | 62.0544 | -0.2253 | -0.0080024 | -0.0094207 | 0.00071144 | 0.057969 | -0.0058639 | 0.066129 | -61.0016 | 62.0636 | -61.1343 | -61.116 | 61.8256 | 0.086975 | 0.10071 | 0.18768 | 62.1048 | -61.1618 | -0.24261 | 0.009156 | -0.10986 | -0.2243 | -0.22888 | -0.27008 | 0.050354 | 0.13275 | 60.9924 | 61.0794 | 122.7173 | 122.9553 | -0.10986 | 122.9965 | 60.9787 | -0.27008 | 122.9553 | -0.10986 | 60.9787 | 122.7173 | 122.9965 | -123.1888 | -123.2162
1337.7812 | 123.1476 | -60.9238 | 62.0087 | 0.27824 | -0.0024482 | -0.0070709 | 0.0062656 | 0.062028 | -0.0035141 | 0.06677 | -61.0428 | 62.0956 | -61.1893 | -61.1618 | 61.7661 | -0.036621 | -0.091553 | 0.054932 | 62.0682 | -61.1847 | -0.2655 | 0.086975 | -0.11902 | -0.23804 | -0.24262 | -0.26093 | 0.059509 | 0.14648 | 60.8322 | 60.9787 | 122.6898 | 123.0194 | -0.11902 | 122.9919 | 60.8871 | -0.26093 | 123.0194 | -0.11902 | 60.8871 | 122.6898 | 122.9919 | -123.1979 | -123.1934
1338.7656 | 123.1201 | -60.8734 | 62.0499 | -0.21767 | -0.0062934 | -0.010489 | 0.00092504 | 0.061387 | -0.0024459 | 0.067624 | -61.0016 | 62.0773 | -61.1526 | -61.0748 | 61.853 | 0.086975 | 0.073242 | 0.20599 | 62.0773 | -61.1618 | -0.27924 | 0.027466 | -0.12817 | -0.20142 | -0.19684 | -0.28839 | 0.027466 | 0.15106 | 60.9467 | 61.0794 | 122.7264 | 122.9507 | -0.12817 | 122.9507 | 60.9604 | -0.28839 | 122.9507 | -0.12817 | 60.9604 | 122.7264 | 122.9507 | -123.2025 | -123.2117
1339.7656 | 123.111 | -60.878 | 62.0636 | -0.18715 | -0.005866 | -0.01113 | -0.00057036 | 0.059891 | -0.0033005 | 0.069761 | -60.9924 | 62.0636 | -61.1435 | -61.0703 | 61.8668 | 0.10986 | 0.073242 | 0.2243 | 62.0773 | -61.1481 | -0.2655 | 0 | -0.11444 | -0.19226 | -0.19684 | -0.27008 | 0.013733 | 0.15106 | 60.9512 | 61.1023 | 122.7448 | 122.9416 | -0.11444 | 122.9553 | 60.9879 | -0.27008 | 122.9416 | -0.11444 | 60.9879 | 122.7448 | 122.9553 | -123.2071 | -123.2117
1340.7656 | 123.1705 | -60.8597 | 62.0224 | -0.17189 | -0.006507 | -0.013266 | 7.0444e-05 | 0.060746 | -0.0041549 | 0.067624 | -60.759 | 62.1048 | -61.084 | -61.0474 | 61.8576 | 0.12817 | -0.054932 | 0.30212 | 62.027 | -61.1252 | -0.2243 | 0.082397 | 0.10071 | -0.18768 | -0.16479 | -0.2655 | 0.004578 | 0.32501 | 60.8047 | 61.1618 | 122.7173 | 122.9645 | 0.10071 | 122.8867 | 60.9879 | -0.2655 | 122.9645 | 0.10071 | 60.9879 | 122.7173 | 122.8867 | -123.1064 | -123.1476
1341.7656 | 123.1338 | -60.8597 | 62.0499 | -0.17189 | -0.0077888 | -0.0083527 | 0.0017794 | 0.060746 | -0.0041549 | 0.068052 | -60.9695 | 62.0499 | -61.1114 | -61.0703 | 61.8713 | 0.1236 | 0.036621 | 0.24719 | 62.059 | -61.1389 | -0.25177 | 0 | -0.10986 | -0.21057 | -0.17853 | -0.27924 | 0.009155 | 0.14191 | 60.8963 | 61.1069 | 122.731 | 122.9095 | -0.10986 | 122.9187 | 60.9833 | -0.27924 | 122.9095 | -0.10986 | 60.9833 | 122.731 | 122.9187 | -123.1613 | -123.1888
1342.7812 | 123.1064 | -60.9055 | 61.9995 | 0.32402 | -0.0024482 | -0.0053619 | 0.0051974 | 0.062455 | -0.0033005 | 0.066129 | -61.0565 | 62.114 | -61.1893 | -61.1618 | 61.7432 | -0.054932 | -0.050354 | 0.022888 | 62.0316 | -61.1984 | -0.28381 | 0.11444 | -0.15106 | -0.25635 | -0.25635 | -0.29297 | 0.032043 | 0.13275 | 60.8551 | 60.9283 | 122.6486 | 123.0194 | -0.15106 | 122.937 | 60.8505 | -0.29297 | 123.0194 | -0.15106 | 60.8505 | 122.6486 | 122.937 | -123.1888 | -123.1979
1343.7656 | 123.1155 | -60.8963 | 62.0636 | -0.17952 | -0.0045844 | -0.0040801 | 0.0022066 | 0.058182 | -0.0033005 | 0.066984 | -61.0336 | 62.0773 | -61.1618 | -61.1343 | 61.8073 | 0.054932 | 0.13733 | 0.18768 | 62.0911 | -61.1481 | -0.2655 | 0.013733 | -0.13733 | -0.23804 | -0.25635 | -0.25177 | 0.027465 | 0.12817 | 61.0336 | 61.084 | 122.7036 | 122.9736 | -0.13733 | 122.9874 | 60.9512 | -0.25177 | 122.9736 | -0.13733 | 60.9512 | 122.7036 | 122.9874 | -123.2254 | -123.2117
1344.7656 | 123.1293 | -60.9009 | 62.059 | -0.20241 | -0.0080024 | -0.0030121 | 0.0013522 | 0.061173 | -0.0039413 | 0.067197 | -61.0336 | 62.0682 | -61.1481 | -61.116 | 61.8027 | 0.07782 | 0.14648 | 0.1831 | 62.0773 | -61.1618 | -0.24719 | 0.009155 | -0.13275 | -0.21515 | -0.25635 | -0.26092 | 0.018311 | 0.11444 | 61.0474 | 61.084 | 122.7036 | 122.9691 | -0.13275 | 122.9782 | 60.9787 | -0.26092 | 122.9691 | -0.13275 | 60.9787 | 122.7036 | 122.9782 | -123.2071 | -123.2208
1345.7656 | 123.1247 | -60.8871 | 62.0499 | -0.19478 | -0.0054388 | -0.0087799 | 0.0015658 | 0.062241 | -0.0056503 | 0.06912 | -60.997 | 62.0728 | -61.1435 | -61.0977 | 61.8393 | 0.091553 | 0.091553 | 0.20599 | 62.0773 | -61.1389 | -0.25635 | 0.022888 | -0.10986 | -0.21057 | -0.21057 | -0.25177 | 0.027466 | 0.14648 | 60.9787 | 61.0931 | 122.7264 | 122.9599 | -0.10986 | 122.9645 | 60.9787 | -0.25177 | 122.9599 | -0.10986 | 60.9787 | 122.7264 | 122.9645 | -123.1934 | -123.1888
1346.7656 | 123.1659 | -60.8734 | 62.0361 | -1.8809 | -0.0056524 | -0.010489 | -0.00078396 | 0.060319 | -0.0037277 | 0.065488 | -61.1481 | 62.0728 | -61.1481 | -61.0474 | 61.8896 | 0.16022 | -0.027466 | 0.28381 | 62.027 | -61.1435 | -0.27466 | 0.036621 | -0.27466 | -0.17395 | -0.14648 | -0.27008 | -0.009155 | 0 | 60.8459 | 61.1572 | 122.7631 | 122.9462 | -0.27466 | 122.9004 | 61.0336 | -0.27008 | 122.9462 | -0.27466 | 61.0336 | 122.7631 | 122.9004 | -123.1842 | -123.1796
1347.7812 | 123.111 | -60.8963 | 62.0544 | 0.072251 | -0.0052252 | -0.0015167 | 0.0069064 | 0.063096 | -0.0037277 | 0.067411 | -61.0428 | 62.1323 | -61.1664 | -61.1435 | 61.7615 | -0.032043 | 0.018311 | 0.068665 | 62.0636 | -61.1755 | -0.27008 | 0.07782 | -0.14648 | -0.24719 | -0.29297 | -0.27924 | 0.009156 | 0.1236 | 60.9146 | 60.965 | 122.6578 | 123.0286 | -0.14648 | 122.9599 | 60.8643 | -0.27924 | 123.0286 | -0.14648 | 60.8643 | 122.6578 | 122.9599 | -123.2208 | -123.23
1348.7656 | 123.0881 | -60.8963 | 62.0911 | -0.16426 | -0.0043708 | -0.0077117 | 0.0017794 | 0.061814 | -0.0041549 | 0.068693 | -61.0428 | 62.1277 | -61.1481 | -61.1298 | 61.821 | 0.059509 | 0.12817 | 0.1831 | 62.0911 | -61.1252 | -0.25177 | 0.036622 | -0.14648 | -0.23346 | -0.27008 | -0.22888 | 0 | 0.10529 | 61.0245 | 61.0794 | 122.7173 | 123.024 | -0.14648 | 122.9874 | 60.9558 | -0.22888 | 123.024 | -0.14648 | 60.9558 | 122.7173 | 122.9874 | -123.2391 | -123.2162
1349.7656 | 123.1155 | -60.878 | 62.0499 | -0.17189 | -0.0056524 | -0.0072845 | 0.00092504 | 0.060319 | -0.0033005 | 0.066984 | -61.0153 | 62.1048 | -61.1389 | -61.116 | 61.8393 | 0.068665 | 0.10529 | 0.1831 | 62.0728 | -61.171 | -0.26093 | 0.054931 | -0.13733 | -0.23804 | -0.21057 | -0.29297 | 0.022888 | 0.1236 | 60.9833 | 61.0611 | 122.7173 | 122.9828 | -0.13733 | 122.9507 | 60.9467 | -0.29297 | 122.9828 | -0.13733 | 60.9467 | 122.7173 | 122.9507 | -123.1888 | -123.2208
1350.7656 | 123.1155 | -60.8826 | 62.0453 | -0.19478 | -0.005866 | -0.0060027 | 0.0017794 | 0.06096 | -0.0050095 | 0.065702 | -60.9924 | 62.0682 | -61.1298 | -61.0977 | 61.8576 | 0.1236 | 0.082397 | 0.22888 | 62.0728 | -61.1206 | -0.24719 | 0.022888 | -0.10986 | -0.21515 | -0.18768 | -0.23804 | 0.027466 | 0.13733 | 60.965 | 61.1114 | 122.7402 | 122.9507 | -0.10986 | 122.9553 | 61.0062 | -0.23804 | 122.9507 | -0.10986 | 61.0062 | 122.7402 | 122.9553 | -123.175 | -123.1659
1351.7656 | 123.1338 | -60.8688 | 62.0316 | -0.19478 | -0.0052252 | -0.010275 | 0.0013522 | 0.06096 | -0.0052231 | 0.071042 | -60.9924 | 62.0636 | -61.1298 | -61.0657 | 61.8759 | 0.13275 | 0.045776 | 0.25635 | 62.0728 | -61.1206 | -0.26093 | 0.032044 | -0.1236 | -0.19684 | -0.15564 | -0.25177 | 0.041199 | 0.13733 | 60.9146 | 61.1252 | 122.7448 | 122.9324 | -0.1236 | 122.9416 | 61.0016 | -0.25177 | 122.9324 | -0.1236 | 61.0016 | 122.7448 | 122.9416 | -123.1613 | -123.1522
1352.7656 | 123.1567 | -60.91 | 62.0132 | 0.2401 | -0.0050116 | -0.0034393 | 0.003702 | 0.064164 | -0.0052231 | 0.067838 | -61.0428 | 62.0544 | -61.171 | -61.1572 | 61.7706 | -0.018311 | -0.091553 | 0.050354 | 62.0407 | -61.1664 | -0.26093 | 0.041198 | -0.13275 | -0.24719 | -0.24262 | -0.25635 | 0.027465 | 0.12817 | 60.8185 | 60.9604 | 122.6807 | 122.9645 | -0.13275 | 122.9507 | 60.8917 | -0.25635 | 122.9645 | -0.13275 | 60.8917 | 122.6807 | 122.9507 | -123.1842 | -123.1796
1353.7656 | 123.2346 | -60.878 | 62.0224 | -0.149 | -0.0039434 | -0.0096343 | -0.0027066 | 0.060532 | -0.0028731 | 0.06912 | -60.9695 | 62.0407 | -61.1114 | -61.0382 | 61.9125 | 0.14191 | -0.027466 | 0.28381 | 62.0453 | -61.1206 | -0.23346 | 0.01831 | -0.091552 | -0.16022 | -0.10986 | -0.24261 | 0.022888 | 0.14191 | 60.8505 | 61.1618 | 122.7905 | 122.9187 | -0.091552 | 122.9233 | 61.0199 | -0.24261 | 122.9187 | -0.091552 | 61.0199 | 122.7905 | 122.9233 | -123.1338 | -123.143
1354.7656 | 123.2346 | -60.8505 | 62.027 | -0.04982 | -0.0077888 | -0.0098479 | -0.00014316 | 0.060532 | -0.0052231 | 0.068265 | -60.9741 | 62.0224 | -61.1389 | -61.0336 | 61.9171 | 0.15564 | -0.07782 | 0.29297 | 62.0499 | -61.1252 | -0.28839 | -0.004578 | -0.1236 | -0.18311 | -0.10986 | -0.27466 | 0.022888 | 0.1648 | 60.7727 | 61.1435 | 122.7676 | 122.8729 | -0.1236 | 122.9004 | 61.0062 | -0.27466 | 122.8729 | -0.1236 | 61.0062 | 122.7676 | 122.9004 | -123.1659 | -123.1522
1355.7656 | 123.1476 | -60.8871 | 62.0224 | -0.17189 | -0.0067206 | -0.011557 | 0.00092504 | 0.060532 | -0.0050095 | 0.067197 | -60.9787 | 62.0316 | -61.1389 | -61.0794 | 61.8668 | 0.10986 | 0.045776 | 0.24719 | 62.0544 | -61.1526 | -0.25177 | 0.009155 | -0.091553 | -0.19226 | -0.15564 | -0.2655 | 0.032043 | 0.16022 | 60.9329 | 61.1343 | 122.7539 | 122.9187 | -0.091553 | 122.9416 | 60.997 | -0.2655 | 122.9187 | -0.091553 | 60.997 | 122.7539 | 122.9416 | -123.1613 | -123.175
1356.7656 | 123.1796 | -60.8734 | 62.0361 | -0.12611 | -0.0069342 | -0.0062163 | 0.0041292 | 0.057969 | -0.0054367 | 0.067838 | -60.9879 | 62.059 | -61.1298 | -61.0336 | 61.8759 | 0.14648 | 0.018311 | 0.27008 | 62.0453 | -61.1572 | -0.25635 | 0.022888 | -0.11444 | -0.16022 | -0.16022 | -0.28381 | 0.009155 | 0.14191 | 60.8917 | 61.1435 | 122.7493 | 122.9324 | -0.11444 | 122.9187 | 61.0199 | -0.28381 | 122.9324 | -0.11444 | 61.0199 | 122.7493 | 122.9187 | -123.1659 | -123.1934
1357.7656 | 123.1842 | -60.8505 | 62.0499 | 0.1638 | -0.006507 | -0.0072845 | 0.0024202 | 0.060532 | -0.0033005 | 0.067411 | -60.9879 | 62.0407 | -61.1435 | -61.0611 | 61.8942 | 0.14191 | -0.013733 | 0.26093 | 62.0361 | -61.116 | -0.29297 | -0.009156 | -0.13733 | -0.21057 | -0.15564 | -0.2655 | -0.013733 | 0.15564 | 60.8368 | 61.1114 | 122.7448 | 122.8912 | -0.13733 | 122.8867 | 60.9924 | -0.2655 | 122.8912 | -0.13733 | 60.9924 | 122.7448 | 122.8867 | -123.1934 | -123.1659
1358.7656 | 123.1796 | -60.8505 | 62.0224 | -2.7201 | -0.004798 | -0.0055755 | 0.0028476 | 0.060746 | -0.0060775 | 0.068479 | -61.0062 | 62.0819 | -61.1298 | -61.0428 | 61.8805 | 0.13733 | -0.004578 | 0.29297 | 62.0316 | -61.1206 | -0.27924 | 0.059509 | -0.15564 | -0.19226 | -0.14191 | -0.27008 | 0.009155 | 0.1236 | 60.8459 | 61.1435 | 122.731 | 122.9324 | -0.15564 | 122.8821 | 60.9879 | -0.27008 | 122.9324 | -0.15564 | 60.9879 | 122.731 | 122.8821 | -123.1522 | -123.143
1359.7656 | 123.1888 | -60.8459 | 62.0407 | -0.14137 | -0.0090704 | -0.013693 | -0.00078396 | 0.058823 | -0.0056503 | 0.066984 | -60.9695 | 62.0407 | -61.1252 | -60.997 | 61.6425 | 0.027466 | -0.091553 | 0.23346 | 62.0178 | -61.1252 | -0.27924 | 0 | -0.1236 | -0.15106 | -0.39825 | -0.27924 | -0.022888 | 0.15564 | 60.7544 | 61.0794 | 122.4884 | 122.8867 | -0.1236 | 122.8638 | 60.8734 | -0.27924 | 122.8867 | -0.1236 | 60.8734 | 122.4884 | 122.8638 | -123.1659 | -123.1659
1360.7656 | 123.2208 | -60.8368 | 61.9949 | -0.019302 | -0.0071478 | -0.010703 | 0.0015658 | 0.059037 | -0.0045821 | 0.067838 | -61.0107 | 62.0316 | -61.1481 | -61.0565 | 61.908 | 0.11444 | -0.09613 | 0.27008 | 62.027 | -61.0977 | -0.31128 | 0.036621 | -0.17395 | -0.21973 | -0.086975 | -0.26093 | 0.032044 | 0.13733 | 60.7407 | 61.1069 | 122.7448 | 122.8683 | -0.17395 | 122.8638 | 60.9512 | -0.26093 | 122.8683 | -0.17395 | 60.9512 | 122.7448 | 122.8638 | -123.143 | -123.0927
1361.7656 | 123.1979 | -60.8597 | 62.0132 | -0.04219 | -0.0071478 | -0.010489 | -0.00035676 | 0.059678 | -0.0052231 | 0.068265 | -61.0062 | 62.0316 | -61.1801 | -61.0565 | 61.8713 | 0.11902 | -0.07782 | 0.23804 | 62.0361 | -61.1252 | -0.32044 | 0.01831 | -0.14649 | -0.19684 | -0.14191 | -0.2655 | 0.022888 | 0.17395 | 60.7819 | 61.0977 | 122.731 | 122.8912 | -0.14649 | 122.8958 | 60.9787 | -0.2655 | 122.8912 | -0.14649 | 60.9787 | 122.731 | 122.8958 | -123.1934 | -123.1384
1362.7656 | 123.1979 | -60.878 | 62.0178 | -0.37025 | -0.0069342 | -0.0057891 | 0.0022066 | 0.060319 | -0.0045821 | 0.067197 | -61.0886 | 62.0224 | -61.1343 | -61.0428 | 61.908 | 0.16022 | -0.022888 | 0.27924 | 62.0499 | -61.1114 | -0.25635 | 0.004578 | -0.21057 | -0.16479 | -0.10986 | -0.23346 | 0.032044 | 0.045776 | 60.8551 | 61.1572 | 122.7859 | 122.9004 | -0.21057 | 122.9279 | 61.0382 | -0.23346 | 122.9004 | -0.21057 | 61.0382 | 122.7859 | 122.9279 | -123.1522 | -123.1293
1363.7656 | 123.2071 | -60.8688 | 61.9904 | -0.149 | -0.0077888 | -0.0089935 | 0.002634 | 0.056473 | -0.0084273 | 0.067197 | -60.965 | 62.0224 | -61.1298 | -61.1206 | 61.6837 | 0.09613 | -0.11444 | 0.27008 | 62.0453 | -61.1206 | -0.26093 | 0.032044 | -0.096131 | -0.25177 | -0.3067 | -0.25177 | 0.054932 | 0.1648 | 60.7544 | 61.1389 | 122.5525 | 122.8912 | -0.096131 | 122.9141 | 60.965 | -0.25177 | 122.8912 | -0.096131 | 60.965 | 122.5525 | 122.9141 | -123.1201 | -123.111
1364.7656 | 123.2941 | -60.8185 | 62.0728 | -0.087967 | -0.0088568 | -0.012625 | 0.0013522 | 0.059891 | -0.0080001 | 0.067197 | -60.9558 | 62.059 | -61.1252 | -61.0428 | 61.9034 | 0.14191 | -0.045776 | 0.27466 | 62.0453 | -61.0931 | -0.3067 | -0.013733 | -0.13733 | -0.22431 | -0.16937 | -0.27466 | -0.027466 | 0.16937 | 60.7727 | 61.0931 | 122.7219 | 122.8775 | -0.13733 | 122.8638 | 60.9604 | -0.27466 | 122.8775 | -0.13733 | 60.9604 | 122.7219 | 122.8638 | -123.1979 | -123.1659
1365.7656 | 123.2071 | -60.8597 | 62.0224 | -0.095596 | -0.0067206 | -0.0098479 | 0.0028476 | 0.060105 | -0.0062911 | 0.066984 | -60.9467 | 62.0453 | -61.1343 | -61.0199 | 61.9171 | 0.13733 | -0.041199 | 0.28381 | 62.0544 | -61.1298 | -0.27466 | 0.022888 | -0.086975 | -0.16022 | -0.10529 | -0.27008 | 0.032043 | 0.18768 | 60.8185 | 61.1435 | 122.7768 | 122.905 | -0.086975 | 122.9141 | 60.997 | -0.27008 | 122.905 | -0.086975 | 60.997 | 122.7768 | 122.9141 | -123.1567 | -123.1522
1366.7656 | 123.2391 | -60.8551 | 61.9904 | -0.080337 | -0.0056524 | -0.01113 | 0.00049764 | 0.059464 | -0.0054367 | 0.067411 | -60.9879 | 62.027 | -61.1572 | -61.0336 | 61.9171 | 0.16479 | -0.073242 | 0.30212 | 62.0407 | -61.1435 | -0.30212 | 0.036622 | -0.13275 | -0.17853 | -0.073242 | -0.28839 | 0.050354 | 0.16937 | 60.7819 | 61.1572 | 122.7722 | 122.8821 | -0.13275 | 122.8958 | 61.0199 | -0.28839 | 122.8821 | -0.13275 | 61.0199 | 122.7722 | 122.8958 | -123.1476 | -123.1338
1367.7656 | 123.1888 | -60.878 | 62.0087 | 0.049362 | -0.0071478 | -0.0089935 | 0.0013522 | 0.05861 | -0.0024459 | 0.067197 | -61.0474 | 62.0316 | -61.1526 | -61.0748 | 61.8668 | 0.064087 | -0.064087 | 0.20142 | 62.0087 | -61.1435 | -0.27466 | 0.022888 | -0.16937 | -0.19684 | -0.14191 | -0.2655 | 0 | 0.10529 | 60.8139 | 61.0794 | 122.7448 | 122.9095 | -0.16937 | 122.8867 | 60.9421 | -0.2655 | 122.9095 | -0.16937 | 60.9421 | 122.7448 | 122.8867 | -123.1613 | -123.1522
1368.7656 | 123.1705 | -60.8597 | 61.9904 | -0.04982 | -0.007575 | -0.0053619 | -0.00014316 | 0.059678 | -0.0035141 | 0.069333 | -61.0428 | 62.027 | -61.1801 | -61.0977 | 61.8347 | 0.064087 | -0.068665 | 0.17853 | 62.0361 | -61.1343 | -0.32044 | 0.036622 | -0.18311 | -0.23804 | -0.15564 | -0.27466 | 0.045777 | 0.13733 | 60.791 | 61.0382 | 122.6944 | 122.8867 | -0.18311 | 122.8958 | 60.9238 | -0.27466 | 122.8867 | -0.18311 | 60.9238 | 122.6944 | 122.8958 | -123.1705 | -123.1247
1369.7656 | 123.23 | -60.8459 | 62.0132 | -0.14137 | -0.0088568 | -0.0064301 | 0.001993 | 0.059037 | -0.0041549 | 0.068479 | -60.9512 | 62.027 | -61.1389 | -61.0107 | 61.9263 | 0.14648 | -0.054932 | 0.28381 | 62.0224 | -61.1114 | -0.29297 | 0.013733 | -0.10529 | -0.16479 | -0.086975 | -0.2655 | 0.009155 | 0.18768 | 60.791 | 61.1298 | 122.7722 | 122.8729 | -0.10529 | 122.8683 | 60.9924 | -0.2655 | 122.8729 | -0.10529 | 60.9924 | 122.7722 | 122.8683 | -123.1522 | -123.1247
1370.7656 | 123.2208 | -60.8643 | 61.9858 | -0.080337 | -0.0067206 | -0.0098479 | -0.00078396 | 0.060746 | -0.0037277 | 0.067197 | -60.9421 | 62.0316 | -61.1206 | -61.0062 | 61.9217 | 0.15564 | -0.091553 | 0.29755 | 62.0453 | -61.0977 | -0.25635 | 0.045776 | -0.07782 | -0.14191 | -0.064087 | -0.23346 | 0.059509 | 0.17853 | 60.7727 | 61.1618 | 122.7859 | 122.8958 | -0.07782 | 122.9095 | 61.0199 | -0.23346 | 122.8958 | -0.07782 | 61.0199 | 122.7859 | 122.9095 | -123.1064 | -123.0835
1371.7656 | 123.2162 | -60.8322 | 62.0361 | -0.034561 | -0.009284 | -0.0074981 | 0.003702 | 0.059037 | -0.0037277 | 0.068265 | -60.9879 | 62.027 | -61.1572 | -61.0153 | 61.9034 | 0.16479 | -0.082397 | 0.27924 | 62.0316 | -61.1023 | -0.32501 | -0.009155 | -0.15564 | -0.18311 | -0.13275 | -0.27008 | -0.004578 | 0.16937 | 60.7498 | 61.1114 | 122.7356 | 122.8592 | -0.15564 | 122.8638 | 60.997 | -0.27008 | 122.8592 | -0.15564 | 60.997 | 122.7356 | 122.8638 | -123.1934 | -123.1384
1372.7656 | 123.2391 | -60.8505 | 61.9995 | 0.0035856 | -0.005866 | -0.010275 | 0.0028476 | 0.060105 | -0.0056503 | 0.065916 | -60.9924 | 62.0224 | -61.1435 | -61.0474 | 61.8851 | 0.13733 | -0.086975 | 0.26093 | 62.0453 | -61.1069 | -0.29297 | 0.022888 | -0.14191 | -0.19684 | -0.11444 | -0.25635 | 0.045776 | 0.15106 | 60.7635 | 61.1114 | 122.7356 | 122.8729 | -0.14191 | 122.8958 | 60.9879 | -0.25635 | 122.8729 | -0.14191 | 60.9879 | 122.7356 | 122.8958 | -123.143 | -123.1064
1373.7656 | 123.2254 | -60.8505 | 62.0041 | -0.072708 | -0.006507 | -0.011557 | 0.00028404 | 0.0616 | -0.0041549 | 0.065275 | -60.9924 | 62.0178 | -61.1343 | -61.0611 | 61.8805 | 0.10529 | -0.073242 | 0.23804 | 62.0499 | -61.0886 | -0.28381 | 0.013733 | -0.14191 | -0.21057 | -0.1236 | -0.23804 | 0.045777 | 0.14191 | 60.7773 | 61.0886 | 122.731 | 122.8683 | -0.14191 | 122.9004 | 60.9558 | -0.23804 | 122.8683 | -0.14191 | 60.9558 | 122.731 | 122.9004 | -123.1384 | -123.0927
1374.7656 | 123.1567 | -60.8734 | 62.0087 | 0.049362 | -0.008216 | -0.0089935 | 0.00049764 | 0.062028 | -0.0065047 | 0.065275 | -61.0428 | 62.0316 | -61.1618 | -61.0428 | 61.8439 | 0.013733 | -0.086975 | 0.13275 | 62.0453 | -61.116 | -0.28839 | 0.022888 | -0.16937 | -0.16937 | -0.1648 | -0.24262 | 0.036621 | 0.11902 | 60.7864 | 61.0062 | 122.7173 | 122.905 | -0.16937 | 122.9187 | 60.8871 | -0.24262 | 122.905 | -0.16937 | 60.8871 | 122.7173 | 122.9187 | -123.1705 | -123.1247
1375.7656 | 123.2117 | -60.8597 | 62.027 | 0.10277 | -0.0060798 | -0.010275 | 0.001993 | 0.060532 | -0.0052231 | 0.069333 | -61.0199 | 62.0087 | -61.1572 | -61.0794 | 61.8622 | 0.059509 | -0.068665 | 0.21057 | 62.0316 | -61.1114 | -0.29755 | -0.018311 | -0.16022 | -0.21973 | -0.16479 | -0.25177 | 0.004577 | 0.13733 | 60.791 | 61.0703 | 122.7219 | 122.8683 | -0.16022 | 122.8912 | 60.9192 | -0.25177 | 122.8683 | -0.16022 | 60.9192 | 122.7219 | 122.8912 | -123.1842 | -123.1384
1376.7656 | 123.2071 | -60.8322 | 62.0041 | -0.019302 | -0.0060798 | -0.010703 | 0.0013522 | 0.057542 | -0.0035141 | 0.067624 | -60.9924 | 62.0499 | -61.1481 | -61.0474 | 61.8851 | 0.10986 | -0.082397 | 0.25635 | 62.0316 | -61.1069 | -0.31586 | 0.045777 | -0.16022 | -0.21515 | -0.11902 | -0.27466 | 0.027466 | 0.15564 | 60.7498 | 61.0886 | 122.7173 | 122.8821 | -0.16022 | 122.8638 | 60.9421 | -0.27466 | 122.8821 | -0.16022 | 60.9421 | 122.7173 | 122.8638 | -123.1522 | -123.111
1377.7656 | 123.1979 | -60.878 | 62.0178 | 0.0035856 | -0.0069342 | -0.0098479 | 0.0017794 | 0.059891 | -0.0043685 | 0.067411 | -61.0062 | 62.0178 | -61.1481 | -61.0748 | 61.8576 | 0.086975 | -0.064087 | 0.22888 | 62.0178 | -61.1069 | -0.27008 | 0 | -0.12817 | -0.19684 | -0.16022 | -0.22888 | 0 | 0.14191 | 60.8139 | 61.1069 | 122.7356 | 122.8958 | -0.12817 | 122.8958 | 60.965 | -0.22888 | 122.8958 | -0.12817 | 60.965 | 122.7356 | 122.8958 | -123.1659 | -123.1247
1378.7656 | 123.1659 | -60.8826 | 62.0087 | 0.087509 | -0.005866 | -0.010703 | 0.00028404 | 0.059891 | -0.0039413 | 0.066984 | -61.0153 | 62.0178 | -61.1435 | -61.0703 | 61.8713 | 0.10071 | -0.064087 | 0.19684 | 62.0361 | -61.1206 | -0.26093 | 0.009155 | -0.13275 | -0.18768 | -0.13733 | -0.23804 | 0.027466 | 0.12817 | 60.8185 | 61.0794 | 122.7539 | 122.9004 | -0.13275 | 122.9187 | 60.9833 | -0.23804 | 122.9004 | -0.13275 | 60.9833 | 122.7539 | 122.9187 | -123.1522 | -123.1293
1379.7656 | 123.1705 | -60.8688 | 62.0178 | 0.14854 | -0.0067206 | -0.0081389 | -0.00057036 | 0.0616 | -0.0045821 | 0.067411 | -61.0291 | 62.0407 | -61.1481 | -61.0977 | 61.8347 | 0.045776 | -0.073242 | 0.1831 | 62.0132 | -61.1114 | -0.27924 | 0.022888 | -0.16022 | -0.22888 | -0.18311 | -0.24262 | -0.004577 | 0.11902 | 60.7956 | 61.0519 | 122.7036 | 122.9095 | -0.16022 | 122.8821 | 60.9146 | -0.24262 | 122.9095 | -0.16022 | 60.9146 | 122.7036 | 122.8821 | -123.1659 | -123.1293
1380.7656 | 123.1338 | -60.9009 | 62.0087 | 0.064621 | -0.0069342 | -0.0057891 | -0.00057036 | 0.060746 | -0.0033005 | 0.070402 | -60.9787 | 62.027 | -61.1435 | -61.0931 | 61.8301 | 0.022888 | -0.082397 | 0.16022 | 62.0316 | -61.1114 | -0.24261 | 0.018311 | -0.07782 | -0.19226 | -0.17853 | -0.21057 | 0.022888 | 0.16479 | 60.8185 | 61.0611 | 122.731 | 122.9279 | -0.07782 | 122.9324 | 60.9238 | -0.21057 | 122.9279 | -0.07782 | 60.9238 | 122.731 | 122.9324 | -123.1522 | -123.1201
1381.7656 | 123.1522 | -60.8917 | 62.0087 | 0.1638 | -0.0077888 | -0.010275 | 0.001993 | 0.061387 | -0.0047957 | 0.068265 | -61.0382 | 61.9858 | -61.1526 | -61.1069 | 61.8027 | 0.009155 | -0.10529 | 0.14191 | 61.9949 | -61.1526 | -0.26092 | -0.022888 | -0.14648 | -0.21515 | -0.20599 | -0.26092 | -0.013733 | 0.11444 | 60.7864 | 61.0336 | 122.6944 | 122.8775 | -0.14648 | 122.8867 | 60.9009 | -0.26092 | 122.8775 | -0.14648 | 60.9009 | 122.6944 | 122.8867 | -123.1613 | -123.1613
1382.7656 | 123.1384 | -60.8688 | 62.0361 | 0.15617 | -0.008216 | -0.011557 | -0.00078396 | 0.060746 | -0.0045821 | 0.068052 | -61.0474 | 62.0132 | -61.1526 | -61.1069 | 61.821 | 0.013733 | -0.082397 | 0.14191 | 62.0544 | -61.1252 | -0.28381 | -0.022888 | -0.17853 | -0.23804 | -0.21515 | -0.25635 | 0.01831 | 0.10529 | 60.7864 | 61.0107 | 122.6898 | 122.8821 | -0.17853 | 122.9233 | 60.8826 | -0.25635 | 122.8821 | -0.17853 | 60.8826 | 122.6898 | 122.9233 | -123.1888 | -123.1613
1383.7656 | 123.175 | -60.9009 | 62.0041 | 0.07988 | -0.0073614 | -0.011771 | 7.0444e-05 | 0.060319 | -0.0047957 | 0.068693 | -60.9192 | 62.0499 | -61.1435 | -61.1023 | 61.8439 | 0.050354 | -0.082397 | 0.15106 | 62.0087 | -61.1206 | -0.24261 | 0.045777 | -0.01831 | -0.20142 | -0.16022 | -0.21973 | 0.004578 | 0.2243 | 60.8185 | 61.0519 | 122.7448 | 122.9507 | -0.01831 | 122.9095 | 60.9512 | -0.21973 | 122.9507 | -0.01831 | 60.9512 | 122.7448 | 122.9095 | -123.1476 | -123.1247
1384.7656 | 123.1659 | -60.8597 | 62.0132 | 0.07988 | -0.0045844 | -0.0074981 | 0.0024202 | 0.059251 | -0.0039413 | 0.067838 | -61.0428 | 62.0087 | -61.1847 | -61.1114 | 61.8347 | 0.032043 | -0.009155 | 0.30212 | 62.0636 | -61.1069 | -0.32501 | -0.004578 | -0.18311 | -0.25177 | -0.17853 | -0.24719 | 0.050354 | 0.14191 | 60.8505 | 61.1618 | 122.6944 | 122.8683 | -0.18311 | 122.9233 | 60.8917 | -0.24719 | 122.8683 | -0.18311 | 60.8917 | 122.6944 | 122.9233 | -123.1979 | -123.1201
1385.7656 | 123.1888 | -60.8688 | 61.9949 | 0.095139 | -0.0069342 | -0.0055755 | -0.00057036 | 0.059037 | -0.0041549 | 0.068479 | -61.0382 | 62.0361 | -61.1618 | -61.116 | 61.821 | 0.027466 | -0.082397 | 0.13275 | 62.0041 | -61.1481 | -0.29297 | 0.041199 | -0.16937 | -0.24719 | -0.17395 | -0.27924 | 0.009155 | 0.1236 | 60.7864 | 61.0016 | 122.6898 | 122.905 | -0.16937 | 122.8729 | 60.8963 | -0.27924 | 122.905 | -0.16937 | 60.8963 | 122.6898 | 122.8729 | -123.1567 | -123.143
1386.7656 | 123.1567 | -60.8826 | 61.9995 | 0.11803 | -0.0060798 | -0.0060027 | -0.00099756 | 0.061387 | -0.0041549 | 0.067624 | -61.0336 | 62.0178 | -61.1435 | -61.1206 | 61.8301 | 0.027466 | -0.086975 | 0.14191 | 62.0178 | -61.116 | -0.26093 | 0.01831 | -0.15106 | -0.23804 | -0.16937 | -0.23346 | 0.01831 | 0.10986 | 60.7956 | 61.0245 | 122.7127 | 122.9004 | -0.15106 | 122.9004 | 60.91 | -0.23346 | 122.9004 | -0.15106 | 60.91 | 122.7127 | 122.9004 | -123.143 | -123.1155
1387.7656 | 123.1934 | -60.8734 | 61.9812 | 0.21721 | -0.0073614 | -0.00087594 | 0.0015658 | 0.059464 | -0.0067185 | 0.066984 | -60.9879 | 62.0178 | -61.1618 | -61.0703 | 61.853 | 0.041199 | -0.17853 | 0.14648 | 61.9949 | -61.1298 | -0.28839 | 0.036621 | -0.11444 | -0.19684 | -0.12817 | -0.25635 | 0.013733 | 0.17395 | 60.6949 | 61.0199 | 122.7264 | 122.8912 | -0.11444 | 122.8683 | 60.9146 | -0.25635 | 122.8912 | -0.11444 | 60.9146 | 122.7264 | 122.8683 | -123.143 | -123.111
1388.7656 | 123.2025 | -60.8688 | 61.9858 | 0.14854 | -0.005866 | -0.0066437 | 0.0024202 | 0.061173 | -0.0060775 | 0.066984 | -60.9833 | 62.0178 | -61.1664 | -61.0565 | 61.853 | 0.050354 | -0.18768 | 0.15564 | 62.0316 | -61.1252 | -0.29755 | 0.032043 | -0.11444 | -0.18768 | -0.13275 | -0.25635 | 0.045776 | 0.18311 | 60.6812 | 61.0245 | 122.7219 | 122.8867 | -0.11444 | 122.9004 | 60.9192 | -0.25635 | 122.8867 | -0.11444 | 60.9192 | 122.7219 | 122.9004 | -123.1522 | -123.111
1389.7656 | 123.1842 | -60.8871 | 61.9995 | 0.20958 | -0.0056524 | -0.0062163 | 0.00028404 | 0.063309 | -0.0054367 | 0.065702 | -61.0107 | 62.0041 | -61.1664 | -61.1023 | 61.8301 | 0.018311 | -0.14648 | 0.13275 | 62.0224 | -61.1481 | -0.27924 | 0.004577 | -0.1236 | -0.21515 | -0.16937 | -0.26093 | 0.022888 | 0.15564 | 60.7407 | 61.0199 | 122.7173 | 122.8912 | -0.1236 | 122.9095 | 60.9055 | -0.26093 | 122.8912 | -0.1236 | 60.9055 | 122.7173 | 122.9095 | -123.1659 | -123.1476
1390.7656 | 123.143 | -60.8551 | 62.0178 | 0.12566 | -0.0054388 | -0.0087799 | -0.00035676 | 0.059891 | -0.0047957 | 0.066343 | -61.0519 | 62.027 | -61.1526 | -61.1206 | 61.8256 | 0.032043 | -0.082397 | 0.13275 | 62.0041 | -61.1435 | -0.29755 | 0.009156 | -0.19684 | -0.2655 | -0.19226 | -0.28839 | -0.013733 | 0.10071 | 60.7727 | 60.9879 | 122.6807 | 122.8821 | -0.19684 | 122.8592 | 60.8871 | -0.28839 | 122.8821 | -0.19684 | 60.8871 | 122.6807 | 122.8592 | -123.1705 | -123.1613
1391.7656 | 123.1476 | -60.8826 | 61.9858 | 0.18669 | -0.0060798 | -0.0079253 | 0.00049764 | 0.060319 | -0.0045821 | 0.066129 | -61.0428 | 61.9995 | -61.1755 | -61.1206 | 61.8347 | 0.027466 | -0.10986 | 0.10986 | 62.0087 | -61.1435 | -0.29297 | 0.013733 | -0.16022 | -0.23804 | -0.15106 | -0.26093 | 0.022888 | 0.13275 | 60.7727 | 60.9924 | 122.7173 | 122.8821 | -0.16022 | 122.8912 | 60.91 | -0.26093 | 122.8821 | -0.16022 | 60.91 | 122.7173 | 122.8912 | -123.1613 | -123.1293
1392.7656 | 123.1567 | -60.8826 | 61.9949 | 0.19432 | -0.006507 | -0.010489 | 0.0032748 | 0.062455 | -0.0056503 | 0.067411 | -61.0336 | 62.0132 | -61.1389 | -61.1114 | 61.8256 | 0.013733 | -0.1236 | 0.12817 | 62.0224 | -61.1206 | -0.25635 | 0.018311 | -0.15106 | -0.22888 | -0.16937 | -0.23804 | 0.027466 | 0.10529 | 60.759 | 61.0107 | 122.7081 | 122.8958 | -0.15106 | 122.905 | 60.8963 | -0.23804 | 122.8958 | -0.15106 | 60.8963 | 122.7081 | 122.905 | -123.1338 | -123.1155
1393.7656 | 123.1979 | -60.8734 | 61.9995 | 0.041733 | -0.005866 | -0.0064301 | -0.00035676 | 0.062028 | -0.0028731 | 0.067197 | -61.0245 | 62.0224 | -61.171 | -61.0794 | 61.8942 | 0.10529 | -0.068665 | 0.20599 | 62.027 | -61.1252 | -0.29755 | 0.022888 | -0.15106 | -0.20599 | -0.10529 | -0.25177 | 0.027466 | 0.14648 | 60.8047 | 61.0794 | 122.7676 | 122.8958 | -0.15106 | 122.9004 | 60.9787 | -0.25177 | 122.8958 | -0.15106 | 60.9787 | 122.7676 | 122.9004 | -123.1705 | -123.1247
1394.7656 | 123.2071 | -60.8734 | 61.9904 | 0.27824 | -0.0073614 | -0.0096343 | 0.0051974 | 0.061814 | -0.0047957 | 0.068693 | -60.9787 | 62.0316 | -61.1481 | -61.235 | 61.8851 | 0.11902 | -0.13275 | 0.1831 | 61.9858 | -61.1343 | -0.27466 | 0.041199 | -0.10529 | -0.36163 | -0.10528 | -0.26093 | -0.004577 | 0.16937 | 60.7407 | 61.0565 | 122.7585 | 122.905 | -0.10529 | 122.8592 | 60.9924 | -0.26093 | 122.905 | -0.10529 | 60.9924 | 122.7585 | 122.8592 | -123.1384 | -123.1247
1395.7656 | 123.2346 | -60.8734 | 61.9675 | 0.26299 | -0.0067206 | -0.0089935 | 0.0045566 | 0.062241 | -0.0058639 | 0.067197 | -60.965 | 62.0361 | -61.1618 | -61.0703 | 61.853 | 0.045776 | -0.20142 | 0.13733 | 61.972 | -61.1526 | -0.28839 | 0.068665 | -0.091553 | -0.19684 | -0.11444 | -0.27924 | 0.004578 | 0.19684 | 60.672 | 61.0107 | 122.7264 | 122.9095 | -0.091553 | 122.8455 | 60.9192 | -0.27924 | 122.9095 | -0.091553 | 60.9192 | 122.7264 | 122.8455 | -123.1293 | -123.1201
1396.7656 | 123.1613 | -60.9055 | 62.0132 | 0.18669 | -0.0039434 | -0.0083527 | 7.0444e-05 | 0.060319 | -0.0041549 | 0.067411 | -61.0382 | 62.027 | -61.1526 | -61.1252 | 61.8164 | 0.036621 | -0.10986 | 0.12817 | 62.0316 | -61.1298 | -0.24719 | 0.013733 | -0.13275 | -0.21973 | -0.19684 | -0.2243 | 0.01831 | 0.11444 | 60.7956 | 61.0336 | 122.7219 | 122.9324 | -0.13275 | 122.937 | 60.9421 | -0.2243 | 122.9324 | -0.13275 | 60.9421 | 122.7219 | 122.937 | -123.1659 | -123.143
1397.7656 | 123.1613 | -60.8688 | 62.0087 | 0.17906 | -0.0041572 | -0.0066437 | 0.00092504 | 0.059678 | -0.0030869 | 0.068693 | -61.0336 | 62.0544 | -61.1664 | -61.1298 | 61.8347 | 0.018311 | -0.10986 | 0.11902 | 62.0132 | -61.1481 | -0.29755 | 0.045776 | -0.1648 | -0.26093 | -0.17395 | -0.27924 | 0.004578 | 0.13275 | 60.759 | 60.9879 | 122.7036 | 122.9233 | -0.1648 | 122.8821 | 60.8871 | -0.27924 | 122.9233 | -0.1648 | 60.8871 | 122.7036 | 122.8821 | -123.175 | -123.1567
1398.7812 | 123.2346 | -60.878 | 62.0087 | 0.011215 | -0.0086432 | -0.010916 | -0.00057036 | 0.058823 | -0.0067185 | 0.068265 | -61.0062 | 62.0453 | -61.1481 | -61.0519 | 61.8988 | 0.13275 | -0.07782 | 0.27924 | 61.9995 | -61.0886 | -0.27008 | 0.036621 | -0.12817 | -0.17395 | -0.10986 | -0.21057 | -0.009155 | 0.14191 | 60.8002 | 61.1572 | 122.7768 | 122.9233 | -0.12817 | 122.8775 | 61.0107 | -0.21057 | 122.9233 | -0.12817 | 61.0107 | 122.7768 | 122.8775 | -123.1567 | -123.0972
1399.7656 | 123.1888 | -60.9009 | 62.0041 | 0.21721 | -0.005866 | -0.0051483 | 0.0022066 | 0.060105 | -0.0052231 | 0.065916 | -61.0153 | 62.0224 | -61.1801 | -61.1114 | 61.821 | 0.041199 | -0.13733 | 0.1236 | 61.9995 | -61.1343 | -0.27924 | 0.018311 | -0.11444 | -0.21057 | -0.1831 | -0.23346 | -0.004577 | 0.16479 | 60.7636 | 61.0245 | 122.7219 | 122.9233 | -0.11444 | 122.9004 | 60.9421 | -0.23346 | 122.9233 | -0.11444 | 60.9421 | 122.7219 | 122.9004 | -123.1842 | -123.1384
1400.7656 | 123.1842 | -60.8688 | 61.9995 | 0.20195 | -0.0043708 | -0.0092071 | 0.0024202 | 0.060319 | -0.0037277 | 0.068906 | -61.0062 | 62.0178 | -61.1572 | -61.0931 | 61.8347 | 0.036621 | -0.15564 | 0.13733 | 61.9995 | -61.1435 | -0.28839 | 0.01831 | -0.13733 | -0.22431 | -0.1648 | -0.27466 | 0 | 0.15106 | 60.7132 | 61.0062 | 122.7036 | 122.8867 | -0.13733 | 122.8683 | 60.9055 | -0.27466 | 122.8867 | -0.13733 | 60.9055 | 122.7036 | 122.8683 | -123.1567 | -123.143
1401.7656 | 123.2025 | -60.878 | 61.9949 | 0.26299 | -0.006507 | -0.0066437 | 0.0060518 | 0.064591 | -0.0043685 | 0.065916 | -60.965 | 62.0132 | -61.1664 | -60.9695 | 61.9492 | 0.09613 | -0.17853 | 0.18768 | 61.9904 | -61.1435 | -0.28839 | 0.018311 | -0.086975 | -0.091552 | -0.045776 | -0.2655 | -0.004578 | 0.20142 | 60.6995 | 61.0657 | 122.8271 | 122.8912 | -0.086975 | 122.8683 | 60.9741 | -0.2655 | 122.8912 | -0.086975 | 60.9741 | 122.8271 | 122.8683 | -123.1613 | -123.1384
1402.7656 | 123.2391 | -60.8551 | 62.0087 | 0.27061 | -0.0052252 | -0.0072845 | 0.0034884 | 0.061387 | -0.0058639 | 0.067838 | -60.9741 | 62.0316 | -61.1572 | -61.0382 | 61.6516 | -0.1236 | -0.082397 | 0.21973 | 61.9904 | -61.1298 | -0.30212 | 0.022888 | -0.11902 | -0.1831 | -0.35706 | -0.27466 | -0.018311 | 0.18311 | 60.7727 | 61.0748 | 122.5067 | 122.8867 | -0.11902 | 122.8455 | 60.7315 | -0.27466 | 122.8867 | -0.11902 | 60.7315 | 122.5067 | 122.8455 | -123.1659 | -123.1384
1403.7812 | 123.2162 | -60.8414 | 62.027 | 2.0635 | -0.0039434 | -0.0064301 | 0.0015658 | 0.059678 | -0.0071457 | 0.067838 | -60.9879 | 62.0316 | -61.1435 | -61.0153 | 61.9171 | 0.15106 | -0.032043 | 0.27466 | 62.0316 | -61.1114 | -0.30212 | 0.004577 | -0.14648 | -0.17395 | -0.10986 | -0.27008 | 0.004577 | 0.15564 | 60.8093 | 61.116 | 122.7585 | 122.8729 | -0.14648 | 122.8729 | 60.9924 | -0.27008 | 122.8729 | -0.14648 | 60.9924 | 122.7585 | 122.8729 | -123.1705 | -123.1384
1404.7812 | 123.2071 | -60.8917 | 62.0224 | -0.0040434 | -0.0060798 | -0.011343 | 0.00071144 | 0.059678 | -0.0045821 | 0.067624 | -61.0291 | 62.0316 | -61.1572 | -61.0657 | 61.8622 | 0.091553 | -0.086975 | 0.19684 | 62.0041 | -61.116 | -0.2655 | 0.009155 | -0.13733 | -0.17395 | -0.16022 | -0.2243 | -0.018311 | 0.12817 | 60.8047 | 61.0886 | 122.7539 | 122.9233 | -0.13733 | 122.8958 | 60.9833 | -0.2243 | 122.9233 | -0.13733 | 60.9833 | 122.7539 | 122.8958 | -123.1796 | -123.1384
1405.7656 | 123.1705 | -60.8963 | 62.0178 | 0.19432 | -0.007575 | -0.0079253 | 0.0015658 | 0.059037 | -0.0030869 | 0.068906 | -61.0336 | 62.0132 | -61.1435 | -61.1252 | 61.821 | 0.013733 | -0.11444 | 0.11902 | 62.0224 | -61.1526 | -0.24719 | -0.004577 | -0.13733 | -0.22888 | -0.19684 | -0.25635 | 0.004578 | 0.10986 | 60.7819 | 61.0153 | 122.7173 | 122.9095 | -0.13733 | 122.9187 | 60.91 | -0.25635 | 122.9095 | -0.13733 | 60.91 | 122.7173 | 122.9187 | -123.1613 | -123.1705
1406.7656 | 123.1522 | -60.8917 | 62.0041 | 0.20195 | -0.0050116 | -0.0083527 | 0.0034884 | 0.057542 | -0.0062911 | 0.069547 | -61.0291 | 62.0132 | -61.1664 | -61.1252 | 61.821 | 0.027466 | -0.10986 | 0.13275 | 62.0087 | -61.1252 | -0.27466 | 0.009156 | -0.13733 | -0.23346 | -0.1831 | -0.23346 | 0.004578 | 0.13733 | 60.7819 | 61.0245 | 122.7127 | 122.905 | -0.13733 | 122.9004 | 60.9192 | -0.23346 | 122.905 | -0.13733 | 60.9192 | 122.7127 | 122.9004 | -123.1705 | -123.1293
1407.7656 | 123.1705 | -60.8551 | 62.0132 | 0.20958 | -0.0043708 | -0.0094207 | 0.0022066 | 0.059891 | -0.0024459 | 0.067838 | -61.0245 | 62.0361 | -61.1755 | -61.1069 | 61.8301 | 0.018311 | -0.12817 | 0.13275 | 61.9995 | -61.1389 | -0.32043 | 0.022888 | -0.16937 | -0.25177 | -0.18311 | -0.28381 | -0.013733 | 0.15106 | 60.7269 | 60.9879 | 122.6852 | 122.8912 | -0.16937 | 122.8546 | 60.8734 | -0.28381 | 122.8912 | -0.16937 | 60.8734 | 122.6852 | 122.8546 | -123.1888 | -123.1522
1408.7812 | 123.143 | -60.8871 | 62.0636 | -0.072708 | -0.0037298 | -0.0019439 | 0.0077608 | 0.061814 | -0.0039413 | 0.066556 | -60.9695 | 62.146 | -61.1618 | -61.0794 | 61.8256 | 0.059509 | 0.041199 | 0.18768 | 62.0453 | -61.1893 | -0.27466 | 0.082397 | -0.082397 | -0.19226 | -0.23804 | -0.30212 | -0.018311 | 0.19226 | 60.9283 | 61.0748 | 122.7127 | 123.0331 | -0.082397 | 122.9324 | 60.9467 | -0.30212 | 123.0331 | -0.082397 | 60.9467 | 122.7127 | 122.9324 | -123.2254 | -123.2529
1409.7656 | 123.1979 | -60.8871 | 61.9537 | 0.26299 | -0.0069342 | -0.0066437 | 0.0030612 | 0.060746 | -0.0033005 | 0.068052 | -60.9055 | 62.0316 | -61.1755 | -61.0657 | 61.8668 | 0.059509 | -0.17395 | 0.17395 | 62.0407 | -61.1435 | -0.28839 | 0.07782 | -0.018311 | -0.17853 | -0.086975 | -0.25635 | 0.086975 | 0.27008 | 60.7132 | 61.0611 | 122.7539 | 122.9187 | -0.018311 | 122.9279 | 60.9467 | -0.25635 | 122.9187 | -0.018311 | 60.9467 | 122.7539 | 122.9279 | -123.1293 | -123.0972
1410.7656 | 123.1796 | -60.8917 | 61.9995 | 0.20195 | -0.0045844 | -0.0053619 | -0.00078396 | 0.059678 | -0.0043685 | 0.069761 | -61.0703 | 62.0544 | -61.1801 | -61.1023 | 61.8118 | 0.036621 | -0.091553 | 0.14191 | 62.0087 | -61.1343 | -0.28839 | 0.054931 | -0.17853 | -0.21057 | -0.18768 | -0.24261 | 0.009155 | 0.10986 | 60.8002 | 61.0336 | 122.7036 | 122.9462 | -0.17853 | 122.9004 | 60.9283 | -0.24261 | 122.9462 | -0.17853 | 60.9283 | 122.7036 | 122.9004 | -123.1796 | -123.1338
1411.7812 | 123.1705 | -60.8917 | 61.9995 | 0.095139 | -0.0041572 | -0.0060027 | 0.00028404 | 0.060746 | -0.0047957 | 0.06677 | -61.0474 | 62.0316 | -61.171 | -61.1298 | 61.8393 | 0.032043 | -0.059509 | 0.15564 | 62.0316 | -61.1389 | -0.27923 | 0.032043 | -0.15564 | -0.23804 | -0.16022 | -0.24719 | 0.032043 | 0.1236 | 60.8322 | 61.0474 | 122.731 | 122.9233 | -0.15564 | 122.9233 | 60.9238 | -0.24719 | 122.9233 | -0.15564 | 60.9238 | 122.731 | 122.9233 | -123.1705 | -123.1384
1412.7812 | 123.1476 | -60.8871 | 61.9949 | 0.095139 | -0.0056524 | -0.010275 | 0.001993 | 0.058823 | -0.0028731 | 0.066556 | -61.0565 | 62.0224 | -61.1526 | -61.0199 | 61.853 | 0.022888 | -0.068665 | 0.15106 | 62.0178 | -61.1298 | -0.2655 | 0.027466 | -0.16937 | -0.13275 | -0.14191 | -0.24262 | 0.022888 | 0.09613 | 60.8185 | 61.0382 | 122.7402 | 122.9095 | -0.16937 | 122.905 | 60.91 | -0.24262 | 122.9095 | -0.16937 | 60.91 | 122.7402 | 122.905 | -123.1476 | -123.1247
1413.7812 | 123.0927 | -60.8917 | 62.0316 | 0.07988 | -0.0045844 | -0.0062163 | 0.0096834 | 0.059251 | -0.0041549 | 0.065916 | -60.9695 | 62.1368 | -61.1526 | -61.0931 | 61.8027 | 0.032043 | 0.009155 | 0.13275 | 62.0224 | -61.1984 | -0.26092 | 0.10529 | -0.077819 | -0.20142 | -0.22888 | -0.3067 | -0.009155 | 0.18311 | 60.9009 | 61.0245 | 122.6944 | 123.0286 | -0.077819 | 122.9141 | 60.9238 | -0.3067 | 123.0286 | -0.077819 | 60.9238 | 122.6944 | 122.9141 | -123.1842 | -123.23
1414.7656 | 123.1888 | -60.8688 | 61.9858 | 0.10277 | -0.0050116 | -0.0047211 | 0.0022066 | 0.062882 | -0.0058639 | 0.068052 | -60.9787 | 62.0224 | -61.1435 | -61.0748 | 61.8622 | 0.054932 | -0.17853 | 0.14191 | 62.0316 | -61.1664 | -0.27466 | 0.036621 | -0.10986 | -0.20599 | -0.1236 | -0.29755 | 0.045776 | 0.16479 | 60.6903 | 61.0107 | 122.731 | 122.8912 | -0.10986 | 122.9004 | 60.9238 | -0.29755 | 122.8912 | -0.10986 | 60.9238 | 122.731 | 122.9004 | -123.1293 | -123.1522
1415.7656 | 123.2025 | -60.8871 | 62.0178 | 0.13329 | -0.006507 | -0.0089935 | 0.0022066 | 0.063737 | -0.0043685 | 0.06912 | -60.9055 | 62.027 | -61.1435 | -61.0657 | 61.8439 | 0.041199 | -0.20599 | 0.14191 | 62.0224 | -61.116 | -0.25635 | 0.009156 | -0.018311 | -0.17853 | -0.17395 | -0.22888 | 0.004578 | 0.23804 | 60.6812 | 61.0291 | 122.731 | 122.9141 | -0.018311 | 122.9095 | 60.9283 | -0.22888 | 122.9141 | -0.018311 | 60.9283 | 122.731 | 122.9095 | -123.1613 | -123.1338
1416.7656 | 123.2025 | -60.8597 | 61.9949 | 0.2401 | -0.0054388 | -0.0049347 | 0.0015658 | 0.061173 | -0.0056503 | 0.068479 | -60.997 | 62.027 | -61.171 | -61.0565 | 61.8851 | 0.059509 | -0.16479 | 0.16479 | 62.0178 | -61.1206 | -0.31128 | 0.032044 | -0.13733 | -0.19684 | -0.10986 | -0.26093 | 0.022888 | 0.17395 | 60.6949 | 61.0245 | 122.7448 | 122.8867 | -0.13733 | 122.8775 | 60.9192 | -0.26093 | 122.8867 | -0.13733 | 60.9192 | 122.7448 | 122.8775 | -123.1659 | -123.1155
1417.7656 | 123.1384 | -60.8963 | 61.9949 | 0.15617 | -0.0067206 | -0.011343 | 0.0032748 | 0.062028 | -0.0039413 | 0.06677 | -61.0336 | 62.0316 | -61.1755 | -61.1252 | 61.8256 | 0.036621 | -0.091553 | 0.12817 | 62.0041 | -61.1343 | -0.27924 | 0.036621 | -0.13733 | -0.22888 | -0.16937 | -0.23804 | 0.009155 | 0.14191 | 60.8047 | 61.0245 | 122.7219 | 122.9279 | -0.13733 | 122.9004 | 60.9329 | -0.23804 | 122.9279 | -0.13733 | 60.9329 | 122.7219 | 122.9004 | -123.1705 | -123.1293
1418.7812 | 123.0606 | -60.91 | 62.0316 | 0.14854 | -0.0045844 | -0.0051483 | 0.0092562 | 0.061814 | -0.0067185 | 0.068265 | -61.0382 | 62.1323 | -61.1435 | -61.1572 | 61.7523 | -0.036621 | 0.027466 | 0.050354 | 62.0636 | -61.2076 | -0.23346 | 0.10071 | -0.12817 | -0.24719 | -0.27924 | -0.29755 | 0.032044 | 0.10529 | 60.9375 | 60.9604 | 122.6624 | 123.0423 | -0.12817 | 122.9736 | 60.8734 | -0.29755 | 123.0423 | -0.12817 | 60.8734 | 122.6624 | 122.9736 | -123.175 | -123.2391
1419.7656 | 123.1796 | -60.8963 | 62.0041 | 0.20195 | -0.0054388 | -0.01113 | -0.00014316 | 0.062241 | -0.0020187 | 0.069761 | -61.0519 | 62.027 | -61.1893 | -61.1252 | 61.8347 | 0.022888 | -0.10986 | 0.13275 | 62.027 | -61.1435 | -0.29297 | 0.022889 | -0.15564 | -0.22888 | -0.16937 | -0.24719 | 0.022889 | 0.13733 | 60.7864 | 61.0291 | 122.731 | 122.9233 | -0.15564 | 122.9233 | 60.9192 | -0.24719 | 122.9233 | -0.15564 | 60.9192 | 122.731 | 122.9233 | -123.1934 | -123.1476
1420.7656 | 123.1567 | -60.878 | 61.9858 | 0.21721 | -0.0039434 | -0.0055755 | -0.00014316 | 0.060746 | -0.0054367 | 0.068265 | -61.0199 | 62.0499 | -61.1801 | -61.1252 | 61.8347 | 0.032043 | -0.15564 | 0.14191 | 61.9949 | -61.1435 | -0.30212 | 0.064087 | -0.14191 | -0.24719 | -0.15106 | -0.2655 | 0.009155 | 0.16022 | 60.7224 | 61.0199 | 122.7127 | 122.9279 | -0.14191 | 122.8729 | 60.91 | -0.2655 | 122.9279 | -0.14191 | 60.91 | 122.7127 | 122.8729 | -123.1659 | -123.1293
1421.7656 | 123.1842 | -60.8688 | 61.9949 | 0.20958 | -0.0056524 | -0.0081389 | 0.00071144 | 0.059891 | -0.0043685 | 0.06912 | -61.0153 | 62.0316 | -61.1618 | -61.1023 | 61.8439 | 0.036621 | -0.15564 | 0.15106 | 62.0178 | -61.1664 | -0.29297 | 0.036621 | -0.14649 | -0.23346 | -0.15106 | -0.29755 | 0.022888 | 0.14648 | 60.7132 | 61.0199 | 122.7127 | 122.9004 | -0.14649 | 122.8867 | 60.9055 | -0.29755 | 122.9004 | -0.14649 | 60.9055 | 122.7127 | 122.8867 | -123.1567 | -123.1613
1422.7656 | 123.2071 | -60.8917 | 61.9629 | 0.23247 | -0.0067206 | -0.0064301 | 0.003702 | 0.060105 | -0.0043685 | 0.068906 | -60.9879 | 62.0316 | -61.1664 | -61.0748 | 61.8484 | 0.050354 | -0.18768 | 0.16022 | 62.0087 | -61.1526 | -0.27466 | 0.068664 | -0.09613 | -0.1831 | -0.11444 | -0.26092 | 0.045776 | 0.17853 | 60.704 | 61.0519 | 122.7402 | 122.9233 | -0.09613 | 122.9004 | 60.9421 | -0.26092 | 122.9233 | -0.09613 | 60.9421 | 122.7402 | 122.9004 | -123.1293 | -123.1155
1423.7969 | 123.2162 | -60.878 | 61.9904 | -0.14137 | -0.0073614 | -0.010703 | 0.0017794 | 0.060532 | -0.0058639 | 0.06912 | -60.9879 | 62.0407 | -61.1298 | -60.9421 | 62.2055 | 0.39825 | -0.26093 | 0.26093 | 62.0819 | -61.1206 | -0.25177 | 0.050354 | -0.10986 | -0.064087 | 0.21515 | -0.24261 | 0.091553 | 0.14191 | 60.6171 | 61.1389 | 123.0835 | 122.9187 | -0.10986 | 122.9599 | 61.2762 | -0.24261 | 122.9187 | -0.10986 | 61.2762 | 123.0835 | 122.9599 | -123.1201 | -123.111
1424.7812 | 123.143 | -60.8734 | 62.0224 | 0.15617 | -0.0084296 | -0.0098479 | 0.00049764 | 0.059037 | -0.0045821 | 0.069547 | -61.0657 | 62.027 | -61.1664 | -61.1389 | 61.8164 | 0.022888 | -0.09613 | 0.14648 | 62.0407 | -61.1572 | -0.29297 | 0.004578 | -0.19226 | -0.2655 | -0.20599 | -0.28381 | 0.01831 | 0.10071 | 60.7773 | 61.0199 | 122.6898 | 122.9004 | -0.19226 | 122.9141 | 60.8963 | -0.28381 | 122.9004 | -0.19226 | 60.8963 | 122.6898 | 122.9141 | -123.1888 | -123.1796
1425.7812 | 123.1659 | -60.8826 | 62.0041 | 0.19432 | -0.0067206 | -0.0092071 | 0.0034884 | 0.061173 | -0.0052231 | 0.067197 | -61.0336 | 62.0132 | -61.1801 | -61.116 | 61.8118 | 0.013733 | -0.10986 | 0.12817 | 62.0407 | -61.1252 | -0.29755 | 0.009156 | -0.15106 | -0.23346 | -0.19226 | -0.24262 | 0.036621 | 0.14648 | 60.7727 | 61.0107 | 122.6944 | 122.8958 | -0.15106 | 122.9233 | 60.8963 | -0.24262 | 122.8958 | -0.15106 | 60.8963 | 122.6944 | 122.9233 | -123.1842 | -123.1293
1426.7812 | 123.1842 | -60.8688 | 62.0041 | 0.12566 | -0.0062934 | -0.0081389 | 0.0015658 | 0.059251 | -0.0030869 | 0.06677 | -61.0336 | 62.0453 | -61.171 | -61.0931 | 61.8301 | 0.073242 | -0.073242 | 0.18768 | 62.0178 | -61.1481 | -0.30212 | 0.041199 | -0.1648 | -0.22431 | -0.17395 | -0.27924 | 0.013733 | 0.13733 | 60.7956 | 61.0565 | 122.699 | 122.9141 | -0.1648 | 122.8867 | 60.9421 | -0.27924 | 122.9141 | -0.1648 | 60.9421 | 122.699 | 122.8867 | -123.175 | -123.1522
1427.7812 | 123.1796 | -60.8871 | 62.0453 | 0.69023 | -0.008216 | -0.010916 | 0.00071144 | 0.06096 | -0.0039413 | 0.067624 | -61.0291 | 62.0499 | -61.1572 | -61.1298 | 61.8301 | 0.059509 | -0.086975 | 0.16479 | 62.0361 | -61.1206 | -0.27008 | 0.004578 | -0.14191 | -0.24262 | -0.21515 | -0.23346 | -0.009155 | 0.12817 | 60.8002 | 61.0519 | 122.7173 | 122.937 | -0.14191 | 122.9233 | 60.9467 | -0.23346 | 122.937 | -0.14191 | 60.9467 | 122.7173 | 122.9233 | -123.2025 | -123.1659
1428.7969 | 123.0927 | -60.91 | 62.0728 | -0.19478 | -0.0067206 | -0.0079253 | 0.004343 | 0.058823 | -0.0058639 | 0.068693 | -61.0016 | 62.0819 | -61.1572 | -61.1114 | 61.8118 | 0.068665 | 0.091553 | 0.21515 | 62.0911 | -61.1435 | -0.24719 | 0.009155 | -0.091553 | -0.20142 | -0.26093 | -0.23346 | 0.01831 | 0.15564 | 61.0016 | 61.1252 | 122.7219 | 122.9919 | -0.091553 | 123.0011 | 60.9787 | -0.23346 | 122.9919 | -0.091553 | 60.9787 | 122.7219 | 123.0011 | -123.23 | -123.2162
1429.7812 | 123.2254 | -60.8368 | 62.0316 | -0.019302 | -0.0069342 | -0.011984 | 0.00071144 | 0.060105 | -0.0052231 | 0.066556 | -60.9833 | 62.0224 | -61.1389 | -61.0336 | 61.8896 | 0.12817 | -0.07782 | 0.28381 | 62.0224 | -61.084 | -0.30212 | -0.009155 | -0.14648 | -0.19684 | -0.14191 | -0.24719 | -0.009155 | 0.15564 | 60.759 | 61.1206 | 122.7264 | 122.8592 | -0.14648 | 122.8592 | 60.965 | -0.24719 | 122.8592 | -0.14648 | 60.965 | 122.7264 | 122.8592 | -123.1705 | -123.1155
1430.7812 | 123.2071 | -60.8643 | 62.027 | -0.057449 | -0.0090704 | -0.0098479 | 0.001993 | 0.059464 | -0.0037277 | 0.066343 | -60.997 | 62.0407 | -61.1526 | -61.0565 | 61.8896 | 0.11902 | -0.082397 | 0.23804 | 61.9995 | -61.1206 | -0.28839 | 0.013732 | -0.13275 | -0.19226 | -0.13733 | -0.25635 | -0.027466 | 0.15564 | 60.7819 | 61.1023 | 122.7539 | 122.905 | -0.13275 | 122.8638 | 60.9833 | -0.25635 | 122.905 | -0.13275 | 60.9833 | 122.7539 | 122.8638 | -123.1796 | -123.1476
1431.7812 | 123.2208 | -60.8459 | 62.027 | -0.19478 | -0.005866 | -0.0072845 | 0.0034884 | 0.058182 | -0.0043685 | 0.066984 | -60.9604 | 62.0361 | -61.1343 | -61.0428 | 61.8942 | 0.13275 | -0.036621 | 0.27924 | 62.0407 | -61.1298 | -0.28839 | 0.009155 | -0.11444 | -0.19684 | -0.13275 | -0.28381 | 0.013732 | 0.17395 | 60.8093 | 61.1252 | 122.7402 | 122.8821 | -0.11444 | 122.8867 | 60.9787 | -0.28381 | 122.8821 | -0.11444 | 60.9787 | 122.7402 | 122.8867 | -123.1613 | -123.1567
1432.7812 | 123.1293 | -60.9009 | 62.027 | 0.056992 | -0.005866 | -0.0079253 | -0.0016386 | 0.06096 | -0.0035141 | 0.066343 | -61.0474 | 62.0361 | -61.171 | -61.1069 | 61.8347 | 0.009155 | -0.054932 | 0.16937 | 62.027 | -61.1481 | -0.27008 | 0.009155 | -0.14648 | -0.20599 | -0.19226 | -0.24719 | 0 | 0.1236 | 60.8459 | 61.0703 | 122.7356 | 122.937 | -0.14648 | 122.9279 | 60.91 | -0.24719 | 122.937 | -0.14648 | 60.91 | 122.7356 | 122.9279 | -123.1979 | -123.175
1433.7969 | 123.1293 | -60.8871 | 62.0499 | -0.21767 | -0.0052252 | -0.010916 | 0.0039156 | 0.061387 | -0.0033005 | 0.065916 | -60.9879 | 62.1048 | -61.1572 | -61.0794 | 61.8439 | 0.10071 | 0.07782 | 0.20142 | 62.0773 | -61.1435 | -0.27008 | 0.054931 | -0.10071 | -0.19226 | -0.20599 | -0.25635 | 0.027466 | 0.16937 | 60.965 | 61.0886 | 122.731 | 122.9919 | -0.10071 | 122.9645 | 60.9879 | -0.25635 | 122.9919 | -0.10071 | 60.9879 | 122.731 | 122.9645 | -123.2071 | -123.1934
1434.7812 | 123.1659 | -60.8459 | 62.0224 | -0.087967 | -0.008216 | -0.0068573 | 0.0030612 | 0.060532 | -0.0041549 | 0.068906 | -60.9741 | 62.027 | -61.1572 | -61.0382 | 61.9125 | 0.13733 | 0.068665 | 0.64545 | 62.0911 | -61.0794 | -0.31128 | 0.004578 | -0.12817 | -0.19226 | -0.10986 | -0.23346 | 0.068664 | 0.18311 | 60.9146 | 61.4914 | 122.7585 | 122.8729 | -0.12817 | 122.937 | 60.9833 | -0.23346 | 122.8729 | -0.12817 | 60.9833 | 122.7585 | 122.937 | -123.1796 | -123.1018
1435.7812 | 123.2208 | -60.878 | 62.0453 | -0.13374 | -0.008216 | -0.0092071 | 0.0030612 | 0.056687 | -0.0045821 | 0.068693 | -60.9558 | 62.0224 | -61.1481 | -61.0291 | 61.908 | 0.14648 | -0.059509 | 0.27924 | 62.0453 | -61.1206 | -0.27008 | -0.022888 | -0.07782 | -0.15106 | -0.13733 | -0.24261 | 0 | 0.19226 | 60.8185 | 61.1572 | 122.7859 | 122.9004 | -0.07782 | 122.9233 | 61.0245 | -0.24261 | 122.9004 | -0.07782 | 61.0245 | 122.7859 | 122.9233 | -123.1934 | -123.1659
1436.7812 | 123.2391 | -60.8368 | 62.027 | -0.095596 | -0.0050116 | -0.0092071 | 0.0024202 | 0.05861 | -0.0058639 | 0.068265 | -60.9695 | 62.0407 | -61.1572 | -61.0062 | 61.9217 | 0.16022 | -0.068665 | 0.29297 | 62.0361 | -61.1298 | -0.32043 | 0.013732 | -0.13275 | -0.16937 | -0.10529 | -0.29297 | 0.009155 | 0.18768 | 60.7681 | 61.1298 | 122.7585 | 122.8775 | -0.13275 | 122.8729 | 60.997 | -0.29297 | 122.8775 | -0.13275 | 60.997 | 122.7585 | 122.8729 | -123.1842 | -123.1567
1437.7812 | 123.2071 | -60.8505 | 62.0453 | -0.10323 | -0.0073614 | -0.0089935 | 0.00092504 | 0.059678 | -0.0033005 | 0.06677 | -60.9741 | 62.0499 | -61.1114 | -61.0474 | 61.853 | 0.091553 | -0.045776 | 0.23804 | 62.0132 | -61.1298 | -0.26093 | 0.004578 | -0.1236 | -0.19684 | -0.19226 | -0.27924 | -0.032043 | 0.13733 | 60.8047 | 61.0886 | 122.7036 | 122.9004 | -0.1236 | 122.8638 | 60.9421 | -0.27924 | 122.9004 | -0.1236 | 60.9421 | 122.7036 | 122.8638 | -123.1567 | -123.175
1438.7969 | 123.0972 | -60.8826 | 62.0132 | 0.1104 | -0.0035162 | -0.0060027 | 0.010111 | 0.062669 | -0.0039413 | 0.06677 | -61.0199 | 62.1414 | -61.1572 | -61.1389 | 61.7661 | -0.041199 | -0.004578 | 0.045776 | 62.0407 | -61.1984 | -0.27466 | 0.12817 | -0.13733 | -0.25635 | -0.24719 | -0.31586 | 0.027465 | 0.13733 | 60.878 | 60.9283 | 122.6486 | 123.024 | -0.13733 | 122.9233 | 60.8414 | -0.31586 | 123.024 | -0.13733 | 60.8414 | 122.6486 | 122.9233 | -123.1705 | -123.2117
1439.7812 | 123.1155 | -60.8734 | 62.059 | -0.21004 | -0.0069342 | -0.0089935 | 0.0024202 | 0.06395 | -0.0047957 | 0.068906 | -61.0107 | 62.0773 | -61.1664 | -61.116 | 61.8439 | 0.059509 | 0.091553 | 0.1831 | 62.0956 | -61.116 | -0.29297 | 0.018311 | -0.13733 | -0.24262 | -0.21515 | -0.24262 | 0.036621 | 0.15564 | 60.965 | 61.0565 | 122.7173 | 122.9507 | -0.13733 | 122.9691 | 60.9329 | -0.24262 | 122.9507 | -0.13733 | 60.9329 | 122.7173 | 122.9691 | -123.2254 | -123.175
1440.7812 | 123.0835 | -60.9146 | 62.0728 | -0.11848 | -0.0077888 | -0.0064301 | 0.0011386 | 0.061814 | -0.0035141 | 0.068052 | -61.0519 | 62.1277 | -61.1847 | -61.1298 | 61.8256 | 0.041199 | 0.16937 | 0.17395 | 62.1048 | -61.1664 | -0.27008 | 0.054932 | -0.13733 | -0.21515 | -0.24719 | -0.25177 | 0.032043 | 0.13275 | 61.084 | 61.0886 | 122.7402 | 123.0423 | -0.13733 | 123.0194 | 60.9558 | -0.25177 | 123.0423 | -0.13733 | 60.9558 | 122.7402 | 123.0194 | -123.2574 | -123.2391
1441.7812 | 123.1796 | -60.878 | 62.0087 | 0.026474 | -0.0069342 | -0.011771 | -0.001425 | 0.061173 | -0.0043685 | 0.06677 | -61.0428 | 62.027 | -61.1526 | -61.0931 | 61.8668 | 0.086975 | -0.059509 | 0.21973 | 62.0087 | -61.1389 | -0.27466 | 0.018311 | -0.16479 | -0.21515 | -0.14191 | -0.26093 | 0 | 0.10986 | 60.8185 | 61.0977 | 122.7448 | 122.905 | -0.16479 | 122.8867 | 60.965 | -0.26093 | 122.905 | -0.16479 | 60.965 | 122.7448 | 122.8867 | -123.1613 | -123.1476
1442.7812 | 123.2254 | -60.8551 | 62.0132 | -0.072708 | -0.0069342 | -0.010703 | -0.00078396 | 0.057114 | -0.0024459 | 0.06912 | -61.0062 | 62.0544 | -61.1252 | -61.0519 | 61.8988 | 0.13275 | -0.073242 | 0.27008 | 62.0316 | -61.1389 | -0.27008 | 0.041198 | -0.15106 | -0.19684 | -0.11444 | -0.28381 | 0.01831 | 0.11902 | 60.7819 | 61.1252 | 122.7539 | 122.9095 | -0.15106 | 122.8867 | 60.9879 | -0.28381 | 122.9095 | -0.15106 | 60.9879 | 122.7539 | 122.8867 | -123.1384 | -123.1522
1443.7969 | 123.1293 | -60.8871 | 62.0087 | -0.095596 | -0.0033026 | -0.0045075 | 0.0064792 | 0.063523 | -0.0069321 | 0.067197 | -60.9604 | 62.0956 | -61.1755 | -61.084 | 61.8256 | 0.045776 | 0.018311 | 0.13733 | 62.0865 | -61.1298 | -0.28839 | 0.086975 | -0.073242 | -0.19684 | -0.18311 | -0.24262 | 0.07782 | 0.21515 | 60.9055 | 61.0245 | 122.7127 | 122.9828 | -0.073242 | 122.9736 | 60.9329 | -0.24262 | 122.9828 | -0.073242 | 60.9329 | 122.7127 | 122.9736 | -123.1842 | -123.1384
1444.7812 | 123.2391 | -60.8551 | 62.0224 | -0.18715 | -0.0069342 | -0.0070709 | 7.0444e-05 | 0.062455 | -0.0043685 | 0.067838 | -60.9604 | 62.0636 | -61.1435 | -61.0336 | 61.94 | 0.17395 | -0.086975 | 0.28839 | 62.0636 | -61.1069 | -0.28839 | 0.041199 | -0.10529 | -0.17853 | -0.082398 | -0.25177 | 0.041199 | 0.18311 | 60.7681 | 61.1435 | 122.7951 | 122.9187 | -0.10529 | 122.9187 | 61.0291 | -0.25177 | 122.9187 | -0.10529 | 61.0291 | 122.7951 | 122.9187 | -123.1659 | -123.1293
1445.7812 | 123.2254 | -60.8551 | 62.0087 | -0.13374 | -0.0062934 | -0.0064301 | 0.00028404 | 0.06395 | -0.0050095 | 0.07147 | -60.9695 | 62.0544 | -61.1298 | -61.0748 | 61.8805 | 0.16022 | -0.10071 | 0.27008 | 62.0499 | -61.1298 | -0.27466 | 0.045776 | -0.11444 | -0.21973 | -0.12817 | -0.27466 | 0.041199 | 0.16022 | 60.7544 | 61.1252 | 122.7356 | 122.9095 | -0.11444 | 122.905 | 61.0153 | -0.27466 | 122.9095 | -0.11444 | 61.0153 | 122.7356 | 122.905 | -123.1384 | -123.1384
1446.7969 | 123.1155 | -60.91 | 62.0178 | -0.0040434 | -0.0052252 | -0.0083527 | 0.0079744 | 0.063523 | -0.0058639 | 0.067624 | -60.9604 | 62.1414 | -61.1389 | -61.084 | 61.8393 | 0.059509 | 0.027466 | 0.16479 | 62.059 | -61.1984 | -0.22888 | 0.1236 | -0.050354 | -0.17395 | -0.17853 | -0.28839 | 0.041199 | 0.17853 | 60.9375 | 61.0748 | 122.7493 | 123.0515 | -0.050354 | 122.9691 | 60.9695 | -0.28839 | 123.0515 | -0.050354 | 60.9695 | 122.7493 | 122.9691 | -123.1567 | -123.2162
1447.7812 | 123.1384 | -60.8917 | 62.0407 | -0.065079 | -0.0041572 | -0.0053619 | 0.0064792 | 0.063523 | -0.0035141 | 0.065702 | -60.9604 | 62.1735 | -61.1801 | -61.0748 | 61.8393 | 0.073242 | 0.054932 | 0.18768 | 62.0728 | -61.1938 | -0.28839 | 0.13275 | -0.068664 | -0.1831 | -0.20142 | -0.30212 | 0.032044 | 0.21973 | 60.9467 | 61.0794 | 122.731 | 123.0652 | -0.068664 | 122.9645 | 60.965 | -0.30212 | 123.0652 | -0.068664 | 60.965 | 122.731 | 122.9645 | -123.2208 | -123.2346
1448.9219 | 123.2117 | -60.8643 | 62.0178 | -0.087967 | -0.008216 | -0.0087799 | -0.001425 | 0.061814 | -0.0045821 | 0.067838 | -60.965 | 62.0453 | -61.171 | -61.0291 | 61.9446 | 0.17395 | -0.045776 | 0.27466 | 62.0636 | -61.1252 | -0.3067 | 0.027466 | -0.10071 | -0.16479 | -0.073242 | -0.26093 | 0.045777 | 0.20599 | 60.8185 | 61.1389 | 122.8088 | 122.9095 | -0.10071 | 122.9279 | 61.0382 | -0.26093 | 122.9095 | -0.10071 | 61.0382 | 122.8088 | 122.9279 | -123.1888 | -123.143
1449.7969 | 123.143 | -60.9009 | 62.027 | -0.13374 | -0.0043708 | -0.0051483 | 0.0066928 | 0.063309 | -0.0052231 | 0.06912 | -60.965 | 62.1414 | -61.1618 | -61.0931 | 61.8347 | 0.086975 | 0.041199 | 0.1831 | 62.1094 | -61.1847 | -0.26092 | 0.11444 | -0.064087 | -0.19226 | -0.19226 | -0.28381 | 0.082397 | 0.19684 | 60.9421 | 61.084 | 122.7356 | 123.0423 | -0.064087 | 123.0103 | 60.9879 | -0.28381 | 123.0423 | -0.064087 | 60.9879 | 122.7356 | 123.0103 | -123.1888 | -123.2117
1450.7812 | 123.1247 | -60.9192 | 62.027 | 0.011215 | -0.0043708 | -0.0066437 | 0.0049838 | 0.064591 | -0.0047957 | 0.067411 | -60.9741 | 62.1597 | -61.171 | -61.0886 | 61.8301 | 0.064087 | 0.018311 | 0.16937 | 62.0956 | -61.1618 | -0.25177 | 0.13275 | -0.054932 | -0.16937 | -0.19684 | -0.24261 | 0.068664 | 0.19684 | 60.9375 | 61.0886 | 122.7493 | 123.0789 | -0.054932 | 123.0148 | 60.9833 | -0.24261 | 123.0789 | -0.054932 | 60.9833 | 122.7493 | 123.0148 | -123.1979 | -123.1888
1451.7812 | 123.1338 | -60.9192 | 62.0499 | -0.011673 | -0.0015936 | -0.0047211 | 0.0060518 | 0.065446 | -0.0050095 | 0.068906 | -60.9879 | 62.146 | -61.1526 | -61.0977 | 61.8439 | 0.068665 | 0.032043 | 0.18768 | 62.0956 | -61.1526 | -0.23346 | 0.09613 | -0.068665 | -0.17853 | -0.20599 | -0.23346 | 0.045776 | 0.16479 | 60.9512 | 61.1069 | 122.7631 | 123.0652 | -0.068665 | 123.0148 | 60.9879 | -0.23346 | 123.0652 | -0.068665 | 60.9879 | 122.7631 | 123.0148 | -123.2025 | -123.2025
1452.7812 | 123.1338 | -60.8963 | 62.059 | -0.087967 | -0.0035162 | -0.0023711 | 0.0013522 | 0.062882 | -0.0037277 | 0.066343 | -60.9787 | 62.1689 | -61.1618 | -61.1023 | 61.853 | 0.07782 | 0.050354 | 0.16479 | 62.1048 | -61.1847 | -0.2655 | 0.10986 | -0.082398 | -0.20599 | -0.20599 | -0.28839 | 0.045776 | 0.1831 | 60.9467 | 61.0611 | 122.7493 | 123.0652 | -0.082398 | 123.0011 | 60.9741 | -0.28839 | 123.0652 | -0.082398 | 60.9741 | 122.7493 | 123.0011 | -123.2208 | -123.2437
1453.7969 | 123.143 | -60.9009 | 61.9766 | 0.24773 | -0.005866 | -0.0030121 | 0.0041292 | 0.065873 | -0.0033005 | 0.068693 | -61.0336 | 62.1368 | -61.1664 | -61.1481 | 61.7889 | -0.018311 | -0.091553 | 0.059509 | 62.0682 | -61.2076 | -0.2655 | 0.16022 | -0.13275 | -0.24719 | -0.18768 | -0.3067 | 0.091552 | 0.13275 | 60.8093 | 60.9604 | 122.6898 | 123.0377 | -0.13275 | 122.9691 | 60.8826 | -0.3067 | 123.0377 | -0.13275 | 60.8826 | 122.6898 | 122.9691 | -123.143 | -123.1842
1454.7812 | 123.0927 | -60.9467 | 62.0361 | 0.14854 | -0.0039434 | -0.0045075 | 0.0041292 | 0.064805 | -0.0033005 | 0.06912 | -61.0428 | 62.1597 | -61.1984 | -61.2122 | 61.7661 | -0.036621 | 0.041199 | 0.022888 | 62.0911 | -61.2122 | -0.25177 | 0.1236 | -0.096131 | -0.2655 | -0.27008 | -0.2655 | 0.054931 | 0.15564 | 60.9879 | 60.9695 | 122.7127 | 123.1064 | -0.096131 | 123.0377 | 60.91 | -0.2655 | 123.1064 | -0.096131 | 60.91 | 122.7127 | 123.0377 | -123.2346 | -123.2483
1455.7812 | 123.262 | -60.8551 | 61.9812 | -0.034561 | -0.0069342 | -0.011557 | -0.0033476 | 0.063523 | -0.0045821 | 0.068265 | -60.9924 | 62.0544 | -61.1618 | -61.0382 | 61.9308 | 0.17395 | -0.073242 | 0.28839 | 62.0361 | -61.0977 | -0.3067 | 0.073242 | -0.13733 | -0.1831 | -0.050354 | -0.24261 | 0.054932 | 0.16937 | 60.7819 | 61.1435 | 122.7859 | 122.9095 | -0.13733 | 122.8912 | 61.0291 | -0.24261 | 122.9095 | -0.13733 | 61.0291 | 122.7859 | 122.8912 | -123.143 | -123.0789
1456.7812 | 123.2117 | -60.878 | 62.0224 | 0.087509 | -0.0060798 | -0.0081389 | -0.0029202 | 0.0616 | -0.0026595 | 0.071042 | -61.0428 | 62.0453 | -61.1664 | -61.1206 | 61.8713 | 0.082397 | -0.054932 | 0.20599 | 62.0224 | -61.1435 | -0.28839 | 0.022888 | -0.16479 | -0.24261 | -0.15106 | -0.2655 | 0 | 0.1236 | 60.8231 | 61.084 | 122.7493 | 122.9233 | -0.16479 | 122.9004 | 60.9604 | -0.2655 | 122.9233 | -0.16479 | 60.9604 | 122.7493 | 122.9004 | -123.1888 | -123.1659
1457.7812 | 123.0743 | -60.9192 | 62.0316 | 0.07988 | -0.0039434 | -0.0055755 | 0.0081882 | 0.064591 | -0.0033005 | 0.067197 | -61.0016 | 62.1735 | -61.1664 | -61.1526 | 61.7706 | -0.022888 | 0.018311 | 0.091553 | 62.0544 | -61.2122 | -0.24719 | 0.14191 | -0.082398 | -0.23346 | -0.26093 | -0.29297 | 0.022888 | 0.16479 | 60.9375 | 61.0107 | 122.6898 | 123.0927 | -0.082398 | 122.9736 | 60.8963 | -0.29297 | 123.0927 | -0.082398 | 60.8963 | 122.6898 | 122.9736 | -123.1979 | -123.2437
1458.7812 | 123.0606 | -60.8734 | 62.0728 | -0.23293 | -0.0039434 | -0.010275 | 0.001993 | 0.063737 | -0.0037277 | 0.068052 | -61.0291 | 62.1689 | -61.1847 | -61.1526 | 61.8027 | 0.050354 | 0.14648 | 0.36621 | 62.1323 | -61.1801 | -0.31128 | 0.09613 | -0.15564 | -0.27924 | -0.27008 | -0.3067 | 0.059509 | 0.15564 | 61.0199 | 61.2396 | 122.6761 | 123.0423 | -0.15564 | 123.0057 | 60.9238 | -0.3067 | 123.0423 | -0.15564 | 60.9238 | 122.6761 | 123.0057 | -123.2574 | -123.2529
1459.7812 | 123.2346 | -60.8505 | 62.0178 | -0.065079 | -0.0071478 | -0.0036529 | -0.0022794 | 0.0616 | -0.0037277 | 0.068906 | -60.965 | 62.0636 | -61.1206 | -61.0291 | 61.9263 | 0.14648 | -0.045776 | 0.29755 | 62.0819 | -61.1252 | -0.27008 | 0.045777 | -0.11444 | -0.17853 | -0.091552 | -0.27466 | 0.064087 | 0.15564 | 60.8047 | 61.1481 | 122.7768 | 122.9141 | -0.11444 | 122.9324 | 60.997 | -0.27466 | 122.9141 | -0.11444 | 60.997 | 122.7768 | 122.9324 | -123.1384 | -123.143
1460.7812 | 123.1934 | -60.8826 | 61.9949 | 0.17143 | -0.0056524 | -0.0062163 | 0.00092504 | 0.06096 | -0.0043685 | 0.070402 | -60.9787 | 62.0636 | -61.1938 | -61.1252 | 61.8393 | 0.027466 | -0.15106 | 0.16022 | 62.0178 | -61.1343 | -0.31128 | 0.068665 | -0.096131 | -0.24262 | -0.15564 | -0.25177 | 0.022888 | 0.21515 | 60.7315 | 61.0428 | 122.7219 | 122.9462 | -0.096131 | 122.9004 | 60.91 | -0.25177 | 122.9462 | -0.096131 | 60.91 | 122.7219 | 122.9004 | -123.1888 | -123.1293
1461.7812 | 123.143 | -60.8917 | 62.0224 | 0.18669 | -0.004798 | -0.0036529 | 0.0017794 | 0.0616 | -0.0062911 | 0.068906 | -61.0199 | 62.0178 | -61.171 | -61.1435 | 61.8118 | 0.018311 | -0.09613 | 0.15564 | 62.0407 | -61.1618 | -0.27923 | -0.004578 | -0.12817 | -0.25177 | -0.21057 | -0.27008 | 0.01831 | 0.15106 | 60.7956 | 61.0474 | 122.7036 | 122.9095 | -0.12817 | 122.9324 | 60.91 | -0.27008 | 122.9095 | -0.12817 | 60.91 | 122.7036 | 122.9324 | -123.1934 | -123.1842
1462.7812 | 123.1613 | -60.9055 | 62.0132 | 0.1104 | -0.0067206 | -0.010275 | 7.0444e-05 | 0.061387 | -0.0041549 | 0.06677 | -61.0336 | 62.0682 | -61.171 | -61.1298 | 61.821 | 0.041199 | -0.054932 | 0.15564 | 62.0224 | -61.171 | -0.2655 | 0.054931 | -0.12817 | -0.2243 | -0.19226 | -0.2655 | 0.009155 | 0.13733 | 60.8505 | 61.0611 | 122.7264 | 122.9736 | -0.12817 | 122.9279 | 60.9467 | -0.2655 | 122.9736 | -0.12817 | 60.9467 | 122.7264 | 122.9279 | -123.1842 | -123.1842
1463.7812 | 123.1796 | -60.8505 | 62.059 | -0.10323 | -0.0050116 | -0.0062163 | 0.0022066 | 0.061173 | -0.0062911 | 0.067624 | -60.9695 | 62.059 | -61.1389 | -61.0703 | 61.8896 | 0.12817 | 0.022888 | 0.27466 | 62.0819 | -61.1343 | -0.28839 | 0 | -0.11902 | -0.21973 | -0.16937 | -0.28381 | 0.022888 | 0.16937 | 60.8734 | 61.1252 | 122.7402 | 122.9095 | -0.11902 | 122.9324 | 60.9787 | -0.28381 | 122.9095 | -0.11902 | 60.9787 | 122.7402 | 122.9324 | -123.1979 | -123.1934
1464.7812 | 123.2208 | -60.8871 | 61.9904 | 0.14092 | -0.0043708 | -0.0081389 | 0.008829 | 0.062241 | -0.0043685 | 0.06912 | -61.0245 | 62.0544 | -61.1664 | -61.0931 | 61.8347 | 0.032043 | -0.1831 | 0.15106 | 62.027 | -61.1618 | -0.27924 | 0.064087 | -0.13733 | -0.20599 | -0.15564 | -0.27466 | 0.036622 | 0.14191 | 60.704 | 61.0382 | 122.7219 | 122.9416 | -0.13733 | 122.9141 | 60.9192 | -0.27466 | 122.9416 | -0.13733 | 60.9192 | 122.7219 | 122.9141 | -123.1567 | -123.1522
1465.7812 | 123.1659 | -60.8963 | 62.0316 | 0.22484 | -0.0062934 | -0.0094207 | -0.00057036 | 0.060105 | -0.0039413 | 0.067838 | -61.0565 | 62.0316 | -61.1847 | -61.1389 | 61.8256 | 0.041199 | -0.091553 | 0.13275 | 62.0316 | -61.1618 | -0.28839 | 0 | -0.16022 | -0.24262 | -0.20599 | -0.2655 | 0 | 0.12817 | 60.8047 | 61.0291 | 122.7219 | 122.9279 | -0.16022 | 122.9279 | 60.9375 | -0.2655 | 122.9279 | -0.16022 | 60.9375 | 122.7219 | 122.9279 | -123.2162 | -123.1934
1466.7812 | 123.2162 | -60.8826 | 61.9949 | -0.019302 | -0.007575 | -0.0087799 | 0.00028404 | 0.058396 | -0.0050095 | 0.068693 | -61.0016 | 62.0499 | -61.1664 | -61.0886 | 61.8622 | 0.091553 | -0.068665 | 0.23346 | 62.0453 | -61.1618 | -0.28381 | 0.054932 | -0.11902 | -0.20599 | -0.13275 | -0.27924 | 0.050354 | 0.16479 | 60.8139 | 61.116 | 122.7448 | 122.9324 | -0.11902 | 122.9279 | 60.9741 | -0.27924 | 122.9324 | -0.11902 | 60.9741 | 122.7448 | 122.9279 | -123.1613 | -123.1567
1467.7812 | 123.2025 | -60.8688 | 62.0041 | 0.018845 | -0.0071478 | -0.011771 | 0.0015658 | 0.058396 | -0.0045821 | 0.066129 | -61.0382 | 62.0453 | -61.1435 | -61.1023 | 61.8668 | 0.091553 | -0.064087 | 0.21973 | 62.0224 | -61.1389 | -0.27466 | 0.041199 | -0.16937 | -0.23346 | -0.13733 | -0.27008 | 0.018311 | 0.10529 | 60.8047 | 61.0886 | 122.7356 | 122.9141 | -0.16937 | 122.8912 | 60.9604 | -0.27008 | 122.9141 | -0.16937 | 60.9604 | 122.7356 | 122.8912 | -123.1476 | -123.143
1468.7812 | 123.1338 | -60.8917 | 62.0636 | -0.087967 | -0.0056524 | -0.0072845 | 0.0075472 | 0.059464 | -0.0035141 | 0.068693 | -60.9879 | 62.1552 | -61.1526 | -61.0977 | 61.8301 | 0.064087 | 0.073242 | 0.18768 | 62.0728 | -61.2076 | -0.26092 | 0.091552 | -0.09613 | -0.20599 | -0.23346 | -0.31586 | 0.009155 | 0.16479 | 60.965 | 61.0794 | 122.7219 | 123.0469 | -0.09613 | 122.9645 | 60.9558 | -0.31586 | 123.0469 | -0.09613 | 60.9558 | 122.7219 | 122.9645 | -123.2162 | -123.2712
1469.7812 | 123.1934 | -60.8826 | 61.9949 | 0.19432 | -0.005866 | -0.0083527 | 0.0015658 | 0.060746 | -0.0045821 | 0.067838 | -61.0199 | 62.0132 | -61.1801 | -61.1298 | 61.821 | 0 | -0.12817 | 0.13733 | 62.027 | -61.1435 | -0.29755 | 0.018311 | -0.13733 | -0.24719 | -0.17395 | -0.26093 | 0.032044 | 0.16022 | 60.7544 | 61.0199 | 122.7036 | 122.8958 | -0.13733 | 122.9095 | 60.8826 | -0.26093 | 122.8958 | -0.13733 | 60.8826 | 122.7036 | 122.9095 | -123.175 | -123.1384
1470.7812 | 123.1659 | -60.8734 | 62.0224 | 0.13329 | -0.0062934 | -0.011343 | 0.0011386 | 0.059464 | -0.0020187 | 0.067197 | -61.0519 | 62.0361 | -61.1755 | -61.1343 | 61.821 | 0.022888 | -0.082397 | 0.13275 | 62.0453 | -61.1526 | -0.30212 | 0.013733 | -0.17853 | -0.26093 | -0.20142 | -0.27924 | 0.022888 | 0.1236 | 60.791 | 61.0062 | 122.6944 | 122.9095 | -0.17853 | 122.9187 | 60.8963 | -0.27924 | 122.9095 | -0.17853 | 60.8963 | 122.6944 | 122.9187 | -123.1979 | -123.175
1471.7812 | 123.1247 | -60.91 | 62.0132 | 0.23247 | -0.0026618 | -0.0062163 | 0.0041292 | 0.062241 | -0.0028731 | 0.069761 | -61.0291 | 62.1048 | -61.1938 | -61.171 | 61.7615 | -0.059509 | -0.073242 | 0.050354 | 62.0773 | -61.1938 | -0.28381 | 0.091552 | -0.11902 | -0.26093 | -0.25177 | -0.28381 | 0.064087 | 0.1648 | 60.8368 | 60.9604 | 122.6715 | 123.0148 | -0.11902 | 122.9874 | 60.8505 | -0.28381 | 123.0148 | -0.11902 | 60.8505 | 122.6715 | 122.9874 | -123.2071 | -123.2071
1472.7812 | 123.1705 | -60.8963 | 61.9949 | 0.064621 | -0.006507 | -0.0077117 | -0.00078396 | 0.06096 | -0.0062911 | 0.069761 | -61.0519 | 62.0544 | -61.1664 | -61.0931 | 61.7935 | 0.059509 | -0.10986 | 0.15564 | 62.0499 | -61.1481 | -0.27008 | 0.059509 | -0.15564 | -0.19684 | -0.20142 | -0.25177 | 0.054932 | 0.11444 | 60.7864 | 61.0519 | 122.6898 | 122.9507 | -0.15564 | 122.9462 | 60.9558 | -0.25177 | 122.9507 | -0.15564 | 60.9558 | 122.6898 | 122.9462 | -123.1613 | -123.143
1473.7812 | 123.0972 | -60.8917 | 62.0316 | -0.27107 | -0.0060798 | -0.0068573 | 0.005411 | 0.061387 | -0.0050095 | 0.066343 | -61.0245 | 62.1277 | -61.1526 | -61.1252 | 61.8164 | 0.045776 | 0.13733 | 0.17853 | 62.1002 | -61.1801 | -0.26092 | 0.096131 | -0.13275 | -0.23346 | -0.21515 | -0.28839 | 0.068665 | 0.12817 | 61.0291 | 61.0703 | 122.7081 | 123.0194 | -0.13275 | 122.9919 | 60.9375 | -0.28839 | 123.0194 | -0.13275 | 60.9375 | 122.7081 | 122.9919 | -123.1842 | -123.2117
1474.7812 | 123.23 | -60.8688 | 62.0178 | -0.0040434 | -0.0071478 | -0.0072845 | 0.00049764 | 0.062028 | -0.0039413 | 0.066556 | -61.0016 | 62.0132 | -61.1481 | -61.0428 | 61.8988 | 0.11902 | -0.091553 | 0.25177 | 62.0453 | -61.1206 | -0.27924 | -0.004577 | -0.13275 | -0.17395 | -0.11902 | -0.25177 | 0.027466 | 0.14648 | 60.7773 | 61.1206 | 122.7676 | 122.8821 | -0.13275 | 122.9141 | 60.9879 | -0.25177 | 122.8821 | -0.13275 | 60.9879 | 122.7676 | 122.9141 | -123.1659 | -123.1384
1475.7812 | 123.2483 | -60.8505 | 62.0407 | -0.11848 | -0.0080024 | -0.0066437 | 0.00049764 | 0.058182 | -0.0037277 | 0.067838 | -60.9467 | 62.0453 | -61.1389 | -61.0382 | 61.9034 | 0.15564 | -0.045776 | 0.27924 | 62.0407 | -61.1389 | -0.28839 | 0.004578 | -0.09613 | -0.18768 | -0.13733 | -0.28839 | 0 | 0.19226 | 60.8047 | 61.1298 | 122.7539 | 122.8958 | -0.09613 | 122.8912 | 61.0062 | -0.28839 | 122.8958 | -0.09613 | 61.0062 | 122.7539 | 122.8912 | -123.1796 | -123.1796
1476.7812 | 123.2483 | -60.91 | 61.9812 | 0.28587 | -0.0039434 | -0.0064301 | 0.0058382 | 0.06096 | -0.0037277 | 0.066556 | -60.9787 | 62.0316 | -61.1618 | -61.0748 | 61.8484 | 0.032043 | -0.20142 | 0.15106 | 61.9766 | -61.1435 | -0.25177 | 0.050354 | -0.068665 | -0.16479 | -0.13275 | -0.23346 | -0.004577 | 0.1831 | 60.7086 | 61.0611 | 122.7585 | 122.9416 | -0.068665 | 122.8867 | 60.9421 | -0.23346 | 122.9416 | -0.068665 | 60.9421 | 122.7585 | 122.8867 | -123.143 | -123.1247
1477.7812 | 123.1796 | -60.8643 | 61.9995 | 0.17143 | -0.0071478 | -0.010062 | 0.0028476 | 0.059037 | -0.0058639 | 0.067411 | -60.997 | 62.0728 | -61.1755 | -61.0977 | 61.8484 | 0.027466 | -0.19226 | 0.13275 | 61.9858 | -61.1481 | -0.31128 | 0.073242 | -0.13275 | -0.23346 | -0.15106 | -0.28381 | -0.013733 | 0.17853 | 60.672 | 60.997 | 122.7127 | 122.937 | -0.13275 | 122.85 | 60.8917 | -0.28381 | 122.937 | -0.13275 | 60.8917 | 122.7127 | 122.85 | -123.175 | -123.1476
1478.7812 | 123.1705 | -60.8917 | 61.9995 | 0.072251 | -0.0037298 | -0.0070709 | -0.0022794 | 0.059678 | -0.0065047 | 0.066343 | -61.0565 | 62.0361 | -61.1984 | -61.1298 | 61.8301 | 0.013733 | -0.091553 | 0.13275 | 62.0132 | -61.1618 | -0.3067 | 0.036621 | -0.16479 | -0.23804 | -0.16937 | -0.27008 | 0.013733 | 0.14191 | 60.8002 | 61.0245 | 122.7219 | 122.9279 | -0.16479 | 122.905 | 60.9055 | -0.27008 | 122.9279 | -0.16479 | 60.9055 | 122.7219 | 122.905 | -123.1979 | -123.1613
1479.7812 | 123.1979 | -60.878 | 62.0132 | 0.24773 | -0.0071478 | -0.0034393 | 0.0047702 | 0.059464 | -0.0054367 | 0.06677 | -61.0062 | 62.0361 | -61.171 | -61.0931 | 61.8301 | 0.036621 | -0.16022 | 0.15106 | 62.0041 | -61.1526 | -0.29297 | 0.022888 | -0.12817 | -0.21515 | -0.18311 | -0.27466 | -0.009156 | 0.16479 | 60.7178 | 61.0291 | 122.7081 | 122.9141 | -0.12817 | 122.8821 | 60.9146 | -0.27466 | 122.9141 | -0.12817 | 60.9146 | 122.7081 | 122.8821 | -123.1842 | -123.1659
1480.7812 | 123.1567 | -60.8734 | 62.0132 | 0.14092 | -0.0060798 | -0.012625 | 0.0022066 | 0.061387 | -0.0058639 | 0.067624 | -61.0703 | 62.0636 | -61.1801 | -61.1252 | 61.8118 | 0.10071 | -0.064087 | 0.14191 | 62.0407 | -61.1481 | -0.3067 | 0.050354 | -0.19684 | -0.25177 | -0.20142 | -0.27466 | 0.027465 | 0.10986 | 60.8093 | 61.0153 | 122.6852 | 122.937 | -0.19684 | 122.9141 | 60.9741 | -0.27466 | 122.937 | -0.19684 | 60.9741 | 122.6852 | 122.9141 | -123.1934 | -123.1613
1481.7812 | 123.1796 | -60.8734 | 62.0087 | 0.087509 | -0.0054388 | -0.0092071 | 0.0011386 | 0.058823 | -0.0043685 | 0.068693 | -61.0428 | 62.0407 | -61.1801 | -61.1069 | 61.8393 | 0.059509 | -0.068665 | 0.1831 | 62.0087 | -61.171 | -0.3067 | 0.032043 | -0.16937 | -0.23346 | -0.16937 | -0.29755 | 0 | 0.13733 | 60.8047 | 61.0565 | 122.7127 | 122.9141 | -0.16937 | 122.8821 | 60.9329 | -0.29755 | 122.9141 | -0.16937 | 60.9329 | 122.7127 | 122.8821 | -123.1888 | -123.1796
1482.7812 | 123.1934 | -60.8826 | 62.0041 | 0.2401 | -0.0037298 | -0.0074981 | 0.0034884 | 0.059251 | -0.0020187 | 0.068906 | -61.0062 | 62.0224 | -61.171 | -61.0931 | 61.8347 | 0.027466 | -0.15106 | 0.15106 | 62.0087 | -61.1801 | -0.28839 | 0.018311 | -0.1236 | -0.21057 | -0.16937 | -0.29755 | 0.004578 | 0.16479 | 60.7315 | 61.0336 | 122.7173 | 122.905 | -0.1236 | 122.8912 | 60.91 | -0.29755 | 122.905 | -0.1236 | 60.91 | 122.7173 | 122.8912 | -123.175 | -123.1842
1483.7812 | 123.1384 | -60.8688 | 62.0499 | -0.17952 | -0.0069342 | -0.010916 | 0.0056246 | 0.059251 | -0.0062911 | 0.068265 | -60.9787 | 62.0956 | -61.1664 | -61.0565 | 61.8622 | 0.10529 | 0.045776 | 0.23804 | 62.0636 | -61.1435 | -0.29755 | 0.045776 | -0.10986 | -0.18768 | -0.18768 | -0.27466 | 0.013733 | 0.18768 | 60.9146 | 61.1069 | 122.731 | 122.9645 | -0.10986 | 122.9324 | 60.9741 | -0.27466 | 122.9645 | -0.10986 | 60.9741 | 122.731 | 122.9324 | -123.2162 | -123.1934
1484.7812 | 123.111 | -60.9192 | 62.0087 | 0.24773 | 0.0011834 | -0.0032257 | 0.0073336 | 0.059678 | -0.0035141 | 0.066343 | -61.3083 | 62.0773 | -61.2076 | -61.1481 | 61.7844 | -0.054932 | 0.004578 | 0.018311 | 62.0544 | -61.1984 | -0.28839 | 0.068665 | -0.3891 | -0.22888 | -0.2243 | -0.27924 | 0.045776 | -0.10071 | 60.9238 | 60.9375 | 122.7036 | 122.9965 | -0.3891 | 122.9736 | 60.8643 | -0.27924 | 122.9965 | -0.3891 | 60.8643 | 122.7036 | 122.9736 | -123.2162 | -123.2071
1485.7812 | 123.1247 | -60.8963 | 62.0178 | 0.20195 | -0.0037298 | -0.0068573 | 0.0049838 | 0.063096 | -0.0039413 | 0.069333 | -61.0611 | 62.1323 | -61.1984 | -61.1481 | 61.7661 | -0.036621 | -0.082397 | 0.045776 | 62.0132 | -61.2259 | -0.30212 | 0.11444 | -0.16479 | -0.25177 | -0.25177 | -0.32959 | -0.004577 | 0.13733 | 60.8139 | 60.9421 | 122.6624 | 123.0286 | -0.16479 | 122.9095 | 60.8597 | -0.32959 | 123.0286 | -0.16479 | 60.8597 | 122.6624 | 122.9095 | -123.2162 | -123.2437
1486.7812 | 123.1796 | -60.8826 | 61.9904 | 0.072251 | -0.0060798 | -0.0055755 | -0.002493 | 0.06096 | -0.0030869 | 0.067838 | -61.0565 | 62.0361 | -61.1526 | -61.0977 | 61.7981 | 0.068665 | -0.086975 | 0.14648 | 62.0224 | -61.1618 | -0.27008 | 0.045777 | -0.17395 | -0.21515 | -0.19226 | -0.27924 | 0.032044 | 0.09613 | 60.7956 | 61.0291 | 122.6807 | 122.9187 | -0.17395 | 122.905 | 60.9512 | -0.27924 | 122.9187 | -0.17395 | 60.9512 | 122.6807 | 122.905 | -123.143 | -123.1522
1487.7812 | 123.1796 | -60.878 | 62.0361 | -0.0040434 | -0.0071478 | -0.0053619 | -0.0012112 | 0.058823 | -0.0045821 | 0.067411 | -61.0474 | 62.0453 | -61.1664 | -61.1023 | 61.8576 | 0.073242 | -0.064087 | 0.19684 | 62.0407 | -61.1572 | -0.28839 | 0.009155 | -0.16937 | -0.2243 | -0.17853 | -0.27924 | 0.004577 | 0.11902 | 60.8139 | 61.0748 | 122.7356 | 122.9233 | -0.16937 | 122.9187 | 60.9512 | -0.27924 | 122.9233 | -0.16937 | 60.9512 | 122.7356 | 122.9187 | -123.2025 | -123.1934
1488.7812 | 123.1659 | -60.8826 | 62.0361 | 0.049362 | -0.007575 | -0.010062 | 0.00071144 | 0.05861 | -0.0011643 | 0.067624 | -61.0474 | 62.0453 | -61.1618 | -61.1023 | 61.8439 | 0.050354 | -0.07782 | 0.17853 | 62.0361 | -61.1526 | -0.27924 | 0.009155 | -0.16479 | -0.21973 | -0.19226 | -0.27008 | 0 | 0.11444 | 60.8047 | 61.0611 | 122.7264 | 122.9279 | -0.16479 | 122.9187 | 60.9329 | -0.27008 | 122.9279 | -0.16479 | 60.9329 | 122.7264 | 122.9187 | -123.1979 | -123.1888
1489.7812 | 123.1796 | -60.8826 | 61.9766 | 0.21721 | -0.0035162 | -0.0070709 | 0.005411 | 0.059464 | -0.0035141 | 0.067411 | -61.0016 | 62.027 | -61.1847 | -61.084 | 61.8393 | 0.041199 | -0.16937 | 0.14191 | 61.9766 | -61.1389 | -0.30212 | 0.050354 | -0.11902 | -0.20142 | -0.13733 | -0.25635 | 0 | 0.1831 | 60.7132 | 61.0245 | 122.7219 | 122.9095 | -0.11902 | 122.8592 | 60.9238 | -0.25635 | 122.9095 | -0.11902 | 60.9238 | 122.7219 | 122.8592 | -123.1613 | -123.1155
1490.7812 | 123.2529 | -60.8871 | 62.0087 | 0.10277 | -0.0071478 | -0.010916 | 0.00071144 | 0.057969 | -0.0056503 | 0.067411 | -61.0519 | 62.0453 | -61.1389 | -61.1252 | 61.8393 | 0.036621 | -0.064087 | 0.15106 | 62.0316 | -61.1298 | -0.25177 | 0.036621 | -0.16479 | -0.23804 | -0.16937 | -0.24262 | 0.022888 | 0.086975 | 60.8231 | 61.0382 | 122.7264 | 122.9324 | -0.16479 | 122.9187 | 60.9238 | -0.24262 | 122.9324 | -0.16479 | 60.9238 | 122.7264 | 122.9187 | -123.1476 | -123.1384
1491.7812 | 123.2117 | -60.8826 | 61.9766 | 1.8804 | -0.003089 | -0.0066437 | 0.0041292 | 0.060746 | -0.0058639 | 0.068052 | -60.9421 | 62.0087 | -61.1893 | -61.0748 | 61.8668 | 0.059509 | -0.20142 | 0.15106 | 61.9995 | -61.1389 | -0.3067 | 0.032043 | -0.05951 | -0.19226 | -0.10986 | -0.25635 | 0.022888 | 0.24719 | 60.6812 | 61.0336 | 122.7493 | 122.8912 | -0.05951 | 122.8821 | 60.9421 | -0.25635 | 122.8912 | -0.05951 | 60.9421 | 122.7493 | 122.8821 | -123.1659 | -123.1155
1492.7812 | 123.1934 | -60.8643 | 61.9904 | 0.24773 | -0.0024482 | -0.010916 | 0.0034884 | 0.061387 | -0.0039413 | 0.067197 | -60.9787 | 62.027 | -61.1664 | -61.2396 | 61.8027 | 0.082397 | -0.13733 | 0.18768 | 62.0041 | -61.1481 | -0.30212 | 0.036622 | -0.11444 | -0.37537 | -0.18768 | -0.28381 | 0.013733 | 0.18768 | 60.7269 | 61.0519 | 122.6669 | 122.8912 | -0.11444 | 122.8683 | 60.9467 | -0.28381 | 122.8912 | -0.11444 | 60.9467 | 122.6669 | 122.8683 | -123.1567 | -123.1384
1493.7812 | 123.1659 | -60.8597 | 62.0041 | 0.20958 | -0.0067206 | -0.0092071 | -0.00099756 | 0.060105 | -0.0035141 | 0.069547 | -61.0519 | 62.0407 | -61.1618 | -61.116 | 61.8027 | 0.018311 | -0.091553 | 0.11902 | 61.9904 | -61.1298 | -0.30212 | 0.036621 | -0.19226 | -0.25635 | -0.20142 | -0.27008 | -0.013733 | 0.10986 | 60.7681 | 60.9787 | 122.6624 | 122.9004 | -0.19226 | 122.85 | 60.878 | -0.27008 | 122.9004 | -0.19226 | 60.878 | 122.6624 | 122.85 | -123.1659 | -123.1338
1494.7812 | 123.1293 | -60.91 | 62.0132 | 0.2401 | -0.00138 | -0.0089935 | 0.008829 | 0.061173 | -0.0033005 | 0.06912 | -61.0519 | 62.1185 | -61.1801 | -61.1389 | 61.7844 | -0.032043 | -0.11902 | 0.068665 | 62.0041 | -61.203 | -0.27008 | 0.10529 | -0.14191 | -0.22888 | -0.22888 | -0.29297 | -0.009156 | 0.12817 | 60.791 | 60.9787 | 122.6944 | 123.0286 | -0.14191 | 122.9141 | 60.878 | -0.29297 | 123.0286 | -0.14191 | 60.878 | 122.6944 | 122.9141 | -123.1934 | -123.2162
1495.7812 | 123.2208 | -60.8871 | 61.9858 | 0.19432 | -0.0041572 | -0.0068573 | 0.0056246 | 0.061387 | -0.0037277 | 0.068265 | -60.9879 | 62.0682 | -61.171 | -61.0886 | 61.853 | 0.036621 | -0.17853 | 0.13733 | 62.0132 | -61.1618 | -0.28381 | 0.082397 | -0.10071 | -0.20142 | -0.13275 | -0.27466 | 0.027466 | 0.18311 | 60.7086 | 61.0245 | 122.7402 | 122.9553 | -0.10071 | 122.9004 | 60.9238 | -0.27466 | 122.9553 | -0.10071 | 60.9238 | 122.7402 | 122.9004 | -123.1567 | -123.1476
1496.7812 | 123.0652 | -60.9329 | 62.0407 | 0.10277 | -0.003089 | -0.00066214 | 0.0058382 | 0.062669 | -0.0041549 | 0.068693 | -61.0291 | 62.1735 | -61.1664 | -61.1389 | 61.7706 | -0.018311 | 0.013733 | 0.068665 | 62.0819 | -61.1893 | -0.23346 | 0.13275 | -0.096131 | -0.20599 | -0.27008 | -0.25635 | 0.041199 | 0.13733 | 60.9467 | 61.0016 | 122.7036 | 123.1064 | -0.096131 | 123.0148 | 60.9146 | -0.25635 | 123.1064 | -0.096131 | 60.9146 | 122.7036 | 123.0148 | -123.2071 | -123.23
1497.7812 | 123.1247 | -60.9192 | 62.027 | -0.2787 | -0.0018072 | -0.0055755 | 0.004343 | 0.066727 | -0.0035141 | 0.069974 | -61.0748 | 62.1368 | -61.1938 | -61.1664 | 61.7798 | -0.045776 | -0.027466 | 0.041199 | 62.0636 | -61.1984 | -0.27466 | 0.10986 | -0.15564 | -0.24719 | -0.24719 | -0.27924 | 0.036621 | 0.11902 | 60.8917 | 60.9604 | 122.699 | 123.056 | -0.15564 | 122.9828 | 60.8734 | -0.27924 | 123.056 | -0.15564 | 60.8734 | 122.699 | 122.9828 | -123.2208 | -123.2254
1498.7812 | 123.23 | -60.8826 | 61.972 | 0.27061 | -0.0045844 | -0.0089935 | 0.0032748 | 0.065018 | -0.0033005 | 0.069547 | -60.9787 | 62.0499 | -61.1801 | -61.084 | 61.8622 | 0.045776 | -0.19684 | 0.13733 | 62.0178 | -61.1343 | -0.29755 | 0.07782 | -0.096131 | -0.20142 | -0.10986 | -0.25177 | 0.045776 | 0.20142 | 60.6857 | 61.0199 | 122.7448 | 122.9324 | -0.096131 | 122.9004 | 60.9283 | -0.25177 | 122.9324 | -0.096131 | 60.9283 | 122.7448 | 122.9004 | -123.1522 | -123.1064
1499.7812 | 123.1842 | -60.8917 | 61.9904 | 0.26299 | -0.0073614 | -0.0047211 | -0.00035676 | 0.061387 | -0.0060775 | 0.066556 | -60.9604 | 62.027 | -61.1938 | -61.0657 | 61.8713 | 0.068665 | -0.17395 | 0.17395 | 62.0041 | -61.1618 | -0.30212 | 0.036622 | -0.068664 | -0.17395 | -0.11902 | -0.27008 | 0.013733 | 0.23346 | 60.7178 | 61.0657 | 122.7631 | 122.9187 | -0.068664 | 122.8958 | 60.9604 | -0.27008 | 122.9187 | -0.068664 | 60.9604 | 122.7631 | 122.8958 | -123.1842 | -123.1522
1500.7812 | 123.175 | -60.8963 | 61.9858 | 0.30113 | -0.0054388 | -0.010703 | 0.0030612 | 0.06395 | -0.0024459 | 0.067624 | -61.0107 | 62.0819 | -61.1801 | -61.1023 | 61.853 | 0.022888 | -0.17395 | 0.12817 | 62.0132 | -61.1572 | -0.28381 | 0.09613 | -0.11444 | -0.20599 | -0.13275 | -0.26093 | 0.027466 | 0.16937 | 60.7224 | 61.0245 | 122.7493 | 122.9782 | -0.11444 | 122.9095 | 60.9192 | -0.26093 | 122.9782 | -0.11444 | 60.9192 | 122.7493 | 122.9095 | -123.1659 | -123.143
1501.7812 | 123.2025 | -60.8917 | 61.9629 | 0.17906 | -0.0071478 | -0.0060027 | 0.00049764 | 0.062241 | -0.0071457 | 0.070188 | -61.0016 | 62.0361 | -61.1755 | -61.1114 | 61.8393 | 0.036621 | -0.16022 | 0.16022 | 62.0132 | -61.1389 | -0.28381 | 0.073242 | -0.10986 | -0.21973 | -0.1236 | -0.24719 | 0.050354 | 0.17395 | 60.7315 | 61.0519 | 122.731 | 122.9279 | -0.10986 | 122.905 | 60.9283 | -0.24719 | 122.9279 | -0.10986 | 60.9283 | 122.731 | 122.905 | -123.1384 | -123.1018
1502.7812 | 123.2071 | -60.8734 | 61.9812 | 0.2401 | -0.0052252 | -0.0077117 | 0.0022066 | 0.061173 | -0.0047957 | 0.070188 | -61.0153 | 62.027 | -61.1755 | -61.0977 | 61.8484 | 0.045776 | -0.17395 | 0.14191 | 61.9949 | -61.1343 | -0.30212 | 0.045777 | -0.14191 | -0.2243 | -0.13275 | -0.26093 | 0.013733 | 0.16022 | 60.6995 | 61.0153 | 122.7219 | 122.9004 | -0.14191 | 122.8683 | 60.9192 | -0.26093 | 122.9004 | -0.14191 | 60.9192 | 122.7219 | 122.8683 | -123.1567 | -123.1155
1503.7812 | 123.23 | -60.91 | 61.9949 | 0.1104 | -0.0050116 | -0.01113 | 0.00092504 | 0.060532 | -0.0050095 | 0.067197 | -61.0016 | 62.0407 | -61.1298 | -61.0931 | 61.8484 | 0.041199 | -0.17395 | 0.15564 | 62.0132 | -61.1526 | -0.21973 | 0.045776 | -0.091553 | -0.18311 | -0.14648 | -0.24261 | 0.018311 | 0.12817 | 60.7361 | 61.0657 | 122.7585 | 122.9507 | -0.091553 | 122.9233 | 60.9512 | -0.24261 | 122.9507 | -0.091553 | 60.9512 | 122.7585 | 122.9233 | -123.1247 | -123.1476
1504.7812 | 123.111 | -60.9055 | 62.0499 | -0.20241 | -0.0054388 | -0.0060027 | 7.0444e-05 | 0.059464 | -0.0056503 | 0.067411 | -61.0291 | 62.114 | -61.1435 | -61.1298 | 61.8301 | 0.073242 | 0.11902 | 0.19226 | 62.0911 | -61.1618 | -0.23804 | 0.064087 | -0.1236 | -0.2243 | -0.21973 | -0.25635 | 0.041198 | 0.11444 | 61.0245 | 61.0977 | 122.7356 | 123.0194 | -0.1236 | 122.9965 | 60.9787 | -0.25635 | 123.0194 | -0.1236 | 60.9787 | 122.7356 | 122.9965 | -123.1934 | -123.2117
1505.7812 | 123.2346 | -60.8826 | 61.9858 | 0.43083 | -0.005866 | -0.0068573 | 0.0051974 | 0.0616 | -0.0050095 | 0.069761 | -60.9833 | 62.0911 | -61.171 | -61.0931 | 61.8576 | 0.041199 | -0.1831 | 0.13275 | 61.9858 | -61.1893 | -0.28839 | 0.10529 | -0.10071 | -0.21057 | -0.12817 | -0.3067 | 0 | 0.18768 | 60.6995 | 61.0153 | 122.7402 | 122.9736 | -0.10071 | 122.8683 | 60.9238 | -0.3067 | 122.9736 | -0.10071 | 60.9238 | 122.7402 | 122.8683 | -123.1567 | -123.175
1506.7812 | 123.1979 | -60.9009 | 61.9583 | 0.21721 | -0.0039434 | -0.0036529 | 0.0049838 | 0.06096 | -0.0041549 | 0.068906 | -61.0107 | 62.0728 | -61.1755 | -61.0886 | 61.8484 | 0.050354 | -0.18768 | 0.13733 | 61.9949 | -61.1664 | -0.27466 | 0.11444 | -0.10986 | -0.18768 | -0.10986 | -0.2655 | 0.036621 | 0.16479 | 60.7132 | 61.0382 | 122.7493 | 122.9736 | -0.10986 | 122.8958 | 60.9512 | -0.2655 | 122.9736 | -0.10986 | 60.9512 | 122.7493 | 122.8958 | -123.1338 | -123.1247
1507.7812 | 123.1888 | -60.8826 | 61.9904 | 0.26299 | -0.0043708 | -0.0027985 | 0.0022066 | 0.06395 | -0.0045821 | 0.068479 | -61.0016 | 62.0911 | -61.1481 | -61.0886 | 61.821 | 0.013733 | -0.17395 | 0.13275 | 62.0087 | -61.1801 | -0.2655 | 0.10071 | -0.11902 | -0.20599 | -0.16937 | -0.29755 | 0.018311 | 0.14648 | 60.7086 | 61.0153 | 122.7036 | 122.9736 | -0.11902 | 122.8912 | 60.8963 | -0.29755 | 122.9736 | -0.11902 | 60.8963 | 122.7036 | 122.8912 | -123.1384 | -123.1705
1508.7812 | 123.2391 | -60.8551 | 62.0041 | -0.10323 | -0.006507 | -0.0072845 | -0.00014316 | 0.059251 | -0.0045821 | 0.069333 | -60.9787 | 62.0682 | -61.1481 | -61.0336 | 61.9217 | 0.16022 | -0.054932 | 0.27924 | 62.0499 | -61.1252 | -0.29297 | 0.064087 | -0.1236 | -0.17853 | -0.082397 | -0.27008 | 0.045777 | 0.16937 | 60.8002 | 61.1343 | 122.7768 | 122.9233 | -0.1236 | 122.905 | 61.0153 | -0.27008 | 122.9233 | -0.1236 | 61.0153 | 122.7768 | 122.905 | -123.1522 | -123.1293
1509.7812 | 123.2574 | -60.8643 | 62.0132 | -0.095596 | -0.0062934 | -0.0098479 | 0.00071144 | 0.063096 | -0.0052231 | 0.068052 | -60.9695 | 62.0407 | -61.1389 | -61.0107 | 61.9171 | 0.16022 | -0.082397 | 0.29755 | 62.0499 | -61.1206 | -0.27466 | 0.027465 | -0.10529 | -0.14648 | -0.096131 | -0.25635 | 0.036621 | 0.16937 | 60.7819 | 61.1618 | 122.7814 | 122.905 | -0.10529 | 122.9141 | 61.0245 | -0.25635 | 122.905 | -0.10529 | 61.0245 | 122.7814 | 122.9141 | -123.1522 | -123.1338
1510.7812 | 123.1064 | -60.9146 | 62.0224 | -0.21767 | -0.0022346 | -0.0068573 | 0.0077608 | 0.063096 | -0.0030869 | 0.066984 | -61.0336 | 62.1185 | -61.1664 | -61.1938 | 61.7523 | -0.045776 | -0.022888 | 0.054932 | 62.0407 | -61.203 | -0.25177 | 0.09613 | -0.11902 | -0.27924 | -0.27008 | -0.28839 | 0.01831 | 0.13275 | 60.8917 | 60.9695 | 122.6669 | 123.0331 | -0.11902 | 122.9553 | 60.8688 | -0.28839 | 123.0331 | -0.11902 | 60.8688 | 122.6669 | 122.9553 | -123.1888 | -123.2254
1511.7812 | 123.1522 | -60.8963 | 62.0087 | 0.28587 | -0.003089 | -0.0051483 | 0.0056246 | 0.062455 | -0.0052231 | 0.067624 | -61.0336 | 62.1048 | -61.1893 | -61.1435 | 61.8027 | -0.013733 | -0.1236 | 0.082397 | 62.0224 | -61.1847 | -0.29297 | 0.09613 | -0.13733 | -0.24719 | -0.20599 | -0.28839 | 0.013733 | 0.15564 | 60.7727 | 60.9787 | 122.699 | 123.0011 | -0.13733 | 122.9187 | 60.8826 | -0.28839 | 123.0011 | -0.13733 | 60.8826 | 122.699 | 122.9187 | -123.1979 | -123.1934
1512.7812 | 123.1338 | -60.9055 | 62.0407 | 0.056992 | -0.0022346 | -0.0038665 | 0.0075472 | 0.06395 | -0.0058639 | 0.065275 | -60.997 | 62.1414 | -61.1664 | -61.1481 | 61.7935 | 0.009155 | 0.009155 | 0.10529 | 62.0865 | -61.203 | -0.26093 | 0.10071 | -0.091552 | -0.24261 | -0.24719 | -0.29755 | 0.045777 | 0.16937 | 60.9146 | 61.0107 | 122.699 | 123.0469 | -0.091552 | 122.9919 | 60.9146 | -0.29755 | 123.0469 | -0.091552 | 60.9146 | 122.699 | 122.9919 | -123.2071 | -123.2437
1513.7812 | 123.0743 | -60.8826 | 62.0041 | 0.26299 | -0.00138 | -0.0049347 | 0.0047702 | 0.064805 | -0.0043685 | 0.068479 | -61.0748 | 62.1368 | -61.2076 | -61.1755 | 61.8576 | -0.13275 | -0.27466 | 0.24261 | 62.0316 | -61.2213 | -0.32501 | 0.13275 | -0.19226 | -0.29297 | -0.14648 | -0.33875 | 0.027466 | 0.13275 | 60.6079 | 61.1252 | 122.7402 | 123.0194 | -0.19226 | 122.9141 | 60.7498 | -0.33875 | 123.0194 | -0.19226 | 60.7498 | 122.7402 | 122.9141 | -123.2117 | -123.2254
1514.7812 | 123.1934 | -60.8643 | 62.0453 | -0.019302 | -0.005866 | -0.0074981 | -0.00099756 | 0.062882 | -0.0041549 | 0.068906 | -61.0245 | 62.0728 | -61.1481 | -61.0474 | 61.9125 | 0.14191 | -0.032043 | 0.28839 | 62.0544 | -61.1206 | -0.28381 | 0.027466 | -0.16022 | -0.1831 | -0.13275 | -0.25635 | 0.009155 | 0.1236 | 60.8322 | 61.1526 | 122.7768 | 122.937 | -0.16022 | 122.9187 | 61.0062 | -0.25635 | 122.937 | -0.16022 | 61.0062 | 122.7768 | 122.9187 | -123.1934 | -123.1659
1515.7812 | 123.1705 | -60.8917 | 61.9949 | 0.17143 | -0.0062934 | -0.0042937 | -0.002493 | 0.062241 | -0.0045821 | 0.06912 | -61.0428 | 62.0361 | -61.1938 | -61.1526 | 61.8256 | 0.009155 | -0.091553 | 0.12817 | 62.0453 | -61.1481 | -0.30212 | 0.041199 | -0.15106 | -0.26092 | -0.16937 | -0.25635 | 0.050354 | 0.15106 | 60.8002 | 61.0199 | 122.7173 | 122.9279 | -0.15106 | 122.937 | 60.9009 | -0.25635 | 122.9279 | -0.15106 | 60.9009 | 122.7173 | 122.937 | -123.1888 | -123.143
1516.7812 | 123.1613 | -60.8963 | 62.0132 | 0.13329 | -0.0056524 | -0.0068573 | -0.0016386 | 0.059891 | -0.0037277 | 0.068906 | -61.0611 | 62.0544 | -61.1664 | -61.1389 | 61.821 | 0.036621 | -0.064087 | 0.15106 | 62.0361 | -61.1526 | -0.27008 | 0.041198 | -0.16479 | -0.24262 | -0.19226 | -0.25635 | 0.022888 | 0.10529 | 60.8322 | 61.0474 | 122.7173 | 122.9507 | -0.16479 | 122.9324 | 60.9329 | -0.25635 | 122.9507 | -0.16479 | 60.9329 | 122.7173 | 122.9324 | -123.1796 | -123.1659
1517.7812 | 123.23 | -60.8551 | 62.0224 | -0.11085 | -0.009284 | -0.0083527 | -0.00099756 | 0.059891 | -0.0054367 | 0.066556 | -60.9512 | 62.0453 | -61.1526 | -61.0382 | 61.9034 | 0.15106 | -0.064087 | 0.29297 | 62.0728 | -61.1206 | -0.29755 | 0.022888 | -0.09613 | -0.1831 | -0.11902 | -0.2655 | 0.050354 | 0.20142 | 60.791 | 61.1481 | 122.7585 | 122.9004 | -0.09613 | 122.9279 | 61.0062 | -0.2655 | 122.9004 | -0.09613 | 61.0062 | 122.7585 | 122.9279 | -123.175 | -123.143
1518.7812 | 123.175 | -60.8871 | 62.0224 | 0.14092 | -0.007575 | -0.0087799 | -0.00035676 | 0.0616 | -0.0030869 | 0.067411 | -61.0428 | 62.0544 | -61.1298 | -61.1435 | 61.8256 | 0.009155 | -0.068665 | 0.13733 | 62.0224 | -61.1481 | -0.24262 | 0.032043 | -0.15564 | -0.25635 | -0.19684 | -0.26093 | 0 | 0.086975 | 60.8185 | 61.0245 | 122.7127 | 122.9416 | -0.15564 | 122.9095 | 60.8963 | -0.26093 | 122.9416 | -0.15564 | 60.8963 | 122.7127 | 122.9095 | -123.1522 | -123.1705
1519.7812 | 123.0789 | -60.9238 | 62.0132 | 0.20195 | -0.0043708 | -0.0081389 | 0.0077608 | 0.063737 | -0.0052231 | 0.068479 | -61.0657 | 62.1231 | -61.1801 | -61.1755 | 61.7386 | -0.059509 | -0.004578 | 0.022888 | 62.0911 | -61.1984 | -0.25635 | 0.10986 | -0.14191 | -0.25177 | -0.27466 | -0.27466 | 0.077819 | 0.11444 | 60.9192 | 60.9467 | 122.6624 | 123.0469 | -0.14191 | 123.0148 | 60.8643 | -0.27466 | 123.0469 | -0.14191 | 60.8643 | 122.6624 | 123.0148 | -123.1934 | -123.2117
1520.7812 | 123.0927 | -60.9283 | 62.027 | -1.6367 | -0.006507 | -0.0042937 | 0.0058382 | 0.062455 | -0.0041549 | 0.066984 | -61.0474 | 62.1185 | -61.1801 | -61.1938 | 61.7386 | -0.059509 | -0.013733 | 0.054932 | 62.0636 | -61.2122 | -0.25177 | 0.091552 | -0.11902 | -0.2655 | -0.28839 | -0.28381 | 0.036621 | 0.13275 | 60.9146 | 60.9833 | 122.6669 | 123.0469 | -0.11902 | 122.9919 | 60.8688 | -0.28381 | 123.0469 | -0.11902 | 60.8688 | 122.6669 | 122.9919 | -123.2071 | -123.2391
1521.7812 | 123.1979 | -60.9055 | 61.972 | 0.041733 | -0.0069342 | -0.0066437 | 0.0062656 | 0.062455 | -0.0035141 | 0.068693 | -61.0107 | 62.0819 | -61.1755 | -61.0977 | 61.8622 | 0.036621 | -0.19226 | 0.13275 | 62.0087 | -61.1755 | -0.27008 | 0.10986 | -0.10529 | -0.19226 | -0.10986 | -0.27008 | 0.036621 | 0.16479 | 60.7132 | 61.0382 | 122.7676 | 122.9874 | -0.10529 | 122.9141 | 60.9421 | -0.27008 | 122.9874 | -0.10529 | 60.9421 | 122.7676 | 122.9141 | -123.1476 | -123.1476
1522.7812 | 123.1796 | -60.9421 | 62.0178 | 0.20195 | -0.0037298 | -0.0070709 | 0.0073336 | 0.063096 | -0.0050095 | 0.067411 | -61.0519 | 62.1597 | -61.1938 | -61.1755 | 61.7294 | -0.059509 | -0.004578 | -0.28381 | 62.0453 | -61.2259 | -0.25177 | 0.14191 | -0.10986 | -0.23346 | -0.28839 | -0.28381 | 0.027466 | 0.14191 | 60.9375 | 60.6583 | 122.6715 | 123.1018 | -0.10986 | 122.9874 | 60.8826 | -0.28381 | 123.1018 | -0.10986 | 60.8826 | 122.6715 | 122.9874 | -123.2117 | -123.2437
1523.7812 | 123.1979 | -60.8871 | 62.0132 | 0.056992 | -0.0060798 | -0.010275 | -0.002493 | 0.061387 | -0.0058639 | 0.068265 | -61.0519 | 62.0453 | -61.171 | -61.0977 | 61.8805 | 0.082397 | -0.050354 | 0.21973 | 62.0544 | -61.1389 | -0.28381 | 0.032043 | -0.16479 | -0.21057 | -0.13275 | -0.25177 | 0.041198 | 0.11902 | 60.8368 | 61.1069 | 122.7676 | 122.9324 | -0.16479 | 122.9416 | 60.9695 | -0.25177 | 122.9324 | -0.16479 | 60.9695 | 122.7676 | 122.9416 | -123.1842 | -123.1522
1524.7812 | 123.1247 | -60.9009 | 62.0636 | -0.0040434 | -0.004798 | -0.0015167 | 0.0084018 | 0.065232 | -0.0050095 | 0.068479 | -60.997 | 62.1597 | -61.171 | -61.1252 | 61.8576 | 0.032043 | 0.045776 | 0.16937 | 62.059 | -61.1938 | -0.27008 | 0.09613 | -0.09613 | -0.2243 | -0.20599 | -0.29297 | -0.004578 | 0.17395 | 60.9467 | 61.0703 | 122.7585 | 123.0606 | -0.09613 | 122.9599 | 60.9329 | -0.29297 | 123.0606 | -0.09613 | 60.9329 | 122.7585 | 122.9599 | -123.2346 | -123.2574
1525.7812 | 123.1155 | -60.9055 | 62.0407 | 0.049362 | -0.003089 | -0.0064301 | 0.0066928 | 0.062669 | -0.0065047 | 0.067624 | -60.997 | 62.1506 | -61.1664 | -61.1206 | 61.8118 | 0.018311 | 0.009155 | 0.11902 | 62.0773 | -61.203 | -0.26093 | 0.10986 | -0.091552 | -0.21515 | -0.22888 | -0.29755 | 0.036622 | 0.16937 | 60.9146 | 61.0245 | 122.7173 | 123.056 | -0.091552 | 122.9828 | 60.9238 | -0.29755 | 123.056 | -0.091552 | 60.9238 | 122.7173 | 122.9828 | -123.2071 | -123.2437
1526.7812 | 123.1201 | -60.9055 | 62.0316 | 0.07988 | -0.0041572 | -0.0055755 | 0.0049838 | 0.064164 | -0.0045821 | 0.068265 | -61.0153 | 62.1323 | -61.1755 | -61.116 | 61.8118 | 0.050354 | 0.018311 | 0.11902 | 62.1048 | -61.1984 | -0.27008 | 0.10071 | -0.10986 | -0.21057 | -0.21973 | -0.29297 | 0.073242 | 0.16022 | 60.9238 | 61.0245 | 122.7173 | 123.0377 | -0.10986 | 123.0103 | 60.9558 | -0.29297 | 123.0377 | -0.10986 | 60.9558 | 122.7173 | 123.0103 | -123.2071 | -123.23
1527.7812 | 123.2071 | -60.9009 | 61.9995 | 0.2935 | -0.0054388 | -0.0083527 | -0.00057036 | 0.063737 | -0.0037277 | 0.068906 | -61.0062 | 62.0453 | -61.1938 | -61.1069 | 61.8668 | 0.045776 | -0.1831 | 0.14648 | 62.0316 | -61.1526 | -0.29297 | 0.045776 | -0.10529 | -0.20599 | -0.13275 | -0.25177 | 0.032043 | 0.18768 | 60.7178 | 61.0474 | 122.7676 | 122.9462 | -0.10529 | 122.9324 | 60.9467 | -0.25177 | 122.9462 | -0.10529 | 60.9467 | 122.7676 | 122.9324 | -123.1934 | -123.1522
1528.7812 | 123.1796 | -60.8688 | 61.9904 | 0.23247 | -0.0071478 | -0.0077117 | -0.0018522 | 0.064164 | -0.0037277 | 0.069333 | -61.0336 | 62.027 | -61.1893 | -61.116 | 61.8393 | 0.036621 | -0.13275 | 0.14191 | 62.0453 | -61.1526 | -0.32044 | 0.036622 | -0.1648 | -0.24719 | -0.15106 | -0.28381 | 0.054932 | 0.15564 | 60.7361 | 61.0107 | 122.7081 | 122.8958 | -0.1648 | 122.9141 | 60.9055 | -0.28381 | 122.8958 | -0.1648 | 60.9055 | 122.7081 | 122.9141 | -123.1796 | -123.143
1529.7812 | 123.0927 | -60.9238 | 62.027 | 0.1638 | -0.0026618 | -0.0057891 | 0.0066928 | 0.062882 | -0.0030869 | 0.069547 | -61.0519 | 62.1506 | -61.2076 | -61.1755 | 61.7661 | -0.041199 | -0.054932 | 0.054932 | 62.0636 | -61.203 | -0.28381 | 0.1236 | -0.12817 | -0.25177 | -0.26093 | -0.27924 | 0.036621 | 0.15564 | 60.8688 | 60.9787 | 122.6898 | 123.0743 | -0.12817 | 122.9874 | 60.8826 | -0.27924 | 123.0743 | -0.12817 | 60.8826 | 122.6898 | 122.9874 | -123.2346 | -123.23
1530.7812 | 123.1018 | -60.9055 | 62.0224 | 0.11803 | -0.0052252 | -0.0081389 | 0.0075472 | 0.06395 | -0.0028731 | 0.06912 | -61.0336 | 62.2009 | -61.1664 | -61.1664 | 61.7889 | -0.004578 | 0.022888 | 0.091553 | 62.0636 | -61.2076 | -0.26093 | 0.17853 | -0.12817 | -0.26093 | -0.23346 | -0.30212 | 0.041199 | 0.13275 | 60.9283 | 60.997 | 122.6944 | 123.1064 | -0.12817 | 122.9691 | 60.9009 | -0.30212 | 123.1064 | -0.12817 | 60.9009 | 122.6944 | 122.9691 | -123.1888 | -123.23
1531.7812 | 123.1476 | -60.8963 | 61.9949 | 0.24773 | -0.0018072 | -0.0064301 | 0.0051974 | 0.066087 | -0.0037277 | 0.069333 | -61.0703 | 62.114 | -61.1984 | -61.1618 | 61.7889 | -0.027466 | -0.09613 | 0.068665 | 62.0773 | -61.1618 | -0.30212 | 0.11902 | -0.17395 | -0.2655 | -0.20599 | -0.2655 | 0.082398 | 0.12817 | 60.8002 | 60.965 | 122.6852 | 123.0103 | -0.17395 | 122.9736 | 60.8688 | -0.2655 | 123.0103 | -0.17395 | 60.8688 | 122.6852 | 122.9736 | -123.1934 | -123.1567
1532.7812 | 123.2254 | -60.8643 | 62.0087 | 0.22484 | -0.0077888 | -0.0064301 | -0.0016386 | 0.06395 | -0.0030869 | 0.064634 | -60.9924 | 62.0499 | -61.1893 | -61.1755 | 61.9629 | 0.13275 | -0.15106 | 0.1831 | 62.0361 | -61.1572 | -0.32501 | 0.041199 | -0.12817 | -0.31128 | -0.045776 | -0.29297 | 0.027466 | 0.19684 | 60.7132 | 61.0474 | 122.8271 | 122.9141 | -0.12817 | 122.9004 | 60.997 | -0.29297 | 122.9141 | -0.12817 | 60.997 | 122.8271 | 122.9004 | -123.1979 | -123.1659
1533.7812 | 123.2117 | -60.8826 | 61.9812 | 0.2935 | -0.0080024 | -0.0051483 | 0.0015658 | 0.063309 | -0.0041549 | 0.069547 | -60.9833 | 62.0453 | -61.1847 | -61.0794 | 61.8576 | 0.050354 | -0.19226 | 0.15564 | 62.0544 | -61.1389 | -0.30212 | 0.064087 | -0.10071 | -0.19684 | -0.1236 | -0.25635 | 0.073242 | 0.20142 | 60.6903 | 61.0382 | 122.7402 | 122.9279 | -0.10071 | 122.937 | 60.9329 | -0.25635 | 122.9279 | -0.10071 | 60.9329 | 122.7402 | 122.937 | -123.1659 | -123.1201
1534.7812 | 123.0881 | -60.9146 | 62.0316 | 0.064621 | -0.003089 | -0.0030121 | 0.0066928 | 0.063523 | -0.0033005 | 0.068479 | -60.9924 | 62.1506 | -61.1801 | -61.1435 | 61.8073 | 0 | 0.022888 | 0.10986 | 62.1002 | -61.1984 | -0.2655 | 0.11902 | -0.07782 | -0.22888 | -0.2243 | -0.28381 | 0.068665 | 0.18768 | 60.9375 | 61.0245 | 122.7219 | 123.0652 | -0.07782 | 123.0148 | 60.9146 | -0.28381 | 123.0652 | -0.07782 | 60.9146 | 122.7219 | 123.0148 | -123.2117 | -123.23
1535.7812 | 123.1293 | -60.8963 | 62.0499 | -0.034561 | -0.0050116 | -0.0096343 | 0.0064792 | 0.064164 | -0.0022323 | 0.068906 | -60.9787 | 62.178 | -61.1755 | -61.1114 | 61.821 | 0.07782 | 0.018311 | 0.16937 | 62.0773 | -61.1847 | -0.27924 | 0.12817 | -0.082398 | -0.21515 | -0.22888 | -0.28839 | 0.027466 | 0.19684 | 60.9146 | 61.0657 | 122.7173 | 123.0743 | -0.082398 | 122.9736 | 60.9741 | -0.28839 | 123.0743 | -0.082398 | 60.9741 | 122.7173 | 122.9736 | -123.2254 | -123.2346
1536.7812 | 123.1522 | -60.9283 | 62.027 | 0.17143 | -0.005866 | -0.0092071 | 0.005411 | 0.062455 | -0.0047957 | 0.067838 | -60.9741 | 62.1506 | -61.1938 | -61.1069 | 61.8393 | 0.032043 | 0.013733 | 0.15564 | 62.1002 | -61.171 | -0.2655 | 0.1236 | -0.045776 | -0.17853 | -0.18768 | -0.24261 | 0.073242 | 0.21973 | 60.9421 | 61.084 | 122.7676 | 123.0789 | -0.045776 | 123.0286 | 60.9604 | -0.24261 | 123.0789 | -0.045776 | 60.9604 | 122.7676 | 123.0286 | -123.2208 | -123.1979
1537.7812 | 123.0927 | -60.9055 | 62.0682 | -0.12611 | -0.005866 | -0.0072845 | 0.003702 | 0.062241 | -0.0045821 | 0.067197 | -61.0519 | 62.1277 | -61.1984 | -61.1389 | 61.8301 | 0.050354 | 0.12817 | 0.17395 | 62.114 | -61.1893 | -0.29297 | 0.05951 | -0.14648 | -0.23346 | -0.23804 | -0.28381 | 0.045777 | 0.14648 | 61.0336 | 61.0794 | 122.7356 | 123.0331 | -0.14648 | 123.0194 | 60.9558 | -0.28381 | 123.0331 | -0.14648 | 60.9558 | 122.7356 | 123.0194 | -123.2666 | -123.2574
1538.7812 | 123.1247 | -60.9192 | 62.059 | 0.0035856 | -0.0033026 | -0.00066214 | 0.005411 | 0.064591 | -0.0045821 | 0.066129 | -61.0062 | 62.1552 | -61.1755 | -61.1298 | 61.8027 | 0.032043 | 0.027466 | 0.12817 | 62.1002 | -61.1755 | -0.25635 | 0.09613 | -0.086976 | -0.21057 | -0.25635 | -0.25635 | 0.041199 | 0.16937 | 60.9467 | 61.0474 | 122.7219 | 123.0743 | -0.086976 | 123.0194 | 60.9512 | -0.25635 | 123.0743 | -0.086976 | 60.9512 | 122.7219 | 123.0194 | -123.2346 | -123.2346
1539.7812 | 123.143 | -60.8963 | 62.027 | -0.095596 | -0.0052252 | -0.010489 | 0.0041292 | 0.067155 | -0.0054367 | 0.073179 | -60.9558 | 62.1323 | -61.1618 | -61.116 | 61.8118 | 0.045776 | 0.022888 | 0.14191 | 62.1231 | -61.1801 | -0.2655 | 0.10529 | -0.05951 | -0.21973 | -0.21515 | -0.28381 | 0.09613 | 0.20599 | 60.9192 | 61.0382 | 122.7081 | 123.0286 | -0.05951 | 123.0194 | 60.9421 | -0.28381 | 123.0286 | -0.05951 | 60.9421 | 122.7081 | 123.0194 | -123.1888 | -123.2071
1540.7812 | 123.0469 | -60.8826 | 62.0499 | -0.20241 | -0.0062934 | -0.0070709 | -0.002493 | 0.064164 | -0.0047957 | 0.070188 | -61.0657 | 62.1643 | -61.203 | -61.1618 | 61.8073 | 0.054932 | 0.24261 | 0.36163 | 62.1826 | -61.1572 | -0.32044 | 0.11444 | -0.18311 | -0.27924 | -0.24262 | -0.27466 | 0.13275 | 0.13733 | 61.1252 | 61.2442 | 122.6898 | 123.0469 | -0.18311 | 123.0652 | 60.9375 | -0.27466 | 123.0469 | -0.18311 | 60.9375 | 122.6898 | 123.0652 | -123.2529 | -123.2071
1541.7812 | 123.1201 | -60.9009 | 62.0316 | -0.0040434 | -0.0028754 | -0.010916 | 0.0056246 | 0.063523 | -0.0056503 | 0.069974 | -61.0016 | 62.1552 | -61.1755 | -61.1435 | 61.8118 | 0.027466 | 0.013733 | 0.10529 | 62.0911 | -61.2076 | -0.27466 | 0.1236 | -0.10071 | -0.24261 | -0.21973 | -0.3067 | 0.059509 | 0.17395 | 60.9146 | 61.0062 | 122.7127 | 123.056 | -0.10071 | 122.9919 | 60.9283 | -0.3067 | 123.056 | -0.10071 | 60.9283 | 122.7127 | 122.9919 | -123.2071 | -123.2391
1542.7812 | 123.1155 | -60.8917 | 62.0316 | 0.10277 | -0.0037298 | -0.0049347 | 0.0051974 | 0.066514 | -0.0052231 | 0.069974 | -60.9833 | 62.1689 | -61.1572 | -61.1252 | 61.8073 | 0.041199 | 0.027466 | 0.13733 | 62.114 | -61.1801 | -0.2655 | 0.13733 | -0.091552 | -0.23346 | -0.2243 | -0.28839 | 0.082398 | 0.17395 | 60.9192 | 61.0291 | 122.699 | 123.0606 | -0.091552 | 123.0057 | 60.9329 | -0.28839 | 123.0606 | -0.091552 | 60.9329 | 122.699 | 123.0057 | -123.1888 | -123.2117
1543.7812 | 123.1293 | -60.9192 | 62.027 | 0.026474 | 0.00011541 | -0.0042937 | 0.0032748 | 0.064805 | -0.0043685 | 0.067197 | -61.1023 | 62.1231 | -61.1801 | -61.1389 | 61.8164 | 0.054932 | 0.032043 | 0.15564 | 62.1002 | -61.1847 | -0.26093 | 0.09613 | -0.18311 | -0.21973 | -0.21057 | -0.2655 | 0.073242 | 0.07782 | 60.9512 | 61.0748 | 122.7356 | 123.0423 | -0.18311 | 123.0194 | 60.9741 | -0.2655 | 123.0423 | -0.18311 | 60.9741 | 122.7356 | 123.0194 | -123.2071 | -123.2117
1544.7812 | 123.1293 | -60.91 | 62.0316 | 0.018845 | -0.004798 | -2.1336e-05 | 0.0045566 | 0.065873 | -0.0039413 | 0.066343 | -61.0016 | 62.146 | -61.1618 | -61.1801 | 61.7065 | 0 | 0.036621 | 0.15564 | 62.114 | -61.1893 | -0.25177 | 0.11444 | -0.091553 | -0.27008 | -0.32501 | -0.27924 | 0.082398 | 0.16022 | 60.9467 | 61.0657 | 122.6166 | 123.056 | -0.091553 | 123.024 | 60.91 | -0.27924 | 123.056 | -0.091553 | 60.91 | 122.6166 | 123.024 | -123.1934 | -123.2208
1545.7812 | 123.0927 | -60.91 | 62.0682 | -0.20241 | -0.0052252 | -0.0070709 | -0.00057036 | 0.063096 | -0.0033005 | 0.068265 | -61.0611 | 62.1368 | -61.1801 | -61.1664 | 61.8118 | 0.064087 | 0.15564 | 0.16022 | 62.1414 | -61.1664 | -0.27008 | 0.068665 | -0.15106 | -0.25635 | -0.25635 | -0.25635 | 0.073242 | 0.11902 | 61.0657 | 61.0703 | 122.7219 | 123.0469 | -0.15106 | 123.0515 | 60.9741 | -0.25635 | 123.0469 | -0.15106 | 60.9741 | 122.7219 | 123.0515 | -123.2483 | -123.2346
1546.7812 | 123.1018 | -60.8963 | 62.0956 | -0.46181 | -0.0041572 | -0.0081389 | 0.00071144 | 0.06096 | -0.0030869 | 0.069547 | -61.0611 | 62.1506 | -61.1618 | -61.1618 | 61.8073 | 0.054932 | 0.14648 | 0.1831 | 62.1231 | -61.1572 | -0.2655 | 0.054932 | -0.16479 | -0.2655 | -0.28839 | -0.26093 | 0.027466 | 0.10071 | 61.0428 | 61.0794 | 122.7036 | 123.0469 | -0.16479 | 123.0194 | 60.9512 | -0.26093 | 123.0469 | -0.16479 | 60.9512 | 122.7036 | 123.0194 | -123.2574 | -123.2529
1547.7812 | 123.0835 | -60.8871 | 62.059 | -0.149 | -0.0069342 | -0.0092071 | 0.00071144 | 0.060319 | -0.0037277 | 0.068479 | -61.0657 | 62.146 | -61.1664 | -61.2671 | 61.6974 | -0.004578 | 0.09613 | 0.13275 | 62.1048 | -61.2076 | -0.27924 | 0.086975 | -0.17853 | -0.37994 | -0.36163 | -0.32043 | 0.045776 | 0.10071 | 60.9833 | 61.0199 | 122.5845 | 123.0331 | -0.17853 | 122.9919 | 60.8826 | -0.32043 | 123.0331 | -0.17853 | 60.8826 | 122.5845 | 122.9919 | -123.2254 | -123.2666
1548.7812 | 123.1476 | -60.9055 | 62.0453 | 0.011215 | -0.0037298 | -0.0081389 | 0.0064792 | 0.063737 | -0.0041549 | 0.070615 | -60.9833 | 62.1643 | -61.1572 | -61.1023 | 61.8164 | 0.036621 | 0.036621 | 0.15106 | 62.0911 | -61.1893 | -0.25177 | 0.11902 | -0.077819 | -0.19684 | -0.22888 | -0.28381 | 0.045776 | 0.17395 | 60.9421 | 61.0565 | 122.7219 | 123.0698 | -0.077819 | 122.9965 | 60.9421 | -0.28381 | 123.0698 | -0.077819 | 60.9421 | 122.7219 | 122.9965 | -123.2025 | -123.2346
1549.7812 | 123.1155 | -60.9192 | 62.0316 | 0.056992 | -0.0041572 | -0.0057891 | 0.0039156 | 0.064164 | -0.0058639 | 0.066984 | -60.997 | 62.1643 | -61.1893 | -61.1572 | 61.7798 | 0.022888 | 0.013733 | 0.11444 | 62.1185 | -61.2076 | -0.27008 | 0.13275 | -0.07782 | -0.23804 | -0.25177 | -0.28839 | 0.086975 | 0.19226 | 60.9329 | 61.0336 | 122.699 | 123.0835 | -0.07782 | 123.0377 | 60.9421 | -0.28839 | 123.0835 | -0.07782 | 60.9421 | 122.699 | 123.0377 | -123.2208 | -123.2391
1550.7812 | 123.0927 | -60.8963 | 62.0773 | 0.46898 | -0.0052252 | -0.0036529 | 0.00092504 | 0.063523 | -0.0045821 | 0.068906 | -61.0748 | 62.1368 | -61.1984 | -61.1526 | 61.8118 | 0.050354 | 0.14191 | 0.16937 | 62.146 | -61.2122 | -0.30212 | 0.059509 | -0.17853 | -0.25635 | -0.2655 | -0.31586 | 0.068664 | 0.1236 | 61.0382 | 61.0657 | 122.7081 | 123.0331 | -0.17853 | 123.0423 | 60.9467 | -0.31586 | 123.0331 | -0.17853 | 60.9467 | 122.7081 | 123.0423 | -123.2758 | -123.2895
1551.7812 | 123.1018 | -60.91 | 62.0682 | -0.12611 | -0.0033026 | -0.0060027 | 0.0051974 | 0.063096 | -0.0041549 | 0.067838 | -61.0245 | 62.146 | -61.171 | -61.1252 | 61.8164 | 0.082397 | 0.091553 | 0.18768 | 62.1185 | -61.2305 | -0.26093 | 0.07782 | -0.11444 | -0.21515 | -0.25177 | -0.32043 | 0.050354 | 0.14648 | 61.0016 | 61.0977 | 122.7264 | 123.056 | -0.11444 | 123.0286 | 60.9924 | -0.32043 | 123.056 | -0.11444 | 60.9924 | 122.7264 | 123.0286 | -123.2391 | -123.2986
1552.7812 | 123.143 | -60.8917 | 62.0316 | -0.095596 | -0.0050116 | -0.010275 | 0.004343 | 0.063737 | -0.0047957 | 0.067838 | -61.0016 | 62.1597 | -61.1618 | -61.1206 | 61.8301 | 0.073242 | 0.041199 | 0.19226 | 62.1185 | -61.2076 | -0.27008 | 0.12817 | -0.10986 | -0.22888 | -0.20142 | -0.31586 | 0.086975 | 0.16022 | 60.9329 | 61.084 | 122.7219 | 123.0515 | -0.10986 | 123.0103 | 60.965 | -0.31586 | 123.0515 | -0.10986 | 60.965 | 122.7219 | 123.0103 | -123.1934 | -123.2391
1553.7812 | 123.0835 | -60.9283 | 62.059 | 0.034104 | -0.00138 | -0.0060027 | 0.0073336 | 0.064378 | -0.0037277 | 0.066984 | -61.0016 | 62.1552 | -61.1664 | -61.1481 | 61.7752 | -0.009155 | 0.041199 | 0.10529 | 62.1323 | -61.1893 | -0.23804 | 0.09613 | -0.073242 | -0.21973 | -0.28381 | -0.26093 | 0.073242 | 0.16479 | 60.9695 | 61.0336 | 122.7036 | 123.0835 | -0.073242 | 123.0606 | 60.9192 | -0.26093 | 123.0835 | -0.073242 | 60.9192 | 122.7036 | 123.0606 | -123.2254 | -123.2483
1554.7812 | 123.1293 | -60.8871 | 62.0407 | -0.17952 | -0.0080024 | -0.01113 | -0.001425 | 0.062882 | -0.0030869 | 0.068693 | -61.0062 | 62.1185 | -61.1481 | -61.1069 | 61.8484 | 0.10986 | 0.073242 | 0.23804 | 62.1094 | -61.1526 | -0.26093 | 0.07782 | -0.11902 | -0.21973 | -0.19226 | -0.2655 | 0.068665 | 0.14191 | 60.9604 | 61.1252 | 122.7356 | 123.0057 | -0.11902 | 122.9965 | 60.997 | -0.2655 | 123.0057 | -0.11902 | 60.997 | 122.7356 | 122.9965 | -123.1888 | -123.1934
1555.7812 | 123.111 | -60.8734 | 62.0544 | -0.0040434 | -0.004798 | -0.0094207 | 0.0015658 | 0.062455 | -0.0039413 | 0.06677 | -61.1114 | 62.1597 | -61.203 | -61.1618 | 61.7844 | 0.054932 | 0.14191 | 0.17395 | 62.1552 | -61.1893 | -0.32959 | 0.10529 | -0.23804 | -0.28839 | -0.27008 | -0.31586 | 0.10071 | 0.091553 | 61.0153 | 61.0474 | 122.6578 | 123.0331 | -0.23804 | 123.0286 | 60.9283 | -0.31586 | 123.0331 | -0.23804 | 60.9283 | 122.6578 | 123.0286 | -123.2574 | -123.2437
1556.7812 | 123.1476 | -60.8826 | 62.0682 | -0.10323 | -0.0028754 | -0.0077117 | 0.0015658 | 0.06395 | -0.0073593 | 0.065916 | -61.0336 | 62.1368 | -61.1893 | -61.1252 | 61.821 | 0.064087 | 0.10986 | 0.18768 | 62.1414 | -61.1755 | -0.3067 | 0.068665 | -0.15106 | -0.24262 | -0.24719 | -0.29297 | 0.073242 | 0.15564 | 60.9924 | 61.0703 | 122.7036 | 123.0194 | -0.15106 | 123.024 | 60.9467 | -0.29297 | 123.0194 | -0.15106 | 60.9467 | 122.7036 | 123.024 | -123.2574 | -123.2437
1557.7812 | 123.1064 | -60.9146 | 62.059 | -0.019302 | -0.0037298 | -0.0053619 | 0.0049838 | 0.064805 | -0.0030869 | 0.065488 | -60.9787 | 62.1643 | -61.1526 | -61.0931 | 61.7935 | 0.050354 | 0.036621 | 0.16022 | 62.114 | -61.1984 | -0.23804 | 0.10529 | -0.064087 | -0.17853 | -0.2655 | -0.28381 | 0.054932 | 0.17395 | 60.9512 | 61.0748 | 122.7081 | 123.0789 | -0.064087 | 123.0286 | 60.965 | -0.28381 | 123.0789 | -0.064087 | 60.965 | 122.7081 | 123.0286 | -123.2117 | -123.2574
1558.7812 | 123.0927 | -60.8963 | 62.0728 | -0.13374 | -0.0045844 | -0.0072845 | 0.0013522 | 0.064378 | -0.0033005 | 0.067838 | -61.0519 | 62.1552 | -61.1755 | -61.1435 | 61.7844 | 0.059509 | 0.13275 | 0.16937 | 62.1368 | -61.1801 | -0.27924 | 0.082397 | -0.15564 | -0.24719 | -0.28839 | -0.28381 | 0.064087 | 0.1236 | 61.0291 | 61.0657 | 122.6807 | 123.0515 | -0.15564 | 123.0331 | 60.9558 | -0.28381 | 123.0515 | -0.15564 | 60.9558 | 122.6807 | 123.0331 | -123.2483 | -123.2529
1559.7812 | 123.111 | -60.91 | 62.0682 | -0.080337 | -0.004798 | -0.0079253 | 0.0013522 | 0.062455 | -0.0041549 | 0.066984 | -61.1435 | 62.1597 | -61.1893 | -61.171 | 61.7844 | 0.036621 | 0.15106 | 0.16022 | 62.114 | -61.1893 | -0.27924 | 0.091553 | -0.23346 | -0.26093 | -0.28381 | -0.27924 | 0.045777 | 0.045776 | 61.0611 | 61.0703 | 122.6944 | 123.0698 | -0.23346 | 123.024 | 60.9467 | -0.27924 | 123.0698 | -0.23346 | 60.9467 | 122.6944 | 123.024 | -123.2574 | -123.2574
1560.7812 | 123.0881 | -60.9467 | 62.0407 | 0.1638 | -0.0041572 | -0.0068573 | 0.0045566 | 0.067155 | -0.0037277 | 0.067624 | -61.0703 | 62.1323 | -61.171 | -61.2259 | 61.7432 | -0.054932 | -0.018311 | 0.036621 | 62.114 | -61.2259 | -0.2243 | 0.091553 | -0.1236 | -0.27924 | -0.29755 | -0.27924 | 0.073243 | 0.10071 | 60.9283 | 60.9833 | 122.6898 | 123.0789 | -0.1236 | 123.0606 | 60.8917 | -0.27924 | 123.0789 | -0.1236 | 60.8917 | 122.6898 | 123.0606 | -123.2117 | -123.2666
1561.7812 | 123.2025 | -60.8688 | 62.0178 | -0.087967 | -0.0056524 | -0.012412 | -0.0020658 | 0.062028 | -0.0041549 | 0.067624 | -60.9558 | 62.0544 | -61.1526 | -61.0748 | 61.8851 | 0.15564 | -0.050354 | 0.30212 | 62.0956 | -61.0886 | -0.28381 | 0.036621 | -0.086976 | -0.20599 | -0.13275 | -0.21973 | 0.07782 | 0.19684 | 60.8185 | 61.171 | 122.7539 | 122.9233 | -0.086976 | 122.9645 | 61.0245 | -0.21973 | 122.9233 | -0.086976 | 61.0245 | 122.7539 | 122.9645 | -123.1705 | -123.1064
1562.7812 | 123.1201 | -60.8963 | 62.0728 | -0.16426 | -0.0060798 | -0.013907 | -0.0033476 | 0.059251 | -0.0054367 | 0.068479 | -61.0062 | 62.0865 | -61.1526 | -61.0977 | 61.8393 | 0.082397 | 0.073242 | 0.23804 | 62.1002 | -61.1526 | -0.25635 | 0.013733 | -0.10986 | -0.20142 | -0.23346 | -0.25635 | 0.027466 | 0.14648 | 60.9695 | 61.1343 | 122.7356 | 122.9828 | -0.10986 | 122.9965 | 60.9787 | -0.25635 | 122.9828 | -0.10986 | 60.9787 | 122.7356 | 122.9965 | -123.2254 | -123.2254
1563.7812 | 123.1201 | -60.8963 | 62.0361 | -0.04982 | -0.0035162 | -0.0057891 | 0.0069064 | 0.062241 | -0.0035141 | 0.067197 | -60.9833 | 62.1552 | -61.1526 | -61.1023 | 61.8301 | 0.054932 | 0.022888 | 0.1831 | 62.0865 | -61.1984 | -0.25635 | 0.11902 | -0.086975 | -0.20599 | -0.20599 | -0.30212 | 0.050354 | 0.16937 | 60.9192 | 61.0794 | 122.7264 | 123.0515 | -0.086975 | 122.9828 | 60.9512 | -0.30212 | 123.0515 | -0.086975 | 60.9512 | 122.7264 | 122.9828 | -123.1888 | -123.2346
1564.7812 | 123.1293 | -60.8734 | 62.0499 | -0.17189 | -0.0054388 | -0.010703 | 0.0062656 | 0.064805 | -0.0058639 | 0.06677 | -61.0153 | 62.1368 | -61.1801 | -61.1343 | 61.8073 | 0.050354 | 0.11444 | 0.18768 | 62.1185 | -61.1801 | -0.3067 | 0.086975 | -0.14191 | -0.26093 | -0.24262 | -0.3067 | 0.068664 | 0.16479 | 60.9879 | 61.0611 | 122.6807 | 123.0103 | -0.14191 | 122.9919 | 60.9238 | -0.3067 | 123.0103 | -0.14191 | 60.9238 | 122.6807 | 122.9919 | -123.23 | -123.23
1565.7812 | 123.1338 | -60.9238 | 62.0224 | -0.11085 | -0.0050116 | -0.0047211 | 0.0049838 | 0.066087 | -0.0028731 | 0.067838 | -60.9879 | 62.1552 | -61.1801 | -61.0977 | 61.8484 | 0.059509 | 0.059509 | 0.18768 | 62.1323 | -61.1984 | -0.25635 | 0.13275 | -0.064087 | -0.17395 | -0.17395 | -0.27466 | 0.10986 | 0.19226 | 60.9833 | 61.1114 | 122.7722 | 123.0789 | -0.064087 | 123.056 | 60.9833 | -0.27466 | 123.0789 | -0.064087 | 60.9833 | 122.7722 | 123.056 | -123.2025 | -123.2208
1566.7812 | 123.2025 | -60.8597 | 62.0132 | -2.7964 | -0.0060798 | -0.010489 | -0.0033476 | 0.062455 | -0.0060775 | 0.071256 | -60.8871 | 62.1048 | -61.1343 | -61.0931 | 61.8896 | 0.1236 | -0.004578 | 0.29755 | 62.0728 | -61.1298 | -0.27466 | 0.091552 | -0.027466 | -0.23346 | -0.1236 | -0.27008 | 0.059509 | 0.24719 | 60.8551 | 61.1572 | 122.7493 | 122.9645 | -0.027466 | 122.9324 | 60.9833 | -0.27008 | 122.9645 | -0.027466 | 60.9833 | 122.7493 | 122.9324 | -123.1476 | -123.143
1567.7812 | 123.111 | -60.91 | 62.0773 | -0.31685 | -0.0041572 | -0.0070709 | -0.00057036 | 0.062882 | -0.0020187 | 0.067411 | -61.0199 | 62.1414 | -61.1572 | -61.1526 | 61.8027 | 0.050354 | 0.14191 | 0.16937 | 62.1231 | -61.203 | -0.24719 | 0.064086 | -0.10986 | -0.24261 | -0.27466 | -0.29297 | 0.045776 | 0.13733 | 61.0519 | 61.0794 | 122.7127 | 123.0515 | -0.10986 | 123.0331 | 60.9604 | -0.29297 | 123.0515 | -0.10986 | 60.9604 | 122.7127 | 123.0331 | -123.2346 | -123.2803
1568.7812 | 123.1476 | -60.9009 | 62.0728 | -0.13374 | -0.0041572 | -0.0089935 | 0.0051974 | 0.062241 | -0.0035141 | 0.068052 | -61.0245 | 62.1872 | -61.1481 | -61.1389 | 61.8164 | 0.054932 | 0.11444 | 0.16022 | 62.1094 | -61.1893 | -0.24719 | 0.11444 | -0.1236 | -0.23804 | -0.25635 | -0.28839 | 0.036621 | 0.1236 | 61.0153 | 61.0611 | 122.7173 | 123.0881 | -0.1236 | 123.0103 | 60.9558 | -0.28839 | 123.0881 | -0.1236 | 60.9558 | 122.7173 | 123.0103 | -123.2208 | -123.262
1569.7812 | 123.111 | -60.878 | 62.0682 | -0.149 | -0.004798 | -0.0040801 | 0.0041292 | 0.063737 | -0.0050095 | 0.069333 | -61.0428 | 62.1597 | -61.1435 | -61.1435 | 61.8118 | 0.050354 | 0.11902 | 0.16937 | 62.1368 | -61.1664 | -0.2655 | 0.091553 | -0.16479 | -0.2655 | -0.25635 | -0.28839 | 0.068665 | 0.10071 | 60.997 | 61.0474 | 122.6898 | 123.0377 | -0.16479 | 123.0148 | 60.9283 | -0.28839 | 123.0377 | -0.16479 | 60.9283 | 122.6898 | 123.0148 | -123.2117 | -123.2346
1570.7812 | 123.1934 | -60.8551 | 62.0499 | 2.2009 | -0.006507 | -0.0038665 | -0.00057036 | 0.062241 | -0.0056503 | 0.065702 | -61.0016 | 62.0453 | -61.1618 | -61.0611 | 61.9308 | 0.14648 | -0.027466 | 0.28839 | 62.0956 | -61.1114 | -0.3067 | -0.004578 | -0.14648 | -0.20599 | -0.11902 | -0.25635 | 0.045776 | 0.16022 | 60.8276 | 61.1435 | 122.7859 | 122.9004 | -0.14648 | 122.9507 | 61.0016 | -0.25635 | 122.9004 | -0.14648 | 61.0016 | 122.7859 | 122.9507 | -123.2117 | -123.1613
1571.7812 | 123.143 | -60.8597 | 62.0499 | -0.149 | -0.0056524 | -0.010489 | 0.00049764 | 0.060746 | -0.0069321 | 0.068693 | -60.9833 | 62.0773 | -61.1481 | -61.084 | 61.8713 | 0.13275 | 0.036621 | 0.24719 | 62.0911 | -61.1343 | -0.28839 | 0.027466 | -0.1236 | -0.2243 | -0.17853 | -0.27466 | 0.041198 | 0.1648 | 60.8963 | 61.1069 | 122.731 | 122.937 | -0.1236 | 122.9507 | 60.9924 | -0.27466 | 122.937 | -0.1236 | 60.9924 | 122.731 | 122.9507 | -123.1979 | -123.1842
1572.7812 | 123.1064 | -60.9146 | 62.0499 | -0.17952 | -0.0022346 | -0.0098479 | 0.002634 | 0.060319 | -0.0067185 | 0.066984 | -61.0565 | 62.146 | -61.1801 | -61.2579 | 61.6974 | -0.009155 | 0.12817 | 0.1236 | 62.1094 | -61.1984 | -0.2655 | 0.09613 | -0.14191 | -0.34332 | -0.35248 | -0.28381 | 0.059509 | 0.1236 | 61.0428 | 61.0382 | 122.612 | 123.0606 | -0.14191 | 123.024 | 60.9055 | -0.28381 | 123.0606 | -0.14191 | 60.9055 | 122.612 | 123.024 | -123.23 | -123.2483
1573.7812 | 123.1155 | -60.8963 | 62.0178 | -0.034561 | -0.0028754 | -0.0079253 | 0.0062656 | 0.065873 | -0.0052231 | 0.065916 | -60.9833 | 62.146 | -61.1755 | -61.0794 | 61.8164 | 0.027466 | 0.013733 | 0.17395 | 62.1002 | -61.1801 | -0.27924 | 0.12817 | -0.086975 | -0.18311 | -0.20142 | -0.28381 | 0.082398 | 0.19226 | 60.91 | 61.0703 | 122.7127 | 123.0423 | -0.086975 | 122.9965 | 60.9238 | -0.28381 | 123.0423 | -0.086975 | 60.9238 | 122.7127 | 122.9965 | -123.1934 | -123.1979
1574.7812 | 123.2483 | -60.8734 | 62.0224 | -0.057449 | -0.0060798 | -0.010703 | -0.0027066 | 0.061814 | -0.0054367 | 0.067838 | -60.9787 | 62.0453 | -61.1343 | -61.0428 | 61.9263 | 0.15106 | -0.068665 | 0.31128 | 62.0682 | -61.116 | -0.26093 | 0.022888 | -0.10529 | -0.16937 | -0.09613 | -0.24262 | 0.045776 | 0.15564 | 60.8047 | 61.1847 | 122.7997 | 122.9187 | -0.10529 | 122.9416 | 61.0245 | -0.24262 | 122.9187 | -0.10529 | 61.0245 | 122.7997 | 122.9416 | -123.1567 | -123.1384
1575.7812 | 123.2254 | -60.8643 | 62.027 | -0.13374 | -0.0077888 | -0.0055755 | -0.0012112 | 0.064805 | -0.0058639 | 0.067411 | -60.9741 | 62.0682 | -61.1572 | -61.1114 | 61.8576 | 0.14648 | -0.091553 | 0.26093 | 62.0636 | -61.1206 | -0.29297 | 0.041198 | -0.10986 | -0.24719 | -0.16937 | -0.25635 | 0.036621 | 0.18311 | 60.7727 | 61.1252 | 122.7219 | 122.9324 | -0.10986 | 122.9279 | 61.0107 | -0.25635 | 122.9324 | -0.10986 | 61.0107 | 122.7219 | 122.9279 | -123.1842 | -123.1476
1576.7812 | 123.1384 | -60.9009 | 62.0361 | -0.149 | -0.0037298 | -0.0049347 | 0.0066928 | 0.062882 | -0.0043685 | 0.066343 | -60.9695 | 62.1643 | -61.1984 | -61.0794 | 61.821 | 0.073242 | 0.045776 | 0.1831 | 62.1048 | -61.1984 | -0.29755 | 0.12817 | -0.068664 | -0.17853 | -0.21515 | -0.29755 | 0.068664 | 0.22888 | 60.9467 | 61.084 | 122.7219 | 123.0652 | -0.068664 | 123.0057 | 60.9741 | -0.29755 | 123.0652 | -0.068664 | 60.9741 | 122.7219 | 123.0057 | -123.2346 | -123.2346
1577.7812 | 123.111 | -60.9192 | 62.059 | 0.095139 | -0.00052559 | -0.0092071 | 0.008829 | 0.0663 | -0.0047957 | 0.066556 | -60.997 | 62.146 | -61.203 | -61.1343 | 61.7844 | -0.013733 | 0.013733 | 0.10529 | 62.1094 | -61.2122 | -0.28381 | 0.086975 | -0.07782 | -0.21515 | -0.27466 | -0.29297 | 0.050354 | 0.20599 | 60.9329 | 61.0245 | 122.7036 | 123.0652 | -0.07782 | 123.0286 | 60.9055 | -0.29297 | 123.0652 | -0.07782 | 60.9055 | 122.7036 | 123.0286 | -123.262 | -123.2712
1578.7812 | 123.1064 | -60.9009 | 62.027 | -0.026932 | -0.0020208 | -0.0053619 | 0.0039156 | 0.062241 | -0.0043685 | 0.065702 | -60.9741 | 62.1552 | -61.1893 | -61.0886 | 61.8347 | 0.041199 | 0.027466 | 0.16022 | 62.1094 | -61.1893 | -0.28839 | 0.12817 | -0.073242 | -0.18768 | -0.19226 | -0.28839 | 0.082397 | 0.21515 | 60.9283 | 61.0611 | 122.7356 | 123.056 | -0.073242 | 123.0103 | 60.9421 | -0.28839 | 123.056 | -0.073242 | 60.9421 | 122.7356 | 123.0103 | -123.2162 | -123.2162
1579.7812 | 123.2117 | -60.878 | 62.0316 | -0.149 | -0.0054388 | -0.013907 | -0.0050566 | 0.057328 | -0.0050095 | 0.069761 | -60.9924 | 62.059 | -61.1526 | -61.2625 | 61.8439 | 0.1236 | -0.086975 | 0.28381 | 62.0407 | -61.1298 | -0.27466 | 0.027466 | -0.11444 | -0.38452 | -0.18768 | -0.25177 | 0.009155 | 0.16022 | 60.791 | 61.1618 | 122.7219 | 122.937 | -0.11444 | 122.9187 | 61.0016 | -0.25177 | 122.937 | -0.11444 | 61.0016 | 122.7219 | 122.9187 | -123.1842 | -123.1613
1580.7812 | 123.1888 | -60.8734 | 62.0499 | -0.149 | -0.007575 | -0.0068573 | -0.0012112 | 0.060532 | -0.0015915 | 0.068265 | -60.9695 | 62.0911 | -61.1526 | -61.0611 | 61.8896 | 0.13733 | -0.004578 | 0.28839 | 62.0773 | -61.1252 | -0.27924 | 0.041198 | -0.09613 | -0.18768 | -0.16022 | -0.25177 | 0.027466 | 0.18311 | 60.8688 | 61.1618 | 122.7631 | 122.9645 | -0.09613 | 122.9507 | 61.0107 | -0.25177 | 122.9645 | -0.09613 | 61.0107 | 122.7631 | 122.9507 | -123.2025 | -123.175
1581.7812 | 123.2162 | -60.8459 | 62.0407 | -0.026932 | -0.004798 | -0.010275 | 0.00028404 | 0.059037 | -0.0041549 | 0.067838 | -60.9924 | 62.0636 | -61.171 | -61.0519 | 61.8851 | 0.13275 | -0.022888 | 0.28839 | 62.059 | -61.1389 | -0.32501 | 0.022889 | -0.14648 | -0.20599 | -0.15564 | -0.29297 | 0.018311 | 0.17853 | 60.8231 | 61.1343 | 122.731 | 122.9095 | -0.14648 | 122.905 | 60.9787 | -0.29297 | 122.9095 | -0.14648 | 60.9787 | 122.731 | 122.905 | -123.2117 | -123.1796
1582.7812 | 123.1018 | -60.9055 | 62.0636 | -0.13374 | -0.0054388 | -0.0068573 | 0.0034884 | 0.060319 | -0.0039413 | 0.065061 | -61.0336 | 62.1597 | -61.1755 | -61.1481 | 61.7935 | 0.045776 | 0.14191 | 0.1831 | 62.1185 | -61.171 | -0.27008 | 0.09613 | -0.12817 | -0.24261 | -0.27008 | -0.2655 | 0.054931 | 0.14191 | 61.0474 | 61.0886 | 122.699 | 123.0652 | -0.12817 | 123.024 | 60.9512 | -0.2655 | 123.0652 | -0.12817 | 60.9512 | 122.699 | 123.024 | -123.2391 | -123.2346
1583.7812 | 123.143 | -60.8826 | 62.059 | -0.072708 | -0.0024482 | -0.0066437 | 0.0049838 | 0.062455 | -0.0037277 | 0.066984 | -60.9924 | 62.1552 | -61.1755 | -61.0977 | 61.8256 | 0.064087 | 0.036621 | 0.1831 | 62.0865 | -61.1893 | -0.29297 | 0.09613 | -0.10986 | -0.21515 | -0.23346 | -0.3067 | 0.027466 | 0.1831 | 60.9192 | 61.0657 | 122.7081 | 123.0377 | -0.10986 | 122.9691 | 60.9467 | -0.3067 | 123.0377 | -0.10986 | 60.9467 | 122.7081 | 122.9691 | -123.2346 | -123.2483
1584.7812 | 123.1705 | -60.8551 | 62.0316 | -0.2787 | -0.0071478 | -0.0057891 | 7.0444e-05 | 0.059891 | -0.0047957 | 0.067411 | -60.9833 | 62.0544 | -61.1664 | -61.0703 | 61.908 | 0.14648 | -0.009155 | 0.27924 | 62.1002 | -61.1343 | -0.31128 | 0.022888 | -0.12817 | -0.21515 | -0.1236 | -0.27923 | 0.068665 | 0.18311 | 60.8459 | 61.1343 | 122.7631 | 122.9095 | -0.12817 | 122.9553 | 61.0016 | -0.27923 | 122.9095 | -0.12817 | 61.0016 | 122.7631 | 122.9553 | -123.1979 | -123.1659
1585.7812 | 123.2162 | -60.8871 | 61.972 | 0.43083 | -0.0062934 | -0.0070709 | 0.004343 | 0.062882 | -0.0058639 | 0.066556 | -61.0062 | 62.0819 | -61.1801 | -61.1023 | 61.8347 | 0.041199 | -0.19226 | 0.13733 | 62.0499 | -61.1755 | -0.29297 | 0.10986 | -0.11902 | -0.21515 | -0.13733 | -0.28839 | 0.07782 | 0.17395 | 60.6949 | 61.0245 | 122.7219 | 122.9691 | -0.11902 | 122.937 | 60.9283 | -0.28839 | 122.9691 | -0.11902 | 60.9283 | 122.7219 | 122.937 | -123.1522 | -123.1476
1586.7812 | 123.2208 | -60.8276 | 61.9995 | -0.065079 | -0.0067206 | -0.0087799 | -0.0016386 | 0.058823 | -0.0035141 | 0.069974 | -60.9787 | 62.059 | -61.1755 | -61.0474 | 61.9034 | 0.13733 | -0.086975 | 0.28839 | 62.0773 | -61.1069 | -0.3479 | 0.059509 | -0.15106 | -0.21973 | -0.096131 | -0.27924 | 0.07782 | 0.19684 | 60.7407 | 61.116 | 122.731 | 122.8867 | -0.15106 | 122.905 | 60.965 | -0.27924 | 122.8867 | -0.15106 | 60.965 | 122.731 | 122.905 | -123.175 | -123.1064
1587.7812 | 123.2162 | -60.8688 | 62.027 | 0.0035856 | -0.0094976 | -0.010703 | -0.00014316 | 0.057969 | -0.0052231 | 0.068052 | -61.0199 | 62.0407 | -61.1572 | -61.0748 | 61.8851 | 0.1236 | -0.064087 | 0.2655 | 62.0544 | -61.1252 | -0.28839 | 0.013732 | -0.15106 | -0.20599 | -0.14191 | -0.25635 | 0.027465 | 0.13733 | 60.8047 | 61.1343 | 122.7539 | 122.9095 | -0.15106 | 122.9233 | 60.9924 | -0.25635 | 122.9095 | -0.15106 | 60.9924 | 122.7539 | 122.9233 | -123.1842 | -123.1522
1588.7812 | 123.2117 | -60.8597 | 62.059 | -0.24055 | -0.0067206 | -0.0087799 | 0.0017794 | 0.059891 | -0.0080001 | 0.066129 | -61.0062 | 62.0819 | -61.171 | -61.0565 | 61.8896 | 0.14648 | -0.018311 | 0.28381 | 62.0636 | -61.1389 | -0.31128 | 0.022888 | -0.14649 | -0.19684 | -0.16937 | -0.27924 | 0.004578 | 0.16479 | 60.8414 | 61.1435 | 122.7493 | 122.9416 | -0.14649 | 122.9233 | 61.0062 | -0.27924 | 122.9416 | -0.14649 | 61.0062 | 122.7493 | 122.9233 | -123.23 | -123.1979
1589.7812 | 123.2208 | -60.8643 | 62.0544 | -0.11848 | -0.0073614 | -0.0096343 | 0.0041292 | 0.061814 | -0.0056503 | 0.065916 | -60.965 | 62.0682 | -61.116 | -61.0748 | 61.8942 | 0.16022 | -0.082397 | 0.27924 | 62.059 | -61.1343 | -0.25177 | 0.013733 | -0.10071 | -0.21057 | -0.16022 | -0.27008 | 0.004578 | 0.15106 | 60.7819 | 61.1435 | 122.7585 | 122.9324 | -0.10071 | 122.9233 | 61.0245 | -0.27008 | 122.9324 | -0.10071 | 61.0245 | 122.7585 | 122.9233 | -123.1705 | -123.1888
1590.7812 | 123.1613 | -60.8871 | 62.0361 | -0.087967 | -0.0052252 | -0.0098479 | 0.0092562 | 0.060105 | -0.0056503 | 0.065488 | -60.9695 | 62.1597 | -61.1572 | -61.084 | 61.821 | 0.054932 | 0.027466 | 0.17395 | 62.0956 | -61.203 | -0.27008 | 0.1236 | -0.082397 | -0.19684 | -0.21515 | -0.31586 | 0.059509 | 0.18768 | 60.9146 | 61.0611 | 122.7081 | 123.0469 | -0.082397 | 122.9828 | 60.9421 | -0.31586 | 123.0469 | -0.082397 | 60.9421 | 122.7081 | 122.9828 | -123.1934 | -123.2391
1591.7812 | 123.2254 | -60.8459 | 62.0316 | -0.019302 | -0.005866 | -0.0068573 | -0.002493 | 0.057542 | -0.0039413 | 0.068052 | -61.0245 | 62.0499 | -61.1755 | -61.0794 | 61.8805 | 0.10529 | -0.082397 | 0.22888 | 62.0499 | -61.1481 | -0.32959 | 0.018311 | -0.17853 | -0.23346 | -0.15106 | -0.30212 | 0.018311 | 0.15106 | 60.7636 | 61.0748 | 122.7264 | 122.8958 | -0.17853 | 122.8958 | 60.9512 | -0.30212 | 122.8958 | -0.17853 | 60.9512 | 122.7264 | 122.8958 | -123.2071 | -123.1796
1592.7812 | 123.1979 | -60.8368 | 62.0087 | -0.14137 | -0.0054388 | -0.013693 | -0.00057036 | 0.061814 | -0.0041549 | 0.069761 | -60.9695 | 62.0499 | -61.1343 | -61.0748 | 61.8439 | 0.1236 | -0.082397 | 0.25177 | 62.0453 | -61.1298 | -0.29755 | 0.041199 | -0.13275 | -0.23804 | -0.1648 | -0.29297 | 0.036621 | 0.16479 | 60.7544 | 61.0886 | 122.6807 | 122.8867 | -0.13275 | 122.8821 | 60.9604 | -0.29297 | 122.8867 | -0.13275 | 60.9604 | 122.6807 | 122.8821 | -123.143 | -123.1384
1593.7812 | 123.0927 | -60.9009 | 62.0956 | -0.17189 | -0.005866 | -0.0085663 | 0.005411 | 0.059251 | -0.0043685 | 0.063566 | -61.0565 | 62.1323 | -61.1984 | -60.9833 | 61.9354 | 0.009155 | 0.041199 | 0.1236 | 62.0956 | -61.1847 | -0.29755 | 0.036621 | -0.15564 | -0.082397 | -0.16022 | -0.28381 | 0 | 0.14191 | 60.9421 | 61.0245 | 122.8363 | 123.0331 | -0.15564 | 122.9965 | 60.91 | -0.28381 | 123.0331 | -0.15564 | 60.91 | 122.8363 | 122.9965 | -123.2941 | -123.2803
1594.7812 | 123.2071 | -60.8688 | 62.0453 | 0.07988 | -0.0067206 | -0.0049347 | -0.00035676 | 0.060319 | -0.0043685 | 0.069547 | -60.9558 | 62.027 | -61.1847 | -61.0565 | 61.9034 | 0.13733 | -0.022888 | 0.29755 | 62.0682 | -61.1298 | -0.31586 | -0.01831 | -0.086976 | -0.18768 | -0.14191 | -0.26093 | 0.022888 | 0.22888 | 60.8459 | 61.1664 | 122.7722 | 122.8958 | -0.086976 | 122.937 | 61.0062 | -0.26093 | 122.8958 | -0.086976 | 61.0062 | 122.7722 | 122.937 | -123.23 | -123.175
1595.7812 | 123.1338 | -60.9009 | 62.0132 | 0.018845 | -0.0022346 | -0.0070709 | 0.0084018 | 0.062028 | -0.0035141 | 0.065488 | -60.9787 | 62.1506 | -61.1572 | -61.1069 | 61.8164 | 0.018311 | 0.009155 | 0.12817 | 62.0911 | -61.203 | -0.25635 | 0.13733 | -0.07782 | -0.20599 | -0.19684 | -0.30212 | 0.077819 | 0.17853 | 60.91 | 61.0291 | 122.7173 | 123.0515 | -0.07782 | 122.9919 | 60.9192 | -0.30212 | 123.0515 | -0.07782 | 60.9192 | 122.7173 | 122.9919 | -123.1705 | -123.2162
1596.7812 | 123.175 | -60.8826 | 62.0178 | 0.1104 | -0.0067206 | -0.0083527 | -0.0020658 | 0.063309 | -0.0024459 | 0.067411 | -61.0565 | 62.0316 | -61.203 | -61.116 | 61.8576 | 0.054932 | -0.064087 | 0.16937 | 62.059 | -61.1526 | -0.32044 | 0.013733 | -0.17395 | -0.23346 | -0.16022 | -0.27008 | 0.041199 | 0.14648 | 60.8185 | 61.0519 | 122.7402 | 122.9141 | -0.17395 | 122.9416 | 60.9375 | -0.27008 | 122.9141 | -0.17395 | 60.9375 | 122.7402 | 122.9416 | -123.2208 | -123.1705
1597.7812 | 123.2391 | -60.8505 | 62.027 | -0.065079 | -0.0080024 | -0.0077117 | -0.0012112 | 0.059678 | -0.0065047 | 0.066343 | -60.965 | 62.0453 | -61.1481 | -61.0382 | 61.908 | 0.14191 | -0.091553 | 0.32044 | 62.0636 | -61.1069 | -0.29755 | 0.01831 | -0.11444 | -0.18768 | -0.11902 | -0.25635 | 0.036621 | 0.18311 | 60.759 | 61.171 | 122.7585 | 122.8958 | -0.11444 | 122.9141 | 60.9924 | -0.25635 | 122.8958 | -0.11444 | 60.9924 | 122.7585 | 122.9141 | -123.175 | -123.1339
1598.7812 | 123.1293 | -60.8871 | 62.0819 | -0.16426 | -0.0062934 | -0.0092071 | 0.0066928 | 0.061814 | -0.0067185 | 0.066343 | -61.0291 | 62.1002 | -61.171 | -61.1023 | 61.8301 | 0.041199 | 0.09613 | 0.16479 | 62.0819 | -61.1618 | -0.28381 | 0.018311 | -0.14191 | -0.21515 | -0.25177 | -0.27466 | 0 | 0.14191 | 60.9833 | 61.0519 | 122.7173 | 122.9874 | -0.14191 | 122.9691 | 60.9283 | -0.27466 | 122.9874 | -0.14191 | 60.9283 | 122.7173 | 122.9691 | -123.2529 | -123.2437
1599.7812 | 123.1888 | -60.878 | 61.9995 | 0.14854 | -0.0069342 | -0.0089935 | -0.00014316 | 0.061814 | -0.0028731 | 0.069333 | -61.0474 | 62.0316 | -61.1938 | -61.1343 | 61.8301 | 0.022888 | -0.09613 | 0.14648 | 62.0453 | -61.1435 | -0.31586 | 0.032043 | -0.16937 | -0.25635 | -0.16937 | -0.2655 | 0.045776 | 0.14649 | 60.7819 | 61.0245 | 122.7081 | 122.9095 | -0.16937 | 122.9233 | 60.9009 | -0.2655 | 122.9095 | -0.16937 | 60.9009 | 122.7081 | 122.9233 | -123.1934 | -123.143
1600.7812 | 123.1384 | -60.8917 | 62.0361 | -0.04219 | -0.005866 | -0.0094207 | 0.0079744 | 0.060746 | -0.0052231 | 0.066984 | -60.9879 | 62.1094 | -61.1755 | -61.084 | 61.8439 | 0.059509 | 0.018311 | 0.17395 | 62.0773 | -61.1526 | -0.28381 | 0.073242 | -0.09613 | -0.19226 | -0.19226 | -0.26092 | 0.041199 | 0.18768 | 60.91 | 61.0657 | 122.7356 | 123.0011 | -0.09613 | 122.9691 | 60.9512 | -0.26092 | 123.0011 | -0.09613 | 60.9512 | 122.7356 | 122.9691 | -123.2117 | -123.1888
1601.7812 | 123.2117 | -60.8917 | 61.9766 | 0.35454 | -0.006507 | -0.0025847 | 0.0051974 | 0.063309 | -0.0052231 | 0.067411 | -60.9879 | 62.0453 | -61.1801 | -61.0977 | 61.8347 | 0.036621 | -0.18768 | 0.13275 | 62.0132 | -61.1572 | -0.28839 | 0.068664 | -0.09613 | -0.20599 | -0.14191 | -0.2655 | 0.036621 | 0.19226 | 60.704 | 61.0245 | 122.7264 | 122.937 | -0.09613 | 122.905 | 60.9283 | -0.2655 | 122.937 | -0.09613 | 60.9283 | 122.7264 | 122.905 | -123.1567 | -123.1339
1602.7812 | 123.2117 | -60.9009 | 61.9858 | 0.27824 | -0.0060798 | -0.0072845 | 0.001993 | 0.06395 | -0.0058639 | 0.068052 | -60.9833 | 62.0453 | -61.1618 | -61.0886 | 61.853 | 0.15106 | -0.44403 | 0.059509 | 62.0041 | -61.171 | -0.26092 | 0.059509 | -0.082397 | -0.18768 | -0.13275 | -0.27008 | 0.01831 | 0.17853 | 60.4568 | 60.9604 | 122.7539 | 122.9462 | -0.082397 | 122.905 | 61.0519 | -0.27008 | 122.9462 | -0.082397 | 61.0519 | 122.7539 | 122.905 | -123.1476 | -123.1567
1603.7812 | 123.1613 | -60.8917 | 61.9995 | 0.18669 | -0.0052252 | -0.012198 | 0.00071144 | 0.059678 | -0.0047957 | 0.068479 | -61.0153 | 62.0865 | -61.1847 | -61.1389 | 61.8118 | 0.009155 | -0.10529 | 0.12817 | 62.0682 | -61.171 | -0.29297 | 0.086975 | -0.1236 | -0.24719 | -0.18768 | -0.27923 | 0.068664 | 0.16937 | 60.7864 | 61.0199 | 122.7036 | 122.9782 | -0.1236 | 122.9599 | 60.9009 | -0.27923 | 122.9782 | -0.1236 | 60.9009 | 122.7036 | 122.9599 | -123.1842 | -123.1705
1604.7812 | 123.1613 | -60.878 | 61.9995 | 0.20195 | -0.005866 | -0.0092071 | 0.00028404 | 0.061387 | -0.0041549 | 0.068906 | -61.0107 | 62.0316 | -61.1801 | -61.1343 | 61.821 | 0.018311 | -0.15106 | 0.14191 | 62.027 | -61.1572 | -0.30212 | 0.032043 | -0.13275 | -0.25635 | -0.17853 | -0.27924 | 0.027466 | 0.16937 | 60.7269 | 61.0199 | 122.699 | 122.9095 | -0.13275 | 122.905 | 60.8963 | -0.27924 | 122.9095 | -0.13275 | 60.8963 | 122.699 | 122.905 | -123.1796 | -123.1567
1605.7812 | 123.1705 | -60.8963 | 61.9949 | 0.1638 | -0.008216 | -0.0081389 | -0.00078396 | 0.06096 | -0.0080001 | 0.069761 | -61.0611 | 62.0316 | -61.1801 | -61.1343 | 61.8073 | 0.018311 | -0.09613 | 0.14191 | 62.0361 | -61.1435 | -0.28381 | 0.036621 | -0.16479 | -0.23804 | -0.18768 | -0.24719 | 0.041199 | 0.11902 | 60.8002 | 61.0382 | 122.7036 | 122.9279 | -0.16479 | 122.9324 | 60.9146 | -0.24719 | 122.9279 | -0.16479 | 60.9146 | 122.7036 | 122.9324 | -123.175 | -123.1384
1606.7812 | 123.23 | -60.8597 | 62.0224 | 0.28587 | -0.0037298 | -0.0053619 | 0.0051974 | 0.061814 | -0.0054367 | 0.066556 | -60.9695 | 62.0819 | -61.1618 | -61.0931 | 61.8393 | 0.045776 | -0.18768 | 0.13733 | 62.0316 | -61.1801 | -0.30212 | 0.059509 | -0.10986 | -0.23346 | -0.18311 | -0.32044 | 0.009155 | 0.19226 | 60.672 | 60.997 | 122.699 | 122.9416 | -0.10986 | 122.8912 | 60.9055 | -0.32044 | 122.9416 | -0.10986 | 60.9055 | 122.699 | 122.8912 | -123.1842 | -123.2025
1607.7812 | 123.143 | -60.8826 | 62.0087 | 0.75127 | -0.0060798 | -0.0092071 | 0.00049764 | 0.060105 | -0.0056503 | 0.070829 | -61.0382 | 62.0544 | -61.1893 | -61.1206 | 61.8347 | 0.013733 | -0.091553 | 0.11902 | 62.0132 | -61.1481 | -0.3067 | 0.045776 | -0.15564 | -0.23804 | -0.17395 | -0.2655 | 0.004578 | 0.15106 | 60.791 | 61.0016 | 122.7173 | 122.937 | -0.15564 | 122.8958 | 60.8963 | -0.2655 | 122.937 | -0.15564 | 60.8963 | 122.7173 | 122.8958 | -123.1979 | -123.1567
1608.7656 | 123.2437 | -60.8688 | 62.0316 | -0.0040434 | -0.0052252 | -0.010916 | 7.0444e-05 | 0.060532 | -0.0039413 | 0.067838 | -60.965 | 62.0911 | -61.1435 | -61.0474 | 61.8896 | 0.14191 | -0.086975 | 0.25635 | 62.0224 | -61.1801 | -0.27466 | 0.059509 | -0.096131 | -0.17853 | -0.14191 | -0.31128 | -0.009155 | 0.17853 | 60.7819 | 61.1252 | 122.7585 | 122.9599 | -0.096131 | 122.8912 | 61.0107 | -0.31128 | 122.9599 | -0.096131 | 61.0107 | 122.7585 | 122.8912 | -123.175 | -123.2117
1609.7812 | 123.2162 | -60.8871 | 61.9858 | 0.25536 | -0.005866 | -0.0079253 | 0.0051974 | 0.06096 | -0.0058639 | 0.06677 | -60.9833 | 62.0224 | -61.1938 | -61.0794 | 61.8622 | 0.041199 | -0.20142 | 0.16022 | 62.0224 | -61.171 | -0.3067 | 0.036621 | -0.09613 | -0.19226 | -0.1236 | -0.28381 | 0.036621 | 0.21057 | 60.6857 | 61.0474 | 122.7493 | 122.9095 | -0.09613 | 122.9095 | 60.9283 | -0.28381 | 122.9095 | -0.09613 | 60.9283 | 122.7493 | 122.9095 | -123.1796 | -123.1567
1610.7812 | 123.1613 | -60.9146 | 61.9949 | 0.2401 | -0.0090704 | -0.0074981 | 0.0034884 | 0.059678 | -0.0075729 | 0.06677 | -60.9924 | 62.0544 | -61.2122 | -61.0977 | 61.8347 | 0.022888 | -0.1831 | 0.15106 | 62.0178 | -61.1572 | -0.29755 | 0.059509 | -0.07782 | -0.18311 | -0.16022 | -0.24262 | 0.022888 | 0.21973 | 60.7315 | 61.0657 | 122.7493 | 122.9691 | -0.07782 | 122.9324 | 60.9375 | -0.24262 | 122.9691 | -0.07782 | 60.9375 | 122.7493 | 122.9324 | -123.2071 | -123.1522
1611.7812 | 123.1979 | -60.8826 | 62.0041 | 0.23247 | -0.0041572 | -0.0062163 | 0.0030612 | 0.060746 | -0.0052231 | 0.066556 | -60.997 | 62.0407 | -61.1938 | -61.0886 | 61.853 | 0.036621 | -0.18768 | 0.15106 | 62.0132 | -61.1572 | -0.31128 | 0.036621 | -0.11444 | -0.20599 | -0.15106 | -0.27466 | 0.009156 | 0.19684 | 60.6949 | 61.0336 | 122.7356 | 122.9233 | -0.11444 | 122.8958 | 60.9192 | -0.27466 | 122.9233 | -0.11444 | 60.9192 | 122.7356 | 122.8958 | -123.1979 | -123.1613
1612.7812 | 123.2025 | -60.8826 | 61.9949 | 0.6292 | -0.0045844 | -0.0074981 | 0.0073336 | 0.061814 | -0.0039413 | 0.06912 | -60.9604 | 62.0956 | -61.1481 | -61.084 | 61.8347 | 0.045776 | -0.20142 | 0.13275 | 61.9858 | -61.1801 | -0.2655 | 0.10071 | -0.07782 | -0.20142 | -0.16022 | -0.29755 | -0.009155 | 0.18768 | 60.6812 | 61.0153 | 122.7173 | 122.9782 | -0.07782 | 122.8683 | 60.9283 | -0.29755 | 122.9782 | -0.07782 | 60.9283 | 122.7173 | 122.8683 | -123.143 | -123.175
1613.7812 | 123.1979 | -60.8643 | 62.0178 | 0.39269 | -0.0077888 | -0.0066437 | 0.001993 | 0.059251 | -0.0030869 | 0.067838 | -61.0291 | 62.1002 | -61.1389 | -61.0794 | 61.8759 | 0.09613 | -0.068665 | 0.21973 | 62.0544 | -61.1984 | -0.27466 | 0.082398 | -0.16479 | -0.21515 | -0.14191 | -0.33417 | 0.036621 | 0.10986 | 60.7956 | 61.084 | 122.7402 | 122.9645 | -0.16479 | 122.9187 | 60.9604 | -0.33417 | 122.9645 | -0.16479 | 60.9604 | 122.7402 | 122.9187 | -123.1567 | -123.2162
1614.7812 | 123.2025 | -60.8826 | 62.0087 | 0.43083 | -0.0060798 | -0.0087799 | 0.0028476 | 0.059891 | -0.0024459 | 0.06677 | -60.997 | 62.0865 | -61.1755 | -61.1298 | 61.8256 | 0.013733 | -0.11902 | 0.1236 | 62.0087 | -61.1938 | -0.29297 | 0.07782 | -0.11444 | -0.24719 | -0.18311 | -0.31128 | 0 | 0.17853 | 60.7635 | 61.0062 | 122.7081 | 122.9691 | -0.11444 | 122.8912 | 60.8963 | -0.31128 | 122.9691 | -0.11444 | 60.8963 | 122.7081 | 122.8912 | -123.1842 | -123.2025
1615.7812 | 123.0835 | -60.9512 | 62.0224 | 0.23247 | -0.004798 | -0.0057891 | 0.010111 | 0.062669 | -0.0024459 | 0.066343 | -61.0657 | 62.1552 | -61.1938 | -61.1572 | 61.7386 | -0.064087 | -0.022888 | 0.027466 | 62.059 | -61.2167 | -0.24262 | 0.13275 | -0.11444 | -0.20599 | -0.28381 | -0.2655 | 0.036621 | 0.12817 | 60.9283 | 60.9787 | 122.6898 | 123.1064 | -0.11444 | 123.0103 | 60.8871 | -0.2655 | 123.1064 | -0.11444 | 60.8871 | 122.6898 | 123.0103 | -123.2162 | -123.2391
1616.7812 | 123.1064 | -60.9375 | 62.0316 | 0.20195 | -0.004798 | -0.0081389 | 0.0066928 | 0.063523 | -0.0026595 | 0.069333 | -61.0611 | 62.1597 | -61.2213 | -61.171 | 61.7615 | -0.054932 | -0.041199 | 0.045776 | 62.0636 | -61.2442 | -0.28381 | 0.12817 | -0.1236 | -0.23346 | -0.27008 | -0.3067 | 0.032044 | 0.16022 | 60.8963 | 60.9833 | 122.699 | 123.0972 | -0.1236 | 123.0011 | 60.8826 | -0.3067 | 123.0972 | -0.1236 | 60.8826 | 122.699 | 123.0011 | -123.2529 | -123.2758
1617.7812 | 123.1934 | -60.8917 | 62.0224 | 0.049362 | -0.0080024 | -0.0083527 | -0.00057036 | 0.061814 | -0.0033005 | 0.067838 | -61.0428 | 62.1368 | -61.1755 | -61.1114 | 61.8622 | 0.086975 | -0.068665 | 0.20142 | 62.0407 | -61.2122 | -0.28381 | 0.11444 | -0.15106 | -0.21973 | -0.16022 | -0.32043 | 0.01831 | 0.13275 | 60.8231 | 61.0931 | 122.7539 | 123.0286 | -0.15106 | 122.9324 | 60.9787 | -0.32043 | 123.0286 | -0.15106 | 60.9787 | 122.7539 | 122.9324 | -123.1979 | -123.2346
1618.7812 | 123.1934 | -60.91 | 62.0132 | 0.1638 | -0.0052252 | -0.0074981 | 0.0032748 | 0.060105 | -0.0033005 | 0.06677 | -61.0199 | 62.0956 | -61.1893 | -61.1069 | 61.8484 | 0.041199 | -0.17853 | 0.15564 | 62.027 | -61.203 | -0.27924 | 0.082397 | -0.10986 | -0.19684 | -0.16479 | -0.29297 | 0.013733 | 0.16937 | 60.7315 | 61.0657 | 122.7585 | 123.0057 | -0.10986 | 122.937 | 60.9512 | -0.29297 | 123.0057 | -0.10986 | 60.9512 | 122.7585 | 122.937 | -123.2025 | -123.2162
1619.7812 | 123.0972 | -60.9421 | 62.0316 | -0.11848 | -0.0037298 | -0.0015167 | 0.0079744 | 0.063523 | -0.0035141 | 0.06912 | -61.0382 | 62.1872 | -61.1847 | -61.1847 | 61.7615 | -0.041199 | -0.036621 | 0.059509 | 62.0316 | -61.235 | -0.24261 | 0.15564 | -0.09613 | -0.24261 | -0.27008 | -0.29297 | 0 | 0.14648 | 60.9055 | 61.0016 | 122.7036 | 123.1293 | -0.09613 | 122.9736 | 60.9009 | -0.29297 | 123.1293 | -0.09613 | 60.9009 | 122.7036 | 122.9736 | -123.2162 | -123.2666
1620.7812 | 123.1201 | -60.91 | 62.0224 | 0.23247 | -0.004798 | -0.0055755 | 0.0060518 | 0.065018 | -0.0033005 | 0.067624 | -61.0382 | 62.1597 | -61.2167 | -61.1664 | 61.7889 | -0.036621 | -0.082397 | 0.054932 | 62.0499 | -61.2122 | -0.3067 | 0.13733 | -0.12817 | -0.25635 | -0.23346 | -0.30212 | 0.027466 | 0.17853 | 60.8276 | 60.965 | 122.699 | 123.0698 | -0.12817 | 122.9599 | 60.8734 | -0.30212 | 123.0698 | -0.12817 | 60.8734 | 122.699 | 122.9599 | -123.2391 | -123.2346
1621.7812 | 123.1934 | -60.9192 | 61.9904 | 0.26299 | -0.0062934 | -0.0060027 | 0.004343 | 0.064164 | -0.0039413 | 0.066984 | -61.0199 | 62.1277 | -61.1801 | -61.1114 | 61.821 | 0.013733 | -0.14648 | 0.11902 | 62.0361 | -61.1847 | -0.26093 | 0.13733 | -0.10071 | -0.19226 | -0.16937 | -0.2655 | 0.045777 | 0.16022 | 60.7727 | 61.0382 | 122.7402 | 123.0469 | -0.10071 | 122.9553 | 60.9329 | -0.2655 | 123.0469 | -0.10071 | 60.9329 | 122.7402 | 122.9553 | -123.1705 | -123.175
1622.7812 | 123.2437 | -60.9238 | 61.9492 | 0.24773 | -0.0050116 | -0.0060027 | 0.0022066 | 0.062669 | -0.0026595 | 0.06912 | -60.997 | 62.0773 | -61.1664 | -61.0977 | 61.8668 | 0.050354 | -0.17853 | 0.14648 | 62.0178 | -61.1893 | -0.24262 | 0.12817 | -0.073242 | -0.17395 | -0.082398 | -0.2655 | 0.068664 | 0.16937 | 60.7452 | 61.0703 | 122.7905 | 123.0011 | -0.073242 | 122.9416 | 60.9741 | -0.2655 | 123.0011 | -0.073242 | 60.9741 | 122.7905 | 122.9416 | -123.1155 | -123.1384
1623.7656 | 123.0927 | -60.9146 | 62.0316 | 0.15617 | -0.004798 | -0.0070709 | 0.0077608 | 0.061173 | -0.0024459 | 0.067838 | -61.0703 | 62.1689 | -61.2167 | -61.203 | 61.7569 | -0.054932 | 0.013733 | 0.032043 | 62.0544 | -61.2213 | -0.30212 | 0.13733 | -0.15564 | -0.28839 | -0.27466 | -0.3067 | 0.022888 | 0.14648 | 60.9283 | 60.9467 | 122.6715 | 123.0835 | -0.15564 | 122.9691 | 60.8597 | -0.3067 | 123.0835 | -0.15564 | 60.8597 | 122.6715 | 122.9691 | -123.2483 | -123.2529
1624.7656 | 123.1338 | -60.9192 | 61.9949 | 0.2401 | -0.0039434 | -0.0077117 | 0.0066928 | 0.062241 | -0.0047957 | 0.067624 | -61.0519 | 62.1506 | -61.2259 | -61.1572 | 61.7981 | 0 | -0.054932 | 0.082397 | 62.059 | -61.2167 | -0.3067 | 0.15564 | -0.13275 | -0.23804 | -0.19684 | -0.29755 | 0.064087 | 0.17395 | 60.8643 | 61.0016 | 122.7173 | 123.0698 | -0.13275 | 122.9782 | 60.9192 | -0.29755 | 123.0698 | -0.13275 | 60.9192 | 122.7173 | 122.9782 | -123.2208 | -123.2117
1625.7812 | 123.2025 | -60.8871 | 61.9949 | 0.20958 | -0.0050116 | -0.0057891 | 0.0030612 | 0.062882 | -0.0041549 | 0.065916 | -61.0062 | 62.1368 | -61.1938 | -61.1023 | 61.8439 | 0.032043 | -0.1831 | 0.15106 | 62.0178 | -61.1755 | -0.3067 | 0.14191 | -0.11902 | -0.21515 | -0.15106 | -0.28839 | 0.022888 | 0.18768 | 60.704 | 61.0382 | 122.731 | 123.024 | -0.11902 | 122.905 | 60.9192 | -0.28839 | 123.024 | -0.11902 | 60.9192 | 122.731 | 122.905 | -123.1888 | -123.1705
1626.7812 | 123.2162 | -60.8734 | 61.9949 | 0.27061 | -0.0024482 | -0.0055755 | 0.00049764 | 0.06395 | -0.0058639 | 0.068479 | -60.9879 | 62.0865 | -61.1755 | -61.0931 | 61.8622 | 0.059509 | -0.19226 | 0.15106 | 62.027 | -61.1664 | -0.30212 | 0.091553 | -0.11444 | -0.21973 | -0.13275 | -0.29297 | 0.032044 | 0.18768 | 60.6812 | 61.0245 | 122.7356 | 122.9599 | -0.11444 | 122.9004 | 60.9329 | -0.29297 | 122.9599 | -0.11444 | 60.9329 | 122.7356 | 122.9004 | -123.1705 | -123.1613
1627.7656 | 123.1842 | -60.9009 | 62.0041 | 0.23247 | -0.009925 | -0.01113 | -0.0012112 | 0.06096 | -0.0041549 | 0.067838 | -61.0153 | 62.059 | -61.1618 | -61.1114 | 61.8347 | 0.041199 | -0.15106 | 0.091553 | 62.0224 | -61.1893 | -0.26092 | 0.054932 | -0.11444 | -0.21057 | -0.16937 | -0.28839 | 0.018311 | 0.14648 | 60.7498 | 60.9924 | 122.7356 | 122.9599 | -0.11444 | 122.9233 | 60.9421 | -0.28839 | 122.9599 | -0.11444 | 60.9421 | 122.7356 | 122.9233 | -123.1659 | -123.1934
1628.7656 | 123.0881 | -60.9192 | 62.0361 | 0.11803 | -0.0054388 | -0.0083527 | 0.0075472 | 0.064591 | -0.0052231 | 0.064847 | -61.0336 | 62.1414 | -61.2122 | -61.203 | 61.7752 | -0.004578 | 0.050354 | 0.09613 | 62.0819 | -61.2259 | -0.29297 | 0.10529 | -0.11444 | -0.28381 | -0.26093 | -0.3067 | 0.045776 | 0.17853 | 60.9695 | 61.0153 | 122.6944 | 123.0606 | -0.11444 | 123.0011 | 60.9146 | -0.3067 | 123.0606 | -0.11444 | 60.9146 | 122.6944 | 123.0011 | -123.2483 | -123.262
1629.7656 | 123.1522 | -60.9146 | 61.9949 | 0.25536 | -0.0050116 | -0.011343 | 0.003702 | 0.061387 | -0.0043685 | 0.068693 | -61.0657 | 62.0956 | -61.1893 | -61.1618 | 61.7889 | -0.036621 | -0.09613 | 0.068665 | 62.0453 | -61.1893 | -0.27466 | 0.10071 | -0.15106 | -0.24719 | -0.20599 | -0.27466 | 0.050354 | 0.1236 | 60.8185 | 60.9833 | 122.7036 | 123.0103 | -0.15106 | 122.9599 | 60.878 | -0.27466 | 123.0103 | -0.15106 | 60.878 | 122.7036 | 122.9599 | -123.1842 | -123.1842
1630.7812 | 123.0469 | -60.9375 | 62.0361 | 0.064621 | -0.0028754 | -0.0098479 | 0.0049838 | 0.064591 | -0.0039413 | 0.070402 | -61.0428 | 62.1414 | -61.1801 | -61.1984 | 61.7432 | -0.054932 | 0.022888 | 0.054932 | 62.0682 | -61.2213 | -0.24262 | 0.10529 | -0.10529 | -0.26093 | -0.29297 | -0.28381 | 0.032043 | 0.13733 | 60.9604 | 60.9924 | 122.6807 | 123.0789 | -0.10529 | 123.0057 | 60.8826 | -0.28381 | 123.0789 | -0.10529 | 60.8826 | 122.6807 | 123.0057 | -123.2162 | -123.2574
1631.7812 | 123.1293 | -60.9192 | 61.9858 | 0.25536 | -0.0035162 | -0.0079253 | 0.0032748 | 0.064164 | -0.0037277 | 0.06677 | -61.0748 | 62.1323 | -61.2122 | -61.1801 | 61.7844 | -0.036621 | -0.073242 | 0.045776 | 62.0682 | -61.1893 | -0.29297 | 0.14648 | -0.15564 | -0.26093 | -0.20142 | -0.27008 | 0.082397 | 0.13733 | 60.8459 | 60.965 | 122.7036 | 123.0515 | -0.15564 | 122.9874 | 60.8826 | -0.27008 | 123.0515 | -0.15564 | 60.8826 | 122.7036 | 122.9874 | -123.1979 | -123.175
1632.7656 | 123.1476 | -60.8963 | 62.0132 | 0.27824 | -0.003089 | -0.0072845 | 0.004343 | 0.065018 | -0.0039413 | 0.066343 | -61.0657 | 62.1094 | -61.2122 | -61.1664 | 61.7935 | -0.018311 | -0.10986 | 0.073242 | 62.0544 | -61.1847 | -0.31586 | 0.09613 | -0.16937 | -0.27008 | -0.21973 | -0.28839 | 0.041198 | 0.14648 | 60.7864 | 60.9695 | 122.6898 | 123.0057 | -0.16937 | 122.9507 | 60.878 | -0.28839 | 123.0057 | -0.16937 | 60.878 | 122.6898 | 122.9507 | -123.2254 | -123.1979
1633.7656 | 123.0652 | -60.9146 | 62.0499 | 0.17143 | -0.0062934 | -0.0081389 | 0.0039156 | 0.064805 | -0.0052231 | 0.066556 | -61.0474 | 62.1185 | -61.2076 | -61.1801 | 61.7661 | -0.036621 | 0.022888 | 0.073242 | 62.114 | -61.1847 | -0.29297 | 0.068664 | -0.13275 | -0.2655 | -0.28381 | -0.27008 | 0.064087 | 0.16022 | 60.9375 | 60.9879 | 122.6807 | 123.0331 | -0.13275 | 123.0286 | 60.878 | -0.27008 | 123.0331 | -0.13275 | 60.878 | 122.6807 | 123.0286 | -123.2574 | -123.2346
1634.7656 | 123.1934 | -60.9055 | 61.9904 | 0.25536 | -0.0062934 | -0.0092071 | 0.001993 | 0.063096 | -0.0058639 | 0.067838 | -61.0336 | 62.0819 | -61.1938 | -61.1481 | 61.7981 | -0.004578 | -0.13275 | 0.1236 | 62.0361 | -61.1755 | -0.28839 | 0.091553 | -0.12817 | -0.24261 | -0.19226 | -0.27008 | 0.045777 | 0.16022 | 60.7727 | 61.0291 | 122.7036 | 122.9874 | -0.12817 | 122.9416 | 60.9009 | -0.27008 | 122.9874 | -0.12817 | 60.9009 | 122.7036 | 122.9416 | -123.1842 | -123.1659
1635.7656 | 123.0881 | -60.9192 | 62.0682 | 0.07988 | -0.0067206 | -0.0060027 | 0.0051974 | 0.063309 | -0.0065047 | 0.066984 | -61.0199 | 62.1048 | -61.1801 | -61.1343 | 61.8073 | 0.018311 | 0.013733 | 0.10071 | 62.0956 | -61.1984 | -0.26093 | 0.036621 | -0.10071 | -0.21515 | -0.26093 | -0.27924 | 0.027466 | 0.16022 | 60.9329 | 61.0199 | 122.7264 | 123.024 | -0.10071 | 123.0148 | 60.9375 | -0.27924 | 123.024 | -0.10071 | 60.9375 | 122.7264 | 123.0148 | -123.2483 | -123.2666
1636.7656 | 123.0972 | -60.8871 | 62.0361 | 0.026474 | -0.0043708 | -0.0040801 | 0.0045566 | 0.06395 | -0.0069321 | 0.070188 | -61.0199 | 62.1048 | -61.2076 | -61.1435 | 61.7981 | 0.018311 | 0.032043 | 0.11902 | 62.1185 | -61.1801 | -0.32043 | 0.068664 | -0.13275 | -0.25635 | -0.23804 | -0.29297 | 0.082397 | 0.18768 | 60.9192 | 61.0062 | 122.6852 | 122.9919 | -0.13275 | 123.0057 | 60.9055 | -0.29297 | 122.9919 | -0.13275 | 60.9055 | 122.6852 | 123.0057 | -123.2437 | -123.2162
1637.7656 | 123.1522 | -60.8871 | 62.0224 | 0.034104 | -0.007575 | -0.0094207 | -0.0035612 | 0.062028 | -0.0050095 | 0.067411 | -61.0611 | 62.0819 | -61.1618 | -61.1664 | 61.8301 | 0.036621 | -0.059509 | 0.16937 | 62.0865 | -61.1526 | -0.27466 | 0.059509 | -0.17395 | -0.27924 | -0.19226 | -0.2655 | 0.064087 | 0.10071 | 60.8276 | 61.0565 | 122.7173 | 122.9691 | -0.17395 | 122.9736 | 60.9238 | -0.2655 | 122.9691 | -0.17395 | 60.9238 | 122.7173 | 122.9736 | -123.1842 | -123.175
1638.7656 | 123.1201 | -60.91 | 62.0682 | -0.011673 | -0.005866 | -0.0094207 | 0.0058382 | 0.064164 | -0.0039413 | 0.06912 | -61.0016 | 62.1323 | -61.1893 | -61.1389 | 61.8256 | 0.073242 | 0.050354 | 0.19684 | 62.0956 | -61.1847 | -0.27924 | 0.064087 | -0.091553 | -0.22888 | -0.24261 | -0.27466 | 0.027466 | 0.18768 | 60.9604 | 61.1069 | 122.7356 | 123.0423 | -0.091553 | 123.0057 | 60.9833 | -0.27466 | 123.0423 | -0.091553 | 60.9833 | 122.7356 | 123.0057 | -123.2574 | -123.2529
1639.7656 | 123.0835 | -60.91 | 62.0316 | 0.20195 | -0.0028754 | -0.0077117 | 0.0056246 | 0.065018 | -0.0060775 | 0.068479 | -61.084 | 62.1094 | -61.2259 | -61.2076 | 61.7569 | -0.068665 | -0.004578 | 0.022888 | 62.1048 | -61.1801 | -0.31586 | 0.07782 | -0.17395 | -0.29755 | -0.27466 | -0.27008 | 0.073242 | 0.14191 | 60.9055 | 60.9329 | 122.6669 | 123.0194 | -0.17395 | 123.0148 | 60.8414 | -0.27008 | 123.0194 | -0.17395 | 60.8414 | 122.6669 | 123.0148 | -123.2574 | -123.2117
1640.7656 | 123.1293 | -60.8963 | 62.0636 | -0.12611 | -0.0045844 | -0.0066437 | 0.0039156 | 0.064378 | -0.0043685 | 0.066129 | -61.0062 | 62.1323 | -61.2167 | -61.0977 | 61.8896 | 0.091553 | 0.041199 | 0.16022 | 62.1094 | -61.1435 | -0.32043 | 0.068664 | -0.10986 | -0.20142 | -0.17395 | -0.24719 | 0.045776 | 0.21057 | 60.9375 | 61.0565 | 122.7859 | 123.0286 | -0.10986 | 123.0057 | 60.9879 | -0.24719 | 123.0286 | -0.10986 | 60.9879 | 122.7859 | 123.0057 | -123.2803 | -123.2071
1641.7656 | 123.1705 | -60.878 | 62.0407 | -0.19478 | -0.0056524 | -0.0085663 | -0.0044156 | 0.062455 | -0.0065047 | 0.06677 | -61.0062 | 62.0819 | -61.1664 | -61.1069 | 61.8576 | 0.018311 | 0.21057 | 0.30212 | 62.114 | -61.1526 | -0.28839 | 0.041199 | -0.12817 | -0.22888 | -0.1831 | -0.27466 | 0.073243 | 0.16022 | 61.0886 | 61.1801 | 122.7356 | 122.9599 | -0.12817 | 122.9919 | 60.8963 | -0.27466 | 122.9599 | -0.12817 | 60.8963 | 122.7356 | 122.9919 | -123.2071 | -123.1934
1642.7656 | 123.1476 | -60.8871 | 62.0361 | -0.095596 | -0.0050116 | -0.0083527 | 0.0045566 | 0.062455 | -0.0056503 | 0.067197 | -61.0016 | 62.1277 | -61.1938 | -61.116 | 61.8256 | 0.068665 | 0.054932 | 0.17853 | 62.114 | -61.1618 | -0.3067 | 0.091553 | -0.11444 | -0.22888 | -0.21057 | -0.27466 | 0.07782 | 0.19226 | 60.9421 | 61.0657 | 122.7127 | 123.0148 | -0.11444 | 123.0011 | 60.9558 | -0.27466 | 123.0148 | -0.11444 | 60.9558 | 122.7127 | 123.0011 | -123.23 | -123.1979
1643.7656 | 123.1155 | -60.8963 | 62.0819 | -0.17952 | -0.0039434 | -0.0079253 | 0.002634 | 0.060746 | -0.0050095 | 0.068265 | -61.0611 | 62.146 | -61.1755 | -61.1526 | 61.7889 | 0.041199 | 0.13733 | 0.16479 | 62.114 | -61.171 | -0.27924 | 0.064087 | -0.16479 | -0.25635 | -0.29297 | -0.27466 | 0.032044 | 0.11444 | 61.0336 | 61.0611 | 122.6852 | 123.0423 | -0.16479 | 123.0103 | 60.9375 | -0.27466 | 123.0423 | -0.16479 | 60.9375 | 122.6852 | 123.0103 | -123.2574 | -123.2529
1644.7656 | 123.111 | -60.9055 | 62.0728 | -0.149 | -0.005866 | -0.0094207 | 0.0024202 | 0.061387 | -0.0022323 | 0.065916 | -61.0565 | 62.1231 | -61.1755 | -61.171 | 61.8073 | 0.032043 | 0.13275 | 0.16022 | 62.1277 | -61.1526 | -0.27008 | 0.050354 | -0.15106 | -0.2655 | -0.2655 | -0.24719 | 0.054932 | 0.11902 | 61.0382 | 61.0657 | 122.7127 | 123.0286 | -0.15106 | 123.0331 | 60.9375 | -0.24719 | 123.0286 | -0.15106 | 60.9375 | 122.7127 | 123.0331 | -123.2483 | -123.2254
1645.7656 | 123.1293 | -60.9055 | 62.0682 | -0.149 | -0.0077888 | -0.011343 | 0.0015658 | 0.06096 | -0.0056503 | 0.06677 | -61.0291 | 62.1368 | -61.1893 | -61.0886 | 61.7752 | 0.036621 | 0.036621 | 0.16479 | 62.1323 | -61.1755 | -0.28381 | 0.068665 | -0.1236 | -0.18311 | -0.29297 | -0.27008 | 0.064087 | 0.16022 | 60.9421 | 61.0703 | 122.6807 | 123.0423 | -0.1236 | 123.0377 | 60.9421 | -0.27008 | 123.0423 | -0.1236 | 60.9421 | 122.6807 | 123.0377 | -123.2574 | -123.2437
1646.7656 | 123.1384 | -60.8917 | 62.0316 | -0.10323 | -0.005866 | -0.0049347 | 0.0039156 | 0.062455 | -0.0045821 | 0.068052 | -61.0199 | 62.114 | -61.203 | -61.1114 | 61.8393 | 0.073242 | 0.059509 | 0.18768 | 62.1094 | -61.1481 | -0.31128 | 0.082398 | -0.12817 | -0.21973 | -0.19226 | -0.25635 | 0.07782 | 0.18311 | 60.9512 | 61.0794 | 122.731 | 123.0057 | -0.12817 | 123.0011 | 60.965 | -0.25635 | 123.0057 | -0.12817 | 60.965 | 122.731 | 123.0011 | -123.2346 | -123.1796
1647.7656 | 123.1201 | -60.8871 | 62.0773 | -0.10323 | -0.0050116 | -0.0096343 | 0.0028476 | 0.062241 | -0.0050095 | 0.068479 | -61.0428 | 62.114 | -61.171 | -61.1114 | 61.821 | 0.07782 | 0.07782 | 0.19226 | 62.1002 | -61.1618 | -0.28381 | 0.036621 | -0.15564 | -0.2243 | -0.25635 | -0.27466 | 0.022888 | 0.12817 | 60.965 | 61.0794 | 122.7081 | 123.0011 | -0.15564 | 122.9874 | 60.965 | -0.27466 | 123.0011 | -0.15564 | 60.965 | 122.7081 | 122.9874 | -123.2483 | -123.2391
1648.7656 | 123.1293 | -60.8643 | 62.0453 | -0.19478 | -0.0071478 | -0.010916 | -0.00014316 | 0.063309 | -0.0052231 | 0.065916 | -61.0153 | 62.0865 | -61.1847 | -61.1023 | 61.853 | 0.10071 | 0.054932 | 0.24719 | 62.0956 | -61.1435 | -0.32043 | 0.041199 | -0.15106 | -0.23804 | -0.19226 | -0.27924 | 0.050354 | 0.16937 | 60.9192 | 61.1114 | 122.7173 | 122.9507 | -0.15106 | 122.9599 | 60.965 | -0.27924 | 122.9507 | -0.15106 | 60.965 | 122.7173 | 122.9599 | -123.23 | -123.1888
1649.7656 | 123.1613 | -60.8871 | 62.0316 | -0.149 | -0.007575 | -0.013907 | -0.0012112 | 0.063737 | -0.0060775 | 0.067838 | -60.8231 | 62.114 | -61.1114 | -61.1114 | 61.8484 | 0.11444 | 0.018311 | 0.24719 | 62.0865 | -61.1389 | -0.2243 | 0.082398 | 0.064087 | -0.2243 | -0.1831 | -0.25177 | 0.054932 | 0.28839 | 60.9055 | 61.1343 | 122.7356 | 123.0011 | 0.064087 | 122.9736 | 61.0016 | -0.25177 | 123.0011 | 0.064087 | 61.0016 | 122.7356 | 122.9736 | -123.143 | -123.1705
1650.7812 | 123.1064 | -60.8826 | 62.0682 | -0.19478 | -0.0054388 | -0.0077117 | -0.00035676 | 0.060746 | -0.0073593 | 0.067411 | -61.0153 | 62.0819 | -61.1572 | -61.1298 | 61.8164 | 0.07782 | 0.086975 | 0.2243 | 62.1185 | -61.1481 | -0.27466 | 0.013733 | -0.13275 | -0.24719 | -0.25177 | -0.2655 | 0.050354 | 0.14191 | 60.9695 | 61.1069 | 122.699 | 122.9645 | -0.13275 | 123.0011 | 60.9604 | -0.2655 | 122.9645 | -0.13275 | 60.9604 | 122.699 | 123.0011 | -123.2254 | -123.2162
1651.7812 | 123.0743 | -60.8963 | 62.0865 | -0.15663 | -0.0043708 | -0.012625 | 0.0024202 | 0.061387 | -0.0054367 | 0.068052 | -61.0336 | 62.1094 | -61.1893 | -61.1572 | 61.8027 | 0.050354 | 0.14191 | 0.1831 | 62.1277 | -61.171 | -0.29297 | 0.022888 | -0.13733 | -0.26093 | -0.28381 | -0.27466 | 0.041199 | 0.15564 | 61.0382 | 61.0794 | 122.699 | 123.0057 | -0.13733 | 123.024 | 60.9467 | -0.27466 | 123.0057 | -0.13733 | 60.9467 | 122.699 | 123.024 | -123.2758 | -123.2574
1652.7812 | 123.0881 | -60.9009 | 62.0728 | -0.17189 | -0.0045844 | -0.0096343 | 0.0047702 | 0.059678 | -0.0065047 | 0.067624 | -61.0474 | 62.1048 | -61.1893 | -61.1526 | 61.7844 | 0.022888 | 0.14648 | 0.16937 | 62.1323 | -61.1618 | -0.28839 | 0.032043 | -0.14648 | -0.25177 | -0.28839 | -0.26092 | 0.059509 | 0.14191 | 61.0474 | 61.0703 | 122.6852 | 123.0057 | -0.14648 | 123.0331 | 60.9238 | -0.26092 | 123.0057 | -0.14648 | 60.9238 | 122.6852 | 123.0331 | -123.262 | -123.2346
1653.7656 | 123.2162 | -60.8597 | 62.0087 | -0.11848 | -0.0067206 | -0.0087799 | -0.0016386 | 0.0616 | -0.0058639 | 0.066556 | -60.9695 | 62.0819 | -61.1526 | -61.0519 | 61.9034 | 0.13275 | -0.036621 | 0.29297 | 62.0636 | -61.116 | -0.29297 | 0.073242 | -0.10986 | -0.19226 | -0.10529 | -0.25635 | 0.054932 | 0.18311 | 60.8231 | 61.1526 | 122.7631 | 122.9416 | -0.10986 | 122.9233 | 60.9924 | -0.25635 | 122.9416 | -0.10986 | 60.9924 | 122.7631 | 122.9233 | -123.1613 | -123.1247
1654.7812 | 123.1338 | -60.878 | 62.0544 | -0.095596 | -0.0043708 | -0.0085663 | 0.0069064 | 0.061387 | -0.0075729 | 0.068906 | -61.0062 | 62.0728 | -61.1893 | -61.1023 | 61.8256 | 0.054932 | 0.054932 | 0.20599 | 62.1277 | -61.1526 | -0.31128 | 0.018311 | -0.12817 | -0.2243 | -0.22888 | -0.27466 | 0.073243 | 0.1831 | 60.9329 | 61.084 | 122.7036 | 122.9507 | -0.12817 | 123.0057 | 60.9329 | -0.27466 | 122.9507 | -0.12817 | 60.9329 | 122.7036 | 123.0057 | -123.2437 | -123.2071
1655.7812 | 123.1476 | -60.9055 | 62.0361 | -0.019302 | -0.0071478 | -0.010489 | 0.0041292 | 0.06395 | -0.0047957 | 0.068052 | -60.997 | 62.1002 | -61.1847 | -61.0794 | 61.8393 | 0.068665 | 0.027466 | 0.1831 | 62.1185 | -61.1572 | -0.27923 | 0.064087 | -0.091552 | -0.17395 | -0.19684 | -0.25177 | 0.082397 | 0.18768 | 60.9329 | 61.0886 | 122.7448 | 123.0057 | -0.091552 | 123.024 | 60.9741 | -0.25177 | 123.0057 | -0.091552 | 60.9741 | 122.7448 | 123.024 | -123.2208 | -123.1934
1656.7656 | 123.1888 | -60.8643 | 62.0132 | 0.072251 | -0.0069342 | -0.01113 | -0.0022794 | 0.064378 | -0.0054367 | 0.068265 | -61.0519 | 62.0361 | -61.1664 | -61.1618 | 61.8668 | 0.054932 | -0.082397 | 0.16479 | 62.0773 | -61.1435 | -0.30212 | 0.022888 | -0.18768 | -0.29755 | -0.14648 | -0.27924 | 0.064087 | 0.11444 | 60.7819 | 61.0291 | 122.731 | 122.9004 | -0.18768 | 122.9416 | 60.9192 | -0.27924 | 122.9004 | -0.18768 | 60.9192 | 122.731 | 122.9416 | -123.1796 | -123.1567
1657.7656 | 123.1888 | -60.8871 | 61.9904 | 0.072251 | -0.0080024 | -0.013052 | -0.002493 | 0.062669 | -0.0071457 | 0.068052 | -61.0199 | 62.0316 | -61.1755 | -61.0977 | 61.8576 | 0.068665 | -0.091553 | 0.2243 | 62.0865 | -61.1389 | -0.28839 | 0.041199 | -0.13275 | -0.21057 | -0.13275 | -0.25177 | 0.096131 | 0.15564 | 60.7956 | 61.1114 | 122.7448 | 122.9187 | -0.13275 | 122.9736 | 60.9558 | -0.25177 | 122.9187 | -0.13275 | 60.9558 | 122.7448 | 122.9736 | -123.1659 | -123.1293
1658.7656 | 123.23 | -60.8505 | 62.0132 | -0.04219 | -0.0080024 | -0.0094207 | -0.001425 | 0.06096 | -0.0062911 | 0.06677 | -60.9879 | 62.0499 | -61.1618 | -61.0794 | 61.8851 | 0.1236 | -0.091553 | 0.25177 | 62.0819 | -61.1023 | -0.31128 | 0.036621 | -0.13733 | -0.22888 | -0.12817 | -0.25177 | 0.068664 | 0.17395 | 60.759 | 61.1023 | 122.7356 | 122.9004 | -0.13733 | 122.9324 | 60.9741 | -0.25177 | 122.9004 | -0.13733 | 60.9741 | 122.7356 | 122.9324 | -123.175 | -123.1155
1659.7656 | 123.1979 | -60.8551 | 62.0224 | -0.04982 | -0.007575 | -0.0092071 | 0.001993 | 0.058396 | -0.0062911 | 0.066984 | -61.0107 | 62.0361 | -61.1526 | -61.0931 | 61.8668 | 0.09613 | -0.082397 | 0.23346 | 62.0728 | -61.1298 | -0.29755 | 0.013733 | -0.15564 | -0.23804 | -0.15564 | -0.27466 | 0.050354 | 0.14191 | 60.7727 | 61.0886 | 122.7219 | 122.8912 | -0.15564 | 122.9279 | 60.9512 | -0.27466 | 122.8912 | -0.15564 | 60.9512 | 122.7219 | 122.9279 | -123.175 | -123.1522
1660.7656 | 123.2346 | -60.8505 | 62.0087 | -0.057449 | -0.005866 | -0.010703 | 0.0032748 | 0.057114 | -0.0050095 | 0.067411 | -61.0016 | 62.0407 | -61.1526 | -61.0382 | 61.908 | 0.13733 | -0.10071 | 0.29755 | 62.0544 | -61.1481 | -0.30212 | 0.032043 | -0.15106 | -0.18768 | -0.10071 | -0.29755 | 0.045776 | 0.15106 | 60.7498 | 61.1481 | 122.7585 | 122.8912 | -0.15106 | 122.905 | 60.9879 | -0.29755 | 122.8912 | -0.15106 | 60.9879 | 122.7585 | 122.905 | -123.1613 | -123.1567
1661.7656 | 123.2162 | -60.8505 | 62.0316 | -0.026932 | -0.0069342 | -0.01348 | 0.0017794 | 0.057542 | -0.0071457 | 0.068479 | -60.9833 | 62.0178 | -61.1893 | -61.0519 | 61.8805 | 0.10986 | -0.082397 | 0.24261 | 62.0865 | -61.1069 | -0.33875 | -0.013733 | -0.13275 | -0.20142 | -0.15106 | -0.25635 | 0.054932 | 0.20599 | 60.7681 | 61.0931 | 122.731 | 122.8683 | -0.13275 | 122.937 | 60.9604 | -0.25635 | 122.8683 | -0.13275 | 60.9604 | 122.731 | 122.937 | -123.2208 | -123.1384
1662.7656 | 123.2162 | -60.8551 | 62.0224 | -0.026932 | -0.0062934 | -0.010916 | 0.00049764 | 0.059678 | -0.0041549 | 0.067197 | -61.0062 | 62.0499 | -61.1618 | -61.0794 | 61.8622 | 0.082397 | -0.07782 | 0.22888 | 62.0819 | -61.1114 | -0.3067 | 0.027466 | -0.15106 | -0.2243 | -0.16022 | -0.25635 | 0.059509 | 0.15564 | 60.7773 | 61.084 | 122.7173 | 122.905 | -0.15106 | 122.937 | 60.9375 | -0.25635 | 122.905 | -0.15106 | 60.9375 | 122.7173 | 122.937 | -123.1842 | -123.1338
1663.7656 | 123.1796 | -60.8917 | 62.0224 | 0.21721 | -0.007575 | -0.0072845 | 0.0011386 | 0.060746 | -0.0060775 | 0.066556 | -61.0107 | 62.0087 | -61.1801 | -61.1206 | 61.8118 | 0.004578 | -0.12817 | 0.13733 | 62.0682 | -61.1389 | -0.28839 | -0.013733 | -0.11902 | -0.22888 | -0.21057 | -0.24719 | 0.045776 | 0.16937 | 60.7636 | 61.0291 | 122.7036 | 122.9004 | -0.11902 | 122.9599 | 60.8963 | -0.24719 | 122.9004 | -0.11902 | 60.8963 | 122.7036 | 122.9599 | -123.2025 | -123.1613
1664.7656 | 123.1659 | -60.878 | 62.0041 | 0.2401 | -0.0077888 | -0.01348 | 0.00071144 | 0.062028 | -0.0052231 | 0.069333 | -61.0062 | 62.0087 | -61.1893 | -61.1023 | 61.8347 | 0.018311 | -0.16022 | 0.16022 | 62.0316 | -61.1435 | -0.31128 | 0.004578 | -0.12817 | -0.2243 | -0.16937 | -0.2655 | 0.027466 | 0.1831 | 60.7178 | 61.0382 | 122.7127 | 122.8867 | -0.12817 | 122.9095 | 60.8963 | -0.2655 | 122.8867 | -0.12817 | 60.8963 | 122.7127 | 122.9095 | -123.1934 | -123.1476
1665.7656 | 123.175 | -60.8871 | 62.0224 | 0.087509 | -0.0084296 | -0.012412 | 0.00071144 | 0.060319 | -0.0054367 | 0.067838 | -61.0703 | 62.0316 | -61.1893 | -61.1343 | 61.7935 | 0.018311 | -0.091553 | 0.15564 | 62.059 | -61.1389 | -0.30212 | 0.009155 | -0.1831 | -0.24719 | -0.22888 | -0.25177 | 0.036621 | 0.11902 | 60.7956 | 61.0428 | 122.6807 | 122.9187 | -0.1831 | 122.9462 | 60.9055 | -0.25177 | 122.9187 | -0.1831 | 60.9055 | 122.6807 | 122.9462 | -123.2117 | -123.1613
1666.7656 | 123.1842 | -60.8505 | 62.0316 | 0.10277 | -0.0056524 | -0.010703 | 0.002634 | 0.059891 | -0.0050095 | 0.06912 | -61.0336 | 62.0316 | -61.1847 | -61.1298 | 61.821 | 0.018311 | -0.07782 | 0.14191 | 62.0499 | -61.116 | -0.33417 | 0 | -0.18311 | -0.27924 | -0.21057 | -0.2655 | 0.018311 | 0.15106 | 60.7727 | 60.9924 | 122.6715 | 122.8821 | -0.18311 | 122.9004 | 60.8688 | -0.2655 | 122.8821 | -0.18311 | 60.8688 | 122.6715 | 122.9004 | -123.2162 | -123.1476
1667.7656 | 123.1659 | -60.8688 | 62.0224 | 0.12566 | -0.0043708 | -0.0077117 | 0.00049764 | 0.059678 | -0.0058639 | 0.06677 | -61.0474 | 62.0499 | -61.1847 | -61.1206 | 61.8347 | 0.009155 | -0.10986 | 0.13733 | 62.0316 | -61.171 | -0.31586 | 0.027466 | -0.17853 | -0.25177 | -0.18768 | -0.30212 | 0.009155 | 0.13733 | 60.759 | 61.0062 | 122.7036 | 122.9187 | -0.17853 | 122.9004 | 60.878 | -0.30212 | 122.9187 | -0.17853 | 60.878 | 122.7036 | 122.9004 | -123.2071 | -123.1934
1668.7656 | 123.1796 | -60.8734 | 62.0041 | 0.10277 | -0.0073614 | -0.0083527 | 0.002634 | 0.057328 | -0.0035141 | 0.068052 | -61.0107 | 62.0361 | -61.1755 | -61.0886 | 61.8118 | 0 | -0.11902 | 0.15564 | 62.0132 | -61.1801 | -0.30212 | 0.032044 | -0.13733 | -0.21515 | -0.19226 | -0.3067 | 0.009156 | 0.16479 | 60.7544 | 61.0291 | 122.6852 | 122.9095 | -0.13733 | 122.8867 | 60.8734 | -0.3067 | 122.9095 | -0.13733 | 60.8734 | 122.6852 | 122.8867 | -123.1796 | -123.1842
1669.7656 | 123.1888 | -60.8917 | 61.9904 | 0.22484 | -0.004798 | -0.0070709 | 0.0030612 | 0.059464 | -0.0045821 | 0.068693 | -61.0062 | 62.0499 | -61.1755 | -61.0931 | 61.821 | 0.032043 | -0.17853 | 0.13275 | 62.0087 | -61.1481 | -0.28381 | 0.05951 | -0.11444 | -0.20142 | -0.16937 | -0.25635 | 0.018311 | 0.16937 | 60.7132 | 61.0245 | 122.7127 | 122.9416 | -0.11444 | 122.9004 | 60.9238 | -0.25635 | 122.9416 | -0.11444 | 60.9238 | 122.7127 | 122.9004 | -123.1659 | -123.1384
1670.7656 | 123.1979 | -60.878 | 62.0041 | 0.32402 | -0.0060798 | -0.0079253 | 0.0073336 | 0.061387 | -0.0065047 | 0.065275 | -60.9879 | 62.0361 | -61.1938 | -61.0703 | 61.8484 | -0.12817 | -0.25177 | 0.28381 | 61.9858 | -61.1618 | -0.31586 | 0.032044 | -0.10986 | -0.19226 | -0.15564 | -0.28381 | -0.01831 | 0.20599 | 60.6262 | 61.1618 | 122.7264 | 122.9141 | -0.10986 | 122.8638 | 60.7498 | -0.28381 | 122.9141 | -0.10986 | 60.7498 | 122.7264 | 122.8638 | -123.1979 | -123.1659
1671.7656 | 123.2025 | -60.8917 | 61.9858 | 0.18669 | -0.0039434 | -0.0072845 | 0.00712 | 0.062241 | -0.0062911 | 0.06912 | -60.9924 | 62.0636 | -61.1801 | -61.084 | 61.853 | 0.032043 | -0.18768 | 0.13275 | 62.0499 | -61.1481 | -0.28839 | 0.07782 | -0.10071 | -0.19226 | -0.13275 | -0.25635 | 0.064087 | 0.18768 | 60.704 | 61.0245 | 122.7448 | 122.9553 | -0.10071 | 122.9416 | 60.9238 | -0.25635 | 122.9553 | -0.10071 | 60.9238 | 122.7448 | 122.9416 | -123.1659 | -123.1338
1672.7656 | 123.1796 | -60.91 | 61.972 | 0.22484 | -0.0062934 | -0.011343 | 0.0034884 | 0.059891 | -0.0043685 | 0.06912 | -61.0016 | 62.059 | -61.1618 | -61.084 | 61.8576 | 0.041199 | -0.1831 | 0.14191 | 62.0224 | -61.1481 | -0.25177 | 0.086975 | -0.091553 | -0.17395 | -0.11444 | -0.23804 | 0.050354 | 0.16022 | 60.7269 | 61.0519 | 122.7676 | 122.9691 | -0.091553 | 122.9324 | 60.9512 | -0.23804 | 122.9691 | -0.091553 | 60.9512 | 122.7676 | 122.9324 | -123.1338 | -123.1201
1673.7656 | 123.1979 | -60.8963 | 61.9858 | 0.22484 | -0.008216 | -0.0083527 | 0.0047702 | 0.063096 | -0.0035141 | 0.069974 | -60.9787 | 62.0636 | -61.171 | -61.084 | 61.8668 | 0.032043 | -0.19226 | 0.16022 | 62.0132 | -61.1526 | -0.27466 | 0.07782 | -0.082398 | -0.18768 | -0.11902 | -0.25635 | 0.027466 | 0.19226 | 60.704 | 61.0565 | 122.7631 | 122.9599 | -0.082398 | 122.9095 | 60.9283 | -0.25635 | 122.9599 | -0.082398 | 60.9283 | 122.7631 | 122.9095 | -123.1567 | -123.1384
1674.7656 | 123.2025 | -60.8917 | 61.9766 | 0.19432 | -0.0056524 | -0.0085663 | 0.0017794 | 0.060746 | -0.0035141 | 0.066984 | -60.9741 | 62.0407 | -61.1664 | -61.084 | 61.8484 | 0.041199 | -0.1831 | 0.15106 | 62.0087 | -61.1481 | -0.27466 | 0.064086 | -0.082397 | -0.19226 | -0.12817 | -0.25635 | 0.032043 | 0.19226 | 60.7086 | 61.0428 | 122.7402 | 122.9324 | -0.082397 | 122.9004 | 60.9329 | -0.25635 | 122.9324 | -0.082397 | 60.9329 | 122.7402 | 122.9004 | -123.143 | -123.1247
1675.7656 | 123.2071 | -60.8597 | 62.0041 | 0.24773 | -0.004798 | -0.0064301 | 0.0051974 | 0.063309 | -0.0037277 | 0.066984 | -60.9833 | 62.0819 | -61.1984 | -61.2305 | 61.9629 | 0.11444 | -0.14648 | 0.12817 | 62.0087 | -61.1664 | -0.33875 | 0.07782 | -0.1236 | -0.37079 | -0.041198 | -0.3067 | 0.004578 | 0.21515 | 60.7132 | 60.9879 | 122.8226 | 122.9416 | -0.1236 | 122.8683 | 60.9741 | -0.3067 | 122.9416 | -0.1236 | 60.9741 | 122.8226 | 122.8683 | -123.2025 | -123.1705
1676.7812 | 123.1979 | -60.8505 | 62.0087 | -0.026932 | -0.0056524 | -0.010489 | 0.00028404 | 0.060532 | -0.0047957 | 0.069547 | -61.0153 | 62.059 | -61.1984 | -61.0657 | 61.8805 | 0.13275 | -0.064087 | 0.26093 | 62.0453 | -61.1206 | -0.3479 | 0.050354 | -0.1648 | -0.21515 | -0.12817 | -0.27008 | 0.036621 | 0.1831 | 60.7864 | 61.1114 | 122.731 | 122.9095 | -0.1648 | 122.8958 | 60.9833 | -0.27008 | 122.9095 | -0.1648 | 60.9833 | 122.731 | 122.8958 | -123.2071 | -123.1293
1677.7656 | 123.111 | -60.9146 | 62.0316 | 0.22484 | -0.005866 | -0.0092071 | 0.0075472 | 0.061173 | -0.0039413 | 0.066129 | -61.0336 | 62.1094 | -61.2076 | -61.1618 | 61.7706 | -0.041199 | -0.059509 | 0.041199 | 62.0636 | -61.2122 | -0.29297 | 0.07782 | -0.11902 | -0.24719 | -0.26093 | -0.29755 | 0.032044 | 0.17395 | 60.8551 | 60.9558 | 122.6852 | 123.024 | -0.11902 | 122.9782 | 60.8734 | -0.29755 | 123.024 | -0.11902 | 60.8734 | 122.6852 | 122.9782 | -123.2391 | -123.2437
1678.7656 | 123.0835 | -60.9375 | 62.0178 | 0.1638 | -0.0043708 | -0.0070709 | 0.0066928 | 0.0616 | -0.0052231 | 0.066343 | -61.0611 | 62.1323 | -61.203 | -61.1755 | 61.7615 | -0.054932 | -0.018311 | 0.022888 | 62.0636 | -61.2076 | -0.2655 | 0.11444 | -0.1236 | -0.23804 | -0.25635 | -0.27008 | 0.045777 | 0.14191 | 60.9192 | 60.9604 | 122.699 | 123.0698 | -0.1236 | 123.0011 | 60.8826 | -0.27008 | 123.0698 | -0.1236 | 60.8826 | 122.699 | 123.0011 | -123.2208 | -123.2254
1679.7656 | 123.2437 | -60.8643 | 61.9949 | 0.07988 | -0.0045844 | -0.0081389 | 0.001993 | 0.06395 | -0.0035141 | 0.068479 | -60.997 | 62.1048 | -61.1801 | -61.0886 | 61.8668 | 0.041199 | -0.20142 | 0.14191 | 62.0361 | -61.1526 | -0.31586 | 0.10986 | -0.13275 | -0.2243 | -0.12817 | -0.28839 | 0.041199 | 0.18311 | 60.6628 | 61.0062 | 122.731 | 122.9691 | -0.13275 | 122.9004 | 60.9055 | -0.28839 | 122.9691 | -0.13275 | 60.9055 | 122.731 | 122.9004 | -123.175 | -123.1476
1680.7656 | 123.2162 | -60.9055 | 61.9949 | 0.25536 | -0.0026618 | -0.0047211 | 0.0058382 | 0.063523 | -0.0011643 | 0.067411 | -61.0107 | 62.0911 | -61.203 | -61.1114 | 61.8805 | 0.054932 | -0.17395 | 0.14191 | 62.0361 | -61.1893 | -0.29755 | 0.09613 | -0.10529 | -0.20599 | -0.11444 | -0.28381 | 0.041199 | 0.19226 | 60.7315 | 61.0474 | 122.7859 | 122.9965 | -0.10529 | 122.9416 | 60.9604 | -0.28381 | 122.9965 | -0.10529 | 60.9604 | 122.7859 | 122.9416 | -123.1979 | -123.1842
1681.7812 | 123.2346 | -60.8597 | 62.0178 | -0.17189 | -0.0084296 | -0.0068573 | -0.0020658 | 0.059891 | -0.0075729 | 0.069974 | -60.9879 | 62.0453 | -61.1526 | -61.0474 | 61.9171 | 0.16022 | -0.045776 | 0.28839 | 62.0728 | -61.1206 | -0.29297 | 0.027466 | -0.12817 | -0.18768 | -0.10071 | -0.26093 | 0.054932 | 0.16479 | 60.8139 | 61.1481 | 122.7768 | 122.905 | -0.12817 | 122.9324 | 61.0199 | -0.26093 | 122.905 | -0.12817 | 61.0199 | 122.7768 | 122.9324 | -123.1705 | -123.1384
1682.7656 | 123.1659 | -60.9146 | 62.0087 | 0.27061 | -0.0043708 | -0.0045075 | 0.0039156 | 0.063309 | -0.0043685 | 0.066129 | -61.0291 | 62.1368 | -61.1664 | -61.1435 | 61.8027 | -0.032043 | -0.09613 | 0.082397 | 62.0636 | -61.1755 | -0.25177 | 0.12817 | -0.11444 | -0.22888 | -0.20599 | -0.26093 | 0.054932 | 0.13733 | 60.8185 | 60.997 | 122.7173 | 123.0515 | -0.11444 | 122.9782 | 60.8826 | -0.26093 | 123.0515 | -0.11444 | 60.8826 | 122.7173 | 122.9782 | -123.175 | -123.1842
1683.7656 | 123.1201 | -60.91 | 62.027 | 0.20958 | -0.0026618 | -0.0055755 | 0.0069064 | 0.062882 | -0.0050095 | 0.068479 | -61.0474 | 62.1689 | -61.203 | -61.1664 | 61.7752 | -0.050354 | -0.068665 | 0.054932 | 62.0499 | -61.203 | -0.29297 | 0.14191 | -0.13733 | -0.25635 | -0.25177 | -0.29297 | 0.022888 | 0.15564 | 60.8414 | 60.965 | 122.6852 | 123.0789 | -0.13733 | 122.9599 | 60.8597 | -0.29297 | 123.0789 | -0.13733 | 60.8597 | 122.6852 | 122.9599 | -123.23 | -123.23
1684.7656 | 123.0698 | -60.9009 | 61.9812 | 0.17906 | -0.0045844 | -0.0055755 | 0.0081882 | 0.063096 | -0.0030869 | 0.068052 | -61.0748 | 62.1643 | -61.2442 | -61.1893 | 61.7386 | -0.068665 | 0.004578 | 0.045776 | 62.0682 | -61.2442 | -0.34332 | 0.18311 | -0.17395 | -0.28839 | -0.24262 | -0.34332 | 0.086975 | 0.16937 | 60.9055 | 60.9467 | 122.6395 | 123.0652 | -0.17395 | 122.9691 | 60.8322 | -0.34332 | 123.0652 | -0.17395 | 60.8322 | 122.6395 | 122.9691 | -123.2254 | -123.2254
1685.7656 | 123.0835 | -60.9375 | 62.0361 | 0.10277 | -0.0039434 | -0.0060027 | 0.0047702 | 0.062669 | -0.0050095 | 0.068693 | -61.0657 | 62.1735 | -61.203 | -61.1893 | 61.7661 | -0.045776 | 0.013733 | 0.027466 | 62.0636 | -61.2259 | -0.2655 | 0.13733 | -0.12817 | -0.25177 | -0.27008 | -0.28839 | 0.027466 | 0.13733 | 60.9512 | 60.965 | 122.7036 | 123.111 | -0.12817 | 123.0011 | 60.8917 | -0.28839 | 123.111 | -0.12817 | 60.8917 | 122.7036 | 123.0011 | -123.2391 | -123.262
1686.7812 | 123.1934 | -60.8871 | 62.0132 | 0.20195 | -0.0041572 | -0.0092071 | -0.0029202 | 0.062028 | -0.0026595 | 0.068479 | -61.0428 | 62.1048 | -61.171 | -61.1526 | 61.853 | 0.036621 | -0.073242 | 0.12817 | 62.0453 | -61.1847 | -0.28381 | 0.091552 | -0.15564 | -0.2655 | -0.16022 | -0.29755 | 0.032043 | 0.12817 | 60.8139 | 61.0153 | 122.7402 | 122.9919 | -0.15564 | 122.9324 | 60.9238 | -0.29755 | 122.9919 | -0.15564 | 60.9238 | 122.7402 | 122.9324 | -123.1842 | -123.1979
1687.7656 | 123.0927 | -60.9146 | 62.0316 | 0.27824 | -0.0035162 | -0.0030121 | 0.0064792 | 0.06395 | -0.0033005 | 0.068052 | -61.0565 | 62.1689 | -61.2076 | -61.1847 | 61.7661 | -0.054932 | -0.032043 | 0.050354 | 62.0636 | -61.203 | -0.29297 | 0.13733 | -0.14191 | -0.27008 | -0.2655 | -0.28839 | 0.032044 | 0.15106 | 60.8826 | 60.965 | 122.6807 | 123.0835 | -0.14191 | 122.9782 | 60.8597 | -0.28839 | 123.0835 | -0.14191 | 60.8597 | 122.6807 | 122.9782 | -123.2391 | -123.2346
1688.7656 | 123.1064 | -60.9192 | 62.0361 | 0.0035856 | -0.0054388 | -0.0060027 | 0.0073336 | 0.062669 | -0.0054367 | 0.068479 | -61.0107 | 62.1918 | -61.2076 | -61.2122 | 61.7432 | -0.045776 | 0 | 0.041199 | 62.0682 | -61.2213 | -0.28839 | 0.15564 | -0.091553 | -0.29297 | -0.29297 | -0.30212 | 0.032043 | 0.19684 | 60.9192 | 60.9604 | 122.6624 | 123.111 | -0.091553 | 122.9874 | 60.8734 | -0.30212 | 123.111 | -0.091553 | 60.8734 | 122.6624 | 122.9874 | -123.2437 | -123.2574
1689.7656 | 123.0606 | -60.9238 | 62.0544 | 0.21721 | -0.0033026 | -0.0070709 | 0.0066928 | 0.062669 | -0.0024459 | 0.072111 | -61.0703 | 62.1643 | -61.2122 | -61.4639 | 61.647 | 0.091553 | 0.018311 | 0.13733 | 62.0911 | -61.2259 | -0.28839 | 0.10986 | -0.14648 | -0.54016 | -0.40741 | -0.30212 | 0.036621 | 0.14191 | 60.9421 | 61.0611 | 122.5708 | 123.0881 | -0.14648 | 123.0148 | 61.0153 | -0.30212 | 123.0881 | -0.14648 | 61.0153 | 122.5708 | 123.0148 | -123.2666 | -123.2803
1690.7656 | 123.0743 | -60.9238 | 62.0132 | 0.14854 | -0.004798 | -0.0015167 | 0.0060518 | 0.062028 | -0.0041549 | 0.069761 | -61.0703 | 62.1689 | -61.1938 | -61.2259 | 61.734 | -0.054932 | 0 | 0.050354 | 62.0682 | -61.2305 | -0.27008 | 0.15564 | -0.14648 | -0.30212 | -0.27924 | -0.3067 | 0.054931 | 0.1236 | 60.9238 | 60.9741 | 122.6578 | 123.0927 | -0.14648 | 122.9919 | 60.8688 | -0.3067 | 123.0927 | -0.14648 | 60.8688 | 122.6578 | 122.9919 | -123.2071 | -123.2437
1691.7656 | 123.1064 | -60.9055 | 62.0407 | 0.056992 | -0.0056524 | -0.0068573 | 0.0060518 | 0.063523 | -0.0060775 | 0.06912 | -61.0016 | 62.1689 | -61.1984 | -61.1526 | 61.8027 | 0.013733 | 0.013733 | 0.12817 | 62.1185 | -61.2305 | -0.29297 | 0.12817 | -0.09613 | -0.24719 | -0.23804 | -0.32501 | 0.07782 | 0.19684 | 60.9192 | 61.0336 | 122.7081 | 123.0743 | -0.09613 | 123.024 | 60.9192 | -0.32501 | 123.0743 | -0.09613 | 60.9192 | 122.7081 | 123.024 | -123.2391 | -123.2712
1692.7656 | 123.1064 | -60.8871 | 62.0453 | -0.04219 | -0.0033026 | -0.0053619 | 0.0056246 | 0.063309 | -0.0045821 | 0.069333 | -61.0062 | 62.178 | -61.1572 | -61.1252 | 61.8347 | 0.041199 | 0.018311 | 0.14191 | 62.0819 | -61.1938 | -0.27008 | 0.13275 | -0.11902 | -0.23804 | -0.21057 | -0.3067 | 0.036621 | 0.15106 | 60.9055 | 61.0291 | 122.7219 | 123.0652 | -0.11902 | 122.9691 | 60.9283 | -0.3067 | 123.0652 | -0.11902 | 60.9283 | 122.7219 | 122.9691 | -123.2025 | -123.2391
1693.7656 | 123.0835 | -60.9192 | 62.0499 | 0.12566 | -0.00138 | -0.0066437 | 0.0028476 | 0.062882 | -0.0033005 | 0.067838 | -61.0657 | 62.1735 | -61.2213 | -61.2167 | 61.7477 | -0.073242 | 0.032043 | 0.027466 | 62.0865 | -61.2076 | -0.30212 | 0.1236 | -0.14648 | -0.29755 | -0.30212 | -0.28839 | 0.036621 | 0.15564 | 60.9512 | 60.9467 | 122.6669 | 123.0927 | -0.14648 | 123.0057 | 60.8459 | -0.28839 | 123.0927 | -0.14648 | 60.8459 | 122.6669 | 123.0057 | -123.2712 | -123.2574
1694.7656 | 123.1155 | -60.9238 | 62.059 | 0.095139 | -0.0015936 | -0.0034393 | 0.0045566 | 0.064591 | -0.0039413 | 0.068265 | -61.0382 | 62.2009 | -61.1984 | -61.1984 | 61.7615 | -0.027466 | 0.018311 | 0.050354 | 62.1002 | -61.235 | -0.27466 | 0.14191 | -0.11444 | -0.27466 | -0.29755 | -0.31128 | 0.041199 | 0.16022 | 60.9421 | 60.9741 | 122.6852 | 123.1247 | -0.11444 | 123.024 | 60.8963 | -0.31128 | 123.1247 | -0.11444 | 60.8963 | 122.6852 | 123.024 | -123.2574 | -123.2941
1695.7656 | 123.0881 | -60.9238 | 62.0682 | 0.087509 | -0.0015936 | -0.0060027 | 0.0039156 | 0.064164 | -0.0041549 | 0.06677 | -61.0336 | 62.1964 | -61.2076 | -61.171 | 61.7889 | 0.009155 | 0.027466 | 0.10529 | 62.1048 | -61.2213 | -0.28381 | 0.12817 | -0.10986 | -0.24719 | -0.27924 | -0.29755 | 0.036621 | 0.17395 | 60.9512 | 61.0291 | 122.7127 | 123.1201 | -0.10986 | 123.0286 | 60.9329 | -0.29755 | 123.1201 | -0.10986 | 60.9329 | 122.7127 | 123.0286 | -123.2758 | -123.2895
1696.7656 | 123.1384 | -60.9146 | 62.0132 | -0.011673 | -0.0026618 | -0.0077117 | 0.0041292 | 0.064164 | -0.0035141 | 0.068693 | -61.0107 | 62.2009 | -61.2076 | -61.1389 | 61.8027 | 0.018311 | 0.022888 | 0.1236 | 62.1094 | -61.2534 | -0.29297 | 0.18768 | -0.09613 | -0.2243 | -0.21057 | -0.33875 | 0.09613 | 0.19684 | 60.9375 | 61.0382 | 122.7173 | 123.1155 | -0.09613 | 123.024 | 60.9329 | -0.33875 | 123.1155 | -0.09613 | 60.9329 | 122.7173 | 123.024 | -123.2208 | -123.2666
1697.7656 | 123.1384 | -60.9009 | 62.027 | -0.39314 | -0.0037298 | -0.010062 | 0.0056246 | 0.064805 | -0.0067185 | 0.067624 | -61.0016 | 62.1918 | -61.1847 | -61.1252 | 61.8301 | 0.068665 | 0.018311 | 0.15564 | 62.0865 | -61.1984 | -0.28381 | 0.16479 | -0.10071 | -0.2243 | -0.19684 | -0.29755 | 0.059509 | 0.1831 | 60.9192 | 61.0565 | 122.731 | 123.0927 | -0.10071 | 122.9874 | 60.9695 | -0.29755 | 123.0927 | -0.10071 | 60.9695 | 122.731 | 122.9874 | -123.2117 | -123.2254
1698.7656 | 123.1384 | -60.9055 | 62.059 | -0.095596 | -0.0043708 | -0.0034393 | 0.0056246 | 0.065018 | -0.0026595 | 0.069761 | -61.0153 | 62.2101 | -61.1938 | -61.1206 | 61.8393 | 0.082397 | 0.073242 | 0.1831 | 62.1094 | -61.203 | -0.28839 | 0.15106 | -0.10986 | -0.21515 | -0.21973 | -0.29755 | 0.050354 | 0.17853 | 60.9787 | 61.0886 | 122.7448 | 123.1155 | -0.10986 | 123.0148 | 60.9879 | -0.29755 | 123.1155 | -0.10986 | 60.9879 | 122.7448 | 123.0148 | -123.2529 | -123.262
1699.7656 | 123.1522 | -60.8963 | 62.059 | -0.04982 | -0.0024482 | -0.0062163 | 0.0041292 | 0.062669 | -0.0039413 | 0.067197 | -60.9879 | 62.1918 | -61.1847 | -61.1114 | 61.8301 | 0.068665 | 0.041199 | 0.18768 | 62.1094 | -61.2076 | -0.28839 | 0.13275 | -0.091553 | -0.21515 | -0.22888 | -0.31128 | 0.050354 | 0.19684 | 60.9375 | 61.084 | 122.7264 | 123.0881 | -0.091553 | 123.0057 | 60.965 | -0.31128 | 123.0881 | -0.091553 | 60.965 | 122.7264 | 123.0057 | -123.2437 | -123.2666
1700.7656 | 123.1384 | -60.91 | 62.0544 | -0.04219 | -0.0015936 | -0.0036529 | 0.0034884 | 0.065659 | -0.0058639 | 0.066984 | -60.997 | 62.1689 | -61.2167 | -61.116 | 61.7615 | -0.082397 | 0.064087 | 0.19226 | 62.1048 | -61.2076 | -0.3067 | 0.11444 | -0.086975 | -0.20599 | -0.29297 | -0.29755 | 0.050354 | 0.21973 | 60.9741 | 61.1023 | 122.6715 | 123.0789 | -0.086975 | 123.0148 | 60.8276 | -0.29755 | 123.0789 | -0.086975 | 60.8276 | 122.6715 | 123.0148 | -123.2712 | -123.262
1701.7656 | 123.1384 | -60.8917 | 62.0499 | -0.087967 | -0.0052252 | -0.0072845 | 0.0058382 | 0.063096 | -0.0041549 | 0.068265 | -60.9924 | 62.1964 | -61.2076 | -61.1206 | 61.8484 | 0.073242 | 0.036621 | 0.19226 | 62.1002 | -61.2213 | -0.31586 | 0.14648 | -0.10071 | -0.22888 | -0.20142 | -0.32959 | 0.050354 | 0.21515 | 60.9283 | 61.084 | 122.7402 | 123.0881 | -0.10071 | 122.9919 | 60.965 | -0.32959 | 123.0881 | -0.10071 | 60.965 | 122.7402 | 122.9919 | -123.2574 | -123.2712
1702.7656 | 123.0789 | -60.9283 | 62.0544 | 0.095139 | -0.0039434 | -0.0057891 | 0.0041292 | 0.060746 | -0.0030869 | 0.068906 | -61.0657 | 62.1872 | -61.1984 | -61.2122 | 61.7523 | -0.027466 | 0.032043 | 0.050354 | 62.0636 | -61.2442 | -0.27008 | 0.13275 | -0.13733 | -0.28381 | -0.30212 | -0.31586 | 0.009156 | 0.13275 | 60.9604 | 60.9787 | 122.6807 | 123.1155 | -0.13733 | 122.9919 | 60.9009 | -0.31586 | 123.1155 | -0.13733 | 60.9009 | 122.6807 | 122.9919 | -123.2529 | -123.2986
1703.7656 | 123.1201 | -60.9009 | 62.0499 | -0.149 | -0.0033026 | -0.0060027 | 0.0024202 | 0.062241 | -0.0035141 | 0.068906 | -61.0382 | 62.2055 | -61.2122 | -61.1435 | 61.8393 | 0.064087 | 0.10071 | 0.1831 | 62.1185 | -61.2076 | -0.31128 | 0.15564 | -0.13733 | -0.24261 | -0.21057 | -0.3067 | 0.068664 | 0.17395 | 61.0016 | 61.084 | 122.7402 | 123.1064 | -0.13733 | 123.0194 | 60.965 | -0.3067 | 123.1064 | -0.13733 | 60.965 | 122.7402 | 123.0194 | -123.262 | -123.2574
1704.7656 | 123.0927 | -60.9055 | 62.0636 | -0.149 | -0.0050116 | -0.0070709 | 0.00028404 | 0.064591 | -0.0033005 | 0.068265 | -61.0382 | 62.1872 | -61.1755 | -61.1572 | 61.8073 | 0.059509 | 0.1236 | 0.1831 | 62.1368 | -61.2076 | -0.27008 | 0.1236 | -0.13275 | -0.25177 | -0.25635 | -0.30212 | 0.073242 | 0.13733 | 61.0291 | 61.0886 | 122.7127 | 123.0927 | -0.13275 | 123.0423 | 60.965 | -0.30212 | 123.0927 | -0.13275 | 60.965 | 122.7127 | 123.0423 | -123.2391 | -123.2712
1705.7656 | 123.0881 | -60.8871 | 62.0956 | -0.15663 | -0.0054388 | -0.0087799 | -0.00014316 | 0.0616 | -0.0037277 | 0.068479 | -61.0657 | 62.178 | -61.2167 | -61.171 | 61.7889 | 0.045776 | 0.15106 | 0.17853 | 62.1414 | -61.2122 | -0.32959 | 0.082398 | -0.17853 | -0.28381 | -0.3067 | -0.32501 | 0.045776 | 0.15106 | 61.0382 | 61.0657 | 122.6761 | 123.0652 | -0.17853 | 123.0286 | 60.9329 | -0.32501 | 123.0652 | -0.17853 | 60.9329 | 122.6761 | 123.0286 | -123.3124 | -123.3078
1706.7656 | 123.1201 | -60.9055 | 62.0773 | -0.149 | -0.0037298 | -0.0070709 | 0.0024202 | 0.061387 | -0.0050095 | 0.068906 | -61.0245 | 62.1689 | -61.1984 | -61.1298 | 61.821 | 0.059509 | 0.10986 | 0.19684 | 62.1368 | -61.1984 | -0.29297 | 0.091552 | -0.11902 | -0.2243 | -0.25635 | -0.29297 | 0.059509 | 0.17395 | 61.0153 | 61.1023 | 122.7264 | 123.0743 | -0.11902 | 123.0423 | 60.965 | -0.29297 | 123.0743 | -0.11902 | 60.965 | 122.7264 | 123.0423 | -123.2758 | -123.2758
1707.7656 | 123.1384 | -60.9009 | 62.0636 | -0.149 | -0.004798 | -0.0087799 | 0.00092504 | 0.062669 | -0.0043685 | 0.068265 | -61.0611 | 62.1643 | -61.1801 | -61.1572 | 61.7889 | 0.054932 | 0.12817 | 0.1831 | 62.146 | -61.1801 | -0.27924 | 0.10071 | -0.16022 | -0.25635 | -0.27466 | -0.27924 | 0.082397 | 0.11902 | 61.0291 | 61.084 | 122.6898 | 123.0652 | -0.16022 | 123.0469 | 60.9558 | -0.27924 | 123.0652 | -0.16022 | 60.9558 | 122.6898 | 123.0469 | -123.2437 | -123.2437
1708.7656 | 123.1201 | -60.9192 | 62.059 | -0.087967 | -0.0041572 | -0.0057891 | 0.0013522 | 0.064378 | -0.0060775 | 0.067197 | -61.0657 | 62.1552 | -61.2167 | -61.1526 | 61.7981 | 0.045776 | 0.14191 | 0.17395 | 62.1323 | -61.1664 | -0.29755 | 0.09613 | -0.14648 | -0.23346 | -0.26093 | -0.24719 | 0.073242 | 0.15106 | 61.0611 | 61.0931 | 122.7173 | 123.0743 | -0.14648 | 123.0515 | 60.965 | -0.24719 | 123.0743 | -0.14648 | 60.965 | 122.7173 | 123.0515 | -123.2758 | -123.2254
1709.7656 | 123.0835 | -60.8917 | 62.0636 | -0.18715 | -0.0062934 | -0.012625 | 0.001993 | 0.062028 | -0.0075729 | 0.064847 | -61.0657 | 62.1506 | -61.1938 | -61.1206 | 61.6974 | -0.036621 | 0.091553 | 0.13733 | 62.1277 | -61.2076 | -0.30212 | 0.086975 | -0.17395 | -0.22888 | -0.36621 | -0.31586 | 0.064087 | 0.12817 | 60.9833 | 61.0291 | 122.5891 | 123.0423 | -0.17395 | 123.0194 | 60.8551 | -0.31586 | 123.0423 | -0.17395 | 60.8551 | 122.5891 | 123.0194 | -123.2574 | -123.2712
1710.7656 | 123.0881 | -60.8871 | 62.059 | -0.17952 | -0.004798 | -0.0066437 | 0.00071144 | 0.059464 | -0.0065047 | 0.067624 | -61.0748 | 62.1643 | -61.1847 | -61.171 | 61.7798 | 0.045776 | 0.13275 | 0.16937 | 62.1597 | -61.1893 | -0.29755 | 0.10529 | -0.18768 | -0.28381 | -0.27924 | -0.30212 | 0.10071 | 0.10986 | 61.0199 | 61.0565 | 122.6669 | 123.0515 | -0.18768 | 123.0469 | 60.9329 | -0.30212 | 123.0515 | -0.18768 | 60.9329 | 122.6669 | 123.0469 | -123.2437 | -123.2483
1711.7656 | 123.1842 | -60.878 | 62.059 | -0.19478 | -0.0056524 | -0.010062 | -0.002493 | 0.06096 | -0.0062911 | 0.065916 | -61.0016 | 62.0956 | -61.1618 | -61.1114 | 61.8576 | 0.11444 | 0.045776 | 0.2655 | 62.0956 | -61.1572 | -0.28381 | 0.036621 | -0.1236 | -0.23346 | -0.20142 | -0.27924 | 0.036621 | 0.16022 | 60.9238 | 61.1435 | 122.7356 | 122.9736 | -0.1236 | 122.9736 | 60.9924 | -0.27924 | 122.9736 | -0.1236 | 60.9924 | 122.7356 | 122.9736 | -123.2208 | -123.2162
1712.7656 | 123.1934 | -60.878 | 62.0316 | -0.13374 | -0.0071478 | -0.0089935 | -0.00057036 | 0.059678 | -0.0060775 | 0.06677 | -60.9879 | 62.0773 | -61.1481 | -61.0748 | 61.8942 | 0.13275 | 0.022888 | 0.25635 | 62.1094 | -61.1526 | -0.27008 | 0.045777 | -0.10986 | -0.19684 | -0.13733 | -0.27466 | 0.07782 | 0.16022 | 60.9009 | 61.1343 | 122.7722 | 122.9553 | -0.10986 | 122.9874 | 61.0107 | -0.27466 | 122.9553 | -0.10986 | 61.0107 | 122.7722 | 122.9874 | -123.1796 | -123.1842
1713.7656 | 123.1384 | -60.8826 | 62.1277 | -0.16426 | -0.0054388 | -0.0053619 | 0.0011386 | 0.059464 | -0.0033005 | 0.065275 | -61.0428 | 62.1368 | -61.171 | -61.1664 | 61.7981 | 0.032043 | 0.14648 | 0.16937 | 62.1368 | -61.1755 | -0.28839 | 0.009155 | -0.16022 | -0.28381 | -0.32959 | -0.29297 | 0.009155 | 0.12817 | 61.0291 | 61.0519 | 122.6807 | 123.0194 | -0.16022 | 123.0194 | 60.9146 | -0.29297 | 123.0194 | -0.16022 | 60.9146 | 122.6807 | 123.0194 | -123.2986 | -123.3032
1714.7656 | 123.0789 | -60.9009 | 62.0865 | -0.16426 | -0.0037298 | -0.0066437 | 7.0444e-05 | 0.059678 | -0.0058639 | 0.069761 | -61.0428 | 62.1231 | -61.1847 | -61.1481 | 61.7935 | 0.041199 | 0.15564 | 0.18768 | 62.1506 | -61.171 | -0.28381 | 0.036621 | -0.14191 | -0.24719 | -0.29297 | -0.27008 | 0.064087 | 0.14191 | 61.0565 | 61.0886 | 122.6944 | 123.024 | -0.14191 | 123.0515 | 60.9421 | -0.27008 | 123.024 | -0.14191 | 60.9421 | 122.6944 | 123.0515 | -123.2712 | -123.2574
1715.7656 | 123.0927 | -60.9009 | 62.0956 | -0.17952 | -0.005866 | -0.0079253 | 0.00092504 | 0.06096 | -0.0047957 | 0.066984 | -61.0519 | 62.1231 | -61.1938 | -61.1343 | 61.8073 | 0.050354 | 0.12817 | 0.20142 | 62.1231 | -61.1847 | -0.29297 | 0.027466 | -0.15106 | -0.23346 | -0.28839 | -0.28381 | 0.027466 | 0.14191 | 61.0291 | 61.1023 | 122.7081 | 123.024 | -0.15106 | 123.024 | 60.9512 | -0.28381 | 123.024 | -0.15106 | 60.9512 | 122.7081 | 123.024 | -123.2895 | -123.2803
1716.7656 | 123.111 | -60.8688 | 62.0636 | -0.16426 | -0.0060798 | -0.0051483 | 0.00092504 | 0.061387 | -0.0056503 | 0.067197 | -61.0016 | 62.0819 | -61.1755 | -61.1206 | 61.8347 | 0.068665 | 0.10071 | 0.22888 | 62.1277 | -61.1526 | -0.3067 | 0.01831 | -0.13275 | -0.25177 | -0.22888 | -0.28381 | 0.064087 | 0.17395 | 60.9695 | 61.0977 | 122.7036 | 122.9507 | -0.13275 | 122.9965 | 60.9375 | -0.28381 | 122.9507 | -0.13275 | 60.9375 | 122.7036 | 122.9965 | -123.2391 | -123.2162
1717.7656 | 123.1522 | -60.8734 | 62.059 | -0.17189 | -0.0067206 | -0.013693 | 0.00092504 | 0.060105 | -0.0052231 | 0.068479 | -60.9833 | 62.0865 | -61.1664 | -61.0977 | 61.8668 | 0.10529 | 0.045776 | 0.26093 | 62.1048 | -61.1435 | -0.29297 | 0.027466 | -0.10986 | -0.2243 | -0.19226 | -0.27008 | 0.045776 | 0.18311 | 60.9192 | 61.1343 | 122.7402 | 122.9599 | -0.10986 | 122.9782 | 60.9787 | -0.27008 | 122.9599 | -0.10986 | 60.9787 | 122.7402 | 122.9782 | -123.2254 | -123.2025
1718.7656 | 123.2162 | -60.8597 | 62.0041 | -0.095596 | -0.0084296 | -0.01113 | 0.0028476 | 0.060105 | -0.0045821 | 0.068052 | -60.965 | 62.0544 | -61.1435 | -61.0291 | 61.9308 | 0.25177 | 0.1831 | 0.082397 | 62.146 | -61.1389 | -0.28381 | 0.050354 | -0.10529 | -0.16937 | -0.073242 | -0.27924 | 0.14191 | 0.17853 | 61.0428 | 60.9421 | 122.7905 | 122.9141 | -0.10529 | 123.0057 | 61.1114 | -0.27924 | 122.9141 | -0.10529 | 61.1114 | 122.7905 | 123.0057 | -123.1476 | -123.143
1719.7656 | 123.2254 | -60.8597 | 62.0178 | -0.080337 | -0.0071478 | -0.011343 | -0.0012112 | 0.059891 | -0.0058639 | 0.067197 | -60.9512 | 62.0361 | -61.1572 | -61.0199 | 61.9171 | 0.13733 | -0.064087 | 0.28381 | 62.0819 | -61.1481 | -0.29755 | 0.018311 | -0.091553 | -0.16022 | -0.10071 | -0.28839 | 0.064087 | 0.20599 | 60.7956 | 61.1435 | 122.7768 | 122.8958 | -0.091553 | 122.9416 | 60.997 | -0.28839 | 122.8958 | -0.091553 | 60.997 | 122.7768 | 122.9416 | -123.175 | -123.1659
1720.7656 | 123.1705 | -60.8597 | 62.059 | -0.15663 | -0.0086432 | -0.0083527 | 0.00092504 | 0.061387 | -0.0062911 | 0.067411 | -60.9604 | 62.0636 | -61.1526 | -61.0748 | 61.8805 | 0.10986 | 0.022888 | 0.26093 | 62.1368 | -61.1252 | -0.29297 | 0.004578 | -0.10071 | -0.21515 | -0.17853 | -0.2655 | 0.07782 | 0.19226 | 60.8826 | 61.1206 | 122.7402 | 122.9233 | -0.10071 | 122.9965 | 60.9695 | -0.2655 | 122.9233 | -0.10071 | 60.9695 | 122.7402 | 122.9965 | -123.2117 | -123.1842
1721.7656 | 123.1888 | -60.878 | 62.0361 | -0.087967 | -0.0069342 | -0.013266 | 0.0017794 | 0.057969 | -0.0075729 | 0.066984 | -60.9833 | 62.0773 | -61.1481 | -61.0519 | 61.8896 | 0.13275 | -0.009155 | 0.27466 | 62.1048 | -61.1481 | -0.27008 | 0.041199 | -0.10528 | -0.17395 | -0.14648 | -0.27008 | 0.068664 | 0.1648 | 60.8688 | 61.1526 | 122.7676 | 122.9553 | -0.10528 | 122.9828 | 61.0107 | -0.27008 | 122.9553 | -0.10528 | 61.0107 | 122.7676 | 122.9828 | -123.1842 | -123.1842
1722.7656 | 123.23 | -60.8643 | 62.0224 | 0.48424 | -0.0073614 | -0.011557 | 0.0017794 | 0.059891 | -0.0062911 | 0.067624 | -61.0199 | 62.0728 | -61.1526 | -61.0565 | 61.9171 | 0.13733 | -0.050354 | 0.28381 | 62.059 | -61.1069 | -0.28839 | 0.050354 | -0.15564 | -0.19226 | -0.10529 | -0.24262 | 0.036621 | 0.13275 | 60.8139 | 61.1481 | 122.7814 | 122.937 | -0.15564 | 122.9233 | 61.0016 | -0.24262 | 122.937 | -0.15564 | 61.0016 | 122.7814 | 122.9233 | -123.175 | -123.1293
1723.7656 | 123.1979 | -60.8414 | 61.9904 | -0.11085 | -0.0097114 | -0.0089935 | 0.0011386 | 0.059251 | -0.0077865 | 0.068906 | -60.965 | 62.0544 | -61.171 | -61.0565 | 61.7752 | 0.33417 | 0.091553 | 0.07782 | 62.0865 | -61.1069 | -0.32959 | 0.064087 | -0.1236 | -0.21515 | -0.21515 | -0.2655 | 0.096131 | 0.20599 | 60.9329 | 60.9192 | 122.6166 | 122.8958 | -0.1236 | 122.9279 | 61.1755 | -0.2655 | 122.8958 | -0.1236 | 61.1755 | 122.6166 | 122.9279 | -123.1613 | -123.0972
1724.7656 | 123.2574 | -60.8414 | 62.0316 | -0.04982 | -0.0069342 | -0.01113 | 0.00028404 | 0.060532 | -0.0056503 | 0.068265 | -60.965 | 62.0224 | -61.1755 | -61.0153 | 61.9217 | 0.13733 | -0.059509 | 0.29297 | 62.0773 | -61.1114 | -0.33417 | -0.009155 | -0.1236 | -0.17395 | -0.10986 | -0.27008 | 0.045777 | 0.21057 | 60.7819 | 61.1343 | 122.7631 | 122.8638 | -0.1236 | 122.9187 | 60.9787 | -0.27008 | 122.8638 | -0.1236 | 60.9787 | 122.7631 | 122.9187 | -123.2071 | -123.143
1725.7656 | 123.2117 | -60.9055 | 62.0087 | 0.026474 | -0.0067206 | -0.010489 | 0.00049764 | 0.059037 | -0.0071457 | 0.069333 | -61.0153 | 62.0361 | -61.1618 | -61.0886 | 61.853 | 0.050354 | -0.07782 | 0.21057 | 62.0773 | -61.1298 | -0.25635 | 0.027466 | -0.10986 | -0.18311 | -0.15564 | -0.2243 | 0.068665 | 0.14648 | 60.8276 | 61.116 | 122.7585 | 122.9416 | -0.10986 | 122.9828 | 60.9558 | -0.2243 | 122.9416 | -0.10986 | 60.9558 | 122.7585 | 122.9828 | -123.1705 | -123.1384
1726.7656 | 123.1934 | -60.8459 | 62.027 | -0.057449 | -0.0069342 | -0.0098479 | -0.0016386 | 0.060319 | -0.0058639 | 0.067624 | -61.0428 | 62.0361 | -61.1847 | -61.1069 | 61.8393 | 0.036621 | -0.07782 | 0.16479 | 62.0819 | -61.1389 | -0.33874 | 0.009155 | -0.19684 | -0.26093 | -0.18768 | -0.29297 | 0.054931 | 0.14191 | 60.7681 | 61.0107 | 122.6852 | 122.8821 | -0.19684 | 122.9279 | 60.8826 | -0.29297 | 122.8821 | -0.19684 | 60.8826 | 122.6852 | 122.9279 | -123.2117 | -123.1659
1727.7656 | 123.2117 | -60.8505 | 62.0132 | -0.21767 | -0.0067206 | -0.0096343 | 0.00071144 | 0.057542 | -0.0045821 | 0.068479 | -60.9512 | 62.0499 | -61.1664 | -61.0199 | 61.9217 | 0.14648 | -0.09613 | 0.3067 | 62.0773 | -61.1114 | -0.31586 | 0.036621 | -0.10071 | -0.16937 | -0.091553 | -0.26093 | 0.064087 | 0.21515 | 60.7544 | 61.1572 | 122.7722 | 122.9004 | -0.10071 | 122.9279 | 60.997 | -0.26093 | 122.9004 | -0.10071 | 60.997 | 122.7722 | 122.9279 | -123.1796 | -123.1247
1728.7656 | 123.2254 | -60.8368 | 62.0224 | -0.034561 | -0.0090704 | -0.0089935 | 0.00049764 | 0.058823 | -0.0056503 | 0.067197 | -60.9741 | 62.0224 | -61.1801 | -61.0474 | 61.8851 | 0.11902 | -0.073242 | 0.27924 | 62.0728 | -61.1206 | -0.34332 | 0 | -0.13733 | -0.21057 | -0.13733 | -0.28381 | 0.050354 | 0.20599 | 60.7636 | 61.116 | 122.7219 | 122.8592 | -0.13733 | 122.9095 | 60.9558 | -0.28381 | 122.8592 | -0.13733 | 60.9558 | 122.7219 | 122.9095 | -123.2025 | -123.143
1729.7656 | 123.1842 | -60.8643 | 62.0132 | 0.0035856 | -0.0077888 | -0.013907 | 0.002634 | 0.058396 | -0.0054367 | 0.065061 | -61.0062 | 62.059 | -61.1618 | -61.0703 | 61.8713 | 0.07782 | -0.07782 | 0.24261 | 62.0544 | -61.1481 | -0.29755 | 0.045776 | -0.14191 | -0.20599 | -0.14191 | -0.28381 | 0.041198 | 0.15564 | 60.7864 | 61.1069 | 122.7356 | 122.9233 | -0.14191 | 122.9187 | 60.9421 | -0.28381 | 122.9233 | -0.14191 | 60.9421 | 122.7356 | 122.9187 | -123.175 | -123.1613
1730.7656 | 123.1934 | -60.9055 | 62.027 | 0.026474 | -0.0086432 | -0.010062 | 0.00071144 | 0.057969 | -0.0047957 | 0.065702 | -61.0153 | 62.0361 | -61.1664 | -61.0794 | 61.8805 | 0.086975 | -0.068665 | 0.19684 | 62.0819 | -61.1481 | -0.26093 | 0.009155 | -0.10986 | -0.17395 | -0.14648 | -0.24261 | 0.054931 | 0.15106 | 60.8368 | 61.1023 | 122.7859 | 122.9416 | -0.10986 | 122.9874 | 60.9924 | -0.24261 | 122.9416 | -0.10986 | 60.9924 | 122.7859 | 122.9874 | -123.1934 | -123.175
1731.7656 | 123.1705 | -60.8597 | 62.0224 | 0.17906 | -0.0054388 | -0.0092071 | -0.00035676 | 0.058396 | -0.0050095 | 0.06912 | -61.0336 | 62.0407 | -61.1755 | -61.0931 | 61.8256 | 0.032043 | -0.10071 | 0.17395 | 62.0407 | -61.1343 | -0.31586 | 0.01831 | -0.17395 | -0.23346 | -0.19684 | -0.27466 | 0.01831 | 0.14191 | 60.759 | 61.0336 | 122.6852 | 122.9004 | -0.17395 | 122.9004 | 60.8917 | -0.27466 | 122.9004 | -0.17395 | 60.8917 | 122.6852 | 122.9004 | -123.1979 | -123.1567
1732.7656 | 123.1384 | -60.9009 | 62.0407 | 0.17143 | -0.007575 | -0.010703 | 0.00049764 | 0.058823 | -0.0030869 | 0.067411 | -61.0519 | 62.0407 | -61.1755 | -61.1114 | 61.821 | 0.018311 | -0.10529 | 0.13275 | 62.0865 | -61.1389 | -0.27466 | 0 | -0.15106 | -0.21057 | -0.21973 | -0.23804 | 0.045777 | 0.1236 | 60.7956 | 61.0336 | 122.7219 | 122.9416 | -0.15106 | 122.9874 | 60.9192 | -0.23804 | 122.9416 | -0.15106 | 60.9192 | 122.7219 | 122.9874 | -123.2162 | -123.1796
1733.7656 | 123.1796 | -60.878 | 62.0132 | 0.18669 | -0.006507 | -0.0089935 | 0.0022066 | 0.06096 | -0.0065047 | 0.067838 | -61.0062 | 62.0132 | -61.1664 | -61.1114 | 61.8256 | 0.004578 | -0.15106 | 0.12817 | 62.0499 | -61.1252 | -0.28839 | 0 | -0.12817 | -0.23346 | -0.18768 | -0.24719 | 0.036621 | 0.16022 | 60.7269 | 61.0062 | 122.7036 | 122.8912 | -0.12817 | 122.9279 | 60.8826 | -0.24719 | 122.8912 | -0.12817 | 60.8826 | 122.7036 | 122.9279 | -123.1796 | -123.1384
1734.7656 | 123.1979 | -60.878 | 62.0224 | 0.11803 | -0.0084296 | -0.0077117 | 0.00028404 | 0.059464 | -0.0054367 | 0.06677 | -60.9283 | 62.0361 | -61.1572 | -61.0931 | 61.8439 | 0.032043 | -0.073242 | 0.16022 | 62.0544 | -61.1252 | -0.27924 | 0.013733 | -0.050354 | -0.21515 | -0.17853 | -0.24719 | 0.032043 | 0.22888 | 60.8047 | 61.0382 | 122.7219 | 122.9141 | -0.050354 | 122.9324 | 60.91 | -0.24719 | 122.9141 | -0.050354 | 60.91 | 122.7219 | 122.9324 | -123.1796 | -123.1476
1735.7656 | 123.2254 | -60.8688 | 62.0361 | 0.11803 | -0.0054388 | -0.0077117 | 0.00028404 | 0.059678 | -0.0045821 | 0.067411 | -61.0199 | 62.0499 | -61.1526 | -61.116 | 61.8256 | 0.018311 | -0.09613 | 0.14648 | 62.059 | -61.1618 | -0.28381 | 0.013733 | -0.15106 | -0.24719 | -0.21057 | -0.29297 | 0.022888 | 0.13275 | 60.7727 | 61.0153 | 122.6944 | 122.9187 | -0.15106 | 122.9279 | 60.8871 | -0.29297 | 122.9187 | -0.15106 | 60.8871 | 122.6944 | 122.9279 | -123.1888 | -123.1979
1736.7656 | 123.1842 | -60.8734 | 62.0224 | 0.17143 | -0.0062934 | -0.0092071 | 0.0013522 | 0.060319 | -0.0037277 | 0.069333 | -61.0336 | 62.0316 | -61.1847 | -61.1114 | 61.8301 | 0.018311 | -0.082397 | 0.14191 | 62.0316 | -61.1206 | -0.31128 | 0.009155 | -0.16022 | -0.23804 | -0.19226 | -0.24719 | 0.009155 | 0.15106 | 60.791 | 61.0153 | 122.7036 | 122.905 | -0.16022 | 122.905 | 60.8917 | -0.24719 | 122.905 | -0.16022 | 60.8917 | 122.7036 | 122.905 | -123.2071 | -123.143
1737.7656 | 123.1659 | -60.9055 | 62.0178 | 0.20195 | -0.006507 | -0.0083527 | 0.00092504 | 0.061387 | -0.0062911 | 0.068479 | -61.0291 | 62.0316 | -61.1847 | -61.1206 | 61.8347 | 0.027466 | -0.13275 | 0.13733 | 62.0361 | -61.1481 | -0.27923 | 0.013733 | -0.1236 | -0.21515 | -0.18311 | -0.24261 | 0.018311 | 0.15564 | 60.7727 | 61.0428 | 122.7402 | 122.937 | -0.1236 | 122.9416 | 60.9329 | -0.24261 | 122.937 | -0.1236 | 60.9329 | 122.7402 | 122.9416 | -123.2025 | -123.1659
1738.7656 | 123.1888 | -60.878 | 62.0041 | 0.18669 | -0.0077888 | -0.0072845 | 0.001993 | 0.060105 | -0.0056503 | 0.066343 | -61.0153 | 62.0407 | -61.1755 | -61.084 | 61.821 | 0.018311 | -0.16937 | 0.13275 | 62.0178 | -61.1389 | -0.29755 | 0.036621 | -0.13733 | -0.20599 | -0.1831 | -0.26093 | 0.013733 | 0.16022 | 60.7086 | 61.0107 | 122.699 | 122.9187 | -0.13733 | 122.8958 | 60.8963 | -0.26093 | 122.9187 | -0.13733 | 60.8963 | 122.699 | 122.8958 | -123.1796 | -123.143
1739.7656 | 123.2758 | -60.8643 | 62.0041 | 0.25536 | -0.0056524 | -0.0062163 | 0.0064792 | 0.062882 | -0.0080001 | 0.065702 | -60.9695 | 62.027 | -61.1755 | -61.0657 | 61.8759 | 0.022888 | -0.25635 | -0.045776 | 62.0087 | -61.1755 | -0.31128 | 0.022889 | -0.10529 | -0.20142 | -0.12817 | -0.31128 | 0.004578 | 0.20599 | 60.6079 | 60.8185 | 122.7402 | 122.8912 | -0.10529 | 122.8729 | 60.8871 | -0.31128 | 122.8912 | -0.10529 | 60.8871 | 122.7402 | 122.8729 | -123.1796 | -123.1796
1740.7656 | 123.2208 | -60.8871 | 61.9812 | 0.21721 | -0.0043708 | -0.011557 | 0.0049838 | 0.061387 | -0.0041549 | 0.067624 | -60.9879 | 62.0453 | -61.1847 | -61.084 | 61.853 | 0.032043 | -0.21057 | 0.13733 | 62.0178 | -61.1664 | -0.29755 | 0.064087 | -0.10071 | -0.19684 | -0.12817 | -0.27924 | 0.036621 | 0.19684 | 60.6766 | 61.0245 | 122.7402 | 122.9324 | -0.10071 | 122.905 | 60.9192 | -0.27924 | 122.9324 | -0.10071 | 60.9192 | 122.7402 | 122.905 | -123.1659 | -123.1476
1741.7656 | 123.1796 | -60.8871 | 61.9949 | 0.20958 | -0.0060798 | -0.0045075 | 0.0032748 | 0.06096 | -0.0056503 | 0.067838 | -60.997 | 62.059 | -61.1938 | -61.084 | 61.8484 | 0.036621 | -0.18768 | 0.15106 | 62.027 | -61.1389 | -0.3067 | 0.064087 | -0.10986 | -0.19684 | -0.14648 | -0.25177 | 0.032044 | 0.19684 | 60.6995 | 61.0382 | 122.7356 | 122.9462 | -0.10986 | 122.9141 | 60.9238 | -0.25177 | 122.9462 | -0.10986 | 60.9238 | 122.7356 | 122.9141 | -123.1888 | -123.1338
1742.7656 | 123.2025 | -60.8643 | 61.9995 | 0.12566 | -0.0056524 | -0.0030121 | 0.0011386 | 0.061814 | -0.0041549 | 0.069974 | -60.997 | 62.0773 | -61.1755 | -61.084 | 61.8668 | 0.050354 | -0.1831 | 0.15564 | 62.0224 | -61.1526 | -0.31128 | 0.07782 | -0.13275 | -0.21973 | -0.13275 | -0.28839 | 0.022888 | 0.17853 | 60.6812 | 61.0199 | 122.731 | 122.9416 | -0.13275 | 122.8867 | 60.9146 | -0.28839 | 122.9416 | -0.13275 | 60.9146 | 122.731 | 122.8867 | -123.175 | -123.1522
1743.7656 | 123.1934 | -60.8734 | 62.0132 | 0.22484 | -0.004798 | -0.0079253 | 0.0047702 | 0.063523 | -0.0069321 | 0.068479 | -60.9833 | 62.0636 | -61.1755 | -61.0428 | 61.8942 | 0.054932 | -0.17395 | 0.16479 | 62.059 | -61.1481 | -0.30212 | 0.050354 | -0.10986 | -0.16937 | -0.11902 | -0.27466 | 0.045776 | 0.19226 | 60.6995 | 61.0382 | 122.7676 | 122.937 | -0.10986 | 122.9324 | 60.9283 | -0.27466 | 122.937 | -0.10986 | 60.9283 | 122.7676 | 122.9324 | -123.1888 | -123.1613
1744.7656 | 123.1659 | -60.8871 | 61.972 | 0.25536 | -0.0043708 | -0.010916 | 0.0060518 | 0.062669 | -0.0050095 | 0.068052 | -60.9833 | 62.0544 | -61.1801 | -61.0794 | 61.8622 | 0.041199 | -0.19684 | 0.15564 | 62.0087 | -61.1526 | -0.29297 | 0.082397 | -0.09613 | -0.19226 | -0.10986 | -0.2655 | 0.036621 | 0.19684 | 60.6903 | 61.0428 | 122.7493 | 122.9416 | -0.09613 | 122.8958 | 60.9283 | -0.2655 | 122.9416 | -0.09613 | 60.9283 | 122.7493 | 122.8958 | -123.1522 | -123.1247
1745.7656 | 123.2254 | -60.9146 | 61.9904 | 0.26299 | -0.0056524 | -0.0092071 | 0.0056246 | 0.060746 | -0.0045821 | 0.067197 | -60.9879 | 62.1048 | -61.1847 | -61.0703 | 61.853 | 0.041199 | -0.19684 | 0.14191 | 62.0224 | -61.1847 | -0.27008 | 0.11444 | -0.073242 | -0.15564 | -0.13733 | -0.27008 | 0.032044 | 0.19684 | 60.7178 | 61.0565 | 122.7676 | 123.0194 | -0.073242 | 122.937 | 60.9558 | -0.27008 | 123.0194 | -0.073242 | 60.9558 | 122.7676 | 122.937 | -123.175 | -123.175
1746.7656 | 123.1338 | -60.9146 | 62.027 | 0.19432 | -0.0037298 | -0.0068573 | 0.0034884 | 0.063309 | -0.0037277 | 0.068052 | -61.0565 | 62.1597 | -61.2259 | -61.1664 | 61.7798 | -0.036621 | -0.068665 | 0.041199 | 62.0316 | -61.1938 | -0.31128 | 0.13275 | -0.14191 | -0.25177 | -0.24719 | -0.27924 | 0.004577 | 0.16937 | 60.8459 | 60.9558 | 122.6944 | 123.0743 | -0.14191 | 122.9462 | 60.878 | -0.27924 | 123.0743 | -0.14191 | 60.878 | 122.6944 | 122.9462 | -123.2529 | -123.2208
1747.7656 | 123.1934 | -60.8963 | 62.027 | 0.27824 | -0.0037298 | -0.0081389 | 0.0030612 | 0.062241 | -0.0039413 | 0.066984 | -61.0336 | 62.114 | -61.2122 | -61.1252 | 61.8347 | 0 | -0.15106 | 0.11902 | 62.0316 | -61.1801 | -0.31586 | 0.086975 | -0.13733 | -0.22888 | -0.19226 | -0.28381 | 0.004577 | 0.17853 | 60.7452 | 61.0153 | 122.731 | 123.0103 | -0.13733 | 122.9279 | 60.8963 | -0.28381 | 123.0103 | -0.13733 | 60.8963 | 122.731 | 122.9279 | -123.2391 | -123.2071
1748.7656 | 123.23 | -60.8917 | 61.9995 | 0.28587 | -0.0056524 | -0.0034393 | 0.0024202 | 0.0616 | -0.0039413 | 0.069333 | -61.0062 | 62.0956 | -61.1801 | -61.0886 | 61.853 | 0.054932 | -0.21057 | 0.12817 | 61.9949 | -61.1664 | -0.28839 | 0.09613 | -0.11444 | -0.19684 | -0.14649 | -0.27466 | -0.004578 | 0.17395 | 60.6812 | 61.0199 | 122.7448 | 122.9874 | -0.11444 | 122.8867 | 60.9467 | -0.27466 | 122.9874 | -0.11444 | 60.9467 | 122.7448 | 122.8867 | -123.1796 | -123.1659
1749.7656 | 123.2162 | -60.8597 | 62.0041 | 0.49187 | -0.0056524 | -0.010916 | 0.0024202 | 0.062455 | -0.0058639 | 0.067197 | -60.997 | 62.0819 | -61.1847 | -61.0977 | 61.8576 | 0.032043 | -0.17395 | 0.14191 | 62.0407 | -61.1664 | -0.32501 | 0.07782 | -0.13733 | -0.23804 | -0.14648 | -0.3067 | 0.036621 | 0.18768 | 60.6857 | 61.0016 | 122.7173 | 122.9416 | -0.13733 | 122.9004 | 60.8917 | -0.3067 | 122.9416 | -0.13733 | 60.8917 | 122.7173 | 122.9004 | -123.1888 | -123.1705
1750.7656 | 123.1842 | -60.8917 | 61.9904 | 0.27824 | -0.0052252 | -0.0042937 | 0.0064792 | 0.061173 | -0.0037277 | 0.065488 | -61.0291 | 62.1185 | -61.1938 | -61.1206 | 61.8439 | 0.027466 | -0.16937 | 0.13733 | 62.0316 | -61.203 | -0.30212 | 0.12817 | -0.13733 | -0.22888 | -0.14648 | -0.31128 | 0.041199 | 0.1648 | 60.7224 | 61.0291 | 122.7356 | 123.0103 | -0.13733 | 122.9233 | 60.9192 | -0.31128 | 123.0103 | -0.13733 | 60.9192 | 122.7356 | 122.9233 | -123.1842 | -123.1934
1751.7656 | 123.2071 | -60.8963 | 61.9949 | 0.25536 | -0.0033026 | -0.0047211 | 0.003702 | 0.062882 | -0.0054367 | 0.068906 | -61.0428 | 62.1185 | -61.1984 | -61.1298 | 61.8118 | 0.013733 | -0.13733 | 0.1236 | 62.027 | -61.1893 | -0.30212 | 0.1236 | -0.14648 | -0.23346 | -0.1831 | -0.29297 | 0.032044 | 0.15564 | 60.759 | 61.0199 | 122.7081 | 123.0148 | -0.14648 | 122.9233 | 60.91 | -0.29297 | 123.0148 | -0.14648 | 60.91 | 122.7081 | 122.9233 | -123.1934 | -123.1842
1752.7656 | 123.175 | -60.9055 | 62.0178 | 0.26299 | -0.0045844 | -0.0074981 | 0.003702 | 0.063096 | -0.0028731 | 0.068906 | -61.0565 | 62.1368 | -61.2305 | -61.1572 | 61.8118 | -0.013733 | -0.11444 | 0.091553 | 62.0407 | -61.1938 | -0.32501 | 0.11902 | -0.15106 | -0.25177 | -0.20599 | -0.28839 | 0.022888 | 0.17395 | 60.791 | 60.997 | 122.7173 | 123.0423 | -0.15106 | 122.9462 | 60.8917 | -0.28839 | 123.0423 | -0.15106 | 60.8917 | 122.7173 | 122.9462 | -123.2483 | -123.2117
1753.7656 | 123.1247 | -60.9055 | 62.0453 | 0.19432 | -0.0028754 | -0.0079253 | 0.0060518 | 0.064591 | -0.0022323 | 0.066984 | -60.9787 | 62.1277 | -61.2442 | -61.1893 | 61.7798 | -0.013733 | 0.032043 | 0.064087 | 62.1048 | -61.2076 | -0.33875 | 0.082398 | -0.073242 | -0.28381 | -0.2655 | -0.30212 | 0.059509 | 0.2655 | 60.9375 | 60.9695 | 122.6852 | 123.0331 | -0.073242 | 123.0103 | 60.8917 | -0.30212 | 123.0331 | -0.073242 | 60.8917 | 122.6852 | 123.0103 | -123.2895 | -123.2529
1754.7656 | 123.1567 | -60.9192 | 62.0316 | 0.24773 | -0.0041572 | -0.0094207 | 0.0041292 | 0.062455 | -0.0024459 | 0.066556 | -61.0657 | 62.1689 | -61.203 | -61.1893 | 61.7889 | -0.032043 | -0.07782 | 0.054932 | 62.0544 | -61.2259 | -0.28381 | 0.13733 | -0.14648 | -0.27008 | -0.24262 | -0.3067 | 0.022888 | 0.13733 | 60.8414 | 60.9741 | 122.7081 | 123.0881 | -0.14648 | 122.9736 | 60.8871 | -0.3067 | 123.0881 | -0.14648 | 60.8871 | 122.7081 | 122.9736 | -123.2346 | -123.2574
1755.7656 | 123.1979 | -60.8917 | 61.9904 | 0.27061 | -0.0043708 | -0.0081389 | 0.0032748 | 0.063523 | -0.0030869 | 0.067624 | -61.0336 | 62.1277 | -61.235 | -61.1252 | 61.821 | 0.018311 | -0.14191 | 0.1236 | 62.059 | -61.1984 | -0.34332 | 0.13733 | -0.14191 | -0.23346 | -0.16937 | -0.3067 | 0.068665 | 0.20142 | 60.7498 | 61.0153 | 122.7127 | 123.0194 | -0.14191 | 122.9507 | 60.91 | -0.3067 | 123.0194 | -0.14191 | 60.91 | 122.7127 | 122.9507 | -123.2254 | -123.1888
1756.7656 | 123.1522 | -60.9055 | 61.9858 | 0.26299 | -0.0033026 | -0.0074981 | 0.0028476 | 0.063523 | -0.0037277 | 0.068265 | -61.0611 | 62.1506 | -61.2122 | -61.171 | 61.7935 | -0.009155 | -0.10071 | 0.09613 | 62.0316 | -61.2122 | -0.3067 | 0.16479 | -0.15564 | -0.2655 | -0.19226 | -0.3067 | 0.045776 | 0.15106 | 60.8047 | 61.0016 | 122.699 | 123.056 | -0.15564 | 122.937 | 60.8963 | -0.3067 | 123.056 | -0.15564 | 60.8963 | 122.699 | 122.937 | -123.1979 | -123.1979
1757.7812 | 123.1705 | -60.8688 | 62.0499 | -0.11848 | -0.0067206 | -0.011343 | -0.0018522 | 0.062455 | -0.0041549 | 0.068479 | -61.0016 | 62.0728 | -61.1847 | -61.0703 | 61.8896 | 0.15564 | 0 | 0.27924 | 62.0819 | -61.1664 | -0.31586 | 0.022888 | -0.13275 | -0.20142 | -0.16022 | -0.29755 | 0.032043 | 0.1831 | 60.8688 | 61.1481 | 122.7585 | 122.9416 | -0.13275 | 122.9507 | 61.0245 | -0.29755 | 122.9416 | -0.13275 | 61.0245 | 122.7585 | 122.9507 | -123.2346 | -123.2162
1758.7656 | 123.111 | -60.9009 | 61.9995 | 0.24773 | -0.0035162 | -0.0072845 | 0.003702 | 0.063309 | -0.0043685 | 0.068693 | -61.0565 | 62.146 | -61.1755 | -61.1755 | 61.7615 | -0.045776 | -0.068665 | 0.050354 | 62.0956 | -61.2122 | -0.27466 | 0.14648 | -0.15564 | -0.27466 | -0.23804 | -0.31128 | 0.09613 | 0.11902 | 60.8322 | 60.9512 | 122.6624 | 123.0469 | -0.15564 | 122.9965 | 60.8551 | -0.31128 | 123.0469 | -0.15564 | 60.8551 | 122.6624 | 122.9965 | -123.175 | -123.2117
1759.7656 | 123.0972 | -60.9192 | 62.0132 | 0.1638 | -0.003089 | -0.0085663 | 0.0045566 | 0.062028 | -0.0037277 | 0.067197 | -61.0611 | 62.146 | -61.2076 | -61.1938 | 61.7752 | -0.050354 | -0.045776 | 0.041199 | 62.059 | -61.2305 | -0.28839 | 0.13275 | -0.14191 | -0.27466 | -0.23804 | -0.31128 | 0.045776 | 0.14648 | 60.8734 | 60.9604 | 122.6944 | 123.0652 | -0.14191 | 122.9782 | 60.8688 | -0.31128 | 123.0652 | -0.14191 | 60.8688 | 122.6944 | 122.9782 | -123.2208 | -123.2437
1760.7656 | 123.0652 | -60.91 | 62.0407 | 0.10277 | -0.0039434 | -0.0062163 | 0.0062656 | 0.062882 | -0.0022323 | 0.067411 | -61.0703 | 62.1735 | -61.2122 | -61.2122 | 61.7249 | -0.068665 | 0.032043 | 0.041199 | 62.0682 | -61.2579 | -0.30212 | 0.13275 | -0.16022 | -0.30212 | -0.31586 | -0.3479 | 0.027466 | 0.14191 | 60.9421 | 60.9512 | 122.6349 | 123.0835 | -0.16022 | 122.9782 | 60.8414 | -0.3479 | 123.0835 | -0.16022 | 60.8414 | 122.6349 | 122.9782 | -123.2529 | -123.2986
1761.7656 | 123.0972 | -60.9329 | 62.027 | 0.2401 | -0.0026618 | -0.0034393 | 0.0030612 | 0.061814 | -0.0035141 | 0.068479 | -61.3358 | 62.1277 | -61.2488 | -61.1755 | 61.7752 | -0.041199 | -0.004578 | 0.022888 | 62.0956 | -61.2213 | -0.31586 | 0.10071 | -0.40283 | -0.24262 | -0.25177 | -0.28839 | 0.068664 | -0.086975 | 60.9283 | 60.9558 | 122.7081 | 123.0606 | -0.40283 | 123.0286 | 60.8917 | -0.28839 | 123.0606 | -0.40283 | 60.8917 | 122.7081 | 123.0286 | -123.2758 | -123.2483
1762.7812 | 123.23 | -60.8826 | 62.0361 | -0.034561 | -0.008216 | -0.011984 | -0.0022794 | 0.061173 | -0.0047957 | 0.068906 | -61.0245 | 62.1002 | -61.1664 | -61.0931 | 61.8896 | 0.11444 | -0.059509 | 0.25177 | 62.0728 | -61.1618 | -0.28381 | 0.064087 | -0.14191 | -0.21057 | -0.14648 | -0.27924 | 0.036621 | 0.14191 | 60.8231 | 61.1343 | 122.7722 | 122.9828 | -0.14191 | 122.9553 | 60.997 | -0.27924 | 122.9828 | -0.14191 | 60.997 | 122.7722 | 122.9553 | -123.2025 | -123.1979
1763.7656 | 123.143 | -60.9055 | 62.0316 | 0.17143 | -0.0041572 | -0.0072845 | 0.0066928 | 0.060105 | -0.0045821 | 0.067838 | -61.0519 | 62.1231 | -61.1984 | -61.1847 | 61.7477 | -0.041199 | -0.050354 | 0.050354 | 62.0773 | -61.2122 | -0.29297 | 0.091553 | -0.14648 | -0.27923 | -0.28381 | -0.3067 | 0.045777 | 0.14648 | 60.8551 | 60.9558 | 122.6532 | 123.0286 | -0.14648 | 122.9828 | 60.8643 | -0.3067 | 123.0286 | -0.14648 | 60.8643 | 122.6532 | 122.9828 | -123.23 | -123.2437
1764.7656 | 123.1064 | -60.9192 | 62.0178 | 0.19432 | -0.0015936 | -0.0042937 | 0.0030612 | 0.061387 | -0.0026595 | 0.068052 | -61.0611 | 62.1414 | -61.235 | -61.2076 | 61.7432 | -0.059509 | -0.045776 | 0.036621 | 62.0544 | -61.2122 | -0.31586 | 0.1236 | -0.14191 | -0.28839 | -0.27466 | -0.29297 | 0.036621 | 0.17395 | 60.8734 | 60.9558 | 122.6624 | 123.0606 | -0.14191 | 122.9736 | 60.8597 | -0.29297 | 123.0606 | -0.14191 | 60.8597 | 122.6624 | 122.9736 | -123.2529 | -123.23
1765.7656 | 123.1155 | -60.9329 | 62.027 | -0.24818 | -0.0039434 | -0.0060027 | 0.0073336 | 0.063523 | -0.0050095 | 0.069974 | -61.0565 | 62.146 | -61.2122 | -61.2122 | 61.7569 | -0.050354 | -0.013733 | 0.041199 | 62.0773 | -61.2213 | -0.27924 | 0.11902 | -0.1236 | -0.27924 | -0.27008 | -0.28839 | 0.050354 | 0.15564 | 60.9192 | 60.9741 | 122.6898 | 123.0789 | -0.1236 | 123.0103 | 60.8826 | -0.28839 | 123.0789 | -0.1236 | 60.8826 | 122.6898 | 123.0103 | -123.2391 | -123.2483
1766.7656 | 123.0835 | -60.9192 | 62.059 | -1.652 | -0.0043708 | -0.010062 | 0.0045566 | 0.063309 | -0.0035141 | 0.068052 | -61.0428 | 62.1826 | -61.2213 | -61.2213 | 61.7432 | -0.07782 | -0.018311 | 0.050354 | 62.0453 | -61.2625 | -0.30212 | 0.1236 | -0.1236 | -0.30212 | -0.31586 | -0.34332 | -0.013733 | 0.17853 | 60.9009 | 60.9695 | 122.6624 | 123.1018 | -0.1236 | 122.9645 | 60.8414 | -0.34332 | 123.1018 | -0.1236 | 60.8414 | 122.6624 | 122.9645 | -123.2803 | -123.3215
1767.7812 | 123.2025 | -60.8093 | 62.0453 | -0.14137 | -0.0088568 | -0.0066437 | -0.0048428 | 0.059891 | -0.0050095 | 0.068265 | -60.997 | 62.0911 | -61.1572 | -61.0611 | 61.9034 | 0.13733 | -0.045776 | 0.3067 | 62.0224 | -61.1343 | -0.3479 | 0.045776 | -0.18768 | -0.25177 | -0.14191 | -0.32501 | -0.022888 | 0.16022 | 60.7636 | 61.116 | 122.7127 | 122.9004 | -0.18768 | 122.8317 | 60.9467 | -0.32501 | 122.9004 | -0.18768 | 60.9467 | 122.7127 | 122.8317 | -123.2025 | -123.1796
1768.7656 | 123.1064 | -60.9009 | 62.0178 | 0.22484 | -0.0028754 | -0.0036529 | 0.0047702 | 0.064378 | -0.0043685 | 0.069333 | -61.0565 | 62.1323 | -61.2213 | -61.1847 | 61.7844 | -0.054932 | -0.082397 | 0.050354 | 62.0911 | -61.2076 | -0.32043 | 0.11444 | -0.15564 | -0.28381 | -0.23346 | -0.3067 | 0.073242 | 0.16479 | 60.8185 | 60.9512 | 122.6852 | 123.0331 | -0.15564 | 122.9919 | 60.8459 | -0.3067 | 123.0331 | -0.15564 | 60.8459 | 122.6852 | 122.9919 | -123.2391 | -123.2254
1769.7656 | 123.1201 | -60.9238 | 62.0316 | 0.14854 | -0.0052252 | -0.0077117 | 0.0056246 | 0.063096 | -0.0030869 | 0.067411 | -61.0474 | 62.146 | -61.203 | -61.1893 | 61.7569 | -0.059509 | -0.054932 | 0.041199 | 62.0819 | -61.2167 | -0.27924 | 0.11444 | -0.1236 | -0.2655 | -0.27466 | -0.29297 | 0.050354 | 0.15564 | 60.8688 | 60.965 | 122.6807 | 123.0698 | -0.1236 | 123.0057 | 60.8643 | -0.29297 | 123.0698 | -0.1236 | 60.8643 | 122.6807 | 123.0057 | -123.2346 | -123.2483
1770.7656 | 123.0881 | -60.9192 | 61.9949 | 0.41557 | -0.0024482 | -0.0057891 | 0.0062656 | 0.063096 | -0.0045821 | 0.067411 | -61.0519 | 62.1552 | -61.2259 | -61.1893 | 61.7523 | -0.059509 | -0.032043 | 0.041199 | 62.0544 | -61.2442 | -0.3067 | 0.16022 | -0.13275 | -0.27008 | -0.24262 | -0.32501 | 0.059509 | 0.17395 | 60.8871 | 60.9604 | 122.6715 | 123.0743 | -0.13275 | 122.9736 | 60.8597 | -0.32501 | 123.0743 | -0.13275 | 60.8597 | 122.6715 | 122.9736 | -123.2208 | -123.2391
1771.7656 | 123.0881 | -60.9283 | 62.0316 | -0.15663 | -0.0060798 | -0.0077117 | 0.004343 | 0.060746 | -0.0013779 | 0.067624 | -61.0748 | 62.1597 | -61.1801 | -61.1893 | 61.7432 | -0.050354 | -0.027466 | 0.041199 | 62.0773 | -61.2442 | -0.25177 | 0.12817 | -0.14648 | -0.26093 | -0.28839 | -0.31586 | 0.045777 | 0.10529 | 60.9009 | 60.9695 | 122.6715 | 123.0881 | -0.14648 | 123.0057 | 60.878 | -0.31586 | 123.0881 | -0.14648 | 60.878 | 122.6715 | 123.0057 | -123.2117 | -123.2758
1772.7656 | 123.1476 | -60.8917 | 62.0224 | 0.38506 | -0.0035162 | -0.0072845 | -0.0037748 | 0.06096 | -0.0020187 | 0.068693 | -61.0931 | 62.1414 | -61.1618 | -61.1435 | 61.821 | 0.050354 | -0.054932 | 0.16937 | 62.0499 | -61.2167 | -0.27008 | 0.11902 | -0.20142 | -0.25177 | -0.20142 | -0.32501 | 0.027466 | 0.068664 | 60.8368 | 61.0611 | 122.7127 | 123.0331 | -0.20142 | 122.9416 | 60.9421 | -0.32501 | 123.0331 | -0.20142 | 60.9421 | 122.7127 | 122.9416 | -123.1842 | -123.2391
1773.7656 | 123.0881 | -60.9283 | 62.0499 | 0.13329 | -0.0026618 | -0.0051483 | 0.0056246 | 0.062669 | -0.0065047 | 0.06677 | -61.0382 | 62.2009 | -61.2076 | -61.1847 | 61.7523 | -0.054932 | 0.027466 | 0.045776 | 62.1048 | -61.2259 | -0.27924 | 0.15106 | -0.10986 | -0.25635 | -0.29755 | -0.29755 | 0.054931 | 0.16937 | 60.9558 | 60.9741 | 122.6807 | 123.1293 | -0.10986 | 123.0331 | 60.8734 | -0.29755 | 123.1293 | -0.10986 | 60.8734 | 122.6807 | 123.0331 | -123.2574 | -123.2758
1774.7656 | 123.0972 | -60.9329 | 62.0407 | 0.056992 | -0.0037298 | -0.0062163 | 0.0056246 | 0.062669 | -0.0026595 | 0.066556 | -61.0382 | 62.1826 | -61.1984 | -61.1755 | 61.7661 | -0.041199 | 0.041199 | 0.073242 | 62.0956 | -61.2534 | -0.2655 | 0.14191 | -0.10529 | -0.24262 | -0.27466 | -0.32044 | 0.054932 | 0.16022 | 60.9741 | 61.0062 | 122.699 | 123.1155 | -0.10529 | 123.0286 | 60.8917 | -0.32044 | 123.1155 | -0.10529 | 60.8917 | 122.699 | 123.0286 | -123.2391 | -123.2941
1775.7656 | 123.111 | -60.9375 | 62.0361 | 0.32402 | -0.0018072 | -0.010916 | 0.004343 | 0.062028 | -0.0033005 | 0.067838 | -61.0336 | 62.1643 | -61.1984 | -61.1938 | 61.7569 | -0.082397 | -0.032043 | 0.050354 | 62.0819 | -61.235 | -0.26093 | 0.12817 | -0.09613 | -0.25635 | -0.27924 | -0.29755 | 0.045776 | 0.16479 | 60.9055 | 60.9879 | 122.6944 | 123.1018 | -0.09613 | 123.0194 | 60.8551 | -0.29755 | 123.1018 | -0.09613 | 60.8551 | 122.6944 | 123.0194 | -123.2346 | -123.2712
1776.7656 | 123.1247 | -60.9009 | 62.0361 | 0.21721 | -0.0041572 | -0.0045075 | 0.0024202 | 0.063096 | -0.0015915 | 0.069547 | -61.3541 | 62.1323 | -61.235 | -61.171 | 61.7752 | -0.054932 | 0.009155 | 0.022888 | 62.0911 | -61.2534 | -0.33417 | 0.09613 | -0.45319 | -0.27008 | -0.26093 | -0.35248 | 0.054931 | -0.11902 | 60.91 | 60.9238 | 122.6761 | 123.0331 | -0.45319 | 122.9919 | 60.8459 | -0.35248 | 123.0331 | -0.45319 | 60.8459 | 122.6761 | 122.9919 | -123.2712 | -123.2895
1777.7656 | 123.0927 | -60.9146 | 62.0316 | 0.20958 | -0.0039434 | -0.0070709 | 0.003702 | 0.063096 | -0.0015915 | 0.06912 | -61.0794 | 62.1918 | -61.2259 | -61.3815 | 61.4731 | -0.21057 | 0.19226 | 0.036621 | 62.0956 | -61.2396 | -0.31128 | 0.16022 | -0.1648 | -0.46692 | -0.55847 | -0.32501 | 0.064087 | 0.14648 | 61.1069 | 60.9512 | 122.3877 | 123.1064 | -0.1648 | 123.0103 | 60.704 | -0.32501 | 123.1064 | -0.1648 | 60.704 | 122.3877 | 123.0103 | -123.2574 | -123.2712
1778.7656 | 123.0927 | -60.91 | 62.027 | 0.12566 | -0.0039434 | -0.0066437 | 0.0064792 | 0.065018 | -0.0022323 | 0.067624 | -61.0382 | 62.178 | -61.1847 | -61.1847 | 61.7661 | -0.036621 | 0.022888 | 0.07782 | 62.1277 | -61.2122 | -0.27466 | 0.15106 | -0.12817 | -0.27466 | -0.26093 | -0.30212 | 0.10071 | 0.14648 | 60.9329 | 60.9879 | 122.6761 | 123.0881 | -0.12817 | 123.0377 | 60.8734 | -0.30212 | 123.0881 | -0.12817 | 60.8734 | 122.6761 | 123.0377 | -123.2117 | -123.2391
1779.7656 | 123.0789 | -60.9283 | 62.0361 | 0.20958 | -0.0050116 | -0.0045075 | 0.0049838 | 0.065659 | -0.0037277 | 0.066343 | -61.0886 | 62.1964 | -61.2213 | -61.2167 | 61.7249 | -0.054932 | 0.009155 | 0.059509 | 62.1002 | -61.235 | -0.29297 | 0.16022 | -0.16022 | -0.28839 | -0.31128 | -0.3067 | 0.064087 | 0.13275 | 60.9375 | 60.9879 | 122.6532 | 123.1247 | -0.16022 | 123.0286 | 60.8734 | -0.3067 | 123.1247 | -0.16022 | 60.8734 | 122.6532 | 123.0286 | -123.2574 | -123.2712
1780.7656 | 123.1155 | -60.91 | 62.0636 | 0.049362 | -0.0037298 | -0.0060027 | 0.0051974 | 0.06395 | -0.0035141 | 0.066556 | -61.0107 | 62.178 | -61.2213 | -61.1618 | 61.7981 | 0.013733 | -0.004578 | 0.11444 | 62.1048 | -61.2259 | -0.31128 | 0.11444 | -0.10071 | -0.25177 | -0.2655 | -0.31586 | 0.041198 | 0.21057 | 60.9055 | 61.0245 | 122.7081 | 123.0881 | -0.10071 | 123.0148 | 60.9238 | -0.31586 | 123.0881 | -0.10071 | 60.9238 | 122.7081 | 123.0148 | -123.2849 | -123.2895
1781.7656 | 123.1018 | -60.9055 | 62.027 | 0.011215 | -0.0026618 | -0.011771 | 0.0028476 | 0.062669 | -0.0056503 | 0.068265 | -61.0062 | 62.178 | -61.1984 | -61.1389 | 61.8118 | 0.027466 | 0.013733 | 0.15106 | 62.1048 | -61.203 | -0.29297 | 0.15106 | -0.10071 | -0.23346 | -0.21515 | -0.29755 | 0.077819 | 0.19226 | 60.9192 | 61.0565 | 122.7173 | 123.0835 | -0.10071 | 123.0103 | 60.9329 | -0.29755 | 123.0835 | -0.10071 | 60.9329 | 122.7173 | 123.0103 | -123.2254 | -123.23
1782.7656 | 123.0743 | -60.9146 | 62.0316 | 0.15617 | -0.0011664 | -0.0068573 | 0.0045566 | 0.062882 | -0.0047957 | 0.068479 | -61.0748 | 62.1826 | -61.235 | -61.2122 | 61.7432 | -0.059509 | -0.009155 | 0.036621 | 62.0819 | -61.2671 | -0.32043 | 0.15106 | -0.16022 | -0.29755 | -0.28839 | -0.35248 | 0.050354 | 0.16022 | 60.9055 | 60.9512 | 122.6578 | 123.0972 | -0.16022 | 122.9965 | 60.8551 | -0.35248 | 123.0972 | -0.16022 | 60.8551 | 122.6578 | 122.9965 | -123.2666 | -123.2986
1783.7656 | 123.1018 | -60.9283 | 62.0316 | 0.17906 | -0.0035162 | -0.0064301 | 0.0062656 | 0.064378 | -0.0037277 | 0.066343 | -61.0657 | 62.1872 | -61.2122 | -61.2122 | 61.7432 | -0.059509 | 0.009155 | 0.036621 | 62.1048 | -61.235 | -0.28381 | 0.15564 | -0.13733 | -0.28381 | -0.28839 | -0.3067 | 0.073242 | 0.14648 | 60.9375 | 60.965 | 122.6715 | 123.1155 | -0.13733 | 123.0331 | 60.8688 | -0.3067 | 123.1155 | -0.13733 | 60.8688 | 122.6715 | 123.0331 | -123.2437 | -123.2666
1784.7656 | 123.0972 | -60.9192 | 62.0499 | -0.026932 | -0.0045844 | -0.0034393 | 0.0047702 | 0.064378 | -0.0039413 | 0.068265 | -61.0107 | 62.1689 | -61.1755 | -61.1481 | 61.8118 | 0.013733 | 0.032043 | 0.13733 | 62.1185 | -61.2305 | -0.25635 | 0.11902 | -0.091553 | -0.22888 | -0.23804 | -0.31128 | 0.068664 | 0.16479 | 60.9512 | 61.0565 | 122.731 | 123.0881 | -0.091553 | 123.0377 | 60.9329 | -0.31128 | 123.0881 | -0.091553 | 60.9329 | 122.731 | 123.0377 | -123.2254 | -123.2803
1785.7656 | 123.0789 | -60.9238 | 62.0316 | 0.072251 | -0.0022346 | -0.0055755 | 0.005411 | 0.065018 | -0.0026595 | 0.066556 | -61.0519 | 62.1872 | -61.1938 | -61.1847 | 61.7661 | -0.022888 | 0.018311 | 0.064087 | 62.1002 | -61.2213 | -0.27008 | 0.15564 | -0.12817 | -0.26093 | -0.2655 | -0.29755 | 0.068665 | 0.14191 | 60.9421 | 60.9879 | 122.6898 | 123.111 | -0.12817 | 123.024 | 60.9009 | -0.29755 | 123.111 | -0.12817 | 60.9009 | 122.6898 | 123.024 | -123.2254 | -123.2529
1786.7656 | 123.1201 | -60.9283 | 62.0453 | 0.07988 | -0.0022346 | -0.0060027 | 0.0051974 | 0.062669 | -0.0043685 | 0.069761 | -61.0428 | 62.1964 | -61.1938 | -61.1755 | 61.7706 | -0.013733 | 0.022888 | 0.091553 | 62.1185 | -61.2625 | -0.2655 | 0.15106 | -0.11444 | -0.24719 | -0.27466 | -0.33417 | 0.073242 | 0.15106 | 60.9512 | 61.0199 | 122.699 | 123.1247 | -0.11444 | 123.0469 | 60.9146 | -0.33417 | 123.1247 | -0.11444 | 60.9146 | 122.699 | 123.0469 | -123.2391 | -123.3078
1787.7656 | 123.1018 | -60.9192 | 62.0636 | -0.011673 | -0.0045844 | -0.0038665 | 0.0041292 | 0.06395 | -0.0013779 | 0.067838 | -60.9879 | 62.2009 | -61.1801 | -61.171 | 61.7203 | -0.041199 | 0.068665 | 0.13733 | 62.1094 | -61.2396 | -0.26093 | 0.13733 | -0.068665 | -0.25177 | -0.34332 | -0.32043 | 0.045776 | 0.19226 | 60.9879 | 61.0565 | 122.6395 | 123.1201 | -0.068665 | 123.0286 | 60.878 | -0.32043 | 123.1201 | -0.068665 | 60.878 | 122.6395 | 123.0286 | -123.2437 | -123.3032
1788.7656 | 123.1522 | -60.8871 | 62.027 | -0.057449 | -0.0022346 | -0.0072845 | 0.005411 | 0.064378 | -0.0043685 | 0.068693 | -61.0153 | 62.2238 | -61.1801 | -61.1298 | 61.8393 | 0.059509 | 0.032043 | 0.17853 | 62.1048 | -61.2167 | -0.29297 | 0.19684 | -0.12817 | -0.24262 | -0.18768 | -0.32959 | 0.077819 | 0.16479 | 60.9192 | 61.0657 | 122.7264 | 123.111 | -0.12817 | 122.9919 | 60.9467 | -0.32959 | 123.111 | -0.12817 | 60.9467 | 122.7264 | 122.9919 | -123.2071 | -123.2437
1789.7656 | 123.0835 | -60.9192 | 62.0453 | 0.11803 | -0.0024482 | -0.0040801 | 0.0056246 | 0.06395 | -0.0035141 | 0.067624 | -61.0474 | 62.2055 | -61.1893 | -61.1893 | 61.7798 | -0.018311 | 0.032043 | 0.086975 | 62.0865 | -61.2488 | -0.27008 | 0.16022 | -0.12817 | -0.27008 | -0.2655 | -0.32959 | 0.041199 | 0.14191 | 60.9512 | 61.0062 | 122.699 | 123.1247 | -0.12817 | 123.0057 | 60.9009 | -0.32959 | 123.1247 | -0.12817 | 60.9009 | 122.699 | 123.0057 | -123.2346 | -123.2941
1790.7656 | 123.1247 | -60.9009 | 62.0453 | 0.041733 | -0.004798 | -0.0079253 | 0.003702 | 0.065446 | -0.0045821 | 0.067838 | -61.0336 | 62.1918 | -61.1893 | -61.1618 | 61.7889 | 0 | 0.018311 | 0.10529 | 62.0911 | -61.235 | -0.28839 | 0.14648 | -0.13275 | -0.26092 | -0.25635 | -0.33417 | 0.045776 | 0.15564 | 60.9192 | 61.0062 | 122.6898 | 123.0927 | -0.13275 | 122.9919 | 60.9009 | -0.33417 | 123.0927 | -0.13275 | 60.9009 | 122.6898 | 122.9919 | -123.2346 | -123.2803
1791.7656 | 123.1247 | -60.8963 | 62.0041 | -0.087967 | -0.0052252 | -0.011557 | 0.0058382 | 0.063737 | -0.0045821 | 0.067624 | -60.9879 | 62.2101 | -61.1893 | -61.1114 | 61.8347 | 0.064087 | 0.018311 | 0.1831 | 62.1185 | -61.2167 | -0.29297 | 0.20599 | -0.091553 | -0.21515 | -0.16937 | -0.32043 | 0.11444 | 0.20142 | 60.9146 | 61.0794 | 122.731 | 123.1064 | -0.091553 | 123.0148 | 60.9604 | -0.32043 | 123.1064 | -0.091553 | 60.9604 | 122.731 | 123.0148 | -123.1934 | -123.2208
1792.7656 | 123.1201 | -60.9146 | 62.0544 | 0.2935 | -0.0041572 | -0.01113 | 0.004343 | 0.064378 | -0.0047957 | 0.066984 | -60.9604 | 62.1689 | -61.1938 | -61.1343 | 61.8073 | 0.036621 | 0.022888 | 0.16937 | 62.1185 | -61.2442 | -0.27924 | 0.11444 | -0.045776 | -0.21973 | -0.24719 | -0.32959 | 0.064087 | 0.23346 | 60.9375 | 61.084 | 122.7219 | 123.0835 | -0.045776 | 123.0331 | 60.9512 | -0.32959 | 123.0835 | -0.045776 | 60.9512 | 122.7219 | 123.0331 | -123.2483 | -123.2986
1793.7656 | 123.1293 | -60.8963 | 62.0499 | -0.026932 | -0.0037298 | -0.0070709 | 0.004343 | 0.064591 | -0.0041549 | 0.070402 | -61.0062 | 62.1872 | -61.1847 | -61.1481 | 61.8713 | 0.036621 | 0.064087 | 0.16479 | 62.1506 | -61.2076 | -0.28839 | 0.13733 | -0.10986 | -0.25177 | -0.17853 | -0.31128 | 0.10071 | 0.17853 | 60.9604 | 61.0611 | 122.7676 | 123.0835 | -0.10986 | 123.0469 | 60.9329 | -0.31128 | 123.0835 | -0.10986 | 60.9329 | 122.7676 | 123.0469 | -123.2346 | -123.2574
1794.7656 | 123.1522 | -60.8871 | 62.0544 | -0.11848 | -0.0033026 | -0.0068573 | 0.004343 | 0.062669 | -0.0041549 | 0.068693 | -61.0291 | 62.2192 | -61.1938 | -61.1343 | 61.8439 | 0.073242 | 0.082397 | 0.17853 | 62.146 | -61.2259 | -0.3067 | 0.16479 | -0.14191 | -0.24719 | -0.21057 | -0.33874 | 0.091553 | 0.1648 | 60.9695 | 61.0657 | 122.731 | 123.1064 | -0.14191 | 123.0331 | 60.9604 | -0.33874 | 123.1064 | -0.14191 | 60.9604 | 122.731 | 123.0331 | -123.2483 | -123.2803
1795.7656 | 123.1338 | -60.9055 | 62.0682 | -0.095596 | -0.0054388 | -0.0047211 | 0.005411 | 0.063523 | -0.0041549 | 0.066984 | -61.0519 | 62.2101 | -61.1755 | -61.1343 | 61.8164 | 0.054932 | 0.1236 | 0.1831 | 62.1552 | -61.2396 | -0.27008 | 0.14191 | -0.14648 | -0.22888 | -0.25177 | -0.33417 | 0.086975 | 0.1236 | 61.0291 | 61.0886 | 122.7219 | 123.1155 | -0.14648 | 123.0606 | 60.9604 | -0.33417 | 123.1155 | -0.14648 | 60.9604 | 122.7219 | 123.0606 | -123.2437 | -123.3078
1796.7656 | 123.1476 | -60.91 | 62.0544 | -0.04219 | -0.00095279 | -0.010916 | 0.003702 | 0.062669 | -0.0052231 | 0.069333 | -60.9833 | 62.1597 | -61.2122 | -61.1206 | 61.7294 | -0.10071 | 0.059509 | 0.19684 | 62.1277 | -61.2122 | -0.30212 | 0.10529 | -0.073242 | -0.21057 | -0.32501 | -0.30212 | 0.073243 | 0.22888 | 60.9695 | 61.1069 | 122.6395 | 123.0698 | -0.073242 | 123.0377 | 60.8093 | -0.30212 | 123.0698 | -0.073242 | 60.8093 | 122.6395 | 123.0377 | -123.2666 | -123.2666
1797.7656 | 123.1522 | -60.8917 | 62.0682 | -0.065079 | -0.0035162 | -0.0034393 | 0.0049838 | 0.066727 | -0.0071457 | 0.06677 | -60.997 | 62.2101 | -61.1664 | -61.1069 | 61.8347 | 0.059509 | 0.027466 | 0.19226 | 62.1185 | -61.2259 | -0.27466 | 0.14191 | -0.10528 | -0.21515 | -0.23346 | -0.33417 | 0.050354 | 0.16937 | 60.9192 | 61.084 | 122.7264 | 123.1018 | -0.10528 | 123.0103 | 60.9512 | -0.33417 | 123.1018 | -0.10528 | 60.9512 | 122.7264 | 123.0103 | -123.2346 | -123.2941
1798.7656 | 123.1338 | -60.8963 | 62.0544 | -0.095596 | -0.0026618 | -0.0072845 | 0.004343 | 0.06096 | -0.0047957 | 0.067838 | -61.0016 | 62.2009 | -61.1847 | -61.1298 | 61.8256 | 0.068665 | 0.054932 | 0.21057 | 62.1048 | -61.203 | -0.28839 | 0.14648 | -0.10529 | -0.23346 | -0.22888 | -0.3067 | 0.050354 | 0.1831 | 60.9512 | 61.1069 | 122.7219 | 123.0972 | -0.10529 | 123.0011 | 60.965 | -0.3067 | 123.0972 | -0.10529 | 60.965 | 122.7219 | 123.0011 | -123.2391 | -123.2574
1799.7656 | 123.1476 | -60.878 | 62.0316 | -0.13374 | -0.0050116 | -0.0068573 | 0.0051974 | 0.063523 | -0.0028731 | 0.068265 | -61.0153 | 62.1735 | -61.2167 | -61.1343 | 61.8393 | 0.068665 | 0.086975 | 0.20142 | 62.1277 | -61.2122 | -0.33874 | 0.14191 | -0.13733 | -0.25635 | -0.19226 | -0.33417 | 0.096131 | 0.20142 | 60.965 | 61.0794 | 122.7173 | 123.0515 | -0.13733 | 123.0057 | 60.9467 | -0.33417 | 123.0515 | -0.13733 | 60.9467 | 122.7173 | 123.0057 | -123.2483 | -123.2437
1800.7656 | 123.1476 | -60.9146 | 62.0728 | -0.072708 | -0.0050116 | -0.0051483 | 0.0032748 | 0.061814 | -0.0022323 | 0.067624 | -61.0336 | 62.178 | -61.1847 | -61.1389 | 61.8073 | 0.054932 | 0.10986 | 0.19226 | 62.1094 | -61.1984 | -0.27008 | 0.10529 | -0.11902 | -0.2243 | -0.2655 | -0.28381 | 0.036621 | 0.15106 | 61.0245 | 61.1069 | 122.7219 | 123.0927 | -0.11902 | 123.024 | 60.9695 | -0.28381 | 123.0927 | -0.11902 | 60.9695 | 122.7219 | 123.024 | -123.2574 | -123.2712
1801.7656 | 123.1155 | -60.8871 | 62.0728 | -0.17952 | -0.0060798 | -0.010062 | -0.00099756 | 0.060105 | -0.0041549 | 0.065488 | -61.0611 | 62.1735 | -61.1847 | -61.1755 | 61.7935 | 0.036621 | 0.13275 | 0.18768 | 62.1552 | -61.1938 | -0.29755 | 0.10071 | -0.17395 | -0.28839 | -0.27924 | -0.3067 | 0.082397 | 0.1236 | 61.0199 | 61.0748 | 122.6807 | 123.0606 | -0.17395 | 123.0423 | 60.9238 | -0.3067 | 123.0606 | -0.17395 | 60.9238 | 122.6807 | 123.0423 | -123.2574 | -123.2666
1802.7656 | 123.0972 | -60.91 | 62.0682 | 0.072251 | -0.0045844 | -0.0094207 | 0.0022066 | 0.064164 | -0.0037277 | 0.068479 | -61.1343 | 62.178 | -61.203 | -61.1801 | 61.821 | 0.036621 | 0.16022 | 0.16937 | 62.1231 | -61.203 | -0.29297 | 0.10986 | -0.2243 | -0.27008 | -0.24719 | -0.29297 | 0.054932 | 0.068665 | 61.0703 | 61.0794 | 122.731 | 123.0881 | -0.2243 | 123.0331 | 60.9467 | -0.29297 | 123.0881 | -0.2243 | 60.9467 | 122.731 | 123.0331 | -123.2712 | -123.2712
1803.7656 | 123.1476 | -60.8871 | 62.0682 | -0.14137 | -0.0052252 | -0.0070709 | 0.0030612 | 0.062241 | -0.0043685 | 0.066556 | -61.0382 | 62.1826 | -61.1847 | -61.1572 | 61.821 | 0.041199 | 0.13275 | 0.16937 | 62.1689 | -61.1755 | -0.29755 | 0.11444 | -0.15106 | -0.27008 | -0.24719 | -0.28839 | 0.10071 | 0.14648 | 61.0199 | 61.0565 | 122.7081 | 123.0698 | -0.15106 | 123.056 | 60.9283 | -0.28839 | 123.0698 | -0.15106 | 60.9283 | 122.7081 | 123.056 | -123.2529 | -123.2437
1804.7656 | 123.0927 | -60.8826 | 62.0728 | -0.057449 | -0.0062934 | -0.0060027 | 0.002634 | 0.062028 | -0.0024459 | 0.067411 | -61.0565 | 62.1643 | -61.2213 | -61.1664 | 61.7889 | 0.036621 | 0.13275 | 0.16937 | 62.1597 | -61.203 | -0.33875 | 0.091553 | -0.17395 | -0.28381 | -0.28381 | -0.32044 | 0.086975 | 0.16479 | 61.0153 | 61.0519 | 122.6715 | 123.0469 | -0.17395 | 123.0423 | 60.9192 | -0.32044 | 123.0469 | -0.17395 | 60.9192 | 122.6715 | 123.0423 | -123.2941 | -123.2758
1805.7656 | 123.1018 | -60.9192 | 62.059 | -0.20241 | -0.0035162 | -0.01113 | 0.00092504 | 0.062669 | -0.0024459 | 0.066556 | -61.0474 | 62.1689 | -61.1664 | -61.2167 | 61.9675 | 0.21515 | 0.036621 | 0.082397 | 62.1918 | -61.1801 | -0.24719 | 0.10986 | -0.12817 | -0.29755 | -0.091553 | -0.26093 | 0.13275 | 0.11902 | 60.9558 | 61.0016 | 122.8867 | 123.0881 | -0.12817 | 123.111 | 61.1343 | -0.26093 | 123.0881 | -0.12817 | 61.1343 | 122.8867 | 123.111 | -123.2254 | -123.2391
1806.7656 | 123.0835 | -60.8963 | 62.0728 | -0.13374 | -0.005866 | -0.013052 | -0.00078396 | 0.062028 | -0.0039413 | 0.066984 | -61.0519 | 62.1414 | -61.1755 | -61.1618 | 61.8073 | 0.027466 | 0.14648 | 0.19684 | 62.1597 | -61.171 | -0.27924 | 0.068664 | -0.15564 | -0.2655 | -0.2655 | -0.27466 | 0.086975 | 0.1236 | 61.0428 | 61.0931 | 122.7036 | 123.0377 | -0.15564 | 123.056 | 60.9238 | -0.27466 | 123.0377 | -0.15564 | 60.9238 | 122.7036 | 123.056 | -123.2483 | -123.2437
1807.7656 | 123.1018 | -60.8963 | 62.0728 | -0.18715 | -0.0062934 | -0.010062 | -0.0016386 | 0.063309 | -0.0041549 | 0.068479 | -61.0153 | 62.114 | -61.1984 | -61.1389 | 61.8118 | 0.059509 | 0.13275 | 0.22888 | 62.1597 | -61.1664 | -0.30212 | 0.041199 | -0.11902 | -0.24262 | -0.26093 | -0.27008 | 0.086975 | 0.1831 | 61.0291 | 61.1252 | 122.7081 | 123.0103 | -0.11902 | 123.056 | 60.9558 | -0.27008 | 123.0103 | -0.11902 | 60.9558 | 122.7081 | 123.056 | -123.2712 | -123.2391
1808.7656 | 123.2254 | -60.8597 | 62.0316 | -0.4084 | -0.005866 | -0.0096343 | 0.00028404 | 0.0616 | -0.0056503 | 0.068479 | -61.1435 | 62.0682 | -61.1481 | -61.0886 | 61.8759 | 0.13733 | -0.054932 | 0.29755 | 62.1185 | -61.1435 | -0.28839 | 0.036621 | -0.28381 | -0.22888 | -0.15564 | -0.28381 | 0.086975 | 0.004577 | 60.8047 | 61.1572 | 122.7356 | 122.9279 | -0.28381 | 122.9782 | 60.997 | -0.28381 | 122.9279 | -0.28381 | 60.997 | 122.7356 | 122.9782 | -123.1796 | -123.175
1809.7656 | 123.2025 | -60.8551 | 62.027 | -0.14137 | -0.0088568 | -0.014334 | 0.0015658 | 0.060532 | -0.0033005 | 0.068265 | -60.9787 | 62.0636 | -61.1572 | -61.0748 | 61.8851 | 0.1236 | -0.013733 | 0.29755 | 62.114 | -61.1618 | -0.30212 | 0.036621 | -0.1236 | -0.21973 | -0.14191 | -0.3067 | 0.086975 | 0.17853 | 60.8414 | 61.1526 | 122.7402 | 122.9187 | -0.1236 | 122.9691 | 60.9787 | -0.3067 | 122.9187 | -0.1236 | 60.9787 | 122.7402 | 122.9691 | -123.1842 | -123.1888
1810.7656 | 123.1842 | -60.8688 | 62.0453 | -0.18715 | -0.005866 | -0.0089935 | -0.0016386 | 0.060319 | -0.0056503 | 0.068693 | -60.9833 | 62.1002 | -61.1572 | -61.0931 | 61.8668 | 0.11444 | 0.027466 | 0.24719 | 62.1048 | -61.1572 | -0.28839 | 0.054932 | -0.11444 | -0.22431 | -0.17853 | -0.28839 | 0.059509 | 0.17395 | 60.8963 | 61.116 | 122.7356 | 122.9691 | -0.11444 | 122.9736 | 60.9833 | -0.28839 | 122.9691 | -0.11444 | 60.9833 | 122.7356 | 122.9736 | -123.2025 | -123.2025
1811.7656 | 123.2162 | -60.8551 | 62.0453 | -0.087967 | -0.0077888 | -0.0079253 | 0.00071144 | 0.0616 | -0.0052231 | 0.070829 | -60.9787 | 62.0819 | -61.1526 | -61.0565 | 61.8896 | 0.1236 | -0.018311 | 0.27924 | 62.0956 | -61.1343 | -0.29755 | 0.036621 | -0.1236 | -0.20142 | -0.15564 | -0.27923 | 0.050354 | 0.17395 | 60.8368 | 61.1343 | 122.7448 | 122.937 | -0.1236 | 122.9507 | 60.9787 | -0.27923 | 122.937 | -0.1236 | 60.9787 | 122.7448 | 122.9507 | -123.1979 | -123.1796
1812.7656 | 123.2162 | -60.8688 | 62.027 | -0.19478 | -0.010566 | -0.011343 | -0.00099756 | 0.062455 | -0.0062911 | 0.06677 | -60.9695 | 62.059 | -61.1526 | -61.1069 | 61.853 | 0.10071 | -0.10071 | 0.23804 | 62.0728 | -61.1389 | -0.28381 | 0.032043 | -0.10071 | -0.23804 | -0.17395 | -0.27008 | 0.045776 | 0.18311 | 60.7681 | 61.1069 | 122.7219 | 122.9279 | -0.10071 | 122.9416 | 60.9695 | -0.27008 | 122.9279 | -0.10071 | 60.9695 | 122.7219 | 122.9416 | -123.1796 | -123.1659
1813.7656 | 123.2529 | -60.8734 | 62.0453 | -0.04982 | -0.0084296 | -0.0089935 | 0.0011386 | 0.061814 | -0.0067185 | 0.067197 | -60.9604 | 62.0316 | -61.1664 | -61.0153 | 61.9034 | 0.13275 | -0.073242 | 0.29755 | 62.1002 | -61.1343 | -0.29297 | -0.013733 | -0.086975 | -0.14191 | -0.14191 | -0.26093 | 0.054932 | 0.20599 | 60.8002 | 61.171 | 122.7768 | 122.905 | -0.086975 | 122.9736 | 61.0062 | -0.26093 | 122.905 | -0.086975 | 61.0062 | 122.7768 | 122.9736 | -123.2117 | -123.1796
1814.7656 | 123.2483 | -60.8597 | 62.0224 | -0.0040434 | -0.0062934 | -0.0042937 | 0.0011386 | 0.059891 | -0.0045821 | 0.066343 | -60.9879 | 62.0636 | -61.171 | -61.0336 | 61.8988 | 0.13275 | -0.091553 | 0.29297 | 62.1048 | -61.1389 | -0.31128 | 0.041199 | -0.12817 | -0.17395 | -0.1236 | -0.27924 | 0.082397 | 0.18311 | 60.7681 | 61.1526 | 122.7585 | 122.9233 | -0.12817 | 122.9645 | 60.9924 | -0.27924 | 122.9233 | -0.12817 | 60.9924 | 122.7585 | 122.9645 | -123.1934 | -123.1613
1815.7656 | 123.2208 | -60.878 | 62.0361 | -0.60677 | -0.0090704 | -0.012198 | 0.001993 | 0.060532 | -0.0052231 | 0.066556 | -61.0703 | 62.0636 | -61.1893 | -61.1206 | 61.8027 | 0.018311 | -0.064087 | 0.17395 | 62.0636 | -61.1481 | -0.31128 | 0.027466 | -0.19226 | -0.24261 | -0.23346 | -0.27008 | 0.027466 | 0.11902 | 60.8139 | 61.0519 | 122.6807 | 122.9416 | -0.19226 | 122.9416 | 60.8963 | -0.27008 | 122.9416 | -0.19226 | 60.8963 | 122.6807 | 122.9416 | -123.2254 | -123.1842
1816.7656 | 123.2025 | -60.8871 | 62.0316 | 0.072251 | -0.0060798 | -0.0077117 | 0.0013522 | 0.059251 | -0.0077865 | 0.066984 | -61.0336 | 62.0178 | -61.1893 | -61.0977 | 61.8439 | 0.050354 | -0.07782 | 0.19684 | 62.0819 | -61.1298 | -0.30212 | -0.013733 | -0.14648 | -0.21057 | -0.18768 | -0.24262 | 0.050354 | 0.15564 | 60.8093 | 61.084 | 122.731 | 122.905 | -0.14648 | 122.9691 | 60.9375 | -0.24262 | 122.905 | -0.14648 | 60.9375 | 122.731 | 122.9691 | -123.2208 | -123.1613
1817.7656 | 123.2025 | -60.8459 | 62.0453 | -0.0040434 | -0.0071478 | -0.011343 | 0.00092504 | 0.05861 | -0.0043685 | 0.069547 | -61.0153 | 62.0407 | -61.1755 | -61.0794 | 61.8805 | 0.09613 | -0.082397 | 0.21973 | 62.0773 | -61.1206 | -0.32959 | -0.004578 | -0.16937 | -0.23346 | -0.16479 | -0.27466 | 0.032044 | 0.16022 | 60.7636 | 61.0657 | 122.7264 | 122.8867 | -0.16937 | 122.9233 | 60.9421 | -0.27466 | 122.8867 | -0.16937 | 60.9421 | 122.7264 | 122.9233 | -123.2208 | -123.1659
1818.7656 | 123.175 | -60.878 | 62.0316 | 0.0035856 | -0.0086432 | -0.0094207 | 0.00092504 | 0.058182 | -0.0058639 | 0.067411 | -61.0336 | 62.0407 | -61.1755 | -61.1023 | 61.8576 | 0.045776 | -0.091553 | 0.18768 | 62.0728 | -61.1526 | -0.29755 | 0.009155 | -0.15564 | -0.2243 | -0.17395 | -0.27466 | 0.041199 | 0.14191 | 60.7864 | 61.0657 | 122.7356 | 122.9187 | -0.15564 | 122.9507 | 60.9238 | -0.27466 | 122.9187 | -0.15564 | 60.9238 | 122.7356 | 122.9507 | -123.2071 | -123.1842
1819.7656 | 123.1659 | -60.8917 | 62.0361 | 0.087509 | -0.0071478 | -0.012625 | -0.00014316 | 0.059464 | -0.0039413 | 0.068052 | -61.0428 | 62.0453 | -61.1938 | -61.1435 | 61.8439 | 0.004578 | -0.082397 | 0.16022 | 62.0728 | -61.1526 | -0.30212 | 0.009155 | -0.15106 | -0.25177 | -0.19226 | -0.26092 | 0.036621 | 0.15106 | 60.8093 | 61.0519 | 122.7356 | 122.937 | -0.15106 | 122.9645 | 60.8963 | -0.26092 | 122.937 | -0.15106 | 60.8963 | 122.7356 | 122.9645 | -123.23 | -123.1888
1820.7656 | 123.1522 | -60.8826 | 62.0316 | 0.17906 | -0.006507 | -0.0098479 | 0.002634 | 0.05861 | -0.0043685 | 0.067411 | -61.0336 | 62.0316 | -61.1893 | -61.1206 | 61.8027 | 0.009155 | -0.10071 | 0.13733 | 62.0728 | -61.1298 | -0.3067 | 0 | -0.15106 | -0.23804 | -0.22888 | -0.24719 | 0.041199 | 0.15564 | 60.7819 | 61.0199 | 122.6852 | 122.9141 | -0.15106 | 122.9553 | 60.8917 | -0.24719 | 122.9141 | -0.15106 | 60.8917 | 122.6852 | 122.9553 | -123.2208 | -123.1613
1821.7656 | 123.1567 | -60.8963 | 62.0224 | 0.1638 | -0.007575 | -0.0087799 | 0.00028404 | 0.059037 | -0.0045821 | 0.067197 | -61.0336 | 62.0544 | -61.1801 | -61.1114 | 61.8118 | 0.009155 | -0.1236 | 0.13275 | 62.059 | -61.1618 | -0.28381 | 0.032043 | -0.13733 | -0.21515 | -0.21057 | -0.2655 | 0.036621 | 0.14648 | 60.7727 | 61.0291 | 122.7081 | 122.9507 | -0.13733 | 122.9553 | 60.9055 | -0.2655 | 122.9507 | -0.13733 | 60.9055 | 122.7081 | 122.9553 | -123.2025 | -123.1842
1822.7656 | 123.2208 | -60.8826 | 61.9812 | 0.2401 | -0.0050116 | -0.0077117 | 0.004343 | 0.06096 | -0.0069321 | 0.067411 | -61.1618 | 62.0041 | -61.2122 | -61.0382 | 61.8576 | 0.050354 | -0.18768 | 0.16479 | 62.0682 | -61.1526 | -0.32959 | 0.022888 | -0.27924 | -0.15564 | -0.1236 | -0.27008 | 0.086975 | 0.050354 | 60.6949 | 61.0474 | 122.7402 | 122.8867 | -0.27924 | 122.9507 | 60.9329 | -0.27008 | 122.8867 | -0.27924 | 60.9329 | 122.7402 | 122.9507 | -123.1934 | -123.1338
1823.7656 | 123.1934 | -60.8826 | 62.027 | 0.22484 | -0.0077888 | -0.0089935 | 0.0041292 | 0.060319 | -0.0043685 | 0.068479 | -60.9833 | 62.0407 | -61.203 | -61.0977 | 61.8622 | 0.032043 | -0.1831 | 0.16022 | 62.0453 | -61.1618 | -0.32044 | 0.013732 | -0.10071 | -0.21515 | -0.16479 | -0.27924 | 0.01831 | 0.21973 | 60.6995 | 61.0428 | 122.7448 | 122.9233 | -0.10071 | 122.9279 | 60.9146 | -0.27924 | 122.9233 | -0.10071 | 60.9146 | 122.7448 | 122.9279 | -123.23 | -123.1888
1824.7656 | 123.1842 | -60.8963 | 62.0224 | 0.24773 | -0.0045844 | -0.0074981 | 0.0013522 | 0.057755 | -0.0047957 | 0.066984 | -61.0107 | 62.0544 | -61.1893 | -61.1069 | 61.8256 | 0.022888 | -0.16022 | 0.14648 | 62.0407 | -61.171 | -0.29297 | 0.032043 | -0.11444 | -0.21057 | -0.19684 | -0.27466 | 0.01831 | 0.17853 | 60.7361 | 61.0428 | 122.7219 | 122.9507 | -0.11444 | 122.937 | 60.9192 | -0.27466 | 122.9507 | -0.11444 | 60.9192 | 122.7219 | 122.937 | -123.2117 | -123.1934
1825.7656 | 123.2162 | -60.91 | 61.9858 | 0.30876 | -0.0039434 | -0.0087799 | 0.0049838 | 0.060319 | -0.0037277 | 0.067838 | -60.9924 | 62.0636 | -61.1801 | -61.0931 | 61.8393 | 0.036621 | -0.19684 | 0.15106 | 62.0453 | -61.1618 | -0.27008 | 0.07782 | -0.082398 | -0.18311 | -0.14648 | -0.25177 | 0.059509 | 0.18768 | 60.7132 | 61.0611 | 122.7493 | 122.9736 | -0.082398 | 122.9553 | 60.9467 | -0.25177 | 122.9736 | -0.082398 | 60.9467 | 122.7493 | 122.9553 | -123.1659 | -123.1476
1826.7656 | 123.2483 | -60.8597 | 61.9904 | 0.27061 | -0.0054388 | -0.0085663 | 0.0049838 | 0.06096 | -0.0056503 | 0.068693 | -60.9741 | 62.0544 | -61.1984 | -61.0291 | 61.8713 | 0.059509 | -0.17395 | 0.17853 | 62.0544 | -61.1435 | -0.33875 | 0.064087 | -0.11444 | -0.16937 | -0.11902 | -0.28381 | 0.064087 | 0.2243 | 60.6857 | 61.0382 | 122.731 | 122.9141 | -0.11444 | 122.9141 | 60.9192 | -0.28381 | 122.9141 | -0.11444 | 60.9192 | 122.731 | 122.9141 | -123.1888 | -123.1338
1827.7656 | 123.23 | -60.8826 | 62.0132 | 0.23247 | -0.0054388 | -0.0066437 | 0.0075472 | 0.062028 | -0.0037277 | 0.067411 | -60.9741 | 62.0911 | -61.1847 | -61.0886 | 61.8622 | 0.032043 | -0.23346 | 0.15106 | 62.0087 | -61.1893 | -0.30212 | 0.077819 | -0.091553 | -0.20599 | -0.15106 | -0.3067 | -0.004578 | 0.21057 | 60.6491 | 61.0336 | 122.7448 | 122.9736 | -0.091553 | 122.8912 | 60.9146 | -0.3067 | 122.9736 | -0.091553 | 60.9146 | 122.7448 | 122.8912 | -123.1979 | -123.2025
1828.7656 | 123.2254 | -60.91 | 61.9949 | 0.26299 | -0.0052252 | -0.0096343 | 0.0079744 | 0.063737 | -0.0039413 | 0.068693 | -61.0062 | 62.0911 | -61.2167 | -61.0657 | 61.8439 | 0.022888 | -0.19226 | 0.12817 | 62.0132 | -61.2076 | -0.3067 | 0.09613 | -0.096131 | -0.15564 | -0.15106 | -0.29755 | 0.018311 | 0.21057 | 60.7178 | 61.0382 | 122.7539 | 123.0011 | -0.096131 | 122.9233 | 60.9329 | -0.29755 | 123.0011 | -0.096131 | 60.9329 | 122.7539 | 122.9233 | -123.2117 | -123.2025
1829.7656 | 123.1384 | -60.9146 | 62.0407 | 0.30876 | -0.004798 | -0.0079253 | 0.0066928 | 0.060532 | -0.0058639 | 0.067197 | -61.0382 | 62.1506 | -61.1984 | -61.1572 | 61.7706 | -0.050354 | -0.041199 | 0.054932 | 62.0636 | -61.2213 | -0.28381 | 0.10986 | -0.1236 | -0.24262 | -0.27008 | -0.3067 | 0.022889 | 0.16022 | 60.8734 | 60.9695 | 122.6852 | 123.0652 | -0.1236 | 122.9782 | 60.8643 | -0.3067 | 123.0652 | -0.1236 | 60.8643 | 122.6852 | 122.9782 | -123.2391 | -123.262
1830.7656 | 123.1567 | -60.9055 | 62.0178 | 0.25536 | -0.0050116 | -0.0098479 | 0.0056246 | 0.062669 | -0.0062911 | 0.068265 | -61.0382 | 62.1185 | -61.2213 | -61.1572 | 61.8027 | -0.036621 | -0.09613 | 0.064087 | 62.0728 | -61.2076 | -0.31586 | 0.10071 | -0.13275 | -0.25177 | -0.21515 | -0.30212 | 0.054932 | 0.18311 | 60.8093 | 60.9695 | 122.7081 | 123.024 | -0.13275 | 122.9782 | 60.8688 | -0.30212 | 123.024 | -0.13275 | 60.8688 | 122.7081 | 122.9782 | -123.2391 | -123.2254
1831.7656 | 123.1705 | -60.9192 | 62.0041 | 0.2935 | -0.004798 | -0.0072845 | 0.0058382 | 0.063096 | -0.0030869 | 0.070188 | -61.0382 | 62.1185 | -61.235 | -61.116 | 61.8347 | 0.013733 | -0.14648 | 0.13275 | 62.0361 | -61.203 | -0.31586 | 0.11444 | -0.11902 | -0.19684 | -0.16937 | -0.28381 | 0.032044 | 0.19684 | 60.7727 | 61.0519 | 122.7539 | 123.0377 | -0.11902 | 122.9553 | 60.9329 | -0.28381 | 123.0377 | -0.11902 | 60.9329 | 122.7539 | 122.9553 | -123.2391 | -123.2071
1832.7656 | 123.1705 | -60.91 | 61.9904 | 0.23247 | -0.0056524 | -0.0053619 | 0.0039156 | 0.063309 | -0.0047957 | 0.06677 | -61.0474 | 62.146 | -61.2259 | -61.1664 | 61.8027 | -0.027466 | -0.10529 | 0.068665 | 62.059 | -61.1984 | -0.31586 | 0.15564 | -0.13733 | -0.25635 | -0.18768 | -0.28839 | 0.068665 | 0.17853 | 60.8047 | 60.9787 | 122.7127 | 123.056 | -0.13733 | 122.9691 | 60.8826 | -0.28839 | 123.056 | -0.13733 | 60.8826 | 122.7127 | 122.9691 | -123.2162 | -123.1888
1833.7656 | 123.1064 | -60.9329 | 62.0224 | 0.1638 | -0.0022346 | -0.0089935 | 0.0030612 | 0.063096 | -0.0058639 | 0.068052 | -61.0565 | 62.1506 | -61.2259 | -61.1847 | 61.7752 | -0.045776 | -0.054932 | 0.022888 | 62.0544 | -61.2167 | -0.29297 | 0.12817 | -0.1236 | -0.25177 | -0.24719 | -0.28381 | 0.032043 | 0.16937 | 60.878 | 60.9558 | 122.7081 | 123.0835 | -0.1236 | 122.9874 | 60.8871 | -0.28381 | 123.0835 | -0.1236 | 60.8871 | 122.7081 | 122.9874 | -123.2483 | -123.2391
1834.7656 | 123.111 | -60.9146 | 61.9995 | 0.30876 | -0.0015936 | -0.0098479 | 0.0049838 | 0.062028 | -0.0035141 | 0.070615 | -60.9787 | 62.146 | -61.2167 | -61.1664 | 61.7569 | -0.064087 | -0.022888 | 0.036621 | 62.0956 | -61.2213 | -0.30212 | 0.14648 | -0.064087 | -0.25177 | -0.24262 | -0.3067 | 0.09613 | 0.23804 | 60.8917 | 60.9512 | 122.6715 | 123.0606 | -0.064087 | 123.0103 | 60.8505 | -0.3067 | 123.0606 | -0.064087 | 60.8505 | 122.6715 | 123.0103 | -123.2162 | -123.2208
1835.7656 | 123.0698 | -60.9329 | 62.0544 | 0.07988 | -0.0043708 | -0.0072845 | 0.0081882 | 0.064805 | -0.0020187 | 0.06677 | -61.0519 | 62.178 | -61.2076 | -61.1526 | 61.7844 | -0.004578 | 0.009155 | 0.032043 | 62.0636 | -61.2213 | -0.27466 | 0.1236 | -0.11902 | -0.21973 | -0.27008 | -0.28839 | 0.009156 | 0.15564 | 60.9421 | 60.965 | 122.7173 | 123.111 | -0.11902 | 122.9965 | 60.9283 | -0.28839 | 123.111 | -0.11902 | 60.9283 | 122.7173 | 122.9965 | -123.262 | -123.2758
1836.7656 | 123.0927 | -60.9329 | 62.0316 | 0.07988 | -0.003089 | -0.0047211 | 0.003702 | 0.065873 | -0.0045821 | 0.067624 | -61.0153 | 62.1872 | -61.2076 | -61.1618 | 61.7889 | -0.013733 | 0.036621 | 0.091553 | 62.0956 | -61.2305 | -0.27466 | 0.15564 | -0.082398 | -0.22888 | -0.24262 | -0.29755 | 0.064087 | 0.19226 | 60.9695 | 61.0245 | 122.7219 | 123.1201 | -0.082398 | 123.0286 | 60.9192 | -0.29755 | 123.1201 | -0.082398 | 60.9192 | 122.7219 | 123.0286 | -123.2391 | -123.262
1837.7656 | 123.0972 | -60.9467 | 62.027 | 0.20958 | -0.0028754 | -0.0072845 | 0.0051974 | 0.063096 | -0.0020187 | 0.068693 | -61.0794 | 62.1872 | -61.2122 | -61.1664 | 61.8118 | -0.041199 | 0.041199 | 0.082397 | 62.1323 | -61.2076 | -0.2655 | 0.16022 | -0.13275 | -0.21973 | -0.21515 | -0.26093 | 0.10529 | 0.13275 | 60.9879 | 61.0291 | 122.7585 | 123.1338 | -0.13275 | 123.0789 | 60.9055 | -0.26093 | 123.1338 | -0.13275 | 60.9055 | 122.7585 | 123.0789 | -123.2391 | -123.2346
1838.7656 | 123.0423 | -60.9192 | 62.0087 | 0.20195 | -0.0045844 | -0.0083527 | 0.0049838 | 0.063523 | -0.0043685 | 0.067838 | -61.1069 | 62.1643 | -61.2076 | -61.1984 | 61.7477 | -0.068665 | 0.004578 | 0.045776 | 62.0819 | -61.2167 | -0.28839 | 0.15564 | -0.18768 | -0.27924 | -0.26093 | -0.29755 | 0.073242 | 0.10071 | 60.9238 | 60.965 | 122.6669 | 123.0835 | -0.18768 | 123.0011 | 60.8505 | -0.29755 | 123.0835 | -0.18768 | 60.8505 | 122.6669 | 123.0011 | -123.2162 | -123.2254
1839.7656 | 123.0698 | -60.9375 | 62.0544 | 0.21721 | -0.0033026 | -0.0047211 | 0.0049838 | 0.065446 | -0.0028731 | 0.067197 | -61.0703 | 62.1872 | -61.2076 | -61.2167 | 61.734 | -0.07782 | 0.045776 | 0.022888 | 62.0956 | -61.2396 | -0.27008 | 0.13275 | -0.13275 | -0.27924 | -0.32043 | -0.30212 | 0.041199 | 0.13733 | 60.9833 | 60.9604 | 122.6715 | 123.1247 | -0.13275 | 123.0331 | 60.8597 | -0.30212 | 123.1247 | -0.13275 | 60.8597 | 122.6715 | 123.0331 | -123.262 | -123.2941
1840.7656 | 123.0972 | -60.9146 | 62.0544 | 0.12566 | -0.0028754 | -0.0055755 | 0.0058382 | 0.065446 | -0.0043685 | 0.06912 | -61.0519 | 62.2055 | -61.2122 | -61.1984 | 61.7615 | -0.041199 | 0.018311 | 0.068665 | 62.1185 | -61.2396 | -0.29755 | 0.15106 | -0.13733 | -0.28381 | -0.29297 | -0.32501 | 0.064087 | 0.16022 | 60.9329 | 60.9833 | 122.6761 | 123.1201 | -0.13733 | 123.0331 | 60.8734 | -0.32501 | 123.1201 | -0.13733 | 60.8734 | 122.6761 | 123.0331 | -123.2666 | -123.2941
1841.7656 | 123.1155 | -60.9192 | 62.0544 | 0.087509 | -0.0022346 | -0.0098479 | 0.0045566 | 0.062882 | -0.0052231 | 0.068052 | -61.0428 | 62.2055 | -61.203 | -61.171 | 61.7752 | -0.004578 | 0.027466 | 0.091553 | 62.0728 | -61.2259 | -0.28381 | 0.15106 | -0.1236 | -0.25177 | -0.27923 | -0.3067 | 0.018311 | 0.16022 | 60.9467 | 61.0107 | 122.6944 | 123.1247 | -0.1236 | 122.9919 | 60.9146 | -0.3067 | 123.1247 | -0.1236 | 60.9146 | 122.6944 | 122.9919 | -123.2574 | -123.2803
1842.7656 | 123.1384 | -60.9146 | 62.059 | -0.0040434 | -0.006507 | -0.0094207 | 0.003702 | 0.065018 | -0.0018051 | 0.067411 | -60.997 | 62.2009 | -61.1893 | -61.1252 | 61.853 | 0.018311 | 0.045776 | 0.17853 | 62.0865 | -61.2259 | -0.27466 | 0.14191 | -0.082397 | -0.21057 | -0.20599 | -0.31128 | 0.027466 | 0.19226 | 60.9604 | 61.0931 | 122.7676 | 123.1155 | -0.082397 | 123.0011 | 60.9329 | -0.31128 | 123.1155 | -0.082397 | 60.9329 | 122.7676 | 123.0011 | -123.2483 | -123.2849
1843.7812 | 123.175 | -60.8871 | 61.9949 | 0.22484 | -0.007575 | -0.0053619 | -0.0018522 | 0.063737 | -0.0043685 | 0.067411 | -61.0474 | 62.0361 | -61.2122 | -61.1618 | 61.8439 | 0.032043 | -0.15106 | 0.15106 | 62.0728 | -61.1618 | -0.32501 | 0.041199 | -0.16022 | -0.27466 | -0.15106 | -0.27466 | 0.07782 | 0.1648 | 60.7361 | 61.0382 | 122.731 | 122.9233 | -0.16022 | 122.9599 | 60.9192 | -0.27466 | 122.9233 | -0.16022 | 60.9192 | 122.731 | 122.9599 | -123.2071 | -123.1567
1844.7656 | 123.0972 | -60.9192 | 62.0636 | 0.07988 | -0.0028754 | -0.0057891 | 0.0064792 | 0.063737 | -0.0062911 | 0.069333 | -61.0291 | 62.1918 | -61.1984 | -61.1755 | 61.7706 | -0.004578 | 0.022888 | 0.10071 | 62.0865 | -61.2213 | -0.27924 | 0.12817 | -0.10986 | -0.25635 | -0.29297 | -0.30212 | 0.022888 | 0.16937 | 60.9421 | 61.0199 | 122.6898 | 123.111 | -0.10986 | 123.0057 | 60.9146 | -0.30212 | 123.111 | -0.10986 | 60.9146 | 122.6898 | 123.0057 | -123.262 | -123.2849
1845.7656 | 123.1064 | -60.9009 | 62.0636 | 0.064621 | -0.0018072 | -0.0062163 | 0.0039156 | 0.062241 | -0.0039413 | 0.066984 | -61.0062 | 62.2009 | -61.1938 | -61.1664 | 61.7752 | 0.018311 | 0.027466 | 0.10529 | 62.0865 | -61.2396 | -0.29297 | 0.13733 | -0.10529 | -0.2655 | -0.28839 | -0.33874 | 0.022888 | 0.18768 | 60.9283 | 61.0062 | 122.6761 | 123.1018 | -0.10529 | 122.9874 | 60.9192 | -0.33874 | 123.1018 | -0.10529 | 60.9192 | 122.6761 | 122.9874 | -123.2574 | -123.3032
1846.7656 | 123.1155 | -60.8917 | 62.0499 | 0.011215 | -0.0035162 | -0.0089935 | 0.0039156 | 0.062028 | -0.0045821 | 0.068265 | -61.0153 | 62.1918 | -61.1755 | -61.1618 | 61.7981 | 0.009155 | 0.032043 | 0.13733 | 62.0819 | -61.2259 | -0.28381 | 0.14191 | -0.1236 | -0.27008 | -0.25177 | -0.33417 | 0.032043 | 0.16022 | 60.9238 | 61.0291 | 122.6898 | 123.0835 | -0.1236 | 122.9736 | 60.9009 | -0.33417 | 123.0835 | -0.1236 | 60.9009 | 122.6898 | 122.9736 | -123.2254 | -123.2758
1847.7656 | 123.1247 | -60.9146 | 62.0361 | -0.026932 | -0.0045844 | -0.0081389 | 0.005411 | 0.063096 | -0.0039413 | 0.067838 | -61.0062 | 62.2009 | -61.1938 | -61.1481 | 61.8301 | 0.036621 | 0.022888 | 0.13733 | 62.0956 | -61.235 | -0.27924 | 0.16479 | -0.091553 | -0.23346 | -0.20599 | -0.32043 | 0.059509 | 0.18768 | 60.9375 | 61.0519 | 122.7448 | 123.1155 | -0.091553 | 123.0103 | 60.9512 | -0.32043 | 123.1155 | -0.091553 | 60.9512 | 122.7448 | 123.0103 | -123.23 | -123.2712
1848.7812 | 123.1476 | -60.9146 | 62.0132 | 0.19432 | -0.0052252 | -0.0060027 | -0.0046292 | 0.060746 | -0.0047957 | 0.06912 | -61.0657 | 62.059 | -61.2167 | -61.171 | 61.8164 | 0.018311 | -0.10071 | 0.13733 | 62.0728 | -61.1664 | -0.30212 | 0.045776 | -0.15106 | -0.25635 | -0.19684 | -0.25177 | 0.059509 | 0.15106 | 60.8139 | 61.0519 | 122.731 | 122.9736 | -0.15106 | 122.9874 | 60.9329 | -0.25177 | 122.9736 | -0.15106 | 60.9329 | 122.731 | 122.9874 | -123.23 | -123.1796
1849.7656 | 123.1338 | -60.9009 | 62.0682 | -0.095596 | -0.0033026 | -0.0060027 | 0.0047702 | 0.062882 | -0.0050095 | 0.065488 | -60.9787 | 62.1964 | -61.1847 | -61.1206 | 61.821 | 0.059509 | 0.082397 | 0.20142 | 62.1231 | -61.235 | -0.28381 | 0.12817 | -0.07782 | -0.21973 | -0.24719 | -0.33417 | 0.054932 | 0.20599 | 60.9833 | 61.1023 | 122.7219 | 123.0972 | -0.07782 | 123.024 | 60.9604 | -0.33417 | 123.0972 | -0.07782 | 60.9604 | 122.7219 | 123.024 | -123.2529 | -123.3032
1850.7656 | 123.1338 | -60.8917 | 62.0544 | -0.095596 | -0.0026618 | -0.0077117 | 0.0051974 | 0.063309 | -0.0028731 | 0.066556 | -61.0062 | 62.1918 | -61.1984 | -61.116 | 61.821 | 0.082397 | 0.082397 | 0.20142 | 62.0956 | -61.2259 | -0.3067 | 0.13733 | -0.11444 | -0.2243 | -0.23346 | -0.33417 | 0.041199 | 0.19226 | 60.9741 | 61.0931 | 122.7127 | 123.0835 | -0.11444 | 122.9874 | 60.9741 | -0.33417 | 123.0835 | -0.11444 | 60.9741 | 122.7127 | 122.9874 | -123.2529 | -123.2803
1851.7656 | 123.1567 | -60.9283 | 62.059 | 0.1638 | -0.0069342 | -0.0057891 | 0.0058382 | 0.064805 | -0.0050095 | 0.066556 | -60.9604 | 62.1964 | -61.1893 | -61.1389 | 61.8164 | 0.036621 | 0.022888 | 0.16937 | 62.114 | -61.1938 | -0.26093 | 0.13733 | -0.032043 | -0.21057 | -0.24262 | -0.2655 | 0.054932 | 0.22888 | 60.9512 | 61.0977 | 122.7448 | 123.1247 | -0.032043 | 123.0423 | 60.965 | -0.2655 | 123.1247 | -0.032043 | 60.965 | 122.7448 | 123.0423 | -123.2483 | -123.2529
1852.7656 | 123.1613 | -60.9146 | 62.0178 | -0.019302 | -0.004798 | -0.0064301 | 0.0041292 | 0.062669 | -0.0073593 | 0.068265 | -61.0794 | 62.1689 | -61.1984 | -61.1206 | 61.8164 | 0.045776 | 0.036621 | 0.17853 | 62.1552 | -61.2076 | -0.28381 | 0.15106 | -0.1648 | -0.20599 | -0.20142 | -0.29297 | 0.13733 | 0.11902 | 60.9512 | 61.0931 | 122.731 | 123.0835 | -0.1648 | 123.0698 | 60.9604 | -0.29297 | 123.0835 | -0.1648 | 60.9604 | 122.731 | 123.0698 | -123.2162 | -123.2254
1853.7812 | 123.175 | -60.9009 | 62.0224 | 0.13329 | -0.0071478 | -0.0089935 | -0.0037748 | 0.062028 | -0.0054367 | 0.06912 | -61.0565 | 62.0682 | -61.203 | -61.171 | 61.8347 | 0.022888 | -0.086975 | 0.13733 | 62.0819 | -61.1572 | -0.30212 | 0.045776 | -0.15564 | -0.27008 | -0.18768 | -0.25635 | 0.059509 | 0.14648 | 60.8139 | 61.0382 | 122.7356 | 122.9691 | -0.15564 | 122.9828 | 60.9238 | -0.25635 | 122.9691 | -0.15564 | 60.9238 | 122.7356 | 122.9828 | -123.2254 | -123.1796
1854.7656 | 123.1567 | -60.9009 | 62.0453 | 0.018845 | -0.0060798 | -0.0070709 | 0.005411 | 0.061387 | -0.0037277 | 0.067197 | -60.9879 | 62.178 | -61.203 | -61.0931 | 61.821 | 0.068665 | 0.032043 | 0.20142 | 62.1277 | -61.2213 | -0.30212 | 0.13275 | -0.086975 | -0.19226 | -0.2243 | -0.32043 | 0.082398 | 0.21515 | 60.9329 | 61.1023 | 122.7219 | 123.0789 | -0.086975 | 123.0286 | 60.9695 | -0.32043 | 123.0789 | -0.086975 | 60.9695 | 122.7219 | 123.0286 | -123.2483 | -123.2666
1855.7656 | 123.1659 | -60.91 | 62.0316 | -0.13374 | -0.004798 | -0.0085663 | 0.0047702 | 0.063523 | -0.0052231 | 0.071042 | -60.9879 | 62.1689 | -61.1847 | -61.116 | 61.8347 | 0.073242 | 0.050354 | 0.1831 | 62.1094 | -61.2076 | -0.27466 | 0.13733 | -0.07782 | -0.20599 | -0.19684 | -0.29755 | 0.07782 | 0.19684 | 60.9604 | 61.0931 | 122.7448 | 123.0789 | -0.07782 | 123.0194 | 60.9833 | -0.29755 | 123.0789 | -0.07782 | 60.9833 | 122.7448 | 123.0194 | -123.2162 | -123.2391
1856.7656 | 123.1293 | -60.8871 | 62.0636 | -0.21004 | -0.005866 | -0.0064301 | 0.0022066 | 0.062241 | -0.0030869 | 0.069761 | -61.0245 | 62.2009 | -61.1893 | -61.1481 | 61.8027 | 0.045776 | 0.1236 | 0.17853 | 62.1323 | -61.2259 | -0.30212 | 0.13733 | -0.13733 | -0.26093 | -0.26093 | -0.33874 | 0.068664 | 0.16479 | 61.0107 | 61.0657 | 122.6898 | 123.0881 | -0.13733 | 123.0194 | 60.9329 | -0.33874 | 123.0881 | -0.13733 | 60.9329 | 122.6898 | 123.0194 | -123.2529 | -123.2895
1857.7656 | 123.1338 | -60.9055 | 62.0773 | -0.14137 | -0.0037298 | -0.0066437 | 0.002634 | 0.064378 | -0.0054367 | 0.065916 | -61.0153 | 62.1918 | -61.1801 | -61.116 | 61.8164 | 0.059509 | 0.091553 | 0.18768 | 62.1414 | -61.1801 | -0.27466 | 0.11444 | -0.10986 | -0.21057 | -0.26093 | -0.27466 | 0.064086 | 0.16479 | 60.997 | 61.0931 | 122.7219 | 123.0972 | -0.10986 | 123.0469 | 60.965 | -0.27466 | 123.0972 | -0.10986 | 60.965 | 122.7219 | 123.0469 | -123.2574 | -123.2574
1858.7656 | 123.1796 | -60.9009 | 62.0178 | 0.18669 | -0.006507 | -0.01113 | -0.0012112 | 0.063737 | -0.0020187 | 0.065702 | -61.0153 | 62.0956 | -61.1984 | -61.1389 | 61.821 | 0.009155 | -0.14191 | 0.14191 | 62.0728 | -61.1801 | -0.29755 | 0.07782 | -0.11444 | -0.23804 | -0.19684 | -0.27924 | 0.054932 | 0.1831 | 60.759 | 61.0428 | 122.7219 | 122.9965 | -0.11444 | 122.9736 | 60.91 | -0.27924 | 122.9965 | -0.11444 | 60.91 | 122.7219 | 122.9736 | -123.2162 | -123.1979
1859.7656 | 123.1567 | -60.9009 | 62.0453 | -0.10323 | -0.0037298 | -0.0083527 | 0.0060518 | 0.062669 | -0.0060775 | 0.067411 | -61.0016 | 62.1735 | -61.171 | -61.1298 | 61.8301 | 0.064087 | 0.068665 | 0.19684 | 62.1002 | -61.203 | -0.27008 | 0.12817 | -0.10071 | -0.22888 | -0.21515 | -0.30212 | 0.054932 | 0.16937 | 60.9695 | 61.0977 | 122.731 | 123.0743 | -0.10071 | 123.0011 | 60.965 | -0.30212 | 123.0743 | -0.10071 | 60.965 | 122.731 | 123.0011 | -123.2162 | -123.2483
1860.7656 | 123.1338 | -60.9146 | 62.0453 | -0.11848 | -0.0060798 | -0.0064301 | 0.0015658 | 0.062455 | -0.0054367 | 0.066556 | -61.0199 | 62.1826 | -61.1938 | -61.116 | 61.8164 | 0.059509 | 0.10071 | 0.19226 | 62.1414 | -61.1984 | -0.27924 | 0.13733 | -0.10529 | -0.20142 | -0.22888 | -0.28381 | 0.09613 | 0.17395 | 61.0153 | 61.1069 | 122.731 | 123.0972 | -0.10529 | 123.056 | 60.9741 | -0.28381 | 123.0972 | -0.10529 | 60.9741 | 122.731 | 123.056 | -123.2391 | -123.2437
1861.7656 | 123.1247 | -60.91 | 62.0773 | -0.14137 | -0.0054388 | -0.0081389 | 0.0028476 | 0.062882 | -0.0039413 | 0.068265 | -61.0336 | 62.146 | -61.2076 | -61.1435 | 61.8164 | 0.054932 | 0.10529 | 0.16937 | 62.1826 | -61.203 | -0.29755 | 0.068664 | -0.1236 | -0.23346 | -0.26093 | -0.29297 | 0.10529 | 0.17395 | 61.0153 | 61.0794 | 122.7264 | 123.056 | -0.1236 | 123.0927 | 60.965 | -0.29297 | 123.056 | -0.1236 | 60.965 | 122.7264 | 123.0927 | -123.2849 | -123.2803
1862.7656 | 123.0881 | -60.9009 | 62.0956 | -0.13374 | -0.0033026 | -0.012198 | -0.001425 | 0.062241 | -0.0043685 | 0.065916 | -61.0657 | 62.1506 | -61.1847 | -61.1389 | 61.7935 | 0.050354 | 0.14191 | 0.17853 | 62.1506 | -61.1755 | -0.28381 | 0.054932 | -0.16479 | -0.23804 | -0.30212 | -0.27466 | 0.054932 | 0.11902 | 61.0428 | 61.0794 | 122.6944 | 123.0515 | -0.16479 | 123.0515 | 60.9512 | -0.27466 | 123.0515 | -0.16479 | 60.9512 | 122.6944 | 123.0515 | -123.2803 | -123.2712
1863.7656 | 123.0972 | -60.8963 | 62.0773 | -0.21004 | -0.008216 | -0.010703 | 0.0011386 | 0.059251 | -0.0039413 | 0.066984 | -61.0336 | 62.146 | -61.1664 | -61.1618 | 61.8164 | 0.054932 | 0.12817 | 0.20142 | 62.1643 | -61.1801 | -0.27008 | 0.068664 | -0.13733 | -0.2655 | -0.26093 | -0.28381 | 0.086975 | 0.13275 | 61.0245 | 61.0977 | 122.7127 | 123.0423 | -0.13733 | 123.0606 | 60.9512 | -0.28381 | 123.0423 | -0.13733 | 60.9512 | 122.7127 | 123.0606 | -123.2437 | -123.2574
1864.7656 | 123.0835 | -60.8963 | 62.1048 | -0.21767 | -0.0039434 | -0.0087799 | 0.0011386 | 0.0616 | -0.0054367 | 0.068479 | -61.0428 | 62.1643 | -61.1938 | -61.1526 | 61.7981 | 0.036621 | 0.13275 | 0.18768 | 62.146 | -61.1938 | -0.29755 | 0.05951 | -0.14648 | -0.25635 | -0.3067 | -0.29755 | 0.041199 | 0.15106 | 61.0291 | 61.084 | 122.6944 | 123.0606 | -0.14648 | 123.0423 | 60.9329 | -0.29755 | 123.0606 | -0.14648 | 60.9329 | 122.6944 | 123.0423 | -123.2986 | -123.2986
1865.7656 | 123.1201 | -60.9055 | 62.0728 | 0.1104 | -0.0060798 | -0.0089935 | 0.0017794 | 0.059464 | -0.0052231 | 0.068479 | -61.0519 | 62.1643 | -61.2213 | -61.1435 | 61.8027 | 0.045776 | 0.11902 | 0.1831 | 62.1231 | -61.1938 | -0.31586 | 0.091553 | -0.14648 | -0.23804 | -0.27008 | -0.28839 | 0.050354 | 0.16937 | 61.0245 | 61.0886 | 122.7081 | 123.0698 | -0.14648 | 123.0286 | 60.9512 | -0.28839 | 123.0698 | -0.14648 | 60.9512 | 122.7081 | 123.0286 | -123.2941 | -123.2666
1866.7656 | 123.111 | -60.91 | 62.0682 | -0.17189 | -0.0054388 | -0.0074981 | 0.0024202 | 0.063096 | -0.0035141 | 0.068479 | -61.0428 | 62.1506 | -61.2167 | -61.1893 | 61.7798 | 0.032043 | 0.091553 | 0.15564 | 62.1368 | -61.2076 | -0.3067 | 0.082398 | -0.13275 | -0.27924 | -0.28839 | -0.29755 | 0.068665 | 0.17395 | 61.0016 | 61.0657 | 122.6898 | 123.0606 | -0.13275 | 123.0469 | 60.9421 | -0.29755 | 123.0606 | -0.13275 | 60.9421 | 122.6898 | 123.0469 | -123.2849 | -123.2758
1867.7656 | 123.0743 | -60.878 | 62.1002 | -0.21004 | -0.0069342 | -0.012412 | 0.00071144 | 0.06096 | -0.0050095 | 0.066343 | -61.0611 | 62.1414 | -61.1847 | -61.1664 | 61.7752 | 0.045776 | 0.13733 | 0.1831 | 62.1552 | -61.1755 | -0.3067 | 0.041198 | -0.1831 | -0.28839 | -0.32501 | -0.29755 | 0.054931 | 0.1236 | 61.0153 | 61.0611 | 122.6532 | 123.0194 | -0.1831 | 123.0331 | 60.9238 | -0.29755 | 123.0194 | -0.1831 | 60.9238 | 122.6532 | 123.0331 | -123.2849 | -123.2758
1868.7656 | 123.0743 | -60.8871 | 62.0819 | -0.18715 | -0.006507 | -0.0094207 | -0.0012112 | 0.0616 | -0.0056503 | 0.067624 | -61.0428 | 62.1506 | -61.1847 | -61.1435 | 61.7935 | 0.054932 | 0.14648 | 0.18768 | 62.1414 | -61.1801 | -0.29755 | 0.068665 | -0.15564 | -0.25635 | -0.28839 | -0.29297 | 0.059509 | 0.14191 | 61.0336 | 61.0748 | 122.6807 | 123.0377 | -0.15564 | 123.0286 | 60.9421 | -0.29297 | 123.0377 | -0.15564 | 60.9421 | 122.6807 | 123.0286 | -123.2666 | -123.262
1869.7656 | 123.0606 | -60.8963 | 62.0865 | -0.11085 | -0.0071478 | -0.0096343 | 0.0015658 | 0.059891 | -0.0054367 | 0.067197 | -61.0519 | 62.1552 | -61.1618 | -61.1526 | 61.8118 | 0.041199 | 0.1236 | 0.19226 | 62.1414 | -61.1938 | -0.2655 | 0.068664 | -0.15564 | -0.25635 | -0.27466 | -0.29755 | 0.054931 | 0.10986 | 61.0199 | 61.0886 | 122.7081 | 123.0515 | -0.15564 | 123.0377 | 60.9375 | -0.29755 | 123.0515 | -0.15564 | 60.9375 | 122.7081 | 123.0377 | -123.2483 | -123.2803
1870.7656 | 123.2071 | -60.8688 | 62.0453 | -0.16426 | -0.0077888 | -0.011343 | -0.0012112 | 0.059891 | -0.0047957 | 0.06442 | -60.9787 | 62.1094 | -61.1755 | -61.0748 | 61.8896 | 0.14191 | -0.009155 | 0.28381 | 62.0865 | -61.1389 | -0.3067 | 0.064087 | -0.10986 | -0.20599 | -0.15564 | -0.27008 | 0.041199 | 0.19684 | 60.8597 | 61.1526 | 122.7585 | 122.9782 | -0.10986 | 122.9553 | 61.0107 | -0.27008 | 122.9782 | -0.10986 | 61.0107 | 122.7585 | 122.9553 | -123.2208 | -123.1842
1871.7656 | 123.1201 | -60.8963 | 62.0682 | -0.19478 | -0.0041572 | -0.0096343 | 0.00028404 | 0.060105 | -0.0039413 | 0.067624 | -60.9879 | 62.1048 | -61.1755 | -61.0977 | 61.8256 | 0.086975 | 0.07782 | 0.23346 | 62.1323 | -61.171 | -0.27924 | 0.036621 | -0.091553 | -0.20142 | -0.24261 | -0.27466 | 0.064087 | 0.18768 | 60.9741 | 61.1298 | 122.7219 | 123.0011 | -0.091553 | 123.0286 | 60.9833 | -0.27466 | 123.0011 | -0.091553 | 60.9833 | 122.7219 | 123.0286 | -123.2437 | -123.2391
1872.7656 | 123.0927 | -60.91 | 62.1002 | -0.12611 | -0.0077888 | -0.01348 | 0.0039156 | 0.060105 | -0.0045821 | 0.066984 | -61.0519 | 62.1414 | -61.1664 | -61.1389 | 61.7889 | 0.041199 | 0.14648 | 0.18768 | 62.1185 | -61.1664 | -0.25635 | 0.041198 | -0.14191 | -0.22888 | -0.31128 | -0.25635 | 0.01831 | 0.11444 | 61.0565 | 61.0977 | 122.699 | 123.0515 | -0.14191 | 123.0286 | 60.9512 | -0.25635 | 123.0515 | -0.14191 | 60.9512 | 122.699 | 123.0286 | -123.2666 | -123.2666
1873.7656 | 123.1155 | -60.8917 | 62.0728 | -0.18715 | -0.0071478 | -0.010916 | 0.004343 | 0.059251 | -0.0037277 | 0.066343 | -61.0245 | 62.1368 | -61.171 | -61.1526 | 61.8118 | 0.050354 | 0.12817 | 0.20599 | 62.1323 | -61.1893 | -0.27923 | 0.064087 | -0.13275 | -0.26092 | -0.26093 | -0.29755 | 0.059509 | 0.14648 | 61.0199 | 61.0977 | 122.7036 | 123.0286 | -0.13275 | 123.024 | 60.9421 | -0.29755 | 123.0286 | -0.13275 | 60.9421 | 122.7036 | 123.024 | -123.2437 | -123.262
1874.7656 | 123.1384 | -60.8734 | 62.0499 | -0.17952 | -0.005866 | -0.0070709 | 0.0022066 | 0.060105 | -0.0060775 | 0.066984 | -60.997 | 62.1185 | -61.1893 | -61.1023 | 61.821 | 0.073242 | 0.086975 | 0.21973 | 62.1552 | -61.1526 | -0.31586 | 0.068664 | -0.1236 | -0.22888 | -0.22888 | -0.27924 | 0.10528 | 0.19226 | 60.9604 | 61.0931 | 122.6944 | 122.9919 | -0.1236 | 123.0286 | 60.9467 | -0.27924 | 122.9919 | -0.1236 | 60.9467 | 122.6944 | 123.0286 | -123.2391 | -123.2025
1875.7656 | 123.1659 | -60.8826 | 62.0728 | -0.19478 | -0.0069342 | -0.0070709 | 0.0015658 | 0.058823 | -0.0056503 | 0.067197 | -60.9924 | 62.0911 | -61.171 | -61.1069 | 61.8668 | 0.10529 | 0.041199 | 0.25177 | 62.114 | -61.1618 | -0.28839 | 0.01831 | -0.10986 | -0.22431 | -0.20599 | -0.27924 | 0.041199 | 0.17853 | 60.9238 | 61.1343 | 122.7493 | 122.9736 | -0.10986 | 122.9965 | 60.9879 | -0.27924 | 122.9736 | -0.10986 | 60.9879 | 122.7493 | 122.9965 | -123.2437 | -123.2346
1876.7656 | 123.175 | -60.8734 | 62.0453 | -0.15663 | -0.0084296 | -0.0072845 | 0.00049764 | 0.057755 | -0.0043685 | 0.065488 | -60.9741 | 62.1048 | -61.171 | -61.0565 | 61.8759 | 0.1236 | 0.018311 | 0.26093 | 62.0865 | -61.1481 | -0.29755 | 0.059509 | -0.10071 | -0.18311 | -0.16937 | -0.27466 | 0.041199 | 0.19684 | 60.8917 | 61.1343 | 122.7493 | 122.9782 | -0.10071 | 122.9599 | 60.997 | -0.27466 | 122.9782 | -0.10071 | 60.997 | 122.7493 | 122.9599 | -123.2162 | -123.1934
1877.7656 | 123.2391 | -60.8597 | 62.0316 | -0.057449 | -0.0086432 | -0.013693 | -0.00035676 | 0.056687 | -0.0050095 | 0.067197 | -60.9558 | 62.0499 | -61.1664 | -61.0382 | 61.8942 | 0.13733 | -0.050354 | 0.28381 | 62.0682 | -61.1435 | -0.3067 | 0.018311 | -0.096131 | -0.17853 | -0.13733 | -0.28381 | 0.036621 | 0.21057 | 60.8093 | 61.1435 | 122.7539 | 122.9095 | -0.096131 | 122.9279 | 60.997 | -0.28381 | 122.9095 | -0.096131 | 60.997 | 122.7539 | 122.9279 | -123.1979 | -123.175
1878.7656 | 123.2346 | -60.8597 | 62.0361 | -0.47707 | -0.006507 | -0.0089935 | -0.00014316 | 0.057542 | -0.0047957 | 0.067197 | -61.1481 | 62.0956 | -61.1526 | -61.0565 | 61.8851 | 0.14648 | -0.041199 | 0.29755 | 62.0544 | -61.1526 | -0.29297 | 0.059509 | -0.28839 | -0.19684 | -0.15106 | -0.29297 | 0.01831 | 0.004578 | 60.8185 | 61.1572 | 122.7448 | 122.9553 | -0.28839 | 122.9141 | 61.0062 | -0.29297 | 122.9553 | -0.28839 | 61.0062 | 122.7448 | 122.9141 | -123.1888 | -123.1888
1879.7656 | 123.1979 | -60.878 | 62.0636 | -0.14137 | -0.0071478 | -0.010062 | 0.0024202 | 0.057114 | -0.0054367 | 0.067624 | -60.9879 | 62.0682 | -61.171 | -61.0428 | 61.8805 | 0.1236 | 0.009155 | 0.28381 | 62.1094 | -61.1206 | -0.29297 | 0.004577 | -0.10986 | -0.16479 | -0.18311 | -0.24261 | 0.045776 | 0.18311 | 60.8871 | 61.1618 | 122.7585 | 122.9462 | -0.10986 | 122.9874 | 61.0016 | -0.24261 | 122.9462 | -0.10986 | 61.0016 | 122.7585 | 122.9874 | -123.2346 | -123.1842
1880.7656 | 123.2117 | -60.8551 | 62.0728 | -0.19478 | -0.009284 | -0.0096343 | 0.001993 | 0.060532 | -0.0060775 | 0.068906 | -60.9741 | 62.1002 | -61.171 | -61.0474 | 61.8896 | 0.13733 | -0.013733 | 0.27924 | 62.0819 | -61.1252 | -0.31586 | 0.027466 | -0.11902 | -0.19226 | -0.18311 | -0.27008 | 0.009155 | 0.19684 | 60.8414 | 61.1343 | 122.7448 | 122.9553 | -0.11902 | 122.937 | 60.9924 | -0.27008 | 122.9553 | -0.11902 | 60.9924 | 122.7448 | 122.937 | -123.2437 | -123.1979
1881.7656 | 123.1979 | -60.8597 | 62.0407 | 1.7278 | -0.008216 | -0.0098479 | 0.0030612 | 0.058396 | -0.0058639 | 0.067411 | -61.0062 | 62.0636 | -61.1801 | -61.0336 | 61.9263 | 0.1236 | -0.045776 | 0.27008 | 62.0728 | -61.1343 | -0.32044 | 0.022889 | -0.14649 | -0.17395 | -0.11444 | -0.27466 | 0.032044 | 0.17395 | 60.8139 | 61.1298 | 122.7859 | 122.9233 | -0.14649 | 122.9324 | 60.9833 | -0.27466 | 122.9233 | -0.14649 | 60.9833 | 122.7859 | 122.9324 | -123.2208 | -123.175
1882.7656 | 123.2071 | -60.878 | 62.027 | -0.12611 | -0.008216 | -0.010489 | 0.00028404 | 0.059251 | -0.0065047 | 0.068265 | -60.9741 | 62.0773 | -61.1755 | -61.2122 | 61.7889 | 0.11444 | -0.1236 | 0.30212 | 62.0544 | -61.1481 | -0.29755 | 0.050354 | -0.09613 | -0.33417 | -0.23804 | -0.27008 | 0.027465 | 0.20142 | 60.7544 | 61.1801 | 122.6669 | 122.9553 | -0.09613 | 122.9324 | 60.9924 | -0.27008 | 122.9553 | -0.09613 | 60.9924 | 122.6669 | 122.9324 | -123.2025 | -123.175
1883.7656 | 123.2941 | -60.8459 | 62.0728 | -0.13374 | -0.0067206 | -0.012625 | 0.0011386 | 0.058182 | -0.0054367 | 0.067197 | -60.965 | 62.0636 | -61.1801 | -61.0291 | 61.908 | 0.14191 | -0.064087 | 0.31586 | 62.0728 | -61.116 | -0.33417 | -0.009155 | -0.11902 | -0.18311 | -0.1648 | -0.27008 | 0 | 0.21515 | 60.7819 | 61.1618 | 122.7539 | 122.9095 | -0.11902 | 122.9187 | 60.9879 | -0.27008 | 122.9095 | -0.11902 | 60.9879 | 122.7539 | 122.9187 | -123.2529 | -123.1888
1884.7656 | 123.2208 | -60.8826 | 62.0453 | 0.0035856 | -0.0080024 | -0.012625 | 0.00049764 | 0.057542 | -0.0037277 | 0.066984 | -61.0016 | 62.0316 | -61.1801 | -61.0611 | 61.8896 | 0.11444 | -0.09613 | 0.22888 | 62.0316 | -61.1252 | -0.29755 | -0.013733 | -0.11902 | -0.17853 | -0.15564 | -0.24262 | -0.013733 | 0.17853 | 60.7864 | 61.1114 | 122.7722 | 122.9141 | -0.11902 | 122.9141 | 60.997 | -0.24262 | 122.9141 | -0.11902 | 60.997 | 122.7722 | 122.9141 | -123.2254 | -123.1705
1885.7656 | 123.2529 | -60.8688 | 62.0499 | -0.20241 | -0.0080024 | -0.012412 | 0.00028404 | 0.057328 | -0.0060775 | 0.066556 | -60.965 | 62.0728 | -61.1526 | -61.0153 | 61.9171 | 0.15106 | -0.086975 | 0.29755 | 62.0682 | -61.1435 | -0.28381 | 0.022888 | -0.096131 | -0.14649 | -0.13275 | -0.27466 | 0.01831 | 0.18768 | 60.7819 | 61.1664 | 122.7859 | 122.9416 | -0.096131 | 122.937 | 61.0199 | -0.27466 | 122.9416 | -0.096131 | 61.0199 | 122.7859 | 122.937 | -123.2025 | -123.1934
1886.7656 | 123.2437 | -60.8734 | 62.0499 | -0.149 | -0.0088568 | -0.012839 | 0.00071144 | 0.056473 | -0.0062911 | 0.065916 | -60.9741 | 62.059 | -61.1618 | -60.8826 | 62.1689 | 0.32959 | -0.25635 | 0.29297 | 62.0728 | -61.116 | -0.28839 | 0.009155 | -0.10071 | -0.009155 | 0.11902 | -0.24262 | 0.022888 | 0.18768 | 60.6171 | 61.1664 | 123.0423 | 122.9324 | -0.10071 | 122.9462 | 61.203 | -0.24262 | 122.9324 | -0.10071 | 61.203 | 123.0423 | 122.9462 | -123.2117 | -123.1659
1887.7656 | 123.23 | -60.8597 | 62.0407 | -0.13374 | -0.0084296 | -0.0083527 | 0.0013522 | 0.058396 | -0.0075729 | 0.066984 | -60.9558 | 62.0636 | -61.1435 | -61.0382 | 61.9034 | 0.13733 | -0.064087 | 0.30212 | 62.0682 | -61.1343 | -0.28381 | 0.022889 | -0.096131 | -0.17853 | -0.13733 | -0.27466 | 0.027466 | 0.18768 | 60.7956 | 61.1618 | 122.7631 | 122.9233 | -0.096131 | 122.9279 | 60.997 | -0.27466 | 122.9233 | -0.096131 | 60.997 | 122.7631 | 122.9279 | -123.1842 | -123.175
1888.7656 | 123.2483 | -60.8734 | 62.0453 | -0.15663 | -0.0080024 | -0.0077117 | -0.00035676 | 0.05861 | -0.0045821 | 0.06912 | -60.965 | 62.0453 | -61.1664 | -61.0153 | 61.9263 | 0.14648 | -0.10529 | 0.28839 | 62.0407 | -61.1069 | -0.29297 | 0 | -0.091553 | -0.14191 | -0.11902 | -0.23346 | -0.004578 | 0.20142 | 60.7681 | 61.1618 | 122.7997 | 122.9187 | -0.091553 | 122.9141 | 61.0199 | -0.23346 | 122.9187 | -0.091553 | 61.0199 | 122.7997 | 122.9141 | -123.2117 | -123.1522
1889.7656 | 123.23 | -60.8505 | 62.0361 | -0.065079 | -0.0069342 | -0.013052 | 0.00028404 | 0.057755 | -0.0052231 | 0.067411 | -60.9741 | 62.0453 | -61.1893 | -61.0107 | 61.8988 | 0.13733 | -0.10071 | 0.27008 | 62.0361 | -61.1298 | -0.33875 | 0.009155 | -0.1236 | -0.16022 | -0.13733 | -0.27924 | 0 | 0.21515 | 60.7498 | 61.1206 | 122.7493 | 122.8958 | -0.1236 | 122.8867 | 60.9879 | -0.27924 | 122.8958 | -0.1236 | 60.9879 | 122.7493 | 122.8867 | -123.2254 | -123.1659
1890.7656 | 123.2208 | -60.8597 | 62.0361 | -0.034561 | -0.0073614 | -0.012412 | 7.0444e-05 | 0.058182 | -0.0039413 | 0.067838 | -61.0107 | 62.0499 | -61.1481 | -61.0565 | 61.8942 | 0.11444 | -0.07782 | 0.24719 | 62.059 | -61.1343 | -0.28839 | 0.013733 | -0.15106 | -0.19684 | -0.14191 | -0.27466 | 0.022888 | 0.13733 | 60.7819 | 61.1069 | 122.7539 | 122.9095 | -0.15106 | 122.9187 | 60.9741 | -0.27466 | 122.9095 | -0.15106 | 60.9741 | 122.7539 | 122.9187 | -123.1842 | -123.1705
1891.7656 | 123.1842 | -60.8963 | 62.0316 | 0.049362 | -0.0052252 | -0.010916 | 0.00071144 | 0.056473 | -0.0050095 | 0.066556 | -61.0474 | 62.059 | -61.1847 | -61.0886 | 61.821 | 0.004578 | -0.068665 | 0.15564 | 62.0316 | -61.1298 | -0.28839 | 0.027466 | -0.15106 | -0.19226 | -0.21057 | -0.23346 | 0 | 0.13733 | 60.8276 | 61.0519 | 122.7173 | 122.9553 | -0.15106 | 122.9279 | 60.9009 | -0.23346 | 122.9553 | -0.15106 | 60.9009 | 122.7173 | 122.9279 | -123.2162 | -123.1613
1892.7656 | 123.1888 | -60.878 | 62.027 | 0.07988 | -0.0060798 | -0.013266 | 0.0017794 | 0.059251 | -0.0030869 | 0.066343 | -61.0428 | 62.0499 | -61.1664 | -61.0794 | 61.8347 | 0.068665 | -0.068665 | 0.21057 | 62.0316 | -61.1526 | -0.28839 | 0.022888 | -0.16479 | -0.20142 | -0.19226 | -0.27466 | 0.004577 | 0.1236 | 60.8093 | 61.0886 | 122.7127 | 122.9279 | -0.16479 | 122.9095 | 60.9467 | -0.27466 | 122.9279 | -0.16479 | 60.9467 | 122.7127 | 122.9095 | -123.1934 | -123.1796
1893.7656 | 123.2025 | -60.8734 | 62.0453 | -0.095596 | -0.0077888 | -0.0092071 | 0.00071144 | 0.056473 | -0.0033005 | 0.067624 | -61.0016 | 62.0819 | -61.1847 | -61.0748 | 61.8942 | 0.091553 | -0.091553 | 0.24719 | 62.0544 | -61.1435 | -0.31128 | 0.036621 | -0.12817 | -0.20142 | -0.15106 | -0.27008 | 0.009155 | 0.1831 | 60.7819 | 61.1206 | 122.7676 | 122.9553 | -0.12817 | 122.9279 | 60.965 | -0.27008 | 122.9553 | -0.12817 | 60.965 | 122.7676 | 122.9279 | -123.23 | -123.1888
1894.7656 | 123.1979 | -60.8643 | 62.0361 | -0.019302 | -0.0084296 | -0.01113 | 0.0013522 | 0.056901 | -0.0050095 | 0.068479 | -61.0428 | 62.0361 | -61.1893 | -61.0657 | 61.8622 | 0.091553 | -0.091553 | 0.22888 | 62.0499 | -61.116 | -0.32501 | 0 | -0.17853 | -0.20142 | -0.17395 | -0.25177 | 0.013733 | 0.14648 | 60.7727 | 61.0931 | 122.7264 | 122.9004 | -0.17853 | 122.9141 | 60.9558 | -0.25177 | 122.9004 | -0.17853 | 60.9558 | 122.7264 | 122.9141 | -123.2254 | -123.1522
1895.7656 | 123.1934 | -60.8917 | 62.0544 | 0.072251 | -0.0060798 | -0.015402 | -0.0012112 | 0.059464 | -0.0035141 | 0.065916 | -61.0428 | 62.0499 | -61.1755 | -61.0748 | 61.8622 | 0.036621 | -0.068665 | 0.20599 | 62.0453 | -61.1481 | -0.28381 | -0.004577 | -0.15106 | -0.1831 | -0.19226 | -0.25635 | -0.009155 | 0.13275 | 60.8231 | 61.0977 | 122.7539 | 122.9416 | -0.15106 | 122.937 | 60.9283 | -0.25635 | 122.9416 | -0.15106 | 60.9283 | 122.7539 | 122.937 | -123.23 | -123.2025
1896.7656 | 123.1888 | -60.9055 | 62.0453 | 0.40031 | -0.0090704 | -0.013266 | -0.00035676 | 0.059037 | -0.0026595 | 0.065916 | -61.0703 | 62.059 | -61.171 | -61.0886 | 61.8347 | 0.036621 | -0.068665 | 0.17395 | 62.0361 | -61.1572 | -0.2655 | 0.013733 | -0.16479 | -0.18311 | -0.21057 | -0.25177 | -0.009155 | 0.10071 | 60.8368 | 61.0794 | 122.7402 | 122.9645 | -0.16479 | 122.9416 | 60.9421 | -0.25177 | 122.9645 | -0.16479 | 60.9421 | 122.7402 | 122.9416 | -123.2162 | -123.2025
1897.7656 | 123.1934 | -60.8688 | 62.0544 | 0.13329 | -0.0067206 | -0.01348 | 0.00028404 | 0.059891 | -0.0050095 | 0.068693 | -61.0565 | 62.0499 | -61.2259 | -61.1389 | 61.8484 | 0.022888 | -0.09613 | 0.19226 | 62.0453 | -61.1206 | -0.35706 | -0.004577 | -0.18768 | -0.27008 | -0.20599 | -0.25177 | -0.009155 | 0.16937 | 60.7727 | 61.0611 | 122.7173 | 122.9187 | -0.18768 | 122.9141 | 60.8917 | -0.25177 | 122.9187 | -0.18768 | 60.8917 | 122.7173 | 122.9141 | -123.2803 | -123.175
1898.7656 | 123.1888 | -60.8871 | 62.027 | 0.17143 | -0.0069342 | -0.010916 | 0.001993 | 0.057542 | -0.0039413 | 0.067624 | -61.0245 | 62.027 | -61.2167 | -61.1023 | 61.8256 | 0.018311 | -0.13733 | 0.13733 | 62.0224 | -61.1435 | -0.32959 | 0 | -0.13733 | -0.21515 | -0.20142 | -0.25635 | -0.004578 | 0.19226 | 60.7498 | 61.0245 | 122.7127 | 122.9141 | -0.13733 | 122.9095 | 60.9055 | -0.25635 | 122.9141 | -0.13733 | 60.9055 | 122.7127 | 122.9095 | -123.2437 | -123.1705
1899.7656 | 123.1888 | -60.8734 | 62.027 | 0.66734 | -0.0069342 | -0.015616 | 0.00028404 | 0.05861 | -0.0037277 | 0.068052 | -61.0245 | 62.0728 | -61.1664 | -61.1206 | 61.8301 | 0.032043 | -0.07782 | 0.16937 | 62.0682 | -61.1481 | -0.29297 | 0.045776 | -0.15106 | -0.24719 | -0.19684 | -0.27466 | 0.041198 | 0.14191 | 60.7956 | 61.0428 | 122.7036 | 122.9462 | -0.15106 | 122.9416 | 60.9055 | -0.27466 | 122.9462 | -0.15106 | 60.9055 | 122.7036 | 122.9416 | -123.1934 | -123.175
1900.7656 | 123.1476 | -60.8871 | 62.027 | 0.087509 | -0.0077888 | -0.011771 | 0.0011386 | 0.05861 | -0.0024459 | 0.068693 | -61.0474 | 62.0636 | -61.171 | -61.1114 | 61.9263 | 0.16937 | -0.11902 | 0.13275 | 62.0682 | -61.1526 | -0.28381 | 0.036621 | -0.16022 | -0.2243 | -0.10071 | -0.2655 | 0.041198 | 0.1236 | 60.7681 | 61.0199 | 122.8134 | 122.9507 | -0.16022 | 122.9553 | 61.0565 | -0.2655 | 122.9507 | -0.16022 | 61.0565 | 122.8134 | 122.9553 | -123.1979 | -123.1796
1901.7656 | 123.1567 | -60.8871 | 62.0316 | 0.064621 | -0.006507 | -0.010062 | 0.00071144 | 0.058823 | -0.0067185 | 0.066984 | -61.0382 | 62.0407 | -61.1984 | -61.1206 | 61.821 | 0.022888 | -0.082397 | 0.15564 | 62.0407 | -61.1481 | -0.31128 | 0.009155 | -0.15106 | -0.23346 | -0.21057 | -0.26093 | 0.009155 | 0.16022 | 60.8047 | 61.0428 | 122.7081 | 122.9279 | -0.15106 | 122.9279 | 60.91 | -0.26093 | 122.9279 | -0.15106 | 60.91 | 122.7081 | 122.9279 | -123.23 | -123.1796
1902.7656 | 123.1705 | -60.8871 | 62.0316 | 0.14092 | -0.0069342 | -0.013907 | 0.0028476 | 0.058182 | -0.0050095 | 0.067838 | -61.0382 | 62.059 | -61.1664 | -61.116 | 61.8393 | 0.018311 | -0.09613 | 0.13275 | 62.0499 | -61.1618 | -0.27924 | 0.027466 | -0.15106 | -0.22888 | -0.19226 | -0.27466 | 0.018311 | 0.12817 | 60.791 | 61.0199 | 122.7264 | 122.9462 | -0.15106 | 122.937 | 60.9055 | -0.27466 | 122.9462 | -0.15106 | 60.9055 | 122.7264 | 122.937 | -123.1979 | -123.1934
1903.7656 | 123.1567 | -60.8826 | 62.0178 | 0.18669 | -0.0054388 | -0.0070709 | 0.0015658 | 0.06096 | -0.0043685 | 0.066984 | -61.0199 | 62.0316 | -61.1938 | -61.1114 | 61.8393 | 0.013733 | -0.12817 | 0.13275 | 62.0178 | -61.1435 | -0.31128 | 0.013733 | -0.13733 | -0.22888 | -0.17853 | -0.26093 | 0 | 0.17395 | 60.7544 | 61.0153 | 122.7219 | 122.9141 | -0.13733 | 122.9004 | 60.8963 | -0.26093 | 122.9141 | -0.13733 | 60.8963 | 122.7219 | 122.9004 | -123.2117 | -123.1613
1904.7656 | 123.1979 | -60.8551 | 61.9949 | 0.25536 | -0.005866 | -0.0085663 | 0.003702 | 0.060319 | -0.0058639 | 0.06677 | -60.9833 | 62.027 | -61.1938 | -61.2076 | 61.9537 | 0.11902 | -0.16479 | 0.19226 | 62.0407 | -61.1435 | -0.33875 | 0.032044 | -0.12817 | -0.35248 | -0.041199 | -0.28839 | 0.045776 | 0.21057 | 60.6903 | 61.0474 | 122.8088 | 122.8821 | -0.12817 | 122.8958 | 60.9741 | -0.28839 | 122.8821 | -0.12817 | 60.9741 | 122.8088 | 122.8958 | -123.1888 | -123.1384
1905.7656 | 123.1934 | -60.878 | 62.0041 | 0.14092 | -0.0062934 | -0.0060027 | 0.002634 | 0.060105 | -0.0056503 | 0.068052 | -61.0016 | 62.0499 | -61.203 | -61.0703 | 61.8622 | 0.036621 | -0.19226 | 0.15106 | 62.0499 | -61.1435 | -0.32501 | 0.045777 | -0.1236 | -0.19226 | -0.14191 | -0.2655 | 0.045777 | 0.20142 | 60.6857 | 61.0291 | 122.7402 | 122.9279 | -0.1236 | 122.9279 | 60.9146 | -0.2655 | 122.9279 | -0.1236 | 60.9146 | 122.7402 | 122.9279 | -123.2071 | -123.1476
1906.7656 | 123.1934 | -60.878 | 61.9995 | 0.21721 | -0.0054388 | -0.01113 | 0.0015658 | 0.057969 | -0.0050095 | 0.064634 | -61.0016 | 62.0316 | -61.203 | -61.0977 | 61.8576 | 0.036621 | -0.1831 | 0.15106 | 62.0224 | -61.1526 | -0.32501 | 0.032043 | -0.1236 | -0.21973 | -0.14191 | -0.27466 | 0.022888 | 0.20142 | 60.6949 | 61.0291 | 122.7356 | 122.9095 | -0.1236 | 122.9004 | 60.9146 | -0.27466 | 122.9095 | -0.1236 | 60.9146 | 122.7356 | 122.9004 | -123.2025 | -123.1522
1907.7656 | 123.2117 | -60.8688 | 61.9766 | 0.14854 | -0.0043708 | -0.0083527 | 0.0039156 | 0.059891 | -0.0060775 | 0.069761 | -61.0016 | 62.0636 | -61.171 | -61.0794 | 61.8896 | 0.041199 | -0.19684 | 0.14191 | 62.0499 | -61.1389 | -0.30212 | 0.086975 | -0.13275 | -0.21057 | -0.086976 | -0.27008 | 0.073242 | 0.16937 | 60.672 | 61.0107 | 122.7585 | 122.9324 | -0.13275 | 122.9187 | 60.91 | -0.27008 | 122.9324 | -0.13275 | 60.91 | 122.7585 | 122.9187 | -123.1476 | -123.1155
1908.7656 | 123.2254 | -60.8459 | 62.0041 | 0.20958 | -0.0052252 | -0.0089935 | 0.0041292 | 0.060105 | -0.0067185 | 0.065488 | -60.9833 | 62.0453 | -61.1801 | -60.9924 | 61.8988 | 0.050354 | -0.16022 | 0.18768 | 62.0499 | -61.1481 | -0.33417 | 0.041199 | -0.13733 | -0.14648 | -0.10529 | -0.30212 | 0.045777 | 0.19684 | 60.6857 | 61.0336 | 122.7448 | 122.8912 | -0.13733 | 122.8958 | 60.8963 | -0.30212 | 122.8912 | -0.13733 | 60.8963 | 122.7448 | 122.8958 | -123.1842 | -123.1522
1909.7656 | 123.2254 | -60.8917 | 61.9675 | 0.27061 | -0.004798 | -0.0051483 | 0.0045566 | 0.061814 | -0.0043685 | 0.068906 | -60.9833 | 62.0865 | -61.1938 | -61.0931 | 61.8622 | 0.036621 | -0.19684 | 0.15106 | 62.0178 | -61.1572 | -0.30212 | 0.11902 | -0.091552 | -0.20142 | -0.10528 | -0.2655 | 0.050354 | 0.21057 | 60.6949 | 61.0428 | 122.7539 | 122.9782 | -0.091552 | 122.9095 | 60.9283 | -0.2655 | 122.9782 | -0.091552 | 60.9283 | 122.7539 | 122.9095 | -123.1613 | -123.1247
1910.7656 | 123.2162 | -60.8917 | 61.9904 | 0.30113 | -0.0037298 | -0.0081389 | 0.003702 | 0.061387 | -0.0033005 | 0.067624 | -61.0062 | 62.0956 | -61.203 | -61.1298 | 61.8073 | 0.027466 | -0.15564 | 0.11444 | 62.0316 | -61.1801 | -0.31128 | 0.10529 | -0.11444 | -0.23804 | -0.1831 | -0.28839 | 0.041199 | 0.19684 | 60.7361 | 61.0062 | 122.699 | 122.9874 | -0.11444 | 122.9233 | 60.9192 | -0.28839 | 122.9874 | -0.11444 | 60.9192 | 122.699 | 122.9233 | -123.1934 | -123.1705
1911.7656 | 123.1384 | -60.9467 | 62.0499 | 0.14854 | -0.0041572 | -0.010489 | 0.0064792 | 0.062882 | -0.0058639 | 0.068265 | -61.0062 | 62.1552 | -61.1984 | -61.1801 | 61.7569 | -0.054932 | -0.018311 | 0.036621 | 62.0956 | -61.2076 | -0.25177 | 0.10528 | -0.05951 | -0.23346 | -0.29297 | -0.26093 | 0.045776 | 0.19226 | 60.9283 | 60.9833 | 122.7036 | 123.1018 | -0.05951 | 123.0423 | 60.8917 | -0.26093 | 123.1018 | -0.05951 | 60.8917 | 122.7036 | 123.0423 | -123.2483 | -123.2574
1912.7656 | 123.1064 | -60.9146 | 62.0636 | 0.22484 | -0.0041572 | -0.0079253 | 0.003702 | 0.063737 | -0.0062911 | 0.068693 | -61.0565 | 62.1506 | -61.2122 | -61.1618 | 61.7615 | -0.064087 | -0.33875 | -0.22888 | 62.0453 | -61.2259 | -0.29755 | 0.086975 | -0.14191 | -0.24719 | -0.30212 | -0.31128 | -0.018311 | 0.15564 | 60.5759 | 60.6857 | 122.6761 | 123.0652 | -0.14191 | 122.9599 | 60.8505 | -0.31128 | 123.0652 | -0.14191 | 60.8505 | 122.6761 | 122.9599 | -123.2758 | -123.2895
1913.7656 | 123.1384 | -60.9055 | 62.0087 | 0.27061 | -0.0035162 | -0.0072845 | 0.003702 | 0.064164 | -0.0047957 | 0.069547 | -61.0245 | 62.1048 | -61.2122 | -61.1526 | 61.821 | -0.022888 | -0.10986 | 0.091553 | 62.059 | -61.2076 | -0.3067 | 0.09613 | -0.11902 | -0.24719 | -0.18768 | -0.30212 | 0.050354 | 0.18768 | 60.7956 | 60.997 | 122.7264 | 123.0103 | -0.11902 | 122.9645 | 60.8826 | -0.30212 | 123.0103 | -0.11902 | 60.8826 | 122.7264 | 122.9645 | -123.2208 | -123.2162
1914.7656 | 123.1247 | -60.9238 | 62.0041 | 0.23247 | -0.0018072 | -0.0070709 | 0.0032748 | 0.060746 | -0.0056503 | 0.068693 | -61.0519 | 62.1826 | -61.2305 | -61.1801 | 61.7661 | -0.032043 | -0.064087 | 0.054932 | 62.0819 | -61.2076 | -0.3067 | 0.17853 | -0.12817 | -0.25635 | -0.23804 | -0.28381 | 0.07782 | 0.17853 | 60.8597 | 60.9787 | 122.6898 | 123.1064 | -0.12817 | 123.0057 | 60.8917 | -0.28381 | 123.1064 | -0.12817 | 60.8917 | 122.6898 | 123.0057 | -123.2346 | -123.2117
1915.7656 | 123.111 | -60.91 | 62.0407 | 0.46135 | -0.0039434 | -0.0085663 | 0.0060518 | 0.062241 | -0.0047957 | 0.068693 | -61.0291 | 62.1597 | -61.2122 | -61.1801 | 61.7798 | -0.041199 | -0.009155 | 0.050354 | 62.0636 | -61.2534 | -0.30212 | 0.11902 | -0.11902 | -0.27008 | -0.26093 | -0.34332 | 0.022889 | 0.18311 | 60.9009 | 60.9604 | 122.6898 | 123.0698 | -0.11902 | 122.9736 | 60.8688 | -0.34332 | 123.0698 | -0.11902 | 60.8688 | 122.6898 | 122.9736 | -123.2529 | -123.2941
1916.7656 | 123.1155 | -60.9329 | 62.0224 | 0.20195 | -0.0028754 | -0.011343 | 0.0047702 | 0.063737 | -0.0041549 | 0.068906 | -61.0519 | 62.1597 | -61.2259 | -61.3541 | 61.9583 | 0.1236 | 0.073242 | 0.10986 | 62.0956 | -61.2122 | -0.29297 | 0.13733 | -0.11902 | -0.42114 | -0.064087 | -0.27924 | 0.073242 | 0.17395 | 61.0062 | 61.0428 | 122.8912 | 123.0927 | -0.11902 | 123.0286 | 61.0565 | -0.27924 | 123.0927 | -0.11902 | 61.0565 | 122.8912 | 123.0286 | -123.2483 | -123.2346
1917.7656 | 123.0881 | -60.9421 | 62.0453 | 0.13329 | -0.0037298 | -0.0049347 | 0.0060518 | 0.065232 | -0.0060775 | 0.071042 | -61.084 | 62.1872 | -61.2305 | -61.235 | 61.734 | -0.041199 | -0.004578 | 0.032043 | 62.0865 | -61.2213 | -0.28839 | 0.14191 | -0.14191 | -0.29297 | -0.31128 | -0.27923 | 0.041199 | 0.14648 | 60.9375 | 60.9741 | 122.6761 | 123.1293 | -0.14191 | 123.0286 | 60.9009 | -0.27923 | 123.1293 | -0.14191 | 60.9009 | 122.6761 | 123.0286 | -123.2758 | -123.2666
1918.7656 | 123.0881 | -60.9009 | 62.0544 | 0.011215 | -0.0037298 | -0.0089935 | 0.0066928 | 0.06395 | -0.0062911 | 0.068265 | -60.9879 | 62.178 | -61.203 | -61.1435 | 61.8301 | 0.004578 | 0.032043 | 0.11444 | 62.114 | -61.2213 | -0.30212 | 0.1236 | -0.086975 | -0.24261 | -0.2243 | -0.32043 | 0.05951 | 0.21515 | 60.9329 | 61.0153 | 122.731 | 123.0789 | -0.086975 | 123.0148 | 60.9055 | -0.32043 | 123.0789 | -0.086975 | 60.9055 | 122.731 | 123.0148 | -123.2574 | -123.2758
1919.7656 | 123.111 | -60.9238 | 62.0682 | 0.064621 | -0.0033026 | -0.0051483 | 0.0039156 | 0.064805 | -0.0047957 | 0.066984 | -61.0336 | 62.178 | -61.2167 | -61.171 | 61.7889 | -0.004578 | 0.041199 | 0.09613 | 62.0911 | -61.2167 | -0.29297 | 0.10986 | -0.10986 | -0.24719 | -0.27924 | -0.29297 | 0.022888 | 0.18311 | 60.965 | 61.0199 | 122.7127 | 123.1018 | -0.10986 | 123.0148 | 60.9192 | -0.29297 | 123.1018 | -0.10986 | 60.9192 | 122.7127 | 123.0148 | -123.2849 | -123.2849
1920.7656 | 123.0972 | -60.9512 | 62.059 | 0.1104 | -0.0024482 | -0.0083527 | 0.0013522 | 0.0663 | -0.0058639 | 0.068052 | -61.0611 | 62.2009 | -61.235 | -61.2167 | 61.7661 | -0.054932 | 0.027466 | 0.036621 | 62.1094 | -61.235 | -0.28381 | 0.14191 | -0.10986 | -0.2655 | -0.29297 | -0.28381 | 0.050354 | 0.17395 | 60.9787 | 60.9879 | 122.7173 | 123.1522 | -0.10986 | 123.0606 | 60.8963 | -0.28381 | 123.1522 | -0.10986 | 60.8963 | 122.7173 | 123.0606 | -123.2941 | -123.2941
1921.7656 | 123.0881 | -60.9192 | 62.0453 | 0.1104 | -0.0018072 | -0.0057891 | 0.0056246 | 0.065018 | -0.0043685 | 0.069761 | -61.0291 | 62.1872 | -61.2076 | -61.1801 | 61.7661 | -0.009155 | 0.032043 | 0.086975 | 62.0819 | -61.2076 | -0.28839 | 0.14191 | -0.10986 | -0.26093 | -0.27924 | -0.28839 | 0.036621 | 0.17853 | 60.9512 | 61.0062 | 122.6852 | 123.1064 | -0.10986 | 123.0011 | 60.91 | -0.28839 | 123.1064 | -0.10986 | 60.91 | 122.6852 | 123.0011 | -123.2529 | -123.2529
1922.7656 | 123.1247 | -60.9146 | 62.0361 | 0.095139 | -0.00138 | -0.0057891 | 0.0039156 | 0.067155 | -0.0052231 | 0.070188 | -61.0199 | 62.1918 | -61.203 | -61.1618 | 61.8118 | 0.009155 | 0.036621 | 0.10529 | 62.1048 | -61.2076 | -0.28839 | 0.15564 | -0.10529 | -0.24719 | -0.2243 | -0.29297 | 0.068664 | 0.18311 | 60.9512 | 61.0199 | 122.7264 | 123.1064 | -0.10529 | 123.0194 | 60.9238 | -0.29297 | 123.1064 | -0.10529 | 60.9238 | 122.7264 | 123.0194 | -123.2391 | -123.2437
1923.7656 | 123.1384 | -60.91 | 62.0544 | -0.026932 | -0.0033026 | -0.0089935 | 0.0045566 | 0.066087 | -0.0062911 | 0.068479 | -61.0153 | 62.1826 | -61.2167 | -61.1435 | 61.821 | 0.022888 | 0.036621 | 0.14191 | 62.114 | -61.235 | -0.3067 | 0.12817 | -0.10529 | -0.23346 | -0.23346 | -0.32501 | 0.05951 | 0.20142 | 60.9467 | 61.0519 | 122.731 | 123.0927 | -0.10529 | 123.024 | 60.9329 | -0.32501 | 123.0927 | -0.10529 | 60.9329 | 122.731 | 123.024 | -123.2712 | -123.2895
1924.7656 | 123.1384 | -60.8826 | 62.0728 | 0.30113 | -0.0035162 | -0.0096343 | 0.0039156 | 0.064378 | -0.0060775 | 0.067197 | -60.9467 | 62.2009 | -61.2076 | -61.116 | 61.8301 | 0.054932 | 0.027466 | 0.16022 | 62.1185 | -61.2076 | -0.32501 | 0.12817 | -0.064087 | -0.23346 | -0.24262 | -0.32501 | 0.045776 | 0.26093 | 60.91 | 61.0428 | 122.7127 | 123.0835 | -0.064087 | 123.0011 | 60.9375 | -0.32501 | 123.0835 | -0.064087 | 60.9375 | 122.7127 | 123.0011 | -123.2803 | -123.2803
1925.7656 | 123.1338 | -60.8917 | 62.0636 | -0.11848 | -0.0052252 | -0.0092071 | 0.0024202 | 0.063096 | -0.0058639 | 0.067411 | -61.0062 | 62.2238 | -61.1893 | -61.1298 | 61.8484 | 0.086975 | 0.059509 | 0.18768 | 62.1323 | -61.1938 | -0.29755 | 0.16022 | -0.11444 | -0.23804 | -0.21515 | -0.30212 | 0.068664 | 0.1831 | 60.9512 | 61.0794 | 122.7402 | 123.1155 | -0.11444 | 123.024 | 60.9787 | -0.30212 | 123.1155 | -0.11444 | 60.9787 | 122.7402 | 123.024 | -123.2529 | -123.2574
1926.7656 | 123.1247 | -60.8917 | 62.0407 | -0.087967 | -0.004798 | -0.0072845 | 0.003702 | 0.062882 | -0.0054367 | 0.067411 | -60.997 | 62.2192 | -61.203 | -61.1252 | 61.8439 | 0.082397 | 0.054932 | 0.20599 | 62.0956 | -61.2076 | -0.31128 | 0.17853 | -0.10528 | -0.23346 | -0.19684 | -0.31586 | 0.054932 | 0.20599 | 60.9467 | 61.0977 | 122.7356 | 123.111 | -0.10528 | 122.9874 | 60.9741 | -0.31586 | 123.111 | -0.10528 | 60.9741 | 122.7356 | 122.9874 | -123.2437 | -123.2483
1927.7656 | 123.1201 | -60.9009 | 62.0453 | -0.019302 | -0.0041572 | -0.0092071 | 0.004343 | 0.065659 | -0.0056503 | 0.067624 | -60.9192 | 62.1826 | -61.2076 | -61.1389 | 61.821 | 0.045776 | 0.027466 | 0.18768 | 62.1094 | -61.2167 | -0.3067 | 0.13733 | -0.01831 | -0.23804 | -0.2243 | -0.31586 | 0.064087 | 0.28839 | 60.9283 | 61.0886 | 122.7219 | 123.0835 | -0.01831 | 123.0103 | 60.9467 | -0.31586 | 123.0835 | -0.01831 | 60.9467 | 122.7219 | 123.0103 | -123.2529 | -123.262
1928.7656 | 123.0698 | -60.91 | 62.0361 | -0.04219 | -0.0039434 | -0.0068573 | 0.0034884 | 0.062028 | -0.0054367 | 0.068479 | -60.997 | 62.1826 | -61.1801 | -61.1206 | 61.8484 | 0.082397 | 0.041199 | 0.19684 | 62.1048 | -61.2076 | -0.27008 | 0.14648 | -0.086975 | -0.21057 | -0.18768 | -0.29755 | 0.068664 | 0.18311 | 60.9512 | 61.1069 | 122.7585 | 123.0927 | -0.086975 | 123.0148 | 60.9924 | -0.29755 | 123.0927 | -0.086975 | 60.9924 | 122.7585 | 123.0148 | -123.2162 | -123.2437
1929.7812 | 123.23 | -60.9146 | 61.94 | 0.2401 | -0.0043708 | -0.0036529 | 0.0011386 | 0.065446 | -0.0026595 | 0.068479 | -61.0153 | 62.0728 | -61.1984 | -61.1252 | 61.8576 | 0.041199 | -0.17853 | 0.16022 | 62.0453 | -61.2076 | -0.28381 | 0.13275 | -0.10071 | -0.21057 | -0.082397 | -0.29297 | 0.10529 | 0.1831 | 60.7361 | 61.0748 | 122.7722 | 122.9874 | -0.10071 | 122.9599 | 60.9558 | -0.29297 | 122.9874 | -0.10071 | 60.9558 | 122.7722 | 122.9599 | -123.1384 | -123.1476
1930.7656 | 123.1201 | -60.91 | 62.0544 | -0.072708 | -0.0045844 | -0.0042937 | 0.004343 | 0.062241 | -0.0045821 | 0.068052 | -61.0016 | 62.2009 | -61.1847 | -61.1298 | 61.8256 | 0.073242 | 0.073242 | 0.21057 | 62.1643 | -61.2076 | -0.27466 | 0.14648 | -0.091553 | -0.21973 | -0.22888 | -0.29755 | 0.10986 | 0.1831 | 60.9833 | 61.1206 | 122.7356 | 123.111 | -0.091553 | 123.0743 | 60.9833 | -0.29755 | 123.111 | -0.091553 | 60.9833 | 122.7356 | 123.0743 | -123.2391 | -123.262
1931.7656 | 123.0927 | -60.8917 | 62.0773 | -0.080337 | -0.0039434 | -0.010275 | 0.0024202 | 0.062455 | -0.0080001 | 0.067838 | -61.0474 | 62.1735 | -61.1984 | -61.1618 | 61.7935 | 0.041199 | 0.1236 | 0.16022 | 62.1323 | -61.2122 | -0.3067 | 0.09613 | -0.15564 | -0.27008 | -0.28381 | -0.32043 | 0.054931 | 0.15106 | 61.0153 | 61.0519 | 122.6852 | 123.0652 | -0.15564 | 123.024 | 60.9329 | -0.32043 | 123.0652 | -0.15564 | 60.9329 | 122.6852 | 123.024 | -123.2758 | -123.2895
1932.7656 | 123.1064 | -60.9009 | 62.0956 | -0.17952 | -0.0045844 | -0.0077117 | 0.0022066 | 0.062241 | -0.0041549 | 0.068052 | -61.0565 | 62.178 | -61.203 | -61.1984 | 61.7798 | 0.022888 | 0.12817 | 0.16937 | 62.1094 | -61.2213 | -0.30212 | 0.082398 | -0.15564 | -0.29755 | -0.31586 | -0.32043 | 0.013733 | 0.14648 | 61.0291 | 61.0703 | 122.6807 | 123.0789 | -0.15564 | 123.0103 | 60.9238 | -0.32043 | 123.0789 | -0.15564 | 60.9238 | 122.6807 | 123.0103 | -123.2986 | -123.317
1933.7656 | 123.0743 | -60.8688 | 62.1185 | -0.20241 | -0.0067206 | -0.010062 | 0.00092504 | 0.061814 | -0.0052231 | 0.06677 | -61.0703 | 62.1964 | -61.1984 | -61.1572 | 61.7981 | 0.059509 | 0.14191 | 0.17853 | 62.146 | -61.2122 | -0.32959 | 0.07782 | -0.20142 | -0.28839 | -0.32043 | -0.34332 | 0.027466 | 0.12817 | 61.0107 | 61.0474 | 122.6669 | 123.0652 | -0.20142 | 123.0148 | 60.9283 | -0.34332 | 123.0652 | -0.20142 | 60.9283 | 122.6669 | 123.0148 | -123.317 | -123.3307
1934.7812 | 123.0698 | -60.9146 | 62.0499 | 0.11803 | -0.0043708 | -0.0085663 | 0.0051974 | 0.061814 | -0.0045821 | 0.06442 | -61.0382 | 62.1826 | -61.203 | -61.1801 | 61.7432 | -0.059509 | 0.009155 | 0.068665 | 62.1323 | -61.2442 | -0.28839 | 0.13275 | -0.1236 | -0.2655 | -0.3067 | -0.32959 | 0.082397 | 0.1648 | 60.9238 | 60.9833 | 122.6578 | 123.0972 | -0.1236 | 123.0469 | 60.8551 | -0.32959 | 123.0972 | -0.1236 | 60.8551 | 122.6578 | 123.0469 | -123.2529 | -123.2941
1935.7656 | 123.1338 | -60.8871 | 62.0819 | -0.12611 | -0.0041572 | -0.010703 | 0.00071144 | 0.061387 | -0.0052231 | 0.068479 | -61.0245 | 62.1826 | -61.1984 | -61.1298 | 61.821 | 0.050354 | 0.10529 | 0.18768 | 62.1506 | -61.2076 | -0.31128 | 0.10071 | -0.13733 | -0.24262 | -0.26093 | -0.32043 | 0.068665 | 0.17395 | 60.9924 | 61.0748 | 122.7081 | 123.0698 | -0.13733 | 123.0377 | 60.9375 | -0.32043 | 123.0698 | -0.13733 | 60.9375 | 122.7081 | 123.0377 | -123.2803 | -123.2895
1936.7656 | 123.0972 | -60.9238 | 62.0773 | -0.18715 | -0.007575 | -0.011984 | 7.0444e-05 | 0.059678 | -0.0062911 | 0.066556 | -61.0565 | 62.2101 | -61.1938 | -61.2717 | 61.702 | -0.009155 | 0.13275 | 0.14191 | 62.146 | -61.1938 | -0.27008 | 0.13275 | -0.13275 | -0.3479 | -0.37537 | -0.27008 | 0.068664 | 0.13733 | 61.0565 | 61.0657 | 122.6257 | 123.1338 | -0.13275 | 123.0698 | 60.9146 | -0.27008 | 123.1338 | -0.13275 | 60.9146 | 122.6257 | 123.0698 | -123.2712 | -123.2712
1937.7656 | 123.1018 | -60.8917 | 62.059 | -0.149 | -0.006507 | -0.0066437 | 0.001993 | 0.062241 | -0.0069321 | 0.065916 | -61.0428 | 62.1918 | -61.1938 | -61.1481 | 61.7889 | 0.032043 | 0.11902 | 0.18768 | 62.1185 | -61.2396 | -0.30212 | 0.13275 | -0.15106 | -0.25635 | -0.27008 | -0.3479 | 0.059509 | 0.15106 | 61.0107 | 61.0794 | 122.6807 | 123.0835 | -0.15106 | 123.0103 | 60.9238 | -0.3479 | 123.0835 | -0.15106 | 60.9238 | 122.6807 | 123.0103 | -123.2529 | -123.2986
1938.7656 | 123.0927 | -60.9238 | 62.1094 | -0.17952 | -0.005866 | -0.0098479 | -0.00014316 | 0.062028 | -0.0056503 | 0.068052 | -61.0611 | 62.1597 | -61.1984 | -61.1664 | 61.7981 | 0.036621 | 0.14648 | 0.18768 | 62.1506 | -61.1847 | -0.27466 | 0.050354 | -0.13733 | -0.24262 | -0.31128 | -0.26093 | 0.041199 | 0.13733 | 61.0703 | 61.1114 | 122.7219 | 123.0835 | -0.13733 | 123.0743 | 60.9604 | -0.26093 | 123.0835 | -0.13733 | 60.9604 | 122.7219 | 123.0743 | -123.3078 | -123.2941
1939.7812 | 123.2071 | -60.8963 | 61.9995 | 0.25536 | -0.0069342 | -0.0062163 | -0.00099756 | 0.060105 | -0.0015915 | 0.065702 | -61.0565 | 62.0682 | -61.2167 | -61.0977 | 61.8713 | 0.041199 | -0.16937 | 0.17395 | 62.0682 | -61.2122 | -0.32043 | 0.068664 | -0.16022 | -0.20142 | -0.12817 | -0.31586 | 0.068664 | 0.16022 | 60.7269 | 61.0703 | 122.7676 | 122.9645 | -0.16022 | 122.9645 | 60.9375 | -0.31586 | 122.9645 | -0.16022 | 60.9375 | 122.7676 | 122.9645 | -123.2162 | -123.2117
1940.7656 | 123.0972 | -60.9009 | 62.0819 | -0.46944 | -0.006507 | -0.0077117 | 0.0032748 | 0.059037 | -0.0043685 | 0.067197 | -61.0062 | 62.1689 | -61.1984 | -61.1618 | 61.7981 | 0.059509 | 0.13275 | 0.18768 | 62.1277 | -61.2259 | -0.29755 | 0.086975 | -0.10529 | -0.26092 | -0.28381 | -0.32501 | 0.045777 | 0.19226 | 61.0336 | 61.0886 | 122.699 | 123.0698 | -0.10529 | 123.0286 | 60.9604 | -0.32501 | 123.0698 | -0.10529 | 60.9604 | 122.699 | 123.0286 | -123.2803 | -123.3078
1941.7656 | 123.1384 | -60.9146 | 62.0544 | -0.12611 | -0.0069342 | -0.011771 | 0.0034884 | 0.062241 | -0.0043685 | 0.067411 | -61.0382 | 62.1689 | -61.2076 | -61.116 | 61.8164 | 0.045776 | 0.10986 | 0.19226 | 62.1002 | -61.2259 | -0.29297 | 0.11444 | -0.1236 | -0.20142 | -0.23804 | -0.31128 | 0.045777 | 0.16937 | 61.0245 | 61.1069 | 122.731 | 123.0835 | -0.1236 | 123.0148 | 60.9604 | -0.31128 | 123.0835 | -0.1236 | 60.9604 | 122.731 | 123.0148 | -123.262 | -123.2803
1942.7656 | 123.1018 | -60.9146 | 62.0865 | -0.19478 | -0.0067206 | -0.0083527 | 0.0011386 | 0.059678 | -0.0037277 | 0.066343 | -61.0611 | 62.1918 | -61.235 | -61.2625 | 61.6928 | -0.004578 | 0.1236 | 0.13275 | 62.1414 | -61.1801 | -0.32043 | 0.10529 | -0.14648 | -0.3479 | -0.39368 | -0.2655 | 0.054931 | 0.17395 | 61.0382 | 61.0474 | 122.6074 | 123.1064 | -0.14648 | 123.056 | 60.91 | -0.2655 | 123.1064 | -0.14648 | 60.91 | 122.6074 | 123.056 | -123.3215 | -123.2666
1943.7656 | 123.1338 | -60.8917 | 62.0728 | -0.16426 | -0.0037298 | -0.0085663 | 0.004343 | 0.061387 | -0.0054367 | 0.065702 | -61.0382 | 62.1872 | -61.203 | -61.1343 | 61.8027 | 0.045776 | 0.11902 | 0.1831 | 62.1277 | -61.2167 | -0.31128 | 0.11444 | -0.14648 | -0.24261 | -0.27008 | -0.32501 | 0.054932 | 0.1648 | 61.0107 | 61.0748 | 122.6944 | 123.0789 | -0.14648 | 123.0194 | 60.9375 | -0.32501 | 123.0789 | -0.14648 | 60.9375 | 122.6944 | 123.0194 | -123.2758 | -123.2895
1944.7656 | 123.2071 | -60.8963 | 61.9812 | 0.27824 | -0.0071478 | -0.0083527 | 0.0013522 | 0.062028 | -0.0026595 | 0.068052 | -61.0199 | 62.1185 | -61.1984 | -61.1618 | 61.8073 | 0.013733 | -0.16937 | 0.13275 | 62.059 | -61.1755 | -0.30212 | 0.13733 | -0.1236 | -0.2655 | -0.17395 | -0.27924 | 0.07782 | 0.17853 | 60.7269 | 61.0291 | 122.7036 | 123.0148 | -0.1236 | 122.9553 | 60.91 | -0.27924 | 123.0148 | -0.1236 | 60.91 | 122.7036 | 122.9553 | -123.1796 | -123.1567
1945.7656 | 123.1201 | -60.9055 | 62.0865 | -0.057449 | -0.0073614 | -0.011343 | 0.0015658 | 0.059464 | -0.0041549 | 0.067838 | -61.0291 | 62.1689 | -61.1984 | -61.1481 | 61.7981 | 0.041199 | 0.12817 | 0.16479 | 62.1323 | -61.2442 | -0.29297 | 0.082397 | -0.1236 | -0.24261 | -0.28839 | -0.33875 | 0.045776 | 0.16937 | 61.0336 | 61.0703 | 122.7036 | 123.0743 | -0.1236 | 123.0377 | 60.9467 | -0.33875 | 123.0743 | -0.1236 | 60.9467 | 122.7036 | 123.0377 | -123.2849 | -123.3307
1946.7656 | 123.143 | -60.9055 | 62.0499 | -0.15663 | -0.0080024 | -0.010275 | 0.00049764 | 0.060532 | -0.0039413 | 0.065702 | -61.0016 | 62.114 | -61.1938 | -61.0931 | 61.8668 | 0.10529 | 0.050354 | 0.25177 | 62.1185 | -61.1572 | -0.28839 | 0.064087 | -0.09613 | -0.18768 | -0.18311 | -0.25177 | 0.068664 | 0.19226 | 60.9558 | 61.1572 | 122.7722 | 123.0194 | -0.09613 | 123.024 | 61.0107 | -0.25177 | 123.0194 | -0.09613 | 61.0107 | 122.7722 | 123.024 | -123.2437 | -123.2071
1947.7656 | 123.1018 | -60.8871 | 62.0728 | -0.91957 | -0.005866 | -0.0079253 | 0.0022066 | 0.060746 | -0.0039413 | 0.06442 | -61.1252 | 62.2147 | -61.1984 | -61.171 | 61.7935 | 0.041199 | 0.13733 | 0.17853 | 62.1323 | -61.2213 | -0.31128 | 0.14191 | -0.23804 | -0.28381 | -0.27924 | -0.33417 | 0.059509 | 0.073242 | 61.0245 | 61.0657 | 122.6807 | 123.1018 | -0.23804 | 123.0194 | 60.9283 | -0.33417 | 123.1018 | -0.23804 | 60.9283 | 122.6807 | 123.0194 | -123.2712 | -123.2941
1948.7656 | 123.111 | -60.8963 | 62.0773 | -0.18715 | -0.0060798 | -0.011343 | 0.0045566 | 0.064378 | -0.0041549 | 0.06677 | -61.0428 | 62.1643 | -61.203 | -61.1664 | 61.7615 | 0.018311 | 0.11902 | 0.17395 | 62.1323 | -61.2122 | -0.3067 | 0.086975 | -0.14648 | -0.27008 | -0.31586 | -0.31586 | 0.054931 | 0.16022 | 61.0153 | 61.0703 | 122.6578 | 123.0606 | -0.14648 | 123.0286 | 60.9146 | -0.31586 | 123.0606 | -0.14648 | 60.9146 | 122.6578 | 123.0286 | -123.2803 | -123.2895
1949.7656 | 123.1338 | -60.8734 | 62.0499 | -0.12611 | -0.0052252 | -0.0072845 | 0.0051974 | 0.062241 | -0.0037277 | 0.066984 | -61.0291 | 62.1872 | -61.1984 | -61.1298 | 61.8164 | 0.045776 | 0.11902 | 0.17853 | 62.1506 | -61.235 | -0.32501 | 0.13733 | -0.15564 | -0.25635 | -0.23346 | -0.36163 | 0.10071 | 0.16937 | 60.9924 | 61.0519 | 122.6898 | 123.0606 | -0.15564 | 123.024 | 60.9192 | -0.36163 | 123.0606 | -0.15564 | 60.9192 | 122.6898 | 123.024 | -123.2483 | -123.2849
1950.7656 | 123.0927 | -60.9329 | 62.0499 | -0.20241 | -0.0067206 | -0.011343 | 0.0028476 | 0.061387 | -0.0056503 | 0.068693 | -61.0565 | 62.1597 | -61.2259 | -61.1664 | 61.7935 | 0.059509 | 0.37079 | 0.09613 | 62.178 | -61.1984 | -0.29297 | 0.10986 | -0.1236 | -0.23346 | -0.25635 | -0.2655 | 0.12817 | 0.16937 | 61.3037 | 61.0291 | 122.7264 | 123.0927 | -0.1236 | 123.111 | 60.9924 | -0.2655 | 123.0927 | -0.1236 | 60.9924 | 122.7264 | 123.111 | -123.2758 | -123.2483
1951.7656 | 123.1201 | -60.91 | 62.0728 | -0.11848 | -0.0045844 | -0.0064301 | 0.0047702 | 0.060319 | -0.0045821 | 0.067838 | -61.0474 | 62.2009 | -61.1801 | -61.1343 | 61.7935 | 0.045776 | 0.11444 | 0.1831 | 62.114 | -61.2213 | -0.27008 | 0.12817 | -0.13733 | -0.2243 | -0.27924 | -0.31128 | 0.041199 | 0.13275 | 61.0245 | 61.0931 | 122.7036 | 123.111 | -0.13733 | 123.024 | 60.9558 | -0.31128 | 123.111 | -0.13733 | 60.9558 | 122.7036 | 123.024 | -123.2529 | -123.2941
1952.7656 | 123.1155 | -60.9009 | 62.0773 | -0.15663 | -0.003089 | -0.0079253 | 0.0034884 | 0.0616 | -0.0060775 | 0.068052 | -61.0428 | 62.1872 | -61.2259 | -61.1435 | 61.8118 | 0.050354 | 0.13275 | 0.16937 | 62.1368 | -61.2167 | -0.32501 | 0.10986 | -0.14191 | -0.24261 | -0.2655 | -0.31586 | 0.059509 | 0.1831 | 61.0336 | 61.0703 | 122.7127 | 123.0881 | -0.14191 | 123.0377 | 60.9512 | -0.31586 | 123.0881 | -0.14191 | 60.9512 | 122.7127 | 123.0377 | -123.3032 | -123.2941
1953.7656 | 123.1293 | -60.9009 | 62.0819 | -0.21767 | -0.0037298 | -0.011984 | -0.00035676 | 0.06096 | -0.0041549 | 0.067624 | -61.0565 | 62.1735 | -61.1801 | -61.1572 | 61.821 | 0.045776 | 0.15106 | 0.17395 | 62.1368 | -61.203 | -0.27924 | 0.091553 | -0.15564 | -0.25635 | -0.26093 | -0.30212 | 0.054932 | 0.1236 | 61.0519 | 61.0748 | 122.7219 | 123.0743 | -0.15564 | 123.0377 | 60.9467 | -0.30212 | 123.0743 | -0.15564 | 60.9467 | 122.7219 | 123.0377 | -123.262 | -123.2849
1954.7656 | 123.1064 | -60.9055 | 62.0728 | -0.080337 | -0.0052252 | -0.0072845 | 0.001993 | 0.060532 | -0.0028731 | 0.067411 | -61.0474 | 62.1597 | -61.2076 | -61.1481 | 61.7844 | 0.059509 | 0.12817 | 0.16479 | 62.1414 | -61.2076 | -0.30212 | 0.086975 | -0.14191 | -0.24261 | -0.28839 | -0.30212 | 0.068664 | 0.16022 | 61.0336 | 61.0703 | 122.6898 | 123.0652 | -0.14191 | 123.0469 | 60.965 | -0.30212 | 123.0652 | -0.14191 | 60.965 | 122.6898 | 123.0469 | -123.2803 | -123.2803
1955.7656 | 123.1293 | -60.9009 | 62.0682 | -0.149 | -0.0037298 | -0.0085663 | 0.0030612 | 0.06395 | -0.0056503 | 0.068906 | -61.0199 | 62.1964 | -61.1938 | -61.1206 | 61.8256 | 0.059509 | 0.10071 | 0.18768 | 62.114 | -61.1984 | -0.29297 | 0.12817 | -0.11902 | -0.21973 | -0.24261 | -0.29755 | 0.045777 | 0.17395 | 61.0016 | 61.0886 | 122.7264 | 123.0972 | -0.11902 | 123.0148 | 60.9604 | -0.29755 | 123.0972 | -0.11902 | 60.9604 | 122.7264 | 123.0148 | -123.262 | -123.2666
1956.7656 | 123.1247 | -60.91 | 62.0773 | -0.17189 | -0.0056524 | -0.0089935 | 0.0028476 | 0.062882 | -0.0050095 | 0.06912 | -61.0245 | 62.1735 | -61.1893 | -61.1389 | 61.8118 | 0.036621 | 0.11902 | 0.17853 | 62.1552 | -61.1893 | -0.27924 | 0.09613 | -0.11444 | -0.22888 | -0.2655 | -0.27924 | 0.077819 | 0.16479 | 61.0291 | 61.0886 | 122.7219 | 123.0835 | -0.11444 | 123.0652 | 60.9467 | -0.27924 | 123.0835 | -0.11444 | 60.9467 | 122.7219 | 123.0652 | -123.2666 | -123.2666
1957.7656 | 123.1293 | -60.8917 | 62.1002 | -0.12611 | -0.0050116 | -0.0077117 | 0.0045566 | 0.062241 | -0.0041549 | 0.068479 | -61.0565 | 62.1872 | -61.2122 | -61.1389 | 61.7981 | 0.059509 | 0.11902 | 0.17853 | 62.1368 | -61.2122 | -0.32043 | 0.086975 | -0.16479 | -0.24719 | -0.30212 | -0.32043 | 0.036621 | 0.15564 | 61.0107 | 61.0703 | 122.6898 | 123.0789 | -0.16479 | 123.0286 | 60.9512 | -0.32043 | 123.0789 | -0.16479 | 60.9512 | 122.6898 | 123.0286 | -123.3124 | -123.3124
1958.7656 | 123.1247 | -60.8917 | 62.0865 | -0.19478 | -0.0039434 | -0.010062 | 0.0013522 | 0.062882 | -0.0045821 | 0.067197 | -61.0291 | 62.1918 | -61.1847 | -61.1435 | 61.8164 | 0.045776 | 0.13275 | 0.18768 | 62.1368 | -61.2076 | -0.29297 | 0.10529 | -0.13733 | -0.25177 | -0.27008 | -0.31586 | 0.050354 | 0.15564 | 61.0245 | 61.0794 | 122.7081 | 123.0835 | -0.13733 | 123.0286 | 60.9375 | -0.31586 | 123.0835 | -0.13733 | 60.9375 | 122.7081 | 123.0286 | -123.2712 | -123.2941
1959.7656 | 123.0881 | -60.91 | 62.0956 | -0.034561 | -0.0056524 | -0.0085663 | 0.0015658 | 0.059678 | -0.0037277 | 0.065488 | -61.0794 | 62.1689 | -61.235 | -61.1389 | 61.7889 | 0.027466 | 0.11902 | 0.16022 | 62.1185 | -61.1893 | -0.32501 | 0.073242 | -0.16937 | -0.22888 | -0.3067 | -0.27924 | 0.022888 | 0.15564 | 61.0291 | 61.0703 | 122.699 | 123.0789 | -0.16937 | 123.0286 | 60.9375 | -0.27924 | 123.0789 | -0.16937 | 60.9375 | 122.699 | 123.0286 | -123.3307 | -123.2849
1960.7656 | 123.1155 | -60.8917 | 62.0911 | -0.10323 | -0.005866 | -0.0089935 | -0.00057036 | 0.059464 | -0.0045821 | 0.067411 | -61.0428 | 62.1643 | -61.1984 | -61.1526 | 61.7981 | 0.068665 | 0.13275 | 0.19684 | 62.1185 | -61.2167 | -0.3067 | 0.073243 | -0.15106 | -0.26092 | -0.29297 | -0.32501 | 0.027466 | 0.15564 | 61.0245 | 61.0886 | 122.6898 | 123.056 | -0.15106 | 123.0103 | 60.9604 | -0.32501 | 123.056 | -0.15106 | 60.9604 | 122.6898 | 123.0103 | -123.2895 | -123.3078
1961.7656 | 123.1338 | -60.91 | 62.0544 | -0.11085 | -0.003089 | -0.0064301 | 0.0041292 | 0.062669 | -0.0039413 | 0.065702 | -61.0382 | 62.1689 | -61.1847 | -61.1481 | 61.8118 | 0.045776 | 0.1236 | 0.19684 | 62.146 | -61.2076 | -0.27466 | 0.11444 | -0.12817 | -0.23804 | -0.24261 | -0.29755 | 0.091553 | 0.14648 | 61.0336 | 61.1069 | 122.7219 | 123.0789 | -0.12817 | 123.056 | 60.9558 | -0.29755 | 123.0789 | -0.12817 | 60.9558 | 122.7219 | 123.056 | -123.2391 | -123.262
1962.7656 | 123.1155 | -60.8963 | 62.059 | -0.065079 | -0.0043708 | -0.0085663 | 0.001993 | 0.061387 | -0.0067185 | 0.06677 | -61.0519 | 62.1826 | -61.2122 | -61.1664 | 61.8027 | 0.032043 | 0.13733 | 0.17395 | 62.1368 | -61.1801 | -0.31586 | 0.1236 | -0.15564 | -0.27008 | -0.25635 | -0.28381 | 0.07782 | 0.16022 | 61.0336 | 61.0703 | 122.699 | 123.0789 | -0.15564 | 123.0331 | 60.9283 | -0.28381 | 123.0789 | -0.15564 | 60.9283 | 122.699 | 123.0331 | -123.2712 | -123.2391
1963.7656 | 123.1201 | -60.91 | 62.0819 | -0.149 | -0.004798 | -0.011343 | 0.0013522 | 0.062669 | -0.0052231 | 0.069333 | -61.0519 | 62.1643 | -61.1984 | -61.1893 | 61.7844 | 0.041199 | 0.10986 | 0.16022 | 62.1368 | -61.2167 | -0.28839 | 0.082398 | -0.14191 | -0.27924 | -0.29755 | -0.3067 | 0.054932 | 0.14648 | 61.0199 | 61.0703 | 122.6944 | 123.0743 | -0.14191 | 123.0469 | 60.9512 | -0.3067 | 123.0743 | -0.14191 | 60.9512 | 122.6944 | 123.0469 | -123.2803 | -123.2986
1964.7656 | 123.0743 | -60.878 | 62.0865 | -0.16426 | -0.0050116 | -0.01113 | 0.00092504 | 0.062455 | -0.0052231 | 0.066343 | -61.0657 | 62.1689 | -61.1938 | -61.1481 | 61.8027 | 0.059509 | 0.13733 | 0.17853 | 62.1414 | -61.1893 | -0.31586 | 0.082397 | -0.18768 | -0.27008 | -0.28381 | -0.31128 | 0.054931 | 0.12817 | 61.0153 | 61.0565 | 122.6807 | 123.0469 | -0.18768 | 123.0194 | 60.9375 | -0.31128 | 123.0469 | -0.18768 | 60.9375 | 122.6807 | 123.0194 | -123.2803 | -123.2758
1965.7656 | 123.0972 | -60.8963 | 62.0819 | -0.28633 | -0.008216 | -0.010062 | -0.00057036 | 0.061814 | -0.0052231 | 0.068265 | -61.0336 | 62.1689 | -61.1893 | -61.1526 | 61.821 | 0.054932 | 0.13733 | 0.18768 | 62.1506 | -61.1801 | -0.29297 | 0.086975 | -0.13733 | -0.25635 | -0.26093 | -0.28381 | 0.068665 | 0.15564 | 61.0336 | 61.084 | 122.7173 | 123.0652 | -0.13733 | 123.0469 | 60.9512 | -0.28381 | 123.0652 | -0.13733 | 60.9512 | 122.7173 | 123.0469 | -123.2712 | -123.262
1966.7656 | 123.2208 | -60.8963 | 62.0453 | -0.14137 | -0.008216 | -0.0085663 | -0.00099756 | 0.059891 | -0.0043685 | 0.067197 | -60.9741 | 62.1185 | -61.1847 | -61.0611 | 61.8896 | 0.12817 | -0.013733 | 0.28839 | 62.0865 | -61.1526 | -0.28839 | 0.073242 | -0.07782 | -0.16479 | -0.15564 | -0.25635 | 0.041199 | 0.21057 | 60.8826 | 61.1847 | 122.7859 | 123.0148 | -0.07782 | 122.9828 | 61.0245 | -0.25635 | 123.0148 | -0.07782 | 61.0245 | 122.7859 | 122.9828 | -123.23 | -123.1979
1967.7656 | 123.175 | -60.8871 | 62.0544 | -0.20241 | -0.0077888 | -0.0079253 | 0.00028404 | 0.0616 | -0.0062911 | 0.06677 | -60.9879 | 62.114 | -61.1664 | -61.0794 | 61.8484 | 0.10986 | 0.045776 | 0.2655 | 62.1048 | -61.1618 | -0.27924 | 0.05951 | -0.10071 | -0.19226 | -0.20599 | -0.27466 | 0.050354 | 0.17853 | 60.9329 | 61.1526 | 122.7356 | 123.0011 | -0.10071 | 122.9919 | 60.997 | -0.27466 | 123.0011 | -0.10071 | 60.997 | 122.7356 | 122.9919 | -123.2208 | -123.2162
1968.7656 | 123.1064 | -60.8826 | 62.0728 | -0.18715 | -0.0056524 | -0.010275 | 0.0013522 | 0.059891 | -0.0062911 | 0.066129 | -61.0245 | 62.1048 | -61.1893 | -61.1481 | 61.7844 | 0.064087 | 0.16479 | 0.19226 | 62.1277 | -61.1755 | -0.3067 | 0.032043 | -0.14191 | -0.2655 | -0.28839 | -0.29297 | 0.054932 | 0.16479 | 61.0474 | 61.0748 | 122.6669 | 122.9874 | -0.14191 | 123.0103 | 60.9467 | -0.29297 | 122.9874 | -0.14191 | 60.9467 | 122.6669 | 123.0103 | -123.262 | -123.2483
1969.7656 | 123.1293 | -60.8734 | 62.0728 | -0.18715 | -0.007575 | -0.011984 | 0.003702 | 0.059678 | -0.0047957 | 0.064847 | -60.997 | 62.0819 | -61.1847 | -61.1023 | 61.8668 | 0.10071 | 0.054932 | 0.2655 | 62.1048 | -61.1572 | -0.31128 | 0.009155 | -0.1236 | -0.22888 | -0.20599 | -0.28381 | 0.032043 | 0.18768 | 60.9283 | 61.1389 | 122.7402 | 122.9553 | -0.1236 | 122.9782 | 60.9741 | -0.28381 | 122.9553 | -0.1236 | 60.9741 | 122.7402 | 122.9782 | -123.2574 | -123.23
1970.7656 | 123.2071 | -60.878 | 62.0453 | -0.11848 | -0.008216 | -0.011343 | -0.00078396 | 0.059464 | -0.0054367 | 0.067411 | -60.9787 | 62.0865 | -61.1755 | -61.0565 | 61.8805 | 0.13733 | -0.004578 | 0.27924 | 62.1002 | -61.1343 | -0.29755 | 0.041199 | -0.10071 | -0.17853 | -0.16479 | -0.25635 | 0.054932 | 0.19684 | 60.8734 | 61.1572 | 122.7585 | 122.9645 | -0.10071 | 122.9782 | 61.0153 | -0.25635 | 122.9645 | -0.10071 | 61.0153 | 122.7585 | 122.9782 | -123.2208 | -123.1796
1971.7656 | 123.2025 | -60.8643 | 62.0178 | 0.52238 | -0.0080024 | -0.012198 | 0.00028404 | 0.059251 | -0.0056503 | 0.067197 | -60.9695 | 62.0773 | -61.1938 | -61.0474 | 61.8942 | 0.13275 | -0.022888 | 0.27466 | 62.0911 | -61.1481 | -0.32959 | 0.05951 | -0.10529 | -0.1831 | -0.1236 | -0.28381 | 0.073242 | 0.22431 | 60.8414 | 61.1389 | 122.7585 | 122.9416 | -0.10529 | 122.9553 | 60.997 | -0.28381 | 122.9416 | -0.10529 | 60.997 | 122.7585 | 122.9553 | -123.2117 | -123.1659
1972.7656 | 123.1934 | -60.878 | 62.0361 | -0.15663 | -0.0090704 | -0.011557 | -0.00057036 | 0.058396 | -0.0065047 | 0.067197 | -60.9695 | 62.0865 | -61.1847 | -61.0565 | 61.9492 | 0.37079 | -0.073242 | 0.091553 | 62.1048 | -61.1206 | -0.3067 | 0.050354 | -0.091552 | -0.17853 | -0.086975 | -0.24261 | 0.068664 | 0.21515 | 60.8047 | 60.9695 | 122.8271 | 122.9645 | -0.091552 | 122.9828 | 61.2488 | -0.24261 | 122.9645 | -0.091552 | 61.2488 | 122.8271 | 122.9828 | -123.2208 | -123.1567
1973.7656 | 123.2117 | -60.8643 | 62.0544 | 0.011215 | -0.0084296 | -0.0083527 | -0.00099756 | 0.057969 | -0.0028731 | 0.066556 | -61.0062 | 62.0773 | -61.203 | -61.0794 | 61.8576 | 0.09613 | -0.073242 | 0.25177 | 62.0453 | -61.1435 | -0.33875 | 0.022889 | -0.14191 | -0.21515 | -0.19684 | -0.27924 | -0.009155 | 0.19684 | 60.791 | 61.116 | 122.7219 | 122.9416 | -0.14191 | 122.9095 | 60.9604 | -0.27924 | 122.9416 | -0.14191 | 60.9604 | 122.7219 | 122.9095 | -123.2574 | -123.1979
1974.7656 | 123.262 | -60.8917 | 62.0178 | -0.04219 | -0.0094976 | -0.013693 | -0.00014316 | 0.056901 | -0.0047957 | 0.067838 | -61.0062 | 62.059 | -61.1801 | -61.0703 | 61.8942 | 0.13733 | -0.086975 | 0.30212 | 62.0682 | -61.1481 | -0.28839 | 0.041199 | -0.11444 | -0.17853 | -0.1236 | -0.25635 | 0.050354 | 0.17395 | 60.8047 | 61.1938 | 122.786 | 122.9507 | -0.11444 | 122.9599 | 61.0291 | -0.25635 | 122.9507 | -0.11444 | 61.0291 | 122.786 | 122.9599 | -123.1979 | -123.1659
1975.7656 | 123.2574 | -60.8551 | 62.0544 | -0.11848 | -0.0084296 | -0.0098479 | -0.00057036 | 0.060105 | -0.0062911 | 0.065916 | -60.965 | 62.0499 | -61.1526 | -61.0199 | 61.9125 | 0.13275 | -0.054932 | 0.29755 | 62.0956 | -61.1298 | -0.29755 | -0.004577 | -0.10986 | -0.16479 | -0.14191 | -0.27466 | 0.041199 | 0.18768 | 60.8002 | 61.1526 | 122.7676 | 122.905 | -0.10986 | 122.9507 | 60.9879 | -0.27466 | 122.905 | -0.10986 | 60.9879 | 122.7676 | 122.9507 | -123.2071 | -123.1842
1976.7656 | 123.2346 | -60.8551 | 62.027 | -0.034561 | -0.008216 | -0.014334 | 0.00049764 | 0.057969 | -0.0033005 | 0.066556 | -60.9879 | 62.0453 | -61.1481 | -61.0336 | 61.908 | 0.11902 | -0.10529 | 0.29297 | 62.059 | -61.1252 | -0.29297 | 0.01831 | -0.13275 | -0.17853 | -0.11902 | -0.27008 | 0.032043 | 0.16022 | 60.7498 | 61.1481 | 122.7631 | 122.9004 | -0.13275 | 122.9141 | 60.9741 | -0.27008 | 122.9004 | -0.13275 | 60.9741 | 122.7631 | 122.9141 | -123.175 | -123.1522
1977.7656 | 123.1979 | -60.878 | 62.0361 | -0.04219 | -0.0097114 | -0.011557 | 0.00071144 | 0.057969 | -0.0062911 | 0.068479 | -61.0245 | 62.0728 | -61.1572 | -61.0519 | 61.8759 | 0.09613 | -0.091553 | 0.24261 | 62.0453 | -61.1435 | -0.27924 | 0.036621 | -0.14648 | -0.17395 | -0.16022 | -0.2655 | 0.009155 | 0.13275 | 60.7864 | 61.1206 | 122.7539 | 122.9507 | -0.14648 | 122.9233 | 60.9741 | -0.2655 | 122.9507 | -0.14648 | 60.9741 | 122.7539 | 122.9233 | -123.1934 | -123.1796
1978.7656 | 123.2391 | -60.8871 | 62.0544 | -0.019302 | -0.0094976 | -0.013052 | 0.00049764 | 0.058396 | -0.0043685 | 0.068265 | -61.0291 | 62.0453 | -61.171 | -61.0794 | 61.8484 | 0.059509 | -0.073242 | 0.23804 | 62.0361 | -61.1526 | -0.28381 | -0.009155 | -0.14191 | -0.19226 | -0.20599 | -0.2655 | -0.01831 | 0.14191 | 60.8139 | 61.1252 | 122.7356 | 122.9324 | -0.14191 | 122.9233 | 60.9467 | -0.2655 | 122.9324 | -0.14191 | 60.9467 | 122.7356 | 122.9233 | -123.2254 | -123.2071
1979.7656 | 123.1888 | -60.8826 | 62.0316 | 0.056992 | -0.0069342 | -0.011984 | 7.0444e-05 | 0.05861 | -0.0054367 | 0.068693 | -61.0474 | 62.0499 | -61.1984 | -61.116 | 61.8347 | 0.045776 | -0.07782 | 0.18768 | 62.0499 | -61.1664 | -0.31586 | 0.018311 | -0.16479 | -0.23346 | -0.19684 | -0.28381 | 0.018311 | 0.15106 | 60.8047 | 61.0703 | 122.7173 | 122.9324 | -0.16479 | 122.9324 | 60.9283 | -0.28381 | 122.9324 | -0.16479 | 60.9283 | 122.7173 | 122.9324 | -123.23 | -123.1979
1980.7656 | 123.1705 | -60.8734 | 62.0407 | 0.14854 | -0.0069342 | -0.011984 | 0.0013522 | 0.056901 | -0.0062911 | 0.067838 | -61.0519 | 62.0407 | -61.1938 | -61.1069 | 61.8164 | 0.013733 | -0.11902 | 0.1236 | 62.0361 | -61.1389 | -0.32044 | 0 | -0.17853 | -0.23346 | -0.2243 | -0.2655 | -0.004577 | 0.14191 | 60.7544 | 60.997 | 122.6898 | 122.9141 | -0.17853 | 122.9095 | 60.8871 | -0.2655 | 122.9141 | -0.17853 | 60.8871 | 122.6898 | 122.9095 | -123.2346 | -123.1796
1981.7656 | 123.1842 | -60.8643 | 62.0407 | 0.11803 | -0.006507 | -0.011771 | -0.00014316 | 0.059891 | -0.0054367 | 0.066984 | -61.0474 | 62.0453 | -61.1801 | -61.1206 | 61.8301 | 0.009155 | -0.091553 | 0.16022 | 62.0499 | -61.1298 | -0.31586 | 0.004578 | -0.1831 | -0.25635 | -0.21057 | -0.2655 | 0.009156 | 0.13275 | 60.7727 | 61.0245 | 122.6944 | 122.9095 | -0.1831 | 122.9141 | 60.8734 | -0.2655 | 122.9095 | -0.1831 | 60.8734 | 122.6944 | 122.9141 | -123.2208 | -123.1705
1982.7656 | 123.1934 | -60.8917 | 62.0224 | -0.11085 | -0.0088568 | -0.011557 | 0.0013522 | 0.057755 | -0.0067185 | 0.067411 | -61.0336 | 62.0316 | -61.1938 | -61.1069 | 61.8484 | 0.041199 | -0.091553 | 0.17395 | 62.0773 | -61.1481 | -0.30212 | 0.009155 | -0.14191 | -0.21515 | -0.17395 | -0.25635 | 0.054932 | 0.16022 | 60.8002 | 61.0657 | 122.7402 | 122.9233 | -0.14191 | 122.9691 | 60.9329 | -0.25635 | 122.9233 | -0.14191 | 60.9329 | 122.7402 | 122.9691 | -123.2162 | -123.1705
1983.7656 | 123.1705 | -60.9146 | 62.0178 | 0.1104 | -0.0077888 | -0.01113 | -0.00099756 | 0.060105 | -0.0050095 | 0.06677 | -61.0611 | 62.0499 | -61.171 | -61.1252 | 61.821 | 0.027466 | -0.07782 | 0.1831 | 62.0499 | -61.1801 | -0.25635 | 0.032044 | -0.14648 | -0.21057 | -0.19684 | -0.2655 | 0.032044 | 0.10986 | 60.8368 | 61.0977 | 122.7356 | 122.9645 | -0.14648 | 122.9645 | 60.9421 | -0.2655 | 122.9645 | -0.14648 | 60.9421 | 122.7356 | 122.9645 | -123.1888 | -123.1979
1984.7656 | 123.2254 | -60.878 | 62.0361 | 0.095139 | -0.0073614 | -0.0087799 | 0.0030612 | 0.057542 | -0.0024459 | 0.066343 | -61.0565 | 62.0453 | -61.1984 | -61.1298 | 61.821 | 0.013733 | -0.086975 | 0.15106 | 62.0407 | -61.1618 | -0.32043 | 0.009155 | -0.17853 | -0.25177 | -0.21515 | -0.28381 | 0.004577 | 0.14191 | 60.791 | 61.0291 | 122.699 | 122.9233 | -0.17853 | 122.9187 | 60.8917 | -0.28381 | 122.9233 | -0.17853 | 60.8917 | 122.699 | 122.9187 | -123.2346 | -123.1979
1985.7656 | 123.1842 | -60.91 | 62.0316 | 0.034104 | -0.0086432 | -0.014334 | 0.00049764 | 0.059037 | -0.0028731 | 0.066984 | -61.0428 | 62.0636 | -61.203 | -61.1206 | 61.8073 | 0 | -0.10071 | 0.15106 | 62.0499 | -61.1435 | -0.29297 | 0.032044 | -0.13275 | -0.21057 | -0.2243 | -0.23346 | 0.018311 | 0.16022 | 60.8093 | 61.0611 | 122.7173 | 122.9736 | -0.13275 | 122.9599 | 60.91 | -0.23346 | 122.9736 | -0.13275 | 60.91 | 122.7173 | 122.9599 | -123.2346 | -123.175
1986.7656 | 123.1796 | -60.8963 | 61.9949 | 0.15617 | -0.006507 | -0.0094207 | 0.0017794 | 0.061814 | -0.0043685 | 0.066129 | -61.0565 | 62.0499 | -61.2122 | -61.1252 | 61.8256 | 0.013733 | -0.11902 | 0.15106 | 62.0499 | -61.1618 | -0.31586 | 0.054932 | -0.16022 | -0.22888 | -0.16937 | -0.2655 | 0.054932 | 0.15564 | 60.7773 | 61.0474 | 122.7219 | 122.9462 | -0.16022 | 122.9462 | 60.91 | -0.2655 | 122.9462 | -0.16022 | 60.91 | 122.7219 | 122.9462 | -123.2071 | -123.1567
1987.7656 | 123.2208 | -60.8688 | 61.9858 | 0.27824 | -0.0054388 | -0.011984 | 0.0041292 | 0.060532 | -0.0062911 | 0.067624 | -60.9924 | 62.0361 | -61.1847 | -61.0703 | 61.8576 | 0.032043 | -0.21057 | 0.16937 | 62.0453 | -61.171 | -0.31586 | 0.050354 | -0.1236 | -0.20142 | -0.12817 | -0.30212 | 0.059509 | 0.19226 | 60.6583 | 61.0382 | 122.7264 | 122.905 | -0.1236 | 122.9141 | 60.9009 | -0.30212 | 122.905 | -0.1236 | 60.9009 | 122.7264 | 122.9141 | -123.1705 | -123.1567
1988.7656 | 123.1934 | -60.8871 | 61.9995 | 0.2401 | -0.008216 | -0.011771 | 0.0022066 | 0.058182 | -0.0047957 | 0.066343 | -61.0245 | 62.0453 | -61.2305 | -61.1023 | 61.8301 | 0.009155 | -0.14191 | 0.14191 | 62.0224 | -61.1893 | -0.34332 | 0.045776 | -0.13733 | -0.21515 | -0.16937 | -0.30212 | 0.022888 | 0.20599 | 60.7452 | 61.0291 | 122.7173 | 122.9324 | -0.13733 | 122.9095 | 60.8963 | -0.30212 | 122.9324 | -0.13733 | 60.8963 | 122.7173 | 122.9095 | -123.23 | -123.1888
1989.7656 | 123.1613 | -60.8688 | 62.0178 | 0.17906 | -0.0080024 | -0.0077117 | 0.0011386 | 0.060319 | -0.0039413 | 0.068479 | -61.0428 | 62.0407 | -61.1847 | -61.1252 | 61.8439 | 0.022888 | -0.091553 | 0.15106 | 62.0819 | -61.1435 | -0.31586 | 0.022888 | -0.17395 | -0.25635 | -0.17395 | -0.27466 | 0.064087 | 0.14191 | 60.7773 | 61.0199 | 122.7127 | 122.9095 | -0.17395 | 122.9507 | 60.8917 | -0.27466 | 122.9095 | -0.17395 | 60.8917 | 122.7127 | 122.9507 | -123.2025 | -123.1613
1990.7656 | 123.175 | -60.9009 | 62.0132 | 0.14092 | -0.0071478 | -0.010275 | -0.00078396 | 0.057328 | -0.0058639 | 0.067411 | -61.0474 | 62.0636 | -61.1893 | -61.1206 | 61.821 | 0.032043 | -0.10529 | 0.13733 | 62.0316 | -61.171 | -0.28839 | 0.050354 | -0.14648 | -0.21973 | -0.19226 | -0.27008 | 0.01831 | 0.14191 | 60.7956 | 61.0382 | 122.7219 | 122.9645 | -0.14648 | 122.9324 | 60.9329 | -0.27008 | 122.9645 | -0.14648 | 60.9329 | 122.7219 | 122.9324 | -123.2025 | -123.1842
1991.7656 | 123.1796 | -60.8688 | 62.027 | 0.1638 | -0.0071478 | -0.010703 | -0.00035676 | 0.06096 | -0.0041549 | 0.067197 | -61.0519 | 62.0407 | -61.203 | -61.1114 | 61.8484 | 0.009155 | -0.13733 | 0.13275 | 62.0407 | -61.1435 | -0.33417 | 0.013732 | -0.18311 | -0.24262 | -0.17853 | -0.27466 | 0.013732 | 0.15106 | 60.7315 | 61.0016 | 122.7173 | 122.9095 | -0.18311 | 122.9095 | 60.878 | -0.27466 | 122.9095 | -0.18311 | 60.878 | 122.7173 | 122.9095 | -123.23 | -123.1705
1992.7656 | 123.1796 | -60.8826 | 62.0087 | 0.27824 | -0.0062934 | -0.010916 | 0.0039156 | 0.059251 | -0.0047957 | 0.067624 | -60.997 | 62.0407 | -61.1847 | -61.0703 | 61.8622 | 0.036621 | -0.19226 | 0.15106 | 62.0361 | -61.1984 | -0.30212 | 0.032043 | -0.11444 | -0.18768 | -0.14648 | -0.31586 | 0.027466 | 0.18768 | 60.6903 | 61.0336 | 122.7448 | 122.9233 | -0.11444 | 122.9187 | 60.9192 | -0.31586 | 122.9233 | -0.11444 | 60.9192 | 122.7448 | 122.9187 | -123.1934 | -123.2071
1993.7656 | 123.2025 | -60.8734 | 62.0178 | -0.034561 | -0.0077888 | -0.0055755 | 0.0045566 | 0.061173 | -0.0045821 | 0.065916 | -60.9833 | 62.0636 | -61.1847 | -61.0611 | 61.8759 | 0.054932 | -0.18768 | 0.15564 | 62.0316 | -61.1481 | -0.31128 | 0.045777 | -0.10986 | -0.18768 | -0.14191 | -0.27466 | 0.013733 | 0.20142 | 60.6857 | 61.0291 | 122.7493 | 122.937 | -0.10986 | 122.905 | 60.9283 | -0.27466 | 122.937 | -0.10986 | 60.9283 | 122.7493 | 122.905 | -123.2025 | -123.1659
1994.7656 | 123.1888 | -60.8734 | 62.0041 | -0.62965 | -0.0073614 | -0.0087799 | 0.0049838 | 0.061173 | -0.0054367 | 0.067624 | -60.9283 | 62.0453 | -61.1847 | -61.0886 | 61.8576 | 0.027466 | -0.21057 | 0.16937 | 62.0499 | -61.1618 | -0.31128 | 0.041199 | -0.054932 | -0.21515 | -0.14648 | -0.28839 | 0.045777 | 0.25635 | 60.6628 | 61.0428 | 122.731 | 122.9187 | -0.054932 | 122.9233 | 60.9009 | -0.28839 | 122.9187 | -0.054932 | 60.9009 | 122.731 | 122.9233 | -123.1888 | -123.1659
1995.7656 | 123.1979 | -60.8917 | 62.0132 | 0.25536 | -0.007575 | -0.0064301 | 0.00028404 | 0.0616 | -0.0047957 | 0.068693 | -61.0291 | 62.0361 | -61.203 | -61.0611 | 61.8896 | 0.054932 | -0.16937 | 0.16022 | 62.059 | -61.1389 | -0.31128 | 0.022888 | -0.13733 | -0.16937 | -0.1236 | -0.24719 | 0.045776 | 0.17395 | 60.7224 | 61.0519 | 122.7814 | 122.9279 | -0.13733 | 122.9507 | 60.9467 | -0.24719 | 122.9279 | -0.13733 | 60.9467 | 122.7814 | 122.9507 | -123.2162 | -123.1522
1996.7656 | 123.1796 | -60.8871 | 61.9766 | 0.25536 | -0.0067206 | -0.014121 | 0.0013522 | 0.060319 | -0.0039413 | 0.06677 | -61.0062 | 62.059 | -61.1847 | -61.1069 | 61.853 | 0.022888 | -0.17395 | 0.16022 | 62.0041 | -61.1618 | -0.29755 | 0.082397 | -0.11902 | -0.21973 | -0.1236 | -0.27466 | 0.027465 | 0.17853 | 60.7132 | 61.0474 | 122.7402 | 122.9462 | -0.11902 | 122.8912 | 60.91 | -0.27466 | 122.9462 | -0.11902 | 60.91 | 122.7402 | 122.8912 | -123.1613 | -123.1384
1997.7656 | 123.1842 | -60.878 | 61.9949 | 0.21721 | -0.0071478 | -0.0092071 | 0.0032748 | 0.061173 | -0.0062911 | 0.068265 | -60.997 | 62.0499 | -61.2076 | -61.0931 | 61.8484 | 0.045776 | -0.1831 | 0.15106 | 62.0361 | -61.1526 | -0.32959 | 0.054932 | -0.11902 | -0.21515 | -0.14648 | -0.27466 | 0.041199 | 0.21057 | 60.6949 | 61.0291 | 122.7264 | 122.9279 | -0.11902 | 122.9141 | 60.9238 | -0.27466 | 122.9279 | -0.11902 | 60.9238 | 122.7264 | 122.9141 | -123.2025 | -123.1476
1998.7656 | 123.2162 | -60.878 | 61.9949 | 0.19432 | -0.0094976 | -0.011557 | 0.0034884 | 0.060319 | -0.0050095 | 0.068479 | -60.9924 | 62.059 | -61.1755 | -61.0977 | 61.8484 | 0.041199 | -0.18768 | 0.16479 | 62.027 | -61.1801 | -0.29755 | 0.064087 | -0.11444 | -0.21973 | -0.14648 | -0.30212 | 0.032044 | 0.1831 | 60.6903 | 61.0428 | 122.7264 | 122.937 | -0.11444 | 122.905 | 60.9192 | -0.30212 | 122.937 | -0.11444 | 60.9192 | 122.7264 | 122.905 | -123.1705 | -123.175
1999.7656 | 123.2208 | -60.8917 | 62.0178 | 0.26299 | -0.0069342 | -0.011771 | 0.0030612 | 0.062882 | -0.0069321 | 0.06912 | -60.9924 | 62.0773 | -61.2167 | -61.0886 | 61.8668 | 0.045776 | -0.19226 | 0.16937 | 62.0178 | -61.1618 | -0.32501 | 0.05951 | -0.10071 | -0.19684 | -0.15106 | -0.27008 | 0 | 0.2243 | 60.6995 | 61.0611 | 122.7585 | 122.9691 | -0.10071 | 122.9095 | 60.9375 | -0.27008 | 122.9691 | -0.10071 | 60.9375 | 122.7585 | 122.9095 | -123.2346 | -123.1796
2000.7656 | 123.1888 | -60.8688 | 61.9858 | 0.20958 | -0.006507 | -0.0072845 | 0.0022066 | 0.060319 | -0.0043685 | 0.066556 | -60.9833 | 62.059 | -61.2122 | -61.0657 | 61.8668 | 0.045776 | -0.1831 | 0.17395 | 62.0316 | -61.1618 | -0.34332 | 0.073242 | -0.11444 | -0.19684 | -0.11902 | -0.29297 | 0.045776 | 0.22888 | 60.6857 | 61.0428 | 122.7356 | 122.9279 | -0.11444 | 122.9004 | 60.9146 | -0.29297 | 122.9279 | -0.11444 | 60.9146 | 122.7356 | 122.9004 | -123.1979 | -123.1476
2001.7656 | 123.2346 | -60.8871 | 61.9904 | 0.56816 | -0.0035162 | -0.0068573 | 0.0045566 | 0.062455 | -0.0073593 | 0.066556 | -60.9695 | 62.0773 | -61.2259 | -61.084 | 61.8439 | 0.036621 | -0.18768 | 0.16022 | 62.0407 | -61.1893 | -0.33874 | 0.086976 | -0.082397 | -0.19684 | -0.14648 | -0.30212 | 0.050354 | 0.25635 | 60.6995 | 61.0474 | 122.731 | 122.9645 | -0.082397 | 122.9279 | 60.9238 | -0.30212 | 122.9645 | -0.082397 | 60.9238 | 122.731 | 122.9279 | -123.2162 | -123.1796
2002.7656 | 123.2483 | -60.8917 | 62.0132 | 0.22484 | -0.0073614 | -0.010489 | 0.0032748 | 0.060746 | -0.0039413 | 0.068693 | -61.0291 | 62.0178 | -61.2076 | -61.0794 | 61.8805 | 0.054932 | -0.20142 | 0.14648 | 62.0316 | -61.1664 | -0.31586 | 0.004577 | -0.13733 | -0.18768 | -0.13275 | -0.27466 | 0.01831 | 0.17853 | 60.6903 | 61.0382 | 122.7722 | 122.9095 | -0.13733 | 122.9233 | 60.9467 | -0.27466 | 122.9095 | -0.13733 | 60.9467 | 122.7722 | 122.9233 | -123.2208 | -123.1796
2003.7656 | 123.1934 | -60.878 | 62.0224 | 0.18669 | -0.0086432 | -0.010916 | 0.00028404 | 0.062669 | -0.0065047 | 0.06912 | -61.0016 | 62.0544 | -61.1893 | -61.1114 | 61.8393 | 0.036621 | -0.16479 | 0.16022 | 62.0224 | -61.1572 | -0.31128 | 0.032043 | -0.1236 | -0.23346 | -0.18311 | -0.27924 | 0 | 0.18768 | 60.7132 | 61.0382 | 122.7173 | 122.9324 | -0.1236 | 122.9004 | 60.9146 | -0.27924 | 122.9324 | -0.1236 | 60.9146 | 122.7173 | 122.9004 | -123.2117 | -123.1796
2004.7656 | 123.175 | -60.8871 | 62.0361 | 0.14092 | -0.0071478 | -0.0096343 | 0.00092504 | 0.058396 | -0.0043685 | 0.06912 | -61.0519 | 62.0499 | -61.2076 | -61.1481 | 61.8164 | 0.032043 | -0.082397 | 0.15564 | 62.0407 | -61.1618 | -0.32043 | 0.013733 | -0.16479 | -0.26093 | -0.21973 | -0.27466 | 0.004577 | 0.15564 | 60.8047 | 61.0428 | 122.7036 | 122.937 | -0.16479 | 122.9279 | 60.9192 | -0.27466 | 122.937 | -0.16479 | 60.9192 | 122.7036 | 122.9279 | -123.2437 | -123.1979
2005.7656 | 123.2117 | -60.8963 | 62.0178 | 0.20958 | -0.0056524 | -0.010275 | 0.0015658 | 0.060105 | -0.0043685 | 0.066556 | -61.0062 | 62.0636 | -61.171 | -61.0931 | 61.853 | 0.036621 | -0.17395 | 0.14648 | 62.0316 | -61.1755 | -0.27466 | 0.045777 | -0.10986 | -0.19684 | -0.1648 | -0.27924 | 0.013733 | 0.16479 | 60.7224 | 61.0428 | 122.7493 | 122.9599 | -0.10986 | 122.9279 | 60.9329 | -0.27924 | 122.9599 | -0.10986 | 60.9329 | 122.7493 | 122.9279 | -123.1888 | -123.1934
2006.7656 | 123.1659 | -60.8688 | 62.0178 | 0.19432 | -0.0073614 | -0.011557 | -0.00035676 | 0.059891 | -0.0045821 | 0.067411 | -61.0565 | 62.0453 | -61.1664 | -61.1435 | 61.8118 | 0.004578 | -0.10529 | 0.15106 | 62.0041 | -61.1664 | -0.29755 | 0.027466 | -0.18768 | -0.27466 | -0.20599 | -0.29755 | -0.013733 | 0.10986 | 60.7635 | 61.0199 | 122.6807 | 122.9141 | -0.18768 | 122.8729 | 60.8734 | -0.29755 | 122.9141 | -0.18768 | 60.8734 | 122.6807 | 122.8729 | -123.1842 | -123.1842
2007.7656 | 123.1979 | -60.8734 | 62.0041 | 0.19432 | -0.006507 | -0.0098479 | 0.0034884 | 0.06096 | -0.0069321 | 0.067411 | -60.9833 | 62.059 | -61.203 | -61.0886 | 61.853 | 0.027466 | -0.1831 | 0.17395 | 62.027 | -61.1343 | -0.32959 | 0.054932 | -0.10986 | -0.21515 | -0.15106 | -0.26093 | 0.022889 | 0.21973 | 60.6903 | 61.0474 | 122.7264 | 122.9324 | -0.10986 | 122.9004 | 60.9009 | -0.26093 | 122.9324 | -0.10986 | 60.9009 | 122.7264 | 122.9004 | -123.2071 | -123.1384
2008.7656 | 123.2437 | -60.8826 | 62.0132 | 0.27824 | -0.0043708 | -0.0077117 | 0.005411 | 0.062882 | -0.0041549 | 0.067838 | -60.9924 | 62.0819 | -61.1984 | -61.0794 | 61.8393 | 0.041199 | -0.19226 | 0.16022 | 62.0224 | -61.203 | -0.31586 | 0.068664 | -0.10986 | -0.19684 | -0.17395 | -0.32044 | 0.009155 | 0.20599 | 60.6903 | 61.0428 | 122.7219 | 122.9645 | -0.10986 | 122.905 | 60.9238 | -0.32044 | 122.9645 | -0.10986 | 60.9238 | 122.7219 | 122.905 | -123.2117 | -123.2162
2009.7656 | 123.1979 | -60.8459 | 62.0041 | 0.28587 | -0.007575 | -0.0094207 | 0.0032748 | 0.060105 | -0.0071457 | 0.06677 | -61.0107 | 62.0544 | -61.203 | -61.1023 | 61.8439 | 0.045776 | -0.17395 | 0.16022 | 62.027 | -61.1847 | -0.35706 | 0.050354 | -0.16479 | -0.25635 | -0.16022 | -0.33874 | 0.022889 | 0.19226 | 60.672 | 61.0062 | 122.6898 | 122.9004 | -0.16479 | 122.8729 | 60.8917 | -0.33874 | 122.9004 | -0.16479 | 60.8917 | 122.6898 | 122.8729 | -123.2071 | -123.1888
2010.7656 | 123.1659 | -60.9009 | 62.0178 | 0.17143 | -0.0062934 | -0.013052 | 7.0444e-05 | 0.05861 | -0.0052231 | 0.068052 | -61.0519 | 62.0499 | -61.1938 | -61.116 | 61.8393 | 0.013733 | -0.11444 | 0.13733 | 62.0361 | -61.1984 | -0.29297 | 0.032044 | -0.15106 | -0.21515 | -0.17853 | -0.29755 | 0.018311 | 0.14191 | 60.7864 | 61.0382 | 122.7402 | 122.9507 | -0.15106 | 122.937 | 60.9146 | -0.29755 | 122.9507 | -0.15106 | 60.9146 | 122.7402 | 122.937 | -123.2117 | -123.2162
2011.7656 | 123.175 | -60.9009 | 62.0041 | 0.18669 | -0.0080024 | -0.010275 | 0.0017794 | 0.057969 | -0.0045821 | 0.068906 | -61.0474 | 62.059 | -61.1938 | -61.1252 | 61.8256 | 0.018311 | -0.11444 | 0.15564 | 62.059 | -61.1526 | -0.29297 | 0.054932 | -0.14648 | -0.2243 | -0.17853 | -0.25177 | 0.054932 | 0.14649 | 60.7864 | 61.0565 | 122.7264 | 122.9599 | -0.14648 | 122.9599 | 60.9192 | -0.25177 | 122.9599 | -0.14648 | 60.9192 | 122.7264 | 122.9599 | -123.1979 | -123.1567
2012.7656 | 123.2208 | -60.878 | 62.0453 | 0.11803 | -0.0077888 | -0.011557 | 0.0013522 | 0.057969 | -0.0037277 | 0.067411 | -61.0611 | 62.0636 | -61.1938 | -61.1298 | 61.8256 | 0.032043 | -0.068665 | 0.16937 | 62.0453 | -61.1664 | -0.31586 | 0.018311 | -0.1831 | -0.25177 | -0.21973 | -0.28839 | 0 | 0.13275 | 60.8093 | 61.0474 | 122.7036 | 122.9416 | -0.1831 | 122.9233 | 60.91 | -0.28839 | 122.9416 | -0.1831 | 60.91 | 122.7036 | 122.9233 | -123.2391 | -123.2117
2013.7656 | 123.2208 | -60.8917 | 62.0407 | 0.17143 | -0.0077888 | -0.01348 | -0.00035676 | 0.057114 | -0.0067185 | 0.065702 | -61.0382 | 62.0544 | -61.2076 | -61.1252 | 61.8301 | 0.041199 | -0.07782 | 0.17395 | 62.0728 | -61.1526 | -0.31586 | 0.013733 | -0.14648 | -0.23346 | -0.21057 | -0.26092 | 0.032044 | 0.16937 | 60.8139 | 61.0657 | 122.7219 | 122.9462 | -0.14648 | 122.9645 | 60.9329 | -0.26092 | 122.9462 | -0.14648 | 60.9329 | 122.7219 | 122.9645 | -123.2483 | -123.1934
2014.7656 | 123.2117 | -60.878 | 62.0636 | 0.13329 | -0.0062934 | -0.012625 | 0.0011386 | 0.059037 | -0.0043685 | 0.065702 | -61.0611 | 62.0453 | -61.2076 | -61.1252 | 61.821 | 0.032043 | -0.073242 | 0.14648 | 62.0453 | -61.1526 | -0.32959 | -0.018311 | -0.1831 | -0.24719 | -0.24262 | -0.27466 | -0.018311 | 0.14648 | 60.8047 | 61.0245 | 122.699 | 122.9233 | -0.1831 | 122.9233 | 60.91 | -0.27466 | 122.9233 | -0.1831 | 60.91 | 122.699 | 122.9233 | -123.2712 | -123.2162
2015.7812 | 123.2208 | -60.8597 | 62.027 | -0.18715 | -0.0069342 | -0.010489 | -0.00035676 | 0.057114 | -0.0056503 | 0.067624 | -60.9741 | 62.0728 | -61.1526 | -61.2076 | 61.7615 | 0.13275 | -0.13275 | 0.3067 | 62.0178 | -61.1435 | -0.29297 | 0.045776 | -0.11444 | -0.3479 | -0.2655 | -0.28381 | -0.009156 | 0.17853 | 60.7269 | 61.1664 | 122.6212 | 122.9324 | -0.11444 | 122.8775 | 60.9924 | -0.28381 | 122.9324 | -0.11444 | 60.9924 | 122.6212 | 122.8775 | -123.1796 | -123.1705
2016.7656 | 123.1934 | -60.8734 | 62.0087 | 0.1104 | -0.007575 | -0.010916 | -0.00014316 | 0.057969 | -0.0056503 | 0.067838 | -61.0703 | 62.059 | -61.2122 | -61.116 | 61.8118 | 0.027466 | -0.073242 | 0.16479 | 62.0636 | -61.1389 | -0.33875 | 0.050354 | -0.19684 | -0.24262 | -0.19684 | -0.2655 | 0.054932 | 0.14191 | 60.8002 | 61.0382 | 122.6852 | 122.9324 | -0.19684 | 122.937 | 60.9009 | -0.2655 | 122.9324 | -0.19684 | 60.9009 | 122.6852 | 122.937 | -123.2208 | -123.1476
2017.7656 | 123.2117 | -60.9055 | 62.0499 | 0.041733 | -0.0086432 | -0.012625 | 0.00028404 | 0.059678 | -0.0041549 | 0.066556 | -61.0382 | 62.0499 | -61.1526 | -61.0657 | 61.8576 | 0.082397 | -0.068665 | 0.23346 | 62.0819 | -61.1343 | -0.24719 | 0 | -0.13275 | -0.16022 | -0.19226 | -0.22888 | 0.032043 | 0.11444 | 60.8368 | 61.1389 | 122.7631 | 122.9553 | -0.13275 | 122.9874 | 60.9879 | -0.22888 | 122.9553 | -0.13275 | 60.9879 | 122.7631 | 122.9874 | -123.2025 | -123.1842
2018.7656 | 123.1888 | -60.8643 | 62.0453 | 0.064621 | -0.0086432 | -0.011984 | 0.00092504 | 0.058182 | -0.0060775 | 0.067411 | -61.0245 | 62.0728 | -61.1984 | -61.0748 | 61.8713 | 0.068665 | -0.068665 | 0.23346 | 62.0636 | -61.1389 | -0.33417 | 0.027466 | -0.16022 | -0.21057 | -0.17395 | -0.27466 | 0.018311 | 0.17395 | 60.7956 | 61.0977 | 122.7356 | 122.937 | -0.16022 | 122.9279 | 60.9329 | -0.27466 | 122.937 | -0.16022 | 60.9329 | 122.7356 | 122.9279 | -123.2437 | -123.1842
2019.7656 | 123.2162 | -60.8734 | 62.0453 | 0.018845 | -0.0071478 | -0.0079253 | -0.00014316 | 0.056687 | -0.0054367 | 0.06677 | -61.0291 | 62.0911 | -61.1893 | -61.0794 | 61.8622 | 0.082397 | -0.082397 | 0.23346 | 62.0407 | -61.116 | -0.31586 | 0.045776 | -0.15564 | -0.20599 | -0.1831 | -0.24262 | -0.004578 | 0.16022 | 60.791 | 61.1069 | 122.7356 | 122.9645 | -0.15564 | 122.9141 | 60.9558 | -0.24262 | 122.9645 | -0.15564 | 60.9558 | 122.7356 | 122.9141 | -123.2346 | -123.1613
2020.7812 | 123.1247 | -60.9009 | 62.059 | 0.056992 | -0.0043708 | -0.010062 | 0.0098972 | 0.059464 | -0.0043685 | 0.066343 | -60.9741 | 62.1643 | -61.1801 | -61.0931 | 61.8027 | 0.013733 | 0 | 0.13275 | 62.0819 | -61.2167 | -0.27924 | 0.10529 | -0.073242 | -0.19226 | -0.25635 | -0.31586 | 0.022888 | 0.20599 | 60.9009 | 61.0336 | 122.7036 | 123.0652 | -0.073242 | 122.9828 | 60.9146 | -0.31586 | 123.0652 | -0.073242 | 60.9146 | 122.7036 | 122.9828 | -123.2391 | -123.2758
2021.7656 | 123.23 | -60.878 | 62.0224 | -0.026932 | -0.008216 | -0.014548 | -0.0020658 | 0.058182 | -0.0050095 | 0.06677 | -61.0245 | 62.0636 | -61.1801 | -61.0886 | 61.8851 | 0.09613 | -0.073242 | 0.23804 | 62.0544 | -61.1389 | -0.30212 | 0.041199 | -0.14648 | -0.21057 | -0.13733 | -0.26093 | 0.032043 | 0.15564 | 60.8047 | 61.116 | 122.7631 | 122.9416 | -0.14648 | 122.9324 | 60.9741 | -0.26093 | 122.9416 | -0.14648 | 60.9741 | 122.7631 | 122.9324 | -123.2025 | -123.1613
2022.7656 | 123.1705 | -60.8871 | 62.0132 | 0.056992 | -0.0080024 | -0.0096343 | -0.0018522 | 0.059464 | -0.0043685 | 0.068906 | -61.0703 | 62.0728 | -61.2122 | -61.1343 | 61.8439 | 0.022888 | -0.054932 | 0.15106 | 62.0224 | -61.1664 | -0.32501 | 0.059509 | -0.1831 | -0.24719 | -0.16937 | -0.27924 | 0.009155 | 0.14191 | 60.8322 | 61.0382 | 122.731 | 122.9599 | -0.1831 | 122.9095 | 60.91 | -0.27924 | 122.9599 | -0.1831 | 60.91 | 122.731 | 122.9095 | -123.2254 | -123.1796
2023.7812 | 123.2162 | -60.8551 | 62.0499 | -0.57625 | -0.0073614 | -0.010275 | 0.0015658 | 0.058396 | -0.0075729 | 0.06677 | -60.9787 | 62.0544 | -61.1526 | -61.0291 | 61.9171 | 0.15564 | -0.054932 | 0.29297 | 62.0819 | -61.1343 | -0.29755 | 0.004577 | -0.1236 | -0.17395 | -0.13275 | -0.27923 | 0.032043 | 0.17395 | 60.8002 | 61.1481 | 122.7722 | 122.9095 | -0.1236 | 122.937 | 61.0107 | -0.27923 | 122.9095 | -0.1236 | 61.0107 | 122.7722 | 122.937 | -123.2025 | -123.1842
2024.7656 | 123.2483 | -60.8826 | 62.0316 | -0.16426 | -0.0077888 | -0.010489 | 0.0024202 | 0.059251 | -0.0050095 | 0.067411 | -60.9741 | 62.0728 | -61.1755 | -61.0016 | 61.9263 | 0.16022 | -0.07782 | 0.27466 | 62.0636 | -61.1252 | -0.29297 | 0.041199 | -0.091553 | -0.11902 | -0.10528 | -0.24262 | 0.032044 | 0.20142 | 60.8047 | 61.1572 | 122.8088 | 122.9553 | -0.091553 | 122.9462 | 61.0428 | -0.24262 | 122.9553 | -0.091553 | 61.0428 | 122.8088 | 122.9462 | -123.2071 | -123.1567
2025.7812 | 123.1247 | -60.9238 | 62.0499 | 0.056992 | -0.0026618 | -0.0057891 | 0.0092562 | 0.061387 | -0.0043685 | 0.064847 | -60.9604 | 62.1597 | -61.1984 | -61.1069 | 61.7981 | 0.022888 | 0 | 0.11902 | 62.1002 | -61.1893 | -0.27466 | 0.10986 | -0.036621 | -0.18311 | -0.25177 | -0.2655 | 0.050354 | 0.23804 | 60.9238 | 61.0428 | 122.7219 | 123.0835 | -0.036621 | 123.024 | 60.9467 | -0.2655 | 123.0835 | -0.036621 | 60.9467 | 122.7219 | 123.024 | -123.2483 | -123.2391
2026.7656 | 123.2437 | -60.8688 | 62.0178 | -0.072708 | -0.007575 | -0.012198 | 7.0444e-05 | 0.063096 | -0.0056503 | 0.066556 | -60.9695 | 62.0453 | -61.203 | -61.0153 | 61.9308 | 0.16479 | -0.073242 | 0.28839 | 62.1094 | -61.0931 | -0.33417 | 0.027466 | -0.10071 | -0.14649 | -0.086975 | -0.22431 | 0.091553 | 0.23346 | 60.7956 | 61.1572 | 122.7997 | 122.9141 | -0.10071 | 122.9782 | 61.0336 | -0.22431 | 122.9141 | -0.10071 | 61.0336 | 122.7997 | 122.9782 | -123.2208 | -123.111
2027.7656 | 123.23 | -60.8505 | 62.0407 | -0.11085 | -0.008216 | -0.0057891 | -0.00078396 | 0.058396 | -0.0060775 | 0.06912 | -60.9833 | 62.0636 | -61.1618 | -61.0199 | 61.9217 | 0.16022 | -0.091553 | 0.3067 | 62.0728 | -61.1526 | -0.31128 | 0.022889 | -0.13275 | -0.16937 | -0.11902 | -0.30212 | 0.032044 | 0.17853 | 60.759 | 61.1572 | 122.7722 | 122.9141 | -0.13275 | 122.9233 | 61.0107 | -0.30212 | 122.9141 | -0.13275 | 61.0107 | 122.7722 | 122.9233 | -123.2025 | -123.1934
2028.7656 | 123.2208 | -60.8917 | 62.027 | -0.04219 | -0.0084296 | -0.0094207 | -0.00078396 | 0.056046 | -0.0062911 | 0.067411 | -61.0382 | 62.0728 | -61.1893 | -61.0748 | 61.8713 | 0.10071 | -0.073242 | 0.23804 | 62.0453 | -61.1435 | -0.29755 | 0.045776 | -0.14648 | -0.1831 | -0.15564 | -0.25177 | 0.01831 | 0.15106 | 60.8185 | 61.1298 | 122.7631 | 122.9645 | -0.14648 | 122.937 | 60.9924 | -0.25177 | 122.9645 | -0.14648 | 60.9924 | 122.7631 | 122.937 | -123.2162 | -123.1705
2029.7656 | 123.2208 | -60.8597 | 62.0453 | -0.0040434 | -0.0077888 | -0.011984 | 0.002634 | 0.058823 | -0.0060775 | 0.068479 | -60.965 | 62.0911 | -61.1526 | -61.0382 | 61.9308 | 0.14191 | -0.086975 | 0.32044 | 62.0911 | -61.1114 | -0.29297 | 0.045776 | -0.10529 | -0.17853 | -0.11444 | -0.25177 | 0.045776 | 0.18768 | 60.7727 | 61.1801 | 122.7905 | 122.9507 | -0.10529 | 122.9507 | 61.0016 | -0.25177 | 122.9507 | -0.10529 | 61.0016 | 122.7905 | 122.9507 | -123.1979 | -123.1567
2030.7812 | 123.0881 | -60.9146 | 62.0728 | 0.23247 | -0.005866 | -0.0089935 | 0.0086154 | 0.060105 | -0.0043685 | 0.067624 | -61.0611 | 62.1048 | -61.2259 | -61.1801 | 61.7569 | 0.086975 | -0.45776 | -0.13733 | 62.0132 | -61.2305 | -0.31128 | 0.032043 | -0.14648 | -0.2655 | -0.31586 | -0.31586 | -0.059509 | 0.16479 | 60.4568 | 60.7773 | 122.6715 | 123.0194 | -0.14648 | 122.9279 | 61.0016 | -0.31586 | 123.0194 | -0.14648 | 61.0016 | 122.6715 | 122.9279 | -123.2986 | -123.3032
2031.7656 | 123.2162 | -60.8551 | 62.0361 | -0.149 | -0.010352 | -0.012412 | -0.00014316 | 0.060319 | -0.0047957 | 0.06677 | -60.9695 | 62.1277 | -61.1389 | -61.0199 | 61.8713 | 0.10986 | -0.064087 | 0.27924 | 62.0728 | -61.1526 | -0.28381 | 0.091553 | -0.11444 | -0.16479 | -0.16479 | -0.29755 | 0.036621 | 0.16937 | 60.791 | 61.1343 | 122.7264 | 122.9828 | -0.11444 | 122.9279 | 60.965 | -0.29755 | 122.9828 | -0.11444 | 60.965 | 122.7264 | 122.9279 | -123.175 | -123.1888
2032.7656 | 123.2437 | -60.8414 | 62.0224 | -0.149 | -0.0088568 | -0.015402 | -0.00099756 | 0.061173 | -0.0037277 | 0.068265 | -60.9695 | 62.0819 | -61.171 | -61.1023 | 61.8759 | 0.14191 | -0.10071 | 0.2655 | 62.059 | -61.1252 | -0.32959 | 0.059509 | -0.12817 | -0.26093 | -0.14648 | -0.28381 | 0.036621 | 0.20142 | 60.7407 | 61.1069 | 122.7173 | 122.9233 | -0.12817 | 122.9004 | 60.9833 | -0.28381 | 122.9233 | -0.12817 | 60.9833 | 122.7173 | 122.9004 | -123.1934 | -123.1476
2033.7656 | 123.23 | -60.8734 | 61.9904 | -0.11085 | -0.0071478 | -0.012412 | -0.0027066 | 0.056901 | -0.0069321 | 0.069333 | -60.9741 | 62.0636 | -61.1755 | -61.1755 | 61.7203 | 0.1236 | -0.15106 | 0.3067 | 62.0682 | -61.1572 | -0.30212 | 0.073243 | -0.10071 | -0.30212 | -0.27008 | -0.28381 | 0.07782 | 0.20142 | 60.7224 | 61.1801 | 122.5937 | 122.937 | -0.10071 | 122.9416 | 60.997 | -0.28381 | 122.937 | -0.10071 | 60.997 | 122.5937 | 122.9416 | -123.1659 | -123.1476
2034.7656 | 123.2254 | -60.8734 | 62.0316 | -0.10323 | -0.0080024 | -0.012625 | -0.00057036 | 0.057114 | -0.0067185 | 0.068052 | -60.9695 | 62.0865 | -61.1847 | -61.0336 | 62.2421 | 0.43945 | -0.28839 | 0.25177 | 62.0499 | -61.116 | -0.31128 | 0.054932 | -0.09613 | -0.16022 | 0.21057 | -0.24262 | 0.018311 | 0.21515 | 60.585 | 61.1252 | 123.1155 | 122.9599 | -0.09613 | 122.9233 | 61.3129 | -0.24262 | 122.9599 | -0.09613 | 61.3129 | 123.1155 | 122.9233 | -123.2162 | -123.1476
2035.7656 | 123.2208 | -60.8643 | 62.0178 | 0.0035856 | -0.0060798 | -0.012412 | 0.00028404 | 0.058823 | -0.0047957 | 0.066343 | -61.0016 | 62.0453 | -61.171 | -61.0519 | 61.8805 | 0.10986 | -0.07782 | 0.27924 | 62.0453 | -61.1343 | -0.3067 | 0.027466 | -0.13733 | -0.18768 | -0.13733 | -0.27008 | 0.027466 | 0.16937 | 60.7864 | 61.1435 | 122.7448 | 122.9095 | -0.13733 | 122.9095 | 60.9741 | -0.27008 | 122.9095 | -0.13733 | 60.9741 | 122.7448 | 122.9095 | -123.1888 | -123.1522
2036.7656 | 123.2162 | -60.8185 | 62.0499 | -0.11085 | -0.009284 | -0.012198 | 7.0444e-05 | 0.059251 | -0.0080001 | 0.066984 | -60.9604 | 62.0544 | -61.1847 | -61.0382 | 61.908 | 0.13733 | -0.054932 | 0.30212 | 62.0728 | -61.1252 | -0.36621 | 0.004577 | -0.14191 | -0.21973 | -0.14191 | -0.3067 | 0.022888 | 0.2243 | 60.7635 | 61.1206 | 122.7264 | 122.8729 | -0.14191 | 122.8912 | 60.9558 | -0.3067 | 122.8729 | -0.14191 | 60.9558 | 122.7264 | 122.8912 | -123.2346 | -123.175
2037.7656 | 123.1613 | -60.8597 | 62.0499 | -0.15663 | -0.0077888 | -0.011984 | 0.0013522 | 0.058396 | -0.0071457 | 0.065061 | -60.9604 | 62.0911 | -61.171 | -61.0428 | 61.9034 | 0.15106 | -0.032043 | 0.30212 | 62.0865 | -61.116 | -0.31128 | 0.041198 | -0.10071 | -0.18311 | -0.14648 | -0.25635 | 0.036621 | 0.21057 | 60.8276 | 61.1618 | 122.7631 | 122.9507 | -0.10071 | 122.9462 | 61.0107 | -0.25635 | 122.9507 | -0.10071 | 61.0107 | 122.7631 | 122.9462 | -123.2208 | -123.1659
2038.7656 | 123.2071 | -60.8643 | 62.059 | -0.087967 | -0.0094976 | -0.01113 | 0.0015658 | 0.05861 | -0.0050095 | 0.066129 | -60.9741 | 62.0819 | -61.1664 | -61.0336 | 61.9034 | 0.13275 | -0.022888 | 0.29297 | 62.0544 | -61.1114 | -0.30212 | 0.022888 | -0.10986 | -0.16937 | -0.15564 | -0.24719 | -0.004578 | 0.19226 | 60.8414 | 61.1572 | 122.7676 | 122.9462 | -0.10986 | 122.9187 | 60.997 | -0.24719 | 122.9462 | -0.10986 | 60.997 | 122.7676 | 122.9187 | -123.2254 | -123.1705
2039.7656 | 123.23 | -60.8734 | 62.059 | -0.27107 | -0.0097114 | -0.0098479 | 0.0017794 | 0.06096 | -0.0071457 | 0.067197 | -60.9467 | 62.059 | -61.1618 | -61.0382 | 61.908 | 0.12817 | -0.022888 | 0.3067 | 62.0636 | -61.1343 | -0.28839 | 0 | -0.073242 | -0.16479 | -0.15106 | -0.26093 | 0.004578 | 0.21515 | 60.8505 | 61.1801 | 122.7814 | 122.9324 | -0.073242 | 122.937 | 61.0016 | -0.26093 | 122.9324 | -0.073242 | 61.0016 | 122.7814 | 122.937 | -123.2208 | -123.1934
2040.7656 | 123.2117 | -60.878 | 62.0636 | 0.40031 | -0.0086432 | -0.0096343 | 0.00071144 | 0.059251 | -0.0041549 | 0.068906 | -60.9787 | 62.059 | -61.1618 | -61.0428 | 61.8942 | 0.13275 | -0.041199 | 0.27924 | 62.0773 | -61.116 | -0.28381 | -0.004578 | -0.10071 | -0.16479 | -0.16937 | -0.23804 | 0.013733 | 0.1831 | 60.8368 | 61.1572 | 122.7722 | 122.937 | -0.10071 | 122.9553 | 61.0107 | -0.23804 | 122.937 | -0.10071 | 61.0107 | 122.7722 | 122.9553 | -123.2254 | -123.1796
2041.7656 | 123.2025 | -60.8368 | 62.059 | -0.087967 | -0.0086432 | -0.0085663 | 0.001993 | 0.057969 | -0.0090683 | 0.068265 | -61.0382 | 62.0773 | -61.1938 | -61.0382 | 61.9125 | 0.15564 | -0.045776 | 0.29755 | 62.0636 | -61.1343 | -0.35706 | 0.018311 | -0.20142 | -0.20142 | -0.14648 | -0.29755 | 0.004578 | 0.15564 | 60.791 | 61.1343 | 122.7493 | 122.9141 | -0.20142 | 122.9004 | 60.9924 | -0.29755 | 122.9141 | -0.20142 | 60.9924 | 122.7493 | 122.9004 | -123.2529 | -123.1934
2042.7656 | 123.23 | -60.8643 | 62.0224 | -0.057449 | -0.0088568 | -0.012625 | 0.0022066 | 0.057755 | -0.0050095 | 0.067838 | -60.9787 | 62.0865 | -61.1893 | -61.0291 | 61.908 | 0.15106 | -0.09613 | 0.29755 | 62.0728 | -61.1206 | -0.32501 | 0.064087 | -0.11444 | -0.16479 | -0.11444 | -0.25635 | 0.050354 | 0.21057 | 60.7681 | 61.1618 | 122.7722 | 122.9507 | -0.11444 | 122.937 | 61.0153 | -0.25635 | 122.9507 | -0.11444 | 61.0153 | 122.7722 | 122.937 | -123.2117 | -123.143
2043.7656 | 123.2117 | -60.8643 | 62.0407 | -0.15663 | -0.0067206 | -0.011343 | -0.004202 | 0.058396 | -0.0039413 | 0.067411 | -60.965 | 62.0773 | -61.1343 | -61.0565 | 61.8622 | 0.10071 | -0.041199 | 0.24719 | 62.0544 | -61.1343 | -0.27008 | 0.036622 | -0.10071 | -0.19226 | -0.17853 | -0.27008 | 0.013733 | 0.16937 | 60.8231 | 61.1114 | 122.7264 | 122.9416 | -0.10071 | 122.9187 | 60.965 | -0.27008 | 122.9416 | -0.10071 | 60.965 | 122.7264 | 122.9187 | -123.175 | -123.175
2044.7656 | 123.1934 | -60.8551 | 62.0499 | -0.14137 | -0.0090704 | -0.0085663 | 0.0032748 | 0.057969 | -0.0060775 | 0.068906 | -60.9695 | 62.0956 | -61.1938 | -61.0565 | 61.8942 | 0.13275 | 0.009155 | 0.28839 | 62.0544 | -61.1481 | -0.33875 | 0.045776 | -0.11444 | -0.20142 | -0.15564 | -0.29297 | 0.004577 | 0.22431 | 60.8643 | 61.1435 | 122.7493 | 122.9507 | -0.11444 | 122.9095 | 60.9879 | -0.29297 | 122.9507 | -0.11444 | 60.9879 | 122.7493 | 122.9095 | -123.2437 | -123.1979
2045.7656 | 123.1842 | -60.8414 | 62.0224 | -0.072708 | -0.009284 | -0.010703 | 0.0028476 | 0.059251 | -0.0062911 | 0.065702 | -60.9695 | 62.0728 | -61.1664 | -61.0428 | 61.908 | 0.1236 | 0.004578 | 0.29755 | 62.0819 | -61.1526 | -0.32501 | 0.050354 | -0.12817 | -0.20142 | -0.11444 | -0.31128 | 0.059509 | 0.19684 | 60.8459 | 61.1389 | 122.7493 | 122.9141 | -0.12817 | 122.9233 | 60.965 | -0.31128 | 122.9141 | -0.12817 | 60.965 | 122.7493 | 122.9233 | -123.1888 | -123.175
2046.7656 | 123.2071 | -60.8963 | 62.0407 | -0.12611 | -0.0067206 | -0.0066437 | 0.00071144 | 0.059251 | -0.0075729 | 0.066556 | -60.9741 | 62.0773 | -61.1664 | -61.0382 | 61.908 | 0.13275 | -0.022888 | 0.29297 | 62.0773 | -61.0977 | -0.27008 | 0.036622 | -0.07782 | -0.14191 | -0.13275 | -0.20142 | 0.036622 | 0.19226 | 60.8734 | 61.1893 | 122.8043 | 122.9736 | -0.07782 | 122.9736 | 61.0291 | -0.20142 | 122.9736 | -0.07782 | 61.0291 | 122.8043 | 122.9736 | -123.2071 | -123.1384
2047.7656 | 123.1979 | -60.8551 | 62.0499 | 0.018845 | -0.0086432 | -0.0087799 | 0.0011386 | 0.057969 | -0.0071457 | 0.067197 | -60.9879 | 62.0773 | -61.1984 | -61.0519 | 61.8988 | 0.14191 | -0.032043 | 0.29755 | 62.0407 | -61.1343 | -0.34332 | 0.027466 | -0.13275 | -0.19684 | -0.15106 | -0.27923 | -0.009156 | 0.21057 | 60.8231 | 61.1526 | 122.7539 | 122.9324 | -0.13275 | 122.8958 | 60.997 | -0.27923 | 122.9324 | -0.13275 | 60.997 | 122.7539 | 122.8958 | -123.2483 | -123.1842
2048.7656 | 123.2117 | -60.878 | 62.0407 | -0.67543 | -0.0080024 | -0.012839 | 0.002634 | 0.058396 | -0.0069321 | 0.068265 | -60.9879 | 62.0865 | -61.171 | -61.0245 | 61.908 | 0.14191 | -0.027466 | 0.29297 | 62.0682 | -61.1343 | -0.29297 | 0.045777 | -0.10986 | -0.14648 | -0.13275 | -0.25635 | 0.027466 | 0.18311 | 60.8505 | 61.171 | 122.7859 | 122.9645 | -0.10986 | 122.9462 | 61.0199 | -0.25635 | 122.9645 | -0.10986 | 61.0199 | 122.7859 | 122.9462 | -123.2117 | -123.175
2049.7656 | 123.2712 | -60.8505 | 62.0316 | 0.0035856 | -0.0077888 | -0.0089935 | 7.0444e-05 | 0.056473 | -0.0047957 | 0.067197 | -60.9558 | 62.0636 | -61.1664 | -61.0291 | 61.9217 | 0.15106 | -0.086975 | 0.3067 | 62.0636 | -61.1435 | -0.31586 | 0.032044 | -0.10529 | -0.17853 | -0.10986 | -0.29297 | 0.032044 | 0.21057 | 60.7635 | 61.1572 | 122.7722 | 122.9141 | -0.10529 | 122.9141 | 61.0016 | -0.29297 | 122.9141 | -0.10529 | 61.0016 | 122.7722 | 122.9141 | -123.1979 | -123.175
2050.7656 | 123.2254 | -60.8551 | 62.027 | -0.149 | -0.008216 | -0.013693 | -0.00035676 | 0.062028 | -0.0054367 | 0.066129 | -60.9695 | 62.0956 | -61.1847 | -61.0886 | 61.8484 | 0.11444 | -0.086975 | 0.24719 | 62.0453 | -61.1435 | -0.32959 | 0.068664 | -0.11444 | -0.23346 | -0.17853 | -0.28839 | 0.01831 | 0.21515 | 60.7681 | 61.1023 | 122.7036 | 122.9507 | -0.11444 | 122.9004 | 60.9695 | -0.28839 | 122.9507 | -0.11444 | 60.9695 | 122.7036 | 122.9004 | -123.2117 | -123.1705
2051.7656 | 123.175 | -60.8734 | 62.0499 | -0.14137 | -0.0060798 | -0.011343 | 0.001993 | 0.057755 | -0.0052231 | 0.067838 | -60.9879 | 62.0865 | -61.1801 | -61.0474 | 61.8805 | 0.1236 | 0.032043 | 0.27924 | 62.0956 | -61.1298 | -0.3067 | 0.036621 | -0.11444 | -0.17395 | -0.16937 | -0.25635 | 0.045776 | 0.19226 | 60.9055 | 61.1526 | 122.7539 | 122.9599 | -0.11444 | 122.9691 | 60.997 | -0.25635 | 122.9599 | -0.11444 | 60.997 | 122.7539 | 122.9691 | -123.23 | -123.1796
2052.7656 | 123.1888 | -60.8734 | 62.0544 | -0.14137 | -0.0073614 | -0.013907 | 0.0015658 | 0.057328 | -0.0054367 | 0.066984 | -60.9924 | 62.0956 | -61.1938 | -61.0428 | 61.8988 | 0.1236 | 0.013733 | 0.28381 | 62.0865 | -61.1252 | -0.32044 | 0.041199 | -0.11902 | -0.16937 | -0.15564 | -0.25177 | 0.032044 | 0.20142 | 60.8871 | 61.1572 | 122.7722 | 122.9691 | -0.11902 | 122.9599 | 60.997 | -0.25177 | 122.9691 | -0.11902 | 60.997 | 122.7722 | 122.9599 | -123.2483 | -123.1796
2053.7656 | 123.1979 | -60.8688 | 62.0453 | -0.13374 | -0.0077888 | -0.011557 | 7.0444e-05 | 0.060319 | -0.0060775 | 0.068479 | -60.9695 | 62.0544 | -61.1801 | -61.0519 | 61.8942 | 0.13733 | 0.009155 | 0.29297 | 62.0773 | -61.1343 | -0.31128 | 0.009155 | -0.10071 | -0.18311 | -0.15106 | -0.2655 | 0.032044 | 0.21057 | 60.878 | 61.1618 | 122.7631 | 122.9233 | -0.10071 | 122.9462 | 61.0062 | -0.2655 | 122.9233 | -0.10071 | 61.0062 | 122.7631 | 122.9462 | -123.2254 | -123.1796
2055.0312 | 123.2162 | -60.8826 | 61.9995 | 0.23247 | -0.0060798 | -0.0089935 | 0.0041292 | 0.0616 | -0.0039413 | 0.066556 | -60.9741 | 62.0911 | -61.1938 | -61.0977 | 61.8439 | 0.032043 | -0.19684 | 0.17395 | 62.0453 | -61.1893 | -0.31128 | 0.091552 | -0.091553 | -0.21515 | -0.15564 | -0.3067 | 0.045776 | 0.21973 | 60.6857 | 61.0565 | 122.7264 | 122.9736 | -0.091553 | 122.9279 | 60.9146 | -0.3067 | 122.9736 | -0.091553 | 60.9146 | 122.7264 | 122.9279 | -123.1934 | -123.1888
2055.7656 | 123.1522 | -60.9009 | 62.0682 | -0.026932 | -0.004798 | -0.010489 | 0.0069064 | 0.05861 | -0.0088547 | 0.066343 | -61.0611 | 62.1643 | -61.2213 | -61.1206 | 61.7844 | 0.036621 | 0.10529 | 0.1831 | 62.114 | -61.1938 | -0.32043 | 0.096131 | -0.16022 | -0.21973 | -0.28381 | -0.29297 | 0.045777 | 0.16022 | 61.0062 | 61.084 | 122.6852 | 123.0652 | -0.16022 | 123.0148 | 60.9375 | -0.29297 | 123.0652 | -0.16022 | 60.9375 | 122.6852 | 123.0148 | -123.2895 | -123.262
2056.7656 | 123.2162 | -60.8688 | 62.027 | -0.065079 | -0.010993 | -0.014121 | -0.00099756 | 0.058182 | -0.0080001 | 0.066343 | -60.9787 | 62.0728 | -61.171 | -61.0153 | 61.94 | 0.14648 | -0.059509 | 0.30212 | 62.0773 | -61.1343 | -0.30212 | 0.045776 | -0.10986 | -0.14649 | -0.086976 | -0.2655 | 0.050354 | 0.19226 | 60.8093 | 61.171 | 122.8088 | 122.9416 | -0.10986 | 122.9462 | 61.0153 | -0.2655 | 122.9416 | -0.10986 | 61.0153 | 122.8088 | 122.9462 | -123.1979 | -123.1613
2057.7656 | 123.2437 | -60.8597 | 62.0407 | -0.75935 | -0.0052252 | -0.013052 | 0.0015658 | 0.057755 | -0.0022323 | 0.066984 | -61.0016 | 62.0819 | -61.1572 | -61.0336 | 61.908 | 0.15564 | -0.036621 | 0.28839 | 62.0728 | -61.1481 | -0.29755 | 0.041199 | -0.14191 | -0.17395 | -0.13275 | -0.28839 | 0.032044 | 0.15564 | 60.8231 | 61.1481 | 122.7676 | 122.9416 | -0.14191 | 122.9324 | 61.0153 | -0.28839 | 122.9416 | -0.14191 | 61.0153 | 122.7676 | 122.9324 | -123.1979 | -123.1888
2058.7656 | 123.1796 | -60.8963 | 62.0682 | -0.18715 | -0.007575 | -0.015402 | 0.0017794 | 0.056473 | -0.0071457 | 0.066343 | -60.997 | 62.0911 | -61.1664 | -61.0794 | 61.8759 | 0.10529 | 0.045776 | 0.2655 | 62.0819 | -61.1206 | -0.27008 | 0.022888 | -0.10071 | -0.18311 | -0.19226 | -0.2243 | 0.013733 | 0.16937 | 60.9421 | 61.1618 | 122.7722 | 122.9874 | -0.10071 | 122.9782 | 61.0016 | -0.2243 | 122.9874 | -0.10071 | 61.0016 | 122.7722 | 122.9782 | -123.2346 | -123.1888
2059.7656 | 123.1659 | -60.8734 | 62.0636 | -0.17189 | -0.0097114 | -0.012412 | 0.0013522 | 0.057969 | -0.0075729 | 0.067411 | -60.9833 | 62.1094 | -61.1893 | -61.0657 | 61.8851 | 0.1236 | 0.018311 | 0.27924 | 62.0682 | -61.1298 | -0.31586 | 0.045776 | -0.10986 | -0.19226 | -0.17853 | -0.25635 | 0.004577 | 0.20599 | 60.8917 | 61.1526 | 122.7585 | 122.9828 | -0.10986 | 122.9416 | 60.997 | -0.25635 | 122.9828 | -0.10986 | 60.997 | 122.7585 | 122.9416 | -123.2529 | -123.1934
2060.7656 | 123.2071 | -60.8688 | 62.0636 | -0.10323 | -0.0088568 | -0.013907 | 0.002634 | 0.059678 | -0.0062911 | 0.067197 | -61.0016 | 62.0865 | -61.1847 | -61.0611 | 61.9034 | 0.13733 | 0.004578 | 0.29297 | 62.0499 | -61.1481 | -0.31586 | 0.022888 | -0.13275 | -0.19226 | -0.16022 | -0.27924 | -0.013733 | 0.1831 | 60.8734 | 61.1618 | 122.7722 | 122.9553 | -0.13275 | 122.9187 | 61.0062 | -0.27924 | 122.9553 | -0.13275 | 61.0062 | 122.7722 | 122.9187 | -123.2483 | -123.2117
2061.7656 | 123.2025 | -60.8597 | 62.0361 | -0.28633 | -0.0090704 | -0.011771 | 0.00071144 | 0.060105 | -0.0067185 | 0.065702 | -60.9741 | 62.0865 | -61.171 | -61.0428 | 61.8851 | 0.13733 | -0.004578 | 0.29297 | 62.0682 | -61.1435 | -0.31128 | 0.050354 | -0.11444 | -0.18311 | -0.15106 | -0.28381 | 0.032043 | 0.19684 | 60.8551 | 61.1526 | 122.7448 | 122.9462 | -0.11444 | 122.9279 | 60.997 | -0.28381 | 122.9462 | -0.11444 | 60.997 | 122.7448 | 122.9279 | -123.2071 | -123.1796
2062.7656 | 123.1934 | -60.8643 | 62.0407 | 0.28587 | -0.010139 | -0.010489 | 0.00071144 | 0.0616 | -0.0069321 | 0.067838 | -60.9467 | 62.059 | -61.1893 | -61.0382 | 61.8942 | 0.13733 | -0.032043 | 0.29297 | 62.0636 | -61.1298 | -0.32501 | 0.018311 | -0.082397 | -0.17395 | -0.14648 | -0.2655 | 0.022889 | 0.24262 | 60.8322 | 61.1572 | 122.7585 | 122.9233 | -0.082397 | 122.9279 | 61.0016 | -0.2655 | 122.9233 | -0.082397 | 61.0016 | 122.7585 | 122.9279 | -123.23 | -123.1705
2063.7656 | 123.2208 | -60.8871 | 62.0544 | -0.14137 | -0.008216 | -0.011343 | 0.0032748 | 0.059251 | -0.0067185 | 0.067197 | -60.9558 | 62.1002 | -61.1481 | -61.0291 | 61.8851 | 0.10071 | -0.068665 | 0.27466 | 62.027 | -61.1206 | -0.26093 | 0.045777 | -0.068665 | -0.14191 | -0.16937 | -0.23346 | -0.027465 | 0.19226 | 60.8185 | 61.1618 | 122.7722 | 122.9874 | -0.068665 | 122.9141 | 60.9879 | -0.23346 | 122.9874 | -0.068665 | 60.9879 | 122.7722 | 122.9141 | -123.2025 | -123.175
2064.7656 | 123.2346 | -60.8917 | 62.0224 | -0.10323 | -0.009284 | -0.0062163 | 0.0013522 | 0.059464 | -0.0058639 | 0.068265 | -60.965 | 62.0544 | -61.1755 | -60.9421 | 62.233 | 0.40283 | -0.29297 | 0.30212 | 62.0911 | -61.1252 | -0.28381 | 0.032043 | -0.073242 | -0.050354 | 0.21057 | -0.23346 | 0.068664 | 0.21057 | 60.5988 | 61.1938 | 123.1247 | 122.9462 | -0.073242 | 122.9828 | 61.2946 | -0.23346 | 122.9462 | -0.073242 | 61.2946 | 123.1247 | 122.9828 | -123.1979 | -123.1476
2065.7656 | 123.2162 | -60.8871 | 62.0636 | -0.13374 | -0.009284 | -0.014334 | 0.0024202 | 0.057969 | -0.0080001 | 0.067197 | -60.9833 | 62.0865 | -61.1618 | -61.0565 | 61.8851 | 0.13733 | -0.018311 | 0.28839 | 62.0865 | -61.116 | -0.27466 | 0.022888 | -0.09613 | -0.16937 | -0.17853 | -0.22888 | 0.022888 | 0.17853 | 60.8688 | 61.1755 | 122.7722 | 122.9736 | -0.09613 | 122.9736 | 61.0245 | -0.22888 | 122.9736 | -0.09613 | 61.0245 | 122.7722 | 122.9736 | -123.2254 | -123.1796
2066.7656 | 123.2346 | -60.878 | 62.0544 | 0.20958 | -0.010139 | -0.011557 | 0.00092504 | 0.059678 | -0.0082137 | 0.067838 | -60.9879 | 62.059 | -61.1847 | -61.0611 | 61.8988 | 0.13275 | -0.032043 | 0.29755 | 62.059 | -61.1572 | -0.3067 | 0.004578 | -0.10986 | -0.1831 | -0.15564 | -0.27924 | 0.004578 | 0.19684 | 60.8459 | 61.1755 | 122.7768 | 122.937 | -0.10986 | 122.937 | 61.0107 | -0.27924 | 122.937 | -0.10986 | 61.0107 | 122.7768 | 122.937 | -123.2391 | -123.2117
2067.7656 | 123.2346 | -60.8505 | 62.0682 | -2.27 | -0.0080024 | -0.0094207 | 0.0017794 | 0.057969 | -0.0056503 | 0.06677 | -61.171 | 62.1048 | -61.171 | -61.0474 | 61.8668 | 0.1236 | -0.041199 | 0.31128 | 62.0773 | -61.1252 | -0.32043 | 0.036621 | -0.32043 | -0.19684 | -0.20142 | -0.27466 | 0.009156 | 0 | 60.8093 | 61.1618 | 122.7173 | 122.9553 | -0.32043 | 122.9279 | 60.9741 | -0.27466 | 122.9553 | -0.32043 | 60.9741 | 122.7173 | 122.9279 | -123.2391 | -123.1934
2068.7656 | 123.2162 | -60.878 | 62.0361 | -0.13374 | -0.0073614 | -0.012839 | 0.00071144 | 0.052842 | -0.0088547 | 0.067624 | -60.965 | 62.0636 | -61.1801 | -61.1938 | 61.7523 | 0.1236 | -0.13275 | 0.3067 | 62.0636 | -61.1389 | -0.30212 | 0.027466 | -0.086975 | -0.31586 | -0.28381 | -0.26093 | 0.027466 | 0.21515 | 60.7452 | 61.1847 | 122.6303 | 122.9416 | -0.086975 | 122.9416 | 61.0016 | -0.26093 | 122.9416 | -0.086975 | 61.0016 | 122.6303 | 122.9416 | -123.2162 | -123.175
2069.7656 | 123.3398 | -60.8368 | 62.0956 | -0.15663 | -0.009284 | -0.015189 | 0.001993 | 0.058182 | -0.0062911 | 0.068052 | -60.9558 | 62.0682 | -61.1755 | -61.0382 | 61.908 | 0.14648 | -0.045776 | 0.3067 | 62.0728 | -61.1114 | -0.33874 | -0.027466 | -0.11902 | -0.20142 | -0.18768 | -0.27466 | -0.022888 | 0.21973 | 60.791 | 61.1435 | 122.7448 | 122.905 | -0.11902 | 122.9095 | 60.9833 | -0.27466 | 122.905 | -0.11902 | 60.9833 | 122.7448 | 122.9095 | -123.2712 | -123.2071
2070.7656 | 123.2025 | -60.8917 | 62.0316 | -0.011673 | -0.009284 | -0.012412 | -0.0012112 | 0.059891 | -0.0058639 | 0.065702 | -61.0153 | 62.0682 | -61.1847 | -61.0703 | 61.8805 | 0.10071 | -0.068665 | 0.25635 | 62.0544 | -61.1481 | -0.29297 | 0.036621 | -0.1236 | -0.17853 | -0.15106 | -0.25635 | 0.022888 | 0.16937 | 60.8231 | 61.1481 | 122.7722 | 122.9599 | -0.1236 | 122.9462 | 60.9924 | -0.25635 | 122.9599 | -0.1236 | 60.9924 | 122.7722 | 122.9462 | -123.2162 | -123.1796
2071.7656 | 123.2483 | -60.8597 | 62.0544 | -0.026932 | -0.010352 | -0.0094207 | 0.00049764 | 0.057755 | -0.0026595 | 0.066556 | -60.9741 | 62.0453 | -61.1801 | -61.0199 | 61.9171 | 0.15106 | -0.086975 | 0.31128 | 62.0453 | -61.1435 | -0.32044 | -0.009155 | -0.11444 | -0.16022 | -0.13733 | -0.28381 | -0.009155 | 0.20599 | 60.7727 | 61.171 | 122.7768 | 122.905 | -0.11444 | 122.905 | 61.0107 | -0.28381 | 122.905 | -0.11444 | 61.0107 | 122.7768 | 122.905 | -123.2346 | -123.1979
2072.7656 | 123.2117 | -60.8734 | 62.0361 | -0.14137 | -0.0073614 | -0.01113 | -0.0020658 | 0.057328 | -0.0058639 | 0.067838 | -60.9695 | 62.0773 | -61.1664 | -60.8093 | 62.1643 | 0.2243 | -0.23346 | 0.28839 | 62.0453 | -61.1069 | -0.29297 | 0.041199 | -0.09613 | 0.064087 | 0.12817 | -0.23346 | 0.009155 | 0.19684 | 60.64 | 61.1618 | 123.0377 | 122.9507 | -0.09613 | 122.9187 | 61.0977 | -0.23346 | 122.9507 | -0.09613 | 61.0977 | 123.0377 | 122.9187 | -123.2025 | -123.143
2073.7656 | 123.2346 | -60.8551 | 62.0407 | -0.095596 | -0.0069342 | -0.014548 | -0.00035676 | 0.057542 | -0.0062911 | 0.067624 | -60.9467 | 62.0544 | -61.1755 | -61.0336 | 61.9034 | 0.14648 | -0.041199 | 0.32501 | 62.0361 | -61.1389 | -0.32043 | 0.013733 | -0.091552 | -0.17853 | -0.13733 | -0.28381 | -0.004577 | 0.22888 | 60.8139 | 61.1801 | 122.7585 | 122.9095 | -0.091552 | 122.8912 | 61.0016 | -0.28381 | 122.9095 | -0.091552 | 61.0016 | 122.7585 | 122.8912 | -123.2162 | -123.1796
2074.7656 | 123.2254 | -60.8368 | 62.0316 | -0.0040434 | -0.009284 | -0.012198 | 7.0444e-05 | 0.055405 | -0.0045821 | 0.068052 | -60.9604 | 62.059 | -61.1893 | -61.0245 | 61.9217 | 0.14648 | -0.068665 | 0.30212 | 62.0728 | -61.1206 | -0.35248 | 0.027466 | -0.1236 | -0.18768 | -0.10986 | -0.28381 | 0.041199 | 0.22888 | 60.7681 | 61.1389 | 122.7585 | 122.8958 | -0.1236 | 122.9095 | 60.9833 | -0.28381 | 122.8958 | -0.1236 | 60.9833 | 122.7585 | 122.9095 | -123.2208 | -123.1522
2075.7656 | 123.2437 | -60.8734 | 62.0361 | -0.0040434 | -0.0088568 | -0.012625 | -0.00057036 | 0.057328 | -0.0039413 | 0.067197 | -60.9924 | 62.0544 | -61.171 | -61.0291 | 61.908 | 0.14648 | -0.10529 | 0.3067 | 62.0499 | -61.1252 | -0.29755 | 0.01831 | -0.11902 | -0.15564 | -0.12817 | -0.25177 | 0.013733 | 0.17853 | 60.7681 | 61.1801 | 122.7814 | 122.9279 | -0.11902 | 122.9233 | 61.0199 | -0.25177 | 122.9279 | -0.11902 | 61.0199 | 122.7814 | 122.9233 | -123.2071 | -123.1613
2076.7656 | 123.2208 | -60.8459 | 62.0499 | 0.026474 | -0.0088568 | -0.0094207 | 0.00049764 | 0.060105 | -0.0047957 | 0.066343 | -61.0062 | 62.0499 | -61.1893 | -61.0565 | 61.8896 | 0.11444 | -0.082397 | 0.27466 | 62.0361 | -61.1526 | -0.34332 | 0 | -0.16022 | -0.21057 | -0.16022 | -0.3067 | -0.013733 | 0.1831 | 60.7636 | 61.1206 | 122.7356 | 122.8958 | -0.16022 | 122.8821 | 60.9604 | -0.3067 | 122.8958 | -0.16022 | 60.9604 | 122.7356 | 122.8821 | -123.2391 | -123.2025
2077.7656 | 123.1705 | -60.8643 | 62.059 | 0.72838 | -0.0060798 | -0.014121 | -0.00057036 | 0.059678 | -0.0056503 | 0.065702 | -61.0199 | 62.0499 | -61.203 | -61.1343 | 61.8393 | 0.022888 | -0.091553 | 0.17853 | 62.0773 | -61.1343 | -0.33875 | -0.009155 | -0.15564 | -0.27008 | -0.21973 | -0.27008 | 0.018311 | 0.18311 | 60.7727 | 61.0428 | 122.7036 | 122.9141 | -0.15564 | 122.9416 | 60.8871 | -0.27008 | 122.9141 | -0.15564 | 60.8871 | 122.7036 | 122.9416 | -123.262 | -123.1934
2078.7656 | 123.1888 | -60.8734 | 62.027 | 0.072251 | -0.0080024 | -0.013052 | -0.0018522 | 0.057328 | -0.0028731 | 0.070402 | -61.0428 | 62.059 | -61.1801 | -61.0657 | 61.8622 | 0.07782 | -0.086975 | 0.21973 | 62.027 | -61.1526 | -0.3067 | 0.032043 | -0.16937 | -0.19226 | -0.16479 | -0.27924 | 0 | 0.13733 | 60.7864 | 61.0931 | 122.7356 | 122.9324 | -0.16937 | 122.9004 | 60.9512 | -0.27924 | 122.9324 | -0.16937 | 60.9512 | 122.7356 | 122.9004 | -123.2071 | -123.1796
2079.7656 | 123.2483 | -60.8505 | 62.0316 | 0.026474 | -0.0090704 | -0.0094207 | -0.00078396 | 0.057542 | -0.0041549 | 0.065275 | -61.0062 | 62.059 | -61.203 | -61.0565 | 61.8988 | 0.11902 | -0.091553 | 0.25635 | 62.0407 | -61.1526 | -0.35248 | 0.027466 | -0.15564 | -0.20599 | -0.13275 | -0.30212 | 0.009155 | 0.19684 | 60.759 | 61.1069 | 122.7493 | 122.9095 | -0.15564 | 122.8912 | 60.9695 | -0.30212 | 122.9095 | -0.15564 | 60.9695 | 122.7493 | 122.8912 | -123.2346 | -123.1842
2080.7656 | 123.2254 | -60.8734 | 62.027 | -0.04982 | -0.008216 | -0.014548 | 0.00071144 | 0.060105 | -0.0045821 | 0.066556 | -61.0107 | 62.0636 | -61.2076 | -61.0611 | 61.8576 | 0.086975 | -0.09613 | 0.23346 | 62.0773 | -61.1206 | -0.33417 | 0.036621 | -0.13733 | -0.18768 | -0.16937 | -0.24719 | 0.050354 | 0.19684 | 60.7773 | 61.1069 | 122.731 | 122.937 | -0.13733 | 122.9507 | 60.9604 | -0.24719 | 122.937 | -0.13733 | 60.9604 | 122.731 | 122.9507 | -123.2346 | -123.1476
2081.7656 | 123.2162 | -60.8826 | 62.0544 | 0.034104 | -0.0080024 | -0.013907 | 0.0034884 | 0.059037 | -0.0047957 | 0.066129 | -61.0336 | 62.059 | -61.1801 | -61.0886 | 61.8393 | 0.059509 | -0.082397 | 0.19684 | 62.0407 | -61.1435 | -0.29755 | 0.004578 | -0.15106 | -0.20599 | -0.21515 | -0.26093 | -0.013733 | 0.14648 | 60.8002 | 61.0794 | 122.7219 | 122.9416 | -0.15106 | 122.9233 | 60.9421 | -0.26093 | 122.9416 | -0.15106 | 60.9421 | 122.7219 | 122.9233 | -123.2346 | -123.1979
2082.7656 | 123.2208 | -60.8871 | 62.0499 | -0.18715 | -0.008216 | -0.014761 | 7.0444e-05 | 0.059464 | -0.0041549 | 0.065916 | -61.0794 | 62.0407 | -61.1893 | -61.116 | 61.8301 | 0.032043 | -0.073242 | 0.17853 | 62.0728 | -61.1481 | -0.30212 | -0.009156 | -0.19226 | -0.22888 | -0.21973 | -0.26093 | 0.022888 | 0.10986 | 60.8139 | 61.0657 | 122.7173 | 122.9279 | -0.19226 | 122.9599 | 60.9192 | -0.26093 | 122.9279 | -0.19226 | 60.9192 | 122.7173 | 122.9599 | -123.2391 | -123.1979
2083.7656 | 123.2071 | -60.9055 | 62.0224 | 0.14092 | -0.0080024 | -0.010062 | 7.0444e-05 | 0.058823 | -0.0018051 | 0.065702 | -61.0519 | 62.059 | -61.2122 | -61.1069 | 62.0316 | 0.1236 | -0.13275 | 0.17395 | 62.0544 | -61.116 | -0.3067 | 0.036621 | -0.14648 | -0.20142 | 0.009155 | -0.21057 | 0.032043 | 0.16022 | 60.7727 | 61.0794 | 122.937 | 122.9645 | -0.14648 | 122.9599 | 61.0291 | -0.21057 | 122.9645 | -0.14648 | 61.0291 | 122.937 | 122.9599 | -123.2346 | -123.1384
2084.7656 | 123.1796 | -60.8917 | 61.9904 | 0.12566 | -0.0056524 | -0.012198 | 7.0444e-05 | 0.059037 | -0.0052231 | 0.067411 | -61.0474 | 62.0636 | -61.1801 | -61.1252 | 61.8164 | 0 | -0.09613 | 0.14648 | 62.1048 | -61.116 | -0.28839 | 0.073243 | -0.15564 | -0.23346 | -0.17395 | -0.2243 | 0.11444 | 0.13275 | 60.7956 | 61.0382 | 122.7081 | 122.9553 | -0.15564 | 122.9965 | 60.8917 | -0.2243 | 122.9553 | -0.15564 | 60.8917 | 122.7081 | 122.9965 | -123.1705 | -123.1064
2085.7656 | 123.1888 | -60.91 | 62.0087 | 0.17906 | -0.008216 | -0.011984 | 0.0011386 | 0.057755 | -0.0067185 | 0.065488 | -61.0565 | 62.0544 | -61.2076 | -61.0931 | 61.8256 | 0.018311 | -0.09613 | 0.13733 | 62.0178 | -61.1389 | -0.29755 | 0.045776 | -0.14648 | -0.18311 | -0.18311 | -0.22888 | 0.009155 | 0.15106 | 60.8139 | 61.0474 | 122.7356 | 122.9645 | -0.14648 | 122.9279 | 60.9283 | -0.22888 | 122.9645 | -0.14648 | 60.9283 | 122.7356 | 122.9279 | -123.2162 | -123.1476
2086.7656 | 123.2483 | -60.8688 | 62.0453 | 0.087509 | -0.008216 | -0.011984 | 0.00049764 | 0.059251 | -0.0041549 | 0.06677 | -61.0291 | 62.0682 | -61.203 | -61.1114 | 61.8256 | 0.036621 | -0.09613 | 0.16022 | 62.0636 | -61.1481 | -0.33417 | 0.022888 | -0.16022 | -0.24262 | -0.21973 | -0.27924 | 0.018311 | 0.17395 | 60.7727 | 61.0291 | 122.6944 | 122.937 | -0.16022 | 122.9324 | 60.9055 | -0.27924 | 122.937 | -0.16022 | 60.9055 | 122.6944 | 122.9324 | -123.2483 | -123.1934
2087.7656 | 123.1796 | -60.9055 | 62.0132 | 0.1104 | -0.0097114 | -0.011984 | -0.00099756 | 0.058182 | -0.0035141 | 0.067624 | -61.0519 | 62.0819 | -61.2213 | -61.116 | 61.821 | 0.022888 | -0.11444 | 0.15106 | 62.059 | -61.1664 | -0.31586 | 0.068664 | -0.14648 | -0.21057 | -0.19226 | -0.26093 | 0.045776 | 0.16937 | 60.791 | 61.0565 | 122.7264 | 122.9874 | -0.14648 | 122.9645 | 60.9283 | -0.26093 | 122.9874 | -0.14648 | 60.9283 | 122.7264 | 122.9645 | -123.2346 | -123.1796
2088.7656 | 123.2025 | -60.8917 | 62.0132 | 0.20195 | -0.0054388 | -0.0083527 | -0.00035676 | 0.060319 | -0.0050095 | 0.067411 | -61.0336 | 62.0499 | -61.1893 | -61.1206 | 61.821 | 0.022888 | -0.10529 | 0.15564 | 62.059 | -61.1389 | -0.29755 | 0.036621 | -0.14191 | -0.22888 | -0.19226 | -0.24719 | 0.045776 | 0.15564 | 60.7864 | 61.0474 | 122.7127 | 122.9416 | -0.14191 | 122.9507 | 60.9146 | -0.24719 | 122.9416 | -0.14191 | 60.9146 | 122.7127 | 122.9507 | -123.2025 | -123.1522
2089.7656 | 123.1705 | -60.8963 | 62.0132 | 0.21721 | -0.0062934 | -0.010916 | 0.0017794 | 0.057542 | -0.0052231 | 0.068479 | -61.0336 | 62.0636 | -61.1938 | -61.1069 | 61.821 | 0.022888 | -0.10529 | 0.16479 | 62.0453 | -61.1618 | -0.29755 | 0.050354 | -0.13733 | -0.21057 | -0.19226 | -0.2655 | 0.032043 | 0.16022 | 60.791 | 61.0611 | 122.7173 | 122.9599 | -0.13733 | 122.9416 | 60.9192 | -0.2655 | 122.9599 | -0.13733 | 60.9192 | 122.7173 | 122.9416 | -123.2071 | -123.175
2090.7656 | 123.1888 | -60.8643 | 62.0132 | 0.19432 | -0.006507 | -0.010062 | 0.00092504 | 0.061173 | -0.0052231 | 0.065061 | -61.0153 | 62.0361 | -61.1847 | -61.1069 | 61.8118 | 0.013733 | -0.15564 | 0.16022 | 62.0453 | -61.1572 | -0.32043 | 0.022888 | -0.15106 | -0.24262 | -0.20142 | -0.29297 | 0.032043 | 0.16937 | 60.7086 | 61.0245 | 122.6761 | 122.9004 | -0.15106 | 122.9095 | 60.878 | -0.29297 | 122.9004 | -0.15106 | 60.878 | 122.6761 | 122.9095 | -123.1979 | -123.1705
2091.7656 | 123.1888 | -60.8826 | 61.9995 | 0.18669 | -0.005866 | -0.013907 | 0.0013522 | 0.059464 | -0.0056503 | 0.069547 | -61.0016 | 62.0728 | -61.2122 | -61.0748 | 61.8393 | 0.041199 | -0.17395 | 0.15106 | 62.0453 | -61.1664 | -0.32959 | 0.073242 | -0.11902 | -0.19226 | -0.16022 | -0.28381 | 0.045776 | 0.21057 | 60.7086 | 61.0336 | 122.7219 | 122.9553 | -0.11902 | 122.9279 | 60.9238 | -0.28381 | 122.9553 | -0.11902 | 60.9238 | 122.7219 | 122.9279 | -123.2117 | -123.1659
2092.7656 | 123.1796 | -60.9146 | 62.027 | 0.20195 | -0.0069342 | -0.010489 | 0.0024202 | 0.059251 | -0.0067185 | 0.06677 | -61.0291 | 62.0544 | -61.1984 | -61.1206 | 61.8393 | 0.009155 | -0.11444 | 0.15106 | 62.059 | -61.1252 | -0.28381 | 0.027465 | -0.11444 | -0.20599 | -0.18768 | -0.21057 | 0.032043 | 0.16937 | 60.8002 | 61.0657 | 122.7539 | 122.9691 | -0.11444 | 122.9736 | 60.9238 | -0.21057 | 122.9691 | -0.11444 | 60.9238 | 122.7539 | 122.9736 | -123.2254 | -123.1522
2093.7656 | 123.1888 | -60.8917 | 61.9904 | 0.19432 | -0.0056524 | -0.010916 | 0.001993 | 0.058396 | -0.0047957 | 0.067197 | -61.0474 | 62.059 | -61.1938 | -61.1252 | 61.8256 | 0.018311 | -0.1236 | 0.14191 | 62.0407 | -61.1618 | -0.30212 | 0.068665 | -0.15564 | -0.23346 | -0.16479 | -0.27008 | 0.050354 | 0.14649 | 60.7681 | 61.0336 | 122.7173 | 122.9507 | -0.15564 | 122.9324 | 60.91 | -0.27008 | 122.9507 | -0.15564 | 60.91 | 122.7173 | 122.9324 | -123.1842 | -123.1522
2094.7656 | 123.1842 | -60.8734 | 61.9904 | 0.2401 | -0.0088568 | -0.011343 | 0.0024202 | 0.059891 | -0.0060775 | 0.066343 | -61.0153 | 62.059 | -61.1938 | -61.1069 | 61.8347 | 0.036621 | -0.15106 | 0.14191 | 62.0361 | -61.1343 | -0.32044 | 0.068665 | -0.14191 | -0.23346 | -0.15564 | -0.26093 | 0.045777 | 0.17853 | 60.7224 | 61.0153 | 122.7081 | 122.9324 | -0.14191 | 122.9095 | 60.91 | -0.26093 | 122.9324 | -0.14191 | 60.91 | 122.7081 | 122.9095 | -123.1842 | -123.1247
2095.7656 | 123.1888 | -60.9009 | 62.0224 | 0.22484 | -0.0086432 | -0.0096343 | 0.0022066 | 0.059464 | -0.0060775 | 0.068052 | -61.0062 | 62.0316 | -61.1938 | -61.0886 | 61.8347 | 0.036621 | -0.17395 | 0.15106 | 62.0499 | -61.1435 | -0.29297 | 0.009155 | -0.10529 | -0.18768 | -0.18768 | -0.24261 | 0.027466 | 0.18768 | 60.7269 | 61.0519 | 122.7356 | 122.9324 | -0.10529 | 122.9507 | 60.9375 | -0.24261 | 122.9324 | -0.10529 | 60.9375 | 122.7356 | 122.9507 | -123.2162 | -123.1659
2096.7656 | 123.1934 | -60.9055 | 61.9949 | 0.20195 | -0.0069342 | -0.0051483 | 0.0024202 | 0.060532 | -0.0045821 | 0.067838 | -60.997 | 62.0773 | -61.1847 | -61.0977 | 61.853 | 0.036621 | -0.16479 | 0.16937 | 62.059 | -61.1572 | -0.27923 | 0.082398 | -0.091552 | -0.19226 | -0.14191 | -0.25177 | 0.064087 | 0.18768 | 60.7407 | 61.0748 | 122.7585 | 122.9828 | -0.091552 | 122.9645 | 60.9421 | -0.25177 | 122.9828 | -0.091552 | 60.9421 | 122.7585 | 122.9645 | -123.1796 | -123.1522
2097.7656 | 123.2208 | -60.8734 | 62.0041 | 0.27824 | -0.0050116 | -0.0098479 | 0.0056246 | 0.060105 | -0.0056503 | 0.066984 | -60.9787 | 62.0499 | -61.2122 | -61.0703 | 61.853 | 0.041199 | -0.20142 | 0.15564 | 62.027 | -61.1755 | -0.33875 | 0.045777 | -0.10529 | -0.19684 | -0.15106 | -0.30212 | 0.022889 | 0.23346 | 60.672 | 61.0291 | 122.7264 | 122.9233 | -0.10529 | 122.9004 | 60.9146 | -0.30212 | 122.9233 | -0.10529 | 60.9146 | 122.7264 | 122.9004 | -123.2162 | -123.1796
2098.7656 | 123.2117 | -60.8826 | 61.9995 | 0.018845 | -0.009284 | -0.0079253 | 0.0015658 | 0.060746 | -0.0060775 | 0.066556 | -60.9833 | 62.0636 | -61.171 | -61.0886 | 61.8484 | 0.036621 | -0.18768 | 0.16937 | 62.0407 | -61.1618 | -0.28839 | 0.064087 | -0.10071 | -0.20599 | -0.15106 | -0.27924 | 0.041198 | 0.18768 | 60.6949 | 61.0519 | 122.731 | 122.9462 | -0.10071 | 122.9233 | 60.9192 | -0.27924 | 122.9462 | -0.10071 | 60.9192 | 122.731 | 122.9233 | -123.1705 | -123.1613
2099.7656 | 123.175 | -60.8917 | 62.0087 | 0.19432 | -0.006507 | -0.0062163 | 0.0011386 | 0.058396 | -0.0039413 | 0.069547 | -61.0062 | 62.0728 | -61.1847 | -61.1069 | 61.8301 | 0.027466 | -0.15564 | 0.15564 | 62.0224 | -61.1664 | -0.29297 | 0.064087 | -0.11444 | -0.21515 | -0.17853 | -0.27466 | 0.013733 | 0.17853 | 60.7361 | 61.0474 | 122.7219 | 122.9645 | -0.11444 | 122.9141 | 60.9192 | -0.27466 | 122.9645 | -0.11444 | 60.9192 | 122.7219 | 122.9141 | -123.1934 | -123.175
2100.7656 | 123.2254 | -60.878 | 61.9858 | 0.22484 | -0.0054388 | -0.0060027 | 0.0047702 | 0.0616 | -0.0082137 | 0.068906 | -61.0153 | 62.0544 | -61.203 | -61.1023 | 61.8393 | 0.036621 | -0.17395 | 0.16937 | 62.0682 | -61.1298 | -0.32501 | 0.068664 | -0.13733 | -0.2243 | -0.14648 | -0.25177 | 0.082397 | 0.18768 | 60.704 | 61.0474 | 122.7173 | 122.9324 | -0.13733 | 122.9462 | 60.9146 | -0.25177 | 122.9324 | -0.13733 | 60.9146 | 122.7173 | 122.9462 | -123.1888 | -123.1155
2101.7656 | 123.175 | -60.8643 | 61.9858 | 0.17143 | -0.0069342 | -0.0085663 | 0.0024202 | 0.060319 | -0.0050095 | 0.067197 | -60.9787 | 62.059 | -61.2122 | -61.1023 | 61.8622 | 0.036621 | -0.19226 | 0.17395 | 62.0132 | -61.1755 | -0.3479 | 0.073242 | -0.11444 | -0.23804 | -0.1236 | -0.31128 | 0.027466 | 0.23346 | 60.672 | 61.0382 | 122.7264 | 122.9233 | -0.11444 | 122.8775 | 60.9009 | -0.31128 | 122.9233 | -0.11444 | 60.9009 | 122.7264 | 122.8775 | -123.1979 | -123.1613
2102.7656 | 123.23 | -60.8643 | 61.9812 | 0.26299 | -0.0067206 | -0.0094207 | 0.0041292 | 0.0616 | -0.0047957 | 0.066556 | -60.997 | 62.0773 | -61.2213 | -61.084 | 61.853 | 0.054932 | -0.1831 | 0.16479 | 62.0361 | -61.1755 | -0.35706 | 0.096131 | -0.13275 | -0.21973 | -0.12817 | -0.31128 | 0.054932 | 0.2243 | 60.6812 | 61.0291 | 122.7173 | 122.9416 | -0.13275 | 122.9004 | 60.9192 | -0.31128 | 122.9416 | -0.13275 | 60.9192 | 122.7173 | 122.9004 | -123.2025 | -123.1567
2103.7656 | 123.2162 | -60.8871 | 61.9995 | 0.1638 | -0.0050116 | -0.010489 | 0.0034884 | 0.061387 | -0.0065047 | 0.066343 | -60.9879 | 62.0499 | -61.2076 | -61.0977 | 61.8576 | 0.045776 | -0.18768 | 0.16937 | 62.0316 | -61.1664 | -0.32043 | 0.050354 | -0.10071 | -0.21057 | -0.14191 | -0.27924 | 0.032043 | 0.21973 | 60.6995 | 61.0565 | 122.7448 | 122.937 | -0.10071 | 122.9187 | 60.9329 | -0.27924 | 122.937 | -0.10071 | 60.9329 | 122.7448 | 122.9187 | -123.2071 | -123.1659
2104.7656 | 123.2208 | -60.8963 | 62.0041 | 0.34691 | -0.0028754 | -0.0074981 | 0.0064792 | 0.062241 | -0.0056503 | 0.067838 | -60.9879 | 62.0865 | -61.203 | -61.084 | 61.8439 | 0.041199 | -0.20142 | 0.15564 | 62.0544 | -61.1618 | -0.3067 | 0.082398 | -0.091553 | -0.18768 | -0.16022 | -0.2655 | 0.050354 | 0.21515 | 60.6949 | 61.0519 | 122.7402 | 122.9828 | -0.091553 | 122.9507 | 60.9375 | -0.2655 | 122.9828 | -0.091553 | 60.9375 | 122.7402 | 122.9507 | -123.2071 | -123.1659
2105.7656 | 123.2254 | -60.9009 | 61.9949 | 0.2401 | -0.005866 | -0.0083527 | 0.0058382 | 0.060105 | -0.0045821 | 0.069333 | -60.997 | 62.0544 | -61.203 | -61.0245 | 61.8759 | 0.064087 | -0.16479 | 0.19226 | 62.0316 | -61.1389 | -0.30212 | 0.059509 | -0.09613 | -0.1236 | -0.11902 | -0.23804 | 0.036621 | 0.20599 | 60.7361 | 61.0931 | 122.7768 | 122.9553 | -0.09613 | 122.9324 | 60.965 | -0.23804 | 122.9553 | -0.09613 | 60.965 | 122.7768 | 122.9324 | -123.1979 | -123.1338
2106.7812 | 123.262 | -60.8505 | 62.0316 | -0.19478 | -0.009284 | -0.013266 | -0.00014316 | 0.058396 | -0.0045821 | 0.068906 | -60.9879 | 62.1002 | -61.1801 | -61.0199 | 61.9125 | 0.14191 | -0.054932 | 0.3067 | 62.0316 | -61.1389 | -0.32959 | 0.068665 | -0.13733 | -0.16937 | -0.11902 | -0.28839 | 0 | 0.19226 | 60.7956 | 61.1572 | 122.7631 | 122.9507 | -0.13733 | 122.8821 | 60.9924 | -0.28839 | 122.9507 | -0.13733 | 60.9924 | 122.7631 | 122.8821 | -123.2117 | -123.1705
2107.7656 | 123.1796 | -60.8917 | 62.0087 | 0.19432 | -0.0073614 | -0.010489 | 0.0017794 | 0.05861 | -0.0045821 | 0.067197 | -61.0107 | 62.0773 | -61.1984 | -61.1069 | 61.8393 | 0.036621 | -0.16479 | 0.16937 | 62.0178 | -61.1938 | -0.3067 | 0.068665 | -0.11902 | -0.21515 | -0.16937 | -0.30212 | 0.009155 | 0.18768 | 60.7269 | 61.0611 | 122.731 | 122.9691 | -0.11902 | 122.9095 | 60.9283 | -0.30212 | 122.9691 | -0.11902 | 60.9283 | 122.731 | 122.9095 | -123.2071 | -123.2025
2108.7656 | 123.1934 | -60.8597 | 62.0224 | 0.19432 | -0.0069342 | -0.0079253 | 0.0039156 | 0.063096 | -0.0058639 | 0.066556 | -60.9833 | 62.0911 | -61.1938 | -61.1114 | 61.8484 | 0.041199 | -0.19226 | 0.16937 | 62.0407 | -61.1435 | -0.33417 | 0.068664 | -0.1236 | -0.25177 | -0.17395 | -0.28381 | 0.01831 | 0.21057 | 60.6674 | 61.0291 | 122.7081 | 122.9507 | -0.1236 | 122.9004 | 60.9009 | -0.28381 | 122.9507 | -0.1236 | 60.9009 | 122.7081 | 122.9004 | -123.2162 | -123.1659
2109.7656 | 123.1934 | -60.9055 | 61.9949 | 0.22484 | -0.0043708 | -0.014548 | 0.0030612 | 0.059464 | -0.0071457 | 0.067838 | -60.9924 | 62.0544 | -61.2076 | -61.084 | 61.8484 | 0.032043 | -0.17853 | 0.17853 | 62.0407 | -61.1847 | -0.30212 | 0.059509 | -0.086975 | -0.17853 | -0.14648 | -0.27923 | 0.045776 | 0.21515 | 60.7269 | 61.084 | 122.7539 | 122.9599 | -0.086975 | 122.9462 | 60.9375 | -0.27923 | 122.9599 | -0.086975 | 60.9375 | 122.7539 | 122.9462 | -123.2025 | -123.1796
2110.7656 | 123.1979 | -60.8917 | 62.0178 | 0.24773 | -0.0062934 | -0.0064301 | 0.0034884 | 0.059678 | -0.0058639 | 0.067624 | -60.997 | 62.0728 | -61.1801 | -61.0931 | 61.8576 | 0.027466 | -0.19226 | 0.17395 | 62.027 | -61.1664 | -0.28839 | 0.054932 | -0.10528 | -0.20142 | -0.16022 | -0.27466 | 0.009156 | 0.18311 | 60.6995 | 61.0657 | 122.7493 | 122.9645 | -0.10528 | 122.9187 | 60.9192 | -0.27466 | 122.9645 | -0.10528 | 60.9192 | 122.7493 | 122.9187 | -123.1979 | -123.1842
2111.7812 | 123.2529 | -60.8505 | 62.0224 | -0.12611 | -0.0067206 | -0.0085663 | 0.0022066 | 0.059037 | -0.0062911 | 0.065488 | -60.9695 | 62.0956 | -61.171 | -60.9787 | 62.2009 | 0.42114 | -0.27466 | 0.28381 | 62.0453 | -61.1755 | -0.32043 | 0.073242 | -0.11902 | -0.12817 | 0.17853 | -0.32501 | 0.022888 | 0.20142 | 60.5759 | 61.1343 | 123.0515 | 122.9462 | -0.11902 | 122.8958 | 61.2717 | -0.32501 | 122.9462 | -0.11902 | 61.2717 | 123.0515 | 122.8958 | -123.1934 | -123.1979
2112.7656 | 123.2117 | -60.8871 | 62.0087 | 0.17143 | -0.0069342 | -0.015402 | 0.0056246 | 0.059464 | -0.0058639 | 0.067197 | -60.9741 | 62.0682 | -61.1847 | -61.0886 | 61.8484 | 0.045776 | -0.1831 | 0.17395 | 62.0453 | -61.1526 | -0.29755 | 0.059509 | -0.086975 | -0.20142 | -0.16022 | -0.2655 | 0.036621 | 0.21057 | 60.704 | 61.0611 | 122.7356 | 122.9553 | -0.086975 | 122.9324 | 60.9329 | -0.2655 | 122.9553 | -0.086975 | 60.9329 | 122.7356 | 122.9324 | -123.1934 | -123.1613
2113.7656 | 123.1934 | -60.8688 | 62.0041 | 0.21721 | -0.0069342 | -0.0089935 | 0.0028476 | 0.057755 | -0.0047957 | 0.068906 | -61.0199 | 62.059 | -61.2167 | -61.116 | 61.8393 | 0.004578 | -0.13733 | 0.15106 | 62.0544 | -61.1847 | -0.3479 | 0.054932 | -0.15106 | -0.24719 | -0.16479 | -0.31586 | 0.050354 | 0.19684 | 60.7315 | 61.0199 | 122.7081 | 122.9279 | -0.15106 | 122.9233 | 60.8734 | -0.31586 | 122.9279 | -0.15106 | 60.8734 | 122.7081 | 122.9233 | -123.2208 | -123.1888
2114.7656 | 123.1705 | -60.8963 | 61.9904 | 0.22484 | -0.006507 | -0.010062 | 0.0013522 | 0.05861 | -0.0054367 | 0.067624 | -61.0062 | 62.0682 | -61.1847 | -61.1114 | 61.8256 | 0.018311 | -0.14648 | 0.14648 | 62.0728 | -61.1526 | -0.28839 | 0.07782 | -0.10986 | -0.21515 | -0.16479 | -0.25635 | 0.082398 | 0.17853 | 60.7498 | 61.0428 | 122.7219 | 122.9645 | -0.10986 | 122.9691 | 60.9146 | -0.25635 | 122.9645 | -0.10986 | 60.9146 | 122.7219 | 122.9691 | -123.175 | -123.143
2115.7656 | 123.2025 | -60.9009 | 62.0178 | 0.18669 | -0.0052252 | -0.01113 | 0.0028476 | 0.057969 | -0.0056503 | 0.06912 | -61.0199 | 62.0682 | -61.203 | -61.1114 | 61.8164 | 0.018311 | -0.16022 | 0.14648 | 62.0316 | -61.1801 | -0.30212 | 0.050354 | -0.11902 | -0.21057 | -0.20142 | -0.27924 | 0.013733 | 0.18311 | 60.7407 | 61.0474 | 122.7173 | 122.9691 | -0.11902 | 122.9324 | 60.9192 | -0.27924 | 122.9691 | -0.11902 | 60.9192 | 122.7173 | 122.9324 | -123.2208 | -123.1979
2116.7812 | 123.1201 | -60.878 | 62.0865 | -0.17189 | -0.0052252 | -0.0081389 | 0.0028476 | 0.059037 | -0.0075729 | 0.065916 | -61.0016 | 62.114 | -61.203 | -61.0977 | 61.8393 | 0.073242 | 0.091553 | 0.21973 | 62.1277 | -61.1755 | -0.32501 | 0.027466 | -0.1236 | -0.21973 | -0.24719 | -0.29755 | 0.041199 | 0.20142 | 60.9695 | 61.0977 | 122.7173 | 122.9919 | -0.1236 | 123.0057 | 60.9512 | -0.29755 | 122.9919 | -0.1236 | 60.9512 | 122.7173 | 123.0057 | -123.2895 | -123.262
2117.7656 | 123.1842 | -60.9009 | 62.0361 | 0.18669 | -0.0073614 | -0.010703 | 0.002634 | 0.059464 | -0.0058639 | 0.067411 | -61.0062 | 62.059 | -61.1938 | -61.1114 | 61.8439 | 0.027466 | -0.17853 | 0.16479 | 62.0361 | -61.1664 | -0.29297 | 0.022888 | -0.10529 | -0.21057 | -0.19226 | -0.2655 | 0 | 0.18768 | 60.7224 | 61.0657 | 122.7448 | 122.9599 | -0.10529 | 122.937 | 60.9283 | -0.2655 | 122.9599 | -0.10529 | 60.9283 | 122.7448 | 122.937 | -123.23 | -123.2025
2118.7656 | 123.2391 | -60.8688 | 61.9995 | 0.27061 | -0.0060798 | -0.0060027 | 0.0056246 | 0.061387 | -0.0082137 | 0.071683 | -60.9741 | 62.0407 | -61.1801 | -61.2488 | 61.8576 | 0.10529 | -0.13733 | 0.21057 | 62.0773 | -61.1389 | -0.31128 | 0.041198 | -0.10529 | -0.37994 | -0.14191 | -0.27008 | 0.07782 | 0.20599 | 60.7315 | 61.0794 | 122.7264 | 122.9095 | -0.10529 | 122.9462 | 60.9741 | -0.27008 | 122.9095 | -0.10529 | 60.9741 | 122.7264 | 122.9462 | -123.1796 | -123.1384
2119.7656 | 123.2071 | -60.8871 | 61.9995 | 0.20958 | -0.0069342 | -0.010916 | 0.0030612 | 0.061173 | -0.0052231 | 0.06912 | -61.0153 | 62.0453 | -61.2167 | -61.1114 | 61.8439 | 0.041199 | -0.16937 | 0.16022 | 62.0361 | -61.1893 | -0.32959 | 0.045776 | -0.12817 | -0.2243 | -0.15564 | -0.30212 | 0.036621 | 0.20142 | 60.7178 | 61.0474 | 122.731 | 122.9324 | -0.12817 | 122.9233 | 60.9283 | -0.30212 | 122.9324 | -0.12817 | 60.9283 | 122.731 | 122.9233 | -123.2162 | -123.1888
2120.7656 | 123.1979 | -60.8917 | 62.0316 | 0.14854 | -0.007575 | -0.014761 | 0.0024202 | 0.059891 | -0.0084273 | 0.067624 | -61.0611 | 62.059 | -61.1938 | -61.1252 | 61.8393 | 0.009155 | -0.10071 | 0.15106 | 62.0865 | -61.1481 | -0.30212 | 0.027466 | -0.16937 | -0.23346 | -0.19226 | -0.25635 | 0.054932 | 0.13275 | 60.791 | 61.0428 | 122.731 | 122.9507 | -0.16937 | 122.9782 | 60.9009 | -0.25635 | 122.9507 | -0.16937 | 60.9009 | 122.731 | 122.9782 | -123.2254 | -123.1796
2121.7812 | 123.23 | -60.8414 | 62.0499 | -0.15663 | -0.0080024 | -0.010916 | 0.00071144 | 0.056046 | -0.0047957 | 0.06677 | -60.7727 | 62.1094 | -61.1526 | -61.084 | 61.908 | 0.1236 | -0.027466 | 0.32959 | 62.0544 | -61.1526 | -0.31128 | 0.059509 | 0.068665 | -0.24261 | -0.14191 | -0.31128 | 0.004577 | 0.37994 | 60.8139 | 61.171 | 122.7493 | 122.9507 | 0.068665 | 122.8958 | 60.965 | -0.31128 | 122.9507 | 0.068665 | 60.965 | 122.7493 | 122.8958 | -123.2025 | -123.2025
2122.7656 | 123.1934 | -60.8963 | 62.0178 | 0.18669 | -0.0073614 | -0.011557 | 0.001993 | 0.059678 | -0.0071457 | 0.067197 | -61.0382 | 62.0773 | -61.2122 | -61.1206 | 61.8301 | 0.004578 | -0.11902 | 0.14191 | 62.0636 | -61.1755 | -0.31586 | 0.05951 | -0.14191 | -0.2243 | -0.18768 | -0.27924 | 0.045777 | 0.17395 | 60.7773 | 61.0382 | 122.7264 | 122.9736 | -0.14191 | 122.9599 | 60.9009 | -0.27924 | 122.9736 | -0.14191 | 60.9009 | 122.7264 | 122.9599 | -123.23 | -123.1934
2123.7656 | 123.1888 | -60.8871 | 62.0224 | 0.20958 | -0.007575 | -0.013693 | 0.0022066 | 0.057969 | -0.0052231 | 0.066556 | -61.0336 | 62.0682 | -61.2076 | -61.1298 | 61.821 | 0.018311 | -0.12817 | 0.14648 | 62.0544 | -61.1847 | -0.32043 | 0.045776 | -0.14648 | -0.24262 | -0.20142 | -0.29755 | 0.032043 | 0.17395 | 60.759 | 61.0336 | 122.7081 | 122.9553 | -0.14648 | 122.9416 | 60.9055 | -0.29755 | 122.9553 | -0.14648 | 60.9055 | 122.7081 | 122.9416 | -123.23 | -123.2071
2124.7656 | 123.1659 | -60.8688 | 62.0178 | 0.095139 | -0.0071478 | -0.0094207 | 0.001993 | 0.060746 | -0.0062911 | 0.067197 | -61.0474 | 62.0682 | -61.2122 | -61.1252 | 61.8118 | 0.013733 | -0.073242 | 0.20142 | 62.0773 | -61.1481 | -0.34332 | 0.050354 | -0.17853 | -0.25635 | -0.20599 | -0.27924 | 0.05951 | 0.1648 | 60.7956 | 61.0703 | 122.6807 | 122.937 | -0.17853 | 122.9462 | 60.8826 | -0.27924 | 122.937 | -0.17853 | 60.8826 | 122.6807 | 122.9462 | -123.23 | -123.1659
2125.7656 | 123.2346 | -60.8963 | 62.0087 | 0.13329 | -0.007575 | -0.0089935 | 0.0028476 | 0.060105 | -0.0067185 | 0.068052 | -60.9879 | 62.0773 | -61.2122 | -61.084 | 61.8484 | 0.041199 | -0.20599 | 0.16937 | 62.027 | -61.1572 | -0.31586 | 0.068665 | -0.091553 | -0.18768 | -0.16022 | -0.26093 | 0.018311 | 0.2243 | 60.6903 | 61.0657 | 122.7448 | 122.9736 | -0.091553 | 122.9233 | 60.9375 | -0.26093 | 122.9736 | -0.091553 | 60.9375 | 122.7448 | 122.9233 | -123.2208 | -123.1659
2126.7656 | 123.1842 | -60.9146 | 62.0224 | 0.21721 | -0.0071478 | -0.011343 | 0.0013522 | 0.059464 | -0.0037277 | 0.068479 | -61.0382 | 62.0224 | -61.2076 | -61.1252 | 61.8164 | 0.018311 | -0.14191 | 0.15564 | 62.0773 | -61.1389 | -0.29297 | 0 | -0.1236 | -0.21057 | -0.20599 | -0.2243 | 0.054932 | 0.16937 | 60.7727 | 61.0703 | 122.731 | 122.937 | -0.1236 | 122.9919 | 60.9329 | -0.2243 | 122.937 | -0.1236 | 60.9329 | 122.731 | 122.9919 | -123.23 | -123.1613
2127.7656 | 123.1705 | -60.878 | 62.027 | 0.07988 | -0.0073614 | -0.011771 | 0.0011386 | 0.058823 | -0.0065047 | 0.065702 | -61.0565 | 62.059 | -61.1938 | -61.1206 | 61.8347 | 0.022888 | -0.091553 | 0.16479 | 62.0499 | -61.1526 | -0.31586 | 0.032043 | -0.17853 | -0.24261 | -0.19226 | -0.27466 | 0.022888 | 0.13733 | 60.7864 | 61.0428 | 122.7127 | 122.937 | -0.17853 | 122.9279 | 60.9009 | -0.27466 | 122.937 | -0.17853 | 60.9009 | 122.7127 | 122.9279 | -123.2208 | -123.1796
2128.7656 | 123.1796 | -60.9055 | 62.027 | 0.17143 | -0.0090704 | -0.0081389 | 0.0013522 | 0.060532 | -0.0073593 | 0.06677 | -61.0382 | 62.0544 | -61.1984 | -61.116 | 61.821 | 0.032043 | -0.091553 | 0.15564 | 62.0865 | -61.1847 | -0.29297 | 0.027465 | -0.13275 | -0.21057 | -0.20599 | -0.27923 | 0.059509 | 0.16022 | 60.8139 | 61.0611 | 122.7264 | 122.9599 | -0.13275 | 122.9919 | 60.9375 | -0.27923 | 122.9599 | -0.13275 | 60.9375 | 122.7264 | 122.9919 | -123.2254 | -123.2117
2129.7656 | 123.1796 | -60.8963 | 61.972 | 0.23247 | -0.0052252 | -0.0060027 | 0.0022066 | 0.06096 | -0.0047957 | 0.066556 | -60.997 | 62.0499 | -61.2122 | -61.0977 | 61.8256 | 0.027466 | -0.17395 | 0.15564 | 62.0316 | -61.1755 | -0.31586 | 0.07782 | -0.10071 | -0.20142 | -0.14648 | -0.27924 | 0.059509 | 0.21515 | 60.7224 | 61.0519 | 122.7219 | 122.9462 | -0.10071 | 122.9279 | 60.9238 | -0.27924 | 122.9462 | -0.10071 | 60.9238 | 122.7219 | 122.9279 | -123.1842 | -123.1476
2130.7656 | 123.1934 | -60.8826 | 62.0407 | 0.17906 | -0.004798 | -0.0070709 | 0.0022066 | 0.059891 | -0.0082137 | 0.068052 | -60.9924 | 62.0453 | -61.1984 | -61.0748 | 61.8439 | 0.036621 | -0.17395 | 0.17395 | 62.0636 | -61.1572 | -0.31586 | 0.004578 | -0.10986 | -0.19226 | -0.19684 | -0.27466 | 0.022889 | 0.20599 | 60.7086 | 61.0565 | 122.7264 | 122.9279 | -0.10986 | 122.9462 | 60.9192 | -0.27466 | 122.9279 | -0.10986 | 60.9192 | 122.7264 | 122.9462 | -123.2391 | -123.1979
2131.7656 | 123.2117 | -60.8734 | 61.9995 | 0.18669 | -0.0056524 | -0.0064301 | 0.0039156 | 0.05861 | -0.0065047 | 0.065702 | -60.997 | 62.0499 | -61.203 | -61.0886 | 61.8393 | 0.041199 | -0.16937 | 0.16022 | 62.0361 | -61.1755 | -0.32959 | 0.050354 | -0.1236 | -0.21515 | -0.16022 | -0.30212 | 0.036621 | 0.20599 | 60.704 | 61.0336 | 122.7127 | 122.9233 | -0.1236 | 122.9095 | 60.9146 | -0.30212 | 122.9233 | -0.1236 | 60.9146 | 122.7127 | 122.9095 | -123.2025 | -123.175
2132.7656 | 123.2025 | -60.8871 | 62.0224 | 0.24773 | -0.0073614 | -0.013266 | 0.0051974 | 0.060532 | -0.0047957 | 0.065702 | -60.997 | 62.0407 | -61.203 | -61.0794 | 61.8668 | 0.036621 | -0.19684 | 0.16937 | 62.027 | -61.1755 | -0.31586 | 0.01831 | -0.10986 | -0.19226 | -0.15564 | -0.28839 | 0.004578 | 0.20599 | 60.6903 | 61.0565 | 122.7539 | 122.9279 | -0.10986 | 122.9141 | 60.9238 | -0.28839 | 122.9279 | -0.10986 | 60.9238 | 122.7539 | 122.9141 | -123.2254 | -123.1979
2133.7656 | 123.1796 | -60.8917 | 62.0041 | 0.2401 | -0.0054388 | -0.0062163 | 0.0039156 | 0.059251 | -0.0050095 | 0.066984 | -61.0382 | 62.0361 | -61.203 | -61.1114 | 61.8301 | 0.013733 | -0.1236 | 0.15106 | 62.0407 | -61.1572 | -0.31128 | 0.032044 | -0.14648 | -0.21973 | -0.17395 | -0.2655 | 0.036621 | 0.1648 | 60.7681 | 61.0428 | 122.7219 | 122.9279 | -0.14648 | 122.9324 | 60.9055 | -0.2655 | 122.9279 | -0.14648 | 60.9055 | 122.7219 | 122.9324 | -123.2071 | -123.1613
2134.7656 | 123.1934 | -60.8871 | 62.0087 | 0.20958 | -0.0071478 | -0.011771 | 0.00092504 | 0.059678 | -0.0062911 | 0.067197 | -61.0199 | 62.0728 | -61.2076 | -61.1298 | 61.8393 | 0.027466 | -0.15564 | 0.14191 | 62.0636 | -61.1526 | -0.32043 | 0.064087 | -0.13275 | -0.24262 | -0.16937 | -0.2655 | 0.054932 | 0.18768 | 60.7315 | 61.0291 | 122.7264 | 122.9599 | -0.13275 | 122.9507 | 60.9146 | -0.2655 | 122.9599 | -0.13275 | 60.9146 | 122.7264 | 122.9507 | -123.2162 | -123.1613
2135.7656 | 123.2162 | -60.8734 | 62.0224 | 0.20958 | -0.0071478 | -0.013052 | 0.0047702 | 0.058823 | -0.0047957 | 0.066343 | -61.0016 | 62.0636 | -61.2167 | -61.1114 | 61.8393 | 0.018311 | -0.16479 | 0.15564 | 62.0407 | -61.1572 | -0.34332 | 0.041199 | -0.12817 | -0.23804 | -0.18311 | -0.28381 | 0.01831 | 0.21515 | 60.7086 | 61.0291 | 122.7127 | 122.937 | -0.12817 | 122.9141 | 60.8917 | -0.28381 | 122.937 | -0.12817 | 60.8917 | 122.7127 | 122.9141 | -123.2391 | -123.1796
2136.7656 | 123.1796 | -60.8688 | 62.0041 | 0.23247 | -0.0045844 | -0.012839 | 0.002634 | 0.060319 | -0.0043685 | 0.068052 | -61.0107 | 62.0544 | -61.1893 | -61.1023 | 61.8347 | 0.032043 | -0.17395 | 0.16022 | 62.059 | -61.1526 | -0.32044 | 0.050354 | -0.14191 | -0.23346 | -0.16937 | -0.28381 | 0.054932 | 0.17853 | 60.6949 | 61.0291 | 122.7036 | 122.9233 | -0.14191 | 122.9279 | 60.9009 | -0.28381 | 122.9233 | -0.14191 | 60.9009 | 122.7036 | 122.9279 | -123.1934 | -123.1567
2137.7656 | 123.2254 | -60.9009 | 62.0132 | 0.20195 | -0.007575 | -0.0085663 | 0.0022066 | 0.058823 | -0.0050095 | 0.067838 | -61.0016 | 62.0544 | -61.1984 | -61.0886 | 61.8393 | 0.036621 | -0.20599 | 0.16022 | 62.0453 | -61.1847 | -0.29755 | 0.041198 | -0.10071 | -0.18768 | -0.17395 | -0.28381 | 0.032043 | 0.19684 | 60.6949 | 61.0611 | 122.7402 | 122.9553 | -0.10071 | 122.9462 | 60.9375 | -0.28381 | 122.9553 | -0.10071 | 60.9375 | 122.7402 | 122.9462 | -123.2117 | -123.1979
2138.7656 | 123.175 | -60.8963 | 62.0087 | 0.19432 | -0.0062934 | -0.010703 | -0.00014316 | 0.06096 | -0.0067185 | 0.067411 | -61.0474 | 62.0682 | -61.2213 | -61.1206 | 61.8393 | 0.022888 | -0.14191 | 0.12817 | 62.059 | -61.1526 | -0.32501 | 0.059509 | -0.15106 | -0.2243 | -0.16937 | -0.25635 | 0.050354 | 0.17395 | 60.7544 | 61.0245 | 122.7356 | 122.9645 | -0.15106 | 122.9553 | 60.9192 | -0.25635 | 122.9645 | -0.15106 | 60.9192 | 122.7356 | 122.9553 | -123.23 | -123.1613
2139.7656 | 123.2437 | -60.8734 | 62.0087 | 0.20958 | -0.0067206 | -0.010703 | 0.0047702 | 0.057969 | -0.0054367 | 0.067838 | -61.0062 | 62.0636 | -61.1984 | -61.0886 | 61.8484 | 0.036621 | -0.17853 | 0.16937 | 62.0544 | -61.1755 | -0.32501 | 0.054932 | -0.13275 | -0.21515 | -0.16022 | -0.30212 | 0.045776 | 0.19226 | 60.6949 | 61.0428 | 122.7219 | 122.937 | -0.13275 | 122.9279 | 60.91 | -0.30212 | 122.937 | -0.13275 | 60.91 | 122.7219 | 122.9279 | -123.2071 | -123.1842
2140.7656 | 123.1705 | -60.8826 | 62.0041 | 0.20195 | -0.0050116 | -0.012625 | 0.00092504 | 0.060105 | -0.0045821 | 0.06677 | -61.0199 | 62.0728 | -61.1847 | -61.1298 | 61.8256 | 0.013733 | -0.15106 | 0.15106 | 62.0499 | -61.1664 | -0.30212 | 0.068665 | -0.13733 | -0.24719 | -0.17853 | -0.28381 | 0.045777 | 0.16479 | 60.7315 | 61.0336 | 122.7081 | 122.9553 | -0.13733 | 122.9324 | 60.8963 | -0.28381 | 122.9553 | -0.13733 | 60.8963 | 122.7081 | 122.9324 | -123.1888 | -123.1705
2141.7656 | 123.175 | -60.8734 | 62.0087 | 0.19432 | -0.0054388 | -0.010489 | 0.0015658 | 0.061173 | -0.0045821 | 0.067624 | -61.0153 | 62.0819 | -61.2122 | -61.116 | 61.8347 | -0.004578 | -0.15106 | 0.16022 | 62.0453 | -61.1572 | -0.33875 | 0.073242 | -0.14191 | -0.24262 | -0.17395 | -0.28381 | 0.036621 | 0.19684 | 60.7224 | 61.0336 | 122.7081 | 122.9553 | -0.14191 | 122.9187 | 60.8688 | -0.28381 | 122.9553 | -0.14191 | 60.8688 | 122.7081 | 122.9187 | -123.2208 | -123.1659
2142.7656 | 123.2071 | -60.8643 | 62.0087 | 0.23247 | -0.005866 | -0.0072845 | 0.002634 | 0.060319 | -0.0088547 | 0.066984 | -61.0062 | 62.059 | -61.203 | -61.1069 | 61.8484 | 0.036621 | -0.16937 | 0.15564 | 62.0499 | -61.1664 | -0.33875 | 0.050354 | -0.14191 | -0.24262 | -0.16022 | -0.30212 | 0.041199 | 0.19684 | 60.6949 | 61.0199 | 122.7127 | 122.9233 | -0.14191 | 122.9141 | 60.9009 | -0.30212 | 122.9233 | -0.14191 | 60.9009 | 122.7127 | 122.9141 | -123.2117 | -123.175
2143.7656 | 123.1934 | -60.8734 | 61.9995 | 0.20195 | -0.0071478 | -0.013052 | 0.0041292 | 0.057542 | -0.0058639 | 0.068052 | -60.997 | 62.0773 | -61.1938 | -61.0886 | 61.8393 | 0.036621 | -0.19226 | 0.1831 | 62.0407 | -61.1755 | -0.32044 | 0.07782 | -0.1236 | -0.21515 | -0.16022 | -0.30212 | 0.041198 | 0.19684 | 60.6812 | 61.0565 | 122.7127 | 122.9507 | -0.1236 | 122.9141 | 60.91 | -0.30212 | 122.9507 | -0.1236 | 60.91 | 122.7127 | 122.9141 | -123.1934 | -123.175
2144.7656 | 123.2117 | -60.9009 | 62.0041 | 0.25536 | -0.007575 | -0.0068573 | 0.0045566 | 0.06096 | -0.0047957 | 0.067838 | -60.9695 | 62.0728 | -61.203 | -61.0794 | 61.853 | 0.045776 | -0.19226 | 0.16937 | 62.0453 | -61.1572 | -0.30212 | 0.068665 | -0.068664 | -0.17853 | -0.15106 | -0.25635 | 0.041199 | 0.23346 | 60.7086 | 61.0703 | 122.7539 | 122.9736 | -0.068664 | 122.9462 | 60.9467 | -0.25635 | 122.9736 | -0.068664 | 60.9467 | 122.7539 | 122.9462 | -123.2071 | -123.1613
2145.7656 | 123.2071 | -60.8688 | 61.9904 | 0.21721 | -0.0050116 | -0.0064301 | 0.0075472 | 0.059891 | -0.0047957 | 0.068479 | -60.9879 | 62.1048 | -61.2167 | -61.0977 | 61.8484 | 0.036621 | -0.19684 | 0.14648 | 62.027 | -61.1755 | -0.3479 | 0.11444 | -0.11902 | -0.22888 | -0.14191 | -0.3067 | 0.036622 | 0.22888 | 60.672 | 61.0153 | 122.7173 | 122.9736 | -0.11902 | 122.8958 | 60.9055 | -0.3067 | 122.9736 | -0.11902 | 60.9055 | 122.7173 | 122.8958 | -123.2071 | -123.1659
2146.7656 | 123.2162 | -60.8688 | 62.0178 | 0.2935 | -0.0050116 | -0.0096343 | 0.005411 | 0.062455 | -0.0073593 | 0.06677 | -60.9833 | 62.0407 | -61.2259 | -61.1389 | 61.6379 | -0.059509 | -0.082397 | 0.21515 | 62.0453 | -61.1343 | -0.35706 | 0.022888 | -0.11444 | -0.27008 | -0.37994 | -0.2655 | 0.027466 | 0.24262 | 60.7864 | 61.084 | 122.5067 | 122.9095 | -0.11444 | 122.9141 | 60.8093 | -0.2655 | 122.9095 | -0.11444 | 60.8093 | 122.5067 | 122.9141 | -123.2437 | -123.1522
2147.7656 | 123.23 | -60.9009 | 61.9766 | 0.26299 | -0.0041572 | -0.0074981 | 0.0032748 | 0.060746 | -0.0056503 | 0.069974 | -60.997 | 62.0728 | -61.2122 | -61.0931 | 61.8576 | 0.045776 | -0.16937 | 0.17853 | 62.0636 | -61.2076 | -0.31128 | 0.09613 | -0.09613 | -0.19226 | -0.11902 | -0.3067 | 0.086975 | 0.21515 | 60.7315 | 61.0794 | 122.7585 | 122.9736 | -0.09613 | 122.9645 | 60.9467 | -0.3067 | 122.9736 | -0.09613 | 60.9467 | 122.7585 | 122.9645 | -123.1888 | -123.1842
2148.7656 | 123.2071 | -60.9192 | 61.9904 | 0.17143 | -0.008216 | -0.0057891 | 0.0039156 | 0.0616 | -0.0047957 | 0.066556 | -60.9695 | 62.0911 | -61.1984 | -61.0886 | 61.8622 | 0.050354 | -0.20142 | 0.1831 | 62.0499 | -61.1801 | -0.27924 | 0.10071 | -0.050354 | -0.16937 | -0.12817 | -0.26093 | 0.05951 | 0.22888 | 60.7178 | 61.1023 | 122.7814 | 123.0103 | -0.050354 | 122.9691 | 60.9695 | -0.26093 | 123.0103 | -0.050354 | 60.9695 | 122.7814 | 122.9691 | -123.1888 | -123.1705
2149.7656 | 123.2071 | -60.8917 | 61.9949 | 0.24773 | -0.0056524 | -0.0094207 | 0.0047702 | 0.059037 | -0.0077865 | 0.068479 | -60.965 | 62.0773 | -61.1847 | -61.0565 | 61.8805 | 0.050354 | -0.17395 | 0.18768 | 62.0682 | -61.1847 | -0.29297 | 0.082398 | -0.073242 | -0.16479 | -0.11444 | -0.29297 | 0.073242 | 0.21973 | 60.7178 | 61.0794 | 122.7722 | 122.9691 | -0.073242 | 122.9599 | 60.9421 | -0.29297 | 122.9691 | -0.073242 | 60.9421 | 122.7722 | 122.9599 | -123.1796 | -123.1796
2150.7656 | 123.262 | -60.8734 | 62.0041 | 0.27061 | -0.0050116 | -0.0057891 | 0.0049838 | 0.0616 | -0.0062911 | 0.069333 | -60.9741 | 62.1002 | -61.1938 | -61.084 | 61.8484 | 0.09613 | -0.42572 | 0.022888 | 62.0224 | -61.2167 | -0.32044 | 0.096131 | -0.10071 | -0.21057 | -0.15564 | -0.34332 | 0.018311 | 0.21973 | 60.4477 | 60.8963 | 122.7219 | 122.9736 | -0.10071 | 122.8958 | 60.9695 | -0.34332 | 122.9736 | -0.10071 | 60.9695 | 122.7219 | 122.8958 | -123.1979 | -123.2208
2151.7656 | 123.2346 | -60.8871 | 62.0041 | 0.23247 | -0.005866 | -0.0096343 | 0.0032748 | 0.059891 | -0.0058639 | 0.068906 | -60.9787 | 62.0911 | -61.2213 | -61.0977 | 61.8622 | 0.050354 | -0.20599 | 0.16937 | 62.059 | -61.1938 | -0.33417 | 0.086975 | -0.091553 | -0.21057 | -0.14191 | -0.3067 | 0.054932 | 0.24261 | 60.6812 | 61.0565 | 122.7493 | 122.9782 | -0.091553 | 122.9462 | 60.9375 | -0.3067 | 122.9782 | -0.091553 | 60.9375 | 122.7493 | 122.9462 | -123.2254 | -123.1979
2152.7656 | 123.1476 | -60.9238 | 62.0224 | 0.25536 | -0.003089 | -0.010062 | 0.0062656 | 0.061387 | -0.0060775 | 0.066343 | -61.0519 | 62.1368 | -61.2305 | -61.1526 | 61.7981 | -0.041199 | -0.09613 | 0.068665 | 62.0956 | -61.235 | -0.3067 | 0.11444 | -0.12817 | -0.22888 | -0.2243 | -0.31128 | 0.073242 | 0.17853 | 60.8276 | 60.9924 | 122.7219 | 123.0606 | -0.12817 | 123.0194 | 60.8826 | -0.31128 | 123.0606 | -0.12817 | 60.8826 | 122.7219 | 123.0194 | -123.2529 | -123.2574
2153.7656 | 123.23 | -60.8643 | 61.9995 | 0.23247 | -0.0039434 | -0.0094207 | 0.0058382 | 0.063523 | -0.0047957 | 0.067838 | -61.0107 | 62.114 | -61.2259 | -61.1298 | 61.8484 | 0.018311 | -0.15564 | 0.15106 | 62.0544 | -61.1664 | -0.36163 | 0.11444 | -0.14648 | -0.2655 | -0.15106 | -0.30212 | 0.054931 | 0.21515 | 60.7086 | 61.0153 | 122.7127 | 122.9782 | -0.14648 | 122.9187 | 60.8826 | -0.30212 | 122.9782 | -0.14648 | 60.8826 | 122.7127 | 122.9187 | -123.2254 | -123.1659
2154.7656 | 123.2071 | -60.8826 | 61.9904 | 0.27061 | -0.0052252 | -0.0081389 | 0.0039156 | 0.062241 | -0.0069321 | 0.067624 | -60.9833 | 62.0911 | -61.2259 | -61.0977 | 61.853 | 0.054932 | -0.19226 | 0.16937 | 62.0728 | -61.1893 | -0.34332 | 0.10071 | -0.10071 | -0.21515 | -0.13733 | -0.3067 | 0.082398 | 0.24262 | 60.6903 | 61.0519 | 122.7356 | 122.9736 | -0.10071 | 122.9553 | 60.9375 | -0.3067 | 122.9736 | -0.10071 | 60.9375 | 122.7356 | 122.9553 | -123.2162 | -123.1796
2155.7656 | 123.2117 | -60.9192 | 61.9949 | 0.25536 | -0.0056524 | -0.0062163 | 0.0032748 | 0.062241 | -0.0043685 | 0.068479 | -60.9924 | 62.114 | -61.2076 | -61.0977 | 61.8439 | 0.032043 | -0.21057 | 0.16937 | 62.0499 | -61.203 | -0.28839 | 0.11902 | -0.073243 | -0.17853 | -0.15106 | -0.28381 | 0.054932 | 0.21515 | 60.7086 | 61.0886 | 122.7631 | 123.0331 | -0.073243 | 122.9691 | 60.9512 | -0.28381 | 123.0331 | -0.073243 | 60.9512 | 122.7631 | 122.9691 | -123.2025 | -123.1979
2156.7656 | 123.2162 | -60.9283 | 62.0224 | 0.39269 | -0.0052252 | -0.0070709 | 0.0047702 | 0.063737 | -0.0039413 | 0.067197 | -61.0016 | 62.1231 | -61.2122 | -61.0886 | 61.8393 | 0.032043 | -0.1831 | 0.16479 | 62.0224 | -61.1755 | -0.28381 | 0.10071 | -0.073242 | -0.16022 | -0.18311 | -0.24719 | 0 | 0.21057 | 60.7452 | 61.0931 | 122.7676 | 123.0515 | -0.073242 | 122.9507 | 60.9604 | -0.24719 | 123.0515 | -0.073242 | 60.9604 | 122.7676 | 122.9507 | -123.2346 | -123.1979
2157.7656 | 123.23 | -60.9009 | 61.9904 | 0.27824 | -0.0015936 | -0.010916 | 0.0024202 | 0.0616 | -0.0060775 | 0.065702 | -61.0107 | 62.0956 | -61.1801 | -61.1069 | 61.7981 | -0.032043 | -0.15564 | 0.14191 | 62.0453 | -61.2213 | -0.27924 | 0.10529 | -0.10986 | -0.20599 | -0.19226 | -0.32043 | 0.054932 | 0.16937 | 60.7452 | 61.0428 | 122.699 | 122.9965 | -0.10986 | 122.9462 | 60.8688 | -0.32043 | 122.9965 | -0.10986 | 60.8688 | 122.699 | 122.9462 | -123.1705 | -123.2117
2158.7656 | 123.2117 | -60.91 | 62.027 | 0.24773 | -0.0035162 | -0.0085663 | 0.005411 | 0.061173 | -0.0067185 | 0.067624 | -61.0199 | 62.1414 | -61.2167 | -61.116 | 61.8118 | 0 | -0.16022 | 0.12817 | 62.0728 | -61.1893 | -0.3067 | 0.11444 | -0.10986 | -0.20599 | -0.21515 | -0.27924 | 0.045776 | 0.19684 | 60.7498 | 61.0382 | 122.7219 | 123.0515 | -0.10986 | 122.9828 | 60.91 | -0.27924 | 123.0515 | -0.10986 | 60.91 | 122.7219 | 122.9828 | -123.2437 | -123.2162
2159.7656 | 123.1384 | -60.9375 | 62.0499 | -1.7359 | -0.0054388 | -0.0072845 | 0.0058382 | 0.061814 | -0.0030869 | 0.067197 | -61.0428 | 62.178 | -61.2167 | -61.203 | 61.7523 | -0.054932 | -0.022888 | 0.050354 | 62.1185 | -61.2167 | -0.27924 | 0.12817 | -0.10529 | -0.2655 | -0.29755 | -0.27924 | 0.068664 | 0.17395 | 60.9146 | 60.9879 | 122.6898 | 123.1155 | -0.10529 | 123.056 | 60.8826 | -0.27924 | 123.1155 | -0.10529 | 60.8826 | 122.6898 | 123.056 | -123.2666 | -123.2666
2160.7656 | 123.1293 | -60.9055 | 62.0316 | 0.22484 | -0.0060798 | -0.0081389 | 0.0047702 | 0.063523 | -0.0043685 | 0.065488 | -61.0703 | 62.146 | -61.2259 | -61.171 | 61.7844 | -0.041199 | -0.091553 | 0.073242 | 62.0728 | -61.2167 | -0.32043 | 0.11444 | -0.16479 | -0.2655 | -0.24719 | -0.31128 | 0.041199 | 0.15564 | 60.8139 | 60.9787 | 122.6898 | 123.0515 | -0.16479 | 122.9782 | 60.8643 | -0.31128 | 123.0515 | -0.16479 | 60.8643 | 122.6898 | 122.9782 | -123.2574 | -123.2483
2161.7656 | 123.2346 | -60.9009 | 62.0041 | 0.2401 | -0.0062934 | -0.0077117 | 0.0028476 | 0.064378 | -0.0030869 | 0.065702 | -61.0062 | 62.1277 | -61.2259 | -61.1114 | 61.8256 | 0.004578 | -0.15564 | 0.14191 | 62.0819 | -61.2167 | -0.32501 | 0.1236 | -0.10529 | -0.21057 | -0.17853 | -0.31586 | 0.07782 | 0.21973 | 60.7452 | 61.0428 | 122.7264 | 123.0286 | -0.10529 | 122.9828 | 60.9055 | -0.31586 | 123.0286 | -0.10529 | 60.9055 | 122.7264 | 122.9828 | -123.23 | -123.2208
2162.7656 | 123.2025 | -60.9146 | 62.0132 | 0.24773 | -0.0045844 | -0.0098479 | 0.0047702 | 0.062028 | -0.0047957 | 0.069761 | -61.0336 | 62.1368 | -61.2076 | -61.1298 | 61.8164 | -0.004578 | -0.14191 | 0.1236 | 62.0819 | -61.2122 | -0.29297 | 0.1236 | -0.11902 | -0.21515 | -0.19684 | -0.29755 | 0.068664 | 0.17395 | 60.7727 | 61.0382 | 122.731 | 123.0515 | -0.11902 | 122.9965 | 60.91 | -0.29755 | 123.0515 | -0.11902 | 60.91 | 122.731 | 122.9965 | -123.2208 | -123.2254
2163.7656 | 123.1522 | -60.8963 | 61.9995 | 0.27061 | -0.0035162 | -0.0051483 | 0.004343 | 0.062669 | -0.0047957 | 0.064634 | -61.0519 | 62.1414 | -61.2259 | -61.171 | 61.8027 | -0.027466 | -0.11444 | 0.10529 | 62.0865 | -61.2396 | -0.32959 | 0.14191 | -0.15564 | -0.27466 | -0.19684 | -0.34332 | 0.086975 | 0.17395 | 60.7819 | 61.0016 | 122.699 | 123.0377 | -0.15564 | 122.9828 | 60.8688 | -0.34332 | 123.0377 | -0.15564 | 60.8688 | 122.699 | 122.9828 | -123.2254 | -123.2391
2164.7656 | 123.1613 | -60.91 | 62.0224 | 0.23247 | -0.0050116 | -0.0062163 | 0.0039156 | 0.062882 | -0.0045821 | 0.069333 | -61.0519 | 62.1597 | -61.2259 | -61.171 | 61.7661 | -0.027466 | -0.10071 | 0.091553 | 62.1048 | -61.2534 | -0.31586 | 0.13733 | -0.14191 | -0.26093 | -0.25635 | -0.34332 | 0.082397 | 0.17395 | 60.8093 | 61.0016 | 122.6761 | 123.0698 | -0.14191 | 123.0148 | 60.8826 | -0.34332 | 123.0698 | -0.14191 | 60.8826 | 122.6761 | 123.0148 | -123.2483 | -123.2758
2165.7656 | 123.1201 | -60.9329 | 62.0224 | 0.1638 | -0.004798 | -0.0072845 | 0.0056246 | 0.063309 | -0.0041549 | 0.067624 | -61.0519 | 62.1735 | -61.2442 | -61.1801 | 61.7661 | -0.050354 | -0.064087 | 0.064087 | 62.114 | -61.2213 | -0.31128 | 0.15106 | -0.11902 | -0.24719 | -0.25635 | -0.28839 | 0.091553 | 0.19226 | 60.8688 | 60.997 | 122.699 | 123.1064 | -0.11902 | 123.0469 | 60.8826 | -0.28839 | 123.1064 | -0.11902 | 60.8826 | 122.699 | 123.0469 | -123.2666 | -123.2437
2166.7656 | 123.0743 | -60.9329 | 62.0453 | 0.17143 | -0.004798 | -0.0070709 | 0.0062656 | 0.062455 | -0.0043685 | 0.066984 | -61.084 | 62.2009 | -61.2259 | -61.2122 | 61.7249 | -0.050354 | 0.004578 | 0.059509 | 62.1185 | -61.2305 | -0.29297 | 0.15564 | -0.15106 | -0.27924 | -0.32043 | -0.29755 | 0.073242 | 0.14191 | 60.9375 | 60.9924 | 122.6578 | 123.1338 | -0.15106 | 123.0515 | 60.8826 | -0.29755 | 123.1338 | -0.15106 | 60.8826 | 122.6578 | 123.0515 | -123.2712 | -123.2758
2167.7656 | 123.0927 | -60.9283 | 62.0361 | 2.3687 | -0.0054388 | -0.013052 | 0.004343 | 0.062882 | -0.0037277 | 0.066556 | -60.9009 | 62.1414 | -61.2625 | -61.1801 | 61.7523 | -0.059509 | -0.018311 | 0.045776 | 62.1048 | -61.235 | -0.33417 | 0.10529 | 0.027466 | -0.25177 | -0.28381 | -0.3067 | 0.068664 | 0.36163 | 60.91 | 60.9741 | 122.6807 | 123.0698 | 0.027466 | 123.0331 | 60.8688 | -0.3067 | 123.0698 | 0.027466 | 60.8688 | 122.6807 | 123.0331 | -123.2986 | -123.2712
2168.7656 | 123.1522 | -60.9283 | 62.0178 | 0.2401 | -0.0037298 | -0.0077117 | 0.0030612 | 0.063523 | -0.0058639 | 0.067838 | -61.0657 | 62.1735 | -61.2122 | -61.1755 | 61.7752 | -0.041199 | -0.09613 | 0.091553 | 62.1185 | -61.2442 | -0.28381 | 0.15564 | -0.13733 | -0.24719 | -0.24261 | -0.31586 | 0.10071 | 0.14648 | 60.8322 | 61.0199 | 122.7036 | 123.1018 | -0.13733 | 123.0469 | 60.8871 | -0.31586 | 123.1018 | -0.13733 | 60.8871 | 122.7036 | 123.0469 | -123.23 | -123.262
2169.7656 | 123.1293 | -60.9146 | 62.0361 | 0.19432 | -0.0035162 | -0.010062 | 0.004343 | 0.064591 | -0.0062911 | 0.068052 | -61.0519 | 62.1918 | -61.235 | -61.1893 | 61.7523 | -0.045776 | -0.07782 | 0.064087 | 62.1231 | -61.2167 | -0.32043 | 0.15564 | -0.13733 | -0.27466 | -0.28381 | -0.30212 | 0.086975 | 0.1831 | 60.8368 | 60.9787 | 122.6669 | 123.1064 | -0.13733 | 123.0377 | 60.8688 | -0.30212 | 123.1064 | -0.13733 | 60.8688 | 122.6669 | 123.0377 | -123.2712 | -123.2529
2170.7656 | 123.111 | -60.9329 | 62.0087 | 0.21721 | -0.0028754 | -0.010062 | 0.004343 | 0.062669 | -0.0037277 | 0.06677 | -61.0611 | 62.1689 | -61.2305 | -61.1893 | 61.7615 | -0.050354 | -0.054932 | 0.064087 | 62.0819 | -61.2625 | -0.29755 | 0.16022 | -0.12817 | -0.25635 | -0.24719 | -0.32959 | 0.073242 | 0.16937 | 60.878 | 60.997 | 122.6944 | 123.1018 | -0.12817 | 123.0148 | 60.8826 | -0.32959 | 123.1018 | -0.12817 | 60.8826 | 122.6944 | 123.0148 | -123.2391 | -123.2712
2171.7656 | 123.1201 | -60.91 | 62.027 | -0.057449 | -0.0050116 | -0.0096343 | 0.0051974 | 0.062028 | -0.0045821 | 0.066556 | -61.0703 | 62.1872 | -61.2305 | -61.1847 | 61.7523 | -0.050354 | -0.018311 | 0.050354 | 62.0911 | -61.2305 | -0.32043 | 0.16022 | -0.16022 | -0.27466 | -0.27466 | -0.32043 | 0.064086 | 0.16022 | 60.8917 | 60.9604 | 122.6624 | 123.0972 | -0.16022 | 123.0011 | 60.8597 | -0.32043 | 123.0972 | -0.16022 | 60.8597 | 122.6624 | 123.0011 | -123.2574 | -123.2574
2172.7656 | 123.1201 | -60.9467 | 62.0636 | 0.5529 | -0.0045844 | -0.010489 | 0.0024202 | 0.063309 | -0.0039413 | 0.066343 | -60.91 | 62.178 | -61.2213 | -61.1801 | 61.7569 | -0.082397 | -0.013733 | 0.054932 | 62.114 | -61.2396 | -0.27466 | 0.11444 | 0.036621 | -0.23346 | -0.3067 | -0.29297 | 0.050354 | 0.31128 | 60.9329 | 61.0016 | 122.7036 | 123.1247 | 0.036621 | 123.0606 | 60.8643 | -0.29297 | 123.1247 | 0.036621 | 60.8643 | 122.7036 | 123.0606 | -123.2849 | -123.3032
2173.7656 | 123.0652 | -60.9238 | 62.0407 | 0.11803 | -0.0020208 | -0.0060027 | 0.004343 | 0.062028 | -0.0033005 | 0.067411 | -61.0519 | 62.1918 | -61.2122 | -61.2167 | 61.7615 | -0.036621 | 0.032043 | 0.045776 | 62.1185 | -61.2488 | -0.28839 | 0.15106 | -0.12817 | -0.29297 | -0.27923 | -0.32501 | 0.07782 | 0.16022 | 60.9558 | 60.9695 | 122.6852 | 123.1155 | -0.12817 | 123.0423 | 60.8871 | -0.32501 | 123.1155 | -0.12817 | 60.8871 | 122.6852 | 123.0423 | -123.2529 | -123.2895
2174.7656 | 123.143 | -60.8963 | 62.0361 | 0.22484 | -0.0041572 | -0.0092071 | 0.0022066 | 0.06395 | -0.0030869 | 0.066984 | -61.0748 | 62.1735 | -61.2488 | -61.1938 | 61.7569 | -0.036621 | -0.059509 | 0.068665 | 62.1048 | -61.2579 | -0.35248 | 0.13733 | -0.17853 | -0.29755 | -0.27924 | -0.36163 | 0.068664 | 0.17395 | 60.8368 | 60.965 | 122.6532 | 123.0698 | -0.17853 | 123.0011 | 60.8597 | -0.36163 | 123.0698 | -0.17853 | 60.8597 | 122.6532 | 123.0011 | -123.2849 | -123.2941
2175.7656 | 123.143 | -60.9238 | 62.0499 | 0.2401 | -0.0033026 | -0.0077117 | 0.0047702 | 0.064164 | -0.0056503 | 0.068052 | -61.0519 | 62.1826 | -61.235 | -61.1984 | 61.7569 | -0.054932 | -0.032043 | 0.054932 | 62.1002 | -61.2579 | -0.31128 | 0.13275 | -0.12817 | -0.27466 | -0.29297 | -0.33417 | 0.050354 | 0.1831 | 60.8917 | 60.9787 | 122.6807 | 123.1064 | -0.12817 | 123.024 | 60.8688 | -0.33417 | 123.1064 | -0.12817 | 60.8688 | 122.6807 | 123.024 | -123.2849 | -123.3078
2176.7656 | 123.1338 | -60.9375 | 62.027 | -0.087967 | -0.0069342 | -0.0089935 | 0.00712 | 0.063096 | -0.0056503 | 0.068265 | -61.0794 | 62.2009 | -61.235 | -61.1984 | 61.7432 | -0.059509 | -0.018311 | 0.059509 | 62.146 | -61.2442 | -0.29755 | 0.17395 | -0.14191 | -0.26093 | -0.28381 | -0.3067 | 0.11902 | 0.15564 | 60.9192 | 60.997 | 122.6807 | 123.1384 | -0.14191 | 123.0835 | 60.878 | -0.3067 | 123.1384 | -0.14191 | 60.878 | 122.6807 | 123.0835 | -123.262 | -123.2712
2177.7656 | 123.1338 | -60.9283 | 62.027 | 0.22484 | -9.819e-05 | -0.0087799 | 0.0045566 | 0.061814 | -0.0024459 | 0.067838 | -61.3495 | 62.1231 | -61.2625 | -61.1618 | 61.7661 | -0.050354 | 0.013733 | 0.036621 | 62.1323 | -61.2534 | -0.33417 | 0.09613 | -0.42114 | -0.23346 | -0.26093 | -0.32501 | 0.10529 | -0.086975 | 60.9421 | 60.965 | 122.6944 | 123.0515 | -0.42114 | 123.0606 | 60.878 | -0.32501 | 123.0515 | -0.42114 | 60.878 | 122.6944 | 123.0606 | -123.2895 | -123.2803
2178.7656 | 123.1018 | -60.9329 | 62.0544 | 0.21721 | -0.0052252 | -0.010275 | 0.0049838 | 0.064378 | -0.0043685 | 0.073179 | -61.0611 | 62.1918 | -61.2305 | -61.4639 | 61.5143 | -0.036621 | 0.091553 | 0.10986 | 62.1689 | -61.2259 | -0.29755 | 0.13733 | -0.12817 | -0.53101 | -0.54016 | -0.29297 | 0.11444 | 0.16937 | 61.0245 | 61.0428 | 122.4472 | 123.1247 | -0.12817 | 123.1018 | 60.8963 | -0.29297 | 123.1247 | -0.12817 | 60.8963 | 122.4472 | 123.1018 | -123.2849 | -123.2803
2179.7656 | 123.1018 | -60.9375 | 62.0224 | 0.20958 | -0.0043708 | -0.0070709 | 0.0028476 | 0.064591 | -0.0026595 | 0.067197 | -61.084 | 62.1918 | -61.2625 | -61.2122 | 61.7569 | -0.064087 | -0.013733 | 0.050354 | 62.1368 | -61.2396 | -0.32501 | 0.16937 | -0.14648 | -0.27466 | -0.2655 | -0.30212 | 0.11444 | 0.17853 | 60.9238 | 60.9879 | 122.6944 | 123.1293 | -0.14648 | 123.0743 | 60.8734 | -0.30212 | 123.1293 | -0.14648 | 60.8734 | 122.6944 | 123.0743 | -123.2849 | -123.262
2180.7656 | 123.1018 | -60.9375 | 62.0636 | 0.18669 | -0.0035162 | -0.0098479 | 0.0051974 | 0.066087 | -0.0065047 | 0.066984 | -61.084 | 62.178 | -61.2625 | -61.2167 | 61.734 | -0.068665 | -0.009155 | 0.064087 | 62.1277 | -61.2534 | -0.32501 | 0.11444 | -0.14648 | -0.27924 | -0.32959 | -0.31586 | 0.064087 | 0.17853 | 60.9283 | 61.0016 | 122.6715 | 123.1155 | -0.14648 | 123.0652 | 60.8688 | -0.31586 | 123.1155 | -0.14648 | 60.8688 | 122.6715 | 123.0652 | -123.3261 | -123.317
2181.7656 | 123.0881 | -60.9375 | 62.0544 | 0.1104 | -0.0056524 | -0.011984 | 0.0066928 | 0.065446 | -0.0067185 | 0.066556 | -61.0382 | 62.2101 | -61.2213 | -61.2122 | 61.7386 | -0.064087 | 0.018311 | 0.068665 | 62.1368 | -61.2442 | -0.28381 | 0.15564 | -0.10071 | -0.27466 | -0.31586 | -0.3067 | 0.082398 | 0.18311 | 60.9558 | 61.0062 | 122.6761 | 123.1476 | -0.10071 | 123.0743 | 60.8734 | -0.3067 | 123.1476 | -0.10071 | 60.8734 | 122.6761 | 123.0743 | -123.2758 | -123.2986
2182.7656 | 123.1338 | -60.9375 | 62.0087 | 0.21721 | -0.0052252 | -0.011771 | 0.0017794 | 0.062455 | -0.0024459 | 0.068052 | -61.0611 | 62.178 | -61.2442 | -61.1847 | 61.7798 | -0.050354 | -0.082397 | 0.064087 | 62.1002 | -61.2396 | -0.3067 | 0.16937 | -0.1236 | -0.24719 | -0.22888 | -0.30212 | 0.091553 | 0.18311 | 60.8551 | 61.0016 | 122.7173 | 123.1155 | -0.1236 | 123.0377 | 60.8871 | -0.30212 | 123.1155 | -0.1236 | 60.8871 | 122.7173 | 123.0377 | -123.2529 | -123.2483
2183.7656 | 123.1018 | -60.9329 | 62.0361 | 0.14092 | -0.004798 | -0.0087799 | 0.0049838 | 0.060532 | -0.0028731 | 0.068052 | -61.0886 | 62.1964 | -61.2396 | -61.2076 | 61.7432 | -0.054932 | -0.009155 | 0.054932 | 62.1048 | -61.2717 | -0.3067 | 0.16022 | -0.15564 | -0.27466 | -0.29297 | -0.33875 | 0.068664 | 0.15106 | 60.9238 | 60.9879 | 122.6761 | 123.1293 | -0.15564 | 123.0377 | 60.878 | -0.33875 | 123.1293 | -0.15564 | 60.878 | 122.6761 | 123.0377 | -123.2758 | -123.3078
2184.7656 | 123.0972 | -60.9512 | 62.0361 | 0.1638 | -0.0024482 | -0.0045075 | 0.004343 | 0.063523 | -0.0052231 | 0.068693 | -61.084 | 62.2055 | -61.2396 | -61.2259 | 61.7294 | -0.082397 | 0.009155 | 0.054932 | 62.0865 | -61.2488 | -0.28839 | 0.16937 | -0.13275 | -0.27466 | -0.3067 | -0.29755 | 0.050354 | 0.15564 | 60.9604 | 61.0062 | 122.6807 | 123.1567 | -0.13275 | 123.0377 | 60.8688 | -0.29755 | 123.1567 | -0.13275 | 60.8688 | 122.6807 | 123.0377 | -123.2758 | -123.2849
2185.7656 | 123.0698 | -60.9375 | 62.0544 | 0.14092 | -0.0037298 | -0.0036529 | 0.0056246 | 0.063096 | -0.0039413 | 0.065702 | -61.0703 | 62.1918 | -61.2213 | -61.2122 | 61.734 | -0.054932 | 0.013733 | 0.036621 | 62.1414 | -61.2808 | -0.28381 | 0.13733 | -0.13275 | -0.27466 | -0.32043 | -0.34332 | 0.086975 | 0.15106 | 60.9512 | 60.9741 | 122.6715 | 123.1293 | -0.13275 | 123.0789 | 60.8826 | -0.34332 | 123.1293 | -0.13275 | 60.8826 | 122.6715 | 123.0789 | -123.2758 | -123.3353
2186.7656 | 123.0972 | -60.9055 | 62.059 | 0.087509 | -0.003089 | -0.0083527 | 0.0047702 | 0.065018 | -0.0039413 | 0.065702 | -61.0565 | 62.2192 | -61.2442 | -61.1984 | 61.7523 | -0.036621 | 0.018311 | 0.064087 | 62.1826 | -61.235 | -0.33875 | 0.16022 | -0.15106 | -0.29297 | -0.3067 | -0.32959 | 0.1236 | 0.18768 | 60.9238 | 60.9695 | 122.6578 | 123.1247 | -0.15106 | 123.0881 | 60.8688 | -0.32959 | 123.1247 | -0.15106 | 60.8688 | 122.6578 | 123.0881 | -123.3032 | -123.2941
2187.7656 | 123.0927 | -60.9283 | 62.027 | 0.10277 | -0.0041572 | -0.0089935 | 0.0077608 | 0.065659 | -0.0047957 | 0.066343 | -61.0336 | 62.1964 | -61.2167 | -61.1847 | 61.7569 | -0.032043 | 0.032043 | 0.09613 | 62.114 | -61.2488 | -0.28839 | 0.16937 | -0.10529 | -0.25635 | -0.27008 | -0.32043 | 0.086975 | 0.18311 | 60.9604 | 61.0245 | 122.6852 | 123.1247 | -0.10529 | 123.0423 | 60.8963 | -0.32043 | 123.1247 | -0.10529 | 60.8963 | 122.6852 | 123.0423 | -123.2437 | -123.2758
2188.7656 | 123.1247 | -60.9283 | 62.0361 | 0.095139 | -0.0035162 | -0.0053619 | 0.0045566 | 0.064164 | -0.0052231 | 0.067624 | -61.0245 | 62.2055 | -61.203 | -61.1664 | 61.7661 | -0.013733 | 0.032043 | 0.11444 | 62.1414 | -61.2625 | -0.27466 | 0.16937 | -0.09613 | -0.23804 | -0.27008 | -0.33417 | 0.10529 | 0.17853 | 60.9604 | 61.0428 | 122.6944 | 123.1338 | -0.09613 | 123.0698 | 60.9146 | -0.33417 | 123.1338 | -0.09613 | 60.9146 | 122.6944 | 123.0698 | -123.2391 | -123.2986
2189.7656 | 123.0881 | -60.9192 | 62.0453 | 0.1638 | -0.003089 | -0.0064301 | 0.0045566 | 0.063523 | -0.0058639 | 0.068479 | -61.0611 | 62.2192 | -61.2717 | -61.2213 | 61.734 | -0.059509 | 0.032043 | 0.050354 | 62.1323 | -61.2625 | -0.35248 | 0.17395 | -0.14191 | -0.30212 | -0.31128 | -0.34332 | 0.086975 | 0.21057 | 60.9512 | 60.9695 | 122.6532 | 123.1384 | -0.14191 | 123.0515 | 60.8597 | -0.34332 | 123.1384 | -0.14191 | 60.8597 | 122.6532 | 123.0515 | -123.317 | -123.3078
2190.7656 | 123.1018 | -60.9238 | 62.0911 | 0.24773 | -0.0037298 | -0.0068573 | 0.0056246 | 0.069291 | -0.0026595 | 0.067624 | -61.084 | 62.2101 | -61.2671 | -61.116 | 61.9583 | -0.022888 | 0.073242 | 0.059509 | 62.1368 | -61.2396 | -0.34332 | 0.11902 | -0.16022 | -0.19226 | -0.13275 | -0.31586 | 0.045777 | 0.18311 | 60.997 | 60.9833 | 122.8821 | 123.1338 | -0.16022 | 123.0606 | 60.9009 | -0.31586 | 123.1338 | -0.16022 | 60.9009 | 122.8821 | 123.0606 | -123.3582 | -123.3307
2191.7656 | 123.0881 | -60.9375 | 62.0407 | 0.10277 | -0.0041572 | -0.0068573 | 0.0079744 | 0.065232 | -0.0035141 | 0.067838 | -61.0336 | 62.2147 | -61.2488 | -61.1893 | 61.7615 | -0.032043 | 0.036621 | 0.068665 | 62.1323 | -61.2442 | -0.31128 | 0.17395 | -0.09613 | -0.25177 | -0.27923 | -0.3067 | 0.091553 | 0.21515 | 60.9741 | 61.0062 | 122.699 | 123.1522 | -0.09613 | 123.0698 | 60.9055 | -0.3067 | 123.1522 | -0.09613 | 60.9055 | 122.699 | 123.0698 | -123.2895 | -123.2849
2192.7656 | 123.1018 | -60.9375 | 62.0636 | 0.087509 | -0.0015936 | -0.0051483 | 0.0060518 | 0.064378 | -0.0056503 | 0.068693 | -61.0291 | 62.1872 | -61.235 | -61.1847 | 61.7752 | -0.018311 | 0.018311 | 0.091553 | 62.1323 | -61.2396 | -0.29755 | 0.1236 | -0.091553 | -0.24719 | -0.28839 | -0.30212 | 0.068664 | 0.20599 | 60.9558 | 61.0291 | 122.7127 | 123.1247 | -0.091553 | 123.0698 | 60.9192 | -0.30212 | 123.1247 | -0.091553 | 60.9192 | 122.7127 | 123.0698 | -123.2986 | -123.3032
2193.7656 | 123.1018 | -60.9238 | 62.0316 | 0.087509 | -0.0033026 | -0.0049347 | 0.0032748 | 0.062455 | -0.0041549 | 0.067624 | -61.0107 | 62.178 | -61.2305 | -61.1893 | 61.7661 | -0.004578 | 0.022888 | 0.10529 | 62.114 | -61.2534 | -0.3067 | 0.14649 | -0.086975 | -0.2655 | -0.2655 | -0.32959 | 0.082398 | 0.21973 | 60.9467 | 61.0291 | 122.6898 | 123.1018 | -0.086975 | 123.0377 | 60.9192 | -0.32959 | 123.1018 | -0.086975 | 60.9192 | 122.6898 | 123.0377 | -123.262 | -123.2849
2194.7656 | 123.1064 | -60.9055 | 62.0544 | 0.0035856 | -0.0043708 | -0.0049347 | 0.0062656 | 0.064164 | -0.0045821 | 0.065916 | -61.0199 | 62.2055 | -61.2122 | -61.1618 | 61.7844 | -0.004578 | 0.009155 | 0.13275 | 62.1231 | -61.235 | -0.3067 | 0.15106 | -0.11444 | -0.25635 | -0.27008 | -0.32959 | 0.068665 | 0.19226 | 60.9146 | 61.0382 | 122.6898 | 123.111 | -0.11444 | 123.0286 | 60.9009 | -0.32959 | 123.111 | -0.11444 | 60.9009 | 122.6898 | 123.0286 | -123.2666 | -123.2895
2195.7656 | 123.1293 | -60.9192 | 62.0499 | 0.026474 | -0.0033026 | -0.0077117 | 0.0058382 | 0.061814 | -0.0062911 | 0.068052 | -61.0062 | 62.2009 | -61.2213 | -61.1298 | 61.8027 | 0.032043 | 0.004578 | 0.14191 | 62.146 | -61.2671 | -0.30212 | 0.15106 | -0.086976 | -0.21057 | -0.24719 | -0.3479 | 0.09613 | 0.21515 | 60.9238 | 61.0611 | 122.7219 | 123.1201 | -0.086976 | 123.0652 | 60.9512 | -0.3479 | 123.1201 | -0.086976 | 60.9512 | 122.7219 | 123.0652 | -123.2712 | -123.317
2196.7656 | 123.1247 | -60.9467 | 62.0224 | 0.12566 | -0.0045844 | -0.0079253 | 0.0051974 | 0.064805 | -0.0060775 | 0.066129 | -61.0291 | 62.2009 | -61.2122 | -61.1984 | 61.7706 | -0.022888 | 0.036621 | 0.082397 | 62.1597 | -61.2625 | -0.2655 | 0.17853 | -0.082398 | -0.25177 | -0.25177 | -0.31586 | 0.13733 | 0.18311 | 60.9833 | 61.0291 | 122.7173 | 123.1476 | -0.082398 | 123.1064 | 60.9238 | -0.31586 | 123.1476 | -0.082398 | 60.9238 | 122.7173 | 123.1064 | -123.2346 | -123.2849
2197.7812 | 123.2071 | -60.9055 | 61.9858 | 0.24773 | -0.0056524 | -0.0068573 | 0.0032748 | 0.063523 | -0.0026595 | 0.066129 | -61.0107 | 62.1048 | -61.2122 | -61.1114 | 61.8439 | 0.050354 | -0.20142 | 0.17853 | 62.0819 | -61.1847 | -0.3067 | 0.11902 | -0.10529 | -0.20599 | -0.14191 | -0.27923 | 0.09613 | 0.20142 | 60.704 | 61.084 | 122.7493 | 123.0103 | -0.10529 | 122.9874 | 60.9558 | -0.27923 | 123.0103 | -0.10529 | 60.9558 | 122.7493 | 122.9874 | -123.1979 | -123.1705
2198.7656 | 123.111 | -60.9238 | 62.0178 | 0.095139 | -0.0035162 | -0.0038665 | 0.0058382 | 0.065446 | -0.0054367 | 0.065488 | -61.0474 | 62.1872 | -61.2213 | -61.2167 | 61.7386 | -0.068665 | 0.027466 | 0.045776 | 62.1643 | -61.2579 | -0.29755 | 0.16937 | -0.1236 | -0.29297 | -0.27924 | -0.33417 | 0.14648 | 0.17395 | 60.9512 | 60.9695 | 122.6624 | 123.111 | -0.1236 | 123.0881 | 60.8551 | -0.33417 | 123.111 | -0.1236 | 60.8551 | 122.6624 | 123.0881 | -123.2391 | -123.2758
2199.7656 | 123.1613 | -60.91 | 62.027 | 0.018845 | -0.0062934 | -0.0040801 | 0.0056246 | 0.063523 | -0.0052231 | 0.066343 | -60.9787 | 62.1826 | -61.2305 | -61.1526 | 61.7981 | 0.018311 | 0.004578 | 0.13733 | 62.1597 | -61.2259 | -0.32043 | 0.15564 | -0.068665 | -0.24261 | -0.22888 | -0.31586 | 0.13275 | 0.25177 | 60.9146 | 61.0474 | 122.7081 | 123.0927 | -0.068665 | 123.0698 | 60.9283 | -0.31586 | 123.0927 | -0.068665 | 60.9283 | 122.7081 | 123.0698 | -123.2574 | -123.2529
2200.7656 | 123.1476 | -60.9009 | 62.0773 | 0.07988 | -0.0045844 | -0.0027985 | 0.005411 | 0.062028 | -0.0056503 | 0.066129 | -61.0199 | 62.2055 | -61.2167 | -61.1298 | 61.8073 | 0.032043 | 0.022888 | 0.16022 | 62.1368 | -61.2488 | -0.31586 | 0.12817 | -0.11902 | -0.22888 | -0.27008 | -0.3479 | 0.059509 | 0.19684 | 60.9238 | 61.0611 | 122.7081 | 123.1064 | -0.11902 | 123.0377 | 60.9329 | -0.3479 | 123.1064 | -0.11902 | 60.9329 | 122.7081 | 123.0377 | -123.2941 | -123.3261
2201.7656 | 123.1567 | -60.91 | 62.0773 | 0.0035856 | -0.0060798 | -0.0092071 | 0.0062656 | 0.065873 | -0.0056503 | 0.069974 | -60.9879 | 62.1689 | -61.2213 | -61.1206 | 61.8027 | 0.041199 | 0.009155 | 0.1831 | 62.1414 | -61.235 | -0.31128 | 0.091552 | -0.07782 | -0.21057 | -0.27466 | -0.32501 | 0.064086 | 0.23346 | 60.9192 | 61.0931 | 122.7127 | 123.0789 | -0.07782 | 123.0515 | 60.9512 | -0.32501 | 123.0789 | -0.07782 | 60.9512 | 122.7127 | 123.0515 | -123.2986 | -123.3124
2202.7812 | 123.1979 | -60.8826 | 61.9949 | 0.36217 | -0.0050116 | -0.0070709 | 0.00028404 | 0.064591 | -0.0039413 | 0.068479 | -61.0107 | 62.1094 | -61.2167 | -61.1252 | 61.8301 | 0.045776 | -0.1831 | 0.15564 | 62.059 | -61.2122 | -0.33417 | 0.11444 | -0.12817 | -0.24262 | -0.16479 | -0.32959 | 0.064087 | 0.20599 | 60.6995 | 61.0382 | 122.7127 | 122.9919 | -0.12817 | 122.9416 | 60.9283 | -0.32959 | 122.9919 | -0.12817 | 60.9283 | 122.7127 | 122.9416 | -123.2117 | -123.2071
2203.7656 | 123.1201 | -60.9055 | 62.0544 | -0.065079 | -0.003089 | -0.0064301 | 0.0060518 | 0.060105 | -0.0045821 | 0.067838 | -60.997 | 62.2192 | -61.203 | -61.1481 | 61.8073 | 0.018311 | 0.027466 | 0.16022 | 62.1231 | -61.2762 | -0.29755 | 0.16479 | -0.091552 | -0.24261 | -0.24719 | -0.37079 | 0.068665 | 0.20599 | 60.9329 | 61.0657 | 122.7127 | 123.1247 | -0.091552 | 123.0286 | 60.9238 | -0.37079 | 123.1247 | -0.091552 | 60.9238 | 122.7127 | 123.0286 | -123.2574 | -123.3307
2204.7656 | 123.143 | -60.9283 | 62.0636 | -0.52284 | -0.0067206 | -0.0062163 | 0.0049838 | 0.064591 | -0.0045821 | 0.067624 | -61.0153 | 62.2101 | -61.2305 | -61.1252 | 61.821 | 0.054932 | 0.022888 | 0.17395 | 62.1231 | -61.2534 | -0.30212 | 0.14648 | -0.086975 | -0.19684 | -0.24262 | -0.32501 | 0.059509 | 0.21515 | 60.9512 | 61.1023 | 122.7493 | 123.1384 | -0.086975 | 123.0515 | 60.9833 | -0.32501 | 123.1384 | -0.086975 | 60.9833 | 122.7493 | 123.0515 | -123.2941 | -123.317
2205.7656 | 123.1476 | -60.878 | 62.059 | -0.034561 | -0.0033026 | -0.0098479 | 0.0058382 | 0.069504 | -0.0047957 | 0.067838 | -60.9924 | 62.2101 | -61.2076 | -61.1343 | 61.8439 | 0.032043 | 0.059509 | 0.16937 | 62.1323 | -61.2534 | -0.32959 | 0.15106 | -0.11444 | -0.25635 | -0.21515 | -0.37537 | 0.073242 | 0.21515 | 60.9375 | 61.0474 | 122.7219 | 123.0881 | -0.11444 | 123.0103 | 60.91 | -0.37537 | 123.0881 | -0.11444 | 60.91 | 122.7219 | 123.0103 | -123.2666 | -123.3124
2206.7656 | 123.1155 | -60.91 | 62.0407 | 0.049362 | -0.004798 | -0.0057891 | 0.0049838 | 0.060746 | -0.0050095 | 0.066343 | -60.997 | 62.2238 | -61.2167 | -61.1618 | 61.8027 | 0.018311 | 0 | 0.13733 | 62.1368 | -61.2671 | -0.3067 | 0.18311 | -0.086975 | -0.25177 | -0.23804 | -0.35706 | 0.096131 | 0.21973 | 60.91 | 61.0474 | 122.7127 | 123.1338 | -0.086975 | 123.0469 | 60.9283 | -0.35706 | 123.1338 | -0.086975 | 60.9283 | 122.7127 | 123.0469 | -123.2574 | -123.3078
2207.7812 | 123.2162 | -60.9238 | 62.0087 | 0.2401 | -0.0045844 | -0.0096343 | 7.0444e-05 | 0.063737 | -0.0037277 | 0.068693 | -61.0382 | 62.146 | -61.2305 | -61.1389 | 61.8164 | 0.013733 | -0.15106 | 0.10529 | 62.0956 | -61.2488 | -0.3067 | 0.13733 | -0.11444 | -0.21515 | -0.19226 | -0.32501 | 0.086975 | 0.19226 | 60.7727 | 61.0291 | 122.7402 | 123.0698 | -0.11444 | 123.0194 | 60.9375 | -0.32501 | 123.0698 | -0.11444 | 60.9375 | 122.7402 | 123.0194 | -123.2391 | -123.2574
2208.7656 | 123.1338 | -60.9146 | 62.0636 | -0.065079 | -0.0052252 | -0.0077117 | 0.0030612 | 0.060746 | -0.0050095 | 0.067411 | -60.9833 | 62.233 | -61.1984 | -61.1252 | 61.821 | 0.064087 | 0.041199 | 0.21515 | 62.1323 | -61.2396 | -0.28381 | 0.16937 | -0.068664 | -0.21057 | -0.24262 | -0.32501 | 0.068664 | 0.21515 | 60.9558 | 61.1298 | 122.7356 | 123.1476 | -0.068664 | 123.0469 | 60.9787 | -0.32501 | 123.1476 | -0.068664 | 60.9787 | 122.7356 | 123.0469 | -123.262 | -123.3032
2209.7656 | 123.1567 | -60.9055 | 62.0636 | -0.04982 | -0.003089 | -0.0089935 | 0.0049838 | 0.062669 | -0.0022323 | 0.068265 | -60.9879 | 62.2238 | -61.203 | -61.1252 | 61.7798 | -0.064087 | 0.022888 | 0.19684 | 62.1323 | -61.2625 | -0.29755 | 0.16022 | -0.082397 | -0.21973 | -0.28381 | -0.35706 | 0.068664 | 0.21515 | 60.9283 | 61.1023 | 122.6852 | 123.1293 | -0.082397 | 123.0377 | 60.8414 | -0.35706 | 123.1293 | -0.082397 | 60.8414 | 122.6852 | 123.0377 | -123.2666 | -123.3261
2210.7656 | 123.1338 | -60.9009 | 62.0682 | -0.026932 | -0.003089 | -0.0053619 | 0.0062656 | 0.062455 | -0.0041549 | 0.067411 | -60.9879 | 62.2238 | -61.2213 | -61.1252 | 61.8118 | 0.068665 | 0.027466 | 0.21515 | 62.1185 | -61.235 | -0.32043 | 0.15564 | -0.086975 | -0.2243 | -0.25635 | -0.33417 | 0.050354 | 0.23346 | 60.9283 | 61.116 | 122.7127 | 123.1247 | -0.086975 | 123.0194 | 60.9695 | -0.33417 | 123.1247 | -0.086975 | 60.9695 | 122.7127 | 123.0194 | -123.2895 | -123.3032
2211.7656 | 123.1522 | -60.8917 | 62.0956 | -0.16426 | -0.0073614 | -0.0074981 | 0.0058382 | 0.063737 | -0.0033005 | 0.065275 | -60.997 | 62.2009 | -61.2076 | -61.1114 | 61.821 | 0.045776 | 0.045776 | 0.21057 | 62.146 | -61.2305 | -0.31586 | 0.10529 | -0.10528 | -0.21973 | -0.27466 | -0.33874 | 0.050354 | 0.21057 | 60.9375 | 61.1023 | 122.7127 | 123.0927 | -0.10528 | 123.0377 | 60.9375 | -0.33874 | 123.0927 | -0.10528 | 60.9375 | 122.7127 | 123.0377 | -123.3032 | -123.3261
2212.7656 | 123.1705 | -60.9283 | 62.0316 | 0.17906 | -0.008216 | -0.0085663 | -0.003134 | 0.062455 | -0.0041549 | 0.068906 | -61.0519 | 62.1094 | -61.1938 | -61.1572 | 61.821 | 0.013733 | -0.10529 | 0.15564 | 62.0956 | -61.2396 | -0.2655 | 0.07782 | -0.1236 | -0.22888 | -0.21057 | -0.31128 | 0.064087 | 0.14191 | 60.8231 | 61.084 | 122.7493 | 123.0377 | -0.1236 | 123.024 | 60.9421 | -0.31128 | 123.0377 | -0.1236 | 60.9421 | 122.7493 | 123.024 | -123.2254 | -123.2712
2213.7656 | 123.1201 | -60.8871 | 62.0682 | -0.12611 | -0.0054388 | -0.010275 | 0.0047702 | 0.0616 | -0.0050095 | 0.067197 | -61.0062 | 62.2192 | -61.2167 | -61.1298 | 61.821 | 0.07782 | 0.07782 | 0.2243 | 62.1552 | -61.2305 | -0.32959 | 0.15106 | -0.11902 | -0.24262 | -0.24719 | -0.34332 | 0.086975 | 0.21057 | 60.965 | 61.1114 | 122.7081 | 123.1064 | -0.11902 | 123.0423 | 60.965 | -0.34332 | 123.1064 | -0.11902 | 60.965 | 122.7081 | 123.0423 | -123.2849 | -123.2986
2214.7656 | 123.1476 | -60.9192 | 62.0773 | -0.13374 | -0.0060798 | -0.0062163 | 0.0041292 | 0.06096 | -0.0050095 | 0.067838 | -61.0428 | 62.2238 | -61.2213 | -61.1298 | 61.7981 | 0.050354 | 0.086975 | 0.21057 | 62.146 | -61.2259 | -0.30212 | 0.14648 | -0.1236 | -0.21057 | -0.27924 | -0.3067 | 0.068664 | 0.17853 | 61.0062 | 61.1298 | 122.7173 | 123.143 | -0.1236 | 123.0652 | 60.9695 | -0.3067 | 123.143 | -0.1236 | 60.9695 | 122.7173 | 123.0652 | -123.2986 | -123.3032
2215.7656 | 123.143 | -60.91 | 62.0865 | -0.149 | -0.0050116 | -0.0096343 | 0.0032748 | 0.060105 | -0.0056503 | 0.067197 | -61.0382 | 62.1872 | -61.2076 | -61.1618 | 61.7981 | 0.032043 | 0.12817 | 0.17853 | 62.1552 | -61.2122 | -0.29755 | 0.10071 | -0.12817 | -0.25177 | -0.28839 | -0.30212 | 0.068664 | 0.16937 | 61.0382 | 61.0886 | 122.7081 | 123.0972 | -0.12817 | 123.0652 | 60.9421 | -0.30212 | 123.0972 | -0.12817 | 60.9421 | 122.7081 | 123.0652 | -123.2941 | -123.2986
2216.7656 | 123.175 | -60.9009 | 62.059 | -0.11848 | -0.0056524 | -0.0045075 | 0.0028476 | 0.060319 | -0.0035141 | 0.068265 | -61.0153 | 62.2284 | -61.2122 | -61.1252 | 61.8164 | 0.073242 | 0.064087 | 0.20142 | 62.146 | -61.2167 | -0.31128 | 0.16937 | -0.11444 | -0.2243 | -0.24262 | -0.31586 | 0.086975 | 0.19684 | 60.965 | 61.1023 | 122.7173 | 123.1293 | -0.11444 | 123.0469 | 60.9741 | -0.31586 | 123.1293 | -0.11444 | 60.9741 | 122.7173 | 123.0469 | -123.2712 | -123.2758
2217.7656 | 123.1384 | -60.8917 | 62.0819 | -0.12611 | -0.0069342 | -0.012839 | 0.001993 | 0.063523 | -0.0047957 | 0.066556 | -61.0336 | 62.1964 | -61.2259 | -61.1206 | 61.821 | 0.068665 | 0.091553 | 0.20599 | 62.1918 | -61.2167 | -0.33417 | 0.11444 | -0.14191 | -0.22888 | -0.26093 | -0.32501 | 0.10986 | 0.19226 | 60.9833 | 61.0977 | 122.7127 | 123.0881 | -0.14191 | 123.0835 | 60.9604 | -0.32501 | 123.0881 | -0.14191 | 60.9604 | 122.7127 | 123.0835 | -123.3078 | -123.2986
2218.7656 | 123.143 | -60.91 | 62.1094 | -0.16426 | -0.005866 | -0.011557 | 0.001993 | 0.059891 | -0.0030869 | 0.067838 | -61.0519 | 62.2009 | -61.1938 | -61.1526 | 61.7981 | 0.036621 | 0.1236 | 0.1831 | 62.1597 | -61.2213 | -0.28381 | 0.091553 | -0.14191 | -0.24261 | -0.31128 | -0.31128 | 0.050354 | 0.14191 | 61.0336 | 61.0931 | 122.7081 | 123.111 | -0.14191 | 123.0698 | 60.9467 | -0.31128 | 123.111 | -0.14191 | 60.9467 | 122.7081 | 123.0698 | -123.3032 | -123.3307
2219.7656 | 123.111 | -60.91 | 62.0773 | -0.20241 | -0.0052252 | -0.0096343 | -0.00057036 | 0.063096 | -0.0045821 | 0.067624 | -61.0519 | 62.1872 | -61.1984 | -61.1664 | 61.7935 | 0.032043 | 0.11444 | 0.18768 | 62.1643 | -61.203 | -0.28839 | 0.10986 | -0.14191 | -0.25635 | -0.28381 | -0.29297 | 0.086975 | 0.14648 | 61.0245 | 61.0977 | 122.7036 | 123.0972 | -0.14191 | 123.0743 | 60.9421 | -0.29297 | 123.0972 | -0.14191 | 60.9421 | 122.7036 | 123.0743 | -123.2758 | -123.2803
2220.7656 | 123.1064 | -60.8917 | 62.1048 | 0.034104 | -0.0071478 | -0.010275 | 0.0015658 | 0.0616 | -0.0030869 | 0.067197 | -61.0611 | 62.1872 | -61.2259 | -61.1481 | 61.821 | 0.041199 | 0.1236 | 0.17853 | 62.1414 | -61.2305 | -0.33417 | 0.082398 | -0.16937 | -0.25635 | -0.28381 | -0.33874 | 0.036621 | 0.16479 | 61.0153 | 61.0703 | 122.7127 | 123.0789 | -0.16937 | 123.0331 | 60.9329 | -0.33874 | 123.0789 | -0.16937 | 60.9329 | 122.7127 | 123.0331 | -123.3307 | -123.3353
2221.7656 | 123.1155 | -60.91 | 62.0956 | -0.17189 | -0.0080024 | -0.010275 | -0.0022794 | 0.059464 | -0.0052231 | 0.065275 | -61.0428 | 62.1506 | -61.2167 | -61.1298 | 61.7889 | 0.036621 | 0.12817 | 0.21057 | 62.146 | -61.203 | -0.3067 | 0.054932 | -0.13275 | -0.21973 | -0.3067 | -0.29297 | 0.050354 | 0.17395 | 61.0382 | 61.1206 | 122.699 | 123.0606 | -0.13275 | 123.056 | 60.9467 | -0.29297 | 123.0606 | -0.13275 | 60.9467 | 122.699 | 123.056 | -123.3124 | -123.2986
2222.7656 | 123.0515 | -60.8963 | 62.0956 | -0.18715 | -0.005866 | -0.0051483 | 0.00028404 | 0.059678 | -0.0056503 | 0.066984 | -61.0519 | 62.1964 | -61.2076 | -61.1664 | 61.7798 | 0.032043 | 0.14648 | 0.27466 | 62.1643 | -61.2122 | -0.31128 | 0.10071 | -0.15564 | -0.27008 | -0.31586 | -0.31586 | 0.068665 | 0.15564 | 61.0428 | 61.171 | 122.6761 | 123.0927 | -0.15564 | 123.0606 | 60.9283 | -0.31586 | 123.0927 | -0.15564 | 60.9283 | 122.6761 | 123.0606 | -123.3032 | -123.3078
2223.7656 | 123.1018 | -60.9192 | 62.0728 | -0.20241 | -0.006507 | -0.010062 | 0.0041292 | 0.060105 | -0.0054367 | 0.067411 | -61.0291 | 62.1735 | -61.2167 | -61.1664 | 61.7889 | 0.045776 | 0.1236 | 0.18768 | 62.178 | -61.203 | -0.29755 | 0.10071 | -0.10986 | -0.24719 | -0.28381 | -0.28381 | 0.10529 | 0.18768 | 61.0428 | 61.1069 | 122.7081 | 123.0927 | -0.10986 | 123.0972 | 60.965 | -0.28381 | 123.0927 | -0.10986 | 60.965 | 122.7081 | 123.0972 | -123.2895 | -123.2758
2224.7656 | 123.0835 | -60.9055 | 62.0865 | -0.072708 | -0.0050116 | -0.013693 | 0.0017794 | 0.058396 | -0.0056503 | 0.064847 | -61.0611 | 62.1918 | -61.2122 | -61.1526 | 61.8073 | 0.045776 | 0.12817 | 0.17853 | 62.146 | -61.2488 | -0.3067 | 0.10529 | -0.15564 | -0.24719 | -0.27924 | -0.34332 | 0.059509 | 0.15106 | 61.0336 | 61.084 | 122.7127 | 123.0972 | -0.15564 | 123.0515 | 60.9512 | -0.34332 | 123.0972 | -0.15564 | 60.9512 | 122.7127 | 123.0515 | -123.2986 | -123.3353
2225.7656 | 123.1293 | -60.9055 | 62.0728 | -0.17189 | -0.0043708 | -0.0089935 | 0.004343 | 0.063523 | -0.0035141 | 0.06677 | -61.0382 | 62.178 | -61.203 | -61.1435 | 61.8164 | 0.032043 | 0.10071 | 0.17853 | 62.1689 | -61.1984 | -0.29755 | 0.10529 | -0.13275 | -0.23804 | -0.25635 | -0.29297 | 0.09613 | 0.1648 | 61.0062 | 61.084 | 122.7219 | 123.0835 | -0.13275 | 123.0743 | 60.9375 | -0.29297 | 123.0835 | -0.13275 | 60.9375 | 122.7219 | 123.0743 | -123.2758 | -123.2712
2226.7656 | 123.1476 | -60.9146 | 62.0865 | -0.13374 | -0.006507 | -0.0098479 | 0.00071144 | 0.061387 | -0.0043685 | 0.067197 | -61.0199 | 62.2238 | -61.2167 | -61.1481 | 61.8118 | 0.041199 | 0.11444 | 0.20599 | 62.1506 | -61.235 | -0.30212 | 0.13733 | -0.10529 | -0.23346 | -0.27466 | -0.32043 | 0.064087 | 0.19684 | 61.0291 | 61.1206 | 122.7264 | 123.1384 | -0.10529 | 123.0652 | 60.9558 | -0.32043 | 123.1384 | -0.10529 | 60.9558 | 122.7264 | 123.0652 | -123.3032 | -123.3215
2227.7656 | 123.143 | -60.8917 | 62.0728 | -0.13374 | -0.0043708 | -0.0092071 | 0.0034884 | 0.062028 | -0.0056503 | 0.06677 | -61.0565 | 62.2009 | -61.203 | -61.1389 | 61.8027 | 0.036621 | 0.10986 | 0.17853 | 62.1597 | -61.2076 | -0.31128 | 0.12817 | -0.16479 | -0.24719 | -0.27008 | -0.31586 | 0.086975 | 0.14648 | 61.0016 | 61.0703 | 122.6944 | 123.0927 | -0.16479 | 123.0515 | 60.9283 | -0.31586 | 123.0927 | -0.16479 | 60.9283 | 122.6944 | 123.0515 | -123.2758 | -123.2803
2228.7656 | 123.0927 | -60.9009 | 62.0636 | -0.16426 | -0.0060798 | -0.010489 | -0.00014316 | 0.059891 | -0.0050095 | 0.066556 | -61.0428 | 62.1964 | -61.2213 | -61.1664 | 61.8027 | 0.050354 | 0.13275 | 0.1831 | 62.1735 | -61.2442 | -0.32043 | 0.13275 | -0.14191 | -0.2655 | -0.26093 | -0.34332 | 0.10986 | 0.17853 | 61.0336 | 61.084 | 122.7036 | 123.0972 | -0.14191 | 123.0743 | 60.9512 | -0.34332 | 123.0972 | -0.14191 | 60.9512 | 122.7036 | 123.0743 | -123.2849 | -123.3078
2229.7656 | 123.1064 | -60.9055 | 62.0682 | 0.095139 | -0.0050116 | -0.013266 | 0.002634 | 0.060105 | -0.0030869 | 0.067838 | -61.0565 | 62.2009 | -61.2305 | -61.1526 | 61.8027 | 0.032043 | 0.12817 | 0.17853 | 62.1826 | -61.2122 | -0.32501 | 0.13275 | -0.15106 | -0.24719 | -0.2655 | -0.3067 | 0.11444 | 0.17395 | 61.0336 | 61.084 | 122.7081 | 123.1064 | -0.15106 | 123.0881 | 60.9375 | -0.3067 | 123.1064 | -0.15106 | 60.9375 | 122.7081 | 123.0881 | -123.2986 | -123.2803
2230.7656 | 123.143 | -60.9055 | 62.0865 | -0.10323 | -0.0043708 | -0.0068573 | 0.003702 | 0.0616 | -0.0037277 | 0.06912 | -61.0153 | 62.2009 | -61.1984 | -61.1252 | 61.8256 | 0.059509 | 0.082397 | 0.21057 | 62.1414 | -61.2259 | -0.29297 | 0.11444 | -0.10986 | -0.21973 | -0.26093 | -0.32043 | 0.054931 | 0.1831 | 60.9879 | 61.116 | 122.731 | 123.1064 | -0.10986 | 123.0469 | 60.965 | -0.32043 | 123.1064 | -0.10986 | 60.965 | 122.731 | 123.0469 | -123.2849 | -123.3124
2231.7656 | 123.1384 | -60.9238 | 62.0865 | -0.149 | -0.0037298 | -0.0085663 | 0.003702 | 0.062669 | -0.0030869 | 0.067411 | -61.0245 | 62.2009 | -61.203 | -61.1389 | 61.8118 | 0.041199 | 0.10986 | 0.19226 | 62.1506 | -61.1938 | -0.27924 | 0.11444 | -0.10071 | -0.21515 | -0.27466 | -0.27008 | 0.064087 | 0.17853 | 61.0336 | 61.116 | 122.7356 | 123.1247 | -0.10071 | 123.0743 | 60.965 | -0.27008 | 123.1247 | -0.10071 | 60.965 | 122.7356 | 123.0743 | -123.2895 | -123.2803
2232.7656 | 123.143 | -60.9009 | 62.0773 | -0.11085 | -0.007575 | -0.010062 | 0.0030612 | 0.06096 | -0.0045821 | 0.067838 | -61.0382 | 62.178 | -61.203 | -61.1343 | 61.8027 | 0.045776 | 0.12817 | 0.19684 | 62.146 | -61.2396 | -0.30212 | 0.10071 | -0.13733 | -0.23346 | -0.27466 | -0.33874 | 0.068664 | 0.1648 | 61.0291 | 61.0977 | 122.7036 | 123.0789 | -0.13733 | 123.0469 | 60.9467 | -0.33874 | 123.0789 | -0.13733 | 60.9467 | 122.7036 | 123.0469 | -123.2803 | -123.317
2233.7656 | 123.1476 | -60.9192 | 62.0728 | -0.2253 | -0.004798 | -0.0066437 | 0.0022066 | 0.062241 | -0.0039413 | 0.066343 | -61.0382 | 62.1643 | -61.235 | -61.171 | 61.8027 | 0.059509 | 0.1236 | 0.19684 | 62.1597 | -61.1938 | -0.31586 | 0.091553 | -0.11902 | -0.25177 | -0.27008 | -0.27466 | 0.086975 | 0.19684 | 61.0428 | 61.116 | 122.7219 | 123.0835 | -0.11902 | 123.0789 | 60.9787 | -0.27466 | 123.0835 | -0.11902 | 60.9787 | 122.7219 | 123.0789 | -123.3078 | -123.2666
2234.7656 | 123.1384 | -60.8917 | 62.0636 | -0.0040434 | -0.0067206 | -0.010489 | 0.002634 | 0.061814 | -0.0056503 | 0.066129 | -61.0657 | 62.1826 | -61.235 | -61.1435 | 61.8118 | 0.059509 | 0.13275 | 0.18768 | 62.1643 | -61.1984 | -0.34332 | 0.11902 | -0.17395 | -0.25177 | -0.25177 | -0.3067 | 0.10071 | 0.16937 | 61.0245 | 61.0794 | 122.7036 | 123.0743 | -0.17395 | 123.056 | 60.9512 | -0.3067 | 123.0743 | -0.17395 | 60.9512 | 122.7036 | 123.056 | -123.2986 | -123.262
2235.7656 | 123.1201 | -60.91 | 62.0911 | -0.17952 | -0.0060798 | -0.01113 | -0.0012112 | 0.059037 | -0.0062911 | 0.067838 | -61.0382 | 62.1826 | -61.2076 | -61.1618 | 61.8073 | 0.059509 | 0.11444 | 0.21515 | 62.1552 | -61.2167 | -0.29755 | 0.091553 | -0.12817 | -0.25177 | -0.28381 | -0.3067 | 0.064087 | 0.16937 | 61.0245 | 61.1252 | 122.7173 | 123.0927 | -0.12817 | 123.0652 | 60.9695 | -0.3067 | 123.0927 | -0.12817 | 60.9695 | 122.7173 | 123.0652 | -123.2986 | -123.3078
2236.7656 | 123.1018 | -60.91 | 62.0819 | -0.2253 | -0.0050116 | -0.0089935 | 0.0030612 | 0.059891 | -0.0033005 | 0.067838 | -61.0748 | 62.2101 | -61.1755 | -61.1618 | 61.7798 | -0.032043 | 0.41657 | 0.16479 | 62.1643 | -61.2122 | -0.2655 | 0.12817 | -0.16479 | -0.25177 | -0.30212 | -0.30212 | 0.082398 | 0.10071 | 61.3266 | 61.0748 | 122.6898 | 123.1201 | -0.16479 | 123.0743 | 60.878 | -0.30212 | 123.1201 | -0.16479 | 60.878 | 122.6898 | 123.0743 | -123.2574 | -123.2941
2237.7656 | 123.1384 | -60.9146 | 62.0728 | -0.20241 | -0.0033026 | -0.012839 | 0.0058382 | 0.0616 | -0.0039413 | 0.068906 | -61.0474 | 62.1918 | -61.203 | -61.1618 | 61.8118 | 0.032043 | 0.13275 | 0.18768 | 62.1506 | -61.1938 | -0.28839 | 0.11902 | -0.13275 | -0.24719 | -0.26093 | -0.27924 | 0.07782 | 0.15564 | 61.0474 | 61.1023 | 122.7264 | 123.1064 | -0.13275 | 123.0652 | 60.9467 | -0.27924 | 123.1064 | -0.13275 | 60.9467 | 122.7264 | 123.0652 | -123.2758 | -123.2666
2238.7656 | 123.0835 | -60.9146 | 62.0865 | -0.080337 | -0.0041572 | -0.011343 | 0.0017794 | 0.05861 | -0.0058639 | 0.065488 | -61.0611 | 62.1918 | -61.2213 | -61.1572 | 61.7935 | 0.041199 | 0.13275 | 0.1831 | 62.1552 | -61.2167 | -0.3067 | 0.10529 | -0.14648 | -0.24262 | -0.29297 | -0.30212 | 0.068664 | 0.16022 | 61.0474 | 61.0977 | 122.7081 | 123.1064 | -0.14648 | 123.0698 | 60.9558 | -0.30212 | 123.1064 | -0.14648 | 60.9558 | 122.7081 | 123.0698 | -123.3078 | -123.3032
2239.7656 | 123.1338 | -60.9283 | 62.0728 | -0.14137 | -0.0094976 | -0.016043 | 0.004343 | 0.058823 | -0.0060775 | 0.068906 | -60.8917 | 62.2238 | -61.203 | -61.1755 | 61.7935 | 0.018311 | 0.15564 | 0.18768 | 62.1643 | -61.2213 | -0.27466 | 0.15106 | 0.036621 | -0.24719 | -0.27924 | -0.29297 | 0.091553 | 0.31128 | 61.084 | 61.116 | 122.7219 | 123.1522 | 0.036621 | 123.0927 | 60.9467 | -0.29297 | 123.1522 | 0.036621 | 60.9467 | 122.7219 | 123.0927 | -123.2758 | -123.2941
2240.7656 | 123.1842 | -60.9146 | 62.0636 | -0.019302 | -0.0037298 | -0.010703 | 0.0039156 | 0.064164 | -0.0050095 | 0.067411 | -60.997 | 62.178 | -61.2122 | -61.1023 | 61.8164 | 0.13275 | -0.18768 | 0.16937 | 62.1277 | -61.2396 | -0.29755 | 0.11444 | -0.082397 | -0.18768 | -0.24719 | -0.32501 | 0.064087 | 0.21515 | 60.7269 | 61.084 | 122.731 | 123.0927 | -0.082397 | 123.0423 | 61.0474 | -0.32501 | 123.0927 | -0.082397 | 61.0474 | 122.731 | 123.0423 | -123.2758 | -123.3032
2241.7656 | 123.143 | -60.91 | 62.1506 | -0.21767 | -0.0054388 | -0.01348 | -0.00078396 | 0.062028 | -0.0067185 | 0.066343 | -61.0565 | 62.1689 | -61.2213 | -61.1481 | 61.8027 | 0.041199 | 0.15106 | 0.17395 | 62.1689 | -61.1893 | -0.31128 | 0.01831 | -0.14648 | -0.23804 | -0.3479 | -0.27924 | 0.01831 | 0.16479 | 61.0611 | 61.084 | 122.7127 | 123.0789 | -0.14648 | 123.0789 | 60.9512 | -0.27924 | 123.0789 | -0.14648 | 60.9512 | 122.7127 | 123.0789 | -123.3719 | -123.3398
2242.7812 | 123.1018 | -60.9009 | 62.0956 | -0.04982 | -0.0071478 | -0.0057891 | 0.0022066 | 0.059251 | -0.0047957 | 0.066343 | -61.0382 | 62.1918 | -61.1984 | -61.1526 | 61.7981 | 0.032043 | 0.13275 | 0.19226 | 62.1506 | -61.2259 | -0.29755 | 0.09613 | -0.13733 | -0.25177 | -0.29755 | -0.32501 | 0.054932 | 0.16022 | 61.0336 | 61.0931 | 122.699 | 123.0927 | -0.13733 | 123.0515 | 60.9329 | -0.32501 | 123.0927 | -0.13733 | 60.9329 | 122.699 | 123.0515 | -123.2941 | -123.3215
2243.7656 | 123.0927 | -60.9283 | 62.0773 | -0.24818 | -0.0050116 | -0.0087799 | 0.00092504 | 0.059464 | -0.0050095 | 0.065702 | -61.0382 | 62.178 | -61.1893 | -61.171 | 61.8073 | 0.036621 | 0.13275 | 0.19684 | 62.1689 | -61.1984 | -0.26093 | 0.10071 | -0.10986 | -0.24261 | -0.27008 | -0.27008 | 0.091552 | 0.15106 | 61.0611 | 61.1252 | 122.7356 | 123.1064 | -0.10986 | 123.0972 | 60.965 | -0.27008 | 123.1064 | -0.10986 | 60.965 | 122.7356 | 123.0972 | -123.2666 | -123.2758
2244.7656 | 123.1018 | -60.9055 | 62.0956 | -0.15663 | -0.005866 | -0.011343 | 0.0022066 | 0.062455 | -0.0020187 | 0.06677 | -61.0657 | 62.1643 | -61.2305 | -61.1755 | 61.7798 | 0.018311 | 0.11444 | 0.15106 | 62.1643 | -61.2213 | -0.32501 | 0.068665 | -0.16022 | -0.27008 | -0.31586 | -0.31586 | 0.068665 | 0.16479 | 61.0199 | 61.0565 | 122.6852 | 123.0698 | -0.16022 | 123.0698 | 60.9238 | -0.31586 | 123.0698 | -0.16022 | 60.9238 | 122.6852 | 123.0698 | -123.3261 | -123.317
2245.7656 | 123.111 | -60.9146 | 62.0728 | -0.18715 | -0.0060798 | -0.0092071 | 0.0013522 | 0.060532 | -0.0069321 | 0.066556 | -61.0657 | 62.1964 | -61.203 | -61.1481 | 61.734 | 0.16937 | 0.20142 | 0.064087 | 62.178 | -61.1847 | -0.28839 | 0.1236 | -0.15106 | -0.23346 | -0.33875 | -0.27008 | 0.10529 | 0.13733 | 61.116 | 60.9787 | 122.6486 | 123.111 | -0.15106 | 123.0927 | 61.084 | -0.27008 | 123.111 | -0.15106 | 61.084 | 122.6486 | 123.0927 | -123.2758 | -123.2574
2246.7656 | 123.1155 | -60.8871 | 62.0956 | -0.16426 | -0.0050116 | -0.012412 | -0.00014316 | 0.060319 | -0.0058639 | 0.066129 | -61.084 | 62.178 | -61.2305 | -61.1526 | 61.7935 | 0.036621 | 0.15106 | 0.18768 | 62.1323 | -61.2076 | -0.34332 | 0.082398 | -0.19684 | -0.2655 | -0.30212 | -0.32043 | 0.036621 | 0.14648 | 61.0382 | 61.0748 | 122.6807 | 123.0652 | -0.19684 | 123.0194 | 60.9238 | -0.32043 | 123.0652 | -0.19684 | 60.9238 | 122.6807 | 123.0194 | -123.3261 | -123.3032
2247.7656 | 123.0972 | -60.9283 | 62.0819 | -0.19478 | -0.0071478 | -0.015189 | 0.0017794 | 0.059891 | -0.0069321 | 0.065061 | -61.0611 | 62.1735 | -61.2122 | -61.1664 | 61.8027 | 0.032043 | 0.14191 | 0.19684 | 62.178 | -61.2076 | -0.28381 | 0.091553 | -0.13275 | -0.23804 | -0.27924 | -0.27924 | 0.096131 | 0.15106 | 61.0703 | 61.1252 | 122.731 | 123.1018 | -0.13275 | 123.1064 | 60.9604 | -0.27924 | 123.1018 | -0.13275 | 60.9604 | 122.731 | 123.1064 | -123.2941 | -123.2895
2248.7656 | 123.1705 | -60.8871 | 62.0499 | -0.072708 | -0.0043708 | -0.013266 | 0.0077608 | 0.06395 | -0.0069321 | 0.065275 | -60.9833 | 62.1597 | -61.2076 | -61.1069 | 61.8118 | 0.059509 | 0.036621 | 0.19684 | 62.1414 | -61.1664 | -0.32043 | 0.10986 | -0.09613 | -0.21973 | -0.23804 | -0.27924 | 0.091552 | 0.22431 | 60.9238 | 61.084 | 122.699 | 123.0469 | -0.09613 | 123.0286 | 60.9467 | -0.27924 | 123.0469 | -0.09613 | 60.9467 | 122.699 | 123.0286 | -123.2574 | -123.2162
2249.7656 | 123.1338 | -60.8917 | 62.0728 | -0.20241 | -0.0050116 | -0.010916 | -0.0016386 | 0.061387 | -0.0080001 | 0.066343 | -61.0382 | 62.1506 | -61.2076 | -61.1389 | 61.8347 | 0.086975 | 0.10986 | 0.21973 | 62.1643 | -61.1664 | -0.31586 | 0.07782 | -0.14648 | -0.24719 | -0.23804 | -0.27466 | 0.091553 | 0.16937 | 61.0016 | 61.1115 | 122.7264 | 123.0423 | -0.14648 | 123.056 | 60.9787 | -0.27466 | 123.0423 | -0.14648 | 60.9787 | 122.7264 | 123.056 | -123.2803 | -123.2391
2250.7812 | 123.1247 | -60.9009 | 62.1002 | -0.17952 | -0.0067206 | -0.0092071 | 0.00071144 | 0.059678 | -0.0050095 | 0.067624 | -61.0611 | 62.2055 | -61.1847 | -61.1435 | 61.7981 | 0.050354 | 0.14648 | 0.1831 | 62.1506 | -61.1938 | -0.28381 | 0.10529 | -0.16022 | -0.24261 | -0.30212 | -0.29297 | 0.050354 | 0.1236 | 61.0474 | 61.084 | 122.699 | 123.1064 | -0.16022 | 123.0515 | 60.9512 | -0.29297 | 123.1064 | -0.16022 | 60.9512 | 122.699 | 123.0515 | -123.2849 | -123.2941
2251.7656 | 123.111 | -60.9009 | 62.0956 | -0.14137 | -0.008216 | -0.012412 | -0.00078396 | 0.060532 | -0.0050095 | 0.068265 | -61.0519 | 62.1735 | -61.203 | -61.1481 | 61.7935 | 0.041199 | 0.14191 | 0.1831 | 62.1735 | -61.1893 | -0.30212 | 0.07782 | -0.15106 | -0.24719 | -0.30212 | -0.28839 | 0.07782 | 0.15106 | 61.0428 | 61.084 | 122.6944 | 123.0743 | -0.15106 | 123.0743 | 60.9421 | -0.28839 | 123.0743 | -0.15106 | 60.9421 | 122.6944 | 123.0743 | -123.2986 | -123.2849
2252.7656 | 123.1201 | -60.8917 | 62.0728 | -0.18715 | -0.0060798 | -0.011343 | 0.0011386 | 0.059464 | -0.0071457 | 0.066556 | -61.0336 | 62.146 | -61.2076 | -61.1114 | 61.8484 | 0.068665 | 0.11444 | 0.21515 | 62.178 | -61.171 | -0.31586 | 0.073242 | -0.14191 | -0.21973 | -0.2243 | -0.27923 | 0.10529 | 0.17395 | 61.0062 | 61.1069 | 122.7402 | 123.0377 | -0.14191 | 123.0698 | 60.9604 | -0.27923 | 123.0377 | -0.14191 | 60.9604 | 122.7402 | 123.0698 | -123.2803 | -123.2437
2253.7656 | 123.1659 | -60.8917 | 62.0728 | -0.17189 | -0.008216 | -0.010489 | 7.0444e-05 | 0.059891 | -0.0056503 | 0.067624 | -60.997 | 62.1277 | -61.1847 | -61.1114 | 61.853 | 0.09613 | 0.086975 | 0.24261 | 62.1552 | -61.1801 | -0.29297 | 0.054932 | -0.10528 | -0.21973 | -0.21973 | -0.28839 | 0.082397 | 0.18768 | 60.9787 | 61.1343 | 122.7448 | 123.0194 | -0.10528 | 123.0469 | 60.9879 | -0.28839 | 123.0194 | -0.10528 | 60.9879 | 122.7448 | 123.0469 | -123.2574 | -123.2529
2254.7656 | 123.175 | -60.878 | 62.0773 | -0.17952 | -0.010352 | -0.016043 | 0.0011386 | 0.05861 | -0.0060775 | 0.065916 | -60.9879 | 62.1185 | -61.1893 | -61.0977 | 61.8668 | 0.11902 | 0.036621 | 0.28839 | 62.1185 | -61.1526 | -0.31128 | 0.041198 | -0.10986 | -0.21973 | -0.21057 | -0.27466 | 0.041198 | 0.20142 | 60.9146 | 61.1664 | 122.7448 | 122.9965 | -0.10986 | 122.9965 | 60.997 | -0.27466 | 122.9965 | -0.10986 | 60.997 | 122.7448 | 122.9965 | -123.2666 | -123.23
2255.7656 | 123.2071 | -60.8597 | 62.0453 | -0.30159 | -0.008216 | -0.013052 | -0.00099756 | 0.059037 | -0.0088547 | 0.067838 | -60.9879 | 62.0956 | -61.1801 | -61.0657 | 61.8805 | 0.12817 | -0.013733 | 0.28839 | 62.0911 | -61.1526 | -0.32044 | 0.050354 | -0.12817 | -0.20599 | -0.16479 | -0.29297 | 0.045776 | 0.19226 | 60.8459 | 61.1481 | 122.7402 | 122.9553 | -0.12817 | 122.9507 | 60.9879 | -0.29297 | 122.9553 | -0.12817 | 60.9879 | 122.7402 | 122.9507 | -123.2254 | -123.1979
2256.7656 | 123.23 | -60.8643 | 62.0453 | -0.17189 | -0.0097114 | -0.012839 | 0.00049764 | 0.060105 | -0.0052231 | 0.06912 | -60.7407 | 62.1368 | -61.1847 | -61.0886 | 61.8668 | 0.13275 | -0.045776 | 0.32959 | 62.0911 | -61.171 | -0.32043 | 0.091553 | 0.1236 | -0.2243 | -0.17853 | -0.3067 | 0.045776 | 0.44403 | 60.8185 | 61.1938 | 122.731 | 123.0011 | 0.1236 | 122.9553 | 60.997 | -0.3067 | 123.0011 | 0.1236 | 60.997 | 122.731 | 122.9553 | -123.23 | -123.2162
2257.7656 | 123.3398 | -60.8322 | 62.0911 | -0.13374 | -0.0073614 | -0.012839 | 0.0017794 | 0.057114 | -0.0043685 | 0.067197 | -60.9787 | 62.0636 | -61.1847 | -61.0474 | 61.908 | 0.14191 | -0.054932 | 0.31128 | 62.1094 | -61.1252 | -0.35248 | -0.027465 | -0.14648 | -0.21515 | -0.18311 | -0.29297 | 0.018311 | 0.20599 | 60.7773 | 61.1435 | 122.7402 | 122.8958 | -0.14648 | 122.9416 | 60.9741 | -0.29297 | 122.8958 | -0.14648 | 60.9741 | 122.7402 | 122.9416 | -123.2758 | -123.2162
2258.7812 | 123.1476 | -60.8597 | 62.0453 | -0.2253 | -0.0071478 | -0.01113 | 0.0039156 | 0.057755 | -0.0067185 | 0.066129 | -61.0153 | 62.114 | -61.1893 | -61.0977 | 61.8439 | 0.10071 | 0.054932 | 0.25177 | 62.1323 | -61.1755 | -0.32959 | 0.068665 | -0.15564 | -0.23804 | -0.20142 | -0.31586 | 0.086975 | 0.17395 | 60.9146 | 61.1114 | 122.7036 | 122.9736 | -0.15564 | 122.9919 | 60.9604 | -0.31586 | 122.9736 | -0.15564 | 60.9604 | 122.7036 | 122.9919 | -123.2346 | -123.2208
2259.7656 | 123.2254 | -60.8414 | 62.0132 | -0.026932 | -0.012061 | -0.01113 | -0.003134 | 0.056473 | -0.0077865 | 0.068265 | -61.0016 | 62.0682 | -61.2076 | -61.0794 | 61.908 | 0.10986 | -0.082397 | 0.28839 | 62.0819 | -61.1389 | -0.36621 | 0.054931 | -0.16022 | -0.23804 | -0.10529 | -0.29755 | 0.068664 | 0.20599 | 60.759 | 61.1298 | 122.7493 | 122.9095 | -0.16022 | 122.9233 | 60.9512 | -0.29755 | 122.9095 | -0.16022 | 60.9512 | 122.7493 | 122.9233 | -123.2208 | -123.1522
2260.7656 | 123.1934 | -60.8871 | 62.0453 | -0.034561 | -0.0077888 | -0.014548 | 0.0011386 | 0.059891 | -0.0056503 | 0.067197 | -61.0016 | 62.059 | -61.1984 | -61.084 | 61.8576 | 0.07782 | -0.054932 | 0.25635 | 62.0956 | -61.1435 | -0.31128 | 0.013733 | -0.11444 | -0.19684 | -0.18768 | -0.25635 | 0.050354 | 0.19684 | 60.8322 | 61.1435 | 122.7448 | 122.9462 | -0.11444 | 122.9828 | 60.965 | -0.25635 | 122.9462 | -0.11444 | 60.965 | 122.7448 | 122.9828 | -123.2437 | -123.1888
2261.7656 | 123.1888 | -60.8688 | 62.027 | 0.056992 | -0.0071478 | -0.016684 | 0.00071144 | 0.059251 | -0.0039413 | 0.066129 | -61.0428 | 62.0728 | -61.2122 | -61.1023 | 61.853 | 0.068665 | -0.082397 | 0.21973 | 62.0819 | -61.1572 | -0.34332 | 0.045776 | -0.17395 | -0.23346 | -0.17395 | -0.28839 | 0.054931 | 0.16937 | 60.7864 | 61.0886 | 122.7219 | 122.9416 | -0.17395 | 122.9507 | 60.9375 | -0.28839 | 122.9416 | -0.17395 | 60.9375 | 122.7219 | 122.9507 | -123.2391 | -123.1842
2262.7656 | 123.2391 | -60.8688 | 62.0316 | -0.072708 | -0.0084296 | -0.010916 | -0.001425 | 0.057542 | -0.0080001 | 0.065702 | -61.0199 | 62.0636 | -61.1893 | -61.0794 | 61.8668 | 0.082397 | -0.086975 | 0.2655 | 62.1002 | -61.1526 | -0.32044 | 0.032044 | -0.15106 | -0.21057 | -0.16479 | -0.28381 | 0.068665 | 0.16937 | 60.7819 | 61.1343 | 122.7356 | 122.9324 | -0.15106 | 122.9691 | 60.9512 | -0.28381 | 122.9324 | -0.15106 | 60.9512 | 122.7356 | 122.9691 | -123.2208 | -123.1842
2263.7656 | 123.1705 | -60.8963 | 62.0407 | 0.10277 | -0.0062934 | -0.013693 | 0.00071144 | 0.06096 | -0.0037277 | 0.068479 | -61.0611 | 62.0728 | -61.2213 | -61.1114 | 61.8347 | 0.004578 | -0.09613 | 0.3479 | 62.0956 | -61.1481 | -0.32501 | 0.032044 | -0.16479 | -0.21515 | -0.20599 | -0.25177 | 0.054932 | 0.16022 | 60.8002 | 61.2442 | 122.731 | 122.9691 | -0.16479 | 122.9919 | 60.9009 | -0.25177 | 122.9691 | -0.16479 | 60.9009 | 122.731 | 122.9919 | -123.262 | -123.1888
2264.7656 | 123.2071 | -60.8917 | 62.0544 | 0.43083 | -0.007575 | -0.015402 | -0.00035676 | 0.057542 | -0.0062911 | 0.067624 | -61.0474 | 62.0636 | -61.2076 | -61.1114 | 61.8073 | 0.027466 | -0.091553 | 0.19226 | 62.0865 | -61.1481 | -0.31586 | 0.009156 | -0.15564 | -0.21973 | -0.24719 | -0.25635 | 0.032044 | 0.16022 | 60.8002 | 61.084 | 122.699 | 122.9553 | -0.15564 | 122.9782 | 60.9192 | -0.25635 | 122.9553 | -0.15564 | 60.9192 | 122.699 | 122.9782 | -123.262 | -123.2025
2265.7656 | 123.1934 | -60.8871 | 62.027 | 0.12566 | -0.0080024 | -0.010916 | -0.002493 | 0.059251 | -0.0047957 | 0.067411 | -61.0565 | 62.0636 | -61.2167 | -61.1114 | 61.8256 | 0.013733 | 0.086975 | 0.2243 | 62.114 | -61.1481 | -0.32959 | 0.036621 | -0.16937 | -0.2243 | -0.20142 | -0.26093 | 0.086975 | 0.16022 | 60.9741 | 61.1114 | 122.7127 | 122.9507 | -0.16937 | 123.0011 | 60.9009 | -0.26093 | 122.9507 | -0.16937 | 60.9009 | 122.7127 | 123.0011 | -123.2437 | -123.175
2266.7656 | 123.1979 | -60.8551 | 62.0316 | 0.12566 | -0.0077888 | -0.0055755 | 0.0015658 | 0.05626 | -0.0047957 | 0.066984 | -61.0336 | 62.0728 | -61.2076 | -61.1343 | 61.7935 | 0.018311 | -0.10529 | 0.15106 | 62.0544 | -61.1618 | -0.35248 | 0.041199 | -0.17853 | -0.27923 | -0.23804 | -0.3067 | 0.022888 | 0.17395 | 60.7498 | 61.0062 | 122.6486 | 122.9279 | -0.17853 | 122.9095 | 60.8734 | -0.3067 | 122.9279 | -0.17853 | 60.8734 | 122.6486 | 122.9095 | -123.2391 | -123.1934
2267.7656 | 123.1842 | -60.8734 | 62.0361 | 0.19432 | -0.006507 | -0.011771 | 0.0015658 | 0.055405 | -0.0056503 | 0.066343 | -61.0519 | 62.0773 | -61.203 | -61.1206 | 61.8118 | 0.009155 | -0.15106 | 0.14191 | 62.027 | -61.1893 | -0.32959 | 0.041199 | -0.17853 | -0.24719 | -0.2243 | -0.31586 | -0.009155 | 0.15106 | 60.7224 | 61.0153 | 122.6852 | 122.9507 | -0.17853 | 122.9004 | 60.8826 | -0.31586 | 122.9507 | -0.17853 | 60.8826 | 122.6852 | 122.9004 | -123.2391 | -123.2254
2268.7656 | 123.1888 | -60.9146 | 61.9904 | 0.20958 | -0.0077888 | -0.011343 | 0.0039156 | 0.059678 | -0.0062911 | 0.067838 | -61.0199 | 62.0636 | -61.203 | -61.1069 | 61.821 | 0.009155 | -0.16479 | 0.14191 | 62.0819 | -61.1755 | -0.28839 | 0.073243 | -0.10529 | -0.19226 | -0.16937 | -0.26093 | 0.091553 | 0.18311 | 60.7498 | 61.0565 | 122.7356 | 122.9782 | -0.10529 | 122.9965 | 60.9238 | -0.26093 | 122.9782 | -0.10529 | 60.9238 | 122.7356 | 122.9965 | -123.1934 | -123.1659
2269.7656 | 123.2712 | -60.8917 | 61.9995 | 0.25536 | -0.0052252 | -0.010062 | 0.0041292 | 0.059464 | -0.0056503 | 0.06912 | -60.9879 | 62.0636 | -61.2213 | -61.084 | 61.8576 | 0.041199 | -0.42114 | -0.032043 | 62.0178 | -61.2076 | -0.32959 | 0.064087 | -0.09613 | -0.19226 | -0.14191 | -0.31586 | 0.01831 | 0.23346 | 60.4706 | 60.8597 | 122.7493 | 122.9553 | -0.09613 | 122.9095 | 60.9329 | -0.31586 | 122.9553 | -0.09613 | 60.9329 | 122.7493 | 122.9095 | -123.2208 | -123.2071
2270.7656 | 123.2254 | -60.8688 | 62.0132 | 0.17143 | -0.0080024 | -0.013693 | 0.0017794 | 0.061387 | -0.0062911 | 0.06677 | -60.997 | 62.0819 | -61.1801 | -61.0886 | 61.853 | 0.027466 | -0.18768 | 0.17395 | 62.0407 | -61.1664 | -0.31128 | 0.068664 | -0.12817 | -0.21973 | -0.16022 | -0.29755 | 0.027465 | 0.18311 | 60.6812 | 61.0428 | 122.7219 | 122.9507 | -0.12817 | 122.9095 | 60.8963 | -0.29755 | 122.9507 | -0.12817 | 60.8963 | 122.7219 | 122.9095 | -123.1934 | -123.1796
2271.7656 | 123.175 | -60.8826 | 62.0132 | 0.21721 | -0.0071478 | -0.0096343 | 0.0022066 | 0.059037 | -0.0067185 | 0.068265 | -61.0062 | 62.0682 | -61.1984 | -61.0931 | 61.8393 | 0.032043 | -0.18768 | 0.15564 | 62.0407 | -61.1893 | -0.31586 | 0.054931 | -0.1236 | -0.21057 | -0.17395 | -0.3067 | 0.027465 | 0.19226 | 60.6949 | 61.0382 | 122.7219 | 122.9507 | -0.1236 | 122.9233 | 60.9146 | -0.3067 | 122.9507 | -0.1236 | 60.9146 | 122.7219 | 122.9233 | -123.2117 | -123.2025
2272.7656 | 123.1842 | -60.8688 | 62.0224 | 0.18669 | -0.0060798 | -0.0074981 | -0.001425 | 0.059464 | -0.0050095 | 0.067838 | -61.0245 | 62.0773 | -61.2076 | -61.1206 | 61.8256 | 0 | -0.13275 | 0.14648 | 62.0682 | -61.1847 | -0.33875 | 0.054932 | -0.15564 | -0.25177 | -0.19684 | -0.31586 | 0.045776 | 0.18311 | 60.7361 | 61.0153 | 122.6944 | 122.9462 | -0.15564 | 122.937 | 60.8688 | -0.31586 | 122.9462 | -0.15564 | 60.8688 | 122.6944 | 122.937 | -123.23 | -123.2071
2273.7656 | 123.2208 | -60.8871 | 61.9949 | 0.26299 | -0.0039434 | -0.010703 | 0.0022066 | 0.060532 | -0.0052231 | 0.067624 | -61.0748 | 62.0865 | -61.235 | -61.0657 | 61.8713 | 0.059509 | -0.2243 | 0.16022 | 62.059 | -61.171 | -0.3479 | 0.091553 | -0.18768 | -0.17853 | -0.1236 | -0.28381 | 0.064087 | 0.16022 | 60.6628 | 61.0474 | 122.7585 | 122.9736 | -0.18768 | 122.9462 | 60.9467 | -0.28381 | 122.9736 | -0.18768 | 60.9467 | 122.7585 | 122.9462 | -123.23 | -123.1659
2274.7656 | 123.2529 | -60.8917 | 61.9904 | 0.27061 | -0.0067206 | -0.011984 | 0.0051974 | 0.058823 | -0.0071457 | 0.065275 | -60.9741 | 62.1094 | -61.2259 | -61.0657 | 61.8484 | 0.045776 | -0.21057 | 0.050354 | 62.059 | -61.203 | -0.33417 | 0.11902 | -0.082397 | -0.17395 | -0.14191 | -0.31128 | 0.068665 | 0.25177 | 60.6812 | 60.9421 | 122.7402 | 123.0011 | -0.082397 | 122.9507 | 60.9375 | -0.31128 | 123.0011 | -0.082397 | 60.9375 | 122.7402 | 122.9507 | -123.2162 | -123.1934
2275.7656 | 123.2025 | -60.8871 | 61.9904 | 0.0035856 | -0.0043708 | -0.0070709 | 0.0045566 | 0.060746 | -0.0058639 | 0.065916 | -60.9741 | 62.1094 | -61.2213 | -61.0886 | 61.8622 | 0.041199 | -0.21057 | 0.15106 | 62.0453 | -61.2076 | -0.33417 | 0.11902 | -0.086975 | -0.20142 | -0.12817 | -0.32043 | 0.054932 | 0.24719 | 60.6766 | 61.0382 | 122.7493 | 122.9965 | -0.086975 | 122.9324 | 60.9283 | -0.32043 | 122.9965 | -0.086975 | 60.9283 | 122.7493 | 122.9324 | -123.2117 | -123.1979
2276.7656 | 123.23 | -60.878 | 62.0178 | 0.24773 | -0.0062934 | -0.0087799 | 0.0069064 | 0.0663 | -0.0056503 | 0.067624 | -60.9833 | 62.0728 | -61.1938 | -60.9787 | 61.9492 | 0.07782 | -0.18768 | 0.20599 | 62.0544 | -61.1801 | -0.31586 | 0.054932 | -0.10528 | -0.10071 | -0.068664 | -0.30212 | 0.036621 | 0.21057 | 60.6903 | 61.084 | 122.8271 | 122.9507 | -0.10528 | 122.9324 | 60.9558 | -0.30212 | 122.9507 | -0.10528 | 60.9558 | 122.8271 | 122.9324 | -123.2117 | -123.1979
2277.7656 | 123.175 | -60.9192 | 61.9995 | 0.25536 | -0.0052252 | -0.0089935 | 0.0073336 | 0.062241 | -0.0060775 | 0.068479 | -61.0291 | 62.1277 | -61.2396 | -61.1206 | 61.8118 | -0.013733 | -0.14648 | 0.10529 | 62.0682 | -61.2122 | -0.32043 | 0.12817 | -0.10986 | -0.20142 | -0.18768 | -0.29297 | 0.068664 | 0.21057 | 60.7727 | 61.0245 | 122.731 | 123.0469 | -0.10986 | 122.9874 | 60.9055 | -0.29297 | 123.0469 | -0.10986 | 60.9055 | 122.731 | 122.9874 | -123.2391 | -123.2117
2278.7656 | 123.2254 | -60.8917 | 61.9766 | 0.33928 | -0.004798 | -0.011557 | 0.0041292 | 0.062882 | -0.0069321 | 0.067197 | -60.997 | 62.0956 | -61.1984 | -61.084 | 61.8668 | 0.041199 | -0.18768 | 0.15106 | 62.0544 | -61.1984 | -0.3067 | 0.11902 | -0.10528 | -0.19226 | -0.10986 | -0.3067 | 0.077819 | 0.20142 | 60.704 | 61.0428 | 122.7585 | 122.9874 | -0.10528 | 122.9462 | 60.9329 | -0.3067 | 122.9874 | -0.10528 | 60.9329 | 122.7585 | 122.9462 | -123.175 | -123.175
2279.7656 | 123.1888 | -60.9009 | 62.0041 | 0.27061 | -0.0050116 | -0.012839 | 0.004343 | 0.063096 | -0.0058639 | 0.065488 | -61.0153 | 62.1094 | -61.2122 | -61.1069 | 61.8393 | 0 | -0.19684 | 0.16937 | 62.0453 | -61.2076 | -0.31128 | 0.10529 | -0.11444 | -0.20599 | -0.16479 | -0.3067 | 0.041199 | 0.19684 | 60.704 | 61.0703 | 122.7402 | 123.0103 | -0.11444 | 122.9462 | 60.9009 | -0.3067 | 123.0103 | -0.11444 | 60.9009 | 122.7402 | 122.9462 | -123.2162 | -123.2117
2280.7656 | 123.2529 | -60.9055 | 62.0316 | 0.19432 | -0.006507 | -0.0092071 | 0.0030612 | 0.062455 | -0.0050095 | 0.069761 | -61.0016 | 62.0865 | -61.2076 | -61.0748 | 61.8439 | 0.050354 | -0.2243 | 0.16937 | 62.0453 | -61.1801 | -0.30212 | 0.054932 | -0.09613 | -0.16937 | -0.18768 | -0.27466 | 0.013733 | 0.20599 | 60.6812 | 61.0748 | 122.7493 | 122.9919 | -0.09613 | 122.9507 | 60.9558 | -0.27466 | 122.9919 | -0.09613 | 60.9558 | 122.7493 | 122.9507 | -123.2391 | -123.2117
2281.7656 | 123.1659 | -60.9283 | 62.0407 | 0.24773 | -0.004798 | -0.0087799 | 0.0034884 | 0.060746 | -0.0024459 | 0.067624 | -61.0565 | 62.1597 | -61.2442 | -61.1526 | 61.7889 | -0.036621 | -0.10529 | 0.086975 | 62.0407 | -61.2305 | -0.31586 | 0.11902 | -0.12817 | -0.2243 | -0.25177 | -0.30212 | 0 | 0.18768 | 60.8231 | 61.0153 | 122.7173 | 123.0881 | -0.12817 | 122.9691 | 60.8917 | -0.30212 | 123.0881 | -0.12817 | 60.8917 | 122.7173 | 122.9691 | -123.2849 | -123.2712
2282.7656 | 123.1476 | -60.9329 | 62.0499 | 0.17906 | -0.0045844 | -0.0079253 | 0.0056246 | 0.060532 | -0.0043685 | 0.066984 | -61.0657 | 62.1597 | -61.235 | -61.171 | 61.7706 | -0.036621 | -0.059509 | 0.082397 | 62.0911 | -61.2534 | -0.30212 | 0.10986 | -0.13275 | -0.23804 | -0.27924 | -0.32044 | 0.041198 | 0.16937 | 60.8734 | 61.0153 | 122.7036 | 123.0927 | -0.13275 | 123.024 | 60.8963 | -0.32044 | 123.0927 | -0.13275 | 60.8963 | 122.7036 | 123.024 | -123.2849 | -123.3032
2283.7656 | 123.1201 | -60.9467 | 62.0453 | 0.19432 | -0.0052252 | -0.0066437 | 0.005411 | 0.0616 | -0.0047957 | 0.06912 | -61.0703 | 62.1964 | -61.2625 | -61.2076 | 61.7386 | -0.045776 | -0.004578 | 0.050354 | 62.1094 | -61.2396 | -0.31586 | 0.15106 | -0.1236 | -0.26093 | -0.3067 | -0.29297 | 0.064087 | 0.19226 | 60.9421 | 60.997 | 122.6852 | 123.143 | -0.1236 | 123.056 | 60.9009 | -0.29297 | 123.143 | -0.1236 | 60.9009 | 122.6852 | 123.056 | -123.3078 | -123.2849
2284.7656 | 123.1247 | -60.9192 | 62.0499 | 0.20195 | -0.0050116 | -0.0062163 | 0.0056246 | 0.062028 | -0.0045821 | 0.068052 | -61.3129 | 62.1368 | -61.2625 | -61.171 | 61.7935 | -0.041199 | -0.004578 | 0.041199 | 62.1094 | -61.2167 | -0.34332 | 0.086975 | -0.39368 | -0.25177 | -0.25635 | -0.29755 | 0.059509 | -0.050354 | 60.9146 | 60.9604 | 122.7127 | 123.056 | -0.39368 | 123.0286 | 60.878 | -0.29755 | 123.056 | -0.39368 | 60.878 | 122.7127 | 123.0286 | -123.3124 | -123.2666
2285.7656 | 123.1384 | -60.9238 | 62.0316 | 0.19432 | -0.0039434 | -0.0085663 | 0.0056246 | 0.063523 | -0.0018051 | 0.068479 | -61.0748 | 62.1826 | -61.2305 | -61.1984 | 61.7706 | -0.045776 | -0.054932 | 0.059509 | 62.0865 | -61.2213 | -0.3067 | 0.15106 | -0.15106 | -0.27466 | -0.26093 | -0.29755 | 0.054932 | 0.15564 | 60.8688 | 60.9833 | 122.6944 | 123.1064 | -0.15106 | 123.0103 | 60.878 | -0.29755 | 123.1064 | -0.15106 | 60.878 | 122.6944 | 123.0103 | -123.262 | -123.2529
2286.7656 | 123.1155 | -60.9375 | 62.0316 | 0.1638 | -0.0033026 | -0.0089935 | 0.0041292 | 0.063096 | -0.0050095 | 0.067411 | -61.0611 | 62.1918 | -61.2305 | -61.1801 | 61.7615 | -0.041199 | -0.032043 | 0.059509 | 62.114 | -61.235 | -0.29297 | 0.16022 | -0.1236 | -0.24262 | -0.27008 | -0.29755 | 0.082398 | 0.16937 | 60.9055 | 60.997 | 122.699 | 123.1293 | -0.1236 | 123.0515 | 60.8963 | -0.29755 | 123.1293 | -0.1236 | 60.8963 | 122.699 | 123.0515 | -123.262 | -123.2666
2287.7656 | 123.1567 | -60.9192 | 62.0041 | 0.25536 | -0.004798 | -0.0074981 | 0.0041292 | 0.063737 | -0.0052231 | 0.068906 | -61.0519 | 62.1506 | -61.2442 | -61.1618 | 61.7981 | -0.036621 | -0.10986 | 0.10529 | 62.0819 | -61.1984 | -0.32501 | 0.14648 | -0.13275 | -0.24261 | -0.20599 | -0.27924 | 0.07782 | 0.19226 | 60.8093 | 61.0245 | 122.7173 | 123.0698 | -0.13275 | 123.0011 | 60.8826 | -0.27924 | 123.0698 | -0.13275 | 60.8826 | 122.7173 | 123.0011 | -123.2483 | -123.2025
2288.7812 | 123.1613 | -60.8963 | 62.0316 | 0.17143 | -0.0067206 | -0.013052 | -0.0029202 | 0.062455 | -0.0067185 | 0.069761 | -61.0703 | 62.0682 | -61.2305 | -61.1435 | 61.821 | 0.018311 | -0.059509 | 0.15564 | 62.1002 | -61.171 | -0.33417 | 0.036621 | -0.17395 | -0.24719 | -0.21057 | -0.27466 | 0.068665 | 0.16022 | 60.8368 | 61.0519 | 122.7173 | 122.9645 | -0.17395 | 122.9965 | 60.9146 | -0.27466 | 122.9645 | -0.17395 | 60.9146 | 122.7173 | 122.9965 | -123.262 | -123.2025
2289.7656 | 123.1567 | -60.9192 | 62.0361 | 0.17143 | -0.0050116 | -0.0079253 | 0.0041292 | 0.0616 | -0.0033005 | 0.066984 | -61.0519 | 62.1872 | -61.2213 | -61.1847 | 61.7615 | -0.032043 | -0.068665 | 0.059509 | 62.1094 | -61.2305 | -0.30212 | 0.15106 | -0.13275 | -0.2655 | -0.27466 | -0.31128 | 0.073242 | 0.16937 | 60.8505 | 60.9787 | 122.6807 | 123.1064 | -0.13275 | 123.0286 | 60.8871 | -0.31128 | 123.1064 | -0.13275 | 60.8871 | 122.6807 | 123.0286 | -123.2574 | -123.2666
2290.7656 | 123.143 | -60.9329 | 62.0316 | 0.21721 | -0.0039434 | -0.0045075 | 0.0073336 | 0.063096 | -0.0058639 | 0.068052 | -61.0519 | 62.1872 | -61.2305 | -61.203 | 61.7661 | -0.054932 | -0.013733 | 0.068665 | 62.1185 | -61.2259 | -0.29755 | 0.15564 | -0.11902 | -0.27008 | -0.2655 | -0.29297 | 0.086975 | 0.17853 | 60.9192 | 61.0016 | 122.699 | 123.1201 | -0.11902 | 123.0515 | 60.878 | -0.29297 | 123.1201 | -0.11902 | 60.878 | 122.699 | 123.0515 | -123.262 | -123.2574
2291.7656 | 123.1064 | -60.9283 | 62.0728 | 0.095139 | -0.0054388 | -0.0089935 | 0.0069064 | 0.062455 | -0.0035141 | 0.065275 | -61.0703 | 62.1964 | -61.2167 | -61.2122 | 61.7523 | -0.064087 | 0.027466 | 0.068665 | 62.1323 | -61.235 | -0.28839 | 0.1236 | -0.14191 | -0.28381 | -0.32044 | -0.3067 | 0.059509 | 0.14648 | 60.9558 | 60.997 | 122.6807 | 123.1247 | -0.14191 | 123.0606 | 60.8643 | -0.3067 | 123.1247 | -0.14191 | 60.8643 | 122.6807 | 123.0606 | -123.2895 | -123.3078
2292.7656 | 123.1338 | -60.9192 | 62.0453 | 0.19432 | -0.0035162 | -0.0077117 | 0.004343 | 0.063096 | -0.0054367 | 0.070402 | -61.0794 | 62.1735 | -61.2534 | -61.203 | 61.6882 | -0.28381 | 0.022888 | 0.25177 | 62.1094 | -61.2671 | -0.33417 | 0.12817 | -0.16022 | -0.28381 | -0.35706 | -0.3479 | 0.064087 | 0.17395 | 60.9421 | 61.171 | 122.6074 | 123.0927 | -0.16022 | 123.0286 | 60.6354 | -0.3479 | 123.0927 | -0.16022 | 60.6354 | 122.6074 | 123.0286 | -123.2986 | -123.3124
2293.7812 | 123.2162 | -60.8505 | 62.0407 | 1.4532 | -0.0090704 | -0.0089935 | -0.0027066 | 0.061387 | -0.0047957 | 0.067624 | -61.0107 | 62.1048 | -61.2076 | -61.0748 | 61.9171 | 0.15564 | -0.013733 | 0.30212 | 62.1185 | -61.1664 | -0.35706 | 0.064087 | -0.16022 | -0.2243 | -0.1236 | -0.31586 | 0.07782 | 0.19684 | 60.8368 | 61.1526 | 122.7676 | 122.9553 | -0.16022 | 122.9691 | 61.0062 | -0.31586 | 122.9553 | -0.16022 | 61.0062 | 122.7676 | 122.9691 | -123.2483 | -123.2071
2294.7656 | 123.0972 | -60.9375 | 62.0453 | 0.1638 | -0.0060798 | -0.0066437 | 0.005411 | 0.062669 | -0.0054367 | 0.067838 | -61.0794 | 62.178 | -61.235 | -61.2305 | 61.7203 | -0.064087 | 0.013733 | 0.064087 | 62.1277 | -61.2717 | -0.29755 | 0.13275 | -0.14191 | -0.29297 | -0.32501 | -0.33417 | 0.082398 | 0.15564 | 60.9512 | 61.0016 | 122.6578 | 123.1155 | -0.14191 | 123.0652 | 60.8734 | -0.33417 | 123.1155 | -0.14191 | 60.8734 | 122.6578 | 123.0652 | -123.2803 | -123.317
2295.7656 | 123.1064 | -60.9375 | 62.0407 | 0.11803 | -0.0035162 | -0.0057891 | 0.0047702 | 0.064378 | -0.0062911 | 0.06677 | -61.0611 | 62.2055 | -61.2534 | -61.203 | 61.7477 | -0.064087 | 0.036621 | 0.050354 | 62.1094 | -61.2488 | -0.31586 | 0.1648 | -0.1236 | -0.2655 | -0.29297 | -0.31128 | 0.068665 | 0.19226 | 60.9741 | 60.9879 | 122.6852 | 123.143 | -0.1236 | 123.0469 | 60.8734 | -0.31128 | 123.143 | -0.1236 | 60.8734 | 122.6852 | 123.0469 | -123.2941 | -123.2895
2296.7656 | 123.1705 | -60.9375 | 62.0361 | 0.24773 | -0.0043708 | -0.0098479 | 0.005411 | 0.063096 | -0.0047957 | 0.069547 | -61.0657 | 62.2284 | -61.2396 | -61.2305 | 61.7477 | -0.068665 | -0.059509 | -0.30212 | 62.0544 | -61.2762 | -0.30212 | 0.19226 | -0.12817 | -0.29297 | -0.28839 | -0.33875 | 0.01831 | 0.17395 | 60.878 | 60.6354 | 122.6852 | 123.1659 | -0.12817 | 122.9919 | 60.8688 | -0.33875 | 123.1659 | -0.12817 | 60.8688 | 122.6852 | 122.9919 | -123.2758 | -123.3124
2297.7656 | 123.0972 | -60.9055 | 62.0361 | 0.11803 | -0.0041572 | -0.010916 | 0.004343 | 0.064164 | -0.0030869 | 0.068479 | -61.0199 | 62.2009 | -61.2396 | -61.1801 | 61.7706 | -0.018311 | 0.022888 | 0.10071 | 62.1277 | -61.2534 | -0.33417 | 0.16479 | -0.11444 | -0.27466 | -0.2655 | -0.3479 | 0.091553 | 0.21973 | 60.9283 | 61.0062 | 122.6761 | 123.1064 | -0.11444 | 123.0331 | 60.8871 | -0.3479 | 123.1064 | -0.11444 | 60.8871 | 122.6761 | 123.0331 | -123.2758 | -123.2895
2298.7812 | 123.2437 | -60.9009 | 62.0361 | 0.087509 | -0.0069342 | -0.010916 | -0.0065518 | 0.060532 | -0.0030869 | 0.068479 | -61.0474 | 62.146 | -61.1801 | -61.1526 | 61.8301 | 0.036621 | -0.064087 | 0.16937 | 62.1094 | -61.1984 | -0.27924 | 0.10986 | -0.14648 | -0.25177 | -0.20599 | -0.29755 | 0.073242 | 0.13275 | 60.8368 | 61.0703 | 122.731 | 123.0469 | -0.14648 | 123.0103 | 60.9375 | -0.29755 | 123.0469 | -0.14648 | 60.9375 | 122.731 | 123.0103 | -123.2162 | -123.2346
2299.7656 | 123.0881 | -60.9558 | 62.059 | 0.095139 | -0.0054388 | -0.0074981 | 0.0073336 | 0.063309 | -0.0054367 | 0.067411 | -61.0565 | 62.2375 | -61.2305 | -61.1893 | 61.7294 | -0.073242 | 0.022888 | 0.068665 | 62.1323 | -61.2671 | -0.27466 | 0.17853 | -0.10071 | -0.23346 | -0.32959 | -0.31128 | 0.073242 | 0.17395 | 60.9787 | 61.0245 | 122.6852 | 123.1934 | -0.10071 | 123.0881 | 60.8826 | -0.31128 | 123.1934 | -0.10071 | 60.8826 | 122.6852 | 123.0881 | -123.2895 | -123.3261
2300.7656 | 123.0972 | -60.9421 | 62.0728 | 0.14092 | -0.0045844 | -0.0079253 | 0.0056246 | 0.061814 | -0.0060775 | 0.065916 | -61.0428 | 62.2192 | -61.235 | -61.1938 | 61.7432 | -0.022888 | 0.018311 | 0.10071 | 62.1185 | -61.2762 | -0.29297 | 0.14648 | -0.10071 | -0.25177 | -0.32959 | -0.33417 | 0.045776 | 0.19226 | 60.9604 | 61.0428 | 122.6852 | 123.1613 | -0.10071 | 123.0606 | 60.9192 | -0.33417 | 123.1613 | -0.10071 | 60.9192 | 122.6852 | 123.0606 | -123.3078 | -123.349
2301.7656 | 123.0927 | -60.9192 | 62.0453 | 0.064621 | -0.0041572 | -0.0081389 | 0.0034884 | 0.063523 | -0.0033005 | 0.066343 | -61.0245 | 62.2055 | -61.235 | -61.1664 | 61.7706 | -0.018311 | 0.027466 | 0.10986 | 62.1185 | -61.2488 | -0.31586 | 0.16022 | -0.10529 | -0.24719 | -0.27466 | -0.32959 | 0.073242 | 0.21057 | 60.9467 | 61.0291 | 122.6898 | 123.1247 | -0.10529 | 123.0377 | 60.9009 | -0.32959 | 123.1247 | -0.10529 | 60.9009 | 122.6898 | 123.0377 | -123.2803 | -123.2941
2302.7656 | 123.1155 | -60.9055 | 62.059 | 0.095139 | -0.0041572 | -0.0094207 | 0.0051974 | 0.06096 | -0.0045821 | 0.06677 | -61.0245 | 62.2238 | -61.2442 | -61.1526 | 61.7889 | -0.013733 | 0.013733 | 0.13275 | 62.1323 | -61.2717 | -0.33875 | 0.16479 | -0.11902 | -0.24719 | -0.27008 | -0.36621 | 0.073242 | 0.21973 | 60.9192 | 61.0382 | 122.6944 | 123.1293 | -0.11902 | 123.0377 | 60.8917 | -0.36621 | 123.1293 | -0.11902 | 60.8917 | 122.6944 | 123.0377 | -123.3032 | -123.3307
2303.7656 | 123.1018 | -60.91 | 62.0544 | 0.018845 | -0.0033026 | -0.0055755 | 0.004343 | 0.064591 | -0.0050095 | 0.068265 | -61.0153 | 62.2055 | -61.2259 | -61.1435 | 61.7935 | 0.013733 | 0.018311 | 0.15106 | 62.1414 | -61.2442 | -0.31586 | 0.15106 | -0.10529 | -0.23346 | -0.26093 | -0.33417 | 0.086975 | 0.21057 | 60.9283 | 61.0611 | 122.7036 | 123.1155 | -0.10529 | 123.0515 | 60.9238 | -0.33417 | 123.1155 | -0.10529 | 60.9238 | 122.7036 | 123.0515 | -123.2803 | -123.2986
2304.7656 | 123.1567 | -60.9329 | 62.0636 | -0.065079 | -0.0054388 | -0.010275 | 0.0064792 | 0.063737 | -0.0047957 | 0.067197 | -61.0062 | 62.2055 | -61.2213 | -61.1435 | 61.7981 | 0.032043 | 0.032043 | 0.15564 | 62.1368 | -61.2305 | -0.28839 | 0.14191 | -0.073243 | -0.21057 | -0.2655 | -0.29755 | 0.073242 | 0.21515 | 60.965 | 61.0886 | 122.731 | 123.1384 | -0.073243 | 123.0698 | 60.965 | -0.29755 | 123.1384 | -0.073243 | 60.965 | 122.731 | 123.0698 | -123.2849 | -123.2941
2305.7656 | 123.1476 | -60.9055 | 62.0728 | 0.59868 | -0.0039434 | -0.0055755 | 0.0075472 | 0.062669 | -0.0041549 | 0.066556 | -60.997 | 62.178 | -61.235 | -61.1298 | 61.8164 | 0.059509 | 0.013733 | 0.17853 | 62.1506 | -61.235 | -0.32959 | 0.10529 | -0.091552 | -0.2243 | -0.25635 | -0.32959 | 0.07782 | 0.23804 | 60.9192 | 61.084 | 122.7219 | 123.0835 | -0.091552 | 123.056 | 60.965 | -0.32959 | 123.0835 | -0.091552 | 60.965 | 122.7219 | 123.056 | -123.3078 | -123.3078
2306.7656 | 123.111 | -60.9192 | 62.0453 | 0.13329 | -0.0037298 | -0.011771 | 0.0041292 | 0.064591 | -0.0054367 | 0.068693 | -61.0794 | 62.2101 | -61.2259 | -61.2213 | 61.7477 | -0.050354 | 0.032043 | 0.054932 | 62.1323 | -61.2671 | -0.3067 | 0.16479 | -0.16022 | -0.30212 | -0.29755 | -0.3479 | 0.086975 | 0.14648 | 60.9512 | 60.9741 | 122.6669 | 123.1293 | -0.16022 | 123.0515 | 60.8688 | -0.3479 | 123.1293 | -0.16022 | 60.8688 | 122.6669 | 123.0515 | -123.2712 | -123.3124
2307.7656 | 123.0835 | -60.9055 | 62.0636 | 0.11803 | -0.003089 | -0.011557 | 0.004343 | 0.063737 | -0.0041549 | 0.066984 | -61.0474 | 62.2375 | -61.2167 | -61.203 | 61.7432 | -0.068665 | 0.022888 | 0.073242 | 62.1368 | -61.2717 | -0.31128 | 0.17395 | -0.14191 | -0.29755 | -0.32044 | -0.36621 | 0.073242 | 0.16937 | 60.9283 | 60.9787 | 122.6486 | 123.143 | -0.14191 | 123.0423 | 60.8368 | -0.36621 | 123.143 | -0.14191 | 60.8368 | 122.6486 | 123.0423 | -123.2803 | -123.3353
2308.7656 | 123.0789 | -60.9146 | 62.0636 | 0.1104 | -0.0022346 | -0.010275 | 0.0064792 | 0.062882 | -0.0030869 | 0.069547 | -61.0474 | 62.2192 | -61.203 | -61.2122 | 61.7523 | -0.032043 | 0.050354 | 0.07782 | 62.1368 | -61.2854 | -0.28839 | 0.15564 | -0.13275 | -0.29755 | -0.31128 | -0.37079 | 0.073242 | 0.15564 | 60.965 | 60.9924 | 122.6669 | 123.1338 | -0.13275 | 123.0515 | 60.8826 | -0.37079 | 123.1338 | -0.13275 | 60.8826 | 122.6669 | 123.0515 | -123.2666 | -123.349
2309.7656 | 123.1384 | -60.91 | 62.0499 | -0.33211 | -0.0050116 | -0.0098479 | 0.0045566 | 0.064378 | -0.0045821 | 0.066129 | -61.0062 | 62.2192 | -61.2259 | -61.1664 | 61.8027 | 0.045776 | 0.022888 | 0.17395 | 62.1185 | -61.2534 | -0.31586 | 0.16937 | -0.096131 | -0.25635 | -0.24719 | -0.34332 | 0.068664 | 0.21973 | 60.9329 | 61.084 | 122.7127 | 123.1293 | -0.096131 | 123.0286 | 60.9558 | -0.34332 | 123.1293 | -0.096131 | 60.9558 | 122.7127 | 123.0286 | -123.2758 | -123.3032
2310.7656 | 123.1247 | -60.91 | 62.0636 | 0.14092 | -0.004798 | -0.010275 | 0.0049838 | 0.061173 | -0.0015915 | 0.069974 | -61.0336 | 62.233 | -61.2396 | -61.1801 | 61.7706 | -0.009155 | 0.027466 | 0.1236 | 62.1277 | -61.2946 | -0.32959 | 0.16937 | -0.1236 | -0.27008 | -0.29297 | -0.38452 | 0.064087 | 0.20599 | 60.9375 | 61.0336 | 122.6807 | 123.143 | -0.1236 | 123.0377 | 60.9009 | -0.38452 | 123.143 | -0.1236 | 60.9009 | 122.6807 | 123.0377 | -123.3032 | -123.3582
2311.7656 | 123.1018 | -60.8963 | 62.0499 | 0.10277 | -0.0052252 | -0.010489 | 0.0056246 | 0.066514 | -0.0054367 | 0.068265 | -61.0107 | 62.2101 | -61.2122 | -61.171 | 61.7981 | -0.009155 | -0.004578 | 0.10986 | 62.1323 | -61.2579 | -0.31586 | 0.16022 | -0.11444 | -0.27466 | -0.25177 | -0.36163 | 0.082397 | 0.20142 | 60.8917 | 61.0062 | 122.6944 | 123.1064 | -0.11444 | 123.0286 | 60.8871 | -0.36163 | 123.1064 | -0.11444 | 60.8871 | 122.6944 | 123.0286 | -123.262 | -123.3078
2312.7656 | 123.0927 | -60.91 | 62.0544 | 0.056992 | -0.0020208 | -0.0096343 | 0.0060518 | 0.060532 | -0.0041549 | 0.068052 | -61.0153 | 62.2192 | -61.1984 | -61.1618 | 61.7844 | 0.004578 | 0.022888 | 0.13733 | 62.1185 | -61.2579 | -0.28839 | 0.16479 | -0.10529 | -0.25177 | -0.27008 | -0.3479 | 0.064087 | 0.1831 | 60.9329 | 61.0474 | 122.6944 | 123.1293 | -0.10529 | 123.0286 | 60.9146 | -0.3479 | 123.1293 | -0.10529 | 60.9146 | 122.6944 | 123.0286 | -123.2529 | -123.3124
2313.7656 | 123.1018 | -60.9238 | 62.0728 | 0.07988 | -0.0037298 | -0.0077117 | 0.0066928 | 0.064805 | -0.0039413 | 0.067197 | -61.0474 | 62.1918 | -61.2396 | -61.1984 | 61.734 | -0.036621 | 0.022888 | 0.07782 | 62.1368 | -61.2579 | -0.31586 | 0.11902 | -0.1236 | -0.27466 | -0.33875 | -0.33417 | 0.064087 | 0.19226 | 60.9467 | 61.0016 | 122.6578 | 123.1155 | -0.1236 | 123.0606 | 60.8871 | -0.33417 | 123.1155 | -0.1236 | 60.8871 | 122.6578 | 123.0606 | -123.3124 | -123.3307
2314.7656 | 123.1201 | -60.9558 | 62.0544 | 0.018845 | -0.0022346 | -0.0062163 | 0.0039156 | 0.063523 | -0.0035141 | 0.065275 | -61.0474 | 62.2238 | -61.2305 | -61.1984 | 61.7615 | -0.022888 | 0.036621 | 0.082397 | 62.1231 | -61.2534 | -0.27466 | 0.16937 | -0.091552 | -0.24261 | -0.29297 | -0.29755 | 0.068665 | 0.18311 | 60.9924 | 61.0382 | 122.7173 | 123.1796 | -0.091552 | 123.0789 | 60.9329 | -0.29755 | 123.1796 | -0.091552 | 60.9329 | 122.7173 | 123.0789 | -123.2849 | -123.3078
2315.7656 | 123.1293 | -60.9375 | 62.0499 | 0.10277 | -0.0028754 | -0.0055755 | 0.0066928 | 0.063737 | -0.0043685 | 0.068693 | -61.0199 | 62.2101 | -61.2579 | -61.1664 | 61.7523 | -0.013733 | 0.022888 | 0.10071 | 62.146 | -61.2488 | -0.32044 | 0.16022 | -0.082397 | -0.22888 | -0.29755 | -0.31128 | 0.09613 | 0.23804 | 60.9604 | 61.0382 | 122.6898 | 123.1476 | -0.082397 | 123.0835 | 60.9238 | -0.31128 | 123.1476 | -0.082397 | 60.9238 | 122.6898 | 123.0835 | -123.3078 | -123.2986
2316.7656 | 123.1201 | -60.9283 | 62.0773 | 0.07988 | -0.0037298 | -0.0032257 | 0.0049838 | 0.06096 | -0.0030869 | 0.069333 | -61.0428 | 62.2147 | -61.2305 | -61.1847 | 61.7661 | -0.018311 | 0.018311 | 0.12817 | 62.1414 | -61.2579 | -0.30212 | 0.13733 | -0.11444 | -0.25635 | -0.31128 | -0.32959 | 0.064086 | 0.18768 | 60.9467 | 61.0565 | 122.6944 | 123.143 | -0.11444 | 123.0698 | 60.91 | -0.32959 | 123.143 | -0.11444 | 60.91 | 122.6944 | 123.0698 | -123.3078 | -123.3353
2317.7656 | 123.1247 | -60.91 | 62.0544 | 0.041733 | -0.0052252 | -0.0042937 | 0.0051974 | 0.063737 | -0.0028731 | 0.06677 | -61.0153 | 62.2101 | -61.2305 | -61.1618 | 61.7661 | -0.009155 | 0.013733 | 0.14648 | 62.1552 | -61.2488 | -0.32043 | 0.15564 | -0.10529 | -0.25177 | -0.28839 | -0.33874 | 0.10071 | 0.21515 | 60.9238 | 61.0565 | 122.6761 | 123.1201 | -0.10529 | 123.0652 | 60.9009 | -0.33874 | 123.1201 | -0.10529 | 60.9009 | 122.6761 | 123.0652 | -123.2849 | -123.3032
2318.7656 | 123.1476 | -60.9238 | 62.059 | 0.072251 | -0.0018072 | -0.01113 | 0.0069064 | 0.064591 | -0.0060775 | 0.067624 | -61.0016 | 62.233 | -61.2259 | -61.1618 | 61.7889 | 0.022888 | 0.027466 | 0.14648 | 62.1414 | -61.2579 | -0.30212 | 0.17395 | -0.07782 | -0.23804 | -0.27008 | -0.33417 | 0.082397 | 0.2243 | 60.9512 | 61.0703 | 122.7127 | 123.1567 | -0.07782 | 123.0652 | 60.9467 | -0.33417 | 123.1567 | -0.07782 | 60.9467 | 122.7127 | 123.0652 | -123.2849 | -123.317
2319.7656 | 123.143 | -60.9055 | 62.0453 | 0.026474 | -0.0052252 | -0.0038665 | 0.003702 | 0.063309 | -0.0054367 | 0.066984 | -60.9833 | 62.2238 | -61.1984 | -61.1389 | 61.7844 | 0.032043 | 0.009155 | 0.16479 | 62.1643 | -61.2717 | -0.29297 | 0.17853 | -0.077819 | -0.23346 | -0.26093 | -0.36621 | 0.11902 | 0.21515 | 60.9146 | 61.0703 | 122.6898 | 123.1293 | -0.077819 | 123.0698 | 60.9375 | -0.36621 | 123.1293 | -0.077819 | 60.9375 | 122.6898 | 123.0698 | -123.2437 | -123.317
2320.7656 | 123.1201 | -60.9146 | 62.0499 | 0.087509 | -0.0022346 | -0.0098479 | 0.0051974 | 0.062241 | -0.0024459 | 0.067624 | -61.0153 | 62.2147 | -61.2534 | -61.1755 | 61.7752 | -0.004578 | 0.022888 | 0.1236 | 62.1368 | -61.2579 | -0.33875 | 0.16479 | -0.10071 | -0.26093 | -0.27466 | -0.34332 | 0.086975 | 0.23804 | 60.9375 | 61.0382 | 122.6898 | 123.1293 | -0.10071 | 123.0515 | 60.91 | -0.34332 | 123.1293 | -0.10071 | 60.91 | 122.6898 | 123.0515 | -123.3032 | -123.3078
2321.7656 | 123.0972 | -60.9009 | 62.0544 | 0.026474 | -0.0045844 | -0.0074981 | 0.0039156 | 0.0616 | -0.0037277 | 0.068479 | -61.0153 | 62.2055 | -61.2213 | -61.1664 | 61.7798 | 0 | 0.013733 | 0.13275 | 62.1368 | -61.235 | -0.32043 | 0.15106 | -0.11444 | -0.2655 | -0.27466 | -0.33417 | 0.082398 | 0.20599 | 60.9146 | 61.0336 | 122.6807 | 123.1064 | -0.11444 | 123.0377 | 60.9009 | -0.33417 | 123.1064 | -0.11444 | 60.9009 | 122.6807 | 123.0377 | -123.2758 | -123.2895
2322.7656 | 123.1293 | -60.9238 | 62.0499 | 0.018845 | -0.0050116 | -0.012625 | 0.0062656 | 0.062669 | -0.0037277 | 0.066984 | -61.0062 | 62.2284 | -61.203 | -61.1435 | 61.7844 | 0.018311 | 0.050354 | 0.14191 | 62.1368 | -61.2762 | -0.27924 | 0.17853 | -0.082398 | -0.21973 | -0.2655 | -0.35248 | 0.086975 | 0.19684 | 60.9741 | 61.0657 | 122.7081 | 123.1522 | -0.082398 | 123.0606 | 60.9421 | -0.35248 | 123.1522 | -0.082398 | 60.9421 | 122.7081 | 123.0606 | -123.2529 | -123.3261
2323.7656 | 123.1476 | -60.91 | 62.0499 | 0.0035856 | -0.0067206 | -0.0070709 | 0.0032748 | 0.061173 | -0.0065047 | 0.066556 | -61.0748 | 62.1964 | -61.235 | -61.1526 | 61.7981 | 0.059509 | 0.004578 | 0.20599 | 62.1597 | -61.235 | -0.32501 | 0.14648 | -0.16479 | -0.24261 | -0.25177 | -0.32501 | 0.10986 | 0.16022 | 60.9146 | 61.116 | 122.7081 | 123.1064 | -0.16479 | 123.0698 | 60.9695 | -0.32501 | 123.1064 | -0.16479 | 60.9695 | 122.7081 | 123.0698 | -123.2849 | -123.2849
2324.7812 | 123.0927 | -60.9329 | 62.0544 | 0.07988 | -0.0041572 | -0.0096343 | 0.0060518 | 0.0616 | -0.0060775 | 0.065916 | -61.0794 | 62.233 | -61.235 | -61.235 | 61.734 | -0.064087 | 0.018311 | 0.050354 | 62.1368 | -61.29 | -0.30212 | 0.17853 | -0.14649 | -0.30212 | -0.32043 | -0.35706 | 0.082398 | 0.15564 | 60.9512 | 60.9833 | 122.6669 | 123.1659 | -0.14649 | 123.0698 | 60.8688 | -0.35706 | 123.1659 | -0.14649 | 60.8688 | 122.6669 | 123.0698 | -123.2895 | -123.3444
2325.7656 | 123.1476 | -60.9055 | 62.059 | -0.04219 | -0.0060798 | -0.0055755 | 0.0049838 | 0.06096 | -0.0052231 | 0.067197 | -60.997 | 62.233 | -61.2167 | -61.1206 | 61.8164 | 0.059509 | 0.027466 | 0.21515 | 62.1552 | -61.2122 | -0.31128 | 0.17395 | -0.091552 | -0.21515 | -0.24262 | -0.3067 | 0.09613 | 0.21973 | 60.9329 | 61.1206 | 122.7219 | 123.1384 | -0.091552 | 123.0606 | 60.965 | -0.3067 | 123.1384 | -0.091552 | 60.965 | 122.7219 | 123.0606 | -123.2758 | -123.2712
2326.7656 | 123.1293 | -60.8826 | 62.0636 | -0.087967 | -0.0039434 | -0.010703 | 0.0028476 | 0.063523 | -0.0069321 | 0.06442 | -61.0107 | 62.2238 | -61.203 | -61.1206 | 61.8073 | 0.082397 | 0.054932 | 0.21515 | 62.1323 | -61.2488 | -0.32044 | 0.16022 | -0.12817 | -0.23804 | -0.25635 | -0.36621 | 0.068664 | 0.19226 | 60.9375 | 61.0977 | 122.6898 | 123.1064 | -0.12817 | 123.0148 | 60.965 | -0.36621 | 123.1064 | -0.12817 | 60.965 | 122.6898 | 123.0148 | -123.2666 | -123.3124
2327.7656 | 123.1064 | -60.9009 | 62.0544 | -0.04219 | -0.0062934 | -0.0085663 | 0.004343 | 0.063096 | -0.0043685 | 0.065488 | -60.9879 | 62.2101 | -61.2259 | -61.1252 | 61.821 | 0.054932 | 0.009155 | 0.19226 | 62.1414 | -61.2396 | -0.32501 | 0.15564 | -0.086975 | -0.2243 | -0.23346 | -0.33874 | 0.086975 | 0.23804 | 60.91 | 61.0931 | 122.7219 | 123.111 | -0.086975 | 123.0423 | 60.9558 | -0.33874 | 123.111 | -0.086975 | 60.9558 | 122.7219 | 123.0423 | -123.2803 | -123.2941
2328.7656 | 123.1613 | -60.9146 | 62.0865 | -0.080337 | -0.004798 | -0.0038665 | 0.004343 | 0.060746 | -0.0052231 | 0.068693 | -61.0016 | 62.2421 | -61.1938 | -61.1343 | 61.8164 | 0.054932 | 0.041199 | 0.20142 | 62.1506 | -61.2396 | -0.27924 | 0.15564 | -0.086975 | -0.21973 | -0.27008 | -0.32501 | 0.064087 | 0.19226 | 60.9558 | 61.116 | 122.731 | 123.1567 | -0.086975 | 123.0652 | 60.9695 | -0.32501 | 123.1567 | -0.086975 | 60.9695 | 122.731 | 123.0652 | -123.2803 | -123.3261
2329.7656 | 123.1659 | -60.9009 | 62.0499 | -0.10323 | -0.005866 | -0.0074981 | 0.004343 | 0.062241 | -0.0045821 | 0.066129 | -61.0199 | 62.2055 | -61.235 | -61.1343 | 61.8164 | 0.073242 | 0.064087 | 0.2243 | 62.1643 | -61.2076 | -0.33417 | 0.15564 | -0.11902 | -0.23346 | -0.23346 | -0.3067 | 0.11444 | 0.21515 | 60.965 | 61.1252 | 122.7173 | 123.1064 | -0.11902 | 123.0652 | 60.9741 | -0.3067 | 123.1064 | -0.11902 | 60.9741 | 122.7173 | 123.0652 | -123.2849 | -123.2574
2330.7656 | 123.1155 | -60.9375 | 62.0544 | 0.095139 | -0.0035162 | -0.0096343 | 0.0049838 | 0.061814 | -0.0037277 | 0.066343 | -61.0336 | 62.2009 | -61.2305 | -61.1801 | 61.7752 | -0.022888 | 0 | 0.10071 | 62.146 | -61.2534 | -0.29297 | 0.14648 | -0.09613 | -0.24262 | -0.27923 | -0.31586 | 0.091553 | 0.19684 | 60.9375 | 61.0382 | 122.7127 | 123.1384 | -0.09613 | 123.0835 | 60.9146 | -0.31586 | 123.1384 | -0.09613 | 60.9146 | 122.7127 | 123.0835 | -123.2849 | -123.3078
2331.7656 | 123.1384 | -60.9055 | 62.0865 | -0.15663 | -0.0077888 | -0.0096343 | 0.0041292 | 0.063309 | -0.0054367 | 0.066343 | -61.0474 | 62.1964 | -61.2167 | -61.1664 | 61.7935 | 0.045776 | 0.11902 | 0.19226 | 62.1826 | -61.1984 | -0.31128 | 0.10986 | -0.14191 | -0.26093 | -0.29297 | -0.29297 | 0.09613 | 0.16937 | 61.0245 | 61.0977 | 122.699 | 123.1018 | -0.14191 | 123.0881 | 60.9512 | -0.29297 | 123.1018 | -0.14191 | 60.9512 | 122.699 | 123.0881 | -123.3032 | -123.2849
2332.7812 | 123.1476 | -60.8871 | 62.059 | -0.11848 | -0.0039434 | -0.011557 | 0.0041292 | 0.060746 | -0.0062911 | 0.067411 | -61.0245 | 62.2055 | -61.2076 | -61.1343 | 61.8164 | 0.068665 | 0.07782 | 0.21057 | 62.1323 | -61.2534 | -0.32043 | 0.14648 | -0.13733 | -0.24719 | -0.24262 | -0.36621 | 0.073242 | 0.18311 | 60.965 | 61.0977 | 122.7036 | 123.0927 | -0.13733 | 123.0194 | 60.9558 | -0.36621 | 123.0927 | -0.13733 | 60.9558 | 122.7036 | 123.0194 | -123.2666 | -123.3124
2333.7656 | 123.1201 | -60.9238 | 62.0911 | -0.17952 | -0.0069342 | -0.0089935 | -0.0037748 | 0.060105 | -0.0024459 | 0.067197 | -61.0565 | 62.2147 | -61.2396 | -61.2442 | 61.7615 | 0.032043 | 0.10986 | 0.16937 | 62.1826 | -61.2259 | -0.31586 | 0.1236 | -0.13275 | -0.32044 | -0.32959 | -0.30212 | 0.091553 | 0.1831 | 61.0336 | 61.0931 | 122.6852 | 123.1384 | -0.13275 | 123.1064 | 60.9558 | -0.30212 | 123.1384 | -0.13275 | 60.9558 | 122.6852 | 123.1064 | -123.3307 | -123.317
2334.7656 | 123.1064 | -60.9009 | 62.0728 | -0.16426 | -0.006507 | -0.0081389 | 0.00071144 | 0.059678 | -0.0035141 | 0.067838 | -61.0474 | 62.2055 | -61.2259 | -61.1755 | 61.8073 | 0.045776 | 0.13275 | 0.19226 | 62.1597 | -61.235 | -0.32501 | 0.13275 | -0.14648 | -0.27466 | -0.2655 | -0.33417 | 0.086975 | 0.17853 | 61.0336 | 61.0931 | 122.7081 | 123.1064 | -0.14648 | 123.0606 | 60.9467 | -0.33417 | 123.1064 | -0.14648 | 60.9467 | 122.7081 | 123.0606 | -123.2986 | -123.3078
2335.7656 | 123.1293 | -60.9055 | 62.1094 | -0.17952 | -0.010993 | -0.014761 | 0.00049764 | 0.063523 | -0.0024459 | 0.064847 | -60.8734 | 62.2421 | -61.1938 | -61.203 | 61.7798 | 0.018311 | 0.13733 | 0.20142 | 62.1735 | -61.1984 | -0.28839 | 0.13275 | 0.032044 | -0.29755 | -0.32959 | -0.29297 | 0.064087 | 0.32044 | 61.0428 | 61.1069 | 122.6852 | 123.1476 | 0.032044 | 123.0789 | 60.9238 | -0.29297 | 123.1476 | 0.032044 | 60.9238 | 122.6852 | 123.0789 | -123.3032 | -123.3078
2336.7656 | 123.175 | -60.8871 | 62.1231 | -0.20241 | -0.0069342 | -0.010703 | -0.00014316 | 0.060532 | -0.0045821 | 0.067624 | -61.0748 | 62.2009 | -61.2167 | -61.1755 | 61.7889 | 0.036621 | 0.12817 | 0.20599 | 62.1872 | -61.2122 | -0.32959 | 0.07782 | -0.18768 | -0.28839 | -0.33417 | -0.32501 | 0.064087 | 0.14191 | 61.0153 | 61.0931 | 122.6761 | 123.0881 | -0.18768 | 123.0743 | 60.9238 | -0.32501 | 123.0881 | -0.18768 | 60.9238 | 122.6761 | 123.0743 | -123.3398 | -123.3353
2337.7656 | 123.111 | -60.9238 | 62.114 | -0.43129 | -0.0062934 | -0.0074981 | -0.002493 | 0.058823 | -0.0026595 | 0.067197 | -61.0611 | 62.178 | -61.2076 | -61.1572 | 61.7935 | 0.041199 | 0.13275 | 0.21057 | 62.178 | -61.1938 | -0.28381 | 0.064087 | -0.13733 | -0.23346 | -0.32044 | -0.27008 | 0.064087 | 0.14648 | 61.0565 | 61.1343 | 122.7173 | 123.1018 | -0.13733 | 123.1018 | 60.965 | -0.27008 | 123.1018 | -0.13733 | 60.965 | 122.7173 | 123.1018 | -123.3215 | -123.3078
2338.7656 | 123.1522 | -60.8963 | 62.1048 | -0.080337 | -0.0056524 | -0.011343 | 0.0032748 | 0.060746 | -0.0077865 | 0.067838 | -61.0153 | 62.1735 | -61.2167 | -61.1206 | 61.8164 | 0.045776 | 0.054932 | 0.21057 | 62.146 | -61.2305 | -0.32043 | 0.068665 | -0.11902 | -0.2243 | -0.28839 | -0.33417 | 0.041199 | 0.20142 | 60.9512 | 61.1069 | 122.7127 | 123.0698 | -0.11902 | 123.0423 | 60.9421 | -0.33417 | 123.0698 | -0.11902 | 60.9421 | 122.7127 | 123.0423 | -123.3215 | -123.3353
2339.7656 | 123.1613 | -60.878 | 62.0728 | -0.18715 | -0.0077888 | -0.016257 | -0.0018522 | 0.060532 | -0.0062911 | 0.066556 | -61.0016 | 62.1597 | -61.1893 | -61.1069 | 61.853 | 0.10071 | 0.050354 | 0.2655 | 62.1506 | -61.171 | -0.31128 | 0.086975 | -0.1236 | -0.22888 | -0.21973 | -0.29297 | 0.07782 | 0.18768 | 60.9283 | 61.1435 | 122.731 | 123.0377 | -0.1236 | 123.0286 | 60.9787 | -0.29297 | 123.0377 | -0.1236 | 60.9787 | 122.731 | 123.0286 | -123.262 | -123.2437
2340.7812 | 123.1247 | -60.9009 | 62.0773 | -0.17189 | -0.0054388 | -0.010703 | 0.00092504 | 0.057542 | -0.0045821 | 0.06442 | -61.0428 | 62.1597 | -61.2076 | -61.1572 | 61.7661 | 0.054932 | 0.10071 | 0.19684 | 62.1826 | -61.2167 | -0.3067 | 0.082397 | -0.14191 | -0.25635 | -0.31128 | -0.31586 | 0.10529 | 0.16479 | 61.0016 | 61.0977 | 122.6669 | 123.0606 | -0.14191 | 123.0835 | 60.9558 | -0.31586 | 123.0606 | -0.14191 | 60.9558 | 122.6669 | 123.0835 | -123.2849 | -123.2941
2341.7656 | 123.1796 | -60.8963 | 62.0911 | -0.18715 | -0.0080024 | -0.011984 | 0.00049764 | 0.06096 | -0.0056503 | 0.064207 | -61.0153 | 62.1323 | -61.2167 | -61.1298 | 61.8301 | 0.082397 | 0.086975 | 0.24719 | 62.1552 | -61.171 | -0.32043 | 0.041199 | -0.11902 | -0.23346 | -0.26093 | -0.27466 | 0.064087 | 0.20142 | 60.9833 | 61.1435 | 122.7264 | 123.0286 | -0.11902 | 123.0515 | 60.9787 | -0.27466 | 123.0286 | -0.11902 | 60.9787 | 122.7264 | 123.0515 | -123.3078 | -123.262
2342.7656 | 123.2437 | -60.8597 | 62.0636 | -0.16426 | -0.0069342 | -0.013266 | 0.002634 | 0.056901 | -0.0052231 | 0.065916 | -61.1114 | 62.0911 | -61.1893 | -61.0931 | 61.9171 | 0.11444 | -0.07782 | 0.27924 | 62.0728 | -61.1847 | -0.32959 | 0.027465 | -0.25177 | -0.23346 | -0.14649 | -0.32501 | 0.009155 | 0.07782 | 60.7819 | 61.1389 | 122.7768 | 122.9507 | -0.25177 | 122.9324 | 60.9741 | -0.32501 | 122.9507 | -0.25177 | 60.9741 | 122.7768 | 122.9324 | -123.2529 | -123.2483
2343.7656 | 123.2758 | -60.8368 | 62.1231 | -0.11848 | -0.0086432 | -0.01348 | -0.00099756 | 0.05861 | -0.0033005 | 0.065702 | -60.9695 | 62.0819 | -61.1847 | -61.0565 | 61.8668 | 0.14191 | -0.059509 | 0.32959 | 62.0773 | -61.1435 | -0.3479 | -0.041199 | -0.13275 | -0.21973 | -0.25635 | -0.3067 | -0.045776 | 0.21515 | 60.7773 | 61.1664 | 122.7036 | 122.9187 | -0.13275 | 122.9141 | 60.9787 | -0.3067 | 122.9187 | -0.13275 | 60.9787 | 122.7036 | 122.9141 | -123.3078 | -123.2666
2344.7656 | 123.2758 | -60.8688 | 62.0407 | -0.10323 | -0.007575 | -0.012839 | -0.00014316 | 0.060319 | -0.0039413 | 0.068479 | -60.965 | 62.0728 | -61.1893 | -61.0519 | 61.8988 | 0.13275 | -0.073242 | 0.32959 | 62.1414 | -61.1526 | -0.32044 | 0.032044 | -0.096131 | -0.18311 | -0.14191 | -0.28381 | 0.10071 | 0.2243 | 60.7956 | 61.1984 | 122.7676 | 122.9416 | -0.096131 | 123.0103 | 61.0016 | -0.28381 | 122.9416 | -0.096131 | 61.0016 | 122.7676 | 123.0103 | -123.23 | -123.1934
2345.7656 | 123.2574 | -60.878 | 62.0407 | -0.057449 | -0.0069342 | -0.012625 | 0.00092504 | 0.057542 | -0.0069321 | 0.067197 | -60.9924 | 62.0636 | -61.1938 | -61.0382 | 61.8896 | 0.1236 | -0.091553 | 0.28839 | 62.1002 | -61.1435 | -0.31586 | 0.022889 | -0.11444 | -0.16022 | -0.15106 | -0.2655 | 0.05951 | 0.20142 | 60.7864 | 61.1664 | 122.7676 | 122.9416 | -0.11444 | 122.9782 | 61.0016 | -0.2655 | 122.9416 | -0.11444 | 61.0016 | 122.7676 | 122.9782 | -123.2346 | -123.1842
2346.7656 | 123.2391 | -60.8688 | 62.0453 | -0.095596 | -0.0077888 | -0.015189 | 0.0011386 | 0.056473 | -0.0067185 | 0.065488 | -60.9695 | 62.0911 | -61.1938 | -61.0428 | 61.9034 | 0.12817 | -0.064087 | 0.29755 | 62.0819 | -61.1389 | -0.32501 | 0.045776 | -0.10071 | -0.17395 | -0.14191 | -0.27008 | 0.036621 | 0.22431 | 60.8047 | 61.1664 | 122.7722 | 122.9599 | -0.10071 | 122.9507 | 60.997 | -0.27008 | 122.9599 | -0.10071 | 60.997 | 122.7722 | 122.9507 | -123.2391 | -123.1842
2347.7656 | 123.2437 | -60.8734 | 62.0453 | -0.20241 | -0.0071478 | -0.011771 | 0.00071144 | 0.058182 | -0.0050095 | 0.067624 | -60.9695 | 62.0819 | -61.2122 | -61.0382 | 61.8896 | 0.15106 | -0.10529 | 0.32044 | 62.0911 | -61.1572 | -0.33875 | 0.036621 | -0.09613 | -0.16479 | -0.15564 | -0.28381 | 0.045776 | 0.24262 | 60.7681 | 61.1938 | 122.7631 | 122.9553 | -0.09613 | 122.9645 | 61.0245 | -0.28381 | 122.9553 | -0.09613 | 61.0245 | 122.7631 | 122.9645 | -123.2574 | -123.2025
2348.7812 | 123.175 | -60.8826 | 62.0544 | -0.14137 | -0.0094976 | -0.0092071 | 0.0045566 | 0.058823 | -0.0067185 | 0.065702 | -60.9924 | 62.0956 | -61.1755 | -61.0519 | 61.8622 | 0.09613 | 0.013733 | 0.27924 | 62.1368 | -61.1664 | -0.29297 | 0.041199 | -0.10986 | -0.16937 | -0.19226 | -0.28381 | 0.082398 | 0.1831 | 60.8963 | 61.1618 | 122.7448 | 122.9782 | -0.10986 | 123.0194 | 60.9787 | -0.28381 | 122.9782 | -0.10986 | 60.9787 | 122.7448 | 123.0194 | -123.23 | -123.2208
2349.7656 | 123.2162 | -60.8597 | 62.0544 | -0.11085 | -0.0086432 | -0.0092071 | 0.00028404 | 0.057328 | -0.0058639 | 0.065702 | -60.9695 | 62.0728 | -61.1938 | -61.0336 | 61.8805 | 0.13733 | -0.07782 | 0.31586 | 62.0911 | -61.1572 | -0.33417 | 0.018311 | -0.10986 | -0.17395 | -0.17395 | -0.29755 | 0.036621 | 0.22431 | 60.7819 | 61.1755 | 122.7402 | 122.9324 | -0.10986 | 122.9507 | 60.997 | -0.29755 | 122.9324 | -0.10986 | 60.997 | 122.7402 | 122.9507 | -123.2483 | -123.2117
2350.7656 | 123.2483 | -60.8688 | 62.0316 | -0.15663 | -0.0094976 | -0.0085663 | -0.00035676 | 0.059891 | -0.0067185 | 0.068052 | -60.9695 | 62.0728 | -61.203 | -61.0245 | 61.9034 | 0.14191 | -0.091553 | 0.31128 | 62.1231 | -61.1526 | -0.33417 | 0.041199 | -0.10071 | -0.15564 | -0.12817 | -0.28381 | 0.091553 | 0.23346 | 60.7773 | 61.1801 | 122.7722 | 122.9416 | -0.10071 | 122.9919 | 61.0107 | -0.28381 | 122.9416 | -0.10071 | 61.0107 | 122.7722 | 122.9919 | -123.2346 | -123.1842
2351.7656 | 123.2208 | -60.8597 | 62.0407 | -0.057449 | -0.0097114 | -0.0089935 | -0.00078396 | 0.059678 | -0.0071457 | 0.06677 | -60.9833 | 62.0911 | -61.1893 | -61.0474 | 61.908 | 0.12817 | -0.10986 | 0.29755 | 62.0819 | -61.116 | -0.32959 | 0.050354 | -0.1236 | -0.18768 | -0.13275 | -0.25635 | 0.041199 | 0.20599 | 60.7498 | 61.1572 | 122.7676 | 122.9507 | -0.1236 | 122.9416 | 60.9879 | -0.25635 | 122.9507 | -0.1236 | 60.9879 | 122.7676 | 122.9416 | -123.23 | -123.1567
2352.7656 | 123.2391 | -60.8643 | 62.059 | -0.034561 | -0.0067206 | -0.013693 | -0.00099756 | 0.057542 | -0.0080001 | 0.066343 | -61.0016 | 62.0728 | -61.203 | -61.0519 | 61.8759 | 0.10071 | -0.10986 | 0.28381 | 62.1094 | -61.1618 | -0.33875 | 0.013733 | -0.13733 | -0.18768 | -0.18311 | -0.29755 | 0.050354 | 0.20142 | 60.7544 | 61.1481 | 122.7402 | 122.937 | -0.13733 | 122.9736 | 60.965 | -0.29755 | 122.937 | -0.13733 | 60.965 | 122.7402 | 122.9736 | -123.262 | -123.2208
2353.7656 | 123.2391 | -60.8643 | 62.0453 | -0.04219 | -0.0086432 | -0.014548 | -0.00014316 | 0.055833 | -0.0035141 | 0.066343 | -61.0062 | 62.059 | -61.2122 | -61.0748 | 61.8622 | 0.10529 | -0.10529 | 0.26093 | 62.0682 | -61.1618 | -0.3479 | 0.013733 | -0.14191 | -0.21057 | -0.1831 | -0.29755 | 0.022888 | 0.20599 | 60.759 | 61.1252 | 122.7264 | 122.9233 | -0.14191 | 122.9324 | 60.9695 | -0.29755 | 122.9233 | -0.14191 | 60.9695 | 122.7264 | 122.9324 | -123.2574 | -123.2071
2354.7656 | 123.262 | -60.8688 | 62.0316 | -0.072708 | -0.0080024 | -0.013907 | 0.002634 | 0.058396 | -0.0065047 | 0.066556 | -60.9695 | 62.0728 | -61.1984 | -61.0336 | 61.9171 | 0.14191 | -0.10071 | 0.31586 | 62.1048 | -61.1298 | -0.32959 | 0.041199 | -0.10071 | -0.1648 | -0.11444 | -0.26093 | 0.073242 | 0.22888 | 60.7681 | 61.1847 | 122.7859 | 122.9416 | -0.10071 | 122.9736 | 61.0107 | -0.26093 | 122.9416 | -0.10071 | 61.0107 | 122.7859 | 122.9736 | -123.23 | -123.1613
2355.7656 | 123.2346 | -60.8322 | 62.0178 | -0.072708 | -0.01142 | -0.014548 | 0.00028404 | 0.057969 | -0.0056503 | 0.067624 | -61.0016 | 62.0773 | -61.2213 | -61.0291 | 61.8988 | 0.13733 | -0.10529 | 0.30212 | 62.0819 | -61.1526 | -0.3891 | 0.05951 | -0.16937 | -0.19684 | -0.11902 | -0.32043 | 0.064087 | 0.21973 | 60.7269 | 61.1343 | 122.731 | 122.9095 | -0.16937 | 122.9141 | 60.9695 | -0.32043 | 122.9095 | -0.16937 | 60.9695 | 122.731 | 122.9141 | -123.2391 | -123.1705
2356.7812 | 123.1796 | -60.8597 | 62.0361 | -0.149 | -0.010352 | -0.011557 | -0.0027066 | 0.058396 | -0.0073593 | 0.066129 | -60.9604 | 62.0773 | -61.1664 | -61.0291 | 61.8896 | 0.13275 | -0.064087 | 0.66376 | 62.1323 | -61.1069 | -0.3067 | 0.041199 | -0.10071 | -0.16937 | -0.14648 | -0.24719 | 0.09613 | 0.20599 | 60.7956 | 61.5234 | 122.7493 | 122.937 | -0.10071 | 122.9919 | 60.9924 | -0.24719 | 122.937 | -0.10071 | 60.9924 | 122.7493 | 122.9919 | -123.2025 | -123.143
2357.7656 | 123.2208 | -60.8826 | 62.0407 | -0.04982 | -0.007575 | -0.019888 | -0.001425 | 0.057114 | -0.0069321 | 0.06677 | -61.0062 | 62.0728 | -61.1938 | -61.0519 | 61.8896 | 0.10071 | -0.10071 | 0.25177 | 62.1002 | -61.1526 | -0.31128 | 0.032044 | -0.1236 | -0.16937 | -0.15106 | -0.27008 | 0.05951 | 0.18768 | 60.7819 | 61.1343 | 122.7722 | 122.9553 | -0.1236 | 122.9828 | 60.9833 | -0.27008 | 122.9553 | -0.1236 | 60.9833 | 122.7722 | 122.9828 | -123.2346 | -123.1934
2358.7656 | 123.2391 | -60.8917 | 62.027 | -0.0040434 | -0.0071478 | -0.012412 | -0.00078396 | 0.058823 | -0.0065047 | 0.067197 | -61.0153 | 62.059 | -61.1984 | -61.0657 | 61.8942 | 0.086975 | -0.086975 | 0.24719 | 62.114 | -61.1343 | -0.3067 | 0.032043 | -0.1236 | -0.17395 | -0.13275 | -0.24261 | 0.086975 | 0.1831 | 60.8047 | 61.1389 | 122.786 | 122.9507 | -0.1236 | 123.0057 | 60.9787 | -0.24261 | 122.9507 | -0.1236 | 60.9787 | 122.786 | 123.0057 | -123.2254 | -123.1613
2359.7656 | 123.23 | -60.878 | 62.0407 | 0.072251 | -0.0084296 | -0.015189 | -0.0012112 | 0.057328 | -0.0050095 | 0.066556 | -61.0428 | 62.0819 | -61.2213 | -61.0703 | 61.8668 | 0.064087 | -0.086975 | 0.21973 | 62.0636 | -61.1206 | -0.34332 | 0.041199 | -0.16479 | -0.19226 | -0.17395 | -0.24261 | 0.022889 | 0.17853 | 60.791 | 61.0977 | 122.7448 | 122.9599 | -0.16479 | 122.9416 | 60.9421 | -0.24261 | 122.9599 | -0.16479 | 60.9421 | 122.7448 | 122.9416 | -123.262 | -123.1613
2360.7656 | 123.2208 | -60.8826 | 62.0499 | 0.034104 | -0.007575 | -0.011343 | -0.00014316 | 0.05861 | -0.0060775 | 0.067411 | -61.0519 | 62.059 | -61.2122 | -61.0748 | 61.8484 | 0.045776 | -0.091553 | 0.20142 | 62.0865 | -61.1343 | -0.32959 | 0.009155 | -0.16937 | -0.19226 | -0.20142 | -0.25177 | 0.036621 | 0.16022 | 60.791 | 61.084 | 122.731 | 122.9416 | -0.16937 | 122.9691 | 60.9283 | -0.25177 | 122.9416 | -0.16937 | 60.9283 | 122.731 | 122.9691 | -123.262 | -123.1842
2361.7656 | 123.2437 | -60.8688 | 62.0544 | 0.056992 | -0.0077888 | -0.011984 | 7.0444e-05 | 0.056473 | -0.0056503 | 0.064847 | -61.0062 | 62.0773 | -61.1938 | -61.0519 | 61.8668 | 0.10986 | -0.082397 | 0.25635 | 62.0682 | -61.1389 | -0.32501 | 0.022889 | -0.13733 | -0.18311 | -0.18768 | -0.27008 | 0.013733 | 0.18768 | 60.7864 | 61.1252 | 122.7356 | 122.9462 | -0.13733 | 122.937 | 60.9787 | -0.27008 | 122.9462 | -0.13733 | 60.9787 | 122.7356 | 122.937 | -123.2483 | -123.1934
2362.7656 | 123.2254 | -60.878 | 62.0178 | -0.0040434 | -0.008216 | -0.012412 | -0.0012112 | 0.058396 | -0.0067185 | 0.067624 | -61.0245 | 62.0544 | -61.203 | -61.0748 | 61.8713 | 0.07782 | -0.09613 | 0.24261 | 62.0773 | -61.1389 | -0.32501 | 0.036621 | -0.14648 | -0.19684 | -0.14648 | -0.26093 | 0.05951 | 0.17853 | 60.7819 | 61.1206 | 122.7493 | 122.9324 | -0.14648 | 122.9553 | 60.9558 | -0.26093 | 122.9324 | -0.14648 | 60.9558 | 122.7493 | 122.9553 | -123.2208 | -123.1567
2363.7656 | 123.2117 | -60.8688 | 62.0407 | 0.056992 | -0.0069342 | -0.013693 | -0.00078396 | 0.056901 | -0.0065047 | 0.068265 | -61.0382 | 62.0865 | -61.1801 | -61.0748 | 61.8668 | 0.068665 | -0.091553 | 0.22888 | 62.059 | -61.1435 | -0.31128 | 0.045777 | -0.16937 | -0.20599 | -0.17395 | -0.27466 | 0.018311 | 0.14191 | 60.7773 | 61.0977 | 122.7356 | 122.9553 | -0.16937 | 122.9279 | 60.9375 | -0.27466 | 122.9553 | -0.16937 | 60.9375 | 122.7356 | 122.9279 | -123.2208 | -123.1842
2364.7656 | 123.2162 | -60.8826 | 62.0453 | 0.25536 | -0.0088568 | -0.012412 | 0.0015658 | 0.059251 | -0.0065047 | 0.064207 | -60.9741 | 62.0773 | -61.2122 | -61.0199 | 61.8851 | 0.13733 | -0.036621 | 0.27924 | 62.0865 | -61.116 | -0.32959 | 0.032044 | -0.091553 | -0.13733 | -0.16022 | -0.23346 | 0.041199 | 0.23804 | 60.8459 | 61.1618 | 122.7676 | 122.9599 | -0.091553 | 122.9691 | 61.0199 | -0.23346 | 122.9599 | -0.091553 | 61.0199 | 122.7676 | 122.9691 | -123.2574 | -123.1613
2365.7656 | 123.1979 | -60.8917 | 62.0224 | 0.34691 | -0.006507 | -0.014121 | -0.00057036 | 0.057114 | -0.0037277 | 0.067197 | -61.0474 | 62.0636 | -61.1984 | -61.1114 | 61.8347 | 0.045776 | -0.07782 | 0.20142 | 62.0819 | -61.1435 | -0.3067 | 0.041199 | -0.15564 | -0.21973 | -0.18768 | -0.25177 | 0.059509 | 0.15106 | 60.8139 | 61.0931 | 122.7264 | 122.9553 | -0.15564 | 122.9736 | 60.9375 | -0.25177 | 122.9553 | -0.15564 | 60.9375 | 122.7264 | 122.9736 | -123.2208 | -123.1659
2366.7656 | 123.1934 | -60.8734 | 62.0224 | 0.072251 | -0.0097114 | -0.011343 | 0.00049764 | 0.058396 | -0.0052231 | 0.065916 | -61.0474 | 62.0819 | -61.203 | -61.1298 | 61.8393 | 0.041199 | -0.073242 | 0.19684 | 62.0636 | -61.1572 | -0.32959 | 0.059509 | -0.17395 | -0.25635 | -0.18311 | -0.28381 | 0.041199 | 0.15564 | 60.8002 | 61.0703 | 122.7127 | 122.9553 | -0.17395 | 122.937 | 60.9146 | -0.28381 | 122.9553 | -0.17395 | 60.9146 | 122.7127 | 122.937 | -123.2254 | -123.1796
2367.7656 | 123.1888 | -60.9146 | 62.027 | 0.087509 | -0.006507 | -0.010703 | 0.0011386 | 0.057328 | -0.0067185 | 0.067197 | -61.0657 | 62.059 | -61.2122 | -61.1526 | 61.8942 | 0.14648 | -0.11902 | 0.18768 | 62.0682 | -61.1481 | -0.29755 | 0.032043 | -0.15106 | -0.23804 | -0.13275 | -0.23346 | 0.041198 | 0.14648 | 60.7956 | 61.1023 | 122.8088 | 122.9736 | -0.15106 | 122.9828 | 61.0611 | -0.23346 | 122.9736 | -0.15106 | 61.0611 | 122.8088 | 122.9828 | -123.2391 | -123.175
2368.7656 | 123.2117 | -60.8917 | 62.0544 | 0.07988 | -0.0097114 | -0.010489 | 0.00092504 | 0.058182 | -0.0041549 | 0.068265 | -61.0336 | 62.1094 | -61.1984 | -61.0977 | 61.8668 | 0.068665 | -0.073242 | 0.23346 | 62.0453 | -61.1755 | -0.3067 | 0.054932 | -0.14191 | -0.20599 | -0.18768 | -0.28381 | -0.009155 | 0.16479 | 60.8185 | 61.1252 | 122.7585 | 123.0011 | -0.14191 | 122.937 | 60.9604 | -0.28381 | 123.0011 | -0.14191 | 60.9604 | 122.7585 | 122.937 | -123.2529 | -123.23
2369.7812 | 123.1293 | -60.9009 | 62.0819 | -0.12611 | -0.0086432 | -0.01113 | 0.0030612 | 0.056473 | -0.0035141 | 0.065488 | -61.0336 | 62.1506 | -61.1893 | -61.1343 | 61.8256 | 0.068665 | 0.09613 | 0.20599 | 62.1277 | -61.1938 | -0.28839 | 0.068665 | -0.13275 | -0.23346 | -0.25635 | -0.29297 | 0.045777 | 0.15564 | 60.997 | 61.1069 | 122.7264 | 123.0515 | -0.13275 | 123.0286 | 60.9695 | -0.29297 | 123.0515 | -0.13275 | 60.9695 | 122.7264 | 123.0286 | -123.2712 | -123.2758
2370.7656 | 123.1934 | -60.8871 | 62.0316 | 0.14092 | -0.0086432 | -0.011771 | 0.0011386 | 0.057328 | -0.0052231 | 0.065702 | -61.0519 | 62.0865 | -61.235 | -61.0931 | 61.8622 | 0.054932 | -0.086975 | 0.20142 | 62.0544 | -61.1526 | -0.3479 | 0.054932 | -0.16479 | -0.20599 | -0.16937 | -0.2655 | 0.022888 | 0.1831 | 60.8002 | 61.0886 | 122.7493 | 122.9736 | -0.16479 | 122.9416 | 60.9421 | -0.2655 | 122.9736 | -0.16479 | 60.9421 | 122.7493 | 122.9416 | -123.2666 | -123.1842
2371.7656 | 123.175 | -60.8963 | 62.0361 | 0.10277 | -0.006507 | -0.0096343 | -0.00078396 | 0.056473 | -0.0033005 | 0.066129 | -61.0657 | 62.0865 | -61.2259 | -61.1069 | 61.8439 | 0.045776 | -0.086975 | 0.17853 | 62.0682 | -61.1618 | -0.32959 | 0.050354 | -0.16937 | -0.21057 | -0.19226 | -0.2655 | 0.032043 | 0.16022 | 60.8093 | 61.0748 | 122.7402 | 122.9828 | -0.16937 | 122.9645 | 60.9421 | -0.2655 | 122.9828 | -0.16937 | 60.9421 | 122.7402 | 122.9645 | -123.262 | -123.1979
2372.7656 | 123.2117 | -60.8597 | 62.0544 | -2.5523 | -0.0090704 | -0.0079253 | -0.00014316 | 0.058823 | -0.0050095 | 0.065702 | -61.1298 | 62.1094 | -61.1984 | -61.0474 | 61.8851 | 0.11902 | -0.041199 | 0.3067 | 62.0911 | -61.1389 | -0.33875 | 0.054932 | -0.27008 | -0.18768 | -0.16937 | -0.27924 | 0.036621 | 0.068664 | 60.8185 | 61.1664 | 122.7448 | 122.9691 | -0.27008 | 122.9507 | 60.9787 | -0.27924 | 122.9691 | -0.27008 | 60.9787 | 122.7448 | 122.9507 | -123.2529 | -123.1934
2373.7656 | 123.1796 | -60.8734 | 62.0224 | 0.22484 | -0.0084296 | -0.010275 | 0.0011386 | 0.057328 | -0.0060775 | 0.067838 | -61.0428 | 62.1048 | -61.1938 | -61.1114 | 61.8256 | 0.027466 | -0.086975 | 0.19684 | 62.0956 | -61.1526 | -0.32044 | 0.082397 | -0.16937 | -0.23804 | -0.19684 | -0.27924 | 0.073242 | 0.15106 | 60.7864 | 61.0703 | 122.699 | 122.9782 | -0.16937 | 122.9691 | 60.9009 | -0.27924 | 122.9782 | -0.16937 | 60.9009 | 122.699 | 122.9691 | -123.2162 | -123.175
2374.7812 | 123.1476 | -60.8871 | 62.0728 | -0.10323 | -0.0039434 | -0.0094207 | 0.0066928 | 0.061387 | -0.0037277 | 0.06442 | -60.9833 | 62.1872 | -61.1938 | -61.0703 | 61.8164 | 0.059509 | 0.073242 | 0.21973 | 62.0773 | -61.1938 | -0.3067 | 0.11444 | -0.09613 | -0.1831 | -0.25635 | -0.3067 | 0.004578 | 0.21057 | 60.9604 | 61.1069 | 122.7036 | 123.0743 | -0.09613 | 122.9645 | 60.9467 | -0.3067 | 123.0743 | -0.09613 | 60.9467 | 122.7036 | 122.9645 | -123.2666 | -123.2666
2375.7656 | 123.2208 | -60.8643 | 62.0178 | -0.011673 | -0.0088568 | -0.010916 | -0.00099756 | 0.06096 | -0.0062911 | 0.068052 | -61.0382 | 62.0728 | -61.2213 | -61.0703 | 61.8759 | 0.07782 | -0.073242 | 0.2243 | 62.0956 | -61.1298 | -0.35706 | 0.054932 | -0.17395 | -0.20599 | -0.14191 | -0.2655 | 0.07782 | 0.18311 | 60.791 | 61.0886 | 122.7402 | 122.937 | -0.17395 | 122.9599 | 60.9421 | -0.2655 | 122.937 | -0.17395 | 60.9421 | 122.7402 | 122.9599 | -123.2391 | -123.1476
2376.7656 | 123.2117 | -60.8734 | 62.0361 | 0.087509 | -0.0077888 | -0.01113 | 0.0015658 | 0.058823 | -0.0047957 | 0.066556 | -61.0428 | 62.0682 | -61.2122 | -61.0931 | 61.8805 | 0.068665 | -0.059509 | 0.23346 | 62.0728 | -61.1343 | -0.33875 | 0.032043 | -0.16937 | -0.21973 | -0.15564 | -0.26093 | 0.036621 | 0.16937 | 60.8139 | 61.1069 | 122.7539 | 122.9416 | -0.16937 | 122.9462 | 60.9421 | -0.26093 | 122.9416 | -0.16937 | 60.9421 | 122.7539 | 122.9462 | -123.2483 | -123.1705
2377.7656 | 123.2117 | -60.9055 | 62.027 | 0.095139 | -0.0060798 | -0.011557 | -0.0018522 | 0.05626 | -0.0054367 | 0.067838 | -61.0565 | 62.0956 | -61.2305 | -61.0977 | 61.8439 | 0.059509 | -0.07782 | 0.2243 | 62.0499 | -61.1801 | -0.32501 | 0.068664 | -0.15106 | -0.19226 | -0.18311 | -0.27466 | 0.022888 | 0.17395 | 60.8276 | 61.1298 | 122.7493 | 123.0011 | -0.15106 | 122.9553 | 60.965 | -0.27466 | 123.0011 | -0.15106 | 60.965 | 122.7493 | 122.9553 | -123.2574 | -123.2071
2378.7656 | 123.2025 | -60.8734 | 62.0407 | 0.19432 | -0.010139 | -0.014761 | 0.00049764 | 0.059678 | -0.0037277 | 0.067411 | -61.0611 | 62.0773 | -61.2213 | -61.1069 | 61.8439 | 0.068665 | -0.07782 | 0.20142 | 62.0728 | -61.1481 | -0.3479 | 0.036622 | -0.18768 | -0.23346 | -0.19684 | -0.27466 | 0.032044 | 0.16022 | 60.7956 | 61.0748 | 122.7173 | 122.9507 | -0.18768 | 122.9462 | 60.9421 | -0.27466 | 122.9507 | -0.18768 | 60.9421 | 122.7173 | 122.9462 | -123.262 | -123.1888
2379.7812 | 123.23 | -60.8734 | 62.0453 | -0.31685 | -0.0084296 | -0.011984 | 0.0013522 | 0.056687 | -0.0056503 | 0.068052 | -60.9787 | 62.1002 | -61.1984 | -61.0428 | 61.8988 | 0.13733 | -0.027466 | 0.29755 | 62.0728 | -61.1389 | -0.32501 | 0.054932 | -0.10529 | -0.16937 | -0.14648 | -0.2655 | 0.027466 | 0.21973 | 60.8459 | 61.171 | 122.7722 | 122.9736 | -0.10529 | 122.9462 | 61.0107 | -0.2655 | 122.9736 | -0.10529 | 61.0107 | 122.7722 | 122.9462 | -123.2437 | -123.1842
2380.7656 | 123.1888 | -60.8871 | 62.0316 | -1.4765 | -0.0080024 | -0.013693 | -0.00014316 | 0.058182 | -0.0058639 | 0.068479 | -61.0886 | 62.1094 | -61.1984 | -61.1069 | 61.821 | 0.027466 | -0.073242 | 0.1831 | 62.0453 | -61.1664 | -0.31128 | 0.07782 | -0.20142 | -0.21973 | -0.21057 | -0.27924 | 0.013733 | 0.10986 | 60.8139 | 61.0703 | 122.7081 | 122.9965 | -0.20142 | 122.9324 | 60.9146 | -0.27924 | 122.9965 | -0.20142 | 60.9146 | 122.7081 | 122.9324 | -123.23 | -123.1979
2381.7656 | 123.1796 | -60.8734 | 62.027 | 0.14092 | -0.0086432 | -0.012198 | 0.0017794 | 0.05861 | -0.0041549 | 0.066984 | -61.0565 | 62.0636 | -61.1984 | -61.1252 | 61.8439 | 0.027466 | -0.050354 | 0.14648 | 62.0819 | -61.1526 | -0.32501 | 0.036621 | -0.18311 | -0.25177 | -0.18311 | -0.27924 | 0.054931 | 0.14191 | 60.8231 | 61.0199 | 122.7173 | 122.937 | -0.18311 | 122.9553 | 60.9009 | -0.27924 | 122.937 | -0.18311 | 60.9009 | 122.7173 | 122.9553 | -123.2254 | -123.1796
2382.7656 | 123.2117 | -60.8643 | 62.0499 | 0.0035856 | -0.0080024 | -0.01348 | -0.00078396 | 0.057328 | -0.0043685 | 0.065488 | -61.0245 | 62.0728 | -61.203 | -61.0794 | 61.8668 | 0.073242 | -0.07782 | 0.23804 | 62.0453 | -61.1435 | -0.33875 | 0.022888 | -0.16022 | -0.21515 | -0.18311 | -0.27924 | -0.004578 | 0.17853 | 60.7864 | 61.1023 | 122.731 | 122.937 | -0.16022 | 122.9095 | 60.9375 | -0.27924 | 122.937 | -0.16022 | 60.9375 | 122.731 | 122.9095 | -123.2529 | -123.1934
2383.7656 | 123.2117 | -60.8688 | 62.059 | 0.049362 | -0.0090704 | -0.012412 | -0.00078396 | 0.05626 | -0.0050095 | 0.063352 | -61.0428 | 62.0636 | -61.1938 | -61.0886 | 61.8668 | 0.086975 | -0.09613 | 0.23346 | 62.0544 | -61.1618 | -0.32501 | 0.004578 | -0.17395 | -0.21973 | -0.19226 | -0.29297 | -0.004578 | 0.15106 | 60.7727 | 61.1023 | 122.7356 | 122.9324 | -0.17395 | 122.9233 | 60.9558 | -0.29297 | 122.9324 | -0.17395 | 60.9558 | 122.7356 | 122.9233 | -123.2529 | -123.2208
2384.7656 | 123.1476 | -60.8871 | 62.0636 | -0.0040434 | -0.0067206 | -0.011343 | 0.008829 | 0.058182 | -0.0075729 | 0.067197 | -61.0016 | 62.1277 | -61.235 | -61.0748 | 61.8164 | 0.073242 | -0.009155 | 0.19226 | 62.1231 | -61.1481 | -0.3479 | 0.064087 | -0.11444 | -0.18768 | -0.24719 | -0.26093 | 0.059509 | 0.23346 | 60.878 | 61.0794 | 122.7036 | 123.0148 | -0.11444 | 123.0103 | 60.9604 | -0.26093 | 123.0148 | -0.11444 | 60.9604 | 122.7036 | 123.0103 | -123.2986 | -123.2117
2385.7656 | 123.1659 | -60.8963 | 62.0132 | 0.087509 | -0.005866 | -0.013266 | 7.0444e-05 | 0.06096 | -0.0041549 | 0.067411 | -61.0519 | 62.0773 | -61.2259 | -61.1343 | 61.8393 | 0.018311 | -0.086975 | 0.15564 | 62.0636 | -61.1572 | -0.32959 | 0.064087 | -0.15564 | -0.23804 | -0.17395 | -0.26093 | 0.050354 | 0.17395 | 60.8093 | 61.0519 | 122.7356 | 122.9736 | -0.15564 | 122.9599 | 60.9146 | -0.26093 | 122.9736 | -0.15564 | 60.9146 | 122.7356 | 122.9599 | -123.2391 | -123.1705
2386.7656 | 123.1979 | -60.878 | 62.0499 | 0.1638 | -0.011207 | -0.011984 | -0.0012112 | 0.059251 | -0.0022323 | 0.067838 | -61.0657 | 62.0819 | -61.2076 | -61.1069 | 61.8347 | 0.064087 | -0.073242 | 0.21057 | 62.0728 | -61.1572 | -0.32959 | 0.032043 | -0.18768 | -0.22888 | -0.21515 | -0.27924 | 0.022888 | 0.14191 | 60.8047 | 61.0886 | 122.7127 | 122.9599 | -0.18768 | 122.9507 | 60.9421 | -0.27924 | 122.9599 | -0.18768 | 60.9421 | 122.7127 | 122.9507 | -123.2574 | -123.2071
2387.7656 | 123.1979 | -60.8826 | 62.0224 | 0.15617 | -0.0060798 | -0.012412 | -0.0012112 | 0.058182 | -0.0047957 | 0.067838 | -61.0611 | 62.0819 | -61.203 | -61.1298 | 61.821 | 0.018311 | -0.10071 | 0.16022 | 62.0636 | -61.1664 | -0.32044 | 0.059509 | -0.17853 | -0.24719 | -0.20142 | -0.28381 | 0.041199 | 0.14191 | 60.7819 | 61.0428 | 122.7036 | 122.9645 | -0.17853 | 122.9462 | 60.9009 | -0.28381 | 122.9645 | -0.17853 | 60.9009 | 122.7036 | 122.9462 | -123.2254 | -123.1888
2388.7656 | 123.1888 | -60.8826 | 62.0361 | 0.13329 | -0.0069342 | -0.011557 | 0.00071144 | 0.060532 | -0.0054367 | 0.066984 | -61.0519 | 62.0544 | -61.1984 | -61.1252 | 61.8256 | 0.032043 | -0.10986 | 0.15564 | 62.0773 | -61.1755 | -0.31586 | 0.01831 | -0.16937 | -0.24262 | -0.21057 | -0.29297 | 0.041199 | 0.14648 | 60.7727 | 61.0382 | 122.7081 | 122.937 | -0.16937 | 122.9599 | 60.9146 | -0.29297 | 122.937 | -0.16937 | 60.9146 | 122.7081 | 122.9599 | -123.2346 | -123.2117
2389.7656 | 123.175 | -60.878 | 62.0316 | 0.041733 | -0.010352 | -0.01113 | 0.0013522 | 0.055192 | -0.0043685 | 0.065916 | -61.0657 | 62.0773 | -61.203 | -61.1252 | 61.8347 | 0.004578 | -0.050354 | 0.16937 | 62.0499 | -61.1481 | -0.32501 | 0.045777 | -0.18768 | -0.24719 | -0.19684 | -0.27008 | 0.018311 | 0.13733 | 60.8276 | 61.0474 | 122.7127 | 122.9553 | -0.18768 | 122.9279 | 60.8826 | -0.27008 | 122.9553 | -0.18768 | 60.8826 | 122.7127 | 122.9279 | -123.2346 | -123.1796
2390.7656 | 123.1796 | -60.8871 | 62.0224 | 0.10277 | -0.0080024 | -0.014975 | 0.0011386 | 0.057328 | -0.0033005 | 0.068693 | -61.0657 | 62.0728 | -61.2122 | -61.1069 | 61.9354 | 0.10529 | -0.11902 | 0.20599 | 62.0773 | -61.1664 | -0.32501 | 0.050354 | -0.17853 | -0.21973 | -0.086975 | -0.27924 | 0.054932 | 0.14648 | 60.7681 | 61.0931 | 122.8226 | 122.9599 | -0.17853 | 122.9645 | 60.9924 | -0.27924 | 122.9599 | -0.17853 | 60.9924 | 122.8226 | 122.9645 | -123.2346 | -123.1888
2391.7656 | 123.1934 | -60.8734 | 62.0407 | 0.087509 | -0.0090704 | -0.011984 | -0.00035676 | 0.056901 | -0.0028731 | 0.066343 | -61.0657 | 62.0728 | -61.1984 | -61.1298 | 61.8256 | 0.013733 | -0.07782 | 0.17395 | 62.0636 | -61.1618 | -0.32501 | 0.032044 | -0.19226 | -0.25635 | -0.21515 | -0.28839 | 0.022889 | 0.13275 | 60.7956 | 61.0474 | 122.699 | 122.9462 | -0.19226 | 122.937 | 60.8871 | -0.28839 | 122.9462 | -0.19226 | 60.8871 | 122.699 | 122.937 | -123.2391 | -123.2025
2392.7656 | 123.2254 | -60.8597 | 62.0499 | -0.17189 | -0.006507 | -0.0089935 | 0.00092504 | 0.05861 | -0.0039413 | 0.068265 | -60.9787 | 62.0682 | -61.1938 | -61.0336 | 61.9034 | 0.1236 | -0.018311 | 0.3067 | 62.0865 | -61.116 | -0.33417 | 0.01831 | -0.11902 | -0.17395 | -0.14648 | -0.25635 | 0.036621 | 0.21515 | 60.8414 | 61.1664 | 122.7631 | 122.9279 | -0.11902 | 122.9462 | 60.9833 | -0.25635 | 122.9279 | -0.11902 | 60.9833 | 122.7631 | 122.9462 | -123.2437 | -123.1659
2393.7812 | 123.2941 | -60.8414 | 62.0819 | -0.11848 | -0.010352 | -0.012198 | 0.00049764 | 0.057755 | -0.0069321 | 0.065488 | -60.965 | 62.0819 | -61.2076 | -61.0199 | 61.9034 | 0.14648 | -0.059509 | 0.32044 | 62.0865 | -61.116 | -0.36621 | 0 | -0.1236 | -0.17853 | -0.17853 | -0.27466 | 0.004578 | 0.24262 | 60.7819 | 61.1618 | 122.7448 | 122.9233 | -0.1236 | 122.9279 | 60.9879 | -0.27466 | 122.9233 | -0.1236 | 60.9879 | 122.7448 | 122.9279 | -123.2895 | -123.1979
2394.7656 | 123.1979 | -60.878 | 62.027 | 0.018845 | -0.0094976 | -0.014975 | -0.0012112 | 0.057969 | -0.0060775 | 0.067197 | -61.0336 | 62.0682 | -61.203 | -61.116 | 61.8484 | 0.054932 | -0.068665 | 0.20599 | 62.114 | -61.1481 | -0.32501 | 0.041198 | -0.15564 | -0.23804 | -0.17853 | -0.27008 | 0.086975 | 0.16937 | 60.8093 | 61.084 | 122.7264 | 122.9462 | -0.15564 | 122.9919 | 60.9329 | -0.27008 | 122.9462 | -0.15564 | 60.9329 | 122.7264 | 122.9919 | -123.23 | -123.175
2395.7656 | 123.2254 | -60.8917 | 62.0224 | 0.026474 | -0.0086432 | -0.015402 | 7.0444e-05 | 0.057328 | -0.0065047 | 0.06442 | -61.0062 | 62.059 | -61.1893 | -61.0703 | 61.8896 | 0.10529 | -0.082397 | 0.25177 | 62.114 | -61.1252 | -0.29755 | 0.036621 | -0.11444 | -0.17853 | -0.13275 | -0.23346 | 0.091553 | 0.1831 | 60.8093 | 61.1435 | 122.7814 | 122.9507 | -0.11444 | 123.0057 | 60.997 | -0.23346 | 122.9507 | -0.11444 | 60.997 | 122.7814 | 123.0057 | -123.2117 | -123.1476
2396.7656 | 123.1934 | -60.8826 | 62.0224 | -0.026932 | -0.0077888 | -0.014761 | 0.0030612 | 0.058823 | -0.0037277 | 0.066556 | -61.0107 | 62.0819 | -61.171 | -61.0657 | 61.853 | 0.09613 | -0.091553 | 0.25177 | 62.0773 | -61.1389 | -0.28839 | 0.059509 | -0.12817 | -0.18311 | -0.16937 | -0.25635 | 0.054932 | 0.16022 | 60.791 | 61.1343 | 122.7356 | 122.9645 | -0.12817 | 122.9599 | 60.9787 | -0.25635 | 122.9645 | -0.12817 | 60.9787 | 122.7356 | 122.9599 | -123.1934 | -123.1613
2397.7656 | 123.2162 | -60.8643 | 62.027 | 0.064621 | -0.009284 | -0.011984 | -0.00099756 | 0.056901 | -0.0077865 | 0.065488 | -61.0199 | 62.0544 | -61.2122 | -61.0657 | 61.8805 | 0.091553 | -0.07782 | 0.22888 | 62.0865 | -61.1664 | -0.3479 | 0.027465 | -0.15564 | -0.20142 | -0.14648 | -0.30212 | 0.059509 | 0.19226 | 60.7864 | 61.0931 | 122.7448 | 122.9187 | -0.15564 | 122.9507 | 60.9558 | -0.30212 | 122.9187 | -0.15564 | 60.9558 | 122.7448 | 122.9507 | -123.2391 | -123.1934
2398.7812 | 123.1613 | -60.91 | 62.0911 | -0.14137 | -0.0052252 | -0.0070709 | 0.0069064 | 0.05861 | -0.0043685 | 0.065916 | -61.0062 | 62.1735 | -61.1984 | -61.0794 | 61.8256 | 0.054932 | 0.073242 | 0.20142 | 62.1231 | -61.2076 | -0.28839 | 0.082398 | -0.096131 | -0.16937 | -0.2655 | -0.29755 | 0.032044 | 0.19226 | 60.9833 | 61.1115 | 122.7356 | 123.0835 | -0.096131 | 123.0331 | 60.965 | -0.29755 | 123.0835 | -0.096131 | 60.965 | 122.7356 | 123.0331 | -123.2895 | -123.2986
2399.7656 | 123.2025 | -60.8963 | 62.0361 | 0.13329 | -0.0073614 | -0.014121 | -0.0012112 | 0.058823 | -0.0054367 | 0.067838 | -61.0519 | 62.0728 | -61.2396 | -61.1206 | 61.853 | 0.041199 | -0.059509 | 0.18768 | 62.1048 | -61.1526 | -0.34332 | 0.036621 | -0.15564 | -0.2243 | -0.18311 | -0.25635 | 0.068664 | 0.18768 | 60.8368 | 61.084 | 122.7493 | 122.9691 | -0.15564 | 123.0011 | 60.9375 | -0.25635 | 122.9691 | -0.15564 | 60.9375 | 122.7493 | 123.0011 | -123.2758 | -123.1888
2400.7656 | 123.2254 | -60.878 | 62.0453 | -0.11085 | -0.0088568 | -0.012412 | 0.0058382 | 0.059678 | -0.0045821 | 0.069333 | -60.9833 | 62.0911 | -61.1938 | -61.084 | 61.8805 | 0.16937 | -0.09613 | 0.28839 | 62.0361 | -61.116 | -0.31586 | 0.045776 | -0.10528 | -0.20599 | -0.16479 | -0.23804 | -0.009155 | 0.21057 | 60.7819 | 61.1664 | 122.7585 | 122.9691 | -0.10528 | 122.9141 | 61.0474 | -0.23804 | 122.9691 | -0.10528 | 61.0474 | 122.7585 | 122.9141 | -123.2391 | -123.1613
2401.7656 | 123.1888 | -60.8917 | 62.0316 | 0.14092 | -0.0077888 | -0.012412 | -0.0012112 | 0.059891 | -0.0041549 | 0.06677 | -61.0657 | 62.0773 | -61.2122 | -61.0153 | 61.8393 | -0.022888 | -0.07782 | 0.16479 | 62.0773 | -61.1618 | -0.32043 | 0.045777 | -0.17395 | -0.1236 | -0.19226 | -0.27008 | 0.045777 | 0.14648 | 60.8139 | 61.0565 | 122.731 | 122.9691 | -0.17395 | 122.9691 | 60.8688 | -0.27008 | 122.9691 | -0.17395 | 60.8688 | 122.731 | 122.9691 | -123.2437 | -123.1934
2402.7656 | 123.2162 | -60.9055 | 62.0636 | 0.072251 | -0.007575 | -0.014548 | 0.00071144 | 0.059251 | -0.0065047 | 0.066556 | -61.0336 | 62.0819 | -61.1984 | -61.0886 | 61.8622 | 0.064087 | -0.086975 | 0.21973 | 62.0819 | -61.1526 | -0.29297 | 0.01831 | -0.12817 | -0.18311 | -0.20142 | -0.24719 | 0.01831 | 0.16479 | 60.8185 | 61.1252 | 122.7676 | 122.9874 | -0.12817 | 122.9874 | 60.9695 | -0.24719 | 122.9874 | -0.12817 | 60.9695 | 122.7676 | 122.9874 | -123.262 | -123.2162
2403.7812 | 123.1522 | -60.8734 | 62.059 | -0.14137 | -0.004798 | -0.014761 | 0.0062656 | 0.057542 | -0.0062911 | 0.068265 | -61.0016 | 62.1689 | -61.2076 | -61.1252 | 61.8164 | 0.032043 | 0.10529 | 0.20142 | 62.1368 | -61.1893 | -0.33417 | 0.10986 | -0.12817 | -0.25177 | -0.24262 | -0.31586 | 0.07782 | 0.20599 | 60.9787 | 61.0748 | 122.6898 | 123.0423 | -0.12817 | 123.0103 | 60.9055 | -0.31586 | 123.0423 | -0.12817 | 60.9055 | 122.6898 | 123.0103 | -123.2666 | -123.2483
2404.7656 | 123.1979 | -60.9146 | 62.059 | 0.049362 | -0.0090704 | -0.0092071 | -0.0012112 | 0.058396 | -0.0047957 | 0.065916 | -60.9375 | 62.114 | -61.2213 | -61.116 | 61.8576 | 0.027466 | -0.068665 | 0.1831 | 62.0636 | -61.1572 | -0.3067 | 0.054932 | -0.022888 | -0.20142 | -0.20142 | -0.24262 | 0.004578 | 0.28381 | 60.8459 | 61.0977 | 122.7722 | 123.0286 | -0.022888 | 122.9782 | 60.9421 | -0.24262 | 123.0286 | -0.022888 | 60.9421 | 122.7722 | 122.9782 | -123.2803 | -123.2162
2405.7656 | 123.1979 | -60.8917 | 62.0178 | 0.11803 | -0.0071478 | -0.013907 | 0.00071144 | 0.057542 | -0.0056503 | 0.066984 | -61.0519 | 62.0728 | -61.2122 | -61.1114 | 61.853 | 0.16937 | -0.10529 | 0.16022 | 62.1002 | -61.1343 | -0.32043 | 0.054932 | -0.16022 | -0.21973 | -0.1648 | -0.24261 | 0.082398 | 0.16022 | 60.7864 | 61.0519 | 122.7448 | 122.9645 | -0.16022 | 122.9919 | 61.0611 | -0.24261 | 122.9645 | -0.16022 | 61.0611 | 122.7448 | 122.9919 | -123.23 | -123.1522
2406.7656 | 123.1842 | -60.8688 | 62.0453 | 0.13329 | -0.0077888 | -0.014975 | -0.00014316 | 0.059037 | -0.0043685 | 0.068265 | -61.0565 | 62.0819 | -61.2122 | -61.116 | 61.8393 | 0.027466 | -0.09613 | 0.14648 | 62.059 | -61.1526 | -0.34332 | 0.036621 | -0.18768 | -0.24719 | -0.20599 | -0.28381 | 0.013733 | 0.15564 | 60.7727 | 61.0153 | 122.7081 | 122.9507 | -0.18768 | 122.9279 | 60.8963 | -0.28381 | 122.9507 | -0.18768 | 60.8963 | 122.7081 | 122.9279 | -123.2574 | -123.1979
2407.7656 | 123.262 | -60.8505 | 62.0453 | -0.065079 | -0.0090704 | -0.013693 | -0.0022794 | 0.057328 | -0.0037277 | 0.067838 | -61.0062 | 62.1002 | -61.203 | -61.0336 | 61.9034 | 0.13733 | -0.091553 | 0.32044 | 62.059 | -61.1526 | -0.35248 | 0.054932 | -0.15564 | -0.18311 | -0.14191 | -0.30212 | 0.013733 | 0.19684 | 60.759 | 61.171 | 122.7539 | 122.9507 | -0.15564 | 122.9095 | 60.9879 | -0.30212 | 122.9507 | -0.15564 | 60.9879 | 122.7539 | 122.9095 | -123.2483 | -123.1979
2408.7812 | 123.1155 | -60.9283 | 62.059 | 0.056992 | -0.0028754 | -0.0066437 | 0.010752 | 0.060319 | -0.0054367 | 0.063993 | -61.0016 | 62.2055 | -61.2076 | -61.1389 | 61.7615 | -0.045776 | 0.018311 | 0.086975 | 62.0865 | -61.235 | -0.27924 | 0.14648 | -0.073242 | -0.21057 | -0.29755 | -0.3067 | 0.027466 | 0.20599 | 60.9467 | 61.0153 | 122.6898 | 123.1338 | -0.073242 | 123.0148 | 60.8826 | -0.3067 | 123.1338 | -0.073242 | 60.8826 | 122.6898 | 123.0148 | -123.2666 | -123.2941
2409.7656 | 123.1888 | -60.9009 | 62.0316 | 0.1104 | -0.008216 | -0.010489 | -0.00057036 | 0.056901 | -0.0052231 | 0.066343 | -61.0794 | 62.0773 | -61.2167 | -61.1206 | 61.8256 | 0.018311 | -0.10071 | 0.16022 | 62.0499 | -61.1664 | -0.31586 | 0.045777 | -0.17853 | -0.21973 | -0.20599 | -0.2655 | 0.018311 | 0.13733 | 60.8002 | 61.0611 | 122.7264 | 122.9782 | -0.17853 | 122.9507 | 60.9192 | -0.2655 | 122.9782 | -0.17853 | 60.9192 | 122.7264 | 122.9507 | -123.2483 | -123.1979
2410.7656 | 123.1796 | -60.9055 | 62.027 | 0.056992 | -0.0088568 | -0.011343 | -0.00035676 | 0.059678 | -0.0065047 | 0.068052 | -61.0519 | 62.0819 | -61.2213 | -61.1252 | 61.8347 | 0.013733 | -0.10529 | 0.17395 | 62.0636 | -61.1755 | -0.31586 | 0.054931 | -0.14648 | -0.21973 | -0.19226 | -0.27008 | 0.036621 | 0.16937 | 60.8002 | 61.0794 | 122.7402 | 122.9874 | -0.14648 | 122.9691 | 60.9192 | -0.27008 | 122.9874 | -0.14648 | 60.9192 | 122.7402 | 122.9691 | -123.2483 | -123.2025
2411.7656 | 123.175 | -60.8826 | 62.0178 | 0.17143 | -0.008216 | -0.012625 | 0.0017794 | 0.057969 | -0.0050095 | 0.06677 | -61.0382 | 62.0728 | -61.1984 | -61.1343 | 61.8027 | 0.022888 | -0.1236 | 0.16479 | 62.0453 | -61.1801 | -0.31586 | 0.054932 | -0.15564 | -0.25177 | -0.21515 | -0.29755 | 0.027466 | 0.16022 | 60.759 | 61.0474 | 122.6852 | 122.9553 | -0.15564 | 122.9279 | 60.9055 | -0.29755 | 122.9553 | -0.15564 | 60.9055 | 122.6852 | 122.9279 | -123.2162 | -123.1979
2412.7656 | 123.2117 | -60.8597 | 62.0407 | 0.0035856 | -0.0069342 | -0.010489 | -0.0022794 | 0.057755 | -0.0077865 | 0.065275 | -61.0291 | 62.0728 | -61.2076 | -61.0794 | 61.8668 | 0.07782 | -0.073242 | 0.23804 | 62.0819 | -61.1572 | -0.3479 | 0.032044 | -0.16937 | -0.21973 | -0.17395 | -0.29755 | 0.041199 | 0.17853 | 60.7864 | 61.0977 | 122.7264 | 122.9324 | -0.16937 | 122.9416 | 60.9375 | -0.29755 | 122.9324 | -0.16937 | 60.9375 | 122.7264 | 122.9416 | -123.2483 | -123.1979
2413.7812 | 123.1705 | -60.8688 | 62.0728 | -0.11848 | -0.0050116 | -0.011343 | 0.0079744 | 0.060105 | -0.0069321 | 0.063138 | -61.0107 | 62.1872 | -61.2076 | -61.0977 | 61.821 | 0.073242 | 0.07782 | 0.19226 | 62.1231 | -61.2076 | -0.33875 | 0.11444 | -0.14191 | -0.22888 | -0.25177 | -0.33875 | 0.050354 | 0.19684 | 60.9467 | 61.0611 | 122.6898 | 123.056 | -0.14191 | 122.9919 | 60.9421 | -0.33875 | 123.056 | -0.14191 | 60.9421 | 122.6898 | 122.9919 | -123.2803 | -123.2803
2414.7812 | 123.1934 | -60.9146 | 62.0407 | 0.13329 | -0.0080024 | -0.015616 | -0.00014316 | 0.058823 | -0.0047957 | 0.068693 | -61.0519 | 62.059 | -61.2213 | -61.1435 | 61.8164 | 0.009155 | -0.086975 | 0.14648 | 62.0865 | -61.1526 | -0.3067 | 0.018311 | -0.13733 | -0.22888 | -0.2243 | -0.23804 | 0.045777 | 0.16937 | 60.8276 | 61.0611 | 122.731 | 122.9736 | -0.13733 | 123.0011 | 60.9238 | -0.23804 | 122.9736 | -0.13733 | 60.9238 | 122.731 | 123.0011 | -123.262 | -123.1934
2415.7656 | 123.1934 | -60.8871 | 61.9812 | 0.2935 | -0.0062934 | -0.012625 | 0.00712 | 0.060319 | -0.0060775 | 0.066343 | -60.997 | 62.059 | -61.2305 | -61.084 | 61.8484 | 0.041199 | -0.19684 | 0.17853 | 62.0132 | -61.1984 | -0.34332 | 0.07782 | -0.10986 | -0.19684 | -0.13275 | -0.31128 | 0.032044 | 0.23346 | 60.6903 | 61.0657 | 122.7356 | 122.9462 | -0.10986 | 122.9004 | 60.9283 | -0.31128 | 122.9462 | -0.10986 | 60.9283 | 122.7356 | 122.9004 | -123.2117 | -123.1796
2416.7656 | 123.23 | -60.8826 | 62.0178 | -0.0040434 | -0.0056524 | -0.01113 | 0.0039156 | 0.061173 | -0.0043685 | 0.067838 | -60.9741 | 62.1048 | -61.203 | -61.0886 | 61.8393 | 0.032043 | -0.1831 | 0.1831 | 62.0865 | -61.1618 | -0.32044 | 0.086975 | -0.091553 | -0.20599 | -0.17853 | -0.27924 | 0.068665 | 0.22888 | 60.6995 | 61.0657 | 122.7219 | 122.9874 | -0.091553 | 122.9691 | 60.9146 | -0.27924 | 122.9874 | -0.091553 | 60.9146 | 122.7219 | 122.9691 | -123.2208 | -123.1796
2417.7656 | 123.2254 | -60.8871 | 62.0041 | 0.24773 | -0.0071478 | -0.0098479 | 0.005411 | 0.059464 | -0.0056503 | 0.065275 | -60.9879 | 62.0819 | -61.1664 | -60.9787 | 61.94 | 0.082397 | -0.17395 | 0.21057 | 62.0819 | -61.1847 | -0.27924 | 0.07782 | -0.10071 | -0.091553 | -0.064087 | -0.29755 | 0.07782 | 0.17853 | 60.7132 | 61.0977 | 122.8271 | 122.9691 | -0.10071 | 122.9691 | 60.9695 | -0.29755 | 122.9691 | -0.10071 | 60.9695 | 122.8271 | 122.9691 | -123.1705 | -123.1888
2418.7969 | 123.1979 | -60.8917 | 61.9995 | 0.26299 | -0.0052252 | -0.0077117 | 0.0056246 | 0.060532 | -0.0043685 | 0.066129 | -61.0153 | 62.1002 | -61.2213 | -61.0931 | 61.8393 | 0 | -0.17395 | 0.14191 | 62.0407 | -61.1938 | -0.32959 | 0.10071 | -0.1236 | -0.20142 | -0.16022 | -0.30212 | 0.041198 | 0.20599 | 60.7178 | 61.0336 | 122.731 | 122.9919 | -0.1236 | 122.9324 | 60.8917 | -0.30212 | 122.9919 | -0.1236 | 60.8917 | 122.731 | 122.9324 | -123.2208 | -123.1934
2419.7656 | 123.175 | -60.8963 | 62.0361 | 0.1638 | -0.0069342 | -0.011557 | 0.00071144 | 0.057969 | -0.0065047 | 0.065916 | -61.0657 | 62.0819 | -61.2122 | -61.1252 | 61.821 | 0.022888 | -0.073242 | 0.16937 | 62.0956 | -61.1847 | -0.31586 | 0.045776 | -0.16937 | -0.22888 | -0.21515 | -0.28839 | 0.059509 | 0.14648 | 60.8231 | 61.0657 | 122.7173 | 122.9782 | -0.16937 | 122.9919 | 60.9192 | -0.28839 | 122.9782 | -0.16937 | 60.9192 | 122.7173 | 122.9919 | -123.2483 | -123.2208
2420.7656 | 123.2117 | -60.9055 | 62.0087 | 0.17906 | -0.0090704 | -0.015616 | 7.0444e-05 | 0.059037 | -0.0065047 | 0.065916 | -61.0382 | 62.0911 | -61.1984 | -61.1206 | 61.8164 | 0.022888 | -0.1236 | 0.15564 | 62.0819 | -61.1755 | -0.29297 | 0.082397 | -0.13275 | -0.21515 | -0.19226 | -0.27008 | 0.073242 | 0.16022 | 60.7819 | 61.0611 | 122.7219 | 122.9965 | -0.13275 | 122.9874 | 60.9283 | -0.27008 | 122.9965 | -0.13275 | 60.9283 | 122.7219 | 122.9874 | -123.2071 | -123.1842
2421.7812 | 123.2208 | -60.8826 | 62.0178 | 0.14854 | -0.0067206 | -0.010916 | 0.0060518 | 0.058182 | -0.0062911 | 0.068052 | -61.0062 | 62.0773 | -61.2305 | -61.0794 | 61.8347 | 0.022888 | -0.19684 | 0.19226 | 62.0316 | -61.1984 | -0.3479 | 0.05951 | -0.1236 | -0.19684 | -0.18311 | -0.31586 | 0.013733 | 0.2243 | 60.6857 | 61.0748 | 122.7173 | 122.9599 | -0.1236 | 122.9141 | 60.9055 | -0.31586 | 122.9599 | -0.1236 | 60.9055 | 122.7173 | 122.9141 | -123.2483 | -123.2162
2422.7812 | 123.2254 | -60.9055 | 62.0132 | 0.21721 | -0.006507 | -0.0068573 | 0.0064792 | 0.063309 | -0.0058639 | 0.06912 | -60.9924 | 62.0956 | -61.235 | -61.0794 | 61.8393 | 0.018311 | -0.19226 | 0.16022 | 62.0865 | -61.1801 | -0.32959 | 0.082397 | -0.086975 | -0.17395 | -0.17395 | -0.27466 | 0.073242 | 0.24261 | 60.7132 | 61.0657 | 122.7448 | 123.0011 | -0.086975 | 122.9919 | 60.9238 | -0.27466 | 123.0011 | -0.086975 | 60.9238 | 122.7448 | 122.9919 | -123.2483 | -123.1934
2423.7812 | 123.2346 | -60.8963 | 61.9858 | 0.2935 | -0.0071478 | -0.0089935 | 0.0051974 | 0.059678 | -0.0054367 | 0.065061 | -60.9787 | 62.1185 | -61.203 | -61.0748 | 61.853 | 0.14648 | -0.46692 | 0.10071 | 62.0361 | -61.1984 | -0.3067 | 0.13275 | -0.082398 | -0.17853 | -0.13275 | -0.30212 | 0.050354 | 0.2243 | 60.4294 | 60.997 | 122.7493 | 123.0148 | -0.082398 | 122.9324 | 61.0428 | -0.30212 | 123.0148 | -0.082398 | 61.0428 | 122.7493 | 122.9324 | -123.1888 | -123.1842
2424.7812 | 123.1934 | -60.8734 | 62.0361 | 0.17906 | -0.0086432 | -0.012839 | 0.00049764 | 0.059251 | -0.0060775 | 0.067838 | -61.0565 | 62.0728 | -61.2122 | -61.1252 | 61.8164 | 0.009155 | -0.10986 | 0.15564 | 62.0544 | -61.1938 | -0.33875 | 0.036621 | -0.18311 | -0.25177 | -0.21973 | -0.32044 | 0.01831 | 0.15564 | 60.7636 | 61.0291 | 122.6898 | 122.9462 | -0.18311 | 122.9279 | 60.8826 | -0.32044 | 122.9462 | -0.18311 | 60.8826 | 122.6898 | 122.9279 | -123.2483 | -123.23
2425.7812 | 123.2071 | -60.8871 | 62.0041 | 0.22484 | -0.0067206 | -0.014975 | 0.001993 | 0.060105 | -0.0041549 | 0.068052 | -61.0199 | 62.0956 | -61.2122 | -61.116 | 61.8347 | 0.009155 | -0.15106 | 0.16479 | 62.0544 | -61.1847 | -0.32501 | 0.091553 | -0.13275 | -0.22888 | -0.16937 | -0.29755 | 0.050354 | 0.19226 | 60.7361 | 61.0519 | 122.7219 | 122.9828 | -0.13275 | 122.9416 | 60.8963 | -0.29755 | 122.9828 | -0.13275 | 60.8963 | 122.7219 | 122.9416 | -123.2162 | -123.1888
2426.7812 | 123.1842 | -60.8871 | 62.0316 | 0.17906 | -0.0084296 | -0.014548 | 0.00049764 | 0.058182 | -0.0060775 | 0.066556 | -61.0611 | 62.0636 | -61.2122 | -61.1298 | 61.8073 | 0.022888 | -0.1236 | 0.16479 | 62.1002 | -61.171 | -0.32501 | 0.032044 | -0.17395 | -0.24262 | -0.2243 | -0.28381 | 0.068665 | 0.15106 | 60.7636 | 61.0519 | 122.6944 | 122.9507 | -0.17395 | 122.9874 | 60.91 | -0.28381 | 122.9507 | -0.17395 | 60.91 | 122.6944 | 122.9874 | -123.2437 | -123.2025
2427.7812 | 123.1842 | -60.8963 | 62.0316 | 0.1104 | -0.0067206 | -0.011984 | 0.00071144 | 0.058182 | -0.0045821 | 0.068906 | -61.0611 | 62.0682 | -61.2167 | -61.1298 | 61.8118 | 0.009155 | -0.086975 | 0.15564 | 62.0636 | -61.1893 | -0.32043 | 0.036621 | -0.16479 | -0.23346 | -0.21973 | -0.29297 | 0.032044 | 0.15564 | 60.8093 | 61.0519 | 122.7081 | 122.9645 | -0.16479 | 122.9599 | 60.9055 | -0.29297 | 122.9645 | -0.16479 | 60.9055 | 122.7081 | 122.9599 | -123.2483 | -123.2208
2428.7969 | 123.2025 | -60.8826 | 62.0224 | 0.24773 | -0.0077888 | -0.015402 | 0.0024202 | 0.059464 | -0.0047957 | 0.067624 | -61.0153 | 62.0499 | -61.2167 | -61.1206 | 61.8301 | 0.013733 | -0.13275 | 0.16022 | 62.0544 | -61.1618 | -0.33417 | 0.027466 | -0.13275 | -0.23804 | -0.19226 | -0.27924 | 0.032043 | 0.20142 | 60.7498 | 61.0428 | 122.7127 | 122.9324 | -0.13275 | 122.937 | 60.8963 | -0.27924 | 122.9324 | -0.13275 | 60.8963 | 122.7127 | 122.937 | -123.2391 | -123.1842
2429.7969 | 123.2346 | -60.8597 | 62.0132 | 0.26299 | -0.0069342 | -0.011343 | 0.0034884 | 0.057542 | -0.0045821 | 0.067624 | -60.9833 | 62.1002 | -61.203 | -61.1298 | 61.9308 | 0.10529 | -0.16022 | 0.20599 | 62.0499 | -61.1755 | -0.34332 | 0.086975 | -0.1236 | -0.27008 | -0.082398 | -0.31586 | 0.036621 | 0.21973 | 60.6995 | 61.0657 | 122.7905 | 122.9599 | -0.1236 | 122.9095 | 60.965 | -0.31586 | 122.9599 | -0.1236 | 60.965 | 122.7905 | 122.9095 | -123.2162 | -123.1888
2430.7812 | 123.2208 | -60.8826 | 62.0087 | 0.41557 | -0.0067206 | -0.010062 | 0.0032748 | 0.060532 | -0.0045821 | 0.064847 | -60.9009 | 62.1048 | -61.2167 | -61.0611 | 61.8301 | 0.032043 | -0.21973 | 0.17395 | 62.0407 | -61.1847 | -0.33417 | 0.09613 | -0.018311 | -0.17853 | -0.17853 | -0.30212 | 0.032043 | 0.31586 | 60.6628 | 61.0565 | 122.7127 | 122.9874 | -0.018311 | 122.9233 | 60.9146 | -0.30212 | 122.9874 | -0.018311 | 60.9146 | 122.7127 | 122.9233 | -123.2254 | -123.1934
2431.7812 | 123.1659 | -60.878 | 62.0453 | 0.21721 | -0.0086432 | -0.01348 | 0.00071144 | 0.057328 | -0.0043685 | 0.068479 | -61.0611 | 62.0956 | -61.2122 | -61.1389 | 61.8027 | 0.009155 | -0.091553 | 0.16479 | 62.0956 | -61.2167 | -0.33417 | 0.050354 | -0.1831 | -0.26093 | -0.24262 | -0.33874 | 0.050354 | 0.15106 | 60.7864 | 61.0428 | 122.6807 | 122.9736 | -0.1831 | 122.9736 | 60.8871 | -0.33874 | 122.9736 | -0.1831 | 60.8871 | 122.6807 | 122.9736 | -123.2574 | -123.262
2432.7812 | 123.2437 | -60.878 | 62.0041 | 0.087509 | -0.0073614 | -0.011984 | 0.0013522 | 0.056473 | -0.0028731 | 0.068052 | -61.0565 | 62.0865 | -61.2122 | -61.1343 | 61.8347 | 0.013733 | -0.07782 | 0.17395 | 62.0819 | -61.171 | -0.33417 | 0.082398 | -0.17853 | -0.25635 | -0.16937 | -0.29297 | 0.07782 | 0.15564 | 60.8002 | 61.0519 | 122.7127 | 122.9645 | -0.17853 | 122.9599 | 60.8917 | -0.29297 | 122.9645 | -0.17853 | 60.8917 | 122.7127 | 122.9599 | -123.2162 | -123.175
2433.7969 | 123.2391 | -60.8963 | 62.0087 | 0.14854 | -0.0060798 | -0.013266 | 0.005411 | 0.05861 | -0.0060775 | 0.066343 | -61.0199 | 62.1094 | -61.1938 | -61.0794 | 61.8439 | 0.041199 | -0.19226 | 0.1831 | 62.0316 | -61.171 | -0.29755 | 0.10071 | -0.1236 | -0.18311 | -0.1648 | -0.27466 | 0.022888 | 0.17395 | 60.704 | 61.0794 | 122.7402 | 123.0057 | -0.1236 | 122.9279 | 60.9375 | -0.27466 | 123.0057 | -0.1236 | 60.9375 | 122.7402 | 122.9279 | -123.2025 | -123.1796
2434.7812 | 123.1979 | -60.8871 | 62.027 | 0.15617 | -0.0088568 | -0.010703 | 0.00049764 | 0.058182 | -0.0054367 | 0.068906 | -61.0519 | 62.0865 | -61.2076 | -61.1572 | 61.8164 | 0.018311 | -0.10071 | 0.16022 | 62.0682 | -61.1801 | -0.32043 | 0.059509 | -0.16479 | -0.27008 | -0.21057 | -0.29297 | 0.041198 | 0.15564 | 60.7864 | 61.0474 | 122.7036 | 122.9736 | -0.16479 | 122.9553 | 60.9055 | -0.29297 | 122.9736 | -0.16479 | 60.9055 | 122.7036 | 122.9553 | -123.2346 | -123.2071
2435.7812 | 123.1705 | -60.8917 | 62.0407 | 0.07988 | -0.008216 | -0.010062 | 0.0013522 | 0.058396 | -0.0037277 | 0.065275 | -61.0703 | 62.0773 | -61.2167 | -61.1252 | 61.821 | 0.013733 | -0.073242 | 0.21057 | 62.0819 | -61.1664 | -0.32501 | 0.036622 | -0.17853 | -0.23346 | -0.21973 | -0.27466 | 0.041199 | 0.14648 | 60.8185 | 61.1023 | 122.7127 | 122.9691 | -0.17853 | 122.9736 | 60.9055 | -0.27466 | 122.9691 | -0.17853 | 60.9055 | 122.7127 | 122.9736 | -123.2574 | -123.2071
2436.7812 | 123.1979 | -60.9283 | 62.027 | -0.026932 | -0.007575 | -0.0079253 | -0.0012112 | 0.057542 | -0.0065047 | 0.066984 | -61.0657 | 62.0773 | -61.2305 | -61.1023 | 61.8301 | 0.032043 | -0.073242 | 0.20142 | 62.0636 | -61.171 | -0.30212 | 0.050354 | -0.13733 | -0.17395 | -0.19684 | -0.24261 | 0.036621 | 0.16479 | 60.8551 | 61.1298 | 122.7585 | 123.0057 | -0.13733 | 122.9919 | 60.9604 | -0.24261 | 123.0057 | -0.13733 | 60.9604 | 122.7585 | 122.9919 | -123.2574 | -123.1979
2437.7812 | 123.2254 | -60.8597 | 62.0407 | 0.026474 | -0.006507 | -0.013266 | 0.002634 | 0.056687 | -0.0062911 | 0.065702 | -61.0336 | 62.0911 | -61.1984 | -61.0703 | 61.8713 | 0.086975 | -0.09613 | 0.26093 | 62.059 | -61.1755 | -0.33875 | 0.050354 | -0.17395 | -0.21057 | -0.16937 | -0.31586 | 0.018311 | 0.16479 | 60.7635 | 61.1206 | 122.731 | 122.9507 | -0.17395 | 122.9187 | 60.9467 | -0.31586 | 122.9507 | -0.17395 | 60.9467 | 122.731 | 122.9187 | -123.2391 | -123.2162
2438.7969 | 123.2346 | -60.8688 | 62.0132 | 0.2401 | -0.005866 | -0.010703 | 0.0060518 | 0.057969 | -0.0052231 | 0.068265 | -60.9833 | 62.0956 | -61.203 | -61.2167 | 61.94 | 0.09613 | -0.15106 | 0.21057 | 62.059 | -61.1847 | -0.33417 | 0.082397 | -0.11444 | -0.3479 | -0.073243 | -0.31586 | 0.045776 | 0.21973 | 60.7178 | 61.0794 | 122.8088 | 122.9645 | -0.11444 | 122.9279 | 60.965 | -0.31586 | 122.9645 | -0.11444 | 60.965 | 122.8088 | 122.9279 | -123.2162 | -123.1979
2439.7812 | 123.1705 | -60.8917 | 62.0453 | 0.072251 | -0.009284 | -0.013052 | -0.00035676 | 0.055619 | -0.0062911 | 0.069761 | -61.0565 | 62.0728 | -61.2442 | -61.1069 | 61.8439 | 0.059509 | -0.086975 | 0.21973 | 62.059 | -61.1572 | -0.35248 | 0.027466 | -0.16479 | -0.21515 | -0.20142 | -0.2655 | 0.013733 | 0.18768 | 60.8047 | 61.1115 | 122.7356 | 122.9645 | -0.16479 | 122.9507 | 60.9512 | -0.2655 | 122.9645 | -0.16479 | 60.9512 | 122.7356 | 122.9507 | -123.2895 | -123.2025
2440.7812 | 123.2437 | -60.8322 | 62.0819 | -0.057449 | -0.0080024 | -0.012839 | -0.00014316 | 0.056687 | -0.0077865 | 0.068693 | -60.9879 | 62.0911 | -61.203 | -61.0062 | 61.9263 | 0.13733 | -0.054932 | 0.32044 | 62.0865 | -61.1389 | -0.37079 | 0.009155 | -0.15564 | -0.17395 | -0.15564 | -0.3067 | 0.004578 | 0.21515 | 60.7773 | 61.1526 | 122.7585 | 122.9233 | -0.15564 | 122.9187 | 60.9695 | -0.3067 | 122.9233 | -0.15564 | 60.9695 | 122.7585 | 122.9187 | -123.2849 | -123.2208
2441.7812 | 123.1842 | -60.8917 | 62.0453 | 0.15617 | -0.0062934 | -0.01113 | 0.0017794 | 0.056687 | -0.0045821 | 0.066129 | -61.0519 | 62.0865 | -61.2122 | -61.1298 | 61.8164 | -0.009155 | -0.10071 | 0.16022 | 62.059 | -61.1847 | -0.32043 | 0.041199 | -0.16022 | -0.23804 | -0.22888 | -0.29297 | 0.013733 | 0.16022 | 60.791 | 61.0519 | 122.7081 | 122.9782 | -0.16022 | 122.9507 | 60.8826 | -0.29297 | 122.9782 | -0.16022 | 60.8826 | 122.7081 | 122.9507 | -123.2574 | -123.23
2442.7812 | 123.2254 | -60.878 | 62.0453 | 0.049362 | -0.0077888 | -0.011771 | -0.0012112 | 0.055619 | -0.0052231 | 0.068479 | -61.0474 | 62.0819 | -61.2213 | -61.1023 | 61.8576 | 0.059509 | -0.073242 | 0.21515 | 62.0865 | -61.171 | -0.34332 | 0.036621 | -0.16937 | -0.2243 | -0.18768 | -0.29297 | 0.041199 | 0.17395 | 60.8047 | 61.0931 | 122.7356 | 122.9599 | -0.16937 | 122.9645 | 60.9375 | -0.29297 | 122.9599 | -0.16937 | 60.9375 | 122.7356 | 122.9645 | -123.2666 | -123.2162
2443.7969 | 123.2208 | -60.9055 | 62.0087 | 0.17143 | -0.0067206 | -0.013907 | 0.0039156 | 0.058396 | -0.0047957 | 0.065702 | -60.9879 | 62.0911 | -61.203 | -61.084 | 61.8439 | 0.022888 | -0.20142 | 0.17395 | 62.0361 | -61.1984 | -0.29755 | 0.082397 | -0.082397 | -0.17853 | -0.1648 | -0.29297 | 0.027466 | 0.21515 | 60.704 | 61.0794 | 122.7493 | 122.9965 | -0.082397 | 122.9416 | 60.9283 | -0.29297 | 122.9965 | -0.082397 | 60.9283 | 122.7493 | 122.9416 | -123.2117 | -123.2071
2444.7812 | 123.2071 | -60.9055 | 62.0316 | 0.095139 | -0.0088568 | -0.015189 | -0.0016386 | 0.058182 | -0.0047957 | 0.067838 | -61.0565 | 62.0911 | -61.2213 | -61.0977 | 61.8256 | 0.004578 | -0.068665 | 0.18768 | 62.0544 | -61.1938 | -0.31586 | 0.059509 | -0.15106 | -0.19226 | -0.20599 | -0.28839 | 0.022888 | 0.16479 | 60.8368 | 61.0931 | 122.731 | 122.9965 | -0.15106 | 122.9599 | 60.91 | -0.28839 | 122.9965 | -0.15106 | 60.91 | 122.731 | 122.9599 | -123.2529 | -123.2254
2445.7812 | 123.23 | -60.8551 | 62.0407 | -0.019302 | -0.0094976 | -0.0096343 | 0.0015658 | 0.057542 | -0.0054367 | 0.066984 | -60.997 | 62.0819 | -61.2076 | -61.0199 | 61.8942 | 0.1236 | -0.068665 | 0.3067 | 62.0499 | -61.1206 | -0.35248 | 0.041199 | -0.14191 | -0.16479 | -0.14648 | -0.2655 | 0.009156 | 0.21057 | 60.7864 | 61.1618 | 122.7493 | 122.937 | -0.14191 | 122.905 | 60.9787 | -0.2655 | 122.937 | -0.14191 | 60.9787 | 122.7493 | 122.905 | -123.2483 | -123.1613
2446.7812 | 123.2254 | -60.8643 | 62.0407 | -0.10323 | -0.0069342 | -0.012625 | -0.00099756 | 0.057542 | -0.0041549 | 0.066556 | -60.965 | 62.0865 | -61.2076 | -61.0382 | 61.8896 | 0.13275 | -0.059509 | 0.3067 | 62.0865 | -61.1298 | -0.34332 | 0.045777 | -0.10071 | -0.17395 | -0.15106 | -0.2655 | 0.045777 | 0.24262 | 60.8047 | 61.171 | 122.7539 | 122.9507 | -0.10071 | 122.9507 | 60.997 | -0.2655 | 122.9507 | -0.10071 | 60.997 | 122.7539 | 122.9507 | -123.2483 | -123.1705
2447.7812 | 123.2346 | -60.8643 | 62.0682 | -2.0106 | -0.0084296 | -0.0066437 | 0.002634 | 0.05861 | -0.0071457 | 0.067624 | -61.1618 | 62.1277 | -61.1938 | -61.0428 | 61.8851 | 0.13275 | -0.032043 | 0.31586 | 62.0911 | -61.171 | -0.32959 | 0.05951 | -0.29755 | -0.17853 | -0.1831 | -0.3067 | 0.022888 | 0.032044 | 60.8322 | 61.1801 | 122.7493 | 122.9919 | -0.29755 | 122.9553 | 60.997 | -0.3067 | 122.9919 | -0.29755 | 60.997 | 122.7493 | 122.9553 | -123.262 | -123.2391
2448.7969 | 123.1201 | -60.9283 | 62.1002 | 0.10277 | -0.0043708 | -0.0085663 | 0.010538 | 0.058823 | -0.0052231 | 0.06912 | -61.0107 | 62.1826 | -61.2213 | -61.1389 | 61.7661 | -0.027466 | 0.004578 | 0.11444 | 62.1048 | -61.2259 | -0.29297 | 0.082397 | -0.082397 | -0.21057 | -0.33417 | -0.29755 | 0.004577 | 0.21057 | 60.9329 | 61.0428 | 122.6944 | 123.111 | -0.082397 | 123.0331 | 60.9009 | -0.29755 | 123.111 | -0.082397 | 60.9009 | 122.6944 | 123.0331 | -123.3215 | -123.3261
2449.7812 | 123.1476 | -60.91 | 62.0773 | -0.17952 | -0.009284 | -0.01113 | 0.00049764 | 0.060105 | -0.0060775 | 0.068265 | -61.0153 | 62.1552 | -61.203 | -61.1023 | 61.8256 | 0.068665 | 0.09613 | 0.25177 | 62.146 | -61.1755 | -0.29297 | 0.077819 | -0.10529 | -0.19226 | -0.25177 | -0.2655 | 0.068664 | 0.18768 | 61.0062 | 61.1618 | 122.7356 | 123.0652 | -0.10529 | 123.056 | 60.9787 | -0.2655 | 123.0652 | -0.10529 | 60.9787 | 122.7356 | 123.056 | -123.2803 | -123.2529
2450.7812 | 123.1659 | -60.8734 | 62.059 | -0.24055 | -0.0086432 | -0.011984 | 0.0017794 | 0.059251 | -0.0060775 | 0.067411 | -61.0062 | 62.1368 | -61.203 | -61.0794 | 61.8576 | 0.11444 | 0.059509 | 0.27008 | 62.0865 | -61.171 | -0.32959 | 0.07782 | -0.13275 | -0.20599 | -0.20142 | -0.29755 | 0.027466 | 0.19684 | 60.9329 | 61.1435 | 122.731 | 123.0103 | -0.13275 | 122.9599 | 60.9879 | -0.29755 | 123.0103 | -0.13275 | 60.9879 | 122.731 | 122.9599 | -123.262 | -123.23
2451.7812 | 123.1934 | -60.8643 | 62.0544 | -0.17189 | -0.0077888 | -0.012198 | 0.00028404 | 0.060746 | -0.0047957 | 0.066984 | -60.9833 | 62.1368 | -61.1618 | -61.0565 | 61.8805 | 0.1236 | 0.022888 | 0.28381 | 62.1002 | -61.1664 | -0.29755 | 0.082398 | -0.11902 | -0.19226 | -0.17395 | -0.30212 | 0.045777 | 0.17853 | 60.8871 | 61.1481 | 122.7448 | 123.0011 | -0.11902 | 122.9645 | 60.9879 | -0.30212 | 123.0011 | -0.11902 | 60.9879 | 122.7448 | 122.9645 | -123.2162 | -123.2208
2452.7812 | 123.0972 | -60.9146 | 62.0865 | -0.17952 | -0.0069342 | -0.010489 | 0.0028476 | 0.059891 | -0.0060775 | 0.065061 | -61.0428 | 62.2055 | -61.2167 | -60.9787 | 61.9492 | 0.022888 | 0.054932 | 0.14648 | 62.1277 | -61.2122 | -0.30212 | 0.11902 | -0.12817 | -0.064087 | -0.13733 | -0.29755 | 0.041199 | 0.17395 | 60.9695 | 61.0611 | 122.8638 | 123.1201 | -0.12817 | 123.0423 | 60.9375 | -0.29755 | 123.1201 | -0.12817 | 60.9375 | 122.8638 | 123.0423 | -123.3032 | -123.2986
2453.7812 | 123.1842 | -60.8917 | 62.059 | -0.87379 | -0.009284 | -0.017111 | -0.0016386 | 0.060319 | -0.0054367 | 0.068693 | -61.0886 | 62.1048 | -61.2305 | -61.1206 | 61.8301 | 0.032043 | -0.082397 | 0.1831 | 62.0682 | -61.1435 | -0.33874 | 0.045776 | -0.19684 | -0.22888 | -0.22888 | -0.25177 | 0.009155 | 0.14191 | 60.8093 | 61.0748 | 122.7219 | 122.9965 | -0.19684 | 122.9599 | 60.9238 | -0.25177 | 122.9965 | -0.19684 | 60.9238 | 122.7219 | 122.9599 | -123.2895 | -123.2025
2454.7812 | 123.2391 | -60.8963 | 62.027 | 0.2401 | -0.0045844 | -0.011771 | 0.00712 | 0.061173 | -0.0067185 | 0.065702 | -61.0291 | 62.1597 | -61.2213 | -61.1252 | 61.8073 | 0.009155 | -0.16479 | 0.12817 | 62.0636 | -61.2076 | -0.32501 | 0.13275 | -0.13275 | -0.22888 | -0.21973 | -0.31128 | 0.036621 | 0.19226 | 60.7315 | 61.0245 | 122.7036 | 123.056 | -0.13275 | 122.9599 | 60.9055 | -0.31128 | 123.056 | -0.13275 | 60.9055 | 122.7036 | 122.9599 | -123.2483 | -123.2346
2455.7969 | 123.1064 | -60.9421 | 62.0361 | 0.1104 | -0.0035162 | -0.0083527 | 0.0079744 | 0.062669 | -0.0060775 | 0.065488 | -61.0199 | 62.2101 | -61.2259 | -61.1343 | 61.7706 | -0.018311 | 0 | 0.082397 | 62.1002 | -61.235 | -0.28381 | 0.17395 | -0.077819 | -0.19226 | -0.2655 | -0.29297 | 0.064087 | 0.20599 | 60.9421 | 61.0245 | 122.7127 | 123.1522 | -0.077819 | 123.0423 | 60.9238 | -0.29297 | 123.1522 | -0.077819 | 60.9238 | 122.7127 | 123.0423 | -123.262 | -123.2712
2456.7812 | 123.2162 | -60.8871 | 62.0132 | 2.2924 | -0.0084296 | -0.010916 | 0.00071144 | 0.06096 | -0.0058639 | 0.065275 | -60.9695 | 62.0956 | -61.1938 | -61.0931 | 61.8759 | 0.032043 | -0.19226 | 0.15564 | 62.0636 | -61.1618 | -0.3067 | 0.082397 | -0.082397 | -0.20599 | -0.13733 | -0.27466 | 0.050354 | 0.22431 | 60.6949 | 61.0428 | 122.7631 | 122.9828 | -0.082397 | 122.9507 | 60.9192 | -0.27466 | 122.9828 | -0.082397 | 60.9192 | 122.7631 | 122.9507 | -123.2071 | -123.175
2457.7812 | 123.143 | -60.8963 | 62.0224 | 0.22484 | -0.0054388 | -0.0096343 | 0.0056246 | 0.060532 | -0.0056503 | 0.066129 | -61.0565 | 62.178 | -61.2579 | -61.1664 | 61.7752 | -0.050354 | -0.064087 | 0.064087 | 62.0819 | -61.2259 | -0.36163 | 0.15564 | -0.16022 | -0.27008 | -0.24719 | -0.32959 | 0.059509 | 0.20142 | 60.8322 | 60.9604 | 122.6715 | 123.0743 | -0.16022 | 122.9782 | 60.8459 | -0.32959 | 123.0743 | -0.16022 | 60.8459 | 122.6715 | 122.9782 | -123.2803 | -123.2483
2458.7812 | 123.1979 | -60.8688 | 62.0178 | 0.17906 | -0.004798 | -0.013266 | 0.0022066 | 0.059678 | -0.0062911 | 0.068052 | -61.0153 | 62.1002 | -61.2534 | -61.0977 | 61.8484 | 0.059509 | -0.16937 | 0.17853 | 62.0453 | -61.1801 | -0.38452 | 0.082398 | -0.14649 | -0.22888 | -0.16937 | -0.31128 | 0.027466 | 0.23804 | 60.6995 | 61.0474 | 122.7173 | 122.9691 | -0.14649 | 122.9141 | 60.9283 | -0.31128 | 122.9691 | -0.14649 | 60.9283 | 122.7173 | 122.9141 | -123.2712 | -123.1979
2459.7812 | 123.1934 | -60.8917 | 62.0132 | 0.1638 | -0.007575 | -0.012839 | 0.003702 | 0.058823 | -0.0020187 | 0.066556 | -61.0016 | 62.1002 | -61.203 | -61.1069 | 61.8668 | 0.054932 | -0.18768 | 0.16937 | 62.0499 | -61.1893 | -0.31128 | 0.086975 | -0.10986 | -0.21515 | -0.14648 | -0.29755 | 0.036621 | 0.20142 | 60.704 | 61.0611 | 122.7585 | 122.9919 | -0.10986 | 122.9416 | 60.9467 | -0.29755 | 122.9919 | -0.10986 | 60.9467 | 122.7585 | 122.9416 | -123.2162 | -123.2025
2460.7812 | 123.175 | -60.878 | 62.0453 | 0.11803 | -0.0077888 | -0.012198 | -0.0018522 | 0.059251 | -0.0047957 | 0.068052 | -61.0657 | 62.0773 | -61.2167 | -61.1481 | 61.8301 | 0.027466 | -0.082397 | 0.16479 | 62.0865 | -61.1618 | -0.33874 | 0.032044 | -0.18768 | -0.27008 | -0.21515 | -0.28381 | 0.041199 | 0.15106 | 60.7956 | 61.0428 | 122.7081 | 122.9553 | -0.18768 | 122.9645 | 60.9055 | -0.28381 | 122.9553 | -0.18768 | 60.9055 | 122.7081 | 122.9645 | -123.262 | -123.2071
2461.7812 | 123.1934 | -60.9329 | 62.0361 | 0.21721 | -0.005866 | -0.010489 | 0.0079744 | 0.060746 | -0.0052231 | 0.066556 | -61.0703 | 62.1826 | -61.2213 | -61.1847 | 61.7477 | -0.073242 | -0.11902 | -0.31586 | 62.0316 | -61.2854 | -0.28839 | 0.14648 | -0.13733 | -0.25177 | -0.28839 | -0.35248 | -0.004578 | 0.15106 | 60.8139 | 60.6171 | 122.6807 | 123.1155 | -0.13733 | 122.9645 | 60.8597 | -0.35248 | 123.1155 | -0.13733 | 60.8597 | 122.6807 | 122.9645 | -123.2574 | -123.3215
2462.7812 | 123.1201 | -60.9238 | 62.0453 | 0.25536 | -0.0039434 | -0.0094207 | 0.0073336 | 0.058396 | -0.0035141 | 0.066129 | -61.0886 | 62.1964 | -61.2717 | -61.1893 | 61.7569 | -0.050354 | -0.041199 | 0.064087 | 62.0865 | -61.2625 | -0.3479 | 0.15106 | -0.1648 | -0.2655 | -0.28839 | -0.33875 | 0.041199 | 0.1831 | 60.8826 | 60.9879 | 122.6807 | 123.1201 | -0.1648 | 123.0103 | 60.8734 | -0.33875 | 123.1201 | -0.1648 | 60.8734 | 122.6807 | 123.0103 | -123.317 | -123.3078
2463.7812 | 123.2071 | -60.878 | 62.0132 | 0.19432 | -0.008216 | -0.0072845 | 0.0011386 | 0.060319 | -0.0043685 | 0.067197 | -61.0565 | 62.0865 | -61.2396 | -61.1526 | 61.8347 | 0.013733 | -0.1236 | 0.16937 | 62.0728 | -61.1664 | -0.36163 | 0.073242 | -0.17853 | -0.27466 | -0.17853 | -0.28839 | 0.059509 | 0.1831 | 60.7544 | 61.0474 | 122.7127 | 122.9645 | -0.17853 | 122.9507 | 60.8917 | -0.28839 | 122.9645 | -0.17853 | 60.8917 | 122.7127 | 122.9507 | -123.2529 | -123.1796
2464.7812 | 123.2391 | -60.9009 | 62.0087 | 0.27061 | -0.0060798 | -0.011984 | 0.0051974 | 0.059678 | -0.0047957 | 0.068265 | -61.0382 | 62.1048 | -61.2442 | -61.0931 | 61.8393 | 0.036621 | -0.19226 | 0.16022 | 62.0453 | -61.1984 | -0.34332 | 0.09613 | -0.13733 | -0.19226 | -0.16937 | -0.29755 | 0.036621 | 0.20599 | 60.7086 | 61.0611 | 122.7402 | 123.0057 | -0.13733 | 122.9462 | 60.9375 | -0.29755 | 123.0057 | -0.13733 | 60.9375 | 122.7402 | 122.9462 | -123.2529 | -123.2071
2465.7969 | 123.1247 | -60.9238 | 62.0773 | -0.16426 | -0.0026618 | -0.012839 | 0.0032748 | 0.059464 | -0.0069321 | 0.066984 | -61.0565 | 62.2101 | -61.1984 | -61.1206 | 61.8118 | 0.041199 | 0.11444 | 0.20142 | 62.1231 | -61.1938 | -0.27466 | 0.13275 | -0.13275 | -0.19684 | -0.2655 | -0.27008 | 0.045776 | 0.14191 | 61.0382 | 61.1252 | 122.7356 | 123.1338 | -0.13275 | 123.0469 | 60.965 | -0.27008 | 123.1338 | -0.13275 | 60.965 | 122.7356 | 123.0469 | -123.2758 | -123.2712
2466.7812 | 123.0927 | -60.9421 | 62.0407 | 0.064621 | -0.0015936 | -0.0072845 | 0.00712 | 0.063737 | -0.0050095 | 0.065916 | -61.0245 | 62.2147 | -61.2167 | -61.1526 | 61.7661 | -0.032043 | 0.004578 | 0.11902 | 62.1277 | -61.2167 | -0.27466 | 0.17395 | -0.082397 | -0.21057 | -0.27466 | -0.27466 | 0.086976 | 0.19226 | 60.9467 | 61.0611 | 122.7081 | 123.1567 | -0.082397 | 123.0698 | 60.91 | -0.27466 | 123.1567 | -0.082397 | 60.91 | 122.7081 | 123.0698 | -123.2574 | -123.2574
2467.7812 | 123.1064 | -60.91 | 62.0544 | 0.064621 | -0.0045844 | -0.010703 | 0.0084018 | 0.06395 | -0.0058639 | 0.06912 | -61.0062 | 62.1964 | -61.2259 | -61.1526 | 61.7661 | 0.009155 | 0.013733 | 0.13275 | 62.146 | -61.2396 | -0.31586 | 0.14191 | -0.096131 | -0.24261 | -0.28839 | -0.32959 | 0.091553 | 0.21973 | 60.9238 | 61.0428 | 122.6761 | 123.1064 | -0.096131 | 123.056 | 60.9192 | -0.32959 | 123.1064 | -0.096131 | 60.9192 | 122.6761 | 123.056 | -123.2803 | -123.2941
2468.7812 | 123.2025 | -60.9009 | 62.0224 | 0.23247 | -0.005866 | -0.012198 | -0.00078396 | 0.060532 | -0.0037277 | 0.066984 | -61.0428 | 62.0728 | -61.2442 | -61.1526 | 61.8347 | 0.022888 | -0.14648 | 0.14648 | 62.0865 | -61.171 | -0.34332 | 0.050354 | -0.14191 | -0.25177 | -0.18768 | -0.27008 | 0.064087 | 0.20142 | 60.7544 | 61.0474 | 122.7356 | 122.9736 | -0.14191 | 122.9874 | 60.9238 | -0.27008 | 122.9736 | -0.14191 | 60.9238 | 122.7356 | 122.9874 | -123.2666 | -123.1934
2469.7812 | 123.1201 | -60.9238 | 62.0544 | 0.20195 | -0.0033026 | -0.0094207 | 0.0062656 | 0.062028 | 0.00054465 | 0.068906 | -61.0611 | 62.1872 | -61.2442 | -61.4365 | 61.7981 | 0.10986 | -0.004578 | 0.13275 | 62.1277 | -61.235 | -0.32044 | 0.13275 | -0.13733 | -0.5127 | -0.25635 | -0.31128 | 0.073243 | 0.18311 | 60.9192 | 61.0565 | 122.7219 | 123.111 | -0.13733 | 123.0515 | 61.0336 | -0.31128 | 123.111 | -0.13733 | 61.0336 | 122.7219 | 123.0515 | -123.2986 | -123.2895
2470.7812 | 123.2071 | -60.9009 | 62.0087 | 0.20195 | -0.0073614 | -0.011343 | -0.0020658 | 0.060319 | -0.0047957 | 0.068693 | -61.0245 | 62.1048 | -61.2305 | -61.1252 | 61.8301 | 0.022888 | -0.16937 | 0.16937 | 62.0682 | -61.1801 | -0.32959 | 0.09613 | -0.1236 | -0.2243 | -0.17853 | -0.27924 | 0.059509 | 0.20599 | 60.7315 | 61.0703 | 122.731 | 123.0057 | -0.1236 | 122.9691 | 60.9238 | -0.27924 | 123.0057 | -0.1236 | 60.9238 | 122.731 | 122.9691 | -123.2391 | -123.1888
2471.7812 | 123.1018 | -60.9329 | 62.0316 | 0.17143 | -0.0043708 | -0.0085663 | 0.0066928 | 0.061173 | -0.0058639 | 0.067624 | -61.0748 | 62.2009 | -61.235 | -61.1984 | 61.7203 | -0.059509 | 0.004578 | 0.064087 | 62.1414 | -61.2442 | -0.30212 | 0.16937 | -0.14191 | -0.2655 | -0.31128 | -0.31128 | 0.10986 | 0.16022 | 60.9375 | 60.997 | 122.6532 | 123.1338 | -0.14191 | 123.0743 | 60.8734 | -0.31128 | 123.1338 | -0.14191 | 60.8734 | 122.6532 | 123.0743 | -123.2666 | -123.2758
2472.7812 | 123.1522 | -60.9375 | 62.0316 | 0.18669 | -0.0045844 | -0.012839 | 0.0062656 | 0.060532 | -0.0041549 | 0.06677 | -61.0565 | 62.1918 | -61.2305 | -61.2076 | 61.7569 | -0.050354 | -0.027466 | 0.073242 | 62.1414 | -61.2213 | -0.29297 | 0.16022 | -0.11902 | -0.27008 | -0.27466 | -0.28381 | 0.10986 | 0.17395 | 60.91 | 61.0107 | 122.6944 | 123.1293 | -0.11902 | 123.0789 | 60.8871 | -0.28381 | 123.1293 | -0.11902 | 60.8871 | 122.6944 | 123.0789 | -123.262 | -123.2529
2473.7812 | 123.2346 | -60.878 | 62.0316 | 0.064621 | -0.008216 | -0.0096343 | -0.005911 | 0.060319 | -0.0041549 | 0.066556 | -61.0703 | 62.0682 | -61.2076 | -61.116 | 61.853 | 0.07782 | -0.068665 | 0.24719 | 62.1277 | -61.171 | -0.32959 | 0.036621 | -0.19226 | -0.23804 | -0.17853 | -0.29297 | 0.096131 | 0.13733 | 60.8093 | 61.1252 | 122.731 | 122.9462 | -0.19226 | 123.0057 | 60.9558 | -0.29297 | 122.9462 | -0.19226 | 60.9558 | 122.731 | 123.0057 | -123.2391 | -123.2025
2474.7812 | 123.1247 | -60.9329 | 62.0682 | 0.049362 | -0.0045844 | -0.0085663 | 0.0066928 | 0.062028 | -0.0035141 | 0.066129 | -61.0016 | 62.1964 | -61.2076 | -61.1389 | 61.7569 | -0.004578 | 0.013733 | 0.13275 | 62.1506 | -61.203 | -0.27466 | 0.12817 | -0.068665 | -0.20599 | -0.31128 | -0.27008 | 0.082398 | 0.20599 | 60.9467 | 61.0657 | 122.6898 | 123.1293 | -0.068665 | 123.0835 | 60.9283 | -0.27008 | 123.1293 | -0.068665 | 60.9283 | 122.6898 | 123.0835 | -123.2758 | -123.2712
2475.7812 | 123.175 | -60.9009 | 62.0544 | -0.026932 | -0.0054388 | -0.0094207 | 0.0077608 | 0.064164 | -0.0062911 | 0.06677 | -60.9787 | 62.2147 | -61.2122 | -61.1252 | 61.8301 | -0.082397 | 0.041199 | 0.21515 | 62.1506 | -61.2259 | -0.31128 | 0.16022 | -0.07782 | -0.2243 | -0.2243 | -0.32501 | 0.096131 | 0.23346 | 60.9421 | 61.116 | 122.731 | 123.1155 | -0.07782 | 123.0515 | 60.8185 | -0.32501 | 123.1155 | -0.07782 | 60.8185 | 122.731 | 123.0515 | -123.2666 | -123.2803
2476.7812 | 123.1064 | -60.9421 | 62.0636 | 0.095139 | -0.0035162 | -0.0098479 | 0.0066928 | 0.0616 | -0.0045821 | 0.067624 | -61.0565 | 62.2101 | -61.2671 | -61.1755 | 61.7432 | -0.059509 | 0.022888 | 0.054932 | 62.0956 | -61.2442 | -0.32501 | 0.14648 | -0.11444 | -0.23346 | -0.32044 | -0.30212 | 0.032043 | 0.21057 | 60.965 | 60.997 | 122.6852 | 123.1522 | -0.11444 | 123.0377 | 60.8826 | -0.30212 | 123.1522 | -0.11444 | 60.8826 | 122.6852 | 123.0377 | -123.3307 | -123.3078
2477.7812 | 123.111 | -60.9238 | 62.0544 | 0.087509 | -0.0043708 | -0.010275 | 0.0058382 | 0.063309 | -0.0035141 | 0.067838 | -61.0382 | 62.2055 | -61.2396 | -61.1801 | 61.7661 | -0.027466 | 0.027466 | 0.07782 | 62.1368 | -61.2259 | -0.31586 | 0.15106 | -0.11444 | -0.25635 | -0.28839 | -0.30212 | 0.082398 | 0.20142 | 60.9512 | 61.0016 | 122.6898 | 123.1293 | -0.11444 | 123.0606 | 60.8963 | -0.30212 | 123.1293 | -0.11444 | 60.8963 | 122.6898 | 123.0606 | -123.2941 | -123.2803
2478.7969 | 123.1567 | -60.8826 | 62.0499 | -0.0040434 | -0.0039434 | -0.0089935 | 0.00712 | 0.062882 | -0.0047957 | 0.067838 | -61.0016 | 62.2238 | -61.1984 | -61.1298 | 61.8393 | 0.11902 | -0.16022 | 0.14648 | 62.1094 | -61.2488 | -0.31586 | 0.17395 | -0.11902 | -0.24719 | -0.21057 | -0.36621 | 0.059509 | 0.19684 | 60.7224 | 61.0291 | 122.7219 | 123.1064 | -0.11902 | 122.9919 | 61.0016 | -0.36621 | 123.1064 | -0.11902 | 61.0016 | 122.7219 | 122.9919 | -123.2483 | -123.2986
2479.7812 | 123.2025 | -60.8963 | 62.0041 | 0.28587 | -0.0054388 | -0.0083527 | 0.0022066 | 0.063309 | -0.0047957 | 0.070829 | -61.0428 | 62.1506 | -61.2305 | -61.1526 | 61.8256 | 0 | -0.14648 | 0.13733 | 62.1048 | -61.1984 | -0.33417 | 0.14648 | -0.14648 | -0.25635 | -0.17853 | -0.30212 | 0.10071 | 0.18768 | 60.7498 | 61.0336 | 122.7219 | 123.0469 | -0.14648 | 123.0011 | 60.8963 | -0.30212 | 123.0469 | -0.14648 | 60.8963 | 122.7219 | 123.0011 | -123.2346 | -123.2025
2480.7812 | 123.2254 | -60.8826 | 61.9949 | 0.28587 | -0.0062934 | -0.0042937 | 0.0013522 | 0.065446 | -0.0050095 | 0.066556 | -60.9924 | 62.1185 | -61.2167 | -61.116 | 61.853 | 0.041199 | -0.1831 | 0.17853 | 62.0911 | -61.1801 | -0.33417 | 0.1236 | -0.10986 | -0.23346 | -0.14191 | -0.29755 | 0.09613 | 0.2243 | 60.6995 | 61.0611 | 122.7356 | 123.0011 | -0.10986 | 122.9736 | 60.9238 | -0.29755 | 123.0011 | -0.10986 | 60.9238 | 122.7356 | 122.9736 | -123.2117 | -123.175
2481.7812 | 123.2025 | -60.9283 | 62.0132 | 0.28587 | -0.0062934 | -0.0096343 | 0.0030612 | 0.062028 | -0.0013779 | 0.068265 | -61.0519 | 62.1689 | -61.2579 | -61.1481 | 61.7935 | -0.022888 | -0.12817 | 0.1236 | 62.1048 | -61.2259 | -0.32959 | 0.15564 | -0.1236 | -0.21973 | -0.21973 | -0.29755 | 0.091552 | 0.20599 | 60.8002 | 61.0519 | 122.7219 | 123.0972 | -0.1236 | 123.0331 | 60.9055 | -0.29755 | 123.0972 | -0.1236 | 60.9055 | 122.7219 | 123.0331 | -123.2712 | -123.2391
2482.7812 | 123.1979 | -60.8871 | 62.0407 | 0.20958 | -0.0088568 | -0.0087799 | -0.0020658 | 0.06096 | -0.0037277 | 0.067411 | -61.0565 | 62.0773 | -61.235 | -61.1572 | 61.7981 | 0.013733 | -0.12817 | 0.15564 | 62.1002 | -61.1984 | -0.3479 | 0.036622 | -0.16937 | -0.27008 | -0.24261 | -0.31128 | 0.05951 | 0.17853 | 60.759 | 61.0428 | 122.6852 | 122.9645 | -0.16937 | 122.9874 | 60.9009 | -0.31128 | 122.9645 | -0.16937 | 60.9009 | 122.6852 | 122.9874 | -123.2758 | -123.2391
2483.7812 | 123.1567 | -60.91 | 62.0224 | 0.27824 | -0.0077888 | -0.010916 | 0.005411 | 0.060105 | -0.0052231 | 0.066129 | -61.0565 | 62.1643 | -61.235 | -61.1618 | 61.7752 | -0.036621 | -0.10071 | 0.10071 | 62.0819 | -61.2625 | -0.32501 | 0.14191 | -0.14648 | -0.25177 | -0.24719 | -0.35248 | 0.059509 | 0.17853 | 60.8093 | 61.0107 | 122.6852 | 123.0743 | -0.14648 | 122.9919 | 60.8734 | -0.35248 | 123.0743 | -0.14648 | 60.8734 | 122.6852 | 122.9919 | -123.2574 | -123.2849
2484.7812 | 123.1338 | -60.9283 | 62.0636 | 0.049362 | -0.0050116 | -0.010489 | 0.0090426 | 0.060319 | -0.0058639 | 0.068479 | -61.0153 | 62.2055 | -61.2167 | -61.1389 | 61.7889 | 0.004578 | 0.018311 | 0.14191 | 62.114 | -61.2488 | -0.28839 | 0.14191 | -0.086975 | -0.21057 | -0.27466 | -0.32043 | 0.050354 | 0.20142 | 60.9467 | 61.0703 | 122.7173 | 123.1338 | -0.086975 | 123.0423 | 60.9329 | -0.32043 | 123.1338 | -0.086975 | 60.9329 | 122.7173 | 123.0423 | -123.2803 | -123.3124
2485.7812 | 123.0927 | -60.9238 | 62.0499 | 0.087509 | -0.0050116 | -0.012198 | 0.0051974 | 0.063096 | -0.0037277 | 0.064207 | -61.0474 | 62.1872 | -61.2396 | -61.1801 | 61.7569 | -0.054932 | 0.018311 | 0.091553 | 62.146 | -61.2488 | -0.31586 | 0.13733 | -0.1236 | -0.25635 | -0.29297 | -0.32501 | 0.09613 | 0.19226 | 60.9421 | 61.0153 | 122.6807 | 123.111 | -0.1236 | 123.0698 | 60.8688 | -0.32501 | 123.111 | -0.1236 | 60.8688 | 122.6807 | 123.0698 | -123.2895 | -123.2986
2486.7812 | 123.1293 | -60.9146 | 62.0316 | 0.23247 | -0.0033026 | -0.0077117 | 0.0039156 | 0.062882 | -0.0033005 | 0.06912 | -61.0931 | 62.1735 | -61.2488 | -61.203 | 61.7569 | -0.064087 | -0.041199 | 0.068665 | 62.1185 | -61.2259 | -0.33417 | 0.14191 | -0.17853 | -0.28839 | -0.27466 | -0.31128 | 0.086975 | 0.15564 | 60.8734 | 60.9833 | 122.6715 | 123.0881 | -0.17853 | 123.0331 | 60.8505 | -0.31128 | 123.0881 | -0.17853 | 60.8505 | 122.6715 | 123.0331 | -123.2803 | -123.2574
2487.7812 | 123.2025 | -60.9238 | 62.027 | 0.27061 | -0.0033026 | -0.0062163 | 0.0024202 | 0.062241 | -0.0047957 | 0.068265 | -61.0428 | 62.146 | -61.235 | -61.1435 | 61.8073 | -0.013733 | -0.16022 | 0.13275 | 62.0911 | -61.2122 | -0.31128 | 0.11902 | -0.11902 | -0.21973 | -0.21973 | -0.28839 | 0.064086 | 0.19226 | 60.7635 | 61.0565 | 122.731 | 123.0698 | -0.11902 | 123.0148 | 60.91 | -0.28839 | 123.0698 | -0.11902 | 60.91 | 122.731 | 123.0148 | -123.262 | -123.2391
2488.7812 | 123.2254 | -60.8826 | 61.9949 | 0.19432 | -0.0088568 | -0.0094207 | -0.00099756 | 0.061814 | -0.0075729 | 0.067411 | -61.0107 | 62.1002 | -61.2213 | -61.1114 | 61.8393 | 0.045776 | -0.1831 | 0.17395 | 62.1002 | -61.1984 | -0.33875 | 0.10529 | -0.12817 | -0.22888 | -0.15564 | -0.31586 | 0.10529 | 0.21057 | 60.6995 | 61.0565 | 122.7219 | 122.9828 | -0.12817 | 122.9828 | 60.9283 | -0.31586 | 122.9828 | -0.12817 | 60.9283 | 122.7219 | 122.9828 | -123.2162 | -123.1934
2489.7812 | 123.1476 | -60.8917 | 62.0728 | -0.12611 | -0.006507 | -0.012625 | 0.0049838 | 0.062669 | -0.0035141 | 0.065916 | -60.997 | 62.2284 | -61.203 | -61.1252 | 61.8301 | 0.059509 | 0.050354 | 0.21515 | 62.146 | -61.2167 | -0.31128 | 0.15564 | -0.10528 | -0.23346 | -0.24262 | -0.32501 | 0.073242 | 0.20599 | 60.9421 | 61.1069 | 122.7219 | 123.1201 | -0.10528 | 123.0377 | 60.9512 | -0.32501 | 123.1201 | -0.10528 | 60.9512 | 122.7219 | 123.0377 | -123.2758 | -123.2895
2490.7812 | 123.2117 | -60.9009 | 61.9904 | 0.25536 | -0.0045844 | -0.010703 | 0.0017794 | 0.062028 | -0.0043685 | 0.067197 | -61.0291 | 62.1506 | -61.2396 | -61.1114 | 61.8256 | 0.027466 | -0.17395 | 0.16022 | 62.0544 | -61.2305 | -0.33874 | 0.16022 | -0.12817 | -0.21057 | -0.16479 | -0.32959 | 0.064087 | 0.21057 | 60.7269 | 61.0611 | 122.7264 | 123.0515 | -0.12817 | 122.9553 | 60.9283 | -0.32959 | 123.0515 | -0.12817 | 60.9283 | 122.7264 | 122.9553 | -123.23 | -123.2208
2491.7812 | 123.1384 | -60.9146 | 62.0453 | -0.2253 | -0.0054388 | -0.010275 | 0.0049838 | 0.061814 | -0.0045821 | 0.066129 | -61.0016 | 62.2055 | -61.2122 | -61.1298 | 61.8027 | 0.018311 | 0.032043 | 0.16937 | 62.1506 | -61.2305 | -0.29755 | 0.16022 | -0.086975 | -0.21515 | -0.24262 | -0.31586 | 0.10529 | 0.21057 | 60.9467 | 61.084 | 122.7173 | 123.1201 | -0.086975 | 123.0652 | 60.9329 | -0.31586 | 123.1201 | -0.086975 | 60.9329 | 122.7173 | 123.0652 | -123.2574 | -123.2758
2492.7812 | 123.1476 | -60.9009 | 62.0728 | 0.041733 | -0.0069342 | -0.0098479 | 0.0056246 | 0.061814 | -0.0041549 | 0.066556 | -60.997 | 62.2009 | -61.2167 | -61.1023 | 61.8027 | 0.041199 | -0.013733 | 0.1831 | 62.0956 | -61.2259 | -0.31586 | 0.12817 | -0.09613 | -0.20142 | -0.27008 | -0.32501 | 0.022888 | 0.21973 | 60.8871 | 61.084 | 122.7036 | 123.1018 | -0.09613 | 122.9965 | 60.9421 | -0.32501 | 123.1018 | -0.09613 | 60.9421 | 122.7036 | 122.9965 | -123.2895 | -123.2986
2493.7812 | 123.23 | -60.9009 | 62.0087 | -0.13374 | -0.0056524 | -0.0087799 | -0.0012112 | 0.06096 | -0.0056503 | 0.067411 | -60.9879 | 62.0956 | -61.2396 | -61.1298 | 61.8393 | 0.041199 | -0.20142 | 0.1831 | 62.0956 | -61.1847 | -0.33874 | 0.086975 | -0.086975 | -0.22888 | -0.16937 | -0.28381 | 0.086975 | 0.25177 | 60.6995 | 61.084 | 122.7402 | 122.9965 | -0.086975 | 122.9965 | 60.9421 | -0.28381 | 122.9965 | -0.086975 | 60.9421 | 122.7402 | 122.9965 | -123.2483 | -123.1934
2494.7812 | 123.1384 | -60.9421 | 62.059 | 0.18669 | -0.0045844 | -0.0089935 | 0.0058382 | 0.062882 | -0.0065047 | 0.06677 | -61.0611 | 62.1918 | -61.2442 | -61.1984 | 61.7386 | -0.07782 | -0.22888 | -0.24261 | 62.0911 | -61.2534 | -0.30212 | 0.13275 | -0.11902 | -0.25635 | -0.32044 | -0.31128 | 0.032043 | 0.18311 | 60.7132 | 60.6995 | 122.6807 | 123.1338 | -0.11902 | 123.0331 | 60.8643 | -0.31128 | 123.1338 | -0.11902 | 60.8643 | 122.6807 | 123.0331 | -123.3032 | -123.3124
2495.7812 | 123.1338 | -60.9283 | 62.0453 | 0.087509 | -0.004798 | -0.0094207 | 0.0051974 | 0.061387 | -0.0030869 | 0.065702 | -61.0657 | 62.1643 | -61.2488 | -61.1801 | 61.7615 | -0.064087 | -0.041199 | 0.07782 | 62.146 | -61.2396 | -0.32043 | 0.11902 | -0.13733 | -0.25177 | -0.28381 | -0.31128 | 0.10071 | 0.1831 | 60.8871 | 61.0062 | 122.6898 | 123.0927 | -0.13733 | 123.0743 | 60.8643 | -0.31128 | 123.0927 | -0.13733 | 60.8643 | 122.6898 | 123.0743 | -123.2941 | -123.2849
2496.7812 | 123.1888 | -60.9375 | 62.0224 | 0.2935 | -0.0050116 | -0.011343 | 0.001993 | 0.060319 | -0.0043685 | 0.068693 | -61.0565 | 62.1231 | -61.2442 | -61.1618 | 61.7935 | -0.032043 | -0.11444 | 0.10529 | 62.1231 | -61.2396 | -0.3067 | 0.10071 | -0.11902 | -0.2243 | -0.22888 | -0.30212 | 0.10071 | 0.18768 | 60.8231 | 61.0428 | 122.731 | 123.0606 | -0.11902 | 123.0606 | 60.9055 | -0.30212 | 123.0606 | -0.11902 | 60.9055 | 122.731 | 123.0606 | -123.2666 | -123.262
2497.7812 | 123.1567 | -60.9283 | 62.0819 | 0.22484 | -0.0056524 | -0.010703 | 0.0045566 | 0.064164 | -0.0062911 | 0.068265 | -61.0703 | 62.178 | -61.2488 | -61.4365 | 61.647 | 0.068665 | 0.004578 | 0.12817 | 62.146 | -61.2488 | -0.32043 | 0.096131 | -0.14191 | -0.50812 | -0.43488 | -0.32043 | 0.064087 | 0.17853 | 60.9329 | 61.0565 | 122.5754 | 123.1064 | -0.14191 | 123.0743 | 60.997 | -0.32043 | 123.1064 | -0.14191 | 60.997 | 122.5754 | 123.0743 | -123.3307 | -123.3307
2498.7812 | 123.2254 | -60.8551 | 62.0361 | -0.011673 | -0.0077888 | -0.014761 | -0.0050566 | 0.060319 | -0.0039413 | 0.067624 | -61.0565 | 62.1048 | -61.2259 | -61.116 | 61.8759 | 0.10529 | -0.064087 | 0.25635 | 62.0956 | -61.1664 | -0.37079 | 0.068664 | -0.20142 | -0.26093 | -0.16022 | -0.31128 | 0.059509 | 0.16937 | 60.791 | 61.1115 | 122.731 | 122.9599 | -0.20142 | 122.9507 | 60.9604 | -0.31128 | 122.9599 | -0.20142 | 60.9604 | 122.731 | 122.9507 | -123.262 | -123.2025
2499.7812 | 123.1613 | -60.8917 | 62.059 | -0.10323 | -0.0071478 | -0.0083527 | 0.0047702 | 0.057969 | -0.0028731 | 0.067411 | -60.9787 | 62.233 | -61.2076 | -61.1389 | 61.8256 | 0.041199 | 0.045776 | 0.20599 | 62.1323 | -61.2396 | -0.31586 | 0.17395 | -0.086975 | -0.24719 | -0.23346 | -0.3479 | 0.073242 | 0.22888 | 60.9375 | 61.0977 | 122.7173 | 123.1247 | -0.086975 | 123.024 | 60.9329 | -0.3479 | 123.1247 | -0.086975 | 60.9329 | 122.7173 | 123.024 | -123.2666 | -123.2986
2500.7812 | 123.1293 | -60.9146 | 62.059 | 0.049362 | -0.0041572 | -0.012412 | 0.00712 | 0.060532 | -0.0037277 | 0.06677 | -61.0153 | 62.2101 | -61.2396 | -61.1618 | 61.7798 | 0 | 0.018311 | 0.1236 | 62.1048 | -61.2076 | -0.32501 | 0.15106 | -0.10071 | -0.24719 | -0.27924 | -0.29297 | 0.045776 | 0.2243 | 60.9329 | 61.0382 | 122.6944 | 123.1247 | -0.10071 | 123.0194 | 60.9146 | -0.29297 | 123.1247 | -0.10071 | 60.9146 | 122.6944 | 123.0194 | -123.2986 | -123.2666
2501.7812 | 123.1293 | -60.9192 | 62.0865 | 0.064621 | -0.0050116 | -0.0079253 | 0.003702 | 0.060746 | -0.0050095 | 0.065916 | -60.9879 | 62.1964 | -61.2167 | -61.1435 | 61.7844 | 0.018311 | 0.018311 | 0.13733 | 62.1368 | -61.2396 | -0.29755 | 0.10986 | -0.068665 | -0.2243 | -0.30212 | -0.32043 | 0.050354 | 0.22888 | 60.9375 | 61.0565 | 122.7036 | 123.1155 | -0.068665 | 123.056 | 60.9375 | -0.32043 | 123.1155 | -0.068665 | 60.9375 | 122.7036 | 123.056 | -123.3032 | -123.3261
2502.7812 | 123.111 | -60.91 | 62.059 | 0.056992 | -0.0056524 | -0.010062 | 0.0041292 | 0.064378 | -0.0045821 | 0.06677 | -61.0291 | 62.1872 | -61.2488 | -61.1847 | 61.7752 | -0.036621 | 0.027466 | 0.09613 | 62.1414 | -61.2534 | -0.33874 | 0.12817 | -0.11902 | -0.27466 | -0.28381 | -0.34332 | 0.082397 | 0.21973 | 60.9375 | 61.0062 | 122.6852 | 123.0972 | -0.11902 | 123.0515 | 60.8734 | -0.34332 | 123.0972 | -0.11902 | 60.8734 | 122.6852 | 123.0515 | -123.3078 | -123.3124
2503.7812 | 123.2162 | -60.9055 | 62.0132 | 0.27824 | -0.0071478 | -0.01113 | -0.002493 | 0.0616 | -0.0045821 | 0.067838 | -61.0336 | 62.1048 | -61.2213 | -61.1114 | 61.8439 | 0.032043 | -0.17853 | 0.17395 | 62.1094 | -61.1847 | -0.31586 | 0.091552 | -0.12817 | -0.20599 | -0.16937 | -0.27923 | 0.09613 | 0.18768 | 60.7269 | 61.0794 | 122.7493 | 123.0103 | -0.12817 | 123.0148 | 60.9375 | -0.27923 | 123.0103 | -0.12817 | 60.9375 | 122.7493 | 123.0148 | -123.2346 | -123.1979
2504.7812 | 123.1338 | -60.9192 | 62.0865 | 0.20958 | -0.0054388 | -0.0094207 | 0.005411 | 0.059251 | -0.0060775 | 0.068479 | -61.084 | 62.1826 | -61.2442 | -61.1343 | 61.7798 | -0.068665 | 0.045776 | 0.086975 | 62.1506 | -61.2396 | -0.32501 | 0.09613 | -0.16479 | -0.21515 | -0.3067 | -0.32043 | 0.064087 | 0.16022 | 60.965 | 61.0062 | 122.699 | 123.1018 | -0.16479 | 123.0698 | 60.8505 | -0.32043 | 123.1018 | -0.16479 | 60.8505 | 122.699 | 123.0698 | -123.3307 | -123.3261
2505.7812 | 123.0972 | -60.9238 | 62.0544 | 0.049362 | -0.0052252 | -0.0094207 | 0.0081882 | 0.062028 | -0.0088547 | 0.068906 | -61.0336 | 62.2101 | -61.2259 | -61.1893 | 61.7569 | -0.045776 | 0.022888 | 0.086975 | 62.1368 | -61.2442 | -0.30212 | 0.15564 | -0.10986 | -0.2655 | -0.29755 | -0.32044 | 0.082398 | 0.19226 | 60.9467 | 61.0107 | 122.6807 | 123.1338 | -0.10986 | 123.0606 | 60.878 | -0.32044 | 123.1338 | -0.10986 | 60.878 | 122.6807 | 123.0606 | -123.2803 | -123.2986
2506.7812 | 123.1201 | -60.9192 | 62.0728 | 0.095139 | -0.0056524 | -0.0094207 | 0.0058382 | 0.062241 | -0.0039413 | 0.068265 | -61.0428 | 62.2009 | -61.2442 | -61.1755 | 61.7798 | -0.018311 | 0.022888 | 0.11902 | 62.146 | -61.2167 | -0.32501 | 0.12817 | -0.1236 | -0.25635 | -0.29297 | -0.29755 | 0.073242 | 0.20142 | 60.9421 | 61.0382 | 122.699 | 123.1201 | -0.1236 | 123.0652 | 60.9009 | -0.29755 | 123.1201 | -0.1236 | 60.9009 | 122.699 | 123.0652 | -123.317 | -123.2895
2507.7812 | 123.1613 | -60.9192 | 62.0636 | -0.11085 | -0.0060798 | -0.015189 | 0.004343 | 0.061173 | -0.0056503 | 0.065916 | -61.0016 | 62.2147 | -61.2259 | -61.1252 | 61.8393 | 0.073242 | 0.07782 | 0.20142 | 62.1872 | -61.2076 | -0.3067 | 0.15106 | -0.082398 | -0.20599 | -0.22431 | -0.28839 | 0.1236 | 0.2243 | 60.997 | 61.1206 | 122.7585 | 123.1338 | -0.082398 | 123.1064 | 60.9924 | -0.28839 | 123.1338 | -0.082398 | 60.9924 | 122.7585 | 123.1064 | -123.2895 | -123.2712
2508.7812 | 123.111 | -60.9375 | 62.0453 | 0.07988 | -0.0037298 | -0.0081389 | 0.0032748 | 0.0663 | -0.0030869 | 0.068265 | -61.0519 | 62.1872 | -61.2671 | -61.1801 | 61.7477 | -0.059509 | 0.041199 | 0.068665 | 62.1368 | -61.2305 | -0.32959 | 0.14191 | -0.11444 | -0.24262 | -0.29755 | -0.29297 | 0.091553 | 0.21515 | 60.9787 | 61.0062 | 122.6852 | 123.1247 | -0.11444 | 123.0743 | 60.878 | -0.29297 | 123.1247 | -0.11444 | 60.878 | 122.6852 | 123.0743 | -123.3124 | -123.2758
2509.7812 | 123.1842 | -60.9146 | 62.0682 | -0.057449 | -0.0060798 | -0.010489 | 0.0034884 | 0.064164 | -0.0041549 | 0.066984 | -61.0199 | 62.1964 | -61.2122 | -61.1114 | 61.821 | 0.059509 | 0.041199 | 0.20599 | 62.1872 | -61.2259 | -0.29755 | 0.12817 | -0.10529 | -0.19684 | -0.24719 | -0.31128 | 0.11902 | 0.19226 | 60.9558 | 61.1206 | 122.7356 | 123.111 | -0.10529 | 123.1018 | 60.9741 | -0.31128 | 123.111 | -0.10529 | 60.9741 | 122.7356 | 123.1018 | -123.2803 | -123.2941
2510.7812 | 123.1567 | -60.8963 | 62.0544 | -0.33974 | -0.0069342 | -0.011984 | 0.0062656 | 0.063096 | -0.0052231 | 0.067838 | -60.9879 | 62.2009 | -61.2442 | -61.1298 | 61.8118 | 0.045776 | 0.027466 | 0.17395 | 62.1323 | -61.2305 | -0.3479 | 0.14648 | -0.091553 | -0.23346 | -0.24261 | -0.33417 | 0.07782 | 0.25635 | 60.9238 | 61.0703 | 122.7081 | 123.0972 | -0.091553 | 123.0286 | 60.9421 | -0.33417 | 123.0972 | -0.091553 | 60.9421 | 122.7081 | 123.0286 | -123.2986 | -123.2849
2511.7812 | 123.111 | -60.8917 | 62.0453 | 0.1104 | -0.0035162 | -0.01113 | 0.0041292 | 0.063737 | -0.0086411 | 0.066343 | -61.0199 | 62.2009 | -61.235 | -61.171 | 61.7935 | 0 | 0.018311 | 0.11902 | 62.1735 | -61.2442 | -0.34332 | 0.15564 | -0.12817 | -0.27923 | -0.25177 | -0.35248 | 0.12817 | 0.21515 | 60.91 | 61.0107 | 122.6852 | 123.0927 | -0.12817 | 123.0652 | 60.8917 | -0.35248 | 123.0927 | -0.12817 | 60.8917 | 122.6852 | 123.0652 | -123.2803 | -123.2895
2512.7812 | 123.1155 | -60.9238 | 62.0728 | 0.13329 | -0.0026618 | -0.0077117 | 0.0056246 | 0.063096 | -0.0052231 | 0.069547 | -61.0748 | 62.2101 | -61.235 | -61.2122 | 61.7477 | -0.045776 | 0.045776 | 0.064087 | 62.1368 | -61.235 | -0.31128 | 0.13733 | -0.15106 | -0.28839 | -0.32501 | -0.31128 | 0.064087 | 0.16022 | 60.9695 | 60.9879 | 122.6715 | 123.1338 | -0.15106 | 123.0606 | 60.878 | -0.31128 | 123.1338 | -0.15106 | 60.878 | 122.6715 | 123.0606 | -123.3078 | -123.3078
2513.7812 | 122.9782 | -60.9375 | 61.9949 | 0.17143 | -0.005866 | -0.0092071 | 0.0034884 | 0.064164 | -0.0039413 | 0.066343 | -61.1069 | 62.1689 | -61.2625 | -61.2259 | 61.7386 | -0.059509 | -0.013733 | 0.064087 | 62.1552 | -61.2534 | -0.32501 | 0.17395 | -0.16937 | -0.28839 | -0.25635 | -0.31586 | 0.16022 | 0.15564 | 60.9238 | 61.0016 | 122.6761 | 123.1064 | -0.16937 | 123.0927 | 60.878 | -0.31586 | 123.1064 | -0.16937 | 60.878 | 122.6761 | 123.0927 | -123.2574 | -123.2483
2514.7812 | 123.1293 | -60.9329 | 62.0499 | 0.15617 | -0.0043708 | -0.013907 | 0.0034884 | 0.0616 | -0.0058639 | 0.067838 | -61.0886 | 62.2055 | -61.2579 | -61.2122 | 61.7615 | -0.059509 | -0.022888 | 0.050354 | 62.1277 | -61.2579 | -0.32501 | 0.15564 | -0.15564 | -0.27924 | -0.28839 | -0.32501 | 0.07782 | 0.16937 | 60.91 | 60.9833 | 122.6944 | 123.1384 | -0.15564 | 123.0606 | 60.8734 | -0.32501 | 123.1384 | -0.15564 | 60.8734 | 122.6944 | 123.0606 | -123.3078 | -123.3078
2515.7812 | 123.1247 | -60.91 | 62.0773 | -0.072708 | -0.0084296 | -0.0077117 | 0.00028404 | 0.061814 | -0.0067185 | 0.067197 | -61.0611 | 62.2055 | -61.203 | -61.1664 | 61.8073 | 0.054932 | 0.11902 | 0.20599 | 62.1826 | -61.2259 | -0.29297 | 0.12817 | -0.15106 | -0.25635 | -0.27008 | -0.31586 | 0.10529 | 0.14191 | 61.0291 | 61.116 | 122.7173 | 123.1155 | -0.15106 | 123.0927 | 60.965 | -0.31586 | 123.1155 | -0.15106 | 60.965 | 122.7173 | 123.0927 | -123.2803 | -123.3032
2516.7812 | 123.1155 | -60.9055 | 62.0865 | -0.057449 | -0.0054388 | -0.0087799 | 0.00028404 | 0.061173 | -0.0043685 | 0.065702 | -61.0703 | 62.1735 | -61.2488 | -61.1801 | 61.7935 | 0.036621 | 0.14648 | 0.20142 | 62.1552 | -61.2122 | -0.34332 | 0.086975 | -0.16479 | -0.27466 | -0.29297 | -0.3067 | 0.068664 | 0.17853 | 61.0519 | 61.1069 | 122.699 | 123.0789 | -0.16479 | 123.0606 | 60.9421 | -0.3067 | 123.0789 | -0.16479 | 60.9421 | 122.699 | 123.0606 | -123.3353 | -123.2986
2517.7812 | 123.1384 | -60.9283 | 62.0819 | -0.17189 | -0.005866 | -0.010916 | 0.0051974 | 0.062241 | -0.0054367 | 0.06677 | -61.0336 | 62.2284 | -61.2305 | -61.1343 | 61.8027 | 0.068665 | 0.10071 | 0.20142 | 62.1735 | -61.2122 | -0.30212 | 0.14648 | -0.10529 | -0.20599 | -0.27924 | -0.28381 | 0.091553 | 0.19684 | 61.0291 | 61.1298 | 122.731 | 123.1567 | -0.10529 | 123.1018 | 60.997 | -0.28381 | 123.1567 | -0.10529 | 60.997 | 122.731 | 123.1018 | -123.3124 | -123.2941
2518.7812 | 123.0927 | -60.9283 | 62.0636 | 0.095139 | -0.0056524 | -0.0089935 | 0.0028476 | 0.063309 | -0.0035141 | 0.066984 | -61.0657 | 62.2147 | -61.2396 | -61.2122 | 61.7432 | -0.07782 | -0.009155 | 0.07782 | 62.1185 | -61.235 | -0.31128 | 0.15106 | -0.13733 | -0.28381 | -0.32044 | -0.3067 | 0.054931 | 0.17395 | 60.9192 | 61.0062 | 122.6715 | 123.143 | -0.13733 | 123.0469 | 60.8505 | -0.3067 | 123.143 | -0.13733 | 60.8505 | 122.6715 | 123.0469 | -123.3032 | -123.2986
2519.7812 | 123.1476 | -60.8963 | 62.0773 | -0.11085 | -0.0086432 | -0.0098479 | 0.0051974 | 0.060532 | -0.0035141 | 0.065275 | -61.0062 | 62.233 | -61.2122 | -61.1206 | 61.8118 | 0.073242 | 0.07782 | 0.21057 | 62.1643 | -61.2442 | -0.31586 | 0.15564 | -0.10986 | -0.2243 | -0.2655 | -0.3479 | 0.086975 | 0.20599 | 60.9741 | 61.1069 | 122.7081 | 123.1293 | -0.10986 | 123.0606 | 60.9695 | -0.3479 | 123.1293 | -0.10986 | 60.9695 | 122.7081 | 123.0606 | -123.2895 | -123.3215
2520.7812 | 123.1201 | -60.9192 | 62.0636 | 0.011215 | -0.0060798 | -0.010275 | 0.0047702 | 0.0616 | -0.0056503 | 0.068265 | -61.0153 | 62.1872 | -61.2167 | -61.1435 | 61.7889 | 0.018311 | 0.032043 | 0.13275 | 62.1506 | -61.235 | -0.29755 | 0.1236 | -0.096131 | -0.2243 | -0.27466 | -0.31586 | 0.086975 | 0.20142 | 60.9512 | 61.0519 | 122.7081 | 123.1064 | -0.096131 | 123.0698 | 60.9375 | -0.31586 | 123.1064 | -0.096131 | 60.9375 | 122.7081 | 123.0698 | -123.2803 | -123.2986
2521.7812 | 123.1659 | -60.9192 | 62.059 | -0.04219 | -0.0039434 | -0.0094207 | 0.005411 | 0.064164 | -0.0043685 | 0.066129 | -60.997 | 62.2192 | -61.2488 | -61.1252 | 61.8027 | 0.036621 | 0.022888 | 0.16937 | 62.1689 | -61.2305 | -0.32959 | 0.16022 | -0.07782 | -0.20599 | -0.25635 | -0.31128 | 0.10986 | 0.25177 | 60.9421 | 61.0886 | 122.7219 | 123.1384 | -0.07782 | 123.0881 | 60.9558 | -0.31128 | 123.1384 | -0.07782 | 60.9558 | 122.7219 | 123.0881 | -123.3078 | -123.2895
2522.7812 | 123.1384 | -60.8963 | 62.0773 | -0.034561 | -0.0033026 | -0.010703 | 0.0045566 | 0.062241 | -0.0054367 | 0.066984 | -60.9924 | 62.178 | -61.2122 | -61.1343 | 61.8164 | 0.054932 | 0.009155 | 0.1831 | 62.1552 | -61.2122 | -0.31586 | 0.10071 | -0.096131 | -0.23804 | -0.26093 | -0.31586 | 0.077819 | 0.21973 | 60.9055 | 61.0794 | 122.7127 | 123.0743 | -0.096131 | 123.0515 | 60.9512 | -0.31586 | 123.0743 | -0.096131 | 60.9512 | 122.7127 | 123.0515 | -123.2895 | -123.2895
2523.7812 | 123.1659 | -60.9192 | 62.0499 | -0.034561 | -0.0035162 | -0.0083527 | 0.0039156 | 0.067795 | -0.0060775 | 0.063779 | -60.9924 | 62.2055 | -61.2259 | -61.1069 | 61.8073 | 0.068665 | 0.009155 | 0.17853 | 62.178 | -61.2305 | -0.3067 | 0.15564 | -0.073243 | -0.18768 | -0.24262 | -0.31128 | 0.12817 | 0.23346 | 60.9283 | 61.0977 | 122.7264 | 123.1247 | -0.073243 | 123.0972 | 60.9879 | -0.31128 | 123.1247 | -0.073243 | 60.9879 | 122.7264 | 123.0972 | -123.2758 | -123.2803
2524.7812 | 123.1476 | -60.878 | 62.0865 | -0.19478 | -0.0080024 | -0.011343 | -0.0012112 | 0.061173 | -0.0050095 | 0.068693 | -61.0382 | 62.146 | -61.2305 | -61.1298 | 61.8347 | 0.10529 | 0.091553 | 0.25635 | 62.146 | -61.1755 | -0.35248 | 0.059509 | -0.16022 | -0.25177 | -0.25177 | -0.29755 | 0.059509 | 0.19226 | 60.9695 | 61.1343 | 122.7127 | 123.024 | -0.16022 | 123.024 | 60.9833 | -0.29755 | 123.024 | -0.16022 | 60.9833 | 122.7127 | 123.024 | -123.317 | -123.262
2525.7812 | 123.1247 | -60.9055 | 62.0773 | 0.064621 | -0.0080024 | -0.0098479 | 0.00071144 | 0.059464 | -0.0043685 | 0.067197 | -61.0519 | 62.2147 | -61.2396 | -61.1847 | 61.7889 | 0.036621 | 0.15106 | 0.20142 | 62.1506 | -61.2076 | -0.33417 | 0.13733 | -0.14648 | -0.27923 | -0.28839 | -0.30212 | 0.073242 | 0.18768 | 61.0565 | 61.1069 | 122.6944 | 123.1201 | -0.14648 | 123.056 | 60.9421 | -0.30212 | 123.1201 | -0.14648 | 60.9421 | 122.6944 | 123.056 | -123.317 | -123.2849
2526.7812 | 123.143 | -60.91 | 62.0819 | -0.16426 | -0.0086432 | -0.015402 | 0.0060518 | 0.059464 | -0.0028731 | 0.066343 | -61.0474 | 62.1872 | -61.2076 | -61.171 | 61.7798 | 0.036621 | 0.14191 | 0.19684 | 62.1643 | -61.2213 | -0.29755 | 0.10529 | -0.13733 | -0.26093 | -0.30212 | -0.31128 | 0.082398 | 0.16022 | 61.0519 | 61.1069 | 122.6898 | 123.0972 | -0.13733 | 123.0743 | 60.9467 | -0.31128 | 123.0972 | -0.13733 | 60.9467 | 122.6898 | 123.0743 | -123.2895 | -123.3032
2527.7812 | 123.1567 | -60.9192 | 62.0682 | -0.087967 | -0.0060798 | -0.0092071 | 0.0032748 | 0.062241 | -0.0065047 | 0.067411 | -60.9833 | 62.1964 | -61.2259 | -61.0519 | 61.8393 | 0.032043 | 0.050354 | 0.21973 | 62.1964 | -61.2122 | -0.3067 | 0.12817 | -0.064087 | -0.13275 | -0.22888 | -0.29297 | 0.12817 | 0.24262 | 60.9695 | 61.1389 | 122.7585 | 123.1155 | -0.064087 | 123.1155 | 60.9512 | -0.29297 | 123.1155 | -0.064087 | 60.9512 | 122.7585 | 123.1155 | -123.2941 | -123.2803
2528.7812 | 123.1705 | -60.9192 | 62.0544 | -0.30159 | -0.005866 | -0.0094207 | 0.0034884 | 0.060319 | -0.0056503 | 0.065061 | -60.9787 | 62.1918 | -61.2488 | -61.1206 | 61.8164 | 0.050354 | 0.041199 | 0.21515 | 62.1872 | -61.1893 | -0.32959 | 0.13733 | -0.05951 | -0.20142 | -0.23804 | -0.27008 | 0.13275 | 0.27008 | 60.9604 | 61.1343 | 122.7356 | 123.111 | -0.05951 | 123.1064 | 60.9695 | -0.27008 | 123.111 | -0.05951 | 60.9695 | 122.7356 | 123.1064 | -123.3032 | -123.2437
2529.7812 | 123.143 | -60.91 | 62.0911 | -0.149 | -0.0069342 | -0.01113 | -0.001425 | 0.058823 | -0.0030869 | 0.067838 | -61.0611 | 62.1826 | -61.203 | -61.1618 | 61.8027 | 0.036621 | 0.15564 | 0.21057 | 62.1918 | -61.1984 | -0.29297 | 0.091553 | -0.15106 | -0.25177 | -0.28839 | -0.28839 | 0.10071 | 0.14191 | 61.0657 | 61.1206 | 122.7127 | 123.0927 | -0.15106 | 123.1018 | 60.9467 | -0.28839 | 123.0927 | -0.15106 | 60.9467 | 122.7127 | 123.1018 | -123.2941 | -123.2895
2530.7812 | 123.1201 | -60.9421 | 62.0407 | 0.14854 | -0.0045844 | -0.0066437 | 0.0077608 | 0.061173 | -0.0043685 | 0.066129 | -61.0428 | 62.2009 | -61.2259 | -61.1755 | 61.7477 | -0.032043 | 0.041199 | 0.091553 | 62.1277 | -61.2488 | -0.28381 | 0.16022 | -0.10071 | -0.23346 | -0.29297 | -0.3067 | 0.086976 | 0.1831 | 60.9833 | 61.0336 | 122.6898 | 123.143 | -0.10071 | 123.0698 | 60.91 | -0.3067 | 123.143 | -0.10071 | 60.91 | 122.6898 | 123.0698 | -123.2666 | -123.2895
2531.7812 | 123.1522 | -60.9055 | 62.0819 | -0.095596 | -0.0067206 | -0.011984 | 0.0032748 | 0.061814 | -0.0028731 | 0.069547 | -61.0336 | 62.2238 | -61.1984 | -61.2442 | 61.734 | 0.045776 | 0.11902 | 0.27924 | 62.1918 | -61.1984 | -0.29297 | 0.14191 | -0.12817 | -0.33875 | -0.3479 | -0.29297 | 0.10986 | 0.16479 | 61.0245 | 61.1847 | 122.6395 | 123.1293 | -0.12817 | 123.0972 | 60.9512 | -0.29297 | 123.1293 | -0.12817 | 60.9512 | 122.6395 | 123.0972 | -123.2803 | -123.2803
2532.7812 | 123.2391 | -60.8734 | 62.0224 | -0.011673 | -0.0090704 | -0.017111 | -0.0069792 | 0.060105 | -0.0043685 | 0.067411 | -61.0336 | 62.1185 | -61.1984 | -61.0886 | 61.8851 | 0.10529 | -0.068665 | 0.2655 | 62.114 | -61.171 | -0.32501 | 0.09613 | -0.16022 | -0.21515 | -0.13733 | -0.29755 | 0.091553 | 0.16479 | 60.8047 | 61.1389 | 122.7585 | 122.9919 | -0.16022 | 122.9874 | 60.9787 | -0.29755 | 122.9919 | -0.16022 | 60.9787 | 122.7585 | 122.9874 | -123.2208 | -123.1934
2533.7812 | 123.1659 | -60.9055 | 62.0911 | -0.0040434 | -0.0073614 | -0.0079253 | 0.0069064 | 0.061173 | -0.0058639 | 0.067624 | -60.9924 | 62.2101 | -61.1984 | -61.1206 | 61.6379 | -0.15106 | 0.082397 | 0.2243 | 62.1277 | -61.2442 | -0.29297 | 0.11902 | -0.086975 | -0.21515 | -0.45319 | -0.33875 | 0.036622 | 0.20599 | 60.9879 | 61.1298 | 122.5433 | 123.1155 | -0.086975 | 123.0331 | 60.7544 | -0.33875 | 123.1155 | -0.086975 | 60.7544 | 122.5433 | 123.0331 | -123.2895 | -123.3353
2534.7812 | 123.1201 | -60.9055 | 62.0865 | -0.17189 | -0.0069342 | -0.010062 | 0.0032748 | 0.060746 | -0.0043685 | 0.066129 | -61.0703 | 62.2147 | -61.2076 | -61.1572 | 61.7844 | 0.054932 | 0.13733 | 0.19226 | 62.1414 | -61.2442 | -0.30212 | 0.12817 | -0.16479 | -0.25177 | -0.30212 | -0.33875 | 0.054931 | 0.13733 | 61.0428 | 61.0977 | 122.6898 | 123.1201 | -0.16479 | 123.0469 | 60.9604 | -0.33875 | 123.1201 | -0.16479 | 60.9604 | 122.6898 | 123.0469 | -123.2941 | -123.3307
2535.7812 | 123.2254 | -60.8414 | 62.0499 | -0.15663 | -0.010352 | -0.01583 | -0.0035612 | 0.059037 | -0.0073593 | 0.067838 | -60.997 | 62.1323 | -61.203 | -61.0565 | 61.9034 | 0.13733 | -0.041199 | 0.32501 | 62.1094 | -61.1481 | -0.36163 | 0.082397 | -0.15564 | -0.21515 | -0.14648 | -0.3067 | 0.059509 | 0.20599 | 60.8002 | 61.1664 | 122.7448 | 122.9736 | -0.15564 | 122.9507 | 60.9787 | -0.3067 | 122.9736 | -0.15564 | 60.9787 | 122.7448 | 122.9507 | -123.2529 | -123.1979
2536.7812 | 123.1979 | -60.8688 | 62.0682 | -0.11085 | -0.0097114 | -0.014975 | -0.0027066 | 0.056046 | -0.0030869 | 0.065916 | -60.9924 | 62.1048 | -61.1893 | -61.084 | 61.8759 | 0.11902 | 0.036621 | 0.28839 | 62.1094 | -61.1755 | -0.32044 | 0.036621 | -0.1236 | -0.21515 | -0.19226 | -0.3067 | 0.041199 | 0.19684 | 60.9055 | 61.1572 | 122.7448 | 122.9736 | -0.1236 | 122.9782 | 60.9879 | -0.3067 | 122.9736 | -0.1236 | 60.9879 | 122.7448 | 122.9782 | -123.2574 | -123.2437
2537.7812 | 123.111 | -60.8826 | 62.1094 | -0.18715 | -0.008216 | -0.0081389 | 0.0034884 | 0.058396 | -0.0052231 | 0.068052 | -61.0199 | 62.1323 | -61.203 | -61.1343 | 61.8164 | 0.045776 | 0.091553 | 0.25635 | 62.1414 | -61.1938 | -0.32044 | 0.022888 | -0.13733 | -0.25177 | -0.29297 | -0.31128 | 0.032043 | 0.18311 | 60.9741 | 61.1389 | 122.699 | 123.0148 | -0.13733 | 123.024 | 60.9283 | -0.31128 | 123.0148 | -0.13733 | 60.9283 | 122.699 | 123.024 | -123.3124 | -123.3032
2538.7812 | 123.175 | -60.8963 | 62.0316 | 0.095139 | -0.0080024 | -0.012198 | -0.0016386 | 0.057328 | -0.0039413 | 0.067838 | -61.0703 | 62.0911 | -61.2122 | -61.1481 | 62.0132 | 0.15564 | -0.1831 | 0.16022 | 62.114 | -61.171 | -0.31586 | 0.059509 | -0.17395 | -0.25177 | -0.01831 | -0.27466 | 0.082398 | 0.14191 | 60.7132 | 61.0565 | 122.9095 | 122.9874 | -0.17395 | 123.0103 | 61.0519 | -0.27466 | 122.9874 | -0.17395 | 61.0519 | 122.9095 | 123.0103 | -123.2437 | -123.2025
2539.7812 | 123.2117 | -60.8688 | 62.059 | -0.56099 | -0.0088568 | -0.01113 | 0.00028404 | 0.056046 | -0.0047957 | 0.066984 | -61.0062 | 62.0728 | -61.1801 | -61.0565 | 61.8896 | 0.12817 | -0.050354 | 0.30212 | 62.1094 | -61.1847 | -0.31128 | 0.013733 | -0.13733 | -0.18768 | -0.16937 | -0.31586 | 0.050354 | 0.17395 | 60.8185 | 61.171 | 122.7585 | 122.9416 | -0.13733 | 122.9782 | 60.997 | -0.31586 | 122.9416 | -0.13733 | 60.997 | 122.7585 | 122.9782 | -123.2391 | -123.2437
2540.7812 | 123.2025 | -60.8963 | 62.0544 | -0.14137 | -0.008216 | -0.011557 | 0.0047702 | 0.057328 | -0.0084273 | 0.064207 | -60.9924 | 62.114 | -61.1984 | -61.0748 | 61.8622 | 0.11902 | 0.013733 | 0.29755 | 62.1185 | -61.1938 | -0.30212 | 0.05951 | -0.096131 | -0.17853 | -0.19226 | -0.29755 | 0.064087 | 0.20599 | 60.91 | 61.1938 | 122.7585 | 123.0103 | -0.096131 | 123.0148 | 61.0153 | -0.29755 | 123.0103 | -0.096131 | 61.0153 | 122.7585 | 123.0148 | -123.2529 | -123.2483
2541.7812 | 123.0743 | -60.9283 | 62.0224 | 0.14854 | -0.0037298 | -0.0096343 | 0.0086154 | 0.059251 | -0.0069321 | 0.066129 | -61.0611 | 62.1964 | -61.203 | -61.1984 | 61.7157 | -0.086975 | -0.004578 | 0.050354 | 62.1368 | -61.2762 | -0.27466 | 0.17395 | -0.13275 | -0.27008 | -0.3067 | -0.3479 | 0.11444 | 0.14191 | 60.9238 | 60.9787 | 122.644 | 123.1247 | -0.13275 | 123.0652 | 60.8414 | -0.3479 | 123.1247 | -0.13275 | 60.8414 | 122.644 | 123.0652 | -123.2254 | -123.2986
2542.7812 | 123.1338 | -60.9192 | 62.0865 | -0.17189 | -0.007575 | -0.010489 | 0.0030612 | 0.059464 | -0.0077865 | 0.066556 | -61.0519 | 62.178 | -61.2167 | -61.1664 | 61.8027 | 0.022888 | 0.13733 | 0.20142 | 62.2009 | -61.1893 | -0.29755 | 0.091553 | -0.13275 | -0.24719 | -0.28381 | -0.27008 | 0.11444 | 0.16479 | 61.0565 | 61.1206 | 122.7219 | 123.0972 | -0.13275 | 123.1201 | 60.9421 | -0.27008 | 123.0972 | -0.13275 | 60.9421 | 122.7219 | 123.1201 | -123.3032 | -123.2758
2543.7812 | 123.111 | -60.9146 | 62.0728 | -0.15663 | -0.0052252 | -0.01348 | 0.0034884 | 0.061814 | -0.0067185 | 0.066343 | -61.0474 | 62.2055 | -61.2396 | -61.0794 | 61.7569 | 0.004578 | 0.064087 | 0.16937 | 62.146 | -61.2305 | -0.32501 | 0.13275 | -0.13275 | -0.1648 | -0.31586 | -0.31586 | 0.073242 | 0.19226 | 60.9787 | 61.084 | 122.6715 | 123.1201 | -0.13275 | 123.0606 | 60.9192 | -0.31586 | 123.1201 | -0.13275 | 60.9192 | 122.6715 | 123.0606 | -123.3124 | -123.3032
2544.7812 | 123.2391 | -60.8597 | 62.0453 | -0.12611 | -0.0088568 | -0.01348 | -0.0012112 | 0.06096 | -0.0069321 | 0.067197 | -61.0016 | 62.0956 | -61.1801 | -61.0428 | 61.8988 | 0.14191 | -0.041199 | 0.31586 | 62.114 | -61.1618 | -0.32044 | 0.050354 | -0.14191 | -0.18311 | -0.14648 | -0.30212 | 0.068665 | 0.17853 | 60.8185 | 61.1755 | 122.7585 | 122.9553 | -0.14191 | 122.9736 | 61.0016 | -0.30212 | 122.9553 | -0.14191 | 61.0016 | 122.7585 | 122.9736 | -123.2254 | -123.2071
2545.7812 | 123.2117 | -60.8688 | 62.059 | -0.17189 | -0.0088568 | -0.011984 | -0.0027066 | 0.05861 | -0.0028731 | 0.06677 | -61.0107 | 62.0865 | -61.1984 | -61.1069 | 61.8622 | 0.091553 | 0.009155 | 0.25635 | 62.1094 | -61.1755 | -0.32959 | 0.027466 | -0.14191 | -0.23804 | -0.19684 | -0.3067 | 0.050354 | 0.18768 | 60.878 | 61.1252 | 122.731 | 122.9553 | -0.14191 | 122.9782 | 60.9604 | -0.3067 | 122.9553 | -0.14191 | 60.9604 | 122.731 | 122.9782 | -123.2574 | -123.2346
2546.7812 | 123.1888 | -60.9146 | 62.0499 | 0.47661 | -0.0054388 | -0.0049347 | 0.0058382 | 0.061173 | -0.0045821 | 0.067838 | -61.0062 | 62.146 | -61.2167 | -61.1618 | 61.7798 | -0.032043 | -0.13275 | 0.10986 | 62.1002 | -61.2442 | -0.30212 | 0.09613 | -0.091553 | -0.24719 | -0.27008 | -0.32959 | 0.050354 | 0.21057 | 60.7819 | 61.0245 | 122.6944 | 123.0606 | -0.091553 | 123.0148 | 60.8826 | -0.32959 | 123.0606 | -0.091553 | 60.8826 | 122.6944 | 123.0148 | -123.2666 | -123.2941
2547.7812 | 123.1613 | -60.9146 | 62.0544 | 0.13329 | -0.0071478 | -0.014334 | 0.0022066 | 0.057969 | -0.0037277 | 0.067838 | -61.0245 | 62.1414 | -61.203 | -61.1069 | 61.8439 | 0.086975 | 0.082397 | 0.23346 | 62.1597 | -61.1801 | -0.28839 | 0.086975 | -0.10986 | -0.19226 | -0.21057 | -0.2655 | 0.10529 | 0.17853 | 60.997 | 61.1481 | 122.7585 | 123.056 | -0.10986 | 123.0743 | 61.0016 | -0.2655 | 123.056 | -0.10986 | 61.0016 | 122.7585 | 123.0743 | -123.2574 | -123.2346
2548.7812 | 123.1522 | -60.8871 | 62.0911 | -0.04982 | -0.0043708 | -0.012198 | 0.0084018 | 0.060532 | -0.0056503 | 0.065275 | -60.9879 | 62.2009 | -61.2259 | -61.0748 | 61.821 | 0.054932 | 0.004578 | 0.21057 | 62.1506 | -61.1984 | -0.33874 | 0.10986 | -0.10071 | -0.18768 | -0.27008 | -0.31128 | 0.05951 | 0.23804 | 60.8917 | 61.0977 | 122.7081 | 123.0881 | -0.10071 | 123.0377 | 60.9421 | -0.31128 | 123.0881 | -0.10071 | 60.9421 | 122.7081 | 123.0377 | -123.317 | -123.2895
2549.7812 | 123.1659 | -60.8597 | 62.0682 | -0.17189 | -0.0060798 | -0.013266 | -0.001425 | 0.059037 | -0.0067185 | 0.067411 | -61.0016 | 62.1277 | -61.2213 | -61.0794 | 61.8668 | 0.11444 | 0.032043 | 0.28839 | 62.1368 | -61.1343 | -0.36163 | 0.05951 | -0.14191 | -0.21973 | -0.20142 | -0.27466 | 0.068665 | 0.21973 | 60.8917 | 61.1481 | 122.7264 | 122.9874 | -0.14191 | 122.9965 | 60.9741 | -0.27466 | 122.9874 | -0.14191 | 60.9741 | 122.7264 | 122.9965 | -123.2895 | -123.2025
2550.7812 | 123.1201 | -60.8963 | 62.0819 | -0.23293 | -0.008216 | -0.0094207 | 0.003702 | 0.060746 | -0.0069321 | 0.064634 | -61.0336 | 62.1506 | -61.2442 | -61.1206 | 61.8256 | 0.073242 | 0.13275 | 0.20599 | 62.178 | -61.1801 | -0.3479 | 0.068665 | -0.13733 | -0.2243 | -0.25635 | -0.28381 | 0.096131 | 0.21057 | 61.0291 | 61.1023 | 122.7219 | 123.0469 | -0.13733 | 123.0743 | 60.9695 | -0.28381 | 123.0469 | -0.13733 | 60.9695 | 122.7219 | 123.0743 | -123.3261 | -123.262
2551.7812 | 123.0835 | -60.9467 | 62.0682 | 0.072251 | -0.0037298 | -0.0081389 | 0.0060518 | 0.059251 | -0.0043685 | 0.066343 | -61.0245 | 62.2101 | -61.2213 | -61.203 | 61.7432 | -0.059509 | 0.004578 | 0.068665 | 62.1277 | -61.2396 | -0.27466 | 0.14191 | -0.07782 | -0.25635 | -0.32501 | -0.29297 | 0.05951 | 0.19684 | 60.9512 | 61.0153 | 122.6898 | 123.1567 | -0.07782 | 123.0743 | 60.8871 | -0.29297 | 123.1567 | -0.07782 | 60.8871 | 122.6898 | 123.0743 | -123.2895 | -123.3078
2552.7812 | 123.1201 | -60.8963 | 62.0773 | -0.29396 | -0.0052252 | -0.014975 | 0.0032748 | 0.06096 | -0.0058639 | 0.067197 | -61.0611 | 62.1277 | -61.2442 | -61.1526 | 61.821 | 0.050354 | 0.15106 | 0.20599 | 62.1735 | -61.1755 | -0.3479 | 0.050354 | -0.16479 | -0.25635 | -0.25635 | -0.27924 | 0.09613 | 0.18311 | 61.0474 | 61.1023 | 122.7173 | 123.024 | -0.16479 | 123.0698 | 60.9467 | -0.27924 | 123.024 | -0.16479 | 60.9467 | 122.7173 | 123.0698 | -123.3215 | -123.2529
2553.7812 | 123.1338 | -60.878 | 62.0773 | -0.057449 | -0.0054388 | -0.0098479 | 0.004343 | 0.062882 | -0.0062911 | 0.06442 | -60.9879 | 62.2055 | -61.1984 | -61.1023 | 61.8439 | 0.064087 | 0.036621 | 0.21515 | 62.1231 | -61.2076 | -0.32043 | 0.12817 | -0.10986 | -0.2243 | -0.23346 | -0.32959 | 0.045776 | 0.21057 | 60.9146 | 61.0931 | 122.7219 | 123.0835 | -0.10986 | 123.0011 | 60.9421 | -0.32959 | 123.0835 | -0.10986 | 60.9421 | 122.7219 | 123.0011 | -123.2758 | -123.2849
2554.7812 | 123.1979 | -60.8551 | 62.0728 | -0.15663 | -0.009284 | -0.010703 | -0.00035676 | 0.06096 | -0.0060775 | 0.067624 | -60.9741 | 62.114 | -61.1938 | -61.0657 | 61.9125 | 0.13733 | 0.013733 | 0.29755 | 62.1231 | -61.1298 | -0.33875 | 0.041199 | -0.11902 | -0.21057 | -0.16022 | -0.27466 | 0.050354 | 0.21973 | 60.8688 | 61.1526 | 122.7676 | 122.9691 | -0.11902 | 122.9782 | 60.9924 | -0.27466 | 122.9691 | -0.11902 | 60.9924 | 122.7676 | 122.9782 | -123.2666 | -123.2025
2555.7812 | 123.1796 | -60.8688 | 62.0773 | -0.21004 | -0.009925 | -0.012412 | -0.0020658 | 0.057755 | -0.0060775 | 0.065916 | -60.8917 | 62.178 | -61.1893 | -61.084 | 61.8393 | 0.082397 | 0.059509 | 0.25635 | 62.1002 | -61.1755 | -0.32044 | 0.10071 | -0.022889 | -0.21515 | -0.23804 | -0.3067 | 0.022888 | 0.29755 | 60.9283 | 61.1252 | 122.7081 | 123.0469 | -0.022889 | 122.9691 | 60.9512 | -0.3067 | 123.0469 | -0.022889 | 60.9512 | 122.7081 | 122.9691 | -123.2666 | -123.2529
2556.7812 | 123.1338 | -60.9009 | 62.0453 | 0.0035856 | -0.006507 | -0.010916 | 0.0092562 | 0.059464 | -0.0071457 | 0.067411 | -61.0199 | 62.114 | -61.2625 | -61.1389 | 61.8027 | 0.022888 | 0.013733 | 0.15106 | 62.1048 | -61.2167 | -0.36163 | 0.068665 | -0.11902 | -0.23804 | -0.24262 | -0.31586 | 0.059509 | 0.24262 | 60.9146 | 61.0519 | 122.7036 | 123.0148 | -0.11902 | 123.0057 | 60.9238 | -0.31586 | 123.0148 | -0.11902 | 60.9238 | 122.7036 | 123.0057 | -123.3078 | -123.262
2557.7812 | 123.2346 | -60.8643 | 62.0453 | 0.087509 | -0.0086432 | -0.0072845 | -0.0050566 | 0.059891 | -0.0037277 | 0.065488 | -61.0153 | 62.0865 | -61.203 | -61.0794 | 61.8805 | 0.10529 | -0.09613 | 0.25635 | 62.1048 | -61.1801 | -0.33875 | 0.041199 | -0.15106 | -0.21515 | -0.16479 | -0.31586 | 0.059509 | 0.18768 | 60.7681 | 61.1206 | 122.7448 | 122.9507 | -0.15106 | 122.9691 | 60.9695 | -0.31586 | 122.9507 | -0.15106 | 60.9695 | 122.7448 | 122.9691 | -123.2483 | -123.2254
2558.7812 | 123.143 | -60.91 | 62.0819 | -0.087967 | -0.0045844 | -0.0077117 | 0.0066928 | 0.062669 | -0.0060775 | 0.066129 | -60.965 | 62.2055 | -61.2213 | -61.1069 | 61.8073 | 0.050354 | 0.009155 | 0.19226 | 62.1231 | -61.2259 | -0.31128 | 0.1236 | -0.054932 | -0.19684 | -0.27466 | -0.31586 | 0.041199 | 0.25635 | 60.9192 | 61.1023 | 122.7173 | 123.1155 | -0.054932 | 123.0331 | 60.9604 | -0.31586 | 123.1155 | -0.054932 | 60.9604 | 122.7173 | 123.0331 | -123.3032 | -123.3078
2559.7812 | 123.1659 | -60.9055 | 62.0453 | 0.17143 | -0.0090704 | -0.012839 | -0.0044156 | 0.058823 | -0.0073593 | 0.066984 | -61.0428 | 62.0865 | -61.2442 | -61.1572 | 61.8118 | 0 | -0.10529 | 0.15106 | 62.1002 | -61.171 | -0.33875 | 0.041199 | -0.13733 | -0.25177 | -0.23346 | -0.2655 | 0.054932 | 0.20142 | 60.8002 | 61.0565 | 122.7173 | 122.9919 | -0.13733 | 123.0057 | 60.9055 | -0.2655 | 122.9919 | -0.13733 | 60.9055 | 122.7173 | 123.0057 | -123.2895 | -123.2162
2560.7812 | 123.175 | -60.8871 | 62.0453 | 0.13329 | -0.0090704 | -0.017539 | -0.0020658 | 0.059678 | -0.0047957 | 0.065061 | -61.0611 | 62.0865 | -61.2213 | -61.1435 | 61.8118 | 0.022888 | -0.068665 | 0.1831 | 62.1048 | -61.1481 | -0.33417 | 0.041199 | -0.17395 | -0.25635 | -0.23346 | -0.26093 | 0.059509 | 0.16022 | 60.8185 | 61.0703 | 122.699 | 122.9736 | -0.17395 | 122.9919 | 60.91 | -0.26093 | 122.9736 | -0.17395 | 60.91 | 122.699 | 122.9919 | -123.2666 | -123.1934
2561.7812 | 123.2437 | -60.8688 | 62.0361 | -0.034561 | -0.0084296 | -0.010489 | 0.00071144 | 0.056687 | -0.0075729 | 0.070829 | -61.0245 | 62.0819 | -61.235 | -61.0703 | 61.8805 | 0.10986 | -0.082397 | 0.27466 | 62.0956 | -61.1343 | -0.36621 | 0.045776 | -0.15564 | -0.20142 | -0.15564 | -0.2655 | 0.059509 | 0.21057 | 60.7864 | 61.1435 | 122.7493 | 122.9507 | -0.15564 | 122.9645 | 60.9787 | -0.2655 | 122.9507 | -0.15564 | 60.9787 | 122.7493 | 122.9645 | -123.2712 | -123.1705
2562.7812 | 123.2758 | -60.8459 | 62.0682 | -0.080337 | -0.0084296 | -0.011771 | 0.0017794 | 0.056901 | -0.0058639 | 0.066984 | -60.9741 | 62.0819 | -61.1801 | -61.0428 | 61.9125 | 0.13275 | -0.059509 | 0.29755 | 62.114 | -61.1481 | -0.33417 | 0.013733 | -0.12817 | -0.19684 | -0.15564 | -0.30212 | 0.045777 | 0.20599 | 60.7864 | 61.1435 | 122.7585 | 122.9279 | -0.12817 | 122.9599 | 60.9787 | -0.30212 | 122.9279 | -0.12817 | 60.9787 | 122.7585 | 122.9599 | -123.2483 | -123.2162
2563.7812 | 123.1705 | -60.8643 | 62.0682 | -0.10323 | -0.0084296 | -0.0096343 | 0.0034884 | 0.059251 | -0.0062911 | 0.068052 | -60.9924 | 62.1048 | -61.2122 | -61.0794 | 61.8439 | 0.10986 | 0.041199 | 0.27008 | 62.1231 | -61.1984 | -0.3479 | 0.036621 | -0.12817 | -0.21515 | -0.2243 | -0.33417 | 0.054932 | 0.21973 | 60.9055 | 61.1343 | 122.7081 | 122.9691 | -0.12817 | 122.9874 | 60.9741 | -0.33417 | 122.9691 | -0.12817 | 60.9741 | 122.7081 | 122.9874 | -123.2803 | -123.2666
2564.7812 | 123.2025 | -60.91 | 62.0773 | 0.14854 | -0.0071478 | -0.01348 | 0.00049764 | 0.058823 | -0.0052231 | 0.067197 | -61.0611 | 62.1002 | -61.2213 | -61.116 | 61.8073 | 0.013733 | -0.073242 | 0.1831 | 62.0956 | -61.1984 | -0.31128 | 0.022888 | -0.15106 | -0.20599 | -0.27008 | -0.28839 | 0.01831 | 0.16022 | 60.8368 | 61.0931 | 122.7173 | 123.0103 | -0.15106 | 123.0057 | 60.9238 | -0.28839 | 123.0103 | -0.15106 | 60.9238 | 122.7173 | 123.0057 | -123.2986 | -123.2758
2565.7812 | 123.2391 | -60.8963 | 62.0544 | 0.056992 | -0.0069342 | -0.012198 | 0.00049764 | 0.057969 | -0.0077865 | 0.06677 | -61.0474 | 62.0865 | -61.203 | -61.1069 | 61.9034 | 0.17395 | -0.082397 | 0.21973 | 62.1094 | -61.1893 | -0.3067 | 0.032044 | -0.15106 | -0.21057 | -0.15106 | -0.29297 | 0.054932 | 0.15564 | 60.8139 | 61.116 | 122.7997 | 122.9828 | -0.15106 | 123.0057 | 61.0703 | -0.29297 | 122.9828 | -0.15106 | 61.0703 | 122.7997 | 123.0057 | -123.2574 | -123.2437
2566.7812 | 123.2162 | -60.8459 | 62.0224 | -0.13374 | -0.0094976 | -0.01348 | 0.0024202 | 0.057542 | -0.0045821 | 0.066984 | -60.9741 | 62.0682 | -61.2122 | -61.0428 | 61.9171 | 0.13733 | -0.064087 | 0.32501 | 62.0865 | -61.1618 | -0.36621 | 0.045776 | -0.12817 | -0.19684 | -0.10529 | -0.31586 | 0.064087 | 0.23804 | 60.7819 | 61.171 | 122.7631 | 122.9141 | -0.12817 | 122.9324 | 60.9833 | -0.31586 | 122.9141 | -0.12817 | 60.9833 | 122.7631 | 122.9324 | -123.2346 | -123.1842
2567.7812 | 123.2574 | -60.8597 | 62.0407 | -0.14137 | -0.008216 | -0.010489 | 0.0013522 | 0.057969 | -0.0073593 | 0.065275 | -60.9604 | 62.0865 | -61.2076 | -61.0474 | 61.8896 | 0.14191 | -0.086975 | 0.33417 | 62.1094 | -61.1618 | -0.3479 | 0.045777 | -0.10071 | -0.18768 | -0.15106 | -0.30212 | 0.068665 | 0.24719 | 60.7727 | 61.1938 | 122.7493 | 122.9462 | -0.10071 | 122.9691 | 61.0016 | -0.30212 | 122.9462 | -0.10071 | 61.0016 | 122.7493 | 122.9691 | -123.2483 | -123.2025
2568.7812 | 123.2117 | -60.8688 | 62.0407 | 0.018845 | -0.007575 | -0.013907 | 7.0444e-05 | 0.056901 | -0.0056503 | 0.066343 | -61.0336 | 62.0911 | -61.203 | -61.0794 | 61.8576 | 0.059509 | -0.064087 | 0.23804 | 62.0773 | -61.171 | -0.33417 | 0.050354 | -0.1648 | -0.21057 | -0.1831 | -0.30212 | 0.036622 | 0.16937 | 60.8047 | 61.1069 | 122.7264 | 122.9599 | -0.1648 | 122.9462 | 60.9283 | -0.30212 | 122.9599 | -0.1648 | 60.9283 | 122.7264 | 122.9462 | -123.2437 | -123.2117
2569.7812 | 123.23 | -60.8688 | 62.0499 | -0.61439 | -0.008216 | -0.013052 | 0.0022066 | 0.05626 | -0.0056503 | 0.06677 | -61.0657 | 62.1094 | -61.2213 | -61.1069 | 61.8301 | 0.041199 | -0.086975 | 0.21515 | 62.0773 | -61.1618 | -0.35248 | 0.059509 | -0.19684 | -0.23804 | -0.21973 | -0.29297 | 0.027466 | 0.15564 | 60.7819 | 61.084 | 122.699 | 122.9782 | -0.19684 | 122.9462 | 60.91 | -0.29297 | 122.9782 | -0.19684 | 60.91 | 122.699 | 122.9462 | -123.2712 | -123.2117
2570.7812 | 123.2529 | -60.8688 | 62.0499 | -0.065079 | -0.0067206 | -0.011984 | -0.00057036 | 0.057114 | -0.0050095 | 0.067411 | -61.0199 | 62.0911 | -61.2076 | -61.0428 | 61.8851 | 0.11444 | -0.091553 | 0.27008 | 62.0773 | -61.1618 | -0.33875 | 0.041198 | -0.15106 | -0.17395 | -0.16479 | -0.29297 | 0.027466 | 0.18768 | 60.7773 | 61.1389 | 122.7539 | 122.9599 | -0.15106 | 122.9462 | 60.9833 | -0.29297 | 122.9599 | -0.15106 | 60.9833 | 122.7539 | 122.9462 | -123.2574 | -123.2117
2571.7812 | 123.2437 | -60.8643 | 62.0636 | -0.149 | -0.0094976 | -0.012625 | 7.0444e-05 | 0.056473 | -0.0039413 | 0.06677 | -60.9512 | 62.0819 | -61.1847 | -61.0199 | 61.9034 | 0.12817 | -0.045776 | 0.3067 | 62.0865 | -61.1664 | -0.32043 | 0.01831 | -0.086975 | -0.15564 | -0.16022 | -0.30212 | 0.022888 | 0.23346 | 60.8185 | 61.171 | 122.7676 | 122.9462 | -0.086975 | 122.9507 | 60.9924 | -0.30212 | 122.9462 | -0.086975 | 60.9924 | 122.7676 | 122.9507 | -123.2483 | -123.23
2572.7812 | 123.2117 | -60.878 | 62.0544 | -0.16426 | -0.008216 | -0.016043 | 0.0034884 | 0.057755 | -0.0065047 | 0.068265 | -60.7361 | 62.1414 | -61.1664 | -61.0703 | 61.8576 | 0.10529 | -0.045776 | 0.30212 | 62.1048 | -61.1526 | -0.28839 | 0.086975 | 0.14191 | -0.19226 | -0.19684 | -0.27466 | 0.050354 | 0.4303 | 60.8322 | 61.1801 | 122.7356 | 123.0194 | 0.14191 | 122.9828 | 60.9833 | -0.27466 | 123.0194 | 0.14191 | 60.9833 | 122.7356 | 122.9828 | -123.2208 | -123.2071
2573.7812 | 123.2529 | -60.8505 | 62.0453 | -0.095596 | -0.009284 | -0.0092071 | 0.00028404 | 0.058396 | -0.0065047 | 0.065488 | -60.9695 | 62.0682 | -61.1847 | -61.0336 | 61.9171 | 0.14648 | -0.10071 | 0.32959 | 62.1231 | -61.1298 | -0.33417 | 0.022888 | -0.11902 | -0.18311 | -0.12817 | -0.27924 | 0.07782 | 0.21515 | 60.7498 | 61.1801 | 122.7676 | 122.9187 | -0.11902 | 122.9736 | 60.997 | -0.27924 | 122.9187 | -0.11902 | 60.997 | 122.7676 | 122.9736 | -123.23 | -123.175
2574.7812 | 123.2574 | -60.8459 | 62.0544 | -0.13374 | -0.0084296 | -0.014121 | 0.0013522 | 0.056687 | -0.0054367 | 0.066984 | -60.9741 | 62.114 | -61.1893 | -61.0153 | 61.8942 | 0.14648 | -0.07782 | 0.32501 | 62.0865 | -61.1526 | -0.34332 | 0.05951 | -0.12817 | -0.16937 | -0.16022 | -0.3067 | 0.032044 | 0.21515 | 60.7681 | 61.171 | 122.7402 | 122.9599 | -0.12817 | 122.9324 | 60.9924 | -0.3067 | 122.9599 | -0.12817 | 60.9924 | 122.7402 | 122.9324 | -123.2437 | -123.2071
2575.7812 | 123.2346 | -60.8643 | 62.0499 | -0.13374 | -0.0080024 | -0.011557 | 0.0011386 | 0.055192 | -0.0067185 | 0.066556 | -60.9787 | 62.0773 | -61.2122 | -61.2076 | 61.7798 | 0.11444 | -0.13275 | 0.31128 | 62.0682 | -61.1618 | -0.3479 | 0.027466 | -0.11444 | -0.34332 | -0.27008 | -0.29755 | 0.01831 | 0.23346 | 60.7315 | 61.1755 | 122.644 | 122.9416 | -0.11444 | 122.9324 | 60.9787 | -0.29755 | 122.9416 | -0.11444 | 60.9787 | 122.644 | 122.9324 | -123.262 | -123.2117
2576.7812 | 123.262 | -60.878 | 62.0544 | 0.14092 | -0.009284 | -0.011343 | 0.002634 | 0.059891 | -0.0073593 | 0.066984 | -61.0657 | 62.0819 | -61.2076 | -61.1206 | 61.821 | 0.027466 | -0.082397 | 0.16937 | 62.1002 | -61.1526 | -0.32959 | 0.027466 | -0.18768 | -0.24261 | -0.23346 | -0.27466 | 0.045777 | 0.14191 | 60.7956 | 61.0474 | 122.699 | 122.9599 | -0.18768 | 122.9782 | 60.9055 | -0.27466 | 122.9599 | -0.18768 | 60.9055 | 122.699 | 122.9782 | -123.262 | -123.2071
2577.7812 | 123.2254 | -60.8597 | 62.0636 | -0.13374 | -0.0090704 | -0.013693 | 0.0015658 | 0.057328 | -0.0033005 | 0.066129 | -60.9558 | 62.0956 | -61.1938 | -61.0153 | 61.9308 | 0.3479 | -0.036621 | 0.13275 | 62.1185 | -61.1526 | -0.33417 | 0.032043 | -0.096131 | -0.15564 | -0.13275 | -0.29297 | 0.054931 | 0.23804 | 60.8231 | 60.9924 | 122.7905 | 122.9553 | -0.096131 | 122.9782 | 61.2076 | -0.29297 | 122.9553 | -0.096131 | 61.2076 | 122.7905 | 122.9782 | -123.2574 | -123.2162
2578.7812 | 123.2117 | -60.8917 | 62.0636 | -0.14137 | -0.0088568 | -0.0064301 | 0.0032748 | 0.059464 | -0.0073593 | 0.066343 | -60.9741 | 62.1048 | -61.2076 | -61.0382 | 61.8896 | 0.13275 | -0.004578 | 0.29297 | 62.1323 | -61.1298 | -0.31586 | 0.041198 | -0.082397 | -0.14648 | -0.17395 | -0.23804 | 0.068664 | 0.23346 | 60.8871 | 61.1847 | 122.7814 | 122.9965 | -0.082397 | 123.024 | 61.0245 | -0.23804 | 122.9965 | -0.082397 | 61.0245 | 122.7814 | 123.024 | -123.2712 | -123.1934
2579.7812 | 123.3353 | -60.8414 | 62.114 | -0.095596 | -0.0086432 | -0.012839 | -0.00057036 | 0.060319 | -0.0082137 | 0.064847 | -60.9604 | 62.1048 | -61.203 | -61.0336 | 61.908 | 0.15106 | -0.050354 | 0.32501 | 62.1002 | -61.1435 | -0.36163 | -0.009156 | -0.11902 | -0.19226 | -0.20599 | -0.30212 | -0.013733 | 0.24262 | 60.791 | 61.1664 | 122.7493 | 122.9462 | -0.11902 | 122.9416 | 60.9924 | -0.30212 | 122.9462 | -0.11902 | 60.9924 | 122.7493 | 122.9416 | -123.317 | -123.2574
2580.7812 | 123.2254 | -60.8688 | 62.0544 | -0.11848 | -0.0071478 | -0.013266 | 0.0011386 | 0.057114 | -0.0058639 | 0.066343 | -60.965 | 62.1002 | -61.2167 | -61.0336 | 61.9034 | 0.12817 | -0.009155 | 0.29755 | 62.0956 | -61.1481 | -0.3479 | 0.045777 | -0.096131 | -0.1648 | -0.15106 | -0.27924 | 0.041199 | 0.25177 | 60.8597 | 61.1664 | 122.7722 | 122.9691 | -0.096131 | 122.9645 | 60.997 | -0.27924 | 122.9691 | -0.096131 | 60.997 | 122.7722 | 122.9645 | -123.2712 | -123.2025
2581.7812 | 123.1979 | -60.8917 | 62.0407 | 0.15617 | -0.0090704 | -0.014334 | 0.00049764 | 0.058182 | -0.0054367 | 0.06677 | -61.0703 | 62.0682 | -61.2259 | -61.1206 | 61.821 | 0.018311 | -0.10071 | 0.15564 | 62.0682 | -61.1755 | -0.33417 | 0.027466 | -0.17853 | -0.22888 | -0.21973 | -0.28381 | 0.027466 | 0.15564 | 60.791 | 61.0474 | 122.7127 | 122.9599 | -0.17853 | 122.9599 | 60.91 | -0.28381 | 122.9599 | -0.17853 | 60.91 | 122.7127 | 122.9599 | -123.2666 | -123.2162
2582.7812 | 123.2071 | -60.8597 | 62.0728 | -0.10323 | -0.0084296 | -0.0098479 | 0.0011386 | 0.061173 | -0.0077865 | 0.064847 | -60.9695 | 62.0819 | -61.2213 | -61.0291 | 61.9034 | 0.13733 | -0.041199 | 0.30212 | 62.0911 | -61.1435 | -0.36163 | 0.009155 | -0.10986 | -0.16937 | -0.16937 | -0.28381 | 0.01831 | 0.25177 | 60.8185 | 61.1618 | 122.7631 | 122.9416 | -0.10986 | 122.9507 | 60.997 | -0.28381 | 122.9416 | -0.10986 | 60.997 | 122.7631 | 122.9507 | -123.2941 | -123.2162
2583.7812 | 123.143 | -60.8551 | 62.0682 | -0.17952 | -0.0084296 | -0.012412 | 0.0022066 | 0.059037 | -0.0084273 | 0.067838 | -60.9924 | 62.1231 | -61.2076 | -61.0611 | 61.8576 | 0.10986 | 0.041199 | 0.2655 | 62.1002 | -61.1435 | -0.35248 | 0.054932 | -0.13733 | -0.20599 | -0.21057 | -0.28839 | 0.032044 | 0.21515 | 60.8963 | 61.1206 | 122.7127 | 122.9782 | -0.13733 | 122.9553 | 60.965 | -0.28839 | 122.9782 | -0.13733 | 60.965 | 122.7127 | 122.9553 | -123.2758 | -123.2117
2584.7812 | 123.1842 | -60.8505 | 62.0819 | -0.19478 | -0.0077888 | -0.013693 | 0.0024202 | 0.057542 | -0.0090683 | 0.066984 | -60.997 | 62.1185 | -61.203 | -61.0611 | 61.8759 | 0.1236 | 0.027466 | 0.2655 | 62.1048 | -61.1389 | -0.35248 | 0.036621 | -0.14648 | -0.21057 | -0.20599 | -0.28839 | 0.022888 | 0.20599 | 60.878 | 61.116 | 122.7264 | 122.9691 | -0.14648 | 122.9553 | 60.9741 | -0.28839 | 122.9691 | -0.14648 | 60.9741 | 122.7264 | 122.9553 | -123.2849 | -123.2208
2585.7812 | 123.2208 | -60.8688 | 62.0544 | -1.7283 | -0.012916 | -0.013266 | 0.00092504 | 0.057542 | -0.0056503 | 0.064634 | -60.9467 | 62.1094 | -61.1893 | -61.0474 | 61.8942 | 0.11444 | -0.054932 | 0.31128 | 62.0773 | -61.1572 | -0.32044 | 0.054932 | -0.07782 | -0.17853 | -0.16022 | -0.28839 | 0.022889 | 0.24262 | 60.8139 | 61.1801 | 122.7631 | 122.9782 | -0.07782 | 122.9462 | 60.9833 | -0.28839 | 122.9782 | -0.07782 | 60.9833 | 122.7631 | 122.9462 | -123.2437 | -123.2117
2586.7812 | 123.2529 | -60.8459 | 62.0407 | -0.026932 | -0.0084296 | -0.013693 | 0.0015658 | 0.057969 | -0.0058639 | 0.067624 | -61.0062 | 62.0773 | -61.171 | -61.0519 | 61.8942 | 0.10529 | -0.050354 | 0.3067 | 62.1048 | -61.1526 | -0.32501 | 0.036622 | -0.16022 | -0.20599 | -0.14648 | -0.3067 | 0.064087 | 0.16479 | 60.7956 | 61.1526 | 122.7402 | 122.9233 | -0.16022 | 122.9507 | 60.9512 | -0.3067 | 122.9233 | -0.16022 | 60.9512 | 122.7402 | 122.9507 | -123.2117 | -123.1934
2587.7812 | 123.2574 | -60.8597 | 62.0407 | -0.026932 | -0.009284 | -0.010916 | -0.00099756 | 0.056901 | -0.0071457 | 0.064207 | -61.0107 | 62.0773 | -61.1984 | -61.0519 | 61.8988 | 0.10529 | -0.082397 | 0.27924 | 62.0682 | -61.1343 | -0.33875 | 0.036622 | -0.15106 | -0.19226 | -0.14191 | -0.27466 | 0.027466 | 0.18768 | 60.7773 | 61.1389 | 122.7585 | 122.937 | -0.15106 | 122.9279 | 60.965 | -0.27466 | 122.937 | -0.15106 | 60.965 | 122.7585 | 122.9279 | -123.2391 | -123.175
2588.7812 | 123.1522 | -60.8917 | 62.114 | -0.11085 | -0.0069342 | -0.014334 | 0.005411 | 0.057969 | -0.0054367 | 0.067838 | -61.0245 | 62.1597 | -61.2488 | -61.1023 | 61.8118 | 0.045776 | 0.10986 | 0.19226 | 62.1185 | -61.1801 | -0.35705 | 0.045776 | -0.13275 | -0.21057 | -0.30212 | -0.28839 | 0.004577 | 0.2243 | 61.0016 | 61.084 | 122.7036 | 123.0515 | -0.13275 | 123.0103 | 60.9375 | -0.28839 | 123.0515 | -0.13275 | 60.9375 | 122.7036 | 123.0103 | -123.3627 | -123.2941
2589.7812 | 123.1934 | -60.878 | 62.0682 | -0.034561 | -0.0086432 | -0.011984 | -0.00099756 | 0.058182 | -0.0045821 | 0.068052 | -61.0199 | 62.0956 | -61.1893 | -61.0703 | 61.8851 | 0.09613 | -0.086975 | 0.2655 | 62.0636 | -61.1572 | -0.31128 | 0.027466 | -0.14191 | -0.19226 | -0.1831 | -0.27924 | -0.004577 | 0.16937 | 60.791 | 61.1435 | 122.7631 | 122.9736 | -0.14191 | 122.9416 | 60.9741 | -0.27924 | 122.9736 | -0.14191 | 60.9741 | 122.7631 | 122.9416 | -123.2574 | -123.2254
2590.7812 | 123.2483 | -60.8505 | 62.0544 | -0.13374 | -0.0084296 | -0.011771 | -0.00057036 | 0.058396 | -0.0067185 | 0.065488 | -60.9695 | 62.1002 | -61.1938 | -61.0291 | 61.9125 | 0.16022 | -0.10071 | 0.32044 | 62.0956 | -61.1343 | -0.34332 | 0.045777 | -0.11902 | -0.17853 | -0.14191 | -0.28381 | 0.041199 | 0.22431 | 60.7498 | 61.171 | 122.7631 | 122.9507 | -0.11902 | 122.9462 | 61.0107 | -0.28381 | 122.9507 | -0.11902 | 61.0107 | 122.7631 | 122.9462 | -123.2483 | -123.1888
2591.7812 | 123.2574 | -60.8368 | 62.0453 | 0.33928 | -0.0077888 | -0.013907 | 0.0011386 | 0.055192 | -0.0054367 | 0.06442 | -60.9924 | 62.0911 | -61.1893 | -61.0245 | 61.8805 | 0.14191 | -0.059509 | 0.31128 | 62.1002 | -61.1481 | -0.35248 | 0.045776 | -0.15564 | -0.18768 | -0.16479 | -0.31128 | 0.054932 | 0.19684 | 60.7773 | 61.1481 | 122.7173 | 122.9279 | -0.15564 | 122.937 | 60.9787 | -0.31128 | 122.9279 | -0.15564 | 60.9787 | 122.7173 | 122.937 | -123.2346 | -123.1934
2592.7812 | 123.1842 | -60.8688 | 62.1048 | -0.14137 | -0.0073614 | -0.011984 | 0.001993 | 0.057755 | -0.0052231 | 0.066556 | -60.9695 | 62.1323 | -61.1893 | -61.0291 | 61.8851 | 0.14191 | 0.009155 | 0.29755 | 62.114 | -61.1664 | -0.32044 | 0.027466 | -0.10071 | -0.16022 | -0.21973 | -0.29755 | 0.009156 | 0.21973 | 60.878 | 61.1664 | 122.7539 | 123.0011 | -0.10071 | 122.9828 | 61.0107 | -0.29755 | 123.0011 | -0.10071 | 61.0107 | 122.7539 | 122.9828 | -123.2941 | -123.2712
2593.7812 | 123.111 | -60.8871 | 62.1048 | -0.20241 | -0.0067206 | -0.0098479 | 0.0073336 | 0.059464 | -0.0077865 | 0.066984 | -61.1252 | 62.1643 | -61.1938 | -61.1618 | 61.7798 | 0.064087 | 0.10986 | 0.18768 | 62.1368 | -61.1984 | -0.3067 | 0.05951 | -0.23804 | -0.27466 | -0.32501 | -0.31128 | 0.032044 | 0.068665 | 60.997 | 61.0748 | 122.6669 | 123.0515 | -0.23804 | 123.024 | 60.9512 | -0.31128 | 123.0515 | -0.23804 | 60.9512 | 122.6669 | 123.024 | -123.2986 | -123.3032
2594.7812 | 123.1979 | -60.8734 | 62.027 | 0.049362 | -0.0073614 | -0.011557 | -0.0018522 | 0.060105 | -0.0062911 | 0.066984 | -61.084 | 62.0728 | -61.2259 | -61.1069 | 61.8393 | 0.041199 | -0.07782 | 0.19684 | 62.0819 | -61.1435 | -0.35248 | 0.045776 | -0.21057 | -0.23346 | -0.18768 | -0.27008 | 0.054931 | 0.14191 | 60.7956 | 61.0703 | 122.7127 | 122.9462 | -0.21057 | 122.9553 | 60.9146 | -0.27008 | 122.9462 | -0.21057 | 60.9146 | 122.7127 | 122.9553 | -123.2529 | -123.1705
2595.7812 | 123.2391 | -60.8826 | 62.0407 | 0.011215 | -0.0086432 | -0.012198 | -0.00014316 | 0.057755 | -0.0071457 | 0.06912 | -61.0428 | 62.1002 | -61.203 | -61.0657 | 61.8713 | 0.073242 | -0.059509 | 0.24261 | 62.0682 | -61.1618 | -0.32044 | 0.05951 | -0.16022 | -0.18311 | -0.16937 | -0.27924 | 0.027466 | 0.16022 | 60.8231 | 61.1252 | 122.7539 | 122.9828 | -0.16022 | 122.9507 | 60.9558 | -0.27924 | 122.9828 | -0.16022 | 60.9558 | 122.7539 | 122.9507 | -123.2437 | -123.2025
2596.7812 | 123.175 | -60.8551 | 62.0728 | -0.17952 | -0.0088568 | -0.0098479 | 0.003702 | 0.057755 | -0.0060775 | 0.065702 | -60.9787 | 62.1231 | -61.203 | -61.0519 | 61.8805 | 0.10529 | 0.032043 | 0.28839 | 62.1185 | -61.1572 | -0.3479 | 0.050354 | -0.1236 | -0.19684 | -0.19226 | -0.30212 | 0.045776 | 0.2243 | 60.8871 | 61.1435 | 122.7356 | 122.9782 | -0.1236 | 122.9736 | 60.9604 | -0.30212 | 122.9782 | -0.1236 | 60.9604 | 122.7356 | 122.9736 | -123.2758 | -123.23
2597.7812 | 123.1979 | -60.9009 | 62.0407 | 0.1104 | -0.010566 | -0.015616 | -0.00099756 | 0.05861 | -0.0069321 | 0.068052 | -61.0565 | 62.0865 | -61.2076 | -61.0245 | 62.027 | 0.11902 | -0.14191 | 0.13733 | 62.1094 | -61.1618 | -0.3067 | 0.045777 | -0.15564 | -0.1236 | -0.013732 | -0.26092 | 0.068665 | 0.15106 | 60.759 | 61.0382 | 122.9279 | 122.9874 | -0.15564 | 123.0103 | 61.0199 | -0.26092 | 122.9874 | -0.15564 | 61.0199 | 122.9279 | 123.0103 | -123.2483 | -123.2025
2598.7812 | 123.1613 | -60.8963 | 62.0819 | -0.065079 | -0.0067206 | -0.0096343 | 0.0073336 | 0.059464 | -0.0084273 | 0.063993 | -60.997 | 62.1597 | -61.235 | -61.0748 | 61.8347 | 0.068665 | 0.032043 | 0.18768 | 62.1185 | -61.1618 | -0.33874 | 0.07782 | -0.10071 | -0.17853 | -0.24719 | -0.2655 | 0.036621 | 0.23804 | 60.9283 | 61.084 | 122.731 | 123.056 | -0.10071 | 123.0148 | 60.965 | -0.2655 | 123.056 | -0.10071 | 60.965 | 122.731 | 123.0148 | -123.317 | -123.2437
2599.7812 | 123.2208 | -60.8734 | 62.0636 | -0.080337 | -0.0069342 | -0.0098479 | -0.0020658 | 0.058823 | -0.0047957 | 0.066556 | -60.9558 | 62.1048 | -61.1938 | -61.0428 | 61.9125 | 0.24719 | 0.21515 | 0.07782 | 62.1277 | -61.1206 | -0.32044 | 0.041198 | -0.082398 | -0.16937 | -0.15106 | -0.24719 | 0.064087 | 0.23804 | 61.0886 | 60.9512 | 122.7859 | 122.9782 | -0.082398 | 123.0011 | 61.1206 | -0.24719 | 122.9782 | -0.082398 | 61.1206 | 122.7859 | 123.0011 | -123.2574 | -123.1842
2600.7812 | 123.2025 | -60.878 | 62.0499 | -0.11085 | -0.010993 | -0.014548 | 0.0015658 | 0.057755 | -0.0062911 | 0.065702 | -60.9741 | 62.1094 | -61.1801 | -61.0382 | 61.9125 | 0.13733 | -0.009155 | 0.32044 | 62.0819 | -61.1526 | -0.30212 | 0.059509 | -0.09613 | -0.16022 | -0.13733 | -0.27466 | 0.032043 | 0.20599 | 60.8688 | 61.1984 | 122.7905 | 122.9874 | -0.09613 | 122.9599 | 61.0153 | -0.27466 | 122.9874 | -0.09613 | 61.0153 | 122.7905 | 122.9599 | -123.23 | -123.2025
2601.7812 | 123.1979 | -60.8917 | 62.0499 | 0.17143 | -0.0088568 | -0.010703 | 0.0024202 | 0.057755 | -0.0052231 | 0.066129 | -61.0611 | 62.0865 | -61.2122 | -61.1252 | 61.8301 | 0 | -0.10986 | 0.16937 | 62.0911 | -61.1984 | -0.32043 | 0.036621 | -0.16937 | -0.23346 | -0.21973 | -0.3067 | 0.041198 | 0.15106 | 60.7819 | 61.0611 | 122.7219 | 122.9782 | -0.16937 | 122.9828 | 60.8917 | -0.3067 | 122.9782 | -0.16937 | 60.8917 | 122.7219 | 122.9828 | -123.262 | -123.2483
2602.7812 | 123.2391 | -60.878 | 62.059 | -0.11848 | -0.0077888 | -0.016898 | -0.00078396 | 0.059251 | -0.0075729 | 0.066984 | -60.9695 | 62.0865 | -61.1984 | -61.0245 | 61.9125 | 0.14648 | -0.091553 | 0.31586 | 62.0819 | -61.1435 | -0.32043 | 0.027466 | -0.091552 | -0.14648 | -0.14648 | -0.2655 | 0.022888 | 0.22888 | 60.7864 | 61.1938 | 122.7905 | 122.9645 | -0.091552 | 122.9599 | 61.0245 | -0.2655 | 122.9645 | -0.091552 | 61.0245 | 122.7905 | 122.9599 | -123.2574 | -123.2025
2603.7812 | 123.2025 | -60.8871 | 62.0682 | -0.095596 | -0.0090704 | -0.017111 | 0.0028476 | 0.058823 | -0.0052231 | 0.065702 | -60.9604 | 62.0773 | -61.1893 | -61.0382 | 61.9125 | 0.12817 | -0.045776 | 0.32501 | 62.0636 | -61.1343 | -0.30212 | 0.009156 | -0.073242 | -0.15106 | -0.15564 | -0.24719 | -0.004577 | 0.22888 | 60.8414 | 61.2122 | 122.7997 | 122.9645 | -0.073242 | 122.9507 | 61.0153 | -0.24719 | 122.9645 | -0.073242 | 61.0153 | 122.7997 | 122.9507 | -123.2574 | -123.2025
2604.7812 | 123.2254 | -60.8597 | 62.0453 | -0.46944 | -0.0069342 | -0.011343 | 0.00028404 | 0.058823 | -0.0041549 | 0.065061 | -61.0107 | 62.0865 | -61.235 | -61.0428 | 61.8942 | 0.15564 | -0.054932 | 0.3067 | 62.0728 | -61.1435 | -0.37537 | 0.041199 | -0.15106 | -0.18311 | -0.15106 | -0.28381 | 0.027466 | 0.2243 | 60.8047 | 61.1664 | 122.7539 | 122.9462 | -0.15106 | 122.9324 | 61.0153 | -0.28381 | 122.9462 | -0.15106 | 61.0153 | 122.7539 | 122.9324 | -123.2803 | -123.1888
2605.7812 | 123.1888 | -60.9009 | 62.0499 | 0.087509 | -0.0084296 | -0.012412 | 0.0028476 | 0.058823 | -0.0052231 | 0.068479 | -61.0565 | 62.0956 | -61.2167 | -61.1481 | 61.8484 | 0.022888 | -0.050354 | 0.15106 | 62.0819 | -61.1755 | -0.31586 | 0.045776 | -0.15564 | -0.24719 | -0.20142 | -0.27466 | 0.032043 | 0.16022 | 60.8505 | 61.0519 | 122.7493 | 122.9965 | -0.15564 | 122.9828 | 60.9238 | -0.27466 | 122.9965 | -0.15564 | 60.9238 | 122.7493 | 122.9828 | -123.2666 | -123.2254
2606.7812 | 123.2117 | -60.878 | 62.027 | 0.049362 | -0.0077888 | -0.0087799 | 0.00049764 | 0.057542 | -0.0045821 | 0.066343 | -61.0336 | 62.0865 | -61.2442 | -61.0931 | 61.8622 | 0.073242 | -0.07782 | 0.23804 | 62.0819 | -61.1572 | -0.36621 | 0.059509 | -0.15564 | -0.21515 | -0.16479 | -0.27924 | 0.054931 | 0.21057 | 60.8002 | 61.116 | 122.7402 | 122.9645 | -0.15564 | 122.9599 | 60.9512 | -0.27924 | 122.9645 | -0.15564 | 60.9512 | 122.7402 | 122.9599 | -123.2712 | -123.1842
2607.7812 | 123.2391 | -60.8505 | 62.059 | -0.026932 | -0.0090704 | -0.011771 | 0.00049764 | 0.05626 | -0.0043685 | 0.067197 | -61.0062 | 62.1002 | -61.1938 | -61.0474 | 61.8942 | 0.11444 | -0.064087 | 0.3067 | 62.0728 | -61.1435 | -0.34332 | 0.041199 | -0.15564 | -0.19684 | -0.16479 | -0.29297 | 0.013733 | 0.18768 | 60.7864 | 61.1572 | 122.7448 | 122.9507 | -0.15564 | 122.9233 | 60.965 | -0.29297 | 122.9507 | -0.15564 | 60.965 | 122.7448 | 122.9233 | -123.2529 | -123.2025
2608.7812 | 123.1155 | -60.8917 | 62.0728 | -1.8656 | -0.004798 | -0.01583 | 0.0062656 | 0.057114 | -0.0062911 | 0.066984 | -61.1114 | 62.178 | -61.2442 | -61.1389 | 61.7752 | 0.032043 | 0.12817 | 0.20142 | 62.1506 | -61.1526 | -0.35248 | 0.10529 | -0.21973 | -0.24719 | -0.29755 | -0.26092 | 0.07782 | 0.13275 | 61.0199 | 61.0931 | 122.6669 | 123.0698 | -0.21973 | 123.0423 | 60.9238 | -0.26092 | 123.0698 | -0.21973 | 60.9238 | 122.6669 | 123.0423 | -123.317 | -123.2254
2609.7812 | 123.2162 | -60.8597 | 62.0682 | -0.12611 | -0.0088568 | -0.010916 | 0.0032748 | 0.059678 | -0.0084273 | 0.064207 | -60.9833 | 62.114 | -61.1801 | -61.0382 | 61.8942 | 0.13275 | -0.004578 | 0.30212 | 62.114 | -61.1664 | -0.32044 | 0.045777 | -0.1236 | -0.17853 | -0.17395 | -0.3067 | 0.045777 | 0.19684 | 60.8551 | 61.1618 | 122.7539 | 122.9736 | -0.1236 | 122.9736 | 60.9924 | -0.3067 | 122.9736 | -0.1236 | 60.9924 | 122.7539 | 122.9736 | -123.2483 | -123.2346
2610.7812 | 123.2208 | -60.8826 | 62.0407 | 0.041733 | -0.0088568 | -0.011984 | -0.00014316 | 0.057328 | -0.0065047 | 0.066129 | -61.0291 | 62.0773 | -61.1755 | -61.0565 | 61.8759 | 0.09613 | -0.091553 | 0.26093 | 62.0728 | -61.1618 | -0.29297 | 0.036622 | -0.14648 | -0.17395 | -0.16479 | -0.27924 | 0.032044 | 0.14648 | 60.791 | 61.1435 | 122.7585 | 122.9599 | -0.14648 | 122.9553 | 60.9787 | -0.27924 | 122.9599 | -0.14648 | 60.9787 | 122.7585 | 122.9553 | -123.2162 | -123.2025
2611.7812 | 123.2529 | -60.8643 | 62.0453 | -0.080337 | -0.010566 | -0.010489 | -0.00099756 | 0.058396 | -0.0056503 | 0.067411 | -60.9879 | 62.059 | -61.1893 | -61.0336 | 61.9354 | 0.14648 | -0.050354 | 0.31586 | 62.0911 | -61.1572 | -0.32501 | 0.013733 | -0.1236 | -0.16937 | -0.10986 | -0.29297 | 0.045776 | 0.20142 | 60.8139 | 61.1801 | 122.7997 | 122.9233 | -0.1236 | 122.9553 | 61.0107 | -0.29297 | 122.9233 | -0.1236 | 61.0107 | 122.7997 | 122.9553 | -123.2346 | -123.2025
2612.7812 | 123.23 | -60.8688 | 62.0407 | 0.2401 | -0.006507 | -0.01348 | 0.001993 | 0.057328 | -0.0065047 | 0.066984 | -60.997 | 62.0865 | -61.2076 | -61.0382 | 61.8896 | 0.1236 | -0.045776 | 0.31128 | 62.059 | -61.171 | -0.33875 | 0.045777 | -0.12817 | -0.16937 | -0.15106 | -0.30212 | 0.018311 | 0.21057 | 60.8231 | 61.1801 | 122.7585 | 122.9553 | -0.12817 | 122.9279 | 60.9924 | -0.30212 | 122.9553 | -0.12817 | 60.9924 | 122.7585 | 122.9279 | -123.2483 | -123.2117
2613.7812 | 123.2391 | -60.8917 | 62.0544 | -0.0040434 | -0.007575 | -0.014761 | -0.00035676 | 0.057969 | -0.0071457 | 0.067838 | -61.0428 | 62.0728 | -61.2076 | -61.0794 | 61.8759 | 0.10071 | -0.07782 | 0.24719 | 62.0773 | -61.1572 | -0.31586 | 0.018311 | -0.15106 | -0.18768 | -0.17853 | -0.2655 | 0.022889 | 0.16479 | 60.8139 | 61.1389 | 122.7676 | 122.9645 | -0.15106 | 122.9691 | 60.9924 | -0.2655 | 122.9645 | -0.15106 | 60.9924 | 122.7676 | 122.9691 | -123.262 | -123.2117
2614.7812 | 123.2208 | -60.878 | 62.0132 | 0.018845 | -0.0071478 | -0.015402 | 0.00028404 | 0.057542 | -0.0024459 | 0.065916 | -61.0291 | 62.1002 | -61.2305 | -61.0977 | 61.8668 | 0.082397 | -0.059509 | 0.23804 | 62.0728 | -61.1572 | -0.35248 | 0.086975 | -0.15106 | -0.21973 | -0.14648 | -0.27924 | 0.059509 | 0.20142 | 60.8185 | 61.116 | 122.7448 | 122.9782 | -0.15106 | 122.9507 | 60.9604 | -0.27924 | 122.9782 | -0.15106 | 60.9604 | 122.7448 | 122.9507 | -123.2437 | -123.1705
2615.7812 | 123.2437 | -60.8597 | 62.0407 | 0.018845 | -0.0088568 | -0.014761 | 0.00071144 | 0.054978 | -0.0060775 | 0.066343 | -61.0062 | 62.1048 | -61.2122 | -61.0519 | 61.8988 | 0.11444 | -0.068665 | 0.29755 | 62.0773 | -61.1618 | -0.35248 | 0.064087 | -0.14649 | -0.19226 | -0.14191 | -0.30212 | 0.036622 | 0.20599 | 60.791 | 61.1572 | 122.7585 | 122.9645 | -0.14649 | 122.937 | 60.9741 | -0.30212 | 122.9645 | -0.14649 | 60.9741 | 122.7585 | 122.937 | -123.2529 | -123.2025
2616.7812 | 123.2254 | -60.8688 | 62.0178 | -0.10323 | -0.0090704 | -0.012625 | 0.00049764 | 0.057755 | -0.0067185 | 0.065702 | -60.9558 | 62.0865 | -61.1984 | -61.0199 | 61.8988 | 0.004578 | 0.37994 | 0.48065 | 62.1552 | -61.1023 | -0.32959 | 0.068665 | -0.086976 | -0.15106 | -0.11902 | -0.23346 | 0.13733 | 0.24261 | 61.2488 | 61.3495 | 122.7676 | 122.9553 | -0.086976 | 123.024 | 60.8734 | -0.23346 | 122.9553 | -0.086976 | 60.8734 | 122.7676 | 123.024 | -123.2162 | -123.1201
2617.7812 | 123.1979 | -60.878 | 62.0544 | -0.095596 | -0.0088568 | -0.0083527 | 0.0022066 | 0.057969 | -0.0067185 | 0.063779 | -60.9741 | 62.0865 | -61.1893 | -61.0291 | 61.8896 | 0.11902 | -0.027466 | 0.29755 | 62.0956 | -61.1435 | -0.31128 | 0.032044 | -0.09613 | -0.15106 | -0.16479 | -0.2655 | 0.041199 | 0.21515 | 60.8505 | 61.1755 | 122.7676 | 122.9645 | -0.09613 | 122.9736 | 60.997 | -0.2655 | 122.9645 | -0.09613 | 60.997 | 122.7676 | 122.9736 | -123.2437 | -123.1979
2618.7812 | 123.2208 | -60.8871 | 62.0224 | -0.019302 | -0.006507 | -0.012625 | 0.0022066 | 0.058182 | -0.0047957 | 0.067838 | -61.0062 | 62.1094 | -61.2122 | -61.0611 | 61.8805 | 0.091553 | -0.07782 | 0.25177 | 62.0682 | -61.1755 | -0.32501 | 0.086975 | -0.11902 | -0.17395 | -0.14191 | -0.28839 | 0.045776 | 0.20599 | 60.8093 | 61.1389 | 122.7676 | 122.9965 | -0.11902 | 122.9553 | 60.9787 | -0.28839 | 122.9965 | -0.11902 | 60.9787 | 122.7676 | 122.9553 | -123.2346 | -123.1979
2619.7812 | 123.23 | -60.8597 | 62.059 | 0.25536 | -0.0088568 | -0.012412 | 0.00071144 | 0.056046 | -0.0065047 | 0.06442 | -60.997 | 62.1277 | -61.203 | -61.0336 | 61.8896 | 0.13733 | -0.045776 | 0.31586 | 62.0728 | -61.1664 | -0.34332 | 0.068665 | -0.13733 | -0.17395 | -0.16937 | -0.3067 | 0.013733 | 0.20599 | 60.8139 | 61.1755 | 122.7493 | 122.9874 | -0.13733 | 122.9324 | 60.997 | -0.3067 | 122.9874 | -0.13733 | 60.997 | 122.7493 | 122.9324 | -123.262 | -123.2254
2620.7812 | 123.2162 | -60.8368 | 62.059 | -0.11085 | -0.013343 | -0.014975 | 0.0015658 | 0.05861 | -0.0062911 | 0.068265 | -60.7132 | 62.1689 | -61.1526 | -61.0611 | 61.8942 | 0.13733 | -0.059509 | 0.3067 | 62.0544 | -61.1938 | -0.31586 | 0.10986 | 0.1236 | -0.2243 | -0.16479 | -0.35706 | -0.004578 | 0.43945 | 60.7773 | 61.1435 | 122.731 | 123.0057 | 0.1236 | 122.8912 | 60.9741 | -0.35706 | 123.0057 | 0.1236 | 60.9741 | 122.731 | 122.8912 | -123.2117 | -123.2529
2621.7812 | 123.1201 | -60.8917 | 62.1094 | -0.15663 | -0.0077888 | -0.013052 | 0.0028476 | 0.056046 | -0.0065047 | 0.066984 | -61.0474 | 62.1552 | -61.2076 | -61.1206 | 61.821 | 0.054932 | 0.1236 | 0.19226 | 62.1368 | -61.1664 | -0.31586 | 0.045776 | -0.15564 | -0.22888 | -0.28839 | -0.27466 | 0.027466 | 0.16022 | 61.0153 | 61.084 | 122.7127 | 123.0469 | -0.15564 | 123.0286 | 60.9467 | -0.27466 | 123.0469 | -0.15564 | 60.9467 | 122.7127 | 123.0286 | -123.317 | -123.2758
2622.7656 | 123.0423 | -60.8734 | 62.1094 | -0.14137 | -0.0080024 | -0.017539 | 0.002634 | 0.057755 | -0.0084273 | 0.065702 | -61.0565 | 62.146 | -61.2396 | -61.1298 | 61.8073 | 0.036621 | 0.1236 | 0.1831 | 62.1552 | -61.171 | -0.36621 | 0.036621 | -0.18311 | -0.25635 | -0.30212 | -0.29755 | 0.045776 | 0.1831 | 60.997 | 61.0565 | 122.6807 | 123.0194 | -0.18311 | 123.0286 | 60.91 | -0.29755 | 123.0194 | -0.18311 | 60.91 | 122.6807 | 123.0286 | -123.349 | -123.2803
2623.7656 | 123.2529 | -60.878 | 62.059 | 0.0035856 | -0.0060798 | -0.014975 | 0.00092504 | 0.058396 | -0.0041549 | 0.065275 | -60.965 | 62.0911 | -61.2213 | -61.0336 | 61.9217 | 0.15106 | -0.082397 | 0.31128 | 62.0911 | -61.1298 | -0.34332 | 0.032043 | -0.086975 | -0.15564 | -0.13733 | -0.25177 | 0.032043 | 0.25635 | 60.7956 | 61.1893 | 122.7997 | 122.9691 | -0.086975 | 122.9691 | 61.0291 | -0.25177 | 122.9691 | -0.086975 | 61.0291 | 122.7997 | 122.9691 | -123.2803 | -123.1888
2624.7812 | 123.1613 | -60.8917 | 62.1002 | -0.20241 | -0.006507 | -0.0098479 | 0.0034884 | 0.057114 | -0.0094955 | 0.066556 | -60.997 | 62.1597 | -61.2213 | -61.0794 | 61.8622 | 0.10529 | 0.054932 | 0.26093 | 62.114 | -61.171 | -0.32959 | 0.059509 | -0.10528 | -0.18768 | -0.23804 | -0.27923 | 0.013733 | 0.2243 | 60.9467 | 61.1526 | 122.7539 | 123.0515 | -0.10528 | 123.0057 | 60.997 | -0.27923 | 123.0515 | -0.10528 | 60.997 | 122.7539 | 123.0057 | -123.3215 | -123.2712
2625.7656 | 123.143 | -60.8963 | 62.1002 | -0.10323 | -0.004798 | -0.0057891 | 0.0064792 | 0.062028 | -0.0047957 | 0.066343 | -61.0245 | 62.1735 | -61.2396 | -61.1069 | 61.821 | 0.045776 | 0.10071 | 0.19226 | 62.1323 | -61.1755 | -0.34332 | 0.073242 | -0.12817 | -0.21057 | -0.27924 | -0.27924 | 0.032043 | 0.21515 | 60.997 | 61.0886 | 122.7173 | 123.0698 | -0.12817 | 123.0286 | 60.9421 | -0.27924 | 123.0698 | -0.12817 | 60.9421 | 122.7173 | 123.0286 | -123.3398 | -123.2758
2626.7656 | 123.1842 | -60.8917 | 62.0499 | -0.10323 | -0.0039434 | -0.010062 | 0.00712 | 0.059464 | -0.0069321 | 0.065275 | -60.9879 | 62.1735 | -61.2488 | -61.0748 | 61.8393 | 0.068665 | 0.022888 | 0.21515 | 62.1506 | -61.1755 | -0.35705 | 0.1236 | -0.09613 | -0.1831 | -0.21057 | -0.28381 | 0.10071 | 0.26093 | 60.9146 | 61.1069 | 122.731 | 123.0652 | -0.09613 | 123.0423 | 60.9604 | -0.28381 | 123.0652 | -0.09613 | 60.9604 | 122.731 | 123.0423 | -123.2986 | -123.2254
2627.7812 | 123.1293 | -60.9421 | 62.0636 | 0.087509 | -0.0060798 | -0.012412 | 0.0051974 | 0.06096 | -0.0075729 | 0.066556 | -61.0245 | 62.1643 | -61.235 | -61.1206 | 61.7844 | -0.018311 | 0.013733 | 0.10529 | 62.1277 | -61.203 | -0.29297 | 0.10071 | -0.082397 | -0.17853 | -0.27924 | -0.26093 | 0.064087 | 0.21057 | 60.9558 | 61.0474 | 122.7264 | 123.1064 | -0.082397 | 123.0698 | 60.9238 | -0.26093 | 123.1064 | -0.082397 | 60.9238 | 122.7264 | 123.0698 | -123.2986 | -123.2666
2628.7812 | 123.2391 | -60.8963 | 62.0499 | -0.12611 | -0.0084296 | -0.013052 | -0.0022794 | 0.059251 | -0.0054367 | 0.065702 | -60.9879 | 62.1185 | -61.2076 | -61.0519 | 61.8988 | 0.14191 | -0.022888 | 0.3067 | 62.1002 | -61.1343 | -0.31128 | 0.068664 | -0.091553 | -0.15564 | -0.15106 | -0.23804 | 0.050354 | 0.21973 | 60.8734 | 61.203 | 122.7951 | 123.0148 | -0.091553 | 122.9965 | 61.0382 | -0.23804 | 123.0148 | -0.091553 | 61.0382 | 122.7951 | 122.9965 | -123.2574 | -123.1842
2629.7812 | 123.2666 | -60.8643 | 62.0544 | -0.057449 | -0.0088568 | -0.0096343 | -0.0020658 | 0.058396 | -0.0075729 | 0.066343 | -60.9695 | 62.1185 | -61.1801 | -61.0474 | 61.94 | 0.16479 | -0.082397 | 0.31128 | 62.114 | -61.1298 | -0.31586 | 0.064087 | -0.10529 | -0.1831 | -0.11444 | -0.2655 | 0.05951 | 0.21057 | 60.7819 | 61.1755 | 122.8043 | 122.9828 | -0.10529 | 122.9782 | 61.0291 | -0.2655 | 122.9828 | -0.10529 | 61.0291 | 122.8043 | 122.9782 | -123.2346 | -123.1842
2630.7656 | 123.2346 | -60.8597 | 62.059 | 0.0035856 | -0.008216 | -0.01348 | -0.00014316 | 0.060105 | -0.0071457 | 0.066984 | -60.9833 | 62.1048 | -61.1938 | -61.0703 | 61.8851 | 0.1236 | -0.07782 | 0.29755 | 62.0728 | -61.1481 | -0.33417 | 0.045776 | -0.1236 | -0.21057 | -0.17395 | -0.28839 | 0.013733 | 0.21057 | 60.7819 | 61.1572 | 122.7448 | 122.9645 | -0.1236 | 122.9324 | 60.9833 | -0.28839 | 122.9645 | -0.1236 | 60.9833 | 122.7448 | 122.9324 | -123.2529 | -123.2071
2631.7656 | 123.2208 | -60.8688 | 62.0361 | -0.04982 | -0.0090704 | -0.015189 | 0.0017794 | 0.057542 | -0.0052231 | 0.06677 | -61.0107 | 62.1002 | -61.203 | -61.0703 | 61.8896 | 0.11902 | -0.073242 | 0.27008 | 62.0911 | -61.1801 | -0.33417 | 0.064087 | -0.14191 | -0.20142 | -0.14648 | -0.31128 | 0.054931 | 0.19226 | 60.7956 | 61.1389 | 122.7585 | 122.9691 | -0.14191 | 122.9599 | 60.9879 | -0.31128 | 122.9691 | -0.14191 | 60.9879 | 122.7585 | 122.9599 | -123.2391 | -123.2162
2632.7812 | 123.1476 | -60.9009 | 62.0911 | -0.11085 | -0.0060798 | -0.0089935 | 0.0086154 | 0.060532 | -0.0069321 | 0.068693 | -61.0382 | 62.1597 | -61.2122 | -61.1206 | 61.7889 | 0.045776 | 0.11444 | 0.19684 | 62.1277 | -61.1847 | -0.31128 | 0.068665 | -0.13733 | -0.21973 | -0.30212 | -0.28381 | 0.036622 | 0.17395 | 61.0153 | 61.0977 | 122.6898 | 123.0606 | -0.13733 | 123.0286 | 60.9467 | -0.28381 | 123.0606 | -0.13733 | 60.9467 | 122.6898 | 123.0286 | -123.3032 | -123.2758
2633.7656 | 123.2666 | -60.8597 | 62.0407 | -0.034561 | -0.0097114 | -0.014334 | -0.00014316 | 0.058396 | -0.0073593 | 0.065702 | -60.9833 | 62.1231 | -61.1618 | -61.0291 | 61.9125 | 0.15106 | -0.086975 | 0.30212 | 62.0911 | -61.1481 | -0.30212 | 0.082398 | -0.1236 | -0.16937 | -0.12817 | -0.28839 | 0.050354 | 0.17853 | 60.7727 | 61.1618 | 122.7722 | 122.9828 | -0.1236 | 122.9507 | 61.0107 | -0.28839 | 122.9828 | -0.1236 | 61.0107 | 122.7722 | 122.9507 | -123.2025 | -123.1888
2634.7656 | 123.1384 | -60.8963 | 62.0865 | -0.04982 | -0.0041572 | -0.01113 | 0.0051974 | 0.059464 | -0.0073593 | 0.065275 | -61.1343 | 62.178 | -61.235 | -61.1435 | 61.8027 | 0.045776 | 0.16022 | 0.19226 | 62.1597 | -61.2076 | -0.33874 | 0.091553 | -0.23804 | -0.24719 | -0.28381 | -0.31128 | 0.073242 | 0.10071 | 61.0565 | 61.0886 | 122.699 | 123.0743 | -0.23804 | 123.056 | 60.9421 | -0.31128 | 123.0743 | -0.23804 | 60.9421 | 122.699 | 123.056 | -123.3215 | -123.2941
2635.7656 | 123.1842 | -60.8414 | 62.0544 | -0.149 | -0.0067206 | -0.010703 | 7.0444e-05 | 0.058182 | -0.0058639 | 0.066343 | -60.965 | 62.1231 | -61.1893 | -61.0336 | 61.9034 | 0.15106 | 0.10071 | 0.65002 | 62.1231 | -61.1252 | -0.3479 | 0.068665 | -0.1236 | -0.19226 | -0.15106 | -0.28381 | 0.068665 | 0.2243 | 60.9421 | 61.4914 | 122.7448 | 122.9645 | -0.1236 | 122.9645 | 60.9924 | -0.28381 | 122.9645 | -0.1236 | 60.9924 | 122.7448 | 122.9645 | -123.2437 | -123.1796
2636.7656 | 123.1934 | -60.8826 | 62.0773 | -0.13374 | -0.007575 | -0.014975 | 0.00092504 | 0.056687 | -0.0058639 | 0.065916 | -60.9787 | 62.1277 | -61.1755 | -61.0519 | 61.8896 | 0.1236 | -0.027466 | 0.31586 | 62.1002 | -61.1664 | -0.29297 | 0.050354 | -0.096131 | -0.16937 | -0.18768 | -0.28381 | 0.022888 | 0.19684 | 60.8551 | 61.1984 | 122.7722 | 123.0103 | -0.096131 | 122.9828 | 61.0062 | -0.28381 | 123.0103 | -0.096131 | 61.0062 | 122.7722 | 122.9828 | -123.2529 | -123.2437
2637.7812 | 123.143 | -60.8917 | 62.0956 | -0.13374 | -0.0073614 | -0.0089935 | 0.0079744 | 0.057755 | -0.0084273 | 0.068052 | -61.0519 | 62.1826 | -61.2213 | -61.1298 | 61.8073 | 0.041199 | 0.10529 | 0.19684 | 62.1643 | -61.1847 | -0.32959 | 0.086975 | -0.16022 | -0.23804 | -0.28839 | -0.29297 | 0.068665 | 0.16937 | 60.997 | 61.0886 | 122.699 | 123.0743 | -0.16022 | 123.056 | 60.9329 | -0.29297 | 123.0743 | -0.16022 | 60.9329 | 122.699 | 123.056 | -123.317 | -123.2803
2638.7656 | 123.2117 | -60.878 | 62.0499 | -0.011673 | -0.0084296 | -0.012839 | 0.00049764 | 0.059464 | -0.0082137 | 0.065488 | -61.0382 | 62.1231 | -61.2167 | -61.0931 | 61.8668 | 0.073242 | -0.086975 | 0.22888 | 62.0911 | -61.1801 | -0.33874 | 0.073242 | -0.16022 | -0.21515 | -0.18311 | -0.30212 | 0.041198 | 0.17853 | 60.791 | 61.1069 | 122.7448 | 123.0011 | -0.16022 | 122.9691 | 60.9512 | -0.30212 | 123.0011 | -0.16022 | 60.9512 | 122.7448 | 122.9691 | -123.2666 | -123.23
2639.7656 | 123.1842 | -60.8963 | 62.0728 | -0.13374 | -0.0088568 | -0.010916 | 0.0011386 | 0.057969 | -0.0060775 | 0.065488 | -60.9787 | 62.1185 | -61.1938 | -61.0703 | 61.8759 | 0.10986 | 0.004578 | 0.28381 | 62.1231 | -61.171 | -0.29755 | 0.045776 | -0.082398 | -0.17395 | -0.19684 | -0.27466 | 0.050354 | 0.21515 | 60.9009 | 61.1801 | 122.7722 | 123.0148 | -0.082398 | 123.0194 | 61.0062 | -0.27466 | 123.0148 | -0.082398 | 61.0062 | 122.7722 | 123.0194 | -123.2666 | -123.2437
2640.7656 | 123.1934 | -60.9009 | 62.0544 | 0.1104 | -0.005866 | -0.01348 | 0.0013522 | 0.058396 | -0.0071457 | 0.063138 | -61.0611 | 62.1002 | -61.2167 | -61.1252 | 61.8164 | 0.018311 | -0.086975 | 0.17395 | 62.1048 | -61.1755 | -0.31586 | 0.045777 | -0.16022 | -0.2243 | -0.23804 | -0.27466 | 0.050354 | 0.15564 | 60.8139 | 61.0748 | 122.7173 | 123.0011 | -0.16022 | 123.0057 | 60.9192 | -0.27466 | 123.0011 | -0.16022 | 60.9192 | 122.7173 | 123.0057 | -123.2712 | -123.23
2641.7656 | 123.2483 | -60.8963 | 62.0361 | -0.034561 | -0.0069342 | -0.010916 | 0.0032748 | 0.05861 | -0.0050095 | 0.069547 | -61.0016 | 62.1048 | -61.2122 | -61.0657 | 61.8805 | 0.10071 | -0.09613 | 0.27008 | 62.1002 | -61.1389 | -0.31586 | 0.068664 | -0.10529 | -0.16937 | -0.15564 | -0.24262 | 0.064087 | 0.21057 | 60.8002 | 61.1664 | 122.7768 | 123.0011 | -0.10529 | 122.9965 | 60.997 | -0.24262 | 123.0011 | -0.10529 | 60.997 | 122.7768 | 122.9965 | -123.2483 | -123.175
2642.7656 | 123.1567 | -60.9009 | 62.0178 | 0.23247 | -0.0056524 | -0.011771 | 0.010752 | 0.060746 | -0.0056503 | 0.066984 | -61.0428 | 62.1368 | -61.2579 | -61.1572 | 61.7615 | -0.045776 | -0.10071 | 0.07782 | 62.0773 | -61.2167 | -0.35706 | 0.11902 | -0.14191 | -0.25635 | -0.25635 | -0.31586 | 0.05951 | 0.21515 | 60.8002 | 60.9787 | 122.6624 | 123.0377 | -0.14191 | 122.9782 | 60.8551 | -0.31586 | 123.0377 | -0.14191 | 60.8551 | 122.6624 | 122.9782 | -123.2758 | -123.2346
2643.7656 | 123.175 | -60.8826 | 62.0361 | 0.095139 | -0.0073614 | -0.014761 | -0.0033476 | 0.059891 | -0.0071457 | 0.06442 | -61.0657 | 62.1231 | -61.2167 | -61.1206 | 61.8027 | -0.009155 | -0.050354 | 0.17395 | 62.0865 | -61.2167 | -0.33417 | 0.086975 | -0.18311 | -0.23804 | -0.23346 | -0.33417 | 0.050354 | 0.15106 | 60.8322 | 61.0565 | 122.6852 | 123.0057 | -0.18311 | 122.9691 | 60.8734 | -0.33417 | 123.0057 | -0.18311 | 60.8734 | 122.6852 | 122.9691 | -123.2529 | -123.2529
2644.7656 | 123.2346 | -60.8826 | 61.9904 | 0.28587 | -0.0041572 | -0.0081389 | 0.0030612 | 0.059251 | -0.0035141 | 0.069761 | -60.997 | 62.0911 | -61.2305 | -61.2396 | 61.9125 | 0.082397 | -0.15564 | 0.20142 | 62.0819 | -61.1755 | -0.3479 | 0.10071 | -0.11444 | -0.35706 | -0.077819 | -0.29297 | 0.091553 | 0.23346 | 60.7269 | 61.084 | 122.7951 | 122.9736 | -0.11444 | 122.9645 | 60.965 | -0.29297 | 122.9736 | -0.11444 | 60.965 | 122.7951 | 122.9645 | -123.2208 | -123.1659
2645.7656 | 123.2483 | -60.8597 | 62.0499 | -0.019302 | -0.0097114 | -0.015189 | 0.00049764 | 0.056473 | -0.0058639 | 0.064847 | -60.997 | 62.1277 | -61.1893 | -61.0519 | 61.8988 | 0.11444 | -0.086975 | 0.28839 | 62.0819 | -61.171 | -0.32959 | 0.07782 | -0.13733 | -0.19226 | -0.15106 | -0.31128 | 0.032043 | 0.19226 | 60.7727 | 61.1481 | 122.7585 | 122.9874 | -0.13733 | 122.9416 | 60.9741 | -0.31128 | 122.9874 | -0.13733 | 60.9741 | 122.7585 | 122.9416 | -123.2391 | -123.2208
2646.7812 | 123.2391 | -60.8917 | 61.9858 | 0.23247 | -0.0060798 | -0.0060027 | 0.0039156 | 0.058396 | -0.0047957 | 0.067838 | -61.0062 | 62.1002 | -61.2396 | -61.0886 | 61.8347 | 0.032043 | -0.1831 | 0.18768 | 62.0453 | -61.2076 | -0.3479 | 0.11444 | -0.11444 | -0.19684 | -0.15106 | -0.31586 | 0.059509 | 0.23346 | 60.7086 | 61.0794 | 122.7264 | 122.9919 | -0.11444 | 122.937 | 60.9238 | -0.31586 | 122.9919 | -0.11444 | 60.9238 | 122.7264 | 122.937 | -123.2254 | -123.1934
2647.7656 | 123.23 | -60.9009 | 62.0041 | 0.0035856 | -0.008216 | -0.0040801 | 0.003702 | 0.059464 | -0.0056503 | 0.065488 | -60.9833 | 62.1323 | -61.2213 | -61.0886 | 61.8759 | 0.045776 | -0.20599 | 0.1831 | 62.0636 | -61.203 | -0.32043 | 0.12817 | -0.082397 | -0.18768 | -0.12817 | -0.30212 | 0.05951 | 0.23804 | 60.6949 | 61.084 | 122.7768 | 123.0331 | -0.082397 | 122.9645 | 60.9467 | -0.30212 | 123.0331 | -0.082397 | 60.9467 | 122.7768 | 122.9645 | -123.2254 | -123.2071
2648.7656 | 123.1888 | -60.8826 | 62.0361 | 0.18669 | -0.0060798 | -0.010275 | 0.0028476 | 0.059037 | -0.0065047 | 0.066343 | -61.0428 | 62.1048 | -61.2396 | -61.1298 | 61.8256 | 0.022888 | -0.11444 | 0.15106 | 62.0956 | -61.2167 | -0.35706 | 0.068664 | -0.16022 | -0.24719 | -0.21057 | -0.33417 | 0.059509 | 0.19684 | 60.7681 | 61.0336 | 122.7081 | 122.9874 | -0.16022 | 122.9782 | 60.9055 | -0.33417 | 122.9874 | -0.16022 | 60.9055 | 122.7081 | 122.9782 | -123.2758 | -123.2529
2649.7656 | 123.1796 | -60.8826 | 62.0499 | 0.13329 | -0.0071478 | -0.010703 | 0.0030612 | 0.061173 | -0.0047957 | 0.067197 | -61.0565 | 62.1094 | -61.2122 | -61.1435 | 61.8256 | 0.022888 | -0.11902 | 0.15106 | 62.1048 | -61.1801 | -0.32959 | 0.059509 | -0.17395 | -0.26093 | -0.2243 | -0.29755 | 0.054931 | 0.15564 | 60.7635 | 61.0336 | 122.7081 | 122.9919 | -0.17395 | 122.9874 | 60.9055 | -0.29755 | 122.9919 | -0.17395 | 60.9055 | 122.7081 | 122.9874 | -123.262 | -123.23
2650.7812 | 123.175 | -60.9055 | 62.0407 | 0.1638 | -0.0062934 | -0.010062 | 0.002634 | 0.05861 | -0.0052231 | 0.068693 | -61.0428 | 62.1094 | -61.2167 | -61.1114 | 61.821 | 0.013733 | -0.11902 | 0.15564 | 62.059 | -61.2167 | -0.31128 | 0.068665 | -0.13733 | -0.20599 | -0.21973 | -0.31128 | 0.018311 | 0.17395 | 60.7864 | 61.0611 | 122.7264 | 123.0148 | -0.13733 | 122.9645 | 60.9192 | -0.31128 | 123.0148 | -0.13733 | 60.9192 | 122.7264 | 122.9645 | -123.2574 | -123.2574
2651.7812 | 123.23 | -60.9009 | 62.0453 | 0.034104 | -0.0071478 | -0.0087799 | 0.0011386 | 0.057328 | -0.0054367 | 0.067838 | -61.0245 | 62.1231 | -61.2122 | -61.0703 | 61.8805 | 0.07782 | -0.091553 | 0.2243 | 62.0728 | -61.1893 | -0.31128 | 0.07782 | -0.1236 | -0.16937 | -0.16479 | -0.28839 | 0.027466 | 0.18768 | 60.8093 | 61.1252 | 122.7814 | 123.024 | -0.1236 | 122.9736 | 60.9787 | -0.28839 | 123.024 | -0.1236 | 60.9787 | 122.7814 | 122.9736 | -123.2574 | -123.2346
2652.7812 | 123.23 | -60.8505 | 62.0453 | -0.04982 | -0.0090704 | -0.015616 | 0.00092504 | 0.057114 | -0.0050095 | 0.067411 | -61.0016 | 62.1048 | -61.2213 | -61.0565 | 61.8988 | 0.11902 | -0.082397 | 0.29297 | 62.0773 | -61.1893 | -0.37079 | 0.059509 | -0.15106 | -0.20599 | -0.14648 | -0.33875 | 0.032044 | 0.21973 | 60.7681 | 61.1435 | 122.7493 | 122.9553 | -0.15106 | 122.9279 | 60.9695 | -0.33875 | 122.9553 | -0.15106 | 60.9695 | 122.7493 | 122.9279 | -123.2666 | -123.2346
2653.7656 | 123.2483 | -60.8917 | 62.027 | -0.04219 | -0.009284 | -0.012412 | 0.0058382 | 0.060746 | -0.0052231 | 0.068693 | -60.9879 | 62.0956 | -61.2305 | -61.0657 | 61.853 | 0.036621 | -0.19684 | 0.17853 | 62.0682 | -61.171 | -0.33874 | 0.068664 | -0.09613 | -0.17395 | -0.17395 | -0.27923 | 0.041198 | 0.24262 | 60.6949 | 61.0703 | 122.7448 | 122.9874 | -0.09613 | 122.9599 | 60.9283 | -0.27923 | 122.9874 | -0.09613 | 60.9283 | 122.7448 | 122.9599 | -123.2574 | -123.1979
2654.7656 | 123.2208 | -60.878 | 62.0132 | 1.3921 | -0.0090704 | -0.0083527 | 0.005411 | 0.059891 | -0.0054367 | 0.067624 | -60.9421 | 62.1048 | -61.1938 | -61.0657 | 61.8668 | 0.022888 | -0.2243 | 0.16479 | 62.059 | -61.2076 | -0.31586 | 0.091552 | -0.064087 | -0.18768 | -0.14648 | -0.32959 | 0.045776 | 0.25177 | 60.6537 | 61.0428 | 122.7448 | 122.9828 | -0.064087 | 122.937 | 60.9009 | -0.32959 | 122.9828 | -0.064087 | 60.9009 | 122.7448 | 122.937 | -123.2071 | -123.2208
2655.7656 | 123.1888 | -60.8917 | 62.027 | 0.19432 | -0.009284 | -0.012839 | 0.0034884 | 0.060746 | -0.0037277 | 0.068052 | -61.0474 | 62.114 | -61.2442 | -61.1206 | 61.8118 | 0.004578 | -0.1236 | 0.14648 | 62.0636 | -61.2396 | -0.35248 | 0.086975 | -0.15564 | -0.22888 | -0.21515 | -0.3479 | 0.036621 | 0.19684 | 60.7681 | 61.0382 | 122.7036 | 123.0057 | -0.15564 | 122.9553 | 60.8963 | -0.3479 | 123.0057 | -0.15564 | 60.8963 | 122.7036 | 122.9553 | -123.2712 | -123.2666
2656.7656 | 123.2162 | -60.8734 | 62.0407 | 0.27824 | -0.0071478 | -0.011343 | 0.0075472 | 0.060319 | -0.0071457 | 0.065275 | -60.9787 | 62.1094 | -61.2442 | -61.0794 | 61.9492 | -0.009155 | -0.40741 | 0.26093 | 62.0544 | -61.2076 | -0.37079 | 0.068665 | -0.10529 | -0.20599 | -0.091552 | -0.33417 | 0.013733 | 0.2655 | 60.466 | 61.1343 | 122.8226 | 122.9828 | -0.10529 | 122.9279 | 60.8643 | -0.33417 | 122.9828 | -0.10529 | 60.8643 | 122.8226 | 122.9279 | -123.2849 | -123.2483
2657.7656 | 123.2208 | -60.8871 | 61.9949 | 0.25536 | -0.0073614 | -0.010489 | 0.0034884 | 0.060319 | -0.0054367 | 0.067197 | -60.997 | 62.1094 | -61.2259 | -61.0886 | 61.8439 | 0.032043 | -0.20142 | 0.17853 | 62.059 | -61.2122 | -0.33874 | 0.11444 | -0.10986 | -0.20142 | -0.15106 | -0.32501 | 0.064087 | 0.22888 | 60.6857 | 61.0657 | 122.731 | 122.9965 | -0.10986 | 122.9462 | 60.9192 | -0.32501 | 122.9965 | -0.10986 | 60.9192 | 122.731 | 122.9462 | -123.2208 | -123.2071
2658.7812 | 123.2117 | -60.9009 | 62.0224 | -0.12611 | -0.0071478 | -0.013266 | 0.0013522 | 0.06096 | -0.0065047 | 0.06677 | -60.9558 | 62.1277 | -61.1755 | -61.0428 | 61.908 | 0.40283 | -0.045776 | 0.09613 | 62.1368 | -61.1526 | -0.27466 | 0.10529 | -0.054932 | -0.14191 | -0.11444 | -0.25177 | 0.11444 | 0.21973 | 60.8551 | 60.997 | 122.8088 | 123.0286 | -0.054932 | 123.0377 | 61.3037 | -0.25177 | 123.0286 | -0.054932 | 61.3037 | 122.8088 | 123.0377 | -123.1979 | -123.175
2659.7812 | 123.1934 | -60.8963 | 62.0132 | 0.20195 | -0.006507 | -0.0092071 | 0.0032748 | 0.060746 | -0.0075729 | 0.066556 | -60.997 | 62.1277 | -61.2213 | -61.1069 | 61.8301 | 0.018311 | -0.17853 | 0.16022 | 62.0636 | -61.1938 | -0.32501 | 0.11444 | -0.10071 | -0.21057 | -0.18311 | -0.29755 | 0.050354 | 0.2243 | 60.7178 | 61.0565 | 122.7264 | 123.024 | -0.10071 | 122.9599 | 60.9146 | -0.29755 | 123.024 | -0.10071 | 60.9146 | 122.7264 | 122.9599 | -123.2346 | -123.2071
2660.7656 | 123.2208 | -60.9192 | 62.0087 | 0.19432 | -0.0069342 | -0.010703 | 0.0034884 | 0.06096 | -0.0077865 | 0.06677 | -60.9879 | 62.1048 | -61.2259 | -61.0931 | 61.8301 | 0.027466 | -0.1831 | 0.16022 | 62.1002 | -61.1847 | -0.3067 | 0.09613 | -0.068665 | -0.17395 | -0.17853 | -0.2655 | 0.091553 | 0.23804 | 60.7361 | 61.0794 | 122.7493 | 123.024 | -0.068665 | 123.0194 | 60.9467 | -0.2655 | 123.024 | -0.068665 | 60.9467 | 122.7493 | 123.0194 | -123.2346 | -123.1934
2661.7812 | 123.1888 | -60.8826 | 62.0316 | 0.072251 | -0.008216 | -0.0098479 | 0.003702 | 0.056473 | -0.0037277 | 0.067624 | -61.0336 | 62.1323 | -61.2122 | -61.1481 | 61.821 | -0.013733 | -0.068665 | 0.16479 | 62.0865 | -61.2076 | -0.32959 | 0.10071 | -0.15106 | -0.2655 | -0.21057 | -0.32501 | 0.054932 | 0.17853 | 60.8139 | 61.0474 | 122.7036 | 123.0148 | -0.15106 | 122.9691 | 60.8688 | -0.32501 | 123.0148 | -0.15106 | 60.8688 | 122.7036 | 122.9691 | -123.2437 | -123.2391
2662.7656 | 123.1659 | -60.9055 | 62.0316 | 0.26299 | -0.0062934 | -0.010062 | 0.0077608 | 0.061814 | -0.0052231 | 0.067411 | -61.0611 | 62.1368 | -61.2717 | -61.1298 | 61.7889 | -0.041199 | -0.11902 | 0.09613 | 62.0819 | -61.2213 | -0.36621 | 0.10529 | -0.15564 | -0.2243 | -0.24262 | -0.31586 | 0.050354 | 0.21057 | 60.7864 | 61.0016 | 122.6944 | 123.0423 | -0.15564 | 122.9874 | 60.8643 | -0.31586 | 123.0423 | -0.15564 | 60.8643 | 122.6944 | 122.9874 | -123.3032 | -123.2529
2663.7656 | 123.1476 | -60.9283 | 62.0361 | 0.21721 | -0.0052252 | -0.0085663 | 0.0058382 | 0.060746 | -0.0052231 | 0.067838 | -61.0565 | 62.1506 | -61.2625 | -61.1572 | 61.7615 | -0.045776 | -0.11444 | 0.073242 | 62.0636 | -61.2442 | -0.33417 | 0.11444 | -0.12817 | -0.22888 | -0.27466 | -0.31586 | 0.027466 | 0.20599 | 60.8139 | 61.0016 | 122.6898 | 123.0789 | -0.12817 | 122.9919 | 60.8826 | -0.31586 | 123.0789 | -0.12817 | 60.8826 | 122.6898 | 122.9919 | -123.2986 | -123.2803
2664.7656 | 123.2162 | -60.9055 | 62.0224 | 0.24773 | -0.0056524 | -0.0094207 | 0.0058382 | 0.063096 | -0.0052231 | 0.067624 | -61.0291 | 62.1689 | -61.2442 | -61.1252 | 61.7981 | -0.004578 | -0.16479 | 0.14191 | 62.0636 | -61.2213 | -0.33875 | 0.14648 | -0.1236 | -0.21973 | -0.2243 | -0.31586 | 0.041199 | 0.21515 | 60.7407 | 61.0474 | 122.7036 | 123.0743 | -0.1236 | 122.9691 | 60.9009 | -0.31586 | 123.0743 | -0.1236 | 60.9009 | 122.7036 | 122.9691 | -123.2666 | -123.2437
2665.7656 | 123.2208 | -60.8871 | 62.0407 | 0.2401 | -0.0062934 | -0.010275 | 0.0051974 | 0.058182 | -0.0058639 | 0.06677 | -61.0382 | 62.1643 | -61.2442 | -61.1343 | 61.8164 | -0.004578 | -0.16479 | 0.14191 | 62.059 | -61.235 | -0.35706 | 0.1236 | -0.15106 | -0.24719 | -0.2243 | -0.3479 | 0.018311 | 0.20599 | 60.7224 | 61.0291 | 122.7036 | 123.0515 | -0.15106 | 122.9462 | 60.8826 | -0.3479 | 123.0515 | -0.15106 | 60.8826 | 122.7036 | 122.9462 | -123.2849 | -123.2758
2666.7656 | 123.1934 | -60.9055 | 62.0453 | 0.2401 | -0.0054388 | -0.01113 | 0.0056246 | 0.061173 | -0.0047957 | 0.067197 | -61.0474 | 62.1826 | -61.235 | -61.1389 | 61.7981 | -0.022888 | -0.1236 | 0.10986 | 62.0956 | -61.235 | -0.32959 | 0.13733 | -0.14191 | -0.23346 | -0.24719 | -0.32959 | 0.050354 | 0.18768 | 60.7819 | 61.0153 | 122.7036 | 123.0881 | -0.14191 | 123.0011 | 60.8826 | -0.32959 | 123.0881 | -0.14191 | 60.8826 | 122.7036 | 123.0011 | -123.2803 | -123.2803
2667.7656 | 123.1842 | -60.9329 | 62.027 | 0.21721 | -0.0050116 | -0.011984 | 0.0084018 | 0.060532 | -0.0039413 | 0.067838 | -61.0611 | 62.1689 | -61.2579 | -61.1618 | 61.7844 | -0.050354 | -0.10986 | 0.10071 | 62.1185 | -61.2579 | -0.32501 | 0.14191 | -0.12817 | -0.22888 | -0.24262 | -0.32501 | 0.091552 | 0.19684 | 60.8231 | 61.0336 | 122.7173 | 123.1018 | -0.12817 | 123.0515 | 60.8826 | -0.32501 | 123.1018 | -0.12817 | 60.8826 | 122.7173 | 123.0515 | -123.2849 | -123.2849
2668.7656 | 123.1155 | -60.9329 | 62.0361 | 0.18669 | -0.0045844 | -0.010916 | 0.0047702 | 0.063096 | -0.0043685 | 0.065275 | -61.0565 | 62.1735 | -61.2534 | -61.1618 | 61.7661 | -0.059509 | -0.064087 | 0.064087 | 62.1277 | -61.2305 | -0.32044 | 0.13733 | -0.1236 | -0.22888 | -0.27008 | -0.29755 | 0.091553 | 0.19684 | 60.8688 | 60.997 | 122.699 | 123.1064 | -0.1236 | 123.0606 | 60.8734 | -0.29755 | 123.1064 | -0.1236 | 60.8734 | 122.699 | 123.0606 | -123.2895 | -123.2666
2669.7656 | 123.1567 | -60.9467 | 62.0544 | 0.064621 | -0.0052252 | -0.0094207 | 0.0045566 | 0.063737 | -0.0054367 | 0.066984 | -61.0977 | 62.2101 | -61.2442 | -61.1893 | 61.7752 | -0.045776 | -0.036621 | 0.059509 | 62.1002 | -61.2534 | -0.29755 | 0.15564 | -0.15106 | -0.24262 | -0.27923 | -0.3067 | 0.045777 | 0.14648 | 60.91 | 61.0062 | 122.7219 | 123.1567 | -0.15106 | 123.0469 | 60.9009 | -0.3067 | 123.1567 | -0.15106 | 60.9009 | 122.7219 | 123.0469 | -123.2986 | -123.3078
2670.7656 | 123.143 | -60.9329 | 62.0499 | 2.094 | -0.003089 | -0.014121 | 0.0045566 | 0.063309 | -0.0056503 | 0.065488 | -60.91 | 62.1735 | -61.2717 | -61.1847 | 61.7798 | -0.045776 | -0.018311 | 0.041199 | 62.1094 | -61.2213 | -0.33875 | 0.1236 | 0.022888 | -0.25177 | -0.27008 | -0.28839 | 0.059509 | 0.36163 | 60.9146 | 60.9741 | 122.7127 | 123.1064 | 0.022888 | 123.0423 | 60.8871 | -0.28839 | 123.1064 | 0.022888 | 60.8871 | 122.7127 | 123.0423 | -123.3215 | -123.2712
2671.7656 | 123.143 | -60.9238 | 62.0316 | 0.22484 | -0.0054388 | -0.0094207 | 0.0049838 | 0.062455 | -0.0052231 | 0.070188 | -61.0611 | 62.2055 | -61.2671 | -61.1801 | 61.7798 | -0.054932 | -0.073242 | 0.07782 | 62.0499 | -61.2534 | -0.34332 | 0.17395 | -0.13733 | -0.25635 | -0.25177 | -0.32959 | 0.018311 | 0.20599 | 60.8505 | 61.0016 | 122.7036 | 123.1293 | -0.13733 | 122.9736 | 60.8688 | -0.32959 | 123.1293 | -0.13733 | 60.8688 | 122.7036 | 122.9736 | -123.2986 | -123.2849
2672.7656 | 123.1293 | -60.9467 | 62.0224 | 0.18669 | -0.0050116 | -0.010489 | 0.0056246 | 0.0616 | -0.0045821 | 0.068479 | -61.0703 | 62.1735 | -61.2534 | -61.1847 | 61.7569 | -0.036621 | -0.045776 | 0.064087 | 62.146 | -61.2213 | -0.3067 | 0.15106 | -0.1236 | -0.23804 | -0.2655 | -0.27466 | 0.1236 | 0.18311 | 60.9009 | 61.0107 | 122.7036 | 123.1201 | -0.1236 | 123.0927 | 60.91 | -0.27466 | 123.1201 | -0.1236 | 60.91 | 122.7036 | 123.0927 | -123.2758 | -123.2437
2673.7656 | 123.1247 | -60.9238 | 62.0682 | 0.095139 | -0.0035162 | -0.0066437 | 0.0058382 | 0.060319 | -0.0052231 | 0.068479 | -61.0794 | 62.2284 | -61.2671 | -61.1847 | 61.7386 | -0.050354 | -0.027466 | 0.064087 | 62.0956 | -61.2625 | -0.34332 | 0.16022 | -0.15564 | -0.26093 | -0.32959 | -0.33875 | 0.027466 | 0.18768 | 60.8963 | 60.9879 | 122.6624 | 123.1522 | -0.15564 | 123.0194 | 60.8734 | -0.33875 | 123.1522 | -0.15564 | 60.8734 | 122.6624 | 123.0194 | -123.3353 | -123.3307
2674.7656 | 123.1522 | -60.91 | 62.0544 | 0.20958 | -0.0050116 | -0.0064301 | 0.0041292 | 0.062455 | -0.0037277 | 0.067838 | -61.0291 | 62.1735 | -61.2671 | -61.2122 | 61.7615 | -0.018311 | 0.009155 | 0.082397 | 62.146 | -61.2442 | -0.35706 | 0.11902 | -0.11902 | -0.30212 | -0.29297 | -0.33417 | 0.091553 | 0.23804 | 60.9192 | 60.9924 | 122.6715 | 123.0835 | -0.11902 | 123.056 | 60.8917 | -0.33417 | 123.0835 | -0.11902 | 60.8917 | 122.6715 | 123.056 | -123.3215 | -123.2986
2675.7656 | 123.1659 | -60.9146 | 61.9675 | 0.2401 | -0.0056524 | -0.011557 | 0.0015658 | 0.062882 | -0.0043685 | 0.068693 | -61.0016 | 62.1368 | -61.2488 | -61.1069 | 61.8576 | 0.041199 | -0.19226 | 0.14648 | 62.0407 | -61.2167 | -0.33417 | 0.16937 | -0.086975 | -0.19226 | -0.10986 | -0.30212 | 0.073242 | 0.24719 | 60.7224 | 61.0611 | 122.7722 | 123.0515 | -0.086975 | 122.9553 | 60.9558 | -0.30212 | 123.0515 | -0.086975 | 60.9558 | 122.7722 | 122.9553 | -123.2162 | -123.1842
2676.7656 | 123.111 | -60.9238 | 62.0728 | 0.19432 | -0.0062934 | -0.0092071 | 0.0066928 | 0.061387 | -0.0026595 | 0.067838 | -61.0931 | 62.2192 | -61.2671 | -61.2259 | 61.7157 | -0.07782 | -0.013733 | 0.068665 | 62.1094 | -61.2442 | -0.34332 | 0.14648 | -0.16937 | -0.30212 | -0.35706 | -0.32044 | 0.036621 | 0.17395 | 60.91 | 60.9924 | 122.6395 | 123.143 | -0.16937 | 123.0331 | 60.8459 | -0.32044 | 123.143 | -0.16937 | 60.8459 | 122.6395 | 123.0331 | -123.3398 | -123.317
2677.7656 | 123.1018 | -60.9375 | 62.0636 | 0.15617 | -0.005866 | -0.0057891 | 0.0049838 | 0.062882 | -0.0026595 | 0.06912 | -61.0565 | 62.2604 | -61.2442 | -61.2076 | 61.7477 | -0.032043 | 0 | 0.050354 | 62.114 | -61.2808 | -0.3067 | 0.19684 | -0.11902 | -0.27008 | -0.31586 | -0.34332 | 0.050354 | 0.18768 | 60.9375 | 60.9879 | 122.6852 | 123.1979 | -0.11902 | 123.0515 | 60.9055 | -0.34332 | 123.1979 | -0.11902 | 60.9055 | 122.6852 | 123.0515 | -123.3078 | -123.3444
2678.7656 | 123.1796 | -60.965 | 62.0682 | 0.19432 | -0.0045844 | -0.010489 | 0.0045566 | 0.06096 | -0.0030869 | 0.06677 | -61.0977 | 62.2238 | -61.2534 | -61.2213 | 61.7569 | -0.073242 | -0.009155 | -0.11444 | 62.0865 | -61.2946 | -0.28839 | 0.15564 | -0.13275 | -0.25635 | -0.31128 | -0.32959 | 0.018311 | 0.15564 | 60.9558 | 60.8505 | 122.7219 | 123.1888 | -0.13275 | 123.0515 | 60.8917 | -0.32959 | 123.1888 | -0.13275 | 60.8917 | 122.7219 | 123.0515 | -123.3215 | -123.3627
2679.7656 | 123.0743 | -60.9329 | 62.0636 | 0.14092 | -0.0069342 | -0.0087799 | 0.0041292 | 0.062028 | -0.0052231 | 0.064847 | -61.0886 | 62.2421 | -61.2625 | -61.2213 | 61.7294 | -0.073242 | 0.022888 | 0.054932 | 62.1002 | -61.2762 | -0.32959 | 0.17853 | -0.15564 | -0.28839 | -0.33417 | -0.34332 | 0.036621 | 0.17395 | 60.9558 | 60.9879 | 122.6624 | 123.175 | -0.15564 | 123.0331 | 60.8597 | -0.34332 | 123.175 | -0.15564 | 60.8597 | 122.6624 | 123.0331 | -123.3261 | -123.3398
2680.7656 | 123.111 | -60.9329 | 62.1002 | 0.072251 | -0.0041572 | -0.0098479 | 0.0032748 | 0.060319 | -0.0052231 | 0.06912 | -61.0703 | 62.2467 | -61.2488 | -61.203 | 61.7477 | -0.050354 | 0.013733 | 0.064087 | 62.1231 | -61.2717 | -0.31586 | 0.14648 | -0.13733 | -0.27008 | -0.35248 | -0.33875 | 0.022888 | 0.17853 | 60.9467 | 60.997 | 122.6807 | 123.1796 | -0.13733 | 123.056 | 60.8826 | -0.33875 | 123.1796 | -0.13733 | 60.8826 | 122.6807 | 123.056 | -123.349 | -123.3719
2681.7656 | 123.1064 | -60.9329 | 62.0407 | 0.11803 | -0.0022346 | -0.010703 | 0.005411 | 0.060532 | -0.0067185 | 0.067624 | -61.0519 | 62.2421 | -61.2442 | -61.1801 | 61.7615 | -0.032043 | 0.032043 | 0.10986 | 62.1185 | -61.2808 | -0.31128 | 0.20142 | -0.11902 | -0.24719 | -0.27923 | -0.3479 | 0.07782 | 0.19226 | 60.965 | 61.0428 | 122.6944 | 123.175 | -0.11902 | 123.0515 | 60.9009 | -0.3479 | 123.175 | -0.11902 | 60.9009 | 122.6944 | 123.0515 | -123.2849 | -123.3215
2682.7656 | 123.1384 | -60.9375 | 62.0361 | 0.18669 | -0.0050116 | -0.012198 | 0.0022066 | 0.062455 | -0.0056503 | 0.067624 | -61.0703 | 62.233 | -61.2534 | -61.2122 | 61.7752 | -0.073242 | -0.050354 | 0.054932 | 62.1323 | -61.2534 | -0.31586 | 0.19684 | -0.13275 | -0.27466 | -0.26093 | -0.31586 | 0.09613 | 0.18311 | 60.8871 | 60.9924 | 122.7127 | 123.1705 | -0.13275 | 123.0698 | 60.8643 | -0.31586 | 123.1705 | -0.13275 | 60.8643 | 122.7127 | 123.0698 | -123.2895 | -123.2895
2683.7656 | 123.1476 | -60.9192 | 62.0544 | -0.11848 | -0.0037298 | -0.0098479 | 0.0064792 | 0.062669 | -0.0030869 | 0.066129 | -61.0016 | 62.233 | -61.2442 | -61.1435 | 61.7981 | 0.045776 | 0.032043 | 0.16479 | 62.1597 | -61.2579 | -0.32501 | 0.17853 | -0.082398 | -0.2243 | -0.25635 | -0.33875 | 0.10529 | 0.24262 | 60.9512 | 61.084 | 122.7173 | 123.1522 | -0.082398 | 123.0789 | 60.965 | -0.33875 | 123.1522 | -0.082398 | 60.965 | 122.7173 | 123.0789 | -123.2986 | -123.3124
2684.7656 | 123.1522 | -60.8734 | 62.0636 | -0.034561 | -0.0041572 | -0.011343 | 0.0047702 | 0.060105 | -0.0030869 | 0.063779 | -61.0153 | 62.2238 | -61.2579 | -61.1435 | 61.8256 | 0.050354 | 0.041199 | 0.19684 | 62.1323 | -61.2625 | -0.38452 | 0.16022 | -0.14191 | -0.27008 | -0.23804 | -0.3891 | 0.068664 | 0.24262 | 60.9146 | 61.0703 | 122.699 | 123.0972 | -0.14191 | 123.0057 | 60.9238 | -0.3891 | 123.0972 | -0.14191 | 60.9238 | 122.699 | 123.0057 | -123.3215 | -123.3261
2685.7656 | 123.1705 | -60.9146 | 62.0453 | 0.026474 | -0.0041572 | -0.010062 | 0.0077608 | 0.063737 | -0.0047957 | 0.065702 | -61.0062 | 62.2559 | -61.2579 | -61.1572 | 61.7935 | 0.027466 | 0.009155 | 0.15564 | 62.1506 | -61.2534 | -0.34332 | 0.21057 | -0.091553 | -0.24262 | -0.25177 | -0.33875 | 0.10529 | 0.25177 | 60.9238 | 61.0703 | 122.7081 | 123.1705 | -0.091553 | 123.0652 | 60.9421 | -0.33875 | 123.1705 | -0.091553 | 60.9421 | 122.7081 | 123.0652 | -123.3032 | -123.2986
2686.7656 | 123.1522 | -60.9283 | 62.0544 | -0.04219 | -0.0043708 | -0.0096343 | 0.0049838 | 0.062455 | -0.0058639 | 0.068906 | -61.0107 | 62.2421 | -61.235 | -61.1481 | 61.8118 | 0.050354 | 0.018311 | 0.17395 | 62.146 | -61.2579 | -0.3067 | 0.18768 | -0.082397 | -0.21973 | -0.24261 | -0.32959 | 0.091553 | 0.2243 | 60.9467 | 61.1023 | 122.7402 | 123.1705 | -0.082397 | 123.0743 | 60.9787 | -0.32959 | 123.1705 | -0.082397 | 60.9787 | 122.7402 | 123.0743 | -123.2895 | -123.3124
2687.7656 | 123.1705 | -60.8917 | 62.0728 | -0.026932 | -0.0033026 | -0.010062 | 0.0056246 | 0.063309 | -0.0028731 | 0.066984 | -61.0062 | 62.233 | -61.235 | -61.1755 | 61.8805 | 0.064087 | 0.064087 | 0.21057 | 62.1552 | -61.2167 | -0.34332 | 0.16022 | -0.11444 | -0.28381 | -0.19226 | -0.32501 | 0.082397 | 0.22888 | 60.9558 | 61.1023 | 122.7722 | 123.1247 | -0.11444 | 123.0469 | 60.9558 | -0.32501 | 123.1247 | -0.11444 | 60.9558 | 122.7722 | 123.0469 | -123.3078 | -123.2895
2688.7656 | 123.1613 | -60.91 | 62.059 | -0.04982 | -0.0045844 | -0.010489 | 0.0051974 | 0.063737 | -0.0056503 | 0.065702 | -60.9879 | 62.2192 | -61.2259 | -61.1206 | 61.8301 | 0.068665 | 0.027466 | 0.20599 | 62.1643 | -61.2259 | -0.31586 | 0.16022 | -0.07782 | -0.21057 | -0.22888 | -0.31586 | 0.10529 | 0.23804 | 60.9375 | 61.116 | 122.7402 | 123.1293 | -0.07782 | 123.0743 | 60.9787 | -0.31586 | 123.1293 | -0.07782 | 60.9787 | 122.7402 | 123.0743 | -123.2849 | -123.2849
2689.7656 | 123.1155 | -60.9329 | 62.027 | 0.087509 | -0.004798 | -0.012839 | 0.0049838 | 0.063523 | -0.0037277 | 0.066556 | -61.0611 | 62.2238 | -61.2442 | -61.2167 | 61.7386 | -0.050354 | 0.018311 | 0.050354 | 62.1094 | -61.2946 | -0.31128 | 0.19684 | -0.12817 | -0.28381 | -0.28839 | -0.36163 | 0.082397 | 0.18311 | 60.9512 | 60.9833 | 122.6715 | 123.1567 | -0.12817 | 123.0423 | 60.8826 | -0.36163 | 123.1567 | -0.12817 | 60.8826 | 122.6715 | 123.0423 | -123.2712 | -123.3215
2690.7656 | 123.1064 | -60.9192 | 62.0773 | 0.11803 | -0.0050116 | -0.0074981 | 0.0064792 | 0.0616 | -0.0028731 | 0.068052 | -61.0519 | 62.2238 | -61.235 | -61.1801 | 61.7661 | -0.045776 | 0.027466 | 0.10529 | 62.1323 | -61.2534 | -0.31586 | 0.14648 | -0.13275 | -0.26093 | -0.31128 | -0.33417 | 0.054931 | 0.1831 | 60.9467 | 61.0245 | 122.6852 | 123.143 | -0.13275 | 123.0515 | 60.8734 | -0.33417 | 123.143 | -0.13275 | 60.8734 | 122.6852 | 123.0515 | -123.3124 | -123.3307
2691.7656 | 123.175 | -60.9238 | 62.0773 | -0.149 | -0.0069342 | -0.013266 | 0.0034884 | 0.060746 | -0.0050095 | 0.06677 | -61.0336 | 62.2421 | -61.2442 | -61.1343 | 61.8164 | 0.045776 | 0.086975 | 0.21973 | 62.146 | -61.2717 | -0.32044 | 0.16479 | -0.10986 | -0.21057 | -0.26093 | -0.3479 | 0.068664 | 0.21057 | 61.0107 | 61.1435 | 122.7402 | 123.1659 | -0.10986 | 123.0698 | 60.9695 | -0.3479 | 123.1659 | -0.10986 | 60.9695 | 122.7402 | 123.0698 | -123.3215 | -123.349
2692.7656 | 123.1567 | -60.9009 | 62.0636 | -0.087967 | -0.0080024 | -0.011557 | 0.0051974 | 0.062241 | -0.0050095 | 0.067624 | -61.0245 | 62.2467 | -61.2396 | -61.1252 | 61.8347 | 0.068665 | 0.032043 | 0.21057 | 62.1552 | -61.235 | -0.33874 | 0.1831 | -0.1236 | -0.2243 | -0.22888 | -0.33417 | 0.091552 | 0.21515 | 60.9329 | 61.1115 | 122.7356 | 123.1476 | -0.1236 | 123.056 | 60.9695 | -0.33417 | 123.1476 | -0.1236 | 60.9695 | 122.7356 | 123.056 | -123.3032 | -123.2986
2693.7656 | 123.1842 | -60.9055 | 62.0865 | -0.12611 | -0.0060798 | -0.010489 | 0.002634 | 0.061814 | -0.0073593 | 0.066556 | -61.0245 | 62.233 | -61.2259 | -61.1389 | 61.8347 | 0.059509 | 0.054932 | 0.21973 | 62.1597 | -61.2213 | -0.32043 | 0.14648 | -0.11902 | -0.23346 | -0.25177 | -0.31586 | 0.073242 | 0.20142 | 60.9604 | 61.1252 | 122.7402 | 123.1384 | -0.11902 | 123.0652 | 60.965 | -0.31586 | 123.1384 | -0.11902 | 60.965 | 122.7402 | 123.0652 | -123.3124 | -123.3078
2694.7656 | 123.1934 | -60.9055 | 62.0865 | -0.15663 | -0.0056524 | -0.0072845 | 0.0028476 | 0.063096 | -0.0054367 | 0.067838 | -61.0153 | 62.2192 | -61.2259 | -61.1435 | 61.8073 | 0.059509 | 0.086975 | 0.20599 | 62.1643 | -61.2305 | -0.32043 | 0.13275 | -0.10986 | -0.23804 | -0.27924 | -0.32501 | 0.07782 | 0.21057 | 60.9924 | 61.1115 | 122.7127 | 123.1247 | -0.10986 | 123.0698 | 60.965 | -0.32501 | 123.1247 | -0.10986 | 60.965 | 122.7127 | 123.0698 | -123.3124 | -123.317
2695.7656 | 123.1384 | -60.9146 | 62.0819 | -0.095596 | -0.0069342 | -0.011771 | 0.0028476 | 0.063523 | -0.0082137 | 0.067411 | -61.0382 | 62.2101 | -61.235 | -61.1572 | 61.8073 | 0.059509 | 0.10986 | 0.20142 | 62.1964 | -61.235 | -0.32043 | 0.12817 | -0.1236 | -0.24262 | -0.27466 | -0.32043 | 0.11444 | 0.19684 | 61.0245 | 61.116 | 122.7219 | 123.1247 | -0.1236 | 123.111 | 60.9741 | -0.32043 | 123.1247 | -0.1236 | 60.9741 | 122.7219 | 123.111 | -123.317 | -123.317
2696.7656 | 123.1476 | -60.9009 | 62.0407 | 0.026474 | -0.0033026 | -0.010489 | 0.0062656 | 0.063523 | -0.0065047 | 0.067411 | -60.9924 | 62.2055 | -61.2396 | -61.1481 | 61.7798 | 0.022888 | 0.009155 | 0.17853 | 62.1689 | -61.2396 | -0.33874 | 0.1648 | -0.091553 | -0.24719 | -0.26093 | -0.33874 | 0.12817 | 0.24719 | 60.91 | 61.0794 | 122.6807 | 123.1064 | -0.091553 | 123.0698 | 60.9238 | -0.33874 | 123.1064 | -0.091553 | 60.9238 | 122.6807 | 123.0698 | -123.2803 | -123.2803
2697.7656 | 123.111 | -60.9329 | 62.0956 | 0.018845 | -0.006507 | -0.011557 | 0.00092504 | 0.062028 | -0.0060775 | 0.068693 | -61.0474 | 62.2101 | -61.235 | -61.1618 | 61.7981 | 0.032043 | 0.12817 | 0.18768 | 62.1918 | -61.235 | -0.30212 | 0.11444 | -0.11444 | -0.22888 | -0.29755 | -0.30212 | 0.09613 | 0.18768 | 61.0611 | 61.1206 | 122.731 | 123.143 | -0.11444 | 123.1247 | 60.965 | -0.30212 | 123.143 | -0.11444 | 60.965 | 122.731 | 123.1247 | -123.3307 | -123.3307
2698.7656 | 123.1247 | -60.9146 | 62.0911 | -0.16426 | -0.0060798 | -0.0089935 | 0.0034884 | 0.060746 | -0.0065047 | 0.065916 | -61.0657 | 62.2192 | -61.2259 | -61.1801 | 61.7661 | 0.004578 | 0.11902 | 0.16937 | 62.1368 | -61.2625 | -0.31128 | 0.12817 | -0.15106 | -0.2655 | -0.32501 | -0.3479 | 0.045777 | 0.16022 | 61.0336 | 61.084 | 122.6807 | 123.1338 | -0.15106 | 123.0515 | 60.9192 | -0.3479 | 123.1338 | -0.15106 | 60.9192 | 122.6807 | 123.0515 | -123.317 | -123.3536
2699.7656 | 123.1476 | -60.9283 | 62.0819 | -0.16426 | -0.007575 | -0.014121 | 0.001993 | 0.062028 | -0.0050095 | 0.066343 | -61.0611 | 62.2284 | -61.2305 | -61.1572 | 61.7981 | 0.036621 | 0.11444 | 0.18768 | 62.1735 | -61.2579 | -0.30212 | 0.14648 | -0.13275 | -0.22888 | -0.28381 | -0.32959 | 0.091553 | 0.16937 | 61.0428 | 61.116 | 122.7264 | 123.1567 | -0.13275 | 123.1018 | 60.965 | -0.32959 | 123.1567 | -0.13275 | 60.965 | 122.7264 | 123.1018 | -123.3124 | -123.3398
2700.7656 | 123.1247 | -60.91 | 62.0956 | -0.019302 | -0.0073614 | -0.014761 | 0.0015658 | 0.058396 | -0.0045821 | 0.064847 | -61.0519 | 62.2192 | -61.235 | -61.1618 | 61.7935 | 0.027466 | 0.11444 | 0.18768 | 62.1597 | -61.2396 | -0.32501 | 0.1236 | -0.14191 | -0.25177 | -0.30212 | -0.32959 | 0.064087 | 0.1831 | 61.0245 | 61.0977 | 122.7036 | 123.1293 | -0.14191 | 123.0698 | 60.9375 | -0.32959 | 123.1293 | -0.14191 | 60.9375 | 122.7036 | 123.0698 | -123.3307 | -123.3353
2701.7656 | 123.0927 | -60.9192 | 62.0956 | 0.4232 | -0.0052252 | -0.0085663 | 0.003702 | 0.058823 | -0.0058639 | 0.064634 | -61.1343 | 62.1964 | -61.2259 | -61.1755 | 61.8073 | 0.022888 | 0.14191 | 0.1831 | 62.1872 | -61.2167 | -0.3067 | 0.10071 | -0.21515 | -0.25635 | -0.28839 | -0.29755 | 0.091553 | 0.091553 | 61.0611 | 61.1023 | 122.7264 | 123.1155 | -0.21515 | 123.1064 | 60.9421 | -0.29755 | 123.1155 | -0.21515 | 60.9421 | 122.7264 | 123.1064 | -123.3215 | -123.3124
2702.7656 | 123.0881 | -60.9192 | 62.0728 | -0.21004 | -0.0086432 | -0.012625 | -0.00057036 | 0.056046 | -0.0067185 | 0.067624 | -61.0794 | 62.2055 | -61.2259 | -61.2717 | 61.6882 | -0.041199 | 0.11444 | 0.16937 | 62.1597 | -61.2259 | -0.3067 | 0.13275 | -0.16022 | -0.35248 | -0.38452 | -0.3067 | 0.086975 | 0.14648 | 61.0336 | 61.0886 | 122.6074 | 123.1247 | -0.16022 | 123.0789 | 60.878 | -0.3067 | 123.1247 | -0.16022 | 60.878 | 122.6074 | 123.0789 | -123.2986 | -123.2986
2703.7656 | 123.1384 | -60.9009 | 62.0407 | 0.026474 | -0.005866 | -0.01348 | 0.0058382 | 0.062669 | -0.0075729 | 0.06442 | -60.9879 | 62.1735 | -61.2442 | -61.1114 | 61.8256 | 0.050354 | 0.027466 | 0.20599 | 62.1643 | -61.2259 | -0.34332 | 0.13275 | -0.086975 | -0.21057 | -0.21515 | -0.32501 | 0.1236 | 0.25635 | 60.9283 | 61.1069 | 122.7264 | 123.0743 | -0.086975 | 123.0652 | 60.9512 | -0.32501 | 123.0743 | -0.086975 | 60.9512 | 122.7264 | 123.0652 | -123.2849 | -123.2666
2704.7656 | 123.1018 | -60.9055 | 62.0911 | -0.15663 | -0.004798 | -0.011343 | -0.0027066 | 0.057114 | -0.0067185 | 0.066984 | -61.0703 | 62.1872 | -61.2167 | -61.1664 | 61.7889 | 0.041199 | 0.1236 | 0.19684 | 62.1872 | -61.2259 | -0.31128 | 0.096131 | -0.16479 | -0.26093 | -0.30212 | -0.32043 | 0.096131 | 0.14648 | 61.0291 | 61.1023 | 122.6944 | 123.0927 | -0.16479 | 123.0927 | 60.9467 | -0.32043 | 123.0927 | -0.16479 | 60.9467 | 122.6944 | 123.0927 | -123.3078 | -123.317
2705.7656 | 123.0972 | -60.9146 | 62.0819 | -0.11085 | -0.007575 | -0.01348 | 0.00071144 | 0.060105 | -0.0056503 | 0.06677 | -61.0428 | 62.1918 | -61.2167 | -61.1435 | 61.8027 | 0.036621 | 0.12817 | 0.19226 | 62.1964 | -61.1938 | -0.30212 | 0.10986 | -0.12817 | -0.22888 | -0.27924 | -0.27924 | 0.11444 | 0.17395 | 61.0428 | 61.1069 | 122.7173 | 123.1064 | -0.12817 | 123.111 | 60.9512 | -0.27924 | 123.1064 | -0.12817 | 60.9512 | 122.7173 | 123.111 | -123.2986 | -123.2758
2706.7656 | 123.0927 | -60.9009 | 62.0956 | -0.149 | -0.0086432 | -0.011343 | 0.0032748 | 0.058396 | -0.0056503 | 0.065916 | -60.9787 | 62.233 | -61.235 | -61.1664 | 61.7798 | 0 | 0.14191 | 0.20142 | 62.1597 | -61.2305 | -0.33417 | 0.13733 | -0.07782 | -0.2655 | -0.31586 | -0.32959 | 0.064087 | 0.25635 | 61.0428 | 61.1023 | 122.6807 | 123.1338 | -0.07782 | 123.0606 | 60.9009 | -0.32959 | 123.1338 | -0.07782 | 60.9009 | 122.6807 | 123.0606 | -123.3307 | -123.3261
2707.7656 | 123.0927 | -60.9283 | 62.0911 | -0.19478 | -0.0056524 | -0.01348 | 0.0011386 | 0.058823 | -0.0082137 | 0.065061 | -61.0611 | 62.2101 | -61.2259 | -61.0245 | 61.702 | -0.013733 | 0.068665 | 0.17853 | 62.1964 | -61.2122 | -0.29755 | 0.11902 | -0.13275 | -0.09613 | -0.3891 | -0.28381 | 0.10529 | 0.16479 | 60.997 | 61.1069 | 122.6303 | 123.1384 | -0.13275 | 123.1247 | 60.9146 | -0.28381 | 123.1384 | -0.13275 | 60.9146 | 122.6303 | 123.1247 | -123.317 | -123.3032
2708.7656 | 123.1659 | -60.8871 | 62.0956 | -0.15663 | -0.0067206 | -0.0098479 | 0.0039156 | 0.059891 | -0.0047957 | 0.065488 | -61.0519 | 62.1735 | -61.2534 | -61.1481 | 61.7752 | 0.045776 | 0.12817 | 0.19684 | 62.1964 | -61.2122 | -0.36621 | 0.07782 | -0.16479 | -0.26093 | -0.32043 | -0.32501 | 0.10071 | 0.20142 | 61.0153 | 61.084 | 122.6624 | 123.0606 | -0.16479 | 123.0835 | 60.9329 | -0.32501 | 123.0606 | -0.16479 | 60.9329 | 122.6624 | 123.0835 | -123.349 | -123.3078
2709.7656 | 123.1613 | -60.8917 | 62.0819 | -0.20241 | -0.0077888 | -0.01113 | -0.0027066 | 0.05626 | -0.0084273 | 0.066343 | -61.0062 | 62.1414 | -61.235 | -61.0977 | 61.8393 | 0.10071 | 0.018311 | 0.27924 | 62.146 | -61.203 | -0.34332 | 0.059509 | -0.11444 | -0.20599 | -0.24262 | -0.31128 | 0.064087 | 0.22888 | 60.91 | 61.171 | 122.731 | 123.0331 | -0.11444 | 123.0377 | 60.9924 | -0.31128 | 123.0331 | -0.11444 | 60.9924 | 122.731 | 123.0377 | -123.317 | -123.2849
2710.7656 | 123.1522 | -60.91 | 62.1002 | -0.11085 | -0.0069342 | -0.01348 | 0.0041292 | 0.060746 | -0.0071457 | 0.065488 | -60.9879 | 62.1872 | -61.2305 | -61.0886 | 61.8301 | 0.059509 | 0.022888 | 0.21515 | 62.1826 | -61.203 | -0.32043 | 0.086975 | -0.07782 | -0.17853 | -0.27008 | -0.29297 | 0.082397 | 0.24262 | 60.9329 | 61.1252 | 122.7402 | 123.0972 | -0.07782 | 123.0927 | 60.9695 | -0.29297 | 123.0972 | -0.07782 | 60.9695 | 122.7402 | 123.0927 | -123.3307 | -123.3032
2711.7656 | 123.1018 | -60.8963 | 62.0865 | -0.18715 | -0.0062934 | -0.014121 | 0.00071144 | 0.059891 | -0.0052231 | 0.066984 | -61.0199 | 62.1872 | -61.1755 | -61.1572 | 61.7935 | 0.068665 | 0.11902 | 0.18768 | 62.1735 | -61.203 | -0.27924 | 0.10071 | -0.1236 | -0.26093 | -0.29297 | -0.3067 | 0.086975 | 0.15564 | 61.0153 | 61.084 | 122.6898 | 123.0835 | -0.1236 | 123.0698 | 60.965 | -0.3067 | 123.0835 | -0.1236 | 60.965 | 122.6898 | 123.0698 | -123.262 | -123.2895
2712.7656 | 123.1064 | -60.9009 | 62.0682 | -0.17952 | -0.0069342 | -0.011557 | 0.0011386 | 0.059678 | -0.0052231 | 0.065061 | -61.0703 | 62.2009 | -61.2122 | -61.1801 | 61.9354 | 0.21515 | 0.027466 | 0.11444 | 62.178 | -61.2396 | -0.31128 | 0.13275 | -0.16937 | -0.27924 | -0.13275 | -0.33874 | 0.10986 | 0.14191 | 60.9283 | 61.0153 | 122.8363 | 123.1018 | -0.16937 | 123.0789 | 61.116 | -0.33874 | 123.1018 | -0.16937 | 61.116 | 122.8363 | 123.0789 | -123.2803 | -123.3078
2713.7812 | 123.0835 | -60.9283 | 62.059 | 0.19432 | -0.0045844 | -0.011771 | 0.0034884 | 0.060319 | -0.0052231 | 0.065916 | -60.9512 | 62.1643 | -61.2625 | -61.1893 | 61.7294 | -0.036621 | 0 | 0.07782 | 62.146 | -61.2305 | -0.33417 | 0.10529 | -0.022888 | -0.26093 | -0.32959 | -0.30212 | 0.086975 | 0.31128 | 60.9283 | 61.0062 | 122.6578 | 123.0927 | -0.022888 | 123.0743 | 60.8917 | -0.30212 | 123.0927 | -0.022888 | 60.8917 | 122.6578 | 123.0743 | -123.3215 | -123.2895
2714.7656 | 123.1155 | -60.9238 | 62.1002 | -0.149 | -0.008216 | -0.016257 | -0.00057036 | 0.061387 | -0.0045821 | 0.065702 | -61.0794 | 62.1872 | -61.2213 | -61.1481 | 61.7935 | 0.018311 | 0.11902 | 0.19684 | 62.1552 | -61.2076 | -0.29755 | 0.086975 | -0.15564 | -0.2243 | -0.3067 | -0.28381 | 0.054931 | 0.14191 | 61.0428 | 61.1206 | 122.7173 | 123.111 | -0.15564 | 123.0789 | 60.9421 | -0.28381 | 123.111 | -0.15564 | 60.9421 | 122.7173 | 123.0789 | -123.3215 | -123.3078
2715.7656 | 123.1201 | -60.9146 | 62.1094 | -0.15663 | -0.0088568 | -0.0083527 | 0.0011386 | 0.05861 | -0.0026595 | 0.06677 | -61.0565 | 62.1689 | -61.203 | -61.1481 | 61.8073 | 0.036621 | 0.11444 | 0.21515 | 62.1643 | -61.1984 | -0.28839 | 0.059509 | -0.14191 | -0.23346 | -0.30212 | -0.28381 | 0.054932 | 0.14648 | 61.0291 | 61.1298 | 122.7219 | 123.0835 | -0.14191 | 123.0789 | 60.9512 | -0.28381 | 123.0835 | -0.14191 | 60.9512 | 122.7219 | 123.0789 | -123.3124 | -123.3078
2716.7656 | 123.1293 | -60.9009 | 62.0911 | -0.19478 | -0.0067206 | -0.012625 | 0.0028476 | 0.060105 | -0.0052231 | 0.066984 | -61.0291 | 62.1277 | -61.2167 | -61.1252 | 61.8439 | 0.054932 | 0.091553 | 0.2243 | 62.178 | -61.1755 | -0.31586 | 0.036622 | -0.12817 | -0.2243 | -0.24719 | -0.27466 | 0.086976 | 0.18768 | 60.9924 | 61.1252 | 122.7448 | 123.0286 | -0.12817 | 123.0789 | 60.9558 | -0.27466 | 123.0286 | -0.12817 | 60.9558 | 122.7448 | 123.0789 | -123.3078 | -123.2666
2717.7656 | 123.1613 | -60.9009 | 62.0636 | -0.12611 | -0.0080024 | -0.012198 | 0.0064792 | 0.061173 | -0.0080001 | 0.067197 | -61.0062 | 62.2009 | -61.2259 | -61.0931 | 61.8301 | 0.059509 | 0.054932 | 0.21515 | 62.1597 | -61.1984 | -0.32501 | 0.13733 | -0.10529 | -0.19226 | -0.23346 | -0.29755 | 0.09613 | 0.21973 | 60.9558 | 61.116 | 122.731 | 123.1018 | -0.10529 | 123.0606 | 60.9604 | -0.29755 | 123.1018 | -0.10529 | 60.9604 | 122.731 | 123.0606 | -123.2895 | -123.262
2718.7812 | 123.0743 | -60.9512 | 62.059 | 0.095139 | -0.0033026 | -0.010062 | 0.0069064 | 0.06096 | -0.0043685 | 0.066129 | -61.0657 | 62.1964 | -61.235 | -61.1893 | 61.7386 | -0.054932 | 0.004578 | 0.082397 | 62.1185 | -61.2488 | -0.28381 | 0.13733 | -0.11444 | -0.23804 | -0.32044 | -0.29755 | 0.059509 | 0.16937 | 60.9558 | 61.0336 | 122.6898 | 123.1476 | -0.11444 | 123.0698 | 60.8963 | -0.29755 | 123.1476 | -0.11444 | 60.8963 | 122.6898 | 123.0698 | -123.2941 | -123.3078
2719.7656 | 123.1247 | -60.9238 | 62.0819 | -0.17189 | -0.008216 | -0.013693 | 0.00028404 | 0.059037 | -0.0056503 | 0.06677 | -61.0886 | 62.2009 | -61.2442 | -61.1481 | 61.8073 | 0.041199 | 0.13733 | 0.20599 | 62.1643 | -61.2076 | -0.32044 | 0.11902 | -0.1648 | -0.2243 | -0.27466 | -0.28381 | 0.082398 | 0.15564 | 61.0611 | 61.1298 | 122.731 | 123.1247 | -0.1648 | 123.0881 | 60.965 | -0.28381 | 123.1247 | -0.1648 | 60.965 | 122.731 | 123.0881 | -123.3261 | -123.2895
2720.7656 | 123.111 | -60.9192 | 62.0911 | -0.24055 | -0.0084296 | -0.0089935 | 0.0011386 | 0.057328 | -0.0058639 | 0.065916 | -61.0565 | 62.178 | -61.2167 | -61.1435 | 61.8118 | 0.059509 | 0.10986 | 0.19226 | 62.1918 | -61.2076 | -0.29755 | 0.086976 | -0.13733 | -0.2243 | -0.27923 | -0.28839 | 0.10071 | 0.16022 | 61.0291 | 61.1115 | 122.731 | 123.0972 | -0.13733 | 123.111 | 60.9787 | -0.28839 | 123.0972 | -0.13733 | 60.9787 | 122.731 | 123.111 | -123.3078 | -123.2986
2721.7656 | 123.1293 | -60.9192 | 62.0773 | -0.14137 | -0.0071478 | -0.010062 | -0.00014316 | 0.059891 | -0.0069321 | 0.066984 | -61.0291 | 62.1414 | -61.2396 | -61.1343 | 61.8118 | 0.054932 | 0.10529 | 0.21973 | 62.1826 | -61.1847 | -0.32043 | 0.064086 | -0.10986 | -0.21515 | -0.2655 | -0.2655 | 0.10529 | 0.21057 | 61.0245 | 61.1389 | 122.731 | 123.0606 | -0.10986 | 123.1018 | 60.9741 | -0.2655 | 123.0606 | -0.10986 | 60.9741 | 122.731 | 123.1018 | -123.317 | -123.262
2722.7656 | 123.111 | -60.9009 | 62.0911 | -0.17189 | -0.0077888 | -0.013052 | 0.0015658 | 0.059037 | -0.0060775 | 0.067197 | -61.0199 | 62.1643 | -61.2076 | -61.1298 | 61.8256 | 0.041199 | 0.10071 | 0.2243 | 62.1552 | -61.1801 | -0.3067 | 0.073243 | -0.11902 | -0.22888 | -0.2655 | -0.27924 | 0.064087 | 0.18768 | 61.0016 | 61.1252 | 122.7264 | 123.0652 | -0.11902 | 123.056 | 60.9421 | -0.27924 | 123.0652 | -0.11902 | 60.9421 | 122.7264 | 123.056 | -123.2986 | -123.2712
2723.7812 | 123.0881 | -60.9009 | 62.059 | 0.1104 | -0.0052252 | -0.0068573 | 0.0079744 | 0.061387 | -0.0065047 | 0.066984 | -61.0016 | 62.1826 | -61.2259 | -61.1435 | 61.7706 | -0.018311 | 0.004578 | 0.11444 | 62.1643 | -61.2122 | -0.32501 | 0.1236 | -0.10071 | -0.24261 | -0.28839 | -0.31128 | 0.10529 | 0.2243 | 60.9055 | 61.0153 | 122.6715 | 123.0835 | -0.10071 | 123.0652 | 60.8826 | -0.31128 | 123.0835 | -0.10071 | 60.8826 | 122.6715 | 123.0652 | -123.2849 | -123.2712
2724.7656 | 123.1613 | -60.8917 | 62.0819 | -0.19478 | -0.0097114 | -0.0098479 | 0.0017794 | 0.057328 | -0.0062911 | 0.067411 | -61.0291 | 62.1735 | -61.203 | -61.1206 | 61.8301 | 0.068665 | 0.073242 | 0.22888 | 62.146 | -61.2122 | -0.31128 | 0.091553 | -0.13733 | -0.22888 | -0.25177 | -0.32043 | 0.064087 | 0.17395 | 60.965 | 61.1206 | 122.7219 | 123.0652 | -0.13733 | 123.0377 | 60.9604 | -0.32043 | 123.0652 | -0.13733 | 60.9604 | 122.7219 | 123.0377 | -123.2849 | -123.2941
2725.7656 | 123.1384 | -60.8734 | 62.0728 | -0.20241 | -0.008216 | -0.011771 | 0.001993 | 0.056901 | -0.0060775 | 0.067411 | -61.0016 | 62.1323 | -61.1801 | -61.1252 | 61.853 | 0.07782 | 0.07782 | 0.23804 | 62.1689 | -61.1984 | -0.3067 | 0.059509 | -0.12817 | -0.25177 | -0.21973 | -0.32501 | 0.09613 | 0.17853 | 60.9512 | 61.1114 | 122.7264 | 123.0057 | -0.12817 | 123.0423 | 60.9512 | -0.32501 | 123.0057 | -0.12817 | 60.9512 | 122.7264 | 123.0423 | -123.2529 | -123.2712
2726.7656 | 123.1155 | -60.9055 | 62.1002 | -0.20241 | -0.0086432 | -0.01113 | 0.0039156 | 0.060319 | -0.0054367 | 0.065275 | -61.0611 | 62.2147 | -61.235 | -61.1526 | 61.8118 | 0.041199 | 0.14648 | 0.20142 | 62.2009 | -61.2076 | -0.32959 | 0.11444 | -0.15564 | -0.24719 | -0.28839 | -0.30212 | 0.10071 | 0.17395 | 61.0519 | 61.1069 | 122.7173 | 123.1201 | -0.15564 | 123.1064 | 60.9467 | -0.30212 | 123.1201 | -0.15564 | 60.9467 | 122.7173 | 123.1064 | -123.3353 | -123.3078
2727.7656 | 123.0927 | -60.9055 | 62.0956 | -0.17189 | -0.0069342 | -0.01113 | 0.0017794 | 0.060319 | -0.0069321 | 0.067197 | -61.0611 | 62.1826 | -61.2213 | -61.1526 | 61.7935 | 0.045776 | 0.13733 | 0.19684 | 62.1872 | -61.1893 | -0.31586 | 0.086975 | -0.15564 | -0.24719 | -0.30212 | -0.28381 | 0.091553 | 0.16022 | 61.0428 | 61.1023 | 122.699 | 123.0881 | -0.15564 | 123.0927 | 60.9512 | -0.28381 | 123.0881 | -0.15564 | 60.9512 | 122.699 | 123.0927 | -123.317 | -123.2849
2728.7656 | 123.23 | -60.91 | 62.0132 | 0.19432 | -0.0080024 | -0.013907 | 0.0024202 | 0.059891 | -0.0058639 | 0.068052 | -61.0062 | 62.0956 | -61.2213 | -61.1114 | 61.8347 | 0.027466 | -0.19226 | 0.17395 | 62.0865 | -61.203 | -0.31128 | 0.082397 | -0.096131 | -0.20142 | -0.17853 | -0.29297 | 0.073242 | 0.21515 | 60.7178 | 61.084 | 122.7448 | 123.0057 | -0.096131 | 122.9965 | 60.9375 | -0.29297 | 123.0057 | -0.096131 | 60.9375 | 122.7448 | 122.9965 | -123.2346 | -123.2162
2729.7656 | 123.1567 | -60.9192 | 62.1185 | -0.14137 | -0.0073614 | -0.01348 | 0.0017794 | 0.05861 | -0.0062911 | 0.066129 | -61.0611 | 62.1689 | -61.2488 | -61.1435 | 61.7935 | 0.050354 | 0.11902 | 0.21515 | 62.1826 | -61.1893 | -0.32959 | 0.050354 | -0.14191 | -0.2243 | -0.32501 | -0.27008 | 0.064087 | 0.18768 | 61.0382 | 61.1343 | 122.7127 | 123.0881 | -0.14191 | 123.1018 | 60.9695 | -0.27008 | 123.0881 | -0.14191 | 60.9695 | 122.7127 | 123.1018 | -123.3673 | -123.3078
2730.7656 | 123.143 | -60.8917 | 62.0728 | -0.20241 | -0.009284 | -0.014975 | 0.0028476 | 0.059251 | -0.0073593 | 0.068265 | -61.0474 | 62.1506 | -61.2122 | -61.0886 | 61.7889 | 0.036621 | 0.11902 | 0.20142 | 62.1643 | -61.1847 | -0.32043 | 0.07782 | -0.15564 | -0.19684 | -0.28381 | -0.29297 | 0.091553 | 0.1648 | 61.0107 | 61.0931 | 122.6807 | 123.0423 | -0.15564 | 123.056 | 60.9283 | -0.29297 | 123.0423 | -0.15564 | 60.9283 | 122.6807 | 123.056 | -123.2849 | -123.2574
2731.7656 | 123.1476 | -60.8917 | 62.0956 | -0.17189 | -0.008216 | -0.013693 | 7.0444e-05 | 0.058396 | -0.0065047 | 0.066129 | -61.0062 | 62.1735 | -61.2167 | -61.1343 | 61.821 | 0.045776 | 0.1236 | 0.27466 | 62.1872 | -61.1847 | -0.32501 | 0.07782 | -0.11444 | -0.24261 | -0.27466 | -0.29297 | 0.091553 | 0.21057 | 61.0153 | 61.1664 | 122.7127 | 123.0652 | -0.11444 | 123.0789 | 60.9375 | -0.29297 | 123.0652 | -0.11444 | 60.9375 | 122.7127 | 123.0789 | -123.3124 | -123.2803
2732.7656 | 123.1338 | -60.9055 | 62.0956 | -0.20241 | -0.009925 | -0.0098479 | 0.0017794 | 0.060746 | -0.0058639 | 0.063566 | -61.0016 | 62.1323 | -61.203 | -61.1252 | 61.8301 | 0.073242 | 0.082397 | 0.23804 | 62.1552 | -61.1755 | -0.29755 | 0.036621 | -0.09613 | -0.21973 | -0.2655 | -0.27008 | 0.059509 | 0.20142 | 60.9879 | 61.1435 | 122.7356 | 123.0377 | -0.09613 | 123.0606 | 60.9787 | -0.27008 | 123.0377 | -0.09613 | 60.9787 | 122.7356 | 123.0606 | -123.2986 | -123.2712
2733.7656 | 123.1155 | -60.91 | 62.1094 | -0.20241 | -0.0080024 | -0.013693 | 0.0034884 | 0.05861 | -0.0071457 | 0.06677 | -61.0474 | 62.1826 | -61.235 | -61.1343 | 61.8073 | 0.041199 | 0.14648 | 0.19684 | 62.1735 | -61.1984 | -0.32501 | 0.073242 | -0.13733 | -0.2243 | -0.30212 | -0.28839 | 0.064087 | 0.18768 | 61.0565 | 61.1069 | 122.7173 | 123.0927 | -0.13733 | 123.0835 | 60.9512 | -0.28839 | 123.0927 | -0.13733 | 60.9512 | 122.7173 | 123.0835 | -123.3444 | -123.3078
2734.7656 | 123.1018 | -60.9055 | 62.0956 | -0.18715 | -0.0084296 | -0.0092071 | 0.0024202 | 0.059037 | -0.0041549 | 0.064634 | -61.0657 | 62.2101 | -61.2396 | -61.1481 | 61.8164 | 0.050354 | 0.13275 | 0.20599 | 62.1368 | -61.203 | -0.33417 | 0.11444 | -0.16022 | -0.24261 | -0.27924 | -0.29755 | 0.041199 | 0.17395 | 61.0382 | 61.1115 | 122.7219 | 123.1155 | -0.16022 | 123.0423 | 60.9558 | -0.29755 | 123.1155 | -0.16022 | 60.9558 | 122.7219 | 123.0423 | -123.3353 | -123.2986
2735.7656 | 123.1064 | -60.8917 | 62.114 | -0.11848 | -0.0080024 | -0.010062 | 0.0022066 | 0.060105 | -0.0080001 | 0.06677 | -61.0611 | 62.1597 | -61.2167 | -61.1298 | 61.7981 | 0.054932 | 0.1236 | 0.2243 | 62.1597 | -61.1893 | -0.32501 | 0.045776 | -0.16937 | -0.23804 | -0.31586 | -0.29755 | 0.045776 | 0.15564 | 61.0153 | 61.116 | 122.6898 | 123.0515 | -0.16937 | 123.0515 | 60.9467 | -0.29755 | 123.0515 | -0.16937 | 60.9467 | 122.6898 | 123.0515 | -123.3307 | -123.3032
2736.7656 | 123.1201 | -60.91 | 62.0682 | -0.20241 | -0.0067206 | -0.011984 | 0.0034884 | 0.0616 | -0.0094955 | 0.066556 | -61.0291 | 62.146 | -61.2259 | -61.1298 | 61.7844 | 0.054932 | 0.16937 | 0.20142 | 62.1826 | -61.1801 | -0.31586 | 0.07782 | -0.11902 | -0.21973 | -0.28381 | -0.27008 | 0.11444 | 0.19684 | 61.0794 | 61.1115 | 122.6944 | 123.056 | -0.11902 | 123.0927 | 60.965 | -0.27008 | 123.056 | -0.11902 | 60.965 | 122.6944 | 123.0927 | -123.2941 | -123.2483
2737.7656 | 123.175 | -60.91 | 62.0819 | -0.11848 | -0.0077888 | -0.010916 | 0.0069064 | 0.061173 | -0.0082137 | 0.068479 | -61.0062 | 62.178 | -61.235 | -61.116 | 61.8439 | 0.073242 | 0.045776 | 0.21515 | 62.1918 | -61.1893 | -0.32501 | 0.096131 | -0.096131 | -0.20599 | -0.23804 | -0.27924 | 0.10986 | 0.22888 | 60.9558 | 61.1252 | 122.7539 | 123.0881 | -0.096131 | 123.1018 | 60.9833 | -0.27924 | 123.0881 | -0.096131 | 60.9833 | 122.7539 | 123.1018 | -123.317 | -123.2712
2738.7656 | 123.175 | -60.8917 | 62.0636 | -0.21004 | -0.0067206 | -0.012839 | 0.00071144 | 0.059464 | -0.0073593 | 0.067411 | -61.0245 | 62.1506 | -61.1984 | -61.0977 | 61.853 | 0.10529 | 0.045776 | 0.2655 | 62.1414 | -61.2213 | -0.3067 | 0.086975 | -0.13275 | -0.20599 | -0.21057 | -0.32959 | 0.077819 | 0.17395 | 60.9375 | 61.1572 | 122.7448 | 123.0423 | -0.13275 | 123.0331 | 60.997 | -0.32959 | 123.0423 | -0.13275 | 60.997 | 122.7448 | 123.0331 | -123.262 | -123.2849
2739.7656 | 123.1842 | -60.8826 | 62.0865 | -0.17189 | -0.0071478 | -0.01113 | -0.00014316 | 0.059678 | -0.0073593 | 0.065061 | -61.0062 | 62.1597 | -61.1984 | -61.0748 | 61.8622 | 0.10529 | 0.032043 | 0.28381 | 62.1094 | -61.1938 | -0.31586 | 0.073242 | -0.1236 | -0.19226 | -0.2243 | -0.31128 | 0.022888 | 0.19226 | 60.9146 | 61.1664 | 122.7448 | 123.0423 | -0.1236 | 122.9919 | 60.9879 | -0.31128 | 123.0423 | -0.1236 | 60.9879 | 122.7448 | 122.9919 | -123.2849 | -123.2803
2740.7656 | 123.1155 | -60.9192 | 62.114 | -0.21004 | -0.009284 | -0.0094207 | 0.0017794 | 0.060532 | -0.0080001 | 0.065275 | -61.0199 | 62.1643 | -61.2259 | -61.1252 | 61.8301 | 0.054932 | 0.091553 | 0.20599 | 62.1689 | -61.203 | -0.3067 | 0.050354 | -0.10071 | -0.20599 | -0.28381 | -0.28381 | 0.054931 | 0.20599 | 61.0107 | 61.1252 | 122.7493 | 123.0835 | -0.10071 | 123.0881 | 60.9741 | -0.28381 | 123.0835 | -0.10071 | 60.9741 | 122.7493 | 123.0881 | -123.3398 | -123.317
2741.7656 | 123.1064 | -60.9055 | 62.0956 | -0.18715 | -0.008216 | -0.01348 | 0.00049764 | 0.059037 | -0.0065047 | 0.066343 | -61.0107 | 62.1185 | -61.2167 | -61.1114 | 61.8393 | 0.07782 | 0.086975 | 0.22888 | 62.1597 | -61.1664 | -0.31128 | 0.022888 | -0.10529 | -0.20599 | -0.25635 | -0.26093 | 0.064087 | 0.20599 | 60.9924 | 61.1343 | 122.7448 | 123.024 | -0.10529 | 123.0652 | 60.9833 | -0.26093 | 123.024 | -0.10529 | 60.9833 | 122.7448 | 123.0652 | -123.3124 | -123.262
2742.7656 | 123.1705 | -60.9146 | 62.0728 | -0.19478 | -0.0084296 | -0.012625 | -0.00035676 | 0.059891 | -0.0060775 | 0.066343 | -61.0062 | 62.114 | -61.203 | -61.1023 | 61.8484 | 0.09613 | 0.027466 | 0.27924 | 62.1277 | -61.1755 | -0.28839 | 0.041199 | -0.091553 | -0.18768 | -0.2243 | -0.26093 | 0.054932 | 0.19684 | 60.9421 | 61.1938 | 122.7631 | 123.0286 | -0.091553 | 123.0423 | 61.0107 | -0.26093 | 123.0286 | -0.091553 | 61.0107 | 122.7631 | 123.0423 | -123.2758 | -123.2483
2743.7656 | 123.175 | -60.8688 | 62.0728 | -0.16426 | -0.010352 | -0.013693 | 0.00071144 | 0.059037 | -0.0075729 | 0.065916 | -60.9924 | 62.114 | -61.2122 | -61.0703 | 61.8576 | 0.1236 | 0.009155 | 0.28839 | 62.1552 | -61.171 | -0.34332 | 0.041199 | -0.1236 | -0.20142 | -0.21515 | -0.30212 | 0.082397 | 0.21973 | 60.878 | 61.1572 | 122.7264 | 122.9828 | -0.1236 | 123.024 | 60.9924 | -0.30212 | 122.9828 | -0.1236 | 60.9924 | 122.7264 | 123.024 | -123.2849 | -123.2437
2744.7656 | 123.1155 | -60.9009 | 62.0773 | -0.12611 | -0.0067206 | -0.013266 | 0.0049838 | 0.060319 | -0.0077865 | 0.066556 | -61.0474 | 62.1826 | -61.2534 | -61.1298 | 61.8073 | 0.050354 | 0.11444 | 0.17395 | 62.1552 | -61.2076 | -0.35248 | 0.10529 | -0.14648 | -0.22888 | -0.27008 | -0.3067 | 0.077819 | 0.20599 | 61.0153 | 61.0748 | 122.7081 | 123.0835 | -0.14648 | 123.056 | 60.9512 | -0.3067 | 123.0835 | -0.14648 | 60.9512 | 122.7081 | 123.056 | -123.3307 | -123.2849
2745.7656 | 123.2254 | -60.878 | 62.0728 | -0.065079 | -0.009925 | -0.010489 | -0.00099756 | 0.061173 | -0.0065047 | 0.065916 | -60.9787 | 62.1002 | -61.203 | -61.0474 | 61.8851 | 0.13275 | -0.041199 | 0.31128 | 62.1323 | -61.1618 | -0.32501 | 0.027466 | -0.10071 | -0.16937 | -0.18768 | -0.28381 | 0.059509 | 0.2243 | 60.8368 | 61.1893 | 122.7631 | 122.9782 | -0.10071 | 123.0103 | 61.0107 | -0.28381 | 122.9782 | -0.10071 | 61.0107 | 122.7631 | 123.0103 | -123.2758 | -123.2346
2746.7656 | 123.2162 | -60.8551 | 62.0544 | -0.17189 | -0.0069342 | -0.016898 | 0.00028404 | 0.057328 | -0.0060775 | 0.065916 | -61.0748 | 62.1231 | -61.2167 | -61.0748 | 61.908 | 0.16022 | -0.059509 | 0.32959 | 62.0865 | -61.1526 | -0.36163 | 0.068665 | -0.21973 | -0.21973 | -0.14648 | -0.29755 | 0.032044 | 0.14191 | 60.7956 | 61.1847 | 122.7631 | 122.9782 | -0.21973 | 122.9416 | 61.0153 | -0.29755 | 122.9782 | -0.21973 | 61.0153 | 122.7631 | 122.9416 | -123.2712 | -123.2071
2747.7656 | 123.2117 | -60.8826 | 62.0499 | -0.13374 | -0.0097114 | -0.013693 | 0.002634 | 0.05861 | -0.0069321 | 0.065916 | -60.9833 | 62.1277 | -61.171 | -61.0519 | 61.8896 | 0.10986 | -0.004578 | 0.3067 | 62.1643 | -61.1755 | -0.28839 | 0.07782 | -0.10071 | -0.16937 | -0.16022 | -0.29297 | 0.11444 | 0.18768 | 60.878 | 61.1893 | 122.7722 | 123.0103 | -0.10071 | 123.0469 | 60.9924 | -0.29297 | 123.0103 | -0.10071 | 60.9924 | 122.7722 | 123.0469 | -123.2208 | -123.2254
2748.7656 | 123.1888 | -60.8734 | 62.0636 | -0.29396 | -0.0090704 | -0.01113 | 0.00071144 | 0.059037 | -0.0073593 | 0.066129 | -60.9604 | 62.0911 | -61.2167 | -61.0519 | 61.8942 | 0.11902 | -0.054932 | 0.29755 | 62.1094 | -61.1526 | -0.34332 | 0.027465 | -0.086975 | -0.17853 | -0.16937 | -0.27924 | 0.045776 | 0.25635 | 60.8185 | 61.171 | 122.7676 | 122.9645 | -0.086975 | 122.9828 | 60.9924 | -0.27924 | 122.9645 | -0.086975 | 60.9924 | 122.7676 | 122.9828 | -123.2803 | -123.2162
2749.7656 | 123.2208 | -60.8871 | 62.0407 | -0.18715 | -0.009284 | -0.021597 | 0.0011386 | 0.058396 | -0.0065047 | 0.066343 | -60.7452 | 62.1506 | -61.1893 | -61.0748 | 61.8805 | 0.13275 | -0.054932 | 0.31128 | 62.0865 | -61.1481 | -0.30212 | 0.10986 | 0.14191 | -0.18768 | -0.16022 | -0.26093 | 0.045777 | 0.44403 | 60.8322 | 61.1984 | 122.7676 | 123.0377 | 0.14191 | 122.9736 | 61.0199 | -0.26093 | 123.0377 | 0.14191 | 61.0199 | 122.7676 | 122.9736 | -123.23 | -123.1888
2750.7656 | 123.2071 | -60.8597 | 62.0407 | -0.149 | -0.010139 | -0.01348 | 0.00071144 | 0.058396 | -0.0062911 | 0.066984 | -60.9695 | 62.1002 | -61.203 | -61.0291 | 61.8896 | 0.13275 | 0.25177 | 0.64545 | 62.1643 | -61.1206 | -0.34332 | 0.05951 | -0.10986 | -0.16937 | -0.15106 | -0.26093 | 0.1236 | 0.23346 | 61.1114 | 61.5051 | 122.7493 | 122.9599 | -0.10986 | 123.024 | 60.9924 | -0.26093 | 122.9599 | -0.10986 | 60.9924 | 122.7493 | 123.024 | -123.2437 | -123.1613
2751.7656 | 123.1293 | -60.9192 | 62.1094 | -0.11085 | -0.0094976 | -0.014121 | 0.0017794 | 0.057114 | -0.0075729 | 0.065061 | -61.0245 | 62.1414 | -61.2076 | -61.1252 | 61.8073 | 0.050354 | 0.1236 | 0.21057 | 62.1689 | -61.1893 | -0.28839 | 0.032043 | -0.10529 | -0.20599 | -0.30212 | -0.27008 | 0.059509 | 0.18311 | 61.0428 | 61.1298 | 122.7264 | 123.0606 | -0.10529 | 123.0881 | 60.9695 | -0.27008 | 123.0606 | -0.10529 | 60.9695 | 122.7264 | 123.0881 | -123.317 | -123.2986
2752.7656 | 123.2529 | -60.8734 | 62.0499 | -0.04982 | -0.0071478 | -0.014761 | -0.001425 | 0.05626 | -0.0075729 | 0.065275 | -60.9924 | 62.0728 | -61.2076 | -61.0474 | 61.908 | 0.13733 | -0.11444 | 0.30212 | 62.1323 | -61.1481 | -0.33417 | 0.022888 | -0.11902 | -0.17395 | -0.14191 | -0.27466 | 0.082397 | 0.21515 | 60.759 | 61.1755 | 122.7814 | 122.9462 | -0.11902 | 123.0057 | 61.0107 | -0.27466 | 122.9462 | -0.11902 | 61.0107 | 122.7814 | 123.0057 | -123.2574 | -123.1979
2753.7656 | 123.2391 | -60.8688 | 62.0407 | -0.04982 | -0.0088568 | -0.015616 | 0.00028404 | 0.05626 | -0.0056503 | 0.067838 | -61.0153 | 62.0911 | -61.2167 | -61.0611 | 61.8851 | 0.10071 | -0.09613 | 0.27924 | 62.1094 | -61.1298 | -0.3479 | 0.050354 | -0.14649 | -0.19226 | -0.15564 | -0.26093 | 0.068665 | 0.20142 | 60.7727 | 61.1481 | 122.7539 | 122.9599 | -0.14649 | 122.9782 | 60.9695 | -0.26093 | 122.9599 | -0.14649 | 60.9695 | 122.7539 | 122.9782 | -123.2574 | -123.1705
2754.7656 | 123.2574 | -60.878 | 62.0453 | -0.0040434 | -0.0094976 | -0.01583 | -0.00078396 | 0.055405 | -0.0069321 | 0.068265 | -60.965 | 62.0911 | -61.1893 | -61.0291 | 61.9125 | 0.14191 | -0.073242 | 0.31128 | 62.0819 | -61.1389 | -0.31128 | 0.045776 | -0.086975 | -0.15106 | -0.13275 | -0.26093 | 0.036621 | 0.2243 | 60.8047 | 61.1893 | 122.7905 | 122.9691 | -0.086975 | 122.9599 | 61.0199 | -0.26093 | 122.9691 | -0.086975 | 61.0199 | 122.7905 | 122.9599 | -123.2346 | -123.1842
2755.7656 | 123.2391 | -60.8643 | 62.0407 | -0.065079 | -0.0060798 | -0.013052 | -0.00035676 | 0.057328 | -0.0086411 | 0.063779 | -60.9879 | 62.0956 | -61.2213 | -61.0382 | 61.8988 | 0.11902 | -0.09613 | 0.3067 | 62.1094 | -61.1526 | -0.35706 | 0.054932 | -0.1236 | -0.17395 | -0.14191 | -0.28839 | 0.068665 | 0.23346 | 60.7681 | 61.171 | 122.7631 | 122.9599 | -0.1236 | 122.9736 | 60.9833 | -0.28839 | 122.9599 | -0.1236 | 60.9833 | 122.7631 | 122.9736 | -123.262 | -123.1934
2756.7656 | 123.2712 | -60.8597 | 62.059 | -0.034561 | -0.009284 | -0.01647 | 7.0444e-05 | 0.060746 | -0.0067185 | 0.066129 | -61.0062 | 62.0636 | -61.2076 | -61.0703 | 61.8942 | 0.10986 | -0.082397 | 0.29755 | 62.0956 | -61.1389 | -0.3479 | 0.004578 | -0.14649 | -0.21057 | -0.16479 | -0.27924 | 0.036621 | 0.20142 | 60.7773 | 61.1572 | 122.7539 | 122.9233 | -0.14649 | 122.9553 | 60.9695 | -0.27924 | 122.9233 | -0.14649 | 60.9695 | 122.7539 | 122.9553 | -123.2666 | -123.1979
2757.7656 | 123.2437 | -60.8688 | 62.0361 | -0.04219 | -0.010139 | -0.01113 | 0.00049764 | 0.058396 | -0.0062911 | 0.063779 | -61.0107 | 62.0865 | -61.2076 | -61.0519 | 61.8622 | 0.10986 | -0.086975 | 0.27924 | 62.1185 | -61.1481 | -0.33875 | 0.050354 | -0.14191 | -0.18311 | -0.17395 | -0.27924 | 0.082397 | 0.19684 | 60.7819 | 61.1481 | 122.731 | 122.9553 | -0.14191 | 122.9874 | 60.9787 | -0.27924 | 122.9553 | -0.14191 | 60.9787 | 122.731 | 122.9874 | -123.2437 | -123.1842
2758.7656 | 123.1842 | -60.878 | 62.0682 | -0.19478 | -0.0090704 | -0.010489 | 0.0030612 | 0.058396 | -0.0077865 | 0.066343 | -60.9787 | 62.1048 | -61.2122 | -61.0703 | 61.8759 | 0.09613 | 0.022888 | 0.28381 | 62.1368 | -61.1526 | -0.33417 | 0.036621 | -0.10071 | -0.19226 | -0.19226 | -0.27466 | 0.068665 | 0.23346 | 60.9009 | 61.1618 | 122.7539 | 122.9828 | -0.10071 | 123.0148 | 60.9741 | -0.27466 | 122.9828 | -0.10071 | 60.9741 | 122.7539 | 123.0148 | -123.2803 | -123.2208
2759.7656 | 123.2254 | -60.878 | 62.027 | 0.018845 | -0.010566 | -0.015616 | 0.00092504 | 0.057755 | -0.0056503 | 0.067624 | -61.0382 | 62.0911 | -61.203 | -61.0977 | 61.8668 | 0.09613 | -0.09613 | 0.24261 | 62.1094 | -61.1481 | -0.32501 | 0.064086 | -0.16022 | -0.21973 | -0.16022 | -0.27008 | 0.082397 | 0.1648 | 60.7819 | 61.1206 | 122.7448 | 122.9691 | -0.16022 | 122.9874 | 60.9741 | -0.27008 | 122.9691 | -0.16022 | 60.9741 | 122.7448 | 122.9874 | -123.23 | -123.175
2760.7656 | 123.2346 | -60.8643 | 62.0361 | 0.034104 | -0.007575 | -0.011771 | -0.00035676 | 0.05626 | -0.0054367 | 0.067197 | -61.0336 | 62.0956 | -61.1847 | -61.0748 | 61.8393 | 0.064087 | -0.091553 | 0.24261 | 62.0865 | -61.1755 | -0.32043 | 0.059509 | -0.16937 | -0.21057 | -0.19684 | -0.31128 | 0.050354 | 0.15106 | 60.7727 | 61.1069 | 122.7036 | 122.9599 | -0.16937 | 122.9507 | 60.9283 | -0.31128 | 122.9599 | -0.16937 | 60.9283 | 122.7036 | 122.9507 | -123.2208 | -123.2117
2761.7656 | 123.2437 | -60.8963 | 62.0316 | -0.0040434 | -0.0067206 | -0.010916 | 0.00028404 | 0.056901 | -0.0065047 | 0.067838 | -61.0016 | 62.0682 | -61.2213 | -61.0565 | 61.8896 | 0.10986 | -0.091553 | 0.28381 | 62.1094 | -61.1481 | -0.32501 | 0.036621 | -0.10529 | -0.16022 | -0.14191 | -0.25177 | 0.07782 | 0.21973 | 60.8047 | 61.1801 | 122.7859 | 122.9645 | -0.10529 | 123.0057 | 61.0062 | -0.25177 | 122.9645 | -0.10529 | 61.0062 | 122.7859 | 123.0057 | -123.2529 | -123.1796
2762.7656 | 123.2437 | -60.878 | 62.0453 | 0.0035856 | -0.0084296 | -0.012412 | -0.00035676 | 0.056473 | -0.0082137 | 0.064207 | -61.0107 | 62.114 | -61.2167 | -61.0657 | 61.9034 | 0.086975 | -0.10071 | 0.2655 | 62.1277 | -61.1114 | -0.33874 | 0.068665 | -0.13275 | -0.18768 | -0.14191 | -0.23346 | 0.082398 | 0.20599 | 60.7773 | 61.1435 | 122.7814 | 122.9919 | -0.13275 | 123.0057 | 60.965 | -0.23346 | 122.9919 | -0.13275 | 60.965 | 122.7814 | 123.0057 | -123.262 | -123.1567
2763.7656 | 123.2254 | -60.8871 | 62.0499 | 0.041733 | -0.010779 | -0.013693 | -0.0020658 | 0.059251 | -0.0047957 | 0.065275 | -61.0016 | 62.0728 | -61.2167 | -61.0703 | 61.8805 | 0.07782 | -0.10986 | 0.2655 | 62.1048 | -61.1435 | -0.32959 | 0.022888 | -0.11444 | -0.1831 | -0.16937 | -0.25635 | 0.054931 | 0.21515 | 60.7773 | 61.1526 | 122.7676 | 122.9599 | -0.11444 | 122.9919 | 60.965 | -0.25635 | 122.9599 | -0.11444 | 60.965 | 122.7676 | 122.9919 | -123.2666 | -123.1934
2764.7656 | 123.2162 | -60.9009 | 62.0316 | 0.072251 | -0.0094976 | -0.011771 | -0.00099756 | 0.059251 | -0.0069321 | 0.06677 | -61.0199 | 62.0453 | -61.203 | -61.0703 | 61.8851 | 0.086975 | -0.091553 | 0.21515 | 62.1002 | -61.1252 | -0.30212 | 0.013733 | -0.11902 | -0.16937 | -0.14648 | -0.2243 | 0.068665 | 0.18311 | 60.8093 | 61.116 | 122.786 | 122.9462 | -0.11902 | 123.0011 | 60.9879 | -0.2243 | 122.9462 | -0.11902 | 60.9879 | 122.786 | 123.0011 | -123.2346 | -123.1567
2765.7656 | 123.2208 | -60.8917 | 62.0728 | -0.13374 | -0.009284 | -0.010916 | 0.0017794 | 0.059251 | -0.0077865 | 0.065488 | -60.9741 | 62.114 | -61.203 | -61.0291 | 61.8942 | 0.13275 | -0.041199 | 0.29297 | 62.0956 | -61.1343 | -0.31128 | 0.041199 | -0.082397 | -0.13733 | -0.17853 | -0.24261 | 0.022888 | 0.22888 | 60.8505 | 61.1847 | 122.786 | 123.0057 | -0.082397 | 122.9874 | 61.0245 | -0.24261 | 123.0057 | -0.082397 | 61.0245 | 122.786 | 122.9874 | -123.2758 | -123.2071
2766.7656 | 123.2071 | -60.878 | 62.0544 | 0.11803 | -0.0094976 | -0.010703 | -0.00078396 | 0.060319 | -0.0071457 | 0.064207 | -61.0382 | 62.0682 | -61.2442 | -61.0931 | 61.8484 | 0.041199 | -0.09613 | 0.21057 | 62.1414 | -61.1343 | -0.36621 | 0.013733 | -0.16022 | -0.21515 | -0.20599 | -0.25635 | 0.086975 | 0.20599 | 60.7819 | 61.0886 | 122.7264 | 122.9462 | -0.16022 | 123.0194 | 60.9192 | -0.25635 | 122.9462 | -0.16022 | 60.9192 | 122.7264 | 123.0194 | -123.2986 | -123.1888
2767.7656 | 123.2117 | -60.8826 | 62.0316 | 0.095139 | -0.009925 | -0.014334 | -0.001425 | 0.057969 | -0.0045821 | 0.066556 | -61.0748 | 62.0728 | -61.235 | -61.0977 | 61.8164 | 0.036621 | -0.09613 | 0.18768 | 62.1094 | -61.1572 | -0.35248 | 0.041199 | -0.19226 | -0.21515 | -0.21515 | -0.27466 | 0.07782 | 0.16022 | 60.7864 | 61.0703 | 122.699 | 122.9553 | -0.19226 | 122.9919 | 60.9192 | -0.27466 | 122.9553 | -0.19226 | 60.9192 | 122.699 | 122.9919 | -123.2666 | -123.1888
2768.7656 | 123.2071 | -60.8734 | 62.0407 | 0.064621 | -0.0067206 | -0.012625 | -0.0018522 | 0.059037 | -0.0056503 | 0.065061 | -61.0107 | 62.1002 | -61.2122 | -61.0657 | 61.8622 | 0.091553 | -0.09613 | 0.24719 | 62.1094 | -61.1298 | -0.33875 | 0.05951 | -0.13733 | -0.19226 | -0.17853 | -0.25635 | 0.068665 | 0.20142 | 60.7773 | 61.1206 | 122.7356 | 122.9736 | -0.13733 | 122.9828 | 60.965 | -0.25635 | 122.9736 | -0.13733 | 60.965 | 122.7356 | 122.9828 | -123.2529 | -123.1705
2769.7656 | 123.2254 | -60.8963 | 62.0316 | 0.026474 | -0.0090704 | -0.01348 | 0.00071144 | 0.058396 | -0.0065047 | 0.065916 | -61.0107 | 62.0911 | -61.2305 | -61.0703 | 61.8484 | 0.064087 | -0.09613 | 0.23346 | 62.1002 | -61.1435 | -0.33417 | 0.059509 | -0.11444 | -0.17395 | -0.1831 | -0.24719 | 0.068665 | 0.21973 | 60.8002 | 61.1298 | 122.7448 | 122.9874 | -0.11444 | 122.9965 | 60.9604 | -0.24719 | 122.9874 | -0.11444 | 60.9604 | 122.7448 | 122.9965 | -123.262 | -123.175
2770.7656 | 123.2208 | -60.878 | 62.0361 | 0.095139 | -0.0084296 | -0.010916 | 0.00028404 | 0.057328 | -0.0052231 | 0.066129 | -61.0382 | 62.0956 | -61.2305 | -61.084 | 61.8668 | 0.064087 | -0.082397 | 0.21973 | 62.0911 | -61.1435 | -0.35248 | 0.059509 | -0.16022 | -0.20599 | -0.16937 | -0.2655 | 0.054931 | 0.19226 | 60.7956 | 61.0977 | 122.7448 | 122.9736 | -0.16022 | 122.9691 | 60.9421 | -0.2655 | 122.9736 | -0.16022 | 60.9421 | 122.7448 | 122.9691 | -123.2666 | -123.1796
2771.7656 | 123.2254 | -60.9009 | 62.0453 | 0.011215 | -0.009925 | -0.013052 | -0.00078396 | 0.059891 | -0.0067185 | 0.067838 | -61.0565 | 62.0911 | -61.2167 | -61.0931 | 61.853 | 0.054932 | -0.07782 | 0.2243 | 62.1002 | -61.1389 | -0.31586 | 0.045776 | -0.15564 | -0.19226 | -0.19226 | -0.23804 | 0.054932 | 0.16022 | 60.8231 | 61.1252 | 122.7539 | 122.9919 | -0.15564 | 123.0011 | 60.9558 | -0.23804 | 122.9919 | -0.15564 | 60.9558 | 122.7539 | 123.0011 | -123.262 | -123.1842
2772.7656 | 123.2117 | -60.8551 | 62.059 | -0.74409 | -0.0088568 | -0.0089935 | 0.00071144 | 0.061387 | -0.0088547 | 0.06677 | -60.997 | 62.0911 | -61.2076 | -61.0245 | 61.9034 | 0.15106 | -0.059509 | 0.3067 | 62.1048 | -61.1298 | -0.35248 | 0.032043 | -0.14191 | -0.16937 | -0.15564 | -0.27466 | 0.045776 | 0.21057 | 60.7956 | 61.1618 | 122.7585 | 122.9462 | -0.14191 | 122.9599 | 61.0062 | -0.27466 | 122.9462 | -0.14191 | 61.0062 | 122.7585 | 122.9599 | -123.2666 | -123.1888
2773.7656 | 123.1888 | -60.8871 | 62.0361 | 0.30113 | -0.0084296 | -0.013266 | -0.0016386 | 0.057969 | -0.0069321 | 0.067411 | -61.0336 | 62.0865 | -61.2076 | -61.1023 | 61.8484 | 0.036621 | -0.10071 | 0.18768 | 62.0956 | -61.1572 | -0.32043 | 0.050354 | -0.14648 | -0.21515 | -0.18768 | -0.27008 | 0.059509 | 0.17395 | 60.7864 | 61.0748 | 122.7356 | 122.9736 | -0.14648 | 122.9828 | 60.9238 | -0.27008 | 122.9736 | -0.14648 | 60.9238 | 122.7356 | 122.9828 | -123.2437 | -123.1934
2774.7656 | 123.2437 | -60.8643 | 62.0224 | 0.0035856 | -0.0077888 | -0.017539 | -0.00057036 | 0.060319 | -0.0071457 | 0.065702 | -61.0153 | 62.0728 | -61.2259 | -61.0519 | 61.8805 | 0.091553 | -0.09613 | 0.25177 | 62.1185 | -61.1435 | -0.36163 | 0.050354 | -0.15106 | -0.18768 | -0.14191 | -0.27924 | 0.09613 | 0.21057 | 60.7681 | 61.116 | 122.7448 | 122.937 | -0.15106 | 122.9828 | 60.9558 | -0.27924 | 122.937 | -0.15106 | 60.9558 | 122.7448 | 122.9828 | -123.2483 | -123.1659
2775.7656 | 123.2117 | -60.8734 | 62.0407 | -0.034561 | -0.0043708 | -0.012625 | -0.0012112 | 0.058396 | -0.0077865 | 0.065061 | -61.0016 | 62.0865 | -61.2305 | -61.0657 | 61.8713 | 0.086975 | -0.10529 | 0.27008 | 62.114 | -61.1298 | -0.35706 | 0.045777 | -0.12817 | -0.19226 | -0.16937 | -0.25635 | 0.073243 | 0.22888 | 60.7681 | 61.1435 | 122.7448 | 122.9599 | -0.12817 | 122.9874 | 60.9604 | -0.25635 | 122.9599 | -0.12817 | 60.9604 | 122.7448 | 122.9874 | -123.2712 | -123.1705
2776.7656 | 123.1979 | -60.8734 | 62.0316 | 0.0035856 | -0.009925 | -0.010703 | -0.0012112 | 0.059037 | -0.0082137 | 0.064847 | -61.0107 | 62.0956 | -61.2076 | -61.0519 | 61.8713 | 0.09613 | -0.082397 | 0.25177 | 62.114 | -61.1572 | -0.33417 | 0.064087 | -0.13733 | -0.17853 | -0.16022 | -0.28381 | 0.082398 | 0.19684 | 60.791 | 61.1252 | 122.7448 | 122.9691 | -0.13733 | 122.9874 | 60.9695 | -0.28381 | 122.9691 | -0.13733 | 60.9695 | 122.7448 | 122.9874 | -123.2391 | -123.1888
2777.7656 | 123.2117 | -60.8734 | 62.0636 | 0.034104 | -0.0094976 | -0.017752 | -0.00014316 | 0.057542 | -0.0062911 | 0.065488 | -61.0291 | 62.0728 | -61.2305 | -61.0519 | 61.8942 | 0.086975 | -0.086975 | 0.2655 | 62.0956 | -61.1343 | -0.35706 | 0.009155 | -0.15564 | -0.17853 | -0.16937 | -0.26093 | 0.032043 | 0.20142 | 60.7864 | 61.1389 | 122.7676 | 122.9462 | -0.15564 | 122.9691 | 60.9604 | -0.26093 | 122.9462 | -0.15564 | 60.9604 | 122.7676 | 122.9691 | -123.2941 | -123.1979
2778.7656 | 123.2117 | -60.8688 | 62.0407 | -0.04219 | -0.009284 | -0.013266 | 7.0444e-05 | 0.056901 | -0.0035141 | 0.068265 | -61.0245 | 62.0911 | -61.2076 | -61.0428 | 61.8805 | 0.086975 | -0.10071 | 0.26093 | 62.0865 | -61.1481 | -0.33875 | 0.050354 | -0.15564 | -0.17395 | -0.16022 | -0.27924 | 0.045777 | 0.18311 | 60.7681 | 61.1298 | 122.7493 | 122.9599 | -0.15564 | 122.9553 | 60.9558 | -0.27924 | 122.9599 | -0.15564 | 60.9558 | 122.7493 | 122.9553 | -123.2483 | -123.1888
2779.7656 | 123.2208 | -60.8871 | 62.0499 | -0.04219 | -0.009284 | -0.014548 | -0.00035676 | 0.057969 | -0.0069321 | 0.065061 | -61.0153 | 62.0865 | -61.2305 | -61.0474 | 61.8759 | 0.091553 | -0.10529 | 0.23804 | 62.0911 | -61.1435 | -0.34332 | 0.036621 | -0.12817 | -0.16022 | -0.17395 | -0.25635 | 0.041198 | 0.21515 | 60.7819 | 61.1252 | 122.7631 | 122.9736 | -0.12817 | 122.9782 | 60.9787 | -0.25635 | 122.9736 | -0.12817 | 60.9787 | 122.7631 | 122.9782 | -123.2803 | -123.1934
2780.7656 | 123.2346 | -60.8459 | 62.0636 | 0.011215 | -0.0094976 | -0.014761 | -0.0012112 | 0.054978 | -0.0082137 | 0.065275 | -61.0336 | 62.0819 | -61.2259 | -61.0611 | 61.8896 | 0.09613 | -0.11444 | 0.25177 | 62.0865 | -61.1618 | -0.37994 | 0.01831 | -0.18768 | -0.21515 | -0.17395 | -0.31586 | 0.022888 | 0.19226 | 60.7315 | 61.0977 | 122.7356 | 122.9279 | -0.18768 | 122.9324 | 60.9421 | -0.31586 | 122.9279 | -0.18768 | 60.9421 | 122.7356 | 122.9324 | -123.2895 | -123.2254
2781.7656 | 123.2483 | -60.8459 | 62.059 | -0.18715 | -0.010993 | -0.010062 | 0.00049764 | 0.057755 | -0.0056503 | 0.066984 | -60.9741 | 62.0956 | -61.1893 | -61.0153 | 61.908 | 0.14648 | -0.10071 | 0.32959 | 62.0911 | -61.1206 | -0.34332 | 0.036621 | -0.12817 | -0.16937 | -0.15106 | -0.27466 | 0.032043 | 0.21515 | 60.7452 | 61.1755 | 122.7539 | 122.9416 | -0.12817 | 122.937 | 60.9924 | -0.27466 | 122.9416 | -0.12817 | 60.9924 | 122.7539 | 122.937 | -123.2483 | -123.1796
2782.7656 | 123.262 | -60.8505 | 62.0361 | -0.034561 | -0.009925 | -0.012412 | -0.00035676 | 0.05861 | -0.0062911 | 0.066556 | -60.9787 | 62.0911 | -61.2076 | -61.0245 | 61.908 | 0.16937 | -0.091553 | 0.31586 | 62.0956 | -61.1114 | -0.35706 | 0.054931 | -0.12817 | -0.17395 | -0.12817 | -0.26093 | 0.059509 | 0.22888 | 60.759 | 61.1664 | 122.7585 | 122.9416 | -0.12817 | 122.9462 | 61.0199 | -0.26093 | 122.9416 | -0.12817 | 61.0199 | 122.7585 | 122.9462 | -123.2437 | -123.1476
2783.7656 | 123.2666 | -60.878 | 62.027 | -0.034561 | -0.009284 | -0.01647 | 0.00071144 | 0.059891 | -0.0080001 | 0.064634 | -60.9879 | 62.0911 | -61.203 | -61.0153 | 61.9034 | 0.14648 | -0.10986 | 0.31128 | 62.1048 | -61.1526 | -0.32501 | 0.064086 | -0.10986 | -0.13733 | -0.1236 | -0.27466 | 0.077819 | 0.21515 | 60.7681 | 61.1893 | 122.7814 | 122.9691 | -0.10986 | 122.9828 | 61.0245 | -0.27466 | 122.9691 | -0.10986 | 61.0245 | 122.7814 | 122.9828 | -123.23 | -123.1796
2784.7656 | 123.2437 | -60.8597 | 62.0453 | -0.04982 | -0.007575 | -0.014975 | -0.00035676 | 0.058823 | -0.0069321 | 0.066556 | -61.0062 | 62.0682 | -61.203 | -61.0382 | 61.9171 | 0.11902 | -0.091553 | 0.3067 | 62.0499 | -61.1572 | -0.34332 | 0.022888 | -0.14649 | -0.17853 | -0.12817 | -0.29755 | 0.004578 | 0.19684 | 60.7681 | 61.1664 | 122.7768 | 122.9279 | -0.14649 | 122.9095 | 60.9787 | -0.29755 | 122.9279 | -0.14649 | 60.9787 | 122.7768 | 122.9095 | -123.2483 | -123.2025
2785.7656 | 123.143 | -60.8688 | 62.0773 | -0.18715 | -0.009284 | -0.015189 | 0.0013522 | 0.057114 | -0.0062911 | 0.063566 | -60.9879 | 62.114 | -61.2396 | -61.0703 | 61.8668 | 0.09613 | 0.045776 | 0.24719 | 62.1414 | -61.1298 | -0.37079 | 0.036621 | -0.11902 | -0.20142 | -0.21057 | -0.26093 | 0.064086 | 0.25177 | 60.9146 | 61.116 | 122.7356 | 122.9828 | -0.11902 | 123.0103 | 60.965 | -0.26093 | 122.9828 | -0.11902 | 60.965 | 122.7356 | 123.0103 | -123.317 | -123.2071
2786.7656 | 123.2391 | -60.8551 | 62.0499 | -0.04982 | -0.011848 | -0.014761 | -0.00099756 | 0.057542 | -0.0054367 | 0.06442 | -61.0062 | 62.0636 | -61.203 | -61.0519 | 61.8851 | 0.091553 | -0.09613 | 0.27008 | 62.0819 | -61.1664 | -0.3479 | 0.013733 | -0.15106 | -0.19684 | -0.16479 | -0.31128 | 0.032043 | 0.19684 | 60.759 | 61.1252 | 122.7402 | 122.9187 | -0.15106 | 122.937 | 60.9467 | -0.31128 | 122.9187 | -0.15106 | 60.9467 | 122.7402 | 122.937 | -123.2529 | -123.2162
2787.7656 | 123.2208 | -60.8688 | 62.0499 | 0.018845 | -0.008216 | -0.011771 | -0.00057036 | 0.05861 | -0.0047957 | 0.064634 | -61.0107 | 62.0865 | -61.2122 | -61.0657 | 61.8713 | 0.073242 | -0.086975 | 0.25177 | 62.1048 | -61.1435 | -0.34332 | 0.036621 | -0.14191 | -0.19684 | -0.17853 | -0.27466 | 0.054931 | 0.20142 | 60.7819 | 61.1206 | 122.7402 | 122.9553 | -0.14191 | 122.9736 | 60.9421 | -0.27466 | 122.9553 | -0.14191 | 60.9421 | 122.7402 | 122.9736 | -123.262 | -123.1934
2788.7656 | 123.262 | -60.8459 | 62.0544 | -0.026932 | -0.0084296 | -0.016898 | 0.0017794 | 0.059037 | -0.0065047 | 0.06677 | -60.9695 | 62.0773 | -61.235 | -61.0245 | 61.8988 | 0.14191 | -0.11444 | 0.30212 | 62.1002 | -61.1252 | -0.3891 | 0.022889 | -0.1236 | -0.17853 | -0.15564 | -0.27924 | 0.045777 | 0.2655 | 60.7315 | 61.1481 | 122.7448 | 122.9233 | -0.1236 | 122.9462 | 60.9879 | -0.27924 | 122.9233 | -0.1236 | 60.9879 | 122.7448 | 122.9462 | -123.2895 | -123.1796
2789.7656 | 123.2574 | -60.8551 | 62.0224 | -0.11085 | -0.0084296 | -0.013907 | -0.00078396 | 0.060319 | -0.0086411 | 0.065916 | -61.0062 | 62.0819 | -61.2122 | -61.0428 | 61.8759 | 0.11902 | -0.10071 | 0.27924 | 62.1231 | -61.1298 | -0.35706 | 0.059509 | -0.15106 | -0.18768 | -0.14648 | -0.27466 | 0.10071 | 0.20599 | 60.7544 | 61.1343 | 122.731 | 122.937 | -0.15106 | 122.9782 | 60.9741 | -0.27466 | 122.937 | -0.15106 | 60.9741 | 122.731 | 122.9782 | -123.2346 | -123.1522
2790.7656 | 123.2208 | -60.8734 | 62.0224 | -0.0040434 | -0.010566 | -0.018179 | -0.001425 | 0.059891 | -0.0056503 | 0.065275 | -60.9924 | 62.0911 | -61.2122 | -61.0657 | 61.8805 | 0.09613 | -0.07782 | 0.26093 | 62.1094 | -61.1298 | -0.33875 | 0.068664 | -0.11902 | -0.19226 | -0.14191 | -0.25635 | 0.086975 | 0.21973 | 60.7956 | 61.1343 | 122.7539 | 122.9645 | -0.11902 | 122.9828 | 60.9695 | -0.25635 | 122.9645 | -0.11902 | 60.9695 | 122.7539 | 122.9828 | -123.2346 | -123.1522
2791.7656 | 123.2346 | -60.9009 | 62.059 | 0.041733 | -0.009284 | -0.014121 | 0.00049764 | 0.059037 | -0.0067185 | 0.065702 | -61.0336 | 62.0911 | -61.2305 | -61.0703 | 61.8713 | 0.082397 | -0.082397 | 0.23804 | 62.1002 | -61.1435 | -0.32959 | 0.032043 | -0.13275 | -0.16937 | -0.18768 | -0.24261 | 0.041199 | 0.19684 | 60.8185 | 61.1389 | 122.7722 | 122.9919 | -0.13275 | 123.0011 | 60.9833 | -0.24261 | 122.9919 | -0.13275 | 60.9833 | 122.7722 | 123.0011 | -123.2895 | -123.2025
2792.7656 | 123.2391 | -60.8505 | 62.0499 | -0.25581 | -0.0094976 | -0.015189 | 0.0024202 | 0.059037 | -0.0084273 | 0.066343 | -60.9421 | 62.0865 | -61.2122 | -61.0428 | 61.9034 | 0.14191 | -0.041199 | 0.31586 | 62.1231 | -61.1206 | -0.36163 | 0.036621 | -0.091553 | -0.19226 | -0.14648 | -0.27008 | 0.073242 | 0.27008 | 60.8093 | 61.1664 | 122.7539 | 122.937 | -0.091553 | 122.9736 | 60.9924 | -0.27008 | 122.937 | -0.091553 | 60.9924 | 122.7539 | 122.9736 | -123.262 | -123.1705
2793.7656 | 123.2346 | -60.8963 | 62.0453 | 0.19432 | -0.009925 | -0.010916 | 0.0017794 | 0.059891 | -0.0080001 | 0.066129 | -61.0565 | 62.1048 | -61.2579 | -61.1023 | 61.8393 | 0.041199 | -0.09613 | 0.21057 | 62.1002 | -61.1618 | -0.36163 | 0.059509 | -0.16022 | -0.20599 | -0.20599 | -0.2655 | 0.054932 | 0.20142 | 60.8002 | 61.1069 | 122.7356 | 123.0011 | -0.16022 | 122.9965 | 60.9375 | -0.2655 | 123.0011 | -0.16022 | 60.9375 | 122.7356 | 122.9965 | -123.3032 | -123.2071
2794.7656 | 123.2117 | -60.8688 | 62.0544 | 0.07988 | -0.0073614 | -0.011557 | 0.0011386 | 0.057755 | -0.0060775 | 0.068052 | -61.0428 | 62.0728 | -61.2396 | -61.1389 | 61.8393 | 0.009155 | -0.09613 | 0.19684 | 62.1094 | -61.1755 | -0.37079 | 0.018311 | -0.17395 | -0.27008 | -0.21515 | -0.3067 | 0.054932 | 0.19684 | 60.7727 | 61.0657 | 122.7081 | 122.9416 | -0.17395 | 122.9782 | 60.878 | -0.3067 | 122.9416 | -0.17395 | 60.878 | 122.7081 | 122.9782 | -123.2941 | -123.23
2795.7656 | 123.2208 | -60.8917 | 62.0682 | 0.1104 | -0.0084296 | -0.013052 | 0.00028404 | 0.058396 | -0.0075729 | 0.067197 | -61.0428 | 62.0911 | -61.2076 | -61.0931 | 61.853 | 0.054932 | -0.082397 | 0.20142 | 62.059 | -61.1343 | -0.31586 | 0.022888 | -0.15106 | -0.20142 | -0.21515 | -0.24261 | -0.009155 | 0.16479 | 60.8093 | 61.0931 | 122.7448 | 122.9828 | -0.15106 | 122.9507 | 60.9467 | -0.24261 | 122.9828 | -0.15106 | 60.9467 | 122.7448 | 122.9507 | -123.2758 | -123.2025
2796.7656 | 123.2071 | -60.8826 | 62.059 | -0.072708 | -0.0097114 | -0.013052 | -0.00014316 | 0.057969 | -0.0047957 | 0.068693 | -61.0886 | 62.0819 | -61.2305 | -61.1023 | 61.8347 | 0.036621 | -0.10071 | 0.18768 | 62.1002 | -61.1481 | -0.3479 | 0.022888 | -0.20599 | -0.21973 | -0.2243 | -0.2655 | 0.041199 | 0.14191 | 60.7819 | 61.0703 | 122.7173 | 122.9645 | -0.20599 | 122.9828 | 60.9192 | -0.2655 | 122.9645 | -0.20599 | 60.9192 | 122.7173 | 122.9828 | -123.2895 | -123.2071
2797.7656 | 123.175 | -60.878 | 62.0544 | 0.07988 | -0.0050116 | -0.01348 | 0.00028404 | 0.055833 | -0.0067185 | 0.068693 | -61.0519 | 62.0819 | -61.2396 | -60.9512 | 61.9217 | 0.050354 | -0.11902 | 0.14191 | 62.1002 | -61.1526 | -0.36163 | 0.027466 | -0.17395 | -0.073242 | -0.13275 | -0.27466 | 0.045777 | 0.18768 | 60.759 | 61.0199 | 122.7997 | 122.9599 | -0.17395 | 122.9782 | 60.9283 | -0.27466 | 122.9599 | -0.17395 | 60.9283 | 122.7997 | 122.9782 | -123.2941 | -123.2071
2798.7656 | 123.2117 | -60.8871 | 62.0499 | 0.07988 | -0.008216 | -0.012412 | 7.0444e-05 | 0.057542 | -0.0067185 | 0.065702 | -61.0565 | 62.0819 | -61.203 | -61.1252 | 61.8301 | 0.022888 | -0.1236 | 0.16022 | 62.0728 | -61.1664 | -0.31586 | 0.032043 | -0.16937 | -0.23804 | -0.21973 | -0.27924 | 0.022888 | 0.14648 | 60.7636 | 61.0474 | 122.7173 | 122.9691 | -0.16937 | 122.9599 | 60.91 | -0.27924 | 122.9691 | -0.16937 | 60.91 | 122.7173 | 122.9599 | -123.2529 | -123.2162
2799.7656 | 123.2529 | -60.8551 | 62.0407 | 0.011215 | -0.0090704 | -0.01583 | 0.00049764 | 0.059037 | -0.0069321 | 0.064634 | -61.0062 | 62.1002 | -61.1984 | -61.0245 | 61.9263 | 0.13733 | -0.11444 | 0.33417 | 62.0911 | -61.1206 | -0.34332 | 0.05951 | -0.15106 | -0.16937 | -0.11444 | -0.2655 | 0.050354 | 0.19226 | 60.7407 | 61.1893 | 122.7814 | 122.9553 | -0.15106 | 122.9462 | 60.9924 | -0.2655 | 122.9553 | -0.15106 | 60.9924 | 122.7814 | 122.9462 | -123.2391 | -123.1613
2800.7656 | 123.1796 | -60.9009 | 62.0499 | 0.17906 | -0.008216 | -0.0074981 | 0.001993 | 0.058396 | -0.0054367 | 0.063779 | -61.0474 | 62.0728 | -61.2167 | -61.1069 | 61.8164 | -0.004578 | -0.13733 | 0.16022 | 62.0819 | -61.1435 | -0.31586 | 0.022888 | -0.14648 | -0.20599 | -0.23346 | -0.24261 | 0.032043 | 0.16937 | 60.7636 | 61.0611 | 122.7173 | 122.9736 | -0.14648 | 122.9828 | 60.8963 | -0.24261 | 122.9736 | -0.14648 | 60.8963 | 122.7173 | 122.9828 | -123.2666 | -123.1934
2801.7656 | 123.1934 | -60.8871 | 62.0361 | 0.23247 | -0.0094976 | -0.011984 | 0.0022066 | 0.059251 | -0.0062911 | 0.067411 | -61.0245 | 62.0499 | -61.2488 | -61.1206 | 61.8301 | 0.009155 | -0.15106 | 0.15106 | 62.0911 | -61.171 | -0.36163 | 0.013733 | -0.13733 | -0.23346 | -0.20599 | -0.28381 | 0.054931 | 0.2243 | 60.7361 | 61.0382 | 122.7173 | 122.937 | -0.13733 | 122.9782 | 60.8963 | -0.28381 | 122.937 | -0.13733 | 60.8963 | 122.7173 | 122.9782 | -123.2849 | -123.2071
2802.7656 | 123.1659 | -60.878 | 62.0453 | 0.13329 | -0.008216 | -0.013693 | 0.0011386 | 0.058396 | -0.0054367 | 0.06677 | -61.0291 | 62.0911 | -61.2259 | -61.1206 | 61.8301 | 0.009155 | -0.12817 | 0.15564 | 62.0728 | -61.171 | -0.3479 | 0.045776 | -0.15106 | -0.24261 | -0.21515 | -0.29297 | 0.027466 | 0.19684 | 60.7498 | 61.0336 | 122.7081 | 122.9691 | -0.15106 | 122.9507 | 60.8871 | -0.29297 | 122.9691 | -0.15106 | 60.8871 | 122.7081 | 122.9507 | -123.2712 | -123.2162
2803.7656 | 123.1705 | -60.91 | 62.0361 | 0.20195 | -0.0080024 | -0.013266 | 0.0032748 | 0.05861 | -0.0067185 | 0.066556 | -61.0291 | 62.0682 | -61.2259 | -61.116 | 61.8301 | 0 | -0.1236 | 0.17395 | 62.1002 | -61.1755 | -0.31586 | 0.032043 | -0.11902 | -0.20599 | -0.20599 | -0.2655 | 0.064087 | 0.19684 | 60.7864 | 61.084 | 122.7402 | 122.9782 | -0.11902 | 123.0103 | 60.91 | -0.2655 | 122.9782 | -0.11902 | 60.91 | 122.7402 | 123.0103 | -123.262 | -123.2117
2804.7812 | 123.111 | -60.9192 | 62.1002 | -0.20241 | -0.0062934 | -0.014761 | 0.0011386 | 0.059678 | -0.0071457 | 0.065916 | -61.0336 | 62.1964 | -61.2259 | -61.2076 | 61.7798 | 0.027466 | 0.086975 | 0.17853 | 62.1323 | -61.2122 | -0.3067 | 0.09613 | -0.11444 | -0.28839 | -0.32044 | -0.29297 | 0.032043 | 0.19226 | 61.0062 | 61.0977 | 122.699 | 123.1155 | -0.11444 | 123.0515 | 60.9467 | -0.29297 | 123.1155 | -0.11444 | 60.9467 | 122.699 | 123.0515 | -123.3261 | -123.3124
2805.7656 | 123.2071 | -60.8963 | 62.0178 | 0.15617 | -0.0080024 | -0.017111 | 0.0030612 | 0.0616 | -0.0071457 | 0.064847 | -61.0107 | 62.0911 | -61.2167 | -61.0886 | 61.8576 | 0.022888 | -0.19226 | 0.17853 | 62.0544 | -61.1664 | -0.32043 | 0.073242 | -0.11444 | -0.19226 | -0.16022 | -0.27008 | 0.036621 | 0.20599 | 60.704 | 61.0748 | 122.7539 | 122.9874 | -0.11444 | 122.9507 | 60.9192 | -0.27008 | 122.9874 | -0.11444 | 60.9192 | 122.7539 | 122.9507 | -123.2346 | -123.1842
2806.7656 | 123.1979 | -60.8871 | 62.0682 | 0.064621 | -0.0069342 | -0.010489 | -0.00078396 | 0.05861 | -0.0056503 | 0.067624 | -61.0474 | 62.0865 | -61.2213 | -61.1069 | 61.853 | 0.050354 | -0.091553 | 0.21515 | 62.1002 | -61.1481 | -0.33417 | 0.018311 | -0.16022 | -0.21973 | -0.21515 | -0.26093 | 0.032044 | 0.17395 | 60.7956 | 61.1023 | 122.7402 | 122.9736 | -0.16022 | 122.9874 | 60.9375 | -0.26093 | 122.9736 | -0.16022 | 60.9375 | 122.7402 | 122.9874 | -123.2895 | -123.2162
2807.7656 | 123.2071 | -60.8643 | 62.0316 | 0.30876 | -0.0097114 | -0.012412 | 0.0056246 | 0.059678 | -0.0082137 | 0.06677 | -60.965 | 62.0819 | -61.2213 | -61.0794 | 61.8576 | 0.032043 | -0.21973 | 0.17853 | 62.0682 | -61.1572 | -0.35706 | 0.050354 | -0.10071 | -0.21515 | -0.17395 | -0.29297 | 0.036621 | 0.25635 | 60.6445 | 61.0428 | 122.7219 | 122.9462 | -0.10071 | 122.9324 | 60.8963 | -0.29297 | 122.9462 | -0.10071 | 60.8963 | 122.7219 | 122.9324 | -123.2529 | -123.1888
2808.7656 | 123.23 | -60.8734 | 62.0361 | 0.28587 | -0.0071478 | -0.0079253 | 0.0039156 | 0.058182 | -0.0062911 | 0.066129 | -60.9924 | 62.0819 | -61.2122 | -61.2579 | 61.8988 | 0.10529 | -0.16022 | 0.21973 | 62.0682 | -61.1801 | -0.33875 | 0.045776 | -0.11902 | -0.38452 | -0.13733 | -0.3067 | 0.032043 | 0.21973 | 60.7132 | 61.0931 | 122.7722 | 122.9553 | -0.11902 | 122.9416 | 60.9787 | -0.3067 | 122.9553 | -0.11902 | 60.9787 | 122.7722 | 122.9416 | -123.2483 | -123.2162
2809.7812 | 123.1384 | -60.91 | 62.1002 | 0.48424 | -0.0037298 | -0.0072845 | 0.0062656 | 0.058823 | -0.0077865 | 0.067411 | -61.1206 | 62.2055 | -61.2213 | -61.1252 | 61.8118 | 0.050354 | 0.13275 | 0.21057 | 62.1277 | -61.2167 | -0.31128 | 0.10529 | -0.21057 | -0.21515 | -0.28839 | -0.3067 | 0.027466 | 0.10071 | 61.0428 | 61.1206 | 122.7219 | 123.1155 | -0.21057 | 123.0377 | 60.9604 | -0.3067 | 123.1155 | -0.21057 | 60.9604 | 122.7219 | 123.0377 | -123.3215 | -123.317
2810.7656 | 123.2437 | -60.878 | 62.0087 | 0.54527 | -0.0088568 | -0.013693 | 0.0041292 | 0.062028 | -0.0050095 | 0.064207 | -60.9009 | 62.0865 | -61.2213 | -61.0611 | 61.8393 | 0.041199 | -0.2243 | 0.17395 | 62.0682 | -61.1938 | -0.34332 | 0.07782 | -0.022888 | -0.1831 | -0.16937 | -0.31586 | 0.059509 | 0.32043 | 60.6537 | 61.0519 | 122.7173 | 122.9645 | -0.022888 | 122.9462 | 60.9192 | -0.31586 | 122.9645 | -0.022888 | 60.9192 | 122.7173 | 122.9462 | -123.23 | -123.2025
2811.7656 | 123.2437 | -60.8871 | 62.0316 | 0.27824 | -0.005866 | -0.011771 | 0.0051974 | 0.058823 | -0.0080001 | 0.066129 | -60.9924 | 62.1277 | -61.2213 | -61.0931 | 61.9629 | -0.054932 | -0.32501 | 0.28839 | 62.0544 | -61.1847 | -0.33417 | 0.096131 | -0.10529 | -0.20599 | -0.068664 | -0.29755 | 0.022888 | 0.22888 | 60.5621 | 61.1755 | 122.85 | 123.0148 | -0.10529 | 122.9416 | 60.8322 | -0.29755 | 123.0148 | -0.10529 | 60.8322 | 122.85 | 122.9416 | -123.2529 | -123.2162
2812.7656 | 123.2117 | -60.8963 | 62.0224 | 0.25536 | -0.005866 | -0.0083527 | 0.0056246 | 0.062455 | -0.0071457 | 0.064847 | -60.9695 | 62.1323 | -61.2305 | -61.084 | 61.8484 | 0.045776 | -0.21515 | 0.15564 | 62.0865 | -61.1893 | -0.33417 | 0.10986 | -0.073242 | -0.18768 | -0.17395 | -0.29297 | 0.064087 | 0.26093 | 60.6812 | 61.0519 | 122.7448 | 123.0286 | -0.073242 | 122.9828 | 60.9421 | -0.29297 | 123.0286 | -0.073242 | 60.9421 | 122.7448 | 122.9828 | -123.2529 | -123.2117
2813.7656 | 123.1888 | -60.91 | 62.0499 | 0.17143 | -0.008216 | -0.011557 | 0.001993 | 0.059464 | -0.0052231 | 0.065916 | -61.0519 | 62.1094 | -61.2213 | -61.1252 | 61.821 | 0.018311 | -0.13275 | 0.16479 | 62.0773 | -61.1938 | -0.31128 | 0.059509 | -0.14191 | -0.21515 | -0.22888 | -0.28381 | 0.027466 | 0.16937 | 60.7773 | 61.0748 | 122.731 | 123.0194 | -0.14191 | 122.9874 | 60.9283 | -0.28381 | 123.0194 | -0.14191 | 60.9283 | 122.731 | 122.9874 | -123.2712 | -123.2437
2814.7812 | 123.2529 | -60.8597 | 62.0544 | -0.034561 | -0.0071478 | -0.012198 | 0.0017794 | 0.059251 | -0.0060775 | 0.067838 | -60.9833 | 62.1277 | -61.2213 | -61.0245 | 61.9263 | 0.13275 | -0.10529 | 0.31586 | 62.0956 | -61.1755 | -0.36163 | 0.073243 | -0.1236 | -0.1648 | -0.12817 | -0.31586 | 0.041199 | 0.23804 | 60.7544 | 61.1755 | 122.7859 | 122.9874 | -0.1236 | 122.9553 | 60.9924 | -0.31586 | 122.9874 | -0.1236 | 60.9924 | 122.7859 | 122.9553 | -123.2758 | -123.23
2815.7656 | 123.1705 | -60.9238 | 62.0361 | 0.26299 | -0.0035162 | -0.010489 | 0.0058382 | 0.062028 | -0.0056503 | 0.064634 | -61.0382 | 62.1597 | -61.2625 | -61.1389 | 61.7981 | -0.036621 | -0.13733 | 0.09613 | 62.0911 | -61.2167 | -0.33875 | 0.1236 | -0.11444 | -0.21515 | -0.23804 | -0.29297 | 0.054931 | 0.2243 | 60.7864 | 61.0199 | 122.7219 | 123.0835 | -0.11444 | 123.0148 | 60.8871 | -0.29297 | 123.0835 | -0.11444 | 60.8871 | 122.7219 | 123.0148 | -123.2986 | -123.2529
2816.7656 | 123.2346 | -60.8826 | 62.027 | 0.23247 | -0.005866 | -0.0077117 | 0.004343 | 0.060105 | -0.0050095 | 0.065488 | -60.9879 | 62.1323 | -61.2579 | -61.0977 | 61.8439 | 0.022888 | -0.21973 | 0.17395 | 62.0728 | -61.1984 | -0.37537 | 0.10529 | -0.10529 | -0.21515 | -0.18311 | -0.31586 | 0.045776 | 0.27008 | 60.6628 | 61.0565 | 122.7264 | 123.0148 | -0.10529 | 122.9553 | 60.9055 | -0.31586 | 123.0148 | -0.10529 | 60.9055 | 122.7264 | 122.9553 | -123.2849 | -123.2254
2817.7656 | 123.2391 | -60.8871 | 62.0407 | 0.25536 | -0.0043708 | -0.012198 | 0.0060518 | 0.060105 | -0.0062911 | 0.065488 | -61.0107 | 62.1231 | -61.2488 | -61.1023 | 61.8118 | 0 | -0.1831 | 0.16479 | 62.0453 | -61.2167 | -0.36163 | 0.082398 | -0.1236 | -0.21515 | -0.22888 | -0.32959 | 0.004578 | 0.23804 | 60.704 | 61.0519 | 122.699 | 123.0103 | -0.1236 | 122.9324 | 60.8871 | -0.32959 | 123.0103 | -0.1236 | 60.8871 | 122.699 | 122.9324 | -123.2895 | -123.2574
2818.7656 | 123.2208 | -60.91 | 62.0224 | 0.26299 | -0.0041572 | -0.010062 | 0.005411 | 0.061173 | -0.0071457 | 0.065916 | -61.0428 | 62.1643 | -61.2396 | -61.1435 | 61.8164 | 0.004578 | -0.16937 | 0.14191 | 62.0728 | -61.2167 | -0.32959 | 0.14191 | -0.13275 | -0.23346 | -0.20599 | -0.3067 | 0.050354 | 0.19684 | 60.7407 | 61.0519 | 122.7264 | 123.0743 | -0.13275 | 122.9828 | 60.9146 | -0.3067 | 123.0743 | -0.13275 | 60.9146 | 122.7264 | 122.9828 | -123.262 | -123.2391
2819.7812 | 123.2071 | -60.8643 | 62.0407 | -0.17189 | -0.0067206 | -0.0070709 | 0.0013522 | 0.060105 | -0.0047957 | 0.066984 | -61.0016 | 62.1735 | -61.203 | -61.084 | 61.8805 | 0.11444 | 0.027466 | 0.27466 | 62.0911 | -61.1893 | -0.33875 | 0.13275 | -0.13733 | -0.21973 | -0.16022 | -0.32501 | 0.050354 | 0.20142 | 60.8917 | 61.1389 | 122.7448 | 123.0377 | -0.13733 | 122.9553 | 60.9787 | -0.32501 | 123.0377 | -0.13733 | 60.9787 | 122.7448 | 122.9553 | -123.2437 | -123.23
2820.7656 | 123.1979 | -60.9146 | 62.0453 | 0.15617 | -0.0073614 | -0.0094207 | 0.00071144 | 0.06096 | -0.0035141 | 0.066556 | -61.0565 | 62.1231 | -61.2488 | -61.1389 | 61.821 | 0.022888 | -0.091553 | 0.15564 | 62.1048 | -61.1984 | -0.33417 | 0.07782 | -0.14191 | -0.2243 | -0.2243 | -0.28381 | 0.059509 | 0.19226 | 60.8231 | 61.0703 | 122.7356 | 123.0377 | -0.14191 | 123.0194 | 60.9375 | -0.28381 | 123.0377 | -0.14191 | 60.9375 | 122.7356 | 123.0194 | -123.2941 | -123.2437
2821.7656 | 123.1796 | -60.9009 | 62.0499 | 0.27824 | -0.005866 | -0.01113 | 0.00712 | 0.061387 | -0.0065047 | 0.066556 | -61.0519 | 62.146 | -61.2671 | -61.1572 | 61.7661 | -0.032043 | -0.11444 | 0.082397 | 62.1185 | -61.2076 | -0.36621 | 0.09613 | -0.15106 | -0.25635 | -0.28381 | -0.3067 | 0.068664 | 0.21515 | 60.7864 | 60.9833 | 122.6669 | 123.0469 | -0.15106 | 123.0194 | 60.8688 | -0.3067 | 123.0469 | -0.15106 | 60.8688 | 122.6669 | 123.0194 | -123.317 | -123.2574
2822.7656 | 123.1567 | -60.9146 | 62.0499 | 0.20958 | -0.004798 | -0.0085663 | 0.0077608 | 0.060532 | -0.0071457 | 0.066343 | -61.0611 | 62.1735 | -61.2808 | -61.171 | 61.7569 | -0.045776 | -0.10529 | 0.082397 | 62.0956 | -61.2167 | -0.36621 | 0.1236 | -0.14648 | -0.25635 | -0.29297 | -0.30212 | 0.045776 | 0.21973 | 60.8093 | 60.997 | 122.6715 | 123.0881 | -0.14648 | 123.0103 | 60.8688 | -0.30212 | 123.0881 | -0.14648 | 60.8688 | 122.6715 | 123.0103 | -123.3307 | -123.2666
2823.7656 | 123.2071 | -60.8917 | 62.0087 | 0.24773 | -0.006507 | -0.0087799 | 0.004343 | 0.062455 | -0.0028731 | 0.06677 | -61.0336 | 62.1735 | -61.2717 | -61.1298 | 61.8118 | 0.004578 | -0.17853 | 0.15564 | 62.059 | -61.2213 | -0.37994 | 0.16479 | -0.14191 | -0.23804 | -0.19684 | -0.32959 | 0.050354 | 0.23804 | 60.7132 | 61.0474 | 122.7036 | 123.0652 | -0.14191 | 122.9507 | 60.8963 | -0.32959 | 123.0652 | -0.14191 | 60.8963 | 122.7036 | 122.9507 | -123.2803 | -123.23
2824.7656 | 123.23 | -60.9009 | 62.0361 | 0.25536 | -0.0054388 | -0.012198 | 0.0047702 | 0.060746 | -0.0067185 | 0.067838 | -61.0336 | 62.1414 | -61.2488 | -61.116 | 61.821 | 0.018311 | -0.16022 | 0.13733 | 62.0499 | -61.2167 | -0.3479 | 0.10529 | -0.13275 | -0.21515 | -0.21515 | -0.31586 | 0.013733 | 0.21515 | 60.7407 | 61.0382 | 122.7219 | 123.0423 | -0.13275 | 122.9507 | 60.9192 | -0.31586 | 123.0423 | -0.13275 | 60.9192 | 122.7219 | 122.9507 | -123.2849 | -123.2529
2825.7656 | 123.2162 | -60.9009 | 62.0361 | 0.23247 | -0.0054388 | -0.0070709 | 0.0030612 | 0.062882 | -0.0062911 | 0.065488 | -61.0382 | 62.1643 | -61.235 | -61.1343 | 61.7889 | -0.004578 | -0.16937 | 0.1236 | 62.1002 | -61.2167 | -0.33417 | 0.12817 | -0.13733 | -0.23346 | -0.24719 | -0.31586 | 0.064087 | 0.19684 | 60.7315 | 61.0245 | 122.6898 | 123.0652 | -0.13733 | 123.0011 | 60.8963 | -0.31586 | 123.0652 | -0.13733 | 60.8963 | 122.6898 | 123.0011 | -123.2712 | -123.2529
2826.7656 | 123.2254 | -60.9146 | 62.0132 | 0.17143 | -0.0054388 | -0.013907 | 0.00028404 | 0.059251 | -0.0062911 | 0.067838 | -61.0291 | 62.1048 | -61.203 | -61.1435 | 61.8301 | 0.013733 | -0.16022 | 0.16479 | 62.0682 | -61.1984 | -0.28839 | 0.091552 | -0.11444 | -0.22888 | -0.18311 | -0.28381 | 0.054931 | 0.17395 | 60.7544 | 61.0794 | 122.7448 | 123.0194 | -0.11444 | 122.9828 | 60.9283 | -0.28381 | 123.0194 | -0.11444 | 60.9283 | 122.7448 | 122.9828 | -123.2162 | -123.2117
2827.7656 | 123.2071 | -60.878 | 62.0178 | 0.18669 | -0.0090704 | -0.01113 | -0.00057036 | 0.059891 | -0.0058639 | 0.066556 | -61.0153 | 62.1002 | -61.2167 | -61.1298 | 61.8347 | 0.018311 | -0.17395 | 0.1831 | 62.1002 | -61.2076 | -0.33874 | 0.082398 | -0.13733 | -0.25177 | -0.18311 | -0.32959 | 0.082398 | 0.20142 | 60.704 | 61.0611 | 122.7127 | 122.9782 | -0.13733 | 122.9782 | 60.8963 | -0.32959 | 122.9782 | -0.13733 | 60.8963 | 122.7127 | 122.9782 | -123.2346 | -123.2254
2828.7656 | 123.1842 | -60.9146 | 62.027 | 0.24773 | -0.005866 | -0.012198 | 0.0066928 | 0.060532 | -0.0067185 | 0.065488 | -61.0428 | 62.1689 | -61.2488 | -61.1618 | 61.7706 | -0.036621 | -0.11444 | 0.09613 | 62.1002 | -61.1984 | -0.33417 | 0.14191 | -0.12817 | -0.24719 | -0.25635 | -0.28381 | 0.073242 | 0.20599 | 60.8002 | 61.0107 | 122.6852 | 123.0835 | -0.12817 | 123.0148 | 60.878 | -0.28381 | 123.0835 | -0.12817 | 60.878 | 122.6852 | 123.0148 | -123.2758 | -123.2254
2829.7656 | 123.1613 | -60.9009 | 62.059 | 0.2401 | -0.0060798 | -0.013266 | 0.0049838 | 0.060532 | -0.0075729 | 0.067411 | -61.0703 | 62.1597 | -61.2854 | -61.1481 | 61.7661 | -0.032043 | -0.091553 | 0.073242 | 62.0956 | -61.2534 | -0.38452 | 0.10071 | -0.16937 | -0.24719 | -0.29297 | -0.35248 | 0.036621 | 0.21515 | 60.8093 | 60.9741 | 122.6669 | 123.0606 | -0.16937 | 122.9965 | 60.8688 | -0.35248 | 123.0606 | -0.16937 | 60.8688 | 122.6669 | 122.9965 | -123.3444 | -123.3124
2830.7656 | 123.2208 | -60.9146 | 62.0087 | 0.27061 | -0.004798 | -0.011771 | 0.0056246 | 0.061814 | -0.0062911 | 0.066343 | -61.0199 | 62.146 | -61.2442 | -61.116 | 61.7981 | -0.032043 | -0.19226 | 0.17395 | 62.0636 | -61.2213 | -0.32959 | 0.13733 | -0.10529 | -0.20142 | -0.21057 | -0.3067 | 0.054932 | 0.22431 | 60.7224 | 61.0886 | 122.7127 | 123.0606 | -0.10529 | 122.9782 | 60.8826 | -0.3067 | 123.0606 | -0.10529 | 60.8826 | 122.7127 | 122.9782 | -123.2529 | -123.23
2831.7656 | 123.23 | -60.9055 | 62.0407 | 0.27824 | -0.0056524 | -0.0085663 | 0.0062656 | 0.061814 | -0.0065047 | 0.066129 | -61.0199 | 62.1597 | -61.2305 | -61.1298 | 61.8256 | 0.009155 | -0.13733 | 0.10986 | 62.1048 | -61.2122 | -0.32501 | 0.11902 | -0.11444 | -0.2243 | -0.21515 | -0.3067 | 0.064087 | 0.21057 | 60.7681 | 61.0153 | 122.731 | 123.0652 | -0.11444 | 123.0103 | 60.9146 | -0.3067 | 123.0652 | -0.11444 | 60.9146 | 122.731 | 123.0103 | -123.2712 | -123.2529
2832.7656 | 123.1888 | -60.8917 | 62.0361 | 0.23247 | -0.0056524 | -0.010916 | 0.003702 | 0.061173 | -0.0045821 | 0.067197 | -61.0291 | 62.1826 | -61.2534 | -61.1435 | 61.8027 | 0 | -0.16937 | 0.14648 | 62.0728 | -61.2625 | -0.36163 | 0.14648 | -0.13733 | -0.25177 | -0.23346 | -0.37079 | 0.036621 | 0.2243 | 60.7224 | 61.0382 | 122.6944 | 123.0743 | -0.13733 | 122.9645 | 60.8917 | -0.37079 | 123.0743 | -0.13733 | 60.8917 | 122.6944 | 122.9645 | -123.2895 | -123.2986
2833.7656 | 123.1796 | -60.9055 | 61.9995 | 0.25536 | -0.0028754 | -0.0096343 | 0.0030612 | 0.060746 | -0.0028731 | 0.066129 | -61.0382 | 62.1643 | -61.235 | -61.1481 | 61.7935 | -0.009155 | -0.15564 | 0.10986 | 62.0956 | -61.2717 | -0.32959 | 0.16479 | -0.13275 | -0.24261 | -0.20599 | -0.36621 | 0.09613 | 0.19684 | 60.7498 | 61.0153 | 122.699 | 123.0698 | -0.13275 | 123.0011 | 60.8963 | -0.36621 | 123.0698 | -0.13275 | 60.8963 | 122.699 | 123.0011 | -123.2346 | -123.2712
2834.7656 | 123.2071 | -60.9055 | 62.0132 | 0.21721 | -0.0084296 | -0.0062163 | -0.00035676 | 0.05861 | -0.0043685 | 0.068052 | -61.0428 | 62.1323 | -61.235 | -61.1343 | 61.8073 | 0.018311 | -0.16022 | 0.15106 | 62.0819 | -61.203 | -0.32959 | 0.11902 | -0.13733 | -0.22888 | -0.20599 | -0.29755 | 0.068664 | 0.19226 | 60.7452 | 61.0565 | 122.7127 | 123.0377 | -0.13733 | 122.9874 | 60.9238 | -0.29755 | 123.0377 | -0.13733 | 60.9238 | 122.7127 | 122.9874 | -123.2483 | -123.2162
2835.7656 | 123.175 | -60.9055 | 62.0499 | 0.2401 | -0.0090704 | -0.0094207 | 0.0069064 | 0.062241 | -0.0043685 | 0.067411 | -61.0611 | 62.1643 | -61.2762 | -61.1435 | 61.7798 | -0.036621 | -0.1236 | 0.10986 | 62.1323 | -61.2259 | -0.37079 | 0.11444 | -0.15564 | -0.23804 | -0.27008 | -0.32043 | 0.082397 | 0.21515 | 60.7819 | 61.0153 | 122.6852 | 123.0698 | -0.15564 | 123.0377 | 60.8688 | -0.32043 | 123.0698 | -0.15564 | 60.8688 | 122.6852 | 123.0377 | -123.3261 | -123.2758
2836.7656 | 123.2208 | -60.8826 | 62.0087 | 0.39269 | -0.0052252 | -0.0070709 | 0.0041292 | 0.059037 | -0.0041549 | 0.067838 | -60.9924 | 62.1231 | -61.2396 | -61.0931 | 61.8393 | 0.041199 | -0.21057 | 0.17395 | 62.0865 | -61.2396 | -0.35706 | 0.11444 | -0.10986 | -0.21057 | -0.16937 | -0.35706 | 0.07782 | 0.24719 | 60.672 | 61.0565 | 122.7219 | 123.0057 | -0.10986 | 122.9691 | 60.9238 | -0.35706 | 123.0057 | -0.10986 | 60.9238 | 122.7219 | 122.9691 | -123.2483 | -123.2483
2837.7656 | 123.1613 | -60.91 | 62.0361 | 0.26299 | -0.0073614 | -0.013907 | 0.0064792 | 0.061814 | -0.0056503 | 0.067197 | -61.0565 | 62.1735 | -61.2625 | -61.1618 | 61.7889 | -0.041199 | -0.11444 | 0.091553 | 62.1231 | -61.2396 | -0.35248 | 0.13733 | -0.14648 | -0.25177 | -0.24719 | -0.32959 | 0.086975 | 0.20599 | 60.7956 | 61.0016 | 122.699 | 123.0835 | -0.14648 | 123.0331 | 60.8688 | -0.32959 | 123.0835 | -0.14648 | 60.8688 | 122.699 | 123.0331 | -123.2986 | -123.2758
2838.7656 | 123.23 | -60.9055 | 62.0132 | 0.2935 | -0.005866 | -0.013266 | 0.0041292 | 0.0616 | -0.0073593 | 0.067624 | -60.9924 | 62.1323 | -61.2579 | -61.1114 | 61.8347 | 0.027466 | -0.20599 | 0.15106 | 62.0819 | -61.235 | -0.35248 | 0.11902 | -0.086975 | -0.20599 | -0.17853 | -0.32959 | 0.068664 | 0.2655 | 60.6995 | 61.0565 | 122.7402 | 123.0377 | -0.086975 | 122.9874 | 60.9329 | -0.32959 | 123.0377 | -0.086975 | 60.9329 | 122.7402 | 122.9874 | -123.2712 | -123.2483
2839.7656 | 123.1842 | -60.8963 | 62.0224 | 0.14854 | -0.0071478 | -0.012198 | -0.002493 | 0.061387 | -0.0056503 | 0.068052 | -61.0794 | 62.1048 | -61.2122 | -61.1389 | 61.8073 | 0.022888 | -0.11902 | 0.16937 | 62.0865 | -61.1984 | -0.31586 | 0.082397 | -0.18311 | -0.24262 | -0.21515 | -0.30212 | 0.064087 | 0.13275 | 60.7773 | 61.0657 | 122.7036 | 123.0011 | -0.18311 | 122.9828 | 60.9192 | -0.30212 | 123.0011 | -0.18311 | 60.9192 | 122.7036 | 122.9828 | -123.2346 | -123.2208
2840.7656 | 123.1796 | -60.9146 | 62.0407 | 0.14854 | -0.0080024 | -0.013052 | -0.00099756 | 0.057969 | -0.0039413 | 0.065702 | -61.0611 | 62.114 | -61.2442 | -61.1435 | 61.8027 | 0.022888 | -0.10071 | 0.17395 | 62.0682 | -61.2305 | -0.32959 | 0.073243 | -0.14648 | -0.22888 | -0.23804 | -0.31586 | 0.027466 | 0.18311 | 60.8139 | 61.0886 | 122.7173 | 123.0286 | -0.14648 | 122.9828 | 60.9375 | -0.31586 | 123.0286 | -0.14648 | 60.9375 | 122.7173 | 122.9828 | -123.2849 | -123.2712
2841.7656 | 123.2071 | -60.8917 | 62.0316 | 0.34691 | -0.0037298 | -0.01348 | 0.00712 | 0.060532 | -0.0062911 | 0.067197 | -61.0062 | 62.146 | -61.2442 | -61.1023 | 61.821 | 0.036621 | -0.2243 | 0.16937 | 62.0911 | -61.2076 | -0.35248 | 0.11444 | -0.11444 | -0.21057 | -0.21057 | -0.31586 | 0.059509 | 0.23804 | 60.6674 | 61.0611 | 122.7127 | 123.0377 | -0.11444 | 122.9828 | 60.9283 | -0.31586 | 123.0377 | -0.11444 | 60.9283 | 122.7127 | 122.9828 | -123.2758 | -123.2391
2842.7656 | 123.2254 | -60.9009 | 62.0178 | 0.1104 | -0.0050116 | -0.010916 | 0.0049838 | 0.06096 | -0.0062911 | 0.067838 | -61.0474 | 62.1185 | -61.2442 | -61.0886 | 61.821 | 0.013733 | -0.21515 | 0.17853 | 62.0499 | -61.2076 | -0.34332 | 0.10071 | -0.14648 | -0.18768 | -0.19684 | -0.3067 | 0.032044 | 0.19684 | 60.6857 | 61.0794 | 122.7219 | 123.0194 | -0.14648 | 122.9507 | 60.9146 | -0.3067 | 123.0194 | -0.14648 | 60.9146 | 122.7219 | 122.9507 | -123.262 | -123.2254
2843.7656 | 123.2025 | -60.9055 | 62.0132 | 0.087509 | -0.0090704 | -0.011771 | 0.002634 | 0.060319 | -0.0047957 | 0.066556 | -60.9833 | 62.1185 | -61.2305 | -61.0977 | 61.8439 | 0.036621 | -0.19684 | 0.17395 | 62.059 | -61.2259 | -0.32501 | 0.10529 | -0.077819 | -0.19226 | -0.16937 | -0.32043 | 0.045776 | 0.24719 | 60.7086 | 61.0794 | 122.7493 | 123.024 | -0.077819 | 122.9645 | 60.9421 | -0.32043 | 123.024 | -0.077819 | 60.9421 | 122.7493 | 122.9645 | -123.2437 | -123.2391
2844.7656 | 123.23 | -60.8826 | 62.0224 | 0.19432 | -0.0056524 | -0.0068573 | 0.005411 | 0.060532 | -0.0067185 | 0.066343 | -60.997 | 62.1506 | -61.2305 | -61.0931 | 61.8393 | 0.018311 | -0.20599 | 0.16022 | 62.0865 | -61.2488 | -0.3479 | 0.12817 | -0.11444 | -0.21057 | -0.18311 | -0.36621 | 0.064087 | 0.23346 | 60.6766 | 61.0428 | 122.7219 | 123.0331 | -0.11444 | 122.9691 | 60.9009 | -0.36621 | 123.0331 | -0.11444 | 60.9009 | 122.7219 | 122.9691 | -123.2529 | -123.2712
2845.7656 | 123.2529 | -60.8963 | 62.027 | 0.98015 | -0.0088568 | -0.0085663 | 0.0028476 | 0.060319 | -0.0045821 | 0.064207 | -60.9421 | 62.1094 | -61.2213 | -61.0703 | 61.8484 | 0.022888 | -0.21515 | 0.16937 | 62.0499 | -61.203 | -0.32501 | 0.082397 | -0.045777 | -0.17395 | -0.17853 | -0.3067 | 0.022888 | 0.27923 | 60.6812 | 61.0657 | 122.7448 | 123.0057 | -0.045777 | 122.9462 | 60.9192 | -0.3067 | 123.0057 | -0.045777 | 60.9192 | 122.7448 | 122.9462 | -123.2483 | -123.23
2846.7656 | 123.2117 | -60.9009 | 62.0224 | 0.27061 | -0.0086432 | -0.0079253 | 0.0041292 | 0.060746 | -0.0052231 | 0.066129 | -61.0565 | 62.1231 | -61.2579 | -61.0611 | 61.8668 | 0.041199 | -0.19684 | 0.18768 | 62.059 | -61.2076 | -0.35706 | 0.10071 | -0.15564 | -0.16022 | -0.15564 | -0.3067 | 0.036621 | 0.20142 | 60.704 | 61.0886 | 122.7676 | 123.024 | -0.15564 | 122.9599 | 60.9421 | -0.3067 | 123.024 | -0.15564 | 60.9421 | 122.7676 | 122.9599 | -123.2803 | -123.23
2847.7656 | 123.1888 | -60.8917 | 62.0407 | 0.10277 | -0.009284 | -0.011771 | -0.0012112 | 0.057328 | -0.0047957 | 0.065916 | -61.0657 | 62.1185 | -61.2625 | -60.9924 | 61.8805 | -0.022888 | -0.14191 | 0.14191 | 62.1185 | -61.203 | -0.37079 | 0.07782 | -0.17395 | -0.10071 | -0.16022 | -0.31128 | 0.07782 | 0.19684 | 60.7498 | 61.0336 | 122.7722 | 123.0103 | -0.17395 | 123.0103 | 60.8688 | -0.31128 | 123.0103 | -0.17395 | 60.8688 | 122.7722 | 123.0103 | -123.3032 | -123.2437
2848.7656 | 123.2666 | -60.878 | 62.0636 | 0.28587 | -0.0069342 | -0.0085663 | 0.0034884 | 0.059037 | -0.0075729 | 0.065275 | -61.0062 | 62.0911 | -61.2076 | -61.1893 | 61.647 | 0.032043 | -0.1236 | 0.20142 | 62.0773 | -61.1893 | -0.32959 | 0.027465 | -0.12817 | -0.31128 | -0.41657 | -0.31128 | 0.013733 | 0.20142 | 60.7544 | 61.0794 | 122.525 | 122.9691 | -0.12817 | 122.9553 | 60.91 | -0.31128 | 122.9691 | -0.12817 | 60.91 | 122.525 | 122.9553 | -123.2712 | -123.2529
2849.7656 | 123.2941 | -60.8963 | 62.0132 | 0.2935 | -0.0080024 | -0.013266 | 0.0062656 | 0.06096 | -0.0039413 | 0.06677 | -60.9924 | 62.1231 | -61.2442 | -61.0794 | 61.8301 | 0.041199 | -0.24261 | 0.013733 | 62.0682 | -61.2259 | -0.3479 | 0.10986 | -0.096131 | -0.18311 | -0.18311 | -0.32959 | 0.054931 | 0.25177 | 60.6537 | 60.91 | 122.7264 | 123.0194 | -0.096131 | 122.9645 | 60.9375 | -0.32959 | 123.0194 | -0.096131 | 60.9375 | 122.7264 | 122.9645 | -123.2574 | -123.2391
2850.7656 | 123.23 | -60.9055 | 62.0132 | 0.25536 | -0.0071478 | -0.01647 | 0.0034884 | 0.061173 | -0.0071457 | 0.063993 | -60.997 | 62.114 | -61.2396 | -61.1069 | 61.8439 | 0.041199 | -0.19226 | 0.16937 | 62.0911 | -61.1755 | -0.33417 | 0.10071 | -0.091552 | -0.20142 | -0.16937 | -0.27008 | 0.077819 | 0.24262 | 60.7132 | 61.0748 | 122.7493 | 123.0194 | -0.091552 | 122.9965 | 60.9467 | -0.27008 | 123.0194 | -0.091552 | 60.9467 | 122.7493 | 122.9965 | -123.2529 | -123.1888
2851.7656 | 123.2391 | -60.9055 | 62.0224 | 0.18669 | -0.009284 | -0.010703 | 0.0030612 | 0.059037 | -0.0050095 | 0.067197 | -61.0107 | 62.1094 | -61.203 | -61.0931 | 61.8393 | 0.036621 | -0.21973 | 0.18768 | 62.0407 | -61.203 | -0.29755 | 0.086975 | -0.10529 | -0.18768 | -0.18311 | -0.29755 | 0.01831 | 0.19226 | 60.6857 | 61.0931 | 122.7448 | 123.0148 | -0.10529 | 122.9462 | 60.9421 | -0.29755 | 123.0148 | -0.10529 | 60.9421 | 122.7448 | 122.9462 | -123.2254 | -123.2254
2852.7656 | 123.2391 | -60.8917 | 62.0224 | 0.087509 | -0.005866 | -0.012412 | 0.0058382 | 0.059251 | -0.0056503 | 0.066984 | -60.9741 | 62.1323 | -61.1893 | -61.1023 | 61.8484 | 0.032043 | -0.2243 | 0.17853 | 62.0865 | -61.1801 | -0.29755 | 0.10986 | -0.082397 | -0.21057 | -0.17395 | -0.28839 | 0.064087 | 0.21515 | 60.6674 | 61.0703 | 122.7402 | 123.024 | -0.082397 | 122.9782 | 60.9238 | -0.28839 | 123.024 | -0.082397 | 60.9238 | 122.7402 | 122.9782 | -123.2117 | -123.2025
2853.7656 | 123.2346 | -60.8871 | 62.0178 | 0.2401 | -0.0073614 | -0.010916 | 0.0028476 | 0.05861 | -0.0058639 | 0.065916 | -61.0748 | 62.0956 | -61.2579 | -61.0794 | 61.8576 | 0.045776 | -0.2243 | 0.16022 | 62.0636 | -61.2122 | -0.37079 | 0.07782 | -0.18768 | -0.19226 | -0.16022 | -0.32501 | 0.045777 | 0.18311 | 60.6628 | 61.0474 | 122.7448 | 122.9828 | -0.18768 | 122.9507 | 60.9329 | -0.32501 | 122.9828 | -0.18768 | 60.9329 | 122.7448 | 122.9507 | -123.2758 | -123.23
2854.7812 | 123.1842 | -60.8917 | 62.027 | 0.1638 | -0.0088568 | -0.0096343 | -0.00099756 | 0.057542 | -0.0062911 | 0.067624 | -61.0519 | 62.1094 | -61.2213 | -61.1343 | 61.8301 | 0 | -0.11902 | 0.16479 | 62.0911 | -61.1755 | -0.32959 | 0.082397 | -0.16022 | -0.24261 | -0.19684 | -0.28381 | 0.064086 | 0.16937 | 60.7727 | 61.0565 | 122.7219 | 123.0011 | -0.16022 | 122.9828 | 60.8917 | -0.28381 | 123.0011 | -0.16022 | 60.8917 | 122.7219 | 122.9828 | -123.2483 | -123.2025
2855.7656 | 123.2895 | -60.8734 | 62.0407 | 0.27061 | -0.0054388 | -0.015189 | 0.0075472 | 0.059251 | -0.0080001 | 0.067197 | -60.997 | 62.0956 | -61.2534 | -61.0977 | 61.8484 | 0.073242 | -0.44403 | 0.032043 | 62.027 | -61.2259 | -0.37994 | 0.054932 | -0.1236 | -0.2243 | -0.19226 | -0.35248 | -0.013732 | 0.25635 | 60.4294 | 60.9055 | 122.7219 | 122.9691 | -0.1236 | 122.9004 | 60.9467 | -0.35248 | 122.9691 | -0.1236 | 60.9467 | 122.7219 | 122.9004 | -123.2941 | -123.2666
2856.7812 | 123.2254 | -60.8551 | 62.0224 | 0.28587 | -0.0056524 | -0.011343 | 0.001993 | 0.062241 | -0.0071457 | 0.067838 | -61.0107 | 62.0956 | -61.2442 | -61.0886 | 61.8439 | 0.022888 | -0.21057 | 0.18768 | 62.0819 | -61.1938 | -0.3891 | 0.073242 | -0.15564 | -0.23346 | -0.17853 | -0.33875 | 0.059509 | 0.23346 | 60.6445 | 61.0428 | 122.699 | 122.9507 | -0.15564 | 122.937 | 60.878 | -0.33875 | 122.9507 | -0.15564 | 60.878 | 122.699 | 122.937 | -123.2666 | -123.2162
2857.7656 | 123.2391 | -60.8871 | 62.027 | 0.07988 | -0.0077888 | -0.0098479 | 0.005411 | 0.059464 | -0.0067185 | 0.066984 | -60.9787 | 62.1368 | -61.2259 | -61.0977 | 61.853 | 0.036621 | -0.21057 | 0.17395 | 62.0682 | -61.203 | -0.33874 | 0.10986 | -0.091553 | -0.21057 | -0.17395 | -0.31586 | 0.041198 | 0.24719 | 60.6766 | 61.0611 | 122.7402 | 123.024 | -0.091553 | 122.9553 | 60.9238 | -0.31586 | 123.024 | -0.091553 | 60.9238 | 122.7402 | 122.9553 | -123.2529 | -123.23
2858.7656 | 123.2346 | -60.91 | 62.0361 | -0.51521 | -0.0054388 | -0.0094207 | 0.0047702 | 0.061387 | -0.0073593 | 0.065488 | -60.9055 | 62.1185 | -61.2259 | -61.0931 | 61.8439 | 0.018311 | -0.21973 | 0.17395 | 62.0911 | -61.2076 | -0.31586 | 0.082397 | 0.004577 | -0.18311 | -0.19226 | -0.29755 | 0.054931 | 0.32043 | 60.6903 | 61.084 | 122.7539 | 123.0286 | 0.004577 | 123.0011 | 60.9283 | -0.29755 | 123.0286 | 0.004577 | 60.9283 | 122.7539 | 123.0011 | -123.262 | -123.2437
2859.7656 | 123.2437 | -60.878 | 62.027 | 0.26299 | -0.0060798 | -0.012839 | 0.0081882 | 0.061173 | -0.0082137 | 0.066556 | -60.9924 | 62.0865 | -61.2305 | -61.0153 | 61.8759 | 0.027466 | -0.1831 | 0.19684 | 62.0728 | -61.1755 | -0.35248 | 0.059509 | -0.11444 | -0.13733 | -0.15106 | -0.29755 | 0.045776 | 0.23804 | 60.6949 | 61.0748 | 122.7539 | 122.9645 | -0.11444 | 122.9507 | 60.9055 | -0.29755 | 122.9645 | -0.11444 | 60.9055 | 122.7539 | 122.9507 | -123.2574 | -123.2025
2860.7656 | 123.2346 | -60.878 | 62.0407 | 0.2935 | -0.0094976 | -0.010489 | 0.0069064 | 0.059037 | -0.0062911 | 0.067624 | -61.0062 | 62.1094 | -61.2213 | -61.084 | 61.8668 | -0.1236 | -0.27466 | 0.27924 | 62.059 | -61.203 | -0.34332 | 0.068665 | -0.12817 | -0.20599 | -0.17395 | -0.32501 | 0.018311 | 0.21515 | 60.6033 | 61.1572 | 122.7448 | 122.9874 | -0.12817 | 122.937 | 60.7544 | -0.32501 | 122.9874 | -0.12817 | 60.7544 | 122.7448 | 122.937 | -123.262 | -123.2437
2861.7656 | 123.2208 | -60.878 | 62.0407 | 0.1104 | -0.0073614 | -0.014548 | 0.0015658 | 0.056473 | -0.0047957 | 0.066556 | -61.0657 | 62.0956 | -61.2625 | -61.1435 | 61.8164 | 0.009155 | -0.09613 | 0.15106 | 62.114 | -61.1893 | -0.38452 | 0.054932 | -0.18768 | -0.2655 | -0.2243 | -0.31128 | 0.073243 | 0.19684 | 60.7819 | 61.0291 | 122.6944 | 122.9736 | -0.18768 | 122.9919 | 60.8871 | -0.31128 | 122.9736 | -0.18768 | 60.8871 | 122.6944 | 122.9919 | -123.3032 | -123.23
2862.7656 | 123.2391 | -60.8871 | 62.0178 | 0.17143 | -0.006507 | -0.0087799 | 0.0086154 | 0.058396 | -0.0071457 | 0.06677 | -60.997 | 62.0773 | -61.2488 | -61.0886 | 61.8439 | 0.027466 | -0.21515 | 0.16022 | 62.0911 | -61.2213 | -0.36163 | 0.05951 | -0.10986 | -0.20142 | -0.17395 | -0.33417 | 0.073242 | 0.25177 | 60.672 | 61.0474 | 122.731 | 122.9645 | -0.10986 | 122.9782 | 60.9146 | -0.33417 | 122.9645 | -0.10986 | 60.9146 | 122.731 | 122.9782 | -123.2666 | -123.2391
2863.7656 | 123.2208 | -60.8917 | 62.0224 | 0.54527 | -0.005866 | -0.010275 | 0.0058382 | 0.059891 | -0.0060775 | 0.066556 | -60.9787 | 62.1048 | -61.2488 | -61.0886 | 61.8439 | 0.045776 | -0.22888 | 0.17395 | 62.0819 | -61.2122 | -0.35705 | 0.082397 | -0.086975 | -0.19684 | -0.17853 | -0.32043 | 0.059509 | 0.27008 | 60.6628 | 61.0657 | 122.7356 | 122.9965 | -0.086975 | 122.9736 | 60.9375 | -0.32043 | 122.9965 | -0.086975 | 60.9375 | 122.7356 | 122.9736 | -123.2712 | -123.2346
2864.7656 | 123.2071 | -60.8734 | 62.0178 | 0.92674 | -0.0088568 | -0.01113 | 0.0032748 | 0.060532 | -0.0082137 | 0.066343 | -60.9192 | 62.1002 | -61.2122 | -61.0703 | 61.8484 | 0.022888 | -0.2243 | 0.16479 | 62.0499 | -61.2122 | -0.33875 | 0.082398 | -0.045776 | -0.19684 | -0.16937 | -0.33875 | 0.032044 | 0.29297 | 60.6491 | 61.0382 | 122.7219 | 122.9736 | -0.045776 | 122.9233 | 60.8963 | -0.33875 | 122.9736 | -0.045776 | 60.8963 | 122.7219 | 122.9233 | -123.23 | -123.23
2865.7656 | 123.2208 | -60.8871 | 62.027 | 0.2935 | -0.0062934 | -0.01348 | 0.004343 | 0.058182 | -0.0062911 | 0.066129 | -60.9879 | 62.1002 | -61.2442 | -61.0794 | 61.8713 | 0.059509 | -0.20142 | 0.19226 | 62.0819 | -61.1984 | -0.35706 | 0.073242 | -0.10071 | -0.19226 | -0.15564 | -0.31128 | 0.054931 | 0.25635 | 60.6857 | 61.0794 | 122.7585 | 122.9874 | -0.10071 | 122.9691 | 60.9467 | -0.31128 | 122.9874 | -0.10071 | 60.9467 | 122.7585 | 122.9691 | -123.2712 | -123.2254
2866.7656 | 123.2208 | -60.8871 | 62.0132 | 0.28587 | -0.0080024 | -0.010275 | 0.0077608 | 0.057328 | -0.0090683 | 0.063993 | -60.9924 | 62.1002 | -61.2305 | -61.2579 | 61.7798 | 0.07782 | -0.16022 | 0.21515 | 62.0865 | -61.1755 | -0.34332 | 0.086975 | -0.10529 | -0.37079 | -0.23346 | -0.28839 | 0.073242 | 0.23804 | 60.7269 | 61.1023 | 122.6669 | 122.9874 | -0.10529 | 122.9736 | 60.965 | -0.28839 | 122.9874 | -0.10529 | 60.965 | 122.6669 | 122.9736 | -123.2437 | -123.1888
2867.7656 | 123.2483 | -60.8963 | 62.0087 | 0.27824 | -0.0043708 | -0.0098479 | 0.0039156 | 0.060319 | -0.0054367 | 0.066556 | -60.9833 | 62.1048 | -61.2396 | -61.0794 | 61.8393 | 0.022888 | -0.21973 | 0.16479 | 62.0728 | -61.2167 | -0.34332 | 0.09613 | -0.086975 | -0.18311 | -0.16937 | -0.32043 | 0.064087 | 0.25635 | 60.6766 | 61.0611 | 122.7356 | 123.0011 | -0.086975 | 122.9691 | 60.9192 | -0.32043 | 123.0011 | -0.086975 | 60.9192 | 122.7356 | 122.9691 | -123.2483 | -123.2254
2868.7656 | 123.1796 | -60.8826 | 62.0407 | 0.15617 | -0.0077888 | -0.0096343 | 0.00092504 | 0.059037 | -0.0065047 | 0.065702 | -61.0611 | 62.1231 | -61.2122 | -61.1481 | 61.8256 | 0.013733 | -0.1236 | 0.17395 | 62.1185 | -61.1755 | -0.32959 | 0.082398 | -0.17853 | -0.2655 | -0.21515 | -0.29297 | 0.07782 | 0.15106 | 60.759 | 61.0565 | 122.7081 | 123.0057 | -0.17853 | 123.0011 | 60.8963 | -0.29297 | 123.0057 | -0.17853 | 60.8963 | 122.7081 | 123.0011 | -123.2529 | -123.2162
2869.7656 | 123.2208 | -60.8688 | 62.0361 | 0.10277 | -0.007575 | -0.012198 | 0.0056246 | 0.060532 | -0.0067185 | 0.065488 | -61.0062 | 62.1048 | -61.235 | -61.0977 | 61.8439 | 0.032043 | -0.22888 | 0.15564 | 62.0636 | -61.203 | -0.36621 | 0.068664 | -0.13733 | -0.22888 | -0.19226 | -0.33417 | 0.027466 | 0.22888 | 60.64 | 61.0245 | 122.7127 | 122.9736 | -0.13733 | 122.9324 | 60.9009 | -0.33417 | 122.9736 | -0.13733 | 60.9009 | 122.7127 | 122.9324 | -123.2712 | -123.2391
2870.7656 | 123.2208 | -60.9009 | 61.9904 | 0.24773 | -0.0060798 | -0.013693 | 0.008829 | 0.059251 | -0.0082137 | 0.067197 | -61.0062 | 62.1323 | -61.2488 | -61.1069 | 61.8301 | 0.032043 | -0.19226 | 0.16479 | 62.0682 | -61.203 | -0.3479 | 0.14191 | -0.10529 | -0.20599 | -0.16022 | -0.30212 | 0.07782 | 0.24261 | 60.7086 | 61.0657 | 122.731 | 123.0331 | -0.10529 | 122.9691 | 60.9329 | -0.30212 | 123.0331 | -0.10529 | 60.9329 | 122.731 | 122.9691 | -123.2391 | -123.1934
2871.7656 | 123.2162 | -60.9009 | 62.0361 | 0.27824 | -0.0067206 | -0.013907 | 0.0032748 | 0.065446 | -0.0030869 | 0.066343 | -60.9833 | 62.0956 | -61.2396 | -61.0474 | 61.9492 | 0.14191 | -0.20142 | 0.19684 | 62.0911 | -61.1984 | -0.33874 | 0.059509 | -0.082397 | -0.14648 | -0.086975 | -0.29755 | 0.054931 | 0.25635 | 60.6995 | 61.0977 | 122.85 | 122.9965 | -0.082397 | 122.9919 | 61.0428 | -0.29755 | 122.9965 | -0.082397 | 61.0428 | 122.85 | 122.9919 | -123.2758 | -123.2346
2872.7656 | 123.1796 | -60.9238 | 61.9858 | 0.27824 | -0.0062934 | -0.0087799 | 0.0073336 | 0.061387 | -0.0084273 | 0.068693 | -60.965 | 62.1185 | -61.2579 | -61.0886 | 61.853 | 0.036621 | -0.23804 | 0.19684 | 62.1002 | -61.1984 | -0.33417 | 0.13275 | -0.041199 | -0.1648 | -0.13275 | -0.27466 | 0.11444 | 0.29297 | 60.6857 | 61.1206 | 122.7768 | 123.0423 | -0.041199 | 123.024 | 60.9604 | -0.27466 | 123.0423 | -0.041199 | 60.9604 | 122.7768 | 123.024 | -123.2437 | -123.1842
2873.7656 | 123.1659 | -60.9238 | 62.0453 | 0.26299 | -0.0039434 | -0.011771 | 0.0066928 | 0.059678 | -0.0047957 | 0.067838 | -61.0428 | 62.1643 | -61.235 | -61.1435 | 61.7889 | -0.032043 | -0.14191 | 0.10071 | 62.0911 | -61.2488 | -0.31128 | 0.11902 | -0.11902 | -0.21973 | -0.25635 | -0.32501 | 0.045776 | 0.19226 | 60.7819 | 61.0245 | 122.7127 | 123.0881 | -0.11902 | 123.0148 | 60.8917 | -0.32501 | 123.0881 | -0.11902 | 60.8917 | 122.7127 | 123.0148 | -123.2803 | -123.2941
2874.7656 | 123.2208 | -60.9055 | 62.0178 | 0.19432 | -0.0056524 | -0.012412 | 0.0039156 | 0.060532 | -0.0060775 | 0.066556 | -61.0062 | 62.1185 | -61.2534 | -61.0977 | 61.853 | 0.022888 | -0.21515 | 0.16022 | 62.0728 | -61.2213 | -0.3479 | 0.10071 | -0.10071 | -0.19226 | -0.1648 | -0.31586 | 0.054932 | 0.24719 | 60.6903 | 61.0657 | 122.7585 | 123.024 | -0.10071 | 122.9782 | 60.9283 | -0.31586 | 123.024 | -0.10071 | 60.9283 | 122.7585 | 122.9782 | -123.2712 | -123.2391
2875.7656 | 123.1842 | -60.9009 | 62.0224 | 0.20195 | -0.0073614 | -0.011984 | -0.0012112 | 0.060746 | -0.0060775 | 0.066343 | -61.0611 | 62.1231 | -61.2259 | -61.1481 | 61.8347 | 0.013733 | -0.12817 | 0.15564 | 62.114 | -61.1801 | -0.32501 | 0.10071 | -0.16022 | -0.24719 | -0.18768 | -0.27924 | 0.091553 | 0.16479 | 60.7727 | 61.0565 | 122.7356 | 123.024 | -0.16022 | 123.0148 | 60.9146 | -0.27924 | 123.024 | -0.16022 | 60.9146 | 122.7356 | 123.0148 | -123.2483 | -123.2025
2876.7656 | 123.2025 | -60.9055 | 62.0178 | 0.22484 | -0.0056524 | -0.010062 | 0.0049838 | 0.06096 | -0.0054367 | 0.067624 | -61.0428 | 62.1414 | -61.2762 | -61.1435 | 61.8027 | -0.022888 | -0.17853 | 0.12817 | 62.0911 | -61.2167 | -0.37079 | 0.1236 | -0.13733 | -0.23804 | -0.21515 | -0.31128 | 0.073242 | 0.23346 | 60.7269 | 61.0336 | 122.7081 | 123.0469 | -0.13733 | 122.9965 | 60.8826 | -0.31128 | 123.0469 | -0.13733 | 60.8826 | 122.7081 | 122.9965 | -123.2941 | -123.2346
2877.7656 | 123.1888 | -60.9146 | 62.0178 | 0.27061 | -0.0062934 | -0.0089935 | 0.005411 | 0.060532 | -0.0054367 | 0.065488 | -61.0565 | 62.1643 | -61.2671 | -61.1481 | 61.7889 | -0.036621 | -0.11902 | 0.10986 | 62.1002 | -61.2259 | -0.35248 | 0.14648 | -0.14191 | -0.23346 | -0.22888 | -0.31128 | 0.082398 | 0.21057 | 60.7956 | 61.0245 | 122.7036 | 123.0789 | -0.14191 | 123.0148 | 60.878 | -0.31128 | 123.0789 | -0.14191 | 60.878 | 122.7036 | 123.0148 | -123.2849 | -123.2437
2878.7656 | 123.23 | -60.8963 | 61.9995 | 0.22484 | -0.006507 | -0.0068573 | 0.003702 | 0.06096 | -0.0077865 | 0.066129 | -61.0199 | 62.146 | -61.2488 | -61.1206 | 61.8393 | 0.032043 | -0.20142 | 0.15564 | 62.0865 | -61.2213 | -0.35248 | 0.14648 | -0.1236 | -0.2243 | -0.16022 | -0.32501 | 0.086975 | 0.22888 | 60.6949 | 61.0519 | 122.7356 | 123.0423 | -0.1236 | 122.9828 | 60.9283 | -0.32501 | 123.0423 | -0.1236 | 60.9283 | 122.7356 | 122.9828 | -123.2483 | -123.2208
2879.7656 | 123.2483 | -60.9009 | 62.0087 | 0.28587 | -0.0062934 | -0.0055755 | 0.005411 | 0.06096 | -0.0052231 | 0.068479 | -61.0382 | 62.1414 | -61.2671 | -61.116 | 61.8347 | 0.009155 | -0.2243 | 0.14191 | 62.0956 | -61.2259 | -0.36621 | 0.13275 | -0.13733 | -0.21515 | -0.17395 | -0.32501 | 0.086975 | 0.22888 | 60.6766 | 61.0428 | 122.7356 | 123.0423 | -0.13733 | 122.9965 | 60.91 | -0.32501 | 123.0423 | -0.13733 | 60.91 | 122.7356 | 122.9965 | -123.2758 | -123.2346
2880.7656 | 123.2346 | -60.91 | 62.027 | 0.22484 | -0.0062934 | -0.0079253 | 0.0049838 | 0.060319 | -0.0054367 | 0.065061 | -61.0474 | 62.1826 | -61.2488 | -61.1389 | 61.7889 | -0.022888 | -0.16022 | 0.11902 | 62.1048 | -61.2305 | -0.33874 | 0.15564 | -0.13733 | -0.22888 | -0.23804 | -0.32043 | 0.077819 | 0.20142 | 60.7498 | 61.0291 | 122.699 | 123.0927 | -0.13733 | 123.0148 | 60.8871 | -0.32043 | 123.0927 | -0.13733 | 60.8871 | 122.699 | 123.0148 | -123.2758 | -123.2574
2881.7656 | 123.1842 | -60.91 | 62.027 | 0.2935 | -0.0054388 | -0.0096343 | 0.0066928 | 0.059678 | -0.0037277 | 0.065916 | -61.0519 | 62.1643 | -61.2534 | -61.1618 | 61.7889 | -0.036621 | -0.13275 | 0.091553 | 62.1094 | -61.2579 | -0.34332 | 0.13733 | -0.14191 | -0.25177 | -0.23804 | -0.3479 | 0.082397 | 0.20142 | 60.7773 | 61.0016 | 122.699 | 123.0743 | -0.14191 | 123.0194 | 60.8734 | -0.3479 | 123.0743 | -0.14191 | 60.8734 | 122.699 | 123.0194 | -123.2803 | -123.2849
2882.7656 | 123.2071 | -60.8963 | 62.0178 | 0.17906 | -0.0062934 | -0.012625 | 7.0444e-05 | 0.060746 | -0.0045821 | 0.067197 | -61.0153 | 62.1277 | -61.2167 | -61.116 | 61.853 | 0.041199 | -0.19684 | 0.16937 | 62.0819 | -61.2076 | -0.32043 | 0.10986 | -0.11902 | -0.21973 | -0.1648 | -0.31128 | 0.064087 | 0.20142 | 60.6995 | 61.0657 | 122.7493 | 123.024 | -0.11902 | 122.9782 | 60.9375 | -0.31128 | 123.024 | -0.11902 | 60.9375 | 122.7493 | 122.9782 | -123.2346 | -123.2254
2883.7656 | 123.1522 | -60.8963 | 62.0499 | 0.24773 | -0.0039434 | -0.011557 | 0.0069064 | 0.0616 | -0.0060775 | 0.065916 | -61.0703 | 62.1918 | -61.2762 | -61.1893 | 61.7569 | -0.064087 | -0.07782 | 0.073242 | 62.1185 | -61.2488 | -0.37994 | 0.14191 | -0.17395 | -0.29297 | -0.29297 | -0.35248 | 0.068664 | 0.20599 | 60.8185 | 60.9695 | 122.6532 | 123.0881 | -0.17395 | 123.0148 | 60.8322 | -0.35248 | 123.0881 | -0.17395 | 60.8322 | 122.6532 | 123.0148 | -123.3261 | -123.2986
2884.7656 | 123.1522 | -60.9238 | 62.0682 | 0.18669 | -0.0052252 | -0.0096343 | 0.0041292 | 0.062669 | -0.0052231 | 0.066343 | -61.0657 | 62.1826 | -61.2534 | -61.1938 | 61.7798 | -0.064087 | -0.054932 | 0.068665 | 62.0911 | -61.2579 | -0.32959 | 0.11444 | -0.14191 | -0.27008 | -0.28839 | -0.33417 | 0.022888 | 0.18768 | 60.8688 | 60.9924 | 122.7036 | 123.1064 | -0.14191 | 123.0148 | 60.8597 | -0.33417 | 123.1064 | -0.14191 | 60.8597 | 122.7036 | 123.0148 | -123.3215 | -123.3261
2885.7812 | 123.2483 | -60.8917 | 62.0407 | 0.0035856 | -0.0088568 | -0.012625 | -0.0033476 | 0.058823 | -0.0052231 | 0.068693 | -61.0657 | 62.1231 | -61.2305 | -61.1069 | 61.8713 | 0.073242 | -0.086975 | 0.22888 | 62.0865 | -61.1664 | -0.33874 | 0.082398 | -0.17395 | -0.21515 | -0.16937 | -0.27466 | 0.045777 | 0.16479 | 60.8047 | 61.1206 | 122.7631 | 123.0148 | -0.17395 | 122.9782 | 60.965 | -0.27466 | 123.0148 | -0.17395 | 60.965 | 122.7631 | 122.9782 | -123.2712 | -123.2071
2886.7656 | 123.175 | -60.8871 | 62.027 | 0.26299 | -0.005866 | -0.0087799 | 0.0064792 | 0.059464 | -0.0056503 | 0.066984 | -61.0382 | 62.1506 | -61.2488 | -61.1481 | 61.7935 | -0.027466 | -0.13275 | 0.10529 | 62.1094 | -61.2396 | -0.36163 | 0.1236 | -0.15106 | -0.26093 | -0.23346 | -0.35248 | 0.082397 | 0.21057 | 60.7544 | 60.9924 | 122.6807 | 123.0377 | -0.15106 | 122.9965 | 60.8597 | -0.35248 | 123.0377 | -0.15106 | 60.8597 | 122.6807 | 122.9965 | -123.2758 | -123.2666
2887.7656 | 123.1522 | -60.9329 | 62.0361 | 0.25536 | -0.004798 | -0.0072845 | 0.0066928 | 0.060746 | -0.0047957 | 0.065916 | -61.0291 | 62.1735 | -61.2579 | -61.1572 | 61.7798 | -0.041199 | -0.10986 | 0.07782 | 62.1231 | -61.2579 | -0.32501 | 0.13733 | -0.096131 | -0.22431 | -0.25635 | -0.32501 | 0.086975 | 0.22888 | 60.8231 | 61.0107 | 122.7127 | 123.1064 | -0.096131 | 123.056 | 60.8917 | -0.32501 | 123.1064 | -0.096131 | 60.8917 | 122.7127 | 123.056 | -123.2941 | -123.2941
2888.7656 | 123.2025 | -60.9009 | 62.0087 | 0.22484 | -0.0077888 | -0.0096343 | 0.0013522 | 0.059037 | -0.0062911 | 0.068693 | -61.0153 | 62.1368 | -61.2305 | -61.1252 | 61.8484 | 0.027466 | -0.19684 | 0.18768 | 62.0865 | -61.2167 | -0.32959 | 0.12817 | -0.11444 | -0.2243 | -0.16022 | -0.31586 | 0.07782 | 0.21515 | 60.704 | 61.0886 | 122.7493 | 123.0377 | -0.11444 | 122.9874 | 60.9283 | -0.31586 | 123.0377 | -0.11444 | 60.9283 | 122.7493 | 122.9874 | -123.2391 | -123.2254
2889.7656 | 123.2117 | -60.8734 | 62.027 | 0.21721 | -0.007575 | -0.012839 | 0.0024202 | 0.057755 | -0.0067185 | 0.063993 | -61.0107 | 62.1231 | -61.2442 | -61.0931 | 61.8301 | 0.036621 | -0.20599 | 0.1831 | 62.0819 | -61.2442 | -0.37079 | 0.09613 | -0.13733 | -0.21973 | -0.19684 | -0.37079 | 0.054931 | 0.23346 | 60.6674 | 61.0565 | 122.7036 | 122.9965 | -0.13733 | 122.9553 | 60.91 | -0.37079 | 122.9965 | -0.13733 | 60.91 | 122.7036 | 122.9553 | -123.2712 | -123.2712
2890.7812 | 123.1934 | -60.8963 | 62.0819 | -0.20241 | -0.010352 | -0.014548 | 0.003702 | 0.057542 | -0.0058639 | 0.065916 | -61.0062 | 62.1414 | -61.2213 | -61.0794 | 61.8576 | 0.10071 | 0.013733 | 0.27008 | 62.114 | -61.1847 | -0.32501 | 0.059509 | -0.10986 | -0.18311 | -0.2243 | -0.28839 | 0.032044 | 0.21515 | 60.91 | 61.1664 | 122.7539 | 123.0377 | -0.10986 | 123.0103 | 60.997 | -0.28839 | 123.0377 | -0.10986 | 60.997 | 122.7539 | 123.0103 | -123.3032 | -123.2666
2891.7656 | 123.1659 | -60.9009 | 62.0361 | 0.22484 | -0.0050116 | -0.012625 | 0.0081882 | 0.058823 | -0.0058639 | 0.068693 | -61.0428 | 62.1689 | -61.2259 | -61.1572 | 61.7844 | -0.032043 | -0.12817 | 0.10071 | 62.1094 | -61.2671 | -0.32501 | 0.13275 | -0.14191 | -0.25635 | -0.25177 | -0.36621 | 0.073242 | 0.1831 | 60.7727 | 61.0016 | 122.6852 | 123.0698 | -0.14191 | 123.0103 | 60.8688 | -0.36621 | 123.0698 | -0.14191 | 60.8688 | 122.6852 | 123.0103 | -123.262 | -123.3032
2892.7656 | 123.1659 | -60.9238 | 62.0544 | 0.23247 | -0.0054388 | -0.011984 | 0.0051974 | 0.061814 | -0.0054367 | 0.066343 | -61.0519 | 62.1872 | -61.2579 | -61.1664 | 61.7798 | -0.045776 | -0.11444 | 0.09613 | 62.1414 | -61.2488 | -0.33417 | 0.13275 | -0.12817 | -0.24262 | -0.27466 | -0.32501 | 0.086975 | 0.20599 | 60.8093 | 61.0199 | 122.7036 | 123.111 | -0.12817 | 123.0652 | 60.878 | -0.32501 | 123.111 | -0.12817 | 60.878 | 122.7036 | 123.0652 | -123.3124 | -123.3032
2893.7656 | 123.1842 | -60.9238 | 62.059 | 0.25536 | -0.0056524 | -0.012198 | 0.0051974 | 0.06096 | -0.0052231 | 0.066129 | -61.0794 | 62.2009 | -61.2579 | -61.1664 | 61.7523 | -0.059509 | -0.086975 | 0.082397 | 62.1414 | -61.2488 | -0.33417 | 0.14191 | -0.15564 | -0.24262 | -0.3067 | -0.32501 | 0.082397 | 0.17853 | 60.8368 | 61.0062 | 122.6761 | 123.1247 | -0.15564 | 123.0652 | 60.8643 | -0.32501 | 123.1247 | -0.15564 | 60.8643 | 122.6761 | 123.0652 | -123.317 | -123.3078
2894.7656 | 123.23 | -60.9192 | 62.0361 | 0.25536 | -0.0056524 | -0.0094207 | 0.00071144 | 0.061173 | -0.0058639 | 0.068265 | -61.0153 | 62.114 | -61.2305 | -61.1069 | 61.8347 | 0.027466 | -0.20599 | 0.1831 | 62.1231 | -61.2167 | -0.31128 | 0.07782 | -0.096131 | -0.18768 | -0.20142 | -0.29755 | 0.086975 | 0.21515 | 60.7132 | 61.1023 | 122.7539 | 123.0331 | -0.096131 | 123.0423 | 60.9467 | -0.29755 | 123.0331 | -0.096131 | 60.9467 | 122.7539 | 123.0423 | -123.2666 | -123.2529
2895.7812 | 123.2071 | -60.8688 | 62.0773 | -0.18715 | -0.0097114 | -0.0081389 | -0.00035676 | 0.059251 | -0.0056503 | 0.066556 | -61.0016 | 62.1506 | -61.2213 | -61.0886 | 61.8805 | 0.10986 | 0 | 0.30212 | 62.1231 | -61.1938 | -0.35248 | 0.073242 | -0.13275 | -0.21973 | -0.19684 | -0.32501 | 0.045776 | 0.21973 | 60.8688 | 61.171 | 122.7493 | 123.0194 | -0.13275 | 122.9919 | 60.9787 | -0.32501 | 123.0194 | -0.13275 | 60.9787 | 122.7493 | 122.9919 | -123.2986 | -123.2712
2896.7656 | 123.23 | -60.9009 | 62.0178 | 0.26299 | -0.0062934 | -0.011557 | 0.004343 | 0.059891 | -0.0054367 | 0.065916 | -60.9787 | 62.1231 | -61.2259 | -61.0428 | 61.8393 | 0.045776 | -0.19684 | 0.1831 | 62.1094 | -61.2122 | -0.32501 | 0.10529 | -0.07782 | -0.14191 | -0.17853 | -0.31128 | 0.091553 | 0.24719 | 60.704 | 61.084 | 122.7402 | 123.024 | -0.07782 | 123.0103 | 60.9467 | -0.31128 | 123.024 | -0.07782 | 60.9467 | 122.7402 | 123.0103 | -123.2437 | -123.23
2897.7656 | 123.1384 | -60.91 | 62.0865 | 0.20958 | -0.0039434 | -0.011343 | 0.0064792 | 0.061173 | -0.0052231 | 0.065916 | -61.0794 | 62.178 | -61.2488 | -61.3907 | 61.4365 | -0.26093 | 0.21057 | 0.082397 | 62.1506 | -61.2579 | -0.33874 | 0.091553 | -0.16937 | -0.48065 | -0.65002 | -0.3479 | 0.064087 | 0.16937 | 61.1206 | 60.9924 | 122.3465 | 123.0881 | -0.16937 | 123.0606 | 60.6491 | -0.3479 | 123.0881 | -0.16937 | 60.6491 | 122.3465 | 123.0606 | -123.3353 | -123.3444
2898.7656 | 123.1293 | -60.9329 | 62.0178 | 0.25536 | -0.006507 | -0.010275 | 0.00712 | 0.062455 | -0.0054367 | 0.067411 | -61.0565 | 62.2192 | -61.2946 | -61.1984 | 61.7523 | -0.045776 | -0.054932 | 0.068665 | 62.1231 | -61.2396 | -0.36163 | 0.20142 | -0.1236 | -0.2655 | -0.2655 | -0.3067 | 0.10529 | 0.23804 | 60.878 | 61.0016 | 122.6852 | 123.1522 | -0.1236 | 123.056 | 60.8871 | -0.3067 | 123.1522 | -0.1236 | 60.8871 | 122.6852 | 123.056 | -123.3124 | -123.2574
2899.7656 | 123.1338 | -60.9238 | 62.0682 | -0.17189 | -0.0035162 | -0.010703 | 0.0032748 | 0.061387 | -0.0058639 | 0.065488 | -61.0977 | 62.2375 | -61.2442 | -61.1893 | 61.7386 | -0.059509 | -0.050354 | 0.054932 | 62.1323 | -61.2396 | -0.32044 | 0.16937 | -0.17395 | -0.2655 | -0.32959 | -0.31586 | 0.064087 | 0.14648 | 60.8734 | 60.9787 | 122.6624 | 123.1613 | -0.17395 | 123.056 | 60.8643 | -0.31586 | 123.1613 | -0.17395 | 60.8643 | 122.6624 | 123.056 | -123.3124 | -123.3078
2900.7656 | 123.2483 | -60.8917 | 62.0728 | -0.13374 | -0.0045844 | -0.011984 | -0.0012112 | 0.061814 | -0.0077865 | 0.065916 | -60.9879 | 62.1689 | -61.203 | -61.0565 | 61.8988 | 0.14648 | -0.068665 | 0.30212 | 62.1277 | -61.1984 | -0.31128 | 0.09613 | -0.09613 | -0.16479 | -0.17395 | -0.3067 | 0.054932 | 0.21515 | 60.8231 | 61.1938 | 122.7905 | 123.0606 | -0.09613 | 123.0194 | 61.0382 | -0.3067 | 123.0606 | -0.09613 | 61.0382 | 122.7905 | 123.0194 | -123.2758 | -123.2712
2901.7656 | 123.2391 | -60.9375 | 62.0773 | 0.18669 | -0.005866 | -0.010703 | 0.00712 | 0.063096 | -0.0054367 | 0.066556 | -61.0703 | 62.2101 | -61.2534 | -61.1893 | 61.7523 | -0.082397 | -0.022888 | -0.21973 | 62.1185 | -61.2946 | -0.31586 | 0.13275 | -0.13275 | -0.25177 | -0.32501 | -0.35706 | 0.041198 | 0.18311 | 60.9146 | 60.7178 | 122.6898 | 123.1476 | -0.13275 | 123.056 | 60.8551 | -0.35706 | 123.1476 | -0.13275 | 60.8551 | 122.6898 | 123.056 | -123.3307 | -123.3719
2902.7656 | 123.2529 | -60.9009 | 62.0316 | 0.36217 | -0.0071478 | -0.016257 | 0.0030612 | 0.062455 | -0.0047957 | 0.066556 | -60.9879 | 62.1323 | -61.2213 | -61.1114 | 61.8439 | 0.032043 | -0.21057 | 0.17395 | 62.059 | -61.2305 | -0.32043 | 0.10071 | -0.086975 | -0.21057 | -0.18768 | -0.32959 | 0.027466 | 0.23346 | 60.6903 | 61.0748 | 122.7448 | 123.0331 | -0.086975 | 122.9599 | 60.9329 | -0.32959 | 123.0331 | -0.086975 | 60.9329 | 122.7448 | 122.9599 | -123.2529 | -123.262
2903.7656 | 123.1201 | -60.9467 | 62.0636 | 0.1104 | -0.004798 | -0.0079253 | 0.0051974 | 0.062241 | -0.0058639 | 0.065916 | -61.0565 | 62.2284 | -61.2671 | -61.1984 | 61.7477 | -0.064087 | -0.013733 | 0.054932 | 62.1643 | -61.2579 | -0.32044 | 0.16479 | -0.10986 | -0.25177 | -0.31586 | -0.31128 | 0.10071 | 0.21057 | 60.9329 | 61.0016 | 122.6944 | 123.175 | -0.10986 | 123.111 | 60.8826 | -0.31128 | 123.175 | -0.10986 | 60.8826 | 122.6944 | 123.111 | -123.3307 | -123.3215
2904.7656 | 123.0927 | -60.9329 | 62.059 | 0.10277 | -0.006507 | -0.0089935 | 0.005411 | 0.062455 | -0.0073593 | 0.065702 | -61.0474 | 62.2467 | -61.2625 | -61.171 | 61.7569 | -0.036621 | 0.013733 | 0.10529 | 62.1323 | -61.2717 | -0.32959 | 0.18768 | -0.11444 | -0.23804 | -0.30212 | -0.33875 | 0.073242 | 0.21515 | 60.9467 | 61.0382 | 122.6898 | 123.1796 | -0.11444 | 123.0652 | 60.8963 | -0.33875 | 123.1796 | -0.11444 | 60.8963 | 122.6898 | 123.0652 | -123.3215 | -123.3307
2905.7656 | 123.1155 | -60.9283 | 62.0361 | 0.11803 | -0.0041572 | -0.0045075 | 0.0062656 | 0.061814 | -0.0054367 | 0.066343 | -61.084 | 62.2421 | -61.2762 | -61.2259 | 61.7386 | -0.073242 | -0.027466 | 0.059509 | 62.146 | -61.2671 | -0.3479 | 0.20599 | -0.15564 | -0.29755 | -0.29755 | -0.33875 | 0.10986 | 0.19226 | 60.9009 | 60.9879 | 122.6669 | 123.1705 | -0.15564 | 123.0743 | 60.8551 | -0.33875 | 123.1705 | -0.15564 | 60.8551 | 122.6669 | 123.0743 | -123.3124 | -123.3032
2906.7656 | 123.0789 | -60.9375 | 62.0453 | 0.2401 | -0.0054388 | -0.0064301 | 0.0051974 | 0.062455 | -0.0041549 | 0.066984 | -61.0886 | 62.2284 | -61.2625 | -61.2076 | 61.7294 | -0.073242 | 0 | 0.064087 | 62.146 | -61.2946 | -0.32501 | 0.18311 | -0.15106 | -0.27008 | -0.31586 | -0.35706 | 0.10071 | 0.17395 | 60.9375 | 61.0016 | 122.6669 | 123.1659 | -0.15106 | 123.0835 | 60.8643 | -0.35706 | 123.1659 | -0.15106 | 60.8643 | 122.6669 | 123.0835 | -123.3078 | -123.3398
2907.7656 | 123.0698 | -60.9375 | 62.0773 | 0.1104 | -0.0035162 | -0.010062 | 0.0058382 | 0.062882 | -0.0054367 | 0.068693 | -61.0382 | 62.2421 | -61.2579 | -61.1984 | 61.7752 | -0.064087 | -0.004578 | 0.082397 | 62.1597 | -61.2625 | -0.32044 | 0.16479 | -0.10071 | -0.26093 | -0.30212 | -0.32501 | 0.082397 | 0.21973 | 60.9329 | 61.0199 | 122.7127 | 123.1796 | -0.10071 | 123.0972 | 60.8734 | -0.32501 | 123.1796 | -0.10071 | 60.8734 | 122.7127 | 123.0972 | -123.3353 | -123.3398
2908.7656 | 123.111 | -60.9421 | 62.0728 | 0.095139 | -0.0050116 | -0.011343 | 0.0051974 | 0.06096 | -0.0056503 | 0.068479 | -61.0428 | 62.2421 | -61.2305 | -61.1893 | 61.7706 | -0.036621 | 0.009155 | 0.10071 | 62.1597 | -61.2854 | -0.28839 | 0.16937 | -0.10071 | -0.24719 | -0.30212 | -0.34332 | 0.086975 | 0.18768 | 60.9512 | 61.0428 | 122.7127 | 123.1842 | -0.10071 | 123.1018 | 60.9055 | -0.34332 | 123.1842 | -0.10071 | 60.9055 | 122.7127 | 123.1018 | -123.3032 | -123.3582
2909.7656 | 123.1705 | -60.9512 | 62.0361 | 0.22484 | -0.0052252 | -0.0096343 | 0.0030612 | 0.06096 | -0.0033005 | 0.067838 | -61.0565 | 62.2101 | -61.235 | -61.1938 | 61.7706 | -0.032043 | -0.10071 | 0.091553 | 62.1414 | -61.2442 | -0.28381 | 0.17395 | -0.10529 | -0.24262 | -0.2655 | -0.29297 | 0.10529 | 0.17853 | 60.8505 | 61.0428 | 122.7219 | 123.1613 | -0.10529 | 123.0927 | 60.9192 | -0.29297 | 123.1613 | -0.10529 | 60.9192 | 122.7219 | 123.0927 | -123.2712 | -123.2803
2910.7656 | 123.1293 | -60.9192 | 62.0636 | 0.018845 | -0.0026618 | -0.011984 | 0.0066928 | 0.060532 | -0.0043685 | 0.068265 | -61.0062 | 62.2421 | -61.2488 | -61.1618 | 61.7844 | 0 | 0.009155 | 0.13733 | 62.1552 | -61.2534 | -0.32959 | 0.17853 | -0.086976 | -0.24261 | -0.27924 | -0.33417 | 0.091552 | 0.24261 | 60.9283 | 61.0565 | 122.7036 | 123.1613 | -0.086976 | 123.0743 | 60.9192 | -0.33417 | 123.1613 | -0.086976 | 60.9192 | 122.7036 | 123.0743 | -123.3124 | -123.317
2911.7656 | 123.1384 | -60.9055 | 62.0773 | -0.14137 | -0.0045844 | -0.011984 | 0.0047702 | 0.062241 | -0.0037277 | 0.067411 | -61.0016 | 62.2375 | -61.2396 | -61.1481 | 61.821 | 0.032043 | -0.013733 | 0.17395 | 62.1368 | -61.2534 | -0.33417 | 0.16022 | -0.09613 | -0.24261 | -0.25635 | -0.3479 | 0.059509 | 0.23804 | 60.8917 | 61.0794 | 122.7264 | 123.143 | -0.09613 | 123.0423 | 60.9375 | -0.3479 | 123.143 | -0.09613 | 60.9375 | 122.7264 | 123.0423 | -123.317 | -123.3307
2912.7656 | 123.1155 | -60.9192 | 62.059 | 0.10277 | -0.0054388 | -0.0064301 | 0.0056246 | 0.06096 | -0.0028731 | 0.06677 | -61.0336 | 62.2284 | -61.235 | -61.1893 | 61.7752 | -0.018311 | 0.004578 | 0.1236 | 62.1277 | -61.2442 | -0.31586 | 0.16937 | -0.11444 | -0.27008 | -0.28381 | -0.32501 | 0.068665 | 0.20142 | 60.9238 | 61.0428 | 122.6944 | 123.1476 | -0.11444 | 123.0469 | 60.9009 | -0.32501 | 123.1476 | -0.11444 | 60.9009 | 122.6944 | 123.0469 | -123.2941 | -123.3032
2913.7656 | 123.1338 | -60.9238 | 62.0636 | 0.072251 | -0.0071478 | -0.0089935 | 0.0056246 | 0.064164 | -0.0056503 | 0.066556 | -61.0107 | 62.2559 | -61.2808 | -61.171 | 61.7935 | -0.009155 | 0 | 0.15564 | 62.1689 | -61.2579 | -0.35706 | 0.19226 | -0.086975 | -0.24719 | -0.27008 | -0.33417 | 0.10528 | 0.27008 | 60.9238 | 61.0794 | 122.7173 | 123.1796 | -0.086975 | 123.0927 | 60.9146 | -0.33417 | 123.1796 | -0.086975 | 60.9146 | 122.7173 | 123.0927 | -123.3444 | -123.3215
2914.7656 | 123.1476 | -60.9329 | 62.0636 | 0.072251 | -0.004798 | -0.0074981 | 0.0058382 | 0.063096 | -0.0050095 | 0.064847 | -60.997 | 62.2284 | -61.2167 | -61.1481 | 61.7935 | 0.013733 | -0.004578 | 0.17853 | 62.1506 | -61.2717 | -0.28381 | 0.16479 | -0.064087 | -0.21515 | -0.27008 | -0.33875 | 0.086975 | 0.21973 | 60.9283 | 61.1114 | 122.7264 | 123.1613 | -0.064087 | 123.0835 | 60.9467 | -0.33875 | 123.1613 | -0.064087 | 60.9467 | 122.7264 | 123.0835 | -123.2803 | -123.3353
2915.7656 | 123.1796 | -60.9192 | 62.0728 | -0.55336 | -0.006507 | -0.0057891 | 0.005411 | 0.063096 | -0.0065047 | 0.065916 | -61.0199 | 62.2421 | -61.2396 | -61.1343 | 61.8301 | 0.041199 | 0 | 0.17853 | 62.1689 | -61.2579 | -0.32043 | 0.16937 | -0.10071 | -0.21515 | -0.24262 | -0.33875 | 0.09613 | 0.21973 | 60.9192 | 61.0977 | 122.7493 | 123.1613 | -0.10071 | 123.0881 | 60.9604 | -0.33875 | 123.1613 | -0.10071 | 60.9604 | 122.7493 | 123.0881 | -123.3124 | -123.3307
2916.7656 | 123.111 | -60.9558 | 62.0956 | 0.18669 | -0.0077888 | -0.0092071 | 0.0045566 | 0.06096 | -0.0052231 | 0.066129 | -61.0886 | 62.2284 | -61.2579 | -61.2076 | 61.734 | -0.050354 | -0.42572 | -0.18768 | 62.114 | -61.3129 | -0.30212 | 0.13275 | -0.13275 | -0.25177 | -0.36163 | -0.35706 | 0.018311 | 0.16937 | 60.5301 | 60.7681 | 122.6898 | 123.1842 | -0.13275 | 123.0698 | 60.9055 | -0.35706 | 123.1842 | -0.13275 | 60.9055 | 122.6898 | 123.0698 | -123.3536 | -123.4085
2917.7656 | 123.175 | -60.9146 | 62.0544 | -0.011673 | -0.0033026 | -0.01348 | 0.001993 | 0.062669 | -0.0062911 | 0.066984 | -60.9924 | 62.2375 | -61.2488 | -61.1343 | 61.8256 | 0.068665 | 0.018311 | 0.20599 | 62.178 | -61.2488 | -0.33417 | 0.18311 | -0.07782 | -0.21973 | -0.22888 | -0.33417 | 0.1236 | 0.25635 | 60.9329 | 61.1206 | 122.7402 | 123.1522 | -0.07782 | 123.0927 | 60.9833 | -0.33417 | 123.1522 | -0.07782 | 60.9833 | 122.7402 | 123.0927 | -123.3032 | -123.3032
2918.7656 | 123.1796 | -60.9009 | 62.0911 | -0.16426 | -0.0041572 | -0.0087799 | 0.0049838 | 0.062028 | -0.0037277 | 0.068906 | -60.9924 | 62.2559 | -61.2167 | -61.1298 | 61.8256 | 0.050354 | 0.018311 | 0.2243 | 62.1689 | -61.2442 | -0.31586 | 0.16479 | -0.091553 | -0.22888 | -0.2655 | -0.34332 | 0.07782 | 0.2243 | 60.9192 | 61.1252 | 122.7264 | 123.1567 | -0.091553 | 123.0698 | 60.9512 | -0.34332 | 123.1567 | -0.091553 | 60.9512 | 122.7264 | 123.0698 | -123.3078 | -123.3353
2919.7656 | 123.1567 | -60.9055 | 62.0728 | 0.0035856 | -0.0054388 | -0.01113 | 0.0073336 | 0.059251 | -0.0062911 | 0.066343 | -60.9924 | 62.2375 | -61.2259 | -61.1023 | 61.8073 | 0.07782 | -0.009155 | 0.18768 | 62.1689 | -61.2305 | -0.32043 | 0.16479 | -0.086975 | -0.19684 | -0.2655 | -0.32501 | 0.09613 | 0.23346 | 60.8963 | 61.0931 | 122.7127 | 123.143 | -0.086975 | 123.0743 | 60.9833 | -0.32501 | 123.143 | -0.086975 | 60.9833 | 122.7127 | 123.0743 | -123.2986 | -123.3032
2920.7656 | 123.1613 | -60.9238 | 62.059 | -0.04982 | -0.0054388 | -0.0087799 | 0.0045566 | 0.063523 | -0.0071457 | 0.066984 | -61.0153 | 62.2375 | -61.2442 | -61.1252 | 61.8164 | 0.050354 | 0.018311 | 0.20599 | 62.146 | -61.2717 | -0.32044 | 0.17853 | -0.091553 | -0.20142 | -0.24262 | -0.3479 | 0.086975 | 0.22888 | 60.9421 | 61.1298 | 122.7402 | 123.1613 | -0.091553 | 123.0698 | 60.9741 | -0.3479 | 123.1613 | -0.091553 | 60.9741 | 122.7402 | 123.0698 | -123.3032 | -123.3307
2921.7812 | 123.1293 | -60.8917 | 62.0773 | -0.24818 | -0.0039434 | -0.011557 | 0.0062656 | 0.062669 | -0.0054367 | 0.065702 | -61.0153 | 62.233 | -61.2259 | -61.1481 | 61.8118 | 0.027466 | 0 | 0.1831 | 62.1643 | -61.2579 | -0.33417 | 0.15564 | -0.1236 | -0.25635 | -0.2655 | -0.36621 | 0.086975 | 0.21057 | 60.8917 | 61.0748 | 122.7036 | 123.1247 | -0.1236 | 123.056 | 60.9192 | -0.36621 | 123.1247 | -0.1236 | 60.9192 | 122.7036 | 123.056 | -123.3032 | -123.3353
2922.7656 | 123.1842 | -60.91 | 62.0728 | -0.10323 | -0.0056524 | -0.014975 | 0.0058382 | 0.061387 | -0.0069321 | 0.065702 | -61.0199 | 62.2513 | -61.2488 | -61.1343 | 61.8256 | 0.059509 | 0.022888 | 0.2243 | 62.146 | -61.2442 | -0.33874 | 0.17853 | -0.10986 | -0.2243 | -0.24719 | -0.33417 | 0.073242 | 0.22888 | 60.9329 | 61.1343 | 122.7356 | 123.1613 | -0.10986 | 123.056 | 60.9695 | -0.33417 | 123.1613 | -0.10986 | 60.9695 | 122.7356 | 123.056 | -123.3215 | -123.317
2923.7656 | 123.1338 | -60.9146 | 62.0636 | 0.095139 | -0.0035162 | -0.012198 | 0.0028476 | 0.063523 | -0.0030869 | 0.067197 | -61.0565 | 62.2421 | -61.2396 | -61.1938 | 61.7523 | -0.041199 | -0.004578 | 0.10529 | 62.1643 | -61.2534 | -0.32501 | 0.17853 | -0.14191 | -0.27924 | -0.31128 | -0.33875 | 0.10071 | 0.1831 | 60.91 | 61.0199 | 122.6669 | 123.1567 | -0.14191 | 123.0789 | 60.8734 | -0.33875 | 123.1567 | -0.14191 | 60.8734 | 122.6669 | 123.0789 | -123.3032 | -123.317
2924.7656 | 123.143 | -60.9055 | 62.0819 | -0.149 | -0.004798 | -0.012625 | 0.0028476 | 0.060532 | -0.0067185 | 0.066556 | -61.0336 | 62.2375 | -61.2396 | -61.1252 | 61.8301 | 0.045776 | 0.082397 | 0.2243 | 62.1872 | -61.2579 | -0.33417 | 0.15564 | -0.12817 | -0.21973 | -0.25177 | -0.35248 | 0.10529 | 0.20599 | 60.9879 | 61.1298 | 122.7356 | 123.143 | -0.12817 | 123.0927 | 60.9512 | -0.35248 | 123.143 | -0.12817 | 60.9512 | 122.7356 | 123.0927 | -123.3215 | -123.3398
2925.7656 | 123.1293 | -60.9192 | 62.0819 | -0.11848 | -0.0067206 | -0.011984 | 0.0017794 | 0.061387 | -0.0080001 | 0.065275 | -61.0519 | 62.2375 | -61.2534 | -61.1664 | 61.8073 | 0.036621 | 0.091553 | 0.20142 | 62.178 | -61.2259 | -0.33417 | 0.15564 | -0.13275 | -0.24719 | -0.27466 | -0.3067 | 0.096131 | 0.20142 | 61.0107 | 61.1206 | 122.7264 | 123.1567 | -0.13275 | 123.0972 | 60.9558 | -0.3067 | 123.1567 | -0.13275 | 60.9558 | 122.7264 | 123.0972 | -123.3353 | -123.3078
2926.7656 | 123.1476 | -60.8871 | 62.0636 | -0.11848 | -0.006507 | -0.0087799 | 0.0062656 | 0.060532 | -0.0058639 | 0.066984 | -61.0062 | 62.2375 | -61.2579 | -61.116 | 61.8118 | 0.054932 | 0.036621 | 0.24261 | 62.1689 | -61.2671 | -0.37079 | 0.17395 | -0.11902 | -0.22888 | -0.25177 | -0.37994 | 0.10528 | 0.25177 | 60.9238 | 61.1298 | 122.699 | 123.1247 | -0.11902 | 123.056 | 60.9421 | -0.37994 | 123.1247 | -0.11902 | 60.9421 | 122.699 | 123.056 | -123.3215 | -123.3307
2927.7656 | 123.1659 | -60.8917 | 62.0773 | -0.14137 | -0.0052252 | -0.011557 | 0.0032748 | 0.061814 | -0.0067185 | 0.066343 | -61.0199 | 62.2101 | -61.2442 | -61.1435 | 61.8164 | 0.050354 | 0.041199 | 0.21973 | 62.2009 | -61.2213 | -0.35248 | 0.13275 | -0.12817 | -0.25177 | -0.26093 | -0.32959 | 0.1236 | 0.22431 | 60.9329 | 61.1115 | 122.7081 | 123.1018 | -0.12817 | 123.0927 | 60.9421 | -0.32959 | 123.1018 | -0.12817 | 60.9421 | 122.7081 | 123.0927 | -123.3215 | -123.2986
2928.7656 | 123.1476 | -60.91 | 62.0865 | -0.11848 | -0.0060798 | -0.013266 | 0.0028476 | 0.0616 | -0.0056503 | 0.06677 | -61.0336 | 62.2513 | -61.2442 | -61.1389 | 61.8118 | 0.054932 | 0.073242 | 0.21973 | 62.146 | -61.2305 | -0.33417 | 0.1648 | -0.1236 | -0.22888 | -0.27466 | -0.32043 | 0.059509 | 0.21057 | 60.9833 | 61.1298 | 122.7219 | 123.1613 | -0.1236 | 123.056 | 60.965 | -0.32043 | 123.1613 | -0.1236 | 60.965 | 122.7219 | 123.056 | -123.3307 | -123.317
2929.7656 | 123.1613 | -60.9055 | 62.0865 | -0.149 | -0.0062934 | -0.014548 | 0.0030612 | 0.061814 | -0.0052231 | 0.066556 | -61.0336 | 62.2055 | -61.235 | -61.1526 | 61.8073 | 0.041199 | 0.09613 | 0.18768 | 62.1918 | -61.2488 | -0.32959 | 0.11902 | -0.12817 | -0.24719 | -0.27924 | -0.34332 | 0.10529 | 0.20142 | 61.0016 | 61.0931 | 122.7127 | 123.111 | -0.12817 | 123.0972 | 60.9467 | -0.34332 | 123.111 | -0.12817 | 60.9467 | 122.7127 | 123.0972 | -123.3215 | -123.3353
2930.7656 | 123.1659 | -60.8963 | 62.0682 | 0.011215 | -0.0062934 | -0.0072845 | 0.003702 | 0.062455 | -0.0020187 | 0.066343 | -61.0153 | 62.2284 | -61.2488 | -61.1389 | 61.7889 | 0 | -0.022888 | 0.17395 | 62.146 | -61.2717 | -0.35248 | 0.16022 | -0.11902 | -0.24262 | -0.27924 | -0.37537 | 0.07782 | 0.23346 | 60.8734 | 61.0703 | 122.6852 | 123.1247 | -0.11902 | 123.0423 | 60.8963 | -0.37537 | 123.1247 | -0.11902 | 60.8963 | 122.6852 | 123.0423 | -123.317 | -123.3398
2931.7656 | 123.1384 | -60.9146 | 62.0911 | -0.18715 | -0.0062934 | -0.013052 | 0.00092504 | 0.06096 | -0.0062911 | 0.066343 | -61.0474 | 62.2192 | -61.2488 | -61.171 | 61.8027 | 0.045776 | 0.10986 | 0.19226 | 62.1735 | -61.2259 | -0.33417 | 0.12817 | -0.13275 | -0.25635 | -0.28839 | -0.31128 | 0.082398 | 0.20142 | 61.0245 | 61.1069 | 122.7173 | 123.1338 | -0.13275 | 123.0881 | 60.9604 | -0.31128 | 123.1338 | -0.13275 | 60.9604 | 122.7173 | 123.0881 | -123.3398 | -123.317
2932.7656 | 123.1522 | -60.8917 | 62.1002 | -0.10323 | -0.0060798 | -0.01583 | 0.0011386 | 0.061173 | -0.0041549 | 0.065275 | -61.0519 | 62.233 | -61.2305 | -61.1664 | 61.7935 | 0.027466 | 0.10986 | 0.1831 | 62.1735 | -61.2625 | -0.33874 | 0.13275 | -0.16022 | -0.27466 | -0.3067 | -0.37079 | 0.073242 | 0.17853 | 61.0016 | 61.0748 | 122.6852 | 123.1247 | -0.16022 | 123.0652 | 60.9192 | -0.37079 | 123.1247 | -0.16022 | 60.9192 | 122.6852 | 123.0652 | -123.3307 | -123.3627
2933.7656 | 123.1613 | -60.9009 | 62.0819 | -0.149 | -0.0045844 | -0.014121 | 0.001993 | 0.060746 | -0.0052231 | 0.064847 | -61.0291 | 62.2238 | -61.2442 | -61.1343 | 61.821 | 0.054932 | 0.07782 | 0.21515 | 62.1872 | -61.2396 | -0.34332 | 0.14191 | -0.12817 | -0.23346 | -0.26093 | -0.33874 | 0.10529 | 0.21515 | 60.9787 | 61.116 | 122.7219 | 123.1247 | -0.12817 | 123.0881 | 60.9558 | -0.33874 | 123.1247 | -0.12817 | 60.9558 | 122.7219 | 123.0881 | -123.3261 | -123.3215
2934.7656 | 123.1842 | -60.9055 | 62.0865 | -0.149 | -0.0067206 | -0.013693 | 0.0032748 | 0.061173 | -0.0050095 | 0.068693 | -61.0474 | 62.233 | -61.2442 | -61.1389 | 61.8164 | 0.036621 | 0.091553 | 0.20599 | 62.1597 | -61.2534 | -0.33875 | 0.14648 | -0.14191 | -0.23346 | -0.27008 | -0.3479 | 0.073242 | 0.19684 | 60.997 | 61.1115 | 122.7219 | 123.1384 | -0.14191 | 123.0652 | 60.9421 | -0.3479 | 123.1384 | -0.14191 | 60.9421 | 122.7219 | 123.0652 | -123.3307 | -123.3398
2935.7656 | 123.175 | -60.8917 | 62.1094 | -0.12611 | -0.0069342 | -0.011771 | 0.0034884 | 0.060746 | -0.0054367 | 0.067197 | -61.0382 | 62.2238 | -61.2488 | -61.1618 | 61.7935 | 0.032043 | 0.091553 | 0.19684 | 62.1964 | -61.2213 | -0.35705 | 0.11444 | -0.14648 | -0.27008 | -0.31586 | -0.32959 | 0.086975 | 0.21057 | 60.9833 | 61.0886 | 122.6852 | 123.1155 | -0.14648 | 123.0881 | 60.9238 | -0.32959 | 123.1155 | -0.14648 | 60.9238 | 122.6852 | 123.0881 | -123.3582 | -123.3307
2936.7656 | 123.143 | -60.9146 | 62.1002 | -0.11085 | -0.0067206 | -0.011984 | 0.0017794 | 0.060532 | -0.0047957 | 0.066343 | -61.0611 | 62.233 | -61.235 | -61.1755 | 61.8073 | 0.036621 | 0.09613 | 0.20599 | 62.1689 | -61.235 | -0.32043 | 0.13275 | -0.14648 | -0.26093 | -0.29297 | -0.32043 | 0.068664 | 0.17395 | 61.0107 | 61.1206 | 122.7219 | 123.1476 | -0.14648 | 123.0835 | 60.9512 | -0.32043 | 123.1476 | -0.14648 | 60.9512 | 122.7219 | 123.0835 | -123.3353 | -123.3353
2937.7656 | 123.143 | -60.9055 | 62.0682 | 0.12566 | -0.0054388 | -0.0098479 | 0.0041292 | 0.060746 | -0.0030869 | 0.065488 | -60.965 | 62.2101 | -61.235 | -61.1435 | 61.7844 | 0.036621 | -0.013733 | 0.17395 | 62.1735 | -61.2213 | -0.32959 | 0.14191 | -0.059509 | -0.23804 | -0.28381 | -0.31586 | 0.10529 | 0.27008 | 60.8917 | 61.0794 | 122.6898 | 123.1155 | -0.059509 | 123.0789 | 60.9421 | -0.31586 | 123.1155 | -0.059509 | 60.9421 | 122.6898 | 123.0789 | -123.3032 | -123.2895
2938.7656 | 123.1201 | -60.9009 | 62.1002 | -0.13374 | -0.0073614 | -0.011343 | 0.00092504 | 0.060746 | -0.0065047 | 0.065916 | -61.0703 | 62.1918 | -61.2442 | -61.1618 | 61.7889 | 0.036621 | 0.10986 | 0.18768 | 62.2147 | -61.235 | -0.34332 | 0.091552 | -0.16937 | -0.26092 | -0.31128 | -0.33417 | 0.11444 | 0.17395 | 61.0107 | 61.0886 | 122.6898 | 123.0927 | -0.16937 | 123.1155 | 60.9375 | -0.33417 | 123.0927 | -0.16937 | 60.9375 | 122.6898 | 123.1155 | -123.3444 | -123.3353
2939.7656 | 123.1201 | -60.9146 | 62.1094 | -0.18715 | -0.0073614 | -0.013693 | 0.00028404 | 0.059464 | -0.0060775 | 0.066343 | -60.9787 | 62.2559 | -61.2396 | -61.171 | 61.7706 | 0.009155 | 0.12817 | 0.19684 | 62.2009 | -61.2167 | -0.32501 | 0.14648 | -0.064087 | -0.25635 | -0.33875 | -0.30212 | 0.091553 | 0.26093 | 61.0428 | 61.1114 | 122.6852 | 123.1705 | -0.064087 | 123.1155 | 60.9238 | -0.30212 | 123.1705 | -0.064087 | 60.9238 | 122.6852 | 123.1155 | -123.349 | -123.3261
2940.7656 | 123.1293 | -60.9146 | 62.114 | -0.17189 | -0.0056524 | -0.01348 | 0.0047702 | 0.062241 | -0.0069321 | 0.06442 | -61.0565 | 62.2421 | -61.2625 | -61.1435 | 61.7889 | 0.036621 | 0.091553 | 0.19684 | 62.178 | -61.2259 | -0.3479 | 0.12817 | -0.14191 | -0.22888 | -0.32501 | -0.31128 | 0.064087 | 0.20599 | 61.0062 | 61.1114 | 122.7036 | 123.1567 | -0.14191 | 123.0927 | 60.9512 | -0.31128 | 123.1567 | -0.14191 | 60.9512 | 122.7036 | 123.0927 | -123.3765 | -123.3398
2941.7656 | 123.143 | -60.9009 | 62.1002 | -0.13374 | -0.0060798 | -0.011771 | 0.0047702 | 0.060746 | -0.0052231 | 0.066556 | -61.0565 | 62.2238 | -61.2442 | -61.1481 | 61.7981 | 0.032043 | 0.10529 | 0.19684 | 62.1826 | -61.2259 | -0.34332 | 0.1236 | -0.15564 | -0.24719 | -0.30212 | -0.32501 | 0.082397 | 0.18768 | 61.0062 | 61.0977 | 122.699 | 123.1247 | -0.15564 | 123.0835 | 60.9329 | -0.32501 | 123.1247 | -0.15564 | 60.9329 | 122.699 | 123.0835 | -123.3444 | -123.3261
2942.7656 | 123.1293 | -60.9055 | 62.0911 | -0.15663 | -0.007575 | -0.017752 | 0.0030612 | 0.058823 | -0.0033005 | 0.066129 | -61.0565 | 62.2284 | -61.2167 | -61.1481 | 61.7935 | 0.032043 | 0.086975 | 0.19226 | 62.1689 | -61.2671 | -0.31128 | 0.13733 | -0.15106 | -0.24261 | -0.29755 | -0.36163 | 0.07782 | 0.16022 | 60.9924 | 61.0977 | 122.699 | 123.1339 | -0.15106 | 123.0743 | 60.9375 | -0.36163 | 123.1339 | -0.15106 | 60.9375 | 122.699 | 123.0743 | -123.3078 | -123.3582
2943.7656 | 123.1338 | -60.878 | 62.0819 | 0.072251 | -0.0054388 | -0.0077117 | 0.0041292 | 0.06096 | -0.0035141 | 0.067838 | -61.0062 | 62.2009 | -61.2534 | -61.1206 | 61.7981 | 0.027466 | 0 | 0.17395 | 62.1643 | -61.2488 | -0.37537 | 0.11902 | -0.12817 | -0.24261 | -0.28381 | -0.37079 | 0.082398 | 0.24719 | 60.878 | 61.0519 | 122.6761 | 123.0789 | -0.12817 | 123.0423 | 60.9055 | -0.37079 | 123.0789 | -0.12817 | 60.9055 | 122.6761 | 123.0423 | -123.3353 | -123.3307
2944.7656 | 123.143 | -60.8917 | 62.0407 | 1.5295 | -0.0062934 | -0.0081389 | 0.0073336 | 0.060532 | -0.0050095 | 0.067838 | -60.9558 | 62.2055 | -61.2671 | -61.1252 | 61.821 | 0.027466 | 0 | 0.17853 | 62.1643 | -61.2579 | -0.37537 | 0.1648 | -0.064087 | -0.23346 | -0.21973 | -0.36621 | 0.1236 | 0.31128 | 60.8917 | 61.0703 | 122.7127 | 123.0972 | -0.064087 | 123.056 | 60.9192 | -0.36621 | 123.0972 | -0.064087 | 60.9192 | 122.7127 | 123.056 | -123.3078 | -123.2986
2945.7656 | 123.1201 | -60.9238 | 62.0956 | -1.0874 | -0.0037298 | -0.011557 | 0.0013522 | 0.060319 | -0.0052231 | 0.067624 | -61.116 | 62.2559 | -61.2259 | -61.1847 | 61.7981 | 0.041199 | 0.11444 | 0.21515 | 62.2238 | -61.2167 | -0.30212 | 0.16022 | -0.19226 | -0.26093 | -0.29755 | -0.29297 | 0.12817 | 0.10986 | 61.0382 | 61.1389 | 122.7219 | 123.1796 | -0.19226 | 123.1476 | 60.965 | -0.29297 | 123.1796 | -0.19226 | 60.965 | 122.7219 | 123.1476 | -123.3215 | -123.3124
2946.7656 | 123.1476 | -60.8826 | 62.1094 | -0.19478 | -0.005866 | -0.014334 | 0.00092504 | 0.062882 | -0.0045821 | 0.066343 | -61.0703 | 62.2467 | -61.2213 | -61.1664 | 61.7661 | 0.022888 | 0.10071 | 0.17395 | 62.2055 | -61.2396 | -0.33875 | 0.13733 | -0.18768 | -0.28381 | -0.34332 | -0.35706 | 0.09613 | 0.15106 | 60.9833 | 61.0565 | 122.6486 | 123.1293 | -0.18768 | 123.0881 | 60.9055 | -0.35706 | 123.1293 | -0.18768 | 60.9055 | 122.6486 | 123.0881 | -123.3307 | -123.349
2947.7656 | 123.1659 | -60.9146 | 62.0773 | -0.14137 | -0.0080024 | -0.0085663 | 0.0017794 | 0.062669 | -0.0050095 | 0.06677 | -61.0474 | 62.2513 | -61.2396 | -61.1435 | 61.8027 | 0.032043 | 0.10071 | 0.20142 | 62.1872 | -61.235 | -0.32501 | 0.17395 | -0.13275 | -0.22888 | -0.27466 | -0.32043 | 0.10986 | 0.19226 | 61.0153 | 61.116 | 122.7173 | 123.1659 | -0.13275 | 123.1018 | 60.9467 | -0.32043 | 123.1659 | -0.13275 | 60.9467 | 122.7173 | 123.1018 | -123.317 | -123.3124
2948.7656 | 123.1659 | -60.9055 | 62.0911 | -0.13374 | -0.0073614 | -0.010916 | 0.005411 | 0.060319 | -0.0050095 | 0.067624 | -61.0474 | 62.2147 | -61.2396 | -61.1343 | 61.8027 | 0.045776 | 0.10071 | 0.20599 | 62.1826 | -61.2396 | -0.33417 | 0.1236 | -0.14191 | -0.22888 | -0.28839 | -0.33417 | 0.091553 | 0.19226 | 61.0062 | 61.1115 | 122.7081 | 123.1201 | -0.14191 | 123.0881 | 60.9512 | -0.33417 | 123.1201 | -0.14191 | 60.9512 | 122.7081 | 123.0881 | -123.3307 | -123.3307
2949.7656 | 123.1476 | -60.9055 | 62.114 | -0.149 | -0.0077888 | -0.013052 | 0.0024202 | 0.060105 | -0.0062911 | 0.067838 | -61.0519 | 62.2101 | -61.2488 | -61.1481 | 61.8027 | 0.036621 | 0.10529 | 0.20142 | 62.1689 | -61.2213 | -0.34332 | 0.09613 | -0.14648 | -0.24261 | -0.31128 | -0.31586 | 0.054931 | 0.19684 | 61.0107 | 61.1069 | 122.7081 | 123.1155 | -0.14648 | 123.0743 | 60.9421 | -0.31586 | 123.1155 | -0.14648 | 60.9421 | 122.7081 | 123.0743 | -123.3627 | -123.3353
2950.7656 | 123.1384 | -60.8917 | 62.0819 | 0.034104 | -0.0062934 | -0.011343 | 0.0056246 | 0.057969 | -0.0056503 | 0.065488 | -60.997 | 62.2467 | -61.2305 | -61.1389 | 61.7889 | 0 | -0.013733 | 0.15106 | 62.1826 | -61.2534 | -0.33874 | 0.16479 | -0.10528 | -0.24719 | -0.29297 | -0.36163 | 0.10071 | 0.23346 | 60.878 | 61.0428 | 122.6807 | 123.1384 | -0.10528 | 123.0743 | 60.8917 | -0.36163 | 123.1384 | -0.10528 | 60.8917 | 122.6807 | 123.0743 | -123.3124 | -123.3353
2951.7656 | 123.1613 | -60.9283 | 62.0682 | 0.064621 | -0.005866 | -0.0098479 | 0.0041292 | 0.062028 | -0.0054367 | 0.064847 | -60.9833 | 62.2055 | -61.2442 | -61.1526 | 61.8118 | 0.022888 | -0.009155 | 0.16937 | 62.1552 | -61.2442 | -0.31586 | 0.13733 | -0.054931 | -0.2243 | -0.25635 | -0.31586 | 0.086975 | 0.26093 | 60.9192 | 61.0977 | 122.7402 | 123.1338 | -0.054931 | 123.0835 | 60.9512 | -0.31586 | 123.1338 | -0.054931 | 60.9512 | 122.7402 | 123.0835 | -123.3124 | -123.3124
2952.7656 | 123.143 | -60.9146 | 62.1002 | -0.19478 | -0.0067206 | -0.012625 | 0.002634 | 0.062028 | -0.0065047 | 0.067197 | -61.0428 | 62.233 | -61.2442 | -61.1526 | 61.8073 | 0.036621 | 0.10529 | 0.20599 | 62.178 | -61.2259 | -0.32959 | 0.13275 | -0.12817 | -0.23804 | -0.29297 | -0.31128 | 0.07782 | 0.20142 | 61.0199 | 61.1206 | 122.7219 | 123.1476 | -0.12817 | 123.0927 | 60.9512 | -0.31128 | 123.1476 | -0.12817 | 60.9512 | 122.7219 | 123.0927 | -123.3444 | -123.3261
2953.7656 | 123.1567 | -60.9238 | 62.0819 | -0.19478 | -0.0067206 | -0.0094207 | 0.0015658 | 0.062241 | -0.0050095 | 0.065061 | -61.0519 | 62.233 | -61.2259 | -61.1526 | 61.7981 | 0.041199 | 0.12817 | 0.19684 | 62.1735 | -61.235 | -0.30212 | 0.15106 | -0.12817 | -0.22888 | -0.28381 | -0.31128 | 0.091553 | 0.17395 | 61.0519 | 61.1206 | 122.7219 | 123.1567 | -0.12817 | 123.0972 | 60.965 | -0.31128 | 123.1567 | -0.12817 | 60.965 | 122.7219 | 123.0972 | -123.3078 | -123.317
2954.7656 | 123.175 | -60.8963 | 62.0819 | -0.13374 | -0.0035162 | -0.015616 | 0.0022066 | 0.062455 | -0.0030869 | 0.065916 | -61.0245 | 62.2192 | -61.2442 | -61.1252 | 61.8301 | 0.050354 | 0.050354 | 0.21057 | 62.1689 | -61.2488 | -0.3479 | 0.13733 | -0.12817 | -0.22888 | -0.25177 | -0.35248 | 0.086975 | 0.21973 | 60.9467 | 61.1069 | 122.7264 | 123.1155 | -0.12817 | 123.0652 | 60.9467 | -0.35248 | 123.1155 | -0.12817 | 60.9467 | 122.7264 | 123.0652 | -123.3261 | -123.3307
2955.7656 | 123.1659 | -60.9055 | 62.1002 | -0.149 | -0.006507 | -0.01113 | 0.0039156 | 0.061173 | -0.0047957 | 0.065061 | -61.0291 | 62.2055 | -61.235 | -61.116 | 61.8256 | 0.068665 | 0.045776 | 0.22888 | 62.1872 | -61.2534 | -0.32959 | 0.10529 | -0.1236 | -0.21057 | -0.27466 | -0.3479 | 0.086975 | 0.20599 | 60.9512 | 61.1343 | 122.731 | 123.111 | -0.1236 | 123.0927 | 60.9741 | -0.3479 | 123.111 | -0.1236 | 60.9741 | 122.731 | 123.0927 | -123.3353 | -123.3536
2956.7656 | 123.1613 | -60.9055 | 62.0636 | -0.149 | -0.007575 | -0.013266 | 0.00028404 | 0.06096 | -0.0033005 | 0.065702 | -61.0199 | 62.2192 | -61.2671 | -61.116 | 61.8393 | 0.050354 | 0.054932 | 0.22888 | 62.1735 | -61.2442 | -0.36163 | 0.15564 | -0.11444 | -0.21057 | -0.22431 | -0.33875 | 0.10986 | 0.24719 | 60.9604 | 61.1343 | 122.7448 | 123.1247 | -0.11444 | 123.0789 | 60.9558 | -0.33875 | 123.1247 | -0.11444 | 60.9558 | 122.7448 | 123.0789 | -123.3307 | -123.3078
2957.7656 | 123.1384 | -60.9558 | 62.0819 | 0.056992 | -0.0039434 | -0.011771 | 0.0032748 | 0.062669 | -0.0043685 | 0.067838 | -61.0382 | 62.2147 | -61.2625 | -61.1755 | 61.7615 | -0.027466 | 0.004578 | 0.10986 | 62.1414 | -61.2717 | -0.3067 | 0.13275 | -0.082397 | -0.21973 | -0.32043 | -0.31586 | 0.059509 | 0.2243 | 60.9604 | 61.0657 | 122.7173 | 123.1705 | -0.082397 | 123.0972 | 60.9283 | -0.31586 | 123.1705 | -0.082397 | 60.9283 | 122.7173 | 123.0972 | -123.3444 | -123.3536
2958.7656 | 123.1247 | -60.9421 | 62.059 | 0.072251 | -0.0050116 | -0.010275 | 0.0060518 | 0.062455 | -0.0060775 | 0.06442 | -61.0336 | 62.2238 | -61.235 | -61.1801 | 61.7615 | -0.022888 | 0.004578 | 0.10529 | 62.178 | -61.2488 | -0.29297 | 0.16479 | -0.091552 | -0.23804 | -0.29755 | -0.3067 | 0.11902 | 0.20142 | 60.9467 | 61.0474 | 122.7036 | 123.1659 | -0.091552 | 123.1201 | 60.9192 | -0.3067 | 123.1659 | -0.091552 | 60.9192 | 122.7036 | 123.1201 | -123.2941 | -123.3078
2959.7656 | 123.1705 | -60.9238 | 62.0728 | -0.16426 | -0.0077888 | -0.0098479 | 0.0045566 | 0.062669 | -0.0022323 | 0.067624 | -61.0291 | 62.2375 | -61.2305 | -61.1343 | 61.821 | 0.054932 | 0.068665 | 0.20599 | 62.2009 | -61.2076 | -0.3067 | 0.16479 | -0.10529 | -0.21057 | -0.25177 | -0.28381 | 0.12817 | 0.20142 | 60.9924 | 61.1298 | 122.7448 | 123.1613 | -0.10529 | 123.1247 | 60.9787 | -0.28381 | 123.1613 | -0.10529 | 60.9787 | 122.7448 | 123.1247 | -123.3032 | -123.2803
2960.7656 | 123.175 | -60.9192 | 62.0773 | -0.080337 | -0.007575 | -0.0092071 | 0.00712 | 0.061814 | -0.0077865 | 0.064634 | -61.0016 | 62.2375 | -61.2442 | -61.116 | 61.8164 | 0.068665 | -0.004578 | 0.20599 | 62.1872 | -61.2488 | -0.32501 | 0.16022 | -0.082398 | -0.19684 | -0.26093 | -0.32959 | 0.10986 | 0.24262 | 60.9146 | 61.1252 | 122.7356 | 123.1567 | -0.082398 | 123.1064 | 60.9879 | -0.32959 | 123.1567 | -0.082398 | 60.9879 | 122.7356 | 123.1064 | -123.3215 | -123.3261
2961.7656 | 123.1522 | -60.9375 | 62.0682 | -0.019302 | -0.0056524 | -0.014761 | 0.0062656 | 0.059891 | -0.0043685 | 0.065488 | -61.0062 | 62.2467 | -61.2442 | -61.116 | 61.821 | 0.036621 | 0 | 0.21057 | 62.1735 | -61.2488 | -0.3067 | 0.17853 | -0.068665 | -0.17853 | -0.24719 | -0.31128 | 0.10529 | 0.23804 | 60.9375 | 61.1481 | 122.7585 | 123.1842 | -0.068665 | 123.111 | 60.9741 | -0.31128 | 123.1842 | -0.068665 | 60.9741 | 122.7585 | 123.111 | -123.3124 | -123.317
2962.7656 | 123.1705 | -60.8963 | 62.0499 | -0.04982 | -0.0054388 | -0.010275 | 0.003702 | 0.062028 | -0.0092819 | 0.066984 | -60.9924 | 62.2238 | -61.2259 | -61.1343 | 61.8301 | 0.050354 | 0 | 0.20599 | 62.1689 | -61.2122 | -0.32959 | 0.17395 | -0.096131 | -0.23804 | -0.21973 | -0.31586 | 0.11902 | 0.23346 | 60.8963 | 61.1023 | 122.7264 | 123.1201 | -0.096131 | 123.0652 | 60.9467 | -0.31586 | 123.1201 | -0.096131 | 60.9467 | 122.7264 | 123.0652 | -123.2758 | -123.262
2963.7656 | 123.1522 | -60.9192 | 62.059 | -0.04219 | -0.005866 | -0.010275 | 0.0051974 | 0.062669 | -0.0047957 | 0.06677 | -60.997 | 62.2192 | -61.2625 | -61.1252 | 61.8073 | 0.059509 | 0.004578 | 0.21515 | 62.1826 | -61.2305 | -0.34332 | 0.16022 | -0.07782 | -0.20599 | -0.25177 | -0.31128 | 0.1236 | 0.2655 | 60.9238 | 61.1343 | 122.7264 | 123.1384 | -0.07782 | 123.1018 | 60.9787 | -0.31128 | 123.1384 | -0.07782 | 60.9787 | 122.7264 | 123.1018 | -123.3215 | -123.2895
2964.7656 | 123.0927 | -60.9375 | 62.0636 | 0.25536 | -0.0039434 | -0.012839 | 0.0056246 | 0.065659 | -0.0054367 | 0.06677 | -61.0794 | 62.2238 | -61.2579 | -61.2167 | 61.7523 | -0.07782 | 0.004578 | 0.064087 | 62.1689 | -61.2717 | -0.32044 | 0.16022 | -0.14191 | -0.27924 | -0.31128 | -0.33417 | 0.10528 | 0.17853 | 60.9421 | 61.0016 | 122.6898 | 123.1613 | -0.14191 | 123.1064 | 60.8597 | -0.33417 | 123.1613 | -0.14191 | 60.8597 | 122.6898 | 123.1064 | -123.3215 | -123.3353
2965.7656 | 123.143 | -60.8917 | 62.0636 | -0.026932 | -0.0039434 | -0.014761 | 0.0017794 | 0.062241 | -0.0060775 | 0.067624 | -60.9879 | 62.2192 | -61.2579 | -61.1206 | 61.821 | 0.059509 | 0.004578 | 0.21973 | 62.2101 | -61.2305 | -0.36621 | 0.15564 | -0.09613 | -0.22888 | -0.24262 | -0.33874 | 0.14648 | 0.27008 | 60.8963 | 61.1115 | 122.7127 | 123.111 | -0.09613 | 123.1018 | 60.9512 | -0.33874 | 123.111 | -0.09613 | 60.9512 | 122.7127 | 123.1018 | -123.3215 | -123.2941
2966.7656 | 123.1522 | -60.91 | 62.0682 | -0.10323 | -0.0073614 | -0.012625 | 0.0022066 | 0.062882 | -0.0067185 | 0.066556 | -60.9833 | 62.2284 | -61.235 | -61.116 | 61.8347 | 0.054932 | 0.004578 | 0.2243 | 62.1918 | -61.2305 | -0.32501 | 0.16022 | -0.073242 | -0.20599 | -0.23346 | -0.32043 | 0.1236 | 0.25177 | 60.9146 | 61.1343 | 122.7448 | 123.1384 | -0.073242 | 123.1018 | 60.965 | -0.32043 | 123.1384 | -0.073242 | 60.965 | 122.7448 | 123.1018 | -123.3032 | -123.2986
2967.7656 | 123.1293 | -60.9283 | 62.0819 | 0.1638 | -0.006507 | -0.010489 | 0.004343 | 0.06096 | -0.0052231 | 0.06677 | -60.9787 | 62.2467 | -61.2396 | -61.1526 | 61.821 | 0.022888 | 0 | 0.17853 | 62.1414 | -61.2717 | -0.31128 | 0.16479 | -0.050354 | -0.2243 | -0.26093 | -0.34332 | 0.059509 | 0.26093 | 60.9283 | 61.1069 | 122.7493 | 123.175 | -0.050354 | 123.0698 | 60.9512 | -0.34332 | 123.175 | -0.050354 | 60.9512 | 122.7493 | 123.0698 | -123.3215 | -123.3536
2968.7656 | 123.1522 | -60.8871 | 62.0544 | -0.011673 | -0.0062934 | -0.011557 | 0.0049838 | 0.063737 | -0.0056503 | 0.066343 | -60.965 | 62.2284 | -61.2396 | -61.1435 | 61.8073 | 0.041199 | 0.004578 | 0.17853 | 62.1506 | -61.2534 | -0.35248 | 0.17395 | -0.07782 | -0.25635 | -0.24719 | -0.36621 | 0.096131 | 0.27466 | 60.8917 | 61.0657 | 122.6944 | 123.1155 | -0.07782 | 123.0377 | 60.9283 | -0.36621 | 123.1155 | -0.07782 | 60.9283 | 122.6944 | 123.0377 | -123.2941 | -123.3078
2969.7656 | 123.1613 | -60.9146 | 62.0544 | -0.11848 | -0.0050116 | -0.0070709 | 0.0056246 | 0.062669 | -0.0067185 | 0.067838 | -61.0062 | 62.2238 | -61.2534 | -61.1664 | 61.7981 | 0.036621 | 0 | 0.17395 | 62.1414 | -61.2717 | -0.33875 | 0.16937 | -0.091553 | -0.25177 | -0.25635 | -0.35706 | 0.086975 | 0.24719 | 60.9146 | 61.0886 | 122.7127 | 123.1384 | -0.091553 | 123.056 | 60.9512 | -0.35706 | 123.1384 | -0.091553 | 60.9512 | 122.7127 | 123.056 | -123.3078 | -123.3261
2970.7656 | 123.1293 | -60.91 | 62.0728 | 0.095139 | -0.0050116 | -0.011557 | 0.0041292 | 0.062241 | -0.0043685 | 0.06677 | -61.0062 | 62.2375 | -61.2579 | -61.1481 | 61.7935 | 0.022888 | 0.004578 | 0.16479 | 62.1552 | -61.2534 | -0.3479 | 0.16479 | -0.096131 | -0.23804 | -0.27924 | -0.34332 | 0.082397 | 0.25177 | 60.9146 | 61.0748 | 122.7036 | 123.1476 | -0.096131 | 123.0652 | 60.9329 | -0.34332 | 123.1476 | -0.096131 | 60.9329 | 122.7036 | 123.0652 | -123.3307 | -123.3261
2971.7812 | 123.23 | -60.8871 | 62.0361 | -0.019302 | -0.0094976 | -0.016257 | -0.0061246 | 0.057969 | -0.0052231 | 0.067838 | -61.0565 | 62.1185 | -61.2396 | -61.116 | 61.8805 | 0.10986 | -0.11902 | 0.25635 | 62.1231 | -61.203 | -0.35248 | 0.082397 | -0.16937 | -0.22888 | -0.15564 | -0.31586 | 0.086975 | 0.1831 | 60.7681 | 61.1435 | 122.7676 | 123.0057 | -0.16937 | 123.0103 | 60.997 | -0.31586 | 123.0057 | -0.16937 | 60.997 | 122.7676 | 123.0103 | -123.2758 | -123.2391
2972.7656 | 123.143 | -60.9283 | 62.0819 | -0.019302 | -0.0028754 | -0.010916 | 0.0049838 | 0.057969 | -0.0058639 | 0.067624 | -60.997 | 62.2055 | -61.235 | -61.1389 | 61.7798 | 0.022888 | -0.018311 | 0.15564 | 62.1597 | -61.2717 | -0.3067 | 0.1236 | -0.068664 | -0.21057 | -0.30212 | -0.34332 | 0.07782 | 0.23804 | 60.91 | 61.084 | 122.7081 | 123.1338 | -0.068664 | 123.0881 | 60.9512 | -0.34332 | 123.1338 | -0.068664 | 60.9512 | 122.7081 | 123.0881 | -123.317 | -123.3536
2973.7656 | 123.1522 | -60.91 | 62.0636 | -0.019302 | -0.0041572 | -0.0079253 | 0.0069064 | 0.059464 | -0.0045821 | 0.066556 | -61.0062 | 62.2284 | -61.235 | -61.1526 | 61.7706 | 0.009155 | -0.004578 | 0.14648 | 62.1414 | -61.2808 | -0.32501 | 0.16479 | -0.096131 | -0.24261 | -0.29297 | -0.37079 | 0.077819 | 0.22888 | 60.9055 | 61.0565 | 122.6807 | 123.1384 | -0.096131 | 123.0515 | 60.9192 | -0.37079 | 123.1384 | -0.096131 | 60.9192 | 122.6807 | 123.0515 | -123.2986 | -123.3444
2974.7656 | 123.1201 | -60.9467 | 62.0453 | 0.14854 | -0.0035162 | -0.0089935 | 0.0058382 | 0.062241 | -0.0052231 | 0.068265 | -61.0657 | 62.2375 | -61.2442 | -61.2076 | 61.734 | -0.082397 | 0.022888 | 0.07782 | 62.178 | -61.2534 | -0.29755 | 0.19226 | -0.11902 | -0.26093 | -0.31128 | -0.3067 | 0.13275 | 0.17853 | 60.9695 | 61.0245 | 122.6807 | 123.1842 | -0.11902 | 123.1247 | 60.8643 | -0.3067 | 123.1842 | -0.11902 | 60.8643 | 122.6807 | 123.1247 | -123.2895 | -123.2986
2975.7656 | 123.0881 | -60.965 | 62.0636 | 0.1104 | -0.0056524 | -0.013266 | 0.0058382 | 0.062669 | -0.0054367 | 0.067624 | -61.0611 | 62.2375 | -61.2488 | -61.2076 | 61.7523 | -0.068665 | 0.004578 | 0.064087 | 62.1323 | -61.2946 | -0.28381 | 0.17395 | -0.09613 | -0.24262 | -0.31128 | -0.32959 | 0.068664 | 0.18768 | 60.9695 | 61.0291 | 122.7173 | 123.2025 | -0.09613 | 123.0972 | 60.8963 | -0.32959 | 123.2025 | -0.09613 | 60.8963 | 122.7173 | 123.0972 | -123.3124 | -123.3582
2976.7812 | 123.1934 | -60.8917 | 62.0316 | 0.13329 | -0.0088568 | -0.01113 | -0.0027066 | 0.060746 | -0.0047957 | 0.068693 | -61.0886 | 62.1094 | -61.2488 | -61.1847 | 61.8073 | 0.013733 | -0.10071 | 0.16937 | 62.1185 | -61.2076 | -0.35705 | 0.07782 | -0.19684 | -0.29297 | -0.2243 | -0.31586 | 0.086975 | 0.16022 | 60.791 | 61.0611 | 122.699 | 123.0011 | -0.19684 | 123.0103 | 60.9055 | -0.31586 | 123.0011 | -0.19684 | 60.9055 | 122.699 | 123.0103 | -123.2803 | -123.2391
2977.7656 | 123.0972 | -60.9467 | 62.0544 | 0.07988 | -0.0039434 | -0.010703 | 0.0079744 | 0.060532 | -0.0054367 | 0.065916 | -61.0748 | 62.2284 | -61.2717 | -61.1984 | 61.7157 | -0.082397 | -0.013733 | 0.050354 | 62.1414 | -61.29 | -0.32501 | 0.17395 | -0.12817 | -0.25177 | -0.33874 | -0.34332 | 0.086975 | 0.19684 | 60.9329 | 60.997 | 122.6624 | 123.175 | -0.12817 | 123.0881 | 60.8643 | -0.34332 | 123.175 | -0.12817 | 60.8643 | 122.6624 | 123.0881 | -123.3261 | -123.3444
2978.7656 | 123.2254 | -60.91 | 62.0041 | 0.2401 | -0.0090704 | -0.0096343 | 0.002634 | 0.061387 | -0.0026595 | 0.066343 | -61.0016 | 62.146 | -61.2442 | -61.116 | 61.8164 | 0.027466 | -0.19226 | 0.15564 | 62.114 | -61.2534 | -0.33417 | 0.14191 | -0.091553 | -0.20599 | -0.18768 | -0.34332 | 0.10986 | 0.24262 | 60.7178 | 61.0657 | 122.7264 | 123.056 | -0.091553 | 123.024 | 60.9375 | -0.34332 | 123.056 | -0.091553 | 60.9375 | 122.7264 | 123.024 | -123.2483 | -123.2574
2979.7656 | 123.1155 | -60.9283 | 62.0636 | 0.041733 | -0.0033026 | -0.010275 | 0.0064792 | 0.062455 | -0.0060775 | 0.065702 | -61.0794 | 62.2147 | -61.2762 | -61.2076 | 61.7203 | -0.068665 | 0.004578 | 0.059509 | 62.1643 | -61.2991 | -0.3479 | 0.15106 | -0.15106 | -0.27924 | -0.34332 | -0.37079 | 0.10071 | 0.19684 | 60.9329 | 60.9879 | 122.6486 | 123.143 | -0.15106 | 123.0927 | 60.8597 | -0.37079 | 123.143 | -0.15106 | 60.8597 | 122.6486 | 123.0927 | -123.3398 | -123.3627
2980.7656 | 123.0972 | -60.9375 | 62.059 | 0.23247 | -0.0043708 | -0.011343 | 0.0064792 | 0.060319 | -0.0062911 | 0.065275 | -61.0794 | 62.2101 | -61.2808 | -61.2076 | 61.7249 | -0.091553 | -0.004578 | 0.050354 | 62.1597 | -61.2854 | -0.34332 | 0.15106 | -0.14191 | -0.27008 | -0.33417 | -0.3479 | 0.10071 | 0.20142 | 60.9329 | 60.9879 | 122.6624 | 123.1476 | -0.14191 | 123.0972 | 60.8459 | -0.3479 | 123.1476 | -0.14191 | 60.8459 | 122.6624 | 123.0972 | -123.3398 | -123.3444
2981.7812 | 123.2208 | -60.8826 | 62.059 | 0.049362 | -0.0088568 | -0.013693 | -0.0074064 | 0.058823 | -0.0033005 | 0.067197 | -61.0794 | 62.114 | -61.2579 | -61.1298 | 61.8576 | 0.059509 | -0.10071 | 0.24261 | 62.1231 | -61.2076 | -0.37537 | 0.054932 | -0.19684 | -0.24719 | -0.20142 | -0.32501 | 0.064087 | 0.17853 | 60.7819 | 61.1252 | 122.7402 | 122.9965 | -0.19684 | 123.0057 | 60.9421 | -0.32501 | 122.9965 | -0.19684 | 60.9421 | 122.7402 | 123.0057 | -123.317 | -123.2666
2982.7656 | 123.1293 | -60.9283 | 62.0773 | -0.37788 | -0.0054388 | -0.012412 | 0.0049838 | 0.060105 | -0.0050095 | 0.064634 | -61.084 | 62.2147 | -61.2534 | -61.2122 | 61.7523 | -0.068665 | -0.054932 | 0.082397 | 62.1231 | -61.3037 | -0.32501 | 0.13733 | -0.15564 | -0.28381 | -0.32501 | -0.37537 | 0.045776 | 0.16937 | 60.8734 | 61.0107 | 122.6807 | 123.143 | -0.15564 | 123.0515 | 60.8597 | -0.37537 | 123.143 | -0.15564 | 60.8597 | 122.6807 | 123.0515 | -123.3307 | -123.381
2983.7656 | 123.1476 | -60.9375 | 62.0682 | -0.20241 | -0.0028754 | -0.010916 | 0.003702 | 0.059464 | -0.0058639 | 0.067197 | -61.0657 | 62.2238 | -61.2488 | -61.203 | 61.7386 | -0.073242 | -0.059509 | 0.073242 | 62.1414 | -61.3083 | -0.31128 | 0.15564 | -0.12817 | -0.2655 | -0.32959 | -0.37079 | 0.073242 | 0.1831 | 60.878 | 61.0107 | 122.6761 | 123.1613 | -0.12817 | 123.0789 | 60.8643 | -0.37079 | 123.1613 | -0.12817 | 60.8643 | 122.6761 | 123.0789 | -123.317 | -123.3765
2984.7656 | 123.1293 | -60.9421 | 62.0636 | 0.51476 | -0.0062934 | -0.014761 | 0.0045566 | 0.06096 | -0.0035141 | 0.065702 | -61.0291 | 62.2421 | -61.2579 | -61.1938 | 61.7523 | -0.068665 | -0.045776 | 0.068665 | 62.1552 | -61.2762 | -0.31586 | 0.17853 | -0.086975 | -0.25177 | -0.31128 | -0.33417 | 0.091552 | 0.22888 | 60.8963 | 61.0107 | 122.6944 | 123.1842 | -0.086975 | 123.0972 | 60.8734 | -0.33417 | 123.1842 | -0.086975 | 60.8734 | 122.6944 | 123.0972 | -123.3215 | -123.3398
2985.7656 | 123.2483 | -60.9009 | 62.0087 | 0.049362 | -0.0067206 | -0.0098479 | 0.0028476 | 0.0616 | -0.0062911 | 0.06677 | -60.9787 | 62.1414 | -61.2167 | -61.1343 | 61.8347 | 0.018311 | -0.21515 | 0.17853 | 62.0956 | -61.2305 | -0.31586 | 0.13275 | -0.07782 | -0.23346 | -0.17395 | -0.32959 | 0.086975 | 0.23804 | 60.6857 | 61.0794 | 122.7356 | 123.0423 | -0.07782 | 122.9965 | 60.9192 | -0.32959 | 123.0423 | -0.07782 | 60.9192 | 122.7356 | 122.9965 | -123.2254 | -123.2391
2986.7812 | 123.2529 | -60.8551 | 62.0636 | -0.14137 | -0.0088568 | -0.013052 | 0.00092504 | 0.057969 | -0.0035141 | 0.06677 | -61.1847 | 62.1689 | -61.2213 | -61.0794 | 61.8942 | 0.10071 | -0.09613 | 0.29297 | 62.1048 | -61.1938 | -0.36621 | 0.10528 | -0.32959 | -0.2243 | -0.16937 | -0.33875 | 0.041198 | 0.036621 | 60.759 | 61.1481 | 122.7493 | 123.024 | -0.32959 | 122.9599 | 60.9558 | -0.33875 | 123.024 | -0.32959 | 60.9558 | 122.7493 | 122.9599 | -123.2849 | -123.2574
2987.7656 | 123.1247 | -60.9192 | 62.0453 | 0.23247 | -0.0026618 | -0.014548 | 0.0066928 | 0.059678 | -0.0043685 | 0.068265 | -61.0519 | 62.2055 | -61.2579 | -61.1984 | 61.7432 | -0.07782 | -0.054932 | 0.068665 | 62.1231 | -61.2671 | -0.33875 | 0.16022 | -0.13275 | -0.27924 | -0.30212 | -0.3479 | 0.07782 | 0.20599 | 60.8643 | 60.9879 | 122.6624 | 123.1247 | -0.13275 | 123.0423 | 60.8414 | -0.3479 | 123.1247 | -0.13275 | 60.8414 | 122.6624 | 123.0423 | -123.3032 | -123.3124
2988.7656 | 123.1567 | -60.9146 | 62.027 | 0.26299 | -0.0054388 | -0.013052 | 0.0051974 | 0.061387 | -0.0035141 | 0.066129 | -61.0565 | 62.1826 | -61.2671 | -61.1618 | 61.7844 | -0.032043 | -0.15564 | 0.10071 | 62.114 | -61.2534 | -0.35248 | 0.15564 | -0.14191 | -0.24719 | -0.24262 | -0.33875 | 0.086975 | 0.21057 | 60.759 | 61.0153 | 122.699 | 123.0972 | -0.14191 | 123.0286 | 60.8826 | -0.33875 | 123.0972 | -0.14191 | 60.8826 | 122.699 | 123.0286 | -123.2941 | -123.2803
2989.7656 | 123.1796 | -60.9192 | 62.0316 | 0.26299 | -0.0056524 | -0.0087799 | 0.0047702 | 0.063737 | -0.0054367 | 0.064847 | -61.0611 | 62.1964 | -61.2534 | -61.1572 | 61.7752 | -0.045776 | -0.14191 | 0.10986 | 62.146 | -61.2534 | -0.33417 | 0.1648 | -0.14191 | -0.23804 | -0.25635 | -0.33417 | 0.11444 | 0.19226 | 60.7773 | 61.0291 | 122.6944 | 123.1155 | -0.14191 | 123.0652 | 60.8734 | -0.33417 | 123.1155 | -0.14191 | 60.8734 | 122.6944 | 123.0652 | -123.2849 | -123.2849
2990.7656 | 123.1842 | -60.9146 | 62.0544 | 0.26299 | -0.004798 | -0.01113 | 0.0049838 | 0.061814 | -0.0050095 | 0.067197 | -61.0474 | 62.1643 | -61.2717 | -61.1618 | 61.7889 | -0.045776 | -0.14648 | 0.091553 | 62.1368 | -61.235 | -0.35706 | 0.10986 | -0.13275 | -0.24719 | -0.2655 | -0.32043 | 0.082398 | 0.2243 | 60.7681 | 61.0062 | 122.7036 | 123.0789 | -0.13275 | 123.0515 | 60.8688 | -0.32043 | 123.0789 | -0.13275 | 60.8688 | 122.7036 | 123.0515 | -123.3261 | -123.2895
2991.7656 | 123.1796 | -60.91 | 62.0224 | 0.2401 | -0.0073614 | -0.014548 | 0.0011386 | 0.060746 | -0.0045821 | 0.064207 | -61.0199 | 62.1414 | -61.235 | -61.1252 | 61.8347 | 0.009155 | -0.19226 | 0.17395 | 62.0956 | -61.2259 | -0.32501 | 0.11902 | -0.10986 | -0.21515 | -0.18768 | -0.31586 | 0.073242 | 0.21515 | 60.7178 | 61.084 | 122.7448 | 123.0515 | -0.10986 | 123.0057 | 60.9192 | -0.31586 | 123.0515 | -0.10986 | 60.9192 | 122.7448 | 123.0057 | -123.2574 | -123.2483
2992.7656 | 123.1979 | -60.8917 | 62.027 | 0.20195 | -0.0097114 | -0.0092071 | 0.0013522 | 0.061387 | -0.0045821 | 0.066984 | -61.0382 | 62.1368 | -61.2488 | -61.1114 | 61.8347 | 0.032043 | -0.20599 | 0.17395 | 62.059 | -61.2396 | -0.35705 | 0.10986 | -0.14648 | -0.21973 | -0.19226 | -0.3479 | 0.032043 | 0.21057 | 60.6857 | 61.0657 | 122.7264 | 123.0286 | -0.14648 | 122.9507 | 60.9238 | -0.3479 | 123.0286 | -0.14648 | 60.9238 | 122.7264 | 122.9507 | -123.2758 | -123.2666
2993.7656 | 123.1522 | -60.9283 | 62.0453 | 0.22484 | -0.0056524 | -0.012412 | 0.0090426 | 0.0616 | -0.0062911 | 0.066129 | -61.0703 | 62.1964 | -61.2671 | -61.1755 | 61.7523 | -0.059509 | -0.10986 | 0.086975 | 62.1002 | -61.2808 | -0.33875 | 0.15106 | -0.14191 | -0.24719 | -0.29297 | -0.35248 | 0.054932 | 0.19684 | 60.8185 | 61.0153 | 122.6807 | 123.1247 | -0.14191 | 123.0286 | 60.8688 | -0.35248 | 123.1247 | -0.14191 | 60.8688 | 122.6807 | 123.0286 | -123.3124 | -123.3261
2994.7656 | 123.1476 | -60.9375 | 62.0407 | 0.20195 | -0.0052252 | -0.010062 | 0.0062656 | 0.061814 | -0.0052231 | 0.068693 | -61.0703 | 62.1872 | -61.2717 | -61.1664 | 61.7477 | -0.073242 | -0.09613 | 0.073242 | 62.1323 | -61.2442 | -0.33417 | 0.14649 | -0.13275 | -0.22888 | -0.29297 | -0.3067 | 0.091553 | 0.20142 | 60.8414 | 61.0107 | 122.6852 | 123.1247 | -0.13275 | 123.0698 | 60.8643 | -0.3067 | 123.1247 | -0.13275 | 60.8643 | 122.6852 | 123.0698 | -123.3124 | -123.2849
2995.7656 | 123.23 | -60.9055 | 62.0178 | 0.25536 | -0.0052252 | -0.012412 | 0.0032748 | 0.059891 | -0.0047957 | 0.06677 | -61.0428 | 62.1689 | -61.2579 | -61.1298 | 61.8301 | -0.013733 | -0.20142 | 0.15564 | 62.1002 | -61.2488 | -0.35248 | 0.15106 | -0.13733 | -0.2243 | -0.18768 | -0.34332 | 0.082398 | 0.21515 | 60.704 | 61.0611 | 122.7356 | 123.0743 | -0.13733 | 123.0057 | 60.8917 | -0.34332 | 123.0743 | -0.13733 | 60.8917 | 122.7356 | 123.0057 | -123.2758 | -123.2666
2996.7656 | 123.2208 | -60.9009 | 62.0087 | 0.30876 | -0.0056524 | -0.011984 | 0.0032748 | 0.06096 | -0.0041549 | 0.063993 | -61.0336 | 62.1552 | -61.2396 | -61.1252 | 61.8256 | -0.013733 | -0.15106 | 0.16022 | 62.1048 | -61.2625 | -0.33874 | 0.14648 | -0.13275 | -0.2243 | -0.18311 | -0.36163 | 0.09613 | 0.20599 | 60.7498 | 61.0611 | 122.7264 | 123.056 | -0.13275 | 123.0057 | 60.8871 | -0.36163 | 123.056 | -0.13275 | 60.8871 | 122.7264 | 123.0057 | -123.2483 | -123.2712
2997.7656 | 123.2346 | -60.9192 | 62.0178 | 0.26299 | -0.0062934 | -0.010275 | 0.0028476 | 0.062028 | -0.0045821 | 0.066556 | -61.0336 | 62.1643 | -61.2717 | -61.1435 | 61.8164 | -0.004578 | -0.1831 | 0.15106 | 62.0911 | -61.2808 | -0.35248 | 0.14648 | -0.11444 | -0.2243 | -0.20142 | -0.36163 | 0.073242 | 0.23804 | 60.7361 | 61.0703 | 122.7356 | 123.0835 | -0.11444 | 123.0103 | 60.9146 | -0.36163 | 123.0835 | -0.11444 | 60.9146 | 122.7356 | 123.0103 | -123.2895 | -123.2986
2998.7656 | 123.2025 | -60.9146 | 62.027 | 0.18669 | -0.0067206 | -0.012839 | -0.00078396 | 0.060532 | -0.0050095 | 0.067838 | -61.0428 | 62.1414 | -61.2442 | -61.1481 | 61.8118 | 0 | -0.16022 | 0.16479 | 62.0956 | -61.235 | -0.32959 | 0.11444 | -0.12817 | -0.23346 | -0.21515 | -0.32043 | 0.068664 | 0.20142 | 60.7544 | 61.0794 | 122.7264 | 123.056 | -0.12817 | 123.0103 | 60.9146 | -0.32043 | 123.056 | -0.12817 | 60.9146 | 122.7264 | 123.0103 | -123.2712 | -123.262
2999.7656 | 123.1934 | -60.9009 | 62.0407 | 0.20958 | -0.0060798 | -0.013907 | 0.0013522 | 0.05861 | -0.0052231 | 0.065702 | -61.0382 | 62.1231 | -61.2259 | -61.1298 | 61.8118 | -0.009155 | -0.1831 | 0.17395 | 62.0728 | -61.2213 | -0.32501 | 0.082398 | -0.13733 | -0.22888 | -0.22888 | -0.32043 | 0.032044 | 0.18768 | 60.7178 | 61.0748 | 122.7127 | 123.024 | -0.13733 | 122.9736 | 60.8917 | -0.32043 | 123.024 | -0.13733 | 60.8917 | 122.7127 | 122.9736 | -123.2666 | -123.262
3000.7656 | 123.1934 | -60.9146 | 62.0453 | 0.24773 | -0.0050116 | -0.0083527 | 0.005411 | 0.05861 | -0.0043685 | 0.067624 | -61.0474 | 62.1689 | -61.2579 | -61.171 | 61.7935 | -0.045776 | -0.14648 | 0.09613 | 62.1048 | -61.2534 | -0.34332 | 0.1236 | -0.13275 | -0.25635 | -0.25177 | -0.33875 | 0.059509 | 0.21057 | 60.7681 | 61.0107 | 122.7081 | 123.0835 | -0.13275 | 123.0194 | 60.8688 | -0.33875 | 123.0835 | -0.13275 | 60.8688 | 122.7081 | 123.0194 | -123.3032 | -123.2986
3001.7656 | 123.1842 | -60.9192 | 62.0407 | 0.23247 | -0.0052252 | -0.0083527 | 0.0051974 | 0.06096 | -0.0065047 | 0.068265 | -61.0657 | 62.1597 | -61.2534 | -61.1755 | 61.7752 | -0.050354 | -0.13275 | 0.09613 | 62.1414 | -61.2671 | -0.33417 | 0.11902 | -0.14648 | -0.25635 | -0.2655 | -0.3479 | 0.10071 | 0.18768 | 60.7864 | 61.0153 | 122.6944 | 123.0789 | -0.14648 | 123.0606 | 60.8688 | -0.3479 | 123.0789 | -0.14648 | 60.8688 | 122.6944 | 123.0606 | -123.2941 | -123.3078
3002.7656 | 123.2574 | -60.8917 | 62.0132 | 0.2401 | -0.0050116 | -0.012839 | 0.003702 | 0.060532 | -0.0050095 | 0.067197 | -61.0245 | 62.1643 | -61.2579 | -61.116 | 61.8301 | 0.027466 | -0.21057 | 0.16022 | 62.0728 | -61.2396 | -0.36621 | 0.15106 | -0.13275 | -0.2243 | -0.18311 | -0.3479 | 0.059509 | 0.23346 | 60.6812 | 61.0519 | 122.7219 | 123.056 | -0.13275 | 122.9645 | 60.9192 | -0.3479 | 123.056 | -0.13275 | 60.9192 | 122.7219 | 122.9645 | -123.2712 | -123.2529
3003.7656 | 123.23 | -60.9192 | 62.0316 | 0.27061 | -0.0077888 | -0.010275 | 0.003702 | 0.06096 | -0.0043685 | 0.067411 | -61.0245 | 62.1506 | -61.2488 | -61.116 | 61.8073 | 0.009155 | -0.20142 | 0.16479 | 62.1094 | -61.235 | -0.32959 | 0.11902 | -0.10529 | -0.19684 | -0.2243 | -0.31586 | 0.07782 | 0.2243 | 60.7178 | 61.084 | 122.7264 | 123.0698 | -0.10529 | 123.0286 | 60.9283 | -0.31586 | 123.0698 | -0.10529 | 60.9283 | 122.7264 | 123.0286 | -123.2803 | -123.2666
3004.7656 | 123.23 | -60.91 | 62.0224 | 0.25536 | -0.0043708 | -0.011557 | 0.003702 | 0.06096 | -0.0077865 | 0.066343 | -61.0428 | 62.1643 | -61.2488 | -61.1343 | 61.7935 | -0.022888 | -0.17853 | 0.1236 | 62.1231 | -61.2534 | -0.33874 | 0.14191 | -0.13275 | -0.2243 | -0.22888 | -0.34332 | 0.10071 | 0.20599 | 60.7315 | 61.0336 | 122.7036 | 123.0743 | -0.13275 | 123.0331 | 60.8871 | -0.34332 | 123.0743 | -0.13275 | 60.8871 | 122.7036 | 123.0331 | -123.2712 | -123.2758
3005.7656 | 123.2162 | -60.8963 | 62.0453 | 0.20195 | -0.0071478 | -0.010275 | -0.00057036 | 0.060746 | -0.0056503 | 0.063138 | -61.0245 | 62.1094 | -61.235 | -61.1114 | 61.821 | 0.018311 | -0.18768 | 0.17853 | 62.0956 | -61.2122 | -0.33874 | 0.064087 | -0.12817 | -0.21515 | -0.2243 | -0.31586 | 0.050354 | 0.21057 | 60.7086 | 61.0748 | 122.7173 | 123.0057 | -0.12817 | 122.9919 | 60.9146 | -0.31586 | 123.0057 | -0.12817 | 60.9146 | 122.7173 | 122.9919 | -123.2803 | -123.2574
3006.7656 | 123.2117 | -60.8826 | 62.0224 | 0.17906 | -0.006507 | -0.0072845 | 0.00071144 | 0.060105 | -0.0052231 | 0.065702 | -61.0199 | 62.146 | -61.235 | -61.116 | 61.8347 | 0.027466 | -0.20599 | 0.17853 | 62.0819 | -61.2305 | -0.35248 | 0.1236 | -0.13733 | -0.23346 | -0.18768 | -0.3479 | 0.059509 | 0.21515 | 60.6766 | 61.0611 | 122.7173 | 123.0286 | -0.13733 | 122.9645 | 60.91 | -0.3479 | 123.0286 | -0.13733 | 60.91 | 122.7173 | 122.9645 | -123.2574 | -123.2529
3007.7656 | 123.1796 | -60.9375 | 62.0361 | 0.2401 | -0.0067206 | -0.010916 | 0.0051974 | 0.059678 | -0.0058639 | 0.067624 | -61.0565 | 62.1826 | -61.2625 | -61.171 | 61.7477 | -0.064087 | -0.091553 | 0.082397 | 62.1048 | -61.2534 | -0.32501 | 0.14648 | -0.11902 | -0.23346 | -0.28839 | -0.31586 | 0.068664 | 0.20599 | 60.8459 | 61.0199 | 122.6852 | 123.1201 | -0.11902 | 123.0423 | 60.8734 | -0.31586 | 123.1201 | -0.11902 | 60.8734 | 122.6852 | 123.0423 | -123.2986 | -123.2895
3008.7656 | 123.1567 | -60.9238 | 62.0407 | 0.22484 | -0.004798 | -0.010703 | 0.003702 | 0.060532 | -0.0037277 | 0.066129 | -61.0703 | 62.2055 | -61.2534 | -61.1801 | 61.7661 | -0.064087 | -0.059509 | 0.07782 | 62.1368 | -61.2808 | -0.32959 | 0.1648 | -0.14648 | -0.25635 | -0.27466 | -0.35706 | 0.096131 | 0.18311 | 60.8643 | 61.0016 | 122.6898 | 123.1293 | -0.14648 | 123.0606 | 60.8597 | -0.35706 | 123.1293 | -0.14648 | 60.8597 | 122.6898 | 123.0606 | -123.2941 | -123.3215
3009.7656 | 123.1934 | -60.9238 | 62.0224 | 0.26299 | -0.0060798 | -0.013266 | 0.0032748 | 0.060746 | -0.0050095 | 0.067411 | -61.0519 | 62.1964 | -61.2717 | -61.1343 | 61.8073 | -0.022888 | -0.16479 | 0.11444 | 62.1185 | -61.2396 | -0.3479 | 0.17395 | -0.12817 | -0.21057 | -0.21515 | -0.31586 | 0.09613 | 0.21973 | 60.759 | 61.0382 | 122.731 | 123.1201 | -0.12817 | 123.0423 | 60.9009 | -0.31586 | 123.1201 | -0.12817 | 60.9009 | 122.731 | 123.0423 | -123.2941 | -123.262
3010.7656 | 123.1842 | -60.9146 | 62.0407 | 0.27061 | -0.0071478 | -0.0049347 | 0.0041292 | 0.060105 | -0.0054367 | 0.065702 | -61.0565 | 62.1826 | -61.2762 | -61.1389 | 61.7798 | -0.045776 | -0.13275 | 0.10529 | 62.1094 | -61.2442 | -0.36163 | 0.14191 | -0.14191 | -0.2243 | -0.26093 | -0.32959 | 0.068665 | 0.21973 | 60.7819 | 61.0199 | 122.6944 | 123.0972 | -0.14191 | 123.024 | 60.8688 | -0.32959 | 123.0972 | -0.14191 | 60.8688 | 122.6944 | 123.024 | -123.317 | -123.2849
3011.7656 | 123.143 | -60.9283 | 62.0407 | 0.23247 | -0.0054388 | -0.011557 | 0.0049838 | 0.0616 | -0.0047957 | 0.066984 | -61.0703 | 62.2055 | -61.2762 | -61.1801 | 61.7706 | -0.054932 | -0.11902 | 0.086975 | 62.114 | -61.2488 | -0.3479 | 0.1648 | -0.14191 | -0.25177 | -0.27008 | -0.32043 | 0.073243 | 0.20599 | 60.8093 | 61.0153 | 122.699 | 123.1338 | -0.14191 | 123.0423 | 60.8734 | -0.32043 | 123.1338 | -0.14191 | 60.8734 | 122.699 | 123.0423 | -123.317 | -123.2895
3012.7656 | 123.2346 | -60.8734 | 62.0178 | 0.25536 | -0.009284 | -0.010916 | -0.00057036 | 0.061814 | -0.0043685 | 0.066343 | -61.0062 | 62.1368 | -61.2305 | -61.116 | 61.8439 | 0.032043 | -0.20599 | 0.1831 | 62.0911 | -61.2167 | -0.35706 | 0.11902 | -0.13275 | -0.24262 | -0.17395 | -0.34332 | 0.073242 | 0.2243 | 60.6674 | 61.0565 | 122.7173 | 123.0103 | -0.13275 | 122.9645 | 60.9055 | -0.34332 | 123.0103 | -0.13275 | 60.9055 | 122.7173 | 122.9645 | -123.2483 | -123.2346
3013.7656 | 123.2437 | -60.8826 | 62.0453 | -0.019302 | -0.0052252 | -0.01113 | 0.0030612 | 0.06096 | -0.0054367 | 0.063566 | -60.997 | 62.1368 | -61.2259 | -61.0886 | 61.853 | 0.036621 | -0.21515 | 0.1831 | 62.114 | -61.2167 | -0.34332 | 0.091553 | -0.11444 | -0.20599 | -0.19226 | -0.33417 | 0.068665 | 0.22888 | 60.6674 | 61.0657 | 122.7356 | 123.0194 | -0.11444 | 122.9965 | 60.9192 | -0.33417 | 123.0194 | -0.11444 | 60.9192 | 122.7356 | 122.9965 | -123.2712 | -123.262
3014.7656 | 123.1384 | -60.9421 | 62.0636 | 0.25536 | -0.0073614 | -0.012625 | 0.0066928 | 0.06096 | -0.0043685 | 0.065061 | -61.0245 | 62.2192 | -61.2625 | -61.1984 | 61.7477 | -0.068665 | -0.036621 | 0.064087 | 62.1277 | -61.2762 | -0.32043 | 0.15564 | -0.082397 | -0.25635 | -0.31586 | -0.33417 | 0.064087 | 0.23804 | 60.9055 | 61.0062 | 122.6898 | 123.1613 | -0.082397 | 123.0698 | 60.8734 | -0.33417 | 123.1613 | -0.082397 | 60.8734 | 122.6898 | 123.0698 | -123.3261 | -123.3398
3015.7656 | 123.143 | -60.9283 | 62.0773 | 0.20195 | -0.0043708 | -0.011984 | 0.0028476 | 0.059251 | -0.0058639 | 0.067411 | -61.0748 | 62.1964 | -61.2762 | -61.1481 | 61.7569 | -0.091553 | 0.009155 | 0.073242 | 62.1506 | -61.2396 | -0.3479 | 0.11902 | -0.14648 | -0.21973 | -0.32043 | -0.31128 | 0.073242 | 0.20142 | 60.9375 | 61.0016 | 122.6852 | 123.1247 | -0.14648 | 123.0789 | 60.8368 | -0.31128 | 123.1247 | -0.14648 | 60.8368 | 122.6852 | 123.0789 | -123.3536 | -123.317
3016.7656 | 123.1384 | -60.9192 | 62.0544 | 0.17143 | -0.0056524 | -0.0072845 | 0.0047702 | 0.065446 | -0.0041549 | 0.064634 | -61.0657 | 62.1826 | -61.2579 | -61.1755 | 61.7615 | -0.059509 | -0.082397 | 0.064087 | 62.1231 | -61.2534 | -0.33875 | 0.12817 | -0.14648 | -0.25635 | -0.29297 | -0.33417 | 0.068665 | 0.19226 | 60.8368 | 60.9833 | 122.6807 | 123.1018 | -0.14648 | 123.0423 | 60.8597 | -0.33417 | 123.1018 | -0.14648 | 60.8597 | 122.6807 | 123.0423 | -123.3124 | -123.3078
3017.7656 | 123.143 | -60.91 | 62.0499 | 0.19432 | -0.0045844 | -0.010489 | 0.0039156 | 0.060746 | -0.0060775 | 0.067624 | -61.0748 | 62.178 | -61.2579 | -61.1984 | 61.7477 | -0.064087 | -0.054932 | 0.064087 | 62.1368 | -61.2717 | -0.3479 | 0.12817 | -0.16479 | -0.28839 | -0.30212 | -0.36163 | 0.086975 | 0.18311 | 60.8551 | 60.9741 | 122.6578 | 123.0881 | -0.16479 | 123.0469 | 60.8459 | -0.36163 | 123.0881 | -0.16479 | 60.8459 | 122.6578 | 123.0469 | -123.3078 | -123.3215
3018.7656 | 123.2391 | -60.8826 | 62.0041 | 0.38506 | -0.009284 | -0.012839 | 7.0444e-05 | 0.060532 | -0.0043685 | 0.065061 | -60.9055 | 62.1231 | -61.2259 | -61.1023 | 61.8393 | 0.036621 | -0.23346 | 0.17853 | 62.0819 | -61.2122 | -0.34332 | 0.11902 | -0.022889 | -0.21973 | -0.16479 | -0.32959 | 0.07782 | 0.32043 | 60.6491 | 61.0611 | 122.7219 | 123.0057 | -0.022889 | 122.9645 | 60.9192 | -0.32959 | 123.0057 | -0.022889 | 60.9192 | 122.7219 | 122.9645 | -123.23 | -123.2162
3019.7656 | 123.23 | -60.8963 | 61.9995 | 0.26299 | -0.0054388 | -0.010275 | 0.0028476 | 0.062669 | -0.0062911 | 0.065702 | -60.9924 | 62.1414 | -61.2488 | -61.0336 | 61.8805 | 0.045776 | -0.1831 | 0.21515 | 62.0773 | -61.2167 | -0.35248 | 0.14191 | -0.096131 | -0.13733 | -0.11902 | -0.32043 | 0.07782 | 0.25635 | 60.7132 | 61.1114 | 122.7768 | 123.0377 | -0.096131 | 122.9736 | 60.9421 | -0.32043 | 123.0377 | -0.096131 | 60.9421 | 122.7768 | 122.9736 | -123.2483 | -123.2162
3020.7656 | 123.2895 | -60.9238 | 62.0041 | 0.24773 | -0.0069342 | -0.01113 | 0.0039156 | 0.058823 | -0.0065047 | 0.068052 | -60.9787 | 62.1414 | -61.2076 | -61.1114 | 61.8484 | 0.036621 | -0.31128 | -0.036621 | 62.0316 | -61.2442 | -0.28381 | 0.13733 | -0.054932 | -0.18768 | -0.15564 | -0.32044 | 0.027466 | 0.22888 | 60.6125 | 60.8871 | 122.7722 | 123.0652 | -0.054932 | 122.9553 | 60.9604 | -0.32044 | 123.0652 | -0.054932 | 60.9604 | 122.7722 | 122.9553 | -123.2117 | -123.2483
3021.7656 | 122.9645 | -60.9787 | 62.0041 | 0.19432 | -0.0062934 | -0.0098479 | 0.0075472 | 0.061387 | -0.0047957 | 0.065061 | -61.0794 | 62.2055 | -61.2671 | -61.1938 | 61.7432 | -0.086975 | -0.032043 | 0.064087 | 62.1552 | -61.2808 | -0.28839 | 0.20142 | -0.10071 | -0.21515 | -0.26093 | -0.30212 | 0.15106 | 0.18768 | 60.9467 | 61.0428 | 122.7219 | 123.1842 | -0.10071 | 123.1338 | 60.8917 | -0.30212 | 123.1842 | -0.10071 | 60.8917 | 122.7219 | 123.1338 | -123.2712 | -123.2849
3022.7656 | 123.1064 | -60.9146 | 62.059 | 0.049362 | -0.0035162 | -0.01348 | 0.0032748 | 0.061814 | -0.0069321 | 0.066556 | -61.0931 | 62.233 | -61.2854 | -61.1755 | 61.734 | -0.064087 | -0.050354 | 0.054932 | 62.1368 | -61.2762 | -0.37079 | 0.17395 | -0.17853 | -0.26093 | -0.32501 | -0.36163 | 0.07782 | 0.19226 | 60.8643 | 60.9695 | 122.6486 | 123.1476 | -0.17853 | 123.0515 | 60.8505 | -0.36163 | 123.1476 | -0.17853 | 60.8505 | 122.6486 | 123.0515 | -123.3444 | -123.3353
3023.7656 | 123.0927 | -60.9375 | 62.059 | -0.0040434 | -0.0056524 | -0.01113 | 0.0047702 | 0.062241 | -0.0052231 | 0.065488 | -61.0291 | 62.2284 | -61.2579 | -61.1984 | 61.7569 | -0.059509 | -0.036621 | 0.068665 | 62.1414 | -61.2762 | -0.32044 | 0.16937 | -0.091553 | -0.26093 | -0.30212 | -0.33875 | 0.082397 | 0.22888 | 60.9009 | 61.0062 | 122.6944 | 123.1659 | -0.091553 | 123.0789 | 60.878 | -0.33875 | 123.1659 | -0.091553 | 60.878 | 122.6944 | 123.0789 | -123.317 | -123.3353
3024.7656 | 123.111 | -60.9192 | 62.0499 | 0.19432 | -0.004798 | -0.0096343 | 0.0024202 | 0.059891 | -0.0020187 | 0.065702 | -61.084 | 62.2284 | -61.2579 | -61.1526 | 61.7523 | -0.09613 | 0.018311 | 0.086975 | 62.1552 | -61.2534 | -0.33875 | 0.17853 | -0.16479 | -0.23346 | -0.29755 | -0.33417 | 0.10528 | 0.17395 | 60.9375 | 61.0062 | 122.6715 | 123.1476 | -0.16479 | 123.0743 | 60.8231 | -0.33417 | 123.1476 | -0.16479 | 60.8231 | 122.6715 | 123.0743 | -123.3078 | -123.3032
3025.7656 | 123.143 | -60.9146 | 62.0773 | 0.20958 | -0.006507 | -0.012198 | 0.0039156 | 0.061814 | -0.0052231 | 0.066129 | -61.0931 | 62.2375 | -61.2717 | -61.203 | 61.702 | -0.30212 | -0.12817 | 0.29755 | 62.1048 | -61.2946 | -0.35706 | 0.16022 | -0.17853 | -0.28839 | -0.37537 | -0.37994 | 0.027465 | 0.17853 | 60.7864 | 61.2122 | 122.6166 | 123.1522 | -0.17853 | 123.0194 | 60.6125 | -0.37994 | 123.1522 | -0.17853 | 60.6125 | 122.6166 | 123.0194 | -123.349 | -123.3719
3026.7656 | 123.2437 | -60.9009 | 61.9995 | 0.27824 | -0.0084296 | -0.0068573 | 0.00092504 | 0.064378 | -0.0045821 | 0.068265 | -61.0016 | 62.1552 | -61.2305 | -61.1069 | 61.8439 | 0.041199 | -0.23346 | 0.17853 | 62.0911 | -61.2213 | -0.32959 | 0.15564 | -0.10071 | -0.20599 | -0.15564 | -0.32043 | 0.091552 | 0.22888 | 60.6674 | 61.0794 | 122.7448 | 123.056 | -0.10071 | 122.9919 | 60.9421 | -0.32043 | 123.056 | -0.10071 | 60.9421 | 122.7448 | 122.9919 | -123.23 | -123.2208
3027.7656 | 123.0927 | -60.9146 | 62.0819 | 0.2401 | -0.0035162 | -0.013693 | 0.0047702 | 0.062455 | -0.0052231 | 0.067411 | -61.0886 | 62.2375 | -61.29 | -61.203 | 61.7249 | -0.064087 | -0.032043 | 0.07782 | 62.1689 | -61.2671 | -0.37537 | 0.15564 | -0.17395 | -0.28839 | -0.35706 | -0.35248 | 0.086975 | 0.20142 | 60.8826 | 60.9924 | 122.6395 | 123.1522 | -0.17395 | 123.0835 | 60.8505 | -0.35248 | 123.1522 | -0.17395 | 60.8505 | 122.6395 | 123.0835 | -123.3719 | -123.349
3028.7656 | 123.0881 | -60.9329 | 62.0728 | 0.1638 | -0.0052252 | -0.012625 | 0.005411 | 0.0616 | -0.0080001 | 0.06677 | -61.0794 | 62.2192 | -61.2534 | -61.2213 | 61.7386 | -0.082397 | 0 | 0.073242 | 62.1735 | -61.2488 | -0.32044 | 0.14648 | -0.14649 | -0.28839 | -0.33417 | -0.31586 | 0.10071 | 0.17395 | 60.9329 | 61.0062 | 122.6715 | 123.1522 | -0.14649 | 123.1064 | 60.8505 | -0.31586 | 123.1522 | -0.14649 | 60.8505 | 122.6715 | 123.1064 | -123.3261 | -123.3215
3029.7656 | 123.1338 | -60.9467 | 62.0728 | -1.1332 | -0.0050116 | -0.0077117 | 0.004343 | 0.063737 | -0.0047957 | 0.067197 | -61.0519 | 62.2421 | -61.2488 | -61.1984 | 61.7249 | -0.064087 | -0.032043 | 0.054932 | 62.1597 | -61.2854 | -0.30212 | 0.16937 | -0.10529 | -0.25177 | -0.3479 | -0.33875 | 0.086975 | 0.19684 | 60.9146 | 61.0016 | 122.6715 | 123.1888 | -0.10529 | 123.1064 | 60.8826 | -0.33875 | 123.1888 | -0.10529 | 60.8826 | 122.6715 | 123.1064 | -123.3215 | -123.3582
3030.7656 | 123.1018 | -60.9375 | 62.0544 | 0.20195 | -0.0026618 | -0.0092071 | 0.003702 | 0.063096 | -0.0050095 | 0.065488 | -61.2625 | 62.178 | -61.2946 | -61.1664 | 61.7569 | -0.054932 | -0.064087 | 0.064087 | 62.1552 | -61.2762 | -0.35706 | 0.1236 | -0.32501 | -0.22888 | -0.29755 | -0.33875 | 0.10071 | 0.032044 | 60.8734 | 61.0016 | 122.6944 | 123.1155 | -0.32501 | 123.0927 | 60.8826 | -0.33875 | 123.1155 | -0.32501 | 60.8826 | 122.6944 | 123.0927 | -123.349 | -123.3307
3031.7656 | 123.1201 | -60.9375 | 62.0499 | 0.17906 | -0.0043708 | -0.010062 | 0.005411 | 0.058396 | -0.0045821 | 0.066556 | -61.0703 | 62.2467 | -61.2671 | -61.1481 | 61.8118 | -0.07782 | 0.018311 | 0.086975 | 62.1323 | -61.2808 | -0.32959 | 0.19684 | -0.13275 | -0.21057 | -0.23804 | -0.34332 | 0.082397 | 0.19684 | 60.9558 | 61.0245 | 122.7493 | 123.1842 | -0.13275 | 123.0698 | 60.8597 | -0.34332 | 123.1842 | -0.13275 | 60.8597 | 122.7493 | 123.0698 | -123.317 | -123.3307
3032.7656 | 123.1293 | -60.9375 | 62.0956 | 0.2401 | -0.0041572 | -0.010275 | 0.0032748 | 0.060532 | -0.0020187 | 0.070829 | -61.084 | 62.2101 | -61.2442 | -61.4319 | 61.7752 | 0.10071 | -0.013733 | 0.14648 | 62.1872 | -61.2717 | -0.3067 | 0.11444 | -0.14648 | -0.49439 | -0.32043 | -0.33417 | 0.091553 | 0.16022 | 60.9238 | 61.084 | 122.7127 | 123.1476 | -0.14648 | 123.1247 | 61.0382 | -0.33417 | 123.1476 | -0.14648 | 61.0382 | 122.7127 | 123.1247 | -123.3398 | -123.3673
3033.7656 | 123.317 | -60.8963 | 62.0041 | 0.23247 | -0.007575 | -0.012839 | 0.00071144 | 0.059891 | -0.0030869 | 0.06677 | -61.0107 | 62.1735 | -61.2488 | -61.1114 | 61.8347 | 0.036621 | -0.23346 | 0.17395 | 62.0728 | -61.2442 | -0.35248 | 0.16937 | -0.11444 | -0.21515 | -0.16937 | -0.3479 | 0.068665 | 0.23804 | 60.6628 | 61.0703 | 122.731 | 123.0698 | -0.11444 | 122.9691 | 60.9329 | -0.3479 | 123.0698 | -0.11444 | 60.9329 | 122.731 | 122.9691 | -123.2529 | -123.2483
3034.7656 | 123.1064 | -60.9467 | 62.0544 | 0.12566 | -0.0043708 | -0.011771 | 0.0058382 | 0.062028 | -0.0045821 | 0.06677 | -61.0794 | 62.2055 | -61.2762 | -61.1847 | 61.7477 | -0.068665 | -0.027466 | 0.054932 | 62.1552 | -61.2854 | -0.32959 | 0.15106 | -0.13275 | -0.23804 | -0.3067 | -0.33875 | 0.10071 | 0.19684 | 60.9192 | 61.0016 | 122.6944 | 123.1522 | -0.13275 | 123.1018 | 60.878 | -0.33875 | 123.1522 | -0.13275 | 60.878 | 122.6944 | 123.1018 | -123.3307 | -123.3398
3035.7656 | 123.1201 | -60.9421 | 62.0407 | 0.19432 | -0.006507 | -0.0068573 | 0.0047702 | 0.060532 | -0.0054367 | 0.066556 | -61.084 | 62.233 | -61.2625 | -61.2167 | 61.7249 | -0.073242 | -0.032043 | 0.073242 | 62.1506 | -61.2488 | -0.32043 | 0.19226 | -0.14191 | -0.27466 | -0.31586 | -0.3067 | 0.10986 | 0.17853 | 60.91 | 61.0153 | 122.6669 | 123.175 | -0.14191 | 123.0927 | 60.8688 | -0.3067 | 123.175 | -0.14191 | 60.8688 | 122.6669 | 123.0927 | -123.3032 | -123.2895
3036.7656 | 123.1247 | -60.9375 | 62.0453 | 0.07988 | -0.0045844 | -0.011984 | 0.0022066 | 0.062669 | -0.0050095 | 0.066984 | -61.0794 | 62.2238 | -61.2808 | -61.1893 | 61.7477 | -0.059509 | -0.050354 | 0.073242 | 62.1597 | -61.2579 | -0.34332 | 0.17853 | -0.14191 | -0.25177 | -0.29755 | -0.32044 | 0.11444 | 0.20142 | 60.8871 | 61.0107 | 122.6852 | 123.1613 | -0.14191 | 123.0972 | 60.878 | -0.32044 | 123.1613 | -0.14191 | 60.878 | 122.6852 | 123.0972 | -123.3261 | -123.3032
3037.7656 | 123.1247 | -60.91 | 62.059 | -0.33211 | -0.0073614 | -0.012625 | 0.0034884 | 0.059891 | -0.0054367 | 0.06677 | -61.0886 | 62.2284 | -61.2442 | -61.2122 | 61.7477 | -0.082397 | -0.036621 | 0.064087 | 62.1323 | -61.2808 | -0.33417 | 0.16937 | -0.17853 | -0.30212 | -0.31128 | -0.37079 | 0.073242 | 0.15564 | 60.8734 | 60.9741 | 122.6578 | 123.1384 | -0.17853 | 123.0423 | 60.8276 | -0.37079 | 123.1384 | -0.17853 | 60.8276 | 122.6578 | 123.0423 | -123.3032 | -123.3398
3038.7656 | 123.1522 | -60.9329 | 62.059 | 2.033 | -0.0050116 | -0.012625 | 0.0047702 | 0.062882 | -0.0067185 | 0.066129 | -60.8871 | 62.2055 | -61.2579 | -61.1847 | 61.7523 | -0.082397 | -0.059509 | 0.068665 | 62.1414 | -61.2625 | -0.32501 | 0.14648 | 0.045776 | -0.25177 | -0.3067 | -0.32959 | 0.082397 | 0.37079 | 60.8734 | 61.0016 | 122.6852 | 123.1384 | 0.045776 | 123.0743 | 60.8505 | -0.32959 | 123.1384 | 0.045776 | 60.8505 | 122.6852 | 123.0743 | -123.317 | -123.3215
3039.7656 | 123.1155 | -60.9329 | 62.059 | 0.23247 | -0.008216 | -0.012625 | 0.0032748 | 0.060319 | -0.0054367 | 0.065061 | -61.116 | 62.1918 | -61.29 | -61.2122 | 61.7889 | -0.041199 | -0.013733 | 0.086975 | 62.1689 | -61.2717 | -0.35706 | 0.13275 | -0.18311 | -0.27924 | -0.27008 | -0.33875 | 0.10986 | 0.17395 | 60.9192 | 61.0199 | 122.7219 | 123.1247 | -0.18311 | 123.1018 | 60.8917 | -0.33875 | 123.1247 | -0.18311 | 60.8917 | 122.7219 | 123.1018 | -123.349 | -123.3307
3040.7656 | 123.2391 | -60.8871 | 62.0132 | 0.26299 | -0.0080024 | -0.013693 | 7.0444e-05 | 0.061814 | -0.0020187 | 0.066129 | -60.997 | 62.1414 | -61.2213 | -61.2991 | 61.7569 | 0.059509 | -0.15106 | 0.21057 | 62.1094 | -61.2305 | -0.33417 | 0.12817 | -0.10986 | -0.41199 | -0.25635 | -0.34332 | 0.09613 | 0.2243 | 60.7361 | 61.0977 | 122.644 | 123.0286 | -0.10986 | 122.9965 | 60.9467 | -0.34332 | 123.0286 | -0.10986 | 60.9467 | 122.644 | 122.9965 | -123.2346 | -123.2437
3041.7656 | 123.0881 | -60.9283 | 62.0728 | 0.17143 | -0.0037298 | -0.011771 | 0.0066928 | 0.061387 | -0.0058639 | 0.071897 | -61.0794 | 62.2421 | -61.2671 | -61.4594 | 61.4868 | -0.050354 | 0.073242 | 0.13275 | 62.1552 | -61.2808 | -0.33875 | 0.16937 | -0.15106 | -0.53101 | -0.58594 | -0.35248 | 0.082397 | 0.18768 | 61.0016 | 61.0611 | 122.4152 | 123.1705 | -0.15106 | 123.0835 | 60.878 | -0.35248 | 123.1705 | -0.15106 | 60.878 | 122.4152 | 123.0835 | -123.3398 | -123.3536
3042.7656 | 123.1796 | -60.9329 | 62.0499 | 0.17906 | -0.0052252 | -0.0092071 | 0.0058382 | 0.062241 | -0.0056503 | 0.065275 | -61.0886 | 62.2192 | -61.29 | -61.203 | 61.734 | -0.082397 | -0.068665 | -0.31128 | 62.1094 | -61.3083 | -0.35706 | 0.16937 | -0.15564 | -0.27008 | -0.31586 | -0.37537 | 0.059509 | 0.20142 | 60.8643 | 60.6216 | 122.6669 | 123.1522 | -0.15564 | 123.0423 | 60.8505 | -0.37537 | 123.1522 | -0.15564 | 60.8505 | 122.6669 | 123.0423 | -123.3398 | -123.3582
3043.7656 | 123.1338 | -60.9421 | 62.0499 | 0.1638 | -0.0056524 | -0.0092071 | 0.0022066 | 0.0616 | -0.0037277 | 0.067624 | -61.0703 | 62.2101 | -61.2625 | -61.203 | 61.7615 | -0.059509 | -0.068665 | 0.073242 | 62.1323 | -61.29 | -0.32043 | 0.16022 | -0.12817 | -0.26093 | -0.28839 | -0.3479 | 0.082397 | 0.19226 | 60.8734 | 61.0153 | 122.7036 | 123.1522 | -0.12817 | 123.0743 | 60.8826 | -0.3479 | 123.1522 | -0.12817 | 60.8826 | 122.7036 | 123.0743 | -123.3124 | -123.3398
3044.7656 | 123.1384 | -60.9283 | 62.0544 | 0.12566 | -0.0054388 | -0.01113 | 0.0045566 | 0.061814 | -0.0045821 | 0.067197 | -61.0931 | 62.2101 | -61.2534 | -61.1938 | 61.7477 | -0.073242 | -0.059509 | 0.082397 | 62.1368 | -61.2808 | -0.32501 | 0.15564 | -0.16479 | -0.2655 | -0.3067 | -0.35248 | 0.082398 | 0.16022 | 60.8688 | 61.0107 | 122.6761 | 123.1384 | -0.16479 | 123.0652 | 60.8551 | -0.35248 | 123.1384 | -0.16479 | 60.8551 | 122.6761 | 123.0652 | -123.3078 | -123.3353
3045.7656 | 123.2208 | -60.8871 | 62.0178 | -0.32448 | -0.008216 | -0.010703 | -0.0022794 | 0.060319 | -0.0073593 | 0.065275 | -60.997 | 62.1643 | -61.2213 | -61.1298 | 61.8301 | 0.013733 | -0.2243 | 0.18768 | 62.0819 | -61.2305 | -0.33417 | 0.14648 | -0.10986 | -0.24262 | -0.18768 | -0.34332 | 0.064087 | 0.2243 | 60.6628 | 61.0748 | 122.7173 | 123.0515 | -0.10986 | 122.9691 | 60.9009 | -0.34332 | 123.0515 | -0.10986 | 60.9009 | 122.7173 | 122.9691 | -123.2391 | -123.2483
3046.7656 | 123.2346 | -60.8917 | 62.0132 | 0.20195 | -0.0073614 | -0.011557 | -0.00035676 | 0.059251 | -0.0054367 | 0.066556 | -60.9741 | 62.1368 | -61.2488 | -61.0703 | 61.8713 | 0.036621 | -0.19226 | 0.20142 | 62.0865 | -61.2259 | -0.35705 | 0.1236 | -0.082397 | -0.17853 | -0.14191 | -0.33417 | 0.073242 | 0.27466 | 60.6995 | 61.0931 | 122.7631 | 123.0286 | -0.082397 | 122.9782 | 60.9283 | -0.33417 | 123.0286 | -0.082397 | 60.9283 | 122.7631 | 122.9782 | -123.262 | -123.2391
3047.7656 | 123.2391 | -60.8734 | 62.0132 | 0.31639 | -0.0062934 | -0.010703 | 0.001993 | 0.061173 | -0.0060775 | 0.064207 | -61.0107 | 62.1368 | -61.2305 | -61.2396 | 61.9354 | 0.07782 | -0.18768 | 0.21973 | 62.1002 | -61.2122 | -0.35706 | 0.1236 | -0.13733 | -0.36621 | -0.07782 | -0.33875 | 0.086975 | 0.21973 | 60.6857 | 61.0931 | 122.8088 | 123.0103 | -0.13733 | 122.9736 | 60.9512 | -0.33875 | 123.0103 | -0.13733 | 60.9512 | 122.8088 | 122.9736 | -123.2437 | -123.2254
3048.7656 | 123.1293 | -60.9467 | 62.0819 | 0.19432 | -0.0037298 | -0.010703 | 0.0064792 | 0.062028 | -0.0045821 | 0.068265 | -61.0703 | 62.2238 | -61.2808 | -61.4639 | 61.5601 | 0.032043 | 0.009155 | 0.15106 | 62.1368 | -61.29 | -0.33417 | 0.14191 | -0.1236 | -0.51727 | -0.52185 | -0.34332 | 0.054932 | 0.21057 | 60.9558 | 61.0977 | 122.5067 | 123.1705 | -0.1236 | 123.0835 | 60.9787 | -0.34332 | 123.1705 | -0.1236 | 60.9787 | 122.5067 | 123.0835 | -123.3627 | -123.3719
3049.7656 | 123.1247 | -60.9421 | 62.0819 | 0.19432 | -0.0045844 | -0.0085663 | 0.00712 | 0.059891 | -0.0037277 | 0.066556 | -61.0886 | 62.2101 | -61.2762 | -61.1893 | 61.734 | -0.086975 | -0.4303 | -0.19226 | 62.0773 | -61.3083 | -0.33417 | 0.12817 | -0.14648 | -0.24719 | -0.3479 | -0.36621 | -0.004577 | 0.18768 | 60.5118 | 60.7498 | 122.6761 | 123.1522 | -0.14648 | 123.0194 | 60.8551 | -0.36621 | 123.1522 | -0.14648 | 60.8551 | 122.6761 | 123.0194 | -123.3582 | -123.3902
3050.7656 | 123.1293 | -60.9421 | 62.059 | 0.21721 | -0.0067206 | -0.01348 | 0.0041292 | 0.0616 | -0.0033005 | 0.067624 | -61.0611 | 62.2101 | -61.29 | -61.1893 | 61.7615 | -0.054932 | -0.07782 | 0.068665 | 62.1368 | -61.2762 | -0.3479 | 0.15106 | -0.11902 | -0.24719 | -0.29755 | -0.33417 | 0.07782 | 0.22888 | 60.8643 | 61.0107 | 122.7036 | 123.1522 | -0.11902 | 123.0789 | 60.8871 | -0.33417 | 123.1522 | -0.11902 | 60.8871 | 122.7036 | 123.0789 | -123.349 | -123.3353
3051.7656 | 123.1155 | -60.8963 | 62.0361 | 0.23247 | -0.0033026 | -0.0066437 | 0.0039156 | 0.062028 | -0.0043685 | 0.066343 | -61.0748 | 62.2055 | -61.2579 | -61.203 | 61.7752 | -0.07782 | -0.064087 | 0.064087 | 62.1597 | -61.2442 | -0.36163 | 0.16937 | -0.17853 | -0.3067 | -0.26093 | -0.3479 | 0.1236 | 0.18311 | 60.8322 | 60.9604 | 122.6715 | 123.1018 | -0.17853 | 123.056 | 60.8185 | -0.3479 | 123.1018 | -0.17853 | 60.8185 | 122.6715 | 123.056 | -123.2941 | -123.2803
3052.7656 | 123.1064 | -60.9375 | 62.0407 | -0.29396 | -0.0035162 | -0.012198 | 0.0030612 | 0.063309 | -0.0045821 | 0.066129 | -61.0703 | 62.2375 | -61.2991 | -61.2076 | 61.7386 | -0.068665 | -0.050354 | 0.073242 | 62.1323 | -61.2762 | -0.36163 | 0.19684 | -0.13275 | -0.27008 | -0.30212 | -0.33875 | 0.091553 | 0.22888 | 60.8871 | 61.0107 | 122.6761 | 123.175 | -0.13275 | 123.0698 | 60.8688 | -0.33875 | 123.175 | -0.13275 | 60.8688 | 122.6761 | 123.0698 | -123.3398 | -123.317
3053.7656 | 123.2483 | -60.9055 | 62.0407 | -0.19478 | -0.0073614 | -0.014121 | 0.00049764 | 0.059678 | -0.0052231 | 0.065916 | -60.91 | 62.1414 | -61.235 | -61.1069 | 61.821 | 0.013733 | -0.22888 | 0.17853 | 62.1094 | -61.2579 | -0.32959 | 0.10071 | -0.004577 | -0.20142 | -0.21973 | -0.35248 | 0.068665 | 0.32501 | 60.6766 | 61.084 | 122.7264 | 123.0469 | -0.004577 | 123.0148 | 60.9192 | -0.35248 | 123.0469 | -0.004577 | 60.9192 | 122.7264 | 123.0148 | -123.2758 | -123.2986
3054.7656 | 123.2254 | -60.8871 | 62.0087 | 0.2401 | -0.0060798 | -0.01348 | 0.0011386 | 0.060319 | -0.0052231 | 0.065702 | -61.1526 | 62.1094 | -61.235 | -61.0977 | 61.8393 | 0.032043 | -0.22888 | 0.16937 | 62.1094 | -61.2396 | -0.3479 | 0.10071 | -0.2655 | -0.21057 | -0.16937 | -0.35248 | 0.10071 | 0.082397 | 60.6583 | 61.0565 | 122.7264 | 122.9965 | -0.2655 | 122.9965 | 60.9192 | -0.35248 | 122.9965 | -0.2655 | 60.9192 | 122.7264 | 122.9965 | -123.2437 | -123.2483
3055.7656 | 123.1247 | -60.9238 | 62.0728 | 0.20195 | 0.0016108 | -0.0068573 | 0.0062656 | 0.060746 | -0.0058639 | 0.064634 | -61.3541 | 62.1506 | -61.3037 | -61.1618 | 61.7615 | -0.064087 | -0.032043 | 0.059509 | 62.1277 | -61.2671 | -0.37994 | 0.07782 | -0.4303 | -0.23804 | -0.31128 | -0.34332 | 0.054932 | -0.050354 | 60.8917 | 60.9833 | 122.6852 | 123.0743 | -0.4303 | 123.0515 | 60.8597 | -0.34332 | 123.0743 | -0.4303 | 60.8597 | 122.6852 | 123.0515 | -123.3765 | -123.3398
3056.7656 | 123.1293 | -60.91 | 62.0544 | 0.22484 | -0.0035162 | -0.0053619 | 0.0062656 | 0.06096 | -0.0056503 | 0.06677 | -61.0794 | 62.2101 | -61.2946 | -61.1435 | 61.7981 | -0.073242 | 0.004578 | 0.10986 | 62.1506 | -61.2717 | -0.38452 | 0.15564 | -0.16937 | -0.23346 | -0.25635 | -0.36163 | 0.096131 | 0.21515 | 60.9146 | 61.0199 | 122.7081 | 123.1201 | -0.16937 | 123.0606 | 60.8368 | -0.36163 | 123.1201 | -0.16937 | 60.8368 | 122.7081 | 123.0606 | -123.349 | -123.3261
3057.7656 | 123.1796 | -60.9192 | 62.0499 | 0.22484 | -0.0054388 | -0.0092071 | 0.0047702 | 0.060746 | -0.0058639 | 0.065916 | -61.0565 | 62.2055 | -61.2762 | -61.1847 | 61.7798 | -0.059509 | -0.1236 | 0.086975 | 62.1048 | -61.2808 | -0.35706 | 0.15564 | -0.13733 | -0.2655 | -0.27008 | -0.36163 | 0.054931 | 0.21973 | 60.7956 | 61.0062 | 122.699 | 123.1247 | -0.13733 | 123.024 | 60.8597 | -0.36163 | 123.1247 | -0.13733 | 60.8597 | 122.699 | 123.024 | -123.3261 | -123.3307
3058.7656 | 123.1613 | -60.9741 | 62.0636 | 0.24773 | -0.0056524 | -0.0070709 | 0.002634 | 0.061173 | -0.0028731 | 0.066129 | -61.0794 | 62.2101 | -61.2534 | -61.1938 | 61.7661 | -0.068665 | -0.10071 | 0.091553 | 62.1323 | -61.2854 | -0.27924 | 0.14648 | -0.10529 | -0.21973 | -0.29755 | -0.31128 | 0.068664 | 0.17395 | 60.8734 | 61.0657 | 122.7402 | 123.1842 | -0.10529 | 123.1064 | 60.9055 | -0.31128 | 123.1842 | -0.10529 | 60.9055 | 122.7402 | 123.1064 | -123.317 | -123.349
3059.7656 | 123.1659 | -60.9192 | 62.0316 | 0.22484 | -0.0054388 | -0.011771 | 0.0030612 | 0.062455 | -0.0041549 | 0.065275 | -61.0519 | 62.2101 | -61.2579 | -61.1984 | 61.7615 | -0.082397 | -0.09613 | 0.07782 | 62.1506 | -61.2488 | -0.33875 | 0.17853 | -0.13275 | -0.27924 | -0.27008 | -0.32959 | 0.11902 | 0.20599 | 60.8231 | 60.997 | 122.6807 | 123.1293 | -0.13275 | 123.0698 | 60.8368 | -0.32959 | 123.1293 | -0.13275 | 60.8368 | 122.6807 | 123.0698 | -123.2895 | -123.2803
3060.7656 | 123.2483 | -60.9283 | 62.027 | 0.19432 | -0.0062934 | -0.011343 | -0.00099756 | 0.062241 | -0.0054367 | 0.068052 | -61.0153 | 62.1185 | -61.2396 | -61.1206 | 61.8484 | 0.013733 | -0.20599 | 0.1831 | 62.0956 | -61.2305 | -0.31128 | 0.091552 | -0.086975 | -0.19226 | -0.17853 | -0.30212 | 0.068664 | 0.2243 | 60.7224 | 61.1114 | 122.7768 | 123.0469 | -0.086975 | 123.024 | 60.9421 | -0.30212 | 123.0469 | -0.086975 | 60.9421 | 122.7768 | 123.024 | -123.2666 | -123.2574
3061.7656 | 123.2208 | -60.9009 | 62.0087 | 0.17906 | -0.004798 | -0.013266 | -0.00057036 | 0.060319 | -0.0043685 | 0.067197 | -61.0062 | 62.1506 | -61.2259 | -61.116 | 61.8439 | 0.018311 | -0.19226 | 0.19226 | 62.0911 | -61.2305 | -0.32501 | 0.14191 | -0.10529 | -0.21515 | -0.1648 | -0.32959 | 0.082397 | 0.21973 | 60.7086 | 61.0931 | 122.7448 | 123.0515 | -0.10529 | 122.9919 | 60.9192 | -0.32959 | 123.0515 | -0.10529 | 60.9192 | 122.7448 | 122.9919 | -123.2346 | -123.2391
3062.7812 | 123.2346 | -60.8551 | 62.0728 | -0.087967 | -0.010566 | -0.011771 | -0.00057036 | 0.057328 | -0.0062911 | 0.066129 | -60.997 | 62.114 | -61.2717 | -61.0748 | 61.8759 | 0.13733 | -0.068665 | 0.32501 | 62.1368 | -61.1847 | -0.41656 | 0.041199 | -0.14191 | -0.21973 | -0.19684 | -0.32959 | 0.064087 | 0.27466 | 60.7864 | 61.1801 | 122.731 | 122.9691 | -0.14191 | 122.9919 | 60.9924 | -0.32959 | 122.9691 | -0.14191 | 60.9924 | 122.731 | 122.9919 | -123.3444 | -123.2574
3063.7656 | 123.2437 | -60.8917 | 62.0316 | 0.2401 | -0.0069342 | -0.01348 | 0.0045566 | 0.058823 | -0.0047957 | 0.065488 | -61.0336 | 62.1689 | -61.2579 | -61.1206 | 61.7981 | -0.018311 | -0.19684 | 0.16479 | 62.0773 | -61.2488 | -0.36621 | 0.13733 | -0.14191 | -0.22888 | -0.23346 | -0.35705 | 0.045777 | 0.22431 | 60.6949 | 61.0565 | 122.6898 | 123.0606 | -0.14191 | 122.9691 | 60.8734 | -0.35705 | 123.0606 | -0.14191 | 60.8734 | 122.6898 | 122.9691 | -123.2895 | -123.2803
3064.7656 | 123.2208 | -60.9192 | 62.0041 | 0.2401 | -0.0060798 | -0.014548 | 0.0056246 | 0.060105 | -0.0041549 | 0.064847 | -61.0245 | 62.1414 | -61.2442 | -61.1206 | 61.821 | -0.018311 | -0.20599 | 0.17395 | 62.0956 | -61.2488 | -0.32501 | 0.13733 | -0.10529 | -0.20142 | -0.1831 | -0.32959 | 0.091553 | 0.21973 | 60.7132 | 61.0931 | 122.7402 | 123.0606 | -0.10529 | 123.0148 | 60.9009 | -0.32959 | 123.0606 | -0.10529 | 60.9009 | 122.7402 | 123.0148 | -123.2483 | -123.2529
3065.7812 | 123.2529 | -60.9055 | 62.0361 | 0.24773 | -0.0077888 | -0.010916 | 0.0015658 | 0.065873 | -0.0054367 | 0.066129 | -60.997 | 62.1185 | -61.2396 | -61.0153 | 61.9308 | 0.10071 | -0.19226 | 0.20599 | 62.1002 | -61.203 | -0.33417 | 0.082397 | -0.091552 | -0.10986 | -0.10529 | -0.29755 | 0.064087 | 0.24262 | 60.7132 | 61.1115 | 122.8363 | 123.024 | -0.091552 | 123.0057 | 61.0062 | -0.29755 | 123.024 | -0.091552 | 61.0062 | 122.8363 | 123.0057 | -123.2758 | -123.2391
3066.7656 | 123.23 | -60.9238 | 62.027 | 0.27061 | -0.0062934 | -0.010703 | 0.0058382 | 0.060319 | -0.0039413 | 0.065275 | -61.0291 | 62.1872 | -61.2488 | -61.1343 | 61.8073 | -0.013733 | -0.17853 | 0.15106 | 62.1002 | -61.2259 | -0.32501 | 0.16022 | -0.10529 | -0.21057 | -0.21973 | -0.30212 | 0.073242 | 0.21973 | 60.7452 | 61.0748 | 122.731 | 123.111 | -0.10529 | 123.024 | 60.91 | -0.30212 | 123.111 | -0.10529 | 60.91 | 122.731 | 123.024 | -123.2758 | -123.2529
3067.7812 | 123.175 | -60.878 | 62.0728 | -0.19478 | -0.009284 | -0.013693 | -0.00078396 | 0.061173 | -0.0054367 | 0.066556 | -61.0062 | 62.1689 | -61.2122 | -61.0931 | 61.8668 | 0.09613 | 0.027466 | 0.29297 | 62.1506 | -61.1938 | -0.33417 | 0.09613 | -0.12817 | -0.21515 | -0.20599 | -0.31586 | 0.07782 | 0.20599 | 60.9055 | 61.171 | 122.7448 | 123.0469 | -0.12817 | 123.0286 | 60.9741 | -0.31586 | 123.0469 | -0.12817 | 60.9741 | 122.7448 | 123.0286 | -123.2849 | -123.2666
3068.7656 | 123.2025 | -60.8688 | 62.0636 | 0.23247 | -0.007575 | -0.014761 | -0.00057036 | 0.060105 | -0.0037277 | 0.066129 | -61.0428 | 62.1048 | -61.2488 | -61.1252 | 61.821 | 0.009155 | -0.15564 | 0.16937 | 62.1094 | -61.2305 | -0.37994 | 0.041198 | -0.17395 | -0.25635 | -0.24262 | -0.36163 | 0.045776 | 0.20599 | 60.7132 | 61.0382 | 122.6898 | 122.9736 | -0.17395 | 122.9782 | 60.878 | -0.36163 | 122.9736 | -0.17395 | 60.878 | 122.6898 | 122.9782 | -123.3124 | -123.2941
3069.7656 | 123.2071 | -60.9192 | 62.0499 | 0.27061 | -0.006507 | -0.011771 | 0.0066928 | 0.060105 | -0.0050095 | 0.065702 | -61.0565 | 62.1643 | -61.2762 | -61.1435 | 61.8027 | -0.032043 | -0.16479 | 0.11902 | 62.1002 | -61.2717 | -0.35706 | 0.11444 | -0.13733 | -0.2243 | -0.24719 | -0.35248 | 0.050354 | 0.21973 | 60.7544 | 61.0382 | 122.7219 | 123.0835 | -0.13733 | 123.0194 | 60.8871 | -0.35248 | 123.0835 | -0.13733 | 60.8871 | 122.7219 | 123.0194 | -123.3261 | -123.3215
3070.7656 | 123.2437 | -60.8871 | 62.0087 | 0.25536 | -0.0060798 | -0.0083527 | 0.004343 | 0.06096 | -0.0058639 | 0.066984 | -60.997 | 62.1231 | -61.2305 | -61.1069 | 61.8301 | -0.004578 | -0.25177 | 0.17853 | 62.0911 | -61.2167 | -0.34332 | 0.11444 | -0.10986 | -0.21973 | -0.17853 | -0.32959 | 0.082397 | 0.23346 | 60.6354 | 61.0657 | 122.7173 | 123.0103 | -0.10986 | 122.9782 | 60.8826 | -0.32959 | 123.0103 | -0.10986 | 60.8826 | 122.7173 | 122.9782 | -123.2391 | -123.2254
3071.7656 | 123.2346 | -60.8871 | 62.0224 | 0.28587 | -0.006507 | -0.0087799 | 0.005411 | 0.062882 | -0.0073593 | 0.063993 | -60.997 | 62.1231 | -61.2534 | -61.0931 | 61.8347 | 0.009155 | -0.24719 | 0.17395 | 62.1048 | -61.1847 | -0.36621 | 0.10071 | -0.10986 | -0.20599 | -0.18768 | -0.29755 | 0.082397 | 0.25635 | 60.64 | 61.0611 | 122.7219 | 123.0103 | -0.10986 | 122.9919 | 60.8963 | -0.29755 | 123.0103 | -0.10986 | 60.8963 | 122.7219 | 122.9919 | -123.2758 | -123.2071
3072.7812 | 123.2346 | -60.8734 | 62.0453 | -0.072708 | -0.0069342 | -0.011771 | -0.0063382 | 0.056473 | -0.0024459 | 0.065488 | -60.9833 | 62.1277 | -61.2305 | -61.1298 | 61.8301 | 0.073242 | -0.064087 | 0.27466 | 62.0911 | -61.1755 | -0.35706 | 0.082398 | -0.10986 | -0.25635 | -0.21515 | -0.30212 | 0.045776 | 0.24719 | 60.8093 | 61.1481 | 122.7036 | 123.0011 | -0.10986 | 122.9645 | 60.9467 | -0.30212 | 123.0011 | -0.10986 | 60.9467 | 122.7036 | 122.9645 | -123.2758 | -123.2208
3073.7656 | 123.2346 | -60.8826 | 62.0224 | 0.18669 | -0.0073614 | -0.010062 | 0.00712 | 0.060532 | -0.0052231 | 0.066129 | -60.9787 | 62.1277 | -61.2305 | -61.0886 | 61.8347 | 0.027466 | -0.24261 | 0.16479 | 62.0956 | -61.2167 | -0.3479 | 0.10529 | -0.096131 | -0.20599 | -0.18768 | -0.33417 | 0.073242 | 0.25177 | 60.64 | 61.0474 | 122.7173 | 123.0103 | -0.096131 | 122.9782 | 60.91 | -0.33417 | 123.0103 | -0.096131 | 60.91 | 122.7173 | 122.9782 | -123.2529 | -123.2391
3074.7656 | 123.1888 | -60.8871 | 62.059 | 0.064621 | -0.0073614 | -0.013693 | -0.00014316 | 0.059678 | -0.0058639 | 0.067197 | -61.0611 | 62.1231 | -61.235 | -61.1435 | 61.821 | -0.004578 | -0.11444 | 0.17395 | 62.0865 | -61.2213 | -0.3479 | 0.064087 | -0.17395 | -0.25635 | -0.23804 | -0.33417 | 0.027466 | 0.17395 | 60.7727 | 61.0611 | 122.7081 | 123.0103 | -0.17395 | 122.9736 | 60.8826 | -0.33417 | 123.0103 | -0.17395 | 60.8826 | 122.7081 | 122.9736 | -123.2941 | -123.2803
3075.7656 | 123.2071 | -60.8917 | 62.0407 | 0.064621 | -0.0088568 | -0.010916 | -0.00057036 | 0.057328 | -0.0052231 | 0.068265 | -61.0565 | 62.114 | -61.2442 | -61.1343 | 61.8118 | 0 | -0.12817 | 0.17853 | 62.0911 | -61.2167 | -0.35248 | 0.073243 | -0.16479 | -0.24261 | -0.22888 | -0.32501 | 0.050354 | 0.18768 | 60.7636 | 61.0703 | 122.7036 | 123.0057 | -0.16479 | 122.9828 | 60.8917 | -0.32501 | 123.0057 | -0.16479 | 60.8917 | 122.7036 | 122.9828 | -123.2849 | -123.2574
3076.7656 | 123.23 | -60.8826 | 62.0178 | 0.46898 | -0.009925 | -0.014121 | 0.0060518 | 0.055619 | -0.0041549 | 0.06677 | -60.9924 | 62.1002 | -61.235 | -61.1069 | 61.8301 | 0.022888 | -0.23346 | 0.16479 | 62.0728 | -61.2213 | -0.35248 | 0.082398 | -0.10986 | -0.22431 | -0.18768 | -0.33875 | 0.054932 | 0.24261 | 60.6491 | 61.0474 | 122.7127 | 122.9828 | -0.10986 | 122.9553 | 60.9055 | -0.33875 | 122.9828 | -0.10986 | 60.9055 | 122.7127 | 122.9553 | -123.2529 | -123.2391
3077.7812 | 123.2529 | -60.878 | 62.059 | -0.034561 | -0.0090704 | -0.015402 | -0.0018522 | 0.056901 | -0.0043685 | 0.06677 | -60.9924 | 62.1323 | -61.2213 | -61.0611 | 61.8942 | 0.091553 | -0.1236 | 0.30212 | 62.0865 | -61.1984 | -0.34332 | 0.073242 | -0.11444 | -0.1831 | -0.16479 | -0.32043 | 0.027466 | 0.22888 | 60.7544 | 61.1801 | 122.7722 | 123.0103 | -0.11444 | 122.9645 | 60.9695 | -0.32043 | 123.0103 | -0.11444 | 60.9695 | 122.7722 | 122.9645 | -123.2803 | -123.2574
3078.7656 | 123.2391 | -60.8963 | 62.0087 | 0.20958 | -0.0084296 | -0.014121 | 0.0041292 | 0.058396 | -0.0060775 | 0.065916 | -61.0016 | 62.1277 | -61.2442 | -61.0748 | 61.853 | 0.009155 | -0.20599 | 0.18768 | 62.0453 | -61.2259 | -0.3479 | 0.11902 | -0.10529 | -0.17853 | -0.15564 | -0.32959 | 0.036621 | 0.24262 | 60.6903 | 61.084 | 122.7493 | 123.024 | -0.10529 | 122.9416 | 60.9055 | -0.32959 | 123.024 | -0.10529 | 60.9055 | 122.7493 | 122.9416 | -123.2529 | -123.2346
3079.7656 | 123.2117 | -60.878 | 62.0361 | -0.10323 | -0.0073614 | -0.013693 | 0.0034884 | 0.060319 | -0.0067185 | 0.066343 | -61.0016 | 62.1277 | -61.2167 | -61.0657 | 61.8484 | 0.013733 | -0.21515 | 0.18768 | 62.0865 | -61.1984 | -0.33874 | 0.091553 | -0.1236 | -0.18768 | -0.18768 | -0.32043 | 0.050354 | 0.21515 | 60.6628 | 61.0657 | 122.7264 | 123.0057 | -0.1236 | 122.9645 | 60.8917 | -0.32043 | 123.0057 | -0.1236 | 60.8917 | 122.7264 | 122.9645 | -123.2529 | -123.2346
3080.7656 | 123.23 | -60.878 | 62.0224 | 0.049362 | -0.0071478 | -0.016684 | 0.0051974 | 0.05861 | -0.0054367 | 0.066556 | -60.9833 | 62.1231 | -61.2305 | -61.084 | 61.853 | 0.013733 | -0.2243 | 0.19226 | 62.059 | -61.2076 | -0.35248 | 0.10071 | -0.10528 | -0.20599 | -0.16937 | -0.32959 | 0.036621 | 0.24719 | 60.6537 | 61.0703 | 122.731 | 123.0011 | -0.10528 | 122.937 | 60.8917 | -0.32959 | 123.0011 | -0.10528 | 60.8917 | 122.731 | 122.937 | -123.2529 | -123.23
3081.7656 | 123.1842 | -60.878 | 62.0453 | -1.385 | -0.0071478 | -0.01583 | -0.0020658 | 0.057114 | -0.0069321 | 0.067838 | -61.0977 | 62.1277 | -61.2167 | -61.1343 | 61.821 | -0.018311 | -0.10071 | 0.20142 | 62.1414 | -61.2213 | -0.33874 | 0.082398 | -0.21973 | -0.25635 | -0.2243 | -0.34332 | 0.09613 | 0.11902 | 60.7773 | 61.0794 | 122.699 | 123.0057 | -0.21973 | 123.0194 | 60.8597 | -0.34332 | 123.0057 | -0.21973 | 60.8597 | 122.699 | 123.0194 | -123.262 | -123.2666
3082.7656 | 123.2025 | -60.8917 | 62.0682 | -0.99586 | -0.0088568 | -0.01113 | -0.0012112 | 0.057328 | -0.0052231 | 0.063352 | -61.1023 | 62.1323 | -61.2305 | -61.116 | 61.8118 | 0.004578 | -0.10986 | 0.19684 | 62.1185 | -61.1984 | -0.33874 | 0.064087 | -0.21057 | -0.2243 | -0.25635 | -0.3067 | 0.050354 | 0.12817 | 60.7819 | 61.0886 | 122.7036 | 123.024 | -0.21057 | 123.0103 | 60.8963 | -0.3067 | 123.024 | -0.21057 | 60.8963 | 122.7036 | 123.0103 | -123.2986 | -123.2666
3083.7656 | 123.2254 | -60.878 | 62.0224 | -0.28633 | -0.007575 | -0.012839 | 0.0032748 | 0.058182 | -0.0090683 | 0.065488 | -60.9009 | 62.0956 | -61.2122 | -61.0886 | 61.8393 | 0.009155 | -0.24719 | 0.19226 | 62.0682 | -61.1938 | -0.33417 | 0.073242 | -0.022888 | -0.21057 | -0.18311 | -0.31586 | 0.045776 | 0.31128 | 60.6308 | 61.0703 | 122.7173 | 122.9736 | -0.022888 | 122.9462 | 60.8871 | -0.31586 | 122.9736 | -0.022888 | 60.8871 | 122.7173 | 122.9462 | -123.2346 | -123.2162
3084.7656 | 123.2025 | -60.8963 | 62.0316 | 0.21721 | -0.0080024 | -0.014975 | 0.0013522 | 0.057114 | -0.0056503 | 0.065916 | -61.0153 | 62.1185 | -61.235 | -61.1252 | 61.8393 | -0.009155 | -0.20142 | 0.16937 | 62.059 | -61.2122 | -0.33874 | 0.086975 | -0.11902 | -0.22888 | -0.19226 | -0.31586 | 0.027466 | 0.21973 | 60.6949 | 61.0657 | 122.7356 | 123.0148 | -0.11902 | 122.9553 | 60.8871 | -0.31586 | 123.0148 | -0.11902 | 60.8871 | 122.7356 | 122.9553 | -123.2666 | -123.2437
3085.7656 | 123.2071 | -60.8963 | 62.0407 | 0.20195 | -0.0090704 | -0.0096343 | 0.00092504 | 0.057755 | -0.0056503 | 0.065702 | -61.0107 | 62.1048 | -61.2259 | -61.1206 | 61.8301 | 0.004578 | -0.19684 | 0.17395 | 62.0728 | -61.1984 | -0.32959 | 0.064087 | -0.11444 | -0.2243 | -0.21057 | -0.30212 | 0.032044 | 0.21515 | 60.6995 | 61.0703 | 122.7264 | 123.0011 | -0.11444 | 122.9691 | 60.9009 | -0.30212 | 123.0011 | -0.11444 | 60.9009 | 122.7264 | 122.9691 | -123.2666 | -123.2391
3086.7656 | 123.2162 | -60.8917 | 62.0316 | 0.13329 | -0.0088568 | -0.016684 | 0.0034884 | 0.058396 | -0.0062911 | 0.066984 | -61.0153 | 62.0865 | -61.2442 | -61.116 | 61.8256 | 0.018311 | -0.21057 | 0.16022 | 62.0636 | -61.2122 | -0.35248 | 0.054932 | -0.1236 | -0.2243 | -0.20599 | -0.32043 | 0.032044 | 0.22888 | 60.6812 | 61.0519 | 122.7173 | 122.9782 | -0.1236 | 122.9553 | 60.91 | -0.32043 | 122.9782 | -0.1236 | 60.91 | 122.7173 | 122.9553 | -123.2758 | -123.2437
3087.7656 | 123.23 | -60.9009 | 62.027 | 0.21721 | -0.0086432 | -0.012198 | 0.0028476 | 0.057114 | -0.0080001 | 0.065916 | -61.0107 | 62.0865 | -61.2305 | -61.1114 | 61.8576 | 0.004578 | -0.20599 | 0.16022 | 62.0636 | -61.2122 | -0.32959 | 0.059509 | -0.10986 | -0.21057 | -0.16937 | -0.31128 | 0.036621 | 0.21973 | 60.6949 | 61.0611 | 122.7585 | 122.9874 | -0.10986 | 122.9645 | 60.9055 | -0.31128 | 122.9874 | -0.10986 | 60.9055 | 122.7585 | 122.9645 | -123.2574 | -123.2391
3088.7656 | 123.2071 | -60.8551 | 62.0636 | 0.034104 | -0.008216 | -0.013052 | -0.001425 | 0.056473 | -0.0073593 | 0.06442 | -61.0611 | 62.1323 | -61.2213 | -61.0931 | 61.853 | 0.064087 | -0.10986 | 0.24261 | 62.1048 | -61.1893 | -0.36621 | 0.068664 | -0.20599 | -0.23804 | -0.21057 | -0.33417 | 0.041198 | 0.16022 | 60.7452 | 61.0977 | 122.7081 | 122.9874 | -0.20599 | 122.9599 | 60.9192 | -0.33417 | 122.9874 | -0.20599 | 60.9192 | 122.7081 | 122.9599 | -123.2849 | -123.2529
3089.7656 | 123.2162 | -60.91 | 62.0361 | 0.23247 | -0.0062934 | -0.011771 | 0.0017794 | 0.057114 | -0.0062911 | 0.064207 | -61.0153 | 62.0865 | -61.2442 | -61.0931 | 61.8347 | 0.018311 | -0.21057 | 0.16937 | 62.0544 | -61.2122 | -0.33417 | 0.050354 | -0.10529 | -0.18311 | -0.20142 | -0.30212 | 0.01831 | 0.22888 | 60.6995 | 61.0794 | 122.7448 | 122.9965 | -0.10529 | 122.9645 | 60.9283 | -0.30212 | 122.9965 | -0.10529 | 60.9283 | 122.7448 | 122.9645 | -123.2803 | -123.2483
3090.7656 | 123.2117 | -60.9009 | 62.0224 | 0.20958 | -0.008216 | -0.01647 | 0.001993 | 0.055405 | -0.0056503 | 0.068693 | -61.0062 | 62.0956 | -61.2579 | -61.1023 | 61.8576 | 0.018311 | -0.20599 | 0.17395 | 62.0636 | -61.2167 | -0.35706 | 0.073242 | -0.10529 | -0.20142 | -0.16479 | -0.31586 | 0.041199 | 0.25177 | 60.6949 | 61.0748 | 122.7585 | 122.9965 | -0.10529 | 122.9645 | 60.9192 | -0.31586 | 122.9965 | -0.10529 | 60.9192 | 122.7585 | 122.9645 | -123.2803 | -123.2391
3091.7656 | 123.1796 | -60.8917 | 62.0453 | 0.15617 | -0.010139 | -0.014121 | 0.001993 | 0.058823 | -0.0075729 | 0.06442 | -61.0428 | 62.0911 | -61.2259 | -61.1252 | 61.8484 | -0.009155 | -0.16937 | 0.15564 | 62.1002 | -61.2076 | -0.33417 | 0.045776 | -0.15106 | -0.23346 | -0.19684 | -0.31586 | 0.054932 | 0.1831 | 60.7224 | 61.0474 | 122.7402 | 122.9828 | -0.15106 | 122.9919 | 60.8826 | -0.31586 | 122.9828 | -0.15106 | 60.8826 | 122.7402 | 122.9919 | -123.2712 | -123.2529
3092.7656 | 123.1842 | -60.9055 | 62.0453 | 0.20958 | -0.008216 | -0.012412 | 0.00071144 | 0.058182 | -0.0050095 | 0.067197 | -61.0565 | 62.0956 | -61.2396 | -61.1252 | 61.821 | -0.004578 | -0.14191 | 0.16022 | 62.0911 | -61.1847 | -0.33417 | 0.050354 | -0.15106 | -0.21973 | -0.2243 | -0.27923 | 0.045776 | 0.1831 | 60.7635 | 61.0657 | 122.7264 | 123.0011 | -0.15106 | 122.9965 | 60.9009 | -0.27923 | 123.0011 | -0.15106 | 60.9009 | 122.7264 | 122.9965 | -123.2849 | -123.23
3093.7656 | 123.1979 | -60.9009 | 62.0361 | 0.17143 | -0.0077888 | -0.018393 | -0.00035676 | 0.058396 | -0.0056503 | 0.066129 | -61.0336 | 62.0865 | -61.2396 | -61.1114 | 61.8256 | 0 | -0.15106 | 0.16022 | 62.0865 | -61.1984 | -0.33874 | 0.050354 | -0.13275 | -0.21057 | -0.21057 | -0.29755 | 0.050354 | 0.20599 | 60.7498 | 61.0611 | 122.7264 | 122.9874 | -0.13275 | 122.9874 | 60.9009 | -0.29755 | 122.9874 | -0.13275 | 60.9009 | 122.7264 | 122.9874 | -123.2758 | -123.2346
3094.7656 | 123.1934 | -60.8826 | 62.0224 | 0.26299 | -0.007575 | -0.016043 | -0.00014316 | 0.057755 | -0.0071457 | 0.065061 | -61.0428 | 62.1002 | -61.2259 | -61.1252 | 61.8118 | 0 | -0.16022 | 0.16937 | 62.0728 | -61.1893 | -0.34332 | 0.07782 | -0.16022 | -0.24262 | -0.21057 | -0.3067 | 0.050354 | 0.1831 | 60.7224 | 61.0519 | 122.6944 | 122.9828 | -0.16022 | 122.9553 | 60.8826 | -0.3067 | 122.9828 | -0.16022 | 60.8826 | 122.6944 | 122.9553 | -123.2483 | -123.2117
3095.7656 | 123.2437 | -60.8734 | 62.0316 | 0.011215 | -0.0077888 | -0.019461 | 0.00049764 | 0.057755 | -0.0073593 | 0.065702 | -61.0107 | 62.1048 | -61.2167 | -61.0703 | 61.8759 | 0.07782 | -0.10071 | 0.27008 | 62.1323 | -61.1481 | -0.34332 | 0.073242 | -0.13733 | -0.19684 | -0.15564 | -0.27466 | 0.10071 | 0.20599 | 60.7727 | 61.1435 | 122.7493 | 122.9782 | -0.13733 | 123.0057 | 60.9512 | -0.27466 | 122.9782 | -0.13733 | 60.9512 | 122.7493 | 123.0057 | -123.2483 | -123.1796
3096.7656 | 123.2025 | -60.9146 | 62.027 | 0.20195 | -0.011207 | -0.012839 | 0.0030612 | 0.058182 | -0.0069321 | 0.065916 | -61.0291 | 62.0956 | -61.2305 | -61.1252 | 61.821 | 0.013733 | -0.16937 | 0.31586 | 62.0911 | -61.1893 | -0.31586 | 0.068664 | -0.11444 | -0.21057 | -0.20599 | -0.27466 | 0.064086 | 0.20142 | 60.7452 | 61.2305 | 122.7356 | 123.0103 | -0.11444 | 123.0057 | 60.9283 | -0.27466 | 123.0103 | -0.11444 | 60.9283 | 122.7356 | 123.0057 | -123.2574 | -123.2162
3097.7656 | 123.2071 | -60.8826 | 62.027 | 0.23247 | -0.0090704 | -0.014334 | 0.0015658 | 0.057969 | -0.0067185 | 0.065702 | -61.0153 | 62.0682 | -61.2579 | -61.1023 | 61.8347 | -0.054932 | -0.018311 | 0.2243 | 62.1002 | -61.1847 | -0.37537 | 0.041198 | -0.13275 | -0.21973 | -0.19226 | -0.30212 | 0.073242 | 0.24262 | 60.8643 | 61.1069 | 122.7173 | 122.9507 | -0.13275 | 122.9828 | 60.8276 | -0.30212 | 122.9507 | -0.13275 | 60.8276 | 122.7173 | 122.9828 | -123.2849 | -123.2117
3098.7656 | 123.2025 | -60.8826 | 62.0361 | 0.14092 | -0.010139 | -0.01647 | 7.0444e-05 | 0.057755 | -0.0084273 | 0.066984 | -61.0611 | 62.1094 | -61.235 | -61.1206 | 61.821 | 0.013733 | -0.12817 | 0.17853 | 62.0865 | -61.2122 | -0.35248 | 0.073242 | -0.17853 | -0.23804 | -0.21515 | -0.32959 | 0.050354 | 0.17395 | 60.7544 | 61.0611 | 122.7036 | 122.9919 | -0.17853 | 122.9691 | 60.8963 | -0.32959 | 122.9919 | -0.17853 | 60.8963 | 122.7036 | 122.9691 | -123.2712 | -123.2483
3099.7656 | 123.1888 | -60.8871 | 62.027 | 0.17143 | -0.0094976 | -0.0098479 | 0.002634 | 0.056687 | -0.0056503 | 0.066343 | -61.0657 | 62.0819 | -61.2579 | -61.116 | 61.8301 | 0.009155 | -0.14191 | 0.17395 | 62.1094 | -61.1755 | -0.37079 | 0.054931 | -0.17853 | -0.22888 | -0.19684 | -0.28839 | 0.082397 | 0.19226 | 60.7452 | 61.0611 | 122.7173 | 122.9691 | -0.17853 | 122.9965 | 60.8963 | -0.28839 | 122.9691 | -0.17853 | 60.8963 | 122.7173 | 122.9965 | -123.2849 | -123.2025
3100.7656 | 123.1979 | -60.9055 | 62.0453 | 0.38506 | -0.007575 | -0.013266 | 0.0013522 | 0.056473 | -0.0077865 | 0.067838 | -61.0748 | 62.0682 | -61.2442 | -61.1069 | 61.8347 | -0.004578 | -0.16937 | 0.16479 | 62.0819 | -61.1893 | -0.33875 | 0.022888 | -0.16937 | -0.20142 | -0.21057 | -0.28381 | 0.036621 | 0.16937 | 60.7361 | 61.0703 | 122.7402 | 122.9736 | -0.16937 | 122.9874 | 60.9009 | -0.28381 | 122.9736 | -0.16937 | 60.9009 | 122.7402 | 122.9874 | -123.2895 | -123.2346
3101.7656 | 123.2437 | -60.8734 | 62.0682 | -0.019302 | -0.0084296 | -0.017966 | 0.0013522 | 0.057755 | -0.0067185 | 0.064634 | -61.0199 | 62.1231 | -61.2076 | -61.0519 | 61.8851 | 0.07782 | -0.10529 | 0.27008 | 62.1048 | -61.1572 | -0.33417 | 0.054932 | -0.14648 | -0.17853 | -0.1831 | -0.28381 | 0.036621 | 0.18768 | 60.7681 | 61.1435 | 122.7585 | 122.9965 | -0.14648 | 122.9782 | 60.9512 | -0.28381 | 122.9965 | -0.14648 | 60.9512 | 122.7585 | 122.9782 | -123.2758 | -123.2254
3102.7656 | 123.23 | -60.8917 | 62.0316 | 0.3698 | -0.0084296 | -0.017966 | 0.0011386 | 0.054978 | -0.0050095 | 0.067838 | -61.0519 | 62.1048 | -61.2579 | -61.0977 | 61.8576 | 0.073242 | -0.11444 | 0.25177 | 62.0773 | -61.1481 | -0.36621 | 0.073242 | -0.16022 | -0.20599 | -0.17395 | -0.25635 | 0.045777 | 0.20599 | 60.7773 | 61.1435 | 122.7493 | 122.9965 | -0.16022 | 122.9691 | 60.965 | -0.25635 | 122.9965 | -0.16022 | 60.965 | 122.7493 | 122.9691 | -123.2895 | -123.1796
3103.7656 | 123.3078 | -60.8826 | 62.0728 | 0.22484 | -0.0090704 | -0.012412 | 0.00071144 | 0.057969 | -0.0035141 | 0.065702 | -61.0199 | 62.0819 | -61.2625 | -61.084 | 61.8347 | 0.013733 | -0.21515 | 0.17853 | 62.0407 | -61.1938 | -0.37994 | 0.009155 | -0.13733 | -0.20142 | -0.23804 | -0.31128 | -0.032044 | 0.24262 | 60.6674 | 61.0611 | 122.7173 | 122.9645 | -0.13733 | 122.9233 | 60.8963 | -0.31128 | 122.9645 | -0.13733 | 60.8963 | 122.7173 | 122.9233 | -123.3353 | -123.2666
3104.7656 | 123.2071 | -60.8871 | 62.0407 | 0.22484 | -0.0073614 | -0.016257 | 0.0030612 | 0.058396 | -0.0060775 | 0.064847 | -61.0016 | 62.0682 | -61.2259 | -61.0931 | 61.8347 | 0.009155 | -0.21057 | 0.17395 | 62.0636 | -61.2076 | -0.33874 | 0.027466 | -0.11444 | -0.20599 | -0.20599 | -0.32043 | 0.022889 | 0.2243 | 60.6766 | 61.0611 | 122.7219 | 122.9553 | -0.11444 | 122.9507 | 60.8963 | -0.32043 | 122.9553 | -0.11444 | 60.8963 | 122.7219 | 122.9507 | -123.2666 | -123.2483
3105.7656 | 123.1934 | -60.8917 | 62.0361 | 0.20195 | -0.009284 | -0.015189 | 0.001993 | 0.055833 | -0.0062911 | 0.067624 | -61.0336 | 62.0773 | -61.2442 | -61.1252 | 61.8256 | 0 | -0.15564 | 0.16937 | 62.0728 | -61.1893 | -0.35248 | 0.041199 | -0.14191 | -0.23346 | -0.21057 | -0.29755 | 0.036621 | 0.21057 | 60.7361 | 61.0611 | 122.7173 | 122.9691 | -0.14191 | 122.9645 | 60.8917 | -0.29755 | 122.9691 | -0.14191 | 60.8917 | 122.7173 | 122.9645 | -123.2803 | -123.2254
3106.7656 | 123.1842 | -60.8963 | 62.0224 | 0.21721 | -0.009284 | -0.015402 | 0.001993 | 0.058396 | -0.0058639 | 0.066343 | -61.0245 | 62.1094 | -61.2488 | -61.1069 | 61.821 | 0.013733 | -0.1831 | 0.16479 | 62.0773 | -61.2076 | -0.35248 | 0.086975 | -0.12817 | -0.21057 | -0.20142 | -0.31128 | 0.054932 | 0.2243 | 60.7132 | 61.0611 | 122.7173 | 123.0057 | -0.12817 | 122.9736 | 60.91 | -0.31128 | 123.0057 | -0.12817 | 60.91 | 122.7173 | 122.9736 | -123.2712 | -123.23
3107.7656 | 123.2208 | -60.8917 | 62.027 | 0.20958 | -0.0069342 | -0.016898 | 0.0024202 | 0.057328 | -0.0075729 | 0.06442 | -61.0062 | 62.0865 | -61.2305 | -61.1023 | 61.8439 | 0.013733 | -0.21057 | 0.1831 | 62.0911 | -61.1938 | -0.33874 | 0.059509 | -0.11444 | -0.21057 | -0.18311 | -0.30212 | 0.064086 | 0.2243 | 60.6812 | 61.0748 | 122.7356 | 122.9782 | -0.11444 | 122.9828 | 60.9055 | -0.30212 | 122.9782 | -0.11444 | 60.9055 | 122.7356 | 122.9828 | -123.2574 | -123.2208
3108.7656 | 123.2208 | -60.8734 | 62.0499 | 0.072251 | -0.0069342 | -0.017966 | 0.0011386 | 0.056046 | -0.0050095 | 0.065916 | -61.0657 | 62.0956 | -61.2167 | -61.1069 | 61.8576 | 0.045776 | -0.10529 | 0.23804 | 62.0911 | -61.1801 | -0.34332 | 0.045776 | -0.19226 | -0.23346 | -0.19226 | -0.3067 | 0.041198 | 0.15106 | 60.7681 | 61.1114 | 122.731 | 122.9691 | -0.19226 | 122.9645 | 60.9192 | -0.3067 | 122.9691 | -0.19226 | 60.9192 | 122.731 | 122.9645 | -123.2666 | -123.23
3109.7656 | 123.2162 | -60.8871 | 62.0636 | 0.041733 | -0.0088568 | -0.015616 | -0.00099756 | 0.056901 | -0.0045821 | 0.06677 | -61.0657 | 62.1185 | -61.2305 | -61.1252 | 61.8393 | 0.036621 | -0.10986 | 0.2243 | 62.0728 | -61.1847 | -0.34332 | 0.054931 | -0.17853 | -0.23804 | -0.22431 | -0.29755 | 0.009155 | 0.16479 | 60.7773 | 61.1114 | 122.7264 | 123.0057 | -0.17853 | 122.9599 | 60.9238 | -0.29755 | 123.0057 | -0.17853 | 60.9238 | 122.7264 | 122.9599 | -123.2941 | -123.2483
3110.7656 | 123.2162 | -60.878 | 62.0361 | 0.25536 | -0.0062934 | -0.01113 | 0.0069064 | 0.05861 | -0.0065047 | 0.065061 | -61.0016 | 62.1002 | -61.2213 | -61.0611 | 61.8347 | 0.022888 | -0.22888 | 0.17395 | 62.0453 | -61.2122 | -0.34332 | 0.064087 | -0.1236 | -0.1831 | -0.20142 | -0.33417 | 0.009155 | 0.21973 | 60.6491 | 61.0519 | 122.7127 | 122.9782 | -0.1236 | 122.9233 | 60.9009 | -0.33417 | 122.9782 | -0.1236 | 60.9009 | 122.7127 | 122.9233 | -123.2574 | -123.2483
3111.7656 | 123.2071 | -60.8826 | 62.0041 | 0.27061 | -0.0056524 | -0.010703 | 0.0064792 | 0.058823 | -0.0058639 | 0.065061 | -60.9924 | 62.1002 | -61.2534 | -61.0886 | 61.8668 | 0.027466 | -0.23346 | 0.19226 | 62.0865 | -61.1801 | -0.37079 | 0.096131 | -0.10986 | -0.20599 | -0.13733 | -0.29755 | 0.082398 | 0.26093 | 60.6491 | 61.0748 | 122.7493 | 122.9828 | -0.10986 | 122.9691 | 60.91 | -0.29755 | 122.9828 | -0.10986 | 60.91 | 122.7493 | 122.9691 | -123.2574 | -123.1842
3112.7656 | 123.2208 | -60.9055 | 61.9949 | 0.23247 | -0.0067206 | -0.011343 | 0.0039156 | 0.057969 | -0.0069321 | 0.06442 | -60.997 | 62.0956 | -61.2442 | -61.0794 | 61.8713 | 0.022888 | -0.22888 | 0.1831 | 62.0407 | -61.1847 | -0.33875 | 0.10071 | -0.091552 | -0.17395 | -0.1236 | -0.27923 | 0.045776 | 0.24719 | 60.6766 | 61.0886 | 122.7768 | 123.0011 | -0.091552 | 122.9462 | 60.9283 | -0.27923 | 123.0011 | -0.091552 | 60.9283 | 122.7768 | 122.9462 | -123.2391 | -123.1796
3113.7656 | 123.2483 | -60.8597 | 62.0178 | 0.2401 | -0.0097114 | -0.012625 | 0.0041292 | 0.059251 | -0.0060775 | 0.065702 | -60.9879 | 62.0911 | -61.2442 | -61.0794 | 61.8622 | 0.032043 | -0.25635 | 0.1831 | 62.0956 | -61.1984 | -0.38452 | 0.073242 | -0.12817 | -0.21973 | -0.15564 | -0.33875 | 0.07782 | 0.25635 | 60.6033 | 61.0428 | 122.7219 | 122.9507 | -0.12817 | 122.9553 | 60.8917 | -0.33875 | 122.9507 | -0.12817 | 60.8917 | 122.7219 | 122.9553 | -123.262 | -123.2162
3114.7656 | 123.23 | -60.8963 | 62.0224 | 0.2935 | -0.0060798 | -0.012625 | 0.0062656 | 0.058823 | -0.0077865 | 0.066343 | -60.9833 | 62.1048 | -61.2442 | -61.0703 | 61.853 | 0.027466 | -0.24261 | 0.17853 | 62.0819 | -61.1938 | -0.3479 | 0.082397 | -0.086975 | -0.17395 | -0.16937 | -0.29755 | 0.059509 | 0.26093 | 60.6537 | 61.0748 | 122.7493 | 123.0011 | -0.086975 | 122.9782 | 60.9238 | -0.29755 | 123.0011 | -0.086975 | 60.9238 | 122.7493 | 122.9782 | -123.2666 | -123.2162
3115.7656 | 123.1842 | -60.91 | 62.059 | 0.1638 | -0.0090704 | -0.012839 | -0.00078396 | 0.060105 | -0.0082137 | 0.065275 | -61.0657 | 62.1002 | -61.2259 | -61.1298 | 61.8393 | 0.013733 | -0.11902 | 0.1831 | 62.0911 | -61.171 | -0.31586 | 0.041199 | -0.15564 | -0.21973 | -0.21973 | -0.26093 | 0.032043 | 0.16022 | 60.791 | 61.0931 | 122.7493 | 123.0103 | -0.15564 | 123.0011 | 60.9238 | -0.26093 | 123.0103 | -0.15564 | 60.9238 | 122.7493 | 123.0011 | -123.2849 | -123.23
3116.7656 | 123.2117 | -60.9009 | 62.0407 | 0.20195 | -0.0094976 | -0.011557 | -0.00099756 | 0.057969 | -0.0058639 | 0.06677 | -61.0519 | 62.1048 | -61.2259 | -61.1252 | 61.8164 | -0.009155 | -0.13275 | 0.1831 | 62.0911 | -61.2167 | -0.32501 | 0.064087 | -0.15106 | -0.2243 | -0.2243 | -0.31586 | 0.050354 | 0.17395 | 60.7681 | 61.084 | 122.7173 | 123.0057 | -0.15106 | 122.9919 | 60.8917 | -0.31586 | 123.0057 | -0.15106 | 60.8917 | 122.7173 | 122.9919 | -123.2666 | -123.2574
3117.7656 | 123.2208 | -60.8963 | 62.027 | 0.18669 | -0.0071478 | -0.014121 | 0.0073336 | 0.057542 | -0.0075729 | 0.066556 | -61.0474 | 62.146 | -61.2762 | -61.1114 | 61.8027 | 0 | -0.19684 | 0.14191 | 62.0682 | -61.2396 | -0.37994 | 0.11902 | -0.15106 | -0.21515 | -0.22431 | -0.34332 | 0.041198 | 0.22888 | 60.6995 | 61.0382 | 122.699 | 123.0423 | -0.15106 | 122.9645 | 60.8963 | -0.34332 | 123.0423 | -0.15106 | 60.8963 | 122.699 | 122.9645 | -123.3032 | -123.2666
3118.7656 | 123.1796 | -60.9283 | 62.027 | 0.26299 | -0.0050116 | -0.0092071 | 0.00712 | 0.059037 | -0.0043685 | 0.063993 | -61.1847 | 62.1414 | -61.2854 | -61.1206 | 61.7889 | -0.041199 | -0.14648 | 0.10529 | 62.1002 | -61.235 | -0.35706 | 0.11444 | -0.25635 | -0.19226 | -0.23804 | -0.3067 | 0.073242 | 0.10071 | 60.7819 | 61.0336 | 122.7173 | 123.0698 | -0.25635 | 123.0286 | 60.8871 | -0.3067 | 123.0698 | -0.25635 | 60.8871 | 122.7173 | 123.0286 | -123.3124 | -123.262
3119.7656 | 123.2666 | -60.9055 | 61.9904 | 0.27061 | -0.0052252 | -0.0072845 | 0.0045566 | 0.062241 | -0.0086411 | 0.068479 | -61.0153 | 62.146 | -61.2534 | -61.084 | 61.853 | 0.022888 | -0.21515 | 0.16937 | 62.0682 | -61.2122 | -0.3479 | 0.15564 | -0.10986 | -0.17853 | -0.13733 | -0.3067 | 0.07782 | 0.23804 | 60.6903 | 61.0748 | 122.7585 | 123.0515 | -0.10986 | 122.9736 | 60.9283 | -0.3067 | 123.0515 | -0.10986 | 60.9283 | 122.7585 | 122.9736 | -123.2437 | -123.2025
3120.7656 | 123.1522 | -60.9283 | 62.0682 | 0.25536 | -0.0052252 | -0.011557 | 0.0066928 | 0.059891 | -0.0047957 | 0.065916 | -61.0565 | 62.2009 | -61.2671 | -61.1893 | 61.7615 | -0.073242 | -0.082397 | 0.064087 | 62.1231 | -61.2625 | -0.33875 | 0.13275 | -0.12817 | -0.26093 | -0.3067 | -0.33417 | 0.054932 | 0.21057 | 60.8459 | 60.9924 | 122.6898 | 123.1293 | -0.12817 | 123.0515 | 60.8551 | -0.33417 | 123.1293 | -0.12817 | 60.8551 | 122.6898 | 123.0515 | -123.3353 | -123.3307
3121.7656 | 123.1293 | -60.9283 | 62.027 | 0.19432 | -0.0037298 | -0.014548 | 0.0073336 | 0.060319 | -0.0050095 | 0.065916 | -61.0703 | 62.2467 | -61.2488 | -61.1893 | 61.7569 | -0.068665 | -0.073242 | 0.07782 | 62.1048 | -61.2579 | -0.32043 | 0.21973 | -0.14191 | -0.26093 | -0.27008 | -0.32959 | 0.077819 | 0.17853 | 60.8551 | 61.0062 | 122.6852 | 123.175 | -0.14191 | 123.0331 | 60.8597 | -0.32959 | 123.175 | -0.14191 | 60.8597 | 122.6852 | 123.0331 | -123.2758 | -123.2849
3122.7656 | 123.2437 | -60.8688 | 62.0132 | 0.18669 | -0.0069342 | -0.0096343 | 0.0011386 | 0.060319 | -0.0045821 | 0.067197 | -61.0062 | 62.1231 | -61.2396 | -61.0703 | 61.7523 | -0.073242 | -0.20599 | 0.22888 | 62.0728 | -61.203 | -0.37079 | 0.10986 | -0.13733 | -0.20142 | -0.26093 | -0.33417 | 0.059509 | 0.23346 | 60.6628 | 61.0977 | 122.6212 | 122.9919 | -0.13733 | 122.9416 | 60.7956 | -0.33417 | 122.9919 | -0.13733 | 60.7956 | 122.6212 | 122.9416 | -123.2529 | -123.2162
3123.7656 | 123.2574 | -60.9329 | 62.0087 | 0.22484 | -0.0069342 | -0.0092071 | 0.0013522 | 0.059891 | -0.0062911 | 0.06677 | -61.0107 | 62.146 | -61.2305 | -61.0977 | 61.8484 | 0.032043 | -0.20599 | 0.18768 | 62.0544 | -61.203 | -0.29755 | 0.13733 | -0.07782 | -0.1648 | -0.16022 | -0.27008 | 0.045776 | 0.21973 | 60.7269 | 61.1206 | 122.7814 | 123.0789 | -0.07782 | 122.9874 | 60.965 | -0.27008 | 123.0789 | -0.07782 | 60.965 | 122.7814 | 122.9874 | -123.2391 | -123.2117
3124.7656 | 123.1384 | -60.9283 | 62.0407 | 0.20958 | -0.0056524 | -0.013052 | 0.0064792 | 0.06096 | -0.0037277 | 0.06677 | -61.0703 | 62.2055 | -61.2625 | -61.1893 | 61.7477 | -0.07782 | -0.086975 | 0.054932 | 62.0911 | -61.2442 | -0.33417 | 0.1648 | -0.14191 | -0.26093 | -0.29297 | -0.31586 | 0.050354 | 0.19226 | 60.8414 | 60.9833 | 122.6761 | 123.1338 | -0.14191 | 123.0194 | 60.8505 | -0.31586 | 123.1338 | -0.14191 | 60.8505 | 122.6761 | 123.0194 | -123.3032 | -123.2849
3125.7656 | 123.1842 | -60.9329 | 62.0453 | 0.84282 | -0.006507 | -0.012198 | 0.0028476 | 0.059891 | -0.0052231 | 0.064634 | -60.9283 | 62.1872 | -61.2717 | -61.1664 | 61.7889 | -0.036621 | -0.10986 | 0.11444 | 62.1185 | -61.2213 | -0.33875 | 0.14191 | 0.004577 | -0.23346 | -0.25635 | -0.28839 | 0.073242 | 0.34332 | 60.8231 | 61.0474 | 122.7219 | 123.1201 | 0.004577 | 123.0515 | 60.8963 | -0.28839 | 123.1201 | 0.004577 | 60.8963 | 122.7219 | 123.0515 | -123.317 | -123.2666
3126.7656 | 123.1476 | -60.9329 | 62.0544 | 0.27824 | -0.004798 | -0.011343 | 0.0056246 | 0.064164 | -0.0033005 | 0.067411 | -61.0611 | 62.2192 | -61.2762 | -61.0611 | 61.9537 | -0.013733 | -0.027466 | 0.13275 | 62.114 | -61.2625 | -0.34332 | 0.16479 | -0.12817 | -0.12817 | -0.10071 | -0.32959 | 0.05951 | 0.21515 | 60.9055 | 61.0657 | 122.8867 | 123.1522 | -0.12817 | 123.0469 | 60.9192 | -0.32959 | 123.1522 | -0.12817 | 60.9192 | 122.8867 | 123.0469 | -123.3307 | -123.317
3127.7656 | 123.0652 | -60.9329 | 62.0132 | 0.19432 | -0.003089 | -0.010062 | 0.0039156 | 0.062669 | -0.0069321 | 0.06677 | -61.084 | 62.2055 | -61.2808 | -61.1801 | 61.7569 | -0.068665 | -0.082397 | 0.07782 | 62.1094 | -61.2854 | -0.3479 | 0.19226 | -0.15106 | -0.24719 | -0.25635 | -0.35248 | 0.09613 | 0.19684 | 60.8505 | 61.0107 | 122.6898 | 123.1384 | -0.15106 | 123.0423 | 60.8643 | -0.35248 | 123.1384 | -0.15106 | 60.8643 | 122.6898 | 123.0423 | -123.2941 | -123.2986
3128.7656 | 123.1155 | -60.9421 | 62.0682 | 0.19432 | -0.0011664 | -0.012412 | 0.0060518 | 0.060532 | -0.0041549 | 0.065061 | -61.0703 | 62.2238 | -61.2625 | -61.203 | 61.7432 | -0.073242 | -0.041199 | 0.073242 | 62.1414 | -61.2534 | -0.32043 | 0.15564 | -0.12817 | -0.26093 | -0.32501 | -0.31128 | 0.073242 | 0.19226 | 60.9009 | 61.0153 | 122.6852 | 123.1659 | -0.12817 | 123.0835 | 60.8688 | -0.31128 | 123.1659 | -0.12817 | 60.8688 | 122.6852 | 123.0835 | -123.3307 | -123.3215
3129.7656 | 123.23 | -60.8871 | 62.027 | 0.25536 | -0.007575 | -0.014121 | 0.0015658 | 0.062241 | -0.0056503 | 0.066556 | -60.9924 | 62.146 | -61.2717 | -61.0931 | 61.8713 | 0.032043 | -0.23346 | 0.18768 | 62.059 | -61.2122 | -0.38452 | 0.11902 | -0.10529 | -0.20599 | -0.15564 | -0.32501 | 0.032043 | 0.27923 | 60.6537 | 61.0748 | 122.7585 | 123.0331 | -0.10529 | 122.9462 | 60.9192 | -0.32501 | 123.0331 | -0.10529 | 60.9192 | 122.7585 | 122.9462 | -123.2986 | -123.2391
3130.7656 | 123.2346 | -60.9055 | 61.9995 | 0.27824 | -0.008216 | -0.0085663 | 0.0028476 | 0.059678 | -0.0054367 | 0.06677 | -61.0062 | 62.1552 | -61.2488 | -61.0977 | 61.8439 | 0.009155 | -0.22888 | 0.18768 | 62.0499 | -61.2579 | -0.34332 | 0.15564 | -0.10071 | -0.19226 | -0.15564 | -0.35248 | 0.050354 | 0.24261 | 60.6766 | 61.0931 | 122.7493 | 123.0606 | -0.10071 | 122.9553 | 60.9146 | -0.35248 | 123.0606 | -0.10071 | 60.9146 | 122.7493 | 122.9553 | -123.2483 | -123.2574
3131.7656 | 123.1155 | -60.9375 | 62.0773 | 0.21721 | -0.0043708 | -0.013266 | 0.004343 | 0.063737 | -0.0035141 | 0.070188 | -61.0794 | 62.2101 | -61.2579 | -61.3312 | 61.4822 | -0.22888 | 0.11902 | 0.07782 | 62.1323 | -61.2579 | -0.32044 | 0.13275 | -0.14191 | -0.39368 | -0.59509 | -0.32044 | 0.054931 | 0.17853 | 61.0565 | 61.0153 | 122.4197 | 123.1476 | -0.14191 | 123.0698 | 60.7086 | -0.32044 | 123.1476 | -0.14191 | 60.7086 | 122.4197 | 123.0698 | -123.3353 | -123.3353
3132.7656 | 123.1064 | -60.9238 | 62.0544 | 0.095139 | -0.0022346 | -0.013907 | 0.0058382 | 0.062028 | -0.0035141 | 0.06677 | -61.0474 | 62.2375 | -61.2671 | -61.1984 | 61.7294 | -0.073242 | -0.022888 | 0.068665 | 62.1552 | -61.2717 | -0.34332 | 0.18311 | -0.1236 | -0.27466 | -0.32501 | -0.3479 | 0.10071 | 0.21973 | 60.9009 | 60.9924 | 122.6532 | 123.1613 | -0.1236 | 123.0789 | 60.8505 | -0.3479 | 123.1613 | -0.1236 | 60.8505 | 122.6532 | 123.0789 | -123.3215 | -123.3261
3133.7656 | 123.1247 | -60.9283 | 62.0316 | 0.20958 | -0.0020208 | -0.011771 | 0.0056246 | 0.061387 | -0.0039413 | 0.065702 | -61.0794 | 62.2101 | -61.2762 | -61.2076 | 61.7569 | -0.086975 | -0.036621 | 0.059509 | 62.114 | -61.2762 | -0.3479 | 0.17853 | -0.15106 | -0.27924 | -0.27466 | -0.3479 | 0.082398 | 0.19684 | 60.8917 | 60.9879 | 122.6852 | 123.1384 | -0.15106 | 123.0423 | 60.8414 | -0.3479 | 123.1384 | -0.15106 | 60.8414 | 122.6852 | 123.0423 | -123.3078 | -123.3078
3134.7656 | 123.1293 | -60.9375 | 62.0773 | 0.20958 | -0.0054388 | -0.010489 | 0.0032748 | 0.061387 | -0.0047957 | 0.065275 | -61.084 | 62.2513 | -61.2671 | -61.2076 | 61.7477 | -0.086975 | -0.036621 | 0.068665 | 62.1506 | -61.2579 | -0.32959 | 0.17395 | -0.14648 | -0.27008 | -0.32959 | -0.32044 | 0.073242 | 0.18311 | 60.9009 | 61.0062 | 122.6852 | 123.1888 | -0.14648 | 123.0881 | 60.8505 | -0.32044 | 123.1888 | -0.14648 | 60.8505 | 122.6852 | 123.0881 | -123.3444 | -123.3353
3135.7656 | 123.1155 | -60.9283 | 62.0728 | 0.10277 | -0.0067206 | -0.0092071 | 0.0045566 | 0.063309 | -0.0062911 | 0.066556 | -61.1023 | 62.2467 | -61.2991 | -61.2305 | 61.734 | -0.064087 | -0.059509 | 0.07782 | 62.1323 | -61.2579 | -0.37079 | 0.17395 | -0.17395 | -0.30212 | -0.33875 | -0.32959 | 0.059509 | 0.19684 | 60.8688 | 61.0062 | 122.6624 | 123.175 | -0.17395 | 123.0606 | 60.8643 | -0.32959 | 123.175 | -0.17395 | 60.8643 | 122.6624 | 123.0606 | -123.3719 | -123.3307
3136.7656 | 123.2529 | -60.8826 | 62.0041 | 0.20195 | -0.0073614 | -0.0089935 | 0.0034884 | 0.061814 | -0.0043685 | 0.06677 | -61.0245 | 62.1735 | -61.2488 | -61.1252 | 61.8393 | 0.013733 | -0.2243 | 0.1831 | 62.0956 | -61.2167 | -0.36621 | 0.16937 | -0.14191 | -0.24262 | -0.16479 | -0.33417 | 0.091553 | 0.2243 | 60.6583 | 61.0657 | 122.7219 | 123.056 | -0.14191 | 122.9782 | 60.8963 | -0.33417 | 123.056 | -0.14191 | 60.8963 | 122.7219 | 122.9782 | -123.2529 | -123.2208
3137.7656 | 123.2208 | -60.9146 | 62.0361 | 0.24773 | -0.0052252 | -0.01113 | 0.0022066 | 0.062455 | -0.0073593 | 0.067197 | -61.0245 | 62.1918 | -61.2671 | -61.1343 | 61.7889 | -0.045776 | -0.1831 | 0.15564 | 62.0728 | -61.2488 | -0.35248 | 0.15564 | -0.10986 | -0.21973 | -0.24719 | -0.33417 | 0.036621 | 0.24262 | 60.7315 | 61.0703 | 122.7036 | 123.1064 | -0.10986 | 122.9874 | 60.8688 | -0.33417 | 123.1064 | -0.10986 | 60.8688 | 122.7036 | 122.9874 | -123.3032 | -123.2849
3138.7656 | 123.1201 | -60.9375 | 62.0819 | 0.14092 | -0.0041572 | -0.010916 | 0.0056246 | 0.061387 | -0.0058639 | 0.067838 | -61.0611 | 62.2284 | -61.2442 | -61.203 | 61.7523 | -0.068665 | -0.009155 | 0.07782 | 62.1552 | -61.2808 | -0.3067 | 0.14648 | -0.1236 | -0.2655 | -0.32959 | -0.34332 | 0.073242 | 0.18311 | 60.9283 | 61.0153 | 122.6898 | 123.1659 | -0.1236 | 123.0927 | 60.8688 | -0.34332 | 123.1659 | -0.1236 | 60.8688 | 122.6898 | 123.0927 | -123.3261 | -123.3627
3139.7656 | 123.1384 | -60.9467 | 62.0773 | 0.19432 | -0.0062934 | -0.0083527 | 0.0066928 | 0.060532 | -0.0039413 | 0.067624 | -61.0748 | 62.2467 | -61.2717 | -61.2076 | 61.7432 | -0.073242 | -0.036621 | 0.073242 | 62.1277 | -61.2762 | -0.32501 | 0.16937 | -0.12817 | -0.26093 | -0.33417 | -0.32959 | 0.050354 | 0.19684 | 60.91 | 61.0199 | 122.6898 | 123.1934 | -0.12817 | 123.0743 | 60.8734 | -0.32959 | 123.1934 | -0.12817 | 60.8734 | 122.6898 | 123.0743 | -123.349 | -123.3536
3140.7656 | 123.0927 | -60.9238 | 62.0544 | 0.15617 | -0.0069342 | -0.014761 | 0.0047702 | 0.0616 | -0.0050095 | 0.065916 | -61.0794 | 62.233 | -61.2717 | -61.2167 | 61.7294 | -0.07782 | -0.036621 | 0.082397 | 62.1689 | -61.2717 | -0.3479 | 0.17853 | -0.15564 | -0.29297 | -0.32501 | -0.3479 | 0.11444 | 0.19226 | 60.8871 | 61.0062 | 122.6532 | 123.1567 | -0.15564 | 123.0927 | 60.8459 | -0.3479 | 123.1567 | -0.15564 | 60.8459 | 122.6532 | 123.0927 | -123.3261 | -123.3261
3141.7656 | 123.1201 | -60.9467 | 62.0911 | 0.1104 | -0.0054388 | -0.01113 | 0.0047702 | 0.060532 | -0.0058639 | 0.066343 | -61.0748 | 62.2101 | -61.2717 | -61.2167 | 61.7432 | -0.09613 | -0.032043 | 0.068665 | 62.1414 | -61.29 | -0.32501 | 0.11902 | -0.12817 | -0.27008 | -0.3479 | -0.34332 | 0.050354 | 0.19684 | 60.9146 | 61.0153 | 122.6898 | 123.1567 | -0.12817 | 123.0881 | 60.8505 | -0.34332 | 123.1567 | -0.12817 | 60.8505 | 122.6898 | 123.0881 | -123.3627 | -123.381
3142.7656 | 123.111 | -60.9467 | 62.0773 | 0.087509 | -0.0037298 | -0.0092071 | 0.003702 | 0.062455 | -0.0060775 | 0.066343 | -61.0657 | 62.2559 | -61.2625 | -61.2122 | 61.7477 | -0.064087 | -0.018311 | 0.068665 | 62.1918 | -61.2808 | -0.31586 | 0.17853 | -0.11902 | -0.2655 | -0.32959 | -0.33417 | 0.11444 | 0.19684 | 60.9283 | 61.0153 | 122.6944 | 123.2025 | -0.11902 | 123.1384 | 60.8826 | -0.33417 | 123.2025 | -0.11902 | 60.8826 | 122.6944 | 123.1384 | -123.3398 | -123.3582
3143.7656 | 123.2208 | -60.9192 | 62.0499 | 0.23247 | -0.0062934 | -0.0092071 | 0.0034884 | 0.063737 | -0.0037277 | 0.066129 | -61.0519 | 62.2055 | -61.2762 | -61.1664 | 61.7981 | -0.032043 | -0.15564 | 0.1236 | 62.114 | -61.2579 | -0.35706 | 0.15564 | -0.13275 | -0.24719 | -0.25177 | -0.33875 | 0.064087 | 0.2243 | 60.7635 | 61.0428 | 122.7173 | 123.1247 | -0.13275 | 123.0331 | 60.8871 | -0.33875 | 123.1247 | -0.13275 | 60.8871 | 122.7173 | 123.0331 | -123.3261 | -123.3078
3144.7656 | 123.1476 | -60.9375 | 62.0865 | 0.07988 | -0.0035162 | -0.011984 | 0.0039156 | 0.061173 | -0.0039413 | 0.067197 | -61.0428 | 62.2375 | -61.2579 | -61.1847 | 61.7615 | -0.027466 | -0.009155 | 0.12817 | 62.1414 | -61.2625 | -0.32044 | 0.15106 | -0.10529 | -0.24719 | -0.32501 | -0.32501 | 0.054931 | 0.21515 | 60.9283 | 61.0657 | 122.699 | 123.175 | -0.10529 | 123.0789 | 60.91 | -0.32501 | 123.175 | -0.10529 | 60.91 | 122.699 | 123.0789 | -123.3444 | -123.349
3145.7656 | 123.143 | -60.9009 | 62.0773 | 0.034104 | -0.0052252 | -0.0092071 | 0.0060518 | 0.060105 | -0.0054367 | 0.06677 | -61.0291 | 62.2284 | -61.235 | -61.1664 | 61.7752 | -0.009155 | -0.022888 | 0.14191 | 62.1643 | -61.2808 | -0.33417 | 0.15106 | -0.12817 | -0.2655 | -0.30212 | -0.37994 | 0.086975 | 0.20599 | 60.878 | 61.0428 | 122.6761 | 123.1293 | -0.12817 | 123.0652 | 60.8917 | -0.37994 | 123.1293 | -0.12817 | 60.8917 | 122.6761 | 123.0652 | -123.3124 | -123.3582
3146.7656 | 123.1155 | -60.9558 | 62.059 | 0.10277 | -0.0056524 | -0.0089935 | 0.004343 | 0.06096 | -0.0062911 | 0.066129 | -61.0565 | 62.2375 | -61.2579 | -61.1984 | 61.7477 | -0.073242 | -0.032043 | 0.091553 | 62.1552 | -61.2717 | -0.30212 | 0.17853 | -0.10071 | -0.24261 | -0.31128 | -0.31586 | 0.09613 | 0.20142 | 60.9238 | 61.0474 | 122.7036 | 123.1934 | -0.10071 | 123.111 | 60.8826 | -0.31586 | 123.1934 | -0.10071 | 60.8826 | 122.7036 | 123.111 | -123.317 | -123.3307
3147.7656 | 123.1384 | -60.9283 | 62.0636 | 0.12566 | -0.0043708 | -0.011557 | 0.0058382 | 0.0616 | -0.0045821 | 0.065488 | -61.0565 | 62.2421 | -61.2991 | -61.1938 | 61.7615 | -0.036621 | -0.022888 | 0.11902 | 62.1735 | -61.2854 | -0.37079 | 0.17853 | -0.12817 | -0.2655 | -0.30212 | -0.35706 | 0.10986 | 0.24261 | 60.9055 | 61.0474 | 122.6898 | 123.1705 | -0.12817 | 123.1018 | 60.8917 | -0.35706 | 123.1705 | -0.12817 | 60.8917 | 122.6898 | 123.1018 | -123.3627 | -123.349
3148.7812 | 123.1934 | -60.91 | 62.0407 | 0.11803 | -0.0086432 | -0.020316 | -0.003134 | 0.05861 | -0.0065047 | 0.067838 | -60.9512 | 62.1414 | -61.235 | -61.171 | 61.8393 | 0.009155 | -0.1236 | 0.17853 | 62.1552 | -61.2305 | -0.32501 | 0.10071 | -0.041199 | -0.26093 | -0.20142 | -0.32043 | 0.11444 | 0.28381 | 60.7864 | 61.0886 | 122.7493 | 123.0515 | -0.041199 | 123.0652 | 60.9192 | -0.32043 | 123.0515 | -0.041199 | 60.9192 | 122.7493 | 123.0652 | -123.2758 | -123.2712
3149.7656 | 123.1064 | -60.9467 | 62.0636 | 0.095139 | -0.0052252 | -0.0098479 | 0.0062656 | 0.06096 | -0.0047957 | 0.065488 | -61.0153 | 62.2375 | -61.2305 | -61.1801 | 61.7661 | -0.018311 | -0.013733 | 0.13275 | 62.1597 | -61.2579 | -0.28381 | 0.17395 | -0.068665 | -0.23346 | -0.29755 | -0.31128 | 0.09613 | 0.21515 | 60.9329 | 61.0794 | 122.7127 | 123.1842 | -0.068665 | 123.1064 | 60.9283 | -0.31128 | 123.1842 | -0.068665 | 60.9283 | 122.7127 | 123.1064 | -123.2941 | -123.3215
3150.7656 | 123.1293 | -60.9421 | 62.059 | 0.20958 | -0.0050116 | -0.012412 | 0.0024202 | 0.064164 | -0.0054367 | 0.066984 | -61.0611 | 62.2147 | -61.2442 | -61.203 | 61.7523 | -0.07782 | -0.086975 | 0.086975 | 62.178 | -61.2625 | -0.30212 | 0.15564 | -0.11902 | -0.26093 | -0.3067 | -0.32043 | 0.11902 | 0.18311 | 60.8551 | 61.0291 | 122.6944 | 123.1567 | -0.11902 | 123.1201 | 60.8643 | -0.32043 | 123.1567 | -0.11902 | 60.8643 | 122.6944 | 123.1201 | -123.3032 | -123.3215
3151.7656 | 123.1384 | -60.9283 | 62.0453 | 0.011215 | -0.0052252 | -0.010703 | 0.0047702 | 0.06096 | -0.0050095 | 0.066129 | -61.0016 | 62.2375 | -61.2305 | -61.1526 | 61.8073 | 0.018311 | -0.027466 | 0.1831 | 62.1597 | -61.2762 | -0.30212 | 0.19226 | -0.073242 | -0.2243 | -0.23804 | -0.3479 | 0.11444 | 0.22888 | 60.9009 | 61.1114 | 122.7356 | 123.1659 | -0.073242 | 123.0881 | 60.9467 | -0.3479 | 123.1659 | -0.073242 | 60.9467 | 122.7356 | 123.0881 | -123.2758 | -123.3215
3152.7656 | 123.1796 | -60.91 | 62.0911 | -0.20241 | -0.0045844 | -0.010062 | 0.0056246 | 0.062669 | -0.0067185 | 0.06442 | -60.997 | 62.2513 | -61.2488 | -61.1343 | 61.8118 | 0.009155 | -0.013733 | 0.20142 | 62.1643 | -61.2305 | -0.33874 | 0.16022 | -0.086975 | -0.2243 | -0.27923 | -0.32043 | 0.073243 | 0.25177 | 60.8963 | 61.1115 | 122.7219 | 123.1613 | -0.086975 | 123.0743 | 60.9192 | -0.32043 | 123.1613 | -0.086975 | 60.9192 | 122.7219 | 123.0743 | -123.3398 | -123.3215
3153.7812 | 123.2025 | -60.9009 | 62.0224 | 0.28587 | -0.007575 | -0.012198 | 0.0013522 | 0.0616 | -0.0050095 | 0.066556 | -61.0245 | 62.1002 | -61.2671 | -61.116 | 61.8347 | 0.013733 | -0.23804 | 0.17853 | 62.1277 | -61.1801 | -0.36621 | 0.07782 | -0.1236 | -0.21515 | -0.18768 | -0.27924 | 0.10529 | 0.24262 | 60.6628 | 61.0794 | 122.7356 | 123.0011 | -0.1236 | 123.0286 | 60.9146 | -0.27924 | 123.0011 | -0.1236 | 60.9146 | 122.7356 | 123.0286 | -123.2895 | -123.2025
3154.7656 | 123.143 | -60.9283 | 62.0773 | 0.011215 | -0.0045844 | -0.012412 | 0.0047702 | 0.063523 | -0.0039413 | 0.067411 | -60.9924 | 62.2284 | -61.2534 | -61.1618 | 61.7844 | -0.013733 | -0.045776 | 0.16022 | 62.1597 | -61.2671 | -0.32501 | 0.15106 | -0.064087 | -0.23346 | -0.29297 | -0.33875 | 0.082397 | 0.26093 | 60.8826 | 61.0886 | 122.7127 | 123.1567 | -0.064087 | 123.0881 | 60.9146 | -0.33875 | 123.1567 | -0.064087 | 60.9146 | 122.7127 | 123.0881 | -123.3307 | -123.3444
3155.7656 | 123.1659 | -60.8917 | 62.0682 | 0.056992 | -0.0067206 | -0.012839 | 0.0056246 | 0.063309 | -0.0041549 | 0.067197 | -60.997 | 62.2284 | -61.2442 | -61.1343 | 61.8073 | 0.004578 | -0.045776 | 0.19226 | 62.1414 | -61.29 | -0.35248 | 0.16022 | -0.10528 | -0.24261 | -0.26093 | -0.39825 | 0.073242 | 0.24719 | 60.8459 | 61.084 | 122.699 | 123.1201 | -0.10528 | 123.0331 | 60.8963 | -0.39825 | 123.1201 | -0.10528 | 60.8963 | 122.699 | 123.0331 | -123.3124 | -123.3582
3156.7656 | 123.1293 | -60.9421 | 62.0682 | 0.20195 | 0.002038 | -0.0077117 | 0.003702 | 0.064378 | -0.0075729 | 0.068693 | -61.3907 | 62.1689 | -61.2579 | -61.171 | 61.7615 | -0.068665 | -0.036621 | 0.054932 | 62.1552 | -61.2717 | -0.31586 | 0.10071 | -0.44861 | -0.22888 | -0.3067 | -0.32959 | 0.086975 | -0.13275 | 60.9055 | 60.997 | 122.7036 | 123.111 | -0.44861 | 123.0972 | 60.8734 | -0.32959 | 123.111 | -0.44861 | 60.8734 | 122.7036 | 123.0972 | -123.3261 | -123.3398
3157.7656 | 123.1384 | -60.9467 | 62.059 | 0.14092 | -0.0060798 | -0.011771 | 0.003702 | 0.062669 | -0.0080001 | 0.067624 | -61.0794 | 62.2284 | -61.2808 | -61.2259 | 61.7249 | -0.068665 | -0.26093 | -0.28839 | 62.1414 | -61.3037 | -0.33417 | 0.16937 | -0.13275 | -0.27924 | -0.33417 | -0.35706 | 0.082397 | 0.20142 | 60.6857 | 60.6583 | 122.6715 | 123.175 | -0.13275 | 123.0881 | 60.878 | -0.35706 | 123.175 | -0.13275 | 60.878 | 122.6715 | 123.0881 | -123.3398 | -123.3627
3158.7812 | 123.2071 | -60.9009 | 62.0361 | 0.21721 | -0.007575 | -0.014975 | 0.001993 | 0.060746 | -0.0041549 | 0.066129 | -61.0611 | 62.1964 | -61.2717 | -61.1618 | 61.7935 | -0.041199 | -0.18768 | 0.13733 | 62.1231 | -61.2534 | -0.37079 | 0.16022 | -0.16022 | -0.26092 | -0.24262 | -0.35248 | 0.086975 | 0.21057 | 60.7132 | 61.0382 | 122.6944 | 123.0972 | -0.16022 | 123.024 | 60.8597 | -0.35248 | 123.0972 | -0.16022 | 60.8597 | 122.6944 | 123.024 | -123.3078 | -123.2895
3159.7656 | 123.1705 | -60.9009 | 62.0819 | -0.12611 | -0.0050116 | -0.0074981 | 0.004343 | 0.060746 | -0.0069321 | 0.064847 | -61.0291 | 62.265 | -61.2534 | -61.1206 | 61.8301 | 0.045776 | 0.022888 | 0.2243 | 62.1918 | -61.2671 | -0.35248 | 0.18311 | -0.12817 | -0.21973 | -0.25177 | -0.36621 | 0.10986 | 0.2243 | 60.9238 | 61.1252 | 122.731 | 123.1659 | -0.12817 | 123.0927 | 60.9467 | -0.36621 | 123.1659 | -0.12817 | 60.9467 | 122.731 | 123.0927 | -123.3353 | -123.349
3160.7656 | 123.2391 | -60.9146 | 62.0407 | -0.057449 | -0.0056524 | -0.0092071 | 0.0039156 | 0.06395 | -0.0071457 | 0.065702 | -61.0016 | 62.2284 | -61.2442 | -61.1114 | 61.8256 | 0.045776 | -0.009155 | 0.23346 | 62.1826 | -61.235 | -0.32959 | 0.18768 | -0.086975 | -0.19684 | -0.21515 | -0.32043 | 0.14191 | 0.24262 | 60.9055 | 61.1481 | 122.7402 | 123.143 | -0.086975 | 123.0972 | 60.9604 | -0.32043 | 123.143 | -0.086975 | 60.9604 | 122.7402 | 123.0972 | -123.2849 | -123.2758
3161.7656 | 123.1522 | -60.9146 | 62.0773 | -0.11085 | -0.0086432 | -0.010703 | 0.0047702 | 0.058823 | -0.0045821 | 0.065488 | -61.0062 | 62.2467 | -61.2762 | -61.1435 | 61.8256 | 0.045776 | 0.009155 | 0.24719 | 62.1643 | -61.2534 | -0.36163 | 0.16937 | -0.091553 | -0.22888 | -0.25177 | -0.33875 | 0.086975 | 0.27008 | 60.9238 | 61.1618 | 122.7402 | 123.1613 | -0.091553 | 123.0789 | 60.9604 | -0.33875 | 123.1613 | -0.091553 | 60.9604 | 122.7402 | 123.0789 | -123.3536 | -123.3307
3162.7656 | 123.1522 | -60.9283 | 62.0636 | -0.149 | -0.0077888 | -0.011343 | 0.003702 | 0.060105 | -0.0062911 | 0.065488 | -61.0428 | 62.2421 | -61.235 | -61.1298 | 61.8027 | 0.045776 | 0.036621 | 0.21057 | 62.2009 | -61.2396 | -0.3067 | 0.17853 | -0.11444 | -0.20142 | -0.26093 | -0.31128 | 0.13733 | 0.19226 | 60.965 | 61.1389 | 122.731 | 123.1705 | -0.11444 | 123.1293 | 60.9741 | -0.31128 | 123.1705 | -0.11444 | 60.9741 | 122.731 | 123.1293 | -123.2986 | -123.3032
3163.7656 | 123.2346 | -60.8643 | 62.0224 | 0.034104 | -0.0088568 | -0.017111 | -0.0029202 | 0.059891 | -0.0050095 | 0.06677 | -61.0245 | 62.1826 | -61.2167 | -61.1023 | 61.8805 | 0.082397 | -0.12817 | 0.27008 | 62.1368 | -61.2167 | -0.35248 | 0.16022 | -0.16022 | -0.23804 | -0.14191 | -0.35248 | 0.11444 | 0.19226 | 60.7361 | 61.1343 | 122.7448 | 123.0469 | -0.16022 | 123.0011 | 60.9467 | -0.35248 | 123.0469 | -0.16022 | 60.9467 | 122.7448 | 123.0011 | -123.2391 | -123.2391
3164.7656 | 123.1842 | -60.8917 | 62.0453 | -0.011673 | -0.004798 | -0.012839 | 0.00712 | 0.060532 | -0.0065047 | 0.06677 | -60.9924 | 62.2101 | -61.2854 | -61.116 | 61.8027 | 0.022888 | -0.022888 | 0.19226 | 62.1735 | -61.2717 | -0.39368 | 0.16479 | -0.10071 | -0.2243 | -0.24262 | -0.37994 | 0.12817 | 0.29297 | 60.8688 | 61.084 | 122.6944 | 123.1018 | -0.10071 | 123.0652 | 60.9146 | -0.37994 | 123.1018 | -0.10071 | 60.9146 | 122.6944 | 123.0652 | -123.3307 | -123.317
3165.7656 | 123.1247 | -60.9329 | 62.0865 | -0.17189 | -0.008216 | -0.01348 | -0.00014316 | 0.061387 | -0.0050095 | 0.065061 | -61.0428 | 62.2147 | -61.2442 | -61.0703 | 62.0087 | 0.041199 | -0.018311 | 0.14648 | 62.2101 | -61.2717 | -0.31128 | 0.12817 | -0.10986 | -0.13733 | -0.07782 | -0.33875 | 0.1236 | 0.20142 | 60.9146 | 61.0794 | 122.9416 | 123.1476 | -0.10986 | 123.143 | 60.9741 | -0.33875 | 123.1476 | -0.10986 | 60.9741 | 122.9416 | 123.143 | -123.3307 | -123.3582
3166.7656 | 123.1384 | -60.9055 | 62.1323 | -0.15663 | -0.0062934 | -0.014334 | -0.00057036 | 0.059891 | -0.0077865 | 0.064207 | -61.0382 | 62.178 | -61.2259 | -61.1069 | 61.7981 | 0.009155 | 0.091553 | 0.22888 | 62.1918 | -61.2122 | -0.32043 | 0.045777 | -0.13275 | -0.20142 | -0.33417 | -0.3067 | 0.059509 | 0.18768 | 60.997 | 61.1343 | 122.7036 | 123.0835 | -0.13275 | 123.0972 | 60.9146 | -0.3067 | 123.0835 | -0.13275 | 60.9146 | 122.7036 | 123.0972 | -123.3582 | -123.3444
3167.7656 | 123.0881 | -60.8917 | 62.1002 | -0.17189 | -0.005866 | -0.01583 | 0.0022066 | 0.059251 | -0.0045821 | 0.065702 | -61.0565 | 62.2192 | -61.2625 | -61.1618 | 61.7935 | 0.009155 | 0.1831 | 0.42114 | 62.2284 | -61.1893 | -0.37079 | 0.11902 | -0.16479 | -0.27008 | -0.3067 | -0.29755 | 0.12817 | 0.20599 | 61.0748 | 61.3129 | 122.6852 | 123.111 | -0.16479 | 123.1201 | 60.9009 | -0.29755 | 123.111 | -0.16479 | 60.9009 | 122.6852 | 123.1201 | -123.3627 | -123.2895
3168.7656 | 123.1201 | -60.91 | 62.0956 | -0.17952 | -0.0077888 | -0.0089935 | -0.0012112 | 0.059464 | -0.0056503 | 0.065916 | -61.0519 | 62.1826 | -61.2076 | -61.1481 | 61.8256 | 0.036621 | 0.073242 | 0.2243 | 62.1918 | -61.235 | -0.29755 | 0.086975 | -0.14191 | -0.23804 | -0.27008 | -0.32501 | 0.09613 | 0.15564 | 60.9833 | 61.1343 | 122.7356 | 123.0927 | -0.14191 | 123.1018 | 60.9467 | -0.32501 | 123.0927 | -0.14191 | 60.9467 | 122.7356 | 123.1018 | -123.3032 | -123.3307
3169.7656 | 123.1842 | -60.9055 | 62.0956 | -0.18715 | -0.0094976 | -0.013052 | -0.0018522 | 0.057114 | -0.0047957 | 0.065916 | -61.0062 | 62.1368 | -61.2259 | -61.0931 | 61.8439 | 0.082397 | 0.004578 | 0.29755 | 62.1552 | -61.1984 | -0.32043 | 0.041199 | -0.10071 | -0.18768 | -0.25177 | -0.29297 | 0.059509 | 0.21973 | 60.91 | 61.203 | 122.7493 | 123.0423 | -0.10071 | 123.0606 | 60.9879 | -0.29297 | 123.0423 | -0.10071 | 60.9879 | 122.7493 | 123.0606 | -123.3215 | -123.2941
3170.7656 | 123.2208 | -60.8826 | 62.0544 | -0.15663 | -0.010566 | -0.011771 | -0.00057036 | 0.05861 | -0.0060775 | 0.065488 | -60.9924 | 62.1414 | -61.2122 | -61.0748 | 61.8759 | 0.10529 | -0.041199 | 0.31586 | 62.1552 | -61.1664 | -0.32959 | 0.086975 | -0.10986 | -0.19226 | -0.17853 | -0.28381 | 0.10071 | 0.21973 | 60.8414 | 61.1984 | 122.7585 | 123.024 | -0.10986 | 123.0377 | 60.9879 | -0.28381 | 123.024 | -0.10986 | 60.9879 | 122.7585 | 123.0377 | -123.2666 | -123.2208
3171.7656 | 123.2254 | -60.8597 | 62.0453 | 0.35454 | -0.010139 | -0.014548 | -0.00014316 | 0.058396 | -0.0073593 | 0.067838 | -61.0199 | 62.114 | -61.1984 | -61.0565 | 61.8896 | 0.10986 | -0.11444 | 0.32044 | 62.1368 | -61.1481 | -0.33875 | 0.068665 | -0.16022 | -0.19684 | -0.15564 | -0.28839 | 0.091553 | 0.17853 | 60.7452 | 61.1801 | 122.7493 | 122.9736 | -0.16022 | 122.9965 | 60.9695 | -0.28839 | 122.9736 | -0.16022 | 60.9695 | 122.7493 | 122.9965 | -123.2437 | -123.1934
3172.7656 | 123.2483 | -60.9009 | 62.0819 | -0.011673 | -0.011207 | -0.016257 | -0.0012112 | 0.055833 | -0.0065047 | 0.065702 | -61.0382 | 62.1323 | -61.2305 | -61.084 | 61.8668 | 0.073242 | -0.14191 | 0.28381 | 62.1002 | -61.1893 | -0.32959 | 0.050354 | -0.13733 | -0.1831 | -0.21515 | -0.28839 | 0.018311 | 0.19226 | 60.759 | 61.1847 | 122.7676 | 123.0331 | -0.13733 | 123.0011 | 60.9741 | -0.28839 | 123.0331 | -0.13733 | 60.9741 | 122.7676 | 123.0011 | -123.3124 | -123.2712
3173.7656 | 123.2574 | -60.8551 | 62.0453 | -0.026932 | -0.0094976 | -0.011343 | -0.00057036 | 0.057755 | -0.0056503 | 0.065488 | -61.0016 | 62.0911 | -61.2213 | -61.0382 | 61.8805 | 0.10071 | -0.13733 | 0.32959 | 62.146 | -61.1755 | -0.36621 | 0.045776 | -0.14648 | -0.1831 | -0.16479 | -0.32043 | 0.10071 | 0.21973 | 60.7178 | 61.1847 | 122.7356 | 122.9462 | -0.14648 | 123.0011 | 60.9558 | -0.32043 | 122.9462 | -0.14648 | 60.9558 | 122.7356 | 123.0011 | -123.2666 | -123.2208
3174.7656 | 123.2208 | -60.8871 | 62.0499 | -0.11848 | -0.010139 | -0.018607 | 0.0017794 | 0.057969 | -0.0050095 | 0.064847 | -60.9604 | 62.1002 | -61.2488 | -61.0382 | 61.9034 | 0.10986 | 0.15564 | 0.66376 | 62.2055 | -61.1298 | -0.36163 | 0.050354 | -0.073242 | -0.15106 | -0.14648 | -0.24262 | 0.15564 | 0.28839 | 61.0428 | 61.5509 | 122.7905 | 122.9874 | -0.073242 | 123.0927 | 60.997 | -0.24262 | 122.9874 | -0.073242 | 60.997 | 122.7905 | 123.0927 | -123.2986 | -123.1796
3175.7656 | 123.2483 | -60.8734 | 62.0407 | -0.057449 | -0.012061 | -0.01882 | -0.00099756 | 0.054978 | -0.0084273 | 0.062925 | -60.9879 | 62.1094 | -61.2213 | -61.0474 | 61.8896 | 0.10986 | -0.15106 | 0.32501 | 62.114 | -61.1755 | -0.3479 | 0.068665 | -0.11444 | -0.17395 | -0.15106 | -0.30212 | 0.073243 | 0.23346 | 60.7224 | 61.1984 | 122.7631 | 122.9828 | -0.11444 | 122.9874 | 60.9833 | -0.30212 | 122.9828 | -0.11444 | 60.9833 | 122.7631 | 122.9874 | -123.262 | -123.2162
3176.7656 | 123.2346 | -60.8551 | 62.059 | -0.019302 | -0.0097114 | -0.016257 | -0.00057036 | 0.055619 | -0.0065047 | 0.065488 | -61.0153 | 62.0956 | -61.235 | -61.084 | 61.8622 | 0.068665 | -0.14191 | 0.28381 | 62.1277 | -61.171 | -0.37994 | 0.036621 | -0.16022 | -0.22888 | -0.19684 | -0.31586 | 0.068665 | 0.21973 | 60.7132 | 61.1389 | 122.7173 | 122.9507 | -0.16022 | 122.9828 | 60.9238 | -0.31586 | 122.9507 | -0.16022 | 60.9238 | 122.7173 | 122.9828 | -123.2941 | -123.23
3177.7656 | 123.2025 | -60.8643 | 62.0682 | -0.13374 | -0.010352 | -0.014761 | 0.0017794 | 0.057755 | -0.0077865 | 0.067624 | -60.965 | 62.1048 | -61.203 | -61.0474 | 61.8805 | 0.07782 | -0.07782 | 0.32044 | 62.1643 | -61.1572 | -0.33875 | 0.036621 | -0.10071 | -0.1831 | -0.18768 | -0.29297 | 0.096131 | 0.23804 | 60.7864 | 61.1847 | 122.7448 | 122.9691 | -0.10071 | 123.0286 | 60.9421 | -0.29297 | 122.9691 | -0.10071 | 60.9421 | 122.7448 | 123.0286 | -123.2712 | -123.2254
3178.7656 | 123.2529 | -60.8734 | 62.0682 | 0.20958 | -0.0088568 | -0.01113 | 0.002634 | 0.057328 | -0.0065047 | 0.065916 | -61.0474 | 62.0911 | -61.2305 | -61.0245 | 61.8851 | 0.09613 | -0.10071 | 0.32501 | 62.1368 | -61.1526 | -0.35706 | 0.022888 | -0.17395 | -0.15106 | -0.1831 | -0.27924 | 0.068665 | 0.18311 | 60.7727 | 61.1984 | 122.7585 | 122.9645 | -0.17395 | 123.0103 | 60.9695 | -0.27924 | 122.9645 | -0.17395 | 60.9695 | 122.7585 | 123.0103 | -123.2986 | -123.2208
3179.7656 | 123.2071 | -60.9146 | 62.0819 | 0.11803 | -0.008216 | -0.017966 | 0.00028404 | 0.058182 | -0.0043685 | 0.06677 | -61.0657 | 62.0911 | -61.2625 | -61.1252 | 61.7798 | 0.12817 | -0.16022 | 0.15564 | 62.1506 | -61.1755 | -0.3479 | 0.009155 | -0.15106 | -0.21057 | -0.30212 | -0.26093 | 0.068665 | 0.19684 | 60.7544 | 61.0703 | 122.6944 | 123.0057 | -0.15106 | 123.0652 | 61.0428 | -0.26093 | 123.0057 | -0.15106 | 61.0428 | 122.6944 | 123.0652 | -123.3444 | -123.2574
3180.7656 | 123.1934 | -60.8917 | 62.0316 | 0.13329 | -0.0086432 | -0.011771 | -0.00014316 | 0.058396 | -0.0069321 | 0.063566 | -61.0657 | 62.0773 | -61.2534 | -61.1343 | 61.8256 | -0.018311 | -0.16937 | 0.16022 | 62.1002 | -61.1847 | -0.36163 | 0.045777 | -0.17395 | -0.24261 | -0.20599 | -0.29297 | 0.068665 | 0.18768 | 60.7224 | 61.0519 | 122.7173 | 122.9691 | -0.17395 | 122.9919 | 60.8734 | -0.29297 | 122.9691 | -0.17395 | 60.8734 | 122.7173 | 122.9919 | -123.2849 | -123.2162
3181.7656 | 123.2117 | -60.8734 | 62.0407 | 0.087509 | -0.0094976 | -0.013693 | 0.001993 | 0.056473 | -0.0065047 | 0.06442 | -61.0657 | 62.1002 | -61.2305 | -61.1252 | 61.8256 | -0.022888 | -0.14648 | 0.40741 | 62.1094 | -61.1984 | -0.35706 | 0.05951 | -0.19226 | -0.25177 | -0.21515 | -0.32501 | 0.068665 | 0.16479 | 60.7269 | 61.2808 | 122.699 | 122.9736 | -0.19226 | 122.9828 | 60.8505 | -0.32501 | 122.9736 | -0.19226 | 60.8505 | 122.699 | 122.9828 | -123.2712 | -123.2391
3182.7656 | 123.1796 | -60.8963 | 62.0224 | 0.15617 | -0.010139 | -0.020956 | 0.0017794 | 0.056046 | -0.0043685 | 0.06442 | -61.0519 | 62.1048 | -61.2442 | -61.1206 | 61.821 | -0.027466 | -0.17853 | 0.17853 | 62.0773 | -61.1847 | -0.3479 | 0.082397 | -0.15564 | -0.2243 | -0.20142 | -0.28839 | 0.054932 | 0.19226 | 60.7178 | 61.0748 | 122.7173 | 123.0011 | -0.15564 | 122.9736 | 60.8688 | -0.28839 | 123.0011 | -0.15564 | 60.8688 | 122.7173 | 122.9736 | -123.2666 | -123.2071
3183.7656 | 123.2025 | -60.878 | 62.0361 | 0.21721 | -0.0090704 | -0.016898 | 0.0015658 | 0.055405 | -0.0060775 | 0.065275 | -61.0382 | 62.0819 | -61.2671 | -61.1069 | 61.8118 | -0.013733 | -0.20142 | 0.16937 | 62.0636 | -61.1938 | -0.3891 | 0.045776 | -0.16022 | -0.22888 | -0.2243 | -0.31586 | 0.027466 | 0.22888 | 60.6766 | 61.0474 | 122.6898 | 122.9599 | -0.16022 | 122.9416 | 60.8643 | -0.31586 | 122.9599 | -0.16022 | 60.8643 | 122.6898 | 122.9416 | -123.3032 | -123.23
3184.7656 | 123.2391 | -60.878 | 62.0728 | 0.056992 | -0.0080024 | -0.016257 | 7.0444e-05 | 0.057542 | -0.0056503 | 0.064207 | -61.0748 | 62.1002 | -61.2213 | -61.0886 | 61.8713 | 0.032043 | -0.15106 | 0.25635 | 62.1048 | -61.203 | -0.34332 | 0.027466 | -0.19684 | -0.21057 | -0.20142 | -0.32501 | 0.032043 | 0.14648 | 60.7269 | 61.1343 | 122.7493 | 122.9782 | -0.19684 | 122.9828 | 60.91 | -0.32501 | 122.9782 | -0.19684 | 60.91 | 122.7493 | 122.9828 | -123.2941 | -123.2758
3185.7656 | 123.2208 | -60.8826 | 62.0728 | -0.17952 | -0.010779 | -0.012198 | 0.0013522 | 0.056687 | -0.0039413 | 0.067624 | -61.0474 | 62.1368 | -61.2488 | -61.1206 | 61.8439 | 0 | -0.12817 | 0.20599 | 62.1002 | -61.1984 | -0.36621 | 0.064087 | -0.16479 | -0.23804 | -0.22888 | -0.31586 | 0.027466 | 0.20142 | 60.7544 | 61.0886 | 122.7264 | 123.0194 | -0.16479 | 122.9828 | 60.8826 | -0.31586 | 123.0194 | -0.16479 | 60.8826 | 122.7264 | 122.9828 | -123.3215 | -123.2712
3186.7656 | 123.2437 | -60.8826 | 62.0316 | 0.25536 | -0.007575 | -0.0087799 | 0.0051974 | 0.060105 | -0.0077865 | 0.065916 | -60.9924 | 62.1185 | -61.235 | -60.9741 | 61.94 | 0.068665 | -0.25177 | 0.21973 | 62.0544 | -61.2076 | -0.35248 | 0.086975 | -0.10986 | -0.091553 | -0.091553 | -0.32501 | 0.022888 | 0.24261 | 60.6308 | 61.1023 | 122.8226 | 123.0011 | -0.10986 | 122.937 | 60.9512 | -0.32501 | 123.0011 | -0.10986 | 60.9512 | 122.8226 | 122.937 | -123.2666 | -123.2391
3187.7656 | 123.2437 | -60.878 | 62.0224 | 0.23247 | -0.010139 | -0.010062 | 0.0045566 | 0.057542 | -0.0065047 | 0.066129 | -61.0016 | 62.1094 | -61.2167 | -61.0886 | 61.853 | 0.004578 | -0.2655 | 0.17395 | 62.0865 | -61.2076 | -0.33874 | 0.086975 | -0.1236 | -0.21057 | -0.16937 | -0.32959 | 0.064087 | 0.21515 | 60.6125 | 61.0519 | 122.731 | 122.9874 | -0.1236 | 122.9645 | 60.8826 | -0.32959 | 122.9874 | -0.1236 | 60.8826 | 122.731 | 122.9645 | -123.2391 | -123.23
3188.7656 | 123.2483 | -60.9009 | 62.0132 | 0.30113 | -0.0060798 | -0.01113 | 0.0030612 | 0.061173 | -0.0047957 | 0.066556 | -60.9787 | 62.1048 | -61.2442 | -60.9833 | 61.9492 | 0.059509 | -0.26093 | 0.21973 | 62.0682 | -61.1664 | -0.34332 | 0.091552 | -0.07782 | -0.082397 | -0.064087 | -0.2655 | 0.054931 | 0.2655 | 60.64 | 61.1206 | 122.85 | 123.0057 | -0.07782 | 122.9691 | 60.9604 | -0.2655 | 123.0057 | -0.07782 | 60.9604 | 122.85 | 122.9691 | -123.2574 | -123.1796
3189.7656 | 123.2117 | -60.8826 | 62.0132 | 0.21721 | -0.0073614 | -0.010916 | 0.0041292 | 0.059678 | -0.0052231 | 0.064847 | -61.0062 | 62.1094 | -61.2396 | -61.0886 | 61.8622 | 0.004578 | -0.25635 | 0.16937 | 62.0682 | -61.1984 | -0.35706 | 0.09613 | -0.1236 | -0.20599 | -0.15106 | -0.31586 | 0.054931 | 0.23346 | 60.6262 | 61.0519 | 122.7448 | 122.9919 | -0.1236 | 122.9507 | 60.8871 | -0.31586 | 122.9919 | -0.1236 | 60.8871 | 122.7448 | 122.9507 | -123.2529 | -123.2117
3190.7656 | 123.2346 | -60.91 | 62.0316 | 0.24773 | -0.005866 | -0.012412 | 0.0060518 | 0.059678 | -0.0062911 | 0.065061 | -61.0245 | 62.1689 | -61.2488 | -61.0977 | 61.8439 | -0.013733 | -0.19226 | 0.15106 | 62.0728 | -61.2167 | -0.33874 | 0.13733 | -0.11444 | -0.18768 | -0.18768 | -0.3067 | 0.041199 | 0.2243 | 60.7178 | 61.0611 | 122.7539 | 123.0789 | -0.11444 | 122.9828 | 60.8963 | -0.3067 | 123.0789 | -0.11444 | 60.8963 | 122.7539 | 122.9828 | -123.2803 | -123.2483
3191.7656 | 123.1888 | -60.9009 | 62.0407 | 0.20195 | -0.0054388 | -0.01348 | 0.0024202 | 0.058182 | -0.0047957 | 0.065061 | -61.0336 | 62.1323 | -61.235 | -61.1206 | 61.8393 | 0.009155 | -0.22888 | 0.17853 | 62.0682 | -61.2122 | -0.33417 | 0.091553 | -0.13275 | -0.21973 | -0.20142 | -0.31128 | 0.027466 | 0.20142 | 60.672 | 61.0794 | 122.7402 | 123.0331 | -0.13275 | 122.9691 | 60.91 | -0.31128 | 123.0331 | -0.13275 | 60.91 | 122.7402 | 122.9691 | -123.2758 | -123.2529
3192.7656 | 123.2254 | -60.8917 | 62.027 | 0.21721 | -0.005866 | -0.0089935 | 0.002634 | 0.059037 | -0.0056503 | 0.067197 | -61.0199 | 62.1414 | -61.2305 | -61.0931 | 61.8439 | 0.004578 | -0.23804 | 0.17395 | 62.0773 | -61.2259 | -0.33874 | 0.11444 | -0.12817 | -0.20142 | -0.18311 | -0.33417 | 0.050354 | 0.21057 | 60.6537 | 61.0657 | 122.7356 | 123.0331 | -0.12817 | 122.9691 | 60.8963 | -0.33417 | 123.0331 | -0.12817 | 60.8963 | 122.7356 | 122.9691 | -123.2574 | -123.2529
3193.7656 | 123.1476 | -60.9192 | 62.027 | 0.25536 | -0.0041572 | -0.012625 | 0.0064792 | 0.060105 | -0.0071457 | 0.067197 | -61.0611 | 62.233 | -61.2717 | -61.1755 | 61.7615 | -0.07782 | -0.082397 | 0.073242 | 62.114 | -61.2442 | -0.35248 | 0.20599 | -0.14191 | -0.25635 | -0.2655 | -0.32501 | 0.086975 | 0.21057 | 60.8368 | 60.9924 | 122.6807 | 123.1522 | -0.14191 | 123.0331 | 60.8414 | -0.32501 | 123.1522 | -0.14191 | 60.8414 | 122.6807 | 123.0331 | -123.2986 | -123.2712
3194.7656 | 123.1247 | -60.9329 | 62.0453 | 0.20958 | -0.006507 | -0.011771 | 0.0045566 | 0.060105 | -0.0050095 | 0.068265 | -61.0794 | 62.2284 | -61.2762 | -61.1435 | 61.7477 | -0.12817 | -0.018311 | 0.07782 | 62.1689 | -61.2579 | -0.34332 | 0.18311 | -0.14649 | -0.21057 | -0.29755 | -0.32501 | 0.1236 | 0.19684 | 60.9146 | 61.0107 | 122.6807 | 123.1613 | -0.14649 | 123.1018 | 60.8047 | -0.32501 | 123.1613 | -0.14649 | 60.8047 | 122.6807 | 123.1018 | -123.3215 | -123.3032
3195.7656 | 123.1476 | -60.9375 | 62.0728 | 0.15617 | -0.0041572 | -0.0064301 | 0.0066928 | 0.06096 | -0.0058639 | 0.065702 | -61.0565 | 62.233 | -61.2854 | -61.203 | 61.7798 | -0.082397 | -0.10986 | 0.068665 | 62.1185 | -61.2488 | -0.3479 | 0.16022 | -0.11902 | -0.2655 | -0.29297 | -0.31128 | 0.045776 | 0.22888 | 60.8276 | 61.0062 | 122.7173 | 123.1705 | -0.11902 | 123.056 | 60.8551 | -0.31128 | 123.1705 | -0.11902 | 60.8551 | 122.7173 | 123.056 | -123.3582 | -123.3215
3196.7656 | 123.1476 | -60.9283 | 62.059 | -2.0411 | -0.008216 | -0.01113 | 0.0058382 | 0.063096 | -0.0067185 | 0.06442 | -61.0382 | 62.2238 | -61.2579 | -61.203 | 61.7615 | -0.073242 | -0.073242 | 0.073242 | 62.1231 | -61.2488 | -0.32959 | 0.16479 | -0.10986 | -0.27466 | -0.29755 | -0.32043 | 0.064087 | 0.21973 | 60.8551 | 61.0016 | 122.6898 | 123.1522 | -0.10986 | 123.0515 | 60.8551 | -0.32043 | 123.1522 | -0.10986 | 60.8551 | 122.6898 | 123.0515 | -123.317 | -123.3078
3197.7656 | 123.1384 | -60.9467 | 62.0865 | 0.1638 | -0.0045844 | -0.0089935 | 0.0047702 | 0.062669 | -0.0037277 | 0.067411 | -61.0931 | 62.2375 | -61.2808 | -61.1252 | 61.5738 | -0.37994 | 0.15564 | 0.24719 | 62.114 | -61.2534 | -0.33417 | 0.15106 | -0.14648 | -0.17853 | -0.5127 | -0.3067 | 0.027466 | 0.18768 | 61.1023 | 61.1938 | 122.5204 | 123.1842 | -0.14648 | 123.0606 | 60.5667 | -0.3067 | 123.1842 | -0.14648 | 60.5667 | 122.5204 | 123.0606 | -123.3673 | -123.3398
3198.7656 | 123.2254 | -60.8917 | 62.0178 | 0.20958 | -0.007575 | -0.0083527 | 0.0030612 | 0.061173 | -0.0043685 | 0.065275 | -61.0382 | 62.1826 | -61.2671 | -61.1069 | 61.853 | 0.013733 | -0.24261 | 0.16479 | 62.0636 | -61.2167 | -0.37537 | 0.16479 | -0.14648 | -0.21515 | -0.1648 | -0.32501 | 0.045777 | 0.22888 | 60.6491 | 61.0565 | 122.7448 | 123.0743 | -0.14648 | 122.9553 | 60.9055 | -0.32501 | 123.0743 | -0.14648 | 60.9055 | 122.7448 | 122.9553 | -123.2849 | -123.2346
3199.7656 | 123.23 | -60.9192 | 62.0132 | 0.25536 | -0.0077888 | -0.011557 | 0.005411 | 0.059678 | -0.0022323 | 0.06677 | -61.0428 | 62.2009 | -61.2717 | -61.1252 | 61.8347 | -0.022888 | -0.21057 | 0.15564 | 62.0773 | -61.2305 | -0.35248 | 0.18768 | -0.1236 | -0.20599 | -0.17853 | -0.31128 | 0.064087 | 0.22888 | 60.7086 | 61.0748 | 122.7539 | 123.1201 | -0.1236 | 122.9965 | 60.8963 | -0.31128 | 123.1201 | -0.1236 | 60.8963 | 122.7539 | 122.9965 | -123.2849 | -123.2437
3200.7656 | 123.1338 | -60.9421 | 62.0636 | 0.10277 | -0.005866 | -0.013266 | 0.0058382 | 0.062241 | -0.0043685 | 0.065702 | -61.0382 | 62.2375 | -61.2534 | -61.1801 | 61.7706 | -0.045776 | -0.054932 | 0.11902 | 62.1277 | -61.2488 | -0.31128 | 0.17395 | -0.09613 | -0.23804 | -0.29297 | -0.3067 | 0.064087 | 0.21515 | 60.8871 | 61.0611 | 122.7127 | 123.1796 | -0.09613 | 123.0698 | 60.8963 | -0.3067 | 123.1796 | -0.09613 | 60.8963 | 122.7127 | 123.0698 | -123.317 | -123.3124
3201.7656 | 123.1064 | -60.9283 | 62.0544 | 0.1638 | -0.0052252 | -0.014975 | 0.0077608 | 0.062028 | -0.0045821 | 0.065916 | -61.0886 | 62.2559 | -61.2946 | -61.2213 | 61.7432 | -0.07782 | -0.064087 | 0.082397 | 62.1323 | -61.2671 | -0.36621 | 0.20142 | -0.16022 | -0.29297 | -0.31128 | -0.33875 | 0.07782 | 0.20599 | 60.8643 | 61.0107 | 122.6715 | 123.1842 | -0.16022 | 123.0606 | 60.8505 | -0.33875 | 123.1842 | -0.16022 | 60.8505 | 122.6715 | 123.0606 | -123.349 | -123.3215
3202.7656 | 123.0927 | -60.9329 | 62.0361 | 0.14092 | -0.0037298 | -0.010275 | 0.0041292 | 0.062669 | -0.0077865 | 0.066343 | -61.0931 | 62.2192 | -61.2671 | -61.2122 | 61.7523 | -0.068665 | -0.050354 | 0.068665 | 62.1414 | -61.2396 | -0.33417 | 0.1831 | -0.16022 | -0.27924 | -0.28381 | -0.3067 | 0.10529 | 0.17395 | 60.8826 | 61.0016 | 122.6852 | 123.1522 | -0.16022 | 123.0743 | 60.8643 | -0.3067 | 123.1522 | -0.16022 | 60.8643 | 122.6852 | 123.0743 | -123.3032 | -123.2758
3203.7656 | 123.0972 | -60.9558 | 62.0682 | 0.14854 | -0.005866 | -0.0087799 | 0.004343 | 0.062241 | -0.0065047 | 0.066129 | -61.0611 | 62.2513 | -61.2762 | -61.2122 | 61.7386 | -0.054932 | -0.018311 | 0.091553 | 62.1277 | -61.2808 | -0.32043 | 0.18311 | -0.10529 | -0.25635 | -0.32959 | -0.32501 | 0.05951 | 0.21515 | 60.9375 | 61.0474 | 122.6944 | 123.2071 | -0.10529 | 123.0835 | 60.9009 | -0.32501 | 123.2071 | -0.10529 | 60.9009 | 122.6944 | 123.0835 | -123.3444 | -123.349
3204.7656 | 123.2391 | -60.9055 | 61.9995 | 0.27824 | -0.0045844 | -0.010489 | 0.0030612 | 0.064164 | -0.0054367 | 0.067624 | -61.0428 | 62.2009 | -61.2991 | -61.1664 | 61.8256 | -0.036621 | -0.20599 | 0.15564 | 62.1185 | -61.2442 | -0.39368 | 0.20142 | -0.13733 | -0.26093 | -0.17395 | -0.33875 | 0.11902 | 0.25635 | 60.6995 | 61.0611 | 122.731 | 123.1064 | -0.13733 | 123.024 | 60.8688 | -0.33875 | 123.1064 | -0.13733 | 60.8688 | 122.731 | 123.024 | -123.2986 | -123.2437
3205.7656 | 123.1979 | -60.9192 | 62.0178 | 0.25536 | -0.006507 | -0.0096343 | 0.002634 | 0.063737 | -0.0035141 | 0.067838 | -61.0565 | 62.1964 | -61.2671 | -61.1526 | 61.8027 | -0.036621 | -0.19226 | 0.13275 | 62.0956 | -61.2579 | -0.3479 | 0.17853 | -0.13733 | -0.23346 | -0.21515 | -0.33875 | 0.07782 | 0.21057 | 60.7269 | 61.0519 | 122.7219 | 123.1155 | -0.13733 | 123.0148 | 60.8826 | -0.33875 | 123.1155 | -0.13733 | 60.8826 | 122.7219 | 123.0148 | -123.2849 | -123.2758
3206.7656 | 123.1018 | -60.9283 | 62.0453 | 0.072251 | -0.0056524 | -0.0062163 | 0.0039156 | 0.062669 | -0.0058639 | 0.066343 | -61.0382 | 62.2284 | -61.2396 | -61.1801 | 61.7798 | -0.045776 | -0.041199 | 0.13275 | 62.1689 | -61.2579 | -0.31128 | 0.18311 | -0.10986 | -0.25177 | -0.2655 | -0.32959 | 0.1236 | 0.20142 | 60.8871 | 61.0611 | 122.7081 | 123.1567 | -0.10986 | 123.0972 | 60.8826 | -0.32959 | 123.1567 | -0.10986 | 60.8826 | 122.7081 | 123.0972 | -123.2849 | -123.3032
3207.7656 | 123.1338 | -60.9055 | 62.0819 | 0.041733 | -0.0052252 | -0.010489 | 0.0056246 | 0.061814 | -0.0067185 | 0.068479 | -61.0291 | 62.2284 | -61.2625 | -61.171 | 61.7844 | -0.045776 | -0.054932 | 0.1236 | 62.1323 | -61.2534 | -0.35706 | 0.14648 | -0.1236 | -0.2655 | -0.29755 | -0.3479 | 0.050354 | 0.23346 | 60.8505 | 61.0291 | 122.6898 | 123.1339 | -0.1236 | 123.0377 | 60.8597 | -0.3479 | 123.1339 | -0.1236 | 60.8597 | 122.6898 | 123.0377 | -123.3444 | -123.3353
3208.7656 | 123.1064 | -60.9558 | 62.0499 | 0.14854 | -0.0043708 | -0.014975 | 0.0058382 | 0.063523 | -0.0058639 | 0.067197 | -61.084 | 62.2238 | -61.2625 | -61.235 | 61.7386 | -0.091553 | -0.059509 | 0.082397 | 62.1643 | -61.2808 | -0.3067 | 0.17395 | -0.12817 | -0.27923 | -0.31128 | -0.32501 | 0.11444 | 0.17853 | 60.8963 | 61.0382 | 122.6944 | 123.1796 | -0.12817 | 123.1201 | 60.8643 | -0.32501 | 123.1796 | -0.12817 | 60.8643 | 122.6944 | 123.1201 | -123.3124 | -123.3307
3209.7656 | 123.1155 | -60.9329 | 62.0819 | 0.14092 | -0.0033026 | -0.011771 | 0.00712 | 0.060746 | -0.0039413 | 0.066556 | -61.0886 | 62.2696 | -61.2671 | -61.203 | 61.7386 | -0.10986 | -0.036621 | 0.064087 | 62.1368 | -61.2808 | -0.33417 | 0.18768 | -0.15564 | -0.27008 | -0.34332 | -0.3479 | 0.054932 | 0.17853 | 60.8963 | 60.997 | 122.6715 | 123.2025 | -0.15564 | 123.0698 | 60.8231 | -0.3479 | 123.2025 | -0.15564 | 60.8231 | 122.6715 | 123.0698 | -123.349 | -123.3627
3210.7656 | 123.0927 | -60.9467 | 62.059 | 0.14854 | -0.0056524 | -0.0085663 | 0.005411 | 0.062028 | -0.0060775 | 0.067197 | -61.0748 | 62.2513 | -61.2579 | -61.2259 | 61.7477 | -0.086975 | -0.036621 | 0.064087 | 62.1552 | -61.2717 | -0.31128 | 0.19226 | -0.12817 | -0.27924 | -0.31128 | -0.32501 | 0.09613 | 0.18311 | 60.91 | 61.0107 | 122.6944 | 123.1979 | -0.12817 | 123.1018 | 60.8597 | -0.32501 | 123.1979 | -0.12817 | 60.8597 | 122.6944 | 123.1018 | -123.317 | -123.3307
3211.7656 | 123.2162 | -60.8963 | 62.0087 | 0.2401 | -0.0060798 | -0.011771 | 0.0049838 | 0.058182 | -0.0056503 | 0.066556 | -61.0428 | 62.1964 | -61.2717 | -61.1298 | 61.8164 | -0.013733 | -0.25177 | 0.16937 | 62.0911 | -61.2717 | -0.37537 | 0.18768 | -0.14648 | -0.23346 | -0.19226 | -0.37537 | 0.082397 | 0.22888 | 60.6445 | 61.0657 | 122.7127 | 123.0927 | -0.14648 | 122.9874 | 60.8826 | -0.37537 | 123.0927 | -0.14648 | 60.8826 | 122.7127 | 122.9874 | -123.2803 | -123.2803
3212.7656 | 123.1842 | -60.9283 | 61.9995 | 0.2935 | -0.0073614 | -0.01113 | 0.0028476 | 0.060746 | -0.00073695 | 0.067197 | -61.0519 | 62.1872 | -61.2488 | -61.171 | 61.8073 | -0.032043 | -0.20142 | 0.15564 | 62.1094 | -61.2625 | -0.32043 | 0.18768 | -0.1236 | -0.24261 | -0.19226 | -0.33417 | 0.10986 | 0.19684 | 60.7269 | 61.084 | 122.7356 | 123.1155 | -0.1236 | 123.0377 | 60.8963 | -0.33417 | 123.1155 | -0.1236 | 60.8963 | 122.7356 | 123.0377 | -123.2483 | -123.262
3213.7656 | 123.0789 | -60.9238 | 62.0956 | 0.10277 | -0.0071478 | -0.0077117 | 0.0058382 | 0.06096 | -0.0071457 | 0.069761 | -61.0474 | 62.2284 | -61.2762 | -61.1893 | 61.7477 | -0.073242 | -0.045776 | 0.10529 | 62.1368 | -61.2717 | -0.35248 | 0.13275 | -0.1236 | -0.2655 | -0.3479 | -0.3479 | 0.041199 | 0.22888 | 60.878 | 61.0291 | 122.6715 | 123.1522 | -0.1236 | 123.0606 | 60.8505 | -0.3479 | 123.1522 | -0.1236 | 60.8505 | 122.6715 | 123.0606 | -123.3719 | -123.3673
3214.7656 | 123.111 | -60.8963 | 62.0544 | 0.095139 | -0.0045844 | -0.010916 | 0.0064792 | 0.06096 | -0.0056503 | 0.064847 | -61.0336 | 62.2375 | -61.2671 | -61.171 | 61.7706 | -0.050354 | -0.041199 | 0.1236 | 62.1872 | -61.2488 | -0.37079 | 0.18311 | -0.13733 | -0.27466 | -0.28381 | -0.35248 | 0.13275 | 0.23346 | 60.8551 | 61.0199 | 122.6669 | 123.1338 | -0.13733 | 123.0835 | 60.8459 | -0.35248 | 123.1338 | -0.13733 | 60.8459 | 122.6669 | 123.0835 | -123.3215 | -123.3032
3215.7656 | 123.1201 | -60.91 | 62.0636 | 0.18669 | -0.0052252 | -0.0083527 | 0.0049838 | 0.061814 | -0.0037277 | 0.066343 | -61.0886 | 62.2559 | -61.2671 | -61.2167 | 61.7203 | -0.091553 | -0.041199 | 0.086975 | 62.1735 | -61.2717 | -0.35706 | 0.19226 | -0.17853 | -0.3067 | -0.34332 | -0.36163 | 0.10986 | 0.17853 | 60.8688 | 60.997 | 122.6303 | 123.1659 | -0.17853 | 123.0835 | 60.8185 | -0.36163 | 123.1659 | -0.17853 | 60.8185 | 122.6303 | 123.0835 | -123.3307 | -123.3353
3216.7656 | 123.1201 | -60.9375 | 62.0499 | 0.07988 | -0.006507 | -0.013907 | 0.0047702 | 0.063523 | -0.0069321 | 0.064847 | -61.0703 | 62.2421 | -61.2442 | -61.2122 | 61.7249 | -0.10071 | -0.050354 | 0.086975 | 62.1368 | -61.2671 | -0.3067 | 0.19226 | -0.13275 | -0.27466 | -0.32501 | -0.32959 | 0.086975 | 0.17395 | 60.8871 | 61.0245 | 122.6624 | 123.1796 | -0.13275 | 123.0743 | 60.8368 | -0.32959 | 123.1796 | -0.13275 | 60.8368 | 122.6624 | 123.0743 | -123.2941 | -123.317
3217.7656 | 123.1567 | -60.9146 | 62.0819 | 0.018845 | -0.0062934 | -0.013266 | 0.0066928 | 0.062455 | -0.0054367 | 0.066343 | -61.0291 | 62.2421 | -61.2671 | -61.1572 | 61.7889 | -0.018311 | -0.045776 | 0.14648 | 62.1552 | -61.2671 | -0.35248 | 0.16022 | -0.11444 | -0.24262 | -0.29297 | -0.35248 | 0.073242 | 0.23804 | 60.8688 | 61.0611 | 122.7036 | 123.1567 | -0.11444 | 123.0698 | 60.8963 | -0.35248 | 123.1567 | -0.11444 | 60.8963 | 122.7036 | 123.0698 | -123.349 | -123.349
3218.7656 | 123.1338 | -60.9009 | 62.059 | 0.041733 | -0.0041572 | -0.014548 | 0.0051974 | 0.062241 | -0.0062911 | 0.06677 | -61.0474 | 62.233 | -61.2579 | -61.1938 | 61.7569 | -0.073242 | -0.032043 | 0.10529 | 62.178 | -61.2625 | -0.35706 | 0.17395 | -0.14648 | -0.29297 | -0.30212 | -0.36163 | 0.11902 | 0.21057 | 60.8688 | 61.0062 | 122.6578 | 123.1338 | -0.14648 | 123.0789 | 60.8276 | -0.36163 | 123.1338 | -0.14648 | 60.8276 | 122.6578 | 123.0789 | -123.317 | -123.3215
3219.7656 | 123.1705 | -60.9421 | 62.059 | 0.24773 | -0.0073614 | -0.015189 | 0.001993 | 0.062028 | -0.0058639 | 0.068693 | -61.084 | 62.2192 | -61.2762 | -61.1755 | 61.7661 | -0.041199 | -0.17395 | 0.10529 | 62.1094 | -61.2671 | -0.33417 | 0.16022 | -0.14191 | -0.23346 | -0.29297 | -0.32501 | 0.050354 | 0.19226 | 60.7681 | 61.0474 | 122.7081 | 123.1613 | -0.14191 | 123.0515 | 60.9009 | -0.32501 | 123.1613 | -0.14191 | 60.9009 | 122.7081 | 123.0515 | -123.3353 | -123.3261
3220.7656 | 123.1293 | -60.9146 | 62.0682 | 0.07988 | -0.0054388 | -0.013052 | 0.0075472 | 0.062669 | -0.0035141 | 0.066343 | -61.0199 | 62.2375 | -61.2396 | -61.1893 | 61.7706 | -0.050354 | -0.032043 | 0.14191 | 62.1689 | -61.29 | -0.32501 | 0.16937 | -0.10529 | -0.27466 | -0.29755 | -0.37537 | 0.10071 | 0.21973 | 60.8826 | 61.0565 | 122.6852 | 123.1522 | -0.10529 | 123.0835 | 60.8643 | -0.37537 | 123.1522 | -0.10529 | 60.8643 | 122.6852 | 123.0835 | -123.3078 | -123.3582
3221.7656 | 123.1613 | -60.91 | 62.0728 | 0.087509 | -0.0050116 | -0.012198 | 0.0045566 | 0.061387 | -0.0050095 | 0.066984 | -61.0245 | 62.2375 | -61.2488 | -61.1664 | 61.7752 | -0.032043 | -0.054932 | 0.16937 | 62.146 | -61.2671 | -0.33874 | 0.16479 | -0.11444 | -0.25635 | -0.29755 | -0.35706 | 0.073242 | 0.2243 | 60.8551 | 61.0794 | 122.6852 | 123.1476 | -0.11444 | 123.056 | 60.878 | -0.35706 | 123.1476 | -0.11444 | 60.878 | 122.6852 | 123.056 | -123.3215 | -123.3398
3222.7656 | 123.143 | -60.9467 | 62.0865 | 0.064621 | -0.0062934 | -0.010275 | 0.004343 | 0.064591 | -0.0060775 | 0.068052 | -61.0611 | 62.2375 | -61.2488 | -61.1984 | 61.7477 | -0.073242 | -0.064087 | 0.10986 | 62.178 | -61.29 | -0.30212 | 0.15106 | -0.11444 | -0.25177 | -0.33874 | -0.34332 | 0.091553 | 0.18768 | 60.8826 | 61.0565 | 122.6944 | 123.1842 | -0.11444 | 123.1247 | 60.8734 | -0.34332 | 123.1842 | -0.11444 | 60.8734 | 122.6944 | 123.1247 | -123.3353 | -123.3765
3223.7656 | 123.1293 | -60.9558 | 62.059 | 0.1104 | -0.0039434 | -0.0094207 | 0.0060518 | 0.065018 | -0.0052231 | 0.065061 | -61.0474 | 62.2375 | -61.2488 | -61.1984 | 61.7706 | -0.050354 | -0.041199 | 0.1236 | 62.1918 | -61.2762 | -0.29297 | 0.17853 | -0.091552 | -0.24261 | -0.28839 | -0.32043 | 0.13275 | 0.20142 | 60.9146 | 61.0794 | 122.7264 | 123.1934 | -0.091552 | 123.1476 | 60.9055 | -0.32043 | 123.1934 | -0.091552 | 60.9055 | 122.7264 | 123.1476 | -123.3078 | -123.3353
3224.7656 | 123.143 | -60.9329 | 62.0682 | 0.049362 | -0.0041572 | -0.0096343 | 0.0066928 | 0.064378 | -0.0073593 | 0.068693 | -61.0199 | 62.2467 | -61.2671 | -61.171 | 61.7752 | -0.036621 | -0.041199 | 0.15106 | 62.1872 | -61.2671 | -0.33417 | 0.17853 | -0.086975 | -0.23804 | -0.29297 | -0.33417 | 0.11902 | 0.24719 | 60.8917 | 61.084 | 122.7081 | 123.1796 | -0.086975 | 123.1201 | 60.8963 | -0.33417 | 123.1796 | -0.086975 | 60.8963 | 122.7081 | 123.1201 | -123.3353 | -123.3353
3225.7656 | 123.1567 | -60.9283 | 62.0361 | 0.18669 | -0.0045844 | -0.012412 | 0.0041292 | 0.061387 | -0.0043685 | 0.067624 | -61.0657 | 62.2147 | -61.2671 | -61.2305 | 61.7615 | -0.091553 | -0.10529 | 0.082397 | 62.1826 | -61.2762 | -0.33875 | 0.17853 | -0.13733 | -0.30212 | -0.27466 | -0.3479 | 0.14648 | 0.20142 | 60.8231 | 61.0107 | 122.6898 | 123.143 | -0.13733 | 123.111 | 60.8368 | -0.3479 | 123.143 | -0.13733 | 60.8368 | 122.6898 | 123.111 | -123.3032 | -123.3124
3226.7656 | 123.1247 | -60.9146 | 62.0544 | 0.35454 | -0.004798 | -0.010489 | 0.0028476 | 0.063096 | -0.0056503 | 0.069761 | -61.0382 | 62.2467 | -61.2625 | -61.2167 | 61.7523 | -0.10529 | -0.073242 | 0.073242 | 62.1964 | -61.2991 | -0.3479 | 0.19226 | -0.1236 | -0.30212 | -0.30212 | -0.38452 | 0.14191 | 0.2243 | 60.8414 | 60.9879 | 122.6669 | 123.1613 | -0.1236 | 123.111 | 60.8093 | -0.38452 | 123.1613 | -0.1236 | 60.8093 | 122.6669 | 123.111 | -123.317 | -123.3536
3227.7656 | 123.1796 | -60.8871 | 62.0499 | -0.04982 | -0.0080024 | -0.013052 | 0.003702 | 0.061387 | -0.0045821 | 0.066343 | -61.1755 | 62.2055 | -61.2717 | -61.1481 | 61.8118 | 0.009155 | -0.041199 | 0.22888 | 62.2009 | -61.2442 | -0.38452 | 0.15564 | -0.28839 | -0.26093 | -0.23804 | -0.35706 | 0.15106 | 0.09613 | 60.8459 | 61.116 | 122.699 | 123.0927 | -0.28839 | 123.0881 | 60.8963 | -0.35706 | 123.0927 | -0.28839 | 60.8963 | 122.699 | 123.0881 | -123.3215 | -123.2941
3228.7656 | 123.1659 | -60.9375 | 62.0636 | -0.04982 | -0.0024482 | -0.014548 | 0.0058382 | 0.06096 | -0.0047957 | 0.066343 | -60.9879 | 62.2375 | -61.2488 | -61.1389 | 61.8164 | 0.032043 | -0.045776 | 0.004578 | 62.1368 | -61.2717 | -0.31128 | 0.17395 | -0.050354 | -0.20142 | -0.24719 | -0.33417 | 0.073242 | 0.26093 | 60.8917 | 60.9421 | 122.7539 | 123.175 | -0.050354 | 123.0743 | 60.9695 | -0.33417 | 123.175 | -0.050354 | 60.9695 | 122.7539 | 123.0743 | -123.3124 | -123.3353
3229.7656 | 123.1613 | -60.9192 | 62.0682 | -0.21767 | -0.005866 | -0.01113 | 0.0069064 | 0.061387 | -0.0037277 | 0.066343 | -61.0199 | 62.2284 | -61.2213 | -61.1343 | 61.7844 | -0.004578 | -0.054932 | 0.20142 | 62.1964 | -61.2534 | -0.30212 | 0.16022 | -0.10071 | -0.21515 | -0.28381 | -0.33417 | 0.12817 | 0.20142 | 60.8643 | 61.1206 | 122.7036 | 123.1476 | -0.10071 | 123.1155 | 60.9146 | -0.33417 | 123.1476 | -0.10071 | 60.9146 | 122.7036 | 123.1155 | -123.2895 | -123.3215
3230.7656 | 123.1659 | -60.9055 | 62.0773 | -0.026932 | -0.005866 | -0.010916 | 0.0060518 | 0.06395 | -0.0067185 | 0.066129 | -61.0153 | 62.2513 | -61.2808 | -61.084 | 61.8073 | 0.036621 | -0.041199 | 0.23346 | 62.178 | -61.2534 | -0.37537 | 0.17395 | -0.10986 | -0.17853 | -0.27008 | -0.3479 | 0.10071 | 0.2655 | 60.8643 | 61.1389 | 122.7127 | 123.1567 | -0.10986 | 123.0835 | 60.9421 | -0.3479 | 123.1567 | -0.10986 | 60.9421 | 122.7127 | 123.0835 | -123.3582 | -123.3307
3231.7656 | 123.1796 | -60.9192 | 62.0956 | -0.15663 | -0.0069342 | -0.012412 | 0.0051974 | 0.061814 | -0.0045821 | 0.066343 | -61.0245 | 62.2421 | -61.2488 | -61.1526 | 61.8073 | 0.018311 | -0.045776 | 0.21515 | 62.1643 | -61.2625 | -0.32959 | 0.14648 | -0.10529 | -0.23346 | -0.28839 | -0.34332 | 0.068665 | 0.2243 | 60.8734 | 61.1343 | 122.7264 | 123.1613 | -0.10529 | 123.0835 | 60.9375 | -0.34332 | 123.1613 | -0.10529 | 60.9375 | 122.7264 | 123.0835 | -123.3444 | -123.3582
3232.7656 | 123.0972 | -60.9238 | 62.0728 | 0.13329 | -0.0033026 | -0.0096343 | 0.0039156 | 0.060746 | -0.0058639 | 0.068265 | -61.0657 | 62.2559 | -61.2534 | -61.2076 | 61.7477 | -0.082397 | -0.041199 | 0.09613 | 62.1872 | -61.29 | -0.32959 | 0.1831 | -0.14191 | -0.28381 | -0.32501 | -0.36621 | 0.11444 | 0.18768 | 60.8826 | 61.0199 | 122.6715 | 123.1796 | -0.14191 | 123.111 | 60.8414 | -0.36621 | 123.1796 | -0.14191 | 60.8414 | 122.6715 | 123.111 | -123.3261 | -123.3627
3233.7656 | 123.1247 | -60.8917 | 62.0682 | 0.072251 | -0.004798 | -0.011343 | 0.0047702 | 0.061814 | -0.0073593 | 0.066343 | -61.0474 | 62.2147 | -61.2442 | -61.1847 | 61.7569 | -0.068665 | -0.050354 | 0.14191 | 62.178 | -61.2762 | -0.35248 | 0.14648 | -0.15564 | -0.29297 | -0.31128 | -0.38452 | 0.10986 | 0.19684 | 60.8414 | 61.0336 | 122.6486 | 123.1064 | -0.15564 | 123.0698 | 60.8231 | -0.38452 | 123.1064 | -0.15564 | 60.8231 | 122.6486 | 123.0698 | -123.3124 | -123.3444
3234.7812 | 123.1934 | -60.9009 | 62.0132 | 0.25536 | -0.006507 | -0.013907 | 0.0028476 | 0.0616 | -0.0043685 | 0.065916 | -61.0794 | 62.2009 | -61.2488 | -61.171 | 61.7844 | -0.054932 | -0.19684 | 0.13733 | 62.1323 | -61.2671 | -0.3479 | 0.18768 | -0.17853 | -0.27008 | -0.22888 | -0.36621 | 0.11902 | 0.16937 | 60.704 | 61.0382 | 122.6852 | 123.1018 | -0.17853 | 123.0331 | 60.8459 | -0.36621 | 123.1018 | -0.17853 | 60.8459 | 122.6852 | 123.0331 | -123.262 | -123.2803
3235.7656 | 123.1155 | -60.91 | 62.0865 | -0.13374 | -0.0067206 | -0.012412 | 0.0015658 | 0.060319 | -0.0071457 | 0.064207 | -61.0474 | 62.2192 | -61.2625 | -61.1618 | 61.7981 | 0 | 0.045776 | 0.20599 | 62.1964 | -61.2213 | -0.35248 | 0.13275 | -0.13733 | -0.25177 | -0.28839 | -0.31128 | 0.10986 | 0.21515 | 60.9558 | 61.116 | 122.7081 | 123.1293 | -0.13733 | 123.1064 | 60.91 | -0.31128 | 123.1293 | -0.13733 | 60.91 | 122.7081 | 123.1064 | -123.349 | -123.3078
3236.7656 | 123.1659 | -60.9192 | 62.1002 | -0.14137 | -0.0071478 | -0.017966 | 0.0030612 | 0.060746 | -0.0054367 | 0.066129 | -61.0428 | 62.2604 | -61.2534 | -61.1618 | 61.8118 | 0.013733 | 0.022888 | 0.22888 | 62.2009 | -61.2534 | -0.33417 | 0.16022 | -0.1236 | -0.24261 | -0.28839 | -0.33417 | 0.10071 | 0.21057 | 60.9421 | 61.1481 | 122.731 | 123.1796 | -0.1236 | 123.1201 | 60.9329 | -0.33417 | 123.1796 | -0.1236 | 60.9329 | 122.731 | 123.1201 | -123.3536 | -123.3536
3237.7656 | 123.1201 | -60.8963 | 62.1002 | -0.149 | -0.0071478 | -0.014761 | 0.0030612 | 0.062241 | -0.0035141 | 0.067411 | -61.0703 | 62.2421 | -61.2579 | -61.1572 | 61.7981 | 0.009155 | 0.050354 | 0.21057 | 62.2101 | -61.2579 | -0.36163 | 0.14191 | -0.17395 | -0.26093 | -0.30212 | -0.36163 | 0.10986 | 0.18768 | 60.9467 | 61.1069 | 122.6944 | 123.1384 | -0.17395 | 123.1064 | 60.9055 | -0.36163 | 123.1384 | -0.17395 | 60.9055 | 122.6944 | 123.1064 | -123.3582 | -123.3582
3238.7656 | 123.175 | -60.9009 | 62.059 | 0.0035856 | -0.0041572 | -0.0089935 | 0.004343 | 0.062669 | -0.0077865 | 0.064207 | -61.1069 | 62.1918 | -61.2717 | -61.1572 | 61.8027 | 0.032043 | -0.050354 | 0.21057 | 62.1552 | -61.2534 | -0.37079 | 0.13275 | -0.20599 | -0.25635 | -0.25635 | -0.35248 | 0.09613 | 0.16479 | 60.8505 | 61.1115 | 122.7036 | 123.0927 | -0.20599 | 123.056 | 60.9329 | -0.35248 | 123.0927 | -0.20599 | 60.9329 | 122.7036 | 123.056 | -123.3307 | -123.3124
3239.7812 | 123.2529 | -60.91 | 62.027 | 0.20958 | -0.0062934 | -0.014761 | 0.002634 | 0.06096 | -0.0058639 | 0.068052 | -61.0153 | 62.146 | -61.2625 | -61.116 | 61.8439 | -0.027466 | -0.27008 | 0.1831 | 62.114 | -61.2167 | -0.35248 | 0.11902 | -0.10529 | -0.20599 | -0.18311 | -0.3067 | 0.086975 | 0.24719 | 60.64 | 61.0931 | 122.7539 | 123.056 | -0.10529 | 123.024 | 60.8826 | -0.3067 | 123.056 | -0.10529 | 60.8826 | 122.7539 | 123.024 | -123.2895 | -123.2437
3240.7656 | 123.175 | -60.9192 | 62.059 | -0.072708 | -0.0077888 | -0.013266 | 0.005411 | 0.061814 | -0.0084273 | 0.065488 | -60.997 | 62.2238 | -61.2762 | -61.1298 | 61.8301 | 0.018311 | -0.022888 | 0.2243 | 62.1735 | -61.2305 | -0.35706 | 0.16479 | -0.07782 | -0.21057 | -0.22888 | -0.31128 | 0.11444 | 0.27924 | 60.8963 | 61.1435 | 122.7493 | 123.143 | -0.07782 | 123.0927 | 60.9375 | -0.31128 | 123.143 | -0.07782 | 60.9375 | 122.7493 | 123.0927 | -123.3353 | -123.2895
3241.7656 | 123.1705 | -60.8917 | 62.0773 | -0.20241 | -0.010779 | -0.010916 | -0.0018522 | 0.059251 | -0.0062911 | 0.065275 | -61.0336 | 62.1918 | -61.2076 | -61.1435 | 61.821 | 0.022888 | 0.022888 | 0.23804 | 62.2147 | -61.2076 | -0.31586 | 0.11444 | -0.14191 | -0.25177 | -0.25635 | -0.31586 | 0.13733 | 0.17395 | 60.9146 | 61.1298 | 122.7127 | 123.0835 | -0.14191 | 123.1064 | 60.9146 | -0.31586 | 123.0835 | -0.14191 | 60.9146 | 122.7127 | 123.1064 | -123.2849 | -123.2849
3242.8906 | 123.143 | -60.878 | 62.1002 | -0.19478 | -0.010352 | -0.01348 | -0.0018522 | 0.057542 | -0.0058639 | 0.065275 | -61.0245 | 62.1368 | -61.2167 | -61.1298 | 61.821 | 0.045776 | 0.004578 | 0.27466 | 62.2284 | -61.1847 | -0.33874 | 0.036621 | -0.14648 | -0.25177 | -0.27924 | -0.3067 | 0.12817 | 0.19226 | 60.8826 | 61.1526 | 122.699 | 123.0148 | -0.14648 | 123.1064 | 60.9238 | -0.3067 | 123.0148 | -0.14648 | 60.9238 | 122.699 | 123.1064 | -123.317 | -123.2849
3243.7812 | 123.1338 | -60.8871 | 62.1094 | -0.12611 | -0.0077888 | -0.011557 | 0.0045566 | 0.05861 | -0.0056503 | 0.063993 | -61.0199 | 62.2192 | -61.2625 | -61.1435 | 61.7981 | -0.004578 | 0.032043 | 0.20599 | 62.2009 | -61.2534 | -0.37537 | 0.10986 | -0.13275 | -0.25635 | -0.31128 | -0.36621 | 0.091553 | 0.24262 | 60.9192 | 61.0931 | 122.6852 | 123.1064 | -0.13275 | 123.0881 | 60.8826 | -0.36621 | 123.1064 | -0.13275 | 60.8826 | 122.6852 | 123.0881 | -123.3719 | -123.3627
3244.7812 | 123.1155 | -60.9512 | 62.1231 | -0.21767 | -0.0080024 | -0.012839 | 0.002634 | 0.059464 | -0.0028731 | 0.063779 | -61.0474 | 62.2101 | -61.2442 | -61.1572 | 61.8027 | -0.013733 | 0.041199 | 0.20142 | 62.1964 | -61.2396 | -0.29297 | 0.086975 | -0.09613 | -0.20599 | -0.32044 | -0.28839 | 0.073242 | 0.19684 | 60.9924 | 61.1526 | 122.7539 | 123.1613 | -0.09613 | 123.1476 | 60.9375 | -0.28839 | 123.1613 | -0.09613 | 60.9375 | 122.7539 | 123.1476 | -123.3673 | -123.3627
3245.7656 | 123.2025 | -60.8734 | 62.0865 | -0.15663 | -0.009284 | -0.013907 | -0.0018522 | 0.059891 | -0.0060775 | 0.065916 | -61.0016 | 62.1414 | -61.2213 | -61.0977 | 61.8713 | 0.064087 | -0.064087 | 0.32044 | 62.1643 | -61.171 | -0.3479 | 0.054931 | -0.12817 | -0.2243 | -0.21515 | -0.29755 | 0.07782 | 0.21973 | 60.8093 | 61.1938 | 122.7448 | 123.0148 | -0.12817 | 123.0377 | 60.9375 | -0.29755 | 123.0148 | -0.12817 | 60.9375 | 122.7448 | 123.0377 | -123.3078 | -123.2574
3246.7656 | 123.1384 | -60.9055 | 62.114 | -0.19478 | -0.0073614 | -0.012625 | 0.004343 | 0.058396 | -0.0060775 | 0.064634 | -61.0565 | 62.2101 | -61.2671 | -61.1618 | 61.7889 | -0.013733 | 0.045776 | 0.20142 | 62.2101 | -61.235 | -0.36163 | 0.09613 | -0.15106 | -0.25635 | -0.32501 | -0.32959 | 0.09613 | 0.21057 | 60.9512 | 61.1069 | 122.6944 | 123.1155 | -0.15106 | 123.1155 | 60.8917 | -0.32959 | 123.1155 | -0.15106 | 60.8917 | 122.6944 | 123.1155 | -123.381 | -123.349
3247.7656 | 123.1338 | -60.8871 | 62.0773 | 0.43083 | -0.0094976 | -0.010916 | 0.0011386 | 0.060105 | -0.0073593 | 0.068265 | -61.0886 | 62.1918 | -61.2625 | -61.1572 | 61.8027 | -0.013733 | 0.059509 | 0.19684 | 62.1964 | -61.2076 | -0.37537 | 0.11444 | -0.20142 | -0.27008 | -0.27466 | -0.32043 | 0.11902 | 0.17395 | 60.9467 | 61.084 | 122.6898 | 123.0789 | -0.20142 | 123.0835 | 60.8734 | -0.32043 | 123.0789 | -0.20142 | 60.8734 | 122.6898 | 123.0835 | -123.3398 | -123.2849
3248.7656 | 123.2391 | -60.8871 | 62.0453 | -0.14137 | -0.010993 | -0.013907 | -0.0080472 | 0.059251 | -0.0043685 | 0.065916 | -60.9924 | 62.1185 | -61.2076 | -61.1847 | 61.8622 | 0.041199 | -0.1236 | 0.27924 | 62.1277 | -61.1664 | -0.32043 | 0.073242 | -0.10529 | -0.29755 | -0.1831 | -0.27924 | 0.082398 | 0.21515 | 60.7636 | 61.1664 | 122.7493 | 123.0057 | -0.10529 | 123.0148 | 60.9283 | -0.27924 | 123.0057 | -0.10529 | 60.9283 | 122.7493 | 123.0148 | -123.2529 | -123.2117
3249.7656 | 123.3307 | -60.8505 | 62.1094 | -0.11085 | -0.010993 | -0.013907 | -0.0027066 | 0.057542 | -0.0073593 | 0.06677 | -60.9879 | 62.1094 | -61.2076 | -61.0519 | 61.8896 | 0.073242 | -0.13275 | 0.32044 | 62.1185 | -61.1526 | -0.35706 | 0 | -0.13733 | -0.20142 | -0.21973 | -0.30212 | 0.009155 | 0.21973 | 60.7178 | 61.171 | 122.7402 | 122.9599 | -0.13733 | 122.9691 | 60.9238 | -0.30212 | 122.9599 | -0.13733 | 60.9238 | 122.7402 | 122.9691 | -123.317 | -123.262
3250.7656 | 123.2254 | -60.8643 | 62.0636 | -0.58388 | -0.0090704 | -0.012412 | -0.00035676 | 0.059464 | -0.0084273 | 0.065916 | -61.0153 | 62.0911 | -61.2122 | -61.0703 | 61.8805 | 0.082397 | -0.13275 | 0.32044 | 62.1506 | -61.1618 | -0.3479 | 0.027465 | -0.15106 | -0.20599 | -0.18311 | -0.29755 | 0.086975 | 0.19684 | 60.7315 | 61.1847 | 122.7448 | 122.9553 | -0.15106 | 123.0148 | 60.9467 | -0.29755 | 122.9553 | -0.15106 | 60.9467 | 122.7448 | 123.0148 | -123.2758 | -123.2254
3251.7656 | 123.2391 | -60.8734 | 62.059 | -0.17189 | -0.0097114 | -0.018607 | -0.004202 | 0.060532 | -0.0035141 | 0.06677 | -60.997 | 62.1231 | -61.2305 | -61.0748 | 61.8256 | 0.059509 | -0.13733 | 0.26093 | 62.1277 | -61.1755 | -0.35706 | 0.064087 | -0.1236 | -0.20142 | -0.23346 | -0.30212 | 0.068665 | 0.23346 | 60.7361 | 61.1343 | 122.699 | 122.9965 | -0.1236 | 123.0011 | 60.9329 | -0.30212 | 122.9965 | -0.1236 | 60.9329 | 122.699 | 123.0011 | -123.2895 | -123.2346
3252.7812 | 123.2025 | -60.8643 | 62.0361 | 0.1638 | -0.0088568 | -0.013266 | 0.00071144 | 0.054978 | -0.0065047 | 0.065488 | -61.0565 | 62.1002 | -61.2671 | -61.1481 | 61.7935 | -0.036621 | -0.16479 | 0.40741 | 62.1231 | -61.1755 | -0.40283 | 0.064087 | -0.19226 | -0.28381 | -0.24262 | -0.31128 | 0.086975 | 0.21057 | 60.6995 | 61.2717 | 122.6578 | 122.9645 | -0.19226 | 122.9874 | 60.8276 | -0.31128 | 122.9645 | -0.19226 | 60.8276 | 122.6578 | 122.9874 | -123.3032 | -123.2117
3254.375 | 123.2071 | -60.8734 | 62.0682 | -0.14137 | -0.010779 | -0.014548 | 0.00092504 | 0.054978 | -0.0071457 | 0.065275 | -60.9879 | 62.1323 | -61.2167 | -61.0611 | 61.8576 | 0.068665 | -0.064087 | 0.32044 | 62.1368 | -61.203 | -0.34332 | 0.064087 | -0.11444 | -0.18768 | -0.21057 | -0.32959 | 0.068665 | 0.22888 | 60.8093 | 61.1938 | 122.731 | 123.0057 | -0.11444 | 123.0103 | 60.9421 | -0.32959 | 123.0057 | -0.11444 | 60.9421 | 122.731 | 123.0103 | -123.2849 | -123.2712
3254.9375 | 123.175 | -60.9146 | 62.1094 | -0.15663 | -0.0077888 | -0.010489 | 0.0084018 | 0.056687 | -0.0054367 | 0.065061 | -61.0199 | 62.2192 | -61.2259 | -61.116 | 61.8118 | 0 | -0.004578 | 0.22888 | 62.1643 | -61.2488 | -0.31128 | 0.10986 | -0.10529 | -0.20142 | -0.29755 | -0.33417 | 0.054932 | 0.20599 | 60.91 | 61.1435 | 122.7264 | 123.1338 | -0.10529 | 123.0789 | 60.9146 | -0.33417 | 123.1338 | -0.10529 | 60.9146 | 122.7264 | 123.0789 | -123.3353 | -123.3582
3256.3281 | 123.143 | -60.91 | 62.0636 | 0.21721 | -0.0056524 | -0.0092071 | 0.0062656 | 0.059891 | -0.0065047 | 0.065061 | -61.0519 | 62.1918 | -61.2717 | -61.1755 | 61.7661 | -0.11902 | -0.16022 | 0.086975 | 62.1506 | -61.2442 | -0.36163 | 0.12817 | -0.14191 | -0.2655 | -0.29755 | -0.33417 | 0.086975 | 0.21973 | 60.7498 | 60.997 | 122.6761 | 123.1018 | -0.14191 | 123.0606 | 60.791 | -0.33417 | 123.1018 | -0.14191 | 60.791 | 122.6761 | 123.0606 | -123.3353 | -123.3078
3256.7812 | 123.1201 | -60.9375 | 62.0773 | 0.15617 | -0.0043708 | -0.011771 | 0.0047702 | 0.05861 | -0.0052231 | 0.065275 | -61.0748 | 62.2101 | -61.2808 | -61.171 | 61.7569 | -0.10986 | -0.13275 | 0.07782 | 62.1552 | -61.2762 | -0.34332 | 0.13275 | -0.13733 | -0.23346 | -0.32043 | -0.33875 | 0.077819 | 0.20599 | 60.8047 | 61.0153 | 122.6944 | 123.1476 | -0.13733 | 123.0927 | 60.8276 | -0.33875 | 123.1476 | -0.13733 | 60.8276 | 122.6944 | 123.0927 | -123.3582 | -123.3536
3258.7812 | 123.23 | -60.8963 | 62.0132 | 0.20195 | -0.005866 | -0.013052 | 0.0015658 | 0.057542 | -0.0043685 | 0.063779 | -61.0291 | 62.1368 | -61.2442 | -61.1252 | 61.8393 | -0.018311 | -0.24261 | 0.17395 | 62.0819 | -61.2488 | -0.3479 | 0.1236 | -0.13275 | -0.22888 | -0.17395 | -0.35248 | 0.068664 | 0.21515 | 60.6537 | 61.0703 | 122.7356 | 123.0331 | -0.13275 | 122.9782 | 60.878 | -0.35248 | 123.0331 | -0.13275 | 60.878 | 122.7356 | 122.9782 | -123.2574 | -123.262
3259.7656 | 123.143 | -60.9238 | 62.0728 | -0.04219 | -0.0069342 | -0.011771 | 0.0069064 | 0.060746 | -0.0062911 | 0.065488 | -61.0428 | 62.1689 | -61.2717 | -61.203 | 61.7477 | -0.11902 | -0.091553 | 0.07782 | 62.146 | -61.2579 | -0.3479 | 0.09613 | -0.11902 | -0.27924 | -0.32501 | -0.33417 | 0.073242 | 0.22888 | 60.8322 | 61.0016 | 122.6715 | 123.0927 | -0.11902 | 123.0698 | 60.8047 | -0.33417 | 123.0927 | -0.11902 | 60.8047 | 122.6715 | 123.0698 | -123.3444 | -123.3307
3260.2969 | 123.2025 | -60.8826 | 62.0773 | -0.149 | -0.0097114 | -0.013693 | -0.00035676 | 0.059037 | -0.0088547 | 0.065916 | -61.0199 | 62.1414 | -61.2259 | -61.084 | 61.8851 | 0.082397 | -0.064087 | 0.28839 | 62.146 | -61.1481 | -0.34332 | 0.064086 | -0.13733 | -0.20142 | -0.19226 | -0.2655 | 0.068664 | 0.20599 | 60.8185 | 61.171 | 122.7676 | 123.024 | -0.13733 | 123.0286 | 60.965 | -0.2655 | 123.024 | -0.13733 | 60.965 | 122.7676 | 123.0286 | -123.3032 | -123.2254
3261.2188 | 123.262 | -60.8826 | 62.0819 | -0.11085 | -0.011207 | -0.014975 | -0.0022794 | 0.058823 | -0.0047957 | 0.065702 | -60.997 | 62.114 | -61.2167 | -61.0519 | 61.9125 | 0.09613 | -0.16022 | 0.34332 | 62.0911 | -61.1664 | -0.33417 | 0.032044 | -0.11444 | -0.16937 | -0.16937 | -0.28381 | 0.009155 | 0.21973 | 60.7224 | 61.2259 | 122.7951 | 122.9965 | -0.11444 | 122.9736 | 60.9787 | -0.28381 | 122.9965 | -0.11444 | 60.9787 | 122.7951 | 122.9736 | -123.2986 | -123.2483
3265.5781 | 123.2346 | -60.9055 | 61.9858 | 0.28587 | -0.0080024 | -0.0094207 | 0.0045566 | 0.059678 | -0.0075729 | 0.064847 | -60.9879 | 62.1231 | -61.2488 | -61.1069 | 61.8439 | -0.032043 | -0.29297 | 0.17395 | 62.0911 | -61.203 | -0.34332 | 0.13733 | -0.082397 | -0.20142 | -0.14191 | -0.29755 | 0.10529 | 0.26093 | 60.6125 | 61.0794 | 122.7493 | 123.0286 | -0.082397 | 122.9965 | 60.8734 | -0.29755 | 123.0286 | -0.082397 | 60.8734 | 122.7493 | 122.9965 | -123.2346 | -123.1888
3266.0781 | 123.1842 | -60.91 | 62.0407 | 0.14092 | -0.0077888 | -0.012198 | -0.0022794 | 0.057114 | -0.0062911 | 0.065488 | -61.0611 | 62.1048 | -61.2396 | -61.116 | 61.8256 | -0.027466 | -0.1831 | 0.17853 | 62.1094 | -61.203 | -0.32959 | 0.064087 | -0.15106 | -0.20599 | -0.21515 | -0.29297 | 0.068665 | 0.17853 | 60.7269 | 61.0886 | 122.7356 | 123.0148 | -0.15106 | 123.0194 | 60.8826 | -0.29297 | 123.0148 | -0.15106 | 60.8826 | 122.7356 | 123.0194 | -123.2803 | -123.2437
3266.7656 | 123.1796 | -60.9146 | 62.0407 | 0.1638 | -0.0086432 | -0.013266 | -0.00014316 | 0.059037 | -0.0067185 | 0.065061 | -61.0703 | 62.1185 | -61.2534 | -61.1526 | 61.8027 | -0.050354 | -0.18768 | 0.18768 | 62.1002 | -61.1984 | -0.33875 | 0.07782 | -0.15564 | -0.23804 | -0.23804 | -0.28381 | 0.05951 | 0.18311 | 60.7269 | 61.1023 | 122.7173 | 123.0331 | -0.15564 | 123.0148 | 60.8643 | -0.28381 | 123.0331 | -0.15564 | 60.8643 | 122.7173 | 123.0148 | -123.2941 | -123.2391
3267.7656 | 123.2483 | -60.8688 | 62.0544 | -0.080337 | -0.011634 | -0.016043 | -0.00035676 | 0.055405 | -0.0060775 | 0.067197 | -61.0199 | 62.1048 | -61.2076 | -61.084 | 61.8851 | 0.054932 | -0.16022 | 0.30212 | 62.1185 | -61.1801 | -0.33875 | 0.050354 | -0.15106 | -0.21515 | -0.16937 | -0.31128 | 0.064087 | 0.18768 | 60.7086 | 61.171 | 122.7539 | 122.9736 | -0.15106 | 122.9874 | 60.9238 | -0.31128 | 122.9736 | -0.15106 | 60.9238 | 122.7539 | 122.9874 | -123.262 | -123.2346
3268.7656 | 123.2162 | -60.8963 | 62.0407 | 0.22484 | -0.010779 | -0.012625 | 0.0022066 | 0.05626 | -0.0039413 | 0.066984 | -61.0382 | 62.0911 | -61.2488 | -61.1206 | 61.8301 | -0.027466 | -0.25635 | 0.19684 | 62.0773 | -61.203 | -0.35248 | 0.050354 | -0.14191 | -0.2243 | -0.21057 | -0.3067 | 0.036622 | 0.21057 | 60.64 | 61.0931 | 122.7264 | 122.9874 | -0.14191 | 122.9736 | 60.8688 | -0.3067 | 122.9874 | -0.14191 | 60.8688 | 122.7264 | 122.9736 | -123.2895 | -123.2437
3269.7656 | 123.2391 | -60.8871 | 62.0316 | 0.22484 | -0.0067206 | -0.013693 | 0.004343 | 0.056901 | -0.0056503 | 0.061216 | -61.0153 | 62.0956 | -61.2625 | -61.1023 | 61.8301 | -0.036621 | -0.27924 | 0.19684 | 62.0499 | -61.2076 | -0.37537 | 0.064087 | -0.12817 | -0.21515 | -0.20142 | -0.32043 | 0.018311 | 0.24719 | 60.6079 | 61.084 | 122.7173 | 122.9828 | -0.12817 | 122.937 | 60.8505 | -0.32043 | 122.9828 | -0.12817 | 60.8505 | 122.7173 | 122.937 | -123.2941 | -123.2391
3270.7656 | 123.2208 | -60.8917 | 62.0316 | 0.23247 | -0.0086432 | -0.013266 | 0.0030612 | 0.057755 | -0.0065047 | 0.065702 | -61.0474 | 62.0819 | -61.235 | -61.1252 | 61.8118 | -0.045776 | -0.21973 | 0.16937 | 62.0865 | -61.1801 | -0.34332 | 0.050354 | -0.15564 | -0.23346 | -0.21973 | -0.28839 | 0.054932 | 0.18768 | 60.672 | 61.0611 | 122.7036 | 122.9736 | -0.15564 | 122.9782 | 60.8459 | -0.28839 | 122.9736 | -0.15564 | 60.8459 | 122.7036 | 122.9782 | -123.2666 | -123.2117
3271.7656 | 123.2346 | -60.8826 | 62.0316 | 0.20958 | -0.009284 | -0.0094207 | 0.0034884 | 0.057755 | -0.0039413 | 0.065916 | -61.0245 | 62.1048 | -61.235 | -61.1114 | 61.8301 | -0.027466 | -0.26093 | 0.20142 | 62.0819 | -61.2122 | -0.35248 | 0.073242 | -0.14191 | -0.22888 | -0.20142 | -0.32959 | 0.050354 | 0.21057 | 60.6216 | 61.084 | 122.7127 | 122.9874 | -0.14191 | 122.9645 | 60.8551 | -0.32959 | 122.9874 | -0.14191 | 60.8551 | 122.7127 | 122.9645 | -123.2666 | -123.2437
3272.7812 | 123.2071 | -60.9146 | 62.0316 | 0.15617 | -0.009925 | -0.013907 | -0.00057036 | 0.055405 | -0.0069321 | 0.066129 | -61.0611 | 62.1185 | -61.2259 | -61.1206 | 61.8301 | -0.045776 | -0.21973 | 0.17395 | 62.0956 | -61.2122 | -0.31128 | 0.086975 | -0.14648 | -0.20599 | -0.20142 | -0.29755 | 0.064087 | 0.16479 | 60.6949 | 61.0886 | 122.7448 | 123.0331 | -0.14648 | 123.0103 | 60.8688 | -0.29755 | 123.0331 | -0.14648 | 60.8688 | 122.7448 | 123.0103 | -123.2574 | -123.2437
3273.7656 | 123.2254 | -60.9055 | 62.0544 | 0.11803 | -0.0080024 | -0.012198 | -0.00078396 | 0.057114 | -0.0041549 | 0.066556 | -61.0794 | 62.1231 | -61.2534 | -61.1069 | 61.8393 | -0.018311 | -0.15106 | 0.20142 | 62.0865 | -61.2076 | -0.3479 | 0.068665 | -0.17395 | -0.20142 | -0.21515 | -0.30212 | 0.032044 | 0.17395 | 60.7544 | 61.1069 | 122.7448 | 123.0286 | -0.17395 | 122.9919 | 60.8871 | -0.30212 | 123.0286 | -0.17395 | 60.8871 | 122.7448 | 122.9919 | -123.3078 | -123.262
3274.7656 | 123.2071 | -60.8826 | 62.0453 | 0.12566 | -0.0094976 | -0.019675 | 0.00071144 | 0.055405 | -0.0062911 | 0.066984 | -60.8871 | 62.1414 | -61.2167 | -61.1206 | 61.8439 | -0.018311 | -0.18768 | 0.17853 | 62.0911 | -61.1984 | -0.33417 | 0.09613 | -0.004578 | -0.23804 | -0.20142 | -0.31586 | 0.045776 | 0.32959 | 60.6949 | 61.0611 | 122.7264 | 123.024 | -0.004578 | 122.9736 | 60.8643 | -0.31586 | 123.024 | -0.004578 | 60.8643 | 122.7264 | 122.9736 | -123.262 | -123.2437
3275.7656 | 123.2483 | -60.8734 | 62.0544 | 0.27061 | -0.008216 | -0.012625 | 0.0051974 | 0.059037 | -0.0065047 | 0.065916 | -60.9833 | 62.1185 | -61.2534 | -61.1481 | 61.6013 | -0.082397 | -0.1831 | 0.25177 | 62.027 | -61.1847 | -0.37994 | 0.064087 | -0.10986 | -0.27466 | -0.45319 | -0.31128 | -0.027465 | 0.27008 | 60.6903 | 61.1252 | 122.4747 | 122.9919 | -0.10986 | 122.9004 | 60.791 | -0.31128 | 122.9919 | -0.10986 | 60.791 | 122.4747 | 122.9004 | -123.3078 | -123.2391
3276.7656 | 123.2574 | -60.91 | 62.0132 | 0.17906 | -0.0067206 | -0.010062 | 0.0051974 | 0.058182 | -0.0067185 | 0.065275 | -60.997 | 62.1185 | -61.2442 | -61.084 | 61.853 | -0.022888 | -0.28839 | 0.17853 | 62.0728 | -61.2259 | -0.33417 | 0.10529 | -0.086975 | -0.17395 | -0.16022 | -0.31586 | 0.059509 | 0.24719 | 60.6216 | 61.0886 | 122.7631 | 123.0286 | -0.086975 | 122.9828 | 60.8871 | -0.31586 | 123.0286 | -0.086975 | 60.8871 | 122.7631 | 122.9828 | -123.2574 | -123.2391
3277.7812 | 123.2071 | -60.8643 | 62.0224 | 0.1638 | -0.0088568 | -0.012625 | 0.00049764 | 0.05861 | -0.0056503 | 0.066556 | -61.0886 | 62.1368 | -61.2488 | -61.1298 | 61.8256 | -0.036621 | -0.19684 | 0.16937 | 62.0956 | -61.2076 | -0.38452 | 0.11444 | -0.2243 | -0.2655 | -0.19684 | -0.34332 | 0.073242 | 0.16022 | 60.6674 | 61.0336 | 122.6898 | 123.0011 | -0.2243 | 122.9599 | 60.8276 | -0.34332 | 123.0011 | -0.2243 | 60.8276 | 122.6898 | 122.9599 | -123.2712 | -123.23
3278.7656 | 123.2712 | -60.8963 | 62.0453 | 0.25536 | -0.009284 | -0.012198 | 0.0051974 | 0.060532 | -0.0043685 | 0.06677 | -60.9879 | 62.1323 | -61.2534 | -61.0245 | 61.9492 | 0.059509 | -0.2655 | 0.2243 | 62.0682 | -61.1984 | -0.35706 | 0.086975 | -0.091553 | -0.12817 | -0.09613 | -0.30212 | 0.022888 | 0.2655 | 60.6308 | 61.1206 | 122.8455 | 123.0286 | -0.091553 | 122.9645 | 60.9558 | -0.30212 | 123.0286 | -0.091553 | 60.9558 | 122.8455 | 122.9645 | -123.2986 | -123.2437
3279.7656 | 123.3536 | -60.8871 | 62.0224 | 0.2401 | -0.0073614 | -0.011984 | 0.0056246 | 0.056687 | -0.0056503 | 0.06442 | -60.9833 | 62.1368 | -61.2259 | -61.0794 | 61.8347 | -0.027466 | -0.30212 | 0.18768 | 62.059 | -61.2122 | -0.33874 | 0.11444 | -0.09613 | -0.19226 | -0.18768 | -0.32501 | 0.036621 | 0.24262 | 60.585 | 61.0748 | 122.7219 | 123.024 | -0.09613 | 122.9462 | 60.8597 | -0.32501 | 123.024 | -0.09613 | 60.8597 | 122.7219 | 122.9462 | -123.2483 | -123.2346
3280.7656 | 123.2117 | -60.9009 | 62.0224 | 0.19432 | -0.0084296 | -0.01113 | -0.00035676 | 0.059678 | -0.0039413 | 0.067838 | -61.0519 | 62.1048 | -61.2579 | -61.116 | 61.821 | -0.045776 | -0.18768 | 0.19226 | 62.1048 | -61.1847 | -0.35706 | 0.082397 | -0.15106 | -0.21515 | -0.20142 | -0.28381 | 0.082397 | 0.20599 | 60.7132 | 61.0931 | 122.7219 | 123.0057 | -0.15106 | 123.0057 | 60.8551 | -0.28381 | 123.0057 | -0.15106 | 60.8551 | 122.7219 | 123.0057 | -123.2803 | -123.2071
3281.7656 | 123.1796 | -60.9055 | 62.0499 | 0.20195 | -0.0077888 | -0.014548 | 0.0017794 | 0.056901 | -0.0050095 | 0.064207 | -61.0291 | 62.1414 | -61.2579 | -61.1252 | 61.8118 | -0.050354 | -0.20599 | 0.17853 | 62.0911 | -61.2076 | -0.35248 | 0.091552 | -0.1236 | -0.21973 | -0.23804 | -0.30212 | 0.041198 | 0.22888 | 60.6995 | 61.084 | 122.7173 | 123.0469 | -0.1236 | 122.9965 | 60.8551 | -0.30212 | 123.0469 | -0.1236 | 60.8551 | 122.7173 | 122.9965 | -123.3078 | -123.2574
3282.7812 | 123.23 | -60.8597 | 62.027 | -0.026932 | -0.012275 | -0.011771 | -0.0018522 | 0.056473 | -0.0054367 | 0.066129 | -61.0519 | 62.1094 | -61.2305 | -61.0886 | 61.853 | 0.032043 | -0.16937 | 0.26093 | 62.0956 | -61.1572 | -0.37079 | 0.082397 | -0.19226 | -0.22888 | -0.17395 | -0.29755 | 0.068664 | 0.17853 | 60.6903 | 61.1206 | 122.7127 | 122.9691 | -0.19226 | 122.9553 | 60.8917 | -0.29755 | 122.9691 | -0.19226 | 60.8917 | 122.7127 | 122.9553 | -123.2574 | -123.1842
3283.7656 | 123.175 | -60.91 | 62.0453 | 0.26299 | -0.007575 | -0.010275 | 0.0079744 | 0.06096 | -0.0056503 | 0.065061 | -61.0428 | 62.1689 | -61.2579 | -61.1389 | 61.7706 | -0.086975 | -0.20599 | 0.11902 | 62.0728 | -61.2534 | -0.3479 | 0.1236 | -0.13275 | -0.22888 | -0.27466 | -0.34332 | 0.027466 | 0.21515 | 60.704 | 61.0291 | 122.6807 | 123.0789 | -0.13275 | 122.9828 | 60.8231 | -0.34332 | 123.0789 | -0.13275 | 60.8231 | 122.6807 | 122.9828 | -123.3032 | -123.2986
3284.7656 | 123.2117 | -60.8871 | 62.0087 | 0.27061 | -0.007575 | -0.013907 | 0.0049838 | 0.059037 | -0.0054367 | 0.063566 | -60.9879 | 62.1506 | -61.2442 | -61.0977 | 61.8439 | -0.032043 | -0.27466 | 0.17853 | 62.0773 | -61.2396 | -0.35706 | 0.14191 | -0.10071 | -0.21057 | -0.1648 | -0.35248 | 0.068665 | 0.25635 | 60.6125 | 61.0657 | 122.731 | 123.0377 | -0.10071 | 122.9645 | 60.8551 | -0.35248 | 123.0377 | -0.10071 | 60.8551 | 122.731 | 122.9645 | -123.2529 | -123.2483
3285.7656 | 123.2162 | -60.9055 | 62.0132 | 0.23247 | -0.008216 | -0.015189 | 0.0056246 | 0.058396 | -0.0086411 | 0.065702 | -61.0428 | 62.1735 | -61.2717 | -61.116 | 61.8256 | -0.050354 | -0.23346 | 0.17853 | 62.0911 | -61.235 | -0.36621 | 0.16022 | -0.13733 | -0.21057 | -0.18768 | -0.32959 | 0.077819 | 0.22888 | 60.672 | 61.084 | 122.731 | 123.0789 | -0.13733 | 122.9965 | 60.8551 | -0.32959 | 123.0789 | -0.13733 | 60.8551 | 122.731 | 122.9965 | -123.2849 | -123.2483
3286.7656 | 123.2208 | -60.9055 | 62.0316 | 0.20195 | -0.0054388 | -0.016684 | -0.00035676 | 0.059037 | -0.0056503 | 0.066556 | -61.0336 | 62.1277 | -61.2396 | -61.1206 | 61.8301 | -0.041199 | -0.23346 | 0.1831 | 62.0773 | -61.2122 | -0.33417 | 0.096131 | -0.12817 | -0.21515 | -0.20142 | -0.3067 | 0.045777 | 0.20599 | 60.672 | 61.0886 | 122.7356 | 123.0331 | -0.12817 | 122.9828 | 60.8643 | -0.3067 | 123.0331 | -0.12817 | 60.8643 | 122.7356 | 122.9828 | -123.2712 | -123.2437
3287.7812 | 123.2712 | -60.8688 | 62.0361 | 0.0035856 | -0.0094976 | -0.018179 | -0.0027066 | 0.059037 | -0.0077865 | 0.068052 | -61.0336 | 62.114 | -61.235 | -61.0657 | 61.8851 | 0.050354 | -0.15564 | 0.30212 | 62.1002 | -61.1801 | -0.36621 | 0.07782 | -0.1648 | -0.19684 | -0.15106 | -0.31128 | 0.064087 | 0.20142 | 60.7132 | 61.171 | 122.7539 | 122.9828 | -0.1648 | 122.9691 | 60.9192 | -0.31128 | 122.9828 | -0.1648 | 60.9192 | 122.7539 | 122.9691 | -123.2712 | -123.2162
3288.7656 | 123.1934 | -60.9055 | 62.0132 | 0.20958 | -0.0077888 | -0.012839 | 0.0039156 | 0.059678 | -0.0067185 | 0.066556 | -61.0153 | 62.1277 | -61.2396 | -61.1023 | 61.853 | -0.022888 | -0.27924 | 0.21515 | 62.0361 | -61.235 | -0.33417 | 0.11444 | -0.10986 | -0.19684 | -0.16022 | -0.32959 | 0.022888 | 0.2243 | 60.6262 | 61.1206 | 122.7585 | 123.0331 | -0.10986 | 122.9416 | 60.8826 | -0.32959 | 123.0331 | -0.10986 | 60.8826 | 122.7585 | 122.9416 | -123.2529 | -123.2483
3289.7656 | 123.1567 | -60.9055 | 62.0636 | 0.20195 | -0.0043708 | -0.013693 | 0.0079744 | 0.06096 | -0.0058639 | 0.065061 | -61.0657 | 62.1918 | -61.2625 | -61.1847 | 61.7477 | -0.12817 | -0.16022 | 0.09613 | 62.1231 | -61.2625 | -0.35706 | 0.12817 | -0.16022 | -0.27923 | -0.31586 | -0.35706 | 0.059509 | 0.19684 | 60.7452 | 61.0016 | 122.6532 | 123.0972 | -0.16022 | 123.0286 | 60.7773 | -0.35706 | 123.0972 | -0.16022 | 60.7773 | 122.6532 | 123.0286 | -123.3261 | -123.3261
3290.7656 | 123.1247 | -60.9283 | 62.0316 | 0.18669 | -0.005866 | -0.015189 | 0.0056246 | 0.059037 | -0.0052231 | 0.066343 | -61.0474 | 62.1918 | -61.2808 | -61.1755 | 61.7661 | -0.1236 | -0.13733 | 0.09613 | 62.1414 | -61.2534 | -0.35248 | 0.16022 | -0.11902 | -0.24719 | -0.2655 | -0.32501 | 0.10986 | 0.23346 | 60.791 | 61.0245 | 122.6944 | 123.1201 | -0.11902 | 123.0698 | 60.8047 | -0.32501 | 123.1201 | -0.11902 | 60.8047 | 122.6944 | 123.0698 | -123.3124 | -123.2849
3291.7656 | 123.23 | -60.9192 | 62.0224 | 0.27061 | -0.004798 | -0.015402 | 0.0049838 | 0.059678 | -0.0060775 | 0.064207 | -61.0428 | 62.178 | -61.2717 | -61.1206 | 61.7889 | -0.068665 | -0.23346 | 0.14648 | 62.0636 | -61.2259 | -0.35248 | 0.15564 | -0.1236 | -0.20142 | -0.23346 | -0.3067 | 0.041199 | 0.22888 | 60.6857 | 61.0657 | 122.7081 | 123.0972 | -0.1236 | 122.9828 | 60.8505 | -0.3067 | 123.0972 | -0.1236 | 60.8505 | 122.7081 | 122.9828 | -123.2941 | -123.2483
3292.7812 | 123.1201 | -60.9055 | 62.1094 | -0.149 | -0.0077888 | -0.01647 | 0.0013522 | 0.059037 | -0.0047957 | 0.064847 | -61.0611 | 62.1964 | -61.2396 | -61.1572 | 61.8347 | 0 | 0.041199 | 0.24261 | 62.1506 | -61.1847 | -0.33417 | 0.086975 | -0.15564 | -0.25177 | -0.27466 | -0.27923 | 0.041199 | 0.17853 | 60.9467 | 61.1481 | 122.7402 | 123.1018 | -0.15564 | 123.056 | 60.9055 | -0.27923 | 123.1018 | -0.15564 | 60.9055 | 122.7402 | 123.056 | -123.349 | -123.2941
3293.7656 | 123.2254 | -60.9055 | 62.027 | 0.18669 | -0.0073614 | -0.014121 | 0.0013522 | 0.060532 | -0.0071457 | 0.065275 | -61.0245 | 62.1552 | -61.2213 | -61.116 | 61.8622 | -0.036621 | -0.2655 | 0.20599 | 62.0865 | -61.2167 | -0.31586 | 0.12817 | -0.11902 | -0.21057 | -0.16479 | -0.31128 | 0.059509 | 0.19684 | 60.64 | 61.1115 | 122.7676 | 123.0606 | -0.11902 | 122.9919 | 60.8688 | -0.31128 | 123.0606 | -0.11902 | 60.8688 | 122.7676 | 122.9919 | -123.2483 | -123.2437
3294.7656 | 123.2391 | -60.9192 | 62.0224 | 0.23247 | -0.0090704 | -0.0092071 | 0.0017794 | 0.057542 | -0.0050095 | 0.065702 | -61.0107 | 62.114 | -61.2305 | -61.1114 | 61.8347 | -0.022888 | -0.27008 | 0.19684 | 62.0682 | -61.2305 | -0.31128 | 0.091553 | -0.091553 | -0.19226 | -0.18768 | -0.31128 | 0.045776 | 0.21973 | 60.6491 | 61.116 | 122.7539 | 123.0331 | -0.091553 | 122.9874 | 60.8963 | -0.31128 | 123.0331 | -0.091553 | 60.8963 | 122.7539 | 122.9874 | -123.2529 | -123.2529
3295.7656 | 123.2162 | -60.9009 | 62.0178 | 0.23247 | -0.0084296 | -0.013266 | 0.0030612 | 0.05861 | -0.0067185 | 0.06677 | -61.0062 | 62.1414 | -61.2305 | -61.1069 | 61.8484 | -0.022888 | -0.27466 | 0.21057 | 62.0773 | -61.2167 | -0.32959 | 0.1236 | -0.10529 | -0.20599 | -0.16937 | -0.31586 | 0.05951 | 0.2243 | 60.6262 | 61.1115 | 122.7493 | 123.0423 | -0.10529 | 122.9782 | 60.878 | -0.31586 | 123.0423 | -0.10529 | 60.878 | 122.7493 | 122.9782 | -123.2483 | -123.2346
3296.7812 | 123.2025 | -60.8826 | 62.059 | -0.15663 | -0.010139 | -0.015402 | 0.0011386 | 0.057114 | -0.0058639 | 0.065488 | -61.0062 | 62.1414 | -61.2213 | -61.0703 | 61.8805 | 0.073242 | -0.064087 | 0.32044 | 62.1368 | -61.171 | -0.33875 | 0.082397 | -0.1236 | -0.18768 | -0.17853 | -0.28839 | 0.07782 | 0.21515 | 60.8185 | 61.203 | 122.7631 | 123.024 | -0.1236 | 123.0194 | 60.9558 | -0.28839 | 123.024 | -0.1236 | 60.9558 | 122.7631 | 123.0194 | -123.2803 | -123.23
3297.7812 | 123.2071 | -60.8871 | 62.0819 | -0.16426 | -0.009925 | -0.012625 | 0.004343 | 0.055192 | -0.0069321 | 0.065061 | -60.9879 | 62.1506 | -61.2122 | -61.0474 | 61.8896 | 0.07782 | -0.091553 | 0.32959 | 62.1094 | -61.2122 | -0.32501 | 0.068665 | -0.10071 | -0.16022 | -0.19226 | -0.32501 | 0.027466 | 0.2243 | 60.7956 | 61.2167 | 122.7768 | 123.0377 | -0.10071 | 122.9965 | 60.965 | -0.32501 | 123.0377 | -0.10071 | 60.965 | 122.7768 | 122.9965 | -123.2941 | -123.2941
3298.7656 | 123.1567 | -60.9055 | 62.059 | 0.21721 | -0.0052252 | -0.010916 | 0.00712 | 0.058823 | -0.0041549 | 0.064847 | -61.0611 | 62.2421 | -61.2854 | -61.1847 | 61.7523 | -0.11902 | -0.16022 | 0.10529 | 62.0911 | -61.2671 | -0.37994 | 0.1831 | -0.15564 | -0.27923 | -0.3067 | -0.36163 | 0.032043 | 0.2243 | 60.7452 | 61.0107 | 122.6578 | 123.1476 | -0.15564 | 122.9965 | 60.7864 | -0.36163 | 123.1476 | -0.15564 | 60.7864 | 122.6578 | 122.9965 | -123.3444 | -123.3261
3299.7656 | 123.1476 | -60.9467 | 62.0453 | 0.17143 | -0.0060798 | -0.010916 | 0.0086154 | 0.060746 | -0.0041549 | 0.065916 | -61.0657 | 62.2009 | -61.2717 | -61.1801 | 61.7569 | -0.10529 | -0.12817 | 0.073242 | 62.146 | -61.2717 | -0.32501 | 0.15564 | -0.11902 | -0.23346 | -0.28839 | -0.32501 | 0.10071 | 0.20599 | 60.8185 | 61.0199 | 122.7036 | 123.1476 | -0.11902 | 123.0927 | 60.8414 | -0.32501 | 123.1476 | -0.11902 | 60.8414 | 122.7036 | 123.0927 | -123.317 | -123.317
3300.7656 | 123.2346 | -60.9009 | 62.0316 | 0.4995 | -0.0071478 | -0.012198 | 0.005411 | 0.060319 | -0.0033005 | 0.06442 | -60.91 | 62.146 | -61.1984 | -61.0794 | 61.8576 | -0.032043 | -0.30212 | 0.20142 | 62.114 | -61.2442 | -0.29755 | 0.11444 | -0.009155 | -0.17853 | -0.17395 | -0.34332 | 0.082398 | 0.28839 | 60.5988 | 61.1023 | 122.7585 | 123.0469 | -0.009155 | 123.0148 | 60.8688 | -0.34332 | 123.0469 | -0.009155 | 60.8688 | 122.7585 | 123.0148 | -123.23 | -123.2758
3301.7812 | 123.2346 | -60.8734 | 62.059 | 0.17906 | -0.0094976 | -0.014761 | -0.0020658 | 0.058182 | -0.0050095 | 0.065061 | -61.0886 | 62.1185 | -61.235 | -61.1298 | 61.8347 | -0.032043 | -0.17395 | 0.22888 | 62.1002 | -61.1984 | -0.36163 | 0.059509 | -0.21515 | -0.25635 | -0.2243 | -0.32501 | 0.041199 | 0.14648 | 60.6995 | 61.1023 | 122.7081 | 122.9919 | -0.21515 | 122.9736 | 60.8414 | -0.32501 | 122.9919 | -0.21515 | 60.8414 | 122.7081 | 122.9736 | -123.2941 | -123.2574
3302.7812 | 123.1796 | -60.91 | 62.1048 | -0.13374 | -0.0077888 | -0.01348 | 0.0075472 | 0.058182 | -0.0060775 | 0.063779 | -61.0199 | 62.233 | -61.235 | -61.1023 | 61.8301 | 0.004578 | -0.018311 | 0.23804 | 62.1506 | -61.2305 | -0.32501 | 0.12817 | -0.10986 | -0.19226 | -0.27466 | -0.32043 | 0.045777 | 0.21515 | 60.8917 | 61.1481 | 122.7402 | 123.143 | -0.10986 | 123.0606 | 60.9146 | -0.32043 | 123.143 | -0.10986 | 60.9146 | 122.7402 | 123.0606 | -123.3398 | -123.3353
3303.7656 | 123.1201 | -60.91 | 62.0819 | 0.11803 | -0.0060798 | -0.011557 | 0.0090426 | 0.057755 | -0.0056503 | 0.065061 | -61.0519 | 62.2284 | -61.2671 | -61.1984 | 61.7249 | -0.15106 | -0.059509 | 0.09613 | 62.1277 | -61.2762 | -0.35706 | 0.14648 | -0.14191 | -0.28839 | -0.35706 | -0.36621 | 0.045777 | 0.21515 | 60.8505 | 61.0062 | 122.6349 | 123.1384 | -0.14191 | 123.0377 | 60.759 | -0.36621 | 123.1384 | -0.14191 | 60.759 | 122.6349 | 123.0377 | -123.349 | -123.3582
3304.7656 | 123.111 | -60.9146 | 62.059 | 0.12566 | -0.0054388 | -0.0040801 | 0.0060518 | 0.061387 | -0.0058639 | 0.064847 | -61.0382 | 62.233 | -61.2717 | -61.1755 | 61.7706 | -0.09613 | -0.068665 | 0.10986 | 62.1643 | -61.2488 | -0.35706 | 0.17395 | -0.1236 | -0.26093 | -0.28839 | -0.33417 | 0.10529 | 0.23346 | 60.8459 | 61.0245 | 122.6852 | 123.1476 | -0.1236 | 123.0789 | 60.8185 | -0.33417 | 123.1476 | -0.1236 | 60.8185 | 122.6852 | 123.0789 | -123.3307 | -123.3078
3305.7812 | 123.2483 | -60.9238 | 62.027 | 0.21721 | -0.0071478 | -0.012839 | 0.0032748 | 0.061814 | -0.0045821 | 0.065061 | -60.9924 | 62.1323 | -61.2808 | -61.1069 | 61.8484 | 0.082397 | -0.56305 | 0.1831 | 62.0682 | -61.2076 | -0.35706 | 0.10529 | -0.068665 | -0.18311 | -0.17853 | -0.28381 | 0.041198 | 0.28839 | 60.3607 | 61.1069 | 122.7722 | 123.056 | -0.068665 | 122.9919 | 61.0062 | -0.28381 | 123.056 | -0.068665 | 61.0062 | 122.7722 | 122.9919 | -123.3078 | -123.2346
3306.7812 | 123.2346 | -60.8643 | 62.0544 | 0.041733 | -0.009284 | -0.012839 | -0.002493 | 0.059678 | -0.0071457 | 0.06677 | -61.0657 | 62.146 | -61.2488 | -61.1298 | 61.8484 | -0.004578 | -0.16022 | 0.25177 | 62.1277 | -61.1847 | -0.38452 | 0.091553 | -0.20142 | -0.2655 | -0.20599 | -0.32043 | 0.073243 | 0.1831 | 60.704 | 61.116 | 122.7127 | 123.0103 | -0.20142 | 122.9919 | 60.8597 | -0.32043 | 123.0103 | -0.20142 | 60.8597 | 122.7127 | 122.9919 | -123.3032 | -123.2391
3307.7969 | 123.1201 | -60.9375 | 62.0544 | -0.37025 | -0.0039434 | -0.012839 | 0.0069064 | 0.059891 | -0.0026595 | 0.064847 | -61.0382 | 62.2192 | -61.2534 | -61.2259 | 61.7661 | -0.12817 | -0.10529 | 0.082397 | 62.114 | -61.2717 | -0.31586 | 0.16479 | -0.10071 | -0.28839 | -0.28839 | -0.33417 | 0.05951 | 0.21515 | 60.8322 | 61.0199 | 122.7036 | 123.1567 | -0.10071 | 123.0515 | 60.8093 | -0.33417 | 123.1567 | -0.10071 | 60.8093 | 122.7036 | 123.0515 | -123.3078 | -123.3261
3308.7812 | 123.2208 | -60.9055 | 62.0041 | 0.2401 | -0.0056524 | -0.0085663 | 0.0041292 | 0.061814 | -0.0047957 | 0.066343 | -61.0245 | 62.1643 | -61.2534 | -61.1435 | 61.7935 | -0.07782 | -0.23346 | 0.16937 | 62.1094 | -61.235 | -0.3479 | 0.16022 | -0.11902 | -0.23804 | -0.21057 | -0.32959 | 0.10529 | 0.22888 | 60.672 | 61.0748 | 122.699 | 123.0698 | -0.11902 | 123.0148 | 60.8276 | -0.32959 | 123.0698 | -0.11902 | 60.8276 | 122.699 | 123.0148 | -123.2574 | -123.2391
3309.7812 | 123.1888 | -60.9055 | 62.027 | 0.20195 | -0.0094976 | -0.011557 | -0.001425 | 0.060746 | -0.0047957 | 0.065916 | -61.0657 | 62.1323 | -61.2534 | -61.1435 | 61.8164 | -0.054932 | -0.21515 | 0.17395 | 62.1277 | -61.2076 | -0.3479 | 0.10529 | -0.16022 | -0.23804 | -0.21057 | -0.30212 | 0.10071 | 0.18768 | 60.6903 | 61.0794 | 122.7219 | 123.0377 | -0.16022 | 123.0331 | 60.8505 | -0.30212 | 123.0377 | -0.16022 | 60.8505 | 122.7219 | 123.0331 | -123.2803 | -123.2346
3310.7812 | 123.2437 | -60.8963 | 62.0178 | 0.24773 | -0.004798 | -0.016043 | 0.0047702 | 0.059464 | -0.0062911 | 0.06677 | -60.997 | 62.1368 | -61.2671 | -61.1069 | 61.8301 | -0.036621 | -0.28381 | 0.19226 | 62.114 | -61.2167 | -0.37079 | 0.11902 | -0.10071 | -0.21057 | -0.18768 | -0.32043 | 0.096131 | 0.27008 | 60.6125 | 61.0886 | 122.7264 | 123.0331 | -0.10071 | 123.0103 | 60.8597 | -0.32043 | 123.0331 | -0.10071 | 60.8597 | 122.7264 | 123.0103 | -123.2849 | -123.2346
3311.7812 | 123.1613 | -60.8963 | 62.1414 | -0.18715 | -0.0056524 | -0.016257 | 0.0013522 | 0.05861 | -0.0052231 | 0.064847 | -61.0794 | 62.1735 | -61.2854 | -61.1526 | 61.8118 | -0.027466 | 0.050354 | 0.23346 | 62.2009 | -61.2076 | -0.3891 | 0.032044 | -0.18311 | -0.25635 | -0.32959 | -0.31128 | 0.05951 | 0.20599 | 60.9467 | 61.1298 | 122.7081 | 123.0698 | -0.18311 | 123.0972 | 60.8688 | -0.31128 | 123.0698 | -0.18311 | 60.8688 | 122.7081 | 123.0972 | -123.4268 | -123.349
3312.7969 | 123.2437 | -60.8871 | 62.0132 | 0.26299 | -0.0084296 | -0.014761 | 0.0028476 | 0.059037 | -0.0067185 | 0.065061 | -61.0062 | 62.1185 | -61.2396 | -61.1069 | 61.8668 | -0.013733 | -0.27924 | 0.21515 | 62.0911 | -61.1847 | -0.35248 | 0.10529 | -0.11902 | -0.21973 | -0.14648 | -0.29755 | 0.077819 | 0.23346 | 60.6079 | 61.1023 | 122.7539 | 123.0057 | -0.11902 | 122.9782 | 60.8734 | -0.29755 | 123.0057 | -0.11902 | 60.8734 | 122.7539 | 122.9782 | -123.2529 | -123.1979
3313.7812 | 123.2346 | -60.9055 | 61.9904 | 0.52238 | -0.0071478 | -0.01113 | 0.0049838 | 0.058823 | -0.0056503 | 0.065275 | -60.9695 | 62.146 | -61.2579 | -61.116 | 61.8393 | -0.036621 | -0.29297 | 0.21057 | 62.0911 | -61.235 | -0.35248 | 0.15564 | -0.064086 | -0.21057 | -0.15106 | -0.32959 | 0.10071 | 0.28839 | 60.6125 | 61.116 | 122.7448 | 123.0515 | -0.064086 | 122.9965 | 60.8688 | -0.32959 | 123.0515 | -0.064086 | 60.8688 | 122.7448 | 122.9965 | -123.2483 | -123.2254
3314.7812 | 123.2574 | -60.8963 | 62.0316 | -0.59914 | -0.0086432 | -0.010062 | 0.003702 | 0.06096 | -0.0071457 | 0.067197 | -60.9421 | 62.1277 | -61.235 | -61.1023 | 61.8301 | -0.041199 | -0.3067 | 0.22888 | 62.1002 | -61.1847 | -0.33874 | 0.096131 | -0.045777 | -0.20599 | -0.20142 | -0.28839 | 0.068665 | 0.29297 | 60.5896 | 61.1252 | 122.7264 | 123.024 | -0.045777 | 122.9965 | 60.8551 | -0.28839 | 123.024 | -0.045777 | 60.8551 | 122.7264 | 122.9965 | -123.2666 | -123.2162
3315.7812 | 123.1979 | -60.9009 | 62.0544 | 0.83519 | -0.0086432 | -0.016257 | -0.0018522 | 0.058182 | -0.0075729 | 0.068265 | -61.116 | 62.114 | -61.2534 | -61.1343 | 61.821 | -0.041199 | -0.17395 | 0.21057 | 62.1002 | -61.1938 | -0.35248 | 0.05951 | -0.21515 | -0.23346 | -0.23346 | -0.29297 | 0.045777 | 0.13733 | 60.7269 | 61.1115 | 122.7219 | 123.0148 | -0.21515 | 123.0011 | 60.8597 | -0.29297 | 123.0148 | -0.21515 | 60.8597 | 122.7219 | 123.0011 | -123.3078 | -123.2483
3316.7812 | 123.2391 | -60.8688 | 62.0316 | 0.23247 | -0.008216 | -0.013907 | 0.0039156 | 0.059678 | -0.0088547 | 0.065702 | -61.0062 | 62.0956 | -61.2442 | -61.1069 | 61.8439 | -0.050354 | -0.28381 | 0.20142 | 62.1002 | -61.2076 | -0.37537 | 0.064087 | -0.13733 | -0.23804 | -0.18768 | -0.33875 | 0.068665 | 0.23804 | 60.585 | 61.0703 | 122.7127 | 122.9645 | -0.13733 | 122.9691 | 60.8185 | -0.33875 | 122.9645 | -0.13733 | 60.8185 | 122.7127 | 122.9691 | -123.2758 | -123.2391
3317.7969 | 123.2117 | -60.8734 | 62.027 | 0.22484 | -0.0090704 | -0.013052 | 0.0039156 | 0.057969 | -0.0058639 | 0.065916 | -61.0016 | 62.1094 | -61.2488 | -61.1069 | 61.8256 | -0.041199 | -0.27924 | 0.20599 | 62.0773 | -61.2122 | -0.37537 | 0.082397 | -0.12817 | -0.23346 | -0.20142 | -0.33875 | 0.050354 | 0.24719 | 60.5942 | 61.0794 | 122.699 | 122.9828 | -0.12817 | 122.9507 | 60.8322 | -0.33875 | 122.9828 | -0.12817 | 60.8322 | 122.699 | 122.9507 | -123.2758 | -123.2391
3318.7812 | 123.2254 | -60.9055 | 62.0499 | 0.20958 | -0.0094976 | -0.011771 | 0.0013522 | 0.058396 | -0.0067185 | 0.064847 | -61.0382 | 62.114 | -61.2671 | -61.1114 | 61.8301 | -0.045776 | -0.26093 | 0.20599 | 62.1094 | -61.1984 | -0.36163 | 0.064087 | -0.13275 | -0.20599 | -0.21973 | -0.29297 | 0.059509 | 0.22888 | 60.6445 | 61.1115 | 122.7356 | 123.0194 | -0.13275 | 123.0148 | 60.8597 | -0.29297 | 123.0194 | -0.13275 | 60.8597 | 122.7356 | 123.0148 | -123.317 | -123.2483
3319.7812 | 123.1796 | -60.8688 | 62.0956 | -0.17189 | -0.0073614 | -0.01113 | 0.0056246 | 0.056901 | -0.0058639 | 0.065061 | -61.0016 | 62.1552 | -61.2122 | -61.1069 | 61.853 | 0.018311 | -0.022888 | 0.29297 | 62.1506 | -61.2259 | -0.34332 | 0.059509 | -0.13275 | -0.23804 | -0.24262 | -0.35706 | 0.054932 | 0.21057 | 60.8459 | 61.1618 | 122.7219 | 123.024 | -0.13275 | 123.0194 | 60.8871 | -0.35706 | 123.024 | -0.13275 | 60.8871 | 122.7219 | 123.0194 | -123.3078 | -123.3215
3320.7812 | 123.2529 | -60.8643 | 62.0773 | -0.0040434 | -0.010779 | -0.01348 | -0.00035676 | 0.055833 | -0.0067185 | 0.067411 | -61.0474 | 62.1277 | -61.2442 | -61.1114 | 61.8393 | 0 | -0.16937 | 0.27466 | 62.0911 | -61.1618 | -0.37994 | 0.050354 | -0.1831 | -0.24719 | -0.23804 | -0.29755 | 0.013732 | 0.19684 | 60.6949 | 61.1389 | 122.7036 | 122.9919 | -0.1831 | 122.9553 | 60.8643 | -0.29755 | 122.9919 | -0.1831 | 60.8643 | 122.7036 | 122.9553 | -123.3215 | -123.2391
3321.7812 | 123.2666 | -60.8597 | 62.0361 | -0.026932 | -0.010352 | -0.018179 | 7.0444e-05 | 0.054978 | -0.0065047 | 0.065275 | -61.0153 | 62.1094 | -61.2488 | -61.0611 | 61.8942 | 0.064087 | -0.17853 | 0.32959 | 62.0819 | -61.1572 | -0.3891 | 0.073242 | -0.15564 | -0.20142 | -0.14191 | -0.29755 | 0.045776 | 0.23346 | 60.6812 | 61.1893 | 122.7539 | 122.9691 | -0.15564 | 122.9416 | 60.9238 | -0.29755 | 122.9691 | -0.15564 | 60.9238 | 122.7539 | 122.9416 | -123.2849 | -123.1934
3322.7969 | 123.2437 | -60.8963 | 62.0407 | 0.27061 | -0.0097114 | -0.012412 | 0.0060518 | 0.060532 | -0.0071457 | 0.063779 | -60.9604 | 62.1231 | -61.2122 | -61.0931 | 61.8759 | -0.1236 | -0.45319 | 0.32501 | 62.0636 | -61.2305 | -0.31586 | 0.082398 | -0.064087 | -0.19684 | -0.16479 | -0.33417 | 0.022889 | 0.25177 | 60.4431 | 61.2213 | 122.7722 | 123.0194 | -0.064087 | 122.9599 | 60.7727 | -0.33417 | 123.0194 | -0.064087 | 60.7727 | 122.7722 | 122.9599 | -123.2529 | -123.2712
3323.7812 | 123.1796 | -60.9009 | 62.0636 | 0.087509 | -0.010566 | -0.019247 | 7.0444e-05 | 0.056901 | -0.0050095 | 0.065488 | -61.0657 | 62.0956 | -61.2625 | -61.1252 | 61.7981 | -0.054932 | -0.19684 | 0.19684 | 62.1094 | -61.2076 | -0.36163 | 0.032043 | -0.16479 | -0.2243 | -0.2655 | -0.3067 | 0.045776 | 0.19684 | 60.704 | 61.0977 | 122.699 | 122.9965 | -0.16479 | 123.0103 | 60.8459 | -0.3067 | 122.9965 | -0.16479 | 60.8459 | 122.699 | 123.0103 | -123.3261 | -123.2712
3324.7812 | 123.2025 | -60.8826 | 62.0087 | 0.26299 | -0.0077888 | -0.0094207 | 0.0030612 | 0.058396 | -0.0058639 | 0.065488 | -61.1893 | 62.0911 | -61.2625 | -61.0794 | 61.8484 | -0.041199 | -0.29755 | 0.21057 | 62.059 | -61.2396 | -0.37994 | 0.082397 | -0.3067 | -0.19684 | -0.16022 | -0.35706 | 0.050354 | 0.073242 | 60.585 | 61.0931 | 122.731 | 122.9736 | -0.3067 | 122.9416 | 60.8414 | -0.35706 | 122.9736 | -0.3067 | 60.8414 | 122.731 | 122.9416 | -123.2712 | -123.2483
3325.7812 | 123.2025 | -60.9009 | 62.0316 | 0.10277 | -0.011207 | -0.0098479 | 0.0017794 | 0.057542 | -0.0043685 | 0.067838 | -60.9238 | 62.1826 | -61.2305 | -61.1206 | 61.8347 | -0.064087 | -0.17853 | 0.21515 | 62.0956 | -61.2122 | -0.32959 | 0.15106 | -0.022888 | -0.21973 | -0.19684 | -0.31128 | 0.064087 | 0.3067 | 60.7224 | 61.116 | 122.7356 | 123.0835 | -0.022888 | 122.9965 | 60.8368 | -0.31128 | 123.0835 | -0.022888 | 60.8368 | 122.7356 | 122.9965 | -123.262 | -123.2437
3326.7812 | 123.1979 | -60.878 | 62.027 | 0.20958 | -0.0073614 | -0.013693 | 0.0013522 | 0.054551 | -0.0069321 | 0.064634 | -61.0382 | 62.1048 | -61.235 | -61.1343 | 61.821 | -0.068665 | -0.21973 | 0.18768 | 62.0819 | -61.2259 | -0.35705 | 0.077819 | -0.16022 | -0.25635 | -0.20599 | -0.3479 | 0.054931 | 0.19684 | 60.6583 | 61.0657 | 122.699 | 122.9828 | -0.16022 | 122.9599 | 60.8093 | -0.3479 | 122.9828 | -0.16022 | 60.8093 | 122.699 | 122.9599 | -123.262 | -123.2529
3327.7969 | 123.23 | -60.8963 | 62.0361 | 0.21721 | -0.010139 | -0.013052 | 0.001993 | 0.060532 | -0.0069321 | 0.065488 | -61.0016 | 62.0636 | -61.2488 | -61.0977 | 61.8256 | -0.036621 | -0.28839 | 0.20599 | 62.0728 | -61.2122 | -0.35248 | 0.027466 | -0.10529 | -0.20142 | -0.21057 | -0.31586 | 0.036621 | 0.24719 | 60.6079 | 61.1023 | 122.7219 | 122.9599 | -0.10529 | 122.9691 | 60.8597 | -0.31586 | 122.9599 | -0.10529 | 60.8597 | 122.7219 | 122.9691 | -123.2849 | -123.2483
3328.7812 | 123.2391 | -60.8871 | 62.0499 | -0.011673 | -0.0090704 | -0.011984 | 0.00092504 | 0.054551 | -0.0080001 | 0.065488 | -61.0199 | 62.0956 | -61.2305 | -61.0794 | 61.8851 | 0.018311 | -0.20142 | 0.32044 | 62.1277 | -61.1618 | -0.34332 | 0.045776 | -0.13275 | -0.19226 | -0.16479 | -0.27466 | 0.07782 | 0.21057 | 60.6857 | 61.2076 | 122.7722 | 122.9828 | -0.13275 | 123.0148 | 60.9055 | -0.27466 | 122.9828 | -0.13275 | 60.9055 | 122.7722 | 123.0148 | -123.2803 | -123.2117
3329.7812 | 123.175 | -60.8643 | 62.1048 | -0.20241 | -0.0088568 | -0.013693 | 0.0034884 | 0.055833 | -0.0075729 | 0.063779 | -61.0016 | 62.1826 | -61.2167 | -61.084 | 61.8393 | 0.018311 | -0.032043 | 0.28381 | 62.1506 | -61.2122 | -0.35248 | 0.07782 | -0.13733 | -0.21973 | -0.2655 | -0.3479 | 0.045777 | 0.21515 | 60.8322 | 61.1481 | 122.7036 | 123.0469 | -0.13733 | 123.0148 | 60.8826 | -0.3479 | 123.0469 | -0.13733 | 60.8826 | 122.7036 | 123.0148 | -123.3215 | -123.317
3330.7812 | 123.2346 | -60.8505 | 62.0682 | 1.8423 | -0.0069342 | -0.014761 | 0.0015658 | 0.055405 | -0.0082137 | 0.06442 | -61.0245 | 62.1231 | -61.235 | -61.0336 | 61.9217 | 0.050354 | -0.13733 | 0.33417 | 62.1231 | -61.171 | -0.38452 | 0.054932 | -0.17395 | -0.18311 | -0.14648 | -0.32043 | 0.054932 | 0.21057 | 60.7132 | 61.1847 | 122.7722 | 122.9736 | -0.17395 | 122.9736 | 60.9009 | -0.32043 | 122.9736 | -0.17395 | 60.9009 | 122.7722 | 122.9736 | -123.3032 | -123.2391
3331.7812 | 123.1613 | -60.8963 | 62.1002 | 0.43846 | -0.007575 | -0.012412 | 0.0051974 | 0.055192 | -0.0056503 | 0.065488 | -61.0519 | 62.2238 | -61.2488 | -61.116 | 61.8027 | -0.027466 | 0.018311 | 0.22888 | 62.1689 | -61.2122 | -0.35248 | 0.1236 | -0.15564 | -0.21973 | -0.29755 | -0.31586 | 0.068664 | 0.19684 | 60.9146 | 61.1252 | 122.699 | 123.1201 | -0.15564 | 123.0652 | 60.8688 | -0.31586 | 123.1201 | -0.15564 | 60.8688 | 122.699 | 123.0652 | -123.349 | -123.3124
3332.7812 | 123.1567 | -60.9009 | 62.1185 | -0.11085 | -0.0045844 | -0.015189 | 0.0075472 | 0.0616 | -0.0075729 | 0.067197 | -61.0382 | 62.2467 | -61.2671 | -61.1114 | 61.8301 | -0.027466 | 0.004578 | 0.21515 | 62.1872 | -61.2122 | -0.36621 | 0.12817 | -0.13733 | -0.21057 | -0.28839 | -0.31128 | 0.068665 | 0.22888 | 60.9055 | 61.116 | 122.731 | 123.1476 | -0.13733 | 123.0881 | 60.8734 | -0.31128 | 123.1476 | -0.13733 | 60.8734 | 122.731 | 123.0881 | -123.3856 | -123.3307
3333.7812 | 123.1384 | -60.9375 | 62.0956 | -0.19478 | -0.0073614 | -0.016684 | 0.0034884 | 0.058823 | -0.0062911 | 0.065916 | -61.0428 | 62.233 | -61.2579 | -61.1435 | 61.7752 | 0.041199 | 0.21057 | 0.10986 | 62.2101 | -61.203 | -0.32044 | 0.13733 | -0.10529 | -0.20599 | -0.32043 | -0.2655 | 0.11444 | 0.21515 | 61.1481 | 61.0474 | 122.7127 | 123.1705 | -0.10529 | 123.1476 | 60.9787 | -0.2655 | 123.1705 | -0.10529 | 60.9787 | 122.7127 | 123.1476 | -123.3536 | -123.2986
3334.7812 | 123.1293 | -60.91 | 62.1002 | -0.15663 | -0.0086432 | -0.016684 | 0.0024202 | 0.060532 | -0.0065047 | 0.06442 | -61.0565 | 62.2055 | -61.2488 | -61.1298 | 61.8256 | -0.032043 | 0.041199 | 0.21057 | 62.1735 | -61.2122 | -0.33874 | 0.10529 | -0.14648 | -0.21973 | -0.27466 | -0.30212 | 0.073242 | 0.19226 | 60.9512 | 61.1206 | 122.7356 | 123.1155 | -0.14648 | 123.0835 | 60.878 | -0.30212 | 123.1155 | -0.14648 | 60.878 | 122.7356 | 123.0835 | -123.349 | -123.3124
3335.7969 | 123.1018 | -60.9283 | 62.059 | -0.04982 | -0.0054388 | -0.011343 | 0.0064792 | 0.063523 | -0.0082137 | 0.065061 | -60.9787 | 62.2147 | -61.2259 | -61.1069 | 61.8256 | -0.022888 | -0.064087 | 0.2243 | 62.1918 | -61.2122 | -0.29755 | 0.15564 | -0.050354 | -0.17853 | -0.23346 | -0.28381 | 0.13275 | 0.24719 | 60.8643 | 61.1526 | 122.7539 | 123.143 | -0.050354 | 123.1201 | 60.9055 | -0.28381 | 123.143 | -0.050354 | 60.9055 | 122.7539 | 123.1201 | -123.2849 | -123.2712
3336.7812 | 123.1659 | -60.91 | 62.0911 | -0.17952 | -0.0077888 | -0.013907 | 0.0049838 | 0.062669 | -0.0060775 | 0.065702 | -61.0062 | 62.2284 | -61.2259 | -61.1252 | 61.8439 | -0.018311 | 0 | 0.22888 | 62.1872 | -61.2167 | -0.31586 | 0.13733 | -0.096131 | -0.21515 | -0.24719 | -0.3067 | 0.096131 | 0.21973 | 60.91 | 61.1389 | 122.7539 | 123.1384 | -0.096131 | 123.0972 | 60.8917 | -0.3067 | 123.1384 | -0.096131 | 60.8917 | 122.7539 | 123.0972 | -123.317 | -123.3078
3337.7812 | 123.1934 | -60.8917 | 62.0407 | 0.018845 | -0.0097114 | -0.013266 | -0.0037748 | 0.059678 | -0.0060775 | 0.065488 | -61.0748 | 62.1094 | -61.2579 | -61.1114 | 61.8851 | -0.022888 | -0.16479 | 0.23804 | 62.146 | -61.1801 | -0.36621 | 0.068665 | -0.1831 | -0.21973 | -0.15564 | -0.28839 | 0.10529 | 0.18311 | 60.7269 | 61.1298 | 122.7768 | 123.0011 | -0.1831 | 123.0377 | 60.8688 | -0.28839 | 123.0011 | -0.1831 | 60.8688 | 122.7768 | 123.0377 | -123.2986 | -123.2208
3338.7812 | 123.2529 | -60.8871 | 62.0224 | 0.21721 | -0.0071478 | -0.011343 | 0.0049838 | 0.060105 | -0.0054367 | 0.06677 | -60.9695 | 62.1643 | -61.2396 | -61.0977 | 61.8484 | -0.045776 | -0.29297 | 0.20142 | 62.0682 | -61.2259 | -0.35248 | 0.14191 | -0.082397 | -0.21057 | -0.17395 | -0.33874 | 0.045776 | 0.27008 | 60.5942 | 61.0886 | 122.7356 | 123.0515 | -0.082397 | 122.9553 | 60.8414 | -0.33874 | 123.0515 | -0.082397 | 60.8414 | 122.7356 | 122.9553 | -123.262 | -123.2483
3339.7812 | 123.2391 | -60.9009 | 62.0132 | 0.27824 | -0.007575 | -0.011984 | 0.004343 | 0.059251 | -0.0054367 | 0.065916 | -61.0245 | 62.146 | -61.2442 | -61.1435 | 61.853 | -0.036621 | -0.30212 | 0.1831 | 62.059 | -61.2167 | -0.34332 | 0.13275 | -0.1236 | -0.24261 | -0.16022 | -0.31586 | 0.045776 | 0.21973 | 60.5988 | 61.084 | 122.7539 | 123.0469 | -0.1236 | 122.9599 | 60.8643 | -0.31586 | 123.0469 | -0.1236 | 60.8643 | 122.7539 | 122.9599 | -123.2574 | -123.23
3340.7812 | 123.2346 | -60.8963 | 62.0316 | 0.27061 | -0.008216 | -0.0094207 | 0.0022066 | 0.063737 | -0.0020187 | 0.065916 | -60.9787 | 62.1231 | -61.2213 | -61.0336 | 61.9583 | 0.041199 | -0.26093 | 0.21973 | 62.0956 | -61.1938 | -0.32501 | 0.091553 | -0.082398 | -0.13733 | -0.073242 | -0.29755 | 0.064087 | 0.24261 | 60.6354 | 61.116 | 122.8546 | 123.0194 | -0.082398 | 122.9919 | 60.9375 | -0.29755 | 123.0194 | -0.082398 | 60.9375 | 122.8546 | 122.9919 | -123.2529 | -123.2254
3341.7812 | 123.1934 | -60.91 | 62.0636 | 0.18669 | -0.0086432 | -0.014121 | -0.00035676 | 0.059251 | -0.0062911 | 0.066343 | -61.0519 | 62.0956 | -61.2259 | -61.1481 | 61.8256 | -0.064087 | -0.21973 | 0.19684 | 62.114 | -61.1984 | -0.31586 | 0.032043 | -0.14191 | -0.23804 | -0.23804 | -0.28839 | 0.050354 | 0.17395 | 60.6903 | 61.1069 | 122.7356 | 123.0057 | -0.14191 | 123.024 | 60.8459 | -0.28839 | 123.0057 | -0.14191 | 60.8459 | 122.7356 | 123.024 | -123.2895 | -123.262
3342.7812 | 123.2071 | -60.9055 | 62.0544 | 0.072251 | -0.0097114 | -0.012839 | -0.001425 | 0.055833 | -0.0062911 | 0.065916 | -61.0748 | 62.1368 | -61.235 | -61.1389 | 62.0316 | 0.07782 | -0.24719 | 0.23804 | 62.1094 | -61.2122 | -0.32959 | 0.082398 | -0.16937 | -0.23346 | -0.022888 | -0.3067 | 0.054932 | 0.16022 | 60.6583 | 61.1435 | 122.937 | 123.0423 | -0.16937 | 123.0148 | 60.9833 | -0.3067 | 123.0423 | -0.16937 | 60.9833 | 122.937 | 123.0148 | -123.2895 | -123.2666
3343.7812 | 123.2346 | -60.878 | 62.0407 | 0.24773 | -0.008216 | -0.010703 | 0.0064792 | 0.059464 | -0.0054367 | 0.064634 | -61.0153 | 62.1277 | -61.235 | -61.1069 | 61.8347 | -0.054932 | -0.28381 | 0.21973 | 62.0728 | -61.1984 | -0.35705 | 0.086976 | -0.13733 | -0.22888 | -0.20599 | -0.32043 | 0.032044 | 0.21973 | 60.5942 | 61.0977 | 122.7127 | 123.0057 | -0.13733 | 122.9507 | 60.8231 | -0.32043 | 123.0057 | -0.13733 | 60.8231 | 122.7127 | 122.9507 | -123.2758 | -123.2391
3344.7812 | 123.2437 | -60.9055 | 62.027 | 0.2935 | -0.0039434 | -0.01583 | 0.0064792 | 0.05861 | -0.0050095 | 0.064847 | -60.9924 | 62.1277 | -61.2579 | -61.084 | 61.8439 | -0.050354 | -0.31586 | 0.20599 | 62.0682 | -61.2305 | -0.35248 | 0.10071 | -0.086975 | -0.17853 | -0.18311 | -0.32501 | 0.041198 | 0.2655 | 60.5896 | 61.1115 | 122.7493 | 123.0331 | -0.086975 | 122.9736 | 60.8551 | -0.32501 | 123.0331 | -0.086975 | 60.8551 | 122.7493 | 122.9736 | -123.2849 | -123.2574
3345.7812 | 123.1476 | -60.9329 | 62.0728 | -2.125 | -0.0062934 | -0.014121 | 0.0077608 | 0.060319 | -0.0047957 | 0.065916 | -61.0519 | 62.2147 | -61.2259 | -61.171 | 61.734 | -0.15106 | -0.1236 | 0.1236 | 62.1277 | -61.2671 | -0.29297 | 0.14191 | -0.11902 | -0.23804 | -0.33875 | -0.33417 | 0.054932 | 0.17395 | 60.8093 | 61.0565 | 122.6669 | 123.1476 | -0.11902 | 123.0606 | 60.7819 | -0.33417 | 123.1476 | -0.11902 | 60.7819 | 122.6669 | 123.0606 | -123.2986 | -123.3398
3346.7812 | 123.2208 | -60.878 | 62.0361 | 0.26299 | -0.0071478 | -0.013907 | 0.0011386 | 0.059037 | -0.0054367 | 0.066556 | -61.0199 | 62.1094 | -61.2579 | -61.0886 | 61.853 | -0.050354 | -0.29755 | 0.22888 | 62.059 | -61.2122 | -0.37994 | 0.073242 | -0.14191 | -0.21057 | -0.18311 | -0.33417 | 0.022888 | 0.23804 | 60.5804 | 61.1069 | 122.731 | 122.9874 | -0.14191 | 122.937 | 60.8276 | -0.33417 | 122.9874 | -0.14191 | 60.8276 | 122.731 | 122.937 | -123.2941 | -123.2483
3347.7812 | 123.2666 | -60.878 | 62.0361 | -0.065079 | -0.009925 | -0.015189 | -0.0012112 | 0.056901 | -0.0050095 | 0.064207 | -61.0428 | 62.1231 | -61.2167 | -61.0611 | 61.8942 | 0.027466 | -0.19684 | 0.32501 | 62.1185 | -61.1847 | -0.33874 | 0.086975 | -0.16479 | -0.1831 | -0.14191 | -0.3067 | 0.082397 | 0.17395 | 60.6812 | 61.203 | 122.7722 | 123.0011 | -0.16479 | 122.9965 | 60.9055 | -0.3067 | 123.0011 | -0.16479 | 60.9055 | 122.7722 | 122.9965 | -123.2529 | -123.2208
3348.7812 | 123.23 | -60.8871 | 62.0407 | 0.07988 | -0.005866 | -0.013052 | 0.0062656 | 0.058396 | -0.0071457 | 0.065275 | -60.997 | 62.1231 | -61.2167 | -61.0931 | 61.8576 | -0.036621 | -0.31128 | 0.22888 | 62.0682 | -61.2122 | -0.32959 | 0.082398 | -0.10986 | -0.20599 | -0.1831 | -0.32501 | 0.027466 | 0.21973 | 60.5759 | 61.116 | 122.7448 | 123.0103 | -0.10986 | 122.9553 | 60.8505 | -0.32501 | 123.0103 | -0.10986 | 60.8505 | 122.7448 | 122.9553 | -123.2574 | -123.2529
3349.7812 | 123.23 | -60.878 | 62.0544 | 0.049362 | -0.007575 | -0.016684 | -0.0012112 | 0.05626 | -0.0071457 | 0.065916 | -61.0657 | 62.114 | -61.235 | -61.1252 | 61.8576 | -0.036621 | -0.17853 | 0.21973 | 62.1231 | -61.1938 | -0.35705 | 0.05951 | -0.18768 | -0.24719 | -0.19684 | -0.31586 | 0.068665 | 0.16937 | 60.6995 | 61.0977 | 122.7356 | 122.9919 | -0.18768 | 123.0011 | 60.8414 | -0.31586 | 122.9919 | -0.18768 | 60.8414 | 122.7356 | 123.0011 | -123.2895 | -123.2483
3350.7812 | 123.175 | -60.9283 | 62.0361 | 0.2401 | -0.0050116 | -0.010062 | 0.0075472 | 0.057114 | -0.0045821 | 0.066129 | -61.0611 | 62.1918 | -61.2534 | -61.1572 | 61.7798 | -0.1236 | -0.20142 | 0.12817 | 62.1002 | -61.2717 | -0.32501 | 0.15564 | -0.13275 | -0.22888 | -0.25635 | -0.34332 | 0.064087 | 0.19226 | 60.7269 | 61.0565 | 122.7081 | 123.1201 | -0.13275 | 123.0286 | 60.8047 | -0.34332 | 123.1201 | -0.13275 | 60.8047 | 122.7081 | 123.0286 | -123.2895 | -123.3078
3351.7812 | 123.2162 | -60.9329 | 62.0132 | 0.35454 | -0.0073614 | -0.013907 | 0.003702 | 0.0616 | -0.0047957 | 0.064847 | -60.997 | 62.1368 | -61.2305 | -61.0931 | 61.8301 | -0.054932 | -0.28381 | 0.20599 | 62.0956 | -61.2213 | -0.29755 | 0.1236 | -0.064087 | -0.16022 | -0.18311 | -0.28839 | 0.082397 | 0.23346 | 60.6491 | 61.1389 | 122.7631 | 123.0698 | -0.064087 | 123.0286 | 60.878 | -0.28839 | 123.0698 | -0.064087 | 60.878 | 122.7631 | 123.0286 | -123.2437 | -123.2346
3352.7812 | 123.1155 | -60.9055 | 62.1094 | -0.2253 | -0.0073614 | -0.0094207 | 0.0028476 | 0.059891 | -0.0058639 | 0.065061 | -61.0565 | 62.2192 | -61.2534 | -61.1893 | 61.8027 | -0.054932 | -0.004578 | 0.21973 | 62.1506 | -61.2259 | -0.3479 | 0.10986 | -0.15106 | -0.28381 | -0.3067 | -0.32043 | 0.041199 | 0.19684 | 60.9009 | 61.1252 | 122.7081 | 123.1247 | -0.15106 | 123.056 | 60.8505 | -0.32043 | 123.1247 | -0.15106 | 60.8505 | 122.7081 | 123.056 | -123.3627 | -123.3353
3353.7812 | 123.2483 | -60.8917 | 62.0499 | 0.26299 | -0.010993 | -0.011984 | 0.0017794 | 0.059678 | -0.0077865 | 0.065061 | -60.9741 | 62.1094 | -61.2579 | -61.1023 | 61.8576 | -0.045776 | -0.29297 | 0.21057 | 62.0865 | -61.1984 | -0.36621 | 0.059509 | -0.082397 | -0.21057 | -0.19226 | -0.3067 | 0.036621 | 0.28381 | 60.5988 | 61.1023 | 122.7493 | 123.0011 | -0.082397 | 122.9782 | 60.8459 | -0.3067 | 123.0011 | -0.082397 | 60.8459 | 122.7493 | 122.9782 | -123.3078 | -123.2483
3354.7812 | 123.2391 | -60.8917 | 62.027 | 0.25536 | -0.0069342 | -0.012625 | 0.0045566 | 0.059678 | -0.0065047 | 0.065488 | -60.997 | 62.1689 | -61.2488 | -61.116 | 61.853 | -0.059509 | -0.3067 | 0.19684 | 62.0956 | -61.2122 | -0.35705 | 0.14191 | -0.10528 | -0.2243 | -0.17395 | -0.32043 | 0.068664 | 0.25177 | 60.585 | 61.0886 | 122.7448 | 123.0606 | -0.10528 | 122.9874 | 60.8322 | -0.32043 | 123.0606 | -0.10528 | 60.8322 | 122.7448 | 122.9874 | -123.2758 | -123.2391
3355.7812 | 123.1888 | -60.8963 | 62.027 | 0.14854 | -0.0071478 | -0.01348 | -0.00078396 | 0.059464 | -0.0056503 | 0.067197 | -61.0519 | 62.1323 | -61.2534 | -61.1343 | 61.8027 | -0.068665 | -0.20142 | 0.19226 | 62.1048 | -61.1984 | -0.35706 | 0.10529 | -0.15564 | -0.23804 | -0.22431 | -0.30212 | 0.077819 | 0.20142 | 60.6949 | 61.0886 | 122.699 | 123.0286 | -0.15564 | 123.0011 | 60.8276 | -0.30212 | 123.0286 | -0.15564 | 60.8276 | 122.699 | 123.0011 | -123.2803 | -123.2254
3356.7812 | 123.2117 | -60.9055 | 62.0407 | 0.24773 | -0.0067206 | -0.017111 | 0.001993 | 0.058396 | -0.0047957 | 0.066343 | -61.0245 | 62.1277 | -61.2488 | -61.1206 | 61.8301 | -0.073242 | -0.25635 | 0.20599 | 62.0636 | -61.1984 | -0.34332 | 0.086976 | -0.11902 | -0.21515 | -0.21057 | -0.29297 | 0.022889 | 0.2243 | 60.6491 | 61.1115 | 122.7356 | 123.0331 | -0.11902 | 122.9691 | 60.8322 | -0.29297 | 123.0331 | -0.11902 | 60.8322 | 122.7356 | 122.9691 | -123.2895 | -123.2391
3357.7812 | 123.2208 | -60.8643 | 62.059 | -0.04219 | -0.010139 | -0.014975 | 0.0013522 | 0.056687 | -0.0060775 | 0.065275 | -61.0382 | 62.1323 | -61.235 | -61.0886 | 61.8668 | 0.013733 | -0.1831 | 0.29297 | 62.0819 | -61.203 | -0.37079 | 0.073242 | -0.17395 | -0.2243 | -0.19226 | -0.33875 | 0.022888 | 0.19684 | 60.6812 | 61.1572 | 122.731 | 122.9965 | -0.17395 | 122.9462 | 60.878 | -0.33875 | 122.9965 | -0.17395 | 60.878 | 122.731 | 122.9462 | -123.2941 | -123.262
3358.7812 | 123.1934 | -60.8826 | 62.0499 | 0.20195 | -0.0069342 | -0.014121 | 0.001993 | 0.05626 | -0.0077865 | 0.065275 | -61.0291 | 62.1185 | -61.2534 | -61.1114 | 61.8256 | -0.064087 | -0.28381 | 0.21057 | 62.0728 | -61.2305 | -0.37079 | 0.068664 | -0.14648 | -0.22888 | -0.2243 | -0.3479 | 0.022888 | 0.2243 | 60.5988 | 61.0931 | 122.7081 | 123.0011 | -0.14648 | 122.9553 | 60.8185 | -0.3479 | 123.0011 | -0.14648 | 60.8185 | 122.7081 | 122.9553 | -123.3032 | -123.2803
3359.7812 | 123.2162 | -60.8917 | 62.0224 | 0.23247 | -0.0094976 | -0.012625 | 0.002634 | 0.05626 | -0.0045821 | 0.064207 | -61.0245 | 62.0819 | -61.2671 | -61.1114 | 61.8256 | -0.073242 | -0.28839 | 0.21057 | 62.0636 | -61.2122 | -0.37537 | 0.059509 | -0.13275 | -0.21973 | -0.19684 | -0.32043 | 0.041199 | 0.24262 | 60.6033 | 61.1023 | 122.7173 | 122.9736 | -0.13275 | 122.9553 | 60.8185 | -0.32043 | 122.9736 | -0.13275 | 60.8185 | 122.7173 | 122.9553 | -123.2895 | -123.2346
3360.7812 | 123.2162 | -60.8826 | 62.027 | 0.18669 | -0.0086432 | -0.012198 | 0.0032748 | 0.057328 | -0.0058639 | 0.065916 | -61.0016 | 62.114 | -61.2305 | -61.1023 | 61.8347 | -0.059509 | -0.27924 | 0.20599 | 62.0819 | -61.2213 | -0.3479 | 0.086975 | -0.11902 | -0.21973 | -0.19226 | -0.33875 | 0.054931 | 0.22888 | 60.6033 | 61.0886 | 122.7173 | 122.9965 | -0.11902 | 122.9645 | 60.8231 | -0.33875 | 122.9965 | -0.11902 | 60.8231 | 122.7173 | 122.9645 | -123.2574 | -123.2483
3361.7812 | 123.2208 | -60.9421 | 62.0132 | 0.24773 | -0.0069342 | -0.012839 | 0.0030612 | 0.058396 | -0.0054367 | 0.066556 | -61.0199 | 62.1277 | -61.2305 | -61.1069 | 61.8256 | -0.073242 | -0.29297 | 0.21515 | 62.0682 | -61.235 | -0.28839 | 0.11444 | -0.077819 | -0.16479 | -0.18768 | -0.29297 | 0.054931 | 0.21057 | 60.6491 | 61.1572 | 122.7676 | 123.0698 | -0.077819 | 123.0103 | 60.8688 | -0.29297 | 123.0698 | -0.077819 | 60.8688 | 122.7676 | 123.0103 | -123.2437 | -123.2483
3362.7812 | 123.1201 | -60.9192 | 62.1048 | -0.14137 | -0.0056524 | -0.016257 | 0.0034884 | 0.05861 | -0.0056503 | 0.065061 | -61.0565 | 62.2055 | -61.2488 | -61.1435 | 61.7981 | -0.059509 | 0.018311 | 0.23346 | 62.1506 | -61.2122 | -0.32959 | 0.10071 | -0.13733 | -0.2243 | -0.3067 | -0.29297 | 0.045777 | 0.19226 | 60.9375 | 61.1526 | 122.7173 | 123.1247 | -0.13733 | 123.0698 | 60.8597 | -0.29297 | 123.1247 | -0.13733 | 60.8597 | 122.7173 | 123.0698 | -123.3536 | -123.317
3363.7812 | 123.2574 | -60.8505 | 62.0453 | -0.04982 | -0.010352 | -0.015402 | 7.0444e-05 | 0.055405 | -0.0071457 | 0.065916 | -61.0107 | 62.0956 | -61.235 | -61.0519 | 61.9034 | 0.050354 | -0.20142 | 0.32959 | 62.1185 | -61.1801 | -0.38452 | 0.050354 | -0.16022 | -0.20142 | -0.14191 | -0.32959 | 0.073242 | 0.2243 | 60.6491 | 61.1801 | 122.7539 | 122.9462 | -0.16022 | 122.9691 | 60.9009 | -0.32959 | 122.9462 | -0.16022 | 60.9009 | 122.7539 | 122.9691 | -123.2803 | -123.2254
3364.7812 | 123.1934 | -60.9009 | 62.0453 | 0.20958 | -0.0069342 | -0.015189 | 0.002634 | 0.056901 | -0.0041549 | 0.063993 | -61.0382 | 62.1048 | -61.235 | -61.1298 | 61.821 | -0.091553 | -0.24261 | 0.18768 | 62.0682 | -61.2122 | -0.33417 | 0.059509 | -0.13733 | -0.22888 | -0.2243 | -0.31128 | 0.022888 | 0.19684 | 60.6583 | 61.0886 | 122.7219 | 123.0057 | -0.13733 | 122.9691 | 60.8093 | -0.31128 | 123.0057 | -0.13733 | 60.8093 | 122.7219 | 122.9691 | -123.2803 | -123.2574
3365.7812 | 123.2391 | -60.8551 | 62.0682 | 0.018845 | -0.0090704 | -0.012839 | -0.00078396 | 0.05626 | -0.0067185 | 0.067411 | -61.0245 | 62.1277 | -61.2305 | -61.0886 | 61.8805 | 0.018311 | -0.20599 | 0.32044 | 62.114 | -61.2076 | -0.37537 | 0.05951 | -0.16937 | -0.23346 | -0.18768 | -0.35248 | 0.045777 | 0.20599 | 60.6491 | 61.1755 | 122.7356 | 122.9828 | -0.16937 | 122.9691 | 60.8734 | -0.35248 | 122.9828 | -0.16937 | 60.8734 | 122.7356 | 122.9691 | -123.2986 | -123.2758
3366.7812 | 123.23 | -60.8963 | 62.0178 | 0.24773 | -0.0054388 | -0.010916 | 0.0060518 | 0.057114 | -0.0054367 | 0.066984 | -61.1801 | 62.0728 | -61.2488 | -61.0703 | 61.8439 | -0.045776 | -0.30212 | 0.21973 | 62.0911 | -61.2122 | -0.35248 | 0.054932 | -0.28381 | -0.17395 | -0.17395 | -0.31586 | 0.073242 | 0.068664 | 60.5942 | 61.116 | 122.7402 | 122.9691 | -0.28381 | 122.9874 | 60.8505 | -0.31586 | 122.9691 | -0.28381 | 60.8505 | 122.7402 | 122.9874 | -123.2666 | -123.23
3367.7812 | 123.2391 | -60.8505 | 62.0636 | 0.38506 | -0.009925 | -0.015189 | 7.0444e-05 | 0.056901 | -0.0082137 | 0.064634 | -60.9558 | 62.1323 | -61.2305 | -61.0519 | 61.8988 | 0.036621 | -0.15106 | 0.33875 | 62.146 | -61.1664 | -0.37994 | 0.068664 | -0.10529 | -0.20142 | -0.1648 | -0.31586 | 0.082397 | 0.27466 | 60.6995 | 61.1893 | 122.7493 | 122.9828 | -0.10529 | 122.9965 | 60.8871 | -0.31586 | 122.9828 | -0.10529 | 60.8871 | 122.7493 | 122.9965 | -123.2941 | -123.23
3368.7812 | 123.262 | -60.8963 | 62.0178 | 0.18669 | -0.0073614 | -0.013266 | 0.0056246 | 0.057114 | -0.0071457 | 0.064634 | -61.0107 | 62.1231 | -61.235 | -61.0886 | 61.8439 | -0.068665 | -0.29755 | 0.2243 | 62.0865 | -61.2122 | -0.33874 | 0.10529 | -0.11444 | -0.19226 | -0.17395 | -0.31586 | 0.068665 | 0.2243 | 60.5988 | 61.1206 | 122.7402 | 123.0194 | -0.11444 | 122.9828 | 60.8276 | -0.31586 | 123.0194 | -0.11444 | 60.8276 | 122.7402 | 122.9828 | -123.2529 | -123.23
3369.7812 | 123.2529 | -60.8963 | 62.0361 | 0.049362 | -0.0077888 | -0.012412 | 0.005411 | 0.058823 | -0.0050095 | 0.064207 | -60.9879 | 62.1002 | -61.2442 | -61.0794 | 61.8484 | -0.064087 | -0.3067 | 0.21515 | 62.0865 | -61.1801 | -0.3479 | 0.064087 | -0.091553 | -0.18311 | -0.18768 | -0.28381 | 0.050354 | 0.25635 | 60.5896 | 61.1114 | 122.7448 | 122.9965 | -0.091553 | 122.9828 | 60.8322 | -0.28381 | 122.9965 | -0.091553 | 60.8322 | 122.7448 | 122.9828 | -123.2803 | -123.2162
3370.7812 | 123.2437 | -60.8917 | 62.0407 | 0.23247 | -0.0039434 | -0.013266 | 0.004343 | 0.059678 | -0.0065047 | 0.067197 | -61.0199 | 62.1552 | -61.2488 | -61.0794 | 61.7889 | -0.13275 | -0.27466 | 0.19684 | 62.0728 | -61.2442 | -0.35705 | 0.11444 | -0.12817 | -0.18768 | -0.25177 | -0.35248 | 0.032044 | 0.22888 | 60.6171 | 61.0886 | 122.6807 | 123.0469 | -0.12817 | 122.9645 | 60.759 | -0.35248 | 123.0469 | -0.12817 | 60.759 | 122.6807 | 122.9645 | -123.2895 | -123.2849
3371.7812 | 123.2208 | -60.878 | 62.0453 | 0.018845 | -0.0080024 | -0.011771 | -0.0020658 | 0.057755 | -0.0075729 | 0.066984 | -61.0611 | 62.1231 | -61.2625 | -61.0977 | 61.8668 | -0.013733 | -0.20142 | 0.27924 | 62.114 | -61.1801 | -0.38452 | 0.07782 | -0.1831 | -0.21973 | -0.17853 | -0.30212 | 0.068665 | 0.20142 | 60.6766 | 61.1572 | 122.7448 | 123.0011 | -0.1831 | 122.9919 | 60.8643 | -0.30212 | 123.0011 | -0.1831 | 60.8643 | 122.7448 | 122.9919 | -123.3078 | -123.2254
3372.7812 | 123.2162 | -60.8734 | 62.0316 | -0.11085 | -0.010139 | -0.01647 | 0.00071144 | 0.055833 | -0.011205 | 0.064847 | -60.9833 | 62.1597 | -61.2213 | -60.7956 | 61.7844 | -0.11902 | -0.1831 | 0.24261 | 62.1002 | -61.1938 | -0.3479 | 0.12817 | -0.10986 | 0.07782 | -0.24719 | -0.32044 | 0.068665 | 0.23804 | 60.6903 | 61.116 | 122.6578 | 123.0331 | -0.10986 | 122.9736 | 60.7544 | -0.32044 | 123.0331 | -0.10986 | 60.7544 | 122.6578 | 122.9736 | -123.2529 | -123.2254
3373.7812 | 123.1842 | -60.9329 | 62.0544 | 0.21721 | -0.004798 | -0.010489 | 0.0084018 | 0.058823 | -0.0071457 | 0.065275 | -61.0611 | 62.1689 | -61.2579 | -61.1893 | 61.7661 | -0.16022 | -0.18768 | 0.10986 | 62.0956 | -61.2625 | -0.32501 | 0.11444 | -0.12817 | -0.25635 | -0.28839 | -0.32959 | 0.041199 | 0.19684 | 60.7452 | 61.0428 | 122.699 | 123.1018 | -0.12817 | 123.0286 | 60.7727 | -0.32959 | 123.1018 | -0.12817 | 60.7727 | 122.699 | 123.0286 | -123.3124 | -123.317
3374.7812 | 123.2254 | -60.9146 | 62.0224 | 0.26299 | -0.0054388 | -0.010062 | 0.0056246 | 0.05861 | -0.0058639 | 0.066984 | -61.0382 | 62.1872 | -61.2488 | -61.1343 | 61.8073 | -0.10986 | -0.26093 | 0.16022 | 62.0956 | -61.2396 | -0.33417 | 0.1648 | -0.1236 | -0.21973 | -0.21515 | -0.32501 | 0.073242 | 0.21057 | 60.6537 | 61.0748 | 122.7219 | 123.1018 | -0.1236 | 123.0103 | 60.8047 | -0.32501 | 123.1018 | -0.1236 | 60.8047 | 122.7219 | 123.0103 | -123.2712 | -123.262
3375.7812 | 123.1842 | -60.9009 | 62.0361 | 0.21721 | -0.008216 | -0.017111 | -0.0016386 | 0.057755 | -0.0073593 | 0.064847 | -61.0565 | 62.114 | -61.2534 | -61.1206 | 61.8256 | -0.064087 | -0.2655 | 0.19226 | 62.0865 | -61.1984 | -0.35248 | 0.07782 | -0.15564 | -0.21973 | -0.21057 | -0.29755 | 0.050354 | 0.19684 | 60.6354 | 61.0931 | 122.7264 | 123.0148 | -0.15564 | 122.9874 | 60.8368 | -0.29755 | 123.0148 | -0.15564 | 60.8368 | 122.7264 | 122.9874 | -123.2895 | -123.2346
3376.7812 | 123.2025 | -60.9055 | 62.0316 | 0.1638 | -0.0097114 | -0.010275 | 0.00049764 | 0.057755 | -0.0058639 | 0.06442 | -61.0748 | 62.114 | -61.2534 | -61.1252 | 61.821 | -0.059509 | -0.22888 | 0.19684 | 62.0865 | -61.2076 | -0.3479 | 0.082398 | -0.16937 | -0.21973 | -0.21057 | -0.30212 | 0.054932 | 0.17853 | 60.6766 | 61.1023 | 122.7264 | 123.0194 | -0.16937 | 122.9919 | 60.8459 | -0.30212 | 123.0194 | -0.16937 | 60.8459 | 122.7264 | 122.9919 | -123.2849 | -123.2391
3377.7812 | 123.1934 | -60.8917 | 62.1048 | -0.15663 | -0.009284 | -0.013693 | 0.00092504 | 0.059037 | -0.0069321 | 0.066129 | -61.0062 | 62.1552 | -61.2259 | -61.0886 | 61.8805 | 0.018311 | -0.054932 | 0.3067 | 62.1323 | -61.203 | -0.33417 | 0.050354 | -0.11444 | -0.19684 | -0.2243 | -0.31128 | 0.027466 | 0.21973 | 60.8368 | 61.1984 | 122.7722 | 123.0469 | -0.11444 | 123.024 | 60.91 | -0.31128 | 123.0469 | -0.11444 | 60.91 | 122.7722 | 123.024 | -123.3307 | -123.3078
3378.7812 | 123.1979 | -60.9146 | 62.0544 | 0.20958 | -0.007575 | -0.01583 | 0.00028404 | 0.057114 | -0.0067185 | 0.066129 | -61.0428 | 62.1048 | -61.2488 | -61.1481 | 61.8301 | -0.09613 | -0.24719 | 0.19226 | 62.0773 | -61.2076 | -0.33417 | 0.050354 | -0.12817 | -0.23346 | -0.2243 | -0.29297 | 0.022889 | 0.20599 | 60.6674 | 61.1069 | 122.7448 | 123.0194 | -0.12817 | 122.9919 | 60.8185 | -0.29297 | 123.0194 | -0.12817 | 60.8185 | 122.7448 | 122.9919 | -123.3032 | -123.262
3379.7812 | 123.2071 | -60.8917 | 62.0453 | 0.1638 | -0.0080024 | -0.0096343 | 0.0015658 | 0.055833 | -0.0071457 | 0.065275 | -61.0748 | 62.1506 | -61.2305 | -61.1252 | 61.821 | -0.09613 | -0.19684 | 0.20599 | 62.0728 | -61.2167 | -0.33874 | 0.10529 | -0.1831 | -0.23346 | -0.2243 | -0.32501 | 0.027466 | 0.15564 | 60.6949 | 61.0977 | 122.7127 | 123.0423 | -0.1831 | 122.9645 | 60.7956 | -0.32501 | 123.0423 | -0.1831 | 60.7956 | 122.7127 | 122.9645 | -123.2758 | -123.262
3380.7812 | 123.2162 | -60.9283 | 62.0361 | 0.27061 | -0.0071478 | -0.014334 | 0.005411 | 0.057114 | -0.0041549 | 0.065702 | -61.0382 | 62.1689 | -61.29 | -61.1206 | 61.7935 | -0.10529 | -0.26093 | 0.20142 | 62.0956 | -61.2442 | -0.36163 | 0.13275 | -0.10986 | -0.19226 | -0.24262 | -0.31586 | 0.059509 | 0.25177 | 60.6674 | 61.1298 | 122.7219 | 123.0972 | -0.10986 | 123.024 | 60.8231 | -0.31586 | 123.0972 | -0.10986 | 60.8231 | 122.7219 | 123.024 | -123.3261 | -123.2803
3381.7812 | 123.2437 | -60.8826 | 62.0041 | 0.22484 | -0.0080024 | -0.0081389 | 0.0013522 | 0.059891 | -0.0056503 | 0.066343 | -60.9924 | 62.1094 | -61.2534 | -61.1069 | 61.8576 | -0.068665 | -0.29755 | 0.22888 | 62.1185 | -61.1984 | -0.37079 | 0.10529 | -0.10986 | -0.22431 | -0.14648 | -0.31586 | 0.11444 | 0.26093 | 60.585 | 61.1114 | 122.7402 | 122.9919 | -0.10986 | 123.0011 | 60.8139 | -0.31586 | 122.9919 | -0.10986 | 60.8139 | 122.7402 | 123.0011 | -123.2574 | -123.2025
3382.7812 | 123.1613 | -60.9283 | 62.0728 | -0.18715 | -0.009284 | -0.016257 | 0.00028404 | 0.058823 | -0.0060775 | 0.066556 | -61.0565 | 62.233 | -61.2625 | -61.2259 | 61.7889 | -0.050354 | -0.027466 | 0.2243 | 62.1552 | -61.235 | -0.33417 | 0.16022 | -0.12817 | -0.29755 | -0.28381 | -0.3067 | 0.082397 | 0.20599 | 60.9009 | 61.1526 | 122.7173 | 123.1613 | -0.12817 | 123.0835 | 60.878 | -0.3067 | 123.1613 | -0.12817 | 60.878 | 122.7173 | 123.0835 | -123.3353 | -123.3078
3383.7812 | 123.1934 | -60.878 | 62.0224 | 0.24773 | -0.008216 | -0.014975 | 0.0051974 | 0.060532 | -0.0077865 | 0.068265 | -61.0291 | 62.1552 | -61.2625 | -61.0977 | 61.8393 | -0.086975 | -0.29297 | 0.16937 | 62.0819 | -61.2259 | -0.38452 | 0.13275 | -0.15106 | -0.21973 | -0.18311 | -0.3479 | 0.059509 | 0.23346 | 60.585 | 61.0474 | 122.7173 | 123.0331 | -0.15106 | 122.9599 | 60.791 | -0.3479 | 123.0331 | -0.15106 | 60.791 | 122.7173 | 122.9599 | -123.2849 | -123.2483
3384.7812 | 123.2117 | -60.9009 | 62.0361 | 0.10277 | -0.011207 | -0.011984 | -0.0050566 | 0.058182 | -0.0047957 | 0.066129 | -61.0611 | 62.114 | -61.2625 | -61.1343 | 61.821 | -0.091553 | -0.16937 | 0.19226 | 62.1094 | -61.1847 | -0.36163 | 0.07782 | -0.16022 | -0.23346 | -0.21515 | -0.28381 | 0.073242 | 0.20142 | 60.7315 | 61.0931 | 122.7219 | 123.0148 | -0.16022 | 123.0103 | 60.8093 | -0.28381 | 123.0148 | -0.16022 | 60.8093 | 122.7219 | 123.0103 | -123.2986 | -123.2208
3385.7812 | 123.23 | -60.9055 | 62.0132 | 0.20195 | -0.0069342 | -0.012198 | 0.0041292 | 0.0616 | -0.0069321 | 0.067197 | -60.9833 | 62.1277 | -61.2396 | -61.0886 | 61.8622 | -0.050354 | -0.31128 | 0.21515 | 62.1048 | -61.2305 | -0.33417 | 0.11444 | -0.077819 | -0.18311 | -0.15106 | -0.32501 | 0.091552 | 0.25635 | 60.5942 | 61.1206 | 122.7676 | 123.0331 | -0.077819 | 123.0103 | 60.8551 | -0.32501 | 123.0331 | -0.077819 | 60.8551 | 122.7676 | 123.0103 | -123.2529 | -123.2437
3386.7812 | 123.1522 | -60.9283 | 62.0728 | 0.041733 | -0.0039434 | -0.0092071 | 0.0073336 | 0.059678 | -0.0067185 | 0.067197 | -60.997 | 62.2101 | -61.2534 | -61.1252 | 61.7935 | -0.064087 | -0.091553 | 0.17395 | 62.1368 | -61.2488 | -0.32501 | 0.13733 | -0.068664 | -0.19684 | -0.27924 | -0.32043 | 0.064087 | 0.25635 | 60.8368 | 61.1023 | 122.7219 | 123.1384 | -0.068664 | 123.0652 | 60.8643 | -0.32043 | 123.1384 | -0.068664 | 60.8643 | 122.7219 | 123.0652 | -123.3261 | -123.3215
3387.7969 | 123.1842 | -60.8871 | 62.059 | -0.11085 | -0.0071478 | -0.01113 | 0.005411 | 0.057969 | -0.0069321 | 0.064207 | -61.0107 | 62.2421 | -61.2625 | -61.1114 | 61.8256 | -0.032043 | -0.054932 | 0.27008 | 62.1323 | -61.2579 | -0.37537 | 0.1831 | -0.1236 | -0.2243 | -0.23346 | -0.37079 | 0.073242 | 0.25177 | 60.8322 | 61.1572 | 122.7127 | 123.1293 | -0.1236 | 123.0194 | 60.8551 | -0.37079 | 123.1293 | -0.1236 | 60.8551 | 122.7127 | 123.0194 | -123.3215 | -123.317
3388.7812 | 123.2346 | -60.8963 | 62.0087 | 0.27061 | -0.0069342 | -0.012412 | 0.0049838 | 0.060532 | -0.0058639 | 0.065488 | -60.997 | 62.1506 | -61.2671 | -61.1069 | 61.8576 | 0.032043 | -0.58594 | 0.21515 | 62.0682 | -61.2396 | -0.37079 | 0.14191 | -0.10071 | -0.21057 | -0.15106 | -0.34332 | 0.059509 | 0.27008 | 60.3104 | 61.1114 | 122.7539 | 123.0469 | -0.10071 | 122.9645 | 60.9283 | -0.34332 | 123.0469 | -0.10071 | 60.9283 | 122.7539 | 122.9645 | -123.2758 | -123.2483
3389.7812 | 123.1934 | -60.8734 | 62.0361 | 0.20195 | -0.008216 | -0.011771 | -0.00078396 | 0.059464 | -0.0054367 | 0.06442 | -61.0565 | 62.0911 | -61.2625 | -61.1435 | 61.8118 | -0.07782 | -0.23804 | 0.19684 | 62.1094 | -61.203 | -0.3891 | 0.054931 | -0.18311 | -0.27008 | -0.2243 | -0.32959 | 0.073242 | 0.20599 | 60.6354 | 61.0703 | 122.6852 | 122.9645 | -0.18311 | 122.9828 | 60.7956 | -0.32959 | 122.9645 | -0.18311 | 60.7956 | 122.6852 | 122.9828 | -123.2986 | -123.2391
3390.7812 | 123.1064 | -60.9421 | 62.0911 | 0.095139 | -0.0060798 | -0.0089935 | 0.0092562 | 0.06096 | -0.0060775 | 0.06677 | -61.0565 | 62.2055 | -61.2442 | -61.1893 | 61.7477 | -0.16022 | -0.10071 | 0.11902 | 62.1506 | -61.2717 | -0.30212 | 0.11444 | -0.11444 | -0.24719 | -0.34332 | -0.32959 | 0.05951 | 0.18768 | 60.8414 | 61.0611 | 122.6898 | 123.1476 | -0.11444 | 123.0927 | 60.7819 | -0.32959 | 123.1476 | -0.11444 | 60.7819 | 122.6898 | 123.0927 | -123.3353 | -123.3627
3391.7812 | 123.1522 | -60.9283 | 62.0544 | 0.2401 | -0.0056524 | -0.013052 | 0.0058382 | 0.061387 | -0.0047957 | 0.063779 | -61.0611 | 62.2238 | -61.2854 | -61.171 | 61.7615 | -0.13733 | -0.20599 | 0.12817 | 62.114 | -61.2579 | -0.35706 | 0.16937 | -0.13275 | -0.24261 | -0.29297 | -0.32959 | 0.05951 | 0.2243 | 60.7224 | 61.0565 | 122.6898 | 123.1522 | -0.13275 | 123.0423 | 60.791 | -0.32959 | 123.1522 | -0.13275 | 60.791 | 122.6898 | 123.0423 | -123.3398 | -123.3124
3392.7812 | 123.23 | -60.8688 | 62.059 | -0.11085 | -0.0088568 | -0.017539 | -0.00057036 | 0.059464 | -0.0092819 | 0.064634 | -61.0107 | 62.1414 | -61.2259 | -61.0657 | 61.8942 | 0.050354 | -0.12817 | 0.36163 | 62.1231 | -61.1938 | -0.35706 | 0.082397 | -0.14191 | -0.19684 | -0.16479 | -0.32501 | 0.064087 | 0.21515 | 60.7407 | 61.2305 | 122.7631 | 123.0103 | -0.14191 | 122.9919 | 60.9192 | -0.32501 | 123.0103 | -0.14191 | 60.9192 | 122.7631 | 122.9919 | -123.2849 | -123.2529
3393.7812 | 123.1293 | -60.9009 | 62.0499 | 0.23247 | -0.0067206 | -0.012625 | 0.0056246 | 0.060532 | -0.0077865 | 0.065702 | -61.0657 | 62.1918 | -61.2946 | -61.1755 | 61.7615 | -0.15564 | -0.1831 | 0.12817 | 62.146 | -61.2305 | -0.39368 | 0.14191 | -0.16479 | -0.27466 | -0.28839 | -0.32959 | 0.09613 | 0.22888 | 60.7178 | 61.0291 | 122.6624 | 123.0927 | -0.16479 | 123.0469 | 60.7452 | -0.32959 | 123.0927 | -0.16479 | 60.7452 | 122.6624 | 123.0469 | -123.3444 | -123.2803
3394.7812 | 123.2391 | -60.8917 | 62.0178 | 0.23247 | -0.0052252 | -0.011343 | 0.0041292 | 0.061387 | -0.0056503 | 0.066343 | -61.0428 | 62.146 | -61.2534 | -61.1298 | 61.8301 | -0.068665 | -0.31128 | 0.15564 | 62.1002 | -61.2122 | -0.36163 | 0.12817 | -0.15106 | -0.23804 | -0.18768 | -0.32043 | 0.082398 | 0.21057 | 60.5804 | 61.0474 | 122.7219 | 123.0377 | -0.15106 | 122.9919 | 60.8231 | -0.32043 | 123.0377 | -0.15106 | 60.8231 | 122.7219 | 122.9919 | -123.2712 | -123.23
3395.7812 | 123.2117 | -60.9238 | 62.0316 | 0.22484 | -0.0080024 | -0.015402 | -0.0020658 | 0.059891 | -0.0062911 | 0.067624 | -61.0199 | 62.1231 | -61.2579 | -61.1252 | 61.8484 | -0.082397 | -0.27924 | 0.20599 | 62.0865 | -61.2076 | -0.33417 | 0.091553 | -0.09613 | -0.20142 | -0.1831 | -0.28381 | 0.054932 | 0.23804 | 60.6445 | 61.1298 | 122.7722 | 123.0469 | -0.09613 | 123.0103 | 60.8414 | -0.28381 | 123.0469 | -0.09613 | 60.8414 | 122.7722 | 123.0103 | -123.2895 | -123.2391
3396.7812 | 123.1842 | -60.8917 | 62.0544 | 0.17906 | -0.0077888 | -0.01583 | -0.00014316 | 0.057755 | -0.0075729 | 0.06677 | -61.0611 | 62.114 | -61.2488 | -61.1481 | 61.8027 | -0.10071 | -0.20599 | 0.19684 | 62.114 | -61.1984 | -0.35705 | 0.05951 | -0.16937 | -0.25635 | -0.25177 | -0.3067 | 0.05951 | 0.18768 | 60.6857 | 61.0886 | 122.6944 | 123.0057 | -0.16937 | 123.0057 | 60.791 | -0.3067 | 123.0057 | -0.16937 | 60.791 | 122.6944 | 123.0057 | -123.3032 | -123.2529
3397.7812 | 123.2208 | -60.9009 | 62.027 | 0.21721 | -0.0069342 | -0.012625 | 0.0024202 | 0.05626 | -0.0058639 | 0.065916 | -61.0062 | 62.1414 | -61.2534 | -61.1206 | 61.853 | -0.073242 | -0.28381 | 0.21057 | 62.1002 | -61.2167 | -0.35248 | 0.11444 | -0.10529 | -0.21973 | -0.17395 | -0.31586 | 0.073242 | 0.24719 | 60.6171 | 61.1115 | 122.7539 | 123.0423 | -0.10529 | 123.0011 | 60.8276 | -0.31586 | 123.0423 | -0.10529 | 60.8276 | 122.7539 | 123.0011 | -123.2803 | -123.2437
3398.7812 | 123.2437 | -60.8826 | 62.0361 | 0.27061 | -0.008216 | -0.014975 | 0.0051974 | 0.059678 | -0.0067185 | 0.066984 | -61.0107 | 62.1414 | -61.2259 | -61.1023 | 61.8301 | -0.07782 | -0.3067 | 0.23346 | 62.0773 | -61.2305 | -0.34332 | 0.10529 | -0.12817 | -0.21973 | -0.20599 | -0.3479 | 0.041199 | 0.21515 | 60.5759 | 61.116 | 122.7127 | 123.024 | -0.12817 | 122.9599 | 60.8047 | -0.3479 | 123.024 | -0.12817 | 60.8047 | 122.7127 | 122.9599 | -123.262 | -123.2666
3399.7812 | 123.2712 | -60.8826 | 62.0407 | 0.25536 | -0.007575 | -0.0096343 | 0.005411 | 0.058823 | -0.0073593 | 0.065702 | -60.9833 | 62.1277 | -61.2854 | -61.116 | 61.8347 | -0.086975 | -0.32044 | 0.21057 | 62.1002 | -61.2259 | -0.40283 | 0.086976 | -0.10071 | -0.23346 | -0.20599 | -0.34332 | 0.05951 | 0.30212 | 60.5621 | 61.0931 | 122.7173 | 123.0103 | -0.10071 | 122.9828 | 60.7956 | -0.34332 | 123.0103 | -0.10071 | 60.7956 | 122.7173 | 122.9828 | -123.3261 | -123.2666
3400.7812 | 123.1293 | -60.9421 | 62.0728 | 2.5365 | -0.0054388 | -0.0096343 | 0.005411 | 0.059464 | -0.0058639 | 0.064207 | -61.0931 | 62.1872 | -61.2854 | -61.1755 | 61.7752 | -0.15564 | -0.13275 | 0.11902 | 62.1323 | -61.2762 | -0.34332 | 0.11444 | -0.15106 | -0.23346 | -0.29755 | -0.33417 | 0.059509 | 0.19226 | 60.8093 | 61.0611 | 122.7173 | 123.1293 | -0.15106 | 123.0743 | 60.7864 | -0.33417 | 123.1293 | -0.15106 | 60.7864 | 122.7173 | 123.0743 | -123.3582 | -123.349
3401.7812 | 123.2529 | -60.8871 | 62.0407 | 0.20958 | -0.0073614 | -0.010703 | 0.0039156 | 0.058823 | -0.0058639 | 0.067838 | -61.0336 | 62.1643 | -61.2625 | -61.1023 | 61.8439 | -0.068665 | -0.29755 | 0.21515 | 62.0728 | -61.235 | -0.37537 | 0.1236 | -0.14648 | -0.21515 | -0.19684 | -0.3479 | 0.032044 | 0.22888 | 60.5896 | 61.1023 | 122.731 | 123.0515 | -0.14648 | 122.9599 | 60.8185 | -0.3479 | 123.0515 | -0.14648 | 60.8185 | 122.731 | 122.9599 | -123.3032 | -123.2758
3402.7812 | 123.2391 | -60.8597 | 62.0132 | 1.415 | -0.0097114 | -0.012625 | 0.0022066 | 0.06096 | -0.0043685 | 0.066984 | -60.9558 | 62.1002 | -61.2442 | -61.1069 | 61.8713 | -0.059509 | -0.32044 | 0.21057 | 62.0728 | -61.2213 | -0.38452 | 0.086975 | -0.096131 | -0.24719 | -0.14191 | -0.36163 | 0.059509 | 0.28839 | 60.5392 | 61.0703 | 122.731 | 122.9599 | -0.096131 | 122.9324 | 60.8002 | -0.36163 | 122.9599 | -0.096131 | 60.8002 | 122.731 | 122.9324 | -123.2574 | -123.2346
3403.7812 | 123.23 | -60.9009 | 62.0316 | 0.22484 | -0.0062934 | -0.015616 | 0.0049838 | 0.058396 | -0.0035141 | 0.065275 | -61.0382 | 62.1826 | -61.2625 | -61.1252 | 61.8027 | -0.11444 | -0.27008 | 0.21515 | 62.0911 | -61.2396 | -0.36163 | 0.15106 | -0.13733 | -0.2243 | -0.22888 | -0.33874 | 0.059509 | 0.2243 | 60.6308 | 61.116 | 122.7036 | 123.0835 | -0.13733 | 122.9919 | 60.7864 | -0.33874 | 123.0835 | -0.13733 | 60.7864 | 122.7036 | 122.9919 | -123.2941 | -123.2712
3404.7812 | 123.2529 | -60.8643 | 62.0178 | 0.32402 | -0.0077888 | -0.010703 | 0.0056246 | 0.057542 | -0.0065047 | 0.065061 | -61.0062 | 62.114 | -61.2442 | -61.0199 | 61.853 | -0.082397 | -0.26093 | 0.2243 | 62.0773 | -61.2259 | -0.37994 | 0.096131 | -0.14191 | -0.15564 | -0.1648 | -0.36163 | 0.05951 | 0.23804 | 60.6033 | 61.0886 | 122.7173 | 122.9782 | -0.14191 | 122.9416 | 60.7819 | -0.36163 | 122.9782 | -0.14191 | 60.7819 | 122.7173 | 122.9416 | -123.262 | -123.2437
3405.7812 | 123.1888 | -60.8963 | 62.0407 | 0.15617 | -0.0080024 | -0.014975 | -0.0018522 | 0.057755 | -0.0041549 | 0.065916 | -61.0657 | 62.1231 | -61.2579 | -61.171 | 61.8027 | -0.082397 | -0.20599 | 0.22888 | 62.1231 | -61.1938 | -0.36163 | 0.082398 | -0.16937 | -0.27466 | -0.23804 | -0.29755 | 0.082398 | 0.19226 | 60.6903 | 61.1252 | 122.699 | 123.0194 | -0.16937 | 123.0194 | 60.8139 | -0.29755 | 123.0194 | -0.16937 | 60.8139 | 122.699 | 123.0194 | -123.2986 | -123.2346
3406.7812 | 123.175 | -60.9192 | 62.0865 | -0.18715 | -0.0062934 | -0.012198 | 0.0096834 | 0.059251 | -0.0060775 | 0.067411 | -60.9787 | 62.2604 | -61.2625 | -61.116 | 61.7981 | -0.064087 | -0.10529 | 0.21515 | 62.1643 | -61.2625 | -0.34332 | 0.17395 | -0.05951 | -0.19684 | -0.28839 | -0.34332 | 0.07782 | 0.28381 | 60.8139 | 61.1343 | 122.7173 | 123.1796 | -0.05951 | 123.0835 | 60.8551 | -0.34332 | 123.1796 | -0.05951 | 60.8551 | 122.7173 | 123.0835 | -123.349 | -123.349
3407.7812 | 123.1384 | -60.9467 | 62.0453 | 0.27061 | -0.0043708 | -0.011771 | 0.008829 | 0.058823 | -0.0039413 | 0.064847 | -61.0794 | 62.1964 | -61.2854 | -61.1847 | 61.7477 | -0.16479 | -0.13275 | 0.10529 | 62.1689 | -61.2442 | -0.33875 | 0.15106 | -0.13275 | -0.23804 | -0.29755 | -0.29755 | 0.1236 | 0.20599 | 60.8139 | 61.0519 | 122.6944 | 123.143 | -0.13275 | 123.1155 | 60.7819 | -0.29755 | 123.143 | -0.13275 | 60.7819 | 122.6944 | 123.1155 | -123.3307 | -123.2895
3408.7812 | 123.2117 | -60.878 | 62.0316 | 0.19432 | -0.0084296 | -0.01583 | -0.00057036 | 0.059678 | -0.0052231 | 0.067624 | -61.084 | 62.1185 | -61.2671 | -61.1435 | 61.8118 | -0.091553 | -0.23346 | 0.20142 | 62.0956 | -61.2122 | -0.3891 | 0.086975 | -0.20599 | -0.2655 | -0.21973 | -0.33417 | 0.064087 | 0.18311 | 60.6445 | 61.0794 | 122.6898 | 122.9965 | -0.20599 | 122.9736 | 60.7864 | -0.33417 | 122.9965 | -0.20599 | 60.7864 | 122.6898 | 122.9736 | -123.2986 | -123.2437
3409.7812 | 117.6086 | -36.8271 | 86.4395 | 0.2935 | -0.013984 | -0.016684 | 6.9197 | 0.018876 | -0.0099227 | 7.0016 | -44.0918 | 73.645 | -45.2179 | 0.3479 | 67.2226 | 0.83313 | 67.9047 | 5.1956 | 70.4727 | -34.0485 | -8.3908 | -12.7945 | -7.2647 | 37.175 | -19.2169 | 2.7786 | -15.9668 | 1.1261 | 104.7318 | 42.0227 | 104.0497 | 110.4721 | -7.2647 | 107.2998 | 37.6602 | 2.7786 | 110.4721 | -7.2647 | 37.6602 | 104.0497 | 107.2998 | -131.6574 | -120.488
3410.7812 | 122.8455 | -26.3168 | 96.2677 | 0.087509 | -0.010139 | -0.012412 | -0.00057036 | 0.051987 | -0.0054367 | 0.057798 | -26.5274 | 96.3913 | -26.6464 | -11.3342 | 95.9564 | 0.67291 | 53.334 | 1.4511 | 96.3913 | -26.5915 | -0.32959 | 0.1236 | -0.21057 | 14.9826 | -0.31128 | -0.27466 | 0.1236 | 0.11902 | 79.6509 | 27.7679 | 122.2733 | 122.7081 | -0.21057 | 122.7081 | 26.9897 | -0.27466 | 122.7081 | -0.21057 | 26.9897 | 122.2733 | 122.7081 | -122.9141 | -122.8592
3411.7812 | 122.8912 | -28.2898 | 94.3405 | 0.17143 | -0.010993 | -0.016684 | -0.001425 | 0.05156 | -0.0022323 | 0.059934 | -28.5599 | 94.4824 | -28.6377 | -16.1316 | 93.9926 | 0.48981 | 45.639 | 1.3046 | 94.4321 | -28.624 | -0.3479 | 0.14191 | -0.27008 | 12.1582 | -0.3479 | -0.33417 | 0.091553 | 0.07782 | 73.9288 | 29.5944 | 122.2824 | 122.7722 | -0.27008 | 122.7219 | 28.7796 | -0.33417 | 122.7722 | -0.27008 | 28.7796 | 122.2824 | 122.7219 | -122.9782 | -122.9645
3412.7812 | 122.937 | -21.6385 | 101.0788 | 0.27824 | -0.011207 | -0.015402 | 0.001993 | 0.054978 | -0.0054367 | 0.061216 | -21.8582 | 101.2802 | -21.9681 | -10.7574 | 100.7126 | -10.762 | -19.4824 | 0.76446 | 101.1475 | -21.9543 | -0.32959 | 0.20142 | -0.21973 | 10.881 | -0.36621 | -0.31586 | 0.068665 | 0.10986 | 2.1561 | 22.403 | 122.3511 | 122.9187 | -0.21973 | 122.786 | 10.8765 | -0.31586 | 122.9187 | -0.21973 | 10.8765 | 122.3511 | 122.786 | -123.0469 | -123.0331
3413.7812 | 122.9874 | -20.7184 | 102.0355 | 0.27061 | -0.0094976 | -0.015616 | 0.0028476 | 0.054551 | -0.0028731 | 0.065488 | -20.9793 | 102.2415 | -21.0617 | -10.6201 | 101.6281 | -10.6522 | -21.0342 | 0.72327 | 102.0767 | -21.0297 | -0.34332 | 0.20599 | -0.26093 | 10.0983 | -0.40741 | -0.31128 | 0.041199 | 0.082398 | -0.31586 | 21.4417 | 122.3465 | 122.9599 | -0.26093 | 122.7951 | 10.0662 | -0.31128 | 122.9599 | -0.26093 | 10.0662 | 122.3465 | 122.7951 | -123.0972 | -123.0652
3414.7812 | 122.937 | -20.4254 | 102.4109 | 0.095139 | -0.0067206 | -0.017111 | 0.01182 | 0.055405 | -0.0041549 | 0.071683 | -20.5719 | 102.6581 | -20.7413 | -10.4919 | 101.9714 | -10.5515 | -20.4895 | 0.75073 | 102.507 | -20.7184 | -0.31586 | 0.24719 | -0.14648 | 9.9335 | -0.43945 | -0.29297 | 0.09613 | 0.16937 | -0.064087 | 21.1761 | 122.3969 | 123.0835 | -0.14648 | 122.9324 | 9.874 | -0.29297 | 123.0835 | -0.14648 | 9.874 | 122.3969 | 122.9324 | -123.1522 | -123.1293
3415.7812 | 122.8912 | -14.2685 | 108.6273 | 0.064621 | -0.009284 | -0.018393 | 0.0084018 | 0.0616 | -0.0043685 | 0.078092 | -14.4608 | 108.8242 | -14.5889 | -13.8153 | 108.046 | -13.8519 | 101.0834 | 1.8082 | 108.6823 | -14.5752 | -0.32043 | 0.19684 | -0.19226 | 0.45319 | -0.58136 | -0.3067 | 0.054932 | 0.12817 | 115.3519 | 16.0767 | 122.3145 | 123.0927 | -0.19226 | 122.9507 | 0.41657 | -0.3067 | 123.0927 | -0.19226 | 0.41657 | 122.3145 | 122.9507 | -123.2162 | -123.2025
3416.7812 | 122.8821 | -11.9064 | 111.0397 | 0.064621 | -0.0080024 | -0.017111 | 0.030191 | 0.060319 | -0.0050095 | 0.0939 | -12.0117 | 111.2732 | -12.1857 | -11.348 | 110.4767 | -11.4212 | 102.4704 | 1.6205 | 111.1267 | -12.1674 | -0.27924 | 0.23346 | -0.10529 | 0.55847 | -0.56305 | -0.26093 | 0.086975 | 0.17395 | 114.3768 | 13.5269 | 122.3831 | 123.1796 | -0.10529 | 123.0331 | 0.48523 | -0.26093 | 123.1796 | -0.10529 | 0.48523 | 122.3831 | 123.0331 | -123.2254 | -123.2071
3417.7812 | 123.0881 | -12.2498 | 110.6003 | 0.22484 | -0.010779 | -0.014121 | 0.030619 | 0.060319 | -0.0050095 | 0.12381 | -12.3962 | 110.7605 | -12.5885 | -11.5128 | 110.1791 | -11.5082 | -9.2239 | 0.95673 | 110.6827 | -12.5336 | -0.33875 | 0.16022 | -0.14648 | 0.737 | -0.42114 | -0.28381 | 0.082397 | 0.19226 | 3.0258 | 13.2065 | 122.4289 | 123.0103 | -0.14648 | 122.9324 | 0.74158 | -0.28381 | 123.0103 | -0.14648 | 0.74158 | 122.4289 | 122.9324 | -123.1888 | -123.1338
3418.7812 | 123.0011 | -12.7991 | 110.0922 | 0.23247 | -0.010139 | -0.017539 | 0.20494 | 0.060105 | -0.0052231 | 0.27676 | -12.941 | 110.3348 | -13.1424 | -10.3546 | 109.5657 | -10.3867 | -9.9152 | 1.0025 | 110.1791 | -13.0783 | -0.34332 | 0.24262 | -0.14191 | 2.4445 | -0.52643 | -0.27924 | 0.086975 | 0.20142 | 2.8839 | 13.8016 | 122.3648 | 123.1338 | -0.14191 | 122.9782 | 2.4124 | -0.27924 | 123.1338 | -0.14191 | 2.4124 | 122.3648 | 122.9782 | -123.2346 | -123.1705
3419.7812 | 123.0469 | -12.7487 | 110.0739 | 0.27061 | -0.012061 | -0.017539 | 0.030832 | 0.059678 | -0.0030869 | 0.099241 | -12.9135 | 110.3485 | -13.1241 | -11.8469 | 109.6619 | -11.8698 | -10.9497 | 0.70496 | 110.1791 | -13.0463 | -0.37537 | 0.27466 | -0.16479 | 0.90179 | -0.41199 | -0.29755 | 0.10528 | 0.21057 | 1.799 | 13.4537 | 122.4106 | 123.0972 | -0.16479 | 122.9279 | 0.87891 | -0.29755 | 123.0972 | -0.16479 | 0.87891 | 122.4106 | 122.9279 | -123.1979 | -123.1201
3420.7812 | 122.8821 | -21.2631 | 101.5457 | 0.21721 | -0.0062934 | -0.015616 | 0.004343 | -0.0048365 | -0.0039413 | 0.0014014 | -21.4462 | 101.7654 | -21.5698 | 100.795 | 101.0971 | 100.4334 | -19.8624 | -21.2173 | 101.6556 | -21.5286 | -0.3067 | 0.21973 | -0.18311 | 122.0581 | -0.44861 | -0.2655 | 0.10986 | 0.1236 | 1.4008 | 0.045777 | 122.3602 | 123.0286 | -0.18311 | 122.9187 | 121.6965 | -0.2655 | 123.0286 | -0.18311 | 121.6965 | 122.3602 | 122.9187 | -123.1155 | -123.0743
3421.7812 | 122.9462 | -17.6559 | 105.1941 | 0.28587 | -0.0090704 | -0.014121 | 0.0028476 | -0.0033411 | -0.0045821 | 0.0041784 | -17.8757 | 105.4459 | -17.9855 | 105.0705 | 104.7134 | 104.6585 | -16.1591 | -17.6193 | 105.3085 | -17.9398 | -0.32959 | 0.25177 | -0.21973 | 122.7264 | -0.48065 | -0.28381 | 0.11444 | 0.10986 | 1.4969 | 0.036621 | 122.3694 | 123.1018 | -0.21973 | 122.9645 | 122.3145 | -0.28381 | 123.1018 | -0.21973 | 122.3145 | 122.3694 | 122.9645 | -123.1796 | -123.1338
3422.7812 | 123.0652 | -17.0609 | 105.7159 | 0.26299 | -0.011634 | -0.014334 | 0.003702 | -0.0069727 | -0.0024459 | 0.008451 | -17.2531 | 105.9402 | -17.395 | 105.8075 | 105.3726 | 105.4138 | 71.5118 | -16.9418 | 105.8395 | -17.3447 | -0.33417 | 0.22431 | -0.19226 | 122.8683 | -0.34332 | -0.28381 | 0.1236 | 0.14191 | 88.5727 | 0.11902 | 122.4335 | 123.0011 | -0.19226 | 122.9004 | 122.4747 | -0.28381 | 123.0011 | -0.19226 | 122.4747 | 122.4335 | 122.9004 | -123.111 | -123.0606
3423.7812 | 123.0103 | -17.2531 | 105.6335 | 0.2401 | -0.0088568 | -0.010703 | 0.0032748 | -0.0048365 | -0.0039413 | 0.0056738 | -17.45 | 105.899 | -17.5735 | 105.6244 | 105.1804 | 105.1987 | -15.6372 | -17.1844 | 105.7755 | -17.5278 | -0.32043 | 0.2655 | -0.19684 | 122.8775 | -0.45319 | -0.27466 | 0.14191 | 0.1236 | 1.6159 | 0.068665 | 122.4335 | 123.1522 | -0.19684 | 123.0286 | 122.4518 | -0.27466 | 123.1522 | -0.19684 | 122.4518 | 122.4335 | 123.0286 | -123.2071 | -123.1613
3424.7812 | 122.9691 | -18.7683 | 104.0955 | 0.23247 | -0.0094976 | -0.013907 | 0.003702 | -0.0044091 | -0.0060775 | 0.004392 | -18.9743 | 104.361 | -19.0842 | 104.1229 | 103.6743 | 103.7155 | -17.3401 | -18.7408 | 104.2694 | -19.0521 | -0.31586 | 0.2655 | -0.20599 | 122.8912 | -0.42114 | -0.28381 | 0.17395 | 0.10986 | 1.4282 | 0.027466 | 122.4426 | 123.1293 | -0.20599 | 123.0377 | 122.4838 | -0.28381 | 123.1293 | -0.20599 | 122.4838 | 122.4426 | 123.0377 | -123.1796 | -123.1476
3425.7812 | 123.0743 | -22.1924 | 100.6119 | 0.27061 | -0.008216 | -0.014121 | 0.002634 | -0.0033411 | -0.0028731 | 0.0031104 | -22.4304 | 100.8545 | -22.5449 | 100.7126 | 100.2731 | 100.351 | -20.7642 | -22.197 | 100.7355 | -22.5082 | -0.35248 | 0.24261 | -0.23804 | 122.905 | -0.33875 | -0.31586 | 0.1236 | 0.11444 | 1.4282 | -0.004577 | 122.4655 | 123.0469 | -0.23804 | 122.9279 | 122.5433 | -0.31586 | 123.0469 | -0.23804 | 122.5433 | 122.4655 | 122.9279 | -123.1567 | -123.1201
3426.7812 | 123.0103 | -22.7417 | 100.1724 | 0.17143 | -0.0062934 | -0.014975 | 0.0045566 | -0.0048365 | -0.0058639 | 0.0035376 | -22.9614 | 100.4242 | -23.0438 | 100.1175 | 99.7238 | 99.7421 | -21.1395 | -22.7417 | 100.2777 | -23.0164 | -0.30212 | 0.25177 | -0.21973 | 122.8592 | -0.44861 | -0.27466 | 0.10529 | 0.082397 | 1.6022 | 0 | 122.4655 | 123.1659 | -0.21973 | 123.0194 | 122.4838 | -0.27466 | 123.1659 | -0.21973 | 122.4838 | 122.4655 | 123.0194 | -123.2162 | -123.1888
3427.7812 | 123.0698 | -19.6106 | 103.3218 | 0.18669 | -0.009284 | -0.017111 | 0.0079744 | -0.0044091 | -0.0047957 | 0.0046056 | -19.8349 | 103.5873 | -19.9219 | 103.2944 | 102.8458 | 102.8641 | -15.3534 | -19.5969 | 103.4271 | -19.8807 | -0.31128 | 0.2655 | -0.2243 | 122.905 | -0.47607 | -0.27008 | 0.10529 | 0.086975 | 4.2572 | 0.013733 | 122.4564 | 123.1979 | -0.2243 | 123.0377 | 122.4747 | -0.27008 | 123.1979 | -0.2243 | 122.4747 | 122.4564 | 123.0377 | -123.2437 | -123.2025
3428.7812 | 123.056 | -23.3231 | 99.6277 | 0.26299 | -0.0090704 | -0.01647 | 0.0066928 | -0.0056909 | -0.0043685 | 0.010587 | -24.115 | 99.234 | -24.2935 | 96.8903 | 98.4421 | 99.4949 | -18.1229 | -23.0484 | 99.2935 | -23.9456 | -0.97046 | -0.39368 | -0.79193 | 120.2133 | -1.1856 | -0.62256 | -0.33417 | 0.17853 | 5.2002 | 0.27466 | 121.7651 | 122.5571 | -0.79193 | 122.6166 | 122.818 | -0.62256 | 122.5571 | -0.79193 | 122.818 | 121.7651 | 122.6166 | -123.9212 | -123.5733
3429.7812 | 123.0927 | -29.1229 | 93.7958 | 0.23247 | -0.010993 | -0.015402 | 0.00712 | -0.0059045 | -0.0026595 | 0.01016 | -29.0131 | 95.0684 | -28.45 | 92.8848 | 92.7383 | 92.1387 | -24.7467 | -29.5029 | 93.3426 | -29.7684 | 0.67291 | 1.2726 | 0.10986 | 122.0078 | -1.0574 | -0.64545 | -0.45319 | -0.56305 | 4.3762 | -0.37994 | 121.8613 | 124.1913 | 0.10986 | 122.4655 | 121.2616 | -0.64545 | 124.1913 | 0.10986 | 121.2616 | 121.8613 | 122.4655 | -122.2458 | -123.5641
3430.7812 | 123.0103 | -19.5831 | 103.4134 | 0.095139 | -0.010993 | -0.017966 | 0.0079744 | -0.0059045 | -0.0054367 | 0.0069556 | -19.7159 | 103.6423 | -19.8441 | 103.4042 | 102.8824 | 102.951 | -14.447 | -19.5648 | 103.4775 | -19.8853 | -0.26093 | 0.22888 | -0.13275 | 122.9874 | -0.53101 | -0.30212 | 0.064087 | 0.12817 | 5.1361 | 0.018311 | 122.4655 | 123.2254 | -0.13275 | 123.0606 | 122.5342 | -0.30212 | 123.2254 | -0.13275 | 122.5342 | 122.4655 | 123.0606 | -123.2574 | -123.2986
3431.7812 | 123.0469 | -20.0455 | 102.7863 | 0.27061 | -0.0073614 | -0.014975 | 0.0066928 | -0.0078271 | -0.0035141 | 0.0080236 | -20.3979 | 103.1754 | -20.3247 | 102.9602 | 102.4475 | 102.4338 | -14.9139 | -20.0043 | 103.0151 | -20.3064 | -0.27924 | 0.3891 | -0.35248 | 123.0057 | -0.33875 | -0.26093 | 0.22888 | -0.073242 | 5.1315 | 0.041199 | 122.493 | 123.2208 | -0.35248 | 123.0606 | 122.4792 | -0.26093 | 123.2208 | -0.35248 | 122.4792 | 122.493 | 123.0606 | -123.111 | -123.0927
3432.7812 | 123.0469 | -20.6863 | 102.2324 | 0.23247 | -0.0077888 | -0.013266 | 0.0047702 | -0.0059045 | -0.0043685 | 0.0073828 | -21.0022 | 102.3926 | -21.0938 | 102.1225 | 101.7105 | 101.8616 | -15.5777 | -20.7047 | 102.2919 | -21.048 | -0.40741 | 0.16022 | -0.31586 | 122.8088 | -0.52185 | -0.36163 | 0.059509 | 0.091553 | 5.1086 | -0.018311 | 122.3969 | 123.0789 | -0.31586 | 122.9782 | 122.5479 | -0.36163 | 123.0789 | -0.31586 | 122.5479 | 122.3969 | 122.9782 | -123.3261 | -123.2803
3433.7812 | 123.143 | -20.7184 | 102.2003 | 1.5524 | -0.012488 | -0.017325 | 0.002634 | -0.0071863 | -0.0056503 | 0.0058874 | -20.8099 | 102.3239 | -21.0297 | 102.2369 | 101.7654 | 101.857 | -15.889 | -20.6497 | 102.2278 | -21.0251 | -0.31128 | 0.1236 | -0.091553 | 122.9553 | -0.43488 | -0.3067 | 0.027466 | 0.21973 | 4.8294 | 0.068665 | 122.4838 | 123.0423 | -0.091553 | 122.9462 | 122.5754 | -0.3067 | 123.0423 | -0.091553 | 122.5754 | 122.4838 | 122.9462 | -123.23 | -123.2254
3434.7812 | 123.0286 | -28.3539 | 94.5374 | 0.14854 | -0.006507 | -0.018393 | 0.0073336 | -0.0076135 | -0.0056503 | 0.0037512 | -28.5599 | 94.8853 | -28.624 | 94.6518 | 94.1849 | 94.1254 | -23.4558 | -28.1113 | 94.6884 | -28.6606 | -0.27008 | 0.3479 | -0.20599 | 123.0057 | -0.35248 | -0.3067 | 0.15106 | 0.064087 | 4.8981 | 0.24261 | 122.5388 | 123.2391 | -0.20599 | 123.0423 | 122.4792 | -0.3067 | 123.2391 | -0.20599 | 122.4792 | 122.5388 | 123.0423 | -123.1613 | -123.1979
3435.7812 | 123.024 | -22.1008 | 100.8865 | 0.072251 | -0.0088568 | -0.014548 | 0.0062656 | -0.0059045 | -0.0071457 | 0.005033 | -22.348 | 101.0376 | -22.4487 | 100.8682 | 100.3418 | 100.4471 | -17.2668 | -22.1512 | 100.946 | -22.4167 | -0.3479 | 0.15106 | -0.24719 | 122.9691 | -0.54474 | -0.31586 | 0.059509 | 0.10071 | 4.834 | -0.050354 | 122.4426 | 123.1384 | -0.24719 | 123.0469 | 122.5479 | -0.31586 | 123.1384 | -0.24719 | 122.5479 | 122.4426 | 123.0469 | -123.3353 | -123.3032
3436.7812 | 123.0423 | -18.8141 | 104.1733 | 0.26299 | -0.0094976 | -0.016684 | 0.005411 | -0.0039819 | -0.0041549 | 0.0065284 | -19.0338 | 104.4113 | -19.1254 | 104.1916 | 103.6789 | 103.7888 | -14.0671 | -18.7912 | 104.3106 | -19.0933 | -0.31128 | 0.23804 | -0.21973 | 123.0057 | -0.49438 | -0.27924 | 0.13733 | 0.091553 | 4.747 | 0.022888 | 122.493 | 123.2254 | -0.21973 | 123.1247 | 122.6028 | -0.27924 | 123.2254 | -0.21973 | 122.6028 | 122.493 | 123.1247 | -123.2986 | -123.2666
3437.7812 | 123.1338 | -19.4366 | 103.4454 | 0.17906 | -0.011207 | -0.015616 | 0.00028404 | -0.0048365 | -0.0028731 | 0.0086646 | -19.6793 | 103.5645 | -19.8395 | 103.5095 | 103.0472 | 103.1799 | -14.9689 | -19.3451 | 103.5507 | -19.7433 | -0.40283 | 0.11902 | -0.24261 | 122.9462 | -0.39826 | -0.3067 | 0.10528 | 0.16022 | 4.4678 | 0.091553 | 122.4838 | 123.0011 | -0.24261 | 122.9874 | 122.6166 | -0.3067 | 123.0011 | -0.24261 | 122.6166 | 122.4838 | 122.9874 | -123.2849 | -123.1888
3438.7812 | 123.1201 | -19.606 | 103.2898 | 0.2401 | -0.010993 | -0.013266 | 0.00071144 | -0.0056909 | -0.0058639 | 0.0069556 | -19.7754 | 103.5049 | -19.9173 | 103.4637 | 102.919 | 103.0792 | -15.2573 | -19.5236 | 103.3813 | -19.899 | -0.31128 | 0.21515 | -0.16937 | 123.0698 | -0.37079 | -0.29297 | 0.091553 | 0.14191 | 4.3488 | 0.082397 | 122.525 | 123.111 | -0.16937 | 122.9874 | 122.6852 | -0.29297 | 123.111 | -0.16937 | 122.6852 | 122.525 | 122.9874 | -123.2071 | -123.1888
3439.7812 | 123.1201 | -19.7159 | 103.2486 | 0.072251 | -0.010779 | -0.02117 | 0.00028404 | -0.0093225 | -0.0056503 | 0.0048194 | -20.0043 | 103.3768 | -20.0546 | 103.3081 | 102.8091 | 102.9602 | -15.2161 | -19.6198 | 103.2852 | -20.018 | -0.33874 | 0.12817 | -0.28839 | 123.024 | -0.43945 | -0.30212 | 0.036621 | 0.050354 | 4.4998 | 0.09613 | 122.525 | 123.0927 | -0.28839 | 123.0011 | 122.6761 | -0.30212 | 123.0927 | -0.28839 | 122.6761 | 122.525 | 123.0011 | -123.3032 | -123.2666
3440.7812 | 122.9919 | -22.7921 | 100.5249 | 0.30876 | -0.0084296 | -0.0098479 | 0.88062 | 0.016099 | -0.0037277 | 0.93792 | -22.2107 | 101.7929 | -21.7621 | 59.0012 | 101.2985 | 59.2667 | -10.4279 | -23.5336 | 100.3281 | -22.8195 | 1.03 | 1.268 | 0.58136 | 81.7932 | 0.77362 | -0.027466 | -0.19684 | -0.44861 | 12.3642 | -0.74158 | 124.0906 | 124.585 | 0.58136 | 123.1201 | 82.0587 | -0.027466 | 124.585 | 0.58136 | 82.0587 | 124.0906 | 123.1201 | -122.287 | -123.3444
3441.7812 | 123.1522 | -3.3234 | 119.6274 | 0.30113 | -0.01142 | -0.016684 | 0.0022066 | 0.038102 | -0.0020187 | 0.063566 | -3.3325 | 119.7418 | -3.653 | 32.9864 | 119.0048 | 32.8995 | -3.1769 | -2.6871 | 119.7647 | -3.6987 | -0.32959 | 0.11444 | -0.009156 | 36.3098 | -0.62256 | -0.37537 | 0.13733 | 0.32043 | 0.14648 | 0.63629 | 122.3282 | 123.0652 | -0.009156 | 123.0881 | 36.2228 | -0.37537 | 123.0652 | -0.009156 | 36.2228 | 122.3282 | 123.0881 | -123.2803 | -123.3261
3442.7812 | 123.1522 | -6.1478 | 116.8076 | 0.24773 | -0.010352 | -0.012198 | 0.0069064 | 0.036607 | -0.0024459 | 0.056943 | -6.0837 | 117.1371 | -6.4041 | 37.3077 | 116.2903 | 36.6669 | -6.0333 | -5.8914 | 116.9174 | -6.4362 | -0.25635 | 0.32959 | 0.064087 | 43.4555 | -0.51727 | -0.28839 | 0.10986 | 0.32043 | 0.11444 | 0.25635 | 122.438 | 123.2849 | 0.064087 | 123.0652 | 42.8146 | -0.28839 | 123.2849 | 0.064087 | 42.8146 | 122.438 | 123.0652 | -123.2117 | -123.2437
3443.7812 | 123.0423 | -13.1424 | 109.7443 | 0.35454 | -0.006507 | -0.014121 | 0.12376 | 0.018662 | -0.0033005 | 0.15884 | -13.353 | 109.9091 | -13.5361 | 60.2371 | 109.3323 | 59.9716 | 65.1627 | -13.1882 | 109.8633 | -13.3804 | -0.39368 | 0.16479 | -0.21057 | 73.3795 | -0.41199 | -0.23804 | 0.11902 | 0.18311 | 78.3051 | -0.045776 | 122.4747 | 123.0515 | -0.21057 | 123.0057 | 73.114 | -0.23804 | 123.0515 | -0.21057 | 73.114 | 122.4747 | 123.0057 | -123.2803 | -123.1247
3444.7812 | 121.9162 | -2.8107 | 113.3057 | 0.32402 | -0.0094976 | -0.016898 | 0.022074 | -0.0022729 | -0.0041549 | 0.021696 | -2.948 | 119.8059 | -3.035 | 118.6111 | 119.0369 | 117.8009 | 115.4068 | 116.3818 | 119.7006 | -3.1174 | -0.2243 | 6.5002 | -0.13733 | 121.4218 | 5.7312 | -0.3067 | 6.395 | 0.086975 | 118.2175 | 119.1925 | 121.8475 | 122.6166 | -0.13733 | 122.5113 | 120.6116 | -0.3067 | 122.6166 | -0.13733 | 120.6116 | 121.8475 | 122.5113 | -116.3406 | -116.423
3445.7812 | 122.7905 | -49.4339 | 73.3383 | -0.61439 | -0.010352 | -0.016257 | 0.38224 | 0.047501 | -0.0050095 | 0.50235 | -48.967 | 74.1165 | -49.0585 | -25.1724 | 70.166 | -23.6938 | 29.0634 | 29.1962 | 72.2717 | -50.1938 | 0.37537 | 0.7782 | 0.46692 | 24.2615 | -3.1723 | -0.75989 | -1.0666 | 0.091553 | 78.4973 | 78.6301 | 119.5999 | 123.5504 | 0.46692 | 121.7056 | 25.7401 | -0.75989 | 123.5504 | 0.46692 | 25.7401 | 119.5999 | 121.7056 | -122.3969 | -123.5321
3446.7812 | 123.3856 | -50.7202 | 70.816 | 0.32402 | -0.0094976 | -0.017325 | 0.47196 | 0.01674 | -0.0077865 | 0.48932 | -48.8571 | 73.8052 | -48.999 | 32.3227 | 71.933 | 30.7892 | 22.7966 | 21.9406 | 71.2372 | -51.4114 | 1.7212 | 2.9892 | 1.8631 | 83.0429 | 1.1169 | -0.69122 | 0.42114 | 0.14191 | 73.5168 | 72.6608 | 122.6532 | 124.5255 | 1.8631 | 121.9574 | 81.5094 | -0.69122 | 124.5255 | 1.8631 | 81.5094 | 122.6532 | 121.9574 | -119.8151 | -122.2275
3447.7812 | 115.3885 | -1.2405 | 100.5295 | 0.26299 | -0.0080024 | -0.017752 | 0.0058382 | 0.056473 | -0.0026595 | 0.069974 | -0.95215 | 121.8704 | -1.3092 | 11.586 | 121.019 | 11.554 | 103.8895 | 0.11902 | 121.7239 | -1.2909 | -0.068664 | 21.3409 | 0.28839 | 12.8265 | 20.4895 | -0.050354 | 21.1945 | 0.35706 | 105.13 | 1.3596 | 122.2595 | 123.111 | 0.28839 | 122.9645 | 12.7945 | -0.050354 | 123.111 | 0.28839 | 12.7945 | 122.2595 | 122.9645 | -101.8387 | -101.8204
3448.7812 | 111.5616 | -1.0574 | 93.5028 | 0.072251 | -0.0090704 | -0.016898 | 0.021006 | 0.057542 | -0.0058639 | 0.085996 | -0.84228 | 122.0993 | -1.2131 | 7.6767 | 121.2204 | 7.1182 | 5.809 | 0.10986 | 121.9437 | -1.0895 | -0.15564 | 28.5965 | 0.21515 | 8.7341 | 27.7176 | -0.032044 | 28.4409 | 0.37079 | 6.8665 | 1.1673 | 122.2778 | 123.1567 | 0.21515 | 123.0011 | 8.1757 | -0.032044 | 123.1567 | 0.21515 | 8.1757 | 122.2778 | 123.0011 | -94.7159 | -94.5923
3449.7812 | 122.5937 | -1.5472 | 118.2724 | 0.2401 | -0.0084296 | -0.017111 | 0.075907 | 0.058823 | -0.0035141 | 0.14795 | -1.6846 | 121.3074 | -2.0325 | 4.4449 | 120.4285 | 4.3259 | 4.9667 | 0.12817 | 121.1288 | -1.973 | -0.48523 | 3.035 | -0.13733 | 5.9921 | 2.1561 | -0.42572 | 2.8564 | 0.3479 | 6.514 | 1.6754 | 121.9757 | 122.8546 | -0.13733 | 122.6761 | 5.8731 | -0.42572 | 122.8546 | -0.13733 | 5.8731 | 121.9757 | 122.6761 | -120.3049 | -120.2454
3450.7812 | 122.6303 | -1.6388 | 120.108 | 0.27824 | -0.010993 | -0.017325 | 0.30363 | 0.057328 | -0.0052231 | 0.384 | -1.6159 | 121.3211 | -2.0325 | 6.6513 | 120.4376 | 6.5781 | 5.1086 | 0.18768 | 121.1929 | -1.9272 | -0.39368 | 1.2131 | 0.022888 | 8.2901 | 0.32959 | -0.28839 | 1.0849 | 0.41657 | 6.7474 | 1.8265 | 122.0764 | 122.9599 | 0.022888 | 122.8317 | 8.2169 | -0.28839 | 122.9599 | 0.022888 | 8.2169 | 122.0764 | 122.8317 | -122.1405 | -122.0352
3451.7812 | 122.8363 | -0.3479 | 115.7776 | 3.2156 | -0.0090704 | -0.025015 | 0.037027 | 0.054978 | 0.039424 | 0.14111 | -0.33417 | 122.8134 | -0.60883 | 11.1694 | 38.9008 | 10.5377 | 2.2339 | 0.11444 | 122.5754 | -0.60425 | -0.26093 | 7.0358 | 0.013733 | 11.5173 | -76.8768 | -0.25635 | 6.7978 | 0.27466 | 2.5818 | 0.46234 | 39.2487 | 123.1613 | 0.013733 | 122.9233 | 10.8856 | -0.25635 | 123.1613 | 0.013733 | 10.8856 | 39.2487 | 122.9233 | -116.3864 | -116.3818
3452.7812 | 122.8546 | -1.918 | 120.0714 | 0.20195 | -0.012488 | -0.016043 | 0.62321 | 0.047501 | 0.050319 | 0.69995 | -1.8494 | 120.9778 | -2.2842 | 23.616 | 17.9993 | 22.4762 | 25.2731 | 0.23804 | 120.8084 | -2.124 | -0.36621 | 0.90637 | 0.068665 | 25.5341 | -102.0721 | -0.20599 | 0.737 | 0.43488 | 27.1912 | 2.1561 | 19.9173 | 122.8958 | 0.068665 | 122.7264 | 24.3942 | -0.20599 | 122.8958 | 0.068665 | 24.3942 | 19.9173 | 122.7264 | -122.3557 | -122.1954
3453.7812 | 122.8729 | -1.3687 | 120.6894 | 0.2401 | -0.0086432 | -0.019461 | 0.51725 | 0.053483 | 0.055446 | 0.72259 | -1.3046 | 121.7331 | -1.6342 | 12.0392 | 11.2427 | 9.2926 | 18.8095 | 0.19226 | 121.4905 | -1.5656 | -0.2655 | 1.0437 | 0.064087 | 13.4079 | -109.4467 | -0.19684 | 0.80109 | 0.32959 | 20.1782 | 1.561 | 12.6114 | 123.1018 | 0.064087 | 122.8592 | 10.6613 | -0.19684 | 123.1018 | 0.064087 | 10.6613 | 12.6114 | 122.8592 | -122.3236 | -122.2549
3454.7812 | 122.4243 | -0.33875 | 120.369 | 2.857 | -0.007575 | -0.013907 | 0.034891 | 0.060105 | 0.061427 | 0.15606 | -0.3479 | 122.8317 | -0.61798 | 2.5772 | 4.2938 | 2.6642 | 2.8564 | 0.09613 | 122.6395 | -0.56763 | -0.27924 | 2.4628 | -0.009155 | 2.916 | -116.0751 | -0.22888 | 2.2705 | 0.27008 | 3.1952 | 0.43488 | 4.6326 | 123.1705 | -0.009155 | 122.9782 | 3.0029 | -0.22888 | 123.1705 | -0.009155 | 3.0029 | 4.6326 | 122.9782 | -120.9869 | -120.9366
3455.7812 | 102.3788 | -2.1652 | 100.5753 | 0.22484 | -0.010139 | -0.017752 | 0.02656 | 0.0037085 | -0.0041549 | 0.044126 | -1.9592 | 120.6253 | -2.4811 | 106.0638 | 119.7922 | 106.4758 | 120.1675 | 0.009155 | 120.6482 | -2.2202 | -0.31586 | 20.05 | 0.20599 | 108.2291 | 19.2169 | -0.054932 | 20.0729 | 0.52185 | 122.3328 | 2.1744 | 121.9574 | 122.7905 | 0.20599 | 122.8134 | 108.6411 | -0.054932 | 122.7905 | 0.20599 | 108.6411 | 121.9574 | 122.8134 | -103.0563 | -102.7954
3456.7812 | 117.485 | -7.6859 | 91.3376 | -0.14137 | -0.0069342 | -0.016898 | 0.25514 | 0.034257 | -0.0056503 | 0.30987 | -7.5943 | 115.2878 | -7.8644 | 43.0206 | 114.4272 | 42.8925 | 114.8392 | -1.6617 | 115.1047 | -7.8323 | -0.17853 | 23.9502 | 0.091553 | 50.7065 | 23.0896 | -0.14648 | 23.7671 | 0.27008 | 122.525 | 6.0242 | 122.113 | 122.9736 | 0.091553 | 122.7905 | 50.5783 | -0.14648 | 122.9736 | 0.091553 | 50.5783 | 122.113 | 122.7905 | -99.202 | -99.1699
3457.7812 | 122.2366 | -5.0217 | 116.4597 | 0.28587 | -0.011634 | -0.016257 | 0.26582 | 0.013322 | -0.0030869 | 0.28424 | -4.7241 | 118.2404 | -4.8935 | 89.0808 | 116.5329 | 87.149 | 116.4551 | -1.6891 | 117.5491 | -5.3604 | 0.12817 | 1.7807 | 0.29755 | 94.1025 | 0.073242 | -0.33875 | 1.0895 | 0.16937 | 121.4767 | 3.3325 | 121.5546 | 123.262 | 0.29755 | 122.5708 | 92.1707 | -0.33875 | 123.262 | 0.29755 | 92.1707 | 121.5546 | 122.5708 | -121.3531 | -121.8201
3458.7812 | 122.0169 | -5.2872 | 100.708 | 0.27061 | -0.0077888 | -0.016257 | 0.40425 | 0.048142 | 0.0563 | 0.51516 | -5.6122 | 117.3065 | -5.9235 | 14.2776 | 1.6937 | 14.0625 | 116.2354 | 0.37079 | 117.1371 | -5.8548 | -0.63629 | 16.5985 | -0.32501 | 19.5648 | -99.0143 | -0.56763 | 16.4291 | 0.31128 | 121.5225 | 5.658 | 6.9809 | 122.5937 | -0.32501 | 122.4243 | 19.3497 | -0.56763 | 122.5937 | -0.32501 | 19.3497 | 6.9809 | 122.4243 | -106.6315 | -106.5628
3459.7812 | 116.2903 | -2.4307 | 96.0297 | 0.041733 | -0.0077888 | -0.016043 | 0.3816 | 0.05861 | 0.059932 | 0.51474 | -2.2522 | 120.6802 | -2.6047 | 4.7287 | 1.1719 | 4.7195 | 120.2728 | -1.4511 | 120.5887 | -2.4673 | -0.17395 | 24.6506 | 0.17853 | 7.1594 | -94.8578 | -0.036621 | 24.559 | 0.35248 | 122.7036 | 0.97961 | 3.6026 | 123.111 | 0.17853 | 123.0194 | 7.1503 | -0.036621 | 123.111 | 0.17853 | 7.1503 | 3.6026 | 123.0194 | -98.6343 | -98.497
3460.7812 | 122.7036 | -2.179 | 95.3659 | 0.19432 | -0.010139 | -0.011984 | 0.085947 | 0.05391 | 0.058223 | 0.2146 | -2.3529 | 120.5017 | -2.7832 | 11.7416 | 3.9505 | 11.6089 | 11.6135 | 0.16022 | 120.314 | -2.6367 | -0.60425 | 25.1358 | -0.17395 | 13.9206 | -91.4154 | -0.45776 | 24.9481 | 0.4303 | 13.7924 | 2.3392 | 6.1295 | 122.6807 | -0.17395 | 122.493 | 13.7878 | -0.45776 | 122.6807 | -0.17395 | 13.7878 | 6.1295 | 122.493 | -98.1491 | -98.0026
3461.7812 | 123.0927 | -1.561 | 120.639 | -1.9343 | -0.011207 | -0.016043 | 0.019297 | 0.057755 | 0.060573 | 0.26266 | -1.442 | 121.4951 | -1.8356 | 5.1086 | 1.3229 | 4.7333 | 6.6376 | 0.10071 | 121.2982 | -1.8036 | -0.27466 | 0.85602 | 0.11902 | 6.6696 | -119.3161 | -0.24262 | 0.65918 | 0.39368 | 8.1985 | 1.6617 | 2.8839 | 123.056 | 0.11902 | 122.8592 | 6.2942 | -0.24262 | 123.056 | 0.11902 | 6.2942 | 2.8839 | 122.8592 | -122.4747 | -122.4426
3462.7812 | 122.699 | -1.918 | 105.7434 | 0.12566 | -0.0077888 | -0.017752 | 0.1009 | 0.057755 | 0.060786 | 0.22571 | -2.092 | 120.8633 | -2.504 | 6.7703 | 1.8585 | 6.8344 | 9.7092 | 0.10071 | 120.8038 | -2.2614 | -0.58594 | 15.1199 | -0.17395 | 8.6884 | -103.8849 | -0.34332 | 15.0604 | 0.41199 | 11.6272 | 2.0187 | 3.7766 | 122.7814 | -0.17395 | 122.7219 | 8.7524 | -0.34332 | 122.7814 | -0.17395 | 8.7524 | 3.7766 | 122.7219 | -108.2474 | -108.0048
3463.7812 | 122.7768 | -3.1998 | 102.2232 | -0.034561 | -0.010779 | -0.019247 | 0.25044 | 0.051987 | 0.060146 | 0.32376 | -4.1382 | 118.7714 | -4.5639 | 13.6917 | -0.47607 | 13.559 | 19.7937 | -0.48523 | 119.4443 | -3.6804 | -1.3641 | 16.5482 | -0.93842 | 16.8915 | -102.6993 | -0.48065 | 17.2211 | 0.42572 | 22.9935 | 2.7145 | 2.7237 | 121.9711 | -0.93842 | 122.644 | 16.7587 | -0.48065 | 121.9711 | -0.93842 | 16.7587 | 2.7237 | 122.644 | -106.7871 | -105.9036
3464.7812 | 122.9736 | -1.8036 | 120.6711 | -0.37025 | -0.0090704 | -0.017111 | 0.27351 | 0.03212 | 0.031093 | 0.28915 | -2.0325 | 120.9732 | -2.092 | 54.4556 | 51.1826 | 55.513 | 120.4651 | 1.593 | 120.8038 | -1.3687 | -0.28839 | 0.30212 | -0.22888 | 56.2592 | -69.4885 | 0.43488 | 0.13275 | 0.059509 | 122.2687 | 3.3966 | 52.9861 | 122.7768 | -0.22888 | 122.6074 | 57.3166 | 0.43488 | 122.7768 | -0.22888 | 57.3166 | 52.9861 | 122.6074 | -122.7631 | -122.0398
3465.7812 | 121.8979 | 0.004578 | 117.6819 | -0.43892 | -0.008216 | -0.010275 | 0.13743 | -0.0056909 | 0.049892 | 0.19772 | -0.059509 | 122.1222 | -0.39368 | 121.9299 | 23.5519 | 121.4493 | 121.6736 | 0.13275 | 121.9666 | -0.34332 | -0.39826 | 4.4403 | -0.064087 | 121.9254 | -94.1299 | -0.3479 | 4.2847 | 0.33417 | 121.669 | 0.12817 | 23.5474 | 122.1176 | -0.064087 | 121.962 | 121.4447 | -0.3479 | 122.1176 | -0.064087 | 121.4447 | 23.5474 | 121.962 | -118.0756 | -118.0252
3466.7812 | 117.215 | -35.8841 | 81.2027 | 0.14854 | -0.011848 | -0.0098479 | 6.9197 | -0.0091089 | 0.018916 | 7.0016 | -36.1771 | 81.5643 | -36.2595 | 61.9812 | 3.6026 | 7.4249 | 45.9915 | 23.4558 | 60.6354 | -15.6281 | -0.37537 | 0.36163 | -0.29297 | 97.8653 | -77.6001 | 20.256 | -20.5673 | 0.082397 | 81.8756 | 59.3399 | 39.4867 | 117.4484 | -0.29297 | 96.5195 | 43.309 | 20.256 | 117.4484 | -0.29297 | 43.309 | 39.4867 | 96.5195 | -117.4622 | -96.8307
3467.7656 | 122.1542 | -0.10071 | 121.9299 | 0.13329 | -0.0097114 | -0.020529 | 0.06373 | -0.0046229 | 0.057582 | 0.13492 | -0.10986 | 122.5937 | -0.40741 | 119.2383 | 5.4474 | 9.581 | 122.2412 | 3.804 | 122.4518 | -0.34332 | -0.3067 | 0.66376 | -0.009155 | 119.339 | -116.4825 | -0.24261 | 0.52185 | 0.29755 | 122.3419 | 3.9047 | 5.5481 | 122.6944 | -0.009155 | 122.5525 | 9.6817 | -0.24261 | 122.6944 | -0.009155 | 9.6817 | 5.5481 | 122.5525 | -122.3373 | -122.2733
3468.7812 | 122.5571 | -0.022888 | 121.9162 | 0.25536 | -0.010993 | -0.017752 | 0.091715 | -0.0061181 | 0.060786 | 0.15991 | -0.041199 | 122.58 | -0.33417 | 119.426 | 3.8589 | 2.3483 | 122.1497 | 4.5364 | 122.4976 | -0.21973 | -0.31128 | 0.66376 | -0.018311 | 119.4489 | -118.0573 | -0.19684 | 0.58136 | 0.29297 | 122.1725 | 4.5593 | 3.8818 | 122.6028 | -0.018311 | 122.5204 | 2.3712 | -0.19684 | 122.6028 | -0.018311 | 2.3712 | 3.8818 | 122.5204 | -122.2504 | -122.1359
3469.7812 | 122.6761 | -0.1236 | 122.0444 | 0.2401 | -0.012916 | -0.015189 | 0.45786 | -0.0065455 | 0.060359 | 0.55276 | -0.041199 | 122.5571 | -0.43488 | 118.8217 | 4.1748 | 3.6575 | 121.9894 | 7.251 | 122.3831 | -0.32044 | -0.31128 | 0.5127 | 0.082397 | 118.9453 | -117.8696 | -0.19684 | 0.33875 | 0.39368 | 122.113 | 7.3746 | 4.2984 | 122.6807 | 0.082397 | 122.5067 | 3.7811 | -0.19684 | 122.6807 | 0.082397 | 3.7811 | 4.2984 | 122.5067 | -122.4792 | -122.3648
3470.7812 | 117.6178 | -44.7281 | 72.6196 | 0.36217 | -0.007575 | -0.011771 | 6.9197 | -0.0056909 | 0.03921 | 7.0016 | -43.5242 | 74.7391 | -43.8217 | 50.2258 | -12.4786 | 5.6488 | 49.0814 | 23.9227 | 59.4498 | -30.0018 | 0.90637 | 2.1194 | 1.2039 | 94.9539 | -85.0983 | 14.7263 | -13.1699 | 0.29755 | 93.8095 | 68.6508 | 32.2494 | 119.4672 | 1.2039 | 104.1779 | 50.3769 | 14.7263 | 119.4672 | 1.2039 | 50.3769 | 32.2494 | 104.1779 | -116.4413 | -102.6215
3471.7812 | 121.8796 | -0.064087 | 122.2733 | -0.065079 | -0.006507 | -0.015616 | 0.076547 | -0.0037683 | 0.062923 | 0.13513 | 0.004578 | 122.5159 | -0.39368 | 117.7322 | 2.1927 | 2.3666 | 122.0764 | 122.3831 | 122.3877 | -0.30212 | -0.32959 | 0.24262 | 0.068665 | 117.7963 | -120.0806 | -0.23804 | 0.11444 | 0.39826 | 122.1405 | 122.4472 | 2.2568 | 122.58 | 0.068665 | 122.4518 | 2.4307 | -0.23804 | 122.58 | 0.068665 | 2.4307 | 2.2568 | 122.4518 | -122.6669 | -122.5754
3472.7812 | 121.8796 | -0.14191 | 122.2961 | 0.064621 | -0.010993 | -0.013907 | 0.24681 | -0.0035547 | 0.058864 | 0.31329 | -0.032043 | 122.493 | -0.41199 | 120.3781 | 3.7033 | 3.6713 | 122.0764 | 122.3053 | 122.3969 | -0.19684 | -0.27008 | 0.19684 | 0.10986 | 120.52 | -118.5928 | -0.054931 | 0.10071 | 0.37994 | 122.2183 | 122.4472 | 3.8452 | 122.6349 | 0.10986 | 122.5388 | 3.8132 | -0.054931 | 122.6349 | 0.10986 | 3.8132 | 3.8452 | 122.5388 | -122.7081 | -122.493
3473.7812 | 122.5616 | -0.16937 | 122.2595 | 0.15617 | -0.011207 | -0.01882 | 0.42134 | -0.0044091 | 0.059291 | 0.50598 | -0.018311 | 122.4792 | -0.42114 | 119.1742 | 5.0674 | 5.127 | 121.5225 | 122.3099 | 122.2824 | -0.38452 | -0.25177 | 0.21973 | 0.15106 | 119.3436 | -117.1921 | -0.21515 | 0.022889 | 0.40283 | 121.6919 | 122.4792 | 5.2368 | 122.6486 | 0.15106 | 122.4518 | 5.2963 | -0.21515 | 122.6486 | 0.15106 | 5.2963 | 5.2368 | 122.4518 | -122.6807 | -122.644
3474.7812 | 122.3969 | -0.2655 | 122.1405 | 0.10277 | -0.0094976 | -0.01583 | 0.099405 | 0.01204 | 0.038997 | 0.16354 | -0.10986 | 122.6486 | 0.36163 | 89.7217 | 42.2562 | 43.0161 | 122.1405 | 122.3053 | 122.4976 | -0.52643 | 0.62714 | 0.50812 | 0.15564 | 89.9872 | -79.8843 | -0.26093 | 0.35706 | -0.4715 | 122.406 | 122.5708 | 42.5217 | 122.9141 | 0.15564 | 122.7631 | 43.2816 | -0.26093 | 122.9141 | 0.15564 | 43.2816 | 42.5217 | 122.7631 | -121.7789 | -122.6669
3475.7812 | 122.4976 | -0.19226 | 121.994 | -0.0040434 | -0.010566 | -0.011771 | 0.7469 | -0.0039819 | 0.05865 | 0.8529 | -0.09613 | 122.5113 | -0.49896 | 120.8679 | 4.8614 | 4.7424 | 121.5591 | 122.1817 | 122.3465 | -0.34332 | -0.3067 | 0.51727 | 0.096131 | 121.0602 | -117.1326 | -0.15106 | 0.35248 | 0.40283 | 121.7514 | 122.374 | 5.0537 | 122.7036 | 0.096131 | 122.5388 | 4.9347 | -0.15106 | 122.7036 | 0.096131 | 4.9347 | 5.0537 | 122.5388 | -122.493 | -122.3373
3476.7812 | 122.3007 | -0.15564 | 122.1954 | -0.15663 | -0.0094976 | -0.017325 | 0.079538 | 0.057114 | 0.057796 | 0.22784 | -0.050354 | 122.5021 | -0.42114 | 5.1041 | 4.9667 | 4.921 | 122.0901 | 122.2321 | 122.3557 | -0.35248 | -0.2655 | 0.3067 | 0.10529 | 5.2597 | -117.2287 | -0.19684 | 0.16022 | 0.37079 | 122.2458 | 122.3877 | 5.1224 | 122.6578 | 0.10529 | 122.5113 | 5.0766 | -0.19684 | 122.6578 | 0.10529 | 5.0766 | 5.1224 | 122.5113 | -122.6166 | -122.5479
3477.7812 | 122.0215 | -0.10529 | 122.319 | 0.21721 | -0.008216 | -0.015402 | 0.07612 | 0.061173 | 0.061 | 0.18896 | -0.086975 | 122.6028 | -0.41657 | 3.6758 | 3.7491 | 3.7491 | 122.1497 | 122.2046 | 122.4197 | -0.36163 | -0.31128 | 0.28381 | 0.018311 | 3.7811 | -118.5699 | -0.25635 | 0.10071 | 0.32959 | 122.2549 | 122.3099 | 3.8544 | 122.7081 | 0.018311 | 122.525 | 3.8544 | -0.25635 | 122.7081 | 0.018311 | 3.8544 | 3.8544 | 122.525 | -122.7356 | -122.6807
3478.7812 | 122.3923 | -0.11444 | 122.2595 | 0.17906 | -0.012275 | -0.026083 | 0.23377 | 0.059464 | 0.058864 | 0.38614 | -0.068665 | 122.4792 | -0.39825 | 3.447 | 3.4836 | 3.5248 | 121.9894 | 122.3236 | 122.3465 | -0.32501 | -0.28381 | 0.21973 | 0.045776 | 3.5614 | -118.7759 | -0.21057 | 0.086976 | 0.32959 | 122.1039 | 122.438 | 3.598 | 122.5937 | 0.045776 | 122.4609 | 3.6392 | -0.21057 | 122.5937 | 0.045776 | 3.6392 | 3.598 | 122.4609 | -122.6578 | -122.5845
3479.7812 | 122.4609 | -0.14648 | 122.2275 | 0.24773 | -0.011848 | -0.022452 | 0.43244 | 0.057328 | 0.060359 | 0.56088 | -0.054932 | 122.525 | -0.45319 | 4.3671 | 4.3442 | 4.3625 | 121.843 | 122.3007 | 122.3373 | -0.3479 | -0.3067 | 0.29755 | 0.091552 | 4.5135 | -117.8833 | -0.20142 | 0.10986 | 0.39825 | 121.9894 | 122.4472 | 4.4907 | 122.6715 | 0.091552 | 122.4838 | 4.509 | -0.20142 | 122.6715 | 0.091552 | 4.509 | 4.4907 | 122.4838 | -122.6807 | -122.5754
3480.7812 | 121.5408 | -0.068665 | 121.4081 | -0.011673 | -0.0080024 | -0.014121 | 0.13615 | 0.026993 | 0.064204 | 0.24322 | 0 | 122.0215 | -0.41657 | 65.4419 | 0.013733 | 0.19684 | 121.6095 | 118.2358 | 121.907 | -0.27466 | -0.3479 | 0.6134 | 0.068665 | 65.5106 | -121.3943 | -0.20599 | 0.49896 | 0.41657 | 121.6782 | 118.3044 | 0.082398 | 122.0901 | 0.068665 | 121.9757 | 0.2655 | -0.20599 | 122.0901 | 0.068665 | 0.2655 | 0.082398 | 121.9757 | -121.8246 | -121.6827
3481.7812 | 121.6324 | -0.11902 | 121.6415 | 0.23247 | -0.0080024 | -0.019675 | 0.14042 | -0.0022729 | 0.06335 | 0.2099 | -0.064087 | 122.2275 | -0.40283 | 114.9124 | 0 | -0.022888 | 121.8338 | 62.3657 | 122.0306 | -0.33875 | -0.28381 | 0.58594 | 0.054932 | 115.0314 | -121.6415 | -0.21973 | 0.3891 | 0.33875 | 121.9528 | 62.4847 | 0.11902 | 122.3465 | 0.054932 | 122.1497 | 0.096131 | -0.21973 | 122.3465 | 0.054932 | 0.096131 | 0.11902 | 122.1497 | -122.0444 | -121.9803
3482.7812 | 120.5658 | 0.25635 | 96.5424 | 0.049362 | -0.010779 | -0.016257 | 0.0319 | 0.062455 | 0.064204 | 0.19067 | 0 | 121.6736 | -0.4303 | 0.004578 | -0.032043 | -0.032043 | 121.2524 | 109.5978 | 121.5042 | -0.3479 | -0.68665 | 25.1312 | -0.25635 | -0.25177 | -96.5744 | -0.60425 | 24.9619 | 0.4303 | 120.9961 | 109.3414 | -0.28839 | 121.4172 | -0.25635 | 121.2479 | -0.28839 | -0.60425 | 121.4172 | -0.25635 | -0.28839 | -0.28839 | 121.2479 | -96.9727 | -96.8903
3483.7812 | 111.0123 | 0.068665 | 98.9136 | 0.0035856 | -0.0067206 | -0.012839 | -0.00099756 | -0.0035547 | 0.065486 | 0.07147 | 0.032043 | 121.8201 | -0.37079 | 117.9932 | 0.11444 | 4.2297 | 116.5283 | 0.20599 | 121.7331 | -0.2243 | -0.43945 | 22.9065 | -0.036622 | 117.9245 | -98.7991 | -0.29297 | 22.8195 | 0.40283 | 116.4597 | 0.13733 | 0.045776 | 121.7514 | -0.036622 | 121.6644 | 4.1611 | -0.29297 | 121.7514 | -0.036622 | 4.1611 | 0.045776 | 121.6644 | -99.2844 | -99.1379
3484.7812 | 98.7625 | -61.647 | 52.0294 | 0.087509 | -0.0097114 | -0.016257 | 0.0032748 | -0.0056909 | -0.0047957 | -0.010348 | -61.9858 | 59.4727 | -62.2284 | 59.4543 | 59.2255 | 59.2255 | 59.3216 | 2.71 | 59.3948 | -62.2055 | -0.58136 | 7.4432 | -0.33875 | 121.1014 | 7.196 | -0.55847 | 7.3654 | 0.24262 | 120.9686 | 64.357 | 120.8725 | 121.1197 | -0.33875 | 121.0419 | 120.8725 | -0.55847 | 121.1197 | -0.33875 | 120.8725 | 120.8725 | 121.0419 | -114.2578 | -114.2349
3485.7812 | 120.8862 | -62.1918 | 58.1955 | 0.26299 | -0.009925 | -0.014121 | 0.0062656 | -0.0054773 | -0.0039413 | -0.008639 | -62.5351 | 59.0561 | -62.7274 | 59.024 | 58.8272 | 58.8272 | 58.8226 | 58.905 | 58.9462 | -62.6816 | -0.53558 | 0.8606 | -0.34332 | 121.2158 | 0.63171 | -0.48981 | 0.75073 | 0.19226 | 121.0144 | 121.0968 | 121.019 | 121.2479 | -0.34332 | 121.138 | 121.019 | -0.48981 | 121.2479 | -0.34332 | 121.019 | 121.019 | 121.138 | -120.9229 | -120.8771
3486.7812 | 121.2433 | -62.5031 | 57.692 | -1.5681 | -0.0094976 | -0.013907 | 0.003702 | -0.0044091 | -0.0037277 | -0.0090662 | -62.8601 | 58.5571 | -63.0249 | 58.5068 | 58.1955 | 58.2916 | 58.3923 | 55.9525 | 58.5068 | -63.0753 | -0.52185 | 0.86517 | -0.35706 | 121.0098 | 0.50354 | -0.5722 | 0.81482 | 0.16479 | 120.8954 | 118.4555 | 120.6985 | 121.0602 | -0.35706 | 121.0098 | 120.7947 | -0.5722 | 121.0602 | -0.35706 | 120.7947 | 120.6985 | 121.0098 | -120.7169 | -120.7672
3487.7812 | 121.2067 | -85.1669 | 35.7147 | 0.2935 | -0.0077888 | -0.017111 | 0.0051974 | -0.0050501 | 0.029811 | 0.023832 | -85.2859 | 35.9161 | -85.5835 | 35.8749 | -26.1429 | 35.7651 | 35.7056 | -85.1669 | 35.8566 | -85.5881 | -0.41656 | 0.20142 | -0.11902 | 121.0419 | -61.8576 | -0.42114 | 0.14191 | 0.29755 | 120.8725 | 0 | 59.024 | 121.0831 | -0.11902 | 121.0236 | 120.932 | -0.42114 | 121.0831 | -0.11902 | 120.932 | 59.024 | 121.0236 | -121.2982 | -121.3028
3488.7812 | 121.2799 | -99.1562 | 22.0047 | 0.12566 | -0.0086432 | -0.018179 | 0.020578 | -0.0067591 | -0.0039413 | -0.001803 | -99.2249 | 22.1329 | -99.5178 | 22.0047 | 21.8079 | 21.9406 | 22.023 | 22.0459 | 22.1466 | 8.4503 | -0.36163 | 0.12817 | -0.068665 | 121.1609 | -0.19684 | 107.6065 | 0.14191 | 0.29297 | 121.1792 | 121.2021 | 120.9641 | 121.2891 | -0.068665 | 121.3028 | 121.0968 | 107.6065 | 121.2891 | -0.068665 | 121.0968 | 120.9641 | 121.3028 | -121.5225 | -13.5544
3489.7812 | 121.4584 | -100.4791 | 20.8237 | 0.26299 | -0.009284 | -0.017111 | 0.017801 | -0.0071863 | -0.0028731 | -0.00052119 | -100.4745 | 20.9335 | -100.7721 | 20.8603 | 20.7504 | 20.8054 | 20.723 | 20.9106 | 20.9198 | 8.4549 | -0.29297 | 0.10986 | 0.004578 | 121.3394 | -0.073242 | 108.934 | 0.096131 | 0.29755 | 121.2021 | 121.3898 | 121.2296 | 121.4127 | 0.004578 | 121.3989 | 121.2845 | 108.934 | 121.4127 | 0.004578 | 121.2845 | 121.2296 | 121.3989 | -121.5958 | -12.3688
3490.7812 | 121.5042 | -98.5611 | 22.76 | 0.25536 | -0.010993 | -0.014121 | 0.015665 | -0.0078271 | -0.0024459 | -0.0011622 | -98.584 | 22.8699 | -98.8907 | 22.8378 | 22.7142 | 22.7646 | 22.6547 | 22.8653 | 22.8745 | 8.4595 | -0.32959 | 0.10986 | -0.022888 | 121.3989 | -0.045777 | 107.0206 | 0.11444 | 0.3067 | 121.2158 | 121.4264 | 121.2753 | 121.431 | -0.022888 | 121.4355 | 121.3257 | 107.0206 | 121.431 | -0.022888 | 121.3257 | 121.2753 | 121.4355 | -121.6507 | -14.3005
3491.7812 | 121.463 | -94.3314 | 27.0172 | 0.27824 | -0.01142 | -0.01348 | 0.014383 | -0.0059045 | -0.0033005 | -0.001803 | -94.313 | 27.0859 | -94.6198 | 27.1637 | 27.0218 | 27.0813 | 26.8204 | 27.1912 | 27.095 | 8.4549 | -0.28839 | 0.068664 | 0.018311 | 121.4951 | 0.004578 | 102.7863 | 0.07782 | 0.3067 | 121.1517 | 121.5225 | 121.3531 | 121.4172 | 0.018311 | 121.4264 | 121.4127 | 102.7863 | 121.4172 | 0.018311 | 121.4127 | 121.3531 | 121.4264 | -121.637 | -18.5623
3492.7812 | 121.0052 | -89.6255 | 31.7825 | 0.25536 | -0.012275 | -0.017752 | 0.013315 | -0.0073999 | -0.00095055 | -0.0020166 | -89.653 | 31.8878 | -89.9597 | 31.8787 | 31.723 | 31.7734 | 31.6864 | 31.8787 | 31.8649 | 8.4503 | -0.33417 | 0.10528 | -0.027466 | 121.5042 | -0.05951 | 98.0759 | 0.082397 | 0.3067 | 121.312 | 121.5042 | 121.3486 | 121.5134 | -0.027466 | 121.4905 | 121.3989 | 98.0759 | 121.5134 | -0.027466 | 121.3989 | 121.3486 | 121.4905 | -121.7422 | -23.3322
3493.7812 | 121.6599 | -87.4741 | 33.9752 | 0.11803 | -0.010352 | -0.019247 | 0.0069064 | -0.0088953 | -0.0026595 | -0.0015894 | -87.4191 | 34.1446 | -87.6663 | 34.1171 | 33.9661 | 34.021 | 33.8745 | 34.1354 | 34.0439 | 8.4503 | -0.19226 | 0.16937 | 0.054932 | 121.5912 | -0.009156 | 95.9244 | 0.068664 | 0.24719 | 121.3486 | 121.6095 | 121.4401 | 121.6187 | 0.054932 | 121.5179 | 121.4951 | 95.9244 | 121.6187 | 0.054932 | 121.4951 | 121.4401 | 121.5179 | -121.6415 | -25.5249
3494.7812 | 121.6919 | -86.1237 | 35.3119 | -0.072708 | -0.010779 | -0.019675 | 0.012033 | -0.0065455 | -0.0041549 | 0.00011961 | -86.142 | 35.3897 | -86.4166 | 35.495 | 35.3394 | 35.4034 | 35.1151 | 35.5042 | 35.3943 | 8.4641 | -0.29297 | 0.077819 | -0.018311 | 121.6187 | 0.027465 | 94.5877 | 0.082397 | 0.27466 | 121.2387 | 121.6278 | 121.463 | 121.5134 | -0.018311 | 121.5179 | 121.5271 | 94.5877 | 121.5134 | -0.018311 | 121.5271 | 121.463 | 121.5179 | -121.7285 | -26.8478
3495.7812 | 121.6873 | -83.5098 | 37.9578 | 0.20958 | -0.0088568 | -0.017111 | 0.010965 | -0.0088953 | -0.0041549 | -0.00030759 | -83.5419 | 38.0264 | -83.812 | 38.1409 | 37.9623 | 38.0035 | 37.7747 | 38.0951 | 38.0356 | 8.4503 | -0.30212 | 0.068664 | -0.032043 | 121.6507 | 0.004577 | 91.9601 | 0.077819 | 0.27008 | 121.2845 | 121.6049 | 121.4722 | 121.5363 | -0.032043 | 121.5454 | 121.5134 | 91.9601 | 121.5363 | -0.032043 | 121.5134 | 121.4722 | 121.5454 | -121.7697 | -29.5074
3496.7656 | 121.7514 | -81.3629 | 40.1367 | 0.1104 | -0.012061 | -0.02117 | 0.0084018 | -0.010177 | -0.0033005 | -0.0024438 | -81.3675 | 40.2054 | -81.7017 | 40.2878 | 40.1505 | 40.1825 | 40.0085 | 40.3061 | 40.1962 | 8.4503 | -0.33875 | 0.068664 | -0.004578 | 121.6507 | 0.013733 | 89.8132 | 0.059509 | 0.33417 | 121.3715 | 121.669 | 121.5134 | 121.5683 | -0.004578 | 121.5591 | 121.5454 | 89.8132 | 121.5683 | -0.004578 | 121.5454 | 121.5134 | 121.5591 | -121.8384 | -31.6864
3497.7812 | 121.756 | -80.0446 | 41.4734 | 0.17143 | -0.01142 | -0.015189 | 0.0075472 | -0.0086817 | -0.0050095 | -0.0015894 | -80.2963 | 41.4001 | -80.5161 | 41.5924 | 41.4459 | 41.5054 | 41.3452 | 41.6336 | 41.5283 | 8.4503 | -0.4715 | -0.073243 | -0.25177 | 121.637 | -0.027466 | 88.4949 | 0.054931 | 0.21973 | 121.3898 | 121.6782 | 121.4905 | 121.4447 | -0.25177 | 121.5729 | 121.55 | 88.4949 | 121.4447 | -0.25177 | 121.55 | 121.4905 | 121.5729 | -121.9894 | -33.0231
3498.7656 | 121.4218 | -74.2538 | 47.2687 | 0.19432 | -0.01142 | -0.014548 | 0.011606 | -0.0091089 | -0.0043685 | -0.0013758 | -74.2767 | 47.3831 | -74.5697 | 47.4884 | 47.287 | 47.3328 | 47.0947 | 47.4564 | 47.3511 | 8.4503 | -0.31586 | 0.11444 | -0.022888 | 121.7422 | 0.01831 | 82.7042 | 0.082397 | 0.29297 | 121.3486 | 121.7102 | 121.5408 | 121.637 | -0.022888 | 121.6049 | 121.5866 | 82.7042 | 121.637 | -0.022888 | 121.5866 | 121.5408 | 121.6049 | -121.8384 | -38.8184
3499.7812 | 121.7697 | -70.4681 | 51.1276 | -0.24818 | -0.010566 | -0.012625 | 0.0081882 | -0.010391 | -0.0039413 | -0.0013758 | -70.5963 | 51.123 | -70.8389 | 51.3382 | 51.1093 | 51.1185 | 50.9903 | 51.3062 | 51.1505 | 8.4503 | -0.37079 | -0.004578 | -0.12817 | 121.8063 | -0.018311 | 78.9185 | 0.022888 | 0.24262 | 121.4584 | 121.7743 | 121.5775 | 121.5912 | -0.12817 | 121.6187 | 121.5866 | 78.9185 | 121.5912 | -0.12817 | 121.5866 | 121.5775 | 121.6187 | -121.9666 | -42.6773
3500.7656 | 121.2479 | -68.7332 | 52.9037 | 0.94963 | -0.010993 | -0.016043 | 0.01481 | -0.0084681 | -0.0052231 | -0.0013758 | -68.8431 | 53.009 | -69.1086 | 53.009 | 52.7618 | 52.7939 | 52.8534 | 52.9129 | 52.9633 | 8.4457 | -0.37537 | 0.10529 | -0.10986 | 121.7422 | -0.14191 | 77.179 | 0.059509 | 0.2655 | 121.5866 | 121.6461 | 121.4951 | 121.7422 | -0.10986 | 121.6965 | 121.5271 | 77.179 | 121.7422 | -0.10986 | 121.5271 | 121.4951 | 121.6965 | -122.0123 | -44.458
3501.7656 | 121.8475 | -68.4998 | 53.0777 | 0.011215 | -0.010993 | -0.017539 | 0.0024202 | -0.0088953 | -0.0043685 | -0.0015894 | -68.7103 | 53.1143 | -68.9026 | 53.2928 | 53.1143 | 53.1143 | 53.0273 | 53.2516 | 53.183 | 8.4503 | -0.40283 | 0.036621 | -0.21057 | 121.7926 | 0.036621 | 76.9501 | 0.10529 | 0.19226 | 121.5271 | 121.7514 | 121.6141 | 121.6141 | -0.21057 | 121.6827 | 121.6141 | 76.9501 | 121.6141 | -0.21057 | 121.6141 | 121.6141 | 121.6827 | -121.9803 | -44.6274
3502.7656 | 121.9116 | -68.6554 | 52.9404 | -0.072708 | -0.010352 | -0.016043 | 0.0086154 | -0.0091089 | -0.0039413 | -0.0047938 | -68.7057 | 53.096 | -68.9346 | 53.1738 | 52.9587 | 53.0365 | 52.8168 | 53.1372 | 53.0182 | 8.4595 | -0.27923 | 0.15564 | -0.050354 | 121.8292 | 0.01831 | 77.1149 | 0.077819 | 0.22888 | 121.4722 | 121.7926 | 121.6141 | 121.7514 | -0.050354 | 121.6736 | 121.6919 | 77.1149 | 121.7514 | -0.050354 | 121.6919 | 121.6141 | 121.6736 | -121.875 | -44.4809
3503.7656 | 121.875 | -69.1727 | 52.4551 | -0.17952 | -0.01142 | -0.016898 | 0.0051974 | -0.011031 | -0.0035141 | -0.0022302 | -69.3192 | 52.5696 | -69.4702 | 52.6474 | 52.4551 | 52.4506 | 52.3407 | 52.6016 | 52.4963 | 8.4503 | -0.29755 | 0.11444 | -0.14648 | 121.8201 | 0 | 77.623 | 0.041199 | 0.15106 | 121.5134 | 121.7743 | 121.6278 | 121.7422 | -0.14648 | 121.669 | 121.6232 | 77.623 | 121.7422 | -0.14648 | 121.6232 | 121.6278 | 121.669 | -121.9254 | -44.0048
3504.7812 | 121.875 | -67.9642 | 53.7048 | 0.10277 | -0.010993 | -0.020743 | 0.005411 | -0.010177 | -0.0033005 | -0.003512 | -68.042 | 53.8467 | -68.2709 | 53.9062 | 53.6865 | 53.7048 | 53.6041 | 53.8376 | 53.7735 | 8.4503 | -0.3067 | 0.14191 | -0.07782 | 121.8704 | -0.018311 | 76.4145 | 0.068665 | 0.22888 | 121.5683 | 121.8018 | 121.6507 | 121.8109 | -0.07782 | 121.7377 | 121.669 | 76.4145 | 121.8109 | -0.07782 | 121.669 | 121.6507 | 121.7377 | -121.9757 | -45.2545
3505.7656 | 121.9345 | -68.4357 | 53.2013 | 0.20958 | -0.01142 | -0.01583 | 0.0079744 | -0.0084681 | -0.0043685 | -0.00458 | -68.4723 | 53.3615 | -68.7515 | 53.4851 | 53.27 | 53.302 | 53.0594 | 53.3981 | 53.2837 | 8.4457 | -0.31586 | 0.16022 | -0.036621 | 121.9208 | 0.068664 | 76.8814 | 0.082397 | 0.27924 | 121.4951 | 121.8338 | 121.7056 | 121.7972 | -0.036621 | 121.7194 | 121.7377 | 76.8814 | 121.7972 | -0.036621 | 121.7377 | 121.7056 | 121.7194 | -121.9528 | -44.7556
3506.7812 | 121.9711 | -68.3899 | 53.2745 | 0.28587 | -0.010139 | -0.017111 | 0.01182 | -0.0088953 | -0.0052231 | -0.0028712 | -68.4677 | 53.4439 | -68.7286 | 53.5446 | 53.2883 | 53.3249 | 53.1189 | 53.4576 | 53.3478 | 8.4503 | -0.33875 | 0.16937 | -0.077819 | 121.9345 | 0.013733 | 76.8402 | 0.073242 | 0.26093 | 121.5088 | 121.8475 | 121.6782 | 121.8338 | -0.077819 | 121.7377 | 121.7148 | 76.8402 | 121.8338 | -0.077819 | 121.7148 | 121.6782 | 121.7377 | -122.0032 | -44.8242
3507.7656 | 122.0627 | -68.4265 | 53.2791 | 0.22484 | -0.012702 | -0.017752 | 0.01182 | -0.0097497 | -0.0069321 | -0.0030848 | -68.4494 | 53.4164 | -68.7378 | 53.5217 | 53.3295 | 53.3386 | 53.0136 | 53.2562 | 53.2928 | 8.4549 | -0.31128 | 0.13733 | -0.022888 | 121.9482 | 0.050354 | 76.8814 | 0.013733 | 0.28839 | 121.4401 | 121.6827 | 121.756 | 121.843 | -0.022888 | 121.7194 | 121.7651 | 76.8814 | 121.843 | -0.022888 | 121.7651 | 121.756 | 121.7194 | -122.0169 | -44.8242
3508.7656 | 121.8613 | -68.1931 | 53.5767 | 0.11803 | -0.0094976 | -0.017111 | 0.013956 | -0.0076135 | -0.0037277 | -0.0022302 | -68.3304 | 53.714 | -68.5547 | 53.6682 | 53.4531 | 53.4348 | 53.54 | 53.5355 | 53.6041 | 8.4503 | -0.36163 | 0.13733 | -0.13733 | 121.8613 | -0.1236 | 76.6434 | 0.027466 | 0.2243 | 121.7331 | 121.7285 | 121.6461 | 121.907 | -0.13733 | 121.7972 | 121.6278 | 76.6434 | 121.907 | -0.13733 | 121.6278 | 121.6461 | 121.7972 | -122.1313 | -45.1263
3509.7656 | 121.962 | -67.6163 | 54.0939 | 0.27061 | -0.0097114 | -0.019034 | 0.011606 | -0.0080407 | -0.0041549 | -0.0037256 | -67.7399 | 54.2633 | -67.923 | 54.3091 | 54.1168 | 54.1122 | 54.0024 | 54.213 | 54.1809 | 8.4503 | -0.3067 | 0.16937 | -0.1236 | 121.9254 | 0.022888 | 76.0666 | 0.086975 | 0.18311 | 121.6187 | 121.8292 | 121.7331 | 121.8796 | -0.1236 | 121.7972 | 121.7285 | 76.0666 | 121.8796 | -0.1236 | 121.7285 | 121.7331 | 121.7972 | -122.0169 | -45.6436
3510.7656 | 121.8567 | -67.2043 | 54.6295 | 0.19432 | -0.010352 | -0.013052 | 0.012674 | -0.0063317 | -0.0033005 | -0.003512 | -67.305 | 54.7806 | -67.5293 | 54.7165 | 54.5197 | 54.5059 | 54.6112 | 54.6158 | 54.6707 | 8.4457 | -0.32501 | 0.15106 | -0.10071 | 121.9208 | -0.10986 | 75.65 | 0.041198 | 0.2243 | 121.8155 | 121.8201 | 121.7239 | 121.9849 | -0.10071 | 121.875 | 121.7102 | 75.65 | 121.9849 | -0.10071 | 121.7102 | 121.7239 | 121.875 | -122.1588 | -46.1838
3511.7656 | 121.9574 | -67.131 | 54.6295 | 0.26299 | -0.009284 | -0.016898 | 0.010324 | -0.0076135 | -0.0039413 | -0.0030848 | -67.2501 | 54.8035 | -67.4927 | 54.8035 | 54.6066 | 54.6112 | 54.5425 | 54.7211 | 54.7073 | 8.4503 | -0.36163 | 0.17395 | -0.11902 | 121.9345 | -0.022889 | 75.5814 | 0.077819 | 0.24262 | 121.6736 | 121.8521 | 121.7377 | 121.9345 | -0.11902 | 121.8384 | 121.7422 | 75.5814 | 121.9345 | -0.11902 | 121.7422 | 121.7377 | 121.8384 | -122.1222 | -46.1792
3512.7656 | 121.9528 | -66.7969 | 55.0369 | -1.446 | -0.0084296 | -0.013907 | 0.010965 | -0.0059045 | -0.0024459 | -0.0028712 | -66.8838 | 55.2292 | -67.099 | 55.1559 | 54.9408 | 54.9637 | 55.0186 | 55.0552 | 55.1056 | 8.4457 | -0.30212 | 0.19226 | -0.086975 | 121.9528 | -0.09613 | 75.2426 | 0.068665 | 0.21515 | 121.8155 | 121.8521 | 121.7377 | 122.0261 | -0.086975 | 121.9025 | 121.7606 | 75.2426 | 122.0261 | -0.086975 | 121.7606 | 121.7377 | 121.9025 | -122.1359 | -46.5912
3513.7812 | 121.9894 | -66.8198 | 54.9911 | 0.3698 | -0.0086432 | -0.011984 | 0.0094698 | -0.0065455 | -0.0033005 | -0.0015894 | -66.9525 | 55.1788 | -67.1768 | 55.1285 | 54.9316 | 54.9362 | 54.9683 | 55.014 | 55.0964 | 8.4549 | -0.35706 | 0.18768 | -0.13275 | 121.9482 | -0.059509 | 75.2747 | 0.10529 | 0.2243 | 121.788 | 121.8338 | 121.7514 | 121.9986 | -0.13275 | 121.9162 | 121.756 | 75.2747 | 121.9986 | -0.13275 | 121.756 | 121.7514 | 121.9162 | -122.168 | -46.5363
3514.7656 | 122.0306 | -66.806 | 55.014 | 0.24773 | -0.0094976 | -0.015189 | 0.010538 | -0.0054773 | -0.0033005 | -0.0013758 | -66.8884 | 55.2155 | -67.1265 | 55.1926 | 54.982 | 55.0003 | 54.9637 | 55.101 | 55.1147 | 8.4503 | -0.32043 | 0.20142 | -0.082398 | 121.9986 | -0.032043 | 75.2563 | 0.10071 | 0.23804 | 121.7697 | 121.907 | 121.788 | 122.0215 | -0.082398 | 121.9208 | 121.8063 | 75.2563 | 122.0215 | -0.082398 | 121.8063 | 121.788 | 121.9208 | -122.1405 | -46.5637
3515.7656 | 122.0673 | -66.7831 | 55.014 | 0.22484 | -0.009284 | -0.012839 | 0.001993 | -0.0071863 | -0.0033005 | -0.00030759 | -66.8884 | 55.1285 | -67.0898 | 55.2017 | 55.0415 | 55.0644 | 54.8904 | 55.1514 | 55.069 | 8.4549 | -0.3067 | 0.11444 | -0.10529 | 121.9849 | 0.027466 | 75.238 | 0.054932 | 0.20142 | 121.6736 | 121.9345 | 121.8246 | 121.9116 | -0.10529 | 121.8521 | 121.8475 | 75.238 | 121.9116 | -0.10529 | 121.8475 | 121.8246 | 121.8521 | -122.1039 | -46.5591
3516.7656 | 121.994 | -66.7969 | 55.069 | 0.034104 | -0.006507 | -0.011984 | 0.013742 | -0.0080407 | -0.0028731 | -0.001803 | -66.8838 | 55.2383 | -67.131 | 55.22 | 54.9866 | 55.0095 | 55.0552 | 55.1239 | 55.1331 | 8.4457 | -0.33417 | 0.16937 | -0.086975 | 122.0169 | -0.082398 | 75.2426 | 0.064087 | 0.24719 | 121.8521 | 121.9208 | 121.7834 | 122.0352 | -0.086975 | 121.9299 | 121.8063 | 75.2426 | 122.0352 | -0.086975 | 121.8063 | 121.7834 | 121.9299 | -122.2 | -46.6232
3517.7656 | 121.9803 | -66.7557 | 55.1376 | 0.026474 | -0.0080024 | -0.019461 | 0.012888 | -0.0065455 | -0.0058639 | -0.001803 | -66.8381 | 55.2704 | -67.0853 | 55.2521 | 55.0507 | 55.0598 | 55.101 | 55.1743 | 55.1788 | 8.4457 | -0.32959 | 0.13275 | -0.082398 | 122.0078 | -0.086975 | 75.2014 | 0.041199 | 0.24719 | 121.8567 | 121.9299 | 121.8063 | 122.0261 | -0.082398 | 121.9345 | 121.8155 | 75.2014 | 122.0261 | -0.082398 | 121.8155 | 121.8063 | 121.9345 | -122.2229 | -46.6919
3518.7812 | 121.9894 | -66.8198 | 55.101 | 0.11803 | -0.010352 | -0.011771 | 0.012461 | -0.0080407 | -0.0045821 | -0.0030848 | -66.9296 | 55.2567 | -67.1539 | 55.1926 | 55.0049 | 54.9911 | 55.0735 | 55.0827 | 55.1605 | 8.4457 | -0.33417 | 0.15564 | -0.10986 | 122.0123 | -0.09613 | 75.2655 | 0.059509 | 0.22431 | 121.8933 | 121.9025 | 121.8246 | 122.0764 | -0.10986 | 121.9803 | 121.8109 | 75.2655 | 122.0764 | -0.10986 | 121.8109 | 121.8246 | 121.9803 | -122.2549 | -46.6553
3519.7812 | 122.1313 | -66.8701 | 54.9728 | 0.24773 | -0.010139 | -0.014761 | 0.0079744 | -0.0061181 | -0.0033005 | -0.0039392 | -66.9708 | 55.1514 | -67.218 | 55.22 | 55.0323 | 55.0323 | 54.8264 | 55.1285 | 55.0369 | 8.4503 | -0.3479 | 0.17853 | -0.10071 | 122.0901 | 0.05951 | 75.3204 | 0.064087 | 0.24719 | 121.6965 | 121.9986 | 121.9025 | 122.0215 | -0.10071 | 121.907 | 121.9025 | 75.3204 | 122.0215 | -0.10071 | 121.9025 | 121.9025 | 121.907 | -122.1909 | -46.5225
3520.7812 | 122.1268 | -66.9846 | 54.8447 | 0.25536 | -0.0077888 | -0.011557 | 0.010111 | -0.0056909 | -0.0054367 | -0.0024438 | -67.0944 | 55.0095 | -67.3416 | 55.0644 | 54.8401 | 54.8813 | 54.7623 | 55.0049 | 54.9408 | 8.4595 | -0.35706 | 0.16479 | -0.10986 | 122.049 | -0.004578 | 75.444 | 0.09613 | 0.24719 | 121.7468 | 121.9894 | 121.8246 | 121.994 | -0.10986 | 121.9254 | 121.8658 | 75.444 | 121.994 | -0.10986 | 121.8658 | 121.8246 | 121.9254 | -122.1863 | -46.3852
3521.7656 | 122.0352 | -67.0074 | 54.8859 | 0.17143 | -0.0097114 | -0.013052 | 0.010965 | -0.0067591 | -0.0039413 | -0.0039392 | -67.1402 | 55.0598 | -67.337 | 55.014 | 54.8264 | 54.8401 | 54.8721 | 54.9316 | 55.0369 | 8.4549 | -0.32959 | 0.17395 | -0.13275 | 122.0215 | -0.059509 | 75.4623 | 0.15106 | 0.19684 | 121.8796 | 121.9391 | 121.8338 | 122.0673 | -0.13275 | 122.0444 | 121.8475 | 75.4623 | 122.0673 | -0.13275 | 121.8475 | 121.8338 | 122.0444 | -122.2229 | -46.431
3522.7656 | 122.049 | -66.9479 | 54.9637 | 0.2401 | -0.010779 | -0.019675 | 0.01182 | -0.0080407 | -0.0056503 | -0.001803 | -67.0944 | 55.1514 | -67.2821 | 55.1056 | 54.8767 | 54.895 | 54.9408 | 54.9728 | 55.0369 | 8.4503 | -0.33417 | 0.18768 | -0.14648 | 122.0535 | -0.086975 | 75.3983 | 0.073242 | 0.18768 | 121.8887 | 121.9208 | 121.8246 | 122.0993 | -0.14648 | 121.9849 | 121.843 | 75.3983 | 122.0993 | -0.14648 | 121.843 | 121.8246 | 121.9849 | -122.2458 | -46.5134
3523.7656 | 122.0444 | -66.98 | 54.9591 | 0.07988 | -0.0090704 | -0.01348 | 0.012674 | -0.0067591 | -0.0065047 | -0.0039392 | -67.0898 | 55.1102 | -67.3004 | 55.0781 | 54.8859 | 54.8813 | 54.9728 | 55.0003 | 55.0461 | 8.4457 | -0.32044 | 0.15106 | -0.10986 | 122.0581 | -0.073242 | 75.4257 | 0.086976 | 0.21057 | 121.9528 | 121.9803 | 121.8658 | 122.0901 | -0.10986 | 122.0261 | 121.8613 | 75.4257 | 122.0901 | -0.10986 | 121.8613 | 121.8658 | 122.0261 | -122.2595 | -46.5134
3524.7656 | 122.081 | -66.9846 | 54.9454 | 0.087509 | -0.010139 | -0.014761 | 0.010752 | -0.0084681 | -0.0035141 | -0.0043664 | -67.0807 | 55.1147 | -67.3325 | 55.0873 | 54.8996 | 54.8859 | 54.9683 | 55.0049 | 55.0323 | 8.4457 | -0.3479 | 0.16937 | -0.09613 | 122.0718 | -0.045777 | 75.4303 | 0.086975 | 0.25177 | 121.9528 | 121.9894 | 121.8842 | 122.0993 | -0.09613 | 122.0169 | 121.8704 | 75.4303 | 122.0993 | -0.09613 | 121.8704 | 121.8842 | 122.0169 | -122.2778 | -46.4996
3525.7656 | 121.8475 | -65.7166 | 48.7564 | 0.049362 | -0.008216 | -0.014121 | 0.013101 | -0.0078271 | -0.0069321 | -9.3992e-05 | -67.0761 | 55.1102 | -67.3462 | 55.0919 | 54.8859 | 54.895 | 54.9774 | 55.0186 | 55.0461 | 8.4549 | -1.6296 | 6.3538 | -1.3596 | 120.8084 | 6.1295 | 74.1714 | 6.2897 | 0.27008 | 120.694 | 120.7352 | 120.6024 | 120.8267 | -1.3596 | 120.7626 | 120.6116 | 74.1714 | 120.8267 | -1.3596 | 120.6116 | 120.6024 | 120.7626 | -116.1026 | -40.3015
3526.7656 | 76.1993 | -61.5143 | 46.2799 | -0.11848 | 0.00096981 | -0.076712 | 0.010965 | -0.0078271 | -0.0047957 | -0.0015894 | -43.2816 | 55.188 | -75.5035 | 55.1193 | 55.3665 | 54.6982 | 55.1193 | 55.3207 | 55.1559 | -0.35706 | -13.9893 | 8.9081 | 18.2327 | 116.6336 | 9.0866 | 61.1572 | 8.876 | 32.222 | 116.6336 | 116.835 | 116.8808 | 116.7023 | 18.2327 | 116.6702 | 116.2125 | 61.1572 | 116.7023 | 18.2327 | 116.2125 | 116.8808 | 116.6702 | -121.7834 | -46.637
3527.7656 | 121.907 | -66.3528 | 54.3182 | 0.23247 | -0.0090704 | -0.015402 | 0.010965 | -0.0065455 | -0.0058639 | -0.00458 | -67.0624 | 55.1971 | -67.2409 | 55.1926 | 54.9957 | 55.014 | 54.9911 | 55.101 | 55.1285 | 8.4549 | -0.88806 | 0.87891 | -0.70953 | 121.5454 | 0.67749 | 74.8077 | 0.81024 | 0.17853 | 121.344 | 121.4539 | 121.3486 | 121.55 | -0.70953 | 121.4813 | 121.3669 | 74.8077 | 121.55 | -0.70953 | 121.3669 | 121.3486 | 121.4813 | -121.5591 | -45.8633
3528.7656 | 120.2408 | -66.6458 | 54.8813 | 0.1638 | -0.010139 | -0.016043 | 0.010538 | -0.0054773 | -0.0035141 | -0.0022302 | -66.9983 | 55.2246 | -67.2134 | 55.2155 | 55.0278 | 55.0369 | 55.0186 | 55.1468 | 55.1926 | 8.4503 | -0.56763 | 0.34332 | -0.35248 | 121.8613 | 0.14648 | 75.0961 | 0.31128 | 0.21515 | 121.6644 | 121.7926 | 121.6736 | 121.8704 | -0.35248 | 121.8384 | 121.6827 | 75.0961 | 121.8704 | -0.35248 | 121.6827 | 121.6736 | 121.8384 | -122.0947 | -46.431
3529.7656 | 119.3848 | -67.5797 | 53.7369 | 0.2401 | 0.99816 | 1.0057 | 0.010538 | -0.0048365 | -0.0039413 | -0.0039392 | 53.9658 | 54.2633 | -68.0283 | 54.2816 | 54.0756 | 54.0985 | 54.0802 | 54.2038 | 54.2358 | 8.4595 | -0.44861 | 0.52643 | 121.5454 | 121.8613 | 0.33875 | 76.0391 | 0.49896 | 121.994 | 121.6599 | 121.7834 | 121.6553 | 121.843 | 121.5454 | 121.8155 | 121.6782 | 76.0391 | 121.843 | 121.5454 | 121.6782 | 121.6553 | 121.8155 | -121.7651 | -45.2774
3530.7656 | 111.7905 | -67.8635 | 53.6819 | -1.9343 | 1.209 | 1.1995 | 0.0094698 | -0.0052637 | -0.0026595 | -0.00073479 | 53.9566 | 54.2404 | -68.0237 | 54.2542 | 54.0436 | 54.039 | 54.1397 | 54.1718 | 54.2267 | 8.4595 | -0.16022 | 0.55847 | 121.8201 | 122.1176 | 0.36163 | 76.3229 | 0.54474 | 121.9803 | 122.0032 | 122.0352 | 121.907 | 122.1039 | 121.8201 | 122.0901 | 121.9025 | 76.3229 | 122.1039 | 121.8201 | 121.9025 | 121.907 | 122.0901 | -121.7056 | -45.2225
3531.7812 | 121.7789 | -67.3782 | 53.7643 | 0.2401 | 1.9334 | 1.9055 | 0.012033 | -0.0061181 | -0.0045821 | -0.0043664 | 53.7643 | 54.0573 | -68.0145 | 54.2038 | 54.007 | 54.0298 | 53.9886 | 54.1534 | 54.158 | 8.4503 | -0.63629 | 0.29297 | 121.1426 | 121.582 | 0.24262 | 75.8286 | 0.39368 | 121.7789 | 121.3669 | 121.5317 | 121.3852 | 121.4355 | 121.1426 | 121.5363 | 121.4081 | 75.8286 | 121.4355 | 121.1426 | 121.4081 | 121.3852 | 121.5363 | -121.7789 | -45.314
3532.7656 | 102.1545 | -60.8551 | 54.3457 | 0.1104 | 1.1917 | 1.1544 | 0.0086154 | -0.0056909 | -0.0060775 | -0.0020166 | 53.8834 | 54.1397 | -68.1427 | 54.1992 | 53.9978 | 54.0115 | 54.0985 | 54.0802 | 54.1626 | 8.4549 | -7.2876 | -0.20599 | 114.7385 | 115.0543 | -0.3479 | 69.31 | -0.1831 | 122.0261 | 114.9536 | 114.9353 | 114.8529 | 114.9948 | 114.7385 | 115.0177 | 114.8666 | 69.31 | 114.9948 | 114.7385 | 114.8666 | 114.8529 | 115.0177 | -122.4884 | -45.8908
3533.7812 | 121.9666 | -67.2363 | 53.3569 | 0.17143 | 0.016564 | 0.011728 | 0.01182 | -0.0037683 | -0.0041549 | -0.0030848 | 54.0436 | 54.277 | -68.2343 | 54.277 | 54.0756 | 54.0619 | 54.0756 | 54.1809 | 54.1855 | 8.4503 | -0.99792 | 0.9201 | 121.2799 | 121.5134 | 0.71869 | 75.6866 | 0.82855 | 122.2778 | 121.312 | 121.4172 | 121.312 | 121.5134 | 121.2799 | 121.4218 | 121.2982 | 75.6866 | 121.5134 | 121.2799 | 121.2982 | 121.312 | 121.4218 | -121.5912 | -44.9066
3534.7656 | 122.0718 | -67.6666 | 53.5767 | 0.2401 | 0.017205 | 0.01066 | 0.0086154 | -0.0069727 | -0.0054367 | -0.0022302 | 53.9886 | 54.1763 | -68.3395 | 54.1855 | 53.9795 | 54.0207 | 53.9017 | 54.1351 | 54.0665 | 8.4549 | -0.67291 | 0.59967 | 121.6553 | 121.8521 | 0.40283 | 76.1215 | 0.48981 | 122.3282 | 121.5683 | 121.8018 | 121.6461 | 121.843 | 121.6553 | 121.7331 | 121.6873 | 76.1215 | 121.843 | 121.6553 | 121.6873 | 121.6461 | 121.7331 | -121.9162 | -45.1218
3535.7656 | 122.2092 | -67.3737 | 54.0024 | 0.26299 | 0.01806 | 0.0098053 | 0.008829 | -0.0088953 | -0.0039413 | -0.0039392 | 54.1214 | 54.2953 | -68.2068 | 54.3091 | 54.1077 | 54.1443 | 54.0253 | 54.2633 | 54.2175 | 8.4549 | -0.83313 | 0.29297 | 121.4951 | 121.6827 | 0.10529 | 75.8286 | 0.21515 | 122.3282 | 121.3989 | 121.637 | 121.4813 | 121.669 | 121.4951 | 121.5912 | 121.5179 | 75.8286 | 121.669 | 121.4951 | 121.5179 | 121.4813 | 121.5912 | -122.2092 | -45.5475
3536.7656 | 122.3007 | -67.5018 | 53.9886 | 0.27061 | 0.015283 | 0.015146 | 0.010965 | -0.0080407 | -0.0045821 | -0.00094839 | 53.9978 | 54.1809 | -68.3441 | 54.1718 | 53.9749 | 54.007 | 53.9108 | 54.1122 | 54.0802 | 8.4595 | -0.84229 | 0.19226 | 121.4996 | 121.6736 | -0.013732 | 75.9613 | 0.091553 | 122.3419 | 121.4127 | 121.6141 | 121.4767 | 121.6827 | 121.4996 | 121.582 | 121.5088 | 75.9613 | 121.6827 | 121.4996 | 121.5088 | 121.4767 | 121.582 | -122.3328 | -45.5292
3537.7656 | 99.7879 | -64.2746 | 54.071 | 0.11803 | 0.018273 | 0.0093781 | 0.015024 | -0.0082545 | -0.0050095 | -0.0032984 | 54.0985 | 54.2953 | -68.28 | 54.2221 | 54.0298 | 54.039 | 54.1214 | 54.1626 | 54.2084 | 8.4549 | -4.0054 | 0.2243 | 118.3731 | 118.4967 | -0.041199 | 72.7295 | 0.13733 | 122.3785 | 118.396 | 118.4372 | 118.3044 | 118.5699 | 118.3731 | 118.483 | 118.3136 | 72.7295 | 118.5699 | 118.3731 | 118.3136 | 118.3044 | 118.483 | -122.3511 | -45.6161
3538.7656 | 99.939 | -67.7399 | 54.071 | 0.10277 | 0.01806 | 0.0080963 | 0.0098972 | -0.0076135 | -0.0071457 | -0.0024438 | 54.1626 | 54.3732 | -68.1839 | 54.3228 | 54.1168 | 54.1214 | 54.2084 | 54.2496 | 54.277 | 8.4457 | -0.44403 | 0.30212 | 121.9025 | 122.0627 | 0.045776 | 76.1856 | 0.20599 | 122.3465 | 121.9482 | 121.9894 | 121.8567 | 122.113 | 121.9025 | 122.0169 | 121.8613 | 76.1856 | 122.113 | 121.9025 | 121.8613 | 121.8567 | 122.0169 | -122.2549 | -45.6253
3539.7656 | 106.4941 | -67.6025 | 53.9383 | 0.19432 | 0.016137 | 0.0095917 | 0.011606 | -0.0065455 | -0.0035141 | -0.0032984 | 54.1672 | 54.3869 | -68.1885 | 54.2953 | 54.1077 | 54.1122 | 54.245 | 54.2221 | 54.3503 | 8.4595 | -0.58594 | 0.44861 | 121.7697 | 121.8979 | 0.16937 | 76.062 | 0.41199 | 122.3557 | 121.8475 | 121.8246 | 121.7102 | 121.9894 | 121.7697 | 121.9528 | 121.7148 | 76.062 | 121.9894 | 121.7697 | 121.7148 | 121.7102 | 121.9528 | -122.1268 | -45.4788
3540.7656 | 114.1663 | -67.6712 | 53.9795 | 0.1638 | 0.016564 | 0.011728 | 0.010752 | -0.0065455 | -0.0039413 | -0.0026574 | 54.1672 | 54.4144 | -68.2022 | 54.3137 | 54.0939 | 54.1214 | 54.245 | 54.2084 | 54.332 | 8.4595 | -0.531 | 0.43488 | 121.8384 | 121.9849 | 0.11444 | 76.1307 | 0.35248 | 122.3694 | 121.9162 | 121.8796 | 121.7651 | 122.0856 | 121.8384 | 122.0032 | 121.7926 | 76.1307 | 122.0856 | 121.8384 | 121.7926 | 121.7651 | 122.0032 | -122.1817 | -45.52
3541.7656 | 121.6095 | -67.7582 | 54.2084 | 0.20195 | 0.016351 | 0.011301 | 0.0096834 | -0.0048365 | -0.0043685 | -0.00052119 | 54.2084 | 54.3228 | -68.2022 | 54.4189 | 54.2175 | 54.2587 | 54.0573 | 54.3594 | 54.2862 | 8.4641 | -0.44403 | 0.11444 | 121.9666 | 122.1771 | 0.009155 | 76.2222 | 0.07782 | 122.4106 | 121.8155 | 122.1176 | 121.9757 | 122.081 | 121.9666 | 122.0444 | 122.0169 | 76.2222 | 122.081 | 121.9666 | 122.0169 | 121.9757 | 122.0444 | -122.4106 | -45.7443
3542.7656 | 121.8613 | -67.8314 | 54.1626 | 0.20195 | 0.018487 | 0.011301 | 0.0090426 | -0.0065455 | -0.0039413 | -0.0026574 | 54.1992 | 54.332 | -68.2022 | 54.3915 | 54.1855 | 54.2313 | 54.0253 | 54.3228 | 54.2358 | 8.4686 | -0.37079 | 0.16937 | 122.0306 | 122.2229 | 0.022888 | 76.3 | 0.073242 | 122.4014 | 121.8567 | 122.1542 | 122.0169 | 122.1634 | 122.0306 | 122.0673 | 122.0627 | 76.3 | 122.1634 | 122.0306 | 122.0627 | 122.0169 | 122.0673 | -122.3648 | -45.694
3543.7656 | 121.9345 | -67.8314 | 54.1489 | 0.27824 | 0.016778 | 0.010019 | 0.010111 | -0.0084681 | -0.0024459 | -0.0047938 | 54.213 | 54.3091 | -68.2068 | 54.4052 | 54.1855 | 54.2221 | 54.039 | 54.332 | 54.2267 | 8.4641 | -0.37537 | 0.16022 | 122.0444 | 122.2366 | 0.036621 | 76.2955 | 0.07782 | 122.4197 | 121.8704 | 122.1634 | 122.0169 | 122.1405 | 122.0444 | 122.0581 | 122.0535 | 76.2955 | 122.1405 | 122.0444 | 122.0535 | 122.0169 | 122.0581 | -122.3557 | -45.6848
3544.7656 | 122.3694 | -67.5613 | 54.1672 | 0.1104 | 0.017632 | 0.012796 | 0.011606 | -0.0086817 | -0.0047957 | -0.0030848 | 54.1168 | 54.332 | -68.2617 | 54.2725 | 54.0482 | 54.0527 | 54.1718 | 54.1901 | 54.2633 | 8.4503 | -0.70038 | 0.16479 | 121.6782 | 121.8338 | -0.11902 | 76.0117 | 0.096131 | 122.3785 | 121.7331 | 121.7514 | 121.6095 | 121.8933 | 121.6782 | 121.8246 | 121.6141 | 76.0117 | 121.8933 | 121.6782 | 121.6141 | 121.6095 | 121.8246 | -122.4289 | -45.7169
3545.7656 | 121.5866 | -67.5476 | 54.1214 | 0.095139 | 0.019769 | 0.0098053 | 0.011392 | -0.0073999 | -0.0050095 | -0.00073479 | 54.1443 | 54.3594 | -68.2709 | 54.2862 | 54.071 | 54.0802 | 54.1855 | 54.2038 | 54.2953 | 8.4595 | -0.72327 | 0.23804 | 121.6919 | 121.8338 | -0.050354 | 76.0071 | 0.17395 | 122.4152 | 121.7331 | 121.7514 | 121.6187 | 121.907 | 121.6919 | 121.843 | 121.6278 | 76.0071 | 121.907 | 121.6919 | 121.6278 | 121.6187 | 121.843 | -122.3923 | -45.6619
3546.7656 | 121.5637 | -67.8497 | 54.1489 | 0.17906 | 0.018487 | 0.0066009 | 0.015451 | -0.0067591 | -0.0050095 | -0.0030848 | 54.0939 | 54.3365 | -68.3121 | 54.2953 | 54.1077 | 54.1168 | 54.1306 | 54.2267 | 54.2725 | 8.4595 | -0.46234 | 0.18768 | 121.9437 | 122.1451 | -0.041199 | 76.3092 | 0.1236 | 122.406 | 121.9803 | 122.0764 | 121.9574 | 122.1863 | 121.9437 | 122.1222 | 121.9666 | 76.3092 | 122.1863 | 121.9437 | 121.9666 | 121.9574 | 122.1222 | -122.4609 | -45.6894
3547.7812 | 121.637 | -67.9642 | 54.1077 | 0.20195 | 0.017632 | 0.01066 | 0.0098972 | -0.0076135 | -0.0039413 | -0.0015894 | 54.0802 | 54.2862 | -68.3304 | 54.2404 | 54.0482 | 54.0527 | 54.0619 | 54.1672 | 54.1992 | 8.4595 | -0.36621 | 0.17853 | 122.0444 | 122.2046 | -0.059509 | 76.4236 | 0.091553 | 122.4106 | 122.0261 | 122.1313 | 122.0123 | 122.2504 | 122.0444 | 122.1634 | 122.0169 | 76.4236 | 122.2504 | 122.0444 | 122.0169 | 122.0123 | 122.1634 | -122.438 | -45.6482
3548.7656 | 122.2183 | -67.9504 | 54.0756 | 0.27061 | 0.017846 | 0.0068147 | 0.0092562 | -0.0091089 | -0.0045821 | -0.0024438 | 54.1534 | 54.2542 | -68.3029 | 54.332 | 54.1214 | 54.1763 | 53.9566 | 54.2816 | 54.1809 | 8.4595 | -0.35248 | 0.17853 | 122.1039 | 122.2824 | 0.045776 | 76.4099 | 0.10529 | 122.4564 | 121.907 | 122.2321 | 122.0718 | 122.2046 | 122.1039 | 122.1313 | 122.1268 | 76.4099 | 122.2046 | 122.1039 | 122.1268 | 122.0718 | 122.1313 | -122.3785 | -45.6162
3549.7812 | 122.3923 | -67.9642 | 54.1214 | -0.0040434 | 0.012505 | 0.0059601 | 0.0015658 | -0.010604 | -0.0035141 | -0.0028712 | 54.1031 | 54.1901 | -68.3075 | 54.3549 | 54.1718 | 54.1946 | 53.9886 | 54.3503 | 54.1946 | 8.4595 | -0.34332 | 0.068664 | 122.0673 | 122.319 | 0.050354 | 76.4236 | 0.073242 | 122.4106 | 121.9528 | 122.3145 | 122.1359 | 122.1542 | 122.0673 | 122.1588 | 122.1588 | 76.4236 | 122.1542 | 122.0673 | 122.1588 | 122.1359 | 122.1588 | -122.4289 | -45.6619
3550.7656 | 121.8475 | -68.0145 | 54.0619 | 0.34691 | 0.01571 | 0.013223 | 0.013101 | -0.0065455 | -0.0058639 | -0.0011622 | 54.1351 | 54.2038 | -68.3395 | 54.3137 | 54.1031 | 54.126 | 53.92 | 54.2587 | 54.1626 | 8.4686 | -0.32501 | 0.14191 | 122.1497 | 122.3282 | 0.041198 | 76.4832 | 0.10071 | 122.4747 | 121.9345 | 122.2733 | 122.1176 | 122.2183 | 122.1497 | 122.1771 | 122.1405 | 76.4832 | 122.2183 | 122.1497 | 122.1405 | 122.1176 | 122.1771 | -122.4014 | -45.5933
3551.7656 | 121.4767 | -67.749 | 54.0115 | 0.12566 | 0.016564 | 0.01365 | 0.011179 | -0.0061181 | -0.0047957 | -0.0020166 | 53.9795 | 54.2038 | -68.454 | 54.1489 | 53.9291 | 53.9383 | 54.0527 | 54.0573 | 54.1626 | 8.4686 | -0.70496 | 0.19226 | 121.7285 | 121.8979 | -0.082398 | 76.2177 | 0.15106 | 122.4335 | 121.8018 | 121.8063 | 121.6782 | 121.9528 | 121.7285 | 121.9116 | 121.6873 | 76.2177 | 121.9528 | 121.7285 | 121.6873 | 121.6782 | 121.9116 | -122.4655 | -45.5429
3552.7656 | 121.6919 | -67.9596 | 54.1077 | 2.2161 | 0.012505 | 0.0098053 | 0.011179 | -0.0078271 | -0.0043685 | -0.0032984 | 54.2725 | 54.245 | -68.3807 | 54.245 | 54.0436 | 54.0115 | 54.071 | 54.1306 | 54.1992 | 8.4549 | -0.42114 | 0.13733 | 122.2321 | 122.2046 | -0.064087 | 76.4145 | 0.091553 | 122.6532 | 122.0306 | 122.0901 | 122.0032 | 122.2046 | 122.2321 | 122.1588 | 121.9711 | 76.4145 | 122.2046 | 122.2321 | 121.9711 | 122.0032 | 122.1588 | -122.4884 | -45.6528
3553.7656 | 121.8613 | -68.074 | 54.0894 | 0.17143 | 0.01806 | 0.0083099 | 0.0096834 | -0.010177 | -0.0067185 | -0.0020166 | 54.0298 | 54.2404 | -68.4219 | 54.2358 | 54.0344 | 53.9612 | 54.1214 | 54.1214 | 54.1992 | 8.4549 | -0.3479 | 0.15106 | 122.1039 | 122.3099 | -0.054931 | 76.5289 | 0.10986 | 122.4518 | 122.1954 | 122.1954 | 122.1085 | 122.3145 | 122.1039 | 122.2733 | 122.0352 | 76.5289 | 122.3145 | 122.1039 | 122.0352 | 122.1085 | 122.2733 | -122.5113 | -45.6345
3554.7812 | 122.4243 | -68.1152 | 54.0024 | -0.026932 | 0.012292 | 0.0068147 | 0.0024202 | -0.011031 | -0.0030869 | -0.003512 | 53.9749 | 54.0848 | -68.4952 | 54.2221 | 54.0253 | 54.0436 | 53.9017 | 54.2084 | 54.0665 | 8.4641 | -0.37994 | 0.082398 | 122.0901 | 122.3373 | 0.022889 | 76.5793 | 0.064087 | 122.4701 | 122.0169 | 122.3236 | 122.1405 | 122.2 | 122.0901 | 122.1817 | 122.1588 | 76.5793 | 122.2 | 122.0901 | 122.1588 | 122.1405 | 122.1817 | -122.4976 | -45.5383
3555.7656 | 122.1817 | -68.4174 | 53.6499 | 0.40794 | 0.017205 | 0.010446 | 0.012033 | -0.0073999 | -0.0058639 | -0.0037256 | 53.8055 | 53.8605 | -68.7195 | 53.9383 | 53.714 | 53.7598 | 53.5172 | 53.8376 | 53.7643 | 8.4641 | -0.30212 | 0.21057 | 122.2229 | 122.3557 | 0.064087 | 76.8814 | 0.11444 | 122.525 | 121.9345 | 122.2549 | 122.1313 | 122.2778 | 122.2229 | 122.1817 | 122.1771 | 76.8814 | 122.2778 | 122.2229 | 122.1771 | 122.1313 | 122.1817 | -122.3694 | -45.1859
3556.7656 | 122.2504 | -68.1152 | 53.9886 | 0.40031 | 0.01571 | 0.0085235 | 0.011179 | -0.0091089 | -0.0033005 | -0.0024438 | 54.0665 | 54.1397 | -68.4402 | 54.2404 | 54.0207 | 54.0619 | 53.8513 | 54.1901 | 54.071 | 8.4549 | -0.32501 | 0.15106 | 122.1817 | 122.3557 | 0.032044 | 76.5701 | 0.082398 | 122.5067 | 121.9666 | 122.3053 | 122.1359 | 122.2549 | 122.1817 | 122.1863 | 122.1771 | 76.5701 | 122.2549 | 122.1817 | 122.1771 | 122.1359 | 122.1863 | -122.4289 | -45.5338
3557.7656 | 122.4014 | -68.129 | 53.9978 | 0.32402 | 0.015496 | 0.010446 | 0.010538 | -0.0091089 | -0.0028731 | -0.0043664 | 54.0573 | 54.1489 | -68.4586 | 54.2404 | 54.039 | 54.0482 | 53.8696 | 54.1672 | 54.0802 | 8.4641 | -0.32959 | 0.15106 | 122.1863 | 122.3694 | 0.041198 | 76.593 | 0.082397 | 122.5159 | 121.9986 | 122.2961 | 122.168 | 122.2778 | 122.1863 | 122.2092 | 122.1771 | 76.593 | 122.2778 | 122.1863 | 122.1771 | 122.168 | 122.2092 | -122.4564 | -45.5338
3558.7656 | 121.8658 | -68.0328 | 54.1809 | 0.18669 | 0.018487 | 0.014505 | 0.015451 | -0.0084681 | -0.0045821 | -0.0028712 | 54.0939 | 54.2999 | -68.399 | 54.2267 | 54.0298 | 54.0207 | 54.1809 | 54.1718 | 54.245 | 8.4595 | -0.36621 | 0.11902 | 122.1268 | 122.2595 | -0.15106 | 76.4923 | 0.064087 | 122.493 | 122.2137 | 122.2046 | 122.0627 | 122.3328 | 122.1268 | 122.2778 | 122.0535 | 76.4923 | 122.3328 | 122.1268 | 122.0535 | 122.0627 | 122.2778 | -122.58 | -45.7214
3559.7812 | 122.4655 | -68.0786 | 54.0985 | 0.011215 | 0.012505 | 0.0033967 | 0.0039156 | -0.011031 | -0.0045821 | -0.0022302 | 54.0665 | 54.1672 | -68.4357 | 54.3091 | 54.1443 | 54.1489 | 53.9886 | 54.2999 | 54.1306 | 8.4686 | -0.35706 | 0.068664 | 122.1451 | 122.3877 | 0.045776 | 76.5472 | 0.032043 | 122.5021 | 122.0673 | 122.3785 | 122.2229 | 122.2458 | 122.1451 | 122.2092 | 122.2275 | 76.5472 | 122.2458 | 122.1451 | 122.2275 | 122.2229 | 122.2092 | -122.5342 | -45.6299
3560.7656 | 121.9345 | -68.3853 | 53.8467 | 0.20195 | 0.016778 | 0.010019 | 0.012674 | -0.0099633 | -0.0043685 | -0.0037256 | 53.7872 | 53.9749 | -68.6966 | 53.9566 | 53.7186 | 53.7827 | 53.3295 | 53.7781 | 53.8834 | 8.4595 | -0.31128 | 0.12817 | 122.1725 | 122.3419 | -0.12817 | 76.8448 | 0.036621 | 122.4838 | 121.7148 | 122.1634 | 122.1039 | 122.3602 | 122.1725 | 122.2687 | 122.168 | 76.8448 | 122.3602 | 122.1725 | 122.168 | 122.1039 | 122.2687 | -122.5433 | -45.3873
3561.7812 | 122.2321 | -68.4265 | 53.7552 | 0.23247 | 0.016992 | 0.0089509 | 0.0092562 | -0.0073999 | -0.0024459 | -0.00030759 | 53.7506 | 53.9246 | -68.7607 | 53.8971 | 53.6819 | 53.6911 | 53.7231 | 53.8101 | 53.8651 | 8.4641 | -0.33417 | 0.16937 | 122.1771 | 122.3236 | -0.073242 | 76.8906 | 0.10986 | 122.5113 | 122.1497 | 122.2366 | 122.1085 | 122.3511 | 122.1771 | 122.2916 | 122.1176 | 76.8906 | 122.3511 | 122.1771 | 122.1176 | 122.1085 | 122.2916 | -122.5159 | -45.2911
3562.7656 | 122.4838 | -68.8477 | 53.2883 | 0.2401 | 0.015923 | 0.011514 | 0.0086154 | -0.0086817 | -0.0028731 | -0.0041528 | 53.3844 | 53.4897 | -69.1818 | 53.5446 | 53.3524 | 53.3752 | 53.1464 | 53.4714 | 53.3661 | 8.4595 | -0.33417 | 0.20142 | 122.2321 | 122.3923 | 0.064087 | 77.3071 | 0.07782 | 122.5662 | 121.994 | 122.319 | 122.2 | 122.3373 | 122.2321 | 122.2137 | 122.2229 | 77.3071 | 122.3373 | 122.2321 | 122.2229 | 122.2 | 122.2137 | -122.4701 | -44.8288
3563.7656 | 122.4701 | -68.9163 | 53.2196 | 0.21721 | 0.017205 | 0.0061737 | 0.010324 | -0.0086817 | -0.0043685 | -0.0020166 | 53.2928 | 53.3981 | -69.2551 | 53.4805 | 53.2745 | 53.3157 | 53.0823 | 53.4073 | 53.302 | 8.4641 | -0.33875 | 0.17853 | 122.2092 | 122.3969 | 0.054932 | 77.3804 | 0.082398 | 122.5479 | 121.9986 | 122.3236 | 122.1909 | 122.3145 | 122.2092 | 122.2183 | 122.2321 | 77.3804 | 122.3145 | 122.2092 | 122.2321 | 122.1909 | 122.2183 | -122.4747 | -44.7556
3564.7812 | 122.4747 | -69.1635 | 53.0045 | -0.057449 | 0.014214 | 0.0059601 | 0.0045566 | -0.0086817 | -0.0043685 | -0.0022302 | 53.0365 | 53.1372 | -69.5297 | 53.2562 | 53.0777 | 53.0777 | 52.8671 | 53.2333 | 53.0731 | 8.4595 | -0.36621 | 0.13275 | 122.2 | 122.4197 | 0.073242 | 77.623 | 0.068664 | 122.5662 | 122.0306 | 122.3969 | 122.2412 | 122.3007 | 122.2 | 122.2366 | 122.2412 | 77.623 | 122.3007 | 122.2 | 122.2412 | 122.2412 | 122.2366 | -122.5342 | -44.545
3565.7656 | 122.0261 | -68.3304 | 53.9154 | 0.011215 | 0.016351 | 0.013223 | 0.011606 | -0.0084681 | -0.0058639 | -0.0037256 | 53.9474 | 54.0619 | -68.6417 | 54.0756 | 53.8513 | 53.8651 | 53.8834 | 53.9841 | 54.0207 | 8.4549 | -0.31128 | 0.14648 | 122.2778 | 122.406 | -0.064087 | 76.7853 | 0.10529 | 122.5891 | 122.2137 | 122.3145 | 122.1817 | 122.3923 | 122.2778 | 122.3511 | 122.1954 | 76.7853 | 122.3923 | 122.2778 | 122.1954 | 122.1817 | 122.3511 | -122.5571 | -45.4605
3566.7656 | 122.319 | -68.8156 | 53.4164 | 0.15617 | 0.019128 | 0.0093781 | 0.013529 | -0.0067591 | -0.0018051 | 0.00033321 | 53.3524 | 53.5446 | -69.2001 | 53.27 | 53.389 | 53.54 | 53.389 | 53.5309 | 53.54 | 8.4686 | -0.38452 | 0.12817 | 122.168 | 122.0856 | -0.027466 | 77.2842 | 0.1236 | 122.5525 | 122.2046 | 122.3465 | 122.2046 | 122.3602 | 122.168 | 122.3557 | 122.3557 | 77.2842 | 122.3602 | 122.168 | 122.3557 | 122.2046 | 122.3557 | -122.6166 | -44.9478
3567.7656 | 122.406 | -68.8477 | 53.421 | 0.095139 | 0.016992 | 0.011301 | 0.010965 | -0.0061181 | -0.0050095 | -0.00052119 | 53.3569 | 53.6041 | -69.1772 | 53.5126 | 53.3203 | 53.3249 | 53.3661 | 53.2791 | 53.4714 | 8.4641 | -0.32959 | 0.1831 | 122.2046 | 122.3602 | -0.10071 | 77.3117 | 0.050354 | 122.5342 | 122.2137 | 122.1268 | 122.168 | 122.4518 | 122.2046 | 122.319 | 122.1725 | 77.3117 | 122.4518 | 122.2046 | 122.1725 | 122.168 | 122.319 | -122.5983 | -44.957
3568.7812 | 122.2687 | -68.1931 | 54.0573 | 0.40794 | 0.01571 | 0.0087373 | 0.012033 | -0.0059045 | -0.0030869 | -0.0058618 | 54.007 | 54.2175 | -68.541 | 54.1946 | 53.9841 | 53.9841 | 54.0207 | 54.0894 | 54.1489 | 8.4732 | -0.3479 | 0.16022 | 122.2 | 122.3877 | -0.073242 | 76.6663 | 0.091553 | 122.5479 | 122.2137 | 122.2824 | 122.1771 | 122.4106 | 122.2 | 122.3419 | 122.1771 | 76.6663 | 122.4106 | 122.2 | 122.1771 | 122.1771 | 122.3419 | -122.5983 | -45.5841
3569.7656 | 122.4884 | -68.5364 | 53.6591 | 0.22484 | 0.014214 | 0.010446 | 0.0092562 | -0.0071863 | -0.0028731 | -0.0011622 | 53.7552 | 53.8879 | -68.8339 | 53.92 | 53.7186 | 53.7277 | 53.5263 | 53.8284 | 53.7506 | 8.4686 | -0.29755 | 0.22888 | 122.2916 | 122.4564 | 0.059509 | 77.005 | 0.091552 | 122.5891 | 122.0627 | 122.3648 | 122.2549 | 122.4243 | 122.2916 | 122.287 | 122.2641 | 77.005 | 122.4243 | 122.2916 | 122.2641 | 122.2549 | 122.287 | -122.493 | -45.1904
3570.7656 | 122.493 | -68.3716 | 53.8239 | 0.27824 | 0.014001 | 0.014291 | 0.0096834 | -0.0065455 | -0.0060775 | -0.0047938 | 53.8696 | 53.9978 | -68.7149 | 54.0619 | 53.8559 | 53.8879 | 53.7186 | 53.9291 | 53.9291 | 8.4686 | -0.34332 | 0.17395 | 122.2412 | 122.4335 | 0.032043 | 76.8402 | 0.10529 | 122.5845 | 122.0901 | 122.3007 | 122.2275 | 122.3694 | 122.2412 | 122.3007 | 122.2595 | 76.8402 | 122.3694 | 122.2412 | 122.2595 | 122.2275 | 122.3007 | -122.5388 | -45.3552
3571.7656 | 122.3602 | -68.454 | 53.8101 | 0.13329 | 0.016992 | 0.011087 | 0.013101 | -0.0041955 | -0.0037277 | -0.0032984 | 53.7827 | 54.0024 | -68.8293 | 53.9383 | 53.7323 | 53.7323 | 53.7918 | 53.8467 | 53.8971 | 8.4595 | -0.37537 | 0.19226 | 122.2366 | 122.3923 | -0.07782 | 76.9135 | 0.086975 | 122.612 | 122.2458 | 122.3007 | 122.1863 | 122.4564 | 122.2366 | 122.3511 | 122.1863 | 76.9135 | 122.4564 | 122.2366 | 122.1863 | 122.1863 | 122.3511 | -122.6395 | -45.3506
3572.7656 | 122.2 | -68.4402 | 53.8376 | 0.1104 | 0.016564 | 0.0031831 | 0.011606 | -0.0065455 | -0.0052231 | -0.0020166 | 53.8284 | 54.0207 | -68.7515 | 53.9749 | 53.7643 | 53.7689 | 53.8284 | 53.8971 | 53.9383 | 8.4595 | -0.31128 | 0.18311 | 122.2687 | 122.4152 | -0.073242 | 76.8997 | 0.10071 | 122.58 | 122.2687 | 122.3373 | 122.2046 | 122.4609 | 122.2687 | 122.3785 | 122.2092 | 76.8997 | 122.4609 | 122.2687 | 122.2092 | 122.2046 | 122.3785 | -122.5891 | -45.3781
3573.7656 | 122.3877 | -68.2388 | 54.0298 | 0.17906 | 0.015923 | 0.011301 | 0.011392 | -0.0063317 | -0.0043685 | -0.0020166 | 53.9795 | 54.2496 | -68.605 | 54.1122 | 53.9337 | 53.9291 | 54.0253 | 54.0482 | 54.1031 | 8.4641 | -0.36621 | 0.21973 | 122.2183 | 122.3511 | -0.09613 | 76.7029 | 0.073242 | 122.5845 | 122.2641 | 122.287 | 122.1725 | 122.4884 | 122.2183 | 122.3419 | 122.168 | 76.7029 | 122.4884 | 122.2183 | 122.168 | 122.1725 | 122.3419 | -122.6349 | -45.5658
3574.7656 | 122.3282 | -68.367 | 53.9246 | 0.20195 | 0.015496 | 0.010446 | 0.011179 | -0.0067591 | -0.0035141 | -0.0037256 | 53.8559 | 54.0985 | -68.7103 | 54.007 | 53.8101 | 53.8101 | 53.9154 | 53.9108 | 53.9795 | 8.4641 | -0.34332 | 0.17395 | 122.2229 | 122.374 | -0.11444 | 76.8311 | 0.054931 | 122.5662 | 122.2824 | 122.2778 | 122.1771 | 122.4655 | 122.2229 | 122.3465 | 122.1771 | 76.8311 | 122.4655 | 122.2229 | 122.1771 | 122.1771 | 122.3465 | -122.6349 | -45.4605
3575.7656 | 122.4014 | -68.074 | 54.2404 | 0.1104 | 0.016351 | 0.0078827 | 0.012461 | -0.0071863 | -0.0020187 | -0.0026574 | 54.1901 | 54.4281 | -68.3899 | 54.2953 | 54.1168 | 54.1214 | 54.2221 | 54.245 | 54.3091 | 8.4641 | -0.31586 | 0.18768 | 122.2641 | 122.3694 | -0.1236 | 76.5381 | 0.068665 | 122.58 | 122.2961 | 122.319 | 122.1909 | 122.5021 | 122.2641 | 122.3831 | 122.1954 | 76.5381 | 122.5021 | 122.2641 | 122.1954 | 122.1909 | 122.3831 | -122.6303 | -45.7764
3576.7656 | 122.5433 | -68.0923 | 54.126 | 0.27824 | 0.016351 | 0.0095917 | 0.0096834 | -0.0086817 | -0.0043685 | -0.0024438 | 54.1718 | 54.3182 | -68.4402 | 54.3686 | 54.1718 | 54.2038 | 53.9932 | 54.2496 | 54.2221 | 8.4641 | -0.3479 | 0.19226 | 122.2641 | 122.4609 | 0.045776 | 76.5564 | 0.09613 | 122.612 | 122.0856 | 122.3419 | 122.2641 | 122.4106 | 122.2641 | 122.3145 | 122.2961 | 76.5564 | 122.4106 | 122.2641 | 122.2961 | 122.2641 | 122.3145 | -122.5662 | -45.6619
3577.7656 | 122.5479 | -68.074 | 54.1855 | 0.26299 | 0.016992 | 0.010873 | 0.010752 | -0.0065455 | -0.0039413 | -0.00052119 | 54.1855 | 54.3732 | -68.399 | 54.3686 | 54.1901 | 54.2038 | 54.071 | 54.3228 | 54.2816 | 8.4641 | -0.32501 | 0.18768 | 122.2595 | 122.4426 | 0.004577 | 76.5381 | 0.09613 | 122.5845 | 122.1451 | 122.3969 | 122.2641 | 122.4472 | 122.2595 | 122.3557 | 122.2778 | 76.5381 | 122.4472 | 122.2595 | 122.2778 | 122.2641 | 122.3557 | -122.5845 | -45.7214
3578.7656 | 122.4197 | -68.0328 | 54.2908 | 0.049362 | 0.016778 | 0.0095917 | 0.01182 | -0.0050501 | -0.0058639 | -0.0037256 | 54.2587 | 54.451 | -68.3807 | 54.4006 | 54.1855 | 54.1946 | 54.2725 | 54.3182 | 54.3915 | 8.4595 | -0.3479 | 0.16022 | 122.2916 | 122.4335 | -0.10529 | 76.4923 | 0.10071 | 122.6395 | 122.3053 | 122.3511 | 122.2183 | 122.4838 | 122.2916 | 122.4243 | 122.2275 | 76.4923 | 122.4838 | 122.2916 | 122.2275 | 122.2183 | 122.4243 | -122.6715 | -45.8313
3579.7656 | 122.3465 | -68.1427 | 54.158 | 0.10277 | 0.017846 | 0.0093781 | 0.013101 | -0.0076135 | -0.0065047 | -0.001803 | 54.1443 | 54.3503 | -68.4769 | 54.3091 | 54.0985 | 54.1031 | 54.1534 | 54.213 | 54.277 | 8.4503 | -0.33417 | 0.19226 | 122.287 | 122.4518 | -0.059509 | 76.593 | 0.11902 | 122.6212 | 122.2961 | 122.3557 | 122.2412 | 122.493 | 122.287 | 122.4197 | 122.2458 | 76.593 | 122.493 | 122.287 | 122.2458 | 122.2412 | 122.4197 | -122.6349 | -45.7077
3580.7656 | 122.4518 | -68.2297 | 54.1168 | 0.19432 | 0.018701 | 0.014078 | 0.013101 | -0.0073999 | -0.0071457 | -0.0026574 | 54.0253 | 54.3045 | -68.573 | 54.1718 | 54.007 | 53.9658 | 54.0985 | 54.1077 | 54.1946 | 8.4641 | -0.34332 | 0.18768 | 122.2549 | 122.4014 | -0.10986 | 76.6937 | 0.07782 | 122.5983 | 122.3282 | 122.3373 | 122.2366 | 122.5342 | 122.2549 | 122.4243 | 122.1954 | 76.6937 | 122.5342 | 122.2549 | 122.1954 | 122.2366 | 122.4243 | -122.6898 | -45.6528
3581.7656 | 122.4197 | -68.0878 | 54.245 | 0.18669 | 0.015496 | 0.0093781 | 0.012247 | -0.0067591 | -0.0054367 | -0.0015894 | 54.1718 | 54.3915 | -68.454 | 54.3274 | 54.1489 | 54.1306 | 54.2587 | 54.245 | 54.3594 | 8.4549 | -0.36621 | 0.14648 | 122.2595 | 122.4152 | -0.09613 | 76.5427 | 0.11444 | 122.6257 | 122.3465 | 122.3328 | 122.2366 | 122.4792 | 122.2595 | 122.4472 | 122.2183 | 76.5427 | 122.4792 | 122.2595 | 122.2183 | 122.2366 | 122.4472 | -122.699 | -45.7901
3582.7812 | 122.4426 | -68.2114 | 54.0985 | 0.87334 | 0.018487 | 0.0061737 | 0.011392 | -0.0067591 | -0.0026595 | -0.0024438 | 54.0665 | 54.2862 | -68.5684 | 54.2313 | 54.0344 | 54.039 | 54.1031 | 54.1397 | 54.2313 | 8.4686 | -0.35706 | 0.18768 | 122.2778 | 122.4426 | -0.064087 | 76.68 | 0.13275 | 122.6349 | 122.3145 | 122.3511 | 122.2458 | 122.4976 | 122.2778 | 122.4426 | 122.2504 | 76.68 | 122.4976 | 122.2778 | 122.2504 | 122.2458 | 122.4426 | -122.6669 | -45.6299
3583.7656 | 122.5708 | -68.1427 | 54.0894 | 0.25536 | 0.014642 | 0.011087 | 0.0096834 | -0.0059045 | -0.0062911 | -0.0013758 | 54.1489 | 54.2908 | -68.5089 | 54.3228 | 54.1397 | 54.158 | 53.9566 | 54.2038 | 54.213 | 8.4686 | -0.36621 | 0.20142 | 122.2916 | 122.4655 | 0.050354 | 76.6113 | 0.1236 | 122.6578 | 122.0993 | 122.3465 | 122.2824 | 122.4335 | 122.2916 | 122.3557 | 122.3007 | 76.6113 | 122.4335 | 122.2916 | 122.3007 | 122.2824 | 122.3557 | -122.5983 | -45.6207
3584.7656 | 122.5479 | -68.1976 | 54.0848 | 0.2401 | 0.017419 | 0.015359 | 0.0081882 | -0.0046229 | -0.0030869 | -0.00073479 | 54.1077 | 54.245 | -68.5501 | 54.2816 | 54.0756 | 54.1077 | 53.9795 | 54.2313 | 54.1763 | 8.4641 | -0.35248 | 0.16022 | 122.3053 | 122.4792 | -0.009155 | 76.6617 | 0.091553 | 122.6578 | 122.1771 | 122.4289 | 122.2733 | 122.4426 | 122.3053 | 122.374 | 122.3053 | 76.6617 | 122.4426 | 122.3053 | 122.3053 | 122.2733 | 122.374 | -122.6349 | -45.6207
3585.7656 | 122.4243 | -68.3304 | 54.007 | 0.10277 | 0.019982 | 0.0085235 | 0.012247 | -0.0076135 | -0.0041549 | -0.00073479 | 53.9978 | 54.1901 | -68.6462 | 54.1306 | 53.9383 | 53.9383 | 53.9978 | 54.0436 | 54.1306 | 8.4595 | -0.31586 | 0.18311 | 122.3282 | 122.4609 | -0.068665 | 76.7899 | 0.1236 | 122.644 | 122.3282 | 122.374 | 122.2687 | 122.5204 | 122.3282 | 122.4609 | 122.2687 | 76.7899 | 122.5204 | 122.3282 | 122.2687 | 122.2687 | 122.4609 | -122.6532 | -45.5475
3586.7656 | 122.4747 | -76.4832 | 45.8359 | 0.07988 | 0.018273 | 0.0083099 | 0.01417 | -0.0080407 | -0.0045821 | -0.0015894 | 45.8359 | 45.9961 | -76.8402 | 45.9595 | 45.7672 | 45.7901 | 45.5429 | 45.8954 | 45.9274 | 8.4595 | -0.35706 | 0.16022 | 122.319 | 122.4426 | -0.068664 | 84.9426 | 0.091553 | 122.6761 | 122.0261 | 122.3785 | 122.2504 | 122.4792 | 122.319 | 122.4106 | 122.2733 | 84.9426 | 122.4792 | 122.319 | 122.2733 | 122.2504 | 122.4106 | -122.6761 | -37.3764
3587.7656 | 122.4655 | -76.3779 | 45.9641 | 0.1638 | 0.016778 | 0.0080963 | 0.012247 | -0.0048365 | -0.0037277 | -0.0028712 | 45.9274 | 46.1105 | -76.7441 | 46.0419 | 45.8542 | 45.8817 | 45.6528 | 45.9915 | 46.1105 | 8.4732 | -0.36621 | 0.14648 | 122.3053 | 122.4197 | -0.10986 | 84.8511 | 0.14648 | 122.6715 | 122.0306 | 122.3694 | 122.2321 | 122.4884 | 122.3053 | 122.4884 | 122.2595 | 84.8511 | 122.4884 | 122.3053 | 122.2595 | 122.2321 | 122.4884 | -122.7081 | -37.4908
3588.7656 | 122.4701 | -76.1261 | 46.225 | 0.15617 | 0.016351 | 0.0085235 | 0.013529 | -0.0052637 | -0.0041549 | -0.0030848 | 46.1746 | 46.3943 | -76.4557 | 46.3074 | 46.1151 | 46.1472 | 45.9366 | 46.2433 | 46.3257 | 8.4641 | -0.32959 | 0.16937 | 122.3007 | 122.4335 | -0.10986 | 84.5901 | 0.10071 | 122.6303 | 122.0627 | 122.3694 | 122.2412 | 122.5204 | 122.3007 | 122.4518 | 122.2733 | 84.5901 | 122.5204 | 122.3007 | 122.2733 | 122.2412 | 122.4518 | -122.6807 | -37.7609
3589.7656 | 122.612 | -76.1398 | 46.1472 | 0.22484 | 0.01336 | 0.0066009 | 0.012674 | -0.0063317 | -0.0041549 | -0.00073479 | 46.1838 | 46.2936 | -76.506 | 46.344 | 46.1334 | 46.1609 | 45.7352 | 46.3257 | 46.2296 | 8.4732 | -0.36621 | 0.14648 | 122.3236 | 122.4838 | -0.013733 | 84.613 | 0.082397 | 122.6898 | 121.875 | 122.4655 | 122.2733 | 122.4335 | 122.3236 | 122.3694 | 122.3007 | 84.613 | 122.4335 | 122.3236 | 122.3007 | 122.2733 | 122.3694 | -122.6532 | -37.674
3590.7656 | 122.2504 | -68.1244 | 54.1901 | 0.25536 | 0.017632 | 0.011301 | 0.010324 | -0.0067591 | -0.0039413 | -0.0039392 | 54.2038 | 54.3274 | -68.4723 | 54.4006 | 54.2038 | 54.2313 | 54.0344 | 54.277 | 54.2633 | 8.4686 | -0.3479 | 0.13733 | 122.3282 | 122.525 | 0.013733 | 76.593 | 0.073243 | 122.6761 | 122.1588 | 122.4014 | 122.3282 | 122.4518 | 122.3282 | 122.3877 | 122.3557 | 76.593 | 122.4518 | 122.3282 | 122.3557 | 122.3282 | 122.3877 | -122.6624 | -45.7214
3591.7656 | 122.5891 | -68.0923 | 54.1946 | 0.21721 | 0.016351 | 0.011728 | 0.010324 | -0.0091089 | -0.0030869 | -0.003512 | 54.2313 | 54.3823 | -68.4677 | 54.4052 | 54.2084 | 54.2496 | 54.0985 | 54.3365 | 54.2862 | 8.4686 | -0.37537 | 0.18768 | 122.3236 | 122.4976 | 0.013733 | 76.561 | 0.091553 | 122.699 | 122.1909 | 122.4289 | 122.3007 | 122.4747 | 122.3236 | 122.3785 | 122.3419 | 76.561 | 122.4747 | 122.3236 | 122.3419 | 122.3007 | 122.3785 | -122.6624 | -45.726
3592.7656 | 122.3373 | -68.1976 | 54.2267 | 0.095139 | 0.01806 | 0.0072419 | 0.013101 | -0.0063317 | -0.0035141 | -0.0024438 | 54.1672 | 54.3594 | -68.5043 | 54.3137 | 54.0894 | 54.1122 | 54.1946 | 54.2313 | 54.2816 | 8.4641 | -0.3067 | 0.13275 | 122.3648 | 122.5113 | -0.13733 | 76.6617 | 0.054931 | 122.6715 | 122.3923 | 122.4289 | 122.287 | 122.5571 | 122.3648 | 122.4792 | 122.3099 | 76.6617 | 122.5571 | 122.3648 | 122.3099 | 122.287 | 122.4792 | -122.731 | -45.7626
3593.7656 | 122.1268 | -68.1427 | 54.2404 | 0.087509 | 0.015496 | 0.012796 | 0.012461 | -0.0076135 | -0.0058639 | -0.0032984 | 54.2038 | 54.4235 | -68.4769 | 54.3503 | 54.1214 | 54.1534 | 54.2221 | 54.2633 | 54.332 | 8.4686 | -0.33417 | 0.18311 | 122.3465 | 122.493 | -0.11902 | 76.6113 | 0.091553 | 122.6807 | 122.3648 | 122.406 | 122.2641 | 122.5662 | 122.3465 | 122.4747 | 122.2961 | 76.6113 | 122.5662 | 122.3465 | 122.2961 | 122.2641 | 122.4747 | -122.7173 | -45.7718
3594.7656 | 122.5113 | -75.7736 | 46.5729 | 0.17143 | 0.015069 | 0.0098053 | 0.01481 | -0.0095361 | -0.0020187 | -0.0011622 | 46.55 | 46.7743 | -76.1581 | 46.7331 | 46.5683 | 46.5179 | 46.3623 | 46.6599 | 46.6873 | 8.4686 | -0.38452 | 0.20142 | 122.3236 | 122.5067 | -0.004578 | 84.2422 | 0.11444 | 122.7081 | 122.1359 | 122.4335 | 122.3419 | 122.5479 | 122.3236 | 122.4609 | 122.2916 | 84.2422 | 122.5479 | 122.3236 | 122.2916 | 122.3419 | 122.4609 | -122.731 | -38.1042
3595.7656 | 122.5159 | -75.7645 | 46.6415 | 0.18669 | 0.016992 | 0.010232 | 0.010752 | -0.0054773 | -0.0054367 | -0.0028712 | 46.6049 | 46.8018 | -76.1215 | 46.756 | 46.5271 | 46.5683 | 46.3943 | 46.6827 | 46.7239 | 8.4686 | -0.35706 | 0.16022 | 122.3694 | 122.5204 | -0.11444 | 84.2331 | 0.082397 | 122.7264 | 122.1588 | 122.4472 | 122.2916 | 122.5662 | 122.3694 | 122.4884 | 122.3328 | 84.2331 | 122.5662 | 122.3694 | 122.3328 | 122.2916 | 122.4884 | -122.7631 | -38.1729
3596.7656 | 122.6349 | -75.6683 | 46.6827 | 0.28587 | 0.013574 | 0.015146 | 0.011606 | -0.0080407 | -0.0043685 | -0.0015894 | 46.7285 | 46.8063 | -76.0025 | 46.9666 | 46.7468 | 46.7422 | 46.3074 | 46.8887 | 46.7468 | 8.4732 | -0.33417 | 0.1236 | 122.3969 | 122.6349 | 0.064087 | 84.1415 | 0.064087 | 122.731 | 121.9757 | 122.5571 | 122.4152 | 122.4747 | 122.3969 | 122.4152 | 122.4106 | 84.1415 | 122.4747 | 122.3969 | 122.4106 | 122.4152 | 122.4152 | -122.6852 | -38.2095
3597.7656 | 122.6624 | -75.3799 | 46.9162 | 0.2935 | 0.016992 | 0.011301 | 0.0062656 | -0.011031 | -0.0052231 | -0.0015894 | 47.0123 | 47.0398 | -75.7599 | 47.1405 | 46.9986 | 47.0169 | 46.5179 | 47.1405 | 47.0261 | 8.4686 | -0.37994 | 0.1236 | 122.3923 | 122.5204 | 0.082397 | 83.8486 | 0.10986 | 122.7722 | 121.8979 | 122.5204 | 122.3785 | 122.4197 | 122.3923 | 122.406 | 122.3969 | 83.8486 | 122.4197 | 122.3923 | 122.3969 | 122.3785 | 122.406 | -122.6761 | -38.4476
3598.7656 | 122.6395 | -75.3021 | 46.9894 | 0.27824 | 0.013146 | 0.012369 | 0.011392 | -0.0071863 | -0.0056503 | -0.0043664 | 46.9116 | 47.0947 | -75.6958 | 47.2504 | 47.0489 | 47.0993 | 46.6141 | 47.2 | 47.1039 | 8.4778 | -0.39368 | 0.10529 | 122.2137 | 122.5525 | 0.059509 | 83.7799 | 0.11444 | 122.6074 | 121.9162 | 122.5021 | 122.3511 | 122.3969 | 122.2137 | 122.406 | 122.4014 | 83.7799 | 122.3969 | 122.2137 | 122.4014 | 122.3511 | 122.406 | -122.6852 | -38.5117
3599.7656 | 122.525 | -75.1923 | 47.2 | 0.44609 | 0.01806 | 0.011301 | 0.012888 | -0.0067591 | -0.0058639 | -0.0058618 | 47.2046 | 47.4197 | -75.4944 | 47.3053 | 47.1085 | 47.1497 | 46.9437 | 47.2458 | 47.3236 | 8.4641 | -0.30212 | 0.21973 | 122.3969 | 122.4976 | -0.091553 | 83.6563 | 0.1236 | 122.699 | 122.1359 | 122.4381 | 122.3007 | 122.612 | 122.3969 | 122.5159 | 122.3419 | 83.6563 | 122.612 | 122.3969 | 122.3419 | 122.3007 | 122.5159 | -122.6944 | -38.736
3600.7656 | 122.5388 | -75.1602 | 47.2092 | 0.59105 | 0.016778 | 0.0085235 | 0.013956 | -0.0078271 | -0.0062911 | -0.0022302 | 47.2229 | 47.3785 | -75.5127 | 47.3099 | 47.1405 | 47.1451 | 46.9666 | 47.2641 | 47.3373 | 8.4686 | -0.35248 | 0.16937 | 122.3831 | 122.4701 | -0.068664 | 83.6288 | 0.12817 | 122.7356 | 122.1268 | 122.4243 | 122.3007 | 122.5388 | 122.3831 | 122.4976 | 122.3053 | 83.6288 | 122.5388 | 122.3831 | 122.3053 | 122.3007 | 122.4976 | -122.7219 | -38.7405
3601.7656 | 122.6028 | -75.0092 | 47.3557 | 0.27824 | 0.018273 | 0.01066 | 0.010752 | -0.0065455 | -0.0047957 | -0.0043664 | 47.3511 | 47.4838 | -75.3937 | 47.4976 | 47.3282 | 47.3511 | 47.0261 | 47.4609 | 47.4564 | 8.4732 | -0.38452 | 0.12817 | 122.3602 | 122.5067 | -0.027466 | 83.4824 | 0.10071 | 122.7448 | 122.0352 | 122.4701 | 122.3373 | 122.493 | 122.3602 | 122.4655 | 122.3602 | 83.4824 | 122.493 | 122.3602 | 122.3602 | 122.3373 | 122.4655 | -122.7493 | -38.8824
3602.7812 | 122.6303 | -74.8764 | 47.4152 | 0.27824 | 0.014855 | 0.0098053 | 0.0092562 | -0.0065455 | -0.0050095 | -0.0030848 | 47.5479 | 47.5662 | -75.2289 | 47.7036 | 47.5296 | 47.5525 | 47.0993 | 47.6578 | 47.5616 | 8.4778 | -0.35248 | 0.15106 | 122.4243 | 122.58 | 0.11444 | 83.3542 | 0.14649 | 122.7768 | 121.9757 | 122.5342 | 122.406 | 122.4426 | 122.4243 | 122.4381 | 122.4289 | 83.3542 | 122.4426 | 122.4243 | 122.4289 | 122.406 | 122.4381 | -122.644 | -38.9374
3603.7656 | 122.6028 | -74.9084 | 47.4243 | 0.21721 | 0.014428 | 0.011728 | 0.0077608 | -0.010604 | -0.0047957 | -0.0015894 | 47.4518 | 47.5113 | -75.2975 | 47.6166 | 47.4472 | 47.4792 | 47.0901 | 47.5937 | 47.525 | 8.4778 | -0.3891 | 0.086976 | 122.3602 | 122.525 | 0.022889 | 83.3862 | 0.10071 | 122.7493 | 121.9986 | 122.5021 | 122.3557 | 122.4197 | 122.3602 | 122.4335 | 122.3877 | 83.3862 | 122.4197 | 122.3602 | 122.3877 | 122.3557 | 122.4335 | -122.7219 | -38.9465
3604.7656 | 122.6166 | -74.6796 | 47.6669 | 0.17906 | 0.01336 | 0.0070283 | 0.0086154 | -0.0095361 | -0.0052231 | -0.0032984 | 47.7036 | 47.7356 | -75.0229 | 47.8729 | 47.6852 | 47.7127 | 47.3557 | 47.8409 | 47.7905 | 8.4732 | -0.34332 | 0.068665 | 122.3831 | 122.5525 | 0.018311 | 83.1528 | 0.1236 | 122.7264 | 122.0352 | 122.5204 | 122.3648 | 122.4152 | 122.3831 | 122.4701 | 122.3923 | 83.1528 | 122.4152 | 122.3831 | 122.3923 | 122.3648 | 122.4701 | -122.6898 | -39.1937
3605.7656 | 122.6532 | -74.4095 | 47.9187 | 0.22484 | 0.013574 | 0.012582 | 0.0081882 | -0.0084681 | -0.0058639 | -0.001803 | 48.2162 | 48.1979 | -74.5422 | 48.1522 | 47.9462 | 47.9874 | 47.6028 | 48.0698 | 48.0606 | 8.4732 | -0.13275 | 0.27924 | 122.6257 | 122.5616 | 0.027466 | 82.8827 | 0.14191 | 122.7585 | 122.0123 | 122.4792 | 122.3557 | 122.6074 | 122.6257 | 122.4701 | 122.3969 | 82.8827 | 122.6074 | 122.6257 | 122.3969 | 122.3557 | 122.4701 | -122.4609 | -39.4455
3606.7656 | 122.6486 | -74.3271 | 48.024 | 0.27061 | 0.014642 | 0.0063873 | 0.012888 | -0.0097497 | -0.0054367 | -0.0032984 | 48.0515 | 48.1247 | -74.7162 | 48.2162 | 48.0103 | 48.0377 | 47.699 | 48.1522 | 48.111 | 8.4686 | -0.3891 | 0.10071 | 122.3785 | 122.5433 | -0.013733 | 82.7957 | 0.086975 | 122.7676 | 122.0261 | 122.4792 | 122.3373 | 122.4518 | 122.3785 | 122.438 | 122.3648 | 82.7957 | 122.4518 | 122.3785 | 122.3648 | 122.3373 | 122.438 | -122.7402 | -39.5554
3607.7656 | 122.6395 | -74.3134 | 48.0286 | 0.25536 | 0.01571 | 0.011301 | 0.012461 | -0.0097497 | -0.0043685 | -0.0020166 | 48.0652 | 48.1384 | -74.7162 | 48.2162 | 48.024 | 48.056 | 47.7127 | 48.1842 | 48.1064 | 8.4732 | -0.40283 | 0.10986 | 122.3785 | 122.5296 | -0.004577 | 82.7866 | 0.07782 | 122.7814 | 122.0261 | 122.4976 | 122.3373 | 122.4518 | 122.3785 | 122.4197 | 122.3694 | 82.7866 | 122.4518 | 122.3785 | 122.3694 | 122.3373 | 122.4197 | -122.7448 | -39.5554
3608.7656 | 122.6807 | -74.1348 | 48.2117 | 0.26299 | 0.015283 | 0.0083099 | 0.010111 | -0.0088953 | -0.0045821 | -0.003512 | 48.2895 | 48.2941 | -74.501 | 48.262 | 48.175 | 48.3444 | 47.9279 | 48.4314 | 48.2849 | 8.4686 | -0.36621 | 0.082397 | 122.4243 | 122.3969 | -0.036621 | 82.6035 | 0.073242 | 122.7905 | 122.0627 | 122.5662 | 122.3099 | 122.4289 | 122.4243 | 122.4197 | 122.4792 | 82.6035 | 122.4289 | 122.4243 | 122.4792 | 122.3099 | 122.4197 | -122.7127 | -39.743
3609.7812 | 122.6486 | -73.9883 | 48.3444 | 0.20958 | 0.013574 | 0.010873 | 0.0094698 | -0.010177 | -0.0037277 | -0.0022302 | 48.4131 | 48.4314 | -74.35 | 48.5916 | 48.4039 | 48.4177 | 48.0331 | 48.5458 | 48.4634 | 8.4732 | -0.36163 | 0.086975 | 122.4014 | 122.58 | 0.05951 | 82.4615 | 0.11902 | 122.7631 | 122.0215 | 122.5342 | 122.3923 | 122.4197 | 122.4014 | 122.4518 | 122.406 | 82.4615 | 122.4197 | 122.4014 | 122.406 | 122.3923 | 122.4518 | -122.6944 | -39.8712
3610.7656 | 122.6349 | -73.6267 | 48.7335 | 0.20195 | 0.013787 | 0.0025421 | 0.0047702 | -0.010818 | -0.0047957 | -0.0020166 | 48.7335 | 48.8159 | -74.0204 | 48.9258 | 48.7473 | 48.793 | 48.5046 | 48.8571 | 48.8297 | 8.4732 | -0.39368 | 0.082397 | 122.3602 | 122.5525 | 0.013732 | 82.0999 | 0.09613 | 122.7539 | 122.1313 | 122.4838 | 122.374 | 122.4426 | 122.3602 | 122.4564 | 122.4197 | 82.0999 | 122.4426 | 122.3602 | 122.4197 | 122.374 | 122.4564 | -122.7539 | -40.2603
3611.7656 | 122.644 | -73.6084 | 48.7747 | 0.11803 | 0.01336 | 0.0057465 | 0.0096834 | -0.0086817 | -0.0047957 | -0.0028712 | 48.7747 | 48.8525 | -73.9746 | 48.9807 | 48.7793 | 48.7839 | 48.7381 | 48.9166 | 48.8892 | 8.4686 | -0.36621 | 0.07782 | 122.3831 | 122.5891 | 0.004578 | 82.077 | 0.11444 | 122.7493 | 122.3465 | 122.525 | 122.3877 | 122.4609 | 122.3831 | 122.4976 | 122.3923 | 82.077 | 122.4609 | 122.3831 | 122.3923 | 122.3877 | 122.4976 | -122.7493 | -40.3061
3612.7656 | 122.6532 | -73.7183 | 48.6969 | 0.10277 | 0.012292 | 0.0036103 | 0.008829 | -0.010604 | -0.0069321 | -0.0030848 | 48.6923 | 48.7839 | -74.0479 | 48.8892 | 48.6832 | 48.6877 | 48.4955 | 48.8022 | 48.7701 | 8.4686 | -0.32959 | 0.086976 | 122.4106 | 122.6074 | -0.013732 | 82.1869 | 0.073243 | 122.7402 | 122.2137 | 122.5204 | 122.4014 | 122.5021 | 122.4106 | 122.4884 | 122.406 | 82.1869 | 122.5021 | 122.4106 | 122.406 | 122.4014 | 122.4884 | -122.7448 | -40.2283
3613.7656 | 122.6761 | -73.5672 | 48.7976 | 0.25536 | 0.014214 | 0.0033967 | 0.013742 | -0.011031 | -0.0067185 | 0.00097421 | 48.8708 | 48.8525 | -73.9609 | 48.8617 | 48.7976 | 48.9258 | 48.5275 | 49.0128 | 48.8525 | 8.4686 | -0.39368 | 0.054932 | 122.4381 | 122.4289 | 0 | 82.0358 | 0.054932 | 122.8317 | 122.0947 | 122.58 | 122.3648 | 122.4197 | 122.4381 | 122.4197 | 122.493 | 82.0358 | 122.4197 | 122.4381 | 122.493 | 122.3648 | 122.4197 | -122.7585 | -40.329
3614.7656 | 122.6898 | -73.2605 | 49.1226 | 0.20195 | 0.013574 | 0.010019 | 0.010324 | -0.0093225 | -0.0065047 | -0.0037256 | 49.1684 | 49.2004 | -73.6176 | 49.3561 | 49.1547 | 49.1638 | 48.8022 | 49.3057 | 49.1684 | 8.4732 | -0.35706 | 0.077819 | 122.4289 | 122.6166 | 0.032043 | 81.7337 | 0.045776 | 122.7859 | 122.0627 | 122.5662 | 122.4152 | 122.4609 | 122.4289 | 122.4289 | 122.4243 | 81.7337 | 122.4609 | 122.4289 | 122.4243 | 122.4152 | 122.4289 | -122.7402 | -40.6494
3615.7656 | 122.6807 | -72.3358 | 50.0839 | 0.21721 | 0.012933 | 0.01066 | 0.011392 | -0.0099633 | -0.0050095 | -0.0024438 | 50.1434 | 50.1709 | -72.6608 | 50.2945 | 50.0748 | 50.0931 | 49.7406 | 50.2258 | 50.1022 | 8.4778 | -0.32501 | 0.086975 | 122.4792 | 122.6303 | -0.009155 | 80.8136 | 0.018311 | 122.8043 | 122.0764 | 122.5616 | 122.4106 | 122.5067 | 122.4792 | 122.438 | 122.4289 | 80.8136 | 122.5067 | 122.4792 | 122.4289 | 122.4106 | 122.438 | -122.7448 | -41.6061
3616.7812 | 122.6578 | -72.7936 | 49.6033 | 0.15617 | 0.01571 | 0.0095917 | 0.008829 | -0.0095361 | -0.0062911 | -0.0020166 | 49.8505 | 50.1251 | -72.8256 | 49.8138 | 49.6262 | 49.6582 | 49.3607 | 49.7543 | 49.6857 | 8.4641 | -0.032044 | 0.52185 | 122.644 | 122.6074 | 0.022889 | 81.2576 | 0.082398 | 122.6761 | 122.1542 | 122.5479 | 122.4197 | 122.9187 | 122.644 | 122.4792 | 122.4518 | 81.2576 | 122.9187 | 122.644 | 122.4518 | 122.4197 | 122.4792 | -122.4289 | -41.1392
3617.7656 | 122.6944 | -72.9767 | 49.4431 | 0.056992 | 0.014214 | 0.0042511 | 0.0073336 | -0.011886 | -0.0056503 | -0.001803 | 49.3881 | 49.4751 | -73.3704 | 49.6262 | 49.4339 | 49.4568 | 49.1592 | 49.6078 | 49.5117 | 8.4778 | -0.39368 | 0.032044 | 122.3648 | 122.6028 | -0.009155 | 81.4545 | 0.068665 | 122.7585 | 122.1359 | 122.5845 | 122.4106 | 122.4518 | 122.3648 | 122.4884 | 122.4335 | 81.4545 | 122.4518 | 122.3648 | 122.4335 | 122.4106 | 122.4884 | -122.8134 | -40.9653
3618.7656 | 122.6715 | -72.7798 | 49.6536 | 0.07988 | 0.012078 | 0.0066009 | 0.0084018 | -0.013381 | -0.0054367 | -0.0022302 | 49.4751 | 49.53 | -73.3109 | 49.6811 | 49.4797 | 49.498 | 49.4431 | 50.0336 | 49.6948 | 8.4824 | -0.53101 | -0.1236 | 122.2549 | 122.4609 | -0.17395 | 81.2622 | 0.041199 | 122.7859 | 122.2229 | 122.8134 | 122.2595 | 122.3099 | 122.2549 | 122.4747 | 122.2778 | 81.2622 | 122.3099 | 122.2549 | 122.2778 | 122.2595 | 122.4747 | -122.9645 | -41.1713
3619.7656 | 122.699 | -68.2617 | 54.1718 | 0.011215 | 0.013146 | 0.0055329 | 0.0064792 | -0.0121 | -0.0054367 | -0.0028712 | 54.1718 | 54.2542 | -68.6188 | 54.3915 | 54.1901 | 54.1901 | 54.0619 | 54.3274 | 54.2542 | 8.4732 | -0.35706 | 0.082397 | 122.4335 | 122.6532 | 0.01831 | 76.7349 | 0.082397 | 122.7905 | 122.3236 | 122.5891 | 122.4518 | 122.5159 | 122.4335 | 122.5159 | 122.4518 | 76.7349 | 122.5159 | 122.4335 | 122.4518 | 122.4518 | 122.5159 | -122.7905 | -45.6985
3620.7656 | 122.7264 | -73.0957 | 49.292 | 0.22484 | 0.012719 | 0.0033967 | 0.011179 | -0.010391 | -0.0058639 | -0.0026574 | 49.3607 | 49.3378 | -73.4665 | 49.5438 | 49.3332 | 49.3515 | 48.9304 | 49.4751 | 49.3652 | 8.4824 | -0.37079 | 0.045777 | 122.4564 | 122.6395 | 0.041199 | 81.5781 | 0.073242 | 122.8271 | 122.0261 | 122.5708 | 122.4289 | 122.4335 | 122.4564 | 122.4609 | 122.4472 | 81.5781 | 122.4335 | 122.4564 | 122.4472 | 122.4289 | 122.4609 | -122.7585 | -40.8096
3621.7656 | 122.6715 | -72.9584 | 49.4843 | 0.17906 | 0.014001 | 0.0074555 | 0.0077608 | -0.011672 | -0.0060775 | -0.0026574 | 49.4797 | 49.5071 | -73.3017 | 49.6765 | 49.4797 | 49.4888 | 49.1592 | 49.6124 | 49.5071 | 8.4778 | -0.34332 | 0.022888 | 122.438 | 122.6349 | -0.004578 | 81.4362 | 0.022888 | 122.7814 | 122.1176 | 122.5708 | 122.438 | 122.4655 | 122.438 | 122.4655 | 122.4472 | 81.4362 | 122.4655 | 122.438 | 122.4472 | 122.438 | 122.4655 | -122.786 | -41.0065
3622.7656 | 122.6898 | -72.8119 | 49.617 | 0.18669 | 0.012719 | 0.0068147 | 0.0092562 | -0.0099633 | -0.0039413 | -0.0037256 | 49.6536 | 49.6811 | -73.1644 | 49.8413 | 49.6445 | 49.6399 | 49.3195 | 49.7726 | 49.7086 | 8.4778 | -0.35248 | 0.064087 | 122.4655 | 122.6532 | 0.027466 | 81.2897 | 0.091553 | 122.818 | 122.1313 | 122.5845 | 122.4564 | 122.493 | 122.4655 | 122.5204 | 122.4518 | 81.2897 | 122.493 | 122.4655 | 122.4518 | 122.4564 | 122.5204 | -122.7814 | -41.1392
3623.7812 | 122.6807 | -69.6762 | 52.7802 | 0.095139 | 0.012292 | 0.0038239 | 0.00712 | -0.0099633 | -0.0045821 | -0.0022302 | 52.7527 | 52.8305 | -70.0287 | 53.1418 | 52.8351 | 52.7664 | 52.6108 | 52.8717 | 52.8397 | 8.4778 | -0.35248 | 0.050354 | 122.4289 | 122.818 | 0.054932 | 78.154 | 0.05951 | 122.7814 | 122.287 | 122.5479 | 122.5113 | 122.5067 | 122.4289 | 122.5159 | 122.4426 | 78.154 | 122.5067 | 122.4289 | 122.4426 | 122.5113 | 122.5159 | -122.8088 | -44.3024
3624.7656 | 122.7493 | -72.052 | 50.3311 | -0.011673 | 0.012505 | 0.0066009 | 0.0058382 | -0.011031 | -0.0084273 | -0.0030848 | 50.3998 | 50.4456 | -72.4365 | 50.647 | 50.4501 | 50.4456 | 50.0931 | 50.5692 | 50.4318 | 8.4732 | -0.38452 | 0.11444 | 122.4518 | 122.699 | 0.11902 | 80.5252 | 0.10071 | 122.8363 | 122.1451 | 122.6212 | 122.5021 | 122.4976 | 122.4518 | 122.4838 | 122.4976 | 80.5252 | 122.4976 | 122.4518 | 122.4976 | 122.5021 | 122.4838 | -122.7676 | -41.8579
3625.7656 | 122.7585 | -69.5251 | 52.9129 | -0.011673 | 0.0093012 | 0.0057465 | 0.0047702 | -0.0099633 | -0.0056503 | -0.0030848 | 52.9495 | 52.9678 | -69.841 | 53.1784 | 52.977 | 52.9678 | 52.7481 | 53.1418 | 53.0273 | 8.4824 | -0.31586 | 0.054931 | 122.4747 | 122.7036 | 0.064087 | 78.0075 | 0.11444 | 122.7905 | 122.2733 | 122.6669 | 122.5021 | 122.493 | 122.4747 | 122.5525 | 122.493 | 78.0075 | 122.493 | 122.4747 | 122.493 | 122.5021 | 122.5525 | -122.7539 | -44.4305
3626.7656 | 122.7036 | -72.258 | 50.1892 | 0.20195 | 0.012933 | 0.0083099 | 0.0096834 | -0.0088953 | -0.0058639 | -0.0032984 | 50.2029 | 50.2167 | -72.6242 | 50.3952 | 50.1801 | 50.1938 | 49.9008 | 50.3403 | 50.267 | 8.4732 | -0.36621 | 0.027466 | 122.4609 | 122.6532 | -0.009155 | 80.7312 | 0.07782 | 122.8271 | 122.1588 | 122.5983 | 122.4381 | 122.4747 | 122.4609 | 122.525 | 122.4518 | 80.7312 | 122.4747 | 122.4609 | 122.4518 | 122.4381 | 122.525 | -122.8134 | -41.716
3627.7656 | 122.7173 | -72.1939 | 50.2441 | 0.19432 | 0.011865 | 0.0085235 | 0.0081882 | -0.010177 | -0.0058639 | -0.0037256 | 50.1984 | 50.2533 | -72.5967 | 50.4318 | 50.2487 | 50.2625 | 49.9786 | 50.4089 | 50.2853 | 8.4824 | -0.40283 | 0.009155 | 122.3923 | 122.6257 | 0.004577 | 80.6763 | 0.041198 | 122.7951 | 122.1725 | 122.6028 | 122.4426 | 122.4472 | 122.3923 | 122.4792 | 122.4564 | 80.6763 | 122.4472 | 122.3923 | 122.4564 | 122.4426 | 122.4792 | -122.8409 | -41.7618
3628.7656 | 122.6852 | -72.3541 | 50.0793 | 0.049362 | 0.013146 | 0.0095917 | 0.0064792 | -0.0097497 | -0.0058639 | -0.0026574 | 50.0702 | 50.1343 | -72.7432 | 50.2579 | 50.0519 | 50.1068 | 49.8001 | 50.235 | 50.1617 | 8.4732 | -0.3891 | 0.054931 | 122.4243 | 122.612 | -0.027466 | 80.8273 | 0.082397 | 122.8134 | 122.1542 | 122.5891 | 122.406 | 122.4884 | 122.4243 | 122.5159 | 122.4609 | 80.8273 | 122.4884 | 122.4243 | 122.4609 | 122.406 | 122.5159 | -122.8226 | -41.6061
3629.7656 | 122.7081 | -69.8502 | 52.6062 | 0.087509 | 0.012292 | 0.0098053 | 0.0084018 | -0.0121 | -0.0075729 | -0.0020166 | 52.5696 | 52.6794 | -70.2072 | 52.8259 | 52.6474 | 52.6382 | 52.4551 | 52.7435 | 52.6794 | 8.4732 | -0.35705 | 0.073242 | 122.4197 | 122.6761 | 0.041199 | 78.3234 | 0.073242 | 122.7768 | 122.3053 | 122.5937 | 122.4976 | 122.5296 | 122.4197 | 122.5296 | 122.4884 | 78.3234 | 122.5296 | 122.4197 | 122.4884 | 122.4976 | 122.5296 | -122.8134 | -44.133
3630.7812 | 122.7585 | -69.4199 | 53.0136 | 0.026474 | 0.012292 | 0.0042511 | 0.0058382 | -0.010177 | -0.0058639 | -0.003512 | 53.0319 | 53.0685 | -69.7495 | 53.2837 | 53.0685 | 53.0823 | 52.8625 | 53.2196 | 53.1006 | 8.4778 | -0.32959 | 0.054931 | 122.4518 | 122.7036 | 0.054931 | 77.8976 | 0.086975 | 122.7814 | 122.2824 | 122.6395 | 122.4884 | 122.4884 | 122.4518 | 122.5204 | 122.5021 | 77.8976 | 122.4884 | 122.4518 | 122.5021 | 122.4884 | 122.5204 | -122.7631 | -44.5358
3631.7656 | 122.7539 | -69.0765 | 53.4027 | -0.10323 | 0.01336 | 0.0040375 | 0.0064792 | -0.0086817 | -0.0069321 | 0.0011878 | 53.4439 | 53.421 | -69.4153 | 53.5858 | 53.4119 | 53.5034 | 53.1784 | 53.5995 | 53.4393 | 8.4824 | -0.33875 | 0.018311 | 122.5204 | 122.6624 | 0.009155 | 77.5589 | 0.036621 | 122.8592 | 122.2549 | 122.6761 | 122.4884 | 122.4976 | 122.5204 | 122.5159 | 122.58 | 77.5589 | 122.4976 | 122.5204 | 122.58 | 122.4884 | 122.5159 | -122.818 | -44.9203
3632.7656 | 122.7676 | -68.9667 | 53.4851 | -0.11848 | 0.012719 | 0.0044647 | 0.010965 | -0.0095361 | -0.0080001 | -0.0024438 | 53.5446 | 53.5217 | -69.31 | 53.7506 | 53.5538 | 53.5583 | 53.2791 | 53.6911 | 53.5309 | 8.4778 | -0.34332 | 0.036622 | 122.5113 | 122.7173 | 0.068665 | 77.4445 | 0.045777 | 122.8546 | 122.2458 | 122.6578 | 122.5204 | 122.4884 | 122.5113 | 122.4976 | 122.525 | 77.4445 | 122.4884 | 122.5113 | 122.525 | 122.5204 | 122.4976 | -122.7951 | -45.0073
3633.7656 | 122.7036 | -69.6579 | 52.8076 | -1.4307 | 0.012933 | 0.011087 | 0.0069064 | -0.010177 | -0.0075729 | -0.0020166 | 52.7618 | 52.8534 | -69.9966 | 53.0228 | 52.7985 | 52.8076 | 52.6611 | 52.9633 | 52.9083 | 8.4824 | -0.33875 | 0.045777 | 122.4197 | 122.6807 | -0.009155 | 78.1403 | 0.10071 | 122.7585 | 122.319 | 122.6212 | 122.4564 | 122.5113 | 122.4197 | 122.5662 | 122.4655 | 78.1403 | 122.5113 | 122.4197 | 122.4655 | 122.4564 | 122.5662 | -122.8043 | -44.3253
3634.7656 | 122.7173 | -69.4656 | 53.0273 | 0.78178 | 0.010156 | 0.0042511 | 0.0077608 | -0.0097497 | -0.0077865 | -0.0030848 | 53.0182 | 53.0731 | -69.841 | 53.2104 | 53.0182 | 53.009 | 52.8671 | 53.1647 | 53.0731 | 8.4824 | -0.37537 | 0.045776 | 122.4838 | 122.6761 | -0.009156 | 77.948 | 0.045776 | 122.8592 | 122.3328 | 122.6303 | 122.4838 | 122.5388 | 122.4838 | 122.5388 | 122.4747 | 77.948 | 122.5388 | 122.4838 | 122.4747 | 122.4838 | 122.5388 | -122.8683 | -44.545
3635.7812 | 122.7081 | -72.3312 | 50.1709 | -0.17189 | 0.012933 | 0.0068147 | 0.010538 | -0.013809 | -0.0060775 | -0.0022302 | 50.1846 | 50.2304 | -72.6883 | 50.3448 | 50.148 | 50.116 | 49.9466 | 50.2853 | 50.235 | 8.4778 | -0.35706 | 0.05951 | 122.5159 | 122.6761 | -0.022888 | 80.809 | 0.064087 | 122.8729 | 122.2778 | 122.6166 | 122.4792 | 122.5616 | 122.5159 | 122.5662 | 122.4472 | 80.809 | 122.5616 | 122.5159 | 122.4472 | 122.4792 | 122.5662 | -122.8592 | -41.6931
3636.7656 | 122.7768 | -72.2443 | 50.2121 | -0.011673 | 0.014001 | 0.0042511 | 0.0084018 | -0.0097497 | -0.0073593 | -0.0028712 | 50.2441 | 50.2853 | -72.6334 | 50.4639 | 50.2853 | 50.2899 | 49.9283 | 50.4272 | 50.2899 | 8.4732 | -0.3891 | 0.073242 | 122.4884 | 122.7081 | 0.073242 | 80.7175 | 0.07782 | 122.8775 | 122.1725 | 122.6715 | 122.5296 | 122.5296 | 122.4884 | 122.5342 | 122.5342 | 80.7175 | 122.5296 | 122.4884 | 122.5342 | 122.5296 | 122.5342 | -122.8455 | -41.7389
3637.7812 | 122.7676 | -69.5847 | 52.8854 | -0.065079 | 0.012933 | 0.010019 | 0.0077608 | -0.011031 | -0.0080001 | -0.0020166 | 52.9358 | 52.8809 | -69.96 | 53.1509 | 52.9404 | 52.9587 | 52.684 | 53.1052 | 52.9449 | 8.4824 | -0.37537 | -0.004578 | 122.5204 | 122.7356 | 0.054932 | 78.067 | 0.059509 | 122.8958 | 122.2687 | 122.6898 | 122.525 | 122.4655 | 122.5204 | 122.5296 | 122.5433 | 78.067 | 122.4655 | 122.5204 | 122.5433 | 122.525 | 122.5296 | -122.8455 | -44.4031
3638.7656 | 122.6761 | -69.4839 | 53.0502 | -0.21004 | 0.011865 | 0.0055329 | 0.0096834 | -0.012313 | -0.0080001 | -0.0030848 | 53.0319 | 53.0823 | -69.8227 | 53.2288 | 53.0182 | 52.9953 | 52.9312 | 53.1647 | 53.0502 | 8.4778 | -0.33875 | 0.032043 | 122.5159 | 122.7127 | -0.032044 | 77.9617 | 0 | 122.8546 | 122.4152 | 122.6486 | 122.5021 | 122.5662 | 122.5159 | 122.5342 | 122.4792 | 77.9617 | 122.5662 | 122.5159 | 122.4792 | 122.5021 | 122.5342 | -122.8729 | -44.5724
3639.7656 | 122.6669 | -69.0903 | 53.421 | -0.19478 | 0.012933 | 0.0059601 | 0.0081882 | -0.012527 | -0.0065047 | -0.0028712 | 53.4164 | 53.4943 | -69.4611 | 53.6087 | 53.4119 | 53.3981 | 53.3661 | 53.54 | 53.5034 | 8.4824 | -0.37079 | 0.073242 | 122.5067 | 122.699 | -0.009156 | 77.5726 | 0.082397 | 122.8775 | 122.4564 | 122.6303 | 122.5021 | 122.5845 | 122.5067 | 122.5937 | 122.4884 | 77.5726 | 122.5845 | 122.5067 | 122.4884 | 122.5021 | 122.5937 | -122.8821 | -44.9387
3640.7812 | 122.6669 | -69.0491 | 53.4851 | 0.1104 | 0.017632 | 0.0068147 | 0.013742 | -0.0088953 | -0.0088547 | -0.00458 | 53.5172 | 53.6499 | -69.3695 | 53.6636 | 53.4302 | 53.4164 | 53.4393 | 53.54 | 53.5812 | 8.4778 | -0.32044 | 0.16479 | 122.5662 | 122.7127 | -0.054931 | 77.5269 | 0.096131 | 122.8867 | 122.4884 | 122.5891 | 122.4792 | 122.699 | 122.5662 | 122.6303 | 122.4655 | 77.5269 | 122.699 | 122.5662 | 122.4655 | 122.4792 | 122.6303 | -122.8546 | -45.0073
3641.7656 | 122.7997 | -69.1406 | 53.2928 | -0.0040434 | 0.012719 | 0.0044647 | 0.0069064 | -0.0097497 | -0.0062911 | -0.0030848 | 53.2928 | 53.3295 | -69.5755 | 53.5995 | 53.4348 | 53.421 | 53.1555 | 53.5858 | 53.4073 | 8.4824 | -0.43488 | 0.036621 | 122.4335 | 122.7402 | 0.14191 | 77.623 | 0.11444 | 122.8683 | 122.2961 | 122.7264 | 122.5754 | 122.4701 | 122.4335 | 122.5479 | 122.5616 | 77.623 | 122.4701 | 122.4335 | 122.5616 | 122.5754 | 122.5479 | -122.8683 | -44.8105
3642.7812 | 122.7448 | -69.278 | 53.2471 | -0.19478 | 0.013574 | 0.0038239 | 0.0090426 | -0.011459 | -0.0080001 | -0.0022302 | 53.2333 | 53.2837 | -69.6396 | 53.4439 | 53.2333 | 53.2333 | 53.1418 | 53.389 | 53.3112 | 8.4778 | -0.36163 | 0.036621 | 122.5113 | 122.7219 | -0.013733 | 77.7557 | 0.064087 | 122.8729 | 122.4197 | 122.6669 | 122.5113 | 122.5616 | 122.5113 | 122.5891 | 122.5113 | 77.7557 | 122.5616 | 122.5113 | 122.5113 | 122.5113 | 122.5891 | -122.8867 | -44.7693
3643.7656 | 122.7814 | -69.2825 | 53.2379 | 0.034104 | 0.011865 | 0.0027557 | 0.0079744 | -0.011031 | -0.0080001 | -0.0030848 | 53.2974 | 53.2837 | -69.6167 | 53.4805 | 53.2928 | 53.2745 | 53.1006 | 53.4485 | 53.2791 | 8.4824 | -0.33417 | 0.045776 | 122.58 | 122.7631 | 0.054932 | 77.7649 | 0.041199 | 122.9141 | 122.3831 | 122.731 | 122.5754 | 122.5662 | 122.58 | 122.5616 | 122.5571 | 77.7649 | 122.5662 | 122.58 | 122.5571 | 122.5754 | 122.5616 | -122.8546 | -44.7556
3644.7656 | 122.6898 | -69.8685 | 52.6749 | -0.23293 | 0.014428 | 0.0040375 | 0.011606 | -0.0084681 | -0.0088547 | -0.0047938 | 52.6474 | 52.771 | -70.2438 | 52.8259 | 52.6199 | 52.6062 | 52.6108 | 52.7527 | 52.7573 | 8.4778 | -0.37537 | 0.09613 | 122.5159 | 122.6944 | -0.054932 | 78.3463 | 0.082397 | 122.8912 | 122.4792 | 122.6212 | 122.4884 | 122.6395 | 122.5159 | 122.6257 | 122.4747 | 78.3463 | 122.6395 | 122.5159 | 122.4747 | 122.4884 | 122.6257 | -122.9187 | -44.1971
3645.7812 | 122.731 | -69.9875 | 52.5421 | -0.072708 | 0.016137 | 0.0059601 | 0.015451 | -0.0073999 | -0.0094955 | -0.0028712 | 52.6154 | 52.6932 | -70.3171 | 52.7573 | 52.5558 | 52.5421 | 52.4323 | 52.6932 | 52.6657 | 8.4824 | -0.32959 | 0.15106 | 122.6028 | 122.7448 | 0.013733 | 78.4698 | 0.1236 | 122.9324 | 122.4197 | 122.6807 | 122.5433 | 122.6807 | 122.6028 | 122.6532 | 122.5296 | 78.4698 | 122.6807 | 122.6028 | 122.5296 | 122.5433 | 122.6532 | -122.8592 | -44.0598
3646.7656 | 122.6898 | -69.8776 | 52.7115 | -0.12611 | 0.015496 | 0.0085235 | 0.010538 | -0.0084681 | -0.0077865 | -0.0043664 | 52.6428 | 52.7847 | -70.2164 | 52.8488 | 52.6428 | 52.6154 | 52.6291 | 52.7618 | 52.7939 | 8.4824 | -0.33875 | 0.073242 | 122.5204 | 122.7264 | -0.068665 | 78.36 | 0.082397 | 122.8592 | 122.5067 | 122.6395 | 122.5204 | 122.6624 | 122.5204 | 122.6715 | 122.493 | 78.36 | 122.6624 | 122.5204 | 122.493 | 122.5204 | 122.6715 | -122.9279 | -44.2291
3647.7656 | 122.7585 | -71.7728 | 50.7248 | -0.17189 | 0.013787 | 0.0085235 | 0.0077608 | -0.010177 | -0.0062911 | -0.0041528 | 50.7385 | 50.8163 | -72.139 | 50.9399 | 50.7706 | 50.7568 | 50.5234 | 50.9216 | 50.8072 | 8.4824 | -0.36621 | 0.091553 | 122.5113 | 122.7127 | 0.045777 | 80.2551 | 0.082398 | 122.8775 | 122.2961 | 122.6944 | 122.5433 | 122.5891 | 122.5113 | 122.58 | 122.5296 | 80.2551 | 122.5891 | 122.5113 | 122.5296 | 122.5433 | 122.58 | -122.8638 | -42.2424
3648.7656 | 122.7676 | -69.6579 | 52.8671 | -0.2253 | 0.012078 | 0.0066009 | 0.0084018 | -0.0088953 | -0.0080001 | -0.0043664 | 52.8854 | 52.9678 | -70.0104 | 53.0823 | 52.8992 | 52.8992 | 52.7847 | 53.0411 | 52.9633 | 8.4824 | -0.35248 | 0.10071 | 122.5433 | 122.7402 | 0.032044 | 78.1403 | 0.096131 | 122.8958 | 122.4426 | 122.699 | 122.5571 | 122.6257 | 122.5433 | 122.6212 | 122.5571 | 78.1403 | 122.6257 | 122.5433 | 122.5571 | 122.5571 | 122.6212 | -122.8775 | -44.3848
3649.7656 | 122.6852 | -71.9101 | 50.6836 | -0.20241 | 0.01101 | 0.0070283 | 0.0090426 | -0.0086817 | -0.0073593 | -0.003512 | 50.6287 | 50.7843 | -72.2534 | 50.8026 | 50.6195 | 50.5966 | 50.592 | 50.7385 | 50.7614 | 8.4824 | -0.34332 | 0.10071 | 122.5388 | 122.7127 | -0.064087 | 80.3925 | 0.07782 | 122.8821 | 122.5021 | 122.6486 | 122.5296 | 122.6944 | 122.5388 | 122.6715 | 122.5067 | 80.3925 | 122.6944 | 122.5388 | 122.5067 | 122.5296 | 122.6715 | -122.937 | -42.2012
3650.7656 | 122.8271 | -69.7403 | 52.7344 | 0.26299 | 0.01101 | 0.0061737 | 0.0094698 | -0.011245 | -0.0086411 | -0.0011622 | 52.8214 | 52.8259 | -70.0974 | 52.9999 | 52.8168 | 52.8488 | 52.5604 | 52.9587 | 52.8351 | 8.4778 | -0.35706 | 0.091553 | 122.5616 | 122.7402 | 0.082397 | 78.2181 | 0.10071 | 122.9187 | 122.3007 | 122.699 | 122.5571 | 122.5662 | 122.5616 | 122.5754 | 122.5891 | 78.2181 | 122.5662 | 122.5616 | 122.5891 | 122.5571 | 122.5754 | -122.8317 | -44.2566
3651.7656 | 122.7539 | -71.5942 | 50.9674 | -0.04219 | 0.016564 | 0.0059601 | 0.015024 | -0.0086817 | -0.0054367 | -0.0011622 | 51.0223 | 51.1139 | -71.9147 | 51.1688 | 50.9445 | 50.9399 | 50.8301 | 51.0498 | 51.0452 | 8.4686 | -0.32043 | 0.14648 | 122.6166 | 122.7631 | -0.022888 | 80.0629 | 0.07782 | 122.937 | 122.4243 | 122.644 | 122.5388 | 122.7081 | 122.6166 | 122.6395 | 122.5342 | 80.0629 | 122.7081 | 122.6166 | 122.5342 | 122.5388 | 122.6395 | -122.8821 | -42.4988
3652.7656 | 122.7676 | -71.0999 | 51.4801 | -0.019302 | 0.014855 | 0.0070283 | 0.012888 | -0.0080407 | -0.0084273 | -0.0020166 | 51.4893 | 51.5945 | -71.4615 | 51.6312 | 51.4847 | 51.3062 | 51.4206 | 51.59 | 51.5167 | 8.4732 | -0.36163 | 0.11444 | 122.5891 | 122.731 | 0.004577 | 79.5731 | 0.036621 | 122.9507 | 122.5204 | 122.6898 | 122.5845 | 122.6944 | 122.5891 | 122.6166 | 122.406 | 79.5731 | 122.6944 | 122.5891 | 122.406 | 122.5845 | 122.6166 | -122.9416 | -43.0069
3653.7656 | 122.7448 | -68.7286 | 53.8467 | -0.034561 | 0.01571 | 0.010019 | 0.012674 | -0.0056909 | -0.0060775 | -0.0024438 | 53.8559 | 53.9703 | -69.0628 | 53.8559 | 53.746 | 53.8193 | 53.746 | 53.9841 | 53.8696 | 8.4686 | -0.33417 | 0.1236 | 122.5845 | 122.5845 | -0.10071 | 77.1973 | 0.022888 | 122.9187 | 122.4747 | 122.7127 | 122.4747 | 122.699 | 122.5845 | 122.5983 | 122.5479 | 77.1973 | 122.699 | 122.5845 | 122.5479 | 122.4747 | 122.5983 | -122.9095 | -45.3781
3654.7812 | 122.731 | -68.8293 | 53.7277 | -0.149 | 0.01571 | 0.013864 | 0.0094698 | -0.010391 | -0.0062911 | -0.0037256 | 53.7827 | 53.9566 | -69.1086 | 53.9474 | 53.7369 | 53.7277 | 53.7598 | 53.8605 | 53.8513 | 8.4686 | -0.27924 | 0.22888 | 122.612 | 122.7768 | 0.009155 | 77.298 | 0.1236 | 122.8912 | 122.5891 | 122.6898 | 122.5662 | 122.7859 | 122.612 | 122.6807 | 122.5571 | 77.298 | 122.7859 | 122.612 | 122.5571 | 122.5662 | 122.6807 | -122.8363 | -45.2591
3655.7812 | 122.7448 | -68.5135 | 54.0802 | -0.16426 | 0.013574 | 0.0059601 | 0.011606 | -0.0080407 | -0.0067185 | -0.0020166 | 54.0665 | 54.2358 | -68.866 | 54.2496 | 54.0573 | 54.0344 | 54.0848 | 54.1946 | 54.1489 | 8.4686 | -0.35248 | 0.15564 | 122.58 | 122.7631 | -0.022888 | 76.9821 | 0.068665 | 122.9324 | 122.5983 | 122.7081 | 122.5708 | 122.7493 | 122.58 | 122.6624 | 122.5479 | 76.9821 | 122.7493 | 122.58 | 122.5479 | 122.5708 | 122.6624 | -122.9462 | -45.6116
3656.7656 | 122.7585 | -68.367 | 54.1718 | -0.12611 | 0.012505 | 0.0085235 | 0.0098972 | -0.0061181 | -0.0052231 | -0.00458 | 54.1855 | 54.3503 | -68.7241 | 54.3823 | 54.1855 | 54.1672 | 54.213 | 54.3045 | 54.3045 | 8.4732 | -0.35706 | 0.17853 | 122.5525 | 122.7493 | 0.013733 | 76.8402 | 0.13275 | 122.9095 | 122.58 | 122.6715 | 122.5525 | 122.7173 | 122.5525 | 122.6715 | 122.5342 | 76.8402 | 122.7173 | 122.5525 | 122.5342 | 122.5525 | 122.6715 | -122.8958 | -45.6985
3657.7656 | 122.7539 | -68.3029 | 54.245 | -0.14137 | 0.013146 | 0.010873 | 0.010538 | -0.0073999 | -0.0039413 | -0.0024438 | 54.2633 | 54.451 | -68.6691 | 54.451 | 54.2496 | 54.2267 | 54.2862 | 54.3869 | 54.3549 | 8.4732 | -0.36621 | 0.20599 | 122.5662 | 122.7539 | 0.004578 | 76.7761 | 0.10986 | 122.9324 | 122.5891 | 122.6898 | 122.5525 | 122.7539 | 122.5662 | 122.6578 | 122.5296 | 76.7761 | 122.7539 | 122.5662 | 122.5296 | 122.5525 | 122.6578 | -122.9141 | -45.7718
3658.7656 | 122.6807 | -68.3441 | 54.245 | 0.14092 | 0.018914 | 0.012369 | 0.010538 | -0.0071863 | -0.0054367 | -0.0026574 | 54.245 | 54.4373 | -68.6874 | 54.3915 | 54.1718 | 54.1946 | 54.2587 | 54.3137 | 54.3503 | 8.4686 | -0.34332 | 0.19226 | 122.5891 | 122.7356 | -0.073242 | 76.8127 | 0.10529 | 122.9324 | 122.6028 | 122.6578 | 122.5159 | 122.7814 | 122.5891 | 122.6944 | 122.5388 | 76.8127 | 122.7814 | 122.5891 | 122.5388 | 122.5159 | 122.6944 | -122.9324 | -45.7764
3659.7656 | 122.7219 | -68.3762 | 54.2267 | 0.049362 | 0.016351 | 0.0070283 | 0.012888 | -0.0091089 | -0.0043685 | -0.00458 | 54.2038 | 54.3961 | -68.7149 | 54.3411 | 54.1397 | 54.1534 | 54.2358 | 54.2816 | 54.3137 | 8.4641 | -0.33875 | 0.16937 | 122.58 | 122.7173 | -0.086976 | 76.8402 | 0.086975 | 122.9187 | 122.612 | 122.6578 | 122.5159 | 122.7722 | 122.58 | 122.6898 | 122.5296 | 76.8402 | 122.7722 | 122.58 | 122.5296 | 122.5159 | 122.6898 | -122.9416 | -45.7626
3660.7656 | 122.7264 | -68.3578 | 54.213 | 0.12566 | 0.017632 | 0.0085235 | 0.012033 | -0.0059045 | -0.0062911 | -0.0026574 | 54.1992 | 54.4052 | -68.7378 | 54.3274 | 54.1397 | 54.1397 | 54.2084 | 54.2404 | 54.3091 | 8.4732 | -0.37994 | 0.19226 | 122.5571 | 122.6852 | -0.073243 | 76.8311 | 0.09613 | 122.937 | 122.5662 | 122.5983 | 122.4976 | 122.7631 | 122.5571 | 122.6669 | 122.4976 | 76.8311 | 122.7631 | 122.5571 | 122.4976 | 122.4976 | 122.6669 | -122.9507 | -45.7397
3661.7656 | 122.7768 | -68.2617 | 54.3137 | -0.095596 | 0.015496 | 0.0078827 | 0.011179 | -0.0063317 | -0.0054367 | -0.0020166 | 54.3228 | 54.4968 | -68.6096 | 54.4876 | 54.3045 | 54.2862 | 54.3045 | 54.4418 | 54.3777 | 8.4686 | -0.3479 | 0.18311 | 122.5845 | 122.7493 | -0.009156 | 76.7303 | 0.064087 | 122.9324 | 122.5662 | 122.7036 | 122.5662 | 122.7585 | 122.5845 | 122.6395 | 122.5479 | 76.7303 | 122.7585 | 122.5845 | 122.5479 | 122.5662 | 122.6395 | -122.9233 | -45.845
3662.7656 | 122.7631 | -68.2938 | 54.2816 | -0.11085 | 0.018701 | 0.010232 | 0.0090426 | -0.0071863 | -0.0041549 | -0.003512 | 54.3137 | 54.4601 | -68.66 | 54.4693 | 54.277 | 54.2725 | 54.2862 | 54.4235 | 54.4006 | 8.4732 | -0.36621 | 0.17853 | 122.6074 | 122.7631 | -0.004577 | 76.767 | 0.11902 | 122.9736 | 122.58 | 122.7173 | 122.5708 | 122.7539 | 122.6074 | 122.6944 | 122.5662 | 76.767 | 122.7539 | 122.6074 | 122.5662 | 122.5708 | 122.6944 | -122.9416 | -45.8084
3663.7656 | 122.7676 | -68.2343 | 54.3137 | 0.026474 | 0.016137 | 0.0070283 | 0.012247 | -0.0082545 | -0.0045821 | -0.0026574 | 54.3777 | 54.5059 | -68.6005 | 54.5013 | 54.3045 | 54.2999 | 54.3365 | 54.4327 | 54.4098 | 8.4641 | -0.36621 | 0.19226 | 122.612 | 122.7356 | -0.009156 | 76.6983 | 0.09613 | 122.9782 | 122.5708 | 122.6669 | 122.5388 | 122.7402 | 122.612 | 122.644 | 122.5342 | 76.6983 | 122.7402 | 122.612 | 122.5342 | 122.5388 | 122.644 | -122.9141 | -45.8496
3664.7656 | 122.7493 | -68.3121 | 54.277 | -0.0040434 | 0.015069 | 0.0072419 | 0.010538 | -0.0078271 | -0.0067185 | -0.0028712 | 54.3228 | 54.5059 | -68.6234 | 54.4693 | 54.2816 | 54.2725 | 54.2953 | 54.4144 | 54.4098 | 8.4686 | -0.31128 | 0.22888 | 122.6349 | 122.7814 | 0.004577 | 76.7807 | 0.13275 | 122.9462 | 122.6074 | 122.7264 | 122.5937 | 122.818 | 122.6349 | 122.7219 | 122.5845 | 76.7807 | 122.818 | 122.6349 | 122.5845 | 122.5937 | 122.7219 | -122.9004 | -45.8084
3665.7656 | 122.7585 | -68.2251 | 54.3503 | 0.1638 | 0.016137 | 0.010873 | 0.0062656 | -0.0067591 | -0.0043685 | -0.0030848 | 54.3091 | 54.5242 | -68.6096 | 54.4693 | 54.2908 | 54.2862 | 54.3274 | 54.4006 | 54.4464 | 8.4732 | -0.38452 | 0.17395 | 122.5342 | 122.6944 | -0.05951 | 76.6983 | 0.09613 | 122.9187 | 122.5525 | 122.6257 | 122.5159 | 122.7493 | 122.5342 | 122.6715 | 122.5113 | 76.6983 | 122.7493 | 122.5342 | 122.5113 | 122.5159 | 122.6715 | -122.9599 | -45.8771
3666.7812 | 122.7493 | -68.1702 | 54.4373 | -0.66017 | 0.015496 | 0.0066009 | 0.0081882 | -0.0073999 | -0.0030869 | -0.001803 | 54.4144 | 54.6112 | -68.5364 | 54.57 | 54.3594 | 54.3503 | 54.4373 | 54.4785 | 54.5242 | 8.4732 | -0.36621 | 0.17395 | 122.5845 | 122.7402 | -0.07782 | 76.6434 | 0.086975 | 122.9507 | 122.6074 | 122.6486 | 122.5296 | 122.7814 | 122.5845 | 122.6944 | 122.5204 | 76.6434 | 122.7814 | 122.5845 | 122.5204 | 122.5296 | 122.6944 | -122.9736 | -45.9641
3667.7656 | 122.7539 | -68.1107 | 54.483 | 0.22484 | 0.015496 | 0.010873 | 0.0098972 | -0.0088953 | -0.0041549 | -0.003512 | 54.4464 | 54.6707 | -68.454 | 54.6249 | 54.4281 | 54.4418 | 54.4556 | 54.57 | 54.5334 | 8.4778 | -0.34332 | 0.18768 | 122.5571 | 122.7356 | -0.054931 | 76.5884 | 0.050354 | 122.9004 | 122.5662 | 122.6807 | 122.5388 | 122.7814 | 122.5571 | 122.644 | 122.5525 | 76.5884 | 122.7814 | 122.5571 | 122.5525 | 122.5388 | 122.644 | -122.937 | -46.0052
3668.7656 | 122.731 | -68.1335 | 54.4739 | 0.072251 | 0.017419 | 0.0042511 | 0.011392 | -0.0061181 | -0.0041549 | -0.00052119 | 54.4739 | 54.657 | -68.4677 | 54.6066 | 54.4052 | 54.4281 | 54.483 | 54.5654 | 54.5792 | 8.4641 | -0.33417 | 0.1831 | 122.6074 | 122.7402 | -0.068665 | 76.5976 | 0.10529 | 122.9416 | 122.6166 | 122.699 | 122.5388 | 122.7905 | 122.6074 | 122.7127 | 122.5616 | 76.5976 | 122.7905 | 122.6074 | 122.5616 | 122.5388 | 122.7127 | -122.9416 | -46.0098
3669.7656 | 122.7493 | -68.1244 | 54.5013 | 0.072251 | 0.014001 | 0.015146 | 0.012674 | -0.0076135 | -0.0043685 | -0.0022302 | 54.4968 | 54.689 | -68.4814 | 54.6158 | 54.4327 | 54.4235 | 54.4968 | 54.5517 | 54.6021 | 8.4641 | -0.35705 | 0.18768 | 122.6212 | 122.7402 | -0.068665 | 76.5884 | 0.10071 | 122.9782 | 122.6212 | 122.6761 | 122.5571 | 122.8134 | 122.6212 | 122.7264 | 122.5479 | 76.5884 | 122.8134 | 122.6212 | 122.5479 | 122.5571 | 122.7264 | -122.9828 | -46.0373
3670.7656 | 122.7173 | -68.0969 | 54.5059 | 0.1638 | 0.014214 | 0.010019 | 0.012674 | -0.0061181 | -0.0050095 | -0.0028712 | 54.451 | 54.6982 | -68.4769 | 54.5929 | 54.4006 | 54.4189 | 54.5288 | 54.5242 | 54.5883 | 8.4686 | -0.37994 | 0.19226 | 122.5479 | 122.6898 | -0.10529 | 76.5656 | 0.082398 | 122.9279 | 122.6257 | 122.6212 | 122.4976 | 122.7951 | 122.5479 | 122.6852 | 122.5159 | 76.5656 | 122.7951 | 122.5479 | 122.5159 | 122.4976 | 122.6852 | -122.9828 | -46.0373
3671.7656 | 122.8546 | -68.1473 | 54.4418 | 0.20195 | 0.017205 | 0.010232 | 0.011606 | -0.0063317 | -0.0050095 | -0.001803 | 54.4235 | 54.689 | -68.4814 | 54.5563 | 54.3823 | 54.3732 | 54.4922 | 54.5197 | 54.5883 | 8.4869 | -0.33417 | 0.24719 | 122.5708 | 122.7036 | -0.059509 | 76.6342 | 0.14648 | 122.905 | 122.6395 | 122.6669 | 122.5296 | 122.8363 | 122.5708 | 122.7356 | 122.5204 | 76.6342 | 122.8363 | 122.5708 | 122.5204 | 122.5296 | 122.7356 | -122.9233 | -45.9549
3672.7656 | 122.8821 | -68.0923 | 54.4785 | 0.19432 | 0.015923 | 0.010446 | 0.0069064 | -0.0080407 | -0.0043685 | -0.0032984 | 54.5242 | 54.6066 | -68.4586 | 54.6982 | 54.5059 | 54.5242 | 54.3137 | 54.6341 | 54.538 | 8.4824 | -0.36621 | 0.12817 | 122.6166 | 122.7905 | 0.027465 | 76.5747 | 0.059509 | 122.9828 | 122.406 | 122.7264 | 122.5983 | 122.699 | 122.6166 | 122.6303 | 122.6166 | 76.5747 | 122.699 | 122.6166 | 122.6166 | 122.5983 | 122.6303 | -122.937 | -45.9961
3673.7656 | 122.8775 | -68.0466 | 54.5197 | 0.27061 | 0.015283 | 0.011087 | 0.0084018 | -0.0073999 | -0.0056503 | -0.0011622 | 54.5837 | 54.6524 | -68.4036 | 54.7531 | 54.538 | 54.5837 | 54.3732 | 54.7028 | 54.5975 | 8.4778 | -0.35706 | 0.13275 | 122.6303 | 122.7997 | 0.018311 | 76.5244 | 0.07782 | 122.9874 | 122.4197 | 122.7493 | 122.5845 | 122.699 | 122.6303 | 122.644 | 122.6303 | 76.5244 | 122.699 | 122.6303 | 122.6303 | 122.5845 | 122.644 | -122.9233 | -46.0419
3674.7656 | 122.8775 | -68.0283 | 54.5334 | 0.27061 | 0.014642 | 0.010019 | 0.010538 | -0.0069727 | -0.0045821 | -0.00073479 | 54.6158 | 54.6433 | -68.3853 | 54.7577 | 54.5517 | 54.5929 | 54.3686 | 54.7073 | 54.6158 | 8.4778 | -0.35706 | 0.10986 | 122.644 | 122.7859 | 0.018311 | 76.506 | 0.082398 | 123.0011 | 122.3969 | 122.7356 | 122.58 | 122.6715 | 122.644 | 122.644 | 122.6212 | 76.506 | 122.6715 | 122.644 | 122.6212 | 122.58 | 122.644 | -122.9187 | -46.0556
3675.7656 | 122.7173 | -68.042 | 54.538 | 0.20958 | 0.016351 | 0.011087 | 0.010111 | -0.0071863 | -0.0047957 | -0.0020166 | 54.5471 | 54.7485 | -68.367 | 54.6982 | 54.4876 | 54.5059 | 54.5746 | 54.6204 | 54.689 | 8.4686 | -0.32501 | 0.21057 | 122.5891 | 122.7402 | -0.050354 | 76.5106 | 0.15106 | 122.9141 | 122.6166 | 122.6624 | 122.5296 | 122.7905 | 122.5891 | 122.731 | 122.5479 | 76.5106 | 122.7905 | 122.5891 | 122.5479 | 122.5296 | 122.731 | -122.905 | -46.0693
3676.7656 | 122.7585 | -68.0695 | 54.5517 | 0.23247 | 0.016351 | 0.010873 | 0.011606 | -0.0073999 | -0.0050095 | -0.0020166 | 54.5288 | 54.7348 | -68.4174 | 54.6844 | 54.4922 | 54.4922 | 54.5425 | 54.6204 | 54.6844 | 8.4732 | -0.3479 | 0.18311 | 122.5983 | 122.7539 | -0.05951 | 76.5427 | 0.13275 | 122.9462 | 122.612 | 122.6898 | 122.5616 | 122.8043 | 122.5983 | 122.7539 | 122.5616 | 76.5427 | 122.8043 | 122.5983 | 122.5616 | 122.5616 | 122.7539 | -122.9691 | -46.0785
3677.7656 | 122.7493 | -68.0695 | 54.5609 | 0.13329 | 0.015283 | 0.0048921 | 0.010111 | -0.0080407 | -0.0037277 | -0.0037256 | 54.5197 | 54.7165 | -68.4265 | 54.6753 | 54.4739 | 54.5013 | 54.5425 | 54.5929 | 54.6478 | 8.4778 | -0.35706 | 0.15564 | 122.5891 | 122.7448 | -0.086975 | 76.5472 | 0.086975 | 122.9462 | 122.612 | 122.6624 | 122.5433 | 122.7859 | 122.5891 | 122.7173 | 122.5708 | 76.5472 | 122.7859 | 122.5891 | 122.5708 | 122.5433 | 122.7173 | -122.9874 | -46.0831
3678.7812 | 122.8409 | -68.0099 | 54.5837 | 0.30113 | 0.016564 | 0.0089509 | 0.0094698 | -0.0078271 | -0.0056503 | -0.0022302 | 54.5883 | 54.7806 | -68.3716 | 54.7806 | 54.5609 | 54.5792 | 54.4922 | 54.7119 | 54.6844 | 8.4732 | -0.36163 | 0.19684 | 122.5983 | 122.7905 | -0.022888 | 76.4832 | 0.10071 | 122.9599 | 122.5021 | 122.7219 | 122.5708 | 122.7905 | 122.5983 | 122.6944 | 122.5891 | 76.4832 | 122.7905 | 122.5983 | 122.5891 | 122.5708 | 122.6944 | -122.9553 | -46.1105
3679.7656 | 122.8821 | -67.9962 | 54.5837 | 0.25536 | 0.013787 | 0.012582 | 0.0066928 | -0.0086817 | -0.0062911 | -0.001803 | 54.483 | 54.6707 | -68.3716 | 54.8309 | 54.6158 | 54.6661 | 54.4373 | 54.7623 | 54.6661 | 8.4732 | -0.37537 | 0.086975 | 122.4792 | 122.8271 | 0.032044 | 76.4694 | 0.082398 | 122.8546 | 122.4335 | 122.7585 | 122.612 | 122.6669 | 122.4792 | 122.6624 | 122.6624 | 76.4694 | 122.6669 | 122.4792 | 122.6624 | 122.612 | 122.6624 | -122.9553 | -46.1105
3680.7656 | 122.8912 | -67.9596 | 54.57 | 0.27824 | 0.015069 | 0.0095917 | 0.010324 | -0.0088953 | -0.0039413 | -0.0026574 | 54.6616 | 54.7073 | -68.3533 | 54.8996 | 54.6753 | 54.6616 | 54.4922 | 54.8126 | 54.6707 | 8.4732 | -0.39368 | 0.13733 | 122.6212 | 122.8592 | 0.10529 | 76.4328 | 0.10071 | 123.0148 | 122.4518 | 122.7722 | 122.6349 | 122.6669 | 122.6212 | 122.6303 | 122.6212 | 76.4328 | 122.6669 | 122.6212 | 122.6212 | 122.6349 | 122.6303 | -122.9233 | -46.0968
3681.7656 | 122.7722 | -67.9962 | 54.6387 | 0.20958 | 0.01806 | 0.0066009 | 0.013101 | -0.0088953 | -0.0062911 | 0.00033321 | 54.5563 | 54.7577 | -68.4082 | 54.4693 | 54.3411 | 54.7119 | 54.6341 | 54.7394 | 54.7165 | 8.4732 | -0.41199 | 0.11902 | 122.5525 | 122.4655 | -0.29755 | 76.4694 | 0.07782 | 122.9645 | 122.6303 | 122.7356 | 122.3373 | 122.7539 | 122.5525 | 122.7127 | 122.7081 | 76.4694 | 122.7539 | 122.5525 | 122.7081 | 122.3373 | 122.7127 | -123.0469 | -46.1655
3682.7656 | 122.8729 | -68.0374 | 54.5471 | 0.18669 | 0.01806 | 0.0091645 | 0.013315 | -0.0065455 | -0.0028731 | -0.0037256 | 54.5609 | 54.7806 | -68.4036 | 54.7119 | 54.5013 | 54.5013 | 54.5975 | 54.6204 | 54.6982 | 8.4824 | -0.36621 | 0.23346 | 122.5983 | 122.7493 | -0.045776 | 76.5198 | 0.15106 | 122.9645 | 122.6349 | 122.6578 | 122.5388 | 122.818 | 122.5983 | 122.7356 | 122.5388 | 76.5198 | 122.818 | 122.5983 | 122.5388 | 122.5388 | 122.7356 | -122.9507 | -46.0648
3683.7656 | 122.7768 | -68.0054 | 54.6158 | 0.21721 | 0.016351 | 0.011514 | 0.010111 | -0.0082545 | -0.0050095 | -0.001803 | 54.5883 | 54.7806 | -68.3716 | 54.7211 | 54.5197 | 54.5151 | 54.5975 | 54.6707 | 54.7073 | 8.4732 | -0.36621 | 0.1648 | 122.5937 | 122.7264 | -0.096131 | 76.4786 | 0.091552 | 122.9599 | 122.6028 | 122.6761 | 122.525 | 122.7859 | 122.5937 | 122.7127 | 122.5204 | 76.4786 | 122.7859 | 122.5937 | 122.5204 | 122.525 | 122.7127 | -122.9874 | -46.1426
3684.7656 | 122.7722 | -68.0237 | 54.6066 | 0.22484 | 0.015069 | 0.014719 | 0.011606 | -0.0091089 | -0.0056503 | -0.00052119 | 54.3457 | 54.7348 | -68.4036 | 54.7211 | 54.57 | 54.538 | 54.6204 | 54.6295 | 54.6936 | 8.4732 | -0.37994 | 0.12817 | 122.3694 | 122.7448 | -0.036621 | 76.4969 | 0.086976 | 122.7493 | 122.644 | 122.6532 | 122.5937 | 122.7585 | 122.3694 | 122.7173 | 122.5616 | 76.4969 | 122.7585 | 122.3694 | 122.5616 | 122.5937 | 122.7173 | -123.0103 | -46.1334
3685.7812 | 122.818 | -68.0374 | 54.5975 | 0.22484 | 0.012719 | 0.0072419 | 0.0098972 | -0.0099633 | -0.0062911 | -0.0026574 | 54.5471 | 54.7714 | -68.399 | 54.7256 | 54.5288 | 54.538 | 54.5517 | 54.657 | 54.689 | 8.4732 | -0.36163 | 0.17395 | 122.5845 | 122.7631 | -0.068664 | 76.5106 | 0.091553 | 122.9462 | 122.5891 | 122.6944 | 122.5662 | 122.8088 | 122.5845 | 122.7264 | 122.5754 | 76.5106 | 122.8088 | 122.5845 | 122.5754 | 122.5662 | 122.7264 | -122.9965 | -46.1243
3686.7656 | 122.905 | -68.0008 | 54.5654 | 0.27061 | 0.015923 | 0.01066 | 0.0094698 | -0.0080407 | -0.0041549 | -0.0026574 | 54.6295 | 54.7256 | -68.3716 | 54.7989 | 54.6158 | 54.6387 | 54.4189 | 54.7531 | 54.6478 | 8.4778 | -0.37079 | 0.16022 | 122.6303 | 122.7997 | 0.050354 | 76.4786 | 0.082397 | 123.0011 | 122.4197 | 122.7539 | 122.6166 | 122.7264 | 122.6303 | 122.6486 | 122.6395 | 76.4786 | 122.7264 | 122.6303 | 122.6395 | 122.6166 | 122.6486 | -122.937 | -46.0876
3687.7656 | 122.8958 | -68.042 | 54.5334 | 0.21721 | 0.015283 | 0.0083099 | 0.0096834 | -0.0069727 | -0.0035141 | -0.00094839 | 54.6021 | 54.7119 | -68.3945 | 54.7989 | 54.5792 | 54.5837 | 54.4098 | 54.7165 | 54.6341 | 8.4732 | -0.35248 | 0.17853 | 122.644 | 122.8409 | 0.045777 | 76.5152 | 0.10071 | 122.9965 | 122.4518 | 122.7585 | 122.6212 | 122.7539 | 122.644 | 122.6761 | 122.6257 | 76.5152 | 122.7539 | 122.644 | 122.6257 | 122.6212 | 122.6761 | -122.9279 | -46.0602
3688.7656 | 122.7402 | -68.0603 | 54.5929 | 0.12566 | 0.016137 | 0.010232 | 0.012674 | -0.0056909 | -0.0050095 | -0.0011622 | 54.5792 | 54.7485 | -68.3762 | 54.7165 | 54.5013 | 54.5059 | 54.6066 | 54.6249 | 54.7302 | 8.4778 | -0.31586 | 0.15564 | 122.6395 | 122.7768 | -0.091553 | 76.5381 | 0.13733 | 122.9553 | 122.6669 | 122.6852 | 122.5616 | 122.8088 | 122.6395 | 122.7905 | 122.5662 | 76.5381 | 122.8088 | 122.6395 | 122.5662 | 122.5616 | 122.7905 | -122.9691 | -46.1151
3689.7656 | 122.7631 | -68.0832 | 54.6021 | 0.10277 | 0.015496 | 0.0095917 | 0.013101 | -0.0071863 | -0.0058639 | -0.0028712 | 54.5792 | 54.7714 | -68.4311 | 54.7394 | 54.5334 | 54.4922 | 54.6158 | 54.6295 | 54.7256 | 8.4686 | -0.3479 | 0.16937 | 122.6624 | 122.8226 | -0.068665 | 76.5518 | 0.1236 | 123.0103 | 122.699 | 122.7127 | 122.6166 | 122.8546 | 122.6624 | 122.8088 | 122.5754 | 76.5518 | 122.8546 | 122.6624 | 122.5754 | 122.6166 | 122.8088 | -123.0331 | -46.1334
3690.7656 | 122.8134 | -68.0603 | 54.6112 | 0.18669 | 0.015923 | 0.011301 | 0.010538 | -0.0073999 | -0.0037277 | -0.0054346 | 54.538 | 54.776 | -68.399 | 54.6982 | 54.5151 | 54.2816 | 54.6936 | 54.8721 | 54.6707 | 8.4686 | -0.33874 | 0.16479 | 122.5983 | 122.7585 | -0.09613 | 76.5289 | 0.059509 | 122.937 | 122.7539 | 122.9324 | 122.5754 | 122.8363 | 122.5983 | 122.731 | 122.3419 | 76.5289 | 122.8363 | 122.5983 | 122.3419 | 122.5754 | 122.731 | -123.0103 | -46.1426
3691.7656 | 122.6578 | -68.1198 | 54.5151 | 0.18669 | 0.015069 | 0.0095917 | 0.010752 | -0.0067591 | -0.0041549 | -0.001803 | 54.5059 | 54.7531 | -68.4265 | 54.6936 | 54.4922 | 54.4739 | 54.57 | 54.5883 | 54.6707 | 8.4778 | -0.3067 | 0.23804 | 122.6257 | 122.8134 | -0.022889 | 76.5976 | 0.15564 | 122.9324 | 122.6898 | 122.7081 | 122.612 | 122.8729 | 122.6257 | 122.7905 | 122.5937 | 76.5976 | 122.8729 | 122.6257 | 122.5937 | 122.612 | 122.7905 | -122.9416 | -46.0373
3692.7812 | 122.818 | -68.1198 | 54.5425 | 0.25536 | 0.018701 | 0.0057465 | 0.010111 | -0.0065455 | -0.0024459 | -0.0024438 | 54.5288 | 54.7119 | -68.4906 | 54.6616 | 54.4693 | 54.4601 | 54.5242 | 54.5883 | 54.6616 | 8.4778 | -0.37079 | 0.16937 | 122.6486 | 122.7814 | -0.073243 | 76.5976 | 0.11902 | 123.0194 | 122.644 | 122.7081 | 122.5891 | 122.8317 | 122.6486 | 122.7814 | 122.58 | 76.5976 | 122.8317 | 122.6486 | 122.58 | 122.5891 | 122.7814 | -123.0331 | -46.0648
3693.7656 | 122.905 | -68.074 | 54.5013 | 0.48424 | 0.016351 | 0.011087 | 0.0066928 | -0.0071863 | -0.0024459 | -0.0013758 | 54.6112 | 54.6524 | -68.4311 | 54.7394 | 54.5654 | 54.5929 | 54.3777 | 54.7028 | 54.5883 | 8.4778 | -0.35705 | 0.15106 | 122.6852 | 122.8134 | 0.064087 | 76.5518 | 0.086975 | 123.0423 | 122.4518 | 122.7768 | 122.6395 | 122.7264 | 122.6852 | 122.6624 | 122.6669 | 76.5518 | 122.7264 | 122.6852 | 122.6669 | 122.6395 | 122.6624 | -122.9324 | -46.0236
3694.7656 | 122.9004 | -68.0466 | 54.5517 | 0.25536 | 0.017632 | 0.010232 | 0.0084018 | -0.0076135 | -0.0058639 | -0.0026574 | 54.6021 | 54.6982 | -68.3945 | 54.808 | 54.6066 | 54.6295 | 54.4189 | 54.7577 | 54.6341 | 8.4778 | -0.3479 | 0.14648 | 122.6486 | 122.8546 | 0.054931 | 76.5244 | 0.082397 | 122.9965 | 122.4655 | 122.8043 | 122.6532 | 122.7448 | 122.6486 | 122.6807 | 122.6761 | 76.5244 | 122.7448 | 122.6486 | 122.6761 | 122.6532 | 122.6807 | -122.9462 | -46.0739
3695.7656 | 122.7814 | -68.0695 | 54.6204 | 0.32402 | 0.014855 | 0.0089509 | 0.01182 | -0.0056909 | -0.0060775 | -0.0024438 | 54.5792 | 54.7806 | -68.3899 | 54.7073 | 54.5059 | 54.5151 | 54.6478 | 54.6341 | 54.6982 | 8.4778 | -0.32044 | 0.16022 | 122.6486 | 122.7768 | -0.11444 | 76.5472 | 0.07782 | 122.9691 | 122.7173 | 122.7036 | 122.5754 | 122.85 | 122.6486 | 122.7676 | 122.5845 | 76.5472 | 122.85 | 122.6486 | 122.5845 | 122.5754 | 122.7676 | -123.0103 | -46.1426
3696.7656 | 122.8043 | -68.0328 | 54.6066 | 0.041733 | 0.014855 | 0.010446 | 0.011392 | -0.0067591 | -0.0052231 | -0.0022302 | 54.6524 | 54.808 | -68.3716 | 54.776 | 54.5654 | 54.5654 | 54.6295 | 54.689 | 54.7302 | 8.4686 | -0.33875 | 0.20142 | 122.6852 | 122.8088 | -0.041198 | 76.5015 | 0.1236 | 123.024 | 122.6624 | 122.7219 | 122.5983 | 122.8409 | 122.6852 | 122.7631 | 122.5983 | 76.5015 | 122.8409 | 122.6852 | 122.5983 | 122.5983 | 122.7631 | -122.9782 | -46.138
3697.7656 | 122.8317 | -68.0786 | 54.6112 | -0.087967 | 0.016778 | 0.0093781 | 0.0094698 | -0.0069727 | -0.0050095 | -0.00030759 | 54.6295 | 54.7897 | -68.399 | 54.7211 | 54.5517 | 54.5425 | 54.6295 | 54.6616 | 54.7165 | 8.4778 | -0.32043 | 0.17853 | 122.7081 | 122.7997 | -0.059509 | 76.5564 | 0.10529 | 123.0286 | 122.7081 | 122.7402 | 122.6303 | 122.8683 | 122.7081 | 122.7951 | 122.6212 | 76.5564 | 122.8683 | 122.7081 | 122.6212 | 122.6303 | 122.7951 | -123.0103 | -46.1334
3698.7656 | 122.8134 | -68.0649 | 54.6204 | -1.9267 | 0.01571 | 0.011087 | 0.0075472 | -0.0059045 | -0.0047957 | -0.0024438 | 54.6021 | 54.7989 | -68.3807 | 54.7485 | 54.5242 | 54.5425 | 54.6112 | 54.6661 | 54.7394 | 8.4824 | -0.31586 | 0.17853 | 122.6669 | 122.8134 | -0.09613 | 76.5472 | 0.11902 | 122.9828 | 122.6761 | 122.731 | 122.5891 | 122.8638 | 122.6669 | 122.8043 | 122.6074 | 76.5472 | 122.8638 | 122.6669 | 122.6074 | 122.5891 | 122.8043 | -123.0011 | -46.138
3699.7812 | 122.8226 | -68.042 | 54.6204 | 0.22484 | 0.017846 | 0.016 | 0.0084018 | -0.0073999 | -0.0045821 | -0.0026574 | 54.5929 | 54.776 | -68.4448 | 54.7577 | 54.5654 | 54.5792 | 54.5563 | 54.6799 | 54.7028 | 8.4732 | -0.40283 | 0.15564 | 122.6349 | 122.7997 | -0.054931 | 76.5152 | 0.082398 | 123.0377 | 122.5983 | 122.7219 | 122.6074 | 122.818 | 122.6349 | 122.7448 | 122.6212 | 76.5152 | 122.818 | 122.6349 | 122.6212 | 122.6074 | 122.7448 | -123.0652 | -46.1472
3700.7656 | 122.9279 | -68.0099 | 54.5746 | 0.27824 | 0.013787 | 0.012796 | 0.0062656 | -0.0082545 | -0.0050095 | 0.00011961 | 54.6478 | 54.7485 | -68.3716 | 54.8676 | 54.6249 | 54.6936 | 54.4647 | 54.7806 | 54.6844 | 8.4778 | -0.36163 | 0.17395 | 122.6578 | 122.8775 | 0.050354 | 76.4877 | 0.10986 | 123.0194 | 122.4747 | 122.7905 | 122.6349 | 122.7585 | 122.6578 | 122.6944 | 122.7036 | 76.4877 | 122.7585 | 122.6578 | 122.7036 | 122.6349 | 122.6944 | -122.9462 | -46.0968
3701.7656 | 122.9233 | -68.0145 | 54.5654 | 0.26299 | 0.014001 | 0.0051057 | 0.0098972 | -0.0078271 | -0.0045821 | -0.0020166 | 54.6661 | 54.7165 | -68.3899 | 54.9225 | 54.6158 | 54.6616 | 54.4785 | 54.7852 | 54.6707 | 8.4824 | -0.37537 | 0.15106 | 122.6807 | 122.937 | 0.050354 | 76.4969 | 0.10529 | 123.056 | 122.493 | 122.7997 | 122.6303 | 122.731 | 122.6807 | 122.6852 | 122.6761 | 76.4969 | 122.731 | 122.6807 | 122.6761 | 122.6303 | 122.6852 | -122.9553 | -46.0831
3702.7656 | 122.818 | -68.0191 | 54.6387 | 0.18669 | 0.014214 | 0.0098053 | 0.010965 | -0.0071863 | -0.0054367 | -0.0022302 | 54.332 | 54.7302 | -68.4128 | 54.8126 | 54.5837 | 54.5609 | 54.6295 | 54.6478 | 54.7623 | 8.4824 | -0.39368 | 0.091553 | 122.3511 | 122.8317 | -0.054932 | 76.5015 | 0.1236 | 122.7448 | 122.6486 | 122.6669 | 122.6028 | 122.7493 | 122.3511 | 122.7814 | 122.58 | 76.5015 | 122.7493 | 122.3511 | 122.58 | 122.6028 | 122.7814 | -123.0515 | -46.1563
3703.7656 | 122.8226 | -68.0695 | 54.6387 | 2.8646 | 0.016564 | 0.0098053 | 0.010111 | -0.0091089 | -0.0039413 | -0.0011622 | 54.7623 | 54.7668 | -68.4219 | 54.7668 | 54.5563 | 54.5609 | 54.6021 | 54.6707 | 54.744 | 8.4686 | -0.35248 | 0.12817 | 122.8317 | 122.8363 | -0.082398 | 76.5381 | 0.10529 | 123.1842 | 122.6715 | 122.7402 | 122.6257 | 122.8363 | 122.8317 | 122.8134 | 122.6303 | 76.5381 | 122.8363 | 122.8317 | 122.6303 | 122.6257 | 122.8134 | -123.0606 | -46.17
3704.7656 | 122.85 | -68.0328 | 54.6112 | 0.25536 | 0.014855 | 0.010232 | 0.0086154 | -0.0052637 | -0.0039413 | -0.001803 | 54.6066 | 54.7897 | -68.3853 | 54.7806 | 54.5837 | 54.5929 | 54.5654 | 54.7073 | 54.7485 | 8.4778 | -0.35248 | 0.17853 | 122.6395 | 122.8134 | -0.027466 | 76.5106 | 0.13733 | 122.9919 | 122.5983 | 122.7402 | 122.6166 | 122.8226 | 122.6395 | 122.7814 | 122.6257 | 76.5106 | 122.8226 | 122.6395 | 122.6257 | 122.6166 | 122.7814 | -122.9965 | -46.1334
3705.7656 | 122.8638 | -68.0237 | 54.6204 | 0.2401 | 0.015923 | 0.012369 | 0.010111 | -0.0071863 | -0.0045821 | -0.001803 | 54.6112 | 54.7806 | -68.4036 | 54.7806 | 54.5792 | 54.5975 | 54.57 | 54.7073 | 54.7256 | 8.4869 | -0.37994 | 0.16022 | 122.6349 | 122.8043 | -0.041198 | 76.5106 | 0.10529 | 123.0148 | 122.5937 | 122.731 | 122.6028 | 122.8043 | 122.6349 | 122.7493 | 122.6212 | 76.5106 | 122.8043 | 122.6349 | 122.6212 | 122.6028 | 122.7493 | -123.024 | -46.1334
3706.7656 | 122.905 | -68.0054 | 54.6066 | 0.19432 | 0.014428 | 0.0066009 | 0.0030612 | -0.0088953 | -0.0054367 | 0.00054681 | 54.6341 | 54.7394 | -68.3853 | 54.8309 | 54.6433 | 54.657 | 54.483 | 54.776 | 54.6661 | 8.4778 | -0.37994 | 0.13275 | 122.6395 | 122.8363 | 0.036622 | 76.4832 | 0.05951 | 123.0194 | 122.4884 | 122.7814 | 122.6486 | 122.7448 | 122.6395 | 122.6715 | 122.6624 | 76.4832 | 122.7448 | 122.6395 | 122.6624 | 122.6486 | 122.6715 | -122.9919 | -46.1288
3707.7656 | 122.9141 | -68.0145 | 54.6158 | 0.24773 | 0.013574 | 0.0085235 | 0.003702 | -0.010177 | -0.0060775 | 0.00011961 | 54.657 | 54.7302 | -68.3899 | 54.8264 | 54.6341 | 54.6524 | 54.4922 | 54.776 | 54.689 | 8.4778 | -0.37537 | 0.11444 | 122.6715 | 122.8409 | 0.01831 | 76.4923 | 0.073242 | 123.0469 | 122.5067 | 122.7905 | 122.6486 | 122.7448 | 122.6715 | 122.7036 | 122.6669 | 76.4923 | 122.7448 | 122.6715 | 122.6669 | 122.6486 | 122.7036 | -123.0057 | -46.138
3708.7656 | 122.8912 | -68.0145 | 54.6158 | 0.19432 | 0.014001 | 0.011301 | 0.0069064 | -0.0076135 | -0.0054367 | -0.0015894 | 54.6661 | 54.7073 | -68.3716 | 54.8447 | 54.6387 | 54.6616 | 54.4922 | 54.7806 | 54.7256 | 8.4824 | -0.35706 | 0.091552 | 122.6807 | 122.8592 | 0.022888 | 76.4969 | 0.10986 | 123.0377 | 122.5067 | 122.7951 | 122.6532 | 122.7219 | 122.6807 | 122.7402 | 122.6761 | 76.4969 | 122.7219 | 122.6807 | 122.6761 | 122.6532 | 122.7402 | -122.9874 | -46.1334
3709.7656 | 122.905 | -68.0237 | 54.6295 | 0.26299 | 0.016778 | 0.0066009 | 0.010752 | -0.0080407 | -0.0067185 | -0.0028712 | 54.6433 | 54.7623 | -68.3807 | 54.8218 | 54.6112 | 54.6112 | 54.5517 | 54.7577 | 54.6936 | 8.4824 | -0.35706 | 0.13275 | 122.6669 | 122.8455 | -0.018311 | 76.506 | 0.064087 | 123.024 | 122.5754 | 122.7814 | 122.6349 | 122.7859 | 122.6669 | 122.7173 | 122.6349 | 76.506 | 122.7859 | 122.6669 | 122.6349 | 122.6349 | 122.7173 | -123.0103 | -46.1472
3710.7656 | 122.905 | -68.0099 | 54.6158 | 0.27824 | 0.01571 | 0.0016877 | 0.0096834 | -0.0086817 | -0.0062911 | -0.0013758 | 54.6433 | 54.7714 | -68.3853 | 54.8126 | 54.6112 | 54.6021 | 54.538 | 54.7485 | 54.689 | 8.4824 | -0.37537 | 0.15564 | 122.6532 | 122.8226 | -0.004578 | 76.4923 | 0.073242 | 123.0286 | 122.5479 | 122.7585 | 122.6212 | 122.7814 | 122.6532 | 122.699 | 122.612 | 76.4923 | 122.7814 | 122.6532 | 122.612 | 122.6212 | 122.699 | -123.0011 | -46.1334
3711.7656 | 122.9599 | -67.9916 | 54.6295 | 0.26299 | 0.012078 | 0.011728 | 0.008829 | -0.0078271 | -0.0043685 | -0.0013758 | 54.6707 | 54.7119 | -68.3533 | 54.863 | 54.6616 | 54.7302 | 54.1901 | 54.7623 | 54.657 | 8.4732 | -0.36163 | 0.082397 | 122.6624 | 122.8546 | 0.032043 | 76.4648 | 0.027465 | 123.024 | 122.1817 | 122.7539 | 122.6532 | 122.7036 | 122.6624 | 122.6486 | 122.7219 | 76.4648 | 122.7036 | 122.6624 | 122.7219 | 122.6532 | 122.6486 | -122.9828 | -46.1563
3712.7656 | 122.9095 | -68.0145 | 54.6295 | 0.25536 | 0.015923 | 0.0051057 | 0.0090426 | -0.0082545 | -0.0050095 | -0.0026574 | 54.6524 | 54.7852 | -68.3853 | 54.8218 | 54.6204 | 54.6387 | 54.5151 | 54.7623 | 54.6982 | 8.4778 | -0.37079 | 0.15564 | 122.6669 | 122.8363 | -0.009156 | 76.4923 | 0.068664 | 123.0377 | 122.5296 | 122.7768 | 122.6349 | 122.7997 | 122.6669 | 122.7127 | 122.6532 | 76.4923 | 122.7997 | 122.6669 | 122.6532 | 122.6349 | 122.7127 | -123.0148 | -46.1517
3713.7656 | 122.9004 | -67.9916 | 54.6387 | 0.13329 | 0.012933 | 0.0051057 | 0.0049838 | -0.011245 | -0.0037277 | -0.0022302 | 54.6158 | 54.7211 | -68.3762 | 54.8309 | 54.776 | 54.8126 | 54.5013 | 54.7897 | 54.7302 | 8.4732 | -0.38452 | 0.082397 | 122.6074 | 122.8226 | 0.13733 | 76.4648 | 0.091553 | 122.9919 | 122.493 | 122.7814 | 122.7676 | 122.7127 | 122.6074 | 122.7219 | 122.8043 | 76.4648 | 122.7127 | 122.6074 | 122.8043 | 122.7676 | 122.7219 | -123.0148 | -46.1655
3714.7656 | 122.9095 | -68.0099 | 54.6433 | 0.13329 | 0.01336 | 0.0083099 | 0.0062656 | -0.011886 | -0.0035141 | -0.0058618 | 54.6387 | 54.7531 | -68.3807 | 54.982 | 54.7256 | 54.6616 | 54.5654 | 54.7714 | 54.7348 | 8.4732 | -0.37079 | 0.10986 | 122.6486 | 122.9919 | 0.082397 | 76.4832 | 0.091552 | 123.0194 | 122.5754 | 122.7814 | 122.7356 | 122.7631 | 122.6486 | 122.7448 | 122.6715 | 76.4832 | 122.7631 | 122.6486 | 122.6715 | 122.7356 | 122.7448 | -123.024 | -46.17
3715.7656 | 122.9279 | -67.9871 | 54.6524 | 0.1104 | 0.012078 | 0.0036103 | 0.0060518 | -0.013381 | -0.0052231 | -0.0032984 | 54.6249 | 54.7348 | -68.3762 | 54.8813 | 54.6021 | 54.6844 | 54.5425 | 54.7989 | 54.7211 | 8.4824 | -0.3891 | 0.082397 | 122.612 | 122.8683 | -0.050354 | 76.4694 | 0.068664 | 123.0011 | 122.5296 | 122.7859 | 122.5891 | 122.7219 | 122.612 | 122.7081 | 122.6715 | 76.4694 | 122.7219 | 122.612 | 122.6715 | 122.5891 | 122.7081 | -123.0286 | -46.17
3716.7656 | 122.9416 | -67.9916 | 54.6021 | 0.27061 | 0.014001 | 0.012582 | 0.0081882 | -0.010177 | -0.0062911 | -0.0024438 | 54.6112 | 54.7073 | -68.3899 | 54.9225 | 54.689 | 54.6982 | 54.5013 | 54.8309 | 54.7073 | 8.4824 | -0.39826 | 0.10528 | 122.6028 | 122.9141 | 0.086975 | 76.474 | 0.10528 | 123.0011 | 122.493 | 122.8226 | 122.6807 | 122.699 | 122.6028 | 122.699 | 122.6898 | 76.474 | 122.699 | 122.6028 | 122.6898 | 122.6807 | 122.699 | -122.9919 | -46.1197
3717.7656 | 122.9599 | -67.9962 | 54.6204 | 0.69023 | 0.014428 | 0.0087373 | 0.0084018 | -0.011459 | -0.0039413 | -0.003512 | 54.7028 | 54.689 | -68.3945 | 54.8904 | 54.689 | 54.7028 | 54.4373 | 54.8035 | 54.689 | 8.4824 | -0.39825 | 0.068665 | 122.699 | 122.8867 | 0.068665 | 76.4786 | 0.068665 | 123.0972 | 122.4335 | 122.7997 | 122.6852 | 122.6852 | 122.699 | 122.6852 | 122.699 | 76.4786 | 122.6852 | 122.699 | 122.699 | 122.6852 | 122.6852 | -123.0148 | -46.138
3718.7656 | 122.9233 | -68.0466 | 54.6341 | 0.24773 | 0.011865 | 0.0053193 | 0.0062656 | -0.010177 | -0.0071457 | -0.0026574 | 54.657 | 54.7119 | -68.3395 | 54.8492 | 54.6478 | 54.6616 | 54.5059 | 54.8035 | 54.7073 | 8.4824 | -0.29297 | 0.07782 | 122.7036 | 122.8958 | 0.013733 | 76.5289 | 0.073242 | 122.9965 | 122.5525 | 122.85 | 122.6944 | 122.7585 | 122.7036 | 122.7539 | 122.7081 | 76.5289 | 122.7585 | 122.7036 | 122.7081 | 122.6944 | 122.7539 | -122.9736 | -46.1517
3719.7656 | 122.9187 | -67.9871 | 54.6433 | 0.23247 | 0.012933 | 0.0040375 | 0.0073336 | -0.012954 | -0.0045821 | -0.0030848 | 54.6616 | 54.7165 | -68.3899 | 54.8584 | 54.657 | 54.6524 | 54.4968 | 54.7897 | 54.689 | 8.4824 | -0.40283 | 0.073242 | 122.6486 | 122.8455 | 0.013732 | 76.4694 | 0.045776 | 123.0515 | 122.4838 | 122.7768 | 122.644 | 122.7036 | 122.6486 | 122.6761 | 122.6395 | 76.4694 | 122.7036 | 122.6486 | 122.6395 | 122.644 | 122.6761 | -123.0331 | -46.1609
3720.7656 | 122.9462 | -67.9916 | 54.6478 | 0.011215 | 0.0095148 | 0.0031831 | 0.004343 | -0.012313 | -0.0071457 | -0.0030848 | 54.6707 | 54.7394 | -68.3762 | 54.8996 | 54.7028 | 54.6936 | 54.5609 | 54.8538 | 54.7073 | 8.4824 | -0.38452 | 0.091553 | 122.6624 | 122.8912 | 0.054932 | 76.474 | 0.059509 | 123.0469 | 122.5525 | 122.8455 | 122.6944 | 122.731 | 122.6624 | 122.699 | 122.6852 | 76.474 | 122.731 | 122.6624 | 122.6852 | 122.6944 | 122.699 | -123.024 | -46.1655
3721.7656 | 122.9553 | -68.0099 | 54.6661 | -0.034561 | 0.013146 | 0.0066009 | 0.0049838 | -0.013168 | -0.0058639 | -0.0022302 | 54.6524 | 54.7302 | -68.3899 | 54.8813 | 54.6844 | 54.7028 | 54.538 | 54.8447 | 54.7073 | 8.4824 | -0.37994 | 0.064087 | 122.6624 | 122.8912 | 0.01831 | 76.4923 | 0.041198 | 123.0423 | 122.5479 | 122.8546 | 122.6944 | 122.7402 | 122.6624 | 122.7173 | 122.7127 | 76.4923 | 122.7402 | 122.6624 | 122.7127 | 122.6944 | 122.7173 | -123.056 | -46.1838
3722.7656 | 122.9599 | -68.0054 | 54.6478 | -0.0040434 | 0.012933 | 0.0021149 | 0.0047702 | -0.011245 | -0.0030869 | -0.0020166 | 54.6433 | 54.7028 | -68.3624 | 54.895 | 54.689 | 54.6799 | 54.5334 | 54.8538 | 54.6844 | 8.4915 | -0.35706 | 0.054932 | 122.6486 | 122.9004 | 0.041199 | 76.4969 | 0.036621 | 123.0057 | 122.5388 | 122.8592 | 122.6944 | 122.7081 | 122.6486 | 122.6898 | 122.6852 | 76.4969 | 122.7081 | 122.6486 | 122.6852 | 122.6944 | 122.6898 | -123.0103 | -46.1563
3723.7812 | 122.9004 | -68.0283 | 54.6341 | 0.10277 | 0.012933 | 0.0080963 | 0.0058382 | -0.011672 | -0.0043685 | -0.0020166 | 54.6249 | 54.7028 | -68.4082 | 54.8172 | 54.6295 | 54.6295 | 54.5334 | 54.7806 | 54.6753 | 8.4778 | -0.37994 | 0.068665 | 122.6532 | 122.8455 | -0.004577 | 76.506 | 0.041199 | 123.0331 | 122.5616 | 122.8088 | 122.6578 | 122.731 | 122.6532 | 122.7036 | 122.6578 | 76.506 | 122.731 | 122.6532 | 122.6578 | 122.6578 | 122.7036 | -123.0423 | -46.1563
3724.7656 | 122.9324 | -68.0557 | 54.6341 | 0.25536 | 0.012292 | 0.0078827 | 0.0092562 | -0.0091089 | -0.0060775 | -0.0026574 | 54.6478 | 54.6478 | -68.4128 | 54.8309 | 54.6433 | 54.6387 | 54.4968 | 54.776 | 54.6982 | 8.4869 | -0.35706 | 0.013733 | 122.7036 | 122.8867 | 0.009156 | 76.5427 | 0.064087 | 123.0606 | 122.5525 | 122.8317 | 122.699 | 122.7036 | 122.7036 | 122.7539 | 122.6944 | 76.5427 | 122.7036 | 122.7036 | 122.6944 | 122.699 | 122.7539 | -123.0469 | -46.1472
3725.7812 | 122.9645 | -68.0328 | 54.6478 | 0.07988 | 0.012719 | -2.1336e-05 | 0.005411 | -0.011245 | -0.0060775 | 0.00011961 | 54.6204 | 54.6753 | -68.399 | 54.863 | 54.6616 | 54.657 | 54.5288 | 54.7989 | 54.7073 | 8.4824 | -0.36621 | 0.027466 | 122.6532 | 122.8958 | 0.013733 | 76.5152 | 0.059509 | 123.0194 | 122.5616 | 122.8317 | 122.6944 | 122.7081 | 122.6532 | 122.7402 | 122.6898 | 76.5152 | 122.7081 | 122.6532 | 122.6898 | 122.6944 | 122.7402 | -123.0469 | -46.1655
3726.7812 | 122.85 | -68.0603 | 54.6616 | 0.064621 | 0.014428 | 0.0078827 | 0.016519 | -0.0069727 | -0.0067185 | -0.0043664 | 54.7028 | 54.808 | -68.3899 | 54.8264 | 54.5837 | 54.5883 | 54.6478 | 54.7028 | 54.7531 | 8.4778 | -0.32959 | 0.14648 | 122.7631 | 122.8867 | -0.07782 | 76.5381 | 0.091553 | 123.0927 | 122.7081 | 122.7631 | 122.644 | 122.8683 | 122.7631 | 122.8134 | 122.6486 | 76.5381 | 122.8683 | 122.7631 | 122.6486 | 122.644 | 122.8134 | -123.0515 | -46.1838
3727.7656 | 122.9279 | -68.0832 | 54.5975 | 0.14092 | 0.01336 | 0.0029693 | 0.0051974 | -0.010818 | -0.0058639 | -0.00073479 | 54.5746 | 54.6524 | -68.4814 | 54.7989 | 54.6021 | 54.5929 | 54.5013 | 54.7302 | 54.6982 | 8.4824 | -0.39825 | 0.054932 | 122.6578 | 122.8821 | 0.004578 | 76.5656 | 0.10071 | 123.056 | 122.5845 | 122.8134 | 122.6852 | 122.7356 | 122.6578 | 122.7814 | 122.6761 | 76.5656 | 122.7356 | 122.6578 | 122.6761 | 122.6852 | 122.7814 | -123.0789 | -46.1151
3728.7812 | 123.0148 | -68.0374 | 54.5975 | -0.034561 | 0.010796 | 0.0051057 | 0.004343 | -0.010391 | -0.0065047 | -0.0015894 | 54.6204 | 54.6707 | -68.4311 | 54.8813 | 54.6982 | 54.6616 | 54.4739 | 54.8355 | 54.6478 | 8.4778 | -0.39368 | 0.073242 | 122.6578 | 122.9187 | 0.10071 | 76.5152 | 0.050354 | 123.0515 | 122.5113 | 122.8729 | 122.7356 | 122.7081 | 122.6578 | 122.6852 | 122.699 | 76.5152 | 122.7081 | 122.6578 | 122.699 | 122.7356 | 122.6852 | -123.0286 | -46.1197
3729.7656 | 122.9279 | -68.0557 | 54.6204 | -0.11848 | 0.012078 | 0.011301 | 0.0047702 | -0.011672 | -0.0077865 | -0.0032984 | 54.6433 | 54.6387 | -68.4311 | 54.8767 | 54.6707 | 54.6433 | 54.4968 | 54.8355 | 54.6524 | 8.4915 | -0.37537 | 0.018311 | 122.699 | 122.9324 | 0.050354 | 76.5472 | 0.032044 | 123.0743 | 122.5525 | 122.8912 | 122.7264 | 122.6944 | 122.699 | 122.7081 | 122.699 | 76.5472 | 122.6944 | 122.699 | 122.699 | 122.7264 | 122.7081 | -123.0515 | -46.1288
3730.7656 | 122.9324 | -68.0923 | 54.5654 | 0.07988 | 0.011865 | 0.0046783 | 0.0049838 | -0.013168 | -0.00095055 | -0.0050074 | 54.5746 | 54.6753 | -68.4494 | 54.8584 | 54.5837 | 54.6249 | 54.483 | 54.7348 | 54.6753 | 8.4732 | -0.35706 | 0.10986 | 122.6669 | 122.9507 | 0.01831 | 76.5656 | 0.10986 | 123.024 | 122.5754 | 122.8271 | 122.6761 | 122.7676 | 122.6669 | 122.7676 | 122.7173 | 76.5656 | 122.7676 | 122.6669 | 122.7173 | 122.6761 | 122.7676 | -123.0148 | -46.0922
3731.7812 | 122.8912 | -68.1564 | 54.5746 | -0.14137 | 0.014214 | 0.0087373 | 0.012247 | -0.010391 | -0.0041549 | -0.0030848 | 54.6295 | 54.7211 | -68.4677 | 54.8035 | 54.5746 | 54.5471 | 54.5837 | 54.7028 | 54.6844 | 8.4778 | -0.31128 | 0.14648 | 122.786 | 122.9599 | 0 | 76.6342 | 0.10986 | 123.0972 | 122.7402 | 122.8592 | 122.731 | 122.8775 | 122.786 | 122.8409 | 122.7036 | 76.6342 | 122.8775 | 122.786 | 122.7036 | 122.731 | 122.8409 | -123.0423 | -46.0968
3732.7656 | 122.9736 | -68.1152 | 54.5517 | -0.034561 | 0.012078 | 0.0085235 | 0.0049838 | -0.010604 | -0.0047957 | -0.0015894 | 54.5792 | 54.6433 | -68.4723 | 54.8355 | 54.6341 | 54.6112 | 54.483 | 54.7806 | 54.6387 | 8.4824 | -0.35706 | 0.091553 | 122.6944 | 122.9507 | 0.082397 | 76.5976 | 0.086975 | 123.0515 | 122.5983 | 122.8958 | 122.7493 | 122.7585 | 122.6944 | 122.7539 | 122.7264 | 76.5976 | 122.7585 | 122.6944 | 122.7264 | 122.7493 | 122.7539 | -123.024 | -46.0693
3733.7656 | 122.9874 | -68.129 | 54.5471 | -0.011673 | 0.011865 | 0.0014741 | 0.0028476 | -0.011886 | -0.0060775 | -0.0020166 | 54.538 | 54.5975 | -68.5043 | 54.7852 | 54.6204 | 54.5929 | 54.4144 | 54.7302 | 54.5837 | 8.4824 | -0.37537 | 0.050354 | 122.6669 | 122.9141 | 0.073242 | 76.6113 | 0.036621 | 123.0423 | 122.5433 | 122.8592 | 122.7493 | 122.7264 | 122.6669 | 122.7127 | 122.7219 | 76.6113 | 122.7264 | 122.6669 | 122.7219 | 122.7493 | 122.7127 | -123.0515 | -46.0648
3734.7656 | 122.8912 | -68.1473 | 54.5334 | -0.18715 | 0.011437 | 0.010232 | 0.0090426 | -0.011672 | -0.0062911 | -0.0022302 | 54.5242 | 54.6066 | -68.5272 | 54.7485 | 54.5197 | 54.5197 | 54.5151 | 54.6799 | 54.6341 | 8.4869 | -0.37994 | 0.073242 | 122.6715 | 122.8958 | -0.013733 | 76.6342 | 0.10071 | 123.0515 | 122.6624 | 122.8271 | 122.6669 | 122.7539 | 122.6715 | 122.7814 | 122.6669 | 76.6342 | 122.7539 | 122.6715 | 122.6669 | 122.6669 | 122.7814 | -123.0606 | -46.0464
3735.7656 | 122.8821 | -68.1335 | 54.5929 | -0.23293 | 0.012078 | 0.0016877 | 0.0090426 | -0.011459 | -0.0056503 | -0.0028712 | 54.57 | 54.6204 | -68.4998 | 54.776 | 54.5563 | 54.5197 | 54.5563 | 54.6844 | 54.6295 | 8.4915 | -0.36621 | 0.027465 | 122.7036 | 122.9095 | -0.036622 | 76.6251 | 0.036621 | 123.0698 | 122.6898 | 122.818 | 122.6898 | 122.7539 | 122.7036 | 122.7631 | 122.6532 | 76.6251 | 122.7539 | 122.7036 | 122.6532 | 122.6898 | 122.7631 | -123.0927 | -46.1014
3736.7812 | 122.8546 | -68.1702 | 54.5746 | 0.095139 | 0.016992 | 0.0089509 | 0.013742 | -0.0121 | -0.0065047 | -0.003512 | 54.5609 | 54.7073 | -68.4998 | 54.7165 | 54.4922 | 54.4739 | 54.5471 | 54.5883 | 54.6295 | 8.4778 | -0.32959 | 0.13275 | 122.731 | 122.8867 | -0.082398 | 76.6479 | 0.054932 | 123.0606 | 122.7173 | 122.7585 | 122.6624 | 122.8775 | 122.731 | 122.7997 | 122.644 | 76.6479 | 122.8775 | 122.731 | 122.644 | 122.6624 | 122.7997 | -123.0743 | -46.0968
3737.7656 | 123.0011 | -68.1015 | 54.57 | -0.04219 | 0.010156 | 0.0055329 | 0.0039156 | -0.0097497 | -0.0060775 | -0.0037256 | 54.6066 | 54.6387 | -68.4677 | 54.8584 | 54.6707 | 54.6524 | 54.4327 | 54.8309 | 54.6341 | 8.4824 | -0.36621 | 0.068665 | 122.7081 | 122.9599 | 0.10071 | 76.5839 | 0.064087 | 123.0743 | 122.5342 | 122.9324 | 122.7722 | 122.7402 | 122.7081 | 122.7356 | 122.7539 | 76.5839 | 122.7402 | 122.7081 | 122.7539 | 122.7722 | 122.7356 | -123.0377 | -46.0876
3738.7656 | 122.9782 | -68.1015 | 54.5792 | -0.11848 | 0.012933 | 0.0053193 | 0.005411 | -0.011031 | -0.0065047 | -0.003512 | 54.6204 | 54.6478 | -68.486 | 54.8492 | 54.6433 | 54.6341 | 54.4968 | 54.7989 | 54.6249 | 8.4869 | -0.38452 | 0.068664 | 122.7219 | 122.9507 | 0.064087 | 76.5884 | 0.045776 | 123.1064 | 122.5983 | 122.9004 | 122.7448 | 122.7493 | 122.7219 | 122.7264 | 122.7356 | 76.5884 | 122.7493 | 122.7219 | 122.7356 | 122.7448 | 122.7264 | -123.0652 | -46.0922
3739.7656 | 122.9507 | -68.042 | 54.6387 | -0.149 | 0.012078 | 0.0051057 | 0.0069064 | -0.0121 | -0.0050095 | -0.0022302 | 54.6707 | 54.7073 | -68.4265 | 54.8721 | 54.6753 | 54.6524 | 54.5883 | 54.8447 | 54.6936 | 8.4869 | -0.38452 | 0.068664 | 122.7127 | 122.9141 | 0.036621 | 76.5289 | 0.054932 | 123.0972 | 122.6303 | 122.8867 | 122.7173 | 122.7493 | 122.7127 | 122.7356 | 122.6944 | 76.5289 | 122.7493 | 122.7127 | 122.6944 | 122.7173 | 122.7356 | -123.0652 | -46.1517
3740.7812 | 122.8821 | -68.1061 | 54.6433 | -0.16426 | 0.011651 | 0.0046783 | 0.00712 | -0.0097497 | -0.0045821 | -0.0024438 | 54.5883 | 54.7394 | -68.4586 | 54.7897 | 54.5837 | 54.5563 | 54.6661 | 54.7485 | 54.7256 | 8.4824 | -0.35248 | 0.09613 | 122.6944 | 122.8958 | -0.05951 | 76.5884 | 0.082397 | 123.0469 | 122.7722 | 122.8546 | 122.6898 | 122.8455 | 122.6944 | 122.8317 | 122.6624 | 76.5884 | 122.8455 | 122.6944 | 122.6624 | 122.6898 | 122.8317 | -123.1018 | -46.1609
3741.7656 | 122.9599 | -68.1015 | 54.5792 | 0.26299 | 0.012505 | 0.0057465 | 0.010965 | -0.0088953 | -0.0065047 | -0.0015894 | 54.6158 | 54.689 | -68.486 | 54.8355 | 54.6295 | 54.6021 | 54.3732 | 54.7623 | 54.6478 | 8.4869 | -0.38452 | 0.10986 | 122.7173 | 122.937 | 0.050354 | 76.5884 | 0.068664 | 123.1018 | 122.4747 | 122.8638 | 122.731 | 122.7905 | 122.7173 | 122.7493 | 122.7036 | 76.5884 | 122.7905 | 122.7173 | 122.7036 | 122.731 | 122.7493 | -123.0652 | -46.0922
3742.7656 | 122.9279 | -68.1061 | 54.6204 | -0.12611 | 0.011651 | 0.0066009 | 0.012461 | -0.0080407 | -0.0065047 | -0.003512 | 54.6478 | 54.7668 | -68.454 | 54.8355 | 54.6112 | 54.6021 | 54.6158 | 54.744 | 54.7073 | 8.4824 | -0.3479 | 0.14648 | 122.7539 | 122.9416 | -0.009155 | 76.5884 | 0.086975 | 123.1018 | 122.7219 | 122.85 | 122.7173 | 122.8729 | 122.7539 | 122.8134 | 122.7081 | 76.5884 | 122.8729 | 122.7539 | 122.7081 | 122.7173 | 122.8134 | -123.0743 | -46.138
3743.7656 | 122.8912 | -68.1107 | 54.6524 | -0.17952 | 0.012505 | 0.0066009 | 0.0075472 | -0.0095361 | -0.0062911 | -0.00073479 | 54.6021 | 54.7348 | -68.4402 | 54.8035 | 54.6066 | 54.5609 | 54.6616 | 54.7485 | 54.744 | 8.4869 | -0.32959 | 0.082397 | 122.7127 | 122.9141 | -0.045777 | 76.5976 | 0.091553 | 123.0423 | 122.7722 | 122.8592 | 122.7173 | 122.8455 | 122.7127 | 122.8546 | 122.6715 | 76.5976 | 122.8455 | 122.7127 | 122.6715 | 122.7173 | 122.8546 | -123.0927 | -46.1655
3744.7656 | 122.8912 | -68.1381 | 54.6158 | -0.087967 | 0.016564 | 0.0059601 | 0.0086154 | -0.010177 | -0.0024459 | -0.001803 | 54.5929 | 54.7623 | -68.454 | 54.776 | 54.5792 | 54.5471 | 54.6433 | 54.6982 | 54.7073 | 8.4869 | -0.31586 | 0.14648 | 122.731 | 122.9141 | -0.036621 | 76.6251 | 0.091552 | 123.0469 | 122.7814 | 122.8363 | 122.7173 | 122.9004 | 122.731 | 122.8455 | 122.6852 | 76.6251 | 122.9004 | 122.731 | 122.6852 | 122.7173 | 122.8455 | -123.0698 | -46.1288
3745.7812 | 122.9187 | -68.1244 | 54.6204 | -0.12611 | 0.013787 | 0.010446 | 0.013101 | -0.0073999 | -0.0071457 | -0.0030848 | 54.6249 | 54.7531 | -68.4677 | 54.8172 | 54.5883 | 54.5837 | 54.5929 | 54.7302 | 54.6844 | 8.4824 | -0.34332 | 0.13275 | 122.7493 | 122.9416 | -0.032043 | 76.6068 | 0.064087 | 123.0927 | 122.7173 | 122.8546 | 122.7127 | 122.8775 | 122.7493 | 122.8088 | 122.7081 | 76.6068 | 122.8775 | 122.7493 | 122.7081 | 122.7127 | 122.8088 | -123.0881 | -46.138
3746.7656 | 122.9095 | -68.1061 | 54.6249 | -0.11085 | 0.014855 | 0.0044647 | 0.011606 | -0.0071863 | -0.0071457 | -0.0013758 | 54.5975 | 54.7806 | -68.4631 | 54.7897 | 54.5792 | 54.57 | 54.6478 | 54.7211 | 54.7485 | 8.4824 | -0.35706 | 0.15564 | 122.7036 | 122.8958 | -0.045776 | 76.5884 | 0.1236 | 123.0606 | 122.7539 | 122.8271 | 122.6852 | 122.8867 | 122.7036 | 122.8546 | 122.6761 | 76.5884 | 122.8867 | 122.7036 | 122.6761 | 122.6852 | 122.8546 | -123.0881 | -46.1426
3747.7812 | 122.9187 | -68.1564 | 54.5837 | -0.026932 | 0.015283 | 0.0098053 | 0.0096834 | -0.0067591 | -0.0065047 | -0.0047938 | 54.6204 | 54.7256 | -68.4952 | 54.7806 | 54.57 | 54.5563 | 54.5563 | 54.7211 | 54.689 | 8.4915 | -0.33874 | 0.14191 | 122.7768 | 122.937 | -0.013733 | 76.6479 | 0.10529 | 123.1155 | 122.7127 | 122.8775 | 122.7264 | 122.8821 | 122.7768 | 122.8455 | 122.7127 | 76.6479 | 122.8821 | 122.7768 | 122.7127 | 122.7264 | 122.8455 | -123.0789 | -46.0922
3748.7656 | 122.8592 | -68.2068 | 54.538 | 0.018845 | 0.013787 | 0.0070283 | 0.011606 | -0.0046229 | -0.0052231 | -0.0030848 | 54.5654 | 54.689 | -68.5501 | 54.7028 | 54.4785 | 54.4876 | 54.5288 | 54.6112 | 54.657 | 8.4778 | -0.34332 | 0.15106 | 122.7722 | 122.9095 | -0.059509 | 76.6846 | 0.11902 | 123.1155 | 122.7356 | 122.818 | 122.6852 | 122.8958 | 122.7722 | 122.8638 | 122.6944 | 76.6846 | 122.8958 | 122.7722 | 122.6944 | 122.6852 | 122.8638 | -123.0881 | -46.0602
3749.7656 | 122.8912 | -68.2434 | 54.5242 | 0.10277 | 0.014855 | 0.0098053 | 0.010538 | -0.0067591 | -0.0045821 | 0.00011961 | 54.5151 | 54.6844 | -68.5822 | 54.6753 | 54.483 | 54.4601 | 54.4922 | 54.5792 | 54.6158 | 8.4824 | -0.33875 | 0.16022 | 122.7585 | 122.9187 | -0.041199 | 76.7258 | 0.091553 | 123.0972 | 122.7356 | 122.8226 | 122.7264 | 122.9279 | 122.7585 | 122.8592 | 122.7036 | 76.7258 | 122.9279 | 122.7585 | 122.7036 | 122.7264 | 122.8592 | -123.1064 | -46.0419
3750.7656 | 122.9095 | -68.2388 | 54.5288 | -0.149 | 0.016778 | 0.0095917 | 0.0096834 | -0.0056909 | -0.0050095 | -0.0026574 | 54.5151 | 54.6799 | -68.6188 | 54.7028 | 54.4922 | 54.4968 | 54.5105 | 54.6341 | 54.6066 | 8.4915 | -0.37994 | 0.15106 | 122.7539 | 122.9416 | -0.036622 | 76.7303 | 0.077819 | 123.1338 | 122.7493 | 122.8729 | 122.731 | 122.9187 | 122.7539 | 122.8455 | 122.7356 | 76.7303 | 122.9187 | 122.7539 | 122.7356 | 122.731 | 122.8455 | -123.1476 | -46.0373
3751.7656 | 122.9141 | -68.2114 | 54.5563 | -0.11085 | 0.013787 | 0.0098053 | 0.0092562 | -0.0059045 | -0.0065047 | -0.0015894 | 54.5563 | 54.7119 | -68.5501 | 54.7394 | 54.5425 | 54.5334 | 54.538 | 54.6707 | 54.657 | 8.4824 | -0.33875 | 0.15564 | 122.7676 | 122.9507 | -0.013732 | 76.6937 | 0.10071 | 123.1064 | 122.7493 | 122.8821 | 122.7539 | 122.9233 | 122.7676 | 122.8683 | 122.7448 | 76.6937 | 122.9233 | 122.7676 | 122.7448 | 122.7539 | 122.8683 | -123.1064 | -46.0739
3752.7656 | 122.9462 | -68.2159 | 54.5517 | -0.11085 | 0.014001 | 0.0078827 | 0.01417 | -0.0076135 | -0.0067185 | -0.0020166 | 54.5746 | 54.7256 | -68.5822 | 54.7165 | 54.5609 | 54.5609 | 54.4739 | 54.657 | 54.6112 | 8.4778 | -0.36621 | 0.17395 | 122.7905 | 122.9324 | 0.009155 | 76.6937 | 0.059509 | 123.1567 | 122.6898 | 122.8729 | 122.7768 | 122.9416 | 122.7905 | 122.8271 | 122.7768 | 76.6937 | 122.9416 | 122.7905 | 122.7768 | 122.7768 | 122.8271 | -123.1338 | -46.0739
3753.7656 | 122.9553 | -68.161 | 54.5837 | -0.04982 | 0.015923 | 0.0076691 | 0.008829 | -0.0067591 | -0.0075729 | -0.00094839 | 54.6524 | 54.7165 | -68.541 | 54.744 | 54.57 | 54.538 | 54.5425 | 54.7119 | 54.6982 | 8.4732 | -0.37994 | 0.13275 | 122.8134 | 122.905 | -0.013733 | 76.6342 | 0.11444 | 123.1934 | 122.7036 | 122.8729 | 122.731 | 122.8775 | 122.8134 | 122.8592 | 122.699 | 76.6342 | 122.8775 | 122.8134 | 122.699 | 122.731 | 122.8592 | -123.1247 | -46.1105
3754.7812 | 122.905 | -68.1793 | 54.5746 | 0.056992 | 0.01571 | 0.011301 | 0.012247 | -0.0059045 | -0.0054367 | -0.0015894 | 54.5837 | 54.7577 | -68.5226 | 54.7211 | 54.5197 | 54.5197 | 54.4876 | 54.6433 | 54.6478 | 8.4732 | -0.34332 | 0.1831 | 122.7631 | 122.9004 | -0.054932 | 76.6525 | 0.073242 | 123.1064 | 122.6669 | 122.8226 | 122.699 | 122.937 | 122.7631 | 122.8271 | 122.699 | 76.6525 | 122.937 | 122.7631 | 122.699 | 122.699 | 122.8271 | -123.0972 | -46.1014
3755.7656 | 122.8729 | -68.2159 | 54.5517 | 0.21721 | 0.015923 | 0.010446 | 0.014383 | -0.0059045 | -0.0060775 | -0.0028712 | 54.5197 | 54.7348 | -68.5959 | 54.6982 | 54.5334 | 54.5197 | 54.4601 | 54.6478 | 54.6936 | 8.4824 | -0.37994 | 0.18311 | 122.7356 | 122.9141 | -0.018311 | 76.6983 | 0.14191 | 123.1155 | 122.6761 | 122.8638 | 122.7493 | 122.9507 | 122.7356 | 122.9095 | 122.7356 | 76.6983 | 122.9507 | 122.7356 | 122.7356 | 122.7493 | 122.9095 | -123.1476 | -46.0693
3756.7656 | 122.8867 | -68.2297 | 54.5471 | 0.19432 | 0.015283 | 0.0068147 | 0.012461 | -0.0076135 | -0.0062911 | -0.0028712 | 54.5105 | 54.7073 | -68.5684 | 54.6936 | 54.5105 | 54.4968 | 54.4601 | 54.6341 | 54.6616 | 8.4824 | -0.33875 | 0.16022 | 122.7402 | 122.9233 | -0.036621 | 76.712 | 0.11444 | 123.0789 | 122.6898 | 122.8638 | 122.7402 | 122.937 | 122.7402 | 122.8912 | 122.7264 | 76.712 | 122.937 | 122.7402 | 122.7264 | 122.7402 | 122.8912 | -123.1155 | -46.0648
3757.7656 | 122.9416 | -68.2434 | 54.5197 | -0.026932 | 0.017632 | 0.0051057 | 0.011179 | -0.0071863 | -0.0058639 | 0.00054681 | 54.5746 | 54.6982 | -68.6005 | 54.6753 | 54.4876 | 54.4693 | 54.4418 | 54.6433 | 54.6021 | 8.4778 | -0.35706 | 0.17853 | 122.818 | 122.9187 | -0.032043 | 76.7212 | 0.082398 | 123.175 | 122.6852 | 122.8867 | 122.731 | 122.9416 | 122.818 | 122.8455 | 122.7127 | 76.7212 | 122.9416 | 122.818 | 122.7127 | 122.731 | 122.8455 | -123.1201 | -46.0419
3758.7656 | 122.9279 | -68.1702 | 54.5883 | -0.04219 | 0.017419 | 0.010446 | 0.011392 | -0.0086817 | -0.0045821 | -0.0015894 | 54.5883 | 54.7394 | -68.5501 | 54.7806 | 54.5242 | 54.5471 | 54.4785 | 54.6982 | 54.657 | 8.4686 | -0.37994 | 0.15106 | 122.7585 | 122.9507 | -0.064087 | 76.6388 | 0.068664 | 123.1384 | 122.6486 | 122.8683 | 122.6944 | 122.9095 | 122.7585 | 122.8271 | 122.7173 | 76.6388 | 122.9095 | 122.7585 | 122.7173 | 122.6944 | 122.8271 | -123.1384 | -46.1197
3759.7656 | 122.9324 | -68.2251 | 54.5609 | 0.056992 | 0.016351 | 0.0085235 | 0.008829 | -0.0033411 | -0.0060775 | -0.0015894 | 54.5425 | 54.7256 | -68.573 | 54.689 | 54.4922 | 54.4876 | 54.4968 | 54.6341 | 54.6478 | 8.4732 | -0.3479 | 0.1648 | 122.7676 | 122.9141 | -0.068665 | 76.6983 | 0.086975 | 123.1155 | 122.7219 | 122.8592 | 122.7173 | 122.9507 | 122.7676 | 122.8729 | 122.7127 | 76.6983 | 122.9507 | 122.7676 | 122.7127 | 122.7173 | 122.8729 | -123.1338 | -46.0876
3760.7656 | 122.9233 | -68.2068 | 54.57 | 0.056992 | 0.014855 | 0.0093781 | 0.011392 | -0.0071863 | -0.0065047 | -0.0013758 | 54.5975 | 54.7485 | -68.5226 | 54.7119 | 54.538 | 54.5288 | 54.5059 | 54.6661 | 54.6844 | 8.4732 | -0.31586 | 0.17853 | 122.8043 | 122.9187 | -0.032043 | 76.68 | 0.11444 | 123.1201 | 122.7127 | 122.8729 | 122.7448 | 122.9553 | 122.8043 | 122.8912 | 122.7356 | 76.68 | 122.9553 | 122.8043 | 122.7356 | 122.7448 | 122.8912 | -123.0927 | -46.0968
3761.7656 | 122.9141 | -68.2251 | 54.57 | 0.15617 | 0.018487 | 0.0068147 | 0.0086154 | -0.0041955 | -0.0060775 | -0.0037256 | 54.5151 | 54.7211 | -68.5455 | 54.6844 | 54.4739 | 54.5013 | 54.4968 | 54.5929 | 54.6707 | 8.4824 | -0.32043 | 0.15106 | 122.7402 | 122.9095 | -0.09613 | 76.7075 | 0.10071 | 123.0606 | 122.7219 | 122.818 | 122.699 | 122.9462 | 122.7402 | 122.8958 | 122.7264 | 76.7075 | 122.9462 | 122.7402 | 122.7264 | 122.699 | 122.8958 | -123.1155 | -46.0876
3762.7656 | 122.9004 | -68.2526 | 54.5105 | 0.14854 | 0.016137 | 0.012796 | 0.0092562 | -0.0063317 | -0.0052231 | -0.0022302 | 54.4693 | 54.7073 | -68.6279 | 54.6387 | 54.4418 | 54.4601 | 54.4464 | 54.5654 | 54.6295 | 8.4824 | -0.37537 | 0.19684 | 122.7219 | 122.8912 | -0.068665 | 76.7349 | 0.11902 | 123.0972 | 122.699 | 122.818 | 122.6944 | 122.9599 | 122.7219 | 122.8821 | 122.7127 | 76.7349 | 122.9599 | 122.7219 | 122.7127 | 122.6944 | 122.8821 | -123.1384 | -46.0281
3763.7656 | 122.9095 | -68.2892 | 54.4556 | -0.5381 | 0.016778 | 0.011301 | 0.0094698 | -0.0059045 | -0.0035141 | -0.0024438 | 54.4006 | 54.6616 | -68.6279 | 54.5975 | 54.4006 | 54.4006 | 54.4052 | 54.5059 | 54.57 | 8.4869 | -0.33875 | 0.20599 | 122.6898 | 122.8867 | -0.054931 | 76.7761 | 0.11444 | 123.0286 | 122.6944 | 122.7951 | 122.6898 | 122.9507 | 122.6898 | 122.8592 | 122.6898 | 76.7761 | 122.9507 | 122.6898 | 122.6898 | 122.6898 | 122.8592 | -123.0835 | -45.9686
3764.7656 | 122.9599 | -68.1747 | 54.5746 | 0.15617 | 0.016564 | 0.0072419 | 0.010324 | -0.0076135 | -0.0052231 | -0.0024438 | 54.6341 | 54.7256 | -68.5455 | 54.744 | 54.5242 | 54.5563 | 54.4785 | 54.6982 | 54.6982 | 8.4778 | -0.37079 | 0.15106 | 122.8088 | 122.9187 | -0.050354 | 76.6525 | 0.1236 | 123.1796 | 122.6532 | 122.8729 | 122.699 | 122.9004 | 122.8088 | 122.8729 | 122.731 | 76.6525 | 122.9004 | 122.8088 | 122.731 | 122.699 | 122.8729 | -123.1201 | -46.0968
3765.7656 | 122.9645 | -68.2068 | 54.5792 | 0.0035856 | 0.013787 | 0.01066 | 0.008829 | -0.0063317 | -0.0071457 | -0.001803 | 54.6661 | 54.7211 | -68.5684 | 54.7256 | 54.5242 | 54.5151 | 54.4739 | 54.6936 | 54.6753 | 8.4915 | -0.36163 | 0.14191 | 122.8729 | 122.9324 | -0.054932 | 76.6983 | 0.09613 | 123.2346 | 122.6807 | 122.9004 | 122.731 | 122.9279 | 122.8729 | 122.8821 | 122.7219 | 76.6983 | 122.9279 | 122.8729 | 122.7219 | 122.731 | 122.8821 | -123.1476 | -46.0876
3766.7656 | 122.9233 | -68.2159 | 54.5654 | 0.056992 | 0.016778 | 0.0087373 | 0.01182 | -0.0052637 | -0.0069321 | -0.0030848 | 54.57 | 54.744 | -68.5501 | 54.6982 | 54.4922 | 54.4968 | 54.4968 | 54.6433 | 54.6661 | 8.4824 | -0.33417 | 0.17853 | 122.7859 | 122.9141 | -0.073243 | 76.6983 | 0.10071 | 123.1201 | 122.7127 | 122.8592 | 122.7081 | 122.9599 | 122.7859 | 122.8821 | 122.7127 | 76.6983 | 122.9599 | 122.7859 | 122.7127 | 122.7081 | 122.8821 | -123.1155 | -46.0831
3767.7656 | 122.9324 | -68.4311 | 54.3365 | -0.019302 | 0.014642 | 0.0091645 | 0.0092562 | -0.0067591 | -0.0060775 | -0.0026574 | 54.3686 | 54.5013 | -68.7515 | 54.5059 | 54.2862 | 54.2862 | 54.2496 | 54.4418 | 54.4556 | 8.4778 | -0.32044 | 0.16479 | 122.7997 | 122.937 | -0.050354 | 76.9089 | 0.11902 | 123.1201 | 122.6807 | 122.8729 | 122.7173 | 122.9324 | 122.7997 | 122.8867 | 122.7173 | 76.9089 | 122.9324 | 122.7997 | 122.7173 | 122.7173 | 122.8867 | -123.0881 | -45.8588
3768.7656 | 122.9141 | -68.4952 | 54.3091 | 0.19432 | 0.01571 | 0.0080963 | 0.0092562 | -0.0061181 | -0.0069321 | -0.0020166 | 54.2679 | 54.4785 | -68.8339 | 54.4052 | 54.1946 | 54.2175 | 54.1763 | 54.3411 | 54.4144 | 8.4824 | -0.33875 | 0.16937 | 122.7631 | 122.9004 | -0.11444 | 76.9775 | 0.10529 | 123.1018 | 122.6715 | 122.8363 | 122.6898 | 122.9736 | 122.7631 | 122.9095 | 122.7127 | 76.9775 | 122.9736 | 122.7631 | 122.7127 | 122.6898 | 122.9095 | -123.143 | -45.8267
3769.7656 | 122.9141 | -68.4128 | 54.3549 | 0.049362 | 0.015496 | 0.0093781 | 0.010538 | -0.0078271 | -0.0073593 | -0.00073479 | 54.3137 | 54.538 | -68.8019 | 54.4556 | 54.2725 | 54.277 | 54.2587 | 54.4052 | 54.4739 | 8.4869 | -0.3891 | 0.18311 | 122.7264 | 122.8683 | -0.082397 | 76.8997 | 0.11902 | 123.1155 | 122.6715 | 122.818 | 122.6852 | 122.9507 | 122.7264 | 122.8867 | 122.6898 | 76.8997 | 122.9507 | 122.7264 | 122.6898 | 122.6852 | 122.8867 | -123.1567 | -45.8679
3770.7656 | 122.9279 | -68.3624 | 54.4098 | 0.22484 | 0.01571 | 0.0083099 | 0.0092562 | -0.0061181 | -0.0056503 | -0.0015894 | 54.1809 | 54.5425 | -68.7607 | 54.5334 | 54.332 | 54.3457 | 54.2679 | 54.4464 | 54.5242 | 8.4778 | -0.39825 | 0.13275 | 122.5433 | 122.8958 | -0.07782 | 76.8402 | 0.11444 | 122.9416 | 122.6303 | 122.8088 | 122.6944 | 122.905 | 122.5433 | 122.8867 | 122.7081 | 76.8402 | 122.905 | 122.5433 | 122.7081 | 122.6944 | 122.8867 | -123.1705 | -45.932
3771.7656 | 122.9416 | -70.6192 | 52.1118 | -0.019302 | 0.017419 | 0.0091645 | 0.008829 | -0.0071863 | -0.0050095 | -0.0013758 | 52.0203 | 52.2583 | -71.022 | 52.2812 | 52.0798 | 52.1072 | 51.7227 | 52.2583 | 52.2446 | 8.4824 | -0.40283 | 0.14649 | 122.6395 | 122.9004 | -0.032043 | 79.1016 | 0.13275 | 123.0423 | 122.3419 | 122.8775 | 122.699 | 122.8775 | 122.6395 | 122.8638 | 122.7264 | 79.1016 | 122.8775 | 122.6395 | 122.7264 | 122.699 | 122.8638 | -123.1338 | -43.6295
3772.7656 | 122.9324 | -70.6558 | 52.1347 | 0.034104 | 0.014428 | 0.0091645 | 0.01182 | -0.0071863 | -0.0037277 | 0.00097421 | 52.1439 | 52.3041 | -71.0037 | 52.2629 | 52.0615 | 52.0798 | 51.7685 | 52.2125 | 52.2217 | 8.4686 | -0.3479 | 0.16937 | 122.7997 | 122.9187 | -0.073243 | 79.1245 | 0.086975 | 123.1476 | 122.4243 | 122.8683 | 122.7173 | 122.9599 | 122.7997 | 122.8775 | 122.7356 | 79.1245 | 122.9599 | 122.7997 | 122.7356 | 122.7173 | 122.8775 | -123.1384 | -43.6661
3773.7656 | 122.9553 | -70.0012 | 52.7893 | 0.064621 | 0.018273 | 0.010232 | 0.0094698 | -0.0035547 | -0.0080001 | -0.0022302 | 52.8214 | 52.9633 | -70.3354 | 52.9358 | 52.7298 | 52.7115 | 52.4963 | 52.8625 | 52.9312 | 8.4778 | -0.33417 | 0.17395 | 122.8226 | 122.937 | -0.05951 | 78.479 | 0.14191 | 123.1567 | 122.4976 | 122.8638 | 122.731 | 122.9645 | 122.8226 | 122.9324 | 122.7127 | 78.479 | 122.9645 | 122.8226 | 122.7127 | 122.731 | 122.9324 | -123.1247 | -44.3115
3774.7812 | 122.9004 | -68.4906 | 54.3274 | 0.1104 | 0.016351 | 0.01066 | 0.008829 | -0.0063317 | -0.0045821 | -0.00094839 | 54.2953 | 54.4968 | -68.8065 | 54.4235 | 54.2267 | 54.2267 | 54.2542 | 54.3457 | 54.4052 | 8.4824 | -0.31586 | 0.16937 | 122.7859 | 122.9141 | -0.10071 | 76.973 | 0.077819 | 123.1018 | 122.7448 | 122.8363 | 122.7173 | 122.9874 | 122.7859 | 122.8958 | 122.7173 | 76.973 | 122.9874 | 122.7859 | 122.7173 | 122.7173 | 122.8958 | -123.1339 | -45.845
3775.7656 | 122.9462 | -68.4952 | 54.2633 | 0.1104 | 0.014214 | 0.0091645 | 0.010752 | -0.0073999 | -0.0071457 | -0.0039392 | 54.2221 | 54.451 | -68.866 | 54.3823 | 54.2038 | 54.2038 | 54.158 | 54.3182 | 54.3869 | 8.4824 | -0.37079 | 0.18768 | 122.7173 | 122.8775 | -0.05951 | 76.9775 | 0.1236 | 123.0881 | 122.6532 | 122.8134 | 122.699 | 122.9462 | 122.7173 | 122.8821 | 122.699 | 76.9775 | 122.9462 | 122.7173 | 122.699 | 122.699 | 122.8821 | -123.1293 | -45.7809
3776.7656 | 122.9187 | -70.4132 | 52.3544 | -0.10323 | 0.017205 | 0.0085235 | 0.011392 | -0.0076135 | -0.0039413 | -0.00073479 | 52.3087 | 52.533 | -70.7703 | 52.4551 | 52.3087 | 52.3041 | 51.9974 | 52.4231 | 52.4506 | 8.4732 | -0.35706 | 0.17853 | 122.7219 | 122.8683 | -0.045776 | 78.8864 | 0.096131 | 123.0789 | 122.4106 | 122.8363 | 122.7219 | 122.9462 | 122.7219 | 122.8638 | 122.7173 | 78.8864 | 122.9462 | 122.7219 | 122.7173 | 122.7219 | 122.8638 | -123.1247 | -43.8812
3777.7656 | 122.9233 | -70.4498 | 52.3636 | 3.1316 | 0.016992 | 0.0095917 | 0.011179 | -0.0044091 | -0.0050095 | -0.0032984 | 52.5055 | 52.4918 | -70.784 | 52.4826 | 52.2949 | 52.2903 | 52.0386 | 52.4231 | 52.5009 | 8.4778 | -0.33417 | 0.12817 | 122.9553 | 122.9324 | -0.068664 | 78.9276 | 0.13733 | 123.2895 | 122.4884 | 122.8729 | 122.7448 | 122.9416 | 122.9553 | 122.9507 | 122.7402 | 78.9276 | 122.9416 | 122.9553 | 122.7402 | 122.7448 | 122.9507 | -123.1476 | -43.8858
3778.7656 | 122.9782 | -70.166 | 52.5925 | -0.019302 | 0.011224 | 0.0057465 | 0.010538 | -0.0054773 | -0.0088547 | -0.00094839 | 52.565 | 52.7527 | -70.5276 | 52.7527 | 52.5604 | 52.5879 | 52.3132 | 52.7206 | 52.739 | 8.4824 | -0.36163 | 0.16022 | 122.731 | 122.9187 | -0.032043 | 78.6484 | 0.14649 | 123.0927 | 122.4792 | 122.8867 | 122.7264 | 122.9187 | 122.731 | 122.905 | 122.7539 | 78.6484 | 122.9187 | 122.731 | 122.7539 | 122.7264 | 122.905 | -123.1201 | -44.1101
3779.7656 | 122.9691 | -70.1706 | 52.6337 | -0.034561 | 0.016564 | 0.010232 | 0.012674 | -0.0063317 | -0.0047957 | -0.00073479 | 52.6657 | 52.8076 | -70.5139 | 52.7939 | 52.6382 | 52.6108 | 52.3773 | 52.7435 | 52.771 | 8.4824 | -0.34332 | 0.17395 | 122.8363 | 122.9645 | 0.004578 | 78.653 | 0.13733 | 123.1796 | 122.5479 | 122.9141 | 122.8088 | 122.9782 | 122.8363 | 122.9416 | 122.7814 | 78.653 | 122.9782 | 122.8363 | 122.7814 | 122.8088 | 122.9416 | -123.1476 | -44.1513
3780.7656 | 122.9462 | -70.2026 | 52.597 | 0.041733 | 0.017419 | 0.010019 | 0.0092562 | -0.0048365 | -0.0058639 | -0.0024438 | 52.6108 | 52.7481 | -70.5322 | 52.7344 | 52.5238 | 52.5284 | 52.3041 | 52.6703 | 52.7069 | 8.4778 | -0.32959 | 0.15106 | 122.8134 | 122.937 | -0.073242 | 78.6804 | 0.10986 | 123.143 | 122.5067 | 122.8729 | 122.7264 | 122.9507 | 122.8134 | 122.9095 | 122.731 | 78.6804 | 122.9507 | 122.8134 | 122.731 | 122.7264 | 122.9095 | -123.1293 | -44.1193
3781.7812 | 122.905 | -70.253 | 52.5375 | 0.1104 | 0.015496 | 0.010232 | 0.012461 | -0.0059045 | -0.0069321 | -0.0015894 | 52.5192 | 52.6886 | -70.6009 | 52.6382 | 52.4506 | 52.4506 | 52.272 | 52.5833 | 52.6886 | 8.4824 | -0.3479 | 0.15106 | 122.7722 | 122.8912 | -0.086975 | 78.7354 | 0.15106 | 123.1201 | 122.525 | 122.8363 | 122.7036 | 122.9416 | 122.7722 | 122.9416 | 122.7036 | 78.7354 | 122.9416 | 122.7722 | 122.7036 | 122.7036 | 122.9416 | -123.1384 | -44.0552
3782.7656 | 122.9462 | -70.1111 | 52.6794 | 0.20195 | 0.016351 | 0.011301 | 0.010324 | -0.0065455 | -0.0045821 | -0.00073479 | 52.6337 | 52.8214 | -70.4865 | 52.7802 | 52.597 | 52.5879 | 52.4002 | 52.7161 | 52.7893 | 8.4824 | -0.37537 | 0.14191 | 122.7448 | 122.8912 | -0.082397 | 78.5934 | 0.10986 | 123.1201 | 122.5113 | 122.8271 | 122.7081 | 122.9324 | 122.7448 | 122.9004 | 122.699 | 78.5934 | 122.9324 | 122.7448 | 122.699 | 122.7081 | 122.9004 | -123.1659 | -44.1971
3783.7656 | 122.9645 | -70.1431 | 52.6291 | 0.25536 | 0.014428 | 0.01066 | 0.0064792 | -0.0065455 | -0.0039413 | -0.0011622 | 52.6108 | 52.803 | -70.5139 | 52.739 | 52.565 | 52.5787 | 52.359 | 52.6932 | 52.739 | 8.4824 | -0.37079 | 0.17395 | 122.7539 | 122.8821 | -0.064087 | 78.6255 | 0.10986 | 123.1247 | 122.5021 | 122.8363 | 122.7081 | 122.9462 | 122.7539 | 122.8821 | 122.7219 | 78.6255 | 122.9462 | 122.7539 | 122.7219 | 122.7081 | 122.8821 | -123.143 | -44.1467
3784.7656 | 122.9599 | -69.9875 | 52.7847 | 0.22484 | 0.01571 | 0.0095917 | 0.0073336 | -0.0059045 | -0.0047957 | -0.0024438 | 52.7618 | 52.9587 | -70.3583 | 52.9175 | 52.7161 | 52.7298 | 52.4918 | 52.8534 | 52.9083 | 8.4778 | -0.37079 | 0.17395 | 122.7493 | 122.905 | -0.068665 | 78.4653 | 0.1236 | 123.1201 | 122.4792 | 122.8409 | 122.7036 | 122.9462 | 122.7493 | 122.8958 | 122.7173 | 78.4653 | 122.9462 | 122.7493 | 122.7173 | 122.7036 | 122.8958 | -123.143 | -44.3069
3785.7656 | 122.9507 | -70.0012 | 52.7802 | 0.11803 | 0.015496 | 0.0053193 | 0.012461 | -0.0061181 | -0.0054367 | -0.0013758 | 52.8076 | 52.9312 | -70.3766 | 52.9221 | 52.7161 | 52.7161 | 52.4551 | 52.8534 | 52.8671 | 8.4778 | -0.37537 | 0.15106 | 122.8088 | 122.9233 | -0.064087 | 78.479 | 0.086975 | 123.1842 | 122.4564 | 122.8546 | 122.7173 | 122.9324 | 122.8088 | 122.8683 | 122.7173 | 78.479 | 122.9324 | 122.8088 | 122.7173 | 122.7173 | 122.8683 | -123.1567 | -44.3024
3786.7656 | 122.9599 | -70.1797 | 52.6108 | 0.018845 | 0.015923 | 0.0078827 | 0.010324 | -0.0050501 | -0.0058639 | -0.0028712 | 52.6703 | 52.7802 | -70.5139 | 52.771 | 52.5925 | 52.5787 | 52.2629 | 52.7161 | 52.7435 | 8.4824 | -0.33417 | 0.16937 | 122.85 | 122.9507 | -0.018311 | 78.6621 | 0.13275 | 123.1842 | 122.4426 | 122.8958 | 122.7722 | 122.9599 | 122.85 | 122.9233 | 122.7585 | 78.6621 | 122.9599 | 122.85 | 122.7585 | 122.7722 | 122.9233 | -123.1247 | -44.1284
3787.7656 | 122.9141 | -70.1157 | 52.684 | 0.041733 | 0.015923 | 0.010019 | 0.010324 | -0.0046229 | -0.0054367 | -0.0022302 | 52.684 | 52.8625 | -70.4636 | 52.8214 | 52.6154 | 52.6154 | 52.3911 | 52.7481 | 52.8076 | 8.4778 | -0.3479 | 0.17853 | 122.7997 | 122.937 | -0.068665 | 78.5934 | 0.1236 | 123.1476 | 122.5067 | 122.8638 | 122.731 | 122.9782 | 122.7997 | 122.9233 | 122.731 | 78.5934 | 122.9782 | 122.7997 | 122.731 | 122.731 | 122.9233 | -123.1476 | -44.2062
3788.7812 | 122.8683 | -69.9463 | 52.8122 | 0.15617 | 0.016778 | 0.0059601 | 0.010538 | -0.0056909 | -0.0039413 | -0.00052119 | 52.8351 | 53.0273 | -70.2896 | 52.9678 | 52.7847 | 52.7802 | 52.565 | 52.9037 | 53.0045 | 8.4824 | -0.34332 | 0.21515 | 122.7814 | 122.9141 | -0.027466 | 78.4286 | 0.19226 | 123.1247 | 122.5113 | 122.85 | 122.731 | 122.9736 | 122.7814 | 122.9507 | 122.7264 | 78.4286 | 122.9736 | 122.7814 | 122.7264 | 122.731 | 122.9507 | -123.1018 | -44.3298
3789.7656 | 123.0057 | -69.722 | 53.0457 | 0.27824 | 0.016564 | 0.010019 | 0.0092562 | -0.0071863 | -0.0043685 | 0.00033321 | 53.0594 | 53.1921 | -70.1019 | 53.2013 | 53.0273 | 53.0319 | 52.6978 | 53.1647 | 53.1509 | 8.4824 | -0.37994 | 0.14648 | 122.7814 | 122.9233 | -0.01831 | 78.2043 | 0.10529 | 123.1613 | 122.4197 | 122.8867 | 122.7493 | 122.9141 | 122.7814 | 122.8729 | 122.7539 | 78.2043 | 122.9141 | 122.7814 | 122.7539 | 122.7493 | 122.8729 | -123.1476 | -44.5633
3790.7656 | 122.9965 | -69.9417 | 52.8214 | 0.28587 | 0.016564 | 0.0098053 | 0.0092562 | -0.0035547 | -0.0054367 | -0.0020166 | 52.8305 | 52.9861 | -70.3171 | 52.9999 | 52.7893 | 52.8214 | 52.478 | 52.9358 | 52.9495 | 8.4778 | -0.37537 | 0.16479 | 122.7722 | 122.9416 | -0.032043 | 78.4195 | 0.12817 | 123.1476 | 122.4197 | 122.8775 | 122.731 | 122.9279 | 122.7722 | 122.8912 | 122.7631 | 78.4195 | 122.9279 | 122.7722 | 122.7631 | 122.731 | 122.8912 | -123.1384 | -44.3436
3791.7656 | 122.9965 | -69.809 | 52.9541 | 0.27061 | 0.015283 | 0.0093781 | 0.0079744 | -0.0065455 | -0.0037277 | -0.00052119 | 52.9587 | 53.1235 | -70.1889 | 53.1189 | 52.9129 | 52.9404 | 52.6062 | 53.0548 | 53.064 | 8.4869 | -0.37994 | 0.16937 | 122.7676 | 122.9279 | -0.041199 | 78.2959 | 0.10986 | 123.1476 | 122.4152 | 122.8638 | 122.7219 | 122.9324 | 122.7676 | 122.8729 | 122.7493 | 78.2959 | 122.9324 | 122.7676 | 122.7493 | 122.7219 | 122.8729 | -123.143 | -44.4672
3792.7656 | 122.9233 | -69.5618 | 53.2242 | 0.14092 | 0.016351 | 0.0093781 | 0.010111 | -0.0059045 | -0.0052231 | -0.001803 | 53.2333 | 53.3798 | -69.928 | 53.3661 | 53.1509 | 53.1555 | 53.0045 | 53.2791 | 53.3432 | 8.4732 | -0.36621 | 0.15564 | 122.7951 | 122.9279 | -0.073242 | 78.035 | 0.11902 | 123.1613 | 122.5662 | 122.8409 | 122.7127 | 122.9416 | 122.7951 | 122.905 | 122.7173 | 78.035 | 122.9416 | 122.7951 | 122.7173 | 122.7127 | 122.905 | -123.1522 | -44.751
3793.7656 | 122.9691 | -69.841 | 52.9724 | 0.13329 | 0.01571 | 0.0076691 | 0.012247 | -0.0078271 | -0.0088547 | -0.001803 | 52.9495 | 53.1876 | -70.1889 | 53.0777 | 52.8763 | 52.8717 | 52.7573 | 53.0045 | 53.096 | 8.4778 | -0.3479 | 0.21515 | 122.7905 | 122.9187 | -0.09613 | 78.3188 | 0.1236 | 123.1384 | 122.5983 | 122.8455 | 122.7173 | 123.0286 | 122.7905 | 122.937 | 122.7127 | 78.3188 | 123.0286 | 122.7905 | 122.7127 | 122.7173 | 122.937 | -123.1613 | -44.4946
3794.7812 | 122.9279 | -69.8044 | 52.9907 | 0.19432 | 0.016351 | 0.0068147 | 0.0096834 | -0.0065455 | -0.0050095 | -0.0015894 | 52.9587 | 53.1601 | -70.166 | 53.1235 | 52.9175 | 52.9312 | 52.7481 | 53.0502 | 53.1097 | 8.4732 | -0.36163 | 0.16937 | 122.7631 | 122.9279 | -0.073243 | 78.2776 | 0.11902 | 123.1247 | 122.5525 | 122.8546 | 122.7219 | 122.9645 | 122.7631 | 122.9141 | 122.7356 | 78.2776 | 122.9645 | 122.7631 | 122.7356 | 122.7219 | 122.9141 | -123.1567 | -44.5175
3795.7812 | 122.9462 | -69.9005 | 52.9266 | 0.20195 | 0.015923 | 0.013223 | 0.0086154 | -0.0080407 | -0.0062911 | -0.0015894 | 52.9037 | 53.0685 | -70.2438 | 53.0457 | 52.8534 | 52.858 | 52.6657 | 52.9724 | 53.0182 | 8.4824 | -0.34332 | 0.14191 | 122.8043 | 122.9462 | -0.073242 | 78.3829 | 0.091552 | 123.1476 | 122.5662 | 122.8729 | 122.7539 | 122.9691 | 122.8043 | 122.9187 | 122.7585 | 78.3829 | 122.9691 | 122.8043 | 122.7585 | 122.7539 | 122.9187 | -123.1705 | -44.4443
3796.7656 | 123.0423 | -69.7952 | 52.9083 | 0.26299 | 0.013787 | 0.0072419 | 0.0077608 | -0.0065455 | -0.0054367 | -0.0013758 | 53.0182 | 53.064 | -70.166 | 53.1921 | 52.9861 | 53.009 | 52.5696 | 53.1281 | 53.0319 | 8.4869 | -0.37079 | 0.15564 | 122.8134 | 122.9874 | 0.07782 | 78.2822 | 0.1236 | 123.1842 | 122.3648 | 122.9233 | 122.7814 | 122.8592 | 122.8134 | 122.8271 | 122.8043 | 78.2822 | 122.8592 | 122.8134 | 122.8043 | 122.7814 | 122.8271 | -123.0743 | -44.4214
3797.7656 | 123.1018 | -69.8822 | 52.8717 | 0.27061 | 0.01336 | 0.0072419 | 0.0075472 | -0.0065455 | -0.0037277 | -0.0024438 | 52.9633 | 53.0594 | -70.2209 | 53.1189 | 52.9266 | 52.9587 | 52.5146 | 53.0731 | 52.9587 | 8.4869 | -0.33874 | 0.18768 | 122.8455 | 123.0011 | 0.054932 | 78.3691 | 0.086975 | 123.1842 | 122.3969 | 122.9553 | 122.8088 | 122.9416 | 122.8455 | 122.8409 | 122.8409 | 78.3691 | 122.9416 | 122.8455 | 122.8409 | 122.8088 | 122.8409 | -123.0927 | -44.3848
3798.7656 | 122.9553 | -69.754 | 53.0914 | 0.17906 | 0.016137 | 0.0091645 | 0.010538 | -0.0088953 | -0.0056503 | -0.00073479 | 53.0182 | 53.2379 | -70.0974 | 52.8717 | 52.7664 | 53.1464 | 52.8992 | 53.1876 | 53.183 | 8.4824 | -0.34332 | 0.14648 | 122.7722 | 122.6257 | -0.32501 | 78.2364 | 0.091552 | 123.1155 | 122.6532 | 122.9416 | 122.5204 | 122.9919 | 122.7722 | 122.937 | 122.9004 | 78.2364 | 122.9919 | 122.7722 | 122.9004 | 122.5204 | 122.937 | -123.1888 | -44.6091
3799.7656 | 122.9279 | -69.6716 | 53.1509 | 0.20958 | 0.016992 | 0.010232 | 0.0098972 | -0.0078271 | -0.0039413 | -0.0032984 | 53.0594 | 53.2654 | -70.0699 | 53.4256 | 53.1921 | 53.0457 | 53.0136 | 53.1418 | 53.2471 | 8.4824 | -0.39825 | 0.11444 | 122.731 | 123.0972 | 0.041199 | 78.154 | 0.09613 | 123.1293 | 122.6852 | 122.8134 | 122.8638 | 122.937 | 122.731 | 122.9187 | 122.7173 | 78.154 | 122.937 | 122.731 | 122.7173 | 122.8638 | 122.9187 | -123.2208 | -44.6686
3800.7656 | 122.9691 | -69.6396 | 53.1372 | 0.20958 | 0.015069 | 0.011087 | 0.0069064 | -0.0080407 | -0.0039413 | -0.0011622 | 53.1601 | 53.3295 | -69.9921 | 53.2974 | 53.1281 | 53.1281 | 52.9495 | 53.2471 | 53.2745 | 8.4824 | -0.35248 | 0.19226 | 122.7997 | 122.937 | -0.009155 | 78.1219 | 0.13733 | 123.1522 | 122.5891 | 122.8867 | 122.7676 | 122.9691 | 122.7997 | 122.9141 | 122.7676 | 78.1219 | 122.9691 | 122.7997 | 122.7676 | 122.7676 | 122.9141 | -123.1293 | -44.6548
3801.7656 | 122.9965 | -69.7083 | 53.0731 | 0.22484 | 0.015923 | 0.0072419 | 0.0079744 | -0.0073999 | -0.0037277 | -0.0024438 | 53.0731 | 53.2333 | -70.0745 | 53.2288 | 53.0228 | 53.0319 | 52.858 | 53.1555 | 53.2013 | 8.4824 | -0.36621 | 0.16022 | 122.7814 | 122.937 | -0.050354 | 78.1906 | 0.12817 | 123.1476 | 122.5662 | 122.8638 | 122.731 | 122.9416 | 122.7814 | 122.9095 | 122.7402 | 78.1906 | 122.9416 | 122.7814 | 122.7402 | 122.731 | 122.9095 | -123.1476 | -44.5908
3802.7812 | 123.0835 | -69.5114 | 53.2379 | 0.28587 | 0.012933 | 0.0074555 | 0.0079744 | -0.0082545 | -0.0050095 | 0.00054681 | 53.2837 | 53.3295 | -69.9051 | 53.4668 | 53.2471 | 53.2837 | 52.9312 | 53.4027 | 53.3295 | 8.4915 | -0.39368 | 0.091553 | 122.7951 | 122.9782 | 0.009155 | 78.0029 | 0.091553 | 123.1888 | 122.4426 | 122.9141 | 122.7585 | 122.8409 | 122.7951 | 122.8409 | 122.7951 | 78.0029 | 122.8409 | 122.7951 | 122.7951 | 122.7585 | 122.8409 | -123.143 | -44.7464
3803.7656 | 123.0331 | -69.4702 | 53.27 | 0.20195 | 0.01336 | 0.0091645 | 0.0032748 | -0.0071863 | -0.0056503 | -0.0028712 | 53.3249 | 53.3661 | -69.8318 | 53.4897 | 53.302 | 53.3157 | 52.9633 | 53.4439 | 53.3386 | 8.4915 | -0.36163 | 0.096131 | 122.7951 | 122.9599 | 0.032044 | 77.9617 | 0.068665 | 123.1567 | 122.4335 | 122.9141 | 122.7722 | 122.8363 | 122.7951 | 122.8088 | 122.7859 | 77.9617 | 122.8363 | 122.7951 | 122.7859 | 122.7722 | 122.8088 | -123.1018 | -44.7784
3804.7656 | 123.024 | -69.4565 | 53.302 | 0.21721 | 0.012292 | 0.0061737 | 0.005411 | -0.0091089 | -0.0026595 | -0.0024438 | 53.3432 | 53.3936 | -69.809 | 53.5034 | 53.3295 | 53.3432 | 52.9999 | 53.4805 | 53.3844 | 8.4915 | -0.35248 | 0.091553 | 122.7997 | 122.9599 | 0.027466 | 77.948 | 0.082397 | 123.1522 | 122.4564 | 122.937 | 122.7859 | 122.85 | 122.7997 | 122.8409 | 122.7997 | 77.948 | 122.85 | 122.7997 | 122.7997 | 122.7859 | 122.8409 | -123.111 | -44.8105
3805.7656 | 123.0057 | -69.4427 | 53.3249 | 0.25536 | 0.016564 | 0.0061737 | 0.010538 | -0.0086817 | -0.0080001 | -0.0032984 | 53.3386 | 53.4668 | -69.8318 | 53.508 | 53.2883 | 53.3112 | 53.064 | 53.4393 | 53.4393 | 8.4824 | -0.3891 | 0.14191 | 122.7814 | 122.9507 | -0.036621 | 77.9251 | 0.11444 | 123.1705 | 122.5067 | 122.8821 | 122.731 | 122.9095 | 122.7814 | 122.8821 | 122.7539 | 77.9251 | 122.9095 | 122.7814 | 122.7539 | 122.731 | 122.8821 | -123.1567 | -44.8425
3806.7656 | 123.0377 | -68.2434 | 54.5242 | 0.26299 | 0.014001 | 0.0061737 | 0.008829 | -0.0073999 | -0.0054367 | -0.00052119 | 54.5334 | 54.657 | -68.5913 | 54.7256 | 54.5151 | 54.5334 | 54.3732 | 54.6524 | 54.6295 | 8.4869 | -0.3479 | 0.13275 | 122.7768 | 122.9691 | -0.009155 | 76.7303 | 0.10529 | 123.1247 | 122.6166 | 122.8958 | 122.7585 | 122.9004 | 122.7768 | 122.8729 | 122.7768 | 76.7303 | 122.9004 | 122.7768 | 122.7768 | 122.7585 | 122.8729 | -123.1155 | -46.0373
3807.7656 | 123.0789 | -68.1519 | 54.6158 | 0.27061 | 0.014214 | 0.0046783 | 0.00712 | -0.0071863 | -0.0026595 | -0.00094839 | 54.6661 | 54.7211 | -68.5181 | 54.8492 | 54.6249 | 54.6661 | 54.1443 | 54.657 | 54.6341 | 8.4915 | -0.36621 | 0.10529 | 122.818 | 123.0011 | 0.009155 | 76.6434 | 0.01831 | 123.1842 | 122.2961 | 122.8088 | 122.7768 | 122.8729 | 122.818 | 122.7859 | 122.818 | 76.6434 | 122.8729 | 122.818 | 122.818 | 122.7768 | 122.7859 | -123.1338 | -46.1243
3808.7656 | 123.0698 | -68.161 | 54.5746 | 0.28587 | 0.013787 | 0.0076691 | 0.0081882 | -0.0078271 | -0.0039413 | -0.005221 | 54.657 | 54.6524 | -68.5226 | 54.744 | 54.7302 | 54.7394 | 54.4006 | 54.7806 | 54.6844 | 8.4824 | -0.36163 | 0.07782 | 122.818 | 122.905 | 0.15564 | 76.6434 | 0.10986 | 123.1796 | 122.5616 | 122.9416 | 122.8912 | 122.8134 | 122.818 | 122.8455 | 122.9004 | 76.6434 | 122.8134 | 122.818 | 122.9004 | 122.8912 | 122.8455 | -123.0972 | -46.0922
3809.7812 | 123.0469 | -69.548 | 53.1967 | 0.20195 | 0.012292 | 0.0070283 | 0.0049838 | -0.010177 | -0.0069321 | -0.0020166 | 53.2425 | 53.27 | -69.9509 | 53.4256 | 53.2333 | 53.2516 | 52.8168 | 53.3707 | 53.27 | 8.4869 | -0.40283 | 0.073242 | 122.7905 | 122.9736 | 0.036621 | 78.035 | 0.073242 | 123.1934 | 122.3648 | 122.9187 | 122.7814 | 122.818 | 122.7905 | 122.818 | 122.7997 | 78.035 | 122.818 | 122.7905 | 122.7997 | 122.7814 | 122.818 | -123.1476 | -44.7098
3810.7656 | 123.0377 | -69.5068 | 53.2654 | 0.14854 | 0.014001 | -0.00087594 | 0.002634 | -0.011672 | -0.0050095 | -0.0015894 | 53.2288 | 53.3432 | -69.873 | 53.4164 | 53.2562 | 53.2425 | 52.977 | 53.4393 | 53.3295 | 8.4824 | -0.36621 | 0.07782 | 122.7356 | 122.9233 | -0.009155 | 77.9892 | 0.064087 | 123.1018 | 122.4838 | 122.9462 | 122.7631 | 122.85 | 122.7356 | 122.8363 | 122.7493 | 77.9892 | 122.85 | 122.7356 | 122.7493 | 122.7631 | 122.8363 | -123.1384 | -44.783
3811.7656 | 123.0194 | -69.6625 | 53.1006 | 0.07988 | 0.010156 | 0.0076691 | 0.003702 | -0.015945 | -0.0039413 | -0.0024438 | 53.0548 | 53.1738 | -70.0424 | 53.2654 | 53.0731 | 53.0319 | 52.8488 | 53.2288 | 53.1692 | 8.4778 | -0.37994 | 0.073242 | 122.7173 | 122.9279 | -0.027466 | 78.1403 | 0.068664 | 123.0972 | 122.5113 | 122.8912 | 122.7356 | 122.8363 | 122.7173 | 122.8317 | 122.6944 | 78.1403 | 122.8363 | 122.7173 | 122.6944 | 122.7356 | 122.8317 | -123.143 | -44.6228
3812.7812 | 122.9919 | -69.7723 | 53.0777 | -0.16426 | 0.016778 | 0.0095917 | 0.010965 | -0.011886 | -0.0065047 | -0.0026574 | 53.0411 | 53.215 | -70.1157 | 53.2288 | 52.9953 | 52.9724 | 52.9221 | 53.1464 | 53.1647 | 8.4824 | -0.34332 | 0.13733 | 122.8134 | 123.0011 | -0.082398 | 78.2547 | 0.086975 | 123.1567 | 122.6944 | 122.9187 | 122.7676 | 122.9874 | 122.8134 | 122.937 | 122.7448 | 78.2547 | 122.9874 | 122.8134 | 122.7448 | 122.7676 | 122.937 | -123.1934 | -44.5953
3813.7656 | 123.056 | -69.5892 | 53.1692 | -0.55336 | 0.011651 | 0.0055329 | 0.0090426 | -0.0099633 | -0.0069321 | -0.0032984 | 53.2928 | 53.2425 | -69.9646 | 53.421 | 53.2104 | 53.2196 | 52.8259 | 53.3524 | 53.2654 | 8.4824 | -0.37537 | 0.073243 | 122.8821 | 123.0103 | 0.041199 | 78.0716 | 0.096131 | 123.2574 | 122.4152 | 122.9416 | 122.7997 | 122.8317 | 122.8821 | 122.8546 | 122.8088 | 78.0716 | 122.8317 | 122.8821 | 122.8088 | 122.7997 | 122.8546 | -123.1338 | -44.6869
3814.7656 | 123.0377 | -69.4839 | 53.2288 | 0.20958 | 0.012933 | 0.0089509 | 0.0073336 | -0.0097497 | -0.0065047 | -0.0022302 | 53.4073 | 53.4302 | -69.7769 | 53.5721 | 53.3981 | 53.3981 | 53.0823 | 53.5034 | 53.421 | 8.4869 | -0.29297 | 0.20142 | 122.8912 | 123.056 | 0.16937 | 77.9709 | 0.19226 | 123.1842 | 122.5662 | 122.9874 | 122.8821 | 122.9141 | 122.8912 | 122.905 | 122.8821 | 77.9709 | 122.9141 | 122.8912 | 122.8821 | 122.8821 | 122.905 | -123.0057 | -44.7418
3815.7656 | 123.0423 | -69.4199 | 53.3295 | 0.23247 | 0.010583 | 0.0031831 | 0.00712 | -0.0093225 | -0.0050095 | -0.0030848 | 53.3936 | 53.4027 | -69.7952 | 53.5767 | 53.3661 | 53.3661 | 53.0228 | 53.5126 | 53.4027 | 8.4824 | -0.37537 | 0.073242 | 122.8134 | 122.9965 | 0.036621 | 77.9022 | 0.073242 | 123.1888 | 122.4426 | 122.9324 | 122.7859 | 122.8226 | 122.8134 | 122.8226 | 122.7859 | 77.9022 | 122.8226 | 122.8134 | 122.7859 | 122.7859 | 122.8226 | -123.1247 | -44.8471
3816.7812 | 123.0286 | -69.4107 | 53.3707 | 0.14854 | 0.013146 | 0.0080963 | 0.0045566 | -0.011672 | -0.0041549 | -0.0026574 | 53.3478 | 53.4164 | -69.7906 | 53.5629 | 53.3478 | 53.3752 | 53.0594 | 53.5034 | 53.421 | 8.4824 | -0.37994 | 0.045776 | 122.7585 | 122.9736 | -0.022889 | 77.8931 | 0.050354 | 123.1384 | 122.4701 | 122.9141 | 122.7585 | 122.8271 | 122.7585 | 122.8317 | 122.786 | 77.8931 | 122.8271 | 122.7585 | 122.786 | 122.7585 | 122.8317 | -123.1613 | -44.8883
3817.7812 | 122.9691 | -69.4473 | 53.3844 | -0.20241 | 0.01336 | 0.0053193 | 0.0079744 | -0.013381 | -0.0060775 | -0.0011622 | 53.3844 | 53.4988 | -69.7723 | 53.5446 | 53.3432 | 53.3295 | 53.2791 | 53.4943 | 53.4805 | 8.4869 | -0.32501 | 0.11444 | 122.8317 | 122.9919 | -0.041198 | 77.9343 | 0.096131 | 123.1567 | 122.7264 | 122.9416 | 122.7905 | 122.9462 | 122.8317 | 122.9279 | 122.7768 | 77.9343 | 122.9462 | 122.8317 | 122.7768 | 122.7905 | 122.9279 | -123.1567 | -44.8975
3818.7656 | 123.0881 | -69.2917 | 53.4805 | 0.026474 | 0.013146 | 0.0019013 | 0.0051974 | -0.012527 | -0.0058639 | -0.0020166 | 53.4714 | 53.5034 | -69.6671 | 53.7277 | 53.5126 | 53.508 | 53.3936 | 53.6682 | 53.5355 | 8.4961 | -0.37537 | 0.022888 | 122.7631 | 123.0194 | 0.032043 | 77.7878 | 0.054931 | 123.1384 | 122.6852 | 122.9599 | 122.8043 | 122.7951 | 122.7631 | 122.8271 | 122.7997 | 77.7878 | 122.7951 | 122.7631 | 122.7997 | 122.8043 | 122.8271 | -123.1476 | -44.9844
3819.7656 | 123.0515 | -69.4794 | 53.2928 | 0.21721 | 0.012292 | 0.0068147 | 0.0066928 | -0.011672 | -0.0054367 | 0.00097421 | 53.3295 | 53.3524 | -69.8502 | 53.5126 | 53.2974 | 53.2974 | 53.1555 | 53.4576 | 53.3249 | 8.4915 | -0.37079 | 0.059509 | 122.8088 | 122.9919 | 0.004577 | 77.9709 | 0.032043 | 123.1796 | 122.6349 | 122.937 | 122.7768 | 122.8317 | 122.8088 | 122.8043 | 122.7768 | 77.9709 | 122.8317 | 122.8088 | 122.7768 | 122.7768 | 122.8043 | -123.143 | -44.8013
3820.7656 | 123.0331 | -69.1864 | 53.5492 | 0.22484 | 0.010156 | 0.0042511 | 0.0069064 | -0.0097497 | -0.0071457 | -0.0024438 | 53.6041 | 53.6133 | -69.5938 | 53.8055 | 53.5721 | 53.5995 | 53.4348 | 53.7231 | 53.6179 | 8.4915 | -0.40741 | 0.064087 | 122.7905 | 122.9919 | 0.022889 | 77.6779 | 0.068665 | 123.1979 | 122.6212 | 122.9095 | 122.7585 | 122.7997 | 122.7905 | 122.8043 | 122.7859 | 77.6779 | 122.7997 | 122.7905 | 122.7859 | 122.7585 | 122.8043 | -123.143 | -45.0577
3821.7656 | 123.0469 | -69.2093 | 53.5721 | 0.1104 | 0.011651 | 0.0076691 | 0.0069064 | -0.0095361 | -0.0065047 | -0.003512 | 53.5675 | 53.6316 | -69.5663 | 53.7872 | 53.5858 | 53.5995 | 53.5034 | 53.714 | 53.6545 | 8.4824 | -0.35706 | 0.059509 | 122.7768 | 122.9965 | 0.013732 | 77.6917 | 0.082397 | 123.1338 | 122.7127 | 122.9233 | 122.7951 | 122.8409 | 122.7768 | 122.8638 | 122.8088 | 77.6917 | 122.8409 | 122.7768 | 122.8088 | 122.7951 | 122.8638 | -123.1384 | -45.0897
3822.7812 | 123.0057 | -69.5526 | 53.3066 | -0.20241 | 0.010796 | 0.0083099 | 0.0090426 | -0.010177 | -0.0071457 | -0.0032984 | 53.2974 | 53.3066 | -69.8868 | 53.476 | 53.27 | 53.2425 | 53.2745 | 53.4073 | 53.3615 | 8.4961 | -0.33417 | 0 | 122.85 | 123.0286 | -0.036622 | 78.0487 | 0.054931 | 123.1842 | 122.8271 | 122.9599 | 122.8226 | 122.8592 | 122.85 | 122.9141 | 122.7951 | 78.0487 | 122.8592 | 122.85 | 122.7951 | 122.8226 | 122.9141 | -123.1934 | -44.8105
3823.7656 | 123.111 | -69.5023 | 53.2379 | 0.011215 | 0.010156 | 0.0083099 | 0.0060518 | -0.010604 | -0.0073593 | -0.001803 | 53.3066 | 53.3203 | -69.8639 | 53.5446 | 53.3386 | 53.334 | 53.1601 | 53.5126 | 53.3295 | 8.4869 | -0.36163 | 0.082397 | 122.8088 | 123.0469 | 0.10071 | 77.9892 | 0.091553 | 123.1705 | 122.6624 | 123.0148 | 122.8409 | 122.8226 | 122.8088 | 122.8317 | 122.8363 | 77.9892 | 122.8226 | 122.8088 | 122.8363 | 122.8409 | 122.8317 | -123.1018 | -44.751
3824.7656 | 123.0927 | -69.4016 | 53.334 | 0.018845 | 0.012078 | 0.0048921 | 0.0030612 | -0.013381 | -0.0050095 | -0.0039392 | 53.3844 | 53.4256 | -69.7723 | 53.6316 | 53.4485 | 53.4256 | 53.2608 | 53.5995 | 53.4164 | 8.5007 | -0.37079 | 0.091553 | 122.7859 | 123.0331 | 0.11444 | 77.9022 | 0.082398 | 123.1567 | 122.6624 | 123.0011 | 122.85 | 122.8271 | 122.7859 | 122.818 | 122.8271 | 77.9022 | 122.8271 | 122.7859 | 122.8271 | 122.85 | 122.818 | -123.1064 | -44.8334
3825.7812 | 123.0927 | -69.2688 | 53.5355 | 0.049362 | 0.012505 | 0.0085235 | 0.0039156 | -0.011672 | -0.0075729 | -0.0039392 | 53.5355 | 53.5858 | -69.6304 | 53.7781 | 53.5675 | 53.5675 | 53.4485 | 53.7186 | 53.5767 | 8.4915 | -0.36163 | 0.050354 | 122.8043 | 123.0469 | 0.032044 | 77.7603 | 0.041199 | 123.1659 | 122.7173 | 122.9874 | 122.8363 | 122.8546 | 122.8043 | 122.8455 | 122.8363 | 77.7603 | 122.8546 | 122.8043 | 122.8363 | 122.8363 | 122.8455 | -123.1659 | -45.0439
3826.7656 | 123.056 | -68.2709 | 54.5197 | 0.18669 | 0.013146 | 0.0057465 | 0.0045566 | -0.010391 | -0.0052231 | -0.0026574 | 54.5059 | 54.5837 | -68.6691 | 54.7165 | 54.5105 | 54.5059 | 54.4281 | 54.6524 | 54.5654 | 8.4915 | -0.39825 | 0.064087 | 122.7768 | 122.9874 | -0.009155 | 76.7624 | 0.045777 | 123.175 | 122.699 | 122.9233 | 122.7814 | 122.8546 | 122.7768 | 122.8363 | 122.7768 | 76.7624 | 122.8546 | 122.7768 | 122.7768 | 122.7814 | 122.8363 | -123.1888 | -46.0281
3827.7656 | 122.9965 | -68.3121 | 54.5242 | -0.64491 | 0.013146 | 0.0059601 | 0.012674 | -0.011031 | -0.0082137 | -0.0039392 | 54.5197 | 54.5883 | -68.7103 | 54.7394 | 54.4785 | 54.4601 | 54.4785 | 54.6158 | 54.5975 | 8.4915 | -0.39825 | 0.064087 | 122.8317 | 123.0515 | -0.045776 | 76.8036 | 0.073242 | 123.23 | 122.7905 | 122.9279 | 122.7905 | 122.9004 | 122.8317 | 122.9095 | 122.7722 | 76.8036 | 122.9004 | 122.8317 | 122.7722 | 122.7905 | 122.9095 | -123.2346 | -46.0327
3828.7656 | 123.0469 | -69.0353 | 53.7186 | 0.1104 | 0.009942 | 0.0061737 | 0.0039156 | -0.010177 | -0.0050095 | -0.0032984 | 53.7094 | 53.8055 | -69.4382 | 53.9383 | 53.7277 | 53.7781 | 53.6957 | 53.8651 | 53.8284 | 8.4915 | -0.40283 | 0.086975 | 122.7448 | 122.9736 | 0.009155 | 77.5269 | 0.10986 | 123.1476 | 122.731 | 122.9004 | 122.7631 | 122.8409 | 122.7448 | 122.8638 | 122.8134 | 77.5269 | 122.8409 | 122.7448 | 122.8134 | 122.7631 | 122.8638 | -123.1567 | -45.2271
3829.7656 | 123.0331 | -68.8889 | 53.8788 | 0.1638 | 0.011651 | 0.0021149 | 0.0039156 | -0.011672 | -0.0065047 | -0.0037256 | 53.8971 | 53.9612 | -69.2688 | 54.1077 | 53.9291 | 53.9017 | 53.8467 | 54.1351 | 54.007 | 8.4915 | -0.37994 | 0.082398 | 122.786 | 122.9965 | 0.050354 | 77.3804 | 0.12817 | 123.1659 | 122.7356 | 123.024 | 122.818 | 122.85 | 122.786 | 122.8958 | 122.7905 | 77.3804 | 122.85 | 122.786 | 122.7905 | 122.818 | 122.8958 | -123.1476 | -45.3873
3830.7656 | 123.111 | -68.8339 | 53.9062 | -0.072708 | 0.012292 | 0.0046783 | 0.003702 | -0.011672 | -0.0056503 | -0.0020166 | 53.9932 | 53.9612 | -69.2322 | 54.2313 | 54.0161 | 54.0253 | 53.8239 | 54.1809 | 53.9795 | 8.4915 | -0.39826 | 0.054932 | 122.8271 | 123.0652 | 0.10986 | 77.3254 | 0.073242 | 123.2254 | 122.6578 | 123.0148 | 122.85 | 122.7951 | 122.8271 | 122.8134 | 122.8592 | 77.3254 | 122.7951 | 122.8271 | 122.8592 | 122.85 | 122.8134 | -123.1384 | -45.4147
3831.7969 | 122.9691 | -68.4631 | 54.4189 | 0.11803 | 0.015283 | 0.0072419 | 0.010965 | -0.0093225 | -0.0054367 | -0.0041528 | 54.4235 | 54.5609 | -68.7744 | 54.5792 | 54.3182 | 54.3182 | 54.4144 | 54.4601 | 54.483 | 8.4915 | -0.31128 | 0.14191 | 122.8867 | 123.0423 | -0.10071 | 76.9547 | 0.064087 | 123.1979 | 122.8775 | 122.9233 | 122.7814 | 123.024 | 122.8867 | 122.9462 | 122.7814 | 76.9547 | 123.024 | 122.8867 | 122.7814 | 122.7814 | 122.9462 | -123.1934 | -45.9274
3832.8281 | 122.9919 | -69.278 | 53.5355 | 0.087509 | 0.014642 | 0.010232 | 0.012888 | -0.0071863 | -0.0071457 | -0.0032984 | 53.6224 | 53.746 | -69.6121 | 53.7323 | 53.4897 | 53.4805 | 53.54 | 53.5812 | 53.6453 | 8.4915 | -0.33417 | 0.21057 | 122.9004 | 123.0103 | -0.045776 | 77.7695 | 0.10986 | 123.2346 | 122.818 | 122.8592 | 122.7676 | 123.024 | 122.9004 | 122.9233 | 122.7585 | 77.7695 | 123.024 | 122.9004 | 122.7585 | 122.7676 | 122.9233 | -123.1476 | -45.0439
3833.8281 | 122.9736 | -68.3945 | 54.4464 | 0.049362 | 0.014855 | 0.0098053 | 0.010965 | -0.0071863 | -0.0065047 | -0.00458 | 54.5105 | 54.5929 | -68.7057 | 54.6295 | 54.4098 | 54.4052 | 54.4693 | 54.5288 | 54.5654 | 8.4869 | -0.31128 | 0.14649 | 122.905 | 123.024 | -0.036621 | 76.8814 | 0.11902 | 123.2162 | 122.8638 | 122.9233 | 122.8043 | 122.9874 | 122.905 | 122.9599 | 122.7997 | 76.8814 | 122.9874 | 122.905 | 122.7997 | 122.8043 | 122.9599 | -123.1522 | -45.9595
3834.7812 | 122.9645 | -68.4631 | 54.4144 | 0.041733 | 0.015923 | 0.0055329 | 0.013529 | -0.0076135 | -0.0045821 | -0.0037256 | 54.4281 | 54.5609 | -68.7881 | 54.5929 | 54.3777 | 54.3503 | 54.4281 | 54.483 | 54.483 | 8.4869 | -0.32501 | 0.14648 | 122.8912 | 123.056 | -0.036621 | 76.9501 | 0.068664 | 123.2162 | 122.8912 | 122.9462 | 122.8409 | 123.024 | 122.8912 | 122.9462 | 122.8134 | 76.9501 | 123.024 | 122.8912 | 122.8134 | 122.8409 | 122.9462 | -123.2025 | -45.9274
3835.7812 | 123.111 | -68.6142 | 54.1901 | -0.034561 | 0.010369 | 0.0044647 | 0.00092504 | -0.010818 | -0.0067185 | -0.001803 | 54.2633 | 54.2862 | -68.9346 | 54.451 | 54.277 | 54.2725 | 54.1443 | 54.4189 | 54.2816 | 8.4869 | -0.32043 | 0.096131 | 122.8775 | 123.0652 | 0.086976 | 77.1011 | 0.091553 | 123.1979 | 122.7585 | 123.0331 | 122.8912 | 122.9004 | 122.8775 | 122.8958 | 122.8867 | 77.1011 | 122.9004 | 122.8775 | 122.8867 | 122.8912 | 122.8958 | -123.1247 | -45.7031
3837.1719 | 122.9828 | -68.3304 | 54.5334 | -0.17189 | 0.013787 | 0.0044647 | 0.0056246 | -0.011245 | -0.0088547 | -0.0022302 | 54.4327 | 54.6112 | -68.7286 | 54.6341 | 54.4556 | 54.4281 | 54.5929 | 54.5975 | 54.5792 | 8.4915 | -0.39826 | 0.07782 | 122.7631 | 122.9645 | -0.07782 | 76.8219 | 0.045777 | 123.1613 | 122.9233 | 122.9279 | 122.7859 | 122.9416 | 122.7631 | 122.9095 | 122.7585 | 76.8219 | 122.9416 | 122.7631 | 122.7585 | 122.7859 | 122.9095 | -123.262 | -46.0419
3837.875 | 122.9828 | -68.3624 | 54.4876 | -0.24818 | 0.014001 | 0.0066009 | 0.0086154 | -0.0097497 | -0.0050095 | -0.0015894 | 54.4556 | 54.6249 | -68.7286 | 54.6433 | 54.4373 | 54.4144 | 54.5471 | 54.5609 | 54.5517 | 8.4915 | -0.36621 | 0.13733 | 122.818 | 123.0057 | -0.050354 | 76.8539 | 0.064087 | 123.1842 | 122.9095 | 122.9233 | 122.7997 | 122.9874 | 122.818 | 122.9141 | 122.7768 | 76.8539 | 122.9874 | 122.818 | 122.7768 | 122.7997 | 122.9141 | -123.2162 | -45.9961
3838.7969 | 122.9919 | -68.573 | 54.3091 | -0.17952 | 0.015283 | 0.0076691 | 0.0090426 | -0.0078271 | -0.0050095 | -0.0024438 | 54.2496 | 54.4281 | -68.9301 | 54.4464 | 54.2496 | 54.2221 | 54.3549 | 54.3869 | 54.3869 | 8.4824 | -0.35706 | 0.11902 | 122.8226 | 123.0194 | -0.059509 | 77.0554 | 0.07782 | 123.1796 | 122.9279 | 122.9599 | 122.8226 | 123.0011 | 122.8226 | 122.9599 | 122.7951 | 77.0554 | 123.0011 | 122.8226 | 122.7951 | 122.8226 | 122.9599 | -123.2391 | -45.8267
3840.2188 | 123.1247 | -68.3258 | 54.4647 | 0.22484 | 0.012933 | 0.0083099 | 0.0077608 | -0.0082545 | -0.0084273 | -0.0022302 | 54.5334 | 54.5517 | -68.7103 | 54.7256 | 54.5242 | 54.5563 | 54.0939 | 54.5151 | 54.5059 | 8.4869 | -0.38452 | 0.086975 | 122.8592 | 123.0515 | 0.059509 | 76.8127 | 0.041198 | 123.2437 | 122.4197 | 122.8409 | 122.85 | 122.8775 | 122.8592 | 122.8317 | 122.8821 | 76.8127 | 122.8775 | 122.8592 | 122.8821 | 122.85 | 122.8317 | -123.175 | -45.9778
3840.9375 | 123.0469 | -68.3487 | 54.4601 | 0.1638 | 0.01101 | 0.0042511 | 0.0030612 | -0.0099633 | -0.0045821 | -0.0020166 | 54.4556 | 54.5471 | -68.692 | 54.6433 | 54.4693 | 54.4739 | 54.3915 | 54.6249 | 54.5563 | 8.4869 | -0.34332 | 0.086975 | 122.8043 | 122.9919 | 0.009155 | 76.8356 | 0.09613 | 123.1476 | 122.7402 | 122.9736 | 122.818 | 122.8958 | 122.8043 | 122.905 | 122.8226 | 76.8356 | 122.8958 | 122.8043 | 122.8226 | 122.818 | 122.905 | -123.1522 | -45.9732
3841.7656 | 123.0515 | -68.3487 | 54.4601 | 0.1104 | 0.012292 | 0.0033967 | 0.0032748 | -0.011459 | -0.0058639 | -0.0011622 | 54.4281 | 54.5425 | -68.7286 | 54.6295 | 54.4464 | 54.4876 | 54.4189 | 54.6112 | 54.5013 | 8.4824 | -0.37994 | 0.082398 | 122.7768 | 122.9782 | -0.013733 | 76.8311 | 0.041199 | 123.1567 | 122.7676 | 122.9599 | 122.7951 | 122.8912 | 122.7768 | 122.85 | 122.8363 | 76.8311 | 122.8912 | 122.7768 | 122.8363 | 122.7951 | 122.85 | -123.1888 | -45.9778
3842.7656 | 123.0927 | -69.397 | 53.389 | 0.049362 | 0.01336 | 0.010873 | 0.0069064 | -0.011031 | -0.0062911 | -0.0032984 | 53.4027 | 53.4988 | -69.722 | 53.6453 | 53.4348 | 53.4576 | 53.3569 | 53.6224 | 53.4531 | 8.4869 | -0.32501 | 0.10986 | 122.7997 | 123.0423 | 0.045776 | 77.8839 | 0.064087 | 123.1247 | 122.7539 | 123.0194 | 122.8317 | 122.8958 | 122.7997 | 122.85 | 122.8546 | 77.8839 | 122.8958 | 122.7997 | 122.8546 | 122.8317 | 122.85 | -123.111 | -44.902
3843.7812 | 123.111 | -69.31 | 53.4988 | -0.0040434 | 0.010583 | 0.0021149 | 0.0032748 | -0.014236 | -0.0067185 | -0.0020166 | 53.5309 | 53.54 | -69.6533 | 53.7552 | 53.5721 | 53.5538 | 53.3936 | 53.7598 | 53.5309 | 8.4869 | -0.34332 | 0.041199 | 122.8409 | 123.0652 | 0.073243 | 77.7969 | 0.032044 | 123.1842 | 122.7036 | 123.0698 | 122.8821 | 122.85 | 122.8409 | 122.8409 | 122.8638 | 77.7969 | 122.85 | 122.8409 | 122.8638 | 122.8821 | 122.8409 | -123.1522 | -45.0119
3844.7656 | 123.0789 | -69.2963 | 53.5217 | -0.149 | 0.010156 | 0.0051057 | 0.0064792 | -0.011031 | -0.0071457 | -0.0037256 | 53.54 | 53.5309 | -69.6625 | 53.7415 | 53.5263 | 53.5355 | 53.4485 | 53.7094 | 53.5629 | 8.4915 | -0.36621 | 0.009155 | 122.8363 | 123.0377 | 0.004577 | 77.7878 | 0.041198 | 123.2025 | 122.7448 | 123.0057 | 122.8226 | 122.8271 | 122.8363 | 122.8592 | 122.8317 | 77.7878 | 122.8271 | 122.8363 | 122.8317 | 122.8226 | 122.8592 | -123.1842 | -45.0302
3845.7656 | 123.0652 | -69.1864 | 53.6179 | -0.149 | 0.0084466 | 0.0021149 | 0.0060518 | -0.011886 | -0.0088547 | -0.0030848 | 53.6591 | 53.6819 | -69.5663 | 53.8834 | 53.6545 | 53.6545 | 53.5904 | 53.833 | 53.6911 | 8.4915 | -0.37994 | 0.064087 | 122.8455 | 123.0698 | 0.036621 | 77.6779 | 0.073242 | 123.2254 | 122.7768 | 123.0194 | 122.8409 | 122.8683 | 122.8455 | 122.8775 | 122.8409 | 77.6779 | 122.8683 | 122.8455 | 122.8409 | 122.8409 | 122.8775 | -123.1842 | -45.1263
3846.7656 | 123.0927 | -68.1793 | 54.6249 | -0.149 | 0.010156 | 0.0046783 | 0.0058382 | -0.012954 | -0.0054367 | -0.0030848 | 54.6433 | 54.6707 | -68.573 | 54.8767 | 54.6524 | 54.6433 | 54.5975 | 54.8401 | 54.6799 | 8.4961 | -0.39368 | 0.045776 | 122.8226 | 123.056 | 0.027466 | 76.6754 | 0.054932 | 123.2162 | 122.7768 | 123.0194 | 122.8317 | 122.85 | 122.8226 | 122.8592 | 122.8226 | 76.6754 | 122.85 | 122.8226 | 122.8226 | 122.8317 | 122.8592 | -123.1979 | -46.1288
3847.7656 | 123.0698 | -68.1839 | 54.6112 | -0.034561 | 0.011437 | 0.0085235 | 0.0049838 | -0.01274 | -0.0052231 | -0.0028712 | 54.6387 | 54.6753 | -68.5226 | 54.863 | 54.6661 | 54.6753 | 54.57 | 54.8309 | 54.6936 | 8.4869 | -0.33875 | 0.064087 | 122.8226 | 123.0469 | 0.054932 | 76.6708 | 0.082398 | 123.1613 | 122.7539 | 123.0148 | 122.85 | 122.8592 | 122.8226 | 122.8775 | 122.8592 | 76.6708 | 122.8592 | 122.8226 | 122.8592 | 122.85 | 122.8775 | -123.1338 | -46.1243
3848.7812 | 123.0331 | -68.161 | 54.6433 | -0.19478 | 0.011651 | 0.0010467 | 0.0064792 | -0.013809 | -0.0050095 | -0.0026574 | 54.6844 | 54.7211 | -68.5089 | 54.8721 | 54.6433 | 54.6433 | 54.6478 | 54.8264 | 54.6982 | 8.4915 | -0.3479 | 0.077819 | 122.8455 | 123.0331 | 0 | 76.6525 | 0.054931 | 123.1934 | 122.8088 | 122.9874 | 122.8043 | 122.8821 | 122.8455 | 122.8592 | 122.8043 | 76.6525 | 122.8821 | 122.8455 | 122.8043 | 122.8043 | 122.8592 | -123.1522 | -46.1517
3849.7656 | 123.1293 | -68.1839 | 54.6158 | -0.065079 | 0.010369 | 0.0068147 | 0.0058382 | -0.013381 | -0.0045821 | -0.0020166 | 54.6616 | 54.6616 | -68.5684 | 54.9179 | 54.7073 | 54.6936 | 54.5151 | 54.895 | 54.6661 | 8.5007 | -0.38452 | 0.045776 | 122.8455 | 123.1018 | 0.091552 | 76.6846 | 0.050354 | 123.23 | 122.699 | 123.0789 | 122.8912 | 122.8455 | 122.8455 | 122.85 | 122.8775 | 76.6846 | 122.8455 | 122.8455 | 122.8775 | 122.8912 | 122.85 | -123.1842 | -46.1151
3850.7812 | 123.0835 | -68.3578 | 54.4601 | 0.011215 | 0.013574 | 0.0033967 | 0.0069064 | -0.0121 | -0.0060775 | -0.0030848 | 54.5059 | 54.5105 | -68.7103 | 54.7073 | 54.4922 | 54.4922 | 54.3915 | 54.689 | 54.5059 | 8.4915 | -0.35248 | 0.050354 | 122.8638 | 123.0652 | 0.032043 | 76.8494 | 0.045776 | 123.2162 | 122.7493 | 123.0469 | 122.85 | 122.8683 | 122.8638 | 122.8638 | 122.85 | 76.8494 | 122.8683 | 122.8638 | 122.85 | 122.85 | 122.8638 | -123.1705 | -45.9686
3851.7656 | 123.0103 | -68.3807 | 54.4785 | -0.18715 | 0.013146 | 0.0025421 | 0.0064792 | -0.011459 | -0.0065047 | -0.0013758 | 54.4464 | 54.5563 | -68.7241 | 54.6524 | 54.4189 | 54.4144 | 54.5609 | 54.5792 | 54.5792 | 8.4915 | -0.34332 | 0.077819 | 122.8271 | 123.0331 | -0.05951 | 76.8723 | 0.10071 | 123.1705 | 122.9416 | 122.9599 | 122.7997 | 122.937 | 122.8271 | 122.9599 | 122.7951 | 76.8723 | 122.937 | 122.8271 | 122.7951 | 122.7997 | 122.9599 | -123.2025 | -45.9869
3852.7656 | 122.9919 | -68.3441 | 54.5425 | -0.21767 | 0.013574 | 0.0029693 | 0.008829 | -0.013381 | -0.0082137 | -0.001803 | 54.4647 | 54.6112 | -68.7103 | 54.6753 | 54.451 | 54.4327 | 54.5975 | 54.6204 | 54.6204 | 8.4915 | -0.36621 | 0.068664 | 122.8088 | 123.0194 | -0.091553 | 76.8356 | 0.077819 | 123.175 | 122.9416 | 122.9645 | 122.7951 | 122.9553 | 122.8088 | 122.9645 | 122.7768 | 76.8356 | 122.9553 | 122.8088 | 122.7768 | 122.7951 | 122.9645 | -123.2529 | -46.051
3853.7656 | 123.0423 | -68.2938 | 54.5563 | -0.2253 | 0.012719 | 0.0051057 | 0.0092562 | -0.010818 | -0.0052231 | -0.005221 | 54.4556 | 54.6204 | -68.7332 | 54.6799 | 54.4693 | 54.4235 | 54.5837 | 54.6158 | 54.6295 | 8.4961 | -0.43945 | 0.064087 | 122.7493 | 122.9736 | -0.086975 | 76.7899 | 0.073243 | 123.1888 | 122.8775 | 122.9095 | 122.7631 | 122.9141 | 122.7493 | 122.9233 | 122.7173 | 76.7899 | 122.9141 | 122.7493 | 122.7173 | 122.7631 | 122.9233 | -123.2895 | -46.0602
3854.7656 | 123.1064 | -68.3258 | 54.4647 | -0.13374 | 0.010156 | 0.00019226 | 0.0034884 | -0.011031 | -0.0067185 | -0.0050074 | 54.5471 | 54.5517 | -68.6691 | 55.0323 | 54.7852 | 54.4189 | 54.3365 | 54.6616 | 54.5471 | 8.4869 | -0.34332 | 0.086975 | 122.8729 | 123.3582 | 0.32043 | 76.8127 | 0.082397 | 123.2162 | 122.6624 | 122.9874 | 123.111 | 122.8775 | 122.8729 | 122.8729 | 122.7448 | 76.8127 | 122.8775 | 122.8729 | 122.7448 | 123.111 | 122.8729 | -123.1338 | -45.9778
3855.7656 | 123.0698 | -68.3578 | 54.451 | -0.13374 | 0.012933 | 0.0057465 | 0.005411 | -0.012954 | -0.0052231 | -0.0024438 | 54.4922 | 54.5242 | -68.7195 | 54.6982 | 54.4968 | 54.483 | 54.4464 | 54.6616 | 54.5334 | 8.4869 | -0.36163 | 0.073242 | 122.85 | 123.056 | 0.045776 | 76.8448 | 0.082397 | 123.2117 | 122.8043 | 123.0194 | 122.8546 | 122.8821 | 122.85 | 122.8912 | 122.8409 | 76.8448 | 122.8821 | 122.85 | 122.8409 | 122.8546 | 122.8912 | -123.1705 | -45.9641
3856.7656 | 123.0698 | -68.3716 | 54.5013 | -0.17952 | 0.011651 | 0.0044647 | 0.0062656 | -0.011886 | -0.0067185 | -0.0032984 | 54.4968 | 54.5425 | -68.7103 | 54.7211 | 54.4922 | 54.4922 | 54.4601 | 54.6524 | 54.5471 | 8.4869 | -0.33875 | 0.041199 | 122.8683 | 123.0927 | -0.009156 | 76.8585 | 0.045776 | 123.2071 | 122.8317 | 123.024 | 122.8638 | 122.9141 | 122.8683 | 122.9187 | 122.8638 | 76.8585 | 122.9141 | 122.8683 | 122.8638 | 122.8638 | 122.9187 | -123.2117 | -46.0144
3857.7812 | 122.9919 | -68.3716 | 54.5059 | -0.17952 | 0.015283 | 0.0061737 | 0.0096834 | -0.010604 | -0.0071457 | -0.0050074 | 54.4556 | 54.6066 | -68.7286 | 54.6616 | 54.4601 | 54.4373 | 54.5883 | 54.6066 | 54.6112 | 8.4915 | -0.35706 | 0.10071 | 122.8271 | 123.0331 | -0.045776 | 76.8631 | 0.10529 | 123.1842 | 122.9599 | 122.9782 | 122.8317 | 122.9782 | 122.8271 | 122.9828 | 122.8088 | 76.8631 | 122.9782 | 122.8271 | 122.8088 | 122.8317 | 122.9828 | -123.2346 | -46.0144
3858.7656 | 123.0606 | -68.5455 | 54.2908 | -0.11848 | 0.01336 | 0.0095917 | 0.010538 | -0.012313 | -0.0060775 | -0.0037256 | 54.2953 | 54.4281 | -68.9392 | 54.4876 | 54.2725 | 54.2496 | 54.3182 | 54.4144 | 54.3823 | 8.4915 | -0.39368 | 0.13733 | 122.8409 | 123.0331 | -0.01831 | 77.037 | 0.091553 | 123.2346 | 122.8638 | 122.9599 | 122.818 | 122.9736 | 122.8409 | 122.9279 | 122.7951 | 77.037 | 122.9736 | 122.8409 | 122.7951 | 122.818 | 122.9279 | -123.23 | -45.7993
3859.7812 | 123.0423 | -68.454 | 54.4052 | -0.6678 | 0.013574 | 0.010446 | 0.010752 | -0.0086817 | -0.0090683 | -0.0032984 | 54.4647 | 54.5563 | -68.7881 | 54.6478 | 54.3961 | 54.3961 | 54.3961 | 54.5151 | 54.5013 | 8.4869 | -0.33417 | 0.15106 | 122.9187 | 123.1018 | -0.009155 | 76.9409 | 0.096131 | 123.2529 | 122.85 | 122.9691 | 122.85 | 123.0103 | 122.9187 | 122.9553 | 122.85 | 76.9409 | 123.0103 | 122.9187 | 122.85 | 122.85 | 122.9553 | -123.1934 | -45.9183
3860.7656 | 123.0011 | -69.3329 | 53.5263 | -0.18715 | 0.012933 | 0.0040375 | 0.0058382 | -0.0097497 | -0.0062911 | -0.0032984 | 53.476 | 53.6224 | -69.6945 | 53.6591 | 53.5126 | 53.4668 | 53.5858 | 53.6224 | 53.6087 | 8.4961 | -0.36163 | 0.096131 | 122.8088 | 122.9919 | -0.013733 | 77.829 | 0.082398 | 123.1705 | 122.9187 | 122.9553 | 122.8455 | 122.9553 | 122.8088 | 122.9416 | 122.7997 | 77.829 | 122.9553 | 122.8088 | 122.7997 | 122.8455 | 122.9416 | -123.2208 | -45.0302
3861.7656 | 123.0057 | -69.4061 | 53.4897 | -0.16426 | 0.012292 | 0.0042511 | 0.0049838 | -0.0097497 | -0.0086411 | -0.0030848 | 53.4164 | 53.5675 | -69.7723 | 53.5995 | 53.4119 | 53.3798 | 53.5538 | 53.5492 | 53.5629 | 8.4869 | -0.36621 | 0.07782 | 122.8226 | 123.0057 | -0.07782 | 77.8931 | 0.073242 | 123.1888 | 122.9599 | 122.9553 | 122.818 | 122.9736 | 122.8226 | 122.9691 | 122.7859 | 77.8931 | 122.9736 | 122.8226 | 122.7859 | 122.818 | 122.9691 | -123.262 | -45.0027
3862.7656 | 123.0194 | -69.3512 | 53.5309 | -0.13374 | 0.011437 | 0.0074555 | 0.0079744 | -0.0091089 | -0.0062911 | -0.0024438 | 53.4851 | 53.6591 | -69.7128 | 53.6774 | 53.4714 | 53.4393 | 53.5904 | 53.5995 | 53.627 | 8.4869 | -0.36163 | 0.12817 | 122.8363 | 123.0286 | -0.059509 | 77.8381 | 0.09613 | 123.1979 | 122.9416 | 122.9507 | 122.8226 | 123.0103 | 122.8363 | 122.9782 | 122.7905 | 77.8381 | 123.0103 | 122.8363 | 122.7905 | 122.8226 | 122.9782 | -123.2437 | -45.0439
3863.7812 | 123.0331 | -69.3787 | 53.5126 | 0.12566 | 0.013787 | 0.0087373 | 0.010965 | -0.0059045 | -0.0075729 | -0.0039392 | 53.5995 | 53.6819 | -69.6899 | 53.7094 | 53.476 | 53.4576 | 53.4943 | 53.6041 | 53.5675 | 8.4869 | -0.31128 | 0.16937 | 122.9782 | 123.0881 | -0.036621 | 77.8656 | 0.054932 | 123.2895 | 122.8729 | 122.9828 | 122.8546 | 123.0606 | 122.9782 | 122.9462 | 122.8363 | 77.8656 | 123.0606 | 122.9782 | 122.8363 | 122.8546 | 122.9462 | -123.2025 | -45.0256
3864.7812 | 123.0423 | -69.4382 | 53.4531 | -0.087967 | 0.015496 | 0.0095917 | 0.010538 | -0.0056909 | -0.0080001 | -0.0020166 | 53.4576 | 53.5492 | -69.8044 | 53.6087 | 53.4119 | 53.4027 | 53.4256 | 53.5538 | 53.5309 | 8.4915 | -0.36621 | 0.09613 | 122.8958 | 123.0469 | -0.041199 | 77.9297 | 0.07782 | 123.262 | 122.8638 | 122.9919 | 122.85 | 122.9874 | 122.8958 | 122.9691 | 122.8409 | 77.9297 | 122.9874 | 122.8958 | 122.8409 | 122.85 | 122.9691 | -123.2574 | -44.9615
3865.7656 | 123.0194 | -68.7469 | 54.1122 | 0.087509 | 0.012078 | 0.0059601 | 0.012033 | -0.0046229 | -0.0041549 | -9.3992e-05 | 54.1214 | 54.2953 | -69.0903 | 54.2725 | 54.0573 | 54.071 | 54.1443 | 54.1855 | 54.2404 | 8.4961 | -0.34332 | 0.18311 | 122.8683 | 123.0194 | -0.054932 | 77.243 | 0.12817 | 123.2117 | 122.8912 | 122.9324 | 122.8043 | 123.0423 | 122.8683 | 122.9874 | 122.818 | 77.243 | 123.0423 | 122.8683 | 122.818 | 122.8043 | 122.9874 | -123.2025 | -45.6161
3866.7656 | 122.9919 | -69.31 | 53.5675 | 0.064621 | 0.01571 | 0.0091645 | 0.010111 | -0.0076135 | -0.0043685 | -0.001803 | 53.5721 | 53.7323 | -69.6533 | 53.7048 | 53.5172 | 53.4805 | 53.6041 | 53.6041 | 53.6636 | 8.4869 | -0.34332 | 0.1648 | 122.8821 | 123.0148 | -0.050354 | 77.7969 | 0.09613 | 123.2254 | 122.9141 | 122.9141 | 122.8271 | 123.0423 | 122.8821 | 122.9736 | 122.7905 | 77.7969 | 123.0423 | 122.8821 | 122.7905 | 122.8271 | 122.9736 | -123.2208 | -45.0806
3867.7656 | 123.0469 | -69.2963 | 53.5812 | -0.080337 | 0.014428 | 0.0031831 | 0.011392 | -0.0061181 | -0.0065047 | -0.0013758 | 53.627 | 53.7689 | -69.6167 | 53.7735 | 53.5904 | 53.5721 | 53.6041 | 53.7277 | 53.6865 | 8.4961 | -0.32043 | 0.18768 | 122.9233 | 123.0698 | 0.009155 | 77.7924 | 0.10529 | 123.2437 | 122.9004 | 123.024 | 122.8867 | 123.0652 | 122.9233 | 122.9828 | 122.8683 | 77.7924 | 123.0652 | 122.9233 | 122.8683 | 122.8867 | 122.9828 | -123.1979 | -45.0851
3868.7656 | 123.0835 | -69.0582 | 53.7277 | -0.095596 | 0.015283 | 0.0091645 | 0.0086154 | -0.0046229 | -0.0052231 | -0.0013758 | 53.8513 | 53.9841 | -69.4427 | 54.0207 | 53.7643 | 53.7964 | 53.8696 | 54.0482 | 53.9749 | 8.4869 | -0.38452 | 0.25635 | 122.9095 | 123.0789 | 0.036621 | 77.5452 | 0.24719 | 123.2941 | 122.9279 | 123.1064 | 122.8226 | 123.0423 | 122.9095 | 123.0331 | 122.8546 | 77.5452 | 123.0423 | 122.9095 | 122.8546 | 122.8226 | 123.0331 | -123.1705 | -45.2408
3869.7656 | 123.0194 | -68.1519 | 54.7119 | 0.034104 | 0.015069 | 0.01066 | 0.010538 | -0.0069727 | -0.0080001 | -0.0011622 | 54.7531 | 54.8996 | -68.4631 | 54.8721 | 54.7073 | 54.6707 | 54.7394 | 54.8126 | 54.8309 | 8.4869 | -0.31128 | 0.18768 | 122.905 | 123.024 | -0.004578 | 76.6388 | 0.11902 | 123.2162 | 122.8912 | 122.9645 | 122.8592 | 123.0515 | 122.905 | 122.9828 | 122.8226 | 76.6388 | 123.0515 | 122.905 | 122.8226 | 122.8592 | 122.9828 | -123.175 | -46.225
3870.7656 | 123.0286 | -68.1564 | 54.7165 | 0.041733 | 0.014642 | 0.0072419 | 0.010538 | -0.0054773 | -0.0062911 | -0.00052119 | 54.7302 | 54.8767 | -68.4952 | 54.8676 | 54.6707 | 54.6661 | 54.744 | 54.7989 | 54.8309 | 8.4961 | -0.33874 | 0.16022 | 122.8867 | 123.024 | -0.045777 | 76.6525 | 0.11444 | 123.2254 | 122.9004 | 122.9553 | 122.8271 | 123.0331 | 122.8867 | 122.9874 | 122.8226 | 76.6525 | 123.0331 | 122.8867 | 122.8226 | 122.8271 | 122.9874 | -123.2117 | -46.2204
3871.7812 | 123.0103 | -68.1839 | 54.6936 | 0.14092 | 0.014428 | 0.0072419 | 0.008829 | -0.0039819 | -0.0050095 | -0.0015894 | 54.6661 | 54.8859 | -68.5547 | 54.8126 | 54.6112 | 54.6112 | 54.7623 | 54.7256 | 54.7897 | 8.4824 | -0.37079 | 0.19226 | 122.85 | 122.9965 | -0.082398 | 76.6663 | 0.09613 | 123.2208 | 122.9462 | 122.9095 | 122.7951 | 123.0698 | 122.85 | 122.9736 | 122.7951 | 76.6663 | 123.0698 | 122.85 | 122.7951 | 122.7951 | 122.9736 | -123.2483 | -46.2112
3872.7656 | 123.0835 | -68.1564 | 54.6753 | 0.25536 | 0.015283 | 0.010446 | 0.0084018 | -0.0044091 | -0.0060775 | -0.0043664 | 54.6982 | 54.863 | -68.5318 | 54.8584 | 54.6844 | 54.6844 | 54.6524 | 54.7989 | 54.7852 | 8.4915 | -0.37537 | 0.18768 | 122.8546 | 123.0148 | 0.009155 | 76.6479 | 0.10986 | 123.23 | 122.8088 | 122.9553 | 122.8409 | 123.0194 | 122.8546 | 122.9416 | 122.8409 | 76.6479 | 123.0194 | 122.8546 | 122.8409 | 122.8409 | 122.9416 | -123.2071 | -46.1838
3873.7656 | 123.111 | -68.1564 | 54.6524 | 0.25536 | 0.013787 | 0.0051057 | 0.0077608 | -0.0082545 | -0.0067185 | -0.0020166 | 54.6982 | 54.8538 | -68.5226 | 54.8767 | 54.6799 | 54.6844 | 54.6158 | 54.8218 | 54.7623 | 8.4869 | -0.36621 | 0.20142 | 122.8546 | 123.0331 | 0.027466 | 76.6434 | 0.10986 | 123.2208 | 122.7722 | 122.9782 | 122.8363 | 123.0103 | 122.8546 | 122.9187 | 122.8409 | 76.6434 | 123.0103 | 122.8546 | 122.8409 | 122.8363 | 122.9187 | -123.175 | -46.1655
3874.7656 | 122.9828 | -68.1839 | 54.7302 | 0.14092 | 0.016992 | 0.010019 | 0.010111 | -0.0073999 | -0.0075729 | -0.00094839 | 54.7119 | 54.8813 | -68.4952 | 54.8401 | 54.6249 | 54.6112 | 54.744 | 54.7668 | 54.8126 | 8.4961 | -0.31128 | 0.15106 | 122.8958 | 123.024 | -0.10529 | 76.68 | 0.082397 | 123.2071 | 122.9279 | 122.9507 | 122.8088 | 123.0652 | 122.8958 | 122.9965 | 122.7951 | 76.68 | 123.0652 | 122.8958 | 122.7951 | 122.8088 | 122.9965 | -123.2254 | -46.2341
3875.7656 | 122.9782 | -68.1885 | 54.689 | 0.11803 | 0.015923 | 0.010873 | 0.0084018 | -0.0063317 | -0.0075729 | -0.0011622 | 54.6936 | 54.895 | -68.5181 | 54.8172 | 54.5975 | 54.6295 | 54.7577 | 54.7623 | 54.8355 | 8.4869 | -0.32959 | 0.20599 | 122.8821 | 123.0057 | -0.091553 | 76.6754 | 0.14648 | 123.2117 | 122.9462 | 122.9507 | 122.786 | 123.0835 | 122.8821 | 123.024 | 122.818 | 76.6754 | 123.0835 | 122.8821 | 122.818 | 122.786 | 123.024 | -123.2071 | -46.2021
3876.7656 | 123.0286 | -68.1564 | 54.6982 | 0.1638 | 0.01571 | 0.0089509 | 0.0079744 | -0.0046229 | -0.0054367 | -0.0022302 | 54.6753 | 54.895 | -68.5364 | 54.8218 | 54.6387 | 54.6433 | 54.7119 | 54.7485 | 54.8172 | 8.4824 | -0.37994 | 0.19684 | 122.8317 | 122.9782 | -0.059509 | 76.6388 | 0.11902 | 123.2117 | 122.8683 | 122.905 | 122.7951 | 123.0515 | 122.8317 | 122.9736 | 122.7997 | 76.6388 | 123.0515 | 122.8317 | 122.7997 | 122.7951 | 122.9736 | -123.2346 | -46.2158
3877.7656 | 123.0377 | -68.1519 | 54.7256 | 0.20195 | 0.016137 | 0.0061737 | 0.010324 | -0.0056909 | -0.0060775 | -0.001803 | 54.6982 | 54.8584 | -68.4814 | 54.8584 | 54.6524 | 54.6753 | 54.7211 | 54.7943 | 54.8355 | 8.4869 | -0.32959 | 0.13275 | 122.85 | 123.0103 | -0.073242 | 76.6388 | 0.10986 | 123.1796 | 122.8729 | 122.9462 | 122.8043 | 123.0103 | 122.85 | 122.9874 | 122.8271 | 76.6388 | 123.0103 | 122.85 | 122.8271 | 122.8043 | 122.9874 | -123.2071 | -46.2387
3878.7656 | 123.1247 | -68.1244 | 54.689 | 0.22484 | 0.014428 | 0.0080963 | 0.002634 | -0.0050501 | -0.0050095 | -0.0020166 | 54.7531 | 54.8035 | -68.5226 | 54.9042 | 54.7302 | 54.7485 | 54.5792 | 54.895 | 54.7668 | 8.4869 | -0.39825 | 0.11444 | 122.8775 | 123.0286 | 0.041199 | 76.6113 | 0.07782 | 123.2758 | 122.7036 | 123.0194 | 122.8546 | 122.9279 | 122.8775 | 122.8912 | 122.8729 | 76.6113 | 122.9279 | 122.8775 | 122.8729 | 122.8546 | 122.8912 | -123.2117 | -46.2021
3879.7656 | 123.0927 | -68.1564 | 54.6616 | 0.20958 | 0.015069 | 0.0074555 | 0.0047702 | -0.0080407 | -0.0056503 | -0.0011622 | 54.7394 | 54.776 | -68.4769 | 54.9042 | 54.7211 | 54.7485 | 54.5609 | 54.8767 | 54.7577 | 8.4869 | -0.32043 | 0.11444 | 122.8958 | 123.0606 | 0.059509 | 76.6434 | 0.09613 | 123.2162 | 122.7173 | 123.0331 | 122.8775 | 122.9324 | 122.8958 | 122.9141 | 122.905 | 76.6434 | 122.9324 | 122.8958 | 122.905 | 122.8775 | 122.9141 | -123.1384 | -46.1746
3880.7656 | 123.0972 | -68.1015 | 54.6844 | 0.21721 | 0.013146 | 0.0076691 | 0.0064792 | -0.0078271 | -0.0028731 | -0.00094839 | 54.7485 | 54.8126 | -68.4769 | 54.9225 | 54.7073 | 54.7394 | 54.6066 | 54.8767 | 54.7852 | 8.4869 | -0.37537 | 0.12817 | 122.85 | 123.024 | 0.022888 | 76.5884 | 0.10071 | 123.2254 | 122.7081 | 122.9782 | 122.8088 | 122.9141 | 122.85 | 122.8867 | 122.8409 | 76.5884 | 122.9141 | 122.85 | 122.8409 | 122.8088 | 122.8867 | -123.1613 | -46.1975
3881.7656 | 123.0789 | -68.7057 | 54.1214 | 0.26299 | 0.014214 | 0.0070283 | 0.0098972 | -0.0080407 | -0.0058639 | -0.003512 | 54.1077 | 54.2496 | -69.1223 | 54.3091 | 54.0939 | 54.1122 | 54.0756 | 54.2404 | 54.213 | 8.4824 | -0.41656 | 0.12817 | 122.8134 | 123.0148 | -0.027466 | 77.1881 | 0.091553 | 123.23 | 122.7814 | 122.9462 | 122.7997 | 122.9553 | 122.8134 | 122.9187 | 122.818 | 77.1881 | 122.9553 | 122.8134 | 122.818 | 122.7997 | 122.9187 | -123.2437 | -45.639
3882.7656 | 123.1201 | -68.2068 | 54.6433 | 0.25536 | 0.016137 | 0.0066009 | 0.0086154 | -0.0082545 | -0.0050095 | -9.3992e-05 | 54.6844 | 54.7852 | -68.5501 | 54.8447 | 54.6341 | 54.6478 | 54.5654 | 54.7943 | 54.7531 | 8.4915 | -0.34332 | 0.14191 | 122.8912 | 123.0515 | -0.009156 | 76.6983 | 0.10986 | 123.2346 | 122.7722 | 123.0011 | 122.8409 | 122.9919 | 122.8912 | 122.9599 | 122.8546 | 76.6983 | 122.9919 | 122.8912 | 122.8546 | 122.8409 | 122.9599 | -123.1934 | -46.1517
3883.7656 | 123.143 | -68.1839 | 54.6066 | 0.27061 | 0.014214 | 0.0066009 | 0.0066928 | -0.0082545 | -0.0058639 | 0.00076041 | 54.7028 | 54.7394 | -68.5364 | 54.689 | 54.5609 | 54.744 | 54.5563 | 54.8355 | 54.6982 | 8.4869 | -0.35248 | 0.13275 | 122.8867 | 122.8729 | -0.045776 | 76.6708 | 0.091553 | 123.2391 | 122.7402 | 123.0194 | 122.7448 | 122.9233 | 122.8867 | 122.8821 | 122.9279 | 76.6708 | 122.9233 | 122.8867 | 122.9279 | 122.7448 | 122.8821 | -123.143 | -46.1197
3884.7812 | 123.1338 | -68.5318 | 54.2404 | 0.20195 | 0.012505 | 0.0061737 | 0.0045566 | -0.0080407 | -0.0052231 | -0.0022302 | 54.2953 | 54.332 | -68.9621 | 54.4876 | 54.2862 | 54.2862 | 54.1351 | 54.4281 | 54.3365 | 8.4915 | -0.4303 | 0.091553 | 122.8271 | 123.0194 | 0.045777 | 77.0233 | 0.096131 | 123.2574 | 122.6669 | 122.9599 | 122.818 | 122.8638 | 122.8271 | 122.8683 | 122.818 | 77.0233 | 122.8638 | 122.8271 | 122.818 | 122.818 | 122.8683 | -123.2025 | -45.7489
3885.7656 | 123.1247 | -68.3304 | 54.5517 | -1.5986 | 0.010369 | 0.0063873 | 0.003702 | -0.012527 | -0.0058639 | -0.0026574 | 54.5288 | 54.6249 | -68.6462 | 54.7256 | 54.5013 | 54.5151 | 54.4601 | 54.689 | 54.5883 | 8.4824 | -0.31586 | 0.073242 | 122.8592 | 123.056 | -0.050354 | 76.8127 | 0.036621 | 123.175 | 122.7905 | 123.0194 | 122.8317 | 122.9553 | 122.8592 | 122.9187 | 122.8455 | 76.8127 | 122.9553 | 122.8592 | 122.8455 | 122.8317 | 122.9187 | -123.1979 | -46.0693
3886.7656 | 123.1018 | -68.1244 | 54.6936 | -0.19478 | 0.011865 | 0.0036103 | 0.0024202 | -0.012313 | -0.0065047 | -0.0026574 | 54.7028 | 54.7668 | -68.5089 | 54.9133 | 54.7348 | 54.7119 | 54.6478 | 54.8721 | 54.7852 | 8.4824 | -0.38452 | 0.073242 | 122.8271 | 123.0377 | 0.041198 | 76.6068 | 0.091552 | 123.2117 | 122.7722 | 122.9965 | 122.8592 | 122.8912 | 122.8271 | 122.9095 | 122.8363 | 76.6068 | 122.8912 | 122.8271 | 122.8363 | 122.8592 | 122.9095 | -123.2025 | -46.2112
3887.7656 | 123.1293 | -68.1519 | 54.6616 | 0.049362 | 0.011437 | 0.0048921 | 0.0047702 | -0.011031 | -0.0056503 | -0.00094839 | 54.657 | 54.776 | -68.5364 | 54.8767 | 54.689 | 54.6799 | 54.6112 | 54.8584 | 54.7531 | 8.4961 | -0.38452 | 0.11444 | 122.8088 | 123.0286 | 0.027466 | 76.6479 | 0.091553 | 123.1934 | 122.7631 | 123.0103 | 122.8409 | 122.9279 | 122.8088 | 122.905 | 122.8317 | 76.6479 | 122.9279 | 122.8088 | 122.8317 | 122.8409 | 122.905 | -123.1979 | -46.1655
3888.7656 | 123.0972 | -68.1473 | 54.6249 | 0.19432 | 0.011437 | 0.0055329 | 0.0066928 | -0.010391 | -0.0084273 | -0.001803 | 54.7165 | 54.7119 | -68.5684 | 54.8996 | 54.6753 | 54.6982 | 54.5334 | 54.8355 | 54.6936 | 8.4961 | -0.42114 | 0.086975 | 122.8638 | 123.0469 | 0.050354 | 76.6434 | 0.068665 | 123.2849 | 122.6807 | 122.9828 | 122.8226 | 122.8592 | 122.8638 | 122.8409 | 122.8455 | 76.6434 | 122.8592 | 122.8638 | 122.8455 | 122.8226 | 122.8409 | -123.1934 | -46.1288
3889.7656 | 123.111 | -68.161 | 54.6387 | 0.23247 | 0.011224 | 0.0070283 | 0.0056246 | -0.010604 | -0.0058639 | -0.0022302 | 54.7073 | 54.7256 | -68.5501 | 54.8996 | 54.6982 | 54.6936 | 54.538 | 54.8264 | 54.7028 | 8.4915 | -0.3891 | 0.086975 | 122.8683 | 123.0606 | 0.059509 | 76.6525 | 0.064087 | 123.2574 | 122.699 | 122.9874 | 122.8592 | 122.8867 | 122.8683 | 122.8638 | 122.8546 | 76.6525 | 122.8867 | 122.8683 | 122.8546 | 122.8592 | 122.8638 | -123.1888 | -46.1472
3890.7656 | 123.0972 | -68.1747 | 54.6799 | 0.14092 | 0.010796 | 0.0074555 | 0.004343 | -0.011245 | -0.0052231 | -0.0030848 | 54.6616 | 54.7485 | -68.5455 | 54.8813 | 54.6844 | 54.6707 | 54.6066 | 54.8355 | 54.7394 | 8.4869 | -0.37079 | 0.068664 | 122.8363 | 123.056 | 0.004577 | 76.6617 | 0.059509 | 123.2071 | 122.7814 | 123.0103 | 122.8592 | 122.9233 | 122.8363 | 122.9141 | 122.8455 | 76.6617 | 122.9233 | 122.8363 | 122.8455 | 122.8592 | 122.9141 | -123.2254 | -46.1929
3891.7812 | 123.1018 | -68.1519 | 54.6707 | 0.1104 | 0.012505 | 0.0036103 | 0.002634 | -0.01274 | -0.0069321 | -0.0011622 | 54.689 | 54.744 | -68.5547 | 54.9133 | 54.7119 | 54.6844 | 54.5975 | 54.8767 | 54.744 | 8.4915 | -0.40283 | 0.073243 | 122.8409 | 123.0652 | 0.041199 | 76.6434 | 0.073243 | 123.2437 | 122.7493 | 123.0286 | 122.8638 | 122.8958 | 122.8409 | 122.8958 | 122.8363 | 76.6434 | 122.8958 | 122.8409 | 122.8363 | 122.8638 | 122.8958 | -123.2254 | -46.1792
3892.7656 | 123.1018 | -68.1335 | 54.6844 | -0.11848 | 0.010583 | 0.0040375 | 0.004343 | -0.012313 | -0.0047957 | -0.0030848 | 54.7714 | 54.7531 | -68.4998 | 54.9637 | 54.7256 | 54.8859 | 54.8035 | 54.6387 | 54.7989 | 8.4961 | -0.36621 | 0.068665 | 122.905 | 123.0972 | 0.041199 | 76.6296 | 0.11444 | 123.2712 | 122.937 | 122.7722 | 122.8592 | 122.8867 | 122.905 | 122.9324 | 123.0194 | 76.6296 | 122.8867 | 122.905 | 123.0194 | 122.8592 | 122.9324 | -123.1842 | -46.1884
3893.7656 | 123.143 | -68.1061 | 54.7028 | -0.11085 | 0.0084466 | 0.0068147 | 0.0069064 | -0.0088953 | -0.0045821 | -0.0026574 | 54.7577 | 54.7256 | -68.5135 | 54.9179 | 54.7302 | 54.7668 | 54.5609 | 54.9316 | 54.7211 | 8.4869 | -0.40741 | 0.022888 | 122.8638 | 123.024 | 0.027466 | 76.593 | 0.01831 | 123.2712 | 122.6669 | 123.0377 | 122.8363 | 122.8317 | 122.8638 | 122.8271 | 122.8729 | 76.593 | 122.8317 | 122.8638 | 122.8729 | 122.8363 | 122.8271 | -123.2162 | -46.2158
3894.7812 | 123.0743 | -68.1656 | 54.7165 | -0.011673 | 0.015283 | 0.0055329 | 0.010538 | -0.0097497 | -0.0054367 | -0.0013758 | 54.7714 | 54.8447 | -68.5226 | 54.9225 | 54.657 | 54.6753 | 54.6753 | 54.8492 | 54.7852 | 8.4824 | -0.35706 | 0.12817 | 122.937 | 123.0881 | -0.05951 | 76.6479 | 0.068664 | 123.2941 | 122.8409 | 123.0148 | 122.8226 | 123.0103 | 122.937 | 122.9507 | 122.8409 | 76.6479 | 123.0103 | 122.937 | 122.8409 | 122.8226 | 122.9507 | -123.2391 | -46.2341
3895.7656 | 123.1155 | -68.1656 | 54.6844 | 0.041733 | 0.011651 | 0.0042511 | 0.002634 | -0.0121 | -0.0050095 | -9.3992e-05 | 54.6661 | 54.7485 | -68.5272 | 54.9042 | 54.7256 | 54.7028 | 54.6249 | 54.8538 | 54.7714 | 8.4915 | -0.36163 | 0.064087 | 122.8317 | 123.0698 | 0.041199 | 76.6571 | 0.086975 | 123.1934 | 122.7905 | 123.0194 | 122.8912 | 122.9141 | 122.8317 | 122.937 | 122.8683 | 76.6571 | 122.9141 | 122.8317 | 122.8683 | 122.8912 | 122.937 | -123.2117 | -46.1929
3896.7656 | 123.1201 | -68.129 | 54.7028 | 0.041733 | 0.011224 | 0.0061737 | 0.003702 | -0.012313 | -0.0062911 | -0.0015894 | 54.6707 | 54.7531 | -68.5043 | 54.9408 | 54.7256 | 54.7302 | 54.6066 | 54.8813 | 54.7531 | 8.4915 | -0.37537 | 0.050354 | 122.7997 | 123.0698 | 0.022888 | 76.6205 | 0.050354 | 123.175 | 122.7356 | 123.0103 | 122.8546 | 122.8821 | 122.7997 | 122.8821 | 122.8592 | 76.6205 | 122.8821 | 122.7997 | 122.8592 | 122.8546 | 122.8821 | -123.2071 | -46.2112
3897.7656 | 123.1659 | -68.1152 | 54.689 | -0.065079 | 0.008233 | 0.0057465 | 0.0032748 | -0.014236 | -0.0056503 | -0.0047938 | 54.7256 | 54.7531 | -68.4769 | 55.0049 | 54.7989 | 54.7852 | 54.5929 | 54.9591 | 54.744 | 8.4915 | -0.36163 | 0.064087 | 122.8409 | 123.1201 | 0.10986 | 76.6068 | 0.054932 | 123.2025 | 122.7081 | 123.0743 | 122.9141 | 122.8683 | 122.8409 | 122.8592 | 122.9004 | 76.6068 | 122.8683 | 122.8409 | 122.9004 | 122.9141 | 122.8592 | -123.1659 | -46.1975
3898.7812 | 123.1476 | -68.129 | 54.7073 | -0.057449 | 0.0093012 | 0.0063873 | 0.0049838 | -0.011672 | -0.0086411 | -0.0028712 | 54.7806 | 54.7668 | -68.4814 | 54.9683 | 54.7668 | 54.7577 | 54.6524 | 54.9271 | 54.7989 | 8.4869 | -0.35248 | 0.05951 | 122.9095 | 123.0972 | 0.05951 | 76.6159 | 0.091553 | 123.262 | 122.7814 | 123.056 | 122.8958 | 122.8958 | 122.9095 | 122.9279 | 122.8867 | 76.6159 | 122.8958 | 122.9095 | 122.8867 | 122.8958 | 122.9279 | -123.1888 | -46.2204
3899.7812 | 123.0423 | -68.1747 | 54.744 | -0.15663 | 0.014214 | 0.0059601 | 0.010324 | -0.0121 | -0.0086411 | -0.0056482 | 54.7165 | 54.863 | -68.5318 | 54.9088 | 54.6982 | 54.6478 | 54.7897 | 54.8264 | 54.8492 | 8.4824 | -0.35706 | 0.11902 | 122.8912 | 123.0835 | -0.045777 | 76.6571 | 0.10529 | 123.2483 | 122.9645 | 123.0011 | 122.8729 | 123.0377 | 122.8912 | 123.024 | 122.8226 | 76.6571 | 123.0377 | 122.8912 | 122.8226 | 122.8729 | 123.024 | -123.2758 | -46.2616
3900.7656 | 122.9782 | -68.1473 | 54.7714 | -0.17952 | 0.010583 | 0.0031831 | 0.0058382 | -0.0082545 | -0.0084273 | -0.0032984 | 54.6936 | 54.8355 | -68.5364 | 54.8904 | 54.689 | 54.6478 | 54.7943 | 54.95 | 54.8447 | 8.4915 | -0.3891 | 0.064087 | 122.8409 | 123.0377 | -0.082397 | 76.6388 | 0.073243 | 123.23 | 122.9416 | 123.0972 | 122.8363 | 122.9828 | 122.8409 | 122.9919 | 122.7951 | 76.6388 | 122.9828 | 122.8409 | 122.7951 | 122.8363 | 122.9919 | -123.3078 | -46.2799
3901.7656 | 123.0057 | -68.1793 | 54.7256 | -0.21004 | 0.012078 | 0.0025421 | 0.0079744 | -0.011672 | -0.0060775 | -0.0030848 | 54.6753 | 54.8355 | -68.5181 | 54.8172 | 54.5975 | 54.6341 | 54.7577 | 54.7806 | 54.808 | 8.4961 | -0.33875 | 0.10986 | 122.8546 | 122.9965 | -0.12817 | 76.6754 | 0.082397 | 123.1934 | 122.937 | 122.9599 | 122.7768 | 123.0148 | 122.8546 | 122.9874 | 122.8134 | 76.6754 | 123.0148 | 122.8546 | 122.8134 | 122.7768 | 122.9874 | -123.2437 | -46.2296
3902.7656 | 123.1384 | -68.1244 | 54.7028 | 0.07988 | 0.010369 | 0.0042511 | 0.001993 | -0.010818 | -0.0077865 | -0.001803 | 54.7119 | 54.7668 | -68.4906 | 54.982 | 54.7897 | 54.7714 | 54.6387 | 54.9454 | 54.7714 | 8.5007 | -0.36621 | 0.064087 | 122.8363 | 123.1064 | 0.086975 | 76.6251 | 0.068664 | 123.2025 | 122.7631 | 123.0698 | 122.9141 | 122.8912 | 122.8363 | 122.8958 | 122.8958 | 76.6251 | 122.8912 | 122.8363 | 122.8958 | 122.9141 | 122.8958 | -123.1934 | -46.2021
3903.7656 | 123.1155 | -68.1335 | 54.7165 | -0.16426 | 0.012719 | 0.0016877 | 0.0073336 | -0.0121 | -0.0052231 | -0.0030848 | 54.7577 | 54.7668 | -68.5043 | 54.9866 | 54.776 | 54.7668 | 54.657 | 54.9454 | 54.7943 | 8.4961 | -0.37079 | 0.050354 | 122.8912 | 123.1201 | 0.059509 | 76.6296 | 0.07782 | 123.262 | 122.7905 | 123.0789 | 122.9095 | 122.9004 | 122.8912 | 122.9279 | 122.9004 | 76.6296 | 122.9004 | 122.8912 | 122.9004 | 122.9095 | 122.9279 | -123.2208 | -46.2204
3904.7812 | 123.0057 | -68.2022 | 54.7348 | 0.034104 | 0.017205 | 0.0066009 | 0.013529 | -0.0093225 | -0.0052231 | -0.0028712 | 54.7119 | 54.8904 | -68.5135 | 54.8676 | 54.6433 | 54.6204 | 54.7394 | 54.7485 | 54.8126 | 8.4915 | -0.31128 | 0.15564 | 122.9141 | 123.0698 | -0.091552 | 76.6937 | 0.07782 | 123.2254 | 122.9416 | 122.9507 | 122.8455 | 123.0927 | 122.9141 | 123.0148 | 122.8226 | 76.6937 | 123.0927 | 122.9141 | 122.8226 | 122.8455 | 123.0148 | -123.2483 | -46.2433
3905.7656 | 123.0743 | -68.1519 | 54.7531 | -0.21004 | 0.012933 | 0.0021149 | 0.004343 | -0.0099633 | -0.0060775 | -0.0020166 | 54.7531 | 54.8538 | -68.5043 | 54.9362 | 54.7165 | 54.689 | 54.8767 | 54.8813 | 54.8538 | 8.4915 | -0.35248 | 0.10071 | 122.905 | 123.0881 | -0.036621 | 76.6434 | 0.10071 | 123.2574 | 123.0286 | 123.0331 | 122.8683 | 123.0057 | 122.905 | 123.0057 | 122.8409 | 76.6434 | 123.0057 | 122.905 | 122.8409 | 122.8683 | 123.0057 | -123.2574 | -46.2616
3906.7656 | 123.0789 | -68.129 | 54.7714 | -0.11085 | 0.01336 | 0.0091645 | 0.010324 | -0.0082545 | -0.0077865 | -0.0039392 | 54.7989 | 54.8767 | -68.486 | 54.9683 | 54.7485 | 54.7302 | 54.7668 | 54.8813 | 54.8309 | 8.5007 | -0.35706 | 0.10529 | 122.9279 | 123.0972 | -0.022888 | 76.6296 | 0.05951 | 123.2849 | 122.8958 | 123.0103 | 122.8775 | 123.0057 | 122.9279 | 122.9599 | 122.8592 | 76.6296 | 123.0057 | 122.9279 | 122.8592 | 122.8775 | 122.9599 | -123.2574 | -46.2708
3907.7656 | 123.0881 | -68.1335 | 54.7531 | -0.087967 | 0.016778 | 0.0070283 | 0.0092562 | -0.0082545 | -0.0060775 | -0.0037256 | 54.7943 | 54.8996 | -68.5135 | 54.9637 | 54.7623 | 54.7348 | 54.7714 | 54.8767 | 54.8447 | 8.4915 | -0.37994 | 0.14648 | 122.9279 | 123.0972 | 0.009155 | 76.6251 | 0.091553 | 123.3078 | 122.905 | 123.0103 | 122.8958 | 123.0331 | 122.9279 | 122.9782 | 122.8683 | 76.6251 | 123.0331 | 122.9279 | 122.8683 | 122.8958 | 122.9782 | -123.2666 | -46.2616
3908.7656 | 123.0789 | -68.1061 | 54.7668 | -0.15663 | 0.015069 | 0.0085235 | 0.0081882 | -0.0063317 | -0.0086411 | -0.00030759 | 54.7989 | 54.8904 | -68.4906 | 54.95 | 54.7485 | 54.7256 | 54.7806 | 54.8859 | 54.863 | 8.4869 | -0.38452 | 0.1236 | 122.905 | 123.056 | -0.018311 | 76.593 | 0.09613 | 123.2895 | 122.8867 | 122.9919 | 122.8546 | 122.9965 | 122.905 | 122.9691 | 122.8317 | 76.593 | 122.9965 | 122.905 | 122.8317 | 122.8546 | 122.9691 | -123.2574 | -46.2799
3909.7656 | 123.0423 | -68.161 | 54.7806 | -0.17952 | 0.014214 | 0.0019013 | 0.004343 | -0.0084681 | -0.0047957 | -0.001803 | 54.7119 | 54.8996 | -68.4814 | 54.9133 | 54.7302 | 54.6936 | 54.8538 | 54.8676 | 54.8767 | 8.5007 | -0.32043 | 0.11902 | 122.8729 | 123.0743 | -0.050354 | 76.6617 | 0.09613 | 123.1934 | 123.0148 | 123.0286 | 122.8912 | 123.0606 | 122.8729 | 123.0377 | 122.8546 | 76.6617 | 123.0606 | 122.8729 | 122.8546 | 122.8912 | 123.0377 | -123.262 | -46.2799
3910.7656 | 123.0606 | -68.1473 | 54.776 | -0.11848 | 0.011651 | 0.0068147 | 0.0077608 | -0.0078271 | -0.0067185 | -0.0026574 | 54.7302 | 54.9042 | -68.5043 | 54.9225 | 54.7211 | 54.7165 | 54.8401 | 54.8676 | 54.8813 | 8.4915 | -0.35706 | 0.12817 | 122.8775 | 123.0698 | -0.054932 | 76.6388 | 0.10529 | 123.2346 | 122.9874 | 123.0148 | 122.8683 | 123.0515 | 122.8775 | 123.0286 | 122.8638 | 76.6388 | 123.0515 | 122.8775 | 122.8638 | 122.8683 | 123.0286 | -123.2803 | -46.2845
3911.7656 | 123.056 | -68.1656 | 54.7943 | -0.14137 | 0.015283 | 0.0044647 | 0.0094698 | -0.0080407 | -0.0065047 | -0.0030848 | 54.7394 | 54.9316 | -68.4906 | 54.9225 | 54.744 | 54.7256 | 54.8538 | 54.8676 | 54.8721 | 8.4961 | -0.32501 | 0.13733 | 122.905 | 123.0881 | -0.050354 | 76.6617 | 0.077819 | 123.23 | 123.0194 | 123.0331 | 122.9095 | 123.0972 | 122.905 | 123.0377 | 122.8912 | 76.6617 | 123.0972 | 122.905 | 122.8912 | 122.9095 | 123.0377 | -123.2849 | -46.2982
3912.7812 | 123.0743 | -68.1152 | 54.7668 | -0.072708 | 0.014642 | 0.0055329 | 0.0075472 | -0.0078271 | -0.0071457 | -0.0024438 | 54.7897 | 54.9225 | -68.4631 | 54.9591 | 54.7577 | 54.7348 | 54.7943 | 54.8904 | 54.863 | 8.4961 | -0.3479 | 0.15564 | 122.905 | 123.0743 | -0.009156 | 76.6113 | 0.09613 | 123.2529 | 122.9095 | 123.0057 | 122.8729 | 123.0377 | 122.905 | 122.9782 | 122.85 | 76.6113 | 123.0377 | 122.905 | 122.85 | 122.8729 | 122.9782 | -123.23 | -46.2708
3913.7656 | 123.0377 | -68.1473 | 54.7714 | 0.10277 | 0.014855 | 0.0070283 | 0.0096834 | -0.0059045 | -0.0075729 | -0.0026574 | 54.776 | 54.9088 | -68.4677 | 54.9133 | 54.7028 | 54.7073 | 54.7897 | 54.8401 | 54.8538 | 8.4915 | -0.32043 | 0.13733 | 122.9233 | 123.0606 | -0.068664 | 76.6388 | 0.082398 | 123.2437 | 122.937 | 122.9874 | 122.85 | 123.056 | 122.9233 | 123.0011 | 122.8546 | 76.6388 | 123.056 | 122.9233 | 122.8546 | 122.85 | 123.0011 | -123.2391 | -46.2799
3914.7656 | 123.0331 | -68.1564 | 54.7714 | 0.07988 | 0.01571 | 0.0074555 | 0.013101 | -0.0056909 | -0.0075729 | -0.0041528 | 54.7623 | 54.9362 | -68.4769 | 54.9225 | 54.7165 | 54.6936 | 54.7943 | 54.8218 | 54.8859 | 8.4869 | -0.32043 | 0.16479 | 122.9187 | 123.0789 | -0.054931 | 76.6434 | 0.11444 | 123.2391 | 122.9507 | 122.9782 | 122.8729 | 123.0927 | 122.9187 | 123.0423 | 122.85 | 76.6434 | 123.0927 | 122.9187 | 122.85 | 122.8729 | 123.0423 | -123.2483 | -46.2845
3915.7656 | 123.0881 | -68.1335 | 54.7668 | -0.12611 | 0.016351 | 0.0083099 | 0.0077608 | -0.0063317 | -0.0047957 | 0.00054681 | 54.7668 | 54.9683 | -68.4769 | 54.95 | 54.7668 | 54.7394 | 54.8355 | 54.895 | 54.8538 | 8.4915 | -0.34332 | 0.20142 | 122.9004 | 123.0835 | 0 | 76.6251 | 0.086975 | 123.2437 | 122.9691 | 123.0286 | 122.9004 | 123.1018 | 122.9004 | 122.9874 | 122.8729 | 76.6251 | 123.1018 | 122.9004 | 122.8729 | 122.9004 | 122.9874 | -123.2437 | -46.2753
3916.7656 | 123.0789 | -68.129 | 54.7714 | -0.13374 | 0.015069 | 0.0070283 | 0.0081882 | -0.0078271 | -0.0069321 | -0.0037256 | 54.7943 | 54.9408 | -68.4723 | 54.9591 | 54.7623 | 54.7485 | 54.8126 | 54.895 | 54.8584 | 8.4915 | -0.34332 | 0.16937 | 122.9233 | 123.0881 | -0.009155 | 76.6205 | 0.086975 | 123.2666 | 122.9416 | 123.024 | 122.8912 | 123.0698 | 122.9233 | 122.9874 | 122.8775 | 76.6205 | 123.0698 | 122.9233 | 122.8775 | 122.8912 | 122.9874 | -123.2437 | -46.2799
3917.7656 | 123.0972 | -68.1198 | 54.7806 | -0.04219 | 0.015283 | 0.01066 | 0.0075472 | -0.0059045 | -0.0071457 | 0.00033321 | 54.7531 | 54.9042 | -68.5043 | 54.95 | 54.744 | 54.7348 | 54.7852 | 54.8813 | 54.8721 | 8.4869 | -0.38452 | 0.1236 | 122.8729 | 123.0698 | -0.036621 | 76.6067 | 0.091552 | 123.2574 | 122.905 | 123.0011 | 122.8638 | 123.024 | 122.8729 | 122.9919 | 122.8546 | 76.6067 | 123.024 | 122.8729 | 122.8546 | 122.8638 | 122.9919 | -123.2849 | -46.2936
3918.7656 | 123.0789 | -68.1244 | 54.7485 | -0.44655 | 0.015923 | 0.0066009 | 0.0077608 | -0.0052637 | -0.0052231 | -0.0024438 | 54.8035 | 54.9179 | -68.5226 | 54.95 | 54.7531 | 54.7485 | 54.7806 | 54.8767 | 54.8859 | 8.4824 | -0.39825 | 0.16937 | 122.9279 | 123.0743 | 0.004578 | 76.6068 | 0.13733 | 123.3261 | 122.905 | 123.0011 | 122.8775 | 123.0423 | 122.9279 | 123.0103 | 122.8729 | 76.6068 | 123.0423 | 122.9279 | 122.8729 | 122.8775 | 123.0103 | -123.2712 | -46.2662
3919.7812 | 123.0606 | -68.1473 | 54.7623 | 0.049362 | 0.014855 | 0.0093781 | 0.0064792 | -0.0073999 | -0.0067185 | -0.0032984 | 54.7714 | 54.9179 | -68.5089 | 54.9042 | 54.7073 | 54.6799 | 54.7943 | 54.8309 | 54.863 | 8.4869 | -0.36163 | 0.15564 | 122.9187 | 123.0515 | -0.054932 | 76.6342 | 0.10071 | 123.2803 | 122.9416 | 122.9782 | 122.8546 | 123.0652 | 122.9187 | 123.0103 | 122.8271 | 76.6342 | 123.0652 | 122.9187 | 122.8271 | 122.8546 | 123.0103 | -123.2712 | -46.2753
3920.7656 | 123.0423 | -68.1564 | 54.7714 | 0.087509 | 0.016137 | 0.0051057 | 0.0081882 | -0.0048365 | -0.0054367 | 0.00011961 | 54.7165 | 54.9454 | -68.5135 | 54.8676 | 54.6707 | 54.6753 | 54.776 | 54.808 | 54.8401 | 8.4869 | -0.35706 | 0.17395 | 122.8729 | 123.024 | -0.10071 | 76.6434 | 0.068665 | 123.23 | 122.9324 | 122.9645 | 122.8271 | 123.1018 | 122.8729 | 122.9965 | 122.8317 | 76.6434 | 123.1018 | 122.8729 | 122.8317 | 122.8271 | 122.9965 | -123.2849 | -46.2845
3921.7656 | 123.056 | -68.161 | 54.7256 | 0.33165 | 0.014855 | 0.0074555 | 0.0062656 | -0.0065455 | -0.0047957 | -0.0026574 | 54.7165 | 54.9179 | -68.5135 | 54.895 | 54.6753 | 54.6707 | 54.776 | 54.8172 | 54.8584 | 8.4824 | -0.35248 | 0.19226 | 122.8775 | 123.056 | -0.050354 | 76.6434 | 0.13275 | 123.23 | 122.937 | 122.9782 | 122.8363 | 123.0789 | 122.8775 | 123.0194 | 122.8317 | 76.6434 | 123.0789 | 122.8775 | 122.8317 | 122.8363 | 123.0194 | -123.2391 | -46.2433
3922.7656 | 123.0743 | -68.1381 | 54.7623 | -0.019302 | 0.015069 | 0.0048921 | 0.0098972 | -0.0078271 | -0.0073593 | -0.0041528 | 54.7943 | 54.9316 | -68.5089 | 54.9316 | 54.7394 | 54.7256 | 54.7852 | 54.8676 | 54.8767 | 8.4824 | -0.37079 | 0.16937 | 122.9324 | 123.0698 | -0.022888 | 76.6205 | 0.11444 | 123.3032 | 122.9233 | 123.0057 | 122.8775 | 123.0698 | 122.9324 | 123.0148 | 122.8638 | 76.6205 | 123.0698 | 122.9324 | 122.8638 | 122.8775 | 123.0148 | -123.2712 | -46.2799
3923.7656 | 123.0606 | -68.1519 | 54.7852 | 0.026474 | 0.015283 | 0.0055329 | 0.010538 | -0.0063317 | -0.0069321 | -0.0020166 | 54.7989 | 54.9408 | -68.5043 | 54.9271 | 54.7256 | 54.7119 | 54.7897 | 54.8584 | 54.8996 | 8.4869 | -0.35248 | 0.15564 | 122.9507 | 123.0789 | -0.059509 | 76.6388 | 0.11444 | 123.3032 | 122.9416 | 123.0103 | 122.8775 | 123.0927 | 122.9507 | 123.0515 | 122.8638 | 76.6388 | 123.0927 | 122.9507 | 122.8638 | 122.8775 | 123.0515 | -123.2895 | -46.2982
3924.7656 | 123.0286 | -68.1702 | 54.776 | 0.10277 | 0.015283 | 0.010019 | 0.0077608 | -0.0056909 | -0.0073593 | -0.0037256 | 54.744 | 54.9591 | -68.4952 | 54.8767 | 54.6616 | 54.6524 | 54.8035 | 54.7806 | 54.8996 | 8.4915 | -0.32501 | 0.1831 | 122.9141 | 123.0469 | -0.11444 | 76.6617 | 0.1236 | 123.2391 | 122.9736 | 122.9507 | 122.8317 | 123.1293 | 122.9141 | 123.0698 | 122.8226 | 76.6617 | 123.1293 | 122.9141 | 122.8226 | 122.8317 | 123.0698 | -123.2712 | -46.2845
3925.7812 | 123.0606 | -68.1381 | 54.7668 | -1.797 | 0.01806 | 0.0025421 | 0.0084018 | -0.0067591 | -0.0054367 | -0.001803 | 54.744 | 54.9591 | -68.4769 | 54.8904 | 54.6524 | 54.6707 | 54.776 | 54.8218 | 54.8584 | 8.4915 | -0.33875 | 0.19226 | 122.8821 | 123.0286 | -0.11444 | 76.6296 | 0.091552 | 123.2208 | 122.9141 | 122.9599 | 122.7905 | 123.0972 | 122.8821 | 122.9965 | 122.8088 | 76.6296 | 123.0972 | 122.8821 | 122.8088 | 122.7905 | 122.9965 | -123.2437 | -46.2753
3926.7812 | 123.056 | -68.1702 | 54.7623 | 0.942 | 0.014642 | 0.0093781 | 0.0073336 | -0.0059045 | -0.0047957 | -0.0028712 | 54.7073 | 54.9179 | -68.4998 | 54.8859 | 54.6799 | 54.6707 | 54.776 | 54.8035 | 54.863 | 8.4915 | -0.32959 | 0.15564 | 122.8775 | 123.056 | -0.082397 | 76.6617 | 0.10071 | 123.2071 | 122.9462 | 122.9736 | 122.85 | 123.0881 | 122.8775 | 123.0331 | 122.8409 | 76.6617 | 123.0881 | 122.8775 | 122.8409 | 122.85 | 123.0331 | -123.262 | -46.2708
3927.7656 | 123.1476 | -68.1335 | 54.689 | 0.19432 | 0.016351 | 0.011087 | 0.0066928 | -0.0078271 | -0.0050095 | -0.003512 | 54.7989 | 54.8447 | -68.5043 | 54.9362 | 54.7714 | 54.776 | 54.6066 | 54.895 | 54.8309 | 8.4915 | -0.37079 | 0.15564 | 122.9324 | 123.0698 | 0.082397 | 76.6251 | 0.14191 | 123.3032 | 122.7402 | 123.0286 | 122.905 | 122.9782 | 122.9324 | 122.9645 | 122.9095 | 76.6251 | 122.9782 | 122.9324 | 122.9095 | 122.905 | 122.9645 | -123.1934 | -46.1975
3928.7656 | 123.1476 | -68.129 | 54.7119 | 0.10277 | 0.014428 | 0.012369 | 0.0056246 | -0.0067591 | -0.0047957 | -0.00030759 | 54.744 | 54.8447 | -68.4952 | 54.9316 | 54.7485 | 54.7714 | 54.6112 | 54.9133 | 54.808 | 8.5007 | -0.36621 | 0.13275 | 122.8729 | 123.0606 | 0.036621 | 76.6296 | 0.09613 | 123.2391 | 122.7402 | 123.0423 | 122.8775 | 122.9736 | 122.8729 | 122.937 | 122.9004 | 76.6296 | 122.9736 | 122.8729 | 122.9004 | 122.8775 | 122.937 | -123.2071 | -46.2112
3929.7656 | 123.0286 | -68.1747 | 54.7302 | 0.07988 | 0.01571 | 0.0063873 | 0.012247 | -0.0056909 | -0.0045821 | -9.3992e-05 | 54.7165 | 54.9454 | -68.5501 | 54.8538 | 54.6616 | 54.6524 | 54.776 | 54.8035 | 54.8721 | 8.4869 | -0.37537 | 0.21515 | 122.8912 | 123.0286 | -0.068665 | 76.6617 | 0.14191 | 123.2666 | 122.9507 | 122.9782 | 122.8363 | 123.1201 | 122.8912 | 123.0469 | 122.8271 | 76.6617 | 123.1201 | 122.8912 | 122.8271 | 122.8363 | 123.0469 | -123.2803 | -46.2433
3930.7656 | 122.9324 | -68.1656 | 54.689 | 0.11803 | 0.01806 | 0.0078827 | 0.0092562 | -0.0059045 | -0.0043685 | -0.0013758 | 54.7119 | 54.9591 | -68.5089 | 54.8721 | 54.6707 | 54.6753 | 54.7806 | 54.7989 | 54.8859 | 8.4869 | -0.34332 | 0.27008 | 122.8775 | 123.0377 | -0.018311 | 76.6525 | 0.19684 | 123.2208 | 122.9462 | 122.9645 | 122.8363 | 123.1247 | 122.8775 | 123.0515 | 122.8409 | 76.6525 | 123.1247 | 122.8775 | 122.8409 | 122.8363 | 123.0515 | -123.1979 | -46.2021
3931.7656 | 123.0881 | -68.1747 | 54.7531 | 0.22484 | 0.015496 | 0.0076691 | 0.0069064 | -0.0076135 | -0.0056503 | -0.00094839 | 54.7394 | 54.9133 | -68.5135 | 54.9042 | 54.6844 | 54.6844 | 54.7348 | 54.8309 | 54.8538 | 8.4915 | -0.33875 | 0.16022 | 122.9141 | 123.0789 | -0.068665 | 76.6663 | 0.10071 | 123.2529 | 122.9095 | 123.0057 | 122.8592 | 123.0881 | 122.9141 | 123.0286 | 122.8592 | 76.6663 | 123.0881 | 122.9141 | 122.8592 | 122.8592 | 123.0286 | -123.2666 | -46.2616
3932.7656 | 123.0881 | -68.1656 | 54.7577 | 0.20195 | 0.01571 | 0.010019 | 0.0066928 | -0.0048365 | -0.0039413 | -0.001803 | 54.744 | 54.8904 | -68.4906 | 54.8996 | 54.6936 | 54.6982 | 54.7394 | 54.8447 | 54.8401 | 8.4961 | -0.32501 | 0.13275 | 122.9095 | 123.0652 | -0.064086 | 76.6617 | 0.082398 | 123.2346 | 122.905 | 123.0103 | 122.8592 | 123.056 | 122.9095 | 123.0057 | 122.8638 | 76.6617 | 123.056 | 122.9095 | 122.8638 | 122.8592 | 123.0057 | -123.2483 | -46.2616
3933.7656 | 123.1201 | -68.1473 | 54.744 | 0.18669 | 0.01101 | 0.0076691 | 0.002634 | -0.0069727 | -0.0024459 | -0.0028712 | 54.808 | 54.8126 | -68.5043 | 54.9591 | 54.7943 | 54.7806 | 54.6387 | 54.9225 | 54.8309 | 8.4961 | -0.35706 | 0.068664 | 122.9553 | 123.1064 | 0.050354 | 76.6434 | 0.086975 | 123.3124 | 122.7859 | 123.0698 | 122.9416 | 122.9599 | 122.9553 | 122.9782 | 122.9279 | 76.6434 | 122.9599 | 122.9553 | 122.9279 | 122.9416 | 122.9782 | -123.2483 | -46.2479
3934.7656 | 123.1201 | -68.129 | 54.7165 | 0.18669 | 0.01336 | 0.0036103 | 0.0034884 | -0.0076135 | -0.0026595 | -0.00094839 | 54.776 | 54.8447 | -68.4814 | 54.95 | 54.7485 | 54.7714 | 54.6295 | 54.9179 | 54.8172 | 8.4915 | -0.35248 | 0.12817 | 122.905 | 123.0789 | 0.032043 | 76.6205 | 0.10071 | 123.2574 | 122.7585 | 123.0469 | 122.8775 | 122.9736 | 122.905 | 122.9462 | 122.9004 | 76.6205 | 122.9736 | 122.905 | 122.9004 | 122.8775 | 122.9462 | -123.1979 | -46.225
3935.7656 | 123.1567 | -68.1015 | 54.7394 | 0.20958 | 0.012078 | 0.0057465 | 0.0030612 | -0.0095361 | -0.0054367 | -0.00073479 | 54.7668 | 54.8264 | -68.4814 | 54.9454 | 54.7577 | 54.7531 | 54.6478 | 54.9088 | 54.8172 | 8.4824 | -0.37994 | 0.086975 | 122.8683 | 123.0469 | 0.01831 | 76.5839 | 0.07782 | 123.2483 | 122.7493 | 123.0103 | 122.8592 | 122.9279 | 122.8683 | 122.9187 | 122.8546 | 76.5839 | 122.9279 | 122.8683 | 122.8546 | 122.8592 | 122.9187 | -123.2208 | -46.257
3936.7656 | 123.1476 | -68.1107 | 54.7302 | 0.26299 | 0.014642 | 0.0059601 | 0.0092562 | -0.0086817 | -0.0058639 | -0.0013758 | 54.7577 | 54.8676 | -68.5272 | 54.9454 | 54.7485 | 54.7485 | 54.6661 | 54.895 | 54.808 | 8.4869 | -0.41656 | 0.13733 | 122.8683 | 123.056 | 0.01831 | 76.5976 | 0.077819 | 123.2849 | 122.7768 | 123.0057 | 122.8592 | 122.9782 | 122.8683 | 122.9187 | 122.8592 | 76.5976 | 122.9782 | 122.8683 | 122.8592 | 122.8592 | 122.9187 | -123.2574 | -46.2433
3937.7656 | 123.1613 | -68.129 | 54.7028 | 0.25536 | 0.015496 | 0.010232 | 0.0075472 | -0.0082545 | -0.0062911 | -0.0013758 | 54.7714 | 54.863 | -68.4952 | 54.9545 | 54.7348 | 54.7623 | 54.6387 | 54.9179 | 54.8355 | 8.4915 | -0.36621 | 0.16022 | 122.9004 | 123.0835 | 0.032043 | 76.6205 | 0.13275 | 123.2666 | 122.7676 | 123.0469 | 122.8638 | 122.9919 | 122.9004 | 122.9645 | 122.8912 | 76.6205 | 122.9919 | 122.9004 | 122.8912 | 122.8638 | 122.9645 | -123.1979 | -46.2112
3938.7656 | 123.1567 | -68.1015 | 54.7256 | -0.20241 | 0.013787 | 0.0068147 | 0.0056246 | -0.0093225 | -0.0052231 | -0.0015894 | 54.8035 | 54.8447 | -68.5043 | 54.9866 | 54.7806 | 54.7943 | 54.6112 | 54.9316 | 54.8126 | 8.4961 | -0.40283 | 0.11902 | 122.905 | 123.0881 | 0.054932 | 76.5976 | 0.086975 | 123.3078 | 122.7127 | 123.0331 | 122.8821 | 122.9462 | 122.905 | 122.9141 | 122.8958 | 76.5976 | 122.9462 | 122.905 | 122.8958 | 122.8821 | 122.9141 | -123.23 | -46.2296
3939.7812 | 123.111 | -68.1061 | 54.7394 | 0.1638 | 0.01101 | 0.0074555 | 0.001993 | -0.0088953 | -0.0056503 | -0.00094839 | 54.7577 | 54.8172 | -68.4906 | 54.9454 | 54.7394 | 54.7485 | 54.6661 | 54.9179 | 54.8309 | 8.4869 | -0.38452 | 0.07782 | 122.8638 | 123.0515 | 0 | 76.593 | 0.091553 | 123.2483 | 122.7722 | 123.024 | 122.8455 | 122.9233 | 122.8638 | 122.937 | 122.8546 | 76.593 | 122.9233 | 122.8638 | 122.8546 | 122.8455 | 122.937 | -123.23 | -46.2524
3940.7656 | 123.143 | -68.1015 | 54.7668 | 0.018845 | 0.0097284 | 0.0010467 | 0.0058382 | -0.010818 | -0.0037277 | -0.0011622 | 54.7394 | 54.8264 | -68.5089 | 54.9866 | 54.7897 | 54.7943 | 54.6936 | 54.9683 | 54.8355 | 8.4961 | -0.40741 | 0.059509 | 122.8409 | 123.0881 | 0.022888 | 76.5976 | 0.068664 | 123.2483 | 122.7951 | 123.0698 | 122.8912 | 122.9279 | 122.8409 | 122.937 | 122.8958 | 76.5976 | 122.9279 | 122.8409 | 122.8958 | 122.8912 | 122.937 | -123.2758 | -46.2708
3941.7656 | 123.1613 | -68.1244 | 54.7668 | -0.0040434 | 0.01101 | 0.0068147 | 0.0024202 | -0.01274 | -0.0039413 | -0.0020166 | 54.7714 | 54.8264 | -68.4906 | 55.0003 | 54.7943 | 54.8126 | 54.6844 | 54.9637 | 54.8447 | 8.4961 | -0.36621 | 0.059509 | 122.8958 | 123.1247 | 0.027466 | 76.6205 | 0.07782 | 123.262 | 122.8088 | 123.0881 | 122.9187 | 122.9507 | 122.8958 | 122.9691 | 122.937 | 76.6205 | 122.9507 | 122.8958 | 122.937 | 122.9187 | 122.9691 | -123.2574 | -46.2708
3942.7656 | 123.1659 | -68.1107 | 54.7668 | -0.034561 | 0.011437 | 0.0031831 | 0.004343 | -0.01274 | -0.0052231 | -0.0026574 | 54.776 | 54.8309 | -68.4906 | 55.0049 | 54.8172 | 54.8035 | 54.6799 | 54.9957 | 54.8264 | 8.4915 | -0.37994 | 0.064087 | 122.8867 | 123.1155 | 0.050354 | 76.6022 | 0.059509 | 123.2666 | 122.7905 | 123.1064 | 122.9279 | 122.9416 | 122.8867 | 122.937 | 122.9141 | 76.6022 | 122.9416 | 122.8867 | 122.9141 | 122.9279 | 122.937 | -123.2574 | -46.2753
3943.7656 | 123.1201 | -68.1152 | 54.776 | 0.19432 | 0.010796 | 0.0021149 | 0.003702 | -0.011672 | -0.0062911 | -0.00094839 | 54.7394 | 54.8218 | -68.5135 | 54.9545 | 54.7485 | 54.7531 | 54.689 | 54.9225 | 54.8355 | 8.4961 | -0.39826 | 0.045776 | 122.8546 | 123.0698 | -0.027466 | 76.6113 | 0.059509 | 123.2529 | 122.8043 | 123.0377 | 122.8638 | 122.937 | 122.8546 | 122.9507 | 122.8683 | 76.6113 | 122.937 | 122.8546 | 122.8683 | 122.8638 | 122.9507 | -123.2895 | -46.2799
3944.7656 | 123.111 | -68.1107 | 54.7714 | 0.14092 | 0.011651 | 0.0031831 | 0.0034884 | -0.012313 | -0.0037277 | -0.0030848 | 54.7302 | 54.8355 | -68.4952 | 54.9774 | 54.7577 | 54.744 | 54.689 | 54.8996 | 54.808 | 8.4915 | -0.38452 | 0.064087 | 122.8409 | 123.0881 | -0.013733 | 76.6022 | 0.036621 | 123.2254 | 122.7997 | 123.0103 | 122.8683 | 122.9462 | 122.8409 | 122.9187 | 122.8546 | 76.6022 | 122.9462 | 122.8409 | 122.8546 | 122.8683 | 122.9187 | -123.2666 | -46.2799
3945.7812 | 123.1842 | -68.0786 | 54.776 | -0.026932 | 0.010583 | 0.00040586 | 0.0022066 | -0.011886 | -0.0062911 | -0.0013758 | 54.808 | 54.8218 | -68.4723 | 55.0552 | 54.8309 | 54.8309 | 54.6661 | 55.014 | 54.8218 | 8.4869 | -0.39368 | 0.045776 | 122.8867 | 123.1338 | 0.054932 | 76.5656 | 0.045776 | 123.2803 | 122.7448 | 123.0927 | 122.9095 | 122.9004 | 122.8867 | 122.9004 | 122.9095 | 76.5656 | 122.9004 | 122.8867 | 122.9095 | 122.9095 | 122.9004 | -123.2483 | -46.2891
3946.7812 | 123.1934 | -68.0786 | 54.776 | -0.10323 | 0.010583 | -0.00066214 | 0.0045566 | -0.011245 | -0.0065047 | -0.001803 | 54.8401 | 54.8264 | -68.4494 | 55.0735 | 54.8492 | 54.8401 | 54.6616 | 55.0369 | 54.8492 | 8.4915 | -0.37079 | 0.050354 | 122.9187 | 123.1522 | 0.073242 | 76.5701 | 0.073242 | 123.2895 | 122.7402 | 123.1155 | 122.9279 | 122.905 | 122.9187 | 122.9279 | 122.9187 | 76.5701 | 122.905 | 122.9187 | 122.9187 | 122.9279 | 122.9279 | -123.2254 | -46.2845
3947.7656 | 123.1018 | -68.1107 | 54.7989 | -0.19478 | 0.011224 | 0.0033967 | 0.0058382 | -0.011245 | -0.0045821 | -0.0022302 | 54.7943 | 54.8447 | -68.4769 | 55.0003 | 54.7531 | 54.7531 | 54.8218 | 54.9225 | 54.8721 | 8.5007 | -0.36621 | 0.045777 | 122.905 | 123.111 | -0.045776 | 76.6113 | 0.073242 | 123.2712 | 122.9324 | 123.0331 | 122.8638 | 122.9553 | 122.905 | 122.9828 | 122.8638 | 76.6113 | 122.9553 | 122.905 | 122.8638 | 122.8638 | 122.9828 | -123.2758 | -46.2982
3948.7656 | 123.0789 | -68.1198 | 54.8264 | -0.17189 | 0.012719 | 0.0023285 | 0.010111 | -0.0121 | -0.0073593 | -0.003512 | 54.7668 | 54.895 | -68.4906 | 54.9728 | 54.7348 | 54.7073 | 54.8538 | 54.9179 | 54.895 | 8.4869 | -0.37079 | 0.068665 | 122.8867 | 123.0927 | -0.091553 | 76.6067 | 0.068665 | 123.2574 | 122.9736 | 123.0377 | 122.8546 | 123.0148 | 122.8867 | 123.0148 | 122.8271 | 76.6067 | 123.0148 | 122.8867 | 122.8271 | 122.8546 | 123.0148 | -123.317 | -46.3394
3949.7656 | 123.056 | -68.1152 | 54.8264 | -0.149 | 0.015496 | 0.0012605 | 0.0079744 | -0.0097497 | -0.0062911 | -0.0039392 | 54.7577 | 54.9088 | -68.4952 | 54.9683 | 54.7577 | 54.7165 | 54.8676 | 54.895 | 54.9133 | 8.4961 | -0.37994 | 0.082397 | 122.8729 | 123.0835 | -0.068665 | 76.6113 | 0.086975 | 123.2529 | 122.9828 | 123.0103 | 122.8729 | 123.024 | 122.8729 | 123.0286 | 122.8317 | 76.6113 | 123.024 | 122.8729 | 122.8317 | 122.8729 | 123.0286 | -123.3215 | -46.3303
3950.7656 | 123.2025 | -68.0969 | 54.7714 | -0.14137 | 0.0097284 | 0.0044647 | 0.0011386 | -0.012527 | -0.0052231 | -0.00094839 | 54.8492 | 54.8584 | -68.4494 | 55.0186 | 54.8172 | 54.7989 | 54.6982 | 54.9545 | 54.8309 | 8.5007 | -0.35248 | 0.086975 | 122.9462 | 123.1155 | 0.045777 | 76.5976 | 0.05951 | 123.2986 | 122.7951 | 123.0515 | 122.9141 | 122.9553 | 122.9462 | 122.9279 | 122.8958 | 76.5976 | 122.9553 | 122.9462 | 122.8958 | 122.9141 | 122.9279 | -123.2208 | -46.2708
3951.7656 | 123.1888 | -68.0832 | 54.776 | -0.29396 | 0.0093012 | 0.0042511 | 0.0028476 | -0.012313 | -0.0077865 | -0.0032984 | 54.7989 | 54.8355 | -68.4677 | 55.0507 | 54.8492 | 54.8309 | 54.7165 | 55.0095 | 54.7989 | 8.4915 | -0.38452 | 0.059509 | 122.8821 | 123.1338 | 0.073242 | 76.5747 | 0.022888 | 123.2666 | 122.7997 | 123.0927 | 122.9324 | 122.9187 | 122.8821 | 122.8821 | 122.9141 | 76.5747 | 122.9187 | 122.8821 | 122.9141 | 122.9324 | 122.8821 | -123.2437 | -46.2845
3952.7656 | 123.056 | -68.1381 | 54.7897 | -0.18715 | 0.011437 | 0.0061737 | 0.0066928 | -0.010604 | -0.0071457 | -0.0028712 | 54.808 | 54.8859 | -68.4723 | 54.9866 | 54.7623 | 54.7302 | 54.8355 | 54.9362 | 54.8767 | 8.5007 | -0.33417 | 0.09613 | 122.9462 | 123.1247 | -0.027466 | 76.6388 | 0.086975 | 123.2803 | 122.9736 | 123.0743 | 122.9004 | 123.024 | 122.9462 | 123.0148 | 122.8683 | 76.6388 | 123.024 | 122.9462 | 122.8683 | 122.9004 | 123.0148 | -123.262 | -46.2891
3953.7812 | 123.0606 | -68.1244 | 54.7897 | 0.072251 | 0.012719 | 0.0023285 | 0.0077608 | -0.011886 | -0.0054367 | -0.0022302 | 54.7714 | 54.9271 | -68.5181 | 54.982 | 54.7485 | 54.7119 | 54.8676 | 54.8721 | 54.8996 | 8.4915 | -0.39368 | 0.13733 | 122.8958 | 123.1064 | -0.041199 | 76.6159 | 0.10986 | 123.2895 | 122.9919 | 122.9965 | 122.8729 | 123.0515 | 122.8958 | 123.024 | 122.8363 | 76.6159 | 123.0515 | 122.8958 | 122.8363 | 122.8729 | 123.024 | -123.3078 | -46.2982
3954.7656 | 123.0927 | -68.1335 | 54.7806 | -0.04219 | 0.014214 | 0.0076691 | 0.011179 | -0.010604 | -0.0058639 | -0.0037256 | 54.8264 | 54.9362 | -68.4998 | 55.0095 | 54.7668 | 54.7531 | 54.7806 | 54.9042 | 54.895 | 8.4869 | -0.36621 | 0.15564 | 122.9599 | 123.143 | -0.013733 | 76.6205 | 0.11444 | 123.3261 | 122.9141 | 123.0377 | 122.9004 | 123.0698 | 122.9599 | 123.0286 | 122.8867 | 76.6205 | 123.0698 | 122.9599 | 122.8867 | 122.9004 | 123.0286 | -123.2803 | -46.2936
3955.7656 | 123.1338 | -68.129 | 54.808 | -0.034561 | 0.013574 | 0.0068147 | 0.0092562 | -0.0069727 | -0.0071457 | -0.0028712 | 54.8447 | 54.9271 | -68.4769 | 55.0003 | 54.7531 | 54.6158 | 54.8401 | 54.9179 | 54.8676 | 8.4961 | -0.3479 | 0.11902 | 122.9736 | 123.1293 | -0.054931 | 76.6251 | 0.05951 | 123.3215 | 122.9691 | 123.0469 | 122.8821 | 123.056 | 122.9736 | 122.9965 | 122.7448 | 76.6251 | 123.056 | 122.9736 | 122.7448 | 122.8821 | 122.9965 | -123.2849 | -46.312
3956.7656 | 123.1064 | -68.129 | 54.808 | 1.6973 | 0.015496 | 0.0078827 | 0.0098972 | -0.0078271 | -0.0054367 | -0.0011622 | 54.8447 | 54.9088 | -68.5043 | 54.9911 | 54.7852 | 54.7623 | 54.7714 | 54.8996 | 54.8813 | 8.4869 | -0.37537 | 0.10071 | 122.9736 | 123.1201 | -0.022888 | 76.6159 | 0.073243 | 123.349 | 122.9004 | 123.0286 | 122.9141 | 123.0377 | 122.9736 | 123.0103 | 122.8912 | 76.6159 | 123.0377 | 122.9736 | 122.8912 | 122.9141 | 123.0103 | -123.3124 | -46.3211
3957.7656 | 123.0652 | -68.1335 | 54.8035 | -0.15663 | 0.013787 | 0.0048921 | 0.0069064 | -0.0078271 | -0.0054367 | -0.0037256 | 54.7668 | 54.9728 | -68.4952 | 54.9728 | 54.776 | 54.7165 | 54.8676 | 54.8996 | 54.9225 | 8.4915 | -0.36163 | 0.16937 | 122.9004 | 123.1064 | -0.027466 | 76.6251 | 0.11902 | 123.262 | 123.0011 | 123.0331 | 122.9095 | 123.1064 | 122.9004 | 123.056 | 122.85 | 76.6251 | 123.1064 | 122.9004 | 122.85 | 122.9095 | 123.056 | -123.2986 | -46.312
3958.7656 | 123.1064 | -68.1381 | 54.7943 | -0.080337 | 0.016351 | 0.010019 | 0.010324 | -0.0056909 | -0.0082137 | -0.0026574 | 54.8309 | 54.9683 | -68.4906 | 54.9866 | 54.7897 | 54.776 | 54.7943 | 54.9133 | 54.8859 | 8.4961 | -0.35248 | 0.17395 | 122.9691 | 123.1247 | -0.004578 | 76.6342 | 0.091552 | 123.3215 | 122.9324 | 123.0515 | 122.9279 | 123.1064 | 122.9691 | 123.024 | 122.9141 | 76.6342 | 123.1064 | 122.9691 | 122.9141 | 122.9279 | 123.024 | -123.2849 | -46.2982
3959.7656 | 123.0881 | -68.1335 | 54.776 | -0.10323 | 0.015069 | 0.0059601 | 0.008829 | -0.0073999 | -0.0060775 | -0.00458 | 54.8264 | 54.9591 | -68.4906 | 54.9957 | 54.8035 | 54.7714 | 54.7989 | 54.9133 | 54.8859 | 8.4961 | -0.35706 | 0.1831 | 122.9599 | 123.1293 | 0.027466 | 76.6296 | 0.10986 | 123.317 | 122.9324 | 123.0469 | 122.937 | 123.0927 | 122.9599 | 123.0194 | 122.905 | 76.6296 | 123.0927 | 122.9599 | 122.905 | 122.937 | 123.0194 | -123.2666 | -46.2799
3960.7812 | 123.0698 | -68.1656 | 54.7943 | 0.041733 | 0.014855 | 0.0066009 | 0.0086154 | -0.0052637 | -0.0035141 | -0.00094839 | 54.8172 | 54.9637 | -68.4952 | 54.9545 | 54.7302 | 54.7348 | 54.8126 | 54.8676 | 54.8904 | 8.4961 | -0.32959 | 0.16937 | 122.9828 | 123.1201 | -0.064087 | 76.6617 | 0.09613 | 123.3124 | 122.9782 | 123.0331 | 122.8958 | 123.1293 | 122.9828 | 123.056 | 122.9004 | 76.6617 | 123.1293 | 122.9828 | 122.9004 | 122.8958 | 123.056 | -123.2895 | -46.2982
3961.7656 | 123.0743 | -68.161 | 54.7485 | 1.5371 | 0.015283 | 0.0091645 | 0.0081882 | -0.0050501 | -0.0054367 | -0.0026574 | 54.7806 | 54.9133 | -68.5318 | 54.9225 | 54.7256 | 54.7165 | 54.7714 | 54.8035 | 54.8996 | 8.4915 | -0.37079 | 0.1648 | 122.9416 | 123.0835 | -0.022888 | 76.6525 | 0.15106 | 123.3124 | 122.9324 | 122.9645 | 122.8867 | 123.0743 | 122.9416 | 123.0606 | 122.8775 | 76.6525 | 123.0743 | 122.9416 | 122.8775 | 122.8867 | 123.0606 | -123.2803 | -46.257
3962.7656 | 123.0881 | -68.1519 | 54.7531 | 0.22484 | 0.015496 | 0.0083099 | 0.0092562 | -0.0037683 | -0.0058639 | -0.0024438 | 54.7577 | 54.9728 | -68.5043 | 54.8996 | 54.7211 | 54.7211 | 54.7989 | 54.8355 | 54.8676 | 8.4915 | -0.35248 | 0.21973 | 122.9095 | 123.0515 | -0.032044 | 76.6434 | 0.11444 | 123.262 | 122.9507 | 122.9874 | 122.8729 | 123.1247 | 122.9095 | 123.0194 | 122.8729 | 76.6434 | 123.1247 | 122.9095 | 122.8729 | 122.8729 | 123.0194 | -123.2574 | -46.2616
3963.7656 | 123.0881 | -68.1564 | 54.7394 | 0.23247 | 0.015923 | 0.0059601 | 0.0064792 | -0.0069727 | -0.0060775 | -0.0030848 | 54.7531 | 54.9545 | -68.5089 | 54.9088 | 54.7256 | 54.7302 | 54.7394 | 54.8492 | 54.8721 | 8.4869 | -0.35248 | 0.21515 | 122.9095 | 123.0652 | -0.013733 | 76.6434 | 0.13275 | 123.262 | 122.8958 | 123.0057 | 122.8821 | 123.111 | 122.9095 | 123.0286 | 122.8867 | 76.6434 | 123.111 | 122.9095 | 122.8867 | 122.8821 | 123.0286 | -123.2483 | -46.2524
3964.7656 | 123.0743 | -68.1381 | 54.7897 | 0.034104 | 0.015923 | 0.0061737 | 0.0096834 | -0.0069727 | -0.0067185 | -0.0030848 | 54.7989 | 54.9637 | -68.4998 | 54.9316 | 54.7256 | 54.7348 | 54.8172 | 54.8492 | 54.8813 | 8.4869 | -0.36163 | 0.17395 | 122.937 | 123.0698 | -0.064087 | 76.6251 | 0.091553 | 123.2986 | 122.9553 | 122.9874 | 122.8638 | 123.1018 | 122.937 | 123.0194 | 122.8729 | 76.6251 | 123.1018 | 122.937 | 122.8729 | 122.8638 | 123.0194 | -123.2895 | -46.3028
3965.7656 | 123.0835 | -68.1473 | 54.7943 | 0.22484 | 0.016992 | 0.010446 | 0.0075472 | -0.0029139 | -0.0065047 | 0.00076041 | 54.7531 | 54.9454 | -68.5043 | 54.9042 | 54.9454 | 54.5013 | 54.6707 | 55.1056 | 54.8355 | 8.4961 | -0.35706 | 0.15106 | 122.9004 | 123.0515 | 0.15106 | 76.6434 | 0.041198 | 123.2574 | 122.818 | 123.2529 | 123.0927 | 123.0927 | 122.9004 | 122.9828 | 122.6486 | 76.6434 | 123.0927 | 122.9004 | 122.6486 | 123.0927 | 122.9828 | -123.2986 | -46.2982
3966.7656 | 123.175 | -68.129 | 54.7256 | 0.27061 | 0.013787 | 0.0059601 | 0.0013522 | -0.0067591 | -0.0045821 | -0.0011622 | 54.8126 | 54.8859 | -68.4769 | 55.0095 | 54.8126 | 54.8492 | 54.6661 | 54.9545 | 54.8447 | 8.4869 | -0.3479 | 0.16022 | 122.9416 | 123.1384 | 0.086975 | 76.6159 | 0.11902 | 123.2895 | 122.7951 | 123.0835 | 122.9416 | 123.0148 | 122.9416 | 122.9736 | 122.9782 | 76.6159 | 123.0148 | 122.9416 | 122.9782 | 122.9416 | 122.9736 | -123.2025 | -46.2387
3967.7812 | 123.143 | -68.1564 | 54.7531 | 0.24773 | 0.015496 | 0.0051057 | 0.0075472 | -0.0059045 | -0.0060775 | -0.003512 | 54.7668 | 54.9042 | -68.5272 | 54.9362 | 54.7668 | 54.7577 | 54.689 | 54.8767 | 54.8538 | 8.4915 | -0.37079 | 0.15106 | 122.9233 | 123.0927 | 0.013733 | 76.6479 | 0.10071 | 123.2941 | 122.8455 | 123.0331 | 122.9233 | 123.0606 | 122.9233 | 123.0103 | 122.9141 | 76.6479 | 123.0606 | 122.9233 | 122.9141 | 122.9233 | 123.0103 | -123.2803 | -46.2616
3968.7656 | 123.1796 | -68.1244 | 54.7394 | 0.23247 | 0.011651 | 0.010019 | 0.0032748 | -0.0067591 | -0.0039413 | -0.00094839 | 54.8126 | 54.8813 | -68.4998 | 54.9866 | 54.7943 | 54.8264 | 54.6524 | 54.95 | 54.8218 | 8.5007 | -0.37537 | 0.14191 | 122.937 | 123.111 | 0.054932 | 76.6251 | 0.082397 | 123.3124 | 122.7768 | 123.0743 | 122.9187 | 123.0057 | 122.937 | 122.9462 | 122.9507 | 76.6251 | 123.0057 | 122.937 | 122.9507 | 122.9187 | 122.9462 | -123.2391 | -46.2387
3969.7656 | 123.1567 | -68.1381 | 54.7165 | 0.18669 | 0.013574 | 0.0063873 | 0.0017794 | -0.0088953 | -0.0050095 | -0.0022302 | 54.7989 | 54.863 | -68.4769 | 54.9683 | 54.7897 | 54.8035 | 54.6341 | 54.9362 | 54.8218 | 8.4915 | -0.33875 | 0.14648 | 122.937 | 123.1064 | 0.073242 | 76.6296 | 0.10528 | 123.2758 | 122.7722 | 123.0743 | 122.9279 | 123.0011 | 122.937 | 122.9599 | 122.9416 | 76.6296 | 123.0011 | 122.937 | 122.9416 | 122.9279 | 122.9599 | -123.1934 | -46.225
3970.7656 | 123.1476 | -68.129 | 54.744 | 0.2401 | 0.01336 | 0.0061737 | 0.0073336 | -0.0086817 | -0.0071457 | -0.0026574 | 54.7668 | 54.9088 | -68.5226 | 54.95 | 54.7348 | 54.744 | 54.7028 | 54.8721 | 54.8355 | 8.4869 | -0.39368 | 0.16479 | 122.8958 | 123.0789 | -0.009156 | 76.6159 | 0.091552 | 123.2895 | 122.8317 | 123.0011 | 122.8638 | 123.0377 | 122.8958 | 122.9645 | 122.8729 | 76.6159 | 123.0377 | 122.8958 | 122.8729 | 122.8638 | 122.9645 | -123.2666 | -46.257
3971.7812 | 123.1705 | -68.0786 | 54.776 | 0.034104 | 0.011865 | 0.0055329 | 0.00049764 | -0.0099633 | -0.0060775 | 0.00011961 | 54.7668 | 54.8492 | -68.4906 | 54.9957 | 54.8035 | 54.808 | 54.7165 | 55.0003 | 54.8401 | 8.4961 | -0.41199 | 0.073242 | 122.8455 | 123.0743 | 0.027466 | 76.5747 | 0.064087 | 123.2574 | 122.7951 | 123.0789 | 122.8821 | 122.9279 | 122.8455 | 122.9187 | 122.8867 | 76.5747 | 122.9279 | 122.8455 | 122.8867 | 122.8821 | 122.9187 | -123.2666 | -46.2799
3972.7656 | 123.1979 | -68.129 | 54.7348 | 0.15617 | 0.012719 | 0.0063873 | 0.0062656 | -0.0076135 | -0.0075729 | -0.0024438 | 54.8172 | 54.8584 | -68.4769 | 54.9911 | 54.7714 | 54.808 | 54.6249 | 54.95 | 54.8126 | 8.4915 | -0.3479 | 0.1236 | 122.9462 | 123.1201 | 0.036621 | 76.6205 | 0.07782 | 123.2941 | 122.7539 | 123.0789 | 122.9004 | 122.9874 | 122.9462 | 122.9416 | 122.937 | 76.6205 | 122.9874 | 122.9462 | 122.937 | 122.9004 | 122.9416 | -123.2117 | -46.2433
3973.7812 | 123.1201 | -68.1244 | 54.7394 | 0.18669 | 0.011651 | 0.0042511 | 0.0028476 | -0.010391 | -0.0071457 | -0.00094839 | 54.7623 | 54.8218 | -68.5135 | 54.9591 | 54.7485 | 54.7714 | 54.6753 | 54.9362 | 54.8355 | 8.4915 | -0.3891 | 0.082397 | 122.8867 | 123.0835 | 0.009155 | 76.6159 | 0.09613 | 123.2758 | 122.7997 | 123.0606 | 122.8729 | 122.9462 | 122.8867 | 122.9599 | 122.8958 | 76.6159 | 122.9462 | 122.8867 | 122.8958 | 122.8729 | 122.9599 | -123.2529 | -46.2479
3974.7812 | 123.1567 | -68.1519 | 54.776 | 0.15617 | 0.011865 | 0.0044647 | 0.0039156 | -0.011245 | -0.0060775 | -0.00094839 | 54.7668 | 54.8172 | -68.5135 | 54.95 | 54.776 | 54.7806 | 54.689 | 54.9225 | 54.8172 | 8.4915 | -0.36163 | 0.041199 | 122.9187 | 123.1018 | 0 | 76.6434 | 0.041199 | 123.2803 | 122.8409 | 123.0743 | 122.9279 | 122.9691 | 122.9187 | 122.9691 | 122.9324 | 76.6434 | 122.9691 | 122.9187 | 122.9324 | 122.9279 | 122.9691 | -123.2895 | -46.2845
3975.7812 | 123.0881 | -68.1152 | 54.8447 | -0.17952 | 0.012719 | 0.0076691 | 0.0056246 | -0.013168 | -0.0043685 | -0.0020166 | 54.808 | 54.8813 | -68.4769 | 54.9911 | 54.7714 | 54.7531 | 54.8309 | 54.9454 | 54.8813 | 8.4961 | -0.36163 | 0.036621 | 122.9233 | 123.1064 | -0.073243 | 76.6113 | 0.036621 | 123.2849 | 122.9462 | 123.0606 | 122.8867 | 122.9965 | 122.9233 | 122.9965 | 122.8683 | 76.6113 | 122.9965 | 122.9233 | 122.8683 | 122.8867 | 122.9965 | -123.3215 | -46.3486
3976.7656 | 123.2254 | -68.0786 | 54.776 | 0.0035856 | 0.012078 | 0.0046783 | 0.004343 | -0.011459 | -0.0069321 | -0.0037256 | 54.7989 | 54.8309 | -68.4769 | 55.0232 | 54.8401 | 54.8218 | 54.6982 | 55.0003 | 54.8355 | 8.5007 | -0.39825 | 0.054932 | 122.8775 | 123.1018 | 0.064087 | 76.5793 | 0.059509 | 123.2758 | 122.7768 | 123.0789 | 122.9187 | 122.9095 | 122.8775 | 122.9141 | 122.9004 | 76.5793 | 122.9095 | 122.8775 | 122.9004 | 122.9187 | 122.9141 | -123.2529 | -46.2753
3977.7656 | 123.1476 | -68.1198 | 54.7668 | 0.1638 | 0.01101 | 0.0051057 | 0.0047702 | -0.011031 | -0.0039413 | -0.001803 | 54.7668 | 54.8126 | -68.5226 | 54.982 | 54.7485 | 54.7714 | 54.6936 | 54.9225 | 54.808 | 8.4915 | -0.40283 | 0.045776 | 122.8867 | 123.1018 | -0.018311 | 76.6113 | 0.041198 | 123.2895 | 122.8134 | 123.0423 | 122.8683 | 122.9324 | 122.8867 | 122.9279 | 122.8912 | 76.6113 | 122.9324 | 122.8867 | 122.8912 | 122.8683 | 122.9279 | -123.2895 | -46.2753
3978.7656 | 123.143 | -68.1061 | 54.7668 | 0.17906 | 0.0095148 | 0.0048921 | 0.0049838 | -0.010604 | -0.0037277 | -0.00030759 | 54.7485 | 54.8584 | -68.4814 | 54.982 | 54.7531 | 54.7623 | 54.6936 | 54.9179 | 54.8264 | 8.4869 | -0.37537 | 0.091552 | 122.8546 | 123.0881 | -0.013733 | 76.593 | 0.059509 | 123.23 | 122.7997 | 123.024 | 122.8592 | 122.9645 | 122.8546 | 122.9324 | 122.8683 | 76.593 | 122.9645 | 122.8546 | 122.8683 | 122.8592 | 122.9324 | -123.2483 | -46.2799
3979.7656 | 123.1842 | -68.1015 | 54.7806 | 0.0035856 | 0.0086602 | 0.0025421 | 0.0024202 | -0.012313 | -0.0035141 | -0.001803 | 54.7623 | 54.8538 | -68.486 | 55.0003 | 54.7989 | 54.7989 | 54.7073 | 54.9683 | 54.8309 | 8.4915 | -0.38452 | 0.073242 | 122.8638 | 123.1018 | 0.01831 | 76.593 | 0.050354 | 123.2483 | 122.8088 | 123.0698 | 122.9004 | 122.9553 | 122.8638 | 122.9324 | 122.9004 | 76.593 | 122.9553 | 122.8638 | 122.9004 | 122.9004 | 122.9324 | -123.2666 | -46.2891
3980.7812 | 123.0972 | -68.1427 | 54.7806 | -0.0040434 | 0.011865 | 0.0070283 | 0.011606 | -0.0097497 | -0.0047957 | -0.0050074 | 54.8309 | 54.9133 | -68.4723 | 54.9774 | 54.7256 | 54.7302 | 54.7943 | 54.8859 | 54.8813 | 8.4869 | -0.32959 | 0.13275 | 122.9736 | 123.1201 | -0.054932 | 76.6296 | 0.10071 | 123.3032 | 122.937 | 123.0286 | 122.8683 | 123.056 | 122.9736 | 123.024 | 122.8729 | 76.6296 | 123.056 | 122.9736 | 122.8729 | 122.8683 | 123.024 | -123.2529 | -46.2936
3981.7812 | 123.1201 | -68.0695 | 54.7714 | -0.072708 | 0.009942 | 0.00083306 | 0.0022066 | -0.0086817 | -0.0058639 | -0.0022302 | 54.8584 | 54.8447 | -68.4814 | 55.0552 | 54.8309 | 54.8492 | 54.7073 | 55.1285 | 54.8676 | 8.4915 | -0.41199 | 0.073243 | 122.9279 | 123.1247 | 0.05951 | 76.561 | 0.096131 | 123.3398 | 122.7768 | 123.1979 | 122.9004 | 122.9141 | 122.9279 | 122.937 | 122.9187 | 76.561 | 122.9141 | 122.9279 | 122.9187 | 122.9004 | 122.937 | -123.2529 | -46.2799
3982.7656 | 123.0789 | -68.1107 | 54.8218 | -0.20241 | 0.0095148 | 0.0027557 | 0.0051974 | -0.0093225 | -0.0047957 | -0.0030848 | 54.7989 | 54.8813 | -68.4769 | 54.9866 | 54.776 | 54.7348 | 54.8264 | 54.9728 | 54.8813 | 8.4961 | -0.36621 | 0.05951 | 122.9095 | 123.0972 | -0.045776 | 76.6068 | 0.05951 | 123.2758 | 122.937 | 123.0835 | 122.8867 | 122.9919 | 122.9095 | 122.9919 | 122.8455 | 76.6068 | 122.9919 | 122.9095 | 122.8455 | 122.8867 | 122.9919 | -123.2986 | -46.3257
3983.7656 | 123.0789 | -68.129 | 54.8309 | -0.29396 | 0.011437 | 0.0051057 | 0.0066928 | -0.0097497 | -0.0065047 | -0.0039392 | 54.7668 | 54.895 | -68.486 | 54.9637 | 54.7623 | 54.7211 | 54.8721 | 54.9133 | 54.8813 | 8.4915 | -0.35706 | 0.064087 | 122.8958 | 123.0927 | -0.068665 | 76.6205 | 0.050354 | 123.2529 | 123.0011 | 123.0423 | 122.8912 | 123.024 | 122.8958 | 123.0103 | 122.85 | 76.6205 | 123.024 | 122.8958 | 122.85 | 122.8912 | 123.0103 | -123.317 | -46.3394
3984.7656 | 123.1796 | -68.1198 | 54.7668 | -0.13374 | 0.010796 | 0.0029693 | 0.0032748 | -0.012313 | -0.0067185 | -0.0039392 | 54.8492 | 54.8401 | -68.4631 | 55.069 | 54.8584 | 54.7897 | 55.0735 | 54.9133 | 54.9042 | 8.4915 | -0.34332 | 0.073242 | 122.9691 | 123.1888 | 0.091552 | 76.6113 | 0.13733 | 123.3124 | 123.1934 | 123.0331 | 122.9782 | 122.9599 | 122.9691 | 123.024 | 122.9095 | 76.6113 | 122.9599 | 122.9691 | 122.9095 | 122.9782 | 123.024 | -123.23 | -46.2753
3985.7812 | 123.0652 | -68.1702 | 54.7989 | 0.07988 | 0.015283 | 0.0076691 | 0.013529 | -0.0097497 | -0.0037277 | -0.0020166 | 54.7897 | 54.9225 | -68.4998 | 54.9316 | 54.6936 | 54.6936 | 54.8172 | 54.8218 | 54.8859 | 8.4824 | -0.32959 | 0.1236 | 122.9599 | 123.1018 | -0.10529 | 76.6525 | 0.086975 | 123.2895 | 122.9874 | 122.9919 | 122.8638 | 123.0927 | 122.9599 | 123.056 | 122.8638 | 76.6525 | 123.0927 | 122.9599 | 122.8638 | 122.8638 | 123.056 | -123.2986 | -46.3165
3986.7656 | 123.111 | -68.1244 | 54.808 | -0.19478 | 0.011865 | 0.0023285 | 0.0041292 | -0.010391 | -0.0069321 | -0.0022302 | 54.7989 | 54.9042 | -68.4769 | 54.9911 | 54.7714 | 54.7577 | 54.8218 | 54.9408 | 54.8859 | 8.5007 | -0.35248 | 0.096131 | 122.9233 | 123.1155 | -0.036621 | 76.6251 | 0.07782 | 123.2758 | 122.9462 | 123.0652 | 122.8958 | 123.0286 | 122.9233 | 123.0103 | 122.8821 | 76.6251 | 123.0286 | 122.9233 | 122.8821 | 122.8958 | 123.0103 | -123.2849 | -46.3074
3987.7812 | 123.0743 | -68.1381 | 54.8447 | -0.11848 | 0.013574 | 0.0098053 | 0.0073336 | -0.010177 | -0.0039413 | -0.0026574 | 54.7485 | 54.95 | -68.5135 | 54.9683 | 54.7623 | 54.7348 | 54.8721 | 54.8904 | 54.9271 | 8.4915 | -0.37537 | 0.10529 | 122.8867 | 123.1064 | -0.082398 | 76.6296 | 0.082397 | 123.262 | 123.0103 | 123.0286 | 122.9004 | 123.0881 | 122.8867 | 123.0652 | 122.8729 | 76.6296 | 123.0881 | 122.8867 | 122.8729 | 122.9004 | 123.0652 | -123.3582 | -46.3531
3988.7812 | 123.111 | -68.1335 | 54.808 | -0.14137 | 0.014214 | 0.0076691 | 0.0084018 | -0.0084681 | -0.0069321 | -0.0030848 | 54.776 | 54.9362 | -68.5089 | 54.9866 | 54.776 | 54.7394 | 54.8859 | 54.895 | 54.8996 | 8.5007 | -0.37537 | 0.12817 | 122.9095 | 123.1201 | -0.032043 | 76.6342 | 0.091553 | 123.2849 | 123.0194 | 123.0286 | 122.9095 | 123.0698 | 122.9095 | 123.0331 | 122.8729 | 76.6342 | 123.0698 | 122.9095 | 122.8729 | 122.9095 | 123.0331 | -123.317 | -46.3074
3989.7656 | 123.1201 | -68.161 | 54.8264 | 0.35454 | 0.017205 | 0.0046783 | 0.0098972 | -0.0071863 | -0.0077865 | -0.0030848 | 54.8492 | 54.9316 | -68.5043 | 54.9957 | 54.7806 | 54.7806 | 54.7989 | 54.9042 | 54.9042 | 8.5007 | -0.34332 | 0.10529 | 123.0103 | 123.1567 | -0.045776 | 76.6617 | 0.07782 | 123.3536 | 122.9599 | 123.0652 | 122.9416 | 123.0927 | 123.0103 | 123.0652 | 122.9416 | 76.6617 | 123.0927 | 123.0103 | 122.9416 | 122.9416 | 123.0652 | -123.3307 | -46.3257
3990.7656 | 123.0972 | -68.1519 | 54.776 | 0.018845 | 0.01571 | 0.0029693 | 0.0075472 | -0.0054773 | -0.0069321 | -0.0024438 | 54.8355 | 54.9454 | -68.5135 | 54.982 | 54.7668 | 54.7577 | 54.808 | 54.8859 | 54.9179 | 8.4961 | -0.36163 | 0.16937 | 122.9874 | 123.1338 | -0.009155 | 76.6479 | 0.14191 | 123.349 | 122.9599 | 123.0377 | 122.9187 | 123.0972 | 122.9874 | 123.0698 | 122.9095 | 76.6479 | 123.0972 | 122.9874 | 122.9095 | 122.9187 | 123.0698 | -123.2895 | -46.2799
3991.7656 | 123.1293 | -68.1427 | 54.7989 | -0.13374 | 0.015283 | 0.0063873 | 0.010111 | -0.0095361 | -0.0062911 | -0.0030848 | 54.7989 | 54.9866 | -68.5043 | 54.9957 | 54.7943 | 54.7714 | 54.8584 | 54.9271 | 54.8767 | 8.4869 | -0.36163 | 0.18768 | 122.9416 | 123.1384 | -0.004577 | 76.6296 | 0.07782 | 123.3032 | 123.0011 | 123.0698 | 122.937 | 123.1293 | 122.9416 | 123.0194 | 122.9141 | 76.6296 | 123.1293 | 122.9416 | 122.9141 | 122.937 | 123.0194 | -123.3032 | -46.312
3992.7656 | 123.1293 | -68.1335 | 54.8126 | -0.12611 | 0.015283 | 0.0059601 | 0.0081882 | -0.0067591 | -0.0045821 | -0.0041528 | 54.8218 | 54.9683 | -68.5135 | 54.9911 | 54.8126 | 54.7714 | 54.8309 | 54.9225 | 54.8996 | 8.4915 | -0.37994 | 0.15564 | 122.9553 | 123.1247 | 0 | 76.6251 | 0.086975 | 123.3353 | 122.9645 | 123.056 | 122.9462 | 123.1018 | 122.9553 | 123.0331 | 122.905 | 76.6251 | 123.1018 | 122.9553 | 122.905 | 122.9462 | 123.0331 | -123.3261 | -46.3211
3993.7656 | 123.1201 | -68.1473 | 54.808 | -0.026932 | 0.01336 | 0.0085235 | 0.0098972 | -0.0065455 | -0.0082137 | -0.0024438 | 54.8401 | 54.982 | -68.5089 | 54.9683 | 54.776 | 54.7623 | 54.808 | 54.9088 | 54.8996 | 8.4915 | -0.36163 | 0.17395 | 122.9874 | 123.1155 | -0.032043 | 76.6388 | 0.091553 | 123.349 | 122.9553 | 123.056 | 122.9233 | 123.1293 | 122.9874 | 123.0469 | 122.9095 | 76.6388 | 123.1293 | 122.9874 | 122.9095 | 122.9233 | 123.0469 | -123.317 | -46.3165
3994.7812 | 123.0515 | -68.1793 | 54.7897 | 0.13329 | 0.014855 | 0.0095917 | 0.011179 | -0.0056909 | -0.0043685 | -0.0024438 | 54.7852 | 54.9408 | -68.5318 | 54.9316 | 54.7348 | 54.7073 | 54.8309 | 54.8218 | 54.8813 | 8.4961 | -0.35248 | 0.15106 | 122.9645 | 123.111 | -0.054932 | 76.6754 | 0.091553 | 123.317 | 123.0103 | 123.0011 | 122.9141 | 123.1201 | 122.9645 | 123.0606 | 122.8867 | 76.6754 | 123.1201 | 122.9645 | 122.8867 | 122.9141 | 123.0606 | -123.3215 | -46.2936
3995.7656 | 123.1201 | -68.1473 | 54.7714 | 0.2401 | 0.01571 | 0.0074555 | 0.0056246 | -0.0041955 | -0.0058639 | -0.0022302 | 54.7394 | 54.9362 | -68.5593 | 54.9408 | 54.7531 | 54.7394 | 54.7485 | 54.8584 | 54.863 | 8.4824 | -0.41199 | 0.16479 | 122.8867 | 123.0881 | -0.01831 | 76.6296 | 0.091553 | 123.2986 | 122.8958 | 123.0057 | 122.9004 | 123.0835 | 122.8867 | 123.0103 | 122.8867 | 76.6296 | 123.0835 | 122.8867 | 122.8867 | 122.9004 | 123.0103 | -123.3307 | -46.2891
3996.7656 | 123.1705 | -68.1656 | 54.7668 | 0.26299 | 0.014001 | 0.0085235 | 0.0058382 | -0.0082545 | -0.0045821 | -0.00052119 | 54.7806 | 54.9408 | -68.5043 | 54.9454 | 54.7623 | 54.7714 | 54.689 | 54.8904 | 54.8264 | 8.4961 | -0.33875 | 0.17395 | 122.9462 | 123.111 | -0.004578 | 76.6617 | 0.059509 | 123.2849 | 122.8546 | 123.056 | 122.9279 | 123.1064 | 122.9462 | 122.9919 | 122.937 | 76.6617 | 123.1064 | 122.9462 | 122.937 | 122.9279 | 122.9919 | -123.2712 | -46.2708
3997.7656 | 123.2025 | -68.1427 | 54.7485 | 0.28587 | 0.015283 | 0.0059601 | 0.0073336 | -0.0052637 | -0.0037277 | -0.0026574 | 54.808 | 54.9042 | -68.486 | 55.0003 | 54.8126 | 54.8172 | 54.6524 | 54.9316 | 54.8264 | 8.4915 | -0.34332 | 0.15564 | 122.9507 | 123.143 | 0.064087 | 76.6342 | 0.07782 | 123.2941 | 122.7951 | 123.0743 | 122.9553 | 123.0469 | 122.9507 | 122.9691 | 122.9599 | 76.6342 | 123.0469 | 122.9507 | 122.9599 | 122.9553 | 122.9691 | -123.2346 | -46.257
3998.7656 | 122.9965 | -68.1976 | 54.7577 | 0.15617 | 0.015496 | 0.0066009 | 0.010324 | -0.0061181 | -0.0050095 | -0.0024438 | 54.7348 | 54.9408 | -68.5593 | 54.8859 | 54.7165 | 54.7073 | 54.8309 | 54.8218 | 54.8813 | 8.4915 | -0.36163 | 0.18311 | 122.9324 | 123.0835 | -0.041198 | 76.6891 | 0.1236 | 123.2941 | 123.0286 | 123.0194 | 122.9141 | 123.1384 | 122.9324 | 123.0789 | 122.905 | 76.6891 | 123.1384 | 122.9324 | 122.905 | 122.9141 | 123.0789 | -123.317 | -46.2662
3999.7812 | 123.1796 | -68.1015 | 54.7668 | 0.095139 | 0.010583 | 0.0031831 | -0.0016386 | -0.0093225 | -0.0052231 | -0.001803 | 54.7256 | 54.8447 | -68.5181 | 54.9774 | 54.8172 | 54.7989 | 54.744 | 54.9683 | 54.8721 | 8.5007 | -0.41657 | 0.07782 | 122.8271 | 123.0789 | 0.050354 | 76.6022 | 0.10529 | 123.2437 | 122.8455 | 123.0698 | 122.9187 | 122.9462 | 122.8271 | 122.9736 | 122.9004 | 76.6022 | 122.9462 | 122.8271 | 122.9004 | 122.9187 | 122.9736 | -123.2849 | -46.2662
4000.7656 | 123.1522 | -68.1702 | 54.7531 | 0.2401 | 0.01571 | 0.0074555 | 0.011179 | -0.0073999 | -0.0052231 | -0.0024438 | 54.7668 | 54.9179 | -68.5089 | 54.9454 | 54.7531 | 54.7531 | 54.689 | 54.895 | 54.8538 | 8.4824 | -0.33875 | 0.16479 | 122.937 | 123.1155 | 0 | 76.6525 | 0.10071 | 123.2758 | 122.8592 | 123.0652 | 122.9233 | 123.0881 | 122.937 | 123.024 | 122.9233 | 76.6525 | 123.0881 | 122.937 | 122.9233 | 122.9233 | 123.024 | -123.262 | -46.2708
4001.7812 | 123.2162 | -68.1198 | 54.7531 | 0.26299 | 0.011865 | 0.010019 | 0.0090426 | -0.0082545 | -0.0086411 | 0.00011961 | 54.8218 | 54.863 | -68.4952 | 55.0827 | 54.8309 | 54.7989 | 54.6799 | 54.9683 | 54.8355 | 8.4869 | -0.37537 | 0.10986 | 122.9416 | 123.2025 | 0.07782 | 76.6067 | 0.082397 | 123.317 | 122.7997 | 123.0881 | 122.9507 | 122.9828 | 122.9416 | 122.9553 | 122.9187 | 76.6067 | 122.9828 | 122.9416 | 122.9187 | 122.9507 | 122.9553 | -123.2483 | -46.2662
4002.7656 | 123.1888 | -68.1335 | 54.7806 | 0.1638 | 0.011224 | 0.0027557 | 0.00028404 | -0.0088953 | -0.0037277 | -0.0022302 | 54.7623 | 54.8538 | -68.486 | 54.9683 | 54.776 | 54.7806 | 54.7302 | 54.9362 | 54.8447 | 8.4915 | -0.35248 | 0.073242 | 122.8958 | 123.1018 | -0.004578 | 76.6251 | 0.064087 | 123.2483 | 122.8638 | 123.0698 | 122.9095 | 122.9874 | 122.8958 | 122.9782 | 122.9141 | 76.6251 | 122.9874 | 122.8958 | 122.9141 | 122.9095 | 122.9782 | -123.2666 | -46.2891
4003.7656 | 123.1659 | -68.1335 | 54.7623 | 0.15617 | 0.012505 | 0.0040375 | 0.0028476 | -0.012313 | -0.0060775 | -0.00030759 | 54.7623 | 54.8767 | -68.5226 | 54.982 | 54.7668 | 54.7806 | 54.7256 | 54.9271 | 54.8538 | 8.4869 | -0.3891 | 0.11444 | 122.8958 | 123.1155 | 0.004578 | 76.6205 | 0.091553 | 123.2849 | 122.8592 | 123.0606 | 122.9004 | 123.0103 | 122.8958 | 122.9874 | 122.9141 | 76.6205 | 123.0103 | 122.8958 | 122.9141 | 122.9004 | 122.9874 | -123.2849 | -46.2753
4004.7656 | 123.1567 | -68.1335 | 54.7852 | 0.14092 | 0.013787 | 0.0059601 | 0.003702 | -0.012313 | -0.0054367 | -9.3992e-05 | 54.7714 | 54.8538 | -68.5272 | 54.9774 | 54.7577 | 54.7714 | 54.8172 | 55.101 | 54.8584 | 8.4915 | -0.39368 | 0.068665 | 122.905 | 123.111 | -0.027466 | 76.6251 | 0.073242 | 123.2986 | 122.9507 | 123.2346 | 122.8912 | 122.9874 | 122.905 | 122.9919 | 122.905 | 76.6251 | 122.9874 | 122.905 | 122.905 | 122.8912 | 122.9919 | -123.3124 | -46.2936
4005.7656 | 123.2071 | -68.1244 | 54.7531 | 0.27061 | 0.013146 | 0.010019 | 0.0079744 | -0.0082545 | -0.0045821 | -0.0022302 | 54.7165 | 54.8172 | -68.541 | 55.0507 | 54.7897 | 54.8035 | 54.6387 | 54.9545 | 54.8264 | 8.4915 | -0.41656 | 0.064087 | 122.8409 | 123.175 | 0.036621 | 76.6159 | 0.073242 | 123.2574 | 122.7631 | 123.0789 | 122.9141 | 122.9416 | 122.8409 | 122.9507 | 122.9279 | 76.6159 | 122.9416 | 122.8409 | 122.9279 | 122.9141 | 122.9507 | -123.2941 | -46.2616
4006.7656 | 123.1934 | -68.129 | 54.7577 | 0.20195 | 0.012292 | 0.0053193 | 0.0092562 | -0.0078271 | -0.0052231 | -0.00094839 | 54.8538 | 54.8584 | -68.5181 | 55.0095 | 54.776 | 54.808 | 54.6204 | 54.9728 | 54.8355 | 8.4869 | -0.3891 | 0.10071 | 122.9828 | 123.1384 | 0.018311 | 76.6159 | 0.07782 | 123.3719 | 122.7493 | 123.1018 | 122.905 | 122.9874 | 122.9828 | 122.9645 | 122.937 | 76.6159 | 122.9874 | 122.9828 | 122.937 | 122.905 | 122.9645 | -123.2758 | -46.2708
4007.7656 | 123.1705 | -68.1381 | 54.776 | 0.20958 | 0.01336 | 0.0085235 | 0.0047702 | -0.010818 | -0.0043685 | -0.00052119 | 54.8035 | 54.8218 | -68.5181 | 54.9866 | 54.776 | 54.7943 | 54.6753 | 54.9408 | 54.8218 | 8.4824 | -0.37994 | 0.045776 | 122.9416 | 123.1247 | 0 | 76.6205 | 0.045776 | 123.3215 | 122.8134 | 123.0789 | 122.9141 | 122.9599 | 122.9416 | 122.9599 | 122.9324 | 76.6205 | 122.9599 | 122.9416 | 122.9324 | 122.9141 | 122.9599 | -123.2941 | -46.2936
4008.7812 | 123.1567 | -68.1152 | 54.7668 | 0.17143 | 0.0088738 | 0.0019013 | 0.0032748 | -0.010604 | -0.0050095 | -0.00052119 | 54.7531 | 54.8355 | -68.4952 | 55.0964 | 54.7897 | 54.7348 | 54.6661 | 54.9133 | 54.8309 | 8.4961 | -0.37994 | 0.068664 | 122.8683 | 123.2117 | 0.022888 | 76.6113 | 0.064087 | 123.2483 | 122.7814 | 123.0286 | 122.905 | 122.9507 | 122.8683 | 122.9462 | 122.85 | 76.6113 | 122.9507 | 122.8683 | 122.85 | 122.905 | 122.9462 | -123.262 | -46.2708
4009.7656 | 123.2117 | -68.0923 | 54.808 | -0.0040434 | 0.010796 | 0.0066009 | 0.002634 | -0.012527 | -0.0062911 | -0.003512 | 54.8126 | 54.8492 | -68.4906 | 55.0552 | 54.8584 | 54.8492 | 54.6982 | 55.0278 | 54.8309 | 8.4961 | -0.39825 | 0.041199 | 122.905 | 123.1476 | 0.050354 | 76.5884 | 0.022889 | 123.3032 | 122.7905 | 123.1201 | 122.9507 | 122.9416 | 122.905 | 122.9233 | 122.9416 | 76.5884 | 122.9416 | 122.905 | 122.9416 | 122.9507 | 122.9233 | -123.2986 | -46.312
4010.7656 | 123.2254 | -68.1061 | 54.7852 | -0.034561 | 0.011651 | 0.0031831 | 0.0030612 | -0.01274 | -0.0054367 | -0.001803 | 54.8218 | 54.8538 | -68.4998 | 55.0644 | 54.8584 | 54.8676 | 54.7119 | 55.0323 | 54.8538 | 8.4961 | -0.39368 | 0.068665 | 122.9279 | 123.1705 | 0.073242 | 76.6022 | 0.068665 | 123.3215 | 122.818 | 123.1384 | 122.9645 | 122.9599 | 122.9279 | 122.9599 | 122.9736 | 76.6022 | 122.9599 | 122.9279 | 122.9736 | 122.9645 | 122.9599 | -123.2849 | -46.2891
4011.7656 | 123.2254 | -68.0878 | 54.7943 | -0.065079 | 0.011865 | 0.0059601 | 0.0030612 | -0.0121 | -0.0035141 | -0.0022302 | 54.8538 | 54.863 | -68.4814 | 55.0919 | 54.863 | 54.8447 | 54.6936 | 55.0461 | 54.8401 | 8.5007 | -0.39368 | 0.068664 | 122.9416 | 123.1796 | 0.068664 | 76.5884 | 0.045776 | 123.3353 | 122.7814 | 123.1339 | 122.9507 | 122.9507 | 122.9416 | 122.9279 | 122.9324 | 76.5884 | 122.9507 | 122.9416 | 122.9324 | 122.9507 | 122.9279 | -123.2758 | -46.2936
4012.7656 | 123.1842 | -68.1335 | 54.7806 | 0.095139 | 0.010796 | 0.00061946 | 0.0022066 | -0.011886 | -0.0073593 | -9.3992e-05 | 54.7714 | 54.8492 | -68.5226 | 54.9911 | 54.7806 | 54.776 | 54.7028 | 54.9454 | 54.8355 | 8.4961 | -0.3891 | 0.068664 | 122.905 | 123.1247 | 0 | 76.6296 | 0.054931 | 123.2941 | 122.8363 | 123.0789 | 122.9141 | 122.9828 | 122.905 | 122.9691 | 122.9095 | 76.6296 | 122.9828 | 122.905 | 122.9095 | 122.9141 | 122.9691 | -123.3032 | -46.2845
4013.7656 | 123.175 | -68.129 | 54.7806 | 0.14092 | 0.009942 | 0.0042511 | 7.0444e-05 | -0.013381 | -0.0054367 | -0.0022302 | 54.7577 | 54.8447 | -68.486 | 54.9866 | 54.7577 | 54.8401 | 54.7165 | 54.9088 | 54.8721 | 8.4961 | -0.35706 | 0.064087 | 122.8867 | 123.1155 | -0.022889 | 76.6251 | 0.091552 | 123.2437 | 122.8455 | 123.0377 | 122.8867 | 122.9736 | 122.8867 | 123.0011 | 122.9691 | 76.6251 | 122.9736 | 122.8867 | 122.9691 | 122.8867 | 123.0011 | -123.2666 | -46.2845
4014.7656 | 123.1934 | -68.1107 | 54.7989 | 0.018845 | 0.013574 | 0.0021149 | 0.0032748 | -0.01274 | -0.0058639 | -0.0037256 | 54.7852 | 54.8447 | -68.5043 | 55.0507 | 54.8172 | 54.8126 | 54.7073 | 54.9957 | 54.8172 | 8.4961 | -0.39368 | 0.045777 | 122.8958 | 123.1613 | 0.018311 | 76.6068 | 0.018311 | 123.2895 | 122.818 | 123.1064 | 122.9279 | 122.9553 | 122.8958 | 122.9279 | 122.9233 | 76.6068 | 122.9553 | 122.8958 | 122.9233 | 122.9279 | 122.9279 | -123.3032 | -46.3028
4015.7812 | 123.23 | -68.0969 | 54.7852 | -0.080337 | 0.01101 | 0.0014741 | 0.0041292 | -0.013381 | -0.0039413 | -0.0039392 | 54.8538 | 54.8355 | -68.4769 | 55.0873 | 54.8767 | 54.8538 | 54.689 | 55.0552 | 54.8447 | 8.4869 | -0.37994 | 0.050354 | 122.9507 | 123.1842 | 0.091553 | 76.5839 | 0.05951 | 123.3307 | 122.7859 | 123.1522 | 122.9736 | 122.9324 | 122.9507 | 122.9416 | 122.9507 | 76.5839 | 122.9324 | 122.9507 | 122.9507 | 122.9736 | 122.9416 | -123.262 | -46.2982
4016.7656 | 123.1338 | -68.1061 | 54.8401 | -0.20241 | 0.011865 | 0.0078827 | 0.0041292 | -0.014022 | -0.0050095 | -0.0024438 | 54.8264 | 54.8676 | -68.4998 | 55.0369 | 54.808 | 54.7806 | 54.8172 | 54.982 | 54.8813 | 8.4915 | -0.39368 | 0.027466 | 122.9324 | 123.143 | -0.032044 | 76.5976 | 0.041199 | 123.3261 | 122.9233 | 123.0881 | 122.9141 | 122.9736 | 122.9324 | 122.9874 | 122.8867 | 76.5976 | 122.9736 | 122.9324 | 122.8867 | 122.9141 | 122.9874 | -123.3398 | -46.3486
4017.7656 | 123.1064 | -68.1198 | 54.8492 | -0.18715 | 0.010796 | 0.0057465 | 0.0058382 | -0.011031 | -0.0058639 | -0.0028712 | 54.8172 | 54.8721 | -68.4906 | 55.0278 | 54.7943 | 54.776 | 54.8218 | 54.9408 | 54.8767 | 8.4961 | -0.37079 | 0.022888 | 122.937 | 123.1476 | -0.054931 | 76.6159 | 0.027466 | 123.3078 | 122.9416 | 123.0606 | 122.9141 | 122.9919 | 122.937 | 122.9965 | 122.8958 | 76.6159 | 122.9919 | 122.937 | 122.8958 | 122.9141 | 122.9965 | -123.3398 | -46.3531
4018.7656 | 123.1018 | -68.1427 | 54.8355 | -0.21767 | 0.013787 | 0.0066009 | 0.00712 | -0.0095361 | -0.0082137 | -0.003512 | 54.7897 | 54.9225 | -68.5043 | 55.0369 | 54.8218 | 54.7623 | 54.863 | 54.9454 | 54.895 | 8.5052 | -0.36163 | 0.086975 | 122.9324 | 123.1796 | -0.013733 | 76.6479 | 0.05951 | 123.2941 | 123.0057 | 123.0881 | 122.9645 | 123.0652 | 122.9324 | 123.0377 | 122.905 | 76.6479 | 123.0652 | 122.9324 | 122.905 | 122.9645 | 123.0377 | -123.3398 | -46.3303
4019.7656 | 123.2346 | -68.1015 | 54.8218 | -0.087967 | 0.0093012 | 0.0019013 | 0.0017794 | -0.012313 | -0.0052231 | -0.0015894 | 54.8676 | 54.863 | -68.4677 | 55.0919 | 54.8904 | 54.8584 | 54.6707 | 55.0507 | 54.8721 | 8.4915 | -0.36621 | 0.041199 | 122.9691 | 123.1934 | 0.068665 | 76.593 | 0.050354 | 123.3353 | 122.7722 | 123.1522 | 122.9919 | 122.9645 | 122.9691 | 122.9736 | 122.9599 | 76.593 | 122.9645 | 122.9691 | 122.9599 | 122.9919 | 122.9736 | -123.2895 | -46.3303
4020.7656 | 123.1979 | -68.1107 | 54.8126 | -0.072708 | 0.012292 | 0.0068147 | 0.004343 | -0.012527 | -0.0056503 | -0.0024438 | 54.8447 | 54.8492 | -68.4723 | 55.0827 | 54.863 | 54.8492 | 54.7623 | 55.0232 | 54.8492 | 8.4961 | -0.36163 | 0.036621 | 122.9553 | 123.1934 | 0.050354 | 76.6068 | 0.036621 | 123.317 | 122.8729 | 123.1338 | 122.9736 | 122.9599 | 122.9553 | 122.9599 | 122.9599 | 76.6068 | 122.9599 | 122.9553 | 122.9599 | 122.9736 | 122.9599 | -123.2849 | -46.3165
4021.7812 | 123.0927 | -68.1381 | 54.8218 | -0.17952 | 0.01101 | 0.0093781 | 0.0056246 | -0.012527 | -0.0050095 | -0.0043664 | 54.8126 | 54.9408 | -68.486 | 55.014 | 54.7989 | 54.7394 | 54.8813 | 54.9362 | 54.895 | 8.4915 | -0.3479 | 0.11902 | 122.9507 | 123.1522 | -0.022888 | 76.6296 | 0.073243 | 123.2986 | 123.0194 | 123.0743 | 122.937 | 123.0789 | 122.9507 | 123.0331 | 122.8775 | 76.6296 | 123.0789 | 122.9507 | 122.8775 | 122.937 | 123.0331 | -123.3078 | -46.3303
4022.7812 | 123.0972 | -68.1519 | 54.8447 | -0.095596 | 0.013146 | 0.0068147 | 0.005411 | -0.012527 | -0.0086411 | -0.0056482 | 54.808 | 54.9362 | -68.4769 | 54.982 | 54.7989 | 54.744 | 54.8813 | 54.9133 | 54.895 | 8.4915 | -0.32501 | 0.091552 | 122.9599 | 123.1338 | -0.045777 | 76.6434 | 0.050354 | 123.2849 | 123.0331 | 123.0652 | 122.9507 | 123.0881 | 122.9599 | 123.0469 | 122.8958 | 76.6434 | 123.0881 | 122.9599 | 122.8958 | 122.9507 | 123.0469 | -123.3215 | -46.3531
4023.7656 | 123.1293 | -68.1473 | 54.863 | -0.149 | 0.011224 | 0.0057465 | 0.010324 | -0.010604 | -0.0056503 | -0.0032984 | 54.808 | 54.9408 | -68.5043 | 55.014 | 54.808 | 54.7714 | 54.8538 | 54.9454 | 54.9042 | 8.4961 | -0.35706 | 0.07782 | 122.9553 | 123.1613 | -0.054932 | 76.6434 | 0.041199 | 123.3124 | 123.0011 | 123.0927 | 122.9553 | 123.0881 | 122.9553 | 123.0515 | 122.9187 | 76.6434 | 123.0881 | 122.9553 | 122.9187 | 122.9553 | 123.0515 | -123.3673 | -46.3669
4024.7656 | 123.1293 | -68.1427 | 54.8264 | -0.17952 | 0.013787 | 0.0070283 | 0.0096834 | -0.0086817 | -0.0073593 | -0.0024438 | 54.8126 | 54.9545 | -68.5226 | 55.0232 | 54.8126 | 54.7714 | 54.8538 | 54.9408 | 54.9042 | 8.5007 | -0.37994 | 0.12817 | 122.9553 | 123.1659 | -0.013733 | 76.6434 | 0.07782 | 123.3353 | 122.9965 | 123.0835 | 122.9553 | 123.0972 | 122.9553 | 123.0469 | 122.9141 | 76.6434 | 123.0972 | 122.9553 | 122.9141 | 122.9553 | 123.0469 | -123.349 | -46.3257
4025.7812 | 123.0927 | -68.1656 | 54.8309 | -0.18715 | 0.014001 | 0.0029693 | 0.0013522 | -0.0073999 | -0.0073593 | -0.0028712 | 54.7577 | 54.9637 | -68.5226 | 54.8996 | 54.7668 | 54.744 | 54.8538 | 54.9042 | 54.9271 | 8.4915 | -0.35706 | 0.13275 | 122.9233 | 123.0652 | -0.064087 | 76.6571 | 0.09613 | 123.2803 | 123.0194 | 123.0698 | 122.9324 | 123.1293 | 122.9233 | 123.0927 | 122.9095 | 76.6571 | 123.1293 | 122.9233 | 122.9095 | 122.9324 | 123.0927 | -123.3536 | -46.3394
4026.7812 | 123.1201 | -68.161 | 54.7623 | 0.20195 | 0.014214 | 0.0070283 | 0.010752 | -0.0093225 | -0.0084273 | -0.0028712 | 54.7806 | 54.9454 | -68.5181 | 54.9591 | 54.7348 | 54.7348 | 54.7852 | 54.8538 | 54.8904 | 8.4915 | -0.35706 | 0.18311 | 122.9416 | 123.1201 | -0.027466 | 76.6525 | 0.12817 | 123.2986 | 122.9462 | 123.0148 | 122.8958 | 123.1064 | 122.9416 | 123.0515 | 122.8958 | 76.6525 | 123.1064 | 122.9416 | 122.8958 | 122.8958 | 123.0515 | -123.2803 | -46.2708
4027.7656 | 123.1018 | -68.1427 | 54.8218 | -0.034561 | 0.013146 | 0.0031831 | 0.0075472 | -0.010604 | -0.0062911 | -0.0047938 | 54.7989 | 54.9728 | -68.5181 | 54.9957 | 54.7852 | 54.7485 | 54.9042 | 54.9133 | 54.9271 | 8.4961 | -0.37537 | 0.15106 | 122.9416 | 123.1384 | -0.036621 | 76.6388 | 0.10529 | 123.317 | 123.0469 | 123.056 | 122.9279 | 123.1155 | 122.9416 | 123.0698 | 122.8912 | 76.6388 | 123.1155 | 122.9416 | 122.8912 | 122.9279 | 123.0698 | -123.3398 | -46.3257
4028.7656 | 123.1201 | -68.1702 | 54.8264 | -0.11848 | 0.016137 | 0.0040375 | 0.0069064 | -0.0086817 | -0.0067185 | -0.0022302 | 54.7806 | 54.982 | -68.4952 | 54.982 | 54.7852 | 54.7668 | 54.8859 | 54.9133 | 54.9133 | 8.4961 | -0.32501 | 0.15564 | 122.9507 | 123.1522 | -0.041199 | 76.6663 | 0.086975 | 123.2758 | 123.056 | 123.0835 | 122.9553 | 123.1522 | 122.9507 | 123.0835 | 122.937 | 76.6663 | 123.1522 | 122.9507 | 122.937 | 122.9553 | 123.0835 | -123.3215 | -46.3303
4029.7812 | 123.1384 | -68.1519 | 54.8355 | -0.095596 | 0.01336 | 0.0076691 | 0.008829 | -0.0084681 | -0.0060775 | -0.001803 | 54.8447 | 54.9683 | -68.5089 | 55.014 | 54.8218 | 54.7943 | 54.8218 | 54.9408 | 54.8996 | 8.4961 | -0.35706 | 0.13275 | 122.9965 | 123.1659 | -0.013733 | 76.6479 | 0.064087 | 123.3536 | 122.9736 | 123.0927 | 122.9736 | 123.1201 | 122.9965 | 123.0515 | 122.9462 | 76.6479 | 123.1201 | 122.9965 | 122.9462 | 122.9736 | 123.0515 | -123.3444 | -46.3394
4030.7656 | 123.1293 | -68.1747 | 54.7989 | 0.049362 | 0.01571 | 0.0031831 | 0.01182 | -0.0048365 | -0.0056503 | -0.0015894 | 54.8264 | 54.9728 | -68.5043 | 54.9728 | 54.7531 | 54.7485 | 54.8264 | 54.895 | 54.895 | 8.4869 | -0.32959 | 0.17395 | 123.0011 | 123.1476 | -0.045776 | 76.6617 | 0.096131 | 123.3307 | 123.0011 | 123.0698 | 122.9279 | 123.1476 | 123.0011 | 123.0698 | 122.9233 | 76.6617 | 123.1476 | 123.0011 | 122.9233 | 122.9279 | 123.0698 | -123.3032 | -46.312
4031.7656 | 123.0743 | -68.1793 | 54.8126 | 0.11803 | 0.015496 | 0.0048921 | 0.0098972 | -0.0052637 | -0.0082137 | -0.0028712 | 54.7897 | 54.982 | -68.5226 | 54.9683 | 54.744 | 54.7394 | 54.8264 | 54.8676 | 54.9133 | 8.4961 | -0.34332 | 0.16937 | 122.9691 | 123.1476 | -0.068664 | 76.6754 | 0.10071 | 123.3124 | 123.0057 | 123.0469 | 122.9233 | 123.1613 | 122.9691 | 123.0927 | 122.9187 | 76.6754 | 123.1613 | 122.9691 | 122.9187 | 122.9233 | 123.0927 | -123.3353 | -46.3165
4032.7656 | 123.1384 | -68.129 | 54.8172 | -0.12611 | 0.014001 | 0.0029693 | 0.0064792 | -0.0065455 | -0.0062911 | -0.00094839 | 54.8447 | 55.0003 | -68.4952 | 55.0186 | 54.8264 | 54.7989 | 54.8447 | 54.95 | 54.9362 | 8.4915 | -0.36621 | 0.1831 | 122.9736 | 123.1476 | 0.009155 | 76.6205 | 0.11902 | 123.3398 | 122.9736 | 123.0789 | 122.9553 | 123.1293 | 122.9736 | 123.0652 | 122.9279 | 76.6205 | 123.1293 | 122.9736 | 122.9279 | 122.9553 | 123.0652 | -123.3124 | -46.3257
4033.7656 | 123.1476 | -68.1702 | 54.8035 | -0.080337 | 0.012292 | 0.0072419 | 0.00712 | -0.0065455 | -0.0088547 | -0.003512 | 54.8401 | 54.9957 | -68.4906 | 54.9957 | 54.7989 | 54.7852 | 54.8264 | 54.9454 | 54.9133 | 8.5007 | -0.32044 | 0.19226 | 123.0103 | 123.1659 | -0.004578 | 76.6708 | 0.10986 | 123.3307 | 122.9965 | 123.1155 | 122.9691 | 123.1659 | 123.0103 | 123.0835 | 122.9553 | 76.6708 | 123.1659 | 123.0103 | 122.9553 | 122.9691 | 123.0835 | -123.2941 | -46.3028
4034.7656 | 123.1338 | -68.1564 | 54.8035 | -0.080337 | 0.01571 | 0.0066009 | 0.0077608 | -0.0041955 | -0.0056503 | -0.0026574 | 54.863 | 54.9728 | -68.5135 | 54.9866 | 54.7943 | 54.7806 | 54.7989 | 54.9362 | 54.9042 | 8.4915 | -0.35706 | 0.16937 | 123.0194 | 123.143 | -0.009155 | 76.6479 | 0.10071 | 123.3765 | 122.9553 | 123.0927 | 122.9507 | 123.1293 | 123.0194 | 123.0606 | 122.937 | 76.6479 | 123.1293 | 123.0194 | 122.937 | 122.9507 | 123.0606 | -123.317 | -46.312
4035.7812 | 123.0881 | -68.1747 | 54.7943 | 0.11803 | 0.016351 | 0.011514 | 0.0081882 | -0.0046229 | -0.0077865 | -0.0013758 | 54.7852 | 54.9728 | -68.5226 | 54.9362 | 54.7256 | 54.7119 | 54.8447 | 54.8538 | 54.9271 | 8.4915 | -0.3479 | 0.17853 | 122.9599 | 123.111 | -0.068665 | 76.6663 | 0.13275 | 123.3078 | 123.0194 | 123.0286 | 122.9004 | 123.1476 | 122.9599 | 123.1018 | 122.8867 | 76.6663 | 123.1476 | 122.9599 | 122.8867 | 122.9004 | 123.1018 | -123.317 | -46.3028
4036.7812 | 123.0835 | -68.1885 | 54.7943 | 0.10277 | 0.01571 | 0.0051057 | 0.008829 | -0.0073999 | -0.0058639 | -0.003512 | 54.7943 | 54.9591 | -68.5364 | 54.9271 | 54.7256 | 54.7211 | 54.8355 | 54.8401 | 54.9271 | 8.4961 | -0.3479 | 0.16479 | 122.9828 | 123.1155 | -0.068665 | 76.6846 | 0.13275 | 123.3307 | 123.024 | 123.0286 | 122.9141 | 123.1476 | 122.9828 | 123.1155 | 122.9095 | 76.6846 | 123.1476 | 122.9828 | 122.9095 | 122.9141 | 123.1155 | -123.3307 | -46.2982
4037.7656 | 123.1293 | -68.1747 | 54.7714 | 0.22484 | 0.014855 | 0.0080963 | 0.0064792 | -0.0056909 | -0.0060775 | -0.0020166 | 54.7806 | 54.95 | -68.5135 | 54.9454 | 54.7577 | 54.7623 | 54.7668 | 54.8767 | 54.8813 | 8.5007 | -0.33875 | 0.17853 | 122.9553 | 123.1201 | -0.013733 | 76.6754 | 0.10986 | 123.2941 | 122.9416 | 123.0515 | 122.9324 | 123.1247 | 122.9553 | 123.056 | 122.937 | 76.6754 | 123.1247 | 122.9553 | 122.937 | 122.9324 | 123.056 | -123.2849 | -46.2708
4038.7656 | 123.1796 | -68.1839 | 54.7714 | 0.30876 | 0.014001 | 0.0083099 | 0.005411 | -0.0078271 | -0.0062911 | -0.0026574 | 54.7852 | 54.9545 | -68.5455 | 54.9637 | 54.7577 | 54.7668 | 54.7348 | 54.8996 | 54.8676 | 8.4915 | -0.36163 | 0.18311 | 122.9691 | 123.1476 | -0.013733 | 76.6754 | 0.096131 | 123.3307 | 122.9187 | 123.0835 | 122.9416 | 123.1384 | 122.9691 | 123.0515 | 122.9507 | 76.6754 | 123.1384 | 122.9691 | 122.9507 | 122.9416 | 123.0515 | -123.317 | -46.2799
4039.7656 | 123.0881 | -68.1656 | 54.8035 | 0.10277 | 0.016351 | 0.0089509 | 0.0084018 | -0.0054773 | -0.0054367 | -0.0043664 | 54.7989 | 54.982 | -68.5272 | 54.9316 | 54.7211 | 54.7394 | 54.8401 | 54.8859 | 54.9225 | 8.4961 | -0.36163 | 0.17853 | 122.9645 | 123.0972 | -0.082398 | 76.6617 | 0.11902 | 123.3261 | 123.0057 | 123.0515 | 122.8867 | 123.1476 | 122.9645 | 123.0881 | 122.905 | 76.6617 | 123.1476 | 122.9645 | 122.905 | 122.8867 | 123.0881 | -123.3307 | -46.3074
4040.7656 | 123.1064 | -68.1793 | 54.8035 | 0.10277 | 0.014428 | 0.0098053 | 0.00712 | -0.0050501 | -0.0041549 | -0.0026574 | 54.776 | 54.9591 | -68.5272 | 54.9179 | 54.7165 | 54.7165 | 54.8492 | 54.8538 | 54.9133 | 8.4915 | -0.3479 | 0.15564 | 122.9553 | 123.0972 | -0.086975 | 76.6708 | 0.10986 | 123.3032 | 123.0286 | 123.0331 | 122.8958 | 123.1384 | 122.9553 | 123.0927 | 122.8958 | 76.6708 | 123.1384 | 122.9553 | 122.8958 | 122.8958 | 123.0927 | -123.3307 | -46.312
4041.7656 | 123.1384 | -68.1747 | 54.8126 | 0.2935 | 0.014428 | 0.0089509 | 0.0086154 | -0.0069727 | -0.0080001 | -0.0011622 | 54.7852 | 54.95 | -68.5638 | 54.9316 | 54.7394 | 54.7211 | 54.8035 | 54.863 | 54.8813 | 8.5007 | -0.3891 | 0.13733 | 122.9599 | 123.1064 | -0.073242 | 76.6754 | 0.068665 | 123.349 | 122.9782 | 123.0377 | 122.9141 | 123.1247 | 122.9599 | 123.056 | 122.8958 | 76.6754 | 123.1247 | 122.9599 | 122.8958 | 122.9141 | 123.056 | -123.3765 | -46.312
4042.7812 | 123.2025 | -68.1473 | 54.7623 | 0.25536 | 0.016564 | 0.010873 | 0.0045566 | -0.0056909 | -0.0058639 | -0.0013758 | 54.8035 | 54.9088 | -68.5181 | 54.9728 | 54.7897 | 54.8035 | 54.689 | 54.9179 | 54.8813 | 8.4869 | -0.37079 | 0.14648 | 122.9507 | 123.1201 | 0.027466 | 76.6342 | 0.11902 | 123.3215 | 122.8363 | 123.0652 | 122.937 | 123.056 | 122.9507 | 123.0286 | 122.9507 | 76.6342 | 123.056 | 122.9507 | 122.9507 | 122.937 | 123.0286 | -123.2803 | -46.2753
4043.7812 | 123.2071 | -68.1519 | 54.7714 | 0.24773 | 0.014642 | 0.0070283 | 0.0069064 | -0.0059045 | -0.0056503 | -0.0020166 | 54.8401 | 54.895 | -68.5272 | 55.014 | 54.7852 | 54.8218 | 54.6707 | 54.9683 | 54.863 | 8.4869 | -0.37537 | 0.1236 | 122.9919 | 123.1659 | 0.013733 | 76.6388 | 0.091553 | 123.3673 | 122.8226 | 123.1201 | 122.937 | 123.0469 | 122.9919 | 123.0148 | 122.9736 | 76.6388 | 123.0469 | 122.9919 | 122.9736 | 122.937 | 123.0148 | -123.2986 | -46.2845
4044.7656 | 123.1934 | -68.1152 | 54.7714 | 0.18669 | 0.013574 | 0.0066009 | 0.0017794 | -0.0073999 | -0.0045821 | 0.00054681 | 54.7989 | 54.8721 | -68.5318 | 54.9866 | 54.7943 | 54.8126 | 54.6936 | 54.9728 | 54.8447 | 8.4961 | -0.41657 | 0.10071 | 122.9141 | 123.1018 | 0.022889 | 76.6113 | 0.073243 | 123.3307 | 122.8088 | 123.0881 | 122.9095 | 122.9874 | 122.9141 | 122.9599 | 122.9279 | 76.6113 | 122.9874 | 122.9141 | 122.9279 | 122.9095 | 122.9599 | -123.3032 | -46.2753
4045.7812 | 123.2025 | -68.1381 | 54.7714 | 0.23247 | 0.012078 | 0.0085235 | 0.0017794 | -0.0091089 | -0.0052231 | 0.0018286 | 54.808 | 54.8538 | -68.5455 | 55.0049 | 54.8035 | 54.8447 | 54.6616 | 54.9637 | 54.8538 | 8.4915 | -0.40741 | 0.082398 | 122.9462 | 123.143 | 0.032044 | 76.6296 | 0.082398 | 123.3536 | 122.7997 | 123.1018 | 122.9416 | 122.9919 | 122.9462 | 122.9919 | 122.9828 | 76.6296 | 122.9919 | 122.9462 | 122.9828 | 122.9416 | 122.9919 | -123.317 | -46.2799
4046.7812 | 123.175 | -68.1152 | 54.7989 | 0.12566 | 0.0095148 | 0.0033967 | 0.00049764 | -0.010818 | -0.0065047 | -0.0013758 | 54.7714 | 54.9042 | -68.5043 | 54.9866 | 54.8172 | 54.808 | 54.7348 | 54.9774 | 54.8584 | 8.4915 | -0.3891 | 0.10529 | 122.8867 | 123.1018 | 0.018311 | 76.6068 | 0.059509 | 123.2758 | 122.85 | 123.0927 | 122.9324 | 123.0194 | 122.8867 | 122.9736 | 122.9233 | 76.6068 | 123.0194 | 122.8867 | 122.9233 | 122.9324 | 122.9736 | -123.3032 | -46.3074
4047.7656 | 123.2162 | -68.1381 | 54.7668 | 0.17906 | 0.013574 | 0.0051057 | 0.0090426 | -0.011672 | -0.0058639 | -0.00073479 | 54.8401 | 54.895 | -68.5181 | 55.014 | 54.776 | 54.8218 | 54.6387 | 54.9637 | 54.8401 | 8.4915 | -0.37994 | 0.12817 | 122.9782 | 123.1522 | 0.009155 | 76.6296 | 0.073242 | 123.3582 | 122.7768 | 123.1018 | 122.9141 | 123.0331 | 122.9782 | 122.9782 | 122.9599 | 76.6296 | 123.0331 | 122.9782 | 122.9599 | 122.9141 | 122.9782 | -123.2849 | -46.2753
4048.7656 | 123.2025 | -68.1198 | 54.7668 | 0.2401 | 0.012933 | 0.0036103 | 0.0041292 | -0.011031 | -0.0060775 | -0.0011622 | 54.8264 | 54.8676 | -68.5226 | 55.0049 | 54.7943 | 54.8218 | 54.6524 | 54.9728 | 54.8447 | 8.4961 | -0.40283 | 0.10071 | 122.9462 | 123.1247 | 0.027466 | 76.6159 | 0.07782 | 123.349 | 122.7722 | 123.0927 | 122.9141 | 122.9874 | 122.9462 | 122.9645 | 122.9416 | 76.6159 | 122.9874 | 122.9462 | 122.9416 | 122.9141 | 122.9645 | -123.2895 | -46.2708
4049.7812 | 123.1934 | -68.1244 | 54.808 | 0.20195 | 0.013146 | 0.0027557 | 0.0028476 | -0.0084681 | -0.0018051 | -0.0043664 | 54.7714 | 54.8447 | -68.5181 | 55.0095 | 54.7852 | 54.7897 | 54.7119 | 54.95 | 54.863 | 8.4869 | -0.39368 | 0.036622 | 122.8958 | 123.1338 | -0.022888 | 76.6113 | 0.054932 | 123.2895 | 122.8363 | 123.0743 | 122.9095 | 122.9691 | 122.8958 | 122.9874 | 122.9141 | 76.6113 | 122.9691 | 122.8958 | 122.9141 | 122.9095 | 122.9874 | -123.3261 | -46.3211
4050.7656 | 123.2254 | -68.1015 | 54.7852 | -0.04219 | 0.0090876 | 0.0055329 | 0.0022066 | -0.012527 | -0.0056503 | -0.0022302 | 54.7989 | 54.8538 | -68.4998 | 55.0369 | 54.8447 | 54.8447 | 54.7348 | 55.0186 | 54.8584 | 8.4961 | -0.39826 | 0.068665 | 122.9004 | 123.1384 | 0.05951 | 76.5976 | 0.073242 | 123.2986 | 122.8363 | 123.1201 | 122.9462 | 122.9553 | 122.9004 | 122.9599 | 122.9462 | 76.5976 | 122.9553 | 122.9004 | 122.9462 | 122.9462 | 122.9599 | -123.2849 | -46.2891
4051.7656 | 123.2483 | -68.1152 | 54.8035 | -0.072708 | 0.010583 | 0.0048921 | 0.0028476 | -0.012313 | -0.0054367 | -0.0030848 | 54.8264 | 54.863 | -68.486 | 55.0552 | 54.8309 | 54.8538 | 54.7119 | 55.0278 | 54.8584 | 8.4961 | -0.37079 | 0.059509 | 122.9416 | 123.1705 | 0.027466 | 76.6113 | 0.054931 | 123.3124 | 122.8271 | 123.143 | 122.9462 | 122.9782 | 122.9416 | 122.9736 | 122.9691 | 76.6113 | 122.9782 | 122.9416 | 122.9691 | 122.9462 | 122.9736 | -123.2895 | -46.3074
4052.7656 | 123.2254 | -68.0969 | 54.7852 | -0.080337 | 0.009942 | 0.0053193 | 0.0015658 | -0.012527 | -0.0077865 | -0.0015894 | 54.8401 | 54.8447 | -68.4906 | 55.0873 | 54.8813 | 54.8584 | 54.7028 | 55.0644 | 54.8676 | 8.4961 | -0.39368 | 0.05951 | 122.937 | 123.1842 | 0.096131 | 76.593 | 0.082398 | 123.3307 | 122.7997 | 123.1613 | 122.9782 | 122.9416 | 122.937 | 122.9645 | 122.9553 | 76.593 | 122.9416 | 122.937 | 122.9553 | 122.9782 | 122.9645 | -123.2758 | -46.2891
4053.7656 | 123.2025 | -68.1061 | 54.7897 | 0.1104 | 0.012078 | 0.0019013 | 0.003702 | -0.012313 | -0.0062911 | -0.0020166 | 54.7668 | 54.8447 | -68.4906 | 54.9866 | 54.7806 | 54.776 | 54.7211 | 54.9637 | 54.8584 | 8.4915 | -0.38452 | 0.054932 | 122.8729 | 123.0927 | -0.009155 | 76.5976 | 0.068664 | 123.2574 | 122.8271 | 123.0698 | 122.8867 | 122.9507 | 122.8729 | 122.9645 | 122.8821 | 76.5976 | 122.9507 | 122.8729 | 122.8821 | 122.8867 | 122.9645 | -123.2803 | -46.2982
4054.7656 | 123.1979 | -68.129 | 54.776 | 0.095139 | 0.01101 | 0.0029693 | 0.0039156 | -0.011886 | -0.0035141 | -0.001803 | 54.7806 | 54.8584 | -68.5181 | 55.0644 | 54.7256 | 54.7943 | 54.6799 | 54.95 | 54.8492 | 8.4915 | -0.3891 | 0.082397 | 122.9095 | 123.1934 | -0.050354 | 76.6205 | 0.073242 | 123.2986 | 122.8088 | 123.0789 | 122.8546 | 122.9874 | 122.9095 | 122.9782 | 122.9233 | 76.6205 | 122.9874 | 122.9095 | 122.9233 | 122.8546 | 122.9782 | -123.2941 | -46.2845
4055.7656 | 123.2208 | -68.1107 | 54.7852 | -0.04219 | 0.0097284 | 0.0044647 | 0.0022066 | -0.012527 | -0.0050095 | -0.0022302 | 54.808 | 54.8447 | -68.4952 | 55.0552 | 54.8309 | 54.8401 | 54.7073 | 55.0232 | 54.863 | 8.4915 | -0.38452 | 0.05951 | 122.9187 | 123.1659 | 0.045777 | 76.6022 | 0.07782 | 123.3032 | 122.818 | 123.1338 | 122.9416 | 122.9553 | 122.9187 | 122.9736 | 122.9507 | 76.6022 | 122.9553 | 122.9187 | 122.9507 | 122.9416 | 122.9736 | -123.2803 | -46.2936
4056.7812 | 123.1522 | -68.1244 | 54.8355 | -0.15663 | 0.014428 | 0.0031831 | 0.010538 | -0.0091089 | -0.0045821 | -0.0032984 | 54.863 | 54.9866 | -68.486 | 55.0461 | 54.7668 | 54.7531 | 54.7989 | 54.9454 | 54.8904 | 8.4824 | -0.36163 | 0.15106 | 122.9874 | 123.1705 | -0.068664 | 76.6068 | 0.054932 | 123.349 | 122.9233 | 123.0698 | 122.8912 | 123.111 | 122.9874 | 123.0148 | 122.8775 | 76.6068 | 123.111 | 122.9874 | 122.8775 | 122.8912 | 123.0148 | -123.3215 | -46.3531
4057.7656 | 123.1293 | -68.1519 | 54.8309 | -0.20241 | 0.011437 | 0.0021149 | 0.0047702 | -0.010604 | -0.0054367 | -0.0015894 | 54.7943 | 54.9133 | -68.5181 | 54.9957 | 54.7897 | 54.7531 | 54.8859 | 54.9454 | 54.9408 | 8.4915 | -0.36621 | 0.082397 | 122.9462 | 123.1476 | -0.041199 | 76.6434 | 0.10986 | 123.3124 | 123.0377 | 123.0972 | 122.9416 | 123.0652 | 122.9462 | 123.0927 | 122.905 | 76.6434 | 123.0652 | 122.9462 | 122.905 | 122.9416 | 123.0927 | -123.349 | -46.3394
4058.7656 | 123.1247 | -68.1473 | 54.8584 | -0.057449 | 0.010583 | 0.0048921 | 0.0073336 | -0.0095361 | -0.0071457 | -0.0026574 | 54.7806 | 54.9408 | -68.4952 | 54.9957 | 54.776 | 54.7485 | 54.9133 | 54.9362 | 54.9408 | 8.5007 | -0.3479 | 0.082398 | 122.9279 | 123.143 | -0.082397 | 76.6479 | 0.082398 | 123.2758 | 123.0606 | 123.0835 | 122.9233 | 123.0881 | 122.9279 | 123.0881 | 122.8958 | 76.6479 | 123.0881 | 122.9279 | 122.8958 | 122.9233 | 123.0881 | -123.3536 | -46.3577
4059.7656 | 123.1018 | -68.161 | 54.8401 | -0.19478 | 0.012505 | 0.0031831 | 0.0039156 | -0.012527 | -0.0069321 | -0.0026574 | 54.7852 | 54.9545 | -68.5043 | 54.9225 | 54.7165 | 54.7531 | 54.8492 | 54.8904 | 54.8996 | 8.5007 | -0.34332 | 0.11444 | 122.9462 | 123.0835 | -0.1236 | 76.6617 | 0.059509 | 123.2895 | 123.0103 | 123.0515 | 122.8775 | 123.1155 | 122.9462 | 123.0606 | 122.9141 | 76.6617 | 123.1155 | 122.9462 | 122.9141 | 122.8775 | 123.0606 | -123.3444 | -46.3394
4060.7656 | 123.2346 | -68.1198 | 54.8218 | -0.14137 | 0.013574 | -0.00044854 | 0.0017794 | -0.0095361 | -0.0056503 | -0.0028712 | 54.863 | 54.8676 | -68.4723 | 55.0827 | 54.8676 | 54.8584 | 54.7485 | 55.0552 | 54.895 | 8.4961 | -0.35248 | 0.045777 | 122.9828 | 123.2025 | 0.045777 | 76.6159 | 0.073243 | 123.3353 | 122.8683 | 123.175 | 122.9874 | 122.9874 | 122.9828 | 123.0148 | 122.9782 | 76.6159 | 122.9874 | 122.9828 | 122.9782 | 122.9874 | 123.0148 | -123.2941 | -46.3257
4061.7812 | 123.111 | -68.1702 | 54.8401 | 0.095139 | 0.014001 | 0.0091645 | 0.012247 | -0.0086817 | -0.0056503 | -0.0032984 | 54.8355 | 54.9728 | -68.5181 | 55.0003 | 54.7302 | 54.7119 | 54.8218 | 54.8813 | 54.9088 | 8.4961 | -0.3479 | 0.13275 | 123.0057 | 123.1705 | -0.10986 | 76.6663 | 0.068664 | 123.3536 | 122.9919 | 123.0515 | 122.9004 | 123.143 | 123.0057 | 123.0789 | 122.8821 | 76.6663 | 123.143 | 123.0057 | 122.8821 | 122.9004 | 123.0789 | -123.3582 | -46.344
4062.7656 | 123.1155 | -68.1564 | 54.8447 | -0.019302 | 0.013574 | 0.0029693 | 0.0066928 | -0.010818 | -0.0056503 | -0.0030848 | 54.7852 | 54.9545 | -68.5043 | 54.9957 | 54.7897 | 54.7577 | 54.9042 | 54.9408 | 54.9454 | 8.4915 | -0.3479 | 0.10986 | 122.9416 | 123.1522 | -0.054932 | 76.6479 | 0.10071 | 123.2895 | 123.0606 | 123.0972 | 122.9462 | 123.111 | 122.9416 | 123.1018 | 122.9141 | 76.6479 | 123.111 | 122.9416 | 122.9141 | 122.9462 | 123.1018 | -123.349 | -46.3531
4063.7812 | 123.1476 | -68.1564 | 54.8309 | -0.15663 | 0.013146 | 0.0074555 | 0.0073336 | -0.0088953 | -0.0086411 | -0.0037256 | 54.8126 | 54.982 | -68.5181 | 55.0003 | 54.7989 | 54.7623 | 54.8904 | 54.9362 | 54.9545 | 8.4961 | -0.36163 | 0.15106 | 122.9691 | 123.1567 | -0.032044 | 76.6525 | 0.1236 | 123.3307 | 123.0469 | 123.0927 | 122.9553 | 123.1384 | 122.9691 | 123.111 | 122.9187 | 76.6525 | 123.1384 | 122.9691 | 122.9187 | 122.9553 | 123.111 | -123.349 | -46.3348
4064.7656 | 123.1338 | -68.1427 | 54.8126 | -0.56862 | 0.013787 | 0.0089509 | 0.0094698 | -0.0056909 | -0.0075729 | -0.0032984 | 54.8767 | 54.9728 | -68.5226 | 55.0415 | 54.8035 | 54.7806 | 54.8172 | 54.9133 | 54.8996 | 8.4961 | -0.37994 | 0.16022 | 123.0194 | 123.1842 | -0.009155 | 76.6388 | 0.086975 | 123.3994 | 122.9599 | 123.056 | 122.9462 | 123.1155 | 123.0194 | 123.0423 | 122.9233 | 76.6388 | 123.1155 | 123.0194 | 122.9233 | 122.9462 | 123.0423 | -123.3353 | -46.3165
4065.7656 | 123.1384 | -68.1656 | 54.8126 | 0.0035856 | 0.014214 | 0.0083099 | 0.0084018 | -0.0054773 | -0.0067185 | -0.0011622 | 54.8538 | 54.982 | -68.5226 | 55.014 | 54.7897 | 54.7577 | 54.8172 | 54.8996 | 54.9271 | 8.4915 | -0.35706 | 0.16937 | 123.0194 | 123.1796 | -0.022888 | 76.6571 | 0.11444 | 123.3765 | 122.9828 | 123.0652 | 122.9553 | 123.1476 | 123.0194 | 123.0927 | 122.9233 | 76.6571 | 123.1476 | 123.0194 | 122.9233 | 122.9553 | 123.0927 | -123.3353 | -46.3211
4066.7812 | 123.2346 | -68.1381 | 54.7668 | 0.23247 | 0.012292 | 0.0083099 | 0.005411 | -0.0082545 | -0.0054367 | -0.0011622 | 54.8492 | 54.8859 | -68.5181 | 55.0278 | 54.8492 | 54.8172 | 54.3915 | 55.0781 | 54.8401 | 8.4915 | -0.37994 | 0.11902 | 122.9874 | 123.1659 | 0.082397 | 76.6296 | 0.073242 | 123.3673 | 122.5296 | 123.2162 | 122.9874 | 123.024 | 122.9874 | 122.9782 | 122.9553 | 76.6296 | 123.024 | 122.9874 | 122.9553 | 122.9874 | 122.9782 | -123.2849 | -46.2753
4067.7656 | 123.143 | -68.1656 | 54.8355 | -0.13374 | 0.015496 | 0.0068147 | 0.0069064 | -0.0082545 | -0.0065047 | -0.00094839 | 54.8355 | 54.9774 | -68.5181 | 55.0232 | 54.7989 | 54.7943 | 54.8721 | 54.9591 | 54.9225 | 8.4915 | -0.35248 | 0.14191 | 123.0011 | 123.1888 | -0.036621 | 76.6571 | 0.086975 | 123.3536 | 123.0377 | 123.1247 | 122.9645 | 123.143 | 123.0011 | 123.0881 | 122.9599 | 76.6571 | 123.143 | 123.0011 | 122.9599 | 122.9645 | 123.0881 | -123.3536 | -46.344
4068.7656 | 123.1613 | -68.161 | 54.8126 | -0.11848 | 0.014428 | 0.0048921 | 0.0090426 | -0.0063317 | -0.0047957 | -0.0024438 | 54.8401 | 55.0049 | -68.5135 | 55.0323 | 54.8035 | 54.7943 | 54.8401 | 54.9545 | 54.9362 | 8.4961 | -0.35248 | 0.19226 | 123.0011 | 123.1934 | -0.009155 | 76.6571 | 0.1236 | 123.3536 | 123.0011 | 123.1155 | 122.9645 | 123.1659 | 123.0011 | 123.0972 | 122.9553 | 76.6571 | 123.1659 | 123.0011 | 122.9553 | 122.9645 | 123.0972 | -123.3261 | -46.3165
4069.7656 | 123.1567 | -68.1747 | 54.8035 | 0.018845 | 0.014642 | 0.0046783 | 0.0090426 | -0.0061181 | -0.0062911 | -0.00094839 | 54.8676 | 54.9866 | -68.5043 | 55.014 | 54.7897 | 54.776 | 54.8264 | 54.9133 | 54.9133 | 8.4869 | -0.32959 | 0.18311 | 123.0423 | 123.1888 | -0.013733 | 76.6617 | 0.10986 | 123.3719 | 123.0011 | 123.0881 | 122.9645 | 123.1613 | 123.0423 | 123.0881 | 122.9507 | 76.6617 | 123.1613 | 123.0423 | 122.9507 | 122.9645 | 123.0881 | -123.3078 | -46.3165
4070.7812 | 123.0972 | -68.1839 | 54.7897 | 0.095139 | 0.015283 | 0.012155 | 0.011179 | -0.0067591 | -0.0050095 | -0.0020166 | 54.808 | 54.982 | -68.5501 | 54.9362 | 54.7394 | 54.7073 | 54.8584 | 54.8492 | 54.9454 | 8.4915 | -0.36621 | 0.19226 | 122.9919 | 123.1201 | -0.050354 | 76.6754 | 0.15564 | 123.3582 | 123.0423 | 123.0331 | 122.9233 | 123.1659 | 122.9919 | 123.1293 | 122.8912 | 76.6754 | 123.1659 | 122.9919 | 122.8912 | 122.9233 | 123.1293 | -123.3398 | -46.2982
4071.7656 | 123.1934 | -68.1702 | 54.7806 | 0.24773 | 0.013787 | 0.0068147 | 0.00712 | -0.0054773 | -0.0067185 | 0.00097421 | 54.776 | 54.9637 | -68.5501 | 54.9728 | 54.776 | 54.776 | 54.744 | 54.8904 | 54.895 | 8.4869 | -0.37994 | 0.1831 | 122.9462 | 123.143 | -0.004578 | 76.6571 | 0.11444 | 123.3261 | 122.9141 | 123.0606 | 122.9462 | 123.1338 | 122.9462 | 123.0652 | 122.9462 | 76.6571 | 123.1338 | 122.9462 | 122.9462 | 122.9462 | 123.0652 | -123.3307 | -46.2936
4072.7656 | 123.2162 | -68.1519 | 54.776 | 0.24773 | 0.014855 | 0.0093781 | 0.0049838 | -0.0065455 | -0.0015915 | -0.00094839 | 54.7989 | 54.95 | -68.5364 | 54.9957 | 54.8218 | 54.8035 | 54.6936 | 54.9362 | 54.8538 | 8.4915 | -0.38452 | 0.17395 | 122.9507 | 123.1476 | 0.045776 | 76.6434 | 0.07782 | 123.3353 | 122.8455 | 123.0881 | 122.9736 | 123.1018 | 122.9507 | 123.0057 | 122.9553 | 76.6434 | 123.1018 | 122.9507 | 122.9553 | 122.9736 | 123.0057 | -123.3124 | -46.2845
4073.7656 | 123.2391 | -68.161 | 54.7623 | 0.2401 | 0.014855 | 0.0074555 | 0.004343 | -0.0056909 | -0.0058639 | 0.00076041 | 54.8447 | 54.9042 | -68.5318 | 55.0232 | 54.8126 | 54.8447 | 54.6799 | 54.9545 | 54.8538 | 8.5007 | -0.37079 | 0.14191 | 123.0057 | 123.1842 | 0.050354 | 76.6617 | 0.091553 | 123.3765 | 122.8409 | 123.1155 | 122.9736 | 123.0652 | 123.0057 | 123.0148 | 123.0057 | 76.6617 | 123.0652 | 123.0057 | 123.0057 | 122.9736 | 123.0148 | -123.2941 | -46.2616
4074.7656 | 123.1338 | -68.1839 | 54.7989 | 0.15617 | 0.013574 | 0.0074555 | 0.00712 | -0.0069727 | -0.0058639 | -0.0024438 | 54.7668 | 54.9866 | -68.541 | 54.9271 | 54.7211 | 54.7302 | 54.8218 | 54.8447 | 54.8996 | 8.4961 | -0.35706 | 0.18768 | 122.9507 | 123.111 | -0.07782 | 76.68 | 0.10071 | 123.3078 | 123.0057 | 123.0286 | 122.905 | 123.1705 | 122.9507 | 123.0835 | 122.9141 | 76.68 | 123.1705 | 122.9507 | 122.9141 | 122.905 | 123.0835 | -123.3398 | -46.3028
4075.7656 | 123.1567 | -68.1885 | 54.808 | 0.20958 | 0.015923 | 0.0053193 | 0.0077608 | -0.0073999 | -0.0028731 | 0.0014014 | 54.7806 | 54.95 | -68.5455 | 54.95 | 54.7485 | 54.7623 | 54.7714 | 54.8904 | 54.895 | 8.4915 | -0.35705 | 0.14191 | 122.9691 | 123.1384 | -0.059509 | 76.68 | 0.086976 | 123.3261 | 122.9599 | 123.0789 | 122.937 | 123.1384 | 122.9691 | 123.0835 | 122.9507 | 76.68 | 123.1384 | 122.9691 | 122.9507 | 122.937 | 123.0835 | -123.3536 | -46.3165
4076.7812 | 123.2162 | -68.1427 | 54.7577 | 0.25536 | 0.012292 | 0.0078827 | 0.0064792 | -0.0078271 | -0.0050095 | -0.00073479 | 54.8309 | 54.8904 | -68.5089 | 55.0278 | 54.8218 | 54.8447 | 54.6433 | 54.9774 | 54.8492 | 8.4915 | -0.36621 | 0.13275 | 122.9736 | 123.1705 | 0.064087 | 76.6342 | 0.091553 | 123.3398 | 122.786 | 123.1201 | 122.9645 | 123.0331 | 122.9736 | 122.9919 | 122.9874 | 76.6342 | 123.0331 | 122.9736 | 122.9874 | 122.9645 | 122.9919 | -123.2666 | -46.2662
4077.7812 | 123.2391 | -68.1061 | 54.776 | 0.25536 | 0.012078 | 0.0063873 | 0.0032748 | -0.0069727 | -0.0043685 | 0.0024694 | 54.8309 | 54.8767 | -68.5501 | 54.9316 | 54.6387 | 54.8767 | 54.7714 | 55.0369 | 54.8538 | 8.4915 | -0.44403 | 0.10071 | 122.937 | 123.0377 | -0.13733 | 76.5976 | 0.07782 | 123.381 | 122.8775 | 123.143 | 122.7448 | 122.9828 | 122.937 | 122.9599 | 122.9828 | 76.5976 | 122.9828 | 122.937 | 122.9828 | 122.7448 | 122.9599 | -123.3261 | -46.2845
4078.7656 | 123.1842 | -68.1519 | 54.8035 | 0.15617 | 0.0095148 | 0.0046783 | 0.0015658 | -0.0099633 | -0.0047957 | -0.0022302 | 54.7897 | 54.895 | -68.5181 | 55.0003 | 54.8035 | 54.808 | 54.744 | 54.9728 | 54.8584 | 8.4961 | -0.36621 | 0.091553 | 122.9416 | 123.1522 | 0 | 76.6479 | 0.054931 | 123.3078 | 122.8958 | 123.1247 | 122.9553 | 123.0469 | 122.9416 | 123.0103 | 122.9599 | 76.6479 | 123.0469 | 122.9416 | 122.9599 | 122.9553 | 123.0103 | -123.3215 | -46.3074
4079.7656 | 123.1888 | -68.1564 | 54.7852 | 0.064621 | 0.012505 | 0.0033967 | 0.0024202 | -0.0093225 | -0.0065047 | -0.0020166 | 54.776 | 54.895 | -68.5135 | 54.9866 | 54.7806 | 54.808 | 54.7394 | 54.9728 | 54.863 | 8.4824 | -0.35706 | 0.10986 | 122.9324 | 123.143 | -0.004577 | 76.6388 | 0.07782 | 123.2895 | 122.8958 | 123.1293 | 122.937 | 123.0515 | 122.9324 | 123.0194 | 122.9645 | 76.6388 | 123.0515 | 122.9324 | 122.9645 | 122.937 | 123.0194 | -123.2986 | -46.3028
4080.7656 | 123.1842 | -68.1427 | 54.7806 | 0.14854 | 0.012078 | 0.00083306 | 0.0024202 | -0.011459 | -0.0082137 | -0.003512 | 54.7806 | 54.8904 | -68.5272 | 54.9957 | 54.8035 | 54.9408 | 54.6936 | 54.9637 | 54.8767 | 8.4915 | -0.38452 | 0.10986 | 122.9233 | 123.1384 | 0.022888 | 76.6342 | 0.09613 | 123.3078 | 122.8363 | 123.1064 | 122.9462 | 123.0331 | 122.9233 | 123.0194 | 123.0835 | 76.6342 | 123.0331 | 122.9233 | 123.0835 | 122.9462 | 123.0194 | -123.3078 | -46.2891
4081.7656 | 123.23 | -68.1564 | 54.7714 | 0.056992 | 0.014855 | 0.0033967 | 0.0090426 | -0.011031 | -0.0033005 | -0.0020166 | 54.8538 | 54.8721 | -68.5089 | 55.0186 | 54.8126 | 54.8264 | 54.6616 | 54.9866 | 54.8401 | 8.5007 | -0.35248 | 0.10071 | 123.0103 | 123.175 | 0.041199 | 76.6571 | 0.068665 | 123.3627 | 122.818 | 123.143 | 122.9691 | 123.0286 | 123.0103 | 122.9965 | 122.9828 | 76.6571 | 123.0286 | 123.0103 | 122.9828 | 122.9691 | 122.9965 | -123.2803 | -46.2708
4082.7656 | 123.1979 | -68.1061 | 54.7943 | 0.19432 | 0.011224 | 0.0044647 | 0.0045566 | -0.013381 | -0.0075729 | -0.0037256 | 54.776 | 54.8492 | -68.5181 | 54.9911 | 54.776 | 54.8035 | 54.7119 | 54.9683 | 54.8492 | 8.4915 | -0.41199 | 0.054931 | 122.8821 | 123.0972 | -0.018311 | 76.5976 | 0.054931 | 123.2941 | 122.818 | 123.0743 | 122.8821 | 122.9553 | 122.8821 | 122.9553 | 122.9095 | 76.5976 | 122.9553 | 122.8821 | 122.9095 | 122.8821 | 122.9553 | -123.3124 | -46.3028
4083.7812 | 123.1842 | -68.1335 | 54.7897 | 0.11803 | 0.010583 | 0.0029693 | 0.0041292 | -0.012527 | -0.0041549 | -0.0015894 | 54.7714 | 54.8584 | -68.5272 | 55.0095 | 54.7989 | 54.808 | 54.7394 | 54.9911 | 54.8721 | 8.4915 | -0.39368 | 0.068664 | 122.905 | 123.143 | 0.009155 | 76.6251 | 0.082397 | 123.2986 | 122.8729 | 123.1247 | 122.9324 | 122.9919 | 122.905 | 123.0057 | 122.9416 | 76.6251 | 122.9919 | 122.905 | 122.9416 | 122.9324 | 123.0057 | -123.317 | -46.2982
4084.7812 | 123.23 | -68.1198 | 54.808 | 0.056992 | 0.010156 | 0.0040375 | 0.0015658 | -0.013381 | -0.0060775 | -0.0026574 | 54.7852 | 54.8676 | -68.5043 | 55.0415 | 54.8264 | 54.8309 | 54.7348 | 55.0095 | 54.8492 | 8.4915 | -0.38452 | 0.05951 | 122.905 | 123.1613 | 0.018311 | 76.6113 | 0.041199 | 123.2895 | 122.8546 | 123.1293 | 122.9462 | 122.9874 | 122.905 | 122.9691 | 122.9507 | 76.6113 | 122.9874 | 122.905 | 122.9507 | 122.9462 | 122.9691 | -123.3124 | -46.3165
4085.7656 | 123.2483 | -68.1152 | 54.8126 | -0.12611 | 0.010796 | 0.0040375 | 0.0060518 | -0.014449 | -0.0047957 | -0.0032984 | 54.863 | 54.8767 | -68.4631 | 54.9271 | 54.8584 | 54.8355 | 54.744 | 55.0461 | 54.8538 | 8.4915 | -0.3479 | 0.064087 | 122.9782 | 123.0423 | 0.045776 | 76.6068 | 0.041199 | 123.3261 | 122.8592 | 123.1613 | 122.9736 | 122.9919 | 122.9782 | 122.9691 | 122.9507 | 76.6068 | 122.9919 | 122.9782 | 122.9507 | 122.9736 | 122.9691 | -123.2758 | -46.3211
4086.7656 | 123.2208 | -68.0969 | 54.8309 | -0.24818 | 0.010156 | 0.0012605 | 0.0011386 | -0.014236 | -0.0054367 | -0.0032984 | 54.8309 | 54.863 | -68.4998 | 55.0827 | 54.8676 | 54.8676 | 54.7485 | 55.0644 | 54.895 | 8.4961 | -0.40283 | 0.032043 | 122.9279 | 123.1796 | 0.036621 | 76.593 | 0.064087 | 123.3307 | 122.8455 | 123.1613 | 122.9645 | 122.9599 | 122.9279 | 122.9919 | 122.9645 | 76.593 | 122.9599 | 122.9279 | 122.9645 | 122.9645 | 122.9919 | -123.3307 | -46.3348
4087.7656 | 123.2437 | -68.1107 | 54.8172 | 0.041733 | 0.010156 | 0.0042511 | 0.0032748 | -0.014022 | -0.0056503 | -0.0047938 | 54.7852 | 54.8492 | -68.5226 | 55.0598 | 54.8355 | 54.8309 | 54.7119 | 55.014 | 54.8859 | 8.5007 | -0.41199 | 0.032043 | 122.8958 | 123.1705 | 0.01831 | 76.6113 | 0.068664 | 123.3078 | 122.8226 | 123.1247 | 122.9462 | 122.9599 | 122.8958 | 122.9965 | 122.9416 | 76.6113 | 122.9599 | 122.8958 | 122.9416 | 122.9462 | 122.9965 | -123.3398 | -46.3165
4088.7656 | 123.2437 | -68.1473 | 54.7852 | -0.011673 | 0.011651 | 0.0040375 | 0.00049764 | -0.011886 | -0.0067185 | -0.0039392 | 54.8172 | 54.8584 | -68.5043 | 55.069 | 54.8447 | 54.8447 | 54.7211 | 55.0232 | 54.8676 | 8.4915 | -0.35706 | 0.073242 | 122.9645 | 123.2162 | 0.05951 | 76.6388 | 0.082398 | 123.3215 | 122.8683 | 123.1705 | 122.9919 | 123.0057 | 122.9645 | 123.0148 | 122.9919 | 76.6388 | 123.0057 | 122.9645 | 122.9919 | 122.9919 | 123.0148 | -123.2895 | -46.2936
4089.7656 | 123.2391 | -68.1152 | 54.8218 | -0.149 | 0.0097284 | 0.0057465 | -0.003134 | -0.015731 | -0.0047957 | 0.00076041 | 54.863 | 54.8676 | -68.486 | 54.9911 | 54.8264 | 54.8035 | 54.7577 | 55.0095 | 54.8538 | 8.4915 | -0.37079 | 0.045777 | 122.9782 | 123.1064 | 0.004578 | 76.6068 | 0.032044 | 123.349 | 122.8729 | 123.1247 | 122.9416 | 122.9828 | 122.9782 | 122.9691 | 122.9187 | 76.6068 | 122.9828 | 122.9782 | 122.9187 | 122.9416 | 122.9691 | -123.3078 | -46.3303
4090.7812 | 123.1796 | -68.129 | 54.8676 | -0.18715 | 0.0090876 | 0.0072419 | 0.0062656 | -0.013168 | -0.0067185 | -0.0041528 | 54.8355 | 54.8996 | -68.4952 | 55.0644 | 54.8309 | 54.8035 | 54.8309 | 55.0049 | 54.9088 | 8.5007 | -0.36621 | 0.032043 | 122.9645 | 123.1934 | -0.036621 | 76.6296 | 0.041198 | 123.3307 | 122.9599 | 123.1338 | 122.9599 | 123.0286 | 122.9645 | 123.0377 | 122.9324 | 76.6296 | 123.0286 | 122.9645 | 122.9324 | 122.9599 | 123.0377 | -123.3627 | -46.3669
4091.7812 | 123.1247 | -68.1427 | 54.8584 | -0.18715 | 0.01101 | 0.0031831 | 0.00712 | -0.0121 | -0.0065047 | -0.0030848 | 54.8172 | 54.9316 | -68.5043 | 55.0507 | 54.8309 | 54.7668 | 54.8767 | 54.9683 | 54.9271 | 8.4915 | -0.36163 | 0.073243 | 122.9599 | 123.1934 | -0.027465 | 76.6342 | 0.068665 | 123.3215 | 123.0194 | 123.111 | 122.9736 | 123.0743 | 122.9599 | 123.0698 | 122.9095 | 76.6342 | 123.0743 | 122.9599 | 122.9095 | 122.9736 | 123.0698 | -123.3627 | -46.3669
4092.7656 | 123.1567 | -68.129 | 54.8355 | -0.13374 | 0.011651 | 0.0044647 | 0.0096834 | -0.010391 | -0.0065047 | -0.0041528 | 54.8264 | 54.9728 | -68.5043 | 55.0278 | 54.7989 | 54.776 | 54.8813 | 54.95 | 54.9728 | 8.4961 | -0.37537 | 0.13733 | 122.9553 | 123.1567 | -0.036621 | 76.6251 | 0.13733 | 123.3307 | 123.0103 | 123.0789 | 122.9279 | 123.1018 | 122.9553 | 123.1018 | 122.905 | 76.6251 | 123.1018 | 122.9553 | 122.905 | 122.9279 | 123.1018 | -123.3398 | -46.3394
4093.7656 | 123.1705 | -68.1427 | 54.8401 | -0.11848 | 0.011437 | 0.0053193 | 0.008829 | -0.010604 | -0.0045821 | -0.0011622 | 54.8538 | 54.9683 | -68.5272 | 55.0369 | 54.8035 | 54.776 | 54.8401 | 54.9591 | 54.9271 | 8.4869 | -0.38452 | 0.12817 | 122.9965 | 123.1796 | -0.036621 | 76.6296 | 0.086975 | 123.381 | 122.9828 | 123.1018 | 122.9462 | 123.111 | 122.9965 | 123.0698 | 122.9187 | 76.6296 | 123.111 | 122.9965 | 122.9187 | 122.9462 | 123.0698 | -123.3673 | -46.3531
4094.7656 | 123.1293 | -68.1519 | 54.8401 | -0.4084 | 0.012933 | 0.0051057 | 0.0051974 | -0.0121 | -0.0060775 | -0.0037256 | 54.7852 | 54.9774 | -68.5135 | 55.0095 | 54.8126 | 54.7577 | 54.9088 | 54.9454 | 54.9591 | 8.5007 | -0.36163 | 0.13733 | 122.937 | 123.1613 | -0.027466 | 76.6525 | 0.11902 | 123.2986 | 123.0606 | 123.0972 | 122.9645 | 123.1293 | 122.937 | 123.111 | 122.9095 | 76.6525 | 123.1293 | 122.937 | 122.9095 | 122.9645 | 123.111 | -123.3536 | -46.3394
4095.7656 | 123.1384 | -68.1839 | 54.8538 | -0.17952 | 0.012719 | 0.0059601 | 0.0062656 | -0.0091089 | -0.0056503 | 0.00033321 | 54.7897 | 54.9774 | -68.5226 | 54.9454 | 54.8767 | 54.9271 | 54.7897 | 54.8126 | 54.9683 | 8.4915 | -0.33875 | 0.1236 | 122.9736 | 123.1293 | 0.022888 | 76.6754 | 0.11444 | 123.3124 | 122.9736 | 122.9965 | 123.0606 | 123.1613 | 122.9736 | 123.1522 | 123.111 | 76.6754 | 123.1613 | 122.9736 | 123.111 | 123.0606 | 123.1522 | -123.3765 | -46.3623
4096.7656 | 123.1613 | -68.1656 | 54.8447 | -0.11848 | 0.013146 | 0.0074555 | 0.010324 | -0.0065455 | -0.0062911 | -0.0037256 | 54.8355 | 54.9866 | -68.5135 | 55.0461 | 54.8264 | 54.7852 | 54.8721 | 54.9591 | 54.9362 | 8.5007 | -0.3479 | 0.14191 | 123.0011 | 123.2117 | -0.018311 | 76.6663 | 0.091552 | 123.349 | 123.0377 | 123.1247 | 122.9919 | 123.1522 | 123.0011 | 123.1018 | 122.9507 | 76.6663 | 123.1522 | 123.0011 | 122.9507 | 122.9919 | 123.1018 | -123.3582 | -46.344
4097.7812 | 123.175 | -68.1564 | 54.8309 | -0.04219 | 0.015283 | 0.0066009 | 0.0094698 | -0.0027003 | -0.0062911 | -0.0024438 | 54.8813 | 54.9683 | -68.5318 | 55.0369 | 54.8218 | 54.8309 | 54.7989 | 54.9545 | 54.9133 | 8.4869 | -0.37537 | 0.13733 | 123.0377 | 123.1934 | -0.009156 | 76.6434 | 0.082397 | 123.4131 | 122.9553 | 123.111 | 122.9782 | 123.1247 | 123.0377 | 123.0698 | 122.9874 | 76.6434 | 123.1247 | 123.0377 | 122.9874 | 122.9782 | 123.0698 | -123.3627 | -46.344
4098.7812 | 123.1705 | -68.1519 | 54.8264 | 0.049362 | 0.016351 | 0.0046783 | 0.0096834 | -0.0073999 | -0.0065047 | -0.00094839 | 54.8676 | 54.9911 | -68.5364 | 55.0095 | 54.8035 | 54.7852 | 54.8218 | 54.9316 | 54.9271 | 8.4961 | -0.38452 | 0.16479 | 123.0194 | 123.1613 | -0.022888 | 76.6479 | 0.10071 | 123.4039 | 122.9736 | 123.0835 | 122.9553 | 123.143 | 123.0194 | 123.0789 | 122.937 | 76.6479 | 123.143 | 123.0194 | 122.937 | 122.9553 | 123.0789 | -123.3627 | -46.3303
4099.7656 | 123.0286 | -68.1885 | 54.7668 | 0.15617 | 0.015923 | 0.0078827 | 0.010538 | -0.0052637 | -0.0060775 | -0.0039392 | 54.7806 | 54.9866 | -68.5501 | 54.9545 | 54.744 | 54.7348 | 54.8447 | 54.8447 | 54.9042 | 8.4961 | -0.36163 | 0.21973 | 122.9691 | 123.143 | -0.022888 | 76.6846 | 0.13733 | 123.3307 | 123.0331 | 123.0331 | 122.9324 | 123.175 | 122.9691 | 123.0927 | 122.9233 | 76.6846 | 123.175 | 122.9691 | 122.9233 | 122.9324 | 123.0927 | -123.317 | -46.2708
4100.7656 | 123.1155 | -68.1931 | 54.8172 | 0.23247 | 0.013146 | 0.0085235 | 0.0073336 | -0.0061181 | -0.0052231 | -0.0024438 | 54.5151 | 54.9316 | -68.5959 | 54.9774 | 54.776 | 54.7348 | 54.8309 | 54.8492 | 54.9042 | 8.4915 | -0.40283 | 0.11444 | 122.7081 | 123.1705 | -0.041199 | 76.6846 | 0.086975 | 123.111 | 123.024 | 123.0423 | 122.9691 | 123.1247 | 122.7081 | 123.0972 | 122.9279 | 76.6846 | 123.1247 | 122.7081 | 122.9279 | 122.9691 | 123.0972 | -123.4131 | -46.3257
4101.7656 | 123.1659 | -68.1839 | 54.808 | 0.026474 | 0.012933 | 0.010446 | 0.0086154 | -0.0046229 | -0.0050095 | -0.0043664 | 54.863 | 54.9911 | -68.5135 | 55.0003 | 54.7897 | 54.7806 | 54.8401 | 54.9088 | 54.9271 | 8.4824 | -0.32959 | 0.18311 | 123.0469 | 123.1842 | -0.01831 | 76.6663 | 0.11902 | 123.3765 | 123.024 | 123.0927 | 122.9736 | 123.175 | 123.0469 | 123.111 | 122.9645 | 76.6663 | 123.175 | 123.0469 | 122.9645 | 122.9736 | 123.111 | -123.3215 | -46.3257
4102.7656 | 123.1567 | -68.1885 | 54.8126 | 0.041733 | 0.01336 | 0.0085235 | 0.0086154 | -0.0065455 | -0.0052231 | -0.0022302 | 54.8492 | 54.9911 | -68.5135 | 54.9683 | 54.776 | 54.7668 | 54.8584 | 54.9179 | 54.895 | 8.4869 | -0.32501 | 0.17853 | 123.0377 | 123.1567 | -0.036621 | 76.6754 | 0.082398 | 123.3627 | 123.0469 | 123.1064 | 122.9645 | 123.1796 | 123.0377 | 123.0835 | 122.9553 | 76.6754 | 123.1796 | 123.0377 | 122.9553 | 122.9645 | 123.0835 | -123.3261 | -46.3257
4103.7656 | 123.1018 | -68.1885 | 54.8172 | 0.18669 | 0.016137 | 0.0063873 | 0.0077608 | -0.0039819 | -0.0069321 | -0.0041528 | 54.7806 | 55.0003 | -68.5776 | 54.9179 | 54.7348 | 54.7165 | 54.8355 | 54.8813 | 54.9225 | 8.4915 | -0.3891 | 0.1831 | 122.9691 | 123.1064 | -0.082398 | 76.68 | 0.10529 | 123.3582 | 123.024 | 123.0698 | 122.9233 | 123.1888 | 122.9691 | 123.111 | 122.905 | 76.68 | 123.1888 | 122.9691 | 122.905 | 122.9233 | 123.111 | -123.3948 | -46.3257
4104.7812 | 123.1705 | -68.1747 | 54.8126 | 0.20195 | 0.015283 | 0.0038239 | 0.0073336 | -0.0044091 | -0.0045821 | -0.0020166 | 54.7989 | 54.9728 | -68.5455 | 54.95 | 54.7623 | 54.7485 | 54.7806 | 54.8859 | 54.9042 | 8.4961 | -0.37079 | 0.16022 | 122.9736 | 123.1247 | -0.050354 | 76.6708 | 0.091553 | 123.3444 | 122.9553 | 123.0606 | 122.937 | 123.1476 | 122.9736 | 123.0789 | 122.9233 | 76.6708 | 123.1476 | 122.9736 | 122.9233 | 122.937 | 123.0789 | -123.3582 | -46.3165
4105.7656 | 123.2254 | -68.1702 | 54.7806 | 0.26299 | 0.016351 | 0.0098053 | 0.0028476 | -0.0056909 | -0.0084273 | -0.0020166 | 54.6844 | 54.8996 | -68.5364 | 55.0232 | 54.8538 | 54.8721 | 54.6753 | 54.982 | 54.8676 | 8.4961 | -0.36621 | 0.11902 | 122.8546 | 123.1934 | 0.073242 | 76.6663 | 0.086975 | 123.2208 | 122.8455 | 123.1522 | 123.024 | 123.0698 | 122.8546 | 123.0377 | 123.0423 | 76.6663 | 123.0698 | 122.8546 | 123.0423 | 123.024 | 123.0377 | -123.317 | -46.2845
4106.7656 | 123.2162 | -68.161 | 54.7485 | 0.17143 | 0.014214 | 0.0098053 | 0.0032748 | -0.0082545 | -0.0045821 | -0.001803 | 54.8309 | 54.9042 | -68.5043 | 55.0278 | 54.8355 | 54.8538 | 54.6753 | 54.982 | 54.8401 | 8.5007 | -0.34332 | 0.15564 | 122.9919 | 123.1888 | 0.086975 | 76.6617 | 0.091553 | 123.3353 | 122.8363 | 123.143 | 122.9965 | 123.0652 | 122.9919 | 123.0011 | 123.0148 | 76.6617 | 123.0652 | 122.9919 | 123.0148 | 122.9965 | 123.0011 | -123.2529 | -46.2479
4107.7656 | 123.2346 | -68.1381 | 54.7852 | 0.23247 | 0.012505 | 0.0029693 | 0.0045566 | -0.010177 | -0.0052231 | -0.0013758 | 54.8538 | 54.8904 | -68.5272 | 55.0232 | 54.8309 | 54.863 | 54.6799 | 54.9866 | 54.8492 | 8.4961 | -0.3891 | 0.10529 | 122.9919 | 123.1613 | 0.045777 | 76.6342 | 0.064087 | 123.381 | 122.818 | 123.1247 | 122.9691 | 123.0286 | 122.9919 | 122.9874 | 123.0011 | 76.6342 | 123.0286 | 122.9919 | 123.0011 | 122.9691 | 122.9874 | -123.3124 | -46.2891
4108.7656 | 123.1796 | -68.1747 | 54.808 | 0.25536 | 0.014855 | 0.0021149 | 0.0081882 | -0.0082545 | -0.0045821 | -0.0030848 | 54.8035 | 54.9454 | -68.5455 | 54.9683 | 54.7714 | 54.7668 | 54.7623 | 54.9042 | 54.8767 | 8.4961 | -0.37079 | 0.13733 | 122.9782 | 123.143 | -0.036621 | 76.6708 | 0.068665 | 123.349 | 122.937 | 123.0789 | 122.9462 | 123.1201 | 122.9782 | 123.0515 | 122.9416 | 76.6708 | 123.1201 | 122.9782 | 122.9416 | 122.9462 | 123.0515 | -123.3536 | -46.312
4109.7656 | 123.2162 | -68.1885 | 54.7806 | 0.30113 | 0.013787 | 0.0095917 | 0.0098972 | -0.0082545 | -0.0060775 | -0.00052119 | 54.7989 | 54.9454 | -68.5455 | 54.982 | 54.7714 | 54.7714 | 54.7302 | 54.9362 | 54.8767 | 8.5007 | -0.35705 | 0.16479 | 122.9874 | 123.1705 | -0.009156 | 76.6891 | 0.09613 | 123.3444 | 122.9187 | 123.1247 | 122.9599 | 123.1339 | 122.9874 | 123.0652 | 122.9599 | 76.6891 | 123.1339 | 122.9874 | 122.9599 | 122.9599 | 123.0652 | -123.3261 | -46.2799
4110.7812 | 123.2162 | -68.1335 | 54.7897 | 0.22484 | 0.012933 | 0.0031831 | 0.002634 | -0.0069727 | -0.0054367 | -0.0020166 | 54.8355 | 54.8904 | -68.5226 | 54.9957 | 54.8172 | 54.8447 | 54.6661 | 54.9911 | 54.8401 | 8.4961 | -0.3891 | 0.10071 | 122.9691 | 123.1293 | 0.027466 | 76.6296 | 0.050354 | 123.3582 | 122.7997 | 123.1247 | 122.9507 | 123.024 | 122.9691 | 122.9736 | 122.9782 | 76.6296 | 123.024 | 122.9691 | 122.9782 | 122.9507 | 122.9736 | -123.3124 | -46.2936
4111.7812 | 123.2071 | -68.1564 | 54.7623 | 0.21721 | 0.012078 | 0.0014741 | 0.002634 | -0.0086817 | -0.0067185 | -0.00052119 | 54.8218 | 54.8767 | -68.5226 | 55.0049 | 54.808 | 54.8218 | 54.6844 | 54.9637 | 54.8538 | 8.4961 | -0.36621 | 0.11444 | 122.9782 | 123.1613 | 0.045776 | 76.6525 | 0.091553 | 123.3444 | 122.8409 | 123.1201 | 122.9645 | 123.0331 | 122.9782 | 123.0103 | 122.9782 | 76.6525 | 123.0331 | 122.9782 | 122.9782 | 122.9645 | 123.0103 | -123.2849 | -46.2662
4112.7656 | 123.2162 | -68.1335 | 54.8264 | 0.14854 | 0.011437 | 0.0033967 | 0.001993 | -0.010604 | -0.0067185 | -0.00073479 | 54.776 | 54.9088 | -68.5181 | 55.0095 | 54.808 | 54.8126 | 54.7577 | 54.9866 | 54.8813 | 8.4869 | -0.38452 | 0.082397 | 122.9095 | 123.143 | -0.018311 | 76.6205 | 0.054932 | 123.2941 | 122.8912 | 123.1201 | 122.9416 | 123.0423 | 122.9095 | 123.0148 | 122.9462 | 76.6205 | 123.0423 | 122.9095 | 122.9462 | 122.9416 | 123.0148 | -123.3444 | -46.3394
4113.7656 | 123.2208 | -68.129 | 54.8172 | 0.041733 | 0.010369 | 0.0044647 | 0.00092504 | -0.011245 | -0.0071457 | -0.00052119 | 54.7852 | 54.8676 | -68.5226 | 55.014 | 54.8355 | 54.8172 | 54.7485 | 55.014 | 54.8813 | 8.4915 | -0.39368 | 0.050354 | 122.9141 | 123.143 | 0.01831 | 76.6205 | 0.064087 | 123.3078 | 122.8775 | 123.143 | 122.9645 | 122.9965 | 122.9141 | 123.0103 | 122.9462 | 76.6205 | 122.9965 | 122.9141 | 122.9462 | 122.9645 | 123.0103 | -123.3398 | -46.3257
4114.7656 | 123.2483 | -68.1473 | 54.8355 | 0.018845 | 0.011865 | 0.0014741 | 0.004343 | -0.012313 | -0.0054367 | -0.0030848 | 54.8126 | 54.8859 | -68.5043 | 55.0415 | 54.8264 | 54.8309 | 54.744 | 55.0095 | 54.8767 | 8.5007 | -0.35706 | 0.050354 | 122.9599 | 123.1888 | -0.009155 | 76.6479 | 0.041199 | 123.317 | 122.8912 | 123.1567 | 122.9736 | 123.0331 | 122.9599 | 123.024 | 122.9782 | 76.6479 | 123.0331 | 122.9599 | 122.9782 | 122.9736 | 123.024 | -123.3398 | -46.3348
4115.7656 | 123.23 | -68.1656 | 54.7943 | 0.25536 | 0.012719 | 0.0025421 | 0.0041292 | -0.011031 | -0.0054367 | -0.0026574 | 54.8309 | 54.8584 | -68.5089 | 55.0186 | 54.7989 | 54.8126 | 54.689 | 54.9683 | 54.8676 | 8.4915 | -0.34332 | 0.064086 | 122.9965 | 123.1842 | 0.004577 | 76.6571 | 0.073242 | 123.3398 | 122.8546 | 123.1338 | 122.9645 | 123.024 | 122.9965 | 123.0331 | 122.9782 | 76.6571 | 123.024 | 122.9965 | 122.9782 | 122.9645 | 123.0331 | -123.3032 | -46.3028
4116.7656 | 123.2071 | -68.129 | 54.7852 | 0.20958 | 0.010156 | 0.0059601 | 0.0049838 | -0.0099633 | -0.0039413 | -0.0024438 | 54.8126 | 54.8538 | -68.5364 | 55.014 | 54.8126 | 54.8172 | 54.6936 | 54.9728 | 54.8492 | 8.4869 | -0.40741 | 0.068665 | 122.9416 | 123.143 | 0.027466 | 76.6159 | 0.064087 | 123.349 | 122.8226 | 123.1018 | 122.9416 | 122.9828 | 122.9416 | 122.9782 | 122.9462 | 76.6159 | 122.9828 | 122.9416 | 122.9462 | 122.9416 | 122.9782 | -123.3215 | -46.2982
4117.7656 | 123.1842 | -68.1152 | 54.8035 | 0.11803 | 0.0097284 | 0.0053193 | 0.0047702 | -0.012313 | -0.0024459 | -0.0013758 | 54.7943 | 54.8584 | -68.5135 | 55.0095 | 54.744 | 54.95 | 54.6753 | 54.95 | 54.895 | 8.4961 | -0.39826 | 0.054931 | 122.9095 | 123.1247 | -0.059509 | 76.6113 | 0.091553 | 123.3078 | 122.7905 | 123.0652 | 122.8592 | 122.9736 | 122.9095 | 123.0103 | 123.0652 | 76.6113 | 122.9736 | 122.9095 | 123.0652 | 122.8592 | 123.0103 | -123.317 | -46.3074
4118.7812 | 123.2391 | -68.1473 | 54.808 | -0.019302 | 0.010156 | 0.0027557 | 0.002634 | -0.011886 | -0.0062911 | -0.001803 | 54.7897 | 54.8676 | -68.5043 | 55.0461 | 54.8401 | 54.8218 | 54.7394 | 55.0186 | 54.8813 | 8.4915 | -0.35706 | 0.05951 | 122.937 | 123.1934 | 0.032044 | 76.6388 | 0.073243 | 123.2941 | 122.8867 | 123.1659 | 122.9874 | 123.0148 | 122.937 | 123.0286 | 122.9691 | 76.6388 | 123.0148 | 122.937 | 122.9691 | 122.9874 | 123.0286 | -123.3124 | -46.3165
4119.7656 | 123.2574 | -68.1107 | 54.7943 | -0.11848 | 0.010583 | 0.0016877 | 0.0075472 | -0.0086817 | -0.0073593 | -0.00094839 | 54.8584 | 54.8538 | -68.4814 | 55.0644 | 54.8859 | 54.8813 | 54.6753 | 55.0644 | 54.8676 | 8.4915 | -0.37079 | 0.059509 | 122.9691 | 123.175 | 0.091552 | 76.6022 | 0.073242 | 123.3398 | 122.786 | 123.175 | 122.9965 | 122.9645 | 122.9691 | 122.9782 | 122.9919 | 76.6022 | 122.9645 | 122.9691 | 122.9919 | 122.9965 | 122.9782 | -123.2758 | -46.3028
4120.7656 | 123.262 | -68.0923 | 54.8172 | 1.1251 | 0.011224 | 0.0033967 | 0.0041292 | -0.012313 | -0.0071457 | -0.001803 | 54.8492 | 54.863 | -68.5043 | 55.0919 | 54.8767 | 54.8813 | 54.7348 | 55.0781 | 54.895 | 8.4961 | -0.41199 | 0.045776 | 122.9416 | 123.1842 | 0.059509 | 76.5884 | 0.07782 | 123.3536 | 122.8271 | 123.1705 | 122.9691 | 122.9553 | 122.9416 | 122.9874 | 122.9736 | 76.5884 | 122.9553 | 122.9416 | 122.9736 | 122.9691 | 122.9874 | -123.3215 | -46.3211
4121.7656 | 123.2574 | -68.1061 | 54.8447 | -0.45418 | 0.0097284 | 0.0027557 | 0.0030612 | -0.012954 | -0.0086411 | 0.00054681 | 54.8309 | 54.8492 | -68.4952 | 55.0964 | 54.8721 | 54.8584 | 54.744 | 55.0644 | 54.8859 | 8.4961 | -0.3891 | 0.004577 | 122.937 | 123.2025 | 0.027465 | 76.6022 | 0.041198 | 123.3261 | 122.85 | 123.1705 | 122.9782 | 122.9553 | 122.937 | 122.9919 | 122.9645 | 76.6022 | 122.9553 | 122.937 | 122.9645 | 122.9782 | 122.9919 | -123.3398 | -46.3486
4122.7656 | 123.2117 | -68.1244 | 54.8126 | 0.041733 | 0.0095148 | 0.0023285 | 0.0022066 | -0.012313 | -0.0056503 | -0.0011622 | 54.7943 | 54.8721 | -68.5272 | 55.0323 | 54.8447 | 54.8264 | 54.7394 | 54.9957 | 54.8676 | 8.4961 | -0.40283 | 0.059509 | 122.9187 | 123.1567 | 0.032044 | 76.6205 | 0.054932 | 123.3215 | 122.8638 | 123.1201 | 122.9691 | 122.9965 | 122.9187 | 122.9919 | 122.9507 | 76.6205 | 122.9965 | 122.9187 | 122.9507 | 122.9691 | 122.9919 | -123.3398 | -46.3165
4123.7656 | 123.23 | -68.1381 | 54.8218 | 0.07988 | 0.011224 | -2.1336e-05 | 0.0013522 | -0.013168 | -0.0065047 | -0.0024438 | 54.7897 | 54.8492 | -68.5089 | 55.069 | 54.8355 | 54.8401 | 54.744 | 54.982 | 54.8904 | 8.4915 | -0.37079 | 0.027466 | 122.9279 | 123.2071 | 0.013733 | 76.6296 | 0.068665 | 123.2986 | 122.8821 | 123.1201 | 122.9736 | 122.9874 | 122.9279 | 123.0286 | 122.9782 | 76.6296 | 122.9874 | 122.9279 | 122.9782 | 122.9736 | 123.0286 | -123.3307 | -46.3303
4124.7812 | 123.262 | -68.1198 | 54.7989 | -0.17952 | 0.0093012 | 0.0046783 | 0.0056246 | -0.011031 | -0.0056503 | -0.0024438 | 54.7623 | 54.8813 | -68.4769 | 55.0964 | 54.8996 | 54.8492 | 54.7302 | 55.0369 | 54.8676 | 8.4961 | -0.35706 | 0.082398 | 122.8821 | 123.2162 | 0.10071 | 76.6159 | 0.068665 | 123.2391 | 122.85 | 123.1567 | 123.0194 | 123.0011 | 122.8821 | 122.9874 | 122.9691 | 76.6159 | 123.0011 | 122.8821 | 122.9691 | 123.0194 | 122.9874 | -123.2758 | -46.3028
4125.7812 | 123.2529 | -68.1061 | 54.8172 | -0.17952 | 0.0093012 | 0.0027557 | 0.004343 | -0.01274 | -0.0082137 | -0.0030848 | 55.0735 | 54.9545 | -68.4814 | 55.069 | 54.8584 | 54.863 | 54.7668 | 55.0735 | 54.8447 | 8.5007 | -0.37537 | 0.13733 | 123.1796 | 123.175 | 0.041198 | 76.6067 | 0.027466 | 123.555 | 122.8729 | 123.1796 | 122.9645 | 123.0606 | 123.1796 | 122.9507 | 122.9691 | 76.6067 | 123.0606 | 123.1796 | 122.9691 | 122.9645 | 122.9507 | -123.2986 | -46.3165
4126.7656 | 123.1613 | -68.1381 | 54.8584 | -0.18715 | 0.0093012 | 0.0053193 | 0.0047702 | -0.0121 | -0.0054367 | -0.0022302 | 54.8126 | 54.9362 | -68.5089 | 55.069 | 54.8584 | 54.7897 | 54.8584 | 54.9683 | 54.9271 | 8.4961 | -0.37079 | 0.07782 | 122.9507 | 123.2071 | 0 | 76.6342 | 0.068665 | 123.3215 | 122.9965 | 123.1064 | 122.9965 | 123.0743 | 122.9507 | 123.0652 | 122.9279 | 76.6342 | 123.0743 | 122.9507 | 122.9279 | 122.9965 | 123.0652 | -123.3673 | -46.3623
4127.7812 | 123.1796 | -68.1793 | 54.808 | 0.20958 | 0.015283 | 0.0072419 | 0.010965 | -0.0091089 | -0.0054367 | -0.0020166 | 54.8264 | 54.95 | -68.5501 | 54.9728 | 54.7394 | 54.7394 | 54.7531 | 54.8859 | 54.8996 | 8.4915 | -0.37079 | 0.14191 | 123.0057 | 123.1522 | -0.068664 | 76.6708 | 0.091553 | 123.3765 | 122.9324 | 123.0652 | 122.9187 | 123.1293 | 123.0057 | 123.0789 | 122.9187 | 76.6708 | 123.1293 | 123.0057 | 122.9187 | 122.9187 | 123.0789 | -123.3582 | -46.3165
4128.7656 | 123.1247 | -68.1564 | 54.863 | -0.17189 | 0.011224 | 0.0076691 | 0.0047702 | -0.0099633 | -0.0067185 | -0.0032984 | 54.7989 | 54.9362 | -68.5593 | 55.0278 | 54.808 | 54.7531 | 54.9042 | 54.9637 | 54.9408 | 8.5007 | -0.40283 | 0.073242 | 122.9553 | 123.1842 | -0.054932 | 76.6571 | 0.07782 | 123.3582 | 123.0606 | 123.1201 | 122.9645 | 123.0927 | 122.9553 | 123.0972 | 122.9095 | 76.6571 | 123.0927 | 122.9553 | 122.9095 | 122.9645 | 123.0972 | -123.4222 | -46.3623
4129.7656 | 123.2803 | -68.1198 | 54.8172 | -0.034561 | 0.0080194 | 0.0016877 | 0.0024202 | -0.013168 | -0.0067185 | -0.00094839 | 54.8584 | 54.895 | -68.486 | 55.1285 | 54.9179 | 54.9088 | 54.7119 | 55.0873 | 54.8676 | 8.4961 | -0.36621 | 0.07782 | 122.9782 | 123.2483 | 0.10071 | 76.6159 | 0.050354 | 123.3444 | 122.8317 | 123.2071 | 123.0377 | 123.0148 | 122.9782 | 122.9874 | 123.0286 | 76.6159 | 123.0148 | 122.9782 | 123.0286 | 123.0377 | 122.9874 | -123.3032 | -46.3211
4130.7812 | 123.2437 | -68.1335 | 54.8355 | -0.16426 | 0.010156 | 0.0068147 | 0.0047702 | -0.010818 | -0.0073593 | -0.0039392 | 54.8676 | 54.8859 | -68.4952 | 55.1056 | 54.8996 | 54.8721 | 54.776 | 55.0598 | 54.8492 | 8.5052 | -0.36163 | 0.050354 | 123.0011 | 123.2391 | 0.064087 | 76.6388 | 0.013733 | 123.3627 | 122.9095 | 123.1934 | 123.0331 | 123.0194 | 123.0011 | 122.9828 | 123.0057 | 76.6388 | 123.0194 | 123.0011 | 123.0057 | 123.0331 | 122.9828 | -123.3307 | -46.3303
4131.7812 | 123.1796 | -68.1564 | 54.8538 | -0.20241 | 0.012292 | 0.0046783 | 0.0051974 | -0.013809 | -0.0058639 | -0.0015894 | 54.8401 | 54.9225 | -68.5089 | 55.0735 | 54.8401 | 54.8126 | 54.8767 | 54.9774 | 54.9088 | 8.4961 | -0.35248 | 0.068664 | 122.9965 | 123.23 | -0.013733 | 76.6525 | 0.054931 | 123.349 | 123.0331 | 123.1339 | 122.9965 | 123.0789 | 122.9965 | 123.0652 | 122.9691 | 76.6525 | 123.0789 | 122.9965 | 122.9691 | 122.9965 | 123.0652 | -123.3627 | -46.3577
4132.7812 | 123.1796 | -68.1747 | 54.8309 | 0.0035856 | 0.011865 | 0.0093781 | 0.010324 | -0.0082545 | -0.0050095 | -0.0028712 | 54.7943 | 54.9545 | -68.5318 | 55.0507 | 54.808 | 54.808 | 54.8309 | 54.9545 | 54.9179 | 8.4915 | -0.35706 | 0.1236 | 122.9691 | 123.2254 | -0.022889 | 76.6663 | 0.086975 | 123.3261 | 123.0057 | 123.1293 | 122.9828 | 123.1293 | 122.9691 | 123.0927 | 122.9828 | 76.6663 | 123.1293 | 122.9691 | 122.9828 | 122.9828 | 123.0927 | -123.3627 | -46.3394
4133.7656 | 123.1613 | -68.1519 | 54.8676 | -0.12611 | 0.0095148 | 0.0068147 | 0.0075472 | -0.010604 | -0.0084273 | -9.3992e-05 | 54.808 | 54.9408 | -68.541 | 55.0232 | 54.8126 | 54.7623 | 54.9133 | 54.9408 | 54.95 | 8.4961 | -0.3891 | 0.073242 | 122.9599 | 123.175 | -0.054932 | 76.6479 | 0.082397 | 123.349 | 123.0652 | 123.0927 | 122.9645 | 123.0927 | 122.9599 | 123.1018 | 122.9141 | 76.6479 | 123.0927 | 122.9599 | 122.9141 | 122.9645 | 123.1018 | -123.4085 | -46.3715
4134.7656 | 123.1567 | -68.1564 | 54.8447 | -0.13374 | 0.013146 | 0.0061737 | 0.0069064 | -0.0084681 | -0.0071457 | -0.0043664 | 54.7943 | 54.9774 | -68.573 | 55.0232 | 54.7989 | 54.7623 | 54.9179 | 54.9454 | 54.9454 | 8.4961 | -0.41656 | 0.13275 | 122.9507 | 123.1796 | -0.045777 | 76.6525 | 0.10071 | 123.3673 | 123.0743 | 123.1018 | 122.9553 | 123.1339 | 122.9507 | 123.1018 | 122.9187 | 76.6525 | 123.1339 | 122.9507 | 122.9187 | 122.9553 | 123.1018 | -123.4177 | -46.3486
4135.7812 | 123.1613 | -68.1839 | 54.8859 | -0.18715 | 0.014214 | 0.0057465 | 0.0073336 | -0.0091089 | -0.0058639 | -0.0026574 | 54.6982 | 54.9774 | -68.4906 | 54.982 | 54.7806 | 54.7485 | 54.9088 | 54.9225 | 54.9225 | 8.4915 | -0.3067 | 0.091553 | 122.8821 | 123.1659 | -0.10528 | 76.6754 | 0.036621 | 123.1888 | 123.0927 | 123.1064 | 122.9645 | 123.1613 | 122.8821 | 123.1064 | 122.9324 | 76.6754 | 123.1613 | 122.8821 | 122.9324 | 122.9645 | 123.1064 | -123.3765 | -46.3943
4136.7656 | 123.2391 | -68.129 | 54.8538 | -0.14137 | 0.013146 | 0.0027557 | 0.00071144 | -0.011031 | -0.0045821 | -0.003512 | 54.8676 | 54.9316 | -68.5043 | 55.0827 | 54.8904 | 54.8676 | 54.808 | 55.0552 | 54.8904 | 8.5052 | -0.37537 | 0.07782 | 122.9965 | 123.2117 | 0.036621 | 76.6342 | 0.036621 | 123.3719 | 122.937 | 123.1842 | 123.0194 | 123.0606 | 122.9965 | 123.0194 | 122.9965 | 76.6342 | 123.0606 | 122.9965 | 122.9965 | 123.0194 | 123.0194 | -123.3582 | -46.3486
4137.7812 | 123.1979 | -68.1564 | 54.8447 | -0.087967 | 0.014214 | 0.0061737 | 0.01182 | -0.0088953 | -0.0067185 | -0.0028712 | 54.8813 | 54.9911 | -68.5135 | 55.0552 | 54.8264 | 54.8035 | 54.8447 | 54.9683 | 54.8996 | 8.4961 | -0.35706 | 0.14648 | 123.0377 | 123.2117 | -0.018311 | 76.6525 | 0.054931 | 123.3948 | 123.0011 | 123.1247 | 122.9828 | 123.1476 | 123.0377 | 123.056 | 122.9599 | 76.6525 | 123.1476 | 123.0377 | 122.9599 | 122.9828 | 123.056 | -123.3582 | -46.3486
4138.7812 | 123.1384 | -68.1747 | 54.8584 | 0.095139 | 0.010369 | 0.0063873 | 0.0056246 | -0.0099633 | -0.0086411 | -0.0022302 | 54.8126 | 54.9957 | -68.5226 | 55.0049 | 54.8309 | 54.7852 | 54.9179 | 54.9545 | 54.9591 | 8.4961 | -0.3479 | 0.13733 | 122.9874 | 123.1796 | -0.027465 | 76.6708 | 0.10071 | 123.3353 | 123.0927 | 123.1293 | 123.0057 | 123.1705 | 122.9874 | 123.1338 | 122.9599 | 76.6708 | 123.1705 | 122.9874 | 122.9599 | 123.0057 | 123.1338 | -123.381 | -46.3623
4139.7812 | 123.1384 | -68.1656 | 54.8492 | -0.21767 | 0.011651 | 0.0057465 | 0.0056246 | -0.0076135 | -0.0067185 | -0.0030848 | 54.7623 | 54.9637 | -68.5593 | 55.0095 | 54.8126 | 54.7852 | 54.8996 | 54.9408 | 54.9454 | 8.4915 | -0.39368 | 0.11444 | 122.9279 | 123.175 | -0.036621 | 76.6571 | 0.096131 | 123.3215 | 123.0652 | 123.1064 | 122.9782 | 123.1293 | 122.9279 | 123.111 | 122.9507 | 76.6571 | 123.1293 | 122.9279 | 122.9507 | 122.9782 | 123.111 | -123.4085 | -46.3577
4140.7656 | 123.175 | -68.1702 | 54.808 | -0.065079 | 0.015069 | 0.0076691 | 0.0079744 | -0.0067591 | -0.0086411 | -0.0041528 | 54.8676 | 55.0003 | -68.5318 | 55.0323 | 54.8218 | 54.8035 | 54.8447 | 54.9728 | 54.9362 | 8.4961 | -0.36163 | 0.19226 | 123.0377 | 123.2025 | 0.013733 | 76.6663 | 0.12817 | 123.3994 | 123.0148 | 123.143 | 122.9919 | 123.1705 | 123.0377 | 123.1064 | 122.9736 | 76.6663 | 123.1705 | 123.0377 | 122.9736 | 122.9919 | 123.1064 | -123.3398 | -46.312
4141.7656 | 123.1705 | -68.161 | 54.8492 | -0.095596 | 0.014855 | 0.0048921 | 0.0090426 | -0.0073999 | -0.0073593 | -0.0043664 | 54.863 | 54.9866 | -68.5135 | 55.0369 | 54.8264 | 54.808 | 54.8584 | 54.982 | 54.9454 | 8.4915 | -0.35248 | 0.13733 | 123.024 | 123.1979 | -0.022888 | 76.6525 | 0.096131 | 123.3765 | 123.0194 | 123.143 | 122.9874 | 123.1476 | 123.024 | 123.1064 | 122.9691 | 76.6525 | 123.1476 | 123.024 | 122.9691 | 122.9874 | 123.1064 | -123.3627 | -46.3577
4142.7812 | 123.2712 | -68.1656 | 54.7714 | 0.27824 | 0.013787 | 0.0068147 | 0.0058382 | -0.0056909 | -0.0069321 | -0.0041528 | 54.8492 | 54.9225 | -68.5364 | 55.0323 | 54.8401 | 54.8309 | 54.6799 | 54.9683 | 54.8904 | 8.5007 | -0.37079 | 0.15106 | 123.0148 | 123.1979 | 0.068665 | 76.6663 | 0.11902 | 123.3856 | 122.8455 | 123.1338 | 123.0057 | 123.0881 | 123.0148 | 123.056 | 122.9965 | 76.6663 | 123.0881 | 123.0148 | 122.9965 | 123.0057 | 123.056 | -123.3078 | -46.2708
4143.7656 | 123.1476 | -68.1747 | 54.8584 | -0.21767 | 0.0097284 | 0.0061737 | 0.0032748 | -0.0080407 | -0.0065047 | -0.0011622 | 54.808 | 54.9911 | -68.5181 | 54.9957 | 54.808 | 54.7714 | 54.9408 | 54.9728 | 54.9225 | 8.5007 | -0.34332 | 0.13275 | 122.9828 | 123.1705 | -0.050354 | 76.6754 | 0.064087 | 123.3261 | 123.1155 | 123.1476 | 122.9828 | 123.1659 | 122.9828 | 123.0972 | 122.9462 | 76.6754 | 123.1659 | 122.9828 | 122.9462 | 122.9828 | 123.0972 | -123.3765 | -46.3577
4144.7656 | 123.1522 | -68.1702 | 54.8676 | -0.14137 | 0.013146 | 0.0093781 | 0.0049838 | -0.0078271 | -0.0088547 | -0.001803 | 54.8035 | 54.9866 | -68.5455 | 55.0095 | 54.8035 | 54.7852 | 54.9225 | 54.9454 | 54.9454 | 8.4915 | -0.37537 | 0.11902 | 122.9736 | 123.1796 | -0.064087 | 76.6617 | 0.07782 | 123.349 | 123.0927 | 123.1155 | 122.9736 | 123.1567 | 122.9736 | 123.1155 | 122.9553 | 76.6617 | 123.1567 | 122.9736 | 122.9553 | 122.9736 | 123.1155 | -123.4131 | -46.376
4145.7812 | 123.175 | -68.1519 | 54.8492 | -0.072708 | 0.014001 | 0.0080963 | 0.0079744 | -0.0084681 | -0.0069321 | -0.0028712 | 54.8721 | 55.014 | -68.5181 | 55.0369 | 54.8172 | 54.8264 | 54.8584 | 54.9728 | 54.9408 | 8.4961 | -0.36621 | 0.16479 | 123.024 | 123.1888 | -0.032043 | 76.6479 | 0.091553 | 123.3902 | 123.0103 | 123.1247 | 122.9691 | 123.1659 | 123.024 | 123.0927 | 122.9782 | 76.6479 | 123.1659 | 123.024 | 122.9782 | 122.9691 | 123.0927 | -123.3673 | -46.3531
4146.7812 | 123.175 | -68.1747 | 54.8447 | -0.11085 | 0.014001 | 0.0089509 | 0.0069064 | -0.0056909 | -0.0082137 | -0.0020166 | 54.8767 | 54.9774 | -68.5593 | 55.0369 | 54.8309 | 54.8218 | 54.8721 | 54.9774 | 54.9271 | 8.4961 | -0.38452 | 0.13275 | 123.0515 | 123.2117 | -0.013733 | 76.6708 | 0.082397 | 123.436 | 123.0469 | 123.1522 | 123.0057 | 123.1522 | 123.0515 | 123.1018 | 122.9965 | 76.6708 | 123.1522 | 123.0515 | 122.9965 | 123.0057 | 123.1018 | -123.4039 | -46.3486
4147.7656 | 123.1796 | -68.1885 | 54.8309 | 0.026474 | 0.014428 | 0.0059601 | 0.0086154 | -0.0065455 | -0.0075729 | -0.0015894 | 54.8676 | 54.9866 | -68.5501 | 55.014 | 54.7943 | 54.8035 | 54.8401 | 54.9316 | 54.9591 | 8.4915 | -0.36163 | 0.15564 | 123.056 | 123.2025 | -0.036621 | 76.68 | 0.12817 | 123.4177 | 123.0286 | 123.1201 | 122.9828 | 123.175 | 123.056 | 123.1476 | 122.9919 | 76.68 | 123.175 | 123.056 | 122.9919 | 122.9828 | 123.1476 | -123.381 | -46.3394
4148.7656 | 123.1842 | -68.1702 | 54.8172 | 0.026474 | 0.014428 | 0.011301 | 0.008829 | -0.0071863 | -0.0050095 | -0.001803 | 54.8538 | 54.9911 | -68.541 | 54.9866 | 54.7989 | 54.7852 | 54.8584 | 54.9408 | 54.9088 | 8.4915 | -0.37079 | 0.17395 | 123.024 | 123.1567 | -0.018311 | 76.6617 | 0.091552 | 123.3948 | 123.0286 | 123.111 | 122.9691 | 123.1613 | 123.024 | 123.0789 | 122.9553 | 76.6617 | 123.1613 | 123.024 | 122.9553 | 122.9691 | 123.0789 | -123.3582 | -46.3257
4149.7656 | 123.1705 | -68.161 | 54.8447 | -0.13374 | 0.014428 | 0.0068147 | 0.0064792 | -0.0071863 | -0.0065047 | -0.0037256 | 54.8172 | 55.014 | -68.541 | 54.9957 | 54.8172 | 54.7897 | 54.9271 | 54.9591 | 54.9683 | 8.4961 | -0.37994 | 0.16937 | 122.9782 | 123.1567 | -0.027466 | 76.6571 | 0.1236 | 123.3582 | 123.0881 | 123.1201 | 122.9782 | 123.175 | 122.9782 | 123.1293 | 122.9507 | 76.6571 | 123.175 | 122.9782 | 122.9507 | 122.9782 | 123.1293 | -123.3856 | -46.3486
4150.7656 | 123.1567 | -68.1519 | 54.8676 | -0.16426 | 0.01336 | 0.0016877 | 0.0064792 | -0.0086817 | -0.0082137 | -0.0026574 | 54.8172 | 55.014 | -68.5318 | 55.0003 | 54.808 | 54.7897 | 54.9408 | 54.9591 | 54.9728 | 8.4961 | -0.37994 | 0.14648 | 122.9691 | 123.1522 | -0.05951 | 76.6479 | 0.10529 | 123.349 | 123.0927 | 123.111 | 122.9599 | 123.1659 | 122.9691 | 123.1247 | 122.9416 | 76.6479 | 123.1659 | 122.9691 | 122.9416 | 122.9599 | 123.1247 | -123.3994 | -46.3715
4151.7656 | 123.1979 | -68.1702 | 54.8538 | -0.095596 | 0.014214 | 0.0029693 | 0.0079744 | -0.0076135 | -0.0075729 | -0.0015894 | 54.863 | 54.9957 | -68.5226 | 55.0369 | 54.8447 | 54.808 | 54.8492 | 54.9683 | 54.9454 | 8.5007 | -0.35248 | 0.14191 | 123.0331 | 123.2071 | -0.009155 | 76.6708 | 0.091553 | 123.3856 | 123.0194 | 123.1384 | 123.0148 | 123.1659 | 123.0331 | 123.1155 | 122.9782 | 76.6708 | 123.1659 | 123.0331 | 122.9782 | 123.0148 | 123.1155 | -123.3765 | -46.3531
4152.7812 | 123.1705 | -68.1747 | 54.8447 | -0.011673 | 0.013574 | 0.0044647 | 0.0058382 | -0.0071863 | -0.0062911 | -0.0030848 | 54.8172 | 54.9774 | -68.5547 | 55.0049 | 54.8035 | 54.8309 | 54.8584 | 54.9683 | 54.95 | 8.4915 | -0.37994 | 0.13275 | 122.9919 | 123.1796 | -0.041199 | 76.6663 | 0.10529 | 123.3719 | 123.0331 | 123.143 | 122.9782 | 123.1522 | 122.9919 | 123.1247 | 123.0057 | 76.6663 | 123.1522 | 122.9919 | 123.0057 | 122.9782 | 123.1247 | -123.3994 | -46.3531
4153.7812 | 123.1705 | -68.161 | 54.8309 | -0.75172 | 0.015923 | 0.0080963 | 0.00712 | -0.0056909 | -0.0073593 | -0.0028712 | 54.8492 | 55.0003 | -68.5272 | 55.0232 | 54.7989 | 54.808 | 54.8401 | 54.9683 | 54.9225 | 8.4869 | -0.36621 | 0.16937 | 123.0103 | 123.1842 | -0.032044 | 76.6479 | 0.091552 | 123.3765 | 123.0011 | 123.1293 | 122.9599 | 123.1613 | 123.0103 | 123.0835 | 122.9691 | 76.6479 | 123.1613 | 123.0103 | 122.9691 | 122.9599 | 123.0835 | -123.3582 | -46.344
4154.7656 | 123.111 | -68.2205 | 54.8447 | 0.19432 | 0.015283 | 0.0083099 | 0.010965 | -0.0046229 | -0.0054367 | -0.0028712 | 54.8035 | 55.0232 | -68.5364 | 54.9362 | 54.7302 | 54.7211 | 54.8904 | 54.8676 | 54.9683 | 8.4961 | -0.31586 | 0.17853 | 123.024 | 123.1567 | -0.11444 | 76.7166 | 0.1236 | 123.3398 | 123.111 | 123.0881 | 122.9507 | 123.2437 | 123.024 | 123.1888 | 122.9416 | 76.7166 | 123.2437 | 123.024 | 122.9416 | 122.9507 | 123.1888 | -123.381 | -46.3486
4155.7656 | 123.111 | -68.2159 | 54.8355 | 0.13329 | 0.013574 | 0.0091645 | 0.0069064 | -0.0071863 | -0.0080001 | -0.0026574 | 54.7943 | 55.0003 | -68.5593 | 54.9316 | 54.7348 | 54.7348 | 54.8767 | 54.8859 | 54.9408 | 8.4961 | -0.34332 | 0.16479 | 123.0103 | 123.1476 | -0.10071 | 76.712 | 0.10529 | 123.3536 | 123.0927 | 123.1018 | 122.9507 | 123.2162 | 123.0103 | 123.1567 | 122.9507 | 76.712 | 123.2162 | 123.0103 | 122.9507 | 122.9507 | 123.1567 | -123.3948 | -46.3394
4156.7656 | 123.1796 | -68.1702 | 54.8309 | -0.12611 | 0.013787 | 0.01066 | 0.0079744 | -0.0061181 | -0.0060775 | -0.00094839 | 54.863 | 54.9728 | -68.5135 | 55.0095 | 54.8126 | 54.808 | 54.8584 | 54.982 | 54.9591 | 8.5007 | -0.34332 | 0.14191 | 123.0331 | 123.1796 | -0.018311 | 76.6708 | 0.12817 | 123.3765 | 123.0286 | 123.1522 | 122.9828 | 123.143 | 123.0331 | 123.1293 | 122.9782 | 76.6708 | 123.143 | 123.0331 | 122.9782 | 122.9828 | 123.1293 | -123.3444 | -46.3303
4157.7656 | 123.1842 | -68.1839 | 54.8355 | -0.057449 | 0.015069 | 0.0033967 | 0.0064792 | -0.0054773 | -0.0047957 | -0.001803 | 54.8676 | 54.9957 | -68.5364 | 55.0232 | 54.8264 | 54.8172 | 54.8538 | 54.9911 | 54.95 | 8.4961 | -0.35248 | 0.16022 | 123.0515 | 123.2071 | -0.009155 | 76.68 | 0.11444 | 123.4039 | 123.0377 | 123.175 | 123.0103 | 123.1796 | 123.0515 | 123.1338 | 123.0011 | 76.68 | 123.1796 | 123.0515 | 123.0011 | 123.0103 | 123.1338 | -123.3719 | -46.3394
4158.7656 | 123.1796 | -68.1839 | 54.8309 | 0.041733 | 0.014214 | 0.0063873 | 0.008829 | -0.0059045 | -0.0065047 | -0.0013758 | 54.863 | 55.0323 | -68.5272 | 54.9911 | 54.7943 | 54.7852 | 54.8538 | 54.9408 | 54.9179 | 8.4869 | -0.34332 | 0.20142 | 123.0469 | 123.175 | -0.036621 | 76.6708 | 0.086975 | 123.3902 | 123.0377 | 123.1247 | 122.9782 | 123.2162 | 123.0469 | 123.1018 | 122.9691 | 76.6708 | 123.2162 | 123.0469 | 122.9691 | 122.9782 | 123.1018 | -123.3582 | -46.344
4159.7812 | 123.1384 | -68.2159 | 54.8309 | 0.14092 | 0.015496 | 0.0053193 | 0.008829 | -0.0061181 | -0.0047957 | -0.0020166 | 54.808 | 55.0323 | -68.541 | 54.9545 | 54.7623 | 54.744 | 54.863 | 54.8813 | 54.9408 | 8.4869 | -0.32501 | 0.20142 | 123.024 | 123.1705 | -0.068665 | 76.7029 | 0.10986 | 123.349 | 123.0789 | 123.0972 | 122.9782 | 123.2483 | 123.024 | 123.1567 | 122.9599 | 76.7029 | 123.2483 | 123.024 | 122.9599 | 122.9782 | 123.1567 | -123.3719 | -46.344
4160.7656 | 123.1476 | -68.2159 | 54.8309 | 0.23247 | 0.016778 | 0.012796 | 0.0058382 | -0.0039819 | -0.0067185 | -9.3992e-05 | 54.7989 | 54.9957 | -68.5638 | 54.9316 | 54.7394 | 54.7531 | 54.8172 | 54.9042 | 54.9362 | 8.4961 | -0.3479 | 0.16479 | 123.0148 | 123.1476 | -0.091553 | 76.712 | 0.10528 | 123.3627 | 123.0331 | 123.1201 | 122.9553 | 123.2117 | 123.0148 | 123.1522 | 122.9691 | 76.712 | 123.2117 | 123.0148 | 122.9691 | 122.9553 | 123.1522 | -123.3948 | -46.3348
4161.7656 | 123.175 | -68.2068 | 54.8218 | 0.21721 | 0.015069 | 0.0070283 | 0.0062656 | -0.0056909 | -0.0054367 | -0.0022302 | 54.8035 | 55.0049 | -68.573 | 54.9454 | 54.7668 | 54.744 | 54.8035 | 54.9042 | 54.9042 | 8.4961 | -0.36621 | 0.18311 | 123.0103 | 123.1522 | -0.054931 | 76.7029 | 0.082398 | 123.3765 | 123.0103 | 123.111 | 122.9736 | 123.2117 | 123.0103 | 123.111 | 122.9507 | 76.7029 | 123.2117 | 123.0103 | 122.9507 | 122.9736 | 123.111 | -123.3948 | -46.3257
4162.7656 | 123.1476 | -68.1747 | 54.8218 | 0.049362 | 0.016137 | 0.0093781 | 0.0066928 | -0.0054773 | -0.0047957 | 0.00054681 | 54.8584 | 55.0095 | -68.5547 | 54.982 | 54.7806 | 54.7577 | 54.8721 | 54.9408 | 54.95 | 8.4824 | -0.37994 | 0.18768 | 123.0331 | 123.1567 | -0.041198 | 76.6571 | 0.12817 | 123.4131 | 123.0469 | 123.1155 | 122.9553 | 123.1842 | 123.0331 | 123.1247 | 122.9324 | 76.6571 | 123.1842 | 123.0331 | 122.9324 | 122.9553 | 123.1247 | -123.3765 | -46.3394
4163.7656 | 123.1842 | -68.161 | 54.8355 | 0.072251 | 0.016778 | 0.0076691 | 0.0090426 | -0.0063317 | -0.0058639 | -0.0013758 | 54.8401 | 55.0095 | -68.5318 | 54.9683 | 54.776 | 54.7714 | 54.8584 | 54.9225 | 54.9316 | 8.4869 | -0.37079 | 0.17395 | 123.0011 | 123.1293 | -0.059509 | 76.6479 | 0.096131 | 123.3719 | 123.0194 | 123.0835 | 122.937 | 123.1705 | 123.0011 | 123.0927 | 122.9324 | 76.6479 | 123.1705 | 123.0011 | 122.9324 | 122.937 | 123.0927 | -123.3673 | -46.3486
4164.7656 | 123.1567 | -68.1976 | 54.8447 | 0.041733 | 0.014855 | 0.0063873 | 0.00712 | -0.0048365 | -0.0065047 | -0.0028712 | 54.8538 | 55.014 | -68.5272 | 54.9866 | 54.7806 | 54.7485 | 54.8584 | 54.9225 | 54.9454 | 8.4824 | -0.32959 | 0.16937 | 123.0515 | 123.1842 | -0.064087 | 76.68 | 0.10071 | 123.381 | 123.056 | 123.1201 | 122.9782 | 123.2117 | 123.0515 | 123.143 | 122.9462 | 76.68 | 123.2117 | 123.0515 | 122.9462 | 122.9782 | 123.143 | -123.3719 | -46.3623
4165.7656 | 123.1338 | -68.1839 | 54.8172 | 0.1638 | 0.014428 | 0.0048921 | 0.0075472 | -0.0052637 | -0.0067185 | -0.0032984 | 54.7806 | 55.0049 | -68.5501 | 54.9316 | 54.7302 | 54.7256 | 54.8676 | 54.8492 | 54.9637 | 8.4869 | -0.36621 | 0.18768 | 122.9645 | 123.1155 | -0.086975 | 76.6708 | 0.14648 | 123.3307 | 123.0515 | 123.0331 | 122.9141 | 123.1888 | 122.9645 | 123.1476 | 122.9095 | 76.6708 | 123.1888 | 122.9645 | 122.9095 | 122.9141 | 123.1476 | -123.3673 | -46.3303
4166.7812 | 123.1705 | -68.2068 | 54.8309 | 0.27061 | 0.014214 | 0.0061737 | 0.0079744 | -0.0073999 | -0.0047957 | -0.0013758 | 54.7897 | 55.0049 | -68.5455 | 54.95 | 54.7577 | 54.7348 | 54.8264 | 54.8904 | 54.9316 | 8.4961 | -0.33874 | 0.17395 | 122.9965 | 123.1567 | -0.073243 | 76.7029 | 0.10071 | 123.3353 | 123.0331 | 123.0972 | 122.9645 | 123.2117 | 122.9965 | 123.1384 | 122.9416 | 76.7029 | 123.2117 | 122.9965 | 122.9416 | 122.9645 | 123.1384 | -123.3765 | -46.3348
4167.7656 | 123.2712 | -68.1656 | 54.7623 | 0.26299 | 0.014642 | 0.0057465 | 0.0056246 | -0.0048365 | -0.0050095 | -0.0011622 | 54.863 | 54.9362 | -68.5272 | 55.0186 | 54.8355 | 54.8584 | 54.6799 | 54.9911 | 54.8904 | 8.4869 | -0.36163 | 0.17395 | 123.0286 | 123.1842 | 0.073242 | 76.6525 | 0.12817 | 123.3902 | 122.8455 | 123.1567 | 123.0011 | 123.1018 | 123.0286 | 123.056 | 123.024 | 76.6525 | 123.1018 | 123.0286 | 123.024 | 123.0011 | 123.056 | -123.2895 | -46.2753
4168.7656 | 123.2849 | -68.1702 | 54.7852 | 0.17906 | 0.012505 | 0.0093781 | 0.0060518 | -0.0067591 | -0.0073593 | -0.001803 | 54.863 | 54.95 | -68.5272 | 55.0461 | 54.8264 | 54.8447 | 54.6707 | 55.0049 | 54.8492 | 8.4961 | -0.35706 | 0.16479 | 123.0331 | 123.2162 | 0.041199 | 76.6663 | 0.064087 | 123.3902 | 122.8409 | 123.175 | 122.9965 | 123.1201 | 123.0331 | 123.0194 | 123.0148 | 76.6663 | 123.1201 | 123.0331 | 123.0148 | 122.9965 | 123.0194 | -123.3124 | -46.2891
4169.7656 | 123.2895 | -68.1519 | 54.7668 | 0.23247 | 0.014214 | 0.0093781 | 0.0039156 | -0.0076135 | -0.0050095 | -0.0028712 | 54.8676 | 54.9316 | -68.5318 | 55.0278 | 54.8355 | 54.8538 | 54.6707 | 54.9866 | 54.8721 | 8.4915 | -0.37994 | 0.16479 | 123.0194 | 123.1796 | 0.068664 | 76.6434 | 0.10529 | 123.3994 | 122.8226 | 123.1384 | 122.9874 | 123.0835 | 123.0194 | 123.024 | 123.0057 | 76.6434 | 123.0835 | 123.0194 | 123.0057 | 122.9874 | 123.024 | -123.2986 | -46.2753
4170.7656 | 123.2117 | -68.1885 | 54.8309 | 0.19432 | 0.015283 | 0.0061737 | 0.0092562 | -0.0059045 | -0.0035141 | -0.0013758 | 54.7806 | 54.9911 | -68.5684 | 54.9545 | 54.7256 | 54.7256 | 54.6295 | 54.5471 | 54.8904 | 8.4869 | -0.37994 | 0.16022 | 122.9691 | 123.143 | -0.10529 | 76.6754 | 0.059509 | 123.349 | 122.818 | 122.7356 | 122.9141 | 123.1796 | 122.9691 | 123.0789 | 122.9141 | 76.6754 | 123.1796 | 122.9691 | 122.9141 | 122.9141 | 123.0789 | -123.3994 | -46.344
4171.7656 | 123.1842 | -68.1747 | 54.808 | 0.20195 | 0.015923 | 0.0093781 | 0.0086154 | -0.0065455 | -0.0058639 | -0.0024438 | 54.8035 | 54.9866 | -68.5822 | 54.9591 | 54.7485 | 54.7485 | 54.8172 | 54.8859 | 54.9454 | 8.4961 | -0.40741 | 0.17853 | 122.9782 | 123.1338 | -0.059509 | 76.6708 | 0.13733 | 123.3856 | 122.9919 | 123.0606 | 122.9233 | 123.1613 | 122.9782 | 123.1201 | 122.9233 | 76.6708 | 123.1613 | 122.9782 | 122.9233 | 122.9233 | 123.1201 | -123.3902 | -46.312
4172.7812 | 123.2437 | -68.161 | 54.7806 | 0.27061 | 0.014214 | 0.010873 | 0.003702 | -0.0056909 | -0.0062911 | -0.0026574 | 54.8218 | 54.9271 | -68.5501 | 55.0049 | 54.8309 | 54.8355 | 54.6844 | 54.9545 | 54.9088 | 8.4961 | -0.3891 | 0.14648 | 122.9828 | 123.1659 | 0.050354 | 76.6571 | 0.12817 | 123.3719 | 122.8455 | 123.1155 | 122.9919 | 123.0881 | 122.9828 | 123.0698 | 122.9965 | 76.6571 | 123.0881 | 122.9828 | 122.9965 | 122.9919 | 123.0698 | -123.3307 | -46.2845
4173.7812 | 123.2529 | -68.1519 | 54.7852 | 0.26299 | 0.014214 | 0.0078827 | 0.0062656 | -0.0067591 | -0.0054367 | -0.0032984 | 54.8218 | 54.9316 | -68.573 | 55.0232 | 54.8035 | 54.8264 | 54.7028 | 54.9225 | 54.8859 | 8.4961 | -0.42114 | 0.14648 | 122.9736 | 123.175 | 0.018311 | 76.6479 | 0.10071 | 123.3948 | 122.8546 | 123.0743 | 122.9553 | 123.0835 | 122.9736 | 123.0377 | 122.9782 | 76.6479 | 123.0835 | 122.9736 | 122.9782 | 122.9553 | 123.0377 | -123.3582 | -46.2891
4174.7656 | 123.2437 | -68.1656 | 54.7577 | 0.2401 | 0.01336 | 0.0068147 | 0.0017794 | -0.0095361 | -0.0054367 | -0.001803 | 54.8584 | 54.9316 | -68.5364 | 55.0369 | 54.8264 | 54.8447 | 54.6844 | 54.9957 | 54.8904 | 8.4915 | -0.37079 | 0.17395 | 123.024 | 123.2025 | 0.068665 | 76.6571 | 0.13275 | 123.3948 | 122.85 | 123.1613 | 122.9919 | 123.0972 | 123.024 | 123.056 | 123.0103 | 76.6571 | 123.0972 | 123.024 | 123.0103 | 122.9919 | 123.056 | -123.2941 | -46.2662
4175.7656 | 123.2758 | -68.1564 | 54.7897 | 0.19432 | 0.01336 | 0.0042511 | 0.0045566 | -0.0084681 | -0.0058639 | -0.0032984 | 54.8584 | 54.8813 | -68.5181 | 55.0278 | 54.8218 | 54.8355 | 54.6753 | 54.9911 | 54.8996 | 8.4915 | -0.36163 | 0.091553 | 123.0148 | 123.1842 | 0.032043 | 76.6479 | 0.10986 | 123.3765 | 122.8317 | 123.1476 | 122.9782 | 123.0377 | 123.0148 | 123.056 | 122.9919 | 76.6479 | 123.0377 | 123.0148 | 122.9919 | 122.9782 | 123.056 | -123.3078 | -46.2982
4176.7656 | 123.2437 | -68.161 | 54.808 | 0.2401 | 0.013787 | 0.0070283 | 0.0066928 | -0.0086817 | -0.0043685 | -0.0028712 | 54.8721 | 54.9133 | -68.4952 | 55.0461 | 54.8355 | 54.8309 | 54.6799 | 55.0049 | 54.8676 | 8.4961 | -0.33417 | 0.10529 | 123.0331 | 123.2071 | 0.027466 | 76.6571 | 0.05951 | 123.3673 | 122.8409 | 123.1659 | 122.9965 | 123.0743 | 123.0331 | 123.0286 | 122.9919 | 76.6571 | 123.0743 | 123.0331 | 122.9919 | 122.9965 | 123.0286 | -123.3032 | -46.312
4177.7656 | 123.1705 | -68.161 | 54.8126 | 0.18669 | 0.014001 | 0.0048921 | 0.010324 | -0.0093225 | -0.0041549 | -0.0015894 | 54.808 | 54.9454 | -68.5593 | 54.9683 | 54.7256 | 54.7485 | 54.8126 | 54.895 | 54.9133 | 8.4961 | -0.39825 | 0.13275 | 122.9691 | 123.1293 | -0.086975 | 76.6571 | 0.10071 | 123.3673 | 122.9736 | 123.056 | 122.8867 | 123.1064 | 122.9691 | 123.0743 | 122.9095 | 76.6571 | 123.1064 | 122.9691 | 122.9095 | 122.8867 | 123.0743 | -123.3719 | -46.3165
4178.7656 | 123.1842 | -68.1931 | 54.8172 | 0.17143 | 0.016778 | 0.0089509 | 0.0092562 | -0.0073999 | -0.0065047 | -0.0013758 | 54.7897 | 54.9637 | -68.5547 | 54.9637 | 54.744 | 54.7394 | 54.8126 | 54.895 | 54.9225 | 8.4961 | -0.36163 | 0.14648 | 122.9828 | 123.1567 | -0.073242 | 76.6891 | 0.10529 | 123.3444 | 123.0057 | 123.0881 | 122.937 | 123.1567 | 122.9828 | 123.1155 | 122.9324 | 76.6891 | 123.1567 | 122.9828 | 122.9324 | 122.937 | 123.1155 | -123.3719 | -46.3211
4179.7812 | 123.2712 | -68.1381 | 54.7897 | 0.25536 | 0.012933 | 0.0025421 | 0.003702 | -0.0069727 | -0.0054367 | 0.0018286 | 54.8721 | 54.895 | -68.541 | 54.9088 | 54.689 | 54.9179 | 54.7668 | 55.0369 | 54.8904 | 8.5007 | -0.40283 | 0.10529 | 123.0103 | 123.0469 | -0.10071 | 76.6388 | 0.10071 | 123.4131 | 122.905 | 123.175 | 122.8271 | 123.0331 | 123.0103 | 123.0286 | 123.056 | 76.6388 | 123.0331 | 123.0103 | 123.056 | 122.8271 | 123.0286 | -123.3307 | -46.2891
4180.7812 | 123.2758 | -68.1564 | 54.7989 | 0.23247 | 0.012078 | 0.01066 | 0.0064792 | -0.0078271 | -0.0058639 | -0.0011622 | 54.8538 | 54.9042 | -68.5455 | 55.0598 | 54.9637 | 54.7989 | 54.4693 | 55.1285 | 54.8218 | 8.5007 | -0.3891 | 0.10529 | 123.0103 | 123.2162 | 0.16479 | 76.6571 | 0.022888 | 123.3994 | 122.6257 | 123.2849 | 123.1201 | 123.0606 | 123.0103 | 122.9782 | 122.9553 | 76.6571 | 123.0606 | 123.0103 | 122.9553 | 123.1201 | 122.9782 | -123.3444 | -46.2982
4181.7656 | 123.2346 | -68.1747 | 54.7897 | 0.23247 | 0.012078 | 0.0055329 | 0.0028476 | -0.0082545 | -0.0045821 | -0.0024438 | 54.8309 | 54.9088 | -68.5318 | 55.014 | 54.8126 | 54.8126 | 54.7119 | 54.9683 | 54.895 | 8.4961 | -0.35706 | 0.11902 | 123.0057 | 123.1888 | 0.022888 | 76.6708 | 0.10529 | 123.3627 | 122.8867 | 123.143 | 122.9874 | 123.0835 | 123.0057 | 123.0698 | 122.9874 | 76.6708 | 123.0835 | 123.0057 | 122.9874 | 122.9874 | 123.0698 | -123.3215 | -46.2936
4182.7656 | 123.2529 | -68.1656 | 54.7989 | 0.20958 | 0.012292 | 0.0038239 | 0.0034884 | -0.0093225 | -0.0065047 | -0.0013758 | 54.8264 | 54.895 | -68.541 | 55.0186 | 54.8401 | 54.8264 | 54.7119 | 54.9774 | 54.8676 | 8.4915 | -0.37537 | 0.096131 | 122.9919 | 123.1842 | 0.041199 | 76.6571 | 0.068665 | 123.3673 | 122.8775 | 123.143 | 123.0057 | 123.0606 | 122.9919 | 123.0331 | 122.9919 | 76.6571 | 123.0606 | 122.9919 | 122.9919 | 123.0057 | 123.0331 | -123.3398 | -46.3074
4183.7656 | 123.2391 | -68.1427 | 54.7897 | 0.20958 | 0.013574 | 0.010019 | 0.0058382 | -0.0099633 | -0.0035141 | -0.00094839 | 54.8447 | 54.9133 | -68.5364 | 55.0323 | 54.8126 | 54.8172 | 54.689 | 54.9774 | 54.8676 | 8.4915 | -0.39368 | 0.1236 | 122.9874 | 123.175 | 0.022888 | 76.6342 | 0.07782 | 123.381 | 122.8317 | 123.1201 | 122.9553 | 123.056 | 122.9874 | 123.0103 | 122.9599 | 76.6342 | 123.056 | 122.9874 | 122.9599 | 122.9553 | 123.0103 | -123.3261 | -46.2982
4184.7656 | 123.2346 | -68.1931 | 54.8126 | 0.28587 | 0.014855 | 0.0070283 | 0.0094698 | -0.0086817 | -0.0028731 | -0.003512 | 54.8218 | 54.95 | -68.5684 | 55.0095 | 54.7668 | 54.7714 | 54.7531 | 54.9133 | 54.8813 | 8.4915 | -0.37537 | 0.13733 | 123.0148 | 123.2025 | -0.045776 | 76.6846 | 0.068665 | 123.3902 | 122.9462 | 123.1064 | 122.9599 | 123.143 | 123.0148 | 123.0743 | 122.9645 | 76.6846 | 123.143 | 123.0148 | 122.9645 | 122.9599 | 123.0743 | -123.381 | -46.3211
4185.7656 | 123.23 | -68.1564 | 54.808 | 0.2935 | 0.015069 | 0.0055329 | 0.0098972 | -0.0073999 | -0.0069321 | -0.0013758 | 54.8126 | 54.9454 | -68.5822 | 55.0049 | 54.7806 | 54.7623 | 54.7577 | 54.9271 | 54.9088 | 8.4915 | -0.42572 | 0.13733 | 122.9691 | 123.1613 | -0.027465 | 76.6479 | 0.10071 | 123.3948 | 122.9141 | 123.0835 | 122.937 | 123.1018 | 122.9691 | 123.0652 | 122.9187 | 76.6479 | 123.1018 | 122.9691 | 122.9187 | 122.937 | 123.0652 | -123.3902 | -46.3165
4186.7812 | 123.2574 | -68.1473 | 54.7943 | 0.19432 | 0.014428 | 0.0038239 | 0.0060518 | -0.0076135 | -0.0069321 | -0.0032984 | 54.8584 | 54.8859 | -68.5272 | 55.0598 | 54.8447 | 54.863 | 54.6661 | 55.0049 | 54.8767 | 8.4961 | -0.37994 | 0.091552 | 123.0057 | 123.2071 | 0.050354 | 76.6434 | 0.082397 | 123.3856 | 122.8134 | 123.1522 | 122.9919 | 123.0331 | 123.0057 | 123.024 | 123.0103 | 76.6434 | 123.0331 | 123.0057 | 123.0103 | 122.9919 | 123.024 | -123.3215 | -46.2982
4187.7812 | 123.2483 | -68.161 | 54.776 | 0.26299 | 0.011865 | 0.0036103 | 0.005411 | -0.0088953 | -0.0043685 | -0.0030848 | 54.8859 | 54.8996 | -68.541 | 55.0461 | 54.8447 | 54.8401 | 54.6707 | 55.0095 | 54.8676 | 8.5007 | -0.37994 | 0.1236 | 123.0469 | 123.2071 | 0.068665 | 76.6617 | 0.091553 | 123.4268 | 122.8317 | 123.1705 | 123.0057 | 123.0606 | 123.0469 | 123.0286 | 123.0011 | 76.6617 | 123.0606 | 123.0469 | 123.0011 | 123.0057 | 123.0286 | -123.317 | -46.2753
4188.7656 | 123.2437 | -68.1747 | 54.8126 | 0.17143 | 0.012933 | 0.0040375 | 0.0028476 | -0.0093225 | -0.0045821 | -0.0020166 | 54.8218 | 54.895 | -68.5455 | 55.0186 | 54.8172 | 54.8126 | 54.7348 | 54.982 | 54.8767 | 8.4961 | -0.37079 | 0.082398 | 122.9965 | 123.1934 | 0.004578 | 76.6708 | 0.064087 | 123.3673 | 122.9095 | 123.1567 | 122.9919 | 123.0698 | 122.9965 | 123.0515 | 122.9874 | 76.6708 | 123.0698 | 122.9965 | 122.9874 | 122.9919 | 123.0515 | -123.3582 | -46.3165
4189.7656 | 123.2162 | -68.1427 | 54.808 | 0.15617 | 0.0093012 | 0.0059601 | 0.0032748 | -0.011031 | -0.0058639 | -0.0026574 | 54.8172 | 54.895 | -68.5318 | 55.0323 | 54.808 | 54.8355 | 54.7211 | 54.9591 | 54.863 | 8.4915 | -0.3891 | 0.086976 | 122.9599 | 123.175 | 0 | 76.6342 | 0.054932 | 123.349 | 122.8638 | 123.1018 | 122.9507 | 123.0377 | 122.9599 | 123.0057 | 122.9782 | 76.6342 | 123.0377 | 122.9599 | 122.9782 | 122.9507 | 123.0057 | -123.3398 | -46.3165
4190.7656 | 123.2208 | -68.1564 | 54.8172 | 0.17906 | 0.012292 | 0.0059601 | 0.0039156 | -0.010604 | -0.0050095 | -0.0024438 | 54.8264 | 54.8859 | -68.5226 | 55.0232 | 54.8126 | 54.8126 | 54.7302 | 54.95 | 54.8584 | 8.4869 | -0.36621 | 0.068664 | 122.9828 | 123.1796 | -0.004578 | 76.6434 | 0.041198 | 123.349 | 122.8867 | 123.1064 | 122.9691 | 123.0423 | 122.9828 | 123.0148 | 122.9691 | 76.6434 | 123.0423 | 122.9828 | 122.9691 | 122.9691 | 123.0148 | -123.3398 | -46.3303
4191.7656 | 123.2529 | -68.1793 | 54.8035 | 0.21721 | 0.014214 | 0.0072419 | 0.0096834 | -0.0099633 | -0.0043685 | -0.0032984 | 54.8309 | 54.9271 | -68.5318 | 55.0369 | 54.8126 | 54.7943 | 54.7073 | 54.9591 | 54.8355 | 8.4961 | -0.35248 | 0.1236 | 123.0103 | 123.2162 | 0.009155 | 76.6754 | 0.032043 | 123.3627 | 122.8867 | 123.1384 | 122.9919 | 123.1064 | 123.0103 | 123.0148 | 122.9736 | 76.6754 | 123.1064 | 123.0103 | 122.9736 | 122.9919 | 123.0148 | -123.3353 | -46.3074
4192.7656 | 123.3124 | -68.1702 | 54.7623 | 0.2401 | 0.014214 | 0.0057465 | 0.0077608 | -0.0093225 | -0.0050095 | -0.0032984 | 54.8813 | 54.9133 | -68.5181 | 55.0644 | 54.8447 | 54.8676 | 54.6478 | 54.8035 | 54.8447 | 8.5007 | -0.3479 | 0.15106 | 123.0515 | 123.2346 | 0.082398 | 76.6708 | 0.082398 | 123.3994 | 122.818 | 122.9736 | 123.0148 | 123.0835 | 123.0515 | 123.0148 | 123.0377 | 76.6708 | 123.0835 | 123.0515 | 123.0377 | 123.0148 | 123.0148 | -123.2803 | -46.2616
4193.7812 | 123.2574 | -68.1564 | 54.7806 | 0.18669 | 0.012292 | 0.0087373 | 0.0056246 | -0.0097497 | -0.0073593 | -0.0020166 | 54.8492 | 54.8904 | -68.5318 | 55.0598 | 54.8447 | 54.8538 | 54.6707 | 54.9866 | 54.863 | 8.5007 | -0.37537 | 0.10986 | 123.0057 | 123.2162 | 0.064087 | 76.6571 | 0.082397 | 123.381 | 122.8271 | 123.143 | 123.0011 | 123.0469 | 123.0057 | 123.0194 | 123.0103 | 76.6571 | 123.0469 | 123.0057 | 123.0103 | 123.0011 | 123.0194 | -123.3124 | -46.2799
4194.7812 | 123.262 | -68.161 | 54.776 | 0.26299 | 0.012292 | 0.0048921 | 0.0064792 | -0.0086817 | -0.0077865 | -0.0022302 | 54.8538 | 54.895 | -68.5455 | 55.0735 | 54.8538 | 54.8538 | 54.6799 | 54.9957 | 54.8492 | 8.4915 | -0.38452 | 0.11902 | 123.0148 | 123.2346 | 0.07782 | 76.6525 | 0.073242 | 123.3994 | 122.8409 | 123.1567 | 123.0148 | 123.056 | 123.0148 | 123.0103 | 123.0148 | 76.6525 | 123.056 | 123.0148 | 123.0148 | 123.0148 | 123.0103 | -123.3215 | -46.2845
4195.7656 | 123.2574 | -68.1702 | 54.8172 | 0.1638 | 0.012505 | 0.0076691 | 0.0030612 | -0.012954 | -0.0037277 | -0.0047938 | 54.8172 | 54.8813 | -68.5318 | 55.0186 | 54.8172 | 54.8035 | 54.7531 | 54.9866 | 54.8721 | 8.4915 | -0.36163 | 0.064087 | 122.9874 | 123.1888 | 0 | 76.6617 | 0.054931 | 123.349 | 122.9233 | 123.1567 | 122.9874 | 123.0515 | 122.9874 | 123.0423 | 122.9736 | 76.6617 | 123.0515 | 122.9874 | 122.9736 | 122.9874 | 123.0423 | -123.349 | -46.3257
4196.7656 | 123.23 | -68.1564 | 54.7943 | 0.19432 | 0.012505 | 0.0070283 | 0.0047702 | -0.01274 | -0.0052231 | -0.0026574 | 54.8126 | 54.8859 | -68.5364 | 55.0278 | 54.8172 | 54.808 | 54.744 | 54.9683 | 54.863 | 8.4915 | -0.37994 | 0.091552 | 122.9691 | 123.1842 | 0.022888 | 76.6479 | 0.068664 | 123.349 | 122.9004 | 123.1247 | 122.9736 | 123.0423 | 122.9691 | 123.0194 | 122.9645 | 76.6479 | 123.0423 | 122.9691 | 122.9645 | 122.9736 | 123.0194 | -123.3307 | -46.3028
4197.7656 | 123.2529 | -68.1564 | 54.7806 | 0.27824 | 0.013146 | 0.0078827 | 0.0060518 | -0.0093225 | -0.0058639 | -0.00052119 | 54.8355 | 54.9133 | -68.5455 | 55.0278 | 54.7943 | 54.8309 | 54.7028 | 54.9591 | 54.863 | 8.4915 | -0.3891 | 0.13275 | 122.9919 | 123.1842 | 0.013733 | 76.6479 | 0.082397 | 123.381 | 122.8592 | 123.1155 | 122.9507 | 123.0698 | 122.9919 | 123.0194 | 122.9874 | 76.6479 | 123.0698 | 122.9919 | 122.9874 | 122.9507 | 123.0194 | -123.3261 | -46.2891
4198.7656 | 123.2712 | -68.1564 | 54.7897 | 0.2935 | 0.016137 | 0.0036103 | 0.011392 | -0.0073999 | -0.0052231 | -0.00052119 | 54.8447 | 54.9271 | -68.5547 | 55.0461 | 54.8264 | 54.8126 | 54.6753 | 54.9545 | 54.8676 | 8.4961 | -0.39825 | 0.13733 | 123.0011 | 123.2025 | 0.036621 | 76.6525 | 0.07782 | 123.3994 | 122.8317 | 123.111 | 122.9828 | 123.0835 | 123.0011 | 123.024 | 122.9691 | 76.6525 | 123.0835 | 123.0011 | 122.9691 | 122.9828 | 123.024 | -123.3444 | -46.2936
4199.7656 | 123.2666 | -68.1656 | 54.7897 | 0.2935 | 0.01336 | 0.0070283 | 0.00712 | -0.0093225 | -0.0060775 | -0.003512 | 54.8676 | 54.8904 | -68.5272 | 54.9179 | 54.7028 | 54.9179 | 54.7623 | 55.0278 | 54.863 | 8.4961 | -0.36163 | 0.10071 | 123.0331 | 123.0835 | -0.086975 | 76.6617 | 0.073242 | 123.3948 | 122.9279 | 123.1934 | 122.8683 | 123.056 | 123.0331 | 123.0286 | 123.0835 | 76.6617 | 123.056 | 123.0331 | 123.0835 | 122.8683 | 123.0286 | -123.317 | -46.2936
4200.7812 | 123.2712 | -68.1656 | 54.7897 | 0.21721 | 0.011224 | 0.0063873 | 0.0039156 | -0.0093225 | -0.0052231 | -0.0024438 | 54.8584 | 54.8813 | -68.5318 | 55.0644 | 54.863 | 54.8447 | 54.6753 | 54.9866 | 54.8859 | 8.4961 | -0.36621 | 0.091553 | 123.024 | 123.23 | 0.073242 | 76.6617 | 0.09613 | 123.3902 | 122.8409 | 123.1522 | 123.0286 | 123.0469 | 123.024 | 123.0515 | 123.0103 | 76.6617 | 123.0469 | 123.024 | 123.0103 | 123.0286 | 123.0515 | -123.3215 | -46.2936
4201.7812 | 123.2986 | -68.1656 | 54.7714 | 0.21721 | 0.013146 | 0.0066009 | 0.0047702 | -0.010177 | -0.0062911 | -0.0024438 | 54.8584 | 54.9088 | -68.5272 | 55.0507 | 54.8355 | 54.8584 | 54.6936 | 55.0095 | 54.8492 | 8.5007 | -0.36163 | 0.13733 | 123.024 | 123.2162 | 0.064087 | 76.6663 | 0.07782 | 123.3856 | 122.8592 | 123.175 | 123.0011 | 123.0743 | 123.024 | 123.0148 | 123.024 | 76.6663 | 123.0743 | 123.024 | 123.024 | 123.0011 | 123.0148 | -123.2986 | -46.2708
4202.7656 | 123.2437 | -68.1427 | 54.8355 | 0.14092 | 0.010369 | 0.0091645 | 0.0028476 | -0.012313 | -0.0060775 | -0.0030848 | 54.8126 | 54.9042 | -68.5318 | 55.0232 | 54.8172 | 54.8218 | 54.744 | 54.982 | 54.8538 | 8.5007 | -0.3891 | 0.068665 | 122.9553 | 123.1659 | -0.01831 | 76.6434 | 0.018311 | 123.3444 | 122.8867 | 123.1247 | 122.9599 | 123.0469 | 122.9553 | 122.9965 | 122.9645 | 76.6434 | 123.0469 | 122.9553 | 122.9645 | 122.9599 | 122.9965 | -123.3673 | -46.3348
4203.7656 | 123.23 | -68.161 | 54.8126 | 0.064621 | 0.01101 | 0.0066009 | 0.002634 | -0.0095361 | -0.0043685 | -0.0013758 | 54.7989 | 54.8813 | -68.5364 | 55.0369 | 54.8218 | 54.8309 | 54.7485 | 54.9866 | 54.895 | 8.4961 | -0.37537 | 0.068665 | 122.9599 | 123.1979 | 0.009155 | 76.6571 | 0.082398 | 123.3353 | 122.9095 | 123.1476 | 122.9828 | 123.0423 | 122.9599 | 123.056 | 122.9919 | 76.6571 | 123.0423 | 122.9599 | 122.9919 | 122.9828 | 123.056 | -123.349 | -46.3165
4204.7656 | 123.3124 | -68.1656 | 54.8035 | 0.36217 | 0.014642 | 0.0085235 | 0.0096834 | -0.011886 | -0.0075729 | -0.00094839 | 54.8721 | 54.9133 | -68.5593 | 55.0735 | 54.8401 | 54.8401 | 54.6707 | 54.982 | 54.8401 | 8.4961 | -0.39368 | 0.10986 | 123.0377 | 123.2391 | 0.036621 | 76.6617 | 0.036621 | 123.4314 | 122.8363 | 123.1476 | 123.0057 | 123.0789 | 123.0377 | 123.0057 | 123.0057 | 76.6617 | 123.0789 | 123.0377 | 123.0057 | 123.0057 | 123.0057 | -123.3627 | -46.3074
4205.7656 | 123.2895 | -68.1473 | 54.7943 | 0.20958 | 0.011651 | 0.0053193 | 0.010324 | -0.0095361 | -0.0056503 | -0.0020166 | 54.8492 | 54.9088 | -68.5501 | 55.0552 | 54.8447 | 54.8492 | 54.6753 | 54.9866 | 54.8676 | 8.4915 | -0.40283 | 0.11444 | 122.9965 | 123.2025 | 0.050354 | 76.6388 | 0.073242 | 123.3994 | 122.8226 | 123.1338 | 122.9919 | 123.056 | 122.9965 | 123.0148 | 122.9965 | 76.6388 | 123.056 | 122.9965 | 122.9965 | 122.9919 | 123.0148 | -123.3444 | -46.3028
4206.7656 | 123.2803 | -68.1747 | 54.7806 | -0.61439 | 0.011865 | 0.0057465 | 0.0049838 | -0.0082545 | -0.0084273 | -0.0030848 | 54.9362 | 54.9133 | -68.5226 | 55.0644 | 54.8492 | 54.8584 | 54.6524 | 55.0003 | 54.8538 | 8.4961 | -0.3479 | 0.13275 | 123.111 | 123.2391 | 0.068664 | 76.6708 | 0.073242 | 123.4589 | 122.8271 | 123.175 | 123.024 | 123.0881 | 123.111 | 123.0286 | 123.0331 | 76.6708 | 123.0881 | 123.111 | 123.0331 | 123.024 | 123.0286 | -123.3032 | -46.2845
4207.7812 | 123.2346 | -68.1702 | 54.8172 | 0.17906 | 0.009942 | 0.0055329 | 0.002634 | -0.0080407 | -0.0062911 | -0.0013758 | 54.7897 | 54.9088 | -68.5593 | 55.0232 | 54.8309 | 54.8218 | 54.7485 | 54.9728 | 54.8676 | 8.4961 | -0.3891 | 0.091552 | 122.9599 | 123.1934 | 0.013733 | 76.6663 | 0.050354 | 123.349 | 122.9187 | 123.143 | 123.0011 | 123.0789 | 122.9599 | 123.0377 | 122.9919 | 76.6663 | 123.0789 | 122.9599 | 122.9919 | 123.0011 | 123.0377 | -123.3765 | -46.3211
4208.7812 | 123.1796 | -68.1793 | 54.8767 | -0.12611 | 0.014001 | 0.0046783 | 0.0098972 | -0.010818 | -0.0050095 | -0.003512 | 54.8309 | 55.014 | -68.541 | 55.0415 | 54.7989 | 54.7714 | 54.9225 | 54.95 | 54.9591 | 8.4915 | -0.36163 | 0.13733 | 123.0103 | 123.2208 | -0.07782 | 76.6708 | 0.082397 | 123.3719 | 123.1018 | 123.1293 | 122.9782 | 123.1934 | 123.0103 | 123.1384 | 122.9507 | 76.6708 | 123.1934 | 123.0103 | 122.9507 | 122.9782 | 123.1384 | -123.4177 | -46.3852
4209.7656 | 123.2437 | -68.1564 | 54.8264 | 0.10277 | 0.010796 | 0.0053193 | 0.0028476 | -0.010604 | -0.0060775 | -0.00052119 | 54.8035 | 54.895 | -68.5226 | 55.0323 | 54.8309 | 54.7714 | 54.9225 | 54.9683 | 54.9225 | 8.4869 | -0.36621 | 0.068665 | 122.9599 | 123.1888 | 0.004578 | 76.6434 | 0.09613 | 123.3261 | 123.0789 | 123.1247 | 122.9874 | 123.0515 | 122.9599 | 123.0789 | 122.9279 | 76.6434 | 123.0515 | 122.9599 | 122.9279 | 122.9874 | 123.0789 | -123.349 | -46.3394
4210.7656 | 123.2574 | -68.1656 | 54.8401 | 0.17906 | 0.012292 | 0.0012605 | 0.004343 | -0.0121 | -0.0062911 | -0.0011622 | 54.808 | 54.9088 | -68.5181 | 55.0278 | 54.8355 | 54.8264 | 54.7714 | 55.0278 | 54.8676 | 8.5007 | -0.35248 | 0.068664 | 122.9736 | 123.1934 | -0.004578 | 76.6663 | 0.027466 | 123.3261 | 122.937 | 123.1934 | 123.0011 | 123.0743 | 122.9736 | 123.0331 | 122.9919 | 76.6663 | 123.0743 | 122.9736 | 122.9919 | 123.0011 | 123.0331 | -123.3582 | -46.3394
4211.7656 | 123.3215 | -68.1702 | 54.7531 | 0.26299 | 0.014428 | 0.010019 | 0.010324 | -0.0088953 | -0.0033005 | -0.0020166 | 54.8813 | 54.8996 | -68.5547 | 55.069 | 54.8447 | 54.8492 | 54.6478 | 54.9591 | 54.8355 | 8.5007 | -0.38452 | 0.14648 | 123.0515 | 123.2391 | 0.091553 | 76.6708 | 0.082397 | 123.436 | 122.818 | 123.1293 | 123.0148 | 123.0698 | 123.0515 | 123.0057 | 123.0194 | 76.6708 | 123.0698 | 123.0515 | 123.0194 | 123.0148 | 123.0057 | -123.3078 | -46.2524
4212.7656 | 123.3032 | -68.1839 | 54.7668 | 0.30113 | 0.012719 | 0.010019 | 0.0094698 | -0.0097497 | -0.0039413 | -0.0032984 | 54.8767 | 54.9133 | -68.5455 | 55.0781 | 54.8538 | 54.863 | 54.6616 | 55.0003 | 54.8492 | 8.5007 | -0.36163 | 0.14648 | 123.0606 | 123.262 | 0.086975 | 76.6846 | 0.082397 | 123.4222 | 122.8455 | 123.1842 | 123.0377 | 123.0972 | 123.0606 | 123.0331 | 123.0469 | 76.6846 | 123.0972 | 123.0606 | 123.0469 | 123.0377 | 123.0331 | -123.3124 | -46.2662
4213.7812 | 123.175 | -68.1519 | 54.895 | -1.4231 | 0.014001 | 0.0070283 | 0.0066928 | -0.0086817 | -0.0054367 | -0.0013758 | 54.7714 | 55.0232 | -68.5272 | 55.014 | 54.7852 | 54.776 | 54.9408 | 54.9728 | 54.9774 | 8.4961 | -0.37537 | 0.12817 | 122.9233 | 123.1659 | -0.10986 | 76.6479 | 0.082397 | 123.2986 | 123.0927 | 123.1247 | 122.937 | 123.175 | 122.9233 | 123.1293 | 122.9279 | 76.6479 | 123.175 | 122.9233 | 122.9279 | 122.937 | 123.1293 | -123.4222 | -46.3989
4214.7812 | 123.2208 | -68.1702 | 54.7989 | 0.21721 | 0.010369 | 0.0033967 | 0.003702 | -0.0084681 | -0.0047957 | -0.0020166 | 54.8355 | 54.8904 | -68.5501 | 55.0461 | 54.8355 | 54.8264 | 54.7256 | 54.9957 | 54.8996 | 8.5007 | -0.37994 | 0.091553 | 123.0057 | 123.2162 | 0.036621 | 76.6708 | 0.10071 | 123.3856 | 122.8958 | 123.1659 | 123.0057 | 123.0606 | 123.0057 | 123.0698 | 122.9965 | 76.6708 | 123.0606 | 123.0057 | 122.9965 | 123.0057 | 123.0698 | -123.349 | -46.2982
4215.7812 | 123.2483 | -68.1747 | 54.808 | 0.11803 | 0.010583 | 0.0063873 | 0.002634 | -0.011245 | -0.0054367 | -0.0028712 | 54.7852 | 54.8813 | -68.5547 | 55.0278 | 54.8309 | 54.8218 | 54.7485 | 54.982 | 54.8676 | 8.4915 | -0.37994 | 0.073243 | 122.9599 | 123.2025 | 0.022889 | 76.6663 | 0.05951 | 123.3398 | 122.9233 | 123.1567 | 123.0057 | 123.056 | 122.9599 | 123.0423 | 122.9965 | 76.6663 | 123.056 | 122.9599 | 122.9965 | 123.0057 | 123.0423 | -123.3627 | -46.3165
4216.7656 | 123.2346 | -68.1793 | 54.8401 | 0.1104 | 0.010156 | 0.00019226 | 0.0030612 | -0.010604 | -0.0052231 | -0.0028712 | 54.7989 | 54.9042 | -68.5043 | 55.0369 | 54.7897 | 54.8126 | 54.7668 | 55.0003 | 54.8859 | 8.4961 | -0.32501 | 0.064087 | 122.9782 | 123.2162 | -0.050354 | 76.6754 | 0.045776 | 123.3032 | 122.9462 | 123.1796 | 122.9691 | 123.0835 | 122.9782 | 123.0652 | 122.9919 | 76.6754 | 123.0835 | 122.9782 | 122.9919 | 122.9691 | 123.0652 | -123.3444 | -46.344
4217.7812 | 123.23 | -68.1427 | 54.808 | 0.17906 | 0.014001 | 0.0036103 | 0.0024202 | -0.012313 | -0.0041549 | -0.0013758 | 54.808 | 54.895 | -68.5455 | 55.0232 | 54.8035 | 54.8401 | 54.7577 | 54.9957 | 54.8538 | 8.4961 | -0.40283 | 0.086976 | 122.9507 | 123.1659 | -0.004577 | 76.6388 | 0.045777 | 123.3536 | 122.9004 | 123.1384 | 122.9462 | 123.0377 | 122.9507 | 122.9965 | 122.9828 | 76.6388 | 123.0377 | 122.9507 | 122.9828 | 122.9462 | 122.9965 | -123.3536 | -46.312
4218.7812 | 123.2803 | -68.1198 | 54.8401 | -2.7735 | 0.011437 | 0.0059601 | 0.0028476 | -0.013595 | -0.0069321 | -0.0022302 | 54.7394 | 54.9591 | -68.4769 | 55.1102 | 54.8676 | 54.8767 | 54.7806 | 55.0827 | 54.8859 | 8.4915 | -0.35706 | 0.11902 | 122.8592 | 123.23 | 0.027466 | 76.6113 | 0.045776 | 123.2162 | 122.9004 | 123.2025 | 122.9874 | 123.0789 | 122.8592 | 123.0057 | 122.9965 | 76.6113 | 123.0789 | 122.8592 | 122.9965 | 122.9874 | 123.0057 | -123.317 | -46.3486
4219.7656 | 123.2941 | -68.1519 | 54.7714 | 0.35454 | 0.014428 | 0.0074555 | 0.0084018 | -0.01274 | -0.0058639 | -0.0032984 | 54.8859 | 54.8996 | -68.5272 | 55.0827 | 54.8584 | 54.8492 | 54.6753 | 54.9957 | 54.8538 | 8.4961 | -0.37537 | 0.12817 | 123.0377 | 123.2346 | 0.086975 | 76.6479 | 0.082398 | 123.4131 | 122.8271 | 123.1476 | 123.0103 | 123.0515 | 123.0377 | 123.0057 | 123.0011 | 76.6479 | 123.0515 | 123.0377 | 123.0011 | 123.0103 | 123.0057 | -123.2986 | -46.2753
4220.7812 | 123.175 | -68.1152 | 54.8264 | -0.065079 | 0.011651 | 0.0048921 | 0.001993 | -0.013809 | -0.0067185 | -0.0015894 | 54.8767 | 54.9042 | -68.5181 | 55.1102 | 54.9088 | 54.9088 | 54.7806 | 55.2658 | 54.9133 | 8.4915 | -0.40283 | 0.07782 | 122.9919 | 123.2254 | 0.082397 | 76.6068 | 0.086975 | 123.3948 | 122.8958 | 123.381 | 123.024 | 123.0194 | 122.9919 | 123.0286 | 123.024 | 76.6068 | 123.0194 | 122.9919 | 123.024 | 123.024 | 123.0286 | -123.3444 | -46.3348
4221.7812 | 123.2391 | -68.1564 | 54.7852 | 0.18669 | 0.012078 | 0.0059601 | 0.0041292 | -0.011245 | -0.0082137 | -0.0013758 | 54.8492 | 54.8721 | -68.5501 | 55.0644 | 54.8355 | 54.8447 | 54.6844 | 54.982 | 54.8401 | 8.4961 | -0.39368 | 0.086975 | 123.0057 | 123.2208 | 0.050354 | 76.6525 | 0.054932 | 123.3994 | 122.8409 | 123.1384 | 122.9919 | 123.0286 | 123.0057 | 122.9965 | 123.0011 | 76.6525 | 123.0286 | 123.0057 | 123.0011 | 122.9919 | 122.9965 | -123.3353 | -46.2891
4222.7656 | 123.2803 | -68.1473 | 54.808 | 0.12566 | 0.013787 | 0.0033967 | 0.0022066 | -0.011886 | -0.0050095 | -0.00458 | 54.8035 | 54.9133 | -68.5593 | 55.0369 | 54.8264 | 54.8172 | 54.776 | 54.9683 | 54.8721 | 8.5007 | -0.41199 | 0.10529 | 122.9507 | 123.1842 | 0.018311 | 76.6479 | 0.064087 | 123.3627 | 122.9233 | 123.1155 | 122.9736 | 123.0606 | 122.9507 | 123.0194 | 122.9645 | 76.6479 | 123.0606 | 122.9507 | 122.9645 | 122.9736 | 123.0194 | -123.3673 | -46.3074
4223.7812 | 123.2895 | -68.1427 | 54.7989 | 0.21721 | 0.011224 | 0.0033967 | 0.0030612 | -0.011459 | -0.0047957 | -0.0028712 | 54.8309 | 54.8584 | -68.5272 | 55.0415 | 54.8218 | 54.8218 | 54.7394 | 54.982 | 54.8492 | 8.5007 | -0.38452 | 0.059509 | 122.9736 | 123.1842 | 0.022888 | 76.6434 | 0.050354 | 123.3582 | 122.8821 | 123.1247 | 122.9645 | 123.0011 | 122.9736 | 122.9919 | 122.9645 | 76.6434 | 123.0011 | 122.9736 | 122.9645 | 122.9645 | 122.9919 | -123.3261 | -46.2982
4224.7656 | 123.2483 | -68.1793 | 54.8309 | 0.15617 | 0.012292 | 0.0053193 | 0.0034884 | -0.011672 | -0.0054367 | -0.00052119 | 54.8218 | 54.8996 | -68.5318 | 55.0369 | 54.8355 | 54.8309 | 54.7348 | 54.9957 | 54.8492 | 8.4915 | -0.35248 | 0.068664 | 123.0011 | 123.2162 | 0.004577 | 76.6708 | 0.01831 | 123.3536 | 122.9141 | 123.175 | 123.0148 | 123.0789 | 123.0011 | 123.0286 | 123.0103 | 76.6708 | 123.0789 | 123.0011 | 123.0103 | 123.0148 | 123.0286 | -123.3627 | -46.3394
4225.7812 | 123.2803 | -68.1427 | 54.7668 | 0.27061 | 0.012933 | 0.0093781 | 0.0062656 | -0.010177 | -0.0050095 | -0.0037256 | 54.9316 | 54.8721 | -68.5822 | 55.101 | 54.8813 | 54.8538 | 54.6936 | 55.0369 | 54.8355 | 8.4915 | -0.43945 | 0.10529 | 123.0743 | 123.2437 | 0.11444 | 76.6342 | 0.068664 | 123.5138 | 122.8363 | 123.1796 | 123.024 | 123.0148 | 123.0743 | 122.9782 | 122.9965 | 76.6342 | 123.0148 | 123.0743 | 122.9965 | 123.024 | 122.9782 | -123.349 | -46.2753
4226.7656 | 123.262 | -68.1702 | 54.7989 | 0.2401 | 0.014001 | 0.0051057 | 0.0096834 | -0.0069727 | -0.0056503 | -0.003512 | 54.8401 | 54.9362 | -68.5684 | 55.0415 | 54.808 | 54.808 | 54.7211 | 54.9683 | 54.8538 | 8.5007 | -0.39825 | 0.13733 | 123.0103 | 123.2117 | 0.009155 | 76.6708 | 0.054932 | 123.4085 | 122.8912 | 123.1384 | 122.9782 | 123.1064 | 123.0103 | 123.024 | 122.9782 | 76.6708 | 123.1064 | 123.0103 | 122.9782 | 122.9782 | 123.024 | -123.3673 | -46.2982
4227.7812 | 123.2666 | -68.1564 | 54.8126 | 0.2401 | 0.011651 | 0.0038239 | 0.005411 | -0.0084681 | -0.0045821 | -0.0013758 | 54.8721 | 54.8813 | -68.5501 | 55.0781 | 54.8447 | 54.8538 | 54.6982 | 54.9866 | 54.8355 | 8.4961 | -0.39368 | 0.068665 | 123.0286 | 123.2346 | 0.032044 | 76.6525 | 0.022888 | 123.4222 | 122.8546 | 123.143 | 123.0011 | 123.0377 | 123.0286 | 122.9919 | 123.0103 | 76.6525 | 123.0377 | 123.0286 | 123.0103 | 123.0011 | 122.9919 | -123.3627 | -46.3165
4228.7812 | 123.2895 | -68.1519 | 54.7943 | 0.15617 | 0.01101 | 0.0046783 | 0.0069064 | -0.0097497 | -0.0065047 | -0.0013758 | 54.8859 | 54.9042 | -68.4998 | 55.069 | 54.8538 | 54.863 | 54.6707 | 54.9957 | 54.8218 | 8.5052 | -0.3479 | 0.10986 | 123.0377 | 123.2208 | 0.059509 | 76.6571 | 0.027465 | 123.3856 | 122.8226 | 123.1476 | 123.0057 | 123.056 | 123.0377 | 122.9736 | 123.0148 | 76.6571 | 123.056 | 123.0377 | 123.0148 | 123.0057 | 122.9736 | -123.2941 | -46.2891
4229.7656 | 123.2483 | -68.1793 | 54.8218 | 0.17143 | 0.011437 | 0.0021149 | 0.0034884 | -0.0088953 | -0.0037277 | -0.00094839 | 54.8126 | 54.895 | -68.5272 | 55.0278 | 54.8355 | 54.8172 | 54.7577 | 54.9728 | 54.8813 | 8.4961 | -0.3479 | 0.073243 | 122.9919 | 123.2071 | 0.013733 | 76.6754 | 0.05951 | 123.3398 | 122.937 | 123.1522 | 123.0148 | 123.0743 | 122.9919 | 123.0606 | 122.9965 | 76.6754 | 123.0743 | 122.9919 | 122.9965 | 123.0148 | 123.0606 | -123.349 | -46.3257
4230.7656 | 123.2254 | -68.1473 | 54.7897 | 0.15617 | 0.011437 | 0.0019013 | 0.0045566 | -0.0121 | -0.0035141 | -0.00458 | 54.8172 | 54.9088 | -68.5364 | 55.0461 | 54.8355 | 54.8218 | 54.7348 | 54.9774 | 54.8355 | 8.5052 | -0.3891 | 0.11902 | 122.9645 | 123.1934 | 0.045776 | 76.6525 | 0.045776 | 123.3536 | 122.8821 | 123.1247 | 122.9828 | 123.056 | 122.9645 | 122.9828 | 122.9691 | 76.6525 | 123.056 | 122.9645 | 122.9691 | 122.9828 | 122.9828 | -123.3261 | -46.2845
4231.7656 | 123.2208 | -68.1656 | 54.8309 | 0.20195 | 0.010796 | 0.0059601 | 0.0034884 | -0.010391 | -0.0052231 | -0.0020166 | 54.8355 | 54.895 | -68.5226 | 55.0415 | 54.8264 | 54.8309 | 54.7302 | 54.9866 | 54.8492 | 8.4869 | -0.35706 | 0.064087 | 123.0011 | 123.2071 | -0.004578 | 76.6525 | 0.01831 | 123.3582 | 122.8958 | 123.1522 | 122.9919 | 123.0606 | 123.0011 | 123.0148 | 122.9965 | 76.6525 | 123.0606 | 123.0011 | 122.9965 | 122.9919 | 123.0148 | -123.3536 | -46.344
4232.7656 | 123.2437 | -68.1519 | 54.7943 | 0.26299 | 0.013146 | 0.0080963 | 0.0096834 | -0.0095361 | -0.0058639 | -0.00052119 | 54.8218 | 54.9545 | -68.5959 | 55.0369 | 54.7943 | 54.7989 | 54.7531 | 54.95 | 54.863 | 8.5007 | -0.44403 | 0.16022 | 122.9736 | 123.1888 | 0 | 76.6525 | 0.068664 | 123.4177 | 122.905 | 123.1018 | 122.9462 | 123.1064 | 122.9736 | 123.0148 | 122.9507 | 76.6525 | 123.1064 | 122.9736 | 122.9507 | 122.9462 | 123.0148 | -123.3902 | -46.2936
4233.7656 | 123.2071 | -68.1793 | 54.8172 | 0.27824 | 0.014855 | 0.0040375 | 0.0096834 | -0.0091089 | -0.0047957 | -0.003512 | 54.808 | 54.9728 | -68.5776 | 55.0186 | 54.8172 | 54.776 | 54.7577 | 54.9179 | 54.8676 | 8.4961 | -0.39825 | 0.15564 | 122.9874 | 123.1979 | 0 | 76.6754 | 0.050354 | 123.3856 | 122.937 | 123.0972 | 122.9965 | 123.1522 | 122.9874 | 123.0469 | 122.9553 | 76.6754 | 123.1522 | 122.9874 | 122.9553 | 122.9965 | 123.0469 | -123.3948 | -46.3211
4234.7812 | 123.2895 | -68.1839 | 54.7897 | -0.62965 | 0.011437 | 0.0048921 | 0.004343 | -0.010818 | -0.0060775 | -0.0041528 | 54.9088 | 54.9362 | -68.5318 | 55.0781 | 54.8584 | 54.8492 | 54.6707 | 55.0049 | 54.8309 | 8.4915 | -0.3479 | 0.14648 | 123.0927 | 123.262 | 0.068664 | 76.6754 | 0.041199 | 123.4406 | 122.8546 | 123.1888 | 123.0423 | 123.1201 | 123.0927 | 123.0148 | 123.0331 | 76.6754 | 123.1201 | 123.0927 | 123.0331 | 123.0423 | 123.0148 | -123.3215 | -46.2982
4235.7812 | 123.3032 | -68.1519 | 54.7897 | 0.26299 | 0.012292 | 0.0089509 | 0.0081882 | -0.0093225 | -0.0056503 | -0.0011622 | 54.8767 | 54.8859 | -68.5364 | 55.1605 | 54.9271 | 54.8721 | 54.7394 | 55.0278 | 54.8538 | 8.4961 | -0.38452 | 0.09613 | 123.0286 | 123.3124 | 0.13733 | 76.6479 | 0.064087 | 123.4131 | 122.8912 | 123.1796 | 123.0789 | 123.0377 | 123.0286 | 123.0057 | 123.024 | 76.6479 | 123.0377 | 123.0286 | 123.024 | 123.0789 | 123.0057 | -123.3261 | -46.2936
4236.7656 | 123.2391 | -68.1519 | 54.8035 | 0.17906 | 0.013574 | 0.0027557 | 0.0051974 | -0.012313 | -0.0062911 | -0.0024438 | 54.8401 | 54.8996 | -68.5501 | 55.0232 | 54.8355 | 54.8309 | 54.7073 | 54.9866 | 54.8355 | 8.4915 | -0.39826 | 0.09613 | 122.9919 | 123.175 | 0.032043 | 76.6434 | 0.032043 | 123.3902 | 122.8592 | 123.1384 | 122.9874 | 123.0515 | 122.9919 | 122.9874 | 122.9828 | 76.6434 | 123.0515 | 122.9919 | 122.9828 | 122.9874 | 122.9874 | -123.3536 | -46.312
4237.7656 | 123.2666 | -68.1702 | 54.776 | 0.23247 | 0.012078 | 0.0036103 | 0.0047702 | -0.0095361 | -0.0052231 | -0.0030848 | 54.8584 | 54.9271 | -68.541 | 55.0461 | 54.8492 | 54.8355 | 54.6936 | 54.982 | 54.8813 | 8.4961 | -0.37079 | 0.15106 | 123.0286 | 123.2162 | 0.073242 | 76.6663 | 0.10529 | 123.3994 | 122.8638 | 123.1522 | 123.0194 | 123.0972 | 123.0286 | 123.0515 | 123.0057 | 76.6663 | 123.0972 | 123.0286 | 123.0057 | 123.0194 | 123.0515 | -123.317 | -46.2799
4238.7656 | 123.2803 | -68.1885 | 54.7943 | 0.18669 | 0.010796 | 0.0061737 | 0.0073336 | -0.0097497 | -0.0047957 | -0.0013758 | 54.8584 | 54.9179 | -68.5455 | 55.0598 | 54.8492 | 54.8584 | 54.6844 | 54.9957 | 54.8447 | 8.5007 | -0.35705 | 0.1236 | 123.0469 | 123.2483 | 0.054931 | 76.6891 | 0.050354 | 123.4039 | 122.8729 | 123.1842 | 123.0377 | 123.1064 | 123.0469 | 123.0331 | 123.0469 | 76.6891 | 123.1064 | 123.0469 | 123.0469 | 123.0377 | 123.0331 | -123.3398 | -46.2936
4239.7812 | 123.2437 | -68.1519 | 54.7943 | 0.21721 | 0.0093012 | 0.0055329 | 0.0060518 | -0.0095361 | -0.0058639 | -0.0013758 | 54.8447 | 54.8859 | -68.5684 | 55.0461 | 54.8401 | 54.8309 | 54.6982 | 55.0003 | 54.8538 | 8.5007 | -0.41657 | 0.091552 | 122.9965 | 123.1979 | 0.045776 | 76.6525 | 0.059509 | 123.4131 | 122.85 | 123.1522 | 122.9919 | 123.0377 | 122.9965 | 123.0057 | 122.9828 | 76.6525 | 123.0377 | 122.9965 | 122.9828 | 122.9919 | 123.0057 | -123.3627 | -46.2936
4240.7656 | 123.1888 | -68.2114 | 54.8218 | 0.12566 | 0.015923 | 0.0057465 | 0.011392 | -0.0084681 | -0.0058639 | -0.00094839 | 54.8035 | 54.9637 | -68.5593 | 54.9866 | 54.7668 | 54.7485 | 54.8264 | 54.8767 | 54.9179 | 8.4915 | -0.3479 | 0.14191 | 123.0148 | 123.1979 | -0.054931 | 76.7029 | 0.096131 | 123.3627 | 123.0377 | 123.0881 | 122.9782 | 123.175 | 123.0148 | 123.1293 | 122.9599 | 76.7029 | 123.175 | 123.0148 | 122.9599 | 122.9782 | 123.1293 | -123.381 | -46.3303
4241.7812 | 123.2758 | -68.1702 | 54.7943 | 0.26299 | 0.012933 | 0.0078827 | 0.0086154 | -0.0088953 | -0.0073593 | -0.0022302 | 54.8859 | 54.9408 | -68.5593 | 55.0735 | 54.8584 | 54.8859 | 54.6661 | 55.0003 | 54.863 | 8.5007 | -0.3891 | 0.14648 | 123.056 | 123.2437 | 0.064086 | 76.6708 | 0.068664 | 123.4451 | 122.8363 | 123.1705 | 123.0286 | 123.111 | 123.056 | 123.0331 | 123.056 | 76.6708 | 123.111 | 123.056 | 123.056 | 123.0286 | 123.0331 | -123.3536 | -46.2936
4242.7812 | 123.2758 | -68.1519 | 54.776 | 0.26299 | 0.014001 | 0.0053193 | 0.0081882 | -0.0099633 | -0.0067185 | -0.0020166 | 54.8584 | 54.95 | -68.5318 | 55.0644 | 54.863 | 54.8355 | 54.689 | 54.9957 | 54.8538 | 8.5007 | -0.37994 | 0.17395 | 123.0103 | 123.2162 | 0.086975 | 76.6525 | 0.07782 | 123.3902 | 122.8409 | 123.1476 | 123.0148 | 123.1018 | 123.0103 | 123.0057 | 122.9874 | 76.6525 | 123.1018 | 123.0103 | 122.9874 | 123.0148 | 123.0057 | -123.3078 | -46.2753
4243.7656 | 123.2895 | -68.1702 | 54.7897 | 0.1638 | 0.016351 | 0.0057465 | 0.0051974 | -0.0076135 | -0.0058639 | -0.0015894 | 54.8813 | 54.9362 | -68.5318 | 55.0461 | 54.8584 | 54.8538 | 54.6982 | 54.9866 | 54.8538 | 8.4961 | -0.36163 | 0.14648 | 123.0515 | 123.2162 | 0.068664 | 76.6663 | 0.064087 | 123.4131 | 122.8683 | 123.1567 | 123.0286 | 123.1064 | 123.0515 | 123.024 | 123.024 | 76.6663 | 123.1064 | 123.0515 | 123.024 | 123.0286 | 123.024 | -123.3215 | -46.2936
4244.7812 | 123.2666 | -68.1931 | 54.8126 | 0.07988 | 0.011865 | 0.0072419 | 0.0013522 | -0.011245 | -0.0052231 | -0.001803 | 54.7714 | 54.9042 | -68.5638 | 55.1331 | 55.0049 | 54.8904 | 54.7256 | 54.9728 | 54.895 | 8.4915 | -0.37079 | 0.091553 | 122.9645 | 123.3261 | 0.19226 | 76.6846 | 0.082398 | 123.3353 | 122.9187 | 123.1659 | 123.1979 | 123.0972 | 122.9645 | 123.0881 | 123.0835 | 76.6846 | 123.0972 | 122.9645 | 123.0835 | 123.1979 | 123.0881 | -123.3765 | -46.3211
4245.7656 | 123.2986 | -68.1473 | 54.776 | 0.31639 | 0.010583 | 0.0063873 | 0.0051974 | -0.0099633 | -0.0047957 | -0.0011622 | 54.8859 | 54.9133 | -68.5501 | 55.0644 | 54.8721 | 54.8859 | 54.6799 | 55.0232 | 54.8401 | 8.5007 | -0.40283 | 0.13733 | 123.0331 | 123.2117 | 0.09613 | 76.6479 | 0.064087 | 123.436 | 122.8271 | 123.1705 | 123.0194 | 123.0606 | 123.0331 | 122.9874 | 123.0331 | 76.6479 | 123.0606 | 123.0331 | 123.0331 | 123.0194 | 122.9874 | -123.3261 | -46.2753
4246.7656 | 123.175 | -68.1976 | 54.8538 | 0.18669 | 0.012292 | 0.0040375 | 0.010324 | -0.010604 | -0.0065047 | -0.0020166 | 54.7852 | 54.982 | -68.5684 | 54.9637 | 54.5746 | 54.5059 | 55.0552 | 55.101 | 54.8996 | 8.4961 | -0.37079 | 0.12817 | 122.9828 | 123.1613 | -0.27924 | 76.6937 | 0.045776 | 123.3536 | 123.2529 | 123.2986 | 122.7722 | 123.1796 | 122.9828 | 123.0972 | 122.7036 | 76.6937 | 123.1796 | 122.9828 | 122.7036 | 122.7722 | 123.0972 | -123.4222 | -46.3577
4247.7656 | 123.175 | -68.1931 | 54.8172 | 0.21721 | 0.014428 | 0.0063873 | 0.0077608 | -0.0067591 | -0.0067185 | -0.0022302 | 54.8218 | 54.9774 | -68.5822 | 54.982 | 54.7714 | 54.7531 | 54.8355 | 54.8904 | 54.9179 | 8.4869 | -0.3891 | 0.16022 | 123.0148 | 123.175 | -0.045777 | 76.68 | 0.10071 | 123.4039 | 123.0286 | 123.0835 | 122.9645 | 123.1705 | 123.0148 | 123.111 | 122.9462 | 76.68 | 123.1705 | 123.0148 | 122.9462 | 122.9645 | 123.111 | -123.3994 | -46.3303
4248.7812 | 123.2208 | -68.1885 | 54.8309 | 0.24773 | 0.013787 | 0.0091645 | 0.0079744 | -0.0080407 | -0.0060775 | -0.0026574 | 54.8126 | 54.9637 | -68.573 | 54.9957 | 54.7806 | 54.7897 | 54.7852 | 54.9225 | 54.895 | 8.4915 | -0.38452 | 0.13275 | 123.0011 | 123.1842 | -0.050354 | 76.68 | 0.064087 | 123.3856 | 122.9736 | 123.111 | 122.9691 | 123.1522 | 123.0011 | 123.0835 | 122.9782 | 76.68 | 123.1522 | 123.0011 | 122.9782 | 122.9691 | 123.0835 | -123.4039 | -46.3394
4249.7812 | 123.2803 | -68.1519 | 54.8172 | 0.011215 | 0.009942 | 0.0044647 | 0.0024202 | -0.0091089 | -0.0090683 | -0.0015894 | 54.8126 | 54.9133 | -68.5455 | 55.0781 | 54.8859 | 54.8721 | 54.7714 | 55.0507 | 54.895 | 8.5007 | -0.39368 | 0.09613 | 122.9645 | 123.23 | 0.068664 | 76.6525 | 0.07782 | 123.3582 | 122.9233 | 123.2025 | 123.0377 | 123.0652 | 122.9645 | 123.0469 | 123.024 | 76.6525 | 123.0652 | 122.9645 | 123.024 | 123.0377 | 123.0469 | -123.3627 | -46.3165
4250.7656 | 123.2803 | -68.2022 | 54.7943 | 0.38506 | 0.013146 | 0.013437 | 0.0084018 | -0.0082545 | -0.0056503 | -0.0026574 | 54.8859 | 54.9454 | -68.541 | 55.0552 | 54.8355 | 54.8355 | 54.6661 | 55.0003 | 54.8538 | 8.4961 | -0.33875 | 0.15106 | 123.0881 | 123.2574 | 0.041198 | 76.6983 | 0.059509 | 123.4268 | 122.8683 | 123.2025 | 123.0377 | 123.1476 | 123.0881 | 123.056 | 123.0377 | 76.6983 | 123.1476 | 123.0881 | 123.0377 | 123.0377 | 123.056 | -123.3353 | -46.2982
4251.7656 | 123.2529 | -68.1747 | 54.7806 | 0.25536 | 0.014642 | 0.0051057 | 0.0064792 | -0.0086817 | -0.0054367 | -0.0030848 | 54.8676 | 54.9454 | -68.5455 | 55.0552 | 54.8447 | 54.8492 | 54.6524 | 54.9866 | 54.8813 | 8.4961 | -0.37079 | 0.16479 | 123.0423 | 123.23 | 0.064087 | 76.6708 | 0.10071 | 123.4131 | 122.8271 | 123.1613 | 123.0194 | 123.1201 | 123.0423 | 123.056 | 123.024 | 76.6708 | 123.1201 | 123.0423 | 123.024 | 123.0194 | 123.056 | -123.3261 | -46.2845
4252.7656 | 123.1659 | -68.1747 | 54.8584 | 0.072251 | 0.016137 | 0.0085235 | 0.0098972 | -0.0071863 | -0.0041549 | -0.0024438 | 54.863 | 55.0095 | -68.5547 | 54.9774 | 54.7714 | 54.7531 | 54.8767 | 54.9042 | 54.9545 | 8.4915 | -0.37994 | 0.15106 | 123.0377 | 123.1522 | -0.086975 | 76.6663 | 0.096131 | 123.4177 | 123.0515 | 123.0789 | 122.9462 | 123.1842 | 123.0377 | 123.1293 | 122.9279 | 76.6663 | 123.1842 | 123.0377 | 122.9279 | 122.9462 | 123.1293 | -123.4131 | -46.3669
4253.7656 | 123.1567 | -68.2205 | 54.8355 | 0.064621 | 0.014001 | 0.0080963 | 0.008829 | -0.0067591 | -0.0054367 | -0.0013758 | 54.8447 | 55.0049 | -68.5364 | 55.014 | 54.7806 | 54.7623 | 54.8538 | 54.9179 | 54.9316 | 8.4915 | -0.31586 | 0.16937 | 123.0652 | 123.2346 | -0.054931 | 76.712 | 0.096131 | 123.381 | 123.0743 | 123.1384 | 123.0011 | 123.2254 | 123.0652 | 123.1522 | 122.9828 | 76.712 | 123.2254 | 123.0652 | 122.9828 | 123.0011 | 123.1522 | -123.3719 | -46.344
4254.7812 | 123.2803 | -68.1656 | 54.8218 | 0.10277 | 0.0086602 | 0.011087 | -0.0022794 | -0.0071863 | -0.0060775 | -0.00052119 | 54.7989 | 54.8904 | -68.5684 | 55.014 | 54.8447 | 54.8401 | 54.7897 | 54.9774 | 54.8676 | 8.4961 | -0.40283 | 0.068665 | 122.9645 | 123.1796 | 0.022889 | 76.6617 | 0.045777 | 123.3673 | 122.9553 | 123.143 | 123.0103 | 123.056 | 122.9645 | 123.0331 | 123.0057 | 76.6617 | 123.056 | 122.9645 | 123.0057 | 123.0103 | 123.0331 | -123.3902 | -46.3257
4255.7812 | 123.1613 | -68.1931 | 54.8309 | 0.20195 | 0.015283 | 0.0072419 | 0.0098972 | -0.0031275 | -0.0020187 | -0.0047938 | 54.8126 | 55.014 | -68.5455 | 55.188 | 54.8218 | 54.7806 | 54.8676 | 54.9042 | 54.9316 | 8.4915 | -0.35248 | 0.1831 | 123.0057 | 123.381 | -0.009156 | 76.6846 | 0.10071 | 123.3582 | 123.0606 | 123.0972 | 123.0148 | 123.2071 | 123.0057 | 123.1247 | 122.9736 | 76.6846 | 123.2071 | 123.0057 | 122.9736 | 123.0148 | 123.1247 | -123.3765 | -46.3394
4256.7812 | 123.1247 | -68.2205 | 54.7852 | 0.17906 | 0.015283 | 0.0089509 | 0.0096834 | -0.0078271 | -0.0067185 | -0.001803 | 54.808 | 55.0186 | -68.5867 | 54.9408 | 54.7485 | 54.744 | 54.8538 | 54.895 | 54.9316 | 8.4915 | -0.36621 | 0.23346 | 123.0286 | 123.1613 | -0.036621 | 76.712 | 0.14648 | 123.3948 | 123.0743 | 123.1155 | 122.9691 | 123.2391 | 123.0286 | 123.1522 | 122.9645 | 76.712 | 123.2391 | 123.0286 | 122.9645 | 122.9691 | 123.1522 | -123.3719 | -46.2936
4257.7656 | 123.2346 | -68.2022 | 54.8218 | 0.2401 | 0.015283 | 0.0055329 | 0.0073336 | -0.0050501 | -0.0056503 | -0.00052119 | 54.8172 | 55.0003 | -68.5684 | 54.9774 | 54.776 | 54.7806 | 54.7852 | 54.9133 | 54.9225 | 8.4869 | -0.36621 | 0.17853 | 123.0194 | 123.1796 | -0.045776 | 76.6891 | 0.10071 | 123.3856 | 122.9874 | 123.1155 | 122.9782 | 123.2025 | 123.0194 | 123.1247 | 122.9828 | 76.6891 | 123.2025 | 123.0194 | 122.9828 | 122.9782 | 123.1247 | -123.3902 | -46.3348
4258.7656 | 123.1888 | -68.2297 | 54.8172 | 0.19432 | 0.014428 | 0.0076691 | 0.0064792 | -0.0065455 | -0.0058639 | -0.0043664 | 54.8172 | 55.0049 | -68.5776 | 54.9957 | 54.7714 | 54.7623 | 54.8172 | 54.8996 | 54.9179 | 8.4915 | -0.3479 | 0.18768 | 123.0469 | 123.2254 | -0.045777 | 76.7212 | 0.10071 | 123.3948 | 123.0469 | 123.1293 | 123.0011 | 123.2346 | 123.0469 | 123.1476 | 122.9919 | 76.7212 | 123.2346 | 123.0469 | 122.9919 | 123.0011 | 123.1476 | -123.3948 | -46.3257
4259.7812 | 123.2895 | -68.1427 | 54.8309 | 0.072251 | 0.010156 | 0.0076691 | -0.00078396 | -0.0086817 | -0.0062911 | -0.00052119 | 54.895 | 54.9179 | -68.5364 | 55.0873 | 54.9088 | 54.8996 | 54.8035 | 55.1056 | 54.9454 | 8.4961 | -0.39368 | 0.086975 | 123.0377 | 123.23 | 0.077819 | 76.6388 | 0.11444 | 123.4314 | 122.9462 | 123.2483 | 123.0515 | 123.0606 | 123.0377 | 123.0881 | 123.0423 | 76.6388 | 123.0606 | 123.0377 | 123.0423 | 123.0515 | 123.0881 | -123.3673 | -46.3348
4260.7656 | 123.1934 | -68.1747 | 54.8401 | 0.20958 | 0.015283 | 0.01066 | 0.0077608 | -0.0078271 | -0.0056503 | -0.00030759 | 54.9179 | 55.0095 | -68.5455 | 55.0461 | 54.8126 | 54.8126 | 54.8447 | 54.9683 | 54.95 | 8.4869 | -0.37079 | 0.16937 | 123.0927 | 123.2208 | -0.027466 | 76.6617 | 0.10986 | 123.4634 | 123.0194 | 123.143 | 122.9874 | 123.1842 | 123.0927 | 123.1247 | 122.9874 | 76.6617 | 123.1842 | 123.0927 | 122.9874 | 122.9874 | 123.1247 | -123.3856 | -46.3531
4261.7812 | 123.143 | -68.2068 | 54.8538 | 0.056992 | 0.015069 | 0.0091645 | 0.0086154 | -0.0063317 | -0.0060775 | -0.0020166 | 54.8401 | 55.0323 | -68.5684 | 54.9637 | 54.7485 | 54.7302 | 54.8904 | 54.8859 | 54.9591 | 8.4869 | -0.36163 | 0.17853 | 123.0469 | 123.1705 | -0.10529 | 76.6937 | 0.10528 | 123.4085 | 123.0972 | 123.0927 | 122.9553 | 123.2391 | 123.0469 | 123.1659 | 122.937 | 76.6937 | 123.2391 | 123.0469 | 122.937 | 122.9553 | 123.1659 | -123.4222 | -46.3669
4262.7812 | 123.2071 | -68.1931 | 54.8309 | 0.13329 | 0.01571 | 0.0031831 | 0.0069064 | -0.0061181 | -0.0058639 | -0.00052119 | 54.8401 | 55.0278 | -68.5593 | 54.9545 | 54.7668 | 54.7623 | 54.8767 | 54.9088 | 54.9774 | 8.4824 | -0.36621 | 0.19684 | 123.0331 | 123.1476 | -0.064087 | 76.6754 | 0.14648 | 123.3994 | 123.0698 | 123.1018 | 122.9599 | 123.2208 | 123.0331 | 123.1705 | 122.9553 | 76.6754 | 123.2208 | 123.0331 | 122.9553 | 122.9599 | 123.1705 | -123.3902 | -46.3486
4263.7812 | 123.1979 | -68.1885 | 54.8492 | 0.095139 | 0.012292 | 0.0093781 | 0.008829 | -0.0056909 | -0.0039413 | -0.0032984 | 54.8355 | 55.0461 | -68.5684 | 54.9866 | 54.7943 | 54.7806 | 54.8721 | 54.9225 | 54.9637 | 8.4915 | -0.37994 | 0.19684 | 123.024 | 123.175 | -0.054931 | 76.68 | 0.11444 | 123.4039 | 123.0606 | 123.111 | 122.9828 | 123.2346 | 123.024 | 123.1522 | 122.9691 | 76.68 | 123.2346 | 123.024 | 122.9691 | 122.9828 | 123.1522 | -123.4177 | -46.3577
4264.7969 | 123.2071 | -68.1931 | 54.8264 | 0.17906 | 0.01336 | 0.00019226 | 0.0077608 | -0.0048365 | -0.0054367 | -0.0015894 | 54.9271 | 55.0003 | -68.573 | 55.0323 | 54.8401 | 54.8126 | 54.863 | 54.9683 | 54.9637 | 8.4869 | -0.37994 | 0.17395 | 123.1201 | 123.2254 | 0.013733 | 76.68 | 0.13733 | 123.5001 | 123.056 | 123.1613 | 123.0331 | 123.1934 | 123.1201 | 123.1567 | 123.0057 | 76.68 | 123.1934 | 123.1201 | 123.0057 | 123.0331 | 123.1567 | -123.3994 | -46.3394
4265.7812 | 123.1842 | -68.2022 | 54.8538 | 0.087509 | 0.013146 | 0.0072419 | 0.0077608 | -0.0059045 | -0.0052231 | -0.0020166 | 54.8447 | 55.0049 | -68.5776 | 54.9866 | 54.7623 | 54.7623 | 54.8904 | 54.9225 | 54.95 | 8.4824 | -0.37537 | 0.15106 | 123.0469 | 123.1888 | -0.091553 | 76.6846 | 0.09613 | 123.4222 | 123.0927 | 123.1247 | 122.9645 | 123.2071 | 123.0469 | 123.1522 | 122.9645 | 76.6846 | 123.2071 | 123.0469 | 122.9645 | 122.9645 | 123.1522 | -123.4314 | -46.3715
4266.7812 | 123.1476 | -68.2114 | 54.8264 | 0.07988 | 0.013146 | 0.0083099 | 0.010324 | -0.0052637 | -0.0028731 | -0.0032984 | 54.8035 | 54.9957 | -68.5684 | 54.9454 | 54.7714 | 54.744 | 54.8813 | 54.8676 | 54.9545 | 8.5007 | -0.35706 | 0.16937 | 123.0148 | 123.1567 | -0.054932 | 76.712 | 0.12817 | 123.3719 | 123.0927 | 123.0789 | 122.9828 | 123.2071 | 123.0148 | 123.1659 | 122.9553 | 76.712 | 123.2071 | 123.0148 | 122.9553 | 122.9828 | 123.1659 | -123.3948 | -46.3257
4267.7812 | 123.1979 | -68.2159 | 54.8447 | 0.018845 | 0.013787 | 0.0080963 | 0.0079744 | -0.0071863 | -0.0065047 | -0.0039392 | 54.8859 | 55.0278 | -68.5684 | 55.0049 | 54.8218 | 54.7989 | 54.8538 | 54.9408 | 54.9683 | 8.4915 | -0.35248 | 0.18311 | 123.1018 | 123.2208 | -0.022889 | 76.7075 | 0.1236 | 123.4543 | 123.0698 | 123.1567 | 123.0377 | 123.2437 | 123.1018 | 123.1842 | 123.0148 | 76.7075 | 123.2437 | 123.1018 | 123.0148 | 123.0377 | 123.1842 | -123.4131 | -46.3531
4268.7812 | 123.1338 | -68.2159 | 54.8538 | 0.14854 | 0.012505 | 0.010446 | 0.0060518 | -0.0050501 | -0.0054367 | 0.00097421 | 54.808 | 55.014 | -68.5638 | 54.9408 | 54.7302 | 54.7211 | 54.8859 | 54.8767 | 54.9637 | 8.5007 | -0.3479 | 0.16022 | 123.024 | 123.1567 | -0.1236 | 76.7166 | 0.10986 | 123.3719 | 123.1018 | 123.0927 | 122.9462 | 123.23 | 123.024 | 123.1796 | 122.937 | 76.7166 | 123.23 | 123.024 | 122.937 | 122.9462 | 123.1796 | -123.4177 | -46.3531
4269.7969 | 123.2208 | -68.2205 | 54.8538 | -0.11085 | 0.016992 | 0.0059601 | 0.0079744 | -0.0076135 | -0.0056503 | -0.0022302 | 54.8813 | 55.0598 | -68.5547 | 55.0232 | 54.8401 | 54.8309 | 54.8767 | 54.9957 | 54.9774 | 8.4915 | -0.33417 | 0.20599 | 123.1018 | 123.2437 | -0.013733 | 76.712 | 0.1236 | 123.436 | 123.0972 | 123.2162 | 123.0606 | 123.2803 | 123.1018 | 123.1979 | 123.0515 | 76.712 | 123.2803 | 123.1018 | 123.0515 | 123.0606 | 123.1979 | -123.4085 | -46.3623
4270.7812 | 123.2758 | -68.1656 | 54.8126 | 0.2401 | 0.014855 | 0.0089509 | 0.0079744 | -0.0052637 | -0.0058639 | -0.00073479 | 54.8401 | 54.9454 | -68.5593 | 55.0323 | 54.8172 | 54.8492 | 54.7302 | 54.9728 | 54.9271 | 8.5007 | -0.39368 | 0.13275 | 123.0057 | 123.1979 | 0.004578 | 76.6663 | 0.11444 | 123.3994 | 122.8958 | 123.1384 | 122.9828 | 123.111 | 123.0057 | 123.0927 | 123.0148 | 76.6663 | 123.111 | 123.0057 | 123.0148 | 122.9828 | 123.0927 | -123.3719 | -46.312
4271.7812 | 123.1705 | -68.2068 | 54.8309 | -0.33211 | 0.013146 | 0.0023285 | 0.0045566 | -0.0065455 | -0.0065047 | -0.00073479 | 54.7806 | 55.0095 | -68.5867 | 54.9545 | 54.7668 | 54.7531 | 54.8447 | 54.9042 | 54.9545 | 8.4915 | -0.37994 | 0.17853 | 122.9874 | 123.1613 | -0.064087 | 76.6983 | 0.1236 | 123.3673 | 123.0515 | 123.111 | 122.9736 | 123.2162 | 122.9874 | 123.1613 | 122.9599 | 76.6983 | 123.2162 | 122.9874 | 122.9599 | 122.9736 | 123.1613 | -123.4177 | -46.3394
4272.7812 | 123.262 | -68.2068 | 54.7852 | 0.20958 | 0.010796 | 0.00083306 | 0.00071144 | -0.0088953 | -0.0077865 | -0.0011622 | 54.8492 | 54.8996 | -68.5593 | 55.0278 | 54.8401 | 54.8538 | 54.7165 | 55.0049 | 54.9088 | 8.4915 | -0.35248 | 0.11444 | 123.056 | 123.2346 | 0.054932 | 76.6983 | 0.1236 | 123.4085 | 122.9233 | 123.2117 | 123.0469 | 123.1064 | 123.056 | 123.1155 | 123.0606 | 76.6983 | 123.1064 | 123.056 | 123.0606 | 123.0469 | 123.1155 | -123.3444 | -46.2936
4273.7812 | 123.1979 | -68.1931 | 54.8447 | 0.072251 | 0.015283 | 0.0057465 | 0.0094698 | -0.0065455 | -0.0069321 | -0.0026574 | 54.863 | 55.0232 | -68.5547 | 54.9911 | 54.7806 | 54.7714 | 54.8676 | 54.9179 | 54.9454 | 8.4869 | -0.36163 | 0.17853 | 123.056 | 123.1842 | -0.064087 | 76.68 | 0.10071 | 123.4177 | 123.0606 | 123.111 | 122.9736 | 123.2162 | 123.056 | 123.1384 | 122.9645 | 76.68 | 123.2162 | 123.056 | 122.9645 | 122.9736 | 123.1384 | -123.3994 | -46.3577
4274.7969 | 123.143 | -68.2159 | 54.8309 | 0.19432 | 0.016351 | 0.0083099 | 0.0069064 | -0.0052637 | -0.0069321 | -0.0013758 | 54.8264 | 55.0186 | -68.5638 | 54.9454 | 54.7394 | 54.7348 | 54.8996 | 54.8859 | 54.95 | 8.4869 | -0.3479 | 0.18768 | 123.0423 | 123.1613 | -0.091553 | 76.7029 | 0.11902 | 123.3902 | 123.1155 | 123.1018 | 122.9553 | 123.2346 | 123.0423 | 123.1659 | 122.9507 | 76.7029 | 123.2346 | 123.0423 | 122.9507 | 122.9553 | 123.1659 | -123.3948 | -46.344
4275.7812 | 123.0377 | -68.2159 | 54.7668 | 0.15617 | 0.015496 | -0.0010895 | 0.0056246 | -0.0046229 | -0.0077865 | -0.0028712 | 54.8126 | 55.0003 | -68.5913 | 54.9545 | 54.7531 | 54.7394 | 54.8492 | 54.895 | 54.9911 | 8.4869 | -0.37537 | 0.23346 | 123.0286 | 123.1705 | -0.013733 | 76.7029 | 0.2243 | 123.4039 | 123.0652 | 123.111 | 122.9691 | 123.2162 | 123.0286 | 123.2071 | 122.9553 | 76.7029 | 123.2162 | 123.0286 | 122.9553 | 122.9691 | 123.2071 | -123.3582 | -46.2799
4276.7812 | 123.2666 | -68.1702 | 54.7897 | 0.30876 | 0.012719 | 0.00019226 | 0.0024202 | -0.0048365 | -0.0067185 | -0.0024438 | 54.8447 | 54.895 | -68.5501 | 55.0461 | 54.8538 | 54.8538 | 54.6982 | 55.0186 | 54.9225 | 8.5007 | -0.37994 | 0.10529 | 123.0148 | 123.2162 | 0.064087 | 76.6708 | 0.13275 | 123.3948 | 122.8683 | 123.1888 | 123.024 | 123.0652 | 123.0148 | 123.0927 | 123.024 | 76.6708 | 123.0652 | 123.0148 | 123.024 | 123.024 | 123.0927 | -123.3398 | -46.2891
4277.7812 | 123.1796 | -68.2114 | 54.8447 | 0.11803 | 0.015283 | 0.0072419 | 0.0086154 | -0.0067591 | -0.0069321 | -0.0026574 | 54.8264 | 55.0095 | -68.541 | 54.9774 | 54.776 | 54.7485 | 54.8492 | 54.8859 | 54.9545 | 8.4915 | -0.32959 | 0.16479 | 123.0377 | 123.1888 | -0.068665 | 76.7029 | 0.10986 | 123.3673 | 123.0606 | 123.0972 | 122.9874 | 123.2208 | 123.0377 | 123.1659 | 122.9599 | 76.7029 | 123.2208 | 123.0377 | 122.9599 | 122.9874 | 123.1659 | -123.3856 | -46.3531
4278.7812 | 123.2529 | -68.1793 | 54.7989 | 0.27061 | 0.013787 | 0.0051057 | 0.0056246 | -0.0071863 | -0.0035141 | -0.0013758 | 54.8355 | 54.9728 | -68.5593 | 55.0323 | 54.8126 | 54.8264 | 54.7211 | 54.9911 | 54.9088 | 8.4961 | -0.37994 | 0.17395 | 123.0148 | 123.2117 | 0.013733 | 76.6754 | 0.10986 | 123.3948 | 122.9004 | 123.1705 | 122.9919 | 123.1522 | 123.0148 | 123.0881 | 123.0057 | 76.6754 | 123.1522 | 123.0148 | 123.0057 | 122.9919 | 123.0881 | -123.3582 | -46.3028
4279.7969 | 123.0698 | -68.2343 | 54.776 | 0.10277 | 0.014001 | 0.0072419 | 0.0092562 | -0.0063317 | -0.0054367 | -0.0020166 | 54.7989 | 55.014 | -68.5867 | 54.95 | 54.744 | 54.7256 | 54.8721 | 54.8904 | 54.9454 | 8.4915 | -0.35248 | 0.23804 | 123.0331 | 123.1842 | -0.032043 | 76.7258 | 0.16937 | 123.3856 | 123.1064 | 123.1247 | 122.9782 | 123.2483 | 123.0331 | 123.1796 | 122.9599 | 76.7258 | 123.2483 | 123.0331 | 122.9599 | 122.9782 | 123.1796 | -123.3627 | -46.2845
4280.7812 | 123.2986 | -68.1244 | 54.8447 | -0.13374 | 0.0095148 | 0.0046783 | -0.002493 | -0.011459 | -0.0058639 | -0.00073479 | 54.895 | 54.8904 | -68.5364 | 55.0827 | 54.9042 | 54.9133 | 54.776 | 55.1056 | 54.9454 | 8.5007 | -0.41199 | 0.045776 | 123.0194 | 123.2071 | 0.059509 | 76.6251 | 0.10071 | 123.4314 | 122.9004 | 123.23 | 123.0286 | 123.0148 | 123.0194 | 123.0698 | 123.0377 | 76.6251 | 123.0148 | 123.0194 | 123.0377 | 123.0286 | 123.0698 | -123.381 | -46.344
4281.7812 | 123.2391 | -68.2343 | 54.8447 | 0.20958 | 0.014001 | 0.0048921 | 0.008829 | -0.0061181 | -0.0069321 | -0.003512 | 54.7989 | 55.0003 | -68.5501 | 54.9637 | 54.7668 | 54.7256 | 54.8584 | 54.8721 | 54.9454 | 8.4915 | -0.31586 | 0.15564 | 123.0331 | 123.1979 | -0.07782 | 76.7258 | 0.10071 | 123.349 | 123.0927 | 123.1064 | 123.0011 | 123.2346 | 123.0331 | 123.1796 | 122.9599 | 76.7258 | 123.2346 | 123.0331 | 122.9599 | 123.0011 | 123.1796 | -123.3948 | -46.3531
4282.7812 | 123.2849 | -68.1656 | 54.7897 | 0.20958 | 0.012505 | 0.0070283 | 0.0049838 | -0.0086817 | -0.0043685 | -0.0028712 | 54.863 | 54.9316 | -68.5226 | 55.0507 | 54.8401 | 54.8676 | 54.6936 | 55.014 | 54.8676 | 8.5007 | -0.35706 | 0.14191 | 123.0286 | 123.2162 | 0.050354 | 76.6663 | 0.07782 | 123.3856 | 122.8592 | 123.1796 | 123.0057 | 123.0972 | 123.0286 | 123.0331 | 123.0331 | 76.6663 | 123.0972 | 123.0286 | 123.0331 | 123.0057 | 123.0331 | -123.3124 | -46.2891
4283.7812 | 123.1567 | -68.2068 | 54.863 | 0.10277 | 0.013787 | 0.0087373 | 0.0077608 | -0.0088953 | -0.0041549 | -0.0022302 | 54.8447 | 55.0003 | -68.5684 | 54.9683 | 54.7394 | 54.7348 | 54.8584 | 54.8859 | 54.9408 | 8.4915 | -0.36163 | 0.13733 | 123.0515 | 123.175 | -0.1236 | 76.6983 | 0.07782 | 123.4131 | 123.0652 | 123.0927 | 122.9462 | 123.2071 | 123.0515 | 123.1476 | 122.9416 | 76.6983 | 123.2071 | 123.0515 | 122.9416 | 122.9462 | 123.1476 | -123.4314 | -46.3715
4284.7969 | 123.2941 | -68.1564 | 54.8309 | -0.080337 | 0.0093012 | 0.0019013 | -0.00078396 | -0.011031 | -0.0054367 | -9.3992e-05 | 54.8355 | 54.8996 | -68.5547 | 55.069 | 54.8859 | 54.8904 | 54.7623 | 55.0735 | 54.9408 | 8.4961 | -0.39825 | 0.068664 | 122.9919 | 123.2254 | 0.054931 | 76.6525 | 0.10986 | 123.3902 | 122.9187 | 123.23 | 123.0423 | 123.056 | 122.9919 | 123.0972 | 123.0469 | 76.6525 | 123.056 | 122.9919 | 123.0469 | 123.0423 | 123.0972 | -123.3856 | -46.3348
4285.7812 | 123.3765 | -68.1747 | 54.7943 | 0.23247 | 0.015283 | 0.0033967 | 0.0045566 | -0.0093225 | -0.0050095 | -0.00094839 | 54.8767 | 54.9133 | -68.5364 | 55.0461 | 54.8401 | 54.8447 | 54.6753 | 55.0003 | 54.863 | 8.4961 | -0.36163 | 0.11902 | 123.0515 | 123.2208 | 0.045776 | 76.6708 | 0.068664 | 123.4131 | 122.85 | 123.175 | 123.0148 | 123.0881 | 123.0515 | 123.0377 | 123.0194 | 76.6708 | 123.0881 | 123.0515 | 123.0194 | 123.0148 | 123.0377 | -123.3307 | -46.2982
4286.7812 | 123.2986 | -68.1885 | 54.808 | -0.087967 | 0.011437 | 0.0027557 | 0.0032748 | -0.0080407 | -0.0050095 | -0.0015894 | 54.8584 | 54.895 | -68.5226 | 55.0461 | 54.8355 | 54.8676 | 54.6707 | 55.0278 | 54.8904 | 8.4961 | -0.33417 | 0.086976 | 123.0469 | 123.2346 | 0.027466 | 76.6846 | 0.082398 | 123.381 | 122.8592 | 123.2162 | 123.024 | 123.0835 | 123.0469 | 123.0789 | 123.056 | 76.6846 | 123.0835 | 123.0469 | 123.056 | 123.024 | 123.0789 | -123.3307 | -46.312
4287.7812 | 123.2712 | -68.1793 | 54.8035 | 0.2401 | 0.012933 | 0.011941 | 0.0077608 | -0.0082545 | -0.0058639 | -0.0011622 | 54.8401 | 54.9728 | -68.5501 | 55.014 | 54.808 | 54.8218 | 54.7165 | 54.9728 | 54.9042 | 8.5007 | -0.37079 | 0.16937 | 123.0194 | 123.1934 | 0.004577 | 76.68 | 0.10071 | 123.3902 | 122.8958 | 123.1522 | 122.9874 | 123.1522 | 123.0194 | 123.0835 | 123.0011 | 76.68 | 123.1522 | 123.0194 | 123.0011 | 122.9874 | 123.0835 | -123.3536 | -46.3028
4288.7812 | 123.2712 | -68.1885 | 54.808 | 0.20195 | 0.011865 | 0.0036103 | 0.0011386 | -0.0084681 | -0.0054367 | -0.0026574 | 54.8355 | 54.8904 | -68.5593 | 55.014 | 54.8355 | 54.8309 | 54.7348 | 54.982 | 54.895 | 8.4961 | -0.37079 | 0.082398 | 123.024 | 123.2025 | 0.027466 | 76.6846 | 0.086976 | 123.3948 | 122.9233 | 123.1705 | 123.024 | 123.0789 | 123.024 | 123.0835 | 123.0194 | 76.6846 | 123.0789 | 123.024 | 123.0194 | 123.024 | 123.0835 | -123.3673 | -46.312
4289.7969 | 123.349 | -68.1427 | 54.8126 | 0.11803 | 0.010156 | 0.0074555 | -0.00057036 | -0.011459 | -0.0058639 | -0.0028712 | 54.808 | 54.9133 | -68.5638 | 55.014 | 54.8264 | 54.8401 | 54.7668 | 54.982 | 54.895 | 8.4915 | -0.42114 | 0.10071 | 122.9507 | 123.1567 | 0.013733 | 76.6342 | 0.082398 | 123.3719 | 122.9095 | 123.1247 | 122.9691 | 123.056 | 122.9507 | 123.0377 | 122.9828 | 76.6342 | 123.056 | 122.9507 | 122.9828 | 122.9691 | 123.0377 | -123.3765 | -46.3211
4290.7812 | 123.2712 | -68.1519 | 54.8355 | 0.0035856 | 0.0080194 | -0.00023494 | -0.00014316 | -0.0121 | -0.0073593 | -0.001803 | 54.8218 | 54.895 | -68.541 | 55.0644 | 54.8584 | 54.8859 | 54.7485 | 55.0461 | 54.895 | 8.4961 | -0.3891 | 0.05951 | 122.9736 | 123.2162 | 0.022888 | 76.6479 | 0.05951 | 123.3627 | 122.9004 | 123.1979 | 123.0103 | 123.0469 | 122.9736 | 123.0469 | 123.0377 | 76.6479 | 123.0469 | 122.9736 | 123.0377 | 123.0103 | 123.0469 | -123.3765 | -46.3394
4291.7812 | 123.2941 | -68.1839 | 54.7943 | 0.2401 | 0.013574 | 0.0059601 | 0.005411 | -0.0097497 | -0.0058639 | -0.0015894 | 54.8767 | 54.895 | -68.5272 | 55.0598 | 54.8492 | 54.8538 | 54.6753 | 55.0186 | 54.8767 | 8.4961 | -0.34332 | 0.10071 | 123.0606 | 123.2437 | 0.054931 | 76.68 | 0.082397 | 123.4039 | 122.8592 | 123.2025 | 123.0331 | 123.0789 | 123.0606 | 123.0606 | 123.0377 | 76.68 | 123.0789 | 123.0606 | 123.0377 | 123.0331 | 123.0606 | -123.3215 | -46.2982
4292.7812 | 123.262 | -68.1747 | 54.8172 | -0.04219 | 0.0093012 | 0.00083306 | 0.0017794 | -0.010177 | -0.0075729 | -0.0011622 | 54.8172 | 54.9042 | -68.5455 | 55.0415 | 54.8447 | 54.8309 | 54.7806 | 55.014 | 54.8904 | 8.4961 | -0.37079 | 0.086975 | 122.9919 | 123.2162 | 0.027466 | 76.6708 | 0.073242 | 123.3627 | 122.9553 | 123.1888 | 123.0194 | 123.0789 | 122.9919 | 123.0652 | 123.0057 | 76.6708 | 123.0789 | 122.9919 | 123.0057 | 123.0194 | 123.0652 | -123.3627 | -46.3211
4293.7812 | 123.2529 | -68.161 | 54.7989 | 0.21721 | 0.0090876 | 0.0083099 | 0.0047702 | -0.011031 | -0.0058639 | -0.0024438 | 54.863 | 54.8813 | -68.5593 | 55.0598 | 54.8492 | 54.8401 | 54.6799 | 54.9957 | 54.863 | 8.4961 | -0.39825 | 0.082398 | 123.024 | 123.2208 | 0.050354 | 76.6571 | 0.064087 | 123.4222 | 122.8409 | 123.1567 | 123.0103 | 123.0423 | 123.024 | 123.024 | 123.0011 | 76.6571 | 123.0423 | 123.024 | 123.0011 | 123.0103 | 123.024 | -123.3582 | -46.3028
4294.7969 | 123.1842 | -68.1747 | 54.8813 | 0.072251 | 0.01336 | 0.0012605 | 0.0086154 | -0.011886 | -0.0069321 | -0.0032984 | 54.8218 | 54.9866 | -68.5684 | 55.0507 | 54.8172 | 54.7897 | 54.9316 | 54.9591 | 54.9454 | 8.5007 | -0.39368 | 0.10529 | 122.9965 | 123.2254 | -0.064087 | 76.6754 | 0.064087 | 123.3902 | 123.1064 | 123.1338 | 122.9919 | 123.1613 | 122.9965 | 123.1201 | 122.9645 | 76.6754 | 123.1613 | 122.9965 | 122.9645 | 122.9919 | 123.1201 | -123.4497 | -46.3806
4295.7812 | 123.3032 | -68.1381 | 54.8401 | -0.17952 | 0.01101 | 0.0044647 | 0.0034884 | -0.010818 | -0.0071457 | -0.0028712 | 54.8904 | 54.8721 | -68.5272 | 55.1147 | 54.9133 | 54.8721 | 54.7852 | 55.0964 | 54.9362 | 8.5052 | -0.3891 | 0.032043 | 123.0286 | 123.2529 | 0.073242 | 76.6434 | 0.09613 | 123.4177 | 122.9233 | 123.2346 | 123.0515 | 123.0103 | 123.0286 | 123.0743 | 123.0103 | 76.6434 | 123.0103 | 123.0286 | 123.0103 | 123.0515 | 123.0743 | -123.3673 | -46.3348
4296.7969 | 123.2803 | -68.1381 | 54.863 | -0.15663 | 0.0084466 | 0.0055329 | 0.0034884 | -0.012527 | -0.0069321 | -0.0015894 | 54.895 | 54.9225 | -68.541 | 55.1102 | 54.9042 | 54.8721 | 54.7897 | 55.0735 | 54.9088 | 8.5007 | -0.40283 | 0.059509 | 123.0331 | 123.2483 | 0.041199 | 76.6388 | 0.045776 | 123.436 | 122.9279 | 123.2117 | 123.0423 | 123.0606 | 123.0331 | 123.0469 | 123.0103 | 76.6388 | 123.0606 | 123.0331 | 123.0103 | 123.0423 | 123.0469 | -123.4039 | -46.3623
4297.7812 | 123.2574 | -68.1747 | 54.8264 | 0.064621 | 0.008233 | 0.0038239 | 0.0017794 | -0.012954 | -0.0058639 | -0.0037256 | 54.895 | 54.9408 | -68.5364 | 55.0598 | 54.8492 | 54.8035 | 54.7623 | 55.0003 | 54.9042 | 8.4961 | -0.36163 | 0.11444 | 123.0698 | 123.2346 | 0.022888 | 76.6708 | 0.07782 | 123.4314 | 122.937 | 123.175 | 123.024 | 123.1155 | 123.0698 | 123.0789 | 122.9782 | 76.6708 | 123.1155 | 123.0698 | 122.9782 | 123.024 | 123.0789 | -123.3627 | -46.3303
4298.7812 | 123.1522 | -68.2343 | 54.8538 | 0.12566 | 0.015496 | 0.0066009 | 0.011392 | -0.011459 | -0.0071457 | -0.0039392 | 54.8218 | 55.0186 | -68.573 | 54.9866 | 54.7485 | 54.7302 | 54.8721 | 54.863 | 54.9179 | 8.4915 | -0.33875 | 0.16479 | 123.056 | 123.2208 | -0.10529 | 76.7258 | 0.064087 | 123.3948 | 123.1064 | 123.0972 | 122.9828 | 123.2529 | 123.056 | 123.1522 | 122.9645 | 76.7258 | 123.2529 | 123.056 | 122.9645 | 122.9828 | 123.1522 | -123.4268 | -46.3623
4299.7969 | 123.3032 | -68.1427 | 54.8309 | -0.011673 | 0.010156 | -2.1336e-05 | 0.00049764 | -0.0097497 | -0.0082137 | -0.0032984 | 54.8447 | 54.9042 | -68.5318 | 55.101 | 54.9179 | 54.8859 | 54.744 | 55.0644 | 54.8904 | 8.5007 | -0.3891 | 0.073242 | 122.9874 | 123.2437 | 0.086975 | 76.6434 | 0.059509 | 123.3765 | 122.8867 | 123.2071 | 123.0606 | 123.0469 | 122.9874 | 123.0331 | 123.0286 | 76.6434 | 123.0469 | 122.9874 | 123.0286 | 123.0606 | 123.0331 | -123.3627 | -46.3303
4300.7812 | 123.2071 | -68.2159 | 54.8676 | 0.22484 | 0.014001 | 0.0078827 | 0.010324 | -0.0078271 | -0.0050095 | -0.0043664 | 54.8172 | 54.9683 | -68.5913 | 55.1743 | 54.9042 | 54.7531 | 54.9088 | 54.895 | 54.9362 | 8.4961 | -0.37537 | 0.10071 | 123.0331 | 123.3902 | 0.036621 | 76.712 | 0.068664 | 123.4085 | 123.1247 | 123.111 | 123.1201 | 123.1842 | 123.0331 | 123.1522 | 122.9691 | 76.712 | 123.1842 | 123.0331 | 122.9691 | 123.1201 | 123.1522 | -123.4589 | -46.3715
4301.7812 | 123.1888 | -68.1931 | 54.8813 | 0.50713 | 0.014642 | 0.0046783 | 0.0051974 | -0.0093225 | -0.0073593 | -0.0024438 | 54.8355 | 55.0186 | -68.5364 | 55.0323 | 54.8355 | 54.7989 | 54.9225 | 54.95 | 54.9728 | 8.5007 | -0.34332 | 0.13733 | 123.0286 | 123.2254 | -0.045777 | 76.6937 | 0.091552 | 123.3719 | 123.1155 | 123.143 | 123.0286 | 123.2117 | 123.0286 | 123.1659 | 122.9919 | 76.6937 | 123.2117 | 123.0286 | 122.9919 | 123.0286 | 123.1659 | -123.4177 | -46.3806
4302.7812 | 123.1888 | -68.1793 | 54.8767 | -0.16426 | 0.012292 | 0.0078827 | 0.0062656 | -0.0088953 | -0.0052231 | -0.0024438 | 54.8264 | 55.0186 | -68.5547 | 55.0003 | 54.8218 | 54.7577 | 54.9271 | 54.9545 | 54.9683 | 8.5007 | -0.37537 | 0.14191 | 123.0057 | 123.1796 | -0.054932 | 76.68 | 0.091553 | 123.381 | 123.1064 | 123.1338 | 123.0011 | 123.1979 | 123.0057 | 123.1476 | 122.937 | 76.68 | 123.1979 | 123.0057 | 122.937 | 123.0011 | 123.1476 | -123.4314 | -46.376
4303.7812 | 123.2025 | -68.1931 | 54.8767 | -0.16426 | 0.013574 | 0.010019 | 0.0084018 | -0.0078271 | -0.0067185 | -0.0020166 | 54.8126 | 55.014 | -68.5684 | 55.0369 | 54.8172 | 54.7852 | 54.9362 | 54.9683 | 54.9683 | 8.4961 | -0.37537 | 0.13733 | 123.0057 | 123.23 | -0.059509 | 76.6891 | 0.091553 | 123.381 | 123.1293 | 123.1613 | 123.0103 | 123.2071 | 123.0057 | 123.1613 | 122.9782 | 76.6891 | 123.2071 | 123.0057 | 122.9782 | 123.0103 | 123.1613 | -123.4451 | -46.3806
4304.7812 | 123.1842 | -68.2114 | 54.8401 | 0.23247 | 0.015069 | 0.0044647 | 0.012674 | -0.00013669 | -0.0082137 | -0.0024438 | 54.808 | 54.9957 | -68.605 | 55.0507 | 54.8309 | 54.7897 | 54.8309 | 54.9545 | 54.9179 | 8.5007 | -0.39368 | 0.15564 | 123.0194 | 123.262 | -0.009155 | 76.712 | 0.07782 | 123.4131 | 123.0423 | 123.1659 | 123.0423 | 123.2071 | 123.0194 | 123.1293 | 123.0011 | 76.712 | 123.2071 | 123.0194 | 123.0011 | 123.0423 | 123.1293 | -123.4451 | -46.3394
4305.7812 | 123.2346 | -68.1839 | 54.8355 | -0.087967 | 0.014428 | 0.0063873 | 0.0073336 | -0.0052637 | -0.0071457 | -0.0020166 | 54.895 | 55.0186 | -68.5501 | 55.0507 | 54.8538 | 54.8264 | 54.863 | 54.9911 | 54.95 | 8.4915 | -0.36621 | 0.18311 | 123.0789 | 123.2346 | 0.018311 | 76.6754 | 0.11444 | 123.4451 | 123.0469 | 123.175 | 123.0377 | 123.2025 | 123.0789 | 123.1338 | 123.0103 | 76.6754 | 123.2025 | 123.0789 | 123.0103 | 123.0377 | 123.1338 | -123.3856 | -46.344
4306.7812 | 123.1796 | -68.1976 | 54.8447 | 0.056992 | 0.014214 | 0.0040375 | 0.0064792 | -0.0059045 | -0.0067185 | -0.001803 | 54.8538 | 55.014 | -68.5455 | 55.0003 | 54.8126 | 54.7897 | 54.863 | 54.9179 | 54.9591 | 8.4915 | -0.3479 | 0.16937 | 123.0515 | 123.1979 | -0.032044 | 76.6891 | 0.11444 | 123.3994 | 123.0606 | 123.1155 | 123.0103 | 123.2117 | 123.0515 | 123.1567 | 122.9874 | 76.6891 | 123.2117 | 123.0515 | 122.9874 | 123.0103 | 123.1567 | -123.3902 | -46.3531
4307.7812 | 123.1934 | -68.1931 | 54.8767 | -0.17189 | 0.012933 | 0.0053193 | 0.0051974 | -0.0061181 | -0.0054367 | -0.00030759 | 54.7897 | 55.0232 | -68.5638 | 55.014 | 54.9545 | 54.9774 | 54.8538 | 54.8447 | 54.9911 | 8.5052 | -0.37079 | 0.14648 | 122.9828 | 123.2071 | 0.07782 | 76.6983 | 0.11444 | 123.3536 | 123.0469 | 123.0377 | 123.1476 | 123.2162 | 122.9828 | 123.1842 | 123.1705 | 76.6983 | 123.2162 | 122.9828 | 123.1705 | 123.1476 | 123.1842 | -123.4406 | -46.3715
4308.7812 | 123.2483 | -68.1702 | 54.8721 | -0.065079 | 0.012719 | 0.0042511 | 0.00712 | -0.0065455 | -0.0065047 | -0.0032984 | 54.895 | 54.9866 | -68.5684 | 55.0507 | 54.7897 | 54.6524 | 54.9362 | 54.9911 | 54.9316 | 8.4961 | -0.39825 | 0.11444 | 123.0652 | 123.2208 | -0.082397 | 76.6663 | 0.05951 | 123.4634 | 123.1064 | 123.1613 | 122.9599 | 123.1567 | 123.0652 | 123.1018 | 122.8226 | 76.6663 | 123.1567 | 123.0652 | 122.8226 | 122.9599 | 123.1018 | -123.4406 | -46.376
4309.7812 | 123.2117 | -68.2114 | 54.8401 | 0.20195 | 0.014214 | 0.0089509 | 0.0081882 | -0.0059045 | -0.0045821 | -0.0030848 | 54.808 | 54.9911 | -68.573 | 54.9728 | 54.776 | 54.7806 | 54.8355 | 54.8996 | 54.9637 | 8.4961 | -0.36163 | 0.15106 | 123.0194 | 123.1842 | -0.064087 | 76.7075 | 0.1236 | 123.381 | 123.0469 | 123.111 | 122.9874 | 123.2025 | 123.0194 | 123.175 | 122.9919 | 76.7075 | 123.2025 | 123.0194 | 122.9919 | 122.9874 | 123.175 | -123.4131 | -46.344
4310.7812 | 123.2162 | -68.1747 | 54.8676 | -0.16426 | 0.012505 | 0.0033967 | 0.0056246 | -0.0067591 | -0.0060775 | -0.0037256 | 54.8218 | 55.0186 | -68.5593 | 55.0049 | 54.8264 | 54.8126 | 54.9362 | 54.9866 | 54.9362 | 8.4915 | -0.38452 | 0.15106 | 122.9965 | 123.1796 | -0.041199 | 76.6663 | 0.068664 | 123.381 | 123.111 | 123.1613 | 123.0011 | 123.1934 | 122.9965 | 123.111 | 122.9874 | 76.6663 | 123.1934 | 122.9965 | 122.9874 | 123.0011 | 123.111 | -123.4268 | -46.376
4311.7812 | 123.2071 | -68.1656 | 54.8584 | -0.11085 | 0.012292 | 0.0074555 | 0.0064792 | -0.0099633 | -0.0058639 | -0.0024438 | 54.8676 | 55.0323 | -68.541 | 55.0507 | 54.8538 | 54.8355 | 54.8996 | 54.9911 | 54.9591 | 8.5052 | -0.37537 | 0.17395 | 123.0331 | 123.2162 | -0.004577 | 76.6708 | 0.10071 | 123.4085 | 123.0652 | 123.1567 | 123.0194 | 123.1979 | 123.0331 | 123.1247 | 123.0011 | 76.6708 | 123.1979 | 123.0331 | 123.0011 | 123.0194 | 123.1247 | -123.3994 | -46.3531
4312.7812 | 123.2574 | -68.1793 | 54.8538 | -0.080337 | 0.011651 | 0.0074555 | 0.0069064 | -0.0071863 | -0.0071457 | 0.00011961 | 54.9042 | 55.0278 | -68.5455 | 55.0369 | 54.8492 | 54.776 | 54.8492 | 55.0186 | 54.9179 | 8.5007 | -0.36621 | 0.17395 | 123.0835 | 123.2162 | -0.004578 | 76.68 | 0.064087 | 123.4497 | 123.0286 | 123.1979 | 123.0286 | 123.2071 | 123.0835 | 123.0972 | 122.9553 | 76.68 | 123.2071 | 123.0835 | 122.9553 | 123.0286 | 123.0972 | -123.3994 | -46.3531
4313.7812 | 123.2346 | -68.1519 | 54.8538 | -0.011673 | 0.012078 | 0.0046783 | 0.0056246 | -0.0069727 | -0.0067185 | -0.001803 | 54.8813 | 55.014 | -68.5593 | 55.0415 | 54.8447 | 54.8218 | 54.8813 | 55.0095 | 54.9637 | 8.5007 | -0.40741 | 0.16022 | 123.0331 | 123.1934 | -0.009155 | 76.6525 | 0.10986 | 123.4406 | 123.0331 | 123.1613 | 122.9965 | 123.1659 | 123.0331 | 123.1155 | 122.9736 | 76.6525 | 123.1659 | 123.0331 | 122.9736 | 122.9965 | 123.1155 | -123.4131 | -46.3531
4314.7812 | 123.3124 | -68.1473 | 54.8447 | -0.12611 | 0.011224 | 0.0027557 | -0.002493 | -0.0071863 | -0.0090683 | 0.00033321 | 54.8767 | 54.9179 | -68.5501 | 55.0781 | 54.9225 | 54.8904 | 54.8172 | 55.0873 | 54.9271 | 8.5007 | -0.40283 | 0.073242 | 123.024 | 123.2254 | 0.077819 | 76.6479 | 0.082397 | 123.4268 | 122.9645 | 123.2346 | 123.0698 | 123.0652 | 123.024 | 123.0743 | 123.0377 | 76.6479 | 123.0652 | 123.024 | 123.0377 | 123.0698 | 123.0743 | -123.3948 | -46.344
4315.7812 | 123.2666 | -68.1702 | 54.863 | -0.20241 | 0.010583 | 0.0010467 | 0.0013522 | -0.010604 | -0.0080001 | -0.0022302 | 54.8721 | 54.9454 | -68.5181 | 55.0598 | 54.863 | 54.8584 | 54.863 | 55.0461 | 54.9545 | 8.5052 | -0.3479 | 0.082398 | 123.0423 | 123.23 | 0 | 76.6754 | 0.091553 | 123.3902 | 123.0331 | 123.2162 | 123.0331 | 123.1155 | 123.0423 | 123.1247 | 123.0286 | 76.6754 | 123.1155 | 123.0423 | 123.0286 | 123.0331 | 123.1247 | -123.381 | -46.3577
4316.7812 | 123.1842 | -68.1931 | 54.8767 | -0.27107 | 0.01336 | 0.0042511 | 0.00712 | -0.0082545 | -0.0073593 | -0.00052119 | 54.8035 | 55.0003 | -68.573 | 55.0278 | 54.8309 | 54.7943 | 54.9362 | 54.9866 | 54.9866 | 8.4915 | -0.37994 | 0.1236 | 122.9965 | 123.2208 | -0.045776 | 76.6846 | 0.10986 | 123.3765 | 123.1293 | 123.1796 | 123.024 | 123.1934 | 122.9965 | 123.1796 | 122.9874 | 76.6846 | 123.1934 | 122.9965 | 122.9874 | 123.024 | 123.1796 | -123.4497 | -46.3852
4317.7812 | 123.1979 | -68.161 | 54.863 | -0.13374 | 0.013146 | 0.0042511 | 0.0079744 | -0.0088953 | -0.0052231 | -0.0020166 | 54.8447 | 54.9911 | -68.5593 | 55.0278 | 54.8172 | 54.8035 | 54.9362 | 54.9957 | 54.9545 | 8.5007 | -0.39825 | 0.12817 | 123.0057 | 123.1888 | -0.045776 | 76.6617 | 0.091553 | 123.4039 | 123.0972 | 123.1567 | 122.9782 | 123.1522 | 123.0057 | 123.1155 | 122.9645 | 76.6617 | 123.1522 | 123.0057 | 122.9645 | 122.9782 | 123.1155 | -123.4222 | -46.3623
4318.7812 | 123.175 | -68.161 | 54.8721 | -0.18715 | 0.009942 | 0.0029693 | -0.00099756 | -0.0082545 | -0.0035141 | -0.0020166 | 54.8264 | 55.0003 | -68.5913 | 55.014 | 54.8126 | 54.7897 | 54.9728 | 54.9911 | 54.9957 | 8.4961 | -0.4303 | 0.12817 | 122.9874 | 123.175 | -0.059509 | 76.6571 | 0.1236 | 123.4177 | 123.1338 | 123.1522 | 122.9736 | 123.1613 | 122.9874 | 123.1567 | 122.9507 | 76.6571 | 123.1613 | 122.9874 | 122.9507 | 122.9736 | 123.1567 | -123.4634 | -46.376
4319.7812 | 123.1979 | -68.1747 | 54.863 | 0.38506 | 0.011651 | 0.0059601 | 0.0056246 | -0.0097497 | -0.0090683 | -0.0030848 | 54.7897 | 54.9911 | -68.573 | 55.0186 | 54.8172 | 54.8035 | 54.9728 | 54.9774 | 54.9911 | 8.5007 | -0.39825 | 0.12817 | 122.9645 | 123.1934 | -0.045776 | 76.6754 | 0.12817 | 123.3627 | 123.1476 | 123.1522 | 122.9919 | 123.1659 | 122.9645 | 123.1659 | 122.9782 | 76.6754 | 123.1659 | 122.9645 | 122.9782 | 122.9919 | 123.1659 | -123.436 | -46.3623
4320.7812 | 123.2071 | -68.1885 | 54.9133 | -0.13374 | 0.012292 | 0.0061737 | 0.005411 | -0.0071863 | -0.0062911 | -0.0015894 | 54.8447 | 55.0003 | -68.5776 | 55.0186 | 54.808 | 54.7989 | 54.9408 | 55.0003 | 54.982 | 8.5007 | -0.3891 | 0.086975 | 123.0331 | 123.2071 | -0.10529 | 76.6891 | 0.068665 | 123.4222 | 123.1293 | 123.1888 | 122.9965 | 123.1888 | 123.0331 | 123.1705 | 122.9874 | 76.6891 | 123.1888 | 123.0331 | 122.9874 | 122.9965 | 123.1705 | -123.4909 | -46.4127
4321.7812 | 123.2025 | -68.2114 | 54.8767 | -0.065079 | 0.012292 | 0.0033967 | 0.0041292 | -0.0086817 | -0.0080001 | -0.00073479 | 54.8172 | 55.0232 | -68.5638 | 55.0186 | 54.8172 | 54.7897 | 54.9454 | 54.9866 | 54.9774 | 8.5007 | -0.35248 | 0.14648 | 123.0286 | 123.23 | -0.059509 | 76.712 | 0.10071 | 123.381 | 123.1567 | 123.1979 | 123.0286 | 123.2346 | 123.0286 | 123.1888 | 123.0011 | 76.712 | 123.2346 | 123.0286 | 123.0011 | 123.0286 | 123.1888 | -123.4406 | -46.376
4322.7812 | 123.2941 | -68.1564 | 54.8401 | -0.149 | 0.012292 | 0.0038239 | 0.00028404 | -0.011031 | -0.0062911 | -0.00073479 | 54.8859 | 54.9271 | -68.5455 | 55.0827 | 54.895 | 54.8859 | 54.8309 | 55.0827 | 54.9362 | 8.5007 | -0.3891 | 0.086975 | 123.0423 | 123.2391 | 0.054932 | 76.6571 | 0.09613 | 123.4314 | 122.9874 | 123.2391 | 123.0515 | 123.0835 | 123.0423 | 123.0927 | 123.0423 | 76.6571 | 123.0835 | 123.0423 | 123.0423 | 123.0515 | 123.0927 | -123.3856 | -46.3394
4323.7812 | 123.3398 | -68.1519 | 54.8584 | -0.12611 | 0.0090876 | 0.00040586 | 7.0444e-05 | -0.0086817 | -0.0071457 | 0.00097421 | 54.8813 | 54.9271 | -68.5318 | 55.101 | 54.9316 | 54.9225 | 54.7623 | 55.1239 | 54.8996 | 8.4961 | -0.37994 | 0.068665 | 123.0331 | 123.2529 | 0.073243 | 76.6479 | 0.041199 | 123.4131 | 122.9141 | 123.2758 | 123.0835 | 123.0789 | 123.0331 | 123.0515 | 123.0743 | 76.6479 | 123.0789 | 123.0331 | 123.0743 | 123.0835 | 123.0515 | -123.3902 | -46.3623
4324.7812 | 123.143 | -68.2159 | 54.808 | 0.31639 | 0.014428 | 0.0068147 | 0.0096834 | -0.0069727 | -0.0082137 | -0.0037256 | 54.7989 | 55.0003 | -68.5776 | 54.982 | 54.7577 | 54.7302 | 54.8492 | 54.9088 | 54.9545 | 8.4869 | -0.36163 | 0.19226 | 123.0148 | 123.1979 | -0.050354 | 76.7029 | 0.14648 | 123.3765 | 123.0652 | 123.1247 | 122.9736 | 123.2162 | 123.0148 | 123.1705 | 122.9462 | 76.7029 | 123.2162 | 123.0148 | 122.9462 | 122.9736 | 123.1705 | -123.3856 | -46.3211
4325.7812 | 123.2117 | -68.1656 | 54.8767 | -0.20241 | 0.011865 | 0.0038239 | 0.0047702 | -0.0080407 | -0.0080001 | -0.0022302 | 54.8721 | 54.9591 | -68.5455 | 55.0598 | 54.863 | 54.8218 | 54.9088 | 55.0095 | 54.9591 | 8.4915 | -0.37994 | 0.082397 | 123.0377 | 123.2254 | -0.013733 | 76.6571 | 0.082397 | 123.4177 | 123.0743 | 123.175 | 123.0286 | 123.1247 | 123.0377 | 123.1247 | 122.9874 | 76.6571 | 123.1247 | 123.0377 | 122.9874 | 123.0286 | 123.1247 | -123.4222 | -46.3852
4326.7812 | 123.2071 | -68.2022 | 54.8859 | -0.095596 | 0.012292 | 0.0038239 | 0.0062656 | -0.0091089 | -0.0080001 | -0.0037256 | 54.8218 | 55.014 | -68.5684 | 55.0278 | 54.8035 | 54.7806 | 54.9408 | 54.982 | 54.9728 | 8.5007 | -0.36621 | 0.12817 | 123.024 | 123.23 | -0.082397 | 76.7029 | 0.086975 | 123.3902 | 123.143 | 123.1842 | 123.0057 | 123.2162 | 123.024 | 123.175 | 122.9828 | 76.7029 | 123.2162 | 123.024 | 122.9828 | 123.0057 | 123.175 | -123.4543 | -46.3852
4327.7812 | 123.3124 | -68.1702 | 54.8447 | -0.057449 | 0.0097284 | -0.0019439 | -0.00078396 | -0.0097497 | -0.0056503 | -0.0032984 | 54.8538 | 54.8996 | -68.573 | 55.0781 | 54.8996 | 54.9042 | 54.7531 | 55.0873 | 54.9316 | 8.5007 | -0.40283 | 0.054931 | 123.024 | 123.2483 | 0.054931 | 76.6708 | 0.086975 | 123.4268 | 122.9233 | 123.2574 | 123.0698 | 123.0698 | 123.024 | 123.1018 | 123.0743 | 76.6708 | 123.0698 | 123.024 | 123.0743 | 123.0698 | 123.1018 | -123.4177 | -46.344
4328.7812 | 123.2025 | -68.1976 | 54.8813 | -0.149 | 0.012933 | 0.0046783 | 0.0075472 | -0.0099633 | -0.0058639 | -0.00073479 | 54.8492 | 55.0003 | -68.5455 | 55.0232 | 54.8126 | 54.7897 | 54.9454 | 54.9637 | 54.9728 | 8.4961 | -0.3479 | 0.11902 | 123.0469 | 123.2208 | -0.068665 | 76.6937 | 0.091552 | 123.3948 | 123.143 | 123.1613 | 123.0103 | 123.1979 | 123.0469 | 123.1705 | 122.9874 | 76.6937 | 123.1979 | 123.0469 | 122.9874 | 123.0103 | 123.1705 | -123.4268 | -46.3852
4329.7812 | 123.2071 | -68.2159 | 54.8676 | 0.07988 | 0.014642 | 0.0066009 | 0.010324 | -0.0048365 | -0.0043685 | -0.0024438 | 54.9133 | 55.0095 | -68.5684 | 55.0507 | 54.8172 | 54.8035 | 54.8767 | 54.9637 | 54.9728 | 8.4915 | -0.35248 | 0.14191 | 123.1293 | 123.2666 | -0.050354 | 76.7075 | 0.10529 | 123.4818 | 123.0927 | 123.1796 | 123.0331 | 123.2254 | 123.1293 | 123.1888 | 123.0194 | 76.7075 | 123.2254 | 123.1293 | 123.0194 | 123.0331 | 123.1888 | -123.436 | -46.376
4330.7812 | 123.3032 | -68.1747 | 54.8538 | -0.149 | 0.011865 | 0.0053193 | -0.00078396 | -0.0093225 | -0.0067185 | -0.00094839 | 54.895 | 54.9454 | -68.5364 | 55.0919 | 54.895 | 54.895 | 54.8035 | 55.0781 | 54.9545 | 8.5007 | -0.36163 | 0.091553 | 123.0698 | 123.2666 | 0.041199 | 76.6754 | 0.10071 | 123.4314 | 122.9782 | 123.2529 | 123.0698 | 123.1201 | 123.0698 | 123.1293 | 123.0698 | 76.6754 | 123.1201 | 123.0698 | 123.0698 | 123.0698 | 123.1293 | -123.3902 | -46.3531
4331.7812 | 123.3215 | -68.1244 | 54.8492 | 0.22484 | 0.010156 | 0.0055329 | 0.0015658 | -0.0099633 | -0.0071457 | -0.0015894 | 54.9042 | 54.8904 | -68.5226 | 55.1102 | 54.9042 | 54.895 | 54.7989 | 55.0781 | 54.9271 | 8.4961 | -0.39825 | 0.041199 | 123.0286 | 123.2346 | 0.054932 | 76.6205 | 0.07782 | 123.4268 | 122.9233 | 123.2025 | 123.0286 | 123.0148 | 123.0286 | 123.0515 | 123.0194 | 76.6205 | 123.0148 | 123.0286 | 123.0194 | 123.0286 | 123.0515 | -123.3719 | -46.3531
4332.7812 | 123.3215 | -68.1335 | 54.8492 | -0.011673 | 0.0086602 | 0.0019013 | 0.00049764 | -0.010818 | -0.0080001 | -0.0032984 | 54.8584 | 54.9088 | -68.5318 | 55.1056 | 54.9179 | 54.9042 | 54.7485 | 55.0735 | 54.9042 | 8.4961 | -0.39825 | 0.059509 | 122.9919 | 123.2391 | 0.068665 | 76.6296 | 0.054932 | 123.3902 | 122.8821 | 123.2071 | 123.0515 | 123.0423 | 122.9919 | 123.0377 | 123.0377 | 76.6296 | 123.0423 | 122.9919 | 123.0377 | 123.0515 | 123.0377 | -123.381 | -46.3531
4333.7812 | 123.3398 | -68.1335 | 54.863 | -0.12611 | 0.011651 | -0.00023494 | -0.00014316 | -0.01274 | -0.0094955 | -0.0022302 | 54.9088 | 54.9088 | -68.4998 | 55.1331 | 54.9225 | 54.9133 | 54.7531 | 55.1239 | 54.8859 | 8.4961 | -0.36621 | 0.045776 | 123.0423 | 123.2666 | 0.059509 | 76.6296 | 0.022888 | 123.4085 | 122.8867 | 123.2574 | 123.056 | 123.0423 | 123.0423 | 123.0194 | 123.0469 | 76.6296 | 123.0423 | 123.0423 | 123.0469 | 123.056 | 123.0194 | -123.3627 | -46.3669
4334.7812 | 123.2437 | -68.1839 | 54.8996 | -0.149 | 0.012078 | 0.0080963 | 0.0086154 | -0.0095361 | -0.0067185 | -0.0026574 | 54.8813 | 55.0278 | -68.5501 | 55.0827 | 54.8355 | 54.8126 | 54.9042 | 55.0095 | 54.9637 | 8.4961 | -0.36621 | 0.12817 | 123.0652 | 123.2666 | -0.064087 | 76.68 | 0.064087 | 123.4314 | 123.0881 | 123.1934 | 123.0194 | 123.2117 | 123.0652 | 123.1476 | 122.9965 | 76.68 | 123.2117 | 123.0652 | 122.9965 | 123.0194 | 123.1476 | -123.4497 | -46.4035
4335.7812 | 123.2758 | -68.1747 | 54.8218 | 0.10277 | 0.010796 | 0.00040586 | 0.0024202 | -0.011459 | -0.0041549 | -0.0026574 | 54.8172 | 54.895 | -68.573 | 55.0507 | 54.8584 | 54.8538 | 54.7714 | 55.0461 | 54.9042 | 8.4915 | -0.39825 | 0.073243 | 122.9919 | 123.2254 | 0.036621 | 76.6663 | 0.082398 | 123.3902 | 122.9462 | 123.2208 | 123.0331 | 123.0698 | 122.9919 | 123.0789 | 123.0286 | 76.6663 | 123.0698 | 122.9919 | 123.0286 | 123.0331 | 123.0789 | -123.3948 | -46.3303
4336.7812 | 123.3307 | -68.1747 | 54.8401 | -0.072708 | 0.011651 | 0.0036103 | 0.0022066 | -0.010391 | -0.0060775 | -0.001803 | 54.895 | 54.9088 | -68.5455 | 55.1285 | 54.9316 | 54.9271 | 54.7531 | 55.1239 | 54.9042 | 8.4961 | -0.37079 | 0.068664 | 123.0698 | 123.3032 | 0.091553 | 76.6708 | 0.064087 | 123.4406 | 122.9279 | 123.2986 | 123.1064 | 123.0835 | 123.0698 | 123.0789 | 123.1018 | 76.6708 | 123.0835 | 123.0698 | 123.1018 | 123.1064 | 123.0789 | -123.3856 | -46.344
4337.7812 | 123.2986 | -68.1519 | 54.8355 | -0.17189 | 0.010369 | 0.0040375 | 0.0049838 | -0.012527 | -0.0077865 | -0.001803 | 55.1926 | 54.982 | -68.5043 | 55.0781 | 54.8813 | 54.8904 | 54.7852 | 55.1193 | 54.9088 | 8.4961 | -0.35248 | 0.14648 | 123.3444 | 123.23 | 0.045777 | 76.6479 | 0.073242 | 123.6969 | 122.937 | 123.2712 | 123.0331 | 123.1338 | 123.3444 | 123.0606 | 123.0423 | 76.6479 | 123.1338 | 123.3444 | 123.0423 | 123.0331 | 123.0606 | -123.3398 | -46.3394
4338.7812 | 123.2254 | -68.2159 | 54.8859 | -0.21767 | 0.009942 | 0.0070283 | 0.0056246 | -0.011031 | -0.0075729 | -0.0024438 | 54.8721 | 54.9866 | -68.541 | 55.0598 | 54.8309 | 54.7897 | 54.9774 | 55.0415 | 54.95 | 8.4961 | -0.32501 | 0.10071 | 123.0881 | 123.2758 | -0.054931 | 76.712 | 0.064087 | 123.4131 | 123.1934 | 123.2574 | 123.0469 | 123.2025 | 123.0881 | 123.1659 | 123.0057 | 76.712 | 123.2025 | 123.0881 | 123.0057 | 123.0469 | 123.1659 | -123.4268 | -46.3898
4339.7812 | 123.1522 | -68.1656 | 54.9225 | -0.20241 | 0.011865 | -0.0027985 | 0.0062656 | -0.010177 | -0.0043685 | -0.0020166 | 54.8309 | 55.0003 | -68.5455 | 55.0461 | 54.8172 | 54.776 | 54.9545 | 55.0003 | 54.9637 | 8.4824 | -0.37994 | 0.07782 | 122.9965 | 123.2117 | -0.10529 | 76.6479 | 0.041199 | 123.3765 | 123.1201 | 123.1659 | 122.9828 | 123.1659 | 122.9965 | 123.1293 | 122.9416 | 76.6479 | 123.1659 | 122.9965 | 122.9416 | 122.9828 | 123.1293 | -123.468 | -46.4401
4340.7812 | 123.2208 | -68.1885 | 54.8767 | -0.11848 | 0.014001 | 0.0048921 | 0.008829 | -0.0084681 | -0.0060775 | -0.0022302 | 54.8767 | 55.0232 | -68.5547 | 55.0644 | 54.8264 | 54.8035 | 54.8904 | 54.9957 | 54.9911 | 8.4869 | -0.36621 | 0.14648 | 123.0652 | 123.2529 | -0.050354 | 76.6754 | 0.11444 | 123.4314 | 123.0789 | 123.1842 | 123.0148 | 123.2117 | 123.0652 | 123.1796 | 122.9919 | 76.6754 | 123.2117 | 123.0652 | 122.9919 | 123.0148 | 123.1796 | -123.4314 | -46.3898
4341.7812 | 123.3215 | -68.1702 | 54.7897 | 0.26299 | 0.013146 | 0.0093781 | 0.0066928 | -0.0063317 | -0.0067185 | -0.0047938 | 54.8996 | 54.9179 | -68.5455 | 55.0781 | 54.8492 | 54.8538 | 54.6844 | 55.0049 | 54.8538 | 8.4961 | -0.37537 | 0.12817 | 123.0698 | 123.2483 | 0.059509 | 76.6663 | 0.064087 | 123.4451 | 122.8546 | 123.175 | 123.0194 | 123.0881 | 123.0698 | 123.024 | 123.024 | 76.6663 | 123.0881 | 123.0698 | 123.024 | 123.0194 | 123.024 | -123.3353 | -46.2936
4342.7812 | 123.3261 | -68.1519 | 54.8355 | -0.026932 | 0.011865 | 0.0038239 | -0.0012112 | -0.0097497 | -0.0071457 | -0.0037256 | 54.8676 | 54.9225 | -68.5638 | 55.0964 | 54.8996 | 54.9088 | 54.776 | 55.0781 | 54.9088 | 8.4961 | -0.41199 | 0.086975 | 123.0194 | 123.2483 | 0.064087 | 76.6479 | 0.073242 | 123.4314 | 122.9279 | 123.23 | 123.0515 | 123.0743 | 123.0194 | 123.0606 | 123.0606 | 76.6479 | 123.0743 | 123.0194 | 123.0606 | 123.0515 | 123.0606 | -123.3994 | -46.3394
4343.7812 | 123.2986 | -68.1564 | 54.8035 | 0.23247 | 0.01101 | 0.0061737 | 0.0015658 | -0.010818 | -0.0071457 | -0.001803 | 54.8447 | 54.9225 | -68.5913 | 55.0507 | 54.8492 | 54.8492 | 54.7165 | 54.9957 | 54.8492 | 8.5007 | -0.43488 | 0.11902 | 123.0011 | 123.2071 | 0.045776 | 76.6571 | 0.045776 | 123.436 | 122.8729 | 123.1522 | 123.0057 | 123.0789 | 123.0011 | 123.0057 | 123.0057 | 76.6571 | 123.0789 | 123.0011 | 123.0057 | 123.0057 | 123.0057 | -123.3948 | -46.3028
4344.7812 | 123.2117 | -68.1885 | 54.9042 | -0.15663 | 0.013146 | 0.0033967 | 0.0084018 | -0.010818 | -0.0058639 | -0.0026574 | 54.8492 | 55.014 | -68.5684 | 55.0461 | 54.8126 | 54.7943 | 54.9408 | 54.9728 | 54.95 | 8.4961 | -0.37994 | 0.10986 | 123.0377 | 123.2346 | -0.091553 | 76.6846 | 0.045776 | 123.4177 | 123.1293 | 123.1613 | 123.0011 | 123.2025 | 123.0377 | 123.1384 | 122.9828 | 76.6846 | 123.2025 | 123.0377 | 122.9828 | 123.0011 | 123.1384 | -123.4726 | -46.4081
4345.7812 | 123.2986 | -68.1564 | 54.8538 | -0.26344 | 0.012292 | 0.0055329 | 0.0030612 | -0.011886 | -0.0080001 | -0.003512 | 54.863 | 54.8813 | -68.5455 | 55.1193 | 54.9088 | 54.8996 | 54.7806 | 55.1056 | 54.9179 | 8.5007 | -0.3891 | 0.027466 | 123.0194 | 123.2758 | 0.054931 | 76.6571 | 0.064087 | 123.4085 | 122.937 | 123.262 | 123.0652 | 123.0377 | 123.0194 | 123.0743 | 123.056 | 76.6571 | 123.0377 | 123.0194 | 123.056 | 123.0652 | 123.0743 | -123.3994 | -46.3531
4346.7812 | 123.2666 | -68.1839 | 54.8538 | 0.14854 | 0.010796 | 0.0044647 | 0.0041292 | -0.012313 | -0.0067185 | 0.00033321 | 54.8126 | 54.8767 | -68.5547 | 55.0323 | 54.8447 | 54.8126 | 54.8126 | 55.014 | 54.8721 | 8.4915 | -0.37079 | 0.022888 | 122.9965 | 123.2162 | -0.009155 | 76.6754 | 0.01831 | 123.3673 | 122.9965 | 123.1979 | 123.0286 | 123.0606 | 122.9965 | 123.056 | 122.9965 | 76.6754 | 123.0606 | 122.9965 | 122.9965 | 123.0286 | 123.056 | -123.4085 | -46.3623
4347.7812 | 123.2391 | -68.1656 | 54.8172 | 0.19432 | 0.012505 | 0.0042511 | 0.0022066 | -0.011886 | -0.0052231 | -0.0043664 | 54.8264 | 54.8904 | -68.5593 | 55.0461 | 54.8264 | 54.8355 | 54.7531 | 54.9911 | 54.863 | 8.5007 | -0.39368 | 0.073242 | 122.9919 | 123.2117 | 0.009155 | 76.6663 | 0.045776 | 123.3856 | 122.9187 | 123.1567 | 122.9919 | 123.056 | 122.9919 | 123.0286 | 123.0011 | 76.6663 | 123.056 | 122.9919 | 123.0011 | 122.9919 | 123.0286 | -123.3765 | -46.3165
4348.7812 | 123.3032 | -68.1335 | 54.8218 | -0.034561 | 0.010369 | 0.00083306 | 0.0017794 | -0.013381 | -0.0073593 | -0.00073479 | 54.8584 | 54.9133 | -68.5272 | 55.1056 | 54.9088 | 54.8904 | 54.7668 | 55.0598 | 54.8721 | 8.5007 | -0.39368 | 0.091553 | 122.9919 | 123.2391 | 0.086975 | 76.6342 | 0.050354 | 123.3856 | 122.9004 | 123.1934 | 123.0423 | 123.0469 | 122.9919 | 123.0057 | 123.024 | 76.6342 | 123.0469 | 122.9919 | 123.024 | 123.0423 | 123.0057 | -123.349 | -46.3211
4349.7812 | 123.2849 | -68.1656 | 54.8218 | 0.17906 | 0.0093012 | 0.0029693 | 0.002634 | -0.013168 | -0.0039413 | -0.0047938 | 54.8218 | 54.9088 | -68.5593 | 55.0598 | 54.8676 | 54.8492 | 54.7714 | 55.0323 | 54.8813 | 8.5007 | -0.39368 | 0.086975 | 122.9874 | 123.2254 | 0.045777 | 76.6663 | 0.05951 | 123.381 | 122.937 | 123.1979 | 123.0331 | 123.0743 | 122.9874 | 123.0469 | 123.0148 | 76.6663 | 123.0743 | 122.9874 | 123.0148 | 123.0331 | 123.0469 | -123.381 | -46.3211
4350.7812 | 123.2895 | -68.1747 | 54.8355 | 0.21721 | 0.010796 | 0.00019226 | 0.00028404 | -0.013168 | -0.0045821 | -0.0015894 | 54.8126 | 54.8813 | -68.5593 | 55.0507 | 54.8355 | 54.8447 | 54.7485 | 55.0049 | 54.8721 | 8.4869 | -0.38452 | 0.045777 | 122.9874 | 123.2254 | 0 | 76.6617 | 0.036621 | 123.3719 | 122.9233 | 123.1796 | 123.0103 | 123.056 | 122.9874 | 123.0469 | 123.0194 | 76.6617 | 123.056 | 122.9874 | 123.0194 | 123.0103 | 123.0469 | -123.3948 | -46.3486
4351.7812 | 123.2895 | -68.1747 | 54.8355 | 0.15617 | 0.011224 | 0.0046783 | 0.003702 | -0.012954 | -0.0065047 | -0.0013758 | 54.8401 | 54.8996 | -68.541 | 55.0552 | 54.8492 | 54.8447 | 54.7623 | 54.9911 | 54.8904 | 8.4961 | -0.36621 | 0.064087 | 123.0148 | 123.23 | 0.013733 | 76.6708 | 0.054932 | 123.381 | 122.937 | 123.1659 | 123.024 | 123.0743 | 123.0148 | 123.0652 | 123.0194 | 76.6708 | 123.0743 | 123.0148 | 123.0194 | 123.024 | 123.0652 | -123.3765 | -46.3394
4352.7812 | 123.3032 | -68.1656 | 54.8401 | 0.026474 | 0.012292 | -2.1336e-05 | 0.00049764 | -0.012313 | -0.0060775 | 0.00011961 | 54.8309 | 54.895 | -68.541 | 55.0964 | 54.8813 | 54.8813 | 54.7714 | 55.0552 | 54.8676 | 8.4961 | -0.37537 | 0.054932 | 122.9965 | 123.262 | 0.041199 | 76.6617 | 0.027466 | 123.3719 | 122.937 | 123.2208 | 123.0469 | 123.0606 | 122.9965 | 123.0331 | 123.0469 | 76.6617 | 123.0606 | 122.9965 | 123.0469 | 123.0469 | 123.0331 | -123.381 | -46.344
4353.7812 | 123.2986 | -68.1656 | 54.8401 | 0.034104 | 0.012292 | 0.0038239 | 0.0013522 | -0.012527 | -0.0058639 | -0.0030848 | 54.8264 | 54.9271 | -68.5638 | 55.0781 | 54.8767 | 54.863 | 54.7623 | 55.0461 | 54.8584 | 8.5007 | -0.39826 | 0.086975 | 122.9919 | 123.2437 | 0.036621 | 76.6663 | 0.01831 | 123.3902 | 122.9279 | 123.2117 | 123.0423 | 123.0927 | 122.9919 | 123.024 | 123.0286 | 76.6663 | 123.0927 | 122.9919 | 123.0286 | 123.0423 | 123.024 | -123.4039 | -46.3394
4354.7812 | 123.2666 | -68.1793 | 54.8401 | 0.1104 | 0.012078 | 0.0036103 | 0.0030612 | -0.013168 | -0.0050095 | -0.0022302 | 54.8355 | 54.9088 | -68.5501 | 55.0873 | 54.863 | 54.863 | 54.7714 | 55.0507 | 54.8767 | 8.4961 | -0.37079 | 0.068664 | 123.0148 | 123.2666 | 0.022888 | 76.6754 | 0.036621 | 123.3856 | 122.9507 | 123.23 | 123.0423 | 123.0881 | 123.0148 | 123.056 | 123.0423 | 76.6754 | 123.0881 | 123.0148 | 123.0423 | 123.0423 | 123.056 | -123.3902 | -46.344
4355.7812 | 123.2712 | -68.1976 | 54.8401 | 0.21721 | 0.012719 | 0.0074555 | 0.0041292 | -0.013381 | -0.0052231 | -0.0011622 | 54.8767 | 54.9133 | -68.5501 | 55.0552 | 54.8355 | 54.8355 | 54.7256 | 55.0003 | 54.8676 | 8.4961 | -0.35248 | 0.073242 | 123.0743 | 123.2529 | -0.004578 | 76.6937 | 0.027466 | 123.4268 | 122.9233 | 123.1979 | 123.0331 | 123.111 | 123.0743 | 123.0652 | 123.0331 | 76.6937 | 123.111 | 123.0743 | 123.0331 | 123.0331 | 123.0652 | -123.3902 | -46.344
4356.7812 | 123.2941 | -68.1839 | 54.8355 | -0.057449 | 0.01101 | 0.0031831 | 0.00028404 | -0.01274 | -0.0056503 | -0.0026574 | 54.8584 | 54.9133 | -68.5455 | 55.0919 | 54.8721 | 54.8676 | 54.7623 | 55.0781 | 54.8996 | 8.5007 | -0.36163 | 0.07782 | 123.0423 | 123.2758 | 0.036621 | 76.6846 | 0.064087 | 123.4039 | 122.9462 | 123.262 | 123.056 | 123.0972 | 123.0423 | 123.0835 | 123.0515 | 76.6846 | 123.0972 | 123.0423 | 123.0515 | 123.056 | 123.0835 | -123.381 | -46.3348
4357.7812 | 123.2666 | -68.1839 | 54.8264 | 0.1638 | 0.01101 | 0.0031831 | 0.002634 | -0.011245 | -0.0073593 | -0.00052119 | 54.8309 | 54.8813 | -68.5684 | 55.0552 | 54.8309 | 54.8264 | 54.7531 | 55.0003 | 54.8721 | 8.4915 | -0.38452 | 0.054932 | 123.0148 | 123.2391 | 0.004578 | 76.6754 | 0.045776 | 123.3994 | 122.937 | 123.1842 | 123.0148 | 123.0652 | 123.0148 | 123.056 | 123.0103 | 76.6754 | 123.0652 | 123.0148 | 123.0103 | 123.0148 | 123.056 | -123.3948 | -46.3348
4358.7812 | 123.3032 | -68.1747 | 54.8355 | 0.10277 | 0.010156 | 0.0042511 | 0.00071144 | -0.014022 | -0.0035141 | -0.0024438 | 54.808 | 54.9042 | -68.5638 | 55.0735 | 54.7989 | 54.8355 | 54.7623 | 55.0415 | 54.9042 | 8.5007 | -0.3891 | 0.068665 | 122.9828 | 123.2483 | -0.036621 | 76.6754 | 0.068665 | 123.3719 | 122.937 | 123.2162 | 122.9736 | 123.0789 | 122.9828 | 123.0789 | 123.0103 | 76.6754 | 123.0789 | 122.9828 | 123.0103 | 122.9736 | 123.0789 | -123.3994 | -46.3348
4359.7812 | 123.2712 | -68.1747 | 54.8355 | 0.12566 | 0.009942 | 0.0072419 | 0.0024202 | -0.011245 | -0.0047957 | -0.003512 | 54.8172 | 54.9362 | -68.5455 | 55.0552 | 54.8492 | 54.8218 | 54.7714 | 55.188 | 54.9042 | 8.5007 | -0.37079 | 0.10071 | 122.9919 | 123.23 | 0.013733 | 76.6754 | 0.068665 | 123.3627 | 122.9462 | 123.3627 | 123.024 | 123.111 | 122.9919 | 123.0789 | 122.9965 | 76.6754 | 123.111 | 122.9919 | 122.9965 | 123.024 | 123.0789 | -123.381 | -46.3348
4360.7812 | 123.2803 | -68.1473 | 54.8584 | -0.11085 | 0.010156 | 0.0055329 | 0.001993 | -0.011672 | -0.0071457 | -0.00030759 | 54.895 | 54.9225 | -68.5501 | 55.1376 | 54.9042 | 54.8904 | 54.7943 | 55.0873 | 54.9133 | 8.5007 | -0.40283 | 0.064087 | 123.0423 | 123.2849 | 0.045777 | 76.6479 | 0.054932 | 123.4451 | 122.9416 | 123.2346 | 123.0515 | 123.0698 | 123.0423 | 123.0606 | 123.0377 | 76.6479 | 123.0698 | 123.0423 | 123.0377 | 123.0515 | 123.0606 | -123.4085 | -46.3577
4361.7812 | 123.3444 | -68.1152 | 54.8538 | -0.10323 | 0.01101 | 0.0038239 | 0.0030612 | -0.012527 | -0.0058639 | -0.0041528 | 54.9271 | 54.895 | -68.5181 | 55.1605 | 54.9408 | 54.9316 | 54.7577 | 55.1193 | 54.8904 | 8.5007 | -0.40283 | 0.041199 | 123.0423 | 123.2758 | 0.086975 | 76.6159 | 0.036621 | 123.4451 | 122.8729 | 123.2346 | 123.056 | 123.0103 | 123.0423 | 123.0057 | 123.0469 | 76.6159 | 123.0103 | 123.0423 | 123.0469 | 123.056 | 123.0057 | -123.3719 | -46.3531
4362.7812 | 123.2666 | -68.1702 | 54.8355 | 0.17143 | 0.011651 | 0.0068147 | -0.00014316 | -0.011459 | -0.0037277 | -0.0026574 | 54.8264 | 54.8996 | -68.5638 | 55.0461 | 54.8538 | 54.8447 | 54.7577 | 55.0003 | 54.8813 | 8.4961 | -0.39368 | 0.064087 | 122.9965 | 123.2162 | 0.018311 | 76.6663 | 0.045777 | 123.3902 | 122.9279 | 123.1705 | 123.024 | 123.0698 | 122.9965 | 123.0515 | 123.0148 | 76.6663 | 123.0698 | 122.9965 | 123.0148 | 123.024 | 123.0515 | -123.3994 | -46.3394
4363.7812 | 123.3215 | -68.1793 | 54.7897 | 0.26299 | 0.013146 | 0.0078827 | 0.0064792 | -0.0091089 | -0.0082137 | -0.003512 | 54.8767 | 54.9179 | -68.5638 | 55.0919 | 54.8584 | 54.863 | 54.6799 | 55.0095 | 54.8447 | 8.4961 | -0.38452 | 0.12817 | 123.056 | 123.2712 | 0.068664 | 76.6754 | 0.054932 | 123.4406 | 122.8592 | 123.1888 | 123.0377 | 123.0972 | 123.056 | 123.024 | 123.0423 | 76.6754 | 123.0972 | 123.056 | 123.0423 | 123.0377 | 123.024 | -123.3536 | -46.2936
4364.7812 | 123.3032 | -68.1702 | 54.8401 | 0.056992 | 0.010583 | -0.0027985 | -0.00014316 | -0.01274 | -0.0069321 | -0.0024438 | 54.8172 | 54.9179 | -68.5776 | 55.069 | 54.8813 | 54.8538 | 54.776 | 55.0323 | 54.8904 | 8.5007 | -0.40741 | 0.07782 | 122.9874 | 123.2391 | 0.041199 | 76.6708 | 0.050354 | 123.3948 | 122.9462 | 123.2025 | 123.0515 | 123.0881 | 122.9874 | 123.0606 | 123.024 | 76.6708 | 123.0881 | 122.9874 | 123.024 | 123.0515 | 123.0606 | -123.4177 | -46.3394
4365.7812 | 123.2803 | -68.1747 | 54.8401 | -0.065079 | 0.010156 | 0.0038239 | 0.0011386 | -0.010391 | -0.0077865 | -0.0020166 | 54.8355 | 54.8996 | -68.5455 | 55.069 | 54.863 | 54.8355 | 54.7852 | 55.0186 | 54.8676 | 8.4869 | -0.37079 | 0.059509 | 123.0103 | 123.2437 | 0.022888 | 76.6617 | 0.027466 | 123.381 | 122.9599 | 123.1934 | 123.0377 | 123.0743 | 123.0103 | 123.0423 | 123.0103 | 76.6617 | 123.0743 | 123.0103 | 123.0103 | 123.0377 | 123.0423 | -123.3856 | -46.3531
4366.7812 | 123.3032 | -68.1839 | 54.8126 | 0.19432 | 0.012719 | 0.0046783 | 0.0058382 | -0.011031 | -0.0054367 | -0.0022302 | 54.8767 | 54.9271 | -68.573 | 55.0735 | 54.863 | 54.863 | 54.6844 | 55.0095 | 54.8447 | 8.4961 | -0.3891 | 0.11444 | 123.0606 | 123.2574 | 0.050354 | 76.68 | 0.032044 | 123.4497 | 122.8683 | 123.1934 | 123.0469 | 123.111 | 123.0606 | 123.0286 | 123.0469 | 76.68 | 123.111 | 123.0606 | 123.0469 | 123.0469 | 123.0286 | -123.3856 | -46.3165
4367.7812 | 123.317 | -68.1747 | 54.8126 | 0.25536 | 0.01336 | 0.0063873 | 0.0081882 | -0.0095361 | -0.0047957 | -0.0011622 | 54.8996 | 54.9225 | -68.5547 | 55.0964 | 54.8538 | 54.8721 | 54.6707 | 55.0049 | 54.863 | 8.4915 | -0.37994 | 0.10986 | 123.0743 | 123.2712 | 0.041199 | 76.6663 | 0.050354 | 123.4543 | 122.8455 | 123.1796 | 123.0286 | 123.0972 | 123.0743 | 123.0377 | 123.0469 | 76.6663 | 123.0972 | 123.0743 | 123.0469 | 123.0286 | 123.0377 | -123.3673 | -46.3211
4368.7812 | 123.3261 | -68.1427 | 54.8126 | 0.049362 | 0.011865 | 0.00040586 | 0.0015658 | -0.010604 | -0.0047957 | -0.001803 | 54.8492 | 54.9179 | -68.5455 | 55.1147 | 54.9133 | 54.8904 | 54.7668 | 55.0735 | 54.895 | 8.4915 | -0.40283 | 0.10529 | 122.9919 | 123.2574 | 0.10071 | 76.6342 | 0.082398 | 123.3948 | 122.9095 | 123.2162 | 123.056 | 123.0606 | 122.9919 | 123.0377 | 123.0331 | 76.6342 | 123.0606 | 122.9919 | 123.0331 | 123.056 | 123.0377 | -123.3582 | -46.3211
4369.7812 | 123.2941 | -68.1564 | 54.8584 | 0.63683 | 0.012292 | 0.0055329 | 0.0017794 | -0.011245 | -0.0043685 | -0.0013758 | 54.8172 | 54.9133 | -68.5501 | 55.0552 | 54.863 | 54.8401 | 54.7897 | 55.0095 | 54.8996 | 8.4961 | -0.39368 | 0.054932 | 122.9736 | 123.2117 | 0.004578 | 76.6525 | 0.041199 | 123.3673 | 122.9462 | 123.1659 | 123.0194 | 123.0698 | 122.9736 | 123.056 | 122.9965 | 76.6525 | 123.0698 | 122.9736 | 122.9965 | 123.0194 | 123.056 | -123.4085 | -46.3623
4370.7812 | 123.2346 | -68.1793 | 54.9042 | 0.1638 | 0.012933 | 0.0012605 | 0.0092562 | -0.010818 | -0.0071457 | -0.0043664 | 54.8401 | 55.0049 | -68.5455 | 55.0598 | 54.8218 | 54.7852 | 54.9362 | 54.9866 | 54.9133 | 8.5007 | -0.36621 | 0.10071 | 123.0194 | 123.2391 | -0.082398 | 76.68 | 0.009155 | 123.3856 | 123.1155 | 123.1659 | 123.0011 | 123.1842 | 123.0194 | 123.0927 | 122.9645 | 76.68 | 123.1842 | 123.0194 | 122.9645 | 123.0011 | 123.0927 | -123.4497 | -46.4035
4371.7812 | 123.317 | -68.1793 | 54.7989 | 0.33928 | 0.013574 | 0.0029693 | 0.004343 | -0.010391 | -0.0065047 | -0.0030848 | 54.8859 | 54.9408 | -68.5638 | 55.0781 | 54.8767 | 54.8676 | 54.689 | 55.0049 | 54.8767 | 8.5007 | -0.38452 | 0.14191 | 123.0652 | 123.2574 | 0.07782 | 76.68 | 0.07782 | 123.4497 | 122.8683 | 123.1842 | 123.056 | 123.1201 | 123.0652 | 123.056 | 123.0469 | 76.68 | 123.1201 | 123.0652 | 123.0469 | 123.056 | 123.056 | -123.3627 | -46.2982
4372.7812 | 123.2712 | -68.1793 | 54.8401 | 0.17143 | 0.010156 | 0.0046783 | 0.00049764 | -0.011886 | -0.0033005 | -0.0020166 | 54.8126 | 54.9088 | -68.573 | 55.0369 | 54.8447 | 54.8492 | 54.776 | 54.9911 | 54.8767 | 8.4915 | -0.39368 | 0.068664 | 122.9919 | 123.2162 | 0.004578 | 76.6708 | 0.036621 | 123.3856 | 122.9553 | 123.1705 | 123.024 | 123.0881 | 122.9919 | 123.056 | 123.0286 | 76.6708 | 123.0881 | 122.9919 | 123.0286 | 123.024 | 123.056 | -123.4131 | -46.3486
4373.7812 | 123.3032 | -68.1885 | 54.808 | 0.26299 | 0.014642 | 0.0044647 | 0.0092562 | -0.010818 | -0.0041549 | -0.0024438 | 54.8538 | 54.9774 | -68.5776 | 55.0735 | 54.8309 | 54.8401 | 54.7211 | 54.9774 | 54.8584 | 8.4915 | -0.3891 | 0.16937 | 123.0423 | 123.262 | 0.022889 | 76.68 | 0.050354 | 123.4314 | 122.9095 | 123.1659 | 123.0194 | 123.1659 | 123.0423 | 123.0469 | 123.0286 | 76.68 | 123.1659 | 123.0423 | 123.0286 | 123.0194 | 123.0469 | -123.3856 | -46.3165
4374.7812 | 123.2986 | -68.1839 | 54.8172 | 0.20958 | 0.0097284 | 0.0063873 | 0.003702 | -0.010604 | -0.0082137 | -0.0015894 | 54.8309 | 54.895 | -68.573 | 55.0552 | 54.8355 | 54.8355 | 54.7531 | 54.9957 | 54.8767 | 8.4961 | -0.3891 | 0.07782 | 123.0148 | 123.2391 | 0.01831 | 76.68 | 0.059509 | 123.4039 | 122.937 | 123.1796 | 123.0194 | 123.0789 | 123.0148 | 123.0606 | 123.0194 | 76.68 | 123.0789 | 123.0148 | 123.0194 | 123.0194 | 123.0606 | -123.3902 | -46.3211
4375.7812 | 123.2895 | -68.1885 | 54.8264 | 0.034104 | 0.01101 | 0.0068147 | 0.0011386 | -0.011459 | -0.0071457 | -0.0020166 | 54.8126 | 54.9271 | -68.5501 | 55.069 | 54.8859 | 54.8584 | 54.7897 | 55.0323 | 54.8767 | 8.5007 | -0.36163 | 0.10071 | 123.0011 | 123.2574 | 0.059509 | 76.6891 | 0.050354 | 123.3627 | 122.9782 | 123.2208 | 123.0743 | 123.1155 | 123.0011 | 123.0652 | 123.0469 | 76.6891 | 123.1155 | 123.0011 | 123.0469 | 123.0743 | 123.0652 | -123.3765 | -46.3257
4376.7812 | 123.3078 | -68.1839 | 54.8172 | 0.26299 | 0.014428 | 0.0055329 | 0.010111 | -0.0091089 | -0.0060775 | -0.0032984 | 54.8584 | 54.9454 | -68.573 | 55.0964 | 54.8584 | 54.863 | 54.7073 | 55.0232 | 54.8584 | 8.5052 | -0.3891 | 0.12817 | 123.0423 | 123.2803 | 0.041198 | 76.6891 | 0.041198 | 123.4314 | 122.8912 | 123.2071 | 123.0423 | 123.1293 | 123.0423 | 123.0423 | 123.0469 | 76.6891 | 123.1293 | 123.0423 | 123.0469 | 123.0423 | 123.0423 | -123.3902 | -46.312
4377.7812 | 123.2117 | -68.2205 | 54.8492 | 0.17906 | 0.014214 | 0.010019 | 0.0092562 | -0.0095361 | -0.0047957 | -0.0030848 | 54.8309 | 55.0095 | -68.5776 | 55.014 | 54.776 | 54.7714 | 54.8309 | 54.9042 | 54.8996 | 8.4869 | -0.35706 | 0.16022 | 123.0515 | 123.2346 | -0.073242 | 76.7075 | 0.050354 | 123.4085 | 123.0515 | 123.1247 | 122.9965 | 123.23 | 123.0515 | 123.1201 | 122.9919 | 76.7075 | 123.23 | 123.0515 | 122.9919 | 122.9965 | 123.1201 | -123.4268 | -46.3623
4378.7812 | 123.2986 | -68.1885 | 54.808 | 0.24773 | 0.012505 | 0.0036103 | 0.003702 | -0.0099633 | -0.0077865 | -0.0024438 | 54.8721 | 54.8859 | -68.573 | 55.0781 | 54.8676 | 54.8538 | 54.7073 | 55.0186 | 54.863 | 8.4961 | -0.38452 | 0.07782 | 123.0606 | 123.2666 | 0.05951 | 76.6846 | 0.054932 | 123.4451 | 122.8958 | 123.2071 | 123.056 | 123.0743 | 123.0606 | 123.0515 | 123.0423 | 76.6846 | 123.0743 | 123.0606 | 123.0423 | 123.056 | 123.0515 | -123.381 | -46.312
4379.7812 | 123.2574 | -68.1747 | 54.808 | 0.17906 | 0.013574 | 0.0023285 | 0.0015658 | -0.0080407 | -0.0045821 | -0.0011622 | 54.8447 | 54.9179 | -68.5776 | 55.0323 | 54.8538 | 54.8355 | 54.7714 | 54.9911 | 54.8721 | 8.4961 | -0.40283 | 0.10986 | 123.0194 | 123.2071 | 0.045777 | 76.6708 | 0.064087 | 123.4222 | 122.9462 | 123.1659 | 123.0286 | 123.0927 | 123.0194 | 123.0469 | 123.0103 | 76.6708 | 123.0927 | 123.0194 | 123.0103 | 123.0286 | 123.0469 | -123.3856 | -46.312
4380.7812 | 123.2712 | -68.1702 | 54.8538 | -0.16426 | 0.011437 | 0.0063873 | 0.0041292 | -0.012313 | -0.0056503 | -0.00458 | 54.9088 | 54.9728 | -68.5135 | 55.1193 | 54.9088 | 54.8813 | 54.8447 | 55.0781 | 54.895 | 8.5052 | -0.34332 | 0.11902 | 123.0789 | 123.2895 | 0.054931 | 76.6754 | 0.041199 | 123.4222 | 123.0148 | 123.2483 | 123.0789 | 123.143 | 123.0789 | 123.0652 | 123.0515 | 76.6754 | 123.143 | 123.0789 | 123.0515 | 123.0789 | 123.0652 | -123.3673 | -46.3486
4381.7812 | 123.2574 | -68.2205 | 54.8264 | 0.27824 | 0.016351 | 0.0046783 | 0.010324 | -0.0071863 | -0.0077865 | -0.0037256 | 54.8309 | 54.9957 | -68.5822 | 55.0278 | 54.7943 | 54.7989 | 54.7943 | 54.9362 | 54.8721 | 8.4961 | -0.36163 | 0.16937 | 123.0515 | 123.2483 | -0.032043 | 76.7166 | 0.045776 | 123.4131 | 123.0148 | 123.1567 | 123.0148 | 123.2162 | 123.0515 | 123.0927 | 123.0194 | 76.7166 | 123.2162 | 123.0515 | 123.0194 | 123.0148 | 123.0927 | -123.4085 | -46.3303
4382.7812 | 123.2483 | -68.2297 | 54.8126 | 0.20195 | 0.013146 | 0.010019 | 0.0090426 | -0.0076135 | -0.0071457 | -0.0028712 | 54.8401 | 55.0003 | -68.573 | 55.014 | 54.7897 | 54.776 | 54.8035 | 54.9316 | 54.9316 | 8.4869 | -0.34332 | 0.18768 | 123.0698 | 123.2437 | -0.022888 | 76.7166 | 0.11902 | 123.4131 | 123.0331 | 123.1613 | 123.0194 | 123.23 | 123.0698 | 123.1613 | 123.0057 | 76.7166 | 123.23 | 123.0698 | 123.0057 | 123.0194 | 123.1613 | -123.3856 | -46.3257
4383.7812 | 123.23 | -68.2068 | 54.8355 | 0.23247 | 0.015283 | 0.012369 | 0.0096834 | -0.0071863 | -0.0073593 | -0.0026574 | 54.8172 | 55.0232 | -68.5867 | 55.0003 | 54.7852 | 54.7852 | 54.8218 | 54.9225 | 54.9133 | 8.4915 | -0.37994 | 0.18768 | 123.024 | 123.2071 | -0.050354 | 76.6983 | 0.07782 | 123.4039 | 123.0286 | 123.1293 | 122.9919 | 123.23 | 123.024 | 123.1201 | 122.9919 | 76.6983 | 123.23 | 123.024 | 122.9919 | 122.9919 | 123.1201 | -123.4222 | -46.344
4384.7812 | 123.3261 | -68.1793 | 54.8218 | 0.011215 | 0.0084466 | 0.0023285 | -0.00014316 | -0.0097497 | -0.0097091 | -0.0022302 | 54.8264 | 54.895 | -68.5638 | 55.0873 | 54.9042 | 54.8904 | 54.7806 | 55.0598 | 54.9271 | 8.5052 | -0.38452 | 0.073243 | 123.0057 | 123.2666 | 0.082398 | 76.6846 | 0.10529 | 123.3902 | 122.9599 | 123.2391 | 123.0835 | 123.0743 | 123.0057 | 123.1064 | 123.0698 | 76.6846 | 123.0743 | 123.0057 | 123.0698 | 123.0835 | 123.1064 | -123.3856 | -46.3165
4385.7812 | 123.2712 | -68.2022 | 54.8309 | 0.28587 | 0.012933 | 0.0068147 | 0.008829 | -0.0076135 | -0.0060775 | -0.0015894 | 54.8447 | 54.9728 | -68.5684 | 55.0369 | 54.8264 | 54.8264 | 54.7485 | 54.9774 | 54.8859 | 8.4915 | -0.36621 | 0.14191 | 123.0469 | 123.2391 | -0.004578 | 76.6937 | 0.054931 | 123.4131 | 122.9507 | 123.1796 | 123.0286 | 123.175 | 123.0469 | 123.0881 | 123.0286 | 76.6937 | 123.175 | 123.0469 | 123.0286 | 123.0286 | 123.0881 | -123.3994 | -46.3394
4386.7812 | 123.3215 | -68.1656 | 54.8264 | 0.049362 | 0.0090876 | 0.0053193 | 0.00049764 | -0.013168 | -0.0045821 | -0.0015894 | 54.8355 | 54.9133 | -68.5638 | 55.0598 | 54.8767 | 54.8767 | 54.7852 | 55.0461 | 54.8721 | 8.5007 | -0.39826 | 0.086975 | 123.0011 | 123.2254 | 0.050354 | 76.6663 | 0.045776 | 123.3994 | 122.9507 | 123.2117 | 123.0423 | 123.0789 | 123.0011 | 123.0377 | 123.0423 | 76.6663 | 123.0789 | 123.0011 | 123.0423 | 123.0423 | 123.0377 | -123.3902 | -46.3257
4387.7812 | 123.2574 | -68.2022 | 54.8401 | 0.26299 | 0.01336 | -2.1336e-05 | 0.0090426 | -0.0099633 | -0.0067185 | -0.0047938 | 54.8309 | 54.982 | -68.5822 | 55.0278 | 54.7897 | 54.8126 | 54.7852 | 54.9683 | 54.8767 | 8.4869 | -0.37994 | 0.14191 | 123.0331 | 123.23 | -0.050354 | 76.6891 | 0.036621 | 123.4131 | 122.9874 | 123.1705 | 122.9919 | 123.1842 | 123.0331 | 123.0789 | 123.0148 | 76.6891 | 123.1842 | 123.0331 | 123.0148 | 122.9919 | 123.0789 | -123.4222 | -46.3531
4388.7812 | 123.3124 | -68.1839 | 54.8126 | 0.14092 | 0.01101 | 0.0016877 | 0.0039156 | -0.0093225 | -0.0075729 | -0.001803 | 54.8904 | 54.9088 | -68.5638 | 55.069 | 54.8813 | 54.8767 | 54.7073 | 55.0186 | 54.8767 | 8.5007 | -0.37994 | 0.09613 | 123.0743 | 123.2529 | 0.068665 | 76.6846 | 0.064087 | 123.4543 | 122.8912 | 123.2025 | 123.0652 | 123.0927 | 123.0743 | 123.0606 | 123.0606 | 76.6846 | 123.0927 | 123.0743 | 123.0606 | 123.0652 | 123.0606 | -123.3765 | -46.312
4389.7812 | 123.2941 | -68.1747 | 54.8126 | 0.041733 | 0.0093012 | 0.0021149 | 0.0011386 | -0.012313 | -0.0062911 | -0.0020166 | 54.8126 | 54.9316 | -68.5776 | 55.0415 | 54.863 | 54.8538 | 54.7897 | 55.0232 | 54.8676 | 8.5052 | -0.40283 | 0.11902 | 122.9874 | 123.2162 | 0.050354 | 76.68 | 0.054932 | 123.3902 | 122.9645 | 123.1979 | 123.0377 | 123.1064 | 122.9874 | 123.0423 | 123.0286 | 76.68 | 123.1064 | 122.9874 | 123.0286 | 123.0377 | 123.0423 | -123.3902 | -46.3074
4390.7812 | 123.3261 | -68.1885 | 54.808 | 0.30113 | 0.013146 | 0.0040375 | 0.0090426 | -0.0080407 | -0.0069321 | -0.0030848 | 54.8767 | 54.95 | -68.5776 | 55.0507 | 54.8767 | 54.8813 | 54.6936 | 55.014 | 54.8584 | 8.4915 | -0.3891 | 0.14191 | 123.0652 | 123.2391 | 0.068665 | 76.68 | 0.050354 | 123.4543 | 122.8821 | 123.2025 | 123.0652 | 123.1384 | 123.0652 | 123.0469 | 123.0698 | 76.68 | 123.1384 | 123.0652 | 123.0698 | 123.0652 | 123.0469 | -123.3856 | -46.3165
4391.7812 | 123.2071 | -68.2205 | 54.8584 | 0.18669 | 0.01571 | 0.0055329 | 0.0090426 | -0.0061181 | -0.0082137 | -0.0050074 | 54.808 | 55.014 | -68.5867 | 55.1102 | 54.8172 | 54.7852 | 54.863 | 54.9637 | 54.95 | 8.4915 | -0.36621 | 0.15564 | 123.0286 | 123.3307 | -0.041198 | 76.712 | 0.091553 | 123.3948 | 123.0835 | 123.1842 | 123.0377 | 123.2346 | 123.0286 | 123.1705 | 123.0057 | 76.712 | 123.2346 | 123.0286 | 123.0057 | 123.0377 | 123.1705 | -123.4451 | -46.3669
4392.7812 | 123.3032 | -68.1793 | 54.8218 | 0.26299 | 0.010583 | 0.0074555 | 0.003702 | -0.0095361 | -0.0050095 | -0.0022302 | 54.9545 | 54.9225 | -68.6005 | 55.0735 | 54.9088 | 54.9133 | 54.6936 | 55.0644 | 54.8904 | 8.4961 | -0.42114 | 0.10071 | 123.1338 | 123.2529 | 0.086975 | 76.6754 | 0.068665 | 123.555 | 122.8729 | 123.2437 | 123.0881 | 123.1018 | 123.1338 | 123.0698 | 123.0927 | 76.6754 | 123.1018 | 123.1338 | 123.0927 | 123.0881 | 123.0698 | -123.4222 | -46.3257
4393.7812 | 123.3215 | -68.1702 | 54.808 | 0.2401 | 0.013574 | 0.0072419 | 0.0066928 | -0.0067591 | -0.0084273 | -0.0013758 | 54.8813 | 54.9454 | -68.5684 | 54.9133 | 54.8218 | 54.9362 | 54.7714 | 55.0415 | 54.8859 | 8.5007 | -0.39825 | 0.13733 | 123.0515 | 123.0835 | 0.013733 | 76.6708 | 0.07782 | 123.4497 | 122.9416 | 123.2117 | 122.9919 | 123.1155 | 123.0515 | 123.056 | 123.1064 | 76.6708 | 123.1155 | 123.0515 | 123.1064 | 122.9919 | 123.056 | -123.3765 | -46.3074
4394.7812 | 123.2941 | -68.1793 | 54.808 | 0.087509 | 0.010796 | 0.0027557 | -0.0012112 | -0.010177 | -0.0062911 | -0.00052119 | 54.7989 | 54.9088 | -68.5638 | 55.0415 | 54.8218 | 54.808 | 54.8126 | 55.0003 | 54.8996 | 8.4961 | -0.38452 | 0.10071 | 122.9782 | 123.2208 | 0.013733 | 76.6754 | 0.091553 | 123.3627 | 122.9919 | 123.1796 | 123.0011 | 123.0881 | 122.9782 | 123.0789 | 122.9874 | 76.6754 | 123.0881 | 122.9782 | 122.9874 | 123.0011 | 123.0789 | -123.3719 | -46.312
4395.7812 | 123.2574 | -68.2159 | 54.7943 | 0.26299 | 0.016351 | 0.0061737 | 0.008829 | -0.010177 | -0.0058639 | -0.00052119 | 54.8447 | 55.0095 | -68.5822 | 55.0095 | 54.8218 | 54.7806 | 54.7668 | 54.95 | 54.8721 | 8.4869 | -0.36621 | 0.21515 | 123.0606 | 123.2254 | 0.027465 | 76.7029 | 0.077819 | 123.4268 | 122.9828 | 123.1659 | 123.0377 | 123.2254 | 123.0606 | 123.0881 | 122.9965 | 76.7029 | 123.2254 | 123.0606 | 122.9965 | 123.0377 | 123.0881 | -123.3765 | -46.3074
4396.7812 | 123.3124 | -68.1885 | 54.8172 | 0.3698 | 0.012505 | 0.0098053 | 0.00712 | -0.0080407 | -0.0052231 | -0.0011622 | 54.895 | 54.9316 | -68.5638 | 55.0735 | 54.863 | 54.863 | 54.689 | 55.0323 | 54.8309 | 8.4915 | -0.37537 | 0.11444 | 123.0835 | 123.262 | 0.045776 | 76.68 | 0.013733 | 123.4589 | 122.8775 | 123.2208 | 123.0515 | 123.1201 | 123.0835 | 123.0194 | 123.0515 | 76.68 | 123.1201 | 123.0835 | 123.0515 | 123.0515 | 123.0194 | -123.381 | -46.3257
4397.7812 | 123.317 | -68.1747 | 54.7943 | 0.34691 | 0.012292 | 0.0055329 | 0.00712 | -0.0093225 | -0.0054367 | -0.00094839 | 54.9042 | 54.9362 | -68.5684 | 55.0781 | 54.8538 | 54.8859 | 54.7165 | 55.0232 | 54.8767 | 8.4915 | -0.39368 | 0.14191 | 123.0789 | 123.2529 | 0.059509 | 76.6663 | 0.082397 | 123.4726 | 122.8912 | 123.1979 | 123.0286 | 123.111 | 123.0789 | 123.0515 | 123.0606 | 76.6663 | 123.111 | 123.0789 | 123.0606 | 123.0286 | 123.0515 | -123.3627 | -46.3028
4398.7812 | 123.1888 | -68.2297 | 54.8676 | 0.18669 | 0.01336 | 0.0068147 | 0.010324 | -0.0073999 | -0.0060775 | 0.0018286 | 54.8035 | 55.0095 | -68.5822 | 54.7256 | 54.5151 | 54.8813 | 54.9545 | 54.9728 | 54.9042 | 8.4961 | -0.35248 | 0.14191 | 123.0331 | 122.9553 | -0.35248 | 76.7258 | 0.036621 | 123.3856 | 123.1842 | 123.2025 | 122.7448 | 123.2391 | 123.0331 | 123.1338 | 123.111 | 76.7258 | 123.2391 | 123.0331 | 123.111 | 122.7448 | 123.1338 | -123.4497 | -46.3715
4399.7812 | 123.3353 | -68.2114 | 54.8035 | 0.25536 | 0.012933 | 0.0048921 | 0.0062656 | -0.0069727 | -0.0060775 | -0.00458 | 54.8813 | 54.9225 | -68.5913 | 54.9042 | 54.9088 | 54.9545 | 54.7531 | 55.0507 | 54.8904 | 8.4961 | -0.37994 | 0.11902 | 123.0927 | 123.1155 | 0.10529 | 76.7075 | 0.086975 | 123.4726 | 122.9645 | 123.262 | 123.1201 | 123.1338 | 123.0927 | 123.1018 | 123.1659 | 76.7075 | 123.1338 | 123.0927 | 123.1659 | 123.1201 | 123.1018 | -123.3948 | -46.3074
4400.7812 | 123.317 | -68.1519 | 54.8035 | -0.04982 | 0.0086602 | 0.0033967 | 0.00092504 | -0.011672 | -0.0047957 | -0.0022302 | 54.8721 | 54.9179 | -68.541 | 55.1239 | 54.9545 | 54.9271 | 54.7668 | 55.1147 | 54.9042 | 8.5007 | -0.3891 | 0.11444 | 123.024 | 123.2758 | 0.15106 | 76.6525 | 0.10071 | 123.4131 | 122.9187 | 123.2666 | 123.1064 | 123.0698 | 123.024 | 123.056 | 123.0789 | 76.6525 | 123.0698 | 123.024 | 123.0789 | 123.1064 | 123.056 | -123.3444 | -46.3028
4401.7812 | 123.3078 | -68.1702 | 54.7943 | 0.17143 | 0.0093012 | 0.0046783 | 0.0049838 | -0.010818 | -0.0065047 | -0.001803 | 54.8676 | 54.9133 | -68.5776 | 55.0644 | 54.8767 | 54.8721 | 54.6982 | 55.0323 | 54.8401 | 8.4915 | -0.40741 | 0.11902 | 123.0377 | 123.2346 | 0.082397 | 76.6617 | 0.045776 | 123.4451 | 122.8683 | 123.2025 | 123.0469 | 123.0835 | 123.0377 | 123.0103 | 123.0423 | 76.6617 | 123.0835 | 123.0377 | 123.0423 | 123.0469 | 123.0103 | -123.3719 | -46.3028
4402.7812 | 123.2895 | -68.1976 | 54.7714 | 0.2401 | 0.011651 | 0.0031831 | 0.0051974 | -0.011245 | -0.0041549 | -0.0020166 | 54.8676 | 54.9179 | -68.573 | 55.0507 | 54.8309 | 54.8492 | 54.744 | 55.014 | 54.863 | 8.5007 | -0.37537 | 0.14648 | 123.0652 | 123.2483 | 0.05951 | 76.6983 | 0.091553 | 123.4406 | 122.9416 | 123.2117 | 123.0286 | 123.1155 | 123.0652 | 123.0606 | 123.0469 | 76.6983 | 123.1155 | 123.0652 | 123.0469 | 123.0286 | 123.0606 | -123.3444 | -46.2708
4403.7812 | 123.1934 | -68.2343 | 54.8584 | 0.17143 | 0.015283 | 0.0068147 | 0.0098972 | -0.0073999 | -0.0043685 | -0.0030848 | 54.8264 | 55.0278 | -68.5638 | 55.0095 | 54.7531 | 54.8904 | 54.4144 | 54.776 | 54.8721 | 8.4915 | -0.32959 | 0.16937 | 123.0606 | 123.2437 | -0.10529 | 76.7258 | 0.013733 | 123.3902 | 122.6486 | 123.0103 | 122.9874 | 123.262 | 123.0606 | 123.1064 | 123.1247 | 76.7258 | 123.262 | 123.0606 | 123.1247 | 122.9874 | 123.1064 | -123.4222 | -46.3669
4404.7812 | 123.2712 | -68.1976 | 54.808 | 0.1638 | 0.012719 | 0.0051057 | 0.0022066 | -0.0095361 | -0.0060775 | -0.0022302 | 54.8264 | 54.9088 | -68.573 | 55.0415 | 54.8264 | 54.8355 | 54.7531 | 55.0049 | 54.8813 | 8.4961 | -0.37537 | 0.10071 | 123.024 | 123.2391 | 0.018311 | 76.6937 | 0.073243 | 123.3994 | 122.9507 | 123.2025 | 123.024 | 123.1064 | 123.024 | 123.0789 | 123.0331 | 76.6937 | 123.1064 | 123.024 | 123.0331 | 123.024 | 123.0789 | -123.381 | -46.312
4405.7812 | 123.262 | -68.2205 | 54.808 | 0.27061 | 0.012933 | 0.0033967 | 0.0094698 | -0.0078271 | -0.0086411 | -0.0026574 | 54.8309 | 54.9591 | -68.6142 | 55.0232 | 54.8035 | 54.7989 | 54.7668 | 54.9683 | 54.8996 | 8.4961 | -0.39368 | 0.15106 | 123.0515 | 123.2437 | -0.004577 | 76.7166 | 0.091553 | 123.4451 | 122.9874 | 123.1888 | 123.024 | 123.1796 | 123.0515 | 123.1201 | 123.0194 | 76.7166 | 123.1796 | 123.0515 | 123.0194 | 123.024 | 123.1201 | -123.4222 | -46.312
4406.7812 | 123.3398 | -68.1885 | 54.808 | 0.20195 | 0.010369 | 0.0089509 | 0.0049838 | -0.0091089 | -0.0062911 | -0.00073479 | 54.9225 | 54.9225 | -68.5547 | 55.0735 | 54.8813 | 54.863 | 54.6982 | 55.0278 | 54.8813 | 8.4915 | -0.36621 | 0.11444 | 123.111 | 123.262 | 0.073243 | 76.68 | 0.073243 | 123.4772 | 122.8867 | 123.2162 | 123.0698 | 123.111 | 123.111 | 123.0698 | 123.0515 | 76.68 | 123.111 | 123.111 | 123.0515 | 123.0698 | 123.0698 | -123.3627 | -46.3165
4407.7812 | 123.317 | -68.1793 | 54.8035 | 0.2401 | 0.012505 | 0.0031831 | 0.0069064 | -0.0091089 | -0.0069321 | -0.0015894 | 54.8538 | 54.9683 | -68.573 | 55.0735 | 54.863 | 54.863 | 54.6616 | 54.9683 | 54.8721 | 8.5007 | -0.39368 | 0.1648 | 123.0331 | 123.2529 | 0.059509 | 76.68 | 0.068664 | 123.4268 | 122.8409 | 123.1476 | 123.0423 | 123.1476 | 123.0331 | 123.0515 | 123.0423 | 76.68 | 123.1476 | 123.0331 | 123.0423 | 123.0423 | 123.0515 | -123.3765 | -46.3028
4408.7812 | 123.3032 | -68.2159 | 54.808 | 0.24773 | 0.013574 | 0.0055329 | 0.0086154 | -0.0063317 | -0.0075729 | -0.00052119 | 54.8355 | 55.0003 | -68.5638 | 55.0278 | 54.8264 | 54.8126 | 54.7714 | 54.9637 | 54.9088 | 8.5007 | -0.3479 | 0.19226 | 123.0515 | 123.2437 | 0.018311 | 76.7166 | 0.10071 | 123.3994 | 122.9874 | 123.1796 | 123.0423 | 123.2162 | 123.0515 | 123.1247 | 123.0286 | 76.7166 | 123.2162 | 123.0515 | 123.0286 | 123.0423 | 123.1247 | -123.3719 | -46.3074
4409.7812 | 123.3582 | -68.1839 | 54.8492 | 0.15617 | 0.01101 | 0.0036103 | -0.0018522 | -0.0084681 | -0.0065047 | -0.0028712 | 54.8264 | 54.9133 | -68.573 | 55.0323 | 54.8538 | 54.8538 | 54.808 | 55.0049 | 54.895 | 8.4961 | -0.3891 | 0.064087 | 123.0103 | 123.2162 | 0.004578 | 76.68 | 0.045777 | 123.3994 | 122.9919 | 123.1888 | 123.0377 | 123.0972 | 123.0103 | 123.0789 | 123.0377 | 76.68 | 123.0972 | 123.0103 | 123.0377 | 123.0377 | 123.0789 | -123.4222 | -46.3531
4410.7812 | 123.3261 | -68.2022 | 54.8218 | 0.78941 | 0.0093012 | 0.0051057 | 0.005411 | -0.0097497 | -0.0069321 | -0.0015894 | 54.9545 | 54.9225 | -68.5501 | 55.0964 | 54.8584 | 54.8813 | 54.6753 | 55.0232 | 54.8584 | 8.4869 | -0.3479 | 0.10071 | 123.1567 | 123.2986 | 0.036621 | 76.6891 | 0.036621 | 123.5046 | 122.8775 | 123.2254 | 123.0606 | 123.1247 | 123.1567 | 123.0606 | 123.0835 | 76.6891 | 123.1247 | 123.1567 | 123.0835 | 123.0606 | 123.0606 | -123.3719 | -46.3348
4411.7812 | 123.2208 | -68.2114 | 54.8721 | 0.1104 | 0.015496 | 0.0025421 | 0.011179 | -0.0069727 | -0.0077865 | -0.0043664 | 54.8584 | 55.014 | -68.5638 | 55.014 | 54.7806 | 54.7714 | 54.8859 | 54.9316 | 54.9271 | 8.4915 | -0.35248 | 0.14191 | 123.0698 | 123.2254 | -0.091552 | 76.7029 | 0.054932 | 123.4222 | 123.0972 | 123.143 | 122.9919 | 123.2254 | 123.0698 | 123.1384 | 122.9828 | 76.7029 | 123.2254 | 123.0698 | 122.9828 | 122.9919 | 123.1384 | -123.436 | -46.3806
4412.7812 | 123.1934 | -68.2663 | 54.8767 | 0.23247 | 0.015283 | 0.0091645 | 0.010324 | -0.0048365 | -0.0067185 | -0.0011622 | 54.8264 | 55.014 | -68.573 | 54.982 | 54.7668 | 54.7485 | 54.9042 | 54.8859 | 54.9408 | 8.4915 | -0.3067 | 0.13733 | 123.0927 | 123.2483 | -0.10986 | 76.7578 | 0.064087 | 123.3994 | 123.1705 | 123.1522 | 123.0331 | 123.2803 | 123.0927 | 123.2071 | 123.0148 | 76.7578 | 123.2803 | 123.0927 | 123.0148 | 123.0331 | 123.2071 | -123.4497 | -46.3852
4413.7812 | 123.2437 | -68.2343 | 54.8309 | 0.23247 | 0.014428 | 0.0072419 | 0.0090426 | -0.0061181 | -0.0056503 | -0.001803 | 54.8264 | 55.0095 | -68.6005 | 55.014 | 54.7852 | 54.8035 | 54.7989 | 54.9408 | 54.9591 | 8.4961 | -0.36621 | 0.17853 | 123.0606 | 123.2483 | -0.045777 | 76.7303 | 0.12817 | 123.4268 | 123.0331 | 123.175 | 123.0194 | 123.2437 | 123.0606 | 123.1934 | 123.0377 | 76.7303 | 123.2437 | 123.0606 | 123.0377 | 123.0194 | 123.1934 | -123.4314 | -46.3348
4414.7812 | 123.3307 | -68.1656 | 54.8172 | 0.25536 | 0.011865 | 0.0061737 | 0.0024202 | -0.0063317 | -0.0065047 | -0.0013758 | 54.8859 | 54.9225 | -68.5776 | 55.1514 | 54.9637 | 54.9271 | 54.7119 | 55.0644 | 54.9042 | 8.5052 | -0.41199 | 0.10529 | 123.0515 | 123.317 | 0.14648 | 76.6708 | 0.086975 | 123.4634 | 122.8775 | 123.23 | 123.1293 | 123.0881 | 123.0515 | 123.0698 | 123.0927 | 76.6708 | 123.0881 | 123.0515 | 123.0927 | 123.1293 | 123.0698 | -123.3948 | -46.312
4415.7812 | 123.1705 | -68.2343 | 54.8401 | 0.1638 | 0.014428 | 0.0076691 | 0.0096834 | -0.0065455 | -0.0082137 | -0.003512 | 54.8218 | 55.0095 | -68.5913 | 54.9728 | 54.7668 | 54.7394 | 54.8859 | 54.8767 | 54.9591 | 8.4961 | -0.35706 | 0.16937 | 123.056 | 123.2071 | -0.073242 | 76.7303 | 0.11902 | 123.4131 | 123.1201 | 123.111 | 123.0011 | 123.2437 | 123.056 | 123.1934 | 122.9736 | 76.7303 | 123.2437 | 123.056 | 122.9736 | 123.0011 | 123.1934 | -123.4314 | -46.344
4416.7812 | 123.2666 | -68.2205 | 54.8447 | 0.21721 | 0.015923 | 0.0031831 | 0.0064792 | -0.0054773 | -0.0067185 | -0.0030848 | 54.8126 | 55.0095 | -68.5867 | 55.0278 | 54.8126 | 54.7897 | 54.7943 | 54.9316 | 54.9271 | 8.4961 | -0.36621 | 0.16479 | 123.0331 | 123.2483 | -0.032044 | 76.7166 | 0.082397 | 123.3994 | 123.0148 | 123.1522 | 123.0331 | 123.23 | 123.0331 | 123.1476 | 123.0103 | 76.7166 | 123.23 | 123.0331 | 123.0103 | 123.0331 | 123.1476 | -123.4314 | -46.3486
4417.7812 | 123.3307 | -68.1931 | 54.8035 | 0.2935 | 0.012292 | 0.0040375 | 0.004343 | -0.0073999 | -0.0047957 | -0.00094839 | 54.8492 | 54.9637 | -68.573 | 55.0598 | 54.863 | 54.8904 | 54.6753 | 54.9454 | 54.9088 | 8.4961 | -0.37994 | 0.16022 | 123.0423 | 123.2529 | 0.059509 | 76.6891 | 0.10529 | 123.4222 | 122.8683 | 123.1384 | 123.056 | 123.1567 | 123.0423 | 123.1018 | 123.0835 | 76.6891 | 123.1567 | 123.0423 | 123.0835 | 123.056 | 123.1018 | -123.3765 | -46.3074
4418.7812 | 123.3627 | -68.2022 | 54.7943 | 0.30113 | 0.011651 | 0.0038239 | 0.0045566 | -0.0086817 | -0.0065047 | -0.0020166 | 54.8904 | 54.9271 | -68.5684 | 55.0781 | 54.8676 | 54.8767 | 54.6982 | 55.014 | 54.8813 | 8.5052 | -0.36621 | 0.13275 | 123.0927 | 123.2803 | 0.073242 | 76.7075 | 0.086975 | 123.4589 | 122.9004 | 123.2162 | 123.0698 | 123.1293 | 123.0927 | 123.0835 | 123.0789 | 76.7075 | 123.1293 | 123.0927 | 123.0789 | 123.0698 | 123.0835 | -123.3627 | -46.2891
4419.7812 | 123.2574 | -68.2205 | 54.895 | -0.12611 | 0.012933 | 0.0059601 | 0.008829 | -0.0095361 | -0.0082137 | -0.0013758 | 54.8813 | 55.0323 | -68.5501 | 55.0781 | 54.8676 | 54.8309 | 54.8904 | 55.0186 | 54.95 | 8.4915 | -0.32959 | 0.13733 | 123.1018 | 123.2986 | -0.027466 | 76.712 | 0.054931 | 123.4314 | 123.111 | 123.2391 | 123.0881 | 123.2529 | 123.1018 | 123.1705 | 123.0515 | 76.712 | 123.2529 | 123.1018 | 123.0515 | 123.0881 | 123.1705 | -123.4451 | -46.4035
4420.7812 | 123.23 | -68.2526 | 54.8126 | 0.20958 | 0.015496 | 0.010446 | 0.0081882 | -0.0071863 | -0.0050095 | -0.00094839 | 54.8264 | 55.014 | -68.5822 | 54.9774 | 54.7806 | 54.7897 | 54.8172 | 54.9225 | 54.9362 | 8.5007 | -0.32959 | 0.20142 | 123.0789 | 123.23 | -0.032043 | 76.7532 | 0.1236 | 123.4085 | 123.0698 | 123.175 | 123.0331 | 123.2666 | 123.0789 | 123.1888 | 123.0423 | 76.7532 | 123.2666 | 123.0789 | 123.0423 | 123.0331 | 123.1888 | -123.3948 | -46.312
4421.7812 | 123.2162 | -68.2343 | 54.8401 | 0.14854 | 0.015283 | 0.0059601 | 0.0062656 | -0.0059045 | -0.0062911 | -0.0056482 | 54.8035 | 55.014 | -68.6188 | 54.9591 | 54.7485 | 54.7485 | 54.8996 | 54.8904 | 54.9408 | 8.4915 | -0.38452 | 0.17395 | 123.0377 | 123.1934 | -0.091553 | 76.7258 | 0.10071 | 123.4222 | 123.1338 | 123.1247 | 122.9828 | 123.2483 | 123.0377 | 123.175 | 122.9828 | 76.7258 | 123.2483 | 123.0377 | 122.9828 | 122.9828 | 123.175 | -123.4589 | -46.3486
4422.7812 | 123.23 | -68.2022 | 54.8538 | -2.1784 | 0.016351 | 0.0066009 | 0.0079744 | -0.0063317 | -0.0039413 | -0.0032984 | 54.863 | 55.0232 | -68.5776 | 54.9774 | 54.7623 | 54.7668 | 54.863 | 54.9088 | 54.9408 | 8.4961 | -0.37537 | 0.16937 | 123.0652 | 123.1796 | -0.091553 | 76.6983 | 0.086975 | 123.4406 | 123.0652 | 123.111 | 122.9645 | 123.2254 | 123.0652 | 123.143 | 122.9691 | 76.6983 | 123.2254 | 123.0652 | 122.9691 | 122.9645 | 123.143 | -123.4314 | -46.3577
4423.7812 | 123.23 | -68.2022 | 54.8492 | -0.057449 | 0.014001 | 0.0036103 | 0.00712 | -0.0063317 | -0.0075729 | -0.0011622 | 54.8904 | 55.0278 | -68.573 | 55.0644 | 54.8538 | 54.8401 | 54.8721 | 55.0003 | 54.982 | 8.4915 | -0.37079 | 0.17853 | 123.0927 | 123.2666 | 0.004578 | 76.6937 | 0.13275 | 123.4634 | 123.0743 | 123.2025 | 123.056 | 123.23 | 123.0927 | 123.1842 | 123.0423 | 76.6937 | 123.23 | 123.0927 | 123.0423 | 123.056 | 123.1842 | -123.4222 | -46.3577
4424.7812 | 123.1888 | -68.2388 | 54.8721 | 0.15617 | 0.012078 | 0.0063873 | 0.0084018 | -0.0054773 | -0.0054367 | -0.00073479 | 54.808 | 55.0323 | -68.5913 | 54.9683 | 54.7623 | 54.744 | 54.8904 | 54.8859 | 54.9683 | 8.5007 | -0.35248 | 0.16022 | 123.0469 | 123.2071 | -0.10986 | 76.7395 | 0.096131 | 123.3994 | 123.1293 | 123.1247 | 123.0011 | 123.2712 | 123.0469 | 123.2071 | 122.9828 | 76.7395 | 123.2712 | 123.0469 | 122.9828 | 123.0011 | 123.2071 | -123.4634 | -46.3715
4425.7812 | 123.262 | -68.2022 | 54.8538 | -0.080337 | 0.011437 | 0.0044647 | 0.0084018 | -0.0069727 | -0.0050095 | -0.0037256 | 54.8996 | 55.0278 | -68.5822 | 55.069 | 54.8538 | 54.8035 | 54.8767 | 54.9911 | 54.9683 | 8.4961 | -0.37994 | 0.17395 | 123.1018 | 123.2712 | 0 | 76.6983 | 0.11444 | 123.4818 | 123.0789 | 123.1934 | 123.056 | 123.23 | 123.1018 | 123.1705 | 123.0057 | 76.6983 | 123.23 | 123.1018 | 123.0057 | 123.056 | 123.1705 | -123.436 | -46.3577
4426.7812 | 123.23 | -68.2068 | 54.8401 | 0.20195 | 0.014214 | 0.0040375 | 0.005411 | -0.0041955 | -0.0037277 | -0.00073479 | 54.808 | 55.0323 | -68.6234 | 54.9179 | 55.0278 | 54.8676 | 54.95 | 54.9316 | 54.9866 | 8.4961 | -0.41656 | 0.19226 | 123.0148 | 123.1247 | 0.18768 | 76.7029 | 0.14648 | 123.4314 | 123.1567 | 123.1384 | 123.2346 | 123.2391 | 123.0148 | 123.1934 | 123.0743 | 76.7029 | 123.2391 | 123.0148 | 123.0743 | 123.2346 | 123.1934 | -123.4634 | -46.344
4427.7812 | 123.2254 | -68.2388 | 54.8401 | 0.19432 | 0.014855 | 0.0038239 | 0.0047702 | -0.0063317 | -0.0060775 | -9.3992e-05 | 54.8218 | 55.0369 | -68.5913 | 54.9774 | 54.7852 | 54.7806 | 54.8584 | 54.9225 | 54.95 | 8.4961 | -0.35248 | 0.19684 | 123.0606 | 123.2162 | -0.054932 | 76.7349 | 0.10986 | 123.4131 | 123.0972 | 123.1613 | 123.024 | 123.2758 | 123.0606 | 123.1888 | 123.0194 | 76.7349 | 123.2758 | 123.0606 | 123.0194 | 123.024 | 123.1888 | -123.4314 | -46.344
4428.7812 | 123.1705 | -68.2388 | 54.8355 | 0.14854 | 0.014855 | 0.0051057 | 0.0069064 | -0.0063317 | -0.0047957 | -0.0011622 | 54.8401 | 55.0323 | -68.6005 | 54.9637 | 54.744 | 54.7531 | 54.8904 | 54.8904 | 54.9316 | 8.4961 | -0.36163 | 0.19684 | 123.0789 | 123.2025 | -0.091552 | 76.7349 | 0.096131 | 123.4406 | 123.1293 | 123.1293 | 122.9828 | 123.2712 | 123.0789 | 123.1705 | 122.9919 | 76.7349 | 123.2712 | 123.0789 | 122.9919 | 122.9828 | 123.1705 | -123.436 | -46.3394
4429.7812 | 123.3032 | -68.1931 | 54.8309 | 0.27824 | 0.013146 | 0.0078827 | 0.0024202 | -0.0063317 | -0.0054367 | -0.001803 | 54.863 | 54.982 | -68.5959 | 55.0095 | 54.8584 | 54.8676 | 54.7028 | 54.9911 | 54.9179 | 8.4961 | -0.40283 | 0.15106 | 123.056 | 123.2025 | 0.027465 | 76.6891 | 0.086975 | 123.4589 | 122.8958 | 123.1842 | 123.0515 | 123.175 | 123.056 | 123.111 | 123.0606 | 76.6891 | 123.175 | 123.056 | 123.0606 | 123.0515 | 123.111 | -123.4268 | -46.3348
4430.7812 | 123.2895 | -68.2251 | 54.8309 | 0.24773 | 0.014214 | 0.0044647 | 0.0058382 | -0.0041955 | -0.0047957 | -0.0015894 | 54.8264 | 54.9866 | -68.6005 | 55.0278 | 54.8264 | 54.8401 | 54.7485 | 54.9866 | 54.9362 | 8.4961 | -0.37537 | 0.15564 | 123.0515 | 123.2529 | -0.004578 | 76.7212 | 0.10528 | 123.4268 | 122.9736 | 123.2117 | 123.0515 | 123.2117 | 123.0515 | 123.1613 | 123.0652 | 76.7212 | 123.2117 | 123.0515 | 123.0652 | 123.0515 | 123.1613 | -123.4314 | -46.3348
4431.7812 | 123.2437 | -68.1885 | 54.8492 | -0.11848 | 0.012292 | 0.0029693 | 0.00712 | -0.0050501 | -0.0067185 | -0.003512 | 54.8813 | 55.0461 | -68.573 | 55.0461 | 54.8584 | 54.8035 | 54.9133 | 55.0278 | 54.9728 | 8.5007 | -0.38452 | 0.19684 | 123.0698 | 123.2346 | 0.009155 | 76.6891 | 0.1236 | 123.4543 | 123.1018 | 123.2162 | 123.0469 | 123.2346 | 123.0698 | 123.1613 | 122.9919 | 76.6891 | 123.2346 | 123.0698 | 122.9919 | 123.0469 | 123.1613 | -123.4222 | -46.3486
4432.7812 | 123.1338 | -68.2068 | 54.8447 | -0.026932 | 0.011865 | 0.0040375 | 0.0060518 | -0.0059045 | -0.0069321 | -0.0020166 | 54.8904 | 55.0232 | -68.5547 | 55.0598 | 54.863 | 54.8264 | 54.8859 | 55.0186 | 55.0049 | 8.4869 | -0.3479 | 0.17853 | 123.0972 | 123.2666 | 0.01831 | 76.6937 | 0.16022 | 123.4451 | 123.0927 | 123.2254 | 123.0698 | 123.23 | 123.0972 | 123.2117 | 123.0331 | 76.6937 | 123.23 | 123.0972 | 123.0331 | 123.0698 | 123.2117 | -123.3994 | -46.3577
4433.7812 | 123.262 | -68.2022 | 54.8584 | -0.095596 | 0.013787 | 0.0074555 | 0.0062656 | -0.0039819 | -0.0052231 | -0.0020166 | 54.9042 | 55.0415 | -68.5684 | 55.0644 | 54.8492 | 54.8172 | 54.8859 | 55.0095 | 54.9866 | 8.4961 | -0.36621 | 0.18311 | 123.1064 | 123.2666 | -0.009155 | 76.6983 | 0.12817 | 123.4726 | 123.0881 | 123.2117 | 123.0515 | 123.2437 | 123.1064 | 123.1888 | 123.0194 | 76.6983 | 123.2437 | 123.1064 | 123.0194 | 123.0515 | 123.1888 | -123.4268 | -46.3623
4434.7812 | 123.262 | -68.2251 | 54.8309 | 0.26299 | 0.015283 | 0.0038239 | 0.0069064 | -0.0037683 | -0.0047957 | -0.00094839 | 54.8309 | 54.9774 | -68.5776 | 55.0049 | 54.7989 | 54.8035 | 54.7989 | 54.9408 | 54.95 | 8.5007 | -0.35248 | 0.14648 | 123.056 | 123.23 | -0.032044 | 76.7258 | 0.11902 | 123.4085 | 123.024 | 123.1659 | 123.024 | 123.2025 | 123.056 | 123.175 | 123.0286 | 76.7258 | 123.2025 | 123.056 | 123.0286 | 123.024 | 123.175 | -123.4085 | -46.3303
4435.7812 | 123.2483 | -68.2297 | 54.8767 | 0.20195 | 0.014855 | 0.0044647 | 0.0077608 | -0.0059045 | -0.0067185 | 0.0020422 | 54.8126 | 55.0095 | -68.5959 | 54.9683 | 54.7668 | 54.744 | 54.6249 | 54.6112 | 54.9362 | 8.5007 | -0.36621 | 0.13275 | 123.0423 | 123.1979 | -0.10986 | 76.7303 | 0.059509 | 123.4085 | 122.8546 | 122.8409 | 122.9965 | 123.2391 | 123.0423 | 123.1659 | 122.9736 | 76.7303 | 123.2391 | 123.0423 | 122.9736 | 122.9965 | 123.1659 | -123.4726 | -46.376
4436.7812 | 123.2529 | -68.2205 | 54.8813 | -0.56099 | 0.012292 | 0.0098053 | 0.0062656 | -0.0065455 | -0.0071457 | -0.0022302 | 54.8721 | 55.0095 | -68.5867 | 55.0507 | 54.8218 | 54.8172 | 54.8813 | 54.982 | 54.9728 | 8.4961 | -0.36621 | 0.12817 | 123.0927 | 123.2712 | -0.05951 | 76.7166 | 0.091552 | 123.4589 | 123.1018 | 123.2025 | 123.0423 | 123.23 | 123.0927 | 123.1934 | 123.0377 | 76.7166 | 123.23 | 123.0927 | 123.0377 | 123.0423 | 123.1934 | -123.468 | -46.3852
4437.7812 | 123.2574 | -68.1793 | 54.863 | -0.034561 | 0.014001 | 0.0044647 | 0.005411 | -0.0065455 | -0.0043685 | -0.0013758 | 54.9133 | 55.0232 | -68.5638 | 55.0278 | 54.7028 | 54.7485 | 54.9408 | 55.0095 | 54.9683 | 8.4915 | -0.38452 | 0.16022 | 123.0927 | 123.2071 | -0.16022 | 76.6708 | 0.10529 | 123.4772 | 123.1201 | 123.1888 | 122.8821 | 123.2025 | 123.0927 | 123.1476 | 122.9279 | 76.6708 | 123.2025 | 123.0927 | 122.9279 | 122.8821 | 123.1476 | -123.4268 | -46.3715
4438.7812 | 123.2437 | -68.2251 | 54.8492 | 0.041733 | 0.015069 | 0.0042511 | 0.0073336 | -0.0048365 | -0.0071457 | -0.00094839 | 54.9133 | 55.0323 | -68.5684 | 55.0278 | 54.8355 | 54.808 | 54.8996 | 54.9957 | 54.9683 | 8.4915 | -0.34332 | 0.18311 | 123.1384 | 123.2529 | -0.013733 | 76.7166 | 0.11902 | 123.4818 | 123.1247 | 123.2208 | 123.0606 | 123.2574 | 123.1384 | 123.1934 | 123.0331 | 76.7166 | 123.2574 | 123.1384 | 123.0331 | 123.0606 | 123.1934 | -123.4177 | -46.3577
4439.7812 | 123.2803 | -68.2114 | 54.8538 | 0.27824 | 0.012078 | 0.0068147 | 0.0049838 | -0.0050501 | -0.0050095 | -0.00052119 | 54.8401 | 54.95 | -68.6096 | 55.0003 | 54.8035 | 54.8172 | 54.7806 | 54.9728 | 54.9454 | 8.5052 | -0.39825 | 0.09613 | 123.0515 | 123.2117 | -0.050354 | 76.7166 | 0.091553 | 123.4497 | 122.9919 | 123.1842 | 123.0148 | 123.1613 | 123.0515 | 123.1567 | 123.0286 | 76.7166 | 123.1613 | 123.0515 | 123.0286 | 123.0148 | 123.1567 | -123.4634 | -46.3486
4440.7812 | 123.2162 | -68.2114 | 54.8813 | -0.149 | 0.012078 | 0.0025421 | 0.0022066 | -0.0086817 | -0.0056503 | -0.0020166 | 54.8355 | 55.0507 | -68.5822 | 55.0232 | 54.8309 | 54.7989 | 54.9545 | 54.9957 | 54.9866 | 8.4915 | -0.37079 | 0.16937 | 123.0469 | 123.2346 | -0.050354 | 76.7029 | 0.10529 | 123.4177 | 123.1659 | 123.2071 | 123.0423 | 123.262 | 123.0469 | 123.1979 | 123.0103 | 76.7029 | 123.262 | 123.0469 | 123.0103 | 123.0423 | 123.1979 | -123.4634 | -46.3898
4441.7812 | 123.2574 | -68.2068 | 54.895 | -0.11085 | 0.012078 | 0.0038239 | 0.00712 | -0.0082545 | -0.0058639 | -0.001803 | 54.8584 | 55.0232 | -68.5547 | 55.0461 | 54.8264 | 54.8126 | 54.9133 | 55.0186 | 55.0003 | 8.4961 | -0.3479 | 0.12817 | 123.0652 | 123.2529 | -0.068665 | 76.7029 | 0.10528 | 123.4131 | 123.1201 | 123.2254 | 123.0331 | 123.23 | 123.0652 | 123.2071 | 123.0194 | 76.7029 | 123.23 | 123.0652 | 123.0194 | 123.0331 | 123.2071 | -123.4497 | -46.3989
4442.7812 | 123.2803 | -68.2068 | 54.8767 | -0.087967 | 0.013574 | 0.0012605 | 0.0069064 | -0.0065455 | -0.0054367 | -0.001803 | 54.9088 | 55.0232 | -68.5593 | 55.0598 | 54.8447 | 54.8264 | 54.8859 | 55.0003 | 54.9728 | 8.4961 | -0.35248 | 0.14648 | 123.1155 | 123.2666 | -0.032043 | 76.7029 | 0.09613 | 123.468 | 123.0927 | 123.2071 | 123.0515 | 123.23 | 123.1155 | 123.1796 | 123.0331 | 76.7029 | 123.23 | 123.1155 | 123.0331 | 123.0515 | 123.1796 | -123.436 | -46.3806
4443.7812 | 123.2666 | -68.2068 | 54.8584 | -0.04982 | 0.013574 | 0.0044647 | 0.0086154 | -0.0056909 | -0.0065047 | -0.0043664 | 54.9042 | 55.0232 | -68.5959 | 54.8996 | 54.7806 | 54.7989 | 54.8676 | 55.0278 | 54.982 | 8.4915 | -0.3891 | 0.16479 | 123.111 | 123.1064 | -0.077819 | 76.6983 | 0.1236 | 123.5001 | 123.0743 | 123.2346 | 122.9874 | 123.23 | 123.111 | 123.1888 | 123.0057 | 76.6983 | 123.23 | 123.111 | 123.0057 | 122.9874 | 123.1888 | -123.4543 | -46.3669
4444.7812 | 123.1796 | -68.2251 | 54.8492 | 0.10277 | 0.01336 | 0.0048921 | 0.0073336 | -0.0067591 | -0.0060775 | -0.0022302 | 54.8309 | 54.9774 | -68.6234 | 54.982 | 54.7806 | 54.7485 | 54.895 | 54.9271 | 54.9911 | 8.4915 | -0.39825 | 0.12817 | 123.056 | 123.2071 | -0.068664 | 76.7166 | 0.14191 | 123.4543 | 123.1201 | 123.1522 | 123.0057 | 123.2025 | 123.056 | 123.2162 | 122.9736 | 76.7166 | 123.2025 | 123.056 | 122.9736 | 123.0057 | 123.2162 | -123.4726 | -46.3577
4445.7812 | 123.2071 | -68.2251 | 54.9088 | -0.21004 | 0.014855 | 0.0029693 | 0.0011386 | -0.0061181 | -0.0069321 | -0.0013758 | 54.8264 | 55.0232 | -68.5776 | 54.9545 | 54.8172 | 54.7668 | 54.9408 | 54.9591 | 55.0278 | 8.5007 | -0.35248 | 0.11444 | 123.0515 | 123.1796 | -0.091552 | 76.7258 | 0.11902 | 123.4039 | 123.1659 | 123.1842 | 123.0423 | 123.2483 | 123.0515 | 123.2529 | 122.9919 | 76.7258 | 123.2483 | 123.0515 | 122.9919 | 123.0423 | 123.2529 | -123.4863 | -46.4081
4446.7812 | 123.2758 | -68.1976 | 54.8721 | -0.087967 | 0.012933 | 0.0066009 | 0.0058382 | -0.0061181 | -0.0062911 | -0.0032984 | 54.8813 | 55.0507 | -68.5547 | 55.0415 | 54.8584 | 54.8401 | 54.9042 | 55.014 | 54.9866 | 8.5007 | -0.35706 | 0.17853 | 123.0789 | 123.2391 | -0.013733 | 76.6983 | 0.11444 | 123.436 | 123.1018 | 123.2117 | 123.056 | 123.2483 | 123.0789 | 123.1842 | 123.0377 | 76.6983 | 123.2483 | 123.0789 | 123.0377 | 123.056 | 123.1842 | -123.4268 | -46.3715
4447.7812 | 123.2849 | -68.2068 | 54.8813 | -0.13374 | 0.010796 | 0.0046783 | 0.0062656 | -0.0078271 | -0.0071457 | -0.0024438 | 54.8767 | 55.0278 | -68.573 | 55.0552 | 54.8355 | 54.8447 | 54.9088 | 55.0049 | 55.0003 | 8.4915 | -0.36621 | 0.14648 | 123.0835 | 123.262 | -0.045777 | 76.6983 | 0.11902 | 123.4497 | 123.1155 | 123.2117 | 123.0423 | 123.2346 | 123.0835 | 123.2071 | 123.0515 | 76.6983 | 123.2346 | 123.0835 | 123.0515 | 123.0423 | 123.2071 | -123.4543 | -46.3898
4448.7812 | 123.262 | -68.1931 | 54.8676 | -0.20241 | 0.014642 | -0.00044854 | 0.0041292 | -0.0069727 | -0.0069321 | -0.0011622 | 54.9042 | 55.0369 | -68.5638 | 55.0507 | 54.8264 | 54.7897 | 54.8859 | 54.9957 | 54.9911 | 8.4915 | -0.37079 | 0.16937 | 123.0972 | 123.2437 | -0.041199 | 76.6846 | 0.1236 | 123.468 | 123.0789 | 123.1888 | 123.0194 | 123.23 | 123.0972 | 123.1842 | 122.9828 | 76.6846 | 123.23 | 123.0972 | 122.9828 | 123.0194 | 123.1842 | -123.4314 | -46.376
4449.7812 | 123.2391 | -68.1747 | 54.895 | -0.011673 | 0.01101 | 0.0091645 | 0.004343 | -0.0056909 | -0.0075729 | -0.0022302 | 54.7623 | 54.95 | -68.6234 | 55.0507 | 54.8264 | 54.8172 | 54.8996 | 54.9957 | 54.9728 | 8.5007 | -0.44861 | 0.054931 | 122.937 | 123.2254 | -0.068665 | 76.6754 | 0.077819 | 123.3856 | 123.0743 | 123.1705 | 123.0011 | 123.1247 | 122.937 | 123.1476 | 122.9919 | 76.6754 | 123.1247 | 122.937 | 122.9919 | 123.0011 | 123.1476 | -123.5184 | -46.3943
4450.7812 | 123.2346 | -68.1931 | 54.895 | -0.0040434 | 0.015069 | 0.0042511 | 0.0056246 | -0.0065455 | -0.0056503 | -0.001803 | 54.895 | 55.0232 | -68.5638 | 55.0232 | 54.8035 | 54.7989 | 54.8859 | 54.9545 | 54.982 | 8.4961 | -0.37079 | 0.12817 | 123.0881 | 123.2162 | -0.091553 | 76.6891 | 0.086975 | 123.4589 | 123.0789 | 123.1476 | 122.9965 | 123.2162 | 123.0881 | 123.175 | 122.9919 | 76.6891 | 123.2162 | 123.0881 | 122.9919 | 122.9965 | 123.175 | -123.4589 | -46.3989
4451.7812 | 123.2483 | -68.2571 | 54.8813 | 0.25536 | 0.013146 | 0.0063873 | 0.0058382 | -0.0061181 | -0.0052231 | -0.0043664 | 54.808 | 55.0232 | -68.5959 | 54.9774 | 54.7623 | 54.7394 | 54.6112 | 54.6249 | 54.9271 | 8.5007 | -0.33874 | 0.14191 | 123.0652 | 123.2346 | -0.11902 | 76.7578 | 0.045776 | 123.4039 | 122.8683 | 122.8821 | 123.0194 | 123.2803 | 123.0652 | 123.1842 | 122.9965 | 76.7578 | 123.2803 | 123.0652 | 122.9965 | 123.0194 | 123.1842 | -123.4772 | -46.3806
4452.7812 | 123.2254 | -68.1747 | 54.8996 | -0.18715 | 0.010796 | 0.0025421 | -0.00035676 | -0.0063317 | -0.0067185 | -0.0022302 | 54.8218 | 54.9728 | -68.5959 | 55.0369 | 54.8859 | 54.8172 | 54.9179 | 54.9911 | 54.9911 | 8.4915 | -0.42114 | 0.073242 | 122.9965 | 123.2117 | -0.013733 | 76.6663 | 0.091553 | 123.4177 | 123.0927 | 123.1659 | 123.0606 | 123.1476 | 122.9965 | 123.1659 | 122.9919 | 76.6663 | 123.1476 | 122.9965 | 122.9919 | 123.0606 | 123.1659 | -123.4955 | -46.4081
4453.7812 | 123.317 | -68.1656 | 54.8721 | -0.15663 | 0.0075922 | -2.1336e-05 | -0.00014316 | -0.0082545 | -0.0065047 | -0.00052119 | 54.8813 | 54.9225 | -68.5272 | 55.101 | 54.8996 | 54.8996 | 54.8172 | 55.101 | 54.9591 | 8.5007 | -0.36163 | 0.050354 | 123.0469 | 123.2666 | 0.027466 | 76.6663 | 0.086975 | 123.4085 | 122.9828 | 123.2666 | 123.0652 | 123.0881 | 123.0469 | 123.1247 | 123.0652 | 76.6663 | 123.0881 | 123.0469 | 123.0652 | 123.0652 | 123.1247 | -123.3994 | -46.3715
4454.7812 | 123.2666 | -68.1885 | 54.9042 | -0.14137 | 0.010796 | 0.0061737 | 0.0062656 | -0.0080407 | -0.0082137 | -0.0028712 | 54.8676 | 55.0095 | -68.5822 | 55.0552 | 54.8355 | 54.8309 | 54.9042 | 55.014 | 54.982 | 8.4961 | -0.39368 | 0.10528 | 123.056 | 123.2437 | -0.068665 | 76.6846 | 0.07782 | 123.4497 | 123.0927 | 123.2025 | 123.024 | 123.1979 | 123.056 | 123.1705 | 123.0194 | 76.6846 | 123.1979 | 123.056 | 123.0194 | 123.024 | 123.1705 | -123.4863 | -46.4081
4455.7812 | 123.317 | -68.1473 | 54.8721 | -0.12611 | 0.0060968 | -0.0015167 | -0.00014316 | -0.0091089 | -0.0077865 | -0.0015894 | 55.1468 | 54.9637 | -68.5135 | 55.0598 | 54.8904 | 54.8996 | 54.7806 | 55.1285 | 54.9728 | 8.4961 | -0.36621 | 0.091553 | 123.2941 | 123.2071 | 0.018311 | 76.6434 | 0.10071 | 123.6603 | 122.9279 | 123.2758 | 123.0377 | 123.111 | 123.2941 | 123.1201 | 123.0469 | 76.6434 | 123.111 | 123.2941 | 123.0469 | 123.0377 | 123.1201 | -123.3856 | -46.376
4456.7812 | 123.3582 | -68.1656 | 54.8355 | 0.25536 | 0.011224 | 0.0095917 | 0.005411 | -0.0095361 | -0.0069321 | -0.0037256 | 54.8996 | 54.9316 | -68.5547 | 55.069 | 54.8538 | 54.9637 | 54.4464 | 54.9362 | 54.8538 | 8.4915 | -0.3891 | 0.096131 | 123.0652 | 123.2346 | 0.018311 | 76.6571 | 0.018311 | 123.4543 | 122.612 | 123.1018 | 123.0194 | 123.0972 | 123.0652 | 123.0194 | 123.1293 | 76.6571 | 123.0972 | 123.0652 | 123.1293 | 123.0194 | 123.0194 | -123.3902 | -46.344
4457.7812 | 123.3124 | -68.1793 | 54.8584 | -0.17952 | 0.011224 | 0.0051057 | 0.0017794 | -0.0091089 | -0.0086411 | -0.003512 | 54.895 | 54.9408 | -68.5638 | 55.1147 | 54.8904 | 54.9042 | 54.808 | 55.0964 | 54.9316 | 8.4915 | -0.38452 | 0.082398 | 123.0743 | 123.2941 | 0.032044 | 76.6708 | 0.073243 | 123.4589 | 122.9874 | 123.2758 | 123.0698 | 123.1201 | 123.0743 | 123.111 | 123.0835 | 76.6708 | 123.1201 | 123.0743 | 123.0835 | 123.0698 | 123.111 | -123.4222 | -46.3669
4458.7812 | 123.2391 | -68.1931 | 54.895 | -0.149 | 0.011651 | 0.0027557 | 0.0056246 | -0.010604 | -0.0082137 | -0.0030848 | 54.8309 | 55.0049 | -68.573 | 55.0323 | 54.7943 | 54.7852 | 54.9362 | 54.982 | 54.95 | 8.4915 | -0.37994 | 0.10986 | 123.024 | 123.2254 | -0.10071 | 76.6846 | 0.054931 | 123.4039 | 123.1293 | 123.175 | 122.9874 | 123.1979 | 123.024 | 123.143 | 122.9782 | 76.6846 | 123.1979 | 123.024 | 122.9782 | 122.9874 | 123.143 | -123.468 | -46.4035
4459.7812 | 123.2117 | -68.1702 | 54.9088 | -0.080337 | 0.011865 | 0.0076691 | 0.0051974 | -0.011245 | -0.0090683 | -0.0026574 | 54.8447 | 54.95 | -68.605 | 55.0415 | 54.8126 | 54.7852 | 54.9591 | 54.9911 | 55.0003 | 8.4961 | -0.43488 | 0.041199 | 123.0148 | 123.2117 | -0.09613 | 76.6663 | 0.091553 | 123.4497 | 123.1293 | 123.1613 | 122.9828 | 123.1201 | 123.0148 | 123.1705 | 122.9553 | 76.6663 | 123.1201 | 123.0148 | 122.9553 | 122.9828 | 123.1705 | -123.5138 | -46.4127
4460.7812 | 123.2895 | -68.2022 | 54.8447 | 0.22484 | 0.0095148 | 0.0053193 | 0.001993 | -0.010818 | -0.0030869 | -0.0037256 | 54.8721 | 54.8859 | -68.5822 | 55.0598 | 54.8584 | 54.8538 | 54.7073 | 55.0186 | 54.9088 | 8.5007 | -0.37994 | 0.041198 | 123.0743 | 123.262 | 0.013732 | 76.7029 | 0.064086 | 123.4543 | 122.9095 | 123.2208 | 123.0606 | 123.0881 | 123.0743 | 123.111 | 123.056 | 76.7029 | 123.0881 | 123.0743 | 123.056 | 123.0606 | 123.111 | -123.4268 | -46.344
4461.7812 | 123.1934 | -68.248 | 54.8767 | 0.13329 | 0.012719 | 0.0061737 | 0.008829 | -0.0088953 | -0.0058639 | -0.0039392 | 54.8309 | 55.0095 | -68.6005 | 54.982 | 54.7531 | 54.744 | 54.8859 | 54.8721 | 54.9774 | 8.4915 | -0.35248 | 0.13275 | 123.0789 | 123.23 | -0.1236 | 76.7395 | 0.10071 | 123.4314 | 123.1338 | 123.1201 | 123.0011 | 123.2574 | 123.0789 | 123.2254 | 122.9919 | 76.7395 | 123.2574 | 123.0789 | 122.9919 | 123.0011 | 123.2254 | -123.4772 | -46.3852
4462.7812 | 123.23 | -68.2159 | 54.8904 | -0.12611 | 0.01336 | 0.0029693 | 0.004343 | -0.0088953 | -0.0075729 | -0.0024438 | 54.8264 | 55.0049 | -68.6188 | 55.0278 | 54.8218 | 54.7852 | 54.9545 | 54.9866 | 54.9957 | 8.4869 | -0.40283 | 0.11444 | 123.0423 | 123.2437 | -0.068665 | 76.7029 | 0.10529 | 123.4451 | 123.1705 | 123.2025 | 123.0377 | 123.2208 | 123.0423 | 123.2117 | 123.0011 | 76.7029 | 123.2208 | 123.0423 | 123.0011 | 123.0377 | 123.2117 | -123.5092 | -46.4035
4463.7812 | 123.2162 | -68.1793 | 54.9225 | -0.11085 | 0.010156 | 0.0053193 | 0.00049764 | -0.0082545 | -0.0071457 | -0.003512 | 54.8264 | 54.982 | -68.5684 | 55.0323 | 54.8218 | 54.7897 | 54.9591 | 54.9911 | 55.014 | 8.5007 | -0.3891 | 0.05951 | 123.0057 | 123.2117 | -0.10071 | 76.68 | 0.091553 | 123.3948 | 123.1384 | 123.1705 | 123.0011 | 123.1613 | 123.0057 | 123.1934 | 122.9691 | 76.68 | 123.1613 | 123.0057 | 122.9691 | 123.0011 | 123.1934 | -123.4909 | -46.4218
4464.7656 | 123.2666 | -68.1839 | 54.8996 | -0.12611 | 0.0097284 | 0.0021149 | 0.0064792 | -0.0082545 | -0.0082137 | -0.0028712 | 54.8813 | 55.0003 | -68.5913 | 55.069 | 54.863 | 54.8264 | 54.9042 | 55.014 | 55.0003 | 8.4915 | -0.40741 | 0.10071 | 123.0652 | 123.2529 | -0.036621 | 76.6754 | 0.10071 | 123.4726 | 123.0881 | 123.1979 | 123.0469 | 123.1842 | 123.0652 | 123.1842 | 123.0103 | 76.6754 | 123.1842 | 123.0652 | 123.0103 | 123.0469 | 123.1842 | -123.4909 | -46.4081
4465.7812 | 123.262 | -68.1839 | 54.8813 | -0.20241 | 0.009942 | 0.0012605 | 0.0017794 | -0.011245 | -0.0047957 | -0.0026574 | 54.8813 | 54.9683 | -68.5547 | 55.0461 | 54.8538 | 54.8309 | 54.9271 | 55.0186 | 54.9957 | 8.5098 | -0.37079 | 0.086975 | 123.0652 | 123.23 | -0.027466 | 76.6937 | 0.11444 | 123.436 | 123.111 | 123.2025 | 123.0377 | 123.1522 | 123.0652 | 123.1796 | 123.0148 | 76.6937 | 123.1522 | 123.0652 | 123.0148 | 123.0377 | 123.1796 | -123.436 | -46.3715
4466.7812 | 123.2254 | -68.2068 | 54.8721 | 0.011215 | 0.013146 | 0.0055329 | 0.0079744 | -0.0078271 | -0.0071457 | -0.0015894 | 54.8813 | 54.9683 | -68.5684 | 55.0323 | 54.8264 | 54.7989 | 54.863 | 54.9545 | 54.9637 | 8.4961 | -0.36163 | 0.096131 | 123.0881 | 123.2391 | -0.045776 | 76.7029 | 0.091553 | 123.4497 | 123.0698 | 123.1613 | 123.0331 | 123.175 | 123.0881 | 123.1705 | 123.0057 | 76.7029 | 123.175 | 123.0881 | 123.0057 | 123.0331 | 123.1705 | -123.4406 | -46.376
4467.7812 | 123.2117 | -68.1885 | 54.8904 | -0.11848 | 0.01101 | 0.0033967 | 0.00049764 | -0.011031 | -0.0062911 | -0.00094839 | 54.8309 | 54.9683 | -68.541 | 55.0415 | 54.8401 | 54.8035 | 54.9728 | 54.9957 | 55.0003 | 8.4915 | -0.35248 | 0.07782 | 123.0194 | 123.23 | -0.050354 | 76.68 | 0.10986 | 123.3719 | 123.1613 | 123.1842 | 123.0286 | 123.1567 | 123.0194 | 123.1888 | 122.9919 | 76.68 | 123.1567 | 123.0194 | 122.9919 | 123.0286 | 123.1888 | -123.4314 | -46.3989
4468.7812 | 123.2574 | -68.1931 | 54.8859 | -0.095596 | 0.011651 | 0.0068147 | 0.00712 | -0.0082545 | -0.0067185 | -0.0032984 | 54.8813 | 54.982 | -68.5684 | 55.0781 | 54.8584 | 54.8218 | 54.8859 | 55.0095 | 54.9454 | 8.4961 | -0.37537 | 0.096131 | 123.0743 | 123.2712 | -0.027466 | 76.6891 | 0.05951 | 123.4497 | 123.0789 | 123.2025 | 123.0515 | 123.175 | 123.0743 | 123.1384 | 123.0148 | 76.6891 | 123.175 | 123.0743 | 123.0148 | 123.0515 | 123.1384 | -123.4543 | -46.3898
4469.7812 | 123.3307 | -68.161 | 54.8538 | -0.04219 | 0.010369 | 0.0021149 | -0.0020658 | -0.0097497 | -0.0043685 | -0.00458 | 54.8538 | 54.9133 | -68.5455 | 55.0735 | 54.9042 | 54.9088 | 54.7852 | 55.0735 | 54.9225 | 8.5007 | -0.38452 | 0.059509 | 123.0148 | 123.2346 | 0.050354 | 76.6617 | 0.068664 | 123.3994 | 122.9462 | 123.2346 | 123.0652 | 123.0743 | 123.0148 | 123.0835 | 123.0698 | 76.6617 | 123.0743 | 123.0148 | 123.0698 | 123.0652 | 123.0835 | -123.3994 | -46.3531
4470.7812 | 123.2162 | -68.1747 | 54.9088 | -0.21767 | 0.012505 | 0.0033967 | 0.004343 | -0.011031 | -0.0062911 | -0.0028712 | 54.8447 | 54.9957 | -68.5822 | 55.0369 | 54.8264 | 54.7943 | 54.9591 | 54.9774 | 54.9911 | 8.4869 | -0.40741 | 0.086976 | 123.0194 | 123.2117 | -0.082397 | 76.6617 | 0.082398 | 123.4268 | 123.1338 | 123.1522 | 123.0011 | 123.1705 | 123.0194 | 123.1659 | 122.9691 | 76.6617 | 123.1705 | 123.0194 | 122.9691 | 123.0011 | 123.1659 | -123.4909 | -46.4218
4471.7812 | 123.2758 | -68.1839 | 54.8904 | -0.10323 | 0.010583 | 0.0036103 | 0.0062656 | -0.0080407 | -0.0086411 | -0.0022302 | 54.8676 | 54.9911 | -68.5913 | 55.069 | 54.8401 | 54.8172 | 54.9408 | 55.0186 | 54.9774 | 8.4915 | -0.40741 | 0.10071 | 123.0515 | 123.2529 | -0.050354 | 76.6754 | 0.086975 | 123.4589 | 123.1247 | 123.2025 | 123.024 | 123.175 | 123.0515 | 123.1613 | 123.0011 | 76.6754 | 123.175 | 123.0515 | 123.0011 | 123.024 | 123.1613 | -123.4818 | -46.3989
4472.7656 | 123.2254 | -68.1839 | 54.8767 | -0.15663 | 0.011651 | 0.0046783 | 0.0039156 | -0.0091089 | -0.0043685 | -0.00094839 | 54.8538 | 54.9866 | -68.5867 | 55.0278 | 54.8401 | 54.7852 | 54.9545 | 54.9911 | 54.9591 | 8.4915 | -0.40283 | 0.10986 | 123.0377 | 123.2117 | -0.036621 | 76.6754 | 0.082397 | 123.4406 | 123.1384 | 123.175 | 123.024 | 123.1705 | 123.0377 | 123.143 | 122.9691 | 76.6754 | 123.1705 | 123.0377 | 122.9691 | 123.024 | 123.143 | -123.4634 | -46.3852
4473.7656 | 123.3307 | -68.1335 | 54.8721 | 0.07988 | 0.011651 | 0.0010467 | -0.00099756 | -0.0099633 | -0.0071457 | -0.0013758 | 54.8859 | 54.9179 | -68.5181 | 55.1331 | 54.9362 | 54.9088 | 54.808 | 55.1056 | 54.9225 | 8.4961 | -0.38452 | 0.045777 | 123.0194 | 123.2666 | 0.064087 | 76.6296 | 0.050354 | 123.4039 | 122.9416 | 123.2391 | 123.0698 | 123.0515 | 123.0194 | 123.056 | 123.0423 | 76.6296 | 123.0515 | 123.0194 | 123.0423 | 123.0698 | 123.056 | -123.3902 | -46.376
4474.7812 | 123.3444 | -68.1839 | 54.8584 | -0.0040434 | 0.010369 | -0.00044854 | 7.0444e-05 | -0.011672 | -0.0039413 | -0.0026574 | 54.863 | 54.9179 | -68.5501 | 55.0919 | 54.8859 | 54.8859 | 54.776 | 55.0827 | 54.9133 | 8.5007 | -0.36621 | 0.05951 | 123.0469 | 123.2758 | 0.027466 | 76.6846 | 0.054932 | 123.4131 | 122.9599 | 123.2666 | 123.0698 | 123.1018 | 123.0469 | 123.0972 | 123.0698 | 76.6846 | 123.1018 | 123.0469 | 123.0698 | 123.0698 | 123.0972 | -123.4085 | -46.3577
4475.8125 | 123.3307 | -68.1839 | 54.8172 | 0.21721 | 0.01336 | 0.0076691 | 0.0056246 | -0.0088953 | -0.0060775 | -0.00030759 | 54.895 | 54.9133 | -68.5684 | 55.0781 | 54.863 | 54.8813 | 54.7028 | 55.0369 | 54.895 | 8.5007 | -0.38452 | 0.09613 | 123.0789 | 123.262 | 0.045776 | 76.6846 | 0.07782 | 123.4634 | 122.8867 | 123.2208 | 123.0469 | 123.0972 | 123.0789 | 123.0789 | 123.0652 | 76.6846 | 123.0972 | 123.0789 | 123.0652 | 123.0469 | 123.0789 | -123.3856 | -46.3165
4476.7812 | 123.2162 | -68.1976 | 54.9042 | -0.37025 | 0.013146 | 0.0025421 | 0.005411 | -0.0121 | -0.0082137 | -0.0037256 | 54.8172 | 54.982 | -68.5822 | 55.0369 | 54.8264 | 54.7897 | 54.9454 | 54.9911 | 54.9774 | 8.4869 | -0.38452 | 0.07782 | 123.0148 | 123.2346 | -0.07782 | 76.6846 | 0.073242 | 123.3994 | 123.143 | 123.1888 | 123.024 | 123.1796 | 123.0148 | 123.175 | 122.9874 | 76.6846 | 123.1796 | 123.0148 | 122.9874 | 123.024 | 123.175 | -123.4863 | -46.4172
4477.7656 | 123.3261 | -68.161 | 54.8721 | -0.11085 | 0.011224 | 0.0053193 | 0.0041292 | -0.0091089 | -0.0069321 | -0.0030848 | 54.9133 | 54.95 | -68.5501 | 55.1285 | 54.9133 | 54.895 | 54.8309 | 55.101 | 54.95 | 8.4961 | -0.3891 | 0.07782 | 123.0743 | 123.2895 | 0.041199 | 76.6571 | 0.07782 | 123.4634 | 122.9919 | 123.262 | 123.0743 | 123.111 | 123.0743 | 123.111 | 123.056 | 76.6571 | 123.111 | 123.0743 | 123.056 | 123.0743 | 123.111 | -123.4222 | -46.376
4478.7656 | 123.2437 | -68.2022 | 54.895 | -0.17189 | 0.012505 | 0.0057465 | 0.0084018 | -0.010391 | -0.0088547 | -0.0043664 | 54.8401 | 54.9911 | -68.5776 | 55.0461 | 54.8309 | 54.7852 | 54.95 | 54.9866 | 54.9728 | 8.5052 | -0.37537 | 0.09613 | 123.0423 | 123.2483 | -0.064087 | 76.7075 | 0.077819 | 123.4177 | 123.1522 | 123.1888 | 123.0331 | 123.1934 | 123.0423 | 123.175 | 122.9874 | 76.7075 | 123.1934 | 123.0423 | 122.9874 | 123.0331 | 123.175 | -123.4726 | -46.3898
4479.7656 | 123.3215 | -68.1381 | 54.8447 | -0.11848 | 0.009942 | 0.0019013 | -0.00035676 | -0.011245 | -0.0062911 | -0.0032984 | 54.895 | 54.95 | -68.5364 | 55.1147 | 54.9271 | 54.9179 | 54.7852 | 55.1147 | 54.9545 | 8.5052 | -0.39825 | 0.10529 | 123.0331 | 123.2529 | 0.082397 | 76.6434 | 0.10986 | 123.4314 | 122.9233 | 123.2529 | 123.0652 | 123.0881 | 123.0331 | 123.0927 | 123.056 | 76.6434 | 123.0881 | 123.0331 | 123.056 | 123.0652 | 123.0927 | -123.381 | -46.3394
4480.7656 | 123.3261 | -68.1931 | 54.808 | 0.20195 | 0.012292 | 0.0051057 | 0.0041292 | -0.0086817 | -0.0071457 | -0.0030848 | 54.8859 | 54.9225 | -68.5364 | 55.0735 | 54.8492 | 54.8538 | 54.7073 | 55.0003 | 54.8996 | 8.4961 | -0.34332 | 0.11444 | 123.0789 | 123.2666 | 0.041199 | 76.6891 | 0.091553 | 123.4222 | 122.9004 | 123.1934 | 123.0423 | 123.1155 | 123.0789 | 123.0927 | 123.0469 | 76.6891 | 123.1155 | 123.0789 | 123.0469 | 123.0423 | 123.0927 | -123.3444 | -46.312
4481.7812 | 123.262 | -68.1885 | 54.8676 | -0.13374 | 0.012292 | 0.0031831 | 0.010324 | -0.011672 | -0.0094955 | -0.0028712 | 54.8676 | 54.9911 | -68.6096 | 55.1056 | 54.8538 | 54.8264 | 54.8813 | 55.0232 | 54.9728 | 8.4915 | -0.42114 | 0.1236 | 123.056 | 123.2941 | -0.013733 | 76.68 | 0.10529 | 123.4772 | 123.0698 | 123.2117 | 123.0423 | 123.1796 | 123.056 | 123.1613 | 123.0148 | 76.68 | 123.1796 | 123.056 | 123.0148 | 123.0423 | 123.1613 | -123.4772 | -46.376
4482.7812 | 123.317 | -68.161 | 54.8355 | 0.087509 | 0.010583 | 0.0019013 | 0.0015658 | -0.011031 | -0.010564 | -0.0037256 | 54.8355 | 54.9225 | -68.5593 | 55.0964 | 54.8401 | 54.8355 | 54.7531 | 55.0323 | 54.9042 | 8.4961 | -0.39825 | 0.086975 | 122.9965 | 123.2574 | 0.004578 | 76.6571 | 0.068665 | 123.3948 | 122.9141 | 123.1934 | 123.0011 | 123.0835 | 122.9965 | 123.0652 | 122.9965 | 76.6571 | 123.0835 | 122.9965 | 122.9965 | 123.0011 | 123.0652 | -123.3948 | -46.3394
4483.7812 | 123.317 | -68.1931 | 54.8264 | 0.14092 | 0.011651 | 0.0042511 | 0.0017794 | -0.010604 | -0.0062911 | -0.0030848 | 54.8355 | 54.9179 | -68.573 | 55.0644 | 54.8538 | 54.8538 | 54.9179 | 55.1193 | 54.9179 | 8.4915 | -0.37994 | 0.091553 | 123.0286 | 123.2574 | 0.027466 | 76.6846 | 0.091553 | 123.4085 | 123.111 | 123.3124 | 123.0469 | 123.111 | 123.0286 | 123.111 | 123.0469 | 76.6846 | 123.111 | 123.0286 | 123.0469 | 123.0469 | 123.111 | -123.3994 | -46.3348
4484.7656 | 123.3261 | -68.1381 | 54.8721 | 0.034104 | 0.013574 | 0.0053193 | 0.0049838 | -0.012313 | -0.0077865 | -0.0030848 | 54.9225 | 54.9454 | -68.5593 | 55.1422 | 54.9225 | 54.9179 | 54.7943 | 55.1102 | 54.9042 | 8.4915 | -0.42114 | 0.073243 | 123.0606 | 123.2803 | 0.050354 | 76.6296 | 0.032044 | 123.4818 | 122.9324 | 123.2483 | 123.0606 | 123.0835 | 123.0606 | 123.0423 | 123.056 | 76.6296 | 123.0835 | 123.0606 | 123.056 | 123.0606 | 123.0423 | -123.4314 | -46.3806
4485.7656 | 123.2849 | -68.1839 | 54.8492 | 0.11803 | 0.011865 | 0.0061737 | -0.00099756 | -0.0086817 | -0.0041549 | -0.0020166 | 54.8492 | 54.9179 | -68.5501 | 55.0461 | 54.8355 | 54.863 | 54.7714 | 55.0278 | 54.9271 | 8.4915 | -0.36621 | 0.068665 | 123.0331 | 123.23 | -0.013733 | 76.6754 | 0.07782 | 123.3994 | 122.9553 | 123.2117 | 123.0194 | 123.1018 | 123.0331 | 123.111 | 123.0469 | 76.6754 | 123.1018 | 123.0331 | 123.0469 | 123.0194 | 123.111 | -123.3994 | -46.3577
4486.7656 | 123.317 | -68.161 | 54.8447 | 0.041733 | 0.010156 | 0.0059601 | 7.0444e-05 | -0.011245 | -0.0062911 | -0.0028712 | 54.8584 | 54.9362 | -68.5593 | 55.0919 | 54.8904 | 54.8721 | 54.7943 | 55.0644 | 54.9088 | 8.4961 | -0.39825 | 0.091552 | 123.0194 | 123.2529 | 0.045776 | 76.6571 | 0.064086 | 123.4177 | 122.9553 | 123.2254 | 123.0515 | 123.0972 | 123.0194 | 123.0698 | 123.0331 | 76.6571 | 123.0972 | 123.0194 | 123.0331 | 123.0515 | 123.0698 | -123.4039 | -46.3486
4487.7656 | 123.3398 | -68.1564 | 54.8355 | -0.04982 | 0.010796 | 0.0083099 | -0.00014316 | -0.0099633 | -0.0071457 | -0.00030759 | 54.8904 | 54.9316 | -68.5501 | 55.1285 | 54.9133 | 54.895 | 54.7714 | 55.0781 | 54.9088 | 8.5007 | -0.39368 | 0.096131 | 123.0469 | 123.2849 | 0.07782 | 76.6571 | 0.073242 | 123.4406 | 122.9279 | 123.2346 | 123.0698 | 123.0881 | 123.0469 | 123.0652 | 123.0515 | 76.6571 | 123.0881 | 123.0469 | 123.0515 | 123.0698 | 123.0652 | -123.3856 | -46.3348
4488.7812 | 123.317 | -68.1793 | 54.8447 | -0.0040434 | 0.011651 | -0.0013031 | 0.0015658 | -0.010391 | -0.0080001 | -0.0026574 | 54.8721 | 54.9408 | -68.5684 | 55.1376 | 54.9133 | 54.8996 | 54.7623 | 55.0919 | 54.9179 | 8.4915 | -0.3891 | 0.09613 | 123.0515 | 123.317 | 0.068664 | 76.6708 | 0.073242 | 123.4406 | 122.9416 | 123.2712 | 123.0927 | 123.1201 | 123.0515 | 123.0972 | 123.0789 | 76.6708 | 123.1201 | 123.0515 | 123.0789 | 123.0927 | 123.0972 | -123.4131 | -46.3531
4489.7812 | 123.2162 | -68.2297 | 54.8904 | -0.072708 | 0.016351 | 0.0087373 | 0.011179 | -0.0086817 | -0.0041549 | -0.001803 | 54.9042 | 55.0415 | -68.5822 | 55.0278 | 54.776 | 54.7577 | 54.8538 | 54.9225 | 54.9271 | 8.4869 | -0.35248 | 0.15106 | 123.1338 | 123.2574 | -0.11444 | 76.7166 | 0.036621 | 123.4863 | 123.0835 | 123.1522 | 123.0057 | 123.2712 | 123.1338 | 123.1567 | 122.9874 | 76.7166 | 123.2712 | 123.1338 | 122.9874 | 123.0057 | 123.1567 | -123.4726 | -46.4035
4490.7812 | 123.2895 | -68.1793 | 54.8492 | 0.1104 | 0.013146 | 0.0061737 | 0.00028404 | -0.011459 | -0.0047957 | -0.0032984 | 54.9637 | 54.95 | -68.5684 | 55.0919 | 54.8721 | 54.8447 | 54.7897 | 55.0232 | 54.895 | 8.4869 | -0.3891 | 0.10071 | 123.143 | 123.2712 | 0.022888 | 76.6663 | 0.045777 | 123.5321 | 122.9691 | 123.2025 | 123.0515 | 123.1293 | 123.143 | 123.0743 | 123.024 | 76.6663 | 123.1293 | 123.143 | 123.024 | 123.0515 | 123.0743 | -123.4177 | -46.3623
4491.7656 | 123.3032 | -68.2022 | 54.8538 | 0.095139 | 0.012078 | 0.0055329 | 0.0034884 | -0.011886 | -0.0065047 | -0.0022302 | 54.8264 | 54.95 | -68.5822 | 55.0552 | 54.8447 | 54.8355 | 54.7852 | 54.9957 | 54.8859 | 8.4961 | -0.37994 | 0.09613 | 123.0286 | 123.2574 | -0.009155 | 76.6983 | 0.032043 | 123.4085 | 122.9874 | 123.1979 | 123.0469 | 123.1522 | 123.0286 | 123.0881 | 123.0377 | 76.6983 | 123.1522 | 123.0286 | 123.0377 | 123.0469 | 123.0881 | -123.436 | -46.3577
4492.7656 | 123.2895 | -68.1931 | 54.8676 | 0.14854 | 0.011224 | 0.0051057 | 0.00071144 | -0.011245 | -0.0065047 | -0.0015894 | 54.8355 | 54.9316 | -68.5684 | 55.0735 | 54.8492 | 54.8447 | 54.7714 | 55.0186 | 54.9179 | 8.5007 | -0.37537 | 0.064087 | 123.0286 | 123.2666 | -0.018311 | 76.6937 | 0.050354 | 123.4039 | 122.9645 | 123.2117 | 123.0423 | 123.1247 | 123.0286 | 123.111 | 123.0377 | 76.6937 | 123.1247 | 123.0286 | 123.0377 | 123.0423 | 123.111 | -123.436 | -46.3669
4493.7812 | 123.3078 | -68.2068 | 54.8721 | 0.11803 | 0.011224 | 0.0033967 | 0.00092504 | -0.011031 | -0.0069321 | -0.0026574 | 54.8264 | 54.95 | -68.5593 | 55.0781 | 54.8767 | 54.8721 | 54.7806 | 55.0369 | 54.895 | 8.4961 | -0.35248 | 0.07782 | 123.0331 | 123.2849 | 0.004578 | 76.7029 | 0.022889 | 123.3856 | 122.9874 | 123.2437 | 123.0835 | 123.1567 | 123.0331 | 123.1018 | 123.0789 | 76.7029 | 123.1567 | 123.0331 | 123.0789 | 123.0835 | 123.1018 | -123.4314 | -46.376
4494.7656 | 123.3444 | -68.1839 | 54.8264 | 0.27824 | 0.010583 | 0.0087373 | 0.0022066 | -0.0099633 | -0.0065047 | -0.0026574 | 54.8996 | 54.9133 | -68.5959 | 55.1102 | 54.9088 | 54.8904 | 54.6982 | 55.0415 | 54.8767 | 8.4961 | -0.41199 | 0.086975 | 123.0835 | 123.2941 | 0.082397 | 76.68 | 0.050354 | 123.4955 | 122.8821 | 123.2254 | 123.0927 | 123.0972 | 123.0835 | 123.0606 | 123.0743 | 76.68 | 123.0972 | 123.0835 | 123.0743 | 123.0927 | 123.0606 | -123.4222 | -46.3303
4495.7812 | 123.3765 | -68.1564 | 54.8447 | -0.04219 | 0.010369 | 0.0033967 | 0.0017794 | -0.010818 | -0.0047957 | -0.00052119 | 54.9042 | 54.9728 | -68.5455 | 55.1559 | 54.9271 | 54.9316 | 54.7714 | 55.1193 | 54.8767 | 8.5007 | -0.3891 | 0.12817 | 123.0606 | 123.3124 | 0.082397 | 76.6571 | 0.032043 | 123.4497 | 122.9279 | 123.2758 | 123.0835 | 123.1293 | 123.0606 | 123.0331 | 123.0881 | 76.6571 | 123.1293 | 123.0606 | 123.0881 | 123.0835 | 123.0331 | -123.3902 | -46.344
4496.7812 | 123.2849 | -68.1976 | 54.8904 | -0.2253 | 0.011437 | 0.0059601 | 0.001993 | -0.014663 | -0.0056503 | -0.0030848 | 54.9088 | 54.9911 | -68.5364 | 55.1193 | 54.8996 | 54.8767 | 54.8813 | 55.0735 | 54.9179 | 8.5007 | -0.33875 | 0.10071 | 123.1064 | 123.317 | 0.009155 | 76.6983 | 0.027466 | 123.4451 | 123.0789 | 123.2712 | 123.0972 | 123.1888 | 123.1064 | 123.1155 | 123.0743 | 76.6983 | 123.1888 | 123.1064 | 123.0743 | 123.0972 | 123.1155 | -123.4268 | -46.3898
4497.7656 | 123.2895 | -68.1839 | 54.8401 | 0.13329 | 0.011651 | 0.0014741 | 0.0022066 | -0.012313 | -0.0062911 | -0.0022302 | 54.8401 | 54.9316 | -68.573 | 55.0735 | 54.8447 | 54.8447 | 54.7806 | 55.0003 | 54.8813 | 8.4961 | -0.3891 | 0.091553 | 123.024 | 123.2574 | 0.004578 | 76.68 | 0.041199 | 123.4131 | 122.9645 | 123.1842 | 123.0286 | 123.1155 | 123.024 | 123.0652 | 123.0286 | 76.68 | 123.1155 | 123.024 | 123.0286 | 123.0286 | 123.0652 | -123.4131 | -46.344
4498.7656 | 123.2849 | -68.1747 | 54.863 | 0.14092 | 0.0097284 | 0.0046783 | 0.0024202 | -0.011672 | -0.0037277 | -0.0024438 | 54.8401 | 54.9454 | -68.573 | 55.0644 | 54.8676 | 54.8309 | 54.776 | 55.0003 | 54.9179 | 8.4915 | -0.39825 | 0.082398 | 123.0148 | 123.2391 | 0.004578 | 76.6663 | 0.054932 | 123.4131 | 122.9507 | 123.175 | 123.0423 | 123.1201 | 123.0148 | 123.0927 | 123.0057 | 76.6663 | 123.1201 | 123.0148 | 123.0057 | 123.0423 | 123.0927 | -123.436 | -46.3715
4499.7656 | 123.2941 | -68.2068 | 54.8538 | 0.07988 | 0.01101 | 0.0051057 | 0.0030612 | -0.011031 | -0.0060775 | -0.0037256 | 54.8264 | 54.9454 | -68.5776 | 55.069 | 54.8447 | 54.8538 | 54.7668 | 54.9957 | 54.8996 | 8.4915 | -0.37079 | 0.091553 | 123.0331 | 123.2758 | -0.009155 | 76.6983 | 0.045776 | 123.4039 | 122.9736 | 123.2025 | 123.0515 | 123.1522 | 123.0331 | 123.1064 | 123.0606 | 76.6983 | 123.1522 | 123.0331 | 123.0606 | 123.0515 | 123.1064 | -123.4314 | -46.3623
4500.7656 | 123.3215 | -68.1793 | 54.8309 | 0.1104 | 0.011224 | 0.0029693 | 0.0077608 | -0.0097497 | -0.0075729 | -0.0022302 | 54.8904 | 54.9316 | -68.5867 | 55.1102 | 54.8904 | 54.8767 | 54.689 | 55.0278 | 54.8996 | 8.5007 | -0.40741 | 0.10071 | 123.0698 | 123.2895 | 0.059509 | 76.68 | 0.068664 | 123.4772 | 122.8683 | 123.2071 | 123.0698 | 123.111 | 123.0698 | 123.0789 | 123.056 | 76.68 | 123.111 | 123.0698 | 123.056 | 123.0698 | 123.0789 | -123.4177 | -46.3303
4501.7969 | 123.2986 | -68.1839 | 54.863 | 0.1104 | 0.012719 | 0.0014741 | 7.0444e-05 | -0.011672 | -0.0043685 | -0.0030848 | 54.8218 | 54.9179 | -68.5822 | 55.0415 | 54.8676 | 54.8401 | 54.8126 | 55.0186 | 54.8996 | 8.4961 | -0.39825 | 0.054932 | 123.0057 | 123.2254 | 0.004578 | 76.68 | 0.036621 | 123.4039 | 122.9965 | 123.2025 | 123.0515 | 123.1018 | 123.0057 | 123.0835 | 123.024 | 76.68 | 123.1018 | 123.0057 | 123.024 | 123.0515 | 123.0835 | -123.4451 | -46.3669
4502.7812 | 123.3078 | -68.1747 | 54.8355 | 0.14092 | 0.01336 | 0.0025421 | 0.0032748 | -0.012954 | -0.0060775 | -0.0024438 | 54.8264 | 54.9179 | -68.5776 | 55.069 | 54.8538 | 54.8492 | 54.7897 | 55.0186 | 54.8996 | 8.4961 | -0.40283 | 0.082398 | 123.0011 | 123.2437 | 0.018311 | 76.6708 | 0.064087 | 123.4039 | 122.9645 | 123.1934 | 123.0286 | 123.0927 | 123.0011 | 123.0743 | 123.024 | 76.6708 | 123.0927 | 123.0011 | 123.024 | 123.0286 | 123.0743 | -123.4131 | -46.3394
4503.7812 | 123.3261 | -68.2159 | 54.8538 | 0.0035856 | 0.011224 | 0.0010467 | 0.0032748 | -0.011886 | -0.0065047 | -9.3992e-05 | 54.8447 | 54.9316 | -68.5776 | 55.0827 | 54.8767 | 54.863 | 54.7897 | 55.0507 | 54.8767 | 8.4961 | -0.36163 | 0.07782 | 123.0606 | 123.2986 | 0.022888 | 76.712 | 0.022888 | 123.4222 | 123.0057 | 123.2666 | 123.0927 | 123.1476 | 123.0606 | 123.0927 | 123.0789 | 76.712 | 123.1476 | 123.0606 | 123.0789 | 123.0927 | 123.0927 | -123.4314 | -46.3577
4504.7656 | 123.2941 | -68.1747 | 54.8218 | 0.43846 | 0.0095148 | 0.0016877 | 7.0444e-05 | -0.011245 | -0.0071457 | -0.0032984 | 54.7989 | 54.9271 | -68.5455 | 55.0827 | 54.8584 | 54.8492 | 54.7989 | 55.0232 | 54.895 | 8.4961 | -0.37079 | 0.10529 | 122.9736 | 123.2574 | 0.036621 | 76.6708 | 0.073243 | 123.3444 | 122.9736 | 123.1979 | 123.0331 | 123.1018 | 122.9736 | 123.0698 | 123.024 | 76.6708 | 123.1018 | 122.9736 | 123.024 | 123.0331 | 123.0698 | -123.3673 | -46.3257
4505.7656 | 123.3032 | -68.1976 | 54.8401 | -0.04219 | 0.011437 | 0.0038239 | 0.00028404 | -0.011245 | -0.0043685 | -0.0015894 | 54.8035 | 54.9271 | -68.5776 | 55.0735 | 54.8767 | 54.8492 | 54.7897 | 55.0323 | 54.9042 | 8.4961 | -0.37994 | 0.086975 | 123.0011 | 123.2712 | 0.036621 | 76.6937 | 0.064087 | 123.381 | 122.9874 | 123.23 | 123.0743 | 123.1247 | 123.0011 | 123.1018 | 123.0469 | 76.6937 | 123.1247 | 123.0011 | 123.0469 | 123.0743 | 123.1018 | -123.4177 | -46.344
4506.7656 | 123.3078 | -68.1839 | 54.8676 | 0.5529 | 0.011651 | 0.0063873 | 0.00028404 | -0.0088953 | -0.0069321 | -0.0022302 | 54.8126 | 54.9225 | -68.5455 | 55.069 | 54.8584 | 54.8492 | 54.7852 | 55.0186 | 54.9225 | 8.4915 | -0.36163 | 0.054931 | 122.9965 | 123.2529 | -0.009156 | 76.6754 | 0.054931 | 123.3582 | 122.9691 | 123.2025 | 123.0423 | 123.1064 | 122.9965 | 123.1064 | 123.0331 | 76.6754 | 123.1064 | 122.9965 | 123.0331 | 123.0423 | 123.1064 | -123.4131 | -46.376
4507.7656 | 123.3307 | -68.1931 | 54.8126 | 0.27061 | 0.010156 | 0.0038239 | 0.0077608 | -0.010818 | -0.0086411 | -0.0015894 | 54.9271 | 54.9088 | -68.573 | 55.1147 | 54.8676 | 54.895 | 54.6982 | 55.0323 | 54.8676 | 8.4915 | -0.37994 | 0.09613 | 123.1201 | 123.3078 | 0.054932 | 76.6846 | 0.054932 | 123.5001 | 122.8912 | 123.2254 | 123.0606 | 123.1018 | 123.1201 | 123.0606 | 123.0881 | 76.6846 | 123.1018 | 123.1201 | 123.0881 | 123.0606 | 123.0606 | -123.3856 | -46.3211
4508.7812 | 123.2895 | -68.1747 | 54.8492 | 0.087509 | 0.0088738 | 0.0036103 | 0.0022066 | -0.012527 | -0.0050095 | -0.0020166 | 54.8401 | 54.9225 | -68.5913 | 55.0552 | 54.8492 | 54.8447 | 54.7806 | 55.014 | 54.9042 | 8.4915 | -0.41656 | 0.073242 | 123.0148 | 123.23 | 0 | 76.6663 | 0.054932 | 123.4314 | 122.9553 | 123.1888 | 123.024 | 123.0972 | 123.0148 | 123.0789 | 123.0194 | 76.6663 | 123.0972 | 123.0148 | 123.0194 | 123.024 | 123.0789 | -123.4406 | -46.3577
4509.7812 | 123.3078 | -68.1931 | 54.8492 | 0.14092 | 0.010156 | -2.1336e-05 | 0.0022066 | -0.011031 | -0.0050095 | -0.00073479 | 54.8172 | 54.9225 | -68.5593 | 55.0598 | 54.8676 | 54.8401 | 54.776 | 55.014 | 54.895 | 8.4961 | -0.36621 | 0.073242 | 123.0103 | 123.2529 | 0.018311 | 76.6891 | 0.045777 | 123.3765 | 122.9691 | 123.2071 | 123.0606 | 123.1155 | 123.0103 | 123.0881 | 123.0331 | 76.6891 | 123.1155 | 123.0103 | 123.0331 | 123.0606 | 123.0881 | -123.4085 | -46.3531
4510.7812 | 123.317 | -68.2068 | 54.8538 | 0.13329 | 0.0097284 | 0.0048921 | 0.0017794 | -0.011459 | -0.0082137 | -0.0028712 | 54.8447 | 54.9225 | -68.5913 | 55.069 | 54.8401 | 54.8309 | 54.7897 | 55.0186 | 54.895 | 8.5007 | -0.38452 | 0.068664 | 123.0515 | 123.2758 | -0.013733 | 76.7075 | 0.041199 | 123.436 | 122.9965 | 123.2254 | 123.0469 | 123.1293 | 123.0515 | 123.1018 | 123.0377 | 76.7075 | 123.1293 | 123.0515 | 123.0377 | 123.0469 | 123.1018 | -123.4451 | -46.3531
4511.7656 | 123.3353 | -68.1747 | 54.8447 | -0.019302 | 0.0084466 | 0.0042511 | 0.00028404 | -0.0099633 | -0.0058639 | -0.00458 | 54.863 | 54.9133 | -68.5684 | 55.1239 | 54.8904 | 54.8859 | 54.776 | 55.0781 | 54.8996 | 8.4961 | -0.39368 | 0.068664 | 123.0377 | 123.2986 | 0.045776 | 76.6708 | 0.054931 | 123.4314 | 122.9507 | 123.2529 | 123.0652 | 123.0881 | 123.0377 | 123.0743 | 123.0606 | 76.6708 | 123.0881 | 123.0377 | 123.0606 | 123.0652 | 123.0743 | -123.4131 | -46.3486
4512.7656 | 123.349 | -68.1747 | 54.8492 | 0.087509 | 0.009942 | 0.0027557 | -0.001425 | -0.010391 | -0.0073593 | -0.0011622 | 54.8538 | 54.9133 | -68.5501 | 55.1147 | 54.8996 | 54.9088 | 54.7806 | 55.0919 | 54.9179 | 8.4869 | -0.37537 | 0.064087 | 123.0286 | 123.2895 | 0.050354 | 76.6617 | 0.068665 | 123.4039 | 122.9553 | 123.2666 | 123.0743 | 123.0881 | 123.0286 | 123.0927 | 123.0835 | 76.6617 | 123.0881 | 123.0286 | 123.0835 | 123.0743 | 123.0927 | -123.3994 | -46.3623
4513.7656 | 123.3582 | -68.1931 | 54.8355 | 0.0035856 | 0.011865 | 0.0053193 | 0.00071144 | -0.0121 | -0.0075729 | -0.003512 | 54.863 | 54.9042 | -68.5776 | 55.1147 | 54.8904 | 54.8859 | 54.7806 | 55.0781 | 54.9088 | 8.5007 | -0.38452 | 0.068665 | 123.056 | 123.3078 | 0.054932 | 76.6937 | 0.073242 | 123.4406 | 122.9736 | 123.2712 | 123.0835 | 123.0972 | 123.056 | 123.1018 | 123.0789 | 76.6937 | 123.0972 | 123.056 | 123.0789 | 123.0835 | 123.1018 | -123.4131 | -46.3348
4514.7656 | 123.317 | -68.1656 | 54.8492 | 0.21721 | 0.010583 | 0.0036103 | 0.0017794 | -0.011672 | -0.0054367 | -9.3992e-05 | 54.8859 | 54.8904 | -68.605 | 55.0919 | 54.8676 | 54.8447 | 54.7348 | 55.0095 | 54.863 | 8.4961 | -0.43945 | 0.041199 | 123.0515 | 123.2574 | 0.018311 | 76.6617 | 0.013733 | 123.4909 | 122.9004 | 123.175 | 123.0331 | 123.056 | 123.0515 | 123.0286 | 123.0103 | 76.6617 | 123.056 | 123.0515 | 123.0103 | 123.0331 | 123.0286 | -123.4543 | -46.3531
4515.7812 | 123.3261 | -68.2068 | 54.8447 | 0.14092 | 0.0090876 | 0.0059601 | 0.001993 | -0.0095361 | -0.0056503 | -0.0041528 | 54.8218 | 54.9179 | -68.5776 | 55.0507 | 54.8401 | 54.8538 | 54.7806 | 55.0232 | 54.895 | 8.4961 | -0.37079 | 0.073242 | 123.0286 | 123.2574 | -0.004578 | 76.7029 | 0.050354 | 123.3994 | 122.9874 | 123.23 | 123.0469 | 123.1247 | 123.0286 | 123.1018 | 123.0606 | 76.7029 | 123.1247 | 123.0286 | 123.0606 | 123.0469 | 123.1018 | -123.4222 | -46.3486
4516.7812 | 123.3078 | -68.1885 | 54.8309 | 0.59868 | 0.010156 | 0.00061946 | 7.0444e-05 | -0.012954 | -0.0062911 | 0.00011961 | 54.8584 | 54.9179 | -68.5638 | 55.0781 | 54.8538 | 54.8584 | 54.7806 | 55.0186 | 54.9133 | 8.4961 | -0.37537 | 0.086975 | 123.0469 | 123.2666 | 0.022888 | 76.6846 | 0.082397 | 123.4222 | 122.9691 | 123.2071 | 123.0423 | 123.1064 | 123.0469 | 123.1018 | 123.0469 | 76.6846 | 123.1064 | 123.0469 | 123.0469 | 123.0423 | 123.1018 | -123.3948 | -46.3348
4517.7812 | 123.2941 | -68.1885 | 54.8355 | -1.4231 | 0.010796 | 0.0029693 | -0.00099756 | -0.011886 | -0.0060775 | -0.0013758 | 54.863 | 54.9316 | -68.5822 | 55.0873 | 54.8447 | 54.8309 | 54.7943 | 55.0415 | 54.8721 | 8.4961 | -0.39368 | 0.096131 | 123.0515 | 123.2758 | 0.009156 | 76.6846 | 0.036621 | 123.4451 | 122.9828 | 123.23 | 123.0331 | 123.1201 | 123.0515 | 123.0606 | 123.0194 | 76.6846 | 123.1201 | 123.0515 | 123.0194 | 123.0331 | 123.0606 | -123.4177 | -46.3394
4518.7656 | 123.3444 | -68.1519 | 54.8447 | 0.011215 | 0.0090876 | 0.0023285 | 0.00092504 | -0.011459 | -0.0054367 | -0.00094839 | 54.8996 | 54.9225 | -68.5501 | 55.1559 | 54.9408 | 54.9179 | 54.776 | 55.1102 | 54.9088 | 8.5007 | -0.39826 | 0.077819 | 123.0515 | 123.3078 | 0.09613 | 76.6525 | 0.064086 | 123.4497 | 122.9279 | 123.262 | 123.0927 | 123.0743 | 123.0515 | 123.0606 | 123.0698 | 76.6525 | 123.0743 | 123.0515 | 123.0698 | 123.0927 | 123.0606 | -123.3948 | -46.344
4519.7656 | 123.3444 | -68.1519 | 54.8447 | -0.080337 | 0.0088738 | 0.0036103 | -0.00035676 | -0.011459 | -0.0060775 | -0.0030848 | 54.895 | 54.9133 | -68.541 | 55.1285 | 54.9408 | 54.9179 | 54.7623 | 55.0827 | 54.9133 | 8.4961 | -0.3891 | 0.068664 | 123.0469 | 123.2803 | 0.09613 | 76.6479 | 0.068664 | 123.436 | 122.9141 | 123.2346 | 123.0927 | 123.0652 | 123.0469 | 123.0652 | 123.0698 | 76.6479 | 123.0652 | 123.0469 | 123.0698 | 123.0927 | 123.0652 | -123.3856 | -46.3486
4520.7656 | 123.3673 | -68.1519 | 54.8355 | -0.011673 | 0.010369 | 0.0029693 | -0.00014316 | -0.0099633 | -0.0071457 | -0.0028712 | 54.8996 | 54.9179 | -68.5593 | 55.1239 | 54.9179 | 54.8996 | 54.7897 | 55.1056 | 54.8996 | 8.4961 | -0.40741 | 0.082398 | 123.0515 | 123.2758 | 0.082398 | 76.6479 | 0.064087 | 123.4589 | 122.9416 | 123.2574 | 123.0698 | 123.0698 | 123.0515 | 123.0515 | 123.0515 | 76.6479 | 123.0698 | 123.0515 | 123.0515 | 123.0698 | 123.0515 | -123.3948 | -46.3394
4521.7656 | 123.2758 | -68.2159 | 54.8309 | 0.22484 | 0.011437 | 0.0042511 | 0.0024202 | -0.0091089 | -0.0069321 | -0.0037256 | 54.8584 | 54.895 | -68.5684 | 55.0735 | 54.8584 | 54.8538 | 54.7623 | 55.0232 | 54.9225 | 8.4915 | -0.35248 | 0.064087 | 123.0743 | 123.2895 | 0.027465 | 76.7075 | 0.091552 | 123.4268 | 122.9782 | 123.2391 | 123.0743 | 123.111 | 123.0743 | 123.1384 | 123.0698 | 76.7075 | 123.111 | 123.0743 | 123.0698 | 123.0743 | 123.1384 | -123.3994 | -46.3394
4522.7812 | 123.3032 | -68.1747 | 54.8401 | 0.095139 | 0.01101 | 0.0044647 | 0.00071144 | -0.011459 | -0.0047957 | -0.001803 | 54.8264 | 54.9088 | -68.5501 | 55.0781 | 54.8584 | 54.8492 | 54.8401 | 55.2017 | 54.9362 | 8.4961 | -0.37537 | 0.068664 | 123.0011 | 123.2529 | 0.01831 | 76.6708 | 0.09613 | 123.3765 | 123.0148 | 123.3765 | 123.0331 | 123.0835 | 123.0011 | 123.111 | 123.024 | 76.6708 | 123.0835 | 123.0011 | 123.024 | 123.0331 | 123.111 | -123.3902 | -46.344
4523.7812 | 123.3398 | -68.1839 | 54.8355 | 0.056992 | 0.0075922 | 0.00019226 | 0.0013522 | -0.011245 | -0.0077865 | -0.0026574 | 54.8447 | 54.9042 | -68.5318 | 55.1056 | 54.8813 | 54.8813 | 54.7943 | 55.069 | 54.9225 | 8.4961 | -0.3479 | 0.068665 | 123.0286 | 123.2895 | 0.045777 | 76.68 | 0.086975 | 123.3765 | 122.9782 | 123.2529 | 123.0652 | 123.0881 | 123.0286 | 123.1064 | 123.0652 | 76.68 | 123.0881 | 123.0286 | 123.0652 | 123.0652 | 123.1064 | -123.3673 | -46.3394
4524.7812 | 123.3261 | -68.1885 | 54.8401 | 0.1104 | 0.0075922 | 0.0023285 | 7.0444e-05 | -0.011245 | -0.0069321 | -0.0013758 | 54.8492 | 54.9088 | -68.5638 | 55.0964 | 54.9088 | 54.8584 | 54.7897 | 55.0415 | 54.9042 | 8.5007 | -0.37537 | 0.068664 | 123.0377 | 123.2849 | 0.068664 | 76.6891 | 0.064087 | 123.4131 | 122.9782 | 123.23 | 123.0972 | 123.0972 | 123.0377 | 123.0927 | 123.0469 | 76.6891 | 123.0972 | 123.0377 | 123.0469 | 123.0972 | 123.0927 | -123.4039 | -46.3394
4525.7656 | 123.3582 | -68.1747 | 54.8492 | -0.04219 | 0.0088738 | 0.0014741 | 7.0444e-05 | -0.0084681 | -0.0071457 | -0.0011622 | 54.9179 | 54.9133 | -68.5684 | 55.1834 | 54.9591 | 54.9316 | 54.776 | 55.1468 | 54.9179 | 8.4915 | -0.39368 | 0.064087 | 123.0927 | 123.3582 | 0.10986 | 76.6663 | 0.068665 | 123.4863 | 122.9507 | 123.3215 | 123.1338 | 123.0881 | 123.0927 | 123.0927 | 123.1064 | 76.6663 | 123.0881 | 123.0927 | 123.1064 | 123.1338 | 123.0927 | -123.4177 | -46.3577
4526.7656 | 123.3536 | -68.1564 | 54.863 | -0.034561 | 0.0093012 | 0.0048921 | 0.00092504 | -0.011459 | -0.0065047 | -0.0026574 | 54.9133 | 54.9042 | -68.5501 | 55.1697 | 54.9316 | 54.9271 | 54.7668 | 55.1422 | 54.9179 | 8.5007 | -0.39368 | 0.041199 | 123.0698 | 123.3261 | 0.068665 | 76.6571 | 0.054932 | 123.4634 | 122.9233 | 123.2986 | 123.0881 | 123.0606 | 123.0698 | 123.0743 | 123.0835 | 76.6571 | 123.0606 | 123.0698 | 123.0835 | 123.0881 | 123.0743 | -123.4131 | -46.3623
4527.7656 | 123.3582 | -68.1519 | 54.8676 | -0.04219 | 0.012292 | -0.0032257 | 0.0015658 | -0.011245 | -0.0082137 | -0.0026574 | 54.9179 | 54.9225 | -68.5638 | 55.1697 | 54.9454 | 54.9362 | 54.7623 | 55.1239 | 54.9316 | 8.4961 | -0.41199 | 0.054931 | 123.0698 | 123.3215 | 0.07782 | 76.6479 | 0.064087 | 123.4818 | 122.9141 | 123.2758 | 123.0972 | 123.0743 | 123.0698 | 123.0835 | 123.0881 | 76.6479 | 123.0743 | 123.0698 | 123.0881 | 123.0972 | 123.0835 | -123.4314 | -46.3715
4528.7656 | 123.2986 | -68.1793 | 54.863 | 0.1638 | 0.0097284 | 0.0023285 | 0.002634 | -0.0082545 | -0.0075729 | -0.0013758 | 54.863 | 54.8996 | -68.5638 | 55.0735 | 54.8721 | 54.8401 | 54.7623 | 55.014 | 54.9042 | 8.4824 | -0.38452 | 0.036621 | 123.0423 | 123.2529 | 0.009155 | 76.6617 | 0.041199 | 123.4268 | 122.9416 | 123.1934 | 123.0515 | 123.0789 | 123.0423 | 123.0835 | 123.0194 | 76.6617 | 123.0789 | 123.0423 | 123.0194 | 123.0515 | 123.0835 | -123.4268 | -46.3806
4529.7812 | 123.349 | -68.1976 | 54.8309 | 0.28587 | 0.013574 | 0.0029693 | 0.0090426 | -0.010177 | -0.0071457 | -0.0020166 | 54.9225 | 54.95 | -68.5684 | 55.0964 | 54.8859 | 54.8721 | 54.7302 | 55.0232 | 54.8721 | 8.4961 | -0.37079 | 0.11902 | 123.1201 | 123.2941 | 0.054931 | 76.6937 | 0.041198 | 123.4909 | 122.9279 | 123.2208 | 123.0835 | 123.1476 | 123.1201 | 123.0698 | 123.0698 | 76.6937 | 123.1476 | 123.1201 | 123.0698 | 123.0835 | 123.0698 | -123.3994 | -46.3348
4530.7812 | 123.3078 | -68.1702 | 54.8538 | 0.026474 | 0.0097284 | 0.0014741 | -0.00057036 | -0.0099633 | -0.0071457 | -0.0028712 | 54.8447 | 54.9316 | -68.573 | 55.0919 | 54.9042 | 54.895 | 54.7989 | 55.069 | 54.8721 | 8.5098 | -0.40283 | 0.07782 | 123.0148 | 123.262 | 0.050354 | 76.68 | 0.01831 | 123.4177 | 122.9691 | 123.2391 | 123.0743 | 123.1018 | 123.0148 | 123.0423 | 123.0652 | 76.68 | 123.1018 | 123.0148 | 123.0652 | 123.0743 | 123.0423 | -123.4268 | -46.344
4531.7812 | 123.3215 | -68.1931 | 54.8401 | 0.026474 | 0.0097284 | 0.0048921 | 0.00028404 | -0.011245 | -0.0058639 | -0.0024438 | 54.8584 | 54.9316 | -68.5867 | 55.101 | 54.9088 | 54.8813 | 54.7897 | 55.0598 | 54.9133 | 8.5098 | -0.39368 | 0.091553 | 123.0515 | 123.2941 | 0.068664 | 76.7029 | 0.073242 | 123.4451 | 122.9828 | 123.2529 | 123.1018 | 123.1247 | 123.0515 | 123.1064 | 123.0743 | 76.7029 | 123.1247 | 123.0515 | 123.0743 | 123.1018 | 123.1064 | -123.4268 | -46.3303
4532.7812 | 123.1979 | -68.1976 | 54.9133 | -0.15663 | 0.011651 | 0.0029693 | 0.0051974 | -0.0093225 | -0.0060775 | -0.0032984 | 54.9774 | 55.0232 | -68.5547 | 55.0323 | 54.8126 | 54.8035 | 54.9225 | 55.0003 | 54.9545 | 8.5052 | -0.35706 | 0.10986 | 123.175 | 123.23 | -0.10071 | 76.7029 | 0.041199 | 123.5321 | 123.1201 | 123.1979 | 123.0103 | 123.2208 | 123.175 | 123.1522 | 123.0011 | 76.7029 | 123.2208 | 123.175 | 123.0011 | 123.0103 | 123.1522 | -123.468 | -46.4081
4533.7656 | 123.3215 | -68.1931 | 54.8401 | 0.12566 | 0.012933 | 0.00083306 | 0.00028404 | -0.010391 | -0.0060775 | -0.003512 | 54.8309 | 54.9088 | -68.5638 | 55.069 | 54.8584 | 54.863 | 54.7806 | 55.0095 | 54.9133 | 8.4961 | -0.37079 | 0.068664 | 123.024 | 123.262 | 0.01831 | 76.6891 | 0.073242 | 123.3948 | 122.9736 | 123.2025 | 123.0515 | 123.1018 | 123.024 | 123.1064 | 123.056 | 76.6891 | 123.1018 | 123.024 | 123.056 | 123.0515 | 123.1064 | -123.4039 | -46.344
4534.7656 | 123.3078 | -68.2022 | 54.8492 | 0.17143 | 0.0093012 | 0.0016877 | 0.0032748 | -0.011672 | -0.0071457 | -0.0024438 | 54.8401 | 54.9225 | -68.5776 | 55.0598 | 54.8721 | 54.8355 | 54.7897 | 55.0186 | 54.895 | 8.4915 | -0.37537 | 0.073242 | 123.0423 | 123.262 | 0.022888 | 76.6937 | 0.045777 | 123.4177 | 122.9919 | 123.2208 | 123.0743 | 123.1247 | 123.0423 | 123.0972 | 123.0377 | 76.6937 | 123.1247 | 123.0423 | 123.0377 | 123.0743 | 123.0972 | -123.4268 | -46.3577
4535.7656 | 123.2941 | -68.2068 | 54.8492 | 0.15617 | 0.011437 | 0.0025421 | 0.0015658 | -0.0082545 | -0.0058639 | -0.001803 | 54.8538 | 54.9179 | -68.5776 | 55.0552 | 54.8538 | 54.8447 | 54.7806 | 55.0095 | 54.8904 | 8.5007 | -0.37079 | 0.068665 | 123.0606 | 123.262 | 0.004578 | 76.7075 | 0.041199 | 123.4314 | 122.9874 | 123.2162 | 123.0606 | 123.1247 | 123.0606 | 123.0972 | 123.0515 | 76.7075 | 123.1247 | 123.0606 | 123.0515 | 123.0606 | 123.0972 | -123.4268 | -46.3486
4536.7812 | 123.3261 | -68.1885 | 54.8584 | 0.10277 | 0.010583 | 0.0010467 | 0.00092504 | -0.010818 | -0.0054367 | -0.0013758 | 54.8401 | 54.9042 | -68.5638 | 55.1147 | 54.9088 | 54.8904 | 54.776 | 55.0644 | 54.9133 | 8.4915 | -0.37537 | 0.045777 | 123.0286 | 123.3032 | 0.050354 | 76.68 | 0.054932 | 123.4039 | 122.9645 | 123.2529 | 123.0972 | 123.0927 | 123.0286 | 123.1018 | 123.0789 | 76.68 | 123.0927 | 123.0286 | 123.0789 | 123.0972 | 123.1018 | -123.4222 | -46.3669
4537.7812 | 123.2346 | -68.1976 | 54.9179 | -0.11085 | 0.012292 | 0.0033967 | 0.0075472 | -0.011459 | -0.0043685 | -0.00458 | 54.8813 | 55.0323 | -68.5638 | 55.0919 | 54.8584 | 54.808 | 54.9454 | 55.0095 | 54.982 | 8.4961 | -0.36621 | 0.11444 | 123.0789 | 123.2895 | -0.05951 | 76.6937 | 0.064087 | 123.4451 | 123.143 | 123.2071 | 123.056 | 123.23 | 123.0789 | 123.1796 | 123.0057 | 76.6937 | 123.23 | 123.0789 | 123.0057 | 123.056 | 123.1796 | -123.4818 | -46.4218
4538.7656 | 123.2941 | -68.1839 | 54.8355 | 0.14092 | 0.011437 | 0.0014741 | 0.0011386 | -0.0093225 | -0.0073593 | -0.0024438 | 54.8355 | 54.9088 | -68.5822 | 55.0552 | 54.8721 | 54.8538 | 54.7714 | 55.0095 | 54.9179 | 8.4961 | -0.39825 | 0.073242 | 123.0194 | 123.2391 | 0.036621 | 76.68 | 0.082398 | 123.4177 | 122.9553 | 123.1934 | 123.056 | 123.0927 | 123.0194 | 123.1018 | 123.0377 | 76.68 | 123.0927 | 123.0194 | 123.0377 | 123.056 | 123.1018 | -123.4177 | -46.3394
4539.7656 | 123.3398 | -68.1702 | 54.8584 | 0.0035856 | 0.0095148 | -0.0010895 | 0.0028476 | -0.012313 | -0.0056503 | -0.0030848 | 54.8721 | 54.9316 | -68.573 | 55.1239 | 54.9133 | 54.9179 | 54.776 | 55.0964 | 54.9042 | 8.4915 | -0.40283 | 0.073243 | 123.0423 | 123.2941 | 0.054932 | 76.6617 | 0.045777 | 123.4451 | 122.9462 | 123.2666 | 123.0835 | 123.1018 | 123.0423 | 123.0743 | 123.0881 | 76.6617 | 123.1018 | 123.0423 | 123.0881 | 123.0835 | 123.0743 | -123.4314 | -46.3669
4540.7656 | 123.3398 | -68.1931 | 54.8309 | -0.019302 | 0.011437 | 0.0016877 | 0.00071144 | -0.010818 | -0.0054367 | -0.001803 | 54.8859 | 54.9225 | -68.5501 | 55.1331 | 54.9042 | 54.8996 | 54.776 | 55.0827 | 54.9179 | 8.5007 | -0.35706 | 0.091552 | 123.0789 | 123.3261 | 0.073242 | 76.6937 | 0.086975 | 123.436 | 122.9691 | 123.2758 | 123.0972 | 123.1155 | 123.0789 | 123.111 | 123.0927 | 76.6937 | 123.1155 | 123.0789 | 123.0927 | 123.0972 | 123.111 | -123.381 | -46.3303
4541.7656 | 123.3078 | -68.1885 | 54.8218 | 0.21721 | 0.012505 | 0.0019013 | 0.0034884 | -0.0069727 | -0.0067185 | -0.0020166 | 54.8859 | 54.895 | -68.6005 | 55.0735 | 54.8721 | 54.8447 | 54.7394 | 55.0095 | 54.9042 | 8.4961 | -0.41199 | 0.073243 | 123.0743 | 123.262 | 0.050354 | 76.6846 | 0.082398 | 123.4863 | 122.9279 | 123.1979 | 123.0606 | 123.0835 | 123.0743 | 123.0927 | 123.0331 | 76.6846 | 123.0835 | 123.0743 | 123.0331 | 123.0606 | 123.0927 | -123.4222 | -46.3257
4542.7812 | 123.3444 | -68.1747 | 54.8721 | 0.27824 | 0.011224 | 0.0012605 | 0.0024202 | -0.010818 | -0.0052231 | -0.0030848 | 54.9454 | 54.9179 | -68.5593 | 55.1422 | 54.9316 | 54.9225 | 54.7943 | 55.1239 | 54.9271 | 8.5007 | -0.38452 | 0.045777 | 123.1201 | 123.317 | 0.05951 | 76.6754 | 0.054932 | 123.5046 | 122.9691 | 123.2986 | 123.1064 | 123.0927 | 123.1201 | 123.1018 | 123.0972 | 76.6754 | 123.0927 | 123.1201 | 123.0972 | 123.1064 | 123.1018 | -123.4314 | -46.3715
4543.7812 | 123.2941 | -68.1793 | 54.8447 | 0.1104 | 0.0093012 | 0.0016877 | 7.0444e-05 | -0.0097497 | -0.0062911 | -0.0020166 | 54.8401 | 54.9088 | -68.5822 | 55.0644 | 54.8721 | 54.7943 | 54.9408 | 55.014 | 54.9454 | 8.4915 | -0.40283 | 0.064086 | 123.0194 | 123.2437 | 0.027465 | 76.6708 | 0.10071 | 123.4222 | 123.1201 | 123.1934 | 123.0515 | 123.0881 | 123.0194 | 123.1247 | 122.9736 | 76.6708 | 123.0881 | 123.0194 | 122.9736 | 123.0515 | 123.1247 | -123.4268 | -46.3531
4544.7812 | 123.3124 | -68.2022 | 54.8767 | 0.14092 | 0.01101 | 0.0059601 | 0.00049764 | -0.0091089 | -0.0065047 | -0.0043664 | 54.8447 | 54.9042 | -68.5959 | 55.0552 | 54.863 | 54.8401 | 54.7806 | 55.014 | 54.8996 | 8.4961 | -0.39368 | 0.027466 | 123.0469 | 123.2574 | -0.013733 | 76.6983 | 0.022888 | 123.4406 | 122.9828 | 123.2162 | 123.0652 | 123.1064 | 123.0469 | 123.1018 | 123.0423 | 76.6983 | 123.1064 | 123.0469 | 123.0423 | 123.0652 | 123.1018 | -123.4726 | -46.3806
4545.7812 | 123.3078 | -68.2022 | 54.8401 | 0.15617 | 0.012505 | 0.0014741 | 0.0028476 | -0.010177 | -0.0071457 | -0.0015894 | 54.8538 | 54.895 | -68.5867 | 55.0781 | 54.8492 | 54.8401 | 54.7897 | 55.014 | 54.9042 | 8.5007 | -0.38452 | 0.054932 | 123.056 | 123.2803 | 0.009155 | 76.7029 | 0.064087 | 123.4406 | 122.9919 | 123.2162 | 123.0515 | 123.0972 | 123.056 | 123.1064 | 123.0423 | 76.7029 | 123.0972 | 123.056 | 123.0423 | 123.0515 | 123.1064 | -123.4268 | -46.3394
4546.7656 | 123.3307 | -68.1931 | 54.863 | 0.072251 | 0.0093012 | 0.00040586 | -0.0012112 | -0.011459 | -0.0039413 | -0.0026574 | 54.8492 | 54.9316 | -68.5638 | 55.0964 | 54.8859 | 54.8721 | 54.7989 | 55.0461 | 54.895 | 8.5052 | -0.37079 | 0.068665 | 123.0423 | 123.2895 | 0.022888 | 76.6983 | 0.032044 | 123.4131 | 122.9919 | 123.2391 | 123.0789 | 123.1247 | 123.0423 | 123.0881 | 123.0652 | 76.6983 | 123.1247 | 123.0423 | 123.0652 | 123.0789 | 123.0881 | -123.4268 | -46.3577
4547.7812 | 123.2346 | -68.2068 | 54.8996 | 0.69023 | 0.013787 | 0.0074555 | 0.0058382 | -0.011245 | -0.0084273 | -0.0037256 | 54.8035 | 54.9957 | -68.5913 | 55.0735 | 54.8355 | 54.8126 | 54.9774 | 54.9911 | 54.9866 | 8.5007 | -0.38452 | 0.096131 | 123.0103 | 123.2803 | -0.064087 | 76.7075 | 0.086975 | 123.3948 | 123.1842 | 123.1979 | 123.0423 | 123.2025 | 123.0103 | 123.1934 | 123.0194 | 76.7075 | 123.2025 | 123.0103 | 123.0194 | 123.0423 | 123.1934 | -123.4909 | -46.3989
4548.7656 | 123.3353 | -68.1976 | 54.8401 | 0.2935 | 0.012292 | 0.0027557 | 0.0066928 | -0.0095361 | -0.0060775 | -0.0030848 | 54.9271 | 54.9133 | -68.5822 | 55.1056 | 54.8904 | 54.8859 | 54.6844 | 55.0415 | 54.9042 | 8.5007 | -0.38452 | 0.073242 | 123.1247 | 123.3032 | 0.050354 | 76.6983 | 0.064087 | 123.5092 | 122.8821 | 123.2391 | 123.0881 | 123.111 | 123.1247 | 123.1018 | 123.0835 | 76.6983 | 123.111 | 123.1247 | 123.0835 | 123.0881 | 123.1018 | -123.4222 | -46.3394
4549.7656 | 123.3307 | -68.1793 | 54.7989 | 0.27824 | 0.011224 | 0.0068147 | 0.0039156 | -0.010391 | -0.0054367 | -0.0026574 | 54.8447 | 54.8859 | -68.6234 | 55.1285 | 54.8996 | 54.8904 | 54.7302 | 55.0415 | 54.8721 | 8.4961 | -0.44403 | 0.086975 | 123.024 | 123.3078 | 0.10071 | 76.6754 | 0.073242 | 123.468 | 122.9095 | 123.2208 | 123.0789 | 123.0652 | 123.024 | 123.0515 | 123.0698 | 76.6754 | 123.0652 | 123.024 | 123.0698 | 123.0789 | 123.0515 | -123.4222 | -46.3028
4550.7812 | 123.3032 | -68.2205 | 54.8538 | 0.19432 | 0.010583 | 0.0036103 | 0.0028476 | -0.0091089 | -0.0080001 | -0.0024438 | 54.8401 | 54.9088 | -68.5638 | 55.0644 | 54.8492 | 54.8492 | 54.7714 | 55.0232 | 54.8813 | 8.4915 | -0.34332 | 0.054931 | 123.0606 | 123.2849 | -0.004578 | 76.712 | 0.027466 | 123.4039 | 122.9919 | 123.2437 | 123.0698 | 123.1293 | 123.0606 | 123.1018 | 123.0698 | 76.712 | 123.1293 | 123.0606 | 123.0698 | 123.0698 | 123.1018 | -123.4177 | -46.3623
4551.7812 | 123.3261 | -68.2022 | 54.8492 | 0.21721 | 0.011651 | 0.0080963 | 0.0028476 | -0.0121 | -0.0050095 | -0.0022302 | 54.8584 | 54.9088 | -68.5638 | 55.0644 | 54.8538 | 54.863 | 54.7531 | 55.0095 | 54.8721 | 8.4869 | -0.36163 | 0.059509 | 123.0606 | 123.2666 | 0.004578 | 76.6891 | 0.022888 | 123.4222 | 122.9553 | 123.2117 | 123.056 | 123.111 | 123.0606 | 123.0743 | 123.0652 | 76.6891 | 123.111 | 123.0606 | 123.0652 | 123.056 | 123.0743 | -123.4131 | -46.3623
4552.7656 | 123.3078 | -68.1976 | 54.8492 | 0.24773 | 0.009942 | 0.0044647 | 0.0030612 | -0.012954 | -0.0062911 | -0.001803 | 54.8401 | 54.9316 | -68.5684 | 55.0781 | 54.8813 | 54.8538 | 54.8035 | 55.0369 | 54.9088 | 8.4915 | -0.37079 | 0.082398 | 123.0377 | 123.2758 | 0.032044 | 76.6891 | 0.059509 | 123.4085 | 123.0011 | 123.2346 | 123.0789 | 123.1293 | 123.0377 | 123.1064 | 123.0515 | 76.6891 | 123.1293 | 123.0377 | 123.0515 | 123.0789 | 123.1064 | -123.4177 | -46.3577
4553.7656 | 123.2895 | -68.2068 | 54.8218 | -0.84328 | 0.0080194 | 0.0061737 | 0.002634 | -0.0121 | -0.0060775 | -0.0024438 | 54.8813 | 54.9545 | -68.5776 | 55.0964 | 54.8584 | 54.8309 | 54.8035 | 55.0186 | 54.8767 | 8.5007 | -0.37079 | 0.13275 | 123.0881 | 123.3032 | 0.036621 | 76.7075 | 0.054932 | 123.4589 | 123.0103 | 123.2254 | 123.0652 | 123.1613 | 123.0881 | 123.0835 | 123.0377 | 76.7075 | 123.1613 | 123.0881 | 123.0377 | 123.0652 | 123.0835 | -123.3994 | -46.3211
4554.7656 | 123.3261 | -68.1931 | 54.8492 | 0.07988 | 0.0095148 | 0.00019226 | 0.002634 | -0.012527 | -0.0060775 | -0.00094839 | 54.8355 | 54.895 | -68.5776 | 55.0827 | 54.8355 | 54.863 | 54.7623 | 55.0415 | 54.9088 | 8.4915 | -0.38452 | 0.045777 | 123.0286 | 123.2758 | -0.013733 | 76.6846 | 0.059509 | 123.4131 | 122.9553 | 123.2346 | 123.0286 | 123.0881 | 123.0286 | 123.1018 | 123.056 | 76.6846 | 123.0881 | 123.0286 | 123.056 | 123.0286 | 123.1018 | -123.4268 | -46.3577
4555.7656 | 123.3215 | -68.1976 | 54.8676 | 0.26299 | 0.012933 | 0.0059601 | 0.0069064 | -0.0078271 | -0.0058639 | -0.0028712 | 54.9133 | 54.9088 | -68.5867 | 55.1056 | 54.8584 | 54.7302 | 54.6753 | 55.1651 | 54.8721 | 8.4961 | -0.3891 | 0.041198 | 123.111 | 123.3032 | -0.009156 | 76.6937 | 0.004577 | 123.5001 | 122.8729 | 123.3627 | 123.056 | 123.1064 | 123.111 | 123.0698 | 122.9279 | 76.6937 | 123.1064 | 123.111 | 122.9279 | 123.056 | 123.0698 | -123.4543 | -46.3715
4556.7812 | 123.2254 | -68.2022 | 54.8813 | 0.11803 | 0.014428 | 0.0040375 | 0.010111 | -0.0082545 | -0.0062911 | -0.00094839 | 54.8859 | 55.0461 | -68.5638 | 55.0461 | 54.7989 | 54.7714 | 54.8904 | 54.9362 | 54.9179 | 8.4915 | -0.36163 | 0.16479 | 123.0881 | 123.2483 | -0.082398 | 76.6937 | 0.036621 | 123.4497 | 123.0927 | 123.1384 | 123.0011 | 123.2483 | 123.0881 | 123.1201 | 122.9736 | 76.6937 | 123.2483 | 123.0881 | 122.9736 | 123.0011 | 123.1201 | -123.4451 | -46.3898
4557.7812 | 123.317 | -68.2022 | 54.8126 | 0.19432 | 0.012292 | 0.0063873 | 0.0017794 | -0.0091089 | -0.0080001 | -0.0015894 | 54.8447 | 54.9088 | -68.605 | 55.0735 | 54.8721 | 54.863 | 54.776 | 55.0003 | 54.863 | 8.4961 | -0.40283 | 0.09613 | 123.0469 | 123.2758 | 0.059509 | 76.6983 | 0.050354 | 123.4497 | 122.9782 | 123.2025 | 123.0743 | 123.111 | 123.0469 | 123.0652 | 123.0652 | 76.6983 | 123.111 | 123.0469 | 123.0652 | 123.0743 | 123.0652 | -123.4177 | -46.3165
4558.7812 | 123.3078 | -68.2022 | 54.8218 | 0.24773 | 0.011437 | 0.0059601 | 0.0041292 | -0.0093225 | -0.0065047 | -0.0015894 | 54.863 | 54.8996 | -68.5867 | 55.0735 | 54.863 | 54.8767 | 54.7302 | 55.0278 | 54.8904 | 8.5007 | -0.38452 | 0.07782 | 123.0652 | 123.2758 | 0.041199 | 76.7029 | 0.068665 | 123.4497 | 122.9324 | 123.23 | 123.0652 | 123.1018 | 123.0652 | 123.0927 | 123.0789 | 76.7029 | 123.1018 | 123.0652 | 123.0789 | 123.0652 | 123.0927 | -123.4085 | -46.3211
4559.7656 | 123.3307 | -68.1931 | 54.8355 | 0.1104 | 0.010369 | 0.00083306 | -0.00078396 | -0.01274 | -0.0067185 | -0.00094839 | 54.7989 | 54.9271 | -68.573 | 55.1193 | 54.8309 | 54.8401 | 54.7531 | 55.014 | 54.8813 | 8.5007 | -0.37994 | 0.091553 | 122.9919 | 123.3124 | -0.004577 | 76.6937 | 0.045777 | 123.3719 | 122.9462 | 123.2071 | 123.024 | 123.1201 | 122.9919 | 123.0743 | 123.0331 | 76.6937 | 123.1201 | 122.9919 | 123.0331 | 123.024 | 123.0743 | -123.4085 | -46.3348
4560.7656 | 123.2986 | -68.1747 | 54.8584 | 0.087509 | 0.011224 | 0.0036103 | 0.001993 | -0.0080407 | -0.0062911 | -0.0028712 | 54.8401 | 54.9316 | -68.5867 | 55.069 | 54.8492 | 54.8492 | 54.7852 | 55.0827 | 54.9316 | 8.4961 | -0.41199 | 0.073243 | 123.0148 | 123.2437 | -0.009155 | 76.6708 | 0.073243 | 123.4268 | 122.9599 | 123.2574 | 123.024 | 123.1064 | 123.0148 | 123.1064 | 123.024 | 76.6708 | 123.1064 | 123.0148 | 123.024 | 123.024 | 123.1064 | -123.4451 | -46.3623
4561.7656 | 123.3078 | -68.1931 | 54.8492 | 0.10277 | 0.0090876 | 0.00061946 | 0.002634 | -0.0088953 | -0.0056503 | -0.0026574 | 54.8676 | 54.9362 | -68.5638 | 55.0644 | 54.8492 | 54.8492 | 54.7852 | 55.0323 | 54.9088 | 8.4961 | -0.37079 | 0.086975 | 123.0606 | 123.2574 | 0 | 76.6891 | 0.059509 | 123.4314 | 122.9782 | 123.2254 | 123.0423 | 123.1293 | 123.0606 | 123.1018 | 123.0423 | 76.6891 | 123.1293 | 123.0606 | 123.0423 | 123.0423 | 123.1018 | -123.4131 | -46.3531
4562.7656 | 123.349 | -68.2114 | 54.8309 | 0.28587 | 0.013787 | 0.0048921 | 0.0081882 | -0.0073999 | -0.0073593 | -0.0022302 | 54.9316 | 54.9133 | -68.5822 | 55.101 | 54.8767 | 54.8767 | 54.6936 | 55.0369 | 54.8767 | 8.5052 | -0.37079 | 0.082397 | 123.143 | 123.3124 | 0.045776 | 76.7166 | 0.045776 | 123.5138 | 122.905 | 123.2483 | 123.0881 | 123.1247 | 123.143 | 123.0881 | 123.0881 | 76.7166 | 123.1247 | 123.143 | 123.0881 | 123.0881 | 123.0881 | -123.4131 | -46.3257
4563.7656 | 123.3444 | -68.2068 | 54.8126 | 0.31639 | 0.011865 | 0.01066 | 0.0064792 | -0.0080407 | -0.0062911 | -0.0028712 | 54.9362 | 54.9408 | -68.5913 | 55.101 | 54.8676 | 54.8721 | 54.6982 | 55.0369 | 54.895 | 8.4961 | -0.38452 | 0.12817 | 123.143 | 123.3078 | 0.054932 | 76.7029 | 0.082398 | 123.5275 | 122.905 | 123.2437 | 123.0743 | 123.1476 | 123.143 | 123.1018 | 123.0789 | 76.7029 | 123.1476 | 123.143 | 123.0789 | 123.0743 | 123.1018 | -123.4039 | -46.3165
4564.7812 | 123.2986 | -68.2114 | 54.8309 | 0.23247 | 0.011437 | 0.0038239 | 0.0032748 | -0.0095361 | -0.0071457 | -0.0032984 | 54.8767 | 54.9133 | -68.5776 | 55.0827 | 54.8538 | 54.8538 | 54.7302 | 55.0095 | 54.895 | 8.4915 | -0.36621 | 0.082397 | 123.0881 | 123.2941 | 0.022888 | 76.7029 | 0.064087 | 123.4543 | 122.9416 | 123.2208 | 123.0652 | 123.1247 | 123.0881 | 123.1064 | 123.0652 | 76.7029 | 123.1247 | 123.0881 | 123.0652 | 123.0652 | 123.1064 | -123.4085 | -46.3394
4565.7656 | 123.349 | -68.1839 | 54.808 | 1.5829 | 0.012933 | 0.0051057 | 0.0069064 | -0.0078271 | -0.0086411 | -0.00052119 | 54.9408 | 54.8996 | -68.5684 | 55.1102 | 54.9042 | 54.8996 | 54.6936 | 55.0323 | 54.8859 | 8.5007 | -0.38452 | 0.091553 | 123.1247 | 123.2941 | 0.096131 | 76.6846 | 0.07782 | 123.5092 | 122.8775 | 123.2162 | 123.0881 | 123.0835 | 123.1247 | 123.0698 | 123.0835 | 76.6846 | 123.0835 | 123.1247 | 123.0835 | 123.0881 | 123.0698 | -123.3765 | -46.3074
4566.7656 | 123.3032 | -68.1702 | 54.8401 | 0.14092 | 0.012078 | 0.0061737 | 0.0015658 | -0.014877 | -0.0060775 | -0.0022302 | 54.8264 | 54.9362 | -68.5593 | 55.0781 | 54.8355 | 54.8767 | 54.776 | 55.0644 | 54.9179 | 8.4915 | -0.3891 | 0.09613 | 122.9965 | 123.2483 | -0.004578 | 76.6617 | 0.07782 | 123.3856 | 122.9462 | 123.2346 | 123.0057 | 123.1064 | 122.9965 | 123.0881 | 123.0469 | 76.6617 | 123.1064 | 122.9965 | 123.0469 | 123.0057 | 123.0881 | -123.3994 | -46.3486
4567.7656 | 123.3078 | -68.1747 | 54.8538 | 0.087509 | 0.0097284 | 0.0021149 | 0.0034884 | -0.011459 | -0.0054367 | -0.0013758 | 54.8355 | 54.9133 | -68.6096 | 55.0598 | 54.9683 | 54.9683 | 54.7302 | 55.0232 | 54.8859 | 8.4915 | -0.43487 | 0.059509 | 123.0103 | 123.2346 | 0.11444 | 76.6663 | 0.032043 | 123.4451 | 122.905 | 123.1979 | 123.143 | 123.0881 | 123.0103 | 123.0606 | 123.143 | 76.6663 | 123.0881 | 123.0103 | 123.143 | 123.143 | 123.0606 | -123.4634 | -46.3623
4568.7656 | 123.3994 | -68.1976 | 54.8584 | 0.14854 | 0.010796 | 0.0046783 | 0.0028476 | -0.010177 | -0.0054367 | -0.00094839 | 54.8447 | 54.9133 | -68.5867 | 55.0461 | 54.863 | 54.8492 | 54.7897 | 55.0278 | 54.8859 | 8.4961 | -0.3891 | 0.054932 | 123.0423 | 123.2437 | 0.004578 | 76.6937 | 0.027466 | 123.4314 | 122.9874 | 123.2254 | 123.0606 | 123.111 | 123.0423 | 123.0835 | 123.0469 | 76.6937 | 123.111 | 123.0423 | 123.0469 | 123.0606 | 123.0835 | -123.4451 | -46.3623
4569.7656 | 123.3307 | -68.2022 | 54.8035 | 0.23247 | 0.012292 | 0.0029693 | 0.0062656 | -0.011886 | -0.0050095 | -0.0013758 | 54.9133 | 54.9362 | -68.605 | 55.0827 | 54.8859 | 54.8904 | 54.689 | 55.0415 | 54.8721 | 8.5007 | -0.40283 | 0.13275 | 123.1155 | 123.2849 | 0.082397 | 76.7029 | 0.068664 | 123.5184 | 122.8912 | 123.2437 | 123.0881 | 123.1384 | 123.1155 | 123.0743 | 123.0927 | 76.7029 | 123.1384 | 123.1155 | 123.0927 | 123.0881 | 123.0743 | -123.4085 | -46.3028
4570.7812 | 123.3444 | -68.2068 | 54.8218 | 0.2935 | 0.009942 | 0.0042511 | 0.0032748 | -0.010604 | -0.0065047 | -0.001803 | 54.8996 | 54.9362 | -68.5959 | 55.0919 | 54.8813 | 54.8767 | 54.7073 | 55.0369 | 54.8676 | 8.4961 | -0.3891 | 0.11444 | 123.1064 | 123.2986 | 0.05951 | 76.7029 | 0.045777 | 123.4955 | 122.9141 | 123.2437 | 123.0881 | 123.143 | 123.1064 | 123.0743 | 123.0835 | 76.7029 | 123.143 | 123.1064 | 123.0835 | 123.0881 | 123.0743 | -123.4177 | -46.3257
4571.7812 | 123.3353 | -68.1885 | 54.8492 | 0.17906 | 0.010369 | 0.0010467 | 0.0030612 | -0.01274 | -0.0052231 | -0.001803 | 54.8538 | 54.9088 | -68.5684 | 55.0644 | 54.8492 | 54.8492 | 54.7668 | 55.0278 | 54.8721 | 8.4961 | -0.37994 | 0.059509 | 123.0423 | 123.2529 | 0 | 76.6846 | 0.022888 | 123.4222 | 122.9553 | 123.2162 | 123.0377 | 123.0972 | 123.0423 | 123.0606 | 123.0377 | 76.6846 | 123.0972 | 123.0423 | 123.0377 | 123.0377 | 123.0606 | -123.4177 | -46.3531
4572.7812 | 123.3032 | -68.2068 | 54.863 | 0.20195 | 0.011437 | 0.0042511 | 0.0032748 | -0.0097497 | -0.0080001 | -0.0022302 | 54.863 | 54.9133 | -68.5684 | 55.0598 | 54.8584 | 54.8538 | 54.7577 | 55.0095 | 54.8813 | 8.4915 | -0.36163 | 0.050354 | 123.0698 | 123.2666 | -0.004578 | 76.6983 | 0.018311 | 123.4314 | 122.9645 | 123.2162 | 123.0652 | 123.1201 | 123.0698 | 123.0881 | 123.0606 | 76.6983 | 123.1201 | 123.0698 | 123.0606 | 123.0652 | 123.0881 | -123.4314 | -46.3715
4573.7656 | 123.3215 | -68.1702 | 54.8721 | -0.74409 | 0.010156 | 0.0074555 | 0.0028476 | -0.011245 | -0.0058639 | -0.0022302 | 54.7989 | 54.95 | -68.5593 | 55.0735 | 54.8538 | 54.8538 | 54.7897 | 55.0049 | 54.9133 | 8.4915 | -0.3891 | 0.07782 | 122.9691 | 123.2437 | -0.01831 | 76.6617 | 0.041199 | 123.3582 | 122.9599 | 123.175 | 123.024 | 123.1201 | 122.9691 | 123.0835 | 123.024 | 76.6617 | 123.1201 | 122.9691 | 123.024 | 123.024 | 123.0835 | -123.4314 | -46.3806
4574.7656 | 123.317 | -68.2114 | 54.8492 | 0.041733 | 0.011437 | 0.0033967 | 0.0017794 | -0.0091089 | -0.0069321 | -0.0015894 | 54.982 | 54.9591 | -68.541 | 55.0827 | 54.8859 | 54.8538 | 54.7852 | 55.0323 | 54.9225 | 8.5007 | -0.32959 | 0.10986 | 123.1934 | 123.2941 | 0.036621 | 76.712 | 0.073242 | 123.5229 | 122.9965 | 123.2437 | 123.0972 | 123.1705 | 123.1934 | 123.1338 | 123.0652 | 76.712 | 123.1705 | 123.1934 | 123.0652 | 123.0972 | 123.1338 | -123.3902 | -46.3486
4575.7656 | 123.2941 | -68.2114 | 54.8584 | 0.095139 | 0.009942 | 0.0029693 | 0.00049764 | -0.0093225 | -0.0075729 | -0.0024438 | 54.8401 | 54.9271 | -68.5959 | 55.0507 | 54.8447 | 54.8584 | 54.8035 | 55.0461 | 54.8813 | 8.4869 | -0.38452 | 0.068665 | 123.0515 | 123.262 | -0.013732 | 76.6983 | 0.022889 | 123.436 | 123.0148 | 123.2574 | 123.056 | 123.1384 | 123.0515 | 123.0927 | 123.0698 | 76.6983 | 123.1384 | 123.0515 | 123.0698 | 123.056 | 123.0927 | -123.4543 | -46.3715
4576.7656 | 123.3536 | -68.1931 | 54.8401 | 0.26299 | 0.014855 | 0.0068147 | 0.0077608 | -0.0086817 | -0.0069321 | -0.0030848 | 54.9088 | 54.895 | -68.605 | 55.1605 | 54.8676 | 54.895 | 54.7348 | 55.0552 | 54.895 | 8.5007 | -0.41199 | 0.054932 | 123.1018 | 123.3536 | 0.027466 | 76.6937 | 0.054932 | 123.5138 | 122.9279 | 123.2483 | 123.0606 | 123.0881 | 123.1018 | 123.0881 | 123.0881 | 76.6937 | 123.0881 | 123.1018 | 123.0881 | 123.0606 | 123.0881 | -123.4451 | -46.3394
4577.7812 | 123.2254 | -68.2297 | 54.8859 | 0.14092 | 0.012078 | 0.0083099 | 0.012247 | -0.0076135 | -0.0050095 | -0.0041528 | 54.8767 | 55.0278 | -68.5822 | 55.0598 | 54.7714 | 54.7577 | 54.8859 | 54.9133 | 54.9362 | 8.4961 | -0.35248 | 0.14191 | 123.1064 | 123.2895 | -0.11444 | 76.7258 | 0.050354 | 123.4589 | 123.1155 | 123.143 | 123.0011 | 123.2574 | 123.1064 | 123.1659 | 122.9874 | 76.7258 | 123.2574 | 123.1064 | 122.9874 | 123.0011 | 123.1659 | -123.468 | -46.3898
4578.7812 | 123.3032 | -68.2114 | 54.8492 | 0.17143 | 0.012292 | 0.0040375 | 0.0017794 | -0.011672 | -0.0050095 | -0.0020166 | 54.8172 | 54.9225 | -68.5776 | 55.0552 | 54.8492 | 54.8538 | 54.7806 | 55.0095 | 54.8721 | 8.4915 | -0.36621 | 0.073242 | 123.0286 | 123.2666 | 0 | 76.7029 | 0.022888 | 123.3948 | 122.9919 | 123.2208 | 123.0606 | 123.1338 | 123.0286 | 123.0835 | 123.0652 | 76.7029 | 123.1338 | 123.0286 | 123.0652 | 123.0606 | 123.0835 | -123.4268 | -46.3577
4579.7812 | 123.3261 | -68.2159 | 54.8309 | 0.18669 | 0.011865 | 0.0042511 | 0.0011386 | -0.010818 | -0.0080001 | -0.00052119 | 54.8218 | 54.9179 | -68.573 | 55.0598 | 54.8584 | 54.8447 | 54.7714 | 55.0049 | 54.8904 | 8.4915 | -0.35706 | 0.086975 | 123.0377 | 123.2758 | 0.027465 | 76.7075 | 0.059509 | 123.3948 | 122.9874 | 123.2208 | 123.0743 | 123.1338 | 123.0377 | 123.1064 | 123.0606 | 76.7075 | 123.1338 | 123.0377 | 123.0606 | 123.0743 | 123.1064 | -123.4039 | -46.3394
4580.7656 | 123.3261 | -68.1885 | 54.8584 | 0.026474 | 0.011224 | 0.0019013 | 0.0015658 | -0.013381 | -0.0084273 | -0.0037256 | 54.8218 | 54.9225 | -68.5638 | 55.0781 | 54.8813 | 54.863 | 54.7989 | 55.0461 | 54.9362 | 8.5007 | -0.37537 | 0.064087 | 123.0103 | 123.2666 | 0.022889 | 76.6891 | 0.07782 | 123.3856 | 122.9874 | 123.2346 | 123.0698 | 123.111 | 123.0103 | 123.1247 | 123.0515 | 76.6891 | 123.111 | 123.0103 | 123.0515 | 123.0698 | 123.1247 | -123.4222 | -46.3577
4581.7656 | 123.3307 | -68.1839 | 54.8492 | 0.072251 | 0.010369 | -0.0023711 | 0.0013522 | -0.0121 | -0.0080001 | -0.0041528 | 54.8401 | 54.9225 | -68.5776 | 55.0919 | 54.8767 | 54.8584 | 54.7943 | 55.0461 | 54.9042 | 8.5007 | -0.39368 | 0.073242 | 123.024 | 123.2758 | 0.027466 | 76.6846 | 0.054932 | 123.4177 | 122.9782 | 123.23 | 123.0606 | 123.1064 | 123.024 | 123.0881 | 123.0423 | 76.6846 | 123.1064 | 123.024 | 123.0423 | 123.0606 | 123.0881 | -123.4268 | -46.3486
4582.7656 | 123.3215 | -68.1839 | 54.8401 | 0.56816 | 0.011224 | 0.0063873 | 0.00049764 | -0.0099633 | -0.0073593 | -0.0020166 | 54.8538 | 54.9271 | -68.5684 | 55.069 | 54.8721 | 54.8492 | 54.7943 | 55.0323 | 54.8996 | 8.4961 | -0.38452 | 0.086975 | 123.0377 | 123.2529 | 0.032043 | 76.68 | 0.059509 | 123.4222 | 122.9782 | 123.2162 | 123.056 | 123.111 | 123.0377 | 123.0835 | 123.0331 | 76.68 | 123.111 | 123.0377 | 123.0331 | 123.056 | 123.0835 | -123.4085 | -46.344
4583.7656 | 123.3536 | -68.1747 | 54.8355 | 0.5529 | 0.0088738 | 0.0044647 | 0.0062656 | -0.0088953 | -0.0077865 | -0.001803 | 55.0003 | 54.8904 | -68.573 | 55.1193 | 54.8813 | 54.8767 | 54.6936 | 55.0369 | 54.8767 | 8.5007 | -0.39825 | 0.054932 | 123.175 | 123.2941 | 0.045777 | 76.6754 | 0.041199 | 123.5733 | 122.8683 | 123.2117 | 123.056 | 123.0652 | 123.175 | 123.0515 | 123.0515 | 76.6754 | 123.0652 | 123.175 | 123.0515 | 123.056 | 123.0515 | -123.4085 | -46.3348
4584.7812 | 123.317 | -68.1931 | 54.8309 | 0.13329 | 0.010369 | 0.0051057 | 0.0015658 | -0.011886 | -0.0043685 | -0.0015894 | 54.8264 | 54.9088 | -68.6005 | 55.0552 | 54.8447 | 54.8355 | 54.776 | 55.0095 | 54.8904 | 8.5007 | -0.40741 | 0.077819 | 123.0194 | 123.2483 | 0.013733 | 76.6937 | 0.059509 | 123.4268 | 122.9691 | 123.2025 | 123.0377 | 123.1018 | 123.0194 | 123.0835 | 123.0286 | 76.6937 | 123.1018 | 123.0194 | 123.0286 | 123.0377 | 123.0835 | -123.4314 | -46.3303
4585.7812 | 123.3032 | -68.1793 | 54.863 | 0.14092 | 0.009942 | 0.0014741 | 0.002634 | -0.0095361 | -0.0077865 | -0.0011622 | 54.8447 | 54.9088 | -68.573 | 55.0644 | 54.8538 | 54.8355 | 54.7806 | 55.0232 | 54.9225 | 8.4915 | -0.39368 | 0.045776 | 123.024 | 123.2437 | -0.009155 | 76.6708 | 0.059509 | 123.4177 | 122.9599 | 123.2025 | 123.0331 | 123.0881 | 123.024 | 123.1018 | 123.0148 | 76.6708 | 123.0881 | 123.024 | 123.0148 | 123.0331 | 123.1018 | -123.436 | -46.3715
4586.7812 | 123.2849 | -68.1931 | 54.8447 | 0.18669 | 0.010583 | 0.0053193 | -0.0012112 | -0.011672 | -0.0069321 | -0.0020166 | 54.8492 | 54.9133 | -68.5822 | 55.0781 | 54.8355 | 54.8538 | 54.7668 | 55.014 | 54.9088 | 8.4869 | -0.3891 | 0.068664 | 123.0423 | 123.2712 | -0.009156 | 76.68 | 0.064086 | 123.4314 | 122.9599 | 123.2071 | 123.0286 | 123.1064 | 123.0423 | 123.1018 | 123.0469 | 76.68 | 123.1064 | 123.0423 | 123.0469 | 123.0286 | 123.1018 | -123.4268 | -46.3577
4587.7656 | 123.3261 | -68.1976 | 54.863 | 0.1104 | 0.010583 | 0.0036103 | 0.0028476 | -0.011886 | -0.0062911 | -0.0028712 | 54.8264 | 54.9225 | -68.6005 | 55.0827 | 54.8813 | 54.8538 | 54.7852 | 55.0461 | 54.8813 | 8.4961 | -0.40283 | 0.059509 | 123.024 | 123.2803 | 0.018311 | 76.6937 | 0.018311 | 123.4268 | 122.9828 | 123.2437 | 123.0789 | 123.1201 | 123.024 | 123.0789 | 123.0515 | 76.6937 | 123.1201 | 123.024 | 123.0515 | 123.0789 | 123.0789 | -123.4634 | -46.3669
4588.7656 | 123.3078 | -68.1976 | 54.8492 | 0.60631 | 0.011651 | 0.0031831 | 0.0030612 | -0.01274 | -0.0060775 | -0.00458 | 54.863 | 54.95 | -68.5638 | 55.0827 | 54.8584 | 54.8447 | 54.7989 | 55.0461 | 54.9088 | 8.5007 | -0.36621 | 0.10071 | 123.0606 | 123.2803 | 0.009155 | 76.6983 | 0.059509 | 123.4268 | 122.9965 | 123.2437 | 123.056 | 123.1476 | 123.0606 | 123.1064 | 123.0423 | 76.6983 | 123.1476 | 123.0606 | 123.0423 | 123.056 | 123.1064 | -123.4131 | -46.3486
4589.7656 | 123.3536 | -68.1931 | 54.8309 | -0.37788 | 0.010796 | 0.0016877 | 0.0066928 | -0.0095361 | -0.0067185 | -0.0032984 | 54.9179 | 54.8996 | -68.5822 | 55.101 | 54.8859 | 54.8813 | 54.7028 | 55.0552 | 54.8996 | 8.5007 | -0.3891 | 0.068664 | 123.111 | 123.2941 | 0.054931 | 76.6937 | 0.068664 | 123.5001 | 122.8958 | 123.2483 | 123.0789 | 123.0927 | 123.111 | 123.0927 | 123.0743 | 76.6937 | 123.0927 | 123.111 | 123.0743 | 123.0789 | 123.0927 | -123.4131 | -46.3303
4590.7656 | 123.3353 | -68.1931 | 54.8264 | 0.26299 | 0.012505 | 0.0055329 | 0.003702 | -0.0082545 | -0.0056503 | -0.0022302 | 54.8172 | 54.9042 | -68.6371 | 55.1422 | 54.8859 | 54.8721 | 54.7211 | 55.0323 | 54.9088 | 8.4915 | -0.44403 | 0.07782 | 123.0103 | 123.3353 | 0.059509 | 76.6846 | 0.082397 | 123.4543 | 122.9141 | 123.2254 | 123.0789 | 123.0972 | 123.0103 | 123.1018 | 123.0652 | 76.6846 | 123.0972 | 123.0103 | 123.0652 | 123.0789 | 123.1018 | -123.4634 | -46.3348
4591.7812 | 123.317 | -68.2068 | 54.8355 | 0.1638 | 0.010369 | 0.0070283 | 0.0013522 | -0.010177 | -0.0067185 | -0.00030759 | 54.8355 | 54.9179 | -68.5822 | 55.0735 | 54.8492 | 54.8447 | 54.776 | 55.0323 | 54.8767 | 8.4961 | -0.37537 | 0.082398 | 123.0423 | 123.2803 | 0.013733 | 76.7029 | 0.041199 | 123.4177 | 122.9828 | 123.2391 | 123.056 | 123.1247 | 123.0423 | 123.0835 | 123.0515 | 76.7029 | 123.1247 | 123.0423 | 123.0515 | 123.056 | 123.0835 | -123.4177 | -46.3394
4592.7812 | 123.3353 | -68.2114 | 54.8264 | 0.20195 | 0.010156 | -0.0025847 | 0.0017794 | -0.012527 | -0.0058639 | -0.00073479 | 54.8401 | 54.9133 | -68.5867 | 55.0827 | 54.8355 | 54.8676 | 54.7577 | 55.0278 | 54.8904 | 8.4961 | -0.37537 | 0.086975 | 123.0515 | 123.2941 | 0.009155 | 76.7075 | 0.064087 | 123.4268 | 122.9691 | 123.2391 | 123.0469 | 123.1247 | 123.0515 | 123.1018 | 123.0789 | 76.7075 | 123.1247 | 123.0515 | 123.0789 | 123.0469 | 123.1018 | -123.4131 | -46.3303
4593.7812 | 123.3215 | -68.2022 | 54.8355 | 0.20958 | 0.012078 | 0.0072419 | 0.0030612 | -0.010604 | -0.0060775 | -0.0022302 | 54.8492 | 54.9225 | -68.5913 | 55.0827 | 54.8538 | 54.8447 | 54.7531 | 55.014 | 54.895 | 8.4915 | -0.3891 | 0.086975 | 123.0515 | 123.2849 | 0.018311 | 76.6937 | 0.05951 | 123.4406 | 122.9553 | 123.2162 | 123.056 | 123.1247 | 123.0515 | 123.0972 | 123.0469 | 76.6937 | 123.1247 | 123.0515 | 123.0469 | 123.056 | 123.0972 | -123.4268 | -46.344
4594.7656 | 123.3078 | -68.1931 | 54.8401 | -0.057449 | 0.01101 | 0.0033967 | 0.0024202 | -0.0121 | -0.0050095 | -0.0011622 | 54.8172 | 54.9362 | -68.5684 | 55.0964 | 54.8676 | 54.863 | 54.7897 | 55.0369 | 54.9225 | 8.4961 | -0.37537 | 0.09613 | 123.0103 | 123.2895 | 0.027466 | 76.6891 | 0.082397 | 123.3856 | 122.9828 | 123.23 | 123.0606 | 123.1293 | 123.0103 | 123.1155 | 123.056 | 76.6891 | 123.1293 | 123.0103 | 123.056 | 123.0606 | 123.1155 | -123.4085 | -46.344
4595.7656 | 123.3215 | -68.1931 | 54.8309 | 0.12566 | 0.011224 | 0.00019226 | 0.00092504 | -0.0099633 | -0.0067185 | -0.0013758 | 54.8309 | 54.9408 | -68.573 | 55.0415 | 54.8859 | 54.863 | 54.8172 | 55.014 | 54.9179 | 8.4961 | -0.37994 | 0.10986 | 123.024 | 123.2346 | 0.054931 | 76.6891 | 0.086975 | 123.4039 | 123.0103 | 123.2071 | 123.0789 | 123.1338 | 123.024 | 123.111 | 123.056 | 76.6891 | 123.1338 | 123.024 | 123.056 | 123.0789 | 123.111 | -123.4039 | -46.3348
4596.7656 | 123.3353 | -68.1885 | 54.8447 | 0.24773 | 0.010583 | 0.0021149 | 0.0073336 | -0.0069727 | -0.0058639 | -0.003512 | 54.9042 | 54.9225 | -68.573 | 55.1971 | 54.982 | 54.95 | 54.6936 | 55.101 | 54.8767 | 8.5007 | -0.38452 | 0.077819 | 123.0927 | 123.3856 | 0.13733 | 76.6891 | 0.032043 | 123.4772 | 122.8821 | 123.2895 | 123.1705 | 123.111 | 123.0927 | 123.0652 | 123.1384 | 76.6891 | 123.111 | 123.0927 | 123.1384 | 123.1705 | 123.0652 | -123.4177 | -46.344
4597.7656 | 123.3536 | -68.2114 | 54.7897 | 0.25536 | 0.011437 | 0.0040375 | 0.0066928 | -0.010177 | -0.0062911 | -0.0037256 | 54.9042 | 54.9408 | -68.605 | 55.1147 | 54.8859 | 54.8767 | 54.6844 | 55.0278 | 54.8767 | 8.5007 | -0.39368 | 0.15106 | 123.1155 | 123.3261 | 0.09613 | 76.712 | 0.086975 | 123.5092 | 122.8958 | 123.2391 | 123.0972 | 123.1522 | 123.1155 | 123.0881 | 123.0881 | 76.712 | 123.1522 | 123.1155 | 123.0881 | 123.0972 | 123.0881 | -123.3948 | -46.2891
4598.7812 | 123.3307 | -68.2114 | 54.8401 | 0.17906 | 0.012292 | 0.0040375 | 0.0015658 | -0.011459 | -0.0028731 | -0.0026574 | 54.8492 | 54.9088 | -68.5959 | 55.069 | 54.8584 | 54.8584 | 54.7394 | 55.0232 | 54.8721 | 8.4961 | -0.38452 | 0.068664 | 123.0606 | 123.2803 | 0.01831 | 76.7075 | 0.032043 | 123.4451 | 122.9507 | 123.2346 | 123.0698 | 123.1201 | 123.0606 | 123.0835 | 123.0698 | 76.7075 | 123.1201 | 123.0606 | 123.0698 | 123.0698 | 123.0835 | -123.436 | -46.344
4599.7812 | 123.3307 | -68.2022 | 54.8218 | 0.21721 | 0.011224 | 0.0068147 | 0.0041292 | -0.012313 | -0.0073593 | -0.0013758 | 54.8676 | 54.9088 | -68.5867 | 55.0873 | 54.8676 | 54.8584 | 54.7256 | 55.0278 | 54.8538 | 8.4961 | -0.38452 | 0.086975 | 123.0698 | 123.2895 | 0.045777 | 76.6983 | 0.032044 | 123.4543 | 122.9279 | 123.23 | 123.0698 | 123.111 | 123.0698 | 123.056 | 123.0606 | 76.6983 | 123.111 | 123.0698 | 123.0606 | 123.0698 | 123.056 | -123.4085 | -46.3257
4600.7812 | 123.3124 | -68.1793 | 54.8035 | 0.23247 | 0.010156 | 0.0029693 | 0.0039156 | -0.012527 | -0.0073593 | -9.3992e-05 | 54.8721 | 54.9271 | -68.5776 | 55.0964 | 54.8676 | 54.8721 | 54.7211 | 55.0278 | 54.8721 | 8.4961 | -0.39825 | 0.1236 | 123.0515 | 123.2758 | 0.064087 | 76.6754 | 0.068664 | 123.4497 | 122.9004 | 123.2071 | 123.0469 | 123.1064 | 123.0515 | 123.0515 | 123.0515 | 76.6754 | 123.1064 | 123.0515 | 123.0515 | 123.0469 | 123.0515 | -123.381 | -46.3074
4601.7656 | 123.3398 | -68.1793 | 54.8538 | 0.10277 | 0.011224 | 0.0031831 | 0.0017794 | -0.011886 | -0.0043685 | -0.001803 | 54.8401 | 54.9545 | -68.5684 | 55.069 | 54.8538 | 54.8492 | 54.7897 | 55.0095 | 54.8859 | 8.4961 | -0.3891 | 0.10071 | 123.0194 | 123.2483 | 0 | 76.6754 | 0.032043 | 123.4085 | 122.9691 | 123.1888 | 123.0331 | 123.1338 | 123.0194 | 123.0652 | 123.0286 | 76.6754 | 123.1338 | 123.0194 | 123.0286 | 123.0331 | 123.0652 | -123.4222 | -46.3577
4602.7656 | 123.2986 | -68.2114 | 54.8492 | 0.12566 | 0.009942 | 0.0033967 | 0.0017794 | -0.011031 | -0.0067185 | -0.0032984 | 54.8584 | 54.9454 | -68.5638 | 55.0827 | 54.863 | 54.8447 | 54.7989 | 55.0186 | 54.8859 | 8.4915 | -0.35248 | 0.096131 | 123.0698 | 123.2941 | 0.013733 | 76.7029 | 0.036621 | 123.4222 | 123.0103 | 123.23 | 123.0743 | 123.1567 | 123.0698 | 123.0972 | 123.056 | 76.7029 | 123.1567 | 123.0698 | 123.056 | 123.0743 | 123.0972 | -123.4131 | -46.3577
4603.7656 | 123.3353 | -68.1793 | 54.8355 | 0.25536 | 0.014214 | 0.0070283 | 0.0077608 | -0.0095361 | -0.0094955 | -0.0024438 | 54.895 | 54.9545 | -68.6005 | 55.0873 | 54.8355 | 54.8172 | 54.7394 | 55.0278 | 54.8996 | 8.4915 | -0.42114 | 0.11902 | 123.0743 | 123.2666 | 0 | 76.6708 | 0.064087 | 123.4955 | 122.9187 | 123.2071 | 123.0148 | 123.1338 | 123.0743 | 123.0789 | 122.9965 | 76.6708 | 123.1338 | 123.0743 | 122.9965 | 123.0148 | 123.0789 | -123.436 | -46.344
4604.7812 | 123.2529 | -68.2205 | 54.8676 | -0.0040434 | 0.013787 | 0.0053193 | 0.0092562 | -0.0084681 | -0.0077865 | -0.0039392 | 54.9316 | 55.0278 | -68.573 | 55.0827 | 54.8264 | 54.8126 | 54.8721 | 54.9866 | 54.9316 | 8.4778 | -0.35248 | 0.16022 | 123.1522 | 123.3032 | -0.041199 | 76.6983 | 0.064087 | 123.5046 | 123.0927 | 123.2071 | 123.0469 | 123.2483 | 123.1522 | 123.1522 | 123.0331 | 76.6983 | 123.2483 | 123.1522 | 123.0331 | 123.0469 | 123.1522 | -123.4406 | -46.3898
4605.7812 | 123.3261 | -68.1976 | 54.8355 | 0.20958 | 0.011651 | 0.0048921 | 0.0024202 | -0.0073999 | -0.0056503 | -0.0028712 | 54.8859 | 54.9362 | -68.5913 | 55.101 | 54.8904 | 54.8813 | 54.7119 | 55.0507 | 54.8813 | 8.4961 | -0.39368 | 0.10071 | 123.0835 | 123.2986 | 0.054932 | 76.6937 | 0.045777 | 123.4772 | 122.9095 | 123.2483 | 123.0881 | 123.1338 | 123.0835 | 123.0789 | 123.0789 | 76.6937 | 123.1338 | 123.0835 | 123.0789 | 123.0881 | 123.0789 | -123.4268 | -46.3394
4606.7812 | 123.3444 | -68.1976 | 54.808 | -0.065079 | 0.015283 | 0.0027557 | 0.0062656 | -0.0091089 | -0.0043685 | -0.001803 | 54.895 | 54.9316 | -68.5822 | 55.1056 | 54.895 | 54.8996 | 54.7028 | 55.0369 | 54.863 | 8.4915 | -0.38452 | 0.1236 | 123.0927 | 123.3032 | 0.086976 | 76.6891 | 0.054932 | 123.4772 | 122.9004 | 123.2346 | 123.0927 | 123.1293 | 123.0927 | 123.0606 | 123.0972 | 76.6891 | 123.1293 | 123.0927 | 123.0972 | 123.0927 | 123.0606 | -123.3902 | -46.3165
4607.7656 | 123.2895 | -68.1885 | 54.8584 | 0.17906 | 0.011437 | 0.0019013 | 0.002634 | -0.011672 | -0.0054367 | -0.0026574 | 54.8492 | 54.9454 | -68.5822 | 55.0644 | 54.863 | 54.8538 | 54.776 | 55.0415 | 54.863 | 8.4869 | -0.39368 | 0.086976 | 123.0377 | 123.2529 | 0.004578 | 76.6754 | 0.004578 | 123.4314 | 122.9645 | 123.23 | 123.0515 | 123.1339 | 123.0377 | 123.0515 | 123.0423 | 76.6754 | 123.1339 | 123.0377 | 123.0423 | 123.0515 | 123.0515 | -123.4406 | -46.3715
4608.7656 | 123.317 | -68.1976 | 54.8584 | 0.20195 | 0.011224 | 0.0070283 | 0.0056246 | -0.011886 | -0.0058639 | -0.0011622 | 54.8538 | 54.95 | -68.5867 | 55.0644 | 54.8538 | 54.8447 | 54.7577 | 55.0186 | 54.8676 | 8.4961 | -0.3891 | 0.091553 | 123.0515 | 123.262 | -0.004577 | 76.6937 | 0.009156 | 123.4406 | 122.9553 | 123.2162 | 123.0515 | 123.1476 | 123.0515 | 123.0652 | 123.0423 | 76.6937 | 123.1476 | 123.0515 | 123.0423 | 123.0515 | 123.0652 | -123.4451 | -46.3623
4609.7656 | 123.317 | -68.2022 | 54.8309 | 0.20958 | 0.012719 | 0.0029693 | 0.0047702 | -0.011459 | -0.0075729 | -0.001803 | 54.8538 | 54.95 | -68.5822 | 55.069 | 54.863 | 54.8767 | 54.7348 | 55.0186 | 54.8676 | 8.4915 | -0.37994 | 0.11902 | 123.056 | 123.2712 | 0.032043 | 76.6937 | 0.036621 | 123.436 | 122.937 | 123.2208 | 123.0652 | 123.1522 | 123.056 | 123.0698 | 123.0789 | 76.6937 | 123.1522 | 123.056 | 123.0789 | 123.0652 | 123.0698 | -123.4131 | -46.3394
4610.7656 | 123.2712 | -68.2297 | 54.8584 | 0.28587 | 0.016351 | 0.0076691 | 0.0094698 | -0.0082545 | -0.0050095 | -0.0022302 | 54.8538 | 54.982 | -68.6234 | 55.0369 | 54.808 | 54.8126 | 54.808 | 54.9545 | 54.9225 | 8.4915 | -0.39368 | 0.1236 | 123.0835 | 123.2666 | -0.050354 | 76.7212 | 0.064087 | 123.4772 | 123.0377 | 123.1842 | 123.0377 | 123.2117 | 123.0835 | 123.1522 | 123.0423 | 76.7212 | 123.2117 | 123.0835 | 123.0423 | 123.0377 | 123.1522 | -123.4818 | -46.3669
4611.7969 | 123.2666 | -68.2251 | 54.8996 | -0.11085 | 0.013146 | 0.0093781 | 0.010538 | -0.0088953 | -0.0058639 | -0.0039392 | 54.9088 | 55.0507 | -68.5913 | 55.0919 | 54.8401 | 54.8309 | 54.8767 | 55.0003 | 54.9408 | 8.4915 | -0.36621 | 0.15106 | 123.1338 | 123.317 | -0.059509 | 76.7166 | 0.041199 | 123.5001 | 123.1018 | 123.2254 | 123.0652 | 123.2758 | 123.1338 | 123.1659 | 123.056 | 76.7166 | 123.2758 | 123.1338 | 123.056 | 123.0652 | 123.1659 | -123.4909 | -46.4081
4612.7812 | 123.3398 | -68.1839 | 54.808 | 0.24773 | 0.011224 | 0.0044647 | 0.0056246 | -0.0073999 | -0.0056503 | -0.0015894 | 54.895 | 54.9362 | -68.5776 | 55.1697 | 54.9133 | 54.8859 | 54.7531 | 55.0507 | 54.8767 | 8.4915 | -0.39368 | 0.12817 | 123.0789 | 123.3536 | 0.10529 | 76.6754 | 0.068665 | 123.4726 | 122.937 | 123.2346 | 123.0972 | 123.1201 | 123.0789 | 123.0606 | 123.0698 | 76.6754 | 123.1201 | 123.0789 | 123.0698 | 123.0972 | 123.0606 | -123.3856 | -46.3165
4613.7812 | 123.3444 | -68.2022 | 54.8218 | 0.2935 | 0.012719 | 0.00061946 | 0.005411 | -0.0086817 | -0.0054367 | -0.0015894 | 54.8859 | 54.9591 | -68.5822 | 55.0919 | 54.9683 | 54.7852 | 54.6158 | 55.1697 | 54.8309 | 8.5007 | -0.37994 | 0.13733 | 123.0881 | 123.2941 | 0.14649 | 76.7029 | 0.009156 | 123.468 | 122.818 | 123.3719 | 123.1705 | 123.1613 | 123.0881 | 123.0331 | 122.9874 | 76.7029 | 123.1613 | 123.0881 | 122.9874 | 123.1705 | 123.0331 | -123.4039 | -46.3211
4614.7656 | 123.3032 | -68.1976 | 54.8584 | 0.20958 | 0.011865 | 0.0051057 | 0.0013522 | -0.0084681 | -0.0065047 | -0.0013758 | 54.8676 | 54.9774 | -68.5776 | 55.0735 | 54.863 | 54.8584 | 54.7577 | 55.0369 | 54.8904 | 8.4915 | -0.37994 | 0.11902 | 123.0652 | 123.2712 | 0.004578 | 76.6891 | 0.032044 | 123.4451 | 122.9553 | 123.2346 | 123.0606 | 123.175 | 123.0652 | 123.0881 | 123.056 | 76.6891 | 123.175 | 123.0652 | 123.056 | 123.0606 | 123.0881 | -123.436 | -46.3669
4615.7656 | 123.3124 | -68.2205 | 54.8355 | 0.20958 | 0.011224 | 0.0042511 | 0.0034884 | -0.010177 | -0.0037277 | -9.3992e-05 | 54.8859 | 54.9088 | -68.5867 | 55.069 | 54.8676 | 54.8813 | 54.7302 | 55.0415 | 54.895 | 8.5052 | -0.36621 | 0.073242 | 123.1064 | 123.2895 | 0.032044 | 76.7258 | 0.05951 | 123.4726 | 122.9507 | 123.262 | 123.0881 | 123.1293 | 123.1064 | 123.1155 | 123.1018 | 76.7258 | 123.1293 | 123.1064 | 123.1018 | 123.0881 | 123.1155 | -123.4222 | -46.3303
4616.7656 | 123.3261 | -68.2159 | 54.8355 | 0.20958 | 0.011865 | 0.0021149 | 0.0049838 | -0.011459 | -0.0065047 | -0.0026574 | 54.8904 | 54.9454 | -68.5867 | 55.069 | 54.8721 | 54.8721 | 54.7348 | 55.014 | 54.8676 | 8.5007 | -0.37079 | 0.10986 | 123.1064 | 123.2849 | 0.036621 | 76.7166 | 0.032044 | 123.4772 | 122.9507 | 123.23 | 123.0881 | 123.1613 | 123.1064 | 123.0835 | 123.0881 | 76.7166 | 123.1613 | 123.1064 | 123.0881 | 123.0881 | 123.0835 | -123.4222 | -46.3348
4617.7656 | 123.2895 | -68.2251 | 54.8584 | 0.26299 | 0.013574 | 0.0046783 | 0.010111 | -0.0084681 | -0.0088547 | -0.0020166 | 54.8309 | 55.014 | -68.605 | 55.0323 | 54.7943 | 54.808 | 54.8172 | 54.9683 | 54.895 | 8.4961 | -0.37994 | 0.15564 | 123.056 | 123.2574 | -0.064086 | 76.7212 | 0.036622 | 123.436 | 123.0423 | 123.1934 | 123.0194 | 123.2391 | 123.056 | 123.1201 | 123.0331 | 76.7212 | 123.2391 | 123.056 | 123.0331 | 123.0194 | 123.1201 | -123.4634 | -46.3623
4618.7969 | 123.3307 | -68.1747 | 54.8538 | -0.17189 | 0.0084466 | 0.0076691 | 0.0034884 | -0.0121 | -0.0069321 | -0.00073479 | 54.895 | 54.9683 | -68.5638 | 55.1239 | 54.9088 | 54.8996 | 54.863 | 55.1147 | 54.9362 | 8.5007 | -0.3891 | 0.11444 | 123.0698 | 123.2986 | 0.054931 | 76.6754 | 0.082397 | 123.4589 | 123.0377 | 123.2895 | 123.0835 | 123.143 | 123.0698 | 123.111 | 123.0743 | 76.6754 | 123.143 | 123.0698 | 123.0743 | 123.0835 | 123.111 | -123.4177 | -46.3531
4619.7812 | 123.349 | -68.161 | 54.8538 | 0.26299 | 0.013787 | 0.0038239 | 0.0086154 | -0.0084681 | -0.0090683 | -0.003512 | 54.9225 | 54.9225 | -68.5959 | 55.1651 | 54.8813 | 54.8996 | 54.7531 | 55.0644 | 54.8996 | 8.4961 | -0.43487 | 0.068664 | 123.0835 | 123.3261 | 0.027466 | 76.6571 | 0.045776 | 123.5184 | 122.9141 | 123.2254 | 123.0423 | 123.0835 | 123.0835 | 123.0606 | 123.0606 | 76.6571 | 123.0835 | 123.0835 | 123.0606 | 123.0423 | 123.0606 | -123.4497 | -46.3577
4620.7812 | 123.349 | -68.1976 | 54.8492 | 0.25536 | 0.012719 | 0.0025421 | 0.0049838 | -0.0082545 | -0.0062911 | -0.0037256 | 54.9179 | 54.9271 | -68.5867 | 54.9591 | 54.9591 | 54.9774 | 54.7577 | 55.0827 | 54.8813 | 8.5007 | -0.3891 | 0.07782 | 123.1155 | 123.1567 | 0.10986 | 76.6983 | 0.032044 | 123.5046 | 122.9553 | 123.2803 | 123.1567 | 123.1247 | 123.1155 | 123.0789 | 123.175 | 76.6983 | 123.1247 | 123.1155 | 123.175 | 123.1567 | 123.0789 | -123.436 | -46.3486
4621.7656 | 123.3261 | -68.1931 | 54.8538 | 0.17143 | 0.0093012 | 0.0025421 | 0.002634 | -0.010604 | -0.0062911 | -0.00030759 | 54.8401 | 54.9454 | -68.5822 | 55.0781 | 54.8447 | 54.8538 | 54.7531 | 55.0278 | 54.8676 | 8.4915 | -0.3891 | 0.091553 | 123.0331 | 123.2712 | -0.009155 | 76.6846 | 0.013733 | 123.4222 | 122.9462 | 123.2208 | 123.0377 | 123.1384 | 123.0331 | 123.0606 | 123.0469 | 76.6846 | 123.1384 | 123.0331 | 123.0469 | 123.0377 | 123.0606 | -123.436 | -46.3623
4622.7656 | 123.3032 | -68.2205 | 54.8309 | 0.22484 | 0.011651 | 0.0029693 | 0.0034884 | -0.0099633 | -0.0060775 | -0.0020166 | 54.8492 | 54.9362 | -68.605 | 55.0598 | 54.8492 | 54.8447 | 54.7714 | 55.0232 | 54.8904 | 8.4915 | -0.38452 | 0.10528 | 123.0698 | 123.2803 | 0.01831 | 76.712 | 0.059509 | 123.4543 | 122.9919 | 123.2437 | 123.0698 | 123.1567 | 123.0698 | 123.111 | 123.0652 | 76.712 | 123.1567 | 123.0698 | 123.0652 | 123.0698 | 123.111 | -123.436 | -46.3394
4623.7812 | 123.3536 | -68.1427 | 54.8721 | -0.087967 | 0.010796 | -0.0019439 | 0.0041292 | -0.013595 | -0.0073593 | -0.00094839 | 55.1468 | 54.9911 | -68.5318 | 55.0964 | 54.8996 | 54.9179 | 54.7989 | 55.1468 | 54.9133 | 8.5007 | -0.3891 | 0.11902 | 123.2895 | 123.2391 | 0.027466 | 76.6434 | 0.041199 | 123.6786 | 122.9416 | 123.2895 | 123.0423 | 123.1338 | 123.2895 | 123.056 | 123.0606 | 76.6434 | 123.1338 | 123.2895 | 123.0606 | 123.0423 | 123.056 | -123.4039 | -46.3715
4624.7656 | 123.2391 | -68.248 | 54.8676 | -0.011673 | 0.015283 | 0.0070283 | 0.0098972 | -0.0073999 | -0.0052231 | -0.0026574 | 54.8676 | 55.0323 | -68.6142 | 55.0278 | 54.7897 | 54.7623 | 54.8676 | 54.9362 | 54.9545 | 8.4961 | -0.36621 | 0.1648 | 123.1155 | 123.2758 | -0.07782 | 76.7441 | 0.086975 | 123.4818 | 123.1155 | 123.1842 | 123.0377 | 123.2803 | 123.1155 | 123.2025 | 123.0103 | 76.7441 | 123.2803 | 123.1155 | 123.0103 | 123.0377 | 123.2025 | -123.4818 | -46.3715
4625.7812 | 123.3673 | -68.1976 | 54.8218 | 0.23247 | 0.010156 | 0.0063873 | 0.0075472 | -0.0076135 | -0.0050095 | -0.0032984 | 54.8904 | 54.9408 | -68.6096 | 55.1056 | 54.8859 | 54.8813 | 54.6982 | 55.0415 | 54.8767 | 8.4915 | -0.41199 | 0.11902 | 123.0881 | 123.3032 | 0.064087 | 76.6891 | 0.054932 | 123.5001 | 122.8958 | 123.2391 | 123.0835 | 123.1384 | 123.0881 | 123.0743 | 123.0789 | 76.6891 | 123.1384 | 123.0881 | 123.0789 | 123.0835 | 123.0743 | -123.4314 | -46.3303
4626.7812 | 123.3353 | -68.2159 | 54.8355 | 0.14854 | 0.01336 | -0.00066214 | 0.0060518 | -0.0095361 | -0.0080001 | -0.0022302 | 54.8813 | 54.95 | -68.5867 | 55.0964 | 54.8859 | 54.895 | 54.7028 | 55.0323 | 54.8767 | 8.4961 | -0.37079 | 0.11444 | 123.0972 | 123.3124 | 0.050354 | 76.712 | 0.041199 | 123.468 | 122.9187 | 123.2483 | 123.1018 | 123.1659 | 123.0972 | 123.0927 | 123.111 | 76.712 | 123.1659 | 123.0972 | 123.111 | 123.1018 | 123.0927 | -123.4222 | -46.3394
4627.7812 | 123.3444 | -68.2068 | 54.8309 | 0.07988 | 0.011437 | 0.0038239 | 0.0034884 | -0.0084681 | -0.0067185 | -0.0013758 | 54.9225 | 54.9637 | -68.5684 | 55.0873 | 54.8859 | 54.8859 | 54.7028 | 55.0415 | 54.8859 | 8.4915 | -0.36163 | 0.13275 | 123.1293 | 123.2941 | 0.054931 | 76.6983 | 0.054931 | 123.4909 | 122.9095 | 123.2483 | 123.0927 | 123.1705 | 123.1293 | 123.0927 | 123.0927 | 76.6983 | 123.1705 | 123.1293 | 123.0927 | 123.0927 | 123.0927 | -123.3994 | -46.3394
4628.7812 | 123.23 | -68.1931 | 54.9042 | -0.17952 | 0.011651 | -0.00044854 | 0.0047702 | -0.012527 | -0.0060775 | -0.0011622 | 54.8721 | 54.9911 | -68.5776 | 55.0507 | 54.8676 | 54.863 | 54.9271 | 55.0186 | 54.95 | 8.4915 | -0.38452 | 0.086975 | 123.0652 | 123.2437 | -0.036621 | 76.6846 | 0.045776 | 123.4497 | 123.1201 | 123.2117 | 123.0606 | 123.1842 | 123.0652 | 123.143 | 123.056 | 76.6846 | 123.1842 | 123.0652 | 123.056 | 123.0606 | 123.143 | -123.4818 | -46.4127
4629.7656 | 123.3215 | -68.2159 | 54.8218 | 0.1638 | 0.011224 | 0.0033967 | 0.0041292 | -0.010177 | -0.0065047 | -0.0032984 | 54.8355 | 54.9454 | -68.5547 | 55.0827 | 54.8767 | 54.8538 | 54.7806 | 55.0369 | 54.9179 | 8.4961 | -0.33875 | 0.1236 | 123.0515 | 123.2986 | 0.054932 | 76.712 | 0.096131 | 123.3902 | 122.9965 | 123.2529 | 123.0927 | 123.1613 | 123.0515 | 123.1338 | 123.0698 | 76.712 | 123.1613 | 123.0515 | 123.0698 | 123.0927 | 123.1338 | -123.3765 | -46.3257
4630.7656 | 123.3261 | -68.2297 | 54.8767 | 0.15617 | 0.012719 | 0.0093781 | 0.003702 | -0.011245 | -0.0052231 | -0.0028712 | 54.8447 | 54.9591 | -68.5547 | 55.0598 | 54.8355 | 54.8447 | 54.7897 | 55.0232 | 54.8859 | 8.4915 | -0.32501 | 0.082397 | 123.0743 | 123.2895 | -0.041199 | 76.7212 | 0.009155 | 123.3994 | 123.0194 | 123.2529 | 123.0652 | 123.1888 | 123.0743 | 123.1155 | 123.0743 | 76.7212 | 123.1888 | 123.0743 | 123.0743 | 123.0652 | 123.1155 | -123.4314 | -46.3852
4631.7656 | 123.3444 | -68.2022 | 54.8264 | 0.23247 | 0.013146 | 0.0016877 | 0.0090426 | -0.0071863 | -0.0080001 | -0.003512 | 54.8996 | 54.9454 | -68.6005 | 55.0919 | 54.8584 | 54.863 | 54.7256 | 55.014 | 54.895 | 8.4961 | -0.39826 | 0.11902 | 123.1018 | 123.2941 | 0.032043 | 76.6983 | 0.068665 | 123.5001 | 122.9279 | 123.2162 | 123.0606 | 123.1476 | 123.1018 | 123.0972 | 123.0652 | 76.6983 | 123.1476 | 123.1018 | 123.0652 | 123.0606 | 123.0972 | -123.4268 | -46.3303
4632.7812 | 123.3307 | -68.1885 | 54.8126 | 0.22484 | 0.012292 | 0.0033967 | 0.003702 | -0.0099633 | -0.0080001 | -0.00073479 | 54.8996 | 54.9133 | -68.5959 | 55.1147 | 54.8996 | 54.9133 | 54.7119 | 55.0507 | 54.9088 | 8.5007 | -0.40741 | 0.10071 | 123.0881 | 123.3032 | 0.086975 | 76.6891 | 0.09613 | 123.4955 | 122.9004 | 123.2391 | 123.0881 | 123.1018 | 123.0881 | 123.0972 | 123.1018 | 76.6891 | 123.1018 | 123.0881 | 123.1018 | 123.0881 | 123.0972 | -123.4085 | -46.312
4633.7656 | 123.2391 | -68.1885 | 54.895 | 0.46898 | 0.012719 | 0.0044647 | 0.0079744 | -0.01274 | -0.0069321 | -0.0047938 | 54.7623 | 55.0232 | -68.605 | 55.0461 | 54.8492 | 54.808 | 54.9774 | 55.0095 | 54.95 | 8.4915 | -0.41656 | 0.12817 | 122.9507 | 123.2346 | -0.045777 | 76.68 | 0.054931 | 123.3673 | 123.1659 | 123.1979 | 123.0377 | 123.2117 | 122.9507 | 123.1384 | 122.9965 | 76.68 | 123.2117 | 122.9507 | 122.9965 | 123.0377 | 123.1384 | -123.5001 | -46.4035
4634.7812 | 123.3673 | -68.2068 | 54.8355 | 0.20195 | 0.010583 | 0.0053193 | 0.0022066 | -0.010177 | -0.0077865 | -0.0024438 | 54.8996 | 54.9271 | -68.5959 | 55.0827 | 54.8904 | 54.8813 | 54.7211 | 55.0369 | 54.8859 | 8.4961 | -0.3891 | 0.091553 | 123.1064 | 123.2895 | 0.054932 | 76.7029 | 0.050354 | 123.4955 | 122.9279 | 123.2437 | 123.0972 | 123.1338 | 123.1064 | 123.0927 | 123.0881 | 76.7029 | 123.1338 | 123.1064 | 123.0881 | 123.0972 | 123.0927 | -123.4314 | -46.3394
4635.7656 | 123.3307 | -68.2022 | 54.863 | 0.19432 | 0.010796 | 0.00040586 | 0.0011386 | -0.0099633 | -0.0045821 | -0.0015894 | 54.8401 | 54.9454 | -68.5776 | 55.069 | 54.8584 | 54.8538 | 54.7852 | 55.0278 | 54.895 | 8.4961 | -0.37537 | 0.082398 | 123.0423 | 123.2712 | -0.004578 | 76.6983 | 0.032044 | 123.4177 | 122.9874 | 123.23 | 123.0606 | 123.1476 | 123.0423 | 123.0972 | 123.056 | 76.6983 | 123.1476 | 123.0423 | 123.056 | 123.0606 | 123.0972 | -123.4406 | -46.3669
4636.7656 | 123.3215 | -68.2022 | 54.8538 | 0.20958 | 0.0097284 | 0.0036103 | 0.001993 | -0.011245 | -0.0058639 | -0.0032984 | 54.8538 | 54.9362 | -68.5867 | 55.0507 | 54.8492 | 54.8584 | 54.7852 | 55.014 | 54.8996 | 8.4961 | -0.38452 | 0.082397 | 123.056 | 123.2529 | -0.004578 | 76.6983 | 0.045776 | 123.4406 | 122.9874 | 123.2162 | 123.0515 | 123.1384 | 123.056 | 123.1018 | 123.0606 | 76.6983 | 123.1384 | 123.056 | 123.0606 | 123.0515 | 123.1018 | -123.4406 | -46.3577
4637.7656 | 123.3032 | -68.1885 | 54.8813 | 0.17143 | 0.009942 | 0.0048921 | 0.0047702 | -0.01274 | -0.0065047 | -0.0020166 | 54.8492 | 54.9088 | -68.573 | 55.0598 | 54.8676 | 54.8538 | 54.7668 | 55.0049 | 54.8813 | 8.4961 | -0.38452 | 0.027465 | 123.0377 | 123.2483 | -0.013733 | 76.6846 | 0 | 123.4222 | 122.9553 | 123.1934 | 123.056 | 123.0972 | 123.0377 | 123.0698 | 123.0423 | 76.6846 | 123.0972 | 123.0377 | 123.0423 | 123.056 | 123.0698 | -123.4543 | -46.3852
4638.7656 | 123.317 | -68.2022 | 54.8584 | 0.25536 | 0.012933 | 0.0051057 | 0.010111 | -0.0091089 | -0.0073593 | -0.0026574 | 54.8584 | 54.982 | -68.605 | 55.0598 | 54.8401 | 54.8172 | 54.7714 | 54.982 | 54.8904 | 8.4915 | -0.40283 | 0.1236 | 123.0606 | 123.262 | -0.01831 | 76.6937 | 0.032044 | 123.4634 | 122.9736 | 123.1842 | 123.0423 | 123.1842 | 123.0606 | 123.0927 | 123.0194 | 76.6937 | 123.1842 | 123.0606 | 123.0194 | 123.0423 | 123.0927 | -123.4634 | -46.3669
4639.7812 | 123.2162 | -68.2434 | 54.8447 | 0.27824 | 0.015496 | 0.0055329 | 0.010965 | -0.0067591 | -0.0056503 | -0.0022302 | 54.8584 | 55.0507 | -68.6188 | 54.9957 | 54.7806 | 54.7577 | 54.9179 | 54.895 | 54.9362 | 8.4869 | -0.37537 | 0.20599 | 123.1018 | 123.2391 | -0.064087 | 76.7303 | 0.091552 | 123.4772 | 123.1613 | 123.1384 | 123.024 | 123.2941 | 123.1018 | 123.1796 | 123.0011 | 76.7303 | 123.2941 | 123.1018 | 123.0011 | 123.024 | 123.1796 | -123.4634 | -46.3577
4640.7812 | 123.3353 | -68.2022 | 54.8492 | 0.26299 | 0.0093012 | 0.0059601 | 0.0051974 | -0.0086817 | -0.0033005 | -0.0022302 | 54.8904 | 54.9545 | -68.6005 | 55.1193 | 54.9866 | 54.9683 | 54.7165 | 55.0507 | 54.895 | 8.4915 | -0.39826 | 0.10529 | 123.0927 | 123.3215 | 0.13733 | 76.6937 | 0.045777 | 123.4909 | 122.9187 | 123.2529 | 123.1888 | 123.1567 | 123.0927 | 123.0972 | 123.1705 | 76.6937 | 123.1567 | 123.0927 | 123.1705 | 123.1888 | 123.0972 | -123.4497 | -46.3577
4641.7812 | 123.3582 | -68.1931 | 54.8538 | 0.20958 | 0.012078 | 0.0072419 | 0.0058382 | -0.0078271 | -0.0058639 | -0.0043664 | 54.9133 | 54.9545 | -68.5822 | 55.101 | 54.8859 | 54.895 | 54.6982 | 55.0369 | 54.8996 | 8.5052 | -0.3891 | 0.10071 | 123.1064 | 123.2941 | 0.032043 | 76.6983 | 0.045776 | 123.4955 | 122.8912 | 123.23 | 123.0789 | 123.1476 | 123.1064 | 123.0927 | 123.0881 | 76.6983 | 123.1476 | 123.1064 | 123.0881 | 123.0789 | 123.0927 | -123.436 | -46.3486
4642.7656 | 123.317 | -68.2159 | 54.8309 | 0.25536 | 0.011651 | 0.0021149 | 0.0047702 | -0.0082545 | -0.0047957 | -0.00094839 | 54.8904 | 54.9683 | -68.5822 | 55.0781 | 54.8813 | 54.8904 | 54.7165 | 55.0415 | 54.9042 | 8.5007 | -0.36621 | 0.13733 | 123.1064 | 123.2941 | 0.050354 | 76.7166 | 0.073242 | 123.4726 | 122.9324 | 123.2574 | 123.0972 | 123.1842 | 123.1064 | 123.1201 | 123.1064 | 76.7166 | 123.1842 | 123.1064 | 123.1064 | 123.0972 | 123.1201 | -123.4131 | -46.3303
4643.7656 | 123.3353 | -68.2114 | 54.8309 | 0.27061 | 0.012078 | 0.0076691 | 0.002634 | -0.010391 | -0.0058639 | -0.00073479 | 54.895 | 54.9728 | -68.5867 | 55.0873 | 54.8859 | 54.8859 | 54.7028 | 55.0461 | 54.8721 | 8.4961 | -0.37537 | 0.14191 | 123.1064 | 123.2986 | 0.054931 | 76.7075 | 0.041198 | 123.4818 | 122.9141 | 123.2574 | 123.0972 | 123.1842 | 123.1064 | 123.0835 | 123.0972 | 76.7075 | 123.1842 | 123.1064 | 123.0972 | 123.0972 | 123.0835 | -123.4177 | -46.3348
4644.7656 | 123.2483 | -68.2388 | 54.8538 | -0.62202 | 0.014642 | 0.0053193 | 0.0084018 | -0.0069727 | -0.0058639 | -0.0030848 | 54.8767 | 55.0232 | -68.6142 | 55.0232 | 54.7943 | 54.7531 | 54.8767 | 54.9408 | 54.9637 | 8.4961 | -0.37537 | 0.16937 | 123.1155 | 123.262 | -0.059509 | 76.7349 | 0.10986 | 123.4909 | 123.1155 | 123.1796 | 123.0331 | 123.262 | 123.1155 | 123.2025 | 122.9919 | 76.7349 | 123.262 | 123.1155 | 122.9919 | 123.0331 | 123.2025 | -123.468 | -46.3577
4645.7656 | 123.2162 | -68.2434 | 54.8859 | 0.19432 | 0.01336 | 0.0076691 | 0.0079744 | -0.0086817 | -0.0054367 | -0.00052119 | 54.8264 | 55.0232 | -68.6234 | 55.0507 | 54.5105 | 54.538 | 55.1788 | 55.0598 | 54.95 | 8.4915 | -0.37994 | 0.13733 | 123.0698 | 123.2941 | -0.37537 | 76.7349 | 0.064087 | 123.4497 | 123.4222 | 123.3032 | 122.7539 | 123.2666 | 123.0698 | 123.1934 | 122.7814 | 76.7349 | 123.2666 | 123.0698 | 122.7814 | 122.7539 | 123.1934 | -123.5092 | -46.3943
4646.7812 | 123.3215 | -68.2343 | 54.8355 | 0.27061 | 0.013574 | 0.0091645 | 0.005411 | -0.0080407 | -0.0043685 | -0.0015894 | 54.8538 | 55.0186 | -68.6005 | 55.0461 | 54.8492 | 54.8401 | 54.7668 | 54.9957 | 54.9133 | 8.4961 | -0.36621 | 0.18311 | 123.0881 | 123.2803 | 0.013733 | 76.7303 | 0.07782 | 123.4543 | 123.0011 | 123.23 | 123.0835 | 123.2529 | 123.0881 | 123.1476 | 123.0743 | 76.7303 | 123.2529 | 123.0881 | 123.0743 | 123.0835 | 123.1476 | -123.436 | -46.3394
4647.7656 | 123.2437 | -68.2388 | 54.8492 | -0.60677 | 0.013146 | 0.0080963 | 0.0075472 | -0.010391 | -0.0071457 | -0.0026574 | 54.8538 | 55.0369 | -68.6142 | 55.0186 | 54.7943 | 54.7577 | 54.8813 | 54.9362 | 54.9728 | 8.4915 | -0.37537 | 0.18768 | 123.0927 | 123.2574 | -0.054931 | 76.7303 | 0.1236 | 123.468 | 123.1201 | 123.175 | 123.0331 | 123.2758 | 123.0927 | 123.2117 | 122.9965 | 76.7303 | 123.2758 | 123.0927 | 122.9965 | 123.0331 | 123.2117 | -123.4634 | -46.3577
4648.7812 | 123.2758 | -68.2388 | 54.8355 | 0.22484 | 0.015283 | 0.0070283 | 0.0066928 | -0.0061181 | -0.0047957 | -0.001803 | 54.8218 | 55.0598 | -68.6142 | 54.9911 | 54.8126 | 54.8172 | 54.8218 | 54.9408 | 54.9088 | 8.4869 | -0.37537 | 0.2243 | 123.0606 | 123.23 | -0.022888 | 76.7258 | 0.073242 | 123.436 | 123.0606 | 123.1796 | 123.0515 | 123.2986 | 123.0606 | 123.1476 | 123.056 | 76.7258 | 123.2986 | 123.0606 | 123.056 | 123.0515 | 123.1476 | -123.4497 | -46.3486
4649.7656 | 123.3627 | -68.1839 | 54.8218 | 0.20195 | 0.009942 | 0.0025421 | 0.0049838 | -0.0078271 | -0.0039413 | -0.00094839 | 54.895 | 54.9911 | -68.5822 | 55.0873 | 54.8676 | 54.8904 | 54.6936 | 55.0415 | 54.8904 | 8.4961 | -0.39825 | 0.16937 | 123.0789 | 123.2712 | 0.045777 | 76.68 | 0.068665 | 123.4772 | 122.8775 | 123.2254 | 123.0515 | 123.175 | 123.0789 | 123.0743 | 123.0743 | 76.68 | 123.175 | 123.0789 | 123.0743 | 123.0515 | 123.0743 | -123.4039 | -46.3257
4650.7656 | 123.3673 | -68.2159 | 54.7852 | 0.10277 | 0.016137 | 0.0042511 | 0.0060518 | -0.0076135 | -0.0028731 | -0.0013758 | 54.8538 | 54.982 | -68.6188 | 55.0781 | 54.8813 | 54.8767 | 54.7302 | 55.0415 | 54.8813 | 8.4915 | -0.40283 | 0.19684 | 123.0698 | 123.2941 | 0.096131 | 76.7075 | 0.096131 | 123.4726 | 122.9462 | 123.2574 | 123.0972 | 123.1979 | 123.0698 | 123.0972 | 123.0927 | 76.7075 | 123.1979 | 123.0698 | 123.0927 | 123.0972 | 123.0972 | -123.4039 | -46.2936
4651.7656 | 123.2162 | -68.2617 | 54.8904 | 0.095139 | 0.013787 | 0.0068147 | 0.0096834 | -0.0067591 | -0.0069321 | -0.0028712 | 54.8309 | 55.0461 | -68.6188 | 54.9774 | 54.7623 | 54.744 | 54.9271 | 54.9225 | 54.9133 | 8.4915 | -0.35706 | 0.15564 | 123.0927 | 123.2391 | -0.12817 | 76.7532 | 0.022888 | 123.4497 | 123.1888 | 123.1842 | 123.024 | 123.3078 | 123.0927 | 123.175 | 123.0057 | 76.7532 | 123.3078 | 123.0927 | 123.0057 | 123.024 | 123.175 | -123.5092 | -46.3989
4652.7656 | 123.2254 | -68.2388 | 54.8721 | 0.13329 | 0.014428 | 0.0076691 | 0.0060518 | -0.0076135 | -0.0056503 | -0.0024438 | 54.8538 | 55.0598 | -68.6005 | 55.0003 | 54.7897 | 54.7485 | 54.9088 | 54.9179 | 54.9591 | 8.4869 | -0.36163 | 0.18768 | 123.0927 | 123.2391 | -0.082397 | 76.7258 | 0.086975 | 123.4543 | 123.1476 | 123.1567 | 123.0286 | 123.2986 | 123.0927 | 123.1979 | 122.9874 | 76.7258 | 123.2986 | 123.0927 | 122.9874 | 123.0286 | 123.1979 | -123.4726 | -46.3852
4653.7812 | 123.262 | -68.2434 | 54.8401 | 0.20958 | 0.014001 | 0.0061737 | 0.0049838 | -0.0095361 | -0.0043685 | -0.0022302 | 54.8172 | 55.0323 | -68.605 | 55.014 | 54.7989 | 54.7897 | 54.8401 | 54.9408 | 54.9362 | 8.4824 | -0.36163 | 0.19226 | 123.0606 | 123.2574 | -0.041199 | 76.7258 | 0.09613 | 123.4222 | 123.0835 | 123.1842 | 123.0423 | 123.2758 | 123.0606 | 123.1796 | 123.0331 | 76.7258 | 123.2758 | 123.0606 | 123.0331 | 123.0423 | 123.1796 | -123.4451 | -46.3577
4654.7812 | 123.2391 | -68.2526 | 54.8492 | 0.18669 | 0.014428 | 0.0055329 | 0.0069064 | -0.0073999 | -0.0024459 | -9.3992e-05 | 54.8401 | 55.0552 | -68.6005 | 54.9911 | 54.7989 | 54.7897 | 54.8584 | 54.9362 | 54.9637 | 8.4961 | -0.3479 | 0.20599 | 123.0927 | 123.2437 | -0.050354 | 76.7487 | 0.11444 | 123.4406 | 123.111 | 123.1888 | 123.0515 | 123.3078 | 123.0927 | 123.2162 | 123.0423 | 76.7487 | 123.3078 | 123.0927 | 123.0423 | 123.0515 | 123.2162 | -123.4497 | -46.3531
4655.7812 | 123.2437 | -68.2571 | 54.8676 | 0.3698 | 0.011865 | 0.0080963 | 0.0051974 | -0.0065455 | -0.0058639 | -0.0026574 | 54.8172 | 55.0552 | -68.6279 | 55.0095 | 54.7943 | 54.7852 | 54.863 | 54.9362 | 54.9545 | 8.4961 | -0.37079 | 0.18768 | 123.0743 | 123.2666 | -0.073242 | 76.7532 | 0.086975 | 123.4451 | 123.1201 | 123.1934 | 123.0515 | 123.3124 | 123.0743 | 123.2117 | 123.0423 | 76.7532 | 123.3124 | 123.0743 | 123.0423 | 123.0515 | 123.2117 | -123.4955 | -46.3715
4656.7656 | 123.349 | -68.2205 | 54.8218 | 0.22484 | 0.014428 | 0.0048921 | 0.0049838 | -0.0078271 | -0.0056503 | -0.00052119 | 54.8721 | 54.9957 | -68.5822 | 55.069 | 54.8676 | 54.8904 | 54.7302 | 55.0323 | 54.9088 | 8.4961 | -0.36163 | 0.17395 | 123.0927 | 123.2895 | 0.045777 | 76.7166 | 0.086975 | 123.4543 | 122.9507 | 123.2529 | 123.0881 | 123.2162 | 123.0927 | 123.1293 | 123.111 | 76.7166 | 123.2162 | 123.0927 | 123.111 | 123.0881 | 123.1293 | -123.4039 | -46.3257
4657.7656 | 123.3582 | -68.2205 | 54.8309 | 0.23247 | 0.014642 | 0.0070283 | 0.0045566 | -0.0084681 | -0.0058639 | 0.00011961 | 54.863 | 55.0232 | -68.6234 | 55.0507 | 54.8538 | 54.863 | 54.7714 | 55.0049 | 54.9042 | 8.4869 | -0.40283 | 0.19226 | 123.0835 | 123.2712 | 0.022888 | 76.7075 | 0.073242 | 123.4863 | 122.9919 | 123.2254 | 123.0743 | 123.2437 | 123.0835 | 123.1247 | 123.0835 | 76.7075 | 123.2437 | 123.0835 | 123.0835 | 123.0743 | 123.1247 | -123.4543 | -46.344
4658.7656 | 123.2254 | -68.2526 | 54.8767 | 0.07988 | 0.015283 | 0.0055329 | 0.0058382 | -0.0093225 | -0.0045821 | -0.0028712 | 54.8492 | 55.0781 | -68.5867 | 55.014 | 54.8035 | 54.7668 | 54.9088 | 54.9454 | 54.95 | 8.4869 | -0.33417 | 0.20142 | 123.1018 | 123.2666 | -0.073242 | 76.7395 | 0.073242 | 123.436 | 123.1613 | 123.1979 | 123.056 | 123.3307 | 123.1018 | 123.2025 | 123.0194 | 76.7395 | 123.3307 | 123.1018 | 123.0194 | 123.056 | 123.2025 | -123.4634 | -46.3898
4659.7656 | 123.2391 | -68.2343 | 54.8767 | 0.07988 | 0.012505 | 0.0091645 | 0.00712 | -0.0078271 | -0.0071457 | -0.0024438 | 54.8676 | 55.0644 | -68.6234 | 55.0186 | 54.8035 | 54.8126 | 54.8996 | 54.95 | 54.95 | 8.4824 | -0.3891 | 0.18768 | 123.1018 | 123.2529 | -0.073242 | 76.7166 | 0.073242 | 123.4909 | 123.1338 | 123.1842 | 123.0377 | 123.2986 | 123.1018 | 123.1842 | 123.0469 | 76.7166 | 123.2986 | 123.1018 | 123.0469 | 123.0377 | 123.1842 | -123.5001 | -46.3943
4660.7656 | 123.2483 | -68.2663 | 54.8859 | 0.10277 | 0.013787 | 0.0085235 | 0.010965 | -0.0071863 | -0.0056503 | -0.00094839 | 54.8218 | 55.0781 | -68.6188 | 54.9774 | 54.7897 | 54.7577 | 54.9088 | 54.9133 | 54.95 | 8.4824 | -0.35248 | 0.19226 | 123.0881 | 123.2437 | -0.09613 | 76.7487 | 0.064087 | 123.4406 | 123.175 | 123.1796 | 123.056 | 123.3444 | 123.0881 | 123.2162 | 123.024 | 76.7487 | 123.3444 | 123.0881 | 123.024 | 123.056 | 123.2162 | -123.5046 | -46.4035
4661.7812 | 123.23 | -68.2297 | 54.8767 | 0.19432 | 0.014214 | 0.0053193 | 0.0030612 | -0.0046229 | -0.0054367 | -0.001803 | 54.8309 | 55.0781 | -68.6508 | 55.0186 | 54.7623 | 54.7943 | 54.9179 | 54.9591 | 54.95 | 8.4824 | -0.42114 | 0.20142 | 123.0606 | 123.2483 | -0.11444 | 76.712 | 0.073242 | 123.4818 | 123.1476 | 123.1888 | 122.9919 | 123.3078 | 123.0606 | 123.1796 | 123.024 | 76.712 | 123.3078 | 123.0606 | 123.024 | 122.9919 | 123.1796 | -123.5275 | -46.3943
4662.7656 | 123.3078 | -68.2205 | 54.8172 | 0.30113 | 0.013787 | 0.0023285 | 0.001993 | -0.0071863 | -0.0050095 | -0.0013758 | 54.8218 | 55.0415 | -68.6234 | 55.0232 | 54.8172 | 54.8264 | 54.7989 | 54.982 | 54.9088 | 8.4824 | -0.40283 | 0.2243 | 123.0423 | 123.2437 | 0 | 76.7029 | 0.091552 | 123.4451 | 123.0194 | 123.2025 | 123.0377 | 123.262 | 123.0423 | 123.1293 | 123.0469 | 76.7029 | 123.262 | 123.0423 | 123.0469 | 123.0377 | 123.1293 | -123.4406 | -46.3348
4663.7656 | 123.2758 | -68.248 | 54.8538 | 0.24773 | 0.014428 | 0.0053193 | 0.005411 | -0.0088953 | -0.0052231 | -0.0013758 | 54.8218 | 55.0507 | -68.6096 | 55.0095 | 54.8035 | 54.7897 | 54.8264 | 54.9637 | 54.9454 | 8.4869 | -0.36163 | 0.19684 | 123.0698 | 123.2574 | -0.050354 | 76.7349 | 0.091553 | 123.4314 | 123.0743 | 123.2117 | 123.0515 | 123.2986 | 123.0698 | 123.1934 | 123.0377 | 76.7349 | 123.2986 | 123.0698 | 123.0377 | 123.0515 | 123.1934 | -123.4634 | -46.3669
4664.7656 | 123.2758 | -68.2434 | 54.863 | 0.19432 | 0.012933 | 0.0051057 | 0.0056246 | -0.0073999 | -0.0062911 | -0.0022302 | 54.8264 | 55.0644 | -68.6234 | 55.014 | 54.7852 | 54.7852 | 54.8584 | 54.9362 | 54.9225 | 8.4869 | -0.37994 | 0.20142 | 123.0698 | 123.2574 | -0.07782 | 76.7303 | 0.059509 | 123.4497 | 123.1018 | 123.1796 | 123.0286 | 123.3078 | 123.0698 | 123.1659 | 123.0286 | 76.7303 | 123.3078 | 123.0698 | 123.0286 | 123.0286 | 123.1659 | -123.4863 | -46.376
4665.7656 | 123.2574 | -68.2343 | 54.895 | 0.026474 | 0.014214 | 0.0048921 | 0.0079744 | -0.010177 | -0.0033005 | -0.00094839 | 54.8996 | 55.0552 | -68.605 | 55.0461 | 54.8355 | 54.8264 | 54.8904 | 55.0003 | 54.9637 | 8.4824 | -0.37079 | 0.16022 | 123.1338 | 123.2803 | -0.05951 | 76.7166 | 0.068664 | 123.5046 | 123.1247 | 123.2346 | 123.0698 | 123.2895 | 123.1338 | 123.1979 | 123.0606 | 76.7166 | 123.2895 | 123.1338 | 123.0606 | 123.0698 | 123.1979 | -123.5001 | -46.4127
4666.7656 | 123.2712 | -68.2205 | 54.8676 | -0.54573 | 0.014855 | 0.0042511 | 0.0069064 | -0.0063317 | -0.0050095 | -0.0039392 | 54.8767 | 55.0735 | -68.5959 | 55.069 | 54.8309 | 54.8584 | 54.8721 | 55.0232 | 54.9591 | 8.4869 | -0.37537 | 0.20599 | 123.0972 | 123.2895 | -0.036621 | 76.7075 | 0.091552 | 123.4726 | 123.0927 | 123.2437 | 123.0515 | 123.2941 | 123.0972 | 123.1796 | 123.0789 | 76.7075 | 123.2941 | 123.0972 | 123.0789 | 123.0515 | 123.1796 | -123.4634 | -46.3806
4667.7812 | 123.2117 | -68.2388 | 54.8904 | 0.087509 | 0.012505 | 0.0093781 | 0.00712 | -0.0063317 | -0.0060775 | -0.00094839 | 54.8676 | 55.0644 | -68.6005 | 54.9957 | 54.7897 | 54.7668 | 54.9133 | 54.9316 | 54.9637 | 8.4869 | -0.36163 | 0.17395 | 123.1064 | 123.2346 | -0.10071 | 76.7258 | 0.073242 | 123.468 | 123.1522 | 123.1705 | 123.0286 | 123.3032 | 123.1064 | 123.2025 | 123.0057 | 76.7258 | 123.3032 | 123.1064 | 123.0057 | 123.0286 | 123.2025 | -123.4909 | -46.4035
4668.7812 | 123.3444 | -68.2297 | 54.8126 | 0.24773 | 0.014855 | 0.0019013 | 0.0039156 | -0.0067591 | -0.0056503 | -0.0026574 | 54.8447 | 55.0003 | -68.6142 | 55.0369 | 54.8401 | 54.8538 | 54.7577 | 55.014 | 54.9316 | 8.5007 | -0.38452 | 0.18768 | 123.0743 | 123.2666 | 0.027466 | 76.7303 | 0.11902 | 123.4589 | 122.9874 | 123.2437 | 123.0698 | 123.23 | 123.0743 | 123.1613 | 123.0835 | 76.7303 | 123.23 | 123.0743 | 123.0835 | 123.0698 | 123.1613 | -123.4268 | -46.312
4669.7656 | 123.2208 | -68.2205 | 54.8721 | 0.22484 | 0.011651 | 0.0040375 | 0.0077608 | -0.010818 | -0.0043685 | -0.0026574 | 54.8126 | 55.0552 | -68.6188 | 55.0461 | 54.8309 | 54.7668 | 54.9591 | 54.95 | 54.9591 | 8.4869 | -0.39825 | 0.18311 | 123.0331 | 123.2666 | -0.041198 | 76.7075 | 0.086975 | 123.4314 | 123.1796 | 123.1705 | 123.0515 | 123.2758 | 123.0331 | 123.1796 | 122.9874 | 76.7075 | 123.2758 | 123.0331 | 122.9874 | 123.0515 | 123.1796 | -123.4909 | -46.3852
4670.7656 | 123.2071 | -68.2617 | 54.808 | 0.18669 | 0.014642 | 0.0027557 | 0.00712 | -0.0069727 | -0.0041549 | -0.0024438 | 54.8264 | 55.069 | -68.6188 | 54.9637 | 54.7714 | 54.7485 | 54.895 | 54.9271 | 54.982 | 8.4915 | -0.35706 | 0.26093 | 123.0881 | 123.2254 | -0.036621 | 76.7532 | 0.17395 | 123.4451 | 123.1567 | 123.1888 | 123.0331 | 123.3307 | 123.0881 | 123.2437 | 123.0103 | 76.7532 | 123.3307 | 123.0881 | 123.0103 | 123.0331 | 123.2437 | -123.4268 | -46.3165
4671.7656 | 123.2437 | -68.2526 | 54.8676 | 0.13329 | 0.012719 | 0.0074555 | 0.0066928 | -0.0063317 | -0.0056503 | -0.00094839 | 54.8264 | 55.0552 | -68.6096 | 54.9774 | 54.7623 | 54.7348 | 54.9042 | 54.9271 | 54.9728 | 8.5007 | -0.35706 | 0.18768 | 123.0789 | 123.23 | -0.10529 | 76.7532 | 0.10529 | 123.436 | 123.1567 | 123.1796 | 123.0148 | 123.3078 | 123.0789 | 123.2254 | 122.9874 | 76.7532 | 123.3078 | 123.0789 | 122.9874 | 123.0148 | 123.2254 | -123.4772 | -46.3669
4672.7656 | 123.2849 | -68.2068 | 54.8904 | -0.11085 | 0.013146 | 0.0029693 | 0.0047702 | -0.0078271 | -0.0052231 | -0.00094839 | 54.8767 | 55.069 | -68.605 | 55.0644 | 54.8676 | 54.8218 | 54.9042 | 55.0278 | 54.9911 | 8.4824 | -0.39825 | 0.17853 | 123.0835 | 123.2712 | -0.022888 | 76.6891 | 0.10071 | 123.4818 | 123.111 | 123.2346 | 123.0743 | 123.2758 | 123.0835 | 123.1979 | 123.0286 | 76.6891 | 123.2758 | 123.0835 | 123.0286 | 123.0743 | 123.1979 | -123.4955 | -46.4081
4673.7812 | 123.2803 | -68.2114 | 54.863 | -0.026932 | 0.014428 | 0.010019 | 0.005411 | -0.0067591 | -0.0043685 | -0.001803 | 54.8996 | 55.0598 | -68.5913 | 55.0507 | 54.8584 | 54.8401 | 54.9088 | 55.0095 | 54.9774 | 8.4778 | -0.37994 | 0.19684 | 123.111 | 123.262 | -0.004578 | 76.6891 | 0.11444 | 123.4909 | 123.1201 | 123.2208 | 123.0698 | 123.2712 | 123.111 | 123.1888 | 123.0515 | 76.6891 | 123.2712 | 123.111 | 123.0515 | 123.0698 | 123.1888 | -123.4543 | -46.3852
4674.7812 | 123.2666 | -68.2297 | 54.8721 | -0.19478 | 0.014642 | 0.0076691 | 0.00712 | -0.0080407 | -0.0058639 | -0.0020166 | 54.9042 | 55.0552 | -68.5867 | 55.0415 | 54.8492 | 54.8218 | 54.895 | 55.0003 | 54.9454 | 8.4869 | -0.35706 | 0.18311 | 123.1338 | 123.2712 | -0.022888 | 76.7166 | 0.073243 | 123.4909 | 123.1247 | 123.23 | 123.0789 | 123.2849 | 123.1338 | 123.175 | 123.0515 | 76.7166 | 123.2849 | 123.1338 | 123.0515 | 123.0789 | 123.175 | -123.4589 | -46.3852
4675.7812 | 123.2712 | -68.2251 | 54.8584 | 0.0035856 | 0.01101 | 0.0033967 | 0.0041292 | -0.0071863 | -0.0060775 | -0.00030759 | 54.8904 | 55.0644 | -68.6005 | 55.0735 | 54.808 | 54.8492 | 54.8721 | 55.0369 | 54.9637 | 8.4915 | -0.37537 | 0.20599 | 123.1155 | 123.2986 | -0.050354 | 76.7166 | 0.10529 | 123.4909 | 123.0972 | 123.262 | 123.0331 | 123.2895 | 123.1155 | 123.1888 | 123.0743 | 76.7166 | 123.2895 | 123.1155 | 123.0743 | 123.0331 | 123.1888 | -123.4589 | -46.3669
4676.7656 | 123.2529 | -68.2251 | 54.8492 | 0.07988 | 0.014214 | 0.0053193 | 0.0047702 | -0.0069727 | -0.0054367 | -0.0011622 | 54.8492 | 55.0552 | -68.6142 | 55.0186 | 54.7806 | 54.7897 | 54.9133 | 54.9591 | 54.9866 | 8.4869 | -0.3891 | 0.20599 | 123.0743 | 123.2437 | -0.068664 | 76.712 | 0.13733 | 123.4634 | 123.1384 | 123.1842 | 123.0057 | 123.2803 | 123.0743 | 123.2117 | 123.0148 | 76.712 | 123.2803 | 123.0743 | 123.0148 | 123.0057 | 123.2117 | -123.4634 | -46.3623
4677.7656 | 123.2574 | -68.2434 | 54.8676 | 0.041733 | 0.01336 | 0.0057465 | 0.0060518 | -0.0065455 | -0.0058639 | -0.0030848 | 54.8813 | 55.0461 | -68.5822 | 55.0186 | 54.8126 | 54.7989 | 54.9042 | 54.9728 | 54.9911 | 8.4961 | -0.33875 | 0.17853 | 123.1247 | 123.262 | -0.054932 | 76.7395 | 0.1236 | 123.4634 | 123.1476 | 123.2162 | 123.056 | 123.2895 | 123.1247 | 123.2346 | 123.0423 | 76.7395 | 123.2895 | 123.1247 | 123.0423 | 123.056 | 123.2346 | -123.4497 | -46.3715
4678.7656 | 123.2529 | -68.2343 | 54.8538 | -0.04219 | 0.014855 | 0.0093781 | 0.00712 | -0.0069727 | -0.0071457 | -0.0015894 | 54.8859 | 55.0644 | -68.6005 | 55.0323 | 54.8309 | 54.8126 | 54.9133 | 54.9637 | 54.9683 | 8.4961 | -0.36621 | 0.21057 | 123.1201 | 123.2666 | -0.022888 | 76.7303 | 0.11444 | 123.4863 | 123.1476 | 123.1979 | 123.0652 | 123.2986 | 123.1201 | 123.2025 | 123.0469 | 76.7303 | 123.2986 | 123.1201 | 123.0469 | 123.0652 | 123.2025 | -123.4543 | -46.3577
4679.7656 | 123.2574 | -68.2297 | 54.9088 | -0.20241 | 0.014428 | 0.0051057 | 0.0034884 | -0.0076135 | -0.0045821 | -0.0013758 | 54.8401 | 55.0552 | -68.6325 | 55.0186 | 54.8309 | 54.8218 | 54.9866 | 55.014 | 55.0095 | 8.4961 | -0.40283 | 0.14648 | 123.0698 | 123.2483 | -0.077819 | 76.7258 | 0.10071 | 123.4726 | 123.2162 | 123.2437 | 123.0606 | 123.2849 | 123.0698 | 123.2391 | 123.0515 | 76.7258 | 123.2849 | 123.0698 | 123.0515 | 123.0606 | 123.2391 | -123.5413 | -46.4127
4680.7812 | 123.262 | -68.2022 | 54.8904 | -0.149 | 0.014642 | 0.0059601 | 0.0056246 | -0.0056909 | -0.0062911 | -0.001803 | 54.8859 | 55.069 | -68.5913 | 55.0598 | 54.8447 | 54.8355 | 54.9545 | 55.0186 | 55.0232 | 8.4961 | -0.3891 | 0.17853 | 123.0881 | 123.262 | -0.045776 | 76.6983 | 0.13275 | 123.4772 | 123.1567 | 123.2208 | 123.0469 | 123.2712 | 123.0881 | 123.2254 | 123.0377 | 76.6983 | 123.2712 | 123.0881 | 123.0377 | 123.0469 | 123.2254 | -123.4818 | -46.3943
4681.7812 | 123.2849 | -68.2205 | 54.8676 | -0.087967 | 0.013574 | 0.0055329 | 0.0047702 | -0.0093225 | -0.0062911 | -0.0022302 | 54.9088 | 55.0415 | -68.5867 | 55.0644 | 54.8492 | 54.8447 | 54.9225 | 55.0186 | 55.0095 | 8.5007 | -0.36621 | 0.17395 | 123.1293 | 123.2849 | -0.018311 | 76.7212 | 0.14191 | 123.4955 | 123.143 | 123.2391 | 123.0698 | 123.262 | 123.1293 | 123.23 | 123.0652 | 76.7212 | 123.262 | 123.1293 | 123.0652 | 123.0698 | 123.23 | -123.4543 | -46.3669
4682.7656 | 123.2437 | -68.2022 | 54.8904 | -0.13374 | 0.013146 | 0.0033967 | 0.0049838 | -0.0067591 | -0.0052231 | -0.0015894 | 54.8355 | 55.0507 | -68.6371 | 55.014 | 54.8401 | 54.7989 | 54.9591 | 55.0003 | 54.982 | 8.4961 | -0.43488 | 0.16022 | 123.0377 | 123.2162 | -0.050354 | 76.6983 | 0.091553 | 123.4726 | 123.1613 | 123.2025 | 123.0423 | 123.2529 | 123.0377 | 123.1842 | 123.0011 | 76.6983 | 123.2529 | 123.0377 | 123.0011 | 123.0423 | 123.1842 | -123.5275 | -46.3943
4683.7656 | 123.2803 | -68.2251 | 54.8538 | -0.44655 | 0.012719 | 0.0051057 | 0.00712 | -0.0073999 | -0.0088547 | -0.0026574 | 54.8721 | 55.0095 | -68.6279 | 55.069 | 54.8401 | 54.8309 | 54.8721 | 55.0049 | 54.9774 | 8.4869 | -0.40283 | 0.15564 | 123.0972 | 123.2941 | -0.013733 | 76.712 | 0.1236 | 123.5001 | 123.0972 | 123.23 | 123.0652 | 123.2346 | 123.0972 | 123.2025 | 123.056 | 76.712 | 123.2346 | 123.0972 | 123.056 | 123.0652 | 123.2025 | -123.4818 | -46.3669
4684.7656 | 123.3078 | -68.2205 | 54.8584 | -0.057449 | 0.01101 | 0.0055329 | 0.0064792 | -0.0052637 | -0.0060775 | -0.0028712 | 54.9042 | 55.0232 | -68.573 | 54.982 | 54.7165 | 54.7943 | 54.9133 | 55.0278 | 54.9774 | 8.5007 | -0.35248 | 0.16479 | 123.1247 | 123.2025 | -0.14191 | 76.7212 | 0.11902 | 123.4772 | 123.1338 | 123.2483 | 122.937 | 123.2437 | 123.1247 | 123.1979 | 123.0148 | 76.7212 | 123.2437 | 123.1247 | 123.0148 | 122.937 | 123.1979 | -123.4314 | -46.3577
4685.7656 | 123.2895 | -68.2205 | 54.8492 | -0.034561 | 0.012078 | 0.0091645 | 0.0032748 | -0.0067591 | -0.0062911 | -0.0043664 | 54.8904 | 55.0598 | -68.5867 | 55.0644 | 54.8492 | 54.8264 | 54.9133 | 55.0232 | 55.0049 | 8.4961 | -0.36621 | 0.21057 | 123.111 | 123.2849 | 0 | 76.7166 | 0.15564 | 123.4772 | 123.1338 | 123.2437 | 123.0698 | 123.2803 | 123.111 | 123.2254 | 123.0469 | 76.7166 | 123.2803 | 123.111 | 123.0469 | 123.0698 | 123.2254 | -123.436 | -46.3531
4686.7812 | 123.2574 | -68.2388 | 54.9042 | -0.12611 | 0.013574 | 0.0066009 | 0.0039156 | -0.0071863 | -0.0054367 | -0.003512 | 54.8309 | 55.0461 | -68.6096 | 55.0323 | 54.8355 | 54.7989 | 54.9683 | 54.9774 | 55.0186 | 8.4915 | -0.37079 | 0.14191 | 123.0698 | 123.2712 | -0.068665 | 76.7303 | 0.11444 | 123.4406 | 123.2071 | 123.2162 | 123.0743 | 123.2849 | 123.0698 | 123.2574 | 123.0377 | 76.7303 | 123.2849 | 123.0698 | 123.0377 | 123.0743 | 123.2574 | -123.5138 | -46.4127
4687.7812 | 123.2574 | -68.2343 | 54.8996 | -0.16426 | 0.012078 | 0.0057465 | -0.00099756 | -0.0080407 | -0.0030869 | -0.0022302 | 54.8264 | 55.0552 | -68.5913 | 54.95 | 54.8172 | 54.808 | 54.95 | 54.982 | 54.9957 | 8.4915 | -0.35706 | 0.15564 | 123.0606 | 123.1842 | -0.082397 | 76.7258 | 0.096131 | 123.4177 | 123.1842 | 123.2162 | 123.0515 | 123.2895 | 123.0606 | 123.23 | 123.0423 | 76.7258 | 123.2895 | 123.0606 | 123.0423 | 123.0515 | 123.23 | -123.4909 | -46.4081
4688.7812 | 123.2666 | -68.2343 | 54.8996 | -0.149 | 0.012719 | 0.0040375 | 0.0047702 | -0.0082545 | -0.0067185 | -0.0020166 | 54.8492 | 55.0644 | -68.573 | 55.0278 | 54.8538 | 54.8172 | 54.9728 | 55.0049 | 54.9911 | 8.4915 | -0.33875 | 0.16479 | 123.0835 | 123.262 | -0.045776 | 76.7258 | 0.091553 | 123.4222 | 123.2071 | 123.2391 | 123.0881 | 123.2986 | 123.0835 | 123.2254 | 123.0515 | 76.7258 | 123.2986 | 123.0835 | 123.0515 | 123.0881 | 123.2254 | -123.4726 | -46.4081
4689.7812 | 123.2346 | -68.1885 | 54.8996 | 0.18669 | 0.010156 | 0.0036103 | 0.0017794 | -0.0099633 | -0.0075729 | -0.0020166 | 54.8401 | 55.0232 | -68.605 | 55.0186 | 54.8355 | 54.7897 | 54.9683 | 55.014 | 55.0232 | 8.4961 | -0.41656 | 0.1236 | 123.0286 | 123.2071 | -0.064087 | 76.6846 | 0.1236 | 123.4451 | 123.1567 | 123.2025 | 123.024 | 123.2117 | 123.0286 | 123.2117 | 122.9782 | 76.6846 | 123.2117 | 123.0286 | 122.9782 | 123.024 | 123.2117 | -123.5046 | -46.4035
4690.7656 | 123.2895 | -68.1839 | 54.8904 | -0.10323 | 0.012933 | 0.0038239 | 0.0062656 | -0.0073999 | -0.0069321 | -0.0011622 | 54.8859 | 55.0369 | -68.5959 | 55.0644 | 54.8538 | 54.8492 | 54.9088 | 55.0049 | 55.0095 | 8.4915 | -0.41199 | 0.14648 | 123.0698 | 123.2483 | -0.036621 | 76.6754 | 0.11902 | 123.4817 | 123.0927 | 123.1888 | 123.0377 | 123.2208 | 123.0698 | 123.1934 | 123.0331 | 76.6754 | 123.2208 | 123.0698 | 123.0331 | 123.0377 | 123.1934 | -123.4863 | -46.3989
4691.7656 | 123.262 | -68.2251 | 54.8996 | -0.19478 | 0.012078 | 0.0070283 | 0.0062656 | -0.0078271 | -0.0086411 | -0.0043664 | 54.8721 | 55.0278 | -68.6005 | 55.0507 | 54.8492 | 54.8309 | 54.9408 | 55.0186 | 55.0415 | 8.4915 | -0.37537 | 0.12817 | 123.0972 | 123.2758 | -0.050354 | 76.7166 | 0.14191 | 123.4726 | 123.1659 | 123.2437 | 123.0743 | 123.2529 | 123.0972 | 123.2666 | 123.056 | 76.7166 | 123.2529 | 123.0972 | 123.056 | 123.0743 | 123.2666 | -123.5001 | -46.4081
4692.7656 | 123.2574 | -68.2526 | 54.9088 | -0.11848 | 0.0093012 | 0.0044647 | 0.0045566 | -0.0069727 | -0.0080001 | -0.0011622 | 54.8492 | 55.0232 | -68.5822 | 55.0369 | 54.8218 | 54.8172 | 54.9591 | 55.0186 | 55.0507 | 8.4915 | -0.32959 | 0.11444 | 123.1018 | 123.2895 | -0.086975 | 76.7441 | 0.14191 | 123.4314 | 123.2117 | 123.2712 | 123.0743 | 123.2758 | 123.1018 | 123.3032 | 123.0698 | 76.7441 | 123.2758 | 123.1018 | 123.0698 | 123.0743 | 123.3032 | -123.4909 | -46.4172
4693.7656 | 123.3261 | -68.1839 | 54.8721 | -0.12611 | 0.010796 | 0.00019226 | -0.0012112 | -0.010391 | -0.0069321 | -0.0037256 | 54.8996 | 54.9637 | -68.5776 | 55.1147 | 54.9271 | 54.895 | 54.8447 | 55.1056 | 54.9911 | 8.4961 | -0.39368 | 0.091553 | 123.0835 | 123.2986 | 0.054932 | 76.68 | 0.11902 | 123.4772 | 123.0286 | 123.2895 | 123.111 | 123.1476 | 123.0835 | 123.175 | 123.0789 | 76.68 | 123.1476 | 123.0835 | 123.0789 | 123.111 | 123.175 | -123.4497 | -46.376
4694.7812 | 123.2941 | -68.1931 | 54.8859 | -0.19478 | 0.011437 | 0.0040375 | -0.00099756 | -0.0095361 | -0.0071457 | -0.0024438 | 54.9133 | 54.9911 | -68.5638 | 55.0735 | 54.8859 | 54.8538 | 54.8813 | 55.0735 | 54.9957 | 8.4961 | -0.37079 | 0.10529 | 123.1064 | 123.2666 | 0 | 76.6891 | 0.10986 | 123.4772 | 123.0743 | 123.2666 | 123.0789 | 123.1842 | 123.1064 | 123.1888 | 123.0469 | 76.6891 | 123.1842 | 123.1064 | 123.0469 | 123.0789 | 123.1888 | -123.4497 | -46.3898
4695.7812 | 123.2483 | -68.2022 | 54.8996 | -0.19478 | 0.010583 | 0.0042511 | 0.004343 | -0.0095361 | -0.0073593 | -0.003512 | 54.8721 | 55.0049 | -68.5959 | 55.0827 | 54.8904 | 54.8172 | 54.9545 | 55.0415 | 55.0186 | 8.5007 | -0.39368 | 0.10529 | 123.0743 | 123.2849 | -0.009155 | 76.7029 | 0.11902 | 123.468 | 123.1567 | 123.2437 | 123.0927 | 123.2071 | 123.0743 | 123.2208 | 123.0194 | 76.7029 | 123.2071 | 123.0743 | 123.0194 | 123.0927 | 123.2208 | -123.4955 | -46.3989
4696.7812 | 123.3078 | -68.1885 | 54.8813 | -0.20241 | 0.012078 | 0.0055329 | 0.0015658 | -0.0088953 | -0.0090683 | -0.0028712 | 54.8904 | 54.9774 | -68.573 | 55.0873 | 54.8767 | 54.8447 | 54.9362 | 55.0598 | 55.0232 | 8.4961 | -0.38452 | 0.09613 | 123.0789 | 123.2758 | -0.004578 | 76.6846 | 0.14191 | 123.4634 | 123.1247 | 123.2483 | 123.0652 | 123.1659 | 123.0789 | 123.2117 | 123.0331 | 76.6846 | 123.1659 | 123.0789 | 123.0331 | 123.0652 | 123.2117 | -123.4543 | -46.3852
4697.7656 | 123.2483 | -68.248 | 54.9088 | -0.26344 | 0.01101 | 0.0057465 | 0.00092504 | -0.0078271 | -0.0058639 | 0.00033321 | 54.8401 | 55.0232 | -68.6005 | 54.9683 | 54.8172 | 54.7989 | 54.9133 | 54.9957 | 55.014 | 8.4915 | -0.35248 | 0.11444 | 123.0881 | 123.2162 | -0.091552 | 76.7395 | 0.10529 | 123.4406 | 123.1613 | 123.2437 | 123.0652 | 123.2712 | 123.0881 | 123.262 | 123.0469 | 76.7395 | 123.2712 | 123.0881 | 123.0469 | 123.0652 | 123.262 | -123.5092 | -46.4172
4698.7656 | 123.262 | -68.2159 | 54.9088 | -0.19478 | 0.009942 | 0.0010467 | 0.0034884 | -0.011672 | -0.0080001 | -0.003512 | 54.8492 | 55.0095 | -68.605 | 55.0461 | 54.8355 | 54.7897 | 54.982 | 55.014 | 55.014 | 8.4869 | -0.3891 | 0.10071 | 123.0652 | 123.262 | -0.073242 | 76.7029 | 0.10529 | 123.4543 | 123.1979 | 123.23 | 123.0515 | 123.2254 | 123.0652 | 123.23 | 123.0057 | 76.7029 | 123.2254 | 123.0652 | 123.0057 | 123.0515 | 123.23 | -123.5138 | -46.4218
4699.7656 | 123.3948 | -68.1564 | 54.8721 | -0.11848 | 0.008233 | -0.0023711 | -0.00099756 | -0.010818 | -0.0056503 | -0.0026574 | 54.9133 | 54.9591 | -68.541 | 55.1468 | 54.9454 | 54.9271 | 54.7623 | 55.1559 | 54.9683 | 8.4961 | -0.38452 | 0.086975 | 123.0698 | 123.3032 | 0.073243 | 76.6525 | 0.096131 | 123.4543 | 122.9187 | 123.3124 | 123.1018 | 123.1155 | 123.0698 | 123.1247 | 123.0835 | 76.6525 | 123.1155 | 123.0698 | 123.0835 | 123.1018 | 123.1247 | -123.4131 | -46.376
4700.7656 | 123.3856 | -68.1702 | 54.863 | -0.0040434 | 0.0095148 | 0.0059601 | 0.0011386 | -0.014663 | -0.0050095 | -0.003512 | 54.8996 | 54.9225 | -68.573 | 55.1147 | 54.9088 | 54.8996 | 54.7668 | 55.1056 | 54.9133 | 8.4961 | -0.40283 | 0.059509 | 123.0698 | 123.2849 | 0.045776 | 76.6663 | 0.050354 | 123.4726 | 122.937 | 123.2758 | 123.0789 | 123.0927 | 123.0698 | 123.0835 | 123.0698 | 76.6663 | 123.0927 | 123.0698 | 123.0698 | 123.0789 | 123.0835 | -123.436 | -46.3669
4701.7812 | 123.3444 | -68.1885 | 54.8859 | -0.30922 | 0.0090876 | 0.00083306 | 0.0039156 | -0.012313 | -0.0071457 | -0.0037256 | 54.9179 | 54.9454 | -68.5547 | 55.1376 | 54.9133 | 54.9088 | 54.8172 | 55.1193 | 54.9133 | 8.4915 | -0.36621 | 0.05951 | 123.1064 | 123.3261 | 0.027466 | 76.68 | 0.027466 | 123.4726 | 123.0057 | 123.3078 | 123.1018 | 123.1339 | 123.1064 | 123.1018 | 123.0972 | 76.68 | 123.1339 | 123.1064 | 123.0972 | 123.1018 | 123.1018 | -123.4406 | -46.3943
4702.7656 | 123.3627 | -68.1885 | 54.8813 | -0.019302 | 0.0086602 | 0.0070283 | 0.0013522 | -0.0121 | -0.0056503 | -0.0037256 | 54.8996 | 54.9133 | -68.5455 | 55.1331 | 54.9362 | 54.9408 | 54.7943 | 55.101 | 54.9225 | 8.4961 | -0.35705 | 0.032043 | 123.0881 | 123.3215 | 0.054931 | 76.6846 | 0.041198 | 123.4451 | 122.9828 | 123.2895 | 123.1247 | 123.1018 | 123.0881 | 123.111 | 123.1293 | 76.6846 | 123.1018 | 123.0881 | 123.1293 | 123.1247 | 123.111 | -123.4268 | -46.3852
4703.7812 | 123.2529 | -68.1564 | 54.8767 | -0.095596 | 0.010369 | 0.0027557 | 0.0022066 | -0.012527 | -0.0056503 | -0.0024438 | 54.9271 | 54.9271 | -68.5455 | 55.1468 | 54.9225 | 54.9042 | 54.8126 | 55.4398 | 54.9774 | 8.5007 | -0.3891 | 0.050354 | 123.0835 | 123.3032 | 0.045776 | 76.6571 | 0.10071 | 123.4726 | 122.9691 | 123.5962 | 123.0789 | 123.0835 | 123.0835 | 123.1339 | 123.0606 | 76.6571 | 123.0835 | 123.0835 | 123.0606 | 123.0789 | 123.1339 | -123.4222 | -46.376
4704.7656 | 123.3261 | -68.2159 | 54.8721 | -0.0040434 | 0.010369 | 0.0021149 | 0.0011386 | -0.011886 | -0.0075729 | -0.0039392 | 54.863 | 54.9362 | -68.6142 | 55.1056 | 54.8859 | 54.8767 | 54.7897 | 55.101 | 54.9133 | 8.5007 | -0.39826 | 0.064087 | 123.0789 | 123.3215 | 0.013733 | 76.7166 | 0.041199 | 123.4772 | 123.0057 | 123.317 | 123.1018 | 123.1522 | 123.0789 | 123.1293 | 123.0927 | 76.7166 | 123.1522 | 123.0789 | 123.0927 | 123.1018 | 123.1293 | -123.4863 | -46.3715
4705.7656 | 123.3536 | -68.1839 | 54.895 | -0.21767 | 0.010369 | -0.00066214 | 0.0017794 | -0.0121 | -0.0073593 | -0.0022302 | 54.9133 | 54.95 | -68.5776 | 55.1514 | 54.9179 | 54.895 | 54.8126 | 55.1193 | 54.9316 | 8.5007 | -0.39368 | 0.054931 | 123.0972 | 123.3353 | 0.022888 | 76.6846 | 0.036621 | 123.4909 | 122.9965 | 123.3032 | 123.1018 | 123.1338 | 123.0972 | 123.1155 | 123.0789 | 76.6846 | 123.1338 | 123.0972 | 123.0789 | 123.1018 | 123.1155 | -123.4726 | -46.3943
4706.7656 | 123.3353 | -68.2022 | 54.863 | 0.12566 | 0.010156 | 0.0014741 | 0.00092504 | -0.012313 | -0.0062911 | -0.0020166 | 54.8447 | 54.9225 | -68.5822 | 55.0964 | 54.8767 | 54.8584 | 54.7943 | 55.0552 | 54.9316 | 8.4915 | -0.37994 | 0.059509 | 123.0469 | 123.2986 | 0.013733 | 76.6937 | 0.068665 | 123.4268 | 122.9965 | 123.2574 | 123.0789 | 123.1247 | 123.0469 | 123.1338 | 123.0606 | 76.6937 | 123.1247 | 123.0469 | 123.0606 | 123.0789 | 123.1338 | -123.4451 | -46.3715
4707.7656 | 123.3124 | -68.2159 | 54.8676 | 0.087509 | 0.012078 | 0.0044647 | 0.0013522 | -0.0121 | -0.0028731 | -0.00094839 | 54.8996 | 54.9408 | -68.5776 | 55.0964 | 54.863 | 54.8401 | 54.7714 | 55.0232 | 54.9316 | 8.4915 | -0.36163 | 0.073242 | 123.1155 | 123.3124 | -0.004578 | 76.7075 | 0.064087 | 123.4772 | 122.9874 | 123.2391 | 123.0789 | 123.1567 | 123.1155 | 123.1476 | 123.056 | 76.7075 | 123.1567 | 123.1155 | 123.056 | 123.0789 | 123.1476 | -123.4451 | -46.376
4708.7812 | 123.3627 | -68.1793 | 54.863 | -0.026932 | 0.0095148 | 0.00040586 | 0.0013522 | -0.014022 | -0.0041549 | -0.0020166 | 54.895 | 54.9316 | -68.573 | 55.1468 | 54.9271 | 54.9133 | 54.7531 | 55.1102 | 54.8859 | 8.4915 | -0.39368 | 0.068665 | 123.0743 | 123.3261 | 0.064087 | 76.6708 | 0.022888 | 123.468 | 122.9324 | 123.2895 | 123.1064 | 123.111 | 123.0743 | 123.0652 | 123.0927 | 76.6708 | 123.111 | 123.0743 | 123.0927 | 123.1064 | 123.0652 | -123.436 | -46.3715
4709.7812 | 123.2117 | -68.2114 | 54.9042 | -0.17952 | 0.014428 | 0.0012605 | 0.0047702 | -0.013168 | -0.0041549 | -0.00052119 | 54.8538 | 55.0186 | -68.5638 | 55.1331 | 55.0507 | 54.8309 | 54.8309 | 54.9271 | 54.9774 | 8.5007 | -0.35248 | 0.11444 | 123.0652 | 123.3444 | 0.14648 | 76.712 | 0.073242 | 123.4177 | 123.0423 | 123.1384 | 123.262 | 123.23 | 123.0652 | 123.1888 | 123.0423 | 76.712 | 123.23 | 123.0652 | 123.0423 | 123.262 | 123.1888 | -123.468 | -46.4035
4710.7812 | 123.3536 | -68.2022 | 54.8676 | -0.019302 | 0.0086602 | 0.0027557 | 0.00028404 | -0.011245 | -0.0067185 | -0.001803 | 54.8538 | 54.9179 | -68.573 | 55.1147 | 54.9088 | 54.8904 | 54.7806 | 55.0781 | 54.9271 | 8.5007 | -0.37079 | 0.050354 | 123.056 | 123.317 | 0.041198 | 76.7029 | 0.059509 | 123.4268 | 122.9828 | 123.2803 | 123.111 | 123.1201 | 123.056 | 123.1293 | 123.0927 | 76.7029 | 123.1201 | 123.056 | 123.0927 | 123.111 | 123.1293 | -123.4406 | -46.3669
4711.7656 | 123.2712 | -68.1747 | 54.8859 | -0.11085 | 0.0097284 | 0.0023285 | 0.0011386 | -0.011459 | -0.0062911 | -0.003512 | 54.9316 | 54.9271 | -68.541 | 55.1788 | 54.9545 | 54.9225 | 54.7852 | 55.1285 | 54.9088 | 8.4961 | -0.36621 | 0.041199 | 123.1064 | 123.3536 | 0.068665 | 76.6708 | 0.022888 | 123.4726 | 122.9599 | 123.3032 | 123.1293 | 123.1018 | 123.1064 | 123.0835 | 123.0972 | 76.6708 | 123.1018 | 123.1064 | 123.0972 | 123.1293 | 123.0835 | -123.4268 | -46.3898
4712.7656 | 123.3902 | -68.1931 | 54.8584 | 0.0035856 | 0.0078058 | 0.0019013 | 0.0011386 | -0.013595 | -0.0056503 | -0.0043664 | 54.9179 | 54.9225 | -68.5501 | 55.1788 | 54.9545 | 54.9408 | 54.7714 | 55.1376 | 54.8904 | 8.5007 | -0.35706 | 0.064087 | 123.111 | 123.3719 | 0.096131 | 76.6937 | 0.032044 | 123.468 | 122.9645 | 123.3307 | 123.1476 | 123.1155 | 123.111 | 123.0835 | 123.1338 | 76.6937 | 123.1155 | 123.111 | 123.1338 | 123.1476 | 123.0835 | -123.4085 | -46.3577
4713.7656 | 123.3078 | -68.1793 | 54.8538 | 0.15617 | 0.0097284 | 0.0055329 | 0.00092504 | -0.011245 | -0.0060775 | -0.0037256 | 54.8447 | 54.8996 | -68.6005 | 55.069 | 54.8538 | 54.8401 | 54.7668 | 55.0278 | 54.9133 | 8.4869 | -0.42114 | 0.045776 | 123.024 | 123.2483 | 0 | 76.6663 | 0.059509 | 123.4451 | 122.9462 | 123.2071 | 123.0331 | 123.0789 | 123.024 | 123.0927 | 123.0194 | 76.6663 | 123.0789 | 123.024 | 123.0194 | 123.0331 | 123.0927 | -123.4543 | -46.3669
4714.7812 | 123.2758 | -68.2205 | 54.8355 | 0.24773 | 0.014214 | 0.0059601 | 0.0094698 | -0.0097497 | -0.0058639 | -0.0039392 | 54.863 | 54.9957 | -68.6188 | 55.0507 | 54.7989 | 54.7806 | 54.8447 | 54.9408 | 54.9179 | 8.4915 | -0.39825 | 0.16022 | 123.0835 | 123.2712 | -0.036621 | 76.712 | 0.082398 | 123.4818 | 123.0652 | 123.1613 | 123.0194 | 123.2162 | 123.0835 | 123.1384 | 123.0011 | 76.712 | 123.2162 | 123.0835 | 123.0011 | 123.0194 | 123.1384 | -123.4543 | -46.344
4715.7656 | 123.3398 | -68.1931 | 54.863 | 0.13329 | 0.0080194 | 0.0061737 | -0.00035676 | -0.011886 | -0.0065047 | -0.0022302 | 54.8538 | 54.9133 | -68.6096 | 55.0735 | 54.8538 | 54.8538 | 54.7806 | 55.0232 | 54.9133 | 8.4961 | -0.41656 | 0.050354 | 123.0469 | 123.2666 | -0.009155 | 76.6891 | 0.050354 | 123.4634 | 122.9736 | 123.2162 | 123.0469 | 123.1064 | 123.0469 | 123.1064 | 123.0469 | 76.6891 | 123.1064 | 123.0469 | 123.0469 | 123.0469 | 123.1064 | -123.4726 | -46.3669
4716.7812 | 123.3261 | -68.1885 | 54.8538 | -0.095596 | 0.0067376 | 0.00083306 | -0.00014316 | -0.0121 | -0.0047957 | -0.0030848 | 54.8218 | 54.9362 | -68.5638 | 55.0781 | 54.8721 | 54.8584 | 54.7943 | 55.0278 | 54.8996 | 8.5007 | -0.37537 | 0.082397 | 123.0103 | 123.2666 | 0.01831 | 76.6891 | 0.045776 | 123.3856 | 122.9828 | 123.2162 | 123.0606 | 123.1247 | 123.0103 | 123.0881 | 123.0469 | 76.6891 | 123.1247 | 123.0103 | 123.0469 | 123.0606 | 123.0881 | -123.4177 | -46.3531
4717.7656 | 123.3582 | -68.1885 | 54.8676 | -0.04219 | 0.010796 | 0.0019013 | 0.0028476 | -0.011886 | -0.0069321 | -0.0039392 | 54.863 | 54.95 | -68.5776 | 55.1285 | 54.9133 | 54.9088 | 54.776 | 55.1056 | 54.9133 | 8.4961 | -0.3891 | 0.082397 | 123.0515 | 123.317 | 0.045776 | 76.6846 | 0.045776 | 123.4406 | 122.9645 | 123.2941 | 123.1018 | 123.1384 | 123.0515 | 123.1018 | 123.0972 | 76.6846 | 123.1384 | 123.0515 | 123.0972 | 123.1018 | 123.1018 | -123.4451 | -46.3715
4718.7656 | 123.3398 | -68.1656 | 54.8492 | 0.0035856 | 0.0088738 | 0.0010467 | 0.0015658 | -0.012954 | -0.0067185 | -0.0011622 | 54.8538 | 54.9408 | -68.5776 | 55.1239 | 54.9225 | 54.9225 | 54.7668 | 55.0827 | 54.9088 | 8.4961 | -0.41199 | 0.091553 | 123.0194 | 123.2895 | 0.073242 | 76.6617 | 0.059509 | 123.4314 | 122.9324 | 123.2483 | 123.0881 | 123.1064 | 123.0194 | 123.0743 | 123.0881 | 76.6617 | 123.1064 | 123.0194 | 123.0881 | 123.0881 | 123.0743 | -123.4268 | -46.3531
4719.7812 | 123.2895 | -68.2205 | 54.8904 | -0.13374 | 0.014214 | 0.0085235 | 0.0086154 | -0.010177 | -0.0065047 | -0.0024438 | 54.9179 | 55.0507 | -68.6005 | 55.1239 | 54.8584 | 54.8264 | 54.9042 | 55.0095 | 54.95 | 8.4961 | -0.37994 | 0.16022 | 123.1384 | 123.3444 | -0.032044 | 76.7166 | 0.059509 | 123.5184 | 123.1247 | 123.23 | 123.0789 | 123.2712 | 123.1384 | 123.1705 | 123.0469 | 76.7166 | 123.2712 | 123.1384 | 123.0469 | 123.0789 | 123.1705 | -123.4909 | -46.3943
4720.7812 | 123.3948 | -68.161 | 54.8676 | -0.026932 | 0.0084466 | 0.0038239 | 0.0015658 | -0.011031 | -0.0082137 | -0.0022302 | 54.9042 | 54.9179 | -68.5776 | 55.1605 | 54.95 | 54.9316 | 54.776 | 55.1468 | 54.9271 | 8.4915 | -0.41656 | 0.050354 | 123.0652 | 123.3215 | 0.082397 | 76.6525 | 0.059509 | 123.4818 | 122.937 | 123.3078 | 123.111 | 123.0789 | 123.0652 | 123.0881 | 123.0927 | 76.6525 | 123.0789 | 123.0652 | 123.0927 | 123.111 | 123.0881 | -123.4451 | -46.376
4721.7812 | 123.3215 | -68.2159 | 54.863 | 0.23247 | 0.010796 | -0.0019439 | 0.0028476 | -0.013595 | -0.0041549 | -0.0013758 | 54.8538 | 54.9133 | -68.5776 | 55.0873 | 54.863 | 54.8676 | 54.7714 | 55.0232 | 54.8767 | 8.4961 | -0.36163 | 0.050354 | 123.0698 | 123.3032 | 0 | 76.712 | 0.013733 | 123.4314 | 122.9874 | 123.2391 | 123.0789 | 123.1293 | 123.0698 | 123.0927 | 123.0835 | 76.712 | 123.1293 | 123.0698 | 123.0835 | 123.0789 | 123.0927 | -123.4406 | -46.3669
4722.7812 | 123.3261 | -68.2068 | 54.8492 | 0.15617 | 0.010796 | 0.0012605 | 0.0013522 | -0.0121 | -0.0041549 | -0.0043664 | 54.8355 | 54.9133 | -68.5867 | 55.069 | 54.8676 | 54.863 | 54.7943 | 55.0278 | 54.9042 | 8.4961 | -0.37994 | 0.064087 | 123.0423 | 123.2758 | 0.018311 | 76.7029 | 0.054932 | 123.4222 | 123.0011 | 123.2346 | 123.0743 | 123.1201 | 123.0423 | 123.111 | 123.0698 | 76.7029 | 123.1201 | 123.0423 | 123.0698 | 123.0743 | 123.111 | -123.436 | -46.3531
4723.7812 | 123.3215 | -68.1839 | 54.863 | 0.15617 | 0.012292 | 0.00061946 | 0.00028404 | -0.010818 | -0.0050095 | -0.0022302 | 54.8355 | 54.9271 | -68.5913 | 55.0735 | 54.8767 | 54.863 | 54.7852 | 55.0186 | 54.8904 | 8.4961 | -0.40741 | 0.064087 | 123.0194 | 123.2574 | 0.013733 | 76.68 | 0.027466 | 123.4268 | 122.9691 | 123.2025 | 123.0606 | 123.111 | 123.0194 | 123.0743 | 123.0469 | 76.68 | 123.111 | 123.0194 | 123.0469 | 123.0606 | 123.0743 | -123.4543 | -46.3669
4724.7812 | 123.2803 | -68.2297 | 54.8767 | -0.12611 | 0.011437 | 0.0038239 | 0.008829 | -0.011459 | -0.0077865 | -0.0041528 | 54.8813 | 55.0095 | -68.5867 | 55.101 | 54.8676 | 54.8355 | 54.9271 | 55.0278 | 54.95 | 8.4915 | -0.35706 | 0.13275 | 123.111 | 123.3307 | -0.009155 | 76.7212 | 0.073242 | 123.468 | 123.1567 | 123.2574 | 123.0972 | 123.2391 | 123.111 | 123.1796 | 123.0652 | 76.7212 | 123.2391 | 123.111 | 123.0652 | 123.0972 | 123.1796 | -123.4634 | -46.3852
4725.7656 | 123.3444 | -68.1931 | 54.8584 | 0.21721 | 0.011865 | -0.00044854 | 0.00049764 | -0.011459 | -0.0067185 | -0.001803 | 54.8218 | 54.9271 | -68.5776 | 55.0873 | 54.8813 | 54.8767 | 54.8035 | 55.0415 | 54.9179 | 8.5052 | -0.38452 | 0.068665 | 123.0148 | 123.2803 | 0.022889 | 76.6983 | 0.05951 | 123.3994 | 122.9965 | 123.2346 | 123.0743 | 123.1201 | 123.0148 | 123.111 | 123.0698 | 76.6983 | 123.1201 | 123.0148 | 123.0698 | 123.0743 | 123.111 | -123.436 | -46.3531
4726.7656 | 123.3124 | -68.2114 | 54.863 | 0.60631 | 0.0093012 | 0.0010467 | 0.0017794 | -0.0091089 | -0.0069321 | -0.0015894 | 54.8172 | 54.9408 | -68.5867 | 55.0827 | 54.8859 | 54.8676 | 54.808 | 55.0369 | 54.8904 | 8.5007 | -0.37537 | 0.07782 | 123.0286 | 123.2941 | 0.022888 | 76.712 | 0.027466 | 123.4039 | 123.0194 | 123.2483 | 123.0972 | 123.1522 | 123.0286 | 123.1018 | 123.0789 | 76.712 | 123.1522 | 123.0286 | 123.0789 | 123.0972 | 123.1018 | -123.4497 | -46.3623
4727.7656 | 123.3673 | -68.2068 | 54.8309 | 0.24773 | 0.012933 | 0.0048921 | 0.0056246 | -0.0088953 | -0.0065047 | -0.003512 | 54.8172 | 54.9042 | -68.6234 | 55.1422 | 54.9133 | 54.8813 | 54.7302 | 55.0323 | 54.8676 | 8.4915 | -0.41656 | 0.073242 | 123.024 | 123.349 | 0.082397 | 76.6983 | 0.036621 | 123.4406 | 122.937 | 123.2391 | 123.1201 | 123.111 | 123.024 | 123.0743 | 123.0881 | 76.6983 | 123.111 | 123.024 | 123.0881 | 123.1201 | 123.0743 | -123.4543 | -46.3394
4728.7812 | 123.349 | -68.1885 | 54.8126 | 0.22484 | 0.012078 | 0.0042511 | 0.0039156 | -0.011245 | -0.0060775 | -0.0039392 | 54.8859 | 54.9042 | -68.605 | 55.1056 | 54.895 | 54.8721 | 54.7165 | 55.0369 | 54.895 | 8.5052 | -0.41656 | 0.091553 | 123.0743 | 123.2941 | 0.082398 | 76.6937 | 0.082398 | 123.4909 | 122.905 | 123.2254 | 123.0835 | 123.0927 | 123.0743 | 123.0835 | 123.0606 | 76.6937 | 123.0927 | 123.0743 | 123.0606 | 123.0835 | 123.0835 | -123.4177 | -46.3074
4729.7812 | 123.317 | -68.2159 | 54.8538 | 0.18669 | 0.010796 | 0.0036103 | 0.0028476 | -0.011245 | -0.0041549 | -0.001803 | 54.8538 | 54.9179 | -68.6096 | 55.0781 | 54.863 | 54.8721 | 54.776 | 55.0323 | 54.8676 | 8.4961 | -0.39368 | 0.064087 | 123.0698 | 123.2941 | 0.009155 | 76.712 | 0.013733 | 123.4634 | 122.9919 | 123.2483 | 123.0789 | 123.1338 | 123.0698 | 123.0835 | 123.0881 | 76.712 | 123.1338 | 123.0698 | 123.0881 | 123.0789 | 123.0835 | -123.4634 | -46.3577
4730.7812 | 123.3261 | -68.1976 | 54.863 | 0.20195 | 0.011651 | 0.0038239 | 0.004343 | -0.012954 | -0.0067185 | -0.0015894 | 54.8676 | 54.9545 | -68.5959 | 55.0735 | 54.8584 | 54.8676 | 54.7531 | 55.0186 | 54.8859 | 8.4961 | -0.39825 | 0.091553 | 123.0652 | 123.2712 | -0.004578 | 76.6937 | 0.022888 | 123.4634 | 122.9507 | 123.2162 | 123.056 | 123.1522 | 123.0652 | 123.0835 | 123.0652 | 76.6937 | 123.1522 | 123.0652 | 123.0652 | 123.056 | 123.0835 | -123.4589 | -46.3669
4731.7656 | 123.3353 | -68.1839 | 54.863 | 0.6292 | 0.011224 | 0.0068147 | -0.00014316 | -0.011672 | -0.0058639 | -0.0032984 | 54.8447 | 54.9637 | -68.573 | 55.0598 | 54.8859 | 54.8538 | 54.8172 | 55.0369 | 54.9042 | 8.4915 | -0.3891 | 0.10071 | 123.0286 | 123.2437 | 0.022888 | 76.6754 | 0.041199 | 123.4177 | 123.0011 | 123.2208 | 123.0698 | 123.1476 | 123.0286 | 123.0881 | 123.0377 | 76.6754 | 123.1476 | 123.0286 | 123.0377 | 123.0698 | 123.0881 | -123.436 | -46.3715
4732.7656 | 123.3215 | -68.1976 | 54.8721 | 0.07988 | 0.010369 | 0.0025421 | 0.0034884 | -0.0086817 | -0.0062911 | -0.0011622 | 54.8492 | 54.9316 | -68.5822 | 55.0644 | 54.8813 | 54.8676 | 54.8264 | 55.0415 | 54.9133 | 8.4869 | -0.38452 | 0.05951 | 123.0469 | 123.262 | 0.009156 | 76.6846 | 0.041199 | 123.4314 | 123.024 | 123.2391 | 123.0789 | 123.1293 | 123.0469 | 123.111 | 123.0652 | 76.6846 | 123.1293 | 123.0469 | 123.0652 | 123.0789 | 123.111 | -123.4543 | -46.3852
4733.7656 | 123.3444 | -68.2022 | 54.8447 | 0.11803 | 0.010796 | 0.0098053 | 0.0022066 | -0.011245 | -0.0054367 | -0.0037256 | 54.8401 | 54.9637 | -68.5913 | 55.0873 | 54.8126 | 54.9728 | 54.7165 | 55.014 | 54.9133 | 8.4961 | -0.3891 | 0.11902 | 123.0423 | 123.2895 | -0.032044 | 76.6983 | 0.068664 | 123.4314 | 122.9187 | 123.2162 | 123.0148 | 123.1659 | 123.0423 | 123.1155 | 123.175 | 76.6983 | 123.1659 | 123.0423 | 123.175 | 123.0148 | 123.1155 | -123.436 | -46.3486
4734.7656 | 123.4131 | -68.1839 | 54.8355 | 0.2935 | 0.011224 | 0.0083099 | 0.0069064 | -0.012313 | -0.0052231 | -0.00073479 | 54.8996 | 54.9454 | -68.6096 | 55.1056 | 54.8996 | 54.8904 | 54.4693 | 54.863 | 54.8767 | 8.5052 | -0.42572 | 0.10986 | 123.0835 | 123.2895 | 0.064087 | 76.6891 | 0.041199 | 123.5092 | 122.6532 | 123.0469 | 123.0835 | 123.1293 | 123.0835 | 123.0606 | 123.0743 | 76.6891 | 123.1293 | 123.0835 | 123.0743 | 123.0835 | 123.0606 | -123.4451 | -46.3303
4735.7812 | 123.3765 | -68.2068 | 54.863 | 0.21721 | 0.010796 | 0.0031831 | 0.004343 | -0.010177 | -0.0060775 | -0.0013758 | 54.895 | 54.9179 | -68.6005 | 55.101 | 54.8813 | 54.8813 | 54.7073 | 55.0507 | 54.8996 | 8.5007 | -0.39368 | 0.054932 | 123.1018 | 123.3078 | 0.018311 | 76.7075 | 0.036621 | 123.4955 | 122.9141 | 123.2574 | 123.0881 | 123.1247 | 123.1018 | 123.1064 | 123.0881 | 76.7075 | 123.1247 | 123.1018 | 123.0881 | 123.0881 | 123.1064 | -123.4634 | -46.3623
4736.7812 | 123.3353 | -68.2159 | 54.8309 | 0.2401 | 0.010583 | 0.0042511 | 0.0022066 | -0.011245 | -0.0075729 | -0.00094839 | 54.8676 | 54.9225 | -68.5959 | 55.0827 | 54.8584 | 54.863 | 54.7623 | 55.0186 | 54.8584 | 8.4961 | -0.37994 | 0.091552 | 123.0835 | 123.2986 | 0.027465 | 76.712 | 0.027465 | 123.4634 | 122.9782 | 123.2346 | 123.0743 | 123.1384 | 123.0835 | 123.0743 | 123.0789 | 76.712 | 123.1384 | 123.0835 | 123.0789 | 123.0743 | 123.0743 | -123.4268 | -46.3348
4737.7812 | 123.3398 | -68.2068 | 54.8355 | 0.17906 | 0.011437 | 0.0031831 | 0.0041292 | -0.011031 | -0.0047957 | -0.0032984 | 54.8767 | 54.9225 | -68.6005 | 55.0919 | 54.8676 | 54.8676 | 54.7394 | 55.0232 | 54.8767 | 8.5007 | -0.39368 | 0.086975 | 123.0835 | 123.2986 | 0.032044 | 76.7075 | 0.041199 | 123.4772 | 122.9462 | 123.23 | 123.0743 | 123.1293 | 123.0835 | 123.0835 | 123.0743 | 76.7075 | 123.1293 | 123.0835 | 123.0743 | 123.0743 | 123.0835 | -123.436 | -46.3348
4738.7656 | 123.3124 | -68.1747 | 54.8492 | 0.12566 | 0.01101 | 0.00040586 | 0.0028476 | -0.0091089 | -0.0073593 | -0.0020166 | 54.8355 | 54.95 | -68.5959 | 55.0598 | 54.8859 | 54.8721 | 54.8218 | 55.0415 | 54.9362 | 8.5007 | -0.42114 | 0.10071 | 123.0103 | 123.2346 | 0.036621 | 76.6754 | 0.086975 | 123.4314 | 122.9965 | 123.2162 | 123.0606 | 123.1247 | 123.0103 | 123.111 | 123.0469 | 76.6754 | 123.1247 | 123.0103 | 123.0469 | 123.0606 | 123.111 | -123.4451 | -46.3486
4739.7656 | 123.3215 | -68.2114 | 54.8676 | 0.11803 | 0.0086602 | 0.0010467 | -0.00014316 | -0.011031 | -0.0054367 | -0.0054346 | 54.8447 | 54.9271 | -68.5867 | 55.2246 | 54.9133 | 54.8264 | 54.7806 | 55.0095 | 54.895 | 8.4869 | -0.37537 | 0.059509 | 123.056 | 123.436 | 0.045776 | 76.6983 | 0.027466 | 123.4314 | 122.9919 | 123.2208 | 123.1247 | 123.1384 | 123.056 | 123.1064 | 123.0377 | 76.6983 | 123.1384 | 123.056 | 123.0377 | 123.1247 | 123.1064 | -123.4543 | -46.3806
4740.7656 | 123.3353 | -68.1839 | 54.8767 | 0.14092 | 0.012719 | 0.0029693 | 0.001993 | -0.0099633 | -0.0067185 | -0.00073479 | 54.8492 | 54.9545 | -68.5776 | 55.0735 | 54.8584 | 54.8584 | 55.0186 | 55.0964 | 54.9545 | 8.4915 | -0.39368 | 0.07782 | 123.0331 | 123.2574 | -0.018311 | 76.6754 | 0.07782 | 123.4268 | 123.2025 | 123.2803 | 123.0423 | 123.1384 | 123.0331 | 123.1384 | 123.0423 | 76.6754 | 123.1384 | 123.0331 | 123.0423 | 123.0423 | 123.1384 | -123.4543 | -46.3852
4741.7656 | 123.317 | -68.2251 | 54.8126 | 0.2935 | 0.013787 | 0.0048921 | 0.0084018 | -0.0078271 | -0.0050095 | -0.0037256 | 54.9133 | 54.9362 | -68.6142 | 55.1147 | 54.8813 | 54.8859 | 54.7028 | 55.0507 | 54.8492 | 8.4961 | -0.3891 | 0.1236 | 123.1384 | 123.3398 | 0.068665 | 76.7212 | 0.036621 | 123.5275 | 122.9279 | 123.2758 | 123.1064 | 123.1613 | 123.1384 | 123.0743 | 123.111 | 76.7212 | 123.1613 | 123.1384 | 123.111 | 123.1064 | 123.0743 | -123.4268 | -46.3165
4742.7812 | 123.3444 | -68.1976 | 54.8355 | 0.27061 | 0.01101 | 0.0019013 | 0.0030612 | -0.010177 | -0.0062911 | -0.0043664 | 54.8996 | 54.9179 | -68.5913 | 55.101 | 54.8813 | 54.8859 | 54.7073 | 55.0598 | 54.8859 | 8.4961 | -0.39368 | 0.082398 | 123.0972 | 123.2986 | 0.045777 | 76.6937 | 0.050354 | 123.4909 | 122.905 | 123.2574 | 123.0789 | 123.1155 | 123.0972 | 123.0835 | 123.0835 | 76.6937 | 123.1155 | 123.0972 | 123.0835 | 123.0789 | 123.0835 | -123.4268 | -46.3394
4743.7812 | 123.349 | -68.2022 | 54.8538 | 0.22484 | 0.013146 | -0.0025847 | 0.0030612 | -0.0093225 | -0.0062911 | -0.0024438 | 54.8676 | 54.9271 | -68.573 | 55.0827 | 54.863 | 54.8538 | 54.7577 | 55.0232 | 54.8996 | 8.4915 | -0.37079 | 0.073242 | 123.0698 | 123.2849 | 0.009155 | 76.6937 | 0.045776 | 123.4406 | 122.9599 | 123.2254 | 123.0652 | 123.1293 | 123.0698 | 123.1018 | 123.056 | 76.6937 | 123.1293 | 123.0698 | 123.056 | 123.0652 | 123.1018 | -123.4268 | -46.3623
4744.7812 | 123.3353 | -68.2159 | 54.8492 | 0.22484 | 0.0097284 | 0.0076691 | 0.003702 | -0.0097497 | -0.0082137 | -0.00030759 | 54.8904 | 54.9454 | -68.5822 | 55.0919 | 54.8813 | 54.8538 | 54.7485 | 55.014 | 54.8584 | 8.5007 | -0.36621 | 0.096131 | 123.1064 | 123.3078 | 0.032044 | 76.7166 | 0.009155 | 123.4726 | 122.9645 | 123.23 | 123.0972 | 123.1613 | 123.1064 | 123.0743 | 123.0698 | 76.7166 | 123.1613 | 123.1064 | 123.0698 | 123.0972 | 123.0743 | -123.4314 | -46.3486
4745.7656 | 123.3353 | -68.1885 | 54.8401 | 0.095139 | 0.010583 | 0.00019226 | -0.0022794 | -0.011672 | -0.0047957 | -0.0030848 | 54.8401 | 54.95 | -68.5959 | 55.069 | 54.8584 | 54.8492 | 54.7897 | 55.0507 | 54.9225 | 8.4961 | -0.40741 | 0.10986 | 123.0286 | 123.2574 | 0.01831 | 76.6846 | 0.082397 | 123.436 | 122.9782 | 123.2391 | 123.0469 | 123.1384 | 123.0286 | 123.111 | 123.0377 | 76.6846 | 123.1384 | 123.0286 | 123.0377 | 123.0469 | 123.111 | -123.436 | -46.344
4746.7656 | 123.3215 | -68.2297 | 54.863 | 0.10277 | 0.010796 | 0.0042511 | 0.0030612 | -0.011886 | -0.0069321 | -0.0024438 | 54.8538 | 54.9728 | -68.605 | 55.0781 | 54.8813 | 54.8492 | 54.8538 | 55.2017 | 54.9133 | 8.4961 | -0.37537 | 0.10986 | 123.0835 | 123.3078 | 0.018311 | 76.7258 | 0.050354 | 123.4589 | 123.0835 | 123.4314 | 123.111 | 123.2025 | 123.0835 | 123.143 | 123.0789 | 76.7258 | 123.2025 | 123.0835 | 123.0789 | 123.111 | 123.143 | -123.468 | -46.3669
4747.7656 | 123.3261 | -68.2022 | 54.8676 | 0.095139 | 0.011224 | 0.0042511 | 0.0022066 | -0.011459 | -0.0047957 | -0.0024438 | 54.8538 | 54.95 | -68.605 | 55.0919 | 54.8538 | 54.8401 | 54.7943 | 55.0232 | 54.8859 | 8.4961 | -0.40283 | 0.082397 | 123.056 | 123.2941 | -0.013733 | 76.6983 | 0.01831 | 123.4589 | 122.9965 | 123.2254 | 123.056 | 123.1522 | 123.056 | 123.0881 | 123.0423 | 76.6983 | 123.1522 | 123.056 | 123.0423 | 123.056 | 123.0881 | -123.4726 | -46.3715
4748.7656 | 123.349 | -68.1885 | 54.8447 | 0.21721 | 0.013146 | 0.0048921 | 0.0064792 | -0.0071863 | -0.0052231 | -0.003512 | 54.9042 | 54.95 | -68.5959 | 55.1147 | 54.8904 | 54.8767 | 54.7028 | 55.0415 | 54.8538 | 8.4961 | -0.40741 | 0.10529 | 123.0927 | 123.3032 | 0.045776 | 76.6846 | 0.009155 | 123.5001 | 122.8912 | 123.23 | 123.0789 | 123.1384 | 123.0927 | 123.0423 | 123.0652 | 76.6846 | 123.1384 | 123.0927 | 123.0652 | 123.0789 | 123.0423 | -123.4406 | -46.3486
4749.7812 | 123.349 | -68.2251 | 54.8309 | 0.24773 | 0.010156 | 0.0025421 | 0.003702 | -0.0097497 | -0.0080001 | -0.0022302 | 54.8904 | 54.95 | -68.5913 | 55.0964 | 54.8721 | 54.8676 | 54.7394 | 55.0278 | 54.8767 | 8.5007 | -0.36621 | 0.11902 | 123.1155 | 123.3215 | 0.041198 | 76.7258 | 0.045776 | 123.4818 | 122.9645 | 123.2529 | 123.0972 | 123.175 | 123.1155 | 123.1018 | 123.0927 | 76.7258 | 123.175 | 123.1155 | 123.0927 | 123.0972 | 123.1018 | -123.4222 | -46.3303
4750.7812 | 123.349 | -68.2022 | 54.8447 | 0.22484 | 0.01101 | 0.0014741 | 0.004343 | -0.011459 | -0.0052231 | -0.00052119 | 54.8721 | 54.9408 | -68.573 | 55.101 | 54.8767 | 54.895 | 54.7073 | 55.0232 | 54.8767 | 8.4869 | -0.37079 | 0.09613 | 123.0743 | 123.3032 | 0.032043 | 76.6891 | 0.032043 | 123.4451 | 122.9095 | 123.2254 | 123.0789 | 123.143 | 123.0743 | 123.0789 | 123.0972 | 76.6891 | 123.143 | 123.0743 | 123.0972 | 123.0789 | 123.0789 | -123.4177 | -46.3577
4751.7812 | 123.3673 | -68.2114 | 54.8035 | 0.17906 | 0.010583 | 0.0023285 | 0.0028476 | -0.0091089 | -0.0052231 | -0.001803 | 54.895 | 54.9454 | -68.5867 | 55.0827 | 54.895 | 54.8813 | 54.7256 | 55.0507 | 54.8721 | 8.5007 | -0.37537 | 0.14191 | 123.1064 | 123.2941 | 0.091553 | 76.712 | 0.068664 | 123.4818 | 122.937 | 123.262 | 123.1064 | 123.1567 | 123.1064 | 123.0835 | 123.0927 | 76.712 | 123.1567 | 123.1064 | 123.0927 | 123.1064 | 123.0835 | -123.3902 | -46.3028
4752.7656 | 123.2986 | -68.2159 | 54.8447 | 0.14854 | 0.014214 | 0.0016877 | 0.00092504 | -0.013809 | -0.0067185 | -0.003512 | 54.8309 | 54.9591 | -68.5867 | 55.0735 | 54.8538 | 54.8676 | 54.7943 | 55.0186 | 54.9088 | 8.4869 | -0.37079 | 0.11444 | 123.0469 | 123.2895 | 0.009155 | 76.7029 | 0.064086 | 123.4177 | 123.0103 | 123.2346 | 123.0698 | 123.175 | 123.0469 | 123.1247 | 123.0835 | 76.7029 | 123.175 | 123.0469 | 123.0835 | 123.0698 | 123.1247 | -123.4314 | -46.3577
4753.7656 | 123.317 | -68.2205 | 54.8447 | 0.17143 | 0.011651 | 0.0019013 | 0.0032748 | -0.0097497 | -0.0041549 | -0.0013758 | 54.8492 | 54.9362 | -68.605 | 55.0827 | 54.8492 | 54.8401 | 54.7714 | 55.0278 | 54.8813 | 8.4824 | -0.38452 | 0.091552 | 123.0698 | 123.3032 | 0.004577 | 76.7029 | 0.036621 | 123.4543 | 122.9919 | 123.2483 | 123.0698 | 123.1567 | 123.0698 | 123.1018 | 123.0606 | 76.7029 | 123.1567 | 123.0698 | 123.0606 | 123.0698 | 123.1018 | -123.4497 | -46.3623
4754.7656 | 123.3582 | -68.2068 | 54.8264 | 0.26299 | 0.011651 | 0.0029693 | 0.010324 | -0.0091089 | -0.0043685 | -0.0022302 | 54.8721 | 54.9774 | -68.6142 | 55.0781 | 54.863 | 54.8492 | 54.7485 | 55.0186 | 54.895 | 8.4869 | -0.40741 | 0.15106 | 123.0789 | 123.2849 | 0.036621 | 76.6937 | 0.068665 | 123.4863 | 122.9553 | 123.2254 | 123.0698 | 123.1842 | 123.0789 | 123.1018 | 123.056 | 76.6937 | 123.1842 | 123.0789 | 123.056 | 123.0698 | 123.1018 | -123.4406 | -46.3394
4755.7656 | 123.3124 | -68.2388 | 54.8447 | 0.27824 | 0.013574 | 0.0014741 | 0.0079744 | -0.0082545 | -0.0056503 | -0.001803 | 54.8538 | 55.0049 | -68.6096 | 55.0644 | 54.8172 | 54.8401 | 54.7897 | 54.982 | 54.9042 | 8.4915 | -0.37079 | 0.16022 | 123.0927 | 123.3032 | -0.027466 | 76.7303 | 0.059509 | 123.4634 | 123.0286 | 123.2208 | 123.056 | 123.2437 | 123.0927 | 123.143 | 123.0789 | 76.7303 | 123.2437 | 123.0927 | 123.0789 | 123.056 | 123.143 | -123.4543 | -46.3531
4756.7812 | 123.3582 | -68.2297 | 54.8264 | -0.32448 | 0.012078 | 0.0053193 | 0.0047702 | -0.0099633 | -0.0052231 | -0.0015894 | 54.9957 | 54.95 | -68.5867 | 55.1239 | 54.895 | 54.895 | 54.6936 | 55.0507 | 54.9225 | 8.4961 | -0.35706 | 0.1236 | 123.2254 | 123.3536 | 0.068665 | 76.7258 | 0.09613 | 123.5825 | 122.9233 | 123.2803 | 123.1247 | 123.1796 | 123.2254 | 123.1522 | 123.1247 | 76.7258 | 123.1796 | 123.2254 | 123.1247 | 123.1247 | 123.1522 | -123.4131 | -46.3303
4757.7812 | 123.381 | -68.1931 | 54.8401 | 0.25536 | 0.012078 | 0.0059601 | 0.0049838 | -0.0088953 | -0.0043685 | -0.0039392 | 54.9042 | 54.9408 | -68.5776 | 54.9362 | 54.9545 | 54.9683 | 54.7897 | 55.0644 | 54.9042 | 8.4869 | -0.38452 | 0.10071 | 123.0972 | 123.1293 | 0.11444 | 76.68 | 0.064087 | 123.4818 | 122.9828 | 123.2574 | 123.1476 | 123.1338 | 123.0972 | 123.0972 | 123.1613 | 76.68 | 123.1338 | 123.0972 | 123.1613 | 123.1476 | 123.0972 | -123.4177 | -46.3531
4758.7812 | 123.3627 | -68.2205 | 54.8264 | 0.14854 | 0.013146 | 0.0016877 | 0.0039156 | -0.0086817 | -0.0039413 | -0.0022302 | 54.9088 | 54.95 | -68.5959 | 55.1102 | 54.895 | 54.8996 | 54.7119 | 55.0461 | 54.8767 | 8.5007 | -0.37537 | 0.1236 | 123.1293 | 123.3307 | 0.068665 | 76.7212 | 0.050354 | 123.5046 | 122.9324 | 123.2666 | 123.1155 | 123.1705 | 123.1293 | 123.0972 | 123.1201 | 76.7212 | 123.1705 | 123.1293 | 123.1201 | 123.1155 | 123.0972 | -123.4222 | -46.3257
4759.7656 | 123.3398 | -68.2251 | 54.8172 | 0.18669 | 0.011651 | 0.0063873 | 0.0032748 | -0.0097497 | -0.0054367 | -0.0020166 | 54.9042 | 54.982 | -68.5822 | 55.0919 | 54.8904 | 54.8767 | 54.7256 | 55.0278 | 54.8676 | 8.4961 | -0.35706 | 0.16479 | 123.1293 | 123.317 | 0.073242 | 76.7212 | 0.050354 | 123.4863 | 122.9507 | 123.2529 | 123.1155 | 123.2071 | 123.1293 | 123.0927 | 123.1018 | 76.7212 | 123.2071 | 123.1293 | 123.1018 | 123.1155 | 123.0927 | -123.3994 | -46.3211
4760.7656 | 123.3719 | -68.2068 | 54.808 | 0.19432 | 0.011865 | 0.0025421 | 0.003702 | -0.010177 | -0.0058639 | -0.0022302 | 54.9133 | 54.95 | -68.5822 | 55.0919 | 54.8859 | 54.8996 | 54.7211 | 55.0507 | 54.8676 | 8.5007 | -0.37537 | 0.14191 | 123.1201 | 123.2986 | 0.07782 | 76.7075 | 0.05951 | 123.4955 | 122.9279 | 123.2574 | 123.0927 | 123.1567 | 123.1201 | 123.0743 | 123.1064 | 76.7075 | 123.1567 | 123.1201 | 123.1064 | 123.0927 | 123.0743 | -123.3902 | -46.3074
4761.7656 | 123.2391 | -68.2571 | 54.8721 | 0.1638 | 0.013574 | 0.0059601 | 0.0090426 | -0.0097497 | -0.0062911 | -0.0032984 | 54.8676 | 55.0461 | -68.6096 | 55.0278 | 54.8126 | 54.776 | 54.8859 | 54.9362 | 54.9225 | 8.4915 | -0.35248 | 0.17395 | 123.1247 | 123.2849 | -0.059509 | 76.7487 | 0.050354 | 123.4772 | 123.143 | 123.1934 | 123.0698 | 123.3032 | 123.1247 | 123.1796 | 123.0331 | 76.7487 | 123.3032 | 123.1247 | 123.0331 | 123.0698 | 123.1796 | -123.4818 | -46.3806
4762.7812 | 123.3215 | -68.2526 | 54.8309 | 0.2401 | 0.01571 | -0.00023494 | 0.0086154 | -0.0084681 | -0.0067185 | -0.0024438 | 54.8401 | 55.014 | -68.6508 | 55.0415 | 54.8172 | 54.8126 | 54.8309 | 54.9637 | 54.9271 | 8.5007 | -0.39826 | 0.1831 | 123.0927 | 123.2941 | -0.013733 | 76.7532 | 0.09613 | 123.4909 | 123.0835 | 123.2162 | 123.0698 | 123.2666 | 123.0927 | 123.1796 | 123.0652 | 76.7532 | 123.2666 | 123.0927 | 123.0652 | 123.0698 | 123.1796 | -123.4818 | -46.3303
4763.7812 | 123.3307 | -68.2205 | 54.8492 | 0.27824 | 0.011437 | 0.0059601 | 0.0058382 | -0.0071863 | -0.0056503 | -0.0011622 | 54.863 | 54.9637 | -68.6234 | 55.0735 | 54.8538 | 54.8721 | 54.7256 | 55.0186 | 54.9042 | 8.5007 | -0.40283 | 0.11444 | 123.0835 | 123.2941 | 0.004578 | 76.7212 | 0.054932 | 123.4863 | 122.9462 | 123.2391 | 123.0743 | 123.1842 | 123.0835 | 123.1247 | 123.0927 | 76.7212 | 123.1842 | 123.0835 | 123.0927 | 123.0743 | 123.1247 | -123.4726 | -46.3486
4764.7812 | 123.3124 | -68.2251 | 54.8355 | 0.27061 | 0.014214 | 0.0055329 | 0.0079744 | -0.0065455 | -0.0045821 | -0.0028712 | 54.8447 | 55.0003 | -68.605 | 55.0552 | 54.8309 | 54.8264 | 54.7943 | 54.982 | 54.9179 | 8.4915 | -0.37994 | 0.16479 | 123.0698 | 123.2803 | -0.004577 | 76.7166 | 0.082398 | 123.4497 | 123.0194 | 123.2071 | 123.056 | 123.2254 | 123.0698 | 123.143 | 123.0515 | 76.7166 | 123.2254 | 123.0698 | 123.0515 | 123.056 | 123.143 | -123.4406 | -46.344
4765.7812 | 123.3124 | -68.2343 | 54.8355 | 0.2401 | 0.012933 | 0.0044647 | 0.0064792 | -0.0071863 | -0.0062911 | -0.0024438 | 54.8401 | 55.0369 | -68.605 | 55.0323 | 54.8172 | 54.7943 | 54.8218 | 54.95 | 54.9591 | 8.4915 | -0.37079 | 0.20142 | 123.0743 | 123.2666 | -0.01831 | 76.7258 | 0.1236 | 123.4451 | 123.056 | 123.1842 | 123.0515 | 123.2712 | 123.0743 | 123.1934 | 123.0286 | 76.7258 | 123.2712 | 123.0743 | 123.0286 | 123.0515 | 123.1934 | -123.4406 | -46.344
4766.7656 | 123.4634 | -68.2205 | 54.7852 | 0.19432 | 0.013574 | 0.0068147 | 0.0064792 | -0.0061181 | -0.0075729 | -0.0026574 | 54.9133 | 54.9683 | -68.6005 | 55.1056 | 54.8904 | 54.9042 | 54.7256 | 55.0278 | 54.895 | 8.4961 | -0.37994 | 0.18311 | 123.1338 | 123.3261 | 0.10529 | 76.7166 | 0.10986 | 123.5138 | 122.9462 | 123.2483 | 123.111 | 123.1888 | 123.1338 | 123.1155 | 123.1247 | 76.7166 | 123.1888 | 123.1338 | 123.1247 | 123.111 | 123.1155 | -123.3856 | -46.2891
4767.7656 | 123.3856 | -68.2114 | 54.8172 | 0.28587 | 0.012933 | 0.010232 | 0.0045566 | -0.0059045 | -0.0050095 | 0.00054681 | 54.895 | 54.9774 | -68.6096 | 55.101 | 54.8813 | 54.8904 | 54.7256 | 55.0369 | 54.8904 | 8.4915 | -0.39825 | 0.16022 | 123.1064 | 123.3124 | 0.064087 | 76.7029 | 0.073242 | 123.5046 | 122.937 | 123.2483 | 123.0927 | 123.1888 | 123.1064 | 123.1018 | 123.1018 | 76.7029 | 123.1888 | 123.1064 | 123.1018 | 123.0927 | 123.1018 | -123.4268 | -46.3257
4768.7812 | 123.2574 | -68.2388 | 54.8767 | 2.0712 | 0.011651 | 0.0031831 | 0.0094698 | -0.0095361 | -0.0086411 | 0.00054681 | 55.0369 | 55.0369 | -68.6234 | 55.0186 | 54.8218 | 54.776 | 54.8813 | 54.9179 | 54.9454 | 8.4961 | -0.38452 | 0.16022 | 123.2758 | 123.2574 | -0.054932 | 76.7349 | 0.068665 | 123.6603 | 123.1201 | 123.1567 | 123.0606 | 123.2758 | 123.2758 | 123.1842 | 123.0148 | 76.7349 | 123.2758 | 123.2758 | 123.0148 | 123.0606 | 123.1842 | -123.5001 | -46.3806
4769.7812 | 123.2712 | -68.2205 | 54.8859 | 0.17143 | 0.013574 | 0.0074555 | 0.010111 | -0.0069727 | -0.0015915 | -0.0041528 | 54.8264 | 55.0644 | -68.6371 | 55.0186 | 55.0598 | 54.863 | 54.9637 | 54.9362 | 54.9774 | 8.4961 | -0.41657 | 0.17853 | 123.0469 | 123.2391 | 0.17395 | 76.7166 | 0.091553 | 123.4634 | 123.1842 | 123.1567 | 123.2803 | 123.2849 | 123.0469 | 123.1979 | 123.0835 | 76.7166 | 123.2849 | 123.0469 | 123.0835 | 123.2803 | 123.1979 | -123.5229 | -46.3898
4770.7812 | 123.2574 | -68.2709 | 54.8584 | 0.17906 | 0.013146 | 0.0023285 | 0.0064792 | -0.0076135 | -0.0058639 | -0.00073479 | 54.8401 | 55.0415 | -68.6142 | 55.0232 | 54.8035 | 54.7852 | 54.8538 | 54.9408 | 54.9408 | 8.4915 | -0.34332 | 0.18311 | 123.111 | 123.2941 | -0.054931 | 76.7624 | 0.082398 | 123.4543 | 123.1247 | 123.2117 | 123.0743 | 123.3124 | 123.111 | 123.2117 | 123.056 | 76.7624 | 123.3124 | 123.111 | 123.056 | 123.0743 | 123.2117 | -123.4726 | -46.3669
4771.7812 | 123.2758 | -68.2388 | 54.8767 | 0.072251 | 0.013787 | 0.0057465 | 0.0069064 | -0.0073999 | -0.0067185 | -0.0020166 | 54.8264 | 55.0461 | -68.6234 | 55.014 | 54.808 | 54.7989 | 54.8859 | 54.9271 | 54.9683 | 8.4915 | -0.38452 | 0.16937 | 123.0652 | 123.2529 | -0.068665 | 76.7303 | 0.091553 | 123.4497 | 123.1247 | 123.1659 | 123.0469 | 123.2849 | 123.0652 | 123.2071 | 123.0377 | 76.7303 | 123.2849 | 123.0652 | 123.0377 | 123.0469 | 123.2071 | -123.5001 | -46.3852
4772.7656 | 123.3582 | -68.2343 | 54.8538 | 0.27824 | 0.015496 | 0.0066009 | 0.0064792 | -0.0061181 | -0.0062911 | -0.00073479 | 54.8767 | 55.0095 | -68.6371 | 55.0781 | 54.8676 | 54.8767 | 54.7302 | 55.0415 | 54.9042 | 8.5007 | -0.40283 | 0.15564 | 123.111 | 123.3124 | 0.013733 | 76.7349 | 0.050354 | 123.5138 | 122.9645 | 123.2758 | 123.1018 | 123.2437 | 123.111 | 123.1384 | 123.111 | 76.7349 | 123.2437 | 123.111 | 123.111 | 123.1018 | 123.1384 | -123.4909 | -46.3531
4773.7656 | 123.3353 | -68.2388 | 54.8309 | 0.30113 | 0.012719 | 0.0053193 | 0.0049838 | -0.0073999 | -0.0037277 | -0.0022302 | 54.8721 | 55.0278 | -68.5822 | 55.069 | 54.8721 | 54.8676 | 54.7623 | 55.0278 | 54.9088 | 8.4961 | -0.34332 | 0.19684 | 123.111 | 123.3078 | 0.041198 | 76.7349 | 0.077819 | 123.4543 | 123.0011 | 123.2666 | 123.111 | 123.2666 | 123.111 | 123.1476 | 123.1064 | 76.7349 | 123.2666 | 123.111 | 123.1064 | 123.111 | 123.1476 | -123.4131 | -46.3348
4774.7656 | 123.3307 | -68.2297 | 54.8264 | 0.23247 | 0.01336 | 0.0029693 | 0.0064792 | -0.0078271 | -0.0056503 | -0.0013758 | 54.8859 | 55.0186 | -68.6096 | 55.0415 | 54.8492 | 54.8492 | 54.7852 | 55.0003 | 54.95 | 8.4961 | -0.37994 | 0.19226 | 123.1155 | 123.2712 | 0.022888 | 76.7258 | 0.1236 | 123.4955 | 123.0148 | 123.23 | 123.0789 | 123.2483 | 123.1155 | 123.1796 | 123.0789 | 76.7258 | 123.2483 | 123.1155 | 123.0789 | 123.0789 | 123.1796 | -123.436 | -46.3303
4775.7812 | 123.1338 | -68.2571 | 54.8401 | 0.19432 | 0.016778 | 0.0027557 | 0.0077608 | -0.0069727 | -0.0060775 | -0.0011622 | 54.8309 | 55.0461 | -68.6279 | 54.9774 | 54.7623 | 54.7668 | 54.8859 | 54.9271 | 54.9774 | 8.4869 | -0.37079 | 0.20599 | 123.0881 | 123.2346 | -0.07782 | 76.7441 | 0.13733 | 123.4589 | 123.143 | 123.1842 | 123.0194 | 123.3032 | 123.0881 | 123.2346 | 123.024 | 76.7441 | 123.3032 | 123.0881 | 123.024 | 123.0194 | 123.2346 | -123.468 | -46.3531
4776.7812 | 123.2529 | -68.2663 | 54.8767 | 0.10277 | 0.013787 | 0.0059601 | 0.0081882 | -0.0065455 | -0.0080001 | -0.0028712 | 54.8309 | 55.0461 | -68.6325 | 54.9866 | 54.7714 | 54.7623 | 54.9271 | 54.9225 | 54.9728 | 8.4961 | -0.36621 | 0.16937 | 123.0972 | 123.2529 | -0.10529 | 76.7624 | 0.09613 | 123.4634 | 123.1934 | 123.1888 | 123.0377 | 123.3124 | 123.0972 | 123.2391 | 123.0286 | 76.7624 | 123.3124 | 123.0972 | 123.0286 | 123.0377 | 123.2391 | -123.5092 | -46.3806
4777.9219 | 123.3215 | -68.2022 | 54.8538 | 0.10277 | 0.010369 | 0.0016877 | -0.0033476 | -0.0093225 | -0.0043685 | -0.00094839 | 54.808 | 54.9728 | -68.6142 | 55.0552 | 54.8767 | 54.8584 | 54.808 | 55.0369 | 54.9133 | 8.4915 | -0.41199 | 0.11902 | 123.0103 | 123.2574 | 0.022888 | 76.6937 | 0.059509 | 123.4222 | 123.0103 | 123.2391 | 123.0789 | 123.175 | 123.0103 | 123.1155 | 123.0606 | 76.6937 | 123.175 | 123.0103 | 123.0606 | 123.0789 | 123.1155 | -123.468 | -46.3623
4778.7812 | 123.2712 | -68.2617 | 54.8676 | 2.0177 | 0.014855 | 0.0044647 | 0.0073336 | -0.0076135 | -0.0028731 | -0.0015894 | 54.8264 | 54.9866 | -68.6188 | 55.0278 | 54.8035 | 54.7806 | 54.8721 | 54.9362 | 54.9545 | 8.4824 | -0.35706 | 0.11902 | 123.0881 | 123.2895 | -0.064087 | 76.7441 | 0.086975 | 123.4451 | 123.1338 | 123.1979 | 123.0652 | 123.2483 | 123.0881 | 123.2162 | 123.0423 | 76.7441 | 123.2483 | 123.0881 | 123.0423 | 123.0652 | 123.2162 | -123.4863 | -46.3852
4779.7656 | 123.3536 | -68.2343 | 54.8401 | 0.24773 | 0.0093012 | 0.0059601 | 0.0041292 | -0.0084681 | -0.0050095 | -0.0028712 | 54.8721 | 55.0186 | -68.6096 | 55.0552 | 54.8538 | 54.8676 | 54.7714 | 55.0232 | 54.9042 | 8.4869 | -0.37537 | 0.17853 | 123.1064 | 123.2895 | 0.013733 | 76.7212 | 0.064087 | 123.4818 | 123.0057 | 123.2574 | 123.0881 | 123.2529 | 123.1064 | 123.1384 | 123.1018 | 76.7212 | 123.2529 | 123.1064 | 123.1018 | 123.0881 | 123.1384 | -123.4497 | -46.3531
4780.7656 | 123.3261 | -68.2343 | 54.8355 | 0.24773 | 0.014855 | 0.0046783 | 0.0058382 | -0.0082545 | -0.0043685 | -0.0011622 | 54.8676 | 55.0415 | -68.5959 | 55.0598 | 54.8264 | 54.8172 | 54.7714 | 54.9911 | 54.9271 | 8.4961 | -0.36163 | 0.20599 | 123.1018 | 123.2941 | -0.009155 | 76.7303 | 0.091553 | 123.4634 | 123.0057 | 123.2254 | 123.0606 | 123.2758 | 123.1018 | 123.1613 | 123.0515 | 76.7303 | 123.2758 | 123.1018 | 123.0515 | 123.0606 | 123.1613 | -123.4314 | -46.3394
4781.7656 | 123.3215 | -68.248 | 54.8355 | 0.26299 | 0.013787 | 0.0070283 | 0.0069064 | -0.0084681 | -0.0043685 | -9.3992e-05 | 54.863 | 55.0369 | -68.6279 | 55.0415 | 54.8126 | 54.8172 | 54.8172 | 54.9774 | 54.9454 | 8.4915 | -0.37994 | 0.20142 | 123.111 | 123.2895 | -0.022888 | 76.7395 | 0.10986 | 123.4909 | 123.0652 | 123.2254 | 123.0606 | 123.2849 | 123.111 | 123.1934 | 123.0652 | 76.7395 | 123.2849 | 123.111 | 123.0652 | 123.0606 | 123.1934 | -123.4634 | -46.344
4782.7656 | 123.2758 | -68.2205 | 54.863 | 0.095139 | 0.014001 | 0.0059601 | 0.0064792 | -0.0065455 | -0.0092819 | -0.003512 | 54.895 | 55.0644 | -68.6142 | 55.0415 | 54.7989 | 54.8035 | 54.9133 | 54.9683 | 54.9683 | 8.4869 | -0.39368 | 0.20142 | 123.1155 | 123.262 | -0.064087 | 76.7075 | 0.10529 | 123.5092 | 123.1338 | 123.1888 | 123.0194 | 123.2849 | 123.1155 | 123.1888 | 123.024 | 76.7075 | 123.2849 | 123.1155 | 123.024 | 123.0194 | 123.1888 | -123.4772 | -46.376
4783.7812 | 123.3215 | -68.2068 | 54.8447 | 0.18669 | 0.011437 | -0.00023494 | -0.001425 | -0.0082545 | -0.0039413 | -0.001803 | 54.8355 | 54.9271 | -68.6234 | 55.0415 | 54.8676 | 54.8721 | 54.776 | 55.0278 | 54.9362 | 8.4915 | -0.41656 | 0.082397 | 123.0423 | 123.2483 | 0.022888 | 76.6983 | 0.091552 | 123.4589 | 122.9828 | 123.2346 | 123.0743 | 123.1338 | 123.0423 | 123.143 | 123.0789 | 76.6983 | 123.1338 | 123.0423 | 123.0789 | 123.0743 | 123.143 | -123.468 | -46.3531
4784.7812 | 123.262 | -68.2343 | 54.8767 | 0.2401 | 0.011865 | 0.0031831 | 0.0079744 | -0.0073999 | -0.0060775 | -0.00094839 | 54.5654 | 54.9728 | -68.6417 | 55.0507 | 54.8035 | 54.7897 | 54.8721 | 54.9133 | 54.982 | 8.4869 | -0.40741 | 0.09613 | 122.7997 | 123.2849 | -0.073242 | 76.7212 | 0.10529 | 123.2071 | 123.1064 | 123.1476 | 123.0377 | 123.2071 | 122.7997 | 123.2162 | 123.024 | 76.7212 | 123.2071 | 122.7997 | 123.024 | 123.0377 | 123.2162 | -123.5184 | -46.3898
4785.7812 | 123.3536 | -68.1931 | 54.8447 | -0.011673 | 0.010583 | 0.0023285 | 0.00071144 | -0.0095361 | -0.0050095 | -0.0024438 | 54.8767 | 54.9316 | -68.5822 | 55.0919 | 54.8996 | 54.9133 | 54.8035 | 55.1239 | 54.9591 | 8.4961 | -0.3891 | 0.086975 | 123.0698 | 123.2849 | 0.054931 | 76.6891 | 0.11444 | 123.4589 | 122.9965 | 123.317 | 123.0927 | 123.1247 | 123.0698 | 123.1522 | 123.1064 | 76.6891 | 123.1247 | 123.0698 | 123.1064 | 123.0927 | 123.1522 | -123.4268 | -46.3486
4786.7656 | 123.3307 | -68.2343 | 54.863 | 0.28587 | 0.013146 | 0.0055329 | 0.0073336 | -0.0093225 | -0.0062911 | -0.001803 | 54.8676 | 55.0095 | -68.6096 | 55.0461 | 54.8172 | 54.8264 | 54.7943 | 54.982 | 54.895 | 8.4915 | -0.37537 | 0.14648 | 123.1018 | 123.2803 | -0.045776 | 76.7258 | 0.032044 | 123.4772 | 123.0286 | 123.2162 | 123.0515 | 123.2437 | 123.1018 | 123.1293 | 123.0606 | 76.7258 | 123.2437 | 123.1018 | 123.0606 | 123.0515 | 123.1293 | -123.4726 | -46.3715
4787.7656 | 123.3078 | -68.2571 | 54.8264 | 0.27824 | 0.014214 | 0.0057465 | 0.00712 | -0.0071863 | -0.0065047 | -0.0020166 | 54.8584 | 55.014 | -68.6279 | 55.0278 | 54.8309 | 54.8126 | 54.8218 | 54.982 | 54.9362 | 8.4915 | -0.37079 | 0.18768 | 123.1155 | 123.2849 | 0.004578 | 76.7487 | 0.10986 | 123.4863 | 123.0789 | 123.2391 | 123.0881 | 123.2712 | 123.1155 | 123.1934 | 123.0698 | 76.7487 | 123.2712 | 123.1155 | 123.0698 | 123.0881 | 123.1934 | -123.4543 | -46.3348
4788.7656 | 123.2895 | -68.2526 | 54.863 | 0.20958 | 0.014214 | 0.0059601 | 0.0094698 | -0.0063317 | -0.0062911 | -0.0032984 | 54.8492 | 55.0323 | -68.6371 | 55.0323 | 54.7989 | 54.7943 | 54.8355 | 54.9591 | 54.9408 | 8.4915 | -0.38452 | 0.16937 | 123.1018 | 123.2849 | -0.064087 | 76.7441 | 0.07782 | 123.4863 | 123.0881 | 123.2117 | 123.0515 | 123.2849 | 123.1018 | 123.1934 | 123.0469 | 76.7441 | 123.2849 | 123.1018 | 123.0469 | 123.0515 | 123.1934 | -123.5001 | -46.3715
4789.7656 | 123.2803 | -68.2434 | 54.8813 | 0.0035856 | 0.014428 | 0.0070283 | 0.0081882 | -0.0054773 | -0.0069321 | -0.0041528 | 54.9088 | 55.0461 | -68.6234 | 55.0552 | 54.8264 | 54.8126 | 54.8813 | 54.982 | 54.9728 | 8.4869 | -0.37994 | 0.16479 | 123.1522 | 123.2986 | -0.054932 | 76.7303 | 0.091552 | 123.5321 | 123.1247 | 123.2254 | 123.0698 | 123.2895 | 123.1522 | 123.2162 | 123.056 | 76.7303 | 123.2895 | 123.1522 | 123.056 | 123.0698 | 123.2162 | -123.5046 | -46.3943
4790.7812 | 123.3261 | -68.2159 | 54.8538 | 0.14854 | 0.009942 | 0.0036103 | -0.0020658 | -0.0084681 | -0.0052231 | -0.0015894 | 54.8401 | 54.9316 | -68.6279 | 55.0507 | 54.8538 | 54.8538 | 54.7806 | 55.0095 | 54.9454 | 8.5007 | -0.41199 | 0.07782 | 123.056 | 123.2666 | 0 | 76.7166 | 0.091553 | 123.468 | 122.9965 | 123.2254 | 123.0698 | 123.1476 | 123.056 | 123.1613 | 123.0698 | 76.7166 | 123.1476 | 123.056 | 123.0698 | 123.0698 | 123.1613 | -123.4818 | -46.3531
4791.7812 | 123.2391 | -68.2388 | 54.863 | 0.23247 | 0.012505 | 0.0083099 | 0.0094698 | -0.0073999 | -0.0058639 | -0.0024438 | 54.8447 | 55.0415 | -68.605 | 55.0049 | 54.7714 | 54.744 | 54.9133 | 54.9179 | 54.9774 | 8.4824 | -0.36621 | 0.17853 | 123.0835 | 123.2437 | -0.091553 | 76.7212 | 0.11444 | 123.4497 | 123.1522 | 123.1567 | 123.0103 | 123.2803 | 123.0835 | 123.2162 | 122.9828 | 76.7212 | 123.2803 | 123.0835 | 122.9828 | 123.0103 | 123.2162 | -123.468 | -46.3806
4792.7812 | 123.2208 | -68.2571 | 54.8676 | 0.17906 | 0.017632 | 0.0076691 | 0.0084018 | -0.0082545 | -0.0045821 | -0.0030848 | 54.863 | 55.0552 | -68.6142 | 55.0278 | 54.7623 | 54.7623 | 54.8996 | 54.9179 | 54.9774 | 8.4961 | -0.35706 | 0.18768 | 123.1201 | 123.2849 | -0.10529 | 76.7532 | 0.10986 | 123.4772 | 123.1567 | 123.175 | 123.0194 | 123.3124 | 123.1201 | 123.2346 | 123.0194 | 76.7532 | 123.3124 | 123.1201 | 123.0194 | 123.0194 | 123.2346 | -123.4818 | -46.3715
4793.7656 | 123.2346 | -68.2755 | 54.8767 | 0.17143 | 0.013574 | 0.0051057 | 0.0051974 | -0.0071863 | -0.0054367 | -0.0028712 | 54.8264 | 55.0644 | -68.6462 | 55.0095 | 54.7897 | 54.7806 | 54.8721 | 54.9179 | 54.9911 | 8.4869 | -0.37079 | 0.18768 | 123.1018 | 123.2849 | -0.086975 | 76.7624 | 0.11444 | 123.4726 | 123.1476 | 123.1934 | 123.0652 | 123.3398 | 123.1018 | 123.2666 | 123.056 | 76.7624 | 123.3398 | 123.1018 | 123.056 | 123.0652 | 123.2666 | -123.5229 | -46.3898
4794.7656 | 123.2574 | -68.2571 | 54.8538 | 0.22484 | 0.01336 | 0.014932 | 0.0056246 | -0.0069727 | -0.0047957 | -0.0028712 | 54.5883 | 54.9911 | -68.6554 | 55.0415 | 54.8492 | 54.7852 | 54.8904 | 54.9179 | 55.0003 | 8.4915 | -0.39825 | 0.13733 | 122.8455 | 123.2986 | -0.004578 | 76.7487 | 0.14648 | 123.2437 | 123.1476 | 123.175 | 123.1064 | 123.2483 | 122.8455 | 123.2574 | 123.0423 | 76.7487 | 123.2483 | 122.8455 | 123.0423 | 123.1064 | 123.2574 | -123.5092 | -46.3623
4795.7812 | 123.3444 | -68.2068 | 54.8447 | 0.14854 | 0.010583 | 0.00083306 | -0.0033476 | -0.0093225 | -0.0069321 | -0.0015894 | 54.8264 | 54.9545 | -68.6279 | 55.0598 | 54.863 | 54.8584 | 54.7989 | 55.0278 | 54.9454 | 8.4915 | -0.42114 | 0.10986 | 123.0331 | 123.2666 | 0.01831 | 76.6983 | 0.10071 | 123.4543 | 123.0057 | 123.2346 | 123.0698 | 123.1613 | 123.0331 | 123.1522 | 123.0652 | 76.6983 | 123.1613 | 123.0331 | 123.0652 | 123.0698 | 123.1522 | -123.4726 | -46.3531
4796.7656 | 123.2986 | -68.2159 | 54.8721 | -0.10323 | 0.014001 | 0.0068147 | 0.0075472 | -0.0073999 | -0.0041549 | -0.0024438 | 54.9088 | 55.0735 | -68.5913 | 55.0781 | 54.8584 | 54.8538 | 54.8996 | 55.0186 | 54.9637 | 8.4824 | -0.37537 | 0.20142 | 123.1247 | 123.2941 | -0.013733 | 76.6983 | 0.091553 | 123.5001 | 123.1155 | 123.2346 | 123.0743 | 123.2895 | 123.1247 | 123.1796 | 123.0698 | 76.6983 | 123.2895 | 123.1247 | 123.0698 | 123.0743 | 123.1796 | -123.4634 | -46.3898
4797.7812 | 123.2803 | -68.2159 | 54.8676 | 0.30876 | 0.015283 | 0.0053193 | 0.008829 | -0.0063317 | -0.0062911 | -0.0032984 | 54.9225 | 55.0598 | -68.5822 | 55.0598 | 54.8492 | 54.8218 | 54.8996 | 55.0003 | 54.9911 | 8.4824 | -0.36621 | 0.19226 | 123.1384 | 123.2758 | -0.018311 | 76.6983 | 0.1236 | 123.5046 | 123.1155 | 123.2162 | 123.0652 | 123.2758 | 123.1384 | 123.2071 | 123.0377 | 76.6983 | 123.2758 | 123.1384 | 123.0377 | 123.0652 | 123.2071 | -123.4497 | -46.3852
4798.7812 | 123.262 | -68.2343 | 54.8859 | -0.0040434 | 0.012719 | 0.0066009 | 0.0090426 | -0.0061181 | -0.0054367 | -0.0032984 | 54.8996 | 55.0369 | -68.6188 | 55.0461 | 54.8309 | 54.8035 | 54.8996 | 54.9728 | 54.9683 | 8.4824 | -0.38452 | 0.15106 | 123.1338 | 123.2803 | -0.054931 | 76.7166 | 0.082398 | 123.5184 | 123.1338 | 123.2071 | 123.0652 | 123.2712 | 123.1338 | 123.2025 | 123.0377 | 76.7166 | 123.2712 | 123.1338 | 123.0377 | 123.0652 | 123.2025 | -123.5046 | -46.4035
4799.7812 | 123.2758 | -68.2388 | 54.8767 | 0.011215 | 0.016137 | 0.0046783 | 0.0066928 | -0.0059045 | -0.0060775 | 0.00033321 | 54.8859 | 55.0552 | -68.6096 | 55.0323 | 54.8264 | 54.8264 | 54.8859 | 54.982 | 54.9728 | 8.4915 | -0.37079 | 0.17853 | 123.1247 | 123.2712 | -0.050354 | 76.7303 | 0.09613 | 123.4955 | 123.1247 | 123.2208 | 123.0652 | 123.2941 | 123.1247 | 123.2117 | 123.0652 | 76.7303 | 123.2941 | 123.1247 | 123.0652 | 123.0652 | 123.2117 | -123.4863 | -46.3852
4800.7656 | 123.2254 | -68.2571 | 54.8859 | 0.13329 | 0.012933 | 0.0029693 | 0.00712 | -0.0048365 | -0.0073593 | -0.0024438 | 54.8126 | 55.0461 | -68.6462 | 54.982 | 54.7806 | 54.7485 | 54.9179 | 54.8996 | 54.982 | 8.4915 | -0.3891 | 0.16022 | 123.0698 | 123.2391 | -0.10528 | 76.7487 | 0.096131 | 123.4589 | 123.175 | 123.1567 | 123.0377 | 123.3032 | 123.0698 | 123.2391 | 123.0057 | 76.7487 | 123.3032 | 123.0698 | 123.0057 | 123.0377 | 123.2391 | -123.5321 | -46.3943
4801.7656 | 123.262 | -68.248 | 54.8904 | 0.087509 | 0.014214 | 0.0087373 | 0.0056246 | -0.0063317 | -0.0045821 | -0.003512 | 54.8447 | 55.0644 | -68.6371 | 54.9911 | 54.7852 | 54.7714 | 54.9133 | 54.9271 | 54.9454 | 8.4915 | -0.3891 | 0.17395 | 123.0927 | 123.2391 | -0.10529 | 76.7395 | 0.054932 | 123.4818 | 123.1613 | 123.175 | 123.0331 | 123.3124 | 123.0927 | 123.1934 | 123.0194 | 76.7395 | 123.3124 | 123.0927 | 123.0194 | 123.0331 | 123.1934 | -123.5275 | -46.3989
4802.7656 | 123.2529 | -68.2388 | 54.8767 | 0.14854 | 0.013146 | 0.0036103 | 0.0051974 | -0.0056909 | -0.0041549 | -0.0039392 | 54.8676 | 55.069 | -68.6234 | 54.9957 | 54.7989 | 54.7806 | 54.95 | 54.9225 | 55.0095 | 8.4824 | -0.38452 | 0.19226 | 123.1064 | 123.2346 | -0.07782 | 76.7212 | 0.13275 | 123.4909 | 123.1888 | 123.1613 | 123.0377 | 123.3078 | 123.1064 | 123.2483 | 123.0194 | 76.7212 | 123.3078 | 123.1064 | 123.0194 | 123.0377 | 123.2483 | -123.5001 | -46.3943
4803.7656 | 123.2712 | -68.2205 | 54.8996 | -0.14137 | 0.014001 | 0.0023285 | 0.0058382 | -0.0056909 | -0.0060775 | 0.00011961 | 54.9088 | 55.0964 | -68.6096 | 55.0644 | 54.8584 | 54.8538 | 54.9225 | 55.0369 | 55.014 | 8.4869 | -0.3891 | 0.19684 | 123.1293 | 123.2849 | -0.041199 | 76.7075 | 0.11444 | 123.5184 | 123.143 | 123.2574 | 123.0789 | 123.317 | 123.1293 | 123.2346 | 123.0743 | 76.7075 | 123.317 | 123.1293 | 123.0743 | 123.0789 | 123.2346 | -123.5092 | -46.4127
4804.7812 | 123.3078 | -68.2114 | 54.895 | -0.14137 | 0.012933 | 0.0080963 | 0.0079744 | -0.0056909 | -0.0073593 | -0.0024438 | 54.9316 | 55.069 | -68.605 | 55.0552 | 54.8584 | 54.8401 | 54.8904 | 54.9911 | 55.014 | 8.4915 | -0.39368 | 0.17395 | 123.143 | 123.2666 | -0.036622 | 76.7029 | 0.11902 | 123.5367 | 123.1018 | 123.2025 | 123.0698 | 123.2803 | 123.143 | 123.2254 | 123.0515 | 76.7029 | 123.2803 | 123.143 | 123.0515 | 123.0698 | 123.2254 | -123.5001 | -46.4035
4805.7812 | 123.2849 | -68.2251 | 54.8767 | -0.49995 | 0.01336 | 0.0036103 | 0.0064792 | -0.0067591 | -0.0082137 | -0.0024438 | 54.9454 | 55.0552 | -68.5867 | 55.0552 | 54.8309 | 54.8401 | 54.895 | 55.0232 | 54.9866 | 8.4869 | -0.36163 | 0.17853 | 123.1705 | 123.2803 | -0.045776 | 76.712 | 0.10986 | 123.5321 | 123.1201 | 123.2483 | 123.056 | 123.2803 | 123.1705 | 123.2117 | 123.0652 | 76.712 | 123.2803 | 123.1705 | 123.0652 | 123.056 | 123.2117 | -123.4634 | -46.3898
4806.7812 | 123.2941 | -68.2251 | 54.8676 | -0.080337 | 0.014214 | 0.0053193 | 0.0056246 | -0.0076135 | -0.0073593 | -0.00094839 | 54.9042 | 55.0644 | -68.6188 | 55.0644 | 54.8676 | 54.8813 | 54.8584 | 55.0232 | 54.9911 | 8.4824 | -0.39368 | 0.19684 | 123.1293 | 123.2895 | 0 | 76.7075 | 0.1236 | 123.5229 | 123.0835 | 123.2483 | 123.0927 | 123.2895 | 123.1293 | 123.2162 | 123.1064 | 76.7075 | 123.2895 | 123.1293 | 123.1064 | 123.0927 | 123.2162 | -123.4863 | -46.3852
4807.7656 | 123.262 | -68.2709 | 54.863 | 0.095139 | 0.01336 | 0.0059601 | 0.0086154 | -0.0084681 | -0.0054367 | -0.0015894 | 54.8767 | 55.069 | -68.6325 | 55.0186 | 54.7943 | 54.7852 | 54.9088 | 54.9637 | 54.9957 | 8.4915 | -0.36163 | 0.20599 | 123.1476 | 123.2895 | -0.068664 | 76.7624 | 0.13275 | 123.5092 | 123.1796 | 123.2346 | 123.0652 | 123.3398 | 123.1476 | 123.2666 | 123.056 | 76.7624 | 123.3398 | 123.1476 | 123.056 | 123.0652 | 123.2666 | -123.4955 | -46.3715
4808.7656 | 123.2437 | -68.2388 | 54.8721 | 0.07988 | 0.01336 | 0.0044647 | 0.0077608 | -0.0052637 | -0.0050095 | -0.0015894 | 54.8813 | 55.0827 | -68.6142 | 55.0186 | 54.8172 | 54.7989 | 54.9088 | 54.9728 | 54.9957 | 8.5007 | -0.37537 | 0.21057 | 123.1201 | 123.2574 | -0.054931 | 76.7395 | 0.1236 | 123.4955 | 123.1476 | 123.2117 | 123.056 | 123.3215 | 123.1201 | 123.2346 | 123.0377 | 76.7395 | 123.3215 | 123.1201 | 123.0377 | 123.056 | 123.2346 | -123.4863 | -46.3715
4809.7656 | 123.2803 | -68.2205 | 54.9088 | -0.14137 | 0.012292 | 0.0040375 | 0.0039156 | -0.0071863 | -0.0054367 | -0.0022302 | 54.8447 | 55.0644 | -68.5913 | 55.0369 | 54.8492 | 54.8264 | 54.9683 | 55.0186 | 55.0278 | 8.4915 | -0.37079 | 0.15564 | 123.0652 | 123.2574 | -0.059509 | 76.712 | 0.11902 | 123.436 | 123.1888 | 123.2391 | 123.0698 | 123.2849 | 123.0652 | 123.2483 | 123.0469 | 76.712 | 123.2849 | 123.0652 | 123.0469 | 123.0698 | 123.2483 | -123.5001 | -46.4172
4810.7656 | 123.2758 | -68.2159 | 54.9133 | -0.16426 | 0.012078 | 0.0051057 | 0.0024202 | -0.0088953 | -0.0069321 | -0.0011622 | 54.8676 | 55.0552 | -68.5959 | 55.0369 | 54.8492 | 54.808 | 54.9728 | 55.0095 | 55.0369 | 8.4915 | -0.37994 | 0.14191 | 123.0835 | 123.2529 | -0.064087 | 76.7075 | 0.1236 | 123.4634 | 123.1888 | 123.2254 | 123.0652 | 123.2712 | 123.0835 | 123.2529 | 123.024 | 76.7075 | 123.2712 | 123.0835 | 123.024 | 123.0652 | 123.2529 | -123.5092 | -46.4218
4811.7812 | 123.3078 | -68.2297 | 54.8904 | -0.04982 | 0.012292 | 0.0023285 | 0.0069064 | -0.0069727 | -0.0050095 | -0.0015894 | 54.9179 | 55.0598 | -68.6142 | 55.0644 | 54.8538 | 54.8447 | 54.8401 | 55.0369 | 54.9866 | 8.4915 | -0.38452 | 0.16937 | 123.1476 | 123.2941 | -0.036621 | 76.7212 | 0.09613 | 123.5321 | 123.0698 | 123.2666 | 123.0835 | 123.2895 | 123.1476 | 123.2162 | 123.0743 | 76.7212 | 123.2895 | 123.1476 | 123.0743 | 123.0835 | 123.2162 | -123.5046 | -46.3989
4812.7812 | 123.3124 | -68.2251 | 54.8721 | -0.04219 | 0.012933 | 0.0061737 | 0.0039156 | -0.0063317 | -0.0075729 | -0.0028712 | 54.9088 | 55.0369 | -68.605 | 55.0781 | 54.8584 | 54.8401 | 54.9088 | 55.0323 | 55.0003 | 8.4961 | -0.37994 | 0.16479 | 123.1338 | 123.3032 | -0.013733 | 76.7212 | 0.12817 | 123.5138 | 123.1338 | 123.2574 | 123.0835 | 123.262 | 123.1338 | 123.2254 | 123.0652 | 76.7212 | 123.262 | 123.1338 | 123.0652 | 123.0835 | 123.2254 | -123.4772 | -46.376
4813.7812 | 123.3032 | -68.2068 | 54.8767 | -0.12611 | 0.011865 | 0.0055329 | 0.005411 | -0.0052637 | -0.0073593 | -0.0028712 | 54.9133 | 55.0735 | -68.5684 | 55.0827 | 54.8584 | 54.8492 | 54.9042 | 55.0369 | 54.9866 | 8.4869 | -0.36163 | 0.19684 | 123.1201 | 123.2895 | -0.018311 | 76.6937 | 0.10986 | 123.4818 | 123.111 | 123.2437 | 123.0652 | 123.2803 | 123.1201 | 123.1934 | 123.056 | 76.6937 | 123.2803 | 123.1201 | 123.056 | 123.0652 | 123.1934 | -123.4451 | -46.3898
4814.7656 | 123.2666 | -68.2297 | 54.8859 | 0.049362 | 0.012078 | 0.0038239 | 0.0075472 | -0.0052637 | -0.0069321 | -0.0026574 | 54.9179 | 55.0461 | -68.5959 | 55.0278 | 54.8218 | 54.8264 | 54.895 | 54.9911 | 55.0003 | 8.4915 | -0.36621 | 0.16022 | 123.1476 | 123.2574 | -0.064087 | 76.7212 | 0.11444 | 123.5138 | 123.1247 | 123.2208 | 123.0515 | 123.2758 | 123.1476 | 123.23 | 123.056 | 76.7212 | 123.2758 | 123.1476 | 123.056 | 123.0515 | 123.23 | -123.4817 | -46.3943
4815.7656 | 123.2758 | -68.2388 | 54.8813 | -0.026932 | 0.013787 | 0.0042511 | 0.0079744 | -0.0065455 | -0.0084273 | -0.0026574 | 54.9088 | 55.0644 | -68.605 | 55.0415 | 54.8264 | 54.8355 | 54.895 | 55.0003 | 55.0003 | 8.4869 | -0.36621 | 0.1831 | 123.1476 | 123.2803 | -0.054932 | 76.7258 | 0.11902 | 123.5138 | 123.1339 | 123.2391 | 123.0652 | 123.3032 | 123.1476 | 123.2391 | 123.0743 | 76.7258 | 123.3032 | 123.1476 | 123.0743 | 123.0652 | 123.2391 | -123.4863 | -46.3943
4816.7656 | 123.2483 | -68.2343 | 54.9088 | -0.20241 | 0.012933 | 0.0074555 | 0.0015658 | -0.0071863 | -0.0067185 | -0.001803 | 54.8584 | 55.0827 | -68.6142 | 55.0415 | 54.8447 | 54.8218 | 54.9911 | 55.014 | 55.0323 | 8.4915 | -0.37994 | 0.17395 | 123.0927 | 123.2758 | -0.064086 | 76.7258 | 0.1236 | 123.4726 | 123.2254 | 123.2483 | 123.0789 | 123.317 | 123.0927 | 123.2666 | 123.056 | 76.7258 | 123.317 | 123.0927 | 123.056 | 123.0789 | 123.2666 | -123.5229 | -46.4172
4817.7812 | 123.3032 | -68.1839 | 54.9271 | -0.21004 | 0.011224 | -0.00044854 | 0.00028404 | -0.0086817 | -0.0047957 | -0.0032984 | 54.8767 | 54.9728 | -68.5822 | 55.069 | 54.863 | 54.8767 | 54.9271 | 55.0827 | 55.0095 | 8.4961 | -0.39825 | 0.045776 | 123.0606 | 123.2529 | -0.064087 | 76.68 | 0.082397 | 123.4589 | 123.111 | 123.2666 | 123.0469 | 123.1567 | 123.0606 | 123.1934 | 123.0606 | 76.68 | 123.1567 | 123.0606 | 123.0606 | 123.0469 | 123.1934 | -123.5092 | -46.431
4818.7656 | 123.2849 | -68.2159 | 54.8904 | -0.149 | 0.013146 | 0.0016877 | 0.0060518 | -0.0093225 | -0.0067185 | -0.001803 | 54.8721 | 55.0598 | -68.573 | 55.0507 | 54.8401 | 54.8264 | 54.9545 | 55.0369 | 55.0095 | 8.4869 | -0.35706 | 0.16937 | 123.0881 | 123.2666 | -0.050354 | 76.7029 | 0.11902 | 123.4451 | 123.1705 | 123.2529 | 123.056 | 123.2758 | 123.0881 | 123.2254 | 123.0423 | 76.7029 | 123.2758 | 123.0881 | 123.0423 | 123.056 | 123.2254 | -123.4634 | -46.4035
4819.7812 | 123.2986 | -68.2251 | 54.8767 | -0.072708 | 0.010796 | 0.0085235 | 0.0060518 | -0.0078271 | -0.0056503 | -0.003512 | 54.9133 | 55.0552 | -68.5867 | 55.0781 | 54.863 | 54.8218 | 54.9133 | 55.0369 | 54.9774 | 8.4869 | -0.36163 | 0.17853 | 123.1384 | 123.3032 | -0.013733 | 76.712 | 0.10071 | 123.5001 | 123.1384 | 123.262 | 123.0881 | 123.2803 | 123.1384 | 123.2025 | 123.0469 | 76.712 | 123.2803 | 123.1384 | 123.0469 | 123.0881 | 123.2025 | -123.4634 | -46.3898
4820.7812 | 123.2941 | -68.2159 | 54.8904 | -0.10323 | 0.012719 | 0.0031831 | 0.0056246 | -0.0069727 | -0.0086411 | -0.0030848 | 54.9179 | 55.0552 | -68.605 | 55.0873 | 54.8584 | 54.8447 | 54.9179 | 55.0278 | 55.0186 | 8.4869 | -0.3891 | 0.16479 | 123.1338 | 123.3032 | -0.032044 | 76.7029 | 0.12817 | 123.5229 | 123.1338 | 123.2437 | 123.0743 | 123.2712 | 123.1338 | 123.2346 | 123.0606 | 76.7029 | 123.2712 | 123.1338 | 123.0606 | 123.0743 | 123.2346 | -123.4955 | -46.4035
4821.7656 | 123.2849 | -68.2388 | 54.8721 | -0.019302 | 0.014214 | 0.0057465 | 0.0077608 | -0.0080407 | -0.0062911 | -0.0020166 | 54.9133 | 55.0278 | -68.605 | 55.0461 | 54.8309 | 54.808 | 54.8996 | 54.9774 | 55.014 | 8.4915 | -0.36621 | 0.15564 | 123.1522 | 123.2849 | -0.041198 | 76.7303 | 0.14191 | 123.5184 | 123.1384 | 123.2162 | 123.0698 | 123.2666 | 123.1522 | 123.2529 | 123.0469 | 76.7303 | 123.2666 | 123.1522 | 123.0469 | 123.0698 | 123.2529 | -123.4772 | -46.3806
4822.7656 | 123.2849 | -68.2434 | 54.8859 | 0.034104 | 0.01101 | 0.0040375 | 0.0060518 | -0.0076135 | -0.0067185 | -0.0011622 | 54.9316 | 55.0415 | -68.6142 | 55.0415 | 54.8355 | 54.8172 | 54.9179 | 55.0003 | 55.0049 | 8.4961 | -0.37079 | 0.15564 | 123.175 | 123.2849 | -0.050354 | 76.7395 | 0.11902 | 123.5458 | 123.1613 | 123.2437 | 123.0789 | 123.2849 | 123.175 | 123.2483 | 123.0606 | 76.7395 | 123.2849 | 123.175 | 123.0606 | 123.0789 | 123.2483 | -123.5001 | -46.3898
4823.7656 | 123.2529 | -68.2297 | 54.895 | -0.011673 | 0.012292 | 0.0023285 | 0.0034884 | -0.0086817 | -0.0058639 | -0.003512 | 54.8538 | 55.0644 | -68.6142 | 55.0369 | 54.8492 | 54.8172 | 54.9866 | 55.0095 | 55.0369 | 8.4869 | -0.38452 | 0.16937 | 123.0835 | 123.2666 | -0.045777 | 76.7166 | 0.14191 | 123.468 | 123.2162 | 123.2391 | 123.0789 | 123.2941 | 123.0835 | 123.2666 | 123.0469 | 76.7166 | 123.2941 | 123.0835 | 123.0469 | 123.0789 | 123.2666 | -123.5092 | -46.4081
4824.7812 | 123.2254 | -68.2388 | 54.8721 | 0.20195 | 0.014642 | 0.0029693 | 0.00712 | -0.0076135 | -0.0058639 | -0.0013758 | 54.8309 | 55.0552 | -68.6325 | 54.9911 | 54.7989 | 54.9133 | 54.3869 | 54.7943 | 54.9362 | 8.4915 | -0.39368 | 0.18311 | 123.0698 | 123.23 | -0.073242 | 76.7303 | 0.064087 | 123.4634 | 122.6257 | 123.0331 | 123.0377 | 123.2941 | 123.0698 | 123.175 | 123.1522 | 76.7303 | 123.2941 | 123.0698 | 123.1522 | 123.0377 | 123.175 | -123.5046 | -46.3806
4825.7812 | 123.2941 | -68.2343 | 54.8904 | 0.034104 | 0.014855 | 0.0059601 | 0.00712 | -0.0059045 | -0.0075729 | -0.0030848 | 54.9454 | 55.0461 | -68.6188 | 55.0507 | 54.8447 | 54.8218 | 54.8859 | 55.0049 | 54.9957 | 8.4824 | -0.38452 | 0.15564 | 123.1796 | 123.2849 | -0.045776 | 76.7166 | 0.10529 | 123.5641 | 123.1201 | 123.2391 | 123.0789 | 123.2803 | 123.1796 | 123.23 | 123.056 | 76.7166 | 123.2803 | 123.1796 | 123.056 | 123.0789 | 123.23 | -123.5092 | -46.4081
4826.7812 | 123.3032 | -68.2434 | 54.8767 | -0.087967 | 0.014214 | 0.0080963 | 0.0066928 | -0.0073999 | -0.0090683 | -0.0026574 | 54.9133 | 55.0598 | -68.6234 | 55.0781 | 54.8538 | 54.8447 | 54.8904 | 55.0507 | 55.0369 | 8.4824 | -0.37994 | 0.18311 | 123.1567 | 123.3215 | -0.022888 | 76.7258 | 0.16022 | 123.5367 | 123.1338 | 123.2941 | 123.0972 | 123.3032 | 123.1567 | 123.2803 | 123.0881 | 76.7258 | 123.3032 | 123.1567 | 123.0881 | 123.0972 | 123.2803 | -123.5001 | -46.3943
4827.7656 | 123.2803 | -68.2343 | 54.8859 | 0.034104 | 0.014001 | 0.0029693 | 0.00712 | -0.0056909 | -0.0075729 | -0.003512 | 54.9133 | 55.0461 | -68.6188 | 55.0369 | 54.8172 | 54.8264 | 54.8904 | 54.9866 | 55.0003 | 8.4961 | -0.38452 | 0.16022 | 123.1476 | 123.2712 | -0.068664 | 76.7303 | 0.11444 | 123.5321 | 123.1247 | 123.2208 | 123.0515 | 123.2803 | 123.1476 | 123.2346 | 123.0606 | 76.7303 | 123.2803 | 123.1476 | 123.0606 | 123.0515 | 123.2346 | -123.5046 | -46.3898
4828.7656 | 123.2849 | -68.2434 | 54.895 | -0.0040434 | 0.013146 | 0.0074555 | 0.0081882 | -0.0063317 | -0.0058639 | -0.0015894 | 54.9042 | 55.0461 | -68.6142 | 55.0552 | 54.8447 | 54.8218 | 54.8904 | 55.0049 | 55.0095 | 8.4869 | -0.37079 | 0.15106 | 123.1476 | 123.2986 | -0.050354 | 76.7303 | 0.11444 | 123.5184 | 123.1338 | 123.2483 | 123.0881 | 123.2895 | 123.1476 | 123.2529 | 123.0652 | 76.7303 | 123.2895 | 123.1476 | 123.0652 | 123.0881 | 123.2529 | -123.5092 | -46.4081
4829.7656 | 123.3078 | -68.2297 | 54.8676 | -0.080337 | 0.012719 | 0.0051057 | 0.0058382 | -0.0056909 | -0.0084273 | -0.0024438 | 54.9133 | 55.0323 | -68.6005 | 55.0369 | 54.8538 | 54.8492 | 54.8904 | 55.0049 | 55.014 | 8.4869 | -0.37079 | 0.1648 | 123.143 | 123.2666 | -0.013733 | 76.7166 | 0.14648 | 123.5138 | 123.1201 | 123.2346 | 123.0835 | 123.262 | 123.143 | 123.2437 | 123.0789 | 76.7166 | 123.262 | 123.143 | 123.0789 | 123.0835 | 123.2437 | -123.468 | -46.3806
4830.7656 | 123.2483 | -68.2251 | 54.9179 | -0.24818 | 0.011437 | 0.00083306 | 0.0030612 | -0.0084681 | -0.0067185 | -0.00073479 | 54.8355 | 55.0919 | -68.5913 | 55.0186 | 54.8401 | 54.808 | 54.9866 | 55.0049 | 55.0461 | 8.4961 | -0.36621 | 0.17395 | 123.0606 | 123.2437 | -0.07782 | 76.7212 | 0.12817 | 123.4268 | 123.2117 | 123.23 | 123.0652 | 123.317 | 123.0606 | 123.2712 | 123.0331 | 76.7212 | 123.317 | 123.0606 | 123.0331 | 123.0652 | 123.2712 | -123.5092 | -46.4218
4831.7812 | 123.2803 | -68.2205 | 54.9042 | -0.13374 | 0.012292 | 0.0066009 | 0.0060518 | -0.0061181 | -0.0073593 | -0.0028712 | 54.8904 | 55.0873 | -68.5822 | 55.0644 | 54.8584 | 54.8401 | 54.9591 | 55.0232 | 55.0323 | 8.4869 | -0.36163 | 0.1831 | 123.111 | 123.2849 | -0.045777 | 76.7075 | 0.12817 | 123.4726 | 123.1796 | 123.2437 | 123.0789 | 123.3078 | 123.111 | 123.2529 | 123.0606 | 76.7075 | 123.3078 | 123.111 | 123.0606 | 123.0789 | 123.2529 | -123.4863 | -46.4172
4832.7812 | 123.317 | -68.2068 | 54.8904 | -0.065079 | 0.012933 | 0.0053193 | 0.0073336 | -0.0059045 | -0.0060775 | -0.0015894 | 54.9271 | 55.0735 | -68.5959 | 55.0735 | 54.863 | 54.8447 | 54.9088 | 55.0369 | 55.0186 | 8.4824 | -0.3891 | 0.1831 | 123.1338 | 123.2803 | -0.027466 | 76.6891 | 0.12817 | 123.5229 | 123.1155 | 123.2437 | 123.0698 | 123.2803 | 123.1338 | 123.2254 | 123.0515 | 76.6891 | 123.2803 | 123.1338 | 123.0515 | 123.0698 | 123.2254 | -123.4863 | -46.4081
4833.7812 | 123.3032 | -68.2114 | 54.8996 | -0.095596 | 0.012292 | 0.0038239 | 0.0073336 | -0.0065455 | -0.0054367 | -0.001803 | 54.8996 | 55.0415 | -68.5959 | 55.0873 | 54.8538 | 54.8447 | 54.8996 | 55.0323 | 55.0278 | 8.4824 | -0.38452 | 0.14191 | 123.111 | 123.2986 | -0.045776 | 76.6937 | 0.12817 | 123.4955 | 123.111 | 123.2437 | 123.0652 | 123.2529 | 123.111 | 123.2391 | 123.056 | 76.6937 | 123.2529 | 123.111 | 123.056 | 123.0652 | 123.2391 | -123.4955 | -46.4172
4834.7656 | 123.2666 | -68.2297 | 54.8767 | 0.026474 | 0.012292 | 0.0046783 | 0.0077608 | -0.0071863 | -0.0075729 | -0.0013758 | 54.9133 | 55.0461 | -68.5959 | 55.0461 | 54.8401 | 54.8218 | 54.8859 | 54.9911 | 55.0095 | 8.4915 | -0.36621 | 0.16937 | 123.143 | 123.2758 | -0.036621 | 76.7212 | 0.13275 | 123.5092 | 123.1155 | 123.2208 | 123.0698 | 123.2758 | 123.143 | 123.2391 | 123.0515 | 76.7212 | 123.2758 | 123.143 | 123.0515 | 123.0698 | 123.2391 | -123.4726 | -46.3852
4835.7656 | 123.2895 | -68.2205 | 54.8813 | -0.149 | 0.011651 | 0.0083099 | 0.0077608 | -0.0073999 | -0.0067185 | -0.0015894 | 54.9133 | 55.0461 | -68.6234 | 55.069 | 54.8355 | 54.8401 | 54.8996 | 55.0049 | 55.0095 | 8.4915 | -0.40283 | 0.16479 | 123.1338 | 123.2895 | -0.045777 | 76.712 | 0.12817 | 123.5367 | 123.1201 | 123.2254 | 123.056 | 123.2666 | 123.1338 | 123.23 | 123.0606 | 76.712 | 123.2666 | 123.1338 | 123.0606 | 123.056 | 123.23 | -123.5046 | -46.3898
4836.7656 | 123.2986 | -68.2297 | 54.8859 | 0.73601 | 0.010796 | 0.0070283 | 0.0066928 | -0.0082545 | -0.0075729 | -0.0041528 | 54.9042 | 55.0186 | -68.6371 | 55.0598 | 54.8538 | 54.8676 | 54.8859 | 55.014 | 55.0049 | 8.4869 | -0.40741 | 0.13275 | 123.1338 | 123.2895 | -0.032043 | 76.7166 | 0.11902 | 123.5413 | 123.1155 | 123.2437 | 123.0835 | 123.2483 | 123.1338 | 123.2346 | 123.0972 | 76.7166 | 123.2483 | 123.1338 | 123.0972 | 123.0835 | 123.2346 | -123.5229 | -46.3989
4837.7656 | 123.2758 | -68.2617 | 54.8996 | -0.24055 | 0.011865 | -0.0023711 | 0.002634 | -0.0061181 | -0.0060775 | -0.001803 | 54.8492 | 55.0827 | -68.6005 | 54.9911 | 54.8401 | 54.776 | 54.982 | 54.9957 | 55.0278 | 8.4961 | -0.33875 | 0.18311 | 123.111 | 123.2529 | -0.059509 | 76.7578 | 0.12817 | 123.4497 | 123.2437 | 123.2574 | 123.1018 | 123.3444 | 123.111 | 123.2895 | 123.0377 | 76.7578 | 123.3444 | 123.111 | 123.0377 | 123.1018 | 123.2895 | -123.5001 | -46.4035
4838.7812 | 123.2666 | -68.2343 | 54.9225 | -0.149 | 0.011651 | 0.0074555 | 0.0064792 | -0.0071863 | -0.0080001 | -0.0026574 | 54.863 | 55.0735 | -68.6096 | 55.0369 | 54.8355 | 54.8172 | 54.9728 | 55.0049 | 55.0003 | 8.4915 | -0.37537 | 0.15106 | 123.0972 | 123.2712 | -0.086975 | 76.7258 | 0.07782 | 123.4726 | 123.2071 | 123.2391 | 123.0698 | 123.3078 | 123.0972 | 123.2346 | 123.0515 | 76.7258 | 123.3078 | 123.0972 | 123.0515 | 123.0698 | 123.2346 | -123.5321 | -46.431
4839.7812 | 123.2986 | -68.2159 | 54.895 | -0.149 | 0.0090876 | 0.0010467 | 0.0069064 | -0.0093225 | -0.0062911 | -0.0039392 | 54.8904 | 55.0735 | -68.6005 | 55.0735 | 54.8584 | 54.8401 | 54.9408 | 55.0232 | 55.0278 | 8.4915 | -0.38452 | 0.17853 | 123.1064 | 123.2895 | -0.036622 | 76.7075 | 0.13275 | 123.4909 | 123.1567 | 123.2391 | 123.0743 | 123.2895 | 123.1064 | 123.2437 | 123.056 | 76.7075 | 123.2895 | 123.1064 | 123.056 | 123.0743 | 123.2437 | -123.4955 | -46.4035
4840.7812 | 123.2941 | -68.2159 | 54.8996 | -0.16426 | 0.011651 | 0.0074555 | 0.0049838 | -0.0065455 | -0.0062911 | -0.0026574 | 54.8859 | 55.0552 | -68.6142 | 55.0598 | 54.8584 | 54.8309 | 54.9454 | 55.0323 | 55.0232 | 8.4915 | -0.39826 | 0.15564 | 123.1018 | 123.2758 | -0.041199 | 76.7075 | 0.1236 | 123.5001 | 123.1613 | 123.2483 | 123.0743 | 123.2712 | 123.1018 | 123.2391 | 123.0469 | 76.7075 | 123.2712 | 123.1018 | 123.0469 | 123.0743 | 123.2391 | -123.5138 | -46.4081
4841.7656 | 123.3124 | -68.2205 | 54.8721 | -0.072708 | 0.013574 | 0.0048921 | 0.0049838 | -0.0073999 | -0.0082137 | -0.0041528 | 54.9271 | 55.0278 | -68.6188 | 55.0598 | 54.863 | 54.8996 | 54.7577 | 55.0369 | 54.9728 | 8.4869 | -0.39825 | 0.15564 | 123.1476 | 123.2803 | -0.009155 | 76.7075 | 0.10071 | 123.5458 | 122.9782 | 123.2574 | 123.0835 | 123.2483 | 123.1476 | 123.1934 | 123.1201 | 76.7075 | 123.2483 | 123.1476 | 123.1201 | 123.0835 | 123.1934 | -123.4909 | -46.3852
4842.7656 | 123.3032 | -68.2159 | 54.9042 | -0.019302 | 0.014855 | 0.0036103 | 0.0064792 | -0.0082545 | -0.0062911 | -0.0020166 | 54.9133 | 55.014 | -68.6188 | 55.0735 | 54.8584 | 54.8447 | 54.9042 | 55.0323 | 55.0232 | 8.4869 | -0.40283 | 0.10986 | 123.1293 | 123.2895 | -0.045777 | 76.7029 | 0.11902 | 123.5321 | 123.1201 | 123.2483 | 123.0743 | 123.23 | 123.1293 | 123.2391 | 123.0606 | 76.7029 | 123.23 | 123.1293 | 123.0606 | 123.0743 | 123.2391 | -123.5229 | -46.4172
4843.7656 | 123.3078 | -68.2068 | 54.8767 | -0.087967 | 0.01101 | 0.0057465 | 0.0032748 | -0.0076135 | -0.0077865 | -0.0022302 | 54.9179 | 55.0415 | -68.605 | 55.0873 | 54.8584 | 54.8355 | 54.895 | 55.0278 | 55.0186 | 8.4824 | -0.39825 | 0.1648 | 123.1247 | 123.2941 | -0.018311 | 76.6891 | 0.14191 | 123.5229 | 123.1018 | 123.2346 | 123.0652 | 123.2483 | 123.1247 | 123.2254 | 123.0423 | 76.6891 | 123.2483 | 123.1247 | 123.0423 | 123.0652 | 123.2254 | -123.4818 | -46.3943
4844.7812 | 123.2437 | -68.2526 | 54.8859 | -0.2253 | 0.011437 | 0.00019226 | -0.0012112 | -0.0093225 | -0.0060775 | -0.0011622 | 54.8584 | 55.0552 | -68.6096 | 54.9545 | 54.7577 | 54.808 | 54.9545 | 54.9637 | 55.0278 | 8.5007 | -0.35706 | 0.16937 | 123.111 | 123.2071 | -0.12817 | 76.7532 | 0.14191 | 123.468 | 123.2071 | 123.2162 | 123.0103 | 123.3078 | 123.111 | 123.2803 | 123.0606 | 76.7532 | 123.3078 | 123.111 | 123.0606 | 123.0103 | 123.2803 | -123.4955 | -46.3852
4845.7812 | 123.2666 | -68.2388 | 54.9316 | -0.20241 | 0.012719 | 0.0042511 | 0.00049764 | -0.0091089 | -0.0071457 | -0.0020166 | 54.8584 | 55.0415 | -68.6188 | 55.0415 | 54.8401 | 54.8172 | 55.0003 | 55.014 | 55.0278 | 8.5007 | -0.37994 | 0.10986 | 123.0972 | 123.2803 | -0.091553 | 76.7395 | 0.09613 | 123.4772 | 123.2391 | 123.2529 | 123.0789 | 123.2803 | 123.0972 | 123.2666 | 123.056 | 76.7395 | 123.2803 | 123.0972 | 123.056 | 123.0789 | 123.2666 | -123.5504 | -46.431
4846.7812 | 123.2758 | -68.2343 | 54.8859 | 0.041733 | 0.011865 | 0.0046783 | 0.0045566 | -0.0095361 | -0.0082137 | -0.003512 | 54.8584 | 55.0415 | -68.6371 | 55.0415 | 54.8538 | 54.808 | 54.9774 | 55.0095 | 55.0186 | 8.4961 | -0.40283 | 0.15564 | 123.0927 | 123.2758 | -0.032043 | 76.7303 | 0.13275 | 123.4955 | 123.2117 | 123.2437 | 123.0881 | 123.2758 | 123.0927 | 123.2529 | 123.0423 | 76.7303 | 123.2758 | 123.0927 | 123.0423 | 123.0881 | 123.2529 | -123.5229 | -46.3898
4847.7812 | 123.2574 | -68.2571 | 54.9133 | -0.21004 | 0.010796 | 0.00040586 | 0.0047702 | -0.010818 | -0.0080001 | -0.0039392 | 54.8584 | 55.0186 | -68.6096 | 55.1788 | 54.744 | 54.744 | 54.9179 | 54.9911 | 55.0415 | 8.4961 | -0.35248 | 0.10529 | 123.1155 | 123.436 | -0.16937 | 76.7532 | 0.12817 | 123.468 | 123.175 | 123.2483 | 123.0011 | 123.2758 | 123.1155 | 123.2986 | 123.0011 | 76.7532 | 123.2758 | 123.1155 | 123.0011 | 123.0011 | 123.2986 | -123.5229 | -46.4172
4848.7656 | 123.3078 | -68.2343 | 54.9042 | -0.13374 | 0.0093012 | 0.0040375 | 0.0056246 | -0.0088953 | -0.0058639 | -0.00073479 | 54.8584 | 55.0232 | -68.605 | 55.069 | 54.8492 | 54.8447 | 54.9408 | 55.0369 | 55.0003 | 8.4915 | -0.37079 | 0.11902 | 123.0927 | 123.3032 | -0.054932 | 76.7258 | 0.09613 | 123.4634 | 123.175 | 123.2712 | 123.0835 | 123.2574 | 123.0927 | 123.2346 | 123.0789 | 76.7258 | 123.2574 | 123.0927 | 123.0789 | 123.0835 | 123.2346 | -123.5092 | -46.4127
4849.7656 | 123.2849 | -68.2251 | 54.9042 | -0.16426 | 0.011437 | 0.0044647 | 0.003702 | -0.0078271 | -0.0075729 | -0.0028712 | 54.863 | 55.0278 | -68.605 | 55.069 | 54.8401 | 54.8218 | 54.9774 | 55.014 | 55.014 | 8.4915 | -0.37994 | 0.1236 | 123.0881 | 123.2941 | -0.064087 | 76.7166 | 0.10986 | 123.468 | 123.2025 | 123.2391 | 123.0652 | 123.2529 | 123.0881 | 123.2391 | 123.0469 | 76.7166 | 123.2529 | 123.0881 | 123.0469 | 123.0652 | 123.2391 | -123.5092 | -46.4127
4850.7656 | 123.2758 | -68.2297 | 54.8859 | -0.2253 | 0.012719 | 0.0029693 | 0.0045566 | -0.010177 | -0.0069321 | -0.001803 | 54.863 | 55.0278 | -68.605 | 55.0552 | 54.8355 | 54.8172 | 54.9683 | 55.0095 | 55.0049 | 8.4824 | -0.37537 | 0.14191 | 123.0927 | 123.2849 | -0.050354 | 76.712 | 0.11902 | 123.468 | 123.1979 | 123.2391 | 123.0652 | 123.2574 | 123.0927 | 123.2346 | 123.0469 | 76.712 | 123.2574 | 123.0927 | 123.0469 | 123.0652 | 123.2346 | -123.4909 | -46.4035
4851.7656 | 123.3765 | -68.2159 | 54.863 | -0.52284 | 0.0095148 | 0.0042511 | -0.002493 | -0.0097497 | -0.0069321 | -0.00052119 | 54.9179 | 54.9545 | -68.5822 | 55.1239 | 54.9454 | 54.9316 | 54.808 | 55.1376 | 54.9637 | 8.4961 | -0.36621 | 0.091553 | 123.1338 | 123.3398 | 0.082398 | 76.712 | 0.10071 | 123.5001 | 123.024 | 123.3536 | 123.1613 | 123.1705 | 123.1338 | 123.1796 | 123.1476 | 76.712 | 123.1705 | 123.1338 | 123.1476 | 123.1613 | 123.1796 | -123.4451 | -46.3669
4852.7812 | 123.2712 | -68.2159 | 54.9133 | -0.18715 | 0.01101 | 0.0016877 | 0.00049764 | -0.0097497 | -0.0058639 | -0.0026574 | 54.8538 | 55.0049 | -68.6096 | 55.0415 | 54.8309 | 54.8172 | 54.9637 | 55.0323 | 54.9957 | 8.4961 | -0.39368 | 0.091553 | 123.0698 | 123.2574 | -0.082397 | 76.712 | 0.082398 | 123.4634 | 123.1796 | 123.2483 | 123.0469 | 123.2208 | 123.0698 | 123.2117 | 123.0331 | 76.712 | 123.2208 | 123.0698 | 123.0331 | 123.0469 | 123.2117 | -123.5229 | -46.4172
4853.7812 | 123.2803 | -68.2068 | 54.8996 | -0.17952 | 0.0090876 | -2.1336e-05 | 0.0024202 | -0.01274 | -0.0077865 | -0.0030848 | 54.895 | 54.9911 | -68.5913 | 55.0781 | 54.8767 | 54.8401 | 54.9316 | 55.0507 | 55.0049 | 8.4915 | -0.38452 | 0.091553 | 123.1018 | 123.2849 | -0.022888 | 76.6983 | 0.10529 | 123.4863 | 123.1384 | 123.2574 | 123.0835 | 123.1979 | 123.1018 | 123.2117 | 123.0469 | 76.6983 | 123.1979 | 123.1018 | 123.0469 | 123.0835 | 123.2117 | -123.4909 | -46.4081
4854.7812 | 123.3078 | -68.2022 | 54.8996 | -0.20241 | 0.006524 | 0.0016877 | 0.002634 | -0.012954 | -0.0071457 | -0.0030848 | 54.9088 | 54.9866 | -68.5776 | 55.0964 | 54.8996 | 54.8813 | 54.8859 | 55.0781 | 54.9454 | 8.5007 | -0.37537 | 0.086975 | 123.111 | 123.2986 | 0 | 76.7029 | 0.045777 | 123.4863 | 123.0881 | 123.2803 | 123.1018 | 123.1888 | 123.111 | 123.1476 | 123.0835 | 76.7029 | 123.1888 | 123.111 | 123.0835 | 123.1018 | 123.1476 | -123.4772 | -46.3989
4855.7656 | 123.2529 | -68.2343 | 54.9271 | -0.17189 | 0.0093012 | 0.0021149 | 0.0030612 | -0.012527 | -0.0092819 | -0.00458 | 54.8401 | 55.0415 | -68.6142 | 55.0186 | 54.9179 | 54.9591 | 54.8538 | 54.895 | 55.0186 | 8.4915 | -0.37994 | 0.11444 | 123.0743 | 123.2529 | -0.009155 | 76.7258 | 0.091553 | 123.4543 | 123.0881 | 123.1293 | 123.1522 | 123.2758 | 123.0743 | 123.2529 | 123.1934 | 76.7258 | 123.2758 | 123.0743 | 123.1934 | 123.1522 | 123.2529 | -123.5413 | -46.4355
4856.7656 | 123.2529 | -68.2022 | 54.9088 | -0.24055 | 0.0095148 | -0.00087594 | 0.0034884 | -0.010604 | -0.0077865 | -0.0041528 | 54.8447 | 55.0049 | -68.5822 | 55.0415 | 54.8492 | 54.808 | 54.9683 | 55.0278 | 54.9957 | 8.4961 | -0.37994 | 0.096131 | 123.0469 | 123.2437 | -0.059509 | 76.6983 | 0.086976 | 123.4268 | 123.1705 | 123.23 | 123.0515 | 123.2071 | 123.0469 | 123.1979 | 123.0103 | 76.6983 | 123.2071 | 123.0469 | 123.0103 | 123.0515 | 123.1979 | -123.4909 | -46.4127
4857.7656 | 123.2803 | -68.1931 | 54.9316 | -0.16426 | 0.010369 | 0.0036103 | 0.0011386 | -0.011459 | -0.0073593 | -0.003512 | 54.8676 | 54.9911 | -68.5913 | 55.0781 | 54.8492 | 54.8172 | 54.9637 | 55.0232 | 55.0186 | 8.4961 | -0.39825 | 0.059509 | 123.0606 | 123.2712 | -0.082398 | 76.6891 | 0.086975 | 123.4589 | 123.1567 | 123.2162 | 123.0423 | 123.1842 | 123.0606 | 123.2117 | 123.0103 | 76.6891 | 123.1842 | 123.0606 | 123.0103 | 123.0423 | 123.2117 | -123.5229 | -46.4355
4858.7656 | 123.4039 | -68.1885 | 54.8538 | 0.018845 | 0.0090876 | -0.0023711 | -0.0022794 | -0.011245 | -0.0065047 | -0.0030848 | 54.9133 | 54.9133 | -68.5547 | 55.1193 | 54.9362 | 54.9316 | 54.7852 | 55.1331 | 54.9591 | 8.4915 | -0.36621 | 0.059509 | 123.1018 | 123.3078 | 0.082397 | 76.68 | 0.10528 | 123.468 | 122.9736 | 123.3215 | 123.1247 | 123.1018 | 123.1018 | 123.1476 | 123.1201 | 76.68 | 123.1018 | 123.1018 | 123.1201 | 123.1247 | 123.1476 | -123.4085 | -46.3623
4859.7812 | 123.3582 | -68.1976 | 54.8767 | -0.17189 | 0.008233 | 0.0012605 | 0.0041292 | -0.013595 | -0.0062911 | -0.0041528 | 54.9088 | 54.9683 | -68.5684 | 55.1514 | 54.9271 | 54.9088 | 54.8492 | 55.1193 | 54.9591 | 8.4915 | -0.37079 | 0.091553 | 123.1064 | 123.349 | 0.050354 | 76.6891 | 0.082397 | 123.4772 | 123.0469 | 123.317 | 123.1247 | 123.1659 | 123.1064 | 123.1567 | 123.1064 | 76.6891 | 123.1659 | 123.1064 | 123.1064 | 123.1247 | 123.1567 | -123.4451 | -46.3852
4860.7812 | 123.3948 | -68.1885 | 54.8859 | 0.23247 | 0.0090876 | 0.0023285 | 0.0022066 | -0.012954 | -0.0090683 | -0.0043664 | 54.9088 | 54.9454 | -68.6005 | 55.1468 | 54.9225 | 54.9088 | 54.8126 | 55.1239 | 54.95 | 8.4915 | -0.41199 | 0.05951 | 123.0972 | 123.3353 | 0.036621 | 76.68 | 0.064087 | 123.5092 | 123.0011 | 123.3124 | 123.111 | 123.1339 | 123.0972 | 123.1384 | 123.0972 | 76.68 | 123.1339 | 123.0972 | 123.0972 | 123.111 | 123.1384 | -123.4863 | -46.3943
4861.7812 | 123.3627 | -68.1839 | 54.8538 | -0.15663 | 0.005456 | -0.0013031 | 0.0024202 | -0.012954 | -0.0092819 | -0.0024438 | 55.1605 | 54.9911 | -68.5501 | 55.1102 | 54.9042 | 54.9088 | 54.776 | 55.1376 | 54.9362 | 8.4961 | -0.36621 | 0.13733 | 123.3444 | 123.2941 | 0.050354 | 76.68 | 0.082397 | 123.7106 | 122.9599 | 123.3215 | 123.0881 | 123.175 | 123.3444 | 123.1201 | 123.0927 | 76.68 | 123.175 | 123.3444 | 123.0927 | 123.0881 | 123.1201 | -123.4039 | -46.3577
4862.7656 | 123.3215 | -68.1931 | 54.9225 | -0.21004 | 0.0084466 | 0.0023285 | 0.004343 | -0.012954 | -0.0082137 | -0.0032984 | 54.8859 | 54.9683 | -68.5776 | 55.0827 | 54.8813 | 54.8492 | 54.9088 | 55.0644 | 54.982 | 8.5007 | -0.38452 | 0.045777 | 123.0789 | 123.2758 | -0.041198 | 76.6937 | 0.05951 | 123.4634 | 123.1018 | 123.2574 | 123.0743 | 123.1613 | 123.0789 | 123.175 | 123.0423 | 76.6937 | 123.1613 | 123.0789 | 123.0423 | 123.0743 | 123.175 | -123.5001 | -46.4218
4863.7656 | 123.3353 | -68.1976 | 54.8904 | -0.2253 | 0.0088738 | 0.00040586 | 0.001993 | -0.012954 | -0.0073593 | -0.0047938 | 54.9088 | 54.9637 | -68.5913 | 55.1285 | 54.895 | 54.8813 | 54.8813 | 55.0827 | 54.9728 | 8.4961 | -0.39368 | 0.073242 | 123.1064 | 123.3261 | 0.004578 | 76.6937 | 0.082397 | 123.5001 | 123.0789 | 123.2803 | 123.0927 | 123.1613 | 123.1064 | 123.1705 | 123.0789 | 76.6937 | 123.1613 | 123.1064 | 123.0789 | 123.0927 | 123.1705 | -123.4818 | -46.3943
4864.7656 | 123.3765 | -68.2022 | 54.8767 | 0.034104 | 0.0095148 | -0.00044854 | 7.0444e-05 | -0.012313 | -0.0056503 | -0.0015894 | 54.8721 | 54.9454 | -68.5913 | 55.1102 | 54.9088 | 54.8904 | 54.7897 | 55.0781 | 54.9225 | 8.5007 | -0.3891 | 0.068665 | 123.0743 | 123.3124 | 0.032043 | 76.7029 | 0.045776 | 123.4634 | 122.9919 | 123.2803 | 123.111 | 123.1476 | 123.0743 | 123.1247 | 123.0927 | 76.7029 | 123.1476 | 123.0743 | 123.0927 | 123.111 | 123.1247 | -123.468 | -46.376
4865.7812 | 123.3582 | -68.2022 | 54.8721 | -0.15663 | 0.010369 | 0.00061946 | 0.0032748 | -0.0095361 | -0.0060775 | -0.0041528 | 54.9408 | 54.9545 | -68.573 | 55.1376 | 54.9225 | 54.8813 | 54.8492 | 55.1056 | 54.9362 | 8.5007 | -0.37079 | 0.082398 | 123.143 | 123.3398 | 0.050354 | 76.7029 | 0.064087 | 123.5138 | 123.0515 | 123.3078 | 123.1247 | 123.1567 | 123.143 | 123.1384 | 123.0835 | 76.7029 | 123.1567 | 123.143 | 123.0835 | 123.1247 | 123.1384 | -123.4451 | -46.3715
4866.7812 | 123.349 | -68.1885 | 54.8721 | -0.072708 | 0.0088738 | 0.0055329 | 0.0028476 | -0.012527 | -0.0090683 | -0.0037256 | 54.9316 | 54.9408 | -68.5867 | 55.1468 | 54.9316 | 54.9179 | 54.8172 | 55.1147 | 54.9271 | 8.5007 | -0.39825 | 0.068665 | 123.1201 | 123.3353 | 0.05951 | 76.6891 | 0.054932 | 123.5184 | 123.0057 | 123.3032 | 123.1201 | 123.1293 | 123.1201 | 123.1155 | 123.1064 | 76.6891 | 123.1293 | 123.1201 | 123.1064 | 123.1201 | 123.1155 | -123.4589 | -46.3715
4867.7812 | 123.3856 | -68.2022 | 54.8813 | -0.065079 | 0.0088738 | -0.0023711 | 0.001993 | -0.0121 | -0.0043685 | -0.001803 | 54.9133 | 54.9316 | -68.6142 | 55.188 | 54.9408 | 54.9408 | 54.776 | 55.1331 | 54.9316 | 8.4961 | -0.41199 | 0.050354 | 123.1155 | 123.3902 | 0.059509 | 76.6983 | 0.050354 | 123.5275 | 122.9782 | 123.3353 | 123.143 | 123.1338 | 123.1155 | 123.1338 | 123.143 | 76.6983 | 123.1338 | 123.1155 | 123.143 | 123.143 | 123.1338 | -123.4955 | -46.3852
4868.7812 | 123.3765 | -68.2022 | 54.8676 | -0.026932 | 0.0084466 | 0.0033967 | 0.0013522 | -0.013809 | -0.0086411 | -0.0028712 | 54.8813 | 54.9362 | -68.6142 | 55.1376 | 54.9316 | 54.9133 | 54.7806 | 55.101 | 54.9271 | 8.5007 | -0.41199 | 0.068664 | 123.0835 | 123.3398 | 0.064087 | 76.7029 | 0.059509 | 123.4955 | 122.9828 | 123.3032 | 123.1338 | 123.1384 | 123.0835 | 123.1293 | 123.1155 | 76.7029 | 123.1384 | 123.0835 | 123.1155 | 123.1338 | 123.1293 | -123.4818 | -46.3669
4869.7656 | 123.3765 | -68.1519 | 54.8859 | -0.10323 | 0.006524 | -0.00044854 | -0.00078396 | -0.015517 | -0.0082137 | -0.0028712 | 55.1147 | 54.982 | -68.5455 | 55.1651 | 54.8813 | 54.9088 | 54.7714 | 55.1285 | 54.9088 | 8.5007 | -0.39368 | 0.096131 | 123.2666 | 123.317 | -0.004577 | 76.6525 | 0.022888 | 123.6603 | 122.9233 | 123.2803 | 123.0331 | 123.1338 | 123.2666 | 123.0606 | 123.0606 | 76.6525 | 123.1338 | 123.2666 | 123.0606 | 123.0331 | 123.0606 | -123.4314 | -46.3852
4870.7656 | 123.3307 | -68.1702 | 54.9042 | -0.10323 | 0.0067376 | 0.0023285 | 0.0024202 | -0.012954 | -0.0077865 | -0.0015894 | 54.9316 | 54.9545 | -68.6005 | 55.1559 | 54.9271 | 54.9362 | 54.8035 | 55.1971 | 54.9179 | 8.4961 | -0.4303 | 0.050354 | 123.1018 | 123.3261 | 0.022888 | 76.6663 | 0.013733 | 123.5321 | 122.9736 | 123.3673 | 123.0972 | 123.1247 | 123.1018 | 123.0881 | 123.1064 | 76.6663 | 123.1247 | 123.1018 | 123.1064 | 123.0972 | 123.0881 | -123.5046 | -46.4081
4871.7812 | 123.3124 | -68.2114 | 54.9042 | -0.14137 | 0.013146 | 0.0027557 | 0.008829 | -0.012527 | -0.0052231 | -0.0047938 | 54.8813 | 55.069 | -68.5867 | 55.0919 | 54.8401 | 54.8035 | 54.9637 | 55.0186 | 54.9683 | 8.4915 | -0.37537 | 0.16479 | 123.0927 | 123.3032 | -0.064087 | 76.7029 | 0.064087 | 123.468 | 123.175 | 123.23 | 123.0515 | 123.2803 | 123.0927 | 123.1796 | 123.0148 | 76.7029 | 123.2803 | 123.0927 | 123.0148 | 123.0515 | 123.1796 | -123.4909 | -46.4127
4872.7812 | 123.2758 | -68.2205 | 54.9133 | -0.17952 | 0.013787 | 0.00083306 | 0.0047702 | -0.0091089 | -0.0060775 | -0.0022302 | 54.8584 | 55.0552 | -68.5822 | 55.0781 | 54.8538 | 54.8309 | 54.9728 | 55.0095 | 54.9957 | 8.4961 | -0.36163 | 0.14191 | 123.0789 | 123.2986 | -0.059509 | 76.7166 | 0.082398 | 123.4406 | 123.1934 | 123.23 | 123.0743 | 123.2758 | 123.0789 | 123.2162 | 123.0515 | 76.7166 | 123.2758 | 123.0789 | 123.0515 | 123.0743 | 123.2162 | -123.4955 | -46.4172
4873.7812 | 123.3582 | -68.2114 | 54.8721 | 0.064621 | 0.0080194 | 0.00083306 | -0.0016386 | -0.011459 | -0.0052231 | -0.0022302 | 54.8492 | 54.9408 | -68.6417 | 55.0964 | 54.9088 | 54.8721 | 54.7943 | 55.0644 | 54.9316 | 8.4961 | -0.4303 | 0.068665 | 123.0606 | 123.3078 | 0.036621 | 76.7075 | 0.05951 | 123.4909 | 123.0057 | 123.2758 | 123.1201 | 123.1522 | 123.0606 | 123.143 | 123.0835 | 76.7075 | 123.1522 | 123.0606 | 123.0835 | 123.1201 | 123.143 | -123.5138 | -46.376
4874.7812 | 123.3398 | -68.2022 | 54.863 | 0.54527 | 0.011865 | 0.00019226 | 0.0013522 | -0.013168 | -0.0060775 | -0.0015894 | 54.8492 | 54.9637 | -68.605 | 55.0873 | 54.8721 | 54.8538 | 54.7943 | 55.0323 | 54.9133 | 8.4961 | -0.40283 | 0.10071 | 123.0515 | 123.2895 | 0.009155 | 76.6983 | 0.050354 | 123.4543 | 122.9965 | 123.2346 | 123.0743 | 123.1659 | 123.0515 | 123.1155 | 123.056 | 76.6983 | 123.1659 | 123.0515 | 123.056 | 123.0743 | 123.1155 | -123.468 | -46.3669
4875.7812 | 123.3398 | -68.2022 | 54.8813 | 0.14092 | 0.0084466 | 0.0042511 | -0.00099756 | -0.013595 | -0.0065047 | -0.0013758 | 54.8401 | 54.95 | -68.6325 | 55.0735 | 54.8813 | 54.8676 | 54.8584 | 55.2155 | 54.9088 | 8.4961 | -0.4303 | 0.068664 | 123.0423 | 123.2758 | 0 | 76.6983 | 0.027465 | 123.4726 | 123.0606 | 123.4177 | 123.0835 | 123.1522 | 123.0423 | 123.111 | 123.0698 | 76.6983 | 123.1522 | 123.0423 | 123.0698 | 123.0835 | 123.111 | -123.5138 | -46.3852
4876.7812 | 123.2758 | -68.2251 | 54.9088 | -0.149 | 0.012933 | 0.0029693 | 0.0058382 | -0.011245 | -0.0062911 | -0.0037256 | 54.8676 | 55.0461 | -68.605 | 55.0827 | 54.8492 | 54.8126 | 54.9683 | 55.014 | 54.9637 | 8.4915 | -0.37994 | 0.13733 | 123.0927 | 123.3078 | -0.059509 | 76.7166 | 0.054932 | 123.4726 | 123.1934 | 123.2391 | 123.0743 | 123.2712 | 123.0927 | 123.1888 | 123.0377 | 76.7166 | 123.2712 | 123.0927 | 123.0377 | 123.0743 | 123.1888 | -123.5138 | -46.4172
4877.7656 | 123.3582 | -68.1656 | 54.863 | 0.19432 | 0.011651 | 0.0019013 | 0.00049764 | -0.011672 | -0.0056503 | -0.0043664 | 54.8309 | 54.9545 | -68.5867 | 55.0919 | 54.8813 | 54.8721 | 54.7989 | 55.0461 | 54.9454 | 8.4915 | -0.42114 | 0.091553 | 122.9965 | 123.2574 | 0.018311 | 76.6571 | 0.082398 | 123.4177 | 122.9645 | 123.2117 | 123.0469 | 123.1201 | 122.9965 | 123.111 | 123.0377 | 76.6571 | 123.1201 | 122.9965 | 123.0377 | 123.0469 | 123.111 | -123.4497 | -46.3715
4878.7656 | 123.3856 | -68.2114 | 54.8355 | 0.26299 | 0.011865 | 0.0048921 | 0.0034884 | -0.011031 | -0.0062911 | -0.00073479 | 54.9316 | 54.9042 | -68.6142 | 55.1514 | 54.9271 | 54.8904 | 54.7348 | 55.0644 | 54.895 | 8.4961 | -0.40283 | 0.068665 | 123.143 | 123.3627 | 0.091553 | 76.7075 | 0.05951 | 123.5458 | 122.9462 | 123.2758 | 123.1384 | 123.1155 | 123.143 | 123.1064 | 123.1018 | 76.7075 | 123.1155 | 123.143 | 123.1018 | 123.1384 | 123.1064 | -123.4497 | -46.3394
4879.7812 | 123.3856 | -68.2297 | 54.8538 | 0.28587 | 0.012078 | 0.0046783 | 0.003702 | -0.011031 | -0.0069321 | -0.0022302 | 54.8996 | 54.9179 | -68.5913 | 55.0964 | 54.8904 | 54.8767 | 54.7302 | 55.0415 | 54.895 | 8.5007 | -0.36163 | 0.064087 | 123.1293 | 123.3261 | 0.036621 | 76.7303 | 0.041199 | 123.4909 | 122.9599 | 123.2712 | 123.1201 | 123.1476 | 123.1293 | 123.1247 | 123.1064 | 76.7303 | 123.1476 | 123.1293 | 123.1064 | 123.1201 | 123.1247 | -123.4451 | -46.3531
4880.7812 | 123.3444 | -68.2159 | 54.8447 | 0.21721 | 0.010583 | 0.0076691 | 0.003702 | -0.010391 | -0.0073593 | -0.0015894 | 54.895 | 54.9271 | -68.5959 | 55.101 | 54.8767 | 54.8859 | 54.7485 | 55.0278 | 54.895 | 8.5007 | -0.37994 | 0.082397 | 123.111 | 123.317 | 0.032043 | 76.7166 | 0.050354 | 123.4909 | 122.9645 | 123.2437 | 123.0927 | 123.143 | 123.111 | 123.111 | 123.1018 | 76.7166 | 123.143 | 123.111 | 123.1018 | 123.0927 | 123.111 | -123.4406 | -46.344
4881.7812 | 123.3902 | -68.1747 | 54.8859 | -0.019302 | 0.012505 | 0.00061946 | 0.0024202 | -0.011672 | -0.0058639 | -0.003512 | 54.9133 | 54.9545 | -68.5822 | 55.1331 | 54.9545 | 54.9225 | 54.7989 | 55.1468 | 54.9133 | 8.4961 | -0.40741 | 0.068665 | 123.0881 | 123.3078 | 0.068665 | 76.6708 | 0.027466 | 123.4955 | 122.9736 | 123.3215 | 123.1293 | 123.1293 | 123.0881 | 123.0881 | 123.0972 | 76.6708 | 123.1293 | 123.0881 | 123.0972 | 123.1293 | 123.0881 | -123.468 | -46.3898
4882.7656 | 123.3398 | -68.1931 | 54.863 | 0.19432 | 0.010583 | 0.0023285 | 0.0022066 | -0.0121 | -0.0065047 | -0.0013758 | 54.8447 | 54.9408 | -68.5822 | 55.0781 | 54.8676 | 54.8676 | 54.7714 | 55.0369 | 54.8904 | 8.4961 | -0.3891 | 0.07782 | 123.0377 | 123.2712 | 0.004578 | 76.6891 | 0.027466 | 123.4268 | 122.9645 | 123.23 | 123.0606 | 123.1338 | 123.0377 | 123.0835 | 123.0606 | 76.6891 | 123.1338 | 123.0377 | 123.0606 | 123.0606 | 123.0835 | -123.4451 | -46.3669
4883.7656 | 123.3444 | -68.2114 | 54.8447 | 0.20958 | 0.011865 | 0.0091645 | 0.0030612 | -0.012954 | -0.0041549 | -0.0039392 | 54.8904 | 54.9774 | -68.5959 | 55.0735 | 54.863 | 54.8721 | 54.7531 | 55.0232 | 54.8721 | 8.4869 | -0.38452 | 0.13275 | 123.1018 | 123.2849 | 0.01831 | 76.6983 | 0.027465 | 123.4863 | 122.9645 | 123.2346 | 123.0743 | 123.1888 | 123.1018 | 123.0835 | 123.0835 | 76.6983 | 123.1888 | 123.1018 | 123.0835 | 123.0743 | 123.0835 | -123.4406 | -46.3577
4884.7656 | 123.3627 | -68.2297 | 54.8309 | 0.26299 | 0.010369 | 0.0080963 | 0.0051974 | -0.011459 | -0.0062911 | -0.0013758 | 54.9179 | 54.9637 | -68.6188 | 55.1147 | 54.8676 | 54.8996 | 54.7119 | 55.0507 | 54.8721 | 8.4961 | -0.3891 | 0.13275 | 123.1476 | 123.3444 | 0.036621 | 76.7258 | 0.041198 | 123.5367 | 122.9416 | 123.2803 | 123.0972 | 123.1934 | 123.1476 | 123.1018 | 123.1293 | 76.7258 | 123.1934 | 123.1476 | 123.1293 | 123.0972 | 123.1018 | -123.4497 | -46.3348
4885.7656 | 123.262 | -68.2617 | 54.863 | 0.20195 | 0.016137 | 0.0072419 | 0.010111 | -0.0069727 | -0.0054367 | -0.00094839 | 54.8355 | 55.0598 | -68.6234 | 55.0552 | 54.7943 | 54.7806 | 54.8538 | 54.9316 | 54.9133 | 8.4824 | -0.36163 | 0.19684 | 123.0972 | 123.317 | -0.068664 | 76.7441 | 0.050354 | 123.4589 | 123.1155 | 123.1934 | 123.056 | 123.3215 | 123.0972 | 123.175 | 123.0423 | 76.7441 | 123.3215 | 123.0972 | 123.0423 | 123.056 | 123.175 | -123.4863 | -46.3806
4886.7812 | 123.3078 | -68.2434 | 54.8721 | 0.24773 | 0.012078 | 0.0042511 | 0.0096834 | -0.0069727 | -0.0043685 | -0.0026574 | 54.8538 | 55.0323 | -68.6279 | 55.0598 | 54.8218 | 54.808 | 54.8401 | 54.95 | 54.9408 | 8.4961 | -0.38452 | 0.16022 | 123.0972 | 123.3032 | -0.050354 | 76.7395 | 0.068665 | 123.4818 | 123.0835 | 123.1934 | 123.0652 | 123.2758 | 123.0972 | 123.1842 | 123.0515 | 76.7395 | 123.2758 | 123.0972 | 123.0515 | 123.0652 | 123.1842 | -123.5001 | -46.376
4887.7812 | 123.3398 | -68.2343 | 54.8401 | 0.24773 | 0.012719 | 0.0051057 | 0.0084018 | -0.010604 | -0.0069321 | -0.0024438 | 54.8584 | 55.0186 | -68.6096 | 55.0598 | 54.8492 | 54.8355 | 54.7943 | 55.0003 | 54.8859 | 8.4961 | -0.37537 | 0.17853 | 123.0927 | 123.2941 | 0.009155 | 76.7303 | 0.045776 | 123.468 | 123.0286 | 123.2346 | 123.0835 | 123.2529 | 123.0927 | 123.1201 | 123.0698 | 76.7303 | 123.2529 | 123.0927 | 123.0698 | 123.0835 | 123.1201 | -123.4497 | -46.344
4888.7812 | 123.3032 | -68.2571 | 54.8447 | 0.23247 | 0.015923 | 0.0044647 | 0.008829 | -0.0084681 | -0.0065047 | -0.0026574 | 54.8447 | 55.0186 | -68.6417 | 55.0507 | 54.8355 | 54.8126 | 54.8401 | 54.95 | 54.9362 | 8.4961 | -0.38452 | 0.17395 | 123.1018 | 123.3078 | -0.009156 | 76.7532 | 0.091552 | 123.4863 | 123.0972 | 123.2071 | 123.0927 | 123.2758 | 123.1018 | 123.1934 | 123.0698 | 76.7532 | 123.2758 | 123.1018 | 123.0698 | 123.0927 | 123.1934 | -123.4863 | -46.3486
4889.7656 | 123.3582 | -68.2022 | 54.8309 | 0.24773 | 0.013574 | 0.0053193 | 0.0062656 | -0.0067591 | -0.0052231 | 0.00054681 | 54.9042 | 54.9866 | -68.6005 | 55.101 | 54.8996 | 54.8904 | 54.7119 | 55.0323 | 54.895 | 8.4961 | -0.39826 | 0.15564 | 123.1064 | 123.3032 | 0.068664 | 76.6983 | 0.064087 | 123.5046 | 122.9141 | 123.2346 | 123.1018 | 123.1888 | 123.1064 | 123.0972 | 123.0927 | 76.6983 | 123.1888 | 123.1064 | 123.0927 | 123.1018 | 123.0972 | -123.4314 | -46.3348
4890.7656 | 123.3398 | -68.2434 | 54.8172 | 0.28587 | 0.014001 | 0.0021149 | 0.0058382 | -0.0080407 | -0.0047957 | -0.0022302 | 54.8904 | 55.0323 | -68.605 | 55.0873 | 54.8676 | 54.8676 | 54.8904 | 55.1971 | 54.9591 | 8.4961 | -0.36163 | 0.21515 | 123.1338 | 123.3307 | 0.050354 | 76.7395 | 0.14191 | 123.4955 | 123.1338 | 123.4406 | 123.111 | 123.2758 | 123.1338 | 123.2025 | 123.111 | 76.7395 | 123.2758 | 123.1338 | 123.111 | 123.111 | 123.2025 | -123.4222 | -46.3211
4891.7656 | 123.3124 | -68.2297 | 54.8309 | 0.27061 | 0.012719 | 0.0066009 | 0.00712 | -0.0071863 | -0.0067185 | -0.0026574 | 54.863 | 55.0507 | -68.605 | 55.0552 | 54.8355 | 54.8172 | 54.8172 | 54.9774 | 54.9225 | 8.4915 | -0.37537 | 0.21973 | 123.0927 | 123.2849 | 0.004577 | 76.7212 | 0.091552 | 123.468 | 123.0469 | 123.2071 | 123.0652 | 123.2803 | 123.0927 | 123.1522 | 123.0469 | 76.7212 | 123.2803 | 123.0927 | 123.0469 | 123.0652 | 123.1522 | -123.436 | -46.3394
4892.7656 | 123.2849 | -68.248 | 54.8904 | 0.041733 | 0.013787 | 0.00083306 | 0.0090426 | -0.0065455 | -0.0069321 | -0.0028712 | 54.8904 | 55.0781 | -68.5959 | 55.0598 | 54.8538 | 54.8355 | 54.9042 | 54.9911 | 54.9454 | 8.4869 | -0.3479 | 0.18768 | 123.1384 | 123.3078 | -0.036621 | 76.7349 | 0.054932 | 123.4863 | 123.1522 | 123.2391 | 123.1018 | 123.3261 | 123.1384 | 123.1934 | 123.0835 | 76.7349 | 123.3261 | 123.1384 | 123.0835 | 123.1018 | 123.1934 | -123.4863 | -46.4035
4893.7812 | 123.2712 | -68.2434 | 54.8767 | 0.064621 | 0.014001 | 0.010232 | 0.0077608 | -0.0063317 | -0.0067185 | -0.0022302 | 54.8904 | 55.0735 | -68.6142 | 55.0415 | 54.8172 | 54.8218 | 54.9088 | 54.9591 | 54.9545 | 8.4915 | -0.37079 | 0.19684 | 123.1338 | 123.2849 | -0.059509 | 76.7349 | 0.07782 | 123.5046 | 123.1522 | 123.2025 | 123.0606 | 123.317 | 123.1338 | 123.1979 | 123.0652 | 76.7349 | 123.317 | 123.1338 | 123.0652 | 123.0606 | 123.1979 | -123.4909 | -46.3852
4894.7812 | 123.2483 | -68.28 | 54.8996 | 0.1104 | 0.012933 | 0.0038239 | 0.00712 | -0.0076135 | -0.0082137 | -0.0026574 | 54.8813 | 55.0827 | -68.6371 | 55.014 | 54.8035 | 54.7806 | 54.9133 | 54.9271 | 54.9683 | 8.4915 | -0.35706 | 0.18311 | 123.1613 | 123.2941 | -0.09613 | 76.7715 | 0.068665 | 123.5184 | 123.1934 | 123.2071 | 123.0835 | 123.3627 | 123.1613 | 123.2483 | 123.0606 | 76.7715 | 123.3627 | 123.1613 | 123.0606 | 123.0835 | 123.2483 | -123.5367 | -46.4081
4895.7812 | 123.262 | -68.2251 | 54.8767 | -0.74409 | 0.011651 | 0.0068147 | 0.0075472 | -0.0056909 | -0.0073593 | -0.0028712 | 54.863 | 55.0644 | -68.6005 | 55.0369 | 54.8126 | 54.8355 | 54.9042 | 54.9637 | 54.9866 | 8.4915 | -0.37537 | 0.18768 | 123.0881 | 123.262 | -0.064087 | 76.7166 | 0.10986 | 123.4634 | 123.1293 | 123.1888 | 123.0377 | 123.2895 | 123.0881 | 123.2117 | 123.0606 | 76.7166 | 123.2895 | 123.0881 | 123.0606 | 123.0377 | 123.2117 | -123.4772 | -46.3852
4896.7656 | 123.2574 | -68.2663 | 54.8904 | 0.15617 | 0.012719 | 0.0063873 | 0.0090426 | -0.0063317 | -0.0075729 | -0.003512 | 54.8309 | 55.0873 | -68.6234 | 54.982 | 54.7989 | 54.7668 | 54.8859 | 54.9362 | 54.9545 | 8.4915 | -0.35706 | 0.19684 | 123.0972 | 123.2483 | -0.091553 | 76.7578 | 0.064087 | 123.4543 | 123.1522 | 123.2025 | 123.0652 | 123.3536 | 123.0972 | 123.2208 | 123.0331 | 76.7578 | 123.3536 | 123.0972 | 123.0331 | 123.0652 | 123.2208 | -123.5138 | -46.3989
4897.7656 | 123.2529 | -68.2526 | 54.863 | -0.27107 | 0.012292 | 0.0066009 | 0.0075472 | -0.0067591 | -0.0062911 | -0.0030848 | 54.9088 | 55.0644 | -68.6234 | 54.9957 | 54.8126 | 54.7806 | 54.9133 | 54.95 | 54.9545 | 8.4915 | -0.37079 | 0.20142 | 123.1613 | 123.2483 | -0.050354 | 76.7441 | 0.091553 | 123.5321 | 123.1659 | 123.2025 | 123.0652 | 123.317 | 123.1613 | 123.2071 | 123.0331 | 76.7441 | 123.317 | 123.1613 | 123.0331 | 123.0652 | 123.2071 | -123.4863 | -46.3715
4898.7656 | 123.2849 | -68.2434 | 54.8813 | 0.1104 | 0.014214 | 0.0031831 | 0.0058382 | -0.0071863 | -0.0071457 | -0.00030759 | 54.8676 | 55.069 | -68.6142 | 55.0095 | 54.8355 | 54.8035 | 54.9362 | 54.9591 | 54.9911 | 8.4915 | -0.37079 | 0.18768 | 123.111 | 123.2529 | -0.045777 | 76.7349 | 0.10986 | 123.4818 | 123.1796 | 123.2025 | 123.0789 | 123.3124 | 123.111 | 123.2346 | 123.0469 | 76.7349 | 123.3124 | 123.111 | 123.0469 | 123.0789 | 123.2346 | -123.4955 | -46.3898
4899.7812 | 123.2849 | -68.2159 | 54.8859 | -0.04982 | 0.014001 | 0.0085235 | 0.0047702 | -0.0046229 | -0.0054367 | 0.0022558 | 54.9179 | 55.0598 | -68.5867 | 54.95 | 54.7028 | 54.8355 | 54.9271 | 55.1193 | 54.9774 | 8.4915 | -0.37079 | 0.17395 | 123.1338 | 123.1659 | -0.1831 | 76.7075 | 0.091553 | 123.5046 | 123.143 | 123.3353 | 122.9187 | 123.2758 | 123.1338 | 123.1934 | 123.0515 | 76.7075 | 123.2758 | 123.1338 | 123.0515 | 122.9187 | 123.1934 | -123.4726 | -46.3943
4900.7812 | 123.3215 | -68.2251 | 54.9088 | -0.149 | 0.013574 | 0.0036103 | 0.0041292 | -0.0056909 | -0.0090683 | -0.0015894 | 54.895 | 55.0827 | -68.605 | 55.0735 | 54.8721 | 54.8584 | 54.9408 | 55.0415 | 55.014 | 8.4915 | -0.37994 | 0.17395 | 123.1201 | 123.2986 | -0.036621 | 76.7166 | 0.10529 | 123.5001 | 123.1659 | 123.2666 | 123.0972 | 123.3078 | 123.1201 | 123.2391 | 123.0835 | 76.7166 | 123.3078 | 123.1201 | 123.0835 | 123.0972 | 123.2391 | -123.5138 | -46.4172
4901.7812 | 123.3215 | -68.2159 | 54.9179 | 0.0035856 | 0.013146 | 0.0046783 | 0.00712 | -0.0050501 | -0.0069321 | -0.0024438 | 54.9271 | 55.069 | -68.6142 | 55.0644 | 54.863 | 54.8584 | 54.9225 | 55.0415 | 55.0049 | 8.4961 | -0.39826 | 0.15106 | 123.143 | 123.2803 | -0.054932 | 76.712 | 0.086975 | 123.5413 | 123.1384 | 123.2574 | 123.0789 | 123.2849 | 123.143 | 123.2208 | 123.0743 | 76.712 | 123.2849 | 123.143 | 123.0743 | 123.0789 | 123.2208 | -123.5321 | -46.4218
4902.7812 | 123.3124 | -68.248 | 54.8859 | -0.11848 | 0.011224 | 0.0087373 | 0.0041292 | -0.0059045 | -0.0056503 | -0.0026574 | 54.895 | 55.0781 | -68.605 | 55.0735 | 54.8676 | 54.8676 | 54.95 | 55.0369 | 54.982 | 8.5007 | -0.35706 | 0.19226 | 123.143 | 123.3215 | -0.01831 | 76.7487 | 0.096131 | 123.5001 | 123.1979 | 123.2849 | 123.1155 | 123.3261 | 123.143 | 123.23 | 123.1155 | 76.7487 | 123.3261 | 123.143 | 123.1155 | 123.1155 | 123.23 | -123.4909 | -46.3852
4903.7656 | 123.2941 | -68.2388 | 54.895 | 0.011215 | 0.012292 | 0.0033967 | 0.0079744 | -0.0082545 | -0.0073593 | -0.0024438 | 54.9133 | 55.0461 | -68.605 | 55.0644 | 54.8447 | 54.8721 | 54.895 | 55.0415 | 54.9774 | 8.4961 | -0.36621 | 0.15106 | 123.1522 | 123.3032 | -0.050354 | 76.7349 | 0.082397 | 123.5184 | 123.1339 | 123.2803 | 123.0835 | 123.2849 | 123.1522 | 123.2162 | 123.111 | 76.7349 | 123.2849 | 123.1522 | 123.111 | 123.0835 | 123.2162 | -123.5001 | -46.3989
4904.7656 | 123.3353 | -68.2388 | 54.9179 | -0.072708 | 0.013146 | 0.0023285 | 0.005411 | -0.0061181 | -0.0060775 | -0.0020166 | 54.9042 | 55.0415 | -68.6188 | 55.069 | 54.8538 | 54.8538 | 54.9316 | 55.0369 | 54.9911 | 8.4869 | -0.37994 | 0.1236 | 123.143 | 123.3078 | -0.064087 | 76.7258 | 0.073242 | 123.5229 | 123.1705 | 123.2758 | 123.0927 | 123.2803 | 123.143 | 123.23 | 123.0927 | 76.7258 | 123.2803 | 123.143 | 123.0927 | 123.0927 | 123.23 | -123.5367 | -46.431
4905.7656 | 123.3124 | -68.2068 | 54.8904 | -0.10323 | 0.011865 | 0.012582 | 0.004343 | -0.0082545 | -0.0084273 | -0.00094839 | 54.895 | 55.0369 | -68.6005 | 55.0735 | 54.8676 | 54.863 | 54.9088 | 55.0323 | 54.9866 | 8.4961 | -0.39368 | 0.14648 | 123.1018 | 123.2803 | -0.022888 | 76.7029 | 0.09613 | 123.4955 | 123.1155 | 123.2391 | 123.0743 | 123.2437 | 123.1018 | 123.1934 | 123.0698 | 76.7029 | 123.2437 | 123.1018 | 123.0698 | 123.0743 | 123.1934 | -123.4909 | -46.3943
4906.7812 | 123.2529 | -68.2526 | 54.9179 | -0.19478 | 0.012078 | 0.0016877 | 7.0444e-05 | -0.0093225 | -0.0056503 | -0.0030848 | 54.8492 | 55.0598 | -68.5959 | 55.0369 | 54.8447 | 54.8218 | 55.0095 | 55.0186 | 55.0461 | 8.4915 | -0.34332 | 0.14191 | 123.1018 | 123.2895 | -0.073242 | 76.7441 | 0.12817 | 123.4451 | 123.262 | 123.2712 | 123.0972 | 123.3124 | 123.1018 | 123.2986 | 123.0743 | 76.7441 | 123.3124 | 123.1018 | 123.0743 | 123.0972 | 123.2986 | -123.5138 | -46.4264
4907.7812 | 123.2666 | -68.2434 | 54.9316 | -0.20241 | 0.012719 | -0.0010895 | 0.0039156 | -0.0084681 | -0.0073593 | -0.0020166 | 54.9454 | 55.0552 | -68.573 | 55.0095 | 54.8172 | 54.8126 | 54.9911 | 55.0278 | 54.9957 | 8.4915 | -0.32959 | 0.1236 | 123.1888 | 123.2529 | -0.11444 | 76.7349 | 0.064087 | 123.5184 | 123.2346 | 123.2712 | 123.0606 | 123.2986 | 123.1888 | 123.2391 | 123.056 | 76.7349 | 123.2986 | 123.1888 | 123.056 | 123.0606 | 123.2391 | -123.5046 | -46.4401
4908.7812 | 123.2346 | -68.2388 | 54.9225 | -0.23293 | 0.010583 | 0.0053193 | 0.0024202 | -0.010177 | -0.0060775 | -0.0024438 | 54.8447 | 55.0415 | -68.6142 | 55.0232 | 54.8355 | 54.8126 | 55.0095 | 55.0232 | 55.0186 | 8.4915 | -0.37537 | 0.11902 | 123.0835 | 123.262 | -0.086975 | 76.7303 | 0.096131 | 123.4589 | 123.2483 | 123.262 | 123.0743 | 123.2803 | 123.0835 | 123.2574 | 123.0515 | 76.7303 | 123.2803 | 123.0835 | 123.0515 | 123.0743 | 123.2574 | -123.5367 | -46.431
4909.7812 | 123.262 | -68.2251 | 54.9179 | -0.2253 | 0.011651 | 0.0023285 | 0.001993 | -0.0099633 | -0.0069321 | -0.0015894 | 54.8584 | 55.0323 | -68.5822 | 55.0507 | 54.8355 | 54.8218 | 54.9911 | 55.0369 | 55.0232 | 8.4915 | -0.35706 | 0.11444 | 123.0835 | 123.2758 | -0.082398 | 76.7166 | 0.10529 | 123.4406 | 123.2162 | 123.262 | 123.0606 | 123.2574 | 123.0835 | 123.2483 | 123.0469 | 76.7166 | 123.2574 | 123.0835 | 123.0469 | 123.0606 | 123.2483 | -123.5001 | -46.4264
4910.7656 | 123.2712 | -68.2343 | 54.9133 | -0.17189 | 0.013787 | 0.0033967 | 0.004343 | -0.0093225 | -0.0073593 | -9.3992e-05 | 54.8218 | 55.0049 | -68.6508 | 55.0369 | 54.8218 | 54.8035 | 54.982 | 55.0278 | 55.0095 | 8.5007 | -0.41657 | 0.091553 | 123.056 | 123.2712 | -0.091553 | 76.7349 | 0.09613 | 123.4726 | 123.2162 | 123.262 | 123.056 | 123.2391 | 123.056 | 123.2437 | 123.0377 | 76.7349 | 123.2391 | 123.056 | 123.0377 | 123.056 | 123.2437 | -123.5641 | -46.4127
4911.7656 | 123.2758 | -68.2343 | 54.9088 | -0.17952 | 0.01336 | 0.0040375 | -0.00057036 | -0.0076135 | -0.0058639 | -0.0026574 | 54.8538 | 55.0415 | -68.6142 | 54.9728 | 54.8218 | 54.808 | 54.9454 | 55.0186 | 54.9957 | 8.4961 | -0.37994 | 0.13275 | 123.0881 | 123.2071 | -0.086975 | 76.7303 | 0.086976 | 123.468 | 123.1796 | 123.2529 | 123.056 | 123.2758 | 123.0881 | 123.23 | 123.0423 | 76.7303 | 123.2758 | 123.0881 | 123.0423 | 123.056 | 123.23 | -123.5229 | -46.4127
4912.7656 | 123.2758 | -68.2114 | 54.9133 | -0.21767 | 0.0093012 | 0.00083306 | 0.0024202 | -0.010818 | -0.0067185 | -0.0032984 | 54.8355 | 55.0186 | -68.6005 | 55.0323 | 54.8264 | 54.8172 | 54.9911 | 55.0323 | 55.014 | 8.4915 | -0.3891 | 0.10529 | 123.0469 | 123.2437 | -0.086975 | 76.7029 | 0.10071 | 123.436 | 123.2025 | 123.2437 | 123.0377 | 123.23 | 123.0469 | 123.2254 | 123.0286 | 76.7029 | 123.23 | 123.0469 | 123.0286 | 123.0377 | 123.2254 | -123.5138 | -46.4218
4913.7812 | 123.3765 | -68.2159 | 54.8813 | 0.049362 | 0.010156 | -0.0015167 | 0.0013522 | -0.0091089 | -0.0054367 | -0.0030848 | 54.8767 | 54.9454 | -68.5776 | 55.1422 | 54.9133 | 54.9225 | 54.8172 | 55.1422 | 54.9454 | 8.4961 | -0.36163 | 0.064087 | 123.0927 | 123.3582 | 0.032043 | 76.712 | 0.064087 | 123.4543 | 123.0331 | 123.3582 | 123.1293 | 123.1613 | 123.0927 | 123.1613 | 123.1384 | 76.712 | 123.1613 | 123.0927 | 123.1384 | 123.1293 | 123.1613 | -123.4589 | -46.3852
4914.7812 | 123.3627 | -68.1702 | 54.8813 | -0.11848 | 0.0088738 | 0.0014741 | 0.00049764 | -0.010604 | -0.0065047 | -0.0041528 | 54.9042 | 54.9683 | -68.5776 | 55.1239 | 54.9225 | 54.895 | 54.8676 | 55.1193 | 54.9454 | 8.5007 | -0.40741 | 0.086975 | 123.0743 | 123.2941 | 0.041198 | 76.6708 | 0.064087 | 123.4818 | 123.0377 | 123.2895 | 123.0927 | 123.1384 | 123.0743 | 123.1155 | 123.0652 | 76.6708 | 123.1384 | 123.0743 | 123.0652 | 123.0927 | 123.1155 | -123.4589 | -46.3806
4915.7812 | 123.3719 | -68.2068 | 54.8996 | 0.13329 | 0.010156 | 0.0016877 | 0.0013522 | -0.012527 | -0.0084273 | -0.0028712 | 54.8996 | 54.95 | -68.5684 | 55.1331 | 54.9225 | 54.9133 | 54.808 | 55.1468 | 54.9225 | 8.4915 | -0.36163 | 0.050354 | 123.1064 | 123.3398 | 0.022888 | 76.6983 | 0.022888 | 123.468 | 123.0148 | 123.3536 | 123.1293 | 123.1567 | 123.1064 | 123.1293 | 123.1201 | 76.6983 | 123.1567 | 123.1064 | 123.1201 | 123.1293 | 123.1293 | -123.468 | -46.4081
4916.7812 | 123.3902 | -68.1931 | 54.8813 | -0.149 | 0.011437 | 0.0010467 | 7.0444e-05 | -0.011886 | -0.0086411 | -0.0026574 | 54.9271 | 54.95 | -68.5501 | 55.0964 | 54.863 | 54.8904 | 54.7577 | 55.0873 | 54.9362 | 8.4915 | -0.35706 | 0.068664 | 123.1201 | 123.2895 | -0.018311 | 76.6846 | 0.054931 | 123.4772 | 122.9507 | 123.2803 | 123.056 | 123.143 | 123.1201 | 123.1293 | 123.0835 | 76.6846 | 123.143 | 123.1201 | 123.0835 | 123.056 | 123.1293 | -123.4314 | -46.3898
4917.7656 | 123.3398 | -68.1702 | 54.8996 | -0.21767 | 0.010369 | -0.00044854 | 0.0045566 | -0.014236 | -0.0058639 | -0.0043664 | 54.9088 | 54.95 | -68.5867 | 55.1147 | 54.8996 | 54.8813 | 54.8813 | 55.0919 | 54.9683 | 8.4961 | -0.41657 | 0.050354 | 123.0789 | 123.2849 | 0 | 76.6663 | 0.068665 | 123.4955 | 123.0515 | 123.262 | 123.0698 | 123.1201 | 123.0789 | 123.1384 | 123.0515 | 76.6663 | 123.1201 | 123.0789 | 123.0515 | 123.0698 | 123.1384 | -123.4863 | -46.4035
4918.7656 | 123.349 | -68.2022 | 54.8859 | -0.149 | 0.0080194 | -0.0030121 | 0.001993 | -0.014236 | -0.0075729 | -0.0026574 | 54.9088 | 54.95 | -68.5684 | 55.1376 | 54.9133 | 54.8996 | 54.8492 | 55.1193 | 54.9362 | 8.4869 | -0.36621 | 0.064087 | 123.111 | 123.3398 | 0.027466 | 76.6891 | 0.050354 | 123.4772 | 123.0515 | 123.3215 | 123.1155 | 123.1522 | 123.111 | 123.1384 | 123.1018 | 76.6891 | 123.1522 | 123.111 | 123.1018 | 123.1155 | 123.1384 | -123.4543 | -46.3989
4919.7656 | 123.3765 | -68.2068 | 54.8721 | 0.14092 | 0.010796 | -0.0021575 | 0.004343 | -0.014449 | -0.0058639 | 0.00033321 | 54.8309 | 54.9454 | -68.6005 | 55.0781 | 54.8813 | 54.8584 | 54.7897 | 55.069 | 54.95 | 8.4915 | -0.39368 | 0.073243 | 123.0377 | 123.2849 | 0.009156 | 76.6983 | 0.07782 | 123.4314 | 122.9965 | 123.2758 | 123.0881 | 123.1522 | 123.0377 | 123.1567 | 123.0652 | 76.6983 | 123.1522 | 123.0377 | 123.0652 | 123.0881 | 123.1567 | -123.4726 | -46.3806
4920.7812 | 123.2666 | -68.2297 | 54.9362 | 0.0035856 | 0.01101 | -0.0013031 | 0.0084018 | -0.014236 | -0.0067185 | -0.0043664 | 54.8813 | 55.0415 | -68.5867 | 55.0644 | 54.8355 | 54.808 | 54.9728 | 55.0186 | 54.9774 | 8.4915 | -0.35706 | 0.10529 | 123.111 | 123.2941 | -0.10071 | 76.7212 | 0.041199 | 123.468 | 123.2025 | 123.2483 | 123.0652 | 123.2712 | 123.111 | 123.2071 | 123.0377 | 76.7212 | 123.2712 | 123.111 | 123.0377 | 123.0652 | 123.2071 | -123.5229 | -46.4447
4921.7812 | 123.3673 | -68.2022 | 54.863 | 0.011215 | 0.0075922 | 0.0025421 | -0.0012112 | -0.013381 | -0.0065047 | -0.0030848 | 54.8813 | 54.9408 | -68.5822 | 55.1514 | 54.9225 | 54.9179 | 54.776 | 55.1193 | 54.9179 | 8.4915 | -0.37994 | 0.07782 | 123.0835 | 123.3536 | 0.059509 | 76.6937 | 0.054932 | 123.4634 | 122.9782 | 123.3215 | 123.1247 | 123.143 | 123.0835 | 123.1201 | 123.1201 | 76.6937 | 123.143 | 123.0835 | 123.1201 | 123.1247 | 123.1201 | -123.4451 | -46.3715
4922.7812 | 123.3719 | -68.2022 | 54.8813 | -0.057449 | 0.008233 | 0.0038239 | 0.00071144 | -0.011245 | -0.0033005 | -0.0030848 | 54.8721 | 54.9408 | -68.6005 | 55.1285 | 54.9042 | 54.9042 | 54.7897 | 55.0964 | 54.9088 | 8.4961 | -0.39826 | 0.059509 | 123.0743 | 123.3307 | 0.022888 | 76.6983 | 0.027465 | 123.4726 | 122.9919 | 123.2986 | 123.1064 | 123.143 | 123.0743 | 123.111 | 123.1064 | 76.6983 | 123.143 | 123.0743 | 123.1064 | 123.1064 | 123.111 | -123.4818 | -46.3852
4923.7812 | 123.3582 | -68.1931 | 54.8721 | 0.056992 | 0.0084466 | 0.0023285 | 0.001993 | -0.013168 | -0.0050095 | -0.003512 | 54.8584 | 54.9271 | -68.6005 | 55.1193 | 54.895 | 54.8859 | 54.7897 | 55.0827 | 54.9133 | 8.4961 | -0.40741 | 0.054932 | 123.0515 | 123.3124 | 0.022889 | 76.6891 | 0.041199 | 123.4589 | 122.9828 | 123.2758 | 123.0881 | 123.1201 | 123.0515 | 123.1064 | 123.0789 | 76.6891 | 123.1201 | 123.0515 | 123.0789 | 123.0881 | 123.1064 | -123.4726 | -46.376
4924.7656 | 123.3948 | -68.1793 | 54.863 | -0.04982 | 0.0097284 | 0.0040375 | 0.002634 | -0.013595 | -0.0060775 | -0.003512 | 54.9179 | 54.9225 | -68.5822 | 55.1697 | 54.95 | 54.9362 | 54.7806 | 55.1422 | 54.9225 | 8.4915 | -0.40283 | 0.059509 | 123.0972 | 123.349 | 0.086975 | 76.6708 | 0.059509 | 123.5001 | 122.9599 | 123.3215 | 123.1293 | 123.1018 | 123.0972 | 123.1018 | 123.1155 | 76.6708 | 123.1018 | 123.0972 | 123.1155 | 123.1293 | 123.1018 | -123.4451 | -46.3715
4925.7656 | 123.381 | -68.1885 | 54.8584 | -0.019302 | 0.0088738 | 0.0016877 | 0.0013522 | -0.013595 | -0.0047957 | -0.0020166 | 54.9088 | 54.9362 | -68.5822 | 55.1559 | 54.95 | 54.9179 | 54.7714 | 55.1193 | 54.9362 | 8.4869 | -0.39368 | 0.07782 | 123.0972 | 123.3444 | 0.091553 | 76.6754 | 0.07782 | 123.4909 | 122.9599 | 123.3078 | 123.1384 | 123.1247 | 123.0972 | 123.1247 | 123.1064 | 76.6754 | 123.1247 | 123.0972 | 123.1064 | 123.1384 | 123.1247 | -123.4406 | -46.3715
4926.7812 | 123.317 | -68.2434 | 54.8447 | 0.13329 | -0.012702 | -0.025656 | 0.00071144 | -0.012954 | -0.0080001 | -0.0065026 | -0.022888 | 0.19684 | -0.37994 | 55.2841 | 54.95 | 54.8126 | 54.7531 | 54.9728 | 54.9042 | 8.4915 | 67.8635 | -54.6478 | 68.2205 | 123.5275 | 0.10529 | 76.7349 | 0.059509 | 0.35706 | 122.9965 | 123.2162 | 123.1934 | 68.4402 | 68.2205 | 123.1476 | 123.056 | 76.7349 | 68.4402 | 68.2205 | 123.056 | 123.1934 | 123.1476 | -55.2246 | -46.3531
4927.7812 | 123.3398 | -68.2159 | 54.863 | 0.1638 | -0.012061 | -0.02587 | 0.0015658 | -0.012313 | -0.0062911 | -0.0050074 | -0.018311 | 0.19684 | -0.40283 | 55.0873 | 54.8676 | 54.8447 | 54.776 | 55.0278 | 54.9179 | 8.5007 | 67.8131 | -54.6661 | 68.1976 | 123.3032 | 0.004578 | 76.7166 | 0.054932 | 0.38452 | 122.9919 | 123.2437 | 123.0835 | 68.4128 | 68.1976 | 123.1338 | 123.0606 | 76.7166 | 68.4128 | 68.1976 | 123.0606 | 123.0835 | 123.1338 | -55.2658 | -46.3623
4928.7812 | 123.3353 | -68.1885 | 54.863 | 0.99541 | -0.012916 | -0.026083 | -0.00057036 | -0.012313 | -0.0050095 | -0.0032984 | 0.018311 | 0.19684 | -0.37079 | 55.0552 | 54.863 | 54.8584 | 54.808 | 55.0278 | 54.9133 | 8.4915 | 67.8177 | -54.6661 | 68.2068 | 123.2437 | 0 | 76.68 | 0.050354 | 0.3891 | 122.9965 | 123.2162 | 123.0515 | 68.3853 | 68.2068 | 123.1018 | 123.0469 | 76.68 | 68.3853 | 68.2068 | 123.0469 | 123.0515 | 123.1018 | -55.2338 | -46.3715
4929.7812 | 123.3261 | -68.1931 | 54.8492 | 0.095139 | -0.013343 | -0.030783 | 0.0017794 | -0.013595 | -0.0058639 | -0.0028712 | -0.022888 | 0.19684 | -0.3891 | 55.2429 | 55.0644 | 54.9088 | 54.7348 | 54.9683 | 54.8904 | 8.4869 | 67.804 | -54.6524 | 68.1702 | 123.436 | 0.21515 | 76.68 | 0.041199 | 0.36621 | 122.9279 | 123.1613 | 123.2574 | 68.3899 | 68.1702 | 123.0835 | 123.1018 | 76.68 | 68.3899 | 68.1702 | 123.1018 | 123.2574 | 123.0835 | -55.2383 | -46.3623
4930.7812 | 123.3307 | -68.2205 | 54.8584 | 0.13329 | -0.0097114 | -0.023947 | 0.00071144 | -0.010391 | -0.0052231 | -0.0022302 | -0.027466 | 0.20142 | -0.39825 | 55.0919 | 54.8721 | 54.8538 | 54.7668 | 55.0232 | 54.9042 | 8.4915 | 67.8223 | -54.657 | 68.1931 | 123.3124 | 0.013733 | 76.712 | 0.045777 | 0.37079 | 122.9874 | 123.2437 | 123.0927 | 68.4219 | 68.1931 | 123.1247 | 123.0743 | 76.712 | 68.4219 | 68.1931 | 123.0743 | 123.0927 | 123.1247 | -55.2567 | -46.3669
4931.7656 | 123.3582 | -68.2297 | 54.8492 | 0.041733 | -0.011634 | -0.028861 | 0.00092504 | -0.011886 | -0.0054367 | -0.0024438 | -0.027466 | 0.21973 | -0.38452 | 55.1102 | 54.8813 | 54.8676 | 54.7897 | 55.069 | 54.9271 | 8.4915 | 67.8452 | -54.6295 | 68.2022 | 123.3398 | 0.032044 | 76.7212 | 0.07782 | 0.35706 | 123.0194 | 123.2986 | 123.111 | 68.4494 | 68.2022 | 123.1567 | 123.0972 | 76.7212 | 68.4494 | 68.2022 | 123.0972 | 123.111 | 123.1567 | -55.2338 | -46.3577
4932.7656 | 123.3582 | -68.2022 | 54.863 | -0.13374 | -0.013343 | -0.02822 | 0.00092504 | -0.013168 | -0.0073593 | -0.0037256 | -0.022888 | 0.21057 | -0.38452 | 55.0964 | 54.8813 | 54.8767 | 54.8172 | 55.0323 | 54.9088 | 8.4869 | 67.8177 | -54.6524 | 68.1793 | 123.2986 | 0.018311 | 76.6891 | 0.045776 | 0.36163 | 123.0194 | 123.2346 | 123.0835 | 68.4128 | 68.1793 | 123.111 | 123.0789 | 76.6891 | 68.4128 | 68.1793 | 123.0789 | 123.0835 | 123.111 | -55.2475 | -46.376
4933.7656 | 123.3765 | -68.2068 | 54.8492 | -0.019302 | -0.010779 | -0.02587 | 0.0066928 | -0.0088953 | -0.0050095 | -0.0041528 | 0.009155 | 0.11902 | -0.44403 | 55.1331 | 54.8813 | 54.8904 | 54.7211 | 55.0552 | 54.8859 | 8.5007 | 67.7628 | -54.7302 | 68.2159 | 123.3398 | 0.032044 | 76.7075 | 0.036621 | 0.45319 | 122.9279 | 123.262 | 123.0881 | 68.3258 | 68.2159 | 123.0927 | 123.0972 | 76.7075 | 68.3258 | 68.2159 | 123.0972 | 123.0881 | 123.0927 | -55.2933 | -46.3486
4934.7812 | 123.3948 | -68.2068 | 54.8767 | -0.04982 | -0.012916 | -0.029501 | 0.00028404 | -0.0121 | -0.0058639 | -0.0028712 | 0.018311 | 0.21973 | -0.35706 | 55.1605 | 54.9454 | 54.9225 | 54.7989 | 55.1376 | 54.9042 | 8.4961 | 67.8497 | -54.657 | 68.2251 | 123.3673 | 0.068665 | 76.7029 | 0.027466 | 0.37537 | 123.0057 | 123.3444 | 123.1522 | 68.4265 | 68.2251 | 123.111 | 123.1293 | 76.7029 | 68.4265 | 68.2251 | 123.1293 | 123.1522 | 123.111 | -55.2338 | -46.3806
4935.7812 | 123.3536 | -68.2159 | 54.8309 | 0.23247 | -0.013343 | -0.027365 | 0.0032748 | -0.010818 | -0.0060775 | -0.003512 | -0.022888 | 0.13733 | -0.43488 | 55.1056 | 54.8767 | 54.8767 | 54.7256 | 55.0461 | 54.8676 | 8.4961 | 67.7811 | -54.6936 | 68.1931 | 123.3215 | 0.045776 | 76.712 | 0.036621 | 0.41199 | 122.9416 | 123.262 | 123.0927 | 68.3533 | 68.1931 | 123.0835 | 123.0927 | 76.712 | 68.3533 | 68.1931 | 123.0927 | 123.0927 | 123.0835 | -55.2658 | -46.3348
4936.7812 | 123.3536 | -68.2251 | 54.8492 | 0.21721 | -0.010779 | -0.023947 | 0.0051974 | -0.0095361 | -0.0054367 | -0.0032984 | -0.004578 | 0.16937 | -0.41199 | 55.1285 | 54.8996 | 54.895 | 54.7073 | 55.0415 | 54.8767 | 8.4961 | 67.8131 | -54.6799 | 68.2205 | 123.3536 | 0.050354 | 76.7212 | 0.027466 | 0.40741 | 122.9324 | 123.2666 | 123.1247 | 68.3945 | 68.2205 | 123.1018 | 123.1201 | 76.7212 | 68.3945 | 68.2205 | 123.1201 | 123.1247 | 123.1018 | -55.2612 | -46.3531
4937.7656 | 123.3536 | -68.2251 | 54.8447 | 0.21721 | -0.010779 | -0.023306 | 0.0011386 | -0.011031 | -0.0037277 | -0.0024438 | -0.036621 | 0.20142 | -0.37994 | 55.0964 | 54.8859 | 54.863 | 54.7943 | 55.0278 | 54.8996 | 8.4869 | 67.8452 | -54.6432 | 68.1885 | 123.3215 | 0.041198 | 76.712 | 0.054931 | 0.34332 | 123.0194 | 123.2529 | 123.111 | 68.4265 | 68.1885 | 123.1247 | 123.0881 | 76.712 | 68.4265 | 68.1885 | 123.0881 | 123.111 | 123.1247 | -55.2246 | -46.3577
4938.7656 | 123.3444 | -68.2022 | 54.8676 | 0.20958 | -0.0097114 | -0.025015 | 0.0015658 | -0.011886 | -0.0065047 | -0.0047938 | -0.027466 | 0.16022 | -0.40741 | 55.0964 | 54.8676 | 54.8676 | 54.7531 | 55.0369 | 54.8767 | 8.4869 | 67.7948 | -54.7073 | 68.1747 | 123.2986 | 0 | 76.6891 | 0.009155 | 0.37994 | 122.9553 | 123.2391 | 123.0698 | 68.3624 | 68.1747 | 123.0789 | 123.0698 | 76.6891 | 68.3624 | 68.1747 | 123.0698 | 123.0698 | 123.0789 | -55.275 | -46.3806
4939.7656 | 123.3353 | -68.2251 | 54.8264 | 0.21721 | -0.0086432 | -0.025443 | 0.001993 | -0.010818 | -0.0058639 | -0.0028712 | -0.027466 | 0.16022 | -0.43488 | 55.101 | 54.8813 | 54.8584 | 54.7668 | 55.0232 | 54.8584 | 8.4915 | 67.7902 | -54.6661 | 68.1976 | 123.3261 | 0.054932 | 76.7166 | 0.032043 | 0.40741 | 122.9919 | 123.2483 | 123.1064 | 68.3853 | 68.1976 | 123.0835 | 123.0835 | 76.7166 | 68.3853 | 68.1976 | 123.0835 | 123.1064 | 123.0835 | -55.2612 | -46.3348
4940.7812 | 123.3948 | -68.2068 | 54.8401 | 0.27824 | -0.0097114 | -0.020743 | 0.00712 | -0.011459 | -0.0075729 | -0.0030848 | 0.004578 | 0.15564 | -0.43945 | 55.1285 | 54.8996 | 54.895 | 54.7211 | 55.0507 | 54.8676 | 8.4961 | 67.7673 | -54.6844 | 68.2114 | 123.3353 | 0.059509 | 76.7029 | 0.027466 | 0.44403 | 122.9279 | 123.2574 | 123.1064 | 68.3624 | 68.2114 | 123.0743 | 123.1018 | 76.7029 | 68.3624 | 68.2114 | 123.1018 | 123.1064 | 123.0743 | -55.2795 | -46.344
4941.7812 | 123.3627 | -68.2343 | 54.8172 | 0.2401 | -0.0094976 | -0.022238 | 0.0092562 | -0.0095361 | -0.0041549 | -0.003512 | -0.027466 | 0.19226 | -0.42114 | 55.1056 | 54.8492 | 54.8767 | 54.7531 | 55.0507 | 54.8996 | 8.4915 | 67.8131 | -54.6249 | 68.2068 | 123.3398 | 0.032043 | 76.7258 | 0.082397 | 0.39368 | 122.9874 | 123.2849 | 123.0835 | 68.4265 | 68.2068 | 123.1338 | 123.111 | 76.7258 | 68.4265 | 68.2068 | 123.111 | 123.0835 | 123.1338 | -55.2383 | -46.3257
4942.7812 | 123.3719 | -68.2251 | 54.8492 | 0.23247 | -0.0077888 | -0.026083 | 0.0049838 | -0.0086817 | -0.0071457 | -0.003512 | 0.022888 | 0.16022 | -0.40741 | 55.1056 | 54.9316 | 54.9408 | 54.6936 | 55.0644 | 54.8813 | 8.4869 | 67.8177 | -54.689 | 68.248 | 123.3307 | 0.082398 | 76.712 | 0.032044 | 0.4303 | 122.9187 | 123.2895 | 123.1567 | 68.3853 | 68.248 | 123.1064 | 123.1659 | 76.712 | 68.3853 | 68.248 | 123.1659 | 123.1567 | 123.1064 | -55.2567 | -46.3623
4943.7812 | 123.4085 | -68.2068 | 54.8401 | 0.14092 | -0.010139 | -0.022238 | 0.005411 | -0.0086817 | -0.0069321 | -0.0032984 | -0.009155 | 0.16937 | -0.44403 | 55.1285 | 54.8996 | 54.8996 | 54.7119 | 54.8538 | 54.8721 | 8.4961 | 67.7628 | -54.6707 | 68.1976 | 123.3353 | 0.059509 | 76.7029 | 0.032043 | 0.43488 | 122.9187 | 123.0606 | 123.1064 | 68.3762 | 68.1976 | 123.0789 | 123.1064 | 76.7029 | 68.3762 | 68.1976 | 123.1064 | 123.1064 | 123.0789 | -55.2841 | -46.344
4944.7656 | 123.3719 | -68.1976 | 54.8447 | 0.26299 | -0.010139 | -0.020956 | 0.0039156 | -0.0095361 | -0.0045821 | -0.0024438 | -0.004578 | 0.16022 | -0.39368 | 55.1056 | 54.8813 | 54.9088 | 54.7256 | 55.0507 | 54.8813 | 8.4869 | 67.804 | -54.6844 | 68.1931 | 123.3032 | 0.036621 | 76.6846 | 0.036621 | 0.3891 | 122.9233 | 123.2483 | 123.0789 | 68.3578 | 68.1931 | 123.0789 | 123.1064 | 76.6846 | 68.3578 | 68.1931 | 123.1064 | 123.0789 | 123.0789 | -55.2383 | -46.3577
4945.7656 | 123.381 | -68.2343 | 54.8447 | 0.26299 | -0.0097114 | -0.021811 | 0.0062656 | -0.0084681 | -0.0037277 | -0.0028712 | -0.009155 | 0.16479 | -0.39825 | 55.1147 | 54.8904 | 54.8996 | 54.7211 | 55.0552 | 54.9042 | 8.4869 | 67.836 | -54.6799 | 68.2251 | 123.349 | 0.045776 | 76.7212 | 0.059509 | 0.3891 | 122.9553 | 123.2895 | 123.1247 | 68.399 | 68.2251 | 123.1384 | 123.1338 | 76.7212 | 68.399 | 68.2251 | 123.1338 | 123.1247 | 123.1384 | -55.2429 | -46.3577
4946.7656 | 123.3536 | -68.2205 | 54.8309 | 0.28587 | -0.010993 | -0.024588 | 0.0094698 | -0.0093225 | -0.0052231 | -0.00052119 | 0.009155 | 0.15106 | -0.37537 | 55.1193 | 54.8859 | 54.9133 | 54.7256 | 55.0644 | 54.8767 | 8.4824 | 67.8452 | -54.6799 | 68.2297 | 123.3398 | 0.054931 | 76.7029 | 0.045776 | 0.38452 | 122.9462 | 123.2849 | 123.1064 | 68.3716 | 68.2297 | 123.0972 | 123.1338 | 76.7029 | 68.3716 | 68.2297 | 123.1338 | 123.1064 | 123.0972 | -55.2063 | -46.3486
4947.7812 | 123.2666 | -68.1976 | 54.8996 | -0.18715 | -0.011634 | -0.025229 | 0.0060518 | -0.010818 | -0.0067185 | -0.0030848 | 0.027466 | 0.29297 | -0.34332 | 55.0598 | 54.9042 | 54.8859 | 54.9454 | 55.014 | 54.9728 | 8.4961 | 67.8543 | -54.6066 | 68.2251 | 123.2574 | 0.004578 | 76.6937 | 0.073242 | 0.37079 | 123.143 | 123.2117 | 123.1018 | 68.4906 | 68.2251 | 123.1705 | 123.0835 | 76.6937 | 68.4906 | 68.2251 | 123.0835 | 123.1018 | 123.1705 | -55.2429 | -46.4035
4948.7812 | 123.3856 | -68.1976 | 54.8721 | 0.011215 | -0.014197 | -0.02587 | 0.002634 | -0.012313 | -0.0065047 | -0.001803 | 0.004578 | 0.21057 | -0.36163 | 55.1193 | 54.9271 | 54.9088 | 54.8172 | 55.1147 | 54.9042 | 8.4961 | 67.836 | -54.6616 | 68.2022 | 123.317 | 0.054932 | 76.6937 | 0.032044 | 0.36621 | 123.0148 | 123.3124 | 123.1247 | 68.4082 | 68.2022 | 123.1018 | 123.1064 | 76.6937 | 68.4082 | 68.2022 | 123.1064 | 123.1247 | 123.1018 | -55.2338 | -46.376
4949.7812 | 123.3307 | -68.2343 | 54.8264 | 0.26299 | -0.009925 | -0.021811 | 0.0056246 | -0.0086817 | -0.0037277 | -0.0028712 | -0.013733 | 0.20142 | -0.42572 | 55.0781 | 54.8721 | 54.8676 | 54.7714 | 55.0369 | 54.8767 | 8.4869 | 67.8085 | -54.6249 | 68.2205 | 123.3124 | 0.045776 | 76.7212 | 0.050354 | 0.41199 | 123.0057 | 123.2712 | 123.1064 | 68.4357 | 68.2205 | 123.111 | 123.1018 | 76.7212 | 68.4357 | 68.2205 | 123.1018 | 123.1064 | 123.111 | -55.2521 | -46.3394
4950.7812 | 123.3307 | -68.2709 | 54.8538 | 0.24773 | -0.0084296 | -0.028647 | 0.0092562 | -0.0078271 | -0.0050095 | -0.0022302 | -0.022888 | 0.20142 | -0.4303 | 55.0781 | 54.8309 | 54.8264 | 54.808 | 55.0049 | 54.9362 | 8.4869 | 67.8406 | -54.6524 | 68.248 | 123.349 | -0.022888 | 76.7578 | 0.082397 | 0.40741 | 123.0789 | 123.2758 | 123.1018 | 68.4723 | 68.248 | 123.2071 | 123.0972 | 76.7578 | 68.4723 | 68.248 | 123.0972 | 123.1018 | 123.2071 | -55.2841 | -46.3669
4951.7656 | 123.3856 | -68.2251 | 54.863 | -0.56099 | -0.0094976 | -0.024588 | 0.0045566 | -0.0086817 | -0.0073593 | -0.0037256 | 0.11902 | 0.11902 | -0.44403 | 55.1147 | 54.9179 | 54.8996 | 54.7165 | 55.0552 | 54.8904 | 8.4915 | 67.7811 | -54.744 | 68.3441 | 123.3398 | 0.054932 | 76.7166 | 0.027466 | 0.56305 | 122.9416 | 123.2803 | 123.143 | 68.3441 | 68.3441 | 123.1155 | 123.1247 | 76.7166 | 68.3441 | 68.3441 | 123.1247 | 123.143 | 123.1155 | -55.307 | -46.3715
4952.7812 | 123.5687 | -68.1702 | 54.895 | -0.11085 | -0.015693 | -0.027792 | -0.00035676 | -0.010391 | -0.0043685 | -0.0026574 | 0.050354 | 0.20142 | -0.33417 | 55.1651 | 54.9591 | 54.9545 | 54.7897 | 55.1697 | 54.9271 | 8.5007 | 67.836 | -54.6936 | 68.2205 | 123.3353 | 0.064086 | 76.6708 | 0.032043 | 0.38452 | 122.9599 | 123.3398 | 123.1293 | 68.3716 | 68.2205 | 123.0972 | 123.1247 | 76.6708 | 68.3716 | 68.2205 | 123.1247 | 123.1293 | 123.0972 | -55.2292 | -46.3943
4953.7656 | 123.4314 | -68.2205 | 54.7989 | 0.4232 | -0.010352 | -0.023734 | 0.0058382 | -0.010604 | -0.0052231 | -0.0030848 | -0.027466 | 0.17853 | -0.40283 | 55.1056 | 54.8859 | 54.8904 | 54.7394 | 55.0461 | 54.8904 | 8.4915 | 67.8177 | -54.6204 | 68.1931 | 123.3261 | 0.086975 | 76.712 | 0.091553 | 0.37537 | 122.9599 | 123.2666 | 123.1064 | 68.399 | 68.1931 | 123.111 | 123.111 | 76.712 | 68.399 | 68.1931 | 123.111 | 123.1064 | 123.111 | -55.2017 | -46.3074
4954.7812 | 123.2803 | -68.2755 | 54.8721 | -0.04982 | -0.0069342 | -0.023093 | 0.010111 | -0.0093225 | -0.0082137 | -0.00052119 | -0.009155 | 0.22888 | -0.41199 | 55.0323 | 54.8035 | 54.776 | 54.8996 | 54.9545 | 54.9545 | 8.4915 | 67.8635 | -54.6432 | 68.2663 | 123.3078 | -0.068664 | 76.767 | 0.082398 | 0.40283 | 123.175 | 123.23 | 123.0789 | 68.5043 | 68.2663 | 123.23 | 123.0515 | 76.767 | 68.5043 | 68.2663 | 123.0515 | 123.0789 | 123.23 | -55.2841 | -46.3806
4955.7812 | 123.3765 | -68.2114 | 54.8309 | 0.27061 | -0.0088568 | -0.020529 | 0.00712 | -0.0059045 | -0.0056503 | -0.0039392 | -0.004578 | 0.16937 | -0.40741 | 55.1056 | 54.9271 | 54.8767 | 54.6753 | 55.0552 | 54.8996 | 8.4961 | 67.804 | -54.6616 | 68.2068 | 123.317 | 0.09613 | 76.7075 | 0.068664 | 0.40283 | 122.8867 | 123.2666 | 123.1384 | 68.3807 | 68.2068 | 123.111 | 123.0881 | 76.7075 | 68.3807 | 68.2068 | 123.0881 | 123.1384 | 123.111 | -55.2383 | -46.3348
4956.7812 | 123.2803 | -68.2617 | 54.8676 | 0.19432 | -0.0069342 | -0.018393 | 0.0081882 | -0.0082545 | -0.0060775 | -0.00073479 | -0.022888 | 0.24261 | -0.41199 | 55.0323 | 54.808 | 54.7897 | 54.8721 | 54.9362 | 54.9591 | 8.4915 | 67.8497 | -54.6249 | 68.2388 | 123.2941 | -0.05951 | 76.7532 | 0.091552 | 0.3891 | 123.1338 | 123.1979 | 123.0698 | 68.5043 | 68.2388 | 123.2208 | 123.0515 | 76.7532 | 68.5043 | 68.2388 | 123.0515 | 123.0698 | 123.2208 | -55.2795 | -46.376
4957.7812 | 123.4085 | -68.1793 | 54.8813 | 0.011215 | -0.012061 | -0.025229 | -0.00014316 | -0.0093225 | -0.0058639 | -0.0028712 | 0.013733 | 0.23346 | -0.35248 | 55.1331 | 54.9362 | 54.9454 | 54.7852 | 55.1193 | 54.9454 | 8.4961 | 67.8268 | -54.6478 | 68.1931 | 123.3124 | 0.054931 | 76.6754 | 0.064087 | 0.36621 | 122.9645 | 123.2986 | 123.1155 | 68.4128 | 68.1931 | 123.1247 | 123.1247 | 76.6754 | 68.4128 | 68.1931 | 123.1247 | 123.1155 | 123.1247 | -55.2338 | -46.3852
4958.7656 | 123.3398 | -68.248 | 54.8584 | 0.28587 | -0.0088568 | -0.023947 | 0.0075472 | -0.0093225 | -0.0052231 | -0.0028712 | -0.018311 | 0.22888 | -0.41199 | 55.0735 | 54.8401 | 54.8355 | 54.7943 | 54.9911 | 54.9133 | 8.4915 | 67.836 | -54.6295 | 68.2297 | 123.3215 | -0.01831 | 76.7395 | 0.054932 | 0.39368 | 123.0423 | 123.2391 | 123.0881 | 68.4769 | 68.2297 | 123.1613 | 123.0835 | 76.7395 | 68.4769 | 68.2297 | 123.0835 | 123.0881 | 123.1613 | -55.2704 | -46.3669
4959.7656 | 123.3215 | -68.2526 | 54.8538 | 0.26299 | -0.0073614 | -0.025656 | 0.0084018 | -0.0073999 | -0.0077865 | -0.003512 | -0.018311 | 0.21973 | -0.40741 | 55.0461 | 54.8309 | 54.8035 | 54.8309 | 54.9637 | 54.9454 | 8.4915 | 67.8452 | -54.6341 | 68.2343 | 123.2986 | -0.022888 | 76.7441 | 0.091553 | 0.3891 | 123.0835 | 123.2162 | 123.0835 | 68.4723 | 68.2343 | 123.1979 | 123.056 | 76.7441 | 68.4723 | 68.2343 | 123.056 | 123.0835 | 123.1979 | -55.2612 | -46.3623
4960.7656 | 123.2803 | -68.248 | 54.863 | 0.21721 | -0.0060798 | -0.02117 | 0.0090426 | -0.0056909 | -0.0043685 | 0.00011961 | -0.045776 | 0.23346 | -0.40283 | 55.0323 | 54.808 | 54.7989 | 54.8676 | 54.9408 | 54.9591 | 8.4915 | 67.8452 | -54.6295 | 68.2022 | 123.2803 | -0.054932 | 76.7395 | 0.09613 | 0.35706 | 123.1155 | 123.1888 | 123.056 | 68.4814 | 68.2022 | 123.2071 | 123.0469 | 76.7395 | 68.4814 | 68.2022 | 123.0469 | 123.056 | 123.2071 | -55.2658 | -46.3715
4961.7812 | 123.2803 | -68.2571 | 54.9042 | 0.10277 | -0.0084296 | -0.023306 | 0.0062656 | -0.0069727 | -0.0060775 | -0.0022302 | 0.022888 | 0.25635 | -0.37537 | 55.0552 | 54.8218 | 54.808 | 54.9088 | 54.9728 | 54.9683 | 8.4824 | 67.8818 | -54.6478 | 68.28 | 123.3124 | -0.082398 | 76.7395 | 0.064087 | 0.39825 | 123.1659 | 123.23 | 123.0789 | 68.5135 | 68.28 | 123.2254 | 123.0652 | 76.7395 | 68.5135 | 68.28 | 123.0652 | 123.0789 | 123.2254 | -55.2795 | -46.4218
4962.7812 | 123.3902 | -68.2159 | 54.8492 | 0.27824 | -0.009925 | -0.026297 | 0.002634 | -0.0063317 | -0.0069321 | -0.0030848 | 0 | 0.16937 | -0.3891 | 55.0919 | 54.8904 | 54.9042 | 54.7302 | 55.0644 | 54.9225 | 8.4961 | 67.8268 | -54.6799 | 68.2159 | 123.3078 | 0.041199 | 76.712 | 0.073242 | 0.3891 | 122.9462 | 123.2803 | 123.1064 | 68.3853 | 68.2159 | 123.1384 | 123.1201 | 76.712 | 68.3853 | 68.2159 | 123.1201 | 123.1064 | 123.1384 | -55.2383 | -46.3531
4963.7812 | 123.2712 | -68.2251 | 54.895 | 0.087509 | -0.0069342 | -0.025229 | 0.010752 | -0.0082545 | -0.0075729 | -0.0020166 | 0.022888 | 0.26093 | -0.3891 | 55.0278 | 54.8126 | 54.808 | 54.9042 | 54.9728 | 54.9637 | 8.4869 | 67.836 | -54.6341 | 68.248 | 123.2529 | -0.082398 | 76.712 | 0.068664 | 0.41199 | 123.1293 | 123.1979 | 123.0377 | 68.486 | 68.248 | 123.1888 | 123.0331 | 76.712 | 68.486 | 68.248 | 123.0331 | 123.0377 | 123.1888 | -55.2841 | -46.4081
4964.7812 | 123.2849 | -68.2388 | 54.8767 | 0.056992 | -0.010566 | -0.024161 | 0.0092562 | -0.0076135 | -0.0060775 | -0.0013758 | 0.027466 | 0.26093 | -0.37079 | 55.0644 | 54.8309 | 54.8126 | 54.9088 | 54.9911 | 54.9957 | 8.4869 | 67.868 | -54.6158 | 68.2663 | 123.3032 | -0.045776 | 76.7258 | 0.11902 | 0.39825 | 123.1476 | 123.23 | 123.0698 | 68.4998 | 68.2663 | 123.2346 | 123.0515 | 76.7258 | 68.4998 | 68.2663 | 123.0515 | 123.0698 | 123.2346 | -55.2475 | -46.3898
4965.7656 | 123.2437 | -68.2663 | 54.8676 | 0.072251 | -0.0088568 | -0.022879 | 0.0077608 | -0.0046229 | -0.0054367 | -0.0030848 | -0.032043 | 0.25177 | -0.39368 | 55.014 | 54.8035 | 54.7989 | 54.9088 | 54.9316 | 54.9957 | 8.4869 | 67.8726 | -54.6158 | 68.2343 | 123.2803 | -0.064087 | 76.7532 | 0.12817 | 0.36163 | 123.175 | 123.1979 | 123.0698 | 68.5181 | 68.2343 | 123.262 | 123.0652 | 76.7532 | 68.5181 | 68.2343 | 123.0652 | 123.0698 | 123.262 | -55.2612 | -46.3806
4966.7656 | 123.2758 | -68.2617 | 54.895 | 0.034104 | -0.007575 | -0.021811 | 0.0096834 | -0.0073999 | -0.0077865 | -0.0013758 | -0.009155 | 0.24261 | -0.38452 | 55.0186 | 54.7989 | 54.8035 | 54.9042 | 54.95 | 54.9774 | 8.4824 | 67.8772 | -54.6524 | 68.2526 | 123.2803 | -0.096131 | 76.7441 | 0.082397 | 0.37537 | 123.1659 | 123.2117 | 123.0606 | 68.5043 | 68.2526 | 123.2391 | 123.0652 | 76.7441 | 68.5043 | 68.2526 | 123.0652 | 123.0606 | 123.2391 | -55.2795 | -46.4127
4967.7656 | 123.2895 | -68.2526 | 54.8813 | 0.011215 | -0.010352 | -0.026297 | 0.0066928 | -0.0037683 | -0.0067185 | -0.0028712 | 0.009155 | 0.2655 | -0.37537 | 55.0369 | 54.8309 | 54.8264 | 54.9179 | 54.9774 | 54.9728 | 8.4869 | 67.8772 | -54.6158 | 68.2617 | 123.2895 | -0.050354 | 76.7395 | 0.091552 | 0.38452 | 123.1705 | 123.23 | 123.0835 | 68.5181 | 68.2617 | 123.2254 | 123.0789 | 76.7395 | 68.5181 | 68.2617 | 123.0789 | 123.0835 | 123.2254 | -55.2567 | -46.3943
4968.7812 | 123.3124 | -68.2388 | 54.895 | -0.13374 | -0.0094976 | -0.02822 | 0.003702 | -0.0073999 | -0.0058639 | 0.00011961 | 0.036621 | 0.31128 | -0.35248 | 55.069 | 54.8721 | 54.8538 | 54.9454 | 55.0461 | 54.982 | 8.4869 | 67.8864 | -54.5837 | 68.2755 | 123.3078 | -0.022889 | 76.7258 | 0.086975 | 0.3891 | 123.1842 | 123.2849 | 123.111 | 68.5501 | 68.2755 | 123.2208 | 123.0927 | 76.7258 | 68.5501 | 68.2755 | 123.0927 | 123.111 | 123.2208 | -55.2475 | -46.4081
4969.7812 | 123.111 | -68.3166 | 54.8447 | 0.15617 | -0.007575 | -0.022238 | 0.0066928 | -0.0082545 | -0.0045821 | -0.00073479 | -0.086975 | 0.23804 | -0.3891 | 54.9911 | 54.7897 | 54.7852 | 54.9316 | 54.9316 | 54.9728 | 8.4869 | 67.9276 | -54.6066 | 68.2297 | 123.3078 | -0.054932 | 76.8036 | 0.12817 | 0.30212 | 123.2483 | 123.2483 | 123.1064 | 68.5547 | 68.2297 | 123.2895 | 123.1018 | 76.8036 | 68.5547 | 68.2297 | 123.1018 | 123.1064 | 123.2895 | -55.2338 | -46.3577
4970.7812 | 123.317 | -68.248 | 54.9088 | -0.12611 | -0.010566 | -0.023947 | 0.0045566 | -0.0071863 | -0.0092819 | -0.0024438 | 0.050354 | 0.31128 | -0.32501 | 55.0781 | 54.8676 | 54.8447 | 54.9316 | 55.0552 | 55.0095 | 8.4961 | 67.923 | -54.5975 | 68.2983 | 123.3261 | -0.041198 | 76.7441 | 0.10071 | 0.37537 | 123.1796 | 123.3032 | 123.1155 | 68.5593 | 68.2983 | 123.2574 | 123.0927 | 76.7441 | 68.5593 | 68.2983 | 123.0927 | 123.1155 | 123.2574 | -55.2338 | -46.4127
4971.7812 | 123.2986 | -68.2434 | 54.8996 | -0.16426 | -0.0097114 | -0.023734 | 0.0051974 | -0.0073999 | -0.0058639 | -0.003512 | 0.022888 | 0.31586 | -0.32959 | 55.0507 | 54.8492 | 54.8355 | 54.9683 | 55.0323 | 55.0232 | 8.4824 | 67.9138 | -54.5837 | 68.2663 | 123.2941 | -0.050354 | 76.7258 | 0.1236 | 0.35248 | 123.2117 | 123.2758 | 123.0927 | 68.5593 | 68.2663 | 123.2666 | 123.0789 | 76.7258 | 68.5593 | 68.2663 | 123.0789 | 123.0927 | 123.2666 | -55.2292 | -46.4172
4972.7812 | 123.3032 | -68.2434 | 54.9088 | -0.15663 | -0.011634 | -0.019675 | 0.0047702 | -0.0067591 | -0.0073593 | -0.0037256 | 0.027466 | 0.3067 | -0.33875 | 55.0644 | 54.863 | 54.8492 | 54.9454 | 55.0369 | 54.9957 | 8.4869 | 67.9047 | -54.602 | 68.2709 | 123.3078 | -0.045776 | 76.7303 | 0.086976 | 0.36621 | 123.1888 | 123.2803 | 123.1064 | 68.5501 | 68.2709 | 123.2391 | 123.0927 | 76.7303 | 68.5501 | 68.2709 | 123.0927 | 123.1064 | 123.2391 | -55.2475 | -46.4218
4973.7656 | 123.3078 | -68.2388 | 54.895 | -0.18715 | -0.010993 | -0.023734 | 0.0047702 | -0.0067591 | -0.0069321 | -0.0013758 | 0.041199 | 0.28839 | -0.33875 | 55.069 | 54.8584 | 54.8447 | 54.9362 | 55.0461 | 55.0095 | 8.4961 | 67.9001 | -54.6066 | 68.28 | 123.3078 | -0.036622 | 76.7349 | 0.11444 | 0.37994 | 123.175 | 123.2849 | 123.0972 | 68.5272 | 68.28 | 123.2483 | 123.0835 | 76.7349 | 68.5272 | 68.28 | 123.0835 | 123.0972 | 123.2483 | -55.2338 | -46.3989
4974.7656 | 123.3398 | -68.2114 | 54.8904 | -0.17952 | -0.013557 | -0.026724 | -0.00099756 | -0.0082545 | -0.0077865 | 0.00033321 | 0.059509 | 0.2243 | -0.31586 | 55.101 | 54.9179 | 54.8904 | 54.895 | 55.1102 | 54.9866 | 8.5007 | 67.8955 | -54.6661 | 68.2709 | 123.3124 | 0.027466 | 76.712 | 0.09613 | 0.37537 | 123.1064 | 123.3215 | 123.1293 | 68.4357 | 68.2709 | 123.1979 | 123.1018 | 76.712 | 68.4357 | 68.2709 | 123.1018 | 123.1293 | 123.1979 | -55.2063 | -46.3898
4975.7812 | 123.3994 | -68.2022 | 54.863 | -0.026932 | -0.013557 | -0.028647 | -0.0037748 | -0.010818 | -0.0060775 | -0.00073479 | 0.022888 | 0.21057 | -0.34332 | 55.0964 | 54.9316 | 54.9454 | 54.7897 | 55.1422 | 54.9545 | 8.4824 | 67.8589 | -54.6524 | 68.2251 | 123.2986 | 0.068665 | 76.6846 | 0.091553 | 0.36621 | 122.9919 | 123.3444 | 123.1338 | 68.4128 | 68.2251 | 123.1567 | 123.1476 | 76.6846 | 68.4128 | 68.2251 | 123.1476 | 123.1338 | 123.1567 | -55.2063 | -46.3806
4976.7812 | 123.2895 | -68.2343 | 54.9271 | -0.31685 | -0.010352 | -0.02587 | -0.00014316 | -0.0099633 | -0.0045821 | -0.0026574 | 0.027466 | 0.28839 | -0.33875 | 55.0552 | 54.8264 | 54.8264 | 54.982 | 55.0232 | 55.0186 | 8.4824 | 67.8955 | -54.6387 | 68.2617 | 123.2895 | -0.10071 | 76.7166 | 0.091553 | 0.36621 | 123.2162 | 123.2574 | 123.0606 | 68.5226 | 68.2617 | 123.2529 | 123.0606 | 76.7166 | 68.5226 | 68.2617 | 123.0606 | 123.0606 | 123.2529 | -55.2658 | -46.4447
4977.7812 | 123.2986 | -68.2297 | 54.9179 | -0.19478 | -0.01142 | -0.023306 | 0.0039156 | -0.011672 | -0.0067185 | -0.0013758 | 0.054932 | 0.25635 | -0.32501 | 55.0873 | 54.8676 | 54.863 | 54.9362 | 55.069 | 55.0095 | 8.4915 | 67.9047 | -54.6616 | 68.2846 | 123.317 | -0.050354 | 76.7212 | 0.091552 | 0.37994 | 123.1659 | 123.2986 | 123.0972 | 68.486 | 68.2846 | 123.2391 | 123.0927 | 76.7212 | 68.486 | 68.2846 | 123.0927 | 123.0972 | 123.2391 | -55.2429 | -46.4264
4978.7812 | 123.3582 | -68.2251 | 54.8721 | -0.19478 | -0.011848 | -0.027152 | 0.002634 | -0.0121 | -0.0088547 | -0.0028712 | 0.082397 | 0.24261 | -0.31128 | 55.1147 | 54.9179 | 54.8996 | 54.8859 | 55.1102 | 54.9774 | 8.4915 | 67.9138 | -54.6295 | 68.3075 | 123.3398 | 0.045777 | 76.7166 | 0.10529 | 0.39368 | 123.111 | 123.3353 | 123.143 | 68.4677 | 68.3075 | 123.2025 | 123.1247 | 76.7166 | 68.4677 | 68.3075 | 123.1247 | 123.143 | 123.2025 | -55.1834 | -46.3806
4979.7656 | 123.1979 | -68.2343 | 54.9637 | -0.04219 | -0.012702 | -0.027152 | 0.0058382 | -0.0097497 | -0.0073593 | -0.0028712 | 0.027466 | 0.29297 | -0.32959 | 55.0552 | 54.8355 | 54.8218 | 54.9866 | 55.0369 | 55.014 | 8.4915 | 67.9047 | -54.6707 | 68.2617 | 123.2895 | -0.12817 | 76.7258 | 0.050354 | 0.35706 | 123.2208 | 123.2712 | 123.0698 | 68.5272 | 68.2617 | 123.2483 | 123.056 | 76.7258 | 68.5272 | 68.2617 | 123.056 | 123.0698 | 123.2483 | -55.2933 | -46.4722
4980.7656 | 123.3215 | -68.2388 | 54.9179 | -0.18715 | -0.013343 | -0.029715 | 0.001993 | -0.0095361 | -0.0097091 | -0.0020166 | 0.064087 | 0.24261 | -0.33417 | 55.0873 | 54.8676 | 54.8355 | 54.9088 | 55.0507 | 55.0049 | 8.5007 | 67.9047 | -54.6753 | 68.3029 | 123.3261 | -0.050354 | 76.7395 | 0.086975 | 0.39825 | 123.1476 | 123.2895 | 123.1064 | 68.4814 | 68.3029 | 123.2437 | 123.0743 | 76.7395 | 68.4814 | 68.3029 | 123.0743 | 123.1064 | 123.2437 | -55.2521 | -46.4172
4981.7656 | 123.4039 | -68.1976 | 54.8721 | -0.019302 | -0.012061 | -0.029074 | -0.00014316 | -0.011459 | -0.0062911 | -0.0037256 | 0.022888 | 0.21515 | -0.34332 | 55.1102 | 54.9042 | 54.9042 | 54.8035 | 55.101 | 54.9454 | 8.4915 | 67.8543 | -54.657 | 68.2205 | 123.3078 | 0.032044 | 76.6891 | 0.073243 | 0.36621 | 123.0011 | 123.2986 | 123.1018 | 68.4128 | 68.2205 | 123.143 | 123.1018 | 76.6891 | 68.4128 | 68.2205 | 123.1018 | 123.1018 | 123.143 | -55.2155 | -46.3806
4982.7969 | 123.3994 | -68.2159 | 54.8676 | -0.14137 | -0.013557 | -0.029715 | 0.0013522 | -0.012527 | -0.0037277 | -0.0043664 | 0.050354 | 0.19226 | -0.33417 | 55.1514 | 54.9408 | 54.9271 | 54.7943 | 55.1468 | 54.9179 | 8.4869 | 67.8818 | -54.6753 | 68.2663 | 123.3673 | 0.073242 | 76.7029 | 0.050354 | 0.38452 | 123.0103 | 123.3627 | 123.1567 | 68.4082 | 68.2663 | 123.1338 | 123.143 | 76.7029 | 68.4082 | 68.2663 | 123.143 | 123.1567 | 123.1338 | -55.2017 | -46.3806
4983.7812 | 123.4131 | -68.1931 | 54.895 | -0.087967 | -0.01377 | -0.023306 | 0.001993 | -0.010391 | -0.0082137 | -0.0032984 | 0.082397 | 0.19226 | -0.3067 | 55.1651 | 54.9454 | 54.9225 | 54.7897 | 55.1514 | 54.9637 | 8.5007 | 67.8864 | -54.7028 | 68.2755 | 123.3582 | 0.050354 | 76.6937 | 0.068664 | 0.3891 | 122.9828 | 123.3444 | 123.1384 | 68.3853 | 68.2755 | 123.1567 | 123.1155 | 76.6937 | 68.3853 | 68.2755 | 123.1155 | 123.1384 | 123.1567 | -55.2017 | -46.3943
4984.7812 | 123.4085 | -68.1885 | 54.8721 | -0.04982 | -0.012916 | -0.023306 | 0.0024202 | -0.013168 | -0.0052231 | -0.0028712 | 0.045776 | 0.2243 | -0.32959 | 55.1605 | 54.9179 | 54.9133 | 54.7806 | 55.1331 | 54.9316 | 8.5007 | 67.8589 | -54.6478 | 68.2343 | 123.349 | 0.045777 | 76.6891 | 0.05951 | 0.37537 | 122.9691 | 123.3215 | 123.1064 | 68.4128 | 68.2343 | 123.1201 | 123.1018 | 76.6891 | 68.4128 | 68.2343 | 123.1018 | 123.1064 | 123.1201 | -55.2017 | -46.3715
4985.7812 | 123.3765 | -68.1931 | 54.8676 | 0.0035856 | -0.012275 | -0.029074 | 0.0022066 | -0.014022 | -0.0054367 | -0.0037256 | 0.027466 | 0.20142 | -0.32044 | 55.1331 | 54.9179 | 54.895 | 54.7806 | 55.0964 | 54.9362 | 8.4869 | 67.8726 | -54.6661 | 68.2205 | 123.3261 | 0.050354 | 76.68 | 0.068664 | 0.3479 | 122.9736 | 123.2895 | 123.111 | 68.3945 | 68.2205 | 123.1293 | 123.0881 | 76.68 | 68.3945 | 68.2205 | 123.0881 | 123.111 | 123.1293 | -55.188 | -46.3806
4986.7656 | 123.4131 | -68.1976 | 54.8584 | -0.087967 | -0.013984 | -0.029288 | 0.0011386 | -0.013595 | -0.0065047 | -0.0041528 | 0.07782 | 0.21973 | -0.32501 | 55.1743 | 54.95 | 54.8538 | 55.3207 | 55.2475 | 55.0003 | 8.4915 | 67.8726 | -54.6387 | 68.2755 | 123.3719 | 0.091553 | 76.6891 | 0.14191 | 0.40283 | 123.5184 | 123.4451 | 123.1476 | 68.4174 | 68.2755 | 123.1979 | 123.0515 | 76.6891 | 68.4174 | 68.2755 | 123.0515 | 123.1476 | 123.1979 | -55.1834 | -46.3669
4987.7656 | 123.4085 | -68.1656 | 54.8721 | -0.026932 | -0.012702 | -0.02352 | 0.0011386 | -0.013168 | -0.0062911 | -0.0030848 | 0.050354 | 0.21515 | -0.33417 | 55.1788 | 54.9545 | 54.9225 | 54.7714 | 55.1376 | 54.9088 | 8.4915 | 67.8314 | -54.657 | 68.2159 | 123.3444 | 0.082398 | 76.6571 | 0.036621 | 0.38452 | 122.937 | 123.3032 | 123.1201 | 68.3807 | 68.2159 | 123.0743 | 123.0881 | 76.6571 | 68.3807 | 68.2159 | 123.0881 | 123.1201 | 123.0743 | -55.2063 | -46.3806
4988.7656 | 123.3582 | -68.1976 | 54.8538 | 0.21721 | -0.013343 | -0.027792 | 0.00092504 | -0.012954 | -0.0037277 | -0.0020166 | -0.032043 | 0.15106 | -0.39368 | 55.0964 | 54.8584 | 54.8584 | 54.7623 | 55.0323 | 54.9088 | 8.4824 | 67.804 | -54.7028 | 68.1656 | 123.2941 | 0.004577 | 76.68 | 0.054931 | 0.36163 | 122.9599 | 123.23 | 123.056 | 68.3487 | 68.1656 | 123.1064 | 123.056 | 76.68 | 68.3487 | 68.1656 | 123.056 | 123.056 | 123.1064 | -55.2475 | -46.3715
4989.7812 | 123.3398 | -68.2022 | 54.8676 | 0.21721 | -0.01142 | -0.025015 | 0.0015658 | -0.0121 | -0.0067185 | -0.0047938 | -0.027466 | 0.16022 | -0.37537 | 55.0919 | 54.8721 | 54.8355 | 54.7714 | 55.0369 | 54.9088 | 8.4961 | 67.8268 | -54.7073 | 68.1747 | 123.2941 | 0.004577 | 76.6983 | 0.041198 | 0.3479 | 122.9736 | 123.2391 | 123.0743 | 68.3624 | 68.1747 | 123.111 | 123.0377 | 76.6983 | 68.3624 | 68.1747 | 123.0377 | 123.0743 | 123.111 | -55.2429 | -46.3715
4990.7812 | 123.3398 | -68.2388 | 54.8767 | 0.1104 | -0.014411 | -0.028433 | 0.0013522 | -0.011672 | -0.0043685 | -0.00094839 | 0.091553 | 0.18768 | -0.3479 | 55.1056 | 54.8813 | 54.8401 | 54.808 | 55.0507 | 54.9362 | 8.4915 | 67.8909 | -54.689 | 68.3304 | 123.3444 | 0.004578 | 76.7303 | 0.059509 | 0.43945 | 123.0469 | 123.2895 | 123.1201 | 68.4265 | 68.3304 | 123.175 | 123.0789 | 76.7303 | 68.4265 | 68.3304 | 123.0789 | 123.1201 | 123.175 | -55.2246 | -46.3852
4991.7812 | 123.4268 | -68.2205 | 54.8676 | 0.1104 | -0.010993 | -0.022238 | 0.0015658 | -0.012527 | -0.0037277 | -0.0037256 | -0.027466 | 0.17853 | -0.37537 | 55.0827 | 54.8676 | 54.8538 | 54.7897 | 55.0278 | 54.9133 | 8.4915 | 67.8452 | -54.689 | 68.1931 | 123.3032 | 0 | 76.712 | 0.045776 | 0.3479 | 123.0103 | 123.2483 | 123.0881 | 68.399 | 68.1931 | 123.1338 | 123.0743 | 76.712 | 68.399 | 68.1931 | 123.0743 | 123.0881 | 123.1338 | -55.2429 | -46.376
4992.7656 | 123.3673 | -68.2068 | 54.8584 | -0.011673 | -0.010993 | -0.022452 | 0.0015658 | -0.012313 | -0.0058639 | -0.0043664 | -0.009155 | 0.20599 | -0.3479 | 55.1147 | 54.8904 | 54.8996 | 54.7714 | 55.0873 | 54.9545 | 8.4915 | 67.8589 | -54.6524 | 68.1976 | 123.3215 | 0.032044 | 76.6983 | 0.096131 | 0.33874 | 122.9782 | 123.2941 | 123.0972 | 68.4128 | 68.1976 | 123.1613 | 123.1064 | 76.6983 | 68.4128 | 68.1976 | 123.1064 | 123.0972 | 123.1613 | -55.2063 | -46.3669
4993.7656 | 123.3627 | -68.1931 | 54.8767 | 0.064621 | -0.012916 | -0.025229 | 0.0017794 | -0.010604 | -0.0050095 | -0.0013758 | 0 | 0.20599 | -0.32044 | 55.1239 | 54.8721 | 54.8584 | 54.7897 | 55.069 | 54.9088 | 8.4915 | 67.8726 | -54.6707 | 68.1931 | 123.317 | -0.004578 | 76.6846 | 0.032043 | 0.32044 | 122.9828 | 123.262 | 123.0652 | 68.399 | 68.1931 | 123.1018 | 123.0515 | 76.6846 | 68.399 | 68.1931 | 123.0515 | 123.0652 | 123.1018 | -55.1971 | -46.3852
4994.7656 | 123.349 | -68.2343 | 54.8492 | 0.13329 | -0.01142 | -0.025656 | 0.0030612 | -0.011459 | -0.0065047 | -0.0032984 | 0.045776 | 0.17395 | -0.33875 | 55.0919 | 54.9133 | 54.8584 | 54.7943 | 55.0415 | 54.9271 | 8.4961 | 67.8955 | -54.6753 | 68.28 | 123.3261 | 0.064087 | 76.7303 | 0.07782 | 0.38452 | 123.0286 | 123.2758 | 123.1476 | 68.4082 | 68.28 | 123.1613 | 123.0927 | 76.7303 | 68.4082 | 68.28 | 123.0927 | 123.1476 | 123.1613 | -55.188 | -46.3531
4995.7812 | 123.3994 | -68.2022 | 54.8355 | 0.2401 | -0.010993 | -0.020529 | 0.0041292 | -0.012313 | -0.0047957 | -0.0030848 | -0.009155 | 0.13275 | -0.37079 | 55.1331 | 54.895 | 54.8904 | 54.7119 | 55.0507 | 54.8859 | 8.4915 | 67.8314 | -54.7028 | 68.1931 | 123.3353 | 0.05951 | 76.6937 | 0.050354 | 0.36163 | 122.9141 | 123.2529 | 123.0972 | 68.335 | 68.1931 | 123.0881 | 123.0927 | 76.6937 | 68.335 | 68.1931 | 123.0927 | 123.0972 | 123.0881 | -55.2063 | -46.344
4996.7812 | 123.3765 | -68.1885 | 54.8904 | -0.149 | -0.013343 | -0.027152 | 0.0011386 | -0.010391 | -0.0062911 | -0.0037256 | 0.073242 | 0.21973 | -0.29297 | 55.1468 | 54.9454 | 54.9088 | 54.8538 | 55.1285 | 54.9271 | 8.4824 | 67.8955 | -54.6707 | 68.2617 | 123.3353 | 0.054932 | 76.6708 | 0.036621 | 0.36621 | 123.0423 | 123.317 | 123.1339 | 68.4082 | 68.2617 | 123.1155 | 123.0972 | 76.6708 | 68.4082 | 68.2617 | 123.0972 | 123.1339 | 123.1155 | -55.1834 | -46.4081
4997.7812 | 123.3627 | -68.2205 | 54.8492 | 0.17143 | -0.011207 | -0.028433 | 0.002634 | -0.011672 | -0.0073593 | -0.0032984 | -0.004578 | 0.16022 | -0.37994 | 55.1147 | 54.8859 | 54.895 | 54.7302 | 55.0552 | 54.863 | 8.4915 | 67.8406 | -54.689 | 68.2159 | 123.3353 | 0.036621 | 76.712 | 0.013733 | 0.37537 | 122.9507 | 123.2758 | 123.1064 | 68.3807 | 68.2159 | 123.0835 | 123.1155 | 76.712 | 68.3807 | 68.2159 | 123.1155 | 123.1064 | 123.0835 | -55.2292 | -46.3577
4998.7812 | 123.3719 | -68.2114 | 54.8447 | 0.18669 | -0.0094976 | -0.025229 | 0.0028476 | -0.011245 | -0.0067185 | -0.003512 | 0.018311 | 0.15106 | -0.37537 | 55.1376 | 54.8996 | 54.895 | 54.7211 | 55.0735 | 54.8767 | 8.4961 | 67.836 | -54.6936 | 68.2297 | 123.349 | 0.054931 | 76.7075 | 0.032043 | 0.39368 | 122.9324 | 123.2849 | 123.111 | 68.3624 | 68.2297 | 123.0881 | 123.1064 | 76.7075 | 68.3624 | 68.2297 | 123.1064 | 123.111 | 123.0881 | -55.22 | -46.3486
4999.7656 | 123.349 | -68.2205 | 54.863 | 0.15617 | -0.011634 | -0.028861 | 0.0017794 | -0.011245 | -0.0052231 | -0.0024438 | -0.032043 | 0.15564 | -0.37994 | 55.0827 | 54.8676 | 54.863 | 54.7943 | 55.0507 | 54.9042 | 8.4869 | 67.8406 | -54.7073 | 68.1885 | 123.3032 | 0.004578 | 76.7075 | 0.041199 | 0.3479 | 123.0148 | 123.2712 | 123.0881 | 68.3762 | 68.1885 | 123.1247 | 123.0835 | 76.7075 | 68.3762 | 68.1885 | 123.0835 | 123.0881 | 123.1247 | -55.2429 | -46.376
5000.7656 | 123.3673 | -68.2434 | 54.8492 | 0.20195 | -0.010139 | -0.024588 | 0.0028476 | -0.012313 | -0.0039413 | -0.0039392 | -0.009155 | 0.14191 | -0.41657 | 55.101 | 54.8676 | 54.863 | 54.7714 | 55.0461 | 54.9133 | 8.4915 | 67.8268 | -54.7073 | 68.2343 | 123.3444 | 0.018311 | 76.7349 | 0.064087 | 0.40741 | 123.0148 | 123.2895 | 123.111 | 68.3853 | 68.2343 | 123.1567 | 123.1064 | 76.7349 | 68.3853 | 68.2343 | 123.1064 | 123.111 | 123.1567 | -55.2658 | -46.3577
5001.7656 | 123.3765 | -68.2205 | 54.8401 | 0.23247 | -0.010993 | -0.022238 | 0.002634 | -0.011886 | -0.0073593 | -0.0022302 | -0.018311 | 0.14648 | -0.41199 | 55.1147 | 54.8904 | 54.8859 | 54.7302 | 55.0552 | 54.8859 | 8.4961 | 67.8085 | -54.6936 | 68.2022 | 123.3353 | 0.050354 | 76.7166 | 0.045776 | 0.39368 | 122.9507 | 123.2758 | 123.111 | 68.367 | 68.2022 | 123.1064 | 123.1064 | 76.7166 | 68.367 | 68.2022 | 123.1064 | 123.111 | 123.1064 | -55.2521 | -46.344
5002.7812 | 123.3948 | -68.2297 | 54.8492 | 0.30113 | -0.010566 | -0.018607 | 0.0077608 | -0.0095361 | -0.0056503 | -0.0026574 | 0.004578 | 0.16479 | -0.40283 | 55.1147 | 54.8904 | 54.8904 | 54.7348 | 55.0323 | 54.9088 | 8.4869 | 67.8268 | -54.6844 | 68.2343 | 123.3444 | 0.041199 | 76.7166 | 0.059509 | 0.40741 | 122.9645 | 123.262 | 123.1201 | 68.3945 | 68.2343 | 123.1384 | 123.1201 | 76.7166 | 68.3945 | 68.2343 | 123.1201 | 123.1201 | 123.1384 | -55.2521 | -46.3623
5003.7812 | 123.3582 | -68.2251 | 54.863 | -1.3239 | -0.012275 | -0.030142 | -0.0012112 | -0.012527 | -0.0071457 | -0.0022302 | -0.073242 | 0.15106 | -0.37537 | 55.0873 | 54.8767 | 54.8584 | 54.808 | 55.0552 | 54.9271 | 8.4961 | 67.8497 | -54.7119 | 68.1519 | 123.3124 | 0.013733 | 76.7212 | 0.064087 | 0.30212 | 123.0331 | 123.2803 | 123.1018 | 68.3762 | 68.1519 | 123.1522 | 123.0835 | 76.7212 | 68.3762 | 68.1519 | 123.0835 | 123.1018 | 123.1522 | -55.2383 | -46.3669
5004.7812 | 123.3902 | -68.2022 | 54.8492 | 0.31639 | -0.0077888 | -0.021597 | 0.0069064 | -0.0082545 | -0.0069321 | -0.00458 | 0 | 0.16479 | -0.3891 | 55.1239 | 54.8996 | 54.8813 | 54.7302 | 55.0507 | 54.8813 | 8.4869 | 67.8131 | -54.6844 | 68.2022 | 123.3261 | 0.050354 | 76.6891 | 0.032044 | 0.3891 | 122.9324 | 123.2529 | 123.1018 | 68.367 | 68.2022 | 123.0835 | 123.0835 | 76.6891 | 68.367 | 68.2022 | 123.0835 | 123.1018 | 123.0835 | -55.2383 | -46.3623
5005.7812 | 123.3673 | -68.2388 | 54.8172 | 0.27824 | -0.006507 | -0.024161 | 0.0081882 | -0.0091089 | -0.0073593 | -0.0037256 | -0.004578 | 0.19684 | -0.3891 | 55.1193 | 54.8767 | 54.8904 | 54.7668 | 55.0049 | 54.9088 | 8.4961 | 67.8497 | -54.6204 | 68.2343 | 123.3582 | 0.059509 | 76.7349 | 0.091552 | 0.38452 | 123.0057 | 123.2437 | 123.1155 | 68.4357 | 68.2343 | 123.1476 | 123.1293 | 76.7349 | 68.4357 | 68.2343 | 123.1293 | 123.1155 | 123.1476 | -55.2063 | -46.3211
5006.7656 | 123.4085 | -68.2022 | 54.8264 | 0.17143 | -0.010566 | -0.023093 | 0.0047702 | -0.0095361 | -0.0052231 | -0.0022302 | 0.027466 | 0.15564 | -0.38452 | 55.1376 | 54.9133 | 54.9133 | 54.7165 | 55.0507 | 54.8538 | 8.4915 | 67.8177 | -54.6707 | 68.2297 | 123.3398 | 0.086975 | 76.6937 | 0.027466 | 0.41199 | 122.9187 | 123.2529 | 123.1155 | 68.3578 | 68.2297 | 123.056 | 123.1155 | 76.6937 | 68.3578 | 68.2297 | 123.1155 | 123.1155 | 123.056 | -55.2109 | -46.3348
5007.7656 | 123.4085 | -68.2159 | 54.8355 | 0.27061 | -0.0071478 | -0.023306 | 0.0049838 | -0.0097497 | -0.0043685 | -0.005221 | 0.018311 | 0.13275 | -0.39825 | 55.101 | 54.95 | 54.9408 | 54.689 | 55.0827 | 54.8996 | 8.4869 | 67.8177 | -54.7028 | 68.2343 | 123.317 | 0.11444 | 76.7029 | 0.064087 | 0.41657 | 122.905 | 123.2986 | 123.1659 | 68.3487 | 68.2343 | 123.1155 | 123.1567 | 76.7029 | 68.3487 | 68.2343 | 123.1567 | 123.1659 | 123.1155 | -55.2338 | -46.3486
5008.7656 | 123.3902 | -68.2343 | 54.8447 | 0.33165 | -0.011634 | -0.026938 | 0.0077608 | -0.0084681 | -0.0050095 | -0.0022302 | 0.004578 | 0.16937 | -0.40283 | 55.1285 | 54.8996 | 54.9042 | 54.7211 | 55.0735 | 54.8996 | 8.4961 | 67.8314 | -54.6753 | 68.2388 | 123.3627 | 0.054931 | 76.7303 | 0.054931 | 0.40741 | 122.9553 | 123.3078 | 123.1338 | 68.4036 | 68.2388 | 123.1338 | 123.1384 | 76.7303 | 68.4036 | 68.2388 | 123.1384 | 123.1338 | 123.1338 | -55.2475 | -46.3486
5009.7812 | 123.2666 | -68.2526 | 54.8767 | -0.27107 | -0.0090704 | -0.026297 | 0.008829 | -0.0086817 | -0.0075729 | -0.0039392 | 0.032043 | 0.21515 | -0.3891 | 55.0644 | 54.8035 | 54.7806 | 54.895 | 54.95 | 54.95 | 8.4869 | 67.8635 | -54.6616 | 68.2846 | 123.317 | -0.073242 | 76.7395 | 0.073242 | 0.42114 | 123.1476 | 123.2025 | 123.056 | 68.4677 | 68.2846 | 123.2025 | 123.0331 | 76.7395 | 68.4677 | 68.2846 | 123.0331 | 123.056 | 123.2025 | -55.2658 | -46.3898
5010.7812 | 123.2803 | -68.2571 | 54.863 | 0.20195 | -0.0094976 | -0.022879 | 0.0073336 | -0.0082545 | -0.0060775 | -0.0024438 | -0.041199 | 0.23804 | -0.3891 | 55.0323 | 54.6982 | 54.7989 | 54.8813 | 54.9545 | 54.9454 | 8.4915 | 67.868 | -54.6249 | 68.2159 | 123.2895 | -0.1648 | 76.7487 | 0.082398 | 0.3479 | 123.1384 | 123.2117 | 122.9553 | 68.4952 | 68.2159 | 123.2025 | 123.056 | 76.7487 | 68.4952 | 68.2159 | 123.056 | 122.9553 | 123.2025 | -55.2521 | -46.3715
5011.7812 | 123.2758 | -68.2755 | 54.863 | 2.3992 | -0.008216 | -0.027792 | 0.0092562 | -0.0084681 | -0.0058639 | -0.0043664 | 0.11444 | 0.20142 | -0.41199 | 55.0323 | 54.7394 | 54.7943 | 54.895 | 54.9362 | 54.9774 | 8.4961 | 67.8635 | -54.6616 | 68.3899 | 123.3078 | -0.1236 | 76.7715 | 0.11444 | 0.52643 | 123.1705 | 123.2117 | 123.0148 | 68.4769 | 68.3899 | 123.2529 | 123.0698 | 76.7715 | 68.4769 | 68.3899 | 123.0698 | 123.0148 | 123.2529 | -55.275 | -46.3669
5012.7812 | 123.1018 | -68.3029 | 54.8447 | 0.1638 | -0.0067206 | -0.026297 | 0.0075472 | -0.0059045 | -0.0058639 | -0.0020166 | -0.064087 | 0.23804 | -0.3891 | 55.0003 | 54.689 | 54.7806 | 54.9225 | 54.9271 | 54.9683 | 8.4869 | 67.9138 | -54.6066 | 68.2388 | 123.3032 | -0.15564 | 76.7899 | 0.1236 | 0.32501 | 123.2254 | 123.23 | 122.9919 | 68.541 | 68.2388 | 123.2712 | 123.0835 | 76.7899 | 68.541 | 68.2388 | 123.0835 | 122.9919 | 123.2712 | -55.2338 | -46.3577
5013.7656 | 123.2895 | -68.2617 | 54.8904 | 0.22484 | -0.0080024 | -0.023306 | 0.0075472 | -0.0061181 | -0.0052231 | -0.0015894 | -0.041199 | 0.21973 | -0.3891 | 55.0415 | 54.7073 | 54.808 | 54.8767 | 54.9591 | 54.982 | 8.5007 | 67.8726 | -54.6707 | 68.2205 | 123.3032 | -0.18311 | 76.7624 | 0.091553 | 0.3479 | 123.1384 | 123.2208 | 122.9691 | 68.4814 | 68.2205 | 123.2437 | 123.0698 | 76.7624 | 68.4814 | 68.2205 | 123.0698 | 122.9691 | 123.2437 | -55.2795 | -46.3898
5014.7656 | 123.2941 | -68.2709 | 54.895 | -0.11085 | -0.008216 | -0.025656 | 0.0049838 | -0.0054773 | -0.0069321 | -0.0020166 | -0.004578 | 0.20599 | -0.40741 | 55.0278 | 54.689 | 54.7897 | 54.8904 | 54.95 | 54.9637 | 8.4824 | 67.8635 | -54.689 | 68.2663 | 123.2986 | -0.20599 | 76.7532 | 0.068664 | 0.40283 | 123.1613 | 123.2208 | 122.9599 | 68.4769 | 68.2663 | 123.2346 | 123.0606 | 76.7532 | 68.4769 | 68.2663 | 123.0606 | 122.9599 | 123.2346 | -55.3024 | -46.4127
5015.7656 | 123.317 | -68.2617 | 54.895 | 0.17143 | -0.008216 | -0.02352 | 0.0064792 | -0.0067591 | -0.0086411 | -0.0043664 | -0.045776 | 0.23346 | -0.39825 | 55.0049 | 54.9088 | 54.5929 | 54.7989 | 55.2521 | 54.9362 | 8.4915 | 67.8635 | -54.6616 | 68.2159 | 123.2666 | 0.013732 | 76.7532 | 0.041198 | 0.35248 | 123.0606 | 123.5138 | 123.1705 | 68.4952 | 68.2159 | 123.1979 | 122.8546 | 76.7532 | 68.4952 | 68.2159 | 122.8546 | 123.1705 | 123.1979 | -55.2933 | -46.4035
5016.7812 | 123.3215 | -68.2388 | 54.895 | 0.018845 | -0.0088568 | -0.022879 | 0.0077608 | -0.0065455 | -0.0084273 | -0.0026574 | 0.064087 | 0.25635 | -0.33875 | 55.0644 | 54.7577 | 54.8538 | 54.9042 | 55.0232 | 54.9728 | 8.4961 | 67.9001 | -54.6387 | 68.3029 | 123.3032 | -0.13733 | 76.7349 | 0.077819 | 0.40283 | 123.143 | 123.262 | 122.9965 | 68.4952 | 68.3029 | 123.2117 | 123.0927 | 76.7349 | 68.4952 | 68.3029 | 123.0927 | 122.9965 | 123.2117 | -55.2338 | -46.3989
5017.7812 | 123.2758 | -68.2663 | 54.8996 | 0.20195 | -0.0069342 | -0.019247 | 0.0077608 | -0.0065455 | -0.0080001 | -0.0026574 | -0.26093 | 0.2243 | -0.38452 | 55.0232 | 54.7211 | 54.808 | 54.9362 | 54.9408 | 54.9957 | 8.4961 | 67.8818 | -54.6753 | 68.0054 | 123.2895 | -0.17853 | 76.7624 | 0.096131 | 0.1236 | 123.2025 | 123.2071 | 122.9874 | 68.4906 | 68.0054 | 123.262 | 123.0743 | 76.7624 | 68.4906 | 68.0054 | 123.0743 | 122.9874 | 123.262 | -55.2841 | -46.4035
5018.7812 | 123.3261 | -68.2526 | 54.8813 | -0.095596 | -0.0062934 | -0.023306 | 0.0073336 | -0.0050501 | -0.0073593 | -0.0028712 | 0.054932 | 0.25177 | -0.31586 | 55.0552 | 54.7531 | 54.8676 | 54.8996 | 55.0232 | 54.9911 | 8.4869 | 67.9367 | -54.6295 | 68.3075 | 123.3078 | -0.12817 | 76.7395 | 0.10986 | 0.37079 | 123.1522 | 123.2758 | 123.0057 | 68.5043 | 68.3075 | 123.2437 | 123.1201 | 76.7395 | 68.5043 | 68.3075 | 123.1201 | 123.0057 | 123.2437 | -55.1971 | -46.3943
5019.7812 | 123.3307 | -68.2297 | 54.9179 | -0.026932 | -0.0090704 | -0.031851 | 0.0051974 | -0.0041955 | -0.0056503 | -0.0020166 | 0.041199 | 0.27924 | -0.3479 | 55.0827 | 54.6295 | 54.7577 | 55.0232 | 55.0507 | 54.9637 | 8.4915 | 67.8818 | -54.6387 | 68.2709 | 123.3124 | -0.28839 | 76.7212 | 0.045776 | 0.3891 | 123.2529 | 123.2803 | 122.8592 | 68.5089 | 68.2709 | 123.1934 | 122.9874 | 76.7212 | 68.5089 | 68.2709 | 122.9874 | 122.8592 | 123.1934 | -55.2658 | -46.4264
5020.7656 | 123.3032 | -68.248 | 54.8813 | 0.041733 | -0.0086432 | -0.025229 | 0.0077608 | -0.0056909 | -0.0062911 | -0.0015894 | 0.032043 | 0.2243 | -0.36163 | 55.0461 | 54.7119 | 54.8355 | 54.9133 | 54.9957 | 54.9866 | 8.4915 | 67.8864 | -54.657 | 68.28 | 123.2941 | -0.16937 | 76.7395 | 0.10529 | 0.39368 | 123.1613 | 123.2437 | 122.9599 | 68.4723 | 68.28 | 123.2346 | 123.0835 | 76.7395 | 68.4723 | 68.28 | 123.0835 | 122.9599 | 123.2346 | -55.2429 | -46.3898
5021.7656 | 123.317 | -68.2526 | 54.8996 | 0.11803 | -0.0097114 | -0.022238 | 0.0077608 | -0.0048365 | -0.0062911 | -0.0020166 | 0.054932 | 0.25635 | -0.32959 | 55.069 | 54.7394 | 54.8538 | 54.9042 | 55.0369 | 54.9957 | 8.4824 | 67.923 | -54.6432 | 68.3075 | 123.3215 | -0.16022 | 76.7349 | 0.096131 | 0.38452 | 123.1567 | 123.2895 | 122.9919 | 68.5089 | 68.3075 | 123.2483 | 123.1064 | 76.7349 | 68.5089 | 68.3075 | 123.1064 | 122.9919 | 123.2483 | -55.2292 | -46.4172
5022.7656 | 123.3353 | -68.2159 | 54.8859 | -0.011673 | -0.011634 | -0.022879 | 0.0051974 | -0.0073999 | -0.0080001 | -0.00030759 | 0.045776 | 0.25177 | -0.34332 | 55.0919 | 54.7897 | 54.8721 | 54.9271 | 55.0278 | 55.0049 | 8.4915 | 67.8726 | -54.6341 | 68.2617 | 123.3078 | -0.09613 | 76.7075 | 0.11902 | 0.3891 | 123.143 | 123.2437 | 123.0057 | 68.4677 | 68.2617 | 123.2208 | 123.0881 | 76.7075 | 68.4677 | 68.2617 | 123.0881 | 123.0057 | 123.2208 | -55.2292 | -46.3943
5023.7812 | 123.2849 | -68.2571 | 54.9179 | -0.16426 | -0.0088568 | -0.027579 | 0.00092504 | -0.0073999 | -0.0069321 | -0.001803 | 0.013733 | 0.29755 | -0.34332 | 55.0415 | 54.7394 | 54.8355 | 54.9957 | 55.0186 | 55.0278 | 8.4915 | 67.9138 | -54.6204 | 68.2709 | 123.2986 | -0.17853 | 76.7487 | 0.10986 | 0.35706 | 123.2529 | 123.2758 | 122.9965 | 68.5547 | 68.2709 | 123.2849 | 123.0927 | 76.7487 | 68.5547 | 68.2709 | 123.0927 | 122.9965 | 123.2849 | -55.2612 | -46.4264
5024.7812 | 123.2986 | -68.2434 | 54.9133 | -0.11848 | -0.010779 | -0.022879 | 0.0058382 | -0.0086817 | -0.0082137 | -0.0032984 | 0.032043 | 0.3067 | -0.31128 | 55.0507 | 54.7348 | 54.8309 | 54.9957 | 55.0461 | 55.014 | 8.4824 | 67.9321 | -54.6066 | 68.2755 | 123.2941 | -0.17853 | 76.7258 | 0.10071 | 0.34332 | 123.2391 | 123.2895 | 122.9782 | 68.5501 | 68.2755 | 123.2574 | 123.0743 | 76.7258 | 68.5501 | 68.2755 | 123.0743 | 122.9782 | 123.2574 | -55.2246 | -46.431
5025.7812 | 123.3078 | -68.2434 | 54.9179 | -0.16426 | -0.010779 | -0.027365 | 0.004343 | -0.0078271 | -0.0065047 | -0.00030759 | 0.013733 | 0.29755 | -0.33417 | 55.0369 | 54.7119 | 54.8309 | 54.982 | 55.0415 | 55.0323 | 8.4915 | 67.9092 | -54.6204 | 68.2571 | 123.2803 | -0.20599 | 76.7349 | 0.11444 | 0.3479 | 123.2254 | 123.2849 | 122.9553 | 68.541 | 68.2571 | 123.2758 | 123.0743 | 76.7349 | 68.541 | 68.2571 | 123.0743 | 122.9553 | 123.2758 | -55.2521 | -46.4264
5026.7812 | 123.2849 | -68.2388 | 54.9179 | -0.16426 | -0.010352 | -0.028647 | 0.0049838 | -0.0084681 | -0.0071457 | -0.0028712 | 0.013733 | 0.31586 | -0.32044 | 55.0415 | 54.6844 | 54.7852 | 55.0003 | 55.014 | 55.014 | 8.4824 | 67.9184 | -54.6021 | 68.2526 | 123.2803 | -0.23346 | 76.7212 | 0.09613 | 0.33417 | 123.2391 | 123.2529 | 122.9233 | 68.5547 | 68.2526 | 123.2529 | 123.024 | 76.7212 | 68.5547 | 68.2526 | 123.024 | 122.9233 | 123.2529 | -55.2383 | -46.4355
5027.7656 | 123.3124 | -68.2388 | 54.95 | -0.149 | -0.0094976 | -0.020743 | 0.0045566 | -0.0088953 | -0.0075729 | -0.0024438 | 0.036621 | 0.2655 | -0.32959 | 55.0507 | 54.7028 | 54.8264 | 54.9728 | 55.0369 | 54.9911 | 8.4824 | 67.9092 | -54.6844 | 68.2755 | 123.2895 | -0.24719 | 76.7212 | 0.041199 | 0.36621 | 123.2117 | 123.2758 | 122.9416 | 68.5043 | 68.2755 | 123.23 | 123.0652 | 76.7212 | 68.5043 | 68.2755 | 123.0652 | 122.9416 | 123.23 | -55.2795 | -46.4676
5028.7656 | 123.2895 | -68.2251 | 54.9362 | -0.13374 | -0.010779 | -0.02587 | 0.0045566 | -0.011031 | -0.0071457 | -0.00073479 | 0.018311 | 0.28381 | -0.33417 | 55.0507 | 54.7119 | 54.8309 | 54.9957 | 55.014 | 55.0369 | 8.4915 | 67.8909 | -54.6524 | 68.2434 | 123.2758 | -0.2243 | 76.7166 | 0.10071 | 0.35248 | 123.2208 | 123.2391 | 122.937 | 68.5089 | 68.2434 | 123.262 | 123.056 | 76.7166 | 68.5089 | 68.2434 | 123.056 | 122.937 | 123.262 | -55.2704 | -46.4447
5029.7656 | 123.3994 | -68.1656 | 54.8859 | 0.70549 | -0.010779 | -0.027792 | -0.0016386 | -0.0095361 | -0.0080001 | -0.0047938 | 0.032043 | 0.24261 | -0.30212 | 55.1468 | 54.8355 | 54.9316 | 54.8172 | 55.1468 | 54.9774 | 8.4915 | 67.8635 | -54.6432 | 68.1976 | 123.3124 | -0.050354 | 76.6571 | 0.091553 | 0.33417 | 122.9828 | 123.3124 | 123.0011 | 68.4082 | 68.1976 | 123.143 | 123.0972 | 76.6571 | 68.4082 | 68.1976 | 123.0972 | 123.0011 | 123.143 | -55.188 | -46.3943
5030.7812 | 123.3948 | -68.2022 | 54.8813 | -0.13374 | -0.012702 | -0.028433 | 0.00092504 | -0.0088953 | -0.0073593 | -0.003512 | 0.068665 | 0.22888 | -0.32501 | 55.1239 | 54.9225 | 54.9408 | 54.8309 | 55.1468 | 54.9316 | 8.4869 | 67.8772 | -54.6524 | 68.2709 | 123.3261 | 0.041198 | 76.6891 | 0.050354 | 0.39368 | 123.0331 | 123.349 | 123.1247 | 68.4311 | 68.2709 | 123.1338 | 123.143 | 76.6891 | 68.4311 | 68.2709 | 123.143 | 123.1247 | 123.1338 | -55.2063 | -46.3943
5031.7812 | 123.3719 | -68.2022 | 54.9133 | -0.17952 | -0.012488 | -0.023947 | 0.002634 | -0.012313 | -0.0067185 | -0.003512 | 0.086975 | 0.21057 | -0.30212 | 55.1376 | 54.8996 | 54.9042 | 54.8584 | 55.1285 | 54.9683 | 8.4869 | 67.9001 | -54.7028 | 68.2892 | 123.3398 | -0.013733 | 76.6891 | 0.054932 | 0.3891 | 123.0606 | 123.3307 | 123.1018 | 68.4128 | 68.2892 | 123.1705 | 123.1064 | 76.6891 | 68.4128 | 68.2892 | 123.1064 | 123.1018 | 123.1705 | -55.2155 | -46.4264
5032.7812 | 123.4085 | -68.1839 | 54.9088 | -0.11848 | -0.013984 | -0.025656 | 0.0013522 | -0.01274 | -0.0073593 | -0.003512 | 0.07782 | 0.20599 | -0.32501 | 55.1422 | 54.8447 | 54.9225 | 54.8264 | 55.1468 | 54.9637 | 8.4915 | 67.8589 | -54.7028 | 68.2617 | 123.3261 | -0.064086 | 76.6754 | 0.054932 | 0.40283 | 123.0103 | 123.3307 | 123.0286 | 68.3899 | 68.2617 | 123.1476 | 123.1064 | 76.6754 | 68.3899 | 68.2617 | 123.1064 | 123.0286 | 123.1476 | -55.2338 | -46.4172
5033.7812 | 123.2758 | -68.2846 | 54.895 | 0.064621 | -0.006507 | -0.022665 | 0.012461 | -0.0095361 | -0.0037277 | -0.0050074 | 0.036621 | 0.24261 | -0.36621 | 55.0598 | 54.7989 | 54.7943 | 54.895 | 54.9774 | 54.9728 | 8.4778 | 67.9184 | -54.6524 | 68.3212 | 123.3444 | -0.096131 | 76.7624 | 0.077819 | 0.40283 | 123.1796 | 123.262 | 123.0835 | 68.5272 | 68.3212 | 123.2574 | 123.0789 | 76.7624 | 68.5272 | 68.3212 | 123.0789 | 123.0835 | 123.2574 | -55.2612 | -46.4172
5034.7656 | 123.3627 | -68.2068 | 54.8996 | -0.17189 | -0.012061 | -0.022238 | 0.001993 | -0.0095361 | -0.0077865 | -0.00458 | 0.064087 | 0.21973 | -0.31586 | 55.1376 | 54.7806 | 54.8996 | 54.863 | 55.1285 | 54.9957 | 8.4915 | 67.8909 | -54.6799 | 68.2709 | 123.3444 | -0.11902 | 76.6983 | 0.096131 | 0.37994 | 123.0698 | 123.3353 | 122.9874 | 68.4265 | 68.2709 | 123.2025 | 123.1064 | 76.6983 | 68.4265 | 68.2709 | 123.1064 | 122.9874 | 123.2025 | -55.2155 | -46.4081
5035.7656 | 123.3902 | -68.1839 | 54.8859 | -0.072708 | -0.012702 | -0.024588 | 0.0039156 | -0.013381 | -0.0075729 | -0.003512 | 0.050354 | 0.19684 | -0.32959 | 55.1422 | 54.7989 | 54.9316 | 54.8126 | 55.1422 | 54.9911 | 8.5007 | 67.8543 | -54.689 | 68.2343 | 123.3261 | -0.086975 | 76.6846 | 0.10529 | 0.37994 | 122.9965 | 123.3261 | 122.9828 | 68.3807 | 68.2343 | 123.175 | 123.1155 | 76.6846 | 68.3807 | 68.2343 | 123.1155 | 122.9828 | 123.175 | -55.2155 | -46.3852
5036.7656 | 123.349 | -68.2114 | 54.8813 | 0.095139 | -0.012488 | -0.028433 | 0.00071144 | -0.012313 | -0.0060775 | -0.0026574 | 0.091553 | 0.17395 | -0.3479 | 55.0781 | 54.8447 | 54.8447 | 54.8035 | 55.0461 | 54.9545 | 8.4915 | 67.8635 | -54.7073 | 68.3029 | 123.2895 | -0.036621 | 76.7029 | 0.073242 | 0.43945 | 123.0148 | 123.2574 | 123.056 | 68.3853 | 68.3029 | 123.1659 | 123.056 | 76.7029 | 68.3853 | 68.3029 | 123.056 | 123.056 | 123.1659 | -55.2292 | -46.3898
5037.7812 | 123.3582 | -68.2343 | 54.8813 | 0.034104 | -0.015479 | -0.02822 | 0.001993 | -0.013381 | -0.0058639 | -0.0013758 | -0.045776 | 0.19684 | -0.34332 | 55.0964 | 54.8767 | 54.863 | 54.808 | 55.0781 | 54.9454 | 8.4961 | 67.8909 | -54.6844 | 68.1885 | 123.3307 | -0.004578 | 76.7303 | 0.064087 | 0.29755 | 123.0423 | 123.3124 | 123.111 | 68.4311 | 68.1885 | 123.1796 | 123.0972 | 76.7303 | 68.4311 | 68.1885 | 123.0972 | 123.111 | 123.1796 | -55.2246 | -46.3852
5038.7812 | 123.2895 | -68.2343 | 54.9271 | -0.057449 | -0.0097114 | -0.027579 | 0.0079744 | -0.011886 | -0.0077865 | -0.0024438 | 0.018311 | 0.31586 | -0.32959 | 55.0735 | 54.7073 | 54.7989 | 54.9728 | 55.0232 | 54.982 | 8.4824 | 67.9047 | -54.6112 | 68.2526 | 123.3078 | -0.21973 | 76.7166 | 0.054932 | 0.3479 | 123.2071 | 123.2574 | 122.9416 | 68.5501 | 68.2526 | 123.2162 | 123.0331 | 76.7166 | 68.5501 | 68.2526 | 123.0331 | 122.9416 | 123.2162 | -55.2567 | -46.4447
5039.7812 | 123.3673 | -68.2114 | 54.8859 | -0.019302 | -0.011848 | -0.028861 | 0.0022066 | -0.011886 | -0.0058639 | -0.0041528 | -0.022888 | 0.19226 | -0.3479 | 55.0919 | 54.8859 | 54.8676 | 54.808 | 55.0507 | 54.95 | 8.4869 | 67.8635 | -54.6936 | 68.1885 | 123.3032 | 0 | 76.6983 | 0.064087 | 0.32501 | 123.0194 | 123.262 | 123.0972 | 68.4036 | 68.1885 | 123.1613 | 123.0789 | 76.6983 | 68.4036 | 68.1885 | 123.0789 | 123.0972 | 123.1613 | -55.2338 | -46.3989
5040.7812 | 123.349 | -68.2159 | 54.863 | 0.11803 | -0.012275 | -0.026083 | -0.0027066 | -0.010604 | -0.0054367 | -0.0022302 | -0.036621 | 0.18768 | -0.36621 | 55.069 | 54.689 | 54.8355 | 54.776 | 55.0507 | 54.9454 | 8.4961 | 67.8497 | -54.6753 | 68.1793 | 123.2849 | -0.17395 | 76.712 | 0.082398 | 0.32959 | 122.9919 | 123.2666 | 122.905 | 68.4036 | 68.1793 | 123.1613 | 123.0515 | 76.712 | 68.4036 | 68.1793 | 123.0515 | 122.905 | 123.1613 | -55.2292 | -46.3669
5041.7656 | 123.3856 | -68.2114 | 54.863 | -0.0040434 | -0.013984 | -0.027365 | 0.00092504 | -0.013381 | -0.0073593 | -0.0026574 | 0 | 0.19684 | -0.35248 | 55.1193 | 54.7806 | 54.8904 | 54.7989 | 55.0919 | 54.9225 | 8.4824 | 67.8589 | -54.6661 | 68.2114 | 123.3307 | -0.082397 | 76.6937 | 0.059509 | 0.35248 | 123.0103 | 123.3032 | 122.9919 | 68.4082 | 68.2114 | 123.1338 | 123.1018 | 76.6937 | 68.4082 | 68.2114 | 123.1018 | 122.9919 | 123.1338 | -55.2155 | -46.3806
5042.7656 | 123.3673 | -68.2251 | 54.863 | 0.034104 | -0.013557 | -0.028006 | 0.0013522 | -0.012313 | -0.0054367 | -0.0028712 | -0.009155 | 0.18768 | -0.33417 | 55.1193 | 54.744 | 54.863 | 54.7852 | 55.0735 | 54.9454 | 8.4961 | 67.8909 | -54.6753 | 68.2159 | 123.3444 | -0.11902 | 76.7212 | 0.082398 | 0.32501 | 123.0103 | 123.2986 | 122.9691 | 68.4128 | 68.2159 | 123.1705 | 123.0881 | 76.7212 | 68.4128 | 68.2159 | 123.0881 | 122.9691 | 123.1705 | -55.1971 | -46.3669
5043.7812 | 123.3765 | -68.1885 | 54.9088 | -0.18715 | -0.012916 | -0.027152 | 0.0013522 | -0.01274 | -0.0073593 | -0.0047938 | 0.07782 | 0.18768 | -0.29755 | 55.1788 | 54.9316 | 54.9225 | 54.8035 | 55.1331 | 54.95 | 8.4869 | 67.8909 | -54.7211 | 68.2663 | 123.3673 | 0.022889 | 76.6754 | 0.041199 | 0.37537 | 122.9919 | 123.3215 | 123.1201 | 68.3762 | 68.2663 | 123.1384 | 123.111 | 76.6754 | 68.3762 | 68.2663 | 123.111 | 123.1201 | 123.1384 | -55.2063 | -46.4218
5044.7812 | 123.4039 | -68.1931 | 54.8538 | 0.2401 | -0.012061 | -0.027579 | 0.0058382 | -0.0097497 | -0.0047957 | -0.003512 | -0.004578 | 0.1236 | -0.36621 | 55.1376 | 54.8035 | 54.8813 | 54.7348 | 55.069 | 54.9225 | 8.4915 | 67.8268 | -54.7302 | 68.1885 | 123.3307 | -0.050354 | 76.6846 | 0.068664 | 0.36163 | 122.9279 | 123.262 | 122.9965 | 68.3167 | 68.1885 | 123.1155 | 123.0743 | 76.6846 | 68.3167 | 68.1885 | 123.0743 | 122.9965 | 123.1155 | -55.22 | -46.3623
5045.7812 | 123.3765 | -68.1976 | 54.8401 | 0.22484 | -0.010566 | -0.026083 | 0.0056246 | -0.010391 | -0.0073593 | -0.0024438 | -0.004578 | 0.14191 | -0.37537 | 55.1331 | 54.8859 | 54.8904 | 54.7165 | 55.0598 | 54.9133 | 8.4915 | 67.8223 | -54.6982 | 68.1931 | 123.3307 | 0.045776 | 76.6891 | 0.073242 | 0.37079 | 122.9141 | 123.2574 | 123.0835 | 68.3395 | 68.1931 | 123.111 | 123.0881 | 76.6891 | 68.3395 | 68.1931 | 123.0881 | 123.0835 | 123.111 | -55.2155 | -46.3486
5046.7812 | 123.3902 | -68.2343 | 54.8309 | 0.23247 | -0.011207 | -0.020529 | 0.0047702 | -0.0099633 | -0.0056503 | -0.00094839 | 0.022888 | 0.14191 | -0.36163 | 55.1239 | 54.8996 | 54.895 | 54.7119 | 55.0644 | 54.9133 | 8.4869 | 67.8726 | -54.689 | 68.2571 | 123.3582 | 0.068664 | 76.7212 | 0.082397 | 0.38452 | 122.9462 | 123.2986 | 123.1338 | 68.3762 | 68.2571 | 123.1476 | 123.1293 | 76.7212 | 68.3762 | 68.2571 | 123.1293 | 123.1338 | 123.1476 | -55.1926 | -46.344
5047.7656 | 123.3582 | -68.2434 | 54.8538 | 0.20958 | -0.009925 | -0.026297 | 0.0039156 | -0.012313 | -0.0050095 | -0.001803 | -0.009155 | 0.13733 | -0.40283 | 55.0964 | 54.8813 | 54.8538 | 54.7623 | 55.0461 | 54.9179 | 8.4869 | 67.8406 | -54.7165 | 68.2343 | 123.3398 | 0.027466 | 76.7303 | 0.064087 | 0.39368 | 123.0057 | 123.2895 | 123.1247 | 68.3807 | 68.2343 | 123.1613 | 123.0972 | 76.7303 | 68.3807 | 68.2343 | 123.0972 | 123.1247 | 123.1613 | -55.2567 | -46.3669
5048.7656 | 123.3765 | -68.2159 | 54.8492 | 0.20958 | -0.010779 | -0.025656 | 0.003702 | -0.010818 | -0.0060775 | -0.00458 | 0.004578 | 0.12817 | -0.38452 | 55.1147 | 54.9088 | 54.8904 | 54.7211 | 55.0598 | 54.9088 | 8.4824 | 67.8314 | -54.7211 | 68.2205 | 123.3307 | 0.059509 | 76.6983 | 0.059509 | 0.3891 | 122.937 | 123.2758 | 123.1247 | 68.3441 | 68.2205 | 123.1247 | 123.1064 | 76.6983 | 68.3441 | 68.2205 | 123.1064 | 123.1247 | 123.1247 | -55.2338 | -46.3669
5049.7656 | 123.4177 | -68.2159 | 54.8538 | 0.20958 | -0.009925 | -0.022665 | 0.0066928 | -0.010177 | -0.0041549 | -0.00458 | 0.018311 | 0.14191 | -0.35248 | 55.1239 | 54.895 | 54.9042 | 54.7165 | 55.069 | 54.8996 | 8.4915 | 67.8635 | -54.7119 | 68.2343 | 123.3398 | 0.041199 | 76.7075 | 0.045776 | 0.37079 | 122.9324 | 123.2849 | 123.111 | 68.3578 | 68.2343 | 123.1155 | 123.1201 | 76.7075 | 68.3578 | 68.2343 | 123.1201 | 123.111 | 123.1155 | -55.2063 | -46.3623
5050.7812 | 123.3124 | -68.2526 | 54.8676 | 0.23247 | -0.0067206 | -0.028006 | 0.0098972 | -0.010604 | -0.0060775 | -0.0013758 | -0.041199 | 0.21057 | -0.38452 | 55.0598 | 54.8355 | 54.7897 | 54.8447 | 54.9728 | 54.9316 | 8.4869 | 67.868 | -54.657 | 68.2114 | 123.3124 | -0.032044 | 76.7395 | 0.064087 | 0.34332 | 123.0972 | 123.2254 | 123.0881 | 68.4631 | 68.2114 | 123.1842 | 123.0423 | 76.7395 | 68.4631 | 68.2114 | 123.0423 | 123.0881 | 123.1842 | -55.2521 | -46.3806
5051.7812 | 123.2849 | -68.2526 | 54.8721 | 0.17143 | -0.0077888 | -0.023734 | 0.0096834 | -0.0088953 | -0.0050095 | -0.0011622 | -0.036621 | 0.24261 | -0.37994 | 55.0552 | 54.6707 | 54.7897 | 54.8721 | 54.9408 | 54.9728 | 8.4915 | 67.8726 | -54.6295 | 68.2159 | 123.3078 | -0.20142 | 76.7441 | 0.10071 | 0.34332 | 123.1247 | 123.1934 | 122.9233 | 68.4952 | 68.2159 | 123.2254 | 123.0423 | 76.7441 | 68.4952 | 68.2159 | 123.0423 | 122.9233 | 123.2254 | -55.2521 | -46.3806
5052.7812 | 123.3032 | -68.248 | 54.8492 | 0.19432 | -0.0090704 | -0.026083 | 0.0075472 | -0.0056909 | -0.0037277 | -0.0020166 | -0.032043 | 0.22888 | -0.39825 | 55.0598 | 54.6936 | 54.8126 | 54.8355 | 54.9683 | 54.9911 | 8.4915 | 67.8497 | -54.6204 | 68.2159 | 123.3078 | -0.15564 | 76.7395 | 0.14191 | 0.36621 | 123.0835 | 123.2162 | 122.9416 | 68.4769 | 68.2159 | 123.2391 | 123.0606 | 76.7395 | 68.4769 | 68.2159 | 123.0606 | 122.9416 | 123.2391 | -55.2475 | -46.3577
5053.7812 | 123.3032 | -68.248 | 54.8813 | 0.26299 | -0.0045844 | -0.023734 | 0.0077608 | -0.0076135 | -0.0047957 | -0.0050074 | -0.041199 | 0.23346 | -0.37079 | 55.0598 | 54.657 | 54.7943 | 54.8767 | 54.9408 | 54.9774 | 8.4869 | 67.8772 | -54.6478 | 68.2068 | 123.3078 | -0.22431 | 76.7349 | 0.09613 | 0.32959 | 123.1247 | 123.1888 | 122.905 | 68.4814 | 68.2068 | 123.2254 | 123.0423 | 76.7349 | 68.4814 | 68.2068 | 123.0423 | 122.905 | 123.2254 | -55.2521 | -46.3943
5054.7656 | 123.3719 | -68.248 | 54.8447 | 0.25536 | -0.006507 | -0.025443 | 0.0064792 | -0.0084681 | -0.0062911 | -0.0022302 | -0.027466 | 0.17395 | -0.37994 | 55.0827 | 54.7211 | 54.8676 | 54.7806 | 55.0186 | 54.9042 | 8.4915 | 67.868 | -54.6707 | 68.2205 | 123.3307 | -0.1236 | 76.7395 | 0.059509 | 0.35248 | 123.0286 | 123.2666 | 122.9691 | 68.4219 | 68.2205 | 123.1522 | 123.1155 | 76.7395 | 68.4219 | 68.2205 | 123.1155 | 122.9691 | 123.1522 | -55.2246 | -46.3531
5055.7656 | 123.3398 | -68.2526 | 54.863 | 0.24773 | -0.0077888 | -0.024161 | 0.00712 | -0.0071863 | -0.0073593 | -0.00094839 | -0.050354 | 0.20599 | -0.40283 | 55.0598 | 54.6982 | 54.8355 | 54.8172 | 54.982 | 54.95 | 8.4869 | 67.8497 | -54.657 | 68.2022 | 123.3124 | -0.1648 | 76.7395 | 0.086975 | 0.35248 | 123.0698 | 123.2346 | 122.9507 | 68.4586 | 68.2022 | 123.2025 | 123.0881 | 76.7395 | 68.4586 | 68.2022 | 123.0881 | 122.9507 | 123.2025 | -55.2658 | -46.376
5056.7656 | 123.3078 | -68.28 | 54.8676 | 0.23247 | -0.0067206 | -0.02352 | 0.0075472 | -0.0063317 | -0.0047957 | -0.0030848 | -0.041199 | 0.21515 | -0.3891 | 55.0278 | 54.6661 | 54.8035 | 54.8767 | 54.9362 | 54.9545 | 8.4915 | 67.8909 | -54.6524 | 68.2388 | 123.3078 | -0.20142 | 76.7715 | 0.086975 | 0.3479 | 123.1567 | 123.2162 | 122.9462 | 68.4952 | 68.2388 | 123.2346 | 123.0835 | 76.7715 | 68.4952 | 68.2388 | 123.0835 | 122.9462 | 123.2346 | -55.2567 | -46.376
5057.7812 | 123.2849 | -68.2571 | 54.8859 | 0.064621 | -0.0086432 | -0.024588 | 0.0075472 | -0.0078271 | -0.0067185 | -0.0043664 | -0.004578 | 0.24719 | -0.34332 | 55.0507 | 54.689 | 54.8264 | 54.8996 | 54.9728 | 54.9911 | 8.4915 | 67.9138 | -54.6387 | 68.2526 | 123.3078 | -0.19684 | 76.7487 | 0.10529 | 0.33874 | 123.1567 | 123.23 | 122.9462 | 68.5043 | 68.2526 | 123.2483 | 123.0835 | 76.7487 | 68.5043 | 68.2526 | 123.0835 | 122.9462 | 123.2483 | -55.2292 | -46.3943
5058.7812 | 123.3078 | -68.2571 | 54.8813 | 0.072251 | -0.0088568 | -0.020102 | 0.0077608 | -0.0065455 | -0.0062911 | -0.0020166 | 0.041199 | 0.24261 | -0.33875 | 55.069 | 54.8492 | 54.8447 | 54.9088 | 54.9683 | 54.9957 | 8.4824 | 67.9184 | -54.6387 | 68.2983 | 123.3261 | -0.032044 | 76.7395 | 0.11444 | 0.37994 | 123.1659 | 123.2254 | 123.1064 | 68.4998 | 68.2983 | 123.2529 | 123.1018 | 76.7395 | 68.4998 | 68.2983 | 123.1018 | 123.1064 | 123.2529 | -55.22 | -46.3989
5059.7812 | 123.2849 | -68.2571 | 54.9042 | 0.049362 | -0.009284 | -0.023947 | 0.00712 | -0.0069727 | -0.0052231 | -0.0020166 | -0.009155 | 0.24261 | -0.36163 | 55.0369 | 54.8355 | 54.8218 | 54.9133 | 54.9774 | 54.9774 | 8.4732 | 67.8955 | -54.6616 | 68.248 | 123.2941 | -0.068665 | 76.7303 | 0.073242 | 0.35248 | 123.1705 | 123.2346 | 123.0927 | 68.4998 | 68.248 | 123.2346 | 123.0789 | 76.7303 | 68.4998 | 68.248 | 123.0789 | 123.0927 | 123.2346 | -55.2658 | -46.431
5060.7812 | 123.2986 | -68.2617 | 54.9042 | 0.034104 | -0.0094976 | -0.021384 | 0.0073336 | -0.0067591 | -0.0058639 | -0.0032984 | 0.027466 | 0.25177 | -0.34332 | 55.0552 | 54.6936 | 54.8309 | 54.9133 | 54.9866 | 54.9683 | 8.4869 | 67.9184 | -54.6524 | 68.2892 | 123.317 | -0.21057 | 76.7487 | 0.064087 | 0.37079 | 123.175 | 123.2483 | 122.9553 | 68.5135 | 68.2892 | 123.23 | 123.0927 | 76.7487 | 68.5135 | 68.2892 | 123.0927 | 122.9553 | 123.23 | -55.2475 | -46.4172
5061.7656 | 123.262 | -68.28 | 54.8721 | 0.07988 | -0.0088568 | -0.02352 | 0.0066928 | -0.0069727 | -0.0086411 | -0.0015894 | -0.050354 | 0.23346 | -0.3891 | 54.9866 | 54.6524 | 54.8035 | 54.95 | 54.9362 | 54.982 | 8.4915 | 67.8909 | -54.6387 | 68.2297 | 123.2666 | -0.21973 | 76.7715 | 0.10986 | 0.33874 | 123.23 | 123.2162 | 122.9324 | 68.5135 | 68.2297 | 123.262 | 123.0835 | 76.7715 | 68.5135 | 68.2297 | 123.0835 | 122.9324 | 123.262 | -55.2612 | -46.3806
5062.7656 | 123.2803 | -68.2617 | 54.8721 | 0.07988 | -0.0088568 | -0.026938 | 0.0062656 | -0.0050501 | -0.0060775 | -0.0013758 | -0.009155 | 0.21973 | -0.36621 | 55.014 | 54.6753 | 54.808 | 54.9362 | 54.9683 | 54.9866 | 8.4915 | 67.8955 | -54.6524 | 68.2526 | 123.2758 | -0.19684 | 76.7532 | 0.11444 | 0.35706 | 123.1979 | 123.23 | 122.937 | 68.4814 | 68.2526 | 123.2483 | 123.0698 | 76.7532 | 68.4814 | 68.2526 | 123.0698 | 122.937 | 123.2483 | -55.2383 | -46.3806
5063.7656 | 123.2895 | -68.2526 | 54.8859 | 0.049362 | -0.0084296 | -0.023306 | 0.0062656 | -0.0048365 | -0.0050095 | -0.0028712 | 0 | 0.24261 | -0.35248 | 55.0461 | 54.6707 | 54.8172 | 54.9179 | 54.9866 | 55.0186 | 8.4961 | 67.9001 | -54.6432 | 68.2526 | 123.2986 | -0.21515 | 76.7487 | 0.13275 | 0.35248 | 123.1705 | 123.2391 | 122.9233 | 68.4952 | 68.2526 | 123.2712 | 123.0698 | 76.7487 | 68.4952 | 68.2526 | 123.0698 | 122.9233 | 123.2712 | -55.2383 | -46.3898
5064.7812 | 123.3307 | -68.2526 | 54.8859 | -0.087967 | -0.009284 | -0.022665 | 0.0069064 | -0.0073999 | -0.0047957 | -0.0026574 | 0.041199 | 0.29297 | -0.32501 | 55.069 | 54.7073 | 54.8721 | 54.9591 | 55.0461 | 54.9866 | 8.4778 | 67.9276 | -54.5929 | 68.2938 | 123.3215 | -0.17853 | 76.7303 | 0.10071 | 0.36621 | 123.2117 | 123.2986 | 122.9599 | 68.5455 | 68.2938 | 123.2391 | 123.1247 | 76.7303 | 68.5455 | 68.2938 | 123.1247 | 122.9599 | 123.2391 | -55.2109 | -46.4081
5065.7812 | 123.3261 | -68.2343 | 54.9133 | -0.11848 | -0.011207 | -0.023734 | 0.0060518 | -0.0061181 | -0.0062911 | -0.0020166 | 0.032043 | 0.29297 | -0.32959 | 55.069 | 54.7256 | 54.863 | 54.9362 | 55.0598 | 55.0003 | 8.4915 | 67.9047 | -54.6204 | 68.2663 | 123.3032 | -0.18768 | 76.7258 | 0.086975 | 0.36163 | 123.1705 | 123.2941 | 122.9599 | 68.5272 | 68.2663 | 123.2346 | 123.0972 | 76.7258 | 68.5272 | 68.2663 | 123.0972 | 122.9599 | 123.2346 | -55.2429 | -46.4218
5066.7812 | 123.3261 | -68.2205 | 54.8996 | -0.087967 | -0.0094976 | -0.022025 | 0.0058382 | -0.0091089 | -0.0069321 | -0.00073479 | 0.032043 | 0.27008 | -0.32044 | 55.0873 | 54.8767 | 54.863 | 54.9316 | 55.0461 | 55.0095 | 8.4869 | 67.9001 | -54.6295 | 68.2526 | 123.3078 | -0.022888 | 76.7075 | 0.10986 | 0.35248 | 123.1522 | 123.2666 | 123.0972 | 68.4906 | 68.2526 | 123.23 | 123.0835 | 76.7075 | 68.4906 | 68.2526 | 123.0835 | 123.0972 | 123.23 | -55.22 | -46.4127
5067.7812 | 123.3215 | -68.2434 | 54.8996 | -0.12611 | -0.008216 | -0.022238 | 0.0062656 | -0.0080407 | -0.0067185 | -0.0013758 | 0.036621 | 0.29297 | -0.32501 | 55.0735 | 54.8721 | 54.8447 | 54.9545 | 55.0598 | 55.0095 | 8.4961 | 67.9184 | -54.6066 | 68.28 | 123.317 | -0.027466 | 76.7395 | 0.10986 | 0.36163 | 123.1979 | 123.3032 | 123.1155 | 68.5364 | 68.28 | 123.2529 | 123.0881 | 76.7395 | 68.5364 | 68.28 | 123.0881 | 123.1155 | 123.2529 | -55.2246 | -46.4035
5068.7656 | 123.3261 | -68.2159 | 54.9042 | -0.019302 | -0.0094976 | -0.023734 | 0.005411 | -0.0061181 | -0.0084273 | -0.0032984 | 0.2243 | 0.25177 | -0.29755 | 55.0552 | 54.8721 | 54.8538 | 54.9179 | 55.069 | 55.0095 | 8.4915 | 67.9184 | -54.6524 | 68.4402 | 123.2712 | -0.032044 | 76.7075 | 0.10528 | 0.52185 | 123.1338 | 123.2849 | 123.0881 | 68.4677 | 68.4402 | 123.2254 | 123.0698 | 76.7075 | 68.4677 | 68.4402 | 123.0698 | 123.0881 | 123.2254 | -55.2017 | -46.4127
5069.7656 | 123.3582 | -68.2388 | 54.8904 | -0.087967 | -0.010993 | -0.026511 | 0.005411 | -0.0073999 | -0.0084273 | -0.0022302 | 0.054932 | 0.25177 | -0.32501 | 55.069 | 54.8676 | 54.8584 | 54.9316 | 55.0461 | 55.0049 | 8.4869 | 67.9138 | -54.6387 | 68.2938 | 123.3078 | -0.022888 | 76.7258 | 0.11444 | 0.37994 | 123.1705 | 123.2849 | 123.1064 | 68.4906 | 68.2938 | 123.2437 | 123.0972 | 76.7258 | 68.4906 | 68.2938 | 123.0972 | 123.1064 | 123.2437 | -55.2155 | -46.4035
5070.7656 | 123.3261 | -68.2434 | 54.8904 | -0.095596 | -0.010993 | -0.024374 | 0.0062656 | -0.0078271 | -0.0073593 | -0.0024438 | 0.050354 | 0.27008 | -0.32959 | 55.069 | 54.8813 | 54.8584 | 54.9271 | 55.069 | 55.0186 | 8.4869 | 67.9138 | -54.6204 | 68.2938 | 123.3124 | -0.009155 | 76.7303 | 0.12817 | 0.37994 | 123.1705 | 123.3124 | 123.1247 | 68.5135 | 68.2938 | 123.262 | 123.1018 | 76.7303 | 68.5135 | 68.2938 | 123.1018 | 123.1247 | 123.262 | -55.22 | -46.4035
5071.7812 | 123.2712 | -68.2617 | 54.9133 | -0.2253 | -0.0094976 | -0.026511 | -0.00014316 | -0.0076135 | -0.0060775 | -0.00094839 | 0.022888 | 0.27466 | -0.30212 | 55.0781 | 55.0598 | 54.8538 | 54.8355 | 54.9545 | 55.0507 | 8.4869 | 67.9596 | -54.6387 | 68.2846 | 123.3398 | 0.14648 | 76.7487 | 0.13733 | 0.32501 | 123.0972 | 123.2162 | 123.3215 | 68.5364 | 68.2846 | 123.3124 | 123.1155 | 76.7487 | 68.5364 | 68.2846 | 123.1155 | 123.3215 | 123.3124 | -55.2155 | -46.4264
5072.7812 | 123.3078 | -68.2251 | 54.9271 | -0.17189 | -0.010993 | -0.025443 | 0.00049764 | -0.0086817 | -0.0056503 | -0.0028712 | 0.022888 | 0.28839 | -0.31128 | 55.0461 | 54.8538 | 54.8355 | 54.9866 | 55.0461 | 55.0049 | 8.4869 | 67.9138 | -54.6387 | 68.248 | 123.2712 | -0.073242 | 76.712 | 0.07782 | 0.33417 | 123.2117 | 123.2712 | 123.0789 | 68.5135 | 68.248 | 123.23 | 123.0606 | 76.712 | 68.5135 | 68.248 | 123.0606 | 123.0789 | 123.23 | -55.2383 | -46.4401
5073.7812 | 123.2986 | -68.2526 | 54.9133 | -0.19478 | -0.011634 | -0.023306 | 0.0022066 | -0.010177 | -0.0084273 | -0.0028712 | 0.009155 | 0.28839 | -0.3067 | 54.9957 | 54.8584 | 54.808 | 54.982 | 55.0232 | 55.0186 | 8.4915 | 67.9459 | -54.6249 | 68.2617 | 123.2483 | -0.054932 | 76.7441 | 0.10529 | 0.31586 | 123.2346 | 123.2758 | 123.111 | 68.541 | 68.2617 | 123.2712 | 123.0606 | 76.7441 | 68.541 | 68.2617 | 123.0606 | 123.111 | 123.2712 | -55.22 | -46.4218
5074.7812 | 123.317 | -68.2526 | 54.9637 | -0.15663 | -0.010566 | -0.028006 | 0.0039156 | -0.010604 | -0.0054367 | -0.0013758 | 0.032043 | 0.2655 | -0.29755 | 55.0369 | 54.8401 | 54.8218 | 54.9774 | 55.0461 | 55.0186 | 8.4869 | 67.955 | -54.6982 | 68.2846 | 123.2895 | -0.1236 | 76.7395 | 0.054932 | 0.32959 | 123.23 | 123.2986 | 123.0927 | 68.5181 | 68.2846 | 123.2712 | 123.0743 | 76.7395 | 68.5181 | 68.2846 | 123.0743 | 123.0927 | 123.2712 | -55.2612 | -46.4767
5075.7656 | 123.2849 | -68.248 | 54.9179 | -0.16426 | -0.011634 | -0.026511 | 0.0062656 | -0.0091089 | -0.0084273 | -0.0050074 | 0.004578 | 0.2655 | -0.32501 | 55.0507 | 54.8538 | 54.8172 | 54.9728 | 55.0369 | 55.0095 | 8.4869 | 67.923 | -54.6524 | 68.2526 | 123.2986 | -0.064087 | 76.7349 | 0.091552 | 0.32959 | 123.2208 | 123.2849 | 123.1018 | 68.5135 | 68.2526 | 123.2574 | 123.0652 | 76.7349 | 68.5135 | 68.2526 | 123.0652 | 123.1018 | 123.2574 | -55.2429 | -46.431
5076.7656 | 123.2895 | -68.2388 | 54.9362 | 0.48424 | -0.0097114 | -0.029074 | 0.0032748 | -0.0091089 | -0.0088547 | -0.001803 | 0.013733 | 0.33417 | -0.28381 | 55.0507 | 54.8401 | 54.8218 | 54.9866 | 55.0186 | 55.0323 | 8.4869 | 67.955 | -54.6021 | 68.2526 | 123.2895 | -0.09613 | 76.7258 | 0.096131 | 0.29755 | 123.2254 | 123.2574 | 123.0789 | 68.573 | 68.2526 | 123.2712 | 123.0606 | 76.7258 | 68.573 | 68.2526 | 123.0606 | 123.0789 | 123.2712 | -55.22 | -46.4493
5077.7812 | 123.3078 | -68.2388 | 54.9225 | -0.21767 | -0.011634 | -0.02352 | 0.0017794 | -0.010604 | -0.0067185 | -0.0030848 | 0.045776 | 0.24261 | -0.28381 | 55.0873 | 54.776 | 54.8447 | 54.9408 | 55.0598 | 54.9911 | 8.4961 | 67.955 | -54.6799 | 68.2846 | 123.3261 | -0.14648 | 76.7349 | 0.068665 | 0.32959 | 123.1796 | 123.2986 | 123.0148 | 68.4814 | 68.2846 | 123.23 | 123.0835 | 76.7349 | 68.4814 | 68.2846 | 123.0835 | 123.0148 | 123.23 | -55.2063 | -46.4264
5078.7812 | 123.3856 | -68.1931 | 54.8767 | -0.41603 | -0.010993 | -0.029501 | -0.00035676 | -0.011672 | -0.0071457 | -0.0043664 | 0.022888 | 0.21973 | -0.28381 | 55.1285 | 54.9362 | 54.9362 | 54.8172 | 55.1285 | 54.982 | 8.4961 | 67.9092 | -54.657 | 68.2159 | 123.3215 | 0.059509 | 76.6891 | 0.10529 | 0.3067 | 123.0103 | 123.3215 | 123.1293 | 68.4128 | 68.2159 | 123.175 | 123.1293 | 76.6891 | 68.4128 | 68.2159 | 123.1293 | 123.1293 | 123.175 | -55.1605 | -46.3806
5079.7812 | 123.3765 | -68.1931 | 54.9133 | -0.17952 | -0.011207 | -0.03057 | 0.0011386 | -0.013809 | -0.0060775 | -0.0024438 | 0.073242 | 0.21973 | -0.29755 | 55.1422 | 54.9088 | 54.9042 | 54.8538 | 55.1376 | 54.9591 | 8.4869 | 67.8955 | -54.6936 | 68.2663 | 123.3353 | -0.004578 | 76.68 | 0.045776 | 0.37079 | 123.0469 | 123.3307 | 123.1018 | 68.4128 | 68.2663 | 123.1522 | 123.0972 | 76.68 | 68.4128 | 68.2663 | 123.0972 | 123.1018 | 123.1522 | -55.2109 | -46.4264
5080.7812 | 123.4131 | -68.1931 | 54.9088 | 0.056992 | -0.015052 | -0.027365 | 0.0015658 | -0.011245 | -0.0067185 | -0.0026574 | 0.07782 | 0.20599 | -0.32044 | 55.1331 | 54.9408 | 54.9042 | 54.8126 | 55.1422 | 54.9225 | 8.4915 | 67.8726 | -54.7028 | 68.2709 | 123.3261 | 0.032044 | 76.6846 | 0.013733 | 0.39826 | 123.0057 | 123.3353 | 123.1338 | 68.399 | 68.2709 | 123.1155 | 123.0972 | 76.6846 | 68.399 | 68.2709 | 123.0972 | 123.1338 | 123.1155 | -55.2292 | -46.4172
5081.7812 | 123.4131 | -68.2251 | 54.8584 | -0.04219 | -0.013557 | -0.032706 | -0.00057036 | -0.0086817 | -0.0067185 | -0.0022302 | 0.082397 | 0.19684 | -0.29755 | 55.1102 | 54.8767 | 54.9225 | 54.7852 | 55.1239 | 54.9179 | 8.4915 | 67.9276 | -54.6616 | 68.3075 | 123.3353 | 0.018311 | 76.7166 | 0.05951 | 0.37994 | 123.0103 | 123.349 | 123.1018 | 68.4219 | 68.3075 | 123.143 | 123.1476 | 76.7166 | 68.4219 | 68.3075 | 123.1476 | 123.1018 | 123.143 | -55.1559 | -46.3669
5082.7656 | 123.3673 | -68.2068 | 54.9133 | -0.17952 | -0.014411 | -0.02822 | 0.0047702 | -0.014022 | -0.0069321 | -0.0026574 | 0.073242 | 0.21515 | -0.29755 | 55.1422 | 54.9225 | 54.8996 | 54.863 | 55.1193 | 54.95 | 8.4869 | 67.9092 | -54.6982 | 68.28 | 123.349 | 0.009155 | 76.6937 | 0.036621 | 0.37079 | 123.0698 | 123.3261 | 123.1293 | 68.4219 | 68.28 | 123.1567 | 123.1064 | 76.6937 | 68.4219 | 68.28 | 123.1064 | 123.1293 | 123.1567 | -55.2109 | -46.4264
5083.7656 | 123.3765 | -68.1976 | 54.9179 | -0.149 | -0.015266 | -0.026511 | 0.004343 | -0.012313 | -0.0084273 | -0.0028712 | 0.068665 | 0.20599 | -0.32044 | 55.1651 | 54.9316 | 54.8996 | 54.8355 | 55.1331 | 54.9637 | 8.4915 | 67.8772 | -54.7119 | 68.2663 | 123.3627 | 0.013733 | 76.6891 | 0.045776 | 0.3891 | 123.0331 | 123.3307 | 123.1293 | 68.4036 | 68.2663 | 123.1613 | 123.0972 | 76.6891 | 68.4036 | 68.2663 | 123.0972 | 123.1293 | 123.1613 | -55.2383 | -46.4264
5084.7656 | 123.3719 | -68.2388 | 54.863 | 0.14854 | -0.010779 | -0.030783 | 0.001993 | -0.014449 | -0.0086411 | -0.0026574 | -0.018311 | 0.21057 | -0.32044 | 55.1102 | 54.8813 | 54.8538 | 54.8172 | 55.0644 | 54.9637 | 8.4961 | 67.9184 | -54.6524 | 68.2205 | 123.349 | 0.018311 | 76.7349 | 0.10071 | 0.30212 | 123.056 | 123.3032 | 123.1201 | 68.4494 | 68.2205 | 123.2025 | 123.0927 | 76.7349 | 68.4494 | 68.2205 | 123.0927 | 123.1201 | 123.2025 | -55.1834 | -46.3669
5085.7812 | 123.381 | -68.2343 | 54.8721 | 0.018845 | -0.012275 | -0.028433 | 0.003702 | -0.014236 | -0.0047957 | -0.0043664 | -0.004578 | 0.19226 | -0.32501 | 55.1102 | 54.9042 | 54.8813 | 54.7897 | 55.0873 | 54.9316 | 8.4915 | 67.9092 | -54.6799 | 68.2297 | 123.3444 | 0.032044 | 76.7258 | 0.05951 | 0.32043 | 123.024 | 123.3215 | 123.1384 | 68.4265 | 68.2297 | 123.1659 | 123.1155 | 76.7258 | 68.4265 | 68.2297 | 123.1155 | 123.1384 | 123.1659 | -55.1971 | -46.3806
5086.7812 | 123.4085 | -68.2205 | 54.863 | -0.011673 | -0.012061 | -0.030356 | 0.00028404 | -0.011459 | -0.0065047 | -0.0032984 | 0.022888 | 0.20599 | -0.31128 | 55.1422 | 54.9362 | 54.8996 | 54.7852 | 55.1102 | 54.9408 | 8.4961 | 67.9092 | -54.657 | 68.2434 | 123.3627 | 0.073242 | 76.7166 | 0.07782 | 0.33417 | 123.0057 | 123.3307 | 123.1567 | 68.4265 | 68.2434 | 123.1613 | 123.1201 | 76.7166 | 68.4265 | 68.2434 | 123.1201 | 123.1567 | 123.1613 | -55.1743 | -46.3669
5087.7812 | 123.3902 | -68.2297 | 54.8538 | 0.011215 | -0.011207 | -0.030783 | 7.0444e-05 | -0.013809 | -0.0075729 | -0.0047938 | 0.004578 | 0.16937 | -0.33875 | 55.1422 | 54.9042 | 54.8859 | 54.7897 | 55.1102 | 54.9362 | 8.4961 | 67.8909 | -54.6844 | 68.2343 | 123.3719 | 0.050354 | 76.7258 | 0.082397 | 0.34332 | 123.0194 | 123.3398 | 123.1338 | 68.399 | 68.2343 | 123.1659 | 123.1155 | 76.7258 | 68.399 | 68.2343 | 123.1155 | 123.1338 | 123.1659 | -55.1926 | -46.3577
5088.7812 | 123.3948 | -68.1931 | 54.8767 | 0.056992 | -0.012702 | -0.02822 | -0.00014316 | -0.012527 | -0.0065047 | -0.0043664 | -0.027466 | 0.19684 | -0.34332 | 55.1376 | 54.7302 | 54.8813 | 54.8035 | 55.0964 | 54.9362 | 8.4824 | 67.8497 | -54.6799 | 68.1656 | 123.3307 | -0.14648 | 76.6754 | 0.059509 | 0.31586 | 122.9965 | 123.2895 | 122.9233 | 68.3899 | 68.1656 | 123.1293 | 123.0743 | 76.6754 | 68.3899 | 68.1656 | 123.0743 | 122.9233 | 123.1293 | -55.22 | -46.3943
5089.7656 | 123.4177 | -68.1931 | 54.8721 | -0.11085 | -0.010779 | -0.029501 | -0.0016386 | -0.014663 | -0.0050095 | -0.0037256 | 0.045776 | 0.21057 | -0.31586 | 55.1788 | 54.7714 | 54.9179 | 54.7806 | 55.1559 | 54.9316 | 8.4869 | 67.8772 | -54.6616 | 68.2388 | 123.3719 | -0.10071 | 76.68 | 0.05951 | 0.36163 | 122.9736 | 123.349 | 122.9645 | 68.4036 | 68.2388 | 123.1247 | 123.111 | 76.68 | 68.4036 | 68.2388 | 123.111 | 122.9645 | 123.1247 | -55.188 | -46.3852
5090.7656 | 123.4177 | -68.2068 | 54.8721 | -0.026932 | -0.010993 | -0.028433 | -0.0016386 | -0.013809 | -0.0065047 | -0.0028712 | 0.041199 | 0.20142 | -0.31586 | 55.1926 | 54.7897 | 54.9271 | 54.7714 | 55.1376 | 54.9362 | 8.4961 | 67.8909 | -54.6707 | 68.248 | 123.3994 | -0.082397 | 76.7029 | 0.064087 | 0.35706 | 122.9782 | 123.3444 | 122.9965 | 68.4082 | 68.248 | 123.143 | 123.1338 | 76.7029 | 68.4082 | 68.248 | 123.1338 | 122.9965 | 123.143 | -55.188 | -46.376
5091.7812 | 123.3856 | -68.2251 | 54.8767 | 0.049362 | -0.010566 | -0.028433 | 7.0444e-05 | -0.013809 | -0.0045821 | -0.0026574 | -0.018311 | 0.18768 | -0.3479 | 55.1193 | 54.7394 | 54.8813 | 54.7943 | 55.0827 | 54.95 | 8.4915 | 67.8772 | -54.689 | 68.2068 | 123.3444 | -0.13733 | 76.7166 | 0.073242 | 0.32959 | 123.0194 | 123.3078 | 122.9645 | 68.4128 | 68.2068 | 123.175 | 123.1064 | 76.7166 | 68.4128 | 68.2068 | 123.1064 | 122.9645 | 123.175 | -55.2246 | -46.3852
5092.7812 | 123.381 | -68.1931 | 54.8721 | 0.13329 | -0.010566 | -0.025656 | 0.0024202 | -0.013595 | -0.0077865 | -0.0037256 | -0.032043 | 0.16479 | -0.3479 | 55.101 | 54.7028 | 54.8538 | 54.776 | 55.0461 | 54.9316 | 8.4869 | 67.8452 | -54.7073 | 68.161 | 123.2941 | -0.16937 | 76.68 | 0.05951 | 0.31586 | 122.9691 | 123.2391 | 122.8958 | 68.3578 | 68.161 | 123.1247 | 123.0469 | 76.68 | 68.3578 | 68.161 | 123.0469 | 122.8958 | 123.1247 | -55.22 | -46.3852
5093.7812 | 123.3673 | -68.2205 | 54.8676 | 0.10277 | -0.011634 | -0.024588 | 0.00028404 | -0.011245 | -0.0060775 | -0.0032984 | -0.032043 | 0.16937 | -0.33417 | 55.0781 | 54.7119 | 54.863 | 54.8355 | 55.0552 | 54.9179 | 8.4915 | 67.8864 | -54.6982 | 68.1885 | 123.2986 | -0.15564 | 76.712 | 0.050354 | 0.30212 | 123.056 | 123.2758 | 122.9324 | 68.3899 | 68.1885 | 123.1384 | 123.0835 | 76.712 | 68.3899 | 68.1885 | 123.0835 | 122.9324 | 123.1384 | -55.2017 | -46.376
5094.7812 | 123.3582 | -68.1976 | 54.8584 | 0.19432 | -0.012275 | -0.024588 | 0.0024202 | -0.012527 | -0.0069321 | -0.0015894 | -0.032043 | 0.17853 | -0.35706 | 55.1056 | 54.7211 | 54.8538 | 54.7989 | 55.0507 | 54.9271 | 8.4915 | 67.8406 | -54.6799 | 68.1656 | 123.3032 | -0.13733 | 76.6891 | 0.068665 | 0.32501 | 122.9965 | 123.2483 | 122.9187 | 68.3762 | 68.1656 | 123.1247 | 123.0515 | 76.6891 | 68.3762 | 68.1656 | 123.0515 | 122.9187 | 123.1247 | -55.2155 | -46.3669
5095.7812 | 123.3673 | -68.2114 | 54.8538 | 0.1638 | -0.011848 | -0.026511 | 0.00092504 | -0.012313 | -0.0050095 | -0.0024438 | -0.027466 | 0.16479 | -0.3479 | 55.1193 | 54.8859 | 54.8538 | 54.7897 | 55.0461 | 54.9225 | 8.5007 | 67.8635 | -54.689 | 68.1839 | 123.3307 | 0.032043 | 76.712 | 0.068664 | 0.32043 | 123.0011 | 123.2574 | 123.0972 | 68.3762 | 68.1839 | 123.1338 | 123.0652 | 76.712 | 68.3762 | 68.1839 | 123.0652 | 123.0972 | 123.1338 | -55.2017 | -46.3531
5096.7656 | 123.3948 | -68.2068 | 54.8584 | 0.11803 | -0.011207 | -0.02822 | 0.00071144 | -0.012954 | -0.0056503 | -0.0043664 | -0.013733 | 0.19226 | -0.32959 | 55.1193 | 54.9179 | 54.8721 | 54.8126 | 55.0644 | 54.9362 | 8.4915 | 67.8772 | -54.6661 | 68.1931 | 123.3261 | 0.05951 | 76.6983 | 0.07782 | 0.31586 | 123.0194 | 123.2712 | 123.1247 | 68.399 | 68.1931 | 123.143 | 123.0789 | 76.6983 | 68.399 | 68.1931 | 123.0789 | 123.1247 | 123.143 | -55.188 | -46.3669
5097.7656 | 123.3765 | -68.2068 | 54.8538 | -0.11848 | -0.012061 | -0.02587 | 0.0013522 | -0.013381 | -0.0024459 | -0.003512 | -0.045776 | 0.18768 | -0.30212 | 55.0964 | 54.895 | 54.863 | 54.8035 | 55.0461 | 54.8996 | 8.4915 | 67.9047 | -54.6661 | 68.161 | 123.3032 | 0.041199 | 76.6983 | 0.045776 | 0.25635 | 123.0103 | 123.2529 | 123.1018 | 68.3945 | 68.161 | 123.1064 | 123.0698 | 76.6983 | 68.3945 | 68.161 | 123.0698 | 123.1018 | 123.1064 | -55.1559 | -46.3623
5098.7812 | 123.3902 | -68.2068 | 54.8447 | 0.20195 | -0.012916 | -0.027152 | 0.00028404 | -0.010177 | -0.0041549 | -0.0032984 | -0.009155 | 0.1236 | -0.37537 | 55.1331 | 54.9042 | 54.8904 | 54.7256 | 55.0552 | 54.9088 | 8.4915 | 67.8314 | -54.7211 | 68.1976 | 123.3398 | 0.059509 | 76.6983 | 0.064086 | 0.36621 | 122.9324 | 123.262 | 123.111 | 68.3304 | 68.1976 | 123.1155 | 123.0972 | 76.6983 | 68.3304 | 68.1976 | 123.0972 | 123.111 | 123.1155 | -55.22 | -46.3531
5099.7812 | 123.4085 | -68.2343 | 54.8538 | 0.20958 | -0.01142 | -0.024588 | 0.0024202 | -0.010177 | -0.0065047 | -0.0039392 | 0.009155 | 0.14191 | -0.37079 | 55.1376 | 54.9179 | 54.895 | 54.7165 | 55.0644 | 54.8859 | 8.4869 | 67.8635 | -54.7119 | 68.2434 | 123.3719 | 0.064087 | 76.7212 | 0.032043 | 0.37994 | 122.9507 | 123.2986 | 123.1522 | 68.3762 | 68.2434 | 123.1201 | 123.1293 | 76.7212 | 68.3762 | 68.2434 | 123.1293 | 123.1522 | 123.1201 | -55.2246 | -46.3669
5100.7812 | 123.3719 | -68.2205 | 54.8218 | 0.21721 | -0.010352 | -0.029501 | 0.0028476 | -0.011672 | -0.0052231 | -0.0022302 | -0.027466 | 0.13275 | -0.3891 | 55.1331 | 54.8996 | 54.8904 | 54.7394 | 55.0644 | 54.8904 | 8.4961 | 67.8314 | -54.689 | 68.1931 | 123.3536 | 0.07782 | 76.7166 | 0.068665 | 0.36163 | 122.9599 | 123.2849 | 123.1201 | 68.3533 | 68.1931 | 123.111 | 123.111 | 76.7166 | 68.3533 | 68.1931 | 123.111 | 123.1201 | 123.111 | -55.2109 | -46.3257
5101.7812 | 123.3719 | -68.2388 | 54.8492 | 0.21721 | -0.010993 | -0.029501 | 0.003702 | -0.0084681 | -0.0060775 | -0.00052119 | 0.004578 | 0.13733 | -0.35706 | 55.1331 | 54.9179 | 54.895 | 54.7348 | 55.0644 | 54.895 | 8.4869 | 67.8818 | -54.7119 | 68.2434 | 123.3719 | 0.068665 | 76.7258 | 0.045777 | 0.36163 | 122.9736 | 123.3032 | 123.1567 | 68.3762 | 68.2434 | 123.1339 | 123.1339 | 76.7258 | 68.3762 | 68.2434 | 123.1339 | 123.1567 | 123.1339 | -55.2063 | -46.3623
5102.7656 | 123.3673 | -68.2159 | 54.8584 | 0.10277 | -0.010352 | -0.020956 | 0.0017794 | -0.010177 | -0.0052231 | -0.0028712 | -0.018311 | 0.1831 | -0.33417 | 55.1102 | 54.7211 | 54.8676 | 54.7989 | 55.0323 | 54.9133 | 8.4869 | 67.8818 | -54.6753 | 68.1976 | 123.3261 | -0.13733 | 76.7029 | 0.054932 | 0.31586 | 123.0148 | 123.2483 | 122.937 | 68.399 | 68.1976 | 123.1293 | 123.0835 | 76.7029 | 68.399 | 68.1976 | 123.0835 | 122.937 | 123.1293 | -55.1926 | -46.3715
5103.7656 | 123.3765 | -68.2251 | 54.8767 | 0.15617 | -0.010352 | -0.022879 | 0.002634 | -0.011245 | -0.0054367 | -0.0024438 | -0.036621 | 0.14191 | -0.37079 | 55.1102 | 54.7119 | 54.8813 | 54.7852 | 55.0598 | 54.895 | 8.4824 | 67.8543 | -54.7348 | 68.1885 | 123.3353 | -0.16479 | 76.7075 | 0.018311 | 0.33417 | 123.0103 | 123.2849 | 122.937 | 68.367 | 68.1885 | 123.1201 | 123.1064 | 76.7075 | 68.367 | 68.1885 | 123.1064 | 122.937 | 123.1201 | -55.2475 | -46.3943
5104.7656 | 123.3673 | -68.2159 | 54.863 | 0.18669 | -0.0069342 | -0.026724 | 0.0045566 | -0.010818 | -0.0058639 | -0.0026574 | -0.018311 | 0.15106 | -0.38452 | 55.0919 | 54.7211 | 54.8767 | 54.7623 | 55.0552 | 54.9088 | 8.4869 | 67.8314 | -54.7119 | 68.1976 | 123.3078 | -0.14191 | 76.7029 | 0.045776 | 0.36621 | 122.9782 | 123.2712 | 122.937 | 68.367 | 68.1976 | 123.1247 | 123.0927 | 76.7029 | 68.367 | 68.1976 | 123.0927 | 122.937 | 123.1247 | -55.2475 | -46.376
5105.7812 | 123.4039 | -68.1839 | 54.8584 | 0.14092 | -0.0084296 | -0.023306 | 0.0064792 | -0.010391 | -0.0075729 | -0.0043664 | 0.004578 | 0.13733 | -0.37079 | 55.1239 | 54.8904 | 54.9042 | 54.7211 | 55.0598 | 54.8859 | 8.4869 | 67.8131 | -54.7211 | 68.1885 | 123.3078 | 0.032044 | 76.6708 | 0.027466 | 0.37537 | 122.905 | 123.2437 | 123.0743 | 68.3212 | 68.1885 | 123.0698 | 123.0881 | 76.6708 | 68.3212 | 68.1885 | 123.0881 | 123.0743 | 123.0698 | -55.2292 | -46.3715
5106.7812 | 123.4039 | -68.2022 | 54.8721 | 0.041733 | -0.012275 | -0.027792 | 7.0444e-05 | -0.012954 | -0.0062911 | -0.0020166 | -0.009155 | 0.19684 | -0.33417 | 55.1605 | 54.9316 | 54.9271 | 54.7943 | 55.1056 | 54.9088 | 8.4869 | 67.868 | -54.6753 | 68.1931 | 123.3627 | 0.05951 | 76.6891 | 0.036621 | 0.32501 | 122.9965 | 123.3078 | 123.1338 | 68.399 | 68.1931 | 123.111 | 123.1293 | 76.6891 | 68.399 | 68.1931 | 123.1293 | 123.1338 | 123.111 | -55.2063 | -46.3852
5107.7812 | 123.4451 | -68.2297 | 54.8584 | 0.26299 | -0.0094976 | -0.022879 | 0.0066928 | -0.0091089 | -0.0065047 | -0.0041528 | 0.009155 | 0.14648 | -0.37079 | 55.1331 | 54.9179 | 54.9042 | 54.538 | 54.8721 | 54.8401 | 8.4961 | 67.8589 | -54.7119 | 68.2388 | 123.3627 | 0.05951 | 76.7258 | -0.01831 | 0.37994 | 122.7676 | 123.1018 | 123.1476 | 68.3762 | 68.2388 | 123.0698 | 123.1338 | 76.7258 | 68.3762 | 68.2388 | 123.1338 | 123.1476 | 123.0698 | -55.2292 | -46.3623
5108.7812 | 123.4039 | -68.2205 | 54.8218 | 0.26299 | -0.007575 | -0.027152 | 0.0069064 | -0.010604 | -0.0054367 | -0.0041528 | 0 | 0.16479 | -0.37994 | 55.1468 | 54.8904 | 54.8996 | 54.7577 | 55.0598 | 54.895 | 8.4961 | 67.8406 | -54.657 | 68.2205 | 123.3673 | 0.068665 | 76.7166 | 0.073243 | 0.37994 | 122.9782 | 123.2803 | 123.111 | 68.3853 | 68.2205 | 123.1155 | 123.1201 | 76.7166 | 68.3853 | 68.2205 | 123.1201 | 123.111 | 123.1155 | -55.2017 | -46.3257
5109.7656 | 123.381 | -68.2251 | 54.8584 | 0.20195 | -0.010139 | -0.022452 | 0.0049838 | -0.0097497 | -0.0054367 | -0.0022302 | 0.018311 | 0.15106 | -0.35706 | 55.1376 | 54.9133 | 54.9133 | 54.744 | 55.0598 | 54.9179 | 8.4915 | 67.868 | -54.7073 | 68.2434 | 123.3627 | 0.054932 | 76.7166 | 0.05951 | 0.37537 | 122.9691 | 123.2849 | 123.1384 | 68.3762 | 68.2434 | 123.143 | 123.1384 | 76.7166 | 68.3762 | 68.2434 | 123.1384 | 123.1384 | 123.143 | -55.2155 | -46.3669
5110.7656 | 123.4131 | -68.2205 | 54.8126 | 0.041733 | -0.0086432 | -0.022665 | 0.0062656 | -0.0086817 | -0.0067185 | -0.0024438 | 0.036621 | 0.12817 | -0.37537 | 55.1468 | 54.9225 | 54.9088 | 54.7394 | 55.0598 | 54.8996 | 8.4869 | 67.8452 | -54.6844 | 68.2571 | 123.3673 | 0.10986 | 76.7075 | 0.086975 | 0.41199 | 122.9599 | 123.2803 | 123.143 | 68.3487 | 68.2571 | 123.1201 | 123.1293 | 76.7075 | 68.3487 | 68.2571 | 123.1293 | 123.143 | 123.1201 | -55.188 | -46.3257
5111.7656 | 123.3994 | -68.2114 | 54.8218 | 0.27061 | -0.010566 | -0.026724 | 0.0064792 | -0.0091089 | -0.0052231 | -0.0030848 | 0.009155 | 0.1236 | -0.3891 | 55.1605 | 54.9042 | 54.95 | 54.7394 | 55.0644 | 54.8904 | 8.4869 | 67.8223 | -54.6982 | 68.2205 | 123.3719 | 0.082398 | 76.6983 | 0.068665 | 0.39825 | 122.9507 | 123.2758 | 123.1155 | 68.335 | 68.2205 | 123.1018 | 123.1613 | 76.6983 | 68.335 | 68.2205 | 123.1613 | 123.1155 | 123.1018 | -55.2109 | -46.3348
5112.7812 | 123.3032 | -68.2846 | 54.8676 | 0.19432 | -0.0071478 | -0.022452 | 0.0073336 | -0.0078271 | -0.0069321 | -9.3992e-05 | -0.041199 | 0.20142 | -0.38452 | 55.0415 | 54.808 | 54.808 | 54.8767 | 54.9591 | 54.9408 | 8.4961 | 67.9001 | -54.6661 | 68.2434 | 123.3261 | -0.05951 | 76.7807 | 0.073242 | 0.34332 | 123.1613 | 123.2437 | 123.0927 | 68.486 | 68.2434 | 123.2254 | 123.0927 | 76.7807 | 68.486 | 68.2434 | 123.0927 | 123.0927 | 123.2254 | -55.2521 | -46.3715
5113.7812 | 123.2849 | -68.2846 | 54.8813 | -0.019302 | -0.0088568 | -0.019461 | 0.0092562 | -0.0076135 | -0.0080001 | -0.0015894 | -0.041199 | 0.21515 | -0.38452 | 55.0552 | 54.8309 | 54.7989 | 54.8767 | 54.9545 | 54.9728 | 8.5007 | 67.9001 | -54.6661 | 68.2434 | 123.3398 | -0.050354 | 76.7853 | 0.091552 | 0.34332 | 123.1613 | 123.2391 | 123.1155 | 68.4998 | 68.2434 | 123.2574 | 123.0835 | 76.7853 | 68.4998 | 68.2434 | 123.0835 | 123.1155 | 123.2574 | -55.2658 | -46.3806
5114.7812 | 123.317 | -68.2114 | 54.8904 | 0.14854 | -0.013129 | -0.029501 | 0.0013522 | -0.0088953 | -0.0071457 | -0.0024438 | -0.050354 | 0.16479 | -0.3479 | 55.0781 | 54.8904 | 54.8767 | 54.808 | 55.0507 | 54.9271 | 8.4869 | 67.8635 | -54.7256 | 68.161 | 123.2895 | 0 | 76.6983 | 0.036621 | 0.29755 | 123.0194 | 123.262 | 123.1018 | 68.3762 | 68.161 | 123.1384 | 123.0881 | 76.6983 | 68.3762 | 68.161 | 123.0881 | 123.1018 | 123.1384 | -55.2383 | -46.4035
5115.7812 | 123.2941 | -68.2709 | 54.8676 | 0.21721 | -0.0084296 | -0.02587 | 0.0086154 | -0.0080407 | -0.0039413 | -0.0013758 | -0.032043 | 0.21057 | -0.37994 | 55.0461 | 54.6524 | 54.8035 | 54.8767 | 54.9683 | 54.9591 | 8.4915 | 67.8909 | -54.657 | 68.2388 | 123.317 | -0.21515 | 76.7624 | 0.091552 | 0.3479 | 123.1476 | 123.2391 | 122.9233 | 68.4814 | 68.2388 | 123.23 | 123.0743 | 76.7624 | 68.4814 | 68.2388 | 123.0743 | 122.9233 | 123.23 | -55.2475 | -46.376
5116.7656 | 123.4039 | -68.2434 | 54.8447 | 0.23247 | -0.0062934 | -0.022665 | 0.0069064 | -0.0082545 | -0.0056503 | -0.001803 | 0.013733 | 0.15564 | -0.37994 | 55.1193 | 54.7394 | 54.9179 | 54.7485 | 55.0552 | 54.9179 | 8.5007 | 67.8635 | -54.689 | 68.2571 | 123.3627 | -0.10529 | 76.7441 | 0.073242 | 0.39368 | 122.9919 | 123.2986 | 122.9828 | 68.399 | 68.2571 | 123.1613 | 123.1613 | 76.7441 | 68.399 | 68.2571 | 123.1613 | 122.9828 | 123.1613 | -55.2246 | -46.344
5117.7656 | 123.3948 | -68.248 | 54.8538 | 0.27061 | -0.0080024 | -0.023306 | 0.0075472 | -0.0086817 | -0.0067185 | -0.0011622 | -0.009155 | 0.18768 | -0.37537 | 55.0964 | 54.7165 | 54.8859 | 54.8035 | 55.014 | 54.9179 | 8.4915 | 67.8726 | -54.6661 | 68.2388 | 123.3444 | -0.13733 | 76.7395 | 0.064087 | 0.36621 | 123.0515 | 123.262 | 122.9645 | 68.4357 | 68.2388 | 123.1659 | 123.1338 | 76.7395 | 68.4357 | 68.2388 | 123.1338 | 122.9645 | 123.1659 | -55.2292 | -46.3623
5118.7812 | 123.317 | -68.248 | 54.8767 | 0.26299 | -0.0067206 | -0.016684 | 0.00712 | -0.0069727 | -0.0050095 | -0.0030848 | -0.045776 | 0.20599 | -0.38452 | 55.0507 | 54.6478 | 54.8355 | 54.8584 | 54.9683 | 54.9408 | 8.4824 | 67.8635 | -54.6707 | 68.2022 | 123.2986 | -0.22888 | 76.7303 | 0.064087 | 0.33875 | 123.1064 | 123.2162 | 122.8958 | 68.454 | 68.2022 | 123.1888 | 123.0835 | 76.7303 | 68.454 | 68.2022 | 123.0835 | 122.8958 | 123.1888 | -55.2612 | -46.3943
5119.7812 | 123.2986 | -68.2343 | 54.9316 | -0.16426 | -0.0086432 | -0.026083 | 0.0060518 | -0.0121 | -0.0062911 | -0.003512 | 0 | 0.27466 | -0.30212 | 55.0598 | 54.6844 | 54.8355 | 55.0003 | 55.0232 | 55.0003 | 8.4869 | 67.9321 | -54.657 | 68.2343 | 123.2941 | -0.24719 | 76.7212 | 0.068664 | 0.30212 | 123.2346 | 123.2574 | 122.9187 | 68.5089 | 68.2343 | 123.2346 | 123.0698 | 76.7212 | 68.5089 | 68.2343 | 123.0698 | 122.9187 | 123.2346 | -55.2338 | -46.4447
5120.7656 | 123.3032 | -68.2343 | 54.9088 | 0.026474 | -0.010139 | -0.022665 | 0.0096834 | -0.0073999 | -0.0084273 | -0.0041528 | 0.036621 | 0.21973 | -0.35706 | 55.0552 | 54.6707 | 54.8035 | 54.9088 | 54.9911 | 54.9866 | 8.4824 | 67.8772 | -54.689 | 68.2709 | 123.2895 | -0.23804 | 76.7166 | 0.07782 | 0.39368 | 123.143 | 123.2254 | 122.905 | 68.454 | 68.2709 | 123.2208 | 123.0377 | 76.7166 | 68.454 | 68.2709 | 123.0377 | 122.905 | 123.2208 | -55.2658 | -46.4264
5121.7812 | 123.2986 | -68.2846 | 54.8721 | 0.49187 | -0.0071478 | -0.021811 | 0.0077608 | -0.0084681 | -0.0065047 | -0.0020166 | 0.018311 | 0.20142 | -0.37537 | 55.0232 | 54.6478 | 54.8035 | 54.9088 | 54.9637 | 54.9866 | 8.4915 | 67.9092 | -54.6707 | 68.3029 | 123.3078 | -0.2243 | 76.7761 | 0.11444 | 0.39368 | 123.1934 | 123.2483 | 122.9324 | 68.486 | 68.3029 | 123.2712 | 123.0881 | 76.7761 | 68.486 | 68.3029 | 123.0881 | 122.9324 | 123.2712 | -55.2475 | -46.3806
5122.7812 | 123.2986 | -68.28 | 54.8676 | 0.1638 | -0.007575 | -0.023947 | 0.0098972 | -0.0091089 | -0.0073593 | -0.001803 | -0.054932 | 0.2243 | -0.37994 | 55.0919 | 54.689 | 54.776 | 54.9683 | 54.9957 | 54.9957 | 8.4915 | 67.9001 | -54.6433 | 68.2251 | 123.3719 | -0.17853 | 76.7715 | 0.12817 | 0.32501 | 123.2483 | 123.2758 | 122.9691 | 68.5043 | 68.2251 | 123.2758 | 123.056 | 76.7715 | 68.5043 | 68.2251 | 123.056 | 122.9691 | 123.2758 | -55.2475 | -46.376
5123.7656 | 123.3398 | -68.2709 | 54.8584 | 0.21721 | -0.008216 | -0.022025 | 0.0058382 | -0.0069727 | -0.0039413 | -0.001803 | -0.032043 | 0.19684 | -0.3891 | 55.0323 | 54.6661 | 54.8447 | 54.8355 | 54.9957 | 54.9683 | 8.4869 | 67.8818 | -54.6616 | 68.2388 | 123.3032 | -0.19226 | 76.7578 | 0.10986 | 0.35706 | 123.1064 | 123.2666 | 122.937 | 68.4677 | 68.2388 | 123.2391 | 123.1155 | 76.7578 | 68.4677 | 68.2388 | 123.1155 | 122.937 | 123.2391 | -55.2475 | -46.3715
5124.7812 | 123.3856 | -68.2159 | 54.8492 | 0.049362 | -0.013557 | -0.026297 | -0.0027066 | -0.0095361 | -0.0045821 | 0.00033321 | -0.032043 | 0.17853 | -0.34332 | 55.0781 | 54.7394 | 54.8996 | 54.8447 | 55.0873 | 54.9545 | 8.4915 | 67.8726 | -54.6707 | 68.1839 | 123.2941 | -0.10986 | 76.7075 | 0.10529 | 0.31128 | 123.0606 | 123.3032 | 122.9553 | 68.3945 | 68.1839 | 123.1705 | 123.1155 | 76.7075 | 68.3945 | 68.1839 | 123.1155 | 122.9553 | 123.1705 | -55.1926 | -46.3577
5125.7812 | 123.3765 | -68.2068 | 54.8584 | 0.24773 | -0.0097114 | -0.02587 | 0.00071144 | -0.010604 | -0.0060775 | 0.00033321 | -0.018311 | 0.13275 | -0.37079 | 55.0919 | 54.7073 | 54.8904 | 54.7577 | 55.0781 | 54.8996 | 8.4961 | 67.836 | -54.7256 | 68.1885 | 123.2986 | -0.15106 | 76.7029 | 0.041199 | 0.35248 | 122.9645 | 123.2849 | 122.9141 | 68.3395 | 68.1885 | 123.1064 | 123.0972 | 76.7029 | 68.3395 | 68.1885 | 123.0972 | 122.9141 | 123.1064 | -55.2292 | -46.3623
5126.7812 | 123.2895 | -68.2434 | 54.895 | 0.1104 | -0.007575 | -0.024802 | 0.0090426 | -0.0078271 | -0.0067185 | -0.0032984 | 0.022888 | 0.2243 | -0.34332 | 55.0507 | 54.6478 | 54.7989 | 54.9316 | 54.9866 | 54.9683 | 8.4824 | 67.9001 | -54.6707 | 68.2663 | 123.2941 | -0.24719 | 76.7258 | 0.073242 | 0.36621 | 123.175 | 123.23 | 122.8912 | 68.4677 | 68.2663 | 123.2117 | 123.0423 | 76.7258 | 68.4677 | 68.2663 | 123.0423 | 122.8912 | 123.2117 | -55.2383 | -46.4127
5127.7812 | 123.3032 | -68.2343 | 54.9133 | 0.049362 | -0.0067206 | -0.019675 | 0.0077608 | -0.0071863 | -0.0065047 | -0.0030848 | 0.032043 | 0.23346 | -0.33417 | 55.069 | 54.6982 | 54.8309 | 54.9133 | 54.9911 | 54.9911 | 8.4778 | 67.9001 | -54.6799 | 68.2663 | 123.3032 | -0.21515 | 76.712 | 0.07782 | 0.36621 | 123.1476 | 123.2254 | 122.9324 | 68.4677 | 68.2663 | 123.2254 | 123.0652 | 76.712 | 68.4677 | 68.2663 | 123.0652 | 122.9324 | 123.2254 | -55.2475 | -46.4355
5128.7812 | 123.2666 | -68.2571 | 54.9042 | 0.14092 | -0.009284 | -0.02117 | 0.0092562 | -0.0073999 | -0.0084273 | -0.0030848 | 0.009155 | 0.22888 | -0.35248 | 55.0278 | 54.8035 | 54.7852 | 54.9271 | 54.9683 | 54.9911 | 8.4778 | 67.9047 | -54.6753 | 68.2663 | 123.2849 | -0.10071 | 76.7349 | 0.086975 | 0.36163 | 123.1842 | 123.2254 | 123.0606 | 68.486 | 68.2663 | 123.2483 | 123.0423 | 76.7349 | 68.486 | 68.2663 | 123.0423 | 123.0606 | 123.2483 | -55.2567 | -46.4264
5129.7812 | 123.3032 | -68.2617 | 54.895 | 0.034104 | -0.006507 | -0.022665 | 0.0075472 | -0.0071863 | -0.0082137 | -0.003512 | 0.009155 | 0.24261 | -0.35248 | 55.0461 | 54.8218 | 54.808 | 54.9362 | 54.9866 | 55.0095 | 8.4824 | 67.9092 | -54.6524 | 68.2709 | 123.3078 | -0.073243 | 76.7441 | 0.11444 | 0.36163 | 123.1979 | 123.2483 | 123.0835 | 68.5043 | 68.2709 | 123.2712 | 123.0698 | 76.7441 | 68.5043 | 68.2709 | 123.0698 | 123.0835 | 123.2712 | -55.2475 | -46.4127
5130.7656 | 123.2941 | -68.2709 | 54.9088 | 0.20195 | -0.0088568 | -0.017539 | 0.0069064 | -0.0037683 | -0.0011643 | -0.0026574 | -0.082397 | 0.21515 | -0.39368 | 55.0873 | 55.0507 | 54.8447 | 54.982 | 54.9591 | 55.0003 | 8.4961 | 67.8772 | -54.6936 | 68.1885 | 123.3582 | 0.14191 | 76.767 | 0.091553 | 0.31128 | 123.2529 | 123.23 | 123.3215 | 68.486 | 68.1885 | 123.2712 | 123.1155 | 76.767 | 68.486 | 68.1885 | 123.1155 | 123.3215 | 123.2712 | -55.3024 | -46.4127
5131.7656 | 123.2849 | -68.2617 | 54.8767 | 0.2401 | -0.0077888 | -0.02352 | 0.00712 | -0.0061181 | -0.0052231 | -0.00094839 | -0.050354 | 0.22888 | -0.36163 | 55.0003 | 54.7989 | 54.7852 | 54.9271 | 54.9316 | 55.014 | 8.4915 | 67.9001 | -54.6478 | 68.2114 | 123.262 | -0.07782 | 76.7532 | 0.13733 | 0.31128 | 123.1888 | 123.1934 | 123.0606 | 68.4906 | 68.2114 | 123.2758 | 123.0469 | 76.7532 | 68.4906 | 68.2114 | 123.0469 | 123.0606 | 123.2758 | -55.2383 | -46.3852
5132.7656 | 123.3261 | -68.2251 | 54.9042 | -0.10323 | -0.0094976 | -0.024802 | 0.0049838 | -0.0046229 | -0.0047957 | -0.0032984 | 0.045776 | 0.29297 | -0.32501 | 55.0873 | 54.8996 | 54.8447 | 54.9316 | 55.0552 | 55.014 | 8.4824 | 67.9001 | -54.6112 | 68.2709 | 123.3124 | -0.004578 | 76.7075 | 0.10986 | 0.37079 | 123.1567 | 123.2803 | 123.1247 | 68.5181 | 68.2709 | 123.2391 | 123.0698 | 76.7075 | 68.5181 | 68.2709 | 123.0698 | 123.1247 | 123.2391 | -55.2292 | -46.4218
5133.7812 | 123.3627 | -68.2343 | 54.8676 | 0.17143 | -0.013129 | -0.027365 | -0.001425 | -0.0093225 | -0.0058639 | -0.0024438 | -0.054932 | 0.15564 | -0.34332 | 55.0507 | 54.8996 | 54.8859 | 54.8218 | 55.0369 | 54.95 | 8.4869 | 67.8909 | -54.7119 | 68.1793 | 123.2849 | 0.032043 | 76.7212 | 0.082397 | 0.28839 | 123.056 | 123.2712 | 123.1338 | 68.3899 | 68.1793 | 123.1842 | 123.1201 | 76.7212 | 68.3899 | 68.1793 | 123.1201 | 123.1338 | 123.1842 | -55.2109 | -46.3806
5134.7812 | 123.3261 | -68.2343 | 54.9042 | -0.0040434 | -0.0077888 | -0.022879 | 0.0090426 | -0.0069727 | -0.0058639 | -0.001803 | 0.068665 | 0.24261 | -0.35248 | 55.0781 | 54.863 | 54.8447 | 54.9042 | 55.0369 | 54.9683 | 8.4824 | 67.8818 | -54.6616 | 68.3029 | 123.3124 | -0.041199 | 76.7166 | 0.064087 | 0.42114 | 123.1384 | 123.2712 | 123.0972 | 68.4769 | 68.3029 | 123.2025 | 123.0789 | 76.7166 | 68.4769 | 68.3029 | 123.0789 | 123.0972 | 123.2025 | -55.2567 | -46.4218
5135.7812 | 123.3353 | -68.2388 | 54.8904 | 1.1785 | -0.009284 | -0.023093 | 0.0062656 | -0.0078271 | -0.0037277 | -0.0011622 | 0.068665 | 0.25635 | -0.30212 | 55.0964 | 54.895 | 54.863 | 54.9088 | 55.0369 | 55.0003 | 8.4778 | 67.9367 | -54.6341 | 68.3075 | 123.3353 | 0.004578 | 76.7166 | 0.10986 | 0.37079 | 123.1476 | 123.2758 | 123.1339 | 68.4952 | 68.3075 | 123.2391 | 123.1018 | 76.7166 | 68.4952 | 68.3075 | 123.1018 | 123.1339 | 123.2391 | -55.1926 | -46.4127
5136.7812 | 123.3536 | -68.2617 | 54.9042 | -0.034561 | -0.0097114 | -0.028006 | 0.0081882 | -0.0071863 | -0.0075729 | -0.0037256 | 0.045776 | 0.24261 | -0.31586 | 55.0919 | 54.8859 | 54.7028 | 54.9911 | 55.0735 | 54.9866 | 8.4915 | 67.9459 | -54.6616 | 68.3075 | 123.3536 | -0.018311 | 76.7532 | 0.082397 | 0.36163 | 123.2529 | 123.3353 | 123.1476 | 68.5043 | 68.3075 | 123.2483 | 122.9645 | 76.7532 | 68.5043 | 68.3075 | 122.9645 | 123.1476 | 123.2483 | -55.22 | -46.4127
5137.7656 | 123.2941 | -68.2388 | 54.9133 | 0.064621 | -0.007575 | -0.019675 | 0.0090426 | -0.0052637 | -0.0062911 | -0.0022302 | 0.027466 | 0.24261 | -0.33875 | 55.0644 | 54.8355 | 54.8172 | 54.8996 | 55.0095 | 55.0003 | 8.4915 | 67.9001 | -54.6707 | 68.2663 | 123.3032 | -0.07782 | 76.7303 | 0.086975 | 0.36621 | 123.1384 | 123.2483 | 123.0743 | 68.4814 | 68.2663 | 123.2391 | 123.056 | 76.7303 | 68.4814 | 68.2663 | 123.056 | 123.0743 | 123.2391 | -55.2521 | -46.4218
5138.7656 | 123.3124 | -68.2388 | 54.8904 | 0.034104 | -0.0090704 | -0.021384 | 0.0060518 | -0.0080407 | -0.0065047 | -0.0024438 | 0.036621 | 0.23804 | -0.33875 | 55.0598 | 54.8538 | 54.8355 | 54.9179 | 55.0049 | 55.0186 | 8.4869 | 67.9001 | -54.6524 | 68.2755 | 123.2986 | -0.036621 | 76.7258 | 0.12817 | 0.37537 | 123.1567 | 123.2437 | 123.0927 | 68.4769 | 68.2755 | 123.2574 | 123.0743 | 76.7258 | 68.4769 | 68.2755 | 123.0743 | 123.0927 | 123.2574 | -55.2292 | -46.4035
5139.7656 | 123.2986 | -68.2434 | 54.9271 | -0.19478 | -0.009925 | -0.022025 | 0.003702 | -0.0071863 | -0.0067185 | -0.0032984 | 0 | 0.29755 | -0.3067 | 55.0507 | 54.8538 | 54.8264 | 55.0049 | 55.0415 | 55.0415 | 8.4869 | 67.9367 | -54.6295 | 68.2434 | 123.2941 | -0.073242 | 76.7303 | 0.11444 | 0.3067 | 123.2483 | 123.2849 | 123.0972 | 68.541 | 68.2434 | 123.2849 | 123.0698 | 76.7303 | 68.541 | 68.2434 | 123.0698 | 123.0972 | 123.2849 | -55.2338 | -46.4401
5140.7812 | 123.317 | -68.2388 | 54.9179 | -0.15663 | -0.007575 | -0.025656 | 0.0047702 | -0.0054773 | -0.0035141 | -0.001803 | 0.032043 | 0.27008 | -0.30212 | 55.069 | 54.6753 | 54.8309 | 54.9683 | 55.0461 | 55.0186 | 8.4778 | 67.9367 | -54.6478 | 68.2709 | 123.3078 | -0.24261 | 76.7166 | 0.10071 | 0.33417 | 123.2071 | 123.2849 | 122.9141 | 68.5089 | 68.2709 | 123.2574 | 123.0698 | 76.7166 | 68.5089 | 68.2709 | 123.0698 | 122.9141 | 123.2574 | -55.22 | -46.4401
5141.7812 | 123.3261 | -68.2343 | 54.9179 | -0.12611 | -0.011207 | -0.023093 | 0.0084018 | -0.0056909 | -0.0073593 | -0.0013758 | 0.050354 | 0.2655 | -0.3067 | 55.0873 | 54.8721 | 54.8584 | 54.9408 | 55.0644 | 55.014 | 8.4824 | 67.9276 | -54.6524 | 68.2846 | 123.3215 | -0.045777 | 76.7166 | 0.09613 | 0.35706 | 123.175 | 123.2986 | 123.1064 | 68.4998 | 68.2846 | 123.2483 | 123.0927 | 76.7166 | 68.4998 | 68.2846 | 123.0927 | 123.1064 | 123.2483 | -55.2246 | -46.4355
5142.7812 | 123.3353 | -68.2251 | 54.9179 | -0.12611 | -0.0090704 | -0.025015 | 0.0049838 | -0.0084681 | -0.0071457 | -0.0022302 | 0.041199 | 0.29297 | -0.32501 | 55.0873 | 54.6799 | 54.8584 | 54.9591 | 55.0644 | 55.0323 | 8.4869 | 67.9001 | -54.6249 | 68.2663 | 123.3124 | -0.23804 | 76.712 | 0.11444 | 0.36621 | 123.1842 | 123.2895 | 122.905 | 68.5181 | 68.2663 | 123.2574 | 123.0835 | 76.712 | 68.5181 | 68.2663 | 123.0835 | 122.905 | 123.2574 | -55.2429 | -46.431
5143.7812 | 123.3215 | -68.2571 | 54.9225 | -0.17189 | -0.0090704 | -0.025443 | 0.0056246 | -0.0073999 | -0.0084273 | -0.0024438 | 0.027466 | 0.29755 | -0.33875 | 55.0735 | 54.6753 | 54.8584 | 54.9774 | 55.0507 | 55.0232 | 8.4824 | 67.9184 | -54.6249 | 68.2846 | 123.3307 | -0.24719 | 76.7395 | 0.10071 | 0.36621 | 123.2346 | 123.3078 | 122.9324 | 68.5547 | 68.2846 | 123.2803 | 123.1155 | 76.7395 | 68.5547 | 68.2846 | 123.1155 | 122.9324 | 123.2803 | -55.2612 | -46.4401
5144.7656 | 123.3398 | -68.2526 | 54.9179 | -0.072708 | -0.0084296 | -0.025229 | 0.0051974 | -0.0056909 | -0.0073593 | -0.0032984 | 0.050354 | 0.24261 | -0.32501 | 55.0873 | 54.8538 | 54.9454 | 54.6433 | 55.0369 | 54.9774 | 8.4824 | 67.9276 | -54.6753 | 68.3029 | 123.3398 | -0.064087 | 76.7349 | 0.059509 | 0.37537 | 122.8958 | 123.2895 | 123.1064 | 68.4952 | 68.3029 | 123.23 | 123.1979 | 76.7349 | 68.4952 | 68.3029 | 123.1979 | 123.1064 | 123.23 | -55.2429 | -46.4355
5145.7656 | 123.3353 | -68.248 | 54.8996 | -0.072708 | -0.0084296 | -0.024161 | 0.0056246 | -0.0093225 | -0.0082137 | -0.003512 | 0.054932 | 0.26093 | -0.33875 | 55.0781 | 54.8859 | 54.8492 | 54.9179 | 55.0369 | 55.0003 | 8.4915 | 67.9092 | -54.6387 | 68.3029 | 123.3261 | -0.013733 | 76.7395 | 0.10071 | 0.39368 | 123.1659 | 123.2849 | 123.1338 | 68.5089 | 68.3029 | 123.2483 | 123.0972 | 76.7395 | 68.5089 | 68.3029 | 123.0972 | 123.1338 | 123.2483 | -55.2383 | -46.4081
5146.7812 | 123.2849 | -68.2205 | 54.9408 | -2.0564 | -0.010352 | -0.022238 | 0.0022066 | -0.0069727 | -0.0080001 | -0.0011622 | 0.054932 | 0.35248 | -0.26093 | 55.0323 | 54.6478 | 54.8172 | 55.0278 | 55.0278 | 55.0369 | 8.4961 | 67.9596 | -54.5883 | 68.2755 | 123.2529 | -0.29297 | 76.7166 | 0.09613 | 0.31586 | 123.2483 | 123.2483 | 122.8683 | 68.573 | 68.2755 | 123.2574 | 123.0377 | 76.7166 | 68.573 | 68.2755 | 123.0377 | 122.8683 | 123.2574 | -55.2017 | -46.4447
5147.7812 | 123.3536 | -68.2571 | 54.9088 | -0.04219 | -0.007575 | -0.028433 | 0.005411 | -0.0050501 | -0.0062911 | -0.0058618 | 0.082397 | 0.25177 | -0.32959 | 55.0964 | 54.6982 | 54.8859 | 54.8767 | 55.069 | 55.014 | 8.4824 | 67.9276 | -54.657 | 68.3395 | 123.3536 | -0.21057 | 76.7395 | 0.10529 | 0.41199 | 123.1338 | 123.3261 | 122.9553 | 68.5089 | 68.3395 | 123.2712 | 123.143 | 76.7395 | 68.5089 | 68.3395 | 123.143 | 122.9553 | 123.2712 | -55.2383 | -46.4264
5148.7812 | 123.2895 | -68.2434 | 54.9225 | -0.34737 | -0.0097114 | -0.029074 | 0.003702 | -0.0093225 | -0.0060775 | -0.00094839 | -0.041199 | 0.32044 | -0.27008 | 55.0598 | 54.6524 | 54.8172 | 54.9911 | 55.0323 | 55.0369 | 8.4915 | 67.9733 | -54.602 | 68.2022 | 123.3032 | -0.27008 | 76.7349 | 0.11444 | 0.22888 | 123.2346 | 123.2758 | 122.8958 | 68.5638 | 68.2022 | 123.2803 | 123.0606 | 76.7349 | 68.5638 | 68.2022 | 123.0606 | 122.8958 | 123.2803 | -55.1926 | -46.431
5149.7812 | 123.2803 | -68.248 | 54.9179 | -0.21767 | -0.01142 | -0.029074 | 0.0011386 | -0.010818 | -0.0071457 | -0.003512 | 0.004578 | 0.29297 | -0.30212 | 55.1971 | 54.7623 | 54.7394 | 54.9088 | 54.9957 | 55.0323 | 8.4961 | 67.9459 | -54.6249 | 68.2526 | 123.4451 | -0.15564 | 76.7441 | 0.11444 | 0.3067 | 123.1567 | 123.2437 | 123.0103 | 68.541 | 68.2526 | 123.2803 | 122.9874 | 76.7441 | 68.541 | 68.2526 | 122.9874 | 123.0103 | 123.2803 | -55.22 | -46.4218
5150.7812 | 123.317 | -68.2434 | 54.9225 | -0.20241 | -0.0097114 | -0.023947 | 0.0024202 | -0.0080407 | -0.0067185 | -0.0039392 | 0.027466 | 0.27924 | -0.30212 | 55.0552 | 54.6661 | 54.8355 | 54.9911 | 55.0415 | 55.0232 | 8.4915 | 67.9413 | -54.6432 | 68.2709 | 123.2986 | -0.25635 | 76.7349 | 0.10071 | 0.32959 | 123.2346 | 123.2849 | 122.9095 | 68.5226 | 68.2709 | 123.2666 | 123.0789 | 76.7349 | 68.5226 | 68.2709 | 123.0789 | 122.9095 | 123.2666 | -55.2246 | -46.431
5151.7656 | 123.3078 | -68.2388 | 54.9454 | -0.13374 | -0.011207 | -0.025229 | 0.0034884 | -0.0099633 | -0.0082137 | -0.0024438 | 0.013733 | 0.27466 | -0.28839 | 55.0644 | 54.6707 | 54.8172 | 54.982 | 55.0461 | 55.014 | 8.4824 | 67.9504 | -54.6707 | 68.2526 | 123.3032 | -0.27466 | 76.7212 | 0.068664 | 0.30212 | 123.2208 | 123.2849 | 122.9095 | 68.5135 | 68.2526 | 123.2529 | 123.056 | 76.7212 | 68.5135 | 68.2526 | 123.056 | 122.9095 | 123.2529 | -55.2338 | -46.463
5152.7812 | 123.3078 | -68.2434 | 54.9362 | 0.087509 | -0.009925 | -0.028433 | 0.0047702 | -0.011245 | -0.0060775 | -0.0026574 | 0.018311 | 0.28381 | -0.28839 | 55.0552 | 54.6478 | 54.8218 | 54.9774 | 55.0323 | 55.0278 | 8.4869 | 67.955 | -54.6524 | 68.2617 | 123.2986 | -0.28839 | 76.7303 | 0.091553 | 0.3067 | 123.2208 | 123.2758 | 122.8912 | 68.5272 | 68.2617 | 123.2712 | 123.0652 | 76.7303 | 68.5272 | 68.2617 | 123.0652 | 122.8912 | 123.2712 | -55.2246 | -46.4493
5153.7812 | 123.3765 | -68.2114 | 54.9179 | -0.16426 | -0.014411 | -0.030997 | -0.00078396 | -0.0093225 | -0.0086411 | -0.001803 | 0.068665 | 0.2243 | -0.29297 | 55.1605 | 54.7485 | 54.9088 | 54.8813 | 55.1331 | 54.9911 | 8.4915 | 67.9184 | -54.6936 | 68.28 | 123.3719 | -0.16937 | 76.7029 | 0.073242 | 0.36163 | 123.0927 | 123.3444 | 122.9599 | 68.4357 | 68.28 | 123.2025 | 123.1201 | 76.7029 | 68.4357 | 68.28 | 123.1201 | 122.9599 | 123.2025 | -55.2109 | -46.4264
5154.7812 | 123.3994 | -68.1976 | 54.8904 | -0.19478 | -0.012916 | -0.027152 | 0.00049764 | -0.013595 | -0.0065047 | -0.0039392 | 0.068665 | 0.19226 | -0.29755 | 55.1376 | 54.7485 | 54.9179 | 54.8492 | 55.1605 | 54.9545 | 8.4915 | 67.9001 | -54.6982 | 68.2663 | 123.3353 | -0.14191 | 76.6891 | 0.064087 | 0.36621 | 123.0469 | 123.3582 | 122.9462 | 68.3899 | 68.2663 | 123.1522 | 123.1155 | 76.6891 | 68.3899 | 68.2663 | 123.1155 | 122.9462 | 123.1522 | -55.188 | -46.3989
5155.7812 | 123.3398 | -68.248 | 54.9133 | -0.14137 | -0.013343 | -0.026724 | 0.0022066 | -0.012313 | -0.0054367 | -0.0022302 | 0.068665 | 0.2243 | -0.28381 | 55.1376 | 54.7211 | 54.9042 | 54.8721 | 55.1239 | 54.9866 | 8.4961 | 67.9642 | -54.689 | 68.3167 | 123.3856 | -0.19226 | 76.7441 | 0.073242 | 0.35248 | 123.1201 | 123.3719 | 122.9691 | 68.4723 | 68.3167 | 123.2346 | 123.1522 | 76.7441 | 68.4723 | 68.3167 | 123.1522 | 122.9691 | 123.2346 | -55.1971 | -46.4172
5156.7812 | 123.3902 | -68.2022 | 54.9088 | -0.12611 | -0.013129 | -0.022452 | 0.0024202 | -0.01274 | -0.0060775 | -0.0026574 | 0.073242 | 0.18768 | -0.3067 | 55.1605 | 54.7348 | 54.9271 | 54.8584 | 55.1651 | 54.982 | 8.4961 | 67.8955 | -54.7211 | 68.2755 | 123.3627 | -0.17395 | 76.6983 | 0.073243 | 0.37994 | 123.0606 | 123.3673 | 122.937 | 68.3899 | 68.2755 | 123.1842 | 123.1293 | 76.6983 | 68.3899 | 68.2755 | 123.1293 | 122.937 | 123.1842 | -55.2155 | -46.4127
5157.7656 | 123.3124 | -68.2205 | 54.9316 | -0.18715 | -0.013557 | -0.026297 | 0.0058382 | -0.011672 | -0.0090683 | -0.0041528 | 0.041199 | 0.24719 | -0.3067 | 55.0781 | 54.6661 | 54.8218 | 54.9728 | 55.0461 | 54.9866 | 8.4869 | 67.9138 | -54.6844 | 68.2617 | 123.2986 | -0.2655 | 76.7075 | 0.054931 | 0.3479 | 123.1934 | 123.2666 | 122.8867 | 68.4677 | 68.2617 | 123.2071 | 123.0423 | 76.7075 | 68.4677 | 68.2617 | 123.0423 | 122.8867 | 123.2071 | -55.2383 | -46.4447
5158.7656 | 123.3444 | -68.2297 | 54.9133 | -0.19478 | -0.010566 | -0.024802 | 0.004343 | -0.011672 | -0.0099227 | -0.0020166 | 0.050354 | 0.22888 | -0.31586 | 55.1331 | 54.7119 | 54.8676 | 54.9179 | 55.0919 | 54.9866 | 8.5007 | 67.9138 | -54.6844 | 68.28 | 123.3627 | -0.20142 | 76.7303 | 0.073242 | 0.36621 | 123.1476 | 123.3215 | 122.9416 | 68.4586 | 68.28 | 123.2162 | 123.0972 | 76.7303 | 68.4586 | 68.28 | 123.0972 | 122.9416 | 123.2162 | -55.2292 | -46.4127
5159.7656 | 123.3719 | -68.2114 | 54.9088 | -0.15663 | -0.011207 | -0.02822 | 0.001993 | -0.010818 | -0.0054367 | -0.0041528 | 0.07782 | 0.21057 | -0.28839 | 55.1331 | 54.7256 | 54.8859 | 54.8767 | 55.1102 | 54.9728 | 8.4869 | 67.923 | -54.6982 | 68.2892 | 123.3444 | -0.1831 | 76.6983 | 0.064087 | 0.36621 | 123.0881 | 123.3215 | 122.937 | 68.4219 | 68.2892 | 123.1842 | 123.0972 | 76.6983 | 68.4219 | 68.2892 | 123.0972 | 122.937 | 123.1842 | -55.1971 | -46.4218
5160.7812 | 123.4222 | -68.2114 | 54.8859 | -0.034561 | -0.013557 | -0.028861 | 0.0022066 | -0.012954 | -0.0058639 | -0.0050074 | 0.041199 | 0.20142 | -0.29755 | 55.1422 | 54.744 | 54.9225 | 54.7852 | 55.1651 | 54.9774 | 8.4915 | 67.9138 | -54.6844 | 68.2526 | 123.3536 | -0.14191 | 76.7029 | 0.091553 | 0.33874 | 122.9965 | 123.3765 | 122.9553 | 68.4128 | 68.2526 | 123.1888 | 123.1338 | 76.7029 | 68.4128 | 68.2526 | 123.1338 | 122.9553 | 123.1888 | -55.1834 | -46.3943
5161.7812 | 123.4131 | -68.2114 | 54.863 | -0.0040434 | -0.015052 | -0.028006 | 0.0015658 | -0.014449 | -0.0058639 | -0.0011622 | 0.022888 | 0.20599 | -0.32044 | 55.1422 | 54.7119 | 54.9042 | 54.8126 | 55.1422 | 54.9545 | 8.4915 | 67.8909 | -54.657 | 68.2343 | 123.3536 | -0.15106 | 76.7029 | 0.091553 | 0.34332 | 123.024 | 123.3536 | 122.9233 | 68.4174 | 68.2343 | 123.1659 | 123.1155 | 76.7029 | 68.4174 | 68.2343 | 123.1155 | 122.9233 | 123.1659 | -55.1834 | -46.3715
5162.7812 | 123.4314 | -68.1976 | 54.895 | -0.10323 | -0.014197 | -0.028647 | 0.0017794 | -0.011031 | -0.0058639 | -0.0043664 | 0.050354 | 0.20599 | -0.3067 | 55.1834 | 54.7623 | 54.9316 | 54.8035 | 55.1605 | 54.9362 | 8.4915 | 67.8909 | -54.689 | 68.248 | 123.381 | -0.13275 | 76.6891 | 0.041198 | 0.35706 | 123.0011 | 123.3582 | 122.9599 | 68.4036 | 68.248 | 123.1338 | 123.1293 | 76.6891 | 68.4036 | 68.248 | 123.1293 | 122.9599 | 123.1338 | -55.2017 | -46.4035
5163.7812 | 123.3994 | -68.2205 | 54.8721 | -0.04982 | -0.014197 | -0.028647 | 0.00028404 | -0.013381 | -0.0065047 | -0.003512 | 0.018311 | 0.20142 | -0.32501 | 55.1605 | 54.7348 | 54.9088 | 54.7852 | 55.1376 | 54.9316 | 8.4869 | 67.8955 | -54.6707 | 68.2388 | 123.381 | -0.13733 | 76.7075 | 0.05951 | 0.34332 | 123.0057 | 123.3582 | 122.9553 | 68.4219 | 68.2388 | 123.1522 | 123.1293 | 76.7075 | 68.4219 | 68.2388 | 123.1293 | 122.9553 | 123.1522 | -55.1971 | -46.3852
5164.7656 | 123.3994 | -68.2022 | 54.8904 | 0.32402 | -0.010352 | -0.030997 | 0.0011386 | -0.010604 | -0.0058639 | -0.0037256 | 0.059509 | 0.20142 | -0.31128 | 55.188 | 54.7577 | 54.9225 | 54.8035 | 55.1559 | 54.9362 | 8.4869 | 67.8909 | -54.689 | 68.2617 | 123.3902 | -0.13275 | 76.6891 | 0.045776 | 0.37079 | 123.0057 | 123.3582 | 122.9599 | 68.4036 | 68.2617 | 123.1384 | 123.1247 | 76.6891 | 68.4036 | 68.2617 | 123.1247 | 122.9599 | 123.1384 | -55.2017 | -46.4035
5165.7656 | 123.4177 | -68.2251 | 54.8813 | -0.13374 | -0.012275 | -0.03057 | -0.00057036 | -0.017867 | -0.0058639 | -0.0020166 | 0.086975 | 0.20599 | -0.29755 | 54.9728 | 54.6936 | 54.8859 | 54.8218 | 55.1559 | 54.9408 | 8.4869 | 67.9276 | -54.6753 | 68.3121 | 123.1979 | -0.18768 | 76.712 | 0.059509 | 0.38452 | 123.0469 | 123.381 | 122.9187 | 68.4311 | 68.3121 | 123.1659 | 123.111 | 76.712 | 68.4311 | 68.3121 | 123.111 | 122.9187 | 123.1659 | -55.1788 | -46.3943
5166.7656 | 123.436 | -68.2068 | 54.8904 | -0.057449 | -0.012488 | -0.028861 | 7.0444e-05 | -0.011886 | -0.0041549 | -0.0032984 | 0.041199 | 0.19226 | -0.3067 | 55.1971 | 54.7714 | 54.9545 | 54.7897 | 55.1651 | 54.9408 | 8.5007 | 67.9001 | -54.6982 | 68.248 | 123.4039 | -0.11902 | 76.7075 | 0.050354 | 0.3479 | 122.9965 | 123.3719 | 122.9782 | 68.399 | 68.248 | 123.1476 | 123.1613 | 76.7075 | 68.399 | 68.248 | 123.1613 | 122.9782 | 123.1476 | -55.1971 | -46.3898
5167.7812 | 123.3673 | -68.2205 | 54.8584 | 0.64446 | -0.010993 | -0.028647 | 0.0030612 | -0.013168 | -0.0054367 | -0.001803 | -0.013733 | 0.18768 | -0.3067 | 55.0827 | 54.6753 | 54.8584 | 54.8172 | 55.0644 | 54.9316 | 8.4869 | 67.9138 | -54.6707 | 68.2068 | 123.3032 | -0.1831 | 76.7075 | 0.073243 | 0.29297 | 123.0377 | 123.2849 | 122.8958 | 68.4082 | 68.2068 | 123.1522 | 123.0789 | 76.7075 | 68.4082 | 68.2068 | 123.0789 | 122.8958 | 123.1522 | -55.1651 | -46.3715
5168.7812 | 123.3536 | -68.2297 | 54.8676 | 0.14854 | -0.012061 | -0.027365 | 0.0028476 | -0.011459 | -0.0052231 | -0.0022302 | -0.022888 | 0.17853 | -0.34332 | 55.1056 | 54.6936 | 54.8676 | 54.8126 | 55.2704 | 54.9316 | 8.4824 | 67.8864 | -54.689 | 68.2068 | 123.3353 | -0.17395 | 76.712 | 0.064087 | 0.32043 | 123.0423 | 123.5001 | 122.9233 | 68.4082 | 68.2068 | 123.1613 | 123.0972 | 76.712 | 68.4082 | 68.2068 | 123.0972 | 122.9233 | 123.1613 | -55.2109 | -46.3852
5169.7812 | 123.3765 | -68.2251 | 54.8859 | 0.14092 | -0.013557 | -0.026297 | 0.0015658 | -0.013809 | -0.0054367 | -0.0030848 | -0.054932 | 0.1831 | -0.31586 | 55.1285 | 54.6799 | 54.8584 | 54.808 | 55.0598 | 54.9042 | 8.4915 | 67.9092 | -54.7028 | 68.1702 | 123.3536 | -0.20599 | 76.7166 | 0.018311 | 0.26093 | 123.0331 | 123.2849 | 122.905 | 68.4082 | 68.1702 | 123.1293 | 123.0835 | 76.7166 | 68.4082 | 68.1702 | 123.0835 | 122.905 | 123.1293 | -55.2017 | -46.3943
5170.7812 | 123.3398 | -68.2434 | 54.863 | 0.10277 | -0.010779 | -0.022452 | 7.0444e-05 | -0.012313 | -0.0060775 | -0.0022302 | -0.018311 | 0.1831 | -0.33875 | 55.1056 | 54.7028 | 55.0232 | 54.7577 | 54.9911 | 54.9454 | 8.4778 | 67.9047 | -54.6799 | 68.2251 | 123.349 | -0.16022 | 76.7212 | 0.082398 | 0.32043 | 123.0011 | 123.2346 | 122.9462 | 68.4265 | 68.2251 | 123.1888 | 123.2666 | 76.7212 | 68.4265 | 68.2251 | 123.2666 | 122.9462 | 123.1888 | -55.2017 | -46.3852
5171.7656 | 123.3994 | -68.2159 | 54.8813 | 0.034104 | -0.010779 | -0.027792 | -0.00035676 | -0.012313 | -0.0056503 | -0.0030848 | 0 | 0.18768 | -0.31586 | 55.1422 | 54.7302 | 54.8859 | 54.808 | 55.101 | 54.9179 | 8.4961 | 67.9001 | -54.6936 | 68.2159 | 123.3582 | -0.15106 | 76.712 | 0.036621 | 0.31586 | 123.024 | 123.317 | 122.9462 | 68.4036 | 68.2159 | 123.1338 | 123.1018 | 76.712 | 68.4036 | 68.2159 | 123.1018 | 122.9462 | 123.1338 | -55.1971 | -46.3852
5172.7656 | 123.381 | -68.2205 | 54.8676 | 0.10277 | -0.010352 | -0.026724 | 0.0015658 | -0.011886 | -0.0065047 | -0.0024438 | -0.022888 | 0.1831 | -0.32959 | 55.1285 | 54.7073 | 54.863 | 54.8126 | 55.069 | 54.9088 | 8.5007 | 67.8909 | -54.6844 | 68.1976 | 123.349 | -0.16022 | 76.7212 | 0.041198 | 0.3067 | 123.0331 | 123.2895 | 122.9279 | 68.4036 | 68.1976 | 123.1293 | 123.0835 | 76.7212 | 68.4036 | 68.1976 | 123.0835 | 122.9279 | 123.1293 | -55.1971 | -46.3669
5173.7812 | 123.3719 | -68.2434 | 54.8676 | 0.12566 | -0.01142 | -0.031638 | 0.0030612 | -0.012954 | -0.0041549 | -0.0024438 | -0.027466 | 0.15564 | -0.33417 | 55.1056 | 54.6753 | 54.8767 | 54.808 | 55.0552 | 54.8996 | 8.4869 | 67.9092 | -54.7119 | 68.2159 | 123.349 | -0.19226 | 76.7303 | 0.032043 | 0.3067 | 123.0515 | 123.2986 | 122.9187 | 68.399 | 68.2159 | 123.143 | 123.1201 | 76.7303 | 68.399 | 68.2159 | 123.1201 | 122.9187 | 123.143 | -55.2017 | -46.3806
5174.7812 | 123.4039 | -68.248 | 54.8401 | 0.23247 | -0.009284 | -0.02822 | 0.0041292 | -0.011031 | -0.0060775 | -0.00458 | 0.013733 | 0.12817 | -0.34332 | 55.1468 | 54.7256 | 54.9042 | 54.7256 | 55.0735 | 54.9042 | 8.4869 | 67.9047 | -54.7119 | 68.2617 | 123.3948 | -0.11444 | 76.7349 | 0.064087 | 0.35706 | 122.9736 | 123.3215 | 122.9736 | 68.3762 | 68.2617 | 123.1522 | 123.1522 | 76.7349 | 68.3762 | 68.2617 | 123.1522 | 122.9736 | 123.1522 | -55.1834 | -46.3531
5175.7812 | 123.3765 | -68.2159 | 54.8309 | 0.20958 | -0.010139 | -0.029929 | 0.002634 | -0.012527 | -0.0028731 | -0.0022302 | -0.013733 | 0.13275 | -0.37079 | 55.1285 | 54.7028 | 54.8859 | 54.7256 | 55.069 | 54.9042 | 8.4869 | 67.8452 | -54.6982 | 68.2022 | 123.3444 | -0.12817 | 76.7029 | 0.073242 | 0.35706 | 122.9416 | 123.2849 | 122.9187 | 68.3487 | 68.2022 | 123.1201 | 123.1018 | 76.7029 | 68.3487 | 68.2022 | 123.1018 | 122.9187 | 123.1201 | -55.2017 | -46.344
5176.7812 | 123.4131 | -68.2205 | 54.8401 | 0.2401 | -0.009925 | -0.026083 | 0.0056246 | -0.010391 | -0.0045821 | -0.0037256 | 0.022888 | 0.14191 | -0.35706 | 55.1468 | 54.7256 | 54.9179 | 54.7348 | 55.0644 | 54.8996 | 8.4915 | 67.8635 | -54.6982 | 68.2434 | 123.3673 | -0.11444 | 76.712 | 0.059509 | 0.37994 | 122.9553 | 123.2849 | 122.9462 | 68.3624 | 68.2434 | 123.1201 | 123.1384 | 76.712 | 68.3624 | 68.2434 | 123.1384 | 122.9462 | 123.1201 | -55.1971 | -46.3486
5177.7812 | 123.4268 | -68.2297 | 54.8264 | -0.60677 | -0.010139 | -0.026297 | 0.0041292 | -0.0095361 | -0.0069321 | -0.0022302 | 0.086975 | 0.082397 | -0.40283 | 55.1376 | 54.7119 | 54.9042 | 54.7073 | 55.0781 | 54.8996 | 8.4915 | 67.8268 | -54.744 | 68.3166 | 123.3673 | -0.11444 | 76.7212 | 0.073242 | 0.48981 | 122.937 | 123.3078 | 122.9416 | 68.3121 | 68.3166 | 123.1293 | 123.1338 | 76.7212 | 68.3121 | 68.3166 | 123.1338 | 122.9416 | 123.1293 | -55.2292 | -46.3348
5178.7656 | 123.381 | -68.2434 | 54.8492 | 0.21721 | -0.010352 | -0.026938 | 0.0024202 | -0.011886 | -0.0077865 | -0.0037256 | -0.027466 | 0.10986 | -0.40741 | 55.1102 | 54.7028 | 54.8767 | 54.7577 | 55.0415 | 54.9225 | 8.4961 | 67.836 | -54.7394 | 68.2159 | 123.3536 | -0.14648 | 76.7395 | 0.073242 | 0.37994 | 123.0011 | 123.2849 | 122.9462 | 68.3533 | 68.2159 | 123.1659 | 123.1201 | 76.7395 | 68.3533 | 68.2159 | 123.1201 | 122.9462 | 123.1659 | -55.2567 | -46.3531
5179.7656 | 123.3948 | -68.2297 | 54.8401 | 0.20958 | -0.010352 | -0.028006 | 0.0045566 | -0.0099633 | -0.0058639 | -0.0041528 | -0.013733 | 0.13733 | -0.37079 | 55.1239 | 54.7119 | 54.8996 | 54.7302 | 55.0507 | 54.8859 | 8.4961 | 67.8589 | -54.7028 | 68.2159 | 123.3536 | -0.12817 | 76.7258 | 0.045776 | 0.35706 | 122.9599 | 123.2803 | 122.9416 | 68.367 | 68.2159 | 123.1155 | 123.1293 | 76.7258 | 68.367 | 68.2159 | 123.1293 | 122.9416 | 123.1155 | -55.2109 | -46.344
5180.7812 | 123.4131 | -68.2251 | 54.8767 | 0.27824 | -0.01142 | -0.021384 | 0.00712 | -0.0080407 | -0.0015915 | -0.0024438 | 0.004578 | 0.14191 | -0.37994 | 55.0735 | 54.7989 | 55.0003 | 54.7485 | 55.0873 | 54.9088 | 8.5007 | 67.8452 | -54.7348 | 68.2297 | 123.2986 | -0.07782 | 76.7258 | 0.032043 | 0.38452 | 122.9736 | 123.3124 | 123.024 | 68.367 | 68.2297 | 123.1338 | 123.2254 | 76.7258 | 68.367 | 68.2297 | 123.2254 | 123.024 | 123.1338 | -55.2567 | -46.376
5181.7812 | 123.4039 | -68.1885 | 54.8996 | -0.11848 | -0.013557 | -0.027365 | -0.00035676 | -0.011245 | -0.0075729 | -0.0028712 | 0.054932 | 0.20142 | -0.28839 | 55.1376 | 54.7302 | 54.9408 | 54.7897 | 55.101 | 54.9271 | 8.4869 | 67.9001 | -54.6982 | 68.2434 | 123.3261 | -0.16937 | 76.6754 | 0.027466 | 0.34332 | 122.9782 | 123.2895 | 122.9187 | 68.3899 | 68.2434 | 123.1155 | 123.1293 | 76.6754 | 68.3899 | 68.2434 | 123.1293 | 122.9187 | 123.1155 | -55.188 | -46.4127
5182.7812 | 123.3261 | -68.248 | 54.895 | 0.24773 | -0.010352 | -0.024588 | 0.010538 | -0.0097497 | -0.0043685 | -0.001803 | -0.022888 | 0.21515 | -0.37537 | 55.0552 | 54.6204 | 54.8172 | 54.8492 | 54.9728 | 54.9316 | 8.4869 | 67.8726 | -54.6799 | 68.2251 | 123.3032 | -0.27466 | 76.7349 | 0.036621 | 0.35248 | 123.0972 | 123.2208 | 122.8683 | 68.4631 | 68.2251 | 123.1796 | 123.0652 | 76.7349 | 68.4631 | 68.2251 | 123.0652 | 122.8683 | 123.1796 | -55.2704 | -46.4081
5183.7812 | 123.3673 | -68.2343 | 54.8767 | 0.25536 | -0.0067206 | -0.029288 | 0.0073336 | -0.0084681 | -0.0045821 | -0.0032984 | -0.018311 | 0.19226 | -0.37079 | 55.0827 | 54.6844 | 54.8401 | 54.7989 | 55.0095 | 54.9362 | 8.4961 | 67.8635 | -54.6844 | 68.2159 | 123.317 | -0.19226 | 76.7303 | 0.059509 | 0.35248 | 123.0331 | 123.2437 | 122.9187 | 68.4265 | 68.2159 | 123.1705 | 123.0743 | 76.7303 | 68.4265 | 68.2159 | 123.0743 | 122.9187 | 123.1705 | -55.2475 | -46.3806
5184.7812 | 123.3398 | -68.2617 | 54.8538 | 0.23247 | -0.010352 | -0.02352 | 0.0075472 | -0.0080407 | -0.0082137 | -0.0039392 | -0.032043 | 0.19226 | -0.36621 | 55.0735 | 54.6661 | 54.8355 | 54.8401 | 54.9911 | 54.9316 | 8.4869 | 67.8955 | -54.6616 | 68.2297 | 123.3353 | -0.18768 | 76.7487 | 0.07782 | 0.33417 | 123.1018 | 123.2529 | 122.9279 | 68.454 | 68.2297 | 123.1934 | 123.0972 | 76.7487 | 68.454 | 68.2297 | 123.0972 | 122.9279 | 123.1934 | -55.22 | -46.3669
5185.7656 | 123.4222 | -68.2388 | 54.8355 | 0.2401 | -0.008216 | -0.026297 | 0.0062656 | -0.0078271 | -0.0062911 | -0.0015894 | 0.027466 | 0.14191 | -0.37079 | 55.1559 | 54.5609 | 54.7577 | 54.8767 | 55.1651 | 54.9179 | 8.4869 | 67.868 | -54.6936 | 68.2663 | 123.3948 | -0.27466 | 76.7258 | 0.082398 | 0.39825 | 123.1155 | 123.4039 | 122.7997 | 68.3807 | 68.2663 | 123.1567 | 122.9965 | 76.7258 | 68.3807 | 68.2663 | 122.9965 | 122.7997 | 123.1567 | -55.2063 | -46.3486
5186.7656 | 123.4085 | -68.2159 | 54.863 | 0.48424 | -0.0077888 | -0.023734 | 0.0064792 | -0.0086817 | -0.0056503 | -0.0028712 | -0.036621 | 0.15564 | -0.3891 | 55.1239 | 54.6982 | 54.9133 | 54.7531 | 55.069 | 54.9042 | 8.4869 | 67.8268 | -54.7073 | 68.1793 | 123.3398 | -0.1648 | 76.7029 | 0.041199 | 0.35248 | 122.9691 | 123.2849 | 122.9141 | 68.3716 | 68.1793 | 123.1201 | 123.1293 | 76.7029 | 68.3716 | 68.1793 | 123.1293 | 122.9141 | 123.1201 | -55.2521 | -46.376
5187.7812 | 123.3627 | -68.2297 | 54.8355 | 0.27061 | -0.0067206 | -0.025015 | 0.0066928 | -0.0078271 | -0.0073593 | -0.00052119 | -0.018311 | 0.1831 | -0.37994 | 55.0644 | 54.6524 | 54.8355 | 54.8264 | 54.982 | 54.9271 | 8.4869 | 67.8497 | -54.6524 | 68.2114 | 123.2941 | -0.1831 | 76.7166 | 0.091553 | 0.36163 | 123.056 | 123.2117 | 122.8821 | 68.4128 | 68.2114 | 123.1567 | 123.0652 | 76.7166 | 68.4128 | 68.2114 | 123.0652 | 122.8821 | 123.1567 | -55.2155 | -46.3486
5188.7812 | 123.2941 | -68.2709 | 54.8996 | 0.19432 | -0.005866 | -0.023734 | 0.0096834 | -0.0029139 | -0.0094955 | -0.0050074 | -0.050354 | 0.20599 | -0.3891 | 55.2383 | 54.6799 | 54.8401 | 54.8904 | 54.9637 | 54.982 | 8.4824 | 67.8818 | -54.6936 | 68.2205 | 123.5092 | -0.21973 | 76.7532 | 0.082398 | 0.33874 | 123.1613 | 123.2346 | 122.9507 | 68.4769 | 68.2205 | 123.2529 | 123.111 | 76.7532 | 68.4769 | 68.2205 | 123.111 | 122.9507 | 123.2529 | -55.2887 | -46.4172
5189.7812 | 123.3124 | -68.248 | 54.8767 | 0.22484 | -0.010139 | -0.025229 | 0.0066928 | -0.0073999 | -0.0073593 | -0.0041528 | -0.050354 | 0.21973 | -0.37079 | 55.0415 | 54.6387 | 54.8264 | 54.8813 | 54.9728 | 54.982 | 8.4869 | 67.8772 | -54.657 | 68.1976 | 123.2895 | -0.23804 | 76.7349 | 0.10529 | 0.32043 | 123.1293 | 123.2208 | 122.8867 | 68.4677 | 68.1976 | 123.23 | 123.0743 | 76.7349 | 68.4677 | 68.1976 | 123.0743 | 122.8867 | 123.23 | -55.2475 | -46.3898
5190.7812 | 123.2986 | -68.2526 | 54.8721 | 0.12566 | -0.010139 | -0.02587 | 0.0069064 | -0.0071863 | -0.0069321 | -0.0013758 | -0.018311 | 0.2243 | -0.3891 | 55.0278 | 54.6387 | 54.7989 | 54.9179 | 54.9591 | 55.0003 | 8.4915 | 67.8635 | -54.6478 | 68.2343 | 123.2803 | -0.23346 | 76.7441 | 0.12817 | 0.37079 | 123.1705 | 123.2117 | 122.8912 | 68.4769 | 68.2343 | 123.2529 | 123.0515 | 76.7441 | 68.4769 | 68.2343 | 123.0515 | 122.8912 | 123.2529 | -55.2612 | -46.3806
5191.7812 | 123.3124 | -68.28 | 54.9133 | 2.1246 | -0.004798 | -0.023947 | 0.005411 | -0.0059045 | -0.0037277 | -0.0028712 | -0.21515 | 0.20142 | -0.3891 | 55.0461 | 54.6341 | 54.8035 | 54.8996 | 54.9591 | 55.014 | 8.4869 | 67.8909 | -54.7119 | 68.0649 | 123.3261 | -0.27924 | 76.767 | 0.10071 | 0.17395 | 123.1796 | 123.2391 | 122.9141 | 68.4814 | 68.0649 | 123.2941 | 123.0835 | 76.767 | 68.4814 | 68.0649 | 123.0835 | 122.9141 | 123.2941 | -55.3024 | -46.4264
5192.7656 | 123.3627 | -68.2617 | 54.8538 | 0.27824 | -0.0097114 | -0.024588 | 0.00712 | -0.0067591 | -0.0067185 | -0.0026574 | -0.018311 | 0.17395 | -0.37079 | 55.0598 | 54.657 | 54.863 | 54.8264 | 55.014 | 54.9637 | 8.4915 | 67.8909 | -54.6799 | 68.2434 | 123.3215 | -0.19684 | 76.7532 | 0.10986 | 0.35248 | 123.0881 | 123.2758 | 122.9187 | 68.4357 | 68.2434 | 123.2254 | 123.1247 | 76.7532 | 68.4357 | 68.2434 | 123.1247 | 122.9187 | 123.2254 | -55.2246 | -46.3623
5193.7812 | 123.3124 | -68.2709 | 54.8584 | 0.20195 | -0.0069342 | -0.024374 | 0.0047702 | -0.0071863 | -0.0033005 | -0.0026574 | -0.036621 | 0.23346 | -0.36163 | 55.0232 | 54.6295 | 54.8035 | 54.9042 | 54.9637 | 54.9774 | 8.4915 | 67.9092 | -54.6249 | 68.2343 | 123.2941 | -0.22888 | 76.7624 | 0.11902 | 0.32501 | 123.175 | 123.2346 | 122.9004 | 68.5043 | 68.2343 | 123.2483 | 123.0743 | 76.7624 | 68.5043 | 68.2343 | 123.0743 | 122.9004 | 123.2483 | -55.22 | -46.3669
5194.7812 | 123.2986 | -68.2983 | 54.8538 | 0.19432 | -0.0067206 | -0.023306 | 0.0062656 | -0.0052637 | -0.0050095 | -0.00094839 | -0.018311 | 0.22888 | -0.37079 | 55.0232 | 54.6387 | 54.808 | 54.9225 | 54.9591 | 54.982 | 8.4869 | 67.9276 | -54.6249 | 68.28 | 123.3215 | -0.21515 | 76.7853 | 0.12817 | 0.35248 | 123.2208 | 123.2574 | 122.937 | 68.5272 | 68.28 | 123.2803 | 123.1064 | 76.7853 | 68.5272 | 68.28 | 123.1064 | 122.937 | 123.2803 | -55.2246 | -46.3669
5195.7812 | 123.468 | -68.1931 | 54.8996 | 0.1104 | -0.011634 | -0.027792 | -0.0022794 | -0.0063317 | -0.0052231 | -0.00073479 | -0.041199 | 0.16022 | -0.3479 | 55.069 | 54.6936 | 54.8767 | 54.8355 | 55.0415 | 54.982 | 8.4869 | 67.8452 | -54.7394 | 68.1519 | 123.262 | -0.20599 | 76.68 | 0.082398 | 0.3067 | 123.0286 | 123.2346 | 122.8867 | 68.3533 | 68.1519 | 123.175 | 123.0698 | 76.68 | 68.3533 | 68.1519 | 123.0698 | 122.8867 | 123.175 | -55.2475 | -46.4127
5196.7812 | 123.2849 | -68.2617 | 54.895 | 0.18669 | -0.0062934 | -0.029715 | 0.0092562 | -0.0099633 | -0.0067185 | -0.003512 | -0.041199 | 0.21057 | -0.39368 | 55.0919 | 54.6478 | 54.7897 | 54.9866 | 55.0049 | 54.9866 | 8.4824 | 67.868 | -54.6844 | 68.2205 | 123.3536 | -0.24719 | 76.7441 | 0.091552 | 0.35248 | 123.2483 | 123.2666 | 122.9095 | 68.4723 | 68.2205 | 123.2483 | 123.0515 | 76.7441 | 68.4723 | 68.2205 | 123.0515 | 122.9095 | 123.2483 | -55.2887 | -46.4127
5197.7812 | 123.3215 | -68.2755 | 54.9225 | 0.1638 | -0.009284 | -0.022238 | 0.010752 | -0.0056909 | -0.0067185 | -0.001803 | -0.045776 | 0.2243 | -0.3891 | 54.9911 | 54.7165 | 54.6982 | 54.6112 | 55.2429 | 54.9454 | 8.4869 | 67.8864 | -54.6982 | 68.2297 | 123.2666 | -0.20599 | 76.7624 | 0.022889 | 0.34332 | 122.8867 | 123.5184 | 122.9919 | 68.4998 | 68.2297 | 123.2208 | 122.9736 | 76.7624 | 68.4998 | 68.2297 | 122.9736 | 122.9919 | 123.2208 | -55.3116 | -46.4355
5198.7812 | 123.2803 | -68.2755 | 54.8859 | 0.12566 | -0.0080024 | -0.021597 | 0.0081882 | -0.0073999 | -0.0077865 | -0.0026574 | -0.050354 | 0.22888 | -0.36621 | 55.0095 | 54.6066 | 54.7943 | 54.9454 | 54.9454 | 54.9957 | 8.4915 | 67.9092 | -54.657 | 68.2251 | 123.2849 | -0.27924 | 76.767 | 0.10986 | 0.31586 | 123.2208 | 123.2208 | 122.8821 | 68.5043 | 68.2251 | 123.2712 | 123.0698 | 76.767 | 68.5043 | 68.2251 | 123.0698 | 122.8821 | 123.2712 | -55.2521 | -46.3943
5199.7656 | 123.3124 | -68.2755 | 54.8721 | 0.22484 | -0.0084296 | -0.025656 | 0.0066928 | -0.0041955 | -0.0033005 | -0.0043664 | -0.032043 | 0.20599 | -0.3891 | 55.0186 | 54.6387 | 54.8126 | 54.8767 | 54.982 | 55.0003 | 8.4915 | 67.8864 | -54.6661 | 68.2434 | 123.2941 | -0.23346 | 76.767 | 0.12817 | 0.35706 | 123.1522 | 123.2574 | 122.9141 | 68.4814 | 68.2434 | 123.2758 | 123.0881 | 76.767 | 68.4814 | 68.2434 | 123.0881 | 122.9141 | 123.2758 | -55.2612 | -46.3806
5200.7812 | 123.4039 | -68.2068 | 54.8767 | -0.011673 | -0.012061 | -0.029288 | -0.0035612 | -0.010177 | -0.0065047 | -9.3992e-05 | -0.004578 | 0.1831 | -0.3067 | 55.1285 | 54.7485 | 54.9133 | 54.8218 | 55.1285 | 54.9591 | 8.4869 | 67.9001 | -54.6936 | 68.2022 | 123.3353 | -0.12817 | 76.6937 | 0.082397 | 0.30212 | 123.0286 | 123.3353 | 122.9553 | 68.3899 | 68.2022 | 123.1659 | 123.1201 | 76.6937 | 68.3899 | 68.2022 | 123.1201 | 122.9553 | 123.1659 | -55.1834 | -46.3898
5201.7812 | 123.3078 | -68.248 | 54.9088 | 0.064621 | -0.0088568 | -0.019888 | 0.0094698 | -0.0059045 | -0.0067185 | -0.00094839 | 0 | 0.24261 | -0.33875 | 55.0323 | 54.6158 | 54.8035 | 54.9225 | 54.9728 | 54.982 | 8.4732 | 67.9092 | -54.6661 | 68.248 | 123.2803 | -0.29297 | 76.7212 | 0.073243 | 0.33875 | 123.1705 | 123.2208 | 122.8638 | 68.4906 | 68.248 | 123.23 | 123.0515 | 76.7212 | 68.4906 | 68.248 | 123.0515 | 122.8638 | 123.23 | -55.2475 | -46.4355
5202.7812 | 123.3032 | -68.28 | 54.895 | 0.095139 | -0.0073614 | -0.021597 | 0.0094698 | -0.0067591 | -0.0069321 | -0.001803 | 0.018311 | 0.22888 | -0.32959 | 55.0552 | 54.6387 | 54.808 | 54.9179 | 54.9911 | 54.9911 | 8.4824 | 67.9504 | -54.6661 | 68.2983 | 123.3353 | -0.25635 | 76.7624 | 0.09613 | 0.3479 | 123.1979 | 123.2712 | 122.9187 | 68.5089 | 68.2983 | 123.2712 | 123.0881 | 76.7624 | 68.5089 | 68.2983 | 123.0881 | 122.9187 | 123.2712 | -55.2246 | -46.4127
5203.7812 | 123.317 | -68.28 | 54.8813 | 0.2401 | -0.0073614 | -0.023093 | 0.005411 | -0.0059045 | -0.0067185 | -0.0022302 | -0.027466 | 0.24719 | -0.36163 | 55.0186 | 54.6387 | 54.7943 | 54.895 | 54.9545 | 55.0049 | 8.4869 | 67.9184 | -54.6341 | 68.2526 | 123.2986 | -0.24262 | 76.767 | 0.1236 | 0.33417 | 123.175 | 123.2346 | 122.9187 | 68.5272 | 68.2526 | 123.2849 | 123.0743 | 76.767 | 68.5272 | 68.2526 | 123.0743 | 122.9187 | 123.2849 | -55.2429 | -46.3943
5204.7812 | 123.2895 | -68.2755 | 54.9088 | 0.10277 | -0.0097114 | -0.019888 | 0.0062656 | -0.0046229 | -0.0058639 | -0.00073479 | -0.013733 | 0.24261 | -0.37079 | 55.0232 | 54.6204 | 54.7852 | 54.9408 | 54.9591 | 55.0003 | 8.4869 | 67.9047 | -54.6661 | 68.2617 | 123.2986 | -0.28839 | 76.7624 | 0.091553 | 0.35706 | 123.2162 | 123.2346 | 122.8958 | 68.5181 | 68.2617 | 123.2758 | 123.0606 | 76.7624 | 68.5181 | 68.2617 | 123.0606 | 122.8958 | 123.2758 | -55.2795 | -46.4218
5205.7812 | 123.3673 | -68.2297 | 54.8904 | 0.14854 | -0.014411 | -0.023734 | -0.003134 | -0.0091089 | -0.0090683 | -0.001803 | -0.045776 | 0.16022 | -0.3479 | 55.069 | 54.7211 | 54.8767 | 54.8218 | 55.0644 | 54.9683 | 8.4915 | 67.8818 | -54.7302 | 68.1839 | 123.2986 | -0.16937 | 76.7212 | 0.07782 | 0.30212 | 123.0515 | 123.2941 | 122.9507 | 68.3899 | 68.1839 | 123.1979 | 123.1064 | 76.7212 | 68.3899 | 68.1839 | 123.1064 | 122.9507 | 123.1979 | -55.2383 | -46.3989
5206.7656 | 123.2986 | -68.2846 | 54.895 | 0.1638 | -0.0073614 | -0.019034 | 0.0077608 | -0.0080407 | -0.0047957 | -0.001803 | -0.027466 | 0.21515 | -0.35706 | 55.014 | 54.6387 | 54.7989 | 54.8767 | 54.9591 | 54.95 | 8.4915 | 67.9276 | -54.6799 | 68.2571 | 123.2986 | -0.25635 | 76.7761 | 0.054931 | 0.32959 | 123.1613 | 123.2437 | 122.9233 | 68.4998 | 68.2571 | 123.2346 | 123.0835 | 76.7761 | 68.4998 | 68.2571 | 123.0835 | 122.9233 | 123.2346 | -55.2521 | -46.4035
5207.7656 | 123.2986 | -68.2709 | 54.8859 | 0.21721 | -0.0086432 | -0.024374 | 0.0084018 | -0.0082545 | -0.0052231 | -0.0037256 | -0.013733 | 0.2243 | -0.37537 | 55.0186 | 54.6524 | 54.7897 | 54.9042 | 54.9728 | 54.9911 | 8.4778 | 67.8955 | -54.6616 | 68.2571 | 123.2895 | -0.23346 | 76.7487 | 0.10529 | 0.36163 | 123.175 | 123.2437 | 122.9233 | 68.4952 | 68.2571 | 123.262 | 123.0606 | 76.7487 | 68.4952 | 68.2571 | 123.0606 | 122.9233 | 123.262 | -55.2612 | -46.4081
5208.7812 | 123.436 | -68.2388 | 54.8492 | 0.23247 | -0.010566 | -0.026511 | 0.0045566 | -0.0076135 | -0.0054367 | -0.0032984 | 0.022888 | 0.13275 | -0.37079 | 55.1193 | 54.744 | 54.9225 | 54.5059 | 54.9408 | 54.8996 | 8.4961 | 67.868 | -54.7165 | 68.2617 | 123.3582 | -0.10529 | 76.7349 | 0.050354 | 0.39368 | 122.7448 | 123.1796 | 122.9828 | 68.3716 | 68.2617 | 123.1384 | 123.1613 | 76.7349 | 68.3716 | 68.2617 | 123.1613 | 122.9828 | 123.1384 | -55.22 | -46.3531
5209.7812 | 123.3215 | -68.2526 | 54.8996 | 0.049362 | -0.0086432 | -0.025015 | 0.0060518 | -0.0065455 | -0.0058639 | -0.0011622 | 0.022888 | 0.23804 | -0.32501 | 55.0552 | 54.689 | 54.8172 | 54.8996 | 55.0049 | 55.0278 | 8.4824 | 67.9276 | -54.6616 | 68.2755 | 123.3078 | -0.21057 | 76.7349 | 0.12817 | 0.3479 | 123.1522 | 123.2574 | 122.9416 | 68.4906 | 68.2755 | 123.2803 | 123.0698 | 76.7349 | 68.4906 | 68.2755 | 123.0698 | 122.9416 | 123.2803 | -55.2246 | -46.4172
5210.7812 | 123.3719 | -68.2343 | 54.8904 | 0.23247 | -0.0069342 | -0.023947 | -0.00057036 | -0.0099633 | -0.0030869 | -0.00094839 | -0.022888 | 0.13275 | -0.37994 | 55.0781 | 54.7577 | 54.8813 | 54.7623 | 55.0781 | 54.9408 | 8.4869 | 67.8543 | -54.7577 | 68.2114 | 123.3124 | -0.13275 | 76.7212 | 0.050354 | 0.35706 | 122.9965 | 123.3124 | 122.9919 | 68.367 | 68.2114 | 123.175 | 123.1155 | 76.7212 | 68.367 | 68.2114 | 123.1155 | 122.9919 | 123.175 | -55.2704 | -46.4035
5211.7812 | 123.2941 | -68.2571 | 54.9271 | 0.1104 | -0.0094976 | -0.025229 | 0.0098972 | -0.0078271 | -0.0054367 | -0.0013758 | 0.009155 | 0.22888 | -0.33875 | 55.0415 | 54.6844 | 54.7989 | 54.9225 | 54.9774 | 55.0003 | 8.4732 | 67.9184 | -54.6982 | 68.2663 | 123.2986 | -0.24261 | 76.7303 | 0.073242 | 0.3479 | 123.1796 | 123.2346 | 122.9416 | 68.486 | 68.2663 | 123.2574 | 123.056 | 76.7303 | 68.486 | 68.2663 | 123.056 | 122.9416 | 123.2574 | -55.2658 | -46.4539
5212.7656 | 123.2941 | -68.2892 | 54.8767 | 0.48424 | -0.0073614 | -0.023306 | 0.0075472 | -0.0065455 | -0.0077865 | -0.0037256 | -0.027466 | 0.20599 | -0.38452 | 55.0369 | 54.689 | 54.7806 | 54.8996 | 54.9591 | 54.9911 | 8.4869 | 67.9047 | -54.6707 | 68.2617 | 123.3261 | -0.18768 | 76.7761 | 0.11444 | 0.35706 | 123.1888 | 123.2483 | 122.9782 | 68.4952 | 68.2617 | 123.2803 | 123.0698 | 76.7761 | 68.4952 | 68.2617 | 123.0698 | 122.9782 | 123.2803 | -55.2612 | -46.3898
5213.7812 | 123.3856 | -68.2251 | 54.8859 | 0.21721 | -0.0084296 | -0.024588 | -0.0012112 | -0.0084681 | -0.0054367 | -0.00052119 | -0.036621 | 0.10529 | -0.3891 | 55.0735 | 54.776 | 54.8767 | 54.7897 | 55.0598 | 54.9637 | 8.4961 | 67.836 | -54.7806 | 68.1885 | 123.2986 | -0.10986 | 76.7212 | 0.07782 | 0.35248 | 123.0148 | 123.2849 | 123.0011 | 68.3304 | 68.1885 | 123.1888 | 123.1018 | 76.7212 | 68.3304 | 68.1885 | 123.1018 | 123.0011 | 123.1888 | -55.275 | -46.3898
5214.7656 | 123.3124 | -68.3395 | 54.8813 | 0.18669 | -0.008216 | -0.023306 | 0.0084018 | -0.0078271 | -0.0062911 | -0.0024438 | -0.036621 | 0.21515 | -0.36621 | 55.0232 | 54.6753 | 54.7577 | 54.9088 | 54.9637 | 54.9957 | 8.4732 | 67.9733 | -54.6661 | 68.3029 | 123.3627 | -0.20599 | 76.8127 | 0.11444 | 0.32959 | 123.2483 | 123.3032 | 123.0148 | 68.5547 | 68.3029 | 123.3353 | 123.0972 | 76.8127 | 68.5547 | 68.3029 | 123.0972 | 123.0148 | 123.3353 | -55.2475 | -46.4081
5215.7812 | 123.317 | -68.2251 | 54.8904 | 0.072251 | -0.0090704 | -0.026724 | 0.0086154 | -0.0056909 | -0.0056503 | -0.0043664 | 0.013733 | 0.2243 | -0.3479 | 55.0507 | 54.7302 | 54.7989 | 54.9316 | 54.9866 | 54.982 | 8.4732 | 67.8772 | -54.6661 | 68.2388 | 123.2758 | -0.16022 | 76.6983 | 0.091553 | 0.36163 | 123.1567 | 123.2117 | 122.9553 | 68.4494 | 68.2388 | 123.2071 | 123.024 | 76.6983 | 68.4494 | 68.2388 | 123.024 | 122.9553 | 123.2071 | -55.2383 | -46.4172
5216.7812 | 123.3444 | -68.2434 | 54.895 | -0.62202 | -0.0084296 | -0.02352 | 0.0064792 | -0.0093225 | -0.0073593 | -0.00052119 | 0.059509 | 0.2655 | -0.29297 | 55.0827 | 54.7897 | 54.8584 | 54.9088 | 55.0461 | 55.0049 | 8.4778 | 67.9504 | -54.6295 | 68.3029 | 123.3261 | -0.10529 | 76.7212 | 0.10986 | 0.35248 | 123.1522 | 123.2895 | 123.0331 | 68.5089 | 68.3029 | 123.2483 | 123.1018 | 76.7212 | 68.5089 | 68.3029 | 123.1018 | 123.0331 | 123.2483 | -55.188 | -46.4172
5217.7812 | 123.3124 | -68.2343 | 54.9042 | 0.049362 | -0.0077888 | -0.024161 | 0.0069064 | -0.0046229 | -0.0071457 | -0.0032984 | 0.036621 | 0.2243 | -0.34332 | 55.0598 | 54.7714 | 54.8218 | 54.9088 | 55.0095 | 55.0186 | 8.4824 | 67.8909 | -54.6799 | 68.2709 | 123.2941 | -0.13275 | 76.7166 | 0.11444 | 0.37994 | 123.143 | 123.2437 | 123.0057 | 68.4586 | 68.2709 | 123.2529 | 123.056 | 76.7166 | 68.4586 | 68.2709 | 123.056 | 123.0057 | 123.2529 | -55.2475 | -46.4218
5218.7812 | 123.3627 | -68.248 | 54.8721 | 0.14092 | -0.012916 | -0.027365 | -0.0020658 | -0.0069727 | -0.0073593 | -0.00073479 | -0.059509 | 0.15106 | -0.35248 | 55.0735 | 54.8035 | 54.8859 | 54.8172 | 55.0598 | 54.9454 | 8.4869 | 67.8955 | -54.7211 | 68.1885 | 123.3215 | -0.068664 | 76.7349 | 0.073243 | 0.29297 | 123.0652 | 123.3078 | 123.0515 | 68.399 | 68.1885 | 123.1934 | 123.1338 | 76.7349 | 68.399 | 68.1885 | 123.1338 | 123.0515 | 123.1934 | -55.2246 | -46.3852
5219.7656 | 123.2803 | -68.2526 | 54.9088 | 0.087509 | -0.008216 | -0.026511 | 0.0081882 | -0.0093225 | -0.0054367 | 0.00011961 | -0.018311 | 0.2243 | -0.35706 | 55.0323 | 54.7348 | 54.7897 | 54.9179 | 54.9545 | 54.9683 | 8.4869 | 67.8955 | -54.6844 | 68.2343 | 123.2849 | -0.17395 | 76.7395 | 0.05951 | 0.33874 | 123.1705 | 123.2071 | 122.9874 | 68.4769 | 68.2343 | 123.2208 | 123.0423 | 76.7395 | 68.4769 | 68.2343 | 123.0423 | 122.9874 | 123.2208 | -55.2658 | -46.4218
5220.7656 | 123.3124 | -68.2434 | 54.8904 | 0.11803 | -0.007575 | -0.022665 | 0.0073336 | -0.0050501 | -0.0071457 | -0.0020166 | 0.009155 | 0.21973 | -0.35248 | 55.0369 | 54.7348 | 54.7989 | 54.9271 | 54.9866 | 55.0049 | 8.4869 | 67.8909 | -54.6707 | 68.2526 | 123.2803 | -0.15564 | 76.7303 | 0.11444 | 0.36163 | 123.1705 | 123.23 | 122.9782 | 68.4631 | 68.2526 | 123.2483 | 123.0423 | 76.7303 | 68.4631 | 68.2526 | 123.0423 | 122.9782 | 123.2483 | -55.2429 | -46.4035
5221.7656 | 123.317 | -68.2526 | 54.8904 | 0.11803 | -0.0062934 | -0.024802 | 0.0066928 | -0.0056909 | -0.0062911 | -0.0028712 | 0.027466 | 0.24719 | -0.35248 | 55.0552 | 54.7485 | 54.8172 | 54.9042 | 54.9911 | 54.9866 | 8.4778 | 67.9001 | -54.6433 | 68.28 | 123.3078 | -0.14191 | 76.7303 | 0.09613 | 0.37994 | 123.1567 | 123.2437 | 123.0011 | 68.4998 | 68.28 | 123.2391 | 123.0698 | 76.7303 | 68.4998 | 68.28 | 123.0698 | 123.0011 | 123.2391 | -55.2429 | -46.4127
5222.7812 | 123.349 | -68.2434 | 54.9088 | -0.11848 | -0.010352 | -0.026724 | 0.0066928 | -0.0067591 | -0.0052231 | -0.0013758 | 0.059509 | 0.28381 | -0.32044 | 55.0964 | 54.8355 | 54.863 | 54.9362 | 55.0415 | 55.0461 | 8.4915 | 67.923 | -54.6249 | 68.3029 | 123.3398 | -0.073242 | 76.7349 | 0.13733 | 0.37994 | 123.1796 | 123.2849 | 123.0789 | 68.5272 | 68.3029 | 123.2895 | 123.1064 | 76.7349 | 68.5272 | 68.3029 | 123.1064 | 123.0789 | 123.2895 | -55.2292 | -46.4172
5223.7812 | 123.3765 | -68.2343 | 54.8492 | 0.2401 | -0.010779 | -0.023306 | -0.00057036 | -0.0088953 | -0.0050095 | -0.0020166 | -0.032043 | 0.13275 | -0.37994 | 55.0827 | 54.8264 | 54.8904 | 54.776 | 55.0552 | 54.95 | 8.4961 | 67.8543 | -54.7165 | 68.2022 | 123.317 | -0.022888 | 76.7303 | 0.10071 | 0.3479 | 123.0103 | 123.2895 | 123.0606 | 68.367 | 68.2022 | 123.1842 | 123.1247 | 76.7303 | 68.367 | 68.2022 | 123.1247 | 123.0606 | 123.1842 | -55.2292 | -46.3531
5224.7812 | 123.3444 | -68.2617 | 54.9179 | -0.10323 | -0.0090704 | -0.023734 | 0.0075472 | -0.0088953 | -0.0084273 | -0.0022302 | 0.059509 | 0.24719 | -0.31586 | 55.101 | 54.8218 | 54.8584 | 54.9271 | 55.0598 | 55.0095 | 8.4824 | 67.9459 | -54.6707 | 68.3212 | 123.3627 | -0.096131 | 76.7441 | 0.091552 | 0.37537 | 123.1888 | 123.3215 | 123.0835 | 68.5089 | 68.3212 | 123.2712 | 123.1201 | 76.7441 | 68.5089 | 68.3212 | 123.1201 | 123.0835 | 123.2712 | -55.2338 | -46.4355
5225.7812 | 123.349 | -68.2205 | 54.9225 | -0.13374 | -0.0071478 | -0.023093 | 0.0069064 | -0.0097497 | -0.0067185 | -0.003512 | 0.041199 | 0.29755 | -0.3067 | 55.0964 | 54.808 | 54.8584 | 54.9316 | 55.0552 | 55.014 | 8.4869 | 67.9138 | -54.6249 | 68.2617 | 123.317 | -0.11444 | 76.7075 | 0.091553 | 0.3479 | 123.1522 | 123.2758 | 123.0286 | 68.5181 | 68.2617 | 123.2346 | 123.0789 | 76.7075 | 68.5181 | 68.2617 | 123.0789 | 123.0286 | 123.2346 | -55.2292 | -46.4355
5226.7656 | 123.3353 | -68.248 | 54.9088 | -0.072708 | -0.011207 | -0.025656 | 0.00712 | -0.0067591 | -0.0075729 | -0.0028712 | 0.045776 | 0.23804 | -0.30212 | 55.0873 | 54.8126 | 54.8584 | 54.9133 | 55.0323 | 55.0049 | 8.4824 | 67.9459 | -54.6707 | 68.2938 | 123.3353 | -0.09613 | 76.7303 | 0.096131 | 0.3479 | 123.1613 | 123.2803 | 123.0606 | 68.486 | 68.2938 | 123.2529 | 123.1064 | 76.7303 | 68.486 | 68.2938 | 123.1064 | 123.0606 | 123.2529 | -55.2109 | -46.4264
5227.7656 | 123.3307 | -68.2251 | 54.9179 | -0.04982 | -0.0097114 | -0.027365 | 0.0073336 | -0.0078271 | -0.0062911 | -0.0032984 | 0.041199 | 0.23346 | -0.3479 | 55.1331 | 54.8401 | 54.8309 | 54.9179 | 55.0278 | 55.0049 | 8.4915 | 67.8772 | -54.6844 | 68.2663 | 123.3582 | -0.07782 | 76.7166 | 0.086975 | 0.3891 | 123.143 | 123.2529 | 123.0652 | 68.4586 | 68.2663 | 123.23 | 123.056 | 76.7166 | 68.4586 | 68.2663 | 123.056 | 123.0652 | 123.23 | -55.2658 | -46.4264
5228.7812 | 123.4131 | -68.2205 | 54.8813 | -0.034561 | -0.011848 | -0.023734 | -0.0035612 | -0.011031 | -0.0069321 | -0.00094839 | 0 | 0.19684 | -0.31586 | 55.1239 | 54.8859 | 54.9271 | 54.8035 | 55.1285 | 54.9957 | 8.4915 | 67.9047 | -54.6844 | 68.2205 | 123.3444 | 0.004577 | 76.712 | 0.11444 | 0.31586 | 123.024 | 123.349 | 123.1064 | 68.4174 | 68.2205 | 123.2162 | 123.1476 | 76.712 | 68.4174 | 68.2205 | 123.1476 | 123.1064 | 123.2162 | -55.1971 | -46.3898
5229.7812 | 123.2941 | -68.248 | 54.9316 | 0.17143 | -0.0090704 | -0.021811 | 0.005411 | -0.011031 | -0.0060775 | -0.0015894 | -0.009155 | 0.32044 | -0.29297 | 55.0507 | 54.7852 | 54.8264 | 55.0049 | 55.0278 | 55.0323 | 8.4824 | 67.955 | -54.6112 | 68.2388 | 123.2986 | -0.14648 | 76.7303 | 0.10071 | 0.28381 | 123.2529 | 123.2758 | 123.0331 | 68.5684 | 68.2388 | 123.2803 | 123.0743 | 76.7303 | 68.5684 | 68.2388 | 123.0743 | 123.0331 | 123.2803 | -55.2246 | -46.4493
5230.7812 | 123.3124 | -68.2434 | 54.9454 | -0.095596 | -0.010566 | -0.024802 | 0.0064792 | -0.0093225 | -0.0062911 | -0.0043664 | 0.041199 | 0.27008 | -0.29297 | 55.0827 | 54.7897 | 54.8172 | 55.0003 | 55.0415 | 55.0186 | 8.4869 | 67.9504 | -54.6753 | 68.2846 | 123.3261 | -0.15564 | 76.7303 | 0.073242 | 0.33417 | 123.2437 | 123.2849 | 123.0331 | 68.5135 | 68.2846 | 123.262 | 123.0606 | 76.7303 | 68.5135 | 68.2846 | 123.0606 | 123.0331 | 123.262 | -55.2383 | -46.4584
5231.7812 | 123.3444 | -68.2297 | 54.9225 | -0.14137 | -0.009284 | -0.025229 | 0.00712 | -0.0076135 | -0.0058639 | -0.0043664 | 0.059509 | 0.29297 | -0.31128 | 55.101 | 54.7989 | 54.8447 | 54.9545 | 55.0507 | 55.0461 | 8.4824 | 67.9184 | -54.6295 | 68.2892 | 123.3307 | -0.1236 | 76.712 | 0.1236 | 0.37079 | 123.1842 | 123.2803 | 123.0286 | 68.5226 | 68.2892 | 123.2758 | 123.0743 | 76.712 | 68.5226 | 68.2892 | 123.0743 | 123.0286 | 123.2758 | -55.2338 | -46.4401
5232.7812 | 123.3353 | -68.2251 | 54.9316 | -0.16426 | -0.009925 | -0.025015 | 0.0066928 | -0.0088953 | -0.0075729 | -0.0011622 | 0.022888 | 0.30212 | -0.30212 | 55.0735 | 54.7943 | 54.8218 | 54.9683 | 55.0461 | 55.0186 | 8.4869 | 67.923 | -54.6295 | 68.248 | 123.2986 | -0.13733 | 76.712 | 0.086975 | 0.32501 | 123.1934 | 123.2712 | 123.0194 | 68.5272 | 68.248 | 123.2437 | 123.0469 | 76.712 | 68.5272 | 68.248 | 123.0469 | 123.0194 | 123.2437 | -55.2338 | -46.4447
5233.7969 | 123.2941 | -68.2663 | 54.9362 | -0.11085 | -0.010566 | -0.022025 | 0.0041292 | -0.0091089 | -0.0058639 | -0.0026574 | 0.004578 | 0.3067 | -0.27466 | 55.0735 | 54.7806 | 54.8035 | 55.0049 | 55.0369 | 55.014 | 8.4915 | 67.9916 | -54.6295 | 68.2709 | 123.3398 | -0.15564 | 76.7578 | 0.07782 | 0.27924 | 123.2712 | 123.3032 | 123.0469 | 68.573 | 68.2709 | 123.2803 | 123.0698 | 76.7578 | 68.573 | 68.2709 | 123.0698 | 123.0469 | 123.2803 | -55.2109 | -46.4447
5234.7812 | 123.3353 | -68.2434 | 54.9042 | -0.11848 | -0.0094976 | -0.02822 | 0.0039156 | -0.0093225 | -0.0069321 | -0.0054346 | 0.032043 | 0.27008 | -0.30212 | 55.0964 | 54.8035 | 54.8538 | 54.95 | 55.0552 | 55.0186 | 8.4824 | 67.9413 | -54.6341 | 68.2755 | 123.3398 | -0.10071 | 76.7258 | 0.11444 | 0.33417 | 123.1934 | 123.2986 | 123.0469 | 68.5135 | 68.2755 | 123.262 | 123.0972 | 76.7258 | 68.5135 | 68.2755 | 123.0972 | 123.0469 | 123.262 | -55.2063 | -46.4218
5235.7812 | 123.2986 | -68.2434 | 54.8996 | 0.1104 | -0.008216 | -0.025229 | 0.0066928 | -0.0052637 | -0.0067185 | -0.001803 | 0.036621 | 0.23346 | -0.34332 | 55.0598 | 54.7485 | 54.8035 | 54.9225 | 54.9774 | 54.9866 | 8.4869 | 67.9001 | -54.6661 | 68.28 | 123.3032 | -0.15106 | 76.7303 | 0.086975 | 0.37994 | 123.1659 | 123.2208 | 122.9919 | 68.4769 | 68.28 | 123.23 | 123.0469 | 76.7303 | 68.4769 | 68.28 | 123.0469 | 122.9919 | 123.23 | -55.2429 | -46.4127
5236.7812 | 123.3536 | -68.2526 | 54.9225 | -0.14137 | -0.008216 | -0.020956 | 0.0066928 | -0.0071863 | -0.0090683 | -0.001803 | 0.068665 | 0.2655 | -0.31128 | 55.0919 | 54.808 | 54.8538 | 54.9225 | 55.0644 | 55.0232 | 8.4915 | 67.9413 | -54.657 | 68.3212 | 123.3444 | -0.11444 | 76.7441 | 0.10071 | 0.37994 | 123.175 | 123.317 | 123.0606 | 68.5181 | 68.3212 | 123.2758 | 123.1064 | 76.7441 | 68.5181 | 68.3212 | 123.1064 | 123.0606 | 123.2758 | -55.2338 | -46.431
5237.7812 | 123.3444 | -68.2434 | 54.9225 | -0.04982 | -0.011207 | -0.024588 | 0.008829 | -0.0078271 | -0.0052231 | -0.0026574 | 0.064087 | 0.27924 | -0.32959 | 55.1056 | 54.5792 | 54.6844 | 55.0323 | 55.069 | 55.0049 | 8.4824 | 67.9138 | -54.6432 | 68.3075 | 123.349 | -0.34332 | 76.7258 | 0.082398 | 0.39368 | 123.2758 | 123.3124 | 122.8226 | 68.5226 | 68.3075 | 123.2483 | 122.9279 | 76.7258 | 68.5226 | 68.3075 | 122.9279 | 122.8226 | 123.2483 | -55.2521 | -46.4401
5238.7969 | 123.3398 | -68.2434 | 54.8904 | -0.149 | -0.0088568 | -0.024588 | 0.0041292 | -0.0099633 | -0.0054367 | -0.0028712 | 0.032043 | 0.29297 | -0.29297 | 55.101 | 54.7577 | 54.8538 | 54.9591 | 55.0507 | 55.0323 | 8.4824 | 67.9504 | -54.5975 | 68.2755 | 123.3444 | -0.13275 | 76.7258 | 0.14191 | 0.32501 | 123.2025 | 123.2941 | 123.0011 | 68.5364 | 68.2755 | 123.2758 | 123.0972 | 76.7258 | 68.5364 | 68.2755 | 123.0972 | 123.0011 | 123.2758 | -55.1834 | -46.4081
5239.7812 | 123.3032 | -68.28 | 54.9179 | -0.57625 | -0.0086432 | -0.025656 | 0.0056246 | -0.0065455 | -0.0035141 | -0.0028712 | -0.054932 | 0.19226 | -0.37994 | 55.014 | 54.6982 | 54.776 | 54.8996 | 54.9591 | 55.0003 | 8.4915 | 67.9001 | -54.7256 | 68.2251 | 123.2941 | -0.21973 | 76.7715 | 0.082397 | 0.32501 | 123.1796 | 123.2391 | 122.9782 | 68.4723 | 68.2251 | 123.2803 | 123.056 | 76.7715 | 68.4723 | 68.2251 | 123.056 | 122.9782 | 123.2803 | -55.2979 | -46.4264
5240.7812 | 123.2941 | -68.2846 | 54.8996 | 0.14092 | -0.0097114 | -0.028006 | 0.0081882 | -0.0063317 | -0.0056503 | -0.0020166 | 0.004578 | 0.23804 | -0.32959 | 55.0323 | 54.7211 | 54.7943 | 54.9408 | 54.9728 | 55.0278 | 8.4824 | 67.955 | -54.6616 | 68.2892 | 123.317 | -0.17853 | 76.767 | 0.12817 | 0.33417 | 123.2254 | 123.2574 | 123.0057 | 68.5226 | 68.2892 | 123.3124 | 123.0789 | 76.767 | 68.5226 | 68.2892 | 123.0789 | 123.0057 | 123.3124 | -55.2292 | -46.4172
5241.7812 | 123.4039 | -68.2617 | 54.8721 | 0.011215 | -0.012061 | -0.02822 | -0.0050566 | -0.0080407 | -0.0045821 | -0.00030759 | -0.018311 | 0.17853 | -0.32044 | 55.0827 | 54.8218 | 54.9042 | 54.8309 | 55.0964 | 54.9957 | 8.4915 | 67.9413 | -54.6936 | 68.2434 | 123.3444 | -0.050354 | 76.7532 | 0.1236 | 0.30212 | 123.0927 | 123.3582 | 123.0835 | 68.4402 | 68.2434 | 123.2574 | 123.1659 | 76.7532 | 68.4402 | 68.2434 | 123.1659 | 123.0835 | 123.2574 | -55.1926 | -46.3806
5242.7812 | 123.3444 | -68.2251 | 54.9133 | -0.026932 | -0.0071478 | -0.020316 | 0.0084018 | -0.010177 | -0.0060775 | -0.0028712 | 0.064087 | 0.24261 | -0.32044 | 55.0003 | 54.7852 | 54.8996 | 54.9866 | 55.0735 | 55.0049 | 8.4732 | 67.9047 | -54.6707 | 68.2892 | 123.2254 | -0.12817 | 76.6983 | 0.091553 | 0.38452 | 123.2117 | 123.2986 | 123.0103 | 68.4677 | 68.2892 | 123.23 | 123.1247 | 76.6983 | 68.4677 | 68.2892 | 123.1247 | 123.0103 | 123.23 | -55.2338 | -46.4401
5243.7969 | 123.3261 | -68.2526 | 54.9179 | -0.14137 | -0.0090704 | -0.024374 | 0.0064792 | -0.0080407 | -0.0062911 | -0.0022302 | 0.050354 | 0.28839 | -0.3067 | 55.0827 | 54.7897 | 54.8584 | 54.95 | 55.0369 | 55.0232 | 8.4869 | 67.9459 | -54.6295 | 68.3029 | 123.3353 | -0.12817 | 76.7395 | 0.10529 | 0.35706 | 123.2025 | 123.2895 | 123.0423 | 68.541 | 68.3029 | 123.2758 | 123.111 | 76.7395 | 68.541 | 68.3029 | 123.111 | 123.0423 | 123.2758 | -55.2246 | -46.431
5244.7812 | 123.3215 | -68.2526 | 54.9179 | -0.17189 | -0.0097114 | -0.025015 | 0.0047702 | -0.0095361 | -0.0050095 | -0.0039392 | 0.036621 | 0.27924 | -0.32959 | 55.0735 | 54.7714 | 54.8264 | 54.982 | 55.0323 | 55.014 | 8.4915 | 67.923 | -54.6387 | 68.2892 | 123.3261 | -0.14648 | 76.7441 | 0.09613 | 0.36621 | 123.2346 | 123.2849 | 123.024 | 68.5318 | 68.2892 | 123.2666 | 123.0789 | 76.7441 | 68.5318 | 68.2892 | 123.0789 | 123.024 | 123.2666 | -55.2475 | -46.4264
5245.7812 | 123.2895 | -68.2617 | 54.9179 | 0.064621 | -0.007575 | -0.028433 | 0.0073336 | -0.0052637 | -0.0080001 | -0.001803 | 0 | 0.22888 | -0.35248 | 55.0278 | 54.7028 | 54.7897 | 54.9454 | 54.9774 | 55.0186 | 8.4824 | 67.9092 | -54.689 | 68.2617 | 123.2895 | -0.21515 | 76.7441 | 0.10071 | 0.35248 | 123.2071 | 123.2391 | 122.9645 | 68.4906 | 68.2617 | 123.2803 | 123.0515 | 76.7441 | 68.4906 | 68.2617 | 123.0515 | 122.9645 | 123.2803 | -55.2704 | -46.4355
5246.7812 | 123.3398 | -68.248 | 54.9088 | -0.63728 | -0.0088568 | -0.022025 | 0.0062656 | -0.0059045 | -0.0088547 | -0.0011622 | 0.027466 | 0.24261 | -0.27924 | 55.0735 | 54.7714 | 54.8584 | 54.9179 | 55.0369 | 55.0049 | 8.4824 | 67.9688 | -54.6661 | 68.2755 | 123.3215 | -0.13733 | 76.7303 | 0.096131 | 0.3067 | 123.1659 | 123.2849 | 123.0194 | 68.4906 | 68.2755 | 123.2529 | 123.1064 | 76.7303 | 68.4906 | 68.2755 | 123.1064 | 123.0194 | 123.2529 | -55.188 | -46.4264
5247.7812 | 123.3353 | -68.2617 | 54.8447 | 0.2401 | -0.008216 | -0.02117 | 0.0045566 | -0.0063317 | -0.0058639 | -0.0024438 | -0.032043 | 0.19226 | -0.36621 | 55.0369 | 54.7577 | 54.8218 | 54.8492 | 54.9866 | 54.9774 | 8.4915 | 67.8955 | -54.6524 | 68.2297 | 123.2986 | -0.086976 | 76.7532 | 0.13275 | 0.33417 | 123.111 | 123.2483 | 123.0194 | 68.454 | 68.2297 | 123.2391 | 123.0835 | 76.7532 | 68.454 | 68.2297 | 123.0835 | 123.0194 | 123.2391 | -55.2109 | -46.3531
5248.8281 | 123.3765 | -68.2343 | 54.8492 | 0.14092 | -0.012702 | -0.027792 | -0.004202 | -0.0086817 | -0.0075729 | 0.00033321 | -0.022888 | 0.16937 | -0.34332 | 55.0598 | 54.8035 | 54.8813 | 55.0781 | 55.1193 | 54.9774 | 8.4869 | 67.8909 | -54.6799 | 68.2114 | 123.2941 | -0.045776 | 76.7212 | 0.12817 | 0.32043 | 123.3124 | 123.3536 | 123.0377 | 68.4036 | 68.2114 | 123.2117 | 123.1155 | 76.7212 | 68.4036 | 68.2114 | 123.1155 | 123.0377 | 123.2117 | -55.1926 | -46.3623
5249.7812 | 123.2803 | -68.2617 | 54.895 | 0.13329 | -0.0094976 | -0.021384 | 0.0075472 | -0.0076135 | -0.0047957 | -0.001803 | -0.018311 | 0.21973 | -0.35248 | 55.0415 | 54.7165 | 54.776 | 54.9454 | 54.9408 | 54.9911 | 8.4778 | 67.9092 | -54.6753 | 68.2434 | 123.3032 | -0.17853 | 76.7395 | 0.09613 | 0.33417 | 123.2071 | 123.2025 | 122.9782 | 68.4814 | 68.2434 | 123.2529 | 123.0377 | 76.7395 | 68.4814 | 68.2434 | 123.0377 | 122.9782 | 123.2529 | -55.2475 | -46.4172
5250.7812 | 123.3444 | -68.2388 | 54.8904 | -0.11848 | -0.008216 | -0.025443 | 0.0056246 | -0.0067591 | -0.0050095 | -0.0026574 | 0.050354 | 0.28381 | -0.28381 | 55.1056 | 54.7943 | 54.8401 | 54.9591 | 55.0507 | 55.0232 | 8.4869 | 67.955 | -54.6066 | 68.2892 | 123.3444 | -0.09613 | 76.7258 | 0.13275 | 0.33417 | 123.1979 | 123.2895 | 123.0331 | 68.5226 | 68.2892 | 123.262 | 123.0789 | 76.7258 | 68.5226 | 68.2892 | 123.0789 | 123.0331 | 123.262 | -55.1743 | -46.4035
5251.7812 | 123.3536 | -68.2434 | 54.895 | -0.072708 | -0.0090704 | -0.024588 | 0.00712 | -0.0095361 | -0.0071457 | -0.0028712 | 0.054932 | 0.25635 | -0.3067 | 55.101 | 54.8126 | 54.8721 | 54.9225 | 55.0507 | 55.0369 | 8.4869 | 67.9367 | -54.6387 | 68.2983 | 123.3444 | -0.082398 | 76.7303 | 0.14191 | 0.36163 | 123.1659 | 123.2941 | 123.056 | 68.4998 | 68.2983 | 123.2803 | 123.1155 | 76.7303 | 68.4998 | 68.2983 | 123.1155 | 123.056 | 123.2803 | -55.2017 | -46.4081
5252.7812 | 123.3398 | -68.2571 | 54.9362 | -0.12611 | -0.0077888 | -0.025229 | 0.0084018 | -0.0080407 | -0.0062911 | -0.0024438 | 0.059509 | 0.26093 | -0.3067 | 55.0827 | 54.8264 | 54.8492 | 54.9408 | 55.0507 | 55.0232 | 8.4915 | 67.9504 | -54.6753 | 68.3167 | 123.3398 | -0.10986 | 76.7487 | 0.086975 | 0.36621 | 123.1979 | 123.3078 | 123.0835 | 68.5181 | 68.3167 | 123.2803 | 123.1064 | 76.7487 | 68.5181 | 68.3167 | 123.1064 | 123.0835 | 123.2803 | -55.2429 | -46.4447
5253.7969 | 123.3673 | -68.2251 | 54.9179 | -0.149 | -0.013343 | -0.025656 | 7.0444e-05 | -0.0093225 | -0.0062911 | -0.0028712 | 0.050354 | 0.22888 | -0.27008 | 55.1102 | 54.8721 | 54.9042 | 54.9042 | 55.1193 | 55.0095 | 8.4869 | 67.955 | -54.689 | 68.2755 | 123.3353 | -0.045777 | 76.712 | 0.091552 | 0.32044 | 123.1293 | 123.3444 | 123.0972 | 68.454 | 68.2755 | 123.2346 | 123.1293 | 76.712 | 68.454 | 68.2755 | 123.1293 | 123.0972 | 123.2346 | -55.188 | -46.431
5254.7812 | 123.349 | -68.2388 | 54.9408 | -0.057449 | -0.013343 | -0.016684 | 0.0075472 | -0.010604 | -0.0058639 | -9.3992e-05 | -0.032043 | 0.26093 | -0.28381 | 55.101 | 54.7897 | 54.863 | 54.9133 | 55.0415 | 54.9866 | 8.4824 | 67.955 | -54.6799 | 68.2068 | 123.3398 | -0.15106 | 76.7212 | 0.045776 | 0.25177 | 123.1522 | 123.2803 | 123.0286 | 68.4998 | 68.2068 | 123.2254 | 123.1018 | 76.7212 | 68.4998 | 68.2068 | 123.1018 | 123.0286 | 123.2254 | -55.2246 | -46.4584
5255.7812 | 123.2986 | -68.2663 | 54.9042 | 0.2401 | -0.009925 | -0.025229 | 0.0084018 | -0.0086817 | -0.0054367 | -0.006289 | -0.054932 | 0.21057 | -0.37537 | 55.2292 | 54.9042 | 54.8172 | 54.9683 | 54.9454 | 55.0232 | 8.4961 | 67.8909 | -54.6936 | 68.2114 | 123.4955 | 0 | 76.7624 | 0.11902 | 0.32043 | 123.2346 | 123.2117 | 123.1705 | 68.4769 | 68.2114 | 123.2895 | 123.0835 | 76.7624 | 68.4769 | 68.2114 | 123.0835 | 123.1705 | 123.2895 | -55.2795 | -46.4081
5256.7812 | 123.2986 | -68.2617 | 54.895 | 0.072251 | -0.0073614 | -0.02117 | 0.005411 | -0.0071863 | -0.0069321 | -0.00052119 | 0.027466 | 0.2243 | -0.33417 | 55.0552 | 54.776 | 54.808 | 54.9271 | 54.9957 | 55.0095 | 8.4778 | 67.9276 | -54.6707 | 68.2892 | 123.317 | -0.11902 | 76.7395 | 0.11444 | 0.36163 | 123.1888 | 123.2574 | 123.0377 | 68.486 | 68.2892 | 123.2712 | 123.0698 | 76.7395 | 68.486 | 68.2892 | 123.0698 | 123.0377 | 123.2712 | -55.2292 | -46.4172
5257.7812 | 123.3398 | -68.248 | 54.895 | 0.23247 | -0.011207 | -0.021811 | 0.0069064 | -0.0067591 | -0.0071457 | -0.0011622 | -0.036621 | 0.19684 | -0.36621 | 55.0507 | 54.7806 | 54.8126 | 54.8492 | 54.9637 | 54.9957 | 8.4824 | 67.8818 | -54.6982 | 68.2114 | 123.2986 | -0.11444 | 76.7303 | 0.10071 | 0.32959 | 123.0972 | 123.2117 | 123.0286 | 68.4448 | 68.2114 | 123.2437 | 123.0606 | 76.7303 | 68.4448 | 68.2114 | 123.0606 | 123.0286 | 123.2437 | -55.2612 | -46.4127
5258.7969 | 123.3719 | -68.2343 | 54.8492 | 0.10277 | -0.012275 | -0.027792 | -0.004202 | -0.0088953 | -0.0077865 | -0.00073479 | -0.032043 | 0.14648 | -0.33417 | 55.0598 | 54.8355 | 54.8767 | 54.8172 | 55.0369 | 54.9683 | 8.4824 | 67.9001 | -54.7028 | 68.2022 | 123.2941 | -0.013733 | 76.7166 | 0.11902 | 0.30212 | 123.0515 | 123.2712 | 123.0698 | 68.3807 | 68.2022 | 123.2025 | 123.111 | 76.7166 | 68.3807 | 68.2022 | 123.111 | 123.0698 | 123.2025 | -55.1834 | -46.3669
5259.7812 | 123.3765 | -68.2526 | 54.8721 | 0.27061 | -0.0077888 | -0.026511 | 0.0041292 | -0.0080407 | -0.0056503 | -0.0022302 | -0.032043 | 0.18768 | -0.37994 | 55.0598 | 54.808 | 54.8309 | 54.8172 | 55.0186 | 54.9591 | 8.4915 | 67.8726 | -54.6844 | 68.2205 | 123.3124 | -0.064087 | 76.7441 | 0.086975 | 0.3479 | 123.0698 | 123.2712 | 123.0606 | 68.4402 | 68.2205 | 123.2117 | 123.0835 | 76.7441 | 68.4402 | 68.2205 | 123.0835 | 123.0606 | 123.2117 | -55.2521 | -46.3806
5260.7812 | 123.2986 | -68.2755 | 54.895 | 2.712 | -0.010139 | -0.026938 | 0.0077608 | -0.0095361 | -0.0052231 | -0.001803 | 0.10071 | 0.17853 | -0.37079 | 55.0278 | 54.776 | 54.776 | 54.8996 | 54.95 | 54.982 | 8.4824 | 67.9047 | -54.7165 | 68.3762 | 123.3032 | -0.11902 | 76.7578 | 0.086975 | 0.4715 | 123.175 | 123.2254 | 123.0515 | 68.454 | 68.3762 | 123.2574 | 123.0515 | 76.7578 | 68.454 | 68.3762 | 123.0515 | 123.0515 | 123.2574 | -55.2658 | -46.4127
5261.7812 | 123.4314 | -68.2434 | 54.8584 | 0.24773 | -0.012488 | -0.023734 | 0.0013522 | -0.0078271 | -0.0052231 | -0.00073479 | 0 | 0.11902 | -0.35706 | 55.101 | 54.8996 | 54.9316 | 54.7348 | 55.0781 | 54.9637 | 8.4915 | 67.8864 | -54.7394 | 68.2434 | 123.3444 | 0.041199 | 76.7349 | 0.10529 | 0.35706 | 122.9782 | 123.3215 | 123.143 | 68.3624 | 68.2434 | 123.2071 | 123.175 | 76.7349 | 68.3624 | 68.2434 | 123.175 | 123.143 | 123.2071 | -55.2155 | -46.3669
5262.7812 | 123.3902 | -68.2526 | 54.8584 | 0.27061 | -0.0071478 | -0.02352 | 0.0064792 | -0.0082545 | -0.0069321 | -0.0022302 | -0.027466 | 0.18768 | -0.38452 | 55.0598 | 54.7943 | 54.8309 | 54.8264 | 55.0186 | 54.9637 | 8.4869 | 67.868 | -54.6707 | 68.2251 | 123.3124 | -0.064086 | 76.7395 | 0.10529 | 0.35706 | 123.0789 | 123.2712 | 123.0469 | 68.4402 | 68.2251 | 123.2162 | 123.0835 | 76.7395 | 68.4402 | 68.2251 | 123.0835 | 123.0469 | 123.2162 | -55.2429 | -46.3715
5263.7969 | 123.4268 | -68.2159 | 54.8721 | -0.019302 | -0.012275 | -0.030997 | -0.0029202 | -0.010604 | -0.0050095 | -0.0022302 | 0 | 0.19226 | -0.33417 | 55.1376 | 54.8904 | 54.9316 | 54.8172 | 55.1239 | 54.982 | 8.4915 | 67.8818 | -54.6799 | 68.2159 | 123.3536 | 0.018311 | 76.7075 | 0.10986 | 0.33417 | 123.0331 | 123.3398 | 123.1064 | 68.4082 | 68.2159 | 123.1979 | 123.1476 | 76.7075 | 68.4082 | 68.2159 | 123.1476 | 123.1064 | 123.1979 | -55.2063 | -46.3806
5264.7969 | 123.3902 | -68.2388 | 54.8309 | 0.20958 | -0.010779 | -0.032706 | 0.002634 | -0.011459 | -0.0060775 | -0.0011622 | -0.022888 | 0.14191 | -0.36163 | 55.1147 | 54.8447 | 54.895 | 54.7485 | 55.0781 | 54.9088 | 8.4824 | 67.8772 | -54.689 | 68.2159 | 123.3536 | 0.013733 | 76.7212 | 0.077819 | 0.33874 | 122.9874 | 123.317 | 123.0835 | 68.3807 | 68.2159 | 123.1476 | 123.1339 | 76.7212 | 68.3807 | 68.2159 | 123.1339 | 123.0835 | 123.1476 | -55.1926 | -46.3486
5265.7812 | 123.3948 | -68.1976 | 54.9042 | -0.15663 | -0.013984 | -0.02587 | 0.002634 | -0.010604 | -0.0067185 | -0.0032984 | 0.07782 | 0.21515 | -0.28839 | 55.1559 | 54.8859 | 54.9225 | 54.8676 | 55.1331 | 54.9637 | 8.4915 | 67.9092 | -54.689 | 68.2755 | 123.3536 | -0.018311 | 76.6891 | 0.059509 | 0.36621 | 123.0652 | 123.3307 | 123.0835 | 68.4128 | 68.2755 | 123.1613 | 123.1201 | 76.6891 | 68.4128 | 68.2755 | 123.1201 | 123.0835 | 123.1613 | -55.1926 | -46.4127
5266.7812 | 123.4268 | -68.2068 | 54.8767 | -0.072708 | -0.011207 | -0.029074 | -0.00099756 | -0.01274 | -0.0073593 | -0.0026574 | 0.064087 | 0.17853 | -0.29755 | 55.1651 | 54.9179 | 54.9591 | 54.7897 | 55.1743 | 54.9545 | 8.4869 | 67.9092 | -54.6982 | 68.2709 | 123.3719 | 0.041199 | 76.6937 | 0.07782 | 0.36163 | 122.9965 | 123.381 | 123.1247 | 68.3853 | 68.2709 | 123.1613 | 123.1659 | 76.6937 | 68.3853 | 68.2709 | 123.1659 | 123.1247 | 123.1613 | -55.1743 | -46.3898
5267.7812 | 123.3719 | -68.2205 | 54.9133 | -0.18715 | -0.012702 | -0.027792 | 0.0047702 | -0.012954 | -0.0067185 | -0.0026574 | 0.073242 | 0.24261 | -0.28839 | 55.1376 | 54.8492 | 54.8904 | 54.895 | 55.1147 | 54.9774 | 8.4915 | 67.9321 | -54.6707 | 68.2938 | 123.3582 | -0.064087 | 76.712 | 0.064087 | 0.36163 | 123.1155 | 123.3353 | 123.0698 | 68.4631 | 68.2938 | 123.1979 | 123.111 | 76.712 | 68.4631 | 68.2938 | 123.111 | 123.0698 | 123.1979 | -55.2017 | -46.4218
5268.7812 | 123.3307 | -68.2526 | 54.9271 | -0.16426 | -0.010779 | -0.029929 | 0.0045566 | -0.011886 | -0.0065047 | -0.0039392 | 0.050354 | 0.25177 | -0.28381 | 55.0827 | 54.7852 | 54.8355 | 55.0186 | 55.0323 | 55.0003 | 8.4869 | 67.9688 | -54.6753 | 68.3029 | 123.3353 | -0.14191 | 76.7395 | 0.073242 | 0.33417 | 123.2712 | 123.2849 | 123.0377 | 68.5043 | 68.3029 | 123.2529 | 123.0881 | 76.7395 | 68.5043 | 68.3029 | 123.0881 | 123.0377 | 123.2529 | -55.2109 | -46.4401
5269.7812 | 123.3582 | -68.248 | 54.9454 | -0.17189 | -0.011634 | -0.021597 | 0.0028476 | -0.012527 | -0.0050095 | -0.003512 | 0.07782 | 0.23804 | -0.27924 | 55.1147 | 54.8584 | 54.863 | 54.9225 | 55.0735 | 54.9911 | 8.4869 | 67.9688 | -54.7073 | 68.3258 | 123.3627 | -0.086976 | 76.7349 | 0.045776 | 0.35706 | 123.1705 | 123.3215 | 123.1064 | 68.486 | 68.3258 | 123.2391 | 123.111 | 76.7349 | 68.486 | 68.3258 | 123.111 | 123.1064 | 123.2391 | -55.2246 | -46.4584
5270.7812 | 123.3215 | -68.2571 | 54.95 | -0.19478 | -0.009284 | -0.028647 | 0.0069064 | -0.012313 | -0.0077865 | -0.0030848 | 0.009155 | 0.27008 | -0.29755 | 55.0919 | 54.8035 | 54.8126 | 54.9957 | 55.0369 | 54.9957 | 8.4824 | 67.9596 | -54.6799 | 68.2663 | 123.349 | -0.14648 | 76.7395 | 0.045777 | 0.3067 | 123.2529 | 123.2941 | 123.0606 | 68.5272 | 68.2663 | 123.2529 | 123.0698 | 76.7395 | 68.5272 | 68.2663 | 123.0698 | 123.0606 | 123.2529 | -55.2475 | -46.4676
5271.7812 | 123.4314 | -68.2434 | 54.9088 | -0.095596 | -0.012275 | -0.027152 | 0.0069064 | -0.011886 | -0.0058639 | -0.0020166 | -0.11902 | 0.21973 | -0.28839 | 55.1376 | 54.9362 | 54.8996 | 54.8035 | 55.1331 | 54.9637 | 8.4915 | 67.955 | -54.689 | 68.1244 | 123.381 | 0.027466 | 76.7349 | 0.054932 | 0.16937 | 123.0469 | 123.3765 | 123.1796 | 68.4631 | 68.1244 | 123.2071 | 123.143 | 76.7349 | 68.4631 | 68.1244 | 123.143 | 123.1796 | 123.2071 | -55.1971 | -46.4172
5272.7812 | 123.3994 | -68.2297 | 54.895 | -0.04219 | -0.014411 | -0.029501 | 0.00092504 | -0.012313 | -0.0060775 | -0.0022302 | 0.018311 | 0.19684 | -0.29755 | 55.1514 | 54.8813 | 54.9179 | 54.7989 | 55.1285 | 54.982 | 8.4869 | 67.9321 | -54.6982 | 68.248 | 123.381 | -0.013733 | 76.7166 | 0.086975 | 0.31586 | 123.0286 | 123.3582 | 123.111 | 68.4265 | 68.248 | 123.2117 | 123.1476 | 76.7166 | 68.4265 | 68.248 | 123.1476 | 123.111 | 123.2117 | -55.1926 | -46.4081
5273.7812 | 123.317 | -68.2526 | 54.9454 | -0.20241 | -0.010779 | -0.023306 | 0.0086154 | -0.011245 | -0.0077865 | -0.00458 | 0.036621 | 0.28839 | -0.32501 | 55.0873 | 54.8126 | 54.808 | 54.9637 | 55.0323 | 55.0003 | 8.4824 | 67.9276 | -54.657 | 68.2892 | 123.3398 | -0.13275 | 76.7349 | 0.054931 | 0.36163 | 123.2162 | 123.2849 | 123.0652 | 68.541 | 68.2892 | 123.2529 | 123.0606 | 76.7349 | 68.541 | 68.2892 | 123.0606 | 123.0652 | 123.2529 | -55.2704 | -46.463
5274.7812 | 123.4085 | -68.248 | 54.895 | 0.072251 | -0.012916 | -0.030142 | 7.0444e-05 | -0.012313 | -0.0082137 | -0.0028712 | -0.022888 | 0.1831 | -0.34332 | 55.1147 | 54.8676 | 54.8813 | 54.8172 | 55.0781 | 54.9408 | 8.4915 | 67.9047 | -54.7119 | 68.2251 | 123.3627 | -0.027466 | 76.7395 | 0.045776 | 0.32043 | 123.0652 | 123.3261 | 123.1155 | 68.4311 | 68.2251 | 123.1888 | 123.1293 | 76.7395 | 68.4311 | 68.2251 | 123.1293 | 123.1155 | 123.1888 | -55.2383 | -46.4035
5275.7812 | 123.4314 | -68.1839 | 54.9179 | -0.10323 | -0.012916 | -0.026297 | 0.00028404 | -0.011245 | -0.0047957 | -0.0028712 | 0.073242 | 0.20142 | -0.28381 | 55.1834 | 54.9133 | 54.9408 | 54.7852 | 55.1651 | 54.9454 | 8.4915 | 67.9001 | -54.7165 | 68.2571 | 123.3673 | -0.004578 | 76.6754 | 0.027466 | 0.35706 | 122.9691 | 123.349 | 123.0972 | 68.3853 | 68.2571 | 123.1293 | 123.1247 | 76.6754 | 68.3853 | 68.2571 | 123.1247 | 123.0972 | 123.1293 | -55.2017 | -46.4264
5276.7812 | 123.4406 | -68.2205 | 54.8859 | -0.057449 | -0.014411 | -0.026724 | 0.0022066 | -0.0121 | -0.0060775 | -0.0028712 | 0.041199 | 0.19684 | -0.31128 | 55.1651 | 54.8904 | 54.9271 | 54.8172 | 55.1605 | 54.9637 | 8.4824 | 67.9092 | -54.689 | 68.2617 | 123.3856 | 0.004578 | 76.7029 | 0.07782 | 0.35248 | 123.0377 | 123.381 | 123.111 | 68.4174 | 68.2617 | 123.1842 | 123.1476 | 76.7029 | 68.4174 | 68.2617 | 123.1476 | 123.111 | 123.1842 | -55.1971 | -46.4035
5277.7812 | 123.4314 | -68.2022 | 54.8676 | -0.080337 | -0.01377 | -0.03356 | 0.001993 | -0.012954 | -0.0075729 | -0.0026574 | 0.07782 | 0.17853 | -0.27924 | 55.4031 | 55.2795 | 55.0369 | 54.5334 | 55.1285 | 54.9362 | 8.4915 | 67.923 | -54.689 | 68.28 | 123.6053 | 0.41199 | 76.6937 | 0.068664 | 0.35706 | 122.7356 | 123.3307 | 123.4818 | 68.3807 | 68.28 | 123.1384 | 123.2391 | 76.6937 | 68.3807 | 68.28 | 123.2391 | 123.4818 | 123.1384 | -55.1468 | -46.376
5278.7812 | 123.3536 | -68.2251 | 54.9362 | -0.17952 | -0.013129 | -0.025229 | 0.0056246 | -0.012313 | -0.0060775 | -0.0028712 | 0.082397 | 0.21057 | -0.28839 | 55.1514 | 54.8859 | 54.8904 | 54.8996 | 55.1193 | 54.9637 | 8.4915 | 67.9367 | -54.7256 | 68.3075 | 123.3765 | -0.050354 | 76.7166 | 0.027466 | 0.37079 | 123.1247 | 123.3444 | 123.111 | 68.4357 | 68.3075 | 123.1888 | 123.1155 | 76.7166 | 68.4357 | 68.3075 | 123.1155 | 123.111 | 123.1888 | -55.2246 | -46.4447
5279.7812 | 123.4268 | -68.2159 | 54.8904 | -0.0040434 | -0.014838 | -0.026724 | 0.001993 | -0.011459 | -0.0054367 | -0.0030848 | 0.027466 | 0.18768 | -0.31128 | 55.1559 | 54.8996 | 54.9133 | 54.7897 | 55.1285 | 54.9545 | 8.4915 | 67.9047 | -54.7028 | 68.2434 | 123.3719 | 0.009155 | 76.7075 | 0.064087 | 0.33874 | 123.0057 | 123.3444 | 123.1155 | 68.4036 | 68.2434 | 123.1705 | 123.1293 | 76.7075 | 68.4036 | 68.2434 | 123.1293 | 123.1155 | 123.1705 | -55.2017 | -46.3989
5280.7812 | 123.4177 | -68.2205 | 54.8904 | -0.12611 | -0.013129 | -0.031851 | 0.0028476 | -0.012527 | -0.0062911 | -0.0022302 | 0.082397 | 0.17853 | -0.29297 | 55.1697 | 54.9042 | 54.9271 | 54.8264 | 55.1605 | 54.9454 | 8.4869 | 67.9276 | -54.7119 | 68.3029 | 123.3902 | 0.013733 | 76.7075 | 0.054932 | 0.37537 | 123.0469 | 123.381 | 123.1247 | 68.399 | 68.3029 | 123.1659 | 123.1476 | 76.7075 | 68.399 | 68.3029 | 123.1476 | 123.1247 | 123.1659 | -55.1834 | -46.4035
5281.7812 | 123.3444 | -68.2297 | 54.8813 | 0.087509 | -0.0094976 | -0.025015 | 0.011606 | -0.0121 | -0.0056503 | -0.0028712 | 0.073242 | 0.23346 | -0.3067 | 55.1331 | 54.808 | 54.8355 | 54.9042 | 55.0186 | 54.9728 | 8.4824 | 67.923 | -54.6478 | 68.3029 | 123.3627 | -0.073243 | 76.712 | 0.091552 | 0.37994 | 123.1338 | 123.2483 | 123.0377 | 68.4631 | 68.3029 | 123.2025 | 123.0652 | 76.712 | 68.4631 | 68.3029 | 123.0652 | 123.0377 | 123.2025 | -55.188 | -46.3989
5282.7812 | 123.4085 | -68.2343 | 54.8584 | 2.2314 | -0.011207 | -0.022879 | 0.0060518 | -0.0095361 | -0.0060775 | -0.0022302 | -0.086975 | 0.086975 | -0.38452 | 55.1468 | 54.8813 | 54.9225 | 54.7073 | 55.0552 | 54.9225 | 8.4824 | 67.8497 | -54.7714 | 68.1473 | 123.381 | 0.022889 | 76.7166 | 0.064087 | 0.29755 | 122.9416 | 123.2895 | 123.1155 | 68.3212 | 68.1473 | 123.1567 | 123.1567 | 76.7166 | 68.3212 | 68.1473 | 123.1567 | 123.1155 | 123.1567 | -55.2429 | -46.376
5283.7812 | 123.3353 | -68.248 | 54.9133 | -0.14137 | -0.0094976 | -0.024161 | 0.0064792 | -0.0078271 | -0.0077865 | -0.0043664 | 0.041199 | 0.29297 | -0.31128 | 55.1239 | 54.8355 | 54.8447 | 54.9591 | 55.0415 | 55.0232 | 8.4732 | 67.9367 | -54.6204 | 68.2892 | 123.3719 | -0.07782 | 76.7212 | 0.10986 | 0.35248 | 123.2071 | 123.2895 | 123.0835 | 68.541 | 68.2892 | 123.2712 | 123.0927 | 76.7212 | 68.541 | 68.2892 | 123.0927 | 123.0835 | 123.2712 | -55.2246 | -46.4401
5284.7812 | 123.3902 | -68.2388 | 54.895 | 0.2401 | -0.01142 | -0.026511 | 0.00092504 | -0.010818 | -0.0050095 | -0.0043664 | -0.036621 | 0.19226 | -0.31586 | 55.1056 | 54.8676 | 54.8859 | 54.8264 | 55.0781 | 54.9408 | 8.4869 | 67.923 | -54.7028 | 68.2022 | 123.3444 | -0.027466 | 76.7258 | 0.045776 | 0.27924 | 123.0652 | 123.317 | 123.1064 | 68.4311 | 68.2022 | 123.1796 | 123.1247 | 76.7258 | 68.4311 | 68.2022 | 123.1247 | 123.1064 | 123.1796 | -55.2109 | -46.4081
5285.7812 | 123.3627 | -68.2114 | 54.8676 | 0.041733 | -0.012275 | -0.024374 | 0.00028404 | -0.0121 | -0.0086411 | -0.00693 | -0.045776 | 0.17853 | -0.32044 | 55.2521 | 54.895 | 54.8218 | 54.776 | 55.0186 | 54.9133 | 8.4824 | 67.8909 | -54.689 | 68.1656 | 123.4634 | 0.027466 | 76.6937 | 0.045776 | 0.27466 | 122.9874 | 123.23 | 123.1064 | 68.3899 | 68.1656 | 123.1247 | 123.0331 | 76.6937 | 68.3899 | 68.1656 | 123.0331 | 123.1064 | 123.1247 | -55.188 | -46.3852
5286.7812 | 123.349 | -68.2297 | 54.8904 | -0.17952 | -0.0094976 | -0.024802 | 0.004343 | -0.011031 | -0.0060775 | -0.0032984 | 0.064087 | 0.23804 | -0.27466 | 55.1331 | 54.863 | 54.8767 | 54.9179 | 55.0781 | 54.9683 | 8.4869 | 67.955 | -54.6524 | 68.2938 | 123.3627 | -0.027466 | 76.7166 | 0.07782 | 0.33875 | 123.1476 | 123.3078 | 123.0927 | 68.4677 | 68.2938 | 123.1979 | 123.1064 | 76.7166 | 68.4677 | 68.2938 | 123.1064 | 123.0927 | 123.1979 | -55.1651 | -46.4035
5287.7812 | 123.3673 | -68.2434 | 54.8676 | 0.20958 | -0.0094976 | -0.029288 | 0.0039156 | -0.0097497 | -0.0073593 | -0.0024438 | -0.045776 | 0.11902 | -0.38452 | 55.101 | 54.8447 | 54.8859 | 54.7806 | 55.0552 | 54.9133 | 8.4824 | 67.8589 | -54.7485 | 68.1976 | 123.3444 | -0.022888 | 76.7258 | 0.045776 | 0.33875 | 123.024 | 123.2986 | 123.0881 | 68.3624 | 68.1976 | 123.1567 | 123.1293 | 76.7258 | 68.3624 | 68.1976 | 123.1293 | 123.0881 | 123.1567 | -55.2521 | -46.3852
5288.7812 | 123.4451 | -68.1839 | 54.8904 | -0.095596 | -0.010993 | -0.024161 | 0.00071144 | -0.011886 | -0.0094955 | -0.0024438 | 0.068665 | 0.18768 | -0.28381 | 55.1697 | 54.9133 | 54.9591 | 54.7989 | 55.1788 | 54.9316 | 8.4915 | 67.9001 | -54.7028 | 68.2526 | 123.3536 | 0.022888 | 76.6754 | 0.041199 | 0.35248 | 122.9828 | 123.3627 | 123.0972 | 68.3716 | 68.2526 | 123.1155 | 123.143 | 76.6754 | 68.3716 | 68.2526 | 123.143 | 123.0972 | 123.1155 | -55.1743 | -46.3989
5289.7812 | 123.4177 | -68.2526 | 54.8447 | 0.13329 | -0.010352 | -0.026297 | 0.005411 | -0.010818 | -0.0069321 | -0.0013758 | 0.036621 | 0.11902 | -0.33875 | 55.1376 | 54.8538 | 54.9133 | 54.7394 | 55.0735 | 54.8859 | 8.4915 | 67.9138 | -54.7256 | 68.2892 | 123.3902 | 0.009155 | 76.7441 | 0.041198 | 0.37537 | 122.9919 | 123.3261 | 123.1064 | 68.3716 | 68.2892 | 123.1384 | 123.1659 | 76.7441 | 68.3716 | 68.2892 | 123.1659 | 123.1064 | 123.1384 | -55.1834 | -46.3531
5290.7812 | 123.4039 | -68.2297 | 54.8721 | 0.25536 | -0.010566 | -0.025229 | 0.0028476 | -0.011245 | -0.0056503 | -0.0020166 | 0 | 0.14648 | -0.34332 | 55.1376 | 54.8721 | 54.9088 | 54.7394 | 55.0552 | 54.8996 | 8.4915 | 67.8864 | -54.7256 | 68.2297 | 123.3673 | 0 | 76.7212 | 0.027466 | 0.34332 | 122.9691 | 123.2849 | 123.1018 | 68.3762 | 68.2297 | 123.1293 | 123.1384 | 76.7212 | 68.3762 | 68.2297 | 123.1384 | 123.1018 | 123.1293 | -55.2155 | -46.3806
5291.7812 | 123.4085 | -68.2068 | 54.8859 | -0.12611 | -0.012061 | -0.028433 | 0.0028476 | -0.011245 | -0.0062911 | -0.0030848 | 0.059509 | 0.20599 | -0.29755 | 55.1743 | 54.9042 | 54.9316 | 54.8492 | 55.1422 | 54.9637 | 8.4869 | 67.9092 | -54.6799 | 68.2663 | 123.381 | 0.018311 | 76.6937 | 0.07782 | 0.35705 | 123.056 | 123.349 | 123.111 | 68.4128 | 68.2663 | 123.1705 | 123.1384 | 76.6937 | 68.4128 | 68.2663 | 123.1384 | 123.111 | 123.1705 | -55.1834 | -46.3989
5292.7812 | 123.3124 | -68.2571 | 54.8676 | 0.18669 | -0.010779 | -0.027579 | 0.0081882 | -0.0095361 | -0.0043685 | -0.001803 | -0.027466 | 0.21515 | -0.37537 | 55.0644 | 54.7668 | 54.7989 | 54.8721 | 54.9591 | 54.9683 | 8.4869 | 67.8818 | -54.6524 | 68.2297 | 123.3215 | -0.10071 | 76.7441 | 0.10071 | 0.3479 | 123.1293 | 123.2162 | 123.024 | 68.4723 | 68.2297 | 123.2254 | 123.056 | 76.7441 | 68.4723 | 68.2297 | 123.056 | 123.024 | 123.2254 | -55.2429 | -46.3806
5293.7812 | 123.5229 | -68.1747 | 54.9042 | -0.11085 | -0.012916 | -0.024802 | 0.0011386 | -0.010177 | -0.0062911 | -0.0026574 | 0.059509 | 0.18768 | -0.28381 | 55.1971 | 54.9408 | 54.9637 | 54.7989 | 55.1697 | 54.9316 | 8.5007 | 67.8909 | -54.7165 | 68.2343 | 123.3719 | 0.036621 | 76.6754 | 0.027466 | 0.34332 | 122.9736 | 123.3444 | 123.1155 | 68.3624 | 68.2343 | 123.1064 | 123.1384 | 76.6754 | 68.3624 | 68.2343 | 123.1384 | 123.1155 | 123.1064 | -55.188 | -46.4035
5294.7812 | 123.3261 | -68.248 | 54.9042 | 0.11803 | -0.010352 | -0.026083 | 0.0098972 | -0.0080407 | -0.0071457 | -0.00458 | 0.036621 | 0.2243 | -0.32501 | 55.0781 | 54.7989 | 54.8355 | 54.8996 | 55.0003 | 54.95 | 8.4778 | 67.923 | -54.6799 | 68.2846 | 123.3261 | -0.10529 | 76.7258 | 0.045776 | 0.36163 | 123.1476 | 123.2483 | 123.0469 | 68.4723 | 68.2846 | 123.1979 | 123.0835 | 76.7258 | 68.4723 | 68.2846 | 123.0835 | 123.0469 | 123.1979 | -55.2292 | -46.4264
5295.7812 | 123.4222 | -68.2343 | 54.8401 | 0.28587 | -0.010566 | -0.023734 | 0.0032748 | -0.0097497 | -0.0054367 | -0.0015894 | -0.009155 | 0.11902 | -0.37079 | 55.1376 | 54.8721 | 54.9088 | 54.7302 | 55.0598 | 54.9225 | 8.4915 | 67.8635 | -54.7211 | 68.2251 | 123.3719 | 0.032043 | 76.7258 | 0.082397 | 0.36163 | 122.9645 | 123.2941 | 123.1064 | 68.3533 | 68.2251 | 123.1567 | 123.143 | 76.7258 | 68.3533 | 68.2251 | 123.143 | 123.1064 | 123.1567 | -55.2109 | -46.3486
5296.7812 | 123.4131 | -68.1976 | 54.8996 | -0.16426 | -0.010352 | -0.024802 | 0.002634 | -0.011672 | -0.0065047 | -0.003512 | 0.054932 | 0.20599 | -0.27924 | 55.1743 | 54.8996 | 54.9591 | 54.8309 | 55.1605 | 54.9591 | 8.4961 | 67.9184 | -54.6936 | 68.2526 | 123.3719 | 0 | 76.6937 | 0.059509 | 0.33417 | 123.0286 | 123.3582 | 123.0972 | 68.4036 | 68.2526 | 123.1567 | 123.1567 | 76.6937 | 68.4036 | 68.2526 | 123.1567 | 123.0972 | 123.1567 | -55.1788 | -46.4035
5297.7812 | 123.3948 | -68.2388 | 54.8492 | 0.22484 | -0.012916 | -0.023947 | 0.005411 | -0.011459 | -0.0062911 | -0.0026574 | -0.009155 | 0.12817 | -0.36621 | 55.1147 | 54.8447 | 54.9179 | 54.7531 | 55.0598 | 54.9179 | 8.4824 | 67.8726 | -54.7211 | 68.2297 | 123.3536 | -0.004577 | 76.7212 | 0.068665 | 0.35706 | 122.9919 | 123.2986 | 123.0835 | 68.367 | 68.2297 | 123.1567 | 123.1567 | 76.7212 | 68.367 | 68.2297 | 123.1567 | 123.0835 | 123.1567 | -55.2155 | -46.3669
5298.7812 | 123.4085 | -68.2617 | 54.8538 | 0.22484 | -0.0086432 | -0.027365 | 0.0049838 | -0.010177 | -0.0043685 | -0.0015894 | 0 | 0.11902 | -0.37079 | 55.1422 | 54.8492 | 54.9225 | 54.7394 | 55.069 | 54.8904 | 8.4915 | 67.8909 | -54.7348 | 68.2617 | 123.4039 | -0.004578 | 76.7532 | 0.036621 | 0.37079 | 123.0011 | 123.3307 | 123.111 | 68.3807 | 68.2617 | 123.1522 | 123.1842 | 76.7532 | 68.3807 | 68.2617 | 123.1842 | 123.111 | 123.1522 | -55.2246 | -46.3623
5299.7812 | 123.3261 | -68.2617 | 54.9179 | 0.14092 | -0.009925 | -0.024161 | 0.011606 | -0.0084681 | -0.0067185 | -0.003512 | 0.013733 | 0.21973 | -0.33875 | 55.0644 | 54.7668 | 54.8126 | 54.9316 | 54.9774 | 54.9637 | 8.4824 | 67.923 | -54.6982 | 68.2755 | 123.3261 | -0.15106 | 76.7441 | 0.045776 | 0.35248 | 123.1934 | 123.2391 | 123.0286 | 68.4814 | 68.2755 | 123.2254 | 123.0743 | 76.7441 | 68.4814 | 68.2755 | 123.0743 | 123.0286 | 123.2254 | -55.2567 | -46.4355
5300.7812 | 123.3261 | -68.2388 | 54.8904 | 0.041733 | -0.009284 | -0.024161 | 0.0090426 | -0.0063317 | -0.0071457 | -0.0028712 | 0.018311 | 0.23346 | -0.32501 | 55.0827 | 54.7577 | 54.8309 | 54.9225 | 54.9866 | 54.9728 | 8.4824 | 67.9138 | -54.657 | 68.2571 | 123.3215 | -0.13275 | 76.7212 | 0.082397 | 0.34332 | 123.1613 | 123.2254 | 122.9965 | 68.4723 | 68.2571 | 123.2117 | 123.0698 | 76.7212 | 68.4723 | 68.2571 | 123.0698 | 122.9965 | 123.2117 | -55.2155 | -46.4081
5301.7812 | 123.4085 | -68.2251 | 54.8538 | 0.2401 | -0.009925 | -0.024161 | 0.0030612 | -0.0093225 | -0.0062911 | -0.0028712 | -0.022888 | 0.10986 | -0.37537 | 55.1056 | 54.8355 | 54.8996 | 54.7302 | 55.0644 | 54.9271 | 8.4961 | 67.8497 | -54.744 | 68.2022 | 123.3307 | -0.018311 | 76.7212 | 0.073242 | 0.35248 | 122.9553 | 123.2895 | 123.0606 | 68.335 | 68.2022 | 123.1522 | 123.1247 | 76.7212 | 68.335 | 68.2022 | 123.1247 | 123.0606 | 123.1522 | -55.2292 | -46.3577
5302.7812 | 123.3032 | -68.28 | 54.9133 | 0.11803 | -0.0073614 | -0.026938 | 0.0098972 | -0.0078271 | -0.0065047 | -0.0028712 | -0.013733 | 0.21057 | -0.35706 | 55.0644 | 54.7211 | 54.7806 | 54.9271 | 54.9591 | 55.0049 | 8.4778 | 67.923 | -54.7028 | 68.2663 | 123.3444 | -0.19226 | 76.7578 | 0.091553 | 0.34332 | 123.2071 | 123.2391 | 123.0011 | 68.4906 | 68.2663 | 123.2849 | 123.0606 | 76.7578 | 68.4906 | 68.2663 | 123.0606 | 123.0011 | 123.2849 | -55.2704 | -46.4355
5303.7812 | 123.2986 | -68.2114 | 54.9088 | 0.22484 | -0.012702 | -0.026724 | 0.0024202 | -0.0093225 | -0.0077865 | -0.0020166 | -0.018311 | 0.11902 | -0.36621 | 55.101 | 54.8584 | 54.9088 | 54.7485 | 55.069 | 54.9179 | 8.5007 | 67.8452 | -54.7897 | 68.1931 | 123.3124 | -0.050354 | 76.712 | 0.009156 | 0.3479 | 122.9599 | 123.2803 | 123.0698 | 68.3304 | 68.1931 | 123.1293 | 123.1201 | 76.712 | 68.3304 | 68.1931 | 123.1201 | 123.0698 | 123.1293 | -55.275 | -46.4081
5304.7812 | 123.3307 | -68.2343 | 54.9088 | -0.13374 | -0.010566 | -0.027792 | 0.0041292 | -0.013809 | -0.0060775 | -0.0024438 | 0.054932 | 0.27466 | -0.3479 | 55.1605 | 54.8309 | 54.808 | 54.9911 | 55.0919 | 54.9911 | 8.4824 | 67.8864 | -54.6341 | 68.2892 | 123.3948 | -0.077819 | 76.7166 | 0.082398 | 0.40283 | 123.2254 | 123.3261 | 123.0652 | 68.5089 | 68.2892 | 123.2254 | 123.0423 | 76.7166 | 68.5089 | 68.2892 | 123.0423 | 123.0652 | 123.2254 | -55.2567 | -46.4264
5305.7812 | 123.2849 | -68.28 | 54.9088 | -0.2253 | -0.0088568 | -0.027792 | 0.0096834 | -0.0069727 | -0.0084273 | -0.0026574 | -0.041199 | 0.19684 | -0.37079 | 55.0232 | 54.7302 | 54.7943 | 54.9225 | 54.9362 | 54.9774 | 8.4824 | 67.9092 | -54.7119 | 68.2388 | 123.3032 | -0.17853 | 76.7624 | 0.068665 | 0.32959 | 123.2025 | 123.2162 | 123.0103 | 68.4769 | 68.2388 | 123.2574 | 123.0743 | 76.7624 | 68.4769 | 68.2388 | 123.0743 | 123.0103 | 123.2574 | -55.2795 | -46.4264
5306.7812 | 123.4131 | -68.2251 | 54.8676 | -0.10323 | -0.013984 | -0.023734 | 7.0444e-05 | -0.0091089 | -0.0088547 | -0.0011622 | 0.059509 | 0.21515 | -0.27924 | 55.1559 | 54.8859 | 54.9683 | 54.8492 | 55.1468 | 54.9637 | 8.4915 | 67.9459 | -54.6524 | 68.2846 | 123.381 | 0.01831 | 76.7166 | 0.09613 | 0.33874 | 123.0743 | 123.3719 | 123.111 | 68.4402 | 68.2846 | 123.1888 | 123.1934 | 76.7166 | 68.4402 | 68.2846 | 123.1934 | 123.111 | 123.1888 | -55.1468 | -46.376
5307.7812 | 123.3536 | -68.2343 | 54.9225 | -0.149 | -0.009284 | -0.02587 | 0.0047702 | -0.0065455 | -0.0067185 | -0.0024438 | 0.036621 | 0.28381 | -0.29297 | 55.0827 | 54.8126 | 54.8447 | 54.9774 | 55.0415 | 55.0323 | 8.4915 | 67.9413 | -54.6387 | 68.2709 | 123.317 | -0.10986 | 76.7258 | 0.10986 | 0.32959 | 123.2117 | 123.2758 | 123.0469 | 68.5181 | 68.2709 | 123.2666 | 123.0789 | 76.7258 | 68.5181 | 68.2709 | 123.0789 | 123.0469 | 123.2666 | -55.2155 | -46.431
5308.7812 | 123.3444 | -68.28 | 54.8676 | 0.22484 | -0.0073614 | -0.026938 | 0.0075472 | -0.0050501 | -0.0071457 | -0.0013758 | -0.036621 | 0.18768 | -0.36163 | 55.0461 | 54.7714 | 54.8355 | 54.8584 | 54.9774 | 54.982 | 8.4824 | 67.9184 | -54.6799 | 68.2434 | 123.3261 | -0.096131 | 76.7624 | 0.11444 | 0.32501 | 123.1384 | 123.2574 | 123.0515 | 68.4677 | 68.2434 | 123.262 | 123.1155 | 76.7624 | 68.4677 | 68.2434 | 123.1155 | 123.0515 | 123.262 | -55.2292 | -46.3852
5309.7812 | 123.3398 | -68.2434 | 54.9271 | -0.14137 | -0.010352 | -0.029074 | 0.0058382 | -0.010177 | -0.0080001 | -0.0011622 | 0.032043 | 0.27466 | -0.31128 | 55.0598 | 54.7852 | 54.8355 | 54.9911 | 55.0507 | 55.0369 | 8.4915 | 67.9321 | -54.6524 | 68.2755 | 123.3032 | -0.14191 | 76.7349 | 0.10986 | 0.34332 | 123.2346 | 123.2941 | 123.0286 | 68.5181 | 68.2755 | 123.2803 | 123.0789 | 76.7349 | 68.5181 | 68.2755 | 123.0789 | 123.0286 | 123.2803 | -55.2383 | -46.4355
5310.7812 | 123.3627 | -68.2571 | 54.9179 | -0.14137 | -0.0084296 | -0.025656 | 0.0051974 | -0.0099633 | -0.0086411 | -0.0039392 | 0.050354 | 0.28381 | -0.29755 | 55.1102 | 54.7989 | 54.863 | 54.9454 | 55.0507 | 55.0186 | 8.4915 | 67.9596 | -54.6341 | 68.3075 | 123.3673 | -0.11902 | 76.7487 | 0.10071 | 0.3479 | 123.2025 | 123.3078 | 123.056 | 68.541 | 68.3075 | 123.2758 | 123.1201 | 76.7487 | 68.541 | 68.3075 | 123.1201 | 123.056 | 123.2758 | -55.2155 | -46.4264
5311.7812 | 123.3627 | -68.2388 | 54.9088 | -0.080337 | -0.0084296 | -0.022238 | 0.0077608 | -0.0080407 | -0.0077865 | -0.0020166 | 0.068665 | 0.24719 | -0.32959 | 55.101 | 54.7989 | 54.8584 | 54.9316 | 55.0415 | 55.014 | 8.4869 | 67.9092 | -54.6616 | 68.3075 | 123.3398 | -0.10986 | 76.7258 | 0.10529 | 0.39826 | 123.1705 | 123.2803 | 123.0377 | 68.486 | 68.3075 | 123.2529 | 123.0972 | 76.7258 | 68.486 | 68.3075 | 123.0972 | 123.0377 | 123.2529 | -55.2383 | -46.4218
5312.7812 | 123.3261 | -68.2846 | 54.9179 | -0.17189 | -0.0097114 | -0.029074 | 0.0034884 | -0.0088953 | -0.0050095 | -0.0022302 | 0.018311 | 0.28381 | -0.28839 | 55.0095 | 54.7348 | 54.7806 | 54.9957 | 55.0461 | 55.014 | 8.4869 | 67.9962 | -54.6341 | 68.3029 | 123.2941 | -0.18311 | 76.7715 | 0.09613 | 0.3067 | 123.2803 | 123.3307 | 123.0194 | 68.5684 | 68.3029 | 123.2986 | 123.0652 | 76.7715 | 68.5684 | 68.3029 | 123.0652 | 123.0194 | 123.2986 | -55.2063 | -46.431
5313.7812 | 123.3307 | -68.2892 | 54.9042 | 0.23247 | -0.010993 | -0.025443 | 0.0073336 | -0.0071863 | -0.0071457 | -0.0037256 | -0.050354 | 0.17853 | -0.38452 | 54.8538 | 54.5105 | 54.8264 | 55.0095 | 54.9591 | 54.9957 | 8.4869 | 67.9047 | -54.7256 | 68.2388 | 123.143 | -0.39368 | 76.7761 | 0.091553 | 0.33417 | 123.2986 | 123.2483 | 122.7997 | 68.4677 | 68.2388 | 123.2849 | 123.1155 | 76.7761 | 68.4677 | 68.2388 | 123.1155 | 122.7997 | 123.2849 | -55.2887 | -46.4172
5314.7812 | 123.3673 | -68.2388 | 54.8904 | -0.23293 | -0.012061 | -0.028861 | 7.0444e-05 | -0.0080407 | -0.0073593 | -0.0043664 | 0.041199 | 0.21515 | -0.3067 | 55.1102 | 54.808 | 54.8996 | 54.9179 | 55.101 | 55.0323 | 8.4869 | 67.9321 | -54.6753 | 68.28 | 123.349 | -0.082398 | 76.7258 | 0.14191 | 0.3479 | 123.1567 | 123.3398 | 123.0469 | 68.454 | 68.28 | 123.2712 | 123.1384 | 76.7258 | 68.454 | 68.28 | 123.1384 | 123.0469 | 123.2712 | -55.1971 | -46.4035
5315.7812 | 123.436 | -68.2068 | 54.8859 | -0.13374 | -0.014838 | -0.026938 | 0.00071144 | -0.010604 | -0.0077865 | -0.0032984 | 0.068665 | 0.20599 | -0.28839 | 55.1468 | 54.8538 | 54.95 | 54.8447 | 55.1514 | 54.9637 | 8.4824 | 67.9184 | -54.6799 | 68.2755 | 123.3536 | -0.032043 | 76.6891 | 0.07782 | 0.35706 | 123.0515 | 123.3582 | 123.0606 | 68.4128 | 68.2755 | 123.1705 | 123.1567 | 76.6891 | 68.4128 | 68.2755 | 123.1567 | 123.0606 | 123.1705 | -55.1743 | -46.4035
5316.7812 | 123.3353 | -68.2114 | 54.9271 | -0.15663 | -0.013343 | -0.027365 | 0.002634 | -0.011245 | -0.0077865 | -0.0024438 | 0.054932 | 0.2243 | -0.29297 | 55.101 | 54.7989 | 54.8904 | 54.95 | 55.0827 | 54.9911 | 8.4824 | 67.9184 | -54.7028 | 68.2663 | 123.3124 | -0.12817 | 76.6937 | 0.064087 | 0.3479 | 123.1613 | 123.2941 | 123.0103 | 68.4357 | 68.2663 | 123.2025 | 123.1018 | 76.6937 | 68.4357 | 68.2663 | 123.1018 | 123.0103 | 123.2025 | -55.22 | -46.4447
5317.7812 | 123.4177 | -68.1931 | 54.8904 | -0.19478 | -0.011634 | -0.026083 | 0.00028404 | -0.012313 | -0.0084273 | -0.0024438 | 0.073242 | 0.20599 | -0.28839 | 55.1376 | 54.8401 | 54.9408 | 54.8309 | 55.1651 | 54.9454 | 8.4915 | 67.9047 | -54.6844 | 68.2663 | 123.3307 | -0.050354 | 76.6846 | 0.054932 | 0.36163 | 123.024 | 123.3582 | 123.0331 | 68.399 | 68.2663 | 123.1384 | 123.1338 | 76.6846 | 68.399 | 68.2663 | 123.1338 | 123.0331 | 123.1384 | -55.1788 | -46.3989
5318.7812 | 123.2803 | -68.2983 | 54.895 | 0.07988 | -0.0094976 | -0.025229 | 0.010324 | -0.011031 | -0.0052231 | -0.0030848 | -0.032043 | 0.21515 | -0.36621 | 55.0323 | 54.7028 | 54.7852 | 54.9271 | 54.95 | 54.9866 | 8.4824 | 67.9321 | -54.6799 | 68.2663 | 123.3307 | -0.19226 | 76.7807 | 0.091552 | 0.33417 | 123.2254 | 123.2483 | 123.0011 | 68.5135 | 68.2663 | 123.2849 | 123.0835 | 76.7807 | 68.5135 | 68.2663 | 123.0835 | 123.0011 | 123.2849 | -55.2612 | -46.4127
5319.7812 | 123.4589 | -68.2022 | 54.895 | -0.12611 | -0.012061 | -0.026083 | 0.0015658 | -0.011031 | -0.0062911 | -0.0037256 | 0.059509 | 0.19226 | -0.29755 | 55.1651 | 54.8721 | 54.9545 | 54.7989 | 55.1834 | 54.9591 | 8.4961 | 67.9047 | -54.7028 | 68.2617 | 123.3673 | -0.022889 | 76.6983 | 0.064086 | 0.35705 | 123.0011 | 123.3856 | 123.0743 | 68.3945 | 68.2617 | 123.1613 | 123.1567 | 76.6983 | 68.3945 | 68.2617 | 123.1567 | 123.0743 | 123.1613 | -55.1926 | -46.3989
5320.7812 | 123.4268 | -68.1976 | 54.8904 | -0.11848 | -0.012488 | -0.029074 | 0.001993 | -0.013381 | -0.0075729 | -0.0030848 | 0.054932 | 0.20599 | -0.28381 | 55.1743 | 54.8676 | 54.9362 | 54.808 | 55.1651 | 54.9454 | 8.4778 | 67.9138 | -54.6844 | 68.2526 | 123.3719 | -0.022888 | 76.6754 | 0.054932 | 0.33874 | 123.0057 | 123.3627 | 123.0652 | 68.4036 | 68.2526 | 123.143 | 123.1338 | 76.6754 | 68.4036 | 68.2526 | 123.1338 | 123.0652 | 123.143 | -55.1743 | -46.4127
5321.7812 | 123.3261 | -68.2434 | 54.9408 | -0.2253 | -0.0077888 | -0.026724 | 0.0077608 | -0.010604 | -0.0071457 | -0.0011622 | 0.032043 | 0.28839 | -0.28839 | 55.0873 | 54.776 | 54.8309 | 54.9866 | 55.0369 | 55.0003 | 8.4915 | 67.955 | -54.6524 | 68.2755 | 123.3307 | -0.16479 | 76.7349 | 0.059509 | 0.32043 | 123.23 | 123.2803 | 123.0194 | 68.5318 | 68.2755 | 123.2437 | 123.0743 | 76.7349 | 68.5318 | 68.2755 | 123.0743 | 123.0194 | 123.2437 | -55.2292 | -46.4493
5322.7812 | 123.3902 | -68.2297 | 54.9179 | -0.13374 | -0.013343 | -0.027579 | 0.0022066 | -0.011459 | -0.0065047 | -0.0015894 | 0.073242 | 0.21057 | -0.27924 | 55.1559 | 54.8492 | 54.8996 | 54.863 | 55.1102 | 54.9774 | 8.4915 | 67.9504 | -54.7073 | 68.3029 | 123.3856 | -0.068665 | 76.7212 | 0.059509 | 0.35248 | 123.0927 | 123.3398 | 123.0789 | 68.4402 | 68.3029 | 123.2071 | 123.1293 | 76.7212 | 68.4402 | 68.3029 | 123.1293 | 123.0789 | 123.2071 | -55.1971 | -46.4264
5323.7812 | 123.3353 | -68.2663 | 54.9042 | -0.04982 | -0.0080024 | -0.024374 | 0.0098972 | -0.0086817 | -0.0084273 | -0.0015894 | 0.064087 | 0.24261 | -0.3067 | 55.1102 | 54.7211 | 54.8492 | 54.8538 | 54.9133 | 54.9728 | 8.4824 | 67.9596 | -54.6616 | 68.3304 | 123.3765 | -0.18311 | 76.7487 | 0.068664 | 0.37079 | 123.1201 | 123.1796 | 122.9874 | 68.5089 | 68.3304 | 123.2391 | 123.1155 | 76.7487 | 68.5089 | 68.3304 | 123.1155 | 122.9874 | 123.2391 | -55.2109 | -46.4218
5324.7812 | 123.4222 | -68.2251 | 54.8996 | 0.049362 | -0.012702 | -0.031638 | 0.00028404 | -0.013595 | -0.0065047 | -0.0024438 | 0.009155 | 0.20142 | -0.30212 | 55.1422 | 54.7623 | 54.9225 | 54.7943 | 55.1193 | 54.9637 | 8.4915 | 67.923 | -54.6982 | 68.2343 | 123.3673 | -0.13733 | 76.7166 | 0.064087 | 0.31128 | 123.0194 | 123.3444 | 122.9874 | 68.4265 | 68.2343 | 123.1888 | 123.1476 | 76.7166 | 68.4265 | 68.2343 | 123.1476 | 122.9874 | 123.1888 | -55.2017 | -46.4081
5325.7812 | 123.4039 | -68.2205 | 54.9042 | -0.18715 | -0.010352 | -0.027792 | 0.0034884 | -0.012313 | -0.0073593 | -0.0054346 | 0.064087 | 0.20599 | -0.27924 | 55.1605 | 54.7668 | 54.9316 | 54.8447 | 55.1468 | 54.9728 | 8.4869 | 67.9413 | -54.6982 | 68.2846 | 123.381 | -0.13733 | 76.7075 | 0.068664 | 0.34332 | 123.0652 | 123.3673 | 122.9874 | 68.4265 | 68.2846 | 123.1934 | 123.1522 | 76.7075 | 68.4265 | 68.2846 | 123.1522 | 122.9874 | 123.1934 | -55.1834 | -46.4172
5326.7812 | 123.3948 | -68.2343 | 54.8904 | 0.10277 | -0.011634 | -0.02822 | 0.0049838 | -0.012954 | -0.0090683 | -0.0032984 | -0.045776 | 0.16479 | -0.33875 | 55.0873 | 54.744 | 54.8904 | 54.7943 | 55.0598 | 54.95 | 8.4915 | 67.8955 | -54.7256 | 68.1885 | 123.3215 | -0.14648 | 76.7258 | 0.059509 | 0.29297 | 123.0286 | 123.2941 | 122.9782 | 68.399 | 68.1885 | 123.1842 | 123.1247 | 76.7258 | 68.399 | 68.1885 | 123.1247 | 122.9782 | 123.1842 | -55.2292 | -46.3989
5327.7812 | 123.4268 | -68.2388 | 54.8859 | -0.04982 | -0.012702 | -0.026724 | 0.0030612 | -0.012527 | -0.0060775 | -0.0043664 | 0.045776 | 0.18768 | -0.29297 | 55.1697 | 54.8264 | 54.9454 | 54.776 | 55.1743 | 54.9362 | 8.4869 | 67.9459 | -54.6982 | 68.2846 | 123.4085 | -0.059509 | 76.7258 | 0.050354 | 0.33874 | 123.0148 | 123.4131 | 123.0652 | 68.4265 | 68.2846 | 123.175 | 123.1842 | 76.7258 | 68.4265 | 68.2846 | 123.1842 | 123.0652 | 123.175 | -55.1788 | -46.3989
5328.7812 | 123.2803 | -68.2571 | 54.9362 | -0.21004 | -0.010139 | -0.024161 | 0.0047702 | -0.011886 | -0.0082137 | -0.003512 | 0.045776 | 0.3067 | -0.29755 | 55.0873 | 54.7394 | 54.8126 | 55.1743 | 55.2017 | 55.0369 | 8.4778 | 67.9596 | -54.6295 | 68.3029 | 123.3444 | -0.19684 | 76.7349 | 0.10071 | 0.34332 | 123.4314 | 123.4589 | 122.9965 | 68.5638 | 68.3029 | 123.2941 | 123.0698 | 76.7349 | 68.5638 | 68.3029 | 123.0698 | 122.9965 | 123.2941 | -55.2338 | -46.4584
5329.7812 | 123.3032 | -68.2205 | 54.9362 | -0.17189 | -0.010139 | -0.022879 | 0.0041292 | -0.011245 | -0.0092819 | -0.0041528 | 0.022888 | 0.28381 | -0.2655 | 55.0919 | 54.7668 | 54.8172 | 54.95 | 55.0278 | 55.0049 | 8.4869 | 67.955 | -54.6524 | 68.2434 | 123.3124 | -0.16937 | 76.7075 | 0.068665 | 0.28839 | 123.1705 | 123.2483 | 122.9874 | 68.5043 | 68.2434 | 123.2254 | 123.0377 | 76.7075 | 68.5043 | 68.2434 | 123.0377 | 122.9874 | 123.2254 | -55.2017 | -46.4493
5330.7812 | 123.3856 | -68.2526 | 54.895 | 0.22484 | -0.010993 | -0.026938 | 0.0047702 | -0.010391 | -0.0056503 | -0.0022302 | -0.022888 | 0.11444 | -0.38452 | 55.1147 | 54.8264 | 54.863 | 54.7531 | 55.0461 | 54.9316 | 8.4915 | 67.868 | -54.7806 | 68.2297 | 123.3673 | -0.068665 | 76.7441 | 0.036621 | 0.36163 | 123.0057 | 123.2986 | 123.0789 | 68.367 | 68.2297 | 123.1842 | 123.1155 | 76.7441 | 68.367 | 68.2297 | 123.1155 | 123.0789 | 123.1842 | -55.2795 | -46.4035
5331.7812 | 123.3856 | -68.2205 | 54.8813 | -1.7512 | -0.010566 | -0.023734 | 0.00071144 | -0.012954 | -0.0069321 | -0.003512 | 0.022888 | 0.16937 | -0.3067 | 55.1193 | 54.8355 | 54.8447 | 54.808 | 55.0507 | 54.9362 | 8.4869 | 67.9138 | -54.7119 | 68.2434 | 123.3398 | -0.045777 | 76.7075 | 0.054931 | 0.32959 | 123.0286 | 123.2712 | 123.056 | 68.3899 | 68.2434 | 123.1567 | 123.0652 | 76.7075 | 68.3899 | 68.2434 | 123.0652 | 123.056 | 123.1567 | -55.188 | -46.3943
5332.7812 | 123.4314 | -68.2205 | 54.895 | -0.12611 | -0.012916 | -0.025656 | 0.0045566 | -0.018508 | -0.0052231 | -0.001803 | 0.059509 | 0.21057 | -0.28839 | 54.9454 | 54.8676 | 54.9088 | 54.7989 | 55.1743 | 54.9271 | 8.4869 | 67.9321 | -54.6844 | 68.28 | 123.1659 | -0.027466 | 76.7075 | 0.032043 | 0.3479 | 123.0194 | 123.3948 | 123.0881 | 68.4311 | 68.28 | 123.1476 | 123.1293 | 76.7075 | 68.4311 | 68.28 | 123.1293 | 123.0881 | 123.1476 | -55.1834 | -46.4081
5333.7812 | 123.3444 | -68.2297 | 54.9408 | -0.11848 | -0.009284 | -0.019247 | 0.0084018 | -0.0099633 | -0.0069321 | -0.0037256 | 0.073242 | 0.27466 | -0.30212 | 55.1331 | 54.8492 | 54.8538 | 54.9042 | 55.0598 | 54.982 | 8.4732 | 67.9276 | -54.6661 | 68.3029 | 123.3627 | -0.091553 | 76.7029 | 0.041199 | 0.37537 | 123.1338 | 123.2895 | 123.0789 | 68.5043 | 68.3029 | 123.2117 | 123.0835 | 76.7029 | 68.5043 | 68.3029 | 123.0835 | 123.0789 | 123.2117 | -55.2429 | -46.4676
5334.7812 | 123.3627 | -68.2526 | 54.895 | 0.28587 | -0.010779 | -0.023947 | 0.010538 | -0.0093225 | -0.0052231 | -0.0011622 | -0.036621 | 0.16937 | -0.36621 | 55.0827 | 54.8309 | 54.8264 | 54.7806 | 55.0049 | 54.9591 | 8.4824 | 67.8864 | -54.7256 | 68.2159 | 123.3353 | -0.064087 | 76.7349 | 0.064086 | 0.32959 | 123.0331 | 123.2574 | 123.0835 | 68.4219 | 68.2159 | 123.2117 | 123.0789 | 76.7349 | 68.4219 | 68.2159 | 123.0789 | 123.0835 | 123.2117 | -55.2612 | -46.4127
5335.7812 | 123.3994 | -68.2571 | 54.8584 | 0.22484 | -0.010993 | -0.027365 | 0.0017794 | -0.0088953 | -0.0062911 | -0.0037256 | 0 | 0.12817 | -0.37994 | 55.1147 | 54.8859 | 54.895 | 54.7302 | 55.0781 | 54.9271 | 8.4869 | 67.8772 | -54.7302 | 68.2571 | 123.3719 | 0.027466 | 76.7441 | 0.068665 | 0.37994 | 122.9874 | 123.3353 | 123.143 | 68.3853 | 68.2571 | 123.1842 | 123.1522 | 76.7441 | 68.3853 | 68.2571 | 123.1522 | 123.143 | 123.1842 | -55.2383 | -46.3715
5336.7812 | 123.3902 | -68.2434 | 54.863 | 0.14854 | -0.012702 | -0.030997 | 0.0011386 | -0.011245 | -0.011632 | -0.00094839 | -0.036621 | 0.16937 | -0.32501 | 55.1331 | 54.7989 | 54.9042 | 54.744 | 55.0507 | 54.9316 | 8.4824 | 67.9184 | -54.6936 | 68.2068 | 123.3765 | -0.064087 | 76.7258 | 0.068665 | 0.28839 | 122.9874 | 123.2941 | 123.0423 | 68.4128 | 68.2068 | 123.175 | 123.1476 | 76.7258 | 68.4128 | 68.2068 | 123.1476 | 123.0423 | 123.175 | -55.188 | -46.3806
5337.7812 | 123.4039 | -68.2205 | 54.8859 | 0.19432 | -0.011634 | -0.029501 | 0.0041292 | -0.012527 | -0.0084273 | -0.0028712 | -0.032043 | 0.1831 | -0.31586 | 55.0919 | 54.8676 | 54.8813 | 54.7943 | 55.0735 | 54.9591 | 8.4824 | 67.9047 | -54.7028 | 68.1885 | 123.3124 | -0.01831 | 76.7029 | 0.073242 | 0.28381 | 123.0148 | 123.2941 | 123.0881 | 68.4036 | 68.1885 | 123.1796 | 123.1018 | 76.7029 | 68.4036 | 68.1885 | 123.1018 | 123.0881 | 123.1796 | -55.2017 | -46.4035
5338.7812 | 123.349 | -68.2571 | 54.8813 | 0.27061 | -0.0090704 | -0.029929 | 0.0084018 | -0.010604 | -0.0047957 | -0.0028712 | -0.027466 | 0.16479 | -0.36621 | 55.0827 | 54.8035 | 54.8309 | 54.8035 | 54.9957 | 54.9271 | 8.4824 | 67.8909 | -54.7165 | 68.2297 | 123.3398 | -0.07782 | 76.7395 | 0.045776 | 0.33875 | 123.0606 | 123.2529 | 123.0606 | 68.4219 | 68.2297 | 123.1842 | 123.0881 | 76.7395 | 68.4219 | 68.2297 | 123.0881 | 123.0606 | 123.1842 | -55.2475 | -46.3989
5339.7812 | 123.3765 | -68.2343 | 54.8492 | 0.15617 | -0.010139 | -0.02587 | 0.0015658 | -0.0121 | -0.0067185 | -0.003512 | -0.036621 | 0.16022 | -0.32959 | 55.1147 | 54.8309 | 54.8676 | 54.7943 | 55.0507 | 54.9133 | 8.4824 | 67.9047 | -54.689 | 68.1976 | 123.349 | -0.01831 | 76.7166 | 0.064087 | 0.29297 | 123.0286 | 123.2849 | 123.0652 | 68.3945 | 68.1976 | 123.1476 | 123.1018 | 76.7166 | 68.3945 | 68.1976 | 123.1018 | 123.0652 | 123.1476 | -55.1788 | -46.3669
5340.7812 | 123.381 | -68.248 | 54.8767 | 0.18669 | -0.012702 | -0.022879 | 0.0024202 | -0.013595 | -0.0050095 | -0.0022302 | -0.045776 | 0.10529 | -0.36163 | 55.0964 | 54.8492 | 54.8813 | 54.7943 | 55.0552 | 54.9133 | 8.4915 | 67.8864 | -54.7714 | 68.2022 | 123.3444 | -0.027466 | 76.7395 | 0.036621 | 0.31586 | 123.0423 | 123.3032 | 123.0972 | 68.3533 | 68.2022 | 123.1613 | 123.1293 | 76.7395 | 68.3533 | 68.2022 | 123.1293 | 123.0972 | 123.1613 | -55.2383 | -46.3852
5341.7812 | 123.4177 | -68.2297 | 54.8584 | 0.27061 | -0.009925 | -0.025229 | 0.0062656 | -0.010604 | -0.0082137 | -0.0037256 | 0.004578 | 0.17853 | -0.37537 | 55.1285 | 54.8492 | 54.8904 | 54.744 | 55.0095 | 54.9088 | 8.4869 | 67.8543 | -54.6799 | 68.2343 | 123.3582 | -0.009155 | 76.7166 | 0.050354 | 0.37994 | 122.9736 | 123.2391 | 123.0789 | 68.4082 | 68.2343 | 123.1384 | 123.1201 | 76.7166 | 68.4082 | 68.2343 | 123.1201 | 123.0789 | 123.1384 | -55.2338 | -46.3715
5342.7812 | 123.2895 | -68.28 | 54.9042 | 0.13329 | -0.0073614 | -0.024802 | 0.010111 | -0.0088953 | -0.0058639 | -0.0037256 | -0.027466 | 0.21515 | -0.37079 | 55.0415 | 54.7668 | 54.776 | 54.9408 | 54.9454 | 54.9911 | 8.4915 | 67.9092 | -54.689 | 68.2526 | 123.3215 | -0.13733 | 76.7715 | 0.086975 | 0.34332 | 123.2208 | 123.2254 | 123.0469 | 68.4952 | 68.2526 | 123.2712 | 123.056 | 76.7715 | 68.4952 | 68.2526 | 123.056 | 123.0469 | 123.2712 | -55.275 | -46.4127
5343.7812 | 123.4268 | -68.2343 | 54.8492 | 0.59105 | -0.010779 | -0.02587 | 0.0058382 | -0.0071863 | -0.0058639 | -0.0037256 | 0.054932 | 0.09613 | -0.38452 | 55.1376 | 54.8813 | 54.9271 | 54.7302 | 55.0735 | 54.9042 | 8.4915 | 67.8497 | -54.7531 | 68.2892 | 123.3719 | 0.032044 | 76.7258 | 0.054932 | 0.43945 | 122.9645 | 123.3078 | 123.1155 | 68.3304 | 68.2892 | 123.1384 | 123.1613 | 76.7258 | 68.3304 | 68.2892 | 123.1613 | 123.1155 | 123.1384 | -55.2338 | -46.3577
5344.7812 | 123.2986 | -68.2434 | 54.9088 | 0.064621 | -0.010139 | -0.022025 | 0.010324 | -0.0086817 | -0.0075729 | -0.003512 | 0.027466 | 0.23346 | -0.32959 | 55.0919 | 54.8264 | 54.8309 | 54.9088 | 54.9866 | 54.9866 | 8.4869 | 67.9138 | -54.6753 | 68.2709 | 123.3353 | -0.082397 | 76.7303 | 0.07782 | 0.35706 | 123.1522 | 123.23 | 123.0698 | 68.4769 | 68.2709 | 123.23 | 123.0743 | 76.7303 | 68.4769 | 68.2709 | 123.0743 | 123.0698 | 123.23 | -55.2383 | -46.4218
5345.7812 | 123.3032 | -68.2709 | 54.9316 | 0.087509 | -0.0084296 | -0.025229 | 0.0092562 | -0.0061181 | -0.0067185 | -0.0024438 | 0.004578 | 0.2243 | -0.34332 | 55.0552 | 54.8172 | 54.7943 | 54.9133 | 54.9545 | 55.0186 | 8.4869 | 67.9276 | -54.7073 | 68.2755 | 123.3261 | -0.11444 | 76.7578 | 0.086975 | 0.3479 | 123.1842 | 123.2254 | 123.0881 | 68.4952 | 68.2755 | 123.2895 | 123.0652 | 76.7578 | 68.4952 | 68.2755 | 123.0652 | 123.0881 | 123.2895 | -55.275 | -46.4447
5346.7812 | 123.3261 | -68.2709 | 54.9042 | 0.034104 | -0.010139 | -0.026083 | 0.0086154 | -0.0078271 | -0.0056503 | -0.003512 | 0.018311 | 0.23346 | -0.31586 | 55.069 | 54.8218 | 54.8309 | 54.9271 | 54.9957 | 54.9866 | 8.4824 | 67.955 | -54.6707 | 68.2892 | 123.3398 | -0.082398 | 76.7532 | 0.082397 | 0.33417 | 123.1979 | 123.2666 | 123.0927 | 68.5043 | 68.2892 | 123.2574 | 123.1018 | 76.7532 | 68.5043 | 68.2892 | 123.1018 | 123.0927 | 123.2574 | -55.22 | -46.4218
5347.7812 | 123.3627 | -68.2617 | 54.9179 | -0.011673 | -0.010352 | -0.021597 | 0.0051974 | -0.0067591 | -0.0080001 | -0.0032984 | 0.054932 | 0.26093 | -0.30212 | 55.1147 | 54.8676 | 54.8904 | 54.9042 | 55.0919 | 55.0369 | 8.4824 | 67.9596 | -54.657 | 68.3167 | 123.3765 | -0.050354 | 76.7441 | 0.11902 | 0.35706 | 123.1659 | 123.3536 | 123.1293 | 68.5226 | 68.3167 | 123.2986 | 123.1522 | 76.7441 | 68.5226 | 68.3167 | 123.1522 | 123.1293 | 123.2986 | -55.22 | -46.4355
5348.7812 | 123.3261 | -68.2846 | 54.895 | 0.21721 | -0.010993 | -0.027152 | 0.0047702 | -0.0073999 | -0.0047957 | -0.0020166 | -0.054932 | 0.20599 | -0.36621 | 55.0552 | 54.8126 | 54.8126 | 54.8996 | 54.9637 | 54.9728 | 8.4778 | 67.9184 | -54.689 | 68.2297 | 123.3398 | -0.082398 | 76.7624 | 0.077819 | 0.31128 | 123.1842 | 123.2483 | 123.0972 | 68.4906 | 68.2297 | 123.2574 | 123.0972 | 76.7624 | 68.4906 | 68.2297 | 123.0972 | 123.0972 | 123.2574 | -55.2612 | -46.4172
5349.7812 | 123.2986 | -68.2892 | 54.8996 | 0.15617 | -0.0073614 | -0.023947 | 0.010111 | -0.0080407 | -0.0054367 | -0.0030848 | -0.009155 | 0.2243 | -0.33417 | 55.0415 | 54.8172 | 54.8218 | 54.9316 | 54.9408 | 55.0003 | 8.4778 | 67.955 | -54.6753 | 68.28 | 123.3307 | -0.082397 | 76.767 | 0.10071 | 0.32501 | 123.2208 | 123.23 | 123.1064 | 68.5135 | 68.28 | 123.2895 | 123.111 | 76.767 | 68.5135 | 68.28 | 123.111 | 123.1064 | 123.2895 | -55.2338 | -46.4218
5350.7812 | 123.3673 | -68.2617 | 54.9133 | -0.11085 | -0.0090704 | -0.023947 | 0.0084018 | -0.0069727 | -0.0077865 | -0.0020166 | 0.050354 | 0.23804 | -0.31586 | 55.1147 | 54.8813 | 54.8859 | 54.9362 | 55.0186 | 55.0232 | 8.4824 | 67.9459 | -54.6753 | 68.3121 | 123.3765 | -0.032043 | 76.7441 | 0.10986 | 0.36621 | 123.1979 | 123.2803 | 123.143 | 68.4998 | 68.3121 | 123.2849 | 123.1476 | 76.7441 | 68.4998 | 68.3121 | 123.1476 | 123.143 | 123.2849 | -55.2292 | -46.431
5351.7812 | 123.3307 | -68.2663 | 54.895 | 0.011215 | -0.0088568 | -0.021597 | 0.0073336 | -0.0059045 | -0.0054367 | -0.0032984 | 0.018311 | 0.22888 | -0.32501 | 55.0461 | 54.8401 | 54.8492 | 54.9271 | 55.0049 | 55.0095 | 8.4824 | 67.9413 | -54.6661 | 68.2846 | 123.3124 | -0.054932 | 76.7487 | 0.11444 | 0.34332 | 123.1934 | 123.2712 | 123.1064 | 68.4952 | 68.2846 | 123.2758 | 123.1155 | 76.7487 | 68.4952 | 68.2846 | 123.1155 | 123.1064 | 123.2758 | -55.22 | -46.4127
5352.7812 | 123.3261 | -68.2617 | 54.9042 | 0.072251 | -0.0084296 | -0.022452 | 0.0081882 | -0.0056909 | -0.0062911 | -0.0020166 | 0.041199 | 0.23346 | -0.33875 | 55.0644 | 54.8584 | 54.8447 | 54.9225 | 55.0278 | 55.0278 | 8.4778 | 67.923 | -54.6707 | 68.3029 | 123.3261 | -0.045777 | 76.7395 | 0.1236 | 0.37994 | 123.1842 | 123.2895 | 123.1201 | 68.4952 | 68.3029 | 123.2895 | 123.1064 | 76.7395 | 68.4952 | 68.3029 | 123.1064 | 123.1201 | 123.2895 | -55.2429 | -46.4264
5353.7812 | 123.3765 | -68.2617 | 54.8721 | 0.25536 | -0.0084296 | -0.026511 | 0.0024202 | -0.0056909 | -0.0080001 | -0.0011622 | -0.027466 | 0.17853 | -0.37994 | 55.0461 | 54.8676 | 54.8676 | 54.8355 | 55.014 | 54.9728 | 8.4824 | 67.8818 | -54.6936 | 68.2343 | 123.3078 | -0.004577 | 76.7441 | 0.10071 | 0.35248 | 123.0972 | 123.2758 | 123.1293 | 68.4402 | 68.2343 | 123.2346 | 123.1293 | 76.7441 | 68.4402 | 68.2343 | 123.1293 | 123.1293 | 123.2346 | -55.2521 | -46.3898
5354.7812 | 123.3261 | -68.2617 | 54.9133 | 0.026474 | -0.0084296 | -0.024588 | 0.0075472 | -0.0050501 | -0.0077865 | -0.0024438 | 0.027466 | 0.2243 | -0.33875 | 55.0644 | 54.8492 | 54.8538 | 54.9271 | 55.0095 | 55.0369 | 8.4824 | 67.923 | -54.689 | 68.2892 | 123.3261 | -0.064087 | 76.7441 | 0.1236 | 0.36621 | 123.1888 | 123.2712 | 123.111 | 68.486 | 68.2892 | 123.2986 | 123.1155 | 76.7441 | 68.486 | 68.2892 | 123.1155 | 123.111 | 123.2986 | -55.2521 | -46.431
5355.7812 | 123.3444 | -68.2571 | 54.8859 | 0.034104 | -0.0090704 | -0.02117 | 0.0084018 | -0.0054773 | -0.0086411 | -0.0026574 | 0.054932 | 0.23804 | -0.32959 | 55.0827 | 54.8584 | 54.8767 | 54.9271 | 55.0232 | 54.9911 | 8.4824 | 67.9276 | -54.6478 | 68.3121 | 123.3398 | -0.027466 | 76.7395 | 0.10529 | 0.38452 | 123.1842 | 123.2803 | 123.1155 | 68.4952 | 68.3121 | 123.2483 | 123.1338 | 76.7395 | 68.4952 | 68.3121 | 123.1338 | 123.1155 | 123.2483 | -55.2155 | -46.4035
5356.7812 | 123.349 | -68.2709 | 54.9179 | -0.095596 | -0.010139 | -0.026938 | 0.0064792 | -0.0059045 | -0.0045821 | -0.00458 | 0.050354 | 0.25635 | -0.32959 | 55.0919 | 54.8904 | 54.863 | 54.9545 | 55.0598 | 55.0278 | 8.4778 | 67.9413 | -54.6616 | 68.3212 | 123.3627 | -0.027466 | 76.7487 | 0.10986 | 0.37994 | 123.2254 | 123.3307 | 123.1613 | 68.5272 | 68.3212 | 123.2986 | 123.1339 | 76.7487 | 68.5272 | 68.3212 | 123.1339 | 123.1613 | 123.2986 | -55.2475 | -46.4401
5357.7812 | 123.2986 | -68.2755 | 54.8904 | 0.064621 | -0.0073614 | -0.023093 | 0.0073336 | -0.0065455 | -0.0043685 | -0.0024438 | 0 | 0.21515 | -0.33417 | 55.0278 | 54.8126 | 54.7989 | 54.9637 | 54.982 | 55.0186 | 8.4869 | 67.9413 | -54.6753 | 68.2755 | 123.3032 | -0.07782 | 76.7624 | 0.12817 | 0.33417 | 123.2391 | 123.2574 | 123.0881 | 68.4906 | 68.2755 | 123.2941 | 123.0743 | 76.7624 | 68.4906 | 68.2755 | 123.0743 | 123.0881 | 123.2941 | -55.2246 | -46.4035
5358.7812 | 123.3398 | -68.2571 | 54.9316 | -0.149 | -0.01142 | -0.026511 | 0.0047702 | -0.0065455 | -0.0086411 | -0.0013758 | 0.027466 | 0.27924 | -0.29755 | 55.0644 | 54.8584 | 54.8538 | 54.9911 | 55.0507 | 55.0552 | 8.4915 | 67.9596 | -54.6524 | 68.2846 | 123.3215 | -0.073243 | 76.7487 | 0.1236 | 0.32501 | 123.2483 | 123.3078 | 123.1155 | 68.5364 | 68.2846 | 123.3124 | 123.111 | 76.7487 | 68.5364 | 68.2846 | 123.111 | 123.1155 | 123.3124 | -55.2292 | -46.4401
5359.7812 | 123.3078 | -68.2571 | 54.9271 | -0.20241 | -0.010779 | -0.029715 | 0.0039156 | -0.0069727 | -0.0052231 | -0.00073479 | 0.013733 | 0.28839 | -0.27466 | 54.9728 | 54.8859 | 54.8309 | 54.9774 | 55.0461 | 55.0278 | 8.4915 | 67.9825 | -54.6387 | 68.2709 | 123.23 | -0.041199 | 76.7487 | 0.10071 | 0.28839 | 123.2346 | 123.3032 | 123.143 | 68.5455 | 68.2709 | 123.2849 | 123.0881 | 76.7487 | 68.5455 | 68.2709 | 123.0881 | 123.143 | 123.2849 | -55.2017 | -46.4355
5360.7812 | 123.3078 | -68.2571 | 54.95 | -0.149 | -0.014197 | -0.024802 | 0.0017794 | -0.0084681 | -0.0050095 | -0.0024438 | 0.018311 | 0.2655 | -0.27466 | 55.0552 | 54.863 | 54.8401 | 55.0049 | 55.0644 | 55.0323 | 8.4915 | 67.9825 | -54.6844 | 68.2755 | 123.3124 | -0.086975 | 76.7487 | 0.082398 | 0.29297 | 123.262 | 123.3215 | 123.1201 | 68.5226 | 68.2755 | 123.2895 | 123.0972 | 76.7487 | 68.5226 | 68.2755 | 123.0972 | 123.1201 | 123.2895 | -55.2246 | -46.4584
5361.7812 | 123.3765 | -68.2617 | 54.8813 | 0.27061 | -0.0088568 | -0.023093 | 0.0075472 | -0.0088953 | -0.0045821 | -0.0022302 | -0.032043 | 0.17395 | -0.36163 | 55.0552 | 54.8538 | 54.8447 | 54.8401 | 55.0186 | 54.9683 | 8.4961 | 67.9001 | -54.7073 | 68.2297 | 123.317 | -0.027466 | 76.7578 | 0.086975 | 0.32959 | 123.1018 | 123.2803 | 123.1155 | 68.4357 | 68.2297 | 123.23 | 123.1064 | 76.7578 | 68.4357 | 68.2297 | 123.1064 | 123.1155 | 123.23 | -55.2429 | -46.3852
5362.7812 | 123.3627 | -68.2663 | 54.9133 | -0.095596 | -0.011207 | -0.021811 | 0.0077608 | -0.0091089 | -0.0069321 | -0.0026574 | -0.032043 | 0.24719 | -0.27008 | 55.1147 | 54.8447 | 54.8676 | 54.9454 | 55.0598 | 55.0095 | 8.4824 | 67.9962 | -54.6661 | 68.2343 | 123.381 | -0.068664 | 76.7487 | 0.09613 | 0.23804 | 123.2117 | 123.3261 | 123.111 | 68.5135 | 68.2343 | 123.2758 | 123.1338 | 76.7487 | 68.5135 | 68.2343 | 123.1338 | 123.111 | 123.2758 | -55.1834 | -46.431
5363.7812 | 123.3261 | -68.248 | 54.9133 | -0.011673 | -0.009284 | -0.026511 | 0.0073336 | -0.0082545 | -0.0065047 | -0.0030848 | 0.059509 | 0.23804 | -0.33875 | 55.0873 | 54.8492 | 54.8584 | 54.9088 | 55.0415 | 55.0049 | 8.4824 | 67.9092 | -54.6753 | 68.3075 | 123.3353 | -0.064087 | 76.7303 | 0.091553 | 0.39825 | 123.1567 | 123.2895 | 123.0972 | 68.486 | 68.3075 | 123.2529 | 123.1064 | 76.7303 | 68.486 | 68.3075 | 123.1064 | 123.0972 | 123.2529 | -55.2521 | -46.431
5364.7812 | 123.3215 | -68.2709 | 54.9179 | -0.20241 | -0.009925 | -0.029501 | 0.0022066 | -0.0099633 | -0.0065047 | -0.0047938 | 0.27008 | 0.31128 | -0.25635 | 55.0369 | 54.8492 | 54.8264 | 54.9957 | 55.0369 | 55.0461 | 8.4869 | 68.0145 | -54.6066 | 68.541 | 123.3078 | -0.068665 | 76.7578 | 0.12817 | 0.52643 | 123.2666 | 123.3078 | 123.1201 | 68.5822 | 68.541 | 123.317 | 123.0972 | 76.7578 | 68.5822 | 68.541 | 123.0972 | 123.1201 | 123.317 | -55.1743 | -46.431
5365.7812 | 123.3124 | -68.2388 | 54.9454 | -0.18715 | -0.011207 | -0.026511 | 0.0022066 | -0.0073999 | -0.0075729 | -0.0013758 | 0.013733 | 0.28381 | -0.29755 | 55.0781 | 54.8309 | 54.8264 | 55.0003 | 55.0278 | 55.0461 | 8.4869 | 67.9413 | -54.6616 | 68.2526 | 123.317 | -0.11444 | 76.7258 | 0.10071 | 0.31128 | 123.2391 | 123.2666 | 123.0698 | 68.5226 | 68.2526 | 123.2849 | 123.0652 | 76.7258 | 68.5226 | 68.2526 | 123.0652 | 123.0698 | 123.2849 | -55.2429 | -46.4584
5366.7812 | 123.3444 | -68.2663 | 54.95 | -0.17952 | -0.0090704 | -0.026724 | 0.0060518 | -0.0088953 | -0.0077865 | -0.0037256 | 0.032043 | 0.27924 | -0.3067 | 55.0827 | 54.8492 | 54.8447 | 54.9866 | 55.0507 | 55.0369 | 8.4869 | 67.9596 | -54.6707 | 68.2983 | 123.349 | -0.10071 | 76.7532 | 0.086975 | 0.33874 | 123.2529 | 123.317 | 123.1155 | 68.5455 | 68.2983 | 123.3032 | 123.111 | 76.7532 | 68.5455 | 68.2983 | 123.111 | 123.1155 | 123.3032 | -55.2567 | -46.463
5367.7812 | 123.3078 | -68.28 | 54.8904 | 0.19432 | -0.007575 | -0.026938 | 0.00712 | -0.0078271 | -0.0060775 | 0.00076041 | -0.032043 | 0.20142 | -0.36163 | 55.0323 | 54.7989 | 54.7943 | 54.9088 | 54.95 | 55.0003 | 8.4869 | 67.9184 | -54.689 | 68.248 | 123.3124 | -0.091553 | 76.767 | 0.10986 | 0.32959 | 123.1888 | 123.23 | 123.0789 | 68.4814 | 68.248 | 123.2803 | 123.0743 | 76.767 | 68.4814 | 68.248 | 123.0743 | 123.0789 | 123.2803 | -55.2521 | -46.4035
5368.7812 | 123.3124 | -68.2526 | 54.9545 | -0.149 | -0.0094976 | -0.025443 | 0.0024202 | -0.0063317 | -0.0060775 | -0.0039392 | 0.022888 | 0.27924 | -0.29297 | 55.069 | 54.6524 | 54.8309 | 54.9866 | 55.0323 | 55.0461 | 8.4824 | 67.9596 | -54.6753 | 68.2755 | 123.3215 | -0.30212 | 76.7349 | 0.091553 | 0.31586 | 123.2391 | 123.2849 | 122.905 | 68.5318 | 68.2755 | 123.2986 | 123.0835 | 76.7349 | 68.5318 | 68.2755 | 123.0835 | 122.905 | 123.2986 | -55.2475 | -46.4722
5369.7812 | 123.3215 | -68.2388 | 54.95 | -0.24055 | -0.0090704 | -0.028647 | 0.0041292 | -0.0091089 | -0.0041549 | -0.0020166 | -0.027466 | 0.3067 | -0.27466 | 55.0598 | 54.6478 | 54.8126 | 55.0049 | 55.0461 | 55.0461 | 8.4869 | 67.9642 | -54.6432 | 68.2114 | 123.2986 | -0.30212 | 76.7258 | 0.096131 | 0.24719 | 123.2437 | 123.2849 | 122.8867 | 68.5455 | 68.2114 | 123.2849 | 123.0515 | 76.7258 | 68.5455 | 68.2114 | 123.0515 | 122.8867 | 123.2849 | -55.2246 | -46.463
5370.7812 | 123.3307 | -68.2434 | 54.9271 | -0.14137 | -0.010139 | -0.027365 | 0.00712 | -0.0086817 | -0.0062911 | -0.00458 | 0.036621 | 0.28381 | -0.29297 | 55.069 | 54.657 | 54.8309 | 54.9957 | 55.0598 | 55.0552 | 8.4869 | 67.9504 | -54.6432 | 68.28 | 123.3124 | -0.27008 | 76.7303 | 0.12817 | 0.32959 | 123.2391 | 123.3032 | 122.9004 | 68.5272 | 68.28 | 123.2986 | 123.0743 | 76.7303 | 68.5272 | 68.28 | 123.0743 | 122.9004 | 123.2986 | -55.22 | -46.4401
5371.7812 | 123.3536 | -68.248 | 54.95 | -0.17952 | -0.0088568 | -0.02822 | 0.0060518 | -0.0076135 | -0.0080001 | -0.0028712 | 0.064087 | 0.27466 | -0.29755 | 55.1147 | 54.689 | 54.8584 | 54.9454 | 55.0598 | 55.0278 | 8.4869 | 67.9504 | -54.6753 | 68.3121 | 123.3627 | -0.26093 | 76.7349 | 0.07782 | 0.36163 | 123.1934 | 123.3078 | 122.937 | 68.5226 | 68.3121 | 123.2758 | 123.1064 | 76.7349 | 68.5226 | 68.3121 | 123.1064 | 122.937 | 123.2758 | -55.2475 | -46.463
5372.7812 | 123.317 | -68.28 | 54.895 | 0.20958 | -0.009925 | -0.026938 | 0.0062656 | -0.0052637 | -0.0069321 | -0.0030848 | -0.027466 | 0.20142 | -0.36621 | 55.0232 | 54.6066 | 54.7943 | 54.8859 | 54.9774 | 54.9957 | 8.4824 | 67.9138 | -54.6936 | 68.2526 | 123.3032 | -0.28839 | 76.7624 | 0.10071 | 0.33875 | 123.1659 | 123.2574 | 122.8867 | 68.4814 | 68.2526 | 123.2758 | 123.0743 | 76.7624 | 68.4814 | 68.2526 | 123.0743 | 122.8867 | 123.2758 | -55.2612 | -46.4127
5373.7812 | 123.3627 | -68.248 | 54.8996 | -0.2787 | -0.0084296 | -0.027152 | 0.010111 | -0.0063317 | -0.0065047 | -0.001803 | 0.050354 | 0.24261 | -0.28381 | 55.0873 | 54.6936 | 54.8447 | 54.9179 | 55.0323 | 55.0186 | 8.4778 | 67.9642 | -54.657 | 68.2983 | 123.3353 | -0.20599 | 76.7258 | 0.11902 | 0.33417 | 123.1659 | 123.2803 | 122.9416 | 68.4906 | 68.2983 | 123.2666 | 123.0927 | 76.7258 | 68.4906 | 68.2983 | 123.0927 | 122.9416 | 123.2666 | -55.1834 | -46.4218
5374.7812 | 123.3582 | -68.2434 | 54.9271 | -0.23293 | -0.009925 | -0.028647 | -0.003134 | -0.0086817 | -0.0071457 | -0.0028712 | 0.054932 | 0.23346 | -0.2655 | 55.101 | 54.7211 | 54.8813 | 54.9408 | 55.0735 | 55.0507 | 8.4869 | 67.9779 | -54.6936 | 68.2983 | 123.3444 | -0.20599 | 76.7303 | 0.1236 | 0.32043 | 123.1842 | 123.317 | 122.9645 | 68.4769 | 68.2983 | 123.2941 | 123.1247 | 76.7303 | 68.4769 | 68.2983 | 123.1247 | 122.9645 | 123.2941 | -55.1926 | -46.4401
5375.7812 | 123.4634 | -68.2159 | 54.8767 | -0.057449 | -0.01377 | -0.028006 | -0.0022794 | -0.010604 | -0.0071457 | -0.0015894 | 0.041199 | 0.19684 | -0.28839 | 55.1697 | 54.7485 | 54.9637 | 54.8218 | 55.1651 | 54.9683 | 8.4869 | 67.9276 | -54.6799 | 68.2571 | 123.3856 | -0.12817 | 76.7029 | 0.091553 | 0.32959 | 123.0377 | 123.381 | 122.9645 | 68.4128 | 68.2571 | 123.1842 | 123.1796 | 76.7029 | 68.4128 | 68.2571 | 123.1796 | 122.9645 | 123.1842 | -55.1651 | -46.3898
5376.7812 | 123.436 | -68.2068 | 54.8996 | -0.17189 | -0.01142 | -0.031851 | 0.0039156 | -0.013168 | -0.0086411 | -0.0026574 | 0.073242 | 0.18768 | -0.2655 | 55.1147 | 54.7806 | 54.9545 | 54.8035 | 55.1422 | 54.9362 | 8.4961 | 67.9413 | -54.7119 | 68.28 | 123.3215 | -0.11902 | 76.7029 | 0.036621 | 0.33874 | 123.0103 | 123.349 | 122.9874 | 68.3945 | 68.28 | 123.143 | 123.1613 | 76.7029 | 68.3945 | 68.28 | 123.1613 | 122.9874 | 123.143 | -55.1651 | -46.4035
5377.7812 | 123.3032 | -68.2663 | 54.895 | 0.10277 | -0.008216 | -0.023734 | 0.0096834 | -0.0097497 | -0.0060775 | -0.001803 | -0.013733 | 0.23346 | -0.3479 | 55.0323 | 54.5975 | 54.7897 | 54.8996 | 54.9774 | 54.9683 | 8.4824 | 67.9184 | -54.6616 | 68.2526 | 123.2986 | -0.29755 | 76.7487 | 0.073242 | 0.33417 | 123.1659 | 123.2437 | 122.8638 | 68.4998 | 68.2526 | 123.2346 | 123.056 | 76.7487 | 68.4998 | 68.2526 | 123.056 | 122.8638 | 123.2346 | -55.2429 | -46.4127
5378.8438 | 123.4268 | -68.2388 | 54.8584 | 0.14854 | -0.012061 | -0.029501 | 0.0028476 | -0.0084681 | -0.0060775 | -0.0011622 | 0.018311 | 0.10529 | -0.35706 | 55.1193 | 54.7211 | 54.9133 | 54.744 | 55.0827 | 54.9683 | 8.4915 | 67.8818 | -54.7531 | 68.2571 | 123.3582 | -0.13733 | 76.7303 | 0.10986 | 0.37537 | 122.9828 | 123.3215 | 122.9599 | 68.3441 | 68.2571 | 123.2071 | 123.1522 | 76.7303 | 68.3441 | 68.2571 | 123.1522 | 122.9599 | 123.2071 | -55.2155 | -46.3669
5379.7812 | 123.3765 | -68.2297 | 54.9133 | -0.04982 | -0.007575 | -0.025443 | 0.0084018 | -0.0093225 | -0.0077865 | -0.0039392 | 0.064087 | 0.24261 | -0.32501 | 55.1285 | 54.6799 | 54.8584 | 54.8401 | 55.0781 | 54.9728 | 8.4869 | 67.9047 | -54.6707 | 68.2938 | 123.3582 | -0.23346 | 76.7166 | 0.059509 | 0.3891 | 123.0698 | 123.3078 | 122.9095 | 68.4723 | 68.2938 | 123.2025 | 123.0881 | 76.7166 | 68.4723 | 68.2938 | 123.0881 | 122.9095 | 123.2025 | -55.2383 | -46.4264
5380.8281 | 123.3765 | -68.2617 | 54.8309 | 0.011215 | -0.0094976 | -0.024374 | 0.0051974 | -0.0065455 | -0.0056503 | -0.00094839 | 0.009155 | 0.14648 | -0.37079 | 55.1331 | 54.7348 | 54.9088 | 54.7394 | 55.0735 | 54.9591 | 8.4869 | 67.8909 | -54.6844 | 68.2709 | 123.3948 | -0.096131 | 76.7487 | 0.12817 | 0.37994 | 123.0011 | 123.3353 | 122.9965 | 68.4082 | 68.2709 | 123.2208 | 123.1705 | 76.7487 | 68.4082 | 68.2709 | 123.1705 | 122.9965 | 123.2208 | -55.2017 | -46.344
5381.8281 | 123.3536 | -68.2571 | 54.8904 | -0.11085 | -0.0069342 | -0.023947 | 0.010324 | -0.0069727 | -0.0071457 | -0.0022302 | 0.068665 | 0.23804 | -0.30212 | 55.1102 | 54.6982 | 54.863 | 54.895 | 55.0415 | 55.0232 | 8.4824 | 67.955 | -54.6524 | 68.3258 | 123.3673 | -0.19226 | 76.7395 | 0.13275 | 0.37079 | 123.1522 | 123.2986 | 122.9553 | 68.4952 | 68.3258 | 123.2803 | 123.1201 | 76.7395 | 68.4952 | 68.3258 | 123.1201 | 122.9553 | 123.2803 | -55.1926 | -46.4081
5382.7812 | 123.3444 | -68.2434 | 54.9225 | -0.12611 | -0.012061 | -0.028433 | 0.0075472 | -0.0050501 | -0.0056503 | -0.0022302 | 0.050354 | 0.27008 | -0.29297 | 55.1147 | 54.7394 | 54.863 | 54.9271 | 55.0644 | 55.0278 | 8.4869 | 67.9504 | -54.6524 | 68.2938 | 123.3582 | -0.18311 | 76.7303 | 0.10529 | 0.34332 | 123.1705 | 123.3078 | 122.9828 | 68.5135 | 68.2938 | 123.2712 | 123.1064 | 76.7303 | 68.5135 | 68.2938 | 123.1064 | 122.9828 | 123.2712 | -55.2155 | -46.4355
5383.7812 | 123.4222 | -68.2205 | 54.8904 | 0.0035856 | -0.013343 | -0.029074 | -0.0037748 | -0.0099633 | -0.0071457 | -0.0022302 | -0.013733 | 0.16479 | -0.32044 | 55.1193 | 54.7897 | 54.9133 | 54.8172 | 55.1193 | 54.9637 | 8.4915 | 67.9001 | -54.7256 | 68.2068 | 123.3398 | -0.10071 | 76.712 | 0.073242 | 0.3067 | 123.0377 | 123.3398 | 123.0103 | 68.3853 | 68.2068 | 123.1842 | 123.1338 | 76.712 | 68.3853 | 68.2068 | 123.1338 | 123.0103 | 123.1842 | -55.2109 | -46.3989
5384.7812 | 123.4497 | -68.2343 | 54.8996 | -0.04982 | -0.010993 | -0.031638 | -0.0022794 | -0.012527 | -0.0058639 | -0.0015894 | 0.036621 | 0.18768 | -0.31128 | 55.1193 | 54.8218 | 54.9362 | 54.8172 | 55.1514 | 54.9545 | 8.4869 | 67.923 | -54.7119 | 68.2709 | 123.3536 | -0.07782 | 76.7212 | 0.054932 | 0.3479 | 123.0515 | 123.3856 | 123.056 | 68.4219 | 68.2709 | 123.1888 | 123.1705 | 76.7212 | 68.4219 | 68.2709 | 123.1705 | 123.056 | 123.1888 | -55.2109 | -46.4127
5385.7969 | 123.4406 | -68.1931 | 54.9042 | 0.4232 | -0.013984 | -0.027792 | 0.0011386 | -0.012313 | -0.0073593 | -0.0041528 | 0.050354 | 0.20599 | -0.27924 | 55.1697 | 54.8126 | 54.9362 | 54.8218 | 55.1468 | 54.9454 | 8.4824 | 67.9138 | -54.6982 | 68.2434 | 123.3627 | -0.091553 | 76.6754 | 0.041199 | 0.32959 | 123.0148 | 123.3398 | 123.0057 | 68.399 | 68.2434 | 123.1384 | 123.1293 | 76.6754 | 68.399 | 68.2434 | 123.1293 | 123.0057 | 123.1384 | -55.1834 | -46.4218
5386.7812 | 123.4268 | -68.2297 | 54.9042 | -0.11085 | -0.012702 | -0.027579 | 0.0034884 | -0.011886 | -0.0084273 | -0.0022302 | 0.064087 | 0.19684 | -0.28381 | 55.1559 | 54.8035 | 54.9179 | 54.8492 | 55.1559 | 54.9866 | 8.4869 | 67.9459 | -54.7073 | 68.2938 | 123.3856 | -0.10071 | 76.7166 | 0.082397 | 0.3479 | 123.0789 | 123.3856 | 123.0331 | 68.4265 | 68.2938 | 123.2162 | 123.1476 | 76.7166 | 68.4265 | 68.2938 | 123.1476 | 123.0331 | 123.2162 | -55.188 | -46.4172
5387.7812 | 123.317 | -68.2755 | 54.9316 | -0.20241 | -0.010993 | -0.027792 | 0.0047702 | -0.011672 | -0.0077865 | -0.001803 | 0.045776 | 0.27924 | -0.27466 | 55.0507 | 54.8767 | 54.95 | 54.8355 | 54.9454 | 55.0232 | 8.4778 | 68.0008 | -54.6524 | 68.3212 | 123.3261 | -0.054932 | 76.7532 | 0.091552 | 0.32043 | 123.111 | 123.2208 | 123.1522 | 68.5547 | 68.3212 | 123.2986 | 123.2254 | 76.7532 | 68.5547 | 68.3212 | 123.2254 | 123.1522 | 123.2986 | -55.2063 | -46.4539
5388.7812 | 123.4085 | -68.2343 | 54.9179 | 0.034104 | -0.012916 | -0.029929 | -0.00035676 | -0.011886 | -0.0067185 | -0.0037256 | -0.013733 | 0.18768 | -0.32044 | 55.1193 | 54.776 | 54.8996 | 54.8126 | 55.1147 | 54.9591 | 8.4915 | 67.9138 | -54.7302 | 68.2205 | 123.3536 | -0.14191 | 76.7258 | 0.041198 | 0.3067 | 123.0469 | 123.349 | 123.0103 | 68.4219 | 68.2205 | 123.1934 | 123.1338 | 76.7258 | 68.4219 | 68.2205 | 123.1338 | 123.0103 | 123.1934 | -55.2383 | -46.4264
5389.7812 | 123.4177 | -68.2205 | 54.9133 | -0.15663 | -0.013129 | -0.025443 | 0.0041292 | -0.014022 | -0.0082137 | -0.0024438 | 0.068665 | 0.21057 | -0.2655 | 55.1926 | 54.7943 | 54.9225 | 54.8584 | 55.1559 | 54.9591 | 8.4778 | 67.955 | -54.7028 | 68.2892 | 123.4131 | -0.11902 | 76.6983 | 0.045776 | 0.33417 | 123.0789 | 123.3765 | 123.0148 | 68.4311 | 68.2892 | 123.1796 | 123.143 | 76.6983 | 68.4311 | 68.2892 | 123.143 | 123.0148 | 123.1796 | -55.1788 | -46.4355
5390.7812 | 123.349 | -68.2617 | 54.9133 | -0.11848 | -0.010566 | -0.022879 | 0.01182 | -0.010391 | -0.0060775 | -0.00458 | 0.059509 | 0.27924 | -0.28381 | 55.1239 | 54.744 | 54.8447 | 54.9179 | 55.0507 | 55.014 | 8.4824 | 67.9779 | -54.6341 | 68.3212 | 123.3856 | -0.16937 | 76.7441 | 0.10071 | 0.34332 | 123.1796 | 123.3124 | 123.0057 | 68.541 | 68.3212 | 123.2758 | 123.1064 | 76.7441 | 68.541 | 68.3212 | 123.1064 | 123.0057 | 123.2758 | -55.1971 | -46.431
5391.7812 | 123.4406 | -68.1885 | 54.8904 | -0.25581 | -0.011634 | -0.026511 | 0.0030612 | -0.010604 | -0.0077865 | -0.003512 | 0.068665 | 0.19226 | -0.28839 | 55.1605 | 54.8126 | 54.9316 | 54.8401 | 55.1468 | 54.9728 | 8.4915 | 67.9001 | -54.6982 | 68.2571 | 123.349 | -0.07782 | 76.68 | 0.082397 | 0.35706 | 123.0286 | 123.3353 | 123.0011 | 68.3807 | 68.2571 | 123.1613 | 123.1201 | 76.68 | 68.3807 | 68.2571 | 123.1201 | 123.0011 | 123.1613 | -55.1788 | -46.3989
5392.7812 | 123.4085 | -68.2297 | 54.895 | 0.026474 | -0.012702 | -0.026938 | 0.001993 | -0.012313 | -0.0067185 | -0.0020166 | 0 | 0.17395 | -0.3067 | 55.1376 | 54.7806 | 54.9042 | 54.8126 | 55.1056 | 54.9362 | 8.4869 | 67.923 | -54.7211 | 68.2297 | 123.3673 | -0.11444 | 76.7166 | 0.041198 | 0.3067 | 123.0423 | 123.3353 | 123.0103 | 68.4036 | 68.2297 | 123.1659 | 123.1338 | 76.7166 | 68.4036 | 68.2297 | 123.1338 | 123.0103 | 123.1659 | -55.2017 | -46.4081
5393.7812 | 123.4589 | -68.2114 | 54.8859 | -0.080337 | -0.014411 | -0.029715 | 0.0013522 | -0.012527 | -0.0080001 | -0.0047938 | 0.07782 | 0.19684 | -0.27466 | 55.4489 | 55.1971 | 54.95 | 54.5975 | 55.0964 | 54.95 | 8.4915 | 67.9367 | -54.689 | 68.2892 | 123.6603 | 0.31128 | 76.7029 | 0.064087 | 0.35248 | 122.8088 | 123.3078 | 123.4085 | 68.4082 | 68.2892 | 123.1613 | 123.1613 | 76.7029 | 68.4082 | 68.2892 | 123.1613 | 123.4085 | 123.1613 | -55.1605 | -46.3943
5394.7812 | 123.4406 | -68.1885 | 54.9042 | -0.087967 | -0.011634 | -0.025229 | 0.0022066 | -0.013381 | -0.0062911 | -0.0043664 | 0.073242 | 0.20142 | -0.28839 | 55.1743 | 54.8218 | 54.9362 | 54.8218 | 55.1605 | 54.95 | 8.4915 | 67.9001 | -54.7028 | 68.2617 | 123.3627 | -0.082398 | 76.68 | 0.045776 | 0.36163 | 123.0103 | 123.349 | 123.0103 | 68.3899 | 68.2617 | 123.1384 | 123.1247 | 76.68 | 68.3899 | 68.2617 | 123.1247 | 123.0103 | 123.1384 | -55.1926 | -46.4127
5395.7812 | 123.4634 | -68.1931 | 54.863 | -0.0040434 | -0.013343 | -0.029929 | -0.00057036 | -0.014236 | -0.0033005 | -0.003512 | 0.032043 | 0.17853 | -0.28839 | 55.1651 | 54.8309 | 54.9408 | 54.7943 | 55.1559 | 54.9408 | 8.4915 | 67.9047 | -54.6844 | 68.2251 | 123.3582 | -0.032043 | 76.6846 | 0.07782 | 0.32043 | 122.9874 | 123.349 | 123.024 | 68.3716 | 68.2251 | 123.1338 | 123.1338 | 76.6846 | 68.3716 | 68.2251 | 123.1338 | 123.024 | 123.1338 | -55.1514 | -46.3715
5396.7812 | 123.4131 | -68.2617 | 54.8813 | 0.011215 | -0.01142 | -0.027579 | -0.00057036 | -0.013595 | -0.0080001 | -0.00458 | -0.027466 | 0.16937 | -0.29755 | 55.1285 | 54.7852 | 54.8859 | 54.8172 | 55.0919 | 54.9362 | 8.4869 | 67.9642 | -54.7119 | 68.2343 | 123.3902 | -0.096131 | 76.7487 | 0.054931 | 0.27008 | 123.0789 | 123.3536 | 123.0469 | 68.4311 | 68.2343 | 123.1979 | 123.1476 | 76.7487 | 68.4311 | 68.2343 | 123.1476 | 123.0469 | 123.1979 | -55.1788 | -46.3943
5397.7812 | 123.4085 | -68.2343 | 54.9042 | -0.034561 | -0.014411 | -0.028861 | 0.002634 | -0.0121 | -0.0041549 | -0.0047938 | 0 | 0.19226 | -0.31586 | 55.1514 | 54.8264 | 54.895 | 54.8172 | 55.1239 | 54.95 | 8.4915 | 67.9184 | -54.7119 | 68.2343 | 123.3856 | -0.07782 | 76.7258 | 0.045776 | 0.31586 | 123.0515 | 123.3582 | 123.0606 | 68.4265 | 68.2343 | 123.1842 | 123.1293 | 76.7258 | 68.4265 | 68.2343 | 123.1293 | 123.0606 | 123.1842 | -55.22 | -46.4127
5398.7812 | 123.4497 | -68.2068 | 54.8859 | -0.034561 | -0.013984 | -0.030997 | 0.00049764 | -0.013809 | -0.0043685 | -0.0037256 | 0.045776 | 0.19226 | -0.28839 | 55.1788 | 54.8401 | 54.9454 | 54.7989 | 55.1651 | 54.95 | 8.4869 | 67.9184 | -54.6936 | 68.2526 | 123.3856 | -0.045776 | 76.6937 | 0.064087 | 0.33417 | 123.0057 | 123.3719 | 123.0469 | 68.399 | 68.2526 | 123.1567 | 123.1522 | 76.6937 | 68.399 | 68.2526 | 123.1522 | 123.0469 | 123.1567 | -55.1743 | -46.3989
5399.7812 | 123.4039 | -68.2205 | 54.8767 | 0.21721 | -0.011634 | -0.030783 | 0.0032748 | -0.011459 | -0.0030869 | -0.0030848 | -0.018311 | 0.11444 | -0.36621 | 55.1331 | 54.776 | 54.8767 | 54.7531 | 55.0552 | 54.9133 | 8.4778 | 67.8543 | -54.7623 | 68.2022 | 123.3536 | -0.10071 | 76.6983 | 0.036621 | 0.3479 | 122.9736 | 123.2758 | 122.9965 | 68.335 | 68.2022 | 123.1338 | 123.0972 | 76.6983 | 68.335 | 68.2022 | 123.0972 | 122.9965 | 123.1338 | -55.2429 | -46.3989
5400.7812 | 123.4314 | -68.2114 | 54.895 | 0.011215 | -0.011848 | -0.032279 | -0.00057036 | -0.013595 | -0.0035141 | -0.0020166 | 0.022888 | 0.18768 | -0.29297 | 55.1514 | 54.8264 | 54.9088 | 54.8035 | 55.1239 | 54.9316 | 8.4824 | 67.9184 | -54.7073 | 68.2343 | 123.3627 | -0.068665 | 76.6937 | 0.036621 | 0.31586 | 123.0148 | 123.3353 | 123.0377 | 68.399 | 68.2343 | 123.143 | 123.1201 | 76.6937 | 68.399 | 68.2343 | 123.1201 | 123.0377 | 123.143 | -55.188 | -46.4127
5401.7812 | 123.4497 | -68.2068 | 54.9179 | 0.25536 | -0.012488 | -0.028006 | 0.0022066 | -0.014236 | -0.0043685 | -0.00052119 | 0.059509 | 0.20599 | -0.27008 | 55.2017 | 54.863 | 54.9316 | 54.8309 | 55.1422 | 54.9408 | 8.4915 | 67.9367 | -54.7119 | 68.2663 | 123.4085 | -0.054932 | 76.6983 | 0.022888 | 0.32959 | 123.0377 | 123.349 | 123.0698 | 68.4128 | 68.2663 | 123.1476 | 123.1384 | 76.6983 | 68.4128 | 68.2663 | 123.1384 | 123.0698 | 123.1476 | -55.188 | -46.4264
5402.7812 | 123.3948 | -68.2251 | 54.8996 | 0.07988 | -0.012702 | -0.027579 | 0.00049764 | -0.011245 | -0.0043685 | -0.0015894 | -0.036621 | 0.19684 | -0.31586 | 55.1376 | 54.7852 | 54.8859 | 54.8172 | 55.0873 | 54.9179 | 8.4961 | 67.9092 | -54.7028 | 68.1885 | 123.3627 | -0.11444 | 76.7212 | 0.018311 | 0.27924 | 123.0423 | 123.3124 | 123.0103 | 68.4219 | 68.1885 | 123.143 | 123.111 | 76.7212 | 68.4219 | 68.1885 | 123.111 | 123.0103 | 123.143 | -55.2155 | -46.4035
5403.7812 | 123.4589 | -68.1793 | 54.8904 | -0.019302 | -0.014197 | -0.026083 | 0.00049764 | -0.014877 | -0.0060775 | -0.0032984 | 0.036621 | 0.17395 | -0.27008 | 55.22 | 54.8447 | 54.95 | 54.8035 | 55.1651 | 54.9316 | 8.4824 | 67.9092 | -54.7165 | 68.2159 | 123.3994 | -0.045776 | 76.6617 | 0.041199 | 0.3067 | 122.9828 | 123.3444 | 123.024 | 68.3533 | 68.2159 | 123.111 | 123.1293 | 76.6617 | 68.3533 | 68.2159 | 123.1293 | 123.024 | 123.111 | -55.1605 | -46.4081
5404.7812 | 123.3765 | -68.2617 | 54.895 | 0.22484 | -0.011634 | -0.028006 | 0.0032748 | -0.011245 | -0.0082137 | -0.0022302 | -0.022888 | 0.10986 | -0.35248 | 55.1102 | 54.7623 | 54.8721 | 54.7806 | 55.0598 | 54.9179 | 8.4869 | 67.9092 | -54.7852 | 68.2388 | 123.3719 | -0.13275 | 76.7487 | 0.022888 | 0.32959 | 123.0423 | 123.3215 | 123.024 | 68.3716 | 68.2388 | 123.1796 | 123.1338 | 76.7487 | 68.3716 | 68.2388 | 123.1338 | 123.024 | 123.1796 | -55.2475 | -46.4081
5405.7812 | 123.3444 | -68.2388 | 54.9179 | -0.149 | -0.010566 | -0.028433 | 0.005411 | -0.0121 | -0.0041549 | -0.0039392 | 0.068665 | 0.24719 | -0.27924 | 55.1514 | 54.7852 | 54.8859 | 54.9225 | 55.0827 | 54.95 | 8.4961 | 67.9596 | -54.6707 | 68.3075 | 123.3902 | -0.13275 | 76.7349 | 0.032043 | 0.3479 | 123.1613 | 123.3215 | 123.024 | 68.486 | 68.3075 | 123.1888 | 123.1247 | 76.7349 | 68.486 | 68.3075 | 123.1247 | 123.024 | 123.1888 | -55.1971 | -46.4218
5406.7812 | 123.4131 | -68.2388 | 54.8721 | 0.034104 | -0.012702 | -0.029288 | -0.00099756 | -0.012527 | -0.0069321 | -0.0030848 | -0.013733 | 0.1831 | -0.32044 | 55.1468 | 54.7989 | 54.9179 | 54.8264 | 55.1147 | 54.9683 | 8.4869 | 67.9184 | -54.689 | 68.2251 | 123.3856 | -0.073242 | 76.7258 | 0.096131 | 0.3067 | 123.0652 | 123.3536 | 123.0377 | 68.4219 | 68.2251 | 123.2071 | 123.1567 | 76.7258 | 68.4219 | 68.2251 | 123.1567 | 123.0377 | 123.2071 | -55.1926 | -46.3852
5407.7812 | 123.4177 | -68.2251 | 54.8904 | -0.17952 | -0.013557 | -0.031851 | 0.00028404 | -0.014236 | -0.0054367 | -0.0047938 | 0.091553 | 0.20599 | -0.27466 | 55.2109 | 54.7806 | 55.0552 | 55.1239 | 54.8904 | 54.9637 | 8.4869 | 67.9504 | -54.6844 | 68.3167 | 123.436 | -0.10986 | 76.712 | 0.073242 | 0.36621 | 123.349 | 123.1155 | 123.0057 | 68.4311 | 68.3167 | 123.1888 | 123.2803 | 76.712 | 68.4311 | 68.3167 | 123.2803 | 123.0057 | 123.1888 | -55.1651 | -46.4035
5408.7812 | 123.4589 | -68.2297 | 54.863 | 0.27061 | -0.011848 | -0.02352 | 0.0073336 | -0.0097497 | -0.0069321 | 0.00054681 | 0.013733 | 0.1236 | -0.36163 | 55.014 | 54.5609 | 54.9774 | 54.8447 | 55.1285 | 54.9088 | 8.4824 | 67.868 | -54.7394 | 68.2434 | 123.2437 | -0.30212 | 76.712 | 0.045776 | 0.37537 | 123.0743 | 123.3582 | 122.7905 | 68.3533 | 68.2434 | 123.1384 | 123.2071 | 76.712 | 68.3533 | 68.2434 | 123.2071 | 122.7905 | 123.1384 | -55.2246 | -46.3806
5409.7812 | 123.4268 | -68.2434 | 54.8447 | 0.026474 | -0.0088568 | -0.023093 | 0.003702 | -0.0080407 | -0.0050095 | -0.00094839 | 0.036621 | 0.10529 | -0.35248 | 55.1559 | 54.7348 | 54.9179 | 54.7394 | 55.0781 | 54.9088 | 8.4869 | 67.8909 | -54.7394 | 68.28 | 123.3994 | -0.10986 | 76.7303 | 0.064086 | 0.3891 | 122.9828 | 123.3215 | 122.9782 | 68.3487 | 68.28 | 123.1522 | 123.1613 | 76.7303 | 68.3487 | 68.28 | 123.1613 | 122.9782 | 123.1522 | -55.1971 | -46.3577
5410.7812 | 123.4085 | -68.2571 | 54.8813 | -0.0040434 | -0.012916 | -0.028433 | 0.0024202 | -0.013595 | -0.0071457 | -0.0030848 | 0.013733 | 0.20599 | -0.30212 | 55.1605 | 54.7623 | 54.8996 | 54.8126 | 55.1193 | 54.9271 | 8.4778 | 67.955 | -54.6753 | 68.2709 | 123.4177 | -0.11902 | 76.7349 | 0.045776 | 0.31586 | 123.0698 | 123.3765 | 123.0194 | 68.4631 | 68.2709 | 123.1842 | 123.1567 | 76.7349 | 68.4631 | 68.2709 | 123.1567 | 123.0194 | 123.1842 | -55.1834 | -46.4035
5411.7812 | 123.4039 | -68.2526 | 54.895 | 0.034104 | -0.01142 | -0.029074 | 0.0013522 | -0.012313 | -0.0062911 | -0.0024438 | -0.036621 | 0.17395 | -0.33417 | 55.1331 | 54.7943 | 54.8996 | 54.8218 | 55.0964 | 54.9362 | 8.4869 | 67.9184 | -54.7211 | 68.2159 | 123.3856 | -0.10071 | 76.7395 | 0.041198 | 0.29755 | 123.0743 | 123.349 | 123.0469 | 68.4265 | 68.2159 | 123.1888 | 123.1522 | 76.7395 | 68.4265 | 68.2159 | 123.1522 | 123.0469 | 123.1888 | -55.2292 | -46.4081
5412.7812 | 123.3902 | -68.2343 | 54.8721 | 0.21721 | -0.011207 | -0.02352 | 0.0039156 | -0.011672 | -0.0073593 | -0.0030848 | -0.004578 | 0.1236 | -0.35248 | 55.1331 | 54.8447 | 54.9179 | 54.7348 | 55.0644 | 54.9042 | 8.4869 | 67.8818 | -54.7485 | 68.2297 | 123.3673 | -0.027465 | 76.7212 | 0.032044 | 0.3479 | 122.9691 | 123.2986 | 123.0789 | 68.3578 | 68.2297 | 123.1384 | 123.1522 | 76.7212 | 68.3578 | 68.2297 | 123.1522 | 123.0789 | 123.1384 | -55.2246 | -46.3852
5413.7812 | 123.3673 | -68.2526 | 54.8721 | 0.19432 | -0.011207 | -0.023093 | 0.0034884 | -0.010177 | -0.0054367 | -0.001803 | -0.036621 | 0.11444 | -0.35706 | 55.1102 | 54.8264 | 54.8904 | 54.7852 | 55.069 | 54.9179 | 8.4869 | 67.8955 | -54.7577 | 68.2159 | 123.3627 | -0.045776 | 76.7395 | 0.045777 | 0.32043 | 123.0377 | 123.3215 | 123.0789 | 68.367 | 68.2159 | 123.1705 | 123.143 | 76.7395 | 68.367 | 68.2159 | 123.143 | 123.0789 | 123.1705 | -55.2292 | -46.3852
5414.7812 | 123.3994 | -68.2297 | 54.8767 | 0.24773 | -0.011634 | -0.027365 | 0.004343 | -0.0095361 | -0.0052231 | -0.0011622 | -0.004578 | 0.11902 | -0.36621 | 55.1376 | 54.863 | 54.9042 | 54.7394 | 55.0827 | 54.9088 | 8.4869 | 67.8635 | -54.7577 | 68.2251 | 123.3673 | -0.013733 | 76.7166 | 0.032043 | 0.36163 | 122.9691 | 123.3124 | 123.0927 | 68.3487 | 68.2251 | 123.1384 | 123.1338 | 76.7166 | 68.3487 | 68.2251 | 123.1338 | 123.0927 | 123.1384 | -55.2429 | -46.3898
5415.7812 | 123.4177 | -68.2526 | 54.8904 | 0.041733 | -0.010779 | -0.030783 | 0.0034884 | -0.0121 | -0.0056503 | -0.0043664 | 0.009155 | 0.19226 | -0.33417 | 55.1559 | 54.8767 | 54.9042 | 54.8126 | 55.1056 | 54.95 | 8.4869 | 67.9184 | -54.6982 | 68.2617 | 123.4085 | -0.013733 | 76.7395 | 0.059509 | 0.34332 | 123.0652 | 123.3582 | 123.1293 | 68.4448 | 68.2617 | 123.2025 | 123.1567 | 76.7395 | 68.4448 | 68.2617 | 123.1567 | 123.1293 | 123.2025 | -55.2246 | -46.4035
5416.7812 | 123.3948 | -68.2526 | 54.8859 | 0.25536 | -0.010566 | -0.02822 | 0.0032748 | -0.0084681 | -0.0077865 | -0.0011622 | -0.032043 | 0.10529 | -0.37994 | 55.1193 | 54.8492 | 54.9088 | 54.7577 | 55.0735 | 54.8996 | 8.4869 | 67.8726 | -54.7806 | 68.2205 | 123.3719 | -0.036621 | 76.7395 | 0.013733 | 0.3479 | 123.0103 | 123.3261 | 123.1018 | 68.3578 | 68.2205 | 123.1522 | 123.1613 | 76.7395 | 68.3578 | 68.2205 | 123.1613 | 123.1018 | 123.1522 | -55.2658 | -46.3989
5417.7812 | 123.3307 | -68.2846 | 54.8904 | 0.15617 | -0.008216 | -0.02822 | 0.010538 | -0.0097497 | -0.0037277 | -0.0030848 | -0.032043 | 0.21057 | -0.35248 | 55.069 | 54.7714 | 54.808 | 54.8904 | 54.9728 | 54.9408 | 8.4869 | 67.9321 | -54.6799 | 68.2526 | 123.3536 | -0.11902 | 76.7715 | 0.050354 | 0.32044 | 123.175 | 123.2574 | 123.056 | 68.4952 | 68.2526 | 123.2254 | 123.0927 | 76.7715 | 68.4952 | 68.2526 | 123.0927 | 123.056 | 123.2254 | -55.2429 | -46.4035
5418.7812 | 123.4406 | -68.2251 | 54.8538 | 0.19432 | -0.010993 | -0.023093 | 0.0084018 | -0.0091089 | -0.0075729 | -0.0041528 | 0.013733 | 0.14191 | -0.36163 | 55.1468 | 54.863 | 54.8996 | 54.7211 | 55.0735 | 54.9316 | 8.4869 | 67.8635 | -54.7119 | 68.2388 | 123.3719 | 0.009155 | 76.712 | 0.07782 | 0.37537 | 122.9462 | 123.2986 | 123.0881 | 68.367 | 68.2388 | 123.1567 | 123.1247 | 76.712 | 68.367 | 68.2388 | 123.1247 | 123.0881 | 123.1567 | -55.2155 | -46.3669
5419.7812 | 123.4406 | -68.2663 | 54.8309 | 1.4913 | -0.010352 | -0.027579 | 0.004343 | -0.0093225 | -0.0060775 | -0.0039392 | 0.032043 | 0.10071 | -0.39368 | 55.1697 | 54.8904 | 54.9225 | 54.7302 | 55.0781 | 54.895 | 8.4869 | 67.8726 | -54.7302 | 68.2983 | 123.436 | 0.059509 | 76.7532 | 0.064087 | 0.42572 | 122.9965 | 123.3444 | 123.1567 | 68.367 | 68.2983 | 123.1613 | 123.1888 | 76.7532 | 68.367 | 68.2983 | 123.1888 | 123.1567 | 123.1613 | -55.2246 | -46.344
5420.7812 | 123.2849 | -68.2938 | 54.8721 | 0.19432 | -0.009284 | -0.025229 | 0.0098972 | -0.0084681 | -0.0065047 | -0.0047938 | -0.027466 | 0.21057 | -0.3479 | 55.0552 | 54.7668 | 54.7806 | 54.9316 | 54.9362 | 54.9591 | 8.4915 | 67.9459 | -54.6616 | 68.2663 | 123.349 | -0.10529 | 76.7853 | 0.086975 | 0.32043 | 123.2254 | 123.23 | 123.0606 | 68.5043 | 68.2663 | 123.2529 | 123.0743 | 76.7853 | 68.5043 | 68.2663 | 123.0743 | 123.0606 | 123.2529 | -55.22 | -46.3806
5421.7812 | 123.3536 | -68.2388 | 54.8813 | -0.019302 | -0.010139 | -0.025443 | 0.0069064 | -0.0022729 | -0.0075729 | -0.003512 | 0.041199 | 0.23804 | -0.32044 | 55.1605 | 54.8401 | 54.8904 | 54.9225 | 55.0598 | 54.9957 | 8.4824 | 67.9184 | -54.6433 | 68.28 | 123.3994 | -0.041199 | 76.7212 | 0.11444 | 0.36163 | 123.1613 | 123.2986 | 123.0789 | 68.4769 | 68.28 | 123.2346 | 123.1293 | 76.7212 | 68.4769 | 68.28 | 123.1293 | 123.0789 | 123.2346 | -55.2017 | -46.3989
5422.7812 | 123.3078 | -68.2709 | 54.9088 | 0.18669 | -0.0069342 | -0.022879 | 0.0079744 | -0.0050501 | -0.0071457 | -0.0026574 | -0.036621 | 0.21057 | -0.35706 | 55.0369 | 54.776 | 54.8584 | 54.3915 | 54.8813 | 54.9225 | 8.4778 | 67.9138 | -54.6982 | 68.2343 | 123.3078 | -0.13275 | 76.7487 | 0.013733 | 0.32043 | 122.6624 | 123.1522 | 123.0469 | 68.4814 | 68.2343 | 123.1934 | 123.1293 | 76.7487 | 68.4814 | 68.2343 | 123.1293 | 123.0469 | 123.1934 | -55.2658 | -46.431
5423.7812 | 123.3078 | -68.2846 | 54.8859 | 0.064621 | -0.0088568 | -0.022025 | 0.0079744 | -0.0076135 | -0.0082137 | -0.0026574 | -0.032043 | 0.21973 | -0.35248 | 55.0369 | 54.7852 | 54.8126 | 54.9133 | 54.9728 | 54.9911 | 8.4915 | 67.9321 | -54.6661 | 68.2526 | 123.3215 | -0.10071 | 76.7761 | 0.10529 | 0.32044 | 123.1979 | 123.2574 | 123.0698 | 68.5043 | 68.2526 | 123.2758 | 123.0972 | 76.7761 | 68.5043 | 68.2526 | 123.0972 | 123.0698 | 123.2758 | -55.2383 | -46.3943
5424.7812 | 123.3032 | -68.2983 | 54.8904 | 0.1104 | -0.008216 | -0.018607 | 0.0079744 | -0.0069727 | -0.0075729 | -0.0030848 | -0.013733 | 0.21515 | -0.34332 | 55.0507 | 54.7943 | 54.8172 | 54.9591 | 54.982 | 54.9728 | 8.4824 | 67.955 | -54.6753 | 68.2846 | 123.349 | -0.09613 | 76.7807 | 0.082397 | 0.32959 | 123.2574 | 123.2803 | 123.0927 | 68.5135 | 68.2846 | 123.2712 | 123.1155 | 76.7807 | 68.5135 | 68.2846 | 123.1155 | 123.0927 | 123.2712 | -55.2338 | -46.4081
5425.7812 | 123.3353 | -68.3029 | 54.8904 | 0.2401 | -0.0088568 | -0.02352 | 0.0041292 | -0.0054773 | -0.0077865 | -0.00094839 | -0.059509 | 0.20142 | -0.37079 | 55.0461 | 54.7714 | 54.8264 | 54.895 | 54.9774 | 54.9728 | 8.4778 | 67.9321 | -54.689 | 68.2434 | 123.349 | -0.11902 | 76.7807 | 0.082397 | 0.31128 | 123.1979 | 123.2803 | 123.0743 | 68.5043 | 68.2434 | 123.2758 | 123.1293 | 76.7807 | 68.5043 | 68.2434 | 123.1293 | 123.0743 | 123.2758 | -55.2612 | -46.4127
5426.7812 | 123.3261 | -68.2938 | 54.8904 | 0.11803 | -0.0086432 | -0.02587 | 0.0058382 | -0.0067591 | -0.0077865 | -0.0022302 | -0.036621 | 0.21057 | -0.3479 | 55.0323 | 54.7577 | 54.8264 | 54.9088 | 54.9545 | 54.9774 | 8.4824 | 67.9459 | -54.6799 | 68.2571 | 123.3261 | -0.13275 | 76.7761 | 0.086975 | 0.31128 | 123.2025 | 123.2483 | 123.0515 | 68.5043 | 68.2571 | 123.2712 | 123.1201 | 76.7761 | 68.5043 | 68.2571 | 123.1201 | 123.0515 | 123.2712 | -55.2383 | -46.4081
5427.7812 | 123.4222 | -68.2388 | 54.8309 | 0.20195 | -0.0094976 | -0.023734 | 0.0056246 | -0.0056909 | -0.0065047 | -0.0013758 | 0.004578 | 0.14648 | -0.3479 | 55.1056 | 54.8355 | 54.9225 | 54.7623 | 55.0598 | 54.95 | 8.4915 | 67.8909 | -54.6844 | 68.2434 | 123.3444 | 0.004577 | 76.7303 | 0.11902 | 0.35248 | 123.0011 | 123.2986 | 123.0743 | 68.3853 | 68.2434 | 123.1888 | 123.1613 | 76.7303 | 68.3853 | 68.2434 | 123.1613 | 123.0743 | 123.1888 | -55.1788 | -46.3394
5428.7812 | 123.3948 | -68.2571 | 54.8401 | 0.24773 | -0.008216 | -0.027792 | 0.0084018 | -0.0082545 | -0.0039413 | -0.001803 | -0.009155 | 0.15564 | -0.3479 | 55.1056 | 54.8126 | 54.895 | 54.808 | 55.0644 | 54.9683 | 8.4869 | 67.9092 | -54.6844 | 68.248 | 123.3627 | -0.027466 | 76.7441 | 0.12817 | 0.33874 | 123.0652 | 123.3215 | 123.0698 | 68.4128 | 68.248 | 123.2254 | 123.1522 | 76.7441 | 68.4128 | 68.248 | 123.1522 | 123.0698 | 123.2254 | -55.188 | -46.3531
5429.7812 | 123.1613 | -68.3029 | 54.8218 | 0.14092 | -0.0088568 | -0.020102 | 0.0098972 | -0.0093225 | -0.0077865 | -0.0015894 | -0.050354 | 0.2243 | -0.35706 | 55.014 | 54.7256 | 54.7943 | 54.95 | 54.9454 | 54.9957 | 8.4869 | 67.9459 | -54.5975 | 68.2526 | 123.317 | -0.09613 | 76.7899 | 0.17395 | 0.3067 | 123.2529 | 123.2483 | 123.0286 | 68.5272 | 68.2526 | 123.2986 | 123.0972 | 76.7899 | 68.5272 | 68.2526 | 123.0972 | 123.0286 | 123.2986 | -55.1788 | -46.3348
5430.7812 | 123.3124 | -68.28 | 54.9042 | -0.24055 | -0.010139 | -0.021597 | 0.0086154 | -0.0073999 | -0.0073593 | -0.0028712 | -0.032043 | 0.20142 | -0.36163 | 55.0369 | 54.7165 | 54.8172 | 54.9179 | 54.9728 | 55.0049 | 8.4869 | 67.9184 | -54.7028 | 68.248 | 123.317 | -0.18768 | 76.767 | 0.10071 | 0.32959 | 123.1979 | 123.2529 | 122.9965 | 68.4814 | 68.248 | 123.2849 | 123.0972 | 76.767 | 68.4814 | 68.248 | 123.0972 | 122.9965 | 123.2849 | -55.2658 | -46.4172
5431.7812 | 123.3994 | -68.2434 | 54.8584 | 0.27061 | -0.011207 | -0.025015 | 0.0060518 | -0.0065455 | -0.0075729 | -0.00030759 | -0.018311 | 0.16479 | -0.35248 | 55.0919 | 54.8126 | 54.9042 | 54.7485 | 55.0552 | 54.9637 | 8.4869 | 67.8909 | -54.6936 | 68.2251 | 123.3353 | -0.045776 | 76.7303 | 0.10529 | 0.33417 | 122.9919 | 123.2986 | 123.056 | 68.4082 | 68.2251 | 123.2071 | 123.1476 | 76.7303 | 68.4082 | 68.2251 | 123.1476 | 123.056 | 123.2071 | -55.2109 | -46.3715
5432.7812 | 123.317 | -68.2938 | 54.895 | 0.056992 | -0.0088568 | -0.026511 | 0.0077608 | -0.0071863 | -0.0071457 | -0.0030848 | 0.009155 | 0.21057 | -0.3479 | 55.0507 | 54.7852 | 54.8355 | 54.9271 | 55.0095 | 55.0003 | 8.4869 | 67.9459 | -54.6844 | 68.3029 | 123.3444 | -0.10986 | 76.7807 | 0.10528 | 0.35706 | 123.2208 | 123.3032 | 123.0789 | 68.5043 | 68.3029 | 123.2941 | 123.1293 | 76.7807 | 68.5043 | 68.3029 | 123.1293 | 123.0789 | 123.2941 | -55.2429 | -46.4081
5433.7812 | 123.3948 | -68.2434 | 54.8904 | 0.056992 | -0.011207 | -0.025229 | -0.00078396 | -0.0093225 | -0.0060775 | -0.0026574 | -0.009155 | 0.17853 | -0.32959 | 55.0873 | 54.9088 | 54.895 | 54.8309 | 55.1056 | 54.9454 | 8.4869 | 67.9138 | -54.7119 | 68.2343 | 123.3307 | 0.01831 | 76.7303 | 0.054932 | 0.32043 | 123.0743 | 123.349 | 123.1522 | 68.4219 | 68.2343 | 123.1888 | 123.1384 | 76.7303 | 68.4219 | 68.2343 | 123.1384 | 123.1522 | 123.1888 | -55.22 | -46.4035
5434.7812 | 123.3307 | -68.28 | 54.8859 | 0.22484 | -0.010139 | -0.02587 | 0.0086154 | -0.0099633 | -0.0052231 | -0.0015894 | -0.068665 | 0.18768 | -0.37537 | 55.0323 | 54.7897 | 54.8172 | 54.8904 | 54.9774 | 54.9545 | 8.4915 | 67.9047 | -54.6982 | 68.2114 | 123.3124 | -0.09613 | 76.7715 | 0.068665 | 0.3067 | 123.1705 | 123.2574 | 123.0698 | 68.4677 | 68.2114 | 123.2346 | 123.0972 | 76.7715 | 68.4677 | 68.2114 | 123.0972 | 123.0698 | 123.2346 | -55.2612 | -46.3943
5435.7812 | 123.4085 | -68.2343 | 54.863 | 0.20195 | -0.010566 | -0.027792 | 0.0032748 | -0.010177 | -0.0067185 | -0.0013758 | 0.013733 | 0.10529 | -0.33875 | 55.1193 | 54.8767 | 54.9179 | 54.7531 | 55.0919 | 54.9454 | 8.4915 | 67.8955 | -54.7577 | 68.248 | 123.3536 | 0.013733 | 76.7258 | 0.082398 | 0.35248 | 122.9874 | 123.3261 | 123.111 | 68.3395 | 68.248 | 123.1796 | 123.1522 | 76.7258 | 68.3395 | 68.248 | 123.1522 | 123.111 | 123.1796 | -55.2017 | -46.3715
5436.7812 | 123.4268 | -68.2571 | 54.8538 | 0.38506 | -0.01142 | -0.026083 | 0.0051974 | -0.0082545 | -0.0060775 | -0.0022302 | 0.050354 | 0.10529 | -0.3479 | 55.1285 | 54.8813 | 54.9179 | 54.7485 | 55.0919 | 54.9225 | 8.4915 | 67.9092 | -54.7485 | 68.3075 | 123.3856 | 0.027466 | 76.7487 | 0.068664 | 0.39825 | 123.0057 | 123.349 | 123.1384 | 68.3624 | 68.3075 | 123.1796 | 123.175 | 76.7487 | 68.3624 | 68.3075 | 123.175 | 123.1384 | 123.1796 | -55.2017 | -46.3623
5437.7812 | 123.4222 | -68.2388 | 54.8492 | 0.24773 | -0.012275 | -0.026938 | 0.002634 | -0.0084681 | -0.0062911 | -0.0020166 | 0.009155 | 0.10071 | -0.36163 | 55.1376 | 54.9271 | 54.8996 | 54.7668 | 55.0964 | 54.9591 | 8.4869 | 67.8772 | -54.7485 | 68.248 | 123.3765 | 0.07782 | 76.7258 | 0.10986 | 0.37079 | 123.0057 | 123.3353 | 123.1659 | 68.3395 | 68.248 | 123.1979 | 123.1384 | 76.7258 | 68.3395 | 68.248 | 123.1384 | 123.1659 | 123.1979 | -55.2109 | -46.3623
5438.7812 | 123.381 | -68.2663 | 54.8813 | 0.20958 | -0.012702 | -0.027579 | 0.00028404 | -0.010177 | -0.0075729 | -0.0026574 | -0.004578 | 0.10986 | -0.36621 | 55.0873 | 54.8676 | 54.8859 | 54.8035 | 55.0644 | 54.9271 | 8.4869 | 67.9001 | -54.7714 | 68.2617 | 123.3536 | -0.013733 | 76.7532 | 0.045776 | 0.36163 | 123.0698 | 123.3307 | 123.1338 | 68.3762 | 68.2617 | 123.1934 | 123.1522 | 76.7532 | 68.3762 | 68.2617 | 123.1522 | 123.1338 | 123.1934 | -55.2475 | -46.3943
5439.7656 | 123.381 | -68.248 | 54.895 | 0.24773 | -0.010993 | -0.027365 | 0.0077608 | -0.0080407 | -0.0071457 | -0.0015894 | -0.050354 | 0.16937 | -0.36163 | 55.0781 | 54.8264 | 54.8492 | 54.7989 | 55.0507 | 54.9637 | 8.4869 | 67.8864 | -54.7256 | 68.1976 | 123.3261 | -0.068665 | 76.7349 | 0.068664 | 0.31128 | 123.0469 | 123.2986 | 123.0743 | 68.4174 | 68.1976 | 123.2117 | 123.0972 | 76.7349 | 68.4174 | 68.1976 | 123.0972 | 123.0743 | 123.2117 | -55.2567 | -46.4081
5440.7656 | 123.349 | -68.248 | 54.9133 | -0.0040434 | -0.01377 | -0.026511 | 0.0084018 | -0.010391 | -0.0077865 | -0.0050074 | -0.11902 | 0.23804 | -0.28839 | 55.101 | 54.8447 | 54.8813 | 54.895 | 55.0598 | 55.0186 | 8.4778 | 67.9596 | -54.6753 | 68.129 | 123.349 | -0.068664 | 76.7258 | 0.10529 | 0.16937 | 123.143 | 123.3078 | 123.0927 | 68.486 | 68.129 | 123.2666 | 123.1293 | 76.7258 | 68.486 | 68.129 | 123.1293 | 123.0927 | 123.2666 | -55.2017 | -46.4355
5441.7812 | 123.3444 | -68.2571 | 54.9088 | 0.056992 | -0.010352 | -0.027365 | 0.0098972 | -0.0095361 | -0.0084273 | -0.0039392 | 0.036621 | 0.20599 | -0.32959 | 55.0873 | 54.8172 | 54.8309 | 54.9225 | 55.0232 | 55.0186 | 8.4824 | 67.9276 | -54.7028 | 68.2938 | 123.3444 | -0.091552 | 76.7395 | 0.10986 | 0.36621 | 123.1796 | 123.2803 | 123.0743 | 68.4631 | 68.2938 | 123.2758 | 123.0881 | 76.7395 | 68.4631 | 68.2938 | 123.0881 | 123.0743 | 123.2758 | -55.2383 | -46.4264
5442.7969 | 123.3719 | -68.2022 | 54.9133 | -0.19478 | -0.014838 | -0.024588 | -0.0012112 | -0.0091089 | -0.0077865 | -0.0032984 | 0.064087 | 0.21057 | -0.27008 | 55.1102 | 54.9042 | 54.8859 | 54.9133 | 55.1239 | 55.014 | 8.4869 | 67.9321 | -54.7028 | 68.2663 | 123.3124 | -0.009155 | 76.6891 | 0.10071 | 0.33417 | 123.1155 | 123.3261 | 123.1064 | 68.4128 | 68.2663 | 123.2162 | 123.0881 | 76.6891 | 68.4128 | 68.2663 | 123.0881 | 123.1064 | 123.2162 | -55.1834 | -46.4264
5443.7812 | 123.3215 | -68.2617 | 54.9362 | -0.21004 | -0.0077888 | -0.029929 | 0.0039156 | -0.0097497 | -0.0067185 | -0.0043664 | 0.027466 | 0.29755 | -0.28381 | 55.0232 | 54.7256 | 54.7348 | 55.0278 | 55.0323 | 55.0003 | 8.4778 | 67.9779 | -54.6387 | 68.2892 | 123.2849 | -0.21057 | 76.7395 | 0.064087 | 0.31128 | 123.2895 | 123.2941 | 122.9874 | 68.5593 | 68.2892 | 123.262 | 122.9965 | 76.7395 | 68.5593 | 68.2892 | 122.9965 | 122.9874 | 123.262 | -55.22 | -46.4584
5444.7812 | 123.3215 | -68.2434 | 54.9179 | 0.018845 | -0.011848 | -0.026511 | 0.0090426 | -0.0084681 | -0.0092819 | -9.3992e-05 | 0.036621 | 0.21973 | -0.32501 | 55.0919 | 54.7943 | 54.8401 | 54.8996 | 55.0323 | 54.9911 | 8.4824 | 67.9184 | -54.6982 | 68.28 | 123.3353 | -0.1236 | 76.7258 | 0.073242 | 0.36163 | 123.143 | 123.2758 | 123.0377 | 68.4631 | 68.28 | 123.2346 | 123.0835 | 76.7258 | 68.4631 | 68.28 | 123.0835 | 123.0377 | 123.2346 | -55.2429 | -46.4355
5445.7812 | 123.4268 | -68.2068 | 54.8859 | -0.11848 | -0.013129 | -0.025443 | -0.0012112 | -0.0099633 | -0.0080001 | -0.00052119 | 0.07782 | 0.21057 | -0.28381 | 55.1788 | 54.6158 | 54.863 | 54.7394 | 55.1285 | 54.9591 | 8.4824 | 67.923 | -54.6753 | 68.2846 | 123.3856 | -0.27008 | 76.6891 | 0.073242 | 0.36163 | 122.9462 | 123.3353 | 122.8226 | 68.4174 | 68.2846 | 123.1659 | 123.0698 | 76.6891 | 68.4174 | 68.2846 | 123.0698 | 122.8226 | 123.1659 | -55.1697 | -46.4035
5446.7656 | 123.3353 | -68.2571 | 54.895 | 0.0035856 | -0.010566 | -0.027792 | 0.0086154 | -0.0063317 | -0.0082137 | -0.0022302 | 0.045776 | 0.21057 | -0.31586 | 55.101 | 54.7806 | 54.8447 | 54.9133 | 55.0278 | 55.0049 | 8.4824 | 67.9413 | -54.6844 | 68.3029 | 123.3582 | -0.11444 | 76.7395 | 0.10986 | 0.36163 | 123.1705 | 123.2849 | 123.0377 | 68.4677 | 68.3029 | 123.262 | 123.1018 | 76.7395 | 68.4677 | 68.3029 | 123.1018 | 123.0377 | 123.262 | -55.2109 | -46.4127
5447.7656 | 123.3032 | -68.2709 | 54.9179 | 0.14854 | -0.0086432 | -0.026083 | 0.0084018 | -0.0084681 | -0.0090683 | -0.0028712 | -0.041199 | 0.20599 | -0.36621 | 55.0186 | 54.7348 | 54.7852 | 54.9362 | 54.9728 | 55.0049 | 8.4824 | 67.9047 | -54.7119 | 68.2297 | 123.2895 | -0.18311 | 76.7532 | 0.086975 | 0.32501 | 123.2071 | 123.2437 | 123.0057 | 68.4769 | 68.2297 | 123.2758 | 123.056 | 76.7532 | 68.4769 | 68.2297 | 123.056 | 123.0057 | 123.2758 | -55.2841 | -46.4355
5448.7812 | 123.3398 | -68.2434 | 54.8859 | 0.40794 | -0.011634 | -0.027792 | 0.0062656 | -0.0084681 | -0.01035 | -0.0020166 | 0.022888 | 0.23346 | -0.27008 | 55.1239 | 54.8218 | 54.8676 | 54.9088 | 55.0461 | 55.0323 | 8.4778 | 67.9733 | -54.6524 | 68.2663 | 123.3673 | -0.064087 | 76.7212 | 0.14649 | 0.29297 | 123.1522 | 123.2895 | 123.0652 | 68.4769 | 68.2663 | 123.2758 | 123.111 | 76.7212 | 68.4769 | 68.2663 | 123.111 | 123.0652 | 123.2758 | -55.1559 | -46.4081
5449.7812 | 123.349 | -68.2526 | 54.9042 | 0.018845 | -0.009284 | -0.026083 | 0.005411 | -0.0063317 | -0.0082137 | -0.0022302 | 0.054932 | 0.2243 | -0.32501 | 55.0781 | 54.7989 | 54.8401 | 54.9133 | 55.014 | 55.0095 | 8.4869 | 67.9276 | -54.6799 | 68.3075 | 123.3307 | -0.10529 | 76.7395 | 0.10528 | 0.37994 | 123.1659 | 123.2666 | 123.0515 | 68.4769 | 68.3075 | 123.262 | 123.0927 | 76.7395 | 68.4769 | 68.3075 | 123.0927 | 123.0515 | 123.262 | -55.2292 | -46.4172
5450.7812 | 123.4177 | -68.1976 | 54.8904 | -0.14137 | -0.012061 | -0.030142 | 0.00028404 | -0.0091089 | -0.0067185 | -0.0032984 | 0.068665 | 0.20599 | -0.27924 | 55.1376 | 54.9179 | 54.9454 | 54.8538 | 55.1422 | 55.0232 | 8.4869 | 67.9184 | -54.6844 | 68.2663 | 123.3353 | 0.027466 | 76.6846 | 0.13275 | 0.3479 | 123.0515 | 123.3398 | 123.1155 | 68.4036 | 68.2663 | 123.2208 | 123.143 | 76.6846 | 68.4036 | 68.2663 | 123.143 | 123.1155 | 123.2208 | -55.1697 | -46.4035
5451.7812 | 123.4406 | -68.2205 | 54.8813 | 0.0035856 | -0.013557 | -0.025229 | -0.00014316 | -0.010818 | -0.0054367 | -0.0028712 | 0.004578 | 0.16479 | -0.3067 | 55.1147 | 54.8996 | 54.9225 | 54.8126 | 55.1376 | 54.9728 | 8.4915 | 67.9138 | -54.7165 | 68.2251 | 123.3353 | 0.01831 | 76.712 | 0.091552 | 0.31128 | 123.0331 | 123.3582 | 123.1201 | 68.3853 | 68.2251 | 123.1934 | 123.143 | 76.712 | 68.3853 | 68.2251 | 123.143 | 123.1201 | 123.1934 | -55.188 | -46.3898
5452.7812 | 123.4314 | -68.2251 | 54.8904 | 0.018845 | -0.012275 | -0.033347 | 0.0032748 | -0.011886 | -0.0071457 | -0.0024438 | 0.036621 | 0.19226 | -0.29297 | 55.1514 | 54.9133 | 54.9271 | 54.808 | 55.1422 | 54.9591 | 8.4824 | 67.9321 | -54.6982 | 68.2617 | 123.3765 | 0.022888 | 76.7075 | 0.068664 | 0.32959 | 123.0331 | 123.3673 | 123.1384 | 68.4174 | 68.2617 | 123.1842 | 123.1522 | 76.7075 | 68.4174 | 68.2617 | 123.1522 | 123.1384 | 123.1842 | -55.1834 | -46.4081
5453.7656 | 123.4314 | -68.1885 | 54.9316 | -0.13374 | -0.012702 | -0.026083 | 0.0028476 | -0.01274 | -0.0054367 | -0.0024438 | 0.041199 | 0.20142 | -0.27466 | 55.1697 | 54.9408 | 54.9362 | 54.8447 | 55.1743 | 54.9362 | 8.4869 | 67.9138 | -54.7302 | 68.2297 | 123.3582 | 0.009155 | 76.6754 | 0.004577 | 0.31586 | 123.0331 | 123.3627 | 123.1293 | 68.3899 | 68.2297 | 123.1247 | 123.1247 | 76.6754 | 68.3899 | 68.2297 | 123.1247 | 123.1293 | 123.1247 | -55.2063 | -46.4447
5454.7656 | 123.4085 | -68.2251 | 54.9225 | -0.13374 | -0.012275 | -0.030142 | 0.0045566 | -0.011031 | -0.0065047 | -0.0030848 | 0.082397 | 0.21973 | -0.29297 | 55.1605 | 54.9179 | 54.9316 | 54.8676 | 55.1559 | 54.9728 | 8.4869 | 67.9321 | -54.7028 | 68.3075 | 123.3856 | -0.004577 | 76.712 | 0.050354 | 0.37537 | 123.0927 | 123.381 | 123.143 | 68.4448 | 68.3075 | 123.1979 | 123.1567 | 76.712 | 68.4448 | 68.3075 | 123.1567 | 123.143 | 123.1979 | -55.2155 | -46.4355
5455.7812 | 123.4131 | -68.2297 | 54.9271 | -0.17189 | -0.013984 | -0.026511 | 0.0039156 | -0.014022 | -0.0080001 | -0.0028712 | 0.086975 | 0.21057 | -0.27466 | 55.1743 | 54.9316 | 54.9362 | 54.8584 | 55.1559 | 54.9728 | 8.4915 | 67.955 | -54.7165 | 68.3166 | 123.4039 | 0.004578 | 76.7212 | 0.045776 | 0.36163 | 123.0881 | 123.3856 | 123.1613 | 68.4402 | 68.3166 | 123.2025 | 123.1659 | 76.7212 | 68.4402 | 68.3166 | 123.1659 | 123.1613 | 123.2025 | -55.2017 | -46.4355
5456.7812 | 123.468 | -68.2159 | 54.8813 | -0.011673 | -0.012916 | -0.028006 | 0.0017794 | -0.011886 | -0.0077865 | -0.00094839 | 0.068665 | 0.20142 | -0.29755 | 55.1788 | 54.95 | 54.9454 | 54.8172 | 55.1926 | 54.9637 | 8.4869 | 67.9184 | -54.6799 | 68.2846 | 123.3948 | 0.068664 | 76.7029 | 0.082397 | 0.36621 | 123.0331 | 123.4085 | 123.1659 | 68.4174 | 68.2846 | 123.1796 | 123.1613 | 76.7029 | 68.4174 | 68.2846 | 123.1613 | 123.1659 | 123.1796 | -55.1788 | -46.3943
5457.7812 | 123.4131 | -68.2434 | 54.9042 | 0.026474 | -0.012916 | -0.02587 | 0.0013522 | -0.01274 | -0.0080001 | -0.006289 | -0.022888 | 0.17395 | -0.32044 | 55.1376 | 54.8996 | 54.8813 | 54.8172 | 55.101 | 54.95 | 8.4869 | 67.923 | -54.7302 | 68.2205 | 123.381 | -0.004578 | 76.7303 | 0.045776 | 0.29755 | 123.0606 | 123.3444 | 123.143 | 68.4174 | 68.2205 | 123.1934 | 123.1247 | 76.7303 | 68.4174 | 68.2205 | 123.1247 | 123.143 | 123.1934 | -55.2246 | -46.4172
5458.7812 | 123.3856 | -68.2343 | 54.8996 | 0.17143 | -0.015052 | -0.027792 | 0.0041292 | -0.011672 | -0.0071457 | -0.0024438 | 0.09613 | 0.15106 | -0.33875 | 55.101 | 54.8538 | 54.8447 | 54.8264 | 55.0598 | 54.9316 | 8.4824 | 67.8955 | -54.7485 | 68.3304 | 123.3353 | -0.045776 | 76.7166 | 0.032044 | 0.43488 | 123.0606 | 123.2941 | 123.0881 | 68.3853 | 68.3304 | 123.1659 | 123.0789 | 76.7166 | 68.3853 | 68.3304 | 123.0789 | 123.0881 | 123.1659 | -55.2383 | -46.4172
5459.7812 | 123.4497 | -68.2022 | 54.9088 | -0.065079 | -0.012916 | -0.026297 | 0.001993 | -0.012954 | -0.0052231 | -0.0024438 | 0.054932 | 0.1831 | -0.28839 | 55.1788 | 54.9271 | 54.9316 | 54.7852 | 55.1559 | 54.9866 | 8.4732 | 67.9138 | -54.7256 | 68.2571 | 123.381 | 0.018311 | 76.6754 | 0.07782 | 0.34332 | 122.9874 | 123.3582 | 123.1293 | 68.3853 | 68.2571 | 123.1888 | 123.1338 | 76.6754 | 68.3853 | 68.2571 | 123.1338 | 123.1293 | 123.1888 | -55.1971 | -46.4355
5460.7656 | 123.3994 | -68.2571 | 54.8996 | 0.11803 | -0.013343 | -0.029929 | 0.0017794 | -0.012954 | -0.0041549 | -0.0047938 | -0.009155 | 0.16022 | -0.31128 | 55.1147 | 54.8813 | 54.8859 | 54.8264 | 55.0735 | 54.9408 | 8.4869 | 67.9459 | -54.7394 | 68.248 | 123.3719 | -0.01831 | 76.7441 | 0.041199 | 0.30212 | 123.0835 | 123.3307 | 123.1384 | 68.4174 | 68.248 | 123.1979 | 123.143 | 76.7441 | 68.4174 | 68.248 | 123.143 | 123.1384 | 123.1979 | -55.2109 | -46.4127
5461.7656 | 123.3902 | -68.248 | 54.8721 | 0.095139 | -0.010993 | -0.025229 | 0.002634 | -0.0091089 | -0.0050095 | -0.0013758 | -0.013733 | 0.16937 | -0.32044 | 55.101 | 54.8813 | 54.8584 | 54.8218 | 55.0873 | 54.9316 | 8.4824 | 67.9276 | -54.7028 | 68.2343 | 123.349 | 0.009156 | 76.7303 | 0.05951 | 0.3067 | 123.0698 | 123.3353 | 123.1293 | 68.4174 | 68.2343 | 123.1796 | 123.1064 | 76.7303 | 68.4174 | 68.2343 | 123.1064 | 123.1293 | 123.1796 | -55.1926 | -46.3898
5462.7812 | 123.436 | -68.2205 | 54.9271 | -0.11848 | -0.013557 | -0.028433 | 0.0011386 | -0.012313 | -0.0073593 | -0.0030848 | 0.09613 | 0.20142 | -0.28381 | 55.2017 | 54.9316 | 54.9271 | 54.8264 | 55.1605 | 54.9728 | 8.4824 | 67.9367 | -54.7256 | 68.3166 | 123.4222 | 0.004578 | 76.7029 | 0.045776 | 0.37994 | 123.0469 | 123.381 | 123.1522 | 68.4219 | 68.3166 | 123.1934 | 123.1476 | 76.7029 | 68.4219 | 68.3166 | 123.1476 | 123.1522 | 123.1934 | -55.2109 | -46.4447
5463.7812 | 123.3124 | -68.2663 | 54.9545 | -0.33974 | -0.0088568 | -0.02822 | 0.0058382 | -0.011672 | -0.0045821 | -0.003512 | 0.036621 | 0.26093 | -0.28839 | 55.1102 | 54.863 | 54.8309 | 55.0049 | 55.0323 | 55.014 | 8.4824 | 67.9779 | -54.6936 | 68.3029 | 123.3765 | -0.091553 | 76.7487 | 0.059509 | 0.32501 | 123.2712 | 123.2986 | 123.1293 | 68.5272 | 68.3029 | 123.2803 | 123.0972 | 76.7487 | 68.5272 | 68.3029 | 123.0972 | 123.1293 | 123.2803 | -55.2429 | -46.4722
5464.7656 | 123.4497 | -68.2251 | 54.8584 | 0.26299 | -0.015266 | -0.022238 | 0.010111 | -0.0099633 | -0.0054367 | -0.0050074 | 0.27924 | 0.15106 | -0.35706 | 55.1468 | 54.895 | 54.9042 | 54.7302 | 55.069 | 54.9225 | 8.4824 | 67.868 | -54.7073 | 68.5043 | 123.3719 | 0.036622 | 76.7075 | 0.064087 | 0.63629 | 122.9553 | 123.2941 | 123.1201 | 68.3762 | 68.5043 | 123.1476 | 123.1293 | 76.7075 | 68.3762 | 68.5043 | 123.1293 | 123.1201 | 123.1476 | -55.2155 | -46.376
5465.7812 | 123.4268 | -68.2571 | 54.8904 | 0.23247 | -0.010993 | -0.026511 | 0.003702 | -0.0091089 | -0.0054367 | -0.001803 | -0.013733 | 0.11444 | -0.37079 | 55.1559 | 54.895 | 54.9088 | 54.7165 | 55.0735 | 54.9225 | 8.4824 | 67.8864 | -54.776 | 68.2434 | 123.4131 | 0.004578 | 76.7395 | 0.032043 | 0.35706 | 122.9736 | 123.3307 | 123.1522 | 68.3716 | 68.2434 | 123.1796 | 123.1659 | 76.7395 | 68.3716 | 68.2434 | 123.1659 | 123.1522 | 123.1796 | -55.2612 | -46.4081
5466.7812 | 123.4268 | -68.2388 | 54.863 | 0.27824 | -0.010993 | -0.026083 | 0.0028476 | -0.010391 | -0.0052231 | -0.0032984 | 0.004578 | 0.10529 | -0.37079 | 55.1285 | 54.9042 | 54.863 | 54.7668 | 55.0735 | 54.9042 | 8.4824 | 67.868 | -54.7577 | 68.2434 | 123.3673 | 0.041199 | 76.7212 | 0.041199 | 0.37537 | 123.0057 | 123.3124 | 123.143 | 68.3441 | 68.2434 | 123.143 | 123.1018 | 76.7212 | 68.3441 | 68.2434 | 123.1018 | 123.143 | 123.143 | -55.2338 | -46.3806
5467.7656 | 123.3902 | -68.2755 | 54.8676 | 0.24773 | -0.009284 | -0.027792 | 0.0024202 | -0.010177 | -0.0062911 | -0.0022302 | -0.027466 | 0.13275 | -0.36621 | 55.1193 | 54.863 | 54.8859 | 54.7806 | 55.0644 | 54.9271 | 8.4824 | 67.9092 | -54.7348 | 68.248 | 123.3948 | -0.004578 | 76.7578 | 0.059509 | 0.33875 | 123.056 | 123.3398 | 123.1384 | 68.4082 | 68.248 | 123.2025 | 123.1613 | 76.7578 | 68.4082 | 68.248 | 123.1613 | 123.1384 | 123.2025 | -55.2338 | -46.3852
5468.7656 | 123.4085 | -68.248 | 54.8767 | 0.19432 | -0.010566 | -0.026938 | 0.0060518 | -0.0093225 | -0.0073593 | 0.00011961 | 0.30212 | 0.12817 | -0.3479 | 55.1147 | 54.8355 | 54.895 | 54.7623 | 55.0964 | 54.9316 | 8.4869 | 67.9001 | -54.7485 | 68.5501 | 123.3627 | -0.041199 | 76.7349 | 0.054932 | 0.65002 | 123.0103 | 123.3444 | 123.0835 | 68.3762 | 68.5501 | 123.1796 | 123.143 | 76.7349 | 68.3762 | 68.5501 | 123.143 | 123.0835 | 123.1796 | -55.2246 | -46.3898
5469.7812 | 123.4268 | -68.2068 | 54.8676 | 0.27824 | -0.0094976 | -0.028433 | 0.0056246 | -0.0099633 | -0.0067185 | -0.00073479 | 0.009155 | 0.10986 | -0.36621 | 55.1331 | 54.895 | 54.9088 | 54.7485 | 55.069 | 54.9271 | 8.4824 | 67.8406 | -54.7577 | 68.2159 | 123.3398 | 0.027466 | 76.6891 | 0.059509 | 0.37537 | 122.9553 | 123.2758 | 123.1018 | 68.3167 | 68.2159 | 123.1338 | 123.1155 | 76.6891 | 68.3167 | 68.2159 | 123.1155 | 123.1018 | 123.1338 | -55.2338 | -46.3852
5470.7812 | 123.4131 | -68.2388 | 54.863 | 0.25536 | -0.009284 | -0.028433 | 0.0022066 | -0.010177 | -0.0052231 | -0.001803 | 0.018311 | 0.12817 | -0.3479 | 55.1422 | 54.8996 | 54.9088 | 54.7531 | 55.0781 | 54.9316 | 8.4824 | 67.8909 | -54.7348 | 68.2571 | 123.381 | 0.036621 | 76.7212 | 0.068665 | 0.36621 | 122.9919 | 123.317 | 123.1384 | 68.367 | 68.2571 | 123.1705 | 123.1476 | 76.7212 | 68.367 | 68.2571 | 123.1476 | 123.1384 | 123.1705 | -55.2109 | -46.3806
5471.7812 | 123.5596 | -68.2159 | 54.9088 | 0.1638 | -0.011848 | -0.029288 | 0.0015658 | -0.011672 | -0.0071457 | -0.0028712 | -0.041199 | 0.1236 | -0.37537 | 55.101 | 54.8904 | 54.8813 | 54.7943 | 55.0507 | 54.9179 | 8.4824 | 67.8406 | -54.7852 | 68.1747 | 123.317 | -0.01831 | 76.6983 | 0.009156 | 0.33417 | 123.0103 | 123.2666 | 123.1064 | 68.3395 | 68.1747 | 123.1338 | 123.0972 | 76.6983 | 68.3395 | 68.1747 | 123.0972 | 123.1064 | 123.1338 | -55.2841 | -46.4264
5472.7812 | 123.3902 | -68.2343 | 54.8859 | 0.1638 | -0.01142 | -0.026511 | 0.0049838 | -0.012313 | -0.0041549 | -0.003512 | -0.068665 | 0.16479 | -0.27924 | 55.1147 | 54.8904 | 54.8859 | 54.8264 | 55.0781 | 54.9271 | 8.4869 | 67.955 | -54.7211 | 68.1656 | 123.349 | 0.004578 | 76.7212 | 0.041199 | 0.21057 | 123.0606 | 123.3124 | 123.1247 | 68.399 | 68.1656 | 123.1613 | 123.1201 | 76.7212 | 68.399 | 68.1656 | 123.1201 | 123.1247 | 123.1613 | -55.1651 | -46.3989
5473.7656 | 123.4131 | -68.2434 | 54.8676 | 0.25536 | -0.010139 | -0.027152 | 0.005411 | -0.0093225 | -0.0065047 | -0.0026574 | 0.004578 | 0.1236 | -0.3479 | 55.1376 | 54.9088 | 54.9088 | 54.7485 | 55.0873 | 54.9271 | 8.4778 | 67.8955 | -54.744 | 68.248 | 123.381 | 0.041198 | 76.7212 | 0.059509 | 0.35248 | 122.9919 | 123.3307 | 123.1522 | 68.367 | 68.248 | 123.1705 | 123.1522 | 76.7212 | 68.367 | 68.248 | 123.1522 | 123.1522 | 123.1705 | -55.2155 | -46.3898
5474.7656 | 123.4268 | -68.2526 | 54.8721 | 0.24773 | -0.012702 | -0.025656 | 0.0077608 | -0.010818 | -0.0067185 | -0.0011622 | 0.009155 | 0.13275 | -0.33875 | 55.1514 | 54.8996 | 54.9133 | 54.744 | 55.0781 | 54.9042 | 8.4824 | 67.9138 | -54.7394 | 68.2617 | 123.4039 | 0.027466 | 76.7349 | 0.032044 | 0.3479 | 122.9965 | 123.3307 | 123.1522 | 68.3853 | 68.2617 | 123.1567 | 123.1659 | 76.7349 | 68.3853 | 68.2617 | 123.1659 | 123.1522 | 123.1567 | -55.2109 | -46.3898
5475.7656 | 123.4268 | -68.2526 | 54.8767 | 0.22484 | -0.0088568 | -0.028433 | 0.0081882 | -0.011672 | -0.0065047 | -0.0047938 | 0.022888 | 0.12817 | -0.33875 | 55.1651 | 54.9133 | 54.9133 | 54.7394 | 55.0827 | 54.9225 | 8.4824 | 67.9138 | -54.7485 | 68.2755 | 123.4177 | 0.036621 | 76.7349 | 0.045776 | 0.36163 | 122.9919 | 123.3353 | 123.1659 | 68.3807 | 68.2755 | 123.175 | 123.1659 | 76.7349 | 68.3807 | 68.2755 | 123.1659 | 123.1659 | 123.175 | -55.2155 | -46.3943
5476.7812 | 123.3627 | -68.2434 | 54.9042 | 0.26299 | -0.0090704 | -0.027365 | 0.008829 | -0.0073999 | -0.0047957 | -0.00094839 | -0.050354 | 0.18768 | -0.37537 | 55.0781 | 54.8401 | 54.8355 | 54.8447 | 55.0003 | 54.95 | 8.4778 | 67.868 | -54.7165 | 68.1931 | 123.3215 | -0.064087 | 76.7212 | 0.045776 | 0.32501 | 123.0881 | 123.2437 | 123.0835 | 68.4311 | 68.1931 | 123.1934 | 123.0789 | 76.7212 | 68.4311 | 68.1931 | 123.0789 | 123.0835 | 123.1934 | -55.2795 | -46.4264
5477.7812 | 123.3627 | -68.2343 | 54.9316 | -0.13374 | -0.007575 | -0.023734 | 0.0060518 | -0.010818 | -0.0077865 | -0.0032984 | 0.022888 | 0.2655 | -0.31128 | 55.1331 | 54.8996 | 54.8676 | 54.9362 | 55.069 | 54.9866 | 8.4732 | 67.923 | -54.6661 | 68.2571 | 123.3673 | -0.032044 | 76.7075 | 0.054931 | 0.33417 | 123.1705 | 123.3032 | 123.1338 | 68.4998 | 68.2571 | 123.2208 | 123.1018 | 76.7075 | 68.4998 | 68.2571 | 123.1018 | 123.1338 | 123.2208 | -55.2429 | -46.4584
5478.7812 | 123.3765 | -68.2663 | 54.8721 | 0.26299 | -0.0094976 | -0.026724 | 0.0069064 | -0.0073999 | -0.0062911 | -0.001803 | -0.032043 | 0.19226 | -0.38452 | 55.0919 | 54.863 | 54.8584 | 54.8126 | 55.014 | 54.9866 | 8.4824 | 67.8818 | -54.6799 | 68.2343 | 123.3582 | -0.009155 | 76.7487 | 0.11444 | 0.35248 | 123.0789 | 123.2803 | 123.1293 | 68.4586 | 68.2343 | 123.2529 | 123.1247 | 76.7487 | 68.4586 | 68.2343 | 123.1247 | 123.1293 | 123.2529 | -55.2567 | -46.3898
5479.7812 | 123.3582 | -68.2617 | 54.863 | 0.2935 | -0.0069342 | -0.025229 | 0.00712 | -0.0084681 | -0.0033005 | -0.00073479 | -0.036621 | 0.19226 | -0.37079 | 55.0644 | 54.8401 | 54.8264 | 54.8401 | 55.0095 | 54.9271 | 8.4869 | 67.8909 | -54.6707 | 68.2251 | 123.3261 | -0.022888 | 76.7487 | 0.064087 | 0.33417 | 123.1018 | 123.2712 | 123.1018 | 68.454 | 68.2251 | 123.1888 | 123.0881 | 76.7487 | 68.454 | 68.2251 | 123.0881 | 123.1018 | 123.1888 | -55.2338 | -46.376
5480.7656 | 123.4268 | -68.2434 | 54.8584 | 0.24773 | -0.0094976 | -0.024802 | 0.0062656 | -0.0080407 | -0.0047957 | -0.0015894 | 0.013733 | 0.1236 | -0.35248 | 55.1376 | 54.8721 | 54.744 | 54.8218 | 55.2109 | 54.8996 | 8.4824 | 67.8909 | -54.7348 | 68.2571 | 123.381 | 0.013733 | 76.7258 | 0.041199 | 0.36621 | 123.0652 | 123.4543 | 123.1155 | 68.367 | 68.2571 | 123.143 | 122.9874 | 76.7258 | 68.367 | 68.2571 | 122.9874 | 123.1155 | 123.143 | -55.2109 | -46.376
5481.7656 | 123.4314 | -68.2343 | 54.8584 | 0.3698 | -0.010139 | -0.024588 | 0.0051974 | -0.0078271 | -0.0050095 | -0.0026574 | -0.004578 | 0.15564 | -0.35706 | 55.1285 | 54.895 | 54.9088 | 54.7531 | 55.0873 | 54.95 | 8.4824 | 67.8772 | -54.7028 | 68.2297 | 123.3627 | 0.036622 | 76.7166 | 0.091553 | 0.35248 | 122.9874 | 123.3215 | 123.1293 | 68.3899 | 68.2297 | 123.1842 | 123.143 | 76.7166 | 68.3899 | 68.2297 | 123.143 | 123.1293 | 123.1842 | -55.2155 | -46.376
5482.7656 | 123.4131 | -68.2617 | 54.8355 | 0.25536 | -0.0067206 | -0.022665 | 0.0056246 | -0.0073999 | -0.0047957 | -0.0039392 | 0 | 0.16937 | -0.35706 | 55.1147 | 54.8767 | 54.8996 | 54.7714 | 55.069 | 54.9637 | 8.4869 | 67.9047 | -54.6661 | 68.2617 | 123.3765 | 0.041199 | 76.7487 | 0.12817 | 0.35706 | 123.0331 | 123.3307 | 123.1384 | 68.4311 | 68.2617 | 123.2254 | 123.1613 | 76.7487 | 68.4311 | 68.2617 | 123.1613 | 123.1384 | 123.2254 | -55.1926 | -46.3486
5483.7812 | 123.3124 | -68.2755 | 54.8904 | 2.9028 | -0.0069342 | -0.02822 | 0.0090426 | -0.010177 | -0.0075729 | -0.0028712 | 0.11902 | 0.1831 | -0.38452 | 55.0735 | 54.8355 | 54.7897 | 54.9179 | 54.9637 | 54.9683 | 8.4778 | 67.8909 | -54.7073 | 68.3945 | 123.349 | -0.054932 | 76.7532 | 0.07782 | 0.50354 | 123.1934 | 123.2391 | 123.111 | 68.4586 | 68.3945 | 123.2437 | 123.0652 | 76.7532 | 68.4586 | 68.3945 | 123.0652 | 123.111 | 123.2437 | -55.275 | -46.4127
5484.7812 | 123.3261 | -68.2846 | 54.8859 | 0.21721 | -0.0062934 | -0.027365 | 0.0056246 | -0.0095361 | -0.0062911 | -0.00094839 | -0.050354 | 0.20599 | -0.35248 | 55.0507 | 54.7897 | 54.808 | 54.895 | 54.9683 | 54.9637 | 8.4824 | 67.9321 | -54.6799 | 68.2343 | 123.3353 | -0.09613 | 76.767 | 0.07782 | 0.30212 | 123.1796 | 123.2529 | 123.0743 | 68.4906 | 68.2343 | 123.2483 | 123.0927 | 76.767 | 68.4906 | 68.2343 | 123.0927 | 123.0743 | 123.2483 | -55.2383 | -46.4035
5485.7812 | 123.3215 | -68.2938 | 54.9088 | 0.1638 | -0.0062934 | -0.024374 | 0.0075472 | -0.0084681 | -0.0052231 | -0.003512 | -0.041199 | 0.21057 | -0.35706 | 55.0461 | 54.7714 | 54.7852 | 54.9225 | 54.9683 | 54.9774 | 8.4869 | 67.9367 | -54.6982 | 68.2526 | 123.3398 | -0.13733 | 76.7807 | 0.068665 | 0.31586 | 123.2162 | 123.262 | 123.0652 | 68.5043 | 68.2526 | 123.2712 | 123.0789 | 76.7807 | 68.5043 | 68.2526 | 123.0789 | 123.0652 | 123.2712 | -55.2658 | -46.4218
5486.7812 | 123.3261 | -68.3121 | 54.8996 | -0.38551 | -0.008216 | -0.027152 | 0.0062656 | -0.0091089 | -0.0041549 | -0.0032984 | -0.068665 | 0.19684 | -0.37994 | 55.0278 | 54.7852 | 54.7943 | 54.9271 | 54.9591 | 54.9728 | 8.4824 | 67.9321 | -54.7028 | 68.2434 | 123.3398 | -0.11444 | 76.7944 | 0.073242 | 0.31128 | 123.2391 | 123.2712 | 123.0972 | 68.5089 | 68.2434 | 123.2849 | 123.1064 | 76.7944 | 68.5089 | 68.2434 | 123.1064 | 123.0972 | 123.2849 | -55.2795 | -46.4172
5487.7656 | 123.3673 | -68.2663 | 54.8813 | 0.25536 | -0.0073614 | -0.029929 | 0.0056246 | -0.0078271 | -0.0045821 | -0.00030759 | -0.059509 | 0.17853 | -0.35706 | 55.0552 | 54.8264 | 54.8447 | 54.8355 | 55.0095 | 54.95 | 8.4778 | 67.9092 | -54.7028 | 68.2068 | 123.3215 | -0.054932 | 76.7441 | 0.068664 | 0.29755 | 123.1018 | 123.2758 | 123.0927 | 68.4448 | 68.2068 | 123.2162 | 123.111 | 76.7441 | 68.4448 | 68.2068 | 123.111 | 123.0927 | 123.2162 | -55.2383 | -46.4035
5488.7656 | 123.3398 | -68.2846 | 54.895 | 0.23247 | -0.0088568 | -0.023306 | 0.0079744 | -0.0088953 | -0.0041549 | -0.0026574 | -0.041199 | 0.20599 | -0.36163 | 55.0369 | 54.8264 | 54.8264 | 54.895 | 54.9774 | 54.9545 | 8.4915 | 67.923 | -54.689 | 68.2434 | 123.3215 | -0.068665 | 76.7761 | 0.059509 | 0.32043 | 123.1796 | 123.262 | 123.111 | 68.4906 | 68.2434 | 123.2391 | 123.111 | 76.7761 | 68.4906 | 68.2434 | 123.111 | 123.111 | 123.2391 | -55.2567 | -46.4035
5489.7656 | 123.3215 | -68.2892 | 54.8813 | 0.20958 | -0.0088568 | -0.025443 | 0.0056246 | -0.0078271 | -0.0054367 | -0.00073479 | -0.054932 | 0.21973 | -0.37079 | 55.0461 | 54.8172 | 54.808 | 54.8996 | 54.9728 | 54.9591 | 8.4869 | 67.9184 | -54.6616 | 68.2343 | 123.3353 | -0.064087 | 76.7761 | 0.077819 | 0.31586 | 123.1888 | 123.262 | 123.1064 | 68.5089 | 68.2343 | 123.2483 | 123.0972 | 76.7761 | 68.5089 | 68.2343 | 123.0972 | 123.1064 | 123.2483 | -55.2521 | -46.3943
5490.7812 | 123.3261 | -68.2526 | 54.8996 | 0.087509 | -0.0071478 | -0.027365 | 0.008829 | -0.0061181 | -0.0047957 | -0.0020166 | 0.013733 | 0.25177 | -0.33417 | 55.0507 | 54.8401 | 54.8172 | 54.9454 | 55.0278 | 54.9911 | 8.4732 | 67.9184 | -54.6478 | 68.2663 | 123.3032 | -0.059509 | 76.7258 | 0.091553 | 0.3479 | 123.1979 | 123.2803 | 123.0927 | 68.5043 | 68.2663 | 123.2437 | 123.0698 | 76.7258 | 68.5043 | 68.2663 | 123.0698 | 123.0927 | 123.2437 | -55.2338 | -46.4264
5491.7969 | 123.3215 | -68.2709 | 54.9088 | 0.056992 | -0.009925 | -0.02352 | 0.0086154 | -0.0065455 | -0.0041549 | -0.00458 | 0.004578 | 0.22888 | -0.35706 | 55.0507 | 54.8355 | 54.8264 | 54.95 | 55.0095 | 54.9957 | 8.4778 | 67.9138 | -54.6799 | 68.2755 | 123.3215 | -0.073242 | 76.7487 | 0.086976 | 0.36163 | 123.2208 | 123.2803 | 123.1064 | 68.4998 | 68.2755 | 123.2666 | 123.0972 | 76.7487 | 68.4998 | 68.2755 | 123.0972 | 123.1064 | 123.2666 | -55.2658 | -46.431
5492.7812 | 123.3398 | -68.2892 | 54.9133 | 0.12566 | -0.0080024 | -0.023093 | 0.0075472 | -0.0071863 | -0.0067185 | -0.001803 | -0.004578 | 0.22888 | -0.35706 | 55.0507 | 54.8355 | 54.8218 | 54.9271 | 54.982 | 54.9683 | 8.4686 | 67.9321 | -54.6844 | 68.2846 | 123.3398 | -0.07782 | 76.7578 | 0.054932 | 0.35248 | 123.2162 | 123.2712 | 123.1247 | 68.5181 | 68.2846 | 123.2574 | 123.111 | 76.7578 | 68.5181 | 68.2846 | 123.111 | 123.1247 | 123.2574 | -55.2704 | -46.4447
5493.7812 | 123.3307 | -68.2983 | 54.9179 | 0.064621 | -0.009925 | -0.023093 | 0.0051974 | -0.0061181 | -0.0065047 | -0.00094839 | 0.013733 | 0.23346 | -0.33417 | 55.0507 | 54.8264 | 54.8401 | 54.9316 | 55.014 | 55.0049 | 8.4732 | 67.9642 | -54.6844 | 68.3121 | 123.349 | -0.091553 | 76.7715 | 0.086975 | 0.3479 | 123.23 | 123.3124 | 123.1247 | 68.5318 | 68.3121 | 123.3032 | 123.1384 | 76.7715 | 68.5318 | 68.3121 | 123.1384 | 123.1247 | 123.3032 | -55.2521 | -46.4447
5494.7656 | 123.317 | -68.2663 | 54.895 | -1.8275 | -0.0060798 | -0.026724 | 0.0060518 | -0.0063317 | -0.0067185 | -0.0015894 | -0.013733 | 0.18768 | -0.37994 | 54.9957 | 54.7806 | 54.7897 | 54.9271 | 54.9728 | 55.0049 | 8.4778 | 67.8864 | -54.7073 | 68.2526 | 123.262 | -0.11444 | 76.7441 | 0.10986 | 0.36621 | 123.1934 | 123.2391 | 123.0469 | 68.454 | 68.2526 | 123.2712 | 123.056 | 76.7441 | 68.454 | 68.2526 | 123.056 | 123.0469 | 123.2712 | -55.275 | -46.4172
5495.7656 | 123.3536 | -68.2526 | 54.9271 | 0.14092 | -0.0071478 | -0.023306 | 0.0062656 | -0.0059045 | -0.0058639 | -0.0030848 | -0.009155 | 0.23804 | -0.35706 | 55.0232 | 54.8218 | 54.808 | 54.6387 | 55.1331 | 54.9271 | 8.4824 | 67.8955 | -54.689 | 68.2434 | 123.2758 | -0.10529 | 76.7349 | 0 | 0.3479 | 122.8912 | 123.3856 | 123.0743 | 68.4906 | 68.2434 | 123.1796 | 123.0606 | 76.7349 | 68.4906 | 68.2434 | 123.0606 | 123.0743 | 123.1796 | -55.2841 | -46.4447
5496.7656 | 123.2986 | -68.2663 | 54.8996 | 0.07988 | -0.009925 | -0.024161 | 0.005411 | -0.0088953 | -0.0050095 | -0.0037256 | -0.027466 | 0.21515 | -0.37079 | 55.0369 | 54.8401 | 54.808 | 54.9316 | 54.9866 | 54.982 | 8.4778 | 67.8955 | -54.6844 | 68.2388 | 123.3032 | -0.059509 | 76.7441 | 0.082398 | 0.34332 | 123.1979 | 123.2529 | 123.1064 | 68.4814 | 68.2388 | 123.2483 | 123.0743 | 76.7441 | 68.4814 | 68.2388 | 123.0743 | 123.1064 | 123.2483 | -55.2704 | -46.4218
5497.7812 | 123.3765 | -68.2617 | 54.9179 | -0.04219 | -0.0090704 | -0.028861 | 0.0094698 | -0.0084681 | -0.0067185 | -0.0013758 | 0.045776 | 0.24261 | -0.32959 | 55.1285 | 54.9408 | 54.8721 | 54.9683 | 55.0781 | 55.0232 | 8.4732 | 67.9321 | -54.6753 | 68.3075 | 123.3902 | 0.022888 | 76.7349 | 0.10529 | 0.37537 | 123.23 | 123.3398 | 123.2025 | 68.5043 | 68.3075 | 123.2849 | 123.1338 | 76.7349 | 68.5043 | 68.3075 | 123.1338 | 123.2025 | 123.2849 | -55.2475 | -46.4447
5498.7812 | 123.3765 | -68.2526 | 54.9271 | -0.149 | -0.009925 | -0.022665 | 0.0056246 | -0.0088953 | -0.0050095 | -0.0032984 | 0.036621 | 0.27924 | -0.31128 | 55.0964 | 54.6844 | 54.8813 | 54.9591 | 55.0781 | 55.0323 | 8.4778 | 67.9413 | -54.6478 | 68.2892 | 123.349 | -0.24261 | 76.7303 | 0.10529 | 0.3479 | 123.2117 | 123.3307 | 122.937 | 68.5318 | 68.2892 | 123.2849 | 123.1338 | 76.7303 | 68.5318 | 68.2892 | 123.1338 | 122.937 | 123.2849 | -55.2383 | -46.4493
5499.7812 | 123.3582 | -68.2526 | 54.9042 | -0.11085 | -0.009284 | -0.025656 | 0.0069064 | -0.0082545 | -0.0058639 | -0.0039392 | 0.050354 | 0.26093 | -0.35706 | 55.1331 | 54.744 | 54.863 | 54.982 | 55.0827 | 55.0095 | 8.4778 | 67.8955 | -54.6433 | 68.3029 | 123.3856 | -0.16022 | 76.7303 | 0.10528 | 0.40741 | 123.2346 | 123.3353 | 122.9965 | 68.5135 | 68.3029 | 123.262 | 123.1155 | 76.7303 | 68.5135 | 68.3029 | 123.1155 | 122.9965 | 123.262 | -55.2612 | -46.4264
5500.7812 | 123.3398 | -68.2526 | 54.9179 | -0.11085 | -0.009925 | -0.029074 | 0.0086154 | -0.0095361 | -0.0077865 | -0.0030848 | 0.027466 | 0.27924 | -0.29755 | 55.0919 | 54.689 | 54.8721 | 54.95 | 55.0781 | 55.0232 | 8.4732 | 67.955 | -54.6387 | 68.28 | 123.3444 | -0.22888 | 76.7258 | 0.10529 | 0.32501 | 123.2025 | 123.3307 | 122.9416 | 68.5318 | 68.28 | 123.2758 | 123.1247 | 76.7258 | 68.5318 | 68.28 | 123.1247 | 122.9416 | 123.2758 | -55.2155 | -46.4447
5501.7656 | 123.3627 | -68.2251 | 54.895 | 0.0035856 | -0.0090704 | -0.025015 | 0.005411 | -0.0073999 | -0.0050095 | -0.0041528 | 0.064087 | 0.2243 | -0.32044 | 55.0919 | 54.6707 | 54.8767 | 54.9271 | 55.069 | 55.014 | 8.4778 | 67.9047 | -54.6707 | 68.2892 | 123.317 | -0.22431 | 76.7029 | 0.11902 | 0.38452 | 123.1522 | 123.2941 | 122.8958 | 68.4494 | 68.2892 | 123.2391 | 123.1018 | 76.7029 | 68.4494 | 68.2892 | 123.1018 | 122.8958 | 123.2391 | -55.2155 | -46.4172
5502.7656 | 123.3673 | -68.2526 | 54.9133 | -0.065079 | -0.012702 | -0.026938 | 0.0058382 | -0.0052637 | -0.0071457 | -0.0026574 | -0.086975 | 0.25635 | -0.21515 | 55.1056 | 54.7028 | 54.9042 | 54.9133 | 55.0735 | 55.0323 | 8.4778 | 68.0374 | -54.657 | 68.1656 | 123.3582 | -0.21057 | 76.7303 | 0.11902 | 0.12817 | 123.1659 | 123.3261 | 122.9553 | 68.5089 | 68.1656 | 123.2849 | 123.1567 | 76.7303 | 68.5089 | 68.1656 | 123.1567 | 122.9553 | 123.2849 | -55.1285 | -46.4355
5503.7812 | 123.349 | -68.2755 | 54.9133 | -0.15663 | -0.010993 | -0.027152 | 0.0062656 | -0.0097497 | -0.0065047 | -0.0041528 | 0.027466 | 0.27924 | -0.28381 | 55.0735 | 54.6707 | 54.8447 | 54.9866 | 55.069 | 55.0186 | 8.4732 | 67.9916 | -54.6341 | 68.3029 | 123.349 | -0.24262 | 76.7487 | 0.10529 | 0.31128 | 123.262 | 123.3444 | 122.9462 | 68.5547 | 68.3029 | 123.2941 | 123.1201 | 76.7487 | 68.5547 | 68.3029 | 123.1201 | 122.9462 | 123.2941 | -55.1971 | -46.4401
5504.7812 | 123.3078 | -68.2755 | 54.9316 | -2.1632 | -0.0071478 | -0.024802 | 0.00028404 | -0.0071863 | -0.0052231 | -0.0032984 | 0.064087 | 0.32044 | -0.25177 | 55.0735 | 54.6524 | 54.8218 | 55.014 | 55.0461 | 55.0735 | 8.4778 | 68.0237 | -54.6112 | 68.3395 | 123.349 | -0.27924 | 76.7532 | 0.14191 | 0.31586 | 123.2895 | 123.3215 | 122.9279 | 68.5959 | 68.3395 | 123.349 | 123.0972 | 76.7532 | 68.5959 | 68.3395 | 123.0972 | 122.9279 | 123.349 | -55.1834 | -46.4539
5505.7656 | 123.2529 | -68.28 | 54.9774 | -0.2253 | -0.011848 | -0.026938 | 0.0011386 | -0.011886 | -0.0071457 | -0.0026574 | 0.022888 | 0.23804 | -0.29297 | 55.069 | 54.6799 | 54.8447 | 54.9774 | 55.0735 | 55.0186 | 8.4824 | 67.9871 | -54.7394 | 68.3029 | 123.349 | -0.29755 | 76.7624 | 0.041199 | 0.31586 | 123.2574 | 123.3536 | 122.9599 | 68.5181 | 68.3029 | 123.2986 | 123.1247 | 76.7624 | 68.5181 | 68.3029 | 123.1247 | 122.9599 | 123.2986 | -55.2704 | -46.4951
5506.7812 | 123.3307 | -68.2709 | 54.9133 | -2.0182 | -0.010139 | -0.027152 | 0.0015658 | -0.0097497 | -0.0056503 | -0.0026574 | 0.027466 | 0.32044 | -0.22888 | 55.0735 | 54.6341 | 54.8218 | 55.0003 | 55.0552 | 55.0415 | 8.4778 | 68.042 | -54.5929 | 68.2983 | 123.3444 | -0.27924 | 76.7487 | 0.12817 | 0.25635 | 123.2712 | 123.3261 | 122.905 | 68.5913 | 68.2983 | 123.3124 | 123.0927 | 76.7487 | 68.5913 | 68.2983 | 123.0927 | 122.905 | 123.3124 | -55.1422 | -46.4355
5507.7812 | 123.3856 | -68.2388 | 54.9774 | -0.16426 | -0.012702 | -0.024588 | 0.0024202 | -0.011245 | -0.0060775 | -0.0020166 | 0.059509 | 0.23804 | -0.29755 | 55.0461 | 54.689 | 54.8813 | 54.9591 | 55.0644 | 55.0323 | 8.4869 | 67.9413 | -54.7394 | 68.2983 | 123.2849 | -0.28839 | 76.7258 | 0.054932 | 0.35705 | 123.1979 | 123.3032 | 122.9279 | 68.4769 | 68.2983 | 123.2712 | 123.1201 | 76.7258 | 68.4769 | 68.2983 | 123.1201 | 122.9279 | 123.2712 | -55.275 | -46.4905
5508.7656 | 123.3307 | -68.2343 | 54.9179 | -0.18715 | -0.011634 | -0.02822 | 0.003702 | -0.0093225 | -0.0084273 | -0.0024438 | 0.027466 | 0.28381 | -0.27466 | 55.0735 | 54.6478 | 54.8126 | 55.014 | 55.0552 | 55.0644 | 8.4869 | 67.9596 | -54.6341 | 68.2617 | 123.3078 | -0.27008 | 76.7212 | 0.14648 | 0.30212 | 123.2483 | 123.2895 | 122.8821 | 68.5181 | 68.2617 | 123.2986 | 123.0469 | 76.7212 | 68.5181 | 68.2617 | 123.0469 | 122.8821 | 123.2986 | -55.1926 | -46.431
5509.7656 | 123.3261 | -68.2526 | 54.9454 | 0.12566 | -0.009925 | -0.030783 | 0.0049838 | -0.0095361 | -0.0073593 | -0.0056482 | 0.009155 | 0.29297 | -0.26093 | 55.0735 | 54.6478 | 54.8264 | 55.0095 | 55.0461 | 55.0369 | 8.4778 | 67.9916 | -54.6524 | 68.2617 | 123.3261 | -0.29755 | 76.7303 | 0.091552 | 0.27008 | 123.262 | 123.2986 | 122.9004 | 68.5455 | 68.2617 | 123.2895 | 123.0789 | 76.7303 | 68.5455 | 68.2617 | 123.0789 | 122.9004 | 123.2895 | -55.2063 | -46.4676
5510.7812 | 123.381 | -68.2114 | 54.9179 | -0.19478 | -0.012488 | -0.024588 | 0.0024202 | -0.010391 | -0.0054367 | -0.0030848 | 0.059509 | 0.22888 | -0.2655 | 55.1331 | 54.7119 | 54.8859 | 54.9362 | 55.1147 | 55.0232 | 8.4824 | 67.9459 | -54.689 | 68.2709 | 123.3444 | -0.20599 | 76.6937 | 0.10529 | 0.32501 | 123.1476 | 123.3261 | 122.9233 | 68.4402 | 68.2709 | 123.2346 | 123.0972 | 76.6937 | 68.4402 | 68.2709 | 123.0972 | 122.9233 | 123.2346 | -55.1834 | -46.4355
5511.7812 | 123.3994 | -68.2434 | 54.8859 | 0.1638 | -0.014625 | -0.024588 | 0.001993 | -0.0099633 | -0.0073593 | -0.0037256 | -0.004578 | 0.13733 | -0.3479 | 55.0919 | 54.6661 | 54.8492 | 54.8126 | 55.0827 | 54.9957 | 8.4824 | 67.8955 | -54.7485 | 68.2388 | 123.3353 | -0.21973 | 76.7258 | 0.10986 | 0.34332 | 123.056 | 123.3261 | 122.9095 | 68.3807 | 68.2388 | 123.2391 | 123.0927 | 76.7258 | 68.3807 | 68.2388 | 123.0927 | 122.9095 | 123.2391 | -55.2338 | -46.4035
5512.7812 | 123.436 | -68.2205 | 54.9088 | -0.19478 | -0.012275 | -0.026724 | -0.00014316 | -0.012527 | -0.01035 | -0.001803 | 0.082397 | 0.20142 | -0.27924 | 55.1743 | 54.9179 | 54.9408 | 54.8401 | 55.1651 | 54.9866 | 8.4915 | 67.9413 | -54.7073 | 68.3029 | 123.3948 | 0.009156 | 76.712 | 0.07782 | 0.36163 | 123.0606 | 123.3856 | 123.1384 | 68.4219 | 68.3029 | 123.2071 | 123.1613 | 76.712 | 68.4219 | 68.3029 | 123.1613 | 123.1384 | 123.2071 | -55.188 | -46.4172
5513.7812 | 123.4268 | -68.2159 | 54.8904 | -0.2253 | -0.01377 | -0.030783 | 0.0032748 | -0.010818 | -0.0090683 | -0.0028712 | 0.068665 | 0.20599 | -0.28839 | 55.1651 | 54.95 | 54.9408 | 54.8401 | 55.1605 | 54.9957 | 8.4824 | 67.9276 | -54.6844 | 68.2846 | 123.381 | 0.059509 | 76.6983 | 0.10529 | 0.35706 | 123.056 | 123.3765 | 123.1659 | 68.4219 | 68.2846 | 123.2117 | 123.1567 | 76.6983 | 68.4219 | 68.2846 | 123.1567 | 123.1659 | 123.2117 | -55.1788 | -46.4081
5514.7812 | 123.436 | -68.2022 | 54.9088 | -0.095596 | -0.015479 | -0.022879 | 0.004343 | -0.012527 | -0.0094955 | -0.00094839 | -0.054932 | 0.19684 | -0.27466 | 55.1971 | 54.7256 | 54.9088 | 54.7989 | 55.1514 | 54.982 | 8.4869 | 67.9276 | -54.7119 | 68.1473 | 123.3994 | -0.1831 | 76.6891 | 0.073243 | 0.21973 | 123.0011 | 123.3536 | 122.9279 | 68.399 | 68.1473 | 123.1842 | 123.111 | 76.6891 | 68.399 | 68.1473 | 123.111 | 122.9279 | 123.1842 | -55.1834 | -46.4218
5515.7656 | 123.4131 | -68.2388 | 54.895 | -0.15663 | -0.013129 | -0.029501 | 0.0028476 | -0.0099633 | -0.0071457 | -0.005221 | 0.086975 | 0.19684 | -0.2655 | 55.1697 | 54.7485 | 54.9088 | 54.8813 | 55.1422 | 55.0186 | 8.4869 | 67.9733 | -54.6982 | 68.3258 | 123.4085 | -0.14649 | 76.7258 | 0.1236 | 0.35248 | 123.1201 | 123.381 | 122.9874 | 68.4357 | 68.3258 | 123.2574 | 123.1476 | 76.7258 | 68.4357 | 68.3258 | 123.1476 | 122.9874 | 123.2574 | -55.1605 | -46.4081
5516.7656 | 123.4268 | -68.2388 | 54.9225 | -0.16426 | -0.010993 | -0.026724 | 0.0032748 | -0.011459 | -0.0082137 | -0.0037256 | 0.091553 | 0.21057 | -0.30212 | 55.1743 | 54.7623 | 54.9316 | 54.8447 | 55.1697 | 54.9911 | 8.4869 | 67.9367 | -54.7119 | 68.3304 | 123.4131 | -0.16022 | 76.7258 | 0.068665 | 0.39368 | 123.0835 | 123.4085 | 123.0011 | 68.4494 | 68.3304 | 123.23 | 123.1705 | 76.7258 | 68.4494 | 68.3304 | 123.1705 | 123.0011 | 123.23 | -55.2246 | -46.4355
5517.7812 | 123.4268 | -68.2159 | 54.8676 | -0.04219 | -0.013557 | -0.03057 | 0.00071144 | -0.011672 | -0.0071457 | -0.0037256 | 0.022888 | 0.17395 | -0.3067 | 55.1376 | 54.7256 | 54.9133 | 54.8035 | 55.1376 | 54.982 | 8.4824 | 67.9092 | -54.6936 | 68.2388 | 123.3536 | -0.14191 | 76.6983 | 0.11444 | 0.32959 | 123.0194 | 123.3536 | 122.9416 | 68.3899 | 68.2388 | 123.1979 | 123.1293 | 76.6983 | 68.3899 | 68.2388 | 123.1293 | 122.9416 | 123.1979 | -55.1743 | -46.3852
5518.7812 | 123.4177 | -68.2251 | 54.8859 | 0.0035856 | -0.011634 | -0.02822 | 0.0013522 | -0.011886 | -0.0060775 | -0.001803 | 0 | 0.16479 | -0.32959 | 55.1514 | 54.7165 | 54.8904 | 54.8126 | 55.1147 | 54.9728 | 8.4869 | 67.8955 | -54.7211 | 68.2251 | 123.3765 | -0.16937 | 76.712 | 0.086975 | 0.32959 | 123.0377 | 123.3398 | 122.9416 | 68.3899 | 68.2251 | 123.1979 | 123.1155 | 76.712 | 68.3899 | 68.2251 | 123.1155 | 122.9416 | 123.1979 | -55.2155 | -46.3989
5519.7812 | 123.3398 | -68.2434 | 54.9362 | -0.16426 | -0.0094976 | -0.027365 | 0.0077608 | -0.011672 | -0.0077865 | -0.003512 | 0.059509 | 0.27924 | -0.28839 | 55.1239 | 54.6478 | 54.8126 | 54.9866 | 55.0461 | 55.0369 | 8.4869 | 67.955 | -54.657 | 68.3029 | 123.3673 | -0.28839 | 76.7303 | 0.10071 | 0.3479 | 123.23 | 123.2895 | 122.8912 | 68.5226 | 68.3029 | 123.2803 | 123.056 | 76.7303 | 68.5226 | 68.3029 | 123.056 | 122.8912 | 123.2803 | -55.2246 | -46.4493
5520.7812 | 123.4222 | -68.2343 | 54.8859 | 0.034104 | -0.01377 | -0.026297 | -0.00014316 | -0.010604 | -0.0071457 | -0.001803 | 0.004578 | 0.19684 | -0.31586 | 55.1376 | 54.7348 | 54.8996 | 54.8126 | 55.0964 | 54.9774 | 8.4869 | 67.9184 | -54.689 | 68.2388 | 123.3719 | -0.15106 | 76.7212 | 0.091553 | 0.32044 | 123.0469 | 123.3307 | 122.9691 | 68.4311 | 68.2388 | 123.2117 | 123.1338 | 76.7212 | 68.4311 | 68.2388 | 123.1338 | 122.9691 | 123.2117 | -55.2017 | -46.3989
5521.7812 | 123.4222 | -68.2159 | 54.8996 | 0.072251 | -0.01142 | -0.025229 | 0.0030612 | -0.010818 | -0.0075729 | -0.00030759 | -0.009155 | 0.1831 | -0.32044 | 55.1102 | 54.7165 | 54.8676 | 54.8172 | 55.0964 | 54.9866 | 8.4824 | 67.8955 | -54.7165 | 68.2068 | 123.3261 | -0.1831 | 76.6983 | 0.086975 | 0.31128 | 123.0331 | 123.3124 | 122.9324 | 68.399 | 68.2068 | 123.2025 | 123.0835 | 76.6983 | 68.399 | 68.2068 | 123.0835 | 122.9324 | 123.2025 | -55.22 | -46.4172
5522.7656 | 123.4268 | -68.2251 | 54.8996 | 0.0035856 | -0.01142 | -0.027579 | -0.001425 | -0.011672 | -0.0073593 | -0.0013758 | 0.036621 | 0.17395 | -0.29297 | 55.1651 | 54.7623 | 54.9271 | 54.7897 | 55.1468 | 54.9774 | 8.4869 | 67.9321 | -54.7256 | 68.2617 | 123.3902 | -0.13733 | 76.712 | 0.07782 | 0.32959 | 123.0148 | 123.3719 | 122.9874 | 68.399 | 68.2617 | 123.2025 | 123.1522 | 76.712 | 68.399 | 68.2617 | 123.1522 | 122.9874 | 123.2025 | -55.1926 | -46.4127
5523.7656 | 123.4131 | -68.2297 | 54.895 | 0.011215 | -0.012488 | -0.025229 | 0.0024202 | -0.01274 | -0.0058639 | -0.0043664 | 0.036621 | 0.16479 | -0.31128 | 55.1559 | 54.7485 | 54.9179 | 54.8035 | 55.1147 | 54.9454 | 8.4824 | 67.9184 | -54.7302 | 68.2663 | 123.3856 | -0.14649 | 76.712 | 0.050354 | 0.3479 | 123.0331 | 123.3444 | 122.9782 | 68.3945 | 68.2663 | 123.175 | 123.1476 | 76.712 | 68.3945 | 68.2663 | 123.1476 | 122.9782 | 123.175 | -55.2063 | -46.4127
5524.7812 | 123.3398 | -68.2663 | 54.9133 | 0.056992 | -0.0077888 | -0.028433 | 0.010965 | -0.010177 | -0.0082137 | -0.0043664 | 0.07782 | 0.2243 | -0.31586 | 55.1193 | 54.8355 | 54.8447 | 54.8996 | 55.014 | 54.9911 | 8.4824 | 67.9504 | -54.689 | 68.3441 | 123.3856 | -0.07782 | 76.7487 | 0.07782 | 0.39368 | 123.1659 | 123.2803 | 123.1018 | 68.4906 | 68.3441 | 123.2574 | 123.111 | 76.7487 | 68.4906 | 68.3441 | 123.111 | 123.1018 | 123.2574 | -55.2292 | -46.431
5525.7812 | 123.3994 | -68.2617 | 54.863 | 0.21721 | -0.010993 | -0.029715 | 0.0017794 | -0.010818 | -0.0045821 | -0.0030848 | -0.013733 | 0.11444 | -0.37079 | 55.1193 | 54.9133 | 54.8676 | 54.7897 | 55.0507 | 54.9316 | 8.4778 | 67.8909 | -54.7485 | 68.248 | 123.381 | 0.050354 | 76.7395 | 0.068665 | 0.35706 | 123.0515 | 123.3124 | 123.175 | 68.3762 | 68.248 | 123.1934 | 123.1293 | 76.7395 | 68.3762 | 68.248 | 123.1293 | 123.175 | 123.1934 | -55.2338 | -46.3852
5526.7812 | 123.5046 | -68.2251 | 54.8813 | 0.1638 | -0.011634 | -0.026724 | 0.00049764 | -0.01274 | -0.0054367 | -0.0022302 | -0.036621 | 0.14648 | -0.34332 | 55.1102 | 54.8904 | 54.863 | 54.8172 | 55.0598 | 54.9271 | 8.4824 | 67.8818 | -54.7348 | 68.1885 | 123.3353 | 0.009155 | 76.7075 | 0.045776 | 0.3067 | 123.0423 | 123.2849 | 123.1155 | 68.3716 | 68.1885 | 123.1522 | 123.0881 | 76.7075 | 68.3716 | 68.1885 | 123.0881 | 123.1155 | 123.1522 | -55.2246 | -46.3989
5527.7812 | 123.4039 | -68.2434 | 54.8721 | 0.21721 | -0.012916 | -0.026297 | 0.0022066 | -0.012954 | -0.0067185 | -0.0024438 | -0.036621 | 0.10986 | -0.37079 | 55.1193 | 54.6936 | 54.8584 | 54.7989 | 55.0552 | 54.9271 | 8.4824 | 67.8726 | -54.7623 | 68.2068 | 123.3627 | -0.17853 | 76.7258 | 0.054932 | 0.33417 | 123.0423 | 123.2986 | 122.937 | 68.3533 | 68.2068 | 123.1705 | 123.1018 | 76.7258 | 68.3533 | 68.2068 | 123.1018 | 122.937 | 123.1705 | -55.2429 | -46.3898
5528.7812 | 123.3994 | -68.2571 | 54.8676 | 0.17906 | -0.01142 | -0.023093 | 0.0047702 | -0.011245 | -0.0047957 | -0.0030848 | -0.018311 | 0.10986 | -0.37079 | 55.1376 | 54.7073 | 54.8859 | 54.7577 | 55.0735 | 54.9179 | 8.4824 | 67.8864 | -54.7577 | 68.2388 | 123.3948 | -0.16022 | 76.7395 | 0.050354 | 0.35248 | 123.0148 | 123.3307 | 122.9645 | 68.367 | 68.2388 | 123.175 | 123.143 | 76.7395 | 68.367 | 68.2388 | 123.143 | 122.9645 | 123.175 | -55.2383 | -46.3852
5529.7812 | 123.4589 | -68.2114 | 54.9042 | -0.04219 | -0.012916 | -0.029074 | 0.00049764 | -0.010604 | -0.0084273 | -0.0020166 | 0.045776 | 0.18768 | -0.28839 | 55.1926 | 54.776 | 54.9408 | 54.7943 | 55.1514 | 54.9728 | 8.4869 | 67.923 | -54.7165 | 68.2571 | 123.4039 | -0.12817 | 76.6983 | 0.068664 | 0.33417 | 123.0057 | 123.3627 | 122.9874 | 68.399 | 68.2571 | 123.1842 | 123.1522 | 76.6983 | 68.399 | 68.2571 | 123.1522 | 122.9874 | 123.1842 | -55.1926 | -46.4172
5530.7656 | 123.3902 | -68.2388 | 54.895 | 0.17143 | -0.010352 | -0.029501 | 0.0013522 | -0.0091089 | -0.0062911 | -0.0043664 | -0.009155 | 0.13275 | -0.33875 | 55.1102 | 54.6707 | 54.8721 | 54.808 | 55.069 | 54.9454 | 8.4778 | 67.9001 | -54.7623 | 68.2297 | 123.349 | -0.22431 | 76.7166 | 0.050354 | 0.32959 | 123.0469 | 123.3078 | 122.9095 | 68.3716 | 68.2297 | 123.1842 | 123.111 | 76.7166 | 68.3716 | 68.2297 | 123.111 | 122.9095 | 123.1842 | -55.2338 | -46.4172
5531.7812 | 123.436 | -68.2343 | 54.8538 | 0.59868 | -0.01142 | -0.026938 | 0.0049838 | -0.0088953 | -0.0073593 | -0.0037256 | 0.068665 | 0.09613 | -0.37994 | 55.1559 | 54.7165 | 54.9316 | 54.7394 | 55.0827 | 54.9408 | 8.4869 | 67.8543 | -54.7577 | 68.3029 | 123.3902 | -0.13733 | 76.7212 | 0.086975 | 0.44861 | 122.9736 | 123.317 | 122.9507 | 68.3304 | 68.3029 | 123.175 | 123.1659 | 76.7212 | 68.3304 | 68.3029 | 123.1659 | 122.9507 | 123.175 | -55.2338 | -46.3669
5532.7812 | 123.4451 | -68.2388 | 54.8492 | 0.32402 | -0.009925 | -0.028006 | 0.0077608 | -0.010391 | -0.0037277 | -0.0026574 | 0.004578 | 0.14191 | -0.37079 | 54.9637 | 54.7485 | 54.9591 | 54.863 | 55.0781 | 54.9316 | 8.4915 | 67.868 | -54.7073 | 68.2434 | 123.2025 | -0.10071 | 76.7303 | 0.082398 | 0.37537 | 123.1018 | 123.317 | 122.9874 | 68.3807 | 68.2434 | 123.1705 | 123.1979 | 76.7303 | 68.3807 | 68.2434 | 123.1979 | 122.9874 | 123.1705 | -55.22 | -46.3577
5533.7812 | 123.436 | -68.2388 | 54.8721 | 0.31639 | -0.010779 | -0.026511 | 0.008829 | -0.0095361 | -0.0069321 | -0.0024438 | 0.041199 | 0.1236 | -0.35248 | 55.1559 | 54.7348 | 54.9133 | 54.744 | 55.0873 | 54.9088 | 8.4869 | 67.8864 | -54.7485 | 68.28 | 123.3948 | -0.13733 | 76.7258 | 0.036621 | 0.39368 | 122.9828 | 123.3261 | 122.9736 | 68.3624 | 68.28 | 123.1476 | 123.1522 | 76.7258 | 68.3624 | 68.28 | 123.1522 | 122.9736 | 123.1476 | -55.2246 | -46.3852
5534.7812 | 123.4177 | -68.2663 | 54.8859 | 0.63683 | -0.010566 | -0.023734 | 0.0030612 | -0.011672 | -0.0056503 | -0.0011622 | 0.027466 | 0.16479 | -0.28381 | 55.0873 | 54.8355 | 54.8767 | 54.8401 | 55.0644 | 54.9316 | 8.4869 | 67.9825 | -54.7211 | 68.2938 | 123.3536 | -0.050354 | 76.7532 | 0.045777 | 0.31128 | 123.1064 | 123.3307 | 123.1018 | 68.4311 | 68.2938 | 123.1979 | 123.143 | 76.7532 | 68.4311 | 68.2938 | 123.143 | 123.1018 | 123.1979 | -55.1697 | -46.3989
5535.7656 | 123.436 | -68.2388 | 54.8721 | 0.2401 | -0.0097114 | -0.026511 | 0.003702 | -0.010177 | -0.0045821 | -0.003512 | 0.013733 | 0.1236 | -0.3479 | 55.1147 | 54.895 | 54.8996 | 54.7485 | 55.0873 | 54.9042 | 8.4869 | 67.8909 | -54.7485 | 68.2526 | 123.3536 | 0.022889 | 76.7258 | 0.032044 | 0.36163 | 122.9874 | 123.3261 | 123.1339 | 68.3624 | 68.2526 | 123.143 | 123.1384 | 76.7258 | 68.3624 | 68.2526 | 123.1384 | 123.1339 | 123.143 | -55.22 | -46.3852
5536.7656 | 123.4451 | -68.2571 | 54.8767 | 0.25536 | -0.0097114 | -0.022665 | 0.0075472 | -0.011459 | -0.0071457 | -0.0037256 | 0.018311 | 0.14191 | -0.3479 | 55.1468 | 54.9088 | 54.9271 | 54.7348 | 55.0827 | 54.9088 | 8.4869 | 67.9092 | -54.7348 | 68.2755 | 123.4039 | 0.032043 | 76.7441 | 0.032043 | 0.36621 | 122.9919 | 123.3398 | 123.1659 | 68.399 | 68.2755 | 123.1659 | 123.1842 | 76.7441 | 68.399 | 68.2755 | 123.1842 | 123.1659 | 123.1659 | -55.2246 | -46.3898
5537.7656 | 123.4406 | -68.2343 | 54.8492 | -0.026932 | -0.0086432 | -0.023093 | 0.0066928 | -0.010391 | -0.0073593 | -0.003512 | 0.022888 | 0.11444 | -0.35248 | 55.1605 | 54.8904 | 54.9133 | 54.7348 | 55.0827 | 54.9271 | 8.4778 | 67.8818 | -54.7348 | 68.2571 | 123.3948 | 0.041199 | 76.712 | 0.07782 | 0.37537 | 122.9691 | 123.317 | 123.1247 | 68.3487 | 68.2571 | 123.1613 | 123.1476 | 76.712 | 68.3487 | 68.2571 | 123.1476 | 123.1247 | 123.1613 | -55.2017 | -46.3715
5538.7812 | 123.3353 | -68.2663 | 54.9133 | 0.24773 | -0.0067206 | -0.022879 | 0.008829 | -0.0080407 | -0.0045821 | -0.0039392 | -0.036621 | 0.19684 | -0.37537 | 55.0507 | 54.8126 | 54.7989 | 54.895 | 54.9637 | 54.9591 | 8.4778 | 67.8909 | -54.7165 | 68.2297 | 123.317 | -0.10071 | 76.7441 | 0.045776 | 0.33874 | 123.1613 | 123.23 | 123.0789 | 68.4631 | 68.2297 | 123.2254 | 123.0652 | 76.7441 | 68.4631 | 68.2297 | 123.0652 | 123.0789 | 123.2254 | -55.2887 | -46.4355
5539.7812 | 123.3124 | -68.28 | 54.8904 | 0.14854 | -0.0080024 | -0.03057 | 0.0096834 | -0.0095361 | -0.0069321 | -0.0024438 | -0.050354 | 0.21515 | -0.37079 | 55.0598 | 54.8355 | 54.7989 | 54.9179 | 54.9728 | 54.9591 | 8.4778 | 67.9092 | -54.6753 | 68.2297 | 123.3398 | -0.054932 | 76.7578 | 0.068664 | 0.32043 | 123.1979 | 123.2529 | 123.1155 | 68.4952 | 68.2297 | 123.2391 | 123.0789 | 76.7578 | 68.4952 | 68.2297 | 123.0789 | 123.1155 | 123.2391 | -55.2612 | -46.4127
5540.7812 | 123.3444 | -68.2663 | 54.9133 | 0.23247 | -0.0084296 | -0.023947 | 0.0066928 | -0.0088953 | -0.0041549 | -0.00073479 | -0.054932 | 0.20599 | -0.37079 | 55.0369 | 54.8355 | 54.8218 | 54.8904 | 54.9774 | 54.9591 | 8.4869 | 67.8955 | -54.7073 | 68.2114 | 123.3032 | -0.07782 | 76.7532 | 0.045776 | 0.31586 | 123.1567 | 123.2437 | 123.1018 | 68.4723 | 68.2114 | 123.2254 | 123.0881 | 76.7532 | 68.4723 | 68.2114 | 123.0881 | 123.1018 | 123.2254 | -55.2841 | -46.4264
5541.7812 | 123.3261 | -68.28 | 54.9042 | 0.26299 | -0.0062934 | -0.020956 | 0.0084018 | -0.0082545 | -0.0062911 | -0.0032984 | -0.054932 | 0.21515 | -0.35706 | 55.0323 | 54.6295 | 54.8035 | 54.9133 | 54.9774 | 54.9728 | 8.4915 | 67.923 | -54.689 | 68.2251 | 123.3124 | -0.27466 | 76.7715 | 0.068664 | 0.30212 | 123.1934 | 123.2574 | 122.9095 | 68.4952 | 68.2251 | 123.2529 | 123.0835 | 76.7715 | 68.4952 | 68.2251 | 123.0835 | 122.9095 | 123.2529 | -55.2612 | -46.4127
5542.7656 | 123.3994 | -68.28 | 54.8721 | 0.2401 | -0.0069342 | -0.027579 | 0.0073336 | -0.010604 | -0.0054367 | -0.0022302 | -0.054932 | 0.21515 | -0.36621 | 55.0827 | 54.6753 | 54.8584 | 54.8126 | 55.0186 | 54.9362 | 8.4824 | 67.9138 | -54.657 | 68.2251 | 123.3627 | -0.19684 | 76.7624 | 0.064087 | 0.31128 | 123.0927 | 123.2986 | 122.9553 | 68.4952 | 68.2251 | 123.2162 | 123.1384 | 76.7624 | 68.4952 | 68.2251 | 123.1384 | 122.9553 | 123.2162 | -55.2383 | -46.3898
5543.7812 | 123.3307 | -68.2846 | 54.9088 | 0.17906 | -0.0084296 | -0.027792 | 0.0069064 | -0.0073999 | -0.0054367 | 0.00011961 | -0.045776 | 0.21973 | -0.37537 | 55.0415 | 54.6387 | 54.808 | 54.9133 | 54.9637 | 54.9683 | 8.4778 | 67.9092 | -54.689 | 68.2388 | 123.3261 | -0.27008 | 76.7624 | 0.05951 | 0.32959 | 123.1979 | 123.2483 | 122.9233 | 68.5043 | 68.2388 | 123.2529 | 123.0927 | 76.7624 | 68.5043 | 68.2388 | 123.0927 | 122.9233 | 123.2529 | -55.2841 | -46.431
5544.7812 | 123.3261 | -68.3029 | 54.895 | -0.18715 | -0.008216 | -0.022025 | 0.0051974 | -0.0095361 | -0.0043685 | -0.0028712 | 0.027466 | 0.1831 | -0.36621 | 55.0323 | 54.6112 | 54.7943 | 54.9179 | 54.9683 | 54.9454 | 8.4824 | 67.9367 | -54.7119 | 68.3304 | 123.3353 | -0.28381 | 76.7853 | 0.050354 | 0.39368 | 123.2208 | 123.2712 | 122.9141 | 68.486 | 68.3304 | 123.2483 | 123.0972 | 76.7853 | 68.486 | 68.3304 | 123.0972 | 122.9141 | 123.2483 | -55.2612 | -46.4127
5545.7656 | 123.3582 | -68.2434 | 54.9179 | -0.072708 | -0.0086432 | -0.023093 | 0.0064792 | -0.0073999 | -0.0071457 | -0.0026574 | 0.050354 | 0.25177 | -0.28839 | 55.1056 | 54.7028 | 54.863 | 54.9316 | 55.0415 | 54.9866 | 8.4778 | 67.955 | -54.6661 | 68.2938 | 123.349 | -0.21515 | 76.7212 | 0.068664 | 0.33875 | 123.175 | 123.2849 | 122.9462 | 68.4952 | 68.2938 | 123.23 | 123.1064 | 76.7212 | 68.4952 | 68.2938 | 123.1064 | 122.9462 | 123.23 | -55.2063 | -46.4401
5546.7812 | 123.3536 | -68.28 | 54.9088 | -0.011673 | -0.0088568 | -0.023093 | 0.0075472 | -0.0073999 | -0.0065047 | -0.0026574 | 0.032043 | 0.23346 | -0.32959 | 55.069 | 54.6799 | 54.8538 | 54.9408 | 55.0369 | 54.982 | 8.4732 | 67.9504 | -54.6753 | 68.3121 | 123.349 | -0.22888 | 76.7532 | 0.073243 | 0.36163 | 123.2208 | 123.317 | 122.9599 | 68.5135 | 68.3121 | 123.262 | 123.1338 | 76.7532 | 68.5135 | 68.3121 | 123.1338 | 122.9599 | 123.262 | -55.2383 | -46.4355
5547.7812 | 123.3261 | -68.2663 | 54.8996 | 0.049362 | -0.0077888 | -0.022238 | 0.0069064 | -0.0071863 | -0.0067185 | -0.0032984 | 0.009155 | 0.21973 | -0.33417 | 55.0552 | 54.6524 | 54.8355 | 54.9408 | 55.0049 | 54.9774 | 8.4778 | 67.9321 | -54.6799 | 68.2755 | 123.3215 | -0.24719 | 76.7441 | 0.07782 | 0.34332 | 123.2071 | 123.2712 | 122.9187 | 68.486 | 68.2755 | 123.2437 | 123.1018 | 76.7441 | 68.486 | 68.2755 | 123.1018 | 122.9187 | 123.2437 | -55.2338 | -46.4218
5548.7812 | 123.3444 | -68.2755 | 54.9179 | 0.026474 | -0.0086432 | -0.029715 | 0.0081882 | -0.0065455 | -0.0067185 | -0.0011622 | 0.018311 | 0.24261 | -0.3067 | 55.0781 | 54.657 | 54.8492 | 54.9316 | 55.0232 | 54.9774 | 8.4824 | 67.9688 | -54.6753 | 68.2938 | 123.3536 | -0.26093 | 76.7578 | 0.059509 | 0.32501 | 123.2071 | 123.2986 | 122.9324 | 68.5181 | 68.2938 | 123.2529 | 123.1247 | 76.7578 | 68.5181 | 68.2938 | 123.1247 | 122.9324 | 123.2529 | -55.2246 | -46.4355
5549.7656 | 123.3032 | -68.2938 | 54.8996 | 0.11803 | -0.009925 | -0.029288 | 0.0060518 | -0.0076135 | -0.0052231 | -0.0022302 | -0.022888 | 0.23346 | -0.35248 | 55.0232 | 54.6066 | 54.808 | 54.95 | 54.9728 | 54.9911 | 8.4869 | 67.9413 | -54.6661 | 68.2709 | 123.317 | -0.29297 | 76.7807 | 0.091553 | 0.32959 | 123.2437 | 123.2666 | 122.9004 | 68.5272 | 68.2709 | 123.2849 | 123.1018 | 76.7807 | 68.5272 | 68.2709 | 123.1018 | 122.9004 | 123.2849 | -55.2521 | -46.4127
5550.7656 | 123.317 | -68.2617 | 54.9133 | 0.087509 | -0.0086432 | -0.021811 | 0.00712 | -0.0076135 | -0.0067185 | -0.0032984 | -0.009155 | 0.23346 | -0.34332 | 55.0461 | 54.7989 | 54.8309 | 54.9225 | 55.0049 | 55.0095 | 8.4869 | 67.9184 | -54.6799 | 68.2526 | 123.3078 | -0.11444 | 76.7487 | 0.09613 | 0.33417 | 123.1842 | 123.2666 | 123.0606 | 68.4952 | 68.2526 | 123.2712 | 123.0927 | 76.7487 | 68.4952 | 68.2526 | 123.0927 | 123.0606 | 123.2712 | -55.2567 | -46.4264
5551.7812 | 123.3673 | -68.2663 | 54.8996 | 0.034104 | -0.0088568 | -0.02352 | 0.00712 | -0.0076135 | -0.0062911 | 0.00054681 | 0.036621 | 0.23346 | -0.32044 | 55.0919 | 54.8721 | 54.8676 | 54.9271 | 55.0507 | 54.9911 | 8.4778 | 67.9459 | -54.6661 | 68.3029 | 123.3582 | -0.027466 | 76.7441 | 0.091553 | 0.35706 | 123.1934 | 123.317 | 123.1384 | 68.4998 | 68.3029 | 123.2574 | 123.1338 | 76.7441 | 68.4998 | 68.3029 | 123.1338 | 123.1384 | 123.2574 | -55.22 | -46.4218
5552.7812 | 123.3719 | -68.2434 | 54.9362 | -0.10323 | -0.008216 | -0.022879 | 0.0041292 | -0.0069727 | -0.0073593 | -0.001803 | 0.027466 | 0.29755 | -0.30212 | 55.0873 | 54.8859 | 54.8721 | 54.9683 | 55.0644 | 55.0278 | 8.4732 | 67.9413 | -54.6387 | 68.2709 | 123.3307 | -0.050354 | 76.7166 | 0.091553 | 0.32959 | 123.2117 | 123.3078 | 123.1293 | 68.541 | 68.2709 | 123.2712 | 123.1155 | 76.7166 | 68.541 | 68.2709 | 123.1155 | 123.1293 | 123.2712 | -55.2383 | -46.463
5553.7812 | 123.349 | -68.2709 | 54.9637 | -0.16426 | -0.010779 | -0.025015 | 0.0039156 | -0.0082545 | -0.0056503 | -0.001803 | 0.032043 | 0.27924 | -0.30212 | 55.0735 | 54.8767 | 54.8584 | 54.9957 | 55.0552 | 55.014 | 8.4778 | 67.9688 | -54.6844 | 68.3029 | 123.3444 | -0.086975 | 76.7487 | 0.050354 | 0.33417 | 123.2666 | 123.3261 | 123.1476 | 68.5501 | 68.3029 | 123.2849 | 123.1293 | 76.7487 | 68.5501 | 68.3029 | 123.1293 | 123.1476 | 123.2849 | -55.2658 | -46.4859
5554.7812 | 123.3673 | -68.2571 | 54.9042 | -0.15663 | -0.0088568 | -0.027152 | 0.0051974 | -0.0073999 | -0.0082137 | -0.0028712 | 0.022888 | 0.28381 | -0.27924 | 55.0827 | 54.8538 | 54.863 | 54.9683 | 55.069 | 55.0232 | 8.4778 | 67.9779 | -54.6204 | 68.28 | 123.3398 | -0.050354 | 76.7349 | 0.11902 | 0.30212 | 123.2254 | 123.3261 | 123.111 | 68.541 | 68.28 | 123.2803 | 123.1201 | 76.7349 | 68.541 | 68.28 | 123.1201 | 123.111 | 123.2803 | -55.1834 | -46.4264
5555.7812 | 123.3444 | -68.248 | 54.9362 | -0.14137 | -0.010352 | -0.026083 | 0.0032748 | -0.010391 | -0.0086411 | -0.0030848 | 0.022888 | 0.28381 | -0.29297 | 55.0598 | 54.7989 | 54.8492 | 55.0278 | 55.0507 | 55.0278 | 8.4778 | 67.955 | -54.6524 | 68.2709 | 123.3078 | -0.13733 | 76.7258 | 0.091553 | 0.31586 | 123.2758 | 123.2986 | 123.0469 | 68.5318 | 68.2709 | 123.2758 | 123.0972 | 76.7258 | 68.5318 | 68.2709 | 123.0972 | 123.0469 | 123.2758 | -55.2292 | -46.4584
5556.7656 | 123.2346 | -68.2663 | 54.8538 | -0.10323 | -0.0090704 | -0.02587 | 0.0075472 | -0.0071863 | -0.0071457 | -0.003512 | 0.059509 | 0.24261 | -0.3067 | 55.1102 | 54.6936 | 54.8676 | 54.9271 | 55.0735 | 55.0003 | 8.4732 | 67.9596 | -54.6112 | 68.3258 | 123.3765 | -0.16022 | 76.7395 | 0.14648 | 0.36621 | 123.1934 | 123.3398 | 122.9599 | 68.5089 | 68.3258 | 123.2666 | 123.1338 | 76.7395 | 68.5089 | 68.3258 | 123.1338 | 122.9599 | 123.2666 | -55.1605 | -46.3806
5557.7656 | 123.3444 | -68.2571 | 54.9362 | -0.14137 | -0.009925 | -0.027365 | 0.0062656 | -0.0076135 | -0.0069321 | -0.0015894 | 0.032043 | 0.27008 | -0.29755 | 55.0919 | 54.6844 | 54.8767 | 54.9591 | 55.0827 | 55.0369 | 8.4824 | 67.9596 | -54.6661 | 68.2892 | 123.349 | -0.25177 | 76.7395 | 0.10071 | 0.32959 | 123.2162 | 123.3398 | 122.9416 | 68.5272 | 68.2892 | 123.2941 | 123.1338 | 76.7395 | 68.5272 | 68.2892 | 123.1338 | 122.9416 | 123.2941 | -55.2338 | -46.4539
5558.7812 | 123.3261 | -68.2892 | 54.9362 | -0.20241 | -0.0097114 | -0.020529 | 0.0039156 | -0.0088953 | -0.0073593 | -0.0026574 | 0.013733 | 0.27008 | -0.30212 | 55.0644 | 54.8447 | 54.8309 | 55.0003 | 55.0644 | 55.0232 | 8.4824 | 67.9871 | -54.6661 | 68.3029 | 123.3536 | -0.091552 | 76.7715 | 0.086975 | 0.31586 | 123.2895 | 123.3536 | 123.1339 | 68.5593 | 68.3029 | 123.3124 | 123.1201 | 76.7715 | 68.5593 | 68.3029 | 123.1201 | 123.1339 | 123.3124 | -55.2383 | -46.4539
5559.7812 | 123.3582 | -68.2434 | 54.9454 | -0.21004 | -0.011207 | -0.025015 | 0.00049764 | -0.0086817 | -0.0086411 | -0.0030848 | 0.059509 | 0.22888 | -0.27008 | 55.1056 | 54.8538 | 54.8859 | 54.9454 | 55.101 | 55.0369 | 8.4869 | 67.9733 | -54.7165 | 68.3029 | 123.349 | -0.091553 | 76.7303 | 0.091552 | 0.32959 | 123.1888 | 123.3444 | 123.0972 | 68.4723 | 68.3029 | 123.2803 | 123.1293 | 76.7303 | 68.4723 | 68.3029 | 123.1293 | 123.0972 | 123.2803 | -55.2155 | -46.4584
5560.7812 | 123.2895 | -68.2343 | 54.9637 | -0.19478 | -0.012061 | -0.030783 | 0.0024202 | -0.0080407 | -0.0073593 | -0.0043664 | 0.036621 | 0.24719 | -0.3067 | 55.0644 | 54.8218 | 54.8492 | 54.9774 | 55.0598 | 55.0461 | 8.4915 | 67.9276 | -54.7165 | 68.2709 | 123.2986 | -0.14191 | 76.7258 | 0.082398 | 0.34332 | 123.2117 | 123.2941 | 123.056 | 68.4814 | 68.2709 | 123.2803 | 123.0835 | 76.7258 | 68.4814 | 68.2709 | 123.0835 | 123.056 | 123.2803 | -55.2704 | -46.4722
5561.7812 | 123.3627 | -68.2343 | 54.9042 | -0.149 | -0.012916 | -0.027579 | 0.0011386 | -0.0121 | -0.0062911 | -0.0030848 | 0.068665 | 0.21973 | -0.28839 | 55.1147 | 54.8767 | 54.8813 | 54.9316 | 55.1102 | 55.0507 | 8.4915 | 67.9459 | -54.6844 | 68.3029 | 123.349 | -0.027466 | 76.7258 | 0.14648 | 0.35706 | 123.1659 | 123.3444 | 123.111 | 68.454 | 68.3029 | 123.2849 | 123.1155 | 76.7258 | 68.454 | 68.3029 | 123.1155 | 123.111 | 123.2849 | -55.1926 | -46.4127
5562.7812 | 123.4177 | -68.2251 | 54.8996 | -0.19478 | -0.011848 | -0.029715 | 0.001993 | -0.0097497 | -0.0073593 | -0.0011622 | 0.07782 | 0.20142 | -0.27008 | 55.1514 | 54.9271 | 54.9316 | 54.8996 | 55.1559 | 55.0003 | 8.4869 | 67.955 | -54.6982 | 68.3029 | 123.3765 | 0.027466 | 76.712 | 0.10071 | 0.3479 | 123.1247 | 123.381 | 123.1522 | 68.4265 | 68.3029 | 123.2254 | 123.1567 | 76.712 | 68.4265 | 68.3029 | 123.1567 | 123.1522 | 123.2254 | -55.1697 | -46.4127
5563.7656 | 123.3078 | -68.2297 | 54.95 | -0.19478 | -0.010779 | -0.030783 | 0.004343 | -0.0099633 | -0.0069321 | -0.00458 | 0.036621 | 0.2655 | -0.2655 | 55.0735 | 54.8767 | 54.8264 | 54.9866 | 55.069 | 55.0415 | 8.4824 | 67.9642 | -54.6844 | 68.2663 | 123.3032 | -0.073242 | 76.712 | 0.091553 | 0.30212 | 123.2162 | 123.2986 | 123.1064 | 68.4952 | 68.2663 | 123.2712 | 123.056 | 76.712 | 68.4952 | 68.2663 | 123.056 | 123.1064 | 123.2712 | -55.2155 | -46.4676
5564.7656 | 123.349 | -68.248 | 54.9362 | -0.21004 | -0.012916 | -0.029929 | 0.002634 | -0.0099633 | -0.0086411 | -0.005221 | 0.050354 | 0.21515 | -0.27466 | 55.1193 | 54.776 | 54.8767 | 54.9454 | 55.0919 | 55.0369 | 8.4869 | 67.9733 | -54.7211 | 68.2983 | 123.3673 | -0.16022 | 76.7349 | 0.10071 | 0.32501 | 123.1934 | 123.3398 | 123.024 | 68.4631 | 68.2983 | 123.2849 | 123.1247 | 76.7349 | 68.4631 | 68.2983 | 123.1247 | 123.024 | 123.2849 | -55.2109 | -46.4493
5565.7812 | 123.4314 | -68.2297 | 54.895 | -0.149 | -0.013129 | -0.03057 | 0.00071144 | -0.011031 | -0.0067185 | -0.003512 | 0.10529 | 0.19684 | -0.3067 | 55.1834 | 54.9362 | 54.9225 | 54.8447 | 55.1605 | 54.982 | 8.4824 | 67.923 | -54.6982 | 68.335 | 123.4131 | 0.041198 | 76.712 | 0.086975 | 0.41199 | 123.0743 | 123.3902 | 123.1659 | 68.4265 | 68.335 | 123.2117 | 123.1522 | 76.712 | 68.4265 | 68.335 | 123.1522 | 123.1659 | 123.2117 | -55.2017 | -46.4127
5566.7812 | 123.436 | -68.2205 | 54.895 | 0.011215 | -0.015052 | -0.026511 | 0.00028404 | -0.0121 | -0.0082137 | -0.0022302 | 0.045776 | 0.17853 | -0.31128 | 55.1514 | 54.9408 | 54.9088 | 54.8172 | 55.1559 | 54.9728 | 8.4824 | 67.9092 | -54.7165 | 68.2663 | 123.3719 | 0.045776 | 76.7029 | 0.077819 | 0.35705 | 123.0377 | 123.3765 | 123.1613 | 68.399 | 68.2663 | 123.1934 | 123.1293 | 76.7029 | 68.399 | 68.2663 | 123.1293 | 123.1613 | 123.1934 | -55.2063 | -46.4127
5567.7812 | 123.5367 | -68.2022 | 54.9637 | -0.080337 | -0.01377 | -0.027579 | 0.00028404 | -0.010391 | -0.0067185 | -0.001803 | 0.068665 | 0.17853 | -0.3067 | 55.1971 | 54.7623 | 54.9408 | 54.808 | 55.1788 | 54.9866 | 8.4824 | 67.8955 | -54.7852 | 68.2709 | 123.3994 | -0.20142 | 76.6846 | 0.022888 | 0.37537 | 123.0103 | 123.381 | 122.9645 | 68.3807 | 68.2709 | 123.1888 | 123.143 | 76.6846 | 68.3807 | 68.2709 | 123.143 | 122.9645 | 123.1888 | -55.2704 | -46.4813
5568.7812 | 123.4406 | -68.2388 | 54.8859 | 0.0035856 | -0.013984 | -0.032065 | 0.0013522 | -0.010818 | -0.0088547 | -0.0026574 | 0.050354 | 0.20142 | -0.3067 | 55.1605 | 54.7394 | 54.9179 | 54.8035 | 55.1422 | 54.9957 | 8.4869 | 67.9321 | -54.6844 | 68.2892 | 123.3994 | -0.14648 | 76.7258 | 0.10986 | 0.35706 | 123.0423 | 123.381 | 122.9782 | 68.4402 | 68.2892 | 123.2346 | 123.1567 | 76.7258 | 68.4402 | 68.2892 | 123.1567 | 122.9782 | 123.2346 | -55.1926 | -46.3989
5569.7812 | 123.4451 | -68.2297 | 54.9088 | 0.026474 | -0.012702 | -0.03121 | 0.0022066 | -0.011245 | -0.0092819 | -0.0015894 | 0.022888 | 0.1831 | -0.30212 | 55.1468 | 54.7348 | 54.9179 | 54.7989 | 55.1285 | 54.9774 | 8.4869 | 67.9276 | -54.7256 | 68.2526 | 123.3765 | -0.17395 | 76.7166 | 0.068665 | 0.32501 | 123.0286 | 123.3582 | 122.9645 | 68.4128 | 68.2526 | 123.2071 | 123.1476 | 76.7166 | 68.4128 | 68.2526 | 123.1476 | 122.9645 | 123.2071 | -55.2109 | -46.4218
5570.7656 | 123.4451 | -68.2297 | 54.8996 | 0.0035856 | -0.011634 | -0.026083 | 0.0034884 | -0.010604 | -0.011632 | -0.0039392 | 0.09613 | 0.17395 | -0.27924 | 55.2521 | 54.5013 | 54.8767 | 54.7073 | 55.1788 | 54.9545 | 8.4915 | 67.9504 | -54.7256 | 68.3258 | 123.4818 | -0.39825 | 76.7212 | 0.054932 | 0.37537 | 122.937 | 123.4085 | 122.731 | 68.4036 | 68.3258 | 123.1842 | 123.1064 | 76.7212 | 68.4036 | 68.3258 | 123.1064 | 122.731 | 123.1842 | -55.1788 | -46.4081
5571.7812 | 123.4222 | -68.2251 | 54.8996 | -0.011673 | -0.014197 | -0.030142 | 0.001993 | -0.012954 | -0.0071457 | -0.0026574 | 0.018311 | 0.17853 | -0.30212 | 55.1514 | 54.7348 | 54.9133 | 54.808 | 55.1147 | 54.9728 | 8.4824 | 67.923 | -54.7211 | 68.2434 | 123.3765 | -0.16479 | 76.7075 | 0.073242 | 0.32044 | 123.0331 | 123.3398 | 122.9599 | 68.4036 | 68.2434 | 123.1979 | 123.1384 | 76.7075 | 68.4036 | 68.2434 | 123.1384 | 122.9599 | 123.1979 | -55.2017 | -46.4172
5572.7812 | 123.4039 | -68.2434 | 54.8904 | 0.27061 | -0.011848 | -0.02822 | 0.00028404 | -0.011672 | -0.0082137 | -0.0024438 | 0.022888 | 0.17853 | -0.28839 | 55.0919 | 54.6707 | 54.863 | 54.8309 | 55.069 | 54.9637 | 8.4824 | 67.955 | -54.7119 | 68.2663 | 123.3353 | -0.21973 | 76.7258 | 0.073242 | 0.31128 | 123.0743 | 123.3124 | 122.9141 | 68.4219 | 68.2663 | 123.2071 | 123.1064 | 76.7258 | 68.4219 | 68.2663 | 123.1064 | 122.9141 | 123.2071 | -55.1788 | -46.4081
5573.7812 | 123.4177 | -68.2297 | 54.8767 | 0.1638 | -0.01142 | -0.029929 | 0.0017794 | -0.010391 | -0.0050095 | -0.0020166 | -0.032043 | 0.1236 | -0.33417 | 55.1056 | 54.8721 | 54.8538 | 55.0507 | 55.2063 | 54.9683 | 8.4869 | 67.8955 | -54.7531 | 68.1976 | 123.3353 | -0.004578 | 76.7166 | 0.091553 | 0.30212 | 123.2803 | 123.436 | 123.1018 | 68.3533 | 68.1976 | 123.1979 | 123.0835 | 76.7166 | 68.3533 | 68.1976 | 123.0835 | 123.1018 | 123.1979 | -55.2109 | -46.3898
5574.7812 | 123.3856 | -68.2205 | 54.8813 | 0.14854 | -0.012488 | -0.03121 | 7.0444e-05 | -0.011672 | -0.0073593 | -0.0047938 | -0.022888 | 0.16022 | -0.30212 | 55.1193 | 54.6982 | 54.8538 | 54.8264 | 55.0781 | 54.95 | 8.4824 | 67.9184 | -54.7211 | 68.1976 | 123.3398 | -0.18311 | 76.7029 | 0.068664 | 0.27924 | 123.0469 | 123.2986 | 122.9187 | 68.3807 | 68.1976 | 123.1705 | 123.0743 | 76.7029 | 68.3807 | 68.1976 | 123.0743 | 122.9187 | 123.1705 | -55.1834 | -46.3989
5575.7812 | 123.381 | -68.2571 | 54.8813 | 0.12566 | -0.010993 | -0.027365 | 0.0015658 | -0.0121 | -0.0052231 | -0.0026574 | -0.045776 | 0.16022 | -0.31128 | 55.1331 | 54.7028 | 54.8676 | 54.7897 | 55.0598 | 54.9362 | 8.4732 | 67.9459 | -54.7211 | 68.2114 | 123.3902 | -0.17853 | 76.7303 | 0.054931 | 0.2655 | 123.0469 | 123.317 | 122.9599 | 68.4174 | 68.2114 | 123.1934 | 123.1247 | 76.7303 | 68.4174 | 68.2114 | 123.1247 | 122.9599 | 123.1934 | -55.1926 | -46.4081
5576.7812 | 123.3948 | -68.2297 | 54.8721 | 0.14092 | -0.012702 | -0.029288 | 0.0015658 | -0.012954 | -0.0077865 | -0.0058618 | -0.013733 | 0.14648 | -0.32501 | 55.1147 | 54.689 | 54.8813 | 54.8172 | 55.3528 | 54.9866 | 8.4778 | 67.9047 | -54.7256 | 68.2159 | 123.3444 | -0.18311 | 76.7075 | 0.11444 | 0.31128 | 123.0469 | 123.5825 | 122.9187 | 68.3762 | 68.2159 | 123.2162 | 123.111 | 76.7075 | 68.3762 | 68.2159 | 123.111 | 122.9187 | 123.2162 | -55.1971 | -46.3943
5577.7656 | 123.4314 | -68.2343 | 54.9133 | 0.072251 | -0.010779 | -0.029929 | 0.00028404 | -0.01274 | -0.0058639 | -0.0043664 | 0.004578 | 0.19226 | -0.32044 | 55.1514 | 54.7211 | 54.8904 | 54.8172 | 55.101 | 54.982 | 8.4824 | 67.9138 | -54.7211 | 68.2388 | 123.3856 | -0.19226 | 76.7166 | 0.068665 | 0.32501 | 123.0515 | 123.3353 | 122.9553 | 68.4265 | 68.2388 | 123.2162 | 123.1247 | 76.7166 | 68.4265 | 68.2388 | 123.1247 | 122.9553 | 123.2162 | -55.2338 | -46.431
5578.7812 | 123.3902 | -68.2571 | 54.895 | 0.011215 | -0.015693 | -0.029715 | 0.0030612 | -0.011245 | -0.0069321 | -0.0032984 | 0.073242 | 0.17395 | -0.3067 | 55.1285 | 54.6753 | 54.863 | 54.8172 | 55.0644 | 54.9637 | 8.4778 | 67.9504 | -54.7211 | 68.3304 | 123.3856 | -0.21973 | 76.7349 | 0.068664 | 0.37994 | 123.0743 | 123.3215 | 122.9324 | 68.4311 | 68.3304 | 123.2208 | 123.1201 | 76.7349 | 68.4311 | 68.3304 | 123.1201 | 122.9324 | 123.2208 | -55.2017 | -46.4172
5579.7812 | 123.3994 | -68.2205 | 54.8721 | 0.21721 | -0.010779 | -0.027152 | 0.003702 | -0.010391 | -0.0067185 | -0.0026574 | -0.004578 | 0.10071 | -0.35248 | 55.1331 | 54.7119 | 54.895 | 54.7623 | 55.0644 | 54.9133 | 8.4824 | 67.868 | -54.7714 | 68.2159 | 123.3536 | -0.16022 | 76.7029 | 0.041199 | 0.3479 | 122.9828 | 123.2849 | 122.9324 | 68.3212 | 68.2159 | 123.1338 | 123.1155 | 76.7029 | 68.3212 | 68.2159 | 123.1155 | 122.9324 | 123.1338 | -55.2246 | -46.3898
5580.7812 | 123.4406 | -68.2114 | 54.8904 | 0.22484 | -0.012061 | -0.027365 | 0.004343 | -0.011672 | -0.0065047 | -0.0026574 | -0.004578 | 0.10529 | -0.36163 | 55.1514 | 54.7028 | 54.8996 | 54.7394 | 55.0873 | 54.9271 | 8.4915 | 67.8497 | -54.7852 | 68.2068 | 123.3627 | -0.18768 | 76.7029 | 0.036621 | 0.35705 | 122.9507 | 123.2986 | 122.9141 | 68.3167 | 68.2068 | 123.1384 | 123.111 | 76.7029 | 68.3167 | 68.2068 | 123.111 | 122.9141 | 123.1384 | -55.2521 | -46.3989
5581.7812 | 123.4039 | -68.2434 | 54.8767 | 0.20958 | -0.013343 | -0.02822 | 0.004343 | -0.012527 | -0.0084273 | -0.0022302 | -0.022888 | 0.1236 | -0.37537 | 55.1239 | 54.8309 | 54.8767 | 54.7852 | 55.0552 | 54.9042 | 8.4824 | 67.868 | -54.7531 | 68.2205 | 123.3673 | -0.045776 | 76.7258 | 0.027466 | 0.35248 | 123.0286 | 123.2986 | 123.0743 | 68.367 | 68.2205 | 123.1476 | 123.1201 | 76.7258 | 68.367 | 68.2205 | 123.1201 | 123.0743 | 123.1476 | -55.2521 | -46.3943
5582.7812 | 123.4177 | -68.2526 | 54.8767 | 0.21721 | -0.011634 | -0.025656 | 0.0047702 | -0.01274 | -0.0071457 | -0.0015894 | -0.022888 | 0.10986 | -0.35706 | 55.1285 | 54.7073 | 54.8859 | 54.7714 | 55.0644 | 54.9042 | 8.4869 | 67.8955 | -54.7668 | 68.2297 | 123.381 | -0.16937 | 76.7395 | 0.027466 | 0.33417 | 123.024 | 123.317 | 122.9599 | 68.3624 | 68.2297 | 123.1567 | 123.1384 | 76.7395 | 68.3624 | 68.2297 | 123.1384 | 122.9599 | 123.1567 | -55.2338 | -46.3898
5583.7656 | 123.3948 | -68.2434 | 54.8996 | 0.20195 | -0.009925 | -0.029288 | 0.0015658 | -0.011672 | -0.0069321 | -0.0015894 | -0.054932 | 0.16937 | -0.28839 | 55.1239 | 54.895 | 54.8767 | 54.8218 | 55.0644 | 54.9454 | 8.4824 | 67.955 | -54.7302 | 68.1885 | 123.3673 | -0.004577 | 76.7258 | 0.045777 | 0.23346 | 123.0652 | 123.3078 | 123.1384 | 68.4128 | 68.1885 | 123.1888 | 123.1201 | 76.7258 | 68.4128 | 68.1885 | 123.1201 | 123.1384 | 123.1888 | -55.188 | -46.4172
5584.7656 | 123.3856 | -68.2617 | 54.8859 | 0.15617 | -0.010352 | -0.026511 | 0.0047702 | -0.012313 | -0.0045821 | -0.0024438 | -0.018311 | 0.15564 | -0.32501 | 55.0827 | 54.9042 | 54.8813 | 54.8401 | 55.0461 | 54.9271 | 8.4778 | 67.9367 | -54.7302 | 68.2434 | 123.3444 | 0.018311 | 76.7395 | 0.041199 | 0.3067 | 123.1018 | 123.3078 | 123.1659 | 68.4174 | 68.2434 | 123.1888 | 123.143 | 76.7395 | 68.4174 | 68.2434 | 123.143 | 123.1659 | 123.1888 | -55.2109 | -46.4081
5585.7656 | 123.3673 | -68.2526 | 54.8676 | 0.087509 | -0.010779 | -0.024802 | 0.0013522 | -0.012313 | -0.0041549 | -0.0024438 | -0.027466 | 0.16479 | -0.33417 | 55.1239 | 54.8813 | 54.808 | 55.0552 | 55.0781 | 54.9637 | 8.4778 | 67.9184 | -54.7028 | 68.2251 | 123.3765 | 0.013733 | 76.7303 | 0.09613 | 0.3067 | 123.3078 | 123.3307 | 123.1338 | 68.4174 | 68.2251 | 123.2162 | 123.0606 | 76.7303 | 68.4174 | 68.2251 | 123.0606 | 123.1338 | 123.2162 | -55.2017 | -46.3898
5586.7812 | 123.4314 | -68.2343 | 54.8859 | 0.27824 | -0.011634 | -0.023734 | 0.00712 | -0.0076135 | -0.0056503 | -0.0024438 | -0.004578 | 0.13275 | -0.34332 | 55.1514 | 54.9088 | 54.895 | 54.7256 | 55.0873 | 54.9454 | 8.4778 | 67.8909 | -54.7531 | 68.2297 | 123.3856 | 0.022888 | 76.712 | 0.05951 | 0.33874 | 122.9599 | 123.3215 | 123.143 | 68.367 | 68.2297 | 123.1796 | 123.1293 | 76.712 | 68.367 | 68.2297 | 123.1293 | 123.143 | 123.1796 | -55.2292 | -46.4081
5587.7812 | 123.436 | -68.2434 | 54.8584 | 0.31639 | -0.011848 | -0.023947 | 0.0062656 | -0.0121 | -0.0037277 | -0.005221 | 0.032043 | 0.086975 | -0.3479 | 55.1331 | 54.9088 | 54.8996 | 54.7302 | 55.0827 | 54.9088 | 8.4824 | 67.8955 | -54.7714 | 68.2755 | 123.3765 | 0.050354 | 76.7258 | 0.050354 | 0.37994 | 122.9736 | 123.3261 | 123.1522 | 68.3304 | 68.2755 | 123.1522 | 123.143 | 76.7258 | 68.3304 | 68.2755 | 123.143 | 123.1522 | 123.1522 | -55.2063 | -46.376
5588.7812 | 123.4314 | -68.2434 | 54.8538 | 0.25536 | -0.0088568 | -0.026938 | 0.0051974 | -0.0095361 | -0.0080001 | -0.0032984 | -0.027466 | 0.11444 | -0.35248 | 55.1331 | 54.9225 | 54.9133 | 54.7577 | 55.0735 | 54.9042 | 8.4869 | 67.8909 | -54.7394 | 68.2159 | 123.3765 | 0.068664 | 76.7303 | 0.050354 | 0.32501 | 123.0011 | 123.317 | 123.1659 | 68.3578 | 68.2159 | 123.1476 | 123.1567 | 76.7303 | 68.3578 | 68.2159 | 123.1567 | 123.1659 | 123.1476 | -55.2063 | -46.3669
5589.7812 | 123.436 | -68.2526 | 54.8904 | 0.2401 | -0.010566 | -0.022879 | 0.0066928 | -0.0099633 | -0.0060775 | -0.00052119 | 0 | 0.12817 | -0.36163 | 55.1514 | 54.9133 | 54.9042 | 54.744 | 55.0781 | 54.9133 | 8.4824 | 67.8909 | -54.7623 | 68.2526 | 123.4039 | 0.022888 | 76.7349 | 0.022888 | 0.36163 | 122.9965 | 123.3307 | 123.1659 | 68.3807 | 68.2526 | 123.1659 | 123.1567 | 76.7349 | 68.3807 | 68.2526 | 123.1567 | 123.1659 | 123.1659 | -55.2521 | -46.4081
5590.7656 | 123.3398 | -68.248 | 54.9133 | 0.14854 | -0.010139 | -0.027579 | 0.002634 | -0.011031 | -0.0060775 | -0.0015894 | -0.018311 | 0.13733 | -0.32501 | 55.1102 | 54.8859 | 54.8676 | 54.808 | 55.069 | 54.9408 | 8.4824 | 67.923 | -54.776 | 68.2297 | 123.3582 | -0.027466 | 76.7303 | 0.027466 | 0.3067 | 123.056 | 123.317 | 123.1338 | 68.3853 | 68.2297 | 123.1888 | 123.1155 | 76.7303 | 68.3853 | 68.2297 | 123.1155 | 123.1338 | 123.1888 | -55.2383 | -46.431
5591.7656 | 123.4039 | -68.2663 | 54.8904 | 0.18669 | -0.010993 | -0.024802 | 0.0045566 | -0.011459 | -0.0054367 | -0.0032984 | -0.032043 | 0.1236 | -0.35706 | 55.1147 | 54.8996 | 54.895 | 54.7943 | 55.069 | 54.8996 | 8.4778 | 67.9092 | -54.7668 | 68.2343 | 123.381 | 0.009155 | 76.7441 | 0.009155 | 0.32501 | 123.0606 | 123.3353 | 123.1659 | 68.3899 | 68.2343 | 123.1659 | 123.1613 | 76.7441 | 68.3899 | 68.2343 | 123.1613 | 123.1659 | 123.1659 | -55.2475 | -46.4127
5592.7656 | 123.4039 | -68.2617 | 54.863 | 0.19432 | -0.010993 | -0.029074 | 0.0030612 | -0.0121 | -0.0073593 | -0.0022302 | -0.013733 | 0.11902 | -0.36163 | 55.1056 | 54.8996 | 54.8813 | 54.7943 | 55.0644 | 54.9179 | 8.4778 | 67.9001 | -54.744 | 68.248 | 123.3673 | 0.036621 | 76.7395 | 0.054932 | 0.3479 | 123.056 | 123.3261 | 123.1613 | 68.3807 | 68.248 | 123.1796 | 123.143 | 76.7395 | 68.3807 | 68.248 | 123.143 | 123.1613 | 123.1796 | -55.2246 | -46.3852
5593.7812 | 123.436 | -68.2434 | 54.863 | 0.21721 | -0.011848 | -0.024161 | 0.0075472 | -0.010177 | -0.0075729 | -0.0030848 | -0.19684 | 0.10071 | -0.37994 | 55.1285 | 54.8584 | 54.9316 | 54.7302 | 55.0781 | 54.8904 | 8.4824 | 67.8635 | -54.7623 | 68.0466 | 123.3719 | -0.004578 | 76.7258 | 0.027466 | 0.18311 | 122.9736 | 123.3215 | 123.1018 | 68.3441 | 68.0466 | 123.1338 | 123.175 | 76.7258 | 68.3441 | 68.0466 | 123.175 | 123.1018 | 123.1338 | -55.2429 | -46.3806
5594.7812 | 123.4268 | -68.2434 | 54.863 | 0.15617 | -0.0097114 | -0.029074 | 0.0086154 | -0.010391 | -0.0041549 | -0.0028712 | 0.004578 | 0.11902 | -0.36621 | 55.1971 | 55.0049 | 55.014 | 54.7165 | 55.1102 | 54.9042 | 8.4778 | 67.8772 | -54.744 | 68.248 | 123.4406 | 0.14191 | 76.7212 | 0.041199 | 0.37079 | 122.9599 | 123.3536 | 123.2483 | 68.3624 | 68.248 | 123.1476 | 123.2574 | 76.7212 | 68.3624 | 68.248 | 123.2574 | 123.2483 | 123.1476 | -55.2292 | -46.3852
5595.7812 | 123.436 | -68.2571 | 54.8492 | 0.24773 | -0.0097114 | -0.02352 | 0.0056246 | -0.010177 | -0.0058639 | -0.0024438 | -0.004578 | 0.12817 | -0.34332 | 55.1376 | 54.9271 | 54.9133 | 54.7302 | 55.069 | 54.8904 | 8.4869 | 67.9138 | -54.7211 | 68.2526 | 123.3948 | 0.07782 | 76.7441 | 0.041199 | 0.33874 | 122.9874 | 123.3261 | 123.1842 | 68.3853 | 68.2526 | 123.1476 | 123.1705 | 76.7441 | 68.3853 | 68.2526 | 123.1705 | 123.1842 | 123.1476 | -55.1926 | -46.3623
5596.7812 | 123.4268 | -68.2205 | 54.8767 | 0.25536 | -0.011848 | -0.021384 | 0.005411 | -0.011031 | -0.0043685 | -0.0022302 | 0.018311 | 0.1236 | -0.3479 | 55.1331 | 54.8813 | 54.9316 | 54.744 | 55.0964 | 54.9042 | 8.4824 | 67.8726 | -54.7531 | 68.2388 | 123.3536 | 0.004578 | 76.7029 | 0.027466 | 0.36621 | 122.9645 | 123.317 | 123.1018 | 68.3441 | 68.2388 | 123.1247 | 123.1522 | 76.7029 | 68.3441 | 68.2388 | 123.1522 | 123.1018 | 123.1247 | -55.2246 | -46.3943
5597.7656 | 123.4177 | -68.2388 | 54.8721 | 0.21721 | -0.010352 | -0.026083 | 0.0049838 | -0.0121 | -0.0060775 | -0.0022302 | -0.036621 | 0.11902 | -0.36621 | 55.101 | 54.7165 | 54.8859 | 54.7714 | 55.069 | 54.9088 | 8.4778 | 67.8726 | -54.7531 | 68.2022 | 123.3398 | -0.15564 | 76.7166 | 0.036621 | 0.32959 | 123.0103 | 123.3078 | 122.9553 | 68.3578 | 68.2022 | 123.1476 | 123.1247 | 76.7166 | 68.3578 | 68.2022 | 123.1247 | 122.9553 | 123.1476 | -55.2383 | -46.3943
5598.7656 | 123.3948 | -68.2388 | 54.8813 | 0.21721 | -0.010779 | -0.024802 | 0.0047702 | -0.0097497 | -0.0054367 | -0.0041528 | -0.027466 | 0.12817 | -0.37537 | 55.1239 | 54.7028 | 54.8904 | 54.7714 | 55.0735 | 54.9133 | 8.4915 | 67.8635 | -54.7531 | 68.2114 | 123.3627 | -0.17853 | 76.7303 | 0.032043 | 0.3479 | 123.0103 | 123.3124 | 122.9416 | 68.367 | 68.2114 | 123.1522 | 123.1293 | 76.7303 | 68.367 | 68.2114 | 123.1293 | 122.9416 | 123.1522 | -55.2567 | -46.3898
5599.7812 | 123.4497 | -68.2388 | 54.8813 | 0.22484 | -0.012702 | -0.029501 | 0.0081882 | -0.011245 | -0.0062911 | -0.0026574 | 0.013733 | 0.14191 | -0.33875 | 55.1514 | 54.7668 | 54.9225 | 54.7394 | 55.1102 | 54.9179 | 8.4869 | 67.9001 | -54.7394 | 68.2526 | 123.3902 | -0.11444 | 76.7258 | 0.036621 | 0.35248 | 122.9782 | 123.349 | 123.0057 | 68.3807 | 68.2526 | 123.1567 | 123.1613 | 76.7258 | 68.3807 | 68.2526 | 123.1613 | 123.0057 | 123.1567 | -55.22 | -46.3943
5600.7812 | 123.4314 | -68.2434 | 54.8996 | 0.30113 | -0.0080024 | -0.026297 | 0.0079744 | -0.010604 | -0.0045821 | -0.001803 | -0.013733 | 0.16022 | -0.3479 | 55.1331 | 54.8996 | 54.8767 | 54.744 | 55.0644 | 54.9042 | 8.4869 | 67.8955 | -54.7394 | 68.2297 | 123.3765 | 0 | 76.7303 | 0.004578 | 0.33417 | 122.9874 | 123.3078 | 123.143 | 68.4036 | 68.2297 | 123.1476 | 123.1201 | 76.7303 | 68.4036 | 68.2297 | 123.1201 | 123.143 | 123.1476 | -55.2475 | -46.4127
5601.7812 | 123.3994 | -68.2709 | 54.8859 | 0.27824 | -0.0094976 | -0.027579 | 0.0079744 | -0.0088953 | -0.0080001 | -0.00052119 | -0.032043 | 0.17853 | -0.35706 | 55.0964 | 54.8447 | 54.8676 | 54.7943 | 55.0369 | 54.9133 | 8.4869 | 67.9138 | -54.7073 | 68.2388 | 123.3673 | -0.041198 | 76.7578 | 0.027466 | 0.32501 | 123.0652 | 123.3078 | 123.1155 | 68.4494 | 68.2388 | 123.1842 | 123.1384 | 76.7578 | 68.4494 | 68.2388 | 123.1384 | 123.1155 | 123.1842 | -55.2429 | -46.3989
5602.7812 | 123.4497 | -68.2434 | 54.8904 | 0.30876 | -0.01142 | -0.025656 | 0.0090426 | -0.0082545 | -0.0067185 | -0.0032984 | 0 | 0.14191 | -0.37079 | 54.9545 | 54.95 | 54.9774 | 54.8492 | 55.0827 | 54.9179 | 8.4869 | 67.8726 | -54.7485 | 68.2434 | 123.1979 | 0.059509 | 76.7303 | 0.027466 | 0.37079 | 123.0927 | 123.3261 | 123.1934 | 68.3853 | 68.2434 | 123.1613 | 123.2208 | 76.7303 | 68.3853 | 68.2434 | 123.2208 | 123.1934 | 123.1613 | -55.2612 | -46.4035
5603.7812 | 123.4314 | -68.2571 | 54.8721 | 0.27061 | -0.0090704 | -0.027152 | 0.0075472 | -0.0097497 | -0.0077865 | -0.0013758 | -0.027466 | 0.15106 | -0.36163 | 55.1376 | 54.895 | 54.8904 | 54.776 | 55.0781 | 54.9088 | 8.4869 | 67.8955 | -54.7211 | 68.2297 | 123.3948 | 0.022889 | 76.7441 | 0.036621 | 0.33417 | 123.0331 | 123.3353 | 123.1522 | 68.4082 | 68.2297 | 123.1659 | 123.1476 | 76.7441 | 68.4082 | 68.2297 | 123.1476 | 123.1522 | 123.1659 | -55.2338 | -46.3852
5604.7656 | 123.4177 | -68.2388 | 54.8538 | 0.24773 | -0.009925 | -0.022665 | 0.0047702 | -0.011886 | -0.0084273 | -0.0024438 | -0.018311 | 0.16479 | -0.34332 | 55.1193 | 54.9133 | 54.9042 | 54.744 | 55.0827 | 54.8996 | 8.4778 | 67.8955 | -54.689 | 68.2205 | 123.3582 | 0.059509 | 76.7166 | 0.045776 | 0.32501 | 122.9828 | 123.3215 | 123.1522 | 68.4036 | 68.2205 | 123.1384 | 123.143 | 76.7166 | 68.4036 | 68.2205 | 123.143 | 123.1522 | 123.1384 | -55.1971 | -46.376
5605.7656 | 123.4314 | -68.2251 | 54.8813 | 0.24773 | -0.010566 | -0.022025 | 0.0075472 | -0.0097497 | -0.0077865 | -0.001803 | 0.018311 | 0.12817 | -0.34332 | 55.1331 | 54.7211 | 54.9271 | 54.7485 | 55.0873 | 54.9042 | 8.4686 | 67.8818 | -54.7531 | 68.2434 | 123.3582 | -0.16022 | 76.6937 | 0.022888 | 0.36163 | 122.9736 | 123.3124 | 122.9462 | 68.3533 | 68.2434 | 123.1293 | 123.1522 | 76.6937 | 68.3533 | 68.2434 | 123.1522 | 122.9462 | 123.1293 | -55.2246 | -46.4127
5606.7812 | 123.4131 | -68.248 | 54.8447 | 0.28587 | -0.0080024 | -0.027152 | 0.0064792 | -0.0073999 | -0.0067185 | -0.00458 | -0.009155 | 0.14191 | -0.3479 | 55.1102 | 54.8996 | 54.9225 | 54.744 | 55.0873 | 54.9454 | 8.4824 | 67.9001 | -54.7028 | 68.2388 | 123.3582 | 0.054931 | 76.7303 | 0.10071 | 0.33874 | 122.9919 | 123.3353 | 123.1476 | 68.3899 | 68.2388 | 123.1934 | 123.1705 | 76.7303 | 68.3899 | 68.2388 | 123.1705 | 123.1476 | 123.1934 | -55.1926 | -46.3623
5607.7812 | 123.3398 | -68.2755 | 54.895 | 0.30113 | -0.008216 | -0.023093 | 0.008829 | -0.0078271 | -0.0056503 | -0.0024438 | -0.036621 | 0.20599 | -0.36621 | 55.0644 | 54.6295 | 54.8218 | 54.8767 | 54.982 | 54.9728 | 8.4824 | 67.9092 | -54.689 | 68.2388 | 123.3398 | -0.2655 | 76.7578 | 0.077819 | 0.32959 | 123.1522 | 123.2574 | 122.905 | 68.4814 | 68.2388 | 123.2483 | 123.0972 | 76.7578 | 68.4814 | 68.2388 | 123.0972 | 122.905 | 123.2483 | -55.2612 | -46.4127
5608.7812 | 123.3948 | -68.28 | 54.863 | 0.26299 | -0.0080024 | -0.027365 | 0.00712 | -0.0082545 | -0.0047957 | -0.00030759 | -0.045776 | 0.19226 | -0.36163 | 55.0735 | 54.8584 | 54.8538 | 54.8172 | 55.014 | 54.9271 | 8.4732 | 67.9184 | -54.6707 | 68.2343 | 123.3536 | -0.004578 | 76.7532 | 0.064087 | 0.31586 | 123.0972 | 123.2941 | 123.1384 | 68.4723 | 68.2343 | 123.2071 | 123.1338 | 76.7532 | 68.4723 | 68.2343 | 123.1338 | 123.1384 | 123.2071 | -55.2246 | -46.3898
5609.7812 | 123.3673 | -68.2938 | 54.8721 | 0.2401 | -0.009925 | -0.023734 | 0.0079744 | -0.0084681 | -0.0047957 | -0.0020166 | -0.059509 | 0.20142 | -0.36621 | 55.0278 | 54.8492 | 54.8264 | 54.8676 | 54.9866 | 54.9362 | 8.4778 | 67.9276 | -54.6707 | 68.2343 | 123.3215 | -0.022888 | 76.7715 | 0.064087 | 0.3067 | 123.1613 | 123.2803 | 123.143 | 68.4952 | 68.2343 | 123.23 | 123.1201 | 76.7715 | 68.4952 | 68.2343 | 123.1201 | 123.143 | 123.23 | -55.2383 | -46.3943
5610.7812 | 123.3994 | -68.2846 | 54.8813 | 0.33928 | -0.013129 | -0.029929 | 0.0017794 | -0.0086817 | -0.0030869 | -0.0013758 | -0.068665 | 0.16937 | -0.31128 | 55.1056 | 54.9133 | 54.8859 | 54.8401 | 55.0781 | 54.9225 | 8.4824 | 67.9733 | -54.7119 | 68.2159 | 123.3902 | 0.032043 | 76.767 | 0.041198 | 0.24261 | 123.1247 | 123.3627 | 123.1979 | 68.454 | 68.2159 | 123.2071 | 123.1705 | 76.767 | 68.454 | 68.2159 | 123.1705 | 123.1979 | 123.2071 | -55.1926 | -46.3989
5611.7656 | 123.4406 | -68.248 | 54.863 | 0.23247 | -0.0080024 | -0.025015 | 0.0047702 | -0.0080407 | -0.0043685 | -0.00052119 | 0.004578 | 0.16937 | -0.37079 | 55.1331 | 54.8538 | 54.8584 | 54.7852 | 55.0873 | 54.9225 | 8.4824 | 67.8772 | -54.6936 | 68.2526 | 123.381 | -0.009155 | 76.7303 | 0.059509 | 0.37537 | 123.0331 | 123.3353 | 123.1018 | 68.4174 | 68.2526 | 123.1705 | 123.1064 | 76.7303 | 68.4174 | 68.2526 | 123.1064 | 123.1018 | 123.1705 | -55.2338 | -46.3806
5612.7656 | 123.4039 | -68.2846 | 54.8813 | 0.25536 | -0.008216 | -0.019461 | 0.0073336 | -0.0099633 | -0.0050095 | -0.0020166 | -0.045776 | 0.16479 | -0.36163 | 55.1056 | 54.8676 | 54.8584 | 54.7989 | 55.0461 | 54.9271 | 8.4824 | 67.923 | -54.7165 | 68.2388 | 123.3902 | -0.013733 | 76.767 | 0.045776 | 0.31586 | 123.0835 | 123.3307 | 123.1522 | 68.4494 | 68.2388 | 123.2117 | 123.143 | 76.767 | 68.4494 | 68.2388 | 123.143 | 123.1522 | 123.2117 | -55.2429 | -46.3989
5613.7812 | 123.349 | -68.3075 | 54.895 | 0.22484 | -0.007575 | -0.026297 | 0.0064792 | -0.010391 | -0.0065047 | -0.00052119 | -0.050354 | 0.20599 | -0.35706 | 55.0507 | 54.8355 | 54.8126 | 54.895 | 54.982 | 54.9591 | 8.4824 | 67.9504 | -54.689 | 68.2571 | 123.3582 | -0.05951 | 76.7899 | 0.064086 | 0.3067 | 123.2025 | 123.2895 | 123.143 | 68.5135 | 68.2571 | 123.2666 | 123.1201 | 76.7899 | 68.5135 | 68.2571 | 123.1201 | 123.143 | 123.2666 | -55.2521 | -46.4127
5614.7812 | 123.3078 | -68.2983 | 54.9179 | 0.072251 | -0.0073614 | -0.023306 | 0.0077608 | -0.0088953 | -0.0065047 | -0.003512 | -0.004578 | 0.23804 | -0.32044 | 55.0507 | 54.808 | 54.7852 | 54.9408 | 54.9728 | 54.982 | 8.4778 | 67.9779 | -54.6799 | 68.2938 | 123.349 | -0.10986 | 76.7761 | 0.064087 | 0.31586 | 123.2391 | 123.2712 | 123.1064 | 68.5364 | 68.2938 | 123.2803 | 123.0835 | 76.7761 | 68.5364 | 68.2938 | 123.0835 | 123.1064 | 123.2803 | -55.2383 | -46.4401
5615.7812 | 123.3307 | -68.2434 | 54.9271 | 0.15617 | -0.012061 | -0.026724 | 0.00071144 | -0.01274 | -0.0056503 | -0.0011622 | -0.045776 | 0.14191 | -0.3479 | 55.0781 | 54.895 | 54.8904 | 54.8126 | 55.069 | 54.9225 | 8.4778 | 67.8955 | -54.7852 | 68.1976 | 123.3215 | -0.032043 | 76.7212 | -0.004578 | 0.30212 | 123.056 | 123.3124 | 123.1384 | 68.3853 | 68.1976 | 123.1659 | 123.1338 | 76.7212 | 68.3853 | 68.1976 | 123.1338 | 123.1384 | 123.1659 | -55.275 | -46.4493
5616.7656 | 123.3353 | -68.2571 | 54.9179 | 0.034104 | -0.0090704 | -0.02117 | 0.010538 | -0.0088953 | -0.0075729 | -0.0043664 | 0.027466 | 0.2243 | -0.32959 | 55.069 | 54.8584 | 54.8309 | 54.9316 | 55.0095 | 54.9957 | 8.4778 | 67.9276 | -54.6936 | 68.2846 | 123.3261 | -0.05951 | 76.7349 | 0.07782 | 0.35706 | 123.1888 | 123.2666 | 123.1155 | 68.4814 | 68.2846 | 123.2529 | 123.0881 | 76.7349 | 68.4814 | 68.2846 | 123.0881 | 123.1155 | 123.2529 | -55.2475 | -46.4401
5617.7812 | 123.3398 | -68.2709 | 54.8996 | 0.056992 | -0.0090704 | -0.027579 | 0.0092562 | -0.0082545 | -0.0035141 | -0.00094839 | 0 | 0.21515 | -0.34332 | 55.0598 | 54.8218 | 54.8172 | 54.9225 | 54.982 | 54.982 | 8.4686 | 67.9276 | -54.6844 | 68.2709 | 123.3307 | -0.07782 | 76.7395 | 0.082398 | 0.34332 | 123.1934 | 123.2529 | 123.0927 | 68.486 | 68.2709 | 123.2529 | 123.0881 | 76.7395 | 68.486 | 68.2709 | 123.0881 | 123.0927 | 123.2529 | -55.2429 | -46.431
5618.7656 | 123.3261 | -68.3166 | 54.9133 | 0.23247 | -0.0086432 | -0.024161 | 0.0077608 | -0.0091089 | -0.0043685 | -0.0015894 | -0.045776 | 0.2243 | -0.37079 | 55.0323 | 54.8218 | 54.808 | 54.9133 | 54.9545 | 54.9591 | 8.4778 | 67.9459 | -54.689 | 68.2709 | 123.349 | -0.091553 | 76.7944 | 0.045776 | 0.32501 | 123.23 | 123.2712 | 123.1384 | 68.541 | 68.2709 | 123.2758 | 123.1247 | 76.7944 | 68.541 | 68.2709 | 123.1247 | 123.1384 | 123.2758 | -55.2841 | -46.4355
5619.7656 | 123.317 | -68.2755 | 54.8996 | 0.14854 | -0.0088568 | -0.020316 | 0.0073336 | -0.0076135 | -0.0065047 | -0.0011622 | -0.050354 | 0.21057 | -0.37079 | 55.0278 | 54.863 | 54.8218 | 54.9728 | 54.9683 | 54.9911 | 8.4732 | 67.9047 | -54.689 | 68.2251 | 123.3032 | -0.036621 | 76.7487 | 0.091553 | 0.32043 | 123.2483 | 123.2437 | 123.1384 | 68.486 | 68.2251 | 123.2666 | 123.0972 | 76.7487 | 68.486 | 68.2251 | 123.0972 | 123.1384 | 123.2666 | -55.2704 | -46.4264
5620.7812 | 123.4406 | -68.2526 | 54.8538 | 2.1322 | -0.0088568 | -0.022452 | 0.0045566 | -0.0091089 | -0.0043685 | -0.00052119 | -0.064087 | 0.10071 | -0.3891 | 55.1147 | 54.9225 | 54.9179 | 54.7577 | 55.0873 | 54.9133 | 8.4824 | 67.8635 | -54.7531 | 68.1885 | 123.3673 | 0.068664 | 76.7349 | 0.059509 | 0.32501 | 123.0103 | 123.3398 | 123.175 | 68.3533 | 68.1885 | 123.1659 | 123.1705 | 76.7349 | 68.3533 | 68.1885 | 123.1705 | 123.175 | 123.1659 | -55.2429 | -46.3715
5621.7812 | 123.3307 | -68.2526 | 54.9088 | -0.17952 | -0.009925 | -0.023306 | 0.0015658 | -0.0095361 | -0.0084273 | -0.00094839 | 0.036621 | 0.24719 | -0.29755 | 55.0919 | 54.7028 | 54.8584 | 54.9591 | 55.101 | 55.0278 | 8.4824 | 67.955 | -54.6616 | 68.2892 | 123.3444 | -0.20599 | 76.7349 | 0.11902 | 0.33417 | 123.2117 | 123.3536 | 122.9553 | 68.4998 | 68.2892 | 123.2803 | 123.111 | 76.7349 | 68.4998 | 68.2892 | 123.111 | 122.9553 | 123.2803 | -55.2063 | -46.4264
5622.7812 | 123.3673 | -68.2663 | 54.9042 | 0.018845 | -0.0080024 | -0.027365 | 0.010324 | -0.0059045 | -0.0073593 | -0.0030848 | 0.068665 | 0.22888 | -0.29297 | 55.1102 | 54.8721 | 54.8538 | 54.9179 | 55.0461 | 55.0186 | 8.4732 | 67.9733 | -54.6753 | 68.335 | 123.3765 | -0.032044 | 76.7395 | 0.11444 | 0.36163 | 123.1842 | 123.3124 | 123.1384 | 68.4952 | 68.335 | 123.2849 | 123.1201 | 76.7395 | 68.4952 | 68.335 | 123.1201 | 123.1384 | 123.2849 | -55.1971 | -46.431
5623.7812 | 123.3719 | -68.2526 | 54.9133 | -0.33211 | -0.0080024 | -0.026511 | 0.0066928 | -0.0065455 | -0.0067185 | -0.0047938 | 0.041199 | 0.23346 | -0.29297 | 55.1056 | 54.8859 | 54.8721 | 54.9088 | 55.0598 | 55.0095 | 8.4732 | 67.9596 | -54.6799 | 68.2938 | 123.3582 | -0.027466 | 76.7258 | 0.09613 | 0.33417 | 123.1613 | 123.3124 | 123.1384 | 68.486 | 68.2938 | 123.262 | 123.1247 | 76.7258 | 68.486 | 68.2938 | 123.1247 | 123.1384 | 123.262 | -55.2063 | -46.4401
5624.7812 | 123.3627 | -68.2709 | 54.9271 | -0.04982 | -0.0097114 | -0.025656 | 0.0066928 | -0.0063317 | -0.0035141 | -0.0032984 | 0.045776 | 0.24261 | -0.30212 | 55.0461 | 54.9637 | 54.8447 | 55.0049 | 55.0552 | 54.9957 | 8.4778 | 67.9688 | -54.6844 | 68.3167 | 123.317 | 0.036621 | 76.7487 | 0.068665 | 0.3479 | 123.2758 | 123.3261 | 123.2346 | 68.5135 | 68.3167 | 123.2666 | 123.1155 | 76.7487 | 68.5135 | 68.3167 | 123.1155 | 123.2346 | 123.2666 | -55.2292 | -46.4493
5625.7656 | 123.3444 | -68.2846 | 54.8996 | -0.019302 | -0.008216 | -0.022025 | 0.0077608 | -0.0073999 | -0.0071457 | -0.00094839 | 0.022888 | 0.21515 | -0.32959 | 55.0781 | 54.8676 | 54.8309 | 54.9545 | 55.0232 | 55.0095 | 8.4732 | 67.955 | -54.6844 | 68.3075 | 123.3627 | -0.032043 | 76.7578 | 0.10986 | 0.35248 | 123.2391 | 123.3078 | 123.1522 | 68.4998 | 68.3075 | 123.2941 | 123.1155 | 76.7578 | 68.4998 | 68.3075 | 123.1155 | 123.1522 | 123.2941 | -55.2292 | -46.4264
5626.7656 | 123.3673 | -68.28 | 54.895 | 0.0035856 | -0.0088568 | -0.02587 | 0.0079744 | -0.0073999 | -0.0058639 | -0.00030759 | 0.045776 | 0.22888 | -0.31586 | 55.0781 | 54.8676 | 54.8492 | 54.9179 | 55.0644 | 55.0186 | 8.4824 | 67.9642 | -54.6661 | 68.3258 | 123.3582 | -0.027466 | 76.7624 | 0.1236 | 0.36163 | 123.1979 | 123.3444 | 123.1476 | 68.5089 | 68.3258 | 123.2986 | 123.1293 | 76.7624 | 68.5089 | 68.3258 | 123.1293 | 123.1476 | 123.2986 | -55.2109 | -46.4127
5627.7812 | 123.3536 | -68.28 | 54.9271 | -0.15663 | -0.0090704 | -0.025443 | 0.0041292 | -0.0078271 | -0.0067185 | -0.0032984 | 0.027466 | 0.29297 | -0.29297 | 55.0735 | 54.8767 | 54.8401 | 55.0095 | 55.0461 | 55.0507 | 8.4824 | 67.9871 | -54.6341 | 68.3075 | 123.3536 | -0.050354 | 76.7624 | 0.1236 | 0.32043 | 123.2895 | 123.3261 | 123.1567 | 68.573 | 68.3075 | 123.3307 | 123.1201 | 76.7624 | 68.573 | 68.3075 | 123.1201 | 123.1567 | 123.3307 | -55.22 | -46.4447
5628.7812 | 123.3353 | -68.2755 | 54.9408 | -0.13374 | -0.010566 | -0.025656 | 0.0045566 | -0.0091089 | -0.0065047 | -0.0026574 | 0.013733 | 0.28839 | -0.29755 | 55.0598 | 54.8859 | 54.8218 | 55.014 | 55.0323 | 55.0232 | 8.4824 | 67.9779 | -54.6524 | 68.2892 | 123.3353 | -0.054932 | 76.7578 | 0.082397 | 0.31128 | 123.2895 | 123.3078 | 123.1613 | 68.5638 | 68.2892 | 123.2986 | 123.0972 | 76.7578 | 68.5638 | 68.2892 | 123.0972 | 123.1613 | 123.2986 | -55.2383 | -46.4584
5629.7812 | 123.3765 | -68.2755 | 54.9316 | -0.15663 | -0.008216 | -0.025229 | 0.003702 | -0.0071863 | -0.0062911 | -0.0041528 | 0.041199 | 0.27924 | -0.28839 | 55.0781 | 54.8767 | 54.8492 | 54.9866 | 55.0507 | 55.0598 | 8.4869 | 67.9871 | -54.6524 | 68.3167 | 123.3536 | -0.054932 | 76.7624 | 0.12817 | 0.32959 | 123.262 | 123.3261 | 123.1522 | 68.5547 | 68.3167 | 123.3353 | 123.1247 | 76.7624 | 68.5547 | 68.3167 | 123.1247 | 123.1522 | 123.3353 | -55.22 | -46.4447
5630.7812 | 123.3444 | -68.2526 | 54.9362 | -0.17189 | -0.0094976 | -0.02822 | 0.003702 | -0.0088953 | -0.0071457 | -0.0050074 | 0.036621 | 0.29297 | -0.28839 | 55.069 | 54.8767 | 54.8447 | 54.9911 | 55.0598 | 55.0323 | 8.4778 | 67.9642 | -54.6432 | 68.2892 | 123.3215 | -0.059509 | 76.7303 | 0.096131 | 0.32501 | 123.2437 | 123.3124 | 123.1293 | 68.5455 | 68.2892 | 123.2849 | 123.0972 | 76.7303 | 68.5455 | 68.2892 | 123.0972 | 123.1293 | 123.2849 | -55.2246 | -46.4584
5631.7812 | 123.3398 | -68.2755 | 54.9454 | -0.19478 | -0.011207 | -0.031851 | 0.0056246 | -0.010604 | -0.0056503 | -9.3992e-05 | 0.018311 | 0.24719 | -0.3067 | 55.0644 | 54.8447 | 54.8264 | 55.0186 | 55.0507 | 55.0461 | 8.4778 | 67.9688 | -54.6982 | 68.2938 | 123.3398 | -0.10071 | 76.7532 | 0.10071 | 0.32501 | 123.2941 | 123.3261 | 123.1201 | 68.5226 | 68.2938 | 123.3215 | 123.1018 | 76.7532 | 68.5226 | 68.2938 | 123.1018 | 123.1201 | 123.3215 | -55.2521 | -46.4676
5632.7656 | 123.3582 | -68.2617 | 54.895 | -0.11085 | -0.012702 | -0.028861 | 0.0073336 | -0.0069727 | -0.0073593 | -0.0022302 | 0.032043 | 0.27466 | -0.31586 | 55.0919 | 54.895 | 54.8584 | 54.9454 | 55.0735 | 55.0415 | 8.4824 | 67.9459 | -54.6204 | 68.2938 | 123.3536 | 0 | 76.7441 | 0.14648 | 0.3479 | 123.2071 | 123.3353 | 123.1567 | 68.5364 | 68.2938 | 123.3032 | 123.1201 | 76.7441 | 68.5364 | 68.2938 | 123.1201 | 123.1567 | 123.3032 | -55.2109 | -46.4127
5633.7812 | 123.3307 | -68.2709 | 54.9225 | -0.17189 | -0.011634 | -0.025656 | 0.0028476 | -0.0071863 | -0.0094955 | -0.0022302 | 0.027466 | 0.28381 | -0.27924 | 55.0735 | 54.8676 | 54.8355 | 54.9911 | 55.0552 | 55.0507 | 8.4732 | 67.9916 | -54.6387 | 68.2983 | 123.3444 | -0.054931 | 76.7441 | 0.12817 | 0.3067 | 123.262 | 123.3261 | 123.1384 | 68.5547 | 68.2983 | 123.3215 | 123.1064 | 76.7441 | 68.5547 | 68.2983 | 123.1064 | 123.1384 | 123.3215 | -55.2017 | -46.4493
5634.7812 | 123.3353 | -68.2388 | 54.9225 | -0.19478 | -0.010352 | -0.027152 | 0.0015658 | -0.0121 | -0.0050095 | -0.0024438 | 0.045776 | 0.27008 | -0.27924 | 55.0873 | 54.8676 | 54.8309 | 54.9957 | 55.0781 | 55.0369 | 8.4824 | 67.9596 | -54.6524 | 68.2846 | 123.3261 | -0.054931 | 76.7212 | 0.11444 | 0.32501 | 123.2346 | 123.317 | 123.1064 | 68.5089 | 68.2846 | 123.2758 | 123.0698 | 76.7212 | 68.5089 | 68.2846 | 123.0698 | 123.1064 | 123.2758 | -55.2017 | -46.4401
5635.7812 | 123.3673 | -68.2434 | 54.9088 | -0.21004 | -0.011207 | -0.02822 | 0.00092504 | -0.0088953 | -0.0050095 | -0.0024438 | 0.059509 | 0.2243 | -0.27466 | 55.1147 | 54.9088 | 54.8767 | 54.9637 | 55.1102 | 55.0095 | 8.4869 | 67.9688 | -54.6844 | 68.3029 | 123.3582 | 0 | 76.7303 | 0.10071 | 0.33417 | 123.2071 | 123.3536 | 123.1522 | 68.4677 | 68.3029 | 123.2529 | 123.1201 | 76.7303 | 68.4677 | 68.3029 | 123.1201 | 123.1522 | 123.2529 | -55.1834 | -46.4218
5636.7812 | 123.3124 | -68.2571 | 54.9271 | -0.21004 | -0.012061 | -0.030783 | 0.004343 | -0.010391 | -0.0069321 | -0.0020166 | 0.022888 | 0.27924 | -0.28381 | 55.2292 | 54.9545 | 54.7806 | 54.9042 | 55.0323 | 55.0415 | 8.4778 | 67.9733 | -54.6478 | 68.28 | 123.4863 | 0.027466 | 76.7349 | 0.11444 | 0.3067 | 123.1613 | 123.2895 | 123.2117 | 68.5364 | 68.28 | 123.2986 | 123.0377 | 76.7349 | 68.5364 | 68.28 | 123.0377 | 123.2117 | 123.2986 | -55.2109 | -46.4493
5637.7812 | 123.3353 | -68.248 | 54.9316 | -0.19478 | -0.013343 | -0.030142 | 0.002634 | -0.010177 | -0.0082137 | -0.0028712 | 0.054932 | 0.23346 | -0.26093 | 55.0964 | 54.8721 | 54.8538 | 55.0186 | 55.0598 | 55.0552 | 8.4824 | 67.9871 | -54.6982 | 68.3029 | 123.3444 | -0.05951 | 76.7303 | 0.1236 | 0.31586 | 123.2666 | 123.3078 | 123.1201 | 68.4814 | 68.3029 | 123.3032 | 123.1018 | 76.7303 | 68.4814 | 68.3029 | 123.1018 | 123.1201 | 123.3032 | -55.1926 | -46.4493
5638.7656 | 123.3307 | -68.2846 | 54.9271 | -0.17952 | -0.010993 | -0.026297 | 0.001993 | -0.0099633 | -0.0097091 | -0.0032984 | 0.032043 | 0.2655 | -0.28839 | 55.0735 | 54.8355 | 54.8309 | 55.0095 | 55.0598 | 55.0552 | 8.4869 | 67.9962 | -54.6616 | 68.3166 | 123.3582 | -0.091553 | 76.7715 | 0.12817 | 0.32043 | 123.2941 | 123.3444 | 123.1201 | 68.5501 | 68.3166 | 123.3398 | 123.1155 | 76.7715 | 68.5501 | 68.3166 | 123.1155 | 123.1201 | 123.3398 | -55.2155 | -46.4401
5639.7656 | 123.3215 | -68.2709 | 54.9088 | -0.355 | -0.011207 | -0.027152 | 0.0041292 | -0.0078271 | -0.0069321 | -0.0028712 | -0.004578 | 0.27008 | -0.28839 | 55.0644 | 54.8447 | 54.8126 | 54.9957 | 55.0415 | 55.0323 | 8.4732 | 67.9825 | -54.6387 | 68.2663 | 123.3353 | -0.064086 | 76.7441 | 0.1236 | 0.28381 | 123.2666 | 123.3124 | 123.1155 | 68.541 | 68.2663 | 123.3032 | 123.0835 | 76.7441 | 68.541 | 68.2663 | 123.0835 | 123.1155 | 123.3032 | -55.1971 | -46.4355
5640.7656 | 123.3444 | -68.2846 | 54.9179 | -0.32448 | -0.010566 | -0.028006 | -0.00078396 | -0.0091089 | -0.0052231 | -0.0032984 | 0.013733 | 0.25177 | -0.27924 | 54.9957 | 54.895 | 54.8355 | 54.9591 | 55.069 | 55.0278 | 8.4869 | 68.0054 | -54.6661 | 68.2983 | 123.2803 | -0.022888 | 76.7715 | 0.10986 | 0.29297 | 123.2437 | 123.3536 | 123.1796 | 68.5364 | 68.2983 | 123.3124 | 123.1201 | 76.7715 | 68.5364 | 68.2983 | 123.1201 | 123.1796 | 123.3124 | -55.1971 | -46.431
5641.7812 | 123.4451 | -68.2434 | 54.8904 | -0.17952 | -0.010993 | -0.028647 | 0.00028404 | -0.011672 | -0.0069321 | -0.0020166 | 0.07782 | 0.19226 | -0.27924 | 55.1743 | 54.9591 | 54.95 | 54.8309 | 55.1651 | 54.9957 | 8.4824 | 67.9642 | -54.6982 | 68.3212 | 123.4177 | 0.068664 | 76.7258 | 0.10529 | 0.35706 | 123.0743 | 123.4085 | 123.2025 | 68.4357 | 68.3212 | 123.2391 | 123.1934 | 76.7258 | 68.4357 | 68.3212 | 123.1934 | 123.2025 | 123.2391 | -55.1697 | -46.4081
5642.7812 | 123.4589 | -68.2526 | 54.9042 | -0.65254 | -0.01377 | -0.026938 | 0.0013522 | -0.0099633 | -0.0073593 | -0.0041528 | 0.018311 | 0.19226 | -0.26093 | 55.1559 | 54.9545 | 54.9408 | 54.8264 | 55.1559 | 54.9774 | 8.4915 | 67.9916 | -54.7119 | 68.2709 | 123.4085 | 0.050354 | 76.7441 | 0.073242 | 0.27924 | 123.0789 | 123.4085 | 123.2071 | 68.4448 | 68.2709 | 123.23 | 123.1934 | 76.7441 | 68.4448 | 68.2709 | 123.1934 | 123.2071 | 123.23 | -55.1651 | -46.4127
5643.7812 | 123.4406 | -68.2297 | 54.9088 | -0.15663 | -0.010566 | -0.028433 | 0.0028476 | -0.012527 | -0.0097091 | -0.003512 | 0.082397 | 0.20142 | -0.27924 | 55.1514 | 54.9454 | 54.9225 | 54.8538 | 55.1514 | 54.9866 | 8.4778 | 67.9504 | -54.7073 | 68.3121 | 123.381 | 0.036622 | 76.7075 | 0.07782 | 0.36163 | 123.0835 | 123.381 | 123.175 | 68.4311 | 68.3121 | 123.2162 | 123.1522 | 76.7075 | 68.4311 | 68.3121 | 123.1522 | 123.175 | 123.2162 | -55.188 | -46.431
5644.7812 | 123.4451 | -68.2388 | 54.8904 | -0.17952 | -0.011848 | -0.029715 | 0.0041292 | -0.010818 | -0.0067185 | -0.0047938 | 0.086975 | 0.19226 | -0.28839 | 55.1743 | 54.9545 | 54.9454 | 54.8309 | 55.1697 | 54.9957 | 8.4869 | 67.9504 | -54.6982 | 68.3258 | 123.4131 | 0.064087 | 76.7258 | 0.10529 | 0.37537 | 123.0698 | 123.4085 | 123.1934 | 68.4311 | 68.3258 | 123.2346 | 123.1842 | 76.7258 | 68.4311 | 68.3258 | 123.1842 | 123.1934 | 123.2346 | -55.1788 | -46.4035
5645.7656 | 123.3765 | -68.2434 | 54.9133 | -0.18715 | -0.014411 | -0.029501 | 0.0058382 | -0.010604 | -0.0092819 | -0.0032984 | 0.059509 | 0.23346 | -0.2655 | 55.1285 | 54.8996 | 54.8721 | 54.9179 | 55.101 | 55.0003 | 8.4778 | 67.9779 | -54.6799 | 68.3029 | 123.3719 | -0.013733 | 76.7212 | 0.086975 | 0.32501 | 123.1613 | 123.3444 | 123.143 | 68.4769 | 68.3029 | 123.2437 | 123.1155 | 76.7212 | 68.4769 | 68.3029 | 123.1155 | 123.143 | 123.2437 | -55.1788 | -46.4355
5646.7656 | 123.3948 | -68.2205 | 54.9408 | -0.21004 | -0.014197 | -0.03121 | 0.0030612 | -0.010177 | -0.0082137 | -0.0026574 | 0.082397 | 0.20599 | -0.27008 | 55.1559 | 54.9179 | 54.9042 | 54.8904 | 55.1239 | 55.014 | 8.4869 | 67.9504 | -54.7348 | 68.3029 | 123.3765 | -0.022888 | 76.7075 | 0.073242 | 0.35248 | 123.111 | 123.3444 | 123.1384 | 68.4265 | 68.3029 | 123.2346 | 123.1247 | 76.7075 | 68.4265 | 68.3029 | 123.1247 | 123.1384 | 123.2346 | -55.2109 | -46.4539
5647.7812 | 123.4451 | -68.2343 | 54.895 | -0.019302 | -0.013129 | -0.029501 | 0.0049838 | -0.013168 | -0.0077865 | -0.0043664 | 0.073242 | 0.18768 | -0.29755 | 55.188 | 54.9683 | 54.9545 | 54.8126 | 55.1651 | 54.9957 | 8.4824 | 67.9367 | -54.7073 | 68.3075 | 123.4222 | 0.073242 | 76.7166 | 0.10071 | 0.37079 | 123.0469 | 123.3994 | 123.2025 | 68.4219 | 68.3075 | 123.23 | 123.1888 | 76.7166 | 68.4219 | 68.3075 | 123.1888 | 123.2025 | 123.23 | -55.1926 | -46.4127
5648.7812 | 123.4589 | -68.2434 | 54.9179 | -0.04982 | -0.012488 | -0.031851 | 0.0011386 | -0.011245 | -0.0080001 | -0.001803 | 0.032043 | 0.19684 | -0.29297 | 55.1559 | 54.9179 | 54.9362 | 54.7943 | 55.1514 | 54.9637 | 8.4869 | 67.9504 | -54.7211 | 68.2755 | 123.3994 | 0 | 76.7303 | 0.045776 | 0.32501 | 123.0377 | 123.3948 | 123.1613 | 68.4402 | 68.2755 | 123.2071 | 123.1796 | 76.7303 | 68.4402 | 68.2755 | 123.1796 | 123.1613 | 123.2071 | -55.2109 | -46.431
5649.7812 | 123.4406 | -68.2251 | 54.9179 | -0.0040434 | -0.012275 | -0.029501 | 0.0041292 | -0.011459 | -0.0075729 | -0.0037256 | 0.004578 | 0.1831 | -0.29755 | 55.1605 | 54.9271 | 54.9179 | 54.7943 | 55.1285 | 54.9774 | 8.4869 | 67.9276 | -54.7348 | 68.2297 | 123.3856 | 0.009155 | 76.712 | 0.059509 | 0.30212 | 123.0194 | 123.3536 | 123.1522 | 68.4082 | 68.2297 | 123.2025 | 123.143 | 76.712 | 68.4082 | 68.2297 | 123.143 | 123.1522 | 123.2025 | -55.2155 | -46.431
5650.7812 | 123.4589 | -68.2114 | 54.8859 | 0.0035856 | -0.013557 | -0.030356 | -0.00099756 | -0.011459 | -0.0067185 | -0.0028712 | 0.050354 | 0.18768 | -0.28381 | 55.1834 | 54.9454 | 54.9271 | 54.8218 | 55.1651 | 54.982 | 8.4732 | 67.9276 | -54.6982 | 68.2617 | 123.3948 | 0.05951 | 76.6846 | 0.096131 | 0.33417 | 123.0331 | 123.3765 | 123.1567 | 68.399 | 68.2617 | 123.1934 | 123.1384 | 76.6846 | 68.399 | 68.2617 | 123.1384 | 123.1567 | 123.1934 | -55.1697 | -46.4127
5651.7812 | 123.4543 | -68.2343 | 54.8904 | -0.065079 | -0.01142 | -0.03057 | 0.002634 | -0.012313 | -0.0067185 | -0.0030848 | 0.041199 | 0.21973 | -0.28839 | 55.1788 | 54.9454 | 54.9271 | 54.8126 | 55.1422 | 55.0003 | 8.4824 | 67.9459 | -54.6707 | 68.2755 | 123.4131 | 0.054932 | 76.7166 | 0.10986 | 0.32959 | 123.0469 | 123.3765 | 123.1796 | 68.454 | 68.2755 | 123.2346 | 123.1613 | 76.7166 | 68.454 | 68.2755 | 123.1613 | 123.1796 | 123.2346 | -55.1788 | -46.4081
5652.7656 | 123.4497 | -68.2068 | 54.8813 | 0.17143 | -0.012275 | -0.030356 | 0.0032748 | -0.011672 | -0.010564 | -0.0041528 | 0.068665 | 0.19684 | -0.27924 | 55.2017 | 54.9591 | 54.9271 | 54.8126 | 55.1605 | 54.9728 | 8.4869 | 67.9276 | -54.6844 | 68.2755 | 123.4085 | 0.077819 | 76.6937 | 0.091552 | 0.3479 | 123.0194 | 123.3673 | 123.1659 | 68.4036 | 68.2755 | 123.1796 | 123.1338 | 76.6937 | 68.4036 | 68.2755 | 123.1338 | 123.1659 | 123.1796 | -55.1605 | -46.3943
5653.7656 | 123.4406 | -68.2297 | 54.8767 | -0.10323 | -0.010566 | -0.027579 | 0.0062656 | -0.011459 | -0.0082137 | -0.0013758 | -0.082397 | 0.1831 | -0.27466 | 55.22 | 54.9545 | 54.9133 | 54.8035 | 55.1376 | 54.9545 | 8.4824 | 67.955 | -54.6936 | 68.1473 | 123.4497 | 0.07782 | 76.712 | 0.07782 | 0.19226 | 123.0331 | 123.3673 | 123.1842 | 68.4128 | 68.1473 | 123.1842 | 123.143 | 76.712 | 68.4128 | 68.1473 | 123.143 | 123.1842 | 123.1842 | -55.1514 | -46.3943
5654.7812 | 123.4451 | -68.2114 | 54.8676 | -0.0040434 | -0.012061 | -0.029074 | 0.0011386 | -0.014663 | -0.0035141 | -0.0020166 | 0.027466 | 0.1831 | -0.29297 | 55.1559 | 54.9454 | 54.9271 | 54.8172 | 55.1559 | 54.9316 | 8.4824 | 67.9184 | -54.6844 | 68.2388 | 123.3673 | 0.07782 | 76.6937 | 0.064087 | 0.32043 | 123.0286 | 123.3673 | 123.1567 | 68.3945 | 68.2388 | 123.143 | 123.1384 | 76.6937 | 68.3945 | 68.2388 | 123.1384 | 123.1567 | 123.143 | -55.1605 | -46.3852
5655.7812 | 123.3856 | -68.2526 | 54.8996 | 0.1638 | -0.011634 | -0.026724 | 0.00071144 | -0.0121 | -0.0082137 | -0.0030848 | -0.013733 | 0.18768 | -0.28381 | 55.1193 | 54.9088 | 54.8721 | 54.808 | 55.0781 | 54.9728 | 8.4824 | 67.9688 | -54.7119 | 68.2388 | 123.3719 | 0.009155 | 76.7349 | 0.073242 | 0.27008 | 123.0606 | 123.3307 | 123.1613 | 68.4402 | 68.2388 | 123.2254 | 123.1247 | 76.7349 | 68.4402 | 68.2388 | 123.1247 | 123.1613 | 123.2254 | -55.1834 | -46.4172
5656.7812 | 123.3948 | -68.2617 | 54.8767 | -0.21004 | -0.012702 | -0.025443 | 0.00071144 | -0.010177 | -0.0073593 | -0.0032984 | -0.018311 | 0.17853 | -0.29297 | 55.101 | 54.8767 | 54.8584 | 54.8264 | 55.0827 | 54.9271 | 8.4824 | 67.9688 | -54.6982 | 68.2434 | 123.3627 | 0 | 76.7441 | 0.050354 | 0.27466 | 123.0881 | 123.3444 | 123.1384 | 68.4402 | 68.2434 | 123.1888 | 123.1201 | 76.7441 | 68.4402 | 68.2434 | 123.1201 | 123.1384 | 123.1888 | -55.1697 | -46.3943
5657.7812 | 123.4039 | -68.2617 | 54.8813 | 0.034104 | -0.011207 | -0.030997 | 0.0015658 | -0.011672 | -0.0062911 | -0.0020166 | -0.022888 | 0.19684 | -0.31586 | 55.1376 | 54.9042 | 54.8996 | 54.8126 | 55.0964 | 54.9271 | 8.4824 | 67.9459 | -54.6844 | 68.2388 | 123.3994 | 0.022888 | 76.7441 | 0.045776 | 0.29297 | 123.0743 | 123.3582 | 123.1659 | 68.4586 | 68.2388 | 123.1888 | 123.1613 | 76.7441 | 68.4586 | 68.2388 | 123.1613 | 123.1659 | 123.1888 | -55.1971 | -46.3989
5658.7812 | 123.4177 | -68.2434 | 54.9088 | 0.018845 | -0.012275 | -0.030783 | 0.0011386 | -0.011672 | -0.0058639 | -0.0028712 | -0.009155 | 0.16479 | -0.31586 | 55.1285 | 54.9133 | 54.8721 | 54.8126 | 55.0735 | 54.9591 | 8.4824 | 67.9276 | -54.744 | 68.2343 | 123.3719 | 0.004578 | 76.7258 | 0.050354 | 0.3067 | 123.056 | 123.317 | 123.1567 | 68.4082 | 68.2343 | 123.2025 | 123.1155 | 76.7258 | 68.4082 | 68.2343 | 123.1155 | 123.1567 | 123.2025 | -55.2246 | -46.4264
5659.7656 | 123.4543 | -68.2434 | 54.8996 | -0.072708 | -0.013557 | -0.029715 | -0.00014316 | -0.010818 | -0.0065047 | -0.0013758 | 0.050354 | 0.19226 | -0.29297 | 55.1743 | 54.9591 | 54.9316 | 54.7943 | 55.1559 | 54.9591 | 8.4824 | 67.9504 | -54.7073 | 68.2938 | 123.4177 | 0.059509 | 76.7258 | 0.059509 | 0.34332 | 123.0377 | 123.3994 | 123.2025 | 68.4357 | 68.2938 | 123.2025 | 123.175 | 76.7258 | 68.4357 | 68.2938 | 123.175 | 123.2025 | 123.2025 | -55.1926 | -46.4172
5660.7656 | 123.4406 | -68.2388 | 54.8904 | -0.04982 | -0.014625 | -0.027792 | 0.0024202 | -0.0121 | -0.0071457 | -0.0028712 | 0.032043 | 0.18768 | -0.28381 | 55.1697 | 54.9408 | 54.9225 | 54.808 | 55.1422 | 54.9225 | 8.4778 | 67.955 | -54.7028 | 68.2709 | 123.4085 | 0.050354 | 76.7166 | 0.032043 | 0.31586 | 123.0469 | 123.381 | 123.1796 | 68.4265 | 68.2709 | 123.1613 | 123.1613 | 76.7166 | 68.4265 | 68.2709 | 123.1613 | 123.1796 | 123.1613 | -55.1743 | -46.4127
5661.7812 | 123.4085 | -68.248 | 54.8859 | 0.087509 | -0.012275 | -0.029288 | 0.0024202 | -0.011886 | -0.0056503 | -0.0013758 | -0.022888 | 0.17853 | -0.29297 | 55.1376 | 54.8996 | 54.8721 | 54.7989 | 55.0735 | 54.9271 | 8.4778 | 67.955 | -54.7073 | 68.2251 | 123.3856 | 0.013733 | 76.7258 | 0.041199 | 0.27008 | 123.0469 | 123.3215 | 123.1476 | 68.4265 | 68.2251 | 123.175 | 123.1201 | 76.7258 | 68.4265 | 68.2251 | 123.1201 | 123.1476 | 123.175 | -55.1788 | -46.4081
5662.7812 | 123.3948 | -68.2571 | 54.8813 | 0.18669 | -0.011207 | -0.029929 | 0.0028476 | -0.013595 | -0.0058639 | -0.0043664 | -0.022888 | 0.12817 | -0.33875 | 55.1331 | 54.8904 | 54.8676 | 54.7852 | 55.0552 | 54.9271 | 8.4824 | 67.9184 | -54.7531 | 68.2343 | 123.3902 | 0.009155 | 76.7395 | 0.045776 | 0.31586 | 123.0423 | 123.3124 | 123.1476 | 68.3853 | 68.2343 | 123.1842 | 123.1247 | 76.7395 | 68.3853 | 68.2343 | 123.1247 | 123.1476 | 123.1842 | -55.22 | -46.3989
5663.7812 | 123.4268 | -68.2297 | 54.8904 | 0.20195 | -0.011207 | -0.026297 | 0.0015658 | -0.01274 | -0.0075729 | -0.0022302 | -0.036621 | 0.1236 | -0.3891 | 55.1102 | 54.8859 | 54.863 | 54.7852 | 55.0644 | 54.9316 | 8.4824 | 67.8406 | -54.7668 | 68.1931 | 123.3398 | -0.004578 | 76.712 | 0.041199 | 0.35248 | 123.0148 | 123.2941 | 123.1155 | 68.3533 | 68.1931 | 123.1613 | 123.0927 | 76.712 | 68.3533 | 68.1931 | 123.0927 | 123.1155 | 123.1613 | -55.2795 | -46.4081
5664.7812 | 123.3948 | -68.2388 | 54.8904 | 0.14854 | -0.012916 | -0.029288 | 0.0011386 | -0.0121 | -0.0067185 | -0.0030848 | -0.022888 | 0.13275 | -0.32044 | 55.1147 | 54.895 | 54.8813 | 54.7897 | 55.1788 | 54.9362 | 8.4824 | 67.9184 | -54.7577 | 68.2159 | 123.3536 | 0.004578 | 76.7212 | 0.045776 | 0.29755 | 123.0286 | 123.4177 | 123.1339 | 68.3716 | 68.2159 | 123.175 | 123.1201 | 76.7212 | 68.3716 | 68.2159 | 123.1201 | 123.1339 | 123.175 | -55.2109 | -46.4081
5665.7812 | 123.4085 | -68.2571 | 54.8767 | 0.18669 | -0.012275 | -0.026083 | 0.0013522 | -0.012527 | -0.0080001 | -0.0024438 | -0.022888 | 0.1236 | -0.35248 | 55.1239 | 54.895 | 54.8904 | 54.8035 | 55.0598 | 54.9042 | 8.4824 | 67.9047 | -54.7531 | 68.2343 | 123.381 | 0.018311 | 76.7395 | 0.027466 | 0.32959 | 123.0606 | 123.317 | 123.1522 | 68.3807 | 68.2343 | 123.1613 | 123.1476 | 76.7395 | 68.3807 | 68.2343 | 123.1476 | 123.1522 | 123.1613 | -55.2292 | -46.3943
5666.7812 | 123.4177 | -68.2709 | 54.8721 | 0.10277 | -0.010993 | -0.026938 | 0.0017794 | -0.011459 | -0.0062911 | -0.0022302 | -0.23346 | 0.15564 | -0.32044 | 55.1376 | 54.8721 | 54.8859 | 54.7989 | 55.0598 | 54.9042 | 8.4778 | 67.9504 | -54.7165 | 68.0374 | 123.4085 | 0 | 76.7487 | 0.032044 | 0.086976 | 123.0698 | 123.3307 | 123.143 | 68.4265 | 68.0374 | 123.175 | 123.1567 | 76.7487 | 68.4265 | 68.0374 | 123.1567 | 123.143 | 123.175 | -55.1926 | -46.3943
5667.7656 | 123.3994 | -68.2571 | 54.8996 | -0.057449 | -0.012702 | -0.027365 | 0.00028404 | -0.012527 | -0.0071457 | -0.0037256 | -0.045776 | 0.16937 | -0.28381 | 55.1239 | 54.895 | 54.8813 | 54.8264 | 55.0781 | 54.895 | 8.4824 | 67.9733 | -54.7302 | 68.2114 | 123.381 | -0.004577 | 76.7395 | -0.004577 | 0.23804 | 123.0835 | 123.3353 | 123.1522 | 68.4265 | 68.2114 | 123.1522 | 123.1384 | 76.7395 | 68.4265 | 68.2114 | 123.1384 | 123.1522 | 123.1522 | -55.1834 | -46.4172
5668.7812 | 123.3994 | -68.2571 | 54.8721 | 0.20195 | -0.012275 | -0.02117 | 0.00028404 | -0.0121 | -0.0071457 | -0.0037256 | -0.032043 | 0.1236 | -0.35706 | 55.1102 | 54.895 | 54.8859 | 54.8035 | 55.0735 | 54.9316 | 8.4778 | 67.9001 | -54.7485 | 68.2251 | 123.3673 | 0.022889 | 76.7349 | 0.05951 | 0.32501 | 123.0606 | 123.3307 | 123.1522 | 68.3807 | 68.2251 | 123.1888 | 123.143 | 76.7349 | 68.3807 | 68.2251 | 123.143 | 123.1522 | 123.1888 | -55.2292 | -46.3943
5669.7812 | 123.4543 | -68.248 | 54.8538 | 0.23247 | -0.011634 | -0.025656 | 0.0051974 | -0.0099633 | -0.0060775 | -0.0028712 | 0.004578 | 0.1236 | -0.34332 | 55.1651 | 54.9271 | 54.9271 | 54.7256 | 55.0827 | 54.8859 | 8.4824 | 67.9047 | -54.7302 | 68.2526 | 123.4131 | 0.073242 | 76.7303 | 0.032043 | 0.3479 | 122.9736 | 123.3307 | 123.175 | 68.3716 | 68.2526 | 123.1338 | 123.175 | 76.7303 | 68.3716 | 68.2526 | 123.175 | 123.175 | 123.1338 | -55.1971 | -46.3715
5670.7812 | 123.4039 | -68.2571 | 54.8492 | 0.2401 | -0.012061 | -0.026938 | 0.0051974 | -0.011459 | -0.0062911 | -0.0024438 | -0.013733 | 0.091553 | -0.3479 | 55.1468 | 54.9088 | 54.9179 | 54.7531 | 55.0827 | 54.8996 | 8.4778 | 67.9092 | -54.7577 | 68.2434 | 123.4039 | 0.059509 | 76.7349 | 0.050354 | 0.33417 | 123.0103 | 123.3398 | 123.1659 | 68.3487 | 68.2434 | 123.1567 | 123.175 | 76.7349 | 68.3487 | 68.2434 | 123.175 | 123.1659 | 123.1567 | -55.1971 | -46.3715
5671.7656 | 123.4222 | -68.2571 | 54.8584 | 0.21721 | -0.01142 | -0.030356 | 0.0056246 | -0.012313 | -0.0073593 | -0.0047938 | 0.10529 | 0.12817 | -0.37537 | 55.1651 | 54.95 | 54.9362 | 54.7073 | 55.1102 | 54.9133 | 8.4869 | 67.8818 | -54.7302 | 68.3624 | 123.4222 | 0.091553 | 76.7441 | 0.054932 | 0.48065 | 122.9645 | 123.3673 | 123.2071 | 68.3853 | 68.3624 | 123.1705 | 123.1934 | 76.7441 | 68.3853 | 68.3624 | 123.1934 | 123.2071 | 123.1705 | -55.2338 | -46.3715
5672.7812 | 123.4543 | -68.248 | 54.8401 | 0.22484 | -0.010352 | -0.027152 | 0.0064792 | -0.0095361 | -0.0080001 | -0.0039392 | 0.018311 | 0.14191 | -0.32501 | 55.1468 | 54.9179 | 54.9133 | 54.7302 | 55.0919 | 54.8767 | 8.4778 | 67.923 | -54.6982 | 68.2663 | 123.3948 | 0.07782 | 76.7258 | 0.036621 | 0.34332 | 122.9782 | 123.3398 | 123.1659 | 68.3899 | 68.2663 | 123.1247 | 123.1613 | 76.7258 | 68.3899 | 68.2663 | 123.1613 | 123.1659 | 123.1247 | -55.1651 | -46.3623
5673.7656 | 123.3994 | -68.2755 | 54.863 | 0.27061 | -0.0094976 | -0.023093 | 0.0066928 | -0.0086817 | -0.0062911 | -0.003512 | -0.018311 | 0.18768 | -0.35706 | 55.101 | 54.8767 | 54.8584 | 54.7989 | 55.0278 | 54.9316 | 8.4824 | 67.9184 | -54.6753 | 68.2571 | 123.3765 | 0.013733 | 76.7578 | 0.068665 | 0.33874 | 123.0743 | 123.3032 | 123.1522 | 68.4631 | 68.2571 | 123.2071 | 123.1338 | 76.7578 | 68.4631 | 68.2571 | 123.1338 | 123.1522 | 123.2071 | -55.22 | -46.3806
5674.7656 | 123.4177 | -68.28 | 54.863 | 0.22484 | -0.0094976 | -0.026724 | 0.0039156 | -0.010177 | -0.0056503 | -0.0030848 | -0.013733 | 0.11902 | -0.35248 | 55.1285 | 54.9133 | 54.9042 | 54.7394 | 55.0781 | 54.9225 | 8.4824 | 67.9276 | -54.744 | 68.2663 | 123.4085 | 0.050354 | 76.7624 | 0.059509 | 0.33875 | 123.0194 | 123.3582 | 123.1934 | 68.399 | 68.2663 | 123.2025 | 123.1842 | 76.7624 | 68.399 | 68.2663 | 123.1842 | 123.1934 | 123.2025 | -55.2155 | -46.3806
5675.7812 | 123.4497 | -68.248 | 54.8538 | 0.17143 | -0.010139 | -0.025443 | 0.0051974 | -0.010177 | -0.0054367 | -0.0020166 | 0.018311 | 0.10529 | -0.34332 | 55.1468 | 54.9271 | 54.9179 | 54.744 | 55.1102 | 54.9271 | 8.4824 | 67.9047 | -54.7485 | 68.2663 | 123.3948 | 0.073242 | 76.7303 | 0.073242 | 0.36163 | 122.9919 | 123.3582 | 123.175 | 68.3533 | 68.2663 | 123.175 | 123.1659 | 76.7303 | 68.3533 | 68.2663 | 123.1659 | 123.175 | 123.175 | -55.1971 | -46.3715
5676.7812 | 123.3856 | -68.2938 | 54.8721 | 0.24773 | -0.0084296 | -0.022879 | 0.0092562 | -0.0091089 | -0.0075729 | -0.0024438 | -0.032043 | 0.17853 | -0.38452 | 55.0827 | 54.8721 | 54.8492 | 54.8172 | 55.0003 | 54.9408 | 8.4824 | 67.9092 | -54.6936 | 68.2617 | 123.3765 | 0 | 76.7761 | 0.068665 | 0.35248 | 123.111 | 123.2941 | 123.1659 | 68.4723 | 68.2617 | 123.2346 | 123.143 | 76.7761 | 68.4723 | 68.2617 | 123.143 | 123.1659 | 123.2346 | -55.2567 | -46.3898
5677.7812 | 123.4314 | -68.2663 | 54.8584 | 0.26299 | -0.011634 | -0.023947 | 0.0079744 | -0.0078271 | -0.0077865 | 0.00011961 | -0.004578 | 0.14191 | -0.35248 | 55.1285 | 54.8996 | 54.8904 | 54.7623 | 55.0461 | 54.9179 | 8.4824 | 67.9138 | -54.7165 | 68.2617 | 123.3948 | 0.041199 | 76.7487 | 0.05951 | 0.3479 | 123.0286 | 123.3124 | 123.1659 | 68.4082 | 68.2617 | 123.1842 | 123.1567 | 76.7487 | 68.4082 | 68.2617 | 123.1567 | 123.1659 | 123.1842 | -55.2109 | -46.376
5678.7812 | 123.4131 | -68.2892 | 54.8767 | 0.25536 | -0.0094976 | -0.017111 | 0.008829 | -0.0067591 | -0.0092819 | -0.0013758 | -0.004578 | 0.17395 | -0.35706 | 55.0873 | 54.8584 | 54.8584 | 54.8218 | 55.0323 | 54.9454 | 8.4824 | 67.9321 | -54.7028 | 68.2846 | 123.3765 | -0.018311 | 76.7715 | 0.068665 | 0.35248 | 123.111 | 123.3215 | 123.1476 | 68.4631 | 68.2846 | 123.2346 | 123.1476 | 76.7715 | 68.4631 | 68.2846 | 123.1476 | 123.1476 | 123.2346 | -55.2338 | -46.3943
5679.7812 | 123.4039 | -68.2663 | 54.8126 | 0.24773 | -0.010139 | -0.02587 | 0.0062656 | -0.0069727 | -0.0075729 | -0.0011622 | -0.009155 | 0.14191 | -0.35248 | 55.1376 | 54.8996 | 54.9133 | 54.7302 | 55.069 | 54.9316 | 8.4824 | 67.9138 | -54.6707 | 68.2571 | 123.4039 | 0.086975 | 76.7487 | 0.11902 | 0.34332 | 122.9965 | 123.3353 | 123.1659 | 68.4082 | 68.2571 | 123.1979 | 123.1796 | 76.7487 | 68.4082 | 68.2571 | 123.1796 | 123.1659 | 123.1979 | -55.1651 | -46.3303
5680.7656 | 123.436 | -68.2617 | 54.8584 | 0.24773 | -0.01142 | -0.02587 | 0.0060518 | -0.0093225 | -0.0015915 | -0.0011622 | 0.032043 | 0.13275 | -0.35248 | 54.9683 | 54.9957 | 54.9911 | 54.8447 | 55.069 | 54.9271 | 8.4824 | 67.9092 | -54.7256 | 68.2938 | 123.23 | 0.13733 | 76.7441 | 0.068665 | 0.38452 | 123.1064 | 123.3307 | 123.2574 | 68.3945 | 68.2938 | 123.1888 | 123.2529 | 76.7441 | 68.3945 | 68.2938 | 123.2529 | 123.2574 | 123.1888 | -55.2109 | -46.376
5681.7812 | 123.3948 | -68.2663 | 54.8721 | 0.12566 | -0.011848 | -0.028647 | 0.00049764 | -0.0099633 | -0.0077865 | -0.0026574 | -0.032043 | 0.16022 | -0.33417 | 55.0552 | 54.8859 | 54.9088 | 54.8264 | 55.0827 | 54.9591 | 8.4824 | 67.9321 | -54.7119 | 68.2343 | 123.3215 | 0.013733 | 76.7487 | 0.086975 | 0.30212 | 123.0927 | 123.349 | 123.1522 | 68.4265 | 68.2343 | 123.2254 | 123.175 | 76.7487 | 68.4265 | 68.2343 | 123.175 | 123.1522 | 123.2254 | -55.2063 | -46.3898
5682.7812 | 123.3307 | -68.2846 | 54.9088 | 3.0325 | -0.0090704 | -0.022665 | 0.0086154 | -0.0097497 | -0.0058639 | -0.0024438 | 0.045776 | 0.17395 | -0.36621 | 55.0644 | 54.8309 | 54.7943 | 54.8813 | 54.9728 | 54.9591 | 8.4824 | 67.9184 | -54.7348 | 68.3304 | 123.349 | -0.077819 | 76.767 | 0.050354 | 0.41199 | 123.1659 | 123.2574 | 123.1155 | 68.4586 | 68.3304 | 123.2437 | 123.0789 | 76.767 | 68.4586 | 68.3304 | 123.0789 | 123.1155 | 123.2437 | -55.275 | -46.4264
5683.7812 | 123.3353 | -68.2983 | 54.895 | 0.14854 | -0.008216 | -0.024802 | 0.0086154 | -0.0078271 | -0.0082137 | -0.0020166 | -0.041199 | 0.21515 | -0.35248 | 55.0415 | 54.8218 | 54.8264 | 54.8996 | 54.9683 | 54.9957 | 8.4869 | 67.9459 | -54.6799 | 68.2571 | 123.3398 | -0.073243 | 76.7853 | 0.10071 | 0.31128 | 123.1979 | 123.2666 | 123.1201 | 68.5135 | 68.2571 | 123.2941 | 123.1247 | 76.7853 | 68.5135 | 68.2571 | 123.1247 | 123.1201 | 123.2941 | -55.2475 | -46.4081
5684.7812 | 123.3261 | -68.3121 | 54.9133 | -0.2787 | -0.011848 | -0.02352 | 0.010324 | -0.0080407 | -0.0060775 | -0.0030848 | 0.009155 | 0.20142 | -0.37537 | 55.0415 | 54.8264 | 54.8126 | 54.9271 | 54.9683 | 54.9683 | 8.4778 | 67.9367 | -54.7119 | 68.3212 | 123.3536 | -0.086975 | 76.7899 | 0.054932 | 0.38452 | 123.2391 | 123.2803 | 123.1384 | 68.5135 | 68.3212 | 123.2803 | 123.1247 | 76.7899 | 68.5135 | 68.3212 | 123.1247 | 123.1384 | 123.2803 | -55.2887 | -46.4355
5685.7812 | 123.3307 | -68.2892 | 54.9179 | 0.087509 | -0.0071478 | -0.021811 | 0.010111 | -0.0073999 | -0.0062911 | 0.0018286 | -0.059509 | 0.21973 | -0.37994 | 54.6661 | 54.6341 | 54.9774 | 54.9362 | 55.0873 | 55.014 | 8.4732 | 67.9092 | -54.6982 | 68.2297 | 122.9553 | -0.28381 | 76.7624 | 0.09613 | 0.32044 | 123.2254 | 123.3765 | 122.9233 | 68.5089 | 68.2297 | 123.3032 | 123.2666 | 76.7624 | 68.5089 | 68.2297 | 123.2666 | 122.9233 | 123.3032 | -55.2979 | -46.4447
5686.7812 | 123.4314 | -68.2159 | 54.8767 | -0.034561 | -0.013557 | -0.023734 | -0.0022794 | -0.0097497 | -0.0082137 | -0.0028712 | 0.009155 | 0.17853 | -0.29755 | 55.1147 | 54.9591 | 54.95 | 54.8264 | 55.1468 | 54.9637 | 8.4869 | 67.9184 | -54.6982 | 68.2251 | 123.3307 | 0.082397 | 76.7029 | 0.086975 | 0.3067 | 123.0423 | 123.3627 | 123.175 | 68.3945 | 68.2251 | 123.1796 | 123.1659 | 76.7029 | 68.3945 | 68.2251 | 123.1659 | 123.175 | 123.1796 | -55.1743 | -46.3898
5687.7656 | 123.3307 | -68.2983 | 54.8859 | 0.21721 | -0.007575 | -0.02352 | 0.0084018 | -0.0088953 | -0.0062911 | -0.0032984 | -0.036621 | 0.22888 | -0.36621 | 55.0369 | 54.8218 | 54.7989 | 54.9042 | 54.9637 | 54.9591 | 8.4778 | 67.9321 | -54.657 | 68.2617 | 123.3353 | -0.064087 | 76.7761 | 0.073242 | 0.32959 | 123.2025 | 123.262 | 123.1201 | 68.5272 | 68.2617 | 123.2574 | 123.0972 | 76.7761 | 68.5272 | 68.2617 | 123.0972 | 123.1201 | 123.2574 | -55.2521 | -46.4081
5688.7812 | 123.3124 | -68.3075 | 54.8996 | 0.14092 | -0.009925 | -0.023947 | 0.008829 | -0.0080407 | -0.0088547 | -0.0028712 | -0.022888 | 0.22888 | -0.33417 | 55.0278 | 54.8035 | 54.7852 | 54.9454 | 54.9728 | 55.0049 | 8.4686 | 67.9733 | -54.6707 | 68.2846 | 123.3353 | -0.09613 | 76.7761 | 0.10529 | 0.31128 | 123.2529 | 123.2803 | 123.111 | 68.5364 | 68.2846 | 123.3124 | 123.0927 | 76.7761 | 68.5364 | 68.2846 | 123.0927 | 123.111 | 123.3124 | -55.2338 | -46.431
5689.7812 | 123.3582 | -68.2755 | 54.9133 | -0.0040434 | -0.008216 | -0.027792 | 0.0081882 | -0.0086817 | -0.0075729 | -0.0026574 | 0.050354 | 0.22888 | -0.31586 | 55.069 | 54.8676 | 54.8401 | 54.9133 | 55.0323 | 55.014 | 8.4824 | 67.9596 | -54.6844 | 68.3258 | 123.3444 | -0.045776 | 76.7578 | 0.10071 | 0.36621 | 123.1888 | 123.3078 | 123.143 | 68.5043 | 68.3258 | 123.2895 | 123.1155 | 76.7578 | 68.5043 | 68.3258 | 123.1155 | 123.143 | 123.2895 | -55.2292 | -46.431
5690.7812 | 123.3444 | -68.2709 | 54.8904 | -0.25581 | -0.0086432 | -0.025656 | 0.0081882 | -0.0069727 | -0.0067185 | -0.0032984 | 0.064087 | 0.25635 | -0.29297 | 55.0964 | 54.8767 | 54.8767 | 54.9133 | 55.0552 | 55.0186 | 8.4869 | 67.9779 | -54.6341 | 68.335 | 123.3673 | -0.013733 | 76.7578 | 0.12817 | 0.35706 | 123.1842 | 123.3261 | 123.1476 | 68.5272 | 68.335 | 123.2895 | 123.1476 | 76.7578 | 68.5272 | 68.335 | 123.1476 | 123.1476 | 123.2895 | -55.1834 | -46.4035
5691.7812 | 123.3719 | -68.2983 | 54.8676 | 0.2401 | -0.0088568 | -0.024374 | 0.0045566 | -0.0067591 | -0.0060775 | -0.0026574 | -0.054932 | 0.19226 | -0.37079 | 55.0369 | 54.8401 | 54.8126 | 54.8813 | 55.0003 | 55.0049 | 8.4824 | 67.9276 | -54.6753 | 68.2434 | 123.3353 | -0.027466 | 76.7807 | 0.13733 | 0.31586 | 123.1796 | 123.2986 | 123.1384 | 68.4906 | 68.2434 | 123.3032 | 123.111 | 76.7807 | 68.4906 | 68.2434 | 123.111 | 123.1384 | 123.3032 | -55.2383 | -46.3852
5692.7812 | 123.3673 | -68.2709 | 54.9179 | -0.080337 | -0.0086432 | -0.025015 | 0.0090426 | -0.0050501 | -0.0062911 | -0.00052119 | 0.054932 | 0.2243 | -0.32044 | 55.0919 | 54.8721 | 54.8584 | 54.9225 | 55.0507 | 55.014 | 8.4778 | 67.9504 | -54.6936 | 68.3258 | 123.3627 | -0.045777 | 76.7487 | 0.09613 | 0.37537 | 123.1934 | 123.3215 | 123.143 | 68.4952 | 68.3258 | 123.2849 | 123.1293 | 76.7487 | 68.4952 | 68.3258 | 123.1293 | 123.143 | 123.2849 | -55.2383 | -46.4401
5693.7656 | 123.3307 | -68.3075 | 54.9133 | 0.087509 | -0.009284 | -0.020956 | 0.0077608 | -0.0071863 | -0.010777 | -0.0013758 | 0 | 0.21057 | -0.33417 | 55.0461 | 54.8309 | 54.8264 | 54.9316 | 54.982 | 55.0049 | 8.4824 | 67.9733 | -54.7028 | 68.3075 | 123.3536 | -0.082397 | 76.7899 | 0.091553 | 0.33417 | 123.2391 | 123.2895 | 123.1384 | 68.5181 | 68.3075 | 123.3124 | 123.1338 | 76.7899 | 68.5181 | 68.3075 | 123.1338 | 123.1384 | 123.3124 | -55.2475 | -46.431
5694.7812 | 123.3536 | -68.2709 | 54.895 | -0.019302 | -0.0084296 | -0.023734 | 0.0069064 | -0.0061181 | -0.0067185 | -0.0013758 | 0.054932 | 0.2243 | -0.32959 | 55.0735 | 54.8676 | 54.8584 | 54.9179 | 55.0415 | 55.014 | 8.4686 | 67.9413 | -54.6707 | 68.3258 | 123.3444 | -0.027466 | 76.7395 | 0.11902 | 0.38452 | 123.1888 | 123.3124 | 123.1384 | 68.4952 | 68.3258 | 123.2849 | 123.1293 | 76.7395 | 68.4952 | 68.3258 | 123.1293 | 123.1384 | 123.2849 | -55.2246 | -46.4264
5695.7969 | 123.3582 | -68.2938 | 54.9225 | -0.149 | -0.01142 | -0.022879 | 0.004343 | -0.0059045 | -0.0080001 | -0.0026574 | 0.022888 | 0.2655 | -0.3067 | 55.069 | 54.8813 | 54.8401 | 54.9774 | 55.0552 | 55.0598 | 8.4869 | 67.9871 | -54.657 | 68.3166 | 123.3627 | -0.041198 | 76.7807 | 0.13733 | 0.32959 | 123.2712 | 123.349 | 123.175 | 68.5593 | 68.3166 | 123.3536 | 123.1338 | 76.7807 | 68.5593 | 68.3166 | 123.1338 | 123.175 | 123.3536 | -55.2292 | -46.4355
5696.7812 | 123.4131 | -68.248 | 54.895 | 0.15617 | -0.011207 | -0.029501 | 0.00028404 | -0.0073999 | -0.0060775 | -0.00073479 | -0.027466 | 0.17853 | -0.32501 | 55.0644 | 54.8813 | 54.8813 | 54.8218 | 55.0827 | 54.9637 | 8.4824 | 67.923 | -54.7165 | 68.2205 | 123.3124 | -0.013733 | 76.7303 | 0.068664 | 0.29755 | 123.0698 | 123.3307 | 123.1293 | 68.4265 | 68.2205 | 123.2117 | 123.1293 | 76.7303 | 68.4265 | 68.2205 | 123.1293 | 123.1293 | 123.2117 | -55.22 | -46.4127
5697.7812 | 123.3582 | -68.2846 | 54.9408 | -0.14137 | -0.0084296 | -0.025229 | 0.0060518 | -0.0078271 | -0.0077865 | -0.0024438 | 0.036621 | 0.28839 | -0.28839 | 55.0735 | 54.8676 | 54.8355 | 54.9957 | 55.0552 | 55.014 | 8.4778 | 67.9962 | -54.6524 | 68.3212 | 123.3582 | -0.073242 | 76.7624 | 0.073242 | 0.32501 | 123.2803 | 123.3398 | 123.1522 | 68.573 | 68.3212 | 123.2986 | 123.1201 | 76.7624 | 68.573 | 68.3212 | 123.1201 | 123.1522 | 123.2986 | -55.2292 | -46.463
5698.7812 | 123.3719 | -68.248 | 54.9225 | -0.149 | -0.009925 | -0.028647 | 0.0098972 | -0.0084681 | -0.0062911 | -0.0026574 | 0.059509 | 0.26093 | -0.27924 | 55.1056 | 54.8676 | 54.8538 | 54.9545 | 55.0598 | 55.0049 | 8.4732 | 67.9688 | -54.6616 | 68.3075 | 123.3536 | -0.054931 | 76.7212 | 0.082398 | 0.33874 | 123.2025 | 123.3078 | 123.1155 | 68.5089 | 68.3075 | 123.2529 | 123.1018 | 76.7212 | 68.5089 | 68.3075 | 123.1018 | 123.1155 | 123.2529 | -55.2017 | -46.4493
5699.7812 | 123.3673 | -68.3075 | 54.9454 | -0.149 | -0.010779 | -0.025229 | 0.0039156 | -0.0082545 | -0.0065047 | -0.0032984 | 0.022888 | 0.28381 | -0.29755 | 55.0781 | 54.8538 | 54.8355 | 54.9774 | 55.0781 | 55.0415 | 8.4824 | 68.0099 | -54.6616 | 68.3304 | 123.3856 | -0.091553 | 76.7899 | 0.09613 | 0.32043 | 123.2849 | 123.3856 | 123.1613 | 68.5913 | 68.3304 | 123.349 | 123.143 | 76.7899 | 68.5913 | 68.3304 | 123.143 | 123.1613 | 123.349 | -55.2429 | -46.463
5700.7656 | 123.3902 | -68.2571 | 54.9271 | -0.057449 | -0.0094976 | -0.028647 | 0.011179 | -0.0093225 | -0.0088547 | -0.0024438 | 0.045776 | 0.25635 | -0.31128 | 55.1147 | 54.895 | 54.9179 | 54.8721 | 55.0919 | 55.0049 | 8.4869 | 67.9459 | -54.6707 | 68.3029 | 123.3719 | -0.032043 | 76.7441 | 0.07782 | 0.35705 | 123.1293 | 123.349 | 123.1522 | 68.5135 | 68.3029 | 123.262 | 123.175 | 76.7441 | 68.5135 | 68.3029 | 123.175 | 123.1522 | 123.262 | -55.2383 | -46.4401
5701.7656 | 123.381 | -68.2755 | 54.9088 | -0.095596 | -0.009284 | -0.023093 | 0.004343 | -0.0078271 | -0.0069321 | -0.0039392 | 0.059509 | 0.24261 | -0.3067 | 55.1056 | 54.8859 | 54.8401 | 54.9271 | 55.0598 | 55.0323 | 8.4824 | 67.9688 | -54.6661 | 68.335 | 123.381 | -0.022888 | 76.7578 | 0.1236 | 0.36621 | 123.2025 | 123.3353 | 123.1613 | 68.5181 | 68.335 | 123.3078 | 123.1155 | 76.7578 | 68.5181 | 68.335 | 123.1155 | 123.1613 | 123.3078 | -55.2155 | -46.4264
5702.7812 | 123.3627 | -68.2846 | 54.8996 | -0.087967 | -0.0094976 | -0.028647 | 0.0064792 | -0.0091089 | -0.0071457 | -0.00458 | 0.059509 | 0.25635 | -0.30212 | 55.0873 | 54.8767 | 54.863 | 54.9362 | 55.0781 | 55.0049 | 8.4869 | 67.9825 | -54.6432 | 68.3441 | 123.3719 | -0.022888 | 76.7715 | 0.10529 | 0.36163 | 123.2208 | 123.3627 | 123.1613 | 68.541 | 68.3441 | 123.2895 | 123.1476 | 76.7715 | 68.541 | 68.3441 | 123.1476 | 123.1613 | 123.2895 | -55.2017 | -46.4127
5703.7812 | 123.2895 | -68.28 | 54.9362 | -0.18715 | -0.010139 | -0.030142 | 0.0039156 | -0.0084681 | -0.0075729 | -0.0032984 | 0.027466 | 0.27924 | -0.2655 | 55.0552 | 54.8676 | 54.8126 | 55.0049 | 55.1147 | 55.0415 | 8.4824 | 68.0145 | -54.657 | 68.3075 | 123.3353 | -0.068664 | 76.7624 | 0.10529 | 0.29297 | 123.2849 | 123.3948 | 123.1476 | 68.5593 | 68.3075 | 123.3215 | 123.0927 | 76.7624 | 68.5593 | 68.3075 | 123.0927 | 123.1476 | 123.3215 | -55.2017 | -46.4539
5704.7812 | 123.3307 | -68.2571 | 54.9271 | 0.07988 | -0.0097114 | -0.031424 | 0.002634 | -0.0080407 | -0.0084273 | -0.001803 | 0.009155 | 0.31586 | -0.24261 | 55.0735 | 54.863 | 54.8172 | 55.0095 | 55.0415 | 55.0323 | 8.4824 | 68.0145 | -54.6112 | 68.2663 | 123.3307 | -0.064087 | 76.7395 | 0.10529 | 0.25177 | 123.2666 | 123.2986 | 123.1201 | 68.573 | 68.2663 | 123.2895 | 123.0743 | 76.7395 | 68.573 | 68.2663 | 123.0743 | 123.1201 | 123.2895 | -55.1697 | -46.4447
5705.7812 | 123.349 | -68.2892 | 54.9271 | -0.43129 | -0.010993 | -0.027792 | 0.0034884 | -0.010177 | -0.0086411 | -0.0032984 | 0 | 0.27924 | -0.27466 | 55.0644 | 54.7211 | 54.9088 | 55.069 | 54.8767 | 55.0735 | 8.4824 | 68.0145 | -54.6478 | 68.2892 | 123.3536 | -0.20599 | 76.7715 | 0.14648 | 0.27466 | 123.3582 | 123.1659 | 123.0103 | 68.5684 | 68.2892 | 123.3627 | 123.1979 | 76.7715 | 68.5684 | 68.2892 | 123.1979 | 123.0103 | 123.3627 | -55.2017 | -46.4447
5706.7812 | 123.3353 | -68.2663 | 54.9362 | -0.18715 | -0.01142 | -0.029929 | 0.0015658 | -0.010391 | -0.0080001 | -0.003512 | 0.041199 | 0.21973 | -0.27924 | 55.0644 | 54.8676 | 54.8355 | 54.9545 | 55.101 | 55.0186 | 8.4824 | 67.9871 | -54.7165 | 68.3075 | 123.3307 | -0.068664 | 76.7487 | 0.082398 | 0.32043 | 123.2208 | 123.3673 | 123.1338 | 68.486 | 68.3075 | 123.2849 | 123.1018 | 76.7487 | 68.486 | 68.3075 | 123.1018 | 123.1338 | 123.2849 | -55.2155 | -46.4539
5707.7656 | 123.3353 | -68.2938 | 54.9408 | -0.14137 | -0.010993 | -0.023734 | 0.005411 | -0.011459 | -0.0080001 | -0.0011622 | 0.022888 | 0.25635 | -0.31128 | 55.0644 | 54.8401 | 54.8035 | 55.0003 | 55.0323 | 55.0278 | 8.4824 | 67.9825 | -54.6844 | 68.3166 | 123.3582 | -0.10071 | 76.7761 | 0.086975 | 0.33417 | 123.2941 | 123.3261 | 123.1338 | 68.5501 | 68.3166 | 123.3215 | 123.0972 | 76.7761 | 68.5501 | 68.3166 | 123.0972 | 123.1338 | 123.3215 | -55.2521 | -46.4584
5708.7656 | 123.3444 | -68.2617 | 54.9179 | 0.43846 | -0.012061 | -0.030142 | 0.0034884 | -0.0097497 | -0.0052231 | -0.0037256 | -0.027466 | 0.33875 | -0.24719 | 55.0873 | 54.8584 | 54.8218 | 54.9957 | 55.0369 | 55.014 | 8.4869 | 68.0145 | -54.5792 | 68.2343 | 123.349 | -0.05951 | 76.7487 | 0.09613 | 0.21973 | 123.2574 | 123.2986 | 123.1201 | 68.6005 | 68.2343 | 123.2758 | 123.0835 | 76.7487 | 68.6005 | 68.2343 | 123.0835 | 123.1201 | 123.2758 | -55.1651 | -46.431
5709.7812 | 123.3673 | -68.2526 | 54.9225 | -0.21004 | -0.012275 | -0.029074 | 0.001993 | -0.012527 | -0.0082137 | -0.00458 | 0.050354 | 0.24261 | -0.29297 | 55.1056 | 54.895 | 54.863 | 54.9362 | 55.0873 | 55.0186 | 8.4869 | 67.9596 | -54.6799 | 68.3029 | 123.3582 | -0.027465 | 76.7395 | 0.096131 | 0.34332 | 123.1888 | 123.3398 | 123.1476 | 68.4952 | 68.3029 | 123.2712 | 123.1155 | 76.7395 | 68.4952 | 68.3029 | 123.1155 | 123.1476 | 123.2712 | -55.2155 | -46.4355
5710.7812 | 123.4451 | -68.2297 | 54.8813 | -0.14137 | -0.016974 | -0.028861 | 7.0444e-05 | -0.010391 | -0.0060775 | -0.003512 | 0.07782 | 0.20142 | -0.29297 | 55.1514 | 54.95 | 54.9225 | 54.8309 | 55.1559 | 54.982 | 8.4824 | 67.9367 | -54.6799 | 68.3075 | 123.381 | 0.068664 | 76.712 | 0.10071 | 0.37079 | 123.0606 | 123.3856 | 123.1796 | 68.4311 | 68.3075 | 123.2117 | 123.1522 | 76.712 | 68.4311 | 68.3075 | 123.1522 | 123.1796 | 123.2117 | -55.1743 | -46.3989
5711.7812 | 123.4406 | -68.2434 | 54.9042 | -0.13374 | -0.013557 | -0.02587 | 0.001993 | -0.013381 | -0.0050095 | -0.0032984 | 0.07782 | 0.19684 | -0.27924 | 55.1605 | 54.95 | 54.9088 | 54.863 | 55.1468 | 54.9728 | 8.4824 | 67.9642 | -54.7073 | 68.3212 | 123.4039 | 0.045776 | 76.7258 | 0.068664 | 0.35706 | 123.1064 | 123.3902 | 123.1934 | 68.4402 | 68.3212 | 123.2162 | 123.1522 | 76.7258 | 68.4402 | 68.3212 | 123.1522 | 123.1934 | 123.2162 | -55.1834 | -46.4218
5712.7812 | 123.4589 | -68.2434 | 54.8996 | -0.11085 | -0.013129 | -0.033987 | 0.0022066 | -0.012313 | -0.0092819 | -0.0028712 | 0.07782 | 0.21515 | -0.28839 | 55.1468 | 54.9454 | 54.9133 | 54.8355 | 55.1605 | 54.9866 | 8.4915 | 67.955 | -54.6844 | 68.3212 | 123.3902 | 0.045777 | 76.7349 | 0.086975 | 0.36621 | 123.0789 | 123.4039 | 123.1888 | 68.4586 | 68.3212 | 123.23 | 123.1567 | 76.7349 | 68.4586 | 68.3212 | 123.1567 | 123.1888 | 123.23 | -55.188 | -46.4081
5713.7812 | 123.4543 | -68.2434 | 54.8676 | -0.12611 | -0.013984 | -0.033133 | 0.0024202 | -0.013168 | -0.0050095 | -0.0022302 | 0.045776 | 0.20599 | -0.27924 | 55.1605 | 54.9408 | 54.9225 | 54.8035 | 55.1468 | 54.9545 | 8.4824 | 67.9642 | -54.6616 | 68.2892 | 123.4039 | 0.073242 | 76.7258 | 0.086975 | 0.32501 | 123.0469 | 123.3902 | 123.1842 | 68.4494 | 68.2892 | 123.1979 | 123.1659 | 76.7258 | 68.4494 | 68.2892 | 123.1659 | 123.1842 | 123.1979 | -55.1468 | -46.3852
5714.7812 | 123.4497 | -68.2205 | 54.9042 | -0.13374 | -0.01377 | -0.030142 | 0.0041292 | -0.013168 | -0.0082137 | -0.0037256 | 0.068665 | 0.20142 | -0.27008 | 55.1605 | 54.9454 | 54.9133 | 54.8492 | 55.1605 | 54.9728 | 8.4869 | 67.9504 | -54.7028 | 68.2892 | 123.381 | 0.041199 | 76.7075 | 0.068664 | 0.33875 | 123.0698 | 123.381 | 123.1659 | 68.4219 | 68.2892 | 123.1934 | 123.1338 | 76.7075 | 68.4219 | 68.2892 | 123.1338 | 123.1659 | 123.1934 | -55.1743 | -46.4172
5715.7656 | 123.4085 | -68.2297 | 54.8996 | -0.149 | -0.012488 | -0.028433 | 0.005411 | -0.012954 | -0.0077865 | -0.003512 | 0.068665 | 0.20142 | -0.28839 | 55.1514 | 54.9271 | 54.895 | 54.8721 | 55.1376 | 54.9866 | 8.4824 | 67.9413 | -54.6982 | 68.2983 | 123.381 | 0.027466 | 76.712 | 0.086975 | 0.35706 | 123.1018 | 123.3673 | 123.1567 | 68.4311 | 68.2983 | 123.2162 | 123.1247 | 76.712 | 68.4311 | 68.2983 | 123.1247 | 123.1567 | 123.2162 | -55.188 | -46.4172
5716.7812 | 123.4543 | -68.2251 | 54.8996 | -0.17189 | -0.01142 | -0.03057 | 0.0028476 | -0.015731 | -0.0082137 | -0.0015894 | 0.036621 | 0.21057 | -0.27008 | 55.188 | 54.9362 | 54.9362 | 54.808 | 55.1559 | 54.9362 | 8.4732 | 67.955 | -54.689 | 68.2617 | 123.4131 | 0.036621 | 76.6983 | 0.036621 | 0.3067 | 123.0331 | 123.381 | 123.1613 | 68.4357 | 68.2617 | 123.1613 | 123.1613 | 76.6983 | 68.4357 | 68.2617 | 123.1613 | 123.1613 | 123.1613 | -55.1697 | -46.4264
5717.7812 | 123.4497 | -68.2617 | 54.8767 | -0.04219 | -0.010993 | -0.027365 | 0.002634 | -0.012954 | -0.0086411 | -0.0030848 | 0.032043 | 0.19226 | -0.29755 | 55.1651 | 54.9316 | 54.9225 | 54.7852 | 55.1285 | 54.9362 | 8.4869 | 67.9642 | -54.6844 | 68.2938 | 123.4268 | 0.054932 | 76.7487 | 0.059509 | 0.32959 | 123.0469 | 123.3902 | 123.1934 | 68.454 | 68.2938 | 123.1979 | 123.1842 | 76.7487 | 68.454 | 68.2938 | 123.1842 | 123.1934 | 123.1979 | -55.1743 | -46.3898
5718.7812 | 123.436 | -68.2571 | 54.8584 | 0.026474 | -0.013129 | -0.028433 | 0.0011386 | -0.012954 | -0.0084273 | -0.0039392 | 0 | 0.18768 | -0.3067 | 55.1422 | 54.9133 | 54.895 | 54.808 | 55.1193 | 54.95 | 8.4869 | 67.9504 | -54.6707 | 68.2571 | 123.3994 | 0.054932 | 76.7441 | 0.091553 | 0.3067 | 123.0652 | 123.3765 | 123.1705 | 68.4448 | 68.2571 | 123.2071 | 123.1522 | 76.7441 | 68.4448 | 68.2571 | 123.1522 | 123.1705 | 123.2071 | -55.1651 | -46.3715
5719.7812 | 123.4543 | -68.2343 | 54.8676 | 0.018845 | -0.010993 | -0.032706 | 0.0013522 | -0.011672 | -0.0047957 | -0.003512 | 0.045776 | 0.17853 | -0.29297 | 55.1651 | 54.9362 | 54.9225 | 54.7852 | 55.1468 | 54.9316 | 8.4869 | 67.9413 | -54.689 | 68.28 | 123.3994 | 0.068664 | 76.7212 | 0.064087 | 0.33874 | 123.0194 | 123.381 | 123.1705 | 68.4128 | 68.28 | 123.1659 | 123.1567 | 76.7212 | 68.4128 | 68.28 | 123.1567 | 123.1705 | 123.1659 | -55.1605 | -46.3806
5720.7812 | 123.4268 | -68.2571 | 54.8767 | -0.11848 | -0.014625 | -0.027792 | 0.0028476 | -0.013595 | -0.0065047 | -0.0032984 | 0.032043 | 0.16479 | -0.3067 | 55.1834 | 54.9362 | 54.9271 | 54.7989 | 55.1514 | 54.9408 | 8.4778 | 67.9504 | -54.7119 | 68.2892 | 123.4406 | 0.059509 | 76.7349 | 0.064087 | 0.33874 | 123.056 | 123.4085 | 123.1934 | 68.4219 | 68.2892 | 123.1979 | 123.1842 | 76.7349 | 68.4219 | 68.2892 | 123.1842 | 123.1934 | 123.1979 | -55.1834 | -46.3989
5721.7656 | 123.4497 | -68.2343 | 54.895 | -0.10323 | -0.013129 | -0.031851 | 0.0015658 | -0.014236 | -0.0075729 | -0.003512 | 0.073242 | 0.19226 | -0.28381 | 55.1834 | 54.95 | 54.9225 | 54.8126 | 55.1651 | 54.9591 | 8.4778 | 67.9504 | -54.7028 | 68.3075 | 123.4177 | 0.054931 | 76.712 | 0.064086 | 0.35706 | 123.0469 | 123.3994 | 123.1842 | 68.4265 | 68.3075 | 123.1934 | 123.1567 | 76.712 | 68.4265 | 68.3075 | 123.1567 | 123.1842 | 123.1934 | -55.1788 | -46.4172
5722.7812 | 123.6237 | -68.2251 | 54.9362 | -0.057449 | -0.01377 | -0.027152 | 0.0011386 | -0.014022 | -0.0082137 | -0.0030848 | 0.050354 | 0.19226 | -0.29297 | 55.1926 | 54.9683 | 54.9454 | 54.7806 | 55.1605 | 54.9362 | 8.4869 | 67.9321 | -54.744 | 68.2755 | 123.4177 | 0.032044 | 76.712 | 0 | 0.34332 | 123.0057 | 123.3856 | 123.1934 | 68.4174 | 68.2755 | 123.1613 | 123.1705 | 76.712 | 68.4174 | 68.2755 | 123.1705 | 123.1934 | 123.1613 | -55.2292 | -46.4493
5723.7812 | 123.4772 | -68.2343 | 54.8767 | -0.04219 | -0.012916 | -0.029288 | -0.001425 | -0.014663 | -0.0062911 | -0.0020166 | 0.041199 | 0.1831 | -0.27924 | 55.1743 | 54.95 | 54.9225 | 54.7852 | 55.1514 | 54.9408 | 8.4824 | 67.955 | -54.6936 | 68.2755 | 123.4085 | 0.073242 | 76.7166 | 0.064087 | 0.32043 | 123.0194 | 123.3856 | 123.1842 | 68.4174 | 68.2755 | 123.175 | 123.1567 | 76.7166 | 68.4174 | 68.2755 | 123.1567 | 123.1842 | 123.175 | -55.1559 | -46.3943
5724.7812 | 123.4222 | -68.248 | 54.8904 | 0.011215 | -0.012488 | -0.029929 | 7.0444e-05 | -0.012954 | -0.0037277 | -0.0024438 | -0.022888 | 0.19226 | -0.32044 | 55.1376 | 54.8996 | 54.8904 | 54.8035 | 55.0964 | 54.9454 | 8.4824 | 67.9276 | -54.6982 | 68.2251 | 123.3856 | 0.009155 | 76.7303 | 0.054932 | 0.29755 | 123.0515 | 123.3444 | 123.1476 | 68.4402 | 68.2251 | 123.1934 | 123.1384 | 76.7303 | 68.4402 | 68.2251 | 123.1384 | 123.1476 | 123.1934 | -55.2109 | -46.4081
5725.7812 | 123.436 | -68.2617 | 54.8813 | -0.034561 | -0.013129 | -0.028647 | 0.0011386 | -0.013595 | -0.0041549 | -0.0026574 | 0.032043 | 0.20142 | -0.29755 | 55.1514 | 54.9316 | 54.9088 | 54.7852 | 55.1514 | 54.9088 | 8.4778 | 67.9642 | -54.6799 | 68.2938 | 123.4131 | 0.050354 | 76.7395 | 0.027465 | 0.32959 | 123.0469 | 123.4131 | 123.1934 | 68.4631 | 68.2938 | 123.1705 | 123.1705 | 76.7395 | 68.4631 | 68.2938 | 123.1705 | 123.1934 | 123.1705 | -55.1788 | -46.4035
5726.7812 | 123.4314 | -68.2755 | 54.8767 | 0.0035856 | -0.015266 | -0.031424 | -0.00057036 | -0.012954 | -0.0065047 | -0.0028712 | 0.018311 | 0.1831 | -0.32501 | 55.1559 | 54.9179 | 54.9133 | 54.808 | 55.1239 | 54.9545 | 8.4778 | 67.9504 | -54.6936 | 68.2938 | 123.4314 | 0.041199 | 76.7532 | 0.07782 | 0.34332 | 123.0835 | 123.3994 | 123.1934 | 68.4586 | 68.2938 | 123.23 | 123.1888 | 76.7532 | 68.4586 | 68.2938 | 123.1888 | 123.1934 | 123.23 | -55.2017 | -46.3989
5727.7812 | 123.436 | -68.2663 | 54.8721 | 0.07988 | -0.01142 | -0.03057 | -0.00057036 | -0.014236 | -0.0054367 | -0.0015894 | 0.004578 | 0.17853 | -0.31586 | 55.1514 | 54.9225 | 54.8813 | 54.776 | 55.1102 | 54.8904 | 8.4778 | 67.9504 | -54.6936 | 68.2709 | 123.4177 | 0.050354 | 76.7441 | 0.018311 | 0.32044 | 123.0423 | 123.3765 | 123.1888 | 68.4448 | 68.2709 | 123.1567 | 123.1476 | 76.7441 | 68.4448 | 68.2709 | 123.1476 | 123.1888 | 123.1567 | -55.188 | -46.3943
5728.7656 | 123.436 | -68.2343 | 54.8767 | -0.072708 | -0.013343 | -0.027365 | -0.0022794 | -0.013809 | -0.0043685 | -0.0026574 | 0.082397 | 0.19226 | -0.27008 | 55.0919 | 54.8904 | 54.8767 | 54.8401 | 55.1102 | 54.9042 | 8.4732 | 67.9642 | -54.6844 | 68.3166 | 123.3261 | 0.013733 | 76.7075 | 0.027466 | 0.35248 | 123.0743 | 123.3444 | 123.1247 | 68.4265 | 68.3166 | 123.1384 | 123.111 | 76.7075 | 68.4265 | 68.3166 | 123.111 | 123.1247 | 123.1384 | -55.1468 | -46.4035
5729.7656 | 123.4634 | -68.2663 | 54.863 | -0.087967 | -0.013557 | -0.027152 | 0.00049764 | -0.014877 | -0.0050095 | -0.00693 | 0.082397 | 0.17395 | -0.28381 | 55.2063 | 54.9683 | 55.0507 | 55.0781 | 54.9591 | 54.9774 | 8.4824 | 67.9825 | -54.689 | 68.3487 | 123.4726 | 0.10529 | 76.7487 | 0.11444 | 0.36621 | 123.3444 | 123.2254 | 123.2346 | 68.4402 | 68.3487 | 123.2437 | 123.317 | 76.7487 | 68.4402 | 68.3487 | 123.317 | 123.2346 | 123.2437 | -55.1468 | -46.3806
5730.7812 | 123.4039 | -68.248 | 54.8904 | 0.072251 | -0.011848 | -0.026511 | 0.0013522 | -0.01274 | -0.0056503 | -0.0037256 | -0.022888 | 0.17395 | -0.32044 | 55.1285 | 54.9133 | 54.863 | 54.8126 | 55.0781 | 54.9316 | 8.4824 | 67.9276 | -54.7165 | 68.2251 | 123.3765 | 0.022888 | 76.7303 | 0.041199 | 0.29755 | 123.0606 | 123.3261 | 123.1613 | 68.4219 | 68.2251 | 123.1796 | 123.111 | 76.7303 | 68.4219 | 68.2251 | 123.111 | 123.1613 | 123.1796 | -55.2109 | -46.4081
5731.7812 | 123.4131 | -68.2709 | 54.8904 | 0.13329 | -0.013557 | -0.026511 | 0.00049764 | -0.01274 | -0.0067185 | -0.0050074 | -0.041199 | 0.17395 | -0.31128 | 55.1102 | 54.8813 | 54.8721 | 54.808 | 55.069 | 54.9271 | 8.4732 | 67.9596 | -54.7165 | 68.2297 | 123.381 | -0.009155 | 76.7441 | 0.036621 | 0.27008 | 123.0789 | 123.3398 | 123.1522 | 68.4448 | 68.2297 | 123.1979 | 123.143 | 76.7441 | 68.4448 | 68.2297 | 123.143 | 123.1522 | 123.1979 | -55.2017 | -46.4172
5732.7812 | 123.4314 | -68.2709 | 54.8584 | -0.019302 | -0.010352 | -0.028006 | 0.00049764 | -0.01274 | -0.0054367 | -0.0024438 | 0 | 0.18768 | -0.32044 | 55.1559 | 54.9271 | 54.8996 | 54.7989 | 55.1102 | 54.9362 | 8.4778 | 67.9504 | -54.6707 | 68.2709 | 123.4268 | 0.068665 | 76.7487 | 0.07782 | 0.32044 | 123.0698 | 123.381 | 123.1979 | 68.4586 | 68.2709 | 123.2071 | 123.1705 | 76.7487 | 68.4586 | 68.2709 | 123.1705 | 123.1979 | 123.2071 | -55.1788 | -46.3806
5733.7812 | 123.436 | -68.2343 | 54.8767 | 0.034104 | -0.01377 | -0.030356 | -0.001425 | -0.013381 | -0.0071457 | -0.0037256 | -0.009155 | 0.17853 | -0.3067 | 55.1422 | 54.9133 | 54.8859 | 54.7943 | 55.1056 | 54.9362 | 8.4824 | 67.9276 | -54.6982 | 68.2251 | 123.3765 | 0.036621 | 76.7166 | 0.059509 | 0.29755 | 123.0286 | 123.3398 | 123.1476 | 68.4128 | 68.2251 | 123.1705 | 123.1201 | 76.7166 | 68.4128 | 68.2251 | 123.1201 | 123.1476 | 123.1705 | -55.1834 | -46.3943
5734.7812 | 123.4222 | -68.2617 | 54.8813 | 0.056992 | -0.01377 | -0.03121 | -0.00035676 | -0.01274 | -0.0045821 | -0.0020166 | 0 | 0.16937 | -0.31586 | 55.1422 | 54.9042 | 54.8859 | 54.7989 | 55.0964 | 54.9316 | 8.4824 | 67.9459 | -54.7119 | 68.2617 | 123.4039 | 0.022888 | 76.7441 | 0.050354 | 0.31586 | 123.0606 | 123.3582 | 123.1659 | 68.4311 | 68.2617 | 123.1934 | 123.1476 | 76.7441 | 68.4311 | 68.2617 | 123.1476 | 123.1659 | 123.1934 | -55.1971 | -46.3989
5735.7656 | 123.6557 | -68.2068 | 54.9271 | -0.011673 | -0.015479 | -0.030783 | 0.0022066 | -0.014663 | -0.0056503 | -0.0026574 | 0.054932 | 0.17853 | -0.27466 | 55.2017 | 54.982 | 54.9591 | 54.7852 | 55.1605 | 54.9133 | 8.4824 | 67.9321 | -54.7485 | 68.2617 | 123.4085 | 0.054932 | 76.6891 | -0.013733 | 0.32959 | 122.9919 | 123.3673 | 123.1888 | 68.3853 | 68.2617 | 123.1201 | 123.1659 | 76.6891 | 68.3853 | 68.2617 | 123.1659 | 123.1888 | 123.1201 | -55.2017 | -46.4447
5736.7812 | 123.4451 | -68.2388 | 54.8721 | 0.034104 | -0.012275 | -0.030142 | 0.00028404 | -0.013168 | -0.0043685 | -0.00073479 | 0.022888 | 0.19684 | -0.30212 | 55.1651 | 54.9362 | 54.8996 | 54.7943 | 55.1102 | 54.895 | 8.4824 | 67.9367 | -54.6753 | 68.2617 | 123.4039 | 0.064087 | 76.7212 | 0.022889 | 0.32501 | 123.0331 | 123.349 | 123.175 | 68.4357 | 68.2617 | 123.1339 | 123.1384 | 76.7212 | 68.4357 | 68.2617 | 123.1384 | 123.175 | 123.1339 | -55.1743 | -46.3898
5737.7812 | 123.3902 | -68.2526 | 54.8813 | 0.056992 | -0.014625 | -0.028433 | 0.001993 | -0.013381 | -0.0056503 | -0.0020166 | -0.068665 | 0.16479 | -0.32044 | 55.1239 | 54.8813 | 54.8538 | 54.8264 | 55.0598 | 54.9454 | 8.4824 | 67.9321 | -54.7165 | 68.1839 | 123.3765 | 0 | 76.7349 | 0.064087 | 0.25177 | 123.0789 | 123.3124 | 123.1338 | 68.4174 | 68.1839 | 123.1979 | 123.1064 | 76.7349 | 68.4174 | 68.1839 | 123.1064 | 123.1338 | 123.1979 | -55.2017 | -46.3989
5738.7812 | 123.4131 | -68.2663 | 54.8813 | -0.42366 | -0.013984 | -0.026938 | 0.0017794 | -0.014236 | -0.0052231 | -0.0024438 | -0.045776 | 0.17853 | -0.28839 | 55.0827 | 54.8676 | 54.863 | 54.8218 | 55.0781 | 54.8996 | 8.4778 | 67.9779 | -54.7028 | 68.2205 | 123.349 | -0.013733 | 76.7441 | 0.01831 | 0.24262 | 123.0881 | 123.3444 | 123.1338 | 68.4448 | 68.2205 | 123.1659 | 123.1293 | 76.7441 | 68.4448 | 68.2205 | 123.1293 | 123.1338 | 123.1659 | -55.1697 | -46.4035
5739.7812 | 123.4039 | -68.2571 | 54.863 | 0.072251 | -0.011848 | -0.028433 | 0.0015658 | -0.013809 | -0.0050095 | -0.0030848 | -0.027466 | 0.17395 | -0.31586 | 55.1376 | 54.9225 | 54.8767 | 54.8126 | 55.0827 | 54.9088 | 8.4778 | 67.9413 | -54.689 | 68.2297 | 123.3948 | 0.059509 | 76.7349 | 0.045776 | 0.28839 | 123.0698 | 123.3398 | 123.1796 | 68.4311 | 68.2297 | 123.1659 | 123.1338 | 76.7349 | 68.4311 | 68.2297 | 123.1338 | 123.1796 | 123.1659 | -55.1788 | -46.3852
5740.7812 | 123.3994 | -68.2571 | 54.8676 | 0.07988 | -0.012702 | -0.030142 | 0.0015658 | -0.012527 | -0.0075729 | -0.0022302 | -0.022888 | 0.16479 | -0.32959 | 55.1193 | 54.895 | 54.8676 | 54.8035 | 55.0735 | 54.9408 | 8.4824 | 67.9276 | -54.7028 | 68.2343 | 123.3765 | 0.027466 | 76.7395 | 0.073242 | 0.3067 | 123.0606 | 123.3307 | 123.1522 | 68.4219 | 68.2343 | 123.1979 | 123.1247 | 76.7395 | 68.4219 | 68.2343 | 123.1247 | 123.1522 | 123.1979 | -55.1971 | -46.3852
5741.7656 | 123.4589 | -68.2343 | 54.8447 | -0.04219 | -0.012488 | -0.028861 | 0.001993 | -0.01274 | -0.0065047 | -0.0024438 | 0.032043 | 0.18768 | -0.28381 | 55.1743 | 54.9545 | 54.9179 | 54.7943 | 55.1422 | 54.9088 | 8.4869 | 67.9504 | -54.657 | 68.2663 | 123.4085 | 0.10986 | 76.7212 | 0.064086 | 0.31586 | 123.0286 | 123.3765 | 123.1888 | 68.4219 | 68.2663 | 123.143 | 123.1522 | 76.7212 | 68.4219 | 68.2663 | 123.1522 | 123.1888 | 123.143 | -55.1285 | -46.3577
5742.7656 | 123.4451 | -68.2571 | 54.8767 | -0.019302 | -0.01142 | -0.028433 | -0.00078396 | -0.01274 | -0.0060775 | -0.0039392 | 0.022888 | 0.19684 | -0.29755 | 55.1651 | 54.9408 | 54.9042 | 54.808 | 55.1147 | 54.8996 | 8.4778 | 67.9596 | -54.6799 | 68.28 | 123.4222 | 0.064087 | 76.7349 | 0.022888 | 0.32043 | 123.0652 | 123.3719 | 123.1979 | 68.454 | 68.28 | 123.1567 | 123.1613 | 76.7349 | 68.454 | 68.28 | 123.1613 | 123.1979 | 123.1567 | -55.1743 | -46.3989
5743.7812 | 123.4177 | -68.2434 | 54.8767 | 0.072251 | -0.012488 | -0.029929 | 0.00049764 | -0.014663 | -0.0050095 | -0.0026574 | -0.032043 | 0.19684 | -0.32501 | 55.1239 | 54.9133 | 54.8676 | 54.8172 | 55.0919 | 54.9271 | 8.4869 | 67.9184 | -54.6799 | 68.2114 | 123.3673 | 0.036621 | 76.7303 | 0.050354 | 0.29297 | 123.0606 | 123.3353 | 123.1567 | 68.4402 | 68.2114 | 123.1705 | 123.111 | 76.7303 | 68.4402 | 68.2114 | 123.111 | 123.1567 | 123.1705 | -55.2017 | -46.3898
5744.7812 | 123.4131 | -68.2571 | 54.863 | 0.1638 | -0.010993 | -0.025015 | 0.001993 | -0.012527 | -0.0047957 | -0.0037256 | -0.032043 | 0.13733 | -0.33417 | 55.1147 | 54.8813 | 54.863 | 54.7714 | 55.0644 | 54.8859 | 8.4732 | 67.923 | -54.7256 | 68.2251 | 123.3719 | 0.018311 | 76.7303 | 0.022888 | 0.30212 | 123.0286 | 123.3215 | 123.1384 | 68.3945 | 68.2251 | 123.143 | 123.1201 | 76.7303 | 68.3945 | 68.2251 | 123.1201 | 123.1384 | 123.143 | -55.1971 | -46.3898
5745.7812 | 123.4177 | -68.2663 | 54.8538 | 0.20958 | -0.011848 | -0.027792 | 0.0024202 | -0.012954 | -0.0080001 | -0.0030848 | -0.041199 | 0.11902 | -0.34332 | 55.1147 | 54.8813 | 54.8721 | 54.7577 | 55.0552 | 54.8767 | 8.4869 | 67.923 | -54.7348 | 68.2251 | 123.381 | 0.027466 | 76.7532 | 0.022888 | 0.30212 | 123.024 | 123.3215 | 123.1476 | 68.3853 | 68.2251 | 123.143 | 123.1384 | 76.7532 | 68.3853 | 68.2251 | 123.1384 | 123.1476 | 123.143 | -55.1971 | -46.3669
5746.7812 | 123.3902 | -68.2617 | 54.8813 | 0.23247 | -0.010993 | -0.031851 | 0.0024202 | -0.011031 | -0.0054367 | -0.0030848 | -0.041199 | 0.15564 | -0.32959 | 55.1147 | 54.8035 | 54.9911 | 54.7806 | 54.9911 | 54.9271 | 8.4732 | 67.9321 | -54.7256 | 68.2205 | 123.3765 | -0.07782 | 76.7349 | 0.045776 | 0.28839 | 123.0423 | 123.2529 | 123.0652 | 68.4174 | 68.2205 | 123.1888 | 123.2529 | 76.7349 | 68.4174 | 68.2205 | 123.2529 | 123.0652 | 123.1888 | -55.2109 | -46.4081
5747.7812 | 123.4039 | -68.2892 | 54.8676 | 0.19432 | -0.011848 | -0.024374 | 0.0022066 | -0.012313 | -0.0073593 | -0.0011622 | -0.022888 | 0.14648 | -0.33875 | 55.1147 | 54.8904 | 54.8492 | 54.7943 | 55.0644 | 54.9133 | 8.4778 | 67.9504 | -54.7211 | 68.2663 | 123.4039 | 0.022888 | 76.767 | 0.045776 | 0.31586 | 123.0835 | 123.3536 | 123.1796 | 68.4357 | 68.2663 | 123.2025 | 123.1384 | 76.767 | 68.4357 | 68.2663 | 123.1384 | 123.1796 | 123.2025 | -55.2063 | -46.3898
5748.7656 | 123.3994 | -68.2663 | 54.8767 | 0.1104 | -0.010779 | -0.02822 | 0.0015658 | -0.012954 | -0.0060775 | -0.0020166 | -0.004578 | 0.17853 | -0.33417 | 55.1285 | 54.895 | 54.8859 | 54.8172 | 55.0873 | 54.895 | 8.4778 | 67.9321 | -54.6982 | 68.2617 | 123.3948 | 0.018311 | 76.7441 | 0.018311 | 0.32959 | 123.0835 | 123.3536 | 123.1613 | 68.4448 | 68.2617 | 123.1613 | 123.1522 | 76.7441 | 68.4448 | 68.2617 | 123.1522 | 123.1613 | 123.1613 | -55.2109 | -46.3989
5749.7656 | 123.4131 | -68.2663 | 54.8721 | -0.15663 | -0.010566 | -0.024161 | 0.001993 | -0.011672 | -0.0041549 | -0.0037256 | -0.041199 | 0.18768 | -0.29755 | 55.101 | 54.8996 | 54.8767 | 54.8126 | 55.0644 | 54.9225 | 8.4824 | 67.9688 | -54.6844 | 68.2251 | 123.3673 | 0.027466 | 76.7487 | 0.050354 | 0.25635 | 123.0789 | 123.3307 | 123.1659 | 68.454 | 68.2251 | 123.1888 | 123.143 | 76.7487 | 68.454 | 68.2251 | 123.143 | 123.1659 | 123.1888 | -55.1697 | -46.3898
5750.7812 | 123.4177 | -68.2709 | 54.8538 | 0.1638 | -0.012275 | -0.024588 | 0.0017794 | -0.010604 | -0.0054367 | -0.0043664 | -0.041199 | 0.10986 | -0.36621 | 55.1056 | 54.8904 | 54.8767 | 54.7897 | 55.0552 | 54.8996 | 8.4824 | 67.9047 | -54.744 | 68.2297 | 123.3765 | 0.036621 | 76.7532 | 0.045776 | 0.32501 | 123.0606 | 123.3261 | 123.1613 | 68.3807 | 68.2297 | 123.1705 | 123.1476 | 76.7532 | 68.3807 | 68.2297 | 123.1476 | 123.1613 | 123.1705 | -55.22 | -46.3715
5751.7812 | 123.468 | -68.2663 | 54.8355 | 0.24773 | -0.011207 | -0.028006 | 0.0039156 | -0.010391 | -0.0043685 | -0.0024438 | 0.009155 | 0.12817 | -0.32959 | 55.1376 | 54.9133 | 54.9133 | 54.7302 | 55.0827 | 54.863 | 8.4778 | 67.9367 | -54.7073 | 68.2755 | 123.4039 | 0.07782 | 76.7441 | 0.027466 | 0.33875 | 122.9965 | 123.349 | 123.1796 | 68.3945 | 68.2755 | 123.1293 | 123.1796 | 76.7441 | 68.3945 | 68.2755 | 123.1796 | 123.1796 | 123.1293 | -55.1651 | -46.3577
5752.7812 | 123.4543 | -68.248 | 54.8492 | 0.17143 | -0.010993 | -0.024374 | 0.0066928 | -0.011672 | -0.0056503 | -0.0043664 | 0.059509 | 0.10071 | -0.36621 | 55.1376 | 54.9271 | 54.8996 | 54.7211 | 55.0781 | 54.8904 | 8.4869 | 67.8818 | -54.7485 | 68.3075 | 123.3856 | 0.07782 | 76.7349 | 0.041199 | 0.42572 | 122.9691 | 123.3261 | 123.175 | 68.3487 | 68.3075 | 123.1384 | 123.1476 | 76.7349 | 68.3487 | 68.3075 | 123.1476 | 123.175 | 123.1384 | -55.2155 | -46.3623
5753.7812 | 123.4451 | -68.28 | 54.8447 | 0.2401 | -0.010993 | -0.024802 | 0.0047702 | -0.013168 | -0.0045821 | -0.0015894 | 0 | 0.10986 | -0.34332 | 55.1422 | 54.9133 | 54.9088 | 54.7348 | 55.069 | 54.8859 | 8.4869 | 67.9367 | -54.7348 | 68.28 | 123.4222 | 0.068664 | 76.767 | 0.041198 | 0.34332 | 123.0148 | 123.349 | 123.1934 | 68.3899 | 68.28 | 123.1659 | 123.1888 | 76.767 | 68.3899 | 68.28 | 123.1888 | 123.1934 | 123.1659 | -55.188 | -46.3577
5754.7812 | 123.4451 | -68.2526 | 54.8264 | 0.33928 | -0.0090704 | -0.018393 | 0.0062656 | -0.010818 | -0.0050095 | -0.0041528 | 0.013733 | 0.1236 | -0.32959 | 55.1468 | 54.9179 | 54.9133 | 54.7073 | 55.069 | 54.8859 | 8.4778 | 67.923 | -54.7028 | 68.2663 | 123.3994 | 0.091553 | 76.7303 | 0.059509 | 0.34332 | 122.9599 | 123.3215 | 123.1705 | 68.3762 | 68.2663 | 123.1384 | 123.1659 | 76.7303 | 68.3762 | 68.2663 | 123.1659 | 123.1705 | 123.1384 | -55.1559 | -46.3486
5755.7656 | 123.3994 | -68.28 | 54.8355 | 0.22484 | -0.0094976 | -0.027579 | 0.0030612 | -0.011886 | -0.0058639 | -0.0041528 | -0.009155 | 0.1236 | -0.37079 | 55.101 | 54.8996 | 54.8813 | 54.776 | 55.0735 | 54.9133 | 8.4778 | 67.9092 | -54.7119 | 68.2709 | 123.381 | 0.064087 | 76.7578 | 0.07782 | 0.36163 | 123.056 | 123.3536 | 123.1796 | 68.4036 | 68.2709 | 123.1934 | 123.1613 | 76.7578 | 68.4036 | 68.2709 | 123.1613 | 123.1796 | 123.1934 | -55.2063 | -46.3577
5756.7656 | 123.4039 | -68.2755 | 54.8447 | 0.22484 | -0.010139 | -0.02587 | 0.0060518 | -0.010177 | -0.0054367 | -0.0032984 | -0.004578 | 0.11902 | -0.35248 | 55.1193 | 54.9042 | 54.8996 | 54.7348 | 55.0644 | 54.895 | 8.4824 | 67.923 | -54.7256 | 68.2709 | 123.3948 | 0.059509 | 76.7578 | 0.050354 | 0.3479 | 123.0103 | 123.3398 | 123.1796 | 68.3945 | 68.2709 | 123.1705 | 123.175 | 76.7578 | 68.3945 | 68.2709 | 123.175 | 123.1796 | 123.1705 | -55.1971 | -46.3623
5757.7812 | 123.4451 | -68.2755 | 54.8401 | 0.095139 | -0.012061 | -0.022665 | 0.0058382 | -0.010604 | -0.0056503 | -0.003512 | 0.009155 | 0.086975 | -0.35706 | 55.1285 | 54.9042 | 54.8996 | 54.7256 | 55.0781 | 54.9042 | 8.4824 | 67.9184 | -54.7531 | 68.2846 | 123.4039 | 0.064087 | 76.7578 | 0.064087 | 0.36621 | 123.0011 | 123.3536 | 123.1796 | 68.3624 | 68.2846 | 123.1796 | 123.175 | 76.7578 | 68.3624 | 68.2846 | 123.175 | 123.1796 | 123.1796 | -55.1971 | -46.3577
5758.7812 | 123.3856 | -68.2892 | 54.8676 | 0.27824 | -0.0097114 | -0.026724 | 0.0096834 | -0.0080407 | -0.0069321 | -0.0026574 | -0.036621 | 0.18768 | -0.37079 | 55.0781 | 54.8492 | 54.8309 | 54.8172 | 55.0049 | 54.9271 | 8.4778 | 67.9184 | -54.6799 | 68.2526 | 123.3673 | -0.018311 | 76.767 | 0.059509 | 0.33417 | 123.1064 | 123.2941 | 123.1384 | 68.4769 | 68.2526 | 123.2162 | 123.1201 | 76.767 | 68.4769 | 68.2526 | 123.1201 | 123.1384 | 123.2162 | -55.2383 | -46.3898
5759.7812 | 123.3536 | -68.2846 | 54.8721 | 0.2401 | -0.009925 | -0.020956 | 0.010111 | -0.0086817 | -0.0069321 | -0.001803 | -0.054932 | 0.18768 | -0.36621 | 55.0598 | 54.8401 | 54.8218 | 54.8447 | 54.9866 | 54.9637 | 8.4824 | 67.9184 | -54.6844 | 68.2297 | 123.3444 | -0.032043 | 76.767 | 0.091553 | 0.31128 | 123.1293 | 123.2712 | 123.1247 | 68.4723 | 68.2297 | 123.2483 | 123.1064 | 76.767 | 68.4723 | 68.2297 | 123.1064 | 123.1247 | 123.2483 | -55.2383 | -46.3898
5760.7812 | 123.3994 | -68.2938 | 54.8538 | 0.26299 | -0.009284 | -0.025443 | 0.00712 | -0.0071863 | -0.0054367 | -0.0037256 | -0.013733 | 0.18768 | -0.35248 | 55.0873 | 54.8859 | 54.8492 | 54.7897 | 55.0461 | 54.9271 | 8.4778 | 67.9413 | -54.6661 | 68.28 | 123.381 | 0.032043 | 76.7715 | 0.073242 | 0.33875 | 123.0835 | 123.3398 | 123.1796 | 68.4814 | 68.28 | 123.2208 | 123.143 | 76.7715 | 68.4814 | 68.28 | 123.143 | 123.1796 | 123.2208 | -55.2063 | -46.376
5761.7812 | 123.3856 | -68.2846 | 54.8355 | 0.25536 | -0.009284 | -0.024161 | 0.0086154 | -0.0080407 | -0.0043685 | -0.001803 | -0.041199 | 0.19684 | -0.36621 | 55.0644 | 54.8538 | 54.8355 | 54.8218 | 55.0003 | 54.9316 | 8.4778 | 67.9184 | -54.6387 | 68.2434 | 123.349 | 0.018311 | 76.7624 | 0.096131 | 0.32501 | 123.1064 | 123.2849 | 123.1384 | 68.4814 | 68.2434 | 123.2162 | 123.1201 | 76.7624 | 68.4814 | 68.2434 | 123.1201 | 123.1384 | 123.2162 | -55.2017 | -46.3577
5762.7812 | 123.5275 | -68.2434 | 54.8492 | 0.12566 | -0.012061 | -0.02822 | 0.00092504 | -0.010818 | -0.0041549 | -0.00030759 | -0.064087 | 0.16479 | -0.32501 | 55.0827 | 54.9088 | 54.8721 | 54.7989 | 55.0598 | 54.9179 | 8.4824 | 67.9184 | -54.6844 | 68.1793 | 123.3261 | 0.059509 | 76.7258 | 0.068665 | 0.26093 | 123.0423 | 123.3032 | 123.1522 | 68.4082 | 68.1793 | 123.1613 | 123.1155 | 76.7258 | 68.4082 | 68.1793 | 123.1155 | 123.1522 | 123.1613 | -55.1743 | -46.3669
5763.7812 | 123.4222 | -68.2938 | 54.8401 | 0.19432 | -0.012702 | -0.029288 | 0.0024202 | -0.011672 | -0.0065047 | -0.0013758 | -0.045776 | 0.11902 | -0.33417 | 55.0919 | 54.8859 | 54.8721 | 54.7943 | 55.0598 | 54.9225 | 8.4778 | 67.9596 | -54.7211 | 68.248 | 123.3856 | 0.045776 | 76.7715 | 0.082397 | 0.28839 | 123.0881 | 123.3536 | 123.1796 | 68.4128 | 68.248 | 123.2162 | 123.1659 | 76.7715 | 68.4128 | 68.248 | 123.1659 | 123.1796 | 123.2162 | -55.1743 | -46.3623
5764.7812 | 123.3902 | -68.2846 | 54.8813 | 0.25536 | -0.008216 | -0.025443 | 0.0084018 | -0.0084681 | -0.0056503 | -0.0030848 | -0.027466 | 0.1831 | -0.36163 | 55.0735 | 54.8264 | 54.8264 | 54.8309 | 55.0049 | 54.9133 | 8.4732 | 67.923 | -54.6982 | 68.2571 | 123.3582 | -0.054932 | 76.7578 | 0.032043 | 0.33417 | 123.1155 | 123.2895 | 123.111 | 68.4677 | 68.2571 | 123.1979 | 123.111 | 76.7578 | 68.4677 | 68.2571 | 123.111 | 123.111 | 123.1979 | -55.2429 | -46.4081
5765.7812 | 123.3353 | -68.3395 | 54.863 | 0.58342 | -0.0086432 | -0.026297 | 0.0094698 | -0.0071863 | -0.0071457 | -0.0026574 | 0.009155 | 0.1831 | -0.35248 | 55.0461 | 54.7989 | 54.776 | 54.9088 | 54.9637 | 54.9362 | 8.4732 | 67.9871 | -54.6799 | 68.3487 | 123.3856 | -0.064087 | 76.8127 | 0.073242 | 0.36163 | 123.2483 | 123.3032 | 123.1384 | 68.5226 | 68.3487 | 123.2758 | 123.1155 | 76.8127 | 68.5226 | 68.3487 | 123.1155 | 123.1384 | 123.2758 | -55.2155 | -46.3898
5766.7812 | 123.3307 | -68.3075 | 54.8538 | 0.23247 | -0.0086432 | -0.022452 | 0.0094698 | -0.0091089 | -0.0056503 | -0.001803 | -0.041199 | 0.19226 | -0.35706 | 55.0186 | 54.808 | 54.7989 | 54.8813 | 54.9637 | 54.9728 | 8.4824 | 67.9504 | -54.6616 | 68.2663 | 123.3261 | -0.045777 | 76.7899 | 0.11902 | 0.31586 | 123.1888 | 123.2712 | 123.1155 | 68.4998 | 68.2663 | 123.2803 | 123.1064 | 76.7899 | 68.4998 | 68.2663 | 123.1064 | 123.1155 | 123.2803 | -55.2109 | -46.3715
5767.7812 | 123.4726 | -68.2617 | 54.8813 | 1.3006 | -0.010993 | -0.026511 | 0.0024202 | -0.010604 | -0.0054367 | -0.0024438 | 0.045776 | 0.21057 | -0.27008 | 55.1468 | 54.9683 | 54.9454 | 54.8172 | 55.1559 | 54.9728 | 8.4915 | 67.9916 | -54.6707 | 68.3075 | 123.4085 | 0.086975 | 76.7532 | 0.091552 | 0.31586 | 123.0789 | 123.4177 | 123.23 | 68.4723 | 68.3075 | 123.2346 | 123.2071 | 76.7532 | 68.4723 | 68.3075 | 123.2071 | 123.23 | 123.2346 | -55.1514 | -46.3898
5768.7812 | 123.3307 | -68.3212 | 54.8859 | -0.18715 | -0.010566 | -0.029501 | 0.0084018 | -0.0078271 | -0.0077865 | -0.0037256 | 0.036621 | 0.17395 | -0.37994 | 55.0507 | 54.7806 | 54.7623 | 54.8996 | 54.9545 | 54.9545 | 8.4732 | 67.9413 | -54.7119 | 68.3578 | 123.3719 | -0.10528 | 76.7944 | 0.068665 | 0.41657 | 123.2208 | 123.2758 | 123.1018 | 68.4952 | 68.3578 | 123.2758 | 123.0835 | 76.7944 | 68.4952 | 68.3578 | 123.0835 | 123.1018 | 123.2758 | -55.2658 | -46.4127
5769.7656 | 123.3673 | -68.3121 | 54.8676 | 0.2401 | -0.008216 | -0.030142 | 0.008829 | -0.0054773 | -0.0052231 | -0.0013758 | -0.027466 | 0.19226 | -0.35248 | 55.0552 | 54.8309 | 54.8218 | 54.8309 | 54.9911 | 54.9637 | 8.4778 | 67.9596 | -54.6753 | 68.2846 | 123.3673 | -0.036621 | 76.7899 | 0.09613 | 0.32501 | 123.143 | 123.3032 | 123.143 | 68.5043 | 68.2846 | 123.2758 | 123.1338 | 76.7899 | 68.5043 | 68.2846 | 123.1338 | 123.143 | 123.2758 | -55.22 | -46.3898
5770.7812 | 123.3398 | -68.3166 | 54.8721 | 0.14854 | -0.0067206 | -0.025229 | 0.0086154 | -0.0076135 | -0.0073593 | -0.0030848 | -0.041199 | 0.20599 | -0.3479 | 55.0461 | 54.808 | 54.8035 | 54.8996 | 54.9774 | 54.982 | 8.4778 | 67.9688 | -54.6661 | 68.2755 | 123.3627 | -0.064087 | 76.7944 | 0.10986 | 0.3067 | 123.2162 | 123.2941 | 123.1247 | 68.5226 | 68.2755 | 123.2986 | 123.1201 | 76.7944 | 68.5226 | 68.2755 | 123.1201 | 123.1247 | 123.2986 | -55.22 | -46.3943
5771.7812 | 123.3353 | -68.3212 | 54.8721 | -1.5528 | -0.010993 | -0.024802 | 0.0086154 | -0.0076135 | -0.0082137 | -0.0015894 | -0.027466 | 0.17395 | -0.33875 | 55.0323 | 54.7852 | 54.7852 | 54.8904 | 54.9545 | 54.982 | 8.4778 | 67.9825 | -54.6982 | 68.2938 | 123.3536 | -0.086975 | 76.799 | 0.10986 | 0.31128 | 123.2117 | 123.2758 | 123.1064 | 68.4952 | 68.2938 | 123.3032 | 123.1064 | 76.799 | 68.4952 | 68.2938 | 123.1064 | 123.1064 | 123.3032 | -55.2109 | -46.3943
5772.7812 | 123.4543 | -68.28 | 54.8584 | 0.25536 | -0.011207 | -0.024374 | 0.0051974 | -0.0069727 | -0.0041549 | -0.0030848 | -0.041199 | 0.1236 | -0.38452 | 55.1331 | 54.9408 | 54.895 | 54.744 | 55.0873 | 54.9225 | 8.4869 | 67.8955 | -54.7348 | 68.2388 | 123.4131 | 0.082398 | 76.767 | 0.064087 | 0.34332 | 123.024 | 123.3673 | 123.2208 | 68.4036 | 68.2388 | 123.2025 | 123.175 | 76.767 | 68.4036 | 68.2388 | 123.175 | 123.2208 | 123.2025 | -55.2429 | -46.3715
5773.7812 | 123.3215 | -68.3212 | 54.895 | 0.11803 | -0.009284 | -0.017752 | 0.0081882 | -0.0061181 | -0.0058639 | -0.0022302 | -0.009155 | 0.22888 | -0.3479 | 55.0186 | 54.808 | 54.7806 | 54.9271 | 54.95 | 54.9774 | 8.4824 | 67.9733 | -54.6661 | 68.3121 | 123.3398 | -0.086976 | 76.8036 | 0.082397 | 0.33874 | 123.2483 | 123.2712 | 123.1293 | 68.5501 | 68.3121 | 123.2986 | 123.1018 | 76.8036 | 68.5501 | 68.3121 | 123.1018 | 123.1293 | 123.2986 | -55.2429 | -46.4127
5774.7812 | 123.3353 | -68.2892 | 54.8904 | 0.11803 | -0.009925 | -0.023947 | 0.0062656 | -0.0063317 | -0.010136 | -0.0041528 | 0.009155 | 0.21057 | -0.32959 | 55.0507 | 54.8355 | 54.7897 | 54.9225 | 54.9911 | 54.9911 | 8.4686 | 67.9596 | -54.6799 | 68.2983 | 123.3398 | -0.054932 | 76.7578 | 0.10071 | 0.33875 | 123.2117 | 123.2803 | 123.1247 | 68.4998 | 68.2983 | 123.2803 | 123.0789 | 76.7578 | 68.4998 | 68.2983 | 123.0789 | 123.1247 | 123.2803 | -55.22 | -46.4218
5775.7812 | 123.349 | -68.2892 | 54.8767 | 0.056992 | -0.0069342 | -0.025656 | 0.0062656 | -0.0061181 | -0.0086411 | -0.0024438 | 0.027466 | 0.22888 | -0.32959 | 55.0369 | 54.8309 | 54.808 | 54.9225 | 55.0095 | 55.0049 | 8.4686 | 67.9596 | -54.6478 | 68.3167 | 123.3261 | -0.045776 | 76.7578 | 0.12817 | 0.35706 | 123.2117 | 123.2986 | 123.1201 | 68.5181 | 68.3167 | 123.2941 | 123.0972 | 76.7578 | 68.5181 | 68.3167 | 123.0972 | 123.1201 | 123.2941 | -55.2063 | -46.4081
5776.7656 | 123.3032 | -68.3166 | 54.8721 | 0.18669 | -0.0094976 | -0.026511 | 0.0060518 | -0.0073999 | -0.0069321 | -0.0039392 | -0.050354 | 0.21515 | -0.36621 | 55.0461 | 54.7806 | 54.7668 | 54.9225 | 54.9774 | 55.0049 | 8.4869 | 67.9504 | -54.657 | 68.2663 | 123.3627 | -0.091552 | 76.8036 | 0.13275 | 0.31586 | 123.2391 | 123.2941 | 123.0972 | 68.5318 | 68.2663 | 123.3215 | 123.0835 | 76.8036 | 68.5318 | 68.2663 | 123.0835 | 123.0972 | 123.3215 | -55.2383 | -46.3852
5777.7812 | 123.3994 | -68.2571 | 54.8355 | 0.18669 | -0.010779 | -0.029288 | -0.001425 | -0.0086817 | -0.0090683 | 0.00097421 | -0.050354 | 0.13733 | -0.35706 | 55.0507 | 54.8859 | 54.8584 | 54.7943 | 55.0369 | 54.95 | 8.4778 | 67.9001 | -54.6982 | 68.2068 | 123.3078 | 0.050354 | 76.7349 | 0.11444 | 0.3067 | 123.0515 | 123.2941 | 123.143 | 68.3945 | 68.2068 | 123.2071 | 123.1155 | 76.7349 | 68.3945 | 68.2068 | 123.1155 | 123.143 | 123.2071 | -55.1926 | -46.3577
5778.7812 | 123.3398 | -68.2938 | 54.8859 | -0.019302 | -0.0071478 | -0.02352 | 0.010111 | -0.0086817 | -0.0054367 | -0.001803 | 0.045776 | 0.22888 | -0.32044 | 55.0507 | 54.8355 | 54.7897 | 54.9179 | 54.9957 | 54.982 | 8.4732 | 67.9733 | -54.657 | 68.3395 | 123.3444 | -0.050354 | 76.767 | 0.096131 | 0.36621 | 123.2117 | 123.2895 | 123.1293 | 68.5226 | 68.3395 | 123.2758 | 123.0835 | 76.767 | 68.5226 | 68.3395 | 123.0835 | 123.1293 | 123.2758 | -55.2063 | -46.4127
5779.7812 | 123.3765 | -68.28 | 54.8859 | -0.10323 | -0.0088568 | -0.025015 | 0.011392 | -0.0088953 | -0.0084273 | -0.0026574 | 0.059509 | 0.24261 | -0.3067 | 55.1102 | 54.9133 | 54.9088 | 54.8584 | 55.0873 | 55.0049 | 8.4686 | 67.9733 | -54.6432 | 68.3395 | 123.3902 | 0.027466 | 76.7487 | 0.11902 | 0.36621 | 123.1384 | 123.3673 | 123.1934 | 68.5226 | 68.3395 | 123.2849 | 123.1888 | 76.7487 | 68.5226 | 68.3395 | 123.1888 | 123.1934 | 123.2849 | -55.1926 | -46.4172
5780.7812 | 123.3536 | -68.3029 | 54.8676 | 0.0035856 | -0.010352 | -0.024802 | 0.0077608 | -0.0056909 | -0.0077865 | -0.0024438 | 0.054932 | 0.23346 | -0.31586 | 55.0781 | 54.8584 | 54.8401 | 54.8996 | 55.0323 | 55.0232 | 8.4732 | 67.9871 | -54.6341 | 68.3578 | 123.381 | -0.009156 | 76.7761 | 0.15564 | 0.37079 | 123.2025 | 123.3353 | 123.1613 | 68.5364 | 68.3578 | 123.3261 | 123.143 | 76.7761 | 68.5364 | 68.3578 | 123.143 | 123.1613 | 123.3261 | -55.1834 | -46.3943
5781.7812 | 123.3582 | -68.2983 | 54.8813 | 0.072251 | -0.0080024 | -0.024802 | 0.0077608 | -0.0071863 | -0.0077865 | -0.003512 | 0.018311 | 0.23804 | -0.31586 | 55.0507 | 54.8264 | 54.8172 | 54.9133 | 55.014 | 55.0003 | 8.4732 | 67.9825 | -54.6433 | 68.3167 | 123.349 | -0.054932 | 76.7715 | 0.11902 | 0.33417 | 123.2117 | 123.3124 | 123.1247 | 68.5364 | 68.3167 | 123.2986 | 123.1155 | 76.7715 | 68.5364 | 68.3167 | 123.1155 | 123.1247 | 123.2986 | -55.1971 | -46.4081
5782.7812 | 123.381 | -68.2983 | 54.8996 | -0.072708 | -0.0084296 | -0.024161 | 0.0090426 | -0.0041955 | -0.0050095 | -0.0022302 | 0.059509 | 0.24261 | -0.32044 | 55.0827 | 54.8676 | 54.8401 | 54.9225 | 54.9774 | 55.0186 | 8.4778 | 67.9779 | -54.657 | 68.3578 | 123.381 | -0.032043 | 76.7761 | 0.11902 | 0.37994 | 123.2208 | 123.2758 | 123.1659 | 68.541 | 68.3578 | 123.317 | 123.1384 | 76.7761 | 68.541 | 68.3578 | 123.1384 | 123.1659 | 123.317 | -55.22 | -46.4218
5783.7812 | 123.3627 | -68.2983 | 54.8676 | -0.14137 | -0.0077888 | -0.026511 | 0.00712 | -0.0069727 | -0.0062911 | -0.0026574 | 0.059509 | 0.23346 | -0.2243 | 55.0735 | 54.8813 | 54.8584 | 54.895 | 55.0461 | 54.9637 | 8.4686 | 68.074 | -54.6341 | 68.3578 | 123.3719 | 0.013733 | 76.767 | 0.09613 | 0.28381 | 123.1934 | 123.3444 | 123.1796 | 68.5318 | 68.3578 | 123.262 | 123.1567 | 76.767 | 68.5318 | 68.3578 | 123.1567 | 123.1796 | 123.262 | -55.0919 | -46.3989
5784.7812 | 123.381 | -68.2755 | 54.9088 | -0.087967 | -0.0084296 | -0.026938 | 0.005411 | -0.0078271 | -0.0090683 | -0.0050074 | 0.054932 | 0.25177 | -0.3067 | 54.8721 | 54.7943 | 54.9133 | 54.9637 | 55.1239 | 55.0003 | 8.4732 | 67.9688 | -54.657 | 68.3304 | 123.1476 | -0.11444 | 76.7487 | 0.091553 | 0.36163 | 123.2391 | 123.3994 | 123.0698 | 68.5272 | 68.3304 | 123.2758 | 123.1888 | 76.7487 | 68.5272 | 68.3304 | 123.1888 | 123.0698 | 123.2758 | -55.2155 | -46.4355
5785.7812 | 123.349 | -68.2892 | 54.9088 | -0.15663 | -0.0086432 | -0.031424 | 0.0049838 | -0.0080407 | -0.0075729 | -0.0020166 | 0.022888 | 0.27924 | -0.29297 | 55.0461 | 54.8584 | 54.8309 | 54.982 | 55.0415 | 55.0415 | 8.4824 | 67.9962 | -54.6295 | 68.3121 | 123.3353 | -0.050354 | 76.7715 | 0.13275 | 0.31586 | 123.2712 | 123.3307 | 123.1476 | 68.5684 | 68.3121 | 123.3307 | 123.1201 | 76.7715 | 68.5684 | 68.3121 | 123.1201 | 123.1476 | 123.3307 | -55.2017 | -46.4264
5786.7812 | 123.3261 | -68.2846 | 54.9179 | -0.17189 | -0.0094976 | -0.02352 | 0.002634 | -0.0088953 | -0.0060775 | -0.0026574 | 0.018311 | 0.27924 | -0.29755 | 55.0461 | 54.8355 | 54.8126 | 54.9774 | 55.0369 | 55.0278 | 8.4732 | 67.9871 | -54.6387 | 68.3029 | 123.3307 | -0.082398 | 76.7578 | 0.10986 | 0.31586 | 123.262 | 123.3215 | 123.1201 | 68.5638 | 68.3029 | 123.3124 | 123.0972 | 76.7578 | 68.5638 | 68.3029 | 123.0972 | 123.1201 | 123.3124 | -55.2155 | -46.4447
5787.7812 | 123.3582 | -68.2846 | 54.8996 | -0.16426 | -0.0094976 | -0.025229 | 0.0060518 | -0.0065455 | -0.0071457 | -0.0037256 | 0.032043 | 0.28381 | -0.28839 | 55.0507 | 54.8584 | 54.8264 | 54.9911 | 55.0323 | 55.0049 | 8.4778 | 67.9962 | -54.6158 | 68.3166 | 123.3353 | -0.041199 | 76.7624 | 0.10529 | 0.32043 | 123.2758 | 123.317 | 123.143 | 68.5684 | 68.3166 | 123.2895 | 123.111 | 76.7624 | 68.5684 | 68.3166 | 123.111 | 123.143 | 123.2895 | -55.188 | -46.4218
5788.7812 | 123.3261 | -68.3258 | 54.9088 | -0.21767 | -0.009925 | -0.024802 | 0.0028476 | -0.0097497 | -0.0047957 | -0.0030848 | 0.032043 | 0.28381 | -0.27466 | 55.0415 | 54.8447 | 54.8035 | 54.982 | 55.0278 | 55.0049 | 8.4824 | 68.0511 | -54.6249 | 68.3578 | 123.3673 | -0.064086 | 76.8082 | 0.096131 | 0.3067 | 123.3078 | 123.3536 | 123.1705 | 68.6096 | 68.3578 | 123.3307 | 123.1293 | 76.8082 | 68.6096 | 68.3578 | 123.1293 | 123.1705 | 123.3307 | -55.1834 | -46.4264
5789.7812 | 123.3261 | -68.28 | 54.9225 | -0.11085 | -0.013343 | -0.027579 | 0.0028476 | -0.0099633 | -0.0050095 | -0.0050074 | 0.009155 | 0.28839 | -0.29297 | 55.0232 | 54.8126 | 54.808 | 54.9866 | 55.0323 | 54.9957 | 8.4732 | 67.9871 | -54.6341 | 68.2892 | 123.3032 | -0.10986 | 76.7532 | 0.073243 | 0.30212 | 123.2666 | 123.3124 | 123.0927 | 68.5684 | 68.2892 | 123.2758 | 123.0881 | 76.7532 | 68.5684 | 68.2892 | 123.0881 | 123.0927 | 123.2758 | -55.2155 | -46.4493
5790.7656 | 123.3765 | -68.3029 | 54.9133 | -0.13374 | -0.011207 | -0.027152 | 0.0062656 | -0.010818 | -0.0065047 | -0.0043664 | 0.018311 | 0.27924 | -0.30212 | 55.0781 | 54.8355 | 54.8264 | 54.95 | 55.0369 | 55.014 | 8.4778 | 68.0008 | -54.6341 | 68.3212 | 123.381 | -0.07782 | 76.7807 | 0.10071 | 0.32044 | 123.2529 | 123.3398 | 123.1384 | 68.5822 | 68.3212 | 123.317 | 123.1293 | 76.7807 | 68.5822 | 68.3212 | 123.1293 | 123.1384 | 123.317 | -55.2155 | -46.4355
5791.7812 | 123.3444 | -68.3212 | 54.9225 | -0.20241 | -0.009284 | -0.033347 | 0.0049838 | -0.0084681 | -0.0060775 | -0.0030848 | 0.022888 | 0.25635 | -0.31586 | 55.0507 | 54.8538 | 54.7989 | 54.9911 | 55.0186 | 55.0323 | 8.4824 | 68.0054 | -54.6661 | 68.3441 | 123.3719 | -0.068664 | 76.8036 | 0.10986 | 0.33875 | 123.3124 | 123.3398 | 123.175 | 68.5776 | 68.3441 | 123.3536 | 123.1201 | 76.8036 | 68.5776 | 68.3441 | 123.1201 | 123.175 | 123.3536 | -55.2383 | -46.4401
5792.7812 | 123.3582 | -68.2846 | 54.9042 | -0.21767 | -0.014411 | -0.027579 | -0.00057036 | -0.010818 | -0.0082137 | -0.0043664 | 0.045776 | 0.22888 | -0.29297 | 55.0735 | 54.8767 | 54.8538 | 54.9362 | 55.0735 | 54.982 | 8.4824 | 67.9916 | -54.6753 | 68.3304 | 123.3582 | -0.027466 | 76.767 | 0.07782 | 0.33874 | 123.2208 | 123.3582 | 123.1613 | 68.5135 | 68.3304 | 123.2666 | 123.1384 | 76.767 | 68.5135 | 68.3304 | 123.1384 | 123.1613 | 123.2666 | -55.1971 | -46.4218
5793.7812 | 123.4222 | -68.2617 | 54.9179 | -0.18715 | -0.012275 | -0.026511 | 0.0030612 | -0.010818 | -0.010136 | -0.0039392 | 0.068665 | 0.2243 | -0.27924 | 55.1056 | 54.9042 | 54.8767 | 54.8904 | 55.1239 | 54.9957 | 8.4824 | 67.9825 | -54.6936 | 68.3304 | 123.3673 | -0.013733 | 76.7441 | 0.07782 | 0.3479 | 123.1522 | 123.3856 | 123.1659 | 68.486 | 68.3304 | 123.2574 | 123.1384 | 76.7441 | 68.486 | 68.3304 | 123.1384 | 123.1659 | 123.2574 | -55.1971 | -46.4355
5794.7812 | 123.349 | -68.28 | 54.9133 | -0.21004 | -0.012488 | -0.027579 | 0.0030612 | -0.010818 | -0.0084273 | -0.0026574 | 0.045776 | 0.24261 | -0.28839 | 55.069 | 54.8538 | 54.8126 | 54.9316 | 55.0461 | 55.0049 | 8.4778 | 67.9916 | -54.6707 | 68.3258 | 123.349 | -0.059509 | 76.7578 | 0.091553 | 0.33417 | 123.2117 | 123.3261 | 123.1338 | 68.5226 | 68.3258 | 123.2849 | 123.0927 | 76.7578 | 68.5226 | 68.3258 | 123.0927 | 123.1338 | 123.2849 | -55.2017 | -46.4355
5795.7812 | 123.3994 | -68.28 | 54.9225 | -0.18715 | -0.013343 | -0.02587 | 0.0024202 | -0.010818 | -0.0077865 | -0.0037256 | 0.064087 | 0.2243 | -0.26093 | 55.0919 | 54.8996 | 54.8676 | 54.9042 | 55.0919 | 54.9683 | 8.4778 | 68.0191 | -54.6982 | 68.3441 | 123.3719 | -0.022888 | 76.7578 | 0.045777 | 0.32501 | 123.1842 | 123.3719 | 123.1796 | 68.5043 | 68.3441 | 123.2483 | 123.1476 | 76.7578 | 68.5043 | 68.3441 | 123.1476 | 123.1796 | 123.2483 | -55.1834 | -46.4447
5796.7656 | 123.3353 | -68.2938 | 54.9225 | -0.21004 | -0.0090704 | -0.023947 | 0.00712 | -0.013168 | -0.0075729 | -0.005221 | -0.009155 | 0.30212 | -0.24719 | 55.0461 | 54.8401 | 54.7989 | 54.9774 | 55.0323 | 55.0095 | 8.4778 | 68.0466 | -54.6204 | 68.2846 | 123.3398 | -0.082397 | 76.7715 | 0.086975 | 0.23804 | 123.2712 | 123.3261 | 123.1338 | 68.5959 | 68.2846 | 123.3032 | 123.0927 | 76.7715 | 68.5959 | 68.2846 | 123.0927 | 123.1338 | 123.3032 | -55.1697 | -46.4447
5797.7656 | 123.3398 | -68.28 | 54.9225 | -0.49995 | -0.012275 | -0.030356 | 0.005411 | -0.013168 | -0.010564 | -0.0022302 | 0.018311 | 0.26093 | -0.29297 | 55.0827 | 54.7394 | 54.7073 | 54.9545 | 55.014 | 55.0186 | 8.4732 | 67.9871 | -54.6616 | 68.2983 | 123.3627 | -0.18311 | 76.7532 | 0.096131 | 0.31128 | 123.2346 | 123.2941 | 123.0194 | 68.541 | 68.2983 | 123.2986 | 122.9874 | 76.7532 | 68.541 | 68.2983 | 122.9874 | 123.0194 | 123.2986 | -55.2155 | -46.4493
5798.7812 | 123.3994 | -68.28 | 54.8767 | -0.23293 | -0.012702 | -0.030142 | 0.0034884 | -0.012527 | -0.010136 | -0.0039392 | 0.068665 | 0.21973 | -0.27466 | 55.1102 | 54.8996 | 54.863 | 54.8859 | 55.1193 | 54.982 | 8.4824 | 68.0054 | -54.657 | 68.3487 | 123.3902 | 0.022888 | 76.7624 | 0.10529 | 0.34332 | 123.1659 | 123.3994 | 123.1796 | 68.4998 | 68.3487 | 123.262 | 123.143 | 76.7624 | 68.4998 | 68.3487 | 123.143 | 123.1796 | 123.262 | -55.1514 | -46.3943
5799.7812 | 123.4497 | -68.248 | 54.863 | 0.30113 | -0.009925 | -0.031638 | 0.0041292 | -0.010818 | -0.0077865 | -0.0043664 | 0.036621 | 0.19684 | -0.25635 | 55.1147 | 54.9362 | 54.9271 | 54.8035 | 55.1514 | 54.9408 | 8.4778 | 67.9916 | -54.6661 | 68.2846 | 123.3627 | 0.073242 | 76.7258 | 0.07782 | 0.29297 | 123.0515 | 123.3994 | 123.1842 | 68.4448 | 68.2846 | 123.1888 | 123.175 | 76.7258 | 68.4448 | 68.2846 | 123.175 | 123.1842 | 123.1888 | -55.1193 | -46.3852
5800.7812 | 123.4543 | -68.2663 | 54.8447 | -0.095596 | -0.012916 | -0.034415 | 0.0028476 | -0.013595 | -0.0077865 | -0.0024438 | 0.054932 | 0.19684 | -0.27924 | 55.1514 | 54.7668 | 55.1605 | 54.863 | 54.9133 | 54.9728 | 8.4869 | 67.9871 | -54.6478 | 68.3212 | 123.4177 | -0.07782 | 76.7532 | 0.12817 | 0.33417 | 123.1293 | 123.1796 | 123.0331 | 68.4631 | 68.3212 | 123.2391 | 123.4268 | 76.7532 | 68.4631 | 68.3212 | 123.4268 | 123.0331 | 123.2391 | -55.1239 | -46.3577
5801.7812 | 123.468 | -68.2434 | 54.8996 | -0.087967 | -0.01377 | -0.027792 | 0.0017794 | -0.014236 | -0.0080001 | -0.0026574 | 0.032043 | 0.20142 | -0.27466 | 55.1651 | 54.9225 | 54.9271 | 54.7714 | 55.1468 | 54.9362 | 8.4824 | 67.9688 | -54.6982 | 68.2755 | 123.4085 | 0.022888 | 76.7258 | 0.036621 | 0.3067 | 123.0148 | 123.3902 | 123.1659 | 68.4448 | 68.2755 | 123.1796 | 123.1705 | 76.7258 | 68.4448 | 68.2755 | 123.1705 | 123.1659 | 123.1796 | -55.1743 | -46.4172
5802.7812 | 123.4634 | -68.2617 | 54.8767 | -0.095596 | -0.012702 | -0.032065 | 0.0064792 | -0.0099633 | -0.0060775 | -0.0026574 | 0.068665 | 0.17395 | -0.2655 | 55.0964 | 54.9408 | 54.9454 | 54.7302 | 55.1514 | 54.9316 | 8.4869 | 67.9962 | -54.7028 | 68.3304 | 123.3582 | 0.064087 | 76.7487 | 0.054932 | 0.33417 | 122.9919 | 123.4131 | 123.2025 | 68.4357 | 68.3304 | 123.1934 | 123.2071 | 76.7487 | 68.4357 | 68.3304 | 123.2071 | 123.2025 | 123.1934 | -55.1422 | -46.3898
5803.7656 | 123.4268 | -68.2434 | 54.9179 | -0.15663 | -0.013984 | -0.028433 | 0.003702 | -0.014877 | -0.0073593 | -0.0056482 | 0.07782 | 0.19684 | -0.2655 | 55.1468 | 54.9042 | 54.8904 | 54.863 | 55.1147 | 54.9408 | 8.4778 | 67.9779 | -54.7211 | 68.3212 | 123.3902 | -0.013733 | 76.7212 | 0.022888 | 0.34332 | 123.1064 | 123.3582 | 123.1476 | 68.4402 | 68.3212 | 123.1842 | 123.1338 | 76.7212 | 68.4402 | 68.3212 | 123.1338 | 123.1476 | 123.1842 | -55.1834 | -46.4401
5804.7656 | 123.4451 | -68.2434 | 54.8904 | -0.16426 | -0.013557 | -0.029715 | 0.003702 | -0.013595 | -0.0086411 | -0.0032984 | 0.073242 | 0.19684 | -0.27008 | 55.1422 | 54.9316 | 54.895 | 54.8126 | 55.1331 | 54.9408 | 8.4824 | 67.9733 | -54.6936 | 68.3166 | 123.3856 | 0.041199 | 76.7258 | 0.050354 | 0.34332 | 123.056 | 123.3765 | 123.175 | 68.4402 | 68.3166 | 123.1842 | 123.1384 | 76.7258 | 68.4402 | 68.3166 | 123.1384 | 123.175 | 123.1842 | -55.1605 | -46.4081
5805.7812 | 123.468 | -68.2526 | 54.8767 | -0.011673 | -0.012702 | -0.028861 | 0.002634 | -0.013381 | -0.0090683 | -0.0015894 | 0.082397 | 0.19226 | -0.29297 | 54.982 | 54.776 | 54.8676 | 54.7348 | 55.1697 | 54.9088 | 8.4824 | 67.9596 | -54.6844 | 68.335 | 123.2346 | -0.10071 | 76.7349 | 0.032043 | 0.37537 | 122.9874 | 123.4222 | 123.0286 | 68.4448 | 68.335 | 123.1613 | 123.1201 | 76.7349 | 68.4448 | 68.335 | 123.1201 | 123.0286 | 123.1613 | -55.1697 | -46.3943
5806.7812 | 123.4406 | -68.2617 | 54.8355 | 0.041733 | -0.01377 | -0.033347 | 7.0444e-05 | -0.012954 | -0.0075729 | -0.0030848 | -0.013733 | 0.19226 | -0.30212 | 55.1193 | 54.9271 | 54.8767 | 54.7852 | 55.0919 | 54.9088 | 8.4778 | 67.9596 | -54.6432 | 68.248 | 123.381 | 0.091553 | 76.7395 | 0.073242 | 0.28839 | 123.0469 | 123.3536 | 123.1888 | 68.454 | 68.248 | 123.1705 | 123.1384 | 76.7395 | 68.454 | 68.248 | 123.1384 | 123.1888 | 123.1705 | -55.1376 | -46.3577
5807.7812 | 123.4177 | -68.2571 | 54.8721 | 0.07988 | -0.01142 | -0.03121 | 0.0034884 | -0.014877 | -0.0054367 | -0.0041528 | -0.032043 | 0.17395 | -0.31128 | 55.1102 | 54.8904 | 54.8538 | 54.7852 | 55.0644 | 54.9179 | 8.4824 | 67.9459 | -54.6982 | 68.2251 | 123.3673 | 0.018311 | 76.7395 | 0.045777 | 0.27924 | 123.0423 | 123.3215 | 123.1476 | 68.4311 | 68.2251 | 123.175 | 123.111 | 76.7395 | 68.4311 | 68.2251 | 123.111 | 123.1476 | 123.175 | -55.1834 | -46.3898
5808.7812 | 123.4451 | -68.2617 | 54.8767 | -0.011673 | -0.014197 | -0.026724 | 0.001993 | -0.0121 | -0.0056503 | -0.0013758 | 0 | 0.1831 | -0.29755 | 55.1239 | 54.9042 | 54.8813 | 54.7943 | 55.1239 | 54.9362 | 8.4824 | 67.9642 | -54.6936 | 68.2617 | 123.3856 | 0.027466 | 76.7441 | 0.059509 | 0.29755 | 123.056 | 123.3856 | 123.1659 | 68.4448 | 68.2617 | 123.1979 | 123.143 | 76.7441 | 68.4448 | 68.2617 | 123.143 | 123.1659 | 123.1979 | -55.1743 | -46.3943
5809.7812 | 123.4222 | -68.2617 | 54.8721 | 0.049362 | -0.011848 | -0.027152 | 0.00092504 | -0.013168 | -0.0071457 | -0.0037256 | -0.009155 | 0.17395 | -0.30212 | 55.101 | 54.9088 | 54.8584 | 54.7852 | 55.0919 | 54.9271 | 8.4778 | 67.9596 | -54.6982 | 68.2526 | 123.3627 | 0.036621 | 76.7395 | 0.054932 | 0.29297 | 123.0469 | 123.3536 | 123.1705 | 68.4357 | 68.2526 | 123.1888 | 123.1201 | 76.7395 | 68.4357 | 68.2526 | 123.1201 | 123.1705 | 123.1888 | -55.1743 | -46.3943
5810.7656 | 123.4726 | -68.2571 | 54.8813 | -0.04219 | -0.013557 | -0.028433 | 0.00049764 | -0.014022 | -0.0050095 | -0.006289 | 0.059509 | 0.1831 | -0.27924 | 55.1697 | 54.9408 | 54.9271 | 54.776 | 55.1468 | 54.9133 | 8.4732 | 67.9779 | -54.6982 | 68.3167 | 123.4268 | 0.059509 | 76.7303 | 0.032043 | 0.33874 | 123.0331 | 123.4039 | 123.1979 | 68.4402 | 68.3167 | 123.1705 | 123.1842 | 76.7303 | 68.4402 | 68.3167 | 123.1842 | 123.1979 | 123.1705 | -55.1605 | -46.4081
5811.7656 | 123.4726 | -68.2663 | 54.8676 | 0.011215 | -0.014197 | -0.029715 | 0.00092504 | -0.013381 | -0.0067185 | -0.005221 | 0.032043 | 0.19226 | -0.28839 | 55.1468 | 54.9225 | 54.8904 | 54.7806 | 55.1193 | 54.9179 | 8.4869 | 67.9779 | -54.6753 | 68.2983 | 123.4131 | 0.054931 | 76.7532 | 0.050354 | 0.32043 | 123.0469 | 123.3856 | 123.1888 | 68.4586 | 68.2983 | 123.1842 | 123.1567 | 76.7532 | 68.4586 | 68.2983 | 123.1567 | 123.1888 | 123.1842 | -55.1559 | -46.3806
5812.7812 | 123.4177 | -68.2755 | 54.8996 | 0.049362 | -0.013129 | -0.029074 | 0.0024202 | -0.013809 | -0.0065047 | -0.0043664 | -0.022888 | 0.15564 | -0.32501 | 55.1193 | 54.8859 | 54.8584 | 54.7989 | 55.0735 | 54.9133 | 8.4869 | 67.9504 | -54.744 | 68.2526 | 123.3948 | -0.013733 | 76.7624 | 0.013733 | 0.30212 | 123.0743 | 123.349 | 123.1613 | 68.4311 | 68.2526 | 123.1888 | 123.1338 | 76.7624 | 68.4311 | 68.2526 | 123.1338 | 123.1613 | 123.1888 | -55.2246 | -46.4127
5813.7812 | 123.3948 | -68.2709 | 54.8538 | 0.13329 | -0.012488 | -0.03057 | 0.0034884 | -0.012954 | -0.0047957 | -0.0011622 | -0.027466 | 0.11444 | -0.35248 | 55.1056 | 54.8538 | 54.8355 | 54.776 | 55.0369 | 54.9225 | 8.4778 | 67.9184 | -54.7394 | 68.2434 | 123.3765 | 0 | 76.7487 | 0.068664 | 0.32501 | 123.0469 | 123.3078 | 123.1247 | 68.3853 | 68.2434 | 123.1934 | 123.1064 | 76.7487 | 68.3853 | 68.2434 | 123.1064 | 123.1247 | 123.1934 | -55.2063 | -46.376
5814.7812 | 123.4085 | -68.2938 | 54.8584 | 0.22484 | -0.010139 | -0.028861 | 0.0032748 | -0.012954 | -0.0075729 | -0.0039392 | -0.027466 | 0.09613 | -0.36163 | 55.1056 | 54.8767 | 54.8447 | 54.7256 | 55.0369 | 54.8904 | 8.4824 | 67.9321 | -54.7623 | 68.2663 | 123.3994 | 0.018311 | 76.7761 | 0.032044 | 0.33417 | 123.0194 | 123.3307 | 123.1705 | 68.3899 | 68.2663 | 123.1842 | 123.1384 | 76.7761 | 68.3899 | 68.2663 | 123.1384 | 123.1705 | 123.1842 | -55.22 | -46.376
5815.7812 | 123.4177 | -68.2755 | 54.8538 | 0.17906 | -0.010566 | -0.031638 | 0.0024202 | -0.014449 | -0.0060775 | -0.0028712 | -0.032043 | 0.14191 | -0.32959 | 55.1193 | 54.8859 | 54.8355 | 54.776 | 55.0507 | 54.9088 | 8.4824 | 67.9459 | -54.7119 | 68.2434 | 123.3948 | 0.032043 | 76.7578 | 0.054931 | 0.29755 | 123.0515 | 123.3261 | 123.1613 | 68.4174 | 68.2434 | 123.1842 | 123.111 | 76.7578 | 68.4174 | 68.2434 | 123.111 | 123.1613 | 123.1842 | -55.1834 | -46.3715
5816.7812 | 123.4039 | -68.2663 | 54.863 | 0.20958 | -0.01142 | -0.026083 | 0.0034884 | -0.010391 | -0.0039413 | -0.0022302 | -0.045776 | 0.10071 | -0.37994 | 55.0873 | 54.8859 | 54.8584 | 54.7668 | 55.0507 | 54.8767 | 8.4778 | 67.8864 | -54.7623 | 68.2205 | 123.3536 | 0.022888 | 76.7441 | 0.013733 | 0.33417 | 123.0331 | 123.317 | 123.1522 | 68.367 | 68.2205 | 123.143 | 123.1247 | 76.7441 | 68.367 | 68.2205 | 123.1247 | 123.1522 | 123.143 | -55.2429 | -46.3852
5817.7656 | 123.4222 | -68.2892 | 54.8721 | 0.1638 | -0.01142 | -0.025015 | -0.00099756 | -0.013809 | -0.0050095 | -0.0039392 | -0.013733 | 0.17395 | -0.31128 | 55.0964 | 54.8996 | 54.8447 | 54.7852 | 55.0461 | 54.8996 | 8.4732 | 67.9779 | -54.6982 | 68.2755 | 123.3856 | 0.027466 | 76.7624 | 0.027466 | 0.29755 | 123.0743 | 123.3353 | 123.1888 | 68.4631 | 68.2755 | 123.1888 | 123.1339 | 76.7624 | 68.4631 | 68.2755 | 123.1339 | 123.1888 | 123.1888 | -55.1834 | -46.3989
5818.7656 | 123.3994 | -68.28 | 54.8447 | 0.13329 | -0.010779 | -0.028433 | 0.0024202 | -0.011886 | -0.0041549 | -0.0013758 | -0.022888 | 0.16022 | -0.32044 | 55.0827 | 54.8813 | 54.8538 | 54.7897 | 55.0507 | 54.8767 | 8.4778 | 67.9596 | -54.6844 | 68.2571 | 123.3627 | 0.036621 | 76.7578 | 0.032043 | 0.29755 | 123.0698 | 123.3307 | 123.1613 | 68.4402 | 68.2571 | 123.1567 | 123.1338 | 76.7578 | 68.4402 | 68.2571 | 123.1338 | 123.1613 | 123.1567 | -55.1651 | -46.3669
5819.7812 | 123.4085 | -68.2846 | 54.8172 | 0.22484 | -0.010352 | -0.028647 | 0.004343 | -0.01274 | -0.0060775 | -0.0037256 | -0.032043 | 0.09613 | -0.37994 | 55.0964 | 54.8721 | 54.8584 | 54.7348 | 55.0507 | 54.8767 | 8.4778 | 67.9047 | -54.7211 | 68.2526 | 123.381 | 0.054931 | 76.7624 | 0.059509 | 0.3479 | 123.0194 | 123.3353 | 123.1567 | 68.3807 | 68.2526 | 123.1613 | 123.143 | 76.7624 | 68.3807 | 68.2526 | 123.143 | 123.1567 | 123.1613 | -55.1971 | -46.3394
5820.7812 | 123.4543 | -68.2571 | 54.8218 | 0.23247 | -0.009284 | -0.028433 | 0.00712 | -0.010177 | -0.0080001 | -0.0050074 | 0.018311 | 0.10071 | -0.35706 | 55.1331 | 54.8813 | 54.8904 | 54.6982 | 55.0507 | 54.8767 | 8.4778 | 67.9001 | -54.7211 | 68.2755 | 123.3902 | 0.05951 | 76.7349 | 0.054932 | 0.37537 | 122.9553 | 123.3078 | 123.1384 | 68.3578 | 68.2755 | 123.1338 | 123.1476 | 76.7349 | 68.3578 | 68.2755 | 123.1476 | 123.1384 | 123.1338 | -55.1788 | -46.344

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.3865 | 23.7506 | 23.335 | 23.5127
0.6135 | 23.7492 | 23.3323 | 23.5173
1.6135 | 23.7617 | 23.3189 | 23.5113
2.6135 | 23.7866 | 23.3238 | 23.5131
3.6135 | 24.1361 | 23.3209 | 23.5183
4.6135 | 25.1545 | 23.3303 | 23.5161
5.6135 | 26.8884 | 23.3288 | 23.5249
6.6135 | 29.2621 | 23.3503 | 23.5392
7.6135 | 32.161 | 23.3764 | 23.5577
8.6135 | 35.4821 | 23.4183 | 23.5875
9.6135 | 39.2248 | 23.4376 | 23.6342
10.6135 | 43.231 | 23.4941 | 23.6849
11.6135 | 47.5409 | 23.5596 | 23.7473
12.6135 | 52.0691 | 23.6354 | 23.8183
13.6135 | 56.8482 | 23.7105 | 23.897
14.6135 | 61.7528 | 23.8197 | 23.9946
15.6135 | 66.7879 | 23.9367 | 24.116
16.6135 | 71.9673 | 24.0616 | 24.2428
17.6135 | 77.3139 | 24.2026 | 24.4008
18.6135 | 82.7887 | 24.3624 | 24.5427
19.6135 | 88.322 | 24.5306 | 24.7184
20.6135 | 93.885 | 24.7134 | 24.8986
21.6135 | 99.5264 | 24.9147 | 25.1202
22.6135 | 105.3364 | 25.1233 | 25.3458
23.6135 | 111.091 | 25.3466 | 25.5823
24.6135 | 116.8947 | 25.6039 | 25.8417
25.6135 | 122.8252 | 25.867 | 26.1293
26.6135 | 128.7309 | 26.1595 | 26.4366
27.6135 | 134.5756 | 26.4581 | 26.7547
28.6135 | 140.454 | 26.7593 | 27.0804
29.6135 | 146.4169 | 27.0691 | 27.4121
30.6135 | 152.3282 | 27.4387 | 27.778
31.6135 | 158.1379 | 27.7979 | 28.1494
32.6135 | 164.1046 | 28.1948 | 28.5589
33.6135 | 170.0936 | 28.5995 | 29.005
34.6135 | 176.0967 | 29.024 | 29.4714
35.6135 | 182.002 | 29.4778 | 29.9773
36.6135 | 187.8978 | 29.9647 | 30.4894
37.6135 | 193.7203 | 30.426 | 31.0337
38.6135 | 199.542 | 31.0027 | 31.5833
39.6135 | 205.4643 | 31.5537 | 32.158
40.6135 | 211.2239 | 32.1034 | 32.734
41.6135 | 217.0251 | 32.6926 | 33.3239
42.6135 | 222.7407 | 33.3039 | 33.9393
43.6135 | 228.538 | 33.9344 | 34.5837
44.6135 | 234.3623 | 34.5946 | 35.2336
45.6135 | 239.9892 | 35.2737 | 35.9123
46.6135 | 245.5391 | 35.9776 | 36.6355
47.6135 | 251.1728 | 36.7022 | 37.398
48.6135 | 256.7176 | 37.4681 | 38.2048
49.6135 | 262.2777 | 38.2445 | 39.0319
50.6135 | 267.959 | 39.0462 | 39.8732
51.6135 | 273.6076 | 39.8973 | 40.7636
52.6135 | 279.0777 | 40.7517 | 41.6658
53.6135 | 284.3294 | 41.6537 | 42.5659
54.6135 | 289.0913 | 42.5606 | 43.4878
55.6135 | 293.4049 | 43.4848 | 44.3548
56.6135 | 297.5856 | 44.4062 | 45.2436
57.6135 | 301.3638 | 45.3351 | 46.1662
58.6135 | 304.9945 | 46.2522 | 47.0705
59.6135 | 308.6282 | 47.1967 | 47.9727
60.6135 | 312.0609 | 48.144 | 48.904
61.6135 | 315.2572 | 49.0886 | 49.8701
62.6135 | 318.1257 | 50.0487 | 50.8121
63.6135 | 320.6101 | 51.0255 | 51.7349
64.6135 | 322.842 | 52.0037 | 52.6555
65.6135 | 324.945 | 52.9336 | 53.5837
66.6135 | 326.5394 | 53.8863 | 54.5214
67.6135 | 327.9451 | 54.8136 | 55.4395
68.6135 | 328.9926 | 55.7614 | 56.3251
69.6135 | 329.9 | 56.6714 | 57.2016
70.6135 | 330.6934 | 57.5606 | 58.0694
71.6135 | 331.351 | 58.4269 | 58.9563
72.6135 | 331.8298 | 59.2815 | 59.7903
73.6135 | 332.1653 | 60.0843 | 60.607
74.6135 | 332.2935 | 60.8905 | 61.4375
75.6135 | 332.3411 | 61.6763 | 62.2482
76.6135 | 332.3843 | 62.4641 | 63.0348
77.6135 | 332.2312 | 63.2373 | 63.8366
78.6135 | 332.1041 | 63.9751 | 64.6063
79.6135 | 331.9371 | 64.7084 | 65.3416
80.6135 | 331.597 | 65.3996 | 66.0681
81.6135 | 331.2491 | 66.0997 | 66.7697
82.6135 | 330.9579 | 66.7705 | 67.4762
83.6135 | 330.6242 | 67.4827 | 68.2063
84.6135 | 330.232 | 68.1746 | 68.8987
85.6135 | 329.9238 | 68.8528 | 69.5604
86.6135 | 329.58 | 69.5207 | 70.217
87.6135 | 329.035 | 70.1903 | 70.8728
88.6135 | 328.6305 | 70.8619 | 71.519
89.6135 | 328.0009 | 71.5241 | 72.1768
90.6135 | 327.6088 | 72.1811 | 72.8073
91.6135 | 327.1753 | 72.7853 | 73.4304
92.6135 | 326.6593 | 73.4409 | 74.078
93.6135 | 326.3195 | 74.0545 | 74.6829
94.6135 | 326.0495 | 74.6487 | 75.2797
95.6135 | 325.8491 | 75.2175 | 75.8579
96.6135 | 325.3864 | 75.7753 | 76.4249
97.6135 | 324.8522 | 76.3314 | 76.9879
98.6135 | 324.5429 | 76.9209 | 77.561
99.6135 | 324.2031 | 77.5255 | 78.1604
100.6135 | 323.8495 | 78.086 | 78.7322
101.6135 | 323.3543 | 78.6371 | 79.2876
102.6135 | 323.0078 | 79.1683 | 79.8385
103.6135 | 322.8134 | 79.7065 | 80.3943
104.6135 | 322.5923 | 80.2478 | 80.9368
105.6135 | 322.3502 | 80.7871 | 81.4847
106.6135 | 322.1558 | 81.3196 | 82.0118
107.6135 | 322.1399 | 81.8541 | 82.5684
108.6135 | 322.1132 | 82.3745 | 83.105
109.6135 | 322.0429 | 82.8989 | 83.644
110.6135 | 321.9841 | 83.409 | 84.1817
111.6135 | 322.0034 | 83.9048 | 84.7061
112.6135 | 322.135 | 84.419 | 85.253
113.6135 | 322.3057 | 84.9331 | 85.7923
114.6135 | 322.5494 | 85.4654 | 86.3507
115.6135 | 322.7682 | 85.9956 | 86.9235
116.6135 | 322.8449 | 86.5331 | 87.4688
117.6135 | 323.0447 | 87.056 | 87.9942
118.6135 | 323.3095 | 87.5752 | 88.4986
119.6135 | 323.479 | 88.0839 | 89.0235
120.6135 | 323.7727 | 88.5887 | 89.5496
121.6135 | 323.9943 | 89.1229 | 90.0962
122.6135 | 324.189 | 89.632 | 90.6189
123.6135 | 324.3534 | 90.1588 | 91.1505
124.6135 | 324.5889 | 90.6928 | 91.6746
125.6135 | 324.8582 | 91.2134 | 92.2122
126.6135 | 325.1363 | 91.7535 | 92.7678
127.6135 | 325.2881 | 92.2737 | 93.3326
128.6135 | 325.5325 | 92.8049 | 93.8981
129.6135 | 325.7044 | 93.3378 | 94.449
130.6135 | 325.9057 | 93.8255 | 94.9846
131.6135 | 326.0441 | 94.3295 | 95.5269
132.6135 | 326.3139 | 94.8464 | 96.0892
133.6135 | 326.6512 | 95.375 | 96.651
134.6135 | 326.8647 | 95.9264 | 97.1992
135.6135 | 327.0248 | 96.4502 | 97.7466
136.6135 | 327.2806 | 96.9746 | 98.2872
137.6135 | 327.4408 | 97.5016 | 98.8287
138.6135 | 327.5142 | 98.0328 | 99.3717
139.6135 | 327.6333 | 98.5693 | 99.9162
140.6135 | 327.7868 | 99.1164 | 100.485
141.6135 | 327.8194 | 99.6332 | 101.004
142.6135 | 327.8538 | 100.1751 | 101.5158
143.6135 | 327.8896 | 100.7005 | 102.0659
144.6135 | 327.9609 | 101.2219 | 102.5862
145.6135 | 327.9304 | 101.7442 | 103.1071
146.6135 | 327.9314 | 102.2699 | 103.6302
147.6135 | 328.065 | 102.8024 | 104.1581
148.6135 | 328.2776 | 103.3314 | 104.6646
149.6135 | 328.181 | 103.8349 | 105.1502
150.6135 | 328.0935 | 104.3668 | 105.6714
151.6135 | 328.0362 | 104.8524 | 106.178
152.6135 | 328.171 | 105.3737 | 106.6976
153.6135 | 328.2321 | 105.8804 | 107.218
154.6135 | 328.2797 | 106.3849 | 107.7138
155.6135 | 328.1592 | 106.8445 | 108.1568
156.6135 | 328.0873 | 107.3289 | 108.5959
157.6135 | 328.2269 | 107.8003 | 109.0687
158.6135 | 328.2295 | 108.2555 | 109.5435
159.6135 | 328.241 | 108.6986 | 110.0352
160.6135 | 328.1669 | 109.1343 | 110.4915
161.6135 | 328.0194 | 109.5789 | 110.9255
162.6135 | 328.0227 | 110.0282 | 111.393
163.6135 | 327.9455 | 110.4779 | 111.8772
164.6135 | 327.9609 | 110.9509 | 112.3797
165.6135 | 327.91 | 111.4252 | 112.8732
166.6135 | 327.8725 | 111.8488 | 113.366
167.6135 | 327.867 | 112.3108 | 113.8684
168.6135 | 327.7623 | 112.7607 | 114.3634
169.6135 | 327.7253 | 113.234 | 114.8841
170.6135 | 327.7312 | 113.7264 | 115.4215
171.6135 | 327.7506 | 114.2009 | 115.9172
172.6135 | 327.7658 | 114.6771 | 116.4139
173.6135 | 327.8096 | 115.1588 | 116.8983
174.6135 | 327.8013 | 115.608 | 117.4017
175.6135 | 327.8919 | 116.1054 | 117.8515
176.6135 | 327.9099 | 116.5916 | 118.304
177.6135 | 327.9702 | 117.0849 | 118.7698
178.6135 | 328.082 | 117.5618 | 119.2496
179.6135 | 327.9306 | 118.0291 | 119.7239
180.6135 | 327.917 | 118.4905 | 120.2156
181.6135 | 327.8557 | 118.9175 | 120.6777
182.6135 | 327.7865 | 119.3941 | 121.1292
183.6135 | 327.7558 | 119.8035 | 121.5329
184.6135 | 327.7626 | 120.2181 | 121.9379
185.6135 | 327.7655 | 120.6281 | 122.364
186.6135 | 327.8194 | 121.0551 | 122.7976
187.6135 | 327.786 | 121.5061 | 123.2568
188.6135 | 327.7724 | 121.952 | 123.7071
189.6135 | 327.64 | 122.3719 | 124.1107
190.6135 | 327.7056 | 122.7762 | 124.5052
191.6135 | 327.6542 | 123.2215 | 124.872
192.6135 | 327.673 | 123.6537 | 125.2582
193.6135 | 327.7662 | 124.0942 | 125.683
194.6135 | 327.7619 | 124.5555 | 126.1144
195.6135 | 327.6997 | 124.9855 | 126.578
196.6135 | 327.7227 | 125.4096 | 127.0473
197.6135 | 327.8145 | 125.8541 | 127.5077
198.6135 | 327.7647 | 126.2861 | 127.9114
199.6135 | 327.7621 | 126.7267 | 128.3189
200.6135 | 327.6742 | 127.1229 | 128.7476
201.6135 | 327.6309 | 127.4853 | 129.1742
202.6135 | 327.4318 | 127.8983 | 129.6239
203.6135 | 327.3006 | 128.3222 | 130.0921
204.6135 | 327.2674 | 128.7471 | 130.5525
205.6135 | 327.2493 | 129.1423 | 131.0101
206.6135 | 327.0813 | 129.5334 | 131.4392
207.6135 | 326.9298 | 129.9282 | 131.8263
208.6135 | 326.9321 | 130.3218 | 132.2226
209.6135 | 326.897 | 130.7017 | 132.6385
210.6135 | 326.9753 | 131.0466 | 133.0654
211.6135 | 326.8814 | 131.4474 | 133.5181
212.6135 | 326.7849 | 131.8273 | 133.9266
213.6135 | 326.7086 | 132.2073 | 134.3509
214.6135 | 326.6533 | 132.5752 | 134.7745
215.6135 | 326.7477 | 132.9608 | 135.1869
216.6135 | 326.7992 | 133.3405 | 135.5751
217.6135 | 326.7067 | 133.6942 | 135.9615
218.6135 | 326.6944 | 134.0302 | 136.3081
219.6135 | 326.7735 | 134.376 | 136.6586
220.6135 | 326.8375 | 134.7247 | 137.0138
221.6135 | 326.7337 | 135.0876 | 137.3939
222.6135 | 326.6373 | 135.4321 | 137.7396
223.6135 | 326.7128 | 135.7687 | 138.1224
224.6135 | 326.7751 | 136.1393 | 138.5119
225.6135 | 326.805 | 136.5464 | 138.9197
226.6135 | 326.8295 | 136.9363 | 139.3153
227.6135 | 326.9136 | 137.2794 | 139.7037
228.6135 | 326.9989 | 137.6283 | 140.1165
229.6135 | 327.087 | 138.04 | 140.5148
230.6135 | 327.0367 | 138.4297 | 140.9063
231.6135 | 327.0914 | 138.7804 | 141.2923
232.6135 | 327.1321 | 139.0805 | 141.6856
233.6135 | 327.103 | 139.3659 | 142.0835
234.6135 | 327.2432 | 139.6821 | 142.5182
235.6135 | 327.345 | 140.0173 | 142.9335
236.6135 | 327.4477 | 140.3593 | 143.3452
237.6135 | 327.48 | 140.6908 | 143.7519
238.6135 | 327.5253 | 141.0236 | 144.1374
239.6135 | 327.5164 | 141.3564 | 144.5034
240.6135 | 327.5075 | 141.7117 | 144.8663
241.6135 | 327.2935 | 142.0604 | 145.2178
242.6135 | 327.1672 | 142.4303 | 145.5615
243.6135 | 327.142 | 142.7566 | 145.9231
244.6135 | 327.1545 | 143.0894 | 146.2907
245.6135 | 327.1725 | 143.5014 | 146.6762
246.6135 | 327.1924 | 143.9078 | 147.0721
247.6135 | 327.2933 | 144.3174 | 147.4818
248.6135 | 327.299 | 144.6872 | 147.8528
249.6135 | 327.2716 | 145.0608 | 148.2201
250.6135 | 327.3462 | 145.419 | 148.6073
251.6135 | 327.3361 | 145.8035 | 148.9794
252.6135 | 327.3357 | 146.1478 | 149.2986
253.6135 | 327.3271 | 146.4729 | 149.6159
254.6135 | 327.3012 | 146.8366 | 149.9853
255.6135 | 327.1087 | 147.1679 | 150.3475
256.6135 | 326.97 | 147.4639 | 150.6723
257.6135 | 327.0199 | 147.7934 | 151.039
258.6135 | 326.9908 | 148.1203 | 151.3875
259.6135 | 326.9175 | 148.4526 | 151.6922
260.6135 | 326.8137 | 148.7712 | 152.0007
261.6135 | 326.8701 | 149.058 | 152.3422
262.6135 | 326.909 | 149.4119 | 152.7103
263.6135 | 326.851 | 149.7437 | 153.0895
264.6135 | 326.8265 | 150.0539 | 153.465
265.6135 | 326.93 | 150.3778 | 153.8408
266.6135 | 326.9235 | 150.7366 | 154.1811
267.6135 | 326.9126 | 151.0783 | 154.4918
268.6135 | 326.9806 | 151.393 | 154.7839
269.6135 | 326.9696 | 151.706 | 155.095
270.6135 | 326.8813 | 152.0466 | 155.4192
271.6135 | 326.8381 | 152.3817 | 155.7381
272.6135 | 326.7019 | 152.6758 | 156.0672
273.6135 | 326.5906 | 152.9631 | 156.3824
274.6135 | 326.5904 | 153.2769 | 156.7147
275.6135 | 326.4303 | 153.6131 | 157.0695
276.6135 | 326.2135 | 153.9431 | 157.403
277.6135 | 326.2957 | 154.2828 | 157.7208
278.6135 | 326.4169 | 154.6016 | 158.0514
279.6135 | 326.3765 | 154.8764 | 158.3696
280.6135 | 326.4068 | 155.176 | 158.6843
281.6135 | 326.5235 | 155.5135 | 159.0186
282.6135 | 326.6794 | 155.8288 | 159.3517
283.6135 | 326.7739 | 156.0993 | 159.6673
284.6135 | 326.7758 | 156.4513 | 159.9672
285.6135 | 326.7683 | 156.8198 | 160.2536
286.6135 | 326.682 | 157.1432 | 160.5817
287.6135 | 326.518 | 157.418 | 160.906
288.6135 | 326.5628 | 157.6677 | 161.2226
289.6135 | 326.7373 | 157.9199 | 161.4808
290.6135 | 326.8652 | 158.2006 | 161.7361
291.6135 | 326.9287 | 158.4815 | 162.0317
292.6135 | 326.8727 | 158.7691 | 162.3296
293.6135 | 326.8933 | 159.0608 | 162.5948
294.6135 | 326.9691 | 159.3405 | 162.8712
295.6135 | 327.1987 | 159.5661 | 163.1932
296.6135 | 327.2794 | 159.8091 | 163.5436
297.6135 | 327.2963 | 160.0874 | 163.8755
298.6135 | 327.375 | 160.3504 | 164.2057
299.6135 | 327.4673 | 160.6041 | 164.5523
300.6135 | 327.524 | 160.8789 | 164.8969
301.6135 | 327.6782 | 161.1418 | 165.218
302.6135 | 327.6471 | 161.4208 | 165.5331
303.6135 | 327.5937 | 161.7281 | 165.8564
304.6135 | 327.6033 | 162.0336 | 166.1895
305.6135 | 327.6043 | 162.2718 | 166.5318
306.6135 | 327.5641 | 162.5231 | 166.8215
307.6135 | 327.6208 | 162.8172 | 167.0728
308.6135 | 327.6147 | 163.1014 | 167.3659
309.6135 | 327.7056 | 163.4076 | 167.6743
310.6135 | 327.6166 | 163.7393 | 167.9688
311.6135 | 327.4305 | 164.0325 | 168.2788
312.6135 | 327.3785 | 164.326 | 168.6003
313.6135 | 327.343 | 164.5843 | 168.9007
314.6135 | 327.4573 | 164.8795 | 169.1938
315.6135 | 327.4516 | 165.1444 | 169.4879
316.6135 | 327.24 | 165.4007 | 169.7657
317.6135 | 327.1099 | 165.7033 | 170.0264
318.6135 | 326.9616 | 165.8789 | 170.2422
319.6135 | 326.8389 | 166.0646 | 170.4757
320.6135 | 326.7678 | 166.2915 | 170.6867
321.6135 | 326.8088 | 166.5659 | 170.9332
322.6135 | 326.8068 | 166.9017 | 171.1649
323.6135 | 326.9314 | 167.2183 | 171.386
324.6135 | 327.0958 | 167.539 | 171.6455
325.6135 | 327.0818 | 167.7904 | 171.908
326.6135 | 326.9403 | 168.0459 | 172.2214
327.6135 | 326.8181 | 168.3063 | 172.5431
328.6135 | 326.8783 | 168.5541 | 172.856
329.6135 | 326.8351 | 168.8244 | 173.1704
330.6135 | 326.6793 | 169.0967 | 173.4719
331.6135 | 326.6055 | 169.2953 | 173.7796
332.6135 | 326.3722 | 169.5743 | 174.0636
333.6135 | 326.3388 | 169.8681 | 174.2943
334.6135 | 326.4231 | 170.1503 | 174.516
335.6135 | 326.2429 | 170.4362 | 174.7149
336.6135 | 326.2614 | 170.6725 | 174.9418
337.6135 | 326.213 | 170.9051 | 175.1755
338.6135 | 326.194 | 171.1847 | 175.4337
339.6135 | 326.1275 | 171.451 | 175.666
340.6135 | 326.1637 | 171.658 | 175.8901
341.6135 | 326.0947 | 171.8922 | 176.0982
342.6135 | 326.1768 | 172.0882 | 176.3132
343.6135 | 326.3199 | 172.3384 | 176.5647
344.6135 | 326.286 | 172.5215 | 176.8243
345.6135 | 326.27 | 172.6798 | 177.0748
346.6135 | 326.4376 | 172.8912 | 177.3059
347.6135 | 326.3973 | 173.1648 | 177.5458
348.6135 | 326.2311 | 173.3819 | 177.7972
349.6135 | 326.1628 | 173.604 | 178.0452
350.6135 | 326.2507 | 173.8287 | 178.2613
351.6135 | 326.5041 | 174.0925 | 178.5073
352.6135 | 326.5638 | 174.3322 | 178.771
353.6135 | 326.5424 | 174.5776 | 179.0089
354.6135 | 326.5036 | 174.8072 | 179.276
355.6135 | 326.5529 | 175.0854 | 179.5351
356.6135 | 326.6413 | 175.3532 | 179.7925
357.6135 | 326.5932 | 175.5707 | 180.0242
358.6135 | 326.4529 | 175.7421 | 180.2561
359.6135 | 326.3566 | 175.9053 | 180.4898
360.6135 | 326.3596 | 176.0916 | 180.6836
361.6135 | 326.3588 | 176.2858 | 180.9022
362.6135 | 326.3101 | 176.4882 | 181.1234
363.6135 | 326.3093 | 176.7414 | 181.3363
364.6135 | 326.1937 | 176.9628 | 181.5438
365.6135 | 326.216 | 177.1458 | 181.7431
366.6135 | 326.1688 | 177.3515 | 181.9632
367.6135 | 326.1255 | 177.5779 | 182.1906
368.6135 | 326.1646 | 177.7795 | 182.4274
369.6135 | 326.232 | 178.0595 | 182.651
370.6135 | 326.309 | 178.3008 | 182.8706
371.6135 | 326.3741 | 178.574 | 183.0979
372.6135 | 326.5061 | 178.7827 | 183.3109
373.6135 | 326.6325 | 179.0385 | 183.5153
374.6135 | 326.6584 | 179.2767 | 183.6514
375.6135 | 326.6553 | 179.5559 | 183.7731
376.6135 | 326.5935 | 179.8041 | 183.9199
377.6135 | 326.5386 | 180.0629 | 184.1082
378.6135 | 326.6226 | 180.3509 | 184.28
379.6135 | 326.6511 | 180.6333 | 184.4693
380.6135 | 326.665 | 180.818 | 184.6853
381.6135 | 326.6625 | 180.9359 | 184.8654
382.6135 | 326.5764 | 181.0914 | 185.03
383.6135 | 326.5616 | 181.2934 | 185.2084
384.6135 | 326.3557 | 181.453 | 185.4325
385.6135 | 326.2258 | 181.6115 | 185.6731
386.6135 | 326.1937 | 181.7451 | 185.9283
387.6135 | 326.2318 | 181.9164 | 186.1463
388.6135 | 326.2311 | 182.0208 | 186.3943
389.6135 | 326.1635 | 182.1294 | 186.6372
390.6135 | 326.0336 | 182.2315 | 186.8442
391.6135 | 325.8986 | 182.3754 | 187.0302
392.6135 | 325.9217 | 182.5517 | 187.2377
393.6135 | 325.8897 | 182.71 | 187.4433
394.6135 | 325.9292 | 182.8688 | 187.6462
395.6135 | 325.9753 | 183.062 | 187.8423
396.6135 | 326.0433 | 183.2518 | 188.0315
397.6135 | 325.9307 | 183.4537 | 188.2021
398.6135 | 325.861 | 183.6785 | 188.3324
399.6135 | 325.9427 | 183.933 | 188.4757
400.6135 | 325.9749 | 184.2138 | 188.6408
401.6135 | 325.9629 | 184.47 | 188.8532
402.6135 | 326.0204 | 184.7435 | 189.071
403.6135 | 326.0526 | 184.9496 | 189.2816
404.6135 | 326.1432 | 185.1271 | 189.4992
405.6135 | 326.2072 | 185.2765 | 189.7043
406.6135 | 326.1543 | 185.4128 | 189.9121
407.6135 | 326.2249 | 185.6088 | 190.1413
408.6135 | 326.1874 | 185.7963 | 190.3391
409.6135 | 326.1652 | 185.9796 | 190.5164
410.6135 | 326.205 | 186.186 | 190.6917
411.6135 | 326.0711 | 186.3756 | 190.8601
412.6135 | 326.0502 | 186.5614 | 191.0003
413.6135 | 325.8281 | 186.7322 | 191.1482
414.6135 | 325.8902 | 186.9026 | 191.2949
415.6135 | 325.9293 | 187.0612 | 191.4337
416.6135 | 325.9941 | 187.2008 | 191.5309
417.6135 | 326.05 | 187.3783 | 191.6541
418.6135 | 326.1021 | 187.5304 | 191.817
419.6135 | 326.0347 | 187.692 | 192.0272
420.6135 | 326.0028 | 187.8443 | 192.2464
421.6135 | 325.8803 | 187.9721 | 192.4808
422.6135 | 325.8253 | 188.054 | 192.677
423.6135 | 325.8457 | 188.1947 | 192.834
424.6135 | 325.917 | 188.3362 | 192.9756
425.6135 | 325.9621 | 188.4675 | 193.1304
426.6135 | 325.9722 | 188.6341 | 193.2525
427.6135 | 325.9734 | 188.8218 | 193.3493
428.6135 | 325.9154 | 189.0244 | 193.4232
429.6135 | 325.9225 | 189.2428 | 193.5244
430.6135 | 325.9056 | 189.441 | 193.6863
431.6135 | 325.8441 | 189.6011 | 193.8693
432.6135 | 325.7705 | 189.7387 | 194.0417
433.6135 | 325.8107 | 189.8747 | 194.2235
434.6135 | 325.8643 | 190.0536 | 194.3933
435.6135 | 325.8905 | 190.2372 | 194.567
436.6135 | 325.9871 | 190.4389 | 194.7103
437.6135 | 325.9411 | 190.6006 | 194.8494
438.6135 | 325.9264 | 190.7523 | 195.02
439.6135 | 325.7742 | 190.8789 | 195.2024
440.6135 | 325.6698 | 191.0109 | 195.4059
441.6135 | 325.7238 | 191.1457 | 195.6059
442.6135 | 325.8282 | 191.3028 | 195.8054
443.6135 | 325.9157 | 191.4596 | 196.011
444.6135 | 325.9673 | 191.6143 | 196.2019
445.6135 | 325.9617 | 191.8099 | 196.3789
446.6135 | 325.9269 | 192.0362 | 196.5686
447.6135 | 325.8845 | 192.258 | 196.7045
448.6135 | 325.8797 | 192.4316 | 196.8396
449.6135 | 326.0065 | 192.6028 | 196.9841
450.6135 | 325.99 | 192.7764 | 197.1685
451.6135 | 325.9699 | 192.9463 | 197.3202
452.6135 | 325.9995 | 193.0979 | 197.4641
453.6135 | 326.0498 | 193.1552 | 197.6374
454.6135 | 326.1109 | 193.2075 | 197.8108
455.6135 | 326.1602 | 193.2985 | 197.9512
456.6135 | 326.0591 | 193.3913 | 198.1066
457.6135 | 326.0651 | 193.4887 | 198.2441
458.6135 | 326.1283 | 193.6263 | 198.4101
459.6135 | 326.1088 | 193.7887 | 198.5907
460.6135 | 326.1162 | 193.9318 | 198.7672
461.6135 | 326.2229 | 194.0723 | 198.91
462.6135 | 326.2211 | 194.2396 | 199.0114
463.6135 | 326.286 | 194.4186 | 199.1259
464.6135 | 326.3436 | 194.5958 | 199.2829
465.6135 | 326.2774 | 194.7761 | 199.4253
466.6135 | 326.1903 | 194.9592 | 199.5861
467.6135 | 326.095 | 195.1157 | 199.7414
468.6135 | 326.0834 | 195.2791 | 199.8782
469.6135 | 326.0256 | 195.4323 | 199.9927
470.6135 | 326.0438 | 195.6218 | 200.1215
471.6135 | 326.033 | 195.8116 | 200.2711
472.6135 | 326.0683 | 195.973 | 200.4322
473.6135 | 326.1612 | 196.1344 | 200.5914
474.6135 | 326.3142 | 196.316 | 200.7257
475.6135 | 326.2456 | 196.492 | 200.8613
476.6135 | 326.207 | 196.6527 | 201.0017
477.6135 | 326.1782 | 196.7561 | 201.1828
478.6135 | 326.177 | 196.8281 | 201.3787
479.6135 | 326.1707 | 196.8667 | 201.5431
480.6135 | 326.2638 | 196.9194 | 201.6973
481.6135 | 326.3758 | 196.9921 | 201.833
482.6135 | 326.4662 | 197.073 | 201.9927
483.6135 | 326.2649 | 197.1726 | 202.1523
484.6135 | 326.2496 | 197.2915 | 202.2829
485.6135 | 326.2154 | 197.4014 | 202.458
486.6135 | 326.1701 | 197.5261 | 202.6122
487.6135 | 326.036 | 197.6747 | 202.7862
488.6135 | 326.0478 | 197.8455 | 202.9747
489.6135 | 326.114 | 198.0081 | 203.1639
490.6135 | 326.0621 | 198.1339 | 203.3592
491.6135 | 326.0351 | 198.3152 | 203.5168
492.6135 | 326.0298 | 198.4957 | 203.6709
493.6135 | 326.102 | 198.6612 | 203.8237
494.6135 | 326.1465 | 198.8305 | 203.9433
495.6135 | 326.0525 | 198.9341 | 204.0607
496.6135 | 325.8586 | 199.0296 | 204.1799
497.6135 | 325.8855 | 199.1304 | 204.324
498.6135 | 325.9113 | 199.187 | 204.4608
499.6135 | 325.8399 | 199.3215 | 204.6128
500.6135 | 325.929 | 199.4701 | 204.7435
501.6135 | 325.9779 | 199.5995 | 204.8556
502.6135 | 325.8893 | 199.7103 | 204.9594
503.6135 | 325.8492 | 199.8448 | 205.024
504.6135 | 325.8262 | 199.9884 | 205.0655
505.6135 | 325.7403 | 200.1387 | 205.1762
506.6135 | 325.7166 | 200.2755 | 205.296
507.6135 | 325.6353 | 200.4258 | 205.3716
508.6135 | 325.5544 | 200.5843 | 205.4205
509.6135 | 325.5157 | 200.6865 | 205.4505
510.6135 | 325.5716 | 200.7605 | 205.4746
511.6135 | 325.5717 | 200.8514 | 205.5157
512.6135 | 325.5525 | 200.9206 | 205.5496
513.6135 | 325.5842 | 200.9921 | 205.6041
514.6135 | 325.555 | 201.1373 | 205.6489
515.6135 | 325.5104 | 201.2774 | 205.7072
516.6135 | 325.6382 | 201.3954 | 205.7846
517.6135 | 325.675 | 201.511 | 205.8933
518.6135 | 325.6959 | 201.6399 | 205.998
519.6135 | 325.7227 | 201.745 | 206.1214
520.6135 | 325.7512 | 201.8209 | 206.2644
521.6135 | 325.8574 | 201.8927 | 206.4059
522.6135 | 325.9742 | 201.9524 | 206.5237
523.6135 | 325.9877 | 202.0064 | 206.6181
524.6135 | 326.1208 | 202.0817 | 206.7272
525.6135 | 326.1463 | 202.2008 | 206.8731
526.6135 | 326.1126 | 202.3667 | 206.9936
527.6135 | 326.202 | 202.5406 | 207.1086
528.6135 | 326.1692 | 202.6793 | 207.2483
529.6135 | 326.3631 | 202.7966 | 207.4005
530.6135 | 326.4422 | 202.8957 | 207.5698
531.6135 | 326.3555 | 203.0032 | 207.7108
532.6135 | 326.3332 | 203.1058 | 207.8141
533.6135 | 326.2574 | 203.1899 | 207.9173
534.6135 | 326.2165 | 203.284 | 208.0304
535.6135 | 326.2016 | 203.4207 | 208.1669
536.6135 | 326.1191 | 203.5861 | 208.2898
537.6135 | 326.0774 | 203.7163 | 208.3933
538.6135 | 326.0132 | 203.7973 | 208.518
539.6135 | 325.9432 | 203.8969 | 208.6625
540.6135 | 325.8899 | 203.9549 | 208.8269
541.6135 | 325.9125 | 204.0419 | 208.9955
542.6135 | 325.8515 | 204.1183 | 209.1339
543.6135 | 325.7925 | 204.2431 | 209.2215
544.6135 | 325.8776 | 204.3867 | 209.2918
545.6135 | 325.7791 | 204.521 | 209.3494
546.6135 | 325.7154 | 204.6707 | 209.3963
547.6135 | 325.5701 | 204.8353 | 209.4487
548.6135 | 325.5064 | 204.9519 | 209.5144
549.6135 | 325.4749 | 205.0567 | 209.5591
550.6135 | 325.427 | 205.1782 | 209.6114
551.6135 | 325.3258 | 205.3177 | 209.7338
552.6135 | 325.1702 | 205.4428 | 209.8369
553.6135 | 325.1157 | 205.5453 | 209.9136
554.6135 | 325.0533 | 205.5999 | 209.9838
555.6135 | 325.052 | 205.6514 | 210.0946
556.6135 | 325.0926 | 205.7074 | 210.1903
557.6135 | 324.9589 | 205.7344 | 210.2805
558.6135 | 324.8492 | 205.7906 | 210.3641
559.6135 | 324.7944 | 205.8744 | 210.4634
560.6135 | 324.8163 | 206 | 210.5414
561.6135 | 324.748 | 206.0884 | 210.6225
562.6135 | 324.8051 | 206.1539 | 210.6963
563.6135 | 324.7514 | 206.1819 | 210.796
564.6135 | 324.6299 | 206.2063 | 210.9357
565.6135 | 324.5642 | 206.2558 | 211.0827
566.6135 | 324.5655 | 206.3611 | 211.1715
567.6135 | 324.4352 | 206.4581 | 211.247
568.6135 | 324.4665 | 206.5363 | 211.3127
569.6135 | 324.5886 | 206.628 | 211.3656
570.6135 | 324.688 | 206.7343 | 211.4444
571.6135 | 324.6574 | 206.8643 | 211.4889
572.6135 | 324.611 | 206.9926 | 211.5126
573.6135 | 324.6366 | 207.1279 | 211.5557
574.6135 | 324.6981 | 207.259 | 211.6695
575.6135 | 324.8077 | 207.3477 | 211.7672
576.6135 | 324.9174 | 207.4337 | 211.8267
577.6135 | 324.9081 | 207.4792 | 211.8971
578.6135 | 324.9341 | 207.5254 | 212.0144
579.6135 | 324.8952 | 207.5392 | 212.1173
580.6135 | 324.9825 | 207.5519 | 212.2029
581.6135 | 325.0452 | 207.5577 | 212.314
582.6135 | 325.0503 | 207.5952 | 212.4366
583.6135 | 324.9493 | 207.6774 | 212.543
584.6135 | 324.9556 | 207.7766 | 212.6017
585.6135 | 324.9842 | 207.8755 | 212.6258
586.6135 | 324.9904 | 207.9275 | 212.6371
587.6135 | 324.9879 | 207.9712 | 212.6822
588.6135 | 324.9406 | 208.0435 | 212.7477
589.6135 | 325.0471 | 208.1205 | 212.85
590.6135 | 325.2428 | 208.2443 | 212.9238
591.6135 | 325.4017 | 208.3448 | 212.9995
592.6135 | 325.5478 | 208.4308 | 213.1122
593.6135 | 325.6209 | 208.5144 | 213.2633
594.6135 | 325.6315 | 208.6154 | 213.388
595.6135 | 325.7049 | 208.7536 | 213.4237
596.6135 | 325.8366 | 208.8928 | 213.4689
597.6135 | 325.8305 | 209.0348 | 213.5425
598.6135 | 325.7803 | 209.1784 | 213.5913
599.6135 | 325.7084 | 209.3361 | 213.5771
600.6135 | 325.6724 | 209.5101 | 213.5703
601.6135 | 325.7808 | 209.6243 | 213.5696
602.6135 | 325.7614 | 209.6855 | 213.5753
603.6135 | 325.7684 | 209.7392 | 213.6149
604.6135 | 325.7126 | 209.7499 | 213.7067
605.6135 | 325.8221 | 209.8053 | 213.7911
606.6135 | 325.8014 | 209.9014 | 213.869
607.6135 | 325.6691 | 209.9693 | 213.9608
608.6135 | 325.636 | 210.0556 | 214.0663
609.6135 | 325.6345 | 210.0879 | 214.1652
610.6135 | 325.6017 | 210.1753 | 214.2824
611.6135 | 325.6036 | 210.2704 | 214.3848
612.6135 | 325.6242 | 210.3689 | 214.4734
613.6135 | 325.5377 | 210.4495 | 214.591
614.6135 | 325.4803 | 210.5766 | 214.6831
615.6135 | 325.3592 | 210.6439 | 214.7493
616.6135 | 325.3125 | 210.6898 | 214.8415
617.6135 | 325.1877 | 210.7449 | 214.9508
618.6135 | 325.2398 | 210.7737 | 215.0557
619.6135 | 325.3036 | 210.7746 | 215.1696
620.6135 | 325.3644 | 210.783 | 215.2855
621.6135 | 325.343 | 210.7968 | 215.3665
622.6135 | 325.3498 | 210.8174 | 215.4247
623.6135 | 325.4322 | 210.8533 | 215.5021
624.6135 | 325.3906 | 210.9181 | 215.5713
625.6135 | 325.25 | 211.0133 | 215.6436
626.6135 | 325.2188 | 211.1302 | 215.7416
627.6135 | 325.2279 | 211.248 | 215.8251
628.6135 | 325.2335 | 211.3546 | 215.8733
629.6135 | 325.287 | 211.4574 | 215.9273
630.6135 | 325.3458 | 211.5842 | 216.0093
631.6135 | 325.3774 | 211.7105 | 216.0793
632.6135 | 325.4095 | 211.8054 | 216.1423
633.6135 | 325.4585 | 211.893 | 216.1956
634.6135 | 325.49 | 212.0429 | 216.2184
635.6135 | 325.5055 | 212.1448 | 216.2419
636.6135 | 325.4827 | 212.2538 | 216.2752
637.6135 | 325.5442 | 212.346 | 216.3176
638.6135 | 325.5438 | 212.4175 | 216.3816
639.6135 | 325.5015 | 212.5133 | 216.4126
640.6135 | 325.4881 | 212.608 | 216.4563
641.6135 | 325.4056 | 212.6671 | 216.5408
642.6135 | 325.3879 | 212.6953 | 216.616
643.6135 | 325.275 | 212.7309 | 216.6908
644.6135 | 325.2123 | 212.7425 | 216.794
645.6135 | 325.1324 | 212.7468 | 216.9014
646.6135 | 325.2205 | 212.7944 | 216.9846
647.6135 | 325.2494 | 212.8499 | 217.0344
648.6135 | 325.273 | 212.8939 | 217.1267
649.6135 | 325.3386 | 212.9094 | 217.2631
650.6135 | 325.3798 | 212.9276 | 217.4157
651.6135 | 325.3227 | 212.9875 | 217.5442
652.6135 | 325.201 | 213.0094 | 217.6267
653.6135 | 325.3426 | 213.0679 | 217.7058
654.6135 | 325.4024 | 213.1206 | 217.8088
655.6135 | 325.3679 | 213.1458 | 217.9327
656.6135 | 325.254 | 213.2054 | 218.0798
657.6135 | 325.2247 | 213.2123 | 218.2237
658.6135 | 325.362 | 213.2549 | 218.3468
659.6135 | 325.3356 | 213.241 | 218.4438
660.6135 | 325.2976 | 213.2486 | 218.5098
661.6135 | 325.2297 | 213.2527 | 218.5664
662.6135 | 325.2601 | 213.3063 | 218.6285
663.6135 | 325.249 | 213.3868 | 218.7055
664.6135 | 325.3483 | 213.4817 | 218.7883
665.6135 | 325.4105 | 213.5387 | 218.874
666.6135 | 325.3829 | 213.5778 | 218.9703
667.6135 | 325.2419 | 213.6243 | 219.0524
668.6135 | 325.2598 | 213.6753 | 219.1163
669.6135 | 325.3247 | 213.7411 | 219.1891
670.6135 | 325.2458 | 213.8297 | 219.2579
671.6135 | 325.1588 | 213.9026 | 219.2794
672.6135 | 325.2131 | 213.9251 | 219.3048
673.6135 | 325.171 | 213.9351 | 219.3339
674.6135 | 325.0387 | 214.0087 | 219.3657
675.6135 | 324.9599 | 214.0573 | 219.381
676.6135 | 324.8919 | 214.105 | 219.3989
677.6135 | 324.9227 | 214.186 | 219.4307
678.6135 | 324.9032 | 214.2737 | 219.4643
679.6135 | 324.9283 | 214.3441 | 219.5202
680.6135 | 325.0187 | 214.4294 | 219.5261
681.6135 | 325.0009 | 214.5306 | 219.5353
682.6135 | 324.953 | 214.5992 | 219.5509
683.6135 | 324.9628 | 214.6949 | 219.5653
684.6135 | 324.9462 | 214.7562 | 219.5865
685.6135 | 324.9574 | 214.8211 | 219.6839
686.6135 | 324.9277 | 214.8645 | 219.7603
687.6135 | 324.7226 | 214.9476 | 219.7782
688.6135 | 324.6883 | 215.0286 | 219.7722
689.6135 | 324.6566 | 215.1362 | 219.7648
690.6135 | 324.5614 | 215.2412 | 219.7989
691.6135 | 324.6109 | 215.3384 | 219.8566
692.6135 | 324.6886 | 215.42 | 219.8999
693.6135 | 324.5704 | 215.4683 | 219.9733
694.6135 | 324.6319 | 215.5394 | 220.0529
695.6135 | 324.5751 | 215.603 | 220.1403
696.6135 | 324.5018 | 215.6463 | 220.2576
697.6135 | 324.5384 | 215.694 | 220.3639
698.6135 | 324.5421 | 215.7553 | 220.4405
699.6135 | 324.6807 | 215.8022 | 220.484
700.6135 | 324.8279 | 215.7908 | 220.5666
701.6135 | 324.8913 | 215.7953 | 220.6146
702.6135 | 324.8718 | 215.8163 | 220.612
703.6135 | 324.7276 | 215.8602 | 220.6288
704.6135 | 324.7032 | 215.9114 | 220.6851
705.6135 | 324.6441 | 215.9882 | 220.7669
706.6135 | 324.7071 | 216.0991 | 220.8185
707.6135 | 324.8343 | 216.2251 | 220.8682
708.6135 | 324.9238 | 216.2929 | 220.9212
709.6135 | 324.9349 | 216.3221 | 220.985
710.6135 | 324.9255 | 216.3493 | 221.0378
711.6135 | 324.9351 | 216.4228 | 221.0196
712.6135 | 324.889 | 216.4963 | 220.9729
713.6135 | 324.8762 | 216.5774 | 220.9868
714.6135 | 324.8405 | 216.6433 | 221.067
715.6135 | 324.8341 | 216.6873 | 221.1265
716.6135 | 324.8127 | 216.7132 | 221.1812
717.6135 | 324.8055 | 216.7238 | 221.2244
718.6135 | 324.8403 | 216.6881 | 221.2741
719.6135 | 324.7901 | 216.646 | 221.3186
720.6135 | 324.89 | 216.629 | 221.324
721.6135 | 324.9681 | 216.6356 | 221.3312
722.6135 | 324.8464 | 216.7113 | 221.3907
723.6135 | 325.0284 | 216.7466 | 221.4762
724.6135 | 325.0822 | 216.8369 | 221.5669
725.6135 | 325.0548 | 216.9432 | 221.6724
726.6135 | 325.0508 | 217.0389 | 221.72
727.6135 | 324.9342 | 217.0746 | 221.7485
728.6135 | 324.9846 | 217.1057 | 221.7405
729.6135 | 324.9997 | 217.1195 | 221.7884
730.6135 | 325.1093 | 217.1228 | 221.8794
731.6135 | 325.2703 | 217.1396 | 221.9425
732.6135 | 325.2514 | 217.1689 | 222.0107
733.6135 | 325.1843 | 217.1974 | 222.088
734.6135 | 325.1206 | 217.1974 | 222.2013
735.6135 | 325.09 | 217.2174 | 222.288
736.6135 | 325.253 | 217.2258 | 222.3478
737.6135 | 325.3329 | 217.2583 | 222.4258
738.6135 | 325.2558 | 217.2643 | 222.4977
739.6135 | 325.2472 | 217.301 | 222.5441
740.6135 | 325.2076 | 217.344 | 222.5322
741.6135 | 325.1849 | 217.4129 | 222.5415
742.6135 | 325.2268 | 217.4985 | 222.584
743.6135 | 325.2165 | 217.586 | 222.6503
744.6135 | 325.2132 | 217.6607 | 222.6968
745.6135 | 325.165 | 217.7085 | 222.724
746.6135 | 325.1987 | 217.7598 | 222.7278
747.6135 | 325.1401 | 217.8371 | 222.7364
748.6135 | 325.1819 | 217.8891 | 222.7194
749.6135 | 325.207 | 217.9625 | 222.7095
750.6135 | 325.1684 | 218.0432 | 222.7354
751.6135 | 325.0746 | 218.1719 | 222.7837
752.6135 | 325.1238 | 218.2984 | 222.8369
753.6135 | 325.1548 | 218.3722 | 222.9021
754.6135 | 325.1115 | 218.5007 | 222.9818
755.6135 | 325.1554 | 218.537 | 223.0477
756.6135 | 325.1396 | 218.5557 | 223.1048
757.6135 | 325.1414 | 218.6031 | 223.0969
758.6135 | 325.1666 | 218.6766 | 223.0871
759.6135 | 325.1907 | 218.7241 | 223.0813
760.6135 | 325.1301 | 218.7384 | 223.0691
761.6135 | 325.0143 | 218.7668 | 223.0506
762.6135 | 325.0141 | 218.8243 | 223.0452
763.6135 | 325.0472 | 218.8996 | 223.0528
764.6135 | 324.9916 | 218.9763 | 223.0632
765.6135 | 325.0184 | 219.0199 | 223.1027
766.6135 | 325.1463 | 219.0856 | 223.1563
767.6135 | 325.1562 | 219.0906 | 223.2437
768.6135 | 325.2202 | 219.0688 | 223.337
769.6135 | 325.1803 | 219.05 | 223.3872
770.6135 | 325.1017 | 219.0959 | 223.4323
771.6135 | 325.0967 | 219.1672 | 223.5002
772.6135 | 324.9917 | 219.2337 | 223.6048
773.6135 | 324.9683 | 219.3239 | 223.6918
774.6135 | 324.9796 | 219.4269 | 223.7477
775.6135 | 324.9894 | 219.4836 | 223.7699
776.6135 | 324.9742 | 219.4807 | 223.8232
777.6135 | 325.1261 | 219.5048 | 223.885
778.6135 | 325.1889 | 219.5053 | 223.9317
779.6135 | 325.2273 | 219.4622 | 223.9733
780.6135 | 325.3381 | 219.4826 | 223.9842
781.6135 | 325.3107 | 219.4786 | 224.0383
782.6135 | 325.3151 | 219.4925 | 224.0815
783.6135 | 325.2449 | 219.4827 | 224.1488
784.6135 | 325.3117 | 219.5028 | 224.2169
785.6135 | 325.2224 | 219.5423 | 224.3002
786.6135 | 325.1203 | 219.5741 | 224.4093
787.6135 | 325.0801 | 219.5292 | 224.543
788.6135 | 325.2431 | 219.4664 | 224.6295
789.6135 | 325.2382 | 219.4225 | 224.7211
790.6135 | 325.0588 | 219.4334 | 224.7354
791.6135 | 325.0076 | 219.5136 | 224.6768
792.6135 | 325.0361 | 219.5908 | 224.5894
793.6135 | 325.1074 | 219.689 | 224.5038
794.6135 | 325.1731 | 219.7726 | 224.4684
795.6135 | 325.2386 | 219.8237 | 224.4602
796.6135 | 325.307 | 219.8812 | 224.4934
797.6135 | 325.3939 | 219.89 | 224.5436
798.6135 | 325.5085 | 219.8678 | 224.6269
799.6135 | 325.5062 | 219.8871 | 224.6878
800.6135 | 325.5469 | 219.9233 | 224.7598
801.6135 | 325.7504 | 219.956 | 224.7889
802.6135 | 325.7354 | 219.9735 | 224.796
803.6135 | 325.7505 | 219.9445 | 224.8421
804.6135 | 325.8291 | 219.9458 | 224.9147
805.6135 | 325.7902 | 219.9568 | 224.9859
806.6135 | 325.7765 | 219.9372 | 225.0578
807.6135 | 325.7053 | 219.8815 | 225.1244
808.6135 | 325.7125 | 219.8569 | 225.1572
809.6135 | 325.7031 | 219.8571 | 225.1842
810.6135 | 325.6378 | 219.8745 | 225.2132
811.6135 | 325.5535 | 219.9275 | 225.2421
812.6135 | 325.7375 | 219.9986 | 225.2503
813.6135 | 325.7946 | 220.0388 | 225.2571
814.6135 | 325.8173 | 220.0878 | 225.3024
815.6135 | 325.892 | 220.1366 | 225.3649
816.6135 | 325.9653 | 220.2016 | 225.3985
817.6135 | 326.1302 | 220.2907 | 225.4036
818.6135 | 326.1888 | 220.3875 | 225.3766
819.6135 | 326.118 | 220.4763 | 225.3819
820.6135 | 325.9852 | 220.5691 | 225.4214
821.6135 | 326.0218 | 220.6175 | 225.4723
822.6135 | 326.0664 | 220.6993 | 225.5735
823.6135 | 325.9913 | 220.7243 | 225.696
824.6135 | 325.8603 | 220.7507 | 225.8008
825.6135 | 325.7756 | 220.7094 | 225.8406
826.6135 | 325.7374 | 220.6971 | 225.8633
827.6135 | 325.7902 | 220.6891 | 225.8857
828.6135 | 325.7905 | 220.7441 | 225.8958
829.6135 | 325.7886 | 220.7566 | 225.8798
830.6135 | 325.8295 | 220.7787 | 225.8816
831.6135 | 325.8985 | 220.7666 | 225.8932
832.6135 | 325.8801 | 220.7922 | 225.8851
833.6135 | 325.8734 | 220.8174 | 225.9014
834.6135 | 325.752 | 220.8289 | 225.9198
835.6135 | 325.649 | 220.8346 | 225.9554
836.6135 | 325.5474 | 220.8501 | 225.9926
837.6135 | 325.4539 | 220.8603 | 226.0367
838.6135 | 325.3939 | 220.9178 | 226.1035
839.6135 | 325.4492 | 220.9748 | 226.1188
840.6135 | 325.3458 | 220.9952 | 226.1281
841.6135 | 325.2893 | 221.0581 | 226.1662
842.6135 | 325.208 | 221.1507 | 226.2018
843.6135 | 325.2477 | 221.2446 | 226.2373
844.6135 | 325.2298 | 221.366 | 226.3026
845.6135 | 325.1962 | 221.4356 | 226.3508
846.6135 | 325.1563 | 221.4842 | 226.3915
847.6135 | 325.0183 | 221.4957 | 226.416
848.6135 | 325.0026 | 221.4801 | 226.4233
849.6135 | 325.0762 | 221.4672 | 226.433
850.6135 | 325.178 | 221.4921 | 226.4148
851.6135 | 325.0537 | 221.5627 | 226.3794
852.6135 | 325.0347 | 221.5828 | 226.35
853.6135 | 325.1232 | 221.6039 | 226.3853
854.6135 | 325.0835 | 221.6708 | 226.4395
855.6135 | 325.0931 | 221.7284 | 226.4665
856.6135 | 324.9846 | 221.7633 | 226.4838
857.6135 | 325.0923 | 221.8237 | 226.4749
858.6135 | 325.138 | 221.8931 | 226.4382
859.6135 | 325.0968 | 221.9959 | 226.4048
860.6135 | 325.1531 | 222.1211 | 226.363
861.6135 | 325.1726 | 222.2073 | 226.3197
862.6135 | 325.1569 | 222.2681 | 226.3195
863.6135 | 325.2211 | 222.3447 | 226.3312
864.6135 | 325.2734 | 222.4439 | 226.2856
865.6135 | 325.2418 | 222.5291 | 226.2662
866.6135 | 325.2429 | 222.5871 | 226.25
867.6135 | 325.1256 | 222.55 | 226.2726
868.6135 | 324.9735 | 222.4856 | 226.2967
869.6135 | 325.0325 | 222.4253 | 226.3004
870.6135 | 325.0671 | 222.4608 | 226.3129
871.6135 | 325.1789 | 222.4689 | 226.3562
872.6135 | 325.2642 | 222.4693 | 226.4163
873.6135 | 325.2313 | 222.4521 | 226.4416
874.6135 | 325.1801 | 222.4938 | 226.4129
875.6135 | 325.0973 | 222.5363 | 226.38
876.6135 | 325.0438 | 222.5843 | 226.4083
877.6135 | 325.0089 | 222.6447 | 226.4369
878.6135 | 325.0303 | 222.6833 | 226.4782
879.6135 | 325.0053 | 222.7032 | 226.5448
880.6135 | 324.9749 | 222.7097 | 226.6437
881.6135 | 325.046 | 222.7062 | 226.7517
882.6135 | 325.0536 | 222.7517 | 226.8523
883.6135 | 325.0505 | 222.7349 | 226.9527
884.6135 | 325.1295 | 222.7557 | 227.0149
885.6135 | 325.2019 | 222.8027 | 227.0419
886.6135 | 325.1855 | 222.8343 | 227.0503
887.6135 | 325.0444 | 222.907 | 227.0408
888.6135 | 325.0593 | 222.95 | 227.0427
889.6135 | 325.0675 | 222.9354 | 227.0802
890.6135 | 325.1221 | 222.9789 | 227.1346
891.6135 | 325.2709 | 222.9833 | 227.1853
892.6135 | 325.2032 | 223.0024 | 227.2302
893.6135 | 325.2031 | 223.0014 | 227.2671
894.6135 | 325.183 | 222.9676 | 227.2971
895.6135 | 325.097 | 222.9813 | 227.3098
896.6135 | 325.1358 | 223.0261 | 227.3494
897.6135 | 325.1203 | 223.0641 | 227.4105
898.6135 | 325.1522 | 223.0866 | 227.511
899.6135 | 325.175 | 223.0757 | 227.6405
900.6135 | 325.1547 | 223.0811 | 227.7202
901.6135 | 325.1548 | 223.1033 | 227.7628
902.6135 | 325.2437 | 223.1547 | 227.7696
903.6135 | 325.2563 | 223.2215 | 227.7774
904.6135 | 325.3581 | 223.2594 | 227.7939
905.6135 | 325.3893 | 223.2868 | 227.7758
906.6135 | 325.4163 | 223.3191 | 227.7456
907.6135 | 325.4496 | 223.3662 | 227.7384
908.6135 | 325.4936 | 223.4059 | 227.7326
909.6135 | 325.5004 | 223.4339 | 227.77
910.6135 | 325.5888 | 223.4883 | 227.767
911.6135 | 325.6858 | 223.5515 | 227.7376
912.6135 | 325.7767 | 223.6105 | 227.7239
913.6135 | 325.8214 | 223.6714 | 227.7497
914.6135 | 325.7819 | 223.7308 | 227.7926
915.6135 | 325.8655 | 223.7582 | 227.8356
916.6135 | 325.8949 | 223.7602 | 227.8897
917.6135 | 325.8892 | 223.7831 | 227.9847
918.6135 | 325.936 | 223.7788 | 228.0314
919.6135 | 325.9575 | 223.7889 | 228.0653
920.6135 | 325.8924 | 223.7951 | 228.0787
921.6135 | 325.7912 | 223.8201 | 228.0813
922.6135 | 325.7962 | 223.8907 | 228.0605
923.6135 | 325.6881 | 223.9107 | 228.0547
924.6135 | 325.5818 | 223.9091 | 228.0848
925.6135 | 325.5402 | 223.8767 | 228.1064
926.6135 | 325.6183 | 223.8708 | 228.1317
927.6135 | 325.7396 | 223.8493 | 228.1655
928.6135 | 325.6901 | 223.8313 | 228.191
929.6135 | 325.6541 | 223.8042 | 228.2702
930.6135 | 325.5851 | 223.8217 | 228.291
931.6135 | 325.7533 | 223.8618 | 228.3076
932.6135 | 325.9442 | 223.8652 | 228.3373
933.6135 | 325.9425 | 223.8604 | 228.3542
934.6135 | 325.9693 | 223.8647 | 228.3931
935.6135 | 325.8414 | 223.8207 | 228.4784
936.6135 | 325.8009 | 223.7818 | 228.5266
937.6135 | 325.662 | 223.7971 | 228.5414
938.6135 | 325.5835 | 223.8351 | 228.5588
939.6135 | 325.5187 | 223.8808 | 228.6319
940.6135 | 325.4214 | 223.9132 | 228.684
941.6135 | 325.3022 | 223.9138 | 228.7222
942.6135 | 325.3499 | 223.8979 | 228.7469
943.6135 | 325.3205 | 223.9117 | 228.7846
944.6135 | 325.3136 | 223.9237 | 228.8412
945.6135 | 325.1983 | 223.8546 | 228.8875
946.6135 | 325.2311 | 223.854 | 228.8994
947.6135 | 325.2709 | 223.8349 | 228.8893
948.6135 | 325.177 | 223.7593 | 228.8797
949.6135 | 325.0956 | 223.6978 | 228.8745
950.6135 | 325.0228 | 223.7123 | 228.8685
951.6135 | 324.9764 | 223.733 | 228.8796
952.6135 | 324.9226 | 223.7361 | 228.9149
953.6135 | 324.9991 | 223.7631 | 228.9601
954.6135 | 324.9059 | 223.7992 | 228.9898
955.6135 | 324.8633 | 223.8523 | 229.0418
956.6135 | 324.832 | 223.9057 | 229.0708
957.6135 | 324.7996 | 223.9546 | 229.1207
958.6135 | 324.8134 | 223.9796 | 229.1699
959.6135 | 324.8907 | 223.9916 | 229.2332
960.6135 | 324.9915 | 223.9989 | 229.2359
961.6135 | 325.0423 | 224.0248 | 229.2196
962.6135 | 325.06 | 224.0654 | 229.2252
963.6135 | 325.1083 | 224.0913 | 229.2629
964.6135 | 325.1999 | 224.0855 | 229.3179
965.6135 | 325.2387 | 224.1043 | 229.379
966.6135 | 325.347 | 224.1189 | 229.4051
967.6135 | 325.3688 | 224.1373 | 229.4254
968.6135 | 325.4233 | 224.1444 | 229.4389
969.6135 | 325.437 | 224.1705 | 229.469
970.6135 | 325.437 | 224.1392 | 229.4986
971.6135 | 325.4493 | 224.0993 | 229.5169
972.6135 | 325.4254 | 224.065 | 229.4933
973.6135 | 325.3632 | 224.0701 | 229.4781
974.6135 | 325.2969 | 224.117 | 229.4967
975.6135 | 325.3206 | 224.1737 | 229.5528
976.6135 | 325.3775 | 224.1958 | 229.5749
977.6135 | 325.4244 | 224.198 | 229.6116
978.6135 | 325.5416 | 224.1927 | 229.6392
979.6135 | 325.5277 | 224.1757 | 229.6675
980.6135 | 325.5236 | 224.1633 | 229.651
981.6135 | 325.5101 | 224.1978 | 229.592
982.6135 | 325.5838 | 224.2573 | 229.5461
983.6135 | 325.5787 | 224.3097 | 229.4994
984.6135 | 325.5691 | 224.3475 | 229.4934
985.6135 | 325.5415 | 224.3723 | 229.4833
986.6135 | 325.5852 | 224.4144 | 229.484
987.6135 | 325.6313 | 224.4503 | 229.5018
988.6135 | 325.7901 | 224.491 | 229.5244
989.6135 | 325.9145 | 224.5493 | 229.5446
990.6135 | 325.8717 | 224.6339 | 229.5072
991.6135 | 325.6994 | 224.7039 | 229.4247
992.6135 | 325.6673 | 224.7835 | 229.3046
993.6135 | 325.6294 | 224.7979 | 229.2028
994.6135 | 325.5694 | 224.8436 | 229.1503
995.6135 | 325.5936 | 224.8785 | 229.142
996.6135 | 325.722 | 224.8775 | 229.1519
997.6135 | 325.7516 | 224.8662 | 229.2009
998.6135 | 325.6553 | 224.8639 | 229.2335
999.6135 | 325.6783 | 224.861 | 229.2812
1000.6135 | 325.6762 | 224.8608 | 229.3014
1001.6135 | 325.7153 | 224.8267 | 229.3271
1002.6135 | 325.5163 | 224.8142 | 229.3598
1003.6135 | 325.4055 | 224.8327 | 229.4005
1004.6135 | 325.3576 | 224.8575 | 229.4123
1005.6135 | 325.3334 | 224.8456 | 229.3976
1006.6135 | 325.3366 | 224.8562 | 229.4046
1007.6135 | 325.2957 | 224.8767 | 229.4149
1008.6135 | 325.2298 | 224.9039 | 229.4224
1009.6135 | 325.234 | 224.9344 | 229.4245
1010.6135 | 325.1845 | 224.9317 | 229.4154
1011.6135 | 325.1944 | 224.9312 | 229.4452
1012.6135 | 325.1647 | 224.8854 | 229.5024
1013.6135 | 325.2407 | 224.872 | 229.538
1014.6135 | 325.4283 | 224.8513 | 229.5615
1015.6135 | 325.3623 | 224.8378 | 229.5901
1016.6135 | 325.3897 | 224.879 | 229.5759
1017.6135 | 325.4468 | 224.8985 | 229.5547
1018.6135 | 325.36 | 224.9331 | 229.5999
1019.6135 | 325.3335 | 225.0044 | 229.6725
1020.6135 | 325.3317 | 225.0691 | 229.7203
1021.6135 | 325.3547 | 225.1802 | 229.7527
1022.6135 | 325.3641 | 225.2397 | 229.7322
1023.6135 | 325.2644 | 225.3152 | 229.717
1024.6135 | 325.2419 | 225.3155 | 229.7319
1025.6135 | 325.2086 | 225.2903 | 229.7986
1026.6135 | 325.2088 | 225.3027 | 229.9041
1027.6135 | 325.2192 | 225.3283 | 229.98
1028.6135 | 325.1588 | 225.3884 | 230.0246
1029.6135 | 325.3016 | 225.4317 | 230.0556
1030.6135 | 325.3731 | 225.4665 | 230.0584
1031.6135 | 325.3598 | 225.5178 | 230.0699
1032.6135 | 325.3421 | 225.5264 | 230.1002
1033.6135 | 325.3301 | 225.5396 | 230.168
1034.6135 | 325.2907 | 225.5557 | 230.2378
1035.6135 | 325.295 | 225.6101 | 230.3021
1036.6135 | 325.2906 | 225.6279 | 230.3032
1037.6135 | 325.2387 | 225.6555 | 230.3029
1038.6135 | 325.0794 | 225.6994 | 230.311
1039.6135 | 324.8552 | 225.7521 | 230.2759
1040.6135 | 324.8154 | 225.7735 | 230.2659
1041.6135 | 324.8472 | 225.7428 | 230.2586
1042.6135 | 324.9649 | 225.6931 | 230.2726
1043.6135 | 325.0978 | 225.678 | 230.2875
1044.6135 | 325.085 | 225.6774 | 230.3063
1045.6135 | 325.0727 | 225.7113 | 230.3242
1046.6135 | 325.0251 | 225.7399 | 230.3354
1047.6135 | 324.9896 | 225.7934 | 230.3604
1048.6135 | 325.0227 | 225.7733 | 230.382
1049.6135 | 325.0588 | 225.7764 | 230.4381
1050.6135 | 325.0418 | 225.784 | 230.4591
1051.6135 | 325.0657 | 225.8104 | 230.4729
1052.6135 | 325.1196 | 225.7982 | 230.4712
1053.6135 | 325.0226 | 225.7837 | 230.4612
1054.6135 | 325.0417 | 225.732 | 230.4613
1055.6135 | 325.0284 | 225.7008 | 230.5047
1056.6135 | 325.16 | 225.6996 | 230.5399
1057.6135 | 325.3491 | 225.732 | 230.5791
1058.6135 | 325.4036 | 225.7721 | 230.6229
1059.6135 | 325.5409 | 225.8108 | 230.6343
1060.6135 | 325.5993 | 225.8299 | 230.6412
1061.6135 | 325.6137 | 225.8638 | 230.6362
1062.6135 | 325.6604 | 225.9526 | 230.6674
1063.6135 | 325.62 | 226.0143 | 230.7148
1064.6135 | 325.6137 | 225.9968 | 230.7678
1065.6135 | 325.5244 | 225.9961 | 230.7847
1066.6135 | 325.4395 | 226.0256 | 230.7533
1067.6135 | 325.4605 | 226.0354 | 230.7373
1068.6135 | 325.5082 | 226.0606 | 230.7346
1069.6135 | 325.4806 | 226.0847 | 230.7255
1070.6135 | 325.462 | 226.115 | 230.6771
1071.6135 | 325.5162 | 226.1315 | 230.6507
1072.6135 | 325.5008 | 226.1632 | 230.6332
1073.6135 | 325.5367 | 226.2335 | 230.6043
1074.6135 | 325.428 | 226.29 | 230.6393
1075.6135 | 325.3491 | 226.3067 | 230.6982
1076.6135 | 325.373 | 226.2964 | 230.7251
1077.6135 | 325.3399 | 226.3226 | 230.7136
1078.6135 | 325.3681 | 226.3346 | 230.7267
1079.6135 | 325.4018 | 226.3048 | 230.7506
1080.6135 | 325.3277 | 226.2934 | 230.7786
1081.6135 | 325.2448 | 226.3012 | 230.775
1082.6135 | 325.2641 | 226.2987 | 230.7675
1083.6135 | 325.3186 | 226.2501 | 230.785
1084.6135 | 325.3705 | 226.1755 | 230.7991
1085.6135 | 325.411 | 226.1608 | 230.8029
1086.6135 | 325.3692 | 226.122 | 230.8198
1087.6135 | 325.2116 | 226.0296 | 230.8425
1088.6135 | 325.1179 | 226.0015 | 230.8498
1089.6135 | 325.0508 | 225.9705 | 230.8633
1090.6135 | 325.032 | 225.9833 | 230.9024
1091.6135 | 325.0889 | 226.0293 | 230.891
1092.6135 | 325.0449 | 226.0419 | 230.8535
1093.6135 | 325.0985 | 226.0455 | 230.8638
1094.6135 | 325.0901 | 226.0598 | 230.913
1095.6135 | 325.1146 | 226.0805 | 230.9254
1096.6135 | 325.2057 | 226.0776 | 230.9341
1097.6135 | 325.0372 | 226.0823 | 230.9364
1098.6135 | 325.0067 | 226.1114 | 230.8737
1099.6135 | 325.0699 | 226.1304 | 230.7605
1100.6135 | 325.0894 | 226.1979 | 230.6936
1101.6135 | 325.2385 | 226.2589 | 230.6328
1102.6135 | 325.1114 | 226.3249 | 230.5693
1103.6135 | 324.9888 | 226.3695 | 230.5422
1104.6135 | 325.0339 | 226.4002 | 230.5435
1105.6135 | 324.9823 | 226.4365 | 230.5573
1106.6135 | 324.8604 | 226.4103 | 230.5709
1107.6135 | 324.6991 | 226.3834 | 230.548
1108.6135 | 324.7851 | 226.3378 | 230.5148
1109.6135 | 324.7184 | 226.3131 | 230.5005
1110.6135 | 324.7034 | 226.3053 | 230.5239
1111.6135 | 324.6824 | 226.3084 | 230.5275
1112.6135 | 324.6968 | 226.2979 | 230.5358
1113.6135 | 324.7046 | 226.2947 | 230.5659
1114.6135 | 324.768 | 226.3207 | 230.6155
1115.6135 | 324.7813 | 226.3251 | 230.6922
1116.6135 | 324.7573 | 226.3823 | 230.8013
1117.6135 | 324.7472 | 226.4029 | 230.8806
1118.6135 | 324.7169 | 226.3343 | 230.9362
1119.6135 | 324.8465 | 226.288 | 230.985
1120.6135 | 324.92 | 226.2342 | 231.0507
1121.6135 | 324.9184 | 226.1483 | 231.1209
1122.6135 | 324.8648 | 226.1433 | 231.1481
1123.6135 | 324.8023 | 226.1225 | 231.1702
1124.6135 | 324.7729 | 226.0736 | 231.175
1125.6135 | 324.8126 | 226.0565 | 231.1736
1126.6135 | 324.7516 | 226.1117 | 231.1726
1127.6135 | 324.8139 | 226.1601 | 231.1696
1128.6135 | 324.7555 | 226.2231 | 231.1829
1129.6135 | 324.6082 | 226.2906 | 231.15
1130.6135 | 324.5463 | 226.323 | 231.131
1131.6135 | 324.644 | 226.3729 | 231.13
1132.6135 | 324.7358 | 226.4523 | 231.1705
1133.6135 | 324.7601 | 226.5366 | 231.2202
1134.6135 | 324.6342 | 226.6228 | 231.2549
1135.6135 | 324.6303 | 226.69 | 231.2855
1136.6135 | 324.6882 | 226.7589 | 231.2942
1137.6135 | 324.5954 | 226.7484 | 231.2967
1138.6135 | 324.6282 | 226.7741 | 231.3077
1139.6135 | 324.7803 | 226.7817 | 231.3389
1140.6135 | 324.9688 | 226.8079 | 231.3925
1141.6135 | 325.1047 | 226.8083 | 231.481
1142.6135 | 325.0613 | 226.7743 | 231.5663
1143.6135 | 325.0506 | 226.7328 | 231.6603
1144.6135 | 325.0239 | 226.6819 | 231.7198
1145.6135 | 324.9856 | 226.6734 | 231.7258
1146.6135 | 325.0028 | 226.6483 | 231.6747
1147.6135 | 324.9503 | 226.6411 | 231.6408
1148.6135 | 324.9808 | 226.6214 | 231.6363
1149.6135 | 324.9276 | 226.6144 | 231.6586
1150.6135 | 324.8692 | 226.6528 | 231.6809
1151.6135 | 324.8595 | 226.6969 | 231.6234
1152.6135 | 324.8496 | 226.7265 | 231.5878
1153.6135 | 324.7017 | 226.7598 | 231.5841
1154.6135 | 324.6728 | 226.8162 | 231.5983
1155.6135 | 324.6577 | 226.8584 | 231.5829
1156.6135 | 324.6871 | 226.928 | 231.5287
1157.6135 | 324.7036 | 226.9967 | 231.4751
1158.6135 | 324.8168 | 227.029 | 231.3967
1159.6135 | 324.8955 | 227.0653 | 231.357
1160.6135 | 324.8753 | 227.1612 | 231.3316
1161.6135 | 324.7602 | 227.2055 | 231.3021
1162.6135 | 324.776 | 227.2681 | 231.2882
1163.6135 | 324.88 | 227.3172 | 231.2812
1164.6135 | 324.8911 | 227.3705 | 231.273
1165.6135 | 324.8564 | 227.4344 | 231.2607
1166.6135 | 324.9567 | 227.4841 | 231.2498
1167.6135 | 325.0284 | 227.4507 | 231.2637
1168.6135 | 325.0794 | 227.4033 | 231.2939
1169.6135 | 325.0909 | 227.4099 | 231.3313
1170.6135 | 325.242 | 227.4299 | 231.3352
1171.6135 | 325.1848 | 227.4409 | 231.3232
1172.6135 | 325.2023 | 227.4436 | 231.3578
1173.6135 | 325.2415 | 227.4701 | 231.4346
1174.6135 | 325.2231 | 227.4813 | 231.508
1175.6135 | 325.3429 | 227.4934 | 231.5477
1176.6135 | 325.4413 | 227.5239 | 231.5481
1177.6135 | 325.461 | 227.5734 | 231.5532
1178.6135 | 325.3869 | 227.6621 | 231.5531
1179.6135 | 325.4555 | 227.7242 | 231.5849
1180.6135 | 325.3816 | 227.7794 | 231.6385
1181.6135 | 325.4184 | 227.8612 | 231.6761
1182.6135 | 325.4065 | 227.9454 | 231.7325
1183.6135 | 325.3264 | 227.9676 | 231.792
1184.6135 | 325.3778 | 227.9874 | 231.8498
1185.6135 | 325.4056 | 227.9914 | 231.8966
1186.6135 | 325.3585 | 228.0216 | 231.9288
1187.6135 | 325.2738 | 228.0226 | 231.9452
1188.6135 | 325.2317 | 227.974 | 231.9745
1189.6135 | 325.0903 | 227.9263 | 232.015
1190.6135 | 324.9569 | 227.8876 | 232.0439
1191.6135 | 324.8649 | 227.8608 | 232.0888
1192.6135 | 324.8178 | 227.8512 | 232.1227
1193.6135 | 324.7714 | 227.7457 | 232.1615
1194.6135 | 324.5625 | 227.6272 | 232.1908
1195.6135 | 324.5117 | 227.532 | 232.219
1196.6135 | 324.5295 | 227.4435 | 232.2087
1197.6135 | 324.4845 | 227.3975 | 232.1579
1198.6135 | 324.4594 | 227.3892 | 232.1109
1199.6135 | 324.3653 | 227.3854 | 232.0858
1200.6135 | 324.3727 | 227.4018 | 232.1022
1201.6135 | 324.3624 | 227.4229 | 232.1188
1202.6135 | 324.3163 | 227.4981 | 232.1575
1203.6135 | 324.3455 | 227.6072 | 232.1666
1204.6135 | 324.3273 | 227.6897 | 232.1994
1205.6135 | 324.4953 | 227.7027 | 232.2081
1206.6135 | 324.6256 | 227.7092 | 232.2472
1207.6135 | 324.7302 | 227.7148 | 232.2929
1208.6135 | 324.7677 | 227.6961 | 232.336
1209.6135 | 324.8011 | 227.6928 | 232.3736
1210.6135 | 324.7505 | 227.6654 | 232.4067
1211.6135 | 324.777 | 227.6655 | 232.4188
1212.6135 | 324.7865 | 227.6315 | 232.4468
1213.6135 | 324.8244 | 227.611 | 232.4507
1214.6135 | 324.8622 | 227.5833 | 232.4384
1215.6135 | 324.8119 | 227.5294 | 232.4569
1216.6135 | 324.8977 | 227.4838 | 232.4967
1217.6135 | 324.9675 | 227.4599 | 232.5614
1218.6135 | 324.9731 | 227.414 | 232.6156
1219.6135 | 324.8724 | 227.3751 | 232.6821
1220.6135 | 324.9661 | 227.3582 | 232.7026
1221.6135 | 325.0867 | 227.4005 | 232.672
1222.6135 | 325.0821 | 227.4494 | 232.6248
1223.6135 | 325.0575 | 227.5166 | 232.5615
1224.6135 | 325.0097 | 227.4686 | 232.4973
1225.6135 | 325.1434 | 227.3857 | 232.4488
1226.6135 | 325.2097 | 227.362 | 232.4131
1227.6135 | 325.1915 | 227.38 | 232.4223
1228.6135 | 325.1255 | 227.3809 | 232.4629
1229.6135 | 325.0875 | 227.3502 | 232.5228
1230.6135 | 325.0816 | 227.364 | 232.5692
1231.6135 | 325.0967 | 227.3668 | 232.6225
1232.6135 | 325.0764 | 227.381 | 232.6594
1233.6135 | 325.0978 | 227.385 | 232.691
1234.6135 | 325.1986 | 227.3476 | 232.6886
1235.6135 | 325.1478 | 227.3376 | 232.6766
1236.6135 | 325.1236 | 227.3588 | 232.6162
1237.6135 | 325.1125 | 227.3723 | 232.5798
1238.6135 | 325.1752 | 227.4034 | 232.535
1239.6135 | 325.2353 | 227.4527 | 232.4692
1240.6135 | 325.2814 | 227.494 | 232.4123
1241.6135 | 325.3029 | 227.5716 | 232.3915
1242.6135 | 325.3023 | 227.609 | 232.3411
1243.6135 | 325.3052 | 227.6204 | 232.2941
1244.6135 | 325.2585 | 227.5532 | 232.2656
1245.6135 | 325.3265 | 227.413 | 232.2655
1246.6135 | 325.3438 | 227.378 | 232.2459
1247.6135 | 325.3095 | 227.3644 | 232.2251
1248.6135 | 325.2711 | 227.3792 | 232.185
1249.6135 | 325.3268 | 227.4307 | 232.1339
1250.6135 | 325.2679 | 227.4933 | 232.1113
1251.6135 | 325.2669 | 227.5568 | 232.1295
1252.6135 | 325.3045 | 227.5756 | 232.1472
1253.6135 | 325.2066 | 227.597 | 232.1628
1254.6135 | 325.1677 | 227.6538 | 232.1692
1255.6135 | 325.1745 | 227.7057 | 232.138
1256.6135 | 325.1146 | 227.7009 | 232.1219
1257.6292 | 325.0347 | 227.7051 | 232.0992
1258.6135 | 325.029 | 227.6995 | 232.0425
1259.6135 | 325.0438 | 227.6908 | 232.0069
1260.6135 | 325.06 | 227.7034 | 231.9747
1261.6135 | 325.0286 | 227.7128 | 231.9658
1262.6135 | 324.9555 | 227.6845 | 231.9725
1263.6135 | 324.998 | 227.6928 | 231.9728
1264.6135 | 325.0163 | 227.686 | 231.9549
1265.6135 | 325.0251 | 227.6631 | 231.9316
1266.6135 | 325.0197 | 227.6049 | 231.897
1267.6135 | 324.8667 | 227.5213 | 231.8965
1268.6135 | 324.8575 | 227.4897 | 231.8719
1269.6135 | 324.9731 | 227.4465 | 231.8353
1270.6135 | 324.8643 | 227.4148 | 231.8271
1271.6135 | 324.8123 | 227.425 | 231.8297
1272.6135 | 324.8001 | 227.4416 | 231.8324
1273.6135 | 324.8457 | 227.4663 | 231.8877
1274.6135 | 324.8013 | 227.4821 | 231.9765
1275.6135 | 324.8146 | 227.4707 | 232.0396
1276.6135 | 324.8347 | 227.477 | 232.0787
1277.6135 | 324.8 | 227.5522 | 232.1087
1278.6135 | 324.7954 | 227.5877 | 232.1259
1279.6135 | 324.7953 | 227.6286 | 232.152
1280.6135 | 324.8789 | 227.6901 | 232.1641
1281.6135 | 324.9272 | 227.7503 | 232.1379
1282.6135 | 325.0492 | 227.8201 | 232.0869
1283.6135 | 325.0838 | 227.8683 | 232.0724
1284.6135 | 325.1906 | 227.9688 | 232.0598
1285.6135 | 325.1297 | 228.0582 | 232.0112
1286.6135 | 325.1771 | 228.1137 | 231.9809
1287.6135 | 325.1404 | 228.134 | 231.9992
1288.6135 | 325.1301 | 228.134 | 232.0389
1289.6135 | 325.2144 | 228.1736 | 232.0781
1290.6135 | 325.2766 | 228.2096 | 232.1187
1291.6135 | 325.2926 | 228.1847 | 232.1884
1292.6135 | 325.24 | 228.1591 | 232.2254
1293.6135 | 325.1876 | 228.121 | 232.2687
1294.6135 | 325.1329 | 228.0885 | 232.2889
1295.6135 | 325.0848 | 228.0361 | 232.3082
1296.6135 | 325.1219 | 228.0475 | 232.2678
1297.6135 | 325.055 | 228.0253 | 232.2145
1298.6135 | 325.113 | 227.997 | 232.164
1299.6135 | 325.0683 | 228.0653 | 232.0723
1300.6135 | 325.0378 | 228.1323 | 232.0061
1301.6135 | 325.0471 | 228.1619 | 231.9738
1302.6135 | 325.0849 | 228.1792 | 231.9832
1303.6135 | 325.1377 | 228.2046 | 232.0091
1304.6135 | 325.2438 | 228.2251 | 232.0489
1305.6135 | 325.2801 | 228.2535 | 232.0823
1306.6135 | 325.3347 | 228.3065 | 232.132
1307.6135 | 325.3785 | 228.3284 | 232.2017
1308.6135 | 325.3982 | 228.3149 | 232.2641
1309.6135 | 325.4268 | 228.3346 | 232.2691
1310.6135 | 325.4119 | 228.3687 | 232.2599
1311.6135 | 325.4218 | 228.4226 | 232.2322
1312.6135 | 325.4049 | 228.4614 | 232.2053
1313.6135 | 325.393 | 228.4391 | 232.2023
1314.6135 | 325.3404 | 228.4065 | 232.2028
1315.6135 | 325.3184 | 228.3571 | 232.2051
1316.6135 | 325.3946 | 228.3644 | 232.228
1317.6135 | 325.3535 | 228.3899 | 232.2587
1318.6135 | 325.2676 | 228.3882 | 232.3094
1319.6135 | 325.3264 | 228.3582 | 232.3385
1320.6135 | 325.2568 | 228.3513 | 232.3127
1321.6135 | 325.1097 | 228.3628 | 232.2949
1322.6135 | 324.9059 | 228.3412 | 232.3149
1323.6135 | 324.8653 | 228.2893 | 232.3588
1324.6135 | 324.9473 | 228.2858 | 232.3929
1325.6135 | 324.9463 | 228.2631 | 232.4503
1326.6135 | 324.8747 | 228.236 | 232.4944
1327.6135 | 324.8666 | 228.2482 | 232.5479
1328.6135 | 324.8868 | 228.2322 | 232.5787
1329.6135 | 324.8943 | 228.1815 | 232.6318
1330.6135 | 324.972 | 228.1275 | 232.683
1331.6135 | 324.9797 | 228.1464 | 232.7071
1332.6135 | 324.9391 | 228.1465 | 232.7759
1333.6135 | 324.9217 | 228.1587 | 232.8533
1334.6135 | 324.9371 | 228.1767 | 232.893
1335.6135 | 325.0034 | 228.1426 | 232.8966
1336.6135 | 324.9865 | 228.1487 | 232.8875
1337.6135 | 324.9615 | 228.1972 | 232.8582
1338.6135 | 324.9786 | 228.1997 | 232.8534
1339.6135 | 324.9553 | 228.2186 | 232.8418
1340.6135 | 324.9598 | 228.2301 | 232.8903
1341.6135 | 325.0313 | 228.2383 | 232.9335
1342.6135 | 324.9638 | 228.2444 | 232.9235
1343.6135 | 324.9954 | 228.247 | 232.8784
1344.6135 | 325.0241 | 228.2312 | 232.8238
1345.6135 | 325.0402 | 228.1805 | 232.7669
1346.6135 | 325.0988 | 228.1753 | 232.7109
1347.6135 | 325.1642 | 228.1996 | 232.6211
1348.6135 | 325.3112 | 228.2315 | 232.5459
1349.6135 | 325.3438 | 228.2098 | 232.4885
1350.6135 | 325.3546 | 228.2127 | 232.489
1351.6135 | 325.3419 | 228.2198 | 232.4987
1352.6135 | 325.2912 | 228.2011 | 232.5322
1353.6135 | 325.2638 | 228.2393 | 232.5863
1354.6135 | 325.3464 | 228.2321 | 232.666
1355.6135 | 325.3958 | 228.1864 | 232.7433
1356.6135 | 325.4078 | 228.1618 | 232.76
1357.6135 | 325.4081 | 228.1642 | 232.7892
1358.6135 | 325.313 | 228.1582 | 232.845
1359.6135 | 325.2455 | 228.174 | 232.8884
1360.6135 | 325.244 | 228.174 | 232.9246
1361.6135 | 325.0631 | 228.1437 | 232.9966
1362.6135 | 324.9146 | 228.1092 | 233.081
1363.6135 | 324.7875 | 228.1037 | 233.1596
1364.6135 | 324.7135 | 228.0843 | 233.2083
1365.6135 | 324.5461 | 228.0908 | 233.199
1366.6135 | 324.4791 | 228.1024 | 233.1108
1367.6135 | 324.4415 | 228.1417 | 232.9713
1368.6135 | 324.5271 | 228.2245 | 232.8453
1369.6135 | 324.5518 | 228.2891 | 232.7538
1370.6135 | 324.4853 | 228.3503 | 232.6871
1371.6135 | 324.4602 | 228.3873 | 232.6526
1372.6135 | 324.4923 | 228.3945 | 232.6696
1373.6135 | 324.4512 | 228.4484 | 232.7211
1374.6135 | 324.4751 | 228.5071 | 232.8007
1375.6135 | 324.4421 | 228.569 | 232.8557
1376.6135 | 324.414 | 228.6292 | 232.8669
1377.6135 | 324.3845 | 228.6606 | 232.8467
1378.6135 | 324.4488 | 228.6341 | 232.8325
1379.6135 | 324.4675 | 228.6281 | 232.8556
1380.6135 | 324.4944 | 228.6484 | 232.9097
1381.6135 | 324.528 | 228.6816 | 232.9464
1382.6135 | 324.493 | 228.6821 | 232.9561
1383.6135 | 324.5211 | 228.666 | 232.9504
1384.6135 | 324.5119 | 228.607 | 233.0004
1385.6135 | 324.5375 | 228.5682 | 233.0477
1386.6135 | 324.5325 | 228.5463 | 233.0683
1387.6135 | 324.5441 | 228.5666 | 233.0673
1388.6135 | 324.5408 | 228.609 | 233.066
1389.6135 | 324.5818 | 228.6305 | 233.026
1390.6135 | 324.5945 | 228.6614 | 232.9807
1391.6135 | 324.5024 | 228.6904 | 232.9386
1392.6135 | 324.3445 | 228.7055 | 232.9386
1393.6135 | 324.1187 | 228.6673 | 232.9883
1394.6135 | 324.14 | 228.6103 | 233.0162
1395.6135 | 324.2059 | 228.586 | 233.0588
1396.6135 | 324.1977 | 228.5475 | 233.1203
1397.6135 | 324.1865 | 228.4728 | 233.1834
1398.6135 | 324.2863 | 228.4172 | 233.221
1399.6135 | 324.3236 | 228.3692 | 233.2316
1400.6135 | 324.3676 | 228.3797 | 233.2013
1401.6135 | 324.2662 | 228.3768 | 233.1837
1402.6135 | 324.1925 | 228.3027 | 233.1711
1403.6135 | 324.1617 | 228.2238 | 233.1456
1404.6135 | 324.2411 | 228.1283 | 233.1412
1405.6135 | 324.4131 | 228.0698 | 233.1281
1406.6135 | 324.5008 | 228.0167 | 233.0834
1407.6135 | 324.5617 | 228.0281 | 232.9885
1408.6135 | 324.6053 | 228.0404 | 232.8952
1409.6135 | 324.6813 | 228.0745 | 232.8418
1410.6135 | 324.8371 | 228.0895 | 232.8204
1411.6135 | 324.7911 | 228.1278 | 232.8331
1412.6135 | 324.7256 | 228.1196 | 232.8315
1413.6135 | 324.8001 | 228.0952 | 232.7783
1414.6135 | 324.9057 | 228.0946 | 232.7289
1415.6135 | 324.9311 | 228.1225 | 232.6988
1416.6135 | 324.8998 | 228.1611 | 232.6859
1417.6135 | 324.8945 | 228.2119 | 232.7013
1418.6135 | 324.8289 | 228.2722 | 232.6977
1419.6135 | 324.811 | 228.2697 | 232.6986
1420.6135 | 324.8167 | 228.1792 | 232.6626
1421.6135 | 324.9442 | 228.1195 | 232.6318
1422.6135 | 325.0704 | 228.0679 | 232.6147
1423.6135 | 325.055 | 228.0362 | 232.6161
1424.6135 | 325.0587 | 228.0237 | 232.6198
1425.6135 | 324.9788 | 228.032 | 232.6004
1426.6135 | 324.935 | 228.0382 | 232.5691
1427.6135 | 324.8288 | 228.0541 | 232.5793
1428.6135 | 324.7988 | 228.0988 | 232.5809
1429.6135 | 324.8041 | 228.1527 | 232.5574
1430.6135 | 324.8312 | 228.1836 | 232.5377
1431.6135 | 324.8598 | 228.2083 | 232.4846
1432.6135 | 324.9113 | 228.2807 | 232.3646
1433.6135 | 324.863 | 228.3391 | 232.2306
1434.6135 | 324.9373 | 228.4194 | 232.1723
1435.6135 | 325.015 | 228.4837 | 232.1569
1436.6135 | 325.2001 | 228.5637 | 232.147
1437.6135 | 325.1967 | 228.6455 | 232.0909
1438.6135 | 325.1195 | 228.7071 | 232.0946
1439.6135 | 325.1603 | 228.7135 | 232.1265
1440.6135 | 325.2201 | 228.6999 | 232.1774
1441.6135 | 325.2333 | 228.7054 | 232.2525
1442.6135 | 325.2442 | 228.6944 | 232.3274
1443.6135 | 325.3726 | 228.6767 | 232.3881
1444.6135 | 325.388 | 228.6433 | 232.4235
1445.6135 | 325.2724 | 228.5354 | 232.4956
1446.6135 | 325.2157 | 228.4591 | 232.5652
1447.6135 | 325.1735 | 228.4259 | 232.6374
1448.6135 | 325.1902 | 228.3841 | 232.7051
1449.6135 | 325.1834 | 228.318 | 232.7985
1450.6135 | 325.1996 | 228.2715 | 232.8745
1451.6135 | 325.2762 | 228.2136 | 232.9405
1452.6135 | 325.2036 | 228.2047 | 232.981
1453.6135 | 325.1778 | 228.1829 | 232.9684
1454.6135 | 325.2635 | 228.1956 | 232.9435
1455.6135 | 325.2798 | 228.2404 | 232.9514
1456.6135 | 325.3042 | 228.2502 | 232.9589
1457.6135 | 325.3361 | 228.2845 | 232.9579
1458.6135 | 325.3658 | 228.3772 | 232.9479
1459.6135 | 325.3472 | 228.4762 | 232.8981
1460.6135 | 325.1974 | 228.6061 | 232.8057
1461.6135 | 325.2754 | 228.7092 | 232.673
1462.6135 | 325.3166 | 228.7996 | 232.5749
1463.6135 | 325.3607 | 228.8299 | 232.5324
1464.6135 | 325.4171 | 228.8557 | 232.5407
1465.6135 | 325.4322 | 228.905 | 232.5485
1466.6135 | 325.3361 | 228.9569 | 232.5641
1467.6135 | 325.4188 | 228.9899 | 232.5469
1468.6135 | 325.4146 | 228.9905 | 232.5479
1469.6135 | 325.4899 | 228.9543 | 232.6136
1470.6135 | 325.5353 | 228.8869 | 232.7034
1471.6135 | 325.5017 | 228.8606 | 232.8267
1472.6135 | 325.3955 | 228.8279 | 232.9401
1473.6135 | 325.3875 | 228.8278 | 233.0035
1474.6135 | 325.4813 | 228.8017 | 233.0287
1475.6135 | 325.5611 | 228.7938 | 233.0646
1476.6135 | 325.5895 | 228.8287 | 233.0842
1477.6135 | 325.5088 | 228.8118 | 233.0901
1478.6135 | 325.3183 | 228.7824 | 233.0848
1479.6135 | 325.2556 | 228.7222 | 233.0856
1480.6135 | 325.2064 | 228.7063 | 233.079
1481.6135 | 325.2091 | 228.6879 | 233.0623
1482.6135 | 325.1468 | 228.6712 | 233.0817
1483.6135 | 325.1044 | 228.6607 | 233.1478
1484.6135 | 325.1511 | 228.6428 | 233.2313
1485.6135 | 325.2133 | 228.6446 | 233.2966
1486.6135 | 325.2976 | 228.5975 | 233.3386
1487.6135 | 325.3668 | 228.5717 | 233.3833
1488.6135 | 325.2924 | 228.5617 | 233.4349
1489.6135 | 325.1963 | 228.5275 | 233.4756
1490.6135 | 325.2319 | 228.4714 | 233.5181
1491.6135 | 325.1872 | 228.4161 | 233.5654
1492.6135 | 325.1164 | 228.3473 | 233.5827
1493.6135 | 325.1212 | 228.2994 | 233.5529
1494.6135 | 325.1182 | 228.2778 | 233.5058
1495.6135 | 325.0962 | 228.2609 | 233.4476
1496.6135 | 325.0838 | 228.2781 | 233.4041
1497.6135 | 325.2018 | 228.2942 | 233.3696
1498.6135 | 325.3378 | 228.3309 | 233.3365
1499.6135 | 325.4006 | 228.3287 | 233.3332
1500.6135 | 325.3895 | 228.3237 | 233.3286
1501.6135 | 325.3783 | 228.3397 | 233.338
1502.6135 | 325.3957 | 228.3592 | 233.3159
1503.6135 | 325.3229 | 228.4071 | 233.1924
1504.6135 | 325.0986 | 228.4451 | 233.0733
1505.6135 | 324.9415 | 228.4618 | 233.0357
1506.6135 | 324.9385 | 228.4581 | 233.0667
1507.6135 | 325.0105 | 228.4457 | 233.129
1508.6135 | 325.1008 | 228.4305 | 233.1823
1509.6135 | 325.0625 | 228.4072 | 233.2446
1510.6135 | 325.058 | 228.4138 | 233.2715
1511.6135 | 325.0679 | 228.3949 | 233.2725
1512.6135 | 325.1072 | 228.4081 | 233.2679
1513.6135 | 325.0813 | 228.4199 | 233.2662
1514.6135 | 325.0223 | 228.4189 | 233.2555
1515.6135 | 324.9902 | 228.4353 | 233.2336
1516.6135 | 324.9502 | 228.4174 | 233.2193
1517.6135 | 324.9638 | 228.4519 | 233.2226
1518.6135 | 324.9419 | 228.4776 | 233.2645
1519.6135 | 324.8536 | 228.4854 | 233.2877
1520.6135 | 324.8906 | 228.4679 | 233.3056
1521.6135 | 324.9363 | 228.4326 | 233.35
1522.6135 | 325.0551 | 228.4363 | 233.3572
1523.6135 | 325.0732 | 228.4656 | 233.322
1524.6135 | 325.0219 | 228.4733 | 233.3254
1525.6135 | 325.0859 | 228.4889 | 233.3154
1526.6135 | 325.2018 | 228.4958 | 233.312
1527.6135 | 325.1878 | 228.505 | 233.3353
1528.6135 | 325.2308 | 228.5164 | 233.38
1529.6135 | 325.1865 | 228.5089 | 233.4014
1530.6135 | 325.2279 | 228.4695 | 233.4241
1531.6135 | 325.235 | 228.4343 | 233.4688
1532.6135 | 325.2317 | 228.4114 | 233.5102
1533.6135 | 325.283 | 228.4066 | 233.5479
1534.6135 | 325.4364 | 228.4121 | 233.6009
1535.6135 | 325.5476 | 228.4052 | 233.6566
1536.6135 | 325.4787 | 228.3261 | 233.683
1537.6135 | 325.3897 | 228.2654 | 233.6998
1538.6135 | 325.471 | 228.2222 | 233.7116
1539.6135 | 325.4307 | 228.2199 | 233.7078
1540.6135 | 325.3491 | 228.2685 | 233.677
1541.6135 | 325.3133 | 228.3525 | 233.6104
1542.6135 | 325.4182 | 228.3722 | 233.5256
1543.6135 | 325.3731 | 228.338 | 233.4773
1544.6135 | 325.3783 | 228.367 | 233.4531
1545.6135 | 325.4569 | 228.3876 | 233.4283
1546.6135 | 325.4059 | 228.3882 | 233.4185
1547.6135 | 325.3159 | 228.4116 | 233.4175
1548.6135 | 325.1452 | 228.3968 | 233.4139
1549.6135 | 325.0668 | 228.3808 | 233.4262
1550.6135 | 324.9021 | 228.4108 | 233.4241
1551.6135 | 324.8269 | 228.4402 | 233.4426
1552.6135 | 324.7249 | 228.4598 | 233.4763
1553.6135 | 324.5979 | 228.4604 | 233.4706
1554.6135 | 324.5909 | 228.5348 | 233.4489
1555.6135 | 324.6161 | 228.5916 | 233.431
1556.6135 | 324.6815 | 228.6169 | 233.4362
1557.6135 | 324.7977 | 228.6455 | 233.4484
1558.6135 | 324.8125 | 228.6633 | 233.4435
1559.6135 | 324.7881 | 228.6603 | 233.4565
1560.6135 | 324.8508 | 228.7102 | 233.4342
1561.6135 | 324.8739 | 228.7826 | 233.3994
1562.6135 | 324.8588 | 228.7988 | 233.361
1563.6135 | 324.897 | 228.7701 | 233.3307
1564.6135 | 324.8049 | 228.7361 | 233.309
1565.6135 | 324.6152 | 228.6852 | 233.3225
1566.6135 | 324.6254 | 228.641 | 233.3665
1567.6135 | 324.6133 | 228.6329 | 233.4307
1568.6135 | 324.6994 | 228.6404 | 233.4793
1569.6135 | 324.7515 | 228.6285 | 233.5368
1570.6135 | 324.7646 | 228.6165 | 233.5633
1571.6135 | 324.8251 | 228.6353 | 233.5878
1572.6135 | 324.7766 | 228.645 | 233.6345
1573.6135 | 324.7565 | 228.6628 | 233.6376
1574.6135 | 324.7833 | 228.6506 | 233.6375
1575.6135 | 324.7513 | 228.6726 | 233.6574
1576.6135 | 324.8369 | 228.6702 | 233.7029
1577.6135 | 324.8603 | 228.6704 | 233.7758
1578.6135 | 324.8647 | 228.6624 | 233.8342
1579.6135 | 324.8631 | 228.6863 | 233.8198
1580.6135 | 324.8723 | 228.738 | 233.8029
1581.6135 | 324.8679 | 228.7689 | 233.7936
1582.6135 | 324.8512 | 228.8122 | 233.7802
1583.6135 | 324.7825 | 228.8024 | 233.7947
1584.6135 | 324.9282 | 228.8021 | 233.8274
1585.6135 | 325.047 | 228.7943 | 233.8379
1586.6135 | 325.0904 | 228.7916 | 233.8195
1587.6135 | 325.1192 | 228.8622 | 233.7717
1588.6135 | 325.2809 | 228.8712 | 233.7519
1589.6135 | 325.3571 | 228.9158 | 233.7423
1590.6135 | 325.3579 | 228.9543 | 233.722
1591.6135 | 325.41 | 228.9915 | 233.6852
1592.6135 | 325.4875 | 228.9858 | 233.6502
1593.6135 | 325.4489 | 229.0109 | 233.607
1594.6135 | 325.3534 | 229.0655 | 233.5432
1595.6135 | 325.2711 | 229.0831 | 233.4734
1596.6135 | 325.3047 | 229.115 | 233.4405
1597.6135 | 325.3048 | 229.1474 | 233.448
1598.6135 | 325.1804 | 229.1545 | 233.4317
1599.6135 | 325.2523 | 229.1493 | 233.3949
1600.6135 | 325.2702 | 229.1031 | 233.2978
1601.6135 | 325.275 | 229.1173 | 233.1854
1602.6135 | 325.252 | 229.1119 | 233.0866
1603.6135 | 325.2097 | 229.113 | 233.0256
1604.6135 | 325.2034 | 229.1484 | 232.9997
1605.6135 | 325.1843 | 229.1424 | 233.0212
1606.6135 | 325.1684 | 229.114 | 233.0316
1607.6135 | 325.1317 | 229.0589 | 233.0443
1608.6135 | 325.2292 | 229.0089 | 233.0695
1609.6135 | 325.7034 | 228.9921 | 233.0801
1610.6135 | 326.9401 | 228.999 | 233.0877
1611.6135 | 328.9885 | 229.0159 | 233.1408
1612.6135 | 331.5449 | 229.1071 | 233.243
1613.6135 | 334.5989 | 229.2376 | 233.4063
1614.6135 | 337.8509 | 229.3704 | 233.581
1615.6135 | 341.2342 | 229.5214 | 233.7631
1616.6135 | 344.5141 | 229.7168 | 233.962
1617.6135 | 347.6855 | 229.9472 | 234.194
1618.6135 | 350.5591 | 230.1849 | 234.3959
1619.6135 | 353.1753 | 230.4368 | 234.5421
1620.6135 | 355.3519 | 230.7329 | 234.6838
1621.6135 | 357.3511 | 231.0174 | 234.8069
1622.6135 | 358.9441 | 231.2751 | 235.0105
1623.6135 | 360.1119 | 231.5299 | 235.2963
1624.6135 | 360.9841 | 231.7871 | 235.5947
1625.6135 | 361.7216 | 232.0795 | 235.8822
1626.6135 | 362.3146 | 232.3642 | 236.1417
1627.6135 | 362.7745 | 232.6258 | 236.3478
1628.6135 | 363.0754 | 232.8749 | 236.5739
1629.6135 | 363.1932 | 233.0987 | 236.7861
1630.6135 | 363.1861 | 233.3133 | 237.0336
1631.6135 | 363.0725 | 233.4774 | 237.288
1632.6135 | 362.9421 | 233.6225 | 237.4874
1633.6135 | 362.6909 | 233.746 | 237.6716
1634.6135 | 362.4204 | 233.884 | 237.8563
1635.6135 | 362.0736 | 233.9907 | 238.0578
1636.6135 | 361.5615 | 234.124 | 238.2484
1637.6135 | 361.1096 | 234.2333 | 238.3937
1638.6135 | 360.7132 | 234.345 | 238.5453
1639.6135 | 360.2382 | 234.4662 | 238.6868
1640.6135 | 359.7885 | 234.587 | 238.8243
1641.6135 | 359.2915 | 234.6583 | 238.9568
1642.6135 | 358.5909 | 234.6815 | 239.0893
1643.6135 | 358.1021 | 234.7513 | 239.2653
1644.6135 | 357.457 | 234.782 | 239.4444
1645.6135 | 356.946 | 234.821 | 239.6042
1646.6135 | 356.6676 | 234.848 | 239.7207
1647.6135 | 356.048 | 234.9034 | 239.8396
1648.6135 | 355.3165 | 234.956 | 239.9878
1649.6135 | 354.6568 | 234.9822 | 240.1055
1650.6135 | 354.0115 | 235.0103 | 240.2157
1651.6135 | 353.3835 | 235.0389 | 240.2931
1652.6135 | 352.7304 | 235.0722 | 240.3237
1653.6135 | 352.2098 | 235.1135 | 240.3498
1654.6135 | 351.621 | 235.1443 | 240.4095
1655.6135 | 351.1377 | 235.1854 | 240.4579
1656.6135 | 350.6009 | 235.2383 | 240.5041
1657.6135 | 350.0641 | 235.3063 | 240.5342
1658.6135 | 349.6452 | 235.2965 | 240.5346
1659.6135 | 349.1769 | 235.3188 | 240.5599
1660.6135 | 348.7428 | 235.3674 | 240.6275
1661.6135 | 348.307 | 235.4414 | 240.7059
1662.6135 | 348.0314 | 235.5009 | 240.7788
1663.6135 | 347.6939 | 235.5234 | 240.8542
1664.6135 | 347.4845 | 235.5602 | 240.9351
1665.6135 | 347.2758 | 235.6071 | 240.9838
1666.6135 | 346.9977 | 235.6603 | 241.0132
1667.6135 | 346.69 | 235.7217 | 241.0289
1668.6135 | 346.5644 | 235.7702 | 241.0328
1669.6135 | 346.405 | 235.7751 | 241.0306
1670.6135 | 346.4095 | 235.7724 | 240.994
1671.6135 | 346.4929 | 235.7786 | 240.9978
1672.6135 | 346.4963 | 235.8054 | 241.0182
1673.6135 | 346.5186 | 235.8673 | 241.0605
1674.6135 | 346.8001 | 235.9587 | 241.0746
1675.6135 | 346.9364 | 236.1041 | 241.1159
1676.6135 | 347.0618 | 236.2287 | 241.2118
1677.6135 | 347.2255 | 236.3187 | 241.2811
1678.6135 | 347.4152 | 236.379 | 241.3491
1679.6135 | 347.6921 | 236.3713 | 241.4066
1680.6135 | 347.8595 | 236.3665 | 241.5015
1681.6135 | 348.1225 | 236.3546 | 241.5933
1682.6135 | 348.3535 | 236.391 | 241.7189
1683.6135 | 348.6388 | 236.4492 | 241.8726
1684.6135 | 348.782 | 236.5464 | 241.9644
1685.6135 | 348.9293 | 236.6654 | 242.0624
1686.6135 | 349.0914 | 236.7708 | 242.1601
1687.6135 | 349.1183 | 236.809 | 242.2516
1688.6135 | 349.3118 | 236.878 | 242.3256
1689.6135 | 349.5962 | 237.0096 | 242.3974
1690.6135 | 349.8284 | 237.0646 | 242.3921
1691.6135 | 349.7735 | 237.1239 | 242.4771
1692.6135 | 349.9894 | 237.2262 | 242.4803
1693.6135 | 350.3753 | 237.3519 | 242.4523
1694.6135 | 350.626 | 237.5096 | 242.4626
1695.6135 | 350.7338 | 237.6835 | 242.4725
1696.6135 | 350.779 | 237.8477 | 242.5097
1697.6135 | 350.7542 | 237.9911 | 242.546
1698.6135 | 350.8727 | 238.0674 | 242.598
1699.6135 | 350.9685 | 238.1232 | 242.6565
1700.6135 | 351.0642 | 238.1725 | 242.7196
1701.6135 | 351.1342 | 238.2433 | 242.8538
1702.6135 | 350.9986 | 238.3339 | 242.9701
1703.6135 | 351.0532 | 238.4296 | 243.0398
1704.6135 | 351.0189 | 238.5245 | 243.0686
1705.6135 | 351.0764 | 238.6403 | 243.0638
1706.6135 | 351.0935 | 238.7944 | 243.1019
1707.6135 | 351.0391 | 238.9516 | 243.1532
1708.6135 | 350.9018 | 239.0955 | 243.1723
1709.6135 | 350.9669 | 239.1263 | 243.1965
1710.6135 | 351.0361 | 239.1223 | 243.252
1711.6135 | 350.9957 | 239.112 | 243.3309
1712.6135 | 351.0708 | 239.1419 | 243.3896
1713.6135 | 351.0266 | 239.1863 | 243.4686
1714.6135 | 350.9678 | 239.2266 | 243.547
1715.6135 | 350.9417 | 239.2828 | 243.647
1716.6135 | 350.9195 | 239.3176 | 243.7626
1717.6135 | 350.9171 | 239.3482 | 243.8624
1718.6135 | 350.8318 | 239.4132 | 243.9214
1719.6135 | 350.7667 | 239.4781 | 243.9692
1720.6135 | 350.7654 | 239.5536 | 243.9795
1721.6135 | 350.6827 | 239.5871 | 243.9607
1722.6135 | 350.5983 | 239.6309 | 243.9376
1723.6135 | 350.5034 | 239.6956 | 244.0017
1724.6135 | 350.5028 | 239.7806 | 244.0377
1725.6135 | 350.4353 | 239.8943 | 244.0684
1726.6135 | 350.3519 | 239.9902 | 244.0954
1727.6135 | 350.3267 | 240.0575 | 244.1596
1728.6135 | 350.4559 | 240.1043 | 244.1959
1729.6135 | 350.4886 | 240.128 | 244.2398
1730.6135 | 350.5157 | 240.1806 | 244.2771
1731.6135 | 350.4927 | 240.2655 | 244.3229
1732.6135 | 350.4447 | 240.3352 | 244.3795
1733.6135 | 350.4302 | 240.4053 | 244.4366
1734.6135 | 350.3693 | 240.4357 | 244.5555
1735.6135 | 350.3933 | 240.4881 | 244.6854
1736.6135 | 350.4325 | 240.5925 | 244.8207
1737.6135 | 350.4618 | 240.6889 | 244.9482
1738.6135 | 350.5466 | 240.7382 | 245.0414
1739.6135 | 350.6346 | 240.7528 | 245.0599
1740.6135 | 350.5875 | 240.7735 | 245.0869
1741.6135 | 350.5725 | 240.8138 | 245.1434
1742.6135 | 350.5644 | 240.8939 | 245.1557
1743.6135 | 350.4637 | 240.9649 | 245.1008
1744.6135 | 350.567 | 240.991 | 245.0518
1745.6135 | 350.5656 | 240.9906 | 245.0437
1746.6135 | 350.429 | 241.0247 | 245.0653
1747.6135 | 350.4158 | 241.068 | 245.1327
1748.6135 | 350.375 | 241.1305 | 245.221
1749.6135 | 350.1218 | 241.1905 | 245.2945
1750.6135 | 350.0797 | 241.2562 | 245.3162
1751.6135 | 350.0751 | 241.3401 | 245.3322
1752.6135 | 350.0911 | 241.4135 | 245.3719
1753.6135 | 350.091 | 241.4778 | 245.4323
1754.6135 | 350.1246 | 241.5118 | 245.5025
1755.6135 | 350.097 | 241.558 | 245.5752
1756.6135 | 349.9534 | 241.6031 | 245.6322
1757.6135 | 349.9952 | 241.6751 | 245.6432
1758.6135 | 350.0247 | 241.7272 | 245.6694
1759.6135 | 350.0228 | 241.8197 | 245.7385
1760.6135 | 349.9997 | 241.8346 | 245.834
1761.6135 | 350.1401 | 241.8337 | 245.9225
1762.6135 | 350.2554 | 241.8306 | 245.9752
1763.6135 | 350.2452 | 241.8622 | 246.0246
1764.6135 | 350.2754 | 241.9304 | 246.111
1765.6135 | 350.2898 | 242.0147 | 246.1782
1766.6135 | 350.27 | 242.1404 | 246.2119
1767.6135 | 350.1666 | 242.2618 | 246.2506
1768.6135 | 350.1057 | 242.3879 | 246.2588
1769.6135 | 350.2011 | 242.5449 | 246.2591
1770.6135 | 350.2186 | 242.6644 | 246.2689
1771.6135 | 350.2713 | 242.7551 | 246.2739
1772.6135 | 350.342 | 242.8347 | 246.2982
1773.6135 | 350.4192 | 242.8829 | 246.3198
1774.6135 | 350.5284 | 242.9432 | 246.3216
1775.6135 | 350.5801 | 242.9739 | 246.3793
1776.6135 | 350.7382 | 243.0263 | 246.4353
1777.6135 | 350.7314 | 243.0909 | 246.4521
1778.6135 | 350.6447 | 243.1498 | 246.4518
1779.6135 | 350.6762 | 243.1801 | 246.5084
1780.6135 | 350.6161 | 243.2165 | 246.6093
1781.6135 | 350.6754 | 243.2452 | 246.6998
1782.6135 | 350.6176 | 243.2272 | 246.813
1783.6135 | 350.541 | 243.1967 | 246.8998
1784.6135 | 350.5197 | 243.2172 | 246.9971
1785.6135 | 350.4943 | 243.2844 | 247.0954
1786.6135 | 350.4094 | 243.3436 | 247.217
1787.6135 | 350.2406 | 243.3713 | 247.2874
1788.6135 | 350.0995 | 243.3985 | 247.3113
1789.6135 | 350.0842 | 243.4162 | 247.296
1790.6135 | 350.182 | 243.4749 | 247.2901
1791.6135 | 350.2109 | 243.515 | 247.3193
1792.6135 | 350.2364 | 243.5452 | 247.3922
1793.6135 | 350.2415 | 243.5783 | 247.4566
1794.6135 | 350.1527 | 243.5804 | 247.5354
1795.6135 | 350.1162 | 243.5686 | 247.6377
1796.6135 | 350.1292 | 243.5515 | 247.7106
1797.6135 | 350.1564 | 243.5334 | 247.8127
1798.6135 | 350.1511 | 243.5111 | 247.9342
1799.6135 | 350.0119 | 243.4727 | 248.0285
1800.6135 | 350.07 | 243.4974 | 248.0811
1801.6135 | 350.1013 | 243.5024 | 248.1384
1802.6135 | 350.0607 | 243.4793 | 248.2443
1803.6135 | 350.0314 | 243.4661 | 248.338
1804.6135 | 349.9239 | 243.4681 | 248.446
1805.6135 | 349.8316 | 243.4591 | 248.5624
1806.6135 | 349.8426 | 243.509 | 248.6573
1807.6135 | 349.8101 | 243.575 | 248.7044
1808.6135 | 349.8032 | 243.6316 | 248.7592
1809.6135 | 349.8523 | 243.6497 | 248.7998
1810.6135 | 349.8866 | 243.7214 | 248.8403
1811.6135 | 349.9562 | 243.777 | 248.893
1812.6135 | 350.0462 | 243.9108 | 248.934
1813.6135 | 350.1404 | 243.9658 | 248.9972
1814.6135 | 350.0936 | 243.9814 | 249.0691
1815.6135 | 350.1278 | 243.9921 | 249.1044
1816.6135 | 350.29 | 244.0104 | 249.1273
1817.6135 | 350.3166 | 244.0966 | 249.1819
1818.6135 | 350.4044 | 244.1714 | 249.2542
1819.6135 | 350.5192 | 244.2315 | 249.3222
1820.6135 | 350.6103 | 244.2907 | 249.3606
1821.6135 | 350.5767 | 244.3602 | 249.3551
1822.6135 | 350.605 | 244.435 | 249.3544
1823.6135 | 350.5949 | 244.4853 | 249.3655
1824.6135 | 350.5786 | 244.5331 | 249.3286
1825.6135 | 350.6043 | 244.5781 | 249.328
1826.6135 | 350.5604 | 244.641 | 249.3022
1827.6135 | 350.5284 | 244.706 | 249.3217
1828.6135 | 350.5065 | 244.7527 | 249.3623
1829.6135 | 350.5365 | 244.8379 | 249.3369
1830.6135 | 350.5076 | 244.9538 | 249.2899
1831.6135 | 350.5462 | 245.0708 | 249.2598
1832.6135 | 350.5264 | 245.129 | 249.2753
1833.6135 | 350.4249 | 245.2084 | 249.2977
1834.6135 | 350.3958 | 245.2715 | 249.3278
1835.6135 | 350.3279 | 245.3113 | 249.382
1836.6135 | 350.1714 | 245.3603 | 249.4211
1837.6135 | 350.1489 | 245.4147 | 249.4773
1838.6135 | 350.0447 | 245.4452 | 249.5617
1839.6135 | 349.9333 | 245.4241 | 249.605
1840.6135 | 349.9399 | 245.4453 | 249.592
1841.6135 | 349.9164 | 245.4842 | 249.5608
1842.6135 | 349.8969 | 245.5135 | 249.5555
1843.6135 | 349.877 | 245.5542 | 249.5926
1844.6135 | 349.8806 | 245.5672 | 249.6108
1845.6135 | 349.7837 | 245.5929 | 249.612
1846.6135 | 349.6578 | 245.5936 | 249.5954
1847.6135 | 349.7143 | 245.6388 | 249.5413
1848.6135 | 349.9002 | 245.6804 | 249.4882
1849.6135 | 350.0453 | 245.6623 | 249.4998
1850.6135 | 350.1028 | 245.6669 | 249.5342
1851.6135 | 350.128 | 245.6343 | 249.5862
1852.6135 | 350.1394 | 245.662 | 249.6241
1853.6135 | 350.0942 | 245.6697 | 249.6655
1854.6135 | 350.057 | 245.6746 | 249.692
1855.6135 | 350.1383 | 245.6837 | 249.7332
1856.6135 | 350.1715 | 245.7014 | 249.7825
1857.6292 | 350.2133 | 245.7733 | 249.8311
1858.6135 | 350.3321 | 245.8681 | 249.8934
1859.6135 | 350.3939 | 245.9601 | 249.9545
1860.6135 | 350.484 | 246.0303 | 250.0028
1861.6135 | 350.5593 | 246.1205 | 250.0028
1862.6135 | 350.6697 | 246.1916 | 249.9996
1863.6135 | 350.6803 | 246.2486 | 250.0094
1864.6135 | 350.72 | 246.2768 | 250.0483
1865.6135 | 350.7289 | 246.2936 | 250.1134
1866.6135 | 350.8562 | 246.2902 | 250.1783
1867.6135 | 350.961 | 246.2606 | 250.212
1868.6135 | 350.9163 | 246.278 | 250.2045
1869.6135 | 350.8615 | 246.3045 | 250.2314
1870.6135 | 350.9641 | 246.2983 | 250.246
1871.6135 | 351.0128 | 246.2503 | 250.2576
1872.6135 | 350.8526 | 246.1603 | 250.3028
1873.6135 | 350.9909 | 246.1536 | 250.3515
1874.6135 | 351.0621 | 246.1699 | 250.3964
1875.6135 | 351.0463 | 246.1903 | 250.4576
1876.6135 | 350.9221 | 246.2412 | 250.5398
1877.6135 | 350.908 | 246.2752 | 250.5951
1878.6135 | 350.8557 | 246.3131 | 250.6448
1879.6135 | 350.8574 | 246.3345 | 250.6677
1880.6135 | 350.7685 | 246.3802 | 250.6954
1881.6135 | 350.7645 | 246.4343 | 250.7487
1882.6135 | 350.7697 | 246.4515 | 250.8135
1883.6135 | 350.7315 | 246.4942 | 250.8825
1884.6135 | 350.6942 | 246.541 | 250.9455
1885.6135 | 350.6627 | 246.6109 | 250.9964
1886.6135 | 350.6398 | 246.6648 | 251.019
1887.6135 | 350.6459 | 246.6655 | 251.0074
1888.6135 | 350.6072 | 246.6838 | 251.0011
1889.6135 | 350.5043 | 246.6851 | 250.9534
1890.6135 | 350.443 | 246.7289 | 250.8902
1891.6135 | 350.4593 | 246.7659 | 250.8567
1892.6135 | 350.3711 | 246.7853 | 250.8578
1893.6135 | 350.3178 | 246.8802 | 250.8855
1894.6135 | 350.368 | 246.9569 | 250.9227
1895.6135 | 350.2511 | 246.9978 | 250.9277
1896.6135 | 350.1475 | 247.0322 | 250.9235
1897.6135 | 350.1506 | 247.0597 | 250.9803
1898.6135 | 350.1852 | 247.0841 | 251.0591
1899.6135 | 350.0229 | 247.1328 | 251.0836
1900.6135 | 349.9434 | 247.1594 | 251.112
1901.6135 | 349.9198 | 247.1875 | 251.1856
1902.6135 | 349.9174 | 247.2253 | 251.2847
1903.6135 | 349.889 | 247.2683 | 251.363
1904.6135 | 349.9135 | 247.2959 | 251.4072
1905.6135 | 350.0233 | 247.3478 | 251.3952
1906.6135 | 350.0369 | 247.3748 | 251.3713
1907.6135 | 350.0635 | 247.4241 | 251.3045
1908.6135 | 350.0069 | 247.4977 | 251.295
1909.6135 | 350.1083 | 247.5628 | 251.2943
1910.6135 | 350.0991 | 247.6749 | 251.3413
1911.6135 | 350.0968 | 247.7192 | 251.4397
1912.6135 | 350.1307 | 247.7798 | 251.5689
1913.6135 | 350.1206 | 247.8212 | 251.6605
1914.6135 | 350.2054 | 247.8414 | 251.7458
1915.6135 | 350.2863 | 247.8324 | 251.8197
1916.6135 | 350.4223 | 247.8371 | 251.8639
1917.6135 | 350.3929 | 247.8818 | 251.9064
1918.6135 | 350.3537 | 247.9099 | 251.9379
1919.6135 | 350.2891 | 247.9088 | 251.9731
1920.6135 | 350.2204 | 247.8575 | 251.9726
1921.6135 | 350.1848 | 247.8501 | 252.0463
1922.6135 | 350.0821 | 247.804 | 252.0938
1923.6135 | 350.0546 | 247.7883 | 252.1294
1924.6135 | 350.0972 | 247.7439 | 252.2008
1925.6135 | 350.1668 | 247.7193 | 252.2389
1926.6135 | 350.3063 | 247.6838 | 252.3047
1927.6135 | 350.3089 | 247.6772 | 252.3783
1928.6135 | 350.4218 | 247.7113 | 252.4571
1929.6135 | 350.4223 | 247.7378 | 252.5287
1930.6135 | 350.4416 | 247.7697 | 252.6027
1931.6135 | 350.4938 | 247.8284 | 252.6634
1932.6135 | 350.6071 | 247.8846 | 252.6776
1933.6135 | 350.6431 | 247.9388 | 252.7172
1934.6135 | 350.6852 | 247.9511 | 252.7908
1935.6135 | 350.6733 | 247.9638 | 252.8944
1936.6135 | 350.6816 | 247.969 | 252.9815
1937.6135 | 350.7192 | 247.9751 | 253.0636
1938.6135 | 350.6741 | 247.9988 | 253.1299
1939.6135 | 350.7494 | 247.9798 | 253.1612
1940.6135 | 350.7661 | 247.9465 | 253.1929
1941.6135 | 350.8787 | 247.8903 | 253.2088
1942.6135 | 350.9483 | 247.864 | 253.1957
1943.6135 | 351.0919 | 247.836 | 253.2237
1944.6135 | 351.2358 | 247.8068 | 253.2374
1945.6135 | 351.1823 | 247.8323 | 253.2873
1946.6135 | 351.2626 | 247.8855 | 253.3258
1947.6135 | 351.1527 | 247.9221 | 253.3309
1948.6135 | 351.166 | 247.9421 | 253.3404
1949.6135 | 351.2131 | 248.04 | 253.3551
1950.6135 | 351.3202 | 248.0987 | 253.3891
1951.6135 | 351.316 | 248.1476 | 253.4128
1952.6135 | 351.2973 | 248.243 | 253.4396
1953.6135 | 351.2379 | 248.2825 | 253.4637
1954.6135 | 351.2535 | 248.3594 | 253.4714
1955.6135 | 351.2441 | 248.386 | 253.4968
1956.6135 | 351.1873 | 248.3875 | 253.5528
1957.6135 | 351.1087 | 248.4388 | 253.5933
1958.6135 | 351.0328 | 248.5008 | 253.6202
1959.6135 | 351.0543 | 248.5666 | 253.6621
1960.6135 | 351.0286 | 248.6112 | 253.6716
1961.6135 | 351.0077 | 248.6472 | 253.7179
1962.6135 | 351.0059 | 248.6775 | 253.7343
1963.6135 | 350.9402 | 248.6732 | 253.7405
1964.6135 | 350.9338 | 248.6458 | 253.7307
1965.6135 | 350.9139 | 248.6992 | 253.6513
1966.6135 | 350.8467 | 248.7831 | 253.5539
1967.6135 | 350.7783 | 248.8534 | 253.4807
1968.6135 | 350.7052 | 248.8972 | 253.4484
1969.6135 | 350.6238 | 248.9307 | 253.4603
1970.6135 | 350.5956 | 248.9407 | 253.481
1971.6135 | 350.666 | 248.9205 | 253.5091
1972.6135 | 350.6759 | 248.9195 | 253.557
1973.6135 | 350.6557 | 248.9283 | 253.5832
1974.6135 | 350.6886 | 248.9501 | 253.5756
1975.6135 | 350.6464 | 249.0025 | 253.5792
1976.6135 | 350.5988 | 249.0546 | 253.5623
1977.6135 | 350.6131 | 249.1077 | 253.5634
1978.6135 | 350.6615 | 249.1583 | 253.5603
1979.6135 | 350.6289 | 249.1781 | 253.5823
1980.6135 | 350.5626 | 249.1932 | 253.6309
1981.6135 | 350.671 | 249.2367 | 253.7258
1982.6135 | 350.6145 | 249.2634 | 253.7956
1983.6135 | 350.7063 | 249.2308 | 253.8383
1984.6135 | 350.6785 | 249.1727 | 253.836
1985.6135 | 350.7027 | 249.1917 | 253.7859
1986.6135 | 350.72 | 249.2399 | 253.8255
1987.6135 | 350.7834 | 249.2966 | 253.9037
1988.6135 | 350.7202 | 249.32 | 253.9504
1989.6135 | 350.6627 | 249.3282 | 253.9423
1990.6135 | 350.5733 | 249.3622 | 253.8964
1991.6135 | 350.7534 | 249.403 | 253.8359
1992.6135 | 350.8337 | 249.4031 | 253.8336
1993.6135 | 350.909 | 249.4574 | 253.8033
1994.6135 | 350.8175 | 249.507 | 253.7333
1995.6135 | 350.7641 | 249.5756 | 253.6923
1996.6135 | 350.9169 | 249.5855 | 253.6918
1997.6135 | 350.8553 | 249.6233 | 253.7352
1998.6135 | 350.8795 | 249.633 | 253.7913
1999.6135 | 350.9176 | 249.6742 | 253.8468
2000.6135 | 350.9733 | 249.6923 | 253.9048
2001.6135 | 350.992 | 249.6884 | 253.9524
2002.6135 | 350.9468 | 249.6815 | 253.9743
2003.6135 | 350.8306 | 249.6433 | 254.0395
2004.6135 | 350.6671 | 249.5855 | 254.0763
2005.6135 | 350.6413 | 249.5627 | 254.1329
2006.6135 | 350.7231 | 249.5407 | 254.1869
2007.6135 | 350.6277 | 249.5223 | 254.2512
2008.6135 | 350.5425 | 249.5048 | 254.3265
2009.6135 | 350.5776 | 249.541 | 254.3829
2010.6135 | 350.5827 | 249.5816 | 254.4352
2011.6135 | 350.5604 | 249.6259 | 254.4395
2012.6135 | 350.5874 | 249.7227 | 254.4189
2013.6135 | 350.6443 | 249.8266 | 254.3887
2014.6135 | 350.7127 | 249.9517 | 254.3196
2015.6135 | 350.6988 | 250.0319 | 254.2369
2016.6135 | 350.7119 | 250.0458 | 254.216
2017.6135 | 350.7161 | 250.0632 | 254.2064
2018.6135 | 350.8406 | 250.107 | 254.2155
2019.6135 | 350.8414 | 250.1609 | 254.2314
2020.6135 | 350.8581 | 250.2252 | 254.2916
2021.6135 | 351.0306 | 250.2835 | 254.2985
2022.6135 | 351.0557 | 250.3425 | 254.2869
2023.6135 | 350.9717 | 250.3832 | 254.2772
2024.6135 | 350.9751 | 250.3892 | 254.3341
2025.6135 | 351.1277 | 250.4202 | 254.4043
2026.6135 | 351.1747 | 250.4431 | 254.4759
2027.6135 | 351.1759 | 250.4266 | 254.5207
2028.6135 | 351.1049 | 250.4226 | 254.5479
2029.6135 | 350.8916 | 250.3988 | 254.5908
2030.6135 | 350.6292 | 250.4201 | 254.6327
2031.6135 | 350.6031 | 250.4229 | 254.6928
2032.6135 | 350.6019 | 250.4212 | 254.7226
2033.6135 | 350.4618 | 250.3806 | 254.7427
2034.6135 | 350.5213 | 250.3577 | 254.7809
2035.6135 | 350.5631 | 250.3374 | 254.8288
2036.6135 | 350.5308 | 250.3572 | 254.8574
2037.6135 | 350.4751 | 250.3553 | 254.8773
2038.6135 | 350.4928 | 250.3188 | 254.8886
2039.6135 | 350.5 | 250.2627 | 254.8989
2040.6135 | 350.4872 | 250.2543 | 254.9141
2041.6135 | 350.5594 | 250.2605 | 254.9102
2042.6135 | 350.6281 | 250.2687 | 254.9296
2043.6135 | 350.7737 | 250.242 | 254.9672
2044.6135 | 350.9229 | 250.2428 | 255.0391
2045.6135 | 351.1066 | 250.2255 | 255.1258
2046.6135 | 351.2581 | 250.222 | 255.2046
2047.6135 | 351.3503 | 250.1855 | 255.2323
2048.6135 | 351.3513 | 250.1895 | 255.2391
2049.6135 | 351.2785 | 250.2504 | 255.2117
2050.6135 | 351.3208 | 250.2728 | 255.1882
2051.6135 | 351.165 | 250.3277 | 255.1477
2052.6135 | 351.1119 | 250.3764 | 255.1212
2053.6135 | 351.1015 | 250.4193 | 255.101
2054.6135 | 351.1689 | 250.4496 | 255.0786
2055.6135 | 351.214 | 250.5124 | 255.0135
2056.6135 | 351.1848 | 250.5371 | 254.9778
2057.6135 | 351.0284 | 250.5258 | 254.9838
2058.6135 | 351.0901 | 250.4905 | 255.0197
2059.6135 | 351.0569 | 250.4586 | 255.1035
2060.6135 | 351.0833 | 250.433 | 255.1779
2061.6135 | 351.1171 | 250.433 | 255.2006
2062.6135 | 351.054 | 250.4213 | 255.224
2063.6135 | 350.9452 | 250.4326 | 255.2357
2064.6135 | 350.8009 | 250.451 | 255.2326
2065.6135 | 350.8005 | 250.48 | 255.2255
2066.6135 | 350.5905 | 250.5352 | 255.2003
2067.6135 | 350.5143 | 250.6021 | 255.1306
2068.6135 | 350.4625 | 250.6408 | 255.0771
2069.6135 | 350.5168 | 250.6995 | 255.079
2070.6135 | 350.5167 | 250.7161 | 255.1346
2071.6135 | 350.6633 | 250.7422 | 255.1649
2072.6135 | 350.813 | 250.7606 | 255.1854
2073.6135 | 350.8011 | 250.8075 | 255.2088
2074.6135 | 350.5842 | 250.8677 | 255.2267
2075.6135 | 350.5353 | 250.9687 | 255.2199
2076.6135 | 350.5346 | 251.0336 | 255.2314
2077.6135 | 350.4758 | 251.1211 | 255.2019
2078.6135 | 350.3803 | 251.1522 | 255.1702
2079.6135 | 350.2736 | 251.2036 | 255.1045
2080.6135 | 350.4075 | 251.2101 | 255.0186
2081.6135 | 350.492 | 251.2001 | 254.9901
2082.6135 | 350.4943 | 251.158 | 255.0079
2083.6135 | 350.4519 | 251.1166 | 255.0196
2084.6135 | 350.6185 | 251.1201 | 255.0008
2085.6135 | 350.6575 | 251.0867 | 254.9408
2086.6135 | 350.6775 | 251.0769 | 254.9155
2087.6135 | 350.6918 | 251.0662 | 254.9034
2088.6135 | 350.6594 | 251.0908 | 254.8559
2089.6135 | 350.7676 | 251.0461 | 254.8178
2090.6135 | 350.7752 | 251.0376 | 254.7798
2091.6135 | 350.7808 | 251.0077 | 254.7666
2092.6135 | 350.8471 | 251.0223 | 254.7549
2093.6135 | 350.8767 | 251.031 | 254.7077
2094.6135 | 350.9057 | 251.0466 | 254.642
2095.6135 | 350.8484 | 251.0126 | 254.561
2096.6135 | 351.0568 | 250.9572 | 254.5439
2097.6135 | 351.0981 | 250.9252 | 254.5885
2098.6135 | 351.0311 | 250.91 | 254.6742
2099.6135 | 351.0896 | 250.9211 | 254.7658
2100.6135 | 351.2758 | 250.9185 | 254.8437
2101.6135 | 351.2561 | 250.9721 | 254.9408
2102.6135 | 351.2809 | 251.0161 | 255.0294
2103.6135 | 351.3042 | 251.0506 | 255.0706
2104.6135 | 351.1808 | 251.0604 | 255.1691
2105.6135 | 351.1434 | 251.0944 | 255.2572
2106.6135 | 351.0763 | 251.1314 | 255.3051
2107.6135 | 350.9826 | 251.1633 | 255.3548
2108.6135 | 350.8857 | 251.1979 | 255.3432
2109.6135 | 350.8644 | 251.1831 | 255.3335
2110.6135 | 350.7295 | 251.1712 | 255.3599
2111.6135 | 350.746 | 251.1873 | 255.3607
2112.6135 | 350.7441 | 251.2691 | 255.3326
2113.6135 | 350.6646 | 251.3573 | 255.2408
2114.6135 | 350.5489 | 251.4569 | 255.2022
2115.6135 | 350.4895 | 251.5378 | 255.1405
2116.6135 | 350.507 | 251.644 | 255.1279
2117.6135 | 350.5383 | 251.7315 | 255.1039
2118.6135 | 350.4699 | 251.8179 | 255.0763
2119.6135 | 350.376 | 251.9221 | 255.0198
2120.6135 | 350.3599 | 251.9814 | 254.9391
2121.6135 | 350.2772 | 252.057 | 254.8135
2122.6135 | 350.2081 | 252.1425 | 254.6575
2123.6135 | 350.2471 | 252.2146 | 254.5735
2124.6135 | 350.1967 | 252.2883 | 254.5377
2125.6135 | 350.1679 | 252.2915 | 254.5454
2126.6135 | 350.2135 | 252.2544 | 254.5547
2127.6135 | 350.2706 | 252.2239 | 254.5459
2128.6135 | 350.2843 | 252.1903 | 254.5398
2129.6135 | 350.2148 | 252.1748 | 254.559
2130.6135 | 350.163 | 252.1355 | 254.6393
2131.6135 | 350.1382 | 252.0895 | 254.7214
2132.6135 | 350.1982 | 252.0299 | 254.7787
2133.6135 | 350.1995 | 251.9712 | 254.8109
2134.6135 | 350.1877 | 251.8619 | 254.8354
2135.6135 | 350.1987 | 251.7655 | 254.8702
2136.6135 | 350.1228 | 251.7298 | 254.9041
2137.6135 | 350.1517 | 251.7126 | 254.9328
2138.6135 | 350.1655 | 251.7394 | 254.9635
2139.6135 | 350.2263 | 251.7685 | 255.0193
2140.6135 | 350.2233 | 251.7999 | 255.026
2141.6135 | 350.1619 | 251.8041 | 255.0478
2142.6135 | 350.1846 | 251.8154 | 255.0347
2143.6135 | 350.1281 | 251.858 | 255.0466
2144.6135 | 349.9919 | 251.8511 | 255.0713
2145.6135 | 349.8314 | 251.8571 | 255.1412
2146.6135 | 349.6857 | 251.8283 | 255.2108
2147.6135 | 349.6546 | 251.7979 | 255.2897
2148.6135 | 349.7126 | 251.7382 | 255.3415
2149.6135 | 349.7585 | 251.6723 | 255.3911
2150.6135 | 349.6598 | 251.6474 | 255.4283
2151.6135 | 349.5579 | 251.6289 | 255.4503
2152.6135 | 349.6946 | 251.608 | 255.4713
2153.6135 | 349.8056 | 251.5586 | 255.5062
2154.6135 | 349.883 | 251.5566 | 255.5571
2155.6135 | 350.0486 | 251.5283 | 255.6417
2156.6135 | 350.0195 | 251.4846 | 255.7092
2157.6135 | 349.9895 | 251.4777 | 255.7484
2158.6135 | 350.0516 | 251.4598 | 255.788
2159.6135 | 350.0164 | 251.447 | 255.7548
2160.6135 | 349.9835 | 251.4621 | 255.7974
2161.6135 | 349.9866 | 251.47 | 255.8217
2162.6135 | 349.974 | 251.4582 | 255.8537
2163.6135 | 350.0382 | 251.5191 | 255.8117
2164.6135 | 349.9043 | 251.5581 | 255.7537
2165.6135 | 349.859 | 251.6175 | 255.7166
2166.6135 | 349.8455 | 251.6739 | 255.7147
2167.6135 | 349.7897 | 251.7512 | 255.6948
2168.6135 | 349.7466 | 251.7916 | 255.6815
2169.6135 | 349.7152 | 251.8261 | 255.7199
2170.6135 | 349.9117 | 251.8553 | 255.732
2171.6135 | 350.0413 | 251.8968 | 255.7005
2172.6135 | 350.0845 | 251.9497 | 255.6245
2173.6135 | 350.0965 | 251.9463 | 255.6029
2174.6135 | 350.1294 | 251.9379 | 255.6095
2175.6135 | 350.0689 | 251.9411 | 255.6113
2176.6135 | 349.9095 | 251.9202 | 255.5916
2177.6135 | 349.9441 | 251.8658 | 255.6367
2178.6135 | 349.8964 | 251.8164 | 255.6931
2179.6135 | 349.9522 | 251.7807 | 255.6971
2180.6135 | 349.9725 | 251.7657 | 255.6711
2181.6135 | 349.9002 | 251.7751 | 255.661
2182.6135 | 350.059 | 251.7882 | 255.6779
2183.6135 | 350.0978 | 251.8391 | 255.6868
2184.6135 | 350.2011 | 251.8979 | 255.7301
2185.6135 | 350.1576 | 251.9018 | 255.7646
2186.6135 | 350.1284 | 251.9231 | 255.744
2187.6135 | 350.0493 | 251.9176 | 255.6498
2188.6135 | 350.0917 | 251.959 | 255.5056
2189.6135 | 350.0706 | 252.04 | 255.3646
2190.6135 | 349.8942 | 252.1017 | 255.2603
2191.6135 | 349.8625 | 252.1174 | 255.1988
2192.6135 | 349.8117 | 252.0338 | 255.1953
2193.6135 | 349.8523 | 251.9616 | 255.1702
2194.6135 | 349.9365 | 251.9301 | 255.1762
2195.6135 | 349.9992 | 251.9188 | 255.219
2196.6135 | 350.0951 | 251.9464 | 255.25
2197.6135 | 350.006 | 251.9996 | 255.3006
2198.6135 | 349.9467 | 252.0309 | 255.3331
2199.6135 | 349.8975 | 252.0615 | 255.3687
2200.6135 | 349.8222 | 252.0447 | 255.3782
2201.6135 | 349.7988 | 252.0398 | 255.3975
2202.6135 | 349.8313 | 252.1052 | 255.4213
2203.6135 | 349.8094 | 252.1853 | 255.417
2204.6135 | 349.5932 | 252.292 | 255.338
2205.6135 | 349.5442 | 252.3525 | 255.3247
2206.6135 | 349.6201 | 252.3994 | 255.3528
2207.6135 | 349.5044 | 252.4304 | 255.3932
2208.6135 | 349.476 | 252.4433 | 255.3974
2209.6135 | 349.4147 | 252.4424 | 255.363
2210.6135 | 349.4195 | 252.405 | 255.3713
2211.6135 | 349.548 | 252.3822 | 255.389
2212.6135 | 349.581 | 252.3945 | 255.4354
2213.6135 | 349.6534 | 252.3906 | 255.5076
2214.6135 | 349.7256 | 252.4191 | 255.527
2215.6135 | 349.8036 | 252.4477 | 255.4954
2216.6135 | 349.7388 | 252.4882 | 255.4926
2217.6135 | 349.7156 | 252.5134 | 255.5302
2218.6135 | 349.7482 | 252.5961 | 255.5486
2219.6135 | 349.7468 | 252.6453 | 255.5381
2220.6135 | 349.7884 | 252.6534 | 255.5239
2221.6135 | 349.8012 | 252.6105 | 255.5555
2222.6135 | 349.781 | 252.5363 | 255.6097
2223.6135 | 349.7131 | 252.4992 | 255.6406
2224.6135 | 349.7128 | 252.5242 | 255.6265
2225.6135 | 349.7163 | 252.5556 | 255.6339
2226.6135 | 349.7343 | 252.5656 | 255.6944
2227.6135 | 349.7697 | 252.5367 | 255.771
2228.6135 | 349.7782 | 252.5441 | 255.8551
2229.6135 | 349.7518 | 252.5595 | 255.9426
2230.6135 | 349.7985 | 252.5171 | 256.0404
2231.6135 | 349.7702 | 252.491 | 256.1177
2232.6135 | 349.8039 | 252.5028 | 256.1931
2233.6135 | 349.8855 | 252.5296 | 256.2766
2234.6135 | 349.8571 | 252.5182 | 256.3581
2235.6135 | 349.9491 | 252.4987 | 256.4497
2236.6135 | 349.9774 | 252.4618 | 256.5532
2237.6135 | 349.9178 | 252.4198 | 256.6474
2238.6135 | 349.9573 | 252.4101 | 256.7175
2239.6135 | 349.9454 | 252.416 | 256.7685
2240.6135 | 349.8658 | 252.4662 | 256.8084
2241.6135 | 349.7814 | 252.4759 | 256.8496
2242.6135 | 349.7177 | 252.5156 | 256.9231
2243.6135 | 349.708 | 252.4847 | 257.0032
2244.6135 | 349.855 | 252.4568 | 257.0506
2245.6135 | 349.9366 | 252.4581 | 257.0709
2246.6135 | 349.9678 | 252.4665 | 257.0608
2247.6135 | 350.1506 | 252.5026 | 257.018
2248.6135 | 350.2771 | 252.5282 | 256.975
2249.6135 | 350.3509 | 252.539 | 256.8986
2250.6135 | 350.3017 | 252.523 | 256.8695
2251.6135 | 350.5151 | 252.5309 | 256.8101
2252.6135 | 350.4365 | 252.5732 | 256.7636
2253.6135 | 350.3733 | 252.6438 | 256.6964
2254.6135 | 350.2886 | 252.7139 | 256.7277
2255.6135 | 350.2626 | 252.7852 | 256.7661
2256.6135 | 350.215 | 252.8428 | 256.7524
2257.6135 | 350.2416 | 252.9234 | 256.7139
2258.6135 | 350.2522 | 252.9874 | 256.6487
2259.6135 | 350.1768 | 253.0612 | 256.5952
2260.6135 | 350.1368 | 253.0962 | 256.5298
2261.6135 | 349.9805 | 253.1087 | 256.4628
2262.6135 | 350.015 | 253.1164 | 256.3949
2263.6135 | 349.799 | 253.1107 | 256.3632
2264.6135 | 349.8352 | 253.1372 | 256.352
2265.6135 | 349.9273 | 253.1594 | 256.3297
2266.6135 | 349.9932 | 253.152 | 256.3137
2267.6135 | 349.8845 | 253.1667 | 256.2814
2268.6135 | 349.8436 | 253.1703 | 256.3261
2269.6135 | 349.8668 | 253.1775 | 256.3951
2270.6135 | 349.9061 | 253.1803 | 256.4575
2271.6135 | 349.8361 | 253.1808 | 256.5135
2272.6135 | 349.8034 | 253.2181 | 256.5199
2273.6135 | 349.9214 | 253.2495 | 256.5435
2274.6135 | 350.0734 | 253.2438 | 256.612
2275.6135 | 350.0343 | 253.2464 | 256.6835
2276.6135 | 350.0618 | 253.2292 | 256.7728
2277.6135 | 350.0847 | 253.2492 | 256.8599
2278.6135 | 350.1637 | 253.2529 | 256.937
2279.6135 | 350.108 | 253.2165 | 257.0209
2280.6135 | 350.1164 | 253.2323 | 257.0587
2281.6135 | 350.1349 | 253.249 | 257.0449
2282.6135 | 350.1518 | 253.2644 | 257.0072
2283.6135 | 350.2265 | 253.2413 | 256.9606
2284.6135 | 350.2352 | 253.2217 | 256.9428
2285.6135 | 350.2945 | 253.1905 | 256.9615
2286.6135 | 350.2709 | 253.2238 | 256.948
2287.6135 | 350.3951 | 253.2711 | 256.8602
2288.6135 | 350.4422 | 253.3148 | 256.7711
2289.6135 | 350.3176 | 253.3413 | 256.7018
2290.6135 | 350.3105 | 253.3319 | 256.6388
2291.6135 | 350.3842 | 253.3278 | 256.5738
2292.6135 | 350.3079 | 253.3293 | 256.5874
2293.6135 | 350.2393 | 253.3337 | 256.6278
2294.6135 | 350.2677 | 253.3283 | 256.5466
2295.6135 | 350.3889 | 253.3719 | 256.5392
2296.6135 | 350.4979 | 253.4178 | 256.6056
2297.6135 | 350.493 | 253.4583 | 256.6447
2298.6135 | 350.3636 | 253.5256 | 256.669
2299.6135 | 350.325 | 253.5547 | 256.7051
2300.6135 | 350.2083 | 253.5901 | 256.7232
2301.6135 | 350.2028 | 253.5875 | 256.7527
2302.6135 | 350.176 | 253.5829 | 256.7447
2303.6135 | 350.192 | 253.5616 | 256.7039
2304.6135 | 350.2525 | 253.5174 | 256.6987
2305.6135 | 350.2222 | 253.5427 | 256.6894
2306.6135 | 350.2529 | 253.5301 | 256.6654
2307.6135 | 350.2941 | 253.4829 | 256.6392
2308.6135 | 350.374 | 253.4284 | 256.6158
2309.6135 | 350.4146 | 253.3983 | 256.6027
2310.6135 | 350.3736 | 253.3313 | 256.6343
2311.6135 | 350.3206 | 253.2791 | 256.7221
2312.6135 | 350.2502 | 253.2538 | 256.7842
2313.6135 | 350.3273 | 253.2094 | 256.7975
2314.6135 | 350.2774 | 253.2182 | 256.8657
2315.6135 | 350.2085 | 253.245 | 256.9289
2316.6135 | 350.1314 | 253.2646 | 256.9964
2317.6135 | 350.003 | 253.2967 | 257.0642
2318.6135 | 349.9865 | 253.3276 | 257.1091
2319.6135 | 349.9499 | 253.3635 | 257.1833
2320.6135 | 349.9738 | 253.3753 | 257.2721
2321.6135 | 350.0469 | 253.4291 | 257.3396
2322.6135 | 350.1149 | 253.4459 | 257.3868
2323.6135 | 350.2139 | 253.4291 | 257.4242
2324.6135 | 350.202 | 253.4349 | 257.4728
2325.6135 | 350.2711 | 253.4138 | 257.5471
2326.6135 | 350.4148 | 253.4028 | 257.6075
2327.6135 | 350.4565 | 253.38 | 257.6576
2328.6135 | 350.5761 | 253.3639 | 257.6991
2329.6135 | 350.5704 | 253.3732 | 257.6955
2330.6135 | 350.589 | 253.347 | 257.6991
2331.6135 | 350.4852 | 253.313 | 257.7175
2332.6135 | 350.4656 | 253.2569 | 257.7136
2333.6135 | 350.4343 | 253.2536 | 257.6741
2334.6135 | 350.4711 | 253.2695 | 257.6745
2335.6135 | 350.4526 | 253.2961 | 257.6286
2336.6135 | 350.3653 | 253.3161 | 257.5356
2337.6135 | 350.3798 | 253.3156 | 257.4374
2338.6135 | 350.4416 | 253.2986 | 257.3788
2339.6135 | 350.6498 | 253.287 | 257.3771
2340.6135 | 350.7374 | 253.2952 | 257.3542
2341.6135 | 350.7015 | 253.3289 | 257.3391
2342.6135 | 350.7044 | 253.3213 | 257.3376
2343.6135 | 350.7467 | 253.3523 | 257.2954
2344.6135 | 350.7032 | 253.3687 | 257.2863
2345.6135 | 350.6238 | 253.3697 | 257.3354
2346.6135 | 350.7282 | 253.3858 | 257.4277
2347.6135 | 350.6768 | 253.4113 | 257.5126
2348.6135 | 350.6887 | 253.4091 | 257.5952
2349.6135 | 350.7729 | 253.3762 | 257.6562
2350.6135 | 350.846 | 253.32 | 257.7488
2351.6135 | 350.8933 | 253.2683 | 257.8306
2352.6135 | 350.8965 | 253.276 | 257.859
2353.6135 | 350.9 | 253.2748 | 257.8075
2354.6135 | 350.975 | 253.2814 | 257.7703
2355.6135 | 350.9011 | 253.2982 | 257.7151
2356.6135 | 350.8706 | 253.3094 | 257.6793
2357.6135 | 350.9871 | 253.3049 | 257.6716
2358.6135 | 350.9541 | 253.3442 | 257.6753
2359.6135 | 351.1438 | 253.3755 | 257.7313
2360.6135 | 351.3037 | 253.3824 | 257.801
2361.6135 | 351.4329 | 253.4322 | 257.876
2362.6135 | 351.4014 | 253.4289 | 257.9335
2363.6135 | 351.2844 | 253.3983 | 257.9871
2364.6135 | 351.2433 | 253.3795 | 258.0546
2365.6135 | 351.233 | 253.378 | 258.1041
2366.6135 | 351.246 | 253.3525 | 258.1438
2367.6135 | 351.1976 | 253.3348 | 258.2008
2368.6135 | 351.1237 | 253.3348 | 258.2463
2369.6135 | 351.1106 | 253.3047 | 258.2962
2370.6135 | 351.0727 | 253.2514 | 258.3475
2371.6135 | 351.025 | 253.1794 | 258.368
2372.6135 | 350.9239 | 253.162 | 258.3639
2373.6135 | 350.9181 | 253.1709 | 258.3535
2374.6135 | 350.8424 | 253.2237 | 258.3834
2375.6135 | 350.7446 | 253.2296 | 258.423
2376.6135 | 350.6187 | 253.2285 | 258.4415
2377.6135 | 350.6313 | 253.2269 | 258.4086
2378.6135 | 350.592 | 253.2303 | 258.3164
2379.6135 | 350.5604 | 253.2951 | 258.23
2380.6135 | 350.615 | 253.3441 | 258.2116
2381.6135 | 350.6043 | 253.3431 | 258.2104
2382.6135 | 350.5117 | 253.3825 | 258.2049
2383.6135 | 350.6584 | 253.4156 | 258.1449
2384.6135 | 350.5902 | 253.3986 | 258.0741
2385.6135 | 350.5132 | 253.4511 | 258.0059
2386.6135 | 350.6422 | 253.5007 | 257.9888
2387.6135 | 350.6439 | 253.517 | 257.9667
2388.6135 | 350.5953 | 253.4895 | 257.8768
2389.6135 | 350.4975 | 253.4806 | 257.7462
2390.6135 | 350.3528 | 253.4602 | 257.6391
2391.6135 | 350.4437 | 253.4314 | 257.531
2392.6135 | 350.5468 | 253.3901 | 257.4351
2393.6135 | 350.5325 | 253.3654 | 257.3952
2394.6135 | 350.6055 | 253.3372 | 257.3657
2395.6135 | 350.6248 | 253.3382 | 257.3433
2396.6135 | 350.5818 | 253.3163 | 257.3183
2397.6135 | 350.595 | 253.3433 | 257.2709
2398.6135 | 350.6089 | 253.3567 | 257.1981
2399.6135 | 350.5439 | 253.3594 | 257.1199
2400.6135 | 350.4515 | 253.3559 | 257.053
2401.6135 | 350.4757 | 253.3402 | 257.0611
2402.6135 | 350.2665 | 253.3297 | 257.053
2403.6135 | 350.2693 | 253.3402 | 257.0263
2404.6135 | 350.3326 | 253.3726 | 257.0348
2405.6135 | 350.4675 | 253.4155 | 257.0897
2406.6135 | 350.5476 | 253.4319 | 257.1244
2407.6135 | 350.5873 | 253.431 | 257.1202
2408.6135 | 350.4531 | 253.4635 | 257.1089
2409.6135 | 350.4096 | 253.5 | 257.1536
2410.6135 | 350.4194 | 253.5695 | 257.1793
2411.6135 | 350.3288 | 253.6555 | 257.2031
2412.6135 | 350.3441 | 253.7245 | 257.127
2413.6135 | 350.3788 | 253.8044 | 257.0099
2414.6135 | 350.4258 | 253.8443 | 256.9506
2415.6135 | 350.3871 | 253.8527 | 256.9635
2416.6135 | 350.5244 | 253.8723 | 256.9907
2417.6135 | 350.5245 | 253.8784 | 256.9886
2418.6135 | 350.4402 | 253.8466 | 257.0263
2419.6135 | 350.3978 | 253.8228 | 257.0453
2420.6135 | 350.4934 | 253.8172 | 257.0477
2421.6135 | 350.6236 | 253.8039 | 257.0504
2422.6135 | 350.618 | 253.8052 | 257.062
2423.6135 | 350.6956 | 253.7594 | 257.0404
2424.6135 | 350.7484 | 253.6946 | 257.0165
2425.6135 | 350.7096 | 253.6426 | 256.9763
2426.6135 | 350.7622 | 253.5624 | 256.9839
2427.6135 | 350.7768 | 253.5188 | 257.032
2428.6135 | 350.7207 | 253.4734 | 257.0882
2429.6135 | 350.5742 | 253.4533 | 257.1621
2430.6135 | 350.515 | 253.4174 | 257.2105
2431.6135 | 350.4435 | 253.3982 | 257.214
2432.6135 | 350.388 | 253.3734 | 257.2356
2433.6135 | 350.4137 | 253.3773 | 257.2983
2434.6135 | 350.4747 | 253.3859 | 257.3521
2435.6135 | 350.5879 | 253.3735 | 257.2782
2436.6135 | 350.7093 | 253.4352 | 257.3154
2437.6135 | 350.7574 | 253.4871 | 257.3607
2438.6135 | 350.6336 | 253.5189 | 257.4606
2439.6135 | 350.5927 | 253.5408 | 257.5568
2440.6135 | 350.5381 | 253.5867 | 257.5649
2441.6135 | 350.5082 | 253.6005 | 257.5296
2442.6135 | 350.4774 | 253.6028 | 257.4938
2443.6135 | 350.594 | 253.5918 | 257.4335
2444.6135 | 350.6782 | 253.553 | 257.4158
2445.6135 | 350.7628 | 253.5363 | 257.4
2446.6135 | 350.8238 | 253.5512 | 257.4345
2447.6135 | 350.8389 | 253.5655 | 257.4877
2448.6135 | 350.8335 | 253.5821 | 257.5379
2449.6135 | 350.9126 | 253.6333 | 257.5725
2450.6135 | 350.8628 | 253.66 | 257.6248
2451.6135 | 350.8062 | 253.6759 | 257.6825
2452.6135 | 350.8073 | 253.7287 | 257.7268
2453.6135 | 350.8819 | 253.7578 | 257.7594
2454.6135 | 350.9743 | 253.7674 | 257.8321
2455.6135 | 351.0459 | 253.7987 | 257.8535
2456.6135 | 350.968 | 253.8425 | 257.8411
2457.6448 | 350.8512 | 253.8631 | 257.8433
2458.6135 | 350.8109 | 253.8979 | 257.8621
2459.6135 | 350.7983 | 253.9317 | 257.8444
2460.6135 | 350.7555 | 253.9788 | 257.7993
2461.6135 | 350.7153 | 254.0148 | 257.7768
2462.6135 | 350.7794 | 254.0511 | 257.7029
2463.6135 | 350.6574 | 254.0652 | 257.6123
2464.6135 | 350.6734 | 254.0815 | 257.579
2465.6135 | 350.7475 | 254.095 | 257.5882
2466.6135 | 350.6395 | 254.1117 | 257.6524
2467.6135 | 350.6233 | 254.1373 | 257.7011
2468.6135 | 350.6229 | 254.1319 | 257.735
2469.6135 | 350.6702 | 254.0728 | 257.7651
2470.6135 | 350.6485 | 254.0346 | 257.8099
2471.6135 | 350.6399 | 254.0175 | 257.8557
2472.6135 | 350.7082 | 253.9691 | 257.886
2473.6135 | 350.691 | 253.8859 | 257.927
2474.6135 | 350.629 | 253.791 | 257.898
2475.6135 | 350.6812 | 253.6781 | 257.9111
2476.6135 | 350.7198 | 253.5987 | 257.9409
2477.6135 | 350.8327 | 253.5474 | 257.8891
2478.6135 | 350.8855 | 253.5488 | 257.9531
2479.6135 | 351.0382 | 253.6124 | 258.0465
2480.6135 | 351.2485 | 253.6862 | 258.0783
2481.6135 | 351.344 | 253.8051 | 258.0876
2482.6135 | 351.3027 | 253.8973 | 258.1194
2483.6135 | 351.2674 | 253.9688 | 258.1739
2484.6135 | 351.2094 | 253.9479 | 258.2483
2485.6135 | 351.2091 | 253.9425 | 258.2938
2486.6135 | 351.1455 | 253.9482 | 258.2733
2487.6135 | 351.0774 | 253.9756 | 258.2351
2488.6135 | 351.1154 | 253.9953 | 258.2102
2489.6135 | 351.1343 | 254.0152 | 258.1353
2490.6135 | 351.128 | 254.0442 | 258.0601
2491.6135 | 351.0272 | 254.089 | 257.9704
2492.6135 | 350.9763 | 254.1108 | 257.904
2493.6135 | 350.9019 | 254.1204 | 257.8516
2494.6135 | 350.7249 | 254.1296 | 257.8236
2495.6135 | 350.542 | 254.1025 | 257.804
2496.6135 | 350.4367 | 254.0911 | 257.8202
2497.6135 | 350.3641 | 254.0826 | 257.8501
2498.6135 | 350.3442 | 254.0401 | 257.8437
2499.6135 | 350.4224 | 254.0002 | 257.8082
2500.6135 | 350.5959 | 253.9452 | 257.798
2501.6135 | 350.5444 | 253.9579 | 257.8198
2502.6135 | 350.3819 | 253.9422 | 257.8617
2503.6135 | 350.298 | 253.9423 | 257.8987
2504.6135 | 350.1106 | 253.9173 | 257.9279
2505.6135 | 350.2035 | 253.97 | 257.8639
2506.6135 | 350.2503 | 254.0448 | 257.8194
2507.6135 | 350.0904 | 254.0747 | 257.7908
2508.6135 | 350.0764 | 254.0324 | 257.8028
2509.6135 | 350.0682 | 253.9887 | 257.8343
2510.6135 | 350.0396 | 253.9445 | 257.8478
2511.6135 | 350.058 | 253.9054 | 257.6957
2512.6135 | 350.0842 | 253.8702 | 257.7467
2513.6135 | 350.0477 | 253.8719 | 257.7351
2514.6135 | 350.0008 | 253.8791 | 257.7383
2515.6135 | 350.1104 | 253.8482 | 257.729
2516.6135 | 350.2283 | 253.7449 | 257.7605
2517.6135 | 350.2484 | 253.6886 | 257.8254
2518.6135 | 350.1857 | 253.6369 | 257.8512
2519.6135 | 350.2327 | 253.5362 | 257.8769
2520.6135 | 350.3027 | 253.451 | 257.9434
2521.6135 | 350.3677 | 253.4035 | 257.988
2522.6135 | 350.3835 | 253.3934 | 258.0154
2523.6135 | 350.5593 | 253.3902 | 258.0319
2524.6135 | 350.6173 | 253.3952 | 258.0831
2525.6135 | 350.5617 | 253.4206 | 258.1421
2526.6135 | 350.5438 | 253.4415 | 258.1555
2527.6135 | 350.5701 | 253.4582 | 258.0873
2528.6135 | 350.5815 | 253.4993 | 258.0236
2529.6135 | 350.8511 | 253.5604 | 258.0101
2530.6135 | 351.7619 | 253.6453 | 258.0111
2531.6135 | 353.4321 | 253.6998 | 258.0797
2532.6135 | 355.7985 | 253.7738 | 258.1562
2533.6135 | 358.621 | 253.8195 | 258.1604
2534.6135 | 361.6509 | 253.9179 | 258.3494
2535.6135 | 365.0543 | 254.0852 | 258.5381
2536.6135 | 368.4677 | 254.2798 | 258.7271
2537.6135 | 371.8494 | 254.4673 | 259.0345
2538.6135 | 375.0463 | 254.7108 | 259.2235
2539.6135 | 377.6865 | 254.9648 | 259.4756
2540.6135 | 380.0834 | 255.2429 | 259.7074
2541.6135 | 382.1054 | 255.5165 | 259.9244
2542.6135 | 383.7221 | 255.7862 | 260.1202
2543.6135 | 385.021 | 256.0494 | 260.3651
2544.6135 | 386.1354 | 256.309 | 260.621
2545.6135 | 387.0767 | 256.5774 | 260.8515
2546.6135 | 387.5859 | 256.8181 | 261.0617
2547.6135 | 388.0295 | 257.0334 | 261.2733
2548.6135 | 388.2491 | 257.2224 | 261.4576
2549.6135 | 388.3906 | 257.405 | 261.6646
2550.6135 | 388.2498 | 257.5757 | 261.8673
2551.6135 | 388.1991 | 257.7721 | 262.0656
2552.6135 | 388.1186 | 257.9361 | 262.2221
2553.6135 | 388.0437 | 258.096 | 262.4133
2554.6135 | 387.7317 | 258.2721 | 262.6354
2555.6135 | 387.3232 | 258.419 | 262.8357
2556.6135 | 386.8833 | 258.5578 | 262.9955
2557.6135 | 386.1592 | 258.7002 | 263.1524
2558.6135 | 385.4864 | 258.8294 | 263.2722
2559.6135 | 384.9193 | 258.9875 | 263.3652
2560.6135 | 384.4232 | 259.1026 | 263.405
2561.6135 | 383.8994 | 259.2113 | 263.4389
2562.6135 | 383.4146 | 259.2777 | 263.4816
2563.6135 | 382.79 | 259.4152 | 263.5734
2564.6135 | 382.0734 | 259.5018 | 263.6454
2565.6135 | 381.399 | 259.6037 | 263.7005
2566.6135 | 380.8707 | 259.703 | 263.6989
2567.6135 | 380.2474 | 259.7913 | 263.7744
2568.6135 | 379.6482 | 259.8578 | 263.8756
2569.6135 | 379.1188 | 259.9345 | 264.0387
2570.6135 | 378.5609 | 259.99 | 264.1742
2571.6135 | 377.9382 | 260.0001 | 264.314
2572.6135 | 377.3399 | 260.0027 | 264.4963
2573.6135 | 376.8552 | 260.0465 | 264.6389
2574.6135 | 376.2832 | 260.0986 | 264.7186
2575.6135 | 375.7865 | 260.161 | 264.7152
2576.6135 | 375.2165 | 260.2131 | 264.7707
2577.6135 | 374.6918 | 260.2805 | 264.7879
2578.6135 | 374.2448 | 260.329 | 264.8684
2579.6135 | 373.8157 | 260.3447 | 264.9519
2580.6135 | 373.5311 | 260.3447 | 265.0552
2581.6135 | 373.3307 | 260.3331 | 265.2277
2582.6135 | 373.1125 | 260.351 | 265.4045
2583.6135 | 372.9097 | 260.4314 | 265.4491
2584.6135 | 372.8563 | 260.4414 | 265.436
2585.6135 | 372.7582 | 260.4612 | 265.387
2586.6135 | 372.5134 | 260.5016 | 265.3092
2587.6135 | 372.322 | 260.541 | 265.3956
2588.6135 | 372.3123 | 260.6064 | 265.3819
2589.6135 | 372.3428 | 260.6737 | 265.4183
2590.6135 | 372.4052 | 260.7121 | 265.4123
2591.6135 | 372.4898 | 260.7889 | 265.4314
2592.6135 | 372.512 | 260.8228 | 265.5896
2593.6135 | 372.6473 | 260.819 | 265.7392
2594.6135 | 372.8114 | 260.8439 | 265.8299
2595.6135 | 372.9275 | 260.8745 | 265.9013
2596.6135 | 372.9117 | 260.9078 | 265.9723
2597.6135 | 372.9906 | 260.9517 | 265.9919
2598.6135 | 373.1593 | 260.9899 | 266.0211
2599.6135 | 373.3136 | 261.0515 | 265.9815
2600.6135 | 373.3985 | 261.1143 | 265.7476
2601.6135 | 373.5352 | 261.1751 | 265.7228
2602.6135 | 373.649 | 261.2236 | 265.7092
2603.6135 | 373.7925 | 261.3017 | 265.7964
2604.6135 | 373.9573 | 261.3831 | 265.8763
2605.6135 | 374.0713 | 261.4573 | 265.9715
2606.6135 | 374.0305 | 261.4757 | 266.0505
2607.6135 | 374.263 | 261.549 | 266.0717
2608.6135 | 374.3641 | 261.5807 | 266.2489
2609.6135 | 374.564 | 261.6346 | 266.4544
2610.6135 | 374.7228 | 261.6695 | 266.6455
2611.6135 | 374.8787 | 261.7199 | 266.8414
2612.6135 | 374.984 | 261.7682 | 267.0547
2613.6135 | 375.0899 | 261.8337 | 267.1529
2614.6135 | 375.1589 | 261.9251 | 267.3202
2615.6135 | 375.1875 | 261.9922 | 267.5143
2616.6135 | 375.3422 | 262.1049 | 267.5834
2617.6135 | 375.5419 | 262.1981 | 267.7144
2618.6135 | 375.565 | 262.2946 | 267.8288
2619.6135 | 375.4869 | 262.3774 | 268.0388
2620.6135 | 375.5161 | 262.4401 | 268.2266
2621.6135 | 375.431 | 262.4921 | 268.3681
2622.6135 | 375.4097 | 262.5996 | 268.4546
2623.6135 | 375.4551 | 262.7132 | 268.5134
2624.6135 | 375.3545 | 262.8141 | 268.5641
2625.6135 | 375.329 | 262.9201 | 268.6408
2626.6135 | 375.3072 | 263.0368 | 268.854
2627.6135 | 375.3663 | 263.1375 | 268.9121
2628.6135 | 375.4804 | 263.2049 | 268.9312
2629.6135 | 375.4506 | 263.2764 | 268.9173
2630.6135 | 375.5604 | 263.3579 | 268.9609
2631.6135 | 375.5869 | 263.3942 | 269.1205
2632.6135 | 375.501 | 263.511 | 269.2531
2633.6135 | 375.4608 | 263.5841 | 269.3109
2634.6135 | 375.4356 | 263.6729 | 269.3125
2635.6135 | 375.4224 | 263.7936 | 269.3796
2636.6135 | 375.3738 | 263.8571 | 269.3987
2637.6135 | 375.2759 | 263.9332 | 269.3305
2638.6135 | 375.2956 | 264.0245 | 269.2601
2639.6135 | 375.3634 | 264.1171 | 269.148
2640.6135 | 375.3173 | 264.1552 | 269.0999
2641.6135 | 375.2612 | 264.1942 | 269.0653
2642.6135 | 375.1881 | 264.2588 | 269.0586
2643.6135 | 375.1311 | 264.3354 | 269.1837
2644.6135 | 375.1068 | 264.3824 | 269.1866
2645.6135 | 375.0333 | 264.441 | 269.1986
2646.6135 | 375.0255 | 264.5104 | 269.1371
2647.6135 | 375.0425 | 264.5525 | 269.21
2648.6135 | 374.8945 | 264.5816 | 269.2682
2649.6135 | 374.8227 | 264.6484 | 269.3205
2650.6135 | 374.8182 | 264.6575 | 269.3866
2651.6135 | 374.8819 | 264.7171 | 269.5328
2652.6135 | 374.955 | 264.7512 | 269.5422
2653.6135 | 374.9202 | 264.8315 | 269.7477
2654.6135 | 374.7955 | 264.8496 | 269.923
2655.6135 | 374.6977 | 264.8931 | 269.8508
2656.6135 | 374.8377 | 264.9852 | 269.6792
2657.6135 | 374.949 | 265.0269 | 269.4563
2658.6135 | 375.1275 | 265.1102 | 269.5965
2659.6135 | 375.1048 | 265.1674 | 269.7536
2660.6135 | 375.2387 | 265.1946 | 269.9047
2661.6135 | 375.3642 | 265.1894 | 270.1021
2662.6135 | 375.5123 | 265.2107 | 270.3587
2663.6135 | 375.4849 | 265.2012 | 270.5843
2664.6135 | 375.4247 | 265.2326 | 270.6693
2665.6135 | 375.4833 | 265.2717 | 270.6944
2666.6135 | 375.4154 | 265.2945 | 270.7448
2667.6135 | 375.4929 | 265.3618 | 270.7941
2668.6135 | 375.5876 | 265.4397 | 270.7551
2669.6135 | 375.7083 | 265.488 | 270.7012
2670.6135 | 375.8598 | 265.554 | 270.7638
2671.6135 | 375.8927 | 265.6391 | 270.9915
2672.6135 | 375.9203 | 265.6753 | 271.1455
2673.6135 | 376.0626 | 265.695 | 271.4339
2674.6135 | 376.0994 | 265.7819 | 271.6062
2675.6135 | 376.0605 | 265.8339 | 271.7157
2676.6135 | 376.0139 | 265.8649 | 271.7613
2677.6135 | 375.9561 | 265.9032 | 271.852
2678.6135 | 376.0374 | 265.9266 | 271.9696
2679.6135 | 376.0574 | 265.9742 | 272.0159
2680.6135 | 375.9976 | 266.0127 | 272.0107
2681.6135 | 376.0176 | 266.094 | 272.0053
2682.6135 | 375.8381 | 266.1777 | 271.9978
2683.6135 | 375.6798 | 266.2321 | 272.0179
2684.6135 | 375.7359 | 266.2944 | 272.1802
2685.6135 | 375.8085 | 266.3315 | 272.2395
2686.6135 | 375.9193 | 266.3917 | 272.4317
2687.6135 | 375.8927 | 266.4581 | 272.6916
2688.6135 | 375.8025 | 266.502 | 272.901
2689.6135 | 375.7373 | 266.5515 | 273.1308
2690.6135 | 375.892 | 266.6148 | 273.3361
2691.6135 | 375.8671 | 266.6764 | 273.4642
2692.6135 | 375.8637 | 266.7467 | 273.6976
2693.6135 | 375.9091 | 266.7901 | 273.9157
2694.6135 | 375.9223 | 266.8029 | 274.1206
2695.6135 | 376.002 | 266.8188 | 274.3964
2696.6135 | 375.8837 | 266.805 | 274.5324
2697.6135 | 375.7189 | 266.7841 | 274.6214
2698.6135 | 375.6071 | 266.7594 | 274.662
2699.6135 | 375.5486 | 266.7617 | 274.7699
2700.6135 | 375.4464 | 266.7668 | 274.9117
2701.6135 | 375.4265 | 266.8041 | 275.0728
2702.6135 | 375.3017 | 266.8232 | 275.0768
2703.6135 | 375.1925 | 266.8423 | 275.0478
2704.6135 | 375.1949 | 266.8542 | 274.9983
2705.6135 | 375.2182 | 266.8793 | 274.9509
2706.6135 | 375.1853 | 266.9455 | 274.8898
2707.6135 | 375.1467 | 266.9981 | 274.8347
2708.6135 | 375.1719 | 267.0381 | 274.8038
2709.6135 | 375.2805 | 267.0972 | 274.7838
2710.6135 | 375.3609 | 267.1577 | 274.8204
2711.6135 | 375.3722 | 267.2283 | 274.8084
2712.6135 | 375.5446 | 267.2868 | 274.7283
2713.6135 | 375.6412 | 267.3635 | 274.6897
2714.6135 | 375.6359 | 267.4507 | 274.5935
2715.6135 | 375.6383 | 267.5436 | 274.4224
2716.6135 | 375.6108 | 267.6264 | 274.2238
2717.6135 | 375.6664 | 267.7501 | 273.9536
2718.6135 | 375.7889 | 267.8596 | 273.7701
2719.6135 | 375.8426 | 267.9645 | 273.8326
2720.6135 | 375.7651 | 268.0574 | 273.9591
2721.6135 | 375.773 | 268.1206 | 273.9997
2722.6135 | 375.8529 | 268.177 | 274.1963
2723.6135 | 375.9416 | 268.2267 | 274.436
2724.6135 | 376.053 | 268.2994 | 274.626
2725.6135 | 376.0288 | 268.3753 | 274.7572
2726.6135 | 375.9469 | 268.4349 | 274.8175
2727.6135 | 375.8508 | 268.463 | 274.8846
2728.6135 | 375.7741 | 268.4943 | 274.9913
2729.6135 | 375.8675 | 268.5201 | 275.0968
2730.6135 | 375.7285 | 268.5439 | 275.2427
2731.6135 | 375.7075 | 268.553 | 275.242
2732.6135 | 375.5886 | 268.5782 | 275.1249
2733.6135 | 375.4803 | 268.6307 | 274.9412
2734.6135 | 375.5113 | 268.7014 | 274.8315
2735.6135 | 375.4713 | 268.7795 | 274.8266
2736.6135 | 375.4515 | 268.8701 | 274.8056
2737.6135 | 375.4844 | 268.9689 | 274.767
2738.6135 | 375.5482 | 269.062 | 274.7393
2739.6135 | 375.459 | 269.1325 | 274.7898
2740.6135 | 375.4764 | 269.2082 | 274.8852
2741.6135 | 375.4073 | 269.2893 | 274.9657
2742.6135 | 375.3705 | 269.3716 | 275.0947
2743.6135 | 375.3936 | 269.4456 | 275.3473
2744.6135 | 375.4062 | 269.514 | 275.5149
2745.6135 | 375.4649 | 269.5396 | 275.6585
2746.6135 | 375.4808 | 269.5934 | 275.7894
2747.6135 | 375.5156 | 269.6296 | 275.8524
2748.6135 | 375.4902 | 269.6653 | 275.9783
2749.6135 | 375.524 | 269.6954 | 275.9452
2750.6135 | 375.699 | 269.7306 | 275.979
2751.6135 | 375.9125 | 269.7695 | 276.0699
2752.6135 | 376.0259 | 269.8123 | 276.2739
2753.6135 | 375.9997 | 269.8836 | 276.5
2754.6135 | 375.9383 | 269.9637 | 276.7076
2755.6135 | 375.9393 | 270.056 | 276.8688
2756.6135 | 376.008 | 270.1275 | 276.9552
2757.6135 | 376.0228 | 270.1554 | 276.9225
2758.6135 | 376.0847 | 270.1771 | 276.7551
2759.6135 | 376.1039 | 270.2038 | 276.843
2760.6135 | 376.1997 | 270.2572 | 277.1001
2761.6135 | 376.2315 | 270.3146 | 277.1864
2762.6135 | 376.2181 | 270.3549 | 277.1444
2763.6135 | 376.1885 | 270.4283 | 277.0695
2764.6135 | 376.2307 | 270.4341 | 277.0796
2765.6135 | 376.2375 | 270.474 | 277.1157
2766.6135 | 376.2626 | 270.5099 | 277.1701
2767.6135 | 376.2995 | 270.5864 | 277.1327
2768.6135 | 376.3141 | 270.6727 | 277.1294
2769.6135 | 376.3802 | 270.7529 | 277.1624
2770.6135 | 376.3956 | 270.8217 | 277.2974
2771.6135 | 376.2778 | 270.8351 | 277.4648
2772.6135 | 376.1804 | 270.8849 | 277.6411
2773.6135 | 376.2017 | 270.9115 | 277.6903
2774.6135 | 376.2696 | 270.9299 | 277.5786
2775.6135 | 376.3714 | 270.9789 | 277.3787
2776.6135 | 376.3567 | 270.9977 | 277.3462
2777.6135 | 376.4744 | 271.007 | 277.4225
2778.6135 | 376.4919 | 271.0432 | 277.4982
2779.6135 | 376.3574 | 271.0791 | 277.4536
2780.6135 | 376.2213 | 271.1481 | 277.4088
2781.6135 | 376.2041 | 271.1775 | 277.5397
2782.6135 | 376.2369 | 271.256 | 277.7323
2783.6135 | 376.121 | 271.323 | 277.9463
2784.6135 | 376.0918 | 271.395 | 278.2338
2785.6135 | 376.0131 | 271.4698 | 278.3858
2786.6135 | 375.9802 | 271.5323 | 278.514
2787.6135 | 375.889 | 271.5801 | 278.5384
2788.6135 | 375.8181 | 271.6518 | 278.6668
2789.6135 | 375.8486 | 271.744 | 278.7802
2790.6135 | 375.8115 | 271.8106 | 278.8837
2791.6135 | 375.8389 | 271.8747 | 278.9324
2792.6135 | 375.8437 | 271.9459 | 279.0068
2793.6135 | 375.8215 | 271.9634 | 279.0134
2794.6135 | 375.7675 | 272.0249 | 278.9121
2795.6135 | 375.7035 | 272.0501 | 278.806
2796.6135 | 375.5577 | 272.0997 | 278.6617
2797.6135 | 375.6897 | 272.1481 | 278.6295
2798.6135 | 375.5995 | 272.203 | 278.5788
2799.6135 | 375.6696 | 272.2341 | 278.5283
2800.6135 | 375.7605 | 272.2781 | 278.486
2801.6135 | 375.8685 | 272.3226 | 278.6118
2802.6135 | 375.9827 | 272.4135 | 278.5406
2803.6135 | 375.9723 | 272.4831 | 278.4554
2804.6135 | 375.8229 | 272.5446 | 278.5541
2805.6135 | 375.712 | 272.6001 | 278.6864
2806.6135 | 375.7033 | 272.6715 | 278.7612
2807.6135 | 375.8181 | 272.7493 | 278.7505
2808.6135 | 375.7699 | 272.8387 | 278.5141
2809.6135 | 375.7053 | 272.922 | 278.3811
2810.6135 | 375.5534 | 273.0067 | 278.2705
2811.6135 | 375.4624 | 273.0978 | 278.2397
2812.6135 | 375.5976 | 273.1938 | 278.1002
2813.6135 | 375.6503 | 273.34 | 277.9542
2814.6135 | 375.6436 | 273.4853 | 277.7599
2815.6135 | 375.5499 | 273.6189 | 277.6869
2816.6135 | 375.5656 | 273.6689 | 277.7735
2817.6135 | 375.5243 | 273.721 | 277.9178
2818.6135 | 375.328 | 273.7412 | 278.0919
2819.6135 | 375.3219 | 273.7676 | 278.1619
2820.6135 | 375.2318 | 273.7993 | 278.3399
2821.6135 | 375.1809 | 273.8352 | 278.4593
2822.6135 | 375.0767 | 273.8793 | 278.4499
2823.6135 | 375.0546 | 273.9227 | 278.4919
2824.6135 | 374.9973 | 273.9673 | 278.5394
2825.6135 | 374.9379 | 274.0023 | 278.6773
2826.6135 | 374.9943 | 274.0732 | 278.8399
2827.6135 | 374.9012 | 274.1253 | 278.893
2828.6135 | 374.9191 | 274.1718 | 278.9423
2829.6135 | 374.9668 | 274.2377 | 278.9684
2830.6135 | 374.8731 | 274.2419 | 279.0455
2831.6135 | 374.8577 | 274.2385 | 279.2776
2832.6135 | 374.7038 | 274.2586 | 279.3461
2833.6135 | 374.6326 | 274.281 | 279.2596
2834.6135 | 374.4635 | 274.3043 | 279.2149
2835.6135 | 374.3404 | 274.3275 | 279.0946
2836.6135 | 374.281 | 274.3876 | 279.0643
2837.6135 | 374.3813 | 274.4579 | 278.8371
2838.6135 | 374.4221 | 274.5219 | 278.6224
2839.6135 | 374.3374 | 274.6084 | 278.4017
2840.6135 | 374.3763 | 274.6569 | 278.2447
2841.6135 | 374.6527 | 274.7207 | 278.0838
2842.6135 | 374.816 | 274.7524 | 277.9437
2843.6135 | 374.6626 | 274.8068 | 277.8213
2844.6135 | 374.7348 | 274.8278 | 277.7853
2845.6135 | 374.994 | 274.8519 | 277.7945
2846.6135 | 375.1263 | 274.8408 | 278.0083
2847.6135 | 375.2316 | 274.8364 | 278.2946
2848.6135 | 375.2638 | 274.8249 | 278.5351
2849.6135 | 375.2879 | 274.8196 | 278.6817
2850.6135 | 375.4449 | 274.8194 | 278.8517
2851.6135 | 375.4624 | 274.8287 | 279.0708
2852.6135 | 375.4369 | 274.8655 | 279.2628
2853.6135 | 375.3334 | 274.8782 | 279.4599
2854.6135 | 375.2839 | 274.8741 | 279.6178
2855.6135 | 375.2492 | 274.8897 | 279.7277
2856.6135 | 375.2669 | 274.8756 | 279.7814
2857.6135 | 375.3122 | 274.9055 | 279.8287
2858.6135 | 375.4155 | 274.9069 | 280.0522
2859.6135 | 375.4321 | 274.8906 | 280.2215
2860.6135 | 375.575 | 274.8994 | 280.3058
2861.6135 | 375.6145 | 274.903 | 280.4129
2862.6135 | 375.541 | 274.9196 | 280.6412
2863.6135 | 375.4872 | 274.93 | 280.7609
2864.6135 | 375.5712 | 274.9465 | 280.8098
2865.6135 | 375.5343 | 274.9687 | 280.8106
2866.6135 | 375.5282 | 274.9724 | 280.9305
2867.6135 | 375.4714 | 275.0081 | 281.028
2868.6135 | 375.4372 | 275.0345 | 281.0817
2869.6135 | 375.3075 | 275.0515 | 281.1289
2870.6135 | 375.1996 | 275.0769 | 281.1883
2871.6135 | 375.2058 | 275.0801 | 281.264
2872.6135 | 375.1953 | 275.1279 | 281.242
2873.6135 | 375.2666 | 275.1435 | 281.2469
2874.6135 | 375.2657 | 275.1701 | 281.3843
2875.6135 | 375.2358 | 275.2078 | 281.4673
2876.6135 | 375.2107 | 275.2248 | 281.5526
2877.6135 | 375.274 | 275.2426 | 281.7303
2878.6135 | 375.3416 | 275.2577 | 281.828
2879.6135 | 375.2283 | 275.3094 | 281.8323
2880.6135 | 375.3112 | 275.3419 | 281.9358
2881.6135 | 375.3237 | 275.3973 | 281.9847
2882.6135 | 375.2524 | 275.4422 | 281.958
2883.6135 | 375.2601 | 275.4976 | 282.0253
2884.6135 | 375.3096 | 275.5381 | 282.1133
2885.6135 | 375.3864 | 275.6106 | 281.9896
2886.6135 | 375.4574 | 275.6944 | 281.7563
2887.6135 | 375.5212 | 275.7462 | 281.7072
2888.6135 | 375.4916 | 275.7742 | 281.797
2889.6135 | 375.4371 | 275.8284 | 281.9354
2890.6135 | 375.3554 | 275.8526 | 281.946
2891.6135 | 375.1813 | 275.8738 | 281.8732
2892.6135 | 375.2175 | 275.9164 | 281.7409
2893.6135 | 375.2769 | 275.9725 | 281.5629
2894.6135 | 375.2669 | 276.0441 | 281.312
2895.6135 | 375.299 | 276.1093 | 281.0203
2896.6135 | 375.3186 | 276.1912 | 280.9036
2897.6135 | 375.3337 | 276.2677 | 280.9399
2898.6135 | 375.3809 | 276.3056 | 281.0405
2899.6135 | 375.5378 | 276.3245 | 281.2228
2900.6135 | 375.7098 | 276.3197 | 281.3739
2901.6135 | 375.7637 | 276.3386 | 281.4907
2902.6135 | 375.8587 | 276.3629 | 281.6723
2903.6135 | 375.8287 | 276.3951 | 281.7326
2904.6135 | 375.7464 | 276.4628 | 281.7847
2905.6135 | 375.7554 | 276.5079 | 281.7669
2906.6135 | 375.8747 | 276.5978 | 281.6364
2907.6135 | 375.8699 | 276.6652 | 281.6748
2908.6135 | 375.8617 | 276.7491 | 281.7467
2909.6135 | 375.9954 | 276.7876 | 281.7574
2910.6135 | 376.0116 | 276.8509 | 281.7705
2911.6135 | 376.0035 | 276.8913 | 281.539
2912.6135 | 376.102 | 276.9464 | 281.2771
2913.6135 | 376.2047 | 276.9972 | 281.2217
2914.6135 | 376.1149 | 277.0494 | 281.3449
2915.6135 | 376.0476 | 277.1098 | 281.5064
2916.6135 | 375.99 | 277.146 | 281.753
2917.6135 | 375.9714 | 277.1873 | 281.9871
2918.6135 | 375.9816 | 277.2204 | 281.9981
2919.6135 | 375.9151 | 277.2801 | 281.9349
2920.6135 | 375.8455 | 277.2982 | 281.9025
2921.6135 | 375.7598 | 277.3215 | 281.9648
2922.6135 | 375.7717 | 277.3591 | 282.0343
2923.6135 | 375.8495 | 277.3884 | 281.9012
2924.6135 | 375.9041 | 277.3985 | 281.6885
2925.6135 | 375.9499 | 277.4188 | 281.6209
2926.6135 | 375.9441 | 277.4051 | 281.7045
2927.6135 | 376.0894 | 277.3857 | 281.733
2928.6135 | 376.0094 | 277.3299 | 281.8445
2929.6135 | 376.0103 | 277.2636 | 281.9327
2930.6135 | 376.0375 | 277.2356 | 282.0135
2931.6135 | 375.9485 | 277.1829 | 282.0987
2932.6135 | 375.9304 | 277.1523 | 282.1515
2933.6135 | 375.9993 | 277.1345 | 282.2897
2934.6135 | 376.1009 | 277.1487 | 282.4494
2935.6135 | 376.1343 | 277.1966 | 282.578
2936.6135 | 376.2884 | 277.2342 | 282.564
2937.6135 | 376.4102 | 277.2495 | 282.6056
2938.6135 | 376.3465 | 277.2766 | 282.5747
2939.6135 | 376.3232 | 277.3237 | 282.4948
2940.6135 | 376.2666 | 277.364 | 282.4727
2941.6135 | 376.1969 | 277.409 | 282.3891
2942.6135 | 376.1467 | 277.4726 | 282.2569
2943.6135 | 376.1471 | 277.5254 | 282.2325
2944.6135 | 376.0919 | 277.5751 | 282.0367
2945.6135 | 376.0319 | 277.6044 | 281.835
2946.6135 | 376.0727 | 277.629 | 281.8167
2947.6135 | 376.0306 | 277.7106 | 281.963
2948.6135 | 375.981 | 277.7663 | 282.0987
2949.6135 | 376.0035 | 277.8282 | 282.1688
2950.6135 | 375.9603 | 277.8797 | 282.1307
2951.6135 | 375.8425 | 277.9603 | 282.154
2952.6135 | 375.7765 | 278.0068 | 282.0819
2953.6135 | 375.7808 | 278.0509 | 282.0077
2954.6135 | 375.7885 | 278.0528 | 282.1394
2955.6135 | 375.7875 | 277.9942 | 282.2867
2956.6135 | 375.8432 | 277.9695 | 282.4021
2957.6135 | 375.7888 | 277.9525 | 282.5239
2958.6135 | 375.7509 | 277.956 | 282.5327
2959.6135 | 375.6895 | 277.9669 | 282.5744
2960.6135 | 375.737 | 277.9801 | 282.5943
2961.6135 | 375.7671 | 277.9944 | 282.5444
2962.6135 | 375.7024 | 277.9929 | 282.4354
2963.6135 | 375.6176 | 278.0226 | 282.3856
2964.6135 | 375.6311 | 278.0346 | 282.2603
2965.6135 | 375.6422 | 278.0508 | 282.1811
2966.6135 | 375.6298 | 278.0436 | 282.1833
2967.6135 | 375.6269 | 278.0209 | 282.3283
2968.6135 | 375.7736 | 277.9888 | 282.5204
2969.6135 | 375.8296 | 277.924 | 282.6336
2970.6135 | 375.9217 | 277.8889 | 282.7116
2971.6135 | 375.8937 | 277.8918 | 282.8447
2972.6135 | 375.8492 | 277.8721 | 283.1125
2973.6135 | 375.7225 | 277.8631 | 283.3813
2974.6135 | 375.6354 | 277.8317 | 283.4946
2975.6135 | 375.5574 | 277.8178 | 283.6399
2976.6135 | 375.5144 | 277.8121 | 283.6464
2977.6135 | 375.4586 | 277.8088 | 283.7158
2978.6135 | 375.4999 | 277.8063 | 283.6672
2979.6135 | 375.4735 | 277.7937 | 283.6184
2980.6135 | 375.3012 | 277.8122 | 283.5795
2981.6135 | 375.2703 | 277.8407 | 283.7914
2982.6135 | 375.2384 | 277.8777 | 283.8632
2983.6135 | 375.2074 | 277.9105 | 283.8584
2984.6135 | 375.1607 | 277.9572 | 283.8461
2985.6135 | 375.0897 | 278.0253 | 283.7692
2986.6135 | 375.0218 | 278.0736 | 283.8237
2987.6135 | 374.9244 | 278.09 | 283.9455
2988.6135 | 374.768 | 278.1298 | 283.9709
2989.6135 | 374.8835 | 278.1598 | 283.8706
2990.6135 | 374.9259 | 278.1576 | 283.7123
2991.6135 | 374.9666 | 278.1462 | 283.4304
2992.6135 | 374.8377 | 278.1523 | 283.2466
2993.6135 | 374.8626 | 278.1383 | 283.299
2994.6135 | 374.9217 | 278.1145 | 283.351
2995.6135 | 374.9595 | 278.0951 | 283.385
2996.6135 | 374.7194 | 278.1021 | 283.5433
2997.6135 | 374.5504 | 278.1199 | 283.4808
2998.6135 | 374.5309 | 278.1761 | 283.4451
2999.6135 | 374.5959 | 278.2194 | 283.4789
3000.6135 | 374.5589 | 278.2547 | 283.5931
3001.6135 | 374.4849 | 278.283 | 283.6611
3002.6135 | 374.4903 | 278.3291 | 283.6712
3003.6135 | 374.4837 | 278.3761 | 283.5979
3004.6135 | 374.4472 | 278.4148 | 283.5384
3005.6135 | 374.4548 | 278.4462 | 283.3206
3006.6135 | 374.5169 | 278.4509 | 283.239
3007.6135 | 374.5141 | 278.4278 | 283.1421
3008.6135 | 374.7329 | 278.404 | 283.1059
3009.6135 | 374.8731 | 278.4055 | 283.1907
3010.6135 | 374.9789 | 278.403 | 283.1655
3011.6135 | 374.9222 | 278.4214 | 283.188
3012.6135 | 374.9767 | 278.4441 | 283.3065
3013.6135 | 375.0424 | 278.4659 | 283.4206
3014.6135 | 375.0454 | 278.4783 | 283.395
3015.6135 | 375.0566 | 278.5144 | 283.3565
3016.6135 | 375.1487 | 278.5266 | 283.3314
3017.6135 | 375.1259 | 278.5225 | 283.1323
3018.6135 | 375.1142 | 278.5103 | 283.0965
3019.6135 | 375.2207 | 278.471 | 283.1378
3020.6135 | 375.3724 | 278.4265 | 282.9826
3021.6135 | 375.4949 | 278.4162 | 282.9894
3022.6135 | 375.5052 | 278.4063 | 282.8472
3023.6135 | 375.4982 | 278.4237 | 282.8076
3024.6135 | 375.5926 | 278.4451 | 282.8713
3025.6135 | 375.6182 | 278.4706 | 282.8629
3026.6135 | 375.7032 | 278.5189 | 282.6018
3027.6135 | 375.8244 | 278.5701 | 282.4182
3028.6135 | 375.8817 | 278.6364 | 282.3658
3029.6135 | 375.856 | 278.7021 | 282.3881
3030.6135 | 375.8675 | 278.7463 | 282.3809
3031.6135 | 375.8725 | 278.7917 | 282.4112
3032.6135 | 375.694 | 278.8376 | 282.6609
3033.6135 | 375.6366 | 278.8907 | 282.7706
3034.6135 | 375.6746 | 278.929 | 282.6741
3035.6135 | 375.767 | 278.953 | 282.541
3036.6135 | 375.7128 | 278.998 | 282.2284
3037.6135 | 375.6431 | 279.042 | 282.1704
3038.6135 | 375.777 | 279.0978 | 282.1776
3039.6135 | 375.7751 | 279.1212 | 282.2181
3040.6135 | 375.8032 | 279.1613 | 282.322
3041.6135 | 375.6774 | 279.1791 | 282.3771
3042.6135 | 375.5675 | 279.1861 | 282.3623
3043.6135 | 375.6738 | 279.1852 | 282.4818
3044.6135 | 375.7683 | 279.1617 | 282.5896
3045.6135 | 375.6738 | 279.1145 | 282.6976
3046.6135 | 375.5489 | 279.0836 | 282.8864
3047.6135 | 375.4451 | 279.0851 | 283.2464
3048.6135 | 375.2947 | 279.1055 | 283.6257
3049.6135 | 375.2445 | 279.0914 | 283.9096
3050.6135 | 375.2605 | 279.0601 | 284.1982
3051.6135 | 375.1249 | 279.0262 | 284.2678
3052.6135 | 375.0396 | 279.0054 | 284.2327
3053.6135 | 375.064 | 278.974 | 284.2913
3054.6135 | 375.2355 | 278.9668 | 284.2002
3055.6135 | 375.2847 | 278.9698 | 284.1511
3056.6135 | 375.2832 | 279.0056 | 283.9843
3057.6135 | 375.3274 | 279.0713 | 283.8741
3058.6135 | 375.3171 | 279.11 | 283.9025
3059.6135 | 375.253 | 279.1338 | 284.0223
3060.6135 | 375.1407 | 279.1234 | 284.2253
3061.6135 | 375.0706 | 279.1048 | 284.4688
3062.6135 | 374.9995 | 279.1026 | 284.4715
3063.6135 | 374.9361 | 279.1065 | 284.452
3064.6135 | 375.0073 | 279.1437 | 284.3256
3065.6135 | 375.0855 | 279.1892 | 284.1883
3066.6135 | 375.1769 | 279.2164 | 284.2229
3067.6135 | 375.1796 | 279.2062 | 284.0892
3068.6135 | 375.1917 | 279.255 | 283.8319
3069.6135 | 375.2436 | 279.2899 | 283.6484
3070.6135 | 375.1573 | 279.3516 | 283.5243
3071.6135 | 375.176 | 279.4216 | 283.5398
3072.6135 | 375.269 | 279.487 | 283.6277
3073.6135 | 375.3025 | 279.5324 | 283.6791
3074.6135 | 375.1843 | 279.5866 | 283.8153
3075.6135 | 375.2188 | 279.61 | 283.8038
3076.6135 | 375.321 | 279.6246 | 283.6136
3077.6135 | 375.3686 | 279.6845 | 283.4638
3078.6135 | 375.3773 | 279.7383 | 283.2526
3079.6135 | 375.3361 | 279.7738 | 282.9554
3080.6135 | 375.2347 | 279.8278 | 282.913
3081.6135 | 375.3416 | 279.8375 | 282.9283
3082.6135 | 375.4002 | 279.8563 | 282.8487
3083.6135 | 375.3744 | 279.865 | 282.6624
3084.6135 | 375.266 | 279.888 | 282.6157
3085.6135 | 375.1502 | 279.9017 | 282.587
3086.6135 | 375.2322 | 279.911 | 282.509
3087.6135 | 375.2649 | 279.9143 | 282.3882
3088.6135 | 375.3263 | 279.9343 | 282.3812
3089.6135 | 375.2949 | 279.956 | 282.3573
3090.6135 | 375.2924 | 279.9854 | 282.2614
3091.6135 | 375.2608 | 279.9857 | 282.2134
3092.6135 | 375.3731 | 279.9628 | 282.196
3093.6135 | 375.3558 | 279.9267 | 282.0255
3094.6135 | 375.375 | 279.9355 | 281.9884
3095.6135 | 375.5037 | 279.9612 | 282.0486
3096.6135 | 375.5929 | 279.9793 | 282.2322
3097.6135 | 375.9167 | 280.0402 | 282.5509
3098.6135 | 376.8967 | 280.0802 | 282.9109
3099.6135 | 378.6003 | 280.119 | 283.2516
3100.6135 | 380.9992 | 280.1881 | 283.4171
3101.6135 | 383.6791 | 280.2663 | 283.4999
3102.6135 | 386.7359 | 280.3637 | 283.8418
3103.6135 | 390.1268 | 280.4813 | 284.4346
3104.6135 | 393.5775 | 280.623 | 285.1197
3105.6135 | 396.8144 | 280.81 | 285.724
3106.6135 | 399.8767 | 281.0122 | 286.2501
3107.6135 | 402.4533 | 281.2224 | 286.782
3108.6135 | 404.8245 | 281.4191 | 287.2907
3109.6135 | 406.7969 | 281.6054 | 287.8231
3110.6135 | 408.5424 | 281.8432 | 288.5359
3111.6135 | 410.0447 | 282.0818 | 289.3223
3112.6135 | 411.0193 | 282.3547 | 289.9934
3113.6135 | 411.8217 | 282.5921 | 290.6075
3114.6135 | 412.329 | 282.8686 | 291.3513
3115.6135 | 412.7093 | 283.097 | 291.9792
3116.6135 | 412.917 | 283.3196 | 292.5404
3117.6135 | 412.9275 | 283.5137 | 292.9767
3118.6135 | 412.7952 | 283.7134 | 293.4863
3119.6135 | 412.5036 | 283.9011 | 293.9954
3120.6135 | 412.1696 | 284.0679 | 294.4741
3121.6135 | 411.7939 | 284.2483 | 294.9076
3122.6135 | 411.4072 | 284.4335 | 295.2511
3123.6135 | 410.9842 | 284.6153 | 295.5619
3124.6135 | 410.4354 | 284.7843 | 295.7579
3125.6135 | 409.8223 | 284.9198 | 295.8851
3126.6135 | 409.3095 | 285.0748 | 295.9413
3127.6135 | 408.7773 | 285.2367 | 295.9747
3128.6135 | 408.0658 | 285.4099 | 296.0307
3129.6135 | 407.2958 | 285.5778 | 296.1837
3130.6135 | 406.6014 | 285.7504 | 296.2511
3131.6135 | 405.7162 | 285.9362 | 296.1454
3132.6135 | 405.0975 | 286.0958 | 296.1748
3133.6135 | 404.4502 | 286.2539 | 296.2066
3134.6135 | 403.887 | 286.413 | 296.2082
3135.6135 | 403.287 | 286.5523 | 296.1378
3136.6135 | 402.7507 | 286.6591 | 295.9531
3137.6135 | 402.1934 | 286.7673 | 295.8138
3138.6135 | 401.7496 | 286.8314 | 295.8195
3139.6135 | 401.3121 | 286.8921 | 295.8754
3140.6135 | 400.8445 | 286.9392 | 295.9185
3141.6135 | 400.4064 | 287.033 | 296.0315
3142.6135 | 399.9594 | 287.1293 | 296.2268
3143.6135 | 399.5599 | 287.2054 | 296.3377
3144.6135 | 399.1546 | 287.2916 | 296.2725
3145.6135 | 398.9726 | 287.3987 | 296.2594
3146.6135 | 398.7698 | 287.5282 | 296.2456
3147.6135 | 398.6188 | 287.619 | 296.444
3148.6135 | 398.4337 | 287.7216 | 296.5923
3149.6135 | 398.252 | 287.857 | 296.5765
3150.6135 | 398.2971 | 287.9826 | 296.395
3151.6135 | 398.2355 | 288.0839 | 296.227
3152.6135 | 398.0244 | 288.1718 | 296.0963
3153.6135 | 398.0253 | 288.2347 | 296.2217
3154.6135 | 398.1567 | 288.259 | 296.3289
3155.6135 | 398.1437 | 288.3002 | 296.463
3156.6135 | 398.1168 | 288.3641 | 296.5359
3157.6135 | 398.0066 | 288.3995 | 296.6166
3158.6135 | 398.1917 | 288.4657 | 296.6138
3159.6135 | 398.2267 | 288.5457 | 296.72
3160.6135 | 398.1214 | 288.6273 | 296.7609
3161.6135 | 398.2029 | 288.7065 | 296.8608
3162.6135 | 398.292 | 288.7914 | 297.0098
3163.6135 | 398.4766 | 288.8805 | 297.2303
3164.6135 | 398.7254 | 288.9803 | 297.4795
3165.6135 | 398.8762 | 289.0667 | 297.582
3166.6135 | 398.928 | 289.1922 | 297.6747
3167.6135 | 399.2586 | 289.3393 | 297.6053
3168.6135 | 399.4904 | 289.4568 | 297.5956
3169.6135 | 399.4579 | 289.5607 | 297.6905
3170.6135 | 399.4993 | 289.6423 | 297.7344
3171.6135 | 399.5843 | 289.7626 | 297.7406
3172.6135 | 399.7366 | 289.8641 | 297.8061
3173.6135 | 399.8764 | 289.9693 | 297.6912
3174.6135 | 399.9509 | 290.0914 | 297.4613
3175.6135 | 400 | 290.2327 | 297.4834
3176.6135 | 400.0755 | 290.3573 | 297.6504
3177.6135 | 400.1104 | 290.4552 | 297.701
3178.6135 | 400.0966 | 290.5674 | 297.6548
3179.6135 | 400.1809 | 290.679 | 297.3679
3180.6135 | 400.3697 | 290.7611 | 297.3114
3181.6135 | 400.4318 | 290.866 | 297.5471
3182.6135 | 400.4474 | 290.9774 | 297.6988
3183.6135 | 400.5157 | 291.0809 | 297.7618
3184.6135 | 400.4939 | 291.1396 | 297.6137
3185.6135 | 400.5433 | 291.1906 | 297.6445
3186.6135 | 400.5405 | 291.231 | 297.756
3187.6135 | 400.4653 | 291.291 | 297.884
3188.6135 | 400.3199 | 291.3191 | 297.9033
3189.6135 | 400.2969 | 291.3407 | 297.791
3190.6135 | 400.3981 | 291.4119 | 297.666
3191.6135 | 400.2548 | 291.4904 | 297.4999
3192.6135 | 400.2378 | 291.5347 | 297.4314
3193.6135 | 400.1436 | 291.6169 | 297.389
3194.6135 | 400.142 | 291.6962 | 297.2768
3195.6135 | 400.1697 | 291.7924 | 297.1794
3196.6135 | 400.2248 | 291.875 | 297.0108
3197.6135 | 400.2157 | 291.9754 | 297.1841
3198.6135 | 400.1513 | 292.0274 | 297.3742
3199.6135 | 400.2344 | 292.0799 | 297.5909
3200.6135 | 400.1689 | 292.1639 | 297.871
3201.6135 | 400.1959 | 292.2244 | 298.1116
3202.6135 | 400.2585 | 292.3041 | 298.2722
3203.6135 | 400.303 | 292.3916 | 298.3089
3204.6135 | 400.4034 | 292.4579 | 298.2623
3205.6135 | 400.3804 | 292.5481 | 298.1019
3206.6135 | 400.2691 | 292.6281 | 298.0837
3207.6135 | 400.1964 | 292.7161 | 298.0346
3208.6135 | 400.2956 | 292.7835 | 298.2838
3209.6135 | 400.3826 | 292.7963 | 298.6346
3210.6135 | 400.3462 | 292.8284 | 298.9962
3211.6135 | 400.3196 | 292.9006 | 299.0227
3212.6135 | 400.3357 | 292.9921 | 298.9918
3213.6135 | 400.2965 | 293.0844 | 298.9797
3214.6135 | 400.2212 | 293.1614 | 299.0325
3215.6135 | 400.2116 | 293.2685 | 298.9988
3216.6135 | 400.2839 | 293.3846 | 299.0329
3217.6135 | 400.3699 | 293.5045 | 299.1635
3218.6135 | 400.4362 | 293.6633 | 299.3033
3219.6135 | 400.4307 | 293.8002 | 299.5131
3220.6135 | 400.3482 | 293.9446 | 299.6329
3221.6135 | 400.2333 | 294.0571 | 299.7144
3222.6135 | 400.2288 | 294.1641 | 299.6347
3223.6135 | 400.2476 | 294.2593 | 299.48
3224.6135 | 400.2434 | 294.3167 | 299.4285
3225.6135 | 400.211 | 294.3686 | 299.4421
3226.6135 | 400.019 | 294.4022 | 299.5477
3227.6135 | 399.9037 | 294.3977 | 299.5696
3228.6135 | 399.8644 | 294.4401 | 299.5255
3229.6135 | 399.7109 | 294.4687 | 299.4337
3230.6135 | 399.7237 | 294.5076 | 299.4955
3231.6135 | 399.8579 | 294.5593 | 299.7681
3232.6135 | 399.9055 | 294.5965 | 300.1397
3233.6135 | 399.9055 | 294.6306 | 300.3166
3234.6135 | 399.9517 | 294.6676 | 300.236
3235.6135 | 399.9376 | 294.7587 | 300.3057
3236.6135 | 399.9859 | 294.8107 | 300.5838
3237.6135 | 400.0426 | 294.876 | 300.8024
3238.6135 | 400.1002 | 294.9046 | 300.7673
3239.6135 | 400.1266 | 294.9421 | 300.6549
3240.6135 | 400.123 | 294.9803 | 300.5918
3241.6135 | 400.0868 | 295.0338 | 300.4031
3242.6135 | 400.1508 | 295.1168 | 300.3282
3243.6135 | 400.0578 | 295.2108 | 300.3825
3244.6135 | 399.9851 | 295.2945 | 300.401
3245.6135 | 400.054 | 295.3805 | 300.5204
3246.6135 | 400.1474 | 295.3996 | 300.685
3247.6135 | 400.1562 | 295.4273 | 300.9917
3248.6135 | 399.958 | 295.4451 | 301.3595
3249.6135 | 399.9589 | 295.459 | 301.3809
3250.6135 | 399.8763 | 295.4949 | 301.3952
3251.6135 | 399.8275 | 295.5695 | 301.2708
3252.6135 | 399.8097 | 295.6439 | 301.2417
3253.6135 | 399.7815 | 295.6892 | 301.3482
3254.6135 | 399.6283 | 295.7651 | 301.3894
3255.6135 | 399.5626 | 295.8453 | 301.6419
3256.6135 | 399.7461 | 295.9337 | 301.7159
3257.6135 | 399.6727 | 296.0377 | 301.5048
3258.6135 | 399.6759 | 296.0828 | 301.4614
3259.6135 | 399.5932 | 296.1188 | 301.502
3260.6135 | 399.5966 | 296.1622 | 301.5796
3261.6135 | 399.6159 | 296.2239 | 301.7171
3262.6135 | 399.5897 | 296.2964 | 301.8019
3263.6135 | 399.4477 | 296.3754 | 301.6895
3264.6135 | 399.4976 | 296.4264 | 301.7866
3265.6135 | 399.5787 | 296.4584 | 301.7132
3266.6135 | 399.6053 | 296.5098 | 301.7822
3267.6135 | 399.6563 | 296.5761 | 301.9301
3268.6135 | 399.5906 | 296.6656 | 301.9413
3269.6135 | 399.4805 | 296.7743 | 301.9066
3270.6135 | 399.5141 | 296.8667 | 301.6689
3271.6135 | 399.4528 | 296.9955 | 301.6427
3272.6135 | 399.315 | 297.0971 | 301.6382
3273.6135 | 399.3004 | 297.2046 | 301.5144
3274.6135 | 399.3501 | 297.2704 | 301.5239
3275.6135 | 399.4219 | 297.318 | 301.768
3276.6135 | 399.5081 | 297.3363 | 302.0063
3277.6135 | 399.6936 | 297.3515 | 301.8063
3278.6135 | 399.6444 | 297.4154 | 301.5324
3279.6135 | 399.7008 | 297.4873 | 301.147
3280.6135 | 399.7943 | 297.5954 | 300.9822
3281.6135 | 399.8622 | 297.64 | 301.0493
3282.6135 | 399.8678 | 297.656 | 301.2507
3283.6135 | 399.9974 | 297.6604 | 301.489
3284.6135 | 400.0708 | 297.681 | 301.7392
3285.6135 | 400.0352 | 297.6967 | 301.8845
3286.6135 | 400.0582 | 297.719 | 301.9395
3287.6135 | 400.0764 | 297.7776 | 301.9413
3288.6135 | 400.2193 | 297.835 | 302.0602
3289.6135 | 400.1701 | 297.9289 | 302.0903
3290.6135 | 400.292 | 298.0329 | 302.0516
3291.6135 | 400.3033 | 298.0886 | 301.9162
3292.6135 | 400.2928 | 298.2284 | 301.6268
3293.6135 | 400.2689 | 298.3228 | 301.5117
3294.6135 | 400.1226 | 298.4255 | 301.2139
3295.6135 | 400.0132 | 298.5509 | 300.7092
3296.6135 | 400.1042 | 298.6532 | 300.5785
3297.6135 | 400.096 | 298.7662 | 300.6473
3298.6135 | 399.9663 | 298.8761 | 300.6812
3299.6135 | 399.8797 | 298.9593 | 300.4877
3300.6135 | 399.8872 | 299.0571 | 300.3856
3301.6135 | 399.7321 | 299.1649 | 300.6291
3302.6135 | 399.5674 | 299.2668 | 300.9039
3303.6135 | 399.5855 | 299.3459 | 301.0441
3304.6135 | 399.7038 | 299.4447 | 300.9097
3305.6135 | 399.9372 | 299.5505 | 300.6685
3306.6135 | 400.0092 | 299.6471 | 300.5252
3307.6135 | 399.9929 | 299.7031 | 300.5063
3308.6135 | 400.0857 | 299.7168 | 300.3753
3309.6135 | 400.036 | 299.7357 | 300.419
3310.6135 | 400.0651 | 299.7345 | 300.8599
3311.6135 | 400.1414 | 299.7291 | 301.1141
3312.6135 | 400.154 | 299.7515 | 301.3249
3313.6135 | 400.0626 | 299.7336 | 301.5301
3314.6135 | 399.9275 | 299.704 | 301.6534
3315.6135 | 399.8537 | 299.7568 | 301.8135
3316.6135 | 399.8045 | 299.785 | 302.0992
3317.6135 | 399.905 | 299.8093 | 302.333
3318.6135 | 399.9379 | 299.7788 | 302.5273
3319.6135 | 400.0576 | 299.7672 | 302.6143
3320.6135 | 400.1834 | 299.7669 | 302.9182
3321.6135 | 400.1048 | 299.7934 | 303.2869
3322.6135 | 400.2924 | 299.7942 | 303.4886
3323.6135 | 400.3646 | 299.7901 | 303.76
3324.6135 | 400.2963 | 299.7681 | 303.9673
3325.6135 | 400.2798 | 299.7778 | 304.2328
3326.6135 | 400.3239 | 299.7954 | 304.3145
3327.6135 | 400.4185 | 299.7752 | 304.4942
3328.6135 | 400.4335 | 299.7968 | 304.3793
3329.6135 | 400.4009 | 299.7908 | 304.1334
3330.6135 | 400.3699 | 299.8128 | 304.0113
3331.6135 | 400.4084 | 299.8456 | 304.1088
3332.6135 | 400.4739 | 299.8879 | 304.3793
3333.6135 | 400.4511 | 299.9531 | 304.7338
3334.6135 | 400.3909 | 299.985 | 304.8855
3335.6135 | 400.4398 | 300.0729 | 304.7012
3336.6135 | 400.4099 | 300.1632 | 304.7436
3337.6135 | 400.3997 | 300.2367 | 304.8281
3338.6135 | 400.4565 | 300.333 | 304.8434
3339.6135 | 400.3387 | 300.429 | 304.8037
3340.6135 | 400.3248 | 300.508 | 304.5899
3341.6135 | 400.331 | 300.6189 | 304.6451
3342.6135 | 400.2391 | 300.7238 | 304.8544
3343.6135 | 400.2285 | 300.824 | 304.7278
3344.6135 | 400.0375 | 300.9483 | 304.7863
3345.6135 | 399.9046 | 300.9836 | 304.8523
3346.6135 | 399.9406 | 301.0086 | 304.8995
3347.6135 | 399.9481 | 301.0367 | 304.9598
3348.6135 | 399.9752 | 301.0839 | 305.0712
3349.6135 | 400.0215 | 301.1491 | 305.2269
3350.6135 | 400.0299 | 301.1761 | 305.2109
3351.6135 | 399.9067 | 301.2212 | 305.1232
3352.6135 | 399.9848 | 301.2198 | 305.1671
3353.6135 | 400.0833 | 301.2346 | 304.9512
3354.6135 | 400.0751 | 301.2751 | 305.0404
3355.6135 | 399.9759 | 301.3088 | 304.9872
3356.6135 | 399.8869 | 301.3192 | 304.5367
3357.6135 | 399.8632 | 301.367 | 304.2134
3358.6135 | 399.8739 | 301.3994 | 304.1966
3359.6135 | 399.8611 | 301.4326 | 304.3575
3360.6135 | 399.9607 | 301.4686 | 304.53
3361.6135 | 399.9136 | 301.4996 | 304.6894
3362.6135 | 399.8231 | 301.5366 | 304.8173
3363.6135 | 399.8043 | 301.5977 | 304.6987
3364.6135 | 399.726 | 301.6465 | 304.572
3365.6135 | 399.6569 | 301.7587 | 304.4528
3366.6135 | 399.6034 | 301.8422 | 304.4208
3367.6135 | 399.5126 | 301.8898 | 304.4163
3368.6135 | 399.5079 | 301.9045 | 304.3413
3369.6135 | 399.5133 | 301.9387 | 304.2645
3370.6135 | 399.4688 | 301.9598 | 304.3074
3371.6135 | 399.3475 | 302.0264 | 304.3287
3372.6135 | 399.2428 | 302.0386 | 304.3986
3373.6135 | 399.138 | 302.02 | 304.2153
3374.6135 | 399.233 | 302.0376 | 303.9567
3375.6135 | 399.428 | 302.0529 | 303.974
3376.6135 | 399.4691 | 302.0932 | 304.0442
3377.6135 | 399.3663 | 302.1077 | 304.216
3378.6135 | 399.1775 | 302.1372 | 304.2516
3379.6135 | 399.1636 | 302.1441 | 304.1797
3380.6135 | 399.3052 | 302.1852 | 304.2558
3381.6135 | 399.3349 | 302.2169 | 304.1483
3382.6135 | 399.3219 | 302.2314 | 304.2026
3383.6135 | 399.2994 | 302.2585 | 304.2437
3384.6135 | 399.2872 | 302.2984 | 304.1118
3385.6135 | 399.3892 | 302.3198 | 303.6801
3386.6135 | 399.3703 | 302.3524 | 303.6429
3387.6135 | 399.595 | 302.3823 | 303.8965
3388.6135 | 399.658 | 302.4142 | 303.937
3389.6135 | 399.7165 | 302.4487 | 304.0758
3390.6135 | 399.8075 | 302.4741 | 304.2131
3391.6135 | 399.7901 | 302.4908 | 304.3472
3392.6135 | 399.9466 | 302.5241 | 304.1562
3393.6135 | 400.0061 | 302.5415 | 304.2609
3394.6135 | 400.0312 | 302.5714 | 304.4751
3395.6135 | 400.0126 | 302.6553 | 304.6644
3396.6135 | 400.0665 | 302.7068 | 304.7648
3397.6135 | 400.097 | 302.7396 | 304.8146
3398.6135 | 400.0008 | 302.7431 | 304.8576
3399.6135 | 399.8827 | 302.7626 | 304.6889
3400.6135 | 399.8144 | 302.7366 | 304.733
3401.6135 | 399.9173 | 302.742 | 305.0687
3402.6135 | 399.9389 | 302.716 | 305.2534
3403.6135 | 399.9885 | 302.6949 | 305.4122
3404.6135 | 400.0106 | 302.7052 | 305.3816
3405.6135 | 400.0135 | 302.7126 | 305.6251
3406.6135 | 400.0713 | 302.7156 | 305.8979
3407.6135 | 399.9181 | 302.7172 | 306.0144
3408.6135 | 399.7946 | 302.7269 | 306.217
3409.6135 | 399.6576 | 302.7298 | 306.354
3410.6135 | 399.6543 | 302.7607 | 306.2206
3411.6135 | 399.5881 | 302.7732 | 306.1569
3412.6135 | 399.6107 | 302.8016 | 306.3938
3413.6135 | 399.7455 | 302.8642 | 306.3595
3414.6135 | 399.6956 | 302.8793 | 306.1787
3415.6135 | 399.6173 | 302.8863 | 305.9167
3416.6135 | 399.7396 | 302.911 | 305.6061
3417.6135 | 399.8897 | 302.9538 | 305.4449
3418.6135 | 399.9853 | 303.0043 | 305.448
3419.6135 | 400.0619 | 303.05 | 305.2906
3420.6135 | 399.9856 | 303.1372 | 305.4238
3421.6135 | 399.9772 | 303.206 | 305.621
3422.6135 | 399.9482 | 303.2889 | 305.7862
3423.6135 | 399.7683 | 303.3825 | 305.4615
3424.6135 | 399.6575 | 303.5158 | 305.2303
3425.6135 | 399.5992 | 303.6632 | 304.8513
3426.6135 | 399.6243 | 303.7599 | 304.5408
3427.6135 | 399.5485 | 303.8338 | 304.2249
3428.6135 | 399.6085 | 303.9118 | 304.1581
3429.6135 | 399.8377 | 303.9811 | 304.4479
3430.6135 | 399.876 | 303.9752 | 305.0707
3431.6135 | 399.8654 | 303.9573 | 305.4565
3432.6135 | 399.8886 | 303.954 | 305.5941
3433.6135 | 399.8462 | 303.9393 | 305.898
3434.6135 | 399.7826 | 303.9422 | 306.1452
3435.6135 | 399.7342 | 303.9181 | 306.0143
3436.6135 | 399.7888 | 303.8867 | 305.8998
3437.6135 | 399.8546 | 303.8649 | 305.8676
3438.6135 | 399.7886 | 303.8593 | 305.7998
3439.6135 | 399.8421 | 303.8885 | 305.7144
3440.6135 | 399.9499 | 303.9174 | 305.6406
3441.6135 | 400.1783 | 303.9296 | 305.4376
3442.6135 | 400.3618 | 303.9585 | 305.7641
3443.6135 | 400.357 | 304.0027 | 306.1689
3444.6135 | 400.3801 | 304.0876 | 306.4235
3445.6135 | 400.4363 | 304.1501 | 306.6459
3446.6135 | 400.5037 | 304.2086 | 306.9458
3447.6135 | 400.5185 | 304.2781 | 307.2076
3448.6135 | 400.4616 | 304.3258 | 307.2186
3449.6135 | 400.4169 | 304.3271 | 307.3828
3450.6135 | 400.4609 | 304.3135 | 307.6654
3451.6135 | 400.5645 | 304.3311 | 307.8735
3452.6135 | 400.5452 | 304.3248 | 307.9776
3453.6135 | 400.5855 | 304.3239 | 307.959
3454.6135 | 400.5825 | 304.3378 | 307.9396
3455.6135 | 400.6687 | 304.3595 | 307.903
3456.6135 | 400.7358 | 304.4237 | 307.9256
3457.6135 | 400.7511 | 304.5049 | 308.3457
3458.6135 | 400.8428 | 304.6393 | 307.7623
3459.6135 | 400.7682 | 304.746 | 307.0941
3460.6135 | 400.6385 | 304.8301 | 306.7268
3461.6135 | 400.6092 | 304.8728 | 306.397
3462.6135 | 400.5537 | 304.9095 | 306.4202
3463.6135 | 400.4855 | 304.9498 | 306.7238
3464.6135 | 400.5199 | 304.9587 | 306.9038
3465.6135 | 400.4956 | 304.9583 | 306.9241
3466.6135 | 400.4548 | 304.9825 | 307.0285
3467.6135 | 400.3496 | 305.0532 | 307.3261
3468.6135 | 400.3334 | 305.0912 | 307.6235
3469.6135 | 400.2403 | 305.1013 | 307.802
3470.6135 | 400.2401 | 305.0127 | 307.9029
3471.6135 | 400.2073 | 304.9703 | 307.8419
3472.6135 | 400.0283 | 304.971 | 307.8931
3473.6135 | 400.0074 | 304.9617 | 307.5967
3474.6135 | 400.1316 | 304.9766 | 307.2736
3475.6135 | 399.9754 | 305.0037 | 307.0849
3476.6135 | 399.8793 | 305.0429 | 306.627
3477.6135 | 399.8757 | 305.1371 | 306.6915
3478.6135 | 399.8724 | 305.2435 | 307.0436
3479.6135 | 399.9395 | 305.3585 | 306.7097
3480.6135 | 399.9391 | 305.4629 | 306.3445
3481.6135 | 399.8934 | 305.6138 | 306.2767
3482.6135 | 399.6954 | 305.7887 | 307.0103
3483.6135 | 399.7494 | 305.9816 | 307.2607
3484.6135 | 399.7502 | 306.1955 | 307.7025
3485.6135 | 399.6173 | 306.4499 | 308.0255
3486.6135 | 399.6893 | 306.7124 | 308.1479
3487.6135 | 399.6764 | 306.9679 | 308.2509
3488.6135 | 399.7011 | 307.3681 | 308.736
3489.6135 | 399.9052 | 307.6442 | 308.9449
3490.6135 | 400.0053 | 307.928 | 308.8347
3491.6135 | 399.8475 | 308.1525 | 308.6819
3492.6135 | 399.7474 | 308.3743 | 308.3857
3493.6135 | 399.5831 | 308.6425 | 308.1732
3494.6135 | 399.5012 | 308.8669 | 308.054
3495.6135 | 399.3671 | 309.062 | 307.7667
3496.6135 | 399.3228 | 309.2664 | 307.5499
3497.6135 | 399.3174 | 309.4399 | 307.1692
3498.6135 | 399.2589 | 309.5961 | 306.9834
3499.6135 | 399.3094 | 309.7139 | 306.624
3500.6135 | 399.286 | 309.8633 | 306.4826
3501.6135 | 399.3397 | 309.9895 | 306.7262
3502.6135 | 399.3671 | 310.1141 | 306.797
3503.6135 | 399.3553 | 310.2317 | 306.6164
3504.6135 | 399.2967 | 310.352 | 306.7008
3505.6135 | 399.4132 | 310.4303 | 306.5583
3506.6135 | 399.4005 | 310.4844 | 306.4873
3507.6135 | 399.4794 | 310.559 | 306.5374
3508.6135 | 399.4154 | 310.6131 | 306.6446
3509.6135 | 399.5004 | 310.6614 | 306.8916
3510.6135 | 399.6058 | 310.6978 | 307.2495
3511.6135 | 399.6174 | 310.7893 | 307.66
3512.6135 | 399.5442 | 310.8387 | 307.7934
3513.6135 | 399.478 | 310.8735 | 307.8325
3514.6135 | 399.5092 | 310.9168 | 307.9626
3515.6135 | 399.4037 | 310.9324 | 308.012
3516.6135 | 399.2744 | 310.9681 | 308.0262
3517.6135 | 399.2449 | 311.0309 | 308.047
3518.6135 | 399.1316 | 311.0687 | 308.1303
3519.6135 | 399.1638 | 311.0942 | 308.1611
3520.6135 | 399.1484 | 311.1199 | 308.0186
3521.6135 | 399.2706 | 311.1821 | 308.2725
3522.6135 | 399.4821 | 311.2196 | 308.4914
3523.6135 | 399.5935 | 311.2672 | 308.6291
3524.6135 | 399.6125 | 311.3077 | 308.8382
3525.6135 | 399.5865 | 311.338 | 309.1414
3526.6135 | 399.3906 | 311.3832 | 309.5786
3527.6135 | 399.3019 | 311.453 | 309.9341
3528.6135 | 399.238 | 311.4985 | 310.3697
3529.6135 | 399.2782 | 311.5461 | 310.6081
3530.6135 | 399.2781 | 311.5979 | 310.4349
3531.6135 | 399.3226 | 311.6398 | 310.6867
3532.6135 | 399.38 | 311.6424 | 311.0166
3533.6135 | 399.5284 | 311.6919 | 311.1702
3534.6135 | 399.5584 | 311.7404 | 311.3577
3535.6135 | 399.5315 | 311.7897 | 311.4958
3536.6135 | 399.4671 | 311.8225 | 311.543
3537.6135 | 399.5923 | 311.8827 | 311.7172
3538.6135 | 399.6324 | 311.9681 | 311.7333
3539.6135 | 399.5279 | 312.0082 | 311.7792
3540.6135 | 399.4871 | 312.039 | 312.0143
3541.6135 | 399.2206 | 312.0601 | 312.3099
3542.6135 | 399.0881 | 312.0629 | 312.3459
3543.6135 | 399.2612 | 312.112 | 312.1776
3544.6135 | 399.1631 | 312.1755 | 311.7915
3545.6135 | 399.0383 | 312.2311 | 311.511
3546.6135 | 398.9254 | 312.2419 | 311.2339
3547.6135 | 398.9575 | 312.2493 | 310.8574
3548.6135 | 398.9265 | 312.2442 | 310.3993
3549.6135 | 398.8318 | 312.2473 | 310.3164
3550.6135 | 398.7513 | 312.2779 | 310.1279
3551.6135 | 398.7245 | 312.3207 | 309.8666
3552.6135 | 398.75 | 312.3924 | 309.6641
3553.6135 | 398.7757 | 312.4393 | 309.4383
3554.6135 | 398.7579 | 312.4793 | 309.0669
3555.6135 | 398.7784 | 312.5299 | 308.9609
3556.6135 | 398.5886 | 312.5636 | 308.924
3557.6135 | 398.4568 | 312.5805 | 308.5867
3558.6135 | 398.5685 | 312.5766 | 308.2888
3559.6135 | 398.5873 | 312.583 | 308.2339
3560.6135 | 398.6579 | 312.5698 | 308.3675
3561.6135 | 398.5933 | 312.5485 | 308.4977
3562.6135 | 398.581 | 312.4993 | 308.5661
3563.6135 | 398.6136 | 312.4718 | 308.8467
3564.6135 | 398.4922 | 312.4465 | 309.0779
3565.6135 | 398.5398 | 312.4249 | 308.9395
3566.6135 | 398.54 | 312.4125 | 308.9773
3567.6135 | 398.4733 | 312.3884 | 309.1448
3568.6135 | 398.5767 | 312.352 | 309.2567
3569.6135 | 398.617 | 312.3283 | 309.3896
3570.6135 | 398.5895 | 312.3206 | 309.1332
3571.6135 | 398.4854 | 312.3109 | 309.0574
3572.6135 | 398.4817 | 312.3011 | 309.0808
3573.6135 | 398.4834 | 312.2702 | 308.6857
3574.6135 | 398.4983 | 312.2282 | 308.6272
3575.6135 | 398.5889 | 312.1727 | 308.7191
3576.6135 | 398.6046 | 312.1225 | 308.5994
3577.6135 | 398.5183 | 312.0655 | 308.292
3578.6135 | 398.5448 | 312.0025 | 307.98
3579.6135 | 398.7464 | 311.9455 | 307.9999
3580.6135 | 398.7773 | 311.8909 | 308.1738
3581.6135 | 398.7672 | 311.855 | 308.3179
3582.6135 | 398.8416 | 311.8026 | 308.83
3583.6135 | 398.921 | 311.7654 | 309.212
3584.6135 | 398.9133 | 311.7658 | 309.281
3585.6135 | 399.0027 | 311.7348 | 309.2288
3586.6135 | 399.1914 | 311.7185 | 308.9121
3587.6135 | 399.2838 | 311.6731 | 308.7288
3588.6135 | 399.273 | 311.6057 | 308.8355
3589.6135 | 399.3556 | 311.5422 | 309.1004
3590.6135 | 399.3423 | 311.4653 | 309.5699
3591.6135 | 399.3505 | 311.4282 | 309.9171
3592.6135 | 399.2824 | 311.3914 | 310.1434
3593.6135 | 399.1573 | 311.3643 | 309.8641
3594.6135 | 399.0322 | 311.3651 | 309.6881
3595.6135 | 399.0508 | 311.3555 | 309.715
3596.6135 | 399.1369 | 311.3514 | 309.91
3597.6135 | 399.1428 | 311.3546 | 310.0199
3598.6135 | 399.2556 | 311.3569 | 310.0965
3599.6135 | 399.3861 | 311.3574 | 310.3058
3600.6135 | 399.504 | 311.3645 | 310.2645
3601.6135 | 399.5154 | 311.3653 | 310.3907
3602.6135 | 399.5833 | 311.3424 | 310.4947
3603.6135 | 399.7086 | 311.3068 | 310.3278
3604.6135 | 399.5913 | 311.3044 | 310.0872
3605.6135 | 399.5081 | 311.2783 | 309.7802
3606.6135 | 399.5591 | 311.2551 | 309.5152
3607.6135 | 399.6076 | 311.2009 | 309.3018
3608.6135 | 399.6938 | 311.1325 | 309.4607
3609.6135 | 399.7681 | 311.0659 | 309.9327
3610.6135 | 399.6869 | 311.0685 | 310.4691
3611.6135 | 399.6257 | 311.0384 | 310.5583
3612.6135 | 399.6776 | 311.0021 | 310.3329
3613.6135 | 399.8021 | 310.9764 | 310.1272
3614.6135 | 399.6764 | 310.9447 | 310.4157
3615.6135 | 399.558 | 310.9045 | 310.5379
3616.6135 | 399.5565 | 310.8748 | 310.4848
3617.6135 | 399.4838 | 310.82 | 310.8704
3618.6135 | 399.5643 | 310.7792 | 310.9392
3619.6135 | 399.6661 | 310.7457 | 310.5596
3620.6135 | 399.6836 | 310.7017 | 310.2789
3621.6135 | 399.6405 | 310.6769 | 310.1905
3622.6292 | 399.6972 | 310.679 | 309.9508
3623.6135 | 399.7252 | 310.6812 | 309.6684
3624.6135 | 399.8216 | 310.6927 | 309.4531
3625.6135 | 399.8411 | 310.7021 | 309.4485
3626.6135 | 399.7695 | 310.6665 | 309.5113
3627.6135 | 399.7571 | 310.6364 | 309.6496
3628.6135 | 399.78 | 310.6044 | 309.6071
3629.6135 | 399.6582 | 310.6007 | 308.7952
3630.6135 | 399.6903 | 310.6164 | 308.5461
3631.6135 | 399.6875 | 310.6347 | 308.6113
3632.6135 | 399.8587 | 310.6358 | 308.3299
3633.6135 | 399.8746 | 310.6131 | 307.8912
3634.6135 | 399.7605 | 310.594 | 307.8997
3635.6135 | 399.7878 | 310.5667 | 308.2451
3636.6135 | 399.9838 | 310.5453 | 308.3678
3637.6135 | 400.0594 | 310.5638 | 308.6633
3638.6135 | 400.2021 | 310.5704 | 308.8576
3639.6135 | 400.3118 | 310.5534 | 308.7463
3640.6135 | 400.3151 | 310.5963 | 308.8108
3641.6135 | 400.2888 | 310.5923 | 309.0464
3642.6135 | 400.2629 | 310.577 | 309.4182
3643.6135 | 400.1844 | 310.5707 | 309.7237
3644.6135 | 400.1607 | 310.5453 | 310.1555
3645.6135 | 400.25 | 310.4944 | 310.1879
3646.6135 | 400.283 | 310.4684 | 309.6872
3647.6135 | 400.2778 | 310.4289 | 308.9846
3648.6135 | 400.223 | 310.3898 | 308.4684
3649.6135 | 400.1711 | 310.3429 | 308.5034
3650.6135 | 400.0791 | 310.3052 | 308.6692
3651.6135 | 399.8803 | 310.3118 | 308.3908
3652.6135 | 399.7663 | 310.2931 | 308.3068
3653.6135 | 399.6726 | 310.2828 | 308.3372
3654.6135 | 399.5253 | 310.2539 | 308.2968
3655.6135 | 399.4944 | 310.2433 | 308.2811
3656.6135 | 399.4609 | 310.2038 | 308.6657
3657.6135 | 399.3993 | 310.1524 | 308.905
3658.6292 | 399.31 | 310.1216 | 308.7556
3659.6135 | 399.2348 | 310.1055 | 308.7837
3660.6135 | 399.2712 | 310.1062 | 309.1232
3661.6135 | 399.2668 | 310.0824 | 308.928
3662.6135 | 399.2007 | 310.0539 | 308.7824
3663.6135 | 399.2106 | 310.0254 | 308.6575
3664.6135 | 399.1436 | 309.9769 | 308.8271
3665.6135 | 399.185 | 309.9466 | 308.8711
3666.6135 | 399.0499 | 309.8993 | 308.6321
3667.6135 | 399.1302 | 309.8536 | 308.4104
3668.6135 | 399.0833 | 309.8074 | 307.8952
3669.6135 | 399.0166 | 309.7347 | 307.5349
3670.6135 | 398.9364 | 309.6953 | 307.29
3671.6135 | 398.9572 | 309.6686 | 307.036
3672.6135 | 399.1373 | 309.6446 | 307.1321
3673.6135 | 399.2243 | 309.6324 | 307.3928
3674.6135 | 399.3014 | 309.6098 | 307.4935
3675.6135 | 399.3889 | 309.6076 | 307.2249
3676.6135 | 399.4855 | 309.6417 | 306.8086
3677.6135 | 399.4699 | 309.6882 | 306.7546
3678.6135 | 399.4535 | 309.7034 | 306.7665
3679.6135 | 399.5791 | 309.7572 | 306.8902
3680.6135 | 399.6157 | 309.778 | 307.1136
3681.6135 | 399.609 | 309.8042 | 307.1903
3682.6135 | 399.5524 | 309.7845 | 307.0498
3683.6135 | 399.5058 | 309.7687 | 306.6993
3684.6135 | 399.6252 | 309.7446 | 306.7118
3685.6135 | 399.6032 | 309.6947 | 306.7482
3686.6135 | 399.5834 | 309.6485 | 306.3192
3687.6135 | 399.5493 | 309.6003 | 306.3686
3688.6135 | 399.5918 | 309.4973 | 306.2133
3689.6135 | 399.6156 | 309.4221 | 306.3408
3690.6135 | 399.4509 | 309.3496 | 306.4945
3691.6135 | 399.2652 | 309.2561 | 306.8465
3692.6135 | 399.1761 | 309.1667 | 306.9818
3693.6135 | 399.0741 | 309.0925 | 306.7478
3694.6135 | 399.1104 | 309.0001 | 307.1019
3695.6135 | 399.1374 | 308.9101 | 307.7212
3696.6135 | 399.0878 | 308.8636 | 307.9866
3697.6135 | 399.0289 | 308.8289 | 307.9996
3698.6135 | 398.9062 | 308.7894 | 308.1725
3699.6135 | 398.7617 | 308.7953 | 308.1756
3700.6135 | 398.6964 | 308.7776 | 307.9814
3701.6135 | 398.6752 | 308.7434 | 307.6086
3702.6135 | 398.8589 | 308.6956 | 307.3423
3703.6135 | 398.962 | 308.6814 | 307.3785
3704.6135 | 399.0414 | 308.664 | 307.4473
3705.6135 | 399.1795 | 308.6866 | 307.3751
3706.6135 | 399.2956 | 308.6691 | 307.2138
3707.6135 | 399.42 | 308.6285 | 306.8669
3708.6135 | 399.5567 | 308.569 | 306.4393
3709.6135 | 399.5795 | 308.535 | 306.4138
3710.6135 | 399.5249 | 308.477 | 306.2869
3711.6135 | 399.61 | 308.4814 | 306.3197
3712.6135 | 399.683 | 308.4759 | 306.488
3713.6135 | 399.8304 | 308.4542 | 306.5578
3714.6135 | 399.8534 | 308.4079 | 306.8953
3715.6135 | 399.8907 | 308.3477 | 307.3932
3716.6135 | 399.9566 | 308.2986 | 307.346
3717.6135 | 400.0092 | 308.2331 | 307.4418
3718.6135 | 399.9552 | 308.2374 | 307.2443
3719.6135 | 399.9855 | 308.1972 | 306.9001
3720.6135 | 399.9422 | 308.1898 | 306.5766
3721.6135 | 399.8609 | 308.1822 | 306.3533
3722.6135 | 399.8745 | 308.1843 | 306.4406
3723.6135 | 399.8137 | 308.2076 | 306.7725
3724.6135 | 399.7916 | 308.2137 | 307.0574
3725.6135 | 399.7461 | 308.2046 | 306.9833
3726.6135 | 399.6279 | 308.2165 | 306.5166
3727.6135 | 399.5145 | 308.2086 | 306.1754
3728.6135 | 399.7431 | 308.2306 | 306.0616
3729.6135 | 399.75 | 308.26 | 306.4597
3730.6135 | 399.5521 | 308.2719 | 306.5345
3731.6135 | 399.4494 | 308.2964 | 306.1227
3732.6135 | 399.4719 | 308.2864 | 306.0082
3733.6135 | 399.5004 | 308.2914 | 306.5533
3734.6135 | 399.4997 | 308.3126 | 306.8402
3735.6135 | 399.4405 | 308.3371 | 306.4112
3736.6292 | 399.4581 | 308.3602 | 305.9516
3737.6135 | 399.4431 | 308.3496 | 306.0689
3738.6135 | 399.3466 | 308.3217 | 306.0743
3739.6135 | 399.2076 | 308.2976 | 305.9828
3740.6135 | 399.2907 | 308.2584 | 305.8189
3741.6135 | 399.3332 | 308.2541 | 305.7563
3742.6135 | 399.1376 | 308.2419 | 305.6226
3743.6135 | 399.1277 | 308.2544 | 305.7752
3744.6135 | 399.0719 | 308.2322 | 306.5235
3745.6135 | 398.9638 | 308.2288 | 306.9262
3746.6135 | 399.0705 | 308.2084 | 306.9332
3747.6135 | 399.2638 | 308.192 | 306.3971
3748.6135 | 399.2777 | 308.17 | 306.0956
3749.6135 | 399.3884 | 308.1464 | 305.9432
3750.6135 | 399.5049 | 308.1162 | 306.0623
3751.6135 | 399.5436 | 308.1069 | 306.1967
3752.6135 | 399.5475 | 308.1032 | 306.2524
3753.6135 | 399.4724 | 308.0681 | 306.5418
3754.6135 | 399.581 | 308.0361 | 306.857
3755.6135 | 399.6258 | 308.0241 | 306.8254
3756.6135 | 399.5947 | 307.9918 | 307.0606
3757.6135 | 399.7557 | 307.9873 | 307.0051
3758.6135 | 399.9016 | 307.9764 | 307.3715
3759.6135 | 399.9324 | 307.9293 | 307.7921
3760.6135 | 399.9545 | 307.9162 | 307.8601
3761.6135 | 399.9579 | 307.8828 | 307.6692
3762.6135 | 400.0852 | 307.846 | 307.7387
3763.6135 | 400.0843 | 307.8126 | 307.6596
3764.6135 | 400.1552 | 307.7824 | 307.6335
3765.6135 | 400.1443 | 307.7784 | 307.5205
3766.6135 | 400.2692 | 307.7448 | 307.3268
3767.6135 | 400.3182 | 307.7487 | 307.3632
3768.6135 | 400.293 | 307.7216 | 307.4604
3769.6135 | 400.37 | 307.6828 | 306.8815
3770.6135 | 400.2648 | 307.6867 | 306.8895
3771.6135 | 400.0761 | 307.7051 | 306.9706
3772.6135 | 400.0163 | 307.7607 | 306.3303
3773.6135 | 400.1193 | 307.8137 | 305.8454
3774.6135 | 400.087 | 307.8776 | 306.0051
3775.6135 | 400.0912 | 307.9384 | 306.2078
3776.6135 | 400.1836 | 307.9588 | 306.1856
3777.6135 | 399.9981 | 307.9922 | 306.5143
3778.6135 | 399.9891 | 308.0237 | 306.8085
3779.6135 | 399.8805 | 308.0399 | 306.6741
3780.6135 | 399.7539 | 308.0672 | 306.6334
3781.6135 | 399.8486 | 308.0634 | 306.3674
3782.6135 | 399.8661 | 308.073 | 306.5526
3783.6135 | 399.7832 | 308.0401 | 306.7269
3784.6135 | 399.6765 | 308.0376 | 306.9179
3785.6135 | 399.453 | 308.0279 | 307.0884
3786.6135 | 399.4757 | 308.0575 | 307.2347
3787.6135 | 399.4127 | 308.0508 | 307.2061
3788.6135 | 399.403 | 308.0392 | 307.403
3789.6135 | 399.2562 | 308.0025 | 307.3199
3790.6135 | 399.2014 | 307.9635 | 306.7217
3791.6135 | 399.1195 | 307.8958 | 306.4865
3792.6135 | 399.0438 | 307.8274 | 306.4009
3793.6135 | 398.9905 | 307.7234 | 306.0047
3794.6135 | 399.0618 | 307.6427 | 305.9102
3795.6135 | 399.0436 | 307.5664 | 306.1395
3796.6135 | 399.1369 | 307.4983 | 306.5015
3797.6135 | 399.3345 | 307.4449 | 306.8143
3798.6135 | 399.3404 | 307.4181 | 307.3339
3799.6135 | 399.2307 | 307.3993 | 307.7538
3800.6135 | 399.2763 | 307.3869 | 307.7901
3801.6135 | 399.2998 | 307.3284 | 307.6818
3802.6135 | 399.586 | 307.2523 | 307.9615
3803.6135 | 399.767 | 307.1972 | 308.1797
3804.6135 | 399.7376 | 307.1621 | 308.5823
3805.6135 | 399.7849 | 307.087 | 308.7673
3806.6135 | 399.8628 | 307.0426 | 308.8793
3807.6135 | 399.884 | 306.9657 | 308.9801
3808.6135 | 399.6873 | 306.9307 | 309.1434
3809.6135 | 399.6005 | 306.9251 | 309.073
3810.6135 | 399.6303 | 306.9084 | 309.1878
3811.6135 | 399.602 | 306.9193 | 308.7738
3812.6135 | 399.5582 | 306.9352 | 308.4776
3813.6135 | 399.5268 | 306.9348 | 308.2959
3814.6135 | 399.3755 | 306.9742 | 308.2016
3815.6135 | 399.3694 | 307.0211 | 308.5209
3816.6135 | 399.433 | 307.0759 | 308.6504
3817.6135 | 399.5824 | 307.1138 | 308.1992
3818.6135 | 399.8014 | 307.1531 | 307.6304
3819.6135 | 399.9462 | 307.2177 | 307.6633
3820.6135 | 400.1338 | 307.2769 | 307.8575
3821.6135 | 400.2339 | 307.3559 | 307.8373
3822.6135 | 400.1939 | 307.4283 | 307.5298
3823.6135 | 400.1354 | 307.4857 | 307.275
3824.6135 | 400.0441 | 307.5509 | 307.1655
3825.6135 | 400.052 | 307.5986 | 307.1739
3826.6135 | 399.9917 | 307.6453 | 307.31
3827.6135 | 399.9105 | 307.6575 | 307.485
3828.6135 | 399.7675 | 307.6919 | 307.63
3829.6135 | 399.7821 | 307.6928 | 307.5173
3830.6135 | 399.9 | 307.638 | 307.3954
3831.6135 | 399.9343 | 307.5507 | 307.4892
3832.6135 | 399.9896 | 307.4613 | 307.6689
3833.6135 | 399.9811 | 307.3936 | 307.7963
3834.6135 | 399.8983 | 307.3275 | 308.0132
3835.6135 | 399.8137 | 307.2534 | 308.0608
3836.6135 | 399.8442 | 307.1941 | 308.2464
3837.6135 | 399.8607 | 307.1258 | 307.9818
3838.6135 | 399.8122 | 307.074 | 307.5628
3839.6135 | 399.7346 | 307.0058 | 307.21
3840.6135 | 399.729 | 306.9573 | 307.2825
3841.6135 | 399.7281 | 306.945 | 307.4281
3842.6135 | 399.8675 | 306.9426 | 307.1862
3843.6135 | 399.8866 | 306.9457 | 307.3163
3844.6135 | 399.7906 | 306.9552 | 307.1497
3845.6135 | 399.7689 | 306.9521 | 307.0377
3846.6135 | 399.8141 | 306.9662 | 306.7263
3847.6135 | 399.7128 | 306.9635 | 306.446
3848.6135 | 399.7362 | 307.0053 | 306.2666
3849.6135 | 399.76 | 307.0417 | 306.0353
3850.6135 | 399.7851 | 307.092 | 306.1601
3851.6135 | 399.8028 | 307.1313 | 306.4533
3852.6135 | 399.833 | 307.1288 | 306.4591
3853.6135 | 399.8127 | 307.1038 | 306.5852
3854.6135 | 399.9164 | 307.0635 | 306.5834
3855.6135 | 399.937 | 307.0104 | 306.9134
3856.6135 | 400.0233 | 306.9605 | 307.0034
3857.6135 | 399.9652 | 306.9426 | 307.3563
3858.6135 | 400.0112 | 306.9355 | 307.5364
3859.6135 | 400.1498 | 306.9166 | 307.4465
3860.6135 | 400.212 | 306.8849 | 307.2394
3861.6135 | 400.2034 | 306.8637 | 306.7092
3862.6135 | 400.1053 | 306.8403 | 306.8086
3863.6135 | 400.1003 | 306.8141 | 306.9161
3864.6135 | 400.0906 | 306.7941 | 306.9057
3865.6135 | 400.0936 | 306.7751 | 307.0975
3866.6135 | 400.138 | 306.7301 | 307.366
3867.6135 | 400.0622 | 306.6884 | 307.5429
3868.6135 | 399.8625 | 306.6663 | 307.6459
3869.6135 | 399.778 | 306.6124 | 307.4972
3870.6135 | 399.7559 | 306.5878 | 307.4373
3871.6135 | 399.771 | 306.5735 | 306.8833
3872.6135 | 399.9619 | 306.5865 | 306.0351
3873.6135 | 399.9189 | 306.6076 | 306.1136
3874.6135 | 399.8442 | 306.6346 | 306.6422
3875.6135 | 399.866 | 306.6508 | 306.6305
3876.6135 | 399.8556 | 306.6924 | 306.4568
3877.6135 | 399.9048 | 306.7257 | 306.2474
3878.6135 | 399.7933 | 306.7913 | 306.1449
3879.6135 | 399.8059 | 306.8231 | 306.3239
3880.6135 | 399.7811 | 306.8452 | 305.9164
3881.6135 | 399.8677 | 306.8635 | 305.9285
3882.6135 | 399.8285 | 306.8822 | 305.7413
3883.6135 | 399.9123 | 306.8852 | 305.9341
3884.6135 | 399.87 | 306.8836 | 306.5877
3885.6135 | 399.8195 | 306.8863 | 306.9671
3886.6135 | 399.7972 | 306.8682 | 306.5334
3887.6135 | 399.68 | 306.8432 | 306.7461
3888.6135 | 399.6456 | 306.8329 | 306.6931
3889.6135 | 399.7838 | 306.8132 | 306.0398
3890.6135 | 399.7349 | 306.8037 | 305.3889
3891.6135 | 399.7626 | 306.8222 | 305.4542
3892.6135 | 399.838 | 306.8522 | 305.484
3893.6135 | 399.9664 | 306.8593 | 305.3475
3894.6135 | 400.0431 | 306.8781 | 304.8615
3895.6135 | 400.0491 | 306.8858 | 304.5112
3896.6135 | 399.8819 | 306.9001 | 304.1968
3897.6135 | 399.8545 | 306.9421 | 304.1632
3898.6135 | 399.9625 | 306.9861 | 303.9604
3899.6135 | 399.953 | 306.9932 | 303.6488
3900.6135 | 400.0022 | 307.0114 | 303.7729
3901.6135 | 399.99 | 307.0091 | 303.7969
3902.6135 | 399.8527 | 306.9962 | 304.1564
3903.6135 | 399.7275 | 306.9841 | 304.2937
3904.6135 | 399.764 | 306.9924 | 304.1981
3905.6135 | 399.7363 | 307.0135 | 304.1358
3906.6135 | 399.6292 | 307.0057 | 303.9612
3907.6135 | 399.7822 | 306.9863 | 303.7423
3908.6135 | 399.7851 | 306.9615 | 303.5345
3909.6135 | 399.7123 | 306.9216 | 303.3873
3910.6135 | 399.6728 | 306.8833 | 303.4409
3911.6135 | 399.6822 | 306.845 | 303.4561
3912.6135 | 399.7242 | 306.8261 | 303.4774
3913.6135 | 399.6479 | 306.7991 | 303.8771
3914.6135 | 399.6857 | 306.7762 | 304.0247
3915.6135 | 399.4714 | 306.7362 | 303.8344
3916.6135 | 399.2833 | 306.6637 | 303.5062
3917.6135 | 399.1997 | 306.5978 | 303.6526
3918.6135 | 399.2551 | 306.5152 | 304.1261
3919.6135 | 399.283 | 306.4422 | 304.3467
3920.6135 | 399.427 | 306.3779 | 305.0476
3921.6135 | 399.5525 | 306.3356 | 305.6448
3922.6135 | 399.4804 | 306.2975 | 306.0482
3923.6135 | 399.5076 | 306.2512 | 306.5915
3924.6135 | 399.4504 | 306.246 | 306.842
3925.6135 | 399.3808 | 306.2149 | 307.0254
3926.6135 | 399.4428 | 306.1526 | 307.2267
3927.6135 | 399.5612 | 306.0913 | 307.2775
3928.6135 | 399.4586 | 306.0511 | 307.4402
3929.6135 | 399.4034 | 306.0247 | 307.7271
3930.6135 | 399.5133 | 305.9987 | 307.6327
3931.6135 | 399.6619 | 305.9767 | 307.844
3932.6135 | 399.5601 | 305.9689 | 308.1336
3933.6135 | 399.4828 | 305.9513 | 308.3862
3934.6135 | 399.5262 | 305.919 | 308.2463
3935.6135 | 399.517 | 305.9235 | 308.5364
3936.6135 | 399.6461 | 305.9162 | 308.5056
3937.6135 | 399.7573 | 305.9081 | 308.3588
3938.6135 | 399.7658 | 305.9323 | 308.425
3939.6135 | 399.7492 | 305.9612 | 308.3153
3940.6135 | 399.7129 | 305.9953 | 307.8001
3941.6135 | 399.7478 | 306.0171 | 307.4849
3942.6135 | 399.7802 | 306.0379 | 307.4026
3943.6135 | 399.7126 | 306.0625 | 307.4934
3944.6135 | 399.7097 | 306.0945 | 307.3789
3945.6135 | 399.7701 | 306.1001 | 307.4329
3946.6135 | 399.6509 | 306.1029 | 307.6106
3947.6135 | 399.7934 | 306.1078 | 308.1331
3948.6135 | 399.7601 | 306.0942 | 308.7296
3949.6135 | 399.5923 | 306.0752 | 308.9127
3950.6135 | 399.5155 | 306.0531 | 308.7652
3951.6135 | 399.5629 | 306.0672 | 308.4917
3952.6135 | 399.5428 | 306.0561 | 308.4863
3953.6135 | 399.537 | 306.0728 | 308.6417
3954.6135 | 399.4999 | 306.0502 | 308.3829
3955.6135 | 399.5392 | 306.0605 | 307.9038
3956.6135 | 399.5065 | 306.0465 | 307.9915
3957.6135 | 399.6135 | 306.0531 | 308.4686
3958.6135 | 399.5149 | 306.0624 | 309.0374
3959.6135 | 399.4038 | 306.0324 | 309.1288
3960.6135 | 399.5413 | 306.0123 | 309.2434
3961.6135 | 399.5445 | 306.0034 | 309.1088
3962.6135 | 399.5305 | 305.9874 | 308.9659
3963.6135 | 399.5092 | 305.991 | 308.9994
3964.6135 | 399.5041 | 305.9711 | 308.8893
3965.6135 | 399.6396 | 305.9489 | 308.6041
3966.6135 | 399.5019 | 305.9441 | 308.7723
3967.6135 | 399.3218 | 305.9338 | 308.7228
3968.6135 | 399.3201 | 305.9026 | 308.6955
3969.6135 | 399.3951 | 305.8933 | 308.902
3970.6135 | 399.3976 | 305.8943 | 309.048
3971.6135 | 399.4353 | 305.8896 | 309.314
3972.6135 | 399.5822 | 305.9258 | 308.7736
3973.6135 | 399.501 | 305.9415 | 308.42
3974.6135 | 399.4043 | 305.9675 | 308.2548
3975.6135 | 399.4952 | 306.0044 | 308.129
3976.6135 | 399.5986 | 306.0303 | 307.954
3977.6135 | 399.5699 | 306.0788 | 307.9545
3978.6135 | 399.5776 | 306.1289 | 308.2857
3979.6135 | 399.6271 | 306.1547 | 308.6739
3980.6135 | 399.6774 | 306.1914 | 308.8295
3981.6135 | 399.7422 | 306.1952 | 308.7635
3982.6135 | 399.8797 | 306.2051 | 308.8512
3983.6135 | 399.9282 | 306.2185 | 308.6064
3984.6135 | 399.835 | 306.2322 | 308.613
3985.6135 | 399.8753 | 306.2166 | 308.6036
3986.6135 | 399.9389 | 306.2424 | 308.303
3987.6135 | 399.7861 | 306.2552 | 307.4644
3988.6135 | 399.8168 | 306.3014 | 307.333
3989.6135 | 399.7665 | 306.3255 | 307.4266
3990.6135 | 399.7064 | 306.3551 | 307.498
3991.6135 | 399.6034 | 306.374 | 307.9096
3992.6135 | 399.5175 | 306.3776 | 307.7174
3993.6135 | 399.3955 | 306.3727 | 307.4633
3994.6135 | 399.3103 | 306.3607 | 307.1202
3995.6135 | 399.3862 | 306.3578 | 307.0016
3996.6135 | 399.3493 | 306.3421 | 307.1156
3997.6135 | 399.3052 | 306.3667 | 307.1772
3998.6135 | 399.4917 | 306.3792 | 307.0797
3999.6135 | 399.4275 | 306.3721 | 306.9222
4000.6135 | 399.3211 | 306.322 | 307.1926
4001.6135 | 399.3791 | 306.2191 | 307.1538
4002.6135 | 399.4936 | 306.1369 | 306.5903
4003.6135 | 399.4908 | 306.0754 | 306.4377
4004.6135 | 399.5018 | 306.0268 | 306.4024
4005.6135 | 399.5866 | 305.9911 | 305.9456
4006.6135 | 399.6697 | 305.9356 | 305.9047
4007.6135 | 399.7403 | 305.8661 | 306.1836
4008.6135 | 399.834 | 305.7754 | 306.4821
4009.6135 | 399.7833 | 305.7393 | 306.4851
4010.6135 | 399.8576 | 305.6993 | 306.7436
4011.6135 | 399.9999 | 305.6713 | 307.2232
4012.6135 | 399.8781 | 305.6721 | 307.3142
4013.6135 | 399.9168 | 305.6718 | 307.0701
4014.6135 | 399.9548 | 305.6704 | 307.0228
4015.6135 | 400.0074 | 305.6815 | 306.9375
4016.6135 | 399.9779 | 305.6847 | 306.8714
4017.6135 | 400.2325 | 305.6975 | 307.0008
4018.6135 | 400.2407 | 305.7289 | 307.1475
4019.6135 | 400.1885 | 305.7698 | 307.2152
4020.6135 | 400.2494 | 305.8103 | 306.9442
4021.6135 | 400.2657 | 305.8794 | 306.6674
4022.6135 | 400.2241 | 305.9403 | 307.1884
4023.6135 | 400.2059 | 305.9886 | 307.4243
4024.6135 | 400.2562 | 306.0363 | 307.1616
4025.6135 | 400.2613 | 306.044 | 307.2343
4026.6135 | 400.0316 | 306.0942 | 307.4888
4027.6135 | 399.8148 | 306.1597 | 307.1899
4028.6135 | 399.8293 | 306.2442 | 306.7629
4029.6135 | 399.7425 | 306.3281 | 306.1152
4030.6135 | 399.6913 | 306.4178 | 305.9376
4031.6135 | 399.6161 | 306.4896 | 306.4069
4032.6135 | 399.6228 | 306.5754 | 306.1769
4033.6135 | 399.641 | 306.6254 | 305.6129
4034.6135 | 399.615 | 306.6856 | 305.0791
4035.6135 | 399.6189 | 306.736 | 304.4087
4036.6135 | 399.7268 | 306.7517 | 304.5569
4037.6135 | 399.8095 | 306.7408 | 304.7018
4038.6135 | 399.7048 | 306.7246 | 304.5073
4039.6135 | 399.6813 | 306.697 | 304.4702
4040.6135 | 399.7787 | 306.6299 | 304.6175
4041.6135 | 399.8191 | 306.5389 | 305.1756
4042.6135 | 399.7908 | 306.4475 | 305.513
4043.6135 | 399.9036 | 306.3802 | 305.7064
4044.6135 | 399.9898 | 306.3046 | 305.3693
4045.6135 | 399.9347 | 306.2653 | 305.4169
4046.6135 | 399.8888 | 306.2078 | 305.5413
4047.6135 | 400.025 | 306.1577 | 305.8598
4048.6135 | 400.1256 | 306.0987 | 305.9847
4049.6135 | 400.0403 | 306.0738 | 306.2051
4050.6135 | 399.8934 | 306.0384 | 306.8312
4051.6135 | 399.9333 | 306.031 | 307.1377
4052.6135 | 400.0787 | 306.0281 | 306.9149
4053.6135 | 400.1078 | 306.0313 | 306.4531
4054.6135 | 400.0189 | 306.0452 | 306.3042
4055.6135 | 400.1326 | 306.0656 | 306.2123
4056.6135 | 400.3524 | 306.0634 | 305.5806
4057.6135 | 400.3922 | 306.1011 | 305.93
4058.6135 | 400.4193 | 306.1296 | 305.8225
4059.6135 | 400.5005 | 306.1522 | 305.6212
4060.6135 | 400.5712 | 306.2051 | 306.2189
4061.6135 | 400.5809 | 306.2449 | 306.8388
4062.6135 | 400.6495 | 306.2865 | 307.2637
4063.6135 | 400.7909 | 306.2927 | 307.3298
4064.6135 | 400.801 | 306.2647 | 307.3497
4065.6135 | 400.7682 | 306.2372 | 306.9221
4066.6135 | 400.6978 | 306.2158 | 306.382
4067.6135 | 400.6568 | 306.1892 | 305.8996
4068.6135 | 400.6293 | 306.1807 | 305.6508
4069.6135 | 400.4883 | 306.1858 | 305.7893
4070.6135 | 400.4244 | 306.1619 | 305.5371
4071.6135 | 400.2755 | 306.1246 | 305.5297
4072.6135 | 400.2243 | 306.1202 | 305.704
4073.6135 | 400.3101 | 306.0842 | 305.9564
4074.6135 | 400.3785 | 306.0565 | 306.0266
4075.6135 | 400.4143 | 306.0256 | 306.3916
4076.6135 | 400.4686 | 305.9722 | 306.8463
4077.6135 | 400.6702 | 305.9102 | 307.0164
4078.6135 | 400.8399 | 305.8798 | 306.9649
4079.6135 | 400.7464 | 305.8352 | 307.0721
4080.6135 | 400.6684 | 305.8208 | 307.1952
4081.6135 | 400.5661 | 305.8289 | 307.0401
4082.6135 | 400.4233 | 305.8335 | 306.9
4083.6135 | 400.3557 | 305.8704 | 307.0683
4084.6135 | 400.2876 | 305.9041 | 306.9137
4085.6135 | 400.104 | 305.9539 | 306.4634
4086.6135 | 400.0588 | 306.0005 | 306.1199
4087.6135 | 399.9552 | 306.03 | 305.8311
4088.6135 | 399.7768 | 306.04 | 305.6323
4089.6135 | 399.7655 | 306.0304 | 306.0406
4090.6135 | 399.8403 | 306.0295 | 306.4014
4091.6135 | 399.775 | 306.0291 | 306.6001
4092.6135 | 399.6012 | 305.9977 | 306.7618
4093.6135 | 399.5923 | 305.9901 | 306.656
4094.6135 | 399.6043 | 305.9847 | 306.7941
4095.6135 | 399.5493 | 305.9674 | 307.2633
4096.6135 | 399.5066 | 305.9521 | 307.4592
4097.6135 | 399.499 | 305.9559 | 307.6602
4098.6135 | 399.5901 | 305.9861 | 308.0976
4099.6135 | 399.5068 | 306.0126 | 308.4132
4100.6135 | 399.492 | 306.0173 | 308.5659
4101.6135 | 399.4295 | 305.9693 | 308.089
4102.6135 | 399.5605 | 305.9308 | 307.6484
4103.6135 | 399.6478 | 305.849 | 307.5742
4104.6135 | 399.5993 | 305.8087 | 307.4837
4105.6135 | 399.6083 | 305.7486 | 307.4446
4106.6135 | 399.5114 | 305.7168 | 307.1867
4107.6135 | 399.5334 | 305.6884 | 307.0121
4108.6135 | 399.5224 | 305.6471 | 306.8712
4109.6135 | 399.3877 | 305.5861 | 306.7606
4110.6135 | 399.3208 | 305.5424 | 307.1277
4111.6135 | 399.4916 | 305.4965 | 307.0434
4112.6135 | 399.435 | 305.4613 | 307.0338
4113.6135 | 399.4253 | 305.4193 | 307.1102
4114.6135 | 399.4102 | 305.3939 | 306.8858
4115.6135 | 399.3918 | 305.3394 | 306.6141
4116.6135 | 399.5456 | 305.2743 | 306.3474
4117.6135 | 399.6416 | 305.2397 | 306.2749
4118.6135 | 399.6853 | 305.2018 | 306.2551
4119.6135 | 399.7386 | 305.1961 | 306.2479
4120.6135 | 399.7291 | 305.2135 | 306.1665
4121.6135 | 399.6472 | 305.2275 | 306.2228
4122.6135 | 399.6973 | 305.2294 | 306.1273
4123.6135 | 399.621 | 305.2497 | 305.9765
4124.6135 | 399.5692 | 305.2896 | 305.6643
4125.6135 | 399.6214 | 305.3236 | 305.5731
4126.6135 | 399.5841 | 305.3438 | 305.9966
4127.6135 | 399.6566 | 305.3685 | 306.4282
4128.6135 | 399.7567 | 305.4085 | 306.7754
4129.6135 | 399.7708 | 305.4837 | 306.9175
4130.6135 | 399.6741 | 305.5309 | 307.0297
4131.6135 | 399.7162 | 305.5579 | 306.8293
4132.6135 | 399.6675 | 305.5764 | 306.6623
4133.6135 | 399.8451 | 305.5708 | 306.6193
4134.6135 | 399.749 | 305.5775 | 307.0893
4135.6135 | 399.7201 | 305.6086 | 307.2161
4136.6135 | 399.8501 | 305.6482 | 307.3055
4137.6135 | 399.9674 | 305.6964 | 307.6092
4138.6135 | 400.0223 | 305.7291 | 307.1991
4139.6135 | 400.0858 | 305.7538 | 306.9161
4140.6135 | 400.0549 | 305.7708 | 306.8452
4141.6135 | 399.9498 | 305.793 | 307.2969
4142.6135 | 399.8702 | 305.8631 | 307.4567
4143.6135 | 399.7498 | 305.9352 | 307.1796
4144.6135 | 399.8095 | 305.991 | 306.4702
4145.6135 | 399.7536 | 306.0464 | 306.1547
4146.6135 | 399.7493 | 306.0924 | 306.1116
4147.6135 | 399.613 | 306.1521 | 306.0375
4148.6135 | 399.4608 | 306.2378 | 305.7617
4149.6135 | 399.4218 | 306.3083 | 305.1533
4150.6135 | 399.4809 | 306.3579 | 304.8187
4151.6135 | 399.4777 | 306.4099 | 304.6034
4152.6135 | 399.4416 | 306.46 | 304.8318
4153.6135 | 399.4166 | 306.4587 | 305.2178
4154.6135 | 399.3496 | 306.4706 | 305.6559
4155.6135 | 399.2714 | 306.4473 | 305.3387
4156.6135 | 399.0607 | 306.3939 | 304.934
4157.6135 | 399.0362 | 306.3236 | 304.8837
4158.6135 | 399.1136 | 306.2436 | 304.9279
4159.6135 | 399.1987 | 306.2003 | 305.3654
4160.6135 | 399.2498 | 306.1703 | 305.9683
4161.6135 | 399.2533 | 306.1725 | 305.8582
4162.6135 | 399.0881 | 306.2039 | 305.5424
4163.6135 | 399.0152 | 306.2173 | 305.1814
4164.6135 | 398.9448 | 306.2329 | 304.7775
4165.6135 | 398.7994 | 306.2466 | 305.1104
4166.6135 | 398.7256 | 306.2815 | 305.2146
4167.6135 | 398.7502 | 306.3069 | 305.0855
4168.6135 | 398.9004 | 306.2796 | 305.3173
4169.6135 | 399.0738 | 306.2584 | 305.5553
4170.6135 | 399.246 | 306.2605 | 305.854
4171.6135 | 399.126 | 306.2496 | 306.191
4172.6135 | 399.1363 | 306.2341 | 306.4003
4173.6135 | 399.0814 | 306.213 | 306.7542
4174.6135 | 399.0894 | 306.1723 | 306.8586
4175.6135 | 399.0152 | 306.1524 | 307.1206
4176.6135 | 399.1781 | 306.0888 | 307.0761
4177.6135 | 399.1975 | 306.0569 | 306.962
4178.6135 | 399.1003 | 306.0302 | 307.4246
4179.6135 | 398.9406 | 305.9618 | 307.1254
4180.6135 | 398.9137 | 305.9244 | 307.0111
4181.6135 | 398.9206 | 305.8727 | 307.1158
4182.6135 | 399.0035 | 305.876 | 307.3473
4183.6135 | 399.1041 | 305.8483 | 307.4404
4184.6135 | 399.1414 | 305.8284 | 307.3167
4185.6135 | 399.1996 | 305.8167 | 307.4862
4186.6135 | 399.2784 | 305.824 | 307.8318
4187.6135 | 399.235 | 305.8455 | 308.0685
4188.6135 | 399.359 | 305.8774 | 308.0575
4189.6135 | 399.369 | 305.8787 | 308.3891
4190.6135 | 399.3376 | 305.9111 | 308.7417
4191.6135 | 399.3843 | 305.9351 | 308.7107
4192.6135 | 399.4176 | 305.9482 | 308.7688
4193.6135 | 399.4766 | 305.9965 | 308.9555
4194.6135 | 399.4912 | 306.001 | 309.0529
4195.6135 | 399.5241 | 306.0128 | 309.022
4196.6135 | 399.7279 | 305.9929 | 308.973
4197.6135 | 399.7817 | 305.9894 | 308.7471
4198.6135 | 399.8005 | 305.9698 | 308.5607
4199.6135 | 399.6173 | 305.9657 | 308.5157
4200.6135 | 399.6484 | 305.962 | 308.5811
4201.6135 | 399.5235 | 305.9047 | 308.7846
4202.6135 | 399.4233 | 305.8571 | 308.5275
4203.6135 | 399.3551 | 305.7754 | 308.6288
4204.6135 | 399.3639 | 305.7555 | 309.1206
4205.6135 | 399.4145 | 305.6938 | 309.6002
4206.6135 | 399.5861 | 305.6516 | 309.924
4207.6135 | 399.6931 | 305.5687 | 309.8815
4208.6135 | 399.8246 | 305.4955 | 309.9261
4209.6135 | 399.9942 | 305.4215 | 310.3532
4210.6135 | 400.0393 | 305.366 | 310.3524
4211.6135 | 400.0742 | 305.3322 | 310.1386
4212.6135 | 400.1257 | 305.3073 | 309.8877
4213.6135 | 399.9359 | 305.3209 | 309.5487
4214.6135 | 399.9225 | 305.3606 | 308.8401
4215.6135 | 399.941 | 305.4029 | 308.3113
4216.6135 | 399.9794 | 305.4484 | 308.2759
4217.6135 | 400.1025 | 305.5218 | 308.9252
4218.6135 | 400.2415 | 305.5647 | 309.469
4219.6135 | 400.1397 | 305.5891 | 309.4075
4220.6135 | 400.1048 | 305.6075 | 309.2625
4221.6135 | 400.2099 | 305.6309 | 309.4424
4222.6135 | 400.3099 | 305.6587 | 309.279
4223.6135 | 400.3355 | 305.6833 | 309.2999
4224.6135 | 400.3091 | 305.7191 | 308.7125
4225.6135 | 400.2875 | 305.7589 | 308.4238
4226.6135 | 400.2648 | 305.8046 | 308.1675
4227.6135 | 400.2981 | 305.8039 | 308.1501
4228.6135 | 400.3057 | 305.8116 | 307.8074
4229.6135 | 400.2627 | 305.8114 | 307.6815
4230.6135 | 400.311 | 305.8214 | 306.991
4231.6135 | 400.4434 | 305.8328 | 306.6098
4232.6135 | 400.541 | 305.8648 | 306.7541
4233.6135 | 400.5959 | 305.8898 | 307.1877
4234.6135 | 400.6536 | 305.8839 | 307.4651
4235.6135 | 400.6408 | 305.8812 | 307.689
4236.6135 | 400.5902 | 305.8843 | 308.1893
4237.6135 | 400.645 | 305.9088 | 308.7061
4238.6135 | 400.6334 | 305.8917 | 309.1577
4239.6135 | 400.5616 | 305.8763 | 309.1984
4240.6135 | 400.3971 | 305.8413 | 309.1379
4241.6135 | 400.341 | 305.7917 | 308.9131
4242.6135 | 400.2518 | 305.7724 | 308.7414
4243.6135 | 400.2321 | 305.7631 | 308.7564
4244.6135 | 400.1122 | 305.7689 | 308.9231
4245.6135 | 400.1805 | 305.7718 | 309.0215
4246.6135 | 400.1816 | 305.7964 | 309.3678
4247.6135 | 400.1663 | 305.7978 | 309.5024
4248.6135 | 400.1759 | 305.8054 | 309.0486
4249.6135 | 400.1211 | 305.8357 | 308.5002
4250.6135 | 400.2355 | 305.8648 | 308.973
4251.6135 | 400.2947 | 305.9052 | 309.1564
4252.6135 | 400.4681 | 305.9399 | 309.1493
4253.6135 | 400.4753 | 305.9695 | 309.1756
4254.6135 | 400.5352 | 305.9736 | 308.6228
4255.6135 | 400.556 | 305.9596 | 307.8498
4256.6135 | 400.5521 | 305.9528 | 307.4062
4257.6135 | 400.4384 | 305.9893 | 307.7535
4258.6135 | 400.3703 | 306.0277 | 308.0937
4259.6135 | 400.4881 | 306.0525 | 308.1584
4260.6135 | 400.4364 | 306.0369 | 308.0919
4261.6135 | 400.4683 | 306.066 | 308.325
4262.6135 | 400.5321 | 306.0873 | 308.5421
4263.6135 | 400.5995 | 306.0727 | 308.2424
4264.6135 | 400.6156 | 306.0519 | 307.7504
4265.6135 | 400.631 | 306.0336 | 307.362
4266.6135 | 400.5938 | 306.0321 | 307.1452
4267.6135 | 400.6331 | 306.0309 | 307.0698
4268.6135 | 400.6323 | 306.0266 | 307.0123
4269.6135 | 400.653 | 306.04 | 306.7001
4270.6135 | 400.638 | 306.0673 | 306.5348
4271.6135 | 400.5643 | 306.0889 | 306.8581
4272.6135 | 400.5318 | 306.1417 | 307.457
4273.6135 | 400.4955 | 306.1648 | 307.572
4274.6135 | 400.3508 | 306.1612 | 307.6067
4275.6135 | 400.4187 | 306.1162 | 307.8202
4276.6135 | 400.5181 | 306.0513 | 308.207
4277.6135 | 400.5511 | 305.9745 | 308.4532
4278.6135 | 400.5509 | 305.9197 | 308.3286
4279.6135 | 400.4612 | 305.9058 | 308.3809
4280.6135 | 400.332 | 305.9161 | 308.7581
4281.6135 | 400.232 | 305.9387 | 308.9083
4282.6135 | 400.1507 | 305.9312 | 308.471
4283.6135 | 400.1131 | 305.9402 | 308.0035
4284.6135 | 400.3194 | 305.9317 | 307.9985
4285.6135 | 400.4357 | 305.9012 | 308.3997
4286.6135 | 400.5135 | 305.8909 | 308.4926
4287.6135 | 400.5671 | 305.9376 | 308.3576
4288.6135 | 400.5132 | 305.94 | 307.7377
4289.6135 | 400.5722 | 305.9346 | 307.3303
4290.6135 | 400.4035 | 305.9612 | 307.0739
4291.6135 | 400.3007 | 305.9775 | 307.1866
4292.6135 | 400.3944 | 305.9782 | 307.3716
4293.6135 | 400.4386 | 305.9722 | 307.4939
4294.6135 | 400.3637 | 305.9952 | 307.3306
4295.6135 | 400.3331 | 306.0004 | 307.4705
4296.6135 | 400.1637 | 305.9699 | 307.5417
4297.6135 | 400.2446 | 305.9434 | 306.997
4298.6135 | 400.2214 | 305.8952 | 306.5154
4299.6135 | 400.1078 | 305.9104 | 305.7923
4300.6135 | 400.0445 | 305.889 | 305.5671
4301.6135 | 400.0839 | 305.8652 | 305.3008
4302.6135 | 400.012 | 305.867 | 305.1884
4303.6135 | 400.0968 | 305.8807 | 305.5428
4304.6135 | 400.1322 | 305.9116 | 305.9218
4305.6135 | 399.9965 | 305.9247 | 305.612
4306.6135 | 399.8999 | 305.9622 | 305.1109
4307.6135 | 399.8848 | 305.9777 | 304.8732
4308.6135 | 399.88 | 306.0471 | 304.4837
4309.6135 | 399.9562 | 306.1262 | 304.5277
4310.6135 | 400.0085 | 306.1824 | 304.6707
4311.6135 | 400.1505 | 306.2411 | 304.44
4312.6135 | 400.1881 | 306.2727 | 304.3901
4313.6135 | 400.1748 | 306.2626 | 304.3174
4314.6135 | 400.125 | 306.2777 | 304.3661
4315.6135 | 399.9773 | 306.2609 | 304.5161
4316.6135 | 399.8682 | 306.2442 | 304.8936
4317.6135 | 399.8913 | 306.252 | 304.8049
4318.6135 | 399.8785 | 306.2628 | 304.3948
4319.6135 | 399.8066 | 306.27 | 304.4603
4320.6135 | 399.8486 | 306.263 | 304.9896
4321.6135 | 399.9408 | 306.2453 | 305.5391
4322.6135 | 400.0547 | 306.2179 | 306.1062
4323.6135 | 400.1346 | 306.1969 | 306.6499
4324.6135 | 400.2262 | 306.178 | 307.0089
4325.6135 | 400.2304 | 306.1553 | 307.4153
4326.6135 | 400.1142 | 306.0987 | 307.7258
4327.6135 | 400.2076 | 306.0482 | 307.9702
4328.6135 | 400.3584 | 306.0316 | 308.3627
4329.6135 | 400.2597 | 305.9907 | 308.8216
4330.6135 | 400.1238 | 305.977 | 308.8212
4331.6135 | 400.2557 | 305.925 | 308.3895
4332.6135 | 400.3337 | 305.8895 | 308.0274
4333.6135 | 400.2479 | 305.884 | 307.8369
4334.6135 | 400.224 | 305.876 | 307.9574
4335.6135 | 400.092 | 305.9089 | 307.5251
4336.6135 | 400.1022 | 305.9332 | 307.6751
4337.6135 | 400.0076 | 305.9523 | 307.9742
4338.6135 | 400.114 | 305.9265 | 307.9244
4339.6135 | 400.1732 | 305.8828 | 307.4211
4340.6135 | 400.162 | 305.8677 | 307.0605
4341.6135 | 400.1522 | 305.8923 | 306.8153
4342.6135 | 400.1802 | 305.9031 | 306.6158
4343.6135 | 400.141 | 305.92 | 306.4626
4344.6135 | 400.1132 | 305.9403 | 306.6018
4345.6135 | 400.1431 | 305.9592 | 306.4018
4346.6135 | 400.2385 | 305.9978 | 306.3872
4347.6135 | 400.3068 | 306.0095 | 306.4646
4348.6135 | 400.4508 | 306.0391 | 306.8232
4349.6135 | 400.4146 | 306.062 | 307.3115
4350.6135 | 400.3886 | 306.0684 | 307.7988
4351.6135 | 400.4539 | 306.0972 | 307.4773
4352.6135 | 400.395 | 306.0792 | 307.4464
4353.6135 | 400.3622 | 306.0716 | 307.7047
4354.6135 | 400.2724 | 306.0541 | 308.0352
4355.6135 | 400.2219 | 306.0312 | 308.1704
4356.6135 | 400.1527 | 306.0111 | 307.7367
4357.6135 | 400.058 | 306.034 | 307.7047
4358.6135 | 399.9785 | 306.0239 | 307.2746
4359.6135 | 400.0004 | 306.0522 | 306.992
4360.6135 | 399.9328 | 306.0662 | 306.7596
4361.6135 | 399.8127 | 306.0755 | 306.2851
4362.6135 | 399.7255 | 306.0992 | 306.1267
4363.6135 | 399.6731 | 306.1388 | 306.0418
4364.6135 | 399.7413 | 306.2088 | 305.7381
4365.6135 | 399.819 | 306.2662 | 305.6585
4366.6135 | 399.9505 | 306.3067 | 305.7226
4367.6135 | 399.9345 | 306.3133 | 305.8255
4368.6135 | 399.9092 | 306.2995 | 305.9603
4369.6135 | 399.8241 | 306.2964 | 305.7957
4370.6135 | 399.8633 | 306.283 | 305.5482
4371.6135 | 399.9014 | 306.2671 | 305.5002
4372.6135 | 399.8513 | 306.2605 | 305.5303
4373.6135 | 399.7647 | 306.2412 | 305.6079
4374.6135 | 399.7739 | 306.2306 | 305.9019
4375.6135 | 399.7406 | 306.2253 | 306.0206
4376.6135 | 399.7848 | 306.1903 | 305.8917
4377.6135 | 399.8581 | 306.1379 | 305.938
4378.6135 | 399.7935 | 306.0949 | 306.1945
4379.6135 | 399.8303 | 306.0442 | 306.4159
4380.6135 | 399.794 | 306.0218 | 306.4153
4381.6135 | 399.8287 | 305.9906 | 306.3682
4382.6135 | 399.7744 | 305.9432 | 306.4254
4383.6135 | 399.8999 | 305.9003 | 306.3298
4384.6135 | 399.8383 | 305.9003 | 306.1044
4385.6135 | 399.743 | 305.9177 | 305.637
4386.6135 | 399.7287 | 305.95 | 305.4525
4387.6135 | 399.7511 | 306.002 | 305.4202
4388.6135 | 399.7129 | 306.0712 | 305.5822
4389.6135 | 399.7506 | 306.1095 | 305.7606
4390.6135 | 399.7714 | 306.1221 | 305.9426
4391.6135 | 399.8036 | 306.1167 | 306.2583
4392.6135 | 399.7937 | 306.097 | 305.9504
4393.6135 | 399.7821 | 306.0788 | 305.9752
4394.6135 | 399.9608 | 306.0822 | 306.106
4395.6135 | 400.0347 | 306.0993 | 306.0209
4396.6135 | 400.0208 | 306.1242 | 305.7745
4397.6135 | 400.0867 | 306.109 | 305.7881
4398.6135 | 400.3184 | 306.109 | 305.7835
4399.6135 | 400.4389 | 306.1283 | 305.8538
4400.6135 | 400.4836 | 306.1509 | 305.9162
4401.6135 | 400.4715 | 306.1508 | 306.0912
4402.6135 | 400.6299 | 306.151 | 306.1243
4403.6135 | 400.735 | 306.1536 | 306.4068
4404.6135 | 400.7357 | 306.1606 | 306.2239
4405.6135 | 400.544 | 306.1712 | 306.252
4406.6135 | 400.4653 | 306.1648 | 306.495
4407.6135 | 400.4741 | 306.1786 | 306.7122
4408.6135 | 400.4519 | 306.1717 | 306.6591
4409.6135 | 400.3695 | 306.1747 | 306.8919
4410.6135 | 400.4121 | 306.1787 | 306.8473
4411.6135 | 400.4257 | 306.1657 | 306.9255
4412.6135 | 400.5877 | 306.1691 | 307.0055
4413.6135 | 400.6465 | 306.1677 | 307.2252
4414.6135 | 400.6293 | 306.1637 | 307.333
4415.6135 | 400.659 | 306.1499 | 307.3559
4416.6135 | 400.6259 | 306.1585 | 307.3892
4417.6135 | 400.7813 | 306.1664 | 307.557
4418.6135 | 400.6919 | 306.1614 | 307.4297
4419.6135 | 400.6848 | 306.1325 | 307.2994
4420.6135 | 400.5521 | 306.1315 | 307.2761
4421.6135 | 400.2943 | 306.0999 | 307.4269
4422.6135 | 400.2155 | 306.1112 | 307.3673
4423.6135 | 400.1498 | 306.1184 | 307.8421
4424.6135 | 400.2364 | 306.1393 | 307.9532
4425.6135 | 400.1289 | 306.1532 | 308.0346
4426.6135 | 400.0249 | 306.1702 | 308.209
4427.6135 | 400.0252 | 306.1822 | 308.0192
4428.6135 | 400.1031 | 306.1771 | 307.9525
4429.6135 | 400.2377 | 306.1392 | 307.9295
4430.6135 | 400.2145 | 306.1489 | 307.6743
4431.6135 | 400.139 | 306.1628 | 307.4734
4432.6135 | 400.1426 | 306.1667 | 307.5068
4433.6135 | 399.9724 | 306.1734 | 307.7066
4434.6135 | 399.9311 | 306.2026 | 307.8671
4435.6135 | 400.0066 | 306.2338 | 308.4324
4436.6135 | 400.0859 | 306.2665 | 309.1074
4437.6135 | 400.1217 | 306.2723 | 309.324
4438.6135 | 399.8679 | 306.2498 | 308.9955
4439.6135 | 399.8339 | 306.2326 | 308.8417
4440.6135 | 399.8426 | 306.2218 | 308.9833
4441.6135 | 399.8508 | 306.2328 | 309.1964
4442.6135 | 399.9533 | 306.2149 | 309.2932
4443.6135 | 400.0397 | 306.1855 | 309.5225
4444.6135 | 400.0487 | 306.1462 | 309.482
4445.6135 | 400.0981 | 306.1401 | 309.2687
4446.6135 | 400.1014 | 306.1095 | 308.7969
4447.6135 | 400.0007 | 306.084 | 308.6044
4448.6135 | 400.1587 | 306.0984 | 308.876
4449.6135 | 400.0786 | 306.1105 | 308.8331
4450.6135 | 400.1016 | 306.1104 | 308.8885
4451.6135 | 400.1979 | 306.0846 | 308.7335
4452.6135 | 400.28 | 306.0751 | 309.0778
4453.6135 | 400.3377 | 306.0537 | 309.4325
4454.6135 | 400.2431 | 306.0548 | 309.429
4455.6135 | 400.1583 | 306.0761 | 309.0749
4456.6135 | 400.1165 | 306.0775 | 308.8739
4457.6135 | 400.0177 | 306.0681 | 308.8664
4458.6135 | 400.11 | 306.0509 | 308.7349
4459.6135 | 400.0256 | 306.0425 | 308.9982
4460.6135 | 400.0423 | 306.0452 | 309.2487
4461.6135 | 400.0547 | 306.044 | 309.5171
4462.6135 | 400.0309 | 306.0526 | 309.5076
4463.6135 | 399.9702 | 306.0923 | 309.5528
4464.6135 | 400.0467 | 306.0713 | 309.6192
4465.6135 | 400.1502 | 306.1136 | 309.7813
4466.6135 | 400.2258 | 306.1141 | 309.77
4467.6135 | 400.1969 | 306.1248 | 309.9973
4468.6135 | 400.1485 | 306.1294 | 309.6479
4469.6135 | 400.0384 | 306.1469 | 309.3256
4470.6135 | 400.1747 | 306.1456 | 308.8011
4471.6135 | 400.1418 | 306.1614 | 308.2517
4472.6135 | 399.9644 | 306.16 | 308.3808
4473.6135 | 399.9846 | 306.1706 | 308.525
4474.6135 | 399.885 | 306.1608 | 308.9874
4475.6135 | 399.938 | 306.1707 | 309.1417
4476.6135 | 399.9171 | 306.1784 | 308.8642
4477.6135 | 399.9928 | 306.1657 | 308.6587
4478.6135 | 400.0288 | 306.1836 | 308.7135
4479.6135 | 400.0283 | 306.2211 | 308.7194
4480.6135 | 400.0305 | 306.2525 | 308.9315
4481.6135 | 400.0267 | 306.2846 | 309.1994
4482.6135 | 399.9185 | 306.3067 | 309.3713
4483.6135 | 399.8655 | 306.2961 | 309.4855
4484.6135 | 399.9501 | 306.3322 | 309.5417
4485.6135 | 399.8814 | 306.3282 | 309.6728
4486.6135 | 399.8441 | 306.3237 | 309.9222
4487.6135 | 399.8167 | 306.3101 | 310.0175
4488.6135 | 399.8179 | 306.2976 | 309.8175
4489.6135 | 399.906 | 306.337 | 309.992
4490.6135 | 399.9565 | 306.3332 | 309.8861
4491.6135 | 399.8537 | 306.3519 | 309.8835
4492.6135 | 399.8343 | 306.3433 | 310.1346
4493.6135 | 399.9122 | 306.3449 | 310.3069
4494.6135 | 399.9869 | 306.3426 | 310.3587
4495.6135 | 399.976 | 306.3554 | 309.9375
4496.6135 | 399.8608 | 306.3973 | 309.858
4497.6135 | 399.6967 | 306.4478 | 309.9971
4498.6135 | 399.7571 | 306.4995 | 310.3831
4499.6135 | 399.8335 | 306.5166 | 310.4362
4500.6135 | 399.9468 | 306.5326 | 310.476
4501.6135 | 400.0221 | 306.5261 | 310.7068
4502.6135 | 400.0082 | 306.5077 | 310.8195
4503.6135 | 399.9816 | 306.4627 | 310.3386
4504.6135 | 400.2216 | 306.4354 | 309.808
4505.6135 | 400.4328 | 306.4404 | 309.9547
4506.6135 | 400.5776 | 306.4224 | 310.1893
4507.6135 | 400.8086 | 306.393 | 310.1907
4508.6135 | 401.0151 | 306.3642 | 310.2284
4509.6135 | 401.079 | 306.3399 | 310.5161
4510.6135 | 401.0557 | 306.3007 | 310.3111
4511.6135 | 401.0476 | 306.2839 | 310.1765
4512.6135 | 401.074 | 306.2643 | 310.2151
4513.6135 | 401.0663 | 306.2505 | 310.0385
4514.6135 | 401.1119 | 306.256 | 310.1059
4515.6135 | 401.1289 | 306.2518 | 309.8886
4516.6135 | 401.0802 | 306.2631 | 309.6168
4517.6135 | 400.9384 | 306.2541 | 309.6947
4518.6135 | 400.9629 | 306.2567 | 309.9052
4519.6135 | 401.0694 | 306.2528 | 309.973
4520.6135 | 401.1216 | 306.2658 | 309.8617
4521.6135 | 401.009 | 306.2941 | 310.1004
4522.6135 | 401.0603 | 306.3204 | 310.0443
4523.6135 | 401.0925 | 306.3674 | 309.6983
4524.6135 | 401.0656 | 306.3946 | 310.0953
4525.6135 | 401.0284 | 306.439 | 310.0857
4526.6135 | 400.9298 | 306.4619 | 309.9451
4527.6135 | 400.7851 | 306.5116 | 310.0248
4528.6135 | 400.6253 | 306.5397 | 310.2223
4529.6135 | 400.4513 | 306.5659 | 310.0854
4530.6135 | 400.4441 | 306.6169 | 310.1637
4531.6135 | 400.4239 | 306.6296 | 310.2755
4532.6135 | 400.4264 | 306.6533 | 309.9805
4533.6135 | 400.3344 | 306.6663 | 309.3458
4534.6135 | 400.3098 | 306.7157 | 309.1065
4535.6135 | 400.2437 | 306.7134 | 308.7959
4536.6135 | 400.1488 | 306.7099 | 308.5824
4537.6135 | 400.1771 | 306.7133 | 308.3384
4538.6135 | 400.1844 | 306.7166 | 308.4247
4539.6135 | 400.2484 | 306.7658 | 308.2423
4540.6135 | 400.2297 | 306.8249 | 308.4597
4541.6135 | 400.1374 | 306.8866 | 308.44
4542.6135 | 400.1222 | 306.9527 | 308.1588
4543.6135 | 400.1205 | 307.031 | 308.146
4544.6135 | 400.1539 | 307.1154 | 307.8039
4545.6135 | 400.1695 | 307.1937 | 307.7075
4546.6135 | 400.0944 | 307.2975 | 307.7333
4547.6135 | 399.9374 | 307.3634 | 307.9242
4548.6135 | 399.8173 | 307.435 | 308.1099
4549.6135 | 399.8423 | 307.4676 | 308.2503
4550.6135 | 399.9268 | 307.4686 | 308.1901
4551.6135 | 399.8223 | 307.5143 | 308.1054
4552.6135 | 399.7997 | 307.5222 | 308.3086
4553.6135 | 399.9951 | 307.532 | 308.6319
4554.6135 | 400.0576 | 307.5359 | 308.8835
4555.6135 | 400.0736 | 307.5157 | 308.7409
4556.6135 | 400.1775 | 307.4828 | 308.6814
4557.6135 | 400.2979 | 307.443 | 309.0017
4558.6135 | 400.3302 | 307.446 | 308.8964
4559.6135 | 400.4383 | 307.4585 | 308.6847
4560.6135 | 400.3891 | 307.4356 | 308.2891
4561.6135 | 400.3688 | 307.3984 | 307.9251
4562.6135 | 400.2971 | 307.3994 | 307.9917
4563.6135 | 400.2405 | 307.4119 | 308.0166
4564.6135 | 400.3147 | 307.439 | 307.56
4565.6135 | 400.3718 | 307.4396 | 307.2961
4566.6135 | 400.4154 | 307.4118 | 307.4093
4567.6135 | 400.4103 | 307.3346 | 307.6158
4568.6135 | 400.5144 | 307.2836 | 307.7646
4569.6135 | 400.4406 | 307.2602 | 307.9271
4570.6135 | 400.538 | 307.2456 | 307.9283
4571.6135 | 400.703 | 307.243 | 307.6939
4572.6135 | 400.7913 | 307.216 | 307.4481
4573.6135 | 400.7715 | 307.1687 | 307.3246
4574.6135 | 400.6368 | 307.0871 | 307.3135
4575.6135 | 400.6121 | 307.0018 | 307.6485
4576.6135 | 400.4917 | 306.9494 | 307.679
4577.6135 | 400.4273 | 306.9027 | 307.8877
4578.6135 | 400.3292 | 306.8852 | 308.2963
4579.6135 | 400.2035 | 306.8594 | 308.2315
4580.6135 | 399.9966 | 306.8283 | 308.4578
4581.6135 | 400.0157 | 306.8194 | 308.6767
4582.6135 | 400.0534 | 306.7904 | 308.769
4583.6135 | 400.0023 | 306.7955 | 308.5259
4584.6135 | 399.8349 | 306.7697 | 308.3789
4585.6135 | 399.7871 | 306.7612 | 308.0213
4586.6135 | 399.6454 | 306.752 | 307.6949
4587.6135 | 399.5996 | 306.7905 | 307.4076
4588.6135 | 399.5854 | 306.7918 | 307.5719
4589.6135 | 399.5501 | 306.7305 | 307.4952
4590.6135 | 399.4894 | 306.6479 | 306.9319
4591.6135 | 399.5076 | 306.6018 | 306.5506
4592.6135 | 399.4701 | 306.5671 | 306.9285
4593.6135 | 399.4885 | 306.5515 | 306.9021
4594.6135 | 399.5004 | 306.5155 | 306.7391
4595.6135 | 399.4893 | 306.5085 | 306.7093
4596.6135 | 399.5311 | 306.5175 | 306.9804
4597.6135 | 399.6313 | 306.5193 | 306.759
4598.6135 | 399.5816 | 306.5087 | 306.544
4599.6135 | 399.6623 | 306.4715 | 306.4786
4600.6135 | 399.707 | 306.4265 | 306.4115
4601.6135 | 399.9251 | 306.3838 | 306.3064
4602.6135 | 400.095 | 306.3938 | 306.2101
4603.6135 | 400.1858 | 306.3823 | 306.2031
4604.6135 | 400.2952 | 306.3763 | 306.0219
4605.6135 | 400.3587 | 306.3328 | 306.0117
4606.6135 | 400.4296 | 306.3126 | 305.8496
4607.6135 | 400.4787 | 306.2668 | 306.12
4608.6135 | 400.5226 | 306.2117 | 306.346
4609.6135 | 400.5987 | 306.167 | 306.5942
4610.6135 | 400.6479 | 306.1259 | 306.659
4611.6135 | 400.8021 | 306.0701 | 306.172
4612.6135 | 400.9466 | 306.0252 | 305.6925
4613.6135 | 400.9449 | 306.0577 | 305.7496
4614.6135 | 400.967 | 306.0743 | 305.7748
4615.6135 | 400.9958 | 306.1069 | 305.6913
4616.6135 | 401.0625 | 306.1401 | 305.818
4617.6135 | 401.1052 | 306.1623 | 306.2153
4618.6135 | 401.076 | 306.1951 | 306.8329
4619.6135 | 401.002 | 306.2293 | 307.5056
4620.6135 | 400.9033 | 306.2521 | 307.7141
4621.6135 | 400.7782 | 306.2773 | 307.396
4622.6135 | 400.71 | 306.3004 | 307.4189
4623.6135 | 400.6313 | 306.3 | 307.2248
4624.6135 | 400.7465 | 306.297 | 306.5197
4625.6135 | 400.8899 | 306.3111 | 306.6364
4626.6135 | 400.865 | 306.3373 | 306.4769
4627.6135 | 400.7444 | 306.3654 | 306.2218
4628.6135 | 400.6692 | 306.4064 | 305.7773
4629.6135 | 400.6751 | 306.4595 | 305.0417
4630.6135 | 400.4493 | 306.5005 | 305.2464
4631.6135 | 400.5345 | 306.5124 | 305.3999
4632.6135 | 400.5435 | 306.5087 | 305.3102
4633.6135 | 400.4913 | 306.4882 | 305.5199
4634.6135 | 400.4105 | 306.4556 | 305.7749
4635.6135 | 400.3267 | 306.427 | 305.8498
4636.6135 | 400.2496 | 306.4145 | 306.189
4637.6135 | 400.3741 | 306.4003 | 306.6549
4638.6135 | 400.3308 | 306.4082 | 307.0361
4639.6135 | 400.3053 | 306.4101 | 307.3392
4640.6135 | 400.2644 | 306.3742 | 307.5614
4641.6135 | 400.1683 | 306.3426 | 307.7118
4642.6135 | 400.0223 | 306.2865 | 308.0216
4643.6135 | 400.0778 | 306.2233 | 307.9658
4644.6135 | 400.0849 | 306.1776 | 307.9229
4645.6135 | 400.0966 | 306.12 | 307.9119
4646.6135 | 400.1358 | 306.1117 | 307.5343
4647.6135 | 400.0948 | 306.1212 | 307.3353
4648.6135 | 400.0857 | 306.1571 | 307.4141
4649.6135 | 400.0138 | 306.192 | 307.6012
4650.6135 | 400.0563 | 306.1972 | 307.5937
4651.6135 | 399.9417 | 306.2048 | 307.4918
4652.6135 | 399.9066 | 306.2359 | 307.1551
4653.6135 | 399.7394 | 306.2584 | 306.6647
4654.6135 | 399.6511 | 306.2558 | 306.5574
4655.6135 | 399.7322 | 306.2602 | 306.2645
4656.6135 | 399.6833 | 306.2787 | 306.1441
4657.6135 | 399.6597 | 306.3052 | 306.1343
4658.6135 | 399.5742 | 306.3366 | 306.1763
4659.6135 | 399.673 | 306.3722 | 306.0068
4660.6135 | 399.6506 | 306.3705 | 305.9302
4661.6135 | 399.6002 | 306.3678 | 306.016
4662.6135 | 399.4474 | 306.3161 | 306.1489
4663.6135 | 399.3348 | 306.3043 | 306.155
4664.6135 | 399.409 | 306.2717 | 306.084
4665.6135 | 399.36 | 306.2408 | 306.1186
4666.6135 | 399.3085 | 306.2144 | 305.8647
4667.6135 | 399.5204 | 306.1972 | 305.9337
4668.6135 | 399.7114 | 306.224 | 305.7191
4669.6135 | 399.698 | 306.2488 | 306.0273
4670.6135 | 399.5475 | 306.2353 | 306.2771
4671.6135 | 399.5447 | 306.2085 | 306.174
4672.6135 | 399.748 | 306.1712 | 306.2246
4673.6135 | 399.702 | 306.1499 | 306.3336
4674.6135 | 399.7806 | 306.12 | 306.2033
4675.6135 | 399.9622 | 306.1399 | 306.0886
4676.6135 | 400.0809 | 306.1154 | 305.5172
4677.6135 | 400.1851 | 306.1376 | 304.7784
4678.6135 | 400.1948 | 306.1612 | 304.5962
4679.6135 | 400.3327 | 306.1855 | 304.2611
4680.6135 | 400.4513 | 306.2197 | 304.4098
4681.6135 | 400.4983 | 306.2175 | 304.9889
4682.6135 | 400.6487 | 306.2368 | 305.2369
4683.6135 | 400.6661 | 306.2642 | 305.4518
4684.6135 | 400.5329 | 306.268 | 305.6903
4685.6135 | 400.277 | 306.2666 | 306.2502
4686.6135 | 400.0923 | 306.2319 | 306.4913
4687.6135 | 399.9917 | 306.1901 | 306.6252
4688.6135 | 399.9179 | 306.1507 | 306.2309
4689.6135 | 399.9406 | 306.1219 | 306.2492
4690.6135 | 399.8623 | 306.103 | 306.497
4691.6135 | 399.8525 | 306.0904 | 306.525
4692.6135 | 399.9584 | 306.0906 | 306.6343
4693.6135 | 400.018 | 306.0761 | 306.885
4694.6135 | 399.9296 | 306.0616 | 307.1127
4695.6135 | 399.766 | 306.0426 | 307.6403
4696.6135 | 399.6706 | 306.0279 | 308.0156
4697.6135 | 399.698 | 306.0011 | 308.4426
4698.6135 | 399.7908 | 305.9523 | 308.6997
4699.6135 | 399.7278 | 305.9291 | 308.6563
4700.6135 | 399.753 | 305.9114 | 308.7942
4701.6135 | 399.6927 | 305.8915 | 308.971
4702.6135 | 399.4811 | 305.8758 | 308.7328
4703.6135 | 399.2779 | 305.8565 | 308.5218
4704.6135 | 399.2697 | 305.8322 | 308.2138
4705.6135 | 399.3683 | 305.8063 | 308.182
4706.6135 | 399.4525 | 305.7919 | 308.5203
4707.6135 | 399.4497 | 305.7462 | 308.6728
4708.6135 | 399.7047 | 305.6914 | 308.4826
4709.6135 | 399.8036 | 305.652 | 308.4644
4710.6135 | 399.6666 | 305.6222 | 308.6007
4711.6135 | 399.5683 | 305.6253 | 308.3333
4712.6135 | 399.5856 | 305.6454 | 308.243
4713.6135 | 399.6289 | 305.6739 | 308.2505
4714.6135 | 399.5732 | 305.7009 | 308.1324
4715.6135 | 399.5973 | 305.6986 | 307.7624
4716.6135 | 399.6777 | 305.734 | 307.209
4717.6135 | 399.7501 | 305.7868 | 306.9363
4718.6135 | 399.7158 | 305.8511 | 307.0689
4719.6135 | 399.6226 | 305.9168 | 307.0988
4720.6135 | 399.6462 | 305.9985 | 306.9862
4721.6135 | 399.6517 | 306.06 | 306.6467
4722.6135 | 399.609 | 306.1182 | 306.4922
4723.6135 | 399.6208 | 306.1372 | 306.0912
4724.6135 | 399.5391 | 306.1714 | 305.4908
4725.6135 | 399.5456 | 306.1869 | 305.4335
4726.6135 | 399.5698 | 306.1954 | 305.513
4727.6135 | 399.6667 | 306.2303 | 305.2072
4728.6135 | 399.6874 | 306.2795 | 305.163
4729.6135 | 399.7387 | 306.2966 | 305.1922
4730.6135 | 399.62 | 306.2698 | 305.4076
4731.6135 | 399.6474 | 306.22 | 305.6228
4732.6135 | 399.8273 | 306.171 | 305.6085
4733.6135 | 399.7844 | 306.136 | 305.4522
4734.6135 | 399.8545 | 306.1139 | 305.0793
4735.6135 | 399.8927 | 306.0942 | 305.1002
4736.6135 | 400.0769 | 306.0989 | 305.1123
4737.6135 | 400.1858 | 306.0958 | 305.2294
4738.6135 | 400.2543 | 306.0781 | 305.672
4739.6135 | 400.1701 | 306.078 | 305.8253
4740.6135 | 400.1506 | 306.0269 | 305.9287
4741.6135 | 400.1623 | 305.9813 | 306.26
4742.6135 | 400.2711 | 305.9306 | 306.7972
4743.6135 | 400.384 | 305.8995 | 307.1192
4744.6135 | 400.4221 | 305.8838 | 307.3674
4745.6135 | 400.4211 | 305.87 | 307.4813
4746.6135 | 400.3731 | 305.8782 | 307.7266
4747.6135 | 400.3711 | 305.8952 | 307.9954
4748.6135 | 400.4981 | 305.878 | 308.1265
4749.6135 | 400.4702 | 305.8975 | 307.9449
4750.6135 | 400.5467 | 305.8892 | 308.0466
4751.6135 | 400.5683 | 305.8654 | 308.004
4752.6135 | 400.546 | 305.8553 | 308.0031
4753.6135 | 400.4325 | 305.8352 | 308.1819
4754.6135 | 400.3779 | 305.8134 | 308.4836
4755.6135 | 400.4066 | 305.8198 | 309.0294
4756.6135 | 400.4927 | 305.8381 | 309.58
4757.6135 | 400.4923 | 305.8328 | 309.684
4758.6135 | 400.294 | 305.8336 | 309.8823
4759.6135 | 399.9745 | 305.7906 | 310.0335
4760.6135 | 399.7079 | 305.7616 | 310.1612
4761.6135 | 399.5601 | 305.7566 | 310.4378
4762.6135 | 399.7685 | 305.7245 | 310.7219
4763.6135 | 399.8056 | 305.6772 | 311.079
4764.6135 | 399.7141 | 305.6228 | 311.1729
4765.6135 | 399.7947 | 305.5742 | 311.1181
4766.6135 | 399.8791 | 305.5535 | 311.2371
4767.6135 | 399.9266 | 305.5147 | 311.4715
4768.6135 | 399.8901 | 305.5013 | 311.4983
4769.6135 | 399.9278 | 305.4729 | 311.2612
4770.6135 | 399.9672 | 305.4369 | 311.1137
4771.6135 | 400.0361 | 305.4144 | 311.0909
4772.6135 | 400.0445 | 305.4118 | 310.5316
4773.6135 | 400.1405 | 305.4167 | 310.0495
4774.6135 | 400.1203 | 305.3905 | 309.6959
4775.6135 | 400.2546 | 305.4191 | 309.7505
4776.6135 | 400.4493 | 305.437 | 309.7025
4777.6135 | 400.3759 | 305.4908 | 309.8012
4778.6135 | 400.4743 | 305.5461 | 310.045
4779.6135 | 400.3939 | 305.6122 | 310.0826
4780.6135 | 400.5755 | 305.6453 | 309.8847
4781.6135 | 400.5766 | 305.6835 | 309.8395
4782.6135 | 400.6738 | 305.7073 | 309.5222
4783.6135 | 400.7246 | 305.7328 | 309.7633
4784.6135 | 400.8396 | 305.7526 | 310.137
4785.6135 | 400.7718 | 305.79 | 310.4759
4786.6135 | 400.8996 | 305.8023 | 310.5971
4787.6135 | 401.1176 | 305.8218 | 310.8034
4788.6135 | 401.0972 | 305.8269 | 310.7714
4789.6135 | 400.8958 | 305.8453 | 310.5613
4790.6135 | 400.8111 | 305.8729 | 310.6806
4791.6135 | 400.8413 | 305.9235 | 310.6335
4792.6135 | 400.8041 | 305.9669 | 310.5665
4793.6135 | 400.7138 | 306.0289 | 310.9555
4794.6135 | 400.7077 | 306.085 | 310.9994
4795.6135 | 400.6256 | 306.1325 | 311.1117
4796.6135 | 400.6886 | 306.1441 | 310.9314
4797.6135 | 400.7736 | 306.166 | 310.2316
4798.6135 | 400.6476 | 306.1579 | 309.9678
4799.6135 | 400.5407 | 306.156 | 310.1331
4800.6135 | 400.582 | 306.1917 | 310.2091
4801.6135 | 400.554 | 306.22 | 310.3716
4802.6135 | 400.5543 | 306.2387 | 310.3795
4803.6135 | 400.4921 | 306.2475 | 310.2235
4804.6135 | 400.4356 | 306.2568 | 309.9108
4805.6135 | 400.2946 | 306.2467 | 309.6277
4806.6135 | 400.2121 | 306.2131 | 309.3942
4807.6135 | 400.1393 | 306.23 | 309.2953
4808.6135 | 399.9271 | 306.2444 | 309.7116
4809.6135 | 399.989 | 306.2634 | 309.7901
4810.6135 | 399.9787 | 306.2442 | 309.4625
4811.6135 | 399.9446 | 306.1904 | 309.4963
4812.6135 | 399.9388 | 306.1493 | 309.674
4813.6135 | 399.8973 | 306.1057 | 309.4764
4814.6135 | 399.8927 | 306.0797 | 309.5847
4815.6135 | 399.8941 | 306.0379 | 309.6412
4816.6135 | 399.856 | 306.0098 | 309.2895
4817.6135 | 399.8451 | 305.9918 | 309.2528
4818.6135 | 399.8403 | 305.9569 | 309.3934
4819.6135 | 399.7545 | 305.95 | 309.0192
4820.6135 | 399.7922 | 305.9506 | 308.8946
4821.6135 | 399.748 | 305.9723 | 308.8856
4822.6135 | 399.6444 | 306.009 | 308.3805
4823.6135 | 399.681 | 306.0513 | 307.8101
4824.6135 | 399.8119 | 306.0619 | 307.737
4825.6135 | 399.9137 | 306.0583 | 307.7166
4826.6135 | 399.7593 | 306.0882 | 307.7845
4827.6135 | 399.7636 | 306.1092 | 307.7479
4828.6135 | 399.7946 | 306.111 | 307.7542
4829.6135 | 399.8539 | 306.1379 | 307.7374
4830.6135 | 399.8371 | 306.1534 | 307.6174
4831.6135 | 399.8412 | 306.2112 | 307.5945
4832.6135 | 399.8962 | 306.274 | 307.3822
4833.6135 | 399.8958 | 306.3331 | 307.4964
4834.6135 | 399.8522 | 306.3685 | 307.0862
4835.6135 | 399.5935 | 306.4261 | 306.8536
4836.6135 | 399.6917 | 306.4564 | 306.9188
4837.6135 | 399.7802 | 306.4897 | 307.0974
4838.6135 | 399.7536 | 306.4699 | 307.2918
4839.6135 | 399.724 | 306.4564 | 307.4677
4840.6135 | 399.9044 | 306.4349 | 307.875
4841.6135 | 399.8898 | 306.3842 | 308.1597
4842.6135 | 399.9349 | 306.3151 | 308.1236
4843.6135 | 399.9017 | 306.2591 | 308.5712
4844.6135 | 399.98 | 306.206 | 308.9759
4845.6135 | 399.9735 | 306.1673 | 309.2496
4846.6135 | 399.9707 | 306.1402 | 308.9533
4847.6135 | 399.9661 | 306.1191 | 308.7884
4848.6135 | 400.0932 | 306.0844 | 308.6456
4849.6135 | 400.1056 | 306.069 | 308.9442
4850.6135 | 400.1584 | 306.0166 | 309.1642
4851.6135 | 400.1153 | 305.9732 | 309.1463
4852.6135 | 400.1336 | 305.9403 | 309.2554
4853.6135 | 400.1002 | 305.9093 | 308.8981
4854.6135 | 400.1708 | 305.883 | 308.7757
4855.6135 | 399.9692 | 305.8931 | 309.0938
4856.6135 | 399.8606 | 305.8941 | 309.282
4857.6135 | 399.8531 | 305.9039 | 309.5543
4858.6292 | 399.7401 | 305.9131 | 309.8693
4859.6135 | 399.762 | 305.8976 | 309.9075
4860.6135 | 399.6914 | 305.888 | 309.9027
4861.6135 | 399.6085 | 305.8889 | 310.0589
4862.6135 | 399.6737 | 305.8709 | 310.0889
4863.6135 | 399.7125 | 305.8779 | 310.235
4864.6135 | 399.6021 | 305.8851 | 310.3104
4865.6135 | 399.6567 | 305.9024 | 310.3534
4866.6135 | 399.7337 | 305.9053 | 310.7942
4867.6135 | 399.7593 | 305.9134 | 310.8948
4868.6135 | 399.6702 | 305.8827 | 310.7847
4869.6135 | 399.5652 | 305.8501 | 310.9709
4870.6135 | 399.7173 | 305.8295 | 310.9995
4871.6135 | 399.7702 | 305.844 | 311.0764
4872.6135 | 399.8816 | 305.8419 | 311.0373
4873.6135 | 399.8822 | 305.8463 | 311.3084
4874.6135 | 399.8556 | 305.8445 | 311.3775
4875.6135 | 399.8886 | 305.8767 | 311.0282
4876.6135 | 399.7814 | 305.9116 | 310.7982
4877.6135 | 399.6672 | 305.9394 | 310.6512
4878.6135 | 399.4188 | 305.9913 | 310.4602
4879.6135 | 399.1944 | 306.0343 | 310.0783
4880.6135 | 399.157 | 306.0656 | 309.4266
4881.6135 | 399.2643 | 306.0961 | 308.8014
4882.6135 | 399.2249 | 306.1195 | 308.8179
4883.6135 | 399.1262 | 306.1516 | 308.8978
4884.6135 | 399.1106 | 306.1687 | 308.689
4885.6135 | 399.0114 | 306.1785 | 308.75
4886.6135 | 399.1006 | 306.1983 | 308.7206
4887.6135 | 399.5898 | 306.2345 | 308.5311
4888.6135 | 400.8844 | 306.2875 | 308.9195
4889.6135 | 402.9202 | 306.3336 | 308.9752
4890.6135 | 405.4213 | 306.4112 | 309.3339
4891.6135 | 408.2806 | 306.5241 | 310.1943
4892.6135 | 411.288 | 306.6406 | 310.725
4893.6135 | 414.682 | 306.7648 | 311.2453
4894.6135 | 418.2374 | 306.9701 | 311.7605
4895.6135 | 421.8257 | 307.1347 | 312.1393
4896.6135 | 425.3449 | 307.3177 | 313.152
4897.6135 | 428.9094 | 307.4832 | 314.0584
4898.6135 | 432.2587 | 307.6742 | 314.8788
4899.6135 | 435.1856 | 307.9112 | 315.7823
4900.6135 | 437.9113 | 308.1799 | 316.3842
4901.6135 | 440.1078 | 308.427 | 317.0516
4902.6135 | 442.0751 | 308.6885 | 317.8252
4903.6135 | 443.7523 | 308.9735 | 318.5622
4904.6135 | 445.1082 | 309.2768 | 319.6905
4905.6135 | 445.9915 | 309.5826 | 320.7583
4906.6135 | 446.839 | 309.8929 | 321.7409
4907.6135 | 447.2683 | 310.2208 | 322.6994
4908.6135 | 447.7064 | 310.534 | 323.2023
4909.6135 | 447.9863 | 310.843 | 323.9031
4910.6135 | 448.2167 | 311.1561 | 324.5475
4911.6135 | 448.3842 | 311.4627 | 325.2263
4912.6135 | 448.3017 | 311.7722 | 325.7603
4913.6135 | 448.1512 | 312.0297 | 325.763
4914.6135 | 448.14 | 312.2722 | 325.8198
4915.6135 | 448.0329 | 312.5189 | 326.1545
4916.6135 | 448.0394 | 312.7744 | 326.3658
4917.6135 | 447.9418 | 313.0483 | 326.7355
4918.6135 | 447.789 | 313.2959 | 327.3506
4919.6135 | 447.4995 | 313.5701 | 328.1763
4920.6135 | 447.2292 | 313.7837 | 328.6947
4921.6135 | 447.1683 | 313.9921 | 329.3938
4922.6135 | 447.1688 | 314.1963 | 329.9014
4923.6135 | 446.9279 | 314.4134 | 330.2071
4924.6135 | 446.6912 | 314.6375 | 330.3368
4925.6135 | 446.6603 | 314.868 | 330.5067
4926.6135 | 446.6688 | 315.0722 | 330.9649
4927.6135 | 446.6172 | 315.2939 | 331.1617
4928.6135 | 446.4601 | 315.5505 | 331.2113
4929.6135 | 446.5332 | 315.8405 | 331.4958
4930.6135 | 446.5729 | 316.1259 | 331.6089
4931.6135 | 446.6482 | 316.3896 | 331.7491
4932.6135 | 446.7566 | 316.6708 | 331.9164
4933.6135 | 446.8893 | 316.9263 | 332.4929
4934.6135 | 446.8224 | 317.1587 | 332.4684
4935.6135 | 446.9024 | 317.4095 | 332.5642
4936.6135 | 447.0218 | 317.6675 | 332.6855
4937.6135 | 447.2623 | 317.9361 | 332.67
4938.6135 | 447.3222 | 318.2278 | 332.8326
4939.6135 | 447.6715 | 318.4882 | 333.0647
4940.6135 | 447.9496 | 318.7375 | 333.4573
4941.6135 | 447.9424 | 318.9698 | 333.7118
4942.6135 | 448.0067 | 319.2122 | 333.4937
4943.6135 | 448.1173 | 319.4424 | 333.3155
4944.6135 | 448.1101 | 319.6921 | 333.2829
4945.6135 | 448.2816 | 319.9378 | 333.8438
4946.6135 | 448.5725 | 320.1887 | 334.271
4947.6135 | 448.7209 | 320.4476 | 334.6668
4948.6135 | 448.7069 | 320.7262 | 334.8317
4949.6135 | 448.7062 | 320.9638 | 335.0004
4950.6135 | 448.9211 | 321.1728 | 334.9651
4951.6135 | 449.026 | 321.3991 | 335.0425
4952.6135 | 449.1473 | 321.5824 | 335.3322
4953.6135 | 449.4059 | 321.7608 | 335.7532
4954.6135 | 449.4078 | 321.9904 | 336.2226
4955.6135 | 449.5163 | 322.1949 | 336.6342
4956.6135 | 449.5461 | 322.3976 | 337.017
4957.6135 | 449.7278 | 322.6062 | 337.3741
4958.6135 | 449.8816 | 322.8168 | 337.5542
4959.6135 | 449.7762 | 323.0034 | 337.6171
4960.6135 | 449.8552 | 323.2098 | 338.0736
4961.6135 | 450.0057 | 323.4104 | 338.305
4962.6135 | 449.9508 | 323.614 | 338.4068
4963.6135 | 450.0873 | 323.8028 | 338.6093
4964.6135 | 450.2866 | 324.0048 | 338.7893
4965.6135 | 450.1643 | 324.2065 | 339.2347
4966.6135 | 450.1688 | 324.4074 | 339.2946
4967.6135 | 450.1637 | 324.6172 | 339.5725
4968.6135 | 450.2633 | 324.8229 | 339.8011
4969.6135 | 450.2209 | 325.0463 | 340.1017
4970.6135 | 450.2362 | 325.2609 | 340.837
4971.6135 | 450.347 | 325.4989 | 340.9866
4972.6135 | 450.433 | 325.7431 | 341.3113
4973.6135 | 450.5659 | 325.9609 | 341.135
4974.6135 | 450.6316 | 326.1865 | 341.3917
4975.6135 | 450.6254 | 326.4334 | 341.6755
4976.6135 | 450.6473 | 326.6506 | 341.8827
4977.6135 | 450.6162 | 326.8405 | 341.9697
4978.6135 | 450.5057 | 327.0403 | 341.7411
4979.6135 | 450.4263 | 327.257 | 341.8539
4980.6135 | 450.7175 | 327.4872 | 342.0657
4981.6135 | 450.7407 | 327.6923 | 342.1153
4982.6135 | 450.696 | 327.8949 | 342.6616
4983.6135 | 450.9052 | 328.0881 | 343.2073
4984.6135 | 451.0688 | 328.2786 | 343.7988
4985.6135 | 451.069 | 328.4791 | 344.3883
4986.6135 | 450.9922 | 328.6839 | 344.8671
4987.6135 | 450.986 | 328.8799 | 344.8521
4988.6135 | 450.8656 | 329.09 | 344.7117
4989.6135 | 450.826 | 329.2535 | 344.9005
4990.6135 | 450.8246 | 329.4006 | 344.847
4991.6135 | 450.8154 | 329.5682 | 345.2016
4992.6135 | 450.9786 | 329.7633 | 345.4395
4993.6135 | 450.8954 | 329.9385 | 345.5437
4994.6135 | 450.865 | 330.1552 | 345.6255
4995.6135 | 450.7428 | 330.3825 | 345.7547
4996.6135 | 450.7717 | 330.6176 | 346.0174
4997.6135 | 450.6529 | 330.8647 | 346.0674
4998.6135 | 450.6819 | 331.1017 | 346.0143
4999.6135 | 450.7533 | 331.3464 | 345.9805
5000.6135 | 450.702 | 331.5723 | 346.1968
5001.6135 | 450.65 | 331.7806 | 346.3834
5002.6135 | 450.5725 | 331.9548 | 346.3105
5003.6135 | 450.4884 | 332.1067 | 346.4963
5004.6135 | 450.4456 | 332.2505 | 346.0529
5005.6135 | 450.2647 | 332.4048 | 346.1249
5006.6135 | 450.2009 | 332.5851 | 345.8582
5007.6135 | 450.0339 | 332.765 | 345.9748
5008.6135 | 449.9327 | 332.9473 | 346.4046
5009.6135 | 449.8925 | 333.1144 | 346.439
5010.6135 | 449.8204 | 333.2839 | 346.9755
5011.6135 | 449.795 | 333.437 | 347.3351
5012.6135 | 449.8798 | 333.6332 | 347.6556
5013.6135 | 450.0439 | 333.8005 | 348.0005
5014.6135 | 450.1349 | 333.9511 | 348.2548
5015.6135 | 450.2361 | 334.1245 | 348.5158
5016.6135 | 450.2744 | 334.2793 | 348.4507
5017.6135 | 450.3275 | 334.4372 | 348.3826
5018.6135 | 450.4346 | 334.6038 | 348.465
5019.6135 | 450.5126 | 334.7684 | 348.5143
5020.6135 | 450.6244 | 334.9759 | 348.4244
5021.6135 | 450.4655 | 335.1745 | 348.1137
5022.6135 | 450.3267 | 335.3621 | 348.2139
5023.6135 | 450.2811 | 335.5029 | 347.9904
5024.6135 | 450.3215 | 335.6579 | 347.989
5025.6135 | 450.1965 | 335.8141 | 348.0885
5026.6135 | 450.0015 | 335.9745 | 348.1266
5027.6135 | 449.8787 | 336.1131 | 348.2918
5028.6135 | 449.7862 | 336.2102 | 348.4383
5029.6135 | 449.8799 | 336.2809 | 348.7389
5030.6135 | 450.0293 | 336.3437 | 348.8863
5031.6135 | 450.0829 | 336.3984 | 349.3039
5032.6135 | 450.1883 | 336.4834 | 349.4331
5033.6135 | 450.0359 | 336.5923 | 349.5456
5034.6135 | 450.082 | 336.7232 | 349.9097
5035.6135 | 450.1796 | 336.8801 | 350.3599
5036.6135 | 450.1708 | 337.0177 | 350.7522
5037.6135 | 450.2855 | 337.1089 | 351.1632
5038.6135 | 450.3474 | 337.2064 | 351.2719
5039.6135 | 450.2998 | 337.2826 | 351.4183
5040.6135 | 450.2751 | 337.3894 | 351.681
5041.6135 | 450.3268 | 337.4899 | 351.4138
5042.6135 | 450.3265 | 337.611 | 351.1199
5043.6135 | 450.438 | 337.7287 | 351.3006
5044.6135 | 450.3896 | 337.7933 | 351.3842
5045.6135 | 450.3372 | 337.8549 | 351.5253
5046.6135 | 450.5098 | 337.9183 | 351.6039
5047.6135 | 450.7486 | 338.0251 | 351.7556
5048.6135 | 450.5937 | 338.1532 | 351.9434
5049.6135 | 450.5145 | 338.2836 | 351.9389
5050.6135 | 450.5176 | 338.4463 | 352.2528
5051.6135 | 450.5039 | 338.6096 | 352.6876
5052.6135 | 450.4912 | 338.7756 | 353.0535
5053.6135 | 450.6214 | 338.9234 | 353.1743
5054.6135 | 450.7349 | 339.1083 | 353.367
5055.6135 | 450.7228 | 339.2474 | 353.6294
5056.6135 | 450.6997 | 339.3975 | 353.8194
5057.6135 | 450.7289 | 339.5398 | 353.6791
5058.6135 | 450.7059 | 339.6766 | 353.8188
5059.6135 | 450.6088 | 339.8415 | 353.7299
5060.6135 | 450.8905 | 339.9882 | 353.6519
5061.6448 | 450.7889 | 340.1637 | 353.992
5062.6135 | 450.6325 | 340.3251 | 354.3746
5063.6135 | 450.5868 | 340.4473 | 354.3852
5064.6135 | 450.6948 | 340.579 | 354.7606
5065.6135 | 450.6859 | 340.7038 | 355.0885
5066.6135 | 450.7536 | 340.872 | 355.1649
5067.6135 | 450.9591 | 341.0017 | 355.3246
5068.6135 | 451.0223 | 341.0881 | 355.4395
5069.6135 | 451.0351 | 341.1787 | 355.4087
5070.6135 | 450.9667 | 341.2753 | 355.6206
5071.6135 | 450.8782 | 341.3715 | 355.8245
5072.6135 | 450.834 | 341.4864 | 355.8174
5073.6135 | 450.771 | 341.5988 | 355.6496
5074.6135 | 450.7253 | 341.7192 | 355.7614
5075.6135 | 450.7436 | 341.8089 | 355.5535
5076.6135 | 450.6542 | 341.8788 | 355.3148
5077.6135 | 450.696 | 341.9619 | 355.3402
5078.6135 | 450.8657 | 342.0486 | 355.5969
5079.6135 | 450.8072 | 342.1465 | 355.9035
5080.6135 | 450.6411 | 342.2326 | 356.0562
5081.6135 | 450.3372 | 342.3555 | 355.5668
5082.6135 | 450.3695 | 342.4538 | 355.1518
5083.6135 | 450.4371 | 342.6096 | 355.1712
5084.6135 | 450.4227 | 342.7293 | 355.466
5085.6135 | 450.4163 | 342.8489 | 355.2575
5086.6135 | 450.5775 | 342.9806 | 355.2227
5087.6135 | 450.5825 | 343.1122 | 354.9573
5088.6135 | 450.4965 | 343.2099 | 354.8371
5089.6135 | 450.434 | 343.3158 | 355.0327
5090.6135 | 450.4796 | 343.3983 | 355.3148
5091.6135 | 450.4377 | 343.4759 | 355.6206
5092.6135 | 450.481 | 343.5679 | 355.8524
5093.6135 | 450.4901 | 343.6765 | 355.8877
5094.6135 | 450.5548 | 343.8054 | 356.2043
5095.6135 | 450.6397 | 343.9578 | 356.1067
5096.6135 | 450.6341 | 344.1079 | 355.8433
5097.6135 | 450.5449 | 344.2679 | 355.6109
5098.6135 | 450.5115 | 344.4786 | 355.5819
5099.6135 | 450.2554 | 344.6794 | 355.6134
5100.6135 | 450.0978 | 344.8916 | 355.831
5101.6135 | 450.0581 | 345.0859 | 355.7113
5102.6135 | 450.0189 | 345.2087 | 355.7666
5103.6135 | 449.9468 | 345.3578 | 355.9348
5104.6135 | 449.9233 | 345.4752 | 356.1414
5105.6135 | 449.971 | 345.5777 | 356.1456
5106.6135 | 449.977 | 345.6667 | 356.1769
5107.6135 | 449.9804 | 345.7707 | 356.0223
5108.6135 | 449.9907 | 345.8586 | 355.9928
5109.6135 | 450.0866 | 345.9767 | 356.1261
5110.6135 | 450.0313 | 346.0888 | 356.1426
5111.6135 | 450.1724 | 346.2256 | 356.2031
5112.6135 | 450.194 | 346.3648 | 356.2201
5113.6135 | 450.179 | 346.4925 | 356.1754
5114.6135 | 450.2266 | 346.5863 | 356.1353
5115.6135 | 450.2532 | 346.6806 | 356.1763
5116.6135 | 450.2379 | 346.8055 | 356.2748
5117.6135 | 450.2237 | 346.907 | 355.9424
5118.6135 | 450.2368 | 347.0384 | 356.2869
5119.6135 | 450.2391 | 347.1268 | 356.4211
5120.6135 | 450.2167 | 347.2237 | 356.3117
5121.6135 | 450.181 | 347.3272 | 356.367
5122.6135 | 450.1496 | 347.4268 | 356.5058
5123.6135 | 450.1673 | 347.5161 | 356.8793
5124.6135 | 450.2947 | 347.616 | 356.9215
5125.6135 | 450.4805 | 347.6859 | 357.1824
5126.6135 | 450.5283 | 347.789 | 357.4761
5127.6135 | 450.5607 | 347.8881 | 357.5219
5128.6135 | 450.6884 | 348.0434 | 357.693
5129.6135 | 450.7055 | 348.1764 | 357.7409
5130.6135 | 450.7207 | 348.3195 | 357.553
5131.6135 | 450.6897 | 348.4371 | 357.4844
5132.6135 | 450.7681 | 348.5677 | 357.4499
5133.6135 | 450.6463 | 348.6881 | 357.625
5134.6135 | 450.5503 | 348.8361 | 357.4506
5135.6135 | 450.4381 | 348.9467 | 357.4457
5136.6135 | 450.4774 | 349.0677 | 357.6298
5137.6135 | 450.5 | 349.14 | 357.9004
5138.6135 | 450.523 | 349.2544 | 358.3317
5139.6135 | 450.4846 | 349.3415 | 358.3656
5140.6135 | 450.4332 | 349.4483 | 358.1899
5141.6135 | 450.3227 | 349.5629 | 358.5133
5142.6135 | 450.1328 | 349.6541 | 358.7434
5143.6135 | 449.951 | 349.7423 | 358.7809
5144.6135 | 449.9239 | 349.8056 | 358.9574
5145.6135 | 449.9372 | 349.8512 | 359.1337
5146.6135 | 449.9193 | 349.8678 | 359.2331
5147.6135 | 450.0687 | 349.957 | 359.5588
5148.6135 | 450.0381 | 350.0225 | 359.5713
5149.6135 | 449.8985 | 350.0972 | 359.745
5150.6135 | 449.9046 | 350.1702 | 359.8968
5151.6135 | 449.976 | 350.2517 | 360.093
5152.6135 | 449.8967 | 350.3089 | 360.1967
5153.6135 | 449.9029 | 350.3709 | 360.3573
5154.6135 | 449.9645 | 350.4427 | 360.3756
5155.6135 | 449.9172 | 350.5238 | 360.4682
5156.6135 | 449.8431 | 350.5909 | 360.5954
5157.6135 | 449.7352 | 350.6206 | 360.7049
5158.6135 | 449.6595 | 350.6399 | 360.8771
5159.6135 | 449.6078 | 350.6776 | 361.1082
5160.6135 | 449.7999 | 350.7382 | 361.2606
5161.6135 | 449.9327 | 350.8092 | 361.3149
5162.6135 | 450.0391 | 350.8785 | 361.2868
5163.6135 | 450.0794 | 350.9506 | 361.4534
5164.6135 | 450.0733 | 351.0634 | 361.3031
5165.6135 | 450.1254 | 351.1354 | 361.2147
5166.6135 | 450.0037 | 351.2194 | 361.3059
5167.6135 | 449.9675 | 351.3001 | 361.3644
5168.6135 | 449.9094 | 351.3971 | 361.3747
5169.6135 | 449.8566 | 351.4887 | 361.5386
5170.6135 | 449.7699 | 351.5899 | 361.5825
5171.6135 | 449.8424 | 351.6638 | 361.7094
5172.6135 | 450.0645 | 351.7483 | 361.7054
5173.6135 | 450.0666 | 351.8292 | 361.7825
5174.6135 | 450.045 | 351.8891 | 361.9526
5175.6135 | 450.1051 | 351.976 | 361.7607
5176.6135 | 450.1333 | 352.0706 | 361.5496
5177.6135 | 450.2666 | 352.1516 | 361.5754
5178.6135 | 450.3762 | 352.216 | 361.6455
5179.6135 | 450.543 | 352.2898 | 361.8296
5180.6135 | 450.6319 | 352.3394 | 362.0257
5181.6135 | 450.5406 | 352.3935 | 362.0772
5182.6135 | 450.5938 | 352.4264 | 362.1508
5183.6135 | 450.5808 | 352.4367 | 362.3339
5184.6135 | 450.6015 | 352.4475 | 362.5191
5185.6135 | 450.4936 | 352.506 | 362.628
5186.6135 | 450.3622 | 352.5466 | 362.7263
5187.6135 | 450.3555 | 352.5781 | 362.8179
5188.6135 | 450.2617 | 352.6056 | 362.6652
5189.6135 | 450.1976 | 352.6283 | 362.6027
5190.6135 | 450.2206 | 352.6731 | 362.639
5191.6135 | 450.0323 | 352.7078 | 362.8269
5192.6135 | 449.8782 | 352.7203 | 362.9868
5193.6135 | 449.9827 | 352.7387 | 363.15
5194.6135 | 450.0924 | 352.747 | 363.2775
5195.6135 | 450.1104 | 352.7571 | 363.3542
5196.6135 | 450.045 | 352.7793 | 363.4318
5197.6135 | 449.9821 | 352.8204 | 363.5185
5198.6135 | 449.9655 | 352.8611 | 363.5057
5199.6135 | 449.9725 | 352.9472 | 363.4318
5200.6135 | 449.8999 | 353.0052 | 363.464
5201.6135 | 449.8493 | 353.0755 | 363.551
5202.6135 | 449.7208 | 353.1684 | 363.6102
5203.6135 | 449.7527 | 353.2372 | 363.5903
5204.6135 | 449.7094 | 353.3568 | 363.6015
5205.6135 | 449.7125 | 353.4421 | 363.5695
5206.6135 | 449.7455 | 353.5598 | 363.5697
5207.6135 | 449.7544 | 353.6633 | 363.4868
5208.6135 | 449.8097 | 353.7769 | 363.3298
5209.6135 | 449.8073 | 353.881 | 363.3289
5210.6135 | 449.7464 | 354.0559 | 363.324
5211.6135 | 449.7575 | 354.1577 | 363.4697
5212.6135 | 449.7222 | 354.2843 | 363.4265
5213.6135 | 449.699 | 354.4102 | 363.2593
5214.6135 | 449.6889 | 354.5362 | 363.1044
5215.6135 | 449.7933 | 354.6705 | 362.9312
5216.6135 | 449.7628 | 354.7837 | 362.8598
5217.6135 | 449.7126 | 354.8959 | 362.9484
5218.6135 | 449.6022 | 355.0571 | 362.9125
5219.6135 | 449.5219 | 355.1913 | 362.8721
5220.6135 | 449.5542 | 355.3058 | 362.9319
5221.6135 | 449.5137 | 355.4084 | 363.1068
5222.6135 | 449.588 | 355.5128 | 363.0987
5223.6135 | 449.4579 | 355.606 | 363.285
5224.6135 | 449.2499 | 355.683 | 363.2249
5225.6135 | 449.2303 | 355.7681 | 363.2019
5226.6135 | 449.2301 | 355.8469 | 363.2884
5227.6135 | 449.2499 | 355.91 | 363.1931
5228.6135 | 449.1282 | 355.9554 | 363.0983
5229.6135 | 449.2101 | 356.0027 | 362.8605
5230.6135 | 449.2306 | 356.0673 | 362.8525
5231.6135 | 449.118 | 356.1165 | 362.9892
5232.6135 | 449.1257 | 356.1673 | 363.2156
5233.6135 | 449.2436 | 356.235 | 363.3078
5234.6135 | 449.2769 | 356.275 | 363.3266
5235.6135 | 449.3836 | 356.2991 | 363.2416
5236.6135 | 449.6314 | 356.3452 | 363.2784
5237.6135 | 449.7677 | 356.3975 | 363.0997
5238.6135 | 449.8847 | 356.4639 | 362.855
5239.6135 | 449.8593 | 356.5378 | 362.8022
5240.6135 | 449.945 | 356.6092 | 362.7052
5241.6135 | 450.0396 | 356.6909 | 362.5085
5242.6135 | 450.0866 | 356.7768 | 362.5666
5243.6135 | 450.2008 | 356.8408 | 362.6653
5244.6135 | 450.265 | 356.9183 | 362.7082
5245.6135 | 450.291 | 357.0055 | 362.6158
5246.6135 | 450.3031 | 357.0844 | 362.5521
5247.6135 | 450.2419 | 357.1541 | 362.4684
5248.6135 | 450.4024 | 357.2394 | 362.4621
5249.6135 | 450.4205 | 357.3098 | 362.5056
5250.6135 | 450.3537 | 357.3782 | 362.6069
5251.6135 | 450.269 | 357.4703 | 362.5294
5252.6135 | 450.1468 | 357.5338 | 362.3849
5253.6135 | 450.0762 | 357.5829 | 362.3431
5254.6135 | 449.9768 | 357.6395 | 362.2876
5255.6135 | 449.9305 | 357.6779 | 362.4099
5256.6135 | 450.0558 | 357.723 | 362.362
5257.6135 | 450.2004 | 357.764 | 362.3403
5258.6135 | 450.3227 | 357.8036 | 362.5048
5259.6135 | 450.2386 | 357.8324 | 362.3466
5260.6135 | 450.075 | 357.8764 | 362.3997
5261.6135 | 449.9897 | 357.9045 | 362.5575
5262.6135 | 449.9901 | 357.9439 | 362.6155
5263.6135 | 449.8738 | 357.9822 | 362.4593
5264.6135 | 449.9078 | 358.0199 | 362.4101
5265.6135 | 449.9391 | 358.0593 | 362.6006
5266.6135 | 449.8664 | 358.1243 | 362.7149
5267.6135 | 449.8091 | 358.1812 | 362.8136
5268.6135 | 449.7122 | 358.2328 | 362.8231
5269.6135 | 449.7204 | 358.2888 | 362.9775
5270.6135 | 449.7172 | 358.3574 | 362.8243
5271.6135 | 449.7282 | 358.4056 | 362.2471
5272.6135 | 449.6229 | 358.4685 | 362.072
5273.6135 | 449.4925 | 358.5532 | 361.7802
5274.6135 | 449.3443 | 358.6301 | 361.7508
5275.6135 | 449.2939 | 358.7203 | 361.7688
5276.6135 | 449.3068 | 358.7915 | 361.6071
5277.6135 | 449.2906 | 358.8698 | 361.4371
5278.6135 | 449.4671 | 358.9457 | 361.2509
5279.6135 | 449.5797 | 359.02 | 361.1963
5280.6135 | 449.5733 | 359.0797 | 361.3986
5281.6135 | 449.4993 | 359.123 | 361.395
5282.6135 | 449.4963 | 359.1624 | 361.5797
5283.6135 | 449.64 | 359.1957 | 361.862
5284.6135 | 449.6272 | 359.2093 | 362.303
5285.6135 | 449.7202 | 359.2269 | 362.3749
5286.6135 | 449.8037 | 359.246 | 362.3964
5287.6448 | 449.8219 | 359.2733 | 362.5692
5288.6135 | 449.8149 | 359.2804 | 362.7779
5289.6135 | 449.8096 | 359.3044 | 362.6748
5290.6135 | 449.7366 | 359.331 | 362.5909
5291.6135 | 449.7402 | 359.3589 | 362.7163
5292.6135 | 449.7063 | 359.3772 | 362.8035
5293.6135 | 449.8656 | 359.4261 | 362.6749
5294.6135 | 449.892 | 359.4886 | 362.6799
5295.6135 | 449.8282 | 359.5332 | 362.7063
5296.6135 | 449.8539 | 359.5768 | 362.3642
5297.6135 | 450.3448 | 359.6376 | 361.8329
5298.6135 | 451.5343 | 359.7171 | 361.5396
5299.6135 | 453.3725 | 359.8161 | 361.6425
5300.6135 | 455.7474 | 359.8919 | 361.8192
5301.6135 | 458.6774 | 360.0127 | 362.2743
5302.6135 | 461.8068 | 360.1315 | 363.0612
5303.6135 | 465.0819 | 360.2846 | 364.0286
5304.6135 | 468.5326 | 360.4815 | 364.7462
5305.6135 | 471.6928 | 360.6894 | 365.5848
5306.6135 | 474.7037 | 360.9232 | 366.4343
5307.6135 | 477.3597 | 361.1728 | 367.2933
5308.6135 | 479.8241 | 361.4737 | 368.3606
5309.6135 | 481.5865 | 361.7774 | 369.0782
5310.6135 | 482.9645 | 362.0881 | 369.7976
5311.6135 | 484.1515 | 362.3912 | 370.0622
5312.6135 | 485.0757 | 362.6845 | 370.6517
5313.6135 | 485.5552 | 362.9739 | 371.3299
5314.6135 | 485.7772 | 363.2527 | 372.0294
5315.6135 | 485.8586 | 363.554 | 372.7524
5316.6135 | 485.7329 | 363.8158 | 373.0775
5317.6135 | 485.5227 | 364.0825 | 373.4548
5318.6135 | 485.3314 | 364.3331 | 373.6196
5319.6135 | 484.869 | 364.5619 | 374.0899
5320.6135 | 484.4302 | 364.787 | 374.1955
5321.6135 | 483.9116 | 365.0255 | 374.1219
5322.6135 | 483.3191 | 365.2693 | 374.1657
5323.6135 | 482.7371 | 365.5277 | 374.3776
5324.6135 | 482.1664 | 365.7918 | 374.5286
5325.6135 | 481.5486 | 366.0735 | 374.5951
5326.6135 | 480.7779 | 366.3291 | 374.5428
5327.6135 | 480.1574 | 366.6166 | 374.5849
5328.6135 | 479.5175 | 366.8598 | 374.9353
5329.6135 | 479.0589 | 367.0953 | 375.2511
5330.6135 | 478.4267 | 367.3019 | 375.0827
5331.6135 | 477.8535 | 367.4776 | 374.6468
5332.6135 | 477.4216 | 367.6568 | 374.4261
5333.6135 | 477.0606 | 367.8681 | 374.3191
5334.6135 | 476.7212 | 368.0627 | 374.5328
5335.6135 | 476.3566 | 368.2535 | 374.7518
5336.6135 | 475.9415 | 368.4158 | 374.9476
5337.6135 | 475.6342 | 368.6089 | 374.8014
5338.6135 | 475.3716 | 368.7867 | 374.7884
5339.6135 | 475.0005 | 368.9581 | 374.547
5340.6135 | 474.5913 | 369.1099 | 374.8097
5341.6135 | 474.3509 | 369.2711 | 375.3559
5342.6135 | 474.1685 | 369.3997 | 375.7154
5343.6135 | 473.934 | 369.559 | 375.6999
5344.6135 | 473.8196 | 369.6869 | 375.9758
5345.6135 | 473.8236 | 369.8301 | 375.8696
5346.6135 | 473.6084 | 369.9801 | 375.8895
5347.6135 | 473.5824 | 370.1101 | 375.8046
5348.6135 | 473.5505 | 370.2391 | 375.8725
5349.6135 | 473.6499 | 370.3704 | 375.7467
5350.6135 | 473.8498 | 370.5016 | 375.7381
5351.6135 | 473.9926 | 370.6263 | 375.997
5352.6135 | 474.244 | 370.737 | 376.0178
5353.6135 | 474.4558 | 370.8591 | 376.162
5354.6135 | 474.6494 | 370.9648 | 376.4301
5355.6135 | 474.772 | 371.0708 | 377.0594
5356.6135 | 474.8368 | 371.1811 | 377.7124
5357.6135 | 474.8864 | 371.2871 | 378.0208
5358.6135 | 475.0209 | 371.4047 | 378.3307
5359.6135 | 475.0361 | 371.5327 | 378.4428
5360.6135 | 475.1736 | 371.6431 | 378.3844
5361.6135 | 475.3196 | 371.7243 | 378.2195
5362.6135 | 475.3683 | 371.8347 | 378.3258
5363.6135 | 475.5603 | 371.9189 | 378.4772
5364.6135 | 475.7047 | 372.0079 | 378.6634
5365.6135 | 475.7353 | 372.1081 | 378.7694
5366.6135 | 475.8428 | 372.2591 | 378.9606
5367.6135 | 475.7598 | 372.4064 | 378.8958
5368.6135 | 475.7275 | 372.5297 | 378.9745
5369.6135 | 475.7494 | 372.6739 | 379.0797
5370.6135 | 475.5999 | 372.8096 | 379.3318
5371.6135 | 475.7031 | 372.9649 | 379.0986
5372.6135 | 475.7634 | 373.1001 | 379.3609
5373.6135 | 475.7105 | 373.2634 | 379.7188
5374.6135 | 475.6675 | 373.3769 | 380.1268
5375.6135 | 475.5284 | 373.4919 | 380.5652
5376.6135 | 475.4295 | 373.5922 | 380.9785
5377.6135 | 475.3062 | 373.724 | 381.4614
5378.6135 | 475.3796 | 373.858 | 381.594
5379.6135 | 475.625 | 373.9862 | 381.6402
5380.6135 | 475.7221 | 374.0994 | 381.4804
5381.6135 | 475.5144 | 374.2063 | 381.2579
5382.6135 | 475.4054 | 374.2941 | 381.15
5383.6135 | 475.3496 | 374.4005 | 380.8843
5384.6135 | 475.2914 | 374.4606 | 380.7731
5385.6135 | 475.307 | 374.5785 | 380.8745
5386.6135 | 475.3635 | 374.6481 | 381.1827
5387.6135 | 475.3037 | 374.7281 | 381.216
5388.6135 | 475.1242 | 374.8461 | 381.1582
5389.6135 | 474.9649 | 374.9422 | 381.2925
5390.6135 | 474.8458 | 375.069 | 381.6876
5391.6135 | 474.8648 | 375.1905 | 381.9429
5392.6135 | 474.8743 | 375.28 | 381.8596
5393.6135 | 475.064 | 375.4448 | 382.1309
5394.6135 | 475.1609 | 375.5614 | 382.2598
5395.6135 | 475.1108 | 375.6664 | 382.2638
5396.6135 | 475.0952 | 375.7325 | 382.3925
5397.6135 | 475.0978 | 375.8846 | 382.4449
5398.6135 | 475.124 | 375.9864 | 382.4898
5399.6135 | 475.1013 | 376.0929 | 382.6322
5400.6135 | 475.2174 | 376.2421 | 382.7844
5401.6135 | 475.265 | 376.3638 | 382.9117
5402.6135 | 475.306 | 376.5191 | 382.5481
5403.6135 | 475.2224 | 376.6652 | 382.2039
5404.6135 | 475.3895 | 376.7965 | 381.8207
5405.6135 | 475.6324 | 376.9154 | 381.3802
5406.6135 | 475.5993 | 377.0618 | 381.2899
5407.6135 | 475.6216 | 377.1807 | 381.4411
5408.6135 | 475.6524 | 377.2897 | 381.5009
5409.6135 | 475.5835 | 377.3975 | 381.9305
5410.6135 | 475.6884 | 377.5188 | 382.2739
5411.6135 | 475.8393 | 377.6467 | 382.6509
5412.6135 | 475.8359 | 377.7826 | 382.7686
5413.6135 | 475.751 | 377.9144 | 382.8831
5414.6135 | 475.7427 | 378.0399 | 383.2197
5415.6135 | 475.717 | 378.1468 | 383.7104
5416.6135 | 475.9154 | 378.2634 | 384.0305
5417.6135 | 475.7983 | 378.3891 | 384.1333
5418.6135 | 475.6578 | 378.4781 | 383.851
5419.6135 | 475.5088 | 378.5821 | 383.8809
5420.6135 | 475.3184 | 378.6784 | 384.0967
5421.6135 | 475.0428 | 378.7563 | 384.3415
5422.6135 | 474.9846 | 378.872 | 384.1906
5423.6135 | 474.8341 | 378.9958 | 384.2214
5424.6135 | 474.8515 | 379.069 | 384.2182
5425.6135 | 474.98 | 379.1157 | 384.4228
5426.6135 | 474.9499 | 379.1567 | 384.7839
5427.6135 | 474.9532 | 379.2359 | 384.978
5428.6135 | 474.8709 | 379.2856 | 385.1417
5429.6135 | 474.7691 | 379.3359 | 385.2782
5430.6135 | 474.4908 | 379.383 | 385.5062
5431.6135 | 474.5397 | 379.4083 | 385.7261
5432.6135 | 474.4498 | 379.4563 | 385.9927
5433.6135 | 474.5675 | 379.4934 | 386.1055
5434.6135 | 474.5291 | 379.5211 | 386.2975
5435.6135 | 474.6535 | 379.5479 | 386.2695
5436.6135 | 474.7113 | 379.5812 | 386.3536
5437.6135 | 474.6512 | 379.6074 | 386.166
5438.6135 | 474.8571 | 379.6624 | 385.6588
5439.6135 | 474.7624 | 379.7275 | 385.5415
5440.6135 | 474.5862 | 379.8163 | 385.7815
5441.6135 | 474.5646 | 379.9398 | 385.8587
5442.6135 | 474.3627 | 380.0355 | 385.5944
5443.6135 | 474.2664 | 380.1386 | 385.7034
5444.6135 | 474.3752 | 380.2094 | 386.0342
5445.6135 | 474.2989 | 380.2848 | 385.8459
5446.6135 | 474.2699 | 380.3717 | 385.9779
5447.6135 | 474.2812 | 380.4459 | 386.015
5448.6135 | 474.3091 | 380.5151 | 386.0939
5449.6135 | 474.4133 | 380.5468 | 386.2032
5450.6135 | 474.3164 | 380.5746 | 385.9404
5451.6135 | 474.4329 | 380.6309 | 386.0332
5452.6135 | 474.42 | 380.7001 | 386.5219
5453.6135 | 474.4368 | 380.7517 | 386.4639
5454.6135 | 474.5379 | 380.7665 | 386.7609
5455.6135 | 474.5062 | 380.8154 | 386.7119
5456.6135 | 474.5225 | 380.8449 | 386.7027
5457.6135 | 474.5933 | 380.8683 | 386.5141
5458.6135 | 474.6759 | 380.8663 | 385.9767
5459.6135 | 474.8755 | 380.9078 | 385.5343
5460.6135 | 475.6299 | 380.9873 | 385.6803
5461.6135 | 477.1277 | 381.0498 | 386.0244
5462.6135 | 479.0953 | 381.1329 | 385.9654
5463.6135 | 481.3944 | 381.2297 | 386.0796
5464.6135 | 484.0491 | 381.4162 | 386.6424
5465.6135 | 487.1813 | 381.6244 | 386.7351
5466.6135 | 490.3995 | 381.8929 | 387.5338
5467.6135 | 493.5644 | 382.1895 | 388.3731
5468.6135 | 496.8492 | 382.4552 | 388.7659
5469.6135 | 500.0469 | 382.7975 | 389.61
5470.6135 | 503.1872 | 383.1498 | 390.6882
5471.6135 | 506.04 | 383.5462 | 391.5227
5472.6135 | 508.4607 | 383.9046 | 391.6728
5473.6135 | 510.8112 | 384.3274 | 391.9089
5474.6135 | 512.826 | 384.759 | 392.869
5475.6135 | 514.5093 | 385.2193 | 394.085
5476.6135 | 515.8479 | 385.6541 | 394.7936
5477.6135 | 516.9461 | 386.128 | 395.7428
5478.6135 | 517.7836 | 386.61 | 396.9847
5479.6135 | 518.4731 | 387.1211 | 397.9899
5480.6135 | 518.8385 | 387.6236 | 398.7807
5481.6135 | 518.9968 | 388.1521 | 399.3117
5482.6135 | 518.8801 | 388.6449 | 400.0297
5483.6135 | 518.9494 | 389.1313 | 400.0002
5484.6135 | 519.022 | 389.628 | 400.0261
5485.6135 | 519.0022 | 390.0992 | 400.4689
5486.6135 | 518.7978 | 390.5626 | 400.2553
5487.6135 | 518.6537 | 390.9872 | 399.8874
5488.6135 | 518.4027 | 391.386 | 400.2052
5489.6135 | 518.401 | 391.7621 | 400.7589
5490.6135 | 518.5456 | 392.1183 | 401.5478
5491.6135 | 518.6117 | 392.5056 | 402.512
5492.6135 | 518.7817 | 392.8836 | 403.2108
5493.6135 | 518.9006 | 393.2259 | 403.4191
5494.6135 | 518.9829 | 393.6093 | 403.8539
5495.6135 | 518.8698 | 394.0011 | 404.6453
5496.6135 | 518.8829 | 394.3939 | 404.6447
5497.6135 | 518.9713 | 394.7868 | 405.3804
5498.6135 | 519.1947 | 395.1584 | 405.918
5499.6135 | 519.4589 | 395.5145 | 406.4548
5500.6135 | 519.6105 | 395.832 | 406.8447
5501.6135 | 519.818 | 396.1575 | 406.8931
5502.6135 | 520.0256 | 396.4873 | 406.7106
5503.6135 | 520.4692 | 396.7764 | 407.3239
5504.6135 | 520.9592 | 397.1187 | 408.01
5505.6135 | 521.0567 | 397.4154 | 408.5633
5506.6135 | 521.18 | 397.7331 | 408.9603
5507.6135 | 521.3664 | 398.0602 | 409.677
5508.6135 | 521.5747 | 398.3647 | 410.008
5509.6135 | 521.7939 | 398.6674 | 409.9898
5510.6135 | 521.9181 | 399.0236 | 410.2712
5511.6135 | 522.0406 | 399.3781 | 410.6458
5512.6135 | 522.2912 | 399.7137 | 410.9336
5513.6135 | 522.5423 | 400.0481 | 411.174
5514.6135 | 522.7451 | 400.3965 | 411.041
5515.6135 | 522.9223 | 400.7389 | 411.459
5516.6135 | 523.0222 | 401.078 | 411.3359
5517.6135 | 523.0917 | 401.4273 | 412.0884
5518.6135 | 523.1983 | 401.8093 | 412.764
5519.6135 | 523.1626 | 402.1614 | 413.2493
5520.6135 | 523.3085 | 402.5064 | 413.6535
5521.6135 | 523.3492 | 402.839 | 413.0871
5522.6135 | 523.6136 | 403.1269 | 411.3759
5523.6135 | 523.7144 | 403.4084 | 411.309
5524.6135 | 523.6041 | 403.6939 | 411.2133
5525.6135 | 523.7281 | 403.9591 | 411.6176
5526.6135 | 523.8425 | 404.2157 | 412.2041
5527.6135 | 524.0428 | 404.5803 | 412.6825
5528.6135 | 523.9496 | 404.9547 | 411.4334
5529.6135 | 523.8164 | 405.3603 | 412.0313
5530.6135 | 523.8219 | 405.694 | 412.4097
5531.6135 | 524.1136 | 406.0235 | 411.3917
5532.6135 | 524.1162 | 406.4083 | 411.824
5533.6135 | 524.2431 | 406.7378 | 412.4685
5534.6135 | 524.3363 | 407.0352 | 412.5961
5535.6135 | 524.4805 | 407.3587 | 413.1502
5536.6135 | 524.5745 | 407.7041 | 412.6964
5537.6135 | 524.6796 | 408.0311 | 412.1393
5538.6135 | 524.6419 | 408.364 | 411.4922
5539.6135 | 524.7015 | 408.6963 | 410.926
5540.6135 | 524.7744 | 408.9858 | 411.5382
5541.6135 | 524.9944 | 409.2965 | 410.6746
5542.6135 | 524.9984 | 409.5566 | 410.1933
5543.6135 | 524.9032 | 409.7759 | 409.385
5544.6135 | 524.9403 | 409.9477 | 409.2261
5545.6135 | 525.0271 | 410.1115 | 410.3821
5546.6135 | 524.9619 | 410.3706 | 410.1593
5547.6135 | 524.73 | 410.6592 | 409.8834
5548.6135 | 524.864 | 410.9098 | 407.9752
5549.6135 | 524.9056 | 411.1608 | 406.6563
5550.6135 | 524.8268 | 411.4611 | 407.8003
5551.6135 | 524.6636 | 411.7779 | 408.8935
5552.6135 | 524.8675 | 412.0656 | 409.4435
5553.6135 | 524.8971 | 412.3274 | 410.6542
5554.6135 | 524.8832 | 412.6515 | 411.0269
5555.6135 | 524.9385 | 412.9351 | 410.8854
5556.6135 | 524.9562 | 413.2634 | 411.1477
5557.6135 | 524.8565 | 413.4798 | 411.4017
5558.6135 | 524.8625 | 413.6057 | 409.1713
5559.6135 | 524.7775 | 413.7784 | 410.1427
5560.6135 | 524.5706 | 413.991 | 410.1012
5561.6135 | 524.4008 | 414.1613 | 408.44
5562.6135 | 524.5271 | 414.3307 | 406.3843
5563.6135 | 524.5727 | 414.5664 | 405.4722
5564.6135 | 524.7348 | 414.87 | 404.9289
5565.6135 | 524.977 | 415.1046 | 406.5231
5566.6135 | 525.0628 | 415.3586 | 408.4718
5567.6135 | 525.1698 | 415.5871 | 408.9992
5568.6135 | 525.2705 | 415.7753 | 410.8351
5569.6135 | 525.1795 | 415.8861 | 411.1152
5570.6135 | 525.1333 | 416.0159 | 410.7987
5571.6135 | 525.1414 | 416.2413 | 411.4917
5572.6135 | 525.1293 | 416.4993 | 411.0594
5573.6135 | 525.2879 | 416.7217 | 410.3156
5574.6135 | 525.3502 | 417.0009 | 407.1099
5575.6135 | 525.2904 | 417.2626 | 406.6689
5576.6135 | 525.3262 | 417.4646 | 408.5112
5577.6135 | 525.2826 | 417.673 | 411.5504
5578.6135 | 525.1264 | 417.8452 | 412.3924
5579.6135 | 525.2171 | 418.0548 | 412.1588
5580.6135 | 525.2099 | 418.2394 | 411.4779
5581.6135 | 525.0784 | 418.5244 | 410.3961
5582.6135 | 524.9529 | 418.77 | 408.4042
5583.6135 | 525.0796 | 419.0724 | 409.1724
5584.6135 | 525.0354 | 419.3478 | 410.0423
5585.6135 | 525.0878 | 419.551 | 411.532
5586.6135 | 525.2503 | 419.8382 | 413.3234
5587.6135 | 525.4047 | 420.0475 | 413.597
5588.6135 | 525.3021 | 420.1996 | 414.0839
5589.6135 | 525.268 | 420.381 | 414.6023
5590.6135 | 525.3421 | 420.5957 | 412.0275
5591.6135 | 525.3096 | 420.7774 | 410.3275
5592.6135 | 525.4813 | 420.9895 | 411.3938
5593.6135 | 525.4735 | 421.2027 | 412.2292
5594.6135 | 525.4138 | 421.4206 | 412.6912
5595.6135 | 525.2549 | 421.5073 | 411.4006
5596.6135 | 525.4236 | 421.6108 | 412.06
5597.6135 | 525.5826 | 421.7696 | 413.5589
5598.6135 | 525.7711 | 422.021 | 415.5275
5599.6135 | 525.8765 | 422.2726 | 416.7155
5600.6135 | 525.8408 | 422.5763 | 415.6082
5601.6135 | 525.8819 | 422.8261 | 416.6838
5602.6135 | 525.9659 | 423.011 | 413.8541
5603.6135 | 525.8283 | 423.224 | 413.4971
5604.6135 | 525.7809 | 423.4892 | 411.6072
5605.6135 | 525.8026 | 423.7065 | 411.0532
5606.6135 | 525.6754 | 423.9354 | 412.9656
5607.6135 | 525.6612 | 424.0806 | 411.657
5608.6135 | 525.7242 | 424.3172 | 412.6286
5609.6135 | 525.6184 | 424.518 | 414.5822
5610.6135 | 525.4232 | 424.6669 | 414.4472
5611.6135 | 525.4311 | 424.725 | 414.3223
5612.6135 | 525.5084 | 424.7714 | 416.4758
5613.6135 | 525.5533 | 424.8585 | 417.3661
5614.6135 | 525.2488 | 424.9551 | 418.3552
5615.6135 | 525.0983 | 425.0967 | 416.5656
5616.6135 | 525.0753 | 425.2555 | 414.3998
5617.6135 | 525.2127 | 425.3526 | 413.6276
5618.6135 | 525.3671 | 425.3951 | 415.493
5619.6135 | 525.5567 | 425.5034 | 417.3003
5620.6135 | 525.8536 | 425.7181 | 415.6491
5621.6135 | 525.9134 | 425.9347 | 414.4496
5622.6135 | 525.9805 | 426.1837 | 415.4799
5623.6135 | 525.9924 | 426.3819 | 414.7857
5624.6135 | 525.8595 | 426.5977 | 416.6038
5625.6135 | 525.7362 | 426.7647 | 418.0587
5626.6135 | 525.5876 | 426.8865 | 418.2296
5627.6135 | 525.5436 | 427.025 | 418.6544
5628.6135 | 525.3981 | 427.1854 | 418.8736
5629.6135 | 525.3608 | 427.3864 | 419.641
5630.6135 | 525.3842 | 427.5737 | 420.0495
5631.6135 | 525.287 | 427.7961 | 419.3246
5632.6135 | 525.1221 | 428.0543 | 418.4641
5633.6135 | 524.8742 | 428.2104 | 418.9381
5634.6135 | 524.8053 | 428.4238 | 416.6563
5635.6135 | 524.9347 | 428.6864 | 415.9946
5636.6135 | 525.0132 | 428.9779 | 415.809
5637.6135 | 525.1652 | 429.2113 | 415.8323
5638.6135 | 525.1921 | 429.2666 | 417.9286
5639.6135 | 525.0922 | 429.3583 | 417.9001
5640.6135 | 525.0677 | 429.435 | 417.6004
5641.6135 | 525.2043 | 429.5505 | 418.0162
5642.6135 | 525.2471 | 429.6514 | 417.2634
5643.6135 | 525.4036 | 429.6796 | 416.2985
5644.6135 | 525.5208 | 429.7842 | 415.7065
5645.6135 | 525.6357 | 429.8507 | 418.0111
5646.6135 | 525.5576 | 429.9153 | 419.152
5647.6135 | 525.4983 | 430.0022 | 419.5161
5648.6135 | 525.5409 | 430.065 | 418.2055
5649.6135 | 525.6703 | 430.1663 | 419.2932
5650.6135 | 525.5795 | 430.2876 | 420.2971
5651.6135 | 525.5149 | 430.4789 | 420.9753
5652.6135 | 525.8752 | 430.498 | 422.2797
5653.6135 | 526.0471 | 430.5131 | 420.7619
5654.6135 | 526.3003 | 430.53 | 420.689
5655.6135 | 526.2066 | 430.5853 | 420.8698
5656.6135 | 526.1416 | 430.6179 | 421.7155
5657.6135 | 526.0191 | 430.7399 | 422.8707
5658.6135 | 526.055 | 430.9774 | 421.1738
5659.6135 | 525.9346 | 431.1765 | 419.6488
5660.6135 | 525.8411 | 431.3326 | 420.1981
5661.6135 | 525.6683 | 431.5319 | 420.4729
5662.6135 | 525.7225 | 431.816 | 420.7858
5663.6135 | 525.6802 | 432.1103 | 421.1245
5664.6135 | 525.6353 | 432.2993 | 419.933
5665.6135 | 525.5491 | 432.5095 | 418.4337
5666.6135 | 525.4032 | 432.6 | 418.4801
5667.6135 | 525.2711 | 432.6193 | 418.7628
5668.6135 | 525.147 | 432.6925 | 417.9165
5669.6135 | 525.0587 | 432.9062 | 416.3679
5670.6135 | 524.9457 | 433.044 | 416.8538
5671.6135 | 525.0429 | 433.0806 | 415.5791
5672.6135 | 524.93 | 433.1156 | 414.4221
5673.6135 | 524.8156 | 433.1994 | 416.7422
5674.6135 | 524.9585 | 433.2982 | 418.0776
5675.6135 | 525.0644 | 433.4282 | 420.0216
5676.6135 | 525.1385 | 433.4169 | 420.2689
5677.6135 | 524.9434 | 433.3855 | 420.5996
5678.6135 | 524.9472 | 433.4078 | 420.7553
5679.6135 | 524.9809 | 433.5495 | 422.0245
5680.6135 | 525.1223 | 433.7421 | 422.6182
5681.6135 | 525.2122 | 433.8624 | 422.7038
5682.6135 | 525.4296 | 433.9568 | 424.13
5683.6135 | 525.3484 | 434.1025 | 423.7001
5684.6135 | 525.5268 | 434.344 | 422.0168
5685.6135 | 525.5942 | 434.4373 | 423.1566
5686.6135 | 525.6351 | 434.4718 | 423.0358
5687.6135 | 525.635 | 434.5166 | 424.7342
5688.6135 | 525.5987 | 434.4924 | 422.3665
5689.6135 | 525.5947 | 434.4857 | 420.9337
5690.6135 | 525.4332 | 434.3413 | 421.5638
5691.6135 | 525.4336 | 434.2968 | 421.577
5692.6135 | 525.3881 | 434.2856 | 421.7574
5693.6135 | 525.5207 | 434.3293 | 419.9827
5694.6135 | 525.5444 | 434.3225 | 419.5743
5695.6135 | 525.5584 | 434.2505 | 420.8118
5696.6135 | 525.5475 | 434.2511 | 421.5833
5697.6135 | 525.4523 | 434.3294 | 421.976
5698.6135 | 525.5785 | 434.5064 | 422.2159
5699.6135 | 525.4656 | 434.7004 | 423.2492
5700.6135 | 525.5017 | 434.8635 | 422.9719
5701.6135 | 525.379 | 435.0528 | 422.1838
5702.6135 | 525.4111 | 435.165 | 420.4619
5703.6135 | 525.1569 | 435.3234 | 421.381
5704.6135 | 525.0567 | 435.3141 | 419.7142
5705.6135 | 525.0264 | 435.2678 | 421.2603
5706.6135 | 525.0289 | 435.298 | 420.7522
5707.6135 | 525.1696 | 435.3494 | 421.4276
5708.6135 | 525.1388 | 435.4493 | 421.9506
5709.6135 | 525.1154 | 435.639 | 421.6736
5710.6135 | 525.1356 | 435.7905 | 421.06
5711.6135 | 525.1283 | 435.8651 | 419.4852
5712.6135 | 525.0649 | 435.9708 | 419.8058
5713.6135 | 525.1118 | 436.0807 | 420.5607
5714.6135 | 525.3142 | 436.1309 | 420.455
5715.6135 | 525.3704 | 436.1371 | 421.8226
5716.6135 | 525.1597 | 436.168 | 420.2167
5717.6135 | 525.2443 | 436.2141 | 421.4957
5718.6135 | 525.3287 | 436.2618 | 422.5233
5719.6135 | 525.3278 | 436.2692 | 422.8951
5720.6135 | 525.2918 | 436.3655 | 424.6267
5721.6135 | 525.354 | 436.4898 | 423.7313
5722.6135 | 525.3284 | 436.5827 | 423.5447
5723.6135 | 525.3381 | 436.5884 | 425.3453
5724.6135 | 525.3668 | 436.5879 | 426.6545
5725.6135 | 525.3594 | 436.5669 | 426.2656
5726.6135 | 525.2826 | 436.6478 | 427.3796
5727.6135 | 525.08 | 436.6711 | 427.9871
5728.6135 | 525.1715 | 436.5848 | 427.4122
5729.6135 | 525.2771 | 436.4495 | 428.0423
5730.6135 | 525.2991 | 436.3339 | 428.7521
5731.6135 | 525.1161 | 436.2579 | 428.4477
5732.6135 | 524.9234 | 436.2834 | 426.7298
5733.6135 | 524.7457 | 436.3606 | 426.5254
5734.6135 | 524.5812 | 436.4862 | 426.7373
5735.6135 | 524.418 | 436.6353 | 424.0157
5736.6135 | 524.2443 | 436.6839 | 421.184
5737.6135 | 524.309 | 436.7609 | 423.3584
5738.6135 | 524.3747 | 436.8978 | 424.9684
5739.6135 | 524.4046 | 436.9909 | 423.9937
5740.6135 | 524.2756 | 437.0904 | 421.7289
5741.6135 | 524.2714 | 437.1295 | 422.2345
5742.6135 | 524.362 | 437.1719 | 424.5781
5743.6135 | 524.4042 | 437.2718 | 423.6426
5744.6135 | 524.5423 | 437.3508 | 423.2012
5745.6135 | 524.5775 | 437.4296 | 421.6997
5746.6135 | 524.5789 | 437.4273 | 421.1415
5747.6135 | 524.5233 | 437.5171 | 421.7727
5748.6135 | 524.4203 | 437.6504 | 421.129
5749.6135 | 524.4717 | 437.709 | 422.9345
5750.6135 | 524.5173 | 437.8633 | 423.7327
5751.6135 | 524.4887 | 437.9901 | 425.0933
5752.6135 | 524.7361 | 437.9742 | 424.1634
5753.6135 | 524.6913 | 437.8662 | 426.275
5754.6135 | 524.6004 | 437.7624 | 426.764
5755.6135 | 524.6805 | 437.7309 | 426.7901
5756.6135 | 524.8309 | 437.6437 | 424.9156
5757.6135 | 524.8621 | 437.554 | 425.8565
5758.6135 | 525.0533 | 437.6089 | 425.1174
5759.6135 | 525.049 | 437.6021 | 424.0662
5760.6135 | 525.0806 | 437.5968 | 424.6501
5761.6135 | 525.2783 | 437.6359 | 424.4999
5762.6135 | 525.3687 | 437.726 | 425.5698
5763.6135 | 525.4155 | 437.8195 | 423.4585
5764.6135 | 525.2158 | 437.8433 | 423.2278
5765.6135 | 525.1841 | 437.9463 | 424.3657
5766.6135 | 525.2729 | 437.9499 | 426.4463
5767.6135 | 525.1559 | 437.965 | 426.1704
5768.6135 | 524.8901 | 437.9644 | 426.1001
5769.6135 | 524.7371 | 437.9749 | 426.0896
5770.6135 | 524.6248 | 437.9456 | 425.3778
5771.6135 | 524.6206 | 438.0177 | 426.1609
5772.6135 | 524.7737 | 438.1312 | 424.7662
5773.6135 | 524.6976 | 438.24 | 424.9672
5774.6135 | 524.7007 | 438.2447 | 424.8726
5775.6135 | 524.6864 | 438.2394 | 424.3342
5776.6135 | 524.6377 | 438.3357 | 425.2398
5777.6135 | 524.5298 | 438.3003 | 426.9939
5778.6135 | 524.4668 | 438.2918 | 427.8192
5779.6135 | 524.4842 | 438.2771 | 427.2988
5780.6135 | 524.5564 | 438.214 | 427.3896
5781.6135 | 524.5076 | 438.1987 | 425.8386
5782.6135 | 524.5931 | 438.2621 | 428.0635
5783.6135 | 524.7585 | 438.326 | 428.3066
5784.6135 | 524.8063 | 438.4836 | 426.3866
5785.6135 | 524.7193 | 438.6573 | 426.9362
5786.6135 | 524.7474 | 438.7069 | 427.8077
5787.6135 | 524.7249 | 438.7382 | 427.6756
5788.6135 | 524.8723 | 438.6804 | 427.2924
5789.6135 | 524.9794 | 438.6469 | 429.5969
5790.6135 | 524.9893 | 438.6799 | 429.6241
5791.6135 | 525.074 | 438.7957 | 428.5404
5792.6135 | 525.0248 | 438.8367 | 427.611
5793.6135 | 525.1045 | 438.8847 | 428.3797
5794.6135 | 525.0771 | 438.9463 | 428.6032
5795.6135 | 524.9726 | 439.0467 | 425.7184
5796.6135 | 524.7904 | 439.1778 | 422.4266
5797.6135 | 524.9072 | 439.3627 | 422.5042
5798.6135 | 524.9238 | 439.4851 | 423.9139
5799.6135 | 524.8023 | 439.556 | 424.7412
5800.6135 | 524.9359 | 439.6044 | 425.5424
5801.6135 | 524.8914 | 439.6169 | 426.1332
5802.6135 | 525.0834 | 439.5521 | 424.6526
5803.6135 | 525.3727 | 439.4801 | 425.9811
5804.6135 | 525.4307 | 439.38 | 425.1522
5805.6135 | 525.511 | 439.323 | 424.6705
5806.6135 | 525.654 | 439.1576 | 424.5642
5807.6135 | 525.5886 | 439.024 | 425.5922
5808.6135 | 525.6431 | 438.9184 | 426.3433
5809.6135 | 525.4936 | 438.8279 | 426.8563
5810.6135 | 525.5486 | 438.8149 | 425.7621
5811.6135 | 525.7169 | 438.7976 | 425.9642
5812.6135 | 525.8786 | 438.835 | 428.0469
5813.6135 | 525.9066 | 438.9539 | 429.0077
5814.6135 | 525.8438 | 439.147 | 426.7123
5815.6135 | 525.8798 | 439.2695 | 424.9561
5816.6135 | 525.6726 | 439.3401 | 423.6738
5817.6135 | 525.4749 | 439.4162 | 422.4925
5818.6135 | 525.5578 | 439.5153 | 421.8011
5819.6135 | 525.4552 | 439.6287 | 422.3868
5820.6135 | 525.2372 | 439.5869 | 423.6415