## Test Conditions
DESIREE-FIRE Test Number 30 - Circuit Simulator Data Only
Test Date: | 2009-08-13
DCSim DAQ Start Time | 7:48
DCSim Time for Synchronization | 8:25
Heat Source Synchronization | 0:43 | minutes:seconds
Heat Source DAQ Start Time | 8:24
Fire Time | 8:27
Offset | 0:39 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2340 | seconds
Heat Source Offset | 0:03 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 163 | seconds
Heat Source Stop Time | 9:11
Test Duration | 0:44 | minutes:seconds
| 2612 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | Tefzel/Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | Tefzel/Tefzel, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.17188 | 123.2712 | -59.9533 | 62.9791 | -0.052796 | 0.0019803 | 0.063213 | 0.064882 | 0.00025629 | 0.0041358 | -0.00054907 | 0.011932 | 0.0020208 | 0.063854 | 0.061788 | -0.002068 | 0.00053824 | -0.00036747 | 0.041199 | 62.8326 | -60.054 | 63.1119 | -59.761 | -60.0861 | 0.11444 | 0.13733 | 62.8555 | -59.9716 | 63.121 | -59.9258 | -60.022 | -59.9533 | -0.10071 | -0.14648 | 0.13275 | 0.19226 | 60.0677 | -0.13275 | 60.1685 | -0.032044 | -0.018311 | -0.1236 | 0.14191 | 0.027466 | 0 | -0.068665 | 0.018311 | -0.050354 | 0.29297 | 123.1659 | 0.045777 | 123.0927 | 122.8867 | 122.8271 | 122.7859 | 122.8088 | -123.0331 | -122.9507 | 123.0652 | 123.0743 | 59.9945 | 60.0906
0.89062 | 123.262 | -59.9808 | 62.9105 | -0.098572 | 0.0015529 | 0.064709 | 0.067232 | 0.00068369 | 0.00029044 | -0.00097627 | -0.039948 | 0.0009528 | 0.064922 | 0.061575 | -0.0035632 | 0.003529 | 0.0017687 | -0.041199 | 62.8098 | -60.0952 | 63.0569 | -59.8663 | -60.2188 | -0.032043 | 0.13733 | 62.8601 | -59.9762 | 63.0569 | -59.9854 | -60.0632 | -59.9533 | -0.11444 | -0.10071 | 0.14649 | 0.11444 | 59.9487 | -0.23804 | 60.0632 | -0.1236 | 0.004578 | -0.050354 | 0.14649 | -0.004578 | 0.027466 | -0.082397 | 0.022888 | -0.086975 | 0.22888 | 123.1522 | -0.009156 | 123.0331 | 122.905 | 122.8363 | 122.7905 | 122.8409 | -123.0057 | -122.8867 | 123.0377 | 123.0377 | 59.9396 | 60.1181
1.8281 | 123.2666 | -59.9625 | 62.9654 | -0.075684 | -0.00079686 | 0.064281 | 0.061891 | -0.0031617 | -0.0012048 | -0.0011899 | 0.011932 | 0.00138 | 0.065563 | 0.069906 | -0.0016406 | 0.0033154 | -0.0027173 | 0.045776 | 62.8555 | -60.0311 | 63.1165 | -59.761 | -60.1227 | 0.1236 | 0.13733 | 62.851 | -59.935 | 63.1165 | -59.935 | -60.0266 | -59.9487 | -0.068665 | -0.10986 | 0.15106 | 0.20142 | 60.0861 | -0.16022 | 60.1547 | -0.091553 | 0.027465 | -0.11444 | 0.15106 | 0.027465 | 0.013733 | -0.064087 | -0.013732 | -0.091552 | 0.27008 | 123.1476 | 0 | 123.0515 | 122.8867 | 122.7859 | 122.818 | 122.8134 | -122.9965 | -122.9004 | 123.0789 | 123.0789 | 60.0082 | 60.0998
2.8906 | 123.2117 | -60.022 | 62.9105 | -0.037537 | 0.00048494 | 0.065136 | 0.065523 | 0.0021789 | -0.0012048 | -0.00076267 | -0.067413 | 0.0015936 | 0.065777 | 0.060293 | -0.0033496 | 0.0041698 | -0.00058107 | -0.086975 | 62.8281 | -60.1089 | 62.97 | -59.9487 | -60.3058 | -0.082397 | -0.10529 | 62.8464 | -60.0403 | 63.0249 | -59.9442 | -60.26 | -60.1227 | -0.086975 | -0.082397 | 0.05951 | 0.073243 | 59.9396 | -0.28381 | 60.0266 | -0.19684 | -0.01831 | -0.064086 | 0.11444 | 0.07782 | -0.10071 | -0.23804 | -0.082398 | -0.21973 | 0.16022 | 123.0789 | 0.09613 | 123.0652 | 122.937 | 122.8867 | 122.85 | 122.8683 | -123.0194 | -122.9507 | 122.9919 | 123.0469 | 59.935 | 59.9167
3.8281 | 123.2895 | -59.9304 | 62.9517 | -0.075684 | 0.0013393 | 0.062145 | 0.066377 | 0.0015381 | 7.6842e-05 | -0.00097627 | 0.048553 | -0.000329 | 0.06599 | 0.069906 | -0.0039906 | 0.00075204 | 0.0036913 | 0.027466 | 62.8601 | -60.0494 | 63.1073 | -59.7839 | -60.1364 | 0.09613 | 0.12817 | 62.8418 | -59.9762 | 63.1393 | -59.903 | -59.9991 | -59.935 | -0.11902 | -0.091553 | 0.15564 | 0.14648 | 60.0266 | -0.20599 | 60.1456 | -0.086976 | -0.045776 | -0.10986 | 0.18768 | 0.027466 | -0.004578 | -0.068664 | 0.041198 | -0.022888 | 0.2655 | 123.1567 | 0.073242 | 123.1155 | 122.9095 | 122.818 | 122.7905 | 122.7722 | -123.0011 | -122.9279 | 123.0377 | 123.0698 | 59.9579 | 60.0586
4.8906 | 123.262 | -59.9808 | 62.9242 | -0.1062 | 0.0015529 | 0.063641 | 0.065309 | -0.00038451 | -0.00077756 | -0.0018307 | -0.030792 | 0.0011664 | 0.066204 | 0.06777 | -0.0027088 | 0.0024608 | -0.0025037 | -0.027466 | 62.8143 | -60.0769 | 63.0524 | -59.8526 | -60.2234 | -0.036621 | -0.018311 | 62.796 | -60.0174 | 63.0844 | -59.9945 | -60.1089 | -59.9625 | -0.09613 | -0.10986 | 0.12817 | 0.12817 | 59.9442 | -0.24262 | 60.0403 | -0.14648 | -0.036621 | -0.12817 | 0.16022 | -0.013733 | 0.018311 | -0.12817 | 0.054932 | -0.091553 | 0.2243 | 123.1293 | 0.022888 | 123.1018 | 122.8912 | 122.8134 | 122.7951 | 122.7768 | -123.0011 | -122.9416 | 123.0331 | 123.0652 | 59.9533 | 59.9625
5.8281 | 123.2849 | -59.9442 | 62.9745 | -0.068054 | -0.0027195 | 0.065136 | 0.067018 | -0.0031617 | -0.00035036 | -0.00054907 | 0.018036 | 9.8198e-05 | 0.065349 | 0.066061 | -0.003136 | 0.0033154 | 0.0032641 | 0.050354 | 62.8372 | -60.0266 | 63.1165 | -59.7748 | -60.1318 | 0.1236 | 0.15106 | 62.8464 | -59.9487 | 63.1073 | -59.9213 | -60.0403 | -59.9533 | -0.082397 | -0.13733 | 0.14191 | 0.16937 | 60.0677 | -0.18768 | 60.1501 | -0.10529 | -0.004577 | -0.12817 | 0.13275 | 0.022888 | -0.009155 | -0.09613 | -0.004578 | -0.091553 | 0.25177 | 123.143 | 0.027465 | 123.056 | 122.8638 | 122.7951 | 122.7814 | 122.7905 | -123.0011 | -122.9233 | 123.0606 | 123.0515 | 59.9945 | 60.0952
6.8906 | 123.262 | -59.9899 | 62.9425 | -0.068054 | 0.00027134 | 0.063641 | 0.066804 | 0.0017517 | -0.0012048 | -0.0016171 | -0.076569 | 0.0015936 | 0.064495 | 0.064352 | -0.0022816 | 0.003529 | -0.0018629 | -0.10529 | 62.8372 | -60.1135 | 62.9791 | -59.935 | -60.2509 | -0.07782 | -0.07782 | 62.8235 | -60.022 | 63.0661 | -60.0128 | -60.1364 | -60.0037 | -0.1236 | -0.10529 | 0.036621 | 0.054931 | 59.9121 | -0.26093 | 60.0357 | -0.13733 | -0.032044 | -0.11902 | 0.1236 | -0.022888 | -0.013733 | -0.14649 | 0.018311 | -0.11444 | 0.17853 | 123.0927 | 0.009156 | 123.0881 | 122.9507 | 122.8455 | 122.8271 | 122.8134 | -123.056 | -122.9645 | 122.9691 | 123.056 | 59.8846 | 59.9121
7.8281 | 123.2391 | -59.9854 | 62.9425 | -0.068054 | -0.00036966 | 0.064068 | 0.065523 | 0.0011109 | 7.6842e-05 | -0.0011899 | 0.011932 | 9.8198e-05 | 0.066631 | 0.061575 | 6.8432e-05 | 0.0024608 | 0.00070073 | -0.027466 | 62.8555 | -60.0586 | 63.0157 | -59.8755 | -60.2142 | 0.013733 | -0.027466 | 62.8235 | -60.0128 | 63.0661 | -59.9991 | -60.0952 | -59.9762 | -0.073242 | -0.086975 | 0.073242 | 0.10986 | 59.9991 | -0.22888 | 60.0723 | -0.15564 | -0.027465 | -0.11902 | 0.1236 | -0.013732 | 0.009156 | -0.10986 | 0.036621 | -0.082398 | 0.18311 | 123.0743 | 0.013733 | 123.0789 | 122.9141 | 122.8363 | 122.8409 | 122.8088 | -123.0011 | -122.9553 | 123.0011 | 123.0515 | 59.9579 | 59.9579
8.8906 | 123.1476 | -59.9991 | 62.9745 | -0.068054 | 0.0030483 | 0.063641 | 0.064882 | 0.0015381 | 0.00071784 | -0.00012167 | -0.058258 | 9.8198e-05 | 0.064495 | 0.064565 | -0.00057257 | 0.003529 | -0.0014355 | -0.027466 | 62.851 | -60.0815 | 62.9837 | -59.9396 | -60.3012 | -0.064087 | -0.10986 | 62.8693 | -59.9991 | 62.9883 | -60.0952 | -60.2142 | -60.0861 | -0.082398 | -0.1236 | 0.009156 | 0.059509 | 59.935 | -0.30212 | 60.0174 | -0.21973 | 0 | -0.10529 | 0.013733 | -0.096131 | -0.086976 | -0.21515 | -0.086976 | -0.21515 | 0.14191 | 123.0652 | -0.096131 | 122.9874 | 122.9324 | 122.8683 | 122.85 | 122.8683 | -123.056 | -122.9736 | 122.9828 | 122.9874 | 59.9716 | 59.8892
9.8281 | 123.2346 | -59.9579 | 62.9517 | -0.037537 | 5.7742e-05 | 0.064068 | 0.066163 | -0.0042297 | -0.0029138 | -0.0018307 | -0.0033265 | 0.0009528 | 0.068554 | 0.061788 | -0.00099977 | 0.0011792 | -0.00036747 | -0.041199 | 62.8464 | -60.054 | 63.0203 | -59.8846 | -60.2234 | -0.009155 | -0.064087 | 62.8189 | -59.9899 | 63.0341 | -60.0266 | -60.1364 | -60.0082 | -0.09613 | -0.10528 | 0.068665 | 0.073242 | 59.9487 | -0.2655 | 60.0449 | -0.16937 | -0.032043 | -0.13275 | 0.082398 | -0.068664 | -0.050354 | -0.17853 | -0.018311 | -0.14649 | 0.16937 | 123.0743 | -0.036621 | 123.024 | 122.9004 | 122.8088 | 122.8043 | 122.7768 | -123.0057 | -122.9416 | 122.9782 | 122.9919 | 59.9167 | 59.8938
10.8906 | 123.1705 | -60.0128 | 62.9517 | -0.090943 | 0.00048494 | 0.064281 | 0.065095 | 0.0011109 | -0.0012048 | -0.00033547 | -0.097931 | 0.0009528 | 0.064068 | 0.063925 | -0.0012134 | 0.0031018 | -0.0020765 | -0.064087 | 62.8418 | -60.1135 | 62.9379 | -59.9854 | -60.3333 | -0.11444 | -0.14648 | 62.8693 | -60.022 | 62.9837 | -60.1273 | -60.2325 | -60.0861 | -0.10071 | -0.10986 | -0.013733 | 0.027465 | 59.8984 | -0.32044 | 59.9991 | -0.21973 | -0.009156 | -0.082397 | 0.032044 | -0.11444 | -0.073243 | -0.21973 | -0.064087 | -0.21057 | 0.12817 | 123.0515 | -0.10528 | 123.0057 | 122.9553 | 122.8912 | 122.8546 | 122.8821 | -123.0652 | -122.9736 | 122.9507 | 122.9965 | 59.9487 | 59.8663
11.8281 | 123.2346 | -59.9762 | 62.9517 | -0.1062 | -0.00036966 | 0.065777 | 0.064882 | -0.0027343 | -0.0018458 | -0.0033261 | -0.0063781 | -0.0016108 | 0.067699 | 0.063711 | -0.0027088 | 0.0039562 | -0.0012219 | -0.036621 | 62.8372 | -60.0586 | 63.0295 | -59.8709 | -60.2097 | -0.027466 | -0.032043 | 62.8281 | -60.022 | 63.0386 | -60.0128 | -60.1227 | -60.0174 | -0.082398 | -0.11444 | 0.07782 | 0.10529 | 59.9487 | -0.23346 | 60.0311 | -0.15106 | -0.045777 | -0.1236 | 0.086975 | -0.036621 | -0.041199 | -0.14648 | 0.004578 | -0.10071 | 0.18768 | 123.0881 | 0.009156 | 123.0606 | 122.8958 | 122.85 | 122.8134 | 122.8043 | -123.0103 | -122.9736 | 123.0057 | 123.0148 | 59.9396 | 59.9442
12.8906 | 123.2346 | -59.9945 | 62.9379 | -0.1062 | 0.00069854 | 0.063213 | 0.066591 | -0.00081171 | -0.00099116 | 0.0011599 | -0.055206 | 0.0020208 | 0.064281 | 0.066488 | -0.0035632 | 0.00182 | -0.0010083 | -0.091553 | 62.851 | -60.1089 | 62.9745 | -59.935 | -60.3012 | -0.086975 | -0.16479 | 62.8555 | -60.0037 | 63.0432 | -60.0632 | -60.1593 | -60.022 | -0.11444 | -0.086975 | 0.036621 | 0.059509 | 59.9075 | -0.3067 | 60.022 | -0.19226 | -0.009155 | -0.082397 | 0.10529 | -0.068664 | -0.027466 | -0.16479 | -0.018311 | -0.15564 | 0.17395 | 123.0835 | -0.059509 | 123.0469 | 122.9599 | 122.8592 | 122.8455 | 122.85 | -123.0469 | -122.9416 | 122.9691 | 123.0377 | 59.903 | 59.8297
13.8281 | 123.2254 | -59.9945 | 62.9745 | -0.090943 | -0.00036966 | 0.064922 | 0.064668 | -0.0018799 | -0.00099116 | 9.193e-05 | 0.014984 | 0.0007392 | 0.063854 | 0.060293 | -0.00099977 | 0.0031018 | 0.00048713 | -0.041199 | 62.8281 | -60.0494 | 63.0112 | -59.8755 | -60.2325 | -0.004578 | -0.032043 | 62.8464 | -60.0174 | 63.0524 | -60.0128 | -60.1089 | -60.0037 | -0.054931 | -0.14648 | 0.036621 | 0.11902 | 59.9899 | -0.23804 | 60.0449 | -0.18311 | -0.022888 | -0.12817 | 0.07782 | -0.01831 | -0.009155 | -0.11444 | 0.013733 | -0.091553 | 0.17395 | 123.0606 | 0.004578 | 123.0698 | 122.8775 | 122.8638 | 122.8226 | 122.8409 | -123.024 | -122.9919 | 123.0057 | 123.0469 | 59.9533 | 59.9625
14.8906 | 123.2803 | -60.0082 | 62.9105 | -0.12909 | -0.00036966 | 0.064709 | 0.064668 | 0.0019653 | -0.0012048 | -0.00097627 | -0.052155 | 0.0018072 | 0.061718 | 0.062856 | -0.00057257 | 0.0031018 | 0.0013415 | -0.013733 | 62.7914 | -60.0815 | 63.0569 | -59.8526 | -60.2051 | -0.022888 | -0.013733 | 62.8143 | -60.0037 | 63.089 | -59.9762 | -60.1044 | -59.9533 | -0.073242 | -0.11902 | 0.14649 | 0.15564 | 59.9854 | -0.19684 | 60.0586 | -0.1236 | 0.004578 | -0.09613 | 0.17853 | 0.032044 | 0.054932 | -0.09613 | 0.050354 | -0.10071 | 0.22888 | 123.1384 | 0.027466 | 123.0927 | 122.8729 | 122.818 | 122.7997 | 122.8226 | -122.9919 | -122.9141 | 123.0652 | 123.0972 | 59.9945 | 59.9945
15.8281 | 123.2437 | -59.9854 | 62.9562 | -0.1062 | 5.7742e-05 | 0.065136 | 0.065095 | -0.0027343 | 7.6842e-05 | -0.0018307 | -0.0063781 | 0.0009528 | 0.063427 | 0.062856 | -0.00099977 | 0.0016064 | -0.00079467 | -0.041199 | 62.8281 | -60.0815 | 63.0249 | -59.8755 | -60.2417 | -0.022888 | -0.050354 | 62.8326 | -59.9991 | 63.0661 | -60.0128 | -60.0998 | -60.0128 | -0.09613 | -0.12817 | 0.068664 | 0.10986 | 59.9625 | -0.25635 | 60.0586 | -0.16022 | -0.013732 | -0.1236 | 0.10986 | -0.027465 | -0.027465 | -0.11444 | -0.013733 | -0.10071 | 0.20599 | 123.1064 | -0.013733 | 123.0652 | 122.9095 | 122.8317 | 122.8134 | 122.818 | -123.0377 | -122.9553 | 123.0103 | 123.0515 | 59.9442 | 59.935
16.8906 | 123.1979 | -59.9625 | 62.9974 | -0.075684 | -0.00079686 | 0.061932 | 0.06595 | 0.0015381 | 0.00029044 | 0.00094633 | -0.13455 | 0.0022346 | 0.065349 | 0.066488 | -0.003136 | 0.0041698 | -0.0020765 | 0.004578 | 62.8876 | -60.0494 | 62.9974 | -59.9213 | -60.2463 | 0.027466 | 0.054932 | 62.8967 | -59.9716 | 63.0432 | -60.0037 | -60.141 | -60.0037 | -0.086975 | -0.10986 | 0 | 0.041198 | 59.9899 | -0.28381 | 60.0769 | -0.19684 | -0.009156 | -0.10071 | 0.045776 | -0.041199 | -0.041199 | -0.17853 | -0.032043 | -0.16937 | 0.12817 | 123.0469 | -0.032043 | 123.0148 | 122.937 | 122.8683 | 122.85 | 122.8592 | -123.0469 | -122.9691 | 122.9599 | 123.0057 | 59.967 | 60.0174
17.8281 | 123.2666 | -59.9716 | 62.9242 | -0.090943 | 0.0013393 | 0.064068 | 0.0636 | -0.00059811 | 0.00029044 | 0.00094633 | -0.033844 | -0.000329 | 0.066418 | 0.06542 | -0.0035632 | 0.0024608 | -0.0025037 | -0.018311 | 62.7823 | -60.0906 | 63.0753 | -59.8206 | -60.2005 | -0.022888 | -0.013733 | 62.8143 | -59.9854 | 63.0981 | -59.9854 | -60.1044 | -59.9716 | -0.11902 | -0.14191 | 0.15106 | 0.15106 | 59.9487 | -0.22888 | 60.0677 | -0.10986 | -0.013733 | -0.10986 | 0.17395 | -0.013733 | 0 | -0.13275 | 0.013733 | -0.11902 | 0.27008 | 123.1659 | 0 | 123.0835 | 122.8729 | 122.7997 | 122.7539 | 122.7859 | -123.0148 | -122.9095 | 123.0469 | 123.0698 | 59.9533 | 59.9579
18.8906 | 123.1796 | -59.9899 | 62.9745 | -0.029907 | 0.00048494 | 0.063854 | 0.067232 | -0.0014527 | -0.0014184 | 0.00030553 | -0.085724 | 0.0028754 | 0.066845 | 0.069265 | -0.001427 | 0.0043836 | -0.00058107 | -0.009155 | 62.8601 | -60.0769 | 63.0157 | -59.8938 | -60.2509 | -0.004578 | -0.013733 | 62.8693 | -60.0174 | 63.0203 | -60.0632 | -60.1776 | -60.0449 | -0.086975 | -0.11444 | 0.041199 | 0.09613 | 59.9854 | -0.26093 | 60.0723 | -0.17395 | -0.027466 | -0.10529 | 0.045777 | -0.073242 | -0.054932 | -0.18768 | -0.027466 | -0.16022 | 0.1831 | 123.0927 | -0.045776 | 123.0377 | 122.937 | 122.8867 | 122.85 | 122.8592 | -123.0515 | -122.9919 | 123.0057 | 123.0103 | 59.9808 | 59.9762
19.8281 | 123.2712 | -59.9854 | 62.9105 | -0.15961 | 0.0015529 | 0.064922 | 0.06595 | -0.00017091 | -0.00099116 | 0.0013735 | -0.024689 | 0.0003118 | 0.065563 | 0.061361 | -0.0027088 | 0.0031018 | -0.0042127 | -0.013733 | 62.8143 | -60.0403 | 63.0569 | -59.8251 | -60.1868 | -0.009155 | -0.018311 | 62.8235 | -59.9991 | 63.0798 | -59.9762 | -60.0861 | -59.967 | -0.054931 | -0.09613 | 0.14649 | 0.16022 | 59.9762 | -0.20142 | 60.0311 | -0.14648 | -0.013732 | -0.086975 | 0.16937 | 0.009156 | 0.018311 | -0.10071 | 0.032043 | -0.086976 | 0.21515 | 123.0972 | 0.022888 | 123.0789 | 122.8546 | 122.8226 | 122.7997 | 122.8088 | -122.9507 | -122.9095 | 123.0423 | 123.0652 | 59.9716 | 59.967
20.8906 | 123.2162 | -59.9991 | 63.002 | -0.037537 | -0.0012241 | 0.064709 | 0.065095 | 0.0017517 | -0.0018458 | -0.0018307 | -0.042999 | 0.00138 | 0.066631 | 0.058798 | -0.003136 | 0.0020336 | -0.00015387 | -0.068665 | 62.8738 | -60.0861 | 63.0295 | -59.8892 | -60.2142 | 0.036621 | 0.013733 | 62.8876 | -59.9808 | 63.0478 | -60.0037 | -60.1273 | -60.0128 | -0.086976 | -0.12817 | 0.027466 | 0.10986 | 60.0357 | -0.21515 | 60.1227 | -0.12817 | 0.01831 | -0.11444 | 0.045777 | -0.004578 | -0.013733 | -0.12817 | -0.032043 | -0.14648 | 0.19684 | 123.1155 | -0.022888 | 123.0286 | 122.9599 | 122.8683 | 122.8729 | 122.8867 | -123.0881 | -122.9828 | 123.0286 | 123.0469 | 59.9304 | 60.0128
21.8281 | 123.2712 | -59.9991 | 62.915 | -0.037537 | 0.0028347 | 0.063427 | 0.065309 | 0.0030335 | 0.0017858 | 0.0018009 | -0.033844 | 0.0018072 | 0.066631 | 0.066915 | -0.0018542 | 0.0028882 | -0.00058107 | -0.032043 | 62.8235 | -60.0861 | 63.0524 | -59.848 | -60.1959 | -0.032043 | -0.013733 | 62.8189 | -59.9899 | 63.089 | -59.9899 | -60.0952 | -59.9625 | -0.086976 | -0.091553 | 0.13733 | 0.15106 | 59.967 | -0.19684 | 60.054 | -0.10986 | 0.009155 | -0.09613 | 0.17395 | 0.009155 | 0.036621 | -0.096131 | 0.027466 | -0.10529 | 0.23804 | 123.1384 | 0 | 123.0789 | 122.9095 | 122.8088 | 122.8226 | 122.818 | -123.0011 | -122.905 | 123.0515 | 123.0881 | 59.967 | 59.9854
22.8906 | 123.1522 | -60.0082 | 62.9929 | -0.007019 | 5.7742e-05 | 0.063213 | 0.066804 | -0.00059811 | -0.0014184 | -0.0016171 | -0.042999 | 0.0039434 | 0.067058 | 0.063284 | -0.0024952 | 0.0026746 | 0.0019823 | 0 | 62.915 | -60.0677 | 62.9883 | -59.9304 | -60.2417 | 0.018311 | -0.032043 | 62.915 | -60.0037 | 63.0386 | -60.0449 | -60.1456 | -60.0494 | -0.059509 | -0.07782 | -0.004578 | 0.07782 | 60.0266 | -0.23346 | 60.0861 | -0.17395 | 0.004578 | -0.07782 | 0.045776 | -0.036621 | -0.041198 | -0.13733 | -0.045776 | -0.14191 | 0.13733 | 123.056 | -0.041199 | 123.0423 | 122.9828 | 122.9187 | 122.9233 | 122.9233 | -123.0606 | -122.9965 | 122.9965 | 123.0469 | 60.0082 | 59.9762
23.8281 | 123.2391 | -59.9991 | 62.9608 | -0.098572 | 0.0017667 | 0.064068 | 0.064668 | -0.0014527 | 7.6842e-05 | -0.0020443 | -0.042999 | 0.0007392 | 0.065349 | 0.066274 | -0.0012134 | 0.0011792 | 0.0028369 | -0.068665 | 62.851 | -60.0906 | 62.97 | -59.9167 | -60.2509 | -0.07782 | -0.073242 | 62.8326 | -60.022 | 63.0707 | -60.0082 | -60.1181 | -59.9808 | -0.091553 | -0.10986 | 0.009156 | 0.082397 | 59.9213 | -0.25177 | 60.0128 | -0.16022 | -0.022889 | -0.12817 | 0.10986 | -0.009156 | 0.01831 | -0.11902 | 0.041199 | -0.09613 | 0.17395 | 123.0606 | 0.013733 | 123.0927 | 122.9416 | 122.8546 | 122.85 | 122.8317 | -123.0515 | -122.9828 | 122.9691 | 123.0698 | 59.9304 | 59.9258
24.8906 | 123.1888 | -59.9716 | 62.9791 | -0.037537 | 0.00069854 | 0.062786 | 0.067872 | 0.00046989 | -0.0018458 | 0.00051913 | -0.049103 | -0.000329 | 0.065136 | 0.058798 | -0.00099977 | 0.003529 | 0.0015551 | 0.032043 | 62.9013 | -60.0815 | 63.0203 | -59.8709 | -60.2097 | 0.032043 | 0.045776 | 62.8601 | -59.9899 | 63.0386 | -60.0128 | -60.1273 | -60.0128 | -0.10986 | -0.07782 | 0.041199 | 0.10071 | 60.0037 | -0.23804 | 60.1135 | -0.12817 | -0.01831 | -0.11902 | 0.059509 | -0.041198 | -0.041198 | -0.15564 | -0.022888 | -0.13733 | 0.21057 | 123.1018 | -0.022888 | 123.0286 | 122.9828 | 122.85 | 122.8729 | 122.8317 | -123.0606 | -122.9691 | 122.9919 | 123.0103 | 60.0037 | 60.0174
25.8281 | 123.1796 | -60.0311 | 62.9517 | -0.083313 | -0.00036966 | 0.063213 | 0.06595 | 0.0026063 | 0.0030676 | -0.0014035 | -0.039948 | 0.00138 | 0.06364 | 0.063925 | -0.0012134 | 0.0024608 | 0.0013415 | -0.082397 | 62.8418 | -60.1181 | 62.9425 | -59.9716 | -60.3195 | -0.10529 | -0.12817 | 62.8326 | -60.022 | 62.9929 | -60.0861 | -60.2005 | -60.054 | -0.086975 | -0.10986 | -0.009155 | 0.059509 | 59.9258 | -0.28839 | 60.0128 | -0.20142 | 0.009155 | -0.11902 | 0.041199 | -0.054932 | -0.022888 | -0.16937 | -0.032043 | -0.17853 | 0.14648 | 123.0606 | -0.064087 | 123.0148 | 122.9599 | 122.8546 | 122.8729 | 122.8638 | -123.0698 | -122.9736 | 122.9736 | 123.024 | 59.9487 | 59.903
26.8906 | 123.1888 | -59.967 | 62.9745 | -0.068054 | -0.00058326 | 0.065777 | 0.06595 | 0.00089729 | -0.0031274 | -0.00097627 | -0.039948 | 0.0009528 | 0.066204 | 0.064779 | -0.001427 | 0.0016064 | 0.0056139 | 0 | 62.8693 | -60.0815 | 63.0157 | -59.8755 | -60.2142 | 0.018311 | 0.004578 | 62.883 | -60.0311 | 63.0341 | -60.0586 | -60.1639 | -60.0266 | -0.11444 | -0.10529 | 0.041199 | 0.091553 | 59.9854 | -0.24719 | 60.0998 | -0.13275 | -0.064087 | -0.091552 | 0.05951 | -0.091553 | -0.059509 | -0.19684 | 0.004578 | -0.13275 | 0.20599 | 123.0972 | -0.027466 | 123.0652 | 122.9507 | 122.9141 | 122.8363 | 122.85 | -123.056 | -123.0057 | 122.9828 | 123.0011 | 59.967 | 59.9716
27.8281 | 123.2803 | -59.9899 | 62.9288 | -0.1062 | 0.00027134 | 0.064281 | 0.064241 | 0.0015381 | 0.00093144 | -0.00097627 | -0.018585 | -0.0001154 | 0.066418 | 0.060934 | -0.0012134 | 0.0031018 | -0.0016493 | -0.064087 | 62.8189 | -60.0861 | 62.9974 | -59.8801 | -60.228 | -0.036621 | -0.045776 | 62.8326 | -59.9991 | 63.0707 | -59.9945 | -60.1044 | -59.9533 | -0.096131 | -0.10986 | 0.068665 | 0.10986 | 59.9533 | -0.23804 | 60.0494 | -0.14191 | -0.009155 | -0.09613 | 0.14191 | -0.004578 | 0.036621 | -0.11444 | 0.045776 | -0.10529 | 0.20599 | 123.0835 | 0.004577 | 123.0698 | 122.905 | 122.8317 | 122.8088 | 122.8226 | -123.0148 | -122.9279 | 122.9874 | 123.0606 | 59.9258 | 59.9442
28.8906 | 123.1567 | -59.9991 | 63.0157 | -0.090943 | -0.00058326 | 0.063641 | 0.064668 | -0.00059811 | -0.0016322 | -0.0020443 | 0.0058289 | 0.0007392 | 0.067699 | 0.063284 | 0.00070923 | 0.0031018 | 0.0047595 | 0.032043 | 62.9013 | -60.0449 | 63.0066 | -59.8801 | -60.2051 | 0.050354 | 0.013733 | 62.8922 | -59.9625 | 63.002 | -60.0403 | -60.1501 | -60.0632 | -0.045777 | -0.11444 | -0.009155 | 0.11902 | 60.0494 | -0.20599 | 60.0952 | -0.16022 | 0.036621 | -0.1236 | -0.013733 | -0.041199 | -0.064087 | -0.15106 | -0.10071 | -0.18768 | 0.16479 | 123.0515 | -0.07782 | 122.9645 | 122.9462 | 122.8546 | 122.9004 | 122.8912 | -123.0606 | -122.9782 | 123.0057 | 123.0011 | 60.0311 | 60.0128
29.8281 | 123.1522 | -60.0174 | 62.9425 | -0.098572 | -0.0016513 | 0.064495 | 0.064882 | 0.0011109 | 7.6842e-05 | 0.00094633 | -0.055206 | 0.0022346 | 0.06599 | 0.066488 | -0.001427 | 0.0028882 | -0.0025037 | -0.091553 | 62.8464 | -60.1135 | 62.9196 | -59.9808 | -60.347 | -0.091553 | -0.15106 | 62.8418 | -60.022 | 62.9883 | -60.1227 | -60.2325 | -60.0815 | -0.09613 | -0.09613 | -0.022888 | 0.036621 | 59.9258 | -0.32959 | 60.022 | -0.23346 | -0.004578 | -0.10071 | 0.045776 | -0.10529 | -0.064087 | -0.21515 | -0.059509 | -0.21057 | 0.13275 | 123.0331 | -0.10071 | 123.0103 | 122.9599 | 122.8638 | 122.8638 | 122.8592 | -123.056 | -122.9645 | 122.937 | 123.0057 | 59.9258 | 59.8663
30.8281 | 123.1888 | -60.0037 | 62.9745 | -0.068054 | 0.0011257 | 0.065136 | 0.065095 | -0.00017091 | 0.00029044 | -0.0033261 | -0.052155 | 0.0003118 | 0.065136 | 0.06307 | -0.0016406 | 0.0033154 | -0.0020765 | 0.022888 | 62.883 | -60.0723 | 63.0112 | -59.8618 | -60.2325 | 0.022888 | 0.018311 | 62.8601 | -60.0082 | 63.0386 | -60.0311 | -60.1456 | -60.022 | -0.068665 | -0.091552 | 0.036621 | 0.14191 | 60.0266 | -0.22888 | 60.0952 | -0.16022 | -0.004578 | -0.11444 | 0.064087 | -0.027466 | -0.018311 | -0.14191 | -0.013733 | -0.13733 | 0.21057 | 123.0835 | -0.022888 | 123.0469 | 122.9553 | 122.8683 | 122.8867 | 122.8638 | -123.0469 | -122.9828 | 123.0148 | 123.0423 | 60.0266 | 60.022
31.8906 | 123.262 | -59.935 | 62.97 | -0.045166 | 0.0021939 | 0.062572 | 0.065095 | -0.00038451 | 0.0015722 | -0.0016171 | 0.021088 | -0.0005426 | 0.067699 | 0.062002 | -0.00078617 | 0.00182 | -0.00036747 | 0.004578 | 62.8647 | -60.0403 | 63.0569 | -59.8251 | -60.1501 | 0.07782 | 0.068665 | 62.8418 | -59.9762 | 63.0936 | -59.9716 | -60.0494 | -59.9625 | -0.10529 | -0.10529 | 0.086975 | 0.10986 | 60.0128 | -0.21515 | 60.1181 | -0.10986 | -0.041198 | -0.12817 | 0.1236 | -0.036621 | -0.027465 | -0.11444 | 0.013733 | -0.073242 | 0.21515 | 123.0972 | 0.004577 | 123.0698 | 122.905 | 122.818 | 122.7997 | 122.7768 | -123.0103 | -122.9462 | 122.9919 | 123.0286 | 59.9396 | 60.0037
32.8281 | 123.1705 | -60.0128 | 63.002 | -0.12146 | 0.0024075 | 0.064281 | 0.067659 | 0.0053833 | -0.0027002 | -0.00033547 | -0.055206 | 0.0022346 | 0.063854 | 0.070333 | -0.0022816 | 0.0050244 | 0.0032641 | -0.013733 | 62.8693 | -60.0861 | 62.9883 | -59.9075 | -60.2737 | -0.032043 | -0.032043 | 62.8555 | -59.9945 | 62.9745 | -60.0723 | -60.2051 | -60.0769 | -0.073243 | -0.13275 | -0.013733 | 0.10528 | 59.9808 | -0.26093 | 60.054 | -0.18768 | 0.01831 | -0.14648 | -0.027466 | -0.05951 | -0.064087 | -0.19226 | -0.082397 | -0.21057 | 0.17853 | 123.0743 | -0.07782 | 122.9691 | 122.9553 | 122.85 | 122.8821 | 122.8683 | -123.0881 | -122.9965 | 123.0011 | 122.9874 | 59.9991 | 59.9808
33.8906 | 123.1934 | -59.9945 | 62.9974 | -0.045166 | 0.0017667 | 0.063427 | 0.065095 | 0.0036743 | -0.002273 | 0.00094633 | -0.018585 | 0.0018072 | 0.066631 | 0.063925 | -0.0027088 | 0.0031018 | -0.00058107 | -0.004578 | 62.9059 | -60.0723 | 62.9837 | -59.9258 | -60.2417 | 0.032043 | 0 | 62.8876 | -59.9854 | 63.0066 | -60.0494 | -60.1501 | -60.022 | -0.07782 | -0.091553 | -0.013733 | 0.068665 | 60.0266 | -0.24719 | 60.1044 | -0.16937 | 0.009155 | -0.10986 | 0.009155 | -0.054931 | -0.027466 | -0.15564 | -0.036621 | -0.16479 | 0.14648 | 123.056 | -0.064086 | 122.9919 | 122.9782 | 122.8729 | 122.9004 | 122.8821 | -123.0698 | -122.9828 | 122.9782 | 123.0011 | 59.9899 | 59.9945
34.8281 | 123.1705 | -60.0037 | 62.9837 | 0.00061049 | -0.0010105 | 0.062786 | 0.065523 | 0.0015381 | -0.0014184 | 0.00030553 | -0.055206 | 0.00138 | 0.066631 | 0.062429 | -0.0022816 | 0.0026746 | -0.0039991 | 0.041199 | 62.8738 | -60.0449 | 63.0203 | -59.8801 | -60.2097 | 0.027466 | 0.032043 | 62.8876 | -59.9991 | 63.0432 | -60.0266 | -60.1501 | -59.9991 | -0.041199 | -0.10986 | 0.036621 | 0.1236 | 60.0311 | -0.20599 | 60.0723 | -0.1648 | 0.004578 | -0.096131 | 0.059509 | -0.022888 | 0.004578 | -0.14648 | 0 | -0.15106 | 0.16479 | 123.0652 | -0.027466 | 123.0423 | 122.9187 | 122.8867 | 122.8775 | 122.8912 | -123.0286 | -122.9828 | 123.024 | 123.0469 | 60.0449 | 60.0357
35.8906 | 123.2025 | -59.9991 | 63.0203 | -0.19775 | 0.00048494 | 0.062572 | 0.0636 | -0.00038451 | 0.0015722 | -0.0016171 | 0.018036 | 0.0003118 | 0.064709 | 0.062643 | 0.00049563 | 0.0031018 | 0.0017687 | 0.11902 | 62.8784 | -60.0311 | 63.0386 | -59.8297 | -60.2051 | 0.07782 | 0.054932 | 62.8967 | -59.9762 | 63.0066 | -60.0311 | -60.1318 | -60.0266 | -0.032044 | -0.14191 | 0.01831 | 0.16937 | 60.0769 | -0.20599 | 60.1089 | -0.17395 | 0.022888 | -0.1236 | -0.013733 | -0.032044 | -0.027466 | -0.13275 | -0.050354 | -0.15564 | 0.20142 | 123.0698 | -0.054932 | 122.9828 | 122.9095 | 122.8729 | 122.8775 | 122.8958 | -123.0515 | -122.9965 | 123.0377 | 123.0057 | 60.1181 | 60.054
36.8281 | 123.2071 | -59.9899 | 63.0112 | -0.007019 | -0.00036966 | 0.061291 | 0.065523 | -0.0010253 | -0.00099116 | 9.193e-05 | -0.018585 | 0.0020208 | 0.065777 | 0.05837 | -0.0016406 | 0.0022472 | -0.00079467 | 0.013733 | 62.9105 | -60.0769 | 62.9883 | -59.903 | -60.2371 | 0.036621 | 0.045776 | 62.851 | -59.9945 | 63.0386 | -60.0082 | -60.1456 | -60.022 | -0.086975 | -0.10071 | -0.022888 | 0.086975 | 60.0265 | -0.24719 | 60.1135 | -0.16022 | -0.004578 | -0.16022 | 0.027466 | -0.018311 | -0.032044 | -0.15564 | -0.027466 | -0.15106 | 0.17395 | 123.0652 | -0.013733 | 123.0331 | 122.9874 | 122.8455 | 122.9004 | 122.8409 | -123.0881 | -123.0057 | 122.9782 | 123.0286 | 60.0037 | 60.0357
37.8906 | 123.2941 | -59.9716 | 62.9379 | -0.12146 | 0.0011257 | 0.06535 | 0.064027 | -0.00081171 | 0.001145 | -0.0011899 | 0.0058289 | 0.00138 | 0.066845 | 0.06072 | -0.003136 | 0.0026746 | -0.0016493 | -0.013733 | 62.8235 | -60.0677 | 63.0661 | -59.8343 | -60.2005 | -0.018311 | 0.004578 | 62.8098 | -59.9854 | 63.0844 | -59.9808 | -60.0723 | -59.9442 | -0.09613 | -0.11444 | 0.12817 | 0.13733 | 59.9533 | -0.22888 | 60.0494 | -0.13275 | -0.013733 | -0.12817 | 0.14648 | -0.009155 | 0.027466 | -0.10071 | 0.041199 | -0.086975 | 0.23346 | 123.1338 | 0.004578 | 123.0698 | 122.8912 | 122.7951 | 122.7951 | 122.7814 | -123.0057 | -122.9233 | 123.0377 | 123.056 | 59.9579 | 59.9762
38.8281 | 123.1338 | -59.9808 | 63.0066 | -0.029907 | 0.00091214 | 0.062786 | 0.063386 | 0.00025629 | -0.00056396 | -0.0024717 | -0.015534 | 0.00138 | 0.067699 | 0.060293 | -0.0029224 | 0.0031018 | 0.0017687 | 0.004578 | 62.9105 | -60.0677 | 62.9791 | -59.9121 | -60.2554 | 0.022888 | -0.013733 | 62.9196 | -59.9808 | 63.0112 | -60.054 | -60.1547 | -60.0449 | -0.086975 | -0.096131 | -0.027466 | 0.068665 | 60.0037 | -0.27466 | 60.0906 | -0.18768 | 0 | -0.086975 | 0.004577 | -0.073242 | -0.064087 | -0.17395 | -0.064087 | -0.17395 | 0.15564 | 123.0469 | -0.073242 | 122.9919 | 122.9782 | 122.9004 | 122.8912 | 122.9004 | -123.0743 | -122.9874 | 122.9599 | 122.9919 | 59.9854 | 59.967
39.8906 | 123.23 | -59.9716 | 63.002 | -0.075684 | -0.0012241 | 0.061718 | 0.064668 | -0.0050843 | -0.0033412 | -0.00097627 | 0.045502 | 0.0007392 | 0.065349 | 0.068411 | -0.0035632 | 0.00182 | -0.0039991 | 0.068665 | 62.883 | -60.022 | 63.0798 | -59.8068 | -60.1318 | 0.10529 | 0.10071 | 62.8464 | -59.9716 | 63.0661 | -59.9808 | -60.0449 | -59.967 | -0.050354 | -0.11902 | 0.07782 | 0.16479 | 60.0769 | -0.16022 | 60.1273 | -0.10986 | 0 | -0.15564 | 0.064087 | -0.009155 | 0.004578 | -0.073242 | 0.004578 | -0.073242 | 0.21515 | 123.1018 | -0.009155 | 123.0377 | 122.905 | 122.818 | 122.8546 | 122.818 | -123.024 | -122.9736 | 123.0515 | 123.0377 | 60.0403 | 60.0723
40.8281 | 123.1888 | -59.9899 | 63.0249 | -0.075684 | -0.00036966 | 0.065777 | 0.066163 | -0.0010253 | 0.0015722 | -0.00033547 | -0.033844 | 0.00138 | 0.066631 | 0.066488 | -0.0016406 | 0.0031018 | 0.00027333 | -0.004578 | 62.9105 | -60.0861 | 63.002 | -59.9213 | -60.2417 | 0.032043 | -0.018311 | 62.9242 | -59.9762 | 63.0112 | -60.0357 | -60.1639 | -60.0311 | -0.096131 | -0.11444 | -0.022888 | 0.068664 | 60.022 | -0.25177 | 60.1181 | -0.15564 | 0.013733 | -0.10071 | -0.013733 | -0.045777 | -0.041199 | -0.17395 | -0.054932 | -0.18768 | 0.1648 | 123.0881 | -0.05951 | 122.9874 | 122.9965 | 122.9004 | 122.9004 | 122.9141 | -123.111 | -123.0011 | 122.9919 | 123.0011 | 59.9854 | 59.9716
41.8906 | 123.3032 | -59.9487 | 62.9654 | -0.075684 | 0.0013393 | 0.064281 | 0.064027 | 4.2692e-05 | -0.00035036 | -0.0022581 | 0.057709 | 0.0011664 | 0.06599 | 0.057089 | -0.0018542 | 0.0033154 | -0.0018629 | 0.041199 | 62.8693 | -60.0449 | 63.1027 | -59.7565 | -60.1135 | 0.11444 | 0.16022 | 62.8601 | -59.9579 | 63.1256 | -59.9167 | -60.0449 | -59.9258 | -0.096131 | -0.09613 | 0.13733 | 0.19226 | 60.0632 | -0.1648 | 60.1593 | -0.068664 | -0.009156 | -0.10529 | 0.16022 | 0.032043 | 0.022888 | -0.096131 | 0.032044 | -0.086975 | 0.28839 | 123.1476 | 0.041199 | 123.0835 | 122.9141 | 122.818 | 122.818 | 122.8088 | -123.0103 | -122.9233 | 123.0515 | 123.0743 | 59.9899 | 60.1089
42.8281 | 123.1522 | -59.9899 | 63.0112 | -0.037537 | 0.00027134 | 0.064495 | 0.066591 | -0.0014527 | 0.00071784 | -0.0018307 | -0.046051 | 0.0022346 | 0.065136 | 0.060934 | -0.0016406 | 0.00053824 | -0.0025037 | 0.004578 | 62.8967 | -60.054 | 62.9745 | -59.9075 | -60.2371 | 0.027466 | 0 | 62.8967 | -59.9625 | 62.9837 | -60.141 | -60.0632 | -59.9487 | -0.064087 | -0.11444 | -0.036621 | 0.082397 | 60.0174 | -0.24719 | 60.0815 | -0.18311 | 0.027466 | -0.11444 | -0.027465 | -0.15106 | 0.041199 | -0.073242 | 0.013733 | -0.10071 | 0.14648 | 123.0286 | -0.17853 | 122.9462 | 122.9507 | 122.8592 | 122.8867 | 122.8867 | -123.0652 | -122.9736 | 122.9645 | 122.9736 | 59.9945 | 59.9899
43.8906 | 123.2849 | -59.9533 | 62.9471 | -0.083313 | -0.0012241 | 0.063213 | 0.065736 | 0.0011109 | -0.0012048 | -0.00054907 | 0.036346 | -0.001397 | 0.065563 | 0.058157 | -0.0016406 | 0.00182 | -0.0022901 | 0.013733 | 62.8555 | -60.0357 | 63.0478 | -59.8022 | -60.1456 | 0.082397 | 0.068665 | 62.851 | -59.9533 | 63.1073 | -59.9304 | -60.0357 | -59.9487 | -0.082398 | -0.091553 | 0.10071 | 0.15106 | 60.0357 | -0.19226 | 60.1181 | -0.10986 | 0 | -0.096131 | 0.16022 | 0.022888 | 0.004578 | -0.082398 | 0.004578 | -0.082398 | 0.23346 | 123.0835 | 0.022888 | 123.0606 | 122.8912 | 122.8043 | 122.8088 | 122.8043 | -122.9828 | -122.9004 | 123.0011 | 123.0606 | 59.967 | 60.022
44.8281 | 123.1567 | -59.9808 | 63.0203 | -0.083313 | 0.0013393 | 0.063213 | 0.065736 | 0.0011109 | 0.001145 | -0.0018307 | 0.018036 | 0.0009528 | 0.065777 | 0.062216 | -0.0039906 | 0.0033154 | -0.0027173 | 0.032043 | 62.9013 | -60.0494 | 63.0157 | -59.903 | -60.228 | 0.032043 | 0.036621 | 62.883 | -59.9533 | 62.9837 | -60.022 | -60.1456 | -60.0449 | -0.068664 | -0.11902 | -0.004578 | 0.07782 | 60.0128 | -0.24719 | 60.0815 | -0.17853 | 0.027466 | -0.13733 | -0.036621 | -0.041199 | -0.064087 | -0.1648 | -0.091553 | -0.19226 | 0.14648 | 123.0652 | -0.068665 | 122.937 | 122.9507 | 122.8363 | 122.8821 | 122.8638 | -123.0698 | -122.9736 | 122.9965 | 122.9645 | 60.0128 | 60.0174
45.8906 | 123.2941 | -59.9533 | 62.9562 | -0.007019 | 0.0011257 | 0.062145 | 0.065736 | -0.0010253 | -0.0020594 | 0.00073273 | 0.018036 | -0.001397 | 0.067272 | 0.066061 | -0.00099977 | -0.00052976 | -0.0025037 | 0.032043 | 62.8464 | -60.0449 | 63.0798 | -59.7977 | -60.1273 | 0.086975 | 0.13275 | 62.8281 | -59.9808 | 63.121 | -59.8938 | -60.0174 | -59.9258 | -0.091553 | -0.10986 | 0.1236 | 0.15564 | 60.0403 | -0.17395 | 60.1318 | -0.082397 | -0.027466 | -0.12817 | 0.16479 | 0.059509 | 0.027466 | -0.064087 | 0.054932 | -0.036621 | 0.24719 | 123.1247 | 0.086975 | 123.1018 | 122.8912 | 122.8088 | 122.7997 | 122.7814 | -123.0011 | -122.937 | 123.0331 | 123.0743 | 59.9854 | 60.0861
46.8281 | 123.1842 | -59.9945 | 63.0295 | -0.045166 | 0.0024075 | 0.063641 | 0.067232 | -0.00081171 | -0.00013676 | -0.0024717 | -0.06131 | 0.0022346 | 0.065563 | 0.066061 | -0.0027088 | 0.0056652 | 0.0026233 | 0.004578 | 62.8922 | -60.0861 | 62.9929 | -59.9213 | -60.2646 | 0.022888 | 0.009155 | 62.9059 | -60.0037 | 63.0112 | -60.054 | -60.1639 | -60.0311 | -0.091553 | -0.13733 | -0.036621 | 0.073242 | 60.0174 | -0.27008 | 60.1089 | -0.17853 | -0.009155 | -0.1236 | -0.018311 | -0.059509 | -0.036621 | -0.16937 | -0.027466 | -0.16022 | 0.1648 | 123.0789 | -0.050354 | 123.0148 | 122.9782 | 122.9095 | 122.8867 | 122.9004 | -123.1155 | -123.0331 | 122.9874 | 123.0057 | 59.9991 | 60.0037
47.8906 | 123.2941 | -59.9304 | 62.9517 | -0.098572 | 0.00091214 | 0.062359 | 0.065095 | -0.00017091 | 0.00071784 | -0.0011899 | 0.027191 | 0.0018072 | 0.066631 | 0.065634 | -0.001427 | 0.0028882 | 0.00027333 | 0.041199 | 62.8876 | -60.0266 | 63.089 | -59.7519 | -60.1089 | 0.1236 | 0.16937 | 62.8418 | -59.9533 | 63.1393 | -59.9213 | -60.022 | -59.935 | -0.09613 | -0.064087 | 0.13733 | 0.17853 | 60.054 | -0.17853 | 60.1501 | -0.082398 | -0.022888 | -0.10986 | 0.18768 | 0.009155 | -0.004578 | -0.091553 | 0.01831 | -0.068665 | 0.27466 | 123.1155 | 0.032043 | 123.0927 | 122.9141 | 122.7951 | 122.818 | 122.7722 | -122.9782 | -122.905 | 123.0194 | 123.0698 | 59.9716 | 60.0998
48.8281 | 123.1659 | -59.9899 | 63.0157 | -0.022278 | 5.7742e-05 | 0.061504 | 0.065523 | 0.00068369 | -0.0012048 | -0.00054907 | 0.011932 | 0.0018072 | 0.065349 | 0.064779 | -0.0022816 | 0.0022472 | 0.00027333 | 0.050354 | 62.8784 | -60.0677 | 63.0157 | -59.8572 | -60.228 | 0.054932 | 0.036621 | 62.8967 | -59.967 | 63.0112 | -60.0494 | -60.1364 | -60.0403 | -0.07782 | -0.13733 | 0 | 0.13275 | 60.0449 | -0.23804 | 60.1227 | -0.16022 | 0.022888 | -0.11902 | -0.004578 | -0.059509 | -0.050354 | -0.14649 | -0.073242 | -0.16937 | 0.21057 | 123.0835 | -0.082397 | 122.9782 | 122.9462 | 122.8638 | 122.8683 | 122.8867 | -123.0835 | -122.9828 | 123.0057 | 123.0011 | 60.0403 | 60.0265
49.8281 | 123.143 | -60.0174 | 62.9883 | -0.045166 | 0.0017667 | 0.06535 | 0.067018 | 0.0058105 | -0.0048364 | -0.0011899 | -0.052155 | 0.0011664 | 0.06834 | 0.061788 | -0.0033496 | 0.0039562 | -0.00058107 | 0.013733 | 62.8967 | -60.0769 | 62.9929 | -59.9075 | -60.2417 | 0.022888 | 0.009155 | 62.9105 | -59.9808 | 63.0203 | -60.0311 | -60.1547 | -60.0311 | -0.059509 | -0.091552 | 0.004578 | 0.10986 | 60.0403 | -0.2243 | 60.0998 | -0.16479 | 0.036621 | -0.07782 | 0.032044 | -0.013733 | -0.013733 | -0.13733 | -0.050354 | -0.17395 | 0.16937 | 123.0698 | -0.050354 | 123.0011 | 122.9736 | 122.8912 | 122.9141 | 122.9279 | -123.0652 | -122.9691 | 123.0103 | 123.0377 | 60.0311 | 60.0266
50.8906 | 123.2162 | -59.9991 | 62.9379 | -0.14435 | 0.00091214 | 0.063213 | 0.065523 | 0.0023925 | -0.002273 | -0.0011899 | -0.076569 | 0.0003118 | 0.066631 | 0.062216 | -0.0033496 | 0.0026746 | 0.0017687 | -0.073242 | 62.8784 | -60.1181 | 62.9562 | -59.9716 | -60.3287 | -0.09613 | -0.11444 | 62.8555 | -60.0311 | 63.0432 | -59.9945 | -60.2783 | -60.0998 | -0.11902 | -0.059509 | 0.018311 | 0.027465 | 59.903 | -0.32959 | 60.022 | -0.21057 | -0.032044 | -0.082397 | 0.10529 | 0.004577 | -0.10071 | -0.27924 | -0.068664 | -0.24719 | 0.14648 | 123.0743 | 0.036621 | 123.0743 | 122.9965 | 122.8867 | 122.8775 | 122.8546 | -123.056 | -122.9691 | 122.9553 | 123.0423 | 59.9258 | 59.8846
51.8281 | 123.2025 | -59.9533 | 62.97 | -0.068054 | 0.00091214 | 0.063854 | 0.068513 | -0.0014527 | -0.00013676 | -0.0011899 | -0.06131 | 0.0018072 | 0.066631 | 0.06542 | -0.0029224 | 0.003529 | 0.00070073 | 0.036621 | 62.9059 | -60.0677 | 63.0249 | -59.8663 | -60.2142 | 0.009155 | 0.032043 | 62.8693 | -59.9945 | 63.0432 | -60.0082 | -60.1364 | -60.0037 | -0.11444 | -0.064087 | 0.054931 | 0.086975 | 59.9625 | -0.26093 | 60.0769 | -0.14648 | -0.041199 | -0.10071 | 0.073242 | -0.054932 | -0.050354 | -0.18311 | -0.009155 | -0.14191 | 0.20142 | 123.0927 | -0.013733 | 123.0377 | 122.9736 | 122.8638 | 122.8592 | 122.8226 | -123.0377 | -122.9645 | 122.9782 | 122.9965 | 59.9899 | 59.9854
52.8906 | 123.317 | -59.9533 | 62.9562 | -0.11383 | 5.7742e-05 | 0.062359 | 0.065523 | 0.0011109 | -0.0014184 | 0.0018009 | 0.045502 | 0.0003118 | 0.065136 | 0.05837 | -0.00078617 | 0.0016064 | 0.0013415 | 0.013733 | 62.8601 | -60.0586 | 63.0753 | -59.7656 | -60.1593 | 0.10986 | 0.10071 | 62.8464 | -59.9716 | 63.121 | -59.935 | -60.0174 | -59.9304 | -0.10529 | -0.096131 | 0.11902 | 0.18768 | 60.0632 | -0.20599 | 60.1685 | -0.10071 | -0.018311 | -0.10986 | 0.16479 | 0.01831 | 0.022888 | -0.064087 | 0.041199 | -0.045776 | 0.29297 | 123.1338 | 0.036621 | 123.0927 | 122.9187 | 122.818 | 122.8134 | 122.7997 | -123.0148 | -122.9279 | 123.0286 | 123.0743 | 59.967 | 60.054
53.8281 | 123.1842 | -59.967 | 62.9974 | -0.022278 | 0.0021939 | 0.064281 | 0.064241 | 0.0047425 | -0.0012048 | -0.00054907 | -0.06131 | 0.0009528 | 0.065349 | 0.062429 | -0.00078617 | 0.0022472 | 0.0021961 | -0.068665 | 62.8693 | -60.1044 | 63.0203 | -59.8709 | -60.2097 | 0.045776 | 0.032043 | 62.9013 | -59.9854 | 63.0386 | -60.022 | -60.1181 | -59.9991 | -0.13733 | -0.12817 | 0.022888 | 0.09613 | 60.0128 | -0.24262 | 60.1501 | -0.10529 | -0.018311 | -0.096131 | 0.041198 | -0.054932 | -0.032043 | -0.15106 | -0.013732 | -0.13275 | 0.23346 | 123.1247 | -0.036621 | 123.024 | 122.9736 | 122.8867 | 122.8363 | 122.8683 | -123.1018 | -122.9828 | 122.9874 | 123.0057 | 59.8984 | 59.9991
54.8906 | 123.2346 | -59.9854 | 62.9379 | -0.13672 | 0.0021939 | 0.062572 | 0.064668 | 0.0032471 | -0.00035036 | -0.0011899 | 0.011932 | 0.0015936 | 0.064709 | 0.067983 | -0.0027088 | 0.0020336 | -0.00036747 | -0.068665 | 62.851 | -60.054 | 63.0157 | -59.8846 | -60.2234 | -0.032043 | -0.036621 | 62.8189 | -59.9854 | 63.0341 | -60.0311 | -60.0998 | -59.9945 | -0.068664 | -0.086975 | 0.07782 | 0.10071 | 59.9533 | -0.23804 | 60.022 | -0.16937 | 0 | -0.11902 | 0.096131 | -0.045776 | -0.009155 | -0.11444 | -0.009155 | -0.11444 | 0.16937 | 123.0698 | -0.045776 | 123.0194 | 122.905 | 122.8043 | 122.8363 | 122.8043 | -122.9919 | -122.9233 | 123.0011 | 123.0194 | 59.9167 | 59.9487
55.8281 | 123.1796 | -59.9808 | 63.0112 | -0.007019 | -0.00079686 | 0.063427 | 0.064027 | -0.0025207 | -0.00056396 | -0.0016171 | -0.058258 | 0.0026618 | 0.067699 | 0.062856 | 0.00049563 | 0.0011792 | -0.0020765 | -0.009155 | 62.9105 | -60.0586 | 62.8693 | -60.1547 | -60.1044 | 0.20599 | 0.045776 | 62.915 | -59.967 | 62.9929 | -60.0357 | -60.173 | -60.0677 | -0.07782 | -0.10071 | -0.14191 | -0.17395 | 60.1868 | -0.1236 | 60.2646 | -0.045776 | 0.013733 | -0.09613 | -0.01831 | -0.054932 | -0.086975 | -0.19226 | -0.10071 | -0.20599 | -0.09613 | 122.9279 | -0.068665 | 122.9599 | 122.9691 | 122.8821 | 122.8912 | 122.8958 | -123.0698 | -122.9782 | 122.85 | 122.9736 | 59.9716 | 60.0265
56.8906 | 123.2758 | -59.9533 | 62.9471 | -0.3122 | -0.00058326 | 0.063641 | 0.066377 | -0.0012391 | -0.0014184 | 0.00051913 | 0.024139 | 0.0005256 | 0.067486 | 0.063711 | -0.0037768 | 0.0026746 | -0.00015387 | 0.064087 | 62.8647 | -60.0403 | 63.0798 | -59.7885 | -60.1776 | 0.082397 | 0.1236 | 62.8281 | -59.9716 | 63.1165 | -59.9396 | -60.0082 | -59.9304 | -0.086975 | -0.082398 | 0.13275 | 0.16479 | 60.0357 | -0.2243 | 60.1227 | -0.13733 | -0.018311 | -0.11902 | 0.16937 | 0.013733 | 0.022888 | -0.054932 | 0.041199 | -0.036621 | 0.25177 | 123.1201 | 0.032044 | 123.0881 | 122.905 | 122.7997 | 122.818 | 122.7814 | -122.9874 | -122.9187 | 123.0331 | 123.0698 | 60.0174 | 60.0769
57.8281 | 123.1796 | -59.9854 | 63.002 | -0.045166 | 0.00091214 | 0.062572 | 0.067872 | 0.0023925 | -0.00077756 | -0.00012167 | -0.049103 | 0.0009528 | 0.066631 | 0.061575 | -0.0018542 | 0.0031018 | -0.00079467 | 0.009155 | 62.8876 | -60.0632 | 62.9745 | -59.9121 | -60.2417 | 0.032043 | -0.004578 | 62.8967 | -59.9899 | 63.0066 | -60.0357 | -60.1547 | -60.0357 | -0.077819 | -0.11444 | -0.027466 | 0.073243 | 60.0174 | -0.25635 | 60.0952 | -0.17853 | -0.004577 | -0.10529 | 0.004578 | -0.050354 | -0.050354 | -0.16937 | -0.045777 | -0.1648 | 0.15106 | 123.0377 | -0.045777 | 122.9965 | 122.9507 | 122.8867 | 122.8729 | 122.8821 | -123.0652 | -122.9919 | 122.9599 | 122.9919 | 59.9945 | 59.9808
58.8906 | 123.2483 | -59.9808 | 62.9105 | -0.1062 | 5.7742e-05 | 0.064495 | 0.067232 | -0.0010253 | -0.00077756 | 0.0026553 | -0.030792 | 0.0011664 | 0.065777 | 0.070333 | -0.00057257 | 0.0011792 | -0.0012219 | -0.009155 | 62.8098 | -60.0677 | 63.0661 | -59.8251 | -60.2005 | -0.009155 | -0.004578 | 62.8143 | -59.9945 | 63.0798 | -59.9808 | -60.0861 | -59.967 | -0.086975 | -0.10071 | 0.15564 | 0.15564 | 59.9716 | -0.21973 | 60.0586 | -0.13275 | -0.013733 | -0.09613 | 0.16937 | 0 | 0.013733 | -0.10529 | 0.027466 | -0.091553 | 0.24262 | 123.1338 | 0.013733 | 123.0743 | 122.8775 | 122.8088 | 122.7905 | 122.7951 | -122.9782 | -122.905 | 123.0469 | 123.0606 | 59.9716 | 59.9762
59.8281 | 123.1796 | -59.9899 | 62.9929 | -0.045166 | 0.0017667 | 0.062572 | 0.0636 | -0.0033753 | 7.6842e-05 | -0.00033547 | -0.0002747 | 0.0003118 | 0.066418 | 0.067556 | -0.0024952 | 0.0024608 | -0.0016493 | 0 | 62.8784 | -60.0449 | 63.0157 | -59.8709 | -60.2234 | 0.059509 | 0.013733 | 62.9059 | -59.9945 | 63.002 | -60.0449 | -60.1364 | -60.0632 | -0.054932 | -0.11444 | 0.022888 | 0.11902 | 60.0494 | -0.23346 | 60.1044 | -0.17853 | -0.004578 | -0.086975 | 0.009155 | -0.054932 | -0.073242 | -0.14649 | -0.068664 | -0.14191 | 0.17395 | 123.0606 | -0.050354 | 122.9965 | 122.9233 | 122.9004 | 122.8683 | 122.8958 | -123.0377 | -122.9874 | 123.0057 | 122.9919 | 59.9899 | 60.0037
60.8906 | 123.23 | -59.9716 | 62.9379 | -0.090943 | -0.00015586 | 0.064281 | 0.06595 | 0.00089729 | 0.00029044 | -0.0011899 | 0.036346 | 0.0024482 | 0.064922 | 0.064779 | -0.009331 | 0.00053824 | 0.0021961 | -0.013733 | 62.8418 | -60.0403 | 63.0524 | -59.8343 | -60.1822 | 0.045776 | 0.032043 | 62.8464 | -59.967 | 63.1577 | -60.2463 | -60.0723 | -59.8755 | -0.068664 | -0.09613 | 0.11444 | 0.13733 | 60.0174 | -0.21057 | 60.0861 | -0.14191 | 0.004578 | -0.091552 | 0.21973 | -0.27466 | 0.096131 | -0.10071 | 0.091553 | -0.10529 | 0.20599 | 123.0927 | -0.27924 | 123.1247 | 122.8821 | 122.8134 | 122.8134 | 122.818 | -122.9782 | -122.905 | 123.024 | 123.1293 | 59.9579 | 60.0037
61.8281 | 123.1613 | -59.9762 | 62.9837 | 0.015869 | 0.00048494 | 0.063427 | 0.063386 | -0.0027343 | -0.0020594 | -0.00076267 | -0.015534 | 0.0011664 | 0.065563 | 0.066915 | -0.00099977 | 0.0022472 | -0.0014355 | 0.027466 | 62.8967 | -60.0632 | 63.0478 | -59.8618 | -60.173 | 0.086975 | 0.041199 | 62.8922 | -59.9625 | 63.0066 | -60.022 | -60.141 | -60.0403 | -0.086975 | -0.086975 | 0.064087 | 0.11444 | 60.0632 | -0.19684 | 60.1501 | -0.10986 | 0.013733 | -0.091553 | 0.022888 | -0.045777 | -0.064087 | -0.16479 | -0.07782 | -0.17853 | 0.20142 | 123.111 | -0.05951 | 122.9691 | 122.9599 | 122.8546 | 122.8729 | 122.8683 | -123.0469 | -122.9462 | 123.024 | 122.9828 | 60.0037 | 60.0174
62.8281 | 123.143 | -59.9991 | 62.9791 | -0.045166 | -0.00036966 | 0.062359 | 0.066163 | 0.00089729 | -0.002273 | -0.0011899 | -0.049103 | 0.0024482 | 0.067272 | 0.060293 | -0.0016406 | 0.0024608 | 0.0030505 | 0.004578 | 62.8967 | -60.0632 | 62.9883 | -59.8984 | -60.2417 | 0.032043 | 0.013733 | 62.883 | -59.9808 | 63.0066 | -60.0449 | -60.1547 | -60.0403 | -0.064087 | -0.082397 | 0.009155 | 0.10071 | 60.0311 | -0.24261 | 60.0952 | -0.17853 | 0.01831 | -0.09613 | 0.027466 | -0.045777 | -0.041199 | -0.15564 | -0.059509 | -0.17395 | 0.16479 | 123.0515 | -0.064087 | 122.9874 | 122.9599 | 122.8638 | 122.8958 | 122.8821 | -123.0423 | -122.9599 | 122.9874 | 123.0057 | 60.0037 | 60.0128
63.8906 | 123.23 | -59.9716 | 62.97 | -0.045166 | 0.0011257 | 0.064068 | 0.065309 | 4.2692e-05 | -0.0027002 | 0.0013735 | 0.024139 | 0.0003118 | 0.06599 | 0.05837 | -0.001427 | 0.0024608 | -0.00058107 | -0.018311 | 62.8418 | -60.0677 | 63.0203 | -59.8343 | -60.1959 | 0.013733 | 0.009155 | 62.8372 | -59.9808 | 63.0569 | -59.9854 | -60.0632 | -59.967 | -0.09613 | -0.12817 | 0.050354 | 0.13733 | 59.9854 | -0.2243 | 60.0815 | -0.12817 | -0.009155 | -0.13275 | 0.086975 | -0.013733 | 0.004578 | -0.091552 | 0.013733 | -0.082397 | 0.23346 | 123.0881 | -0.004578 | 123.0377 | 122.9095 | 122.818 | 122.8134 | 122.8088 | -123.0377 | -122.9507 | 122.9919 | 123.0286 | 59.9533 | 59.9808
64.8281 | 123.2666 | -59.9533 | 62.9562 | 0.031128 | 0.00091214 | 0.062359 | 0.064454 | -0.0014527 | 0.00050424 | -0.0011899 | -0.0033265 | 0.0007392 | 0.06599 | 0.06542 | -0.0012134 | 0.00053824 | -0.0014355 | 0.07782 | 62.8647 | -60.0494 | 63.1073 | -59.7519 | -60.1227 | 0.11902 | 0.15106 | 62.8464 | -59.9716 | 63.1027 | -59.9213 | -60.0266 | -59.935 | -0.09613 | -0.091553 | 0.15106 | 0.20142 | 60.0723 | -0.16937 | 60.1685 | -0.073243 | -0.018311 | -0.10986 | 0.14648 | 0.032043 | 0.01831 | -0.073242 | 0.036621 | -0.054931 | 0.29755 | 123.1567 | 0.050354 | 123.0743 | 122.9141 | 122.818 | 122.818 | 122.7997 | -123.0057 | -122.9279 | 123.0606 | 123.056 | 60.0311 | 60.1044
65.8906 | 123.1613 | -59.9854 | 63.0157 | -0.007019 | 0.0032619 | 0.063854 | 0.065523 | 0.0013245 | 0.00093144 | 0.0013735 | -0.015534 | 0.0009528 | 0.067058 | 0.064993 | -0.0022816 | -0.00052976 | 5.9726e-05 | 0.054932 | 62.8784 | -60.0311 | 63.0432 | -59.8389 | -60.1959 | 0.082397 | 0.068665 | 62.8922 | -59.9762 | 63.0203 | -59.9991 | -60.1181 | -60.0174 | -0.045776 | -0.13733 | 0.027466 | 0.14648 | 60.0677 | -0.21057 | 60.1135 | -0.16479 | 0.009156 | -0.1236 | 0.004578 | -0.013732 | -0.032043 | -0.13275 | -0.041199 | -0.14191 | 0.19226 | 123.0743 | -0.022888 | 122.9965 | 122.9095 | 122.8683 | 122.8638 | 122.8775 | -123.0469 | -122.9919 | 123.0286 | 123.0057 | 60.0403 | 60.054
66.8281 | 123.1338 | -60.0082 | 63.0066 | -0.045166 | -0.0012241 | 0.063 | 0.067232 | -0.0014527 | -0.0029138 | 9.193e-05 | -0.012482 | 0.0003118 | 0.069195 | 0.063497 | -0.0027088 | 0.0024608 | 0.0024097 | 0 | 62.8967 | -60.0723 | 62.9929 | -59.8892 | -60.2371 | 0.041199 | 0.15106 | 62.9242 | -59.967 | 62.9837 | -60.0357 | -60.1227 | -60.054 | -0.064087 | -0.10986 | -0.013733 | 0.11902 | 60.0494 | -0.22888 | 60.1135 | -0.16479 | 0.041199 | -0.082398 | -0.022888 | -0.027466 | -0.045776 | -0.11444 | -0.086975 | -0.15564 | 0.18311 | 123.0652 | -0.068665 | 122.9507 | 122.9691 | 122.8912 | 122.905 | 122.9324 | -123.0789 | -122.9736 | 123.0011 | 122.9919 | 60.0082 | 60.1593
67.8906 | 123.2529 | -59.9854 | 62.915 | -0.060425 | 0.0028347 | 0.06599 | 0.066377 | 0.0019653 | 0.0017858 | 0.00051913 | -0.052155 | -0.0009698 | 0.066631 | 0.064352 | -0.0029224 | 0.0020336 | -0.0012219 | -0.059509 | 62.8326 | -60.1044 | 62.9974 | -59.8801 | -60.2554 | -0.059509 | -0.036621 | 62.8052 | -59.9899 | 63.0981 | -59.9991 | -60.1273 | -59.9487 | -0.11902 | -0.082397 | 0.082398 | 0.10529 | 59.9258 | -0.27008 | 60.0449 | -0.15106 | -0.004577 | -0.10986 | 0.18311 | -0.013732 | 0.036622 | -0.14191 | 0.041199 | -0.13733 | 0.2243 | 123.1018 | -0.009155 | 123.0881 | 122.937 | 122.7951 | 122.818 | 122.7905 | -123.0194 | -122.905 | 122.9828 | 123.0835 | 59.9258 | 59.9487
68.8281 | 123.2895 | -59.9487 | 62.9562 | -0.11383 | 0.00091214 | 0.063427 | 0.065095 | -0.0025207 | -0.0020594 | 0.0013735 | -0.033844 | 0.0026618 | 0.065349 | 0.065634 | -0.002068 | 0.0022472 | 0.00070073 | 0.068665 | 62.8555 | -60.0449 | 63.3041 | -59.8709 | -60.4568 | 0.11444 | 0.13275 | 62.851 | -59.9808 | 63.1165 | -59.9167 | -60.0128 | -59.9167 | -0.096131 | -0.10071 | 0.3479 | 0.077819 | 60.0632 | -0.50812 | 60.1593 | -0.41199 | -0.032044 | -0.10529 | 0.16022 | 0.032043 | 0.032043 | -0.064087 | 0.064087 | -0.032043 | 0.17395 | 123.349 | 0.064087 | 123.0972 | 122.9004 | 122.8317 | 122.8043 | 122.7997 | -123.0011 | -122.937 | 123.2529 | 123.0652 | 60.0174 | 60.0815
69.8281 | 123.1476 | -59.9991 | 63.0112 | -0.090943 | -0.0010105 | 0.062786 | 0.066591 | 0.0034607 | 0.001145 | 0.00094633 | -0.0094299 | 0.0018072 | 0.06599 | 0.067556 | -0.002068 | 0.0013928 | -0.0020765 | -0.004578 | 62.8784 | -60.0449 | 63.0295 | -59.6695 | -60.3561 | -0.10071 | -0.032043 | 62.9013 | -60.0174 | 63.0066 | -60.0677 | -60.1456 | -60.022 | -0.045777 | -0.13275 | 0.018311 | 0.32959 | 59.8984 | -0.35706 | 59.9442 | -0.31128 | -0.018311 | -0.10986 | -0.004577 | -0.068665 | -0.022889 | -0.14648 | -0.004578 | -0.12817 | 0.37537 | 123.0743 | -0.050354 | 123.024 | 122.9233 | 122.9187 | 122.8775 | 122.9004 | -123.056 | -123.0286 | 123.0286 | 123.0057 | 59.9945 | 59.967
70.8906 | 123.1247 | -59.9716 | 63.0066 | -0.060425 | 0.00027134 | 0.063641 | 0.065523 | 4.2692e-05 | -0.00056396 | -0.0035397 | -0.015534 | 0.0007392 | 0.066418 | 0.059225 | 0.00028203 | 0.00053824 | -0.00036747 | 0.009155 | 62.9105 | -60.0586 | 62.9883 | -59.8892 | -60.228 | 0.032043 | 0.018311 | 62.9105 | -59.9945 | 63.0112 | -60.0357 | -60.1501 | -60.0494 | -0.086975 | -0.096131 | -0.018311 | 0.082398 | 60.0037 | -0.25635 | 60.0906 | -0.16937 | -0.022888 | -0.096131 | 0.004577 | -0.064087 | -0.077819 | -0.17853 | -0.054931 | -0.15564 | 0.16937 | 123.0469 | -0.041199 | 123.0057 | 122.9691 | 122.905 | 122.8821 | 122.8821 | -123.0652 | -123.0011 | 122.9599 | 122.9828 | 59.9808 | 59.9899
71.8281 | 123.1934 | -59.9716 | 62.9974 | -0.029907 | 0.0015529 | 0.063427 | 0.066377 | 0.0013245 | -0.00099116 | 0.00051913 | -0.058258 | 0.0018072 | 0.065777 | 0.068411 | -0.0018542 | 0.0031018 | -0.0012219 | 0.009155 | 62.883 | -60.0723 | 62.9929 | -59.9121 | -60.2325 | 0.022888 | -0.004578 | 62.9105 | -59.9991 | 63.0203 | -60.0266 | -60.1364 | -60.0082 | -0.10071 | -0.11444 | -0.004578 | 0.05951 | 59.9945 | -0.26093 | 60.0952 | -0.16022 | -0.027465 | -0.086976 | 0.022888 | -0.054931 | -0.036621 | -0.1648 | -0.009156 | -0.13733 | 0.16022 | 123.0652 | -0.027466 | 123.0194 | 122.9553 | 122.9095 | 122.8546 | 122.8821 | -123.0698 | -122.9965 | 122.9645 | 122.9919 | 59.9808 | 59.967
72.8906 | 123.2712 | -59.9762 | 62.9517 | -0.045166 | 0.0032619 | 0.062145 | 0.064668 | -0.00017091 | -0.00077756 | 0.0030825 | 0.027191 | -0.000329 | 0.064709 | 0.065206 | -0.0027088 | 0.0022472 | -0.0016493 | 0.091553 | 62.8693 | -60.0449 | 63.0295 | -59.8526 | -60.2005 | 0.013733 | 0.013733 | 62.8326 | -59.9854 | 63.0844 | -59.967 | -60.0632 | -59.9579 | -0.068665 | -0.082397 | 0.07782 | 0.1236 | 59.9899 | -0.2243 | 60.0586 | -0.15564 | -0.009156 | -0.11902 | 0.13275 | 0.009155 | 0.01831 | -0.086975 | 0.027466 | -0.077819 | 0.19226 | 123.0743 | 0.018311 | 123.0698 | 122.9141 | 122.818 | 122.8455 | 122.8088 | -122.9965 | -122.937 | 123.0057 | 123.0606 | 60.0677 | 59.9899
73.8281 | 123.143 | -59.9899 | 63.0203 | -0.060425 | 0.0026211 | 0.063854 | 0.067018 | -0.0010253 | -0.0035548 | -0.0014035 | -0.039948 | 0.0026618 | 0.066418 | 0.064352 | -0.00099977 | 0.0026746 | 0.00048713 | 0.004578 | 62.9059 | -60.0723 | 62.9745 | -59.9167 | -60.2371 | 0.036621 | 0.018311 | 62.9013 | -60.0037 | 62.9929 | -60.0357 | -60.1547 | -60.0357 | -0.082398 | -0.11444 | -0.045777 | 0.073242 | 60.0265 | -0.24719 | 60.1089 | -0.16479 | -0.013733 | -0.11902 | -0.027466 | -0.045777 | -0.045777 | -0.1648 | -0.032044 | -0.15106 | 0.15564 | 123.0469 | -0.032044 | 122.9965 | 122.9782 | 122.905 | 122.8958 | 122.8912 | -123.0927 | -123.024 | 122.9645 | 122.9828 | 59.9945 | 60.0082
74.8906 | 123.2803 | -59.9258 | 62.9883 | -0.090943 | 0.00027134 | 0.063427 | 0.065309 | 0.00046989 | 0.00093144 | -0.0035397 | 0.024139 | 0.0011664 | 0.065349 | 0.06542 | -0.00099977 | 0.0013928 | 0.00048713 | 0.073242 | 62.8555 | -60.0266 | 63.0981 | -59.7565 | -60.0952 | 0.10986 | 0.15564 | 62.8647 | -59.9396 | 63.1073 | -59.9075 | -60.0082 | -59.9213 | -0.10071 | -0.13275 | 0.10986 | 0.16937 | 60.0357 | -0.16937 | 60.1364 | -0.068665 | -0.013733 | -0.1236 | 0.11902 | 0.01831 | 0.004577 | -0.082398 | 0.01831 | -0.068665 | 0.27008 | 123.1247 | 0.032043 | 123.0469 | 122.8821 | 122.8043 | 122.7814 | 122.7905 | -123.0148 | -122.9279 | 123.024 | 123.0331 | 59.9991 | 60.0815
75.8438 | 123.2071 | -59.9579 | 62.9288 | -0.068054 | 0.0024075 | 0.06535 | 0.063386 | 0.0064515 | -0.00056396 | 9.193e-05 | -0.015534 | 0.0018072 | 0.065563 | 0.06542 | -0.001427 | 0.0028882 | 0.0019823 | -0.045776 | 62.8281 | -60.0449 | 63.0524 | -59.8251 | -60.228 | -0.004578 | -0.009155 | 62.8235 | -59.967 | 63.0432 | -60.0128 | -60.0998 | -59.9762 | -0.086975 | -0.10071 | 0.1236 | 0.13275 | 59.9533 | -0.27008 | 60.0403 | -0.18311 | -0.009155 | -0.10529 | 0.11444 | -0.054931 | -0.01831 | -0.14191 | -0.009155 | -0.13275 | 0.21973 | 123.0972 | -0.045776 | 123.0103 | 122.8729 | 122.7905 | 122.7859 | 122.7814 | -122.9736 | -122.8958 | 123.0103 | 123.0011 | 59.9121 | 59.9487
76.8906 | 123.2803 | -59.9625 | 62.9562 | -0.068054 | 0.0017667 | 0.06535 | 0.065095 | -0.0055115 | -0.0029138 | -0.0014035 | 0.039398 | 0.0007392 | 0.065563 | 0.065847 | -0.0018542 | 0.0016064 | -0.0022901 | -0.018311 | 62.8555 | -60.054 | 63.0569 | -59.8389 | -60.1639 | 0.073242 | 0.073242 | 62.8601 | -59.9716 | 63.089 | -59.9533 | -60.0494 | -59.9258 | -0.091553 | -0.10071 | 0.10071 | 0.1236 | 60.0357 | -0.20142 | 60.1273 | -0.10986 | -0.009156 | -0.096131 | 0.13275 | 0.009155 | 0.036621 | -0.086975 | 0.045777 | -0.077819 | 0.21515 | 123.111 | 0.018311 | 123.0606 | 122.9095 | 122.8317 | 122.818 | 122.8226 | -123.0103 | -122.9279 | 123.0194 | 123.0515 | 59.9442 | 60.0357
77.8281 | 123.143 | -59.9625 | 62.9974 | -0.014649 | 0.00069854 | 0.061291 | 0.066163 | 0.0030335 | -0.0012048 | 0.0015871 | -0.076569 | 0.0020208 | 0.067272 | 0.066702 | -0.0018542 | 0.0024608 | 0.0013415 | -0.004578 | 62.9059 | -60.054 | 62.9745 | -59.9258 | -60.2463 | 0.041199 | -0.004578 | 62.8967 | -59.9945 | 63.002 | -60.0403 | -60.1868 | -60.0357 | -0.091553 | -0.091553 | -0.022889 | 0.036621 | 60.0037 | -0.28381 | 60.0952 | -0.19226 | -0.032044 | -0.10071 | 0.004577 | -0.07782 | -0.073243 | -0.22431 | -0.041199 | -0.19226 | 0.12817 | 123.0286 | -0.045776 | 122.9965 | 122.9599 | 122.8912 | 122.8683 | 122.8592 | -123.0515 | -122.9919 | 122.937 | 122.9645 | 59.9579 | 59.9579
78.8906 | 123.2758 | -59.9533 | 62.9425 | -0.098572 | 0.00091214 | 0.062786 | 0.067232 | 0.0013245 | -0.00077756 | 0.00030553 | 0.027191 | 0.0015936 | 0.068127 | 0.062429 | 0.0011364 | 0.00032464 | -0.00079467 | -0.004578 | 62.8555 | -60.0677 | 63.0066 | -59.6832 | -60.1364 | -0.018311 | -0.009155 | 62.8418 | -59.9945 | 63.0753 | -59.9533 | -60.0586 | -59.967 | -0.11444 | -0.086975 | 0.064087 | 0.27008 | 59.935 | -0.18311 | 60.0494 | -0.068665 | -0.041199 | -0.10071 | 0.13275 | 0 | -0.013733 | -0.10529 | 0.027466 | -0.064087 | 0.38452 | 123.0743 | 0.041199 | 123.0698 | 122.9233 | 122.8363 | 122.8088 | 122.7951 | -123.0103 | -122.937 | 122.9599 | 123.0286 | 59.9487 | 59.9442
79.8281 | 123.1842 | -59.9991 | 63.0066 | -0.045166 | 0.0021939 | 0.064922 | 0.067018 | -0.0018799 | -0.0027002 | 0.0018009 | -0.021637 | 0.0020208 | 0.068981 | 0.063711 | -0.0037768 | 0.0013928 | 0.0011279 | 0.013733 | 62.9013 | -60.0769 | 62.9883 | -59.9258 | -60.2463 | 0.073242 | -0.11444 | 62.9013 | -60.0174 | 62.9929 | -60.0357 | -60.1547 | -60.0266 | -0.07782 | -0.10529 | -0.018311 | 0.073242 | 60.0723 | -0.24719 | 60.1501 | -0.16937 | -0.018311 | -0.10529 | -0.013733 | -0.036622 | -0.027466 | -0.15564 | -0.009155 | -0.13733 | 0.15106 | 123.0652 | -0.018311 | 123.0103 | 122.9782 | 122.9187 | 122.9004 | 122.9004 | -123.0835 | -123.024 | 122.9874 | 122.9919 | 60.0128 | 59.8846
80.8906 | 123.1705 | -59.9899 | 62.9974 | -0.068054 | 0.0019803 | 0.063427 | 0.066163 | 0.0036743 | -0.0018458 | -0.0018307 | -0.018585 | 0.0009528 | 0.067486 | 0.057089 | -0.00099977 | 0.00182 | 0.0019823 | 0.050354 | 62.8784 | -60.0357 | 63.0386 | -59.8434 | -60.1868 | 0.059509 | 0.041199 | 62.8922 | -59.9808 | 62.9837 | -60.0403 | -60.1501 | -60.0357 | -0.045777 | -0.11902 | 0.041198 | 0.14648 | 60.0494 | -0.19684 | 60.0952 | -0.15106 | 0.009155 | -0.10529 | -0.013733 | -0.050354 | -0.045777 | -0.16022 | -0.054932 | -0.16937 | 0.19226 | 123.0743 | -0.059509 | 122.9645 | 122.9141 | 122.8729 | 122.8683 | 122.8821 | -123.0331 | -122.9782 | 123.0286 | 122.9736 | 60.0403 | 60.0311
81.8281 | 123.1705 | -59.9945 | 62.97 | -0.068054 | 5.7742e-05 | 0.064922 | 0.065095 | 0.0023925 | -0.00056396 | 0.0013735 | -0.073517 | 0.0011664 | 0.067699 | 0.069479 | -0.0024952 | 0.00182 | -0.0042127 | 0.032043 | 62.8555 | -60.0861 | 63.0341 | -59.8572 | -60.2097 | 0.027466 | 0.041199 | 62.8601 | -59.9854 | 63.0569 | -60.0174 | -60.1318 | -60.0082 | -0.091553 | -0.11444 | 0.064087 | 0.13733 | 60.022 | -0.21515 | 60.1135 | -0.1236 | 0.009155 | -0.10986 | 0.086975 | -0.022888 | -0.013733 | -0.13733 | -0.022888 | -0.14648 | 0.22888 | 123.1201 | -0.032043 | 123.0423 | 122.9416 | 122.8455 | 122.85 | 122.8546 | -123.056 | -122.9553 | 123.0286 | 123.0515 | 60.0266 | 60.0357
82.8906 | 123.2529 | -59.9579 | 62.915 | -0.098572 | 0.0026211 | 0.063 | 0.064241 | -0.0020935 | 0.00050424 | -0.0016171 | 0.0058289 | 0.0024482 | 0.066204 | 0.064565 | -0.00099977 | 0.0043836 | -0.0010083 | -0.041199 | 62.8281 | -60.0723 | 63.0249 | -59.848 | -60.228 | -0.027466 | -0.036621 | 62.8281 | -60.0082 | 63.0386 | -60.022 | -60.1044 | -59.9899 | -0.11444 | -0.086975 | 0.10986 | 0.10986 | 59.9304 | -0.27008 | 60.0449 | -0.15564 | -0.050354 | -0.086975 | 0.1236 | -0.064087 | -0.032043 | -0.14648 | 0.018311 | -0.09613 | 0.22431 | 123.0972 | -0.013733 | 123.0469 | 122.9004 | 122.8363 | 122.7859 | 122.7859 | -122.9874 | -122.9233 | 122.9828 | 122.9965 | 59.9167 | 59.9213
83.8281 | 123.1567 | -59.9808 | 63.0112 | -0.007019 | 0.00091214 | 0.063213 | 0.067232 | -0.0023071 | -0.0014184 | -0.0024717 | -0.0094299 | 0.0028754 | 0.066631 | 0.05837 | -0.00099977 | 0.0020336 | 0.00027333 | -0.004578 | 62.9013 | -60.0769 | 62.97 | -59.8801 | -60.2325 | 0.027466 | 0.004578 | 62.9013 | -59.9808 | 62.9974 | -60.0403 | -60.1593 | -60.0357 | -0.09613 | -0.10986 | -0.041198 | 0.10071 | 60.0082 | -0.25177 | 60.1044 | -0.15564 | 0 | -0.10986 | -0.013732 | -0.059509 | -0.054932 | -0.17853 | -0.054932 | -0.17853 | 0.19684 | 123.0469 | -0.059509 | 122.9782 | 122.9782 | 122.8821 | 122.8821 | 122.8821 | -123.0881 | -122.9919 | 122.9507 | 122.9782 | 59.9762 | 59.9854
84.8906 | 123.3215 | -59.9716 | 62.9745 | -0.15198 | -0.00015586 | 0.061504 | 0.064668 | -0.00017091 | 0.0024268 | -0.0018307 | 0.039398 | 0.0005256 | 0.064922 | 0.066274 | -0.0016406 | 0.0022472 | -0.0018629 | -0.022888 | 62.8647 | -60.0494 | 63.0066 | -59.8572 | -60.2142 | 0.013733 | -0.009155 | 62.851 | -60.0037 | 63.0615 | -59.9808 | -60.0769 | -59.8801 | -0.077819 | -0.10986 | 0.032044 | 0.11444 | 59.9854 | -0.24261 | 60.0632 | -0.16479 | -0.032043 | -0.1236 | 0.086975 | -0.009155 | 0.091553 | -0.10529 | 0.1236 | -0.073242 | 0.19226 | 123.056 | 0.022888 | 123.0652 | 122.9141 | 122.8546 | 122.8363 | 122.8226 | -123.024 | -122.9782 | 122.9782 | 123.0331 | 59.9487 | 59.9625
85.8281 | 123.2117 | -59.9579 | 62.9654 | -0.090943 | 0.00069854 | 0.06535 | 0.065095 | 0.0013245 | -0.0012048 | 0.0024417 | -0.0063781 | -0.0009698 | 0.066204 | 0.062002 | 0.00028203 | 0.0026746 | -0.00036747 | -0.036621 | 62.851 | -60.0586 | 62.9929 | -59.8663 | -60.2234 | -0.013733 | -0.036621 | 62.8555 | -59.9899 | 63.0386 | -60.0174 | -60.1181 | -59.9808 | -0.10071 | -0.11444 | 0.027466 | 0.091553 | 59.9442 | -0.2655 | 60.0449 | -0.16479 | -0.032043 | -0.10986 | 0.073242 | -0.059509 | -0.022888 | -0.16022 | 0.009155 | -0.12817 | 0.19226 | 123.0515 | -0.027466 | 123.0286 | 122.9095 | 122.8455 | 122.8088 | 122.8134 | -123.024 | -122.9553 | 122.9507 | 122.9965 | 59.9213 | 59.9213
86.8906 | 123.1201 | -60.022 | 62.9562 | -0.052796 | 0.0030483 | 0.06599 | 0.066377 | 0.0036743 | -0.0024866 | 9.193e-05 | -0.085724 | 0.0020208 | 0.065349 | 0.064565 | -0.0022816 | 0.003529 | 0.0019823 | -0.064087 | 62.8555 | -60.1044 | 62.9242 | -59.9762 | -60.3378 | -0.09613 | -0.15106 | 62.8693 | -60.0357 | 62.9562 | -60.1501 | -60.26 | -60.0952 | -0.082397 | -0.10071 | -0.032044 | 0.045777 | 59.9258 | -0.31586 | 60.0082 | -0.23346 | -0.013733 | -0.086975 | 0 | -0.12817 | -0.073242 | -0.23804 | -0.059509 | -0.2243 | 0.12817 | 123.0286 | -0.11444 | 122.9919 | 122.9599 | 122.905 | 122.8775 | 122.8912 | -123.0606 | -122.9919 | 122.9462 | 122.9782 | 59.9579 | 59.8709
87.8281 | 123.2071 | -59.9899 | 63.002 | -0.007019 | 5.7742e-05 | 0.06599 | 0.063814 | -0.00081171 | 0.0013586 | 0.00051913 | 0.024139 | 0.00138 | 0.064709 | 0.060079 | -0.0039906 | 0.0013928 | -0.00036747 | 0.004578 | 62.8464 | -60.0449 | 63.0707 | -59.8206 | -60.1501 | 0.091553 | 0.086975 | 62.8784 | -59.9854 | 63.0569 | -59.9716 | -60.0861 | -59.9945 | -0.054932 | -0.15564 | 0.068665 | 0.16937 | 60.0815 | -0.16022 | 60.1364 | -0.10529 | 0.004577 | -0.1236 | 0.054932 | 0.01831 | -0.004578 | -0.096131 | -0.009155 | -0.10071 | 0.2243 | 123.1155 | 0.013733 | 123.0423 | 122.8912 | 122.8638 | 122.8363 | 122.8683 | -123.0469 | -122.9874 | 123.0606 | 123.0469 | 59.9945 | 60.0769
88.8906 | 123.2346 | -59.9899 | 62.9105 | -0.098572 | 0.0036893 | 0.063854 | 0.064454 | 4.2692e-05 | -0.00099116 | -0.0022581 | -0.015534 | -0.0009698 | 0.065349 | 0.06542 | -0.0029224 | 0.0020336 | -0.00079467 | -0.022888 | 62.8281 | -60.0586 | 63.0615 | -59.9442 | -60.3241 | 0.068665 | 0.036621 | 62.8143 | -59.967 | 63.0661 | -59.9899 | -60.0952 | -59.9762 | -0.068665 | -0.082397 | 0.15106 | 0.045776 | 60.0586 | -0.33417 | 60.1273 | -0.2655 | 0.022888 | -0.09613 | 0.15564 | 0 | 0.013733 | -0.10529 | -0.009155 | -0.12817 | 0.11444 | 123.1201 | -0.022888 | 123.0331 | 122.8867 | 122.7814 | 122.818 | 122.8043 | -122.9691 | -122.8775 | 123.0515 | 123.056 | 59.967 | 60.0265
89.8281 | 123.2437 | -59.9487 | 62.9517 | -0.068054 | -0.0012241 | 0.064922 | 0.064241 | 0.00068369 | -0.002273 | 0.00051913 | 0.0088807 | -0.0005426 | 0.065136 | 0.065206 | -0.0029224 | 0.0020336 | -0.00036747 | 0.050354 | 62.8464 | -60.0403 | 63.089 | -59.7656 | -60.1318 | 0.13275 | 0.036621 | 62.8601 | -59.9304 | 63.1027 | -59.9854 | -59.9716 | -59.9258 | -0.091553 | -0.10528 | 0.13733 | 0.1831 | 60.0815 | -0.18311 | 60.173 | -0.091553 | 0.01831 | -0.091553 | 0.15106 | -0.036622 | 0.022888 | -0.022889 | 0.004578 | -0.041199 | 0.27466 | 123.1293 | -0.054932 | 123.0331 | 122.8867 | 122.7905 | 122.7951 | 122.8088 | -122.9919 | -122.8821 | 123.0377 | 123.0515 | 59.9991 | 59.9854
90.8906 | 123.2758 | -59.967 | 62.9196 | -0.11383 | 0.0013393 | 0.063854 | 0.067445 | 0.0017517 | 0.0015722 | -0.00012167 | -0.076569 | 0.0007392 | 0.065777 | 0.05837 | -0.0024952 | 0.003529 | -0.0037855 | -0.068665 | 62.8235 | -60.0906 | 63.0112 | -59.8663 | -60.2463 | -0.045776 | -0.054932 | 62.8464 | -60.0174 | 63.0844 | -60.0037 | -60.0998 | -59.9533 | -0.1236 | -0.096131 | 0.091552 | 0.10071 | 59.9213 | -0.27924 | 60.0449 | -0.15564 | -0.050354 | -0.073242 | 0.16479 | -0.036621 | 0.013733 | -0.13275 | 0.064087 | -0.082397 | 0.2243 | 123.1018 | 0.013733 | 123.1018 | 122.9141 | 122.8638 | 122.7905 | 122.8134 | -123.0103 | -122.937 | 122.9782 | 123.0515 | 59.8984 | 59.9121
91.8281 | 123.1567 | -59.9945 | 62.9837 | 0.00061049 | 0.0017667 | 0.063427 | 0.064454 | 0.0023925 | -0.002273 | 0.00051913 | -0.030792 | -0.000329 | 0.065349 | 0.062002 | -0.0012134 | 0.0031018 | 0.0028369 | 0.050354 | 62.8784 | -60.0494 | 63.0112 | -59.8572 | -60.2234 | 0.064087 | 0.013733 | 62.8876 | -59.9854 | 63.0249 | -60.0403 | -60.141 | -60.0266 | -0.054931 | -0.10529 | 0.027465 | 0.13733 | 60.0586 | -0.22888 | 60.1135 | -0.17395 | 0.009155 | -0.096131 | 0.041198 | -0.045776 | -0.032043 | -0.14648 | -0.041198 | -0.15564 | 0.19226 | 123.0606 | -0.054931 | 123.0103 | 122.9279 | 122.8729 | 122.8729 | 122.8821 | -123.0331 | -122.9691 | 123.0057 | 123.0194 | 60.0449 | 60.0082
92.8906 | 123.2437 | -59.967 | 62.9105 | -0.075684 | -0.00015586 | 0.06599 | 0.063814 | 0.0038879 | -0.0027002 | -0.0014035 | -0.030792 | 0.0020208 | 0.065777 | 0.064779 | -0.0033496 | 0.0031018 | 0.00091433 | -0.013733 | 62.8143 | -60.0632 | 63.0386 | -59.8068 | -60.2005 | -0.004578 | 0.018311 | 62.8052 | -60.022 | 63.0798 | -59.9075 | -60.0952 | -59.9945 | -0.09613 | -0.09613 | 0.12817 | 0.16022 | 59.9625 | -0.23346 | 60.0586 | -0.13733 | -0.054932 | -0.10528 | 0.16937 | 0.059509 | -0.027466 | -0.12817 | 0.027466 | -0.073242 | 0.25635 | 123.1018 | 0.11444 | 123.1018 | 122.8775 | 122.8271 | 122.7814 | 122.7722 | -122.9736 | -122.9324 | 123.0057 | 123.0469 | 59.9533 | 59.9854
93.8281 | 123.2712 | -59.9442 | 62.9471 | -0.060425 | -0.00058326 | 0.063854 | 0.066163 | -0.00059811 | -0.00099116 | -0.0031125 | 0.0058289 | -0.000329 | 0.064709 | 0.064993 | -0.00014517 | 0.003529 | -0.0054945 | 0.036621 | 62.8647 | -60.0357 | 63.1073 | -59.7519 | -60.1135 | 0.11444 | 0.14191 | 62.851 | -59.9625 | 63.1485 | -59.697 | -60.2325 | -60.1273 | -0.091553 | -0.082398 | 0.16022 | 0.19226 | 60.0586 | -0.16937 | 60.1501 | -0.077819 | -0.01831 | -0.096131 | 0.20142 | 0.24719 | -0.1831 | -0.28839 | -0.16479 | -0.27008 | 0.28381 | 123.143 | 0.2655 | 123.111 | 122.9004 | 122.8134 | 122.8088 | 122.7951 | -122.9828 | -122.9095 | 123.0515 | 123.0927 | 59.9808 | 60.0861
94.8906 | 123.2117 | -59.9808 | 62.9379 | -0.052796 | 0.0019803 | 0.064495 | 0.063386 | -0.00017091 | -0.00035036 | 0.00094633 | -0.0002747 | 0.0005256 | 0.065136 | 0.057516 | -0.0027088 | 0.00053824 | 0.00027333 | -0.050354 | 62.8372 | -60.0632 | 63.0203 | -59.8572 | -60.2234 | -0.018311 | -0.036621 | 62.8281 | -59.9945 | 63.0569 | -60.0128 | -60.1181 | -60.0037 | -0.082397 | -0.10071 | 0.082398 | 0.1236 | 59.9625 | -0.24262 | 60.0449 | -0.16022 | -0.013733 | -0.10986 | 0.11902 | -0.032043 | -0.022888 | -0.13733 | -0.009155 | -0.1236 | 0.20599 | 123.0835 | -0.01831 | 123.0515 | 122.9004 | 122.8226 | 122.818 | 122.8088 | -123.0011 | -122.9324 | 123.0011 | 123.0377 | 59.9304 | 59.9442
95.8281 | 123.2712 | -59.935 | 62.9654 | -0.083313 | 0.00091214 | 0.063854 | 0.064668 | -0.0042297 | -0.00056396 | 0.0011599 | 0.014984 | 0.0009528 | 0.066418 | 0.067129 | -0.0027088 | 0.0020336 | -0.00079467 | 0.050354 | 62.8876 | -60.0174 | 63.0936 | -59.729 | -60.1227 | 0.12817 | 0.16022 | 62.8464 | -59.9533 | 63.121 | -59.935 | -59.9991 | -59.9258 | -0.082397 | -0.07782 | 0.12817 | 0.20599 | 60.0632 | -0.18768 | 60.1456 | -0.10529 | -0.01831 | -0.11902 | 0.15564 | 0 | 0.009156 | -0.064086 | 0.027466 | -0.045776 | 0.28839 | 123.111 | 0.01831 | 123.0743 | 122.905 | 122.7997 | 122.8226 | 122.7814 | -122.9828 | -122.9187 | 123.0286 | 123.056 | 59.9854 | 60.0952
96.8906 | 123.1979 | -59.9808 | 62.9379 | -0.1062 | 0.0013393 | 0.064495 | 0.065523 | -0.0020935 | -0.00013676 | -0.00097627 | -0.033844 | 0.0022346 | 0.065563 | 0.064352 | -0.0033496 | 0.0020336 | -0.0018629 | -0.045776 | 62.851 | -60.0677 | 63.0066 | -59.8755 | -60.2325 | -0.013733 | -0.041199 | 62.8326 | -59.9945 | 63.0386 | -60.0128 | -60.1135 | -59.9854 | -0.086975 | -0.086975 | 0.068665 | 0.10529 | 59.967 | -0.25177 | 60.054 | -0.16479 | -0.013733 | -0.10529 | 0.10071 | -0.032043 | -0.004578 | -0.13275 | 0.009155 | -0.11902 | 0.19226 | 123.0743 | -0.01831 | 123.0331 | 122.9187 | 122.8271 | 122.8317 | 122.8134 | -123.0057 | -122.9324 | 122.9874 | 123.0194 | 59.935 | 59.9396
97.8281 | 123.3719 | -59.9121 | 63.0066 | -0.075684 | 0.0019803 | 0.064068 | 0.066163 | 0.00025629 | 0.0026404 | -0.0016171 | -0.0002747 | 0.0011664 | 0.063854 | 0.058798 | -0.0044178 | 0.00011104 | -0.00036747 | 0.086975 | 62.8738 | -60.0403 | 63.1027 | -59.7656 | -60.1273 | 0.11444 | 0.16022 | 62.8418 | -59.967 | 63.1073 | -59.903 | -60.0037 | -60.0815 | -0.12817 | -0.13275 | 0.09613 | 0.14648 | 60.0266 | -0.21515 | 60.1547 | -0.086975 | -0.054932 | -0.16479 | 0.10071 | 0.009155 | -0.16937 | -0.091553 | -0.11444 | -0.036621 | 0.27466 | 123.143 | 0.064087 | 123.0743 | 122.9141 | 122.8088 | 122.7859 | 122.7539 | -123.0469 | -122.9736 | 123.0148 | 123.0194 | 59.9991 | 60.0723
98.8281 | 123.2162 | -59.9533 | 62.9471 | -0.090943 | 0.00091214 | 0.06535 | 0.066163 | -0.00017091 | -0.0014184 | -0.00097627 | -0.0063781 | 0.0009528 | 0.063854 | 0.059011 | -0.0022816 | 0.0028882 | -0.0025037 | -0.022888 | 62.8464 | -60.054 | 63.1119 | -59.8206 | -60.2692 | 0.018311 | -0.018311 | 62.8418 | -59.9854 | 63.0478 | -59.9945 | -60.0906 | -59.9716 | -0.10071 | -0.10071 | 0.16479 | 0.13275 | 59.9716 | -0.31586 | 60.0723 | -0.21515 | -0.032044 | -0.10529 | 0.10071 | -0.041199 | -0.018311 | -0.13733 | 0.013733 | -0.10529 | 0.23346 | 123.1659 | -0.009155 | 123.0331 | 122.9004 | 122.8271 | 122.7997 | 122.7951 | -123.0011 | -122.9324 | 123.0652 | 123.0011 | 59.9304 | 59.935
99.8906 | 123.2666 | -59.967 | 62.9288 | -0.13672 | 0.0017667 | 0.064068 | 0.064882 | 0.0030335 | 0.00093144 | -0.0026853 | -0.073517 | 0.0005256 | 0.06599 | 0.063284 | -0.0029224 | 0.00182 | 0.0011279 | 0.004578 | 62.8143 | -60.054 | 63.0569 | -59.8206 | -60.1776 | -0.17395 | 0.11902 | 62.851 | -59.9991 | 63.1073 | -59.9899 | -60.0677 | -59.935 | -0.086975 | -0.11444 | 0.12817 | 0.14648 | 59.7931 | -0.21057 | 59.8801 | -0.1236 | -0.032043 | -0.07782 | 0.17853 | -0.022888 | 0.032043 | -0.10071 | 0.064086 | -0.068665 | 0.23346 | 123.111 | 0.009155 | 123.1064 | 122.8683 | 122.85 | 122.7814 | 122.818 | -122.9828 | -122.9279 | 123.024 | 123.0743 | 59.9716 | 60.0861
100.8281 | 123.2162 | -59.9625 | 62.9013 | -0.090943 | 5.7742e-05 | 0.062145 | 0.064454 | -0.0010253 | 0.00029044 | 0.0039371 | -0.015534 | -0.000329 | 0.065136 | 0.065847 | -0.0029224 | 0.0037426 | 0.0019823 | -0.059509 | 62.8372 | -60.054 | 63.0066 | -59.8663 | -60.228 | -0.009155 | -0.032043 | 62.8464 | -59.9808 | 63.1302 | -59.9579 | -60.1639 | -59.967 | -0.091553 | -0.064087 | 0.10529 | 0.09613 | 59.9533 | -0.2655 | 60.0449 | -0.17395 | -0.018311 | -0.054931 | 0.22888 | 0.004577 | -0.004578 | -0.20142 | 0.013733 | -0.18311 | 0.18768 | 123.0606 | 0.022888 | 123.111 | 122.8912 | 122.8271 | 122.7997 | 122.8088 | -122.9553 | -122.8821 | 122.9691 | 123.0927 | 59.903 | 59.9304
101.8906 | 123.2574 | -59.9762 | 62.8922 | -0.083313 | 0.00091214 | 0.062572 | 0.063173 | 0.00046989 | -0.0014184 | -0.0028989 | -0.052155 | -0.000329 | 0.063854 | 0.06542 | -0.003136 | 0.0031018 | -0.0046399 | -0.027466 | 62.8235 | -60.0403 | 63.0569 | -59.8022 | -60.2142 | -0.009155 | 0.004578 | 62.8372 | -59.9762 | 63.0844 | -59.9716 | -60.0632 | -59.9533 | -0.064087 | -0.068665 | 0.1648 | 0.17395 | 59.967 | -0.23804 | 60.0311 | -0.17395 | 0 | -0.054932 | 0.19226 | 0.004577 | 0.022888 | -0.086975 | 0.022888 | -0.086975 | 0.23804 | 123.0972 | 0.004577 | 123.0606 | 122.8638 | 122.8134 | 122.7997 | 122.8134 | -122.9324 | -122.8683 | 123.0331 | 123.0606 | 59.9487 | 59.9808
102.8281 | 123.2071 | -59.9945 | 62.9333 | -0.1062 | 5.7742e-05 | 0.062786 | 0.06595 | 0.0013245 | -0.0027002 | -0.00076267 | -0.018585 | -0.0005426 | 0.065563 | 0.062643 | -0.0029224 | 0.0022472 | 0.0028369 | -0.036621 | 62.8418 | -60.0769 | 63.002 | -59.8572 | -60.228 | -0.027466 | -0.032043 | 62.8326 | -59.9899 | 63.0524 | -60.0082 | -60.1181 | -59.9899 | -0.082397 | -0.091553 | 0.068664 | 0.13733 | 59.967 | -0.23346 | 60.0494 | -0.15106 | 0.004578 | -0.10071 | 0.11902 | -0.013733 | 0.004578 | -0.1236 | 0 | -0.12817 | 0.21973 | 123.0789 | -0.018311 | 123.0423 | 122.9187 | 122.8226 | 122.8363 | 122.8271 | -123.0103 | -122.9233 | 122.9965 | 123.0469 | 59.9579 | 59.9625
103.8906 | 123.2254 | -59.9854 | 62.9379 | -0.12146 | 0.0019803 | 0.064281 | 0.065095 | 0.0049561 | -0.00077756 | -0.0018307 | -0.046051 | 0.0005256 | 0.06364 | 0.069052 | -0.002068 | 0.0048108 | 0.00091433 | -0.032043 | 62.8143 | -60.0677 | 63.0295 | -59.816 | -60.2097 | -0.013733 | -0.004578 | 62.8372 | -59.9854 | 63.0524 | -60.0266 | -60.0952 | -59.9808 | -0.082397 | -0.1236 | 0.091553 | 0.16937 | 59.9716 | -0.2243 | 60.054 | -0.14191 | 0 | -0.10071 | 0.11444 | -0.041198 | 0.004578 | -0.10986 | 0.004578 | -0.10986 | 0.25177 | 123.0972 | -0.041198 | 123.0377 | 122.8821 | 122.8226 | 122.7997 | 122.8226 | -123.0057 | -122.9233 | 123.0148 | 123.0377 | 59.9533 | 59.9808
104.8281 | 123.1888 | -59.9991 | 62.9608 | -0.1062 | 0.0011257 | 0.063427 | 0.064668 | -0.0027343 | -0.002273 | -0.0016171 | -0.015534 | 0.00138 | 0.062786 | 0.067983 | -0.00078617 | 0.003529 | -0.0012219 | -0.041199 | 62.8647 | -60.0632 | 63.0112 | -59.8755 | -60.2051 | 0.15106 | -0.004578 | 62.8464 | -59.9854 | 63.0249 | -60.0037 | -60.1089 | -59.9945 | -0.064087 | -0.09613 | 0.050354 | 0.1236 | 60.1501 | -0.20599 | 60.2142 | -0.14191 | 0.013732 | -0.11444 | 0.064087 | -0.004578 | 0.004577 | -0.10986 | -0.009155 | -0.1236 | 0.18768 | 123.0743 | -0.01831 | 123.0103 | 122.9279 | 122.8317 | 122.8638 | 122.8455 | -123.024 | -122.9462 | 123.0103 | 123.024 | 59.9579 | 59.9945
105.8906 | 123.1705 | -59.9854 | 62.9654 | -0.075684 | 0.00091214 | 0.062572 | 0.067872 | 0.0032471 | 7.6842e-05 | 0.0013735 | -0.10403 | 0.0011664 | 0.066631 | 0.067129 | -0.0027088 | 0.0045972 | -0.0012219 | 0.045776 | 62.8876 | -60.0815 | 63.0249 | -59.8572 | -60.2097 | -0.004578 | 0 | 62.8738 | -59.9899 | 63.0478 | -60.0311 | -60.1685 | -60.0174 | -0.09613 | -0.07782 | 0.059509 | 0.12817 | 59.9808 | -0.2243 | 60.0769 | -0.12817 | -0.004577 | -0.091553 | 0.082398 | -0.045776 | -0.032043 | -0.1831 | -0.027466 | -0.17853 | 0.2243 | 123.1064 | -0.041199 | 123.0377 | 122.9691 | 122.8638 | 122.8729 | 122.8592 | -123.0469 | -122.9553 | 123.0103 | 123.0331 | 60.0311 | 59.9854
106.8281 | 123.2208 | -59.9899 | 62.9471 | -0.13672 | 0.00027134 | 0.065136 | 0.0636 | -0.0014527 | 7.6842e-05 | -0.00054907 | 0.0027771 | 0.0024482 | 0.063854 | 0.06072 | -0.0033496 | 0.0020336 | -0.0016493 | -0.050354 | 62.8372 | -60.0723 | 63.0066 | -59.8572 | -60.2051 | -0.013733 | -0.041199 | 62.8326 | -60.0037 | 63.0432 | -59.8343 | -60.1273 | -60.0815 | -0.082398 | -0.10986 | 0.059509 | 0.13275 | 59.9762 | -0.21515 | 60.0586 | -0.13275 | -0.013733 | -0.11444 | 0.09613 | 0.15564 | -0.091553 | -0.13733 | -0.07782 | -0.1236 | 0.21515 | 123.0789 | 0.16937 | 123.0469 | 122.9095 | 122.8363 | 122.8271 | 122.8226 | -123.0194 | -122.9507 | 122.9965 | 123.0331 | 59.9396 | 59.9487
107.8906 | 123.3353 | -59.9945 | 62.9288 | -0.098572 | 0.0026211 | 0.063 | 0.066804 | 0.0036743 | -0.0029138 | 0.0015871 | -0.073517 | -0.000329 | 0.063854 | 0.066488 | -0.003136 | 0.0024608 | -0.00079467 | -0.022888 | 62.8006 | -60.0723 | 63.0432 | -59.8389 | -60.1959 | -0.027466 | -0.022888 | 62.8189 | -59.9991 | 63.0753 | -60.0403 | -60.3836 | -59.9716 | -0.07782 | -0.12817 | 0.11444 | 0.15564 | 59.967 | -0.20142 | 60.0449 | -0.1236 | -0.004577 | -0.10986 | 0.14648 | -0.045776 | 0.022888 | -0.3891 | 0.027465 | -0.38452 | 0.23346 | 123.1155 | -0.041199 | 123.0743 | 122.8729 | 122.818 | 122.7951 | 122.8134 | -123.0011 | -122.9279 | 123.0377 | 123.0698 | 59.9716 | 59.9716
108.8281 | 123.2895 | -59.9487 | 62.9196 | -0.060425 | -0.00079686 | 0.063854 | 0.063386 | -0.0012391 | 0.00029044 | 0.00030553 | -0.0033265 | 0.0007392 | 0.06599 | 0.061361 | -0.0016406 | 0.0024608 | -0.0014355 | 0.013733 | 62.8647 | -60.054 | 63.0524 | -59.8068 | -60.1639 | 0.050354 | 0.050354 | 62.8326 | -59.9808 | 63.0936 | -59.9442 | -60.0357 | -59.9442 | -0.10529 | -0.054932 | 0.13275 | 0.14191 | 59.9991 | -0.21515 | 60.1044 | -0.10986 | -0.032044 | -0.086975 | 0.17395 | 0.004577 | 0.004577 | -0.086976 | 0.036621 | -0.054932 | 0.24719 | 123.1064 | 0.036621 | 123.0743 | 122.9187 | 122.8134 | 122.8134 | 122.7814 | -122.9736 | -122.9004 | 123.0011 | 123.0423 | 59.9625 | 59.9991
109.8906 | 123.262 | -59.9854 | 62.9242 | -0.12146 | 0.00027134 | 0.067059 | 0.066377 | 0.0021789 | -0.0012048 | -0.00033547 | -0.067413 | 0.0015936 | 0.063427 | 0.063711 | -0.0035632 | 0.0026746 | -0.0016493 | -0.15106 | 62.7823 | -60.0998 | 63.0844 | -59.8251 | -60.2051 | 0.009155 | 0.018311 | 62.8098 | -59.9808 | 63.0936 | -59.9716 | -60.0723 | -59.9533 | -0.11444 | -0.14191 | 0.16022 | 0.16022 | 59.9945 | -0.21973 | 60.1089 | -0.10529 | 0.004578 | -0.11444 | 0.16937 | 0.013733 | 0.032044 | -0.086975 | 0.027466 | -0.091553 | 0.27466 | 123.1842 | 0.009155 | 123.0743 | 122.8821 | 122.7905 | 122.7676 | 122.7951 | -123.024 | -122.905 | 123.0698 | 123.0789 | 59.8343 | 60.0037
110.8281 | 123.2071 | -59.9854 | 62.9288 | -0.090943 | 0.0013393 | 0.062145 | 0.06595 | 0.00046989 | -0.0031274 | 0.0028689 | -0.018585 | 0.0003118 | 0.067272 | 0.053671 | -0.0035632 | 0.0026746 | -0.0014355 | -0.041199 | 62.8555 | -60.0449 | 63.1577 | -59.7977 | -60.3516 | 0.004578 | -0.041199 | 62.8189 | -59.9991 | 63.0432 | -59.9991 | -60.1135 | -59.9716 | -0.059509 | -0.073242 | 0.22888 | 0.18768 | 59.9899 | -0.36621 | 60.0494 | -0.3067 | -0.013732 | -0.10986 | 0.11444 | -0.013732 | 0.013733 | -0.12817 | 0.027465 | -0.11444 | 0.24719 | 123.2025 | 0 | 123.0423 | 122.9004 | 122.818 | 122.8409 | 122.8043 | -122.9736 | -122.9279 | 123.143 | 123.0286 | 59.9442 | 59.9442
111.8906 | 123.2666 | -59.9762 | 62.9288 | -0.029907 | 0.0026211 | 0.062572 | 0.065523 | 0.00025629 | -0.00077756 | -0.00033547 | -0.067413 | 0.0018072 | 0.066845 | 0.063925 | -0.0016406 | 0.0031018 | 5.9726e-05 | -0.073242 | 62.8418 | -60.0998 | 62.9974 | -59.8709 | -60.2371 | -0.054932 | -0.050354 | 62.8052 | -59.9991 | 63.0753 | -59.9899 | -60.1044 | -59.9533 | -0.1236 | -0.086975 | 0.068665 | 0.10529 | 59.9213 | -0.26093 | 60.0449 | -0.13733 | -0.022888 | -0.1236 | 0.14648 | -0.013733 | 0.022888 | -0.12817 | 0.045776 | -0.10529 | 0.22888 | 123.0972 | 0.009155 | 123.0743 | 122.9416 | 122.8043 | 122.818 | 122.7814 | -123.0286 | -122.9279 | 122.9736 | 123.0515 | 59.903 | 59.9258
112.8281 | 123.2437 | -59.9945 | 62.9333 | -0.083313 | 0.00027134 | 0.061077 | 0.064882 | 0.00025629 | -0.0020594 | -0.0014035 | -0.0094299 | -0.0016108 | 0.065777 | 0.062216 | -0.0027088 | 0.003529 | -0.0029309 | -0.059509 | 62.8189 | -60.0494 | 62.9929 | -59.8663 | -60.2234 | -0.018311 | -0.004578 | 62.8693 | -59.967 | 63.0478 | -60.022 | -60.0906 | -59.9899 | -0.054931 | -0.11444 | 0.059509 | 0.12817 | 59.9762 | -0.22888 | 60.0311 | -0.17395 | 0.027466 | -0.064087 | 0.11444 | -0.027466 | 0.004578 | -0.09613 | -0.022888 | -0.1236 | 0.18311 | 123.0423 | -0.054932 | 123.0148 | 122.8683 | 122.8363 | 122.8134 | 122.8638 | -122.9828 | -122.9004 | 122.9874 | 123.0423 | 59.935 | 59.9899
113.8906 | 123.2437 | -59.9442 | 62.8967 | -0.083313 | 0.0017667 | 0.062786 | 0.066804 | 0.0041015 | 0.00029044 | -0.0018307 | -0.076569 | 0.0024482 | 0.065563 | 0.059866 | -0.0027088 | 0.0024608 | -0.0027173 | -0.07782 | 62.8281 | -60.0998 | 62.9837 | -59.8984 | -60.2509 | -0.068665 | -0.07782 | 62.8372 | -60.0128 | 63.0707 | -60.0311 | -60.1135 | -59.9533 | -0.15564 | -0.068665 | 0.086975 | 0.045777 | 59.8755 | -0.3067 | 60.0311 | -0.15106 | -0.068664 | -0.05951 | 0.17395 | -0.086975 | -0.009155 | -0.16937 | 0.059509 | -0.10071 | 0.20142 | 123.0835 | -0.018311 | 123.0835 | 122.9279 | 122.85 | 122.7722 | 122.7814 | -122.9965 | -122.9095 | 122.9279 | 123.0148 | 59.8663 | 59.8663
114.8281 | 123.2758 | -59.967 | 62.9333 | -0.060425 | 0.00048494 | 0.063641 | 0.062959 | 0.00025629 | -0.00056396 | -0.0014035 | 0.027191 | 0.0009528 | 0.066418 | 0.065634 | -0.001427 | 0.0031018 | 0.0030505 | 0.018311 | 62.851 | -60.0403 | 63.0569 | -59.8022 | -60.1364 | 0.10071 | 0.10071 | 62.8326 | -59.9716 | 63.121 | -59.8984 | -59.9991 | -59.903 | -0.073242 | -0.082398 | 0.1236 | 0.1648 | 60.0677 | -0.16937 | 60.141 | -0.096131 | -0.004578 | -0.10071 | 0.18768 | 0.068665 | 0.064087 | -0.032043 | 0.068665 | -0.027465 | 0.23804 | 123.0972 | 0.073243 | 123.0927 | 122.8912 | 122.8043 | 122.818 | 122.7997 | -122.9736 | -122.905 | 123.024 | 123.0881 | 59.9854 | 60.0677
115.8906 | 123.2666 | -59.9808 | 62.9196 | -0.13672 | 0.00069854 | 0.064495 | 0.064027 | 0.0023925 | -0.0033412 | 9.193e-05 | -0.046051 | 0.0015936 | 0.062572 | 0.06777 | -0.0042042 | 0.0028882 | -0.0022901 | -0.022888 | 62.8235 | -60.0769 | 63.0432 | -59.8389 | -60.1959 | -0.022888 | -0.022888 | 62.8281 | -59.9899 | 63.1485 | -60.228 | -60.0632 | -59.7748 | -0.09613 | -0.096131 | 0.1236 | 0.14191 | 59.9579 | -0.21515 | 60.054 | -0.11902 | -0.009155 | -0.091553 | 0.22888 | -0.24719 | 0.20599 | -0.082397 | 0.21515 | -0.073242 | 0.23804 | 123.1201 | -0.23804 | 123.1384 | 122.9004 | 122.818 | 122.8043 | 122.8088 | -122.9965 | -122.9095 | 123.024 | 123.1293 | 59.9579 | 59.9579
116.8281 | 123.1888 | -59.9762 | 62.915 | -0.11383 | -0.00058326 | 0.063427 | 0.066377 | -0.00059811 | 7.6842e-05 | -0.0016171 | -0.012482 | 0.0015936 | 0.065563 | 0.064565 | -0.0024952 | 0.0033154 | 0.0017687 | -0.050354 | 62.8326 | -60.0677 | 62.9974 | -59.8755 | -60.2142 | -0.013733 | -0.054932 | 62.8281 | -59.9716 | 63.0386 | -60.0128 | -60.1135 | -59.9808 | -0.091553 | -0.082397 | 0.082398 | 0.10071 | 59.9625 | -0.23804 | 60.054 | -0.14648 | 0.004577 | -0.086975 | 0.1236 | -0.036621 | -0.004578 | -0.13733 | -0.009155 | -0.14191 | 0.19226 | 123.0652 | -0.041198 | 123.0103 | 122.9004 | 122.7997 | 122.8088 | 122.8043 | -122.9828 | -122.8867 | 122.9736 | 123.0148 | 59.9258 | 59.9213
117.8906 | 123.2208 | -59.9533 | 62.9425 | -0.037537 | 0.0013393 | 0.065563 | 0.066377 | -0.0012391 | -0.0012048 | -0.0011899 | -0.0094299 | -0.0001154 | 0.065136 | 0.067983 | -0.0027088 | 0.0026746 | -0.0012219 | -0.059509 | 62.8372 | -60.0632 | 62.9974 | -59.8801 | -60.2325 | -0.036621 | -0.032043 | 62.8235 | -60.0037 | 63.0386 | -60.0082 | -59.935 | -59.8114 | -0.10986 | -0.10529 | 0.054932 | 0.073242 | 59.9167 | -0.27924 | 60.0266 | -0.16937 | -0.050354 | -0.11902 | 0.09613 | -0.054932 | 0.14191 | 0.01831 | 0.19226 | 0.068664 | 0.1831 | 123.0606 | -0.004578 | 123.0423 | 122.9004 | 122.8271 | 122.7905 | 122.7768 | -123.0057 | -122.9462 | 122.9507 | 122.9919 | 59.8938 | 59.9213
118.8281 | 123.23 | -59.9808 | 62.9654 | -0.11383 | 0.0045437 | 0.063427 | 0.065309 | 0.0013245 | -0.00035036 | -0.0037533 | -0.039948 | 0.0009528 | 0.064922 | 0.063925 | -0.0022816 | 0.0016064 | 0.0019823 | -0.036621 | 62.8464 | -60.0677 | 63.1531 | -59.7931 | -60.3561 | 0.004578 | -0.027466 | 62.8281 | -59.9808 | 63.0295 | -59.9808 | -60.0998 | -59.967 | -0.086975 | -0.11902 | 0.18768 | 0.18768 | 59.9854 | -0.37537 | 60.0723 | -0.28839 | 0 | -0.13733 | 0.064087 | 0 | 0.013733 | -0.11902 | 0.013733 | -0.11902 | 0.27466 | 123.2208 | 0 | 123.0103 | 122.9141 | 122.8088 | 122.8271 | 122.8088 | -123.0331 | -122.9462 | 123.1338 | 123.0103 | 59.9442 | 59.9533
119.8906 | 123.1567 | -59.9991 | 62.9929 | -0.068054 | 0.0013393 | 0.064495 | 0.067872 | 0.00025629 | -0.0014184 | 0.0013735 | -0.11014 | 0.0020208 | 0.065777 | 0.063711 | -0.0037768 | 0.0039562 | -0.0022901 | -0.022888 | 62.8418 | -60.0861 | 62.97 | -59.9304 | -60.2921 | -0.068665 | -0.086975 | 62.8784 | -59.9899 | 62.9929 | -60.0952 | -60.2234 | -60.0677 | -0.086976 | -0.15106 | -0.022888 | 0.068664 | 59.9304 | -0.29297 | 60.0174 | -0.20599 | 0.009155 | -0.11444 | 0 | -0.096131 | -0.068665 | -0.2243 | -0.07782 | -0.23346 | 0.15564 | 123.056 | -0.10529 | 122.9828 | 122.9279 | 122.8683 | 122.8409 | 122.8775 | -123.0789 | -122.9828 | 122.9691 | 122.9919 | 59.9762 | 59.9121
120.8281 | 123.1934 | -59.9716 | 62.9333 | -0.12909 | -0.00079686 | 0.062572 | 0.064668 | -0.0023071 | -0.00056396 | -0.0028989 | -0.0094299 | -0.0001154 | 0.065136 | 0.064138 | -0.00035897 | 0.00075204 | -0.0022901 | -0.036621 | 62.8281 | -60.0494 | 62.9974 | -59.8572 | -60.228 | -0.013733 | -0.050354 | 62.8189 | -59.9991 | 63.1302 | -60.1273 | -60.0586 | -59.9625 | -0.077819 | -0.10529 | 0.064087 | 0.11444 | 59.9579 | -0.25635 | 60.0357 | -0.17853 | -0.027465 | -0.11444 | 0.19684 | -0.15564 | 0.009156 | -0.086975 | 0.036621 | -0.05951 | 0.19226 | 123.0469 | -0.12817 | 123.1293 | 122.8775 | 122.818 | 122.7997 | 122.7905 | -122.9828 | -122.9324 | 122.9691 | 123.1018 | 59.935 | 59.9213
121.8906 | 123.2483 | -59.9762 | 62.915 | -0.029907 | 0.0034757 | 0.066204 | 0.065523 | 0.0013245 | 7.6842e-05 | -0.00054907 | -0.049103 | -0.0011834 | 0.065136 | 0.062216 | -0.0022816 | 0.0043836 | 0.00048713 | 0.004578 | 62.8098 | -60.0449 | 63.0478 | -59.8206 | -60.1776 | -0.009155 | 0 | 62.8189 | -60.0357 | 63.0798 | -59.9808 | -60.0723 | -59.9579 | -0.068665 | -0.10529 | 0.13275 | 0.15564 | 59.967 | -0.20142 | 60.0357 | -0.13275 | -0.05951 | -0.09613 | 0.16479 | -0.004578 | 0.01831 | -0.096131 | 0.07782 | -0.036621 | 0.2243 | 123.0927 | 0.054932 | 123.1155 | 122.8546 | 122.8546 | 122.7859 | 122.7951 | -122.9599 | -122.9507 | 123.024 | 123.056 | 59.9808 | 59.9762
122.8281 | 123.262 | -59.9533 | 62.9608 | -0.060425 | 0.0011257 | 0.063 | 0.063386 | -0.0020935 | -0.00013676 | -0.00076267 | -0.012482 | 0.0011664 | 0.064281 | 0.066061 | -0.0022816 | 0.0024608 | 0.0015551 | 0.009155 | 62.8372 | -60.0494 | 63.0569 | -59.8022 | -60.1593 | 0.064087 | 0.050354 | 62.8281 | -59.9808 | 63.1027 | -59.9304 | -60.0174 | -59.9167 | -0.09613 | -0.1236 | 0.096131 | 0.15106 | 60.0174 | -0.20599 | 60.1135 | -0.10986 | -0.027466 | -0.13275 | 0.14191 | 0.022888 | 0.036621 | -0.064087 | 0.064087 | -0.036621 | 0.24719 | 123.1064 | 0.050354 | 123.0835 | 122.8867 | 122.8088 | 122.7905 | 122.7814 | -123.0103 | -122.9416 | 123.0103 | 123.056 | 59.9625 | 60.0037
123.8906 | 123.2895 | -59.9762 | 62.9059 | -0.11383 | -0.00079686 | 0.063854 | 0.064668 | 0.0026063 | 0.00029044 | -0.0011899 | -0.042999 | -0.0007562 | 0.065136 | 0.061575 | -0.0022816 | 0.0022472 | 0.0024097 | 0.050354 | 62.796 | -60.1044 | 63.0615 | -59.7839 | -60.2234 | 0.004578 | 0.004578 | 62.8372 | -59.9945 | 63.0753 | -59.9808 | -60.0632 | -59.935 | -0.12817 | -0.10986 | 0.15564 | 0.19226 | 59.9808 | -0.24719 | 60.1089 | -0.11902 | -0.018311 | -0.068665 | 0.16937 | -0.004578 | 0.041198 | -0.086975 | 0.059509 | -0.068664 | 0.32043 | 123.1659 | 0.013733 | 123.0698 | 122.9004 | 122.8317 | 122.7722 | 122.8134 | -123.0103 | -122.9004 | 123.0377 | 123.0515 | 60.0266 | 59.9808
124.8281 | 123.2208 | -59.9762 | 62.9471 | -0.083313 | 0.00069854 | 0.062786 | 0.064027 | 0.0013245 | 7.6842e-05 | -0.00033547 | -0.015534 | 9.8198e-05 | 0.062359 | 0.065634 | -0.0042042 | 0.0041698 | 0.00070073 | -0.022888 | 62.8601 | -60.0815 | 62.9883 | -59.848 | -59.9487 | 0.036621 | -0.064087 | 62.8281 | -59.9808 | 63.0478 | -60.0082 | -60.1044 | -59.9854 | -0.10529 | -0.086976 | 0.041198 | 0.12817 | 60.0128 | 0.027466 | 60.1181 | 0.13275 | -0.004578 | -0.11902 | 0.10071 | -0.032044 | -0.009156 | -0.12817 | -0.004578 | -0.1236 | 0.23346 | 123.0698 | -0.027466 | 123.0286 | 122.9416 | 122.8088 | 122.8363 | 122.8043 | -123.0286 | -122.9279 | 122.9645 | 123.024 | 59.9533 | 59.9121
125.8906 | 123.2208 | -59.9808 | 62.915 | -0.083313 | 0.0021939 | 0.064068 | 0.067232 | 0.0038879 | -0.00013676 | 0.0015871 | -0.039948 | -0.0011834 | 0.065136 | 0.059225 | -0.0016406 | 0.0028882 | -0.0048535 | -0.013733 | 62.8143 | -60.0677 | 63.0341 | -59.7977 | -60.2097 | -0.009155 | -0.004578 | 62.8326 | -60.0037 | 63.0798 | -59.9945 | -60.1089 | -59.9716 | -0.086975 | -0.10071 | 0.11902 | 0.18311 | 59.9716 | -0.22888 | 60.0586 | -0.14191 | -0.022888 | -0.082397 | 0.16479 | -0.013733 | 0.009155 | -0.12817 | 0.032043 | -0.10529 | 0.27008 | 123.1018 | 0.009155 | 123.0835 | 122.8821 | 122.8363 | 122.7951 | 122.8134 | -122.9828 | -122.9187 | 123.0148 | 123.0606 | 59.967 | 59.9762
126.8281 | 123.1979 | -59.9716 | 62.9379 | -0.075684 | -0.0010105 | 0.064281 | 0.064454 | -0.0042297 | 0.00071784 | 0.00073273 | -0.030792 | 0.0026618 | 0.064922 | 0.06542 | -0.0035632 | 0.0031018 | 0.0011279 | -0.036621 | 62.8372 | -60.0586 | 63.0066 | -59.8801 | -60.2188 | -0.018311 | -0.045776 | 62.8326 | -60.0082 | 63.1577 | -60.141 | -60.054 | -59.9808 | -0.086975 | -0.10071 | 0.068665 | 0.091553 | 59.9533 | -0.24719 | 60.0403 | -0.16022 | -0.036621 | -0.10529 | 0.21973 | -0.16937 | -0.009155 | -0.082397 | 0.027466 | -0.045776 | 0.17853 | 123.0652 | -0.13275 | 123.1659 | 122.8958 | 122.8409 | 122.8088 | 122.8043 | -122.9965 | -122.9462 | 122.9782 | 123.1293 | 59.935 | 59.9258
127.8281 | 123.2437 | -59.9579 | 62.9242 | -0.1062 | 0.0015529 | 0.063854 | 0.066163 | -0.00059811 | -0.0018458 | -0.0018307 | 0.0058289 | 0.0003118 | 0.067272 | 0.067129 | -0.004845 | -0.00010256 | -0.0010083 | 0.068665 | 62.8601 | -60.0311 | 63.121 | -59.7336 | -60.0952 | 0.11902 | 0.14648 | 62.8281 | -59.9533 | 63.0203 | -60.0861 | -59.9899 | -59.8892 | -0.073242 | -0.064087 | 0.19684 | 0.2243 | 60.0769 | -0.13733 | 60.1501 | -0.064087 | 0.004578 | -0.09613 | 0.096131 | -0.12817 | 0.068665 | -0.032043 | 0.064087 | -0.036621 | 0.29755 | 123.1522 | -0.13275 | 122.9736 | 122.8912 | 122.7814 | 122.818 | 122.7859 | -122.9553 | -122.8775 | 123.0789 | 122.9782 | 60.0266 | 60.1044
128.8906 | 123.262 | -59.9533 | 62.9242 | 0.054016 | 0.00091214 | 0.064068 | 0.065736 | 0.0028199 | -0.0018458 | -0.0026853 | -0.042999 | 0.0015936 | 0.064281 | 0.061575 | -0.00078617 | 0.0050244 | -0.00079467 | -0.027466 | 62.8143 | -60.0494 | 63.0478 | -59.816 | -60.1776 | -0.013733 | 0.009155 | 62.8372 | -59.9854 | 63.0936 | -59.9945 | -60.0815 | -59.935 | -0.09613 | -0.10986 | 0.1236 | 0.13733 | 59.9396 | -0.2243 | 60.0357 | -0.12817 | -0.032044 | -0.086975 | 0.16937 | -0.041199 | 0.01831 | -0.12817 | 0.050354 | -0.09613 | 0.23346 | 123.0972 | -0.009155 | 123.0789 | 122.8638 | 122.8226 | 122.7676 | 122.7905 | -122.9736 | -122.9095 | 123.0011 | 123.0469 | 59.9258 | 59.9625
129.8281 | 123.2849 | -59.9442 | 62.9471 | -0.090943 | 0.00069854 | 0.063854 | 0.065523 | -0.0044433 | -0.0018458 | -0.0031125 | -0.0033265 | 0.00138 | 0.066631 | 0.067343 | -0.0024952 | 0.0028882 | 0.0041187 | 0.041199 | 62.8418 | -60.0586 | 63.0981 | -59.761 | -60.1044 | 0.11902 | 0.13733 | 62.851 | -59.9716 | 63.1622 | -59.903 | -59.9945 | -59.8984 | -0.11444 | -0.10529 | 0.15106 | 0.18311 | 60.0632 | -0.16022 | 60.1776 | -0.045776 | -0.027466 | -0.096131 | 0.21515 | 0.041199 | 0.045777 | -0.050354 | 0.073243 | -0.022888 | 0.29755 | 123.1567 | 0.068665 | 123.1338 | 122.9004 | 122.8226 | 122.7859 | 122.7951 | -123.0057 | -122.9187 | 123.0423 | 123.1064 | 59.9854 | 60.0815
130.8906 | 123.1613 | -59.9899 | 62.9837 | -0.12146 | 0.00048494 | 0.062359 | 0.065736 | 0.0011109 | -0.0024866 | 0.0018009 | -0.12234 | 0.0037298 | 0.063854 | 0.067983 | -0.00078617 | 0.0048108 | -0.0025037 | 0.004578 | 62.851 | -60.0861 | 63.0157 | -59.8709 | -60.2371 | -0.022888 | 0 | 62.8693 | -60.0174 | 63.0112 | -60.0357 | -60.1685 | -60.0174 | -0.096131 | -0.13275 | 0.032043 | 0.11902 | 59.967 | -0.24719 | 60.0632 | -0.15106 | -0.027466 | -0.11444 | 0.027465 | -0.045777 | -0.027466 | -0.17853 | 0 | -0.15106 | 0.21515 | 123.1018 | -0.018311 | 123.0286 | 122.937 | 122.8867 | 122.8409 | 122.8592 | -123.0698 | -123.0011 | 123.0057 | 123.0011 | 59.9945 | 59.9899
131.8281 | 123.2254 | -59.9716 | 62.9379 | -0.090943 | 0.0013393 | 0.062786 | 0.063386 | -0.0018799 | -0.00099116 | -0.00076267 | -0.0002747 | 0.0015936 | 0.064922 | 0.062856 | -0.002068 | 0.0037426 | 0.0051867 | -0.018311 | 62.8601 | -60.0311 | 63.0249 | -59.848 | -60.2051 | 0.045776 | 0.009155 | 62.8464 | -59.9716 | 63.0844 | -59.967 | -60.0494 | -59.9396 | -0.059509 | -0.07782 | 0.086975 | 0.1236 | 60.0174 | -0.23346 | 60.0769 | -0.17395 | 0 | -0.091552 | 0.14648 | 0.004578 | 0.032044 | -0.077819 | 0.032044 | -0.077819 | 0.18311 | 123.056 | 0.004578 | 123.056 | 122.8912 | 122.818 | 122.8317 | 122.818 | -122.9691 | -122.9095 | 122.9965 | 123.056 | 59.9533 | 59.9808
132.8906 | 123.2346 | -59.9487 | 62.9288 | -0.12146 | 0.0024075 | 0.062359 | 0.063173 | 0.0026063 | -0.0016322 | 0.00094633 | -0.036896 | 0.00138 | 0.064281 | 0.068624 | -0.00078617 | 0.0039562 | -0.0035719 | -0.018311 | 62.8235 | -60.054 | 63.0478 | -59.7885 | -60.1913 | -0.004578 | 0.013733 | 62.8281 | -60.0128 | 63.0615 | -59.9899 | -60.0815 | -59.9442 | -0.10529 | -0.10529 | 0.11902 | 0.16022 | 59.9442 | -0.24262 | 60.0494 | -0.13733 | -0.064087 | -0.10071 | 0.13275 | -0.041199 | 0.004577 | -0.13275 | 0.068664 | -0.068665 | 0.2655 | 123.1018 | 0.022888 | 123.0743 | 122.8775 | 122.8409 | 122.7722 | 122.7768 | -122.9828 | -122.9416 | 122.9965 | 123.0103 | 59.9304 | 59.9625
133.8281 | 123.23 | -59.9625 | 62.9517 | -0.075684 | 0.0021939 | 0.062572 | 0.065309 | -0.0033753 | -0.00077756 | -0.00097627 | 0.011932 | 0.0005256 | 0.065563 | 0.060507 | -0.0035632 | 0.0022472 | 0.00048713 | 0.059509 | 62.8464 | -60.022 | 63.0798 | -59.7839 | -60.1364 | 0.11902 | 0.1236 | 62.8555 | -59.9716 | 63.089 | -59.9304 | -60.0266 | -59.9258 | -0.05951 | -0.10528 | 0.12817 | 0.17853 | 60.0815 | -0.17395 | 60.141 | -0.11444 | -0.009156 | -0.09613 | 0.13733 | 0.032043 | 0.036621 | -0.064087 | 0.045777 | -0.054931 | 0.23804 | 123.1018 | 0.041199 | 123.0606 | 122.8683 | 122.8271 | 122.8088 | 122.818 | -122.9736 | -122.9233 | 123.0423 | 123.0515 | 60.022 | 60.0861
134.8906 | 123.2529 | -59.9945 | 62.9196 | -0.25116 | 0.0021939 | 0.062572 | 0.065523 | 0.00025629 | -0.0012048 | -0.00076267 | -0.052155 | 0.0011664 | 0.065777 | 0.05837 | -0.00035897 | 0.0041698 | 0.0015551 | 0.1236 | 62.8006 | -60.0586 | 63.0753 | -59.7885 | -60.2051 | -0.013733 | 0.009155 | 62.8372 | -59.9762 | 63.0798 | -59.9716 | -60.0677 | -59.9442 | -0.064087 | -0.11902 | 0.15564 | 0.20599 | 59.9808 | -0.21057 | 60.0449 | -0.14648 | 0.018311 | -0.082398 | 0.16022 | 0.022888 | 0.050354 | -0.073242 | 0.032043 | -0.091553 | 0.27008 | 123.1338 | 0.004577 | 123.056 | 122.8592 | 122.8134 | 122.7951 | 122.8317 | -122.9782 | -122.8958 | 123.0698 | 123.0743 | 60.1181 | 60.0037
135.8281 | 123.3398 | -59.935 | 62.9562 | -0.11383 | 0.0032619 | 0.062572 | 0.06595 | -0.0023071 | -0.00056396 | -0.0041807 | 0.0088807 | 0.0020208 | 0.066204 | 0.056661 | -0.0018542 | 0.0024608 | -0.0022901 | 0.045776 | 62.8464 | -60.0357 | 63.089 | -59.7244 | -60.1318 | 0.11444 | 0.15564 | 62.8464 | -59.935 | 63.1256 | -59.8984 | -59.9899 | -59.8801 | -0.10071 | -0.10986 | 0.13275 | 0.21057 | 60.0494 | -0.19684 | 60.1501 | -0.09613 | 0 | -0.10986 | 0.16937 | 0.036622 | 0.054932 | -0.054931 | 0.054932 | -0.054931 | 0.31128 | 123.1247 | 0.036622 | 123.0606 | 122.8821 | 122.7814 | 122.7814 | 122.7814 | -122.9919 | -122.8912 | 123.024 | 123.0606 | 59.9808 | 60.0906
136.8906 | 123.2483 | -59.9762 | 62.9333 | -0.12146 | 0.0013393 | 0.066631 | 0.064027 | 0.0015381 | -0.00056396 | -0.00076267 | -0.1254 | 9.8198e-05 | 0.063 | 0.066061 | -0.0037768 | 0.0043836 | -0.0018629 | -0.032043 | 62.7823 | -60.0769 | 63.0341 | -59.8114 | -60.2005 | -0.059509 | 0.1831 | 62.8464 | -59.9854 | 63.1165 | -59.9716 | -60.0723 | -59.9396 | -0.10071 | -0.15106 | 0.10071 | 0.1648 | 59.9167 | -0.2243 | 60.0174 | -0.1236 | -0.009156 | -0.086975 | 0.18311 | 0.004577 | 0.036621 | -0.096131 | 0.045777 | -0.086975 | 0.2655 | 123.111 | 0.013733 | 123.1018 | 122.8592 | 122.8317 | 122.7585 | 122.8226 | -123.0103 | -122.9187 | 123.0103 | 123.0927 | 59.9442 | 60.1593
137.8281 | 123.2849 | -59.9213 | 62.9608 | -0.090943 | -0.0020785 | 0.063854 | 0.066377 | -0.0040161 | -0.0016322 | 9.193e-05 | -0.0002747 | -0.0001154 | 0.065777 | 0.065206 | -0.00099977 | 0.0043836 | 0.00070073 | 0.073242 | 62.8464 | -60.0494 | 63.0844 | -59.7565 | -60.0998 | 0.10986 | 0.46692 | 62.9105 | -59.8801 | 63.0844 | -59.8846 | -60.0174 | -59.9442 | -0.12817 | -0.11444 | 0.1236 | 0.16479 | 60.0311 | -0.17853 | 60.1593 | -0.050354 | 0.041199 | -0.050354 | 0.1236 | 0.036621 | -0.022888 | -0.09613 | -0.064087 | -0.13733 | 0.29297 | 123.1338 | -0.004578 | 122.9645 | 122.8958 | 122.7905 | 122.7676 | 122.8317 | -123.0103 | -122.8409 | 123.0057 | 123.0057 | 59.9945 | 60.3882
138.8906 | 123.1888 | -59.9854 | 62.9974 | -0.11383 | -0.00079686 | 0.063641 | 0.067018 | 0.0062379 | -0.0024866 | 0.0018009 | -0.094879 | 0.0015936 | 0.06599 | 0.070547 | -0.0018542 | 0.0043836 | -0.0050671 | 0.018311 | 62.8601 | -60.0769 | 62.9013 | -59.8068 | -60.1776 | 0.013733 | 0.004578 | 62.8784 | -59.9762 | 63.0524 | -60.0082 | -60.1364 | -60.0082 | -0.091552 | -0.13733 | -0.096131 | 0.17853 | 59.9991 | -0.19226 | 60.0906 | -0.10071 | 0.009156 | -0.11902 | 0.054931 | -0.022888 | -0.022888 | -0.15106 | -0.032044 | -0.16022 | 0.27008 | 122.9782 | -0.032044 | 123.0286 | 122.937 | 122.8546 | 122.8455 | 122.8638 | -123.0743 | -122.9736 | 122.8867 | 123.0377 | 60.0037 | 59.9899
139.8281 | 123.2986 | -59.935 | 62.9517 | -0.083313 | -0.0016513 | 0.064495 | 0.064882 | -0.0014527 | 0.00093144 | 0.00051913 | 0.039398 | -0.0009698 | 0.06599 | 0.057943 | -0.0016406 | 0.0011792 | -0.0010083 | 0.07782 | 62.8464 | -60.0174 | 63.0936 | -59.7336 | -60.1089 | 0.13275 | 0.16479 | 62.8647 | -59.967 | 63.121 | -59.8984 | -60.0037 | -59.9121 | -0.082397 | -0.10528 | 0.14191 | 0.20142 | 60.0677 | -0.17395 | 60.1501 | -0.091553 | -0.032043 | -0.086975 | 0.16937 | 0.036622 | 0.022889 | -0.068664 | 0.054932 | -0.036621 | 0.28381 | 123.111 | 0.068665 | 123.0881 | 122.8638 | 122.8317 | 122.7814 | 122.7997 | -122.9691 | -122.9187 | 123.0286 | 123.056 | 60.0128 | 60.0998
140.8906 | 123.1888 | -60.0128 | 62.9333 | -0.029907 | 0.0013393 | 0.064281 | 0.067445 | 0.0036743 | 7.6842e-05 | -0.0028989 | -0.07962 | 0.0005256 | 0.064495 | 0.064565 | -0.003136 | 0.0041698 | 0.0019823 | -0.09613 | 62.8372 | -60.0998 | 62.9471 | -59.935 | -60.3058 | -0.10071 | -0.11902 | 62.8372 | -60.0037 | 63.0112 | -60.0586 | -60.1822 | -60.0357 | -0.086975 | -0.096131 | 0.013733 | 0.077819 | 59.9121 | -0.29297 | 59.9991 | -0.20599 | 0.009155 | -0.096131 | 0.077819 | -0.045777 | -0.022889 | -0.16937 | -0.032044 | -0.17853 | 0.16479 | 123.0469 | -0.054932 | 123.0148 | 122.937 | 122.8409 | 122.85 | 122.85 | -123.0331 | -122.937 | 122.9599 | 123.024 | 59.9167 | 59.8938
141.8281 | 123.2574 | -59.9625 | 62.9196 | -0.037537 | 0.00048494 | 0.064068 | 0.064882 | -0.00081171 | 0.00050424 | 0.0018009 | 0.011932 | 0.0005256 | 0.066418 | 0.060079 | -0.0022816 | 0.00182 | -0.0012219 | -0.032043 | 62.8418 | -60.0586 | 63.0112 | -59.8343 | -60.2005 | 0.045776 | 0.018311 | 62.8464 | -59.9762 | 63.0798 | -59.9625 | -60.0586 | -59.9396 | -0.096131 | -0.07782 | 0.091552 | 0.12817 | 60.0082 | -0.23804 | 60.1044 | -0.14191 | -0.013733 | -0.073242 | 0.16022 | 0 | 0.022888 | -0.096131 | 0.036621 | -0.082398 | 0.2243 | 123.0698 | 0.013733 | 123.056 | 122.9004 | 122.8226 | 122.8043 | 122.8088 | -122.9782 | -122.8958 | 122.9736 | 123.0423 | 59.9304 | 59.9808
142.8906 | 123.1476 | -60.0082 | 62.9654 | -0.29694 | 0.0024075 | 0.061718 | 0.066377 | 0.0011109 | -0.0027002 | -0.00054907 | -0.10098 | 0.0028754 | 0.065777 | 0.063711 | -0.0018542 | 0.0041698 | 0.00070073 | 0.1236 | 62.8326 | -60.0861 | 62.9471 | -59.9442 | -60.3516 | -0.13275 | -0.15106 | 62.8464 | -60.0311 | 62.9929 | -60.0906 | -60.2051 | -60.0494 | -0.07782 | -0.13275 | -0.01831 | 0.064087 | 59.8755 | -0.34332 | 59.9533 | -0.2655 | -0.022888 | -0.11902 | 0.027466 | -0.082397 | -0.041198 | -0.19684 | -0.01831 | -0.17395 | 0.14191 | 123.0331 | -0.059509 | 123.024 | 122.9187 | 122.8775 | 122.8409 | 122.8546 | -123.0515 | -122.9965 | 122.9553 | 123.0011 | 60.1318 | 59.8572
143.8281 | 123.2346 | -59.9579 | 62.9562 | -0.060425 | -0.00079686 | 0.064709 | 0.063386 | -0.0018799 | -0.0024866 | -0.00033547 | 0.011932 | -0.0016108 | 0.065349 | 0.059439 | -0.0027088 | 0.003529 | 0.00048713 | 0.032043 | 62.8052 | -60.0311 | 63.1073 | -59.7656 | -60.1227 | 0.10986 | 0.11902 | 62.8235 | -59.9625 | 63.1073 | -59.9258 | -60.0174 | -59.9167 | -0.073242 | -0.15106 | 0.15106 | 0.19226 | 60.0677 | -0.16479 | 60.141 | -0.091553 | -0.004577 | -0.13275 | 0.15106 | 0.032044 | 0.041199 | -0.059509 | 0.045776 | -0.054932 | 0.2655 | 123.1384 | 0.036621 | 123.0698 | 122.8363 | 122.7859 | 122.7631 | 122.7814 | -122.9874 | -122.9187 | 123.0652 | 123.0652 | 59.9899 | 60.0769
144.8906 | 123.2574 | -59.9762 | 62.9196 | -0.098572 | 0.0021939 | 0.065136 | 0.064454 | 0.0064515 | -0.0014184 | -0.0028989 | -0.015534 | 0.0011664 | 0.068554 | 0.057943 | -0.004845 | 0.0028882 | -0.0014355 | -0.009155 | 62.8006 | -60.0677 | 63.0524 | -59.6054 | -60.1318 | -0.018311 | -0.022888 | 62.8235 | -59.9899 | 63.1073 | -59.9854 | -60.0861 | -59.9579 | -0.091553 | -0.11902 | 0.13275 | 0.37079 | 59.9579 | -0.15564 | 60.0494 | -0.064087 | -0.013733 | -0.096131 | 0.18768 | -0.009156 | 0.01831 | -0.10986 | 0.032043 | -0.096131 | 0.46234 | 123.1201 | 0.004577 | 123.0972 | 122.8683 | 122.8134 | 122.7768 | 122.7997 | -122.9874 | -122.9095 | 123.0286 | 123.0835 | 59.967 | 59.9533
145.8281 | 123.2071 | -59.9579 | 62.9379 | -0.060425 | 0.0011257 | 0.063213 | 0.065523 | 0.0045289 | -0.00099116 | -0.0020443 | 0.0058289 | 0.0005256 | 0.066631 | 0.056234 | -0.002068 | 0.0031018 | -0.0022901 | -0.045776 | 62.8281 | -60.0677 | 63.0112 | -59.8663 | -60.2188 | -0.009155 | -0.10529 | 62.8189 | -59.9487 | 63.0157 | -59.9899 | -60.1135 | -59.9625 | -0.10986 | -0.10986 | 0.073242 | 0.091553 | 59.9487 | -0.26093 | 60.0586 | -0.15106 | 0.009156 | -0.11902 | 0.07782 | -0.032043 | -0.004577 | -0.15564 | -0.013733 | -0.1648 | 0.20142 | 123.0789 | -0.041199 | 122.9645 | 122.8958 | 122.7676 | 122.7859 | 122.7768 | -123.0057 | -122.8867 | 122.9691 | 122.9736 | 59.9121 | 59.8526
146.8906 | 123.1705 | -59.9945 | 62.9379 | -0.068054 | -0.0014377 | 0.063854 | 0.065736 | 0.00046989 | 0.00050424 | -0.00076267 | -0.091827 | 0.0022346 | 0.067486 | 0.059652 | -0.0029224 | 0.0031018 | 0.00048713 | -0.064087 | 62.8784 | -60.1044 | 62.9105 | -59.9533 | -60.2966 | -0.10986 | -0.14191 | 62.8693 | -59.9991 | 63.002 | -60.0861 | -60.2097 | -60.0449 | -0.10986 | -0.059509 | -0.027466 | 0.041199 | 59.8846 | -0.30212 | 59.9945 | -0.19226 | -0.004577 | -0.068664 | 0.064087 | -0.091553 | -0.050354 | -0.21515 | -0.045777 | -0.21057 | 0.15106 | 123.0148 | -0.086976 | 123.0011 | 122.9828 | 122.8683 | 122.8729 | 122.8638 | -123.0423 | -122.937 | 122.905 | 122.9965 | 59.9304 | 59.8526
147.8281 | 123.2758 | -59.9579 | 62.9379 | -0.029907 | 0.00027134 | 0.061932 | 0.065309 | -0.0018799 | -0.002273 | -0.0011899 | 0.027191 | 0.0011664 | 0.066631 | 0.06307 | -0.00057257 | 0.0024608 | 0.0028369 | 0 | 62.851 | -60.0311 | 63.0478 | -59.8068 | -60.1639 | 0.068665 | 0.086975 | 62.8372 | -59.967 | 63.0798 | -59.8938 | -60.0128 | -59.9121 | -0.073242 | -0.086975 | 0.10986 | 0.15106 | 60.0266 | -0.20599 | 60.0998 | -0.13275 | -0.009155 | -0.10071 | 0.14191 | 0.064087 | 0.045777 | -0.054931 | 0.054932 | -0.045776 | 0.2243 | 123.0789 | 0.073242 | 123.0469 | 122.8821 | 122.8043 | 122.8088 | 122.7951 | -122.9691 | -122.905 | 123.0057 | 123.0377 | 59.9579 | 60.0449
148.8906 | 123.2025 | -59.9945 | 62.9425 | -0.1062 | -0.0014377 | 0.061291 | 0.066377 | 0.0028199 | -0.0012048 | -0.0022581 | -0.097931 | 0.0011664 | 0.06599 | 0.062216 | -0.0037768 | 0.0031018 | -0.0059217 | -0.07782 | 62.8372 | -60.1227 | 62.9425 | -59.9396 | -60.2829 | -0.09613 | -0.1236 | 62.851 | -60.0082 | 63.0203 | -60.0494 | -60.1547 | -59.9899 | -0.12817 | -0.10529 | 0 | 0.054932 | 59.8984 | -0.28839 | 60.0266 | -0.16022 | -0.013733 | -0.091553 | 0.07782 | -0.054931 | 0.004578 | -0.16022 | 0.018311 | -0.14648 | 0.18311 | 123.0652 | -0.041198 | 123.0286 | 122.9599 | 122.8592 | 122.8317 | 122.8455 | -123.0652 | -122.9507 | 122.937 | 123.0148 | 59.9167 | 59.8709
149.8281 | 123.2941 | -59.9442 | 62.97 | -0.083313 | 0.00027134 | 0.061932 | 0.065523 | -0.0031617 | -0.0014184 | 0.00030553 | 0.018036 | 0.00138 | 0.065563 | 0.064779 | 0.00049563 | 0.00182 | -0.00036747 | 0.032043 | 62.8601 | -60.0311 | 63.089 | -59.7519 | -60.1273 | 0.11444 | 0.12817 | 62.851 | -59.9533 | 63.1302 | -59.8892 | -59.9716 | -59.8892 | -0.086975 | -0.10986 | 0.11902 | 0.19226 | 60.0586 | -0.1831 | 60.1456 | -0.09613 | -0.009155 | -0.11902 | 0.16022 | 0.054932 | 0.054932 | -0.027466 | 0.064087 | -0.018311 | 0.27924 | 123.1201 | 0.064087 | 123.0835 | 122.8912 | 122.8043 | 122.8043 | 122.7951 | -123.0011 | -122.9233 | 123.0331 | 123.0743 | 59.9762 | 60.0723
150.8906 | 123.1705 | -59.9625 | 62.9837 | -0.12146 | 0.00069854 | 0.063427 | 0.066163 | 0.0011109 | -0.005691 | 9.193e-05 | -0.085724 | 0.0035162 | 0.065777 | 0.063284 | -0.0022816 | 0.0031018 | -0.0037855 | 0.022888 | 62.8738 | -60.0861 | 63.0249 | -59.8663 | -60.228 | -0.004578 | -0.004578 | 62.8738 | -59.9716 | 63.0295 | -60.0311 | -60.1547 | -60.0128 | -0.1236 | -0.10986 | 0.041198 | 0.09613 | 59.9579 | -0.2655 | 60.0815 | -0.14191 | -0.009156 | -0.10986 | 0.045776 | -0.068665 | -0.050354 | -0.19226 | -0.041198 | -0.18311 | 0.21973 | 123.111 | -0.059509 | 123.0011 | 122.9599 | 122.8455 | 122.8363 | 122.8363 | -123.0698 | -122.9553 | 122.9874 | 122.9919 | 59.9854 | 59.9579
151.8281 | 123.1476 | -59.9625 | 62.9745 | -0.052796 | 5.7742e-05 | 0.062359 | 0.066163 | 0.00025629 | -0.00099116 | -0.0024717 | 0.014984 | 0.0009528 | 0.065777 | 0.065847 | -0.001427 | 0.00182 | 0.00091433 | -0.054932 | 62.8235 | -60.0449 | 62.9883 | -59.8663 | -60.2142 | -0.022888 | -0.064087 | 62.8326 | -59.9991 | 63.0295 | -60.0128 | -60.1273 | -59.9716 | -0.082398 | -0.15106 | 0.013733 | 0.09613 | 59.9396 | -0.25177 | 60.022 | -0.16937 | -0.036621 | -0.14191 | 0.054932 | -0.050354 | -0.009156 | -0.16479 | 0.027465 | -0.12817 | 0.17853 | 123.0331 | -0.013733 | 123.0286 | 122.8683 | 122.8317 | 122.7859 | 122.7951 | -123.0194 | -122.9736 | 122.9507 | 122.9919 | 59.9075 | 59.8984
152.8906 | 123.2666 | -59.9762 | 62.9288 | -0.068054 | -0.00036966 | 0.065563 | 0.065736 | 0.0017517 | 7.6842e-05 | -0.0018307 | -0.055206 | 0.0005256 | 0.063 | 0.061148 | -0.002068 | 0.0041698 | -0.00058107 | -0.054932 | 62.796 | -60.0494 | 63.0112 | -59.8206 | -60.2097 | -0.022888 | -0.032043 | 62.8235 | -59.9991 | 63.0936 | -59.9762 | -60.0998 | -59.9442 | -0.073242 | -0.13275 | 0.082397 | 0.15564 | 59.9533 | -0.23346 | 60.0266 | -0.16022 | -0.022888 | -0.10529 | 0.16479 | 0 | 0.032043 | -0.1236 | 0.054931 | -0.10071 | 0.22888 | 123.0606 | 0.022888 | 123.0927 | 122.8455 | 122.8226 | 122.7722 | 122.7997 | -122.9782 | -122.9279 | 122.9874 | 123.0698 | 59.9213 | 59.9442
153.8281 | 123.2208 | -59.9716 | 62.9379 | -0.037537 | 5.7742e-05 | 0.063427 | 0.064882 | 0.0028199 | 7.6842e-05 | 0.0015871 | 0.014984 | 0.0022346 | 0.065563 | 0.063284 | -0.0018542 | 0.0011792 | -0.00036747 | -0.027466 | 62.8189 | -60.054 | 62.9608 | -59.9075 | -60.2097 | -0.027466 | -0.022888 | 62.851 | -59.9854 | 63.0432 | -60.0037 | -60.0769 | -59.9487 | -0.082397 | -0.11902 | 0.022888 | 0.064087 | 59.9442 | -0.23804 | 60.0266 | -0.15564 | -0.013733 | -0.086975 | 0.10529 | -0.032043 | 0.022889 | -0.10529 | 0.036622 | -0.091552 | 0.14648 | 123.0148 | -0.01831 | 123.0286 | 122.8729 | 122.8363 | 122.7905 | 122.8226 | -122.9919 | -122.9233 | 122.9324 | 123.0148 | 59.9442 | 59.9487
154.8906 | 123.175 | -59.9762 | 62.9471 | -0.014649 | 0.00048494 | 0.063641 | 0.067872 | 4.2692e-05 | -0.00056396 | -0.0018307 | -0.073517 | 0.0005256 | 0.064495 | 0.06777 | -0.0022816 | 0.003529 | 0.0017687 | -0.086975 | 62.8738 | -60.1044 | 62.9242 | -59.9533 | -60.2921 | -0.10071 | -0.11902 | 62.851 | -60.022 | 63.0066 | -60.0632 | -60.173 | -60.0128 | -0.12817 | -0.073243 | -0.022889 | 0.022888 | 59.8755 | -0.31586 | 60.0037 | -0.18768 | -0.045777 | -0.096131 | 0.059509 | -0.086975 | -0.036621 | -0.19684 | 0.009156 | -0.15106 | 0.15106 | 123.0286 | -0.041198 | 123.0286 | 122.9782 | 122.8729 | 122.85 | 122.8271 | -123.0515 | -122.9691 | 122.9004 | 122.9828 | 59.8892 | 59.8572
155.8281 | 123.1934 | -59.9945 | 62.9013 | -0.12909 | 0.0011257 | 0.062786 | 0.065309 | -0.0010253 | 0.0015722 | -0.0024717 | -0.0033265 | 0.0005256 | 0.065349 | 0.062643 | -0.00014517 | 0.0016064 | 0.0017687 | -0.050354 | 62.8418 | -60.0403 | 62.9883 | -59.8663 | -60.2234 | -0.027466 | -0.068665 | 62.8464 | -60.0037 | 63.0478 | -60.0357 | -60.0906 | -59.9899 | -0.045776 | -0.059509 | 0.086975 | 0.12817 | 59.967 | -0.22888 | 60.0128 | -0.18311 | -0.009155 | -0.054931 | 0.14648 | -0.041199 | 0.004578 | -0.09613 | 0.013733 | -0.086975 | 0.17395 | 123.0286 | -0.032044 | 123.0515 | 122.8821 | 122.85 | 122.8363 | 122.8409 | -122.9416 | -122.905 | 122.9828 | 123.0423 | 59.9442 | 59.9258
156.8906 | 123.1064 | -60.0037 | 62.9471 | -0.098572 | 0.0030483 | 0.060863 | 0.068941 | 0.00025629 | 0.00029044 | 0.0011599 | -0.070465 | 0.0024482 | 0.068767 | 0.059866 | -0.002068 | 0.003529 | 0.0011279 | -0.086975 | 62.8601 | -60.1089 | 62.9196 | -59.9899 | -60.3378 | -0.11902 | -0.16479 | 62.883 | -60.0357 | 62.9791 | -60.1227 | -60.2234 | -60.0449 | -0.10529 | -0.086976 | -0.027466 | 0.013733 | 59.8846 | -0.33417 | 59.9899 | -0.22888 | -0.032044 | -0.064087 | 0.032043 | -0.11902 | -0.041199 | -0.21973 | -0.009155 | -0.18768 | 0.11902 | 123.0286 | -0.086975 | 123.0148 | 122.9691 | 122.9187 | 122.8638 | 122.8867 | -123.056 | -122.9828 | 122.9233 | 122.9828 | 59.9167 | 59.8389
157.8281 | 123.23 | -59.9716 | 62.9333 | 0.00824 | 0.00048494 | 0.062359 | 0.063386 | -0.0010253 | -0.0035548 | 0.00051913 | 0.039398 | 0.0018072 | 0.064709 | 0.063284 | -0.0029224 | 0.003529 | -0.0037855 | -0.091553 | 62.8784 | -60.022 | 62.9883 | -59.8618 | -60.2005 | 0.009155 | -0.009155 | 62.8464 | -59.9854 | 63.0478 | -59.9899 | -60.0677 | -59.967 | -0.050354 | -0.054932 | 0.054931 | 0.10986 | 59.9808 | -0.22888 | 60.0311 | -0.17853 | -0.013733 | -0.086975 | 0.11444 | -0.01831 | 0.004578 | -0.09613 | 0.018311 | -0.082397 | 0.16022 | 123.0103 | -0.004577 | 123.0331 | 122.9004 | 122.8317 | 122.85 | 122.818 | -122.9553 | -122.9187 | 122.9599 | 123.0194 | 59.8801 | 59.9625
158.8281 | 123.2712 | -59.967 | 62.9242 | -0.11383 | 0.0032619 | 0.065777 | 0.064241 | -0.00059811 | 0.00029044 | 0.00051913 | -0.1315 | -0.000329 | 0.064922 | 0.06542 | -0.002068 | 0.0031018 | 0.0011279 | -0.022888 | 62.8098 | -60.054 | 63.0524 | -59.8206 | -60.2005 | -0.032043 | 0.19226 | 62.8189 | -59.9808 | 63.1073 | -59.9625 | -60.0769 | -59.9258 | -0.086975 | -0.11444 | 0.12817 | 0.14648 | 59.935 | -0.23346 | 60.022 | -0.14648 | -0.013733 | -0.10529 | 0.18311 | 0.004578 | 0.041199 | -0.10986 | 0.054932 | -0.09613 | 0.23346 | 123.1064 | 0.018311 | 123.0881 | 122.8638 | 122.7997 | 122.7768 | 122.7859 | -122.9782 | -122.905 | 123.0194 | 123.0743 | 59.9442 | 60.1593
159.8281 | 123.23 | -59.9762 | 62.9333 | -0.12909 | -0.0010105 | 0.063213 | 0.06595 | 0.0011109 | 0.00029044 | -0.0014035 | -0.0063781 | 0.0015936 | 0.065563 | 0.068411 | -0.002068 | 0.0028882 | -0.0027173 | -0.045776 | 62.8372 | -60.0586 | 62.9974 | -59.8755 | -60.2325 | 0.13733 | -0.004578 | 62.883 | -59.9625 | 63.0524 | -59.9945 | -60.0906 | -59.967 | -0.082398 | -0.096131 | 0.064087 | 0.10071 | 60.1135 | -0.25635 | 60.1959 | -0.17395 | 0.013733 | -0.050354 | 0.11902 | -0.018311 | 0.009155 | -0.11444 | -0.004578 | -0.12817 | 0.18311 | 123.056 | -0.032044 | 123.0148 | 122.8958 | 122.8455 | 122.8134 | 122.8592 | -122.9919 | -122.8958 | 122.9736 | 123.0286 | 59.9304 | 59.9716
160.8906 | 123.1384 | -60.0037 | 62.9608 | -0.12146 | 0.0017667 | 0.064709 | 0.068086 | -0.0010253 | 7.6842e-05 | 0.00051913 | -0.11014 | 0.0020208 | 0.066418 | 0.066061 | -0.001427 | 0.0026746 | -0.0025037 | -0.082397 | 62.851 | -60.1089 | 62.9059 | -59.9716 | -60.3287 | -0.09613 | -0.16022 | 62.8784 | -60.022 | 62.9471 | -60.3378 | -60.0174 | -59.7977 | -0.10529 | -0.10986 | -0.054931 | 0.032043 | 59.9075 | -0.32501 | 60.0128 | -0.21973 | -0.018311 | -0.082397 | -0.013732 | -0.33417 | 0.20599 | -0.013733 | 0.22431 | 0.004578 | 0.13733 | 123.0148 | -0.31586 | 122.9691 | 122.9599 | 122.9004 | 122.8546 | 122.8821 | -123.0698 | -122.9828 | 122.9095 | 122.9507 | 59.9213 | 59.8434
161.8438 | 123.1293 | -60.0037 | 63.0112 | 0.015869 | -0.00036966 | 0.061932 | 0.066377 | 0.00025629 | -0.0020594 | -0.0022581 | -0.13455 | 9.8198e-05 | 0.06599 | 0.069052 | -0.0029224 | 0.003529 | -0.0027173 | 0.004578 | 62.8967 | -60.0815 | 62.9654 | -59.9075 | -59.9854 | 0.21515 | 0.027466 | 62.9059 | -60.0128 | 63.0157 | -60.0357 | -60.1593 | -60.0311 | -0.07782 | -0.11444 | -0.045776 | 0.09613 | 60.2188 | 0.01831 | 60.2966 | 0.09613 | -0.009155 | -0.10529 | 0.004578 | -0.032044 | -0.027466 | -0.15564 | -0.018311 | -0.14648 | 0.17395 | 123.0469 | -0.022889 | 123.0286 | 122.9782 | 122.9187 | 122.9004 | 122.9095 | -123.0927 | -123.024 | 122.9691 | 123.0194 | 60.0082 | 60.0311
162.8906 | 123.143 | -59.9991 | 62.9745 | -0.022278 | 0.0013393 | 0.062786 | 0.066804 | 0.0030335 | 0.0026404 | -0.0018307 | -0.094879 | 0.0028754 | 0.066631 | 0.057516 | -0.0022816 | 0.0060924 | 0.0021961 | -0.013733 | 62.851 | -60.0861 | 62.97 | -59.8984 | -60.2646 | -0.045776 | -0.054932 | 62.8738 | -60.0082 | 63.002 | -60.0769 | -60.1959 | -60.0266 | -0.086976 | -0.1236 | -0.004577 | 0.10071 | 59.9533 | -0.2655 | 60.0403 | -0.17853 | -0.009156 | -0.10071 | 0.027466 | -0.07782 | -0.027466 | -0.19684 | -0.01831 | -0.18768 | 0.18768 | 123.056 | -0.068664 | 123.0103 | 122.937 | 122.8821 | 122.85 | 122.8729 | -123.0606 | -122.9828 | 122.9691 | 123.0011 | 59.9854 | 59.9442
163.8281 | 123.2117 | -59.9533 | 62.97 | -0.1062 | 0.00027134 | 0.064068 | 0.065095 | -0.0027343 | -0.0014184 | -0.0011899 | 0.033295 | 0.0005256 | 0.067272 | 0.063284 | -0.0016406 | 0.00182 | 0.0011279 | -0.045776 | 62.8418 | -60.0494 | 62.9791 | -59.697 | -60.1456 | -0.027466 | -0.054932 | 62.8464 | -59.9991 | 63.0524 | -59.9808 | -60.0998 | -59.9625 | -0.09613 | -0.12817 | 0.009155 | 0.25635 | 59.9258 | -0.19226 | 60.022 | -0.096131 | -0.045776 | -0.1236 | 0.082397 | -0.027466 | -0.009155 | -0.14648 | 0.036621 | -0.10071 | 0.35248 | 123.0286 | 0.01831 | 123.0515 | 122.8912 | 122.8455 | 122.7951 | 122.7997 | -123.0194 | -122.9691 | 122.9324 | 123.0057 | 59.9075 | 59.8984
164.8906 | 123.2208 | -60.0311 | 62.97 | -0.075684 | 0.0019803 | 0.063854 | 0.065736 | -0.0010253 | -0.0012048 | 9.193e-05 | -0.088776 | 0.0011664 | 0.06599 | 0.065206 | -0.0018542 | 0.0043836 | -0.00058107 | -0.082397 | 62.8601 | -60.1227 | 62.8922 | -59.9945 | -60.3287 | -0.07782 | -0.15564 | 62.8693 | -60.0174 | 63.0295 | -60.379 | -60.4431 | -60.0266 | -0.091553 | -0.10986 | -0.07782 | 0.036621 | 59.9533 | -0.29755 | 60.0449 | -0.20599 | 0.013733 | -0.10071 | 0.059509 | -0.3479 | 0.004578 | -0.41199 | -0.009155 | -0.42572 | 0.12817 | 123.0148 | -0.36163 | 123.0469 | 122.9828 | 122.8867 | 122.8912 | 122.9004 | -123.0927 | -122.9874 | 122.9233 | 123.0606 | 59.9487 | 59.8755
165.8281 | 123.2208 | -59.9487 | 62.9333 | -0.098572 | 0.0021939 | 0.063854 | 0.065095 | -0.00017091 | -0.0044092 | -0.00076267 | 0.0088807 | 0.0003118 | 0.064281 | 0.053671 | -0.0022816 | 0.0026746 | 0.00091433 | -0.036621 | 62.8418 | -60.0586 | 62.9883 | -59.8709 | -60.2142 | -0.013733 | -0.045776 | 62.8418 | -60.0037 | 63.0386 | -59.9991 | -60.0998 | -59.967 | -0.10986 | -0.091553 | 0.054931 | 0.077819 | 59.935 | -0.2655 | 60.0449 | -0.15564 | -0.054932 | -0.091553 | 0.10529 | -0.050354 | -0.018311 | -0.15106 | 0.036621 | -0.09613 | 0.18768 | 123.0469 | 0.004578 | 123.0423 | 122.9004 | 122.8455 | 122.7905 | 122.7905 | -122.9919 | -122.937 | 122.937 | 122.9874 | 59.9121 | 59.903
166.8906 | 123.2574 | -59.9442 | 62.9425 | -0.052796 | -0.00079686 | 0.061932 | 0.064668 | -0.00081171 | -0.00013676 | -0.0026853 | 0.030243 | 0.0018072 | 0.064281 | 0.056021 | -0.003136 | 0.003529 | 5.9726e-05 | -0.013733 | 62.8418 | -60.0449 | 63.0295 | -59.8022 | -60.1593 | 0.050354 | 0.054932 | 62.8647 | -59.9579 | 63.0936 | -59.9396 | -60.0494 | -59.9167 | -0.10071 | -0.10071 | 0.086975 | 0.14191 | 59.9945 | -0.21515 | 60.0952 | -0.11444 | -0.013733 | -0.07782 | 0.15106 | 0.004578 | 0.027466 | -0.10529 | 0.041199 | -0.091552 | 0.24262 | 123.0743 | 0.018311 | 123.0515 | 122.8867 | 122.8226 | 122.7859 | 122.8088 | -122.9874 | -122.9004 | 122.9736 | 123.0377 | 59.9304 | 59.9991
167.8281 | 123.2391 | -59.9579 | 62.9333 | -0.090943 | 0.0019803 | 0.064922 | 0.066163 | 0.00089729 | -0.0033412 | -0.0024717 | -0.0063781 | 0.0009528 | 0.064068 | 0.064352 | -0.0022816 | 0.0043836 | -0.0033581 | -0.045776 | 62.8281 | -60.0632 | 63.0112 | -59.8389 | -60.2234 | -0.032043 | -0.041199 | 62.8281 | -59.9945 | 63.0524 | -60.022 | -60.0861 | -59.935 | -0.10528 | -0.10529 | 0.077819 | 0.11902 | 59.9258 | -0.2655 | 60.0311 | -0.16022 | -0.036621 | -0.10529 | 0.11902 | -0.064087 | 0.022888 | -0.12817 | 0.059509 | -0.091553 | 0.2243 | 123.0743 | -0.027466 | 123.0469 | 122.8912 | 122.8226 | 122.7859 | 122.7859 | -122.9965 | -122.9279 | 122.9691 | 123.0103 | 59.9121 | 59.9167
168.8906 | 123.175 | -59.9716 | 62.9974 | -0.014649 | -0.00036966 | 0.064068 | 0.066163 | 0.00068369 | -0.0018458 | -0.0033261 | -0.049103 | 0.0022346 | 0.064709 | 0.066274 | -0.0033496 | 0.0043836 | -0.0018629 | 0.032043 | 62.8784 | -60.0769 | 62.9929 | -59.8755 | -60.1959 | 0.045776 | 0.036621 | 62.8784 | -59.9808 | 63.0478 | -60.0128 | -60.1318 | -59.9899 | -0.10529 | -0.11902 | -0.004578 | 0.096131 | 60.0174 | -0.2243 | 60.1227 | -0.11902 | -0.009155 | -0.11902 | 0.050354 | -0.041198 | -0.01831 | -0.16022 | -0.009155 | -0.15106 | 0.20142 | 123.0698 | -0.032043 | 123.0286 | 122.9553 | 122.8592 | 122.85 | 122.85 | -123.0743 | -122.9782 | 122.9645 | 123.0194 | 60.0037 | 60.0082
169.8281 | 123.2117 | -59.9762 | 62.9562 | -0.090943 | 0.00048494 | 0.061291 | 0.066163 | -0.0012391 | -0.0016322 | 0.00094633 | 0.0027771 | 0.0005256 | 0.065563 | 0.064138 | -0.001427 | 0.00096564 | 0.0028369 | -0.022888 | 62.8281 | -60.054 | 62.9929 | -59.8801 | -60.2234 | -0.013733 | -0.050354 | 62.8418 | -59.9945 | 63.121 | -60.0998 | -60.0632 | -59.9487 | -0.07782 | -0.12817 | 0.036621 | 0.09613 | 59.9625 | -0.24719 | 60.0403 | -0.16937 | -0.018311 | -0.11444 | 0.16479 | -0.1236 | 0.027466 | -0.086975 | 0.045777 | -0.068664 | 0.17395 | 123.0469 | -0.10529 | 123.1155 | 122.8821 | 122.8363 | 122.8043 | 122.818 | -123.0103 | -122.9507 | 122.9691 | 123.0972 | 59.9533 | 59.9258
170.8906 | 123.1384 | -59.9716 | 63.002 | -0.068054 | 0.0019803 | 0.063854 | 0.065309 | -0.0023071 | -0.0027002 | -0.00097627 | -0.018585 | 0.0003118 | 0.065777 | 0.06307 | -0.0022816 | 0.003529 | -0.0031445 | 0.064087 | 62.8647 | -60.0311 | 63.0386 | -59.8206 | -60.1547 | 0.082397 | 0.050354 | 62.8647 | -59.967 | 63.0066 | -60.0037 | -60.1089 | -60.0037 | -0.059509 | -0.13733 | 0.036621 | 0.15106 | 60.054 | -0.18311 | 60.1135 | -0.1236 | 0.004578 | -0.13733 | 0.004578 | -0.032043 | -0.032043 | -0.13733 | -0.036621 | -0.14191 | 0.21057 | 123.0698 | -0.036621 | 122.9736 | 122.8958 | 122.8317 | 122.8363 | 122.8363 | -123.0331 | -122.9691 | 123.0103 | 122.9782 | 60.0357 | 60.022
171.8281 | 123.1659 | -59.9762 | 63.002 | -0.045166 | -0.0018649 | 0.064495 | 0.064241 | 0.0023925 | -0.0027002 | -0.0018307 | 0.0027771 | -0.0009698 | 0.066204 | 0.062643 | -0.00014517 | 0.00096564 | 0.0039049 | 0.041199 | 62.8693 | -60.0449 | 63.0203 | -59.8434 | -60.173 | 0.073242 | 0.032043 | 62.8738 | -59.9808 | 63.0112 | -60.0174 | -60.1273 | -60.022 | -0.068665 | -0.13275 | 0.018311 | 0.13275 | 60.0494 | -0.19684 | 60.1181 | -0.12817 | -0.004578 | -0.12817 | 0.009155 | -0.041199 | -0.045777 | -0.15106 | -0.041199 | -0.14648 | 0.20142 | 123.0652 | -0.036621 | 122.9919 | 122.9141 | 122.8546 | 122.8455 | 122.85 | -123.0469 | -122.9828 | 122.9965 | 122.9874 | 60.0174 | 60.0082
172.8906 | 123.2254 | -59.9625 | 62.9883 | -0.060425 | 0.0013393 | 0.064068 | 0.066163 | 0.0015381 | -0.00099116 | -0.00033547 | -0.073517 | 0.0015936 | 0.064281 | 0.068624 | -0.0042042 | 0.003529 | 0.0039049 | 0.027466 | 62.8738 | -60.0906 | 63.002 | -59.848 | -60.2051 | 0.022888 | 0.027466 | 62.8784 | -59.9899 | 62.9517 | -59.9442 | -60.141 | -59.9899 | -0.12817 | -0.11444 | 0.013733 | 0.11444 | 59.9854 | -0.24262 | 60.1135 | -0.11444 | -0.027466 | -0.10986 | -0.036621 | 0.01831 | -0.027466 | -0.17853 | 0 | -0.15106 | 0.24262 | 123.0927 | 0.045776 | 122.9416 | 122.9645 | 122.8683 | 122.8363 | 122.8409 | -123.0789 | -122.9782 | 122.9645 | 122.9141 | 59.9899 | 59.9899
173.8281 | 123.2529 | -59.9625 | 62.9105 | -0.052796 | 0.0015529 | 0.06599 | 0.066163 | 4.2692e-05 | 0.00093144 | -0.0035397 | -0.055206 | 0.0003118 | 0.064281 | 0.068624 | -0.0018542 | 0.0039562 | 0.0015551 | -0.045776 | 62.8281 | -60.0769 | 63.0295 | -59.8343 | -60.1868 | -0.027466 | -0.032043 | 62.8235 | -60.022 | 63.089 | -59.9716 | -60.0952 | -59.9075 | -0.11444 | -0.082397 | 0.11902 | 0.12817 | 59.935 | -0.22431 | 60.0494 | -0.10986 | -0.05951 | -0.086975 | 0.17853 | -0.009156 | 0.054931 | -0.13275 | 0.11444 | -0.073242 | 0.24261 | 123.1064 | 0.050354 | 123.111 | 122.905 | 122.8455 | 122.7905 | 122.7859 | -122.9874 | -122.9324 | 122.9919 | 123.0515 | 59.9167 | 59.9304
174.8906 | 123.1384 | -59.9854 | 63.002 | 0.031128 | -0.00079686 | 0.063 | 0.066591 | -0.0018799 | 0.00050424 | -0.00097627 | -0.049103 | 0.0007392 | 0.065136 | 0.070547 | -0.0035632 | 0.003529 | -0.00036747 | 0.013733 | 62.9059 | -60.0082 | 62.9242 | -59.9167 | -60.2097 | 0 | -0.018311 | 62.8922 | -59.9991 | 62.9974 | -60.0449 | -60.1456 | -60.0174 | -0.022888 | -0.09613 | -0.07782 | 0.068665 | 59.9854 | -0.2243 | 60.0082 | -0.20142 | -0.013732 | -0.10986 | -0.004577 | -0.059509 | -0.032043 | -0.16022 | -0.018311 | -0.14648 | 0.091553 | 122.9324 | -0.045777 | 122.9965 | 122.9141 | 122.8912 | 122.8912 | 122.8775 | -123.0103 | -123.0011 | 122.9095 | 122.9828 | 59.9991 | 59.967
175.8281 | 123.2529 | -59.9396 | 62.9242 | -0.068054 | -0.0020785 | 0.066845 | 0.066377 | 0.0028199 | 7.6842e-05 | -0.00076267 | -0.018585 | -0.002038 | 0.065777 | 0.066061 | -0.0022816 | 0.003529 | -0.00079467 | -0.059509 | 62.8281 | -60.0815 | 63.0295 | -59.8663 | -60.2692 | -0.054932 | -0.036621 | 62.8098 | -59.9945 | 63.0661 | -59.9854 | -60.0769 | -59.9075 | -0.14191 | -0.09613 | 0.10529 | 0.073242 | 59.8846 | -0.32959 | 60.0266 | -0.18768 | -0.054932 | -0.11444 | 0.14191 | -0.045777 | 0.032043 | -0.13733 | 0.086975 | -0.082397 | 0.21515 | 123.111 | 0.009155 | 123.0606 | 122.9095 | 122.8043 | 122.7676 | 122.7493 | -123.0057 | -122.9187 | 122.9691 | 123.0057 | 59.8801 | 59.903
176.8906 | 123.1384 | -59.9762 | 62.9837 | -0.037537 | -0.00079686 | 0.061932 | 0.065309 | 4.2692e-05 | 7.6842e-05 | -0.0028989 | -0.030792 | 0.0005256 | 0.065349 | 0.066915 | -0.0016406 | 0.0016064 | -0.00058107 | -0.004578 | 62.9013 | -60.0723 | 63.1668 | -59.7977 | -60.5576 | -0.027466 | -0.022888 | 62.8876 | -59.9899 | 63.0157 | -60.0449 | -60.1364 | -60.0082 | -0.096131 | -0.082398 | 0.1831 | 0.17853 | 59.9487 | -0.58136 | 60.0449 | -0.48523 | -0.013733 | -0.096131 | 0.032043 | -0.068665 | -0.032044 | -0.16022 | -0.018311 | -0.14649 | 0.27466 | 123.2391 | -0.054932 | 123.0057 | 122.9736 | 122.8775 | 122.8775 | 122.8638 | -123.056 | -122.9736 | 123.143 | 122.9919 | 59.9716 | 59.9533
177.8281 | 123.143 | -59.9762 | 62.9745 | -0.052796 | 0.00048494 | 0.061718 | 0.066591 | 0.00025629 | -0.00035036 | 0.0013735 | -0.082672 | 0.0007392 | 0.067272 | 0.059866 | -0.00099977 | 0.0084424 | 0.0043323 | -0.10071 | 62.8601 | -60.0906 | 62.9059 | -59.9808 | -60.3149 | -0.09613 | -0.14191 | 62.8601 | -60.0174 | 62.7777 | -59.7748 | -60.0861 | -60.0449 | -0.11444 | -0.11444 | -0.068664 | -0.004578 | 59.8801 | -0.33874 | 59.9945 | -0.2243 | -0.041199 | -0.11444 | -0.19684 | 0.20142 | -0.068665 | -0.10986 | -0.027466 | -0.068665 | 0.10986 | 122.9965 | 0.24262 | 122.7951 | 122.9507 | 122.8775 | 122.8363 | 122.8363 | -123.0652 | -122.9919 | 122.8821 | 122.7539 | 59.8755 | 59.8343
178.8906 | 123.143 | -59.967 | 63.0066 | -0.022278 | 5.7742e-05 | 0.064281 | 0.062532 | 0.0013245 | -0.0027002 | -0.0011899 | 0.024139 | 9.8198e-05 | 0.064922 | 0.05538 | -0.00099977 | 0.0033154 | -0.00058107 | 0.041199 | 62.8922 | -60.0449 | 62.9837 | -59.848 | -60.2005 | 0.073242 | 0.022888 | 62.8967 | -59.9899 | 62.9837 | -60.022 | -60.1135 | -60.0311 | -0.07782 | -0.11444 | -0.022888 | 0.11902 | 60.0403 | -0.23346 | 60.1181 | -0.15564 | -0.022888 | -0.10986 | -0.022888 | -0.054932 | -0.064087 | -0.14648 | -0.041199 | -0.1236 | 0.19684 | 123.0286 | -0.032044 | 122.9736 | 122.937 | 122.8867 | 122.8592 | 122.8638 | -123.0515 | -122.9965 | 122.9507 | 122.9507 | 60.0082 | 59.9899
179.8281 | 123.1064 | -60.022 | 62.97 | -0.052796 | 0.0021939 | 0.064709 | 0.065523 | 0.0019653 | -0.0014184 | -0.00033547 | -0.073517 | 0.0011664 | 0.06599 | 0.06777 | -0.00057257 | 0.0048108 | -0.0029309 | -0.027466 | 62.883 | -60.0906 | 62.9425 | -59.9075 | -60.2737 | -0.073242 | -0.09613 | 62.8922 | -60.0128 | 62.9745 | -60.0952 | -60.1776 | -60.0403 | -0.068664 | -0.086975 | -0.027466 | 0.11444 | 59.9487 | -0.25177 | 60.0174 | -0.18311 | 0.009156 | -0.07782 | 0.004577 | -0.073242 | -0.01831 | -0.15564 | -0.027466 | -0.1648 | 0.1831 | 123.0331 | -0.082398 | 122.9874 | 122.9736 | 122.905 | 122.905 | 122.9141 | -123.0606 | -122.9828 | 122.9645 | 122.9965 | 59.9945 | 59.9258
180.8906 | 123.2712 | -59.9304 | 62.9196 | -0.060425 | 0.0013393 | 0.063 | 0.065309 | 0.00025629 | -0.00035036 | 0.00094633 | 0.057709 | 0.0007392 | 0.067486 | 0.060293 | -0.00078617 | 0.0016064 | 0.0011279 | 0.013733 | 62.8647 | -60.0403 | 63.0524 | -59.761 | -60.141 | 0.086975 | 0.09613 | 62.8326 | -59.9579 | 63.1165 | -59.9167 | -59.9899 | -59.9075 | -0.10986 | -0.054932 | 0.13275 | 0.16937 | 60.0174 | -0.21057 | 60.1273 | -0.10071 | -0.027466 | -0.086975 | 0.19684 | 0.013733 | 0.022888 | -0.059509 | 0.050354 | -0.032043 | 0.27924 | 123.0927 | 0.041199 | 123.0743 | 122.905 | 122.7905 | 122.7951 | 122.7631 | -122.9599 | -122.8775 | 122.9828 | 123.0469 | 59.9442 | 60.0266
181.8281 | 123.1338 | -60.0128 | 62.9562 | -0.083313 | 0.0024075 | 0.064495 | 0.066163 | 0.0013245 | 0.00093144 | -0.00033547 | -0.064362 | 0.0011664 | 0.06599 | 0.066488 | -0.0033496 | 0.0031018 | 0.0026233 | -0.032043 | 62.8693 | -60.0952 | 62.9471 | -59.903 | -60.2829 | -0.054932 | -0.091553 | 62.8876 | -60.0174 | 62.9837 | -60.0632 | -60.1868 | -60.0403 | -0.082398 | -0.086975 | -0.009155 | 0.10986 | 59.9579 | -0.27008 | 60.0403 | -0.18768 | -0.004578 | -0.068665 | 0.027466 | -0.050354 | -0.027466 | -0.17395 | -0.022888 | -0.16937 | 0.19226 | 123.0423 | -0.045776 | 123.0011 | 122.9645 | 122.905 | 122.8821 | 122.9004 | -123.0515 | -122.9736 | 122.9599 | 122.9965 | 59.9808 | 59.9213
182.8906 | 123.2437 | -59.9579 | 62.9425 | -0.075684 | 0.00091214 | 0.063854 | 0.062532 | 0.00089729 | 0.00029044 | 0.0013735 | 0.033295 | 0.0009528 | 0.064922 | 0.05837 | -0.0022816 | 0.0031018 | -0.0022901 | -0.050354 | 62.8464 | -60.0403 | 62.9974 | -59.8618 | -60.1868 | 0.018311 | 0.004578 | 62.8555 | -59.9762 | 63.0524 | -59.9762 | -60.0403 | -59.9533 | -0.082397 | -0.09613 | 0.054932 | 0.096131 | 59.9762 | -0.22888 | 60.0586 | -0.14648 | -0.01831 | -0.086975 | 0.10986 | -0.01831 | 0.004578 | -0.082397 | 0.022888 | -0.064087 | 0.17853 | 123.0377 | 0 | 123.0286 | 122.8867 | 122.8317 | 122.8043 | 122.8134 | -122.9828 | -122.9187 | 122.9553 | 123.0103 | 59.9075 | 59.9625
183.8281 | 123.1522 | -59.9945 | 62.9562 | -0.11383 | 0.0019803 | 0.063 | 0.067659 | 0.0041015 | -0.002273 | 9.193e-05 | -0.06131 | 0.0015936 | 0.06834 | 0.061361 | -0.0037768 | 0.0033154 | -0.0029309 | -0.027466 | 62.8693 | -60.0952 | 62.9517 | -59.903 | -60.2509 | -0.073242 | -0.059509 | 62.8784 | -59.9899 | 62.9837 | -60.0952 | -60.2005 | -60.0449 | -0.10071 | -0.086975 | -0.004578 | 0.091553 | 59.9213 | -0.25635 | 60.022 | -0.15564 | 0.004578 | -0.07782 | 0.027466 | -0.10071 | -0.050354 | -0.20599 | -0.054932 | -0.21057 | 0.19226 | 123.0469 | -0.10529 | 122.9736 | 122.9645 | 122.8683 | 122.8638 | 122.8729 | -123.0515 | -122.9462 | 122.9462 | 122.9782 | 59.967 | 59.935
184.8906 | 123.1522 | -59.9808 | 62.9974 | -0.052796 | 0.0024075 | 0.063641 | 0.064668 | -0.0018799 | 0.00093144 | -0.0026853 | -0.0033265 | 0.0037298 | 0.066845 | 0.058798 | -0.00014517 | 0.0033154 | -0.0022901 | 0.041199 | 62.9013 | -60.0266 | 63.0112 | -59.8434 | -60.1868 | 0.064087 | 0.036621 | 62.8922 | -59.9579 | 62.9883 | -60.0128 | -60.1181 | -59.9991 | -0.045776 | -0.096131 | 0.013732 | 0.13733 | 60.0449 | -0.20599 | 60.0906 | -0.16022 | 0.022888 | -0.10529 | -0.009156 | -0.032043 | -0.01831 | -0.13733 | -0.041198 | -0.16022 | 0.1831 | 123.0377 | -0.054931 | 122.9462 | 122.9279 | 122.85 | 122.8821 | 122.8729 | -123.024 | -122.9553 | 122.9919 | 122.9691 | 60.022 | 60.0174
185.8281 | 123.1338 | -59.9854 | 62.9837 | -0.014649 | 0.0024075 | 0.065136 | 0.067018 | 0.0017517 | -0.0027002 | 0.00051913 | -0.058258 | 0.0018072 | 0.067058 | 0.062856 | -0.002068 | 0.0031018 | -0.00058107 | -0.022888 | 62.8784 | -60.0815 | 62.9517 | -59.8984 | -60.2737 | -0.059509 | -0.059509 | 62.8784 | -59.9899 | 62.97 | -60.0815 | -60.2005 | -60.0311 | -0.09613 | -0.10529 | -0.032044 | 0.086976 | 59.9258 | -0.28839 | 60.022 | -0.19226 | -0.004577 | -0.10529 | -0.013733 | -0.09613 | -0.045776 | -0.21515 | -0.041199 | -0.21057 | 0.18311 | 123.0331 | -0.091553 | 122.9599 | 122.9599 | 122.8683 | 122.8638 | 122.8638 | -123.0652 | -122.9736 | 122.937 | 122.9553 | 59.9625 | 59.9258
186.8906 | 123.23 | -59.9579 | 62.9745 | -0.060425 | 0.0011257 | 0.064709 | 0.065523 | -0.00059811 | -0.0020594 | -0.00033547 | 0.036346 | -0.0011834 | 0.065349 | 0.060507 | -0.001427 | 0.0026746 | 0.0026233 | 0.068665 | 62.8738 | -60.0174 | 63.0661 | -59.7656 | -60.1227 | 0.1236 | 0.11444 | 62.8418 | -59.9716 | 63.0844 | -59.9442 | -60.0449 | -59.9304 | -0.059509 | -0.10071 | 0.091553 | 0.19226 | 60.0815 | -0.16479 | 60.141 | -0.10529 | -0.013733 | -0.13275 | 0.10986 | 0.013733 | 0.027466 | -0.086975 | 0.041199 | -0.073242 | 0.25177 | 123.0835 | 0.027466 | 123.056 | 122.8912 | 122.8134 | 122.8317 | 122.7997 | -122.9919 | -122.9462 | 123.024 | 123.0423 | 60.0266 | 60.0723
187.8281 | 123.1796 | -59.9579 | 62.9562 | -0.022278 | 0.0024075 | 0.063213 | 0.065095 | 0.0026063 | -0.0012048 | 0.0015871 | -0.073517 | 0.00138 | 0.067058 | 0.06777 | -0.0029224 | 0.0043836 | 0.0026233 | -0.009155 | 62.8738 | -60.0815 | 62.9974 | -59.8526 | -60.2325 | 0 | 0 | 62.8876 | -59.9808 | 63.0203 | -60.0311 | -60.1456 | -59.9945 | -0.1236 | -0.082398 | 0.041199 | 0.10529 | 59.9579 | -0.27466 | 60.0815 | -0.15106 | -0.022888 | -0.068665 | 0.064087 | -0.073242 | -0.036621 | -0.18768 | -0.013733 | -0.1648 | 0.22888 | 123.0789 | -0.050354 | 123.0011 | 122.9553 | 122.8683 | 122.8317 | 122.8455 | -123.0377 | -122.937 | 122.9553 | 122.9782 | 59.9487 | 59.9579
188.8906 | 123.2529 | -59.9579 | 62.9288 | -0.029907 | 0.00048494 | 0.063 | 0.065523 | -0.00081171 | -0.00077756 | -0.0039671 | 0.030243 | 0.0005256 | 0.064709 | 0.064993 | -0.00014517 | 0.0033154 | -0.00015387 | -0.073242 | 62.8647 | -60.0815 | 62.9791 | -59.8526 | -60.2142 | -0.013733 | -0.036621 | 62.8372 | -59.9854 | 63.0295 | -59.9991 | -60.1547 | -59.8251 | -0.1236 | -0.064087 | 0.050354 | 0.10529 | 59.9442 | -0.25635 | 60.0677 | -0.13275 | -0.027466 | -0.091553 | 0.10071 | -0.041198 | 0.13275 | -0.19684 | 0.16022 | -0.16937 | 0.22888 | 123.0606 | -0.013732 | 123.0148 | 122.9462 | 122.8226 | 122.8226 | 122.7951 | -123.0103 | -122.9141 | 122.937 | 122.9874 | 59.8846 | 59.9213
189.8281 | 123.1705 | -59.9808 | 63.002 | 0.015869 | 0.0034757 | 0.062572 | 0.064882 | 0.00046989 | -0.0016322 | -0.00076267 | -0.030792 | 0.0005256 | 0.066418 | 0.065206 | -0.0024952 | 0.0033154 | 0.0028369 | 0.009155 | 62.9059 | -60.0815 | 62.9791 | -59.8801 | -60.2051 | 0.018311 | 0.022888 | 62.9059 | -59.9579 | 63.0157 | -60.0037 | -60.1181 | -59.9899 | -0.10071 | -0.09613 | -0.022888 | 0.10071 | 59.9991 | -0.2243 | 60.0998 | -0.1236 | 0.022888 | -0.09613 | 0.013733 | -0.022888 | -0.009155 | -0.13733 | -0.032043 | -0.16022 | 0.20142 | 123.0606 | -0.045776 | 122.9736 | 122.9874 | 122.8638 | 122.8867 | 122.8867 | -123.0835 | -122.9599 | 122.9599 | 122.9965 | 59.9899 | 60.0037
190.8281 | 123.111 | -59.9899 | 62.9974 | -0.022278 | 0.0019803 | 0.063427 | 0.064454 | 4.2692e-05 | -0.00099116 | -0.0018307 | -0.0063781 | 0.0018072 | 0.06834 | 0.066488 | -0.00078617 | 0.0022472 | 0.00027333 | -0.009155 | 62.9196 | -60.054 | 62.9517 | -59.8938 | -60.228 | 0.032043 | 0.036621 | 62.9105 | -59.9762 | 63.0066 | -60.0998 | -60.1227 | -59.9716 | -0.064087 | -0.07782 | -0.045777 | 0.09613 | 60.022 | -0.23804 | 60.0861 | -0.17395 | 0.013733 | -0.086976 | 0.009155 | -0.10986 | 0.01831 | -0.13275 | 0.004577 | -0.14648 | 0.16022 | 123.0057 | -0.1236 | 122.9828 | 122.9736 | 122.8867 | 122.9095 | 122.9004 | -123.0515 | -122.9736 | 122.9416 | 122.9965 | 59.9808 | 60.0265
191.8281 | 123.1476 | -59.9991 | 62.9929 | -0.022278 | 5.7742e-05 | 0.063 | 0.066591 | -0.00017091 | -0.00013676 | -0.0022581 | -0.0094299 | 0.0005256 | 0.066631 | 0.058157 | -0.0044178 | 0.0020336 | -0.0033581 | -0.09613 | 62.9013 | -60.0723 | 62.9288 | -59.9396 | -60.2234 | 0.041199 | -0.009155 | 62.9059 | -59.9854 | 62.9929 | -60.0403 | -60.141 | -59.9808 | -0.073243 | -0.091553 | -0.064087 | 0.059509 | 60.0403 | -0.2243 | 60.1135 | -0.15106 | 0.013732 | -0.086975 | 0 | -0.041199 | 0.01831 | -0.14191 | 0.004578 | -0.15564 | 0.13275 | 123.0011 | -0.054931 | 122.9782 | 122.9736 | 122.8912 | 122.9004 | 122.905 | -123.0652 | -122.9782 | 122.9279 | 122.9919 | 59.903 | 59.9899
192.8906 | 123.2574 | -59.9625 | 62.9471 | -0.11383 | 0.0013393 | 0.064281 | 0.064027 | 0.00046989 | -0.0014184 | -0.0033261 | 0.045502 | 0.0009528 | 0.066631 | 0.063711 | -0.00078617 | 0.0022472 | 0.00027333 | -0.013733 | 62.851 | -60.0449 | 63.0203 | -59.8343 | -60.1639 | 0.032043 | 0.013733 | 62.8418 | -59.9854 | 63.0569 | -59.9625 | -60.054 | -59.9304 | -0.082398 | -0.096131 | 0.073242 | 0.12817 | 59.9945 | -0.20142 | 60.0769 | -0.11902 | -0.022889 | -0.10529 | 0.10986 | 0 | 0.032043 | -0.091553 | 0.054932 | -0.068664 | 0.21057 | 123.0652 | 0.022889 | 123.0423 | 122.8958 | 122.8271 | 122.8134 | 122.8043 | -122.9919 | -122.9324 | 122.9828 | 123.0194 | 59.9487 | 59.9762
193.8281 | 123.1979 | -59.935 | 63.0203 | -0.029907 | 0.0017667 | 0.061504 | 0.066591 | 0.0032471 | -0.0033412 | -0.0024717 | -0.0033265 | 0.00138 | 0.064922 | 0.065634 | -0.0035632 | 0.0031018 | -0.0042127 | 0 | 62.9288 | -60.0861 | 62.9791 | -59.8846 | -60.228 | 0.045776 | 0 | 62.9059 | -59.9579 | 63.002 | -60.0403 | -60.0769 | -59.9121 | -0.15106 | -0.091553 | -0.041199 | 0.050354 | 59.9808 | -0.29297 | 60.1318 | -0.14191 | -0.022888 | -0.11444 | -0.018311 | -0.10529 | 0.022889 | -0.14191 | 0.045777 | -0.11902 | 0.20142 | 123.0652 | -0.082397 | 122.9599 | 123.0148 | 122.8638 | 122.8638 | 122.8409 | -123.1064 | -122.9782 | 122.9141 | 122.937 | 59.935 | 59.935
194.8906 | 123.2162 | -59.9808 | 62.9196 | -0.11383 | 0.0024075 | 0.065777 | 0.064454 | 0.0023925 | 0.00050424 | 0.0015871 | -0.024689 | -0.0007562 | 0.065349 | 0.062643 | -0.0022816 | 0.0033154 | 0.0017687 | -0.022888 | 62.8418 | -60.0586 | 63.0341 | -59.8114 | -60.1822 | -0.013733 | 0.018311 | 62.8143 | -59.9762 | 63.0524 | -59.9991 | -60.0998 | -59.9396 | -0.07782 | -0.07782 | 0.11444 | 0.16937 | 59.967 | -0.20142 | 60.0449 | -0.1236 | 0.004578 | -0.10529 | 0.13275 | -0.01831 | 0.041199 | -0.11902 | 0.036621 | -0.1236 | 0.24719 | 123.0927 | -0.022888 | 123.0286 | 122.9004 | 122.7905 | 122.8226 | 122.7951 | -122.9782 | -122.8958 | 123.0148 | 123.0331 | 59.9579 | 59.9991
195.8281 | 123.1796 | -59.9579 | 63.0112 | -0.052796 | 0.00091214 | 0.060863 | 0.066377 | 0.0030335 | -0.00077756 | 0.00030553 | -0.033844 | 0.0026618 | 0.06599 | 0.066488 | -0.0037768 | 0.0043836 | -0.0033581 | 0.018311 | 62.9196 | -60.0677 | 62.97 | -59.903 | -60.2325 | 0.032043 | 0.009155 | 62.9059 | -60.0037 | 62.9974 | -60.0357 | -60.1227 | -59.9808 | -0.10986 | -0.091552 | -0.041198 | 0.054932 | 59.9899 | -0.27466 | 60.0998 | -0.16479 | -0.045776 | -0.10529 | -0.013732 | -0.07782 | -0.022888 | -0.16479 | 0.022888 | -0.11902 | 0.16479 | 123.0377 | -0.032044 | 123.0011 | 122.9874 | 122.9095 | 122.8775 | 122.8638 | -123.0789 | -123.0148 | 122.9279 | 122.9553 | 59.9762 | 59.967
196.8906 | 123.2391 | -59.967 | 62.9471 | -0.12146 | 0.00091214 | 0.063854 | 0.065736 | 0.0043151 | 0.00093144 | -0.0026853 | 0.021088 | 0.0041572 | 0.067913 | 0.06072 | -0.0027088 | 0.0033154 | 0.00027333 | -0.054932 | 62.8418 | -60.0586 | 62.97 | -59.8572 | -60.2142 | -0.013733 | -0.045776 | 62.8235 | -59.9854 | 63.0249 | -60.0128 | -60.0952 | -59.967 | -0.091553 | -0.10529 | 0.022888 | 0.10986 | 59.9533 | -0.24719 | 60.0449 | -0.15564 | -0.018311 | -0.1236 | 0.077819 | -0.045776 | 0 | -0.12817 | 0.018311 | -0.10986 | 0.20142 | 123.0286 | -0.027465 | 123.0103 | 122.9004 | 122.8088 | 122.8088 | 122.7905 | -123.0057 | -122.9324 | 122.937 | 122.9919 | 59.9121 | 59.9213
197.8281 | 123.143 | -59.9762 | 63.0157 | -0.022278 | -0.0012241 | 0.061504 | 0.066804 | -0.0050843 | -0.002273 | -0.00076267 | -0.046051 | 0.003089 | 0.067272 | 0.061575 | -0.0033496 | 0.0031018 | -0.0033581 | -0.013733 | 62.9242 | -60.0815 | 62.796 | -60.0082 | -60.2005 | 0.004578 | -0.018311 | 62.8784 | -59.9762 | 62.9837 | -60.0632 | -60.1181 | -60.0082 | -0.10529 | -0.091553 | -0.21973 | -0.032044 | 59.9808 | -0.2243 | 60.0861 | -0.11902 | 0 | -0.13733 | -0.032043 | -0.086975 | -0.032044 | -0.14191 | -0.032044 | -0.14191 | 0.073242 | 122.8775 | -0.086975 | 122.9599 | 123.0057 | 122.8546 | 122.9004 | 122.8546 | -123.0972 | -122.9919 | 122.7722 | 122.9599 | 59.9625 | 59.9579
198.8906 | 123.2712 | -59.9625 | 62.9562 | -0.045166 | 5.7742e-05 | 0.062786 | 0.065309 | -0.0016663 | -0.00077756 | -0.00076267 | 0.030243 | 0.0005256 | 0.064922 | 0.057516 | -0.0037768 | 0.0013928 | -0.00058107 | 0.009155 | 62.8601 | -60.0632 | 63.0707 | -59.7977 | -60.1364 | 0.086975 | 0.10529 | 62.8555 | -59.9579 | 63.0981 | -59.8984 | -59.9991 | -59.8984 | -0.10071 | -0.096131 | 0.11444 | 0.16479 | 60.0494 | -0.17395 | 60.1501 | -0.073243 | 0.004577 | -0.10071 | 0.14191 | 0.064087 | 0.064087 | -0.036621 | 0.05951 | -0.041198 | 0.2655 | 123.1338 | 0.05951 | 123.056 | 122.9233 | 122.8134 | 122.8226 | 122.818 | -123.0194 | -122.9141 | 123.0331 | 123.0606 | 59.9716 | 60.0677
199.8281 | 123.1796 | -59.967 | 63.0112 | -0.052796 | -0.00079686 | 0.063213 | 0.067445 | 0.0026063 | -0.0014184 | -0.00012167 | -0.039948 | 0.0037298 | 0.062572 | 0.062002 | -0.004845 | 0.0041698 | -0.0016493 | 0.20599 | 62.9471 | -60.0357 | 62.9654 | -59.9258 | -60.2417 | 0.036621 | -0.009155 | 62.9059 | -60.0082 | 62.9974 | -60.0311 | -60.1547 | -60.0037 | -0.068665 | -0.064086 | -0.045776 | 0.041199 | 60.0037 | -0.27466 | 60.0723 | -0.20599 | -0.041199 | -0.10529 | -0.013732 | -0.064087 | -0.036621 | -0.18768 | 0.004578 | -0.14648 | 0.10986 | 123.0011 | -0.022888 | 123.0057 | 122.9828 | 122.9141 | 122.9141 | 122.8729 | -123.0469 | -123.0194 | 122.9324 | 122.9645 | 60.173 | 59.9579
200.8906 | 123.2437 | -59.9442 | 62.9425 | -0.098572 | 0.00069854 | 0.064709 | 0.063814 | -0.0014527 | -0.00099116 | -0.00012167 | 0.027191 | 0.0020208 | 0.066631 | 0.061361 | -0.0044178 | 0.0028882 | -0.0016493 | -0.032043 | 62.8464 | -60.0723 | 63.0112 | -59.8389 | -60.173 | 0.022888 | 0.032043 | 62.8143 | -59.9762 | 63.0661 | -59.9579 | -60.0494 | -59.9213 | -0.12817 | -0.09613 | 0.068664 | 0.10529 | 59.967 | -0.22888 | 60.0952 | -0.10071 | -0.032043 | -0.12817 | 0.1236 | -0.013733 | 0.022888 | -0.10529 | 0.054931 | -0.073242 | 0.23346 | 123.0835 | 0.01831 | 123.0423 | 122.9187 | 122.7905 | 122.7905 | 122.7585 | -123.0148 | -122.9187 | 122.9553 | 123.0103 | 59.9121 | 59.9762
201.8281 | 123.1476 | -59.967 | 63.0249 | -0.022278 | 0.0019803 | 0.061504 | 0.066377 | -0.00081171 | 0.00093144 | 9.193e-05 | -0.018585 | 0.0005256 | 0.067699 | 0.067129 | -0.002068 | 0.0011792 | 0.0024097 | -0.013733 | 62.9013 | -60.0723 | 62.9608 | -59.8984 | -60.2234 | 0.032043 | 0.013733 | 62.9013 | -59.9762 | 62.9745 | -60.0357 | -60.141 | -60.022 | -0.10529 | -0.1236 | -0.064087 | 0.068665 | 59.9991 | -0.25635 | 60.1044 | -0.15106 | -0.009155 | -0.1236 | -0.050354 | -0.068665 | -0.054932 | -0.17395 | -0.045777 | -0.16479 | 0.17395 | 123.0331 | -0.05951 | 122.9507 | 122.9736 | 122.8775 | 122.8683 | 122.8683 | -123.0972 | -123.0011 | 122.9279 | 122.9416 | 59.9533 | 59.9808
202.8906 | 123.2117 | -59.967 | 62.9425 | -0.075684 | -0.00058326 | 0.062572 | 0.062959 | -0.0018799 | 7.6842e-05 | -0.0018307 | -0.0033265 | -0.0005426 | 0.062145 | 0.057943 | -0.0035632 | 0.0011792 | -0.0044263 | -0.045776 | 62.8464 | -60.0677 | 62.9883 | -59.848 | -60.228 | -0.032043 | -0.045776 | 62.8189 | -59.9899 | 63.0203 | -60.0037 | -60.0861 | -59.967 | -0.10071 | -0.09613 | 0.045776 | 0.11902 | 59.935 | -0.26093 | 60.0357 | -0.16022 | -0.022888 | -0.1236 | 0.07782 | -0.036621 | 0 | -0.11902 | 0.022888 | -0.096131 | 0.21973 | 123.056 | -0.013733 | 123.0103 | 122.9141 | 122.8088 | 122.8134 | 122.7859 | -123.0103 | -122.9324 | 122.9553 | 122.9874 | 59.9213 | 59.9213
203.8281 | 123.2574 | -59.9304 | 62.9562 | -0.060425 | 0.0053983 | 0.064068 | 0.064668 | 0.0043151 | 0.00071784 | -0.00012167 | -0.0063781 | -0.0005426 | 0.061291 | 0.06307 | -0.0016406 | 0.00182 | -0.00079467 | 0.32501 | 62.9196 | -59.9808 | 63.0707 | -59.7336 | -60.141 | 0.10529 | 0.12817 | 62.8647 | -59.967 | 63.0936 | -59.9258 | -60.0266 | -59.9075 | -0.050354 | -0.036621 | 0.11444 | 0.19684 | 60.0357 | -0.21057 | 60.0861 | -0.16022 | -0.036621 | -0.091553 | 0.13733 | 0.004578 | 0.022888 | -0.09613 | 0.059509 | -0.059509 | 0.24719 | 123.0515 | 0.041199 | 123.0606 | 122.9004 | 122.8317 | 122.85 | 122.7951 | -122.937 | -122.9233 | 123.0011 | 123.024 | 60.2554 | 60.0586
204.8906 | 123.23 | -59.9487 | 62.9425 | -0.15198 | 0.0011257 | 0.063213 | 0.063386 | -0.00038451 | -0.0024866 | 0.0015871 | -0.030792 | 0.0007392 | 0.066418 | 0.064138 | -0.0035632 | 0.0048108 | -0.0012219 | -0.009155 | 62.8235 | -60.0769 | 63.0249 | -59.816 | -60.2005 | -0.032043 | 0.004578 | 62.8372 | -59.9991 | 62.915 | -59.7198 | -59.935 | -59.903 | -0.12817 | -0.11902 | 0.082397 | 0.13275 | 59.9167 | -0.25177 | 60.0449 | -0.1236 | -0.050354 | -0.10529 | -0.027466 | 0.22888 | 0.045776 | 0.013732 | 0.09613 | 0.064086 | 0.26093 | 123.1018 | 0.27923 | 122.9141 | 122.9004 | 122.8363 | 122.7722 | 122.7859 | -123.0194 | -122.9416 | 122.9736 | 122.8638 | 59.9396 | 59.9533
205.8281 | 123.1567 | -59.9762 | 62.97 | -0.075684 | 0.0015529 | 0.063 | 0.065523 | -0.00081171 | -0.00035036 | -0.0011899 | -0.012482 | 0.0011664 | 0.065563 | 0.060507 | -0.0024952 | 0.0043836 | -0.0016493 | 0.054932 | 62.9059 | -60.0494 | 63.0386 | -59.816 | -60.1501 | 0.086975 | 0.073242 | 62.8784 | -59.9762 | 63.0203 | -60.0082 | -60.1044 | -59.9808 | -0.073242 | -0.064087 | 0.068664 | 0.16022 | 60.0632 | -0.17395 | 60.1364 | -0.10071 | 0 | -0.091553 | 0.050354 | -0.032044 | -0.004578 | -0.12817 | -0.004578 | -0.12817 | 0.23346 | 123.0881 | -0.032044 | 122.9965 | 122.9553 | 122.8546 | 122.8821 | 122.8546 | -123.0194 | -122.9462 | 123.0148 | 122.9965 | 60.0311 | 60.0494
206.8906 | 123.2346 | -59.9762 | 62.9105 | -0.045166 | 0.00048494 | 0.064068 | 0.065095 | 4.2692e-05 | -0.00099116 | 0.00073273 | -0.058258 | -0.0009698 | 0.065349 | 0.060293 | -0.0044178 | 0.0033154 | -0.0025037 | -0.07782 | 62.8372 | -60.0998 | 62.9654 | -59.8892 | -60.2417 | -0.07782 | -0.050354 | 62.8143 | -59.9991 | 63.0524 | -60.0311 | -60.1227 | -59.9167 | -0.1236 | -0.073242 | 0.054932 | 0.086975 | 59.8984 | -0.2655 | 60.022 | -0.14191 | -0.022888 | -0.09613 | 0.14191 | -0.054932 | 0.059509 | -0.14648 | 0.082397 | -0.1236 | 0.21057 | 123.0652 | -0.032044 | 123.0515 | 122.937 | 122.8134 | 122.8134 | 122.7905 | -123.0103 | -122.9095 | 122.9416 | 123.0286 | 59.8984 | 59.9258
207.8281 | 123.2712 | -59.9442 | 62.9562 | 0.14557 | 0.0017667 | 0.067059 | 0.062959 | -0.0010253 | 7.6842e-05 | -0.0024717 | 0.021088 | 0.0005256 | 0.066204 | 0.061788 | -0.0050586 | 0.0026746 | -0.0016493 | -0.17395 | 62.851 | -60.0403 | 63.0569 | -59.7931 | -60.0586 | 0.11902 | 0.10986 | 62.8555 | -59.9442 | 63.0844 | -59.9167 | -60.0311 | -59.9075 | -0.09613 | -0.10529 | 0.10071 | 0.15106 | 60.0632 | -0.11444 | 60.1593 | -0.018311 | 0 | -0.10071 | 0.12817 | 0.027466 | 0.036621 | -0.086975 | 0.036621 | -0.086975 | 0.24719 | 123.0972 | 0.027466 | 123.0286 | 122.8912 | 122.7997 | 122.7951 | 122.7997 | -122.9965 | -122.9004 | 123.0011 | 123.0286 | 59.7702 | 60.054
208.8906 | 123.2071 | -59.9487 | 62.9425 | -0.098572 | 0.0032619 | 0.063854 | 0.0636 | 0.00025629 | -0.00035036 | -0.00076267 | -0.018585 | 0.00138 | 0.065777 | 0.061788 | -0.0035632 | 0.0020336 | 0.0017687 | -0.054932 | 62.8326 | -60.0449 | 62.9929 | -59.848 | -60.2188 | -0.022888 | -0.050354 | 62.8235 | -59.9899 | 63.0341 | -60.0082 | -60.0998 | -59.9854 | -0.096131 | -0.10986 | 0.050354 | 0.10071 | 59.9258 | -0.27008 | 60.022 | -0.17395 | -0.041199 | -0.11902 | 0.091553 | -0.05951 | -0.036622 | -0.15106 | 0.004577 | -0.10986 | 0.19684 | 123.0377 | -0.018311 | 123.024 | 122.8775 | 122.8134 | 122.7814 | 122.7722 | -122.9874 | -122.9324 | 122.9416 | 122.9828 | 59.8938 | 59.8984
209.8281 | 123.262 | -59.9258 | 62.9517 | -0.052796 | 0.00048494 | 0.061291 | 0.065736 | -0.0057251 | -0.00035036 | -0.00033547 | 0.0058289 | 0.0007392 | 0.064922 | 0.062216 | -0.0022816 | 0.0026746 | -0.0020765 | 0.050354 | 62.8372 | -60.0266 | 63.0707 | -59.729 | -60.1044 | 0.12817 | 0.17395 | 62.8418 | -59.9442 | 63.1027 | -59.903 | -60.0128 | -59.8892 | -0.10071 | -0.11444 | 0.11902 | 0.19684 | 60.054 | -0.17853 | 60.1547 | -0.07782 | -0.018311 | -0.10986 | 0.15106 | 0.022888 | 0.036621 | -0.086975 | 0.054932 | -0.068664 | 0.29755 | 123.0972 | 0.041199 | 123.0469 | 122.8638 | 122.7859 | 122.7631 | 122.7676 | -122.9782 | -122.8958 | 122.9965 | 123.0286 | 59.9762 | 60.0998
210.8906 | 123.1613 | -59.9579 | 62.9745 | -0.060425 | 0.0024075 | 0.064281 | 0.065523 | 0.00025629 | -0.00013676 | -0.00033547 | -0.091827 | 0.0015936 | 0.064922 | 0.059011 | -0.0035632 | 0.0037426 | -0.0029309 | 0.032043 | 62.8738 | -60.0861 | 62.9929 | -59.848 | -60.2097 | 0.032043 | 0.036621 | 62.8784 | -59.9808 | 63.0432 | -59.9945 | -60.1135 | -59.9808 | -0.12817 | -0.10071 | 0.018311 | 0.10986 | 59.9899 | -0.25177 | 60.1181 | -0.1236 | -0.022888 | -0.09613 | 0.068665 | -0.036621 | -0.022888 | -0.15564 | 0 | -0.13275 | 0.23804 | 123.0789 | -0.013733 | 123.024 | 122.9599 | 122.8592 | 122.8317 | 122.8363 | -123.0606 | -122.9553 | 122.9507 | 123.0011 | 59.9899 | 59.9945
211.8438 | 123.1934 | -59.967 | 62.9791 | -0.083313 | 0.0013393 | 0.062145 | 0.06595 | -0.0016663 | -0.0014184 | -0.0011899 | -0.076569 | 0.0037298 | 0.065136 | 0.062643 | -0.0012134 | 0.0011792 | -0.0050671 | 0.018311 | 62.915 | -60.0494 | 62.9929 | -59.8709 | -60.1913 | 0.041199 | 0.032043 | 62.8876 | -59.9945 | 63.0341 | -59.9991 | -60.1273 | -59.9808 | -0.082397 | -0.064087 | 0.013733 | 0.09613 | 60.0082 | -0.2243 | 60.0906 | -0.14191 | -0.027466 | -0.091553 | 0.054932 | -0.032043 | -0.013733 | -0.16022 | 0.013733 | -0.13275 | 0.17853 | 123.0423 | -0.004577 | 123.0286 | 122.9645 | 122.8821 | 122.8821 | 122.8546 | -123.0286 | -122.9736 | 122.9599 | 123.0011 | 59.9854 | 59.9991
212.8906 | 123.23 | -59.9533 | 62.9059 | -0.075684 | 0.0011257 | 0.064709 | 0.063814 | 0.0019653 | 0.001145 | 0.00030553 | -0.046051 | 0.00138 | 0.06599 | 0.061788 | -0.0016406 | 0.0048108 | -0.0022901 | -0.022888 | 62.8052 | -60.0586 | 63.0157 | -59.7977 | -60.2142 | -0.022888 | -0.022888 | 62.8281 | -59.9808 | 62.9105 | -59.9167 | -59.8206 | -59.7885 | -0.10529 | -0.10071 | 0.10986 | 0.15564 | 59.9304 | -0.26093 | 60.0357 | -0.15564 | -0.027466 | -0.07782 | 0.004577 | 0.036621 | 0.16479 | 0.13275 | 0.19226 | 0.16022 | 0.26093 | 123.0743 | 0.064087 | 122.8912 | 122.8638 | 122.8088 | 122.7585 | 122.7814 | -122.9645 | -122.8867 | 122.9691 | 122.8638 | 59.9304 | 59.9304
213.8281 | 123.2208 | -59.9487 | 62.9562 | -0.052796 | 0.00069854 | 0.062359 | 0.064027 | -0.00017091 | 0.0019994 | 0.0015871 | -0.0033265 | -0.000329 | 0.066418 | 0.058157 | -0.0029224 | 0.0026746 | -0.0022901 | -0.036621 | 62.8418 | -60.0357 | 63.1027 | -59.8846 | -60.2554 | 0.018311 | -0.036621 | 62.8281 | -59.9991 | 63.0341 | -59.9945 | -60.0861 | -59.9442 | -0.086976 | -0.11444 | 0.14648 | 0.064086 | 59.967 | -0.3067 | 60.054 | -0.21973 | -0.050354 | -0.12817 | 0.07782 | -0.045777 | 0.004577 | -0.13733 | 0.054931 | -0.086976 | 0.15106 | 123.1384 | 0.004577 | 123.0331 | 122.8775 | 122.8271 | 122.7905 | 122.7768 | -122.9919 | -122.9553 | 123.0515 | 122.9828 | 59.9121 | 59.9121
214.8906 | 123.1384 | -60.0082 | 62.9379 | -0.045166 | -0.00036966 | 0.066204 | 0.065309 | -0.0029479 | -0.00035036 | 9.193e-05 | -0.10403 | 0.00138 | 0.065563 | 0.066915 | -0.0024952 | 0.003529 | 0.0032641 | -0.07782 | 62.8464 | -60.1089 | 62.9242 | -59.9762 | -60.3195 | -0.12817 | -0.17853 | 62.8647 | -60.0311 | 62.9654 | -60.0998 | -60.2097 | -60.0403 | -0.10071 | -0.091552 | -0.013733 | 0.032044 | 59.8801 | -0.31128 | 59.9808 | -0.21057 | -0.022888 | -0.073242 | 0.027466 | -0.091552 | -0.032043 | -0.20142 | -0.009155 | -0.17853 | 0.13275 | 123.0331 | -0.068664 | 122.9965 | 122.9553 | 122.8958 | 122.8546 | 122.8729 | -123.0469 | -122.9691 | 122.9324 | 122.9736 | 59.9304 | 59.8297
215.8281 | 123.2071 | -59.967 | 62.9196 | -0.15198 | 0.0013393 | 0.062359 | 0.064668 | 0.00089729 | -0.00035036 | 0.0015871 | 0.011932 | 0.0011664 | 0.064922 | 0.062002 | -0.0027088 | 0.0020336 | -0.0039991 | -0.064087 | 62.8143 | -60.0494 | 62.9745 | -59.8526 | -60.228 | -0.032043 | -0.07782 | 62.8372 | -59.9808 | 63.0341 | -59.9899 | -60.1044 | -59.9716 | -0.082397 | -0.10529 | 0.054931 | 0.11444 | 59.935 | -0.26093 | 60.0174 | -0.17853 | -0.013733 | -0.082398 | 0.11444 | -0.022888 | -0.004578 | -0.13733 | 0.009155 | -0.1236 | 0.19684 | 123.024 | -0.009155 | 123.0148 | 122.8638 | 122.818 | 122.7814 | 122.8043 | -122.9691 | -122.9004 | 122.9416 | 123.0011 | 59.903 | 59.8892
216.8906 | 123.1613 | -59.9808 | 62.9745 | -0.083313 | 0.00091214 | 0.062359 | 0.066804 | 0.0019653 | -0.00013676 | 0.0056461 | -0.064362 | 0.0043708 | 0.065136 | 0.063711 | -0.0024952 | 0.0039562 | -0.0050671 | 0.004578 | 62.8418 | -60.1044 | 62.883 | -59.9213 | -60.0906 | 0.004578 | 0.018311 | 62.883 | -59.9991 | 63.0203 | -60.0128 | -60.1318 | -59.9899 | -0.1236 | -0.13275 | -0.091552 | 0.059509 | 59.9854 | -0.10986 | 60.1089 | 0.013733 | -0.01831 | -0.091552 | 0.045777 | -0.032043 | -0.009155 | -0.15106 | 0.009155 | -0.13275 | 0.18311 | 122.9874 | -0.013733 | 123.0194 | 122.9462 | 122.8821 | 122.8226 | 122.8638 | -123.0789 | -122.9736 | 122.8638 | 123.0011 | 59.9854 | 59.9991
217.8281 | 123.2071 | -59.9854 | 62.9288 | -0.060425 | 0.0013393 | 0.062145 | 0.0636 | -0.00059811 | -0.00077756 | -0.0011899 | -0.0033265 | -0.0007562 | 0.065563 | 0.061148 | -0.0033496 | 0.0024608 | 0.0017687 | -0.045776 | 62.8326 | -60.054 | 62.9974 | -59.8618 | -60.2142 | -0.027466 | -0.059509 | 62.8235 | -59.9854 | 63.0341 | -59.9991 | -60.1135 | -59.9533 | -0.068664 | -0.09613 | 0.068665 | 0.1236 | 59.9579 | -0.22888 | 60.0266 | -0.16022 | 0 | -0.10529 | 0.10529 | -0.013732 | 0.032044 | -0.12817 | 0.032044 | -0.12817 | 0.19226 | 123.0515 | -0.013732 | 123.0194 | 122.8867 | 122.8088 | 122.818 | 122.8088 | -122.9828 | -122.9141 | 122.9828 | 123.0194 | 59.9396 | 59.9258
218.8906 | 123.1384 | -59.9625 | 62.9929 | -0.037537 | 0.0030483 | 0.063641 | 0.0636 | -0.0014527 | -0.0018458 | -0.00012167 | -0.015534 | 0.0022346 | 0.06599 | 0.061788 | -0.0033496 | 0.003529 | -0.0014355 | 0.041199 | 62.8647 | -60.054 | 63.0112 | -59.8343 | -60.1868 | 0.073242 | 0.041199 | 62.9105 | -59.9716 | 63.0157 | -60.0082 | -60.1318 | -60.0082 | -0.091553 | -0.12817 | 0.01831 | 0.12817 | 60.0357 | -0.22431 | 60.1273 | -0.13275 | -0.009156 | -0.082398 | 0.022888 | -0.045777 | -0.045777 | -0.16937 | -0.036621 | -0.16022 | 0.21973 | 123.0652 | -0.036621 | 122.9874 | 122.9187 | 122.8821 | 122.8271 | 122.8729 | -123.0469 | -122.9645 | 122.9736 | 122.9782 | 60.0037 | 60.0037
219.8281 | 123.23 | -59.9899 | 62.9196 | -0.1062 | 0.0026211 | 0.064709 | 0.067872 | 0.00046989 | -0.00035036 | -0.0046079 | -0.024689 | 0.0003118 | 0.06834 | 0.064993 | -0.0022816 | 0.0020336 | 0.00027333 | -0.022888 | 62.8098 | -60.0723 | 63.0341 | -59.8022 | -60.2051 | -0.004578 | 0.013733 | 62.8281 | -59.9808 | 63.0661 | -59.9716 | -60.0769 | -59.9442 | -0.082398 | -0.10986 | 0.11444 | 0.18768 | 59.9854 | -0.21515 | 60.0677 | -0.13275 | 0.009155 | -0.091553 | 0.14648 | 0.01831 | 0.045776 | -0.086975 | 0.036621 | -0.09613 | 0.27008 | 123.1064 | 0.009155 | 123.0469 | 122.8821 | 122.8088 | 122.7997 | 122.818 | -122.9919 | -122.9004 | 123.024 | 123.056 | 59.967 | 60.0037
220.8906 | 123.1155 | -60.0128 | 62.9654 | -0.090943 | 0.0017667 | 0.063854 | 0.067018 | -0.0031617 | -0.0024866 | 0.0018009 | -0.097931 | -0.0011834 | 0.066845 | 0.071615 | -0.002068 | 0.0048108 | -0.0020765 | -0.059509 | 62.8693 | -60.0861 | 62.9196 | -59.9899 | -60.3012 | -0.11444 | -0.14191 | 62.8738 | -60.0357 | 62.9517 | -60.1135 | -60.2325 | -60.0586 | -0.073243 | -0.09613 | -0.045776 | 0.022888 | 59.8984 | -0.28839 | 59.9716 | -0.21515 | -0.022889 | -0.091553 | -0.013733 | -0.10071 | -0.045777 | -0.21973 | -0.022888 | -0.19684 | 0.096131 | 123.0057 | -0.077819 | 122.9874 | 122.9553 | 122.9095 | 122.8821 | 122.8867 | -123.0515 | -123.0011 | 122.9324 | 122.9645 | 59.9533 | 59.8709
221.8281 | 123.2208 | -59.9854 | 62.9059 | -0.12909 | 0.0026211 | 0.064709 | 0.064454 | -0.0018799 | -0.00035036 | -0.0028989 | -0.042999 | 0.0005256 | 0.063854 | 0.059652 | -0.0029224 | 0.0037426 | 0.00091433 | -0.013733 | 62.8464 | -60.0449 | 63.0157 | -59.8068 | -60.1822 | -0.013733 | -0.013733 | 62.8235 | -59.9762 | 63.0707 | -59.9579 | -60.0769 | -59.9304 | -0.059509 | -0.059509 | 0.10986 | 0.17853 | 59.9716 | -0.19684 | 60.0311 | -0.13733 | 0.009156 | -0.082398 | 0.16479 | 0.027466 | 0.054932 | -0.091552 | 0.045776 | -0.10071 | 0.23804 | 123.0606 | 0.01831 | 123.0469 | 122.8912 | 122.7997 | 122.8317 | 122.8088 | -122.9507 | -122.8821 | 123.0011 | 123.056 | 59.9716 | 59.9716
222.8906 | 123.1522 | -59.9854 | 62.9425 | -0.052796 | 0.0028347 | 0.064922 | 0.065309 | 0.0049561 | 7.6842e-05 | -0.0016171 | -0.064362 | 0.0015936 | 0.066631 | 0.063497 | -0.001427 | 0.0020336 | 0.00048713 | -0.018311 | 62.8693 | -60.0861 | 62.9791 | -59.8663 | -60.2554 | -0.022888 | -0.041199 | 62.8647 | -59.9991 | 62.9791 | -60.0632 | -60.1685 | -60.0082 | -0.10071 | -0.073242 | 0.036621 | 0.11902 | 59.9625 | -0.27008 | 60.0632 | -0.16937 | -0.013732 | -0.07782 | 0.036621 | -0.077819 | -0.022888 | -0.1831 | -0.009156 | -0.16937 | 0.21973 | 123.0652 | -0.064087 | 122.9782 | 122.9553 | 122.8638 | 122.8546 | 122.85 | -123.0286 | -122.9416 | 122.9645 | 122.9645 | 59.967 | 59.9442
223.8281 | 123.2529 | -59.9579 | 62.9059 | -0.12909 | 0.0017667 | 0.06535 | 0.0636 | 0.00025629 | -0.00035036 | -0.0028989 | -0.021637 | 0.0020208 | 0.063 | 0.068838 | -0.0042042 | 0.0026746 | 0.0030505 | -0.045776 | 62.8235 | -60.0815 | 63.0112 | -59.8206 | -60.2005 | -0.018311 | -0.004578 | 62.8281 | -60.0082 | 63.0798 | -59.967 | -60.0677 | -59.903 | -0.1236 | -0.082398 | 0.10529 | 0.13733 | 59.9396 | -0.24261 | 60.0632 | -0.11902 | -0.050354 | -0.07782 | 0.17395 | -0.009155 | 0.054932 | -0.10986 | 0.10529 | -0.059509 | 0.26093 | 123.0927 | 0.041199 | 123.0881 | 122.905 | 122.8363 | 122.7814 | 122.7859 | -122.9874 | -122.9141 | 122.9691 | 123.0377 | 59.9121 | 59.9533
224.8281 | 123.111 | -60.0037 | 62.9608 | -0.083313 | 0.0013393 | 0.065136 | 0.065309 | -0.00017091 | -0.0018458 | -0.0022581 | -0.073517 | 0.0028754 | 0.064922 | 0.062002 | -0.0022816 | 0.003529 | 0.0019823 | -0.032043 | 62.8647 | -60.0769 | 62.9517 | -59.9258 | -60.2737 | -0.050354 | -0.09613 | 62.8738 | -60.022 | 62.97 | -60.0861 | -60.1959 | -59.9991 | -0.073242 | -0.09613 | -0.009155 | 0.07782 | 59.9533 | -0.27008 | 60.0266 | -0.19684 | -0.018311 | -0.086975 | 0.009156 | -0.082398 | 0.004578 | -0.19226 | 0.022889 | -0.17395 | 0.15106 | 123.0286 | -0.064087 | 122.9919 | 122.9416 | 122.8958 | 122.8683 | 122.8775 | -123.0377 | -122.9828 | 122.9553 | 122.9736 | 59.9716 | 59.9075
225.8906 | 123.2162 | -59.9396 | 62.9837 | -0.060425 | 0.0013393 | 0.064495 | 0.064454 | -0.00081171 | -0.0016322 | -0.0028989 | 0.0027771 | -0.0009698 | 0.066418 | 0.062216 | -0.0033496 | 0.0026746 | -0.00058107 | 0.027466 | 62.8555 | -60.0082 | 63.0661 | -59.7839 | -60.1227 | 0.10529 | 0.10986 | 62.8418 | -59.967 | 63.0798 | -59.9258 | -60.0403 | -59.9167 | -0.068665 | -0.12817 | 0.082397 | 0.15564 | 60.0449 | -0.18311 | 60.1135 | -0.11444 | -0.027466 | -0.14191 | 0.09613 | 0.013733 | 0.022888 | -0.10071 | 0.050354 | -0.073242 | 0.2243 | 123.0743 | 0.041199 | 123.0469 | 122.8638 | 122.8088 | 122.7951 | 122.7814 | -122.9919 | -122.9507 | 123.0057 | 123.0194 | 59.967 | 60.0494
226.8281 | 123.0972 | -59.9808 | 62.9791 | -0.037537 | 0.0013393 | 0.064068 | 0.066163 | 0.0034607 | 0.00071784 | 0.00030553 | -0.073517 | 0.00138 | 0.064709 | 0.067556 | -0.0018542 | 0.0048108 | -0.0020765 | -0.036621 | 62.851 | -60.0952 | 62.9471 | -59.903 | -60.26 | -0.054932 | -0.073242 | 62.8876 | -60.0174 | 62.97 | -60.054 | -60.1868 | -60.0037 | -0.11444 | -0.12817 | -0.032043 | 0.07782 | 59.9258 | -0.27924 | 60.0403 | -0.16479 | -0.036621 | -0.091553 | -0.009155 | -0.073242 | -0.022888 | -0.20599 | 0.013733 | -0.16937 | 0.19226 | 123.0423 | -0.036621 | 122.9874 | 122.9462 | 122.905 | 122.8317 | 122.8683 | -123.0743 | -122.9965 | 122.9279 | 122.9507 | 59.9442 | 59.9075
227.8906 | 123.23 | -59.9396 | 62.9471 | -0.098572 | 0.0015529 | 0.062145 | 0.064668 | -0.00017091 | 0.00050424 | 9.193e-05 | 0.027191 | 0.00138 | 0.064068 | 0.076101 | -0.0018542 | 0.0024608 | -0.0010083 | 0.004578 | 62.851 | -60.022 | 63.0569 | -59.7198 | -60.0952 | 0.10071 | 0.11902 | 62.8738 | -59.9716 | 63.0798 | -59.9258 | -60.0037 | -59.9121 | -0.082398 | -0.096131 | 0.10986 | 0.21973 | 60.0403 | -0.15564 | 60.1227 | -0.073242 | -0.032044 | -0.073243 | 0.13275 | 0.013733 | 0.027466 | -0.064087 | 0.05951 | -0.032043 | 0.30212 | 123.0789 | 0.045777 | 123.0515 | 122.8729 | 122.8455 | 122.7905 | 122.8134 | -122.9691 | -122.9187 | 122.9965 | 123.0194 | 59.9442 | 60.0586
228.8281 | 123.1201 | -59.9854 | 62.97 | -0.052796 | 0.0017667 | 0.064068 | 0.068941 | -0.0014527 | -0.0031274 | 0.0018009 | -0.067413 | 9.8198e-05 | 0.065777 | 0.066702 | -0.0044178 | 0.003529 | -0.0020765 | -0.018311 | 62.8693 | -60.0906 | 62.9562 | -59.8846 | -60.2646 | -0.032043 | -0.045776 | 62.8784 | -59.967 | 62.9837 | -60.0723 | -60.1776 | -60.0174 | -0.10529 | -0.10071 | -0.013733 | 0.10071 | 59.9533 | -0.27923 | 60.0586 | -0.17395 | 0.018311 | -0.091553 | 0.013733 | -0.086975 | -0.032043 | -0.19226 | -0.050354 | -0.21057 | 0.20599 | 123.0469 | -0.10529 | 122.9507 | 122.9599 | 122.8455 | 122.8546 | 122.8638 | -123.0606 | -122.937 | 122.9416 | 122.9691 | 59.967 | 59.9396
229.8906 | 123.2666 | -59.9304 | 62.9242 | -0.12909 | 0.0015529 | 0.064709 | 0.066804 | 0.00046989 | -0.0027002 | -0.0018307 | 0.04245 | 0.00138 | 0.065777 | 0.055166 | -0.00099977 | 0.0031018 | -0.00079467 | 0.041199 | 62.8647 | -60.0266 | 63.0615 | -59.729 | -60.0815 | 0.11902 | 0.16022 | 62.8555 | -59.9579 | 63.1302 | -59.8984 | -59.9945 | -59.8938 | -0.09613 | -0.059509 | 0.13733 | 0.20142 | 60.0494 | -0.15106 | 60.1456 | -0.054932 | -0.027466 | -0.068664 | 0.20599 | 0.032044 | 0.036621 | -0.064087 | 0.064087 | -0.036621 | 0.29755 | 123.0881 | 0.05951 | 123.0881 | 122.8912 | 122.8134 | 122.7951 | 122.7859 | -122.9507 | -122.8821 | 122.9919 | 123.0606 | 59.9716 | 60.0906
230.8281 | 123.175 | -60.0037 | 62.97 | -0.060425 | 0.0013393 | 0.061932 | 0.067659 | -0.0010253 | 0.00071784 | -0.0026853 | -0.058258 | 0.0009528 | 0.065563 | 0.065206 | -0.0044178 | 0.003529 | -0.0025037 | 0.036621 | 62.9059 | -60.0723 | 62.9929 | -59.8663 | -60.1913 | 0.027466 | 0.045776 | 62.8967 | -59.9716 | 63.0203 | -59.9991 | -60.1044 | -59.9625 | -0.068665 | -0.064087 | 0.022888 | 0.13733 | 60.0311 | -0.18768 | 60.0998 | -0.11902 | 0.032043 | -0.073242 | 0.050354 | 0.004578 | 0.041199 | -0.10071 | 0.009156 | -0.13275 | 0.20599 | 123.0652 | -0.027465 | 122.9919 | 122.9782 | 122.8683 | 122.9095 | 122.9004 | -123.0423 | -122.9416 | 122.9965 | 123.024 | 60.0403 | 60.0494
231.8906 | 123.2346 | -59.967 | 62.9517 | -0.11383 | 0.00048494 | 0.064709 | 0.063386 | -0.0014527 | -0.0027002 | -0.00054907 | 0.024139 | 0.0009528 | 0.06599 | 0.062856 | -0.0035632 | 0.0048108 | 0.0039049 | -0.018311 | 62.8555 | -60.0357 | 62.9883 | -59.848 | -60.2188 | 0.009155 | -0.027466 | 62.8372 | -59.9899 | 63.002 | -59.9533 | -60.1089 | -59.9808 | -0.068665 | -0.09613 | 0.036621 | 0.11902 | 59.9762 | -0.25177 | 60.0449 | -0.18311 | -0.022888 | -0.11444 | 0.050354 | 0.013733 | -0.013733 | -0.14191 | 0.009155 | -0.11902 | 0.18768 | 123.024 | 0.036621 | 122.9919 | 122.8912 | 122.8271 | 122.8226 | 122.8043 | -122.9874 | -122.9416 | 122.9553 | 122.9691 | 59.9487 | 59.9396
232.8281 | 123.1338 | -59.9716 | 62.97 | -0.083313 | 0.00091214 | 0.064281 | 0.0683 | -0.00059811 | -0.0020594 | -0.00012167 | -0.018585 | 0.0020208 | 0.065349 | 0.059866 | -0.0027088 | 0.0037426 | -0.00015387 | -0.054932 | 62.9242 | -60.0128 | 62.9059 | -59.9258 | -60.1959 | 0.004578 | -0.013733 | 62.9059 | -59.9945 | 62.9974 | -60.0357 | -60.1547 | -59.9945 | -0.041198 | -0.045777 | -0.064087 | 0.045777 | 59.9762 | -0.2243 | 60.0174 | -0.18311 | -0.022888 | -0.064087 | 0.027466 | -0.064087 | -0.022888 | -0.18311 | 0 | -0.16022 | 0.086975 | 122.9187 | -0.041199 | 122.9919 | 122.937 | 122.9004 | 122.8958 | 122.8775 | -122.9828 | -122.9645 | 122.8775 | 122.9691 | 59.9167 | 59.9579
233.8281 | 123.1705 | -60.0082 | 62.9791 | -0.045166 | 0.0011257 | 0.064922 | 0.067018 | 0.0026063 | 0.0015722 | 0.0013735 | -0.058258 | 0.0033026 | 0.067058 | 0.067983 | -0.0016406 | 0.0039562 | -0.00036747 | 0.009155 | 62.8693 | -60.0494 | 62.9883 | -59.8618 | -60.2142 | 0.013733 | -0.11902 | 62.8738 | -60.0037 | 63.0112 | -60.0037 | -60.1318 | -59.9854 | -0.041198 | -0.10986 | 0.009155 | 0.14648 | 60.022 | -0.20599 | 60.0632 | -0.16479 | 0.004578 | -0.10529 | 0.032043 | 0.004578 | 0.022888 | -0.1236 | 0.01831 | -0.12817 | 0.18768 | 123.0377 | 0 | 123.0148 | 122.9187 | 122.8775 | 122.8775 | 122.8821 | -123.0286 | -122.9828 | 122.9965 | 123.0194 | 60.0174 | 59.8892
234.8906 | 123.2941 | -59.9258 | 62.9379 | -0.060425 | 0.00069854 | 0.061718 | 0.06595 | -0.0023071 | -0.0018458 | 0.0013735 | 0.048553 | 0.0009528 | 0.066204 | 0.058157 | -0.0039906 | 0.0028882 | -0.0029309 | 0.027466 | 62.8784 | -60.0449 | 63.0798 | -59.7107 | -60.0815 | 0.10986 | 0.15564 | 62.8372 | -59.9304 | 63.1256 | -59.8663 | -59.9762 | -59.8618 | -0.11902 | -0.059509 | 0.14191 | 0.21515 | 60.0357 | -0.15564 | 60.1547 | -0.036621 | -0.004578 | -0.10071 | 0.18768 | 0.059509 | 0.064087 | -0.050354 | 0.068665 | -0.045776 | 0.33417 | 123.1247 | 0.064087 | 123.056 | 122.9233 | 122.7676 | 122.8043 | 122.7631 | -122.9828 | -122.8683 | 123.0057 | 123.0515 | 59.9533 | 60.0815
235.8281 | 123.1888 | -59.9716 | 62.97 | -0.052796 | -0.0018649 | 0.065563 | 0.066163 | 0.0034607 | -0.0012048 | 0.0018009 | -0.055206 | 0.0011664 | 0.06599 | 0.055166 | -0.0029224 | 0.0045972 | -0.0031445 | 0.022888 | 62.9059 | -60.0723 | 62.9974 | -59.8663 | -60.1959 | 0.041199 | 0.041199 | 62.9059 | -59.967 | 63.0386 | -59.9991 | -60.1135 | -59.9625 | -0.10071 | -0.064087 | 0.027466 | 0.10529 | 60.0128 | -0.2243 | 60.1135 | -0.1236 | 0.004578 | -0.064087 | 0.068664 | -0.027465 | 0.009156 | -0.14191 | 0.004578 | -0.14648 | 0.20599 | 123.0698 | -0.032043 | 123.0057 | 122.9782 | 122.8729 | 122.8775 | 122.8775 | -123.0423 | -122.937 | 122.9691 | 123.0103 | 59.9945 | 60.0128
236.8906 | 123.2254 | -59.9487 | 62.9425 | -0.13672 | 0.0032619 | 0.064495 | 0.063814 | 0.0011109 | -0.00056396 | -0.0014035 | 0.036346 | 0.0007392 | 0.065777 | 0.062429 | -0.00078617 | 0.0028882 | 0.00091433 | -0.041199 | 62.8372 | -60.0494 | 62.9745 | -59.8709 | -60.1913 | -0.013733 | -0.050354 | 62.8372 | -59.9808 | 63.121 | -59.9808 | -60.1501 | -59.9304 | -0.10071 | -0.10529 | 0.032043 | 0.077819 | 59.935 | -0.24262 | 60.0357 | -0.14191 | -0.032044 | -0.10529 | 0.17853 | -0.032044 | 0.01831 | -0.20142 | 0.050354 | -0.16937 | 0.17853 | 123.024 | 0 | 123.1018 | 122.8867 | 122.818 | 122.7859 | 122.7859 | -122.9919 | -122.9233 | 122.9233 | 123.0698 | 59.9075 | 59.8984
237.8438 | 123.2391 | -59.9396 | 62.9425 | -0.075684 | -0.00036966 | 0.064922 | 0.066377 | 0.0017517 | -0.0014184 | -0.00033547 | -0.0063781 | 9.8198e-05 | 0.066631 | 0.062429 | -0.0018542 | 0.0037426 | -0.0042127 | -0.018311 | 62.8189 | -60.0723 | 63.0432 | -59.816 | -60.1913 | -0.009155 | -0.041199 | 62.7869 | -60.0357 | 63.1119 | -59.9762 | -60.0861 | -59.903 | -0.13275 | -0.1236 | 0.10071 | 0.1236 | 59.9304 | -0.25177 | 60.0632 | -0.11902 | -0.096131 | -0.15564 | 0.16937 | -0.036621 | 0.036621 | -0.14649 | 0.13275 | -0.050354 | 0.25635 | 123.1155 | 0.05951 | 123.1476 | 122.8912 | 122.8226 | 122.7585 | 122.7264 | -123.0148 | -122.9782 | 122.9828 | 123.0515 | 59.9213 | 59.8984
238.8906 | 123.2254 | -59.9716 | 62.9517 | -0.090943 | 0.0019803 | 0.062145 | 0.065736 | -0.0050843 | 0.0015722 | 0.00094633 | 0.024139 | -0.0007562 | 0.064495 | 0.059011 | -0.0024952 | 0.0031018 | -0.0029309 | -0.041199 | 62.8464 | -60.0449 | 62.9745 | -59.8618 | -60.1959 | -0.009155 | -0.045776 | 62.8418 | -59.9808 | 63.0249 | -59.9945 | -60.1089 | -59.9579 | -0.073242 | -0.10528 | 0.022888 | 0.10986 | 59.9625 | -0.2243 | 60.0357 | -0.15106 | -0.009155 | -0.10986 | 0.073242 | -0.022888 | 0.013733 | -0.13733 | 0.022888 | -0.12817 | 0.18311 | 123.0194 | -0.013733 | 123.0057 | 122.8912 | 122.8226 | 122.818 | 122.8134 | -122.9965 | -122.9324 | 122.9462 | 122.9965 | 59.9304 | 59.9258
239.8281 | 123.1613 | -59.9991 | 63.0157 | -0.045166 | 0.0024075 | 0.063 | 0.065523 | -0.0014527 | -0.0020594 | 0.00051913 | -0.015534 | 0.0028754 | 0.064922 | 0.067129 | -0.0029224 | 0.0033154 | 0.0024097 | 0.041199 | 62.915 | -60.0266 | 62.9745 | -59.8434 | -60.2005 | 0.059509 | 0.036621 | 62.9013 | -59.967 | 62.9929 | -60.0128 | -60.1135 | -60.0128 | -0.027466 | -0.10071 | -0.041199 | 0.15564 | 60.0586 | -0.20142 | 60.0861 | -0.17395 | 0.032043 | -0.11444 | -0.022888 | -0.013733 | -0.013733 | -0.11444 | -0.045776 | -0.14648 | 0.1831 | 123.0011 | -0.045776 | 122.9599 | 122.9416 | 122.8683 | 122.9141 | 122.9004 | -123.0423 | -122.9828 | 122.9736 | 122.9919 | 60.0403 | 60.0357
240.8906 | 123.2117 | -59.9762 | 62.9562 | -0.037537 | 0.00069854 | 0.062572 | 0.064454 | 0.00089729 | -0.0041956 | -0.0020443 | 0.0027771 | 0.00138 | 0.064281 | 0.06072 | -0.0024952 | 0.0033154 | 0.0011279 | -0.022888 | 62.8372 | -60.0449 | 62.9837 | -59.8755 | -60.1913 | 0.013733 | -0.013733 | 62.8235 | -59.9991 | 63.0569 | -59.9762 | -60.0769 | -59.9533 | -0.068665 | -0.11902 | 0.027466 | 0.10071 | 59.9899 | -0.21515 | 60.0586 | -0.14648 | -0.022888 | -0.13275 | 0.10071 | 0 | 0.022888 | -0.10071 | 0.045776 | -0.07782 | 0.16937 | 123.0286 | 0.022888 | 123.056 | 122.8821 | 122.8226 | 122.8134 | 122.7997 | -123.0011 | -122.9553 | 122.9599 | 123.0331 | 59.9533 | 59.9625
241.8281 | 123.143 | -59.9533 | 63.0066 | -0.037537 | 0.0017667 | 0.062145 | 0.065736 | 0.00046989 | -0.00077756 | 9.193e-05 | -0.0002747 | 0.0007392 | 0.065563 | 0.064565 | -0.0035632 | 0.0026746 | -0.0014355 | 0.045776 | 62.8784 | -60.0632 | 63.002 | -59.8251 | -60.173 | 0.07782 | 0.036621 | 62.915 | -59.9808 | 62.9883 | -60.022 | -60.1181 | -60.0082 | -0.10986 | -0.12817 | -0.004578 | 0.12817 | 60.0311 | -0.21973 | 60.141 | -0.10986 | -0.027466 | -0.091553 | -0.018311 | -0.068665 | -0.054932 | -0.16479 | -0.027466 | -0.13733 | 0.23804 | 123.0652 | -0.041199 | 122.9691 | 122.9416 | 122.8958 | 122.8317 | 122.8683 | -123.0698 | -122.9874 | 122.9553 | 122.9416 | 59.9991 | 59.9899
242.9062 | 123.1842 | -59.9762 | 62.9471 | -0.075684 | 0.00027134 | 0.063641 | 0.06595 | 0.0049561 | -0.0014184 | 0.00094633 | -0.06131 | 0.0026618 | 0.065136 | 0.069692 | 0.003059 | 0.0048108 | -0.00036747 | 0.036621 | 62.8738 | -60.0494 | 63.0112 | -59.848 | -60.1913 | 0.009155 | 0.036621 | 62.9013 | -59.9899 | 63.0569 | -60.0082 | -60.0998 | -59.9442 | -0.073242 | -0.073243 | 0.064086 | 0.12817 | 59.9854 | -0.21515 | 60.0586 | -0.14191 | -0.013733 | -0.045777 | 0.10986 | -0.032044 | 0.032043 | -0.1236 | 0.045776 | -0.10986 | 0.20142 | 123.0606 | -0.018311 | 123.0469 | 122.9233 | 122.8912 | 122.85 | 122.8775 | -122.9965 | -122.937 | 122.9874 | 123.0331 | 60.0128 | 60.0128
243.8281 | 123.23 | -59.9487 | 62.9562 | -0.25116 | 0.0039029 | 0.062145 | 0.064027 | -0.0016663 | -0.0014184 | -0.0018307 | 0.021088 | 0.0007392 | 0.064709 | 0.059866 | -0.0029224 | 0.0016064 | -0.0012219 | 0.086975 | 62.8418 | -60.022 | 63.0798 | -59.7427 | -60.1364 | 0.11902 | 0.12817 | 62.8555 | -59.9762 | 63.0844 | -59.8984 | -60.0128 | -59.9167 | -0.073243 | -0.11444 | 0.1236 | 0.20599 | 60.0677 | -0.18768 | 60.141 | -0.11444 | -0.027466 | -0.10071 | 0.12817 | 0.050354 | 0.032043 | -0.064087 | 0.059509 | -0.036621 | 0.27924 | 123.1018 | 0.07782 | 123.0606 | 122.8638 | 122.8317 | 122.7905 | 122.8043 | -122.9782 | -122.9324 | 123.0286 | 123.0331 | 60.0357 | 60.0769
244.8906 | 123.2162 | -59.9625 | 62.9059 | -0.14435 | 0.0013393 | 0.064709 | 0.06595 | 0.0019653 | -0.00056396 | 9.193e-05 | 0.0027771 | -0.0005426 | 0.066204 | 0.060293 | -0.002068 | 0.0026746 | 0.0015551 | -0.022888 | 62.8098 | -60.0494 | 63.0157 | -59.7931 | -60.2051 | 0 | 0.009155 | 62.8281 | -59.9945 | 63.0569 | -59.9762 | -60.0723 | -59.9258 | -0.086975 | -0.096131 | 0.10986 | 0.16937 | 59.9625 | -0.24262 | 60.0494 | -0.15564 | -0.032044 | -0.07782 | 0.15106 | -0.013733 | 0.036621 | -0.10986 | 0.068665 | -0.07782 | 0.25635 | 123.0652 | 0.018311 | 123.0515 | 122.8592 | 122.8226 | 122.7722 | 122.7905 | -122.9553 | -122.9004 | 122.9782 | 123.0194 | 59.9396 | 59.9716
245.8281 | 123.1293 | -59.9625 | 62.9883 | -0.060425 | 0.0026211 | 0.064922 | 0.065309 | 0.0041015 | -0.0020594 | -0.0018307 | -0.0094299 | 0.0028754 | 0.064495 | 0.063284 | -0.0018542 | 0.0013928 | -0.0035719 | 0.068665 | 62.8876 | -60.022 | 63.0249 | -59.8068 | -60.1547 | 0.091553 | 0.064087 | 62.883 | -59.967 | 63.0295 | -60.0082 | -60.0906 | -59.9899 | -0.05951 | -0.10071 | 0.036621 | 0.15564 | 60.054 | -0.19226 | 60.1135 | -0.13275 | -0.004578 | -0.10529 | 0.041199 | -0.045777 | -0.027466 | -0.12817 | -0.022888 | -0.1236 | 0.21515 | 123.0469 | -0.041199 | 122.9965 | 122.9095 | 122.85 | 122.85 | 122.8455 | -123.0103 | -122.9553 | 122.9874 | 122.9919 | 60.0311 | 60.0266
246.8906 | 123.1659 | -60.0082 | 62.9379 | -0.098572 | 0.00048494 | 0.067059 | 0.066591 | 0.00068369 | -0.0018458 | -0.00076267 | -0.076569 | 0.0024482 | 0.064281 | 0.064779 | -0.0018542 | 0.0043836 | 0.0017687 | -0.31586 | 62.8143 | -60.1593 | 62.9562 | -59.9762 | -60.3058 | -0.091553 | -0.10529 | 62.8601 | -60.0311 | 62.9929 | -60.0861 | -60.2005 | -60.0174 | -0.15106 | -0.1236 | 0.018311 | 0.032044 | 59.9167 | -0.29755 | 60.0677 | -0.14648 | -0.022888 | -0.07782 | 0.054932 | -0.07782 | -0.009155 | -0.19226 | 0.013733 | -0.16937 | 0.18311 | 123.1155 | -0.054932 | 123.024 | 122.9736 | 122.8912 | 122.8226 | 122.8683 | -123.0972 | -122.9691 | 122.9645 | 123.0011 | 59.6924 | 59.903
247.8438 | 123.2025 | -59.9854 | 62.9013 | -0.075684 | 0.0026211 | 0.063 | 0.067232 | -0.00059811 | -0.0033412 | -0.0016171 | -0.058258 | 0.0011664 | 0.065136 | 0.067556 | -0.0018542 | 0.0039562 | -0.00015387 | -0.07782 | 62.883 | -60.1181 | 62.9196 | -59.9396 | -60.2966 | -0.10071 | -0.13275 | 62.8738 | -60.0128 | 62.9929 | -60.0677 | -60.1776 | -59.9945 | -0.13275 | -0.01831 | 0.018311 | 0.045777 | 59.8846 | -0.31128 | 60.0174 | -0.17853 | -0.027465 | -0.027466 | 0.091553 | -0.082397 | -0.009155 | -0.19226 | 0.01831 | -0.1648 | 0.17853 | 123.0377 | -0.054932 | 123.0057 | 123.0011 | 122.8867 | 122.8683 | 122.8592 | -123.0194 | -122.9141 | 122.905 | 122.9782 | 59.9075 | 59.8526
248.8906 | 123.175 | -59.9762 | 62.9105 | -0.090943 | 0.00069854 | 0.064281 | 0.065523 | 0.0028199 | -0.00035036 | -0.0011899 | -0.064362 | 0.0022346 | 0.066845 | 0.061148 | -0.0044178 | 0.0033154 | -0.00079467 | -0.07782 | 62.851 | -60.1135 | 62.9242 | -59.9075 | -60.2783 | -0.09613 | -0.10529 | 62.8372 | -60.0037 | 63.0249 | -60.0266 | -60.1181 | -59.967 | -0.13733 | -0.059509 | 0.013733 | 0.068664 | 59.8801 | -0.30212 | 60.0174 | -0.16479 | -0.027466 | -0.073242 | 0.11444 | -0.050354 | 0.009155 | -0.14191 | 0.036621 | -0.11444 | 0.20599 | 123.0377 | -0.022888 | 123.0286 | 122.9645 | 122.8409 | 122.8271 | 122.8134 | -123.024 | -122.9141 | 122.9004 | 123.0011 | 59.8984 | 59.8709
249.8281 | 123.1888 | -59.9762 | 62.9288 | -0.12909 | 0.0015529 | 0.062572 | 0.064454 | -0.0014527 | 0.0013586 | -0.0024717 | 0.021088 | 0.0005256 | 0.06599 | 0.057943 | -0.0029224 | 0.0024608 | 0.0015551 | -0.054932 | 62.8555 | -60.0357 | 62.97 | -59.8663 | -60.2142 | -0.022888 | -0.045776 | 62.8464 | -59.9899 | 63.0432 | -60.0266 | -59.8846 | -59.8709 | -0.05951 | -0.073242 | 0.041199 | 0.10986 | 59.9533 | -0.23804 | 60.0128 | -0.17853 | -0.013733 | -0.082397 | 0.11444 | -0.050354 | 0.10529 | 0.091552 | 0.11902 | 0.10528 | 0.16937 | 123.0057 | -0.036621 | 123.0331 | 122.8912 | 122.8363 | 122.8317 | 122.8226 | -122.9645 | -122.9187 | 122.9462 | 123.0194 | 59.9213 | 59.9304
250.8906 | 123.1567 | -59.9808 | 62.97 | -0.075684 | 0.0015529 | 0.063213 | 0.067445 | 0.00025629 | -0.0024866 | 0.00094633 | -0.064362 | 0.0026618 | 0.066418 | 0.066061 | -0.0054858 | 0.0048108 | -0.0031445 | -0.009155 | 62.8647 | -60.0677 | 62.9837 | -59.8846 | -60.2371 | -0.027466 | -0.022888 | 62.8647 | -59.9899 | 62.9929 | -60.0449 | -60.1593 | -59.9854 | -0.086975 | -0.10529 | 0.013733 | 0.09613 | 59.9533 | -0.25635 | 60.0403 | -0.16937 | -0.009155 | -0.10529 | 0.022888 | -0.064087 | -0.004578 | -0.17853 | 0.004577 | -0.16937 | 0.1831 | 123.0515 | -0.054932 | 122.9828 | 122.9324 | 122.8546 | 122.8455 | 122.8455 | -123.0377 | -122.9599 | 122.9645 | 122.9736 | 59.9716 | 59.9579
251.8281 | 123.2254 | -59.9167 | 62.97 | -0.12146 | 0.0015529 | 0.063641 | 0.065095 | 0.0017517 | 0.0015722 | -0.0014035 | 0.033295 | 0.0003118 | 0.064281 | 0.060507 | -0.003136 | 0.0033154 | -0.00015387 | 0.091553 | 62.8555 | -60.0266 | 63.0524 | -59.761 | -60.1227 | 0.10986 | 0.1236 | 62.8647 | -59.9579 | 63.0753 | -59.9258 | -60.0449 | -59.9167 | -0.10986 | -0.11444 | 0.082397 | 0.15564 | 60.0266 | -0.20599 | 60.1364 | -0.096131 | -0.041199 | -0.10529 | 0.10529 | -0.009155 | 0 | -0.12817 | 0.041199 | -0.086975 | 0.2655 | 123.0789 | 0.032044 | 123.0331 | 122.8821 | 122.8226 | 122.7722 | 122.7814 | -122.9965 | -122.9279 | 122.9691 | 122.9919 | 60.0082 | 60.0403
252.8281 | 123.2529 | -59.9579 | 62.9517 | -0.098572 | -0.00036966 | 0.060436 | 0.063814 | -0.0027343 | -0.00013676 | 9.193e-05 | 0.039398 | -0.000329 | 0.065563 | 0.06307 | -0.0027088 | 0.0016064 | 0.00027333 | 0.022888 | 62.8189 | -60.0449 | 63.0615 | -59.761 | -60.1089 | 0.10986 | 0.14648 | 62.8464 | -59.9533 | 63.1073 | -59.8892 | -59.9762 | -59.8801 | -0.086975 | -0.13275 | 0.10986 | 0.19684 | 60.0677 | -0.15106 | 60.1547 | -0.064087 | 0.004578 | -0.10528 | 0.15564 | 0.068665 | 0.07782 | -0.01831 | 0.073242 | -0.022888 | 0.28381 | 123.1064 | 0.064087 | 123.0606 | 122.8638 | 122.7997 | 122.7768 | 122.8043 | -122.9965 | -122.905 | 123.0194 | 123.0652 | 59.9808 | 60.1044
253.8906 | 123.1247 | -59.9854 | 62.97 | -0.014649 | 0.0015529 | 0.063213 | 0.0683 | 0.0062379 | -0.0012048 | 0.0013735 | -0.088776 | 0.0015936 | 0.06599 | 0.064993 | -0.004845 | 0.0043836 | 0.00048713 | -0.050354 | 62.8738 | -60.0861 | 62.915 | -59.9442 | -60.2921 | -0.10986 | -0.13733 | 62.8647 | -60.0128 | 62.9517 | -60.1227 | -60.2325 | -60.054 | -0.10071 | -0.096131 | -0.054932 | 0.041199 | 59.8755 | -0.3067 | 59.9762 | -0.20599 | -0.027465 | -0.10529 | -0.018311 | -0.13733 | -0.068664 | -0.24719 | -0.041199 | -0.21973 | 0.14191 | 123.0011 | -0.10986 | 122.9645 | 122.9599 | 122.8775 | 122.8592 | 122.85 | -123.056 | -122.9828 | 122.9004 | 122.937 | 59.935 | 59.848
254.8281 | 123.2391 | -59.967 | 62.9105 | -0.13672 | 0.0024075 | 0.067699 | 0.065095 | 0.0019653 | -0.0027002 | -0.00097627 | -0.015534 | 0.0007392 | 0.067272 | 0.061148 | -0.0052722 | 0.0031018 | -0.00058107 | -0.086975 | 62.7823 | -60.1135 | 63.0661 | -59.8251 | -60.2097 | 0.032043 | -0.009155 | 62.8326 | -60.0082 | 63.0661 | -59.967 | -60.0403 | -59.9258 | -0.14648 | -0.12817 | 0.15564 | 0.14191 | 59.9991 | -0.24262 | 60.1456 | -0.096131 | -0.041199 | -0.077819 | 0.15564 | 0 | 0.041199 | -0.073242 | 0.082398 | -0.032043 | 0.28839 | 123.1796 | 0.041199 | 123.0743 | 122.8958 | 122.8409 | 122.7493 | 122.7997 | -123.024 | -122.9187 | 123.0331 | 123.0331 | 59.8801 | 59.9579
255.8906 | 123.1567 | -59.9945 | 62.9654 | -0.12909 | 0.00027134 | 0.064068 | 0.067872 | -0.0010253 | -0.00035036 | 0.0015871 | -0.073517 | 0.00138 | 0.068127 | 0.063925 | 6.8432e-05 | 0.0054516 | -0.0029309 | -0.086975 | 62.8738 | -60.1135 | 62.9105 | -59.9716 | -60.3287 | -0.1236 | -0.15106 | 62.8784 | -60.0174 | 62.9059 | -59.8618 | -60.228 | -60.0861 | -0.11902 | -0.091553 | -0.054932 | 0.022888 | 59.8709 | -0.33417 | 59.9899 | -0.21515 | -0.022888 | -0.086975 | -0.059509 | 0.13275 | -0.091553 | -0.23346 | -0.068665 | -0.21057 | 0.14191 | 123.024 | 0.15564 | 122.9233 | 122.9874 | 122.8958 | 122.8683 | 122.8729 | -123.0789 | -122.9828 | 122.905 | 122.9004 | 59.9075 | 59.8434
256.8281 | 123.23 | -59.9442 | 62.9242 | -0.17487 | 0.00069854 | 0.065563 | 0.065736 | -0.00017091 | 0.0015722 | 0.00030553 | 0.048553 | 0.0005256 | 0.065563 | 0.059225 | -0.0033496 | 0.003529 | -0.0012219 | -0.022888 | 62.8235 | -60.054 | 63.0157 | -59.7977 | -60.5026 | -0.091553 | -0.054932 | 62.8235 | -59.9854 | 63.0478 | -59.9762 | -60.0449 | -59.935 | -0.10986 | -0.10071 | 0.091553 | 0.14648 | 59.8526 | -0.55847 | 59.9625 | -0.44861 | -0.041199 | -0.10071 | 0.1236 | -0.032043 | 0.009155 | -0.10071 | 0.050354 | -0.059509 | 0.25635 | 123.0698 | 0.009156 | 123.0331 | 122.8775 | 122.8088 | 122.7676 | 122.7676 | -122.9782 | -122.9095 | 122.9599 | 122.9919 | 59.9213 | 59.8892
257.9062 | 123.2254 | -59.9716 | 62.9196 | -0.14435 | 0.0019803 | 0.064281 | 0.066163 | -0.00081171 | -0.0016322 | 9.193e-05 | -0.018585 | 0.0009528 | 0.06599 | 0.062429 | -0.0037768 | 0.0022472 | -0.00036747 | -0.027466 | 62.8326 | -60.0449 | 63.0203 | -59.8068 | -60.1913 | -0.009155 | 0 | 62.8006 | -59.967 | 63.0478 | -59.9808 | -60.0906 | -59.9533 | -0.073242 | -0.086975 | 0.10071 | 0.16479 | 59.9625 | -0.21973 | 60.0357 | -0.14648 | 0.004578 | -0.11902 | 0.12817 | -0.009155 | 0.018311 | -0.11902 | 0.013733 | -0.1236 | 0.23804 | 123.0652 | -0.013733 | 123.0148 | 122.8775 | 122.7676 | 122.8043 | 122.7722 | -122.9645 | -122.8867 | 122.9919 | 123.0194 | 59.9442 | 59.9716
258.8281 | 123.1155 | -59.9945 | 62.9654 | -0.1062 | 0.00048494 | 0.064281 | 0.067659 | 0.0038879 | -0.0014184 | -0.00033547 | -0.091827 | 0.0003118 | 0.065136 | 0.07012 | -0.0022816 | 0.0060924 | 0.0047595 | -0.082397 | 62.8464 | -60.1135 | 62.8876 | -59.9854 | -60.3058 | -0.11902 | -0.16022 | 62.8647 | -60.0128 | 62.9745 | -60.3607 | -60.0494 | -59.7931 | -0.11902 | -0.11902 | -0.07782 | 0.009155 | 59.8755 | -0.31128 | 59.9945 | -0.19226 | -0.01831 | -0.10071 | 0.009155 | -0.36621 | 0.20142 | -0.054931 | 0.21973 | -0.036621 | 0.12817 | 123.0011 | -0.3479 | 122.9874 | 122.9599 | 122.8775 | 122.8409 | 122.8592 | -123.0789 | -122.9782 | 122.8821 | 122.9691 | 59.9121 | 59.8343
259.8906 | 123.143 | -59.9716 | 62.9654 | -0.045166 | 5.7742e-05 | 0.062572 | 0.06595 | 0.0034607 | -0.00099116 | -0.0014035 | -0.070465 | 0.0015936 | 0.065563 | 0.069906 | -0.00099977 | 0.005238 | -0.00079467 | 0.036621 | 62.8738 | -60.0632 | 62.9791 | -59.8434 | -60.2097 | 0.027466 | 0.036621 | 62.9105 | -59.9762 | 63.0386 | -60.0037 | -60.1044 | -59.9579 | -0.091552 | -0.091553 | 0.013733 | 0.12817 | 59.9991 | -0.23804 | 60.0906 | -0.14649 | -0.004577 | -0.054932 | 0.073242 | -0.032043 | 0.013733 | -0.13275 | 0.01831 | -0.12817 | 0.21973 | 123.0423 | -0.027466 | 123.0148 | 122.937 | 122.8867 | 122.8455 | 122.8821 | -123.0286 | -122.9416 | 122.9507 | 123.0103 | 60.0082 | 60.0082
260.8281 | 123.1384 | -60.0037 | 62.9196 | 0.00061049 | 0.0015529 | 0.063854 | 0.067232 | -0.0016663 | -0.0014184 | -0.0011899 | -0.042999 | 0.0024482 | 0.064709 | 0.062429 | -0.00099977 | 0.0037426 | 0.0013415 | -0.10529 | 62.8647 | -60.0815 | 62.9196 | -59.9487 | -60.3149 | -0.091553 | -0.1236 | 62.8601 | -60.0128 | 62.9745 | -60.0632 | -60.1822 | -60.0082 | -0.07782 | -0.054932 | 0 | 0.054932 | 59.9121 | -0.31128 | 59.9899 | -0.23346 | -0.009155 | -0.05951 | 0.054931 | -0.059509 | -0.004578 | -0.17853 | 0.004577 | -0.16937 | 0.13275 | 123.0011 | -0.050354 | 122.9874 | 122.9462 | 122.8729 | 122.8683 | 122.8638 | -123.0011 | -122.9324 | 122.9233 | 122.9782 | 59.8984 | 59.8801
261.8906 | 123.1613 | -59.9579 | 62.9745 | -0.052796 | 0.0011257 | 0.063 | 0.062532 | 0.0023925 | -0.00056396 | 0.00094633 | -0.052155 | 0.0020208 | 0.066845 | 0.062002 | -0.001427 | 0.0039562 | 0.00070073 | 0.041199 | 62.8922 | -60.0723 | 62.9745 | -59.8389 | -60.1822 | 0.027466 | 0.032043 | 62.8967 | -59.9487 | 63.0341 | -59.9899 | -60.1181 | -59.9716 | -0.11444 | -0.082397 | 0 | 0.11902 | 59.9854 | -0.2243 | 60.0998 | -0.10986 | 0.009156 | -0.077819 | 0.05951 | -0.032043 | -0.013733 | -0.16022 | -0.022889 | -0.16937 | 0.23346 | 123.0469 | -0.041199 | 122.9828 | 122.9645 | 122.8455 | 122.85 | 122.8546 | -123.0469 | -122.9233 | 122.9324 | 122.9919 | 59.9991 | 59.9899
262.8281 | 123.111 | -59.9854 | 62.97 | -0.12909 | 0.0013393 | 0.063641 | 0.064882 | 0.0011109 | -0.0037684 | -0.00012167 | -0.030792 | 0.0033026 | 0.065777 | 0.069479 | -0.00078617 | 0.008015 | 0.0045459 | -0.045776 | 62.883 | -60.0632 | 62.9471 | -59.9121 | -60.2783 | -0.068665 | -0.10529 | 62.8693 | -59.9899 | 62.9745 | -60.0677 | -60.1913 | -60.0174 | -0.077819 | -0.086975 | -0.022888 | 0.073243 | 59.9167 | -0.29297 | 59.9945 | -0.21515 | -0.004577 | -0.10071 | 0.004577 | -0.082397 | -0.032043 | -0.20599 | -0.027466 | -0.20142 | 0.15106 | 123.0103 | -0.07782 | 122.9645 | 122.9462 | 122.8592 | 122.8683 | 122.8546 | -123.0331 | -122.9599 | 122.9324 | 122.9599 | 59.9396 | 59.8801
263.8906 | 123.1613 | -59.9762 | 62.9791 | -0.037537 | -0.00036966 | 0.061932 | 0.06595 | -0.0010253 | -0.00035036 | 0.00051913 | -0.036896 | 0.0007392 | 0.064068 | 0.061148 | -0.00078617 | 0.0011792 | -0.00015387 | -0.004578 | 62.9333 | -60.0723 | 62.9379 | -59.903 | -60.2234 | 0.013733 | -0.013733 | 62.8647 | -60.0037 | 62.9929 | -60.0037 | -60.1318 | -59.9899 | -0.096131 | -0.045776 | -0.041199 | 0.073242 | 59.9899 | -0.24719 | 60.0861 | -0.15106 | -0.027466 | -0.11444 | 0.013733 | -0.027466 | -0.013733 | -0.15564 | 0.013733 | -0.12817 | 0.16937 | 123.0103 | 0 | 122.9965 | 123.0057 | 122.8683 | 122.9095 | 122.8409 | -123.0515 | -122.9828 | 122.9141 | 122.9691 | 59.9716 | 59.9625
264.8281 | 123.1522 | -59.9808 | 62.97 | -0.090943 | 0.00069854 | 0.063427 | 0.064668 | 0.00089729 | -0.0014184 | -0.0022581 | -0.070465 | -0.0001154 | 0.067058 | 0.065634 | -0.0016406 | 0.0026746 | -0.00036747 | 0.009155 | 62.8922 | -60.0677 | 62.9837 | -59.967 | -60.3882 | 0.018311 | 0.050354 | 62.883 | -59.9854 | 63.0157 | -60.0037 | -60.1181 | -59.9762 | -0.086975 | -0.07782 | 0.013733 | 0.013733 | 59.9991 | -0.40741 | 60.0861 | -0.32044 | -0.004578 | -0.086975 | 0.045776 | -0.022888 | 0.004578 | -0.13733 | 0.009156 | -0.13275 | 0.10071 | 123.0515 | -0.01831 | 123.0011 | 122.9599 | 122.8683 | 122.8729 | 122.8638 | -123.0377 | -122.9553 | 122.9645 | 122.9965 | 59.9899 | 60.0311
265.8281 | 123.2117 | -59.9899 | 62.9745 | -0.075684 | 0.0021939 | 0.064709 | 0.065736 | -0.00059811 | -0.0016322 | 0.0020145 | -0.073517 | 0.0037298 | 0.068767 | 0.060934 | -0.0027088 | 0.0026746 | 0.0013415 | -0.09613 | 62.8693 | -60.1089 | 62.8693 | -60.0037 | -60.3195 | -0.10071 | -0.15564 | 62.8464 | -60.0311 | 63.1256 | -60.4065 | -60.3561 | -59.9258 | -0.11902 | -0.10529 | -0.10529 | -0.013733 | 59.8892 | -0.32959 | 60.0082 | -0.21057 | -0.041199 | -0.12817 | 0.15106 | -0.41657 | 0.064087 | -0.36621 | 0.10529 | -0.32501 | 0.10529 | 122.9782 | -0.37537 | 123.1567 | 122.9782 | 122.8775 | 122.8592 | 122.8363 | -123.0835 | -123.0057 | 122.8592 | 123.1155 | 59.8938 | 59.8343
266.8906 | 123.1338 | -59.9533 | 63.002 | -0.075684 | -0.00036966 | 0.064709 | 0.061464 | -0.00017091 | -0.00077756 | -0.00097627 | 0.014984 | 0.0007392 | 0.06599 | 0.06307 | -0.0029224 | 0.0024608 | 0.0017687 | 0.027466 | 62.9105 | -60.0449 | 62.9929 | -59.8389 | -60.1868 | 0.059509 | 0.041199 | 62.8876 | -59.9716 | 62.9883 | -60.0174 | -60.1135 | -59.9899 | -0.091553 | -0.091553 | -0.009155 | 0.11444 | 60.0128 | -0.23346 | 60.1044 | -0.14191 | -0.018311 | -0.11444 | -0.013733 | -0.064087 | -0.036621 | -0.16022 | -0.01831 | -0.14191 | 0.20599 | 123.0377 | -0.045776 | 122.9599 | 122.9553 | 122.8592 | 122.8638 | 122.8409 | -123.0469 | -122.9736 | 122.9462 | 122.9416 | 59.9808 | 59.9945
267.8281 | 123.1293 | -59.9991 | 62.9745 | -0.045166 | 5.7742e-05 | 0.063427 | 0.066163 | 0.00025629 | 0.00050424 | 9.193e-05 | -0.027741 | 0.0011664 | 0.065777 | 0.068411 | -0.003136 | 0.0037426 | 0.00027333 | -0.032043 | 62.8876 | -60.0906 | 62.9288 | -59.9075 | -60.2692 | -0.059509 | -0.068665 | 62.8738 | -59.9854 | 62.9791 | -60.0632 | -60.1868 | -60.0128 | -0.091553 | -0.086975 | -0.045776 | 0.091552 | 59.9396 | -0.27008 | 60.0311 | -0.17853 | 0.013732 | -0.10071 | 0.004578 | -0.064087 | -0.013733 | -0.18768 | -0.027465 | -0.20142 | 0.1831 | 123.0194 | -0.077819 | 122.9645 | 122.9782 | 122.8592 | 122.8867 | 122.8729 | -123.0652 | -122.9599 | 122.9279 | 122.9782 | 59.967 | 59.9304
268.8906 | 123.143 | -59.9716 | 62.9883 | -0.060425 | 0.0034757 | 0.062145 | 0.064668 | -0.0018799 | -0.002273 | -0.0022581 | 0.021088 | 0.0018072 | 0.065777 | 0.056875 | -0.0037768 | 0.0024608 | 0.00048713 | 0.059509 | 62.8647 | -60.0266 | 63.0066 | -59.8022 | -60.1639 | 0.07782 | 0.054932 | 62.8784 | -59.9762 | 62.9791 | -59.9945 | -60.0861 | -59.9625 | -0.054931 | -0.1236 | 0.018311 | 0.16937 | 60.0494 | -0.19226 | 60.1044 | -0.13733 | -0.004577 | -0.10986 | -0.009155 | -0.022888 | 0.009156 | -0.11444 | 0.013733 | -0.10986 | 0.2243 | 123.0331 | -0.018311 | 122.9553 | 122.8912 | 122.8546 | 122.8363 | 122.85 | -123.0148 | -122.9645 | 122.9782 | 122.9507 | 60.0311 | 60.0266
269.8281 | 123.1293 | -59.9899 | 62.9974 | -0.029907 | 0.0017667 | 0.064709 | 0.067018 | 0.00046989 | -0.00013676 | 0.00094633 | -0.070465 | 0.0045844 | 0.065563 | 0.055166 | -0.003136 | 0.0028882 | 0.00091433 | -0.027466 | 62.8647 | -60.0769 | 62.9471 | -59.8892 | -60.2554 | -0.054932 | -0.050354 | 62.8784 | -60.0174 | 62.97 | -60.0769 | -60.173 | -60.0037 | -0.086975 | -0.13275 | -0.050354 | 0.10071 | 59.935 | -0.2655 | 60.022 | -0.17853 | -0.027466 | -0.11902 | -0.027466 | -0.086975 | -0.013733 | -0.18311 | 0.013733 | -0.15564 | 0.18768 | 123.024 | -0.059509 | 122.9874 | 122.9416 | 122.8958 | 122.8546 | 122.8683 | -123.0743 | -123.0148 | 122.937 | 122.9599 | 59.9625 | 59.9396
270.8906 | 123.2895 | -59.9304 | 62.9425 | -0.037537 | -0.00058326 | 0.063427 | 0.064454 | -0.0029479 | 0.00029044 | 0.00073273 | 0.048553 | 0.0018072 | 0.065349 | 0.064993 | -0.0016406 | 0.0016064 | -0.0027173 | 0.041199 | 62.8464 | -60.0357 | 63.0569 | -59.7382 | -60.1044 | 0.11444 | 0.15106 | 62.8189 | -59.9579 | 63.1073 | -59.8709 | -59.9945 | -59.8709 | -0.10529 | -0.09613 | 0.11444 | 0.19226 | 60.0449 | -0.17395 | 60.1501 | -0.068664 | -0.027466 | -0.1236 | 0.1648 | 0.059509 | 0.059509 | -0.064087 | 0.086975 | -0.036621 | 0.29755 | 123.0927 | 0.086975 | 123.0652 | 122.8821 | 122.7768 | 122.7768 | 122.7493 | -122.9782 | -122.9004 | 122.9874 | 123.0377 | 59.9716 | 60.0815
271.8281 | 123.1018 | -60.0082 | 62.9608 | -0.068054 | 0.0019803 | 0.065563 | 0.0683 | -0.00017091 | -0.0012048 | 0.0013735 | -0.067413 | 0.0020208 | 0.064495 | 0.066274 | -0.0046314 | 0.0058788 | 0.0017687 | -0.073242 | 62.8922 | -60.1089 | 62.9242 | -59.9442 | -60.2966 | -0.07782 | -0.13275 | 62.8601 | -60.0082 | 62.9425 | -60.1135 | -60.228 | -60.0494 | -0.10071 | -0.068664 | -0.036621 | 0.064087 | 59.9304 | -0.28839 | 60.0311 | -0.18768 | 0 | -0.10071 | -0.01831 | -0.10529 | -0.041198 | -0.21973 | -0.041198 | -0.21973 | 0.16479 | 123.0331 | -0.10529 | 122.9507 | 123.0011 | 122.8683 | 122.9004 | 122.8683 | -123.0698 | -122.9691 | 122.9324 | 122.9507 | 59.935 | 59.8755
272.8281 | 123.111 | -59.9716 | 63.002 | -0.014649 | 0.0011257 | 0.063854 | 0.064668 | 0.0032471 | -0.0016322 | 0.0013735 | 0.011932 | 0.0009528 | 0.063 | 0.061788 | -0.002068 | 0.0022472 | -0.00079467 | 0.041199 | 62.9013 | -60.0449 | 62.97 | -59.8434 | -60.2051 | 0.045776 | 0.050354 | 62.8876 | -59.9716 | 62.9929 | -60.022 | -60.1135 | -59.9945 | -0.073242 | -0.10071 | -0.032043 | 0.12817 | 60.0174 | -0.23346 | 60.0906 | -0.16022 | 0 | -0.11444 | -0.009155 | -0.050354 | -0.022888 | -0.14191 | -0.022888 | -0.14191 | 0.20142 | 123.0148 | -0.050354 | 122.9645 | 122.9462 | 122.8592 | 122.8729 | 122.8592 | -123.0469 | -122.9736 | 122.9416 | 122.9645 | 60.0128 | 60.022
273.8906 | 123.2346 | -59.9625 | 62.9196 | -0.090943 | 0.00027134 | 0.064922 | 0.065523 | 0.00025629 | -0.00099116 | -0.0033261 | -0.021637 | 0.0043708 | 0.066845 | 0.061788 | -0.0037768 | 0.0028882 | 0.0021961 | -0.013733 | 62.8052 | -60.0677 | 63.0066 | -59.7977 | -60.1822 | -0.022888 | -0.25177 | 62.7731 | -60.0128 | 63.0661 | -59.9533 | -60.0449 | -59.8892 | -0.10529 | -0.11444 | 0.086975 | 0.16479 | 59.9396 | -0.21973 | 60.0449 | -0.11444 | -0.050354 | -0.14649 | 0.14648 | 0.009155 | 0.073242 | -0.082398 | 0.1236 | -0.032044 | 0.27008 | 123.0743 | 0.059509 | 123.0789 | 122.8729 | 122.7859 | 122.7676 | 122.7356 | -122.9874 | -122.9324 | 122.9691 | 123.0286 | 59.9487 | 59.7107
274.8281 | 123.1293 | -59.9487 | 62.9929 | -0.075684 | 0.0026211 | 0.063 | 0.065523 | -0.0012391 | -0.00013676 | -0.0048215 | 0.014984 | -0.0007562 | 0.064495 | 0.064565 | -0.004845 | -0.0013844 | 0.0028369 | 0.064087 | 62.883 | -60.0311 | 63.0249 | -59.816 | -60.141 | 0.09613 | 0.068665 | 62.8738 | -59.967 | 62.9929 | -60.0082 | -60.0815 | -59.967 | -0.082398 | -0.10986 | 0.032043 | 0.13275 | 60.0449 | -0.19226 | 60.1273 | -0.10986 | -0.018311 | -0.11902 | 0 | -0.05951 | -0.018311 | -0.13275 | 0 | -0.11444 | 0.21515 | 123.056 | -0.041199 | 122.9599 | 122.9141 | 122.8409 | 122.8317 | 122.8226 | -123.024 | -122.9599 | 122.9736 | 122.9416 | 60.0128 | 60.0174
275.8906 | 123.2071 | -59.9899 | 62.9379 | -0.1062 | 0.0015529 | 0.062572 | 0.066377 | -0.00059811 | -0.0012048 | 0.00030553 | 0.027191 | 0.0009528 | 0.06599 | 0.06542 | -0.0022816 | 0.003529 | -0.0016493 | -0.050354 | 62.8326 | -60.0677 | 62.9517 | -59.848 | -60.2097 | -0.004578 | -0.10071 | 62.8464 | -59.967 | 63.0066 | -59.9945 | -60.0815 | -59.9396 | -0.07782 | -0.10529 | 0.013733 | 0.14191 | 59.9854 | -0.21973 | 60.0632 | -0.14191 | 0.022888 | -0.091552 | 0.068665 | -0.004578 | 0.050354 | -0.091553 | 0.027466 | -0.11444 | 0.21973 | 123.0194 | -0.027466 | 122.9736 | 122.9004 | 122.8134 | 122.8226 | 122.8363 | -123.0057 | -122.905 | 122.9416 | 122.9965 | 59.9396 | 59.8892
276.8281 | 123.2254 | -59.935 | 62.9745 | -0.083313 | 0.0015529 | 0.062359 | 0.064882 | -0.0031617 | -0.00099116 | -0.0035397 | -0.012482 | 0.0007392 | 0.065777 | 0.064138 | -0.0033496 | 0.00182 | -0.0025037 | 0.059509 | 62.8555 | -59.9945 | 63.0844 | -59.6237 | -59.7656 | 0.07782 | 0.17395 | 62.8418 | -59.9762 | 63.121 | -59.903 | -60.0174 | -59.903 | -0.059509 | -0.11902 | 0.10986 | 0.31128 | 60.0128 | 0.16937 | 60.0723 | 0.22888 | -0.041198 | -0.13275 | 0.14648 | 0.032044 | 0.032044 | -0.082397 | 0.073242 | -0.041199 | 0.37079 | 123.0789 | 0.073242 | 123.0972 | 122.85 | 122.818 | 122.7905 | 122.7768 | -122.9691 | -122.9507 | 123.0194 | 123.056 | 59.9945 | 60.1089
277.8906 | 123.2254 | -59.9625 | 62.9333 | -0.022278 | 0.0021939 | 0.064068 | 0.064882 | 0.0055969 | -0.0016322 | -0.0043943 | 0.036346 | 0.0007392 | 0.066418 | 0.060293 | -0.0029224 | 0.0041698 | -0.0012219 | -0.041199 | 62.8372 | -60.054 | 62.9791 | -59.8434 | -60.2142 | 0.009155 | 0.004578 | 62.8326 | -59.9808 | 63.0615 | -59.967 | -60.0769 | -59.9396 | -0.091553 | -0.096131 | 0.045776 | 0.11902 | 59.9716 | -0.25177 | 60.0632 | -0.16022 | -0.018311 | -0.10071 | 0.12817 | -0.004578 | 0.022888 | -0.11444 | 0.041199 | -0.09613 | 0.21057 | 123.0331 | 0.013733 | 123.0423 | 122.8912 | 122.8134 | 122.7997 | 122.7951 | -122.9874 | -122.9141 | 122.9416 | 123.024 | 59.9213 | 59.967
278.8281 | 123.3673 | -59.8755 | 62.9837 | -0.037537 | -0.0012241 | 0.063 | 0.065095 | -0.0012391 | -0.0014184 | -0.00012167 | 0.0088807 | 0.0015936 | 0.066845 | 0.059011 | -0.0029224 | 0.0024608 | 5.9726e-05 | 0.054932 | 62.8555 | -60.0449 | 63.1027 | -59.7198 | -60.0861 | 0.10986 | 0.14648 | 62.8647 | -59.9533 | 63.1073 | -59.8846 | -60.022 | -59.8846 | -0.16937 | -0.12817 | 0.11902 | 0.15564 | 59.9854 | -0.21057 | 60.1547 | -0.041199 | -0.07782 | -0.11902 | 0.1236 | -0.009156 | -0.009156 | -0.14649 | 0.068664 | -0.068665 | 0.32501 | 123.1476 | 0.068664 | 123.0606 | 122.9004 | 122.818 | 122.731 | 122.7402 | -123.0286 | -122.937 | 122.9782 | 122.9828 | 59.9304 | 60.022
279.8906 | 123.1247 | -60.0037 | 62.97 | -0.11383 | 0.0021939 | 0.062572 | 0.06595 | -0.00017091 | -0.00035036 | 0.00094633 | -0.10098 | 0.0015936 | 0.066204 | 0.071615 | -0.0018542 | 0.0043836 | -0.0016493 | -0.07782 | 62.8555 | -60.1227 | 62.8876 | -59.9762 | -60.3378 | -0.13275 | -0.14648 | 62.9059 | -60.0174 | 62.9791 | -60.1089 | -60.2142 | -60.0403 | -0.11902 | -0.11444 | -0.082398 | 0.027466 | 59.8709 | -0.33417 | 59.9899 | -0.21515 | -0.013733 | -0.064087 | 0.009155 | -0.10529 | -0.036621 | -0.21057 | -0.022888 | -0.19684 | 0.14648 | 123.0103 | -0.091553 | 122.9965 | 122.9782 | 122.9233 | 122.8592 | 122.9095 | -123.0927 | -122.9874 | 122.8912 | 122.9828 | 59.9258 | 59.8572
280.8281 | 123.1934 | -59.9762 | 62.9425 | -0.1062 | 0.0017667 | 0.064922 | 0.065736 | -0.0031617 | -0.00099116 | -0.0016171 | 0.030243 | 0.0007392 | 0.063 | 0.056875 | -0.00035897 | 0.0024608 | -0.0039991 | -0.041199 | 62.8418 | -60.0632 | 62.9837 | -59.848 | -60.2005 | -0.004578 | 0.018311 | 62.8601 | -59.9716 | 63.0432 | -59.9854 | -60.0952 | -59.9533 | -0.086975 | -0.10071 | 0.041199 | 0.12817 | 59.9716 | -0.2243 | 60.0586 | -0.13733 | 0.004577 | -0.082398 | 0.10071 | -0.009156 | 0.022888 | -0.11902 | 0.018311 | -0.1236 | 0.21515 | 123.0469 | -0.013733 | 123.0148 | 122.905 | 122.8317 | 122.818 | 122.8363 | -123.0057 | -122.9141 | 122.9599 | 123.0194 | 59.935 | 59.9945
281.8906 | 123.23 | -59.9716 | 62.9517 | -0.090943 | 0.0017667 | 0.064709 | 0.065523 | -0.00059811 | -0.00099116 | -0.0022581 | -0.012482 | 0.0020208 | 0.063854 | 0.061148 | -0.001427 | 0.0043836 | -0.0014355 | -0.036621 | 62.8189 | -60.0586 | 63.0066 | -59.8068 | -60.2097 | -0.009155 | -0.013733 | 62.8143 | -59.9899 | 63.0249 | -60.0128 | -60.0998 | -59.935 | -0.086975 | -0.13275 | 0.054932 | 0.16479 | 59.9625 | -0.23804 | 60.0494 | -0.15106 | -0.01831 | -0.13733 | 0.073242 | -0.041198 | 0.036621 | -0.12817 | 0.054931 | -0.10986 | 0.25177 | 123.0652 | -0.022888 | 123.0148 | 122.8775 | 122.8043 | 122.7905 | 122.7859 | -123.0103 | -122.9416 | 122.9782 | 122.9965 | 59.935 | 59.9579
282.8281 | 123.2071 | -59.9533 | 62.9288 | -0.090943 | -0.00058326 | 0.063641 | 0.064882 | -0.00017091 | -0.00056396 | -0.00012167 | -0.018585 | 0.003089 | 0.064068 | 0.064138 | -0.0016406 | 0.00182 | -0.0010083 | -0.045776 | 62.851 | -60.0723 | 62.9654 | -59.8389 | -60.228 | -0.032043 | -0.045776 | 62.8601 | -60.0082 | 63.0341 | -59.9899 | -60.0952 | -59.9533 | -0.11902 | -0.07782 | 0.036621 | 0.11444 | 59.9213 | -0.27466 | 60.0403 | -0.15564 | -0.054932 | -0.068665 | 0.10529 | -0.036621 | 0 | -0.14191 | 0.054932 | -0.086975 | 0.23346 | 123.0377 | 0.018311 | 123.0423 | 122.9233 | 122.8683 | 122.8043 | 122.8134 | -123.0011 | -122.937 | 122.9187 | 122.9874 | 59.9075 | 59.9075
283.8906 | 123.1201 | -60.0082 | 62.9196 | 0.023498 | 0.0011257 | 0.062786 | 0.066591 | 0.0030335 | -0.0012048 | -0.0022581 | -0.07962 | 0.0024482 | 0.06364 | 0.067129 | -0.003136 | 0.0028882 | 0.0015551 | -0.09613 | 62.883 | -60.1135 | 62.9059 | -59.9625 | -60.3058 | -0.09613 | -0.11902 | 62.8647 | -60.0311 | 62.9654 | -60.0723 | -60.1822 | -60.0037 | -0.10529 | -0.036621 | -0.013733 | 0.045777 | 59.9121 | -0.29755 | 60.0174 | -0.19226 | -0.022888 | -0.054932 | 0.045776 | -0.064087 | 0.004578 | -0.17395 | 0.027466 | -0.15106 | 0.15106 | 123.0194 | -0.041199 | 122.9965 | 122.9965 | 122.8958 | 122.8912 | 122.8729 | -123.0331 | -122.9507 | 122.9141 | 122.9736 | 59.9121 | 59.8892
284.8281 | 123.2208 | -59.9625 | 62.9196 | -0.14435 | 0.0011257 | 0.063 | 0.064241 | 0.00068369 | 0.00029044 | -0.00033547 | -0.018585 | 0.0011664 | 0.066418 | 0.065206 | -0.0016406 | 0.0016064 | 0.00070073 | -0.027466 | 62.8326 | -60.0403 | 63.0157 | -59.7977 | -60.1959 | -0.009155 | 0 | 62.8143 | -59.9716 | 63.0524 | -59.9716 | -60.0906 | -59.935 | -0.07782 | -0.086975 | 0.09613 | 0.16479 | 59.9533 | -0.23346 | 60.0311 | -0.15564 | -0.009156 | -0.10529 | 0.13275 | -0.009156 | 0.027465 | -0.12817 | 0.036621 | -0.11902 | 0.24262 | 123.056 | 0 | 123.024 | 122.8729 | 122.7859 | 122.7951 | 122.7768 | -122.9599 | -122.8912 | 122.9782 | 123.0148 | 59.935 | 59.9625
285.8906 | 123.0789 | -60.0128 | 62.9517 | -0.098572 | 0.0011257 | 0.064281 | 0.067445 | 0.0026063 | -0.0018458 | 0.0013735 | -0.091827 | 0.0018072 | 0.064068 | 0.059439 | -0.0027088 | 0.0045972 | -0.0014355 | -0.059509 | 62.8693 | -60.0952 | 62.9059 | -59.9533 | -60.2875 | -0.09613 | -0.12817 | 62.8693 | -60.0082 | 62.9425 | -60.0998 | -60.2463 | -60.0449 | -0.082398 | -0.082397 | -0.045776 | 0.059509 | 59.9167 | -0.27466 | 59.9991 | -0.19226 | 0.004577 | -0.082397 | -0.009155 | -0.086975 | -0.032044 | -0.23346 | -0.036621 | -0.23804 | 0.14191 | 123.0011 | -0.091552 | 122.9507 | 122.9645 | 122.8775 | 122.8821 | 122.8821 | -123.0469 | -122.9599 | 122.9187 | 122.9553 | 59.9533 | 59.8846
286.8281 | 123.2346 | -59.967 | 62.8967 | -0.12146 | 0.00069854 | 0.063641 | 0.066377 | -0.0014527 | -0.0012048 | 0.00030553 | -0.036896 | 0.0026618 | 0.063427 | 0.068197 | -0.0039906 | 0.0043836 | 0.00070073 | -0.041199 | 62.8326 | -60.0723 | 62.9883 | -59.8251 | -60.1959 | -0.027466 | -0.022888 | 62.8418 | -60.0082 | 63.089 | -59.9579 | -60.0723 | -59.9075 | -0.10529 | -0.064087 | 0.091552 | 0.14191 | 59.9396 | -0.22888 | 60.0449 | -0.1236 | -0.041199 | -0.054932 | 0.19226 | 0.009155 | 0.059509 | -0.10529 | 0.10071 | -0.064087 | 0.24719 | 123.0606 | 0.050354 | 123.0972 | 122.905 | 122.85 | 122.7997 | 122.8088 | -122.9691 | -122.905 | 122.9553 | 123.056 | 59.9258 | 59.9442
287.8281 | 123.175 | -59.9579 | 62.9288 | -0.083313 | 0.0015529 | 0.062786 | 0.064668 | -0.0025207 | -0.00099116 | -0.00097627 | -0.015534 | 0.0009528 | 0.063 | 0.06307 | -0.0022816 | 0.0028882 | 0.00091433 | -0.018311 | 62.8464 | -60.0677 | 62.9745 | -59.8068 | -60.2097 | -0.022888 | -0.027466 | 62.8326 | -59.9762 | 63.0249 | -59.9991 | -60.0815 | -59.9442 | -0.10986 | -0.082397 | 0.045776 | 0.15106 | 59.935 | -0.25177 | 60.0449 | -0.14191 | -0.01831 | -0.09613 | 0.09613 | -0.041198 | 0.013733 | -0.1236 | 0.032043 | -0.10529 | 0.26093 | 123.0423 | -0.022888 | 123.0011 | 122.9141 | 122.8088 | 122.8043 | 122.7905 | -122.9965 | -122.905 | 122.9324 | 122.9828 | 59.9396 | 59.9304
288.8906 | 123.1384 | -59.9808 | 62.9745 | -0.35034 | 0.0034757 | 0.059154 | 0.066804 | 0.0023925 | -0.0016322 | 0.00094633 | -0.085724 | 0.0018072 | 0.067058 | 0.063925 | -0.0027088 | 0.0048108 | 0.00027333 | 0.064087 | 62.8601 | -60.0952 | 62.9791 | -59.848 | -60.2325 | 0 | -0.022888 | 62.8693 | -59.967 | 63.0112 | -60.0082 | -60.1501 | -59.9899 | -0.11444 | -0.11444 | 0.004578 | 0.13275 | 59.9808 | -0.25177 | 60.0952 | -0.13733 | 0.013733 | -0.10529 | 0.036621 | -0.027466 | -0.009155 | -0.16937 | -0.022888 | -0.1831 | 0.24719 | 123.0743 | -0.041199 | 122.9782 | 122.9553 | 122.8363 | 122.8409 | 122.85 | -123.0698 | -122.9416 | 122.9599 | 122.9919 | 60.0449 | 59.9579
289.8281 | 123.2208 | -59.9762 | 62.9333 | -0.12146 | 0.00091214 | 0.063854 | 0.065095 | 0.00068369 | -0.00013676 | 0.00073273 | -0.0063781 | 0.0009528 | 0.066204 | 0.056661 | -0.0024952 | 0.0033154 | -0.0029309 | -0.022888 | 62.8281 | -60.0494 | 63.0066 | -59.7885 | -60.1913 | -0.004578 | -0.004578 | 62.8098 | -59.9899 | 63.0524 | -59.9899 | -60.0861 | -59.9213 | -0.073242 | -0.10529 | 0.073242 | 0.18768 | 59.9716 | -0.21515 | 60.0449 | -0.14191 | -0.013733 | -0.1236 | 0.11902 | -0.013733 | 0.054931 | -0.10986 | 0.068664 | -0.096131 | 0.26093 | 123.056 | 0 | 123.0423 | 122.8775 | 122.7997 | 122.8043 | 122.7859 | -122.9828 | -122.9233 | 122.9828 | 123.0286 | 59.9533 | 59.9716
290.8906 | 123.1384 | -59.967 | 62.9562 | -0.068054 | 5.7742e-05 | 0.064068 | 0.06595 | 0.0013245 | -0.00099116 | 0.00030553 | -0.10403 | 0.00138 | 0.066204 | 0.069265 | -0.00057257 | 0.0041698 | 5.9726e-05 | -0.022888 | 62.8876 | -60.0723 | 62.9608 | -59.8801 | -60.2371 | -0.013733 | -0.041199 | 62.8922 | -59.9854 | 62.9974 | -60.0357 | -60.1685 | -60.0082 | -0.10529 | -0.068665 | 0.004577 | 0.086975 | 59.9533 | -0.27008 | 60.0586 | -0.16479 | -0.018311 | -0.064087 | 0.041199 | -0.068665 | -0.041199 | -0.20142 | -0.022888 | -0.1831 | 0.19226 | 123.0331 | -0.050354 | 122.9828 | 122.9599 | 122.8775 | 122.8546 | 122.8592 | -123.0286 | -122.9416 | 122.9279 | 122.9645 | 59.9442 | 59.9258
291.8281 | 123.1567 | -59.9854 | 62.9288 | -0.075684 | 0.0030483 | 0.063427 | 0.064241 | 0.00046989 | 7.6842e-05 | 0.0028689 | -0.06131 | 0.0035162 | 0.065777 | 0.062643 | -0.0024952 | 0.0043836 | -0.0016493 | -0.07782 | 62.8784 | -60.1135 | 62.9059 | -59.9258 | -60.2829 | -0.10529 | -0.11444 | 62.8555 | -60.0082 | 63.0157 | -60.0357 | -60.1685 | -59.9854 | -0.12817 | -0.050354 | -0.022888 | 0.05951 | 59.8801 | -0.29755 | 60.0082 | -0.16937 | -0.022888 | -0.073242 | 0.086975 | -0.050354 | 0 | -0.1831 | 0.022888 | -0.16022 | 0.18768 | 123.0194 | -0.027466 | 123.024 | 122.9919 | 122.8638 | 122.8638 | 122.8409 | -123.0423 | -122.937 | 122.8912 | 123.0011 | 59.9075 | 59.8709
292.8906 | 123.2071 | -59.935 | 62.9883 | -0.022278 | 0.00091214 | 0.063641 | 0.064668 | -0.0018799 | -0.0012048 | 0.00051913 | -0.0063781 | 0.0022346 | 0.063854 | 0.070547 | -0.002068 | 0.003529 | -0.0010083 | 0.036621 | 62.851 | -60.0494 | 63.0524 | -59.7748 | -60.1089 | 0.10986 | 0.1236 | 62.8601 | -59.9579 | 63.0661 | -59.9213 | -60.0266 | -59.9121 | -0.11444 | -0.13733 | 0.064087 | 0.16022 | 60.0449 | -0.17395 | 60.1593 | -0.05951 | -0.022888 | -0.12817 | 0.07782 | 0.013733 | 0.022889 | -0.091552 | 0.045777 | -0.068664 | 0.27466 | 123.1018 | 0.036621 | 123.024 | 122.9004 | 122.818 | 122.7859 | 122.7951 | -123.0377 | -122.9462 | 122.9874 | 123.0011 | 59.9716 | 60.0586
293.8281 | 123.1018 | -59.9899 | 62.9562 | -0.014649 | 0.0011257 | 0.062786 | 0.065309 | 0.00025629 | -0.0041956 | 0.0011599 | -0.070465 | 0.0022346 | 0.066631 | 0.066915 | -0.0027088 | 0.0026746 | -0.0027173 | -0.059509 | 62.8601 | -60.0906 | 62.8922 | -59.9808 | -60.3241 | -0.10529 | -0.16479 | 62.8784 | -60.0311 | 62.9379 | -60.1044 | -60.2234 | -60.0494 | -0.10071 | -0.096131 | -0.064087 | 0.009155 | 59.8846 | -0.33417 | 59.9854 | -0.23346 | -0.041199 | -0.07782 | -0.018311 | -0.11444 | -0.059509 | -0.23346 | -0.01831 | -0.19226 | 0.10986 | 122.9828 | -0.073242 | 122.9691 | 122.9507 | 122.9095 | 122.85 | 122.8683 | -123.0469 | -122.9874 | 122.8821 | 122.9279 | 59.9304 | 59.8251
294.8906 | 123.3032 | -59.9258 | 62.9425 | -0.090943 | 0.0021939 | 0.063213 | 0.06595 | 0.00025629 | -0.0027002 | -0.0041807 | 0.036346 | -0.000329 | 0.065136 | 0.060293 | -0.0018542 | 0.0037426 | 0.0015551 | 0.036621 | 62.8738 | -60.0449 | 63.0386 | -59.7519 | -60.1273 | 0.10986 | 0.14191 | 62.8281 | -59.9396 | 63.1119 | -59.8709 | -59.9762 | -59.8663 | -0.11902 | -0.068665 | 0.09613 | 0.17395 | 60.0357 | -0.20142 | 60.1547 | -0.082397 | -0.013733 | -0.11444 | 0.16937 | 0.054931 | 0.059509 | -0.050354 | 0.073242 | -0.036621 | 0.29297 | 123.0835 | 0.068664 | 123.0515 | 122.9187 | 122.7676 | 122.7997 | 122.7539 | -122.9874 | -122.8821 | 122.9645 | 123.0377 | 59.9625 | 60.0677
295.8281 | 123.1888 | -59.9991 | 62.9837 | -0.052796 | 5.7742e-05 | 0.062786 | 0.066804 | 0.0051697 | -0.0024866 | -0.0022581 | -0.094879 | 0.0018072 | 0.066418 | 0.072897 | -0.0027088 | 0.0056652 | -0.0061353 | -0.09613 | 62.8555 | -60.1364 | 62.8601 | -59.9899 | -60.3287 | -0.10071 | -0.14191 | 62.8464 | -60.0266 | 63.1622 | -60.4294 | -60.3561 | -59.9121 | -0.13733 | -0.12817 | -0.1236 | 0.009155 | 59.8984 | -0.32959 | 60.0357 | -0.19226 | -0.027466 | -0.13733 | 0.17853 | -0.4303 | 0.086975 | -0.35706 | 0.11444 | -0.32959 | 0.14649 | 122.9965 | -0.40283 | 123.1888 | 122.9919 | 122.8729 | 122.8546 | 122.8455 | -123.1201 | -123.0103 | 122.8592 | 123.1613 | 59.903 | 59.8572
296.8906 | 123.2162 | -59.9487 | 62.97 | -0.12909 | 0.0028347 | 0.061291 | 0.064668 | 0.0023925 | 0.0017858 | -0.0016171 | 0.045502 | 0.0005256 | 0.063427 | 0.064565 | -0.0022816 | 0.0045972 | 0.0021961 | 0.059509 | 62.8647 | -60.0311 | 63.0661 | -59.761 | -60.0998 | 0.11444 | 0.12817 | 62.8555 | -59.9625 | 63.0798 | -59.9121 | -60.0311 | -59.903 | -0.082398 | -0.10529 | 0.09613 | 0.18768 | 60.0632 | -0.15106 | 60.1456 | -0.068664 | -0.013733 | -0.11444 | 0.10986 | 0.036621 | 0.045776 | -0.082398 | 0.059509 | -0.068665 | 0.27008 | 123.0972 | 0.050354 | 123.0423 | 122.8958 | 122.818 | 122.8134 | 122.8043 | -123.0011 | -122.9324 | 123.0148 | 123.0286 | 60.0082 | 60.0769
297.8281 | 123.1659 | -59.9716 | 62.9608 | -0.11383 | 0.00027134 | 0.064068 | 0.068086 | -0.00038451 | -0.0027002 | -0.00033547 | -0.064362 | 0.0009528 | 0.066418 | 0.065634 | -0.0024952 | 0.0043836 | -0.00036747 | 0.022888 | 62.8738 | -60.0906 | 62.9883 | -59.8572 | -60.1822 | -0.091553 | 0 | 62.8601 | -59.9762 | 63.0249 | -60.0037 | -60.1181 | -59.9533 | -0.11902 | -0.086975 | 0.027466 | 0.11444 | 59.8801 | -0.21057 | 59.9991 | -0.091553 | -0.004577 | -0.10071 | 0.064087 | -0.032043 | 0.018311 | -0.14648 | 0.022888 | -0.14191 | 0.23346 | 123.0789 | -0.027466 | 123.0011 | 122.9645 | 122.8363 | 122.8455 | 122.8317 | -123.0515 | -122.937 | 122.9599 | 122.9965 | 59.9945 | 59.9716
298.8906 | 123.2574 | -59.9396 | 62.915 | -0.090943 | 0.00027134 | 0.065563 | 0.064668 | 0.00089729 | 0.0015722 | -0.00012167 | -0.046051 | -0.000329 | 0.064068 | 0.059439 | -0.0033496 | 0.0041698 | 0.0030505 | -0.009155 | 62.8143 | -60.0723 | 63.0066 | -59.8206 | -60.2005 | -0.013733 | -0.013733 | 62.8098 | -59.9762 | 62.8967 | -59.7198 | -59.935 | -59.8755 | -0.13275 | -0.10071 | 0.091553 | 0.11902 | 59.9258 | -0.26093 | 60.0586 | -0.12817 | -0.036621 | -0.10529 | -0.01831 | 0.21973 | 0.064087 | 0.004577 | 0.10071 | 0.041198 | 0.25177 | 123.0789 | 0.25635 | 122.8729 | 122.8867 | 122.7859 | 122.7539 | 122.7493 | -122.9874 | -122.8912 | 122.9462 | 122.8363 | 59.9304 | 59.9258
299.8281 | 123.1476 | -59.9899 | 62.97 | -0.052796 | 0.00091214 | 0.064922 | 0.065309 | 0.0019653 | 0.0017858 | -0.00012167 | -0.042999 | 0.0009528 | 0.066418 | 0.064565 | -0.0018542 | 0.0043836 | 0.00027333 | 0.018311 | 62.8876 | -60.0494 | 62.9837 | -59.8297 | -60.2051 | 0.022888 | 0.050354 | 62.883 | -59.9854 | 63.0341 | -60.0037 | -60.228 | -60.0906 | -0.059509 | -0.082398 | 0.013733 | 0.16022 | 60.0128 | -0.21515 | 60.0723 | -0.15564 | 0.004577 | -0.086975 | 0.064087 | -0.013733 | -0.10071 | -0.23804 | -0.10529 | -0.24261 | 0.21973 | 123.0331 | -0.01831 | 123.0194 | 122.937 | 122.8683 | 122.8775 | 122.8729 | -123.0194 | -122.9553 | 122.9736 | 123.024 | 60.0082 | 60.0403
300.8906 | 123.2117 | -59.9396 | 62.9791 | -0.098572 | 0.00048494 | 0.063641 | 0.064027 | -0.0014527 | -0.0052638 | -0.0020443 | 0.014984 | -0.0009698 | 0.066204 | 0.057943 | -0.003136 | 0.0033154 | -0.00015387 | 0.059509 | 62.8876 | -60.0403 | 63.0569 | -59.7519 | -60.1227 | 0.11902 | 0.10986 | 62.883 | -59.9442 | 63.0661 | -59.9396 | -60.0311 | -59.9167 | -0.10071 | -0.091553 | 0.07782 | 0.18768 | 60.0586 | -0.18311 | 60.1593 | -0.082398 | -0.004578 | -0.09613 | 0.086975 | 0 | 0.022888 | -0.091553 | 0.027466 | -0.086975 | 0.28839 | 123.0972 | 0.004578 | 123.0103 | 122.9279 | 122.8271 | 122.8271 | 122.8226 | -123.0194 | -122.9233 | 122.9965 | 123.0057 | 59.9991 | 60.0494
301.8281 | 123.1064 | -59.9716 | 63.0066 | -0.068054 | -0.0010105 | 0.062359 | 0.065736 | -0.0018799 | -0.0035548 | -0.0035397 | -0.036896 | 0.0011664 | 0.06599 | 0.067129 | -0.003136 | 0.0028882 | 0.00070073 | -0.022888 | 62.9242 | -60.054 | 63.1073 | -60.0677 | -60.4248 | 0.041199 | 0.013733 | 62.8922 | -59.9808 | 62.9654 | -60.0128 | -60.141 | -59.9808 | -0.082397 | -0.082398 | 0.10071 | -0.09613 | 60.0128 | -0.45319 | 60.0952 | -0.37079 | -0.009155 | -0.11444 | -0.041199 | -0.041198 | -0.009155 | -0.16937 | 0 | -0.16022 | -0.013733 | 123.1613 | -0.032043 | 122.9462 | 122.9782 | 122.8729 | 122.8958 | 122.8638 | -123.0606 | -122.9874 | 123.0789 | 122.937 | 59.9487 | 59.9854
302.8906 | 123.2803 | -59.9442 | 62.9654 | -0.12146 | 0.00069854 | 0.063427 | 0.065736 | -0.0033753 | -0.00099116 | 9.193e-05 | 0.027191 | 0.0009528 | 0.064495 | 0.059866 | -0.0016406 | 0.00182 | -0.00015387 | 0.004578 | 62.8418 | -60.0403 | 63.0203 | -59.7931 | -60.1456 | 0.064087 | 0.07782 | 62.8189 | -59.9762 | 63.0936 | -59.9213 | -60.022 | -59.8984 | -0.09613 | -0.1236 | 0.054932 | 0.15106 | 60.0082 | -0.20142 | 60.1044 | -0.10529 | -0.032043 | -0.14648 | 0.12817 | 0.022888 | 0.045777 | -0.07782 | 0.07782 | -0.045777 | 0.24719 | 123.0606 | 0.054931 | 123.0698 | 122.8821 | 122.7951 | 122.7859 | 122.7631 | -123.0057 | -122.9416 | 122.9645 | 123.0377 | 59.9487 | 60.022
303.8281 | 123.1705 | -59.9625 | 62.9837 | -0.060425 | 0.0017667 | 0.061932 | 0.065736 | 0.0023925 | -0.0031274 | 0.00073273 | -0.036896 | 0.0003118 | 0.065563 | 0.066488 | -0.0052722 | 0.0024608 | 0.0024097 | 0.041199 | 62.8922 | -60.0632 | 62.9837 | -59.8526 | -60.1868 | 0.036621 | 0.045776 | 62.9059 | -59.9716 | 63.0157 | -59.9945 | -60.1044 | -59.9487 | -0.10071 | -0.091553 | 0 | 0.10986 | 59.9991 | -0.22431 | 60.0998 | -0.1236 | -0.009156 | -0.07782 | 0.032043 | -0.032044 | 0.013733 | -0.14191 | 0.022889 | -0.13275 | 0.21057 | 123.0469 | -0.022888 | 122.9874 | 122.9553 | 122.8775 | 122.8546 | 122.8683 | -123.0469 | -122.9553 | 122.9462 | 122.9782 | 60.0037 | 60.0082
304.8906 | 123.2254 | -59.9442 | 62.9471 | -0.11383 | -0.00079686 | 0.064495 | 0.062959 | 0.0019653 | -0.0012048 | -0.00076267 | -0.0063781 | 0.0028754 | 0.067486 | 0.059866 | -0.0042042 | 0.0028882 | -0.0027173 | -0.036621 | 62.8281 | -60.054 | 63.0203 | -59.8114 | -60.1913 | -0.036621 | -0.009155 | 62.8235 | -59.9991 | 63.089 | -59.967 | -60.0357 | -59.9121 | -0.10986 | -0.11902 | 0.073242 | 0.13275 | 59.9075 | -0.24719 | 60.0174 | -0.13733 | -0.054931 | -0.1236 | 0.14191 | -0.022888 | 0.032044 | -0.091553 | 0.086975 | -0.036622 | 0.24262 | 123.0743 | 0.032043 | 123.0881 | 122.8821 | 122.8226 | 122.7722 | 122.7676 | -123.0011 | -122.9462 | 122.9645 | 123.0331 | 59.9075 | 59.935
305.8281 | 123.1934 | -59.9396 | 63.0478 | -0.022278 | -0.0010105 | 0.062786 | 0.064241 | 0.00025629 | 0.00071784 | -0.0011899 | -0.018585 | 0.003089 | 0.066418 | 0.068411 | -0.0024952 | 0.0028882 | -0.00058107 | -0.004578 | 62.9196 | -60.0677 | 62.9425 | -59.8801 | -60.2097 | 0.041199 | 0.018311 | 62.8876 | -59.9808 | 62.9745 | -60.0266 | -60.141 | -59.9899 | -0.12817 | -0.12817 | -0.10529 | 0.059509 | 59.9808 | -0.27008 | 60.1089 | -0.14191 | -0.041199 | -0.16022 | -0.073243 | -0.086975 | -0.050354 | -0.20142 | -0.009155 | -0.16022 | 0.18768 | 123.0103 | -0.045776 | 122.9553 | 122.9874 | 122.8683 | 122.8592 | 122.8271 | -123.1155 | -123.0286 | 122.8821 | 122.9141 | 59.935 | 59.9579
306.8906 | 123.1842 | -59.9762 | 62.9288 | -0.068054 | -0.00036966 | 0.063427 | 0.065309 | 4.2692e-05 | -0.0035548 | -0.0011899 | -0.046051 | 0.0028754 | 0.065777 | 0.073324 | -0.0024952 | 0.0037426 | 5.9726e-05 | -0.09613 | 62.851 | -60.0952 | 62.9196 | -59.8938 | -60.26 | -0.086975 | -0.082397 | 62.8372 | -59.9991 | 63.0478 | -59.9945 | -60.1044 | -59.9304 | -0.11902 | -0.07782 | -0.009155 | 0.082397 | 59.8892 | -0.28381 | 60.0082 | -0.16479 | -0.022888 | -0.091553 | 0.11902 | -0.018311 | 0.045776 | -0.12817 | 0.068664 | -0.10529 | 0.20142 | 123.0148 | 0.004577 | 123.0469 | 122.9462 | 122.8363 | 122.8271 | 122.8134 | -123.024 | -122.9279 | 122.8958 | 123.024 | 59.8801 | 59.8938
307.8281 | 123.2712 | -59.9533 | 62.9196 | -0.083313 | 0.00048494 | 0.062786 | 0.066804 | 0.0047425 | 0.0034948 | -0.0054623 | 0.030243 | -0.0005426 | 0.061932 | 0.063497 | -0.002068 | 0.0028882 | -0.0016493 | 0.045776 | 62.8555 | -60.0174 | 63.0524 | -59.6832 | -60.26 | 0.091553 | 0.10071 | 62.8464 | -59.9716 | 63.0753 | -59.8938 | -60.0128 | -59.8801 | -0.064087 | -0.064087 | 0.13275 | 0.27008 | 60.0449 | -0.3067 | 60.1089 | -0.24262 | -0.018311 | -0.073242 | 0.15564 | 0.059509 | 0.073242 | -0.059509 | 0.091553 | -0.041198 | 0.33417 | 123.0698 | 0.07782 | 123.0469 | 122.8729 | 122.818 | 122.8088 | 122.7997 | -122.937 | -122.8912 | 123.0057 | 123.0286 | 59.9991 | 60.054
308.8906 | 123.2574 | -59.9487 | 62.9196 | -0.15198 | 0.0026211 | 0.064281 | 0.0636 | 0.0019653 | -0.0016322 | 0.0011599 | -0.021637 | 0.0009528 | 0.066845 | 0.062643 | -0.0012134 | 0.003529 | -0.0025037 | 0 | 62.8281 | -60.0632 | 63.0157 | -59.7977 | -60.1776 | 0 | 0.004578 | 62.8143 | -59.9899 | 63.0707 | -59.9716 | -60.0769 | -59.9121 | -0.11444 | -0.091553 | 0.09613 | 0.15106 | 59.9487 | -0.22888 | 60.0632 | -0.11444 | -0.041199 | -0.10529 | 0.15106 | -0.022889 | 0.036621 | -0.12817 | 0.07782 | -0.086975 | 0.2655 | 123.0789 | 0.01831 | 123.0606 | 122.8912 | 122.8043 | 122.7768 | 122.7631 | -122.9828 | -122.9095 | 122.9645 | 123.0194 | 59.9487 | 59.9533
309.8281 | 123.1659 | -59.9167 | 62.97 | -0.11383 | -0.00079686 | 0.065136 | 0.066163 | -0.0044433 | -0.0027002 | -0.0018307 | 0.014984 | 0.0011664 | 0.065136 | 0.063925 | -0.0029224 | 0.0033154 | -0.0025037 | 0.059509 | 62.883 | -60.0174 | 63.0157 | -59.7748 | -60.1501 | 0.11444 | 0.091553 | 62.8784 | -59.9716 | 63.0386 | -59.9899 | -60.0677 | -59.9258 | -0.10071 | -0.086975 | 0.045776 | 0.14191 | 60.0311 | -0.23346 | 60.1318 | -0.13275 | -0.054932 | -0.091553 | 0.068664 | -0.073242 | -0.009155 | -0.15106 | 0.045777 | -0.09613 | 0.24262 | 123.0331 | -0.01831 | 123.0103 | 122.9004 | 122.85 | 122.7997 | 122.7951 | -122.9874 | -122.9416 | 122.9324 | 122.9553 | 59.9762 | 60.0082
310.8906 | 123.1979 | -59.9579 | 62.9471 | -0.1062 | 0.0019803 | 0.064281 | 0.06595 | 0.0011109 | -0.0014184 | -0.00097627 | -0.0063781 | 0.0005256 | 0.064709 | 0.057089 | -0.0039906 | 0.0037426 | -0.0012219 | -0.041199 | 62.8098 | -60.0494 | 62.9929 | -59.848 | -60.2005 | -0.027466 | -0.022888 | 62.8464 | -59.9808 | 63.0249 | -60.0082 | -60.0952 | -59.9396 | -0.091552 | -0.13733 | 0.045776 | 0.10986 | 59.9304 | -0.24261 | 60.022 | -0.15106 | -0.022888 | -0.10071 | 0.077819 | -0.050354 | 0.018311 | -0.13733 | 0.041199 | -0.11444 | 0.20142 | 123.0423 | -0.027466 | 123.0057 | 122.8592 | 122.8271 | 122.7676 | 122.8043 | -122.9965 | -122.9279 | 122.9507 | 122.9828 | 59.9167 | 59.935
311.8281 | 123.2254 | -59.9487 | 62.9791 | -0.083313 | 0.0019803 | 0.063213 | 0.066163 | 0.0028199 | -0.00077756 | -0.0018307 | -0.0063781 | 9.8198e-05 | 0.06599 | 0.06542 | -0.0029224 | 0.0033154 | -0.0010083 | 0.041199 | 62.8922 | -60.0082 | 63.0157 | -59.8297 | -60.0494 | 0.10529 | 0.13733 | 62.8555 | -59.9396 | 63.0936 | -59.9258 | -60.0174 | -59.8984 | -0.05951 | -0.086975 | 0.036621 | 0.11902 | 60.054 | -0.10071 | 60.1135 | -0.041198 | 0.009155 | -0.1236 | 0.11444 | 0.022888 | 0.050354 | -0.068665 | 0.041199 | -0.07782 | 0.17853 | 123.024 | 0.013733 | 123.0331 | 122.9004 | 122.7951 | 122.8409 | 122.8043 | -122.9874 | -122.9187 | 122.9645 | 123.0423 | 59.9899 | 60.0861
312.8906 | 123.2162 | -59.9808 | 62.9288 | -0.13672 | -0.0014377 | 0.064709 | 0.065309 | 0.00068369 | 0.0017858 | 0.0013735 | -0.0094299 | 0.0020208 | 0.066204 | 0.061361 | -0.0035632 | 0.0022472 | 0.0017687 | -0.018311 | 62.8326 | -60.0494 | 62.9974 | -59.7885 | -60.173 | -0.018311 | 0 | 62.8281 | -59.9899 | 63.0386 | -59.9625 | -60.0769 | -59.9213 | -0.068664 | -0.09613 | 0.068665 | 0.19226 | 59.9625 | -0.19226 | 60.0311 | -0.1236 | -0.009155 | -0.10071 | 0.10986 | 0.018311 | 0.059509 | -0.09613 | 0.068664 | -0.086975 | 0.26093 | 123.0469 | 0.027466 | 123.0286 | 122.8821 | 122.818 | 122.8134 | 122.8088 | -122.9782 | -122.9187 | 122.9782 | 123.0194 | 59.9625 | 59.9808
313.8281 | 123.2437 | -59.9258 | 62.97 | -0.060425 | 0.0013393 | 0.064068 | 0.066163 | 0.0017517 | -0.002273 | -0.00054907 | 0.030243 | -0.0001154 | 0.064922 | 0.062216 | -0.0029224 | 0.00182 | -0.00058107 | 0.050354 | 62.8601 | -60.0494 | 63.0798 | -59.7244 | -60.0723 | 0.10529 | 0.13275 | 62.8372 | -59.9487 | 63.0981 | -59.8801 | -59.9991 | -59.8846 | -0.1236 | -0.10986 | 0.10986 | 0.20142 | 60.0311 | -0.14648 | 60.1547 | -0.022889 | -0.022888 | -0.13275 | 0.12817 | 0.045776 | 0.041198 | -0.073242 | 0.064086 | -0.050354 | 0.32501 | 123.1293 | 0.068664 | 123.0469 | 122.9095 | 122.7859 | 122.7859 | 122.7631 | -123.0194 | -122.9187 | 123.0057 | 123.024 | 59.9762 | 60.0586
314.8906 | 123.1796 | -59.9716 | 62.9654 | -0.075684 | 0.0017667 | 0.062786 | 0.068727 | 0.0019653 | -0.0027002 | 0.0015871 | -0.10403 | 0.0024482 | 0.064281 | 0.063284 | -0.0037768 | 0.008015 | -0.0018629 | -0.10071 | 62.8464 | -60.1089 | 62.8922 | -59.9533 | -60.3195 | -0.11444 | -0.15106 | 62.8738 | -60.0128 | 63.0112 | -59.903 | -60.2554 | -60.054 | -0.13733 | -0.11902 | -0.073242 | 0.018311 | 59.8572 | -0.3479 | 59.9945 | -0.21057 | -0.041198 | -0.091553 | 0.045776 | 0.068665 | -0.082397 | -0.28381 | -0.041199 | -0.24262 | 0.15564 | 123.0011 | 0.10986 | 123.024 | 122.9553 | 122.8867 | 122.818 | 122.8455 | -123.0743 | -122.9782 | 122.8638 | 122.9828 | 59.8709 | 59.8206
315.8281 | 123.2071 | -59.9258 | 62.9471 | -0.1062 | 0.0011257 | 0.064709 | 0.064668 | 0.0015381 | -0.0033412 | -0.0016171 | 0.011932 | 0.00138 | 0.067913 | 0.058798 | -0.0022816 | 0.0020336 | 0.0011279 | -0.032043 | 62.8464 | -60.0677 | 62.9745 | -59.8297 | -60.2142 | 0.018311 | 0 | 62.8555 | -59.9487 | 63.0707 | -59.9396 | -60.0449 | -59.9213 | -0.14191 | -0.10071 | 0.027465 | 0.09613 | 59.9442 | -0.28839 | 60.0861 | -0.14648 | -0.022888 | -0.091553 | 0.1236 | -0.013733 | 0.004577 | -0.11902 | 0.027465 | -0.096131 | 0.23804 | 123.0423 | 0.009155 | 123.0194 | 122.9141 | 122.8043 | 122.7722 | 122.7814 | -123.0148 | -122.8958 | 122.9004 | 122.9965 | 59.8938 | 59.9258
316.8281 | 123.2208 | -59.9625 | 62.9288 | -0.083313 | 0.0013393 | 0.061932 | 0.065736 | 0.0011109 | -0.00077756 | -0.0011899 | -0.0094299 | 0.0003118 | 0.065349 | 0.06307 | -0.002068 | 0.0048108 | 0.0019823 | -0.054932 | 62.8647 | -60.054 | 62.9608 | -59.8618 | -60.2188 | -0.032043 | -0.059509 | 62.8326 | -59.9762 | 63.0386 | -59.9945 | -60.0906 | -59.9487 | -0.091553 | -0.064087 | 0.032043 | 0.10071 | 59.9304 | -0.25635 | 60.022 | -0.1648 | -0.013733 | -0.09613 | 0.10986 | -0.032044 | 0.013733 | -0.12817 | 0.027466 | -0.11444 | 0.19226 | 123.0148 | -0.018311 | 123.0148 | 122.9187 | 122.8088 | 122.8271 | 122.7951 | -122.9828 | -122.905 | 122.9233 | 123.0011 | 59.9075 | 59.903
317.8906 | 123.2208 | -59.9533 | 62.9242 | -0.098572 | -0.00015586 | 0.064709 | 0.066377 | 0.00025629 | -0.0027002 | 0.0022281 | -0.042999 | 0.0005256 | 0.067699 | 0.059011 | -0.0035632 | 0.0037426 | -0.0012219 | -0.009155 | 62.8189 | -60.0632 | 63.0066 | -59.7839 | -60.1822 | -0.022888 | -0.045776 | 62.796 | -60.0174 | 63.1256 | -59.9533 | -60.0952 | -59.8892 | -0.10986 | -0.10529 | 0.082398 | 0.16937 | 59.9304 | -0.22888 | 60.0403 | -0.11902 | -0.064087 | -0.12817 | 0.20142 | 0 | 0.064087 | -0.14191 | 0.12817 | -0.07782 | 0.27923 | 123.0698 | 0.064087 | 123.143 | 122.8821 | 122.8134 | 122.7722 | 122.7493 | -122.9874 | -122.9416 | 122.9599 | 123.0789 | 59.9442 | 59.9075
318.8281 | 123.2025 | -59.9716 | 62.9471 | -0.075684 | 0.0013393 | 0.064068 | 0.065309 | 0.00025629 | 0.00071784 | -0.0024717 | 0.011932 | -0.0005426 | 0.066845 | 0.061361 | -0.0035632 | 0.0026746 | -0.0020765 | -0.045776 | 62.8372 | -60.0632 | 62.97 | -59.8526 | -60.2142 | -0.018311 | -0.054932 | 62.8326 | -59.9991 | 63.0249 | -59.9808 | -60.0861 | -59.9487 | -0.091552 | -0.10986 | 0.022888 | 0.11902 | 59.9533 | -0.24261 | 60.0449 | -0.15106 | -0.027465 | -0.11444 | 0.077819 | -0.009155 | 0.022889 | -0.11444 | 0.050354 | -0.086976 | 0.21057 | 123.0331 | 0.01831 | 123.024 | 122.9004 | 122.8317 | 122.8088 | 122.8043 | -123.0103 | -122.9462 | 122.9416 | 122.9965 | 59.9258 | 59.9167
319.8906 | 123.2346 | -59.9487 | 62.9105 | -0.14435 | 0.0032619 | 0.064068 | 0.065095 | -0.0020935 | 0.00029044 | -0.0011899 | -0.073517 | 0.0007392 | 0.065563 | 0.062002 | -0.0042042 | 0.0031018 | -0.00036747 | -0.054932 | 62.8052 | -60.0815 | 63.002 | -59.8251 | -60.1959 | -0.036621 | -0.027466 | 62.8189 | -60.0037 | 63.0661 | -59.9762 | -60.0769 | -59.903 | -0.13275 | -0.10528 | 0.091553 | 0.1236 | 59.9121 | -0.24719 | 60.0449 | -0.11444 | -0.054932 | -0.091552 | 0.15564 | -0.027466 | 0.045776 | -0.12817 | 0.10071 | -0.073242 | 0.25635 | 123.0835 | 0.027466 | 123.0698 | 122.8867 | 122.8226 | 122.7539 | 122.7676 | -122.9919 | -122.9141 | 122.9507 | 123.0148 | 59.8938 | 59.9213
320.8281 | 123.1842 | -59.9716 | 62.915 | -0.037537 | -0.00079686 | 0.063 | 0.066591 | -0.0025207 | -0.0016322 | -0.00012167 | -0.0033265 | 0.0007392 | 0.064922 | 0.070333 | -0.0061268 | 0.0028882 | 0.0011279 | -0.054932 | 62.8418 | -60.0403 | 62.9837 | -59.8572 | -60.2097 | -0.004578 | -0.054932 | 62.8555 | -59.967 | 63.0157 | -59.9716 | -60.0815 | -59.9533 | -0.068664 | -0.073242 | 0.068665 | 0.11444 | 59.967 | -0.23804 | 60.0357 | -0.16937 | 0.004578 | -0.059509 | 0.10071 | 0 | 0.018311 | -0.10986 | 0.013733 | -0.11444 | 0.18311 | 123.024 | -0.004578 | 122.9828 | 122.8821 | 122.8226 | 122.8134 | 122.8271 | -122.9553 | -122.8821 | 122.9553 | 122.9874 | 59.9167 | 59.9167
321.8906 | 123.1338 | -59.9762 | 62.9608 | -0.068054 | 0.0019803 | 0.063427 | 0.066591 | -0.0035889 | -0.0041956 | -0.00054907 | -0.11319 | 0.0015936 | 0.066418 | 0.066488 | -0.0037768 | 0.003529 | -0.00058107 | -0.041199 | 62.9059 | -60.0723 | 62.9425 | -59.8801 | -60.2554 | -0.059509 | -0.064087 | 62.8738 | -59.9899 | 62.9837 | -60.0586 | -60.173 | -60.0082 | -0.096131 | -0.054931 | -0.01831 | 0.09613 | 59.9167 | -0.27924 | 60.0128 | -0.1831 | -0.013733 | -0.086975 | 0.022889 | -0.082398 | -0.032044 | -0.19684 | -0.018311 | -0.18311 | 0.19226 | 123.0148 | -0.068665 | 122.9736 | 122.9782 | 122.8638 | 122.8821 | 122.85 | -123.0331 | -122.9507 | 122.9187 | 122.9599 | 59.935 | 59.9121
322.8281 | 123.2025 | -59.9533 | 62.9105 | -0.068054 | -0.00015586 | 0.062145 | 0.064668 | -0.00038451 | -0.00056396 | -0.0014035 | -0.027741 | 0.0018072 | 0.064709 | 0.058584 | -0.002068 | 0.0033154 | 0.0024097 | -0.07782 | 62.8098 | -60.0586 | 62.9745 | -59.8526 | -60.2051 | -0.022888 | -0.059509 | 62.851 | -59.9808 | 63.0295 | -59.9899 | -60.0906 | -59.9487 | -0.10529 | -0.10071 | 0.064087 | 0.10071 | 59.9304 | -0.25177 | 60.0357 | -0.14648 | -0.027466 | -0.059509 | 0.11902 | -0.036621 | 0.004578 | -0.13733 | 0.032044 | -0.10986 | 0.20599 | 123.0331 | -0.009155 | 123.0103 | 122.8683 | 122.8317 | 122.7631 | 122.8043 | -122.9691 | -122.8912 | 122.9279 | 122.9828 | 59.8755 | 59.8938
323.9062 | 123.2254 | -59.9579 | 62.9288 | -0.083313 | 0.0021939 | 0.062572 | 0.0636 | -0.0020935 | 0.001145 | 9.193e-05 | 0.027191 | 0.0018072 | 0.064281 | 0.056875 | -0.003136 | 0.0028882 | -0.00058107 | -0.009155 | 62.8555 | -60.0494 | 63.0157 | -59.7931 | -60.1501 | 0.045776 | 0.059509 | 62.8464 | -59.9487 | 63.0798 | -59.9258 | -60.0174 | -59.8938 | -0.091552 | -0.073242 | 0.086975 | 0.1648 | 60.0037 | -0.19226 | 60.0952 | -0.10071 | 0.009156 | -0.082397 | 0.15106 | 0.032044 | 0.064087 | -0.059509 | 0.054931 | -0.068665 | 0.25635 | 123.0652 | 0.022888 | 123.0286 | 122.905 | 122.7951 | 122.8134 | 122.8043 | -122.9782 | -122.8775 | 122.9736 | 123.0377 | 59.9487 | 60.0174
324.8281 | 123.2208 | -59.9442 | 62.9333 | -0.075684 | 0.0036893 | 0.065563 | 0.065095 | -0.0029479 | -0.00056396 | -0.00076267 | -0.033844 | -0.0007562 | 0.065777 | 0.059652 | -0.004845 | 0.0041698 | 0.00048713 | -0.25177 | 62.7869 | -60.0952 | 63.0066 | -59.7931 | -60.1639 | -0.004578 | 0.018311 | 62.8189 | -59.9625 | 63.0661 | -59.9533 | -60.0677 | -59.9167 | -0.15106 | -0.14648 | 0.073242 | 0.15106 | 59.9396 | -0.21973 | 60.0906 | -0.068664 | -0.01831 | -0.11444 | 0.13275 | -0.009155 | 0.027466 | -0.1236 | 0.045776 | -0.10529 | 0.30212 | 123.1018 | 0.009155 | 123.0286 | 122.8821 | 122.7814 | 122.731 | 122.7631 | -123.0286 | -122.8958 | 122.9507 | 123.0103 | 59.6924 | 59.9625
325.8906 | 123.175 | -59.9808 | 62.9333 | -0.13672 | 0.0011257 | 0.064709 | 0.0683 | 0.0032471 | -0.00013676 | -0.0011899 | -0.070465 | 0.0024482 | 0.065349 | 0.063925 | -0.0044178 | 0.0037426 | 0.00027333 | -0.082397 | 62.8326 | -60.0952 | 62.9196 | -59.9075 | -60.2646 | -0.10071 | -0.11444 | 62.8601 | -59.9991 | 63.0157 | -60.022 | -60.1501 | -59.9625 | -0.11444 | -0.10071 | -0.013733 | 0.073242 | 59.8801 | -0.28381 | 59.9945 | -0.16937 | -0.01831 | -0.073243 | 0.082397 | -0.041199 | 0.018311 | -0.16937 | 0.036621 | -0.15106 | 0.18768 | 123.0148 | -0.022889 | 123.0148 | 122.9279 | 122.8592 | 122.8134 | 122.8409 | -123.0286 | -122.9324 | 122.9004 | 122.9965 | 59.8984 | 59.8663
326.8281 | 123.2529 | -59.9396 | 62.9105 | -0.090943 | 0.00091214 | 0.063213 | 0.066804 | 0.0026063 | -0.0014184 | 0.0028689 | -0.046051 | 0.0003118 | 0.064922 | 0.059439 | -0.0044178 | 0.0041698 | -0.00036747 | -0.027466 | 62.8281 | -60.0677 | 63.0157 | -59.8022 | -60.1776 | -0.032043 | -0.013733 | 62.8098 | -59.9762 | 63.1393 | -59.8251 | -60.0723 | -59.9121 | -0.12817 | -0.082397 | 0.10529 | 0.13733 | 59.9075 | -0.23804 | 60.0357 | -0.10986 | -0.036621 | -0.10071 | 0.22888 | 0.11444 | 0.027466 | -0.13275 | 0.064087 | -0.096131 | 0.2655 | 123.0835 | 0.15106 | 123.1155 | 122.8958 | 122.7859 | 122.7676 | 122.7493 | -122.9782 | -122.8867 | 122.9553 | 123.0789 | 59.9121 | 59.9258
327.8906 | 123.1522 | -59.9533 | 62.9974 | -0.083313 | -0.00058326 | 0.063 | 0.065523 | 0.0015381 | -0.0037684 | -0.00076267 | -0.064362 | 9.8198e-05 | 0.066204 | 0.06307 | -0.0029224 | 0.0024608 | 0.00027333 | 0.009155 | 62.9013 | -60.0998 | 62.9471 | -59.8801 | -60.2051 | 0.013733 | -0.013733 | 62.8922 | -59.967 | 63.0249 | -59.9808 | -60.1181 | -59.9762 | -0.14648 | -0.096131 | -0.050354 | 0.073242 | 59.967 | -0.25177 | 60.1135 | -0.10529 | -0.013733 | -0.10529 | 0.027465 | -0.027466 | -0.022888 | -0.16479 | -0.009155 | -0.15106 | 0.21973 | 123.0469 | -0.013733 | 122.9919 | 123.0011 | 122.8592 | 122.8546 | 122.8455 | -123.0972 | -122.9645 | 122.9004 | 122.9782 | 59.9625 | 59.9396
328.8438 | 123.1247 | -59.9762 | 62.9837 | -0.037537 | 0.0011257 | 0.063854 | 0.064454 | 0.0030335 | -0.00013676 | -0.0024717 | 0.0058289 | 0.0035162 | 0.065563 | 0.060079 | -0.0037768 | 0.0022472 | -0.0012219 | 0.045776 | 62.8876 | -60.0494 | 62.9883 | -59.8206 | -60.1593 | 0.068665 | 0.027466 | 62.8967 | -59.967 | 62.9837 | -60.0128 | -60.1089 | -59.9854 | -0.073242 | -0.096131 | 0.004577 | 0.15564 | 60.0449 | -0.18311 | 60.1181 | -0.10986 | 0.009155 | -0.086975 | 0 | -0.036621 | -0.009156 | -0.13275 | -0.018311 | -0.14191 | 0.22888 | 123.0377 | -0.045776 | 122.9507 | 122.937 | 122.8638 | 122.8638 | 122.8729 | -123.0331 | -122.9507 | 122.9645 | 122.9599 | 60.022 | 60.0037
329.8906 | 123.1613 | -59.9762 | 62.9379 | -0.1062 | 5.7742e-05 | 0.062359 | 0.066163 | 0.00089729 | -0.0029138 | -0.00076267 | -0.067413 | 0.0018072 | 0.066845 | 0.066488 | -0.0037768 | 0.0060924 | 0.00091433 | -0.082397 | 62.8601 | -60.0815 | 62.915 | -59.9075 | -60.2737 | -0.10071 | -0.11444 | 62.851 | -60.0174 | 62.9883 | -60.0357 | -60.1456 | -59.9625 | -0.10529 | -0.07782 | -0.022888 | 0.068664 | 59.8755 | -0.29755 | 59.9808 | -0.19226 | -0.041199 | -0.086975 | 0.050354 | -0.05951 | 0.013733 | -0.16937 | 0.054932 | -0.12817 | 0.17395 | 122.9965 | -0.018311 | 123.0057 | 122.9416 | 122.8683 | 122.8363 | 122.8271 | -123.0194 | -122.9553 | 122.8912 | 122.9645 | 59.8938 | 59.8618
330.8281 | 123.2208 | -59.9579 | 62.8967 | -0.13672 | 0.00069854 | 0.063 | 0.063814 | 0.00068369 | -0.002273 | -0.0024717 | -0.027741 | 0.0005256 | 0.065777 | 0.062002 | -0.0033496 | 0.0028882 | 0.00070073 | -0.032043 | 62.8326 | -60.0449 | 63.0157 | -59.7748 | -60.1776 | -0.018311 | 0.009155 | 62.8235 | -59.9808 | 63.0661 | -59.9716 | -60.054 | -59.9167 | -0.086975 | -0.064087 | 0.11902 | 0.18311 | 59.9396 | -0.21973 | 60.0266 | -0.13275 | -0.022888 | -0.073243 | 0.16937 | -0.013733 | 0.041199 | -0.09613 | 0.064087 | -0.073242 | 0.27008 | 123.0606 | 0.009155 | 123.0469 | 122.8775 | 122.8043 | 122.7905 | 122.7814 | -122.9416 | -122.8775 | 122.9736 | 123.024 | 59.9258 | 59.967
331.8906 | 123.2208 | -59.9487 | 62.9333 | -0.052796 | 0.0015529 | 0.063427 | 0.067445 | -0.0016663 | -0.00013676 | -0.00033547 | -0.070465 | 0.0015936 | 0.065136 | 0.067343 | -0.0033496 | 0.0058788 | 0.00070073 | -0.073242 | 62.8372 | -60.1135 | 62.9471 | -59.8846 | -60.2554 | -0.068665 | -0.086975 | 62.8418 | -60.0037 | 63.0524 | -59.9899 | -60.1044 | -59.9121 | -0.1648 | -0.096131 | 0.013733 | 0.064086 | 59.8801 | -0.3067 | 60.0449 | -0.14191 | -0.054932 | -0.091553 | 0.11902 | -0.041199 | 0.036621 | -0.15564 | 0.091553 | -0.10071 | 0.22888 | 123.0606 | 0.013733 | 123.056 | 122.9507 | 122.8455 | 122.7859 | 122.7905 | -123.0469 | -122.937 | 122.8958 | 123.0011 | 59.8755 | 59.8618
332.8281 | 123.2391 | -59.967 | 62.8967 | -0.13672 | -0.00015586 | 0.063213 | 0.06595 | -0.0010253 | -0.00035036 | 0.0026553 | -0.021637 | -0.0001154 | 0.064922 | 0.064565 | -0.0016406 | 0.0045972 | 0.00027333 | -0.050354 | 62.8052 | -60.0723 | 62.9837 | -59.8389 | -60.2829 | -0.054932 | -0.036621 | 62.8326 | -59.9899 | 63.0707 | -59.9762 | -60.0632 | -59.9167 | -0.10529 | -0.091553 | 0.086975 | 0.12817 | 59.9121 | -0.31586 | 60.0174 | -0.21057 | -0.022888 | -0.064087 | 0.17395 | -0.009155 | 0.050354 | -0.09613 | 0.073242 | -0.073242 | 0.23346 | 123.056 | 0.013733 | 123.0606 | 122.8775 | 122.8226 | 122.7722 | 122.7997 | -122.9691 | -122.8867 | 122.9507 | 123.0377 | 59.9167 | 59.9304
333.9062 | 123.2758 | -59.9442 | 62.9288 | -0.068054 | 0.0011257 | 0.062359 | 0.064241 | -0.0025207 | -0.002273 | 0.00051913 | 0.024139 | 0.0009528 | 0.064495 | 0.060079 | -0.0050586 | 0.00096564 | -0.0039991 | 0.009155 | 62.8738 | -60.0403 | 63.0112 | -59.8022 | -60.1364 | 0.068665 | 0.073242 | 62.8464 | -59.9625 | 63.0936 | -59.9075 | -60.0082 | -59.8892 | -0.09613 | -0.054932 | 0.082397 | 0.14191 | 60.0128 | -0.19226 | 60.1089 | -0.096131 | -0.01831 | -0.082397 | 0.16479 | 0.036621 | 0.054932 | -0.064087 | 0.073242 | -0.045777 | 0.23804 | 123.0515 | 0.054931 | 123.056 | 122.9141 | 122.8088 | 122.818 | 122.7905 | -122.9691 | -122.8912 | 122.9553 | 123.0377 | 59.9533 | 60.0174
334.8281 | 123.1842 | -59.9945 | 62.9242 | -0.060425 | 0.0013393 | 0.062145 | 0.064882 | 0.0019653 | -0.0016322 | -0.00054907 | -0.06131 | 0.0020208 | 0.067058 | 0.060934 | -0.003136 | 0.0041698 | -0.0046399 | -0.064087 | 62.8555 | -60.0815 | 62.9105 | -59.8892 | -60.2783 | -0.086975 | -0.10529 | 62.851 | -60.0128 | 63.0432 | -59.9945 | -60.0998 | -59.9304 | -0.086975 | -0.068664 | -0.013733 | 0.10529 | 59.9075 | -0.28381 | 59.9945 | -0.19684 | -0.01831 | -0.073242 | 0.11902 | 0 | 0.064087 | -0.10529 | 0.082397 | -0.086975 | 0.19226 | 122.9919 | 0.01831 | 123.056 | 122.937 | 122.8638 | 122.85 | 122.8455 | -123.0057 | -122.937 | 122.905 | 123.0377 | 59.9304 | 59.8892
335.8906 | 123.1522 | -59.9625 | 62.9929 | -0.068054 | 0.0011257 | 0.062145 | 0.065736 | 0.0028199 | 0.00071784 | 0.00073273 | -0.046051 | 0.0022346 | 0.067272 | 0.067556 | -0.0035632 | 0.0041698 | -0.00036747 | -0.009155 | 62.9105 | -60.0677 | 62.9425 | -59.8801 | -60.2188 | 0.027466 | -0.018311 | 62.9105 | -59.9854 | 63.0112 | -59.9854 | -60.0952 | -59.9625 | -0.10529 | -0.082398 | -0.050354 | 0.082397 | 59.9899 | -0.25635 | 60.0952 | -0.15106 | -0.022889 | -0.082398 | 0.01831 | -0.022889 | 0 | -0.13275 | 0.022889 | -0.10986 | 0.18768 | 123.0103 | 0 | 122.9965 | 122.9782 | 122.8958 | 122.8729 | 122.8729 | -123.0606 | -122.9782 | 122.905 | 122.9736 | 59.9533 | 59.9442
336.8281 | 123.2391 | -59.9716 | 62.9059 | -0.098572 | 0.0013393 | 0.063 | 0.065095 | 0.0026063 | -0.0016322 | -0.00033547 | -0.049103 | 0.0015936 | 0.066845 | 0.061575 | -0.001427 | 0.0026746 | 0.0032641 | -0.082397 | 62.8372 | -60.0769 | 62.97 | -59.8297 | -60.2005 | -0.041199 | -0.050354 | 62.8189 | -60.0266 | 63.0569 | -59.9625 | -60.0815 | -59.903 | -0.10529 | -0.068665 | 0.064087 | 0.14191 | 59.9304 | -0.22888 | 60.0357 | -0.1236 | -0.054931 | -0.086975 | 0.15106 | 0.009156 | 0.068665 | -0.10986 | 0.1236 | -0.054932 | 0.24719 | 123.0469 | 0.064087 | 123.0835 | 122.9141 | 122.8455 | 122.8088 | 122.7905 | -122.9828 | -122.9324 | 122.9416 | 123.0286 | 59.8892 | 59.9213
337.8906 | 123.1567 | -59.9762 | 62.9654 | -0.075684 | 0.00048494 | 0.063213 | 0.067232 | -0.0025207 | -0.00077756 | -0.00076267 | -0.088776 | 0.0015936 | 0.066845 | 0.060293 | -0.00099977 | 0.0026746 | -0.0031445 | 0.004578 | 62.9059 | -60.0677 | 62.9929 | -59.8526 | -60.2005 | 0.013733 | 0.027466 | 62.8784 | -59.9899 | 63.0295 | -59.9854 | -60.0998 | -59.9442 | -0.091553 | -0.059509 | 0.027466 | 0.1236 | 59.9899 | -0.2243 | 60.0815 | -0.13275 | -0.013733 | -0.086975 | 0.064087 | -0.009156 | 0.032043 | -0.1236 | 0.045776 | -0.10986 | 0.21515 | 123.0606 | 0.004577 | 123.0194 | 122.9736 | 122.8683 | 122.8821 | 122.8546 | -123.0331 | -122.9553 | 122.9691 | 123.0057 | 59.9808 | 60.0037
338.8438 | 123.1247 | -59.9487 | 62.9791 | -0.045166 | 0.00048494 | 0.062359 | 0.064882 | -0.0016663 | -0.00099116 | -0.00012167 | -0.091827 | 0.0018072 | 0.067486 | 0.058798 | -0.002068 | 0.0039562 | -0.0027173 | -0.009155 | 62.9059 | -60.0494 | 62.9242 | -59.9258 | -59.8709 | 0.073242 | 0.018311 | 62.9013 | -60.022 | 62.9974 | -60.0128 | -60.1456 | -59.9716 | -0.10071 | -0.073242 | -0.054932 | 0.022888 | 60.022 | 0.077819 | 60.1227 | 0.17853 | -0.073243 | -0.07782 | 0.018311 | -0.064087 | -0.022889 | -0.19684 | 0.050354 | -0.1236 | 0.1236 | 122.9736 | 0.009156 | 123.0194 | 122.9553 | 122.9233 | 122.8546 | 122.85 | -123.0286 | -123.0011 | 122.8729 | 122.9462 | 59.9396 | 59.967
339.8906 | 123.111 | -60.0082 | 62.9608 | -0.083313 | 0.0015529 | 0.063 | 0.0683 | 0.00046989 | -0.00056396 | 0.00051913 | -0.06131 | 0.0033026 | 0.065349 | 0.062856 | -0.0033496 | 0.0031018 | 0.00027333 | -0.073242 | 62.8601 | -60.0998 | 62.9013 | -59.9579 | -60.3287 | -0.10986 | -0.20142 | 62.8647 | -60.0403 | 62.9288 | -60.0861 | -60.1913 | -60.0128 | -0.091552 | -0.10071 | -0.059509 | 0.050354 | 59.8984 | -0.32043 | 59.9899 | -0.22888 | -0.032043 | -0.09613 | -0.032043 | -0.07782 | -0.004577 | -0.1831 | 0.027466 | -0.15106 | 0.14191 | 123.0011 | -0.045777 | 122.9691 | 122.9599 | 122.905 | 122.8683 | 122.8729 | -123.0606 | -123.0011 | 122.9095 | 122.937 | 59.935 | 59.8068
340.8281 | 123.143 | -59.9945 | 62.9471 | -0.014649 | 0.0024075 | 0.063 | 0.066804 | 0.0028199 | 0.00029044 | -0.0020443 | -0.052155 | 0.0020208 | 0.068127 | 0.064352 | -0.0029224 | 0.0033154 | -0.00036747 | -0.09613 | 62.8738 | -60.1135 | 62.883 | -59.9213 | -60.3012 | -0.091553 | -0.13733 | 62.8326 | -60.0266 | 62.97 | -60.0449 | -60.1868 | -59.9899 | -0.11902 | -0.073243 | -0.064087 | 0.073242 | 59.903 | -0.3067 | 60.022 | -0.18768 | -0.032043 | -0.11444 | 0.022888 | -0.050354 | 0.004578 | -0.19226 | 0.036621 | -0.16022 | 0.19226 | 122.9965 | -0.018311 | 122.9965 | 122.9874 | 122.8592 | 122.8683 | 122.8271 | -123.0606 | -122.9736 | 122.8775 | 122.9645 | 59.8984 | 59.8572
341.8906 | 123.2162 | -59.9762 | 62.9379 | -0.060425 | 0.00069854 | 0.062572 | 0.065095 | -0.0033753 | -0.0031274 | 0.0013735 | -0.055206 | 0.0015936 | 0.067486 | 0.063711 | -0.0037768 | 0.0041698 | 0.0032641 | 0.004578 | 62.8738 | -60.0632 | 62.9974 | -59.8297 | -60.2097 | 0.027466 | 0.022888 | 62.883 | -59.9991 | 63.0112 | -59.9808 | -60.1044 | -59.9579 | -0.086975 | -0.064087 | 0.05951 | 0.14648 | 60.0037 | -0.23346 | 60.0906 | -0.14649 | -0.022888 | -0.054931 | 0.073242 | -0.004578 | 0.01831 | -0.12817 | 0.041198 | -0.10529 | 0.23346 | 123.0606 | 0.01831 | 123.0103 | 122.937 | 122.8821 | 122.85 | 122.8592 | -123.0011 | -122.937 | 122.9736 | 122.9874 | 59.9808 | 59.9991
342.8281 | 123.1247 | -59.9945 | 62.9517 | -0.045166 | 0.00069854 | 0.063213 | 0.0683 | 0.0021789 | 0.0017858 | -0.00076267 | -0.0094299 | 0.0037298 | 0.066631 | 0.062216 | -0.003136 | 0.0031018 | -0.0016493 | -0.09613 | 62.8464 | -60.0998 | 62.7274 | -59.6237 | -60.173 | -0.13733 | -0.1831 | 62.8647 | -59.9899 | 62.9517 | -60.0815 | -60.2051 | -60.022 | -0.10529 | -0.10528 | -0.2243 | 0.37079 | 59.8572 | -0.17853 | 59.9625 | -0.073243 | 0.004578 | -0.086975 | 0 | -0.086975 | -0.027466 | -0.21057 | -0.032044 | -0.21515 | 0.47607 | 122.8271 | -0.091553 | 122.9416 | 122.9462 | 122.8546 | 122.8409 | 122.8592 | -123.0515 | -122.9416 | 122.7219 | 122.9462 | 59.8984 | 59.8114
343.8906 | 123.2529 | -59.9442 | 62.9333 | -0.068054 | -0.0016513 | 0.063641 | 0.061891 | 0.00089729 | -0.00035036 | -0.0026853 | 0.048553 | 0.00138 | 0.06599 | 0.059439 | -0.0033496 | 0.0031018 | -0.0022901 | -0.009155 | 62.8418 | -60.0494 | 63.0157 | -59.7839 | -60.1364 | 0.068665 | 0.068665 | 62.8464 | -59.967 | 63.0936 | -59.9213 | -60.0037 | -59.8984 | -0.10529 | -0.091553 | 0.082397 | 0.16022 | 60.0128 | -0.19226 | 60.1181 | -0.086976 | -0.022888 | -0.086975 | 0.16022 | 0.022888 | 0.045777 | -0.059509 | 0.068665 | -0.036621 | 0.2655 | 123.0652 | 0.045776 | 123.0606 | 122.8912 | 122.8134 | 122.7859 | 122.7905 | -122.9828 | -122.9004 | 122.9599 | 123.0377 | 59.935 | 60.0128
344.8281 | 123.2254 | -59.9533 | 62.8922 | -0.083313 | 0.0013393 | 0.061077 | 0.065309 | 0.0032471 | 0.00029044 | 0.00051913 | -0.030792 | 0.0022346 | 0.064709 | 0.060293 | -0.0061268 | 0.0048108 | -0.0010083 | -0.073242 | 62.8281 | -60.1135 | 62.9471 | -59.8663 | -60.228 | -0.064087 | -0.059509 | 62.8189 | -59.9854 | 63.0478 | -59.9808 | -60.0723 | -59.903 | -0.16022 | -0.064087 | 0.054932 | 0.086975 | 59.8892 | -0.27466 | 60.0494 | -0.11444 | -0.032044 | -0.073242 | 0.15564 | -0.027466 | 0.050354 | -0.11902 | 0.082398 | -0.086975 | 0.24719 | 123.0606 | 0.004578 | 123.0331 | 122.9416 | 122.8043 | 122.7814 | 122.7722 | -123.0057 | -122.8775 | 122.9004 | 123.0011 | 59.8801 | 59.8938
345.8906 | 123.1659 | -59.9808 | 62.9883 | -0.022278 | 0.0011257 | 0.06065 | 0.068086 | 0.0030335 | -0.0012048 | -0.0011899 | -0.030792 | 0.0009528 | 0.064281 | 0.061148 | -0.0054858 | 0.0022472 | -0.0010083 | 0.013733 | 62.9013 | -60.0632 | 62.9471 | -59.8984 | -60.2005 | 0.018311 | 0.004578 | 62.9105 | -59.9579 | 63.0203 | -59.9899 | -60.1089 | -59.9533 | -0.082397 | -0.086975 | -0.041198 | 0.082398 | 59.9991 | -0.21973 | 60.0815 | -0.13733 | 0.022888 | -0.07782 | 0.032044 | -0.009155 | 0.027466 | -0.12817 | 0.004578 | -0.15106 | 0.16479 | 123.0103 | -0.032043 | 122.9782 | 122.9645 | 122.8683 | 122.8821 | 122.8912 | -123.0515 | -122.9462 | 122.9279 | 123.0011 | 59.9945 | 59.9854
346.8281 | 123.1155 | -59.9945 | 62.9562 | -0.090943 | -0.00036966 | 0.064495 | 0.065736 | 0.00089729 | -0.00077756 | 9.193e-05 | 0.079071 | 0.0015936 | 0.068554 | 0.063925 | -0.00057257 | 0.0031018 | -0.0027173 | -0.07782 | 62.8647 | -60.0998 | 62.8922 | -59.9533 | -60.6308 | -0.33875 | -0.17853 | 62.8693 | -60.022 | 62.9837 | -60.1044 | -60.1868 | -59.9899 | -0.10529 | -0.091553 | -0.064087 | 0.041199 | 59.6558 | -0.63629 | 59.761 | -0.53101 | -0.027466 | -0.086975 | 0.027466 | -0.10986 | 0.004578 | -0.19226 | 0.032044 | -0.16479 | 0.14648 | 122.9919 | -0.082397 | 123.0057 | 122.9645 | 122.8912 | 122.8592 | 122.8638 | -123.056 | -122.9782 | 122.8867 | 122.9782 | 59.9167 | 59.816
347.8906 | 123.1064 | -60.0037 | 62.9562 | -0.12146 | 0.0013393 | 0.064495 | 0.067659 | 0.0013245 | -0.00056396 | 9.193e-05 | -0.064362 | -0.0005426 | 0.066845 | 0.065847 | -0.003136 | 0.0045972 | -0.00015387 | -0.059509 | 62.883 | -60.0815 | 62.8876 | -59.9716 | -60.3149 | -0.10071 | -0.15106 | 62.851 | -60.0037 | 62.9288 | -60.1089 | -60.2051 | -60.0311 | -0.07782 | -0.073242 | -0.068665 | 0.032043 | 59.903 | -0.31128 | 59.9808 | -0.23346 | 0 | -0.10529 | -0.027466 | -0.10529 | -0.027466 | -0.20142 | -0.027466 | -0.20142 | 0.10986 | 122.9691 | -0.10529 | 122.9324 | 122.9645 | 122.8546 | 122.8867 | 122.8546 | -123.0377 | -122.9599 | 122.8912 | 122.9324 | 59.9442 | 59.8526
348.8281 | 123.1064 | -60.0174 | 62.9288 | -0.11383 | 0.0013393 | 0.063427 | 0.067872 | 0.0017517 | -0.0012048 | -0.00054907 | -0.042999 | 0.0011664 | 0.067058 | 0.06542 | -0.0042042 | 0.0048108 | 0.0043323 | -0.086975 | 62.8738 | -60.0952 | 62.8555 | -59.9854 | -60.3195 | -0.09613 | -0.16479 | 62.8601 | -60.0174 | 62.9562 | -60.1089 | -60.228 | -60.0266 | -0.07782 | -0.054932 | -0.073242 | 0.032043 | 59.9213 | -0.30212 | 59.9991 | -0.2243 | 0 | -0.068665 | 0.027466 | -0.091553 | -0.009155 | -0.21057 | -0.009155 | -0.21057 | 0.10986 | 122.9507 | -0.091553 | 122.9736 | 122.9691 | 122.8775 | 122.8912 | 122.8775 | -123.024 | -122.9462 | 122.8729 | 122.9736 | 59.9304 | 59.8526
349.8906 | 123.1064 | -59.9716 | 63.0112 | -0.083313 | 0.00091214 | 0.065136 | 0.063173 | 0.0015381 | -0.00013676 | -0.0033261 | 0.024139 | 0.0026618 | 0.067486 | 0.064138 | -0.0033496 | 0.00096564 | 0.0015551 | 0.032043 | 62.8876 | -60.0311 | 62.9425 | -59.8389 | -60.1822 | 0.032043 | 0.018311 | 62.9059 | -59.9854 | 62.97 | -60.022 | -60.1181 | -59.9945 | -0.059509 | -0.1236 | -0.068664 | 0.13275 | 60.0037 | -0.21057 | 60.0632 | -0.15106 | -0.013733 | -0.10529 | -0.041198 | -0.050354 | -0.022888 | -0.14648 | -0.009155 | -0.13275 | 0.19226 | 122.9736 | -0.036621 | 122.9553 | 122.9187 | 122.8912 | 122.8592 | 122.8775 | -123.0423 | -122.9965 | 122.9141 | 122.9416 | 60.0037 | 59.9899
350.8281 | 123.1155 | -59.9899 | 62.9562 | -0.1062 | 0.0024075 | 0.061291 | 0.067445 | 0.0013245 | -0.00077756 | -0.0014035 | -0.042999 | 0.0009528 | 0.068127 | 0.066915 | -0.0046314 | 0.0041698 | -0.0012219 | -0.07782 | 62.8418 | -60.0998 | 62.8922 | -59.9579 | -60.3241 | -0.10529 | -0.44403 | 62.796 | -60.054 | 62.9517 | -60.0632 | -60.1685 | -60.0037 | -0.10986 | -0.11444 | -0.064087 | 0.032043 | 59.8846 | -0.33417 | 59.9945 | -0.22431 | -0.064087 | -0.16022 | -0.004578 | -0.073242 | -0.013733 | -0.17853 | 0.050354 | -0.11444 | 0.14191 | 122.9919 | -0.009155 | 123.0057 | 122.9416 | 122.85 | 122.8317 | 122.7859 | -123.056 | -123.0103 | 122.8821 | 122.9416 | 59.9121 | 59.5459
351.8906 | 123.111 | -59.9442 | 63.002 | -0.083313 | 0.00069854 | 0.062786 | 0.065523 | -0.0020935 | -0.0029138 | -0.0024717 | 0.0088807 | 0.0026618 | 0.065563 | 0.060934 | -0.0024952 | 0.003529 | 0.0039049 | -0.022888 | 62.915 | -60.0494 | 62.9288 | -59.8709 | -60.228 | 0.041199 | 0 | 62.9105 | -59.9854 | 62.9745 | -60.0311 | -60.141 | -59.9991 | -0.10529 | -0.086975 | -0.073242 | 0.073242 | 59.9854 | -0.28381 | 60.0906 | -0.17853 | -0.041199 | -0.091553 | -0.027466 | -0.086975 | -0.054931 | -0.19684 | -0.013732 | -0.15564 | 0.17853 | 122.9782 | -0.045776 | 122.9599 | 122.9645 | 122.8958 | 122.8592 | 122.8546 | -123.0515 | -122.9874 | 122.8729 | 122.9187 | 59.9213 | 59.9442
352.8281 | 123.0789 | -59.9716 | 62.9608 | -0.090943 | 0.0019803 | 0.064709 | 0.066163 | -0.00017091 | -0.0012048 | -0.0018307 | -0.058258 | 0.0015936 | 0.065563 | 0.061575 | -0.0024952 | 0.0058788 | -0.0016493 | -0.068665 | 62.8784 | -60.1044 | 62.8693 | -59.9533 | -60.3104 | -0.11902 | -0.17395 | 62.883 | -60.0082 | 62.9288 | -60.1135 | -60.2005 | -60.0266 | -0.13275 | -0.082397 | -0.091552 | 0.018311 | 59.8526 | -0.33875 | 59.9854 | -0.20599 | -0.036621 | -0.077819 | -0.032043 | -0.14191 | -0.054931 | -0.22888 | -0.01831 | -0.19226 | 0.15106 | 122.9736 | -0.10529 | 122.937 | 122.9828 | 122.8912 | 122.85 | 122.8546 | -123.0652 | -122.9691 | 122.8409 | 122.9004 | 59.903 | 59.7977
353.8906 | 123.1201 | -59.9625 | 62.9929 | -0.083313 | -0.00015586 | 0.061077 | 0.065523 | 4.2692e-05 | -0.0012048 | -0.00076267 | -0.0063781 | 9.8198e-05 | 0.065777 | 0.059225 | -0.0022816 | 0.0024608 | -0.0016493 | 0.036621 | 62.8967 | -60.0174 | 62.9745 | -59.8114 | -60.1639 | 0.064087 | 0.050354 | 62.9013 | -59.9625 | 62.9883 | -60.0037 | -60.1089 | -59.9808 | -0.054932 | -0.09613 | -0.018311 | 0.15106 | 60.0266 | -0.20142 | 60.0815 | -0.14648 | 0 | -0.091553 | -0.004578 | -0.041199 | -0.018311 | -0.14648 | -0.018311 | -0.14648 | 0.20599 | 122.9919 | -0.041199 | 122.9507 | 122.9141 | 122.8638 | 122.8592 | 122.8638 | -123.0103 | -122.9553 | 122.937 | 122.9507 | 59.9991 | 60.0128
354.8281 | 123.0789 | -59.9899 | 62.9837 | -0.060425 | 0.00027134 | 0.064068 | 0.067445 | 0.0038879 | 7.6842e-05 | -0.00076267 | -0.064362 | 0.0009528 | 0.066418 | 0.07012 | -0.003136 | 0.0043836 | -0.0042127 | -0.041199 | 62.8784 | -60.1089 | 62.9242 | -59.8938 | -60.2737 | -0.068665 | -0.07782 | 62.8555 | -59.9762 | 62.9517 | -60.0677 | -60.1822 | -60.0128 | -0.11902 | -0.10529 | -0.05951 | 0.09613 | 59.9213 | -0.28381 | 60.0403 | -0.1648 | 0.013733 | -0.12817 | -0.032044 | -0.07782 | -0.022888 | -0.19226 | -0.036621 | -0.20599 | 0.21515 | 123.0331 | -0.091553 | 122.9279 | 122.9874 | 122.8317 | 122.8683 | 122.8455 | -123.0927 | -122.9599 | 122.9141 | 122.9416 | 59.9487 | 59.9121
355.8906 | 123.1659 | -59.9716 | 62.9517 | -0.060425 | 0.0028347 | 0.063213 | 0.066591 | 0.0026063 | 0.00071784 | 0.00073273 | -0.046051 | 0.0020208 | 0.067486 | 0.058798 | -0.0016406 | 0.0045972 | -0.00015387 | 0.032043 | 62.8876 | -60.0769 | 62.9745 | -59.8206 | -60.2097 | 0.032043 | 0.032043 | 62.8876 | -59.9991 | 63.0203 | -59.9991 | -60.1227 | -59.9396 | -0.10529 | -0.064087 | 0.022888 | 0.15106 | 60.0037 | -0.23804 | 60.1089 | -0.13275 | -0.027465 | -0.064087 | 0.068665 | -0.027465 | 0.032044 | -0.15106 | 0.059509 | -0.1236 | 0.25635 | 123.0515 | 0 | 123.0194 | 122.9645 | 122.8867 | 122.8592 | 122.8592 | -123.0286 | -122.9507 | 122.9462 | 122.9919 | 60.0037 | 60.0037
356.8281 | 123.1155 | -59.9716 | 62.9745 | -0.075684 | 5.7742e-05 | 0.064068 | 0.066804 | -0.0016663 | -0.0012048 | -0.00076267 | -0.046051 | 0.0003118 | 0.066204 | 0.066061 | -0.0035632 | 0.0043836 | 0.0019823 | -0.018311 | 62.883 | -60.0861 | 62.9425 | -59.8572 | -60.2188 | -0.022888 | -0.018311 | 62.883 | -59.9808 | 63.002 | -60.0357 | -60.1364 | -59.9762 | -0.11444 | -0.091552 | -0.032043 | 0.11444 | 59.9487 | -0.24719 | 60.0632 | -0.13275 | -0.009155 | -0.091552 | 0.027466 | -0.064087 | -0.004577 | -0.1648 | 0.004578 | -0.15564 | 0.22888 | 123.0286 | -0.054932 | 122.9828 | 122.9691 | 122.8638 | 122.8546 | 122.8546 | -123.0606 | -122.9553 | 122.9141 | 122.9736 | 59.9533 | 59.9533
357.8906 | 123.1613 | -59.9762 | 62.9791 | -0.029907 | 0.00048494 | 0.061718 | 0.065523 | -0.00017091 | 0.00050424 | -0.00033547 | -0.046051 | 0.0041572 | 0.064922 | 0.063711 | -0.0012134 | 0.0056652 | -0.0027173 | 0.009155 | 62.9059 | -60.0449 | 62.9242 | -59.8755 | -60.1913 | 0.013733 | 0 | 62.8922 | -59.967 | 63.0112 | -59.9945 | -60.0998 | -59.9579 | -0.068665 | -0.073242 | -0.054932 | 0.10071 | 59.9899 | -0.21515 | 60.0586 | -0.14648 | 0.009155 | -0.086975 | 0.032043 | -0.018311 | 0.01831 | -0.1236 | 0.009155 | -0.13275 | 0.16937 | 122.9691 | -0.027466 | 122.9782 | 122.9507 | 122.8592 | 122.8821 | 122.8683 | -123.024 | -122.9462 | 122.9004 | 122.9874 | 59.9854 | 59.9762
358.8281 | 123.1705 | -59.9716 | 62.9517 | -0.045166 | -0.00058326 | 0.064709 | 0.065523 | 0.0021789 | -0.0014184 | -0.0026853 | -0.024689 | 0.0035162 | 0.064495 | 0.060079 | -0.0012134 | 0.0039562 | -0.0014355 | 0.022888 | 62.8876 | -60.0723 | 62.9837 | -59.8343 | -60.2005 | 0.018311 | 0.036621 | 62.8555 | -59.9625 | 63.0249 | -59.9899 | -60.0815 | -59.9533 | -0.10071 | -0.064087 | 0.032044 | 0.13733 | 59.9899 | -0.22888 | 60.0906 | -0.12817 | 0.009156 | -0.09613 | 0.073242 | -0.01831 | 0.018311 | -0.10986 | 0.009155 | -0.11902 | 0.23804 | 123.056 | -0.027466 | 122.9874 | 122.9599 | 122.818 | 122.8592 | 122.8271 | -123.024 | -122.9141 | 122.9553 | 122.9965 | 59.9945 | 60.0082
359.8906 | 123.2208 | -59.9258 | 62.9608 | -0.090943 | 0.00048494 | 0.063854 | 0.065736 | -0.0038025 | 0.0013586 | -0.0014035 | 0.063812 | 9.8198e-05 | 0.065777 | 0.065206 | -0.004845 | 0.00182 | 5.9726e-05 | 0.054932 | 62.9059 | -60.0494 | 62.9425 | -59.6512 | -60.2051 | 0.041199 | 0.091553 | 62.8235 | -59.9579 | 63.0798 | -59.9121 | -59.9854 | -59.8801 | -0.1236 | -0.054931 | -0.01831 | 0.27466 | 59.967 | -0.27924 | 60.0906 | -0.15564 | -0.032044 | -0.13733 | 0.11902 | 0.013733 | 0.045776 | -0.05951 | 0.07782 | -0.027466 | 0.39825 | 122.9919 | 0.045777 | 123.0377 | 122.9553 | 122.7814 | 122.8317 | 122.7493 | -123.0103 | -122.9187 | 122.8683 | 123.0057 | 59.9808 | 60.0174
360.8281 | 123.1613 | -59.9533 | 62.9517 | -0.083313 | 0.00091214 | 0.064068 | 0.06595 | 0.0011109 | -0.0020594 | 9.193e-05 | -0.12234 | 0.0005256 | 0.065136 | 0.066915 | -0.0035632 | 0.0033154 | 0.0028369 | 0.022888 | 62.8693 | -60.0723 | 62.9791 | -59.848 | -60.2051 | 0 | -0.018311 | 62.8555 | -59.9625 | 63.0157 | -59.9808 | -60.1318 | -59.9625 | -0.11902 | -0.082397 | 0.027466 | 0.10529 | 59.9533 | -0.25177 | 60.0723 | -0.13275 | -0.009155 | -0.09613 | 0.064087 | -0.027466 | -0.009155 | -0.17853 | 0 | -0.16937 | 0.22431 | 123.0515 | -0.018311 | 122.9782 | 122.9416 | 122.818 | 122.8226 | 122.8088 | -123.024 | -122.9141 | 122.9324 | 122.9691 | 59.9762 | 59.935
361.8906 | 123.2254 | -59.9167 | 62.9883 | -0.13672 | 0.0015529 | 0.066631 | 0.063386 | -0.00017091 | 7.6842e-05 | -0.00076267 | 0.057709 | 0.0005256 | 0.066631 | 0.059439 | -0.004845 | 0.0031018 | -0.00058107 | -0.009155 | 62.8693 | -60.0357 | 63.0249 | -59.7153 | -60.1089 | 0.09613 | 0.10986 | 62.8647 | -59.9579 | 63.0753 | -59.9167 | -60.0082 | -59.8801 | -0.11902 | -0.11902 | 0.036621 | 0.20142 | 60.0128 | -0.19226 | 60.1318 | -0.073242 | -0.041199 | -0.1236 | 0.086975 | 0 | 0.036621 | -0.091553 | 0.07782 | -0.050354 | 0.32043 | 123.0606 | 0.041199 | 123.0331 | 122.905 | 122.8226 | 122.7859 | 122.7814 | -123.024 | -122.9462 | 122.9416 | 122.9919 | 59.9075 | 60.0266
362.8281 | 123.143 | -59.9579 | 63.002 | -0.075684 | 0.0026211 | 0.063213 | 0.06595 | 0.0047425 | 7.6842e-05 | -0.0016171 | -0.033844 | 0.003089 | 0.066418 | 0.062643 | -0.0039906 | 0.0041698 | 0.00091433 | 0.022888 | 62.8922 | -60.0815 | 62.9883 | -59.8206 | -60.2051 | 0.027466 | 0.036621 | 62.8967 | -59.9716 | 63.0203 | -59.9808 | -60.1044 | -59.9442 | -0.1236 | -0.10986 | -0.013733 | 0.13733 | 59.9854 | -0.24719 | 60.1089 | -0.1236 | -0.013733 | -0.10529 | 0.018311 | -0.022888 | 0.013733 | -0.14648 | 0.027466 | -0.13275 | 0.26093 | 123.0698 | -0.009155 | 122.9919 | 122.9736 | 122.8683 | 122.85 | 122.8546 | -123.0835 | -122.9736 | 122.9462 | 122.9782 | 59.9808 | 59.9945
363.8281 | 123.1155 | -59.9945 | 62.9929 | -0.075684 | 5.7742e-05 | 0.064922 | 0.067018 | 0.0013245 | 0.001145 | 0.00051913 | -0.046051 | 0.0009528 | 0.067058 | 0.064779 | -0.0037768 | 0.0028882 | 0.0013415 | -0.009155 | 62.8647 | -60.0861 | 62.9517 | -59.8709 | -60.2142 | -0.027466 | -0.022888 | 62.9059 | -59.9945 | 62.9883 | -60.0449 | -60.1593 | -59.9854 | -0.091553 | -0.12817 | -0.041199 | 0.1236 | 59.967 | -0.21973 | 60.0586 | -0.12817 | 0 | -0.086975 | -0.004578 | -0.050354 | 0.009155 | -0.16479 | 0.009155 | -0.16479 | 0.21515 | 123.0377 | -0.050354 | 122.9828 | 122.9507 | 122.9004 | 122.8592 | 122.9004 | -123.0789 | -122.9874 | 122.9462 | 122.9828 | 59.9854 | 59.9716
364.8281 | 123.1613 | -59.9716 | 62.9883 | -0.029907 | 0.0028347 | 0.06535 | 0.066804 | -0.0025207 | -0.002273 | 0.00073273 | -0.042999 | 0.0011664 | 0.063854 | 0.065206 | -0.004845 | 0.0022472 | 5.9726e-05 | 0.022888 | 62.9013 | -60.0723 | 62.9745 | -59.8343 | -60.2005 | 0.018311 | 0.032043 | 62.883 | -59.9808 | 63.0203 | -59.9854 | -60.0998 | -59.9396 | -0.10071 | -0.086975 | -0.013733 | 0.13733 | 59.9899 | -0.22888 | 60.0906 | -0.12817 | -0.009155 | -0.10529 | 0.032044 | -0.013733 | 0.032044 | -0.12817 | 0.041199 | -0.11902 | 0.23804 | 123.0469 | -0.004578 | 123.0011 | 122.9736 | 122.8638 | 122.8729 | 122.8546 | -123.0606 | -122.9691 | 122.9462 | 122.9919 | 59.9945 | 60.0037
365.8906 | 123.2712 | -59.9533 | 62.9654 | -0.1062 | 0.0021939 | 0.062572 | 0.0636 | 4.2692e-05 | -0.00035036 | -0.0026853 | 0.027191 | 0.0009528 | 0.066631 | 0.062216 | -0.0033496 | 0.003529 | 0.00048713 | -0.054932 | 62.8464 | -60.0769 | 62.9379 | -59.8434 | -60.2142 | -0.027466 | -0.041199 | 62.8418 | -59.9625 | 63.0203 | -59.9854 | -60.0861 | -60.0449 | -0.1236 | -0.11902 | -0.027466 | 0.10986 | 59.9258 | -0.26093 | 60.0494 | -0.13733 | -0.009155 | -0.1236 | 0.054932 | -0.032044 | -0.091553 | -0.13275 | -0.082398 | -0.1236 | 0.23346 | 123.0148 | -0.022889 | 122.9828 | 122.9233 | 122.8043 | 122.7997 | 122.7951 | -123.0423 | -122.9279 | 122.8912 | 122.9736 | 59.8984 | 59.9121
366.8281 | 123.1842 | -59.967 | 62.9745 | -0.075684 | -0.00015586 | 0.062359 | 0.064882 | 0.0011109 | -0.00099116 | 0.00051913 | -0.058258 | 0.0020208 | 0.066845 | 0.06542 | -0.0056994 | 0.003529 | -0.0012219 | 0.022888 | 62.8876 | -60.0632 | 62.9883 | -59.848 | -60.1913 | 0.018311 | 0.045776 | 62.8693 | -59.9625 | 63.0295 | -59.9854 | -60.1044 | -59.9533 | -0.09613 | -0.086975 | 0.013733 | 0.11902 | 59.9854 | -0.2243 | 60.0815 | -0.12817 | 0.004578 | -0.10529 | 0.054932 | -0.018311 | 0.013733 | -0.13733 | 0.009155 | -0.14191 | 0.21515 | 123.0515 | -0.022889 | 122.9919 | 122.9507 | 122.8317 | 122.8546 | 122.8363 | -123.0377 | -122.937 | 122.9553 | 122.9965 | 59.9899 | 60.0128
367.8906 | 123.1064 | -59.9487 | 63.002 | -0.029907 | 0.0015529 | 0.063641 | 0.065523 | -0.0012391 | -0.0018458 | 0.0018009 | 0.024139 | 0.0015936 | 0.068981 | 0.061788 | -0.0033496 | 0.00096564 | -0.00036747 | 0.009155 | 62.915 | -60.0403 | 62.9562 | -59.8618 | -60.2188 | 0.050354 | 0.013733 | 62.8876 | -60.0037 | 62.9517 | -60.0128 | -60.1318 | -59.9808 | -0.091553 | -0.086975 | -0.045776 | 0.086975 | 59.9991 | -0.27008 | 60.0906 | -0.17853 | -0.054932 | -0.11444 | -0.050354 | -0.064087 | -0.032044 | -0.18311 | 0.022888 | -0.12817 | 0.17853 | 122.9965 | -0.009155 | 122.9553 | 122.9553 | 122.8912 | 122.8638 | 122.8363 | -123.0423 | -123.0057 | 122.905 | 122.9004 | 59.9579 | 59.9625
368.8281 | 123.1018 | -59.9533 | 63.0295 | -0.13672 | -0.0025059 | 0.063854 | 0.067232 | -0.00081171 | -0.0012048 | 0.00030553 | 0.011932 | 0.0020208 | 0.067272 | 0.061361 | -0.0029224 | 0.0026746 | -0.0018629 | 0.032043 | 62.9105 | -60.0723 | 62.9379 | -59.8801 | -60.2463 | 0.032043 | -0.018311 | 62.9105 | -59.9625 | 62.9837 | -60.0266 | -60.1318 | -59.9716 | -0.11902 | -0.11902 | -0.091553 | 0.073242 | 59.9854 | -0.29297 | 60.1044 | -0.17395 | -0.009155 | -0.11902 | -0.045776 | -0.073242 | -0.018311 | -0.17853 | -0.009156 | -0.16937 | 0.19226 | 123.0103 | -0.064087 | 122.9462 | 122.9828 | 122.8729 | 122.8638 | 122.8638 | -123.1018 | -122.9919 | 122.8912 | 122.937 | 59.9854 | 59.935
369.8906 | 123.2483 | -59.9167 | 62.9745 | -0.052796 | 0.00091214 | 0.062359 | 0.065523 | -0.00081171 | -0.0027002 | 0.0026553 | 0.082123 | -0.0001154 | 0.067272 | 0.058584 | -0.004845 | 0.0024608 | -0.0033581 | 0.059509 | 62.851 | -60.0128 | 63.1622 | -59.436 | -60.228 | -0.10071 | 0.027466 | 62.8647 | -59.9533 | 63.1027 | -59.9167 | -59.9945 | -59.8526 | -0.09613 | -0.1236 | 0.18768 | 0.48065 | 59.816 | -0.31128 | 59.9121 | -0.21515 | -0.036621 | -0.10986 | 0.12817 | 0 | 0.064087 | -0.07782 | 0.10071 | -0.041199 | 0.57678 | 123.175 | 0.036621 | 123.056 | 122.8638 | 122.818 | 122.7676 | 122.7814 | -122.9874 | -122.9279 | 123.0789 | 123.0194 | 59.9762 | 59.9442
370.8281 | 123.1613 | -59.9533 | 63.0524 | -0.068054 | 0.0019803 | 0.062145 | 0.065309 | -0.0042297 | -0.0033412 | -0.0026853 | -0.0002747 | 0.0009528 | 0.067699 | 0.061148 | -0.0024952 | 0.0037426 | -0.0025037 | -0.004578 | 62.9013 | -60.0586 | 62.9333 | -59.8755 | -60.2234 | 0.032043 | 0.009155 | 62.9059 | -59.9716 | 62.9517 | -60.0266 | -60.141 | -60.054 | -0.10529 | -0.15106 | -0.11902 | 0.07782 | 59.9854 | -0.27008 | 60.0906 | -0.16479 | -0.018311 | -0.14648 | -0.10071 | -0.073242 | -0.10071 | -0.18768 | -0.082397 | -0.16937 | 0.18311 | 122.9919 | -0.054931 | 122.9233 | 122.9599 | 122.8775 | 122.8546 | 122.8592 | -123.111 | -123.024 | 122.8867 | 122.905 | 59.9487 | 59.9625
371.8906 | 123.2437 | -59.9487 | 62.9608 | -0.083313 | -0.0010105 | 0.063854 | 0.064668 | -0.0023071 | 7.6842e-05 | 9.193e-05 | 0.036346 | -0.0016108 | 0.064922 | 0.060079 | -0.0035632 | 0.00075204 | -0.0016493 | -0.009155 | 62.883 | -60.0632 | 62.9837 | -59.8114 | -60.1547 | 0.045776 | 0.050354 | 62.8281 | -59.9396 | 63.0707 | -59.9442 | -60.0357 | -59.8984 | -0.11444 | -0.077819 | 0.022889 | 0.13733 | 59.9945 | -0.20599 | 60.1089 | -0.091553 | 0.009155 | -0.13275 | 0.10986 | 0.004577 | 0.050354 | -0.086976 | 0.041199 | -0.096131 | 0.25177 | 123.0469 | -0.004578 | 123.0103 | 122.9462 | 122.7676 | 122.8317 | 122.7768 | -123.024 | -122.9004 | 122.9324 | 123.0194 | 59.9396 | 59.9991
372.8281 | 123.1934 | -59.9258 | 63.0295 | -0.029907 | 0.0017667 | 0.063 | 0.065523 | -0.0010253 | -0.0035548 | 0.0013735 | -0.015534 | 0.0024482 | 0.064922 | 0.068411 | -0.0024952 | 0.0013928 | -0.0035719 | -0.004578 | 62.9333 | -60.0586 | 62.9471 | -59.8709 | -60.2188 | 0.032043 | -0.004578 | 62.9059 | -59.9854 | 62.9791 | -60.0311 | -60.0632 | -59.8663 | -0.13275 | -0.09613 | -0.082397 | 0.054931 | 59.9579 | -0.29297 | 60.0906 | -0.16022 | -0.05951 | -0.1236 | -0.050354 | -0.10529 | 0.059509 | -0.13733 | 0.11902 | -0.077819 | 0.18768 | 123.0057 | -0.045776 | 122.9645 | 122.9919 | 122.8912 | 122.8592 | 122.8317 | -123.0881 | -123.0148 | 122.8729 | 122.905 | 59.9213 | 59.9213
373.8906 | 123.2071 | -59.9442 | 62.9517 | -0.083313 | -0.0010105 | 0.063854 | 0.063814 | 0.0032471 | -0.00056396 | 9.193e-05 | 0.051605 | 0.0018072 | 0.065136 | 0.061575 | -0.0024952 | 0.0016064 | 0.00048713 | -0.041199 | 62.851 | -60.0586 | 62.9608 | -59.8389 | -60.1913 | 0.004578 | -0.086975 | 62.8464 | -59.9716 | 63.0112 | -59.9808 | -60.0723 | -59.9167 | -0.11444 | -0.10071 | 0.009155 | 0.10529 | 59.9487 | -0.24719 | 60.0632 | -0.13275 | -0.027466 | -0.10528 | 0.059509 | -0.036621 | 0.027466 | -0.12817 | 0.054932 | -0.10071 | 0.21973 | 123.0194 | -0.009155 | 122.9828 | 122.9095 | 122.818 | 122.7951 | 122.7905 | -123.0103 | -122.9233 | 122.905 | 122.9553 | 59.903 | 59.8572
374.8281 | 123.1979 | -59.9304 | 63.0066 | -0.045166 | 0.00091214 | 0.063641 | 0.06595 | 0.00025629 | -0.00013676 | -0.00054907 | -0.033844 | 0.0018072 | 0.067272 | 0.06072 | -0.0039906 | 0.0028882 | 0.0024097 | -0.004578 | 62.9242 | -60.0677 | 62.9379 | -59.8755 | -60.228 | 0.041199 | -0.009155 | 62.8784 | -59.9899 | 62.9745 | -60.0266 | -60.0723 | -59.8526 | -0.13733 | -0.082398 | -0.068665 | 0.054932 | 59.9716 | -0.29755 | 60.1089 | -0.16022 | -0.059509 | -0.12817 | -0.032044 | -0.09613 | 0.07782 | -0.14191 | 0.13733 | -0.082398 | 0.19226 | 123.0057 | -0.036621 | 122.9645 | 122.9919 | 122.8683 | 122.8546 | 122.8088 | -123.0743 | -122.9965 | 122.8683 | 122.905 | 59.9258 | 59.9213
375.8906 | 123.2071 | -59.9579 | 62.9425 | -0.13672 | 0.0015529 | 0.063427 | 0.065523 | 0.00025629 | -0.002273 | -0.0024717 | 0.014984 | 0.0018072 | 0.067699 | 0.057302 | -0.003136 | 0.0020336 | -0.0033581 | -0.054932 | 62.8555 | -60.0723 | 62.9608 | -59.8389 | -60.228 | -0.041199 | -0.036621 | 62.8281 | -59.9899 | 63.0203 | -59.9945 | -60.1044 | -59.9396 | -0.11444 | -0.086975 | 0.01831 | 0.11902 | 59.9167 | -0.27008 | 60.0311 | -0.15564 | -0.032043 | -0.11444 | 0.07782 | -0.036621 | 0.018311 | -0.14648 | 0.050354 | -0.11444 | 0.23346 | 123.0331 | -0.004578 | 123.0103 | 122.9279 | 122.818 | 122.8134 | 122.7859 | -123.0148 | -122.9324 | 122.9187 | 122.9782 | 59.903 | 59.9213
376.8281 | 123.1338 | -59.9579 | 62.9883 | -0.052796 | 0.00069854 | 0.065136 | 0.066163 | -0.0016663 | -0.0031274 | -0.00076267 | -0.012482 | 0.0039434 | 0.066204 | 0.06307 | -0.0029224 | 0.0033154 | -0.0037855 | 0.064087 | 62.8876 | -60.0357 | 63.002 | -59.8251 | -60.1547 | 0.091553 | 0.050354 | 62.883 | -59.9487 | 63.002 | -59.9899 | -60.1135 | -59.9899 | -0.07782 | -0.10071 | 0.013733 | 0.13275 | 60.0494 | -0.19684 | 60.1273 | -0.11902 | 0.009156 | -0.10529 | 0.013733 | -0.032043 | -0.032043 | -0.15564 | -0.041199 | -0.1648 | 0.21057 | 123.0377 | -0.041199 | 122.9507 | 122.9233 | 122.8317 | 122.8455 | 122.8409 | -123.024 | -122.937 | 122.9599 | 122.9599 | 60.022 | 60.0082
377.8906 | 123.1934 | -59.9625 | 62.9288 | -0.083313 | 0.0015529 | 0.064281 | 0.065736 | 4.2692e-05 | -0.0031274 | 0.00030553 | -0.018585 | 0.0003118 | 0.064495 | 0.059439 | -0.0044178 | 0.0022472 | -0.0048535 | -0.022888 | 62.8281 | -60.0677 | 63.0066 | -59.8068 | -60.1913 | 0 | 0.013733 | 62.8418 | -59.9854 | 63.0341 | -59.9854 | -60.0677 | -59.9167 | -0.10529 | -0.10071 | 0.07782 | 0.15564 | 59.9625 | -0.22888 | 60.0677 | -0.1236 | -0.022889 | -0.086975 | 0.10529 | -0.022889 | 0.045776 | -0.10529 | 0.068665 | -0.082397 | 0.26093 | 123.0743 | 0 | 123.0194 | 122.8958 | 122.8271 | 122.7905 | 122.8043 | -122.9965 | -122.9141 | 122.9691 | 122.9965 | 59.9396 | 59.9762
378.8281 | 123.1338 | -59.9442 | 62.9654 | -0.052796 | 0.0013393 | 0.064922 | 0.067232 | 0.0019653 | 0.0015722 | -0.0020443 | 0.0058289 | 0.0018072 | 0.063854 | 0.062856 | -0.0035632 | 0.0013928 | -0.0010083 | 0.045776 | 62.883 | -60.0311 | 63.002 | -59.8022 | -60.1593 | 0.10071 | 0.050354 | 62.883 | -59.9625 | 63.0066 | -60.0037 | -60.1089 | -59.9899 | -0.086975 | -0.082397 | 0.036621 | 0.14191 | 60.0449 | -0.21515 | 60.1318 | -0.12817 | -0.01831 | -0.082397 | 0.041199 | -0.059509 | -0.045776 | -0.16479 | -0.027466 | -0.14648 | 0.22888 | 123.0331 | -0.041199 | 122.9691 | 122.9141 | 122.8455 | 122.8271 | 122.8271 | -122.9965 | -122.9279 | 122.9462 | 122.9507 | 59.9899 | 59.9945
379.8906 | 123.1201 | -59.9579 | 62.9242 | -0.037537 | -0.00079686 | 0.063213 | 0.066804 | 0.0023925 | 0.00029044 | -0.0020443 | -0.094879 | 0.0028754 | 0.069622 | 0.061148 | -0.0039906 | 0.0031018 | 0.00048713 | -0.09613 | 62.883 | -60.1227 | 62.915 | -59.9258 | -60.3058 | -0.086975 | -0.10986 | 62.8555 | -60.0128 | 62.97 | -60.0632 | -60.1776 | -59.9808 | -0.16479 | -0.041198 | -0.009155 | 0.032044 | 59.8709 | -0.3479 | 60.0357 | -0.1831 | -0.054931 | -0.068664 | 0.045777 | -0.10528 | -0.022888 | -0.21973 | 0.032043 | -0.1648 | 0.19684 | 123.0377 | -0.050354 | 122.9828 | 123.0057 | 122.8683 | 122.8409 | 122.8134 | -123.0469 | -122.937 | 122.8729 | 122.9279 | 59.8618 | 59.848
380.8281 | 123.2254 | -59.9121 | 62.9379 | 0.015869 | 0.0011257 | 0.063213 | 0.063814 | 0.0026063 | -0.0020594 | -0.00054907 | 0.030243 | 0.0011664 | 0.066631 | 0.062643 | -0.0042042 | 0.0043836 | -0.00015387 | 0.050354 | 62.8601 | -60.0174 | 63.0798 | -59.7153 | -60.0723 | 0.10529 | 0.12817 | 62.8555 | -59.9442 | 63.089 | -59.8709 | -59.9991 | -59.8526 | -0.10529 | -0.07782 | 0.14191 | 0.19684 | 60.0174 | -0.16022 | 60.1227 | -0.054932 | -0.032044 | -0.082397 | 0.15106 | 0.041198 | 0.059509 | -0.086975 | 0.091553 | -0.054931 | 0.30212 | 123.0972 | 0.073242 | 123.0331 | 122.8775 | 122.7997 | 122.7722 | 122.7676 | -122.9553 | -122.8821 | 122.9919 | 123.0011 | 59.9625 | 60.0403
381.8906 | 123.2025 | -59.9487 | 62.9379 | -0.1062 | 0.00069854 | 0.063213 | 0.0636 | 0.0017517 | 0.0015722 | 9.193e-05 | -0.027741 | 0.0005256 | 0.065349 | 0.062216 | -0.001427 | 0.0037426 | 0.00048713 | -0.045776 | 62.8601 | -60.0494 | 62.97 | -59.8434 | -60.1364 | 0.13275 | -0.004578 | 62.851 | -59.9762 | 63.0249 | -59.9808 | -60.0769 | -59.9396 | -0.10071 | -0.07782 | 0.032044 | 0.10528 | 60.0815 | -0.18768 | 60.1822 | -0.086976 | -0.027466 | -0.086975 | 0.086975 | -0.032044 | 0.009155 | -0.12817 | 0.036621 | -0.10071 | 0.20599 | 123.0194 | -0.004578 | 123.0011 | 122.9095 | 122.8271 | 122.8088 | 122.7997 | -122.9874 | -122.9141 | 122.9187 | 122.9736 | 59.903 | 59.9442
382.8281 | 123.2162 | -59.935 | 62.9608 | -0.060425 | 0.0026211 | 0.061932 | 0.065523 | -0.0023071 | -0.0014184 | -0.0046079 | 0.027191 | 0.0009528 | 0.065349 | 0.059439 | -0.0022816 | 0.0031018 | -0.00015387 | 0.059509 | 62.8647 | -60.0357 | 63.0661 | -59.697 | -60.0769 | 0.10071 | 0.13275 | 62.8555 | -59.9487 | 63.0981 | -59.8846 | -59.9762 | -59.8572 | -0.10071 | -0.09613 | 0.10529 | 0.23804 | 60.0357 | -0.14191 | 60.1364 | -0.041198 | -0.013732 | -0.10528 | 0.13733 | 0.050354 | 0.07782 | -0.041198 | 0.091552 | -0.027466 | 0.33875 | 123.1018 | 0.064086 | 123.0469 | 122.9004 | 122.8043 | 122.7997 | 122.7905 | -122.9965 | -122.9095 | 123.0011 | 123.0331 | 59.9945 | 60.0677
383.8906 | 123.2391 | -59.9579 | 62.9333 | -0.090943 | 5.7742e-05 | 0.064495 | 0.067232 | 0.0015381 | 0.0017858 | -0.0026853 | -0.049103 | 0.0005256 | 0.064922 | 0.057302 | -0.0061268 | 0.0054516 | 0.0013415 | -0.027466 | 62.8143 | -60.0586 | 63.0157 | -59.7839 | -60.173 | -0.018311 | -0.009155 | 62.8143 | -59.9854 | 63.0386 | -59.8846 | -60.0906 | -59.9396 | -0.10071 | -0.11902 | 0.082397 | 0.17395 | 59.9396 | -0.21515 | 60.0403 | -0.11444 | -0.027466 | -0.11902 | 0.10529 | 0.073242 | 0.018311 | -0.13275 | 0.045777 | -0.10529 | 0.27466 | 123.0743 | 0.10071 | 123.024 | 122.8729 | 122.7997 | 122.7722 | 122.7722 | -122.9919 | -122.9187 | 122.9736 | 122.9965 | 59.9304 | 59.9487
384.8281 | 123.2437 | -59.935 | 62.9517 | -0.045166 | 0.0011257 | 0.061718 | 0.065523 | 0.0013245 | -0.00056396 | -0.00054907 | 0.014984 | 0.0020208 | 0.064922 | 0.059225 | -0.004845 | 0.0041698 | -0.00036747 | -0.013733 | 62.8784 | -60.0449 | 63.0066 | -59.7839 | -60.1456 | 0.073242 | 0.064087 | 62.8372 | -59.9625 | 63.0798 | -59.8938 | -59.9991 | -59.8663 | -0.10986 | -0.073242 | 0.054932 | 0.15106 | 60.0082 | -0.21057 | 60.1181 | -0.10071 | -0.027465 | -0.11444 | 0.12817 | 0.041199 | 0.068665 | -0.064086 | 0.09613 | -0.036621 | 0.26093 | 123.0515 | 0.068664 | 123.0423 | 122.9233 | 122.7997 | 122.8134 | 122.7722 | -122.9965 | -122.9141 | 122.9416 | 123.0148 | 59.9213 | 59.9991
385.8906 | 123.1796 | -59.9487 | 62.9196 | -0.090943 | 0.0030483 | 0.062572 | 0.065736 | -0.0023071 | -0.00077756 | 0.00094633 | -0.0063781 | 0.0007392 | 0.068554 | 0.06072 | -0.0054858 | 0.0028882 | -0.00036747 | -0.064087 | 62.8189 | -60.0815 | 62.9562 | -59.8434 | -60.2097 | -0.022888 | -0.054932 | 62.8464 | -59.9716 | 63.0157 | -59.9991 | -60.0723 | -59.9533 | -0.13275 | -0.10071 | 0.036621 | 0.10528 | 59.9258 | -0.26093 | 60.0586 | -0.12817 | -0.022889 | -0.073242 | 0.09613 | -0.050354 | -0.004578 | -0.1236 | 0.018311 | -0.10071 | 0.23804 | 123.0377 | -0.027465 | 122.9874 | 122.9004 | 122.818 | 122.7676 | 122.7951 | -123.0011 | -122.8912 | 122.905 | 122.9645 | 59.8846 | 59.8938
386.8281 | 123.1842 | -59.9625 | 62.9562 | -0.098572 | 0.0013393 | 0.063213 | 0.068086 | -0.0023071 | 0.0013586 | 0.00094633 | -0.012482 | 0.0011664 | 0.066418 | 0.056448 | -0.0044178 | 0.003529 | -0.0014355 | -0.036621 | 62.8784 | -60.0723 | 62.9791 | -59.8297 | -60.173 | 0.018311 | 0 | 62.8464 | -59.967 | 63.0341 | -59.9533 | -60.0494 | -59.8938 | -0.10986 | -0.07782 | 0.022888 | 0.13275 | 59.9808 | -0.21057 | 60.0906 | -0.10071 | -0.004578 | -0.10986 | 0.07782 | 0.009155 | 0.068664 | -0.086975 | 0.073242 | -0.082397 | 0.24262 | 123.0515 | 0.013733 | 123.0011 | 122.9507 | 122.8134 | 122.8409 | 122.8088 | -123.0286 | -122.9233 | 122.9416 | 122.9965 | 59.9258 | 59.9625
387.8906 | 123.1796 | -59.9533 | 62.9242 | -0.052796 | 0.0030483 | 0.064068 | 0.065523 | 0.00025629 | -0.0018458 | 0.0011599 | -0.039948 | 0.0005256 | 0.064281 | 0.064352 | -0.004845 | 0.00182 | -0.0010083 | -0.041199 | 62.8372 | -60.0815 | 62.9791 | -59.7931 | -60.2097 | -0.004578 | 0 | 62.8235 | -59.9899 | 63.0249 | -59.9808 | -60.0906 | -59.9533 | -0.12817 | -0.086975 | 0.054932 | 0.16022 | 59.9487 | -0.25635 | 60.0769 | -0.12817 | -0.036621 | -0.10071 | 0.10071 | -0.027466 | 0 | -0.13733 | 0.036621 | -0.10071 | 0.28839 | 123.0606 | 0.009155 | 123.0148 | 122.9187 | 122.8134 | 122.7905 | 122.7768 | -123.0057 | -122.9141 | 122.9324 | 122.9782 | 59.9121 | 59.9533
388.8281 | 123.2071 | -59.935 | 62.9333 | -0.083313 | 0.0013393 | 0.062572 | 0.065736 | -0.00017091 | -0.0024866 | -0.0016171 | -0.0002747 | 0.0007392 | 0.067058 | 0.064993 | -0.0022816 | 0.0041698 | -0.0020765 | -0.032043 | 62.8784 | -60.0494 | 62.9837 | -59.8343 | -60.1639 | 0.041199 | 0 | 62.8326 | -59.9625 | 63.0661 | -59.935 | -60.0494 | -59.903 | -0.11444 | -0.054932 | 0.050354 | 0.10071 | 59.9762 | -0.22888 | 60.0906 | -0.11444 | -0.027465 | -0.10071 | 0.13275 | 0 | 0.032044 | -0.11444 | 0.059509 | -0.086975 | 0.21515 | 123.0331 | 0.027465 | 123.0286 | 122.9279 | 122.7951 | 122.8134 | 122.7676 | -122.9828 | -122.8958 | 122.9187 | 123.0011 | 59.903 | 59.935
389.8906 | 123.1522 | -59.967 | 62.9654 | -0.075684 | 0.00048494 | 0.063 | 0.067445 | 0.00089729 | -0.0033412 | 0.00073273 | -0.091827 | 0.0015936 | 0.064709 | 0.06777 | -0.0039906 | 0.0045972 | 0.0015551 | 0.004578 | 62.8876 | -60.0632 | 62.9791 | -59.8343 | -60.1959 | 0.013733 | 0.018311 | 62.8967 | -59.9991 | 63.0386 | -59.9762 | -60.0952 | -59.9579 | -0.09613 | -0.07782 | 0.013733 | 0.13275 | 59.9808 | -0.22888 | 60.0769 | -0.13275 | -0.032043 | -0.068664 | 0.073242 | -0.009155 | 0.009155 | -0.12817 | 0.041198 | -0.096131 | 0.22888 | 123.0423 | 0.022888 | 123.0377 | 122.9507 | 122.8958 | 122.8546 | 122.8638 | -123.0286 | -122.9645 | 122.9462 | 123.0057 | 59.9716 | 59.9854
390.8281 | 123.2574 | -59.9579 | 62.9242 | -0.068054 | 0.00027134 | 0.061932 | 0.066377 | 4.2692e-05 | -0.00077756 | 0.00030553 | -0.0002747 | 0.0020208 | 0.067486 | 0.061148 | -0.0029224 | 0.0016064 | -0.0010083 | -0.027466 | 62.8464 | -60.0449 | 62.9791 | -59.8251 | -60.173 | 0.036621 | 0 | 62.8601 | -59.967 | 63.0661 | -59.9396 | -60.0403 | -59.8938 | -0.086975 | -0.077819 | 0.054932 | 0.13275 | 59.9945 | -0.21515 | 60.0815 | -0.12817 | -0.009155 | -0.064087 | 0.14191 | 0.018311 | 0.064087 | -0.082397 | 0.073242 | -0.073242 | 0.21973 | 123.024 | 0.027466 | 123.0331 | 122.8912 | 122.8271 | 122.8043 | 122.818 | -122.9691 | -122.8912 | 122.937 | 123.024 | 59.9304 | 59.9579
391.8906 | 123.23 | -59.9625 | 62.8967 | -0.11383 | 0.0017667 | 0.063427 | 0.066377 | 0.0021789 | -0.00099116 | 0.0015871 | -0.064362 | 0.0003118 | 0.064709 | 0.066488 | -0.0029224 | 0.0033154 | 0.0013415 | -0.036621 | 62.8372 | -60.0906 | 62.9974 | -59.8114 | -60.1913 | -0.032043 | -0.022888 | 62.851 | -59.9899 | 63.0707 | -59.9442 | -60.0677 | -59.8892 | -0.12817 | -0.05951 | 0.10071 | 0.15106 | 59.9304 | -0.22888 | 60.0586 | -0.10071 | -0.027466 | -0.045777 | 0.17395 | 0.01831 | 0.073242 | -0.10529 | 0.10071 | -0.07782 | 0.27924 | 123.0881 | 0.045776 | 123.0606 | 122.9279 | 122.8409 | 122.7997 | 122.8134 | -122.9874 | -122.8867 | 122.9599 | 123.0331 | 59.9258 | 59.9396
392.8281 | 123.2162 | -59.9762 | 62.9242 | -0.12146 | 0.00027134 | 0.062359 | 0.064454 | 0.0017517 | -0.0024866 | 0.00030553 | -0.018585 | 0.0011664 | 0.066204 | 0.064565 | -0.0033496 | -0.00010256 | 0.00048713 | -0.059509 | 62.8647 | -60.0632 | 62.9654 | -59.8572 | -60.1959 | -0.018311 | -0.054932 | 62.851 | -59.9991 | 63.1393 | -60.1089 | -60.0632 | -59.9304 | -0.086975 | -0.059509 | 0.041199 | 0.11902 | 59.9579 | -0.21973 | 60.0449 | -0.13275 | -0.022888 | -0.073242 | 0.21515 | -0.13275 | 0.045776 | -0.086975 | 0.068664 | -0.064087 | 0.20599 | 123.0286 | -0.10986 | 123.1384 | 122.9279 | 122.85 | 122.8409 | 122.8271 | -122.9874 | -122.9233 | 122.9416 | 123.1155 | 59.9167 | 59.9213
393.8281 | 123.2254 | -59.9442 | 62.9196 | -0.052796 | 0.00027134 | 0.061077 | 0.06595 | 4.2692e-05 | -0.00099116 | -0.00033547 | -0.018585 | 0.0005256 | 0.067058 | 0.060293 | -0.0037768 | 0.0026746 | -0.0012219 | -0.022888 | 62.8647 | -60.0449 | 63.0157 | -59.8114 | -60.141 | 0.064087 | 0.050354 | 62.8555 | -59.9808 | 63.0844 | -59.9167 | -59.9899 | -59.8709 | -0.10071 | -0.054932 | 0.09613 | 0.13275 | 60.0082 | -0.19684 | 60.1089 | -0.09613 | -0.036621 | -0.064087 | 0.16479 | 0.027466 | 0.073242 | -0.045776 | 0.10986 | -0.009155 | 0.23346 | 123.0606 | 0.064087 | 123.0652 | 122.9095 | 122.8363 | 122.8088 | 122.7997 | -122.9645 | -122.9004 | 122.9599 | 123.0286 | 59.9213 | 59.9945
394.8281 | 123.23 | -59.9716 | 62.9425 | -0.12909 | 0.0019803 | 0.063 | 0.066377 | 4.2692e-05 | 0.00071784 | 9.193e-05 | -0.07962 | 0.0009528 | 0.067699 | 0.064993 | -0.0052722 | 0.0041698 | -0.00015387 | -0.045776 | 62.8326 | -60.054 | 62.9929 | -59.8114 | -60.2005 | -0.027466 | -0.018311 | 62.8326 | -59.967 | 63.0707 | -59.9579 | -60.0632 | -59.8938 | -0.082397 | -0.10986 | 0.050354 | 0.16022 | 59.9442 | -0.22888 | 60.0266 | -0.14648 | 0.004578 | -0.10986 | 0.12817 | 0.013733 | 0.07782 | -0.091552 | 0.073242 | -0.09613 | 0.24262 | 123.0469 | 0.009155 | 123.0377 | 122.8867 | 122.7997 | 122.8043 | 122.8043 | -122.9965 | -122.9095 | 122.9645 | 123.0423 | 59.9258 | 59.9533
395.8906 | 123.1659 | -59.9579 | 62.9562 | -0.11383 | 0.0013393 | 0.061932 | 0.067659 | -0.00038451 | 7.6842e-05 | 0.00073273 | -0.088776 | 0.0020208 | 0.066418 | 0.063711 | -0.0022816 | 0.0048108 | -0.0033581 | 0 | 62.9013 | -60.0677 | 62.9654 | -59.8618 | -60.2005 | 0.032043 | 0.013733 | 62.9196 | -59.9808 | 63.0341 | -59.9579 | -60.0998 | -59.9304 | -0.10986 | -0.054932 | 0.009155 | 0.096131 | 59.9899 | -0.24261 | 60.0998 | -0.13275 | -0.022888 | -0.036621 | 0.07782 | 0 | 0.027466 | -0.14191 | 0.050354 | -0.11902 | 0.20599 | 123.0331 | 0.022888 | 123.0148 | 122.9691 | 122.9004 | 122.8592 | 122.8775 | -123.024 | -122.937 | 122.9233 | 122.9919 | 59.9579 | 59.9716
396.8281 | 123.2529 | -59.967 | 62.8922 | -0.13672 | 5.7742e-05 | 0.064709 | 0.06595 | 0.00025629 | -0.0016322 | 9.193e-05 | -0.0094299 | 0.0015936 | 0.067699 | 0.059652 | -0.0042042 | 0.00075204 | 0.0019823 | -0.032043 | 62.8235 | -60.0769 | 62.9654 | -59.7656 | -60.1456 | -0.013733 | -0.009155 | 62.8326 | -59.9854 | 63.0615 | -59.967 | -60.0403 | -59.8801 | -0.10986 | -0.068665 | 0.073242 | 0.20142 | 59.9533 | -0.17853 | 60.0632 | -0.068665 | -0.018311 | -0.059509 | 0.16937 | 0 | 0.086975 | -0.073242 | 0.10529 | -0.054931 | 0.31128 | 123.0423 | 0.018311 | 123.0469 | 122.9004 | 122.818 | 122.7905 | 122.7997 | -122.9691 | -122.8775 | 122.9324 | 123.0286 | 59.935 | 59.9579
397.8906 | 123.0881 | -59.9854 | 62.9471 | -0.060425 | 0.0011257 | 0.063 | 0.067872 | 0.00046989 | -0.0012048 | 0.0018009 | -0.11624 | -0.0001154 | 0.065349 | 0.065206 | -0.0056994 | 0.0054516 | 0.0011279 | -0.041199 | 62.8876 | -60.0861 | 62.9242 | -59.9258 | -60.2737 | -0.09613 | -0.1236 | 62.8876 | -59.9899 | 62.9562 | -60.0952 | -60.2005 | -60.0174 | -0.10071 | -0.05951 | -0.022889 | 0.05951 | 59.8892 | -0.28839 | 59.9899 | -0.18768 | -0.004577 | -0.05951 | 0.009155 | -0.10986 | -0.032043 | -0.21515 | -0.027466 | -0.21057 | 0.16022 | 123.0103 | -0.10529 | 122.9462 | 122.9736 | 122.8775 | 122.8729 | 122.8729 | -123.0331 | -122.937 | 122.9095 | 122.9416 | 59.9442 | 59.8618
398.8281 | 123.1567 | -59.9762 | 62.915 | -0.11383 | 0.0013393 | 0.064922 | 0.062318 | -0.00017091 | -0.00013676 | -0.0048215 | -0.0002747 | 0.0024482 | 0.066204 | 0.062429 | -0.002068 | 0.0022472 | 0.00027333 | -0.045776 | 62.8098 | -60.0723 | 62.9929 | -59.7839 | -60.1822 | -0.027466 | -0.027466 | 62.8052 | -59.9991 | 63.0524 | -59.9945 | -60.0677 | -59.9213 | -0.096131 | -0.10529 | 0.07782 | 0.19226 | 59.9487 | -0.20599 | 60.0449 | -0.10986 | -0.022888 | -0.10986 | 0.13733 | -0.018311 | 0.054931 | -0.091553 | 0.077819 | -0.068665 | 0.28839 | 123.0652 | 0.004577 | 123.0515 | 122.8821 | 122.8043 | 122.7859 | 122.7814 | -122.9874 | -122.9141 | 122.9691 | 123.0286 | 59.9304 | 59.9487
399.8906 | 123.1522 | -59.9533 | 62.9791 | -0.037537 | -0.0010105 | 0.063 | 0.066377 | -0.00081171 | -0.0031274 | -0.0024717 | -0.055206 | 0.0035162 | 0.066845 | 0.066488 | -0.0037768 | 0.0048108 | -0.0010083 | 0.009155 | 62.8876 | -60.0586 | 62.9333 | -59.8846 | -60.1959 | 0.027466 | -0.009155 | 62.8922 | -59.9579 | 63.0066 | -59.9808 | -60.0998 | -59.935 | -0.10529 | -0.091553 | -0.045776 | 0.068664 | 59.9808 | -0.24262 | 60.0861 | -0.13733 | -0.004578 | -0.086975 | 0.027466 | -0.027466 | 0.01831 | -0.14648 | 0.022888 | -0.14191 | 0.17395 | 122.9919 | -0.022888 | 122.9645 | 122.9462 | 122.85 | 122.8409 | 122.8455 | -123.0377 | -122.937 | 122.8867 | 122.9599 | 59.9625 | 59.9442
400.8281 | 123.2529 | -59.9533 | 62.9013 | -0.12909 | -0.00015586 | 0.063 | 0.066163 | 0.0013245 | -0.0016322 | 0.0030825 | -0.027741 | 0.0022346 | 0.065777 | 0.069906 | -0.0035632 | 0.0031018 | 0.00091433 | -0.07782 | 62.8418 | -60.0769 | 62.97 | -59.8343 | -60.2371 | -0.064087 | -0.045776 | 62.8006 | -59.9945 | 63.0524 | -59.9487 | -60.0815 | -59.8755 | -0.1236 | -0.059509 | 0.068665 | 0.11902 | 59.8892 | -0.28381 | 60.0128 | -0.16022 | -0.041199 | -0.10071 | 0.15106 | 0.004578 | 0.07782 | -0.12817 | 0.11902 | -0.086975 | 0.24261 | 123.0469 | 0.045777 | 123.0469 | 122.9187 | 122.7951 | 122.7951 | 122.7539 | -122.9782 | -122.8958 | 122.9233 | 123.0057 | 59.8755 | 59.9075
401.8906 | 123.2391 | -59.935 | 62.9288 | -0.098572 | 0.00048494 | 0.063 | 0.065309 | -0.0023071 | 0.00029044 | -0.0020443 | 0.021088 | 0.0018072 | 0.062359 | 0.061575 | -0.0039906 | 0.0041698 | 0.0030505 | 0.041199 | 62.8647 | -60.0266 | 63.0524 | -59.729 | -60.0815 | 0.11902 | 0.35248 | 62.9059 | -59.9121 | 63.0386 | -59.8663 | -59.967 | -59.8984 | -0.091552 | -0.064087 | 0.1236 | 0.20599 | 60.054 | -0.14648 | 60.1456 | -0.054932 | 0.022889 | -0.022888 | 0.10986 | 0.068665 | 0.036622 | -0.032043 | 0.013733 | -0.054932 | 0.29755 | 123.0789 | 0.045776 | 122.9507 | 122.8912 | 122.818 | 122.7997 | 122.8409 | -122.9553 | -122.8409 | 122.9874 | 122.9736 | 59.9762 | 60.2875
402.8281 | 123.0927 | -59.9991 | 62.9974 | -0.090943 | 0.00027134 | 0.063 | 0.066804 | -0.00038451 | -0.00077756 | -0.00076267 | -0.094879 | 0.0018072 | 0.065136 | 0.060934 | -0.0046314 | 0.011433 | 0.0019823 | -0.09613 | 62.8601 | -60.1135 | 62.8922 | -59.9533 | -60.3058 | -0.11444 | -0.17395 | 62.8464 | -60.0174 | 62.7777 | -59.8892 | -59.9533 | -59.9213 | -0.11444 | -0.13733 | -0.10529 | 0.045776 | 59.8846 | -0.3067 | 59.9991 | -0.19226 | -0.018311 | -0.15106 | -0.21973 | 0.10986 | 0.077819 | 0.045776 | 0.09613 | 0.064087 | 0.16022 | 123.0057 | 0.12817 | 122.7951 | 122.9736 | 122.8638 | 122.8592 | 122.8455 | -123.111 | -123.0148 | 122.8912 | 122.7768 | 59.903 | 59.8251
403.8906 | 123.1888 | -59.9258 | 62.9745 | -0.083313 | 0.00069854 | 0.064922 | 0.064241 | 0.0013245 | -0.00035036 | -0.0018307 | 0.014984 | 0.0020208 | 0.06599 | 0.061148 | -0.0018542 | 0.0016064 | 0.00027333 | 0.045776 | 62.8738 | -60.0311 | 63.0341 | -59.7519 | -60.1273 | 0.11902 | 0.10071 | 62.8601 | -59.9625 | 63.0524 | -59.9304 | -60.0403 | -59.8984 | -0.10529 | -0.10071 | 0.05951 | 0.17395 | 60.0449 | -0.20142 | 60.1501 | -0.09613 | -0.036621 | -0.11444 | 0.07782 | -0.004578 | 0.027466 | -0.11444 | 0.064087 | -0.07782 | 0.27924 | 123.0652 | 0.032043 | 123.0148 | 122.905 | 122.8226 | 122.7997 | 122.7859 | -123.0057 | -122.937 | 122.9599 | 122.9782 | 59.9716 | 60.0266
404.8281 | 123.1934 | -59.9716 | 62.9105 | -0.12146 | 0.0019803 | 0.063 | 0.066163 | -0.00059811 | -0.00013676 | -0.0016171 | -0.030792 | 0.0024482 | 0.066631 | 0.05837 | -0.0039906 | 0.0033154 | -0.0020765 | -0.041199 | 62.8326 | -60.0494 | 63.002 | -59.7794 | -60.1913 | -0.004578 | -0.004578 | 62.8281 | -59.9716 | 63.0524 | -59.9854 | -60.0677 | -59.935 | -0.077819 | -0.077819 | 0.091553 | 0.19226 | 59.967 | -0.21973 | 60.0449 | -0.14191 | 0 | -0.082397 | 0.14191 | -0.013733 | 0.036621 | -0.09613 | 0.036621 | -0.09613 | 0.27008 | 123.0515 | -0.013733 | 123.024 | 122.8821 | 122.7997 | 122.8043 | 122.7997 | -122.9599 | -122.8821 | 122.9736 | 123.024 | 59.9304 | 59.967
405.8906 | 123.2346 | -59.9258 | 62.9425 | -0.052796 | 0.00091214 | 0.063854 | 0.062318 | -0.0014527 | -0.00035036 | 0.0013735 | 0.011932 | -0.0005426 | 0.06599 | 0.063284 | -0.0050586 | 0.0026746 | -0.0016493 | -0.022888 | 62.8418 | -60.0494 | 62.97 | -59.8297 | -60.1822 | 0.009155 | 0.009155 | 62.8464 | -59.9625 | 63.0524 | -59.9579 | -60.054 | -59.8709 | -0.1236 | -0.10071 | 0.027466 | 0.09613 | 59.935 | -0.25635 | 60.0586 | -0.13275 | -0.036621 | -0.09613 | 0.10986 | -0.032044 | 0.054931 | -0.12817 | 0.091552 | -0.091553 | 0.21973 | 123.0194 | 0.004577 | 123.0148 | 122.8912 | 122.8088 | 122.7676 | 122.7722 | -122.9919 | -122.905 | 122.8958 | 122.9782 | 59.903 | 59.935
406.8281 | 123.1155 | -59.9762 | 62.9471 | -0.029907 | 0.0013393 | 0.064495 | 0.068727 | 0.0011109 | 7.6842e-05 | 9.193e-05 | -0.10098 | 0.0026618 | 0.064495 | 0.063925 | -0.0037768 | 0.0033154 | -0.00036747 | -0.041199 | 62.9013 | -60.0998 | 62.9288 | -59.9075 | -60.2783 | -0.068665 | -0.086975 | 62.8784 | -59.9991 | 62.9654 | -60.0677 | -60.1593 | -59.9991 | -0.1236 | -0.045777 | -0.018311 | 0.068664 | 59.9075 | -0.30212 | 60.0311 | -0.17853 | -0.022888 | -0.068665 | 0.01831 | -0.091553 | -0.022888 | -0.18311 | 0 | -0.16022 | 0.19226 | 123.0286 | -0.068665 | 122.9645 | 123.0011 | 122.8775 | 122.8775 | 122.8546 | -123.0469 | -122.9462 | 122.905 | 122.9416 | 59.935 | 59.8892
407.8906 | 123.1293 | -59.9487 | 62.9929 | -0.037537 | 0.00048494 | 0.064068 | 0.066377 | -0.0018799 | -0.0035548 | -0.0022581 | 0.011932 | 0.0015936 | 0.065136 | 0.066915 | -0.0024952 | 0.0039562 | -0.0025037 | 0.036621 | 62.9059 | -60.0403 | 62.9791 | -59.8297 | -60.1685 | 0.059509 | -0.009155 | 62.8876 | -59.9716 | 63.002 | -60.0082 | -60.1227 | -59.9716 | -0.091553 | -0.086975 | -0.013733 | 0.11902 | 60.0082 | -0.21973 | 60.0998 | -0.12817 | -0.022889 | -0.10529 | 0.009155 | -0.05951 | -0.022889 | -0.17395 | 0 | -0.15106 | 0.21057 | 123.0194 | -0.036621 | 122.9736 | 122.9462 | 122.8592 | 122.8546 | 122.8363 | -123.0331 | -122.9645 | 122.9279 | 122.9507 | 59.9854 | 59.9396
408.8281 | 123.1522 | -59.9762 | 62.97 | -0.083313 | 0.0043301 | 0.063 | 0.070222 | 0.00025629 | 0.001145 | 9.193e-05 | -0.085724 | 0.0015936 | 0.067699 | 0.06542 | -0.004845 | 0.0071606 | -0.0010083 | -0.004578 | 62.8647 | -60.0952 | 62.9517 | -59.8618 | -60.1776 | 0 | 0.018311 | 62.9013 | -59.9854 | 63.0112 | -60.0174 | -60.1364 | -59.9533 | -0.11902 | -0.10529 | -0.018311 | 0.11444 | 59.9762 | -0.20142 | 60.0952 | -0.082397 | -0.009156 | -0.068665 | 0.041198 | -0.041199 | 0.022888 | -0.16022 | 0.032044 | -0.15106 | 0.23346 | 123.0469 | -0.032043 | 122.9965 | 122.9599 | 122.8867 | 122.8409 | 122.8775 | -123.0652 | -122.9553 | 122.9279 | 122.9874 | 59.9716 | 59.9945
409.9062 | 123.2208 | -59.935 | 62.9059 | -0.12146 | 0.0011257 | 0.063427 | 0.067018 | 0.0017517 | -0.00077756 | 0.00030553 | -0.024689 | 0.00138 | 0.064922 | 0.070547 | -0.0042042 | 0.0039562 | 0.00091433 | -0.032043 | 62.8281 | -60.0586 | 62.9883 | -59.816 | -60.1822 | -0.009155 | -0.013733 | 62.8006 | -60.0082 | 63.0615 | -59.9396 | -60.0494 | -59.8846 | -0.1236 | -0.07782 | 0.082397 | 0.11902 | 59.9258 | -0.24719 | 60.0494 | -0.1236 | -0.073242 | -0.10529 | 0.15564 | -0.004577 | 0.050354 | -0.11444 | 0.1236 | -0.041198 | 0.24262 | 123.0469 | 0.068665 | 123.0698 | 122.8867 | 122.8088 | 122.7631 | 122.7356 | -122.9645 | -122.9141 | 122.9233 | 122.9965 | 59.903 | 59.9213
410.8281 | 123.143 | -59.9533 | 62.9608 | -0.037537 | 5.7742e-05 | 0.063213 | 0.065523 | 0.0034607 | -0.0016322 | -0.0024717 | -0.058258 | 0.0011664 | 0.067058 | 0.066274 | -0.0027088 | 0.0050244 | -0.00079467 | 0.032043 | 62.9059 | -60.0586 | 62.9745 | -59.848 | -60.2097 | 0.032043 | 0.032043 | 62.8647 | -59.9762 | 63.0295 | -59.9808 | -60.1135 | -59.9304 | -0.10529 | -0.054931 | 0.013733 | 0.10529 | 59.9854 | -0.25635 | 60.0906 | -0.15106 | -0.022888 | -0.09613 | 0.068665 | -0.027466 | 0.022888 | -0.16022 | 0.045776 | -0.13733 | 0.21057 | 123.0331 | -0.004578 | 123.0057 | 122.9645 | 122.8409 | 122.8592 | 122.818 | -123.0194 | -122.937 | 122.9279 | 122.9828 | 59.9854 | 59.9854
411.8906 | 123.1201 | -59.9625 | 63.0295 | -0.060425 | 0.0021939 | 0.063641 | 0.066377 | -0.0018799 | -0.00056396 | -0.00012167 | 0.014984 | 0.0039434 | 0.06834 | 0.064352 | -0.0012134 | 0.0039562 | -0.0037855 | 0.050354 | 62.8922 | -60.0174 | 62.9837 | -59.8114 | -60.1639 | 0.064087 | 0.041199 | 62.8922 | -59.967 | 62.9929 | -60.0128 | -60.0998 | -59.9625 | -0.054932 | -0.13733 | -0.045776 | 0.15106 | 60.0266 | -0.20142 | 60.0815 | -0.14648 | -0.004578 | -0.13733 | -0.036621 | -0.050354 | 0 | -0.13733 | 0.004578 | -0.13275 | 0.20599 | 123.0011 | -0.045776 | 122.9599 | 122.9095 | 122.8592 | 122.8546 | 122.8546 | -123.0469 | -122.9965 | 122.9462 | 122.9553 | 60.0128 | 60.0037
412.8281 | 123.143 | -59.967 | 62.9654 | -0.090943 | 0.0028347 | 0.062786 | 0.068727 | 0.0019653 | -0.0035548 | 0.0037235 | -0.070465 | 0.0011664 | 0.066204 | 0.063284 | -0.002068 | 0.0037426 | -0.00036747 | -0.009155 | 62.8967 | -60.0861 | 63.002 | -59.9304 | -60.3104 | 0.036621 | 0.027466 | 62.8784 | -59.9762 | 63.0157 | -60.0082 | -60.1089 | -59.9487 | -0.11902 | -0.068664 | 0.036621 | 0.036621 | 60.0037 | -0.34332 | 60.1227 | -0.2243 | -0.009155 | -0.086975 | 0.050354 | -0.041199 | 0.018311 | -0.14191 | 0.027466 | -0.13275 | 0.15564 | 123.0881 | -0.032044 | 122.9919 | 122.9828 | 122.8546 | 122.8638 | 122.8455 | -123.0515 | -122.9416 | 122.9691 | 122.9828 | 59.9579 | 59.9945
413.8906 | 123.2162 | -59.9442 | 62.9608 | -0.029907 | 0.00091214 | 0.063427 | 0.065095 | -0.0012391 | 0.00050424 | -0.0028989 | 0.045502 | 0.0020208 | 0.065777 | 0.059439 | -0.002068 | 0.0037426 | 0.0013415 | 0.15106 | 62.915 | -60.0174 | 63.0478 | -59.7794 | -60.1089 | 0.13275 | 0.13275 | 62.8464 | -59.9442 | 63.0798 | -59.9075 | -60.0082 | -59.8801 | -0.073242 | -0.045776 | 0.086976 | 0.16479 | 60.0769 | -0.16479 | 60.1501 | -0.091553 | 0 | -0.11444 | 0.11902 | 0.036621 | 0.064087 | -0.064087 | 0.064087 | -0.064087 | 0.23804 | 123.0652 | 0.036621 | 123.024 | 122.9324 | 122.7905 | 122.8592 | 122.7905 | -122.9782 | -122.905 | 122.9919 | 123.024 | 60.0952 | 60.0769
414.8438 | 123.2391 | -59.9625 | 62.9105 | -0.083313 | 0.00069854 | 0.063854 | 0.064882 | -0.00017091 | 0.00029044 | 0.0018009 | -0.042999 | 0.0035162 | 0.067058 | 0.067129 | -0.0046314 | 0.0028882 | -0.00079467 | -0.022888 | 62.8235 | -60.1044 | 63.002 | -59.8068 | -60.1776 | -0.022888 | 0 | 62.8052 | -59.9899 | 63.0707 | -59.9487 | -60.054 | -59.8663 | -0.14191 | -0.086975 | 0.091553 | 0.15564 | 59.9396 | -0.21515 | 60.0815 | -0.073242 | -0.027466 | -0.10528 | 0.16022 | 0.013733 | 0.09613 | -0.091553 | 0.1236 | -0.064087 | 0.29755 | 123.1064 | 0.041199 | 123.0606 | 122.9279 | 122.7951 | 122.7859 | 122.7676 | -123.0148 | -122.9004 | 122.9645 | 123.0331 | 59.9396 | 59.9625
415.8281 | 123.1476 | -59.9442 | 62.9608 | -0.037537 | 0.0015529 | 0.061932 | 0.065309 | 0.0036743 | 0.00071784 | 0.0039371 | -0.039948 | 0.0035162 | 0.067699 | 0.062216 | -0.0033496 | 0.0033154 | -0.0033581 | 0.004578 | 62.883 | -60.0449 | 62.9425 | -59.8892 | -60.1685 | 0.022888 | 0.013733 | 62.8967 | -59.9533 | 63.0341 | -59.9854 | -60.1044 | -59.935 | -0.10071 | -0.077819 | -0.01831 | 0.054932 | 59.967 | -0.2243 | 60.0677 | -0.1236 | -0.009155 | -0.064086 | 0.073243 | -0.041199 | 0.009155 | -0.16022 | 0.01831 | -0.15106 | 0.15564 | 122.9874 | -0.032044 | 122.9874 | 122.9279 | 122.85 | 122.8271 | 122.8409 | -123.0057 | -122.9141 | 122.8867 | 122.9782 | 59.9487 | 59.9579
416.8906 | 123.2391 | -59.935 | 62.9379 | -0.15198 | 0.00027134 | 0.064709 | 0.064668 | -0.0046569 | -0.0024866 | 0.00051913 | 0.030243 | 0.0015936 | 0.065136 | 0.056661 | -0.004845 | 0.0041698 | 0.0024097 | -0.027466 | 62.8647 | -60.054 | 62.9608 | -59.8434 | -60.1822 | 0.013733 | 0.004578 | 62.8418 | -59.9854 | 63.0249 | -59.9487 | -60.0449 | -59.8938 | -0.11902 | -0.073242 | 0.022888 | 0.091553 | 59.9487 | -0.24719 | 60.0677 | -0.12817 | -0.050354 | -0.09613 | 0.086975 | -0.013732 | 0.041199 | -0.10986 | 0.091553 | -0.059509 | 0.21057 | 123.0148 | 0.036622 | 123.0103 | 122.9187 | 122.8271 | 122.7997 | 122.7768 | -122.9919 | -122.9233 | 122.8958 | 122.9599 | 59.9075 | 59.9396
417.8281 | 123.175 | -59.9579 | 62.9654 | -0.098572 | 0.0030483 | 0.062786 | 0.066591 | -0.0027343 | -0.0033412 | -0.00054907 | -0.070465 | 0.0028754 | 0.066631 | 0.070761 | -0.0042042 | 0.005238 | 0.00070073 | 0.022888 | 62.8967 | -60.054 | 62.9471 | -59.8206 | -60.1685 | 0.018311 | 0.041199 | 62.8693 | -59.9762 | 63.0295 | -59.9945 | -60.0906 | -59.9258 | -0.09613 | -0.068664 | -0.01831 | 0.13733 | 59.9762 | -0.21057 | 60.0723 | -0.11444 | -0.01831 | -0.09613 | 0.064087 | -0.036621 | 0.032044 | -0.13275 | 0.050354 | -0.11444 | 0.23346 | 123.0011 | -0.018311 | 123.0057 | 122.9507 | 122.8455 | 122.8546 | 122.8271 | -123.0194 | -122.9416 | 122.905 | 122.9874 | 59.9808 | 59.9991
418.8906 | 123.2391 | -59.9442 | 62.9288 | -0.12909 | -0.00058326 | 0.062145 | 0.064241 | -0.0016663 | -0.0027002 | -0.0024717 | 0.018036 | 0.0005256 | 0.066418 | 0.060934 | -0.0027088 | 0.0028882 | -0.0037855 | -0.004578 | 62.8693 | -60.054 | 63.002 | -59.7885 | -60.1547 | 0.064087 | 0.086975 | 62.8601 | -59.935 | 63.0936 | -59.9167 | -60.0082 | -59.8709 | -0.10986 | -0.059509 | 0.073242 | 0.15564 | 60.0082 | -0.21057 | 60.1181 | -0.10071 | 0.009155 | -0.068665 | 0.16479 | 0.027466 | 0.073242 | -0.064087 | 0.064087 | -0.073242 | 0.2655 | 123.056 | 0.018311 | 123.0286 | 122.9233 | 122.7951 | 122.8134 | 122.8043 | -122.9828 | -122.8638 | 122.9462 | 123.0377 | 59.9396 | 60.0311
419.8438 | 123.317 | -59.9625 | 62.8967 | -0.090943 | 0.0013393 | 0.064709 | 0.066163 | 0.0011109 | -0.00099116 | -0.0018307 | -0.018585 | 9.8198e-05 | 0.06599 | 0.063284 | -0.0056994 | 0.0056652 | -0.0016493 | -0.018311 | 62.8326 | -60.0586 | 63.0066 | -59.8068 | -60.1913 | -0.027466 | -0.004578 | 62.8189 | -59.9808 | 63.0661 | -59.935 | -60.2921 | -60.0723 | -0.096131 | -0.064087 | 0.10986 | 0.15564 | 59.935 | -0.22888 | 60.0311 | -0.13275 | -0.018311 | -0.07782 | 0.16937 | 0.027465 | -0.10986 | -0.32959 | -0.091553 | -0.31128 | 0.25177 | 123.0652 | 0.045776 | 123.0469 | 122.8912 | 122.7997 | 122.7951 | 122.7814 | -122.9553 | -122.8775 | 122.9691 | 123.0286 | 59.9442 | 59.9579
420.8906 | 123.2346 | -59.9533 | 62.9333 | -0.068054 | 0.00027134 | 0.061718 | 0.067018 | -0.0014527 | -0.003982 | -0.0020443 | 0.024139 | 0.0005256 | 0.065563 | 0.060934 | -0.0039906 | 0.0031018 | -0.0042127 | 0 | 62.8738 | -60.0449 | 63.0066 | -59.7977 | -60.1273 | 0.082397 | 0.064087 | 62.8418 | -59.9716 | 63.0844 | -59.9075 | -59.9991 | -59.8709 | -0.091553 | -0.05951 | 0.073242 | 0.15564 | 60.0357 | -0.17395 | 60.1273 | -0.082397 | -0.018311 | -0.091553 | 0.15106 | 0.045776 | 0.082397 | -0.045776 | 0.10071 | -0.027465 | 0.24719 | 123.0515 | 0.064087 | 123.056 | 122.9187 | 122.8134 | 122.8271 | 122.7951 | -122.9782 | -122.905 | 122.9599 | 123.0377 | 59.9533 | 60.0174
421.8281 | 123.1293 | -59.9762 | 63.0112 | -0.022278 | -0.0014377 | 0.062359 | 0.065309 | -0.00059811 | -0.0018458 | -0.00012167 | 0.045502 | 0.0039434 | 0.066418 | 0.064352 | -0.0042042 | 0.0026746 | -0.00015387 | -0.018311 | 62.9105 | -60.0494 | 62.9288 | -59.8846 | -60.2142 | 0.036621 | -0.21057 | 62.9196 | -59.9762 | 62.9654 | -60.022 | -60.1181 | -59.9808 | -0.073242 | -0.10071 | -0.082397 | 0.091552 | 60.0128 | -0.23804 | 60.0861 | -0.16479 | 0 | -0.091552 | -0.045776 | -0.045777 | -0.004578 | -0.14191 | -0.004578 | -0.14191 | 0.16479 | 122.9782 | -0.045777 | 122.9416 | 122.9599 | 122.8958 | 122.8867 | 122.8958 | -123.0606 | -122.9874 | 122.905 | 122.9416 | 59.9579 | 59.7656
422.8906 | 123.1979 | -59.967 | 62.9242 | -0.068054 | 0.0013393 | 0.064068 | 0.065736 | 0.0013245 | 0.00029044 | 9.193e-05 | -0.0063781 | 0.0015936 | 0.064495 | 0.059439 | -0.0035632 | 0.0028882 | -0.0014355 | -0.07782 | 62.8601 | -60.0723 | 62.9517 | -59.8526 | -60.2005 | -0.022888 | -0.050354 | 62.8281 | -59.9899 | 63.0157 | -59.9854 | -60.0952 | -59.9258 | -0.10529 | -0.064087 | 0.027466 | 0.11444 | 59.9442 | -0.23346 | 60.0494 | -0.12817 | -0.022888 | -0.09613 | 0.091553 | -0.018311 | 0.041199 | -0.12817 | 0.064087 | -0.10529 | 0.21973 | 123.024 | 0.004577 | 123.0057 | 122.9324 | 122.818 | 122.8271 | 122.7951 | -122.9965 | -122.9141 | 122.9187 | 122.9828 | 59.8892 | 59.9167
423.8281 | 123.0972 | -59.9442 | 62.9974 | -0.075684 | 0.00027134 | 0.064068 | 0.067659 | 0.00068369 | -0.0024866 | -0.0039671 | -0.024689 | 0.0020208 | 0.068767 | 0.062429 | -0.0024952 | 0.0022472 | 0.0041187 | 0.018311 | 62.9013 | -60.0403 | 62.9608 | -59.848 | -60.1593 | 0.050354 | 0.027466 | 62.9196 | -59.9854 | 62.9745 | -60.0128 | -60.1181 | -59.9854 | -0.09613 | -0.096131 | -0.036622 | 0.096131 | 59.9945 | -0.21515 | 60.0906 | -0.11902 | -0.041199 | -0.07782 | -0.022889 | -0.068664 | -0.041199 | -0.17395 | 0 | -0.13275 | 0.19226 | 123.0011 | -0.027465 | 122.9599 | 122.9416 | 122.905 | 122.8455 | 122.8638 | -123.0377 | -122.9828 | 122.905 | 122.9187 | 59.9625 | 59.9716
424.8906 | 123.1522 | -59.9716 | 62.9974 | 0.00061049 | 0.0015529 | 0.061504 | 0.066804 | 0.00025629 | -0.0014184 | 0.00051913 | -0.039948 | 0.0022346 | 0.064281 | 0.066274 | -0.0037768 | 0.0022472 | -0.0025037 | 0 | 62.9105 | -60.0723 | 62.9379 | -59.8892 | -60.2188 | 0.013733 | 0 | 62.8967 | -59.9899 | 62.9929 | -60.0082 | -60.1227 | -59.967 | -0.10071 | -0.086976 | -0.05951 | 0.082398 | 59.9854 | -0.24719 | 60.0861 | -0.14648 | -0.01831 | -0.10071 | -0.004578 | -0.036621 | 0.004578 | -0.15106 | 0.022888 | -0.13275 | 0.18311 | 123.0103 | -0.018311 | 122.9828 | 122.9828 | 122.8867 | 122.8821 | 122.8683 | -123.0698 | -122.9874 | 122.9095 | 122.9645 | 59.9716 | 59.9716
425.8281 | 123.1201 | -59.9762 | 63.0157 | 0.054016 | 0.00027134 | 0.065777 | 0.067445 | 0.00046989 | -0.002273 | -0.0022581 | -0.052155 | 0.003089 | 0.067913 | 0.07546 | -0.0027088 | 0.00182 | 0.0028369 | -0.17853 | 62.9105 | -60.0861 | 62.8922 | -59.8892 | -60.1822 | 0.045776 | 0 | 62.9196 | -59.9808 | 62.9883 | -60.0082 | -60.1135 | -59.9442 | -0.10986 | -0.10529 | -0.1236 | 0.086975 | 60.022 | -0.20599 | 60.1318 | -0.09613 | -0.004578 | -0.09613 | -0.027466 | -0.032044 | 0.032043 | -0.13733 | 0.036621 | -0.13275 | 0.19684 | 122.9782 | -0.027466 | 122.9691 | 122.9965 | 122.9004 | 122.8867 | 122.8958 | -123.1018 | -122.9965 | 122.8683 | 122.9645 | 59.7977 | 59.9762
426.8906 | 123.2025 | -59.9533 | 62.9288 | -0.060425 | 0.0032619 | 0.064495 | 0.066591 | 0.00068369 | -0.0033412 | 0.0013735 | 0.0027771 | -0.0011834 | 0.067699 | 0.06072 | -0.0042042 | 0.0041698 | 0.00070073 | -0.027466 | 62.8189 | -60.0494 | 63.002 | -59.7977 | -60.1776 | -0.004578 | 0 | 62.8143 | -59.9808 | 63.0524 | -59.9625 | -60.0632 | -59.9213 | -0.09613 | -0.10986 | 0.073242 | 0.15564 | 59.9487 | -0.2243 | 60.0449 | -0.12817 | -0.027466 | -0.11444 | 0.1236 | -0.009155 | 0.032043 | -0.10986 | 0.059509 | -0.082397 | 0.25177 | 123.0515 | 0.018311 | 123.0331 | 122.8683 | 122.7951 | 122.7722 | 122.7676 | -122.9782 | -122.9095 | 122.9553 | 123.0057 | 59.9258 | 59.9533
427.8281 | 123.1384 | -59.9396 | 62.9608 | -0.060425 | 0.0024075 | 0.062145 | 0.067445 | 0.0043151 | -0.00099116 | -0.0035397 | -0.027741 | 0.0005256 | 0.06599 | 0.065206 | -0.001427 | 0.0031018 | -0.00015387 | 0.004578 | 62.9059 | -60.0632 | 62.9425 | -59.903 | -60.2142 | 0.018311 | -0.036621 | 62.9059 | -59.9854 | 62.9837 | -59.9991 | -60.1318 | -59.9396 | -0.1236 | -0.054931 | -0.01831 | 0.036621 | 59.9579 | -0.27466 | 60.0815 | -0.15106 | -0.045777 | -0.054931 | 0.022889 | -0.059509 | 0 | -0.19226 | 0.045777 | -0.14648 | 0.16022 | 123.0057 | -0.013732 | 122.9691 | 122.9691 | 122.8912 | 122.8455 | 122.8455 | -123.024 | -122.9462 | 122.8821 | 122.9233 | 59.9442 | 59.903
428.8281 | 123.2391 | -59.9487 | 62.9517 | -0.13672 | -0.0012241 | 0.060436 | 0.065095 | 4.2692e-05 | -0.00099116 | -0.0033261 | 0.04245 | 0.0007392 | 0.066418 | 0.058157 | -0.0035632 | 0.0026746 | -0.0016493 | -0.018311 | 62.851 | -60.0494 | 63.0066 | -59.7931 | -60.1593 | 0.045776 | 0.032043 | 62.8738 | -59.967 | 63.0707 | -59.9213 | -60.0082 | -59.8846 | -0.10071 | -0.10071 | 0.054932 | 0.15564 | 59.9945 | -0.21057 | 60.0952 | -0.10986 | -0.018311 | -0.07782 | 0.11902 | 0.027465 | 0.064086 | -0.05951 | 0.082397 | -0.041199 | 0.25635 | 123.056 | 0.045776 | 123.0377 | 122.9004 | 122.8409 | 122.7997 | 122.8226 | -123.0011 | -122.9187 | 122.9553 | 123.0194 | 59.9304 | 59.9808
429.8281 | 123.2254 | -59.9121 | 62.9471 | -0.060425 | 0.0028347 | 0.061932 | 0.066163 | 0.0011109 | -0.0041956 | -0.0022581 | -0.036896 | 0.0011664 | 0.066204 | 0.066061 | -0.0037768 | 0.0028882 | -0.00036747 | 0.050354 | 62.8784 | -60.0082 | 63.0524 | -59.7473 | -60.0082 | 0.37994 | 0.064087 | 62.8372 | -59.9579 | 63.0386 | -59.8663 | -60.0128 | -59.8892 | -0.096131 | -0.068665 | 0.10529 | 0.16479 | 60.2921 | -0.096131 | 60.3882 | 0 | -0.045777 | -0.10986 | 0.091552 | 0.045776 | 0.022888 | -0.10071 | 0.068665 | -0.054931 | 0.26093 | 123.0606 | 0.091553 | 122.9965 | 122.8867 | 122.7951 | 122.7905 | 122.7493 | -122.9553 | -122.905 | 122.9645 | 122.9507 | 59.9625 | 59.9762
430.8281 | 123.23 | -59.9258 | 62.9242 | -0.060425 | 0.0017667 | 0.062359 | 0.064882 | -0.0014527 | -0.0014184 | -0.00012167 | 0.0058289 | 0.0015936 | 0.069836 | 0.064138 | -0.0029224 | 0.00032464 | -0.0018629 | 0.027466 | 62.8738 | -60.054 | 63.0249 | -59.7656 | -60.1227 | 0.07782 | 0.11444 | 62.8601 | -59.9396 | 63.089 | -59.8892 | -59.9991 | -59.848 | -0.12817 | -0.050354 | 0.10071 | 0.16022 | 60.0037 | -0.19684 | 60.1318 | -0.068665 | -0.013733 | -0.064087 | 0.16479 | 0.036621 | 0.07782 | -0.073242 | 0.091553 | -0.059509 | 0.28839 | 123.0789 | 0.050354 | 123.0286 | 122.9279 | 122.7997 | 122.7997 | 122.7859 | -122.9782 | -122.8638 | 122.9507 | 123.0148 | 59.9533 | 60.0403
431.8281 | 123.1979 | -59.9213 | 62.97 | -0.007019 | 0.0017667 | 0.064709 | 0.06595 | -0.0033753 | -0.00099116 | -0.00054907 | -0.015534 | 0.0007392 | 0.066204 | 0.062216 | -0.0033496 | 0.0028882 | 0.0013415 | 0 | 62.8555 | -60.0494 | 63.0615 | -59.7565 | -60.1044 | 0.10529 | 0.09613 | 62.8647 | -59.9533 | 63.0615 | -59.903 | -60.0174 | -59.8846 | -0.12817 | -0.11444 | 0.091552 | 0.16479 | 60.0266 | -0.18311 | 60.1547 | -0.054932 | -0.032043 | -0.10529 | 0.091552 | 0.018311 | 0.036621 | -0.09613 | 0.068664 | -0.064087 | 0.29297 | 123.111 | 0.050354 | 123.0148 | 122.905 | 122.818 | 122.7768 | 122.7859 | -123.0194 | -122.9233 | 122.9828 | 122.9828 | 59.9213 | 60.0174
432.8906 | 123.1842 | -59.9808 | 62.9333 | -0.13672 | -0.00015586 | 0.064281 | 0.0683 | 4.2692e-05 | -0.0031274 | -0.0022581 | -0.064362 | 0.00138 | 0.064281 | 0.066061 | -0.0033496 | 0.0026746 | -0.0027173 | -0.10071 | 62.8555 | -60.1089 | 62.9059 | -59.9258 | -60.2921 | -0.10529 | -0.11444 | 62.851 | -60.0082 | 63.0066 | -60.0174 | -60.1456 | -59.9579 | -0.12817 | -0.07782 | -0.027466 | 0.054932 | 59.8755 | -0.31128 | 60.0037 | -0.18311 | -0.027466 | -0.082398 | 0.073242 | -0.036621 | 0.022888 | -0.1648 | 0.050354 | -0.13733 | 0.18311 | 123.0148 | -0.009155 | 123.0148 | 122.9645 | 122.8592 | 122.8363 | 122.8317 | -123.0423 | -122.9416 | 122.8867 | 122.9874 | 59.8801 | 59.8663
433.8281 | 123.1155 | -59.9258 | 62.9745 | -0.014649 | 0.0019803 | 0.063 | 0.065523 | -0.00038451 | -0.00099116 | -0.00076267 | 0.018036 | 0.00138 | 0.066418 | 0.059225 | -0.0042042 | 0.0031018 | -0.0018629 | -0.004578 | 62.915 | -60.0494 | 62.9425 | -59.8709 | -60.2097 | 0.050354 | 0.004578 | 62.9288 | -59.9808 | 62.9883 | -60.0311 | -60.1273 | -59.9945 | -0.1236 | -0.059509 | -0.032043 | 0.054931 | 59.9762 | -0.28381 | 60.0998 | -0.16022 | -0.054932 | -0.045776 | 0.013733 | -0.10529 | -0.068665 | -0.20142 | -0.013733 | -0.14648 | 0.17853 | 122.9919 | -0.050354 | 122.9691 | 122.9645 | 122.9095 | 122.8409 | 122.8546 | -123.024 | -122.9553 | 122.8683 | 122.9141 | 59.9213 | 59.9304
434.8906 | 123.1888 | -59.9487 | 62.9196 | -0.060425 | 0.0015529 | 0.064281 | 0.064668 | -0.00017091 | -0.0035548 | -0.0026853 | -0.0063781 | 0.0005256 | 0.067058 | 0.060079 | -0.0037768 | 0.00182 | 0.00048713 | -0.045776 | 62.8555 | -60.0449 | 62.9654 | -59.8389 | -60.1913 | 0 | -0.068665 | 62.8601 | -59.9762 | 63.0066 | -59.967 | -60.0632 | -59.9121 | -0.096131 | -0.064087 | 0.045776 | 0.10986 | 59.9487 | -0.24262 | 60.0449 | -0.14648 | -0.027466 | -0.05951 | 0.086975 | -0.018311 | 0.036621 | -0.11444 | 0.064087 | -0.086975 | 0.20599 | 123.0103 | 0.009155 | 122.9828 | 122.9004 | 122.8363 | 122.8043 | 122.8088 | -122.9645 | -122.8958 | 122.9141 | 122.9553 | 59.903 | 59.8801
435.8281 | 123.1155 | -59.9762 | 62.9974 | -0.11383 | 0.00069854 | 0.063854 | 0.065736 | 0.0021789 | -0.00035036 | -0.0018307 | -0.015534 | 0.0033026 | 0.065136 | 0.066702 | -0.0035632 | 0.0022472 | -0.0022901 | 0.045776 | 62.9013 | -60.0449 | 62.9745 | -59.816 | -60.1685 | 0.07782 | 0.032043 | 62.9013 | -59.967 | 62.9654 | -59.9991 | -60.1135 | -59.9762 | -0.068665 | -0.096131 | -0.022889 | 0.16022 | 60.054 | -0.19226 | 60.1227 | -0.1236 | 0.009155 | -0.096131 | -0.032044 | -0.022888 | 0 | -0.13733 | -0.009155 | -0.14648 | 0.22888 | 123.0194 | -0.032043 | 122.9324 | 122.9462 | 122.8683 | 122.8775 | 122.8775 | -123.0423 | -122.9645 | 122.9507 | 122.9416 | 60.022 | 60.0082
436.8906 | 123.2346 | -59.9442 | 62.9288 | -0.090943 | 0.00069854 | 0.064281 | 0.06595 | 0.0013245 | -0.0033412 | -0.0024717 | -0.039948 | 0.0022346 | 0.06599 | 0.06542 | -0.0029224 | 0.0043836 | -0.00058107 | -0.041199 | 62.8235 | -60.0815 | 63.1668 | -59.6878 | -60.2142 | 0.018311 | 0.009155 | 62.8281 | -59.9808 | 63.0753 | -59.9396 | -60.0677 | -59.8984 | -0.13733 | -0.10529 | 0.23804 | 0.25635 | 59.9625 | -0.27008 | 60.0998 | -0.13275 | -0.036621 | -0.10071 | 0.14648 | 0.004578 | 0.045777 | -0.1236 | 0.082398 | -0.086975 | 0.39368 | 123.2483 | 0.041199 | 123.056 | 122.905 | 122.8088 | 122.7676 | 122.7722 | -123.0103 | -122.9095 | 123.111 | 123.0194 | 59.903 | 59.9533
437.8281 | 123.2254 | -59.9213 | 62.9288 | -0.090943 | 5.7742e-05 | 0.062359 | 0.067018 | -0.0031617 | 0.0017858 | -0.0041807 | -0.076569 | 0.0020208 | 0.062786 | 0.061788 | -0.0035632 | 0.003529 | -0.00036747 | 0.064087 | 62.8418 | -60.0311 | 63.0341 | -59.7382 | -60.0037 | 0.37994 | 0.073242 | 62.8418 | -59.967 | 63.0661 | -59.8709 | -59.9945 | -59.8984 | -0.10986 | -0.086975 | 0.10529 | 0.18311 | 60.3012 | -0.082397 | 60.4111 | 0.027466 | -0.045776 | -0.086975 | 0.13733 | 0.050354 | 0.022889 | -0.073242 | 0.068665 | -0.027466 | 0.29297 | 123.0652 | 0.09613 | 123.0331 | 122.8729 | 122.8088 | 122.7631 | 122.7631 | -122.9599 | -122.8958 | 122.9553 | 122.9874 | 59.9854 | 59.9945
438.8906 | 123.1338 | -59.9808 | 62.97 | -0.090943 | 0.0026211 | 0.063213 | 0.065309 | 0.0066651 | -0.0014184 | 0.0020145 | -0.11319 | 0.0007392 | 0.066845 | 0.068411 | -0.006554 | 0.0037426 | -0.0046399 | -0.013733 | 62.8693 | -60.0998 | 62.9333 | -59.7748 | -60.2371 | 0.018311 | -0.004578 | 62.8738 | -59.967 | 63.002 | -59.9991 | -60.1135 | -59.9442 | -0.11902 | -0.10071 | -0.036621 | 0.20599 | 59.9991 | -0.25635 | 60.1181 | -0.13733 | 0.013733 | -0.096131 | 0.032043 | -0.01831 | 0.036621 | -0.13275 | 0.022888 | -0.14648 | 0.32501 | 123.0331 | -0.032043 | 122.9691 | 122.9691 | 122.8409 | 122.85 | 122.8546 | -123.0698 | -122.937 | 122.9141 | 122.9828 | 59.967 | 59.9762
439.8281 | 123.262 | -59.9121 | 62.9608 | -0.083313 | 0.00048494 | 0.060009 | 0.064241 | -0.0018799 | -0.00035036 | 0.0013735 | 0.027191 | 0.0024482 | 0.065777 | 0.060079 | -0.0027088 | 0.0043836 | 0.0045459 | 0.050354 | 62.8601 | -60.0082 | 63.0524 | -59.7107 | -60.0723 | 0.11444 | 0.1236 | 62.851 | -59.9442 | 63.0798 | -59.8709 | -59.9854 | -59.8572 | -0.096131 | -0.10071 | 0.091553 | 0.20142 | 60.0266 | -0.16022 | 60.1227 | -0.064087 | -0.032044 | -0.10986 | 0.11902 | 0.041198 | 0.054931 | -0.073243 | 0.086975 | -0.041199 | 0.29755 | 123.0606 | 0.073242 | 123.024 | 122.8683 | 122.7951 | 122.7722 | 122.7631 | -122.9691 | -122.905 | 122.9645 | 122.9919 | 59.9625 | 60.0357
440.8906 | 123.1247 | -59.9808 | 62.9745 | -0.090943 | 0.00048494 | 0.064495 | 0.067659 | -0.0040161 | -0.00013676 | -0.0022581 | -0.085724 | 0.0011664 | 0.066418 | 0.07247 | -0.0029224 | 0.00096564 | 0.00048713 | -0.10071 | 62.8876 | -60.1044 | 62.8784 | -59.9579 | -60.3058 | -0.11902 | -0.15106 | 62.8601 | -60.0082 | 63.1165 | -60.1135 | -60.1822 | -59.9442 | -0.1236 | -0.086975 | -0.09613 | 0.022888 | 59.8618 | -0.32501 | 59.9854 | -0.20142 | -0.027466 | -0.11444 | 0.14191 | -0.13275 | 0.036621 | -0.20142 | 0.064087 | -0.17395 | 0.14648 | 122.9828 | -0.10529 | 123.1247 | 122.9919 | 122.8683 | 122.8683 | 122.8409 | -123.0789 | -122.9828 | 122.8592 | 123.0972 | 59.8801 | 59.8297
441.8281 | 123.2391 | -59.9442 | 62.9242 | -0.1062 | 0.0013393 | 0.063 | 0.063814 | 0.00068369 | 7.6842e-05 | -0.00054907 | 0.039398 | 0.003089 | 0.064709 | 0.061575 | -0.0046314 | 0.0011792 | -0.00036747 | 0.036621 | 62.8647 | -60.0174 | 63.0569 | -59.729 | -60.0769 | 0.11902 | 0.12817 | 62.8464 | -59.9304 | 63.1485 | -59.9899 | -60.0082 | -59.8251 | -0.073242 | -0.059509 | 0.13275 | 0.21515 | 60.0632 | -0.13275 | 60.1364 | -0.059509 | 0.013733 | -0.077819 | 0.22431 | -0.045776 | 0.11902 | -0.064087 | 0.10529 | -0.07782 | 0.28839 | 123.0743 | -0.059509 | 123.0789 | 122.8821 | 122.7768 | 122.8088 | 122.7905 | -122.9416 | -122.8546 | 123.0011 | 123.0927 | 59.9808 | 60.0723
442.8906 | 123.143 | -59.9854 | 62.9837 | -0.068054 | 0.0017667 | 0.063213 | 0.067232 | -0.0018799 | -0.0029138 | -0.0020443 | -0.14981 | 0.0024482 | 0.064495 | 0.066915 | -0.0037768 | 0.0033154 | 0.0041187 | -0.004578 | 62.8922 | -60.0723 | 62.9471 | -59.8389 | -60.2142 | 0.041199 | 0.082397 | 62.8738 | -59.9808 | 63.0249 | -59.9991 | -60.1135 | -59.9396 | -0.086975 | -0.091553 | -0.036621 | 0.14648 | 60.0266 | -0.22888 | 60.1135 | -0.14191 | 0.004578 | -0.10986 | 0.041198 | -0.013732 | 0.045777 | -0.12817 | 0.041199 | -0.13275 | 0.23346 | 123.0194 | -0.01831 | 123.0057 | 122.9645 | 122.8546 | 122.8775 | 122.8592 | -123.056 | -122.9645 | 122.9324 | 123.0103 | 59.9808 | 60.0677
443.8281 | 123.2391 | -59.935 | 62.9608 | -0.13672 | 0.00069854 | 0.062572 | 0.06595 | -0.0031617 | -0.0041956 | -0.00097627 | 0.011932 | 0.0007392 | 0.06364 | 0.062856 | -0.0018542 | 0.0016064 | 0.0017687 | 0.018311 | 62.8693 | -60.0311 | 63.0569 | -59.7107 | -60.0861 | 0.10986 | 0.15564 | 62.8555 | -59.9396 | 63.0844 | -59.8618 | -59.9945 | -59.8526 | -0.09613 | -0.091552 | 0.096131 | 0.22431 | 60.0449 | -0.15106 | 60.141 | -0.054932 | -0.004577 | -0.10528 | 0.1236 | 0.073243 | 0.082398 | -0.059509 | 0.086975 | -0.054932 | 0.32044 | 123.0881 | 0.07782 | 123.024 | 122.9004 | 122.7951 | 122.8043 | 122.7905 | -122.9919 | -122.9004 | 122.9919 | 123.0194 | 59.9533 | 60.0906
444.8906 | 123.1064 | -59.9808 | 62.9517 | -0.083313 | 0.00091214 | 0.063854 | 0.068086 | -0.0010253 | 0.00050424 | -0.0016171 | -0.06131 | 0.0018072 | 0.068554 | 0.061361 | -0.00078617 | 0.0031018 | 0.0036913 | -0.091553 | 62.8693 | -60.1089 | 62.8876 | -59.903 | -60.2829 | -0.10986 | -0.1236 | 62.8693 | -60.0174 | 62.9837 | -60.054 | -60.1685 | -59.9808 | -0.12817 | -0.082397 | -0.064087 | 0.07782 | 59.8709 | -0.30212 | 59.9991 | -0.17395 | -0.036621 | -0.082397 | 0.032044 | -0.073242 | 0 | -0.18768 | 0.036621 | -0.15106 | 0.20599 | 122.9965 | -0.036621 | 123.0011 | 122.9782 | 122.8867 | 122.85 | 122.85 | -123.0606 | -122.9691 | 122.8683 | 122.9645 | 59.8892 | 59.8572
445.8281 | 123.2437 | -59.9396 | 62.9517 | -0.17487 | 0.00048494 | 0.063641 | 0.06595 | -0.0010253 | -0.00056396 | -0.0026853 | 0.0027771 | 0.0007392 | 0.063427 | 0.063284 | -0.0029224 | 0.0045972 | -0.0014355 | 0.009155 | 62.851 | -60.0403 | 63.0157 | -59.7885 | -60.1181 | 0.082397 | 0.07782 | 62.8464 | -59.9533 | 63.1073 | -59.9167 | -59.9579 | -59.8297 | -0.10071 | -0.10071 | 0.064087 | 0.15106 | 60.022 | -0.17853 | 60.1227 | -0.07782 | -0.013733 | -0.10528 | 0.15564 | 0.022888 | 0.10986 | -0.018311 | 0.1236 | -0.004578 | 0.25177 | 123.056 | 0.036621 | 123.0606 | 122.8912 | 122.7997 | 122.7905 | 122.7859 | -122.9919 | -122.905 | 122.9553 | 123.0469 | 59.9487 | 60.0174
446.8281 | 123.1842 | -59.9716 | 62.9242 | -0.045166 | 0.0017667 | 0.062145 | 0.065523 | 0.0034607 | -0.0014184 | -0.0020443 | 0.014984 | 0.0007392 | 0.064922 | 0.060293 | -0.0042042 | 0.0026746 | -0.0010083 | -0.086975 | 62.8464 | -60.0677 | 62.9517 | -59.8434 | -60.2097 | -0.036621 | -0.07782 | 62.8326 | -59.9762 | 63.0112 | -59.9899 | -60.0861 | -59.9121 | -0.09613 | -0.077819 | 0.027466 | 0.12817 | 59.935 | -0.23804 | 60.0311 | -0.14191 | -0.004577 | -0.091552 | 0.086975 | -0.01831 | 0.05951 | -0.11444 | 0.064087 | -0.10986 | 0.2243 | 123.0194 | -0.013733 | 122.9874 | 122.9141 | 122.8088 | 122.818 | 122.8043 | -122.9919 | -122.9004 | 122.9233 | 122.9828 | 59.8846 | 59.8938
447.8906 | 123.1338 | -59.967 | 62.9654 | -0.12146 | 0.0011257 | 0.06535 | 0.066804 | 0.0021789 | -0.0024866 | -0.00033547 | -0.10098 | 0.0033026 | 0.067486 | 0.06072 | 0.00135 | 0.0071606 | 0.00091433 | -0.11444 | 62.8738 | -60.1089 | 62.883 | -59.9625 | -60.2966 | -0.10986 | -0.17853 | 62.8922 | -60.0357 | 62.8143 | -59.7519 | -60.1501 | -60.0494 | -0.14191 | -0.091553 | -0.082397 | 0.004578 | 59.8572 | -0.32959 | 59.9991 | -0.18768 | -0.068665 | -0.073242 | -0.15106 | 0.21515 | -0.082397 | -0.1831 | -0.013732 | -0.11444 | 0.14648 | 122.9919 | 0.28381 | 122.85 | 122.9828 | 122.9279 | 122.8409 | 122.8592 | -123.0743 | -123.0011 | 122.85 | 122.7814 | 59.8526 | 59.7885
448.8281 | 123.1979 | -59.9396 | 62.9425 | -0.083313 | 0.0021939 | 0.064709 | 0.065736 | -0.0014527 | -0.0031274 | -0.0043943 | 0.021088 | 0.003089 | 0.066845 | 0.062216 | -0.0024952 | 0.0020336 | -0.0018629 | -0.032043 | 62.883 | -60.0403 | 62.9654 | -59.8251 | -60.1776 | 0.022888 | -0.013733 | 62.8784 | -59.967 | 63.0478 | -59.9487 | -60.0311 | -59.8846 | -0.10071 | -0.059509 | 0.022888 | 0.11444 | 59.9625 | -0.23804 | 60.0632 | -0.13733 | -0.027466 | -0.064087 | 0.10529 | -0.009155 | 0.054931 | -0.091553 | 0.082397 | -0.064087 | 0.21515 | 123.0057 | 0.018311 | 123.0148 | 122.9233 | 122.8455 | 122.8226 | 122.818 | -122.9828 | -122.9095 | 122.905 | 122.9874 | 59.9075 | 59.9258
449.8906 | 123.1659 | -59.9716 | 62.9105 | -0.052796 | -0.00015586 | 0.061504 | 0.067018 | -0.00017091 | -0.0020594 | -0.00076267 | -0.070465 | 0.0015936 | 0.065563 | 0.069479 | -0.0039906 | 0.0045972 | -0.0012219 | -0.09613 | 62.8693 | -60.1089 | 62.9059 | -59.8984 | -60.2646 | -0.09613 | -0.10529 | 62.8647 | -60.0082 | 63.0112 | -60.0082 | -60.1227 | -59.9304 | -0.13733 | -0.041198 | -0.004577 | 0.073243 | 59.8755 | -0.29297 | 60.0128 | -0.15564 | -0.036621 | -0.045776 | 0.10071 | -0.036621 | 0.041199 | -0.15106 | 0.07782 | -0.11444 | 0.21057 | 123.0148 | 0 | 123.0194 | 122.9782 | 122.8729 | 122.8409 | 122.8363 | -123.0194 | -122.9187 | 122.8775 | 122.9828 | 59.8755 | 59.8663
450.8281 | 123.1796 | -59.9579 | 62.9608 | -0.090943 | 0.0015529 | 0.062145 | 0.066591 | 0.00089729 | -0.00013676 | -0.0020443 | 0.0027771 | 0.0005256 | 0.066204 | 0.067129 | -0.0037768 | 0.0039562 | -0.0016493 | -0.064087 | 62.8464 | -60.0586 | 62.9471 | -59.8389 | -60.2097 | -0.013733 | -0.07782 | 62.8326 | -59.9899 | 63.0203 | -59.9899 | -60.0815 | -59.9075 | -0.10071 | -0.11444 | -0.013732 | 0.11902 | 59.9442 | -0.25177 | 60.0449 | -0.15106 | -0.032043 | -0.12817 | 0.05951 | -0.032043 | 0.050354 | -0.1236 | 0.082397 | -0.091553 | 0.21973 | 123.0057 | 0 | 123.0103 | 122.905 | 122.8226 | 122.8043 | 122.7905 | -123.0194 | -122.9507 | 122.905 | 122.9782 | 59.8938 | 59.8801
451.8906 | 123.2849 | -59.9487 | 62.915 | -0.12146 | 0.0011257 | 0.063854 | 0.066163 | 0.0015381 | -0.002273 | 0.00073273 | -0.042999 | 0.0011664 | 0.065136 | 0.066488 | -0.0071948 | 0.003529 | 0.0032641 | -0.050354 | 62.8189 | -60.0723 | 62.9974 | -59.7885 | -60.1776 | -0.032043 | -0.022888 | 62.8235 | -59.9945 | 63.1943 | -60.228 | -60.0861 | -59.7427 | -0.1236 | -0.09613 | 0.082398 | 0.16022 | 59.9167 | -0.22888 | 60.0403 | -0.10529 | -0.045777 | -0.091553 | 0.27924 | -0.27924 | 0.20599 | -0.13733 | 0.25177 | -0.091553 | 0.28381 | 123.0698 | -0.23346 | 123.1888 | 122.8912 | 122.818 | 122.7676 | 122.7722 | -122.9874 | -122.9095 | 122.9462 | 123.143 | 59.8984 | 59.9258
452.8281 | 123.1979 | -59.9533 | 62.9425 | -0.1062 | 0.0011257 | 0.063 | 0.067018 | -0.00038451 | 0.0019994 | -0.0024717 | -0.012482 | -0.001397 | 0.067913 | 0.060079 | -0.0029224 | 0.0028882 | -0.0042127 | -0.059509 | 62.8464 | -60.054 | 62.9425 | -59.8343 | -60.1913 | -0.013733 | -0.07782 | 62.8555 | -59.9762 | 63.0112 | -59.9991 | -60.0861 | -59.9167 | -0.10071 | -0.09613 | 0 | 0.11902 | 59.9396 | -0.23804 | 60.0403 | -0.13733 | -0.022888 | -0.086975 | 0.068664 | -0.045776 | 0.036621 | -0.13275 | 0.059509 | -0.10986 | 0.21973 | 122.9965 | -0.022888 | 122.9874 | 122.9004 | 122.8317 | 122.7997 | 122.8088 | -122.9965 | -122.9187 | 122.8958 | 122.9645 | 59.8938 | 59.8755
453.8906 | 123.1613 | -59.9716 | 62.9471 | -0.11383 | 0.00027134 | 0.063 | 0.066804 | -0.0020935 | -0.00056396 | 0.0011599 | -0.088776 | 0.0028754 | 0.066418 | 0.06777 | -0.0035632 | 0.0026746 | 5.9726e-05 | 0 | 62.883 | -60.0677 | 62.9837 | -59.8389 | -60.2051 | 0.027466 | 0.027466 | 62.8967 | -59.9716 | 63.0249 | -59.9808 | -60.1135 | -59.9304 | -0.09613 | -0.064087 | 0.036621 | 0.13275 | 59.9991 | -0.23346 | 60.0952 | -0.13733 | 0 | -0.050354 | 0.077819 | -0.009155 | 0.041199 | -0.14191 | 0.041199 | -0.14191 | 0.22888 | 123.0515 | -0.009155 | 122.9965 | 122.9507 | 122.8683 | 122.8546 | 122.8683 | -123.0148 | -122.9187 | 122.9553 | 122.9965 | 59.9716 | 59.9991
454.8281 | 123.2117 | -59.9625 | 62.9242 | -0.068054 | 0.0021939 | 0.061718 | 0.066804 | 0.0015381 | -0.00099116 | -0.0031125 | 0.033295 | 0.0007392 | 0.067058 | 0.06777 | -0.0024952 | 0.0016064 | -0.00079467 | -0.064087 | 62.883 | -60.0586 | 62.9562 | -59.8251 | -60.2051 | 0.022888 | -0.013733 | 62.8601 | -59.967 | 63.0386 | -59.9533 | -60.0494 | -59.8846 | -0.096131 | -0.041198 | 0.032044 | 0.13733 | 59.9854 | -0.24262 | 60.0815 | -0.14648 | -0.004578 | -0.064087 | 0.11444 | 0.009155 | 0.077819 | -0.086975 | 0.082397 | -0.082397 | 0.23346 | 123.0148 | 0.013733 | 123.0057 | 122.9416 | 122.8271 | 122.8455 | 122.8226 | -122.9828 | -122.8912 | 122.9187 | 123.0011 | 59.8984 | 59.9487
455.8281 | 123.2208 | -59.935 | 62.9288 | -0.052796 | 0.00027134 | 0.062145 | 0.064241 | -0.00059811 | -0.0016322 | 0.00030553 | -0.036896 | -0.0001154 | 0.067058 | 0.062429 | -0.0039906 | 0.0039562 | -0.0025037 | -0.054932 | 62.8464 | -60.054 | 63.0707 | -59.8068 | -60.2921 | 0 | -0.032043 | 62.851 | -59.9762 | 63.0386 | -59.9899 | -60.0632 | -59.9258 | -0.11902 | -0.082397 | 0.14191 | 0.12817 | 59.935 | -0.35706 | 60.054 | -0.23804 | -0.041198 | -0.07782 | 0.10986 | -0.054931 | 0.009156 | -0.12817 | 0.050354 | -0.086975 | 0.24719 | 123.1247 | -0.013733 | 123.0148 | 122.9004 | 122.8271 | 122.7814 | 122.7859 | -122.9828 | -122.905 | 123.0057 | 122.9736 | 59.8801 | 59.903
456.8906 | 123.111 | -60.0082 | 62.9608 | -0.022278 | 0.0013393 | 0.063213 | 0.0683 | 0.0045289 | 0.00029044 | 0.0024417 | -0.094879 | 0.0015936 | 0.065563 | 0.065847 | -0.0044178 | 0.0013928 | 0.00048713 | -0.059509 | 62.8693 | -60.0952 | 62.9288 | -59.9075 | -60.2737 | -0.068665 | -0.10529 | 62.8876 | -59.9854 | 62.9791 | -60.0632 | -60.1822 | -59.9808 | -0.086975 | -0.091552 | -0.032043 | 0.10071 | 59.9396 | -0.2655 | 60.0266 | -0.17853 | 0.022888 | -0.073242 | 0.018311 | -0.054931 | 0.027466 | -0.17395 | 0.004578 | -0.19684 | 0.18768 | 123.024 | -0.077819 | 122.9645 | 122.9645 | 122.8729 | 122.8775 | 122.8958 | -123.056 | -122.9462 | 122.937 | 122.9874 | 59.9487 | 59.903
457.8281 | 123.1796 | -59.9304 | 62.9379 | -0.083313 | 0.0019803 | 0.064495 | 0.06595 | 0.00089729 | -0.003982 | 0.00073273 | -0.0033265 | -0.0001154 | 0.06599 | 0.061361 | -0.0042042 | 0.0011792 | -0.00079467 | -0.073242 | 62.8555 | -60.0769 | 62.9517 | -59.8434 | -60.2005 | -0.013733 | -0.073242 | 62.8235 | -59.9899 | 63.0157 | -59.9899 | -60.0815 | -59.9304 | -0.14648 | -0.082397 | 0.013733 | 0.086975 | 59.9167 | -0.27008 | 60.0632 | -0.1236 | -0.059509 | -0.11444 | 0.07782 | -0.059509 | 0 | -0.15106 | 0.059509 | -0.091553 | 0.23346 | 123.0286 | 0 | 123.0057 | 122.9324 | 122.8134 | 122.7859 | 122.7539 | -123.0148 | -122.9279 | 122.8821 | 122.9462 | 59.8572 | 59.8572
458.8906 | 123.0927 | -59.9854 | 62.97 | -0.1062 | -0.00058326 | 0.064495 | 0.066804 | 0.0015381 | -0.00077756 | -0.00076267 | -0.085724 | 0.0009528 | 0.065777 | 0.064352 | -0.0027088 | 0.0022472 | 5.9726e-05 | -0.11902 | 62.8555 | -60.1181 | 62.8784 | -59.9396 | -60.3241 | -0.11444 | -0.17853 | 62.8555 | -60.0082 | 63.121 | -60.1639 | -60.1639 | -59.9396 | -0.13275 | -0.11444 | -0.091553 | 0.045777 | 59.8709 | -0.33875 | 60.0037 | -0.20599 | -0.022888 | -0.11444 | 0.15106 | -0.17853 | 0.045777 | -0.17853 | 0.068665 | -0.15564 | 0.17853 | 122.9965 | -0.15564 | 123.1293 | 122.9736 | 122.8638 | 122.8409 | 122.8409 | -123.0881 | -122.9782 | 122.8638 | 123.1064 | 59.8663 | 59.8068
459.8281 | 123.1934 | -59.9487 | 62.9379 | -0.075684 | -0.00036966 | 0.06535 | 0.066163 | -0.0012391 | -0.0012048 | -0.0020443 | -0.0033265 | 0.0007392 | 0.065349 | 0.061575 | -0.003136 | 0.0033154 | 0.00070073 | -0.07782 | 62.8326 | -60.054 | 62.9425 | -59.848 | -60.2097 | -0.009155 | -0.059509 | 62.8555 | -59.9854 | 63.0157 | -59.9808 | -60.0723 | -59.9213 | -0.10529 | -0.10529 | 0.004578 | 0.10071 | 59.9396 | -0.26093 | 60.0449 | -0.15564 | -0.036622 | -0.082397 | 0.07782 | -0.032044 | 0.027465 | -0.1236 | 0.064087 | -0.086975 | 0.20599 | 122.9965 | 0.004578 | 123.0011 | 122.8867 | 122.8409 | 122.7814 | 122.8043 | -122.9919 | -122.9233 | 122.8912 | 122.9645 | 59.8709 | 59.8892
460.8906 | 123.1384 | -59.9808 | 62.9608 | -0.052796 | 0.00091214 | 0.061077 | 0.067659 | 0.00025629 | -0.0018458 | 0.00051913 | -0.073517 | 0.0026618 | 0.064922 | 0.06777 | -0.0037768 | 0.0045972 | 5.9726e-05 | -0.004578 | 62.8693 | -60.0632 | 62.9654 | -59.8526 | -60.1959 | 0.009155 | 0.013733 | 62.8876 | -59.9899 | 63.0249 | -59.9854 | -60.1135 | -59.9304 | -0.082397 | -0.091552 | 0.004578 | 0.12817 | 59.9899 | -0.21515 | 60.0723 | -0.13275 | -0.009155 | -0.073242 | 0.064087 | -0.004578 | 0.050354 | -0.13275 | 0.059509 | -0.1236 | 0.21057 | 123.0286 | 0.004577 | 123.0148 | 122.9324 | 122.8775 | 122.85 | 122.8683 | -123.024 | -122.9507 | 122.9462 | 123.0057 | 59.9762 | 59.9945
461.8281 | 123.1842 | -59.967 | 62.9288 | -0.12909 | 0.0011257 | 0.063427 | 0.063814 | -0.0012391 | -0.0027002 | -0.0016171 | 0.0027771 | 0.0011664 | 0.064495 | 0.062002 | -0.0033496 | 0.0022472 | -0.0039991 | -0.059509 | 62.8647 | -60.0357 | 62.9562 | -59.8343 | -60.1868 | 0 | -0.050354 | 62.8418 | -59.9945 | 63.0249 | -59.9991 | -60.054 | -59.9213 | -0.068665 | -0.064087 | 0.027466 | 0.13275 | 59.967 | -0.21973 | 60.0357 | -0.15106 | -0.027466 | -0.086975 | 0.09613 | -0.032043 | 0.045776 | -0.086975 | 0.073242 | -0.059509 | 0.20142 | 122.9919 | -0.004577 | 123.0194 | 122.9004 | 122.8363 | 122.8317 | 122.8088 | -122.9645 | -122.9233 | 122.9233 | 122.9919 | 59.9075 | 59.9167
462.8906 | 123.0927 | -59.9991 | 62.9608 | -0.090943 | -0.00015586 | 0.063854 | 0.06595 | 0.00068369 | -0.002273 | -0.0050351 | -0.11014 | -0.000329 | 0.067486 | 0.067983 | -0.0035632 | 0.003529 | 0.00027333 | -0.07782 | 62.8647 | -60.0952 | 62.8738 | -59.9579 | -60.3241 | -0.1236 | -0.20142 | 62.8601 | -60.0266 | 62.9608 | -60.0861 | -60.2051 | -60.0174 | -0.096131 | -0.09613 | -0.086975 | 0.041198 | 59.8755 | -0.32501 | 59.9716 | -0.22888 | -0.027466 | -0.10071 | 0 | -0.086976 | -0.018311 | -0.20599 | 0.009155 | -0.17853 | 0.13733 | 122.9691 | -0.05951 | 122.9874 | 122.9599 | 122.8867 | 122.8638 | 122.8592 | -123.056 | -122.9874 | 122.8729 | 122.9599 | 59.9213 | 59.7977
463.8281 | 123.1979 | -59.9716 | 62.915 | -0.14435 | 0.0019803 | 0.06535 | 0.061677 | -0.0012391 | -0.0033412 | -0.00012167 | -0.0033265 | 0.0005256 | 0.06599 | 0.05837 | -0.0024952 | 0.0050244 | -0.0033581 | -0.064087 | 62.8189 | -60.0586 | 62.9791 | -59.7839 | -60.1959 | -0.018311 | -0.009155 | 62.8143 | -59.9625 | 63.0432 | -59.9808 | -60.0632 | -59.9121 | -0.086975 | -0.09613 | 0.064087 | 0.18768 | 59.9533 | -0.2243 | 60.0403 | -0.13733 | 0.009156 | -0.10071 | 0.12817 | -0.009155 | 0.05951 | -0.091552 | 0.050354 | -0.10071 | 0.27466 | 123.0377 | -0.018311 | 123.0057 | 122.8775 | 122.7768 | 122.7905 | 122.7859 | -122.9736 | -122.8775 | 122.9507 | 123.0148 | 59.9075 | 59.9625
464.8906 | 123.0835 | -59.9945 | 62.9288 | -0.090943 | 0.0015529 | 0.064922 | 0.0683 | -0.00017091 | 0.00093144 | -0.0018307 | -0.082672 | 0.0037298 | 0.066418 | 0.065206 | -0.003136 | 0.0041698 | -0.0014355 | -0.045776 | 62.8601 | -60.0861 | 62.9105 | -59.9121 | -60.2509 | -0.059509 | -0.11444 | 62.8693 | -60.0082 | 62.9517 | -60.0632 | -60.2097 | -60.0037 | -0.091553 | -0.068665 | -0.018311 | 0.082398 | 59.935 | -0.25635 | 60.0266 | -0.16479 | -0.013733 | -0.059509 | 0.022888 | -0.068664 | -0.009155 | -0.21515 | 0.004578 | -0.20142 | 0.17395 | 122.9965 | -0.054931 | 122.9599 | 122.9462 | 122.8775 | 122.8546 | 122.8638 | -123.0148 | -122.937 | 122.905 | 122.9462 | 59.9487 | 59.8801
465.8281 | 123.1842 | -59.9579 | 62.9562 | 0.22186 | 0.00091214 | 0.063641 | 0.066163 | -0.00059811 | -0.0027002 | 0.0011599 | 0.030243 | -0.001397 | 0.06599 | 0.063711 | -0.0042042 | 0.0022472 | 0.0047595 | -0.018311 | 62.8784 | -60.0449 | 62.9517 | -59.8572 | -60.1776 | 0 | -0.032043 | 62.8372 | -59.9625 | 63.0615 | -59.9487 | -60.0403 | -59.8984 | -0.086975 | -0.07782 | -0.004578 | 0.10071 | 59.9579 | -0.21973 | 60.0449 | -0.13275 | -0.004577 | -0.11902 | 0.10529 | 0.009156 | 0.05951 | -0.082397 | 0.064087 | -0.07782 | 0.18768 | 122.9965 | 0.013733 | 123.024 | 122.9233 | 122.7997 | 122.8363 | 122.7951 | -123.0011 | -122.9187 | 122.9095 | 123.0194 | 59.9396 | 59.9258
466.8906 | 123.0972 | -59.9533 | 62.9791 | -0.037537 | 0.0013393 | 0.06065 | 0.066804 | -0.0052979 | 0.00029044 | 0.00094633 | -0.012482 | 0.0020208 | 0.067272 | 0.065634 | -0.0022816 | 0.0033154 | -0.0020765 | -0.054932 | 62.9242 | -60.0494 | 62.915 | -59.8709 | -60.2097 | 0.050354 | -0.018311 | 62.9242 | -59.9808 | 62.9791 | -60.0082 | -60.1318 | -59.9854 | -0.09613 | -0.054932 | -0.064087 | 0.082397 | 60.0037 | -0.25635 | 60.0998 | -0.16022 | -0.027466 | -0.054932 | 0 | -0.054932 | -0.032044 | -0.17853 | -0.004578 | -0.15106 | 0.17853 | 122.9645 | -0.027466 | 122.9599 | 122.9736 | 122.905 | 122.8775 | 122.8775 | -123.0286 | -122.9599 | 122.8683 | 122.9324 | 59.8984 | 59.935
467.8281 | 123.2254 | -59.9396 | 62.915 | -0.11383 | 0.00048494 | 0.061932 | 0.066804 | 4.2692e-05 | -0.0014184 | -0.00076267 | -0.018585 | 0.0007392 | 0.064709 | 0.064993 | -0.0056994 | 0.0050244 | 0.0034777 | 0.086975 | 62.851 | -60.0632 | 63.0249 | -59.816 | -60.1868 | 0 | -0.018311 | 62.8281 | -59.9945 | 63.0707 | -59.9487 | -60.054 | -59.903 | -0.1236 | -0.064087 | 0.10986 | 0.1236 | 59.9396 | -0.24719 | 60.0632 | -0.1236 | -0.054932 | -0.086975 | 0.15564 | -0.009155 | 0.036621 | -0.11444 | 0.091553 | -0.059509 | 0.24719 | 123.0881 | 0.045777 | 123.0652 | 122.9141 | 122.8226 | 122.7905 | 122.7676 | -122.9782 | -122.9095 | 122.9645 | 123.0103 | 60.0266 | 59.9213
468.8281 | 123.2254 | -59.9487 | 62.9013 | -0.052796 | 0.0013393 | 0.062572 | 0.067018 | 0.0036743 | -0.0031274 | 0.00094633 | 0.06076 | 0.0015936 | 0.063427 | 0.064779 | -0.0039906 | 0.0011792 | 0.0036913 | -0.036621 | 62.8326 | -60.0677 | 62.9974 | -59.7748 | -60.4294 | -0.20599 | -0.07782 | 62.851 | -59.9808 | 63.0615 | -59.9762 | -60.0403 | -59.8801 | -0.11902 | -0.068664 | 0.096131 | 0.17395 | 59.7427 | -0.48065 | 59.8618 | -0.36163 | -0.032044 | -0.050354 | 0.16022 | -0.027466 | 0.068664 | -0.091553 | 0.10071 | -0.059509 | 0.29297 | 123.0652 | 0.004578 | 123.0423 | 122.9004 | 122.8317 | 122.7814 | 122.7997 | -122.9691 | -122.8821 | 122.9462 | 123.0103 | 59.9121 | 59.8709
469.8906 | 123.1796 | -59.9487 | 62.9288 | -0.052796 | 0.0015529 | 0.062786 | 0.067659 | 0.00046989 | -0.0018458 | 0.00030553 | -0.082672 | 0.0003118 | 0.064495 | 0.067129 | -0.003136 | 0.0048108 | -0.0029309 | -0.009155 | 62.8784 | -60.0906 | 62.9608 | -59.8297 | -60.1959 | 0.027466 | 0.032043 | 62.8922 | -59.9762 | 63.0295 | -59.9991 | -60.1044 | -59.9304 | -0.14191 | -0.050354 | 0.032043 | 0.11902 | 59.9762 | -0.24719 | 60.1181 | -0.10529 | -0.027466 | -0.036621 | 0.10071 | -0.050354 | 0.01831 | -0.15564 | 0.045776 | -0.12817 | 0.26093 | 123.0515 | -0.022888 | 123.0057 | 122.9691 | 122.8683 | 122.8271 | 122.8409 | -123.0194 | -122.905 | 122.9095 | 122.9782 | 59.9396 | 59.9808
470.8281 | 123.1064 | -59.9899 | 62.9425 | -0.068054 | 0.00091214 | 0.061077 | 0.065095 | 0.00025629 | 0.00071784 | -0.0011899 | -0.049103 | 0.0035162 | 0.066204 | 0.063284 | -0.003136 | 0.0041698 | -0.0033581 | -0.086975 | 62.851 | -60.1135 | 62.9288 | -60.173 | -60.5942 | 0.032043 | -0.15564 | 62.8967 | -60.0128 | 62.9425 | -60.0677 | -60.1822 | -59.9945 | -0.1236 | -0.091553 | -0.013733 | -0.18311 | 60.022 | -0.60425 | 60.1456 | -0.48065 | -0.022888 | -0.045776 | 0 | -0.07782 | -0.004578 | -0.19226 | 0.01831 | -0.16937 | -0.05951 | 123.0423 | -0.054932 | 122.9553 | 122.9645 | 122.9095 | 122.8409 | 122.8867 | -123.056 | -122.9553 | 122.9187 | 122.9324 | 59.903 | 59.8343
471.8906 | 123.1659 | -59.9762 | 62.9471 | -0.090943 | 5.7742e-05 | 0.062145 | 0.066377 | 4.2692e-05 | -0.0020594 | -0.00054907 | -0.073517 | 0.0026618 | 0.064281 | 0.063925 | 0.00049563 | 0.0031018 | -0.0029309 | 0.009155 | 62.8876 | -60.0723 | 62.9654 | -59.8297 | -60.1959 | 0.032043 | 0.004578 | 62.883 | -59.9762 | 63.0753 | -60.0037 | -60.0861 | -59.8984 | -0.096131 | -0.05951 | 0.01831 | 0.14648 | 60.0082 | -0.21973 | 60.1044 | -0.1236 | 0 | -0.064087 | 0.12817 | -0.027466 | 0.07782 | -0.10986 | 0.07782 | -0.10986 | 0.24262 | 123.0377 | -0.027466 | 123.0515 | 122.9599 | 122.8592 | 122.8638 | 122.8592 | -123.0194 | -122.9233 | 122.9416 | 123.0515 | 59.9854 | 59.9808
472.8281 | 123.1338 | -59.9899 | 62.9471 | -0.090943 | 0.0013393 | 0.064281 | 0.066591 | -0.0010253 | -0.00056396 | 9.193e-05 | -0.052155 | 0.0011664 | 0.065349 | 0.070333 | -0.0039906 | 0.00096564 | 0.00048713 | -0.018311 | 62.8326 | -60.1364 | 62.9425 | -59.8755 | -60.3745 | -0.086975 | -0.16479 | 62.8601 | -59.9991 | 62.9654 | -60.0677 | -60.173 | -59.9899 | -0.14649 | -0.11444 | -0.004578 | 0.11444 | 59.903 | -0.38452 | 60.0494 | -0.23804 | -0.009155 | -0.086976 | 0.01831 | -0.07782 | 0 | -0.18311 | 0.009155 | -0.17395 | 0.26093 | 123.0789 | -0.068665 | 122.9645 | 122.9691 | 122.8592 | 122.8226 | 122.85 | -123.0835 | -122.9462 | 122.9324 | 122.9553 | 59.9716 | 59.8251
473.8906 | 123.1522 | -59.9808 | 62.9791 | -0.052796 | 0.0015529 | 0.063213 | 0.065309 | 0.0011109 | -0.0031274 | 0.00094633 | -0.039948 | 0.0020208 | 0.065349 | 0.06542 | -0.0022816 | 0.0060924 | 0.0011279 | -0.022888 | 62.9196 | -60.0815 | 62.9288 | -59.8846 | -60.2005 | 0.018311 | -0.041199 | 62.9288 | -59.9716 | 62.9974 | -59.9991 | -60.1135 | -59.9396 | -0.10071 | -0.059509 | -0.050354 | 0.09613 | 59.9991 | -0.21973 | 60.0998 | -0.11902 | 0.009155 | -0.050354 | 0.018311 | -0.01831 | 0.041199 | -0.13275 | 0.032044 | -0.14191 | 0.19684 | 123.0103 | -0.027465 | 122.9691 | 123.0011 | 122.9004 | 122.9004 | 122.9095 | -123.0606 | -122.9507 | 122.9095 | 122.9782 | 59.9579 | 59.9396
474.8281 | 123.1567 | -59.9899 | 62.9654 | -0.12909 | 5.7742e-05 | 0.063213 | 0.066163 | 0.0023925 | -0.0012048 | -0.0011899 | -0.070465 | 0.0022346 | 0.065777 | 0.062856 | -0.0029224 | 0.0031018 | -0.00079467 | -0.11444 | 62.8464 | -60.0998 | 62.8418 | -59.967 | -60.3333 | -0.09613 | -0.15564 | 62.8693 | -60.0037 | 63.0203 | -60.4065 | -60.2051 | -59.7931 | -0.10986 | -0.11902 | -0.1236 | 0.022888 | 59.8938 | -0.34332 | 60.0037 | -0.23346 | -0.013733 | -0.09613 | 0.054932 | -0.41657 | 0.19684 | -0.21515 | 0.21057 | -0.20142 | 0.13275 | 122.9416 | -0.40283 | 123.024 | 122.9462 | 122.8729 | 122.8363 | 122.8592 | -123.0652 | -122.9691 | 122.8317 | 123.0103 | 59.8755 | 59.8343
475.8281 | 123.2071 | -59.9762 | 62.9059 | -0.11383 | 0.0011257 | 0.062572 | 0.066591 | -0.0012391 | -0.00013676 | -0.00012167 | -0.030792 | 0.0024482 | 0.065563 | 0.070333 | -0.0044178 | 0.0028882 | -0.00036747 | -0.12817 | 62.8555 | -60.0952 | 62.9059 | -59.8846 | -60.2509 | -0.07782 | -0.10071 | 62.8464 | -59.9945 | 63.0295 | -59.9899 | -60.0861 | -59.903 | -0.11902 | -0.050354 | 0 | 0.091552 | 59.8984 | -0.27466 | 60.0174 | -0.15564 | -0.018311 | -0.059509 | 0.1236 | -0.013733 | 0.073242 | -0.10986 | 0.091553 | -0.091553 | 0.21057 | 123.0011 | 0.004578 | 123.024 | 122.9507 | 122.8409 | 122.8317 | 122.8226 | -123.0011 | -122.9004 | 122.8821 | 123.0057 | 59.848 | 59.8755
476.8906 | 123.1613 | -59.9899 | 62.9654 | -0.052796 | 0.0019803 | 0.061932 | 0.067659 | 0.0028199 | -0.0024866 | -0.0022581 | -0.030792 | 0.0011664 | 0.065563 | 0.064993 | -0.0052722 | 0.0045972 | 0.00091433 | -0.032043 | 62.9105 | -60.0677 | 62.915 | -59.8801 | -60.1868 | 0.022888 | -0.045776 | 62.8922 | -59.9899 | 63.0112 | -59.9899 | -60.1044 | -59.9487 | -0.07782 | -0.054932 | -0.050354 | 0.10986 | 60.0128 | -0.19684 | 60.0906 | -0.11902 | 0 | -0.073242 | 0.045776 | 0 | 0.041199 | -0.11444 | 0.041199 | -0.11444 | 0.18768 | 122.9828 | 0 | 123.0011 | 122.9782 | 122.8821 | 122.9004 | 122.8821 | -123.0331 | -122.9553 | 122.905 | 123.0011 | 59.9579 | 59.9442
477.8281 | 123.1567 | -60.0037 | 62.9379 | -0.17487 | 0.0019803 | 0.063 | 0.065736 | -0.00059811 | -0.0018458 | 9.193e-05 | -0.058258 | 0.0020208 | 0.06599 | 0.067556 | -0.0044178 | 0.003529 | 0.0032641 | -0.091553 | 62.8784 | -60.0769 | 62.8601 | -59.935 | -60.3195 | -0.10071 | -0.13733 | 62.8464 | -60.0082 | 62.9562 | -60.0403 | -60.1639 | -59.967 | -0.073242 | -0.059509 | -0.07782 | 0.068664 | 59.903 | -0.31586 | 59.9762 | -0.24262 | -0.004578 | -0.091552 | 0.018311 | -0.036621 | 0.036621 | -0.16022 | 0.041199 | -0.15564 | 0.14191 | 122.937 | -0.032043 | 122.9645 | 122.9553 | 122.8546 | 122.8821 | 122.85 | -123.0148 | -122.9462 | 122.8638 | 122.9599 | 59.9121 | 59.8663
478.8906 | 123.2391 | -59.935 | 62.9425 | -0.098572 | 0.00048494 | 0.063213 | 0.065095 | -0.00038451 | -0.00077756 | -0.0026853 | 0.036346 | 0.0020208 | 0.065777 | 0.064565 | -0.0052722 | 0.0031018 | -0.00015387 | -0.004578 | 62.8647 | -60.0266 | 63.0066 | -59.7565 | -60.1044 | 0.09613 | 0.11902 | 62.8464 | -59.9167 | 63.1073 | -59.8846 | -59.9716 | -59.8526 | -0.091552 | -0.07782 | 0.064087 | 0.17853 | 60.0311 | -0.16937 | 60.1227 | -0.07782 | 0.018311 | -0.09613 | 0.1648 | 0.050354 | 0.082398 | -0.036621 | 0.064087 | -0.054932 | 0.27008 | 123.0331 | 0.032043 | 123.024 | 122.8912 | 122.7631 | 122.7997 | 122.7814 | -122.9691 | -122.8592 | 122.9416 | 123.0423 | 59.9304 | 60.054
479.8281 | 123.1659 | -59.9762 | 62.9379 | -0.083313 | 0.00027134 | 0.06535 | 0.068086 | -0.0018799 | -0.0016322 | -0.0046079 | -0.049103 | 0.0018072 | 0.066204 | 0.065847 | -0.0042042 | 0.0043836 | 0.0011279 | -0.10071 | 62.8784 | -60.0998 | 62.8876 | -59.9258 | -60.2875 | -0.091553 | -0.11902 | 62.851 | -60.022 | 62.9837 | -60.0357 | -60.1273 | -59.9396 | -0.1236 | -0.059509 | -0.050354 | 0.050354 | 59.8846 | -0.31128 | 60.0082 | -0.18768 | -0.045777 | -0.086975 | 0.045777 | -0.05951 | 0.036621 | -0.15106 | 0.082398 | -0.10528 | 0.17395 | 122.9874 | -0.013733 | 123.0057 | 122.9782 | 122.8729 | 122.8546 | 122.8271 | -123.0377 | -122.9599 | 122.8638 | 122.9599 | 59.8755 | 59.8572
480.8906 | 123.1338 | -59.9533 | 62.9791 | 0.10742 | 0.0011257 | 0.062572 | 0.067018 | -0.00017091 | -0.0012048 | -0.00054907 | -0.042999 | 0.0043708 | 0.065563 | 0.062429 | -0.0059132 | 0.0022472 | -0.00036747 | -0.19684 | 62.9242 | -60.0906 | 62.8967 | -59.9213 | -60.1913 | 0.036621 | -0.009155 | 62.8922 | -59.9716 | 62.9654 | -60.0128 | -60.1227 | -59.9396 | -0.13733 | -0.054932 | -0.082397 | 0.032043 | 59.9899 | -0.23804 | 60.1273 | -0.10071 | -0.018311 | -0.086975 | -0.013733 | -0.059509 | 0.013733 | -0.16937 | 0.032044 | -0.15106 | 0.16937 | 122.9874 | -0.041198 | 122.937 | 123.0148 | 122.8638 | 122.8775 | 122.8455 | -123.0698 | -122.9507 | 122.85 | 122.9187 | 59.7565 | 59.9442
481.8281 | 123.2208 | -60.0037 | 62.9105 | -0.037537 | 0.00091214 | 0.062786 | 0.067445 | 0.0013245 | -0.0018458 | -0.0050351 | -0.055206 | 0.0011664 | 0.067272 | 0.065634 | -0.0033496 | 0.005238 | -0.00036747 | -0.11444 | 62.8555 | -60.0861 | 62.8967 | -59.9075 | -60.2783 | -0.082397 | -0.1236 | 62.8555 | -59.9945 | 63.002 | -60.022 | -60.1044 | -59.935 | -0.082398 | -0.054931 | -0.013732 | 0.09613 | 59.9213 | -0.27466 | 60.0037 | -0.19226 | 0.009155 | -0.054931 | 0.091553 | -0.018311 | 0.068664 | -0.10071 | 0.059509 | -0.10986 | 0.17853 | 122.9828 | -0.027466 | 122.9965 | 122.9416 | 122.85 | 122.8592 | 122.8592 | -122.9965 | -122.905 | 122.9004 | 123.0057 | 59.8892 | 59.8801
482.8906 | 123.1384 | -59.9579 | 63.002 | -0.060425 | 5.7742e-05 | 0.064281 | 0.06595 | -0.0023071 | 0.0017858 | -0.0020443 | 0.024139 | 0.0026618 | 0.066845 | 0.06542 | -0.0027088 | 0.0041698 | -0.0018629 | 0.032043 | 62.883 | -60.022 | 62.9654 | -59.7931 | -60.1456 | 0.07782 | 0.054932 | 62.8784 | -59.935 | 62.9974 | -59.9991 | -60.1135 | -59.9442 | -0.064087 | -0.11902 | -0.036621 | 0.1648 | 60.0357 | -0.18768 | 60.0998 | -0.1236 | 0.022888 | -0.1236 | -0.004577 | -0.041198 | 0.013733 | -0.15564 | -0.009155 | -0.17853 | 0.22888 | 122.9874 | -0.064086 | 122.9324 | 122.905 | 122.8134 | 122.8409 | 122.8363 | -123.024 | -122.937 | 122.9233 | 122.9553 | 59.9899 | 60.0128
483.8281 | 123.2025 | -59.9396 | 62.915 | -0.098572 | -0.00036966 | 0.062145 | 0.067659 | 0.0013245 | 0.0030676 | -0.0011899 | -0.042999 | 0.0007392 | 0.066204 | 0.061788 | -0.0046314 | 0.0048108 | -0.00058107 | -0.11444 | 62.8647 | -60.0998 | 62.915 | -59.8846 | -60.2371 | -0.086975 | -0.09613 | 62.8418 | -59.9854 | 63.0478 | -59.9762 | -60.0815 | -59.8618 | -0.16022 | -0.050354 | 0 | 0.054931 | 59.8526 | -0.29755 | 60.0128 | -0.13733 | -0.045777 | -0.073242 | 0.13275 | -0.036621 | 0.07782 | -0.14191 | 0.1236 | -0.09613 | 0.21515 | 123.0148 | 0.009156 | 123.0331 | 122.9645 | 122.8271 | 122.8043 | 122.7814 | -123.0148 | -122.9004 | 122.8546 | 122.9874 | 59.8251 | 59.8434
484.8906 | 123.0698 | -59.9121 | 62.9196 | -0.045166 | 0.0021939 | 0.063 | 0.065309 | -0.0027343 | -0.0016322 | -0.0011899 | 0.030243 | 0.0015936 | 0.065349 | 0.05837 | -0.0037768 | 0.00096564 | 0.0019823 | 0.032043 | 62.8784 | -60.0037 | 63.0524 | -59.7153 | -60.0815 | 0.11902 | 0.13275 | 62.8464 | -59.9396 | 63.089 | -59.8206 | -59.642 | -59.6283 | -0.091553 | -0.041199 | 0.13275 | 0.19684 | 60.0311 | -0.16937 | 60.1227 | -0.07782 | -0.027466 | -0.073242 | 0.16937 | 0.091552 | 0.28381 | 0.27008 | 0.31128 | 0.29755 | 0.28839 | 123.056 | 0.11902 | 123.0286 | 122.8821 | 122.7859 | 122.7905 | 122.7585 | -122.9233 | -122.8592 | 122.9645 | 123.0011 | 59.9442 | 60.0449
485.8281 | 122.9782 | -60.0357 | 62.9013 | -0.12909 | 0.0026211 | 0.061504 | 0.067445 | 0.0041015 | 0.00093144 | -0.0024717 | -0.082672 | 0.0018072 | 0.063854 | 0.062856 | -0.002068 | 0.0045972 | 0.0019823 | -0.10071 | 62.8555 | -60.1364 | 62.8418 | -59.9625 | -60.3241 | -0.09613 | -0.16022 | 62.8876 | -60.0037 | 62.9517 | -60.0952 | -60.1959 | -59.9167 | -0.10071 | -0.045776 | -0.059509 | 0.073243 | 59.9396 | -0.28839 | 60.0403 | -0.18768 | 0.032044 | -0.013733 | 0.050354 | -0.059509 | 0.11902 | -0.16022 | 0.086975 | -0.19226 | 0.17395 | 122.9782 | -0.091553 | 122.9553 | 122.9919 | 122.8912 | 122.8912 | 122.9233 | -123.0377 | -122.905 | 122.8775 | 122.9874 | 59.935 | 59.8755
486.8906 | 123.1796 | -59.9533 | 62.9379 | -0.11383 | 0.0039029 | 0.065136 | 0.064027 | 0.0015381 | -0.00013676 | -0.0022581 | 0.0058289 | 0.00138 | 0.067486 | 0.062429 | -0.0029224 | 0.0016064 | 0.00091433 | -0.054932 | 62.851 | -60.054 | 62.97 | -59.8114 | -60.2005 | -0.022888 | -0.059509 | 62.8281 | -59.9762 | 63.0386 | -59.9991 | -60.0906 | -59.9258 | -0.10071 | -0.086975 | 0.032044 | 0.14191 | 59.9304 | -0.24719 | 60.0311 | -0.14648 | -0.022888 | -0.10986 | 0.10071 | -0.045776 | 0.027466 | -0.13733 | 0.050354 | -0.11444 | 0.24262 | 123.024 | -0.022888 | 123.0148 | 122.905 | 122.8043 | 122.8043 | 122.7814 | -122.9919 | -122.9141 | 122.9233 | 122.9919 | 59.8984 | 59.8938
487.8281 | 123.1659 | -59.967 | 62.9288 | -0.068054 | 0.00069854 | 0.063854 | 0.067872 | -0.0029479 | 0.0015722 | -0.0024717 | -0.073517 | 0.0020208 | 0.067486 | 0.065206 | -0.003136 | 0.0058788 | 0.0017687 | -0.11444 | 62.8601 | -60.1089 | 62.8738 | -59.9258 | -60.2829 | -0.10071 | -0.11444 | 62.8647 | -60.0128 | 62.9837 | -60.0449 | -60.1501 | -59.9487 | -0.14191 | -0.068665 | -0.054932 | 0.041199 | 59.8663 | -0.31586 | 60.0082 | -0.17395 | -0.045776 | -0.064087 | 0.054932 | -0.07782 | 0.018311 | -0.1831 | 0.064087 | -0.13733 | 0.18311 | 122.9828 | -0.032044 | 122.9965 | 122.9691 | 122.8775 | 122.8271 | 122.8317 | -123.0377 | -122.9416 | 122.8409 | 122.9507 | 59.8526 | 59.8526
488.8906 | 123.262 | -59.9167 | 62.9379 | -0.1062 | 5.7742e-05 | 0.063854 | 0.06595 | -0.0023071 | -0.00099116 | 0.00094633 | 0.057709 | 0.0007392 | 0.06364 | 0.057302 | -0.0037768 | 0.0020336 | 0.00027333 | 0.004578 | 62.851 | -60.0082 | 63.0341 | -59.7107 | -60.0906 | 0.13275 | 0.11444 | 62.8418 | -59.9396 | 63.1119 | -59.8618 | -59.9487 | -59.8297 | -0.091553 | -0.086975 | 0.096131 | 0.20599 | 60.0494 | -0.17395 | 60.141 | -0.082397 | -0.022888 | -0.09613 | 0.17395 | 0.054932 | 0.086975 | -0.032043 | 0.10986 | -0.009155 | 0.29755 | 123.0423 | 0.07782 | 123.0515 | 122.8592 | 122.7814 | 122.7676 | 122.7585 | -122.9462 | -122.8775 | 122.9507 | 123.0286 | 59.9213 | 60.0311
489.8281 | 123.0972 | -59.9899 | 62.9471 | -0.090943 | 0.00048494 | 0.064068 | 0.067659 | 0.00025629 | -0.00056396 | -0.0014035 | -0.076569 | 0.0018072 | 0.066845 | 0.066274 | -0.0024952 | 0.0060924 | 0.00027333 | -0.091553 | 62.883 | -60.0861 | 62.8693 | -59.9487 | -60.2921 | -0.10071 | -0.16022 | 62.8876 | -60.0174 | 62.9242 | -60.0998 | -60.228 | -60.022 | -0.096131 | -0.064087 | -0.07782 | 0.041199 | 59.8892 | -0.30212 | 59.9854 | -0.20599 | -0.027466 | -0.05951 | -0.022889 | -0.10986 | -0.032044 | -0.23804 | -0.004578 | -0.21057 | 0.13733 | 122.9553 | -0.082397 | 122.9416 | 122.9691 | 122.905 | 122.8729 | 122.8775 | -123.0331 | -122.9645 | 122.8592 | 122.9141 | 59.8984 | 59.8297
490.8906 | 123.1247 | -59.9762 | 62.9929 | -0.045166 | 0.00091214 | 0.061718 | 0.068513 | -0.0029479 | -0.00099116 | 0.0022281 | -0.039948 | 0.0024482 | 0.067272 | 0.059866 | -0.0037768 | 0.0039562 | 0.0011279 | -0.004578 | 62.9105 | -60.0677 | 62.9608 | -59.8343 | -60.1959 | 0.041199 | 0.009155 | 62.915 | -59.967 | 63.0203 | -59.9854 | -60.0906 | -59.9167 | -0.091553 | -0.082398 | -0.032044 | 0.14191 | 60.0174 | -0.21973 | 60.1089 | -0.12817 | 0.009155 | -0.07782 | 0.027466 | -0.009156 | 0.059509 | -0.11444 | 0.050354 | -0.1236 | 0.23346 | 123.0286 | -0.018311 | 122.9874 | 122.9782 | 122.8821 | 122.8867 | 122.8912 | -123.0606 | -122.9599 | 122.937 | 122.9965 | 59.9716 | 59.9854
491.8281 | 123.1567 | -59.9487 | 62.9608 | -0.090943 | -0.0010105 | 0.064922 | 0.067445 | 4.2692e-05 | -0.00035036 | -0.0016171 | -0.07962 | 0.0015936 | 0.068127 | 0.066274 | -0.0052722 | 0.0033154 | 0.0030505 | -0.027466 | 62.8876 | -60.0449 | 62.9425 | -59.9213 | -60.3836 | 0.004578 | 0.009155 | 62.8967 | -59.9762 | 63.0112 | -59.9945 | -60.1089 | -59.9258 | -0.096131 | -0.073242 | -0.01831 | 0.027465 | 59.9533 | -0.43488 | 60.0494 | -0.33875 | -0.027466 | -0.064086 | 0.050354 | -0.045777 | 0.022888 | -0.16022 | 0.050354 | -0.13275 | 0.1236 | 122.9874 | -0.018311 | 122.9874 | 122.9324 | 122.8729 | 122.8363 | 122.8455 | -123.0057 | -122.937 | 122.8912 | 122.9599 | 59.9213 | 59.9579
492.8906 | 123.1979 | -59.9533 | 62.9288 | -0.052796 | 0.0011257 | 0.061718 | 0.063386 | -0.0044433 | -0.00099116 | -0.0016171 | 0.027191 | 0.0022346 | 0.065563 | 0.067983 | -0.002068 | 0.0037426 | 0.00027333 | -0.10071 | 62.8784 | -60.0449 | 62.9288 | -59.8297 | -60.1776 | 0 | -0.018311 | 62.8326 | -59.9854 | 63.0341 | -59.9487 | -60.0449 | -59.9121 | -0.091553 | -0.050354 | 0 | 0.1236 | 59.9533 | -0.2243 | 60.0449 | -0.13275 | -0.032044 | -0.09613 | 0.10529 | 0.004578 | 0.041199 | -0.091553 | 0.073243 | -0.059509 | 0.21515 | 122.9736 | 0.036622 | 123.0194 | 122.9233 | 122.818 | 122.8317 | 122.7859 | -122.9736 | -122.9141 | 122.8821 | 122.9874 | 59.8526 | 59.935
493.8281 | 123.1201 | -59.9579 | 62.9837 | -0.090943 | 0.00069854 | 0.062145 | 0.067445 | 0.0030335 | -0.00099116 | -0.00012167 | -0.052155 | 0.00138 | 0.066418 | 0.058798 | -0.0044178 | 0.0048108 | -0.00058107 | -0.022888 | 62.8693 | -60.0677 | 62.9929 | -59.848 | -60.1456 | -0.022888 | 0 | 62.8601 | -59.9716 | 62.9974 | -60.0037 | -60.1318 | -59.9304 | -0.10986 | -0.11444 | 0.009155 | 0.10986 | 59.935 | -0.18768 | 60.0449 | -0.07782 | -0.013733 | -0.1236 | 0.013733 | -0.045776 | 0.027466 | -0.17395 | 0.041199 | -0.16022 | 0.21973 | 123.0606 | -0.032043 | 122.9691 | 122.937 | 122.8317 | 122.8271 | 122.818 | -123.0515 | -122.9553 | 122.9507 | 122.9553 | 59.935 | 59.9579
494.8906 | 123.2025 | -59.9625 | 62.9196 | -0.083313 | 0.0039029 | 0.063641 | 0.066377 | 0.00025629 | -0.00035036 | 0.0013735 | -0.018585 | 0.0035162 | 0.06599 | 0.064565 | -0.0033496 | 0.003529 | 0.00091433 | -0.07782 | 62.8143 | -60.0769 | 62.97 | -59.8663 | -60.2097 | -0.013733 | -0.041199 | 62.8098 | -59.9808 | 63.0478 | -59.9579 | -60.0632 | -59.8572 | -0.11444 | -0.10529 | 0.050354 | 0.09613 | 59.9487 | -0.24719 | 60.0632 | -0.13275 | -0.018311 | -0.10986 | 0.12817 | 0.004577 | 0.10529 | -0.10071 | 0.1236 | -0.082397 | 0.21057 | 123.0469 | 0.022888 | 123.0286 | 122.8912 | 122.7905 | 122.7768 | 122.7722 | -122.9965 | -122.9004 | 122.9324 | 123.0103 | 59.8846 | 59.9213
495.8438 | 123.1613 | -59.9899 | 62.883 | -0.068054 | -0.0014377 | 0.063 | 0.065095 | 0.0013245 | -0.00077756 | 0.00051913 | -0.018585 | -0.000329 | 0.067486 | 0.068838 | -0.0050586 | 0.00075204 | 0.00070073 | -0.054932 | 62.8464 | -60.0449 | 62.97 | -59.7885 | -60.1685 | -0.022888 | -0.018311 | 62.8464 | -59.9808 | 63.0707 | -59.9716 | -60.0357 | -59.8846 | -0.054932 | -0.036621 | 0.086975 | 0.20142 | 59.967 | -0.17853 | 60.022 | -0.1236 | 0.009155 | -0.036621 | 0.18768 | 0.01831 | 0.10528 | -0.045777 | 0.09613 | -0.054932 | 0.25635 | 123.0148 | 0.009155 | 123.0515 | 122.8912 | 122.8271 | 122.8363 | 122.8363 | -122.9279 | -122.8638 | 122.9599 | 123.0606 | 59.935 | 59.9716
496.8906 | 123.2162 | -59.9716 | 62.9425 | -0.045166 | 0.00048494 | 0.063 | 0.064027 | -0.0014527 | -0.0012048 | -0.0011899 | 0.06076 | 0.0009528 | 0.067913 | 0.063284 | -0.0035632 | 0.0056652 | 0.0015551 | -0.027466 | 62.8647 | -60.0449 | 63.002 | -59.7931 | -60.1364 | 0.073242 | 0.050354 | 62.8784 | -59.9579 | 63.0753 | -59.9213 | -60.0128 | -59.848 | -0.073242 | -0.07782 | 0.059509 | 0.17853 | 60.0449 | -0.1648 | 60.1181 | -0.091553 | 0.013733 | -0.064087 | 0.13275 | 0.050354 | 0.1236 | -0.041198 | 0.10986 | -0.054931 | 0.25177 | 123.0469 | 0.036621 | 123.0331 | 122.9095 | 122.8363 | 122.8363 | 122.85 | -122.9874 | -122.9004 | 122.9736 | 123.0469 | 59.9442 | 60.022
497.8281 | 123.1613 | -59.9533 | 62.9608 | -0.037537 | 0.0013393 | 0.063427 | 0.067232 | 0.0019653 | -0.00099116 | -0.0033261 | -0.039948 | 0.0024482 | 0.066845 | 0.062216 | -0.0052722 | 0.0039562 | -0.0029309 | 0.009155 | 62.915 | -60.0769 | 62.9562 | -59.8206 | -60.1822 | 0.045776 | 0.041199 | 62.9013 | -59.9716 | 63.0203 | -59.9625 | -60.0998 | -59.9258 | -0.1236 | -0.045776 | -0.004577 | 0.13275 | 59.9991 | -0.22888 | 60.1227 | -0.10529 | -0.018311 | -0.059509 | 0.05951 | -0.009155 | 0.027466 | -0.14648 | 0.045777 | -0.12817 | 0.25635 | 123.0331 | 0.009156 | 122.9919 | 122.9919 | 122.8729 | 122.8683 | 122.8546 | -123.0377 | -122.9324 | 122.9095 | 122.9736 | 59.9625 | 59.9945
498.8906 | 123.2162 | -59.9213 | 62.9517 | -0.11383 | 5.7742e-05 | 0.063854 | 0.067018 | -0.0012391 | -0.0016322 | -0.00076267 | 0.045502 | 0.0009528 | 0.067913 | 0.062002 | -0.0042042 | 0.0039562 | 0.0015551 | -0.022888 | 62.883 | -60.0449 | 62.9791 | -59.7977 | -60.1547 | 0.050354 | 0.032043 | 62.8555 | -59.9854 | 63.0753 | -59.9258 | -60.0128 | -59.8618 | -0.1236 | -0.068664 | 0.027466 | 0.1236 | 59.9716 | -0.23346 | 60.0952 | -0.10986 | -0.064087 | -0.09613 | 0.1236 | -0.004577 | 0.05951 | -0.091552 | 0.1236 | -0.027465 | 0.24719 | 123.024 | 0.05951 | 123.0606 | 122.9279 | 122.8409 | 122.8043 | 122.7768 | -122.9965 | -122.937 | 122.9004 | 122.9965 | 59.8984 | 59.9533
499.8281 | 123.1155 | -59.967 | 63.002 | -0.090943 | 0.0011257 | 0.062359 | 0.067445 | -0.00017091 | -0.0014184 | -0.0011899 | -0.049103 | 0.0018072 | 0.066418 | 0.061575 | -0.0029224 | 0.0028882 | -0.0025037 | -0.013733 | 62.9059 | -60.0906 | 62.9059 | -59.8892 | -60.2142 | 0.018311 | -0.009155 | 62.9105 | -59.9762 | 62.9745 | -60.022 | -60.1318 | -59.9533 | -0.1236 | -0.09613 | -0.09613 | 0.07782 | 59.9854 | -0.24719 | 60.1089 | -0.1236 | -0.009155 | -0.091553 | -0.027466 | -0.054932 | 0.013733 | -0.16479 | 0.022888 | -0.15564 | 0.20142 | 122.9965 | -0.045777 | 122.9507 | 122.9965 | 122.8867 | 122.8729 | 122.8775 | -123.0927 | -122.9782 | 122.8729 | 122.9416 | 59.9533 | 59.9579
500.8906 | 123.2071 | -59.9442 | 62.9379 | -0.11383 | 5.7742e-05 | 0.063 | 0.064882 | -0.0014527 | -0.0027002 | -0.00033547 | 0.014984 | 0.00138 | 0.065563 | 0.057089 | -0.003136 | 0.0024608 | -0.0012219 | -0.064087 | 62.8601 | -60.0494 | 62.9471 | -59.848 | -60.1913 | -0.009155 | -0.054932 | 62.8418 | -59.9716 | 63.0295 | -59.9762 | -60.0906 | -59.9121 | -0.10529 | -0.07782 | 0.009156 | 0.096131 | 59.935 | -0.24719 | 60.0403 | -0.14191 | -0.027466 | -0.09613 | 0.091553 | -0.032043 | 0.032044 | -0.14648 | 0.05951 | -0.11902 | 0.20142 | 122.9965 | -0.004577 | 123.0011 | 122.9095 | 122.8134 | 122.8043 | 122.7859 | -122.9874 | -122.9095 | 122.8912 | 122.9736 | 59.8801 | 59.8892
501.8281 | 123.1064 | -59.9533 | 63.0203 | -0.090943 | 0.0021939 | 0.063641 | 0.067872 | -0.0020935 | -0.0054774 | 0.00094633 | -0.036896 | 0.0018072 | 0.066845 | 0.069265 | -0.0042042 | 0.0037426 | 0.0024097 | 0.009155 | 62.9242 | -60.0632 | 62.9196 | -59.8618 | -60.2051 | 0.022888 | -0.009155 | 62.9013 | -59.9945 | 62.9608 | -60.0128 | -60.1181 | -59.9625 | -0.10986 | -0.096131 | -0.10071 | 0.091553 | 59.9762 | -0.25177 | 60.0861 | -0.14191 | -0.041199 | -0.11902 | -0.05951 | -0.059509 | -0.009155 | -0.16479 | 0.032044 | -0.1236 | 0.20142 | 122.9828 | -0.01831 | 122.9553 | 122.9874 | 122.8958 | 122.8775 | 122.8546 | -123.0835 | -123.0148 | 122.8729 | 122.9141 | 59.9625 | 59.9442
502.8906 | 123.262 | -59.967 | 62.9288 | -0.12146 | -0.00058326 | 0.064281 | 0.0683 | 0.00068369 | -0.00056396 | 0.0011599 | -0.042999 | 0.0011664 | 0.064281 | 0.063497 | -0.0052722 | 0.0028882 | -0.0035719 | -0.041199 | 62.8235 | -60.0815 | 62.9883 | -59.8068 | -60.1822 | -0.032043 | -0.032043 | 62.8098 | -60.0037 | 63.0707 | -59.9396 | -60.0403 | -59.8618 | -0.11444 | -0.10529 | 0.059509 | 0.16022 | 59.935 | -0.21515 | 60.0494 | -0.10071 | -0.036621 | -0.11902 | 0.14191 | 0.027466 | 0.10529 | -0.073242 | 0.14191 | -0.036621 | 0.27466 | 123.0698 | 0.064087 | 123.0743 | 122.905 | 122.8134 | 122.7905 | 122.7768 | -123.0103 | -122.9324 | 122.9553 | 123.0377 | 59.9258 | 59.935
503.8281 | 123.0927 | -59.9579 | 62.9837 | -0.052796 | 0.00048494 | 0.061718 | 0.066377 | -0.0016663 | -0.002273 | -0.00097627 | -0.0002747 | 0.0033026 | 0.067486 | 0.060507 | -0.0033496 | 0.0016064 | -0.00079467 | -0.013733 | 62.915 | -60.0266 | 62.9333 | -59.8709 | -60.2097 | 0.045776 | 0 | 62.9013 | -59.9899 | 62.9791 | -60.0128 | -60.1273 | -59.9716 | -0.068664 | -0.068665 | -0.050354 | 0.086975 | 60.0037 | -0.25177 | 60.0723 | -0.18311 | -0.032043 | -0.082398 | -0.004578 | -0.054931 | -0.013733 | -0.16937 | 0.01831 | -0.13733 | 0.15564 | 122.9599 | -0.022888 | 122.9691 | 122.9416 | 122.8912 | 122.8729 | 122.8592 | -123.0103 | -122.9736 | 122.8912 | 122.937 | 59.9442 | 59.9579
504.8281 | 123.1934 | -59.9716 | 62.9471 | -0.037537 | 0.00069854 | 0.061077 | 0.066163 | 4.2692e-05 | -0.0037684 | -0.0020443 | -0.0094299 | -0.000329 | 0.06834 | 0.06072 | -0.0039906 | 0.0024608 | 0.0015551 | -0.064087 | 62.8372 | -60.0769 | 62.9562 | -59.8389 | -59.9899 | 0.045776 | -0.050354 | 62.8235 | -59.9808 | 63.0295 | -59.9808 | -60.054 | -59.9167 | -0.10529 | -0.10986 | 0.009155 | 0.13275 | 60.0174 | -0.01831 | 60.1227 | 0.086975 | -0.009155 | -0.1236 | 0.082397 | -0.009155 | 0.054932 | -0.082397 | 0.064087 | -0.073242 | 0.23804 | 123.0331 | 0 | 123.0103 | 122.9141 | 122.8043 | 122.8088 | 122.7951 | -123.024 | -122.9279 | 122.9279 | 123.0011 | 59.9075 | 59.9213
505.8906 | 123.2483 | -59.9075 | 62.9517 | -0.083313 | -0.00015586 | 0.062572 | 0.064027 | -0.0016663 | -0.0020594 | -0.0020443 | 0.0027771 | 0.0026618 | 0.067058 | 0.058157 | -0.0035632 | 0.0031018 | -0.00079467 | -0.009155 | 62.883 | -60.0403 | 63.0157 | -59.7473 | -60.0998 | 0.1236 | 0.13733 | 62.8647 | -59.9258 | 63.0936 | -59.8755 | -59.9625 | -59.8343 | -0.13275 | -0.068664 | 0.064087 | 0.16022 | 60.0311 | -0.19226 | 60.1639 | -0.059509 | -0.01831 | -0.086975 | 0.14191 | 0.032044 | 0.073242 | -0.054931 | 0.091552 | -0.036621 | 0.29297 | 123.056 | 0.050354 | 123.0194 | 122.9233 | 122.7905 | 122.7905 | 122.7722 | -122.9919 | -122.8775 | 122.9233 | 123.0011 | 59.8984 | 60.0449
506.8281 | 123.2208 | -59.9304 | 62.9654 | -0.075684 | 0.0013393 | 0.062572 | 0.065095 | -0.00081171 | 0.00071784 | 0.00073273 | -0.012482 | 0.0015936 | 0.066418 | 0.07012 | -0.0044178 | 0.003529 | -0.0018629 | -0.045776 | 62.8693 | -60.0494 | 62.9791 | -59.816 | -60.1547 | 0.036621 | 0.018311 | 62.8418 | -59.9533 | 63.0569 | -59.9304 | -60.0174 | -59.8709 | -0.11902 | -0.09613 | 0.013733 | 0.11444 | 59.967 | -0.2243 | 60.0861 | -0.10529 | -0.022888 | -0.1236 | 0.091553 | 0 | 0.059509 | -0.086975 | 0.082397 | -0.064087 | 0.23346 | 123.0286 | 0.022888 | 123.0103 | 122.9187 | 122.7951 | 122.7997 | 122.7722 | -123.0148 | -122.9187 | 122.9095 | 122.9874 | 59.8846 | 59.9487
507.8906 | 123.2346 | -59.9716 | 62.9196 | -0.090943 | 0.0028347 | 0.064068 | 0.066591 | 0.0023925 | 0.0019994 | -0.00012167 | -0.055206 | 0.0005256 | 0.066204 | 0.064138 | -0.006554 | 0.0026746 | -0.0080579 | -0.068665 | 62.8098 | -60.0815 | 62.9745 | -59.8068 | -60.1913 | -0.022888 | -0.027466 | 62.8326 | -60.0037 | 63.0615 | -59.9487 | -60.0494 | -59.8618 | -0.10986 | -0.10986 | 0.054931 | 0.16479 | 59.9487 | -0.21973 | 60.0586 | -0.10986 | -0.032043 | -0.086975 | 0.14191 | 0.022889 | 0.10986 | -0.077819 | 0.14191 | -0.045776 | 0.27466 | 123.056 | 0.054932 | 123.0652 | 122.8912 | 122.8363 | 122.7814 | 122.8043 | -123.0011 | -122.9233 | 122.9462 | 123.0331 | 59.903 | 59.9442
508.8281 | 123.1476 | -59.9579 | 62.9471 | -0.14435 | 0.00069854 | 0.061077 | 0.066804 | -0.00038451 | -0.0014184 | -0.00076267 | -0.0033265 | 0.0015936 | 0.065563 | 0.063497 | -0.0027088 | 0.00075204 | -0.00036747 | -0.086975 | 62.8418 | -60.054 | 62.9333 | -59.8434 | -60.1959 | -0.022888 | -0.054932 | 62.8464 | -59.9899 | 62.9974 | -59.9442 | -59.9258 | -59.8434 | -0.09613 | -0.10529 | -0.013733 | 0.11444 | 59.935 | -0.23804 | 60.0311 | -0.14191 | -0.032043 | -0.10071 | 0.050354 | 0.013733 | 0.11444 | 0.032044 | 0.14648 | 0.064087 | 0.21057 | 122.9874 | 0.045776 | 122.9874 | 122.8958 | 122.8363 | 122.7997 | 122.8043 | -123.0011 | -122.937 | 122.8912 | 122.9553 | 59.8709 | 59.903
509.8906 | 123.2162 | -59.935 | 62.9105 | -0.1062 | 0.0015529 | 0.06535 | 0.066804 | 0.00025629 | -0.0016322 | -0.00012167 | -0.052155 | 0.0024482 | 0.066418 | 0.064352 | -0.0078358 | 0.0024608 | -0.0010083 | -0.050354 | 62.8098 | -60.0998 | 62.97 | -59.8022 | -60.1913 | -0.041199 | -0.045776 | 62.8189 | -60.0174 | 63.0798 | -59.9762 | -60.0494 | -59.8801 | -0.16479 | -0.10071 | 0.05951 | 0.13275 | 59.8938 | -0.25635 | 60.0586 | -0.091553 | -0.082397 | -0.091552 | 0.16937 | -0.041198 | 0.054932 | -0.11444 | 0.13733 | -0.032043 | 0.29755 | 123.0698 | 0.041199 | 123.0972 | 122.9095 | 122.8363 | 122.7448 | 122.7539 | -123.0103 | -122.9279 | 122.905 | 123.0148 | 59.8846 | 59.8892
510.8281 | 123.0881 | -59.9945 | 62.9333 | -0.098572 | 5.7742e-05 | 0.062572 | 0.067659 | 0.0019653 | -0.0033412 | 9.193e-05 | -0.11624 | 0.0020208 | 0.066418 | 0.069479 | -0.0059132 | 0.0037426 | -0.0012219 | -0.091553 | 62.8967 | -60.1227 | 62.8784 | -59.9625 | -60.2966 | -0.11444 | -0.19684 | 62.8601 | -60.0266 | 62.9608 | -60.0769 | -60.2005 | -60.0037 | -0.12817 | -0.036621 | -0.054932 | 0.032044 | 59.8801 | -0.30212 | 60.0082 | -0.17395 | -0.032043 | -0.073243 | 0.027465 | -0.082397 | -0.009155 | -0.20599 | 0.022888 | -0.17395 | 0.16022 | 123.0011 | -0.050354 | 122.9874 | 123.0194 | 122.8867 | 122.8912 | 122.8546 | -123.056 | -122.9599 | 122.8729 | 122.9553 | 59.903 | 59.7977
511.8906 | 123.1384 | -59.9991 | 62.9379 | -0.052796 | 5.7742e-05 | 0.063854 | 0.066804 | -0.00038451 | -0.00035036 | 0.0028689 | -0.085724 | 0.0015936 | 0.064922 | 0.061361 | -0.0037768 | 0.0048108 | 0.00048713 | -0.013733 | 62.8738 | -60.0723 | 62.9425 | -59.8297 | -60.1868 | 0.032043 | 0.027466 | 62.9013 | -59.9945 | 63.0203 | -59.9716 | -60.0906 | -59.9396 | -0.073243 | -0.064087 | 0.004578 | 0.16937 | 60.0311 | -0.18768 | 60.1044 | -0.11444 | 0.004577 | -0.036621 | 0.082398 | 0.027465 | 0.059509 | -0.091553 | 0.054932 | -0.09613 | 0.24262 | 123.0148 | 0.022888 | 123.0148 | 122.9462 | 122.8958 | 122.8729 | 122.9004 | -123.0103 | -122.9324 | 122.9416 | 123.0194 | 59.9854 | 60.0266
512.8281 | 123.2117 | -59.967 | 62.9288 | -0.052796 | 0.0045437 | 0.064281 | 0.066804 | 0.0011109 | 7.6842e-05 | -0.0022581 | -0.0033265 | 0.0003118 | 0.065136 | 0.061148 | -0.0027088 | 0.0031018 | -0.0012219 | -0.068665 | 62.8235 | -60.0403 | 62.9837 | -59.7794 | -60.1913 | -0.009155 | -0.022888 | 62.8281 | -59.9762 | 63.0569 | -59.9579 | -60.0494 | -59.8892 | -0.073242 | -0.10529 | 0.054932 | 0.18768 | 59.9579 | -0.2243 | 60.0311 | -0.15106 | -0.009155 | -0.10071 | 0.12817 | 0.009155 | 0.07782 | -0.082397 | 0.086975 | -0.073242 | 0.26093 | 123.024 | 0.01831 | 123.0331 | 122.8638 | 122.8043 | 122.7905 | 122.7951 | -122.9691 | -122.905 | 122.9507 | 123.024 | 59.8984 | 59.9442
513.8906 | 123.111 | -59.9625 | 62.9837 | -0.060425 | 0.0019803 | 0.061718 | 0.064668 | 0.0015381 | -0.0020594 | -0.00076267 | -0.046051 | 0.0009528 | 0.066845 | 0.061575 | -0.0044178 | 0.0026746 | 0.0019823 | -0.027466 | 62.9059 | -60.0815 | 62.9105 | -59.8984 | -60.2005 | 0.027466 | -0.036621 | 62.9105 | -59.9487 | 63.0112 | -59.967 | -60.1044 | -59.9213 | -0.11902 | -0.07782 | -0.073243 | 0.064087 | 59.9899 | -0.23804 | 60.1089 | -0.11902 | 0.013733 | -0.073243 | 0.027465 | -0.004578 | 0.041198 | -0.14191 | 0.027465 | -0.15564 | 0.18311 | 122.9919 | -0.018311 | 122.9599 | 122.9874 | 122.8592 | 122.8683 | 122.8729 | -123.0652 | -122.9324 | 122.8729 | 122.9736 | 59.935 | 59.9258
514.8281 | 123.1934 | -59.9625 | 62.9196 | -0.1062 | 5.7742e-05 | 0.062359 | 0.065523 | 0.00025629 | -0.00077756 | 9.193e-05 | -0.012482 | 0.003089 | 0.068554 | 0.055593 | -0.0035632 | 0.0028882 | -0.00036747 | -0.054932 | 62.8143 | -60.054 | 62.97 | -59.7931 | -60.1776 | 0 | -0.032043 | 62.8372 | -60.0082 | 63.0524 | -59.9625 | -60.0632 | -59.8938 | -0.091553 | -0.10529 | 0.050354 | 0.16937 | 59.9625 | -0.21515 | 60.054 | -0.1236 | -0.045777 | -0.082398 | 0.13275 | 0 | 0.068664 | -0.10071 | 0.11444 | -0.054931 | 0.26093 | 123.024 | 0.045777 | 123.0606 | 122.8683 | 122.8455 | 122.7768 | 122.7997 | -122.9736 | -122.9279 | 122.9324 | 123.0148 | 59.9075 | 59.9304
515.8906 | 123.2117 | -59.9487 | 62.9333 | -0.098572 | 0.0021939 | 0.065136 | 0.065523 | -0.0020935 | 0.00071784 | 0.0013735 | -0.036896 | 0.0015936 | 0.065563 | 0.064352 | -0.0044178 | 0.0060924 | 0.0011279 | -0.050354 | 62.8006 | -60.0952 | 62.9837 | -59.7794 | -60.1822 | -0.032043 | -0.041199 | 62.8052 | -60.0082 | 62.9059 | -59.8206 | -59.848 | -59.7702 | -0.14649 | -0.13275 | 0.050354 | 0.16937 | 59.9167 | -0.23346 | 60.0632 | -0.086975 | -0.05951 | -0.12817 | -0.027466 | 0.12817 | 0.17853 | 0.10071 | 0.23804 | 0.16022 | 0.31586 | 123.0789 | 0.18768 | 122.9141 | 122.8958 | 122.8134 | 122.7493 | 122.7539 | -123.0286 | -122.9416 | 122.9324 | 122.8546 | 59.8984 | 59.9075
516.8281 | 123.1934 | -59.9396 | 62.9196 | -0.068054 | 0.0039029 | 0.064068 | 0.064882 | -0.0014527 | 0.00029044 | -0.00076267 | -0.0063781 | 0.0007392 | 0.063854 | 0.059866 | -0.0039906 | 0.0024608 | -0.0020765 | -0.073242 | 62.8418 | -60.054 | 62.9883 | -59.7839 | -60.1822 | -0.027466 | -0.045776 | 62.8189 | -59.967 | 63.0386 | -59.9762 | -60.0723 | -59.903 | -0.11444 | -0.07782 | 0.068664 | 0.15564 | 59.9121 | -0.24262 | 60.0266 | -0.12817 | -0.027466 | -0.10071 | 0.11902 | -0.036621 | 0.036621 | -0.13275 | 0.064087 | -0.10529 | 0.27008 | 123.0423 | -0.009155 | 123.0057 | 122.8958 | 122.7859 | 122.7814 | 122.7585 | -122.9736 | -122.8867 | 122.9279 | 122.9782 | 59.8663 | 59.8938
517.8906 | 123.1293 | -59.9625 | 62.9379 | -0.022278 | 0.0011257 | 0.063854 | 0.068513 | -0.0025207 | -0.00056396 | 0.00030553 | -0.097931 | 0.003089 | 0.065349 | 0.06307 | -0.0022816 | 0.00182 | 0.00091433 | -0.050354 | 62.8784 | -60.0723 | 62.9333 | -59.8434 | -60.2097 | -0.013733 | -0.036621 | 62.883 | -59.9854 | 63.002 | -60.0037 | -60.1501 | -59.9533 | -0.10986 | -0.059509 | -0.004577 | 0.11902 | 59.9487 | -0.24719 | 60.0586 | -0.13733 | -0.022889 | -0.054931 | 0.064087 | -0.041199 | 0.009155 | -0.18768 | 0.032044 | -0.16479 | 0.22888 | 123.0057 | -0.01831 | 122.9874 | 122.9507 | 122.8683 | 122.8409 | 122.8455 | -123.0103 | -122.9233 | 122.8958 | 122.9645 | 59.9121 | 59.9258
518.8281 | 123.2117 | -59.9396 | 62.883 | -0.083313 | 0.0015529 | 0.06535 | 0.066377 | 0.0058105 | 0.001145 | -0.0014035 | -0.039948 | 0.0015936 | 0.064495 | 0.063925 | -0.0037768 | 0.0037426 | -0.0039991 | -0.068665 | 62.8372 | -60.1044 | 62.9654 | -59.8022 | -60.1913 | -0.041199 | -0.036621 | 62.8098 | -59.9808 | 63.0615 | -59.9579 | -60.0586 | -59.8709 | -0.1648 | -0.045777 | 0.082397 | 0.13733 | 59.8984 | -0.25177 | 60.0632 | -0.086975 | -0.041199 | -0.073243 | 0.17853 | -0.018311 | 0.068664 | -0.11902 | 0.10986 | -0.07782 | 0.30212 | 123.0698 | 0.022888 | 123.0423 | 122.9416 | 122.7905 | 122.7768 | 122.7493 | -122.9874 | -122.8638 | 122.905 | 123.0011 | 59.8709 | 59.903
519.8906 | 123.1567 | -59.9808 | 62.9425 | -0.1062 | 0.0013393 | 0.063213 | 0.066804 | -0.0023071 | -0.0029138 | -0.00054907 | -0.06131 | 0.00138 | 0.064495 | 0.05837 | -0.0046314 | 0.0043836 | 0.0034777 | -0.032043 | 62.8967 | -60.0906 | 62.9471 | -59.848 | -60.2371 | -0.013733 | -0.036621 | 62.883 | -59.9533 | 63.0066 | -60.0128 | -60.1456 | -59.9533 | -0.10986 | -0.045776 | 0.004578 | 0.13275 | 59.967 | -0.25635 | 60.0769 | -0.14648 | 0.027466 | -0.059509 | 0.064087 | -0.032043 | 0.027466 | -0.1648 | 0 | -0.19226 | 0.24262 | 123.0377 | -0.059509 | 122.9599 | 122.9874 | 122.8363 | 122.8775 | 122.8638 | -123.0331 | -122.8958 | 122.9279 | 122.9874 | 59.9487 | 59.9442
520.8281 | 123.2162 | -59.9533 | 62.8876 | -0.090943 | -0.00015586 | 0.063854 | 0.064027 | -0.00081171 | 0.00050424 | -0.00097627 | -0.049103 | 0.0005256 | 0.064709 | 0.064993 | -0.0035632 | 0.0045972 | -0.0035719 | -0.064087 | 62.8052 | -60.0906 | 62.9654 | -59.8114 | -60.1913 | -0.013733 | -0.059509 | 62.8052 | -59.9854 | 63.0569 | -59.9579 | -60.0677 | -59.8618 | -0.13733 | -0.082397 | 0.07782 | 0.14191 | 59.9396 | -0.23804 | 60.0769 | -0.10071 | -0.032044 | -0.082397 | 0.16937 | -0.004578 | 0.091553 | -0.11444 | 0.1236 | -0.082397 | 0.27924 | 123.056 | 0.027466 | 123.0423 | 122.8958 | 122.7905 | 122.7585 | 122.7585 | -122.9782 | -122.8729 | 122.9187 | 123.0103 | 59.8892 | 59.8938
521.8906 | 123.1293 | -59.9304 | 62.9883 | 0.00824 | 0.0024075 | 0.062572 | 0.068513 | 0.00046989 | -0.0024866 | -0.0028989 | -0.027741 | 0.0026618 | 0.066418 | 0.066061 | -0.0054858 | 0.0022472 | -0.00058107 | -0.036621 | 62.9059 | -60.0632 | 62.9288 | -59.8572 | -60.2005 | 0.032043 | -0.009155 | 62.883 | -59.9716 | 63.0157 | -59.9625 | -60.0769 | -59.9213 | -0.13275 | -0.082397 | -0.059509 | 0.073242 | 59.9625 | -0.27008 | 60.0952 | -0.13733 | -0.041199 | -0.10529 | 0.027466 | -0.032043 | 0.009155 | -0.14648 | 0.050354 | -0.10529 | 0.20599 | 122.9919 | 0.009156 | 122.9874 | 122.9691 | 122.8546 | 122.8363 | 122.8134 | -123.0515 | -122.9599 | 122.8592 | 122.9462 | 59.8938 | 59.9213
522.8281 | 123.2437 | -59.9579 | 62.915 | -0.12146 | 0.0011257 | 0.063854 | 0.065523 | 0.0017517 | 0.0017858 | -0.0011899 | -0.0094299 | 0.0011664 | 0.062786 | 0.059439 | -0.0044178 | 0.0022472 | 0.0013415 | -0.19684 | 62.7686 | -60.0998 | 63.0157 | -59.8114 | -60.1776 | 0.013733 | -0.013733 | 62.8098 | -59.9945 | 63.0524 | -59.9442 | -60.0311 | -59.8846 | -0.14191 | -0.14648 | 0.10071 | 0.14649 | 59.9716 | -0.21973 | 60.1135 | -0.07782 | -0.036621 | -0.10529 | 0.13733 | 0.013733 | 0.073242 | -0.073242 | 0.10986 | -0.036621 | 0.28839 | 123.1155 | 0.050354 | 123.0469 | 122.8683 | 122.8043 | 122.7264 | 122.7676 | -123.0148 | -122.9095 | 122.9736 | 123.0103 | 59.761 | 59.9442
523.8906 | 123.1064 | -59.9716 | 62.9654 | -0.045166 | 0.0021939 | 0.061932 | 0.068513 | -0.00017091 | -0.003982 | 0.0022281 | -0.042999 | 0.0011664 | 0.065777 | 0.062002 | -0.0033496 | 0.0043836 | 0.00048713 | -0.036621 | 62.8693 | -60.0815 | 62.9425 | -59.8618 | -60.2142 | -0.022888 | -0.036621 | 62.8693 | -59.9899 | 62.9837 | -60.0266 | -60.141 | -59.967 | -0.10986 | -0.09613 | -0.022888 | 0.10986 | 59.9487 | -0.24261 | 60.0586 | -0.13275 | -0.01831 | -0.09613 | 0.018311 | -0.054931 | 0.004578 | -0.16937 | 0.022888 | -0.15106 | 0.21973 | 123.024 | -0.036621 | 122.9736 | 122.9507 | 122.8592 | 122.8409 | 122.8409 | -123.0469 | -122.9553 | 122.9141 | 122.9553 | 59.935 | 59.935
524.8281 | 123.1613 | -59.967 | 62.9288 | -0.075684 | 0.00091214 | 0.064068 | 0.066804 | -0.0040161 | -0.0018458 | -0.00097627 | -0.042999 | 0.0020208 | 0.063 | 0.06307 | -0.0024952 | 0.0065198 | 0.0017687 | -0.11902 | 62.8601 | -60.1181 | 62.9059 | -59.903 | -60.26 | -0.10071 | -0.14191 | 62.8784 | -60.0037 | 62.9929 | -60.0082 | -60.1089 | -59.9258 | -0.15106 | -0.068665 | -0.022888 | 0.064087 | 59.8663 | -0.29297 | 60.0174 | -0.14191 | -0.036621 | -0.050354 | 0.064087 | -0.041199 | 0.041199 | -0.14191 | 0.07782 | -0.10529 | 0.21515 | 123.024 | -0.004578 | 122.9965 | 122.9782 | 122.8821 | 122.8271 | 122.8455 | -123.0469 | -122.9324 | 122.8729 | 122.9599 | 59.848 | 59.8251
525.8906 | 123.111 | -59.967 | 62.9654 | -0.075684 | 0.0015529 | 0.063 | 0.066804 | 0.0041015 | -0.00056396 | 0.00030553 | -0.070465 | 0.0024482 | 0.063213 | 0.066488 | -0.0033496 | 0.0041698 | -0.0025037 | -0.041199 | 62.8555 | -60.0998 | 62.915 | -59.8572 | -60.2371 | -0.022888 | -0.064087 | 62.9013 | -59.9808 | 62.9745 | -60.0357 | -60.1639 | -59.9579 | -0.13275 | -0.10986 | -0.050354 | 0.10986 | 59.9442 | -0.27008 | 60.0769 | -0.13733 | -0.013733 | -0.064087 | 0.009155 | -0.068665 | 0.009155 | -0.19684 | 0.022888 | -0.18311 | 0.24261 | 123.0148 | -0.054932 | 122.9553 | 122.9553 | 122.8821 | 122.8226 | 122.8683 | -123.0652 | -122.9462 | 122.8821 | 122.9416 | 59.9258 | 59.903
526.8281 | 123.056 | -59.9991 | 62.9379 | -0.12146 | 0.00069854 | 0.064068 | 0.065309 | 0.0032471 | -0.002273 | -0.00012167 | -0.064362 | 0.0009528 | 0.067272 | 0.061575 | -0.002068 | 0.0043836 | 5.9726e-05 | -0.1236 | 62.8555 | -60.0952 | 62.8784 | -59.9533 | -60.3058 | -0.1236 | -0.19226 | 62.8693 | -60.0266 | 62.9425 | -60.0906 | -60.1913 | -59.9854 | -0.096131 | -0.082397 | -0.059509 | 0.045776 | 59.8755 | -0.3067 | 59.9716 | -0.21057 | -0.027466 | -0.068664 | 0.004578 | -0.091553 | 0.013732 | -0.19226 | 0.041198 | -0.16479 | 0.14191 | 122.9736 | -0.064087 | 122.9691 | 122.9507 | 122.8958 | 122.8546 | 122.8683 | -123.0331 | -122.9645 | 122.8775 | 122.9416 | 59.8755 | 59.8068
527.8906 | 123.1384 | -59.9396 | 63.002 | 0.015869 | 0.0017667 | 0.062145 | 0.066163 | -0.0010253 | -0.0024866 | 0.00030553 | -0.024689 | 0.0015936 | 0.065777 | 0.060934 | -0.0035632 | 0.0039562 | -0.00036747 | -0.022888 | 62.8967 | -60.0677 | 62.9517 | -59.8251 | -60.1913 | 0.045776 | -0.004578 | 62.8967 | -59.967 | 63.0249 | -59.9854 | -60.0906 | -59.9121 | -0.12817 | -0.10529 | -0.050354 | 0.11444 | 59.9854 | -0.25177 | 60.1135 | -0.1236 | -0.027466 | -0.10529 | 0.022888 | -0.045777 | 0.027466 | -0.15106 | 0.054932 | -0.1236 | 0.24262 | 123.0194 | -0.018311 | 122.9919 | 122.9645 | 122.8638 | 122.8363 | 122.8363 | -123.0698 | -122.9691 | 122.8912 | 122.9645 | 59.9167 | 59.935
528.8281 | 123.1155 | -60.0082 | 62.9654 | -0.12146 | 0.0013393 | 0.062572 | 0.065736 | 0.0026063 | -0.0052638 | -0.0014035 | -0.049103 | 0.0009528 | 0.065563 | 0.068411 | -0.0042042 | 0.0065198 | 0.0030505 | -0.10529 | 62.8555 | -60.0952 | 62.8372 | -59.9716 | -60.3012 | -0.1236 | -0.1831 | 62.8922 | -60.0037 | 62.9471 | -60.0815 | -60.2051 | -60.0082 | -0.086975 | -0.10986 | -0.12817 | 0.036621 | 59.8846 | -0.29297 | 59.9716 | -0.20599 | 0.004578 | -0.073242 | -0.01831 | -0.073242 | 0 | -0.19684 | -0.004578 | -0.20142 | 0.1236 | 122.9324 | -0.07782 | 122.9507 | 122.9507 | 122.8958 | 122.8638 | 122.9004 | -123.0606 | -122.9691 | 122.8455 | 122.9553 | 59.903 | 59.8251
529.8906 | 123.1018 | -59.9762 | 62.9837 | -0.052796 | 0.00091214 | 0.061718 | 0.066377 | 0.00025629 | -0.0027002 | -0.0028989 | 0.0058289 | 0.00138 | 0.065777 | 0.067983 | -0.003136 | 0.0031018 | 0.0019823 | -0.054932 | 62.9196 | -60.0449 | 62.883 | -59.8801 | -60.2188 | 0.022888 | -0.054932 | 62.9242 | -59.9442 | 63.002 | -60.0861 | -60.0723 | -59.9167 | -0.068665 | -0.064087 | -0.10071 | 0.09613 | 59.9991 | -0.24262 | 60.0677 | -0.17395 | 0.032043 | -0.05951 | 0.01831 | -0.10986 | 0.059509 | -0.096131 | 0.027466 | -0.12817 | 0.16479 | 122.9279 | -0.14191 | 122.9462 | 122.9645 | 122.8683 | 122.8958 | 122.9004 | -123.0286 | -122.9279 | 122.8592 | 122.9782 | 59.9213 | 59.9213
530.8281 | 123.0103 | -60.0174 | 62.9059 | -0.098572 | 0.00091214 | 0.063427 | 0.067445 | 0.0017517 | 0.001145 | -0.00076267 | -0.046051 | 0.0028754 | 0.065563 | 0.061788 | -0.0024952 | 0.0037426 | -0.0039991 | -0.10529 | 62.8967 | -60.1273 | 62.8372 | -59.9854 | -60.3241 | -0.11902 | -0.17853 | 62.8693 | -60.0266 | 62.9425 | -60.0815 | -60.173 | -60.0494 | -0.10986 | -0.009155 | -0.068665 | 0.032043 | 59.8984 | -0.3067 | 60.0082 | -0.19684 | -0.009155 | -0.036621 | 0.036621 | -0.064087 | -0.032043 | -0.15564 | -0.022888 | -0.14648 | 0.14191 | 122.9645 | -0.054932 | 122.9691 | 123.024 | 122.8958 | 122.9141 | 122.8867 | -123.0331 | -122.9324 | 122.8546 | 122.9599 | 59.9121 | 59.8389
531.8906 | 123.1567 | -59.9625 | 62.9837 | -0.022278 | 0.00027134 | 0.063427 | 0.065523 | 0.0047425 | -0.00077756 | -0.0014035 | -0.024689 | 0.0028754 | 0.06599 | 0.068624 | -0.0046314 | 0.0031018 | -0.0018629 | -0.013733 | 62.9013 | -60.0861 | 62.9425 | -59.8343 | -60.2005 | 0.032043 | -0.004578 | 62.883 | -59.967 | 63.0203 | -59.9762 | -60.0906 | -59.9075 | -0.1236 | -0.082398 | -0.041199 | 0.12817 | 59.9945 | -0.23804 | 60.1181 | -0.11444 | -0.004578 | -0.10071 | 0.036621 | -0.013733 | 0.054931 | -0.12817 | 0.059509 | -0.1236 | 0.25177 | 123.0286 | -0.009155 | 122.9874 | 122.9874 | 122.85 | 122.8638 | 122.8455 | -123.0698 | -122.9507 | 122.905 | 122.9828 | 59.9487 | 59.9579
532.8281 | 123.1476 | -59.9625 | 62.9837 | -0.083313 | 0.0019803 | 0.063 | 0.065523 | -0.00081171 | -0.0027002 | -0.0028989 | -0.039948 | 0.0037298 | 0.067913 | 0.068411 | -0.0042042 | 0.0039562 | 0.00048713 | -0.064087 | 62.8601 | -60.0815 | 62.915 | -59.8526 | -60.2097 | -0.018311 | -0.041199 | 62.8693 | -59.9899 | 62.9929 | -60.0266 | -60.1273 | -59.9487 | -0.11902 | -0.1236 | -0.068665 | 0.10986 | 59.9442 | -0.24719 | 60.0632 | -0.12817 | -0.027466 | -0.11444 | 0.009155 | -0.064087 | 0.013733 | -0.16479 | 0.041199 | -0.13733 | 0.22888 | 122.9965 | -0.036621 | 122.9828 | 122.9416 | 122.8592 | 122.8226 | 122.8317 | -123.0652 | -122.9736 | 122.8775 | 122.9553 | 59.8984 | 59.9213
533.8281 | 123.0927 | -59.9762 | 62.97 | -0.060425 | 0.0021939 | 0.063854 | 0.064241 | 0.0015381 | -0.0061182 | -0.00033547 | -0.042999 | 0.0024482 | 0.068554 | 0.061361 | -0.0046314 | 0.0037426 | -0.0014355 | -0.10986 | 62.8647 | -60.1227 | 62.8601 | -59.9533 | -60.3149 | -0.1236 | -0.18768 | 62.883 | -60.0174 | 62.9242 | -60.0861 | -60.1868 | -59.9945 | -0.14648 | -0.10529 | -0.10986 | 0.022888 | 59.8526 | -0.33874 | 59.9991 | -0.19226 | -0.041199 | -0.086975 | -0.045777 | -0.10986 | -0.018311 | -0.21057 | 0.022888 | -0.16937 | 0.16937 | 122.9828 | -0.068665 | 122.9416 | 122.9874 | 122.9004 | 122.8409 | 122.8592 | -123.0927 | -122.9874 | 122.8363 | 122.9004 | 59.8663 | 59.7885
534.8906 | 123.1018 | -59.9808 | 62.9929 | -0.037537 | -0.00036966 | 0.060863 | 0.064027 | -0.00059811 | 7.6842e-05 | -0.0014035 | -0.0094299 | 0.0043708 | 0.065349 | 0.065206 | -0.003136 | 0.0026746 | -0.0016493 | -0.041199 | 62.9196 | -60.0632 | 62.8922 | -59.8846 | -60.2005 | 0.036621 | 0.2243 | 62.9471 | -59.9167 | 62.97 | -60.0174 | -60.1547 | -59.9945 | -0.082397 | -0.073242 | -0.10071 | 0.09613 | 60.0174 | -0.21973 | 60.0998 | -0.13733 | 0.064087 | -0.045776 | -0.022888 | -0.036621 | -0.013733 | -0.17395 | -0.07782 | -0.23804 | 0.17853 | 122.9553 | -0.10071 | 122.8867 | 122.9828 | 122.8638 | 122.9004 | 122.9279 | -123.056 | -122.9095 | 122.8729 | 122.9507 | 59.9396 | 60.2051
535.8281 | 123.1522 | -59.9716 | 62.9745 | -0.098572 | -0.00015586 | 0.063854 | 0.066804 | -0.00059811 | -0.0033412 | -0.0014035 | -0.058258 | 0.0018072 | 0.066631 | 0.060507 | -0.0033496 | 0.0024608 | -0.0012219 | -0.1236 | 62.8876 | -60.1089 | 62.8464 | -59.9625 | -60.3287 | -0.10529 | -0.1831 | 62.8693 | -60.0082 | 63.0707 | -60.434 | -60.2875 | -59.8022 | -0.13733 | -0.086975 | -0.12817 | 0.009156 | 59.8663 | -0.35706 | 60.0037 | -0.21973 | -0.036621 | -0.10529 | 0.096131 | -0.46234 | 0.16937 | -0.31586 | 0.20599 | -0.27924 | 0.14648 | 122.9553 | -0.42572 | 123.0789 | 122.9965 | 122.8775 | 122.8592 | 122.8409 | -123.0835 | -122.9828 | 122.818 | 123.0423 | 59.848 | 59.7885
536.8906 | 123.1476 | -59.9258 | 62.97 | -0.083313 | 0.0024075 | 0.061718 | 0.065095 | -0.0052979 | -0.00056396 | -0.0016171 | 0.051605 | -0.001397 | 0.066845 | 0.060079 | -0.0042042 | 0.0031018 | 0.0026233 | 0.018311 | 62.883 | -60.0174 | 63.0112 | -59.761 | -60.1135 | 0.11444 | 0.064087 | 62.8784 | -59.9487 | 63.0295 | -59.9396 | -60.022 | -59.8801 | -0.091553 | -0.086975 | 0.041198 | 0.1648 | 60.0403 | -0.18768 | 60.1318 | -0.09613 | -0.022888 | -0.091553 | 0.059509 | -0.013733 | 0.045776 | -0.096131 | 0.068664 | -0.073243 | 0.25635 | 123.0286 | 0.009155 | 122.9782 | 122.9004 | 122.8271 | 122.8088 | 122.8043 | -122.9874 | -122.9187 | 122.937 | 122.9553 | 59.9442 | 59.9899
537.8281 | 123.1155 | -59.9625 | 62.97 | -0.037537 | 0.00091214 | 0.064068 | 0.0683 | 0.00068369 | -0.0014184 | -0.00054907 | -0.058258 | 0.0015936 | 0.067272 | 0.067129 | -0.004845 | 0.0031018 | 5.9726e-05 | -0.11902 | 62.8601 | -60.1181 | 62.8601 | -59.9579 | -60.3104 | -0.10529 | -0.19226 | 62.8876 | -60.0174 | 62.8922 | -59.967 | -60.1822 | -60.0494 | -0.15564 | -0.10986 | -0.10986 | 0.004577 | 59.8572 | -0.3479 | 60.0128 | -0.19226 | -0.054932 | -0.082398 | -0.07782 | -0.004578 | -0.086975 | -0.21973 | -0.032043 | -0.16479 | 0.16022 | 122.9782 | 0.050354 | 122.9095 | 122.9782 | 122.905 | 122.8226 | 122.85 | -123.0881 | -122.9874 | 122.8226 | 122.8546 | 59.8434 | 59.7702
538.8906 | 123.1064 | -59.967 | 63.002 | -0.075684 | 0.00048494 | 0.063 | 0.065523 | 0.0011109 | -0.00099116 | -0.0031125 | 0.024139 | 0.0037298 | 0.067913 | 0.063497 | -0.0044178 | 0.0013928 | 0.0013415 | -0.022888 | 62.9013 | -60.054 | 62.915 | -59.8526 | -60.1959 | 0.045776 | -0.022888 | 62.915 | -59.9716 | 62.97 | -60.0037 | -60.1227 | -59.9487 | -0.086975 | -0.10071 | -0.086975 | 0.11444 | 60.0128 | -0.22888 | 60.0998 | -0.14191 | -0.004578 | -0.086975 | -0.032043 | -0.036621 | 0.018311 | -0.15564 | 0.022889 | -0.15106 | 0.20142 | 122.9691 | -0.032043 | 122.9416 | 122.9553 | 122.8867 | 122.8683 | 122.8821 | -123.056 | -122.9736 | 122.8821 | 122.937 | 59.9442 | 59.9442
539.8281 | 123.1201 | -59.9808 | 62.9654 | -0.083313 | -0.00015586 | 0.062359 | 0.066163 | 0.0032471 | 0.002213 | 0.0011599 | -0.021637 | 0.0037298 | 0.06834 | 0.060934 | -0.0042042 | 0.0033154 | 0.0011279 | -0.13275 | 62.8601 | -60.1135 | 62.7502 | -59.5963 | -60.1776 | -0.13275 | -0.21515 | 62.8738 | -60.0174 | 62.9425 | -60.0815 | -60.1913 | -59.9808 | -0.13275 | -0.10529 | -0.21515 | 0.38452 | 59.848 | -0.19684 | 59.9808 | -0.064087 | -0.036621 | -0.091553 | -0.022888 | -0.10071 | 0 | -0.21057 | 0.036621 | -0.17395 | 0.51727 | 122.8638 | -0.064087 | 122.9599 | 122.9736 | 122.8912 | 122.8409 | 122.8546 | -123.0789 | -122.9828 | 122.731 | 122.9233 | 59.848 | 59.7656
540.8906 | 123.0835 | -59.9533 | 62.9929 | -0.037537 | 0.0015529 | 0.063 | 0.063386 | -0.0018799 | 0.001145 | 0.00030553 | -0.027741 | 0.0024482 | 0.063427 | 0.065206 | -0.00014517 | -0.0013844 | 5.9726e-05 | -0.045776 | 62.9196 | -60.0632 | 62.915 | -59.8801 | -60.2234 | 0.032043 | -0.022888 | 62.9242 | -59.9762 | 63.0707 | -60.26 | -60.2142 | -59.9258 | -0.10986 | -0.073242 | -0.07782 | 0.073242 | 59.9854 | -0.27008 | 60.0952 | -0.16022 | -0.022888 | -0.068665 | 0.07782 | -0.3067 | 0.027466 | -0.26093 | 0.050354 | -0.23804 | 0.1831 | 122.9782 | -0.28381 | 123.0469 | 122.9828 | 122.9004 | 122.8729 | 122.8775 | -123.056 | -122.9691 | 122.8683 | 123.024 | 59.9075 | 59.9304
541.8281 | 123.0652 | -60.0449 | 62.9654 | -0.052796 | 0.00027134 | 0.065136 | 0.066377 | 0.00046989 | -0.0016322 | -0.00076267 | -0.058258 | 0.0015936 | 0.064495 | 0.067129 | -0.0044178 | 0.0033154 | 0.0041187 | -0.11444 | 62.9059 | -60.1227 | 62.8464 | -59.967 | -60.3333 | -0.10529 | -0.19226 | 62.8693 | -59.9945 | 62.9333 | -60.0952 | -60.4111 | -60.2234 | -0.07782 | -0.059509 | -0.11902 | 0.07782 | 59.9396 | -0.28839 | 60.0174 | -0.21057 | 0.050354 | -0.09613 | -0.032043 | -0.050354 | -0.17853 | -0.36621 | -0.22888 | -0.41656 | 0.15564 | 122.9691 | -0.10071 | 122.9279 | 123.0286 | 122.8638 | 122.9507 | 122.9141 | -123.0881 | -122.9599 | 122.8912 | 122.9782 | 59.9304 | 59.8526
542.8906 | 123.2162 | -59.9213 | 62.9608 | -0.045166 | 0.0026211 | 0.063 | 0.064668 | -0.0035889 | -0.0016322 | -0.0048215 | 0.066864 | 0.0041572 | 0.067699 | 0.056875 | -0.0042042 | 0.0028882 | -0.0010083 | 0.013733 | 62.8784 | -60.0357 | 63.0249 | -59.7244 | -60.0952 | 0.27466 | -0.13275 | 62.8326 | -59.9579 | 63.0478 | -59.8938 | -59.9945 | -59.8663 | -0.11444 | -0.082397 | 0.064087 | 0.19684 | 60.1959 | -0.17395 | 60.3104 | -0.059509 | -0.036621 | -0.12817 | 0.086976 | 0.027466 | 0.054932 | -0.073242 | 0.091553 | -0.036621 | 0.31128 | 123.0606 | 0.064087 | 123.0057 | 122.9141 | 122.7905 | 122.7997 | 122.7539 | -122.9965 | -122.9187 | 122.9462 | 122.9691 | 59.935 | 59.7885
543.8281 | 123.0789 | -59.9899 | 62.9562 | -0.090943 | -0.00036966 | 0.062786 | 0.0683 | 0.0023925 | -0.0012048 | 0.0013735 | -0.052155 | 0.0020208 | 0.066631 | 0.066488 | -0.0061268 | 0.0026746 | -0.0037855 | -0.086975 | 62.8738 | -60.1089 | 62.8784 | -59.9396 | -60.2829 | -0.11902 | -0.18768 | 62.8784 | -59.9991 | 62.9333 | -60.0998 | -60.2234 | -60.0128 | -0.11902 | -0.082398 | -0.07782 | 0.050354 | 59.8709 | -0.29297 | 59.9899 | -0.17395 | -0.009155 | -0.07782 | -0.022888 | -0.10986 | -0.022888 | -0.23346 | -0.013733 | -0.2243 | 0.16937 | 122.9874 | -0.10071 | 122.9324 | 122.9828 | 122.8775 | 122.8638 | 122.8683 | -123.0652 | -122.9553 | 122.8683 | 122.9233 | 59.903 | 59.8022
544.8906 | 123.1155 | -59.9487 | 62.9929 | -0.083313 | 0.0019803 | 0.062359 | 0.064454 | -0.0020935 | -0.002273 | -0.0024717 | 0.027191 | 0.0024482 | 0.065349 | 0.065206 | -0.0037768 | 0.003529 | -0.0029309 | -0.004578 | 62.8922 | -60.0357 | 62.9471 | -59.816 | -60.173 | 0.086975 | 0.004578 | 62.9379 | -59.967 | 62.9745 | -60.0082 | -60.0906 | -59.9487 | -0.086976 | -0.10071 | -0.045776 | 0.13275 | 60.0357 | -0.22431 | 60.1227 | -0.13733 | -0.018311 | -0.054932 | -0.018311 | -0.05951 | 0 | -0.14191 | 0.018311 | -0.1236 | 0.21973 | 122.9828 | -0.041199 | 122.9416 | 122.9279 | 122.905 | 122.8409 | 122.8867 | -123.0286 | -122.9599 | 122.8958 | 122.9233 | 59.9442 | 59.9533
545.8281 | 123.0835 | -59.9808 | 62.9837 | -0.1062 | 0.0024075 | 0.064495 | 0.067659 | 0.00068369 | 7.6842e-05 | -0.00033547 | -0.064362 | 0.00138 | 0.066845 | 0.06542 | -0.0042042 | 0.0048108 | 5.9726e-05 | -0.086975 | 62.9059 | -60.0815 | 62.8967 | -59.8984 | -60.2463 | -0.073242 | -0.13733 | 62.8922 | -59.9945 | 62.9333 | -60.0906 | -60.1913 | -60.0082 | -0.10071 | -0.07782 | -0.086975 | 0.082398 | 59.9075 | -0.2655 | 60.0082 | -0.16479 | -0.013733 | -0.091553 | -0.050354 | -0.10986 | -0.027466 | -0.21057 | -0.013733 | -0.19684 | 0.18311 | 122.9782 | -0.09613 | 122.9279 | 122.9874 | 122.8867 | 122.8867 | 122.8729 | -123.0652 | -122.9782 | 122.8775 | 122.9141 | 59.8938 | 59.8434
546.8906 | 123.1384 | -59.9304 | 62.9791 | -0.052796 | 0.0019803 | 0.063 | 0.064454 | -0.00059811 | -0.0014184 | -0.0011899 | 0.036346 | 9.8198e-05 | 0.066631 | 0.066061 | -0.0059132 | 0.0022472 | -0.00036747 | 0.009155 | 62.883 | -60.022 | 62.9837 | -59.7702 | -60.1227 | 0.10071 | 0.054932 | 62.8876 | -59.9442 | 63.0157 | -59.9579 | -60.054 | -59.9075 | -0.091553 | -0.09613 | 0.004578 | 0.16022 | 60.0311 | -0.19226 | 60.1227 | -0.10071 | -0.013733 | -0.091553 | 0.036621 | -0.027466 | 0.022888 | -0.1236 | 0.036621 | -0.10986 | 0.25177 | 123.0057 | -0.013733 | 122.9599 | 122.905 | 122.8317 | 122.8134 | 122.818 | -123.0011 | -122.9233 | 122.9141 | 122.9462 | 59.9396 | 59.9854
547.8281 | 123.111 | -59.9625 | 62.9791 | -0.068054 | 0.0026211 | 0.063213 | 0.069581 | 0.0028199 | -0.00077756 | -0.00076267 | -0.049103 | 0.0041572 | 0.064922 | 0.062856 | -0.0035632 | 0.0058788 | 0.00070073 | -0.064087 | 62.8464 | -60.0861 | 62.9242 | -59.8938 | -60.2463 | -0.059509 | -0.086975 | 62.9013 | -59.9899 | 62.9517 | -60.0403 | -60.1547 | -59.9762 | -0.1236 | -0.13275 | -0.054932 | 0.068664 | 59.903 | -0.28381 | 60.0266 | -0.16022 | -0.027466 | -0.07782 | -0.027466 | -0.07782 | -0.013733 | -0.19226 | 0.013733 | -0.1648 | 0.19226 | 123.0103 | -0.050354 | 122.9416 | 122.9324 | 122.8912 | 122.8088 | 122.8638 | -123.0652 | -122.9691 | 122.8867 | 122.9141 | 59.8984 | 59.8755
548.8906 | 123.2437 | -59.9121 | 62.9608 | -0.068054 | 0.00048494 | 0.063854 | 0.066163 | -0.00017091 | -0.0037684 | -0.0028989 | 0.051605 | 0.0018072 | 0.065136 | 0.059439 | -0.0024952 | 0.0016064 | 0.0015551 | -0.018311 | 62.8693 | -60.0128 | 62.9974 | -59.7702 | -60.0952 | 0.09613 | 0.082397 | 62.8647 | -59.9396 | 63.089 | -59.8984 | -59.9854 | -59.8526 | -0.10071 | -0.091552 | 0.036622 | 0.14191 | 60.0082 | -0.18311 | 60.1089 | -0.082398 | -0.027466 | -0.09613 | 0.12817 | 0.013733 | 0.059509 | -0.073243 | 0.086975 | -0.045777 | 0.24261 | 123.0103 | 0.041199 | 123.0286 | 122.8821 | 122.8043 | 122.7814 | 122.7768 | -122.9736 | -122.9004 | 122.9095 | 123.0011 | 59.8938 | 59.9945
549.8281 | 123.0652 | -60.0037 | 62.9654 | -0.090943 | -0.00015586 | 0.063641 | 0.068513 | 0.0026063 | -0.0031274 | 9.193e-05 | -0.055206 | -0.0005426 | 0.06599 | 0.057516 | -0.0059132 | 0.0039562 | 0.00070073 | -0.09613 | 62.883 | -60.1089 | 62.8555 | -59.9213 | -60.2646 | -0.09613 | -0.1831 | 62.8876 | -60.0037 | 62.9288 | -60.1044 | -60.2188 | -59.9945 | -0.10529 | -0.082397 | -0.10986 | 0.082397 | 59.9075 | -0.26093 | 60.0128 | -0.15564 | 0 | -0.07782 | -0.036621 | -0.10071 | 0.009155 | -0.21515 | 0.009155 | -0.21515 | 0.18768 | 122.9645 | -0.10071 | 122.9324 | 122.9919 | 122.8912 | 122.8867 | 122.8912 | -123.0743 | -122.9691 | 122.8592 | 122.9324 | 59.9075 | 59.8206
550.8906 | 123.1796 | -59.9625 | 62.9288 | -0.060425 | 0.0015529 | 0.062572 | 0.066377 | -0.00038451 | -0.0024866 | -0.0014035 | 0.033295 | 0.0005256 | 0.066631 | 0.062429 | -0.0016406 | 0.0041698 | 0.0019823 | -0.082397 | 62.8693 | -60.0403 | 62.9791 | -59.8343 | -60.2005 | 0.009155 | -0.059509 | 62.8418 | -59.9442 | 63.0295 | -59.9487 | -60.0632 | -59.8801 | -0.07782 | -0.059509 | 0.050354 | 0.12817 | 59.9716 | -0.23804 | 60.0494 | -0.16022 | 0.01831 | -0.086975 | 0.10071 | 0.013733 | 0.082397 | -0.10071 | 0.064087 | -0.11902 | 0.20599 | 123.0194 | -0.004577 | 122.9736 | 122.9095 | 122.7859 | 122.8317 | 122.8043 | -122.9691 | -122.8729 | 122.9416 | 122.9919 | 59.8801 | 59.903
551.8281 | 123.1018 | -59.9716 | 62.9562 | -0.060425 | 0.0011257 | 0.064709 | 0.067232 | 0.0028199 | -0.00013676 | -0.0028989 | -0.058258 | -0.0001154 | 0.064922 | 0.063497 | -0.0039906 | 0.0041698 | -0.00015387 | -0.082397 | 62.883 | -60.0998 | 62.8922 | -59.9167 | -60.2646 | -0.073242 | -0.14191 | 62.8738 | -59.9899 | 62.9471 | -60.0952 | -60.1822 | -59.9854 | -0.12817 | -0.073242 | -0.064087 | 0.054932 | 59.8984 | -0.29297 | 60.0266 | -0.16479 | -0.01831 | -0.082398 | -0.009155 | -0.1236 | -0.013733 | -0.21057 | 0.004577 | -0.19226 | 0.1831 | 122.9919 | -0.10529 | 122.937 | 122.9828 | 122.8638 | 122.8546 | 122.8455 | -123.056 | -122.9462 | 122.8638 | 122.9187 | 59.8892 | 59.8297
552.8906 | 123.1934 | -59.9121 | 62.9654 | -0.052796 | 0.0032619 | 0.062145 | 0.066377 | 0.00025629 | -0.002273 | -0.0014035 | -0.015534 | 9.8198e-05 | 0.065136 | 0.06307 | -0.0027088 | 0.003529 | -0.0025037 | 0.018311 | 62.8738 | -60.0266 | 62.9242 | -60.0128 | -60.0403 | 0.10529 | 0.12817 | 62.8235 | -59.967 | 63.0753 | -59.8938 | -59.9716 | -59.8434 | -0.11444 | -0.091553 | -0.041199 | -0.10071 | 60.0174 | -0.12817 | 60.1318 | -0.013733 | -0.054932 | -0.14191 | 0.10986 | 0.01831 | 0.068664 | -0.05951 | 0.1236 | -0.004578 | 0.013733 | 122.9507 | 0.073242 | 123.0423 | 122.9004 | 122.7905 | 122.7859 | 122.7356 | -122.9919 | -122.9324 | 122.8363 | 122.9874 | 59.9304 | 60.0403
553.8281 | 123.1476 | -59.9533 | 62.9745 | -0.068054 | 0.0015529 | 0.062786 | 0.067872 | 0.0053833 | -0.002273 | -0.0031125 | -0.073517 | 0.003089 | 0.067272 | 0.061575 | -0.0033496 | 0.003529 | -0.0014355 | -0.045776 | 62.8784 | -60.0906 | 62.8601 | -59.7427 | -60.2097 | 0 | -0.050354 | 62.8784 | -59.9808 | 63.0066 | -60.0082 | -60.1089 | -59.9396 | -0.13733 | -0.09613 | -0.11444 | 0.21057 | 59.9533 | -0.25635 | 60.0906 | -0.11902 | -0.027466 | -0.09613 | 0.032044 | -0.054932 | 0.013733 | -0.15564 | 0.041199 | -0.12817 | 0.3479 | 122.9507 | -0.027466 | 122.9874 | 122.9691 | 122.8592 | 122.8317 | 122.8317 | -123.0652 | -122.9553 | 122.8134 | 122.9599 | 59.9075 | 59.903
554.8906 | 123.175 | -59.9167 | 62.9929 | -0.098572 | 0.00027134 | 0.062145 | 0.066377 | 0.00025629 | 7.6842e-05 | -0.0022581 | 0.024139 | 0.0015936 | 0.067272 | 0.063925 | -0.0044178 | 0.0031018 | -0.0050671 | 0.004578 | 62.9013 | -60.0403 | 63.0157 | -59.7565 | -60.0952 | 0.10071 | 0.059509 | 62.8738 | -59.9716 | 63.0157 | -59.935 | -60.0403 | -59.8801 | -0.1236 | -0.091553 | 0.022888 | 0.16022 | 60.0174 | -0.17853 | 60.141 | -0.054932 | -0.054932 | -0.11902 | 0.022888 | -0.018311 | 0.036621 | -0.1236 | 0.091553 | -0.068664 | 0.28381 | 123.056 | 0.036621 | 122.9874 | 122.9416 | 122.8455 | 122.818 | 122.7905 | -123.0331 | -122.9645 | 122.9324 | 122.9324 | 59.9213 | 59.9762
555.8281 | 123.1155 | -59.9533 | 62.9562 | -0.090943 | 0.0030483 | 0.062145 | 0.067445 | 0.0015381 | -0.0014184 | -0.00054907 | -0.088776 | 0.0018072 | 0.064922 | 0.063497 | -0.0046314 | 0.0041698 | 0.0015551 | -0.086975 | 62.8784 | -60.0952 | 62.9288 | -59.8801 | -60.228 | -0.032043 | -0.07782 | 62.8647 | -59.9991 | 62.9883 | -60.0357 | -60.1547 | -59.9625 | -0.14191 | -0.07782 | -0.027466 | 0.073242 | 59.9213 | -0.27466 | 60.0632 | -0.13275 | -0.045776 | -0.091553 | 0.032043 | -0.082398 | -0.009155 | -0.20142 | 0.036621 | -0.15564 | 0.21515 | 123.024 | -0.036622 | 122.9874 | 122.9736 | 122.8638 | 122.8317 | 122.818 | -123.0515 | -122.9553 | 122.8821 | 122.9416 | 59.8663 | 59.8755
556.8281 | 123.1338 | -59.9533 | 63.0112 | 0.054016 | 0.00069854 | 0.064709 | 0.067232 | -0.00017091 | -0.003982 | 0.00030553 | -0.021637 | 0.0018072 | 0.065777 | 0.059439 | -0.004845 | 0.0020336 | 0.0013415 | -0.16937 | 62.9105 | -60.054 | 62.8647 | -59.8846 | -60.1913 | 0.032043 | -0.041199 | 62.9013 | -59.9625 | 62.9745 | -59.9945 | -60.1181 | -59.935 | -0.10071 | -0.10071 | -0.14648 | 0.068664 | 59.9854 | -0.23804 | 60.0861 | -0.13733 | -0.009155 | -0.10986 | -0.036621 | -0.041199 | 0.01831 | -0.16479 | 0.027465 | -0.15564 | 0.16937 | 122.9187 | -0.032044 | 122.937 | 122.9645 | 122.8638 | 122.8638 | 122.8546 | -123.0652 | -122.9736 | 122.818 | 122.9279 | 59.7839 | 59.9121
557.8906 | 123.1934 | -59.9625 | 62.9471 | -0.068054 | 0.0017667 | 0.063854 | 0.064454 | -0.00059811 | -0.0012048 | -0.00054907 | 0.024139 | 0.0011664 | 0.067058 | 0.063497 | -0.0024952 | 0.0020336 | -0.0020765 | -0.07782 | 62.8647 | -60.054 | 62.9883 | -59.7244 | -60.1456 | -0.027466 | -0.064087 | 62.851 | -59.967 | 63.0203 | -59.9487 | -60.0586 | -59.9075 | -0.091553 | -0.082398 | 0.041198 | 0.23804 | 59.935 | -0.18311 | 60.0266 | -0.091553 | -0.004578 | -0.096131 | 0.073242 | 0.013733 | 0.054931 | -0.096131 | 0.059509 | -0.091553 | 0.32959 | 123.0423 | 0.018311 | 122.9874 | 122.9187 | 122.818 | 122.8271 | 122.8134 | -123.0011 | -122.9141 | 122.9507 | 122.9828 | 59.8846 | 59.8984
558.8281 | 123.1247 | -59.9487 | 62.9425 | -0.11383 | 0.0013393 | 0.064068 | 0.065523 | 0.00025629 | -0.003982 | -0.00012167 | -0.064362 | 0.0024482 | 0.066631 | 0.066915 | -0.0035632 | 0.003529 | 0.00091433 | -0.018311 | 62.9105 | -60.0677 | 62.9745 | -59.8297 | -60.2188 | 0.013733 | 0 | 62.8876 | -59.967 | 63.002 | -59.9762 | -60.0998 | -59.9121 | -0.11902 | -0.032044 | 0.032043 | 0.11902 | 59.9625 | -0.27008 | 60.0815 | -0.15106 | -0.018311 | -0.054932 | 0.059509 | -0.027466 | 0.036621 | -0.15106 | 0.054932 | -0.13275 | 0.23804 | 123.0423 | -0.009155 | 122.9691 | 122.9782 | 122.8546 | 122.8592 | 122.8363 | -123.0103 | -122.9095 | 122.9233 | 122.9507 | 59.9304 | 59.9487
559.8906 | 123.2162 | -59.935 | 62.9517 | -0.068054 | 0.0019803 | 0.063427 | 0.064668 | 0.00046989 | -0.0018458 | -0.00033547 | 0.011932 | 0.0018072 | 0.063427 | 0.063497 | -0.0050586 | 0.0048108 | -0.0012219 | 0.009155 | 62.8876 | -60.0311 | 63.0295 | -59.7153 | -60.0815 | 0.11902 | 0.31128 | 62.915 | -59.9213 | 63.0295 | -59.8618 | -59.9579 | -59.8709 | -0.09613 | -0.064087 | 0.07782 | 0.21973 | 60.054 | -0.14648 | 60.1501 | -0.050354 | 0.013733 | -0.036621 | 0.07782 | 0.073243 | 0.064087 | -0.022888 | 0.050354 | -0.036621 | 0.31586 | 123.0606 | 0.05951 | 122.9507 | 122.9187 | 122.8363 | 122.8226 | 122.85 | -122.9828 | -122.8729 | 122.9645 | 122.9645 | 59.9442 | 60.2463
560.8281 | 123.1293 | -59.9487 | 62.9745 | -0.11383 | 0.00027134 | 0.061932 | 0.067445 | -0.0044433 | -0.005691 | -0.0022581 | -0.024689 | 0.00138 | 0.066845 | 0.069479 | -0.0033496 | 0.0039562 | 0.0011279 | -0.036621 | 62.8922 | -60.0998 | 62.9333 | -59.8755 | -60.2325 | 0.004578 | -0.054932 | 62.9333 | -60.0037 | 62.9791 | -60.0174 | -60.1181 | -59.9442 | -0.15106 | -0.082397 | -0.041198 | 0.073242 | 59.9533 | -0.28381 | 60.1044 | -0.13275 | -0.054932 | -0.041198 | 0.004578 | -0.068665 | 0.004577 | -0.16937 | 0.059509 | -0.11444 | 0.2243 | 123.0331 | -0.013733 | 122.9828 | 122.9919 | 122.937 | 122.8409 | 122.8821 | -123.0743 | -122.9782 | 122.8821 | 122.9279 | 59.9121 | 59.8938
561.8906 | 123.1705 | -59.9167 | 62.9883 | 0.046386 | 0.0032619 | 0.064068 | 0.065095 | -0.0010253 | -0.0024866 | -0.0022581 | 0.033295 | 0.0011664 | 0.067272 | 0.059011 | -0.0035632 | 0.0013928 | -0.00058107 | -0.16479 | 62.8601 | -60.0357 | 62.9974 | -59.7382 | -60.0815 | 0.11444 | 0.09613 | 62.8738 | -59.9487 | 63.0615 | -59.903 | -59.9945 | -59.8572 | -0.11902 | -0.12817 | 0.009156 | 0.17853 | 60.0311 | -0.16479 | 60.1501 | -0.045776 | -0.032043 | -0.11444 | 0.073242 | 0.013733 | 0.059509 | -0.07782 | 0.091552 | -0.045777 | 0.29755 | 123.0331 | 0.045776 | 123.0103 | 122.8958 | 122.8226 | 122.7768 | 122.7905 | -123.024 | -122.937 | 122.9141 | 122.9782 | 59.7519 | 60.0128
562.8281 | 123.1476 | -59.9396 | 62.97 | -0.052796 | 0.00048494 | 0.061718 | 0.068727 | 0.0019653 | 7.6842e-05 | -0.00054907 | -0.06131 | 0.0011664 | 0.066631 | 0.068197 | -0.002068 | 0.0037426 | -0.0010083 | -0.027466 | 62.883 | -60.0723 | 62.9562 | -59.8297 | -60.1868 | 0.004578 | 0.013733 | 62.9013 | -59.967 | 63.0295 | -59.9808 | -60.0861 | -59.9075 | -0.13275 | -0.086975 | -0.013733 | 0.10986 | 59.9442 | -0.24719 | 60.0769 | -0.11444 | -0.027466 | -0.068665 | 0.059509 | -0.041199 | 0.032043 | -0.14649 | 0.059509 | -0.11902 | 0.24262 | 123.0286 | -0.013733 | 122.9965 | 122.9553 | 122.8683 | 122.8226 | 122.8409 | -123.0423 | -122.937 | 122.8958 | 122.9691 | 59.9121 | 59.9533
563.8906 | 123.23 | -59.9075 | 62.9288 | -0.068054 | 0.0015529 | 0.063641 | 0.06595 | 0.0021789 | -0.00035036 | -0.0016171 | 0.039398 | 0.0011664 | 0.067913 | 0.066915 | -0.002068 | -0.00095696 | -0.0020765 | -0.036621 | 62.8601 | -60.0494 | 62.9974 | -59.7656 | -60.1181 | 0.073242 | 0.064087 | 62.851 | -59.935 | 63.0936 | -59.8892 | -59.9762 | -59.8389 | -0.14191 | -0.068665 | 0.068665 | 0.14191 | 59.9808 | -0.21057 | 60.1227 | -0.068665 | -0.027466 | -0.07782 | 0.16479 | 0.018311 | 0.068665 | -0.068664 | 0.096131 | -0.041198 | 0.28381 | 123.0469 | 0.045777 | 123.0286 | 122.9095 | 122.7859 | 122.7676 | 122.7585 | -122.9782 | -122.8638 | 122.905 | 123.0011 | 59.8709 | 59.9716
564.8281 | 123.0927 | -59.9579 | 63.0066 | -0.022278 | 0.00027134 | 0.062145 | 0.066377 | 0.00068369 | -0.0033412 | -0.0018307 | -0.0033265 | 0.0026618 | 0.066631 | 0.062643 | -0.0037768 | 0.0056652 | -0.00079467 | 0.068665 | 62.9608 | -60.0128 | 62.883 | -59.8709 | -60.2142 | -0.013733 | -0.064087 | 62.9059 | -59.9716 | 62.9837 | -60.0082 | -60.1227 | -59.9396 | -0.054931 | -0.045777 | -0.1236 | 0.086975 | 59.9442 | -0.25635 | 59.9991 | -0.20142 | -0.013733 | -0.10071 | -0.022888 | -0.050354 | 0.018311 | -0.16479 | 0.032044 | -0.15106 | 0.14191 | 122.8958 | -0.036621 | 122.9553 | 122.9736 | 122.8775 | 122.9187 | 122.8638 | -123.0194 | -122.9782 | 122.8409 | 122.9416 | 60.0266 | 59.8938
565.8906 | 123.2666 | -59.9121 | 62.9608 | -0.083313 | 0.0017667 | 0.061077 | 0.065309 | -0.0012391 | -0.00056396 | -0.00033547 | 0.039398 | -0.000329 | 0.064495 | 0.06072 | -0.0052722 | 0.0028882 | 0.0011279 | -0.027466 | 62.8693 | -60.0494 | 63.0112 | -59.7427 | -60.0769 | 0.11444 | 0.10986 | 62.851 | -59.9396 | 63.1119 | -59.8663 | -59.967 | -59.8251 | -0.13733 | -0.091552 | 0.050354 | 0.16937 | 60.0266 | -0.16479 | 60.1639 | -0.027466 | -0.027466 | -0.10986 | 0.15106 | 0.045776 | 0.086975 | -0.054932 | 0.11444 | -0.027466 | 0.3067 | 123.0606 | 0.073242 | 123.0515 | 122.9187 | 122.7905 | 122.7814 | 122.7631 | -123.0103 | -122.9004 | 122.9233 | 123.024 | 59.8846 | 60.022
566.8281 | 123.1293 | -59.9396 | 63.0157 | -0.029907 | -0.00015586 | 0.060863 | 0.067445 | 0.00046989 | -0.00099116 | -0.0022581 | -0.0094299 | 0.0024482 | 0.066631 | 0.064779 | -0.0029224 | 0.0033154 | -0.0029309 | -0.064087 | 62.8784 | -60.054 | 62.9013 | -59.8755 | -60.1959 | 0.041199 | -0.027466 | 62.9196 | -59.9716 | 62.9471 | -59.9991 | -60.1364 | -59.9579 | -0.11444 | -0.13733 | -0.11444 | 0.064087 | 59.9808 | -0.25635 | 60.0952 | -0.14191 | -0.032044 | -0.09613 | -0.068664 | -0.059509 | -0.018311 | -0.19684 | 0.013733 | -0.1648 | 0.17853 | 122.9553 | -0.027465 | 122.9187 | 122.9324 | 122.8912 | 122.818 | 122.8592 | -123.0698 | -122.9874 | 122.8409 | 122.8867 | 59.8755 | 59.9121
567.8906 | 123.2391 | -59.9167 | 62.9562 | -0.060425 | 0.0015529 | 0.063641 | 0.066804 | -0.0016663 | -0.0029138 | -0.0028989 | 0.036346 | 0.0020208 | 0.065349 | 0.066274 | -0.0033496 | 0.0033154 | -0.0025037 | -0.009155 | 62.8693 | -60.0266 | 63.0203 | -59.7336 | -60.0906 | 0.1236 | 0.1236 | 62.8601 | -59.935 | 63.1256 | -59.8572 | -59.9625 | -59.8343 | -0.10986 | -0.086975 | 0.064087 | 0.18311 | 60.0403 | -0.17395 | 60.1501 | -0.064087 | -0.018311 | -0.096131 | 0.16937 | 0.059509 | 0.082397 | -0.045776 | 0.10071 | -0.027465 | 0.29297 | 123.0469 | 0.07782 | 123.0606 | 122.8958 | 122.7951 | 122.7859 | 122.7768 | -122.9828 | -122.8912 | 122.937 | 123.0423 | 59.9075 | 60.0403
568.8281 | 123.0469 | -59.9304 | 63.0157 | -0.075684 | -0.00015586 | 0.063 | 0.067018 | -0.00038451 | -0.0012048 | -0.0024717 | -0.036896 | 0.0043708 | 0.067699 | 0.066061 | -0.0029224 | 0.0048108 | -0.0018629 | -0.059509 | 62.9333 | -60.0677 | 62.8967 | -59.8709 | -60.2097 | 0.032043 | -0.041199 | 62.9333 | -59.9899 | 62.9562 | -60.0677 | -59.8663 | -59.7519 | -0.13733 | -0.082397 | -0.11902 | 0.059509 | 59.9625 | -0.27924 | 60.0998 | -0.14191 | -0.059509 | -0.082397 | -0.059509 | -0.13733 | 0.17853 | 0.064087 | 0.23804 | 0.1236 | 0.19684 | 122.9645 | -0.07782 | 122.9462 | 123.0011 | 122.9233 | 122.8638 | 122.8638 | -123.0835 | -123.0057 | 122.8271 | 122.8867 | 59.8709 | 59.8892
569.8906 | 123.23 | -59.9533 | 62.9379 | -0.037537 | 0.00091214 | 0.059795 | 0.066163 | -0.0012391 | -0.0016322 | -0.00076267 | -0.0002747 | 0.0018072 | 0.066845 | 0.061148 | -0.0052722 | 0.003529 | -0.0044263 | -0.064087 | 62.8784 | -60.0449 | 62.9791 | -59.7839 | -60.1364 | 0.054932 | 0 | 62.8464 | -59.9716 | 63.0569 | -59.9075 | -60.0128 | -59.848 | -0.091553 | -0.059509 | 0.041199 | 0.16937 | 60.0082 | -0.18311 | 60.0998 | -0.091553 | -0.018311 | -0.091552 | 0.11902 | 0.045776 | 0.10529 | -0.059509 | 0.1236 | -0.041198 | 0.26093 | 123.024 | 0.064087 | 123.0286 | 122.9233 | 122.818 | 122.8317 | 122.7997 | -122.9828 | -122.9095 | 122.9324 | 123.0103 | 59.8892 | 59.9533
570.8281 | 123.111 | -59.9579 | 62.9837 | -0.1062 | 0.0015529 | 0.063641 | 0.066377 | -0.0020935 | -0.0014184 | -0.0016171 | -0.030792 | 0.00138 | 0.064922 | 0.06072 | -0.0061268 | 0.0033154 | -0.0027173 | -0.013733 | 62.9105 | -60.0449 | 62.9654 | -59.7977 | -60.1639 | 0.073242 | 0.009155 | 62.9059 | -59.9716 | 63.0249 | -60.022 | -60.1227 | -59.9579 | -0.086975 | -0.073243 | -0.018311 | 0.16022 | 60.0311 | -0.20599 | 60.1181 | -0.11902 | -0.013733 | -0.07782 | 0.041198 | -0.064087 | 0 | -0.16479 | 0.013733 | -0.15106 | 0.24719 | 123.0103 | -0.050354 | 122.9965 | 122.9553 | 122.8775 | 122.8683 | 122.8638 | -123.0286 | -122.9553 | 122.9233 | 122.9828 | 59.9442 | 59.967
571.8906 | 123.1796 | -59.9762 | 62.9288 | -0.052796 | 0.0019803 | 0.063213 | 0.066377 | -0.0018799 | -0.0029138 | -0.00054907 | -0.0002747 | 0.0009528 | 0.065136 | 0.062429 | -0.0039906 | 0.0033154 | -0.0031445 | -0.09613 | 62.8326 | -60.0723 | 62.9562 | -59.8526 | -60.2097 | -0.032043 | -0.07782 | 62.8555 | -59.9854 | 62.9974 | -59.9854 | -60.0815 | -59.9167 | -0.096131 | -0.09613 | 0.027466 | 0.1236 | 59.9442 | -0.23346 | 60.0403 | -0.13733 | -0.009156 | -0.073242 | 0.068665 | -0.009156 | 0.059509 | -0.10529 | 0.068665 | -0.09613 | 0.21973 | 123.0286 | 0 | 122.9828 | 122.905 | 122.8409 | 122.8088 | 122.8317 | -123.0011 | -122.9141 | 122.9324 | 122.9736 | 59.8801 | 59.8984
572.8281 | 123.1247 | -59.935 | 62.9791 | -0.083313 | 0.0021939 | 0.063641 | 0.068086 | -0.00017091 | -0.00077756 | -0.00076267 | -0.024689 | 0.0020208 | 0.067272 | 0.06072 | -0.003136 | 0.0041698 | -0.0010083 | 0 | 62.8738 | -60.0311 | 62.9791 | -59.8114 | -60.1547 | 0.07782 | 0.018311 | 62.8876 | -59.9716 | 62.9837 | -59.9625 | -60.0998 | -59.9442 | -0.09613 | -0.10529 | 0 | 0.1236 | 60.0128 | -0.21973 | 60.1089 | -0.1236 | -0.036621 | -0.091553 | 0.004578 | -0.027465 | -0.009155 | -0.16479 | 0.027466 | -0.12817 | 0.21973 | 123.0103 | 0.009156 | 122.9553 | 122.905 | 122.8592 | 122.8088 | 122.8226 | -123.0103 | -122.9507 | 122.9141 | 122.9187 | 59.935 | 59.9533
573.8906 | 123.2254 | -59.9304 | 62.9425 | -0.060425 | 0.0021939 | 0.063854 | 0.065523 | -0.00059811 | -0.0035548 | -0.00033547 | 0.024139 | 9.8198e-05 | 0.064068 | 0.060293 | -0.0039906 | 0.0041698 | -0.0033581 | -0.068665 | 62.8784 | -60.054 | 62.9791 | -59.8022 | -60.1547 | 0.036621 | -0.004578 | 62.851 | -59.9625 | 63.0707 | -59.9258 | -60.0128 | -59.848 | -0.1236 | -0.064087 | 0.036621 | 0.12817 | 59.967 | -0.2243 | 60.0906 | -0.10071 | -0.032043 | -0.091553 | 0.12817 | 0.004578 | 0.082398 | -0.082397 | 0.11444 | -0.050354 | 0.25177 | 123.0331 | 0.036621 | 123.0331 | 122.9324 | 122.8134 | 122.8088 | 122.7814 | -122.9965 | -122.905 | 122.9095 | 123.0011 | 59.8618 | 59.9258
574.8281 | 123.2574 | -59.9258 | 62.9608 | -0.12909 | -0.0010105 | 0.063427 | 0.065095 | -0.0010253 | -0.00013676 | -0.0011899 | 0.027191 | 0.0015936 | 0.06364 | 0.061361 | -0.0056994 | 0.003529 | -0.0022901 | 0.022888 | 62.883 | -60.0174 | 63.0478 | -59.7061 | -60.0723 | 0.13733 | 0.1236 | 62.8693 | -59.935 | 63.089 | -59.8801 | -59.9854 | -59.8343 | -0.091553 | -0.077819 | 0.086976 | 0.21973 | 60.0632 | -0.14648 | 60.1547 | -0.054932 | -0.009156 | -0.091552 | 0.12817 | 0.045776 | 0.091552 | -0.05951 | 0.10071 | -0.050354 | 0.31128 | 123.0652 | 0.054932 | 123.024 | 122.9004 | 122.8043 | 122.8088 | 122.7951 | -122.9782 | -122.8958 | 122.9736 | 123.0148 | 59.9487 | 60.0494
575.8906 | 123.1796 | -59.9579 | 62.9517 | -0.090943 | 0.00091214 | 0.063427 | 0.066377 | 0.0030335 | -0.0029138 | 0.00030553 | -0.024689 | -0.0001154 | 0.065136 | 0.061788 | -0.004845 | 0.0033154 | -0.0029309 | -0.10529 | 62.8372 | -60.0815 | 62.9471 | -59.8114 | -60.228 | -0.022888 | -0.086975 | 62.851 | -60.0037 | 63.0249 | -59.9716 | -60.0769 | -59.8938 | -0.1236 | -0.11444 | -0.004577 | 0.14649 | 59.935 | -0.27008 | 60.0586 | -0.14648 | -0.045776 | -0.10071 | 0.073242 | -0.013733 | 0.064087 | -0.11902 | 0.10986 | -0.073242 | 0.27008 | 123.0286 | 0.032043 | 123.0286 | 122.9187 | 122.8546 | 122.7951 | 122.8088 | -123.0331 | -122.9553 | 122.905 | 122.9828 | 59.8526 | 59.8709
576.8281 | 123.1796 | -59.9487 | 62.97 | -0.052796 | 0.0028347 | 0.063213 | 0.067018 | 0.0049561 | -0.0029138 | 0.0020145 | -0.076569 | 0.0033026 | 0.065349 | 0.071188 | -0.0033496 | 0.0050244 | -0.00058107 | -0.050354 | 62.915 | -60.0906 | 62.9608 | -59.8343 | -60.1822 | 0.032043 | -0.013733 | 62.9196 | -59.9945 | 62.9974 | -59.967 | -60.0906 | -59.9167 | -0.14191 | -0.054932 | -0.009156 | 0.11444 | 59.9808 | -0.23346 | 60.1227 | -0.091553 | -0.045777 | -0.050354 | 0.027466 | -0.018311 | 0.032043 | -0.14191 | 0.07782 | -0.09613 | 0.25635 | 123.0515 | 0.027466 | 122.9919 | 123.0057 | 122.9141 | 122.8638 | 122.8683 | -123.0606 | -122.9645 | 122.9095 | 122.9462 | 59.8984 | 59.935
577.8906 | 123.2117 | -59.9533 | 62.9105 | -0.090943 | 0.0015529 | 0.064281 | 0.067232 | 0.00089729 | -0.0031274 | -0.00054907 | -0.049103 | -0.0005426 | 0.064068 | 0.064138 | -0.0037768 | 0.0024608 | -0.0031445 | -0.091553 | 62.8281 | -60.0632 | 62.9745 | -59.8068 | -60.1639 | -0.027466 | -0.068665 | 62.8143 | -59.9899 | 63.0753 | -59.9396 | -60.054 | -59.8709 | -0.10986 | -0.082397 | 0.064087 | 0.14648 | 59.9258 | -0.21057 | 60.0357 | -0.10071 | -0.036621 | -0.09613 | 0.1648 | 0.013733 | 0.082397 | -0.10071 | 0.11902 | -0.064087 | 0.25635 | 123.0377 | 0.050354 | 123.0652 | 122.8912 | 122.8043 | 122.7814 | 122.7676 | -122.9736 | -122.9004 | 122.9279 | 123.0286 | 59.8618 | 59.8846
578.8281 | 123.2483 | -59.9258 | 62.915 | -0.090943 | -0.00036966 | 0.064068 | 0.064668 | -0.0023071 | -0.0020594 | 9.193e-05 | -0.0002747 | 0.00138 | 0.065563 | 0.062002 | -0.0039906 | 0.0028882 | -0.0016493 | -0.032043 | 62.8601 | -60.0266 | 63.0157 | -59.7427 | -60.0952 | 0.10986 | 0.073242 | 62.8647 | -59.9625 | 63.1119 | -59.8572 | -59.9579 | -59.8206 | -0.10071 | -0.054932 | 0.10071 | 0.18311 | 60.0357 | -0.16937 | 60.1364 | -0.068665 | -0.036621 | -0.050354 | 0.19684 | 0.068664 | 0.10529 | -0.032044 | 0.14191 | 0.004577 | 0.28381 | 123.0423 | 0.10529 | 123.0743 | 122.8867 | 122.8271 | 122.7859 | 122.7905 | -122.9416 | -122.8775 | 122.9416 | 123.0377 | 59.8938 | 59.9991
579.8906 | 123.1613 | -59.9716 | 62.9105 | -0.12146 | -0.0012241 | 0.064922 | 0.06595 | 0.0011109 | -0.0024866 | -0.00012167 | -0.021637 | 0.0005256 | 0.064495 | 0.059439 | -0.0052722 | 0.003529 | -0.0014355 | -0.10529 | 62.8006 | -60.0723 | 62.9562 | -59.8297 | -60.1959 | -0.018311 | -0.07782 | 62.8555 | -60.0082 | 63.0066 | -59.9716 | -60.0815 | -59.8984 | -0.10071 | -0.10986 | 0.045777 | 0.14191 | 59.9533 | -0.2243 | 60.054 | -0.1236 | -0.036621 | -0.054931 | 0.096131 | 0 | 0.073243 | -0.10986 | 0.10986 | -0.073242 | 0.24262 | 123.0286 | 0.036621 | 123.0148 | 122.8729 | 122.8638 | 122.7722 | 122.8271 | -122.9828 | -122.9187 | 122.9279 | 122.9782 | 59.8663 | 59.8938
580.8281 | 123.23 | -59.9762 | 62.9608 | -0.060425 | 0.0011257 | 0.064495 | 0.064882 | 0.00046989 | -0.0014184 | -0.0024717 | -0.018585 | 0.00138 | 0.065777 | 0.064565 | -0.0044178 | 0.0054516 | -0.0048535 | -0.10986 | 62.8693 | -60.0449 | 62.9379 | -59.8434 | -60.1959 | 0.004578 | -0.091553 | 62.8418 | -59.9762 | 63.0157 | -59.9579 | -60.0815 | -59.903 | -0.068665 | -0.091552 | -0.022888 | 0.13275 | 59.9808 | -0.21973 | 60.0494 | -0.15106 | 0 | -0.11902 | 0.054932 | 0.01831 | 0.073242 | -0.10529 | 0.073242 | -0.10529 | 0.20142 | 122.9828 | 0.01831 | 122.9919 | 122.9141 | 122.818 | 122.8455 | 122.818 | -123.0057 | -122.937 | 122.9141 | 122.9919 | 59.8663 | 59.8846
581.9062 | 123.1018 | -59.9625 | 62.97 | -0.045166 | 0.0013393 | 0.063854 | 0.066163 | 0.00025629 | -0.0012048 | 0.00030553 | -0.036896 | -0.0001154 | 0.063854 | 0.066915 | -0.0044178 | 0.003529 | -0.00036747 | -0.013733 | 62.883 | -60.054 | 62.9425 | -59.8114 | -60.1776 | 0.064087 | -0.013733 | 62.9013 | -59.9533 | 62.9883 | -59.9899 | -60.0906 | -59.935 | -0.091553 | -0.086975 | -0.027466 | 0.15106 | 60.0266 | -0.21515 | 60.1181 | -0.1236 | 0.009155 | -0.068665 | 0.01831 | -0.027466 | 0.027465 | -0.12817 | 0.01831 | -0.13733 | 0.24262 | 122.9965 | -0.036621 | 122.9416 | 122.937 | 122.8546 | 122.8455 | 122.8638 | -123.024 | -122.9233 | 122.905 | 122.9507 | 59.9487 | 59.9487
582.8281 | 123.1842 | -59.9579 | 62.9333 | -0.083313 | 0.00027134 | 0.062145 | 0.06595 | -0.00059811 | -0.0016322 | 0.00030553 | -0.0063781 | -0.000329 | 0.066631 | 0.060293 | -0.004845 | 0.0016064 | -0.0027173 | -0.11902 | 62.8555 | -60.0677 | 62.9379 | -59.8389 | -60.1959 | -0.032043 | -0.10986 | 62.851 | -59.9899 | 62.9974 | -59.9808 | -60.0723 | -59.9121 | -0.10986 | -0.07782 | 0.004577 | 0.11902 | 59.9258 | -0.23804 | 60.0357 | -0.12817 | -0.032043 | -0.082398 | 0.064087 | -0.022888 | 0.045777 | -0.11444 | 0.07782 | -0.082398 | 0.22888 | 123.0057 | 0.009155 | 122.9874 | 122.9233 | 122.8409 | 122.8134 | 122.8088 | -123.0011 | -122.9233 | 122.8958 | 122.9553 | 59.8389 | 59.848
583.8906 | 123.1613 | -59.9533 | 62.9562 | -0.060425 | 0.00069854 | 0.064922 | 0.068513 | -0.0025207 | -0.0012048 | 0.0015871 | -0.11929 | 0.0022346 | 0.066845 | 0.067983 | -0.0044178 | 0.0043836 | -0.0014355 | -0.16022 | 62.8601 | -60.1135 | 62.8738 | -59.9533 | -60.3104 | -0.11444 | -0.21057 | 62.883 | -60.0174 | 63.0295 | -60.347 | -60.1639 | -59.7565 | -0.16022 | -0.096131 | -0.082398 | 0 | 59.8389 | -0.35706 | 59.9991 | -0.19684 | -0.064087 | -0.073242 | 0.073242 | -0.39368 | 0.19684 | -0.21057 | 0.26093 | -0.14648 | 0.16022 | 122.9874 | -0.32959 | 123.0469 | 122.9736 | 122.9004 | 122.8134 | 122.8363 | -123.0698 | -122.9736 | 122.8271 | 122.9828 | 59.7931 | 59.7427
584.8281 | 123.1842 | -59.9762 | 62.9059 | -0.15198 | 0.0011257 | 0.062572 | 0.066591 | -0.0029479 | -0.00035036 | 9.193e-05 | -0.018585 | -0.0007562 | 0.064281 | 0.061361 | -0.0039906 | 0.0043836 | 0.0011279 | -0.11902 | 62.8235 | -60.054 | 62.9745 | -59.7977 | -60.173 | -0.027466 | -0.082397 | 62.8418 | -59.9899 | 63.0249 | -59.9854 | -60.0677 | -59.9075 | -0.07782 | -0.082398 | 0.068664 | 0.17853 | 59.9487 | -0.19684 | 60.0266 | -0.11902 | -0.013733 | -0.064087 | 0.11902 | -0.009156 | 0.068664 | -0.091553 | 0.082397 | -0.07782 | 0.25635 | 123.0286 | 0.004577 | 123.0148 | 122.8775 | 122.8317 | 122.7997 | 122.818 | -122.9599 | -122.8958 | 122.9507 | 123.0011 | 59.8572 | 59.8938
585.8906 | 123.0927 | -59.9716 | 62.9333 | -0.052796 | 0.0015529 | 0.064068 | 0.067018 | 0.0026063 | -0.0020594 | -0.00054907 | -0.10709 | 0.0005256 | 0.065563 | 0.06542 | -0.0037768 | 0.0033154 | 0.00070073 | -0.10529 | 62.8601 | -60.1089 | 62.9013 | -59.9121 | -60.2829 | -0.082397 | -0.15106 | 62.8876 | -59.9899 | 62.9608 | -60.0861 | -60.1776 | -59.9762 | -0.13733 | -0.073243 | -0.032044 | 0.05951 | 59.8892 | -0.31128 | 60.0266 | -0.17395 | -0.01831 | -0.045777 | 0.027465 | -0.11444 | -0.004577 | -0.20599 | 0.013733 | -0.18768 | 0.19684 | 123.0103 | -0.096131 | 122.9507 | 122.9691 | 122.8775 | 122.8317 | 122.8592 | -123.0423 | -122.9233 | 122.8729 | 122.9324 | 59.8663 | 59.8206
586.8438 | 123.1247 | -59.9442 | 62.9654 | -0.052796 | 0.00091214 | 0.062145 | 0.064668 | -0.00059811 | -0.0046228 | -0.00076267 | -0.088776 | 0.00138 | 0.067913 | 0.062856 | -0.0037768 | 0.0037426 | -0.0027173 | -0.064087 | 62.9013 | -60.0769 | 62.9471 | -59.8343 | -60.2097 | 0 | -0.12817 | 62.8601 | -59.9945 | 63.0066 | -59.9762 | -60.1135 | -59.935 | -0.13275 | -0.064087 | -0.01831 | 0.10986 | 59.9442 | -0.2655 | 60.0769 | -0.13275 | -0.050354 | -0.10529 | 0.041199 | -0.032043 | 0.009155 | -0.16937 | 0.059509 | -0.11902 | 0.24261 | 123.024 | 0.018311 | 123.0011 | 122.9782 | 122.8546 | 122.8455 | 122.8043 | -123.0423 | -122.9599 | 122.8912 | 122.9507 | 59.8801 | 59.816
587.8906 | 123.1247 | -59.9899 | 62.9562 | -0.037537 | 0.00091214 | 0.058727 | 0.067659 | 0.00089729 | -0.0018458 | -0.00033547 | -0.082672 | 0.0020208 | 0.066845 | 0.064993 | -0.0044178 | 0.0050244 | -0.00079467 | -0.20599 | 62.8784 | -60.0815 | 62.9379 | -59.8709 | -60.2097 | 0 | -0.073242 | 62.8784 | -59.9945 | 62.9974 | -59.9991 | -60.1273 | -59.9213 | -0.091553 | -0.07782 | -0.018311 | 0.11902 | 59.9899 | -0.21973 | 60.0815 | -0.12817 | -0.004578 | -0.07782 | 0.041199 | -0.009155 | 0.068664 | -0.13733 | 0.073242 | -0.13275 | 0.21057 | 123.0194 | -0.004577 | 122.9919 | 122.9599 | 122.8729 | 122.8683 | 122.8683 | -123.0377 | -122.9507 | 122.9279 | 122.9874 | 59.7839 | 59.9167
588.8281 | 123.1934 | -59.9533 | 62.8967 | -0.1062 | 0.0013393 | 0.063641 | 0.065309 | 0.0017517 | -0.0012048 | -0.00033547 | -0.018585 | 0.0022346 | 0.064495 | 0.060934 | -0.0035632 | 0.0037426 | -0.0025037 | -0.086975 | 62.8098 | -60.0632 | 62.9791 | -59.7885 | -60.1639 | -0.032043 | -0.26093 | 62.7869 | -60.0174 | 63.0478 | -59.9075 | -60.0128 | -59.8526 | -0.10986 | -0.086976 | 0.082397 | 0.16479 | 59.9213 | -0.21057 | 60.0311 | -0.10071 | -0.064087 | -0.10986 | 0.15106 | 0.045776 | 0.10071 | -0.059509 | 0.16479 | 0.004578 | 0.27466 | 123.0423 | 0.10986 | 123.0652 | 122.8729 | 122.8043 | 122.7631 | 122.7402 | -122.9599 | -122.9141 | 122.9324 | 123.0011 | 59.8663 | 59.6924
589.8906 | 123.1018 | -59.9854 | 62.9425 | -0.060425 | 0.0024075 | 0.064495 | 0.068513 | 0.0023925 | -0.0024866 | -0.0018307 | -0.070465 | 0.0026618 | 0.063854 | 0.064565 | -0.004845 | 0.0041698 | 0.0028369 | -0.10529 | 62.883 | -60.0906 | 62.8922 | -59.8892 | -60.2692 | -0.059509 | -0.16479 | 62.9105 | -60.0037 | 62.9608 | -60.0357 | -60.1547 | -59.9533 | -0.10529 | -0.059509 | -0.050354 | 0.096131 | 59.9258 | -0.28381 | 60.0311 | -0.17853 | -0.01831 | -0.032044 | 0.01831 | -0.050354 | 0.032044 | -0.16937 | 0.050354 | -0.15106 | 0.20142 | 122.9828 | -0.032044 | 122.9645 | 122.9736 | 122.9141 | 122.8683 | 122.8958 | -123.0331 | -122.9462 | 122.8775 | 122.9462 | 59.8801 | 59.8206
590.8281 | 123.2254 | -59.935 | 62.8876 | -0.052796 | 0.0017667 | 0.061504 | 0.06595 | -0.0023071 | 7.6842e-05 | 0.0018009 | -0.042999 | 0.0007392 | 0.065136 | 0.060507 | -0.0046314 | 0.00182 | 0.00070073 | -0.16022 | 62.8555 | -60.0769 | 62.9471 | -59.8297 | -60.1822 | -0.059509 | -0.082397 | 62.8281 | -59.9716 | 63.0569 | -59.9396 | -60.0632 | -59.8618 | -0.14191 | -0.032043 | 0.05951 | 0.10529 | 59.8755 | -0.24719 | 60.0174 | -0.10529 | -0.036621 | -0.059509 | 0.16937 | -0.004577 | 0.073243 | -0.12817 | 0.10986 | -0.091552 | 0.24719 | 123.024 | 0.032044 | 123.0286 | 122.9324 | 122.7997 | 122.7905 | 122.7631 | -122.9645 | -122.8592 | 122.8821 | 122.9919 | 59.7748 | 59.8526
591.9062 | 123.1979 | -59.935 | 62.9379 | -0.13672 | -0.00036966 | 0.059795 | 0.066591 | -0.0010253 | -0.0029138 | -0.0033261 | 0.027191 | 0.0015936 | 0.065777 | 0.06307 | -0.0042042 | 0.0043836 | -0.0054945 | -0.059509 | 62.8693 | -60.0174 | 63.0249 | -59.7061 | -60.0815 | 0.11902 | 0.09613 | 62.8326 | -59.9213 | 63.0798 | -59.8801 | -59.9716 | -59.816 | -0.082397 | -0.068664 | 0.086975 | 0.22888 | 60.054 | -0.14648 | 60.1364 | -0.064087 | 0.013733 | -0.10529 | 0.14191 | 0.054932 | 0.11902 | -0.036621 | 0.10529 | -0.050354 | 0.31128 | 123.0423 | 0.041199 | 123.0011 | 122.8867 | 122.7539 | 122.8043 | 122.7676 | -122.9553 | -122.8592 | 122.9599 | 123.0148 | 59.8755 | 60.0311
592.8281 | 123.2208 | -59.9487 | 62.9105 | -0.075684 | 0.00048494 | 0.064281 | 0.065523 | 0.00025629 | -0.00056396 | 0.00073273 | -0.042999 | 0.0011664 | 0.065563 | 0.068197 | -0.0046314 | 0.0054516 | -0.0020765 | -0.13733 | 62.8326 | -60.0586 | 62.9471 | -59.8526 | -60.1913 | -0.036621 | -0.09613 | 62.8281 | -59.967 | 63.0478 | -59.9487 | -60.0632 | -59.8572 | -0.10986 | -0.077819 | 0.036622 | 0.09613 | 59.9121 | -0.24262 | 60.022 | -0.13275 | -0.018311 | -0.082397 | 0.13733 | 0 | 0.091552 | -0.11444 | 0.10986 | -0.09613 | 0.20599 | 123.0057 | 0.018311 | 123.0148 | 122.8912 | 122.7951 | 122.7814 | 122.7768 | -122.9691 | -122.8775 | 122.8958 | 122.9965 | 59.8114 | 59.8526
593.8906 | 123.1155 | -59.9625 | 62.9745 | -0.022278 | 0.0011257 | 0.061504 | 0.068513 | -0.0016663 | -0.0012048 | -0.0046079 | -0.024689 | 0.00138 | 0.06364 | 0.064779 | -0.0044178 | 0.003529 | 0.0034777 | -0.068665 | 62.915 | -60.0266 | 62.9196 | -59.8618 | -60.2051 | 0.041199 | -0.073242 | 62.9242 | -59.9533 | 62.9883 | -60.0082 | -60.1089 | -59.9579 | -0.064087 | -0.059509 | -0.054931 | 0.10071 | 60.0037 | -0.24262 | 60.0677 | -0.17853 | 0.009155 | -0.050354 | 0.013733 | -0.045777 | 0.004577 | -0.14648 | -0.004578 | -0.15564 | 0.16479 | 122.9462 | -0.054932 | 122.9416 | 122.9416 | 122.8775 | 122.8775 | 122.8867 | -123.0011 | -122.9279 | 122.8821 | 122.9507 | 59.8938 | 59.8892
594.8281 | 123.111 | -59.9991 | 62.9654 | -0.1062 | 0.0011257 | 0.062572 | 0.067659 | 0.0021789 | -0.002273 | 9.193e-05 | -0.0094299 | 0.0028754 | 0.066845 | 0.059652 | -0.0039906 | 0.0011792 | -0.00058107 | -0.17395 | 62.8784 | -60.1135 | 62.8372 | -60.022 | -60.7178 | -0.12817 | -0.25635 | 62.8967 | -59.9991 | 62.9471 | -60.0815 | -60.1639 | -59.967 | -0.11444 | -0.086975 | -0.12817 | -0.022889 | 59.8709 | -0.71869 | 59.9854 | -0.60425 | 0 | -0.068664 | -0.01831 | -0.082398 | 0.032043 | -0.16479 | 0.032043 | -0.16479 | 0.091552 | 122.9507 | -0.082398 | 122.9462 | 122.9919 | 122.8958 | 122.8775 | 122.8958 | -123.0789 | -122.9645 | 122.8363 | 122.9462 | 59.8251 | 59.7427
595.8281 | 123.1384 | -59.9991 | 62.9242 | -0.029907 | 0.0021939 | 0.063 | 0.066804 | 0.00046989 | -0.00056396 | -0.0014035 | -0.067413 | 0.0039434 | 0.065563 | 0.061575 | -0.0044178 | 0.0037426 | 0.00091433 | -0.14191 | 62.8967 | -60.1044 | 62.883 | -59.9258 | -60.2966 | -0.11902 | -0.1831 | 62.8738 | -59.9808 | 62.9791 | -60.0494 | -60.141 | -59.9396 | -0.10529 | -0.027465 | -0.041198 | 0.073242 | 59.8801 | -0.29755 | 59.9854 | -0.19226 | 0.01831 | -0.050354 | 0.054932 | -0.050354 | 0.059509 | -0.14191 | 0.041199 | -0.16022 | 0.17853 | 122.9874 | -0.068664 | 122.9599 | 123.0011 | 122.8546 | 122.8958 | 122.8729 | -123.0286 | -122.905 | 122.8821 | 122.9782 | 59.8572 | 59.816
596.8906 | 123.1476 | -59.9716 | 62.9608 | -0.11383 | 0.00048494 | 0.065563 | 0.068086 | 0.0038879 | -0.0020594 | 0.0020145 | -0.076569 | 0.0045844 | 0.067913 | 0.066488 | -0.0052722 | 0.0050244 | -0.00079467 | -0.23346 | 62.8784 | -60.1227 | 62.9517 | -59.8526 | -60.1913 | 0 | -0.059509 | 62.9196 | -59.9808 | 63.002 | -59.9899 | -60.1044 | -59.9121 | -0.15106 | -0.082397 | -0.009155 | 0.11902 | 59.9716 | -0.21973 | 60.1227 | -0.068664 | -0.009155 | -0.041198 | 0.041199 | -0.01831 | 0.05951 | -0.13275 | 0.068665 | -0.1236 | 0.27008 | 123.0743 | -0.009155 | 122.9828 | 123.0011 | 122.9004 | 122.85 | 122.8912 | -123.0835 | -122.9416 | 122.9233 | 122.9736 | 59.7382 | 59.9121
597.8281 | 123.2117 | -59.9304 | 62.9059 | -0.083313 | 0.0026211 | 0.064281 | 0.065309 | 0.0019653 | -0.002273 | 0.00030553 | -0.021637 | 0.00138 | 0.064281 | 0.058798 | -0.0012134 | 0.0045972 | 0.0034777 | -0.15106 | 62.8601 | -60.0861 | 62.9288 | -59.8251 | -60.1776 | -0.036621 | -0.10071 | 62.8098 | -59.9899 | 63.0661 | -59.9579 | -60.0586 | -59.8572 | -0.15564 | -0.045777 | 0.022888 | 0.10529 | 59.8938 | -0.24719 | 60.0494 | -0.091552 | -0.059509 | -0.096131 | 0.16022 | -0.027466 | 0.073242 | -0.12817 | 0.13275 | -0.068665 | 0.26093 | 123.0148 | 0.032043 | 123.056 | 122.9462 | 122.7997 | 122.7905 | 122.7402 | -122.9919 | -122.8958 | 122.8592 | 122.9965 | 59.7794 | 59.8297
598.8281 | 123.1247 | -59.9991 | 62.9562 | -0.045166 | 0.0028347 | 0.064922 | 0.066591 | 0.0019653 | -0.002273 | -0.0014035 | -0.049103 | 0.0018072 | 0.06599 | 0.067556 | -0.0050586 | 0.0039562 | 0.00027333 | -0.11902 | 62.8876 | -60.0677 | 62.9059 | -59.8892 | -60.2463 | -0.059509 | -0.1236 | 62.8922 | -59.9762 | 62.9791 | -60.0357 | -60.1685 | -59.9579 | -0.068665 | -0.068665 | -0.050354 | 0.10986 | 59.9396 | -0.24719 | 60.0082 | -0.17853 | 0.022888 | -0.064087 | 0.022888 | -0.036622 | 0.041198 | -0.16937 | 0.01831 | -0.19226 | 0.17853 | 122.9736 | -0.05951 | 122.9553 | 122.9553 | 122.8683 | 122.8867 | 122.8912 | -123.024 | -122.9324 | 122.905 | 122.9782 | 59.8801 | 59.8755
599.8906 | 123.1247 | -59.9442 | 62.9517 | -0.045166 | 0.00027134 | 0.063 | 0.067232 | 0.0036743 | 0.002213 | -0.0011899 | -0.046051 | -0.0001154 | 0.066204 | 0.064993 | -0.0054858 | 0.0060924 | -0.00058107 | -0.068665 | 62.8922 | -60.0723 | 62.9333 | -59.8297 | -60.1822 | 0.022888 | -0.032043 | 62.8876 | -60.0037 | 63.0112 | -59.9854 | -60.0861 | -59.9213 | -0.12817 | -0.059509 | -0.01831 | 0.11444 | 59.967 | -0.23804 | 60.0952 | -0.10986 | -0.059509 | -0.064087 | 0.059509 | -0.041199 | 0.022888 | -0.14191 | 0.082397 | -0.082398 | 0.24262 | 123.0057 | 0.01831 | 123.0148 | 122.9645 | 122.8912 | 122.8363 | 122.8317 | -123.024 | -122.9553 | 122.8775 | 122.9553 | 59.8755 | 59.9121
600.8281 | 123.024 | -60.0311 | 62.8784 | -0.11383 | 0.0019803 | 0.064709 | 0.066804 | -0.00017091 | -0.0014184 | -0.0022581 | -0.046051 | 0.0028754 | 0.064495 | 0.064352 | -0.0042042 | 0.0048108 | 0.00070073 | -0.16937 | 62.8784 | -60.0815 | 62.8235 | -59.9625 | -60.3149 | -0.11444 | -0.23804 | 62.8693 | -60.0174 | 62.9517 | -60.0769 | -60.1776 | -59.7702 | -0.050354 | 0 | -0.054932 | 0.068665 | 59.9167 | -0.28381 | 59.967 | -0.23346 | 0.013733 | -0.009155 | 0.073242 | -0.045776 | 0.26093 | -0.14648 | 0.24719 | -0.16022 | 0.11902 | 122.905 | -0.059509 | 122.9691 | 122.9599 | 122.8867 | 122.9095 | 122.9004 | -122.9599 | -122.8958 | 122.8546 | 122.9828 | 59.8618 | 59.7931
601.8906 | 123.1522 | -59.9533 | 63.0112 | -0.007019 | -0.00036966 | 0.062359 | 0.064882 | -0.0020935 | -0.0016322 | -0.00033547 | -0.021637 | 0.0015936 | 0.066631 | 0.060507 | -0.0039906 | 0.0033154 | -0.0018629 | -0.07782 | 62.9059 | -60.0357 | 62.8967 | -59.8892 | -60.2005 | 0.027466 | -0.07782 | 62.9105 | -59.967 | 63.002 | -59.9854 | -60.0861 | -59.9121 | -0.082398 | -0.10529 | -0.11444 | 0.064087 | 59.9808 | -0.24719 | 60.0632 | -0.16479 | -0.013733 | -0.10071 | -0.009155 | -0.032044 | 0.041199 | -0.13275 | 0.054932 | -0.11902 | 0.14648 | 122.9324 | -0.018311 | 122.9691 | 122.9416 | 122.8775 | 122.8592 | 122.8638 | -123.0469 | -122.9782 | 122.85 | 122.9553 | 59.8755 | 59.8755
602.8281 | 123.1155 | -59.9854 | 62.9791 | -0.083313 | 0.00091214 | 0.061504 | 0.067659 | -0.00081171 | -0.00035036 | -0.0014035 | -0.033844 | 0.0020208 | 0.068981 | 0.062002 | -0.004845 | 0.0050244 | -0.0014355 | -0.068665 | 62.8738 | -60.0632 | 62.9425 | -59.8434 | -60.1868 | -0.009155 | -0.082397 | 62.883 | -59.9945 | 63.0066 | -60.0174 | -60.1318 | -59.9396 | -0.077819 | -0.10529 | -0.036621 | 0.14191 | 59.9762 | -0.20142 | 60.054 | -0.1236 | -0.009155 | -0.09613 | 0.027466 | -0.032043 | 0.045777 | -0.14648 | 0.054932 | -0.13733 | 0.21973 | 123.0057 | -0.022888 | 123.0011 | 122.937 | 122.8775 | 122.8592 | 122.8683 | -123.0423 | -122.9736 | 122.9279 | 122.9919 | 59.9167 | 59.903
603.8906 | 123.2391 | -59.9258 | 62.9425 | -0.052796 | 0.00069854 | 0.064281 | 0.066163 | -0.0031617 | -0.0020594 | -0.0014035 | 0.036346 | 0.0018072 | 0.065563 | 0.054098 | -0.0035632 | 0.0037426 | -0.00058107 | -0.059509 | 62.883 | -60.0266 | 62.9837 | -59.7427 | -60.1044 | 0.082397 | 0.036621 | 62.8738 | -59.9533 | 63.0936 | -59.8618 | -59.9716 | -59.8206 | -0.10071 | -0.059509 | 0.041199 | 0.18311 | 60.0082 | -0.17853 | 60.1089 | -0.07782 | -0.027466 | -0.068665 | 0.15106 | 0.064087 | 0.10529 | -0.045777 | 0.13275 | -0.018311 | 0.28381 | 123.0103 | 0.091553 | 123.0469 | 122.9095 | 122.8271 | 122.8088 | 122.7997 | -122.9691 | -122.8958 | 122.9095 | 123.0194 | 59.8663 | 59.9625
604.8281 | 123.0835 | -59.9899 | 62.97 | -0.075684 | 0.00048494 | 0.062572 | 0.066377 | 0.0026063 | 0.00029044 | -0.0016171 | -0.067413 | 0.0015936 | 0.067058 | 0.061575 | -0.0056994 | 0.0039562 | -0.0016493 | -0.13275 | 62.8876 | -60.1089 | 62.8784 | -59.9121 | -60.2646 | -0.086975 | -0.16479 | 62.8967 | -59.9945 | 62.9471 | -60.0861 | -60.1776 | -59.9899 | -0.11902 | -0.082398 | -0.091553 | 0.07782 | 59.903 | -0.27466 | 60.022 | -0.15564 | -0.004578 | -0.073242 | -0.022888 | -0.096131 | 0 | -0.18768 | 0.004578 | -0.18311 | 0.19684 | 122.9874 | -0.091553 | 122.9416 | 122.9965 | 122.8912 | 122.8775 | 122.8867 | -123.0789 | -122.9645 | 122.8683 | 122.937 | 59.8572 | 59.8251
605.8906 | 123.143 | -59.9213 | 62.9608 | -0.075684 | 0.0017667 | 0.064495 | 0.066163 | -0.0016663 | -0.0027002 | 9.193e-05 | 0.030243 | 0.0007392 | 0.063427 | 0.055593 | -0.0046314 | 0.0039562 | -0.0012219 | -0.027466 | 62.8876 | -60.022 | 62.9929 | -59.7519 | -60.1089 | 0.10529 | 0.022888 | 62.8601 | -59.9487 | 63.0478 | -59.9258 | -60.0449 | -59.8709 | -0.10071 | -0.073242 | 0.032044 | 0.16937 | 60.0266 | -0.18768 | 60.1273 | -0.086975 | -0.027465 | -0.10071 | 0.086976 | -0.004577 | 0.050354 | -0.1236 | 0.077819 | -0.096131 | 0.27008 | 123.0148 | 0.022888 | 122.9965 | 122.9095 | 122.8088 | 122.8088 | 122.7814 | -122.9828 | -122.9095 | 122.9141 | 122.9691 | 59.8938 | 59.9442
606.8281 | 123.0789 | -59.9808 | 62.9654 | -0.083313 | 0.0026211 | 0.064068 | 0.068727 | -0.0018799 | -0.00099116 | -0.00012167 | -0.033844 | 0.00138 | 0.064068 | 0.063711 | -0.0039906 | 0.0031018 | 0.0015551 | -0.11902 | 62.8922 | -60.1135 | 62.8647 | -59.9167 | -60.2737 | -0.091553 | -0.21057 | 62.883 | -60.0082 | 62.9333 | -60.0769 | -60.1913 | -59.9899 | -0.13275 | -0.073242 | -0.10071 | 0.064087 | 59.8892 | -0.29297 | 60.022 | -0.16022 | -0.027466 | -0.082397 | -0.032043 | -0.09613 | -0.009155 | -0.21057 | 0.018311 | -0.1831 | 0.19684 | 122.9782 | -0.068664 | 122.9416 | 123.0057 | 122.8912 | 122.8729 | 122.8638 | -123.0789 | -122.9736 | 122.8455 | 122.9141 | 59.8618 | 59.7702
607.8906 | 123.1155 | -59.9579 | 62.9929 | -0.045166 | 0.00048494 | 0.064495 | 0.066163 | 0.0011109 | -0.0018458 | -0.0011899 | 0.030243 | 0.0020208 | 0.065563 | 0.065634 | -0.004845 | 0.0028882 | 0.0017687 | -0.07782 | 62.9333 | -60.0586 | 62.9105 | -59.8709 | -60.1959 | 0.032043 | -0.082397 | 62.8922 | -59.9625 | 62.9608 | -60.0128 | -60.1181 | -59.9487 | -0.10071 | -0.059509 | -0.082398 | 0.086975 | 59.9899 | -0.23804 | 60.0906 | -0.13733 | -0.004577 | -0.10071 | -0.032044 | -0.054931 | 0.009156 | -0.16022 | 0.013733 | -0.15564 | 0.18768 | 122.9691 | -0.050354 | 122.9233 | 122.9919 | 122.8546 | 122.8912 | 122.85 | -123.0515 | -122.9553 | 122.8683 | 122.9187 | 59.8801 | 59.8755
608.8281 | 123.1567 | -59.935 | 62.9791 | -0.075684 | 0.0015529 | 0.062786 | 0.069154 | 0.0011109 | -0.0020594 | -0.0011899 | -0.070465 | 0.0018072 | 0.065136 | 0.066061 | -0.0018542 | 0.0045972 | -0.0012219 | -0.082397 | 62.8876 | -60.0815 | 62.9242 | -59.8206 | -60.2051 | 0.013733 | -0.15564 | 62.8738 | -59.9762 | 63.002 | -59.9762 | -60.0906 | -59.9258 | -0.14648 | -0.091553 | -0.054932 | 0.11444 | 59.9487 | -0.27008 | 60.0952 | -0.1236 | -0.041198 | -0.10529 | 0.022888 | -0.041198 | 0.009156 | -0.15564 | 0.050354 | -0.11444 | 0.26093 | 123.0057 | 0 | 122.9782 | 122.9691 | 122.85 | 122.8226 | 122.8088 | -123.0606 | -122.9553 | 122.8592 | 122.937 | 59.8526 | 59.7794
609.8906 | 123.111 | -59.9533 | 62.9974 | -0.060425 | 0.0017667 | 0.06065 | 0.067872 | 0.0017517 | -0.0016322 | -0.0016171 | -0.0002747 | 0.0024482 | 0.06599 | 0.06072 | -0.0054858 | 0.0054516 | -0.0018629 | -0.1236 | 62.9196 | -60.1044 | 62.8784 | -59.8892 | -60.1913 | 0.018311 | -0.082397 | 62.915 | -59.9762 | 62.9883 | -60.0128 | -60.1135 | -59.9167 | -0.15106 | -0.07782 | -0.11902 | 0.064087 | 59.9716 | -0.23804 | 60.1227 | -0.086975 | -0.022888 | -0.082398 | -0.009156 | -0.059509 | 0.036621 | -0.16022 | 0.059509 | -0.13733 | 0.21515 | 122.9828 | -0.036621 | 122.9645 | 123.024 | 122.8912 | 122.8729 | 122.8683 | -123.1018 | -122.9736 | 122.8317 | 122.9416 | 59.8297 | 59.8709
610.8281 | 123.1338 | -59.9396 | 62.9974 | -0.060425 | -0.00036966 | 0.062572 | 0.066591 | 0.0021789 | 0.00029044 | -0.0011899 | -0.024689 | 0.0022346 | 0.066631 | 0.060293 | -0.0042042 | 0.0050244 | -0.0018629 | -0.059509 | 62.9013 | -60.0632 | 62.9471 | -59.8297 | -60.1776 | 0.054932 | -0.018311 | 62.9105 | -59.9579 | 63.0203 | -59.9762 | -60.0906 | -59.8892 | -0.1236 | -0.096131 | -0.050354 | 0.10986 | 59.9945 | -0.23804 | 60.1181 | -0.11444 | -0.018311 | -0.086976 | 0.022888 | -0.036621 | 0.050354 | -0.15106 | 0.068665 | -0.13275 | 0.23346 | 123.0103 | -0.01831 | 122.9782 | 122.9645 | 122.8683 | 122.8409 | 122.85 | -123.0606 | -122.9553 | 122.8867 | 122.9599 | 59.8801 | 59.9213
611.8906 | 123.2437 | -59.9121 | 62.9929 | -0.1062 | 0.0017667 | 0.064495 | 0.06595 | -0.0031617 | -0.0018458 | 0.00051913 | 0.039398 | 0.0020208 | 0.066204 | 0.059652 | -0.0039906 | 0.0039562 | -0.0042127 | -0.041199 | 62.8555 | -60.0174 | 63.0203 | -59.6832 | -60.054 | 0.14648 | 0.041199 | 62.8738 | -59.9396 | 63.0753 | -59.8663 | -59.967 | -59.8343 | -0.10529 | -0.13733 | 0.027466 | 0.22888 | 60.0586 | -0.14191 | 60.1639 | -0.036621 | -0.027466 | -0.11902 | 0.082397 | 0.045776 | 0.077819 | -0.054932 | 0.10528 | -0.027466 | 0.33417 | 123.0377 | 0.073242 | 123.0148 | 122.8729 | 122.8134 | 122.7676 | 122.7859 | -123.0103 | -122.9324 | 122.9324 | 122.9874 | 59.8709 | 59.9533
612.8281 | 123.1247 | -59.9442 | 62.9745 | -0.014649 | 0.0015529 | 0.062786 | 0.066804 | 0.0026063 | -0.0018458 | 0.00030553 | -0.027741 | 0.0028754 | 0.065563 | 0.058798 | -0.0046314 | 0.0039562 | 0.0030505 | -0.082397 | 62.9333 | -60.054 | 62.9105 | -59.8801 | -60.2142 | 0.013733 | -0.073242 | 62.8967 | -59.967 | 62.9883 | -59.9854 | -60.0952 | -59.9258 | -0.10986 | -0.041198 | -0.064087 | 0.064087 | 59.9579 | -0.27008 | 60.0677 | -0.16022 | -0.022888 | -0.077819 | 0.013733 | -0.041199 | 0.018311 | -0.15106 | 0.041199 | -0.12817 | 0.17395 | 122.9645 | -0.018311 | 122.9553 | 122.9874 | 122.8638 | 122.8775 | 122.8409 | -123.0286 | -122.9416 | 122.8546 | 122.9324 | 59.8618 | 59.8709
613.8906 | 123.3215 | -59.8938 | 63.0066 | -0.045166 | 0.0019803 | 0.061932 | 0.066804 | -0.0010253 | -0.00099116 | -0.0026853 | 0.036346 | 0.0005256 | 0.065349 | 0.060934 | -0.002068 | 0.003529 | -0.0018629 | -0.036621 | 62.8876 | -60.022 | 63.0478 | -59.7061 | -60.0632 | 0.12817 | 0.068665 | 62.8647 | -59.9258 | 63.1027 | -59.8892 | -59.9716 | -59.8526 | -0.12817 | -0.11902 | 0.041199 | 0.18768 | 60.022 | -0.16937 | 60.1501 | -0.041198 | -0.032043 | -0.14191 | 0.09613 | 0.004578 | 0.041199 | -0.07782 | 0.073242 | -0.045777 | 0.31586 | 123.0698 | 0.036621 | 123.0286 | 122.9095 | 122.7905 | 122.7814 | 122.7585 | -123.0286 | -122.9324 | 122.9416 | 122.9965 | 59.8572 | 59.9625
614.8281 | 123.1522 | -59.9533 | 62.97 | -0.060425 | 0.0013393 | 0.062572 | 0.068086 | 0.00089729 | -0.0018458 | -0.0024717 | -0.042999 | 0.0024482 | 0.066204 | 0.069052 | -0.004845 | 0.0033154 | 0.0011279 | -0.064087 | 62.8693 | -60.0769 | 62.97 | -59.8251 | -60.2005 | 0.032043 | -0.036621 | 62.9013 | -59.9716 | 63.0112 | -59.9991 | -60.0906 | -59.8984 | -0.1236 | -0.10071 | 0 | 0.12817 | 59.9854 | -0.24719 | 60.1089 | -0.1236 | -0.018311 | -0.068665 | 0.041198 | -0.045776 | 0.054932 | -0.13733 | 0.073243 | -0.11902 | 0.25177 | 123.0469 | -0.027465 | 122.9828 | 122.9462 | 122.8729 | 122.8226 | 122.8546 | -123.0469 | -122.9416 | 122.9233 | 122.9645 | 59.8892 | 59.9167
615.8906 | 123.2071 | -59.9304 | 62.9379 | -0.12146 | 0.0032619 | 0.063 | 0.06595 | 0.0021789 | -0.0029138 | -0.0011899 | -0.033844 | 0.0009528 | 0.064068 | 0.065206 | -0.0029224 | 0.0039562 | -0.0035719 | -0.11444 | 62.8372 | -60.0723 | 63.0295 | -60.0769 | -60.1776 | 0.16022 | -0.045776 | 62.8235 | -59.967 | 63.0432 | -59.9396 | -60.0586 | -59.8618 | -0.14191 | -0.10071 | 0.091553 | -0.14648 | 60.0906 | -0.24719 | 60.2325 | -0.10529 | -0.036621 | -0.11444 | 0.10529 | -0.009155 | 0.068665 | -0.12817 | 0.10529 | -0.091553 | -0.004577 | 123.1018 | 0.027466 | 123.0103 | 122.9095 | 122.7905 | 122.7676 | 122.7539 | -123.0103 | -122.905 | 122.9599 | 122.9736 | 59.816 | 59.8846
616.8281 | 123.1155 | -59.9533 | 62.9883 | -0.083313 | 0.0024075 | 0.061504 | 0.066377 | -0.0033753 | -0.00099116 | 0.0013735 | -0.027741 | 0.0015936 | 0.067272 | 0.064779 | -0.0039906 | 0.0024608 | -0.0016493 | -0.054932 | 62.9013 | -60.0449 | 62.9379 | -59.8297 | -60.1685 | 0.059509 | -0.050354 | 62.9196 | -59.9579 | 62.97 | -60.0128 | -60.0906 | -59.9533 | -0.091553 | -0.086975 | -0.050354 | 0.1236 | 60.0128 | -0.21515 | 60.1044 | -0.1236 | -0.004578 | -0.068664 | -0.01831 | -0.059509 | 0 | -0.13733 | 0.004578 | -0.13275 | 0.21515 | 122.9828 | -0.054931 | 122.9279 | 122.9462 | 122.8775 | 122.8546 | 122.8729 | -123.0331 | -122.9462 | 122.8912 | 122.9233 | 59.8984 | 59.903
617.8906 | 123.2117 | -59.9396 | 62.9333 | -0.083313 | 0.0017667 | 0.061077 | 0.066591 | 0.00025629 | -0.0012048 | -0.00097627 | 0.033295 | -0.000329 | 0.065563 | 0.058584 | -0.0027088 | 0.0022472 | 0.0030505 | -0.10071 | 62.8784 | -60.0357 | 62.9654 | -59.7885 | -60.141 | 0.068665 | -0.013733 | 62.8555 | -59.9625 | 63.0798 | -59.8984 | -59.9899 | -59.8389 | -0.096131 | -0.054932 | 0.032043 | 0.15106 | 60.0082 | -0.20142 | 60.1044 | -0.10529 | -0.022888 | -0.07782 | 0.14648 | 0.041199 | 0.10071 | -0.050354 | 0.1236 | -0.027466 | 0.24719 | 123.0011 | 0.064087 | 123.0423 | 122.9141 | 122.818 | 122.818 | 122.7951 | -122.9691 | -122.8958 | 122.905 | 123.0194 | 59.8389 | 59.9258
618.8281 | 123.1018 | -59.9533 | 63.0112 | -0.029907 | 0.00091214 | 0.061932 | 0.067659 | -0.0035889 | -0.0024866 | 0.00073273 | -0.021637 | 0.0024482 | 0.066204 | 0.06542 | -0.0056994 | 0.0031018 | -0.0018629 | -0.10529 | 62.9288 | -60.0677 | 62.9013 | -59.8892 | -60.2234 | 0.032043 | -0.14191 | 62.9242 | -59.9213 | 62.9471 | -60.0494 | -60.0632 | -59.9167 | -0.11444 | -0.082397 | -0.10986 | 0.064087 | 59.9854 | -0.27008 | 60.0998 | -0.15564 | 0.032043 | -0.086975 | -0.064086 | -0.09613 | 0.036621 | -0.10986 | 0.004578 | -0.14191 | 0.17853 | 122.9691 | -0.12817 | 122.8683 | 122.9965 | 122.8455 | 122.8821 | 122.8775 | -123.0789 | -122.9324 | 122.8546 | 122.9004 | 59.848 | 59.8114
619.8906 | 123.2117 | -59.9442 | 62.9288 | -0.11383 | 0.0030483 | 0.065136 | 0.064454 | 0.00025629 | 0.00093144 | -0.0011899 | -0.049103 | 0.0011664 | 0.064922 | 0.066702 | -0.0033496 | 0.003529 | 0.00027333 | -0.1236 | 62.8143 | -60.0815 | 62.9791 | -59.7977 | -60.173 | -0.027466 | -0.10529 | 62.7869 | -59.9945 | 63.0524 | -59.9121 | -60.0266 | -59.8526 | -0.13733 | -0.11444 | 0.050354 | 0.14648 | 59.9167 | -0.22888 | 60.054 | -0.091553 | -0.050354 | -0.14191 | 0.1236 | 0.032044 | 0.091553 | -0.082397 | 0.14191 | -0.032043 | 0.28381 | 123.0606 | 0.082398 | 123.0469 | 122.8958 | 122.7814 | 122.7585 | 122.731 | -123.0103 | -122.9233 | 122.9233 | 122.9965 | 59.8206 | 59.8389
620.8281 | 123.1293 | -59.9625 | 62.9929 | -0.037537 | 0.00091214 | 0.061077 | 0.066163 | 0.0013245 | -0.00099116 | -0.0022581 | -0.015534 | 0.0026618 | 0.066204 | 0.064352 | -0.0050586 | 0.0024608 | -0.0029309 | -0.045776 | 62.8922 | -60.0449 | 62.97 | -59.8114 | -60.1501 | 0.082397 | -0.032043 | 62.9013 | -59.9762 | 62.9745 | -59.9945 | -60.0998 | -59.9304 | -0.082398 | -0.10071 | -0.022888 | 0.15106 | 60.0449 | -0.18768 | 60.1273 | -0.10529 | -0.013733 | -0.091553 | -0.018311 | -0.032044 | 0.032043 | -0.13733 | 0.045776 | -0.1236 | 0.23346 | 123.0148 | -0.018311 | 122.9507 | 122.937 | 122.8775 | 122.8546 | 122.8638 | -123.0377 | -122.9691 | 122.9324 | 122.937 | 59.9167 | 59.9304
621.8906 | 123.2117 | -59.9304 | 62.9059 | -0.075684 | 0.00069854 | 0.063213 | 0.066163 | -0.00038451 | -0.00077756 | -0.00097627 | -0.015534 | 0.0024482 | 0.064495 | 0.06307 | -0.0046314 | 0.0022472 | -0.0025037 | -0.11902 | 62.8281 | -60.0952 | 62.9745 | -59.8068 | -60.1639 | -0.018311 | 0.022888 | 62.8326 | -60.0082 | 63.0661 | -59.9121 | -60.1089 | -59.8892 | -0.1648 | -0.07782 | 0.068664 | 0.1236 | 59.9121 | -0.23346 | 60.0769 | -0.068664 | -0.07782 | -0.073242 | 0.16022 | 0.018311 | 0.041199 | -0.17853 | 0.11902 | -0.10071 | 0.28839 | 123.0698 | 0.096131 | 123.0743 | 122.9233 | 122.8409 | 122.7585 | 122.7631 | -123.0011 | -122.9141 | 122.905 | 122.9965 | 59.8114 | 59.9533
622.8281 | 123.2208 | -59.9258 | 62.9425 | -0.090943 | -0.0010105 | 0.060863 | 0.06595 | -0.00017091 | -0.00056396 | -0.0020443 | 0.027191 | 0.0003118 | 0.064495 | 0.062856 | -0.0046314 | 0.0020336 | 0.00027333 | -0.054932 | 62.8647 | -60.0403 | 63.0341 | -59.7153 | -60.0723 | 0.10986 | 0.054932 | 62.8693 | -59.935 | 63.0844 | -59.8801 | -59.9716 | -59.8343 | -0.11444 | -0.07782 | 0.091553 | 0.21057 | 60.0357 | -0.14648 | 60.1501 | -0.032044 | -0.009156 | -0.073242 | 0.14191 | 0.045776 | 0.091552 | -0.045777 | 0.10071 | -0.036621 | 0.32501 | 123.0743 | 0.054932 | 123.0194 | 122.905 | 122.8043 | 122.7905 | 122.7951 | -122.9828 | -122.8775 | 122.9599 | 123.0103 | 59.8709 | 59.9808
623.8906 | 123.143 | -59.9854 | 62.9471 | -0.037537 | -0.00036966 | 0.063854 | 0.067232 | -0.00017091 | -0.0029138 | -0.0031125 | -0.07962 | 0.0018072 | 0.066204 | 0.064779 | -0.0059132 | 0.0054516 | -0.0042127 | -0.21973 | 62.8876 | -60.0861 | 62.8693 | -59.9167 | -60.2829 | -0.10986 | -0.19226 | 62.8876 | -59.9716 | 62.9837 | -60.0403 | -60.1639 | -59.9396 | -0.10071 | -0.05951 | -0.07782 | 0.068665 | 59.8755 | -0.29755 | 59.9762 | -0.19684 | 0.013733 | -0.05951 | 0.036621 | -0.054931 | 0.045777 | -0.17853 | 0.032044 | -0.19226 | 0.16937 | 122.9553 | -0.068664 | 122.9553 | 122.9736 | 122.8592 | 122.8729 | 122.8729 | -123.0331 | -122.9187 | 122.8546 | 122.9691 | 59.7656 | 59.7931
624.8281 | 123.2162 | -59.9304 | 62.9562 | -0.090943 | 0.0015529 | 0.061718 | 0.064882 | 0.00068369 | 0.00029044 | -0.0014035 | 0.0027771 | 0.0011664 | 0.064709 | 0.060293 | -0.0054858 | 0.00182 | -0.0012219 | -0.041199 | 62.8876 | -60.0266 | 63.0386 | -59.7061 | -60.0632 | 0.13275 | 0.050354 | 62.8876 | -59.9533 | 63.1027 | -59.8755 | -59.9625 | -59.8206 | -0.09613 | -0.068665 | 0.082397 | 0.2243 | 60.0632 | -0.13275 | 60.1593 | -0.036621 | -0.022888 | -0.068665 | 0.14648 | 0.054932 | 0.10986 | -0.032043 | 0.13275 | -0.009155 | 0.32043 | 123.0652 | 0.07782 | 123.056 | 122.9141 | 122.8409 | 122.818 | 122.818 | -122.9828 | -122.9095 | 122.9691 | 123.0331 | 59.8892 | 59.9808
625.8906 | 123.143 | -59.9625 | 62.9745 | -0.045166 | 0.00048494 | 0.063427 | 0.067232 | 0.0017517 | 7.6842e-05 | -0.0018307 | -0.058258 | 0.0009528 | 0.065777 | 0.064352 | -0.0046314 | 0.0028882 | 0.00027333 | -0.073242 | 62.8784 | -60.0906 | 62.9562 | -59.816 | -60.2005 | 0.022888 | -0.041199 | 62.9105 | -59.967 | 63.0203 | -59.967 | -60.0952 | -59.903 | -0.12817 | -0.09613 | -0.01831 | 0.14648 | 59.9854 | -0.23804 | 60.1135 | -0.10986 | -0.004578 | -0.064087 | 0.045777 | -0.004578 | 0.059509 | -0.13275 | 0.064087 | -0.12817 | 0.27466 | 123.0469 | 0 | 122.9874 | 122.9691 | 122.8775 | 122.8409 | 122.8729 | -123.0652 | -122.9416 | 122.9187 | 122.9828 | 59.8892 | 59.9213
626.8281 | 123.1934 | -59.9304 | 62.9517 | -0.052796 | 0.0021939 | 0.060863 | 0.064668 | 0.0051697 | -0.00077756 | 0.00073273 | -0.0002747 | 0.0028754 | 0.065349 | 0.061575 | -0.0027088 | 0.0041698 | 0.0017687 | 0.20142 | 62.9242 | -59.9945 | 63.0432 | -59.7382 | -60.1364 | 0.11902 | 0 | 62.8784 | -59.9625 | 63.0661 | -59.8938 | -60.0082 | -59.848 | -0.064087 | -0.027466 | 0.091553 | 0.19226 | 60.0494 | -0.20599 | 60.1135 | -0.14191 | -0.032043 | -0.073242 | 0.11444 | 0.036621 | 0.082398 | -0.07782 | 0.11444 | -0.045777 | 0.25635 | 123.0377 | 0.068664 | 123.0286 | 122.9187 | 122.8409 | 122.8546 | 122.8088 | -122.9462 | -122.9141 | 122.9736 | 122.9965 | 60.1318 | 59.9304
627.8906 | 123.0835 | -59.9854 | 62.9929 | -0.12909 | -0.00036966 | 0.063427 | 0.067445 | 0.0045289 | -0.0016322 | 0.00073273 | -0.067413 | 9.8198e-05 | 0.064922 | 0.063711 | -0.0050586 | 0.0067334 | -0.0016493 | -0.13275 | 62.8647 | -60.0861 | 62.9013 | -59.8892 | -60.26 | -0.059509 | -0.16937 | 62.9105 | -59.9991 | 62.9517 | -60.0449 | -60.1685 | -59.9487 | -0.10071 | -0.12817 | -0.091553 | 0.096131 | 59.9258 | -0.27466 | 60.0266 | -0.17395 | -0.013732 | -0.082398 | -0.041199 | -0.059509 | 0.036622 | -0.1831 | 0.050354 | -0.16937 | 0.19684 | 122.9874 | -0.045777 | 122.9507 | 122.9507 | 122.9095 | 122.85 | 122.8958 | -123.0789 | -122.9919 | 122.8867 | 122.937 | 59.8526 | 59.816
628.8281 | 123.2529 | -59.9167 | 62.9471 | -0.068054 | -0.00015586 | 0.063 | 0.065095 | -0.0012391 | 0.00050424 | 0.0018009 | 0.030243 | 0.00138 | 0.066418 | 0.064993 | -0.0027088 | 0.0016064 | -0.0016493 | -0.11902 | 62.8784 | -60.0586 | 62.9608 | -59.7748 | -60.141 | 0.050354 | -0.045776 | 62.8647 | -59.9533 | 63.0615 | -59.8984 | -60.0082 | -59.8297 | -0.14191 | -0.068665 | 0.013732 | 0.14191 | 59.967 | -0.2243 | 60.1089 | -0.082397 | -0.036621 | -0.082398 | 0.11444 | 0.018311 | 0.086975 | -0.091553 | 0.1236 | -0.054932 | 0.28381 | 123.0194 | 0.054932 | 123.0148 | 122.937 | 122.818 | 122.7951 | 122.7814 | -123.0057 | -122.9004 | 122.8775 | 122.9782 | 59.7977 | 59.8709
629.8281 | 123.1979 | -59.9487 | 62.9105 | -0.15198 | -0.00036966 | 0.063427 | 0.064668 | -0.0020935 | -0.00035036 | -0.0026853 | 0.0027771 | 0.0007392 | 0.066631 | 0.064779 | -0.0042042 | 0.0031018 | 5.9726e-05 | -0.13275 | 62.851 | -60.0723 | 62.9471 | -59.8343 | -60.1822 | 0.009155 | -0.07782 | 62.8738 | -59.9716 | 63.0524 | -59.935 | -60.0266 | -59.8434 | -0.1236 | -0.059509 | 0.036622 | 0.11444 | 59.9579 | -0.23346 | 60.0815 | -0.10986 | -0.022889 | -0.036621 | 0.14191 | 0.013732 | 0.10528 | -0.07782 | 0.12817 | -0.054931 | 0.23804 | 123.0194 | 0.036621 | 123.024 | 122.9233 | 122.8455 | 122.7997 | 122.8226 | -122.9828 | -122.8821 | 122.8958 | 123.0011 | 59.816 | 59.8709
630.8906 | 123.111 | -59.9899 | 62.97 | -0.075684 | 0.0024075 | 0.062145 | 0.067445 | 0.0043151 | 0.00050424 | -0.0016171 | -0.097931 | 0.00138 | 0.065563 | 0.066488 | -0.0056994 | 0.0037426 | 0.0019823 | -0.15106 | 62.883 | -60.1089 | 62.8876 | -59.9075 | -60.3012 | -0.07782 | -0.19684 | 62.9059 | -60.0037 | 62.9288 | -60.0769 | -60.1913 | -59.9762 | -0.11902 | -0.086975 | -0.082398 | 0.082397 | 59.9121 | -0.31128 | 60.0311 | -0.19226 | -0.013733 | -0.064087 | -0.041199 | -0.086975 | 0.013733 | -0.20142 | 0.027466 | -0.18768 | 0.20142 | 122.9965 | -0.073242 | 122.9324 | 122.9919 | 122.9095 | 122.8729 | 122.8958 | -123.0789 | -122.9736 | 122.8775 | 122.9187 | 59.8389 | 59.7931
631.8281 | 123.3032 | -59.9121 | 63.0157 | -0.060425 | 0.00091214 | 0.063854 | 0.064668 | -0.0018799 | -0.0016322 | -0.0022581 | 0.018036 | 0.0024482 | 0.067486 | 0.059652 | -0.0044178 | 0.0031018 | -0.0020765 | -0.059509 | 62.8647 | -60.0174 | 63.0432 | -59.7061 | -60.0815 | 0.12817 | 0.036621 | 62.8922 | -59.9487 | 63.0798 | -59.8892 | -59.9625 | -59.9762 | -0.10529 | -0.15106 | 0.027466 | 0.20599 | 60.0403 | -0.16937 | 60.1456 | -0.064087 | -0.036621 | -0.1236 | 0.064087 | 0.022888 | -0.064087 | -0.050354 | -0.027466 | -0.013733 | 0.31128 | 123.0606 | 0.059509 | 123.0286 | 122.8821 | 122.8409 | 122.7768 | 122.8043 | -123.0331 | -122.9645 | 122.9553 | 122.9919 | 59.8526 | 59.9487
632.8906 | 123.1338 | -59.9396 | 62.9608 | -0.052796 | 0.0019803 | 0.063854 | 0.066377 | 0.00046989 | -0.00056396 | 9.193e-05 | -0.082672 | 0.0020208 | 0.064922 | 0.062216 | -0.0044178 | 0.005238 | -0.0027173 | -0.07782 | 62.9105 | -60.0723 | 62.9517 | -59.8389 | -60.1959 | 0.027466 | -0.064087 | 62.9196 | -59.9762 | 63.0203 | -59.9625 | -60.0998 | -59.8984 | -0.13275 | -0.050354 | -0.009155 | 0.10071 | 59.967 | -0.25635 | 60.0998 | -0.1236 | -0.036621 | -0.041198 | 0.05951 | -0.022888 | 0.041199 | -0.16022 | 0.07782 | -0.1236 | 0.23346 | 123.024 | 0.013733 | 122.9965 | 122.9828 | 122.8958 | 122.85 | 122.8592 | -123.0331 | -122.937 | 122.8912 | 122.9599 | 59.8618 | 59.8755
633.8281 | 123.2025 | -59.9533 | 62.9425 | -0.098572 | 0.00069854 | 0.061291 | 0.067872 | -0.0010253 | -0.00077756 | -0.0011899 | 0.018036 | 0.00138 | 0.066418 | 0.064565 | -0.0033496 | 0.0031018 | 0.00070073 | -0.17395 | 62.8784 | -60.0311 | 62.9288 | -59.816 | -60.173 | 0.009155 | -0.09613 | 62.8281 | -59.9716 | 63.0432 | -59.9533 | -60.0403 | -59.8846 | -0.07782 | -0.064087 | -0.013733 | 0.13733 | 59.9625 | -0.21973 | 60.0403 | -0.14191 | -0.018311 | -0.11444 | 0.10071 | 0 | 0.068664 | -0.086975 | 0.086975 | -0.068664 | 0.21515 | 122.9599 | 0.018311 | 123.0148 | 122.9095 | 122.7997 | 122.8317 | 122.7814 | -122.9736 | -122.9141 | 122.8821 | 122.9965 | 59.7794 | 59.8572
634.8906 | 123.143 | -59.9716 | 62.9425 | -0.12146 | -0.00015586 | 0.063 | 0.06595 | 0.00089729 | -0.00056396 | -0.0014035 | -0.064362 | 0.0018072 | 0.064922 | 0.068838 | -0.003136 | 0.0043836 | 0.0013415 | -0.16022 | 62.915 | -60.1044 | 62.8738 | -59.935 | -60.2921 | -0.10071 | -0.2243 | 62.8738 | -60.0082 | 62.9883 | -60.0357 | -60.1547 | -59.9396 | -0.13275 | -0.027466 | -0.068665 | 0.036621 | 59.8709 | -0.32043 | 60.0037 | -0.18768 | -0.036621 | -0.068665 | 0.045776 | -0.064087 | 0.032044 | -0.18311 | 0.068665 | -0.14648 | 0.16937 | 122.9782 | -0.027466 | 122.9965 | 123.0194 | 122.8821 | 122.8867 | 122.8455 | -123.0469 | -122.9507 | 122.8455 | 122.9599 | 59.8114 | 59.7473
635.8281 | 123.2117 | -59.9533 | 62.9288 | -0.045166 | 0.0011257 | 0.063854 | 0.064668 | 0.0013245 | 0.00029044 | -0.0016171 | 0.011932 | 0.0009528 | 0.06599 | 0.056234 | -0.003136 | 0.0020336 | -0.0033581 | -0.15106 | 62.8601 | -60.0586 | 63.0524 | -59.8755 | -60.2234 | 0.022888 | -0.11902 | 62.8601 | -59.9762 | 63.0249 | -59.9579 | -60.054 | -59.8663 | -0.10529 | -0.068665 | 0.1236 | 0.07782 | 59.9762 | -0.27008 | 60.0815 | -0.16479 | -0.022888 | -0.068665 | 0.09613 | -0.004578 | 0.086975 | -0.10071 | 0.10986 | -0.07782 | 0.18311 | 123.111 | 0.01831 | 123.0011 | 122.9187 | 122.8363 | 122.8134 | 122.8134 | -122.9874 | -122.905 | 123.0057 | 122.9782 | 59.8022 | 59.8343
636.8906 | 123.111 | -59.9899 | 62.9379 | -0.28168 | 0.0028347 | 0.057445 | 0.067659 | 0.0011109 | -0.0014184 | -0.0022581 | -0.097931 | 0.0028754 | 0.065563 | 0.06307 | -0.0042042 | 0.0037426 | -0.00036747 | -0.018311 | 62.8693 | -60.1135 | 62.883 | -59.903 | -60.3241 | -0.11444 | -0.22888 | 62.915 | -60.0174 | 62.9791 | -60.0632 | -60.1868 | -59.967 | -0.1236 | -0.068664 | -0.054931 | 0.086975 | 59.8755 | -0.33417 | 59.9991 | -0.21057 | -0.027466 | -0.022888 | 0.041199 | -0.073242 | 0.022888 | -0.19684 | 0.050354 | -0.16937 | 0.21057 | 122.9965 | -0.045776 | 122.9965 | 122.9828 | 122.9324 | 122.8592 | 122.905 | -123.0515 | -122.9553 | 122.8729 | 122.9691 | 59.9716 | 59.761
637.8281 | 123.1888 | -59.9533 | 62.9242 | -0.12146 | 0.00069854 | 0.064281 | 0.066163 | 0.00068369 | -0.00013676 | -0.00097627 | 0.014984 | 0.0028754 | 0.064495 | 0.064993 | -0.0044178 | 0.0031018 | -0.0020765 | -0.18768 | 62.8464 | -60.054 | 62.9379 | -59.8343 | -60.1959 | -0.036621 | -0.13733 | 62.8464 | -59.9716 | 63.0112 | -59.9762 | -60.0769 | -59.8984 | -0.10071 | -0.077819 | 0.013733 | 0.11902 | 59.9167 | -0.24262 | 60.0174 | -0.14191 | -0.018311 | -0.077819 | 0.086975 | -0.022888 | 0.054932 | -0.1236 | 0.073243 | -0.10529 | 0.21973 | 122.9919 | -0.004577 | 122.9828 | 122.9004 | 122.818 | 122.7997 | 122.7997 | -122.9782 | -122.8958 | 122.8912 | 122.9645 | 59.7656 | 59.816
638.8906 | 123.1247 | -59.9442 | 62.9608 | -0.083313 | 0.0021939 | 0.063 | 0.068941 | 0.0026063 | 7.6842e-05 | -0.00097627 | -0.076569 | 0.0011664 | 0.064922 | 0.067983 | -0.0050586 | 0.0039562 | -0.0035719 | -0.1236 | 62.8922 | -60.0632 | 62.9471 | -59.8297 | -60.1913 | 0.004578 | -0.24719 | 62.8876 | -59.9854 | 63.0203 | -59.9991 | -60.0952 | -59.903 | -0.11902 | -0.068664 | -0.013732 | 0.11444 | 59.9487 | -0.24719 | 60.0677 | -0.12817 | -0.041199 | -0.073242 | 0.05951 | -0.054931 | 0.041199 | -0.15106 | 0.082398 | -0.10986 | 0.23346 | 123.0103 | -0.013732 | 123.0057 | 122.9553 | 122.8729 | 122.8363 | 122.8317 | -123.024 | -122.9462 | 122.8912 | 122.9645 | 59.8206 | 59.697
639.8281 | 123.2025 | -59.9442 | 62.9105 | -0.1062 | -0.00036966 | 0.064281 | 0.06595 | -0.0033753 | -0.0016322 | -0.00076267 | -0.018585 | -0.0018244 | 0.063 | 0.064352 | -0.004845 | 0.0024608 | -0.0022901 | -0.068665 | 62.8464 | -60.0266 | 62.9745 | -59.8022 | -60.1501 | -0.013733 | -0.091553 | 62.8372 | -59.9854 | 63.0569 | -59.9396 | -60.0677 | -59.8801 | -0.082397 | -0.064086 | 0.064087 | 0.14191 | 59.9304 | -0.20599 | 60.0128 | -0.1236 | -0.041199 | -0.073242 | 0.14649 | 0.004578 | 0.064087 | -0.1236 | 0.10529 | -0.082397 | 0.2243 | 123.0011 | 0.045777 | 123.0423 | 122.8729 | 122.8226 | 122.7905 | 122.7814 | -122.937 | -122.8958 | 122.9187 | 123.0011 | 59.8755 | 59.8526
640.8281 | 123.1934 | -59.9487 | 62.9059 | -0.052796 | 0.0021939 | 0.063 | 0.068086 | 0.00046989 | -0.00035036 | 0.00073273 | -0.052155 | 0.0020208 | 0.065349 | 0.058584 | -0.0044178 | 0.0041698 | -0.00036747 | -0.19684 | 62.8464 | -60.1044 | 62.9288 | -59.848 | -60.2371 | -0.059509 | -0.15106 | 62.8418 | -59.9762 | 63.0386 | -59.967 | -60.0494 | -59.8434 | -0.15564 | -0.059509 | 0.022888 | 0.10071 | 59.8892 | -0.28839 | 60.0449 | -0.13275 | -0.027466 | -0.064087 | 0.13275 | -0.018311 | 0.10528 | -0.10071 | 0.13275 | -0.073242 | 0.25635 | 123.0331 | 0.009155 | 123.0148 | 122.9507 | 122.818 | 122.7951 | 122.7905 | -123.0103 | -122.8821 | 122.8775 | 122.9874 | 59.7519 | 59.7977
641.8906 | 123.2025 | -59.935 | 62.9517 | 0.015869 | 0.0039029 | 0.06599 | 0.067018 | -0.0014527 | -0.00056396 | -0.0024717 | 0.0027771 | 0.0005256 | 0.064709 | 0.063925 | -0.0067676 | 0.0028882 | 0.0011279 | -0.10529 | 62.8555 | -60.0128 | 63.0066 | -59.7519 | -60.0861 | 0.10071 | 0 | 62.8647 | -59.9442 | 63.0569 | -59.8984 | -60.0128 | -59.8526 | -0.077819 | -0.09613 | 0.054932 | 0.18311 | 60.0357 | -0.15106 | 60.1135 | -0.073243 | -0.009155 | -0.086975 | 0.10529 | 0.036622 | 0.082398 | -0.077819 | 0.091553 | -0.068664 | 0.26093 | 123.0194 | 0.045777 | 123.0011 | 122.8683 | 122.8088 | 122.7905 | 122.7997 | -122.9645 | -122.8958 | 122.9416 | 122.9919 | 59.8297 | 59.935
642.8281 | 123.1613 | -59.9487 | 62.9379 | -0.090943 | 0.00048494 | 0.064709 | 0.065736 | -0.0033753 | -0.0044092 | -0.00076267 | -0.076569 | 0.0005256 | 0.065136 | 0.069479 | -0.0039906 | 0.0041698 | 5.9726e-05 | -0.21057 | 62.851 | -60.1089 | 62.9105 | -59.8755 | -60.2325 | -0.09613 | -0.18768 | 62.8372 | -59.9945 | 63.0341 | -59.9625 | -60.0815 | -59.8892 | -0.16022 | -0.086975 | -0.027466 | 0.073242 | 59.8526 | -0.28381 | 60.0128 | -0.1236 | -0.045777 | -0.10071 | 0.096131 | -0.013733 | 0.059509 | -0.13275 | 0.10529 | -0.086975 | 0.23346 | 123.0194 | 0.032044 | 123.0286 | 122.9599 | 122.8317 | 122.7997 | 122.7859 | -123.0469 | -122.9324 | 122.8592 | 122.9828 | 59.7382 | 59.761
643.8906 | 123.1247 | -59.9533 | 62.9471 | -0.098572 | 0.0019803 | 0.063427 | 0.068086 | 0.00025629 | -0.0037684 | 0.0018009 | -0.07962 | 0.0020208 | 0.065777 | 0.062429 | -0.0012134 | 0.0022472 | -0.0010083 | -0.10529 | 62.8922 | -60.0586 | 62.9517 | -59.8434 | -60.2005 | 0.013733 | -0.082397 | 62.8922 | -59.9854 | 63.0798 | -59.9945 | -60.0723 | -59.8846 | -0.10529 | -0.054932 | 0.004577 | 0.10986 | 59.967 | -0.24719 | 60.0723 | -0.14191 | -0.032044 | -0.054932 | 0.13275 | -0.041199 | 0.068664 | -0.11902 | 0.10071 | -0.086975 | 0.21515 | 123.0103 | -0.009155 | 123.0652 | 122.9507 | 122.8775 | 122.8455 | 122.8455 | -123.0057 | -122.9324 | 122.905 | 123.0331 | 59.848 | 59.8709
644.8281 | 123.0652 | -59.9991 | 62.9608 | -0.098572 | 0.0015529 | 0.064068 | 0.067445 | 0.0026063 | -0.0014184 | -0.0016171 | -0.067413 | 0.00138 | 0.067699 | 0.070761 | -0.0037768 | 0.0073742 | -0.0029309 | -0.17395 | 62.883 | -60.0998 | 62.851 | -59.9396 | -60.2875 | -0.13275 | -0.27008 | 62.8693 | -60.0266 | 62.9471 | -60.0906 | -60.2188 | -59.9854 | -0.10071 | -0.077819 | -0.10986 | 0.059509 | 59.8663 | -0.28839 | 59.967 | -0.18768 | -0.027466 | -0.091552 | -0.013732 | -0.091553 | 0.013732 | -0.21973 | 0.041198 | -0.19226 | 0.16022 | 122.9507 | -0.064087 | 122.9736 | 122.9828 | 122.8958 | 122.8821 | 122.8683 | -123.0606 | -122.9874 | 122.85 | 122.9462 | 59.8251 | 59.729
645.8906 | 123.1979 | -59.9396 | 62.9196 | -0.12146 | 0.0015529 | 0.062145 | 0.065736 | -0.0044433 | -0.00013676 | -0.0033261 | 0.021088 | 9.8198e-05 | 0.067486 | 0.054098 | -0.0059132 | 0.0026746 | -0.0025037 | -0.17853 | 62.8555 | -60.0677 | 62.9288 | -59.8297 | -60.2097 | -0.032043 | -0.17395 | 62.851 | -59.9854 | 63.0157 | -59.9854 | -60.0494 | -59.8892 | -0.12817 | -0.064087 | 0.009155 | 0.10986 | 59.9075 | -0.27008 | 60.0357 | -0.14191 | -0.045777 | -0.068665 | 0.09613 | -0.045777 | 0.050354 | -0.10986 | 0.096131 | -0.064086 | 0.23804 | 122.9965 | 0 | 123.0011 | 122.9233 | 122.8363 | 122.7951 | 122.7905 | -122.9874 | -122.905 | 122.8683 | 122.9553 | 59.761 | 59.7656
646.8281 | 123.0881 | -59.9945 | 62.9379 | -0.045166 | 0.0019803 | 0.064495 | 0.067872 | 0.0011109 | 0.00050424 | 0.00030553 | -0.091827 | 0.0015936 | 0.06599 | 0.068838 | -0.0050586 | 0.003529 | -0.0010083 | -0.17395 | 62.8738 | -60.0998 | 62.8876 | -59.9213 | -60.2692 | -0.086975 | -0.24719 | 62.8738 | -60.022 | 62.9425 | -60.0906 | -60.2051 | -59.9854 | -0.10529 | -0.064087 | -0.050354 | 0.073242 | 59.9075 | -0.27466 | 60.0128 | -0.16937 | -0.027466 | -0.064087 | 0.004578 | -0.09613 | 0.009155 | -0.21057 | 0.036621 | -0.1831 | 0.17853 | 122.9874 | -0.068664 | 122.9645 | 122.9736 | 122.8958 | 122.8683 | 122.8683 | -123.0377 | -122.9599 | 122.8821 | 122.937 | 59.8206 | 59.7473
647.8906 | 123.1842 | -59.9304 | 62.9471 | -0.037537 | 0.0017667 | 0.063427 | 0.065523 | -0.00038451 | -0.0018458 | -0.0039671 | -0.0002747 | 0.0007392 | 0.067272 | 0.056234 | -0.0037768 | 0.0028882 | -0.0012219 | -0.14648 | 62.8693 | -60.0357 | 62.9517 | -59.7977 | -60.1501 | 0.036621 | -0.07782 | 62.8647 | -59.9762 | 63.0661 | -59.9167 | -60.0128 | -59.8663 | -0.10529 | -0.07782 | 0.004577 | 0.13275 | 59.967 | -0.21973 | 60.0723 | -0.11444 | -0.045776 | -0.082398 | 0.11902 | 0.013733 | 0.064087 | -0.082397 | 0.10986 | -0.036621 | 0.23804 | 122.9874 | 0.059509 | 123.0423 | 122.905 | 122.8409 | 122.7997 | 122.7951 | -122.9828 | -122.9233 | 122.8821 | 122.9965 | 59.7839 | 59.8526
648.8281 | 123.1201 | -59.9487 | 62.9471 | -0.083313 | 0.0021939 | 0.062572 | 0.066163 | 0.0026063 | 0.00029044 | 0.0018009 | -0.082672 | 0.00138 | 0.067272 | 0.064138 | -0.0044178 | 0.0028882 | -0.0044263 | -0.12817 | 62.8922 | -60.0769 | 62.9379 | -59.8526 | -60.2188 | 0.004578 | -0.10986 | 62.8738 | -59.9899 | 62.9929 | -60.022 | -60.1364 | -59.9396 | -0.12817 | -0.054932 | -0.009156 | 0.09613 | 59.9533 | -0.27008 | 60.0815 | -0.14191 | -0.041199 | -0.073243 | 0.045776 | -0.073243 | 0.009155 | -0.18768 | 0.050354 | -0.14649 | 0.2243 | 123.0148 | -0.032044 | 122.9828 | 122.9691 | 122.8638 | 122.8409 | 122.8226 | -123.024 | -122.937 | 122.8867 | 122.9416 | 59.8206 | 59.8389
649.8281 | 123.1201 | -59.9899 | 62.9517 | -0.090943 | -0.0022923 | 0.063641 | 0.068513 | 0.00068369 | -0.00099116 | -0.0020443 | -0.058258 | 0.0011664 | 0.066418 | 0.062643 | -0.004845 | 0.005238 | -0.0010083 | -0.18768 | 62.8281 | -60.1501 | 62.9196 | -59.848 | -60.3516 | -0.10071 | -0.24719 | 62.8738 | -59.9945 | 62.9654 | -60.0632 | -60.1685 | -59.9533 | -0.16022 | -0.1236 | -0.032043 | 0.14191 | 59.8892 | -0.36163 | 60.0494 | -0.20142 | -0.004578 | -0.07782 | 0.013733 | -0.073242 | 0.036621 | -0.17853 | 0.041199 | -0.17395 | 0.30212 | 123.0698 | -0.068664 | 122.9599 | 122.9782 | 122.8683 | 122.818 | 122.8638 | -123.1018 | -122.9462 | 122.9095 | 122.9553 | 59.8022 | 59.7427
650.8906 | 123.2208 | -59.9213 | 62.9562 | -0.068054 | 0.0013393 | 0.063 | 0.065309 | 4.2692e-05 | -0.0029138 | -0.00076267 | 0.024139 | 0.0022346 | 0.064281 | 0.062002 | -0.0029224 | 0.0037426 | 5.9726e-05 | -0.11902 | 62.8693 | -60.054 | 62.9791 | -59.7748 | -60.1318 | 0.054932 | -0.068665 | 62.851 | -59.9762 | 63.0661 | -59.9075 | -59.9808 | -59.8526 | -0.13275 | -0.086975 | 0.022888 | 0.14648 | 59.9762 | -0.21057 | 60.1089 | -0.07782 | -0.054931 | -0.10529 | 0.10986 | 0.013733 | 0.068665 | -0.059509 | 0.1236 | -0.004578 | 0.27924 | 123.0331 | 0.068664 | 123.0423 | 122.9233 | 122.8271 | 122.7905 | 122.7722 | -123.0103 | -122.9324 | 122.9004 | 122.9874 | 59.8022 | 59.8526
651.8281 | 123.1476 | -59.9442 | 62.9471 | -0.068054 | 0.0015529 | 0.062786 | 0.067018 | 0.0026063 | -0.0029138 | 0.00030553 | -0.076569 | 0.0041572 | 0.06364 | 0.066274 | -0.0042042 | 0.0039562 | -0.0035719 | -0.10529 | 62.9059 | -60.0815 | 62.9379 | -59.8434 | -60.2005 | 0 | -0.19226 | 62.883 | -59.9808 | 63.0157 | -59.9716 | -60.1089 | -59.9167 | -0.13733 | -0.041199 | -0.009156 | 0.10071 | 59.9442 | -0.25635 | 60.0815 | -0.11902 | -0.036621 | -0.064087 | 0.068664 | -0.027466 | 0.027466 | -0.16479 | 0.064087 | -0.12817 | 0.23804 | 123.0194 | 0.009155 | 122.9965 | 122.9874 | 122.8638 | 122.85 | 122.8271 | -123.0286 | -122.9279 | 122.8821 | 122.9599 | 59.8389 | 59.7519
652.8906 | 123.1796 | -59.9625 | 62.9379 | -0.1062 | -0.00015586 | 0.063641 | 0.065309 | -0.0014527 | 0.00029044 | -0.00033547 | 0.057709 | 0.0007392 | 0.064922 | 0.062856 | -0.0042042 | 0.003529 | 0.00070073 | -0.16479 | 62.8876 | -60.0677 | 62.9379 | -59.8389 | -60.1868 | 0.022888 | -0.18768 | 62.8693 | -59.9716 | 63.002 | -59.9716 | -60.054 | -59.8846 | -0.10529 | -0.050354 | 0 | 0.1236 | 59.9854 | -0.22431 | 60.0906 | -0.11902 | -0.009156 | -0.068664 | 0.064087 | -0.009156 | 0.077819 | -0.091553 | 0.086975 | -0.082397 | 0.22888 | 123.0057 | 0 | 122.9736 | 122.9553 | 122.8409 | 122.85 | 122.8317 | -123.0057 | -122.9095 | 122.9004 | 122.9645 | 59.7977 | 59.7748
653.8281 | 123.1018 | -59.9579 | 62.9608 | -0.090943 | 0.0021939 | 0.063854 | 0.068086 | 0.0023925 | -0.0035548 | -0.0033261 | -0.07962 | 0.0039434 | 0.066204 | 0.070547 | -0.0042042 | 0.0043836 | -0.00079467 | -0.14191 | 62.883 | -60.0723 | 62.9242 | -59.8618 | -60.2188 | -0.027466 | -0.13275 | 62.8876 | -59.9899 | 62.9791 | -60.0311 | -60.1547 | -59.9442 | -0.11444 | -0.077819 | -0.036621 | 0.096131 | 59.9304 | -0.26093 | 60.0449 | -0.14648 | -0.032043 | -0.073242 | 0.018311 | -0.073242 | 0.013733 | -0.19684 | 0.045776 | -0.1648 | 0.21057 | 122.9965 | -0.041199 | 122.9691 | 122.9553 | 122.8775 | 122.8409 | 122.8455 | -123.0331 | -122.9507 | 122.8821 | 122.937 | 59.816 | 59.8251
654.8906 | 123.1796 | -59.935 | 62.9471 | -0.12146 | 0.00091214 | 0.062145 | 0.067445 | -0.0018799 | -0.0027002 | -0.0046079 | 0.018036 | 0.0009528 | 0.064495 | 0.064138 | -0.004845 | 0.0048108 | -0.0016493 | -0.18768 | 62.851 | -60.0632 | 62.9242 | -59.8251 | -60.1868 | -0.027466 | -0.14648 | 62.8326 | -59.9945 | 62.9929 | -59.9899 | -60.0494 | -59.8892 | -0.12817 | -0.096131 | -0.022889 | 0.10986 | 59.9075 | -0.25177 | 60.0357 | -0.1236 | -0.059509 | -0.11444 | 0.045776 | -0.054931 | 0.045777 | -0.11444 | 0.10529 | -0.054931 | 0.23804 | 122.9874 | 0.004578 | 122.9874 | 122.9141 | 122.8271 | 122.7859 | 122.7676 | -123.0103 | -122.9416 | 122.8592 | 122.9279 | 59.7473 | 59.7885
655.8281 | 123.1705 | -59.9487 | 62.9654 | -0.12909 | 0.0024075 | 0.063213 | 0.068727 | -0.00038451 | 7.6842e-05 | -0.00012167 | -0.058258 | 0.00138 | 0.066845 | 0.060934 | -0.0039906 | 0.0063062 | 0.0024097 | -0.10529 | 62.9013 | -60.0586 | 62.9471 | -59.8114 | -60.2097 | 0.032043 | -0.068665 | 62.9059 | -59.9579 | 62.9379 | -59.9762 | -60.0494 | -59.9121 | -0.10986 | -0.064087 | -0.01831 | 0.13733 | 59.9808 | -0.26093 | 60.0906 | -0.15106 | -0.009156 | -0.059509 | -0.027466 | -0.027466 | 0.036621 | -0.10071 | 0.045777 | -0.091552 | 0.24719 | 123.0057 | -0.01831 | 122.8958 | 122.9599 | 122.8638 | 122.85 | 122.8546 | -123.024 | -122.9233 | 122.8958 | 122.8867 | 59.8434 | 59.8801
656.8906 | 123.2254 | -59.935 | 62.9425 | -0.045166 | 0.00091214 | 0.061718 | 0.06595 | -0.00059811 | -0.0016322 | 0.00073273 | 0.14011 | 0.0005256 | 0.06834 | 0.064138 | -0.0035632 | 0.0022472 | 0.00027333 | -0.07782 | 62.8784 | -60.022 | 63.0203 | -59.7198 | -60.0632 | 0.12817 | -0.27008 | 62.8693 | -59.9579 | 63.0753 | -59.9167 | -59.9625 | -59.8297 | -0.086975 | -0.064087 | 0.07782 | 0.21515 | 60.0632 | -0.12817 | 60.1501 | -0.041198 | -0.022888 | -0.073242 | 0.13275 | 0.018311 | 0.10529 | -0.027465 | 0.12817 | -0.004577 | 0.30212 | 123.0423 | 0.041199 | 123.0331 | 122.9004 | 122.8271 | 122.8134 | 122.8043 | -122.9645 | -122.9004 | 122.9553 | 123.0103 | 59.8572 | 59.6649
657.8281 | 123.1018 | -59.9579 | 62.9745 | -0.090943 | 0.00027134 | 0.061718 | 0.068513 | -0.0016663 | -0.0012048 | -0.0024717 | -0.015534 | 0.0011664 | 0.06599 | 0.07247 | -0.0029224 | 0.003529 | 0.0017687 | 0.10986 | 62.9562 | -60.022 | 62.8922 | -59.8846 | -60.2417 | 0 | -0.13733 | 62.9105 | -59.9808 | 62.9974 | -59.9991 | -60.1227 | -59.9533 | -0.064087 | -0.01831 | -0.082397 | 0.073242 | 59.9579 | -0.28381 | 60.022 | -0.21973 | -0.022888 | -0.064087 | 0.022889 | -0.041198 | 0.004578 | -0.16479 | 0.027466 | -0.14191 | 0.13733 | 122.9141 | -0.01831 | 122.9782 | 122.9782 | 122.8912 | 122.9141 | 122.8683 | -122.9965 | -122.9553 | 122.85 | 122.9553 | 60.0677 | 59.8206
658.8281 | 123.2071 | -59.9213 | 62.9562 | -0.16724 | 5.7742e-05 | 0.061077 | 0.064454 | -0.0018799 | -0.00099116 | -0.00054907 | 0.0058289 | 0.00138 | 0.066418 | 0.055166 | -0.0027088 | 0.003529 | -0.0027173 | -0.036621 | 62.8738 | -60.0449 | 63.0157 | -59.7427 | -60.1044 | 0.09613 | 0.009155 | 62.8738 | -59.9442 | 63.0661 | -59.903 | -60.0082 | -59.8526 | -0.1236 | -0.082398 | 0.059509 | 0.17853 | 60.0174 | -0.18311 | 60.141 | -0.059509 | -0.022888 | -0.082398 | 0.10986 | 0.018311 | 0.068665 | -0.086975 | 0.091553 | -0.064087 | 0.30212 | 123.0606 | 0.041199 | 123.0103 | 122.9187 | 122.818 | 122.7951 | 122.7951 | -123.0011 | -122.9004 | 122.937 | 122.9874 | 59.8846 | 59.9304
659.8906 | 123.1979 | -59.9854 | 62.9517 | -0.12909 | 0.00048494 | 0.064709 | 0.069154 | -0.0010253 | -0.0018458 | -0.0014035 | -0.067413 | 0.0022346 | 0.065777 | 0.062216 | -0.0039906 | 0.0054516 | -0.00015387 | -0.20599 | 62.8876 | -60.0861 | 62.8372 | -59.9579 | -60.2829 | -0.10071 | -0.27008 | 62.8876 | -60.0174 | 63.0295 | -60.3333 | -60.4294 | -59.9899 | -0.10071 | -0.064087 | -0.11444 | 0.027466 | 59.8846 | -0.29755 | 59.9854 | -0.19684 | -0.032043 | -0.064087 | 0.07782 | -0.3479 | -0.004577 | -0.44403 | 0.027466 | -0.41199 | 0.12817 | 122.9233 | -0.31586 | 123.0469 | 122.9736 | 122.905 | 122.8729 | 122.8729 | -123.0377 | -122.9691 | 122.8226 | 123.0148 | 59.7794 | 59.7153
660.8281 | 123.2254 | -59.9075 | 62.9745 | -0.19775 | 0.0013393 | 0.062145 | 0.064668 | 0.0015381 | -0.00056396 | -0.00012167 | 0.030243 | 0.0015936 | 0.06599 | 0.061361 | -0.0029224 | 0.0020336 | -0.0037855 | -0.041199 | 62.8647 | -60.0449 | 63.0478 | -59.729 | -60.1089 | 0.11902 | 0.013733 | 62.8967 | -59.9625 | 63.0661 | -59.8892 | -59.9854 | -59.8618 | -0.13733 | -0.10986 | 0.073243 | 0.17853 | 60.0266 | -0.20142 | 60.1639 | -0.064087 | -0.054931 | -0.077819 | 0.091553 | 0.018311 | 0.045777 | -0.07782 | 0.10071 | -0.022889 | 0.31586 | 123.0927 | 0.073242 | 123.0286 | 122.9095 | 122.8592 | 122.7722 | 122.8043 | -123.0194 | -122.937 | 122.9553 | 122.9736 | 59.8663 | 59.9213
661.8906 | 123.2346 | -59.9396 | 62.9288 | -0.1062 | 0.0011257 | 0.063641 | 0.066591 | 0.0017517 | 7.6842e-05 | -0.0037533 | -0.0094299 | 0.0028754 | 0.066204 | 0.066488 | -0.0022816 | 0.003529 | -0.0039991 | -0.14648 | 62.8326 | -60.0677 | 62.9883 | -59.7839 | -60.1639 | -0.013733 | -0.12817 | 62.8189 | -59.9808 | 63.0386 | -59.8755 | -60.0769 | -59.9167 | -0.12817 | -0.09613 | 0.059509 | 0.15564 | 59.9258 | -0.2243 | 60.054 | -0.09613 | -0.041199 | -0.10986 | 0.10986 | 0.064087 | 0.022888 | -0.13733 | 0.064087 | -0.09613 | 0.28381 | 123.056 | 0.10529 | 123.0194 | 122.9004 | 122.7997 | 122.7722 | 122.7585 | -122.9965 | -122.9095 | 122.9279 | 122.9782 | 59.7931 | 59.8114
662.8438 | 123.1201 | -59.9899 | 62.9333 | -0.068054 | -0.00079686 | 0.062786 | 0.067445 | 0.0055969 | 0.00050424 | 0.00073273 | -0.018585 | 0.00138 | 0.069195 | 0.065634 | -0.0054858 | 0.0043836 | 0.00048713 | -0.23346 | 62.8601 | -60.1044 | 62.851 | -59.6146 | -60.2875 | -0.12817 | -0.29755 | 62.8922 | -59.9899 | 62.9562 | -60.0586 | -60.1868 | -59.9625 | -0.11444 | -0.073243 | -0.082398 | 0.37537 | 59.8618 | -0.29755 | 59.9762 | -0.18311 | 0 | -0.041199 | 0.022888 | -0.068665 | 0.027466 | -0.19684 | 0.027466 | -0.19684 | 0.48981 | 122.9553 | -0.068665 | 122.9462 | 122.9645 | 122.8821 | 122.85 | 122.8821 | -123.0377 | -122.9233 | 122.8409 | 122.9462 | 59.7565 | 59.6924
663.8906 | 123.2071 | -59.935 | 62.9105 | -0.075684 | 0.00069854 | 0.064709 | 0.064668 | -0.0014527 | -0.00056396 | -0.0014035 | -0.030792 | 0.0009528 | 0.064281 | 0.053671 | -0.0061268 | 0.0054516 | -0.0018629 | -0.14648 | 62.8189 | -60.0632 | 62.9791 | -59.7748 | -60.1685 | -0.009155 | -0.13733 | 62.8189 | -59.9991 | 63.0478 | -59.8755 | -60.0952 | -59.8938 | -0.12817 | -0.091552 | 0.068665 | 0.16022 | 59.9258 | -0.23346 | 60.054 | -0.10529 | -0.064086 | -0.091552 | 0.13733 | 0.05951 | 0.041199 | -0.16022 | 0.10529 | -0.096131 | 0.28839 | 123.0423 | 0.1236 | 123.0469 | 122.8821 | 122.818 | 122.7539 | 122.7539 | -122.9736 | -122.9095 | 122.9141 | 122.9828 | 59.7885 | 59.7977
664.8281 | 123.1934 | -59.9304 | 62.9517 | -0.068054 | 0.0017667 | 0.063854 | 0.06595 | -0.0038025 | -0.0020594 | -0.0018307 | -0.0033265 | 9.8198e-05 | 0.06599 | 0.06307 | -0.0016406 | 0.0056652 | -0.0033581 | -0.14191 | 62.8738 | -60.054 | 63.0157 | -59.7519 | -60.1089 | 0.11902 | -0.013733 | 62.8647 | -59.9304 | 63.0524 | -59.9121 | -59.9945 | -59.8618 | -0.1236 | -0.07782 | 0.064087 | 0.17853 | 60.0494 | -0.17853 | 60.173 | -0.054932 | 0 | -0.086975 | 0.10071 | 0.018311 | 0.068665 | -0.064087 | 0.068665 | -0.064087 | 0.30212 | 123.0698 | 0.018311 | 122.9828 | 122.9279 | 122.7951 | 122.8043 | 122.7951 | -123.0057 | -122.8821 | 122.9462 | 122.9828 | 59.7885 | 59.9167
665.8906 | 123.1293 | -59.9808 | 62.9562 | -0.13672 | 0.00048494 | 0.061718 | 0.066163 | 0.00068369 | -0.0037684 | 0.00051913 | -0.076569 | 0.0028754 | 0.067913 | 0.061788 | -0.0061268 | 0.0045972 | -0.00058107 | -0.23804 | 62.8876 | -60.1044 | 62.8693 | -59.9213 | -60.2692 | -0.11444 | -0.24719 | 62.8601 | -60.0037 | 62.97 | -60.0449 | -60.1456 | -59.9533 | -0.1236 | -0.068665 | -0.086975 | 0.059509 | 59.8663 | -0.28839 | 59.9899 | -0.16479 | -0.022888 | -0.096131 | 0.013733 | -0.064087 | 0.027466 | -0.1648 | 0.050354 | -0.14191 | 0.18311 | 122.9736 | -0.041199 | 122.9736 | 122.9919 | 122.8638 | 122.8683 | 122.8409 | -123.0606 | -122.9599 | 122.85 | 122.9507 | 59.7427 | 59.7336
666.8281 | 123.2483 | -59.9075 | 62.9562 | -0.068054 | 0.0013393 | 0.063854 | 0.066804 | 0.0017517 | -0.0018458 | -0.0026853 | 0.021088 | 0.0005256 | 0.066631 | 0.057089 | -0.0052722 | 0.003529 | 0.0011279 | -0.13275 | 62.8601 | -60.0403 | 62.9974 | -59.7565 | -60.1089 | 0.068665 | -0.041199 | 62.883 | -59.9579 | 63.089 | -59.8755 | -59.9625 | -59.8297 | -0.13275 | -0.096131 | 0.041199 | 0.15106 | 59.9762 | -0.20142 | 60.1089 | -0.068665 | -0.050354 | -0.073242 | 0.13275 | 0.032044 | 0.07782 | -0.054931 | 0.12817 | -0.004577 | 0.28381 | 123.0377 | 0.082398 | 123.0469 | 122.9004 | 122.8409 | 122.7676 | 122.7905 | -122.9965 | -122.9141 | 122.905 | 122.9965 | 59.7748 | 59.8663
667.8906 | 123.2162 | -59.9442 | 62.9105 | -0.14435 | 0.0024075 | 0.062572 | 0.066804 | 0.00068369 | -0.0012048 | -0.0018307 | -0.046051 | -0.0009698 | 0.064709 | 0.067129 | -0.0033496 | 0.0045972 | -0.00036747 | -0.15106 | 62.8418 | -60.0632 | 62.7731 | -59.8846 | -59.8389 | 0.032043 | -0.1236 | 62.8555 | -59.9533 | 63.0707 | -59.935 | -60.0586 | -59.8709 | -0.11902 | -0.068664 | -0.13733 | 0.059509 | 59.9762 | 0.10529 | 60.0952 | 0.2243 | -0.009155 | -0.054931 | 0.16022 | 0.009155 | 0.073242 | -0.11444 | 0.082397 | -0.10529 | 0.17853 | 122.8363 | 0.01831 | 123.024 | 122.905 | 122.8088 | 122.7859 | 122.7997 | -122.9736 | -122.8638 | 122.7173 | 123.0148 | 59.7931 | 59.8206
668.8281 | 123.2025 | -59.9167 | 62.9379 | -0.15961 | 0.0024075 | 0.063213 | 0.065523 | -0.0038025 | -0.0033412 | -0.0033261 | 0.011932 | 0.0011664 | 0.064922 | 0.067129 | -0.0050586 | 0.0026746 | -0.0029309 | -0.11902 | 62.8647 | -60.0311 | 63.0203 | -59.7382 | -60.1135 | 0.086975 | 0.027466 | 62.8738 | -59.9625 | 63.1027 | -59.8709 | -59.9625 | -59.8114 | -0.11444 | -0.073242 | 0.082398 | 0.17853 | 60.0037 | -0.19684 | 60.1181 | -0.082397 | -0.045776 | -0.064087 | 0.16479 | 0.045776 | 0.10529 | -0.045776 | 0.15106 | 0 | 0.29297 | 123.0515 | 0.091552 | 123.0652 | 122.8958 | 122.8363 | 122.7814 | 122.7905 | -122.9691 | -122.9004 | 122.937 | 123.0194 | 59.7977 | 59.9442
669.8906 | 123.2346 | -59.9442 | 62.915 | -0.17487 | 0.0015529 | 0.060009 | 0.067445 | -0.0018799 | -0.0033412 | 0.0018009 | -0.015534 | 0.0005256 | 0.064281 | 0.063497 | -0.0044178 | 0.0024608 | -0.0016493 | -0.009155 | 62.8143 | -60.054 | 62.9929 | -59.7748 | -60.1868 | -0.018311 | -0.10986 | 62.8235 | -59.9487 | 63.0569 | -59.9396 | -60.0723 | -59.8709 | -0.10986 | -0.10071 | 0.07782 | 0.16937 | 59.9258 | -0.24262 | 60.0357 | -0.13275 | -0.004577 | -0.091553 | 0.14191 | 0.004578 | 0.073242 | -0.12817 | 0.077819 | -0.1236 | 0.27924 | 123.0469 | 0.009155 | 123.0057 | 122.8683 | 122.7722 | 122.7585 | 122.7676 | -122.9691 | -122.8638 | 122.937 | 123.0011 | 59.935 | 59.8343
670.8281 | 123.1796 | -59.9579 | 62.9013 | -0.098572 | 0.0013393 | 0.064495 | 0.066377 | -0.00081171 | 0.0013586 | -0.0026853 | 0.036346 | 0.0005256 | 0.065136 | 0.059011 | -0.0046314 | 0.0056652 | 5.9726e-05 | -0.16937 | 62.8647 | -60.054 | 62.9517 | -59.8297 | -60.1822 | 0.059509 | -0.14191 | 62.8738 | -59.9716 | 63.0066 | -59.9625 | -60.0586 | -59.8801 | -0.09613 | -0.036621 | 0.050354 | 0.12817 | 60.0174 | -0.2243 | 60.1135 | -0.12817 | -0.013733 | -0.027466 | 0.10529 | -0.004577 | 0.07782 | -0.10071 | 0.091553 | -0.086975 | 0.2243 | 123.0057 | 0.009156 | 122.9782 | 122.9187 | 122.8455 | 122.8226 | 122.8317 | -122.9553 | -122.8729 | 122.9095 | 122.9645 | 59.7885 | 59.816
671.8281 | 123.2071 | -59.935 | 62.9654 | -0.075684 | 0.0019803 | 0.060863 | 0.067872 | -0.0012391 | -0.003982 | -0.0022581 | 0.0058289 | -0.001397 | 0.064495 | 0.05837 | -0.0042042 | 0.003529 | -0.0018629 | -0.16479 | 62.8784 | -60.0723 | 62.9654 | -59.8068 | -60.1547 | 0.036621 | -0.091553 | 62.8555 | -59.9808 | 63.0432 | -59.9213 | -60.0266 | -59.8434 | -0.13733 | -0.086975 | 0 | 0.12817 | 59.9716 | -0.21973 | 60.1089 | -0.082397 | -0.045776 | -0.10986 | 0.07782 | 0.013733 | 0.091553 | -0.091552 | 0.13733 | -0.045776 | 0.2655 | 123.0377 | 0.059509 | 123.024 | 122.9507 | 122.8363 | 122.8134 | 122.7905 | -123.0377 | -122.9462 | 122.9004 | 122.9782 | 59.7702 | 59.8434
672.9062 | 123.0972 | -59.9533 | 62.9837 | 0.00061049 | -0.00079686 | 0.062786 | 0.068513 | -0.0018799 | 0.0026404 | -0.0026853 | -0.049103 | 0.0007392 | 0.066204 | 0.066488 | -0.0042042 | 0.0031018 | -0.0029309 | -0.13733 | 62.9196 | -60.0586 | 62.8555 | -59.8114 | -60.2921 | 0.009155 | -0.16022 | 62.9105 | -59.9854 | 62.97 | -60.022 | -60.1135 | -59.9442 | -0.10529 | -0.064087 | -0.12817 | 0.14191 | 59.9625 | -0.33875 | 60.0677 | -0.23346 | -0.032044 | -0.073243 | -0.013733 | -0.068665 | 0.009155 | -0.16022 | 0.041199 | -0.12817 | 0.24719 | 122.9141 | -0.036621 | 122.9553 | 122.9782 | 122.8958 | 122.8729 | 122.8638 | -123.0423 | -122.9691 | 122.8088 | 122.9233 | 59.816 | 59.7931
673.8281 | 123.2254 | -59.9213 | 62.9654 | -0.045166 | 0.00048494 | 0.063427 | 0.064668 | -0.0016663 | -0.00035036 | -0.00097627 | 0.021088 | 0.0009528 | 0.06599 | 0.060507 | -0.004845 | 0.0031018 | -0.0029309 | -0.091553 | 62.8738 | -60.0357 | 63.0341 | -59.7015 | -60.0632 | 0.12817 | 0.009155 | 62.8738 | -59.9258 | 63.0936 | -59.8663 | -59.9808 | -59.8206 | -0.11444 | -0.091553 | 0.068665 | 0.21973 | 60.0494 | -0.14191 | 60.1639 | -0.027465 | -0.004577 | -0.091553 | 0.12817 | 0.054932 | 0.10071 | -0.059509 | 0.10529 | -0.054932 | 0.33417 | 123.0698 | 0.059509 | 123.0194 | 122.9095 | 122.7997 | 122.7951 | 122.7951 | -123.0011 | -122.8912 | 122.9553 | 123.0148 | 59.8297 | 59.9304
674.8906 | 123.1659 | -59.935 | 62.9425 | -0.11383 | 0.0017667 | 0.061932 | 0.066591 | 0.0058105 | -0.0044092 | 0.0015871 | -0.033844 | 0.0009528 | 0.063854 | 0.062429 | -0.0029224 | 0.0026746 | 0.0024097 | -0.19684 | 62.8555 | -60.0632 | 62.9379 | -59.8297 | -60.2005 | -0.013733 | -0.17395 | 62.851 | -59.9808 | 63.0157 | -59.9762 | -60.0906 | -59.8709 | -0.12817 | -0.086975 | -0.004578 | 0.10529 | 59.9213 | -0.2655 | 60.0494 | -0.13733 | -0.045776 | -0.091553 | 0.073242 | -0.041198 | 0.064087 | -0.15564 | 0.10986 | -0.10986 | 0.23346 | 123.0011 | 0.004578 | 122.9965 | 122.9187 | 122.8317 | 122.7905 | 122.7859 | -123.0057 | -122.9233 | 122.8729 | 122.9507 | 59.7382 | 59.761
675.8281 | 123.143 | -59.935 | 62.9562 | -0.045166 | 0.00027134 | 0.061718 | 0.068086 | -0.0023071 | -0.0014184 | 0.0028689 | -0.027741 | 0.0024482 | 0.065349 | 0.06072 | -0.0037768 | 0.003529 | -0.0037855 | -0.086975 | 62.8922 | -60.0174 | 63.0157 | -59.761 | -60.1044 | 0.091553 | -0.013733 | 62.8876 | -59.9442 | 63.0295 | -59.9167 | -60.054 | -59.8663 | -0.082397 | -0.064087 | 0.059509 | 0.17395 | 60.0266 | -0.16937 | 60.1089 | -0.086975 | -0.009155 | -0.068665 | 0.073242 | 0.018311 | 0.068665 | -0.11902 | 0.07782 | -0.10986 | 0.25635 | 123.0331 | 0.027466 | 122.9736 | 122.9095 | 122.8317 | 122.8271 | 122.8226 | -122.9736 | -122.9004 | 122.9507 | 122.9645 | 59.848 | 59.9213
676.8906 | 123.1934 | -59.967 | 62.9333 | -0.1062 | -0.00079686 | 0.063641 | 0.068727 | -0.0018799 | -0.0014184 | -0.0018307 | -0.073517 | 0.0005256 | 0.06834 | 0.064565 | -0.0039906 | 0.0039562 | 5.9726e-05 | -0.21973 | 62.8281 | -60.1318 | 62.9105 | -59.8709 | -60.2234 | -0.07782 | -0.20599 | 62.851 | -60.0128 | 63.0615 | -59.9808 | -60.1318 | -59.903 | -0.16479 | -0.10529 | -0.022889 | 0.09613 | 59.8892 | -0.25635 | 60.054 | -0.091553 | -0.045776 | -0.082398 | 0.12817 | -0.013733 | 0.064087 | -0.16479 | 0.10986 | -0.11902 | 0.26093 | 123.0423 | 0.032043 | 123.0743 | 122.9599 | 122.8638 | 122.7951 | 122.818 | -123.0652 | -122.9462 | 122.8775 | 123.0286 | 59.7473 | 59.761
677.8281 | 123.0698 | -59.9991 | 62.9517 | -0.098572 | 0.0017667 | 0.064281 | 0.066163 | 0.0038879 | 0.00029044 | -0.00033547 | -0.097931 | 0.0026618 | 0.066418 | 0.06072 | -0.003136 | 0.0050244 | -0.0048535 | -0.17853 | 62.9013 | -60.1044 | 62.8738 | -59.9213 | -60.2783 | -0.073242 | -0.25635 | 62.9059 | -60.0037 | 62.9471 | -60.0815 | -60.1913 | -59.9808 | -0.10529 | -0.050354 | -0.07782 | 0.077819 | 59.9258 | -0.27924 | 60.0311 | -0.17395 | -0.004578 | -0.045776 | -0.004577 | -0.082398 | 0.01831 | -0.19226 | 0.022888 | -0.18768 | 0.18311 | 122.9782 | -0.07782 | 122.9507 | 123.0057 | 122.9095 | 122.9004 | 122.905 | -123.056 | -122.9553 | 122.8729 | 122.9462 | 59.8206 | 59.7427
678.8281 | 123.1842 | -59.9533 | 62.9379 | -0.090943 | 0.0013393 | 0.061504 | 0.063814 | 0.0028199 | -0.00099116 | -0.0041807 | 0.021088 | 0.0007392 | 0.064495 | 0.062216 | -0.0016406 | 0.0016064 | 0.00048713 | -0.16479 | 62.8601 | -60.0769 | 62.8922 | -59.8114 | -60.2051 | -0.004578 | -0.15106 | 62.8693 | -59.9808 | 63.0295 | -59.9533 | -60.0494 | -59.8709 | -0.1236 | -0.07782 | -0.045776 | 0.14191 | 59.9487 | -0.25177 | 60.0723 | -0.12817 | -0.027466 | -0.068664 | 0.091553 | 0 | 0.082397 | -0.09613 | 0.10986 | -0.068664 | 0.2655 | 122.9691 | 0.027466 | 123.0103 | 122.937 | 122.85 | 122.8134 | 122.8226 | -123.0148 | -122.9187 | 122.8455 | 122.9828 | 59.7885 | 59.8022
679.8906 | 123.1613 | -59.9899 | 62.9196 | -0.075684 | -0.0018649 | 0.063854 | 0.068513 | 4.2692e-05 | -0.0016322 | -0.00054907 | -0.058258 | 0.0037298 | 0.064922 | 0.062002 | -0.0042042 | 0.005238 | -0.0022901 | -0.24261 | 62.8738 | -60.1181 | 62.8738 | -59.9167 | -60.2921 | -0.09613 | -0.22888 | 62.883 | -59.9991 | 62.9929 | -60.0128 | -60.1318 | -59.9213 | -0.12817 | -0.045777 | -0.045777 | 0.073242 | 59.8938 | -0.30212 | 60.022 | -0.17395 | -0.009155 | -0.036621 | 0.073242 | -0.022888 | 0.068664 | -0.14191 | 0.077819 | -0.13275 | 0.20142 | 122.9919 | -0.013733 | 122.9919 | 122.9919 | 122.8821 | 122.8638 | 122.8729 | -123.0377 | -122.9187 | 122.8638 | 122.9828 | 59.7473 | 59.761
680.8281 | 123.1796 | -59.9396 | 62.9288 | -0.090943 | 0.0021939 | 0.062786 | 0.068513 | -0.0010253 | -0.0037684 | -0.0031125 | -0.015534 | 0.003089 | 0.065777 | 0.06307 | -0.0022816 | 0.00096564 | -0.0042127 | -0.20142 | 62.8922 | -60.0723 | 62.9379 | -59.8343 | -60.1913 | -0.013733 | -0.16022 | 62.8647 | -59.9854 | 63.0341 | -59.9991 | -60.054 | -59.9167 | -0.13275 | -0.036621 | 0.009155 | 0.10528 | 59.9258 | -0.25177 | 60.0586 | -0.11902 | -0.045777 | -0.064087 | 0.10529 | -0.059509 | 0.022888 | -0.11444 | 0.068665 | -0.068664 | 0.23804 | 123.0103 | -0.013732 | 123.0194 | 122.9645 | 122.85 | 122.8317 | 122.8043 | -123.0011 | -122.9141 | 122.8775 | 122.9736 | 59.7382 | 59.7794
681.8906 | 123.1293 | -59.9808 | 62.9517 | -0.15961 | -0.0020785 | 0.062786 | 0.066804 | 0.00025629 | -0.00056396 | -0.0016171 | -0.07962 | 0.0033026 | 0.065136 | 0.066702 | -0.0046314 | 0.0048108 | 0.00070073 | -0.073242 | 62.8784 | -60.0998 | 62.8967 | -59.9579 | -60.2966 | -0.10071 | -0.27008 | 62.8693 | -59.9991 | 62.9654 | -60.0494 | -60.1639 | -59.9579 | -0.11902 | -0.073242 | -0.054931 | 0.022888 | 59.8801 | -0.31586 | 59.9991 | -0.19684 | -0.01831 | -0.082397 | 0.013733 | -0.068664 | 0.022888 | -0.18311 | 0.041198 | -0.16479 | 0.14191 | 122.9965 | -0.050354 | 122.9645 | 122.9782 | 122.8683 | 122.8592 | 122.85 | -123.0515 | -122.9507 | 122.8775 | 122.9462 | 59.9075 | 59.7107
682.8281 | 123.23 | -59.935 | 62.9471 | -0.12146 | 0.00091214 | 0.063854 | 0.066377 | -0.0027343 | -0.0012048 | -0.0011899 | -0.0002747 | 0.0007392 | 0.067272 | 0.06072 | -0.0042042 | 0.0020336 | -0.00015387 | -0.050354 | 62.8922 | -60.0449 | 62.9425 | -59.8206 | -60.1868 | 0.013733 | -0.15106 | 62.8693 | -59.9762 | 63.0249 | -59.9396 | -60.0403 | -59.8801 | -0.10986 | -0.054932 | -0.004578 | 0.11444 | 59.9487 | -0.25177 | 60.0586 | -0.14191 | -0.041198 | -0.07782 | 0.077819 | -0.004577 | 0.054932 | -0.10529 | 0.09613 | -0.064087 | 0.2243 | 122.9874 | 0.036621 | 123.0011 | 122.937 | 122.8455 | 122.8271 | 122.8043 | -122.9919 | -122.9233 | 122.8775 | 122.9599 | 59.8846 | 59.7839
683.8906 | 123.0743 | -59.9854 | 62.9333 | -0.075684 | 0.00048494 | 0.063213 | 0.0683 | 0.00025629 | -0.002273 | -0.0011899 | -0.094879 | 0.0020208 | 0.06364 | 0.067129 | -0.004845 | 0.005238 | -0.0042127 | -0.20142 | 62.883 | -60.1089 | 62.8876 | -59.9304 | -60.26 | -0.11444 | -0.28839 | 62.8967 | -59.9991 | 62.9242 | -60.0815 | -60.1913 | -59.9808 | -0.1236 | -0.050354 | -0.045777 | 0.054932 | 59.8709 | -0.27466 | 59.9945 | -0.15106 | -0.013732 | -0.036621 | -0.009156 | -0.09613 | 0.004578 | -0.20599 | 0.01831 | -0.19226 | 0.17853 | 122.9965 | -0.082398 | 122.9233 | 122.9919 | 122.8958 | 122.8683 | 122.8821 | -123.0423 | -122.9324 | 122.8729 | 122.9095 | 59.7839 | 59.697
684.8438 | 123.1201 | -59.9625 | 62.9379 | -0.052796 | 0.0011257 | 0.064495 | 0.068727 | 0.0049561 | -0.00099116 | 0.00094633 | -0.082672 | 0.0018072 | 0.064495 | 0.06777 | -0.0050586 | 0.005238 | -0.00036747 | -0.13733 | 62.9013 | -60.0861 | 62.9288 | -59.8526 | -60.2051 | -0.009155 | -0.14191 | 62.8876 | -59.9899 | 63.002 | -60.0128 | -60.1318 | -59.9258 | -0.1236 | -0.036621 | -0.009155 | 0.10986 | 59.9533 | -0.24262 | 60.0769 | -0.11902 | -0.027466 | -0.050354 | 0.064087 | -0.050354 | 0.036621 | -0.16937 | 0.064087 | -0.14191 | 0.23346 | 123.0148 | -0.022888 | 122.9919 | 122.9874 | 122.8775 | 122.8638 | 122.85 | -123.024 | -122.9279 | 122.8912 | 122.9645 | 59.8251 | 59.8206
685.8906 | 123.1247 | -59.9442 | 62.9333 | -0.068054 | 0.0017667 | 0.062145 | 0.067445 | 4.2692e-05 | -0.00013676 | -0.0033261 | -0.088776 | 0.0020208 | 0.063427 | 0.06542 | -0.0042042 | 0.0041698 | -0.0031445 | -0.15564 | 62.8922 | -60.0906 | 62.9929 | -59.8526 | -60.173 | 0 | -0.12817 | 62.9059 | -59.9762 | 63.0066 | -60.0037 | -60.1089 | -59.9258 | -0.14648 | -0.041199 | 0.059509 | 0.091553 | 59.9442 | -0.22888 | 60.0906 | -0.082398 | -0.032043 | -0.027466 | 0.073242 | -0.059509 | 0.018311 | -0.16479 | 0.050354 | -0.13275 | 0.23804 | 123.0835 | -0.027466 | 122.9828 | 122.9828 | 122.8821 | 122.8363 | 122.85 | -123.024 | -122.9095 | 122.937 | 122.9507 | 59.7885 | 59.816
686.8281 | 123.175 | -59.9579 | 62.9242 | -0.1062 | -0.00015586 | 0.062359 | 0.067445 | 4.2692e-05 | -0.0014184 | -0.0026853 | 0.027191 | 0.0022346 | 0.066418 | 0.06072 | -0.003136 | 0.003529 | 5.9726e-05 | -0.20599 | 62.8647 | -60.0952 | 62.9333 | -59.8343 | -60.1959 | -0.009155 | -0.21057 | 62.851 | -59.9854 | 63.0112 | -59.967 | -60.0723 | -59.8801 | -0.13733 | -0.059509 | 0.009156 | 0.1236 | 59.9487 | -0.23804 | 60.0861 | -0.10071 | -0.027466 | -0.073242 | 0.086975 | -0.009155 | 0.07782 | -0.11444 | 0.10529 | -0.086975 | 0.26093 | 123.0286 | 0.018311 | 122.9965 | 122.9599 | 122.8363 | 122.8226 | 122.8088 | -123.0194 | -122.9095 | 122.8912 | 122.9691 | 59.7519 | 59.7473
687.8906 | 123.1476 | -59.967 | 62.9471 | -0.098572 | 0.0017667 | 0.061291 | 0.066163 | 0.0011109 | -0.0018458 | -0.00054907 | -0.036896 | 0.00138 | 0.065563 | 0.066702 | -0.0022816 | 0.0045972 | 0.0013415 | -0.22888 | 62.8784 | -60.1044 | 62.8784 | -59.903 | -60.2737 | -0.10986 | -0.27924 | 62.8601 | -59.9808 | 62.9883 | -60.0266 | -60.1456 | -59.9167 | -0.13733 | -0.068665 | -0.068665 | 0.064087 | 59.8572 | -0.3067 | 59.9945 | -0.16937 | -0.013733 | -0.086976 | 0.041198 | -0.059509 | 0.050354 | -0.17853 | 0.064087 | -0.1648 | 0.20142 | 122.9828 | -0.045776 | 122.9691 | 122.9828 | 122.8409 | 122.8455 | 122.8271 | -123.0515 | -122.9279 | 122.8455 | 122.9553 | 59.7382 | 59.6878
688.8281 | 123.1293 | -59.9304 | 62.9379 | -0.12909 | -0.00015586 | 0.063213 | 0.066163 | -0.00017091 | 7.6842e-05 | -0.0054623 | 0.027191 | 0.003089 | 0.066631 | 0.06072 | -0.0024952 | 0.0043836 | 0.0015551 | -0.19684 | 62.8784 | -60.0586 | 62.9242 | -59.8434 | -60.1868 | -0.013733 | -0.17853 | 62.8738 | -59.9716 | 63.0203 | -59.9579 | -60.0632 | -59.8389 | -0.12817 | -0.059509 | -0.013733 | 0.086975 | 59.9167 | -0.25635 | 60.0449 | -0.12817 | -0.041199 | -0.064087 | 0.082398 | -0.027466 | 0.091553 | -0.13275 | 0.13275 | -0.091552 | 0.21515 | 122.9828 | 0.013733 | 122.9919 | 122.937 | 122.8455 | 122.8088 | 122.8043 | -122.9965 | -122.9095 | 122.8546 | 122.9507 | 59.7336 | 59.7519
689.9062 | 123.1293 | -59.9716 | 62.9425 | -0.52582 | 0.0011257 | 0.061932 | 0.067018 | -0.00081171 | -0.00099116 | -0.0016171 | -0.070465 | 0.0015936 | 0.064495 | 0.06542 | -0.006554 | 0.0045972 | 5.9726e-05 | -0.091553 | 62.8693 | -60.0952 | 62.8693 | -59.8938 | -60.3058 | -0.1236 | -0.26093 | 62.8601 | -59.9991 | 62.9562 | -60.0586 | -60.1547 | -59.9487 | -0.1236 | -0.073242 | -0.073242 | 0.07782 | 59.848 | -0.33417 | 59.9716 | -0.21057 | -0.027465 | -0.082398 | 0.013733 | -0.086975 | 0.022889 | -0.18311 | 0.050354 | -0.15564 | 0.20142 | 122.9645 | -0.05951 | 122.9553 | 122.9645 | 122.8592 | 122.8409 | 122.8317 | -123.0377 | -122.9416 | 122.8409 | 122.9279 | 59.8801 | 59.7107
690.8281 | 123.1796 | -59.9533 | 62.9379 | -0.11383 | 5.7742e-05 | 0.061718 | 0.067018 | -0.0016663 | -0.0016322 | 0.00094633 | 0.018036 | 0.0005256 | 0.065777 | 0.062429 | -0.002068 | 0.0033154 | -0.0022901 | -0.19684 | 62.8601 | -60.054 | 62.9288 | -59.8389 | -60.1776 | -0.018311 | -0.17395 | 62.8601 | -59.9762 | 63.0249 | -59.9579 | -60.0494 | -59.8709 | -0.10071 | -0.07782 | -0.009155 | 0.11444 | 59.935 | -0.2243 | 60.0357 | -0.1236 | -0.022888 | -0.07782 | 0.086975 | -0.004578 | 0.082397 | -0.09613 | 0.10529 | -0.073242 | 0.21515 | 122.9828 | 0.01831 | 123.0011 | 122.9141 | 122.8363 | 122.8134 | 122.8134 | -122.9919 | -122.9141 | 122.8821 | 122.9782 | 59.7565 | 59.7794
691.8906 | 123.2025 | -59.935 | 62.9288 | -0.15961 | 0.00069854 | 0.065777 | 0.068086 | -0.00038451 | -0.0012048 | 0.00073273 | -0.027741 | 0.0007392 | 0.068127 | 0.059866 | -0.0056994 | 0.0028882 | -0.0016493 | -0.13733 | 62.8235 | -60.0586 | 62.9791 | -59.7885 | -60.1959 | -0.004578 | -0.13275 | 62.8418 | -59.9945 | 63.0478 | -59.9396 | -60.0494 | -59.8434 | -0.1236 | -0.10529 | 0.050354 | 0.14648 | 59.9304 | -0.26093 | 60.054 | -0.13733 | -0.059509 | -0.086975 | 0.11902 | -0.004577 | 0.091553 | -0.11444 | 0.15106 | -0.054931 | 0.27008 | 123.0377 | 0.054932 | 123.0423 | 122.8821 | 122.8363 | 122.7585 | 122.7768 | -122.9874 | -122.9233 | 122.9141 | 122.9828 | 59.7977 | 59.8022
692.8281 | 123.1888 | -59.9533 | 62.9059 | -0.12146 | 0.0017667 | 0.063641 | 0.068086 | 0.0030335 | 0.00093144 | -0.0016171 | -0.0063781 | 0.00138 | 0.066418 | 0.062429 | -0.0063404 | 0.0028882 | -0.0014355 | -0.17853 | 62.8464 | -60.0677 | 62.97 | -59.7885 | -60.173 | -0.022888 | -0.14191 | 62.8281 | -59.967 | 63.0478 | -59.9716 | -60.0632 | -59.8846 | -0.11444 | -0.059509 | 0.064087 | 0.16479 | 59.9304 | -0.21973 | 60.0449 | -0.10529 | -0.013733 | -0.07782 | 0.14191 | -0.018311 | 0.068664 | -0.10986 | 0.082397 | -0.09613 | 0.27924 | 123.0377 | -0.004578 | 123.0148 | 122.9141 | 122.7951 | 122.7997 | 122.7814 | -122.9736 | -122.8729 | 122.9233 | 123.0011 | 59.7748 | 59.8114
693.8281 | 123.1476 | -59.9625 | 62.9242 | -0.13672 | 0.0026211 | 0.062359 | 0.067445 | 0.0019653 | -0.00035036 | -0.0020443 | 0.0058289 | 9.8198e-05 | 0.065563 | 0.05773 | -0.009972 | 0.0024608 | -0.00036747 | -0.19684 | 62.8693 | -60.0494 | 62.9196 | -59.8434 | -60.1959 | -0.018311 | -0.16937 | 62.8738 | -59.9899 | 63.0981 | -60.0632 | -60.0357 | -59.8892 | -0.086975 | -0.054931 | -0.004577 | 0.11902 | 59.9442 | -0.23346 | 60.0311 | -0.14648 | -0.027466 | -0.050354 | 0.17395 | -0.10071 | 0.073242 | -0.073243 | 0.10071 | -0.045777 | 0.20599 | 122.9691 | -0.073242 | 123.0881 | 122.9187 | 122.8638 | 122.8317 | 122.8363 | -122.9736 | -122.9141 | 122.8821 | 123.0606 | 59.7656 | 59.7931
694.9062 | 123.143 | -59.9396 | 62.9883 | 0.00824 | 0.0021939 | 0.061504 | 0.068086 | -0.00059811 | -0.0024866 | 9.193e-05 | -0.067413 | 0.0022346 | 0.066845 | 0.067556 | -0.0061268 | 0.0054516 | -0.0031445 | -0.12817 | 62.9288 | -60.0494 | 62.9379 | -59.8801 | -60.1776 | 0.032043 | -0.13733 | 62.9105 | -59.9716 | 63.0112 | -59.9716 | -60.0952 | -59.8984 | -0.10986 | -0.059509 | -0.050354 | 0.059509 | 59.9716 | -0.23804 | 60.0815 | -0.12817 | -0.032044 | -0.07782 | 0.022888 | -0.032044 | 0.041199 | -0.15564 | 0.073243 | -0.1236 | 0.16937 | 122.9874 | 0 | 122.9828 | 122.9782 | 122.8821 | 122.8683 | 122.85 | -123.0377 | -122.9599 | 122.8775 | 122.9507 | 59.8114 | 59.8022
695.8281 | 123.1659 | -59.9533 | 62.9242 | -0.075684 | -0.0010105 | 0.064281 | 0.067018 | -0.00059811 | -0.0024866 | -0.0046079 | -0.0033265 | 0.0009528 | 0.062359 | 0.057516 | -0.0054858 | 0.0022472 | -0.0057081 | -0.20142 | 62.851 | -60.0632 | 62.9196 | -59.8297 | -60.1685 | -0.004578 | -0.086975 | 62.8922 | -59.9396 | 63.0386 | -59.9716 | -60.054 | -59.8938 | -0.10986 | -0.073242 | -0.004577 | 0.1236 | 59.9487 | -0.21515 | 60.0586 | -0.10529 | 0.013733 | -0.032043 | 0.11444 | -0.018311 | 0.059509 | -0.10071 | 0.045776 | -0.11444 | 0.23346 | 122.9828 | -0.032044 | 122.9782 | 122.9141 | 122.8317 | 122.8043 | 122.8455 | -122.9874 | -122.8638 | 122.8729 | 122.9919 | 59.7519 | 59.8663
696.8906 | 123.1476 | -59.967 | 62.9654 | -0.068054 | 0.0024075 | 0.063641 | 0.068086 | -0.0027343 | -0.00013676 | 0.0015871 | -0.06131 | 0.0022346 | 0.063213 | 0.063711 | -0.0054858 | 0.0050244 | -0.0010083 | -0.15106 | 62.883 | -60.0586 | 62.915 | -59.9854 | -60.1089 | 0.027466 | -0.12817 | 62.9105 | -59.9808 | 63.0112 | -59.9854 | -60.0998 | -59.9167 | -0.091553 | -0.082397 | -0.050354 | -0.018311 | 59.9945 | -0.14191 | 60.0861 | -0.050354 | -0.013733 | -0.054932 | 0.045776 | -0.018311 | 0.050354 | -0.13275 | 0.064087 | -0.11902 | 0.073242 | 122.9736 | -0.004578 | 122.9919 | 122.9416 | 122.8912 | 122.85 | 122.8775 | -123.024 | -122.9462 | 122.8821 | 122.9782 | 59.816 | 59.8389
697.8281 | 123.1979 | -59.9579 | 62.9242 | -0.15198 | 0.0013393 | 0.061291 | 0.065736 | 0.00046989 | -0.0014184 | 0.00094633 | 0.063812 | 0.0015936 | 0.063213 | 0.059011 | -0.0039906 | 0.0024608 | -0.00015387 | -0.18768 | 62.8601 | -60.0586 | 62.9333 | -59.8343 | -60.1776 | 0.045776 | -0.21057 | 62.8738 | -59.9808 | 63.0203 | -59.9579 | -60.0586 | -59.8892 | -0.10071 | -0.064087 | 0.009156 | 0.1236 | 60.0037 | -0.21973 | 60.1044 | -0.11902 | -0.022888 | -0.050354 | 0.096131 | 0 | 0.068665 | -0.10071 | 0.091553 | -0.07782 | 0.2243 | 122.9919 | 0.022888 | 123.0011 | 122.9187 | 122.8546 | 122.818 | 122.8317 | -122.9828 | -122.905 | 122.8912 | 122.9782 | 59.7702 | 59.7473
698.8906 | 123.0972 | -59.967 | 62.9791 | -0.1062 | 5.7742e-05 | 0.062786 | 0.066804 | 0.0064515 | 0.00029044 | -0.00097627 | -0.082672 | 0.0035162 | 0.064495 | 0.06307 | -0.0029224 | 0.0037426 | 5.9726e-05 | -0.17395 | 62.8922 | -60.0586 | 62.915 | -59.8572 | -60.2509 | -0.054932 | -0.19226 | 62.9288 | -59.9854 | 62.97 | -60.0357 | -60.1547 | -59.9625 | -0.091553 | -0.086975 | -0.064087 | 0.10986 | 59.9121 | -0.28381 | 60.0037 | -0.19226 | -0.018311 | -0.050354 | -0.009155 | -0.068665 | 0.004578 | -0.18768 | 0.022889 | -0.16937 | 0.20142 | 122.9736 | -0.050354 | 122.9553 | 122.9507 | 122.9141 | 122.8592 | 122.8958 | -123.0377 | -122.9645 | 122.8821 | 122.937 | 59.7931 | 59.7748
699.8438 | 123.175 | -59.9533 | 62.9059 | -0.13672 | 0.0026211 | 0.061504 | 0.064882 | -0.0010253 | -0.00013676 | -0.0020443 | -0.021637 | 0.00138 | 0.066845 | 0.064779 | -0.0039906 | 0.0033154 | -0.00036747 | -0.18768 | 62.8372 | -60.0449 | 62.9791 | -59.7885 | -60.1776 | -0.018311 | -0.16479 | 62.8281 | -59.9899 | 63.0386 | -59.9579 | -60.0677 | -59.903 | -0.091553 | -0.068665 | 0.073242 | 0.16479 | 59.935 | -0.2243 | 60.0266 | -0.13275 | -0.036621 | -0.07782 | 0.13275 | -0.004578 | 0.050354 | -0.11444 | 0.086975 | -0.07782 | 0.25635 | 123.024 | 0.032043 | 123.0286 | 122.8821 | 122.818 | 122.7905 | 122.7814 | -122.9507 | -122.8958 | 122.9324 | 122.9919 | 59.7656 | 59.7885
700.8906 | 123.0881 | -59.9716 | 62.9608 | -0.075684 | 0.0015529 | 0.064281 | 0.067232 | 0.0051697 | -0.0014184 | 0.0018009 | -0.088776 | 0.0037298 | 0.064709 | 0.065634 | -0.0044178 | 0.003529 | -0.00058107 | -0.21515 | 62.883 | -60.1044 | 62.8693 | -59.9533 | -60.3058 | -0.1236 | -0.32044 | 62.8922 | -60.0037 | 62.9654 | -60.0769 | -60.1776 | -59.967 | -0.13275 | -0.077819 | -0.091552 | 0.018311 | 59.848 | -0.33417 | 59.9808 | -0.20142 | -0.032043 | -0.068664 | 0.004578 | -0.10529 | 0.004578 | -0.20599 | 0.036621 | -0.17395 | 0.15106 | 122.9736 | -0.073242 | 122.9691 | 122.9874 | 122.8958 | 122.8546 | 122.8638 | -123.0652 | -122.9645 | 122.8409 | 122.937 | 59.7565 | 59.6512
701.8281 | 123.1842 | -59.967 | 62.9471 | -0.075684 | -0.0010105 | 0.06065 | 0.068513 | 0.00068369 | -0.0016322 | 9.193e-05 | -0.0033265 | 0.0009528 | 0.065349 | 0.061575 | -0.0035632 | 0.0050244 | 0.00027333 | -0.20142 | 62.8418 | -60.0403 | 62.9517 | -59.816 | -60.1868 | -0.032043 | -0.2243 | 62.8372 | -59.9991 | 63.0112 | -59.9716 | -60.0723 | -59.8892 | -0.073242 | -0.10529 | 0.004577 | 0.15106 | 59.935 | -0.21973 | 60.0082 | -0.14648 | -0.032043 | -0.10986 | 0.064086 | -0.004578 | 0.07782 | -0.10529 | 0.10986 | -0.073243 | 0.2243 | 122.9919 | 0.027465 | 123.0103 | 122.8821 | 122.8363 | 122.8088 | 122.8043 | -122.9874 | -122.9462 | 122.9187 | 122.9782 | 59.7656 | 59.7427
702.8906 | 123.1338 | -59.9625 | 62.9654 | -0.083313 | 0.00069854 | 0.060863 | 0.068086 | -0.0010253 | -0.0016322 | 0.00030553 | -0.042999 | 0.0033026 | 0.06364 | 0.060934 | -0.0050586 | 0.0048108 | -0.0046399 | -0.14648 | 62.9196 | -60.054 | 62.9425 | -59.8343 | -60.1685 | 0.032043 | -0.10986 | 62.9013 | -59.967 | 63.0295 | -59.9625 | -60.0769 | -59.903 | -0.091553 | -0.045776 | -0.022888 | 0.12817 | 59.9945 | -0.20599 | 60.0861 | -0.11444 | -0.004578 | -0.064087 | 0.064087 | 0 | 0.059509 | -0.11444 | 0.064087 | -0.10986 | 0.21973 | 122.9965 | 0.004578 | 122.9965 | 122.9736 | 122.8683 | 122.8821 | 122.8638 | -123.0194 | -122.9324 | 122.905 | 122.9919 | 59.816 | 59.8526
703.8281 | 123.2162 | -59.9533 | 62.9059 | -0.1062 | 0.0024075 | 0.064068 | 0.065736 | 0.0030335 | -0.00099116 | 9.193e-05 | -0.052155 | 0.0003118 | 0.067913 | 0.065847 | -0.0029224 | 0.0054516 | 0.0028369 | -0.16937 | 62.8464 | -60.0632 | 62.9562 | -59.7794 | -60.1913 | -0.022888 | -0.17395 | 62.8235 | -60.0037 | 63.0661 | -59.9258 | -60.0403 | -59.848 | -0.10986 | -0.059509 | 0.050354 | 0.17395 | 59.9304 | -0.23804 | 60.0403 | -0.12817 | -0.050354 | -0.082398 | 0.16022 | 0.027466 | 0.10529 | -0.086975 | 0.15564 | -0.036621 | 0.28381 | 123.0194 | 0.07782 | 123.0698 | 122.9095 | 122.8271 | 122.7997 | 122.7768 | -122.9691 | -122.9095 | 122.9095 | 123.0194 | 59.7839 | 59.7794
704.9062 | 123.0789 | -59.9579 | 62.97 | -0.075684 | 0.0015529 | 0.061504 | 0.064882 | 0.0011109 | -0.00099116 | -0.0046079 | -0.0063781 | 0.0015936 | 0.065136 | 0.065847 | -0.004845 | 0.0020336 | 0.00091433 | -0.1236 | 62.915 | -60.022 | 62.9196 | -59.8114 | -60.1685 | 0.050354 | -0.11902 | 62.9105 | -59.9762 | 62.97 | -59.9899 | -60.0952 | -59.9533 | -0.064087 | -0.054932 | -0.050354 | 0.14649 | 60.0082 | -0.21057 | 60.0723 | -0.14648 | -0.01831 | -0.05951 | 0 | -0.032043 | 0.004578 | -0.13733 | 0.022888 | -0.11902 | 0.21057 | 122.9416 | -0.013733 | 122.9462 | 122.937 | 122.8867 | 122.8729 | 122.8683 | -122.9919 | -122.9462 | 122.8775 | 122.9279 | 59.8343 | 59.8389
705.8281 | 123.2346 | -59.935 | 62.9105 | -0.090943 | 0.00069854 | 0.061932 | 0.067018 | -0.0040161 | -0.00099116 | -0.0016171 | -0.021637 | 0.0024482 | 0.063854 | 0.060507 | -0.0054858 | 0.0024608 | -0.00058107 | -0.3067 | 62.764 | -60.0906 | 62.9654 | -59.7702 | -60.1547 | -0.027466 | -0.15564 | 62.8326 | -59.9625 | 63.0707 | -59.9396 | -60.0403 | -59.8709 | -0.15564 | -0.14648 | 0.054932 | 0.16479 | 59.9075 | -0.21973 | 60.0632 | -0.064087 | -0.027465 | -0.077819 | 0.16022 | -0.004577 | 0.064087 | -0.10529 | 0.091552 | -0.07782 | 0.32043 | 123.056 | 0.022888 | 123.0331 | 122.8546 | 122.7951 | 122.699 | 122.7676 | -123.0011 | -122.8729 | 122.9004 | 123.0057 | 59.6283 | 59.7794
706.8906 | 123.0469 | -59.9762 | 62.9517 | -0.045166 | 0.0011257 | 0.061932 | 0.068086 | -0.0035889 | -0.0024866 | -0.0035397 | -0.088776 | 0.0020208 | 0.066631 | 0.064565 | -0.0052722 | 0.0058788 | -0.0018629 | -0.16022 | 62.9059 | -60.0723 | 62.9608 | -59.8251 | -60.1868 | 0.027466 | -0.10986 | 62.9013 | -59.967 | 63.0157 | -59.9625 | -60.0586 | -59.9487 | -0.096131 | -0.045776 | 0.009155 | 0.15106 | 60.0037 | -0.21057 | 60.0998 | -0.11444 | 0.009155 | -0.050354 | 0.064087 | 0.013733 | 0.027466 | -0.082398 | 0.018311 | -0.091553 | 0.24719 | 123.0331 | 0.004578 | 122.9828 | 122.9782 | 122.8683 | 122.8821 | 122.8775 | -123.024 | -122.9187 | 122.937 | 122.9919 | 59.816 | 59.8663
707.8281 | 123.0881 | -59.9854 | 62.9425 | -0.045166 | 0.0034757 | 0.064281 | 0.066591 | 0.0049561 | -0.0018458 | -0.0018307 | -0.2139 | 0.003089 | 0.063427 | 0.068624 | -0.0042042 | 0.0045972 | -0.0022901 | -0.23346 | 62.883 | -60.1227 | 62.8418 | -59.935 | -60.2921 | -0.11444 | -0.5127 | 62.8555 | -60.0311 | 62.9379 | -60.0174 | -60.1593 | -59.9487 | -0.13733 | -0.059509 | -0.10071 | 0.050354 | 59.8709 | -0.3067 | 60.0082 | -0.16937 | -0.045776 | -0.086975 | -0.004578 | -0.032043 | 0.036622 | -0.17395 | 0.082398 | -0.12817 | 0.18768 | 122.9645 | 0.013733 | 122.9691 | 123.0057 | 122.8867 | 122.8683 | 122.8409 | -123.0652 | -122.9736 | 122.8271 | 122.9233 | 59.7519 | 59.4727
708.8906 | 123.2208 | -59.9304 | 62.9425 | -0.098572 | 0.0011257 | 0.061932 | 0.065309 | 0.00025629 | -0.00013676 | -0.0024717 | 0.033295 | 0.0018072 | 0.067699 | 0.062429 | -0.0037768 | 0.0026746 | 0.0013415 | -0.17853 | 62.8601 | -60.0494 | 62.9608 | -59.8114 | -60.141 | 0.036621 | -0.11902 | 62.8464 | -59.9808 | 63.0432 | -59.9213 | -60.022 | -59.8434 | -0.11902 | -0.082398 | 0.01831 | 0.11902 | 59.967 | -0.21057 | 60.0861 | -0.091553 | -0.050354 | -0.09613 | 0.10071 | 0.009155 | 0.086975 | -0.091553 | 0.13733 | -0.041199 | 0.23804 | 123.0103 | 0.059509 | 123.024 | 122.9095 | 122.8271 | 122.7905 | 122.7768 | -122.9919 | -122.9233 | 122.8912 | 122.9736 | 59.7519 | 59.8114
709.8438 | 123.175 | -59.9442 | 62.9517 | -0.13672 | 0.0028347 | 0.061504 | 0.064882 | 0.0019653 | -0.0020594 | -0.00097627 | -0.0033265 | 0.0011664 | 0.064709 | 0.062429 | -0.0039906 | 0.0045972 | -0.00079467 | -0.21515 | 62.8876 | -60.0632 | 62.9196 | -59.8343 | -60.1913 | -0.022888 | -0.19226 | 62.8601 | -59.9625 | 63.0203 | -59.9625 | -60.0586 | -59.8892 | -0.11902 | -0.064087 | -0.032043 | 0.10986 | 59.9213 | -0.24719 | 60.0403 | -0.12817 | -0.01831 | -0.091553 | 0.068665 | -0.01831 | 0.054932 | -0.11444 | 0.073242 | -0.096131 | 0.22888 | 122.9828 | 0 | 122.9828 | 122.9507 | 122.8226 | 122.8317 | 122.8043 | -123.0148 | -122.9141 | 122.8638 | 122.9645 | 59.729 | 59.7519
710.9062 | 123.111 | -59.967 | 62.9745 | -0.068054 | 0.00048494 | 0.063854 | 0.0683 | -0.00038451 | -0.0014184 | -0.00076267 | -0.085724 | 0.0024482 | 0.067058 | 0.061575 | -0.0054858 | 0.0020336 | -0.0029309 | -0.20142 | 62.8372 | -60.0815 | 62.9288 | -59.8389 | -60.2005 | 0.004578 | -0.14191 | 62.915 | -59.967 | 63.002 | -59.9991 | -60.1227 | -59.9213 | -0.11444 | -0.13733 | -0.045776 | 0.12817 | 59.9716 | -0.23346 | 60.0861 | -0.11902 | 0 | -0.059509 | 0.027466 | -0.032043 | 0.045776 | -0.15564 | 0.045776 | -0.15564 | 0.24262 | 123.0103 | -0.032043 | 122.9691 | 122.9187 | 122.8821 | 122.8043 | 122.8821 | -123.056 | -122.9416 | 122.8958 | 122.9691 | 59.7656 | 59.8251
711.8281 | 123.0606 | -59.9762 | 62.9471 | -0.12146 | 0.0024075 | 0.064281 | 0.066804 | -0.0020935 | -0.00077756 | -0.0011899 | -0.073517 | 0.0005256 | 0.065349 | 0.068197 | -0.0046314 | 0.0033154 | -0.0022901 | -0.20142 | 62.9013 | -60.0906 | 62.8922 | -59.8892 | -60.2646 | -0.064087 | -0.26093 | 62.8967 | -60.0082 | 62.9288 | -60.0632 | -60.173 | -59.9716 | -0.11444 | -0.045777 | -0.054932 | 0.086975 | 59.9121 | -0.28839 | 60.0266 | -0.17395 | -0.032044 | -0.050354 | -0.018311 | -0.086975 | 0.004577 | -0.19684 | 0.036621 | -0.16479 | 0.20142 | 122.9828 | -0.054931 | 122.937 | 122.9919 | 122.905 | 122.8775 | 122.8729 | -123.0377 | -122.9553 | 122.8683 | 122.905 | 59.7748 | 59.7153
712.8906 | 123.111 | -59.935 | 62.9745 | -0.037537 | 0.0015529 | 0.061932 | 0.066163 | -0.00081171 | -0.00056396 | -0.0022581 | -0.0063781 | 0.0043708 | 0.066845 | 0.06777 | -0.0039906 | 0.0060924 | 0.0019823 | -0.17395 | 62.9333 | -60.054 | 62.8967 | -59.8709 | -60.1868 | 0.013733 | 0.027466 | 62.97 | -59.9442 | 62.9883 | -60.022 | -60.1593 | -59.935 | -0.11902 | -0.041198 | -0.077819 | 0.064087 | 59.9487 | -0.25177 | 60.0677 | -0.13275 | -0.009155 | -0.004577 | 0.013733 | -0.086975 | 0 | -0.2243 | 0.009155 | -0.21515 | 0.1831 | 122.9507 | -0.07782 | 122.9324 | 122.9874 | 122.9141 | 122.8683 | 122.905 | -123.0286 | -122.9187 | 122.8317 | 122.9233 | 59.761 | 59.9625
713.8281 | 123.1338 | -59.9579 | 62.9791 | -0.037537 | 0.0026211 | 0.062359 | 0.066804 | 0.0015381 | -0.00013676 | -0.0011899 | -0.073517 | 0.0015936 | 0.067486 | 0.063497 | -0.0033496 | 0.0043836 | -0.0018629 | -0.1831 | 62.9105 | -60.0861 | 62.9425 | -59.8343 | -60.2051 | 0.004578 | -0.13733 | 62.9059 | -59.967 | 63.002 | -59.9716 | -60.1135 | -59.9075 | -0.12817 | -0.068665 | -0.036621 | 0.1236 | 59.9625 | -0.24719 | 60.0906 | -0.11902 | -0.009155 | -0.073242 | 0.022888 | -0.013733 | 0.050354 | -0.15564 | 0.059509 | -0.14648 | 0.25177 | 123.0286 | -0.004578 | 122.9691 | 122.9965 | 122.8729 | 122.8683 | 122.8638 | -123.0652 | -122.9462 | 122.9004 | 122.9599 | 59.7748 | 59.8206
714.8906 | 123.1064 | -59.9716 | 62.9562 | -0.083313 | 0.00069854 | 0.060009 | 0.068727 | 4.2692e-05 | 0.00029044 | 0.00051913 | -0.052155 | 0.0035162 | 0.066845 | 0.068838 | -0.0046314 | 0.0033154 | -0.0018629 | -0.16479 | 62.8922 | -60.0815 | 62.9288 | -59.848 | -60.2005 | -0.018311 | -0.17395 | 62.8967 | -59.9762 | 62.9654 | -60.0128 | -60.1181 | -59.9258 | -0.10986 | -0.064087 | -0.027466 | 0.1236 | 59.9533 | -0.22888 | 60.0632 | -0.11902 | -0.004577 | -0.059509 | 0.009155 | -0.041198 | 0.045777 | -0.14648 | 0.050354 | -0.14191 | 0.23346 | 123.0103 | -0.036621 | 122.9416 | 122.9736 | 122.8729 | 122.8638 | 122.8683 | -123.0377 | -122.9324 | 122.9004 | 122.937 | 59.8068 | 59.7977
715.8281 | 123.1201 | -59.9442 | 62.9562 | -0.060425 | 0.0021939 | 0.061718 | 0.066591 | -0.00059811 | -0.00056396 | 0.0011599 | -0.027741 | 0.003089 | 0.065777 | 0.067343 | -0.0029224 | 0.0045972 | 0.0019823 | -0.15564 | 62.915 | -60.0769 | 62.9379 | -59.8389 | -60.2692 | -0.12817 | -0.15106 | 62.8876 | -59.9854 | 63.0157 | -59.9808 | -60.0952 | -59.8984 | -0.13275 | -0.041199 | -0.018311 | 0.10529 | 59.816 | -0.32501 | 59.9487 | -0.19226 | -0.041199 | -0.068665 | 0.059509 | -0.036621 | 0.045777 | -0.15106 | 0.086976 | -0.10986 | 0.23804 | 123.0148 | 0.004578 | 123.0011 | 122.9919 | 122.8729 | 122.8592 | 122.8317 | -123.0331 | -122.9416 | 122.8821 | 122.9599 | 59.7885 | 59.7931
716.8906 | 123.2025 | -59.9533 | 62.9196 | -0.15198 | 0.0017667 | 0.063 | 0.067659 | 0.0017517 | 0.001145 | 0.0011599 | -0.0094299 | 9.8198e-05 | 0.066418 | 0.060934 | -0.0054858 | 0.005238 | 0.00027333 | -0.24261 | 62.8647 | -60.0952 | 62.9013 | -59.848 | -60.2325 | -0.07782 | -0.20142 | 62.8372 | -59.9899 | 63.0615 | -59.9762 | -60.054 | -59.8389 | -0.14191 | -0.054932 | -0.018311 | 0.10529 | 59.8755 | -0.27924 | 60.0174 | -0.13733 | -0.036621 | -0.082398 | 0.14191 | -0.022888 | 0.11444 | -0.10071 | 0.15106 | -0.064087 | 0.24719 | 122.9965 | 0.013733 | 123.0515 | 122.9599 | 122.8271 | 122.818 | 122.7905 | -123.0148 | -122.9095 | 122.8546 | 123.0148 | 59.7107 | 59.7519
717.8281 | 123.1338 | -59.9625 | 62.97 | -0.090943 | 0.0034757 | 0.061932 | 0.06595 | 0.0041015 | -0.0012048 | 0.0013735 | -0.058258 | 0.003089 | 0.065777 | 0.060079 | -0.0046314 | 0.005238 | 5.9726e-05 | -0.15106 | 62.8922 | -60.0586 | 62.9379 | -59.8251 | -60.2005 | 0.041199 | -0.1236 | 62.9105 | -59.9762 | 63.0569 | -59.9945 | -60.0632 | -59.8572 | -0.096131 | -0.07782 | -0.032044 | 0.13733 | 60.0037 | -0.23804 | 60.0998 | -0.14191 | -0.013733 | -0.05951 | 0.086975 | -0.032044 | 0.10529 | -0.10071 | 0.11902 | -0.086975 | 0.23346 | 122.9965 | -0.018311 | 123.0331 | 122.9507 | 122.8867 | 122.8546 | 122.8729 | -123.0286 | -122.9462 | 122.9004 | 123.0194 | 59.8114 | 59.8389
718.8906 | 123.2025 | -59.9258 | 62.8967 | -0.083313 | 0.0011257 | 0.064281 | 0.06595 | 0.0017517 | -0.00077756 | -0.0024717 | 0.011932 | 0.0015936 | 0.065136 | 0.067556 | -0.0061268 | 0.0031018 | -0.0018629 | -0.17395 | 62.8281 | -60.0311 | 62.9608 | -59.7748 | -60.1639 | -0.013733 | -0.15106 | 62.8372 | -59.9762 | 63.0524 | -59.935 | -60.0311 | -59.8526 | -0.10529 | -0.068665 | 0.064086 | 0.15106 | 59.9121 | -0.23804 | 60.0174 | -0.13275 | -0.050354 | -0.05951 | 0.15564 | -0.009156 | 0.073242 | -0.10529 | 0.1236 | -0.054932 | 0.25635 | 122.9919 | 0.041198 | 123.0286 | 122.8592 | 122.8134 | 122.7539 | 122.7631 | -122.9279 | -122.8729 | 122.8867 | 122.9782 | 59.7519 | 59.7748
719.8438 | 123.1338 | -59.967 | 62.9242 | -0.1062 | 0.0026211 | 0.062359 | 0.068086 | 0.0021789 | -0.00099116 | 0.00094633 | -0.046051 | 0.00138 | 0.067486 | 0.06307 | -0.0042042 | 0.003529 | -0.0033581 | -0.21515 | 62.9196 | -60.0906 | 62.851 | -59.9167 | -60.2783 | -0.09613 | -0.27466 | 62.8738 | -59.9854 | 62.97 | -60.0357 | -60.1456 | -59.935 | -0.1236 | -0.004577 | -0.073242 | 0.050354 | 59.8709 | -0.31128 | 59.9945 | -0.18768 | -0.018311 | -0.050354 | 0.045777 | -0.068665 | 0.032043 | -0.17853 | 0.050354 | -0.16022 | 0.17395 | 122.9416 | -0.050354 | 122.9553 | 123.0103 | 122.8592 | 122.8867 | 122.8409 | -123.0148 | -122.9095 | 122.818 | 122.937 | 59.7519 | 59.6924
720.8906 | 123.2117 | -59.9442 | 62.8967 | -0.15198 | -0.0010105 | 0.063 | 0.066377 | 0.0023925 | 0.00093144 | -0.0024717 | -0.046051 | 0.0003118 | 0.064281 | 0.067129 | -0.0071948 | 0.0033154 | 0.0019823 | -0.23346 | 62.8326 | -60.0769 | 62.9471 | -59.8709 | -60.1913 | -0.013733 | -0.15106 | 62.851 | -59.9716 | 63.0569 | -59.9442 | -60.0266 | -59.8343 | -0.13275 | -0.064087 | 0.050354 | 0.073242 | 59.9304 | -0.24719 | 60.0632 | -0.11444 | -0.027466 | -0.045777 | 0.16022 | 0 | 0.10986 | -0.082397 | 0.13733 | -0.054931 | 0.20599 | 123.024 | 0.027466 | 123.0286 | 122.9095 | 122.8226 | 122.7768 | 122.7951 | -122.9736 | -122.8683 | 122.8912 | 123.0011 | 59.7107 | 59.7931
721.8281 | 123.0927 | -59.9716 | 62.9929 | -0.068054 | 0.00069854 | 0.062572 | 0.065736 | 0.00025629 | 0.00050424 | -0.0011899 | 0.014984 | 0.0024482 | 0.066204 | 0.05837 | -0.0037768 | 0.0041698 | 0.00027333 | -0.17853 | 62.9379 | -60.0723 | 62.8876 | -59.8801 | -60.1822 | 0.032043 | -0.15106 | 62.9242 | -59.9716 | 62.8555 | -59.9808 | -60.1456 | -59.9442 | -0.10071 | -0.054932 | -0.10529 | 0.091553 | 60.0037 | -0.21057 | 60.1044 | -0.10986 | 0 | -0.068665 | -0.13733 | -0.009155 | 0.027466 | -0.17395 | 0.027466 | -0.17395 | 0.19226 | 122.9599 | -0.009155 | 122.8271 | 123.0103 | 122.8958 | 122.9095 | 122.8958 | -123.0652 | -122.9645 | 122.8592 | 122.8271 | 59.7931 | 59.8206
722.8906 | 123.2391 | -59.9808 | 62.9105 | -0.1062 | 0.0015529 | 0.063641 | 0.067872 | 0.0017517 | -0.0024866 | 0.0015871 | -0.024689 | 0.0026618 | 0.064495 | 0.066061 | -0.0052722 | 0.0060924 | -0.0020765 | -0.25635 | 62.851 | -60.0769 | 62.8967 | -59.8709 | -60.2325 | -0.073242 | -0.22888 | 62.8372 | -59.9854 | 63.0386 | -59.9854 | -60.0723 | -59.8526 | -0.09613 | -0.059509 | -0.013732 | 0.10986 | 59.9075 | -0.25177 | 60.0037 | -0.15564 | -0.004578 | -0.073242 | 0.12817 | -0.004578 | 0.12817 | -0.091553 | 0.13275 | -0.086975 | 0.20599 | 122.9736 | 0 | 123.024 | 122.9279 | 122.8226 | 122.8317 | 122.818 | -122.9874 | -122.8958 | 122.8775 | 123.0194 | 59.7244 | 59.7519
723.8281 | 123.2025 | -59.903 | 62.9471 | -0.060425 | 0.00027134 | 0.061077 | 0.067445 | -0.00017091 | 7.6842e-05 | -0.0011899 | 0.033295 | 0.0011664 | 0.065563 | 0.058798 | -0.0056994 | 0.0016064 | -0.0012219 | -0.10986 | 62.8876 | -60.0128 | 62.9379 | -59.404 | -59.9899 | -0.10986 | -0.091553 | 62.8647 | -59.9533 | 63.0798 | -59.8846 | -59.9854 | -59.8114 | -0.10986 | -0.05951 | -0.009156 | 0.49896 | 59.7931 | -0.086975 | 59.903 | 0.022888 | -0.050354 | -0.082398 | 0.13275 | 0.01831 | 0.091553 | -0.082398 | 0.14191 | -0.032044 | 0.60882 | 122.9507 | 0.068664 | 123.0331 | 122.9004 | 122.818 | 122.7905 | 122.7676 | -122.9599 | -122.9004 | 122.8409 | 122.9828 | 59.7931 | 59.8114
724.9062 | 123.2529 | -59.9258 | 62.9471 | -0.068054 | 0.00091214 | 0.063427 | 0.066163 | 0.0013245 | -0.0016322 | -0.0046079 | 0.027191 | 0.0009528 | 0.06364 | 0.064993 | -0.0059132 | 0.0058788 | 0.0041187 | -0.15564 | 62.8693 | -60.0266 | 62.9745 | -59.7794 | -60.1181 | 0.086975 | -0.07782 | 62.8647 | -59.9442 | 63.0707 | -59.8801 | -60.022 | -59.8206 | -0.10071 | -0.07782 | 0.027465 | 0.14648 | 60.0128 | -0.19226 | 60.1135 | -0.091553 | -0.018311 | -0.082398 | 0.1236 | 0.045776 | 0.10529 | -0.096131 | 0.1236 | -0.07782 | 0.24719 | 123.0011 | 0.064087 | 123.0148 | 122.8958 | 122.8088 | 122.7951 | 122.7905 | -122.9736 | -122.8912 | 122.9004 | 122.9965 | 59.7702 | 59.848
725.8281 | 123.2025 | -59.9304 | 62.9471 | -0.083313 | 0.0011257 | 0.062145 | 0.065523 | 0.0047425 | -0.0024866 | -0.00033547 | 0.021088 | -0.0001154 | 0.067058 | 0.059866 | -0.0042042 | 0.0037426 | 0.0021961 | -0.13275 | 62.8876 | -60.0449 | 63.0112 | -59.7427 | -60.0906 | 0.10986 | -0.041199 | 62.8967 | -59.9533 | 63.0661 | -59.8984 | -60.0082 | -59.8434 | -0.11444 | -0.05951 | 0.064086 | 0.18768 | 60.0403 | -0.16022 | 60.1547 | -0.045776 | -0.022888 | -0.050354 | 0.11902 | 0.032044 | 0.086975 | -0.07782 | 0.10986 | -0.054932 | 0.30212 | 123.056 | 0.054932 | 123.0194 | 122.9324 | 122.85 | 122.818 | 122.8271 | -122.9919 | -122.9004 | 122.9416 | 122.9965 | 59.7977 | 59.8892
726.8906 | 123.1888 | -59.9625 | 62.9196 | -0.11383 | 0.0021939 | 0.063641 | 0.068086 | -0.0023071 | -0.0029138 | -0.00076267 | -0.024689 | 0.0011664 | 0.06364 | 0.065634 | -0.004845 | 0.0028882 | 0.00027333 | -0.16479 | 62.8326 | -60.0632 | 62.9883 | -59.8022 | -60.1822 | -0.013733 | -0.14648 | 62.8418 | -59.9716 | 63.0341 | -59.935 | -60.0449 | -59.8618 | -0.10071 | -0.086975 | 0.068664 | 0.16022 | 59.9487 | -0.21973 | 60.0494 | -0.11902 | -0.009156 | -0.07782 | 0.11444 | 0.027465 | 0.10071 | -0.082398 | 0.10986 | -0.073242 | 0.26093 | 123.0515 | 0.036621 | 123.0057 | 122.8958 | 122.8134 | 122.7951 | 122.8043 | -122.9828 | -122.8912 | 122.9507 | 122.9965 | 59.7977 | 59.816
727.8281 | 123.2071 | -59.9396 | 62.9288 | -0.060425 | -0.00015586 | 0.061932 | 0.064668 | 0.0019653 | -0.0048364 | 0.00073273 | 0.011932 | 0.0020208 | 0.066204 | 0.054952 | -0.0046314 | 0.0026746 | 0.0011279 | -0.19226 | 62.8647 | -60.0723 | 62.9471 | -59.7977 | -60.1547 | 0.032043 | -0.13733 | 62.8601 | -59.9533 | 63.0478 | -59.9396 | -60.0082 | -59.8434 | -0.13275 | -0.064087 | 0.018311 | 0.14191 | 59.9716 | -0.21515 | 60.1044 | -0.082397 | -0.013733 | -0.068665 | 0.11902 | 0 | 0.09613 | -0.068665 | 0.10986 | -0.054932 | 0.27466 | 123.0194 | 0.013733 | 123.0011 | 122.937 | 122.8134 | 122.8043 | 122.7997 | -123.0011 | -122.8821 | 122.8867 | 122.9874 | 59.7473 | 59.8022
728.8906 | 123.0927 | -59.935 | 63.002 | -0.060425 | 0.00091214 | 0.061504 | 0.067018 | -0.0010253 | -0.0014184 | -0.0024717 | -0.018585 | 0.003089 | 0.067058 | 0.069052 | -0.0042042 | 0.0028882 | -0.0010083 | -0.17395 | 62.915 | -60.0632 | 62.9013 | -59.8618 | -60.1913 | 0.027466 | -0.15564 | 62.9196 | -59.967 | 62.9883 | -60.0082 | -60.1227 | -59.9487 | -0.12817 | -0.086975 | -0.10071 | 0.073243 | 59.9625 | -0.25635 | 60.0906 | -0.12817 | -0.032043 | -0.082397 | -0.013733 | -0.073242 | -0.013732 | -0.18768 | 0.018311 | -0.15564 | 0.20142 | 122.9645 | -0.041199 | 122.9553 | 122.9782 | 122.8867 | 122.85 | 122.8546 | -123.0652 | -122.9691 | 122.8363 | 122.9233 | 59.761 | 59.7794
729.8438 | 123.111 | -59.9716 | 62.9837 | -0.060425 | 0.00069854 | 0.062145 | 0.067872 | 0.0038879 | -0.0037684 | -0.0016171 | -0.058258 | 0.0024482 | 0.06599 | 0.064779 | -0.0052722 | 0.00075204 | 0.0024097 | -0.16022 | 62.915 | -60.0723 | 62.9013 | -59.8801 | -60.2051 | 0.013733 | -0.16022 | 62.9333 | -59.9899 | 62.9929 | -59.967 | -60.1089 | -59.9213 | -0.10071 | -0.068665 | -0.082398 | 0.091553 | 59.9854 | -0.23346 | 60.0861 | -0.13275 | -0.01831 | -0.050354 | 0.009155 | 0.004578 | 0.050354 | -0.13733 | 0.068664 | -0.11902 | 0.19226 | 122.9736 | 0.022888 | 122.9828 | 122.9874 | 122.9233 | 122.8867 | 122.905 | -123.056 | -122.9736 | 122.8729 | 122.9645 | 59.8114 | 59.8114
730.8906 | 123.1155 | -59.9716 | 62.9883 | -0.075684 | -0.00079686 | 0.061504 | 0.065736 | -0.0018799 | -0.0035548 | 0.00094633 | -0.024689 | 0.0018072 | 0.06599 | 0.061575 | -0.0035632 | 0.0037426 | -0.0025037 | -0.17853 | 62.915 | -60.0861 | 62.915 | -59.8755 | -60.2097 | 0.013733 | 0 | 62.9608 | -59.935 | 62.9425 | -59.9716 | -60.1089 | -59.9533 | -0.11444 | -0.073242 | -0.073242 | 0.096131 | 59.9854 | -0.23804 | 60.0998 | -0.1236 | 0.036621 | -0.027466 | -0.045776 | 0 | 0.018311 | -0.13733 | -0.01831 | -0.17395 | 0.21057 | 123.0011 | -0.036621 | 122.8775 | 123.0011 | 122.8958 | 122.8867 | 122.9324 | -123.0743 | -122.9233 | 122.8867 | 122.9141 | 59.7931 | 59.9716
731.8438 | 123.1934 | -59.8984 | 62.9471 | -0.090943 | 0.00048494 | 0.061504 | 0.063814 | -0.0031617 | -0.0041956 | -0.00033547 | 0.20419 | 0.0026618 | 0.06599 | 0.065847 | -0.0037768 | 0.003529 | 5.9726e-05 | -0.11902 | 62.8922 | -60.0494 | 63.0295 | -59.729 | -60.0769 | 0.10986 | -0.16937 | 62.8876 | -59.935 | 63.0981 | -59.9167 | -59.9854 | -59.8114 | -0.15106 | -0.054932 | 0.082397 | 0.16937 | 60.0082 | -0.17853 | 60.1593 | -0.027466 | -0.036622 | -0.05951 | 0.15106 | -0.018311 | 0.086975 | -0.086976 | 0.1236 | -0.050354 | 0.32043 | 123.0789 | 0.018311 | 123.0331 | 122.9416 | 122.8226 | 122.7905 | 122.7859 | -122.9965 | -122.8821 | 122.9279 | 122.9965 | 59.7794 | 59.729
732.8906 | 123.1201 | -59.9579 | 62.9745 | -0.037537 | -0.00079686 | 0.063427 | 0.068513 | 0.0021789 | 0.00050424 | 0.00051913 | -0.070465 | 0.0018072 | 0.065349 | 0.069479 | -0.0056994 | 0.0039562 | -0.0039991 | -0.15106 | 62.8784 | -60.0723 | 62.9379 | -59.816 | -60.1822 | 0.009155 | -0.11902 | 62.883 | -59.967 | 63.0981 | -60.0952 | -60.1318 | -59.848 | -0.11444 | -0.09613 | -0.036621 | 0.14191 | 59.967 | -0.2243 | 60.0815 | -0.10986 | -0.009155 | -0.091552 | 0.1236 | -0.13733 | 0.10986 | -0.17395 | 0.11902 | -0.16479 | 0.25635 | 123.0103 | -0.12817 | 123.0652 | 122.9507 | 122.85 | 122.8363 | 122.8409 | -123.0469 | -122.9416 | 122.8958 | 123.056 | 59.8068 | 59.8389
733.8281 | 123.2117 | -59.9258 | 62.9333 | -0.13672 | 0.00091214 | 0.061932 | 0.068513 | 0.0011109 | -0.0035548 | -0.00012167 | -0.027741 | 0.0003118 | 0.06364 | 0.059866 | -0.0033496 | 0.003529 | -0.00015387 | -0.17853 | 62.8326 | -60.0586 | 63.0249 | -60.0449 | -60.1868 | 0.15564 | -0.10071 | 62.8555 | -59.9442 | 63.0386 | -59.9213 | -60.0357 | -59.8663 | -0.13275 | -0.10071 | 0.091552 | -0.11902 | 60.0815 | -0.26093 | 60.2142 | -0.12817 | -0.018311 | -0.07782 | 0.10529 | 0.004577 | 0.059509 | -0.10986 | 0.07782 | -0.091553 | 0.013733 | 123.0835 | 0.022888 | 122.9828 | 122.8912 | 122.7997 | 122.7585 | 122.7814 | -122.9919 | -122.8775 | 122.9507 | 122.9645 | 59.7473 | 59.8251
734.9062 | 123.2483 | -59.9579 | 62.9196 | -0.12146 | 0.0026211 | 0.063641 | 0.066591 | 4.2692e-05 | -0.0031274 | 0.0013735 | -0.012482 | -0.0001154 | 0.065136 | 0.058584 | -0.0063404 | 0.0041698 | -0.0061353 | -0.21515 | 62.8235 | -60.0632 | 62.9745 | -59.7931 | -60.173 | -0.027466 | -0.17395 | 62.8235 | -59.9716 | 63.0524 | -59.8709 | -60.2921 | -60.0494 | -0.10528 | -0.096131 | 0.054931 | 0.1648 | 59.9304 | -0.21515 | 60.0357 | -0.10986 | -0.013733 | -0.096131 | 0.13275 | 0.086975 | -0.091552 | -0.33417 | -0.077819 | -0.32043 | 0.27008 | 123.0377 | 0.10071 | 123.024 | 122.8867 | 122.7951 | 122.7814 | 122.7814 | -122.9828 | -122.8912 | 122.9324 | 123.0103 | 59.7427 | 59.7839
735.8281 | 123.1796 | -59.9533 | 62.9105 | -0.16724 | 0.0013393 | 0.062359 | 0.06595 | -0.0012391 | -0.00099116 | -0.00054907 | -0.0063781 | 0.0007392 | 0.06364 | 0.064779 | -0.0052722 | 0.003529 | -0.0010083 | -0.18768 | 62.8464 | -60.0586 | 62.9791 | -59.7794 | -60.1868 | -0.009155 | -0.14648 | 62.8418 | -59.9991 | 63.0524 | -59.9487 | -60.0357 | -59.8663 | -0.10529 | -0.064086 | 0.068665 | 0.17395 | 59.9442 | -0.23346 | 60.0494 | -0.12817 | -0.045776 | -0.068664 | 0.14191 | 0.004578 | 0.086975 | -0.082398 | 0.13275 | -0.036622 | 0.27924 | 123.0377 | 0.050354 | 123.0515 | 122.905 | 122.8409 | 122.7997 | 122.7951 | -122.9691 | -122.9095 | 122.9324 | 123.0057 | 59.7656 | 59.8068
736.8906 | 123.143 | -59.9258 | 62.9791 | -0.045166 | 0.0032619 | 0.063213 | 0.067232 | -0.0033753 | -0.00056396 | -0.00033547 | -0.0094299 | 0.0007392 | 0.063427 | 0.059652 | -0.0042042 | 0.00182 | 0.0011279 | -0.12817 | 62.8738 | -60.0403 | 62.9837 | -59.7931 | -60.1318 | 0.091553 | -0.10071 | 62.8967 | -59.9579 | 63.002 | -59.9625 | -60.0861 | -59.9213 | -0.11444 | -0.10529 | 0.004578 | 0.13275 | 60.0174 | -0.20599 | 60.1318 | -0.091553 | -0.032044 | -0.082397 | 0.022888 | -0.036621 | 0.004577 | -0.16022 | 0.036621 | -0.12817 | 0.24719 | 123.024 | -0.004577 | 122.9599 | 122.9141 | 122.8546 | 122.7997 | 122.8226 | -123.0194 | -122.937 | 122.9095 | 122.9279 | 59.7977 | 59.8251
737.8281 | 123.1659 | -59.967 | 62.9242 | -0.075684 | 0.00027134 | 0.063427 | 0.067659 | 0.0045289 | 0.00071784 | 0.00051913 | -0.046051 | 0.0026618 | 0.066631 | 0.063711 | -0.0035632 | 0.005238 | 0.00027333 | -0.27466 | 62.8738 | -60.1044 | 62.8876 | -59.9075 | -60.2646 | -0.091553 | -0.25635 | 62.851 | -59.9899 | 63.0066 | -60.0082 | -60.1227 | -59.9258 | -0.13733 | -0.050354 | -0.036621 | 0.059509 | 59.8755 | -0.29755 | 60.0128 | -0.16022 | -0.022888 | -0.073242 | 0.082398 | -0.041199 | 0.041199 | -0.15564 | 0.064087 | -0.13275 | 0.19684 | 122.9919 | -0.018311 | 122.9965 | 122.9782 | 122.8409 | 122.8409 | 122.818 | -123.0286 | -122.9141 | 122.8546 | 122.9736 | 59.6924 | 59.7107
738.8906 | 123.1659 | -59.9533 | 63.002 | -0.068054 | 0.00027134 | 0.062572 | 0.066377 | -0.0014527 | -0.0044092 | -0.0018307 | -0.036896 | 0.0020208 | 0.067486 | 0.062002 | -0.0046314 | 0.0041698 | -0.0027173 | -0.16022 | 62.9379 | -60.054 | 62.9105 | -59.8801 | -60.1913 | 0.009155 | -0.16022 | 62.9242 | -59.9854 | 63.002 | -59.967 | -60.0723 | -59.8892 | -0.10071 | -0.064087 | -0.091553 | 0.073242 | 59.9625 | -0.23804 | 60.0632 | -0.13733 | -0.032044 | -0.07782 | 0 | -0.013733 | 0.064087 | -0.11902 | 0.096131 | -0.086975 | 0.17395 | 122.9645 | 0.018311 | 122.9874 | 122.9919 | 122.9095 | 122.8912 | 122.8775 | -123.056 | -122.9874 | 122.8638 | 122.9553 | 59.7931 | 59.7931
739.8281 | 123.1796 | -59.9579 | 62.915 | -0.1062 | 0.00069854 | 0.063854 | 0.067018 | -0.0016663 | -0.0016322 | -0.0031125 | -0.0063781 | 0.0018072 | 0.066204 | 0.062643 | -0.0050586 | 0.0031018 | 0.0024097 | -0.21515 | 62.8372 | -60.0769 | 62.9517 | -59.8251 | -60.1868 | -0.027466 | -0.18768 | 62.8738 | -59.9945 | 63.0249 | -59.9762 | -60.0769 | -59.8984 | -0.11902 | -0.07782 | 0.036621 | 0.13275 | 59.9304 | -0.22888 | 60.0494 | -0.10986 | -0.036621 | -0.041199 | 0.10986 | -0.01831 | 0.05951 | -0.11902 | 0.096131 | -0.082397 | 0.25177 | 123.0286 | 0.018311 | 123.0194 | 122.9141 | 122.8683 | 122.7951 | 122.8317 | -122.9919 | -122.9095 | 122.9095 | 122.9828 | 59.7427 | 59.7702
740.8906 | 123.1934 | -59.9304 | 62.9791 | -0.037537 | 0.0041165 | 0.064068 | 0.065736 | 0.00025629 | -0.00056396 | -0.0014035 | -0.0063781 | -0.0005426 | 0.064922 | 0.06542 | -0.0063404 | 0.0031018 | -0.0033581 | -0.11902 | 62.9059 | -60.022 | 63.0295 | -59.8526 | -60.0815 | 0.13733 | -0.022888 | 62.8647 | -59.9396 | 63.0478 | -59.8801 | -59.9854 | -59.8343 | -0.091553 | -0.073242 | 0.050354 | 0.07782 | 60.0677 | -0.15106 | 60.1593 | -0.059509 | -0.009155 | -0.11444 | 0.068665 | 0.050354 | 0.09613 | -0.054932 | 0.10528 | -0.045777 | 0.16937 | 123.0515 | 0.059509 | 122.9874 | 122.9279 | 122.8043 | 122.8363 | 122.7951 | -123.0011 | -122.9187 | 122.9599 | 122.9782 | 59.8114 | 59.9075
741.8281 | 123.0972 | -59.9716 | 62.9837 | -0.1062 | 0.00027134 | 0.064281 | 0.068727 | 0.0041015 | -0.0016322 | 0.00051913 | -0.085724 | 0.0011664 | 0.065563 | 0.064565 | -0.0067676 | 0.0065198 | 0.0026233 | -0.16937 | 62.8738 | -60.1044 | 62.9288 | -59.8572 | -60.2051 | -0.013733 | -0.18768 | 62.8967 | -59.9808 | 62.9883 | -60.0311 | -60.1456 | -59.9213 | -0.13275 | -0.10986 | -0.054932 | 0.11444 | 59.9579 | -0.23346 | 60.0906 | -0.10071 | -0.009155 | -0.086975 | 0.004577 | -0.059509 | 0.050354 | -0.17395 | 0.059509 | -0.1648 | 0.24719 | 123.0331 | -0.050354 | 122.9691 | 122.9782 | 122.8775 | 122.8455 | 122.8683 | -123.0881 | -122.9645 | 122.9004 | 122.9599 | 59.8022 | 59.7839
742.8906 | 123.2208 | -59.9304 | 62.9333 | -0.014649 | 0.00027134 | 0.063213 | 0.06595 | -0.0027343 | -0.0014184 | -0.0018307 | 0.030243 | 0.0026618 | 0.063 | 0.059225 | -0.0027088 | 0.0048108 | -0.0010083 | -0.09613 | 62.8738 | -60.0449 | 63.0157 | -59.7336 | -60.0677 | 0.12817 | -0.013733 | 62.8464 | -59.9533 | 62.9379 | -59.8068 | -59.9854 | -59.8709 | -0.11444 | -0.05951 | 0.082397 | 0.19684 | 60.0586 | -0.13733 | 60.173 | -0.022888 | -0.022888 | -0.086975 | 0.004577 | 0.1236 | 0.059509 | -0.054932 | 0.082397 | -0.032044 | 0.31128 | 123.0606 | 0.14648 | 122.8912 | 122.9187 | 122.7997 | 122.8043 | 122.7768 | -122.9782 | -122.8867 | 122.9462 | 122.8683 | 59.8343 | 59.9167
743.8281 | 123.0698 | -59.9625 | 62.97 | -0.083313 | 0.00069854 | 0.062145 | 0.069795 | -0.0012391 | -0.0016322 | -0.0028989 | -0.073517 | 0.0020208 | 0.065777 | 0.065847 | -0.0042042 | 0.0043836 | -0.0025037 | -0.20142 | 62.8693 | -60.1044 | 62.8967 | -59.8755 | -60.2554 | -0.059509 | -0.23804 | 62.883 | -59.9945 | 62.9654 | -60.0357 | -60.1593 | -59.9304 | -0.14191 | -0.10071 | -0.073242 | 0.086975 | 59.903 | -0.29297 | 60.0449 | -0.15106 | -0.032044 | -0.086975 | -0.004578 | -0.073243 | 0.032043 | -0.19684 | 0.064087 | -0.16479 | 0.22888 | 123.0011 | -0.041199 | 122.9599 | 122.9736 | 122.8775 | 122.8317 | 122.8455 | -123.0743 | -122.9645 | 122.8592 | 122.9279 | 59.761 | 59.7244
744.9062 | 123.1567 | -59.9487 | 62.9883 | 0.00061049 | 0.0026211 | 0.062572 | 0.0683 | 0.0015381 | -0.0031274 | -0.0018307 | -0.042999 | 0.0028754 | 0.067913 | 0.063711 | -0.0039906 | 0.0041698 | -0.0022901 | -0.16937 | 62.9196 | -60.0861 | 62.8693 | -59.8801 | -60.2097 | 0.032043 | -0.16479 | 62.9288 | -59.9762 | 62.9837 | -59.9945 | -60.0952 | -59.9213 | -0.13733 | -0.068664 | -0.11902 | 0.068664 | 59.9808 | -0.26093 | 60.1181 | -0.1236 | -0.027466 | -0.059509 | -0.004577 | -0.045777 | 0.027465 | -0.14649 | 0.054931 | -0.11902 | 0.20599 | 122.9553 | -0.018311 | 122.9599 | 123.0057 | 122.905 | 122.8683 | 122.8775 | -123.0743 | -122.9645 | 122.818 | 122.9324 | 59.7794 | 59.7839
745.8281 | 123.1567 | -59.9716 | 62.9654 | -0.11383 | 0.0013393 | 0.061932 | 0.068941 | 0.00046989 | -0.00056396 | 0.0013735 | -0.097931 | 0.0015936 | 0.067058 | 0.06777 | -0.0033496 | 0.0043836 | 0.0021961 | -0.17853 | 62.8922 | -60.0861 | 62.9379 | -59.8343 | -60.1959 | 0.018311 | -0.16937 | 62.8647 | -59.9808 | 63.0249 | -59.9625 | -60.0861 | -59.8984 | -0.11444 | -0.073242 | -0.027466 | 0.13733 | 59.9899 | -0.2243 | 60.1044 | -0.10986 | -0.009155 | -0.10071 | 0.059509 | 0.009156 | 0.073243 | -0.11444 | 0.082398 | -0.10529 | 0.25177 | 123.024 | 0.018311 | 123.0057 | 122.9782 | 122.8455 | 122.8638 | 122.8363 | -123.0515 | -122.9462 | 122.9095 | 122.9965 | 59.7931 | 59.8022
746.8906 | 123.1613 | -59.967 | 62.9333 | -0.083313 | -0.00015586 | 0.063641 | 0.066804 | 0.0026063 | -0.0018458 | -0.0031125 | 0.039398 | 0.0005256 | 0.06364 | 0.058157 | -0.0037768 | 0.0026746 | 0.0021961 | -0.2243 | 62.8693 | -60.0266 | 62.9379 | -59.816 | -60.2005 | 0.009155 | -0.054932 | 62.8784 | -59.9396 | 63.0157 | -59.935 | -60.0723 | -59.8801 | -0.059509 | -0.064087 | 0.004577 | 0.15106 | 59.9762 | -0.23346 | 60.0357 | -0.17395 | 0.027466 | -0.054932 | 0.082397 | 0.032043 | 0.086975 | -0.10529 | 0.059509 | -0.13275 | 0.21057 | 122.9645 | 0.004577 | 122.9553 | 122.8958 | 122.818 | 122.8363 | 122.8455 | -122.9599 | -122.8729 | 122.905 | 122.9828 | 59.7427 | 59.9121
747.8281 | 123.1384 | -59.935 | 62.9837 | -0.17487 | -0.0022923 | 0.061718 | 0.066804 | -0.0029479 | -0.00013676 | -0.00076267 | -0.039948 | 0.0045844 | 0.066204 | 0.06307 | -0.0059132 | 0.0026746 | 0.0019823 | -0.13275 | 62.9013 | -60.0998 | 62.9059 | -59.8618 | -60.2234 | 0.018311 | -0.16479 | 62.9013 | -59.9625 | 62.9791 | -59.9899 | -60.0952 | -59.9213 | -0.16479 | -0.082398 | -0.07782 | 0.073243 | 59.9533 | -0.28839 | 60.1181 | -0.1236 | -0.027465 | -0.082398 | -0.004578 | -0.054931 | 0.013733 | -0.16022 | 0.041198 | -0.13275 | 0.23804 | 123.0057 | -0.027466 | 122.9416 | 123.0011 | 122.8638 | 122.8363 | 122.8363 | -123.0835 | -122.9462 | 122.8409 | 122.9141 | 59.8022 | 59.7702
748.8906 | 123.2071 | -59.9304 | 62.9562 | -0.098572 | 0.0015529 | 0.062572 | 0.066804 | -0.0042297 | -0.0014184 | -0.0026853 | 0.04245 | 0.003089 | 0.064922 | 0.059652 | -0.003136 | 0.0026746 | -0.0016493 | -0.20599 | 62.883 | -60.0449 | 62.9608 | -59.8114 | -60.1501 | 0.027466 | -0.14648 | 62.8647 | -59.9442 | 63.0569 | -59.9213 | -60.0128 | -59.848 | -0.11444 | -0.073242 | 0.004577 | 0.11902 | 59.9579 | -0.21973 | 60.0723 | -0.10529 | -0.013733 | -0.091553 | 0.10071 | 0.009155 | 0.082398 | -0.082397 | 0.096131 | -0.068664 | 0.23346 | 123.0057 | 0.022888 | 123.0011 | 122.9279 | 122.8088 | 122.8134 | 122.7951 | -123.0011 | -122.9004 | 122.8912 | 122.9874 | 59.7244 | 59.7839
749.8438 | 123.0423 | -59.9899 | 62.9654 | -0.083313 | 0.0026211 | 0.061504 | 0.067445 | 4.2692e-05 | -0.0018458 | -0.00054907 | -0.07962 | 0.00138 | 0.066418 | 0.062216 | -0.0054858 | 0.010365 | -0.0031445 | -0.27466 | 62.8784 | -60.1044 | 62.8418 | -59.9762 | -60.2921 | -0.10071 | -0.28839 | 62.8647 | -59.9945 | 62.7594 | -60.0357 | -59.8572 | -59.8068 | -0.11444 | -0.086975 | -0.1236 | 0.013733 | 59.8892 | -0.30212 | 60.0037 | -0.18768 | -0.004578 | -0.10071 | -0.20599 | -0.045777 | 0.1831 | 0.13275 | 0.18768 | 0.13733 | 0.12817 | 122.9462 | -0.041199 | 122.7539 | 122.9828 | 122.8592 | 122.8683 | 122.8546 | -123.0698 | -122.9599 | 122.8317 | 122.7493 | 59.7153 | 59.7015
750.8906 | 123.175 | -59.9442 | 62.9196 | -0.098572 | 0.00048494 | 0.063427 | 0.066377 | 0.0011109 | -0.0012048 | -0.0014035 | 0.0027771 | 0.0020208 | 0.065777 | 0.054952 | -0.003136 | 0.0037426 | -0.00015387 | -0.23346 | 62.8464 | -60.0632 | 62.9471 | -59.8114 | -60.1776 | -0.022888 | -0.20599 | 62.8326 | -59.9716 | 63.0203 | -59.9716 | -60.0632 | -59.8709 | -0.11902 | -0.073242 | 0.027466 | 0.13275 | 59.9213 | -0.23346 | 60.0403 | -0.11444 | -0.027466 | -0.086975 | 0.10071 | -0.027466 | 0.073242 | -0.11902 | 0.10071 | -0.091552 | 0.25177 | 123.0103 | 0 | 122.9919 | 122.9095 | 122.8043 | 122.7905 | 122.7768 | -122.9828 | -122.8912 | 122.8912 | 122.9645 | 59.7107 | 59.7382
751.8281 | 123.1384 | -59.9762 | 62.9974 | -0.060425 | 0.00048494 | 0.060223 | 0.066377 | -0.0020935 | -0.0012048 | -0.0011899 | -0.049103 | 0.0018072 | 0.067058 | 0.066061 | -0.0052722 | 0.0048108 | 0.00048713 | -0.16937 | 62.9196 | -60.054 | 62.9196 | -59.8663 | -60.1822 | 0.018311 | -0.15106 | 62.9379 | -59.9396 | 63.0295 | -59.9808 | -60.0998 | -59.8846 | -0.07782 | -0.07782 | -0.07782 | 0.10986 | 59.9945 | -0.20599 | 60.0723 | -0.12817 | 0.036621 | -0.05951 | 0.032043 | -0.004578 | 0.091552 | -0.1236 | 0.054931 | -0.16022 | 0.18768 | 122.9736 | -0.041199 | 122.9691 | 122.9736 | 122.8775 | 122.8958 | 122.9141 | -123.0515 | -122.937 | 122.8958 | 123.0057 | 59.8068 | 59.8251
752.8906 | 123.1796 | -59.9579 | 62.9196 | -0.13672 | 0.00027134 | 0.064068 | 0.064882 | -0.0020935 | 0.0024268 | -0.0043943 | 0.0027771 | 0.0011664 | 0.066204 | 0.066061 | -0.0050586 | 0.0048108 | -0.00036747 | -0.22888 | 62.851 | -60.0632 | 62.9517 | -59.7977 | -60.1913 | -0.009155 | -0.19684 | 62.8418 | -59.9991 | 63.0341 | -59.9808 | -60.0677 | -59.8892 | -0.10528 | -0.068665 | 0.032043 | 0.16022 | 59.9487 | -0.23346 | 60.054 | -0.12817 | -0.041198 | -0.07782 | 0.11444 | -0.022888 | 0.068665 | -0.10986 | 0.10986 | -0.068665 | 0.2655 | 123.0148 | 0.01831 | 123.0331 | 122.9141 | 122.8409 | 122.8088 | 122.7997 | -122.9828 | -122.9187 | 122.9095 | 122.9919 | 59.729 | 59.761
753.8438 | 123.1247 | -59.967 | 62.9379 | -0.052796 | 0.0021939 | 0.063427 | 0.0683 | 0.00046989 | -0.0031274 | -0.00076267 | -0.067413 | 0.0015936 | 0.066204 | 0.063711 | -0.0054858 | 0.0050244 | 0.00091433 | -0.29297 | 62.8784 | -60.0906 | 62.8601 | -59.9258 | -60.2966 | -0.10071 | -0.29297 | 62.8738 | -59.9991 | 62.9791 | -60.0494 | -60.1501 | -59.9487 | -0.1236 | -0.059509 | -0.07782 | 0.041199 | 59.8663 | -0.32959 | 59.9899 | -0.20599 | -0.032043 | -0.064087 | 0.041199 | -0.082397 | 0.018311 | -0.1831 | 0.050354 | -0.15106 | 0.16479 | 122.9507 | -0.050354 | 122.9782 | 122.9691 | 122.8729 | 122.8455 | 122.8409 | -123.0286 | -122.937 | 122.8271 | 122.9462 | 59.6741 | 59.6741
754.8281 | 123.0743 | -59.9625 | 63.002 | -0.068054 | 0.0017667 | 0.063213 | 0.065736 | -0.0023071 | -0.00099116 | -0.0022581 | 0.014984 | 0.0003118 | 0.064709 | 0.063711 | -0.0037768 | 0.00182 | 0.0015551 | -0.14648 | 62.8922 | -60.0311 | 62.97 | -59.8022 | -60.141 | 0.086975 | -0.10529 | 62.8922 | -59.9533 | 62.97 | -59.9396 | -60.0311 | -59.8846 | -0.068665 | -0.10986 | -0.032043 | 0.16022 | 60.0494 | -0.17853 | 60.1181 | -0.10986 | 0.009155 | -0.10986 | -0.032043 | 0.022888 | 0.077819 | -0.068665 | 0.068664 | -0.07782 | 0.22888 | 123.0011 | 0.013733 | 122.9233 | 122.9233 | 122.8455 | 122.8546 | 122.8546 | -123.0331 | -122.9553 | 122.9324 | 122.9324 | 59.816 | 59.8572
755.8906 | 123.2346 | -59.9121 | 62.9242 | -0.1062 | 0.0011257 | 0.063213 | 0.067232 | 0.00068369 | -0.00035036 | -0.0031125 | -0.024689 | 0.0007392 | 0.062572 | 0.06072 | -0.0069812 | 0.0058788 | -0.0010083 | -0.20599 | 62.8418 | -60.0632 | 62.9883 | -59.7931 | -60.1685 | -0.013733 | -0.16479 | 62.8418 | -59.9854 | 63.0249 | -59.8709 | -60.054 | -59.8846 | -0.15106 | -0.082397 | 0.064087 | 0.11902 | 59.8984 | -0.25635 | 60.0494 | -0.10529 | -0.073243 | -0.082397 | 0.10071 | 0.041198 | 0.027465 | -0.14191 | 0.10071 | -0.068664 | 0.27008 | 123.0515 | 0.11444 | 123.0103 | 122.905 | 122.8271 | 122.7539 | 122.7539 | -122.9874 | -122.9095 | 122.9004 | 122.937 | 59.7061 | 59.7473
756.8281 | 123.2346 | -59.935 | 62.9608 | -0.045166 | 0.0024075 | 0.061718 | 0.066163 | -0.0012391 | -0.0016322 | 0.00051913 | 0.027191 | 0.0003118 | 0.066418 | 0.059439 | -0.0061268 | 0.0033154 | 0.00070073 | -0.17853 | 62.8784 | -60.0449 | 62.9654 | -59.7931 | -60.1181 | 0.07782 | -0.082397 | 62.883 | -59.9487 | 63.0844 | -59.8663 | -59.9854 | -59.8114 | -0.10986 | -0.082397 | 0.004578 | 0.14191 | 60.0128 | -0.1831 | 60.1227 | -0.073242 | -0.013732 | -0.077819 | 0.1236 | 0.068665 | 0.1236 | -0.050354 | 0.13733 | -0.036622 | 0.25177 | 123.0103 | 0.082397 | 123.0331 | 122.9233 | 122.8317 | 122.8134 | 122.818 | -123.0057 | -122.9095 | 122.9004 | 123.0194 | 59.7565 | 59.8526
757.8906 | 123.2391 | -59.9533 | 62.9013 | -0.060425 | 0.0024075 | 0.064281 | 0.067445 | 0.00068369 | -0.0016322 | -0.00054907 | -0.036896 | 0.0003118 | 0.065777 | 0.06307 | -0.006554 | 0.005238 | -0.0016493 | -0.20142 | 62.8189 | -60.0677 | 62.97 | -59.7702 | -60.173 | -0.009155 | -0.42572 | 62.796 | -60.0266 | 63.0844 | -59.9396 | -60.0266 | -59.8251 | -0.11444 | -0.082397 | 0.068665 | 0.1831 | 59.9442 | -0.21973 | 60.0586 | -0.10529 | -0.073242 | -0.10528 | 0.18311 | 0.013733 | 0.12817 | -0.073242 | 0.20142 | 0 | 0.29755 | 123.0377 | 0.086975 | 123.111 | 122.8867 | 122.8226 | 122.7722 | 122.7493 | -122.9691 | -122.9279 | 122.9233 | 123.0377 | 59.7519 | 59.5276
758.8438 | 123.1293 | -59.9487 | 62.9745 | -0.037537 | -0.00015586 | 0.062572 | 0.068727 | -0.0018799 | -0.00013676 | -0.00076267 | -0.085724 | 0.0015936 | 0.066418 | 0.063711 | -0.0059132 | 0.0041698 | -0.00058107 | -0.15564 | 62.9105 | -60.0815 | 62.9471 | -59.8297 | -60.1547 | 0.045776 | -0.11902 | 62.8876 | -59.9808 | 63.0066 | -59.9533 | -60.0952 | -59.8938 | -0.13275 | -0.064087 | -0.027465 | 0.11902 | 59.9945 | -0.20599 | 60.1273 | -0.073242 | -0.032044 | -0.086975 | 0.032044 | -0.004578 | 0.054931 | -0.14649 | 0.086975 | -0.11444 | 0.25177 | 123.0286 | 0.027466 | 122.9874 | 122.9919 | 122.8683 | 122.8592 | 122.8363 | -123.056 | -122.9553 | 122.8958 | 122.9553 | 59.7931 | 59.8297
759.8906 | 123.1567 | -59.9487 | 62.9288 | -0.098572 | -0.0020785 | 0.063427 | 0.064241 | 0.0026063 | -0.00077756 | -0.0026853 | 0.011932 | 0.0033026 | 0.066418 | 0.060934 | -0.0018542 | 0.0028882 | -0.0016493 | -0.21515 | 62.8647 | -60.0677 | 62.8693 | -59.8389 | -60.1913 | 0 | -0.19226 | 62.851 | -59.9945 | 63.0341 | -59.9396 | -60.0449 | -59.8572 | -0.11902 | -0.064087 | -0.059509 | 0.10986 | 59.9487 | -0.24262 | 60.0677 | -0.1236 | -0.045777 | -0.07782 | 0.10529 | 0.009155 | 0.091552 | -0.096131 | 0.13733 | -0.050354 | 0.22888 | 122.937 | 0.054932 | 123.0286 | 122.9324 | 122.8455 | 122.8134 | 122.7997 | -122.9965 | -122.9233 | 122.818 | 122.9828 | 59.7336 | 59.7565
760.8281 | 123.1842 | -59.8938 | 62.9333 | -0.083313 | 0.0024075 | 0.063213 | 0.065736 | -0.00059811 | -0.0031274 | -0.0028989 | 0.018036 | 0.0005256 | 0.064709 | 0.059652 | -0.0044178 | 0.0026746 | -0.0042127 | -0.1236 | 62.8647 | -60.0311 | 63.0478 | -59.7061 | -60.0677 | 0.13275 | -0.027466 | 62.8693 | -59.9258 | 63.0844 | -59.9854 | -59.61 | -59.5871 | -0.13733 | -0.068665 | 0.11444 | 0.18768 | 60.0266 | -0.17395 | 60.1639 | -0.036621 | -0.032043 | -0.064087 | 0.15106 | -0.091553 | 0.3067 | 0.28381 | 0.33875 | 0.31586 | 0.32501 | 123.0789 | -0.05951 | 123.0103 | 122.8958 | 122.7951 | 122.7585 | 122.7631 | -122.9645 | -122.8592 | 122.9416 | 122.9782 | 59.7702 | 59.8663
761.8906 | 123.0972 | -59.9854 | 62.9929 | -0.068054 | 0.00091214 | 0.061504 | 0.069154 | 0.0017517 | -0.0044092 | -0.0011899 | -0.070465 | 0.0020208 | 0.066418 | 0.062216 | -0.0063404 | 0.0050244 | 0.0015551 | -0.2655 | 62.8647 | -60.1318 | 62.8418 | -59.9396 | -60.2966 | -0.10071 | -0.32044 | 62.8876 | -60.0357 | 62.9013 | -59.9579 | -60.1776 | -59.9854 | -0.14648 | -0.12817 | -0.15106 | 0.045777 | 59.8846 | -0.31128 | 60.0311 | -0.16479 | -0.050354 | -0.10529 | -0.091553 | 0.027466 | 0 | -0.19226 | 0.050354 | -0.14191 | 0.19226 | 122.9736 | 0.07782 | 122.937 | 122.9965 | 122.9233 | 122.85 | 122.8729 | -123.1247 | -123.0286 | 122.8271 | 122.8867 | 59.7198 | 59.6649
762.8281 | 123.175 | -59.9442 | 62.9425 | -0.12146 | 0.0013393 | 0.063427 | 0.066591 | -0.0012391 | -0.00056396 | 0.00051913 | 0.0027771 | 0.0009528 | 0.065777 | 0.065847 | -0.0044178 | 0.00182 | -0.0016493 | -0.23346 | 62.8372 | -60.0861 | 62.9471 | -59.7977 | -60.1959 | -0.036621 | -0.20142 | 62.8418 | -59.9899 | 63.0157 | -59.9625 | -60.0723 | -59.8892 | -0.14191 | -0.10529 | 0.004578 | 0.14648 | 59.9075 | -0.25177 | 60.0494 | -0.10986 | -0.045776 | -0.10071 | 0.073242 | -0.01831 | 0.054932 | -0.12817 | 0.10071 | -0.082398 | 0.28839 | 123.0331 | 0.027466 | 123.0057 | 122.9233 | 122.8317 | 122.7814 | 122.7859 | -123.0286 | -122.9324 | 122.8912 | 122.9599 | 59.7107 | 59.7427
763.9062 | 123.2071 | -59.935 | 62.9333 | -0.060425 | 0.0026211 | 0.063213 | 0.065736 | 4.2692e-05 | -0.00077756 | -0.0020443 | 0.0088807 | 0.0009528 | 0.067058 | 0.062643 | -0.0033496 | 0.0022472 | 0.0011279 | -0.23346 | 62.883 | -60.0494 | 62.9333 | -59.8022 | -60.1685 | 0.027466 | -0.17395 | 62.8876 | -59.9579 | 63.0432 | -59.9167 | -60.0266 | -59.8389 | -0.11444 | -0.050354 | 0 | 0.13275 | 59.9625 | -0.23346 | 60.0769 | -0.11902 | -0.022888 | -0.045777 | 0.10986 | 0.018311 | 0.096131 | -0.091552 | 0.11902 | -0.068664 | 0.24719 | 122.9828 | 0.041199 | 123.0011 | 122.9324 | 122.8455 | 122.818 | 122.8226 | -122.9828 | -122.8912 | 122.8683 | 122.9782 | 59.7015 | 59.761
764.8438 | 123.1201 | -59.9533 | 62.9837 | -0.014649 | 0.00048494 | 0.061504 | 0.064668 | 0.0038879 | -0.0018458 | 0.0018009 | -0.030792 | 0.0015936 | 0.065777 | 0.057089 | -0.0035632 | 0.0016064 | -0.0012219 | -0.1831 | 62.9196 | -60.0723 | 62.915 | -59.8526 | -60.1913 | 0.036621 | -0.16479 | 62.9105 | -59.9625 | 62.9745 | -60.0082 | -60.0906 | -59.9396 | -0.11902 | -0.064087 | -0.068665 | 0.10071 | 59.9899 | -0.23804 | 60.1089 | -0.11902 | -0.009155 | -0.073243 | -0.009156 | -0.054932 | 0.013733 | -0.13733 | 0.022888 | -0.12817 | 0.21973 | 122.9874 | -0.045777 | 122.937 | 122.9919 | 122.8729 | 122.8729 | 122.8638 | -123.056 | -122.9462 | 122.8683 | 122.9279 | 59.7702 | 59.7885
765.8906 | 123.1247 | -59.9625 | 62.9517 | -0.090943 | 0.00069854 | 0.062572 | 0.0683 | -0.00038451 | -0.0029138 | -0.00033547 | -0.082672 | 0.0035162 | 0.063427 | 0.059866 | -0.0046314 | 0.0039562 | -0.0010083 | -0.16022 | 62.8922 | -60.0769 | 62.9471 | -59.8251 | -60.1593 | 0.041199 | -0.12817 | 62.915 | -59.9625 | 63.0386 | -59.967 | -60.0632 | -59.8801 | -0.11444 | -0.059509 | -0.004577 | 0.13733 | 60.0037 | -0.19684 | 60.1181 | -0.082398 | 0 | -0.036621 | 0.086975 | -0.004578 | 0.082397 | -0.10071 | 0.082397 | -0.10071 | 0.25177 | 123.024 | -0.004578 | 123.0011 | 122.9691 | 122.8775 | 122.8546 | 122.8775 | -123.0286 | -122.9141 | 122.9095 | 123.0011 | 59.8022 | 59.8343
766.8281 | 123.1934 | -59.9442 | 62.9288 | -0.14435 | 0.0024075 | 0.061718 | 0.066591 | -0.0012391 | 0.0017858 | -0.00012167 | -0.015534 | 0.0011664 | 0.06599 | 0.065847 | -0.0054858 | 0.0033154 | -0.0018629 | -0.21057 | 62.8281 | -60.054 | 62.9791 | -59.7885 | -60.1685 | -0.009155 | -0.16479 | 62.8418 | -59.9716 | 63.0432 | -59.9442 | -60.0632 | -59.8618 | -0.10986 | -0.10071 | 0.050354 | 0.15564 | 59.935 | -0.2243 | 60.0449 | -0.11444 | -0.027466 | -0.086975 | 0.11444 | 0 | 0.082398 | -0.11902 | 0.10986 | -0.091552 | 0.2655 | 123.0331 | 0.027466 | 123.0148 | 122.8821 | 122.8134 | 122.7722 | 122.7859 | -122.9828 | -122.9004 | 122.9233 | 122.9874 | 59.7336 | 59.7794
767.8906 | 123.143 | -59.9396 | 62.97 | -0.014649 | 0.0034757 | 0.062572 | 0.067659 | 0.00025629 | -0.0012048 | -0.0016171 | -0.067413 | 0.0015936 | 0.064495 | 0.066274 | -0.0061268 | 0.0037426 | -0.0025037 | -0.15564 | 62.9196 | -60.0723 | 62.9333 | -59.8206 | -60.1776 | 0.036621 | -0.11902 | 62.9059 | -59.9899 | 63.0386 | -59.967 | -60.0815 | -59.8801 | -0.13275 | -0.050354 | -0.036621 | 0.11902 | 59.9762 | -0.23804 | 60.1089 | -0.10529 | -0.050354 | -0.064087 | 0.068664 | -0.027466 | 0.059509 | -0.14191 | 0.10986 | -0.091553 | 0.25177 | 123.0057 | 0.022888 | 123.0286 | 122.9919 | 122.8958 | 122.8592 | 122.8455 | -123.0423 | -122.9599 | 122.8729 | 122.9782 | 59.7839 | 59.8206
768.8281 | 123.1888 | -59.935 | 62.9196 | -0.083313 | 0.0015529 | 0.062786 | 0.06595 | -0.00059811 | -0.00077756 | -0.0014035 | 0.021088 | 0.0007392 | 0.067058 | 0.064779 | -0.0035632 | 0.0045972 | -0.0027173 | -0.2655 | 62.8418 | -60.0586 | 62.9242 | -59.8343 | -60.1868 | -0.041199 | -0.22888 | 62.8601 | -59.9625 | 63.0203 | -59.967 | -60.054 | -59.8663 | -0.1236 | -0.07782 | 0.004577 | 0.10071 | 59.8938 | -0.25177 | 60.0174 | -0.12817 | -0.027465 | -0.05951 | 0.10071 | -0.032043 | 0.068665 | -0.11902 | 0.09613 | -0.091553 | 0.2243 | 122.9828 | -0.004578 | 122.9828 | 122.9004 | 122.8226 | 122.7768 | 122.7951 | -122.9782 | -122.8821 | 122.8592 | 122.9553 | 59.6695 | 59.7061
769.8438 | 123.2437 | -59.8846 | 62.9333 | -0.060425 | 0.0013393 | 0.063 | 0.064668 | 0.00068369 | -0.0027002 | -0.0033261 | 0.045502 | 0.0020208 | 0.064068 | 0.05538 | -0.0063404 | 0.0045972 | -0.0025037 | -0.17395 | 62.8967 | -60.0449 | 63.0112 | -59.7519 | -60.1044 | 0.10071 | -0.054932 | 62.8555 | -59.935 | 63.0981 | -59.8572 | -59.9442 | -59.7977 | -0.16022 | -0.036621 | 0.077819 | 0.13275 | 59.9854 | -0.21973 | 60.1456 | -0.059509 | -0.050354 | -0.07782 | 0.1648 | 0.027466 | 0.086976 | -0.059509 | 0.13733 | -0.009155 | 0.29297 | 123.056 | 0.07782 | 123.0331 | 122.9416 | 122.7905 | 122.7814 | 122.7402 | -122.9782 | -122.8683 | 122.8958 | 122.9828 | 59.7107 | 59.8297
770.8281 | 123.23 | -59.935 | 62.9105 | -0.1062 | 0.00091214 | 0.062786 | 0.068941 | 0.0036743 | 0.00029044 | 0.0018009 | -0.06131 | 0.00138 | 0.067913 | 0.068838 | -0.0037768 | 0.0056652 | -0.00058107 | -0.22888 | 62.8372 | -60.0677 | 62.9471 | -59.8114 | -60.2097 | -0.07782 | -0.1831 | 62.8372 | -59.9533 | 63.0661 | -59.9625 | -60.0586 | -59.8389 | -0.13275 | -0.073242 | 0.036622 | 0.1236 | 59.8572 | -0.27466 | 59.9899 | -0.14191 | -0.01831 | -0.073242 | 0.15564 | -0.027465 | 0.096131 | -0.1236 | 0.11444 | -0.10529 | 0.25635 | 123.0148 | -0.009155 | 123.0194 | 122.905 | 122.7905 | 122.7722 | 122.7722 | -122.9782 | -122.8638 | 122.8821 | 123.0011 | 59.7061 | 59.7519
771.8906 | 123.2208 | -59.9213 | 62.9471 | -0.090943 | 0.00048494 | 0.062145 | 0.064241 | -0.00038451 | -0.0016322 | -0.00097627 | 0.10959 | 0.0022346 | 0.063427 | 0.053671 | -0.004845 | 0.0043836 | -0.0016493 | -0.14648 | 62.883 | -60.0403 | 63.0249 | -59.729 | -60.0723 | 0.13275 | 0.073242 | 62.9059 | -59.935 | 63.0981 | -59.9167 | -59.9808 | -59.8206 | -0.11902 | -0.064087 | 0.077819 | 0.19226 | 60.054 | -0.15106 | 60.173 | -0.032044 | -0.013733 | -0.041199 | 0.15106 | 0.004578 | 0.10071 | -0.059509 | 0.11444 | -0.045776 | 0.31128 | 123.0652 | 0.018311 | 123.0331 | 122.9233 | 122.8409 | 122.8043 | 122.8271 | -122.9874 | -122.8821 | 122.9462 | 123.0194 | 59.7748 | 59.9945
772.8281 | 123.175 | -59.9442 | 62.9288 | -0.12909 | 0.00048494 | 0.062572 | 0.067018 | -0.0012391 | -0.00013676 | -0.0033261 | 0.011932 | 0.0028754 | 0.064709 | 0.067343 | -0.0044178 | 0.0020336 | 5.9726e-05 | -0.2655 | 62.851 | -60.0632 | 62.9196 | -59.8434 | -60.2005 | -0.032043 | -0.21057 | 62.8464 | -59.967 | 63.0157 | -59.9716 | -60.0677 | -59.8892 | -0.11902 | -0.07782 | -0.009155 | 0.10071 | 59.9121 | -0.25635 | 60.0311 | -0.13733 | -0.022888 | -0.082397 | 0.086975 | -0.027466 | 0.054932 | -0.1236 | 0.07782 | -0.10071 | 0.21973 | 122.9828 | -0.004578 | 122.9828 | 122.9141 | 122.8134 | 122.7951 | 122.7905 | -122.9919 | -122.8958 | 122.8638 | 122.9599 | 59.6786 | 59.7336
773.8906 | 123.1064 | -59.967 | 63.002 | -0.014649 | 0.0013393 | 0.059582 | 0.06595 | -0.0014527 | -0.002273 | 0.0015871 | -0.027741 | 0.0011664 | 0.068554 | 0.06072 | -0.0035632 | 0.003529 | -0.00036747 | -0.1831 | 62.915 | -60.0632 | 62.9059 | -59.8434 | -60.1959 | 0.041199 | -0.16022 | 62.9242 | -59.9854 | 62.9745 | -60.0037 | -60.0861 | -59.9213 | -0.09613 | -0.086975 | -0.09613 | 0.1236 | 60.0082 | -0.22888 | 60.1044 | -0.13275 | -0.018311 | -0.07782 | -0.027466 | -0.036621 | 0.045776 | -0.11902 | 0.064087 | -0.10071 | 0.21973 | 122.9691 | -0.01831 | 122.9599 | 122.9782 | 122.9095 | 122.8821 | 122.8912 | -123.0652 | -122.9874 | 122.8729 | 122.9416 | 59.7839 | 59.8068
774.8438 | 123.2437 | -59.9121 | 62.9608 | -0.075684 | -0.00036966 | 0.064068 | 0.065309 | -0.0020935 | -0.0024866 | -0.0016171 | 0.021088 | 9.8198e-05 | 0.066845 | 0.061361 | -0.0037768 | 0.0041698 | -0.0050671 | -0.14191 | 62.8784 | -60.0174 | 63.0295 | -59.6924 | -60.0586 | 0.10529 | -0.045776 | 62.8784 | -59.9396 | 63.0981 | -59.8572 | -59.967 | -59.8114 | -0.10529 | -0.082397 | 0.068665 | 0.21973 | 60.0174 | -0.14648 | 60.1227 | -0.041199 | -0.027466 | -0.082397 | 0.13733 | 0.054931 | 0.10071 | -0.054932 | 0.12817 | -0.027466 | 0.32501 | 123.0469 | 0.082397 | 123.0377 | 122.8958 | 122.818 | 122.7905 | 122.7905 | -122.9782 | -122.9004 | 122.9416 | 123.0103 | 59.7702 | 59.8663
775.8906 | 123.1522 | -59.935 | 62.9471 | -0.083313 | 0.0019803 | 0.062145 | 0.069581 | 4.2692e-05 | -0.0018458 | -0.00076267 | -0.10098 | 0.0011664 | 0.064281 | 0.062643 | -0.0039906 | 0.0037426 | -0.0018629 | -0.17395 | 62.9013 | -60.0861 | 62.9471 | -59.816 | -60.1822 | 0.027466 | -0.13733 | 62.8967 | -59.9716 | 63.0341 | -59.9716 | -60.0952 | -59.8984 | -0.15106 | -0.045777 | 0 | 0.11902 | 59.9625 | -0.24719 | 60.1135 | -0.09613 | -0.036621 | -0.050354 | 0.086975 | -0.036621 | 0.036622 | -0.16022 | 0.073243 | -0.1236 | 0.27008 | 123.0331 | 0 | 123.0057 | 122.9874 | 122.8683 | 122.8363 | 122.8317 | -123.0331 | -122.9187 | 122.8821 | 122.9691 | 59.761 | 59.7977
776.8281 | 123.2208 | -59.9396 | 62.9059 | -0.090943 | 0.0017667 | 0.062359 | 0.069154 | 0.0034607 | -0.00013676 | -0.0014035 | -0.033844 | 0.0020208 | 0.064068 | 0.069265 | -0.0054858 | 0.0028882 | -0.0046399 | -0.23346 | 62.8326 | -60.0815 | 62.9517 | -59.8068 | -60.1685 | -0.027466 | -0.18768 | 62.8418 | -59.9899 | 63.0707 | -59.9304 | -60.0449 | -59.8389 | -0.14191 | -0.073242 | 0.045776 | 0.13275 | 59.9121 | -0.22888 | 60.054 | -0.086975 | -0.050354 | -0.064087 | 0.16479 | 0.009155 | 0.10071 | -0.10529 | 0.15106 | -0.054932 | 0.27466 | 123.0331 | 0.059509 | 123.0606 | 122.9141 | 122.8317 | 122.7722 | 122.7814 | -122.9874 | -122.8958 | 122.8912 | 123.0103 | 59.7061 | 59.7519
777.8906 | 123.0881 | -59.9625 | 62.9974 | -0.098572 | 0.00069854 | 0.061932 | 0.067445 | -0.0014527 | -0.0027002 | 0.00094633 | -0.0063781 | 0.0011664 | 0.064281 | 0.061788 | -0.0054858 | 0.0045972 | 0.0013415 | -0.22888 | 62.9196 | -60.054 | 62.9105 | -59.8663 | -60.2051 | 0.036621 | -0.16022 | 62.9288 | -59.9945 | 62.9745 | -59.9854 | -60.1089 | -59.935 | -0.091553 | -0.07782 | -0.086976 | 0.09613 | 59.9991 | -0.24262 | 60.0906 | -0.15106 | -0.032044 | -0.068665 | -0.022889 | -0.022889 | 0.027465 | -0.14648 | 0.059509 | -0.11444 | 0.18768 | 122.9645 | 0.009155 | 122.9691 | 122.9736 | 122.9233 | 122.8821 | 122.8912 | -123.0515 | -122.9919 | 122.8729 | 122.937 | 59.7336 | 59.8022
778.8281 | 123.0881 | -59.9899 | 62.9654 | -0.090943 | 0.00069854 | 0.064709 | 0.068941 | 0.00046989 | -0.0012048 | 0.00051913 | -0.097931 | 0.0020208 | 0.067486 | 0.066061 | -0.0035632 | 0.0060924 | -0.0029309 | -0.23346 | 62.8876 | -60.0952 | 62.8693 | -59.935 | -60.2783 | -0.086975 | -0.30212 | 62.9059 | -60.0037 | 62.9379 | -60.0723 | -60.1913 | -59.9808 | -0.10529 | -0.07782 | -0.09613 | 0.054931 | 59.903 | -0.28839 | 60.0082 | -0.1831 | -0.013733 | -0.059509 | -0.027466 | -0.082398 | 0.009155 | -0.20142 | 0.022888 | -0.18768 | 0.16022 | 122.9645 | -0.068665 | 122.9416 | 122.9828 | 122.9095 | 122.8775 | 122.8958 | -123.0606 | -122.9691 | 122.8592 | 122.9279 | 59.7565 | 59.6878
779.9062 | 123.1201 | -59.967 | 62.9608 | -0.083313 | 5.7742e-05 | 0.062786 | 0.068727 | -0.00081171 | -0.0031274 | -0.00012167 | -0.058258 | 0.0018072 | 0.066204 | 0.060293 | -0.0029224 | 0.0056652 | 0.00091433 | -0.2655 | 62.883 | -60.1135 | 62.851 | -59.9396 | -60.2921 | -0.10529 | -0.31586 | 62.8693 | -60.0266 | 63.1073 | -60.0174 | -60.1868 | -59.9396 | -0.14648 | -0.077819 | -0.10986 | 0.027466 | 59.8618 | -0.32501 | 60.0082 | -0.17853 | -0.059509 | -0.091552 | 0.14649 | -0.050354 | 0.027466 | -0.21973 | 0.086975 | -0.16022 | 0.17395 | 122.9645 | 0.009155 | 123.1338 | 122.9965 | 122.8958 | 122.85 | 122.8363 | -123.0743 | -122.9874 | 122.818 | 123.0743 | 59.7015 | 59.6512
780.8281 | 123.1979 | -59.9213 | 62.8876 | -0.15961 | 0.0019803 | 0.064922 | 0.067872 | 0.00068369 | 0.00071784 | 0.0013735 | -0.021637 | 0.0015936 | 0.064709 | 0.060934 | -0.0046314 | 0.0026746 | -0.0014355 | -0.25177 | 62.8464 | -60.0815 | 62.9791 | -59.7977 | -60.173 | -0.032043 | -0.19684 | 62.8326 | -59.9899 | 63.0615 | -59.9304 | -60.0403 | -59.8297 | -0.16022 | -0.041198 | 0.091553 | 0.1236 | 59.8892 | -0.25177 | 60.0494 | -0.091553 | -0.068664 | -0.054931 | 0.17395 | -0.009155 | 0.091553 | -0.11902 | 0.16022 | -0.050354 | 0.28381 | 123.0606 | 0.059509 | 123.0515 | 122.9279 | 122.8226 | 122.7676 | 122.7539 | -122.9691 | -122.8775 | 122.9004 | 122.9828 | 59.6695 | 59.7244
781.8906 | 123.0927 | -59.967 | 62.9791 | -0.068054 | 0.00048494 | 0.062359 | 0.066804 | -0.0023071 | -0.00077756 | -0.0018307 | -0.033844 | 0.0009528 | 0.067058 | 0.063284 | -0.0039906 | 0.0028882 | -0.00079467 | -0.20142 | 62.9425 | -60.0677 | 62.9013 | -59.848 | -60.1913 | 0.022888 | -0.16937 | 62.9196 | -59.967 | 62.9883 | -60.0082 | -60.0998 | -59.9167 | -0.10071 | -0.036621 | -0.07782 | 0.11902 | 59.9899 | -0.2243 | 60.0906 | -0.1236 | 0 | -0.059509 | 0.009155 | -0.041199 | 0.050354 | -0.13275 | 0.050354 | -0.13275 | 0.21973 | 122.9691 | -0.041199 | 122.9553 | 123.0103 | 122.8867 | 122.9095 | 122.8867 | -123.0469 | -122.9462 | 122.8683 | 122.9553 | 59.7656 | 59.7977
782.8281 | 123.0927 | -59.9533 | 62.9608 | -0.068054 | 0.0024075 | 0.064068 | 0.067445 | 0.0011109 | -0.0024866 | 0.0013735 | -0.06131 | 0.00138 | 0.065777 | 0.065206 | -0.0050586 | 0.003529 | -0.0012219 | -0.21973 | 62.8876 | -60.0906 | 62.9105 | -59.8663 | -60.2142 | -0.036621 | -0.2243 | 62.8738 | -59.9808 | 62.9837 | -60.0311 | -60.1364 | -59.9258 | -0.13733 | -0.073242 | -0.050354 | 0.086975 | 59.9167 | -0.26093 | 60.054 | -0.1236 | -0.027466 | -0.086975 | 0.022889 | -0.07782 | 0.027466 | -0.18311 | 0.054932 | -0.15564 | 0.2243 | 123.0011 | -0.050354 | 122.9645 | 122.9782 | 122.8546 | 122.8409 | 122.8271 | -123.0515 | -122.9416 | 122.8638 | 122.937 | 59.7336 | 59.729
783.8906 | 123.1842 | -59.9213 | 62.9745 | -0.060425 | 0.0032619 | 0.061932 | 0.067872 | 0.0038879 | -0.00056396 | -0.0033261 | -0.0002747 | 0.0011664 | 0.066631 | 0.05773 | -0.0035632 | 0.003529 | -0.0010083 | -0.13733 | 62.9059 | -60.0266 | 63.0707 | -59.7565 | -60.2005 | 0.1236 | -0.054932 | 62.8693 | -59.9396 | 63.0615 | -59.8938 | -59.9854 | -59.8343 | -0.10529 | -0.068664 | 0.096131 | 0.16479 | 60.0449 | -0.27923 | 60.1501 | -0.17395 | -0.01831 | -0.10529 | 0.086975 | 0.027466 | 0.086975 | -0.064087 | 0.10528 | -0.045777 | 0.27008 | 123.0972 | 0.045776 | 123.0011 | 122.9324 | 122.8088 | 122.8271 | 122.7905 | -123.0011 | -122.9141 | 122.9919 | 122.9828 | 59.7839 | 59.8663
784.8438 | 123.1934 | -59.9487 | 62.9333 | -0.075684 | 0.0017667 | 0.063213 | 0.066163 | 0.00046989 | -0.002273 | -0.0014035 | 0.014984 | -0.0009698 | 0.067699 | 0.061575 | -0.004845 | 0.0031018 | 0.0026233 | -0.2243 | 62.8967 | -60.0586 | 62.9379 | -59.8068 | -60.173 | 0.027466 | -0.17395 | 62.8693 | -59.9625 | 63.0432 | -59.9304 | -60.0174 | -59.8526 | -0.10986 | -0.036621 | 0.004577 | 0.14191 | 59.9762 | -0.22431 | 60.0861 | -0.11444 | -0.013733 | -0.064087 | 0.10986 | 0.01831 | 0.09613 | -0.068665 | 0.10986 | -0.054932 | 0.25177 | 122.9965 | 0.032043 | 123.0057 | 122.9553 | 122.8317 | 122.8455 | 122.818 | -122.9919 | -122.8958 | 122.8867 | 122.9919 | 59.7244 | 59.7748
785.8906 | 123.1842 | -59.9487 | 62.9196 | -0.098572 | 0.00069854 | 0.064068 | 0.067445 | 0.0030335 | 0.001145 | -0.00033547 | -0.0094299 | 0.0015936 | 0.066631 | 0.06307 | -0.008263 | 0.0041698 | 5.9726e-05 | -0.24261 | 62.8555 | -60.0677 | 62.9608 | -59.7839 | -60.1593 | -0.022888 | -0.17395 | 62.8372 | -59.967 | 63.0432 | -59.9442 | -60.0357 | -59.8572 | -0.11902 | -0.064087 | 0.041198 | 0.16479 | 59.9258 | -0.21057 | 60.0449 | -0.091553 | -0.018311 | -0.082398 | 0.1236 | 0.004577 | 0.091552 | -0.086976 | 0.10986 | -0.068665 | 0.28381 | 123.0286 | 0.022888 | 123.0103 | 122.9233 | 122.8043 | 122.8043 | 122.7859 | -122.9874 | -122.8867 | 122.9095 | 122.9919 | 59.7061 | 59.7748
786.8281 | 123.0972 | -59.967 | 62.9562 | -0.052796 | -0.00015586 | 0.063854 | 0.068086 | 0.0013245 | -0.00099116 | -0.0018307 | -0.082672 | 0.0026618 | 0.066418 | 0.062643 | -0.0061268 | 0.0041698 | -0.00079467 | -0.24719 | 62.8784 | -60.0952 | 62.8693 | -59.9121 | -60.2737 | -0.086975 | -0.32501 | 62.9013 | -59.9991 | 62.9379 | -60.0632 | -60.1913 | -59.9716 | -0.12817 | -0.07782 | -0.086975 | 0.054932 | 59.8801 | -0.3067 | 60.0082 | -0.17853 | -0.032043 | -0.054932 | -0.018311 | -0.09613 | -0.004578 | -0.2243 | 0.027465 | -0.19226 | 0.18311 | 122.9645 | -0.064087 | 122.937 | 122.9736 | 122.9004 | 122.8455 | 122.8683 | -123.0515 | -122.9553 | 122.8363 | 122.905 | 59.7198 | 59.642
787.8906 | 123.1705 | -59.9213 | 62.9791 | -0.083313 | 0.00069854 | 0.062145 | 0.06595 | -0.0012391 | -0.0012048 | 0.0013735 | 0.0058289 | 0.0003118 | 0.064281 | 0.063497 | -0.004845 | 0.0048108 | -0.0010083 | -0.13733 | 62.8876 | -60.0266 | 63.0066 | -59.7519 | -60.0952 | 0.11902 | -0.07782 | 62.8876 | -59.9762 | 63.0478 | -59.9258 | -60.0128 | -59.8526 | -0.10529 | -0.091553 | 0.027466 | 0.16937 | 60.0403 | -0.17395 | 60.1456 | -0.068665 | -0.054931 | -0.091553 | 0.068665 | -0.004577 | 0.068665 | -0.091552 | 0.1236 | -0.036621 | 0.27466 | 123.0331 | 0.050354 | 123.024 | 122.9141 | 122.8638 | 122.8088 | 122.8088 | -123.0057 | -122.9553 | 122.9279 | 122.9691 | 59.7839 | 59.8434
788.8281 | 123.0835 | -59.9396 | 62.9517 | -0.075684 | 0.0024075 | 0.062786 | 0.0683 | -0.0010253 | -0.0027002 | -0.00012167 | -0.064362 | 0.0022346 | 0.065349 | 0.06777 | -0.0054858 | 0.0063062 | -0.0012219 | -0.21057 | 62.8784 | -60.0998 | 62.883 | -59.8892 | -60.26 | -0.045776 | -0.25177 | 62.8922 | -60.0037 | 62.9608 | -60.0494 | -60.1593 | -59.9533 | -0.16022 | -0.073242 | -0.068664 | 0.050354 | 59.8938 | -0.32044 | 60.054 | -0.16022 | -0.064087 | -0.059509 | 0.009155 | -0.10986 | -0.013733 | -0.21973 | 0.050354 | -0.15564 | 0.21057 | 122.9828 | -0.045776 | 122.9645 | 122.9782 | 122.8958 | 122.818 | 122.8317 | -123.0515 | -122.9553 | 122.8226 | 122.9004 | 59.729 | 59.6878
789.9062 | 123.2162 | -59.9579 | 62.9013 | -0.29694 | 0.0030483 | 0.060223 | 0.068086 | -0.00059811 | -0.00077756 | -0.0037533 | -0.018585 | 0.00138 | 0.064281 | 0.059652 | -0.0054858 | 0.003529 | 0.00027333 | -0.068665 | 62.8372 | -60.0403 | 63.0066 | -59.7794 | -60.1868 | -0.013733 | -0.1831 | 62.8372 | -59.9579 | 63.0524 | -59.9487 | -60.0403 | -59.8572 | -0.082397 | -0.064087 | 0.10529 | 0.17853 | 59.9442 | -0.22888 | 60.0266 | -0.14648 | 0 | -0.064087 | 0.15106 | 0.009156 | 0.10071 | -0.082397 | 0.10071 | -0.082397 | 0.26093 | 123.0469 | 0.009156 | 123.0103 | 122.8775 | 122.7951 | 122.7951 | 122.7951 | -122.9416 | -122.8592 | 122.9645 | 123.0103 | 59.8892 | 59.7748
790.8281 | 123.0789 | -59.9945 | 63.002 | -0.060425 | 0.0024075 | 0.061504 | 0.069368 | -0.0012391 | -0.00056396 | -0.0026853 | -0.021637 | 0.00138 | 0.067272 | 0.064993 | -0.0037768 | 0.0022472 | 0.0019823 | -0.20599 | 62.9379 | -60.0769 | 62.9105 | -59.8526 | -60.2051 | 0.036621 | -0.16937 | 62.9379 | -59.9762 | 63.0203 | -60.2051 | -60.1364 | -59.8801 | -0.082397 | -0.064087 | -0.091553 | 0.14191 | 60.0311 | -0.21057 | 60.1135 | -0.12817 | 0.018311 | -0.064087 | 0.018311 | -0.21057 | 0.11444 | -0.14191 | 0.09613 | -0.16022 | 0.2243 | 122.9874 | -0.22888 | 122.9965 | 123.0148 | 122.9141 | 122.9324 | 122.9324 | -123.0789 | -122.9782 | 122.905 | 123.0148 | 59.7885 | 59.8251
791.8906 | 123.2437 | -59.9075 | 62.9379 | -0.090943 | 0.0011257 | 0.062572 | 0.0683 | -0.0025207 | -0.0012048 | -0.0018307 | 0.018036 | 0.0009528 | 0.066418 | 0.064565 | -0.0033496 | 0.0048108 | -0.0020765 | -0.16479 | 62.9013 | -60.054 | 62.9929 | -59.697 | -60.0906 | 0.10986 | -0.041199 | 62.851 | -59.9258 | 63.0936 | -59.8663 | -59.9533 | -59.7748 | -0.14648 | -0.036621 | 0.054932 | 0.21057 | 60.0174 | -0.1831 | 60.1639 | -0.036621 | -0.01831 | -0.086975 | 0.15564 | 0.041199 | 0.13275 | -0.045776 | 0.15106 | -0.027466 | 0.35706 | 123.0469 | 0.059509 | 123.0194 | 122.9553 | 122.7768 | 122.8088 | 122.7585 | -122.9919 | -122.8638 | 122.9004 | 123.0011 | 59.7427 | 59.8663
792.8281 | 123.1659 | -59.9625 | 62.9837 | 0.015869 | 0.0021939 | 0.064709 | 0.068727 | -0.0014527 | -0.0020594 | -0.00033547 | -0.052155 | 0.0018072 | 0.06599 | 0.067343 | -0.0061268 | 0.0048108 | -0.0037855 | -0.18768 | 62.9288 | -60.0586 | 62.9425 | -59.8709 | -60.1822 | 0.022888 | -0.15106 | 62.9288 | -59.967 | 63.0157 | -59.9396 | -60.0723 | -59.8938 | -0.096131 | -0.054932 | -0.041199 | 0.091552 | 59.9854 | -0.21973 | 60.0815 | -0.1236 | -0.004578 | -0.054932 | 0.032043 | 0.022888 | 0.068664 | -0.10986 | 0.073242 | -0.10529 | 0.18768 | 123.0011 | 0.027466 | 122.9828 | 122.9874 | 122.8958 | 122.8912 | 122.8912 | -123.0423 | -122.9507 | 122.905 | 122.9782 | 59.7748 | 59.8114
793.8906 | 123.1842 | -59.9487 | 62.9471 | -0.13672 | 5.7742e-05 | 0.063641 | 0.066804 | 0.00068369 | -0.0035548 | 0.0018009 | 0.0027771 | 0.00138 | 0.067058 | 0.060293 | -0.0037768 | 0.003529 | 0.00048713 | -0.24719 | 62.8738 | -60.0632 | 62.9379 | -59.8251 | -60.1913 | -0.009155 | -0.21515 | 62.8922 | -59.967 | 63.0203 | -59.9716 | -60.0586 | -59.8755 | -0.11444 | -0.073243 | -0.009156 | 0.1236 | 59.9396 | -0.24262 | 60.054 | -0.12817 | -0.018311 | -0.054932 | 0.073242 | -0.022889 | 0.073242 | -0.10986 | 0.091553 | -0.091553 | 0.23804 | 123.0011 | -0.004578 | 122.9874 | 122.937 | 122.8592 | 122.8226 | 122.8409 | -123.0103 | -122.9141 | 122.8867 | 122.9691 | 59.7015 | 59.7336
794.8281 | 123.1247 | -59.9625 | 63.002 | -0.060425 | 0.0013393 | 0.062145 | 0.067872 | 0.0015381 | -0.0014184 | 0.00051913 | -0.042999 | 0.0026618 | 0.06599 | 0.062429 | -0.0054858 | 0.0048108 | 0.00070073 | -0.19684 | 62.9471 | -60.0723 | 62.915 | -59.8709 | -60.2005 | 0.027466 | -0.16937 | 62.9425 | -59.9487 | 62.9837 | -59.9808 | -60.0815 | -59.9075 | -0.10986 | -0.054931 | -0.086975 | 0.091552 | 59.9899 | -0.23804 | 60.0998 | -0.12817 | 0.013733 | -0.059509 | -0.01831 | -0.018311 | 0.054931 | -0.11902 | 0.041198 | -0.13275 | 0.20142 | 122.9874 | -0.032044 | 122.9324 | 123.0194 | 122.8912 | 122.9095 | 122.905 | -123.0743 | -122.9507 | 122.8775 | 122.9462 | 59.7656 | 59.7931
795.8906 | 123.1979 | -59.9579 | 62.9196 | -0.15961 | 0.0011257 | 0.062145 | 0.068086 | 0.0011109 | -0.0020594 | -0.00097627 | -0.0033265 | 0.0018072 | 0.064709 | 0.063925 | -0.0037768 | 0.0028882 | 0.0017687 | -0.22888 | 62.8372 | -60.0403 | 62.9654 | -59.7931 | -60.173 | -0.009155 | -0.16937 | 62.851 | -59.9533 | 63.0341 | -59.9579 | -60.0449 | -59.8618 | -0.082397 | -0.082398 | 0.045776 | 0.1648 | 59.9487 | -0.21515 | 60.0311 | -0.13275 | 0.004578 | -0.068665 | 0.11444 | 0 | 0.096131 | -0.086975 | 0.091553 | -0.091553 | 0.24719 | 123.0057 | -0.004578 | 122.9874 | 122.8775 | 122.8043 | 122.7951 | 122.8088 | -122.9599 | -122.8729 | 122.9233 | 122.9919 | 59.729 | 59.7885
796.8281 | 123.2346 | -59.903 | 62.9608 | -0.052796 | 0.00027134 | 0.063213 | 0.067445 | -0.0016663 | -0.0044092 | -0.0033261 | 0.036346 | 0.0015936 | 0.067699 | 0.060934 | -0.0067676 | 0.0031018 | -0.0016493 | -0.15564 | 62.9013 | -60.054 | 63.0249 | -59.7198 | -60.0632 | 0.15106 | -0.032043 | 62.8647 | -59.9487 | 63.089 | -59.8801 | -59.9579 | -59.8114 | -0.15106 | -0.059509 | 0.064087 | 0.1831 | 60.054 | -0.16022 | 60.2051 | -0.009155 | -0.045776 | -0.09613 | 0.12817 | 0.022888 | 0.091553 | -0.054932 | 0.13733 | -0.009156 | 0.33417 | 123.0789 | 0.068664 | 123.0377 | 122.9553 | 122.8134 | 122.8043 | 122.7676 | -123.0148 | -122.9095 | 122.9279 | 122.9919 | 59.7473 | 59.8709
797.8906 | 123.2025 | -59.9304 | 62.915 | -0.090943 | 0.00048494 | 0.062145 | 0.067018 | 0.0036743 | -0.00099116 | -0.0020443 | -0.027741 | 0.0003118 | 0.063213 | 0.064138 | -0.0063404 | 0.003529 | 0.00048713 | -0.23804 | 62.851 | -60.0494 | 62.9883 | -59.7794 | -60.1639 | -0.004578 | -0.16479 | 62.851 | -59.9625 | 63.0569 | -59.935 | -60.054 | -59.8434 | -0.11902 | -0.064087 | 0.073242 | 0.15106 | 59.9258 | -0.23346 | 60.0449 | -0.11444 | -0.032043 | -0.064087 | 0.14191 | -0.004578 | 0.086975 | -0.1236 | 0.11902 | -0.091553 | 0.27008 | 123.0377 | 0.027465 | 123.0194 | 122.9004 | 122.8134 | 122.7814 | 122.7814 | -122.9645 | -122.8775 | 122.9187 | 122.9874 | 59.6924 | 59.7656
798.8281 | 123.2254 | -59.9304 | 62.9288 | -0.083313 | 0.00027134 | 0.062359 | 0.068086 | -0.0029479 | -0.0027002 | -0.0018307 | -0.012482 | 0.0018072 | 0.065349 | 0.062002 | -0.0067676 | 0.0028882 | -0.00079467 | -0.19684 | 62.8738 | -60.0357 | 62.9562 | -59.7977 | -60.1547 | 0.054932 | -0.14648 | 62.883 | -59.9533 | 63.0432 | -59.9213 | -60.0082 | -59.8297 | -0.10529 | -0.054932 | 0.027466 | 0.13275 | 59.9854 | -0.2243 | 60.0906 | -0.11902 | -0.022888 | -0.045776 | 0.11444 | 0.009155 | 0.10071 | -0.07782 | 0.1236 | -0.054932 | 0.23804 | 122.9919 | 0.032043 | 122.9965 | 122.9095 | 122.8363 | 122.8043 | 122.8134 | -122.9645 | -122.8821 | 122.8867 | 122.9736 | 59.7336 | 59.7839
799.8281 | 123.1338 | -59.9396 | 62.9837 | -0.045166 | -0.0014377 | 0.063427 | 0.06595 | -0.0014527 | -0.0037684 | -0.0035397 | -0.012482 | 0.0024482 | 0.065136 | 0.06307 | -0.0050586 | 0.0022472 | -0.0033581 | -0.15564 | 62.8876 | -60.0311 | 62.9929 | -59.7931 | -60.1227 | 0.086975 | -0.11444 | 62.9059 | -59.935 | 63.002 | -59.967 | -60.0494 | -59.8892 | -0.091553 | -0.096131 | 0.009155 | 0.14648 | 60.0266 | -0.18311 | 60.1181 | -0.091553 | 0.004577 | -0.07782 | 0.01831 | -0.027466 | 0.050354 | -0.10986 | 0.045777 | -0.11444 | 0.23804 | 123.024 | -0.032043 | 122.937 | 122.9187 | 122.8409 | 122.8271 | 122.8455 | -123.0148 | -122.9187 | 122.9324 | 122.9416 | 59.7839 | 59.8251
800.8281 | 123.2254 | -59.9167 | 62.9379 | -0.029907 | 0.0015529 | 0.062145 | 0.065309 | -0.0010253 | -0.0012048 | -0.0020443 | 0.014984 | 0.0018072 | 0.065777 | 0.061148 | -0.006554 | -0.0028796 | 0.0028369 | -0.13733 | 62.8693 | -60.0403 | 63.0341 | -59.7153 | -60.0586 | 0.14648 | -0.022888 | 62.883 | -59.9396 | 63.3041 | -60.2188 | -60.1181 | -59.8114 | -0.1236 | -0.068664 | 0.096131 | 0.20142 | 60.0632 | -0.14191 | 60.1868 | -0.018311 | -0.022888 | -0.054931 | 0.36621 | -0.30212 | 0.10529 | -0.20142 | 0.12817 | -0.17853 | 0.32501 | 123.0743 | -0.27924 | 123.2437 | 122.9095 | 122.8226 | 122.7859 | 122.7997 | -122.9782 | -122.8775 | 122.9507 | 123.2208 | 59.7794 | 59.8938
801.8906 | 123.2162 | -59.9442 | 62.915 | -0.098572 | 0.0019803 | 0.064281 | 0.068086 | -0.00081171 | 0.00071784 | 9.193e-05 | -0.046051 | 0.0028754 | 0.064709 | 0.058584 | -0.0052722 | 0.0054516 | -0.00058107 | -0.2655 | 62.8784 | -60.0906 | 62.9288 | -59.848 | -60.2005 | -0.045776 | -0.1831 | 62.8464 | -59.9808 | 63.0386 | -59.9396 | -60.0449 | -59.8343 | -0.14648 | -0.036621 | 0.013733 | 0.096131 | 59.8984 | -0.25635 | 60.0449 | -0.10986 | -0.036621 | -0.068664 | 0.1236 | 0.004578 | 0.10986 | -0.10071 | 0.14648 | -0.064087 | 0.24262 | 123.0194 | 0.041199 | 123.0194 | 122.9691 | 122.8271 | 122.8226 | 122.7905 | -123.0057 | -122.8958 | 122.8729 | 122.9828 | 59.6786 | 59.761
802.8281 | 123.2025 | -59.9762 | 62.915 | -0.12146 | 0.0011257 | 0.062572 | 0.066804 | -0.0010253 | -0.00099116 | -0.0024717 | -0.015534 | 0.0015936 | 0.065136 | 0.058798 | -0.0052722 | 0.0039562 | 5.9726e-05 | -0.23346 | 62.8418 | -60.0403 | 62.9745 | -59.7794 | -60.1593 | -0.027466 | -0.19226 | 62.8281 | -59.9579 | 63.0478 | -59.9487 | -60.0632 | -59.8618 | -0.064087 | -0.073242 | 0.059509 | 0.19684 | 59.9487 | -0.18311 | 60.0128 | -0.11902 | 0.01831 | -0.086975 | 0.13275 | 0.027466 | 0.11444 | -0.086975 | 0.096131 | -0.10528 | 0.26093 | 123.0148 | 0.009156 | 123.0057 | 122.8821 | 122.7859 | 122.818 | 122.8043 | -122.9553 | -122.8729 | 122.9507 | 123.024 | 59.7427 | 59.7839
803.8906 | 123.1796 | -59.9579 | 62.915 | -0.098572 | 0.00069854 | 0.061932 | 0.068086 | 0.00068369 | -0.00056396 | 0.00051913 | -0.070465 | 0.0026618 | 0.065563 | 0.069265 | -0.0056994 | 0.0037426 | 0.00027333 | -0.31128 | 62.8784 | -60.1044 | 62.9013 | -59.8846 | -60.2371 | -0.082397 | -0.26093 | 62.8601 | -60.0128 | 63.0066 | -59.9762 | -60.0952 | -59.8801 | -0.14648 | -0.036621 | -0.013733 | 0.073242 | 59.8755 | -0.27924 | 60.022 | -0.13275 | -0.054931 | -0.054932 | 0.091553 | -0.01831 | 0.07782 | -0.13733 | 0.13275 | -0.082398 | 0.21973 | 123.0057 | 0.036621 | 123.0194 | 122.9828 | 122.8729 | 122.8363 | 122.818 | -123.0194 | -122.9279 | 122.8592 | 122.9645 | 59.6466 | 59.697
804.8281 | 123.23 | -59.903 | 62.9425 | -0.068054 | -0.00036966 | 0.062786 | 0.066377 | -0.0014527 | -0.0027002 | -0.0035397 | 0.011932 | 0.0024482 | 0.065349 | 0.057302 | -0.0050586 | 0.0028882 | 0.0028369 | -0.17853 | 62.9013 | -60.0357 | 63.002 | -59.729 | -60.0952 | 0.10071 | -0.050354 | 62.8693 | -59.9533 | 63.1119 | -59.8663 | -59.9533 | -59.7977 | -0.13275 | -0.041199 | 0.059509 | 0.17395 | 60.0037 | -0.19226 | 60.1364 | -0.059509 | -0.050354 | -0.073242 | 0.16937 | 0.036621 | 0.10529 | -0.050354 | 0.15564 | 0 | 0.3067 | 123.0377 | 0.086975 | 123.0652 | 122.937 | 122.8226 | 122.8043 | 122.7722 | -122.9782 | -122.8958 | 122.905 | 123.0148 | 59.7244 | 59.8526
805.8906 | 123.111 | -59.9533 | 63.002 | -0.22064 | 5.7742e-05 | 0.06065 | 0.069154 | 0.0015381 | -0.0027002 | -0.0014035 | -0.064362 | 0.0015936 | 0.063 | 0.062002 | -0.0052722 | 0.0024608 | -0.00058107 | -0.18768 | 62.915 | -60.0769 | 62.915 | -59.8526 | -60.2188 | 0.027466 | -0.18768 | 62.9517 | -59.9716 | 62.9745 | -59.9808 | -60.0861 | -59.9167 | -0.1236 | -0.086975 | -0.086975 | 0.10071 | 59.9808 | -0.2655 | 60.1044 | -0.14191 | -0.018311 | -0.050354 | -0.027466 | -0.027466 | 0.036621 | -0.13275 | 0.054932 | -0.11444 | 0.2243 | 122.9919 | -0.009155 | 122.9462 | 122.9919 | 122.9233 | 122.8683 | 122.905 | -123.0789 | -122.9736 | 122.8683 | 122.9279 | 59.7656 | 59.7656
806.8281 | 123.2162 | -59.9304 | 62.915 | -0.090943 | -0.00079686 | 0.064495 | 0.067232 | 0.0013245 | 0.001145 | 0.00073273 | -0.064362 | -0.0009698 | 0.066204 | 0.066702 | -0.0039906 | 0.0041698 | -0.00079467 | -0.21057 | 62.8189 | -60.0998 | 62.8372 | -59.9762 | -59.8206 | 0.064087 | -0.16022 | 62.8281 | -59.967 | 63.0707 | -59.9258 | -60.0311 | -59.848 | -0.16937 | -0.09613 | -0.07782 | -0.045776 | 59.9945 | 0.10986 | 60.1639 | 0.27923 | -0.036621 | -0.086975 | 0.15564 | 0.004578 | 0.082398 | -0.10071 | 0.11902 | -0.064087 | 0.1236 | 122.937 | 0.041199 | 123.0377 | 122.9187 | 122.7951 | 122.7493 | 122.7585 | -123.0148 | -122.8821 | 122.7676 | 123.0011 | 59.7198 | 59.7702
807.8906 | 123.1155 | -59.9991 | 62.97 | -0.090943 | 0.0017667 | 0.061077 | 0.068513 | 0.0015381 | -0.0012048 | -0.00054907 | -0.11014 | 0.0026618 | 0.066418 | 0.066702 | -0.0033496 | 0.006947 | -0.0010083 | -0.27924 | 62.8784 | -60.1135 | 62.8326 | -59.9625 | -60.2966 | -0.13275 | -0.33875 | 62.8922 | -60.0311 | 62.9471 | -60.054 | -60.173 | -59.9579 | -0.11444 | -0.091553 | -0.13733 | 0.036621 | 59.8663 | -0.29755 | 59.9808 | -0.18311 | -0.032044 | -0.07782 | -0.022888 | -0.054932 | 0.041198 | -0.17395 | 0.073242 | -0.14191 | 0.15106 | 122.9462 | -0.022888 | 122.9782 | 122.9919 | 122.9233 | 122.8775 | 122.8912 | -123.0835 | -123.0011 | 122.8317 | 122.9462 | 59.7198 | 59.6603
808.8281 | 123.1567 | -59.9487 | 62.9242 | -0.068054 | 0.0024075 | 0.062572 | 0.066804 | 0.00068369 | -0.0020594 | 9.193e-05 | -0.012482 | 0.0022346 | 0.06364 | 0.067129 | -0.0029224 | 0.0013928 | -0.0010083 | -0.2655 | 62.8693 | -60.0586 | 62.9333 | -59.8206 | -60.1959 | -0.032043 | -0.23804 | 62.8372 | -59.9808 | 63.0249 | -59.9625 | -60.0769 | -59.8709 | -0.10986 | -0.054931 | 0.009156 | 0.12817 | 59.9167 | -0.24719 | 60.0266 | -0.13733 | -0.032044 | -0.086975 | 0.10071 | -0.013733 | 0.077819 | -0.12817 | 0.10986 | -0.09613 | 0.23804 | 122.9919 | 0.018311 | 123.0057 | 122.9279 | 122.818 | 122.818 | 122.7859 | -122.9828 | -122.905 | 122.8821 | 122.9736 | 59.6832 | 59.7107
809.9062 | 123.1201 | -59.9533 | 62.9791 | -0.052796 | 0.0017667 | 0.063213 | 0.067018 | 0.0015381 | -0.00013676 | -0.0037533 | -0.033844 | 0.0022346 | 0.064495 | 0.061148 | -0.0050586 | 0.003529 | -0.0037855 | -0.16479 | 62.9059 | -60.0677 | 62.9608 | -59.8114 | -60.1547 | 0.082397 | -0.14191 | 62.9059 | -59.9625 | 62.9837 | -59.9808 | -60.0723 | -59.935 | -0.11444 | -0.073242 | -0.018311 | 0.14191 | 60.0357 | -0.20142 | 60.1501 | -0.086975 | -0.009155 | -0.073242 | 0.004578 | -0.027466 | 0.01831 | -0.11902 | 0.027465 | -0.10986 | 0.25635 | 123.0286 | -0.018311 | 122.9462 | 122.9736 | 122.8683 | 122.8592 | 122.8592 | -123.0469 | -122.9416 | 122.9141 | 122.937 | 59.7885 | 59.8114
810.8281 | 123.1064 | -59.967 | 62.9425 | -0.098572 | 0.0015529 | 0.062145 | 0.071077 | -0.00017091 | -0.0029138 | 0.00030553 | 0.033295 | 0.0041572 | 0.065136 | 0.061148 | -0.004845 | 0.0060924 | 0.00091433 | -0.28381 | 62.883 | -60.1181 | 62.8555 | -59.9579 | -60.553 | -0.37537 | -0.34332 | 62.9013 | -59.9991 | 62.9654 | -60.0815 | -60.141 | -59.9442 | -0.15106 | -0.059509 | -0.086975 | 0.009155 | 59.5917 | -0.58594 | 59.7427 | -0.43488 | -0.032043 | -0.041199 | 0.022888 | -0.11444 | 0.022888 | -0.17395 | 0.054931 | -0.14191 | 0.16022 | 122.9736 | -0.082398 | 122.9645 | 123.0011 | 122.9004 | 122.85 | 122.8683 | -123.0606 | -122.9416 | 122.8226 | 122.9324 | 59.6832 | 59.6237
811.8906 | 123.1659 | -59.9579 | 62.9745 | -0.060425 | 0.00048494 | 0.061718 | 0.067872 | 0.0023925 | 0.00093144 | -0.0016171 | -0.058258 | 0.00138 | 0.06599 | 0.072897 | -0.0056994 | 0.0043836 | 0.0017687 | -0.16937 | 62.9105 | -60.0723 | 62.9288 | -59.8114 | -60.1822 | 0.032043 | -0.12817 | 62.915 | -59.967 | 63.0249 | -59.9625 | -60.0769 | -59.8846 | -0.11444 | -0.064087 | -0.045776 | 0.14649 | 59.9899 | -0.2243 | 60.1044 | -0.10986 | -0.009155 | -0.059509 | 0.050354 | -0.004577 | 0.073242 | -0.11902 | 0.082397 | -0.10986 | 0.26093 | 123.0011 | 0.004578 | 122.9919 | 122.9828 | 122.8821 | 122.8683 | 122.8729 | -123.0469 | -122.9416 | 122.8867 | 122.9828 | 59.7885 | 59.8297
812.8281 | 122.9736 | -59.9991 | 62.9059 | -0.090943 | 0.0015529 | 0.063213 | 0.069581 | -0.0016663 | -0.0063318 | -0.0020443 | -0.052155 | 0.0020208 | 0.065349 | 0.064565 | -0.0037768 | 0.0058788 | -0.00015387 | -0.29755 | 62.9013 | -60.0998 | 62.8281 | -59.9625 | -60.2921 | -0.10071 | -0.32044 | 62.9013 | -59.9991 | 62.9608 | -60.0494 | -60.1959 | -59.9533 | -0.10071 | -0.004578 | -0.07782 | 0.036621 | 59.8984 | -0.29297 | 59.9991 | -0.19226 | 0 | -0.004578 | 0.054931 | -0.050354 | 0.045776 | -0.19684 | 0.045776 | -0.19684 | 0.13733 | 122.9279 | -0.050354 | 122.9599 | 123.0011 | 122.9004 | 122.9004 | 122.9004 | -123.0057 | -122.905 | 122.8271 | 122.9599 | 59.7015 | 59.6786
813.8906 | 123.0972 | -59.9213 | 63.0112 | -0.060425 | -0.00015586 | 0.060009 | 0.066377 | -0.00081171 | -0.0029138 | -0.00076267 | 0.011932 | 0.0020208 | 0.065777 | 0.058157 | -0.004845 | 0.0022472 | 0.0026233 | -0.16479 | 62.8876 | -60.0311 | 62.9517 | -59.7885 | -60.141 | 0.09613 | -0.13733 | 62.915 | -59.9533 | 62.9837 | -59.9167 | -60.0677 | -59.9121 | -0.10986 | -0.1236 | -0.059509 | 0.13275 | 60.0174 | -0.21973 | 60.1273 | -0.10986 | -0.032043 | -0.09613 | -0.027465 | 0.004578 | 0.009156 | -0.14648 | 0.041199 | -0.11444 | 0.24262 | 122.9828 | 0.036621 | 122.937 | 122.9187 | 122.8683 | 122.8088 | 122.8363 | -123.0423 | -122.9645 | 122.8729 | 122.905 | 59.7565 | 59.7839
814.8281 | 123.2071 | -59.967 | 62.9288 | -0.13672 | 0.00091214 | 0.062572 | 0.066163 | 0.0013245 | 7.6842e-05 | -0.0020443 | -0.042999 | 0.0009528 | 0.067699 | 0.068838 | -0.0039906 | 0.0041698 | -0.0016493 | -0.2243 | 62.8189 | -60.0952 | 62.9608 | -59.7885 | -60.1776 | -0.032043 | -0.21057 | 62.8418 | -59.9808 | 63.0661 | -59.935 | -60.0174 | -59.8251 | -0.12817 | -0.10986 | 0.032043 | 0.17853 | 59.935 | -0.21057 | 60.0632 | -0.082397 | -0.013733 | -0.086975 | 0.13733 | 0.032043 | 0.14191 | -0.050354 | 0.15564 | -0.036621 | 0.3067 | 123.056 | 0.045776 | 123.0469 | 122.9141 | 122.8226 | 122.7859 | 122.8088 | -123.024 | -122.9095 | 122.9279 | 123.0331 | 59.7427 | 59.7565
815.8906 | 123.0789 | -59.9258 | 63.0066 | -0.052796 | 5.7742e-05 | 0.060009 | 0.067872 | 0.00068369 | -0.0018458 | -0.0024717 | -0.042999 | 0.0005256 | 0.06599 | 0.06307 | -0.0044178 | 0.0037426 | -0.0016493 | -0.068665 | 62.9562 | -60.0494 | 62.9013 | -59.9167 | -60.2188 | 0.036621 | -0.17853 | 62.915 | -59.9579 | 62.9883 | -59.9899 | -60.1089 | -59.903 | -0.1236 | -0.050354 | -0.10529 | 0.009155 | 59.9625 | -0.29297 | 60.0861 | -0.16937 | -0.032044 | -0.091553 | -0.018311 | -0.064087 | 0.022888 | -0.18311 | 0.054932 | -0.15106 | 0.13275 | 122.9507 | -0.032043 | 122.9462 | 123.0057 | 122.8729 | 122.8821 | 122.8409 | -123.056 | -122.9645 | 122.8271 | 122.9141 | 59.8572 | 59.7473
816.8281 | 123.1476 | -59.935 | 62.9745 | -0.068054 | 0.00091214 | 0.062572 | 0.067232 | 0.0011109 | -0.0018458 | -0.0028989 | -0.052155 | 0.00138 | 0.065349 | 0.065206 | -0.0056994 | 0.0048108 | -0.0031445 | -0.20599 | 62.9105 | -60.0861 | 62.9196 | -59.848 | -60.1822 | 0.041199 | -0.15106 | 62.9059 | -59.9716 | 63.002 | -59.9442 | -60.0677 | -59.8846 | -0.15106 | -0.064087 | -0.054931 | 0.086976 | 59.9762 | -0.24719 | 60.1273 | -0.09613 | -0.036621 | -0.068664 | 0.027466 | -0.009155 | 0.050354 | -0.13275 | 0.086975 | -0.09613 | 0.23804 | 123.0057 | 0.027466 | 122.9736 | 122.9965 | 122.8775 | 122.8455 | 122.8409 | -123.0606 | -122.9462 | 122.8546 | 122.937 | 59.729 | 59.7839
817.8906 | 123.0927 | -59.9625 | 62.9883 | -0.068054 | 0.0024075 | 0.060863 | 0.068727 | 0.00025629 | -0.0012048 | -0.0018307 | 0.0088807 | 0.0024482 | 0.065136 | 0.06072 | -0.003136 | 0.0039562 | -0.00015387 | -0.21057 | 62.9608 | -60.0632 | 62.8555 | -59.6237 | -60.141 | -0.14648 | -0.23804 | 62.9288 | -59.9991 | 62.9745 | -59.9991 | -60.0906 | -59.8846 | -0.10071 | -0.027466 | -0.13275 | 0.33875 | 59.816 | -0.17853 | 59.9167 | -0.07782 | -0.036621 | -0.059509 | -0.013733 | -0.036621 | 0.077819 | -0.12817 | 0.11444 | -0.091553 | 0.43945 | 122.9187 | 0 | 122.9736 | 123.024 | 122.9279 | 122.9233 | 122.8912 | -123.0515 | -122.9874 | 122.818 | 122.937 | 59.7519 | 59.7244
818.8281 | 123.1338 | -59.9762 | 62.9745 | -0.060425 | 0.0032619 | 0.063 | 0.069581 | -0.00059811 | -0.003982 | 9.193e-05 | -0.049103 | 0.0033026 | 0.064495 | 0.061148 | -0.003136 | 0.005238 | -0.00015387 | -0.19684 | 62.915 | -60.0906 | 62.9333 | -59.8206 | -60.1868 | 0.032043 | -0.15106 | 62.915 | -59.9625 | 63.0157 | -59.9716 | -60.0677 | -59.8892 | -0.11444 | -0.059509 | -0.041198 | 0.15564 | 60.0082 | -0.21057 | 60.1227 | -0.096131 | 0.013733 | -0.059509 | 0.041199 | 0.004577 | 0.086975 | -0.091553 | 0.073242 | -0.10529 | 0.27008 | 123.024 | -0.009156 | 122.9782 | 123.0057 | 122.8775 | 122.8912 | 122.8912 | -123.0652 | -122.937 | 122.9095 | 122.9919 | 59.7794 | 59.8251
819.9062 | 123.1979 | -59.9258 | 62.9196 | -0.068054 | 0.0021939 | 0.063213 | 0.067232 | 0.00046989 | -0.0014184 | -0.00076267 | -0.027741 | 0.0007392 | 0.065777 | 0.06777 | -0.0037768 | 0.0050244 | -0.00058107 | -0.23346 | 62.8418 | -60.0815 | 62.9562 | -59.7977 | -60.1501 | -0.013733 | -0.18768 | 62.8372 | -59.9899 | 63.0615 | -59.9167 | -60.0403 | -59.8297 | -0.15564 | -0.07782 | 0.036621 | 0.12817 | 59.9121 | -0.2243 | 60.0677 | -0.068664 | -0.064087 | -0.082398 | 0.14191 | 0.009155 | 0.09613 | -0.11444 | 0.16022 | -0.050354 | 0.28381 | 123.0377 | 0.073242 | 123.0515 | 122.9233 | 122.8271 | 122.7676 | 122.7631 | -123.0011 | -122.9095 | 122.8821 | 122.9874 | 59.6924 | 59.7382
820.8281 | 123.1476 | -59.9487 | 62.9974 | -0.052796 | 0.0019803 | 0.064068 | 0.066163 | -0.0044433 | -0.00099116 | -0.0018307 | -0.015534 | 0.003089 | 0.064709 | 0.063284 | -0.004845 | 0.0060924 | -0.0042127 | -0.20142 | 62.9105 | -60.0723 | 62.9059 | -59.8618 | -60.2005 | 0.032043 | -0.19226 | 62.9242 | -59.9716 | 63.002 | -59.9762 | -60.0815 | -59.8846 | -0.1236 | -0.086976 | -0.091553 | 0.086975 | 59.9808 | -0.25177 | 60.1044 | -0.12817 | -0.022889 | -0.073243 | 0.004577 | -0.027466 | 0.064086 | -0.13275 | 0.086975 | -0.10986 | 0.21057 | 122.9782 | -0.004577 | 122.9736 | 122.9828 | 122.8958 | 122.8592 | 122.8729 | -123.0698 | -122.9691 | 122.8546 | 122.9507 | 59.7473 | 59.7565
821.8906 | 123.2117 | -59.9075 | 62.9745 | 0.26001 | 0.0011257 | 0.063641 | 0.065309 | 0.00025629 | -0.00013676 | -0.0031125 | 0.036346 | 0.0018072 | 0.067699 | 0.063711 | -0.0059132 | 0.0039562 | 0.0013415 | -0.14191 | 62.9059 | -60.0082 | 63.0249 | -59.7748 | -60.0906 | 0.14191 | -0.059509 | 62.8738 | -59.935 | 63.0707 | -59.8846 | -59.9808 | -59.8068 | -0.10071 | -0.068664 | 0.050354 | 0.13275 | 60.0494 | -0.1831 | 60.1501 | -0.082397 | -0.027466 | -0.10071 | 0.096131 | 0.022888 | 0.10071 | -0.073242 | 0.12817 | -0.045776 | 0.23346 | 123.0331 | 0.050354 | 123.0057 | 122.9141 | 122.8088 | 122.8134 | 122.7814 | -122.9828 | -122.9095 | 122.9324 | 122.9782 | 59.7656 | 59.848
822.8281 | 123.1201 | -59.9396 | 62.9837 | -0.052796 | 0.0019803 | 0.063427 | 0.067018 | 0.0019653 | 0.001145 | -0.0033261 | -0.067413 | 0.0005256 | 0.065563 | 0.063284 | -0.0074084 | 0.0041698 | 0.00027333 | -0.17853 | 62.915 | -60.0677 | 62.9196 | -59.8343 | -60.1776 | 0.022888 | -0.27924 | 62.8784 | -59.9899 | 62.9929 | -59.9625 | -60.0861 | -59.8892 | -0.12817 | -0.068665 | -0.064087 | 0.10528 | 59.9625 | -0.23804 | 60.0906 | -0.10986 | -0.050354 | -0.10529 | 0.009155 | -0.022888 | 0.050354 | -0.14649 | 0.10071 | -0.096131 | 0.23346 | 122.9874 | 0.027466 | 122.9828 | 122.9828 | 122.8683 | 122.8546 | 122.818 | -123.0515 | -122.9736 | 122.8592 | 122.9324 | 59.761 | 59.6603
823.8906 | 123.1705 | -59.9533 | 62.9333 | -0.075684 | 0.00027134 | 0.063 | 0.065736 | -0.0033753 | -0.00099116 | -0.00097627 | -0.0094299 | 0.0020208 | 0.066418 | 0.057089 | -0.0046314 | 0.005238 | -0.0042127 | -0.25177 | 62.8738 | -60.0632 | 62.9288 | -59.8206 | -60.1913 | 0.1236 | -0.17395 | 62.851 | -59.9487 | 63.0112 | -59.9442 | -60.0357 | -59.8618 | -0.10986 | -0.05951 | -0.004578 | 0.13275 | 60.0769 | -0.23804 | 60.1868 | -0.12817 | 0.004578 | -0.082398 | 0.077819 | 0.009155 | 0.091553 | -0.082398 | 0.086975 | -0.086976 | 0.24261 | 122.9919 | 0.004577 | 122.9599 | 122.937 | 122.7997 | 122.8271 | 122.8043 | -122.9965 | -122.8821 | 122.8821 | 122.9645 | 59.7015 | 59.7794
824.8281 | 123.1522 | -59.9716 | 62.9745 | -0.045166 | -0.0016513 | 0.062786 | 0.069581 | 0.0021789 | -0.0016322 | -0.0035397 | -0.082672 | 0.0009528 | 0.064709 | 0.062856 | -0.0069812 | 0.0033154 | -0.0016493 | -0.19226 | 62.9196 | -60.0677 | 62.9242 | -59.816 | -60.1822 | 0.018311 | -0.15564 | 62.8922 | -59.9899 | 62.9974 | -59.9442 | -60.0998 | -59.8846 | -0.09613 | -0.054931 | -0.050354 | 0.15564 | 59.9899 | -0.21057 | 60.0861 | -0.11444 | -0.01831 | -0.082397 | 0.022889 | 0.027466 | 0.086975 | -0.12817 | 0.10528 | -0.10986 | 0.25177 | 122.9919 | 0.045776 | 122.9874 | 122.9874 | 122.8821 | 122.8912 | 122.8638 | -123.0423 | -122.9645 | 122.8958 | 122.9691 | 59.7794 | 59.816
825.8906 | 123.1979 | -59.9213 | 62.9425 | -0.090943 | 0.00091214 | 0.062786 | 0.06595 | -0.0033753 | -0.0012048 | -0.00012167 | 0.057709 | 0.0015936 | 0.066418 | 0.059652 | -0.0042042 | 0.0022472 | 0.0036913 | -0.2243 | 62.8876 | -60.0494 | 62.9654 | -59.7977 | -60.1318 | 0.054932 | -0.12817 | 62.8738 | -59.9808 | 63.0524 | -59.903 | -59.9945 | -59.8251 | -0.12817 | -0.054932 | 0.022888 | 0.1236 | 59.9762 | -0.21057 | 60.1044 | -0.082398 | -0.059509 | -0.068665 | 0.10986 | 0.018311 | 0.096131 | -0.073242 | 0.15564 | -0.013733 | 0.25177 | 123.0148 | 0.07782 | 123.0331 | 122.937 | 122.8546 | 122.8088 | 122.7951 | -122.9919 | -122.9233 | 122.8867 | 122.9736 | 59.697 | 59.7931
826.8281 | 123.1384 | -59.9442 | 62.9883 | -0.12909 | 0.0024075 | 0.062572 | 0.068086 | -0.0042297 | -0.0012048 | -0.0014035 | -0.0002747 | 9.8198e-05 | 0.064495 | 0.067129 | -0.0050586 | 0.0033154 | -0.00058107 | -0.16022 | 62.8876 | -60.0494 | 62.9745 | -59.7702 | -60.1273 | 0.09613 | -0.10071 | 62.8967 | -59.9533 | 63.0203 | -59.9487 | -60.0723 | -59.8755 | -0.10529 | -0.10071 | -0.013733 | 0.17395 | 60.0403 | -0.1831 | 60.1456 | -0.07782 | -0.009155 | -0.091552 | 0.032044 | -0.004577 | 0.068665 | -0.12817 | 0.07782 | -0.11902 | 0.27923 | 123.024 | 0.004578 | 122.9736 | 122.937 | 122.85 | 122.8317 | 122.8409 | -123.0377 | -122.9416 | 122.9187 | 122.9645 | 59.7839 | 59.8434
827.8906 | 123.1567 | -59.9579 | 62.883 | -0.14435 | 0.0021939 | 0.062572 | 0.067445 | -0.0016663 | 0.001145 | -0.0022581 | -0.030792 | 0.0005256 | 0.063854 | 0.065634 | -0.0061268 | 0.0031018 | -0.0014355 | -0.24719 | 62.8418 | -60.0677 | 62.9608 | -59.7931 | -60.1639 | -0.018311 | -0.1831 | 62.8281 | -59.967 | 63.0478 | -59.9304 | -60.0723 | -59.9808 | -0.10986 | -0.041199 | 0.077819 | 0.1648 | 59.9396 | -0.20599 | 60.0494 | -0.09613 | -0.009155 | -0.054932 | 0.16479 | 0.027466 | -0.022888 | -0.11444 | -0.013733 | -0.10529 | 0.27466 | 123.0286 | 0.036621 | 123.0148 | 122.9095 | 122.7951 | 122.7997 | 122.7859 | -122.9507 | -122.85 | 122.9187 | 123.0057 | 59.7107 | 59.7748
828.8281 | 123.0927 | -59.9487 | 62.9974 | 0.054016 | -0.00015586 | 0.061932 | 0.066591 | -0.0012391 | -0.0037684 | -0.0024717 | -0.018585 | 0.0024482 | 0.064922 | 0.061361 | -0.0059132 | 0.0033154 | -0.0020765 | -0.37994 | 62.9425 | -60.0861 | 62.8601 | -59.8846 | -60.1822 | 0.036621 | -0.18768 | 62.9242 | -59.9716 | 62.97 | -60.0037 | -60.0861 | -59.8892 | -0.13733 | -0.054932 | -0.13733 | 0.064086 | 59.9854 | -0.23346 | 60.1227 | -0.09613 | -0.022889 | -0.073243 | -0.027466 | -0.054932 | 0.059509 | -0.13733 | 0.082398 | -0.11444 | 0.20142 | 122.9462 | -0.032043 | 122.9416 | 123.0286 | 122.8958 | 122.8912 | 122.8729 | -123.0835 | -122.9691 | 122.8088 | 122.9187 | 59.5688 | 59.761
829.9062 | 123.1247 | -59.9442 | 62.9883 | -0.060425 | -0.00036966 | 0.061718 | 0.068513 | 0.00068369 | -0.0014184 | 9.193e-05 | -0.027741 | 0.0018072 | 0.065777 | 0.061148 | -0.0059132 | 0.0045972 | -0.0012219 | -0.19684 | 62.9059 | -60.0861 | 62.9196 | -59.8709 | -60.1868 | 0.032043 | -0.18768 | 62.9242 | -59.9625 | 63.0157 | -59.9579 | -60.0723 | -59.8846 | -0.14191 | -0.082397 | -0.068664 | 0.073242 | 59.9762 | -0.24262 | 60.1181 | -0.10071 | -0.01831 | -0.064087 | 0.027466 | -0.013733 | 0.059509 | -0.12817 | 0.077819 | -0.10986 | 0.21515 | 123.0057 | 0.004577 | 122.9782 | 122.9919 | 122.8867 | 122.85 | 122.8683 | -123.0743 | -122.9507 | 122.8638 | 122.9599 | 59.7473 | 59.7565
830.8281 | 123.2254 | -59.8846 | 62.9608 | -0.029907 | 0.00091214 | 0.062572 | 0.065095 | 0.0030335 | -0.00077756 | 0.0020145 | 0.033295 | 0.0005256 | 0.066845 | 0.064779 | -0.004845 | 0.0026746 | 0.0013415 | -0.1831 | 62.8922 | -60.0449 | 62.9883 | -59.7198 | -60.0998 | 0.10071 | -0.027466 | 62.8647 | -59.9442 | 63.1027 | -59.8618 | -59.9442 | -59.7839 | -0.16022 | -0.068664 | 0.027466 | 0.16479 | 59.9854 | -0.21515 | 60.1456 | -0.054931 | -0.059509 | -0.09613 | 0.14191 | 0.022889 | 0.10071 | -0.059509 | 0.16022 | 0 | 0.32501 | 123.0331 | 0.082398 | 123.0469 | 122.937 | 122.8088 | 122.7768 | 122.7493 | -123.0057 | -122.905 | 122.8729 | 122.9874 | 59.7015 | 59.8572
831.8906 | 123.1842 | -59.9625 | 62.8967 | -0.12146 | 0.0015529 | 0.066631 | 0.066377 | 0.0051697 | -0.0014184 | -0.0018307 | -0.027741 | 0.0018072 | 0.065563 | 0.071829 | -0.0056994 | 0.0028882 | 0.0034777 | -0.31586 | 62.8006 | -60.1273 | 63.0112 | -59.7977 | -60.1547 | 0.022888 | -0.16479 | 62.8189 | -59.9945 | 63.0524 | -59.935 | -60.0357 | -59.8526 | -0.16479 | -0.096131 | 0.11444 | 0.16479 | 59.9854 | -0.19226 | 60.1501 | -0.027466 | -0.032044 | -0.07782 | 0.15564 | 0.027465 | 0.10986 | -0.073243 | 0.14191 | -0.041199 | 0.32959 | 123.1384 | 0.059509 | 123.0469 | 122.9279 | 122.8134 | 122.7631 | 122.7814 | -123.024 | -122.8912 | 122.9736 | 123.0148 | 59.6466 | 59.7977
832.8281 | 123.2117 | -59.9442 | 62.9562 | -0.052796 | 0.00069854 | 0.061077 | 0.067872 | -0.0063659 | 7.6842e-05 | -0.00033547 | 0.04245 | 0.0009528 | 0.065777 | 0.059866 | -0.0056994 | 0.0045972 | 0.0019823 | -0.23346 | 62.8647 | -60.0677 | 62.9517 | -59.8114 | -60.1456 | 0.032043 | -0.17395 | 62.8647 | -59.9396 | 63.0432 | -59.9075 | -60.0357 | -59.8434 | -0.1236 | -0.091553 | -0.004578 | 0.13275 | 59.9762 | -0.20142 | 60.0998 | -0.07782 | 0.004578 | -0.091553 | 0.086975 | 0.036621 | 0.10071 | -0.091553 | 0.09613 | -0.096131 | 0.25635 | 123.0194 | 0.032043 | 122.9828 | 122.9324 | 122.8043 | 122.8088 | 122.8088 | -123.024 | -122.8958 | 122.8958 | 122.9874 | 59.7107 | 59.7702
833.8281 | 123.2025 | -59.9213 | 62.9425 | -0.098572 | -0.0012241 | 0.062359 | 0.0683 | -0.0035889 | -0.0031274 | 9.193e-05 | -0.0002747 | 0.0005256 | 0.064709 | 0.060293 | -0.0056994 | 0.0033154 | -0.00079467 | -0.23804 | 62.9013 | -60.0082 | 62.9517 | -59.8068 | -60.0128 | 0.10529 | -0.059509 | 62.8601 | -59.9258 | 63.0524 | -59.8892 | -59.9899 | -59.8251 | -0.086975 | -0.041199 | 0.009155 | 0.11444 | 60.0266 | -0.091552 | 60.1135 | -0.004577 | -0.004577 | -0.082398 | 0.10986 | 0.032044 | 0.096131 | -0.068664 | 0.10071 | -0.064087 | 0.20142 | 122.9599 | 0.036621 | 122.9782 | 122.9095 | 122.7859 | 122.8226 | 122.7814 | -122.9507 | -122.8683 | 122.8729 | 122.9736 | 59.6832 | 59.8618
834.9219 | 123.1934 | -59.8938 | 62.9837 | -0.1062 | 0.0019803 | 0.058941 | 0.066377 | -0.00059811 | -0.00056396 | -0.00076267 | 0.0058289 | 0.0005256 | 0.066418 | 0.059225 | -0.0061268 | 0.0054516 | -0.0035719 | -0.07782 | 62.9242 | -60.0082 | 62.9333 | -59.7427 | -60.0357 | 0.09613 | -0.059509 | 62.8647 | -59.9487 | 63.0661 | -59.8846 | -59.9991 | -59.816 | -0.11444 | -0.05951 | -0.050354 | 0.15106 | 59.9899 | -0.14191 | 60.1044 | -0.027466 | -0.054931 | -0.11902 | 0.082397 | 0.009155 | 0.07782 | -0.10529 | 0.13275 | -0.050354 | 0.2655 | 122.9416 | 0.064086 | 123.0148 | 122.9324 | 122.8134 | 122.818 | 122.7585 | -122.9919 | -122.9324 | 122.8271 | 122.9599 | 59.816 | 59.8343
835.8281 | 123.2208 | -59.9075 | 62.9425 | -0.075684 | 0.0024075 | 0.061718 | 0.0683 | 0.0021789 | -0.0033412 | -0.0067441 | 0.076019 | 0.0011664 | 0.064281 | 0.056234 | -0.0046314 | 0.0041698 | -0.0018629 | -0.14648 | 62.8693 | -60.0357 | 63.1714 | -59.4635 | -60.3241 | -0.064087 | -0.17395 | 62.8647 | -59.9442 | 63.0936 | -59.8801 | -59.9899 | -59.7931 | -0.12817 | -0.073242 | 0.22888 | 0.44403 | 59.8434 | -0.41656 | 59.9716 | -0.28839 | -0.036621 | -0.07782 | 0.15106 | 0.027466 | 0.11444 | -0.082397 | 0.15106 | -0.045776 | 0.5722 | 123.2071 | 0.064087 | 123.0377 | 122.905 | 122.8088 | 122.7768 | 122.7722 | -122.9782 | -122.8867 | 123.0789 | 123.0011 | 59.761 | 59.7336
836.8906 | 123.1934 | -59.9442 | 62.9333 | -0.13672 | 0.0017667 | 0.064709 | 0.067872 | 0.0053833 | -0.0018458 | -0.00076267 | -0.039948 | 0.0005256 | 0.065349 | 0.062643 | -0.0061268 | 0.0037426 | -0.0012219 | -0.23804 | 62.8464 | -60.0586 | 62.9333 | -59.8114 | -60.2005 | -0.013733 | -0.2243 | 62.851 | -59.9762 | 63.0066 | -59.9716 | -60.0632 | -59.8618 | -0.11444 | -0.086975 | 0 | 0.13275 | 59.9304 | -0.25635 | 60.0449 | -0.14191 | -0.032043 | -0.082398 | 0.073242 | -0.027466 | 0.082398 | -0.11902 | 0.11444 | -0.086975 | 0.24719 | 122.9919 | 0.004577 | 122.9828 | 122.905 | 122.8271 | 122.7905 | 122.7951 | -122.9919 | -122.9095 | 122.8775 | 122.9507 | 59.7061 | 59.7198
837.8281 | 123.2391 | -59.9075 | 62.9425 | -0.075684 | 5.7742e-05 | 0.060436 | 0.067232 | -0.0025207 | -0.002273 | 0.0020145 | -0.0002747 | 0.00138 | 0.063427 | 0.063284 | -0.0063404 | 0.003529 | 0.00027333 | -0.19226 | 62.8738 | -60.0266 | 63.002 | -59.729 | -60.0769 | 0.10529 | -0.041199 | 62.8555 | -59.9579 | 63.0981 | -59.8526 | -59.9625 | -59.7931 | -0.11902 | -0.068665 | 0.059509 | 0.17853 | 60.0128 | -0.16937 | 60.1318 | -0.050354 | -0.050354 | -0.086975 | 0.15564 | 0.054932 | 0.11444 | -0.054931 | 0.1648 | -0.004577 | 0.29755 | 123.0286 | 0.10529 | 123.056 | 122.9004 | 122.8134 | 122.7814 | 122.7631 | -122.9691 | -122.9004 | 122.9095 | 123.0057 | 59.7153 | 59.8663
838.8906 | 123.2529 | -59.9121 | 62.9425 | -0.090943 | 0.0017667 | 0.061504 | 0.067232 | 0.00068369 | -0.0033412 | 0.00073273 | 0.0058289 | 0.0009528 | 0.063 | 0.070333 | -0.004845 | 0.0041698 | -0.0044263 | -0.21973 | 62.8693 | -60.0723 | 62.9791 | -59.7839 | -60.141 | 0.09613 | -0.12817 | 62.8647 | -59.9716 | 63.0707 | -59.903 | -59.9899 | -59.816 | -0.16022 | -0.073242 | 0.036621 | 0.12817 | 60.0082 | -0.22888 | 60.1685 | -0.068664 | -0.05951 | -0.07782 | 0.12817 | 0.009155 | 0.09613 | -0.07782 | 0.15564 | -0.01831 | 0.28839 | 123.0515 | 0.068665 | 123.0423 | 122.9416 | 122.8363 | 122.7814 | 122.7768 | -123.0148 | -122.9141 | 122.8912 | 122.9828 | 59.6924 | 59.7839
839.8438 | 123.0972 | -59.9533 | 62.9745 | -0.075684 | 0.0011257 | 0.063213 | 0.068086 | -0.00081171 | 0.00050424 | -0.0033261 | -0.11014 | 0.0020208 | 0.065349 | 0.068411 | -0.0033496 | 0.0039562 | 0.0028369 | -0.21515 | 62.8876 | -60.1044 | 62.97 | -59.8297 | -60.1913 | -0.018311 | -0.16937 | 62.9333 | -59.9625 | 63.0112 | -59.9945 | -60.1227 | -59.8938 | -0.15106 | -0.086975 | -0.004577 | 0.1236 | 59.935 | -0.23804 | 60.0861 | -0.086975 | -0.009155 | -0.041198 | 0.036621 | -0.041199 | 0.059509 | -0.16937 | 0.068664 | -0.16022 | 0.27466 | 123.0743 | -0.032044 | 122.9736 | 122.9919 | 122.8958 | 122.8409 | 122.8867 | -123.0789 | -122.937 | 122.9233 | 122.9645 | 59.7382 | 59.7839
840.8906 | 123.1201 | -59.9487 | 63.0112 | -0.12909 | 5.7742e-05 | 0.060223 | 0.067872 | 0.0023925 | -0.0054774 | -0.0022581 | -0.06131 | 0.0020208 | 0.064709 | 0.063284 | -0.0046314 | 0.0063062 | 0.00070073 | -0.17395 | 62.8967 | -60.0815 | 62.9242 | -59.8801 | -60.2325 | 0.032043 | -0.18768 | 62.9425 | -59.9854 | 62.9837 | -59.9854 | -60.0723 | -59.903 | -0.13275 | -0.11444 | -0.086975 | 0.068664 | 59.9808 | -0.28381 | 60.1135 | -0.15106 | -0.036622 | -0.068664 | -0.027465 | -0.036622 | 0.045776 | -0.1236 | 0.082398 | -0.086975 | 0.20142 | 123.0057 | 0 | 122.9691 | 122.9782 | 122.9279 | 122.8455 | 122.8912 | -123.0927 | -122.9965 | 122.8729 | 122.9324 | 59.7748 | 59.761
841.8281 | 123.2117 | -59.9213 | 62.9242 | -0.052796 | -0.00015586 | 0.061077 | 0.066377 | -0.0012391 | 0.0015722 | -0.0039671 | 0.0088807 | 0.0020208 | 0.065349 | 0.061788 | -0.0033496 | 0.0020336 | -0.0014355 | -0.26093 | 62.8647 | -60.0769 | 62.9333 | -59.816 | -60.1593 | 0.018311 | -0.19226 | 62.8693 | -59.967 | 63.0386 | -59.9258 | -60.0357 | -59.8251 | -0.15564 | -0.059509 | 0.009156 | 0.10529 | 59.9396 | -0.23804 | 60.0952 | -0.082398 | -0.045776 | -0.054931 | 0.11444 | -0.004577 | 0.096131 | -0.11444 | 0.14191 | -0.068665 | 0.26093 | 123.0103 | 0.041199 | 123.0057 | 122.9416 | 122.8363 | 122.7859 | 122.7905 | -123.0011 | -122.8912 | 122.8546 | 122.9599 | 59.6603 | 59.729
842.8281 | 123.1659 | -59.9213 | 62.9105 | -0.13672 | -0.00036966 | 0.063 | 0.067232 | 0.0051697 | -0.00056396 | -0.00054907 | -0.039948 | 0.0018072 | 0.063854 | 0.06072 | -0.0052722 | 0.0048108 | -0.00058107 | -0.21515 | 62.8418 | -60.0586 | 62.9791 | -59.7748 | -60.1685 | -0.022888 | -0.19684 | 62.8281 | -59.967 | 62.97 | -60.1089 | -59.7336 | -59.6741 | -0.13733 | -0.068664 | 0.068665 | 0.14648 | 59.8984 | -0.24719 | 60.0357 | -0.10986 | -0.045776 | -0.082397 | 0.05951 | -0.18768 | 0.24719 | 0.18768 | 0.29297 | 0.23346 | 0.28381 | 123.0377 | -0.14191 | 122.937 | 122.9004 | 122.7951 | 122.7631 | 122.7493 | -122.9691 | -122.8775 | 122.9004 | 122.8912 | 59.7061 | 59.7244
843.8906 | 123.0927 | -59.9442 | 62.9883 | -0.068054 | 0.00091214 | 0.062572 | 0.069795 | 0.0038879 | -0.0014184 | 0.0015871 | -0.14981 | 0.0033026 | 0.064281 | 0.067556 | -0.006554 | 0.0039562 | -0.0014355 | -0.21057 | 62.8967 | -60.0723 | 62.9517 | -59.8343 | -60.1868 | -0.032043 | -0.16479 | 62.8922 | -59.9762 | 63.0203 | -59.9762 | -60.0998 | -59.8984 | -0.12817 | -0.091552 | -0.036621 | 0.10986 | 59.9121 | -0.24262 | 60.0403 | -0.11444 | -0.032043 | -0.09613 | 0.032044 | -0.032043 | 0.045777 | -0.15564 | 0.07782 | -0.1236 | 0.23804 | 123.024 | 0 | 122.9965 | 122.9691 | 122.8683 | 122.8409 | 122.8363 | -123.0606 | -122.9645 | 122.8958 | 122.9645 | 59.7336 | 59.7794
844.8438 | 123.1064 | -59.9533 | 62.9745 | 0.00061049 | 0.0017667 | 0.063427 | 0.067872 | -0.0027343 | -0.00099116 | -0.0028989 | -0.0033265 | 0.0009528 | 0.06364 | 0.059439 | -0.0035632 | 0.0041698 | -0.0016493 | -0.16937 | 62.8647 | -60.0632 | 62.9974 | -59.7794 | -60.1227 | 0.11444 | -0.10986 | 62.9196 | -59.9854 | 63.0341 | -59.9258 | -60.0357 | -59.8709 | -0.10986 | -0.10986 | 0.022889 | 0.17395 | 60.0677 | -0.16937 | 60.1776 | -0.05951 | -0.032044 | -0.054931 | 0.05951 | 0.027466 | 0.082397 | -0.082398 | 0.11444 | -0.050354 | 0.28381 | 123.0606 | 0.05951 | 123.0194 | 122.9279 | 122.905 | 122.818 | 122.8729 | -123.0377 | -122.9599 | 122.9507 | 122.9874 | 59.7839 | 59.8434
845.8906 | 123.1613 | -59.9258 | 62.9288 | -0.068054 | 0.0028347 | 0.06535 | 0.066163 | 0.0011109 | -0.00035036 | -0.0016171 | -0.012482 | 9.8198e-05 | 0.06599 | 0.061788 | -0.0052722 | 0.0048108 | 0.0049731 | -0.24719 | 62.8326 | -60.0952 | 62.9471 | -59.7931 | -60.1959 | -0.009155 | -0.21057 | 62.8235 | -59.9716 | 63.0249 | -59.9533 | -60.0586 | -59.8709 | -0.16937 | -0.09613 | 0.018311 | 0.13275 | 59.9167 | -0.27008 | 60.0861 | -0.10071 | -0.045777 | -0.10529 | 0.09613 | -0.027466 | 0.054931 | -0.13275 | 0.10071 | -0.086975 | 0.30212 | 123.0423 | 0.018311 | 122.9965 | 122.9279 | 122.7951 | 122.7585 | 122.7493 | -123.024 | -122.9004 | 122.8729 | 122.9507 | 59.6787 | 59.7153
846.8281 | 123.2071 | -59.9258 | 62.915 | -0.098572 | 0.00091214 | 0.061932 | 0.069154 | 0.00046989 | -0.0014184 | 0.00051913 | -0.082672 | 0.0018072 | 0.064709 | 0.067983 | -0.0046314 | 0.0056652 | -0.0018629 | -0.29755 | 62.8601 | -60.0861 | 62.915 | -59.8709 | -60.2463 | -0.073242 | -0.27008 | 62.851 | -59.9808 | 63.0569 | -59.9991 | -60.0723 | -59.8297 | -0.16022 | -0.054932 | 0 | 0.054931 | 59.8526 | -0.32043 | 60.0128 | -0.16022 | -0.054932 | -0.064087 | 0.14191 | -0.073242 | 0.09613 | -0.14648 | 0.15106 | -0.091553 | 0.21515 | 123.0011 | -0.01831 | 123.0377 | 122.9462 | 122.8317 | 122.7859 | 122.7768 | -123.0011 | -122.8958 | 122.8409 | 122.9828 | 59.6283 | 59.6558
847.8906 | 123.0789 | -59.9533 | 62.9471 | -0.052796 | 0.0017667 | 0.062572 | 0.069154 | 0.00025629 | 0.0015722 | -0.0011899 | -0.076569 | 0.0028754 | 0.067486 | 0.058157 | -0.0061268 | 0.0041698 | 0.0017687 | -0.23346 | 62.8738 | -60.0998 | 62.9105 | -59.8801 | -60.2325 | -0.041199 | -0.23804 | 62.915 | -59.9716 | 62.97 | -60.022 | -60.1501 | -59.935 | -0.14648 | -0.073243 | -0.036622 | 0.073242 | 59.9121 | -0.27924 | 60.0586 | -0.13275 | -0.018311 | -0.032044 | 0.022888 | -0.068665 | 0.01831 | -0.19684 | 0.036621 | -0.17853 | 0.21973 | 123.0103 | -0.050354 | 122.9416 | 122.9736 | 122.8867 | 122.8271 | 122.8683 | -123.0469 | -122.9187 | 122.8638 | 122.9233 | 59.7198 | 59.7153
848.8281 | 123.1522 | -59.9579 | 62.9013 | -0.090943 | -0.00036966 | 0.062145 | 0.065095 | 0.00046989 | -0.0027002 | -0.00012167 | -0.021637 | 0.0020208 | 0.065777 | 0.060507 | -0.0046314 | 0.003529 | -0.00058107 | -0.25635 | 62.8464 | -60.0677 | 62.9654 | -59.7794 | -60.1593 | -0.022888 | -0.20142 | 62.8418 | -59.9945 | 63.0386 | -59.9396 | -60.0266 | -59.8663 | -0.10986 | -0.054931 | 0.064087 | 0.17853 | 59.935 | -0.20142 | 60.0449 | -0.091553 | -0.036621 | -0.059509 | 0.13733 | 0.018311 | 0.091553 | -0.068664 | 0.12817 | -0.032043 | 0.28839 | 123.0331 | 0.054932 | 123.0331 | 122.9141 | 122.8363 | 122.8043 | 122.7997 | -122.9691 | -122.8958 | 122.9233 | 122.9965 | 59.7015 | 59.7565
849.9062 | 123.111 | -59.9533 | 62.9608 | -0.029907 | 0.0026211 | 0.062572 | 0.068513 | 0.0015381 | 0.00071784 | -0.0016171 | -0.10098 | 0.0020208 | 0.06364 | 0.059011 | -0.0067676 | 0.0045972 | -0.0037855 | -0.17853 | 62.8967 | -60.0906 | 62.9196 | -59.8389 | -60.1913 | -0.013733 | -0.20142 | 62.883 | -59.967 | 62.9883 | -59.9991 | -60.1181 | -59.8984 | -0.13733 | -0.064086 | -0.041198 | 0.11444 | 59.9396 | -0.23804 | 60.0769 | -0.10071 | -0.013733 | -0.077819 | 0.027466 | -0.045776 | 0.054932 | -0.16479 | 0.068665 | -0.15106 | 0.25177 | 123.0103 | -0.032043 | 122.9553 | 122.9874 | 122.85 | 122.85 | 122.8363 | -123.0515 | -122.9279 | 122.8729 | 122.9416 | 59.7748 | 59.7519
850.8281 | 123.1796 | -59.9487 | 62.8922 | -0.098572 | 0.0015529 | 0.063213 | 0.068086 | -0.00038451 | 0.00029044 | -0.0033261 | 0.0027771 | 0.0009528 | 0.064709 | 0.053884 | -0.0052722 | 0.0026746 | 0.0015551 | -0.24719 | 62.8372 | -60.0586 | 62.9608 | -59.7702 | -60.1639 | -0.013733 | -0.1831 | 62.8372 | -59.9945 | 63.0478 | -59.9579 | -60.0494 | -59.8618 | -0.10986 | -0.054932 | 0.068664 | 0.17853 | 59.935 | -0.21515 | 60.0449 | -0.10529 | -0.045777 | -0.054932 | 0.15564 | -0.009156 | 0.086975 | -0.10071 | 0.13275 | -0.054931 | 0.28839 | 123.0194 | 0.036621 | 123.0423 | 122.8958 | 122.8317 | 122.7859 | 122.7859 | -122.9507 | -122.8867 | 122.9095 | 122.9965 | 59.7015 | 59.7656
851.8906 | 123.0972 | -59.9854 | 62.9517 | -0.12909 | 0.0032619 | 0.064709 | 0.067659 | -0.0020935 | -0.002273 | 0.00051913 | -0.088776 | 0.0026618 | 0.064495 | 0.066915 | -0.0042042 | 0.0060924 | 0.0021961 | -0.3067 | 62.8967 | -60.0952 | 62.8372 | -59.9579 | -60.3058 | -0.10071 | -0.33417 | 62.8876 | -59.9991 | 62.9471 | -60.0861 | -60.1868 | -59.9396 | -0.10986 | -0.054931 | -0.11444 | 0.027466 | 59.8846 | -0.32043 | 59.9945 | -0.21057 | -0.013732 | -0.064087 | -0.004577 | -0.10071 | 0.045777 | -0.20142 | 0.059509 | -0.18768 | 0.13733 | 122.9324 | -0.086976 | 122.9462 | 122.9919 | 122.8867 | 122.8821 | 122.8729 | -123.0469 | -122.9507 | 122.8226 | 122.9324 | 59.6786 | 59.6512
852.8281 | 123.0606 | -59.9854 | 62.9562 | -0.1062 | 0.0034757 | 0.062786 | 0.068086 | 0.0017517 | -0.0020594 | -0.00033547 | -0.10709 | 0.0037298 | 0.066204 | 0.065206 | -0.0037768 | 0.0045972 | -0.0012219 | -0.27008 | 62.9105 | -60.0861 | 62.8738 | -59.9075 | -60.2783 | -0.082397 | -0.31128 | 62.9105 | -59.9991 | 62.915 | -60.0403 | -60.173 | -59.9487 | -0.10071 | -0.045777 | -0.082398 | 0.07782 | 59.903 | -0.29297 | 60.0037 | -0.19226 | -0.013732 | -0.045777 | -0.041199 | -0.054931 | 0.036622 | -0.18768 | 0.050354 | -0.17395 | 0.17853 | 122.9599 | -0.041199 | 122.9141 | 122.9965 | 122.9095 | 122.8958 | 122.8958 | -123.0423 | -122.9553 | 122.8592 | 122.9004 | 59.7153 | 59.6741
853.8906 | 123.2025 | -59.9258 | 62.9379 | -0.090943 | 0.00091214 | 0.060436 | 0.066377 | -0.0010253 | 0.001145 | -0.0024717 | 0.057709 | 0.0043708 | 0.066204 | 0.062216 | -0.0046314 | 0.0039562 | -0.0074171 | -0.15564 | 62.8922 | -60.0174 | 63.0203 | -59.7153 | -60.0815 | 0.31128 | -0.29755 | 62.8876 | -59.967 | 63.0707 | -59.8572 | -59.9625 | -59.816 | -0.091553 | -0.045776 | 0.082398 | 0.21057 | 60.2371 | -0.15564 | 60.3287 | -0.064087 | -0.041199 | -0.050354 | 0.13275 | 0.068664 | 0.10986 | -0.036621 | 0.15106 | 0.004578 | 0.30212 | 123.0377 | 0.10986 | 123.0377 | 122.9095 | 122.8546 | 122.818 | 122.8134 | -122.9553 | -122.905 | 122.9462 | 122.9965 | 59.7702 | 59.6283
854.8281 | 123.1201 | -59.9579 | 62.9242 | -0.14435 | -0.00058326 | 0.063641 | 0.067659 | 4.2692e-05 | -0.0020594 | 0.0018009 | -0.058258 | 0.0033026 | 0.065136 | 0.06777 | -0.004845 | 0.0043836 | 0.00027333 | -0.31586 | 62.8784 | -60.1227 | 62.8601 | -59.8984 | -60.2783 | -0.07782 | -0.28839 | 62.8601 | -59.9854 | 62.9929 | -60.0174 | -60.1227 | -59.8846 | -0.16479 | -0.045776 | -0.064087 | 0.05951 | 59.8801 | -0.32043 | 60.0449 | -0.15564 | -0.027466 | -0.064087 | 0.068665 | -0.059509 | 0.073242 | -0.16479 | 0.10071 | -0.13733 | 0.22431 | 122.9828 | -0.032043 | 122.9782 | 123.0011 | 122.8455 | 122.8363 | 122.818 | -123.0469 | -122.9095 | 122.818 | 122.9507 | 59.642 | 59.6695
855.8906 | 123.1338 | -59.935 | 62.9883 | -0.098572 | 0.0013393 | 0.062786 | 0.067232 | -0.0033753 | -0.0020594 | -0.0020443 | 0.0088807 | -0.0001154 | 0.063854 | 0.062216 | -0.0052722 | 0.0033154 | -0.0025037 | -0.16022 | 62.9059 | -60.0403 | 62.9745 | -59.7702 | -60.0998 | 0.10529 | -0.10529 | 62.9013 | -59.9396 | 63.002 | -59.9442 | -60.0677 | -59.8572 | -0.10529 | -0.082397 | -0.013733 | 0.16479 | 60.0403 | -0.16479 | 60.1456 | -0.059509 | -0.004577 | -0.086975 | 0.013733 | -0.009155 | 0.07782 | -0.13275 | 0.082397 | -0.12817 | 0.27008 | 123.0148 | -0.004578 | 122.9416 | 122.9462 | 122.8409 | 122.8409 | 122.8363 | -123.0286 | -122.9279 | 122.9095 | 122.937 | 59.7748 | 59.8297
856.8281 | 123.1567 | -59.9533 | 62.9196 | -0.090943 | -0.00036966 | 0.062572 | 0.069154 | 0.00068369 | -0.0020594 | 0.00030553 | -0.042999 | 0.0045844 | 0.064068 | 0.062643 | -0.0059132 | 0.0060924 | 0.0021961 | -0.30212 | 62.8784 | -60.1089 | 62.8738 | -59.903 | -60.2646 | -0.091553 | -0.29755 | 62.8464 | -59.9854 | 63.002 | -59.9945 | -60.1089 | -59.8892 | -0.15564 | -0.041199 | -0.045777 | 0.050354 | 59.8618 | -0.31128 | 60.0174 | -0.15564 | -0.032044 | -0.073242 | 0.082397 | -0.041199 | 0.064087 | -0.15564 | 0.096131 | -0.1236 | 0.20599 | 122.9828 | -0.009155 | 122.9874 | 122.9874 | 122.8317 | 122.8317 | 122.7997 | -123.0286 | -122.905 | 122.8271 | 122.9553 | 59.6512 | 59.6558
857.8906 | 123.1018 | -59.9258 | 62.9837 | -0.12909 | 0.0013393 | 0.061932 | 0.067018 | 0.00046989 | -0.0041956 | -0.0026853 | -0.0002747 | 0.0020208 | 0.066418 | 0.056875 | -0.0044178 | 0.0031018 | -0.0033581 | -0.16022 | 62.9013 | -60.0266 | 62.9608 | -59.7748 | -60.1318 | 0.082397 | -0.11902 | 62.9105 | -59.9716 | 63.0066 | -59.9396 | -60.0632 | -59.8709 | -0.10071 | -0.082398 | -0.022889 | 0.15106 | 60.0082 | -0.20599 | 60.1089 | -0.10529 | -0.045777 | -0.073243 | 0.022888 | -0.013733 | 0.054931 | -0.13733 | 0.10071 | -0.091552 | 0.25177 | 122.9874 | 0.032044 | 122.9782 | 122.9279 | 122.8821 | 122.8271 | 122.8363 | -123.0103 | -122.9553 | 122.8867 | 122.9324 | 59.7656 | 59.8068
858.8281 | 123.1293 | -59.9487 | 62.9745 | -0.083313 | 0.0015529 | 0.062572 | 0.068086 | 0.0023925 | -0.0016322 | 0.0013735 | -0.039948 | 0.0028754 | 0.067699 | 0.069906 | -0.0042042 | 0.0048108 | -0.0012219 | -0.20599 | 62.915 | -60.0632 | 62.9196 | -59.8343 | -60.1639 | 0.050354 | -0.15564 | 62.9059 | -59.9716 | 63.0157 | -59.967 | -60.0861 | -59.8709 | -0.11444 | -0.059509 | -0.054931 | 0.11444 | 59.9991 | -0.21515 | 60.1135 | -0.10071 | -0.022889 | -0.068664 | 0.041199 | -0.018311 | 0.077819 | -0.13733 | 0.10071 | -0.11444 | 0.22888 | 122.9828 | 0.004578 | 122.9874 | 122.9782 | 122.8775 | 122.8638 | 122.8546 | -123.0377 | -122.9462 | 122.8683 | 122.9645 | 59.7427 | 59.7931
859.9062 | 123.1567 | -59.9762 | 62.9105 | -0.068054 | 0.0024075 | 0.062572 | 0.069154 | -0.0042297 | -0.0024866 | -0.0011899 | -0.049103 | 0.0009528 | 0.067486 | 0.06307 | -0.0078358 | 0.0041698 | -0.00079467 | -0.30212 | 62.883 | -60.0815 | 62.8784 | -59.8801 | -60.26 | -0.086975 | -0.27924 | 62.8647 | -59.9899 | 63.002 | -59.9854 | -60.0906 | -59.8801 | -0.10529 | -0.027465 | -0.032043 | 0.09613 | 59.8892 | -0.28381 | 59.9945 | -0.17853 | -0.013733 | -0.045776 | 0.091553 | -0.009156 | 0.09613 | -0.11444 | 0.10986 | -0.10071 | 0.20142 | 122.9599 | 0.004577 | 122.9919 | 122.9645 | 122.8546 | 122.8592 | 122.8409 | -122.9919 | -122.9004 | 122.8546 | 122.9782 | 59.6741 | 59.697
860.8281 | 123.1522 | -59.9625 | 62.9791 | -0.029907 | 0.0017667 | 0.062572 | 0.069154 | 0.0013245 | -0.0018458 | 0.00030553 | -0.027741 | 0.0009528 | 0.065136 | 0.064138 | -0.0046314 | 0.0041698 | 0.0015551 | -0.20142 | 62.9425 | -60.0632 | 62.8876 | -59.8663 | -60.1913 | 0.032043 | -0.19226 | 62.9105 | -59.9533 | 63.0066 | -59.9716 | -60.0723 | -59.8801 | -0.10071 | -0.036621 | -0.091553 | 0.09613 | 59.9945 | -0.22888 | 60.0952 | -0.12817 | 0.009155 | -0.068665 | 0.027466 | -0.009156 | 0.082397 | -0.10986 | 0.073242 | -0.11902 | 0.19684 | 122.9507 | -0.018311 | 122.9599 | 123.0057 | 122.8638 | 122.905 | 122.8729 | -123.0423 | -122.9324 | 122.85 | 122.9691 | 59.761 | 59.7702
861.8281 | 123.0835 | -59.9762 | 62.9517 | -0.12146 | 0.0015529 | 0.061932 | 0.068941 | -0.0016663 | -0.0020594 | -0.00054907 | -0.076569 | 0.0015936 | 0.066204 | 0.059439 | -0.0052722 | 0.003529 | 0.0015551 | -0.28381 | 62.9196 | -60.1089 | 62.8647 | -59.9396 | -60.2875 | -0.091553 | -0.33875 | 62.8922 | -60.0357 | 62.9288 | -60.0632 | -60.2051 | -59.9442 | -0.13275 | -0.032043 | -0.086975 | 0.036621 | 59.8846 | -0.31128 | 60.0174 | -0.17853 | -0.05951 | -0.059509 | -0.022888 | -0.086975 | 0.032043 | -0.22888 | 0.091553 | -0.16937 | 0.16937 | 122.9736 | -0.027465 | 122.9645 | 123.0286 | 122.9279 | 122.8958 | 122.8683 | -123.0606 | -122.9874 | 122.8409 | 122.905 | 59.6924 | 59.6375
862.8906 | 123.2254 | -59.9121 | 62.9379 | -0.052796 | 0.0013393 | 0.061718 | 0.066591 | -0.0014527 | -0.0012048 | -0.0033261 | 0.045502 | 0.0018072 | 0.065349 | 0.059011 | -0.0033496 | 0.0013928 | -0.0018629 | -0.21057 | 62.8784 | -60.0494 | 62.9654 | -59.7885 | -60.1318 | 0.073242 | -0.13733 | 62.8555 | -59.9579 | 63.0524 | -59.8938 | -59.9854 | -59.8022 | -0.13733 | -0.059509 | 0.027466 | 0.1236 | 59.9854 | -0.21973 | 60.1227 | -0.082398 | -0.045777 | -0.082397 | 0.11444 | 0.01831 | 0.10986 | -0.073243 | 0.15564 | -0.027466 | 0.26093 | 123.0148 | 0.064087 | 123.0103 | 122.9279 | 122.8134 | 122.7905 | 122.7676 | -122.9874 | -122.8958 | 122.8775 | 122.9645 | 59.7015 | 59.7748
863.8281 | 123.1384 | -59.9625 | 62.9654 | -0.068054 | 0.0026211 | 0.065777 | 0.066377 | -0.00017091 | 0.0013586 | 9.193e-05 | -0.058258 | 0.0026618 | 0.068554 | 0.068197 | -0.0052722 | 0.0056652 | -0.0016493 | -0.53101 | 62.8189 | -60.141 | 62.8281 | -59.903 | -60.26 | -0.12817 | -0.31586 | 62.883 | -60.0037 | 62.9517 | -60.0449 | -60.1547 | -59.9304 | -0.17853 | -0.14648 | -0.13733 | 0.059509 | 59.8343 | -0.29755 | 60.0128 | -0.11902 | -0.041199 | -0.082397 | -0.013733 | -0.082398 | 0.032043 | -0.19226 | 0.073242 | -0.15106 | 0.23804 | 122.9691 | -0.041199 | 122.9553 | 122.9599 | 122.8867 | 122.7814 | 122.8455 | -123.1064 | -122.9691 | 122.7905 | 122.9141 | 59.4315 | 59.6466
864.9062 | 123.1018 | -59.967 | 62.9608 | -0.068054 | -0.00015586 | 0.063427 | 0.067232 | 0.0011109 | 7.6842e-05 | -0.0016171 | -0.06131 | 0.0028754 | 0.067272 | 0.06307 | -0.004845 | 0.0041698 | 5.9726e-05 | -0.26093 | 62.9059 | -60.1044 | 62.8967 | -59.8846 | -60.26 | -0.045776 | -0.25635 | 62.9059 | -59.9945 | 62.9608 | -60.0403 | -60.1501 | -59.9442 | -0.13733 | -0.054931 | -0.064086 | 0.082397 | 59.9213 | -0.29297 | 60.0586 | -0.15564 | -0.027466 | -0.054931 | 0 | -0.073242 | 0.022888 | -0.1831 | 0.050354 | -0.15564 | 0.21973 | 123.0011 | -0.045776 | 122.9553 | 123.0103 | 122.9004 | 122.8729 | 122.8729 | -123.0652 | -122.9553 | 122.8638 | 122.9279 | 59.7061 | 59.7107
865.8281 | 123.0469 | -59.9945 | 62.9837 | -0.11383 | 0.0013393 | 0.063213 | 0.066163 | 0.0032471 | 7.6842e-05 | -0.00033547 | -0.06131 | 0.0024482 | 0.064709 | 0.066061 | -0.0052722 | 0.0039562 | 0.00048713 | -0.26093 | 62.8967 | -60.0906 | 62.8601 | -59.903 | -60.2554 | -0.082397 | -0.29755 | 62.9105 | -60.0082 | 62.9562 | -60.0586 | -60.1868 | -59.9396 | -0.09613 | -0.086975 | -0.1236 | 0.091553 | 59.9121 | -0.26093 | 60.0082 | -0.16479 | -0.013733 | -0.073243 | -0.027466 | -0.064087 | 0.054932 | -0.19226 | 0.068665 | -0.17853 | 0.18768 | 122.9507 | -0.050354 | 122.9645 | 122.9874 | 122.9187 | 122.8912 | 122.905 | -123.0743 | -122.9919 | 122.8546 | 122.9507 | 59.7336 | 59.697
866.8906 | 123.2254 | -59.9167 | 62.9333 | -0.068054 | -0.00079686 | 0.062359 | 0.065095 | 0.0021789 | -0.0044092 | -0.0026853 | 0.048553 | 0.0024482 | 0.066845 | 0.060507 | -0.0046314 | 0.0041698 | 0.0017687 | -0.23346 | 62.8738 | -60.0403 | 62.9471 | -59.7977 | -60.1456 | 0.032043 | -0.15106 | 62.8555 | -59.9625 | 63.0432 | -59.8938 | -60.0082 | -59.8251 | -0.1236 | -0.05951 | 0.013733 | 0.11902 | 59.9487 | -0.22888 | 60.0723 | -0.10529 | -0.045776 | -0.07782 | 0.10986 | 0.022888 | 0.091553 | -0.091553 | 0.13733 | -0.045777 | 0.24262 | 122.9874 | 0.068664 | 123.0057 | 122.9141 | 122.818 | 122.7905 | 122.7722 | -122.9736 | -122.8958 | 122.8638 | 122.9599 | 59.6832 | 59.7656
867.8281 | 123.111 | -59.9579 | 62.9517 | -0.12909 | 0.0024075 | 0.062359 | 0.069368 | -0.0012391 | -0.0020594 | 0.00094633 | -0.055206 | 0.003089 | 0.066204 | 0.058798 | -0.0059132 | 0.0050244 | -0.0029309 | -0.23346 | 62.8967 | -60.0906 | 62.8967 | -59.8572 | -60.2371 | -0.045776 | -0.24261 | 62.9105 | -59.9762 | 62.9745 | -60.0311 | -60.1364 | -59.9396 | -0.13275 | -0.054931 | -0.054931 | 0.10071 | 59.9121 | -0.27924 | 60.0449 | -0.14648 | -0.01831 | -0.041199 | 0.022888 | -0.073242 | 0.018311 | -0.17853 | 0.036621 | -0.16022 | 0.23346 | 122.9874 | -0.054932 | 122.9507 | 122.9874 | 122.8867 | 122.8546 | 122.8683 | -123.0423 | -122.9279 | 122.8546 | 122.9324 | 59.7244 | 59.7153
868.8906 | 123.23 | -59.9396 | 62.9654 | -0.083313 | 0.00027134 | 0.061077 | 0.066163 | -0.0016663 | 0.00029044 | -0.0014035 | 0.045502 | 0.0018072 | 0.064068 | 0.057302 | -0.0052722 | 0.0013928 | -0.00058107 | -0.22888 | 62.883 | -60.0403 | 62.97 | -59.7839 | -60.1227 | 0.07782 | -0.11902 | 62.8418 | -59.9304 | 63.0753 | -59.8892 | -59.9762 | -59.816 | -0.10071 | -0.082397 | 0.004578 | 0.15564 | 60.0174 | -0.18311 | 60.1181 | -0.082398 | 0.009155 | -0.1236 | 0.10986 | 0.050354 | 0.1236 | -0.036621 | 0.11444 | -0.045776 | 0.25635 | 123.0103 | 0.041199 | 123.0057 | 122.9233 | 122.7722 | 122.8226 | 122.7814 | -123.0057 | -122.8958 | 122.9095 | 123.0148 | 59.7107 | 59.8206
869.8281 | 123.2071 | -59.9396 | 62.9059 | -0.083313 | 0.0015529 | 0.064068 | 0.067232 | 0.0062379 | -0.0014184 | 0.00051913 | -0.012482 | 0.0005256 | 0.063854 | 0.063497 | -0.0061268 | 0.0039562 | 0.0013415 | -0.26093 | 62.8372 | -60.0906 | 62.9745 | -59.8068 | -60.1639 | -0.027466 | -0.21515 | 62.8464 | -59.967 | 63.0386 | -59.9304 | -60.0403 | -59.8206 | -0.15106 | -0.068665 | 0.068664 | 0.13275 | 59.9121 | -0.2243 | 60.0632 | -0.073242 | -0.027466 | -0.059509 | 0.13275 | 0.009155 | 0.11902 | -0.10071 | 0.14648 | -0.073242 | 0.28381 | 123.0652 | 0.036621 | 123.0057 | 122.9279 | 122.8134 | 122.7768 | 122.7859 | -122.9965 | -122.8729 | 122.9141 | 122.9782 | 59.6786 | 59.7244
870.8906 | 123.1522 | -59.9121 | 62.9791 | -0.052796 | -0.00015586 | 0.062359 | 0.068727 | -0.0012391 | -0.0029138 | 0.0024417 | -0.030792 | 0.003089 | 0.067913 | 0.058798 | -0.0054858 | 0.0026746 | -0.00036747 | -0.21057 | 62.9105 | -60.0632 | 62.8967 | -59.8572 | -60.1868 | 0.054932 | -0.16937 | 62.9196 | -59.9716 | 63.0112 | -59.9579 | -60.1044 | -59.8755 | -0.15106 | -0.068665 | -0.082397 | 0.054931 | 59.967 | -0.27466 | 60.1181 | -0.1236 | -0.05951 | -0.059509 | 0.032043 | -0.045777 | 0.036621 | -0.19226 | 0.096131 | -0.13275 | 0.20599 | 122.9599 | 0.013733 | 122.9828 | 122.9736 | 122.8912 | 122.8226 | 122.8317 | -123.0423 | -122.9507 | 122.8088 | 122.9233 | 59.7015 | 59.7427
871.8281 | 123.0881 | -59.9625 | 62.9837 | -0.090943 | 0.0026211 | 0.061077 | 0.067659 | 0.0053833 | -0.0016322 | -0.0028989 | -0.076569 | 0.0026618 | 0.065563 | 0.067343 | -0.0078358 | 0.0039562 | -0.0033581 | -0.27008 | 62.8876 | -60.0998 | 62.851 | -59.9487 | -60.2875 | -0.09613 | -0.32959 | 62.9105 | -59.9991 | 62.9242 | -60.0815 | -60.1913 | -59.9625 | -0.13733 | -0.096131 | -0.13275 | 0.013733 | 59.8663 | -0.32501 | 60.0037 | -0.18768 | -0.036621 | -0.073243 | -0.05951 | -0.11902 | 0 | -0.22888 | 0.036621 | -0.19226 | 0.15106 | 122.9507 | -0.082398 | 122.9233 | 122.9874 | 122.9095 | 122.85 | 122.8729 | -123.0835 | -122.9828 | 122.8134 | 122.8867 | 59.6924 | 59.6329
872.8906 | 123.1018 | -59.9213 | 63.0066 | -0.037537 | 0.0032619 | 0.063427 | 0.065095 | -0.00038451 | -0.00013676 | 9.193e-05 | 0.011932 | 0.0007392 | 0.064709 | 0.059225 | -0.0035632 | 0.0033154 | -0.0010083 | -0.16937 | 62.9013 | -60.0449 | 62.9471 | -59.8022 | -60.141 | 0.09613 | -0.11444 | 62.915 | -59.9442 | 62.97 | -59.9396 | -60.0128 | -59.8709 | -0.1236 | -0.10529 | -0.059509 | 0.11902 | 60.0174 | -0.21973 | 60.141 | -0.09613 | -0.022888 | -0.091553 | -0.036621 | -0.01831 | 0.050354 | -0.091552 | 0.073242 | -0.068664 | 0.24262 | 122.9919 | 0.004578 | 122.9141 | 122.9462 | 122.8592 | 122.8226 | 122.8363 | -123.0515 | -122.9507 | 122.8683 | 122.8912 | 59.7519 | 59.8068
873.8281 | 123.1201 | -59.9442 | 62.9608 | -0.060425 | 0.0015529 | 0.064068 | 0.068513 | 0.0038879 | -0.0018458 | -0.00054907 | -0.058258 | 0.0020208 | 0.064922 | 0.063284 | -0.0042042 | 0.0063062 | -0.0046399 | -0.19226 | 62.883 | -60.1044 | 62.9242 | -59.8114 | -60.2142 | 0.013733 | -0.17853 | 62.8922 | -59.9762 | 63.002 | -59.9808 | -60.1044 | -59.8984 | -0.16022 | -0.077819 | -0.036621 | 0.13275 | 59.9579 | -0.27008 | 60.1181 | -0.10986 | -0.032043 | -0.068664 | 0.041199 | -0.036621 | 0.045777 | -0.16022 | 0.07782 | -0.12817 | 0.29297 | 123.0286 | -0.004578 | 122.9782 | 122.9874 | 122.8683 | 122.8271 | 122.8363 | -123.0652 | -122.937 | 122.8683 | 122.9462 | 59.7519 | 59.7656
874.8281 | 123.0743 | -59.9625 | 62.9974 | -0.052796 | 0.0019803 | 0.061718 | 0.068941 | -0.0023071 | -0.0029138 | -0.0039671 | -0.021637 | 0.003089 | 0.069408 | 0.059011 | -0.0063404 | 0.0033154 | 0.0032641 | -0.24261 | 62.9425 | -60.0586 | 62.8876 | -59.8618 | -60.1959 | 0.041199 | -0.18768 | 62.9242 | -59.9899 | 62.9379 | -60.1501 | -60.1181 | -59.8846 | -0.096131 | -0.054932 | -0.10986 | 0.10071 | 60.0037 | -0.23346 | 60.0998 | -0.13733 | -0.027466 | -0.073243 | -0.05951 | -0.18768 | 0.077819 | -0.15564 | 0.10528 | -0.12817 | 0.19684 | 122.9462 | -0.16022 | 122.9279 | 123.0011 | 122.9141 | 122.905 | 122.8867 | -123.056 | -122.9874 | 122.85 | 122.9004 | 59.7198 | 59.7748
875.8906 | 123.1796 | -59.9075 | 62.9608 | -0.16724 | 0.0032619 | 0.063 | 0.066163 | -0.00081171 | -0.002273 | 0.00030553 | 0.030243 | 9.8198e-05 | 0.065349 | 0.059011 | -0.0056994 | 0.005238 | -0.0022901 | -0.16022 | 62.8967 | -60.0357 | 63.002 | -59.7382 | -60.0952 | 0.1236 | -0.07782 | 62.8876 | -59.9442 | 63.0478 | -59.8846 | -59.9991 | -59.816 | -0.12817 | -0.064086 | 0.041199 | 0.16937 | 60.0311 | -0.18768 | 60.1593 | -0.059509 | -0.036621 | -0.073242 | 0.086976 | 0.022888 | 0.091553 | -0.091552 | 0.12817 | -0.054931 | 0.29755 | 123.0377 | 0.059509 | 122.9919 | 122.9324 | 122.8317 | 122.8043 | 122.7951 | -122.9965 | -122.905 | 122.9095 | 122.9553 | 59.7473 | 59.8297
876.8281 | 123.1705 | -59.9396 | 62.9517 | -0.075684 | 0.0024075 | 0.063854 | 0.0683 | 0.0017517 | -0.0041956 | -0.0039671 | -0.058258 | 0.00138 | 0.067058 | 0.065206 | -0.0052722 | 0.0033154 | 0.00048713 | -0.1831 | 62.9242 | -60.0769 | 62.9333 | -59.8206 | -60.1593 | 0.027466 | -0.14191 | 62.8967 | -59.9716 | 63.0112 | -59.9579 | -60.0998 | -59.8618 | -0.13733 | -0.027466 | -0.01831 | 0.11902 | 59.967 | -0.21973 | 60.1044 | -0.082398 | -0.032044 | -0.054931 | 0.059509 | -0.018311 | 0.07782 | -0.16022 | 0.10986 | -0.12817 | 0.25635 | 123.0103 | 0.013733 | 122.9828 | 123.0011 | 122.8683 | 122.8638 | 122.8363 | -123.0286 | -122.9233 | 122.8729 | 122.9507 | 59.7565 | 59.7977
877.8906 | 123.1064 | -59.935 | 62.9974 | -0.075684 | 0.0017667 | 0.062359 | 0.065523 | -0.0035889 | -0.0035548 | -0.0022581 | 0.014984 | 9.8198e-05 | 0.066845 | 0.064352 | -0.0029224 | 0.0013928 | -0.00015387 | -0.20599 | 62.9608 | -60.0449 | 62.9379 | -59.848 | -60.2188 | 0.059509 | -0.16937 | 62.9288 | -59.9579 | 62.9517 | -59.9854 | -60.0906 | -59.9213 | -0.10986 | -0.036622 | -0.05951 | 0.086976 | 59.9945 | -0.28381 | 60.1044 | -0.17395 | -0.022888 | -0.068665 | -0.045777 | -0.050354 | 0.013733 | -0.15564 | 0.036621 | -0.13275 | 0.19684 | 122.9828 | -0.027466 | 122.9095 | 123.0057 | 122.8867 | 122.8958 | 122.8638 | -123.0423 | -122.9553 | 122.8729 | 122.8867 | 59.729 | 59.7656
878.8281 | 123.1247 | -59.935 | 62.9929 | -0.037537 | 0.0030483 | 0.060009 | 0.066163 | -0.00017091 | -0.0046228 | -0.0020443 | 0.014984 | 0.0011664 | 0.06364 | 0.064138 | -0.0054858 | 0.0031018 | 0.00091433 | -0.16479 | 62.8922 | -60.0357 | 62.9654 | -59.7748 | -60.1318 | 0.10986 | -0.1236 | 62.9425 | -59.967 | 62.9929 | -59.9442 | -60.0586 | -59.8846 | -0.10071 | -0.10071 | -0.027466 | 0.16022 | 60.0449 | -0.19684 | 60.1456 | -0.09613 | -0.032043 | -0.050354 | 0 | -0.009155 | 0.050354 | -0.1236 | 0.082397 | -0.091553 | 0.26093 | 123.0011 | 0.022888 | 122.9599 | 122.9279 | 122.9095 | 122.8271 | 122.8775 | -123.0286 | -122.9599 | 122.9004 | 122.9279 | 59.7702 | 59.8114
879.9062 | 123.1384 | -59.9304 | 63.002 | -0.060425 | 0.0019803 | 0.063854 | 0.070436 | 0.0062379 | -0.0014184 | -0.0024717 | -0.076569 | 0.0033026 | 0.065136 | 0.064779 | -0.0061268 | 0.006947 | -0.0046399 | -0.20599 | 62.8967 | -60.0677 | 62.9379 | -59.8297 | -60.173 | 0.032043 | -0.15564 | 62.9013 | -59.9808 | 62.9562 | -60.0494 | -60.0128 | -59.8663 | -0.13733 | -0.10529 | -0.064087 | 0.10071 | 59.9625 | -0.24262 | 60.0998 | -0.10529 | -0.050354 | -0.10071 | -0.045776 | -0.11902 | 0.064087 | -0.082397 | 0.11444 | -0.032043 | 0.23804 | 123.0057 | -0.068664 | 122.937 | 122.9645 | 122.8821 | 122.8271 | 122.8317 | -123.0698 | -122.9828 | 122.8683 | 122.8867 | 59.7244 | 59.7748
880.8281 | 123.2025 | -59.9167 | 62.97 | -0.14435 | 0.00091214 | 0.061718 | 0.066591 | -0.0010253 | -0.00077756 | 0.00051913 | 0.054657 | 0.0005256 | 0.067486 | 0.064138 | -0.0050586 | 0.0024608 | -0.0027173 | -0.14648 | 62.8738 | -60.0357 | 62.9883 | -59.7382 | -60.0861 | 0.13275 | -0.082397 | 62.9013 | -59.9487 | 63.0478 | -59.903 | -60.0037 | -59.8343 | -0.11902 | -0.096131 | 0.01831 | 0.17853 | 60.0494 | -0.16937 | 60.1685 | -0.050354 | -0.032043 | -0.068665 | 0.07782 | 0.013733 | 0.082397 | -0.086975 | 0.11444 | -0.054932 | 0.29755 | 123.024 | 0.045776 | 122.9965 | 122.9095 | 122.85 | 122.7905 | 122.818 | -123.0057 | -122.9187 | 122.905 | 122.9645 | 59.7702 | 59.8343
881.8281 | 123.0743 | -59.9625 | 63.0157 | -0.15198 | 0.0021939 | 0.059368 | 0.067232 | 0.0032471 | -0.0024866 | -0.0041807 | -0.049103 | 0.0022346 | 0.067913 | 0.060507 | -0.003136 | 0.0028882 | -0.0012219 | -0.17853 | 62.9333 | -60.0723 | 62.9059 | -59.8755 | -60.2142 | 0.022888 | -0.18768 | 62.9333 | -59.9762 | 62.9654 | -59.9899 | -60.0906 | -59.8938 | -0.10986 | -0.082397 | -0.10986 | 0.086975 | 59.9854 | -0.25177 | 60.0952 | -0.14191 | -0.013733 | -0.082397 | -0.050354 | -0.027466 | 0.068664 | -0.12817 | 0.082397 | -0.11444 | 0.19684 | 122.9782 | -0.013733 | 122.9416 | 123.0057 | 122.9095 | 122.8958 | 122.8958 | -123.0881 | -122.9919 | 122.8683 | 122.9279 | 59.7839 | 59.7748
882.8906 | 123.2117 | -60.0128 | 62.8876 | -0.029907 | 0.00091214 | 0.063427 | 0.068727 | 0.0019653 | -0.0014184 | -0.00076267 | -0.073517 | 0.0028754 | 0.064922 | 0.062002 | -0.0056994 | 0.0058788 | -0.0020765 | -0.31586 | 62.883 | -60.1089 | 62.8372 | -59.9533 | -60.3058 | -0.091553 | -0.32501 | 62.9105 | -60.022 | 62.9425 | -60.0586 | -60.173 | -59.9533 | -0.096131 | -0.004577 | -0.050354 | 0.059509 | 59.9213 | -0.29297 | 60.0174 | -0.19684 | -0.009156 | 0.022888 | 0.054932 | -0.045777 | 0.059509 | -0.16022 | 0.068665 | -0.15106 | 0.15564 | 122.9462 | -0.036621 | 122.9645 | 122.9919 | 122.9324 | 122.8958 | 122.9233 | -122.9965 | -122.9095 | 122.85 | 122.9553 | 59.697 | 59.6878
883.8281 | 123.1293 | -59.9625 | 62.9608 | -0.022278 | 0.0032619 | 0.06535 | 0.067232 | 0.00068369 | -0.003982 | 0.00051913 | -0.042999 | 0.0024482 | 0.065349 | 0.063925 | -0.0059132 | 0.0048108 | -0.00015387 | -0.21057 | 62.8922 | -60.0723 | 62.9288 | -59.8206 | -60.1868 | -0.091553 | -0.1831 | 62.9196 | -59.9808 | 63.0112 | -59.9762 | -60.0861 | -59.8709 | -0.10986 | -0.068664 | -0.032043 | 0.14191 | 59.8709 | -0.22431 | 59.9808 | -0.11444 | -0.018311 | -0.041198 | 0.050354 | -0.013733 | 0.091552 | -0.1236 | 0.10986 | -0.10529 | 0.25177 | 123.0011 | 0.004578 | 122.9919 | 122.9645 | 122.9004 | 122.8546 | 122.8821 | -123.0331 | -122.9416 | 122.8912 | 122.9736 | 59.7519 | 59.7794
884.8906 | 123.2025 | -59.9167 | 62.9929 | -0.052796 | 0.0017667 | 0.061077 | 0.066377 | -0.0012391 | 0.0013586 | -0.0024717 | 0.051605 | 0.0018072 | 0.066418 | 0.058798 | -0.0033496 | 0.0039562 | 0.00048713 | -0.16937 | 62.8876 | -60.0449 | 63.0341 | -59.6786 | -60.0632 | 0.10529 | -0.054932 | 62.8693 | -59.9396 | 63.0844 | -59.8709 | -59.9625 | -59.7885 | -0.12817 | -0.10529 | 0.041199 | 0.23804 | 60.022 | -0.14648 | 60.1501 | -0.01831 | -0.022888 | -0.1236 | 0.091553 | 0.045776 | 0.12817 | -0.045776 | 0.15106 | -0.022888 | 0.36621 | 123.0789 | 0.068664 | 123.024 | 122.9324 | 122.8088 | 122.8043 | 122.7859 | -123.0377 | -122.9324 | 122.9507 | 123.0011 | 59.7473 | 59.8618
885.8281 | 123.1338 | -59.9487 | 62.9745 | -0.1062 | 0.00048494 | 0.063 | 0.068941 | -0.00038451 | -0.0016322 | -0.0024717 | -0.055206 | 0.0011664 | 0.067058 | 0.069052 | -0.0050586 | 0.0037426 | -0.00036747 | -0.18768 | 62.8967 | -60.0815 | 62.9288 | -59.8251 | -60.1822 | 0.041199 | -0.15106 | 62.8967 | -59.967 | 63.0112 | -59.9533 | -60.0815 | -59.8618 | -0.13275 | -0.077819 | -0.045776 | 0.1236 | 59.9899 | -0.23346 | 60.1227 | -0.10071 | -0.018311 | -0.077819 | 0.036621 | -0.004578 | 0.086975 | -0.13275 | 0.10529 | -0.11444 | 0.25635 | 123.0103 | 0.013733 | 122.9782 | 122.9782 | 122.8638 | 122.8455 | 122.8455 | -123.056 | -122.9416 | 122.8775 | 122.9599 | 59.761 | 59.7977
886.8906 | 123.1888 | -59.903 | 62.9562 | -0.052796 | -0.00015586 | 0.062359 | 0.064882 | -0.0052979 | -0.0024866 | -0.0035397 | 0.04245 | 0.0024482 | 0.064922 | 0.05837 | -0.0039906 | 0.0013928 | 0.0011279 | -0.25177 | 62.8784 | -60.054 | 62.9379 | -59.8068 | -60.141 | 0.045776 | -0.1831 | 62.8693 | -59.9625 | 63.0569 | -59.903 | -60.0128 | -59.8251 | -0.15106 | -0.07782 | -0.018311 | 0.09613 | 59.9487 | -0.23804 | 60.0998 | -0.086975 | -0.059509 | -0.086975 | 0.10071 | 0 | 0.07782 | -0.10986 | 0.13733 | -0.050354 | 0.24719 | 122.9919 | 0.059509 | 123.0194 | 122.9324 | 122.8317 | 122.7814 | 122.7722 | -123.0103 | -122.9187 | 122.8409 | 122.9599 | 59.6512 | 59.7198
887.8281 | 123.0743 | -59.9442 | 63.0112 | -0.045166 | 0.0015529 | 0.061718 | 0.067445 | 4.2692e-05 | -0.0037684 | -0.0022581 | -0.018585 | 0.0020208 | 0.064495 | 0.062429 | -0.0054858 | 0.0031018 | -0.0022901 | -0.23346 | 62.9471 | -60.054 | 62.883 | -59.8755 | -60.2142 | 0.050354 | -0.18768 | 62.9242 | -59.967 | 62.9379 | -60.0037 | -60.0952 | -59.9167 | -0.10986 | -0.064086 | -0.12817 | 0.068665 | 59.9945 | -0.27008 | 60.1044 | -0.16022 | -0.022888 | -0.086975 | -0.073242 | -0.059509 | 0.027466 | -0.15106 | 0.050354 | -0.12817 | 0.17853 | 122.937 | -0.036621 | 122.905 | 123.0011 | 122.8912 | 122.8912 | 122.8683 | -123.0652 | -122.9782 | 122.8271 | 122.8821 | 59.7107 | 59.7565
888.8906 | 123.1842 | -59.9258 | 62.915 | -0.083313 | 0.00027134 | 0.065136 | 0.0683 | 0.0011109 | -0.0037684 | -0.0022581 | -0.055206 | 0.0009528 | 0.06364 | 0.063925 | -0.0061268 | 0.0031018 | -0.0037855 | -0.29755 | 62.8601 | -60.0906 | 62.9288 | -59.8343 | -60.173 | -0.036621 | -0.21973 | 62.8601 | -59.9945 | 63.0432 | -59.9396 | -60.0403 | -59.8251 | -0.16479 | -0.054932 | 0.013733 | 0.091552 | 59.8892 | -0.24719 | 60.054 | -0.082398 | -0.068665 | -0.054932 | 0.12817 | -0.013733 | 0.10071 | -0.11444 | 0.16937 | -0.045776 | 0.25635 | 123.0194 | 0.054932 | 123.0377 | 122.9507 | 122.8546 | 122.7859 | 122.7859 | -123.0057 | -122.9095 | 122.8546 | 122.9691 | 59.6283 | 59.7061
889.8281 | 123.1476 | -59.935 | 62.9562 | -0.083313 | 0.0024075 | 0.062359 | 0.068086 | 0.0019653 | 7.6842e-05 | -0.0014035 | -0.073517 | 0.0026618 | 0.065563 | 0.068624 | -0.0076222 | 0.0043836 | -0.0010083 | -0.19226 | 62.915 | -60.0723 | 62.9471 | -59.8389 | -60.1639 | 0.036621 | -0.15106 | 62.8922 | -59.9579 | 63.0066 | -59.9533 | -60.0769 | -59.8709 | -0.13733 | -0.041199 | -0.009155 | 0.096131 | 59.9716 | -0.22888 | 60.1089 | -0.091552 | -0.022888 | -0.064087 | 0.050354 | -0.01831 | 0.064087 | -0.14191 | 0.086975 | -0.11902 | 0.23346 | 123.0194 | 0.004578 | 122.9645 | 122.9874 | 122.85 | 122.85 | 122.8271 | -123.0286 | -122.9141 | 122.8821 | 122.9416 | 59.7427 | 59.7839
890.8906 | 123.2071 | -59.9213 | 62.9471 | -0.045166 | 0.0015529 | 0.062359 | 0.066163 | 0.0011109 | -0.0027002 | -0.0011899 | 0.021088 | 0.0007392 | 0.067486 | 0.060934 | -0.0056994 | 0.0039562 | -0.00058107 | -0.23804 | 62.8784 | -60.0677 | 62.9333 | -59.7977 | -60.1547 | 0.032043 | -0.17395 | 62.8647 | -59.9716 | 63.0295 | -59.9213 | -60.0082 | -59.8251 | -0.14648 | -0.068665 | -0.013733 | 0.1236 | 59.9533 | -0.23346 | 60.0998 | -0.086975 | -0.050354 | -0.082398 | 0.082397 | 0 | 0.096131 | -0.086975 | 0.14648 | -0.036621 | 0.27008 | 123.0011 | 0.050354 | 123.0011 | 122.9462 | 122.8363 | 122.7997 | 122.7859 | -123.0148 | -122.9187 | 122.8546 | 122.9507 | 59.6832 | 59.7473
891.8281 | 123.1384 | -59.935 | 62.9745 | -0.098572 | -0.00079686 | 0.062786 | 0.0683 | 0.00068369 | -0.0014184 | -0.0035397 | -0.049103 | 0.0015936 | 0.067486 | 0.064779 | -0.0037768 | 0.0056652 | -0.0014355 | -0.19684 | 62.9288 | -60.0632 | 62.9379 | -59.8297 | -60.1776 | 0.041199 | -0.13733 | 62.9288 | -59.9579 | 63.0112 | -59.9533 | -60.0815 | -59.8709 | -0.12817 | -0.045776 | -0.036621 | 0.10529 | 59.9762 | -0.24261 | 60.1044 | -0.11444 | -0.022888 | -0.045776 | 0.036621 | -0.01831 | 0.064087 | -0.14648 | 0.086975 | -0.1236 | 0.23346 | 123.0011 | 0.004578 | 122.9691 | 122.9919 | 122.8867 | 122.8638 | 122.8638 | -123.0377 | -122.9324 | 122.8729 | 122.9462 | 59.7382 | 59.7977
892.8906 | 123.175 | -59.9396 | 62.9013 | -0.12146 | 0.0015529 | 0.063213 | 0.066804 | 0.0036743 | -0.0018458 | -0.00097627 | -0.0063781 | 0.0026618 | 0.069195 | 0.055593 | -0.004845 | 0.0028882 | -0.0016493 | -0.24719 | 62.851 | -60.0586 | 62.9517 | -59.8022 | -60.173 | -0.009155 | -0.21057 | 62.8464 | -59.9808 | 63.0157 | -59.9533 | -60.0632 | -59.8663 | -0.11902 | -0.050354 | 0.050354 | 0.13733 | 59.9304 | -0.23346 | 60.0494 | -0.11444 | -0.041199 | -0.054931 | 0.11444 | -0.013733 | 0.073242 | -0.1236 | 0.11444 | -0.082397 | 0.25635 | 123.0103 | 0.027466 | 122.9965 | 122.9095 | 122.8271 | 122.7905 | 122.7859 | -122.9599 | -122.8821 | 122.8912 | 122.9553 | 59.6924 | 59.729
893.8281 | 123.0881 | -59.9487 | 62.9883 | -0.037537 | -0.0012241 | 0.061077 | 0.067872 | -0.0012391 | -0.0031274 | -0.00097627 | -0.030792 | 0.0022346 | 0.066631 | 0.063925 | -0.0050586 | 0.0031018 | -0.00015387 | -0.28839 | 62.9425 | -60.0311 | 62.8326 | -59.8846 | -60.1776 | 0.004578 | -0.20599 | 62.9333 | -59.9854 | 62.97 | -60.0082 | -60.1044 | -59.8938 | -0.082398 | -0.045776 | -0.15564 | 0.064086 | 59.9533 | -0.22888 | 60.0357 | -0.14648 | -0.036622 | -0.054931 | -0.01831 | -0.05951 | 0.054931 | -0.15564 | 0.091553 | -0.11902 | 0.14648 | 122.8638 | -0.022888 | 122.9553 | 122.9736 | 122.9187 | 122.8912 | 122.8821 | -123.0194 | -122.9736 | 122.7814 | 122.9187 | 59.6603 | 59.7427
894.8906 | 123.1842 | -59.9304 | 62.9105 | -0.15961 | 0.0028347 | 0.063641 | 0.067445 | 4.2692e-05 | -0.0012048 | -0.00033547 | -0.018585 | 0.0007392 | 0.067272 | 0.064565 | -0.0054858 | 0.0026746 | 0.0024097 | -0.24261 | 62.8189 | -60.0586 | 62.9562 | -59.7748 | -60.1593 | -0.013733 | -0.19684 | 62.8464 | -59.9808 | 63.1577 | -60.0082 | -59.9762 | -59.7931 | -0.12817 | -0.091552 | 0.045777 | 0.15564 | 59.9167 | -0.22888 | 60.0449 | -0.10071 | -0.050354 | -0.064086 | 0.24719 | -0.07782 | 0.13733 | -0.045776 | 0.18768 | 0.004578 | 0.28381 | 123.0148 | -0.027466 | 123.1384 | 122.8775 | 122.8271 | 122.7493 | 122.7768 | -122.9691 | -122.8912 | 122.8867 | 123.0881 | 59.6878 | 59.7336
895.8281 | 123.1247 | -59.9579 | 62.9654 | -0.083313 | 0.0011257 | 0.062572 | 0.070222 | 0.0036743 | 0.001145 | 0.00094633 | -0.058258 | 0.0011664 | 0.066418 | 0.060293 | -0.0054858 | 0.0037426 | 0.0026233 | -0.18768 | 62.9013 | -60.0906 | 62.9379 | -59.816 | -60.1913 | 0.022888 | -0.16479 | 62.9105 | -59.9533 | 63.0249 | -59.9579 | -60.0677 | -59.8846 | -0.13275 | -0.064087 | -0.027466 | 0.14191 | 59.9808 | -0.23346 | 60.1135 | -0.10071 | 0.004578 | -0.054932 | 0.059509 | 0 | 0.073242 | -0.10986 | 0.068664 | -0.11444 | 0.27466 | 123.0286 | -0.004578 | 122.9782 | 122.9919 | 122.8638 | 122.8592 | 122.8683 | -123.056 | -122.9187 | 122.8958 | 122.9828 | 59.7702 | 59.7931
896.8906 | 123.1979 | -59.9533 | 62.915 | -0.045166 | 0.0013393 | 0.063641 | 0.065523 | 0.0013245 | -0.00099116 | -0.0011899 | -0.012482 | 0.0009528 | 0.064495 | 0.068197 | -0.0059132 | 0.0039562 | 0.00027333 | -0.27466 | 62.8693 | -60.0586 | 62.9333 | -59.7794 | -60.141 | -0.004578 | -0.20142 | 62.8555 | -59.9808 | 63.0432 | -59.9258 | -60.0586 | -59.8434 | -0.10529 | -0.045776 | 0.018311 | 0.17395 | 59.9487 | -0.18768 | 60.054 | -0.082397 | -0.027466 | -0.059509 | 0.12817 | 0.027466 | 0.10986 | -0.10529 | 0.13733 | -0.07782 | 0.27924 | 122.9919 | 0.054932 | 123.024 | 122.9279 | 122.8363 | 122.8226 | 122.8088 | -122.9736 | -122.8958 | 122.8867 | 122.9965 | 59.6786 | 59.7519
897.8281 | 123.1338 | -59.9396 | 62.9929 | -0.060425 | 5.7742e-05 | 0.062145 | 0.069368 | -0.0016663 | -0.00035036 | -0.0033261 | -0.036896 | 0.00138 | 0.066845 | 0.067556 | -0.0056994 | 0.0043836 | -0.0010083 | -0.23346 | 62.9196 | -60.0677 | 62.8967 | -59.8755 | -60.1959 | 0.013733 | -0.20599 | 62.9196 | -59.9579 | 62.9929 | -60.0037 | -60.0952 | -59.8892 | -0.12817 | -0.073242 | -0.09613 | 0.064087 | 59.9533 | -0.25635 | 60.0815 | -0.12817 | -0.018311 | -0.073242 | 0 | -0.064087 | 0.050354 | -0.15564 | 0.068665 | -0.13733 | 0.19226 | 122.9645 | -0.045776 | 122.9507 | 122.9874 | 122.8775 | 122.8592 | 122.8592 | -123.0606 | -122.9507 | 122.8363 | 122.9324 | 59.7061 | 59.7336
898.8906 | 123.1476 | -59.9487 | 62.9379 | -0.1062 | -0.00015586 | 0.062786 | 0.066377 | 0.0038879 | -0.0014184 | -0.0037533 | 0.0088807 | -0.0001154 | 0.06364 | 0.060079 | -0.0059132 | 0.0024608 | -0.0014355 | -0.28381 | 62.851 | -60.0586 | 62.9196 | -59.8297 | -60.1913 | -0.004578 | -0.24719 | 62.851 | -59.9808 | 63.0157 | -59.9716 | -60.0677 | -59.8709 | -0.10986 | -0.086975 | -0.01831 | 0.11902 | 59.9442 | -0.24262 | 60.054 | -0.13275 | -0.032044 | -0.086975 | 0.07782 | -0.022889 | 0.077819 | -0.11902 | 0.10986 | -0.086975 | 0.22888 | 122.9782 | 0.009155 | 122.9965 | 122.9095 | 122.8317 | 122.7997 | 122.7997 | -122.9965 | -122.9187 | 122.8683 | 122.9645 | 59.6649 | 59.7015
899.8438 | 123.0423 | -60.022 | 62.9333 | -0.052796 | 0.0021939 | 0.062359 | 0.070222 | 0.00068369 | -0.0012048 | 0.0015871 | -0.094879 | 0.0026618 | 0.065563 | 0.066488 | -0.004845 | 0.0033154 | 0.0030505 | -0.31128 | 62.9105 | -60.1227 | 62.8143 | -59.9533 | -60.3058 | -0.091553 | -0.35706 | 62.883 | -60.0128 | 62.9562 | -60.0677 | -60.4111 | -60.173 | -0.10071 | -0.022889 | -0.11902 | 0.068665 | 59.9304 | -0.28381 | 60.0311 | -0.1831 | 0.009156 | -0.050354 | 0.022888 | -0.045776 | -0.15106 | -0.3891 | -0.16022 | -0.39825 | 0.16937 | 122.937 | -0.054932 | 122.9691 | 123.0331 | 122.8958 | 122.9324 | 122.905 | -123.056 | -122.9462 | 122.8363 | 122.9782 | 59.7107 | 59.6649
900.8906 | 123.1476 | -59.9579 | 62.8784 | -0.098572 | 0.0026211 | 0.063427 | 0.065309 | -0.00059811 | 0.00093144 | 0.0037235 | -0.036896 | 0.00138 | 0.064281 | 0.064352 | -0.0052722 | 0.0022472 | 0.0024097 | -0.26093 | 62.8281 | -60.0449 | 62.9425 | -59.7931 | -60.173 | -0.018311 | -0.21057 | 62.8418 | -59.9762 | 63.0524 | -59.9304 | -59.9762 | -59.9442 | -0.086975 | -0.050354 | 0.064087 | 0.1648 | 59.9396 | -0.21515 | 60.0266 | -0.12817 | -0.01831 | -0.036621 | 0.17395 | 0.027466 | 0.013733 | -0.01831 | 0.032043 | 0 | 0.25177 | 122.9874 | 0.045776 | 123.0286 | 122.8729 | 122.818 | 122.7859 | 122.7997 | -122.9233 | -122.8546 | 122.9004 | 123.0103 | 59.697 | 59.7473
901.8281 | 123.1247 | -59.9442 | 62.97 | -0.075684 | 0.00091214 | 0.062359 | 0.066377 | 0.0026063 | -0.0012048 | -0.0022581 | 0.011932 | 9.8198e-05 | 0.06599 | 0.05538 | -0.0046314 | 0.003529 | -0.0022901 | -0.17853 | 62.9059 | -60.0494 | 62.9517 | -59.7977 | -60.1318 | 0.091553 | -0.14191 | 62.9242 | -59.9579 | 63.002 | -59.9716 | -60.0906 | -59.9167 | -0.10529 | -0.064087 | -0.018311 | 0.14648 | 60.0357 | -0.18768 | 60.141 | -0.082398 | -0.013733 | -0.045777 | 0.032043 | -0.027466 | 0.027466 | -0.14648 | 0.041199 | -0.13275 | 0.25177 | 123.0011 | -0.013733 | 122.9599 | 122.9553 | 122.8821 | 122.85 | 122.8683 | -123.0194 | -122.9279 | 122.8958 | 122.9462 | 59.7656 | 59.8022
902.8906 | 123.0469 | -59.9625 | 62.9654 | -0.068054 | 5.7742e-05 | 0.065136 | 0.068086 | 0.0015381 | -0.00013676 | -0.00054907 | -0.064362 | 0.0052252 | 0.065563 | 0.067983 | -0.0044178 | 0.0045972 | 0.00048713 | -0.31586 | 62.8784 | -60.0906 | 62.8281 | -59.935 | -60.3058 | -0.09613 | -0.34332 | 62.8876 | -60.0128 | 62.9288 | -60.0403 | -60.0906 | -59.9533 | -0.12817 | -0.086975 | -0.13733 | 0.027465 | 59.8663 | -0.34332 | 59.9945 | -0.21515 | -0.050354 | -0.07782 | -0.036621 | -0.07782 | 0.009155 | -0.12817 | 0.059509 | -0.07782 | 0.15564 | 122.9187 | -0.027466 | 122.9416 | 122.9691 | 122.9004 | 122.8409 | 122.85 | -123.056 | -122.9782 | 122.7905 | 122.8912 | 59.6466 | 59.6191
903.8281 | 123.1064 | -59.9579 | 62.9883 | -0.007019 | 0.0015529 | 0.061291 | 0.067659 | 0.0013245 | -0.0033412 | -0.0043943 | -0.064362 | 0.0020208 | 0.064281 | 0.06542 | -0.0056994 | 0.0037426 | -0.0018629 | -0.23804 | 62.9562 | -60.054 | 63.0707 | -60.0174 | -60.4523 | 0.027466 | -0.18768 | 62.9196 | -59.9899 | 62.9745 | -60.0037 | -60.0861 | -59.8984 | -0.09613 | -0.032043 | 0.082398 | -0.059509 | 59.9854 | -0.49439 | 60.0815 | -0.39826 | -0.032043 | -0.068664 | -0.013733 | -0.045776 | 0.05951 | -0.12817 | 0.091553 | -0.096131 | 0.036621 | 123.1247 | -0.013733 | 122.9645 | 123.0103 | 122.9095 | 122.9141 | 122.8775 | -123.0423 | -122.9782 | 123.0286 | 122.9324 | 59.7198 | 59.7702
904.8906 | 123.1659 | -59.9442 | 62.8967 | -0.11383 | 0.0013393 | 0.062572 | 0.068727 | 0.0047425 | -0.00099116 | 0.00051913 | -0.042999 | 0.0022346 | 0.065563 | 0.06307 | -0.0054858 | 0.0022472 | 0.0041187 | -0.30212 | 62.8784 | -60.1044 | 62.8967 | -59.8801 | -60.2371 | -0.068665 | -0.28381 | 62.8693 | -59.9762 | 63.0203 | -59.9716 | -60.0632 | -59.8526 | -0.16022 | -0.018311 | 0 | 0.064087 | 59.8755 | -0.29297 | 60.0357 | -0.13275 | -0.032043 | -0.027466 | 0.1236 | -0.027466 | 0.091553 | -0.11902 | 0.1236 | -0.086975 | 0.2243 | 123.0011 | 0.004577 | 122.9965 | 122.9828 | 122.8455 | 122.8226 | 122.8134 | -123.0011 | -122.8729 | 122.8409 | 122.9645 | 59.642 | 59.6603
905.8281 | 123.1247 | -59.9533 | 63.0569 | -0.060425 | 0.0017667 | 0.061504 | 0.067232 | 0.0011109 | -0.0016322 | -0.00097627 | -0.015534 | 0.0037298 | 0.065777 | 0.062856 | -0.0042042 | 0.0026746 | -0.0014355 | -0.23346 | 62.9288 | -60.0357 | 62.8876 | -59.8572 | -60.1959 | 0.054932 | -0.21057 | 62.9242 | -59.9899 | 62.97 | -59.9899 | -60.0952 | -59.9121 | -0.082398 | -0.12817 | -0.16937 | 0.09613 | 60.0082 | -0.24262 | 60.0906 | -0.16022 | -0.036621 | -0.13275 | -0.086975 | -0.036621 | 0.041199 | -0.14191 | 0.07782 | -0.10529 | 0.17853 | 122.9233 | 0 | 122.9599 | 122.9645 | 122.9141 | 122.8821 | 122.8775 | -123.0927 | -123.0469 | 122.8409 | 122.9233 | 59.7198 | 59.7427
906.8906 | 123.0606 | -59.9625 | 62.9608 | -0.083313 | -0.0012241 | 0.061504 | 0.067872 | 0.00025629 | -0.0029138 | 9.193e-05 | -0.070465 | 0.0028754 | 0.065563 | 0.061361 | -0.0052722 | 0.0065198 | 0.0030505 | -0.32959 | 62.8738 | -60.1227 | 62.8372 | -59.9533 | -60.2966 | -0.086975 | -0.33875 | 62.8967 | -60.0082 | 62.8647 | -60.3012 | -59.8755 | -59.7061 | -0.16022 | -0.086975 | -0.1236 | 0.009155 | 59.8755 | -0.33417 | 60.0357 | -0.17395 | -0.045777 | -0.064086 | -0.09613 | -0.33875 | 0.25635 | 0.086975 | 0.30212 | 0.13275 | 0.16937 | 122.9599 | -0.29297 | 122.8729 | 122.9965 | 122.905 | 122.8363 | 122.8592 | -123.0835 | -122.9691 | 122.7997 | 122.8271 | 59.6329 | 59.6237
907.8281 | 123.1018 | -59.967 | 62.9837 | -0.090943 | 0.00027134 | 0.061291 | 0.064454 | -0.0010253 | -0.002273 | 0.00030553 | 0.0027771 | 0.0026618 | 0.066418 | 0.060934 | -0.0052722 | 0.0024608 | -0.0018629 | -0.19226 | 62.9242 | -60.0357 | 62.9105 | -59.8343 | -60.173 | 0.050354 | -0.17395 | 62.9379 | -59.9442 | 62.97 | -59.9808 | -60.0952 | -59.9121 | -0.068665 | -0.05951 | -0.073243 | 0.13275 | 60.0174 | -0.20599 | 60.0861 | -0.13733 | 0.022888 | -0.045777 | -0.013733 | -0.013733 | 0.054932 | -0.12817 | 0.032044 | -0.15106 | 0.20142 | 122.9462 | -0.036621 | 122.9141 | 122.9599 | 122.8821 | 122.8912 | 122.905 | -123.0194 | -122.9279 | 122.8775 | 122.937 | 59.7748 | 59.7931
908.8906 | 123.1476 | -59.9442 | 62.9196 | -0.11383 | -0.00079686 | 0.062359 | 0.068513 | -0.0012391 | -0.0027002 | -0.00076267 | -0.058258 | 0.003089 | 0.068981 | 0.072897 | -0.0042042 | 0.0037426 | 5.9726e-05 | -0.32044 | 62.883 | -60.1273 | 62.8464 | -59.8984 | -60.2646 | -0.082397 | -0.31128 | 62.8647 | -59.9899 | 62.9974 | -60.0082 | -60.0998 | -59.8846 | -0.1831 | -0.036621 | -0.073242 | 0.045777 | 59.8618 | -0.32043 | 60.0449 | -0.13733 | -0.045776 | -0.054932 | 0.07782 | -0.064087 | 0.059509 | -0.15564 | 0.10528 | -0.10986 | 0.22888 | 122.9736 | -0.018311 | 122.9874 | 123.0103 | 122.8546 | 122.8271 | 122.8088 | -123.0469 | -122.9095 | 122.7905 | 122.9416 | 59.6237 | 59.6329
909.8281 | 123.0972 | -59.9899 | 62.97 | -0.11383 | 0.0011257 | 0.063427 | 0.070222 | 0.00089729 | -0.00013676 | 0.00051913 | -0.046051 | 0.0018072 | 0.065563 | 0.062856 | -0.0063404 | 0.0045972 | -0.0016493 | -0.23804 | 62.8967 | -60.0723 | 62.9013 | -59.8663 | -60.2509 | -0.045776 | -0.25635 | 62.915 | -59.9991 | 62.9654 | -60.0311 | -60.1685 | -59.9167 | -0.082398 | -0.073242 | -0.068665 | 0.1236 | 59.9442 | -0.26093 | 60.0266 | -0.17853 | -0.009155 | -0.054932 | -0.004578 | -0.041199 | 0.073242 | -0.17853 | 0.082397 | -0.16937 | 0.20599 | 122.9736 | -0.032044 | 122.9645 | 122.9691 | 122.9141 | 122.8867 | 122.905 | -123.0423 | -122.9691 | 122.8912 | 122.9553 | 59.7519 | 59.7336
910.8281 | 123.1842 | -59.9487 | 62.9333 | -0.12909 | 0.00027134 | 0.063427 | 0.067659 | -0.0016663 | -0.0035548 | -0.0046079 | 0.039398 | 0.0018072 | 0.065136 | 0.063711 | -0.0044178 | 0.0026746 | 0.00091433 | -0.26093 | 62.8647 | -60.0403 | 62.9013 | -59.8251 | -60.173 | 0.013733 | -0.21057 | 62.8601 | -59.9854 | 63.0203 | -59.9396 | -60.0128 | -59.8343 | -0.091553 | -0.068665 | -0.032044 | 0.1236 | 59.9625 | -0.22431 | 60.054 | -0.13275 | -0.036622 | -0.073243 | 0.086975 | 0.009155 | 0.11444 | -0.064087 | 0.15106 | -0.027465 | 0.21515 | 122.9416 | 0.045777 | 123.0057 | 122.905 | 122.8455 | 122.8134 | 122.8088 | -122.9736 | -122.9187 | 122.85 | 122.9691 | 59.6878 | 59.7382
911.8906 | 123.2162 | -59.9258 | 62.9196 | -0.075684 | 0.0011257 | 0.063427 | 0.065309 | -0.0012391 | -0.00056396 | 0.0026553 | -0.024689 | 0.0028754 | 0.065136 | 0.06072 | -0.0035632 | 0.0054516 | -0.0037855 | -0.2655 | 62.8372 | -60.0815 | 62.764 | -59.9075 | -59.816 | 0.054932 | -0.17853 | 62.8464 | -59.9625 | 63.0569 | -59.935 | -60.0311 | -59.8434 | -0.15564 | -0.082398 | -0.15564 | 0.01831 | 59.9808 | 0.10986 | 60.1364 | 0.2655 | -0.036621 | -0.073242 | 0.13733 | -0.009156 | 0.082397 | -0.10529 | 0.11902 | -0.068665 | 0.17395 | 122.8455 | 0.027465 | 123.0194 | 122.9187 | 122.8088 | 122.7631 | 122.7722 | -123.0011 | -122.8821 | 122.6898 | 122.9828 | 59.6603 | 59.7473
912.8281 | 123.1979 | -59.9304 | 62.9379 | -0.060425 | 0.0013393 | 0.063 | 0.066377 | -0.0035889 | -0.00077756 | -0.0018307 | 0.039398 | 0.0018072 | 0.063854 | 0.062643 | -0.0059132 | 0.0013928 | 0.00048713 | -0.19226 | 62.9013 | -60.0266 | 63.002 | -59.7153 | -60.0861 | 0.12817 | -0.07782 | 62.9013 | -59.9075 | 63.0157 | -59.8984 | -59.9075 | -59.7885 | -0.09613 | -0.036621 | 0.064087 | 0.21515 | 60.0586 | -0.15564 | 60.1547 | -0.05951 | 0.022888 | -0.036621 | 0.07782 | 0.032044 | 0.14191 | 0.022888 | 0.11902 | 0 | 0.31128 | 123.0286 | 0.009156 | 122.9233 | 122.9279 | 122.8088 | 122.8317 | 122.8317 | -122.9645 | -122.8455 | 122.9324 | 122.9462 | 59.7382 | 59.8526
913.8906 | 123.2254 | -59.935 | 62.9059 | -0.11383 | 0.0011257 | 0.063213 | 0.069581 | 0.0019653 | -0.0029138 | -0.0022581 | -0.064362 | 0.0015936 | 0.067272 | 0.063497 | -0.008263 | 0.0037426 | -0.00079467 | -0.27008 | 62.8464 | -60.0861 | 62.9562 | -59.8022 | -60.173 | -0.018311 | -0.2243 | 62.8372 | -59.9808 | 63.0707 | -59.9487 | -60.0266 | -59.8343 | -0.15106 | -0.059509 | 0.050354 | 0.13275 | 59.9167 | -0.23804 | 60.0677 | -0.086975 | -0.045776 | -0.068665 | 0.16479 | -0.013732 | 0.10071 | -0.091552 | 0.14648 | -0.045776 | 0.28381 | 123.0423 | 0.032044 | 123.0515 | 122.9324 | 122.818 | 122.7814 | 122.7722 | -122.9919 | -122.8867 | 122.8912 | 123.0057 | 59.6649 | 59.7107
914.8281 | 123.1613 | -59.9121 | 62.9791 | -0.037537 | 0.0021939 | 0.061718 | 0.068086 | 0.0028199 | -0.0041956 | -0.00012167 | -0.0063781 | 0.0005256 | 0.064922 | 0.063925 | -0.0052722 | 0.0043836 | -0.0014355 | -0.16937 | 62.8922 | -60.0449 | 62.9837 | -59.7565 | -60.1089 | 0.091553 | -0.10071 | 62.9059 | -59.9533 | 63.0157 | -59.9304 | -60.0266 | -59.8434 | -0.13275 | -0.086975 | 0.004578 | 0.15564 | 60.0037 | -0.19684 | 60.1364 | -0.064087 | -0.041199 | -0.073242 | 0.036621 | -0.018311 | 0.068664 | -0.11444 | 0.10986 | -0.073242 | 0.28839 | 123.0286 | 0.022888 | 122.9691 | 122.937 | 122.8592 | 122.8043 | 122.818 | -123.024 | -122.9324 | 122.8958 | 122.9279 | 59.7427 | 59.8114
915.8906 | 123.1293 | -59.967 | 62.9791 | -0.083313 | 0.00048494 | 0.063854 | 0.069795 | 0.0053833 | 0.00029044 | 0.00073273 | -0.094879 | 0.0033026 | 0.066418 | 0.067983 | -0.0071948 | 0.0031018 | -0.0018629 | -0.26093 | 62.8922 | -60.0815 | 62.9013 | -59.8618 | -60.2371 | -0.027466 | -0.25177 | 62.9059 | -59.9854 | 62.9608 | -60.0174 | -60.141 | -59.9075 | -0.11444 | -0.086975 | -0.07782 | 0.10529 | 59.9396 | -0.27008 | 60.054 | -0.15564 | -0.018311 | -0.073242 | -0.018311 | -0.050354 | 0.059509 | -0.17395 | 0.07782 | -0.15564 | 0.21973 | 122.9828 | -0.032043 | 122.9462 | 122.9736 | 122.8912 | 122.8592 | 122.8729 | -123.0606 | -122.9645 | 122.8683 | 122.9279 | 59.7061 | 59.7153
916.8281 | 123.2025 | -59.9167 | 62.9379 | -0.083313 | 5.7742e-05 | 0.06065 | 0.067018 | 0.0043151 | -0.0024866 | -0.0024717 | 0.033295 | 0.0009528 | 0.065349 | 0.061148 | -0.0054858 | 0.0054516 | -0.0020765 | -0.25635 | 62.8647 | -60.0723 | 62.9471 | -59.7931 | -60.1318 | 0.054932 | -0.17395 | 62.8464 | -59.967 | 63.0432 | -59.903 | -60.0128 | -59.8297 | -0.15564 | -0.073242 | 0.009156 | 0.1236 | 59.9716 | -0.21515 | 60.1273 | -0.059509 | -0.050354 | -0.091552 | 0.10529 | 0.013733 | 0.086975 | -0.09613 | 0.13733 | -0.045776 | 0.27924 | 123.0194 | 0.064087 | 123.0103 | 122.937 | 122.8134 | 122.7814 | 122.7631 | -123.0103 | -122.905 | 122.8638 | 122.9599 | 59.6603 | 59.7427
917.8906 | 123.0743 | -59.9808 | 62.9425 | -0.11383 | 0.0028347 | 0.061932 | 0.0683 | 0.0026063 | 0.00071784 | 0.0011599 | -0.094879 | 0.0024482 | 0.064495 | 0.064993 | -0.004845 | 0.0041698 | 0.0015551 | -0.30212 | 62.9013 | -60.0998 | 62.8326 | -59.9625 | -60.2875 | -0.091553 | -0.36621 | 62.8876 | -60.0128 | 62.9333 | -60.0677 | -60.1776 | -59.9442 | -0.11902 | -0.041199 | -0.10986 | 0.018311 | 59.8892 | -0.3067 | 60.0082 | -0.18768 | -0.032043 | -0.054932 | -0.009155 | -0.086975 | 0.036621 | -0.19684 | 0.068664 | -0.1648 | 0.13733 | 122.9324 | -0.054932 | 122.9462 | 123.0011 | 122.9004 | 122.8821 | 122.8683 | -123.0423 | -122.9553 | 122.8134 | 122.9141 | 59.6786 | 59.6146
918.8281 | 123.1796 | -59.8984 | 62.9745 | -0.083313 | 0.00048494 | 0.062359 | 0.066163 | -0.00081171 | -0.0012048 | -0.0035397 | 0.027191 | 0.0018072 | 0.065777 | 0.061788 | -0.0050586 | 0.0024608 | 0.0017687 | -0.16937 | 62.9059 | -60.0037 | 63.2538 | -59.5596 | -60.5438 | 0.064087 | -0.11902 | 62.8693 | -59.9579 | 63.0615 | -59.8709 | -59.967 | -59.7931 | -0.10529 | -0.068664 | 0.27924 | 0.33874 | 59.9625 | -0.64545 | 60.0677 | -0.54016 | -0.05951 | -0.10529 | 0.086975 | 0.027465 | 0.10529 | -0.068665 | 0.1648 | -0.009155 | 0.44403 | 123.2574 | 0.086975 | 123.0194 | 122.9095 | 122.8271 | 122.8043 | 122.7676 | -122.9782 | -122.9324 | 123.1522 | 122.9599 | 59.729 | 59.7794
919.8906 | 123.1567 | -59.9442 | 62.9471 | -0.11383 | 5.7742e-05 | 0.061291 | 0.067659 | -0.0042297 | 7.6842e-05 | -0.0048215 | 0.018036 | -0.000329 | 0.066204 | 0.059866 | -0.0067676 | 0.0039562 | -0.0020765 | -0.27008 | 62.8418 | -60.0998 | 62.9196 | -59.8251 | -60.1913 | -0.018311 | -0.25177 | 62.8555 | -59.967 | 63.0112 | -59.9487 | -60.054 | -59.8801 | -0.15564 | -0.10529 | -0.027466 | 0.11902 | 59.9258 | -0.24719 | 60.0815 | -0.091553 | -0.022888 | -0.091553 | 0.064086 | -0.004577 | 0.064087 | -0.10986 | 0.086975 | -0.086975 | 0.27466 | 123.0194 | 0.018311 | 122.9782 | 122.9416 | 122.8226 | 122.7859 | 122.7997 | -123.0469 | -122.9141 | 122.8638 | 122.9553 | 59.6741 | 59.6924
920.8438 | 123.1155 | -59.9533 | 63.002 | -0.052796 | 0.00027134 | 0.060223 | 0.068086 | -0.0020935 | -0.0037684 | -0.0014035 | -0.030792 | 0.0020208 | 0.064495 | 0.06072 | -0.004845 | 0.0050244 | 0.00048713 | -0.07782 | 62.9608 | -60.0357 | 62.8876 | -59.8984 | -60.2188 | 0.041199 | -0.2243 | 62.9379 | -59.9625 | 62.9654 | -59.9899 | -60.0952 | -59.8846 | -0.082398 | -0.041199 | -0.11444 | 0.054932 | 59.9945 | -0.2655 | 60.0769 | -0.18311 | -0.009155 | -0.064087 | -0.036621 | -0.036621 | 0.068664 | -0.14191 | 0.077819 | -0.13275 | 0.13733 | 122.9233 | -0.027466 | 122.9279 | 122.9965 | 122.9004 | 122.9141 | 122.8912 | -123.0377 | -122.9645 | 122.8409 | 122.9187 | 59.8755 | 59.729
921.8906 | 123.0835 | -60.0037 | 62.9562 | -0.16724 | 5.7742e-05 | 0.064281 | 0.067232 | 0.0017517 | -0.0024866 | 0.0018009 | -0.073517 | 0.0007392 | 0.064495 | 0.063497 | -0.0035632 | 0.0058788 | -0.0033581 | -0.28839 | 62.8876 | -60.1181 | 62.8143 | -59.9579 | -60.2966 | -0.10071 | -0.37994 | 62.8967 | -60.0266 | 62.9288 | -60.0632 | -60.1913 | -59.9442 | -0.11444 | -0.068665 | -0.14191 | 0.045776 | 59.903 | -0.29297 | 60.0174 | -0.17853 | -0.022888 | -0.059509 | -0.027466 | -0.059509 | 0.059509 | -0.18768 | 0.082397 | -0.16479 | 0.16022 | 122.9324 | -0.036621 | 122.9553 | 123.0057 | 122.9233 | 122.8912 | 122.9004 | -123.0743 | -122.9828 | 122.818 | 122.9324 | 59.7153 | 59.6237
922.8281 | 123.3032 | -59.9442 | 62.9059 | -0.098572 | 0.0011257 | 0.063854 | 0.068086 | -0.00017091 | -0.002273 | -0.0011899 | -0.021637 | 0.0020208 | 0.06364 | 0.061361 | -0.0059132 | 0.0039562 | -0.00058107 | -0.25177 | 62.8235 | -60.0632 | 62.9471 | -59.8022 | -60.1639 | -0.018311 | -0.2243 | 62.8418 | -59.9854 | 63.0569 | -59.8801 | -60.3516 | -59.9625 | -0.11902 | -0.082398 | 0.041199 | 0.14191 | 59.9258 | -0.21973 | 60.0449 | -0.10071 | -0.041199 | -0.064087 | 0.15106 | 0.064087 | -0.01831 | -0.40741 | 0.022889 | -0.36621 | 0.26093 | 123.0103 | 0.10529 | 123.0423 | 122.8867 | 122.8271 | 122.7676 | 122.7859 | -122.9691 | -122.8912 | 122.8912 | 123.0011 | 59.6924 | 59.7198
923.8906 | 123.111 | -59.9625 | 62.9791 | -0.068054 | 0.00048494 | 0.062572 | 0.068941 | 0.00046989 | -0.00056396 | 0.00051913 | -0.058258 | 0.0022346 | 0.064709 | 0.070333 | -0.0042042 | 0.0037426 | -0.0012219 | -0.25177 | 62.9059 | -60.0906 | 62.8922 | -59.8709 | -60.2188 | -0.050354 | -0.26093 | 62.9059 | -59.9762 | 62.9608 | -60.0128 | -60.1593 | -59.935 | -0.12817 | -0.073242 | -0.086975 | 0.091552 | 59.9121 | -0.25635 | 60.0403 | -0.12817 | -0.013733 | -0.073242 | -0.018311 | -0.050354 | 0.027465 | -0.19684 | 0.041198 | -0.18311 | 0.21973 | 122.9828 | -0.036621 | 122.937 | 122.9965 | 122.8821 | 122.8683 | 122.8683 | -123.0698 | -122.9553 | 122.8546 | 122.9233 | 59.7107 | 59.7015
924.8281 | 123.1796 | -59.9396 | 62.915 | -0.075684 | -0.00079686 | 0.063641 | 0.069154 | -0.0010253 | -0.0046228 | -0.0018307 | -0.0094299 | 0.0024482 | 0.066418 | 0.058798 | -0.0042042 | 0.0020336 | -0.0018629 | -0.29297 | 62.8372 | -60.0449 | 62.9562 | -59.7748 | -60.1547 | -0.004578 | -0.21057 | 62.8418 | -59.9945 | 63.0524 | -59.9304 | -60.022 | -59.8297 | -0.10529 | -0.07782 | 0.041199 | 0.16479 | 59.935 | -0.21515 | 60.0403 | -0.10986 | -0.054932 | -0.073242 | 0.13733 | 0.009155 | 0.10986 | -0.082398 | 0.16479 | -0.027466 | 0.27008 | 123.0011 | 0.064087 | 123.0469 | 122.8821 | 122.8363 | 122.7768 | 122.7814 | -122.9599 | -122.9095 | 122.8958 | 122.9919 | 59.6466 | 59.729
925.9062 | 123.1796 | -59.9487 | 62.9196 | -0.1062 | 0.0026211 | 0.063 | 0.067018 | 0.0060241 | -0.00056396 | -0.0033261 | -0.015534 | 0.0022346 | 0.064922 | 0.06072 | -0.0071948 | 0.0037426 | 0.0015551 | -0.27466 | 62.8647 | -60.054 | 62.9379 | -59.8068 | -60.2051 | -0.022888 | -0.23346 | 62.8281 | -59.9808 | 63.0249 | -59.9762 | -60.0586 | -59.848 | -0.10529 | -0.054932 | 0.01831 | 0.14191 | 59.9258 | -0.25635 | 60.0311 | -0.15106 | -0.032044 | -0.091553 | 0.10528 | -0.027466 | 0.10071 | -0.10986 | 0.13275 | -0.07782 | 0.24719 | 122.9919 | 0.004578 | 123.0057 | 122.9187 | 122.8088 | 122.8134 | 122.7768 | -122.9736 | -122.9004 | 122.8867 | 122.9736 | 59.6741 | 59.7153
926.8281 | 123.1888 | -59.9396 | 62.9105 | -0.068054 | 0.0024075 | 0.063427 | 0.067445 | -0.0010253 | -0.0016322 | -0.00033547 | -0.030792 | 0.0015936 | 0.064709 | 0.058798 | -0.0052722 | 0.0056652 | 0.0017687 | -0.21057 | 62.8464 | -60.0677 | 62.9608 | -59.8068 | -60.1639 | 0 | -0.20599 | 62.8281 | -59.9533 | 63.0615 | -59.9213 | -60.0403 | -59.8343 | -0.12817 | -0.064086 | 0.050354 | 0.13275 | 59.9396 | -0.2243 | 60.0677 | -0.09613 | -0.013733 | -0.082397 | 0.15106 | 0.01831 | 0.10528 | -0.10071 | 0.11902 | -0.086975 | 0.26093 | 123.0286 | 0.032043 | 123.0148 | 122.9141 | 122.7814 | 122.7859 | 122.7676 | -122.9782 | -122.8638 | 122.9004 | 123.0011 | 59.729 | 59.7336
927.8281 | 123.2346 | -59.9487 | 62.9379 | -0.13672 | 0.00069854 | 0.063213 | 0.066377 | -0.0025207 | -0.00035036 | 9.193e-05 | -0.036896 | 0.0018072 | 0.066204 | 0.065634 | -0.0052722 | 0.0026746 | -0.00036747 | -0.2655 | 62.8372 | -60.0952 | 62.9608 | -59.7839 | -60.1639 | -0.027466 | -0.12817 | 62.8372 | -60.0174 | 63.0569 | -59.8801 | -60.0861 | -59.8434 | -0.14649 | -0.10071 | 0.022888 | 0.16479 | 59.9213 | -0.21515 | 60.0677 | -0.068664 | -0.068665 | -0.10071 | 0.11902 | 0.068664 | 0.10528 | -0.13733 | 0.17395 | -0.068665 | 0.31128 | 123.056 | 0.13733 | 123.0743 | 122.9324 | 122.8546 | 122.7859 | 122.7859 | -123.0331 | -122.9553 | 122.9095 | 123.0057 | 59.6832 | 59.8206
928.8281 | 123.1613 | -59.9487 | 62.915 | -0.13672 | -0.00015586 | 0.064709 | 0.068727 | -0.00059811 | -0.0012048 | 9.193e-05 | -0.06131 | 0.0043708 | 0.066418 | 0.064138 | -0.004845 | 0.0041698 | 0.0017687 | -0.31586 | 62.8693 | -60.1181 | 62.8647 | -59.8938 | -60.26 | -0.073242 | -0.32044 | 62.883 | -59.9991 | 62.9883 | -59.9854 | -60.1044 | -59.8801 | -0.16937 | -0.045776 | -0.050354 | 0.054931 | 59.8755 | -0.31128 | 60.0449 | -0.14191 | -0.050354 | -0.032043 | 0.073242 | -0.036622 | 0.068664 | -0.15564 | 0.11902 | -0.10529 | 0.2243 | 122.9828 | 0.013732 | 122.9874 | 122.9874 | 122.8821 | 122.818 | 122.8317 | -123.0331 | -122.9141 | 122.8134 | 122.937 | 59.6329 | 59.6283
929.8906 | 123.1384 | -59.9396 | 62.9929 | -0.052796 | 0.0013393 | 0.063427 | 0.067232 | 0.0034607 | -0.0016322 | 0.00030553 | -0.058258 | 0.0018072 | 0.065349 | 0.066061 | -0.0059132 | 0.0037426 | -0.0012219 | -0.21057 | 62.9196 | -60.022 | 62.9196 | -59.8572 | -60.1868 | 0.032043 | -0.1831 | 62.9059 | -59.9945 | 63.0203 | -59.935 | -60.0906 | -59.8892 | -0.082398 | -0.073242 | -0.073242 | 0.082397 | 59.9716 | -0.24719 | 60.054 | -0.16479 | -0.054932 | -0.086975 | 0.027466 | 0.004577 | 0.050354 | -0.15106 | 0.10529 | -0.09613 | 0.1648 | 122.9416 | 0.059509 | 123.0148 | 122.9416 | 122.9004 | 122.8592 | 122.8455 | -123.0148 | -122.9874 | 122.8592 | 122.9599 | 59.729 | 59.7565
930.8281 | 123.2391 | -59.9167 | 62.9379 | -0.075684 | -0.0010105 | 0.062786 | 0.065523 | 0.0023925 | -0.0024866 | 0.00030553 | 0.024139 | 0.0020208 | 0.065349 | 0.061148 | -0.0052722 | 0.0045972 | -0.00036747 | -0.21515 | 62.8784 | -60.0266 | 63.0066 | -59.729 | -60.0723 | 0.12817 | -0.045776 | 62.8784 | -59.935 | 63.1073 | -59.8389 | -59.9625 | -59.7885 | -0.10986 | -0.059509 | 0.068665 | 0.18768 | 60.0449 | -0.15564 | 60.1547 | -0.045777 | -0.018311 | -0.059509 | 0.16937 | 0.07782 | 0.12817 | -0.045776 | 0.14648 | -0.027465 | 0.29755 | 123.0331 | 0.096131 | 123.0423 | 122.905 | 122.8134 | 122.7951 | 122.7951 | -122.9645 | -122.8729 | 122.9233 | 123.024 | 59.7015 | 59.8709
931.8906 | 123.0972 | -59.9396 | 62.9791 | -0.007019 | -0.00036966 | 0.059795 | 0.067659 | -0.00038451 | 7.6842e-05 | -0.0011899 | -0.033844 | 0.0009528 | 0.065563 | 0.064565 | -0.0039906 | 0.003529 | 0.00070073 | -0.23804 | 62.915 | -60.0586 | 62.8098 | -59.816 | -60.2737 | -0.022888 | -0.23346 | 62.9288 | -59.9762 | 62.97 | -59.9991 | -60.1089 | -59.9121 | -0.11902 | -0.064087 | -0.16937 | 0.1236 | 59.9167 | -0.33417 | 60.0357 | -0.21515 | -0.036621 | -0.050354 | -0.009155 | -0.059509 | 0.027466 | -0.16937 | 0.064087 | -0.13275 | 0.24262 | 122.8683 | -0.022888 | 122.9462 | 122.9736 | 122.905 | 122.8546 | 122.8683 | -123.0377 | -122.9553 | 122.7493 | 122.9095 | 59.7015 | 59.7061
932.8281 | 123.1384 | -59.9487 | 62.97 | -0.11383 | -0.00015586 | 0.063854 | 0.068727 | 0.0017517 | -0.0041956 | -0.0018307 | -0.10098 | 0.003089 | 0.064495 | 0.068411 | -0.0035632 | 0.0041698 | -0.0029309 | -0.32959 | 62.883 | -60.141 | 62.8372 | -59.9487 | -60.3058 | -0.10071 | -0.35706 | 62.8876 | -60.022 | 63.1119 | -60.0311 | -60.1776 | -59.9167 | -0.19226 | -0.086975 | -0.13275 | 0 | 59.848 | -0.35706 | 60.0403 | -0.16479 | -0.073243 | -0.082398 | 0.14191 | -0.082398 | 0.032043 | -0.22888 | 0.10529 | -0.15564 | 0.19226 | 122.9782 | -0.009155 | 123.1338 | 123.024 | 122.9095 | 122.8317 | 122.8363 | -123.111 | -122.9919 | 122.7859 | 123.0606 | 59.6191 | 59.5917
933.8906 | 123.1567 | -59.9533 | 62.97 | -0.037537 | 0.0015529 | 0.061291 | 0.066804 | 0.00089729 | -0.0037684 | -0.00076267 | -0.070465 | 0.0018072 | 0.065563 | 0.059011 | -0.0035632 | 0.0058788 | -0.0025037 | -0.19684 | 62.9105 | -60.0677 | 62.915 | -59.816 | -60.1959 | 0.036621 | -0.15106 | 62.9105 | -59.9808 | 63.0157 | -59.9396 | -60.0769 | -59.8755 | -0.11444 | -0.05951 | -0.054932 | 0.13733 | 59.9899 | -0.24262 | 60.1044 | -0.12817 | -0.027466 | -0.05951 | 0.045776 | 0.013733 | 0.07782 | -0.1236 | 0.10529 | -0.09613 | 0.25177 | 122.9828 | 0.041199 | 122.9965 | 122.9782 | 122.8912 | 122.8638 | 122.8638 | -123.0377 | -122.9507 | 122.8683 | 122.9691 | 59.7565 | 59.8022
934.8281 | 123.0698 | -59.9991 | 62.9791 | -0.068054 | 0.0017667 | 0.063854 | 0.068086 | -0.00059811 | -0.0014184 | -0.00097627 | -0.073517 | 0.0022346 | 0.06599 | 0.058798 | -0.0039906 | 0.0048108 | -0.0025037 | -0.28381 | 62.9013 | -60.0815 | 62.8601 | -59.8938 | -60.2509 | -0.068665 | -0.29755 | 62.9196 | -59.9945 | 62.9288 | -60.054 | -60.1868 | -59.9396 | -0.082398 | -0.07782 | -0.11902 | 0.10529 | 59.9304 | -0.25177 | 60.0128 | -0.16937 | 0.004577 | -0.059509 | -0.050354 | -0.054932 | 0.059509 | -0.18768 | 0.054932 | -0.19226 | 0.18768 | 122.9416 | -0.059509 | 122.9233 | 122.9828 | 122.9141 | 122.9004 | 122.9187 | -123.0606 | -122.9736 | 122.8592 | 122.9279 | 59.7153 | 59.7015
935.9062 | 123.1842 | -59.9258 | 62.9013 | -0.075684 | 5.7742e-05 | 0.063427 | 0.064241 | -0.0010253 | 0.00071784 | 0.00030553 | 0.014984 | -0.000329 | 0.066631 | 0.059225 | -0.0033496 | 0.0033154 | 0.0032641 | -0.27466 | 62.8555 | -60.0769 | 62.9471 | -59.7794 | -60.1593 | -0.009155 | -0.21057 | 62.8281 | -59.9762 | 63.0432 | -59.9442 | -60.054 | -59.8434 | -0.15106 | -0.045776 | 0.045777 | 0.14648 | 59.9167 | -0.23346 | 60.0677 | -0.082398 | -0.050354 | -0.073242 | 0.14191 | -0.018311 | 0.082397 | -0.12817 | 0.13275 | -0.07782 | 0.29755 | 123.024 | 0.032043 | 123.0194 | 122.9324 | 122.8043 | 122.7814 | 122.7539 | -122.9782 | -122.8775 | 122.8729 | 122.9691 | 59.6512 | 59.7153
936.8281 | 123.1613 | -59.9442 | 62.9471 | -0.068054 | 0.0028347 | 0.063427 | 0.068941 | 0.0015381 | -0.00077756 | -0.00054907 | -0.058258 | 0.00138 | 0.06364 | 0.06072 | -0.0059132 | 0.0041698 | -0.0029309 | -0.21057 | 62.9059 | -60.0815 | 62.915 | -59.8434 | -60.1822 | 0.036621 | -0.16022 | 62.8967 | -59.9579 | 63.0157 | -59.9762 | -60.0815 | -59.8663 | -0.13733 | -0.041199 | -0.032044 | 0.10071 | 59.9808 | -0.23804 | 60.1181 | -0.10071 | -0.013733 | -0.050354 | 0.068664 | -0.032043 | 0.07782 | -0.13733 | 0.091553 | -0.1236 | 0.23804 | 122.9965 | -0.01831 | 122.9736 | 122.9874 | 122.8546 | 122.85 | 122.8409 | -123.0286 | -122.905 | 122.8592 | 122.9599 | 59.7336 | 59.7839
937.8906 | 123.0835 | -59.9442 | 62.9929 | -0.045166 | 5.7742e-05 | 0.062145 | 0.06595 | -0.0020935 | -0.003982 | -0.0022581 | 0.097381 | 0.0022346 | 0.068127 | 0.062429 | -0.0037768 | 0.0045972 | 0.00070073 | -0.24719 | 62.9196 | -60.0403 | 62.883 | -59.8709 | -60.2097 | 0.027466 | -0.36163 | 62.9562 | -59.9808 | 62.9745 | -60.0311 | -60.0861 | -59.8984 | -0.09613 | -0.073242 | -0.10986 | 0.073242 | 59.9716 | -0.2655 | 60.0677 | -0.16937 | -0.036621 | -0.036621 | -0.018311 | -0.086975 | 0.045777 | -0.14191 | 0.082398 | -0.10529 | 0.16937 | 122.9233 | -0.050354 | 122.9553 | 122.9599 | 122.937 | 122.8638 | 122.9004 | -123.0331 | -122.9736 | 122.8271 | 122.9187 | 59.697 | 59.5825
938.8281 | 123.1293 | -59.967 | 62.9745 | -0.098572 | 0.00027134 | 0.063213 | 0.068941 | 0.0019653 | -0.00056396 | -0.00097627 | -0.067413 | 0.0007392 | 0.066845 | 0.060934 | -0.0039906 | 0.005238 | -0.0046399 | -0.21057 | 62.9105 | -60.0632 | 62.9333 | -59.816 | -60.1776 | 0.032043 | -0.14648 | 62.9059 | -59.9625 | 63.0157 | -59.967 | -60.0769 | -59.8709 | -0.09613 | -0.064087 | -0.041198 | 0.15106 | 59.9991 | -0.21057 | 60.0952 | -0.11444 | 0.004578 | -0.068664 | 0.041199 | 0 | 0.09613 | -0.10986 | 0.091552 | -0.11444 | 0.24719 | 122.9965 | -0.004578 | 122.9782 | 122.9736 | 122.8683 | 122.8775 | 122.8729 | -123.0377 | -122.937 | 122.9004 | 122.9828 | 59.7565 | 59.8206
939.8281 | 123.0881 | -59.9716 | 62.9608 | -0.060425 | 0.0028347 | 0.064709 | 0.069368 | 0.0038879 | -0.0020594 | -0.0022581 | -0.07962 | 0.00138 | 0.064922 | 0.072042 | -0.0039906 | 0.0048108 | 0.0039049 | -0.28839 | 62.8922 | -60.0998 | 62.8464 | -59.9579 | -60.2783 | -0.09613 | -0.33417 | 62.9013 | -60.0082 | 62.9013 | -60.0723 | -60.1913 | -59.9533 | -0.12817 | -0.068664 | -0.11444 | 0.013733 | 59.8755 | -0.3067 | 60.0037 | -0.17853 | -0.036621 | -0.059509 | -0.059509 | -0.10071 | 0.018311 | -0.21973 | 0.054932 | -0.1831 | 0.14191 | 122.9462 | -0.064087 | 122.9095 | 122.9919 | 122.9095 | 122.8638 | 122.8729 | -123.0606 | -122.9691 | 122.818 | 122.8729 | 59.6832 | 59.6375
940.8438 | 123.1934 | -59.967 | 62.9013 | -0.068054 | 0.0019803 | 0.063641 | 0.070009 | -0.0040161 | -0.0016322 | -0.0041807 | -0.042999 | 0.0028754 | 0.066845 | 0.060507 | -0.0052722 | 0.0050244 | -0.0012219 | -0.3067 | 62.9059 | -60.0815 | 62.9059 | -59.8389 | -60.228 | -0.059509 | -0.25177 | 62.8555 | -59.9991 | 63.0249 | -59.9167 | -60.0494 | -59.8251 | -0.11444 | 0.004578 | 0.004578 | 0.12817 | 59.9075 | -0.26093 | 60.022 | -0.14648 | -0.032043 | -0.045776 | 0.1236 | 0.050354 | 0.14191 | -0.082397 | 0.17395 | -0.050354 | 0.24262 | 122.9874 | 0.082397 | 123.024 | 122.9874 | 122.8546 | 122.8729 | 122.8226 | -122.9828 | -122.9004 | 122.8729 | 122.9919 | 59.6603 | 59.7153
941.8281 | 123.1201 | -59.9258 | 62.9837 | -0.007019 | 0.0011257 | 0.061932 | 0.068941 | 0.00068369 | -0.002273 | -0.00097627 | -0.027741 | 0.0033026 | 0.067699 | 0.059439 | -0.0046314 | 0.0026746 | -0.00036747 | -0.27008 | 62.9333 | -60.0632 | 62.8784 | -59.8709 | -60.2005 | 0.022888 | -0.21515 | 62.9288 | -59.967 | 62.97 | -59.9808 | -60.0906 | -59.903 | -0.13733 | -0.050354 | -0.10529 | 0.054931 | 59.9487 | -0.27466 | 60.0861 | -0.13733 | -0.041199 | -0.054932 | -0.013733 | -0.054932 | 0.022888 | -0.16479 | 0.064087 | -0.1236 | 0.19226 | 122.9416 | -0.013733 | 122.937 | 122.9965 | 122.8958 | 122.8592 | 122.8546 | -123.0469 | -122.9507 | 122.8043 | 122.8958 | 59.6558 | 59.7107
942.8281 | 123.1155 | -59.9487 | 62.9608 | -0.098572 | 0.0015529 | 0.063 | 0.066804 | -0.0010253 | -0.0020594 | -0.0018307 | -0.0002747 | 0.0041572 | 0.066204 | 0.05538 | -0.0044178 | 0.0031018 | 5.9726e-05 | -0.21057 | 62.9196 | -60.0494 | 62.8922 | -59.8251 | -60.1547 | 0.045776 | -0.1831 | 62.9288 | -59.9579 | 62.97 | -59.9899 | -60.0998 | -59.903 | -0.10071 | -0.041198 | -0.068664 | 0.1236 | 59.9945 | -0.20599 | 60.0952 | -0.10529 | -0.009156 | -0.032043 | 0.009156 | -0.041199 | 0.045776 | -0.15106 | 0.054932 | -0.14191 | 0.2243 | 122.9416 | -0.032043 | 122.9279 | 122.9691 | 122.8867 | 122.8683 | 122.8775 | -123.0103 | -122.9187 | 122.8409 | 122.9187 | 59.7382 | 59.7656
943.8906 | 123.1979 | -59.9579 | 62.9105 | -0.075684 | 0.0024075 | 0.063427 | 0.068727 | -0.00059811 | -0.0044092 | -0.00076267 | -0.030792 | 0.0011664 | 0.065563 | 0.063711 | -0.006554 | 0.0043836 | 0.00070073 | -0.27008 | 62.8555 | -60.0906 | 62.9379 | -59.8022 | -60.1776 | -0.009155 | -0.21973 | 62.8418 | -59.9808 | 63.0569 | -59.9258 | -60.0403 | -59.8206 | -0.13275 | -0.054931 | 0.027466 | 0.15564 | 59.9487 | -0.21973 | 60.0815 | -0.086975 | -0.022888 | -0.068664 | 0.14649 | 0.032044 | 0.13733 | -0.082397 | 0.16022 | -0.059509 | 0.28839 | 123.0286 | 0.054932 | 123.0377 | 122.9462 | 122.8226 | 122.8134 | 122.7997 | -123.0011 | -122.8912 | 122.8958 | 123.0148 | 59.6878 | 59.7382
944.8281 | 123.1384 | -59.9533 | 62.9654 | -0.068054 | -0.00079686 | 0.064281 | 0.070009 | 4.2692e-05 | -0.0024866 | -0.00076267 | -0.018585 | 0.0005256 | 0.06599 | 0.064352 | -0.008263 | 0.003529 | -0.0027173 | -0.23346 | 62.9379 | -60.0723 | 62.8876 | -59.8846 | -60.1868 | 0.032043 | -0.21057 | 62.9425 | -59.9808 | 63.0112 | -59.9625 | -60.0861 | -59.8709 | -0.11902 | -0.027466 | -0.07782 | 0.068664 | 59.9854 | -0.23346 | 60.1044 | -0.11444 | -0.027466 | -0.022888 | 0.045776 | -0.009155 | 0.082397 | -0.13275 | 0.10986 | -0.10529 | 0.18768 | 122.9599 | 0.018311 | 122.9919 | 123.0103 | 122.9233 | 122.8912 | 122.8958 | -123.0377 | -122.9462 | 122.8409 | 122.9645 | 59.7198 | 59.7427
945.8906 | 123.0972 | -59.9716 | 62.9517 | -0.11383 | 0.0028347 | 0.064281 | 0.069795 | -0.0016663 | -0.002273 | -0.00076267 | -0.20779 | 0.0043708 | 0.064709 | 0.063925 | -0.0061268 | 0.0043836 | -0.0031445 | -0.3067 | 62.9013 | -60.0998 | 62.8372 | -59.935 | -60.2966 | -0.10529 | -0.37537 | 62.8647 | -60.022 | 62.9242 | -60.0128 | -60.173 | -59.9396 | -0.12817 | -0.050354 | -0.11444 | 0.036621 | 59.8663 | -0.32501 | 59.9945 | -0.19684 | -0.050354 | -0.086975 | -0.027466 | -0.041198 | 0.032044 | -0.20142 | 0.082398 | -0.15106 | 0.16479 | 122.937 | 0.009156 | 122.9462 | 123.0011 | 122.8867 | 122.8729 | 122.8363 | -123.0515 | -122.9736 | 122.8088 | 122.8958 | 59.6649 | 59.5963
946.8281 | 123.1293 | -59.9258 | 62.9471 | -0.090943 | 0.0026211 | 0.063641 | 0.067232 | 0.0038879 | -0.0014184 | -0.0026853 | -0.046051 | 0.0026618 | 0.065136 | 0.06777 | -0.0042042 | 0.0054516 | 5.9726e-05 | -0.21057 | 62.9425 | -60.0723 | 62.915 | -59.8251 | -60.1822 | 0.050354 | -0.16937 | 62.9333 | -59.9625 | 62.9883 | -59.9579 | -60.0769 | -59.8618 | -0.14648 | -0.004578 | -0.032044 | 0.10071 | 59.9762 | -0.25635 | 60.1227 | -0.10986 | -0.036621 | -0.013733 | 0.041198 | -0.032044 | 0.064087 | -0.15106 | 0.10071 | -0.11444 | 0.24719 | 122.9874 | 0.004577 | 122.9507 | 123.0148 | 122.8958 | 122.8683 | 122.8592 | -123.0194 | -122.9095 | 122.8409 | 122.9141 | 59.7153 | 59.7565
947.8906 | 123.1979 | -59.9258 | 62.9333 | -0.098572 | 0.0028347 | 0.063427 | 0.067018 | -0.0012391 | 0.00071784 | -0.0011899 | 0.045502 | -0.0001154 | 0.067486 | 0.06072 | -0.0056994 | 0.0033154 | 0.0017687 | -0.27924 | 62.883 | -60.0494 | 62.9242 | -59.816 | -60.173 | 0.027466 | -0.20142 | 62.851 | -59.967 | 63.0249 | -59.9258 | -60.0128 | -59.8343 | -0.1236 | -0.050354 | -0.009156 | 0.10986 | 59.9533 | -0.24719 | 60.0769 | -0.1236 | -0.041199 | -0.082398 | 0.091552 | 0 | 0.091552 | -0.086975 | 0.13275 | -0.045776 | 0.23346 | 122.9736 | 0.041199 | 122.9919 | 122.9324 | 122.818 | 122.8088 | 122.7768 | -122.9828 | -122.9004 | 122.85 | 122.9507 | 59.6466 | 59.7244
948.8281 | 123.1796 | -59.9075 | 62.9425 | -0.083313 | 0.0030483 | 0.063427 | 0.06595 | -0.0016663 | -0.0016322 | -0.0026853 | 0.15536 | 0.00138 | 0.067486 | 0.063925 | -0.0074084 | 0.003529 | -0.0029309 | -0.19226 | 62.8876 | -60.0128 | 62.9974 | -59.729 | -60.0769 | 0.13275 | -0.35248 | 62.851 | -59.9304 | 63.0569 | -59.8938 | -59.9579 | -59.7794 | -0.10528 | -0.054932 | 0.054932 | 0.17853 | 60.0403 | -0.16937 | 60.1456 | -0.064087 | -0.022888 | -0.091553 | 0.11444 | 0.013733 | 0.12817 | -0.050354 | 0.15106 | -0.027466 | 0.28381 | 123.0103 | 0.036621 | 122.9874 | 122.9004 | 122.7814 | 122.7951 | 122.7585 | -122.9553 | -122.8729 | 122.905 | 122.9645 | 59.7153 | 59.5551
949.8906 | 123.1934 | -59.9396 | 62.9425 | -0.075684 | 0.00091214 | 0.062786 | 0.067445 | 4.2692e-05 | -0.0018458 | -0.0024717 | 0.036346 | 0.0007392 | 0.067913 | 0.069265 | -0.0050586 | 0.0037426 | -0.0012219 | -0.25177 | 62.8738 | -60.0632 | 62.9242 | -59.8251 | -60.1456 | 0.036621 | -0.18768 | 62.8647 | -59.9716 | 63.0615 | -59.9258 | -60.0266 | -59.8206 | -0.1236 | -0.068665 | -0.018311 | 0.11444 | 59.9762 | -0.20599 | 60.0998 | -0.082398 | -0.032044 | -0.07782 | 0.11902 | 0.013733 | 0.11902 | -0.086975 | 0.15106 | -0.054931 | 0.23804 | 122.9874 | 0.045777 | 123.0331 | 122.937 | 122.8363 | 122.8134 | 122.8043 | -123.0057 | -122.9141 | 122.8638 | 123.0011 | 59.6878 | 59.7519
950.8281 | 123.2208 | -59.9167 | 62.9745 | -0.11383 | 0.0021939 | 0.061077 | 0.066591 | -0.0010253 | -0.00099116 | -0.0028989 | 0.018036 | 0.0007392 | 0.066418 | 0.065206 | -0.0052722 | 0.0022472 | 5.9726e-05 | -0.18768 | 62.8967 | -60.0174 | 62.9929 | -59.6924 | -60.2234 | 0.10529 | -0.09613 | 62.8922 | -59.9396 | 63.0615 | -59.8801 | -59.9762 | -59.7977 | -0.10071 | -0.077819 | 0.018311 | 0.2243 | 60.022 | -0.3067 | 60.1227 | -0.20599 | -0.022888 | -0.082397 | 0.086975 | 0.036621 | 0.11902 | -0.059509 | 0.14191 | -0.036621 | 0.32501 | 123.0103 | 0.059509 | 123.0011 | 122.9141 | 122.8317 | 122.8134 | 122.8088 | -122.9919 | -122.9141 | 122.9095 | 122.9782 | 59.729 | 59.8206
951.8906 | 123.1522 | -59.9533 | 62.9379 | -0.090943 | 0.0024075 | 0.063213 | 0.0683 | -0.00059811 | -0.00099116 | -0.0028989 | 0.011932 | -0.002038 | 0.067058 | 0.060079 | -0.0071948 | 0.0043836 | 5.9726e-05 | -0.30212 | 62.883 | -60.0815 | 62.9059 | -59.8297 | -60.1868 | -0.027466 | -0.24719 | 62.883 | -59.9945 | 63.0249 | -59.9533 | -60.0494 | -59.8434 | -0.12817 | -0.054931 | -0.032043 | 0.1236 | 59.9258 | -0.23346 | 60.054 | -0.10529 | -0.041199 | -0.054931 | 0.086975 | 0 | 0.10986 | -0.09613 | 0.15106 | -0.054931 | 0.25177 | 122.9874 | 0.041199 | 123.0194 | 122.9645 | 122.8775 | 122.8363 | 122.8363 | -123.0194 | -122.9324 | 122.8592 | 122.9782 | 59.6512 | 59.7061
952.8281 | 123.175 | -59.9075 | 62.9608 | -0.029907 | 0.0015529 | 0.064281 | 0.0683 | -0.0031617 | 0.001145 | 0.00094633 | 0.014984 | 0.0024482 | 0.065563 | 0.062216 | -0.0063404 | 0.0024608 | 0.0011279 | -0.26093 | 62.8784 | -60.0586 | 63.0157 | -59.7519 | -60.0815 | 0.11444 | -0.073242 | 62.9059 | -59.935 | 63.0615 | -59.8801 | -59.9899 | -59.816 | -0.15106 | -0.082397 | 0.054932 | 0.15564 | 60.022 | -0.17395 | 60.173 | -0.022888 | -0.027466 | -0.054931 | 0.10071 | 0.027466 | 0.091553 | -0.082397 | 0.11902 | -0.054931 | 0.3067 | 123.0743 | 0.054932 | 122.9965 | 122.937 | 122.8409 | 122.786 | 122.8134 | -123.0194 | -122.8958 | 122.9233 | 122.9691 | 59.6466 | 59.8343
953.8281 | 123.1384 | -59.935 | 62.9745 | -0.098572 | 0.0013393 | 0.063427 | 0.067018 | -0.00038451 | -0.0020594 | -0.0022581 | -0.0033265 | 9.8198e-05 | 0.064922 | 0.063925 | -0.0054858 | 0.00011104 | 0.00091433 | -0.16937 | 62.9196 | -60.0266 | 62.9929 | -59.7794 | -60.1181 | 0.11444 | -0.10529 | 62.9105 | -59.9487 | 63.0157 | -59.9487 | -60.0494 | -59.8343 | -0.091552 | -0.054931 | 0.018311 | 0.15564 | 60.0494 | -0.1831 | 60.141 | -0.091553 | -0.013732 | -0.064087 | 0.041199 | -0.013732 | 0.10071 | -0.11444 | 0.11444 | -0.10071 | 0.24719 | 123.0194 | 0 | 122.9645 | 122.9462 | 122.8592 | 122.8546 | 122.8455 | -123.0011 | -122.9233 | 122.9279 | 122.9507 | 59.7656 | 59.8297
954.8281 | 123.1796 | -59.9304 | 62.9425 | -0.098572 | 0.0026211 | 0.062359 | 0.068086 | -0.00081171 | -0.0027002 | -0.00097627 | -0.0094299 | 0.0005256 | 0.067058 | 0.061148 | -0.0056994 | 0.0028882 | 5.9726e-05 | -0.25635 | 62.8876 | -60.054 | 62.9379 | -59.8251 | -60.173 | 0.018311 | -0.20142 | 62.8784 | -59.9808 | 63.0386 | -59.9258 | -60.0174 | -59.8343 | -0.1236 | -0.054932 | -0.004578 | 0.10529 | 59.9487 | -0.24262 | 60.0723 | -0.11902 | -0.050354 | -0.064087 | 0.09613 | 0.004578 | 0.09613 | -0.086975 | 0.14648 | -0.036621 | 0.22888 | 122.9919 | 0.054932 | 123.0194 | 122.9416 | 122.8592 | 122.818 | 122.8088 | -122.9965 | -122.9233 | 122.8683 | 122.9691 | 59.6741 | 59.729
955.8906 | 123.1888 | -59.9442 | 62.9288 | -0.098572 | 0.00069854 | 0.061718 | 0.066377 | 0.0011109 | -0.0027002 | -0.0039671 | -0.021637 | 0.0020208 | 0.067272 | 0.062002 | -0.0054858 | 0.0048108 | -0.0018629 | -0.27466 | 62.851 | -60.0677 | 62.9654 | -59.7839 | -60.1868 | 0 | -0.21515 | 62.8601 | -59.9854 | 63.0066 | -59.9716 | -60.0677 | -59.8526 | -0.1236 | -0.07782 | 0.036621 | 0.16022 | 59.9442 | -0.24262 | 60.0677 | -0.11902 | -0.041199 | -0.068665 | 0.07782 | -0.027466 | 0.091553 | -0.1236 | 0.13275 | -0.082397 | 0.28381 | 123.0331 | 0.013733 | 122.9919 | 122.9187 | 122.8455 | 122.7951 | 122.8043 | -122.9965 | -122.9141 | 122.9095 | 122.9507 | 59.6695 | 59.729
956.8281 | 123.2208 | -59.9258 | 62.9654 | -0.1062 | 0.00091214 | 0.061932 | 0.067232 | 4.2692e-05 | -0.0027002 | -0.0033261 | 0.0058289 | 0.0024482 | 0.064281 | 0.063711 | -0.0052722 | 0.0056652 | 0.00091433 | -0.20599 | 62.9013 | -60.0449 | 62.9883 | -59.7565 | -60.0998 | 0.10986 | -0.09613 | 62.8693 | -59.935 | 63.0798 | -59.8572 | -59.9716 | -59.7931 | -0.11902 | -0.064087 | 0.022888 | 0.16937 | 60.0357 | -0.17395 | 60.1547 | -0.054931 | -0.009156 | -0.09613 | 0.11444 | 0.068664 | 0.13275 | -0.045777 | 0.14191 | -0.036621 | 0.28839 | 123.0331 | 0.07782 | 123.0148 | 122.9462 | 122.8043 | 122.8271 | 122.7951 | -123.0103 | -122.9004 | 122.9141 | 123.0057 | 59.7198 | 59.8297
957.8281 | 123.2391 | -59.9213 | 62.9654 | -0.022278 | 0.0017667 | 0.061718 | 0.067872 | 0.0013245 | -0.0016322 | -0.00054907 | 0.024139 | 0.0018072 | 0.065563 | 0.065634 | -0.0071948 | 0.0020336 | -0.0018629 | -0.17853 | 62.8876 | -60.054 | 63.0203 | -59.7015 | -60.0769 | 0.14648 | -0.054932 | 62.8738 | -59.9487 | 63.0753 | -59.8755 | -59.9579 | -59.7885 | -0.13275 | -0.07782 | 0.054932 | 0.21973 | 60.0677 | -0.15564 | 60.2005 | -0.022888 | -0.027465 | -0.091553 | 0.10986 | 0.045777 | 0.13275 | -0.036621 | 0.16022 | -0.009156 | 0.35248 | 123.0743 | 0.073242 | 123.024 | 122.9416 | 122.8226 | 122.8088 | 122.7951 | -123.0194 | -122.9141 | 122.9416 | 122.9965 | 59.7427 | 59.8663
958.8281 | 123.1934 | -59.9213 | 62.9379 | -0.090943 | 0.0019803 | 0.063641 | 0.066377 | 0.00068369 | -0.00099116 | -0.0028989 | 0.018036 | 0.00138 | 0.065136 | 0.063284 | -0.0054858 | 0.0033154 | 0.00027333 | -0.24719 | 62.8784 | -60.0861 | 62.9471 | -59.8068 | -60.1547 | 0.054932 | -0.1831 | 62.8693 | -59.967 | 63.0524 | -59.9075 | -60.0174 | -59.8343 | -0.1648 | -0.059509 | 0.009156 | 0.11444 | 59.9762 | -0.23346 | 60.141 | -0.068664 | -0.045776 | -0.068664 | 0.11444 | 0.013733 | 0.086975 | -0.09613 | 0.13275 | -0.050354 | 0.27924 | 123.0331 | 0.059509 | 123.0194 | 122.9645 | 122.8363 | 122.7997 | 122.7905 | -123.024 | -122.905 | 122.8683 | 122.9736 | 59.6741 | 59.7382
959.8906 | 123.1934 | -59.9716 | 62.9105 | -0.11383 | -0.0027195 | 0.064068 | 0.067445 | 0.00046989 | -0.0044092 | -0.0022581 | -0.030792 | 0.0022346 | 0.06364 | 0.065847 | -0.0061268 | 0.0024608 | -0.0012219 | -0.26093 | 62.8326 | -60.0998 | 62.9517 | -59.7153 | -60.1868 | -0.013733 | -0.21515 | 62.851 | -59.9991 | 63.0615 | -59.9167 | -60.0357 | -59.8206 | -0.12817 | -0.077819 | 0.041199 | 0.25635 | 59.9579 | -0.21515 | 60.0861 | -0.086976 | -0.027465 | -0.059509 | 0.15106 | 0.054932 | 0.15106 | -0.064087 | 0.17853 | -0.036622 | 0.38452 | 123.0515 | 0.082397 | 123.0606 | 122.9324 | 122.85 | 122.8043 | 122.8226 | -123.0103 | -122.9095 | 122.9233 | 123.0331 | 59.7107 | 59.7565
960.8281 | 123.2254 | -59.8892 | 62.9333 | -0.075684 | -0.00036966 | 0.062786 | 0.067018 | -0.00038451 | 0.001145 | -0.0026853 | -0.0033265 | 0.0020208 | 0.065136 | 0.060079 | -0.0061268 | 0.0020336 | -0.0048535 | -0.21057 | 62.883 | -60.0128 | 63.002 | -59.7473 | -60.1044 | 0.10986 | -0.082397 | 62.883 | -59.9533 | 63.0981 | -59.8572 | -59.9396 | -59.7794 | -0.1236 | -0.050354 | 0.068664 | 0.14191 | 59.9991 | -0.21515 | 60.1227 | -0.091553 | -0.064087 | -0.050354 | 0.1648 | 0.032043 | 0.10986 | -0.050354 | 0.17395 | 0.013733 | 0.2655 | 123.0148 | 0.09613 | 123.0515 | 122.8958 | 122.8363 | 122.7722 | 122.7722 | -122.9462 | -122.8867 | 122.8912 | 122.9874 | 59.6786 | 59.8068
961.8906 | 123.2025 | -59.9396 | 62.9105 | -0.12909 | 0.0024075 | 0.062572 | 0.067232 | 0.0013245 | -0.0012048 | 0.0011599 | -0.10098 | 0.00138 | 0.063854 | 0.066915 | -0.006554 | 0.0058788 | -0.00036747 | -0.28381 | 62.8418 | -60.0815 | 62.9608 | -59.8068 | -60.1776 | -0.009155 | -0.21515 | 62.8601 | -59.9899 | 63.0615 | -59.9121 | -60.0494 | -59.8068 | -0.14191 | -0.068664 | 0.050354 | 0.13275 | 59.9304 | -0.23804 | 60.0723 | -0.09613 | -0.050354 | -0.050354 | 0.15106 | 0.027466 | 0.13275 | -0.10986 | 0.1831 | -0.059509 | 0.27466 | 123.0423 | 0.07782 | 123.0515 | 122.9233 | 122.85 | 122.7814 | 122.7997 | -122.9919 | -122.9004 | 122.9004 | 123.0011 | 59.6558 | 59.7244
962.8281 | 123.175 | -59.9258 | 62.9425 | -0.11383 | 0.0013393 | 0.064922 | 0.067872 | -0.0018799 | -0.00099116 | -0.0022581 | -0.046051 | -0.000329 | 0.065349 | 0.060507 | -0.0050586 | 0.0037426 | -0.00079467 | -0.29297 | 62.8372 | -60.0632 | 62.9288 | -59.8068 | -60.1913 | -0.013733 | -0.25177 | 62.8555 | -59.9625 | 63.002 | -59.9533 | -60.0632 | -59.848 | -0.13733 | -0.10529 | -0.013733 | 0.11902 | 59.9121 | -0.2655 | 60.0494 | -0.12817 | -0.036621 | -0.086975 | 0.059509 | -0.027466 | 0.07782 | -0.13733 | 0.11444 | -0.10071 | 0.25635 | 122.9919 | 0.009155 | 122.9645 | 122.9004 | 122.818 | 122.7631 | 122.7814 | -123.0057 | -122.905 | 122.8546 | 122.9279 | 59.6329 | 59.6741
963.8281 | 123.1934 | -59.935 | 62.9288 | -0.075684 | 0.00048494 | 0.061932 | 0.063173 | -0.0010253 | -0.00099116 | -0.0041807 | -0.012482 | 0.003089 | 0.064281 | 0.070547 | -0.0029224 | 0.0031018 | -0.0031445 | -0.28381 | 62.8922 | -60.0769 | 62.9517 | -59.8251 | -60.1959 | 0.027466 | -0.23346 | 62.883 | -59.9899 | 63.0203 | -59.9213 | -60.0403 | -59.8389 | -0.14191 | -0.036621 | 0.022888 | 0.10986 | 59.9625 | -0.26093 | 60.1044 | -0.11902 | -0.054931 | -0.045776 | 0.091553 | 0.013733 | 0.096131 | -0.10529 | 0.15106 | -0.050354 | 0.25177 | 123.0286 | 0.068664 | 123.0103 | 122.9691 | 122.8729 | 122.8271 | 122.818 | -123.0057 | -122.9187 | 122.8867 | 122.9553 | 59.6512 | 59.7015
964.8906 | 123.1705 | -59.9258 | 62.9242 | -0.12146 | 0.0015529 | 0.064922 | 0.068086 | 0.00068369 | -0.0031274 | -0.0018307 | -0.067413 | 0.0011664 | 0.064922 | 0.063284 | -0.0063404 | 0.0037426 | -0.0022901 | -0.2655 | 62.8235 | -60.0861 | 62.9608 | -59.7748 | -60.1593 | -0.013733 | -0.20599 | 62.8555 | -59.9762 | 63.1073 | -59.9533 | -59.9808 | -59.8068 | -0.16022 | -0.10071 | 0.036621 | 0.15106 | 59.9121 | -0.23346 | 60.0723 | -0.073242 | -0.050354 | -0.068664 | 0.18311 | -0.027466 | 0.11902 | -0.054932 | 0.16937 | -0.004578 | 0.31128 | 123.0469 | 0.022888 | 123.0835 | 122.9095 | 122.8317 | 122.7493 | 122.7814 | -123.0103 | -122.9004 | 122.8867 | 123.0331 | 59.6603 | 59.7198
965.8281 | 123.2162 | -59.9121 | 62.9333 | -0.037537 | -0.00015586 | 0.060009 | 0.067872 | 0.00068369 | 0.001145 | -0.0016171 | -0.0002747 | 0.0005256 | 0.065136 | 0.062216 | -0.0037768 | 0.0026746 | -0.00058107 | -0.23346 | 62.9013 | -60.0586 | 62.9791 | -59.7931 | -60.1501 | 0.086975 | -0.14648 | 62.883 | -59.9396 | 63.0661 | -59.8846 | -59.9808 | -59.7931 | -0.14648 | -0.032044 | 0.045776 | 0.11902 | 59.9991 | -0.23804 | 60.1456 | -0.091552 | -0.027466 | -0.050354 | 0.13275 | 0.027465 | 0.11902 | -0.068665 | 0.14648 | -0.041199 | 0.2655 | 123.0377 | 0.054931 | 123.0057 | 122.9599 | 122.8226 | 122.8134 | 122.7951 | -122.9919 | -122.8729 | 122.8912 | 122.9782 | 59.6786 | 59.7656
966.8281 | 123.1613 | -59.9579 | 62.9013 | -0.22827 | 0.0011257 | 0.062359 | 0.067445 | 0.0021789 | 0.00050424 | -0.0011899 | -0.049103 | 0.0018072 | 0.065563 | 0.062643 | -0.0042042 | 0.0031018 | -0.0072035 | -0.2243 | 62.8464 | -60.0586 | 62.9745 | -59.7794 | -60.1776 | 0 | -0.20599 | 62.8418 | -59.9716 | 63.0753 | -59.9396 | -60.0403 | -59.8297 | -0.10071 | -0.054931 | 0.073242 | 0.17853 | 59.9579 | -0.21973 | 60.0586 | -0.11902 | -0.013733 | -0.059509 | 0.17395 | 0.018311 | 0.12817 | -0.082397 | 0.14191 | -0.068664 | 0.27924 | 123.0331 | 0.032044 | 123.0469 | 122.905 | 122.8134 | 122.8043 | 122.7997 | -122.9599 | -122.8729 | 122.9324 | 123.0331 | 59.7336 | 59.7519
967.8906 | 123.1842 | -59.9396 | 62.9242 | -0.1062 | 0.0021939 | 0.064281 | 0.070222 | 0.0019653 | -0.00056396 | -0.00097627 | -0.082672 | 0.0020208 | 0.065349 | 0.062429 | -0.0069812 | 0.0060924 | -0.0014355 | -0.32501 | 62.8967 | -60.0952 | 62.883 | -59.8801 | -60.2509 | -0.07782 | -0.31586 | 62.8876 | -60.0266 | 63.0157 | -59.967 | -60.0815 | -59.8572 | -0.15564 | -0.027465 | -0.041198 | 0.059509 | 59.8618 | -0.31128 | 60.0174 | -0.15564 | -0.086975 | -0.036621 | 0.091553 | -0.027466 | 0.082397 | -0.14191 | 0.16937 | -0.054932 | 0.21515 | 122.9782 | 0.059509 | 123.0423 | 122.9919 | 122.9141 | 122.8363 | 122.8271 | -123.0194 | -122.9507 | 122.8226 | 122.9553 | 59.6146 | 59.6237
968.8281 | 123.1705 | -59.9991 | 62.8601 | -0.14435 | 0.0021939 | 0.064281 | 0.066377 | 0.0013245 | -0.0016322 | 9.193e-05 | -0.039948 | 0.0015936 | 0.064068 | 0.063925 | -0.0074084 | 0.0041698 | 0.00048713 | -0.27008 | 62.8189 | -60.0723 | 62.9608 | -59.7977 | -60.1593 | -0.004578 | -0.21515 | 62.8601 | -59.9808 | 63.0615 | -59.9213 | -60.0403 | -59.7519 | -0.073243 | -0.041198 | 0.10071 | 0.20142 | 59.9945 | -0.16022 | 60.0677 | -0.086975 | 0.01831 | 0 | 0.20142 | 0.077819 | 0.24719 | -0.041199 | 0.22888 | -0.059509 | 0.27466 | 123.0331 | 0.059509 | 123.0423 | 122.8912 | 122.8409 | 122.818 | 122.8592 | -122.9324 | -122.8409 | 122.9599 | 123.0606 | 59.729 | 59.7839
969.8281 | 123.2071 | -59.935 | 62.9013 | -0.16724 | 5.7742e-05 | 0.064709 | 0.067872 | 0.0023925 | -0.00077756 | -0.0020443 | -0.042999 | 0.0005256 | 0.065777 | 0.059439 | -0.004845 | 0.0041698 | 5.9726e-05 | -0.25177 | 62.8464 | -60.054 | 62.7457 | -59.8572 | -59.8343 | 0.036621 | -0.20142 | 62.8647 | -59.9533 | 63.0661 | -59.9213 | -60.0311 | -59.8251 | -0.11902 | -0.054931 | -0.15564 | 0.07782 | 59.9716 | 0.10071 | 60.0906 | 0.21973 | -0.01831 | -0.036621 | 0.1648 | 0.013733 | 0.10986 | -0.09613 | 0.12817 | -0.07782 | 0.19684 | 122.7997 | 0.032043 | 123.0194 | 122.9004 | 122.818 | 122.7814 | 122.7997 | -122.9553 | -122.8546 | 122.6807 | 123.0011 | 59.6832 | 59.7336
970.8906 | 123.0972 | -59.9533 | 62.9745 | -0.11383 | 0.0026211 | 0.063 | 0.068513 | -0.0020935 | -0.0027002 | -0.0018307 | -0.058258 | 0.0009528 | 0.065563 | 0.058798 | -0.0050586 | 0.0048108 | -0.0014355 | -0.21515 | 62.9517 | -60.0311 | 62.9013 | -59.8434 | -60.2142 | 0.050354 | -0.20599 | 62.9288 | -59.9762 | 62.97 | -59.9808 | -60.0906 | -59.9167 | -0.07782 | -0.022888 | -0.073242 | 0.10986 | 60.0037 | -0.26093 | 60.0815 | -0.1831 | -0.022888 | -0.045776 | -0.004577 | -0.027466 | 0.036621 | -0.13733 | 0.059509 | -0.11444 | 0.18768 | 122.9324 | -0.004578 | 122.9462 | 122.9828 | 122.905 | 122.905 | 122.8821 | -123.0057 | -122.9507 | 122.8546 | 122.9233 | 59.7382 | 59.7473
971.8281 | 123.1476 | -59.9442 | 62.9471 | -0.068054 | -0.00036966 | 0.062145 | 0.067018 | -0.0020935 | -0.00056396 | -0.0016171 | -0.042999 | 0.0011664 | 0.066845 | 0.065847 | -0.0044178 | 0.0048108 | 0.0013415 | -0.27924 | 62.851 | -60.0815 | 62.9425 | -59.7748 | -60.1685 | -0.018311 | -0.2243 | 62.8555 | -59.9808 | 63.0112 | -59.9625 | -60.0677 | -59.8663 | -0.13733 | -0.096131 | -0.004578 | 0.16937 | 59.9258 | -0.2243 | 60.0632 | -0.086975 | -0.036621 | -0.091553 | 0.064086 | -0.01831 | 0.07782 | -0.1236 | 0.11444 | -0.086975 | 0.3067 | 123.024 | 0.018311 | 122.9919 | 122.9324 | 122.8363 | 122.7951 | 122.7997 | -123.0286 | -122.9279 | 122.8867 | 122.9553 | 59.6649 | 59.7198
972.8281 | 123.2162 | -59.935 | 62.9288 | -0.090943 | -0.00015586 | 0.063427 | 0.068941 | 0.0011109 | -0.0031274 | -0.0020443 | -0.070465 | 0.0018072 | 0.06364 | 0.066061 | -0.004845 | 0.005238 | -0.0029309 | -0.31128 | 62.8693 | -60.1044 | 62.9196 | -59.8434 | -60.2463 | -0.059509 | -0.2655 | 62.8464 | -59.9808 | 63.0524 | -59.9396 | -60.0586 | -59.8206 | -0.16937 | -0.059509 | -0.009155 | 0.091553 | 59.8755 | -0.31128 | 60.0449 | -0.14191 | -0.045776 | -0.082397 | 0.1236 | -0.004577 | 0.11444 | -0.1236 | 0.16022 | -0.07782 | 0.26093 | 123.024 | 0.041199 | 123.0331 | 122.9736 | 122.8271 | 122.8043 | 122.7814 | -123.0331 | -122.9095 | 122.8546 | 122.9874 | 59.6237 | 59.6695
973.8281 | 123.1934 | -59.9487 | 62.883 | -0.1062 | 0.0021939 | 0.065563 | 0.067659 | 0.0013245 | -0.0041956 | 0.00094633 | -0.055206 | 0.0009528 | 0.065349 | 0.059866 | -0.0067676 | 0.0031018 | 0.00070073 | -0.47607 | 62.7914 | -60.0906 | 62.9562 | -59.7794 | -60.141 | 0.013733 | -0.17853 | 62.8372 | -59.9808 | 63.0707 | -59.9304 | -60.0174 | -59.8251 | -0.14191 | -0.091553 | 0.073242 | 0.16937 | 59.9625 | -0.19226 | 60.1044 | -0.050354 | -0.032044 | -0.045777 | 0.18768 | 0.01831 | 0.1236 | -0.068665 | 0.15564 | -0.036621 | 0.31128 | 123.0469 | 0.050354 | 123.0515 | 122.8821 | 122.818 | 122.7402 | 122.7859 | -122.9736 | -122.8638 | 122.905 | 123.0194 | 59.4727 | 59.7702
974.8906 | 123.1705 | -59.9762 | 62.9242 | -0.14435 | 0.00069854 | 0.059795 | 0.070222 | 0.0011109 | -0.0041956 | 0.0052187 | -0.10098 | 0.0026618 | 0.065777 | 0.070547 | -0.0046314 | 0.0050244 | 5.9726e-05 | -0.31586 | 62.915 | -60.1089 | 62.8555 | -59.903 | -60.2829 | -0.082397 | -0.33417 | 62.8967 | -59.9854 | 63.002 | -60.0128 | -60.1135 | -59.8892 | -0.13275 | -0.009155 | -0.068664 | 0.073242 | 59.8938 | -0.3067 | 60.0266 | -0.17395 | -0.009156 | -0.027465 | 0.07782 | -0.036621 | 0.086975 | -0.13733 | 0.096131 | -0.12817 | 0.20599 | 122.9645 | -0.027465 | 122.9874 | 123.024 | 122.8821 | 122.8912 | 122.8729 | -123.0331 | -122.9095 | 122.8317 | 122.9782 | 59.6603 | 59.642
975.8281 | 123.1796 | -59.9533 | 62.9059 | -0.098572 | 0.0015529 | 0.062359 | 0.066804 | 0.00068369 | 0.00029044 | -0.0022581 | -0.012482 | 0.0028754 | 0.064281 | 0.063711 | -0.0054858 | 0.0024608 | -0.0031445 | -0.28839 | 62.851 | -60.0677 | 62.915 | -59.8022 | -60.2005 | -0.009155 | -0.23804 | 62.8738 | -59.9716 | 63.0203 | -59.9762 | -60.0769 | -59.848 | -0.11444 | -0.054932 | 0.009155 | 0.15106 | 59.9442 | -0.24719 | 60.0586 | -0.13275 | -0.018311 | -0.032044 | 0.11444 | -0.022888 | 0.10529 | -0.1236 | 0.1236 | -0.10529 | 0.2655 | 122.9828 | -0.004577 | 122.9919 | 122.9187 | 122.8455 | 122.8043 | 122.8271 | -122.9736 | -122.8775 | 122.8683 | 122.9736 | 59.6649 | 59.7153
976.8906 | 123.1155 | -59.9579 | 62.97 | -0.090943 | 0.0013393 | 0.065136 | 0.067445 | 0.0015381 | -0.0012048 | -0.0011899 | -0.10098 | 0.0037298 | 0.067486 | 0.06777 | -0.0046314 | 0.0054516 | -0.0035719 | -0.24719 | 62.9105 | -60.0998 | 62.9196 | -59.8526 | -60.2005 | -0.018311 | -0.23804 | 62.9013 | -59.9945 | 62.9883 | -60.0311 | -60.1181 | -59.903 | -0.14191 | -0.05951 | -0.050354 | 0.10529 | 59.9396 | -0.24261 | 60.0815 | -0.10071 | -0.036621 | -0.068665 | 0.01831 | -0.073242 | 0.054932 | -0.16022 | 0.091553 | -0.1236 | 0.24719 | 123.0194 | -0.036621 | 122.9828 | 123.0103 | 122.8958 | 122.8683 | 122.8592 | -123.0698 | -122.9645 | 122.8775 | 122.9462 | 59.7107 | 59.7198
977.8281 | 123.2117 | -59.9442 | 62.9059 | 0.00061049 | 0.0011257 | 0.062572 | 0.067232 | -0.00059811 | -0.0014184 | 0.00073273 | -0.021637 | 0.0009528 | 0.066418 | 0.067129 | -0.0050586 | 0.0022472 | 0.00070073 | -0.26093 | 62.851 | -60.0449 | 62.9379 | -59.7977 | -60.141 | 0 | -0.21973 | 62.851 | -59.9579 | 63.0524 | -59.9304 | -60.0403 | -59.8206 | -0.10071 | -0.054932 | 0.032043 | 0.14648 | 59.9442 | -0.19684 | 60.0449 | -0.09613 | -0.013733 | -0.054932 | 0.14648 | 0.013733 | 0.1236 | -0.09613 | 0.13733 | -0.082397 | 0.24719 | 122.9828 | 0.027466 | 123.0103 | 122.8958 | 122.8088 | 122.7951 | 122.7951 | -122.9507 | -122.8638 | 122.8821 | 122.9965 | 59.6832 | 59.7244
978.8281 | 123.0743 | -59.9716 | 62.9608 | -0.1062 | 0.00048494 | 0.062786 | 0.070649 | -0.0031617 | -0.0031274 | -0.0011899 | -0.091827 | 0.0026618 | 0.065563 | 0.063497 | -0.0063404 | 0.0073742 | -0.0016493 | -0.32501 | 62.9013 | -60.1135 | 62.8326 | -59.9304 | -60.2921 | -0.10071 | -0.37537 | 62.8922 | -60.022 | 62.7411 | -59.7702 | -59.967 | -59.8709 | -0.14191 | -0.059509 | -0.12817 | 0.041199 | 59.8709 | -0.32043 | 60.0128 | -0.17853 | -0.050354 | -0.068664 | -0.21973 | 0.20142 | 0.10071 | 0.004578 | 0.15106 | 0.054932 | 0.18311 | 122.9462 | 0.25177 | 122.7631 | 123.0148 | 122.9141 | 122.8729 | 122.8638 | -123.0743 | -122.9828 | 122.8043 | 122.7127 | 59.6466 | 59.5963
979.8906 | 123.2071 | -59.903 | 62.9425 | -0.068054 | -0.00079686 | 0.061932 | 0.064882 | -0.0016663 | -0.0041956 | -0.0011899 | 0.024139 | -0.0001154 | 0.06364 | 0.056021 | -0.003136 | 0.003529 | 0.0015551 | -0.24719 | 62.8555 | -60.054 | 62.97 | -59.7336 | -60.0998 | 0.10071 | -0.091553 | 62.8738 | -59.9625 | 63.1119 | -59.8572 | -59.9533 | -59.7931 | -0.15106 | -0.086975 | 0.027466 | 0.16937 | 60.0037 | -0.19684 | 60.1547 | -0.045776 | -0.059509 | -0.068665 | 0.16937 | 0.045776 | 0.10986 | -0.050354 | 0.16937 | 0.009155 | 0.32043 | 123.024 | 0.10529 | 123.0743 | 122.9095 | 122.8363 | 122.7585 | 122.7768 | -122.9965 | -122.905 | 122.8729 | 123.0148 | 59.6558 | 59.8114
980.8281 | 123.1567 | -59.9625 | 62.9791 | -0.052796 | 0.00048494 | 0.061504 | 0.068086 | 0.0021789 | -0.0037684 | -0.00033547 | -0.085724 | 0.0020208 | 0.063 | 0.064352 | -0.0035632 | 0.0078014 | -0.00058107 | -0.32501 | 62.883 | -60.1181 | 62.8372 | -59.935 | -60.2921 | -0.10071 | -0.35706 | 62.9013 | -60.0174 | 62.8922 | -59.7702 | -60.1959 | -59.9991 | -0.15564 | -0.09613 | -0.14191 | 0.027465 | 59.8618 | -0.32959 | 60.0174 | -0.17395 | -0.054932 | -0.07782 | -0.086975 | 0.19226 | -0.036621 | -0.23346 | 0.018311 | -0.17853 | 0.1831 | 122.9553 | 0.24719 | 122.9095 | 123.0011 | 122.9187 | 122.8455 | 122.8638 | -123.0972 | -122.9965 | 122.7997 | 122.8546 | 59.6375 | 59.6054
981.8281 | 123.175 | -59.9625 | 62.9105 | -0.19012 | -0.00015586 | 0.061718 | 0.070436 | -0.0010253 | -0.0020594 | -0.0022581 | -0.070465 | 0.0018072 | 0.065777 | 0.063711 | -0.0035632 | 0.0039562 | -0.0010083 | -0.31586 | 62.8784 | -60.1181 | 62.8693 | -59.8755 | -60.2371 | -0.07782 | -0.29297 | 62.8967 | -59.9945 | 63.0157 | -59.9808 | -60.0632 | -59.8572 | -0.15564 | -0.032043 | -0.041198 | 0.086975 | 59.8846 | -0.27466 | 60.0403 | -0.11902 | -0.032044 | -0.013732 | 0.10529 | -0.018311 | 0.10529 | -0.10071 | 0.13733 | -0.068664 | 0.24262 | 122.9874 | 0.013733 | 123.0103 | 122.9965 | 122.8912 | 122.8409 | 122.8592 | -123.0286 | -122.905 | 122.8317 | 122.9782 | 59.6466 | 59.6695
982.8281 | 123.1384 | -59.9579 | 62.9562 | -0.075684 | -0.0016513 | 0.061504 | 0.067872 | 0.0011109 | -0.0031274 | -0.0028989 | -0.082672 | 0.0018072 | 0.065349 | 0.067343 | -0.0039906 | 0.0037426 | -0.0029309 | -0.21973 | 62.9105 | -60.0769 | 62.9196 | -59.8114 | -60.1913 | 0.050354 | -0.17853 | 62.9013 | -59.9487 | 63.0341 | -59.967 | -60.0769 | -59.8709 | -0.11902 | -0.045777 | -0.036621 | 0.14649 | 60.0082 | -0.23346 | 60.1273 | -0.11444 | 0.009156 | -0.054932 | 0.07782 | -0.009155 | 0.086975 | -0.11902 | 0.077819 | -0.12817 | 0.2655 | 122.9965 | -0.018311 | 122.9828 | 122.9874 | 122.85 | 122.8683 | 122.8592 | -123.0331 | -122.905 | 122.8775 | 122.9919 | 59.7382 | 59.7794
983.8281 | 123.0743 | -59.9808 | 62.9471 | -0.11383 | 0.0017667 | 0.064922 | 0.068941 | -0.00081171 | -0.0014184 | -0.0018307 | -0.070465 | 0.003089 | 0.066204 | 0.06542 | -0.0039906 | 0.005238 | 0.0041187 | -0.30212 | 62.8967 | -60.1044 | 62.851 | -59.9258 | -60.2829 | -0.082397 | -0.36163 | 62.9196 | -60.0082 | 62.9288 | -60.0769 | -60.1913 | -59.9487 | -0.1236 | -0.050354 | -0.096131 | 0.054932 | 59.8984 | -0.30212 | 60.022 | -0.17853 | -0.027466 | -0.027466 | -0.018311 | -0.09613 | 0.032044 | -0.21057 | 0.05951 | -0.1831 | 0.17853 | 122.9553 | -0.068664 | 122.937 | 123.0011 | 122.9279 | 122.8775 | 122.9004 | -123.0515 | -122.9553 | 122.8317 | 122.9095 | 59.6786 | 59.6191
984.8906 | 123.1201 | -59.9533 | 62.97 | -0.083313 | 0.0021939 | 0.062572 | 0.067018 | 0.00025629 | -0.00035036 | -0.00033547 | 0.0027771 | 0.0011664 | 0.066204 | 0.065847 | -0.0042042 | 0.003529 | -0.0010083 | -0.18768 | 62.9105 | -60.0311 | 62.9517 | -59.7748 | -60.1227 | 0.10529 | -0.13275 | 62.9013 | -59.9396 | 63.002 | -59.9625 | -60.0494 | -59.8709 | -0.07782 | -0.05951 | -0.018311 | 0.17853 | 60.0586 | -0.16937 | 60.1364 | -0.091553 | 0.013733 | -0.068665 | 0.032043 | -0.009155 | 0.082397 | -0.09613 | 0.068664 | -0.10986 | 0.25635 | 122.9828 | -0.022888 | 122.9416 | 122.9416 | 122.8409 | 122.8638 | 122.8546 | -123.0011 | -122.9095 | 122.905 | 122.9553 | 59.7656 | 59.8206
985.8281 | 123.1247 | -59.9854 | 62.9333 | -0.13672 | 0.00048494 | 0.063427 | 0.068513 | 0.0028199 | 0.0032812 | 0.0022281 | -0.027741 | 0.0024482 | 0.068767 | 0.069479 | -0.0052722 | 0.0039562 | -0.00036747 | -0.32501 | 62.8922 | -60.1089 | 62.6221 | -59.8755 | -59.9304 | -0.09613 | -0.33417 | 62.9105 | -59.9762 | 62.97 | -60.0494 | -60.1685 | -59.9304 | -0.1236 | -0.041199 | -0.31128 | 0.10986 | 59.8892 | 0.054932 | 60.0128 | 0.17853 | 0.009156 | -0.022889 | 0.036621 | -0.064086 | 0.054932 | -0.1831 | 0.045776 | -0.19226 | 0.23346 | 122.731 | -0.073242 | 122.9462 | 123.0011 | 122.8867 | 122.8775 | 122.8958 | -123.0423 | -122.9095 | 122.6074 | 122.9553 | 59.6603 | 59.6512
986.8906 | 123.1247 | -59.9442 | 63.0066 | -0.1062 | 0.0036893 | 0.063427 | 0.067018 | -0.00059811 | -0.0031274 | 0.0018009 | -0.027741 | 0.0035162 | 0.065563 | 0.066702 | -0.0076222 | 0.0039562 | 0.0024097 | -0.32501 | 62.9379 | -60.0677 | 62.8693 | -59.8434 | -60.2097 | 0.027466 | -0.2243 | 62.9288 | -59.967 | 62.9791 | -59.9762 | -60.0723 | -59.8892 | -0.1236 | -0.068665 | -0.13733 | 0.10071 | 59.9716 | -0.2655 | 60.0952 | -0.14191 | -0.022888 | -0.07782 | -0.027466 | -0.032043 | 0.054932 | -0.12817 | 0.07782 | -0.10529 | 0.2243 | 122.937 | -0.009155 | 122.9462 | 123.0057 | 122.8958 | 122.8821 | 122.8729 | -123.0743 | -122.9736 | 122.8134 | 122.9233 | 59.6191 | 59.7198
987.8281 | 123.0606 | -59.9899 | 62.9745 | -0.075684 | 0.0019803 | 0.064068 | 0.067445 | 0.0060241 | -0.00013676 | -0.0033261 | -0.097931 | 0.0018072 | 0.065136 | 0.063284 | -0.0046314 | 0.0056652 | 0.0028369 | -0.31128 | 62.9059 | -60.1181 | 62.8372 | -59.9396 | -60.2921 | -0.091553 | -0.3479 | 62.9013 | -59.9991 | 62.9242 | -60.0906 | -60.2142 | -59.9213 | -0.12817 | -0.068664 | -0.13733 | 0.050354 | 59.8984 | -0.30212 | 60.0266 | -0.17395 | -0.009155 | -0.073242 | -0.050354 | -0.10071 | 0.068664 | -0.2243 | 0.077819 | -0.21515 | 0.17853 | 122.9553 | -0.091553 | 122.9233 | 123.024 | 122.9004 | 122.8958 | 122.8912 | -123.0927 | -122.9736 | 122.8271 | 122.9141 | 59.6786 | 59.642
988.8906 | 123.1384 | -59.9258 | 62.9654 | -0.075684 | 0.0019803 | 0.061932 | 0.0683 | 4.2692e-05 | -0.0029138 | -0.00033547 | 0.024139 | 0.0022346 | 0.065349 | 0.064138 | -0.0037768 | 0.003529 | -0.0048535 | -0.19226 | 62.9105 | -60.0311 | 62.9608 | -59.7794 | -60.1135 | 0.11444 | -0.1236 | 62.9196 | -59.9579 | 63.0112 | -59.935 | -60.0266 | -59.8526 | -0.10529 | -0.054932 | -0.004578 | 0.14648 | 60.0403 | -0.18768 | 60.1456 | -0.082397 | -0.032044 | -0.045776 | 0.045776 | -0.009156 | 0.073242 | -0.10071 | 0.10529 | -0.068664 | 0.25177 | 122.9919 | 0.022888 | 122.9691 | 122.9416 | 122.8775 | 122.8363 | 122.8455 | -122.9965 | -122.9233 | 122.8867 | 122.937 | 59.7336 | 59.8022
989.8281 | 123.1476 | -59.9442 | 62.9745 | -0.052796 | 0.00091214 | 0.062359 | 0.068513 | 0.00046989 | -0.0024866 | -0.0016171 | -0.06131 | 0.0028754 | 0.066631 | 0.062643 | -0.004845 | 0.0043836 | -0.00036747 | -0.23346 | 62.915 | -60.0861 | 62.9105 | -59.816 | -60.1822 | 0.032043 | -0.17853 | 62.9059 | -59.9716 | 62.9654 | -60.0128 | -60.022 | -59.8801 | -0.14191 | -0.059509 | -0.064087 | 0.12817 | 59.9762 | -0.23804 | 60.1181 | -0.09613 | -0.027466 | -0.068664 | -0.009155 | -0.068664 | 0.064087 | -0.07782 | 0.091553 | -0.050354 | 0.27008 | 122.9965 | -0.041198 | 122.937 | 123.0011 | 122.8775 | 122.8592 | 122.85 | -123.0606 | -122.9462 | 122.8546 | 122.9095 | 59.7107 | 59.7656
990.8906 | 123.0835 | -59.9625 | 62.9837 | -0.098572 | 5.7742e-05 | 0.058727 | 0.066163 | -0.0031617 | -0.0035548 | -0.0026853 | -0.012482 | 0.0022346 | 0.068127 | 0.061788 | -0.0044178 | 0.0043836 | -0.0016493 | -0.23804 | 62.9196 | -60.0677 | 62.883 | -59.8389 | -60.1959 | 0.045776 | -0.18768 | 62.9425 | -59.935 | 62.9562 | -59.9991 | -60.0952 | -59.8984 | -0.10529 | -0.064087 | -0.10071 | 0.1236 | 60.0082 | -0.23346 | 60.1135 | -0.12817 | 0.027465 | -0.041199 | -0.027466 | -0.036621 | 0.064087 | -0.13275 | 0.036622 | -0.16022 | 0.22888 | 122.9507 | -0.064086 | 122.8912 | 122.9874 | 122.8775 | 122.8821 | 122.905 | -123.0515 | -122.9187 | 122.8455 | 122.9187 | 59.7244 | 59.7748
991.8281 | 123.1338 | -59.9487 | 62.97 | -0.075684 | 0.00091214 | 0.061932 | 0.067659 | 0.00025629 | -0.0035548 | 0.00030553 | -0.055206 | 0.003089 | 0.063427 | 0.062002 | -0.003136 | 0.0033154 | -0.0037855 | -0.21973 | 62.9242 | -60.0494 | 62.915 | -59.8114 | -60.1639 | 0.050354 | -0.16479 | 62.915 | -59.9899 | 62.9333 | -60.0266 | -60.0266 | -59.8846 | -0.10071 | -0.045777 | -0.054932 | 0.13733 | 59.9991 | -0.21515 | 60.0998 | -0.11444 | -0.041199 | -0.054932 | -0.036621 | -0.07782 | 0.064086 | -0.07782 | 0.10528 | -0.036621 | 0.23804 | 122.9645 | -0.036621 | 122.9233 | 122.9736 | 122.905 | 122.8729 | 122.8638 | -123.0194 | -122.9599 | 122.8638 | 122.8821 | 59.729 | 59.7839
992.8906 | 123.2483 | -59.9304 | 62.9425 | -0.1062 | 0.00027134 | 0.061504 | 0.065095 | -0.00059811 | 0.00029044 | -0.0054623 | 0.06076 | 0.00138 | 0.067486 | 0.057302 | -0.0029224 | 0.0043836 | -0.0037855 | -0.23804 | 62.8784 | -60.0586 | 62.9745 | -59.7198 | -60.0677 | 0.1236 | -0.073242 | 62.8693 | -59.9487 | 63.0844 | -59.8389 | -59.9304 | -59.7748 | -0.12817 | -0.064087 | 0.032043 | 0.21057 | 60.054 | -0.13733 | 60.1822 | -0.009155 | -0.01831 | -0.073242 | 0.14191 | 0.091553 | 0.15564 | 0 | 0.17395 | 0.01831 | 0.33874 | 123.0331 | 0.10986 | 123.0331 | 122.937 | 122.818 | 122.8088 | 122.7997 | -123.0011 | -122.8912 | 122.905 | 123.0148 | 59.6924 | 59.8572
993.8281 | 123.1201 | -59.9579 | 62.9745 | -0.060425 | 0.0011257 | 0.062786 | 0.068941 | -0.00081171 | -0.0016322 | -0.0024717 | -0.058258 | 0.0026618 | 0.06599 | 0.066702 | -0.0056994 | 0.0041698 | 0.0081775 | -0.22888 | 62.883 | -60.0815 | 62.9242 | -59.816 | -60.1868 | 0.045776 | -0.16479 | 62.9196 | -59.9716 | 63.0524 | -60.1135 | -60.0632 | -59.8068 | -0.1236 | -0.091552 | -0.050354 | 0.14191 | 60.0037 | -0.22888 | 60.1273 | -0.10529 | -0.013733 | -0.054931 | 0.07782 | -0.15564 | 0.15106 | -0.10528 | 0.16479 | -0.091552 | 0.2655 | 123.0057 | -0.14191 | 123.024 | 122.9645 | 122.8912 | 122.8409 | 122.8775 | -123.056 | -122.9462 | 122.8821 | 123.0103 | 59.729 | 59.7931
994.8906 | 123.1613 | -59.9396 | 62.9059 | -0.15198 | 0.0013393 | 0.063427 | 0.067232 | 0.0017517 | -0.00099116 | -0.00054907 | 0.014984 | 0.0026618 | 0.065349 | 0.058798 | -0.0042042 | 0.0026746 | -0.0063489 | -0.29755 | 62.8464 | -60.0906 | 62.915 | -59.8206 | -60.2005 | -0.027466 | -0.24719 | 62.851 | -59.9899 | 63.002 | -59.9762 | -60.0403 | -59.8434 | -0.15106 | -0.059509 | 0.009155 | 0.11902 | 59.9121 | -0.26093 | 60.0632 | -0.10986 | -0.050354 | -0.054932 | 0.09613 | -0.036621 | 0.09613 | -0.10071 | 0.14648 | -0.050354 | 0.27008 | 123.0057 | 0.013733 | 122.9919 | 122.937 | 122.8409 | 122.7859 | 122.7905 | -122.9965 | -122.8958 | 122.8546 | 122.9416 | 59.642 | 59.6924
995.8281 | 123.143 | -59.9625 | 62.9608 | -0.1062 | 0.0015529 | 0.063 | 0.068941 | 0.0036743 | -0.0044092 | -0.00012167 | -0.030792 | 0.0018072 | 0.069408 | 0.072256 | -0.0061268 | 0.003529 | -0.00058107 | -0.22888 | 62.9288 | -60.0861 | 62.9196 | -59.8389 | -60.1776 | 0.045776 | -0.19226 | 62.9333 | -59.9762 | 62.9929 | -59.9625 | -60.0632 | -59.8709 | -0.1236 | -0.032043 | -0.041198 | 0.1236 | 60.0082 | -0.21515 | 60.1318 | -0.091552 | -0.013733 | -0.027465 | 0.032044 | 0 | 0.091552 | -0.10071 | 0.10529 | -0.086975 | 0.24719 | 123.0057 | 0.013733 | 122.9691 | 123.0148 | 122.9095 | 122.8912 | 122.8958 | -123.0469 | -122.937 | 122.8821 | 122.9553 | 59.7336 | 59.7702
996.8906 | 123.1567 | -59.935 | 62.9471 | -0.15198 | 0.0028347 | 0.063641 | 0.068086 | 0.0013245 | -0.0033412 | -0.0024717 | -0.0033265 | 0.0020208 | 0.067272 | 0.057302 | -0.0059132 | 0.0033154 | -0.0027173 | -0.2655 | 62.8372 | -60.0815 | 62.9196 | -59.8114 | -60.1913 | -0.013733 | -0.25177 | 62.8418 | -59.9716 | 63.0066 | -59.9808 | -60.0357 | -59.8434 | -0.14648 | -0.10986 | -0.027466 | 0.1236 | 59.9213 | -0.25635 | 60.0677 | -0.10986 | -0.036621 | -0.10529 | 0.059509 | -0.045776 | 0.091553 | -0.10071 | 0.12817 | -0.064087 | 0.27008 | 123.0011 | -0.009155 | 122.9782 | 122.9187 | 122.8134 | 122.7722 | 122.7768 | -123.0286 | -122.9187 | 122.8546 | 122.9416 | 59.6695 | 59.6832
997.8281 | 123.0835 | -59.9167 | 62.9929 | -0.022278 | 0.00027134 | 0.061932 | 0.067872 | -0.0027343 | -0.0029138 | -0.00076267 | 0.0088807 | 0.0018072 | 0.067486 | 0.063284 | -0.0052722 | 0.0022472 | -0.0020765 | -0.23346 | 62.9333 | -60.0632 | 62.9013 | -59.8526 | -60.1868 | 0.050354 | -0.20142 | 62.9242 | -59.9808 | 62.9745 | -59.9762 | -60.0998 | -59.9167 | -0.14648 | -0.059509 | -0.091553 | 0.064087 | 59.967 | -0.27008 | 60.1135 | -0.1236 | -0.064087 | -0.068665 | -0.018311 | -0.059509 | 0 | -0.1831 | 0.064087 | -0.11902 | 0.21057 | 122.9645 | 0.004578 | 122.9553 | 122.9965 | 122.905 | 122.85 | 122.8409 | -123.056 | -122.9736 | 122.818 | 122.8912 | 59.6832 | 59.7153
998.8906 | 123.0835 | -59.9808 | 62.9654 | -0.12909 | 0.00027134 | 0.061718 | 0.069581 | -0.00059811 | -0.00077756 | -0.0020443 | -0.073517 | 0.0022346 | 0.064495 | 0.067556 | -0.0056994 | 0.0056652 | -0.0039991 | -0.29297 | 62.9105 | -60.0998 | 62.8647 | -59.9442 | -60.2875 | -0.082397 | -0.35706 | 62.9105 | -59.9991 | 62.9242 | -60.0952 | -60.2005 | -59.9396 | -0.11902 | -0.054932 | -0.10071 | 0.036621 | 59.8984 | -0.3067 | 60.0174 | -0.18768 | -0.01831 | -0.054932 | -0.041199 | -0.11444 | 0.041199 | -0.21973 | 0.059509 | -0.20142 | 0.15564 | 122.9645 | -0.096131 | 122.9233 | 123.0103 | 122.9095 | 122.8912 | 122.8912 | -123.0652 | -122.9645 | 122.8455 | 122.905 | 59.6878 | 59.6237
999.8281 | 123.0789 | -59.9213 | 63.0066 | 0.015869 | 0.00048494 | 0.061932 | 0.0683 | -0.00017091 | -0.0018458 | -0.0039671 | -0.11929 | 0.0062934 | 0.064709 | 0.059225 | -0.0042042 | 0.0037426 | 0.00091433 | -0.25635 | 62.9517 | -60.0769 | 62.883 | -59.8755 | -60.0723 | 0.24719 | -0.21515 | 62.9196 | -59.967 | 62.9654 | -59.9899 | -60.1181 | -59.9075 | -0.15564 | -0.054932 | -0.1236 | 0.045777 | 60.1685 | -0.15106 | 60.3241 | 0.004577 | -0.045776 | -0.086975 | -0.041199 | -0.068664 | 0.013733 | -0.19684 | 0.059509 | -0.15106 | 0.20142 | 122.9599 | -0.022888 | 122.9324 | 123.0286 | 122.8867 | 122.8729 | 122.8409 | -123.0835 | -122.9736 | 122.8043 | 122.8867 | 59.6649 | 59.7061
1000.8906 | 123.1979 | -59.967 | 62.915 | -0.14435 | 0.0021939 | 0.064281 | 0.068513 | 0.00046989 | -0.00056396 | -0.0046079 | 0.014984 | 0.0028754 | 0.064281 | 0.060934 | -0.0059132 | 0.0043836 | 0.00048713 | -0.27008 | 62.8693 | -60.0769 | 62.9333 | -59.7794 | -60.1776 | 0.009155 | -0.21973 | 62.8372 | -59.9854 | 63.0249 | -59.9579 | -60.0586 | -59.8709 | -0.10986 | -0.045776 | 0.018311 | 0.18768 | 59.9762 | -0.21057 | 60.0861 | -0.10071 | -0.018311 | -0.07782 | 0.10986 | 0.009155 | 0.09613 | -0.091553 | 0.11444 | -0.073242 | 0.29755 | 123.0103 | 0.027466 | 123.0103 | 122.9462 | 122.8226 | 122.8363 | 122.8043 | -122.9919 | -122.9004 | 122.9004 | 122.9919 | 59.697 | 59.7473
1001.8281 | 123.111 | -59.9304 | 62.9837 | -0.014649 | 0.0017667 | 0.061291 | 0.068086 | -0.0010253 | -0.0018458 | -0.00033547 | 0.014984 | 0.0018072 | 0.066418 | 0.063284 | -0.0046314 | 0.0033154 | -0.0039991 | -0.19684 | 62.9105 | -60.0494 | 62.9333 | -59.816 | -60.1364 | 0.082397 | -0.16479 | 62.9471 | -59.9716 | 62.9608 | -59.9716 | -60.0952 | -59.903 | -0.11902 | -0.073243 | -0.050354 | 0.11444 | 60.0128 | -0.20599 | 60.1318 | -0.086976 | -0.041199 | -0.036621 | -0.022889 | -0.041199 | 0.027466 | -0.1648 | 0.068665 | -0.1236 | 0.23346 | 122.9828 | 0 | 122.9324 | 122.9599 | 122.9187 | 122.8409 | 122.8775 | -123.0331 | -122.9553 | 122.8638 | 122.8912 | 59.7336 | 59.7656
1002.8281 | 123.1934 | -59.9304 | 62.9562 | -0.098572 | 0.0013393 | 0.063427 | 0.066804 | 0.00089729 | -0.00035036 | -0.0020443 | 0.039398 | 0.0024482 | 0.067486 | 0.060934 | -0.0059132 | 0.0031018 | -0.0020765 | -0.25635 | 62.9013 | -60.054 | 62.9333 | -59.8114 | -60.1547 | 0.059509 | -0.1831 | 62.851 | -59.9579 | 63.0478 | -59.9075 | -60.0128 | -59.8068 | -0.1236 | -0.054932 | -0.022888 | 0.11902 | 59.9899 | -0.2243 | 60.1135 | -0.10071 | -0.027466 | -0.10529 | 0.091553 | 0.022888 | 0.1236 | -0.082397 | 0.15106 | -0.054931 | 0.24262 | 122.9874 | 0.050354 | 123.0057 | 122.9553 | 122.8088 | 122.8317 | 122.7814 | -123.0103 | -122.9141 | 122.8638 | 122.9782 | 59.6741 | 59.7473
1003.8281 | 123.2071 | -59.9304 | 62.9425 | -0.1062 | 0.00091214 | 0.063213 | 0.067872 | 0.00046989 | -0.0024866 | -0.0035397 | 0.021088 | 0.0020208 | 0.066631 | 0.060293 | -0.0054858 | 0.003529 | -0.0054945 | -0.25177 | 62.8876 | -60.0586 | 62.97 | -59.7702 | -60.1273 | 0.086975 | -0.14191 | 62.883 | -59.967 | 63.0707 | -59.8755 | -59.9899 | -59.7931 | -0.12817 | -0.054932 | 0.027466 | 0.16022 | 60.0174 | -0.19684 | 60.1456 | -0.068664 | -0.036621 | -0.059509 | 0.12817 | 0.054932 | 0.13733 | -0.059509 | 0.17395 | -0.022888 | 0.28839 | 123.0286 | 0.091553 | 123.0377 | 122.9462 | 122.85 | 122.818 | 122.8134 | -123.0011 | -122.9095 | 122.9004 | 123.0011 | 59.6786 | 59.7885
1004.8281 | 123.1659 | -59.9075 | 62.9333 | -0.13672 | 0.00069854 | 0.062359 | 0.066591 | -0.0031617 | -0.00056396 | -0.0041807 | 0.018036 | -0.001397 | 0.065349 | 0.063925 | -0.0054858 | 0.0026746 | -0.0039991 | -0.29297 | 62.883 | -60.0494 | 62.9242 | -59.8389 | -60.1959 | 0 | -0.25177 | 62.851 | -59.9899 | 62.9608 | -59.9258 | -59.8984 | -59.7839 | -0.14191 | -0.050354 | -0.009156 | 0.068665 | 59.9075 | -0.28839 | 60.0494 | -0.14648 | -0.082397 | -0.082398 | 0.027465 | -0.01831 | 0.1236 | 0.009156 | 0.20599 | 0.091553 | 0.21057 | 122.9736 | 0.064087 | 122.9507 | 122.9324 | 122.8409 | 122.7905 | 122.7585 | -122.9828 | -122.9233 | 122.8317 | 122.8683 | 59.6146 | 59.6558
1005.8906 | 123.1796 | -59.9396 | 62.9333 | -0.12146 | 0.0024075 | 0.063641 | 0.068941 | -0.0025207 | 0.004563 | -0.0024717 | -0.0094299 | 0.0007392 | 0.064068 | 0.061361 | -0.006554 | 0.0043836 | -0.0033581 | -0.24719 | 62.8464 | -60.0952 | 62.8418 | -59.5505 | -60.0082 | -0.013733 | -0.24261 | 62.8647 | -59.9716 | 63.0432 | -59.9121 | -60.0449 | -59.8389 | -0.15564 | -0.086975 | -0.091553 | 0.3891 | 59.9258 | -0.068665 | 60.0815 | 0.086975 | -0.032044 | -0.068665 | 0.10986 | 0.027466 | 0.10071 | -0.10529 | 0.13275 | -0.073242 | 0.54474 | 122.937 | 0.05951 | 123.0148 | 122.9416 | 122.8363 | 122.7859 | 122.8043 | -123.0286 | -122.905 | 122.7814 | 122.9828 | 59.6924 | 59.697
1006.8281 | 123.1934 | -59.9075 | 62.9608 | -0.1062 | 0.0011257 | 0.062145 | 0.069795 | -0.0031617 | -0.00099116 | -0.0022581 | -0.0033265 | 9.8198e-05 | 0.064281 | 0.058584 | -0.004845 | 0.0026746 | 0.00091433 | -0.27466 | 62.9059 | -60.0723 | 62.9471 | -59.8068 | -60.1685 | 0.032043 | -0.21973 | 62.8876 | -59.9762 | 63.0341 | -59.935 | -60.0174 | -59.8206 | -0.16479 | -0.054931 | -0.013732 | 0.10071 | 59.9396 | -0.26092 | 60.1044 | -0.09613 | -0.068664 | -0.073242 | 0.073243 | -0.027466 | 0.086975 | -0.10986 | 0.15564 | -0.041199 | 0.2655 | 123.0194 | 0.041198 | 123.0103 | 122.9782 | 122.8638 | 122.8134 | 122.7951 | -123.0331 | -122.937 | 122.8546 | 122.9416 | 59.6329 | 59.6878
1007.8906 | 123.1384 | -59.9716 | 62.9425 | -0.060425 | 5.7742e-05 | 0.061932 | 0.070436 | 0.00068369 | -0.0033412 | -0.00097627 | -0.085724 | 0.0005256 | 0.064495 | 0.065847 | -0.0044178 | 0.0045972 | 0.00027333 | -0.33417 | 62.8693 | -60.1135 | 62.8601 | -59.9121 | -60.2554 | -0.091553 | -0.32501 | 62.8784 | -59.9991 | 62.9837 | -60.0082 | -60.1456 | -59.8984 | -0.14191 | -0.073242 | -0.082398 | 0.05951 | 59.8801 | -0.28381 | 60.022 | -0.14191 | -0.027465 | -0.064087 | 0.041199 | -0.036621 | 0.073243 | -0.17395 | 0.10071 | -0.14648 | 0.20142 | 122.9736 | -0.009156 | 122.9828 | 122.9828 | 122.8775 | 122.8409 | 122.85 | -123.056 | -122.9416 | 122.8317 | 122.9553 | 59.6375 | 59.6466
1008.8281 | 123.1522 | -59.9533 | 62.9379 | -0.11383 | 0.0017667 | 0.063427 | 0.0683 | -0.0010253 | -0.00035036 | -0.0020443 | -0.0094299 | 0.0003118 | 0.065563 | 0.064565 | -0.006554 | 0.0031018 | 0.00091433 | -0.3067 | 62.8372 | -60.0632 | 62.9242 | -59.8343 | -60.1776 | 0.004578 | -0.27008 | 62.8738 | -60.0082 | 63.0112 | -59.9487 | -60.054 | -59.8434 | -0.10986 | -0.10071 | -0.013733 | 0.11902 | 59.9579 | -0.2243 | 60.0677 | -0.11444 | -0.054932 | -0.064087 | 0.073242 | 0.004578 | 0.10986 | -0.10071 | 0.16479 | -0.045776 | 0.22888 | 122.9874 | 0.05951 | 123.0194 | 122.9004 | 122.8821 | 122.7905 | 122.8271 | -123.0011 | -122.9462 | 122.8775 | 122.9645 | 59.6466 | 59.6832
1009.8906 | 123.1796 | -59.9442 | 62.9013 | -0.15961 | -0.00015586 | 0.061718 | 0.068513 | -0.0020935 | -0.0035548 | -0.0014035 | -0.036896 | 9.8198e-05 | 0.065349 | 0.05837 | -0.004845 | 0.0031018 | 0.00048713 | -0.28839 | 62.8372 | -60.0677 | 62.9562 | -59.7977 | -60.1639 | 0.009155 | -0.21057 | 62.8555 | -59.9716 | 63.0341 | -59.935 | -60.0632 | -59.848 | -0.1236 | -0.064087 | 0.054932 | 0.14648 | 59.9533 | -0.21973 | 60.0769 | -0.09613 | -0.027466 | -0.045776 | 0.13275 | 0.009155 | 0.096131 | -0.11902 | 0.1236 | -0.091552 | 0.27008 | 123.024 | 0.036621 | 123.0057 | 122.905 | 122.8271 | 122.7814 | 122.7997 | -122.9691 | -122.8729 | 122.9004 | 122.9782 | 59.6558 | 59.7336
1010.8281 | 123.1522 | -59.9762 | 62.9242 | -0.12909 | 0.0017667 | 0.061504 | 0.067018 | 0.00089729 | 0.00029044 | -0.00033547 | -0.015534 | -0.0005426 | 0.065563 | 0.062643 | -0.0069812 | 0.0041698 | -0.0018629 | -0.27466 | 62.8784 | -60.0494 | 62.9608 | -59.7748 | -60.1776 | 0.009155 | -0.21515 | 62.8555 | -59.9945 | 63.0295 | -59.967 | -60.054 | -59.8526 | -0.073242 | -0.045776 | 0.036621 | 0.20142 | 59.9854 | -0.20142 | 60.0586 | -0.12817 | -0.018311 | -0.068664 | 0.10529 | 0.009155 | 0.1236 | -0.07782 | 0.14191 | -0.059509 | 0.27466 | 123.0103 | 0.027466 | 123.024 | 122.9279 | 122.85 | 122.8546 | 122.8317 | -122.9736 | -122.9187 | 122.937 | 123.0057 | 59.7015 | 59.761
1011.8906 | 123.2071 | -59.9304 | 62.9471 | -0.12146 | 0.0013393 | 0.060223 | 0.068727 | -0.0042297 | 7.6842e-05 | 9.193e-05 | 0.0088807 | 0.0009528 | 0.066845 | 0.056875 | -0.0054858 | 0.003529 | -0.00058107 | -0.2655 | 62.8922 | -60.0403 | 62.9379 | -59.816 | -60.1593 | 0.036621 | -0.20142 | 62.8784 | -59.9762 | 63.0478 | -59.9167 | -60.0128 | -59.8114 | -0.10986 | -0.054932 | -0.009156 | 0.11444 | 59.967 | -0.22888 | 60.0769 | -0.11902 | -0.045776 | -0.068665 | 0.10071 | 0.013733 | 0.11902 | -0.082397 | 0.1648 | -0.036621 | 0.2243 | 122.9782 | 0.059509 | 123.024 | 122.9324 | 122.8546 | 122.8226 | 122.8088 | -122.9874 | -122.9233 | 122.8683 | 122.9782 | 59.6649 | 59.729
1012.8281 | 123.2071 | -59.9304 | 62.9013 | -0.12146 | -0.00015586 | 0.063 | 0.067232 | -0.00081171 | -0.00056396 | -0.00033547 | -0.049103 | 0.0007392 | 0.068767 | 0.062856 | -0.0086902 | 0.0045972 | -0.0020765 | -0.27008 | 62.8647 | -60.0861 | 62.9654 | -59.7748 | -60.1639 | -0.009155 | -0.20142 | 62.851 | -59.967 | 63.0615 | -59.8846 | -60.0128 | -59.8389 | -0.15564 | -0.036621 | 0.064087 | 0.15564 | 59.9213 | -0.23346 | 60.0769 | -0.077819 | -0.036621 | -0.050354 | 0.16022 | 0.045776 | 0.091553 | -0.082397 | 0.12817 | -0.045776 | 0.31128 | 123.0515 | 0.082397 | 123.0286 | 122.9507 | 122.818 | 122.7951 | 122.7814 | -122.9874 | -122.8683 | 122.8958 | 122.9919 | 59.6603 | 59.729
1013.8906 | 123.1018 | -59.9579 | 62.9517 | -0.083313 | 0.00091214 | 0.062145 | 0.068086 | -0.00017091 | -0.0014184 | -0.00054907 | -0.094879 | 0.0041572 | 0.065349 | 0.061788 | -0.0054858 | 0.0041698 | -0.0022901 | -0.27008 | 62.8876 | -60.0815 | 62.8784 | -59.8663 | -60.2371 | -0.032043 | -0.29297 | 62.9105 | -59.9991 | 62.9654 | -60.0311 | -60.1456 | -59.9121 | -0.1236 | -0.064087 | -0.073242 | 0.091553 | 59.9258 | -0.27924 | 60.0494 | -0.15564 | -0.041198 | -0.041199 | 0.013733 | -0.073242 | 0.045777 | -0.18768 | 0.086975 | -0.14648 | 0.21515 | 122.9599 | -0.032044 | 122.9645 | 122.9691 | 122.9095 | 122.8455 | 122.8683 | -123.0331 | -122.9507 | 122.8363 | 122.9233 | 59.6878 | 59.6649
1014.8281 | 123.1659 | -59.9396 | 62.9013 | -0.083313 | 5.7742e-05 | 0.061932 | 0.068086 | 0.0013245 | -0.0018458 | -0.00054907 | -0.024689 | 0.0018072 | 0.067486 | 0.059866 | -0.0035632 | 0.0024608 | -0.00036747 | -0.29297 | 62.851 | -60.0677 | 62.9608 | -59.7748 | -60.1547 | -0.004578 | -0.2243 | 62.851 | -59.9991 | 63.0569 | -59.9396 | -60.054 | -59.8434 | -0.12817 | -0.050354 | 0.059509 | 0.16479 | 59.935 | -0.21515 | 60.0632 | -0.086975 | -0.059509 | -0.050354 | 0.15564 | 0 | 0.09613 | -0.11444 | 0.15564 | -0.054932 | 0.29297 | 123.0286 | 0.059509 | 123.056 | 122.9187 | 122.85 | 122.7905 | 122.7905 | -122.9691 | -122.9004 | 122.9004 | 122.9965 | 59.6466 | 59.7153
1015.8906 | 123.0972 | -59.9487 | 62.9654 | -0.11383 | 0.0013393 | 0.061718 | 0.068941 | 0.00025629 | -0.0035548 | 0.00094633 | -0.015534 | 0.0024482 | 0.064709 | 0.067343 | -0.0033496 | 0.0020336 | -0.0059217 | -0.19226 | 62.9105 | -60.0311 | 62.9333 | -59.8114 | -60.141 | 0.09613 | -0.20142 | 62.9196 | -59.9396 | 62.9837 | -59.9762 | -60.0815 | -59.8938 | -0.082398 | -0.054932 | -0.032043 | 0.13733 | 60.0449 | -0.19226 | 60.1273 | -0.10986 | 0.009155 | -0.045776 | 0.018311 | -0.027466 | 0.054931 | -0.13275 | 0.045776 | -0.14191 | 0.21973 | 122.9645 | -0.036621 | 122.9233 | 122.9416 | 122.8592 | 122.8592 | 122.8683 | -122.9965 | -122.905 | 122.8821 | 122.9324 | 59.7565 | 59.7473
1016.8438 | 123.0835 | -59.9487 | 62.9883 | -0.014649 | 0.0011257 | 0.061077 | 0.069581 | 0.0015381 | -0.0024866 | -0.00076267 | -0.094879 | 0.0024482 | 0.064709 | 0.059011 | -0.0052722 | 0.0045972 | 0.0019823 | -0.24719 | 62.9379 | -60.0723 | 62.9059 | -59.8709 | -60.2829 | 0.045776 | -0.21973 | 62.9196 | -59.9991 | 62.9745 | -59.9808 | -60.0998 | -59.9121 | -0.1236 | -0.050354 | -0.082397 | 0.077819 | 59.9945 | -0.33417 | 60.1181 | -0.21057 | -0.050354 | -0.068664 | -0.013733 | -0.032044 | 0.036621 | -0.15106 | 0.086975 | -0.10071 | 0.20142 | 122.9782 | 0.01831 | 122.9736 | 123.0103 | 122.9187 | 122.8867 | 122.8683 | -123.0606 | -122.9874 | 122.8546 | 122.9233 | 59.7015 | 59.729
1017.8906 | 123.1293 | -59.9808 | 62.9745 | -0.090943 | 0.0017667 | 0.062786 | 0.069154 | -0.00038451 | -0.0016322 | 0.00073273 | -0.085724 | 0.0020208 | 0.065136 | 0.063284 | -0.004845 | 0.0054516 | -0.0029309 | -0.27466 | 62.883 | -60.0952 | 62.8967 | -59.8572 | -60.2142 | -0.027466 | -0.26093 | 62.8967 | -59.9899 | 62.9654 | -60.0128 | -60.1456 | -59.8984 | -0.11444 | -0.091552 | -0.077819 | 0.1236 | 59.9533 | -0.23346 | 60.0677 | -0.11902 | -0.009155 | -0.077819 | -0.009155 | -0.032043 | 0.082398 | -0.1648 | 0.091553 | -0.15564 | 0.23804 | 122.9919 | -0.022888 | 122.9553 | 122.9782 | 122.8867 | 122.8638 | 122.8775 | -123.0698 | -122.9645 | 122.8775 | 122.9462 | 59.7061 | 59.7198
1018.8281 | 123.1201 | -59.9854 | 62.9379 | -0.090943 | 0.0019803 | 0.061504 | 0.069154 | 0.0036743 | -0.0018458 | 0.0020145 | -0.07962 | 0.0033026 | 0.068127 | 0.059439 | -0.0052722 | 0.0054516 | 0.0015551 | -0.32959 | 62.9196 | -60.0998 | 62.8464 | -59.9762 | -60.1227 | -0.054932 | -0.32501 | 62.9196 | -60.022 | 62.9654 | -60.0449 | -60.1547 | -59.9121 | -0.11444 | -0.01831 | -0.091552 | 0.009156 | 59.9304 | -0.13733 | 60.0449 | -0.022889 | -0.036621 | -0.01831 | 0.027466 | -0.059509 | 0.073243 | -0.16937 | 0.10986 | -0.13275 | 0.1236 | 122.9462 | -0.022888 | 122.9874 | 123.0194 | 122.9416 | 122.905 | 122.905 | -123.0377 | -122.9599 | 122.8317 | 122.9507 | 59.6558 | 59.6603
1019.8906 | 123.1064 | -59.935 | 62.9791 | -0.090943 | -0.00036966 | 0.062359 | 0.067659 | 0.00046989 | -0.0035548 | -0.00033547 | 0.0088807 | 0.0035162 | 0.065777 | 0.062429 | -0.0035632 | 0.0031018 | -0.0035719 | -0.19226 | 62.8967 | -60.0403 | 62.9517 | -59.7794 | -60.1273 | 0.09613 | -0.16022 | 62.915 | -59.967 | 62.9883 | -59.9854 | -60.0082 | -59.8251 | -0.10529 | -0.082397 | -0.027466 | 0.15564 | 60.0311 | -0.19226 | 60.1364 | -0.086975 | -0.032043 | -0.064087 | 0.009155 | -0.050354 | 0.10986 | -0.073242 | 0.14191 | -0.041199 | 0.26093 | 122.9919 | -0.018311 | 122.9553 | 122.937 | 122.8821 | 122.8317 | 122.85 | -123.0194 | -122.9462 | 122.8867 | 122.9233 | 59.7427 | 59.7748
1020.8281 | 123.1018 | -59.9899 | 62.9791 | -0.098572 | 0.00091214 | 0.061291 | 0.067232 | -0.00081171 | 0.0024268 | -0.0018307 | -0.018585 | 0.0037298 | 0.064922 | 0.062216 | -0.0071948 | 0.0039562 | 0.00091433 | -0.32959 | 62.8738 | -60.1273 | 62.8967 | -59.6512 | -60.3287 | -0.07782 | -0.38452 | 62.9242 | -60.0082 | 62.9562 | -60.054 | -60.1685 | -59.9258 | -0.13733 | -0.10529 | -0.082397 | 0.33874 | 59.9121 | -0.33875 | 60.0494 | -0.20142 | -0.018311 | -0.054932 | -0.022888 | -0.064087 | 0.064087 | -0.17853 | 0.082398 | -0.16022 | 0.47607 | 123.024 | -0.045776 | 122.9645 | 123.0011 | 122.9324 | 122.8638 | 122.9141 | -123.1064 | -122.9874 | 122.8867 | 122.9462 | 59.6603 | 59.6054
1021.8906 | 123.0972 | -59.9625 | 62.9471 | -0.045166 | 0.00069854 | 0.061291 | 0.067232 | -0.0025207 | -0.00013676 | -0.0016171 | -0.082672 | 0.0020208 | 0.064068 | 0.06542 | -0.0054858 | 0.0045972 | 0.0021961 | -0.24261 | 62.9013 | -60.0906 | 62.8967 | -59.8618 | -60.2142 | -0.018311 | -0.25635 | 62.9288 | -59.9991 | 62.9745 | -59.9945 | -60.1501 | -59.9167 | -0.12817 | -0.045777 | -0.050354 | 0.10071 | 59.9442 | -0.25177 | 60.0723 | -0.1236 | -0.036621 | -0.018311 | 0.027465 | -0.032044 | 0.045776 | -0.18768 | 0.082397 | -0.15106 | 0.22888 | 122.9874 | 0.004577 | 122.9736 | 122.9919 | 122.9279 | 122.8638 | 122.8912 | -123.0377 | -122.9462 | 122.8592 | 122.937 | 59.7198 | 59.7061
1022.8281 | 123.0652 | -59.9854 | 62.9471 | -0.068054 | 0.0032619 | 0.062572 | 0.070222 | -0.0025207 | -0.002273 | -0.00097627 | -0.088776 | 0.0009528 | 0.067913 | 0.063497 | -0.0052722 | 0.0043836 | -0.0018629 | -0.33417 | 62.9105 | -60.1135 | 62.8281 | -59.9625 | -60.2921 | -0.09613 | -0.37994 | 62.8784 | -60.022 | 62.9471 | -60.054 | -60.173 | -59.9304 | -0.12817 | -0.036622 | -0.11902 | 0.022889 | 59.8892 | -0.3067 | 60.0174 | -0.17853 | -0.036621 | -0.068665 | 0 | -0.068664 | 0.054932 | -0.18768 | 0.091553 | -0.15106 | 0.15106 | 122.9416 | -0.032043 | 122.9691 | 123.024 | 122.9004 | 122.8958 | 122.8638 | -123.0606 | -122.9691 | 122.8134 | 122.9324 | 59.6512 | 59.6054
1023.8906 | 123.1384 | -59.9579 | 62.9883 | 0.00824 | -0.00015586 | 0.062359 | 0.068513 | 0.0043151 | -0.00035036 | -0.0014035 | -0.015534 | 0.0024482 | 0.06599 | 0.059439 | -0.0067676 | 0.0028882 | 0.0026233 | -0.27466 | 62.9333 | -60.0723 | 62.8601 | -59.8755 | -60.1913 | 0.045776 | -0.2243 | 62.9196 | -59.9533 | 62.9837 | -59.967 | -60.0952 | -59.8846 | -0.11444 | -0.054931 | -0.12817 | 0.082398 | 60.0037 | -0.23346 | 60.1181 | -0.11902 | 0.004578 | -0.068664 | -0.004577 | -0.009155 | 0.073242 | -0.13733 | 0.068664 | -0.14191 | 0.19684 | 122.9324 | -0.013733 | 122.937 | 123.0057 | 122.8729 | 122.8912 | 122.8775 | -123.0606 | -122.9416 | 122.818 | 122.9416 | 59.6832 | 59.7336
1024.8281 | 123.0972 | -59.9625 | 62.9471 | -0.052796 | 0.0013393 | 0.063641 | 0.068941 | 0.0032471 | -0.00056396 | -0.0020443 | -0.082672 | 0.0033026 | 0.064495 | 0.062643 | -0.0033496 | 0.0050244 | -0.00015387 | -0.27924 | 62.9059 | -60.0815 | 62.8922 | -59.8801 | -60.2371 | -0.027466 | -0.28381 | 62.8967 | -59.9808 | 62.9608 | -60.0266 | -60.1547 | -59.9167 | -0.11902 | -0.041199 | -0.054932 | 0.082397 | 59.935 | -0.27466 | 60.054 | -0.15564 | -0.018311 | -0.050354 | 0.013732 | -0.064087 | 0.045776 | -0.19226 | 0.064087 | -0.17395 | 0.20142 | 122.9736 | -0.045776 | 122.9416 | 122.9874 | 122.8775 | 122.8683 | 122.8592 | -123.0286 | -122.9279 | 122.8546 | 122.9233 | 59.6832 | 59.6786
1025.8906 | 123.1476 | -59.9533 | 63.002 | -0.037537 | 0.00091214 | 0.060223 | 0.070649 | -0.00081171 | -0.0012048 | -0.0022581 | -0.039948 | 0.003089 | 0.065563 | 0.062429 | -0.004845 | 0.0037426 | 0.0015551 | -0.25177 | 62.9425 | -60.0449 | 62.8922 | -59.8618 | -60.2142 | 0.050354 | -0.23346 | 62.9471 | -59.9487 | 62.9883 | -59.9487 | -60.0632 | -59.8755 | -0.091553 | -0.059509 | -0.10986 | 0.091553 | 60.0037 | -0.26093 | 60.0952 | -0.16937 | 0.004578 | -0.054931 | -0.013733 | 0.004578 | 0.07782 | -0.10986 | 0.073242 | -0.11444 | 0.18311 | 122.937 | 0 | 122.937 | 122.9874 | 122.8958 | 122.8958 | 122.9004 | -123.0469 | -122.9507 | 122.8455 | 122.9416 | 59.7015 | 59.7198
1026.8438 | 123.1659 | -59.9625 | 62.9196 | -0.12146 | 0.0026211 | 0.063 | 0.066804 | 4.2692e-05 | -0.00077756 | -0.0011899 | 0.021088 | 0.0007392 | 0.070263 | 0.066061 | -0.004845 | 0.0026746 | -0.00079467 | -0.27924 | 62.8418 | -60.0403 | 62.9379 | -59.7748 | -60.1639 | 0.004578 | -0.21057 | 62.8098 | -59.9899 | 63.0386 | -59.9533 | -60.0449 | -59.8297 | -0.07782 | -0.07782 | 0.01831 | 0.18768 | 59.967 | -0.20142 | 60.0449 | -0.1236 | -0.027466 | -0.10986 | 0.11902 | 0.009155 | 0.13275 | -0.082398 | 0.16022 | -0.054932 | 0.2655 | 122.9782 | 0.036621 | 123.0286 | 122.8821 | 122.7997 | 122.8043 | 122.7722 | -122.9599 | -122.9095 | 122.9004 | 123.0011 | 59.6832 | 59.7519
1027.8906 | 123.2483 | -59.9167 | 62.9242 | -0.11383 | 0.0017667 | 0.062572 | 0.067018 | 0.00068369 | -0.0027002 | -0.0018307 | 0.024139 | 0.0018072 | 0.065349 | 0.054739 | -0.0063404 | 0.0026746 | -0.0033581 | -0.22888 | 62.8738 | -60.0494 | 62.9883 | -59.7198 | -60.0861 | 0.12817 | -0.10529 | 62.8693 | -59.9167 | 63.0798 | -59.848 | -59.935 | -59.761 | -0.13275 | -0.050354 | 0.064087 | 0.19684 | 60.0449 | -0.16937 | 60.1776 | -0.036622 | 0 | -0.054931 | 0.15564 | 0.068665 | 0.15564 | -0.018311 | 0.15564 | -0.018311 | 0.32959 | 123.0377 | 0.068665 | 122.9965 | 122.9233 | 122.7859 | 122.7905 | 122.7859 | -122.9736 | -122.8409 | 122.905 | 122.9965 | 59.6878 | 59.8114
1028.8281 | 90.2161 | -0.78278 | 62.4847 | 0.19897 | -0.0035739 | 0.060009 | 0.064454 | -0.0023071 | 0.013108 | -0.0063169 | -0.19864 | 0.13511 | 0.083294 | -0.23622 | -0.011681 | 0.10415 | 0.013732 | -0.27008 | 62.4619 | -0.76446 | 62.7914 | -60.4568 | -60.6308 | -0.086975 | -0.21515 | 62.3703 | -28.3905 | 64.0411 | -59.5093 | -31.105 | -61.235 | 0.018311 | -0.022888 | 0.3067 | -59.6741 | 0.6958 | -59.848 | 0.67749 | -59.8663 | -27.6077 | -0.11444 | 1.5564 | -58.7265 | -60.4523 | -30.3223 | -32.8445 | -2.7145 | -59.6924 | 63.5559 | -31.1188 | 92.4316 | 63.2263 | 90.7608 | 63.2446 | 63.1531 | -63.2492 | -90.8752 | 63.5742 | 64.8239 | 0.5127 | 0.56763
1029.8906 | 123.2162 | -59.816 | 62.9837 | -0.060425 | 0.0015529 | 0.062572 | 0.06595 | 0.0026063 | -0.0027002 | -0.0052487 | 0.097381 | 0.0009528 | 0.06599 | 0.060293 | -0.0050586 | 0.0082288 | 0.0011279 | -0.10529 | 62.9288 | -60.0174 | 62.8052 | -59.8206 | -60.1135 | 0.13733 | 0.73242 | 62.8235 | -59.9258 | 63.2172 | -59.6695 | -76.2772 | -59.5596 | -0.20142 | -0.054932 | -0.17853 | -0.004578 | 59.9533 | -0.29755 | 60.1547 | -0.09613 | -0.10986 | -0.16022 | 0.23346 | 0.14648 | 0.25635 | -16.4612 | 0.36621 | -16.3513 | 0.19684 | 122.8226 | 0.25635 | 123.143 | 122.9462 | 122.7493 | 122.7448 | 122.6395 | -123.0011 | -122.9095 | 122.6212 | 123.0331 | 59.7107 | 60.5484
1030.8281 | 123.1155 | -59.9304 | 62.9654 | -0.11383 | 0.0024075 | 0.062145 | 0.071077 | 0.0013245 | 0.00050424 | -0.0018307 | -0.039948 | -0.0011834 | 0.065563 | 0.064993 | -0.0059132 | 0.0039562 | -0.0022901 | -0.32044 | 62.9059 | -60.1135 | 62.8326 | -59.9442 | -60.3104 | -0.10071 | -0.30212 | 62.9196 | -59.9991 | 62.9562 | -60.0952 | -58.9508 | -59.9213 | -0.18311 | -0.059509 | -0.13275 | -0.013733 | 59.8297 | -0.37994 | 60.0128 | -0.19684 | -0.068664 | -0.045776 | -0.009155 | -0.1648 | 0.009155 | 0.97961 | 0.077819 | 1.0483 | 0.16937 | 122.9462 | -0.096131 | 122.9553 | 123.0194 | 122.9187 | 122.8363 | 122.85 | -123.0789 | -122.9645 | 122.7631 | 122.8867 | 59.61 | 59.6283
1031.8906 | 123.1476 | -59.9396 | 62.9837 | -0.022278 | 0.0036893 | 0.061718 | 0.068086 | -0.00059811 | -0.0033412 | -0.0011899 | 0.030243 | -0.0011834 | 0.065777 | 0.066061 | -0.0059132 | 0.0048108 | -0.0025037 | -0.20599 | 62.9288 | -60.054 | 62.9196 | -59.816 | -60.1685 | 0.082397 | -0.17395 | 62.9562 | -59.9808 | 62.9791 | -59.9899 | -60.0174 | -59.9075 | -0.11444 | -0.054932 | -0.064087 | 0.1236 | 60.022 | -0.22888 | 60.1364 | -0.11444 | -0.041199 | -0.027466 | -0.004578 | -0.050354 | 0.032043 | -0.07782 | 0.073242 | -0.036621 | 0.23804 | 122.9736 | -0.009155 | 122.9599 | 122.9828 | 122.937 | 122.8683 | 122.8958 | -123.0377 | -122.9645 | 122.8592 | 122.9187 | 59.7336 | 59.7656
1032.8281 | 123.1201 | -59.9579 | 62.9654 | -0.052796 | 0.0017667 | 0.064709 | 0.069368 | -0.00038451 | -0.0041956 | -0.0011899 | -0.042999 | -0.0009698 | 0.065777 | 0.05773 | -0.0029224 | 0.0060924 | 0.0019823 | -0.26093 | 62.8876 | -60.0906 | 62.9288 | -59.848 | -60.1868 | 0.004578 | -0.21515 | 62.9196 | -60.022 | 62.9791 | -60.022 | -60.0174 | -59.8846 | -0.13275 | -0.07782 | -0.036621 | 0.10986 | 59.9625 | -0.22888 | 60.0952 | -0.096131 | -0.064087 | -0.045776 | 0.013733 | -0.064087 | 0.073242 | -0.059509 | 0.13733 | 0.004578 | 0.24262 | 123.0194 | 0 | 123.0011 | 122.9782 | 122.9416 | 122.8455 | 122.8775 | -123.056 | -122.9874 | 122.8867 | 122.937 | 59.697 | 59.7427
1033.8906 | 123.1934 | -59.8938 | 62.9471 | -0.12909 | 0.00069854 | 0.062572 | 0.067232 | 0.0017517 | -0.00077756 | -0.0011899 | 0.027191 | -0.0011834 | 0.06599 | 0.055807 | -0.0063404 | 0.0058788 | -0.0020765 | -0.28381 | 62.8876 | -60.0632 | 62.9288 | -59.8297 | -60.1822 | -0.004578 | -0.28839 | 62.8922 | -60.0037 | 63.0386 | -59.8251 | -74.2996 | -59.5825 | -0.16937 | -0.05951 | -0.018311 | 0.064087 | 59.8892 | -0.28839 | 60.0586 | -0.11902 | -0.10986 | -0.054932 | 0.091552 | 0.068665 | 0.31128 | -14.4058 | 0.42114 | -14.296 | 0.23346 | 122.9919 | 0.17853 | 123.0423 | 122.9507 | 122.8958 | 122.7814 | 122.7859 | -123.0103 | -122.9507 | 122.8226 | 122.9324 | 59.61 | 59.6054
1034.8281 | 123.1384 | -59.9625 | 62.9654 | -0.060425 | 0.0013393 | 0.061504 | 0.069368 | 0.0011109 | 0.0013586 | -0.0022581 | -0.15286 | -0.0024652 | 0.064709 | 0.060293 | -0.004845 | 0.0056652 | -0.00036747 | -0.23804 | 62.9333 | -60.0998 | 62.9196 | -59.8206 | -60.1913 | -0.004578 | -0.1831 | 62.9196 | -59.9899 | 63.0066 | -59.9579 | -60.1318 | -59.816 | -0.13733 | -0.032043 | -0.045776 | 0.14191 | 59.9579 | -0.22888 | 60.0952 | -0.091553 | -0.027466 | -0.045776 | 0.041199 | 0.004577 | 0.14648 | -0.16937 | 0.17395 | -0.14191 | 0.27923 | 123.0194 | 0.032043 | 122.9965 | 123.0331 | 122.9095 | 122.8958 | 122.8821 | -123.0652 | -122.9553 | 122.8821 | 122.9691 | 59.7244 | 59.7794
1035.8281 | 123.1293 | -59.9899 | 62.9425 | -0.075684 | 0.0024075 | 0.065136 | 0.070009 | 0.0019653 | -0.0024866 | -0.0011899 | -0.039948 | -0.0009698 | 0.063427 | 0.057943 | -0.0059132 | 0.0041698 | 0.0013415 | -0.23804 | 62.915 | -60.0723 | 62.8967 | -59.8434 | -60.228 | 0.004578 | -0.16479 | 62.9288 | -59.9899 | 62.97 | -60.054 | -54.451 | -59.967 | -0.082398 | -0.027466 | -0.045776 | 0.14648 | 59.9945 | -0.23804 | 60.0769 | -0.15564 | 0 | -0.013733 | 0.027466 | -0.064087 | 0.022888 | 5.5389 | 0.022888 | 5.5389 | 0.22888 | 122.9691 | -0.064087 | 122.9599 | 122.9874 | 122.9187 | 122.905 | 122.9187 | -123.0148 | -122.9324 | 122.8867 | 122.9599 | 59.7519 | 59.8251
1036.8906 | 123.2071 | -59.9258 | 62.9791 | -0.083313 | -0.00036966 | 0.064709 | 0.066804 | 0.00025629 | -0.0041956 | 9.193e-05 | -0.027741 | -0.0024652 | 0.064922 | 0.054098 | -0.0044178 | 0.003529 | 0.0011279 | -0.1831 | 62.9059 | -60.0311 | 63.0844 | -60.0632 | -60.1685 | 0.16479 | 0.041199 | 62.8784 | -59.967 | 63.0569 | -59.8663 | -59.1385 | -59.816 | -0.10529 | -0.073242 | 0.10529 | -0.13733 | 60.0906 | -0.24261 | 60.1959 | -0.13733 | -0.041199 | -0.10071 | 0.07782 | 0.059509 | 0.10986 | 0.78735 | 0.15106 | 0.82855 | -0.032043 | 123.1155 | 0.10071 | 123.024 | 122.937 | 122.8455 | 122.8317 | 122.8043 | -123.0103 | -122.9462 | 123.0103 | 122.9828 | 59.7427 | 59.967
1037.8281 | 123.1018 | -59.967 | 62.9562 | -0.11383 | 0.0017667 | 0.063427 | 0.069795 | 0.0013245 | -0.00099116 | -0.0011899 | -0.067413 | 0.0011664 | 0.065777 | 0.067343 | -0.0063404 | 0.0058788 | -0.0048535 | -0.2655 | 62.8967 | -60.1181 | 62.9013 | -59.8709 | -60.228 | -0.018311 | -0.32501 | 62.8967 | -59.9716 | 62.9608 | -60.0266 | -60.26 | -59.8892 | -0.15106 | -0.059509 | -0.054932 | 0.09613 | 59.9487 | -0.26093 | 60.0998 | -0.10986 | -0.004578 | -0.059509 | 0.004577 | -0.059509 | 0.07782 | -0.29297 | 0.082398 | -0.28839 | 0.24719 | 123.0194 | -0.054931 | 122.9324 | 123.0148 | 122.8683 | 122.8638 | 122.8638 | -123.0743 | -122.9279 | 122.8683 | 122.9279 | 59.7015 | 59.642
1038.8906 | 123.0927 | -59.9258 | 62.9837 | 0.015869 | 0.0011257 | 0.062572 | 0.066591 | -0.0027343 | -0.0037684 | -0.00012167 | 0.033295 | 9.8198e-05 | 0.065136 | 0.061575 | -0.0052722 | 0.0037426 | -0.00036747 | -0.20599 | 62.9059 | -60.0311 | 62.9196 | -59.8206 | -60.1501 | 0.091553 | -0.60883 | 62.9379 | -59.9487 | 62.9745 | -59.9625 | -60.4935 | -59.8572 | -0.10529 | -0.07782 | -0.064087 | 0.10529 | 60.0174 | -0.2243 | 60.1227 | -0.11902 | -0.022888 | -0.045777 | -0.009156 | -0.036621 | 0.068664 | -0.56763 | 0.091552 | -0.54474 | 0.21057 | 122.9507 | -0.013733 | 122.9233 | 122.937 | 122.8867 | 122.8317 | 122.8638 | -123.0148 | -122.9324 | 122.8455 | 122.9004 | 59.7198 | 59.317
1039.8281 | 123.1338 | -59.9442 | 62.9883 | -0.045166 | 0.0021939 | 0.062145 | 0.070009 | 0.0036743 | -0.00077756 | -0.0024717 | -0.064362 | -0.0007562 | 0.064281 | 0.068197 | -0.0044178 | 0.0026746 | 0.00070073 | -0.22888 | 62.9013 | -60.0906 | 62.9196 | -59.816 | -60.173 | 0.054932 | -0.16479 | 62.915 | -59.9808 | 63.0157 | -59.9533 | -60.1181 | -59.8526 | -0.14648 | -0.086975 | -0.068664 | 0.12817 | 59.9991 | -0.22888 | 60.1456 | -0.082398 | -0.036621 | -0.073242 | 0.027466 | -0.009155 | 0.091553 | -0.17395 | 0.12817 | -0.13733 | 0.27466 | 123.0103 | 0.027466 | 122.9965 | 122.9919 | 122.8958 | 122.8455 | 122.8592 | -123.0789 | -122.9691 | 122.8638 | 122.9599 | 59.7153 | 59.7794
1040.8906 | 123.1796 | -59.935 | 62.9242 | -0.1062 | 0.00091214 | 0.063 | 0.067872 | -0.0029479 | -0.0012048 | -0.00076267 | 0.039398 | -0.0024652 | 0.065563 | 0.057943 | -0.0035632 | 0.0028882 | -0.0050671 | -0.29297 | 62.8693 | -60.0586 | 62.9288 | -59.7977 | -60.173 | -0.009155 | -0.10071 | 62.8555 | -60.0082 | 63.0157 | -59.9716 | -59.8709 | -59.8663 | -0.1236 | -0.054931 | 0.004578 | 0.13733 | 59.9258 | -0.23804 | 60.0494 | -0.11444 | -0.073242 | -0.068664 | 0.091553 | -0.036621 | 0.068665 | 0.064087 | 0.14191 | 0.13733 | 0.26093 | 122.9874 | 0.036621 | 123.024 | 122.9279 | 122.8638 | 122.8043 | 122.7905 | -122.9828 | -122.9324 | 122.8638 | 122.9507 | 59.642 | 59.8343
1041.8281 | 123.1247 | -59.9625 | 62.9791 | -0.090943 | 0.0015529 | 0.063213 | 0.069368 | -0.0010253 | -0.0014184 | 0.0018009 | -0.06131 | -0.0018244 | 0.065349 | 0.064993 | -0.0029224 | 0.0048108 | -0.0033581 | -0.25635 | 62.915 | -60.0861 | 62.9013 | -59.8526 | -60.2188 | -0.013733 | -0.23346 | 62.9013 | -60.0037 | 62.9745 | -60.0128 | -60.3287 | -59.8984 | -0.1236 | -0.064087 | -0.07782 | 0.10986 | 59.9487 | -0.25635 | 60.0723 | -0.13275 | -0.041199 | -0.07782 | -0.004578 | -0.050354 | 0.064087 | -0.36621 | 0.10529 | -0.32501 | 0.23346 | 122.9874 | -0.009155 | 122.9782 | 123.0011 | 122.905 | 122.8775 | 122.8638 | -123.0652 | -122.9828 | 122.8638 | 122.937 | 59.7061 | 59.729
1042.8906 | 123.1842 | -59.9487 | 62.9562 | -0.075684 | -0.00036966 | 0.063 | 0.066804 | 0.0021789 | -0.00099116 | -0.0054623 | 0.011932 | -0.0001154 | 0.065349 | 0.053457 | -0.0050586 | 0.0048108 | -0.0010083 | -0.27924 | 62.8876 | -60.0769 | 62.9562 | -59.6924 | -60.2325 | 0.022888 | -0.28381 | 62.8555 | -59.9762 | 63.0203 | -59.9396 | -59.8801 | -59.8343 | -0.12817 | -0.068665 | 0 | 0.25635 | 59.9716 | -0.28381 | 60.0998 | -0.15564 | -0.027466 | -0.10071 | 0.064087 | 0.009155 | 0.11444 | 0.068664 | 0.14191 | 0.09613 | 0.38452 | 123.0331 | 0.036621 | 122.9965 | 122.9645 | 122.8317 | 122.8363 | 122.8043 | -123.0331 | -122.9324 | 122.905 | 122.9691 | 59.6695 | 59.6649
1043.8281 | 123.111 | -59.9533 | 62.9745 | -0.090943 | 0.0028347 | 0.063641 | 0.071077 | 0.0021789 | -0.0029138 | 9.193e-05 | -0.067413 | -0.0016108 | 0.065349 | 0.062643 | -0.006554 | 0.003529 | -0.00079467 | -0.2655 | 62.8967 | -60.0723 | 62.8876 | -59.8892 | -60.2463 | 0.009155 | -0.32501 | 62.9196 | -60.0082 | 62.9379 | -60.0311 | -60.2463 | -59.9075 | -0.11902 | -0.077819 | -0.086975 | 0.064087 | 59.9625 | -0.29297 | 60.0815 | -0.17395 | -0.054932 | -0.054931 | -0.036621 | -0.07782 | 0.045776 | -0.29297 | 0.10071 | -0.23804 | 0.18311 | 122.9599 | -0.022888 | 122.9462 | 122.9691 | 122.9279 | 122.85 | 122.8729 | -123.0469 | -122.9828 | 122.8409 | 122.8912 | 59.6878 | 59.6283
1044.8906 | 123.2529 | -60.3699 | 62.4573 | -0.098572 | 0.0019803 | 0.063213 | 0.066591 | -0.00081171 | 0.00093144 | -0.0014035 | 0.057709 | -0.0005426 | 0.066845 | 0.057089 | -0.0037768 | 0.0043836 | 5.9726e-05 | -0.22888 | 62.4115 | -60.5164 | 62.4939 | -60.228 | -60.5804 | 61.8896 | -0.1236 | 62.4161 | -60.4294 | 62.5992 | -60.3195 | -60.4477 | -60.1913 | -0.14648 | -0.045776 | 0.036621 | 0.14191 | 122.2595 | -0.21057 | 122.406 | -0.064087 | -0.059509 | -0.041198 | 0.14191 | 0.050354 | 0.17853 | -0.07782 | 0.23804 | -0.018311 | 0.28839 | 123.0103 | 0.10986 | 123.0286 | 122.9279 | 122.8455 | 122.7814 | 122.7859 | -122.9736 | -122.8867 | 122.8638 | 122.9691 | 60.141 | 60.2463
1045.8281 | 124.2462 | -44.1376 | 62.471 | -0.28168 | 0.00048494 | 0.0583 | 0.070222 | -0.0014527 | -0.00013676 | -0.0054623 | -0.015534 | 0.019324 | 0.061077 | 0.062216 | -0.0056994 | 0.032154 | -0.0018629 | -0.21515 | 62.4527 | -52.4551 | 62.9242 | -59.8663 | -60.1959 | 62.9929 | 0.64545 | 62.5259 | -44.783 | 63.1165 | -60.2509 | -83.0338 | -61.1114 | -8.3176 | -0.01831 | 0.45319 | -15.7288 | 107.1304 | -16.0583 | 115.448 | -7.7408 | -0.64545 | 0.054932 | 0.64545 | -16.1133 | -16.9739 | -38.8962 | -16.3284 | -38.2507 | -7.4112 | 115.3793 | -15.4678 | 107.8995 | 114.9078 | 107.309 | 106.5903 | 106.6635 | -114.9261 | -107.254 | 107.0618 | 107.254 | 43.9224 | 44.783
1046.8281 | 123.143 | -60.3745 | 62.5351 | -0.045166 | 0.00048494 | 0.060863 | 0.067659 | -0.00081171 | -0.0027002 | -0.00097627 | 0.076019 | -0.0009698 | 0.067058 | 0.063925 | -0.0029224 | 0.0067334 | -0.0020765 | -0.26093 | 62.4802 | -60.4477 | 62.4115 | -60.347 | -60.4843 | 62.0728 | -0.16022 | 62.5031 | -60.4385 | 62.5214 | -60.5118 | -60.3195 | -60.4019 | -0.073242 | -0.054931 | -0.1236 | 0.027466 | 122.4472 | -0.10986 | 122.5204 | -0.036621 | -0.064087 | -0.032043 | -0.013733 | -0.13733 | -0.027466 | 0.054932 | 0.036621 | 0.11902 | 0.10071 | 122.8592 | -0.073242 | 122.9599 | 122.9279 | 122.9416 | 122.8546 | 122.8775 | -122.9828 | -122.9736 | 122.7859 | 122.8958 | 60.1135 | 60.2142
1047.8906 | 123.2529 | -60.1456 | 62.6312 | -0.098572 | 0.0024075 | 0.061718 | 0.069581 | 0.0036743 | -0.0012048 | 9.193e-05 | 0.039398 | 0.0005256 | 0.066631 | 0.057516 | -0.0059132 | 0.0063062 | -0.00079467 | -0.27924 | 62.4344 | -60.5804 | 62.4161 | -60.2371 | -60.5072 | 62.6038 | 3.6438 | 62.384 | -60.553 | 62.6862 | -60.1547 | -93.1778 | -59.7198 | -0.43487 | -0.19684 | -0.21515 | -0.091553 | 122.7493 | -0.36163 | 123.1842 | 0.073242 | -0.40741 | -0.24719 | 0.054931 | -0.009155 | 0.42572 | -33.0322 | 0.83313 | -32.6248 | 0.34332 | 122.9965 | 0.39825 | 123.2391 | 123.0148 | 122.937 | 122.58 | 122.5296 | -123.2117 | -123.1842 | 122.5616 | 122.8317 | 59.8663 | 63.7894
1048.8281 | 123.0927 | -60.4202 | 62.5122 | -0.045166 | 0.0011257 | 0.060863 | 0.067872 | 0.00068369 | -0.0027002 | -0.0016171 | 0.0058289 | -0.0033196 | 0.065349 | 0.06542 | -0.004845 | 0.0058788 | -0.00079467 | -0.32044 | 62.4802 | -60.5255 | 62.3474 | -60.3928 | -60.5896 | 62.146 | -0.39825 | 62.4573 | -60.4431 | 62.4939 | -60.466 | -60.8185 | -59.9258 | -0.10529 | -0.032043 | -0.16479 | 0.027466 | 122.5662 | -0.16937 | 122.6715 | -0.064087 | -0.022888 | -0.054932 | -0.018311 | -0.045776 | 0.49438 | -0.39825 | 0.51727 | -0.37537 | 0.13275 | 122.8729 | -0.022888 | 122.937 | 123.0057 | 122.9004 | 122.9004 | 122.8775 | -123.0377 | -122.9553 | 122.7676 | 122.9141 | 60.0998 | 60.022
1049.8906 | 123.2758 | -60.379 | 62.4664 | -0.075684 | 0.00048494 | 0.063427 | 0.067018 | -0.00017091 | -0.00056396 | -0.0037533 | 0.06076 | -0.0046014 | 0.066418 | 0.056875 | -0.0044178 | 0.0016064 | -0.0012219 | -0.2243 | 62.4207 | -60.5301 | 62.4893 | -60.2005 | -60.5713 | 62.645 | -0.082397 | 62.4115 | -60.4568 | 62.6038 | -60.3287 | -60.4431 | -60.228 | -0.15106 | -0.045777 | 0.022888 | 0.17853 | 123.024 | -0.19226 | 123.175 | -0.041199 | -0.07782 | -0.054932 | 0.13733 | 0.050354 | 0.15106 | -0.064087 | 0.22888 | 0.013733 | 0.32959 | 123.0194 | 0.12817 | 123.0606 | 122.9507 | 122.8683 | 122.7997 | 122.7905 | -122.9965 | -122.9233 | 122.8683 | 122.9828 | 60.1547 | 60.2966
1050.8281 | 123.2117 | -60.3882 | 62.5671 | 0.00824 | 0.00069854 | 0.061932 | 0.070222 | 0.0038879 | -0.0016322 | -0.0041807 | 0.033295 | -0.0007562 | 0.063854 | 0.066702 | -0.0037768 | 0.0058788 | 0.0015551 | -0.24719 | 62.4619 | -60.5759 | 62.4069 | -60.3241 | -60.6674 | 62.3978 | -0.1236 | 62.4847 | -60.5026 | 62.5122 | -60.4843 | -59.2072 | -60.3607 | -0.18768 | -0.10529 | -0.16022 | 0.064087 | 122.7859 | -0.27923 | 122.9736 | -0.091552 | -0.11444 | -0.082398 | -0.054932 | -0.09613 | 0.027466 | 1.181 | 0.14191 | 1.2955 | 0.25177 | 122.9828 | 0.018311 | 123.0148 | 123.0377 | 122.9874 | 122.85 | 122.8729 | -123.143 | -123.0698 | 122.7951 | 122.9004 | 60.141 | 60.2646
1051.8906 | 123.175 | -60.4202 | 62.4573 | -0.14435 | 0.0019803 | 0.061291 | 0.066163 | -0.0020935 | -0.0044092 | -0.0031125 | 0.033295 | -0.0026788 | 0.06364 | 0.061788 | -0.0054858 | 0.0031018 | -0.0018629 | -0.29755 | 62.3886 | -60.5392 | 62.4435 | -60.2875 | -60.6857 | 62.5351 | -0.27008 | 62.3886 | -60.4797 | 62.5351 | -60.434 | -60.5667 | -60.3287 | -0.11902 | -0.068664 | -0.013733 | 0.13275 | 122.9553 | -0.2655 | 123.0743 | -0.14648 | -0.059509 | -0.068664 | 0.07782 | -0.013733 | 0.091553 | -0.14648 | 0.15106 | -0.086975 | 0.25177 | 122.9828 | 0.045776 | 123.0148 | 122.9279 | 122.8683 | 122.8088 | 122.8088 | -122.9965 | -122.937 | 122.8638 | 122.9553 | 60.1227 | 60.1501
1052.8281 | 123.1979 | -60.4294 | 62.5122 | -0.17487 | -0.00058326 | 0.061718 | 0.067018 | 0.0011109 | -0.00013676 | -0.0033261 | 0.018036 | -0.0046014 | 0.064068 | 0.068838 | -0.0054858 | 0.0041698 | -0.0044263 | -0.14648 | 62.4023 | -60.5301 | 62.5214 | -60.1822 | -60.5576 | 62.6175 | -0.022888 | 62.4207 | -60.4248 | 62.5854 | -60.3699 | -60.3378 | -60.3378 | -0.10071 | -0.10986 | 0.009155 | 0.24719 | 123.0469 | -0.12817 | 123.1476 | -0.027466 | 0.004577 | -0.091553 | 0.073242 | 0.059509 | 0.091552 | 0.091552 | 0.086975 | 0.086975 | 0.3479 | 123.0515 | 0.054932 | 123.0103 | 122.9324 | 122.8455 | 122.8317 | 122.85 | -123.0423 | -122.937 | 122.9507 | 123.0148 | 60.2829 | 60.4065
1053.8906 | 123.2025 | -60.4065 | 62.4802 | -0.083313 | 0.00048494 | 0.062145 | 0.066163 | 0.0013245 | -0.00505 | -0.0020443 | 0.048553 | -0.0046014 | 0.064068 | 0.066488 | -0.0059132 | 0.0028882 | -0.0018629 | -0.2243 | 62.4207 | -60.5621 | 62.4893 | -60.2509 | -60.585 | 62.6038 | -0.14191 | 62.3932 | -60.4477 | 62.5854 | -60.3424 | -60.434 | -60.2692 | -0.15564 | -0.05951 | 0.009155 | 0.15564 | 123.0103 | -0.17853 | 123.1659 | -0.022888 | -0.041199 | -0.086976 | 0.10528 | 0.064087 | 0.13733 | -0.027466 | 0.17853 | 0.013733 | 0.31128 | 123.0515 | 0.10529 | 123.0331 | 122.9828 | 122.8409 | 122.8271 | 122.7997 | -123.0423 | -122.9279 | 122.8958 | 122.9919 | 60.1822 | 60.2646
1054.8281 | 123.1842 | -60.4111 | 62.5031 | -0.075684 | 0.00027134 | 0.061504 | 0.067659 | 0.0019653 | 0.00029044 | -0.0033261 | 0.0027771 | -0.0033196 | 0.064922 | 0.058157 | -0.0054858 | 0.0031018 | -0.0031445 | -0.16479 | 62.4069 | -60.5301 | 62.5031 | -60.2325 | -60.6079 | 62.6175 | -0.24261 | 62.439 | -60.434 | 62.5717 | -60.3928 | -60.3424 | -60.1639 | -0.11902 | -0.096131 | 0 | 0.17853 | 123.0286 | -0.19684 | 123.1476 | -0.07782 | -0.022888 | -0.064087 | 0.068664 | 0.018311 | 0.24719 | 0.068665 | 0.27008 | 0.091553 | 0.29755 | 123.0331 | 0.041199 | 123.0057 | 122.937 | 122.8729 | 122.818 | 122.85 | -123.0331 | -122.937 | 122.9141 | 122.9828 | 60.2463 | 60.1685
1055.8281 | 123.1247 | -60.4156 | 62.5305 | -0.007019 | 0.0013393 | 0.060863 | 0.069581 | -0.00081171 | -0.0020594 | -0.0016171 | -0.052155 | -0.0016108 | 0.065563 | 0.064779 | -0.0033496 | 0.0033154 | -0.0029309 | -0.2655 | 62.4664 | -60.553 | 62.4023 | -60.3516 | -60.6537 | 62.5031 | -0.23804 | 62.471 | -60.466 | 62.5168 | -60.4706 | -60.585 | -60.3561 | -0.13733 | -0.064087 | -0.12817 | 0.064087 | 122.9187 | -0.23804 | 123.056 | -0.10071 | -0.050354 | -0.05951 | -0.013733 | -0.054932 | 0.059509 | -0.16937 | 0.10986 | -0.11902 | 0.20142 | 122.9553 | -0.004578 | 122.9828 | 123.0194 | 122.937 | 122.8821 | 122.8867 | -123.0835 | -122.9965 | 122.818 | 122.9324 | 60.1501 | 60.1776
1056.8906 | 123.1979 | -60.4019 | 62.4756 | -0.083313 | -0.0031467 | 0.064281 | 0.066591 | 0.00089729 | 0.00029044 | 0.00030553 | -0.0063781 | -0.001397 | 0.066845 | 0.066702 | -0.006554 | 0.0043836 | -0.00015387 | -0.20599 | 62.471 | -60.498 | 62.5534 | -60.3195 | -60.7636 | 62.6129 | 0.66834 | 62.384 | -60.4935 | 62.5717 | -60.4248 | -60.1364 | -60.2829 | -0.09613 | -0.004578 | 0.07782 | 0.082398 | 123.0148 | -0.36163 | 123.111 | -0.2655 | -0.091552 | -0.091553 | 0.09613 | -0.022888 | 0.11902 | 0.2655 | 0.21057 | 0.35705 | 0.17853 | 123.0515 | 0.068664 | 123.0652 | 122.9691 | 122.8775 | 122.8729 | 122.7859 | -122.9736 | -122.9691 | 122.9553 | 122.9736 | 60.1959 | 61.0703
1057.8281 | 123.1338 | -60.4477 | 62.5259 | -0.037537 | 0.0019803 | 0.061077 | 0.069154 | -0.0014527 | -0.00099116 | -0.0033261 | -0.049103 | -0.001397 | 0.06599 | 0.058584 | -0.0050586 | 0.0056652 | 0.0019823 | -0.24719 | 62.4664 | -60.5667 | 62.4115 | -60.3378 | -60.6812 | 62.5076 | 0.13275 | 62.5259 | -60.4248 | 62.4939 | -60.4431 | -60.9787 | -60.3516 | -0.11902 | -0.059509 | -0.11444 | 0.10986 | 122.9553 | -0.23346 | 123.0743 | -0.11444 | 0.022888 | 0 | -0.032044 | 0.004578 | 0.096131 | -0.53101 | 0.073243 | -0.55389 | 0.22888 | 122.9782 | -0.01831 | 122.9187 | 123.0331 | 122.9507 | 122.9141 | 122.9736 | -123.0927 | -122.9507 | 122.8592 | 122.9416 | 60.2005 | 60.5804
1058.8906 | 123.2346 | -60.3928 | 62.471 | -0.075684 | 0.0017667 | 0.06065 | 0.068086 | -0.00059811 | 0.00050424 | -0.0014035 | 0.021088 | -0.0028924 | 0.065777 | 0.054312 | -0.0050586 | 0.0037426 | -0.0018629 | -0.23804 | 62.4252 | -60.5392 | 62.4939 | -60.2417 | -60.5942 | 62.5946 | -0.14648 | 62.4023 | -60.4568 | 62.5946 | -60.3607 | -60.3058 | -60.2646 | -0.14648 | -0.045776 | 0.022888 | 0.15106 | 122.9874 | -0.20142 | 123.1338 | -0.054931 | -0.064087 | -0.068664 | 0.1236 | 0.032043 | 0.12817 | 0.086975 | 0.19226 | 0.15106 | 0.29755 | 123.0331 | 0.09613 | 123.0515 | 122.9645 | 122.8592 | 122.818 | 122.7951 | -123.0103 | -122.9279 | 122.8867 | 122.9874 | 60.1547 | 60.2463
1059.8281 | 123.1247 | -60.4248 | 62.5076 | -0.075684 | 0.0017667 | 0.062145 | 0.069581 | -0.00017091 | -0.003982 | -0.0011899 | -0.018585 | -0.0022516 | 0.066845 | 0.068197 | -0.004845 | 0.0039562 | -0.0033581 | -0.23804 | 62.439 | -60.553 | 62.4527 | -60.3607 | -60.6903 | 62.5305 | -0.53101 | 62.4664 | -60.4568 | 62.5305 | -60.4156 | -63.0844 | -60.0723 | -0.12817 | -0.068664 | -0.054931 | 0.064087 | 122.9553 | -0.2655 | 123.0835 | -0.13733 | -0.032043 | -0.041198 | 0.022889 | 0.009156 | 0.35248 | -2.6596 | 0.38452 | -2.6276 | 0.19226 | 123.0057 | 0.041199 | 122.9874 | 122.9919 | 122.9233 | 122.8638 | 122.8912 | -123.0606 | -122.9645 | 122.8775 | 122.9553 | 60.1868 | 59.8938
1060.8906 | 123.2025 | -60.3745 | 62.471 | -0.083313 | 0.0013393 | 0.063641 | 0.067872 | 0.0011109 | -0.0016322 | -0.0020443 | 0.0088807 | -0.0022516 | 0.064922 | 0.059011 | -0.0061268 | 0.0043836 | -0.0029309 | -0.29297 | 62.3428 | -60.5576 | 62.4527 | -60.2829 | -60.672 | 62.5259 | -0.30212 | 62.384 | -60.4523 | 62.5168 | -60.4614 | -60.3699 | -60.2921 | -0.1831 | -0.12817 | -0.01831 | 0.091553 | 122.9004 | -0.29755 | 123.0835 | -0.11444 | -0.07782 | -0.086975 | 0.045777 | -0.086975 | 0.082398 | 0.004578 | 0.16022 | 0.082398 | 0.27466 | 123.0103 | -0.009155 | 122.9691 | 122.9004 | 122.8363 | 122.7173 | 122.7585 | -123.0286 | -122.9233 | 122.8271 | 122.8912 | 60.0815 | 60.0723
1061.8281 | 123.1064 | -60.4065 | 62.5214 | 0.023498 | 0.0030483 | 0.061932 | 0.070009 | -0.00059811 | -0.0044092 | 0.00073273 | -0.052155 | -0.001397 | 0.06834 | 0.069906 | -0.0067676 | 0.0056652 | 5.9726e-05 | -0.29755 | 62.471 | -60.5988 | 62.4161 | -60.3424 | -60.6766 | 62.5214 | -0.26093 | 62.4893 | -60.4614 | 62.5214 | -60.4706 | -60.5118 | -60.3745 | -0.19226 | -0.050354 | -0.10529 | 0.064087 | 122.9279 | -0.27008 | 123.1201 | -0.07782 | -0.054932 | -0.032043 | 0 | -0.064087 | 0.032043 | -0.10529 | 0.086975 | -0.050354 | 0.25635 | 123.0148 | -0.009155 | 122.9828 | 123.0698 | 122.9507 | 122.8775 | 122.8958 | -123.1201 | -122.9828 | 122.8226 | 122.9279 | 60.1089 | 60.1456
1062.8906 | 123.2071 | -60.4431 | 62.4207 | -0.075684 | 0.0036893 | 0.063427 | 0.068086 | -0.0018799 | -0.0020594 | -0.0024717 | -0.036896 | -0.0005426 | 0.068127 | 0.064138 | -0.0063404 | 0.0065198 | -0.0010083 | -0.21973 | 62.4207 | -60.498 | 62.439 | -60.2325 | -60.6766 | 62.5946 | 0.032043 | 62.3749 | -60.4752 | 62.5626 | -60.3928 | -64.3478 | -60.0632 | -0.054932 | 0 | 0.018311 | 0.21057 | 123.0377 | -0.23346 | 123.0927 | -0.17853 | -0.032044 | -0.045776 | 0.14191 | 0.050354 | 0.37994 | -3.9047 | 0.41199 | -3.8727 | 0.2655 | 122.937 | 0.082398 | 123.0377 | 122.9187 | 122.85 | 122.8638 | 122.818 | -122.9187 | -122.8958 | 122.8821 | 123.0057 | 60.2234 | 60.4752
1063.8281 | 123.1476 | -60.3973 | 62.5031 | -0.068054 | 5.7742e-05 | 0.06065 | 0.068086 | -0.00017091 | -0.0033412 | -0.0037533 | 0.045502 | -0.0016108 | 0.063854 | 0.05837 | -0.0052722 | 0.0031018 | -0.00079467 | -0.21515 | 62.4573 | -60.5072 | 62.4435 | -60.2875 | -60.6445 | 62.558 | 0.24261 | 62.4573 | -60.466 | 62.471 | -60.5026 | -55.4947 | -60.5347 | -0.10986 | -0.045777 | -0.05951 | 0.10986 | 122.9553 | -0.24719 | 123.0652 | -0.13733 | -0.068664 | -0.045777 | -0.032044 | -0.10529 | -0.13733 | 4.9026 | -0.068665 | 4.9713 | 0.21973 | 122.9507 | -0.036622 | 122.937 | 122.9645 | 122.9233 | 122.8546 | 122.8546 | -123.0103 | -122.9691 | 122.8409 | 122.8683 | 60.1822 | 60.64
1064.8281 | 123.2895 | -60.3516 | 62.4847 | -0.098572 | 0.00091214 | 0.060223 | 0.067445 | -0.0020935 | -0.0031274 | -0.0020443 | 0.085174 | -0.0033196 | 0.06599 | 0.057516 | -0.0054858 | 0.003529 | -0.00015387 | -0.26093 | 62.439 | -60.553 | 62.4893 | -60.2554 | -60.6079 | 62.5763 | 0.086975 | 62.4023 | -60.4202 | 62.5992 | -60.3928 | -59.642 | -60.3928 | -0.20142 | -0.045776 | 0.004578 | 0.09613 | 122.9279 | -0.25635 | 123.1293 | -0.054931 | -0.068665 | -0.082397 | 0.11444 | -0.041199 | -0.041199 | 0.70953 | 0.027466 | 0.7782 | 0.29755 | 123.0423 | 0.027466 | 123.0194 | 122.9919 | 122.8226 | 122.7905 | 122.7539 | -123.0377 | -122.905 | 122.8409 | 122.9507 | 60.0906 | 60.4385
1065.8906 | 123.1522 | -60.4294 | 62.4847 | -0.045166 | 0.0015529 | 0.06065 | 0.070436 | 0.0036743 | 0.0013586 | 9.193e-05 | -0.012482 | 0.0005256 | 0.067058 | 0.059866 | -0.0039906 | 0.0050244 | 5.9726e-05 | -0.33417 | 62.4252 | -60.585 | 62.3474 | -60.4111 | -60.7681 | 62.4298 | -0.23804 | 62.4115 | -60.5164 | 62.4664 | -60.466 | -60.1364 | -60.4294 | -0.15564 | -0.059509 | -0.13733 | 0.01831 | 122.8592 | -0.33875 | 123.0148 | -0.1831 | -0.086975 | -0.073242 | -0.01831 | -0.036621 | 0 | 0.29297 | 0.086975 | 0.37994 | 0.17395 | 122.9324 | 0.050354 | 122.9828 | 123.0103 | 122.9279 | 122.8546 | 122.8409 | -123.0698 | -123.0011 | 122.7768 | 122.8958 | 60.0952 | 60.1913
1066.8281 | 123.2574 | -60.3607 | 62.4664 | -0.075684 | 0.0026211 | 0.062145 | 0.067872 | -0.0042297 | -0.0012048 | -0.00076267 | 0.054657 | -0.0016108 | 0.065777 | 0.06072 | -0.0059132 | 0.0043836 | 0.00091433 | -0.21973 | 62.4344 | -60.5072 | 62.4939 | -60.2371 | -60.5759 | 62.6129 | -0.33417 | 62.4069 | -60.434 | 62.6358 | -60.3241 | -60.7681 | -60.1501 | -0.14648 | -0.032044 | 0.027465 | 0.1236 | 122.9736 | -0.21515 | 123.1201 | -0.068665 | -0.073242 | -0.05951 | 0.16937 | 0.036621 | 0.21057 | -0.40741 | 0.28381 | -0.33417 | 0.27008 | 123.0011 | 0.10986 | 123.0698 | 122.9416 | 122.8409 | 122.7951 | 122.7676 | -122.9736 | -122.9004 | 122.8546 | 122.9965 | 60.141 | 60.0266
1067.8906 | 123.1979 | -60.4156 | 62.4252 | -0.075684 | 0.0013393 | 0.062145 | 0.067659 | 0.0013245 | -0.0037684 | -0.0028989 | -0.030792 | -0.002038 | 0.065777 | 0.063497 | -0.0046314 | 0.0063062 | 0.0013415 | -0.33417 | 62.384 | -60.585 | 62.4069 | -60.347 | -60.7086 | 62.4893 | -0.28381 | 62.3932 | -60.4752 | 62.5534 | -60.4431 | -60.7269 | -60.2554 | -0.16937 | -0.041199 | -0.018311 | 0.068664 | 122.905 | -0.29297 | 123.0743 | -0.1236 | -0.05951 | -0.032044 | 0.12817 | -0.027466 | 0.16022 | -0.31128 | 0.21973 | -0.25177 | 0.23804 | 122.9919 | 0.032044 | 123.0286 | 122.9691 | 122.8683 | 122.7997 | 122.8088 | -123.0103 | -122.9004 | 122.8226 | 122.9691 | 60.0815 | 60.1318
1068.8281 | 123.2483 | -60.4019 | 62.4527 | -0.12909 | 0.00048494 | 0.059795 | 0.067232 | -0.00017091 | -0.002273 | -0.0011899 | 0.057709 | -0.0028924 | 0.065563 | 0.063711 | -0.0067676 | 0.0041698 | 0.0032641 | -0.25635 | 62.4069 | -60.5347 | 62.4985 | -60.2509 | -60.6125 | 62.59 | -0.050354 | 62.384 | -60.4523 | 62.5946 | -60.3653 | -60.8643 | -60.2646 | -0.13275 | -0.045777 | 0.045776 | 0.15106 | 122.9919 | -0.21057 | 123.1247 | -0.07782 | -0.050354 | -0.068665 | 0.14191 | 0.036622 | 0.13733 | -0.46234 | 0.18768 | -0.41199 | 0.28381 | 123.0331 | 0.086976 | 123.0469 | 122.9416 | 122.8363 | 122.8088 | 122.7859 | -122.9874 | -122.905 | 122.9004 | 122.9965 | 60.1456 | 60.3516
1069.8906 | 123.1201 | -60.4156 | 62.4939 | -0.2359 | -0.0044285 | 0.06065 | 0.066377 | 0.0013245 | -0.0018458 | -0.0014035 | -0.030792 | -0.0005426 | 0.065136 | 0.069479 | -0.0033496 | 0.0043836 | -0.0039991 | -0.28381 | 62.4161 | -60.5804 | 62.4023 | -60.3653 | -60.7361 | 62.3932 | -0.49896 | 62.439 | -60.4797 | 62.4573 | -60.5484 | -60.7086 | -60.4431 | -0.16479 | -0.077819 | -0.091552 | 0.050354 | 122.8088 | -0.32043 | 122.9736 | -0.15564 | -0.064087 | -0.054931 | -0.036621 | -0.13275 | -0.027466 | -0.29297 | 0.036621 | -0.22888 | 0.21515 | 122.9828 | -0.068665 | 122.937 | 122.9965 | 122.9187 | 122.8317 | 122.8546 | -123.0743 | -122.9736 | 122.818 | 122.8729 | 60.1318 | 59.9167
1070.8281 | 123.262 | -60.3378 | 62.5168 | -0.083313 | 0.0011257 | 0.060863 | 0.066804 | -0.00081171 | 7.6842e-05 | -0.0035397 | 0.072967 | -0.0039606 | 0.068127 | 0.055807 | -0.0046314 | 0.0048108 | -0.0031445 | -0.24261 | 62.4023 | -60.5301 | 62.4802 | -60.2417 | -60.5667 | 62.6129 | -0.17853 | 62.4069 | -60.4156 | 62.5992 | -60.2966 | -68.4082 | -60.1318 | -0.19226 | -0.11444 | -0.036621 | 0.096131 | 122.9507 | -0.22888 | 123.143 | -0.036621 | -0.077819 | -0.10986 | 0.082397 | 0.041199 | 0.20599 | -8.0704 | 0.28381 | -7.9926 | 0.28839 | 123.0103 | 0.11902 | 123.0148 | 122.9324 | 122.8226 | 122.7402 | 122.7448 | -123.0469 | -122.9324 | 122.818 | 122.937 | 60.0952 | 60.1593
1071.8906 | 123.111 | -60.4202 | 62.4985 | -0.25116 | -0.0040013 | 0.063854 | 0.071077 | 0.0017517 | -0.0018458 | -0.00054907 | -0.042999 | -0.002038 | 0.068127 | 0.068411 | -0.0039906 | 0.0060924 | -0.0057081 | -0.29755 | 62.3703 | -60.5942 | 62.3703 | -60.4202 | -60.7681 | 62.4298 | -0.59052 | 62.4298 | -60.4889 | 62.4435 | -60.5484 | -60.8459 | -60.434 | -0.17395 | -0.12817 | -0.12817 | 0 | 122.85 | -0.3479 | 123.024 | -0.17395 | -0.068665 | -0.068664 | -0.054932 | -0.12817 | -0.013733 | -0.42572 | 0.054932 | -0.35706 | 0.17395 | 122.9645 | -0.059509 | 122.9324 | 122.9645 | 122.9187 | 122.7905 | 122.85 | -123.0927 | -122.9874 | 122.7905 | 122.8638 | 60.1227 | 59.8297
1072.8281 | 123.1934 | -60.3928 | 62.4619 | -0.060425 | 0.00069854 | 0.063427 | 0.064241 | 0.0045289 | -0.0012048 | 0.00030553 | 0.051605 | 0.0005256 | 0.067913 | 0.060293 | -0.0054858 | 0.0037426 | 0.0017687 | -0.30212 | 62.4023 | -60.5347 | 62.3978 | -60.347 | -60.6583 | 62.6358 | -0.53101 | 62.439 | -60.4477 | 62.5992 | -60.3973 | -62.6953 | -59.8709 | -0.14191 | -0.059509 | -0.064087 | 0.045776 | 123.0286 | -0.2655 | 123.1705 | -0.1236 | -0.054932 | -0.022888 | 0.13733 | -0.004578 | 0.52185 | -2.3026 | 0.57678 | -2.2476 | 0.18768 | 122.9324 | 0.050354 | 123.0469 | 122.937 | 122.8867 | 122.7951 | 122.8317 | -122.9965 | -122.9095 | 122.7905 | 122.9919 | 60.0906 | 59.8618
1073.8906 | 123.1338 | -60.4248 | 62.4527 | -0.022278 | 0.0011257 | 0.063 | 0.070436 | 0.0023925 | -0.0018458 | -0.00012167 | -0.042999 | -0.0016108 | 0.065777 | 0.067556 | -0.0046314 | 0.0039562 | 0.00070073 | -0.31586 | 62.4023 | -60.5759 | 62.3749 | -60.4294 | -60.7407 | 62.4573 | -0.28839 | 62.4161 | -60.5026 | 62.4802 | -60.5255 | -60.5209 | -60.3928 | -0.15106 | -0.050354 | -0.07782 | -0.004577 | 122.8821 | -0.31586 | 123.0331 | -0.16479 | -0.07782 | -0.036621 | 0.027466 | -0.10071 | 0.032044 | -0.09613 | 0.10986 | -0.01831 | 0.14649 | 122.9507 | -0.022888 | 122.9828 | 122.9782 | 122.9187 | 122.8271 | 122.8409 | -123.0286 | -122.9553 | 122.7997 | 122.905 | 60.1089 | 60.1364
1074.8281 | 123.2025 | -60.4202 | 62.4573 | -0.068054 | 0.00027134 | 0.062572 | 0.067232 | -0.00017091 | -0.0029138 | 0.0020145 | 0.036346 | -0.0018244 | 0.067272 | 0.064993 | -0.0035632 | 0.0039562 | 0.0011279 | -0.32044 | 62.3795 | -60.5392 | 62.4161 | -60.3104 | -60.6537 | 62.5259 | -0.3479 | 62.4069 | -60.466 | 62.5259 | -60.4477 | -60.3561 | -60.3699 | -0.11902 | -0.077819 | -0.041198 | 0.10986 | 122.9462 | -0.23346 | 123.0652 | -0.11444 | -0.045776 | -0.050354 | 0.068665 | -0.027466 | 0.050354 | 0.064087 | 0.09613 | 0.10986 | 0.22888 | 122.9553 | 0.01831 | 122.9919 | 122.9187 | 122.8729 | 122.7997 | 122.8271 | -122.9965 | -122.9233 | 122.8363 | 122.9462 | 60.0998 | 60.0723
1075.8906 | 123.1567 | -61.8118 | 61.0931 | -0.060425 | 0.00048494 | 0.060863 | 0.069368 | -0.0018799 | -0.0024866 | 0.0018009 | -0.070465 | 0.10221 | 0.069836 | 0.001974 | 0.061378 | 0.10778 | -0.00015387 | -0.25635 | 61.0519 | -61.972 | 61.0199 | -61.7249 | -62.0773 | 61.1114 | 0.3067 | 61.0474 | -61.8576 | -61.7935 | 61.1755 | 60.9741 | 0.16479 | -0.16022 | -0.041199 | -0.073243 | 0.086975 | 122.9233 | -0.2655 | 123.0835 | -0.10529 | -0.045776 | -0.045777 | -122.8867 | 122.9874 | 61.9766 | 122.7859 | 62.0224 | 122.8317 | 0.24719 | 122.9919 | 123.0331 | 0.064087 | 123.024 | 122.905 | 122.8638 | 122.8592 | -123.0652 | -122.9507 | 122.8317 | 0.018311 | 61.5555 | 62.1185
1076.8281 | 123.1842 | -61.8256 | 61.0474 | -0.12909 | 0.00091214 | 0.062572 | 0.068513 | -0.00038451 | -0.00056396 | -0.0016171 | -0.015534 | 0.102 | 0.069622 | -0.0027258 | 0.061165 | 0.10521 | 0.0011279 | -0.32501 | 60.9695 | -61.9858 | 61.0107 | -61.702 | -62.0682 | 61.1114 | 0.31128 | 60.9695 | -61.8851 | -61.8073 | 61.1755 | 60.9833 | 0.082397 | -0.16022 | -0.07782 | -0.036621 | 0.1236 | 122.937 | -0.24261 | 123.0972 | -0.082397 | -0.059509 | -0.07782 | -122.8546 | 123.0011 | 61.908 | 122.8088 | 61.9675 | 122.8683 | 0.28381 | 122.9965 | 123.0606 | 0.07782 | 122.9553 | 122.8546 | 122.7951 | 122.7951 | -123.0331 | -122.9324 | 122.8363 | 0.018311 | 61.5005 | 62.1368
1077.8281 | 123.2208 | -61.8347 | 61.0565 | -0.060425 | 0.0021939 | 0.062786 | 0.068941 | 0.00046989 | -0.00056396 | -0.0033261 | -0.012482 | 0.10071 | 0.068767 | -0.0022986 | 0.061805 | 0.10521 | 0.0013415 | -0.28839 | 61.0016 | -61.972 | 61.0428 | -61.6608 | -62.027 | 61.1618 | 0.42114 | 60.9741 | -61.8576 | -61.7569 | 61.2213 | 61.0382 | 0.14191 | -0.13733 | -0.054932 | -0.013733 | 0.17395 | 122.9965 | -0.19226 | 123.1338 | -0.054932 | -0.022888 | -0.082398 | -122.8134 | 123.056 | 61.9766 | 122.8729 | 61.9995 | 122.8958 | 0.31128 | 123.0148 | 123.0789 | 0.10071 | 122.9736 | 122.8317 | 122.8363 | 122.8088 | -123.0286 | -122.9141 | 122.8775 | 0.07782 | 61.5463 | 62.2559
1078.8906 | 123.1338 | -61.8484 | 61.0703 | -0.098572 | 0.0015529 | 0.062572 | 0.069368 | -0.010639 | -0.0014184 | -0.0056759 | -0.088776 | 0.097724 | 0.067486 | -0.0012304 | 0.061165 | 0.10799 | -0.0014355 | -0.25635 | 60.9787 | -61.9675 | 61.0199 | -61.6974 | -62.1002 | 60.9421 | 0.38452 | 60.997 | -61.8622 | -61.7935 | 61.1572 | 60.9604 | 0.073242 | -0.11902 | -0.091552 | -0.050354 | 0.15106 | 122.7905 | -0.25177 | 122.9095 | -0.13275 | -0.013733 | -0.073242 | -122.8638 | 123.0057 | 61.9217 | 122.8088 | 61.9354 | 122.8226 | 0.27008 | 122.9874 | 123.0194 | 0.068665 | 122.9462 | 122.8592 | 122.8271 | 122.8455 | -123.0377 | -122.9324 | 122.8683 | 0.054932 | 61.5921 | 62.233
1079.8281 | 123.1476 | -61.821 | 61.0565 | -0.11383 | -0.00079686 | 0.061291 | 0.0683 | -0.0012391 | -0.0024866 | -0.0022581 | 0.0027771 | 0.099647 | 0.069408 | -0.0076392 | 0.063301 | 0.10564 | -0.0039991 | -0.32501 | 60.965 | -61.9492 | 61.0245 | -61.6974 | -62.0636 | 61.1023 | 0.34332 | 60.965 | -61.8439 | -61.8073 | 61.1526 | 61.0107 | 0.027466 | -0.12817 | -0.091553 | -0.032044 | 0.1236 | 122.9233 | -0.24262 | 123.0515 | -0.11444 | -0.022888 | -0.091553 | -122.8638 | 122.9736 | 61.8484 | 122.8317 | 61.8713 | 122.8546 | 0.25177 | 122.9736 | 122.9965 | 0.036621 | 122.9141 | 122.8088 | 122.7859 | 122.7859 | -123.0057 | -122.9004 | 122.8455 | 0.013733 | 61.496 | 62.1643
1080.8906 | 123.1476 | -61.8347 | 61.0565 | -0.060425 | 0.0019803 | 0.062786 | 0.069154 | 0.0017517 | -0.00099116 | 0.00051913 | -0.1254 | 0.099433 | 0.06599 | -0.0022986 | 0.060737 | 0.10778 | -0.0012219 | -0.21973 | 61.0428 | -61.9537 | 61.0107 | -61.6745 | -62.0087 | 61.1023 | 0.4303 | 61.0016 | -61.8347 | -61.7844 | 61.1801 | 60.9787 | 0.1236 | -0.11902 | -0.013733 | -0.045777 | 0.16022 | 122.937 | -0.17395 | 123.056 | -0.054932 | 0 | -0.054932 | -122.8409 | 123.0148 | 61.9583 | 122.8134 | 61.9583 | 122.8134 | 0.27923 | 122.9645 | 123.0148 | 0.050354 | 122.9965 | 122.8363 | 122.8775 | 122.8363 | -123.0103 | -122.8912 | 122.8455 | 0.050354 | 61.615 | 62.265
1081.8281 | 123.1338 | -61.8393 | 61.0107 | -0.16724 | 0.0015529 | 0.061718 | 0.067872 | -0.0016663 | -0.0031274 | -0.0022581 | -0.039948 | 0.10157 | 0.066845 | -0.0052892 | 0.060737 | 0.10735 | 0.0011279 | -0.31128 | 60.9375 | -61.9675 | 61.0153 | -61.6882 | -62.0773 | 61.116 | 0.33417 | 60.9467 | -61.853 | -61.7935 | 61.171 | 61.0016 | 0.032043 | -0.12817 | -0.073242 | 0.004578 | 0.15106 | 122.9553 | -0.23804 | 123.0835 | -0.10986 | -0.013733 | -0.064087 | -122.8043 | 123.0103 | 61.8713 | 122.8409 | 61.8851 | 122.8546 | 0.27924 | 122.9828 | 123.024 | 0.059509 | 122.905 | 122.7997 | 122.7768 | 122.7859 | -122.9782 | -122.8638 | 122.8546 | 0.045776 | 61.528 | 62.1735
1082.8906 | 123.1018 | -61.8668 | 61.084 | -0.022278 | 0.0021939 | 0.060436 | 0.066591 | -0.0010253 | -0.0052638 | -0.0022581 | -0.064362 | 0.10071 | 0.065777 | 0.0056056 | 0.063301 | 0.10756 | 0.00091433 | -0.2655 | 61.0199 | -61.9583 | 60.965 | -61.7386 | -62.0728 | 61.0931 | 0.50354 | 61.0611 | -61.8027 | -61.8759 | 61.1664 | 60.9421 | 0.064087 | -0.091553 | -0.064087 | -0.11902 | 0.12817 | 122.9599 | -0.20599 | 123.0515 | -0.11444 | 0.064087 | -0.022888 | -122.9599 | 123.0331 | 61.9308 | 122.8088 | 61.8668 | 122.7448 | 0.21973 | 122.9233 | 122.9691 | -0.073243 | 122.9782 | 122.8638 | 122.8867 | 122.9279 | -123.0423 | -122.8867 | 122.8317 | -0.009156 | 61.6013 | 62.3703
1083.8281 | 123.1338 | -61.8164 | 61.0382 | -0.12909 | 0.0011257 | 0.062359 | 0.070009 | 0.00089729 | -0.0037684 | -0.0011899 | -0.036896 | 0.10093 | 0.067486 | -0.0061438 | 0.061165 | 0.10692 | 0.00027333 | -0.32044 | 60.965 | -61.9492 | 60.997 | -61.7065 | -62.0636 | 61.116 | 0.33417 | 60.9741 | -61.8668 | -61.7935 | 61.1801 | 61.0153 | 0.018311 | -0.13275 | -0.073242 | -0.041199 | 0.10986 | 122.9324 | -0.24719 | 123.0652 | -0.11444 | -0.050354 | -0.064087 | -122.8317 | 122.9965 | 61.8347 | 122.8317 | 61.8851 | 122.8821 | 0.24261 | 122.9462 | 123.0469 | 0.073242 | 122.9141 | 122.8409 | 122.7814 | 122.7905 | -122.9874 | -122.905 | 122.8134 | 0.022888 | 61.496 | 62.1506
1084.8281 | 123.1705 | -61.8118 | 61.0016 | -0.12909 | 0.00027134 | 0.060436 | 0.067018 | -0.00017091 | -0.0035548 | -0.0031125 | -0.076569 | 0.099433 | 0.067699 | -0.0010168 | 0.061805 | 0.10628 | -0.00015387 | -0.29297 | 60.9512 | -61.9492 | 61.0245 | -61.6379 | -61.9537 | 61.1252 | 0.3891 | 60.9375 | -61.8576 | -61.7569 | 61.1984 | 61.0245 | 0.045776 | -0.13733 | -0.050354 | 0.022888 | 0.17395 | 122.937 | -0.14191 | 123.0743 | -0.004577 | -0.045776 | -0.064087 | -122.7585 | 123.0103 | 61.8576 | 122.8363 | 61.9034 | 122.8821 | 0.31128 | 122.9736 | 123.056 | 0.10071 | 122.9004 | 122.7951 | 122.7631 | 122.7493 | -122.9507 | -122.8592 | 122.8363 | 0.054932 | 61.5189 | 62.2009
1085.8906 | 123.056 | -61.8576 | 61.0611 | -0.098572 | 0.0015529 | 0.063427 | 0.068727 | 0.0017517 | -0.0016322 | 9.193e-05 | -0.14371 | 0.096656 | 0.067486 | -0.0089208 | 0.060737 | 0.10329 | -0.0031445 | -0.2655 | 60.9695 | -61.9629 | 61.0153 | -61.7249 | -62.0728 | 61.0748 | 0.36621 | 60.9924 | -61.8622 | -61.8301 | 61.1435 | 60.9375 | 0.041199 | -0.10529 | -0.091553 | -0.045776 | 0.13275 | 122.9324 | -0.21515 | 123.0377 | -0.10986 | -0.004578 | -0.068664 | -122.8912 | 123.0011 | 61.8988 | 122.7951 | 61.9034 | 122.7997 | 0.23804 | 122.9782 | 123.0057 | 0.032044 | 122.9324 | 122.8546 | 122.8271 | 122.85 | -123.024 | -122.9233 | 122.8729 | 0.027466 | 61.5921 | 62.2238
1086.8281 | 123.0789 | -61.8439 | 61.0336 | -0.083313 | 0.00048494 | 0.061291 | 0.069795 | 0.0041015 | -0.0033412 | -0.00012167 | -0.1315 | 0.10285 | 0.069408 | -0.0025122 | 0.062019 | 0.10692 | -0.0022901 | -0.34332 | 60.9879 | -61.972 | 60.9192 | -61.8118 | -62.1552 | 61.0199 | -0.036621 | 60.9375 | -61.9034 | -61.8668 | 61.1069 | 60.9329 | -0.022888 | -0.12817 | -0.045776 | -0.11444 | 0.032043 | 122.8638 | -0.31128 | 122.9919 | -0.1831 | -0.059509 | -0.09613 | -122.9004 | 122.9507 | 61.821 | 122.7768 | 61.8805 | 122.8363 | 0.16022 | 122.8912 | 123.0103 | 0.036621 | 122.9599 | 122.8409 | 122.8317 | 122.7814 | -123.0057 | -122.937 | 122.7631 | -0.022888 | 61.5005 | 61.8073
1087.8906 | 123.0789 | -61.8347 | 61.0153 | -0.083313 | 0.0013393 | 0.062786 | 0.068513 | -0.0016663 | -0.0012048 | -0.00012167 | -0.12234 | 0.10136 | 0.067058 | -0.0022986 | 0.061805 | 0.10372 | 0.0013415 | -0.23804 | 60.9787 | -61.9583 | 61.0062 | -61.7065 | -62.0773 | 61.0794 | 0.35706 | 60.9787 | -61.853 | -61.821 | 61.1435 | 60.9421 | 0.045776 | -0.1236 | -0.036621 | -0.009155 | 0.12817 | 122.9141 | -0.24262 | 123.0377 | -0.11902 | -0.01831 | -0.036621 | -122.8363 | 122.9782 | 61.8805 | 122.7768 | 61.8988 | 122.7951 | 0.25177 | 122.9645 | 122.9965 | 0.032043 | 122.937 | 122.8317 | 122.8134 | 122.8134 | -122.9736 | -122.8683 | 122.8409 | 0.013733 | 61.5967 | 62.1918
1088.8281 | 123.0835 | -61.8622 | 61.0245 | -0.045166 | 0.0011257 | 0.06065 | 0.070222 | 0.0023925 | -0.0027002 | -0.00054907 | -0.10403 | 0.102 | 0.067058 | 5.1352e-05 | 0.06031 | 0.10671 | 0.00027333 | -0.35248 | 60.9512 | -61.9858 | 60.9283 | -61.7706 | -62.1368 | 61.0291 | 0.26093 | 60.9558 | -61.8851 | -61.8256 | 61.1343 | 60.9329 | -0.027466 | -0.1236 | -0.073242 | -0.09613 | 0.091553 | 122.8912 | -0.27466 | 123.0148 | -0.15106 | -0.022888 | -0.068664 | -122.85 | 122.9965 | 61.8347 | 122.7951 | 61.8576 | 122.818 | 0.21515 | 122.9141 | 123.0194 | 0.059509 | 122.937 | 122.8409 | 122.8134 | 122.818 | -123.0103 | -122.9095 | 122.7905 | 0.036621 | 61.5097 | 62.1231
1089.8906 | 123.1201 | -61.8256 | 61.0519 | -0.098572 | 0.0017667 | 0.063427 | 0.069368 | 0.0053833 | 0.00093144 | -0.0031125 | -0.097931 | 0.10114 | 0.069836 | -0.003153 | 0.062233 | 0.10863 | 0.0028369 | -0.22888 | 61.0062 | -61.972 | 61.0291 | -61.6745 | -62.0316 | 61.1114 | 0.3891 | 60.997 | -61.8484 | -61.7844 | 61.1893 | 60.997 | 0.10071 | -0.14648 | -0.045776 | -0.022888 | 0.15106 | 122.937 | -0.20599 | 123.0835 | -0.059509 | -0.022888 | -0.054932 | -122.8363 | 123.0148 | 61.9263 | 122.8226 | 61.9492 | 122.8455 | 0.29755 | 123.0011 | 123.0377 | 0.064087 | 122.9782 | 122.8455 | 122.8317 | 122.8226 | -123.024 | -122.9004 | 122.8546 | 0.041199 | 61.5967 | 62.2147
1090.8281 | 123.024 | -61.8668 | 61.0474 | -0.11383 | 0.0011257 | 0.061291 | 0.067872 | 0.0041015 | -0.0033412 | -0.00054907 | -0.1376 | 0.10114 | 0.06834 | -0.00037605 | 0.060951 | 0.10927 | 0.0019823 | -0.34332 | 60.9695 | -61.9995 | 60.8963 | -61.7889 | -62.1643 | 61.0107 | 0.20142 | 60.9787 | -61.9171 | -61.9171 | 60.8368 | 61.1755 | 0.15106 | -0.13275 | -0.07782 | -0.15106 | 0.07782 | 122.8775 | -0.29755 | 123.0103 | -0.16479 | -0.050354 | -0.068664 | -122.9645 | 122.7036 | 62.0178 | 123.0423 | 62.0682 | 123.0927 | 0.21057 | 122.8958 | 122.7539 | 0 | 122.9691 | 122.8958 | 122.8363 | 122.8455 | -123.0469 | -122.9645 | 122.7631 | -0.050354 | 61.5234 | 62.0682
1091.8906 | 123.0972 | -61.8164 | 61.0428 | -0.083313 | 0.00027134 | 0.062786 | 0.067659 | 0.0032471 | -0.0029138 | -0.0011899 | -0.082672 | 0.10114 | 0.066845 | 0.0015466 | 0.059456 | 0.10885 | 0.00091433 | -0.23804 | 61.0153 | -61.9492 | 61.0062 | -61.6745 | -62.0316 | 61.0977 | 0.39825 | 60.9879 | -61.8439 | -61.7661 | 61.171 | 60.9833 | 0.09613 | -0.13275 | -0.027466 | -0.036621 | 0.14191 | 122.9141 | -0.21515 | 123.0469 | -0.082397 | -0.027466 | -0.054932 | -122.8088 | 122.9874 | 61.9125 | 122.7997 | 61.94 | 122.8271 | 0.27466 | 122.9553 | 123.0148 | 0.07782 | 122.9645 | 122.8317 | 122.8317 | 122.8043 | -122.9919 | -122.8867 | 122.8226 | 0.050354 | 61.5784 | 62.2147
1092.8281 | 123.0698 | -61.8576 | 61.0016 | -0.090943 | 0.0011257 | 0.062572 | 0.069795 | -0.00059811 | 7.6842e-05 | -0.00012167 | -0.076569 | 0.10136 | 0.066845 | -0.0025122 | 0.062019 | 0.10628 | -0.00058107 | -0.33417 | 61.0107 | -61.972 | 60.91 | -61.7706 | -62.1368 | 61.0336 | 0.22888 | 60.965 | -61.8668 | -61.8393 | 61.1023 | 60.9146 | -0.036621 | -0.11444 | 0.009155 | -0.091553 | 0.086975 | 122.8912 | -0.27924 | 123.0057 | -0.16479 | -0.009155 | -0.036621 | -122.8409 | 122.9599 | 61.821 | 122.7722 | 61.8301 | 122.7814 | 0.20142 | 122.8821 | 122.9691 | 0.027466 | 122.9828 | 122.8317 | 122.8683 | 122.8226 | -122.9736 | -122.8683 | 122.7676 | 0.018311 | 61.5234 | 62.0865
1093.8906 | 123.111 | -61.8027 | 61.0291 | -0.052796 | -0.0018649 | 0.062145 | 0.068941 | 0.0026063 | -0.0012048 | -0.0024717 | -0.10403 | 0.10242 | 0.070049 | -0.001444 | 0.061592 | 0.1082 | -0.0044263 | -0.26093 | 60.9833 | -61.94 | 60.9924 | -61.6333 | -62.2513 | 61.084 | 0.38452 | 60.997 | -61.8439 | -61.7935 | 61.1526 | 60.9604 | 0.068665 | -0.13733 | -0.045777 | -0.036621 | 0.16937 | 122.8867 | -0.44861 | 123.024 | -0.31128 | -0.041199 | -0.032044 | -122.8226 | 122.9553 | 61.8713 | 122.7631 | 61.9125 | 122.8043 | 0.3067 | 122.9324 | 122.9965 | 0.050354 | 122.9233 | 122.8409 | 122.7859 | 122.7997 | -122.9691 | -122.8729 | 122.7951 | 0.009155 | 61.5417 | 62.1872
1094.8281 | 123.0835 | -61.8301 | 61.0428 | -0.083313 | 0.0011257 | 0.062786 | 0.064454 | 0.0045289 | -0.0035548 | -0.00054907 | -0.097931 | 0.10178 | 0.066418 | -0.001444 | 0.060524 | 0.10756 | 0.0030505 | -0.26093 | 60.997 | -61.9583 | 61.0245 | -61.7065 | -62.0316 | 61.0886 | 0.36621 | 60.9741 | -61.8301 | -61.8118 | 61.1526 | 60.9604 | 0.073242 | -0.12817 | -0.045777 | -0.018311 | 0.1236 | 122.9187 | -0.20142 | 123.0469 | -0.073242 | 0 | -0.068665 | -122.8546 | 122.9828 | 61.9034 | 122.7905 | 61.9034 | 122.7905 | 0.25177 | 122.9828 | 122.9828 | 0.01831 | 122.9553 | 122.8043 | 122.8271 | 122.8043 | -123.0011 | -122.8729 | 122.8546 | 0.01831 | 61.5692 | 62.1964
1095.8906 | 123.0743 | -61.8393 | 61.0657 | -0.045166 | 0.00069854 | 0.061718 | 0.067872 | -0.0010253 | -0.0041956 | -0.0022581 | -0.055206 | 0.099006 | 0.067699 | 0.00069215 | 0.061165 | 0.10778 | -0.0014355 | -0.28381 | 61.0428 | -61.9354 | 60.9604 | -61.7157 | -62.0773 | 61.084 | 0.35248 | 61.0016 | -61.8393 | -61.7798 | 61.3632 | 60.7544 | -0.036621 | -0.096131 | -0.022888 | -0.10529 | 0.1236 | 122.9233 | -0.23804 | 123.0194 | -0.14191 | 0 | -0.064087 | -122.8455 | 123.2025 | 61.8027 | 122.5937 | 61.8027 | 122.5937 | 0.21973 | 122.8958 | 123.2025 | 0.059509 | 122.9782 | 122.8409 | 122.8821 | 122.8409 | -123.0011 | -122.905 | 122.7997 | 0.059509 | 61.5555 | 62.1918
1096.8281 | 123.056 | -61.8484 | 61.0565 | -0.1062 | 0.0024075 | 0.063641 | 0.068941 | -0.00081171 | 0.0024268 | -0.0016171 | -0.097931 | 0.1005 | 0.066631 | 0.001974 | 0.059242 | 0.10778 | -0.0025037 | -0.27466 | 60.9833 | -61.9675 | 60.9833 | -61.7615 | -62.1643 | 61.1114 | 0.3891 | 60.9604 | -61.8256 | -61.8118 | 61.1481 | 60.9695 | 0.059509 | -0.11902 | -0.073243 | -0.073243 | 0.086975 | 122.9599 | -0.31586 | 123.0789 | -0.19684 | 0.022888 | -0.096131 | -122.8683 | 122.9965 | 61.908 | 122.818 | 61.8851 | 122.7951 | 0.20599 | 122.9507 | 122.9736 | 0.013733 | 122.9507 | 122.7859 | 122.8317 | 122.8088 | -123.024 | -122.8821 | 122.8317 | 0.036621 | 61.5738 | 62.2375
1097.8906 | 123.0698 | -61.7935 | 61.116 | -0.060425 | -0.00079686 | 0.06065 | 0.068513 | 0.00089729 | -0.0014184 | -0.0024717 | -0.036896 | 0.1005 | 0.067058 | -0.0069982 | 0.061378 | 0.10564 | 5.9726e-05 | -0.27924 | 61.0153 | -61.8942 | 60.9467 | -61.6928 | -62.0499 | 61.0794 | 0.32959 | 61.0199 | -61.8347 | -61.8347 | 61.1389 | 60.9833 | 0.29755 | -0.10071 | -0.10071 | -0.16937 | 0.10071 | 122.8729 | -0.25635 | 122.9736 | -0.15564 | -0.041199 | -0.096131 | -122.9507 | 122.9324 | 62.0911 | 122.7768 | 62.1323 | 122.818 | 0.20142 | 122.8409 | 122.9736 | 0 | 122.9095 | 122.8546 | 122.8088 | 122.8134 | -123.0103 | -122.9507 | 122.7402 | -0.041199 | 61.5143 | 62.1231
1098.8281 | 123.0743 | -61.8256 | 61.0611 | -0.090943 | 0.0030483 | 0.063854 | 0.069154 | 0.0017517 | -0.0037684 | -0.0011899 | -0.07962 | 0.10029 | 0.070263 | -0.0029394 | 0.061165 | 0.10842 | -0.0039991 | -0.23346 | 61.0062 | -61.9354 | 60.9924 | -61.6837 | -62.0224 | 61.0886 | 0.39368 | 60.9787 | -61.8347 | -61.7889 | 61.171 | 61.0016 | 0.10529 | -0.10986 | -0.054931 | -0.068664 | 0.14191 | 122.9141 | -0.19684 | 123.024 | -0.086975 | -0.009155 | -0.082397 | -122.85 | 122.9965 | 61.9308 | 122.8271 | 61.94 | 122.8363 | 0.25177 | 122.9279 | 123.0057 | 0.045777 | 122.9416 | 122.8134 | 122.8317 | 122.8043 | -122.9965 | -122.8958 | 122.818 | 0.036622 | 61.5921 | 62.2192
1099.8281 | 123.0606 | -61.821 | 61.0565 | -0.052796 | 0.0028347 | 0.061718 | 0.068727 | 0.0049561 | -0.0027002 | 0.00073273 | -0.094879 | 0.102 | 0.066204 | -0.002085 | 0.061378 | 0.10842 | 0.00048713 | -0.26093 | 60.9879 | -61.9492 | 60.9787 | -61.6974 | -62.0682 | 61.0565 | 0.31586 | 60.965 | -61.8347 | -61.8256 | 61.116 | 60.9329 | 0.032043 | -0.12817 | -0.068665 | -0.07782 | 0.1236 | 122.8775 | -0.24719 | 123.0057 | -0.11902 | -0.013733 | -0.091553 | -122.8821 | 122.937 | 61.853 | 122.7539 | 61.8668 | 122.7676 | 0.25177 | 122.9279 | 122.9507 | 0.009155 | 122.937 | 122.7997 | 122.8088 | 122.7859 | -123.0057 | -122.8912 | 122.7997 | -0.004578 | 61.5601 | 62.1368
1100.8906 | 123.1796 | -61.7889 | 61.0245 | -0.075684 | 0.0047573 | 0.063 | 0.066377 | 0.0019653 | 0.001145 | 0.0020145 | -0.10403 | 0.10029 | 0.067272 | -0.0025122 | 0.060951 | 0.10585 | 0.00027333 | -0.20142 | 60.965 | -61.9034 | 61.0657 | -61.6333 | -61.4868 | 61.2579 | 0.55389 | 60.9421 | -61.8164 | -61.7157 | 61.2579 | 61.0703 | 0.17395 | -0.11444 | -0.059509 | 0.041199 | 0.15564 | 123.0469 | 0.30212 | 123.1613 | 0.41657 | -0.027466 | -0.082397 | -122.7402 | 123.0469 | 61.9629 | 122.8592 | 61.9904 | 122.8867 | 0.27008 | 122.9691 | 123.0743 | 0.10071 | 122.8683 | 122.7585 | 122.7539 | 122.731 | -122.9279 | -122.8409 | 122.8546 | 0.073242 | 61.5875 | 62.3428
1101.8281 | 123.0835 | -61.8347 | 61.0519 | -0.075684 | 0.0021939 | 0.062572 | 0.068727 | -0.00017091 | -0.0041956 | -0.0031125 | -0.094879 | 0.10071 | 0.066845 | 0.0026148 | 0.062233 | 0.10778 | -0.0054945 | -0.24719 | 60.9787 | -61.9675 | 61.0107 | -61.6653 | -62.0407 | 61.0703 | 0.37079 | 60.9924 | -61.8301 | -61.7889 | 61.1572 | 60.9833 | 0.09613 | -0.13275 | -0.073242 | -0.041199 | 0.16937 | 122.905 | -0.20599 | 123.0377 | -0.073242 | 0.004578 | -0.059509 | -122.8409 | 122.9919 | 61.9308 | 122.818 | 61.9263 | 122.8134 | 0.30212 | 122.9782 | 122.9874 | 0.041199 | 122.9462 | 122.8226 | 122.8134 | 122.8271 | -123.0194 | -122.8821 | 122.8455 | 0.045777 | 61.5875 | 62.2055
1102.8906 | 123.0148 | -61.7981 | 61.0931 | -0.098572 | -0.00015586 | 0.060863 | 0.0683 | -0.00038451 | -0.00077756 | -0.0033261 | -0.055206 | 0.10093 | 0.067486 | -0.002085 | 0.061805 | 0.10543 | 0.00027333 | -0.26093 | 61.0107 | -61.9446 | 60.9512 | -61.6974 | -62.059 | 61.0886 | 0.34332 | 61.0016 | -61.8118 | -61.8347 | 61.1435 | 60.9375 | 0.09613 | -0.14648 | -0.082398 | -0.14191 | 0.10071 | 122.8867 | -0.26093 | 123.0331 | -0.11444 | -0.013733 | -0.091553 | -122.9279 | 122.9416 | 61.8942 | 122.7356 | 61.908 | 122.7493 | 0.24719 | 122.8958 | 122.9553 | -0.022888 | 122.9553 | 122.8134 | 122.8088 | 122.7997 | -123.0377 | -122.905 | 122.7493 | -0.036621 | 61.5372 | 62.1414
1103.8281 | 123.0011 | -61.8576 | 61.0474 | -0.068054 | 0.0032619 | 0.062145 | 0.067445 | 4.2692e-05 | 0.00029044 | 0.00051913 | -0.091827 | 0.1005 | 0.067699 | -0.0029394 | 0.061378 | 0.10671 | -0.00036747 | -0.31128 | 60.9787 | -61.972 | 60.9283 | -61.8118 | -62.1414 | 60.997 | 0.20142 | 60.9741 | -61.8668 | -61.8668 | 61.0336 | 60.8643 | -0.041199 | -0.11444 | -0.068664 | -0.11902 | 0.045776 | 122.8546 | -0.28381 | 122.9691 | -0.16937 | -0.009155 | -0.073242 | -122.9141 | 122.8912 | 61.8164 | 122.7219 | 61.8256 | 122.731 | 0.16022 | 122.9004 | 122.9004 | 0 | 122.9507 | 122.8409 | 122.8363 | 122.8317 | -123.0194 | -122.9141 | 122.7859 | -0.009155 | 61.5463 | 62.059
1104.8906 | 123.1842 | -61.7935 | 60.9787 | -0.11383 | 0.0036893 | 0.064922 | 0.067232 | 0.0023925 | -0.00035036 | -0.0018307 | -0.10403 | 0.099006 | 0.066418 | -0.002085 | 0.061165 | 0.10671 | 0.00070073 | -0.28839 | 60.9421 | -61.9354 | 61.0336 | -61.6287 | -62.0224 | 61.0336 | 0.50354 | 60.9283 | -61.821 | -61.7157 | 61.1847 | 61.0016 | 0.032043 | -0.14191 | -0.036621 | 0.054931 | 0.16479 | 122.8271 | -0.22888 | 122.9691 | -0.086975 | -0.027466 | -0.050354 | -122.6944 | 122.9782 | 61.8256 | 122.7951 | 61.853 | 122.8226 | 0.3067 | 122.9691 | 123.0057 | 0.10529 | 122.8775 | 122.7493 | 122.7356 | 122.7219 | -122.9141 | -122.7997 | 122.8271 | 0.07782 | 61.5051 | 62.2971
1105.8281 | 123.056 | -61.8576 | 61.0245 | -0.052796 | 0.0015529 | 0.062145 | 0.070649 | 0.00025629 | -0.0046228 | -0.0016171 | -0.11929 | 0.10071 | 0.069836 | -0.00037605 | 0.060737 | 0.10756 | 0.00048713 | -0.30212 | 60.9695 | -61.972 | 60.9695 | -61.7477 | -62.0956 | 61.0291 | 0.27008 | 60.9833 | -61.853 | -61.8347 | 61.0931 | 60.9009 | -0.009155 | -0.11444 | -0.054932 | -0.054932 | 0.10986 | 122.8867 | -0.23804 | 123.0011 | -0.1236 | 0.004578 | -0.041199 | -122.8592 | 122.9507 | 61.8484 | 122.7585 | 61.8439 | 122.7539 | 0.2243 | 122.9416 | 122.9462 | 0.01831 | 122.9416 | 122.8363 | 122.8271 | 122.8409 | -122.9965 | -122.8775 | 122.8271 | 0.022888 | 61.5555 | 62.1277
1106.8906 | 123.1613 | -61.8027 | 61.0474 | -0.11383 | 0.0034757 | 0.064281 | 0.066377 | 0.0015381 | -0.002273 | -0.0033261 | -0.0002747 | 0.099219 | 0.068127 | -0.003153 | 0.060951 | 0.10628 | 0.0015551 | -0.18768 | 60.965 | -61.8713 | 61.0703 | -61.6013 | -61.9446 | 61.1801 | 0.45776 | 60.9604 | -61.8027 | -61.7523 | 61.2305 | 61.0428 | 0.17395 | -0.068665 | -0.082397 | 0.022888 | 0.20142 | 122.9828 | -0.14191 | 123.0515 | -0.073242 | 0 | -0.086975 | -122.7997 | 123.0331 | 61.9766 | 122.8455 | 61.9766 | 122.8455 | 0.27008 | 122.9416 | 123.0331 | 0.050354 | 122.8363 | 122.7631 | 122.7676 | 122.7631 | -122.9187 | -122.85 | 122.8729 | 0.050354 | 61.615 | 62.2604
1107.8438 | 123.143 | -61.8393 | 60.9879 | -0.075684 | 0.00091214 | 0.063213 | 0.068941 | 0.0019653 | -0.0020594 | -0.0043943 | -0.082672 | 0.1005 | 0.068127 | 0.0015466 | 0.060096 | 0.10628 | -0.00079467 | -0.32501 | 60.9421 | -61.9583 | 60.9787 | -61.6882 | -62.0728 | 61.084 | 0.32044 | 60.9375 | -61.8484 | -61.7477 | 61.1847 | 60.9924 | 0.027466 | -0.11902 | -0.045776 | -0.009155 | 0.15106 | 122.9233 | -0.23346 | 123.0423 | -0.11444 | -0.009156 | -0.050354 | -122.7356 | 123.024 | 61.8668 | 122.8317 | 61.8759 | 122.8409 | 0.27008 | 122.937 | 123.0331 | 0.10071 | 122.9004 | 122.7859 | 122.7814 | 122.7768 | -122.9462 | -122.8363 | 122.818 | 0.091552 | 61.5143 | 62.1597
1108.8906 | 123.1247 | -61.7935 | 61.0199 | -0.14435 | 0.0021939 | 0.061291 | 0.065523 | 0.0017517 | -0.00099116 | -0.0022581 | -0.0002747 | 0.09986 | 0.067058 | -0.0063574 | 0.062874 | 0.10585 | 0.00027333 | -0.29297 | 60.9741 | -61.9171 | 61.0062 | -61.6562 | -62.0178 | 61.1206 | 0.35248 | 60.9329 | -61.8301 | -61.7615 | 61.2076 | 61.0382 | 0.091553 | -0.1236 | -0.045776 | -0.013732 | 0.13733 | 122.9141 | -0.2243 | 123.0377 | -0.10071 | -0.036621 | -0.086975 | -122.7814 | 123.0011 | 61.8851 | 122.8317 | 61.9217 | 122.8683 | 0.26093 | 122.9233 | 123.0377 | 0.068664 | 122.8912 | 122.7631 | 122.7676 | 122.7264 | -122.937 | -122.85 | 122.7997 | 0.032043 | 61.5005 | 62.146
1109.8281 | 123.0835 | -61.8073 | 61.0519 | -0.068054 | 0.0013393 | 0.062786 | 0.069368 | 0.0015381 | -0.00035036 | -0.0024717 | -0.094879 | 0.10157 | 0.068981 | -0.002085 | 0.059669 | 0.10714 | 0.0021961 | -0.24261 | 61.0382 | -61.9354 | 60.9879 | -61.6974 | -62.027 | 61.0886 | 0.37994 | 61.0016 | -61.8439 | -61.7844 | 61.1664 | 60.9924 | 0.12817 | -0.12817 | -0.013733 | -0.064087 | 0.10986 | 122.8958 | -0.21973 | 123.024 | -0.091553 | -0.036621 | -0.050354 | -122.8363 | 122.9736 | 61.9354 | 122.7997 | 61.972 | 122.8363 | 0.23804 | 122.9233 | 123.0103 | 0.059509 | 122.9736 | 122.8455 | 122.8455 | 122.8088 | -122.9874 | -122.8958 | 122.7951 | 0.022888 | 61.5646 | 62.1872
1110.8906 | 123.1567 | -61.7844 | 61.0382 | -0.014649 | 0.0017667 | 0.062145 | 0.066804 | -0.0010253 | -0.0033412 | 0.00073273 | -0.11624 | 0.10178 | 0.065349 | -0.0055028 | 0.061378 | 0.10671 | -0.0012219 | -0.21973 | 60.965 | -61.9308 | 61.0657 | -61.5692 | -61.702 | 61.4136 | 0.50354 | 60.9421 | -61.821 | -61.7569 | 61.29 | 61.0565 | 0.15564 | -0.14648 | -0.073242 | 0.027466 | 0.21515 | 123.1979 | 0.082398 | 123.3444 | 0.22888 | -0.036621 | -0.09613 | -122.7951 | 123.0743 | 61.94 | 122.8409 | 61.9766 | 122.8775 | 0.36163 | 122.9965 | 123.111 | 0.064087 | 122.8958 | 122.7631 | 122.7493 | 122.7264 | -122.9691 | -122.8592 | 122.85 | 0.027466 | 61.5646 | 62.2879
1111.8281 | 123.0606 | -61.8164 | 61.0748 | -0.090943 | 0.0021939 | 0.060436 | 0.069368 | 0.0013245 | 0.00029044 | -0.0035397 | -0.11929 | 0.10114 | 0.066631 | 0.0049646 | 0.060524 | 0.1065 | -0.0025037 | -0.25177 | 61.0153 | -61.9537 | 61.0016 | -61.6974 | -62.0316 | 61.0931 | 0.36621 | 60.997 | -61.8347 | -61.7661 | 61.1664 | 60.965 | 0.11902 | -0.13733 | -0.059509 | -0.073242 | 0.11902 | 122.9095 | -0.21515 | 123.0469 | -0.07782 | -0.018311 | -0.07782 | -122.8409 | 122.9828 | 61.9354 | 122.7814 | 61.9537 | 122.7997 | 0.25635 | 122.9553 | 123.0011 | 0.068665 | 122.9691 | 122.8317 | 122.8317 | 122.8134 | -123.0286 | -122.9095 | 122.818 | 0.050354 | 61.5646 | 62.1826
1112.9062 | 123.1522 | -61.8118 | 61.0474 | -0.037537 | 0.00027134 | 0.061504 | 0.068727 | 0.0017517 | -0.002273 | -0.0016171 | -0.11624 | 0.099647 | 0.066631 | -0.0044348 | 0.060737 | 0.10564 | -0.0012219 | -0.23346 | 61.0016 | -61.94 | 61.0016 | -61.6745 | -62.0407 | 61.084 | 0.37537 | 60.997 | -61.8347 | -61.7752 | 61.1618 | 60.965 | 0.07782 | -0.12817 | -0.045776 | -0.045776 | 0.13733 | 122.8958 | -0.22888 | 123.024 | -0.10071 | -0.022888 | -0.050354 | -122.8226 | 122.9736 | 61.8896 | 122.7768 | 61.9125 | 122.7997 | 0.2655 | 122.9416 | 122.9965 | 0.059509 | 122.9416 | 122.8317 | 122.8134 | 122.8088 | -122.9874 | -122.8821 | 122.8134 | 0.036621 | 61.5784 | 62.1872
1113.8281 | 123.0652 | -61.8118 | 61.0519 | -0.14435 | 0.0021939 | 0.062145 | 0.071077 | 0.0062379 | 0.0030676 | -0.0011899 | -0.088776 | 0.10071 | 0.066418 | -0.0046484 | 0.066078 | 0.10543 | -0.00036747 | -0.24261 | 60.9924 | -61.9629 | 60.997 | -61.6653 | -62.0316 | 61.0794 | 0.37079 | 60.9833 | -61.8393 | -61.8439 | 61.2122 | 60.9833 | 0.064087 | -0.15106 | -0.059509 | -0.054932 | 0.14649 | 122.8912 | -0.21973 | 123.0423 | -0.068664 | -0.027465 | -0.068665 | -122.8958 | 123.024 | 61.8759 | 122.7951 | 61.9034 | 122.8226 | 0.29755 | 122.9599 | 123.0515 | -0.004578 | 122.9553 | 122.8226 | 122.8043 | 122.7951 | -123.0148 | -122.8912 | 122.8088 | -0.032043 | 61.5692 | 62.1826
1114.8906 | 123.0698 | -61.8439 | 61.0153 | -0.1062 | 5.7742e-05 | 0.059795 | 0.068513 | 0.0013245 | -0.00077756 | -0.00033547 | -0.076569 | 0.10157 | 0.067699 | 0.001333 | 0.059669 | 0.10607 | -0.0016493 | -0.1831 | 60.9833 | -61.9629 | 60.9512 | -61.7706 | -62.1414 | 61.0199 | 0.19684 | 60.9604 | -61.8668 | -61.8301 | 61.0886 | 60.8963 | -0.036621 | -0.11902 | -0.032044 | -0.064087 | 0.073242 | 122.8638 | -0.29755 | 122.9828 | -0.17853 | -0.022888 | -0.054932 | -122.8455 | 122.9324 | 61.8073 | 122.7402 | 61.8301 | 122.7631 | 0.19226 | 122.9141 | 122.9553 | 0.036621 | 122.9462 | 122.8271 | 122.8271 | 122.8043 | -122.9782 | -122.8821 | 122.7951 | 0.013733 | 61.6608 | 62.0407
1115.8281 | 123.0286 | -61.7981 | 61.0794 | -0.11383 | 0.00069854 | 0.061932 | 0.067445 | 0.00046989 | -0.00013676 | -0.00076267 | -0.042999 | 0.10029 | 0.070476 | -0.0059302 | 0.062233 | 0.10585 | 0.0017687 | -0.27924 | 61.0336 | -61.9354 | 60.9467 | -61.7111 | -62.0499 | 61.0794 | 0.32044 | 61.0107 | -61.8393 | -61.8256 | 61.1252 | 60.9604 | 0.09613 | -0.13733 | -0.045777 | -0.13275 | 0.086975 | 122.8775 | -0.25177 | 123.0148 | -0.11444 | -0.041198 | -0.068665 | -122.905 | 122.9233 | 61.8942 | 122.7585 | 61.9354 | 122.7997 | 0.2243 | 122.8821 | 122.9645 | 0.013732 | 122.9691 | 122.85 | 122.8317 | 122.8088 | -123.0148 | -122.9187 | 122.7448 | -0.027466 | 61.5189 | 62.1185
1116.8906 | 123.0789 | -61.853 | 61.0199 | -0.075684 | 0.0026211 | 0.060863 | 0.066377 | 0.0034607 | -0.00099116 | 0.00094633 | -0.10098 | 0.10157 | 0.065136 | -0.0035802 | 0.061592 | 0.1082 | -0.0016493 | -0.30212 | 60.9329 | -61.9949 | 60.9009 | -61.7203 | -62.1552 | 60.9787 | 0.20599 | 60.9467 | -61.8668 | -61.8393 | 61.0886 | 60.8963 | -0.045776 | -0.14191 | -0.086975 | -0.11902 | 0.13275 | 122.8317 | -0.30212 | 122.9736 | -0.16022 | -0.013733 | -0.073242 | -122.8592 | 122.9416 | 61.8073 | 122.7493 | 61.821 | 122.7631 | 0.27466 | 122.8958 | 122.9553 | 0.027466 | 122.9279 | 122.8134 | 122.7859 | 122.7997 | -123.0148 | -122.8867 | 122.7539 | 0.013733 | 61.5509 | 62.059
1117.8438 | 123.0789 | -61.8347 | 60.9833 | -0.037537 | 0.0019803 | 0.063641 | 0.066804 | 0.0028199 | -0.0020594 | -0.0018307 | -0.10709 | 0.09986 | 0.065563 | -0.0059302 | 0.06031 | 0.10628 | 0.00027333 | -0.35248 | 60.965 | -61.9629 | 60.9238 | -61.734 | -62.1185 | 61.0245 | 0.21515 | 60.965 | -61.8439 | -61.8073 | 61.116 | 60.9421 | -0.022888 | -0.12817 | -0.01831 | -0.059509 | 0.10071 | 122.8592 | -0.28381 | 122.9874 | -0.15564 | -0.009155 | -0.01831 | -122.7905 | 122.9507 | 61.8118 | 122.7768 | 61.821 | 122.7859 | 0.22888 | 122.8867 | 122.9599 | 0.036621 | 122.9279 | 122.8088 | 122.7997 | 122.7997 | -122.9462 | -122.8271 | 122.7585 | 0.027466 | 61.4822 | 62.0499
1118.8906 | 123.1338 | -61.821 | 60.9924 | -0.052796 | 0.0011257 | 0.063 | 0.069368 | 0.0015381 | -0.0014184 | -0.0014035 | -0.094879 | 0.099647 | 0.065136 | 0.0024012 | 0.060737 | 0.10585 | -0.0033581 | -0.34332 | 60.9787 | -61.9583 | 60.9558 | -61.6974 | -62.0819 | 61.0611 | 0.2655 | 60.9192 | -61.8439 | -61.7661 | 61.116 | 60.9924 | 0.032043 | -0.13733 | -0.013733 | -0.036621 | 0.1236 | 122.8821 | -0.26093 | 123.0194 | -0.1236 | -0.022888 | -0.073243 | -122.7585 | 122.937 | 61.853 | 122.8134 | 61.8759 | 122.8363 | 0.26093 | 122.9141 | 122.9599 | 0.07782 | 122.937 | 122.7631 | 122.7997 | 122.7402 | -122.9507 | -122.8363 | 122.7768 | 0.054932 | 61.4777 | 62.0865
1119.8281 | 123.0515 | -61.7935 | 61.0611 | -0.037537 | 0.0021939 | 0.062572 | 0.067659 | -0.00038451 | -0.00077756 | -0.0016171 | -0.033844 | 0.1005 | 0.066204 | -0.001444 | 0.059883 | 0.1065 | -0.0025037 | -0.20599 | 60.9787 | -61.8988 | 61.0199 | -61.6379 | -61.9858 | 61.1252 | 0.37994 | 60.9879 | -61.8164 | -61.8118 | 61.1252 | 61.0153 | 0.14648 | -0.10529 | -0.082397 | -0.041199 | 0.15564 | 122.9187 | -0.19226 | 123.024 | -0.086975 | -0.022888 | -0.073242 | -122.8729 | 122.9187 | 61.94 | 122.8088 | 61.9629 | 122.8317 | 0.26093 | 122.9187 | 122.9416 | 0.004577 | 122.8775 | 122.8043 | 122.7722 | 122.7814 | -122.9599 | -122.8775 | 122.8134 | -0.018311 | 61.5875 | 62.1735
1120.8906 | 123.1705 | -61.7889 | 61.0107 | -0.14435 | 0.0039029 | 0.061718 | 0.067232 | -0.0012391 | -0.0024866 | -0.0028989 | -0.058258 | 0.10071 | 0.066204 | 0.0021876 | 0.059242 | 0.10799 | -0.00058107 | -0.28381 | 60.9238 | -61.9492 | 61.0199 | -61.6196 | -62.0087 | 61.0977 | 0.31128 | 60.9146 | -61.8256 | -61.7706 | 61.2625 | 61.0199 | 0.018311 | -0.16022 | -0.086975 | 0.009155 | 0.16937 | 122.8867 | -0.21973 | 123.0469 | -0.059509 | -0.036622 | -0.09613 | -122.7814 | 123.0515 | 61.8073 | 122.8088 | 61.8439 | 122.8455 | 0.32959 | 122.9691 | 123.0881 | 0.054932 | 122.8729 | 122.7402 | 122.7127 | 122.7036 | -122.9599 | -122.8363 | 122.8088 | 0.01831 | 61.5051 | 62.1002
1121.8281 | 123.1934 | -61.7432 | 61.0611 | -0.098572 | 5.7742e-05 | 0.062359 | 0.06595 | -0.00038451 | -0.0016322 | 9.193e-05 | -0.0063781 | 0.09751 | 0.064495 | -0.0052892 | 0.060951 | 0.105 | -0.0014355 | -0.21057 | 60.9512 | -61.9034 | 61.1114 | -61.5417 | -61.9308 | 61.1847 | 0.4715 | 60.9695 | -61.7889 | -61.7294 | 61.2854 | 61.1389 | 0.28839 | -0.16022 | -0.10986 | 0.050354 | 0.20142 | 122.9279 | -0.18768 | 123.0881 | -0.027466 | -0.045776 | -0.091553 | -122.7905 | 123.0286 | 62.0316 | 122.8821 | 62.0773 | 122.9279 | 0.36163 | 123.0148 | 123.0743 | 0.059509 | 122.8546 | 122.7585 | 122.6944 | 122.7127 | -122.9645 | -122.85 | 122.8546 | 0.013733 | 61.5326 | 62.2147
1122.8906 | 123.0927 | -61.8164 | 60.9924 | -0.1062 | 0.0013393 | 0.061291 | 0.071504 | 0.0021789 | -0.0012048 | -0.0016171 | -0.033844 | 0.099219 | 0.065563 | 0.00047855 | 0.058174 | 0.10415 | -0.0059217 | -0.31128 | 60.9329 | -61.9354 | 61.0245 | -61.6287 | -62.0544 | 61.1114 | 0.3067 | 60.9192 | -61.8347 | -61.7935 | 61.1481 | 61.0016 | 0.004578 | -0.11902 | -0.05951 | 0.032043 | 0.18768 | 122.9279 | -0.23804 | 123.0469 | -0.11902 | -0.018311 | -0.073243 | -122.7859 | 122.9645 | 61.821 | 122.818 | 61.8393 | 122.8363 | 0.3067 | 122.9599 | 122.9828 | 0.041199 | 122.8683 | 122.7539 | 122.7493 | 122.7356 | -122.9279 | -122.8271 | 122.8409 | 0.022888 | 61.5051 | 62.1231
1123.8281 | 123.0148 | -61.8347 | 61.0748 | -0.007019 | 0.0030483 | 0.06065 | 0.068086 | -0.0029479 | -0.0024866 | -0.0014035 | -0.052155 | 0.099647 | 0.066204 | -0.0087072 | 0.061592 | 0.10457 | -0.0057081 | -0.26093 | 61.0062 | -61.9171 | 60.9787 | -61.6928 | -62.059 | 61.0748 | 0.33875 | 61.0062 | -61.8301 | -61.8073 | 61.1343 | 60.9421 | 0.082397 | -0.082397 | -0.068664 | -0.09613 | 0.14191 | 122.9095 | -0.2243 | 122.9919 | -0.14191 | 0.004578 | -0.068664 | -122.8821 | 122.9691 | 61.9171 | 122.7768 | 61.9125 | 122.7722 | 0.2243 | 122.8958 | 122.9645 | 0.022888 | 122.9233 | 122.8363 | 122.8409 | 122.8409 | -122.9919 | -122.905 | 122.8134 | 0.027466 | 61.5738 | 62.1735
1124.8906 | 123.0881 | -61.8484 | 60.965 | -0.068054 | 0.0024075 | 0.064922 | 0.069795 | 0.00089729 | 0.0019994 | 0.00051913 | -0.094879 | 0.097938 | 0.067913 | -0.0027258 | 0.059242 | 0.10799 | -0.0027173 | -0.28381 | 60.9375 | -61.9675 | 61.0245 | -61.6562 | -62.0132 | 61.0886 | 0.32959 | 60.9375 | -61.8347 | -61.7477 | 61.1938 | 61.0703 | 0.013733 | -0.11902 | -0.027466 | 0.059509 | 0.19226 | 122.937 | -0.16479 | 123.056 | -0.045777 | 0.013733 | -0.027466 | -122.7127 | 123.0423 | 61.8622 | 122.9187 | 61.8484 | 122.905 | 0.31128 | 122.9919 | 123.0286 | 0.086975 | 122.905 | 122.7722 | 122.7859 | 122.7859 | -122.9324 | -122.7997 | 122.8729 | 0.10071 | 61.5646 | 62.178
1125.8281 | 123.111 | -61.7661 | 61.0565 | -0.19775 | 0.0039029 | 0.060009 | 0.069368 | 0.0030335 | -0.0014184 | -0.0020443 | -0.018585 | 0.099219 | 0.069195 | -0.001444 | 0.06031 | 0.10607 | -0.00079467 | -0.20599 | 60.9604 | -61.9263 | 61.0748 | -61.5601 | -61.9675 | 61.1618 | 0.42572 | 60.9558 | -61.821 | -61.7249 | 61.235 | 61.0565 | 0.16937 | -0.16022 | -0.096131 | 0.01831 | 0.20599 | 122.9279 | -0.20142 | 123.0881 | -0.041198 | -0.054932 | -0.10071 | -122.7814 | 123.0011 | 61.9354 | 122.8226 | 61.9904 | 122.8775 | 0.36621 | 123.0011 | 123.056 | 0.09613 | 122.8867 | 122.7768 | 122.7264 | 122.7219 | -122.9828 | -122.8775 | 122.8409 | 0.041198 | 61.5601 | 62.1918
1126.8906 | 123.1064 | -61.8118 | 61.0016 | -0.060425 | 0.0034757 | 0.061077 | 0.070222 | 0.0030335 | -0.0014184 | -0.0026853 | -0.067413 | 0.09986 | 0.069408 | -0.0025122 | 0.06031 | 0.10415 | 5.9726e-05 | -0.3067 | 60.9283 | -61.9354 | 61.0153 | -61.6241 | -62.027 | 61.0931 | 0.32501 | 60.9329 | -61.8439 | -61.7844 | 61.1526 | 60.9833 | 0.018311 | -0.1236 | -0.073242 | 0.013733 | 0.18768 | 122.905 | -0.21515 | 123.0286 | -0.091553 | -0.032043 | -0.068665 | -122.7859 | 122.9645 | 61.8301 | 122.7951 | 61.8622 | 122.8271 | 0.31128 | 122.9507 | 122.9965 | 0.059509 | 122.8638 | 122.7768 | 122.7402 | 122.7448 | -122.937 | -122.8455 | 122.8271 | 0.027466 | 61.5051 | 62.1368
1127.8281 | 123.1567 | -61.7889 | 61.0291 | -0.052796 | 0.00069854 | 0.061932 | 0.068086 | 0.0051697 | -0.00056396 | -0.0039671 | 0.082123 | 0.10157 | 0.069195 | -0.003153 | 0.05796 | 0.10607 | -0.0033581 | -0.2243 | 60.9741 | -61.9125 | 61.0886 | -61.5555 | -61.9263 | 61.1938 | 0.19226 | 60.965 | -61.8164 | -61.7249 | 61.235 | 61.0886 | 0.1831 | -0.1236 | -0.054932 | 0.059509 | 0.23346 | 122.9828 | -0.13733 | 123.1064 | -0.013733 | -0.027466 | -0.064087 | -122.7539 | 123.024 | 61.972 | 122.8775 | 61.9995 | 122.905 | 0.35706 | 123.0011 | 123.0515 | 0.091552 | 122.8867 | 122.7814 | 122.7631 | 122.7539 | -122.9416 | -122.8455 | 122.8775 | 0.064086 | 61.5646 | 61.9812
1128.8906 | 123.0515 | -61.8347 | 61.0245 | -0.075684 | 0.0011257 | 0.062572 | 0.069795 | 0.00025629 | -0.00505 | -0.0020443 | -0.12845 | 0.10114 | 0.065777 | -0.0029394 | 0.059028 | 0.10714 | 0.0036913 | -0.29755 | 60.9879 | -61.9537 | 60.9375 | -61.7889 | -62.1323 | 61.0199 | 0.19684 | 60.9512 | -61.8576 | -61.8439 | 61.0886 | 60.91 | -0.041199 | -0.11902 | -0.036621 | -0.086975 | 0.045777 | 122.8546 | -0.29755 | 122.9736 | -0.17853 | -0.022888 | -0.073242 | -122.8683 | 122.9233 | 61.7935 | 122.7448 | 61.8164 | 122.7676 | 0.1648 | 122.8912 | 122.9462 | 0.013733 | 122.9416 | 122.8088 | 122.8226 | 122.7859 | -122.9782 | -122.8821 | 122.7722 | -0.009155 | 61.5372 | 62.0316
1129.8281 | 123.1476 | -61.7981 | 61.0199 | -0.052796 | -0.00058326 | 0.061504 | 0.0683 | -0.00017091 | -0.00099116 | -0.0033261 | -0.015534 | 0.10007 | 0.068981 | -0.0072118 | 0.059669 | 0.10308 | 5.9726e-05 | -0.26093 | 60.9558 | -61.9263 | 61.0428 | -61.5967 | -61.9583 | 61.1481 | 0.39368 | 60.9604 | -61.8073 | -61.7203 | 61.2396 | 61.0611 | 0.14191 | -0.12817 | -0.064086 | 0.022889 | 0.20142 | 122.9462 | -0.16022 | 123.0743 | -0.032043 | -0.009155 | -0.059509 | -122.7402 | 123.0377 | 61.94 | 122.8592 | 61.9492 | 122.8683 | 0.32959 | 122.9691 | 123.0469 | 0.086975 | 122.8821 | 122.7676 | 122.7539 | 122.7585 | -122.9462 | -122.8271 | 122.8409 | 0.07782 | 61.5372 | 62.1918
1130.8906 | 123.1293 | -61.821 | 60.9879 | -0.12909 | 0.0028347 | 0.062786 | 0.067659 | -0.00017091 | -0.0016322 | -0.00012167 | -0.064362 | 0.099219 | 0.067058 | 0.001333 | 0.060524 | 0.10671 | -0.0020765 | -0.28839 | 60.9009 | -61.9537 | 61.0016 | -61.5417 | -62.0407 | 61.1023 | 0.30212 | 60.9192 | -61.8347 | -61.734 | 61.1801 | 60.9833 | 0.032043 | -0.13275 | -0.086975 | 0.013733 | 0.27924 | 122.9233 | -0.21973 | 123.056 | -0.086975 | -0.013733 | -0.068665 | -122.7219 | 123.0011 | 61.853 | 122.8043 | 61.8668 | 122.818 | 0.41199 | 122.9553 | 123.0148 | 0.10071 | 122.8546 | 122.7539 | 122.7219 | 122.7402 | -122.9416 | -122.8226 | 122.8226 | 0.086975 | 61.5326 | 62.1231
1131.8281 | 123.0469 | -61.7889 | 61.0336 | -0.083313 | 0.0017667 | 0.061077 | 0.068941 | -0.0010253 | 0.00093144 | -0.0018307 | -0.046051 | 0.099006 | 0.066845 | 0.0017602 | 0.060737 | 0.10564 | -0.0027173 | -0.21057 | 60.9879 | -61.908 | 61.0474 | -61.6196 | -61.9675 | 61.1435 | 0.41199 | 60.9879 | -61.7889 | -61.7844 | 61.1572 | 60.9924 | 0.13733 | -0.11902 | -0.045776 | 0.013733 | 0.16937 | 122.9324 | -0.17853 | 123.0515 | -0.059509 | 0 | -0.045776 | -122.818 | 122.9462 | 61.9263 | 122.7814 | 61.9263 | 122.7814 | 0.28839 | 122.9553 | 122.9462 | 0.004577 | 122.8958 | 122.7768 | 122.7768 | 122.7768 | -122.9416 | -122.8226 | 122.8363 | 0.004577 | 61.5784 | 62.2009
1132.8906 | 123.1293 | -61.8301 | 61.0428 | -0.083313 | 0.0015529 | 0.063 | 0.070436 | 0.0058105 | -0.0012048 | -0.0026853 | -0.13455 | 0.10157 | 0.069408 | -0.00016245 | 0.059669 | 0.10628 | -0.0033581 | -0.34332 | 60.9558 | -61.9766 | 60.8963 | -61.7844 | -62.146 | 60.997 | 0.18768 | 60.965 | -61.853 | -61.7889 | 60.8688 | 60.6491 | -0.2243 | -0.14648 | -0.086975 | -0.14648 | 0.045776 | 122.8271 | -0.31586 | 122.9736 | -0.16937 | -0.022888 | -0.07782 | -122.8317 | 122.699 | 61.6058 | 122.4792 | 61.6287 | 122.5021 | 0.19226 | 122.8729 | 122.7219 | 0.064087 | 122.9324 | 122.818 | 122.7859 | 122.7951 | -123.0194 | -122.8958 | 122.7264 | 0.041199 | 61.4868 | 62.0178
1133.8281 | 123.1522 | -61.7935 | 61.0199 | -0.090943 | -0.00036966 | 0.061291 | 0.065095 | 0.0026063 | -0.00035036 | -0.0011899 | -0.042999 | 0.098151 | 0.067699 | -0.0046484 | 0.061805 | 0.10863 | -0.0035719 | -0.2243 | 60.9787 | -61.8988 | 61.0748 | -61.5646 | -61.9354 | 61.1618 | 0.45776 | 60.9421 | -61.8027 | -61.8301 | 61.3541 | 60.9833 | 0.073242 | -0.10529 | -0.041198 | 0.054932 | 0.22888 | 122.9553 | -0.14191 | 123.0606 | -0.036621 | -0.009155 | -0.077819 | -122.85 | 123.1476 | 61.8668 | 122.7768 | 61.8759 | 122.7859 | 0.33417 | 122.9736 | 123.1567 | -0.027466 | 122.8775 | 122.7448 | 122.7722 | 122.7356 | -122.9187 | -122.8226 | 122.8683 | -0.036621 | 61.5692 | 62.2513
1134.8906 | 123.0423 | -61.7981 | 61.0611 | -0.12146 | 0.0024075 | 0.062145 | 0.070222 | 0.0032471 | -0.0027002 | -0.0014035 | -0.10098 | 0.10007 | 0.066845 | 0.00047855 | 0.06031 | 0.1018 | -0.0020765 | -0.24719 | 60.9879 | -61.9492 | 60.9787 | -61.6699 | -62.0911 | 60.9375 | 0.32959 | 60.9879 | -61.8347 | -61.7752 | 61.1481 | 60.9512 | 0.054932 | -0.15106 | -0.073242 | -0.082397 | 0.12817 | 122.7356 | -0.29297 | 122.8867 | -0.14191 | -0.036621 | -0.073242 | -122.8363 | 122.9462 | 61.853 | 122.7493 | 61.8896 | 122.7859 | 0.27924 | 122.9279 | 122.9828 | 0.059509 | 122.937 | 122.8226 | 122.7859 | 122.7859 | -123.0103 | -122.8958 | 122.7768 | 0.022888 | 61.5509 | 62.1277
1135.8281 | 123.1247 | -61.7981 | 61.0062 | -0.029907 | 0.00069854 | 0.062359 | 0.066591 | 0.0019653 | -0.0041956 | -0.0016171 | -0.012482 | 0.099433 | 0.066845 | -0.0035802 | 0.061805 | 0.10628 | -0.0031445 | -0.2655 | 60.9695 | -61.9263 | 61.0245 | -61.6196 | -61.9904 | 61.1389 | 0.37537 | 60.9421 | -61.8164 | -61.7294 | 61.235 | 61.0565 | 0.13275 | -0.12817 | -0.036622 | 0.01831 | 0.17853 | 122.937 | -0.19226 | 123.0652 | -0.064086 | -0.01831 | -0.064087 | -122.7356 | 123.0331 | 61.9308 | 122.8546 | 61.9492 | 122.8729 | 0.3067 | 122.9507 | 123.0515 | 0.086975 | 122.8958 | 122.7585 | 122.7676 | 122.7402 | -122.9324 | -122.8226 | 122.8226 | 0.068665 | 61.5326 | 62.1735
1136.8906 | 122.9782 | -61.8393 | 61.0336 | -0.083313 | 0.0019803 | 0.063213 | 0.0683 | 0.0017517 | -0.0024866 | -0.00076267 | -0.14066 | 0.1005 | 0.067058 | 0.00069215 | 0.059883 | 0.10885 | -0.0035719 | -0.35248 | 60.9558 | -61.972 | 60.9055 | -61.7889 | -62.1689 | 60.9833 | 0.16479 | 60.9833 | -61.8759 | -61.972 | 60.878 | 61.203 | 0.13733 | -0.13275 | -0.077819 | -0.12817 | 0.050354 | 122.8226 | -0.32959 | 122.9553 | -0.19684 | -0.036622 | -0.050354 | -123.0057 | 122.7173 | 61.9766 | 123.0423 | 62.0132 | 123.0789 | 0.18311 | 122.8775 | 122.7539 | -0.09613 | 122.9279 | 122.8592 | 122.7951 | 122.8226 | -123.0057 | -122.9095 | 122.7448 | -0.13275 | 61.4868 | 62.0041
1137.8281 | 123.1064 | -61.7935 | 61.0336 | -0.083313 | 0.0013393 | 0.064495 | 0.067659 | 0.00068369 | -0.0014184 | -0.0018307 | -0.033844 | 0.097724 | 0.064709 | -0.0063574 | 0.060096 | 0.10543 | -0.0016493 | -0.19684 | 60.9558 | -61.908 | 61.0611 | -61.5875 | -61.9583 | 61.1481 | 0.40283 | 60.997 | -61.821 | -61.7661 | 61.2167 | 61.0474 | 0.15106 | -0.11444 | -0.077819 | 0.027466 | 0.20599 | 122.9416 | -0.16479 | 123.056 | -0.050354 | -0.027466 | -0.036621 | -122.7997 | 123.0103 | 61.9446 | 122.8409 | 61.972 | 122.8683 | 0.32043 | 122.9691 | 123.0377 | 0.054932 | 122.8638 | 122.818 | 122.7493 | 122.7905 | -122.9416 | -122.8546 | 122.8546 | 0.027466 | 61.5967 | 62.1963
1138.8906 | 123.0789 | -61.8118 | 61.0199 | -0.045166 | 0.0017667 | 0.061718 | 0.068727 | -0.0010253 | -0.0020594 | -0.0018307 | -0.10098 | 0.10264 | 0.067486 | 0.003683 | 0.059883 | 0.10778 | 0.0017687 | -0.23804 | 60.9695 | -61.9492 | 60.9879 | -61.6837 | -62.0087 | 61.0794 | 0.34332 | 61.0016 | -61.8164 | -61.7661 | 61.1618 | 60.9695 | 0.10071 | -0.13733 | -0.050354 | -0.032043 | 0.12817 | 122.8912 | -0.19684 | 123.0286 | -0.059509 | -0.004577 | -0.01831 | -122.7859 | 122.9736 | 61.9125 | 122.7814 | 61.9171 | 122.7859 | 0.2655 | 122.937 | 122.9782 | 0.050354 | 122.9187 | 122.818 | 122.7814 | 122.8134 | -122.9691 | -122.8363 | 122.7997 | 0.045777 | 61.5738 | 62.1552
1139.8281 | 123.1796 | -61.7523 | 61.0062 | -0.12909 | 0.0026211 | 0.059368 | 0.067445 | -0.0029479 | -0.00077756 | -0.0018307 | -0.015534 | 0.099219 | 0.065136 | -0.0091344 | 0.062233 | 0.10585 | -0.0022901 | -0.20599 | 60.9558 | -61.9171 | 61.0611 | -61.5463 | -61.9263 | 61.1801 | 0.46234 | 60.9329 | -61.7752 | -61.6928 | 61.2762 | 61.0886 | 0.15564 | -0.16479 | -0.050354 | 0.054931 | 0.20599 | 122.9324 | -0.17395 | 123.0972 | -0.009156 | -0.022889 | -0.073243 | -122.699 | 123.0286 | 61.908 | 122.8409 | 61.9308 | 122.8638 | 0.37079 | 122.9782 | 123.0515 | 0.082398 | 122.8729 | 122.7081 | 122.7081 | 122.6852 | -122.9233 | -122.7814 | 122.8134 | 0.059509 | 61.5463 | 62.2147
1140.8906 | 123.111 | -61.7935 | 61.0016 | -0.14435 | 0.0030483 | 0.063854 | 0.067232 | -0.00017091 | -0.00077756 | 0.0020145 | -0.076569 | 0.098365 | 0.067272 | -0.002085 | 0.060524 | 0.10564 | -0.0059217 | -0.27466 | 60.9146 | -61.9629 | 61.0245 | -61.6379 | -62.0224 | 61.1114 | 0.31586 | 60.9238 | -61.8301 | -61.8759 | 61.4456 | 61.0794 | 0.036621 | -0.16937 | -0.086975 | 0.022888 | 0.15564 | 122.905 | -0.22888 | 123.0743 | -0.059509 | -0.036621 | -0.07782 | -122.8775 | 123.2391 | 61.8301 | 122.8729 | 61.8668 | 122.9095 | 0.32501 | 122.9874 | 123.2758 | -0.045777 | 122.8775 | 122.7539 | 122.7081 | 122.7173 | -122.9645 | -122.8317 | 122.818 | -0.082398 | 61.5189 | 62.1094
1141.8281 | 123.1247 | -61.7844 | 61.0107 | -0.075684 | 0.0011257 | 0.064281 | 0.067872 | -0.0027343 | -0.0020594 | -0.00097627 | -0.021637 | 0.10071 | 0.064922 | -0.0018712 | 0.058387 | 0.10415 | -0.00036747 | -0.26093 | 60.9467 | -61.908 | 61.0291 | -61.5967 | -61.9675 | 61.1435 | 0.39825 | 60.9558 | -61.8073 | -61.7111 | 61.2396 | 61.0565 | 0.14191 | -0.1236 | -0.064087 | 0.018311 | 0.18768 | 122.9279 | -0.1831 | 123.0515 | -0.059509 | -0.022888 | -0.054931 | -122.7219 | 123.024 | 61.9263 | 122.8409 | 61.9492 | 122.8638 | 0.31128 | 122.937 | 123.0469 | 0.09613 | 122.8546 | 122.7631 | 122.731 | 122.7402 | -122.9187 | -122.818 | 122.8134 | 0.073242 | 61.5234 | 62.1826
1142.8281 | 123.0972 | -61.7981 | 60.997 | -0.12146 | 0.0028347 | 0.060009 | 0.067872 | 0.00025629 | -0.00056396 | -0.0031125 | -0.067413 | 0.099647 | 0.065349 | -0.0018712 | 0.059669 | 0.10735 | -0.0048535 | -0.28839 | 60.91 | -61.9217 | 61.0199 | -61.6287 | -62.0087 | 61.1114 | 0.31586 | 60.9055 | -61.8347 | -61.7661 | 61.1755 | 60.9879 | 0.018311 | -0.1236 | -0.086975 | 0.022888 | 0.16937 | 122.9095 | -0.21057 | 123.0331 | -0.086975 | -0.036621 | -0.091552 | -122.7631 | 122.9736 | 61.8164 | 122.7859 | 61.853 | 122.8226 | 0.29297 | 122.9416 | 123.0103 | 0.068665 | 122.8317 | 122.7402 | 122.7081 | 122.7036 | -122.9187 | -122.8317 | 122.818 | 0.032044 | 61.5097 | 62.114
1143.8906 | 123.0515 | -61.7935 | 61.0336 | -0.045166 | 0.0024075 | 0.063854 | 0.069795 | 0.00025629 | -0.0033412 | 0.0026553 | -0.14981 | 0.1005 | 0.068554 | -0.0057166 | 0.05796 | 0.10222 | 0.0011279 | -0.27466 | 60.9833 | -61.972 | 61.0016 | -61.6928 | -62.0728 | 61.0611 | 0.33417 | 60.9924 | -61.8256 | -61.7844 | 61.1389 | 60.9467 | 0.045776 | -0.17853 | -0.050354 | -0.032043 | 0.10071 | 122.8546 | -0.27924 | 123.0331 | -0.10071 | -0.032044 | -0.041198 | -122.818 | 122.9324 | 61.8393 | 122.7402 | 61.8713 | 122.7722 | 0.27924 | 122.9736 | 122.9645 | 0.041199 | 122.9553 | 122.818 | 122.7768 | 122.7859 | -123.0057 | -122.8592 | 122.7951 | 0.009155 | 61.5189 | 62.1277
1144.8281 | 123.0789 | -61.8118 | 61.0153 | -0.1062 | 0.0030483 | 0.062572 | 0.067659 | -0.00059811 | -0.0014184 | -0.00012167 | -0.027741 | 0.097724 | 0.06834 | -0.0025122 | 0.060524 | 0.10543 | 0.0043323 | -0.32501 | 60.9467 | -61.9263 | 60.9833 | -61.6837 | -62.027 | 61.0977 | 0.26093 | 60.9375 | -61.8347 | -61.7798 | 61.1435 | 60.9833 | 0.018311 | -0.11444 | -0.068665 | -0.032044 | 0.12817 | 122.9095 | -0.21515 | 123.024 | -0.10071 | -0.022888 | -0.07782 | -122.7951 | 122.9553 | 61.8301 | 122.7951 | 61.853 | 122.818 | 0.24262 | 122.9095 | 122.9782 | 0.054932 | 122.8729 | 122.7722 | 122.7585 | 122.7493 | -122.9416 | -122.85 | 122.7951 | 0.032044 | 61.4868 | 62.0728
1145.8906 | 122.9965 | -61.8118 | 61.0748 | -0.075684 | 0.00027134 | 0.061932 | 0.069581 | -0.0025207 | -0.00099116 | 0.00051913 | -0.085724 | 0.1005 | 0.067699 | -0.0080664 | 0.061592 | 0.10628 | 0.0013415 | -0.27924 | 60.997 | -61.9492 | 60.9558 | -61.7065 | -62.0407 | 61.0748 | 0.32501 | 61.0107 | -61.8301 | -61.8164 | 61.1389 | 60.9421 | 0.086975 | -0.13733 | -0.07782 | -0.11902 | 0.10529 | 122.8867 | -0.22888 | 123.024 | -0.091552 | -0.01831 | -0.064087 | -122.8912 | 122.9507 | 61.8988 | 122.7539 | 61.9171 | 122.7722 | 0.24261 | 122.905 | 122.9691 | 0.013733 | 122.9462 | 122.8409 | 122.8088 | 122.8226 | -123.024 | -122.905 | 122.7676 | -0.004577 | 61.5326 | 62.1368
1146.8281 | 123.1201 | -61.821 | 61.0016 | -0.14435 | -0.00079686 | 0.061932 | 0.066163 | -0.0014527 | -0.002273 | -0.0031125 | -0.046051 | 0.10007 | 0.065777 | -0.003153 | 0.062019 | 0.10735 | -0.0016493 | -0.30212 | 60.9283 | -61.9492 | 61.0016 | -61.6425 | -62.0544 | 61.084 | 0.29297 | 60.9421 | -61.8439 | -61.7798 | 61.1481 | 60.965 | 0.018311 | -0.12817 | -0.073242 | 0 | 0.17853 | 122.905 | -0.23346 | 123.0331 | -0.10529 | -0.022888 | -0.059509 | -122.7814 | 122.9691 | 61.8393 | 122.7859 | 61.8622 | 122.8088 | 0.3067 | 122.9507 | 122.9919 | 0.064087 | 122.8775 | 122.7859 | 122.7493 | 122.7631 | -122.9507 | -122.8455 | 122.8226 | 0.041199 | 61.5189 | 62.114
1147.8906 | 123.0743 | -61.821 | 61.0016 | -0.1062 | 0.0011257 | 0.060863 | 0.069154 | 0.0011109 | -0.0012048 | 9.193e-05 | -0.11929 | 0.102 | 0.066631 | -0.0052892 | 0.058174 | 0.10735 | -0.0029309 | -0.35706 | 60.9741 | -61.9949 | 60.9329 | -61.734 | -62.1231 | 61.0245 | 0.21057 | 60.9512 | -61.8622 | -61.7752 | 61.1023 | 60.9192 | -0.013733 | -0.17395 | -0.027466 | -0.068665 | 0.086975 | 122.8455 | -0.30212 | 123.0194 | -0.12817 | -0.041199 | -0.050354 | -122.7768 | 122.9233 | 61.8073 | 122.7402 | 61.8484 | 122.7814 | 0.26093 | 122.9279 | 122.9645 | 0.086975 | 122.9691 | 122.8134 | 122.7951 | 122.7722 | -122.9965 | -122.8638 | 122.7539 | 0.045776 | 61.4639 | 62.0316
1148.8281 | 123.1247 | -61.8118 | 61.0153 | -0.15961 | 0.00069854 | 0.061504 | 0.068513 | -0.00081171 | -0.0014184 | -0.0018307 | -0.049103 | 0.10029 | 0.067058 | -0.0040076 | 0.060951 | 0.10607 | 0.0017687 | -0.3067 | 60.9283 | -61.9354 | 60.9741 | -61.6562 | -62.0224 | 61.0886 | 0.27924 | 60.91 | -61.8256 | -61.7844 | 61.1664 | 60.9695 | -0.004578 | -0.1236 | -0.086975 | -0.041199 | 0.15564 | 122.9004 | -0.21057 | 123.024 | -0.086975 | -0.013733 | -0.10529 | -122.7997 | 122.9782 | 61.8073 | 122.7814 | 61.821 | 122.7951 | 0.27924 | 122.9095 | 122.9919 | 0.041199 | 122.8638 | 122.7356 | 122.7402 | 122.7219 | -122.9507 | -122.8409 | 122.7859 | 0.027466 | 61.5051 | 62.0911
1149.8906 | 123.0515 | -61.7981 | 61.0291 | -0.083313 | 0.0019803 | 0.062145 | 0.070863 | 0.0023925 | -0.0018458 | -0.0022581 | -0.10403 | 0.10114 | 0.066204 | 0.00026495 | 0.058387 | 0.10009 | -0.0010083 | -0.24719 | 60.9787 | -61.9537 | 60.9833 | -61.6653 | -62.0361 | 60.9238 | 0.31128 | 60.9924 | -61.8393 | -61.7615 | 61.1343 | 60.9558 | 0.059509 | -0.15564 | -0.050354 | -0.045777 | 0.13275 | 122.7219 | -0.23804 | 122.8775 | -0.082398 | -0.041198 | -0.036621 | -122.7905 | 122.9324 | 61.8576 | 122.7539 | 61.8988 | 122.7951 | 0.28839 | 122.937 | 122.9736 | 0.077819 | 122.9324 | 122.8317 | 122.7768 | 122.7905 | -122.9828 | -122.8683 | 122.7814 | 0.036621 | 61.5509 | 62.1094
1150.8281 | 123.0972 | -61.7981 | 60.965 | -0.12909 | 0.0039029 | 0.061504 | 0.067445 | -0.0025207 | -0.0016322 | -0.0035397 | -0.058258 | 0.098578 | 0.067699 | -0.00016245 | 0.061378 | 0.10393 | -0.0010083 | -0.28839 | 60.91 | -61.9308 | 61.0153 | -61.6058 | -62.0132 | 61.1252 | 0.32501 | 60.91 | -61.8347 | -61.7477 | 61.1664 | 60.9879 | 0.022888 | -0.13275 | -0.054932 | 0.050354 | 0.19226 | 122.9233 | -0.21515 | 123.056 | -0.082398 | -0.036621 | -0.054932 | -122.7127 | 122.9645 | 61.821 | 122.7859 | 61.8576 | 122.8226 | 0.32501 | 122.9462 | 123.0011 | 0.086975 | 122.8409 | 122.7448 | 122.7081 | 122.7081 | -122.8958 | -122.7997 | 122.8134 | 0.050354 | 61.5097 | 62.1231
1151.8906 | 123.0423 | -61.8439 | 60.997 | -0.1062 | -0.0022923 | 0.061718 | 0.067232 | 0.00089729 | -0.002273 | -0.00076267 | -0.10709 | 0.097724 | 0.067699 | -0.0016576 | 0.060737 | 0.10628 | 0.00070073 | -0.19226 | 60.9787 | -61.9583 | 60.9467 | -61.7752 | -62.1323 | 61.0153 | 0.1831 | 60.9558 | -61.8622 | -61.8301 | 61.0931 | 60.8871 | -0.045776 | -0.11444 | -0.01831 | -0.050354 | 0.068664 | 122.8592 | -0.28839 | 122.9736 | -0.17395 | -0.018311 | -0.041198 | -122.8271 | 122.937 | 61.7981 | 122.731 | 61.8164 | 122.7493 | 0.1831 | 122.905 | 122.9553 | 0.032044 | 122.937 | 122.818 | 122.8226 | 122.7997 | -122.9553 | -122.8592 | 122.7905 | 0.013733 | 61.6516 | 62.027
1152.8281 | 123.1384 | -61.7981 | 60.9833 | -0.075684 | 0.0024075 | 0.06065 | 0.066804 | 0.00089729 | -0.002273 | 0.0013735 | -0.15897 | 0.10029 | 0.064709 | -0.0029394 | 0.06031 | 0.10628 | -0.0039991 | -0.28839 | 60.9192 | -61.9354 | 61.0153 | -61.6287 | -62.0224 | 61.1206 | 0.31586 | 60.8871 | -61.853 | -61.7477 | 61.2305 | 60.9833 | 0.022888 | -0.13733 | -0.064087 | 0.032044 | 0.16937 | 122.9187 | -0.2243 | 123.056 | -0.086975 | -0.054931 | -0.09613 | -122.731 | 123.0286 | 61.821 | 122.7814 | 61.8759 | 122.8363 | 0.3067 | 122.9507 | 123.0835 | 0.10528 | 122.8546 | 122.7402 | 122.7173 | 122.6852 | -122.9187 | -122.8363 | 122.8134 | 0.050354 | 61.5097 | 62.114
1153.8906 | 123.0103 | -61.8301 | 61.0519 | -0.052796 | 0.00027134 | 0.062786 | 0.0683 | 0.0019653 | -0.0018458 | -0.0016171 | -0.14371 | 0.10071 | 0.067913 | 0.0041102 | 0.060524 | 0.10628 | -0.0016493 | -0.3067 | 60.9741 | -61.9858 | 60.9375 | -61.7294 | -62.0956 | 61.0107 | 0.20599 | 61.0062 | -61.8439 | -61.8439 | 61.0382 | 60.8871 | -0.036621 | -0.15564 | -0.07782 | -0.11444 | 0.10071 | 122.8409 | -0.2655 | 122.9965 | -0.10986 | -0.013733 | -0.045776 | -122.8958 | 122.8683 | 61.7935 | 122.7173 | 61.8073 | 122.731 | 0.25635 | 122.9233 | 122.8821 | 0 | 122.9599 | 122.85 | 122.8043 | 122.8363 | -123.0377 | -122.8958 | 122.7676 | -0.013733 | 61.5234 | 62.0361
1154.8281 | 123.143 | -61.8164 | 60.9924 | -0.098572 | 0.0032619 | 0.061718 | 0.067018 | 0.0032471 | -0.00077756 | -0.0026853 | -0.082672 | 0.10007 | 0.067272 | 0.0021876 | 0.059028 | 0.10692 | -0.0072035 | -0.29297 | 60.9146 | -61.94 | 61.0016 | -61.647 | -62.0178 | 61.1069 | 0.28839 | 60.9192 | -61.8256 | -61.7203 | 61.1893 | 60.997 | 0.041199 | -0.1236 | -0.07782 | 0.009155 | 0.16937 | 122.9233 | -0.20142 | 123.0469 | -0.07782 | -0.009156 | -0.073243 | -122.7127 | 123.0057 | 61.8576 | 122.8134 | 61.8668 | 122.8226 | 0.29297 | 122.9416 | 123.0148 | 0.10529 | 122.8546 | 122.7448 | 122.731 | 122.7356 | -122.9324 | -122.818 | 122.818 | 0.09613 | 61.5234 | 62.1048
1155.8906 | 123.0286 | -61.821 | 61.0245 | -0.045166 | 0.0024075 | 0.063 | 0.068086 | 0.0062379 | -0.00013676 | -0.0028989 | -0.1376 | 0.098151 | 0.064709 | -0.00016245 | 0.061592 | 0.10671 | -0.0042127 | -0.28839 | 60.9879 | -61.9492 | 60.9695 | -61.6791 | -62.0636 | 61.0428 | 0.27466 | 60.965 | -61.8118 | -61.7981 | 61.1023 | 60.9238 | 0.013733 | -0.12817 | -0.036621 | -0.054932 | 0.14191 | 122.8638 | -0.24262 | 122.9919 | -0.11444 | 0.009155 | -0.059509 | -122.8226 | 122.9233 | 61.8347 | 122.7448 | 61.8256 | 122.7356 | 0.27008 | 122.9187 | 122.9141 | 0.013733 | 122.937 | 122.7768 | 122.8088 | 122.7859 | -122.9736 | -122.8363 | 122.7905 | 0.022888 | 61.5326 | 62.0956
1156.8281 | 123.1064 | -61.8164 | 60.9558 | -0.022278 | 0.0030483 | 0.062359 | 0.067445 | -0.0010253 | -0.00035036 | 9.193e-05 | -0.097931 | 0.10007 | 0.068554 | 5.1352e-05 | 0.06031 | 0.10692 | 0.0021961 | -0.33875 | 60.9604 | -61.9675 | 60.9421 | -61.7065 | -62.0911 | 61.0428 | 0.22888 | 60.9375 | -61.8393 | -61.7615 | 61.1572 | 60.9833 | 0.004578 | -0.15106 | 0.004577 | -0.013733 | 0.10986 | 122.8592 | -0.27466 | 123.0103 | -0.1236 | -0.022888 | -0.018311 | -122.7173 | 122.9736 | 61.821 | 122.7997 | 61.8439 | 122.8226 | 0.26092 | 122.9095 | 122.9965 | 0.077819 | 122.9279 | 122.7768 | 122.7768 | 122.7539 | -122.9233 | -122.7951 | 122.7585 | 0.054931 | 61.4777 | 62.0453
1157.8906 | 123.0972 | -61.7661 | 61.0199 | -0.1062 | 0.0017667 | 0.059582 | 0.067659 | -0.00038451 | -0.0046228 | -0.0026853 | -0.036896 | 0.09986 | 0.066631 | -0.0022986 | 0.059456 | 0.10457 | -0.0029309 | -0.23346 | 60.9558 | -61.9308 | 61.0474 | -61.5738 | -61.9171 | 61.1572 | 0.4303 | 60.9604 | -61.7889 | -61.7477 | 61.2122 | 61.0428 | 0.16479 | -0.16479 | -0.064086 | 0.027466 | 0.19226 | 122.9233 | -0.15106 | 123.0881 | 0.013733 | -0.022888 | -0.059509 | -122.7676 | 122.9782 | 61.9308 | 122.8088 | 61.9537 | 122.8317 | 0.35706 | 122.9782 | 123.0011 | 0.041198 | 122.8867 | 122.7493 | 122.7219 | 122.7264 | -122.9507 | -122.8088 | 122.8134 | 0.01831 | 61.5326 | 62.1964
1158.8281 | 123.056 | -61.853 | 61.0245 | -0.090943 | 0.00027134 | 0.061504 | 0.068727 | -0.00059811 | -0.00099116 | 9.193e-05 | -0.088776 | 0.099219 | 0.067486 | -0.004862 | 0.060096 | 0.10607 | -0.0039991 | -0.37079 | 60.9741 | -61.9629 | 60.9146 | -61.7752 | -62.1231 | 61.0107 | 0.1831 | 60.9512 | -61.8347 | -61.8164 | 61.084 | 60.9009 | -0.027466 | -0.10986 | -0.050354 | -0.10986 | 0.077819 | 122.8638 | -0.27008 | 122.9736 | -0.16022 | 0.01831 | -0.073242 | -122.8409 | 122.937 | 61.8256 | 122.7539 | 61.8073 | 122.7356 | 0.18768 | 122.8775 | 122.9187 | 0.018311 | 122.937 | 122.7859 | 122.8271 | 122.8043 | -122.9874 | -122.8592 | 122.7676 | 0.036621 | 61.4822 | 62.0361
1159.8906 | 123.056 | -61.8164 | 61.0291 | -0.21301 | 0.0017667 | 0.063 | 0.069154 | 0.0017517 | -0.00077756 | -0.0011899 | -0.11014 | 0.10157 | 0.067272 | 0.00646 | 0.058815 | 0.10756 | 0.00091433 | -0.24261 | 60.965 | -61.972 | 60.9833 | -61.6608 | -62.0499 | 61.0657 | 0.30212 | 60.9833 | -61.8256 | -61.7935 | 61.1252 | 60.9375 | 0.036621 | -0.15564 | -0.064087 | -0.045777 | 0.15564 | 122.8821 | -0.23346 | 123.0377 | -0.07782 | -0.009156 | -0.045777 | -122.8226 | 122.9416 | 61.853 | 122.7539 | 61.8622 | 122.7631 | 0.31128 | 122.9553 | 122.9507 | 0.032044 | 122.937 | 122.8088 | 122.7814 | 122.7997 | -123.0011 | -122.8546 | 122.7997 | 0.022888 | 61.5738 | 62.1185
1160.8281 | 123.1567 | -61.8118 | 60.9787 | -0.052796 | 0.0019803 | 0.061291 | 0.070222 | 0.0030335 | -0.0018458 | -0.00076267 | -0.067413 | 0.099433 | 0.067272 | -0.0042212 | 0.060524 | 0.105 | -0.0025037 | -0.31586 | 60.9192 | -61.9675 | 60.9741 | -61.6333 | -62.0178 | 61.0977 | 0.28839 | 60.9009 | -61.8301 | -61.7203 | 61.171 | 60.9741 | 0.041199 | -0.15564 | -0.05951 | -0.004578 | 0.17853 | 122.9095 | -0.20599 | 123.0652 | -0.050354 | -0.01831 | -0.07782 | -122.699 | 122.9828 | 61.853 | 122.7859 | 61.8713 | 122.8043 | 0.33417 | 122.9416 | 123.0011 | 0.10986 | 122.8867 | 122.731 | 122.731 | 122.7127 | -122.9462 | -122.8088 | 122.7859 | 0.091553 | 61.496 | 62.1002
1161.8906 | 123.0423 | -61.7935 | 61.0519 | -0.1062 | 0.0019803 | 0.060863 | 0.068086 | 0.0011109 | -0.00099116 | -0.0018307 | -0.030792 | 0.098151 | 0.067058 | 0.00047855 | 0.060096 | 0.10692 | -0.0018629 | -0.21515 | 60.9375 | -61.8988 | 61.0382 | -61.6241 | -61.9629 | 61.1298 | 0.39368 | 60.9512 | -61.8118 | -61.7935 | 61.1618 | 60.9924 | 0.11902 | -0.10529 | -0.11444 | -0.013733 | 0.16937 | 122.9233 | -0.16937 | 123.0286 | -0.064087 | -0.018311 | -0.10071 | -122.8455 | 122.9553 | 61.9125 | 122.7859 | 61.9308 | 122.8043 | 0.27466 | 122.937 | 122.9736 | 0.018311 | 122.8363 | 122.7631 | 122.731 | 122.7448 | -122.9507 | -122.8638 | 122.8317 | 0 | 61.5784 | 62.1872
1162.8281 | 122.9874 | -61.8439 | 61.0153 | -0.075684 | 5.7742e-05 | 0.061291 | 0.069154 | -0.0014527 | -0.0014184 | -0.00097627 | -0.11624 | 0.10007 | 0.069195 | 0.0053918 | 0.059242 | 0.10607 | -0.0035719 | -0.32959 | 60.965 | -61.9766 | 60.8963 | -61.7798 | -62.1231 | 60.9833 | 0.16479 | 60.9833 | -61.8668 | -61.8713 | 61.0107 | 60.8597 | -0.032043 | -0.13275 | -0.050354 | -0.11902 | 0.064087 | 122.8271 | -0.27924 | 122.9599 | -0.14648 | -0.022888 | -0.032044 | -122.8867 | 122.8546 | 61.8118 | 122.7036 | 61.8347 | 122.7264 | 0.19684 | 122.8729 | 122.8775 | -0.004578 | 122.9416 | 122.85 | 122.8088 | 122.8271 | -122.9919 | -122.8821 | 122.7402 | -0.027466 | 61.5143 | 62.0087
1163.8906 | 123.0698 | -61.8118 | 61.0382 | -0.083313 | 0.0030483 | 0.061504 | 0.070649 | 0.0043151 | -0.0041956 | -0.0016171 | -0.070465 | 0.098792 | 0.070263 | 0.0032556 | 0.059883 | 0.10457 | 0.00048713 | -0.24719 | 61.0062 | -61.94 | 60.9741 | -61.6562 | -62.0407 | 61.0794 | 0.21515 | 60.9512 | -61.8668 | -61.7752 | 61.1298 | 60.9604 | 0.09613 | -0.12817 | -0.032043 | -0.064087 | 0.15564 | 122.8912 | -0.22888 | 123.0194 | -0.10071 | -0.054931 | -0.086975 | -122.8134 | 122.9416 | 61.908 | 122.7722 | 61.9629 | 122.8271 | 0.28381 | 122.9141 | 122.9965 | 0.091552 | 122.9462 | 122.818 | 122.818 | 122.7631 | -122.9782 | -122.905 | 122.7859 | 0.036621 | 61.5646 | 62.027
1164.8281 | 123.0011 | -61.8484 | 61.0291 | -0.068054 | 0.00069854 | 0.062359 | 0.069154 | 0.0030335 | -0.0016322 | 0.00094633 | -0.088776 | 0.10071 | 0.067272 | 0.0032556 | 0.060737 | 0.10692 | -0.00036747 | -0.36163 | 60.965 | -61.9949 | 60.878 | -61.8027 | -62.1506 | 60.9879 | 0.15564 | 60.9741 | -61.853 | -61.8576 | 61.0474 | 60.8734 | -0.041199 | -0.14648 | -0.064087 | -0.15106 | 0.045777 | 122.8363 | -0.30212 | 122.9828 | -0.15564 | -0.004577 | -0.054932 | -122.8867 | 122.8958 | 61.8073 | 122.7219 | 61.8118 | 122.7264 | 0.19226 | 122.8729 | 122.9004 | -0.004578 | 122.9599 | 122.8271 | 122.8134 | 122.8226 | -123.024 | -122.8821 | 122.7264 | -0.009155 | 61.4868 | 62.0041
1165.8906 | 123.056 | -61.7981 | 61.0519 | -0.007019 | 0.00091214 | 0.063213 | 0.068513 | 0.0011109 | -0.0048364 | 0.00073273 | -0.076569 | 0.10114 | 0.069408 | -0.0080664 | 0.061165 | 0.10607 | -0.0014355 | -0.24719 | 60.9879 | -61.9446 | 60.9833 | -61.6425 | -62.0178 | 61.0794 | 0.37537 | 60.9695 | -61.8256 | -61.7661 | 61.1526 | 60.9833 | 0.091553 | -0.14648 | -0.064087 | -0.068665 | 0.15564 | 122.8775 | -0.21973 | 123.024 | -0.073242 | -0.027466 | -0.082398 | -122.818 | 122.9507 | 61.8896 | 122.7814 | 61.9171 | 122.8088 | 0.30212 | 122.9279 | 122.9782 | 0.05951 | 122.9324 | 122.7951 | 122.7859 | 122.7676 | -122.9965 | -122.8775 | 122.7814 | 0.032044 | 61.5509 | 62.1735
1166.8281 | 123.1476 | -61.8668 | 61.0382 | -0.045166 | 0.0028347 | 0.063427 | 0.0683 | 0.0043151 | -0.0024866 | -0.00097627 | -0.088776 | 0.10114 | 0.066204 | 0.0015466 | 0.059242 | 0.10863 | 0.00070073 | -0.35706 | 60.9879 | -61.9812 | 60.8688 | -61.8118 | -62.1597 | 60.9787 | 0.17395 | 60.9512 | -61.8759 | -61.8576 | 60.965 | 60.5759 | -0.31586 | -0.11444 | -0.050354 | -0.16937 | 0.054931 | 122.8455 | -0.29297 | 122.9599 | -0.17853 | -0.009156 | -0.086975 | -122.8958 | 122.8317 | 61.5509 | 122.4426 | 61.5601 | 122.4518 | 0.16937 | 122.85 | 122.8409 | 0.018311 | 122.9691 | 122.8271 | 122.8546 | 122.818 | -123.0194 | -122.9141 | 122.7356 | 0.009155 | 61.5097 | 62.0407
1167.8906 | 123.056 | -61.7981 | 61.0428 | -0.060425 | 0.00048494 | 0.06065 | 0.066591 | 0.0021789 | -0.0027002 | 0.00073273 | -0.082672 | 0.099006 | 0.068981 | 0.0041102 | 0.059883 | 0.10393 | 0.00070073 | -0.27924 | 61.0107 | -61.9583 | 60.9512 | -61.7111 | -62.027 | 61.0748 | 0.3067 | 60.997 | -61.8256 | -61.7981 | 61.1618 | 60.9741 | 0.10986 | -0.16022 | -0.032044 | -0.091553 | 0.086975 | 122.8729 | -0.22888 | 123.0331 | -0.068665 | -0.027466 | -0.045777 | -122.8409 | 122.9599 | 61.908 | 122.7722 | 61.9354 | 122.7997 | 0.24719 | 122.9095 | 122.9874 | 0.027466 | 122.9691 | 122.8226 | 122.8088 | 122.7951 | -123.0011 | -122.8683 | 122.7493 | 0 | 61.5189 | 62.1048
1168.8281 | 123.1247 | -61.8027 | 60.9833 | -0.17487 | 0.0024075 | 0.063 | 0.066591 | 0.0026063 | -0.0016322 | -0.0020443 | -0.042999 | 0.099433 | 0.067486 | -0.0046484 | 0.059883 | 0.10521 | -0.0029309 | -0.32959 | 60.9604 | -61.9583 | 60.9741 | -61.6562 | -62.0178 | 61.0657 | 0.28839 | 60.8826 | -61.8393 | -61.7477 | 61.1664 | 60.9833 | 0.027466 | -0.15564 | -0.022888 | -0.009155 | 0.14648 | 122.8683 | -0.21515 | 123.024 | -0.059509 | -0.036621 | -0.10071 | -122.731 | 122.9691 | 61.8301 | 122.7859 | 61.8668 | 122.8226 | 0.30212 | 122.9324 | 123.0057 | 0.091552 | 122.9187 | 122.7219 | 122.7631 | 122.6852 | -122.9416 | -122.8226 | 122.7768 | 0.054931 | 61.4731 | 62.0911
1169.8906 | 123.0423 | -61.7981 | 61.084 | -0.060425 | 0.00069854 | 0.061504 | 0.070222 | 0.00068369 | -0.0046228 | -0.00033547 | -0.067413 | 0.10029 | 0.068554 | -0.0033666 | 0.060524 | 0.10564 | 0.0019823 | -0.34332 | 61.0107 | -61.908 | 60.9009 | -61.7706 | -62.0041 | 61.0382 | 0.31586 | 60.9833 | -61.8118 | -61.8073 | 61.1069 | 60.9604 | 0.091553 | -0.10986 | -0.073242 | -0.1831 | 0.027466 | 122.8363 | -0.20599 | 122.9462 | -0.09613 | -0.013733 | -0.10071 | -122.8912 | 122.905 | 61.8896 | 122.7585 | 61.9034 | 122.7722 | 0.13733 | 122.8088 | 122.9187 | 0.004578 | 122.9187 | 122.7951 | 122.8088 | 122.7814 | -122.9919 | -122.8958 | 122.699 | -0.009155 | 61.4548 | 62.114
1170.8281 | 123.0469 | -61.8118 | 61.0382 | -0.068054 | 0.0011257 | 0.062572 | 0.069154 | 0.0017517 | -0.0012048 | -0.0018307 | -0.097931 | 0.098792 | 0.067272 | -0.002085 | 0.060737 | 0.10778 | -0.0012219 | -0.24719 | 60.9741 | -61.9263 | 60.9924 | -61.6653 | -62.0316 | 61.0703 | 0.34332 | 60.9467 | -61.8118 | -61.8301 | 61.203 | 60.9604 | 0.068665 | -0.11444 | -0.064087 | -0.045776 | 0.14649 | 122.8821 | -0.21973 | 122.9965 | -0.10528 | 0 | -0.091553 | -122.8683 | 123.0148 | 61.8805 | 122.7722 | 61.8805 | 122.7722 | 0.26093 | 122.9187 | 123.0148 | -0.01831 | 122.9004 | 122.7585 | 122.7859 | 122.7585 | -122.9645 | -122.85 | 122.8043 | -0.01831 | 61.5646 | 62.1552
1171.8906 | 123.1705 | -61.7615 | 61.0153 | -0.12146 | 0.00048494 | 0.060863 | 0.067445 | -0.00059811 | -0.0016322 | -0.00097627 | 0.024139 | 0.099433 | 0.067486 | -0.0033666 | 0.058601 | 0.10585 | 0.0013415 | -0.23346 | 60.9604 | -61.9217 | 61.0565 | -61.5326 | -61.9125 | 61.1618 | 0.46234 | 60.9146 | -61.7752 | -61.6882 | 61.2946 | 61.084 | 0.14191 | -0.16022 | -0.054932 | 0.041199 | 0.22888 | 122.9233 | -0.15106 | 123.0835 | 0.009155 | -0.013733 | -0.10071 | -122.7036 | 123.056 | 61.9034 | 122.8455 | 61.9171 | 122.8592 | 0.3891 | 122.9782 | 123.0698 | 0.086976 | 122.8821 | 122.6898 | 122.7219 | 122.6761 | -122.937 | -122.7905 | 122.818 | 0.073243 | 61.528 | 62.2238
1172.8281 | 123.0194 | -61.8439 | 61.0336 | -0.090943 | 0.0039029 | 0.062786 | 0.068941 | 0.0028199 | 0.00071784 | -0.0011899 | -0.11014 | 0.10029 | 0.067058 | -0.003153 | 0.059883 | 0.10585 | 0.0024097 | -0.27466 | 60.9833 | -61.9537 | 60.9604 | -61.6837 | -62.0773 | 61.0291 | 0.27924 | 60.9695 | -61.8347 | -61.821 | 61.0748 | 60.8917 | -0.004578 | -0.10986 | -0.050354 | -0.073242 | 0.16022 | 122.8729 | -0.23346 | 122.9828 | -0.1236 | 0.009155 | -0.064087 | -122.8546 | 122.9187 | 61.8393 | 122.7356 | 61.8301 | 122.7264 | 0.27008 | 122.9141 | 122.9095 | 0.013733 | 122.937 | 122.8043 | 122.8271 | 122.8134 | -122.9874 | -122.8683 | 122.8043 | 0.022888 | 61.5692 | 62.1231
1173.8906 | 123.1567 | -61.7615 | 61.0062 | -0.090943 | 0.0017667 | 0.061504 | 0.068513 | -0.0012391 | -0.00077756 | -0.0022581 | 0.0088807 | 0.098792 | 0.06599 | 0.004751 | 0.060096 | 0.10543 | 0.0060413 | -0.26093 | 60.9741 | -61.9034 | 61.0336 | -61.6104 | -61.9675 | 61.1389 | 0.37079 | 60.9512 | -61.8027 | -61.7203 | 61.235 | 61.0565 | 0.15564 | -0.14191 | -0.032044 | 0.027465 | 0.15106 | 122.9004 | -0.20599 | 123.0423 | -0.064087 | -0.041198 | -0.054932 | -122.7264 | 122.9965 | 61.9171 | 122.818 | 61.9583 | 122.8592 | 0.29297 | 122.937 | 123.0377 | 0.082397 | 122.8775 | 122.7539 | 122.7356 | 122.7127 | -122.9095 | -122.8088 | 122.7951 | 0.041199 | 61.5005 | 62.1323
1174.8281 | 123.0652 | -61.8027 | 61.0474 | -0.12146 | 0.0032619 | 0.060863 | 0.07364 | 0.0023925 | -0.0014184 | 0.00030553 | -0.10098 | 0.098578 | 0.066845 | 0.00069215 | 0.058601 | 0.10692 | -0.0031445 | -0.27008 | 60.9787 | -61.9446 | 61.0062 | -61.6837 | -62.0087 | 61.0657 | 0.33417 | 60.9604 | -61.8347 | -61.8118 | 61.1298 | 60.9375 | 0.050354 | -0.14191 | -0.068664 | -0.041198 | 0.11902 | 122.8683 | -0.20599 | 123.0103 | -0.064087 | -0.032044 | -0.086975 | -122.8592 | 122.9324 | 61.853 | 122.7402 | 61.8851 | 122.7722 | 0.26093 | 122.9507 | 122.9645 | 0.022888 | 122.9233 | 122.7951 | 122.7814 | 122.7631 | -122.9919 | -122.8821 | 122.8088 | -0.009156 | 61.5326 | 62.1368
1175.8281 | 123.0331 | -61.8393 | 61.0291 | -0.022278 | 0.00069854 | 0.062359 | 0.067445 | 0.0015381 | 0.0019994 | -0.0024717 | -0.085724 | 0.099219 | 0.065349 | -0.0025122 | 0.060737 | 0.10585 | 5.9726e-05 | -0.27924 | 60.9787 | -61.9537 | 60.9604 | -61.6928 | -62.0636 | 61.0428 | 0.27924 | 60.9924 | -61.853 | -61.821 | 61.0886 | 60.9009 | 0 | -0.11444 | -0.050354 | -0.068665 | 0.14648 | 122.8821 | -0.22431 | 122.9965 | -0.10986 | -0.013733 | -0.036621 | -122.85 | 122.9279 | 61.8393 | 122.7402 | 61.853 | 122.7539 | 0.26093 | 122.9141 | 122.9416 | 0.032043 | 122.9324 | 122.8455 | 122.818 | 122.8317 | -122.9828 | -122.8821 | 122.7997 | 0.01831 | 61.5601 | 62.1185
1176.8281 | 123.056 | -61.7981 | 61.0291 | -0.068054 | 0.00091214 | 0.061504 | 0.067872 | 0.0023925 | -0.0027002 | -0.0026853 | -0.06131 | 0.098578 | 0.068554 | -0.003794 | 0.059028 | 0.10692 | 0.0032641 | -0.25177 | 61.0245 | -61.9217 | 60.9558 | -61.6837 | -62.027 | 61.084 | 0.35248 | 60.9879 | -61.8301 | -61.7798 | 61.1572 | 60.9695 | 0.10071 | -0.1236 | -0.004578 | -0.073242 | 0.11444 | 122.8821 | -0.22888 | 123.0057 | -0.10529 | -0.032043 | -0.041199 | -122.8088 | 122.9553 | 61.8988 | 122.7676 | 61.9308 | 122.7997 | 0.23804 | 122.8775 | 122.9874 | 0.050354 | 122.9462 | 122.818 | 122.8226 | 122.7859 | -122.9507 | -122.8592 | 122.7539 | 0.018311 | 61.5463 | 62.1506
1177.8906 | 123.0652 | -61.8027 | 60.997 | -0.1062 | 0.0019803 | 0.062572 | 0.068086 | -0.0035889 | -0.00035036 | -0.0037533 | -0.0063781 | 0.099433 | 0.064709 | -0.0042212 | 0.060951 | 0.10607 | -0.0050671 | -0.3067 | 60.9512 | -61.908 | 60.965 | -61.6562 | -62.0224 | 61.0794 | 0.28839 | 60.9375 | -61.7432 | -61.7844 | 61.1572 | 60.9787 | 0.032043 | -0.10529 | -0.045776 | -0.032043 | 0.14648 | 122.8821 | -0.21973 | 122.9874 | -0.11444 | 0.059509 | -0.059509 | -122.7814 | 122.9599 | 61.8347 | 122.7814 | 61.7752 | 122.7219 | 0.25177 | 122.8729 | 122.9004 | -0.041199 | 122.8592 | 122.6807 | 122.7539 | 122.7402 | -122.905 | -122.7402 | 122.7676 | 0.01831 | 61.496 | 62.0911
1178.8281 | 123.0606 | -61.8073 | 61.0382 | -0.022278 | 0.00048494 | 0.062359 | 0.069154 | 0.0021789 | -0.0024866 | -0.0039671 | -0.088776 | 0.10071 | 0.067486 | -0.0035802 | 0.059028 | 0.10521 | -0.00015387 | -0.23804 | 60.9879 | -61.9354 | 60.9787 | -61.6882 | -62.0087 | 61.0794 | 0.3479 | 60.9741 | -61.8027 | -61.7798 | 61.1526 | 60.965 | 0.10071 | -0.12817 | -0.050354 | -0.059509 | 0.11902 | 122.8867 | -0.20142 | 123.0148 | -0.073242 | 0.004578 | -0.064087 | -122.818 | 122.9599 | 61.908 | 122.7722 | 61.9034 | 122.7676 | 0.24719 | 122.9141 | 122.9553 | 0.022888 | 122.9233 | 122.7768 | 122.7951 | 122.7814 | -122.9736 | -122.8409 | 122.7859 | 0.027466 | 61.5692 | 62.1552
1179.8906 | 123.0927 | -61.8027 | 60.997 | -0.13672 | 0.0036893 | 0.062359 | 0.067659 | -0.0023071 | -0.00035036 | -0.0016171 | -0.0033265 | 0.098365 | 0.065563 | 0.001333 | 0.059669 | 0.10607 | -0.0012219 | -0.32959 | 60.9192 | -61.9308 | 60.9741 | -61.6745 | -62.0407 | 61.084 | 0.27466 | 60.9329 | -61.8256 | -61.7889 | 61.1389 | 60.9604 | 0 | -0.12817 | -0.07782 | -0.022888 | 0.12817 | 122.8867 | -0.23804 | 123.0148 | -0.10986 | -0.022889 | -0.064087 | -122.7859 | 122.9416 | 61.8027 | 122.7631 | 61.8256 | 122.7859 | 0.25635 | 122.905 | 122.9645 | 0.036622 | 122.85 | 122.7585 | 122.7219 | 122.7356 | -122.9279 | -122.8226 | 122.7768 | 0.013733 | 61.4731 | 62.0773
1180.8281 | 123.0469 | -61.8073 | 61.0474 | -0.037537 | 5.7742e-05 | 0.062145 | 0.067872 | 0.0019653 | -0.00013676 | -0.00054907 | -0.07962 | 0.099219 | 0.067272 | -0.0016576 | 0.059456 | 0.10671 | -0.00036747 | -0.23346 | 60.9833 | -61.9629 | 60.997 | -61.6653 | -61.9949 | 61.116 | 0.35248 | 61.0062 | -61.821 | -61.7752 | 61.1572 | 60.9695 | 0.11444 | -0.15564 | -0.064087 | -0.050354 | 0.14191 | 122.9233 | -0.18768 | 123.0789 | -0.032043 | -0.013733 | -0.041198 | -122.8226 | 122.9645 | 61.9217 | 122.7768 | 61.9354 | 122.7905 | 0.29755 | 122.9599 | 122.9782 | 0.045776 | 122.9462 | 122.8271 | 122.7905 | 122.8134 | -123.0103 | -122.8683 | 122.8043 | 0.032043 | 61.5738 | 62.1597
1181.8906 | 123.0881 | -61.7981 | 60.997 | -0.045166 | 0.0034757 | 0.061504 | 0.070863 | -0.0033753 | 0.0013586 | -0.00097627 | -0.0063781 | 0.098578 | 0.066631 | -0.0046484 | 0.058815 | 0.10479 | 0.00027333 | -0.28839 | 60.9512 | -61.9217 | 61.0016 | -61.6791 | -62.0087 | 61.0931 | 0.31586 | 60.9421 | -61.7981 | -61.7569 | 61.1801 | 60.9924 | 0.068665 | -0.1236 | -0.045776 | 0.004578 | 0.11902 | 122.8912 | -0.21057 | 123.0148 | -0.086975 | 0 | -0.054931 | -122.7539 | 122.9782 | 61.8668 | 122.7905 | 61.8668 | 122.7905 | 0.24262 | 122.9233 | 122.9782 | 0.041199 | 122.8729 | 122.7402 | 122.7493 | 122.7402 | -122.9187 | -122.7951 | 122.7997 | 0.041199 | 61.5097 | 62.114
1182.8281 | 123.056 | -61.8073 | 61.0519 | -0.090943 | 0.0028347 | 0.062359 | 0.069154 | -0.00038451 | -0.0020594 | -0.00076267 | -0.07962 | 0.09986 | 0.067058 | 0.0038966 | 0.059456 | 0.10415 | -0.0048535 | -0.25635 | 61.0199 | -61.9354 | 60.9604 | -61.7111 | -62.0316 | 61.0565 | 0.32044 | 60.9879 | -61.8164 | -61.7935 | 61.1343 | 60.9604 | 0.10986 | -0.12817 | -0.032044 | -0.091553 | 0.09613 | 122.8638 | -0.2243 | 122.9919 | -0.09613 | -0.009155 | -0.064087 | -122.8455 | 122.9416 | 61.9171 | 122.7676 | 61.9263 | 122.7768 | 0.2243 | 122.8958 | 122.9507 | 0.022888 | 122.9553 | 122.8043 | 122.8271 | 122.7951 | -122.9874 | -122.8683 | 122.7676 | 0.013733 | 61.5509 | 62.1277
1183.8281 | 123.0743 | -61.7935 | 61.0428 | -0.083313 | 0.0011257 | 0.060863 | 0.070649 | 4.2692e-05 | -0.002273 | 0.00030553 | -0.085724 | 0.1005 | 0.068981 | -0.0055028 | 0.059883 | 0.10286 | -0.0012219 | -0.27008 | 60.9924 | -61.94 | 60.9329 | -61.7065 | -62.0316 | 61.0611 | 0.32044 | 60.9924 | -61.8164 | -61.7981 | 61.1435 | 60.9558 | 0.10529 | -0.14648 | -0.050354 | -0.10986 | 0.086975 | 122.8546 | -0.23804 | 123.0011 | -0.091553 | -0.022888 | -0.050354 | -122.8409 | 122.937 | 61.8988 | 122.7493 | 61.9217 | 122.7722 | 0.23346 | 122.8729 | 122.9599 | 0.01831 | 122.9324 | 122.8088 | 122.7859 | 122.7859 | -122.9828 | -122.8592 | 122.7264 | -0.004578 | 61.5234 | 62.114
1184.8281 | 122.9965 | -61.8256 | 61.0703 | -0.022278 | 0.0017667 | 0.062145 | 0.066591 | -0.0029479 | -0.002273 | -0.0022581 | -0.027741 | 0.102 | 0.067058 | -0.0046484 | 0.061165 | 0.10479 | 0.0017687 | -0.2243 | 61.0291 | -61.9217 | 60.9467 | -61.6974 | -62.0316 | 61.0703 | 0.32044 | 61.0107 | -61.8439 | -61.8393 | 61.1206 | 60.9467 | 0.082397 | -0.09613 | -0.041198 | -0.1236 | 0.12817 | 122.8958 | -0.20599 | 122.9919 | -0.10986 | -0.01831 | -0.059509 | -122.9095 | 122.9462 | 61.908 | 122.7722 | 61.9263 | 122.7905 | 0.2243 | 122.8683 | 122.9645 | 0.004578 | 122.9507 | 122.8546 | 122.8546 | 122.8363 | -122.9919 | -122.9141 | 122.7722 | -0.013732 | 61.6013 | 62.146
1185.8906 | 123.0789 | -61.8073 | 61.0199 | -0.1062 | 0.00069854 | 0.062145 | 0.067445 | 0.00068369 | -0.0014184 | -0.0014035 | 0.0088807 | 0.098578 | 0.068554 | -0.0025122 | 0.059242 | 0.10457 | -0.00036747 | -0.3067 | 60.9467 | -61.94 | 60.9787 | -61.6745 | -62.0132 | 61.0977 | 0.29755 | 60.9329 | -61.8164 | -61.7981 | 61.1618 | 60.997 | 0.041199 | -0.13275 | -0.073242 | -0.041198 | 0.13275 | 122.905 | -0.20599 | 123.0377 | -0.073243 | -0.009155 | -0.086975 | -122.818 | 122.9691 | 61.8484 | 122.8043 | 61.8576 | 122.8134 | 0.2655 | 122.9187 | 122.9782 | 0.01831 | 122.8867 | 122.7493 | 122.7539 | 122.7402 | -122.9599 | -122.8363 | 122.7859 | 0.009155 | 61.5005 | 62.1048
1186.8281 | 123.0423 | -61.7706 | 61.0336 | -0.075684 | 0.00069854 | 0.061932 | 0.068513 | 0.0045289 | -0.0020594 | 0.00030553 | -0.10098 | 0.10178 | 0.066204 | -0.0033666 | 0.057747 | 0.10842 | -0.0014355 | -0.21973 | 61.0016 | -61.9583 | 60.9924 | -61.6562 | -62.027 | 61.0794 | 0.37537 | 60.9787 | -61.8164 | -61.7798 | 61.1572 | 60.9604 | 0.086975 | -0.18768 | -0.032043 | -0.041198 | 0.11444 | 122.85 | -0.25635 | 123.0377 | -0.068665 | -0.045776 | -0.054931 | -122.8134 | 122.9279 | 61.8576 | 122.731 | 61.9034 | 122.7768 | 0.30212 | 122.9507 | 122.9736 | 0.036621 | 122.9599 | 122.7951 | 122.7722 | 122.7493 | -122.9919 | -122.85 | 122.7631 | -0.009155 | 61.5509 | 62.146
1187.8906 | 123.111 | -61.8073 | 61.0062 | -0.1062 | 0.0051845 | 0.059582 | 0.066163 | -0.00081171 | -0.0014184 | -0.0016171 | -0.018585 | 0.099219 | 0.066418 | -0.0027258 | 0.058815 | 0.10436 | 0.0013415 | -0.20599 | 60.9924 | -61.8988 | 60.9924 | -61.6562 | -62.0132 | 61.1069 | 0.31586 | 60.9329 | -61.7935 | -61.7615 | 61.1755 | 61.0062 | 0.068665 | -0.091553 | -0.013733 | -0.013733 | 0.15106 | 122.9141 | -0.20599 | 123.0057 | -0.11444 | 0.013733 | -0.073243 | -122.7676 | 122.9828 | 61.8759 | 122.8134 | 61.8622 | 122.7997 | 0.24262 | 122.8912 | 122.9691 | 0.032043 | 122.8912 | 122.7264 | 122.7997 | 122.7402 | -122.905 | -122.7997 | 122.7997 | 0.045776 | 61.6013 | 62.1231
1188.8281 | 123.0515 | -61.8027 | 61.0428 | -0.068054 | 0.0034757 | 0.063213 | 0.070649 | 0.0038879 | -0.00099116 | -0.0011899 | -0.11319 | 0.10093 | 0.06599 | -0.0012304 | 0.058815 | 0.10735 | -0.00036747 | -0.23346 | 60.965 | -61.9583 | 60.9879 | -61.6562 | -62.0316 | 61.0794 | 0.37537 | 60.9695 | -61.821 | -61.7844 | 61.1435 | 60.9558 | 0.086975 | -0.15564 | -0.07782 | -0.054932 | 0.14648 | 122.8821 | -0.22888 | 123.0377 | -0.073242 | -0.018311 | -0.073243 | -122.8271 | 122.9462 | 61.8896 | 122.7585 | 61.908 | 122.7768 | 0.30212 | 122.9462 | 122.9645 | 0.036621 | 122.9233 | 122.7905 | 122.7676 | 122.7722 | -123.0011 | -122.8638 | 122.7905 | 0.01831 | 61.5692 | 62.178
1189.8906 | 123.1018 | -61.7935 | 60.997 | -0.11383 | 0.0015529 | 0.062145 | 0.067445 | 0.0021789 | -0.00077756 | -0.0028989 | -0.036896 | 0.09687 | 0.065563 | -0.00037605 | 0.059669 | 0.10415 | 0.00091433 | -0.33417 | 60.9375 | -61.9217 | 60.965 | -61.6562 | -62.0453 | 61.0794 | 0.27924 | 60.9146 | -61.8484 | -61.7844 | 61.1435 | 60.9787 | 0.018311 | -0.12817 | -0.059509 | -0.032043 | 0.13733 | 122.8729 | -0.25177 | 123.0011 | -0.1236 | -0.054932 | -0.082397 | -122.7814 | 122.937 | 61.8118 | 122.7722 | 61.8668 | 122.8271 | 0.2655 | 122.8867 | 122.9919 | 0.064087 | 122.8592 | 122.7631 | 122.731 | 122.7081 | -122.9187 | -122.8455 | 122.7585 | 0.009155 | 61.4594 | 62.0728
1190.8281 | 123.0194 | -61.8073 | 61.0794 | -0.12909 | 0.00048494 | 0.062572 | 0.067232 | 4.2692e-05 | -0.0018458 | -0.0018307 | -0.039948 | 0.10093 | 0.067913 | -0.0040076 | 0.059028 | 0.10457 | -0.00079467 | -0.2243 | 60.9833 | -61.9125 | 60.9924 | -61.6333 | -61.9949 | 61.1023 | 0.35706 | 60.9741 | -61.8256 | -61.8027 | 61.1206 | 60.9467 | 0.068665 | -0.10529 | -0.096131 | -0.086975 | 0.17395 | 122.9095 | -0.18768 | 123.0148 | -0.082397 | -0.018311 | -0.10529 | -122.8821 | 122.9279 | 61.8759 | 122.7539 | 61.8942 | 122.7722 | 0.27924 | 122.905 | 122.9462 | 0.022889 | 122.8958 | 122.7997 | 122.7905 | 122.7814 | -122.9919 | -122.905 | 122.7997 | 0.004578 | 61.5829 | 62.1643
1191.8906 | 123.1338 | -61.7798 | 61.0153 | -0.068054 | 5.7742e-05 | 0.061504 | 0.0683 | 0.0015381 | -0.0016322 | -0.0016171 | -0.046051 | 0.098578 | 0.066631 | 0.00090575 | 0.059456 | 0.10671 | -0.0012219 | -0.30212 | 60.9787 | -61.9583 | 60.9924 | -61.6699 | -62.0132 | 61.0886 | 0.32501 | 60.9329 | -61.8256 | -61.7432 | 61.1801 | 61.0336 | 0.086975 | -0.17853 | -0.036621 | -0.022888 | 0.10986 | 122.8683 | -0.23346 | 123.0469 | -0.054932 | -0.045777 | -0.082398 | -122.7585 | 122.9599 | 61.8668 | 122.8134 | 61.9125 | 122.8592 | 0.28839 | 122.9507 | 123.0057 | 0.082398 | 122.937 | 122.7585 | 122.7585 | 122.7127 | -122.9736 | -122.8409 | 122.7722 | 0.036621 | 61.4777 | 62.1048
1192.8281 | 123.0194 | -61.7981 | 61.0611 | 0.00824 | -0.00036966 | 0.061932 | 0.069154 | -0.0018799 | -0.0041956 | -0.0048215 | -0.082672 | 0.099647 | 0.067486 | 0.0011194 | 0.058174 | 0.10564 | -0.0039991 | -0.43488 | 61.0107 | -61.9354 | 60.9329 | -61.7294 | -62.0178 | 61.0611 | 0.32501 | 61.0062 | -61.821 | -61.8301 | 61.1114 | 60.9558 | 0.068665 | -0.13733 | -0.050354 | -0.12817 | 0.068665 | 122.8592 | -0.21973 | 122.9965 | -0.082397 | -0.022888 | -0.054931 | -122.8912 | 122.9095 | 61.8668 | 122.7539 | 61.8896 | 122.7768 | 0.20599 | 122.8683 | 122.9324 | -0.009155 | 122.9462 | 122.8271 | 122.8088 | 122.8043 | -122.9965 | -122.8821 | 122.731 | -0.032043 | 61.3632 | 62.1231
1193.9062 | 123.0011 | -61.8347 | 61.0474 | -0.075684 | 0.0017667 | 0.062145 | 0.070009 | 0.0053833 | -0.00099116 | -0.00033547 | -0.14676 | 0.098578 | 0.067272 | 0.0032556 | 0.059456 | 0.10756 | 0.0019823 | -0.32959 | 60.9833 | -61.9812 | 60.9055 | -61.7615 | -62.0956 | 60.9924 | 0.19684 | 60.9787 | -61.8439 | -61.8484 | 61.0519 | 60.8505 | -0.054932 | -0.14648 | -0.064087 | -0.14191 | 0.073242 | 122.8271 | -0.26093 | 122.9736 | -0.11444 | -0.009155 | -0.068664 | -122.8958 | 122.8867 | 61.7798 | 122.6852 | 61.7889 | 122.6944 | 0.21973 | 122.8867 | 122.8958 | -0.004578 | 122.9645 | 122.8226 | 122.818 | 122.8134 | -123.0286 | -122.8912 | 122.7402 | -0.013733 | 61.5051 | 62.0316
1194.8281 | 123.056 | -61.8164 | 61.0336 | -0.075684 | 0.0011257 | 0.061718 | 0.069795 | 0.00089729 | -0.00056396 | 0.00094633 | -0.10709 | 0.098792 | 0.067699 | -0.0018712 | 0.056892 | 0.10714 | -0.0012219 | -0.24261 | 60.9833 | -61.9125 | 60.9924 | -61.6608 | -62.0087 | 61.0794 | 0.36621 | 60.9695 | -61.8347 | -61.7752 | 61.1618 | 60.9421 | 0.10071 | -0.096131 | -0.050354 | -0.041198 | 0.15564 | 122.8958 | -0.19226 | 122.9919 | -0.09613 | -0.018311 | -0.064087 | -122.8088 | 122.9782 | 61.9171 | 122.7585 | 61.9354 | 122.7768 | 0.25177 | 122.905 | 122.9965 | 0.059509 | 122.8958 | 122.8043 | 122.7997 | 122.7859 | -122.9462 | -122.8683 | 122.8088 | 0.041198 | 61.5738 | 62.1826
1195.8906 | 123.1018 | -61.7752 | 61.0153 | -0.045166 | 0.00027134 | 0.061504 | 0.065736 | -0.0055115 | -0.0020594 | -0.0035397 | -0.0094299 | 0.099647 | 0.067058 | -0.0052892 | 0.060951 | 0.10564 | -0.0029309 | -0.27008 | 60.9558 | -61.9125 | 60.9741 | -61.6379 | -62.0087 | 61.116 | 0.34332 | 60.9421 | -61.8301 | -61.7569 | 61.1938 | 61.0199 | 0.07782 | -0.13733 | -0.059509 | -0.041199 | 0.13733 | 122.8912 | -0.23346 | 123.0286 | -0.09613 | -0.054931 | -0.073242 | -122.7722 | 122.9691 | 61.853 | 122.7951 | 61.908 | 122.85 | 0.27466 | 122.8867 | 123.024 | 0.073242 | 122.8683 | 122.7722 | 122.731 | 122.7173 | -122.9279 | -122.8455 | 122.7493 | 0.018311 | 61.5051 | 62.1185
1196.8281 | 123.0423 | -61.7981 | 61.0657 | -0.007019 | 0.00091214 | 0.060863 | 0.069368 | 0.0041015 | -0.0018458 | -0.0061033 | -0.07962 | 0.10093 | 0.066845 | -0.003153 | 0.060951 | 0.105 | -0.0018629 | -0.27466 | 61.0016 | -61.9583 | 60.9421 | -61.7065 | -62.0499 | 61.0428 | 0.33875 | 60.9833 | -61.821 | -61.8164 | 61.1298 | 60.9558 | 0.09613 | -0.16022 | -0.064087 | -0.1236 | 0.091553 | 122.8409 | -0.25177 | 123.0011 | -0.091553 | -0.022888 | -0.082398 | -122.8821 | 122.9279 | 61.8942 | 122.7539 | 61.9171 | 122.7768 | 0.25177 | 122.9004 | 122.9507 | 0.004578 | 122.9599 | 122.8043 | 122.7997 | 122.7814 | -123.024 | -122.8867 | 122.7402 | -0.01831 | 61.5234 | 62.1368
1197.8906 | 123.0972 | -61.8073 | 61.0153 | -0.075684 | 0.0019803 | 0.063213 | 0.067659 | 0.0023925 | -0.0044092 | -0.0016171 | -0.024689 | 0.098578 | 0.066631 | 0.004751 | 0.060737 | 0.105 | 0.0015551 | -0.32501 | 60.9192 | -61.9354 | 60.9833 | -61.6745 | -62.0316 | 61.0794 | 0.29297 | 60.9375 | -61.8347 | -61.7889 | 61.1389 | 60.9695 | 0.022888 | -0.12817 | -0.096131 | -0.032044 | 0.13275 | 122.8867 | -0.2243 | 123.0148 | -0.09613 | -0.027466 | -0.07782 | -122.8043 | 122.9462 | 61.8301 | 122.7768 | 61.8576 | 122.8043 | 0.26093 | 122.9187 | 122.9736 | 0.045777 | 122.8546 | 122.7722 | 122.7264 | 122.7448 | -122.9507 | -122.85 | 122.7905 | 0.018311 | 61.4822 | 62.1002
1198.8438 | 123.111 | -61.7981 | 60.9741 | -0.075684 | 0.0021939 | 0.062145 | 0.067018 | 0.00068369 | -0.00077756 | 0.00094633 | -0.14371 | 0.10071 | 0.062572 | -0.0074254 | 0.057533 | 0.10735 | -0.00036747 | -0.28839 | 60.9192 | -61.9263 | 61.0199 | -61.6196 | -62.0087 | 61.1069 | 0.44403 | 60.9009 | -61.8073 | -61.7477 | 61.2396 | 60.9741 | 0 | -0.12817 | -0.054932 | 0.045776 | 0.17853 | 122.905 | -0.21057 | 123.0331 | -0.082397 | -0.009155 | -0.073242 | -122.7219 | 123.0377 | 61.7981 | 122.7722 | 61.8073 | 122.7814 | 0.3067 | 122.9462 | 123.0469 | 0.059509 | 122.8455 | 122.7081 | 122.7173 | 122.699 | -122.9004 | -122.7814 | 122.818 | 0.050354 | 61.5097 | 62.2421
1199.8906 | 123.1247 | -61.7798 | 60.9741 | -0.16724 | 0.0026211 | 0.061718 | 0.067872 | 0.0028199 | -0.00077756 | -0.0011899 | -0.085724 | 0.098792 | 0.06364 | -0.0012304 | 0.058601 | 0.10457 | -0.00015387 | -0.27008 | 60.9146 | -61.9354 | 61.0199 | -61.6241 | -61.9995 | 61.0977 | 0.33875 | 60.9055 | -61.8393 | -61.6196 | 61.1298 | 61.0291 | 0.073242 | -0.15564 | -0.059509 | 0.045776 | 0.15564 | 122.8775 | -0.21973 | 123.0331 | -0.064087 | -0.059509 | -0.068664 | -122.5937 | 122.9095 | 61.853 | 122.8088 | 61.9125 | 122.8683 | 0.31128 | 122.9553 | 122.9691 | 0.21973 | 122.85 | 122.7448 | 122.6944 | 122.6852 | -122.9095 | -122.8134 | 122.7997 | 0.16022 | 61.5097 | 62.1185
1200.8281 | 123.0057 | -61.7981 | 61.0474 | -0.068054 | 0.0028347 | 0.061504 | 0.068727 | 0.0017517 | -0.0037684 | 0.00051913 | -0.046051 | 0.10007 | 0.064281 | 0.0011194 | 0.058601 | 0.10564 | -0.0035719 | -0.27008 | 61.0107 | -61.9308 | 60.9283 | -61.702 | -62.0911 | 61.2396 | 0.20599 | 61.0062 | -61.8439 | -61.8439 | 61.1298 | 60.965 | 0.073242 | -0.13275 | -0.036621 | -0.11902 | 0.096131 | 123.0377 | -0.29297 | 123.1705 | -0.16022 | -0.045776 | -0.041198 | -122.8912 | 122.9279 | 61.8713 | 122.7631 | 61.9171 | 122.8088 | 0.22888 | 122.8592 | 122.9736 | 0 | 122.9416 | 122.85 | 122.8088 | 122.8043 | -122.9782 | -122.8912 | 122.7264 | -0.045776 | 61.528 | 62.0041
1201.8906 | 123.0972 | -61.8027 | 60.997 | -0.083313 | 0.0019803 | 0.062572 | 0.068086 | 0.00025629 | 0.0015722 | -0.0026853 | -0.0063781 | 0.10007 | 0.066418 | -0.0040076 | 0.058387 | 0.10521 | 0.0026233 | -0.3067 | 60.9512 | -61.94 | 60.9787 | -61.6653 | -62.0178 | 61.0886 | 0.29755 | 60.9375 | -61.8301 | -61.8027 | 61.1618 | 60.9695 | 0.027466 | -0.13733 | -0.045776 | -0.01831 | 0.13733 | 122.8912 | -0.21515 | 123.0286 | -0.07782 | -0.027466 | -0.059509 | -122.7997 | 122.9645 | 61.8301 | 122.7722 | 61.8576 | 122.7997 | 0.27466 | 122.9187 | 122.9919 | 0.027466 | 122.8912 | 122.7676 | 122.7539 | 122.7402 | -122.937 | -122.8271 | 122.7814 | 0 | 61.496 | 62.1002
1202.8281 | 123.0469 | -61.8027 | 61.0474 | -0.014649 | 0.0017667 | 0.061291 | 0.069154 | 0.00068369 | -0.0031274 | 0.00094633 | -0.073517 | 0.10157 | 0.065777 | -0.0010168 | 0.059456 | 0.105 | -0.0033581 | -0.26093 | 61.0016 | -61.9446 | 60.9558 | -61.7065 | -62.0499 | 61.0703 | 0.32044 | 61.0016 | -61.8301 | -61.7889 | 61.1435 | 60.9558 | 0.09613 | -0.14191 | -0.045776 | -0.091552 | 0.09613 | 122.8729 | -0.24719 | 123.0148 | -0.10529 | -0.027466 | -0.045776 | -122.8363 | 122.9462 | 61.8988 | 122.7585 | 61.9263 | 122.7859 | 0.23804 | 122.9004 | 122.9736 | 0.041199 | 122.9462 | 122.8317 | 122.8043 | 122.8043 | -122.9919 | -122.8775 | 122.7585 | 0.013733 | 61.5417 | 62.1231
1203.9062 | 123.0652 | -61.7935 | 61.0657 | -0.037537 | 0.00048494 | 0.061291 | 0.069154 | 0.00046989 | -0.0014184 | 0.0011599 | -0.10403 | 0.10007 | 0.066418 | -0.0018712 | 0.060524 | 0.10628 | -0.0050671 | -0.25635 | 61.0107 | -61.9354 | 60.9512 | -61.7065 | -62.0087 | 61.0703 | 0.32501 | 60.9741 | -61.7981 | -61.7752 | 61.1389 | 60.9604 | 0.10986 | -0.14191 | -0.054932 | -0.11444 | 0.086975 | 122.8638 | -0.21515 | 123.0057 | -0.073242 | -0.004578 | -0.091553 | -122.8409 | 122.9324 | 61.9034 | 122.7539 | 61.908 | 122.7585 | 0.22888 | 122.8867 | 122.937 | 0.022888 | 122.9462 | 122.7722 | 122.8043 | 122.7676 | -123.0011 | -122.8638 | 122.7448 | 0.01831 | 61.5372 | 62.1185
1204.8281 | 123.024 | -61.8027 | 61.0565 | -0.1062 | 0.0019803 | 0.062786 | 0.068727 | 0.0053833 | -0.0020594 | 0.0022281 | -0.049103 | 0.098578 | 0.065136 | -0.0063574 | 0.062446 | 0.10436 | -0.0025037 | -0.21057 | 60.965 | -61.9034 | 61.0016 | -61.6196 | -61.9675 | 61.1343 | 0.40283 | 60.9833 | -61.8347 | -61.7981 | 61.1572 | 60.9879 | 0.10986 | -0.10071 | -0.091553 | -0.054932 | 0.1831 | 122.937 | -0.16479 | 123.0377 | -0.064087 | -0.032044 | -0.073243 | -122.8546 | 122.9599 | 61.9125 | 122.7905 | 61.9446 | 122.8226 | 0.28381 | 122.905 | 122.9919 | 0.036621 | 122.8683 | 122.818 | 122.7676 | 122.7859 | -122.9599 | -122.8912 | 122.8043 | 0.004577 | 61.5921 | 62.2055
1205.8281 | 123.0377 | -61.8118 | 61.0657 | -0.029907 | 0.00027134 | 0.057445 | 0.067659 | 0.00068369 | 7.6842e-05 | 0.00073273 | -0.067413 | 0.099006 | 0.064495 | 0.0043238 | 0.059028 | 0.10692 | -0.0010083 | -0.050354 | 61.0428 | -61.908 | 60.9467 | -61.7111 | -62.0682 | 61.0703 | 0.32044 | 60.9879 | -61.821 | -61.821 | 61.1206 | 60.9467 | 0.086975 | -0.09613 | -0.022888 | -0.11902 | 0.10071 | 122.8821 | -0.25635 | 122.9782 | -0.16022 | -0.009155 | -0.07782 | -122.8867 | 122.9324 | 61.8988 | 122.7585 | 61.908 | 122.7676 | 0.19684 | 122.8546 | 122.9416 | 0 | 122.9507 | 122.8088 | 122.8546 | 122.7997 | -122.9736 | -122.8867 | 122.7585 | -0.009155 | 61.7615 | 62.1323
1206.8906 | 123.0331 | -61.8439 | 61.0336 | -0.11383 | 0.0026211 | 0.063854 | 0.067445 | 0.0030335 | -0.00056396 | 0.00030553 | -0.10098 | 0.10136 | 0.065349 | 0.004751 | 0.059883 | 0.1065 | 5.9726e-05 | -0.32501 | 60.9375 | -61.9904 | 60.9055 | -61.7432 | -62.1185 | 61.0062 | 0.22888 | 60.9421 | -61.8668 | -61.8118 | 61.0886 | 60.91 | -0.036621 | -0.14648 | -0.09613 | -0.12817 | 0.10071 | 122.85 | -0.27466 | 122.9965 | -0.12817 | -0.022888 | -0.091552 | -122.8455 | 122.9324 | 61.8073 | 122.7539 | 61.8301 | 122.7768 | 0.24719 | 122.8958 | 122.9553 | 0.054931 | 122.9279 | 122.8088 | 122.7814 | 122.7859 | -123.024 | -122.9004 | 122.7493 | 0.032043 | 61.5189 | 62.0728
1207.8281 | 123.0469 | -61.7844 | 61.0474 | -0.060425 | 0.0039029 | 0.062359 | 0.069581 | 0.0017517 | -0.0020594 | 0.00051913 | -0.12845 | 0.099647 | 0.064709 | -0.0018712 | 0.059883 | 0.10735 | 0.00027333 | -0.2243 | 60.9741 | -61.9537 | 60.965 | -61.6516 | -62.0316 | 61.084 | 0.37537 | 60.9787 | -61.821 | -61.7844 | 61.1572 | 60.9604 | 0.086975 | -0.16937 | -0.073242 | -0.082397 | 0.13275 | 122.8683 | -0.24719 | 123.0377 | -0.07782 | -0.036621 | -0.068664 | -122.8317 | 122.9416 | 61.8713 | 122.7448 | 61.908 | 122.7814 | 0.30212 | 122.9187 | 122.9782 | 0.036621 | 122.9279 | 122.7997 | 122.7585 | 122.7631 | -123.0011 | -122.8683 | 122.7493 | 0 | 61.5601 | 62.1597
1208.9062 | 123.1247 | -61.7752 | 60.965 | -0.075684 | -0.00015586 | 0.062359 | 0.066377 | 0.00068369 | -0.0018458 | -0.0022581 | -0.082672 | 0.097724 | 0.064922 | -0.0016576 | 0.060524 | 0.10479 | -0.0016493 | -0.3479 | 60.9421 | -61.9492 | 60.9695 | -61.6882 | -62.059 | 61.0748 | 0.29755 | 60.9146 | -61.8393 | -61.7523 | 61.1664 | 60.9833 | 0.013733 | -0.17395 | -0.022888 | 0.004577 | 0.086976 | 122.85 | -0.28381 | 123.024 | -0.10986 | -0.064086 | -0.050354 | -122.7173 | 122.9416 | 61.7889 | 122.7585 | 61.853 | 122.8226 | 0.26093 | 122.9187 | 123.0057 | 0.086975 | 122.8912 | 122.7539 | 122.7173 | 122.6898 | -122.9141 | -122.8043 | 122.7448 | 0.022889 | 61.4273 | 62.0728
1209.8281 | 123.024 | -61.7981 | 61.0519 | -0.037537 | 0.0015529 | 0.061077 | 0.069795 | -0.0020935 | -0.0024866 | -0.00012167 | -0.082672 | 0.10029 | 0.06599 | 5.1352e-05 | 0.058387 | 0.10607 | -0.0014355 | -0.25635 | 61.0199 | -61.9492 | 60.9421 | -61.7157 | -62.0361 | 61.0611 | 0.32501 | 60.9787 | -61.8347 | -61.8073 | 61.1252 | 60.9467 | 0.09613 | -0.15106 | -0.032044 | -0.10986 | 0.082398 | 122.8592 | -0.23804 | 123.0103 | -0.086975 | -0.036621 | -0.073242 | -122.8592 | 122.9233 | 61.8942 | 122.7448 | 61.9308 | 122.7814 | 0.23346 | 122.8912 | 122.9599 | 0.027466 | 122.9691 | 122.8134 | 122.818 | 122.7768 | -123.0011 | -122.8867 | 122.7402 | -0.009155 | 61.5417 | 62.1231
1210.8906 | 123.143 | -61.8073 | 60.9512 | -0.19012 | 0.0032619 | 0.062786 | 0.067659 | 0.0049561 | -0.0024866 | -0.00076267 | -0.11319 | 0.09751 | 0.063213 | -0.0069982 | 0.057747 | 0.10521 | -0.00079467 | -0.28381 | 60.91 | -61.94 | 61.0062 | -61.6241 | -61.9949 | 61.0611 | 0.49896 | 60.9055 | -61.8164 | -61.7249 | 61.1847 | 60.9695 | 0.009155 | -0.13275 | -0.041199 | 0.054932 | 0.1831 | 122.8683 | -0.18768 | 123.0011 | -0.054932 | -0.009155 | -0.045776 | -122.6761 | 122.9919 | 61.8164 | 122.7768 | 61.8256 | 122.7859 | 0.31586 | 122.9462 | 123.0011 | 0.091552 | 122.85 | 122.7219 | 122.7173 | 122.7127 | -122.8912 | -122.7676 | 122.8134 | 0.082397 | 61.5234 | 62.3062
1211.8281 | 123.0194 | -61.7844 | 61.0611 | -0.022278 | -0.00036966 | 0.063 | 0.068727 | 0.0036743 | -0.00013676 | 0.00073273 | -0.088776 | 0.098365 | 0.066418 | -0.0091344 | 0.059028 | 0.105 | 0.00070073 | -0.2655 | 61.0062 | -61.9308 | 60.9558 | -61.6928 | -62.027 | 61.0657 | 0.33417 | 61.0016 | -61.821 | -61.7935 | 61.1664 | 60.9558 | 0.10529 | -0.14648 | -0.054931 | -0.10529 | 0.091553 | 122.85 | -0.24262 | 122.9965 | -0.096131 | -0.036621 | -0.059509 | -122.8546 | 122.9507 | 61.8896 | 122.7402 | 61.9263 | 122.7768 | 0.23804 | 122.8867 | 122.9874 | 0.027466 | 122.937 | 122.8226 | 122.7905 | 122.7859 | -122.9919 | -122.8821 | 122.7402 | -0.009155 | 61.5189 | 62.1185
1212.8906 | 123.1201 | -61.821 | 60.9695 | -0.15198 | 5.7742e-05 | 0.061504 | 0.066163 | 0.0019653 | 0.0015722 | 0.0011599 | -0.088776 | 0.098578 | 0.063213 | -0.0029394 | 0.060951 | 0.10521 | 0.00048713 | -0.29297 | 60.9375 | -61.9217 | 60.997 | -61.6287 | -62.0087 | 61.084 | 0.31128 | 60.9009 | -61.821 | -61.734 | 61.171 | 60.997 | 0.022888 | -0.10071 | -0.032043 | 0.027466 | 0.19226 | 122.905 | -0.18768 | 123.0057 | -0.086975 | 0 | -0.068664 | -122.7036 | 122.9919 | 61.8439 | 122.818 | 61.8439 | 122.818 | 0.29297 | 122.9187 | 122.9919 | 0.086975 | 122.8592 | 122.7219 | 122.7585 | 122.7219 | -122.8912 | -122.7905 | 122.818 | 0.086975 | 61.528 | 62.1323
1213.8281 | 123.0103 | -61.821 | 61.0291 | -0.037537 | -0.00015586 | 0.063 | 0.069368 | 0.0034607 | -0.0018458 | -0.0022581 | -0.11014 | 0.098578 | 0.064495 | 0.0041102 | 0.058815 | 0.10778 | 0.0021961 | -0.23804 | 60.9924 | -61.9263 | 60.9924 | -61.6562 | -62.0178 | 61.0794 | 0.35706 | 60.9695 | -61.8347 | -61.7157 | 60.997 | 60.9467 | 0.091553 | -0.10529 | -0.036621 | -0.036621 | 0.1648 | 122.9004 | -0.19684 | 123.0057 | -0.091552 | -0.013733 | -0.05951 | -122.7448 | 122.818 | 61.9125 | 122.7676 | 61.9263 | 122.7814 | 0.27008 | 122.9187 | 122.8317 | 0.11902 | 122.9187 | 122.8043 | 122.8134 | 122.7905 | -122.9553 | -122.8638 | 122.8134 | 0.10529 | 61.5829 | 62.178
1214.8906 | 123.056 | -61.8393 | 61.0107 | -0.022278 | 0.0024075 | 0.062359 | 0.069581 | 0.0023925 | -0.0037684 | -0.0011899 | -0.11319 | 0.10029 | 0.066204 | -0.00037605 | 0.060524 | 0.105 | -0.0059217 | -0.3479 | 60.9512 | -61.9537 | 60.8871 | -61.7569 | -62.1185 | 61.0016 | 0.21515 | 60.9558 | -61.8439 | -61.821 | 61.0748 | 60.8917 | -0.045776 | -0.11444 | -0.059509 | -0.1236 | 0.082397 | 122.8409 | -0.27924 | 122.9553 | -0.16479 | -0.004578 | -0.054931 | -122.8317 | 122.9141 | 61.7935 | 122.731 | 61.7981 | 122.7356 | 0.19684 | 122.8409 | 122.9187 | 0.022888 | 122.905 | 122.7997 | 122.7905 | 122.7951 | -122.9645 | -122.8546 | 122.7264 | 0.01831 | 61.4914 | 62.0544
1215.8281 | 123.0331 | -61.7752 | 61.0382 | -0.045166 | 0.00048494 | 0.062145 | 0.069795 | 0.00068369 | -0.0012048 | -0.0037533 | -0.073517 | 0.1005 | 0.065777 | -0.00037605 | 0.057533 | 0.10585 | 0.0024097 | -0.25177 | 60.997 | -61.94 | 60.9329 | -61.7111 | -62.0544 | 61.0657 | 0.32501 | 60.9924 | -61.8256 | -61.8164 | 61.1252 | 60.9512 | 0.082397 | -0.16479 | -0.041199 | -0.10529 | 0.064087 | 122.8409 | -0.27923 | 123.0057 | -0.11444 | -0.050354 | -0.045776 | -122.8546 | 122.9004 | 61.8576 | 122.7264 | 61.908 | 122.7768 | 0.22888 | 122.8729 | 122.9507 | 0.009156 | 122.937 | 122.818 | 122.7722 | 122.7676 | -122.9782 | -122.8638 | 122.7081 | -0.041198 | 61.5234 | 62.1002
1216.8906 | 123.1293 | -61.8118 | 60.965 | -0.11383 | 0.0013393 | 0.063427 | 0.069154 | 0.0013245 | -0.0041956 | -0.0022581 | -0.049103 | 0.097938 | 0.065136 | -0.0016576 | 0.05796 | 0.10628 | 0.00048713 | -0.31586 | 60.9283 | -61.9492 | 60.9695 | -61.6516 | -62.0224 | 61.0977 | 0.3067 | 60.8826 | -61.8393 | -61.7249 | 61.1572 | 61.0107 | 0.027466 | -0.13733 | -0.036621 | 0.004577 | 0.16022 | 122.9095 | -0.21057 | 123.0469 | -0.073242 | -0.027465 | -0.082398 | -122.6898 | 122.9691 | 61.8393 | 122.8226 | 61.8668 | 122.85 | 0.29755 | 122.9187 | 122.9965 | 0.11444 | 122.8775 | 122.7219 | 122.7402 | 122.6944 | -122.9141 | -122.8043 | 122.7814 | 0.086975 | 61.496 | 62.1185
1217.8281 | 122.9965 | -61.8027 | 61.0519 | -0.037537 | 0.0011257 | 0.059795 | 0.069368 | -0.0014527 | -0.0020594 | -0.0020443 | -0.073517 | 0.09986 | 0.066845 | -0.0052892 | 0.059669 | 0.10479 | -0.00036747 | -0.26093 | 61.0199 | -61.9263 | 60.8551 | -61.4731 | -61.8347 | 60.8459 | 0.29297 | 60.9924 | -61.8301 | -61.8027 | 61.1023 | 60.9375 | 0.073242 | -0.1236 | -0.032044 | -0.19684 | 0.32959 | 122.6486 | -0.032044 | 122.7722 | 0.091553 | -0.027466 | -0.059509 | -122.8546 | 122.905 | 61.8759 | 122.7402 | 61.9034 | 122.7676 | 0.45319 | 122.7814 | 122.9324 | 0.027466 | 122.9462 | 122.8226 | 122.8226 | 122.7951 | -122.9782 | -122.8821 | 122.6578 | 0 | 61.5417 | 62.0956
1218.9062 | 123.0103 | -61.7844 | 61.0611 | -0.045166 | -0.00058326 | 0.061077 | 0.067872 | 0.0017517 | -0.005691 | 0.00051913 | -0.052155 | 0.1005 | 0.064068 | -0.0025122 | 0.060737 | 0.10329 | 0.00070073 | -0.27466 | 61.0199 | -61.9217 | 60.9329 | -61.7157 | -62.059 | 61.2305 | 0.19226 | 60.9741 | -61.8256 | -61.8439 | 61.1343 | 60.9512 | 0.073242 | -0.13733 | -0.041199 | -0.12817 | 0.068665 | 123.0148 | -0.27466 | 123.1522 | -0.13733 | -0.041199 | -0.086975 | -122.905 | 122.9187 | 61.8576 | 122.7356 | 61.8988 | 122.7768 | 0.20599 | 122.8546 | 122.9599 | -0.01831 | 122.9416 | 122.7997 | 122.8043 | 122.7585 | -122.9828 | -122.8867 | 122.7173 | -0.059509 | 61.5097 | 61.9766
1219.8281 | 123.0789 | -61.7661 | 61.0519 | -0.075684 | 0.0011257 | 0.063 | 0.068086 | 0.0023925 | -0.00056396 | -0.0028989 | -0.024689 | 0.09986 | 0.065136 | -0.0057166 | 0.060737 | 0.10372 | -0.00058107 | -0.21515 | 60.9741 | -61.9171 | 61.0291 | -61.5921 | -61.9537 | 61.1343 | 0.42114 | 60.9741 | -61.8027 | -61.7752 | 61.1664 | 60.9924 | 0.1236 | -0.15106 | -0.07782 | -0.022888 | 0.17395 | 122.9004 | -0.18768 | 123.0515 | -0.036621 | -0.036621 | -0.07782 | -122.8271 | 122.9324 | 61.8896 | 122.7585 | 61.9263 | 122.7951 | 0.32501 | 122.9462 | 122.9691 | 0.027465 | 122.8912 | 122.7768 | 122.7402 | 122.7402 | -122.9691 | -122.8546 | 122.7951 | -0.009156 | 61.5509 | 62.1872
1220.8906 | 123.0103 | -61.821 | 61.0153 | -0.16724 | 0.0011257 | 0.061291 | 0.070222 | 0.0060241 | 7.6842e-05 | -0.0014035 | -0.11929 | 0.09986 | 0.067486 | -0.0063574 | 0.059456 | 0.10564 | -0.0025037 | -0.54474 | 60.8963 | -62.0087 | 60.9467 | -61.7752 | -62.1277 | 61.0291 | 0.21515 | 60.965 | -61.8713 | -61.8301 | 61.0565 | 60.878 | -0.050354 | -0.18768 | -0.11902 | -0.068665 | 0.045776 | 122.85 | -0.3067 | 123.0377 | -0.11902 | -0.050354 | -0.050354 | -122.8455 | 122.8775 | 61.7706 | 122.699 | 61.821 | 122.7493 | 0.23346 | 122.9553 | 122.9279 | 0.041199 | 122.905 | 122.8363 | 122.7173 | 122.7859 | -123.024 | -122.8867 | 122.7676 | -0.009155 | 61.2762 | 62.0361
1221.8281 | 123.0515 | -61.7935 | 61.0657 | -0.098572 | -0.00036966 | 0.06065 | 0.069581 | 0.00025629 | -0.0020594 | -0.00012167 | -0.082672 | 0.10093 | 0.064709 | -0.0052892 | 0.060096 | 0.10671 | -0.00079467 | -0.26093 | 60.9924 | -61.9537 | 60.9604 | -61.7065 | -62.059 | 61.0657 | 0.31128 | 60.9879 | -61.8073 | -61.8027 | 61.116 | 60.9375 | 0.07782 | -0.16022 | -0.073242 | -0.10529 | 0.086975 | 122.8592 | -0.2655 | 123.0194 | -0.10529 | -0.013733 | -0.07782 | -122.8683 | 122.9095 | 61.8713 | 122.731 | 61.8851 | 122.7448 | 0.24719 | 122.9141 | 122.9233 | 0.004578 | 122.9462 | 122.7951 | 122.7859 | 122.7814 | -123.0194 | -122.8729 | 122.7539 | -0.009155 | 61.5326 | 62.1048
1222.8906 | 123.0515 | -61.821 | 60.9924 | -0.11383 | 0.0015529 | 0.061932 | 0.071077 | 0.0036743 | -0.002273 | -0.00054907 | -0.076569 | 0.10093 | 0.065563 | -0.003153 | 0.059669 | 0.1065 | -0.0029309 | -0.27466 | 60.9787 | -61.9492 | 60.8917 | -61.7477 | -62.1094 | 60.997 | 0.21057 | 60.9329 | -61.853 | -61.8256 | 61.0611 | 60.8917 | -0.059509 | -0.12817 | -0.013733 | -0.10071 | 0.073242 | 122.818 | -0.28839 | 122.9462 | -0.16022 | -0.032043 | -0.05951 | -122.818 | 122.8821 | 61.7615 | 122.7127 | 61.7935 | 122.7448 | 0.20142 | 122.8409 | 122.9141 | 0.027465 | 122.9279 | 122.7859 | 122.7997 | 122.7539 | -122.9416 | -122.8455 | 122.7127 | -0.004578 | 61.5463 | 62.0316
1223.8281 | 123.0148 | -61.8164 | 61.0428 | -0.060425 | 0.0021939 | 0.06065 | 0.068086 | 0.00068369 | -0.00077756 | -0.0043943 | -0.0033265 | 0.099647 | 0.067272 | 0.0015466 | 0.05796 | 0.10521 | 0.00091433 | -0.21515 | 60.9787 | -61.8851 | 61.0062 | -61.6287 | -61.9675 | 61.116 | 0.38452 | 60.9787 | -61.8027 | -61.7889 | 61.1481 | 60.9192 | 0.082397 | -0.068665 | -0.064087 | -0.036621 | 0.18768 | 122.9324 | -0.15106 | 123.0011 | -0.082397 | 0.013733 | -0.064087 | -122.8317 | 122.9645 | 61.8988 | 122.7356 | 61.8851 | 122.7219 | 0.25635 | 122.8912 | 122.9507 | 0.013733 | 122.8638 | 122.7814 | 122.7951 | 122.7951 | -122.9279 | -122.8455 | 122.8226 | 0.027466 | 61.6013 | 62.2009
1224.8906 | 122.9828 | -61.8256 | 61.0199 | -0.060425 | 0.0041165 | 0.060863 | 0.070009 | 0.0021789 | -0.0018458 | 0.00073273 | -0.11319 | 0.10007 | 0.064709 | -0.0050756 | 0.060096 | 0.10479 | 0.0015551 | -0.31586 | 60.9787 | -61.9766 | 60.9146 | -61.7386 | -62.0865 | 60.997 | 0.21973 | 60.9741 | -61.8439 | -61.8393 | 61.0474 | 60.8414 | -0.045776 | -0.15106 | -0.041198 | -0.10529 | 0.086976 | 122.8226 | -0.26093 | 122.9736 | -0.10986 | -0.01831 | -0.045776 | -122.8592 | 122.8729 | 61.7798 | 122.6669 | 61.7981 | 122.6852 | 0.23804 | 122.8912 | 122.8912 | 0.004578 | 122.9553 | 122.818 | 122.8043 | 122.7997 | -122.9965 | -122.8638 | 122.7402 | -0.013732 | 61.5097 | 62.0453
1225.8281 | 123.1293 | -61.7661 | 60.9924 | -0.052796 | 0.0017667 | 0.060863 | 0.067659 | -0.00059811 | -0.00056396 | -0.0052487 | 0.0088807 | 0.098792 | 0.063854 | -0.0069982 | 0.059883 | 0.10457 | -0.0052809 | -0.20599 | 60.965 | -61.8988 | 61.0748 | -61.5326 | -61.9125 | 61.1664 | 0.45776 | 60.9512 | -61.7752 | -61.7661 | 61.5326 | 60.9375 | -0.032043 | -0.13275 | -0.027466 | 0.082397 | 0.23346 | 122.9324 | -0.14648 | 123.0652 | -0.013733 | -0.009156 | -0.041199 | -122.7585 | 123.2986 | 61.734 | 122.7036 | 61.7432 | 122.7127 | 0.36621 | 122.9736 | 123.3078 | 0.009156 | 122.8638 | 122.7264 | 122.731 | 122.7173 | -122.8912 | -122.7676 | 122.8409 | 0 | 61.5601 | 62.2238
1226.8906 | 123.0469 | -61.8393 | 61.0474 | -0.045166 | 0.00048494 | 0.063427 | 0.068086 | 0.0023925 | -0.00056396 | -0.0011899 | -0.094879 | 0.099006 | 0.064068 | 0.0021876 | 0.057747 | 0.10479 | -0.0025037 | -0.27008 | 60.9421 | -61.9629 | 60.9558 | -61.6882 | -62.0544 | 61.0428 | 0.3067 | 60.9924 | -61.8164 | -61.8073 | 61.0977 | 60.9055 | 0 | -0.1236 | -0.10528 | -0.091552 | 0.15106 | 122.8821 | -0.21515 | 123.0057 | -0.091552 | 0.022888 | -0.054931 | -122.8546 | 122.937 | 61.8393 | 122.7448 | 61.8164 | 122.7219 | 0.27466 | 122.9187 | 122.9141 | 0.009155 | 122.905 | 122.8088 | 122.7814 | 122.8317 | -123.0103 | -122.8638 | 122.7951 | 0.032043 | 61.5692 | 62.146
1227.8281 | 123.0011 | -61.8118 | 61.0611 | -0.068054 | 0.0013393 | 0.061932 | 0.068727 | -0.0023071 | -0.0014184 | 0.00073273 | -0.039948 | 0.09986 | 0.064068 | -0.0022986 | 0.060524 | 0.10457 | -0.0025037 | -0.22888 | 61.0062 | -61.9217 | 60.9741 | -61.6608 | -62.0178 | 61.0611 | 0.35248 | 60.997 | -61.821 | -61.8393 | 61.1114 | 60.9467 | 0.068665 | -0.10986 | -0.054931 | -0.086975 | 0.15106 | 122.8729 | -0.20599 | 122.9828 | -0.09613 | -0.009155 | -0.064087 | -122.9004 | 122.9233 | 61.8805 | 122.7585 | 61.8896 | 122.7676 | 0.26093 | 122.8958 | 122.9324 | -0.01831 | 122.9279 | 122.818 | 122.818 | 122.8088 | -122.9828 | -122.8821 | 122.7859 | -0.027465 | 61.5829 | 62.1643
1228.8906 | 122.9965 | -61.821 | 61.0291 | -0.075684 | 5.7742e-05 | 0.060863 | 0.067659 | 0.0019653 | 0.00029044 | 0.00094633 | -0.067413 | 0.10093 | 0.067699 | -0.001444 | 0.057747 | 0.10799 | -0.0012219 | -0.33875 | 60.9741 | -61.9812 | 60.8734 | -61.8805 | -62.4939 | 61.1069 | 0.16022 | 60.9604 | -61.8301 | -61.8622 | 61.0428 | 60.8643 | -0.050354 | -0.16022 | -0.054932 | -0.15564 | -0.059509 | 122.9279 | -0.67291 | 123.0881 | -0.5127 | -0.009155 | -0.068665 | -122.8912 | 122.8638 | 61.7706 | 122.6852 | 61.7798 | 122.6944 | 0.10071 | 122.8546 | 122.8729 | -0.032044 | 122.9553 | 122.7905 | 122.7951 | 122.7814 | -123.0103 | -122.8592 | 122.6944 | -0.041199 | 61.4822 | 61.9812
1229.8281 | 123.0606 | -61.8027 | 61.0428 | -0.11383 | 0.0019803 | 0.06065 | 0.067872 | 0.0017517 | -0.0033412 | -0.00076267 | -0.036896 | 0.098151 | 0.066204 | -0.0016576 | 0.058815 | 0.10457 | 0.0036913 | -0.20599 | 60.9512 | -61.8896 | 61.0291 | -61.5738 | -61.94 | 61.1298 | 0.4303 | 60.9604 | -61.7798 | -61.7661 | 61.1847 | 61.0107 | 0.11902 | -0.086975 | -0.091553 | -0.013733 | 0.22888 | 122.9324 | -0.13733 | 123.0194 | -0.050354 | 0.022888 | -0.082398 | -122.8088 | 122.9874 | 61.9217 | 122.8134 | 61.8988 | 122.7905 | 0.31586 | 122.9187 | 122.9645 | 0.013733 | 122.8409 | 122.7402 | 122.7539 | 122.7631 | -122.9324 | -122.8226 | 122.8317 | 0.036621 | 61.5967 | 62.233
1230.8906 | 123.0927 | -62.7182 | 60.0311 | -0.15961 | 0.0026211 | 0.063854 | 0.067232 | -0.0012391 | -0.0018458 | -0.00076267 | -0.085724 | 0.16544 | 0.13072 | -0.0025122 | 0.059242 | 0.10457 | 0.0039049 | -0.25635 | 59.9533 | -62.8555 | 60.0403 | -62.5031 | -62.9379 | 60.1456 | 0.40741 | 59.9442 | -62.7548 | 60.1181 | 60.2234 | 60.0403 | 0.2243 | -0.13733 | -0.07782 | 0.009155 | 0.21515 | 122.8638 | -0.21973 | 123.0011 | -0.082397 | -0.036621 | -0.086975 | 0.086975 | 122.9416 | 62.9425 | 122.7585 | 62.9791 | 122.7951 | 0.35248 | 122.8958 | 122.9782 | 122.8729 | 122.8088 | 122.699 | 122.6715 | 122.6624 | -122.8867 | -122.7859 | 122.7585 | 122.8363 | 62.4619 | 63.1256
1231.8281 | 123.1064 | -62.7182 | 60.0723 | -0.12146 | 0.00069854 | 0.059795 | 0.067445 | -0.0010253 | -0.0035548 | -0.0020443 | -0.14981 | 0.16437 | 0.12858 | -0.0016576 | 0.058815 | 0.10457 | -0.0014355 | -0.19684 | 60.0082 | -62.8372 | 60.1089 | -62.5534 | -62.4069 | 60.2417 | 0.60883 | 59.9945 | -62.7411 | 60.1501 | 60.2829 | 60.0861 | 0.36163 | -0.11902 | -0.064087 | 0.036621 | 0.16479 | 122.9599 | 0.31128 | 123.0789 | 0.4303 | -0.022888 | -0.07782 | 0.077819 | 123.0011 | 63.0798 | 122.8043 | 63.1027 | 122.8271 | 0.28381 | 122.9462 | 123.024 | 122.8912 | 122.8455 | 122.7356 | 122.7264 | 122.7127 | -122.9095 | -122.8134 | 122.8271 | 122.8683 | 62.5214 | 63.327
1232.8906 | 123.0698 | -62.7319 | 60.0449 | -0.090943 | 0.0011257 | 0.064281 | 0.069795 | 0.0079467 | -0.0044092 | -0.0039671 | -0.12234 | 0.16566 | 0.12922 | -0.0057166 | 0.056465 | 0.1065 | -0.0018629 | -0.35248 | 60.022 | -62.9196 | 59.9762 | -62.6404 | -63.0341 | 60.0815 | 0.32959 | 59.9945 | -62.7869 | 60.0952 | 60.173 | 59.9991 | 0.19226 | -0.18768 | -0.022888 | -0.068665 | 0.091553 | 122.8134 | -0.30212 | 123.0011 | -0.11444 | -0.054931 | -0.050354 | 0.050354 | 122.905 | 62.9242 | 122.731 | 62.9791 | 122.7859 | 0.27924 | 122.8958 | 122.9599 | 122.8821 | 122.9416 | 122.7814 | 122.7539 | 122.7264 | -122.9645 | -122.8317 | 122.7081 | 122.8271 | 62.3795 | 63.0615
1233.8281 | 123.1338 | -62.7319 | 60.0449 | -0.090943 | 0.0013393 | 0.061291 | 0.066163 | 0.0023925 | -0.0037684 | -0.0020443 | -0.052155 | 0.16544 | 0.12965 | -0.00058965 | 0.057106 | 0.10457 | -0.0029309 | -0.30212 | 60.022 | -62.8647 | 60.0494 | -62.5671 | -62.9196 | 60.1593 | 0.43488 | 59.9854 | -62.7365 | 60.141 | 60.2371 | 60.0677 | 0.32044 | -0.13275 | -0.022888 | 0.004577 | 0.1648 | 122.8912 | -0.18768 | 123.024 | -0.054932 | -0.004577 | -0.059509 | 0.09613 | 122.9691 | 63.0524 | 122.7997 | 63.0569 | 122.8043 | 0.29755 | 122.9141 | 122.9736 | 122.8775 | 122.8867 | 122.7219 | 122.7539 | 122.7173 | -122.9095 | -122.7814 | 122.7814 | 122.8729 | 62.4298 | 63.1668
1234.8906 | 123.0469 | -62.764 | 60.0677 | -0.029907 | 0.0028347 | 0.063 | 0.069368 | 0.0017517 | -0.0035548 | -0.0031125 | -0.091827 | 0.16672 | 0.13221 | -0.00016245 | 0.056465 | 0.10543 | 0.0013415 | -0.26093 | 60.0174 | -62.8876 | 60.0357 | -62.5397 | -63.2217 | 60.0769 | 0.43488 | 60.022 | -62.7594 | 60.0998 | 60.1639 | 59.967 | 0.26093 | -0.1236 | -0.050354 | -0.032043 | 0.2243 | 122.8409 | -0.45776 | 122.9645 | -0.33417 | 0.004578 | -0.045776 | 0.032043 | 122.9279 | 63.0249 | 122.731 | 63.0203 | 122.7264 | 0.3479 | 122.9233 | 122.9233 | 122.8592 | 122.905 | 122.7814 | 122.7814 | 122.7859 | -122.9553 | -122.8271 | 122.7997 | 122.8638 | 62.5031 | 63.1989
1235.8281 | 123.0972 | -62.7319 | 60.0449 | -0.1062 | 0.0024075 | 0.062572 | 0.0683 | -0.0029479 | 0.00071784 | -0.00076267 | -0.046051 | 0.16459 | 0.12986 | -0.0097754 | 0.058174 | 0.10436 | -0.0042127 | -0.27924 | 59.9899 | -62.8647 | 60.0266 | -62.5626 | -62.9105 | 60.173 | 0.4303 | 59.9579 | -62.7274 | 60.141 | 60.2417 | 60.0677 | 0.28381 | -0.13275 | -0.054932 | -0.018311 | 0.16937 | 122.905 | -0.17853 | 123.0377 | -0.045776 | 0.004578 | -0.086975 | 0.09613 | 122.9736 | 63.0157 | 122.7997 | 63.0112 | 122.7951 | 0.30212 | 122.8912 | 122.9691 | 122.8683 | 122.8546 | 122.6852 | 122.7219 | 122.6898 | -122.9095 | -122.7722 | 122.7585 | 122.8729 | 62.4527 | 63.1622
1236.8906 | 122.9599 | -62.7731 | 60.0494 | -0.1062 | 0.00091214 | 0.063213 | 0.071077 | 0.0043151 | -0.0018458 | 0.0024417 | -0.14981 | 0.16737 | 0.13115 | 0.0043238 | 0.056892 | 0.10564 | 0.00027333 | -0.32959 | 60.0128 | -62.9059 | 59.9258 | -62.6816 | -63.0707 | 60.0266 | 0.24719 | 60.0357 | -62.7914 | 59.9991 | 60.0632 | 59.8938 | 0.14648 | -0.13275 | -0.036621 | -0.1236 | 0.091552 | 122.7997 | -0.29755 | 122.9324 | -0.16479 | -0.018311 | -0.013732 | -0.050354 | 122.8363 | 62.9196 | 122.6669 | 62.9379 | 122.6852 | 0.2243 | 122.8317 | 122.8546 | 122.7905 | 122.9187 | 122.8271 | 122.7859 | 122.8088 | -122.9553 | -122.8409 | 122.699 | 122.7722 | 62.4435 | 63.0203
1237.8281 | 123.0881 | -62.7365 | 60.0449 | -0.075684 | 0.0017667 | 0.060863 | 0.067018 | -0.0023071 | -0.0016322 | -0.0035397 | -0.052155 | 0.16331 | 0.12901 | -0.012766 | 0.061378 | 0.10372 | -0.00036747 | -0.32959 | 59.9762 | -62.851 | 60.0174 | -62.5992 | -62.9517 | 60.1227 | 0.36163 | 59.9899 | -62.7686 | 60.1089 | 60.1593 | 59.9991 | 0.23804 | -0.11444 | -0.068665 | -0.027466 | 0.13733 | 122.8592 | -0.21515 | 122.9736 | -0.10071 | -0.032044 | -0.054932 | 0.064087 | 122.8958 | 62.9745 | 122.7356 | 63.0066 | 122.7676 | 0.25177 | 122.8683 | 122.9279 | 122.8775 | 122.8271 | 122.7585 | 122.7127 | 122.7264 | -122.8958 | -122.8134 | 122.7539 | 122.8455 | 62.4069 | 63.0981
1238.8281 | 123.0423 | -62.7548 | 60.0403 | -0.14435 | 0.0017667 | 0.062145 | 0.070222 | 0.0015381 | -0.0018458 | -0.0024717 | -0.14676 | 0.1648 | 0.1288 | 0.0015466 | 0.058815 | 0.1065 | -0.0010083 | -0.36621 | 59.9945 | -62.9105 | 59.9579 | -62.6724 | -63.0478 | 60.0632 | 0.29755 | 59.9716 | -62.7823 | 60.0632 | 60.1135 | 59.9396 | 0.16022 | -0.15564 | -0.045776 | -0.082397 | 0.082398 | 122.818 | -0.29297 | 122.9736 | -0.13733 | -0.027466 | -0.068664 | 0.022888 | 122.8683 | 62.915 | 122.6944 | 62.9425 | 122.7219 | 0.23804 | 122.8683 | 122.8958 | 122.8455 | 122.905 | 122.7539 | 122.7493 | 122.7264 | -122.9507 | -122.8226 | 122.7127 | 122.818 | 62.3886 | 63.0524
1239.8906 | 123.0148 | -62.7228 | 60.0998 | -0.083313 | 0.0015529 | 0.06065 | 0.070009 | 0.0013245 | -0.0029138 | -0.00033547 | -0.1376 | 0.16566 | 0.13093 | 0.00047855 | 0.058601 | 0.105 | -0.0022901 | -0.27008 | 60.0449 | -62.8693 | 59.9899 | -62.6266 | -62.9608 | 60.1135 | 0.41199 | 60.0494 | -62.7502 | 60.0906 | 60.1822 | 59.9899 | 0.29297 | -0.14648 | -0.054931 | -0.10986 | 0.09613 | 122.8363 | -0.23804 | 122.9828 | -0.091552 | -0.027466 | -0.050354 | -0.009155 | 122.905 | 63.0157 | 122.7127 | 63.0432 | 122.7402 | 0.24261 | 122.8592 | 122.9324 | 122.8409 | 122.9141 | 122.7997 | 122.7676 | 122.7722 | -122.9691 | -122.85 | 122.7127 | 122.8134 | 62.4527 | 63.1348
1240.8281 | 123.111 | -62.7182 | 60.0128 | -0.068054 | 0.0026211 | 0.063213 | 0.067872 | 0.0028199 | -0.0012048 | 0.00051913 | -0.10403 | 0.16459 | 0.13029 | -0.0029394 | 0.059669 | 0.10436 | 0.00027333 | -0.29297 | 59.9487 | -62.8738 | 60.0632 | -62.5351 | -62.9379 | 60.1456 | 0.47607 | 59.9487 | -62.7823 | 60.1547 | 60.2509 | 60.0082 | 0.21973 | -0.15564 | -0.064087 | 0.050354 | 0.18311 | 122.8638 | -0.21973 | 123.0194 | -0.064087 | -0.064087 | -0.064087 | 0.14191 | 122.9691 | 62.9379 | 122.7264 | 63.002 | 122.7905 | 0.33875 | 122.937 | 123.0331 | 122.937 | 122.8226 | 122.731 | 122.6669 | 122.6669 | -122.8867 | -122.7951 | 122.7814 | 122.8729 | 62.4252 | 63.1943
1241.8906 | 122.9416 | -62.7731 | 60.054 | -0.090943 | 0.0017667 | 0.061291 | 0.070222 | 0.00068369 | -0.0024866 | 0.00094633 | -0.15897 | 0.16437 | 0.12858 | -0.00016245 | 0.058601 | 0.10671 | 0.0024097 | -0.32959 | 60.0357 | -62.9059 | 59.9304 | -62.7136 | -63.0478 | 60.0403 | 0.22888 | 60.0037 | -62.7777 | 60.0128 | 60.0906 | 59.903 | 0.14648 | -0.13275 | -0.01831 | -0.1236 | 0.059509 | 122.8134 | -0.27466 | 122.9462 | -0.14191 | -0.004578 | -0.050354 | -0.041199 | 122.8638 | 62.9196 | 122.6761 | 62.9242 | 122.6807 | 0.19226 | 122.8363 | 122.8683 | 122.7905 | 122.9416 | 122.7814 | 122.8088 | 122.7768 | -122.9599 | -122.8317 | 122.7036 | 122.7859 | 62.4435 | 63.002
1242.8281 | 123.0835 | -62.7502 | 59.9899 | -0.15198 | 0.0024075 | 0.064068 | 0.07129 | -0.0010253 | -0.0012048 | 0.0013735 | -0.11929 | 0.16502 | 0.1305 | -0.00080325 | 0.05796 | 0.10671 | -0.0018629 | -0.3479 | 59.9945 | -62.8876 | 59.9808 | -62.6129 | -62.9974 | 60.0861 | 0.33417 | 59.9762 | -62.7777 | 60.1135 | 60.1868 | 59.9899 | 0.16937 | -0.13733 | 0.004578 | -0.009155 | 0.13733 | 122.8363 | -0.24719 | 122.9736 | -0.10986 | -0.027466 | -0.013733 | 0.1236 | 122.937 | 62.9196 | 122.7402 | 62.9471 | 122.7676 | 0.27466 | 122.8683 | 122.9645 | 122.8912 | 122.8821 | 122.7539 | 122.7448 | 122.7264 | -122.8775 | -122.7676 | 122.731 | 122.8638 | 62.4023 | 63.0844
1243.8906 | 123.024 | -62.7502 | 60.0677 | -0.098572 | 0.0028347 | 0.061504 | 0.069154 | 0.0023925 | 0.00071784 | -0.0020443 | -0.14371 | 0.16544 | 0.12922 | -0.004862 | 0.058601 | 0.10479 | 0.0015551 | -0.25635 | 59.9991 | -62.8464 | 60.0174 | -62.5809 | -62.9608 | 60.0952 | 0.43945 | 59.9899 | -62.7548 | 60.1273 | 60.1776 | 59.9854 | 0.23804 | -0.096131 | -0.068665 | -0.050354 | 0.16937 | 122.8455 | -0.21057 | 122.9416 | -0.11444 | -0.004578 | -0.07782 | 0.059509 | 122.9279 | 62.9883 | 122.7356 | 62.9929 | 122.7402 | 0.2655 | 122.8638 | 122.9324 | 122.8821 | 122.8455 | 122.7448 | 122.7493 | 122.7402 | -122.9141 | -122.8226 | 122.7676 | 122.8775 | 62.4939 | 63.1897
1244.8281 | 122.9782 | -62.7594 | 60.0632 | -0.045166 | -0.0010105 | 0.063213 | 0.070222 | -0.00017091 | -0.00013676 | -0.0011899 | -0.14066 | 0.16523 | 0.13221 | 0.00090575 | 0.059456 | 0.10692 | 0.00070073 | -0.36621 | 60.0311 | -62.8967 | 59.6878 | -62.8555 | -62.6129 | 60.1318 | 0.32959 | 60.0403 | -62.7594 | 60.0403 | 60.0998 | 59.8938 | 0.14648 | -0.13733 | -0.032043 | -0.37537 | -0.096131 | 122.8912 | 0.14648 | 123.0286 | 0.28381 | 0 | -0.022888 | -0.022888 | 122.8592 | 62.9059 | 122.6532 | 62.9059 | 122.6532 | 0.041199 | 122.5845 | 122.8592 | 122.7997 | 122.9279 | 122.7997 | 122.7905 | 122.7997 | -122.9599 | -122.8226 | 122.4472 | 122.7997 | 62.3932 | 63.089
1245.8906 | 123.1155 | -62.7182 | 60.054 | -0.090943 | 0.0021939 | 0.06065 | 0.068086 | -0.0035889 | -0.0035548 | -0.0024717 | -0.11929 | 0.16502 | 0.12815 | -0.00058965 | 0.059669 | 0.10671 | -0.0016493 | -0.2655 | 60.0403 | -62.8693 | 60.022 | -62.558 | -62.9425 | 60.1181 | 0.44403 | 60.0082 | -62.7502 | 60.0906 | 60.173 | 60.0037 | 0.2655 | -0.15106 | -0.013733 | -0.032043 | 0.16022 | 122.8363 | -0.2243 | 122.9874 | -0.073242 | -0.032043 | -0.045776 | 0.036621 | 122.8912 | 62.9837 | 122.7219 | 63.0157 | 122.7539 | 0.31128 | 122.8912 | 122.9233 | 122.8409 | 122.9095 | 122.7585 | 122.7585 | 122.7264 | -122.9233 | -122.8043 | 122.7402 | 122.8088 | 62.4527 | 63.1622
1246.8281 | 123.0011 | -62.764 | 60.0906 | -0.014649 | 0.0026211 | 0.062572 | 0.068513 | 0.00089729 | -0.0029138 | -0.00033547 | -0.11929 | 0.16523 | 0.12944 | 0.0051782 | 0.060524 | 0.10564 | -0.0018629 | -0.28381 | 60.0266 | -62.8738 | 60.0082 | -62.5946 | -62.9608 | 60.0723 | 0.39368 | 60.0082 | -62.7411 | 60.0586 | 60.1456 | 59.9533 | 0.20142 | -0.10986 | -0.064087 | -0.082397 | 0.16937 | 122.8363 | -0.19684 | 122.9462 | -0.086975 | 0.022888 | -0.082397 | -0.032043 | 122.9095 | 62.9654 | 122.7173 | 62.9425 | 122.6944 | 0.27924 | 122.8821 | 122.8867 | 122.7997 | 122.9004 | 122.7493 | 122.7905 | 122.7722 | -122.9645 | -122.8317 | 122.7722 | 122.8226 | 62.4802 | 63.1577
1247.8906 | 123.1018 | -62.7136 | 60.0449 | -0.090943 | 5.7742e-05 | 0.063 | 0.067232 | -0.0052979 | 0.00071784 | -0.0043943 | -0.027741 | 0.16651 | 0.13072 | -0.003794 | 0.056678 | 0.10457 | -0.0027173 | -0.2243 | 60.0174 | -62.8098 | 60.0998 | -62.4664 | -62.8372 | 60.2051 | 0.53101 | 59.9762 | -62.6862 | 60.1822 | 60.1639 | 60.1044 | 0.37079 | -0.09613 | -0.027466 | 0.054931 | 0.24719 | 122.9187 | -0.1236 | 123.0148 | -0.027466 | 0.027466 | -0.068665 | 0.13733 | 122.8775 | 63.0844 | 122.818 | 63.0569 | 122.7905 | 0.34332 | 122.9095 | 122.85 | 122.8683 | 122.8271 | 122.6624 | 122.731 | 122.6898 | -122.8546 | -122.731 | 122.8134 | 122.8958 | 62.4893 | 63.2446
1248.8281 | 122.9645 | -62.7548 | 60.0815 | -0.12146 | -0.00036966 | 0.060009 | 0.069581 | 0.0036743 | -0.0012048 | -0.0016171 | -0.14981 | 0.16779 | 0.12837 | 0.0026148 | 0.059456 | 0.10457 | -0.0018629 | -0.31128 | 60.0037 | -62.8967 | 59.9716 | -62.6633 | -63.0203 | 60.0357 | 0.32044 | 60.0037 | -62.7731 | 60.0311 | 60.0769 | 59.8892 | 0.15106 | -0.14191 | -0.07782 | -0.10986 | 0.091553 | 122.7905 | -0.2655 | 122.9324 | -0.1236 | -0.01831 | -0.07782 | -0.050354 | 122.8317 | 62.9059 | 122.644 | 62.9242 | 122.6624 | 0.23346 | 122.8683 | 122.85 | 122.8043 | 122.9004 | 122.7768 | 122.7585 | 122.7585 | -122.9782 | -122.8546 | 122.7264 | 122.7859 | 62.4435 | 63.0753
1249.8281 | 122.9828 | -62.764 | 60.0632 | -0.068054 | -0.0016513 | 0.063427 | 0.069154 | 0.0028199 | 7.6842e-05 | -0.0014035 | -0.1315 | 0.16587 | 0.12965 | -0.001444 | 0.059669 | 0.10692 | -0.0010083 | -0.32044 | 59.9991 | -62.8922 | 59.9304 | -62.6862 | -63.0295 | 60.0174 | 0.27466 | 59.9945 | -62.7914 | 60.0037 | 60.0586 | 59.8755 | 0.12817 | -0.12817 | -0.064087 | -0.13275 | 0.07782 | 122.7814 | -0.2655 | 122.9095 | -0.13733 | -0.027466 | -0.068664 | -0.059509 | 122.8226 | 62.8922 | 122.6395 | 62.9196 | 122.6669 | 0.20599 | 122.8226 | 122.85 | 122.7951 | 122.8912 | 122.7859 | 122.7631 | 122.7585 | -122.9553 | -122.8546 | 122.6944 | 122.7676 | 62.4435 | 63.0386
1250.8906 | 123.0194 | -62.7182 | 60.0952 | -0.083313 | 0.0013393 | 0.061932 | 0.068513 | 0.0011109 | -0.0020594 | -0.0026853 | -0.052155 | 0.16459 | 0.132 | -0.0033666 | 0.059669 | 0.10735 | 0.0011279 | -0.21973 | 60.0174 | -62.8189 | 60.054 | -62.5214 | -62.8922 | 60.1501 | 0.5127 | 59.9899 | -62.7319 | 60.0861 | 60.1959 | 60.0128 | 0.31128 | -0.10071 | -0.07782 | -0.041199 | 0.19684 | 122.8683 | -0.17395 | 122.9691 | -0.073242 | -0.013733 | -0.10529 | -0.009155 | 122.9141 | 63.0295 | 122.731 | 63.0432 | 122.7448 | 0.29755 | 122.8729 | 122.9279 | 122.818 | 122.8363 | 122.7219 | 122.7356 | 122.7081 | -122.9141 | -122.8271 | 122.7722 | 122.8043 | 62.4985 | 63.2309
1251.8281 | 122.9828 | -62.764 | 60.0494 | -0.12909 | 0.0011257 | 0.064281 | 0.066804 | 4.2692e-05 | 0.00071784 | -0.0028989 | -0.018585 | 0.16459 | 0.13136 | -0.0046484 | 0.058601 | 0.10521 | -0.0014355 | -0.33875 | 60.0082 | -62.8967 | 59.9304 | -62.6816 | -63.3041 | 59.8114 | 0.23346 | 59.9716 | -62.7502 | 60.0449 | 60.0677 | 59.9121 | 0.14191 | -0.13275 | -0.041198 | -0.11902 | 0.082397 | 122.5754 | -0.54016 | 122.7081 | -0.40741 | 0.013733 | -0.077819 | -0.004577 | 122.8317 | 62.9059 | 122.6761 | 62.8922 | 122.6624 | 0.21515 | 122.8271 | 122.818 | 122.7951 | 122.905 | 122.7219 | 122.7722 | 122.7356 | -122.9462 | -122.7997 | 122.6944 | 122.8088 | 62.4252 | 62.9974
1252.8906 | 123.0011 | -62.709 | 60.0723 | -0.037537 | 0.0019803 | 0.061718 | 0.070649 | -0.0018799 | 0.00071784 | -0.0018307 | -0.049103 | 0.1648 | 0.1305 | -0.0025122 | 0.059242 | 0.10564 | -0.0025037 | -0.20599 | 60.0174 | -62.8098 | 60.0449 | -62.5351 | -62.8693 | 60.1685 | 0.48523 | 59.9854 | -62.7319 | 60.0952 | 60.1913 | 60.0357 | 0.28381 | -0.10071 | -0.054932 | -0.027466 | 0.17395 | 122.8775 | -0.16022 | 122.9782 | -0.05951 | -0.022889 | -0.086975 | 0.022888 | 122.9004 | 62.9929 | 122.7448 | 63.0157 | 122.7676 | 0.27466 | 122.8546 | 122.9233 | 122.8271 | 122.8271 | 122.7173 | 122.7264 | 122.6944 | -122.8821 | -122.8043 | 122.7539 | 122.8043 | 62.5031 | 63.1943
1253.8281 | 123.0103 | -62.7411 | 60.0632 | -0.060425 | 0.0015529 | 0.063427 | 0.070649 | 0.0013245 | -0.0029138 | -0.00097627 | -0.11929 | 0.16694 | 0.12901 | 0.0024012 | 0.058815 | 0.10607 | -0.0048535 | -0.24719 | 59.9945 | -62.8738 | 60.0174 | -62.5671 | -62.9562 | 60.1089 | 0.40741 | 59.9762 | -62.7594 | 60.0952 | 60.1639 | 59.9625 | 0.24261 | -0.13275 | -0.068664 | -0.045776 | 0.17395 | 122.85 | -0.21515 | 122.9828 | -0.082398 | -0.01831 | -0.086975 | 0.032044 | 122.905 | 62.9837 | 122.7036 | 63.002 | 122.7219 | 0.3067 | 122.8912 | 122.9233 | 122.8546 | 122.8683 | 122.7356 | 122.7356 | 122.7173 | -122.937 | -122.8226 | 122.7585 | 122.8363 | 62.4939 | 63.1485
1254.8906 | 123.111 | -62.6953 | 60.0586 | -0.075684 | 0.0011257 | 0.061077 | 0.066591 | 0.0011109 | -0.0020594 | -0.0026853 | -0.027741 | 0.16331 | 0.12922 | -0.011271 | 0.05796 | 0.1035 | -0.00015387 | -0.22888 | 60.0037 | -62.8235 | 60.1089 | -62.4481 | -62.8418 | 60.228 | 0.5722 | 59.9533 | -62.6953 | 60.1547 | 60.2783 | 60.1044 | 0.32044 | -0.12817 | -0.054932 | 0.050354 | 0.24719 | 122.9233 | -0.14648 | 123.0515 | -0.018311 | 0 | -0.10529 | 0.09613 | 122.9736 | 63.0157 | 122.7997 | 63.0157 | 122.7997 | 0.37537 | 122.9324 | 122.9736 | 122.85 | 122.8271 | 122.6486 | 122.699 | 122.6486 | -122.8821 | -122.7539 | 122.8043 | 122.85 | 62.4664 | 63.2675
1255.8281 | 122.9919 | -62.7457 | 60.0906 | -0.052796 | 0.0024075 | 0.062572 | 0.068727 | 0.0021789 | -0.00099116 | -0.0016171 | -0.14066 | 0.16566 | 0.12901 | -0.0040076 | 0.059028 | 0.10607 | -0.0039991 | -0.29297 | 60.0128 | -62.8784 | 59.9899 | -62.6083 | -62.9974 | 60.0769 | 0.37537 | 59.9945 | -62.7502 | 60.0311 | 60.0998 | 59.9213 | 0.16022 | -0.13275 | -0.07782 | -0.10071 | 0.13733 | 122.8226 | -0.25177 | 122.9553 | -0.11902 | -0.004577 | -0.09613 | -0.059509 | 122.8455 | 62.9059 | 122.6669 | 62.9105 | 122.6715 | 0.27008 | 122.8683 | 122.85 | 122.7814 | 122.8912 | 122.7448 | 122.7585 | 122.7402 | -122.9691 | -122.8409 | 122.7356 | 122.7768 | 62.4527 | 63.121
1256.8906 | 123.0652 | -62.709 | 60.0357 | -0.1062 | 0.0041165 | 0.063854 | 0.067872 | 0.0026063 | 0.00093144 | -0.00097627 | -0.064362 | 0.16523 | 0.12944 | -0.0069982 | 0.05796 | 0.10415 | -0.0016493 | -0.31128 | 59.9854 | -62.851 | 60.0311 | -62.5397 | -62.9471 | 60.1273 | 0.42114 | 59.9258 | -62.7594 | 60.1044 | 60.1822 | 60.0128 | 0.17853 | -0.14191 | -0.050354 | -0.004578 | 0.16937 | 122.8363 | -0.23804 | 122.9782 | -0.096131 | -0.050354 | -0.10986 | 0.068664 | 122.8912 | 62.8876 | 122.7219 | 62.9379 | 122.7722 | 0.31128 | 122.8821 | 122.9416 | 122.8638 | 122.8363 | 122.6852 | 122.6944 | 122.6349 | -122.8867 | -122.7951 | 122.7402 | 122.8134 | 62.3978 | 63.1302
1257.8281 | 123.0194 | -62.7045 | 60.0769 | -0.052796 | 0.0011257 | 0.062572 | 0.068086 | 0.0045289 | -0.0016322 | 0.0015871 | -0.10098 | 0.16587 | 0.12944 | -0.0097754 | 0.057747 | 0.10628 | -0.0010083 | -0.25635 | 59.9854 | -62.8601 | 60.0266 | -62.5214 | -63.1897 | 60.0723 | 0.44403 | 60.0037 | -62.7457 | 60.0769 | 60.1685 | 59.9854 | 0.22888 | -0.15564 | -0.091552 | -0.050354 | 0.18311 | 122.7768 | -0.48523 | 122.9324 | -0.32959 | -0.041199 | -0.073242 | 0 | 122.8729 | 62.9333 | 122.6898 | 62.9745 | 122.731 | 0.33874 | 122.8867 | 122.9141 | 122.8226 | 122.8455 | 122.7493 | 122.6898 | 122.7081 | -122.937 | -122.8226 | 122.731 | 122.7814 | 62.4481 | 63.1485
1258.8281 | 123.0103 | -62.7228 | 60.0952 | 0.023498 | 0.0017667 | 0.061932 | 0.070436 | 0.0015381 | -0.0020594 | -0.0014035 | -0.085724 | 0.1648 | 0.13136 | -0.0055028 | 0.057747 | 0.10521 | -0.0031445 | -0.43488 | 60.0586 | -62.8738 | 59.9396 | -62.6221 | -62.9471 | 60.0998 | 0.40741 | 60.022 | -62.7548 | 60.054 | 60.1364 | 59.9716 | 0.27008 | -0.15106 | -0.036621 | -0.15564 | 0.10071 | 122.8226 | -0.22431 | 122.9736 | -0.073243 | -0.032044 | -0.073242 | -0.041199 | 122.8592 | 62.9929 | 122.6944 | 63.0249 | 122.7264 | 0.25177 | 122.8134 | 122.8912 | 122.8088 | 122.9324 | 122.7768 | 122.7814 | 122.7448 | -122.9691 | -122.85 | 122.6624 | 122.7768 | 62.2879 | 63.1302
1259.8906 | 123.024 | -62.709 | 60.0494 | -0.052796 | 0.0026211 | 0.063427 | 0.070222 | 0.0021789 | -0.0012048 | -0.0035397 | -0.052155 | 0.16566 | 0.13115 | -0.0089208 | 0.059028 | 0.105 | 0.00070073 | -0.32044 | 59.9899 | -62.8464 | 59.9945 | -62.5854 | -62.9379 | 60.1318 | 0.39368 | 59.967 | -62.7274 | 60.0998 | 60.1547 | 59.9899 | 0.2243 | -0.13733 | -0.059509 | -0.054931 | 0.1236 | 122.8409 | -0.22888 | 122.9782 | -0.091552 | -0.018311 | -0.082397 | 0.050354 | 122.8638 | 62.9333 | 122.699 | 62.9517 | 122.7173 | 0.26093 | 122.8409 | 122.8821 | 122.8271 | 122.8363 | 122.6944 | 122.699 | 122.6761 | -122.8958 | -122.7768 | 122.7036 | 122.8088 | 62.3886 | 63.1027
1260.8281 | 123.0148 | -62.7182 | 60.0769 | -0.068054 | 0.0013393 | 0.06065 | 0.068513 | 0.0021789 | -0.0020594 | -0.00012167 | -0.14066 | 0.16502 | 0.12986 | 0.0011194 | 0.058815 | 0.10329 | 0.0019823 | -0.24719 | 59.9854 | -62.8647 | 60.0266 | -62.5854 | -62.9379 | 60.1181 | 0.45776 | 60.0174 | -62.7411 | 59.9899 | 60.2325 | 59.9899 | 0.21973 | -0.14648 | -0.091552 | -0.050354 | 0.13275 | 122.8363 | -0.21973 | 122.9828 | -0.073242 | -0.022888 | -0.059509 | -0.086975 | 122.9507 | 62.9379 | 122.7081 | 62.9608 | 122.731 | 0.27924 | 122.8912 | 122.9736 | 122.731 | 122.85 | 122.7585 | 122.7036 | 122.7356 | -122.9416 | -122.818 | 122.7448 | 122.7081 | 62.471 | 63.176
1261.8906 | 123.056 | -62.677 | 60.0311 | -0.15961 | 5.7742e-05 | 0.061504 | 0.067872 | 4.2692e-05 | -0.0027002 | 0.00094633 | -0.094879 | 0.16416 | 0.12944 | 5.1352e-05 | 0.056465 | 0.1065 | 0.00091433 | -0.28381 | 59.9579 | -62.8647 | 60.0403 | -62.5534 | -62.9333 | 60.141 | 0.41657 | 59.9396 | -62.7594 | 60.1639 | 59.9762 | 60.2554 | 0.33875 | -0.18768 | -0.073242 | 0.009155 | 0.1236 | 122.818 | -0.25635 | 123.0057 | -0.068665 | -0.082397 | -0.091553 | 0.13275 | 122.6532 | 63.0157 | 122.9324 | 63.0981 | 123.0148 | 0.31128 | 122.905 | 122.7356 | 122.9233 | 122.8226 | 122.699 | 122.6349 | 122.6166 | -122.8958 | -122.7905 | 122.7173 | 122.8409 | 62.3932 | 63.0936
1262.8281 | 122.8683 | -62.6907 | 60.1044 | -0.007019 | 0.00069854 | 0.062359 | 0.069581 | -0.0018799 | -0.0014184 | -0.0041807 | -0.067413 | 0.16758 | 0.13072 | -0.003153 | 0.05796 | 0.10436 | 0.00091433 | -0.27924 | 60.0494 | -62.8555 | 59.9808 | -62.6038 | -62.9425 | 60.0769 | 0.41657 | 60.022 | -62.7365 | 60.0449 | 60.0952 | 60.2097 | 0.5127 | -0.1648 | -0.054932 | -0.1236 | 0.086975 | 122.7676 | -0.25177 | 122.9324 | -0.086975 | -0.045776 | -0.082397 | -0.059509 | 122.7859 | 63.2034 | 122.9004 | 63.2492 | 122.9462 | 0.25177 | 122.8363 | 122.8317 | 122.7814 | 122.905 | 122.7585 | 122.7402 | 122.7127 | -122.9599 | -122.8409 | 122.6715 | 122.7356 | 62.4115 | 63.1073
1263.8906 | 123.0789 | -62.7182 | 60.0128 | -0.052796 | 0.0039029 | 0.061077 | 0.067872 | 0.0034607 | -0.0033412 | -0.0028989 | -0.12234 | 0.16395 | 0.13136 | -0.00058965 | 0.058601 | 0.10521 | 0.0030505 | -0.32501 | 59.9716 | -62.8784 | 60.0174 | -62.5626 | -62.9562 | 60.1044 | 0.36163 | 59.9396 | -62.7365 | 60.141 | 60.1868 | 60.0174 | 0.20142 | -0.16022 | -0.041198 | 0.004578 | 0.15564 | 122.8226 | -0.23804 | 122.9828 | -0.07782 | -0.01831 | -0.073242 | 0.12817 | 122.905 | 62.9196 | 122.7356 | 62.9379 | 122.7539 | 0.31586 | 122.8958 | 122.9233 | 122.8775 | 122.85 | 122.6761 | 122.6898 | 122.6578 | -122.8912 | -122.7493 | 122.7356 | 122.8592 | 62.3932 | 63.0798
1264.8281 | 122.9691 | -62.7365 | 60.1135 | -0.045166 | 0.0034757 | 0.063213 | 0.068727 | -0.00038451 | -0.002273 | -0.0018307 | -0.055206 | 0.16459 | 0.13093 | 0.0017602 | 0.060524 | 0.10393 | -0.00015387 | -0.22888 | 60.0128 | -62.8464 | 59.9991 | -62.5854 | -62.9379 | 60.1135 | 0.47607 | 60.0266 | -62.7228 | 60.0403 | 60.1547 | 59.9716 | 0.24261 | -0.10986 | -0.10071 | -0.11444 | 0.15106 | 122.85 | -0.20142 | 122.9599 | -0.091552 | 0.013733 | -0.086975 | -0.073242 | 122.8912 | 62.9791 | 122.7081 | 62.9654 | 122.6944 | 0.26093 | 122.8455 | 122.8775 | 122.7631 | 122.8592 | 122.7493 | 122.7493 | 122.7631 | -122.9599 | -122.8363 | 122.7356 | 122.7768 | 62.5076 | 63.2126
1265.8906 | 123.0972 | -62.6999 | 60.0266 | -0.12909 | 0.0036893 | 0.06065 | 0.068941 | -0.0046569 | 0.00029044 | -0.0016171 | -0.10709 | 0.16502 | 0.13093 | -0.0025122 | 0.058601 | 0.10521 | -0.0016493 | -0.27008 | 59.9762 | -62.8693 | 60.0266 | -62.5397 | -62.9196 | 60.1227 | 0.40741 | 59.9258 | -62.7548 | 60.1273 | 60.2005 | 60.0174 | 0.20142 | -0.16937 | -0.050354 | 0 | 0.16022 | 122.8226 | -0.21973 | 122.9919 | -0.050354 | -0.054932 | -0.10071 | 0.10071 | 122.9004 | 62.9013 | 122.7173 | 62.9562 | 122.7722 | 0.32959 | 122.8958 | 122.9553 | 122.8821 | 122.8455 | 122.6807 | 122.6761 | 122.6257 | -122.8958 | -122.7814 | 122.7264 | 122.8271 | 62.4298 | 63.1073
1266.8281 | 122.9919 | -62.7274 | 60.0998 | -0.022278 | 0.0013393 | 0.061291 | 0.06595 | 0.00089729 | -0.0012048 | -0.0050351 | -0.082672 | 0.16502 | 0.12815 | -0.0035802 | 0.060096 | 0.10457 | -0.0014355 | -0.28839 | 60.0311 | -62.8418 | 59.9854 | -62.6083 | -62.9562 | 60.0952 | 0.4303 | 60.0403 | -62.7319 | 60.0357 | 60.1456 | 59.9579 | 0.24261 | -0.11444 | -0.068664 | -0.11444 | 0.11902 | 122.8226 | -0.22888 | 122.937 | -0.11444 | -0.004578 | -0.059509 | -0.064086 | 122.8729 | 62.97 | 122.6852 | 62.9745 | 122.6898 | 0.23346 | 122.8271 | 122.8775 | 122.7676 | 122.8729 | 122.7722 | 122.7585 | 122.7676 | -122.9416 | -122.8317 | 122.7127 | 122.7631 | 62.439 | 63.1577
1267.8281 | 122.9645 | -62.7319 | 60.1044 | -0.022278 | 5.7742e-05 | 0.059795 | 0.069795 | 0.0011109 | -0.0012048 | -0.00076267 | -0.10709 | 0.16544 | 0.12837 | -0.0042212 | 0.06031 | 0.10628 | -0.00079467 | -0.25177 | 60.0357 | -62.8464 | 59.9899 | -62.6175 | -62.9333 | 60.1089 | 0.42572 | 60.0082 | -62.7365 | 60.0449 | 60.1547 | 59.9854 | 0.25635 | -0.11444 | -0.068664 | -0.11444 | 0.11444 | 122.8409 | -0.20142 | 122.9553 | -0.086975 | -0.004577 | -0.09613 | -0.059509 | 122.8867 | 62.9883 | 122.7173 | 62.9929 | 122.7219 | 0.22888 | 122.8363 | 122.8912 | 122.7814 | 122.8821 | 122.7448 | 122.7676 | 122.7402 | -122.9507 | -122.8409 | 122.7219 | 122.7768 | 62.4802 | 63.1577
1268.8906 | 123.0789 | -62.7365 | 60.0037 | -0.083313 | 0.0024075 | 0.060223 | 0.069154 | -0.0012391 | 7.6842e-05 | 0.00030553 | -0.070465 | 0.16352 | 0.12901 | -0.0044348 | 0.058815 | 0.10479 | -0.0010083 | -0.32959 | 59.9396 | -62.8647 | 60.0311 | -62.5259 | -62.915 | 60.1318 | 0.42114 | 59.935 | -62.7319 | 60.1181 | 60.2005 | 60.0128 | 0.17395 | -0.12817 | -0.064087 | 0.027466 | 0.21057 | 122.8683 | -0.17853 | 122.9965 | -0.050354 | 0.004577 | -0.068664 | 0.11444 | 122.937 | 62.9105 | 122.7493 | 62.9059 | 122.7448 | 0.33875 | 122.8958 | 122.9324 | 122.85 | 122.8043 | 122.6669 | 122.6761 | 122.6715 | -122.8683 | -122.7356 | 122.7676 | 122.8546 | 62.4069 | 63.1577
1269.8281 | 123.0103 | -62.7182 | 60.0906 | -0.052796 | 0.0021939 | 0.062359 | 0.068727 | 0.0023925 | -0.00077756 | -0.00076267 | -0.1315 | 0.16459 | 0.12837 | 0.00069215 | 0.057747 | 0.10585 | -0.0029309 | -0.23346 | 60.0266 | -62.8647 | 60.0174 | -62.558 | -62.9196 | 60.0998 | 0.46692 | 59.9899 | -62.7594 | 60.0769 | 60.1776 | 59.9945 | 0.26093 | -0.14648 | -0.064087 | -0.073242 | 0.16022 | 122.818 | -0.20142 | 122.9645 | -0.054932 | -0.041198 | -0.10071 | -0.013733 | 122.8958 | 62.9791 | 122.7127 | 63.0203 | 122.7539 | 0.3067 | 122.8821 | 122.937 | 122.8363 | 122.8912 | 122.7493 | 122.7448 | 122.7081 | -122.9553 | -122.85 | 122.7356 | 122.7951 | 62.4847 | 63.1851
1270.8906 | 123.0652 | -62.7182 | 60.0128 | -0.14435 | 0.0021939 | 0.064709 | 0.067659 | 0.0023925 | -0.0033412 | -0.0020443 | -0.097931 | 0.16459 | 0.13093 | -0.0035802 | 0.058815 | 0.10543 | 0.0013415 | -0.29297 | 59.9258 | -62.8693 | 60.022 | -62.5397 | -62.9379 | 60.1181 | 0.39368 | 59.9213 | -62.7365 | 60.1318 | 60.2097 | 60.0357 | 0.19226 | -0.15106 | -0.086975 | 0.009156 | 0.17853 | 122.8363 | -0.21973 | 122.9874 | -0.068664 | -0.01831 | -0.091552 | 0.11902 | 122.9279 | 62.9105 | 122.7539 | 62.9288 | 122.7722 | 0.32959 | 122.8912 | 122.9462 | 122.8683 | 122.7951 | 122.6578 | 122.644 | 122.6395 | -122.8821 | -122.7493 | 122.7402 | 122.85 | 62.4252 | 63.1119
1271.8281 | 123.0057 | -62.7228 | 60.0998 | -0.068054 | 0.0015529 | 0.062786 | 0.070436 | -0.0020935 | -0.00099116 | -0.0028989 | -0.085724 | 0.16672 | 0.13157 | -0.0029394 | 0.060096 | 0.1065 | -0.0022901 | -0.2655 | 60.0266 | -62.8738 | 59.967 | -62.6358 | -62.9517 | 60.0998 | 0.40283 | 60.022 | -62.7228 | 60.0449 | 60.1639 | 59.9808 | 0.26093 | -0.15106 | -0.073242 | -0.13275 | 0.086975 | 122.8226 | -0.22888 | 122.9736 | -0.07782 | 0 | -0.077819 | -0.054931 | 122.8867 | 62.9837 | 122.7036 | 62.9837 | 122.7036 | 0.23804 | 122.8409 | 122.8867 | 122.7676 | 122.9004 | 122.7448 | 122.7493 | 122.7448 | -122.9736 | -122.8226 | 122.6898 | 122.7676 | 62.4573 | 63.1256
1272.8906 | 123.0148 | -62.7182 | 60.0174 | -0.098572 | 0.0019803 | 0.061932 | 0.069154 | -0.0040161 | -0.0029138 | -0.00054907 | -0.058258 | 0.16523 | 0.1305 | -0.00016245 | 0.057319 | 0.10286 | -0.0025037 | -0.3067 | 59.9762 | -62.8647 | 60.0174 | -62.5442 | -62.9654 | 60.1227 | 0.39368 | 59.9121 | -62.7594 | 60.0815 | 60.1639 | 59.9854 | 0.16479 | -0.14648 | -0.041199 | 0 | 0.17395 | 122.8409 | -0.24719 | 122.9874 | -0.10071 | -0.041198 | -0.10529 | 0.064087 | 122.8821 | 62.883 | 122.7036 | 62.9242 | 122.7448 | 0.32044 | 122.8821 | 122.9233 | 122.8409 | 122.8409 | 122.6715 | 122.6944 | 122.6303 | -122.8821 | -122.7768 | 122.7356 | 122.7997 | 62.4115 | 63.1119
1273.8281 | 122.9462 | -62.7411 | 60.0861 | -0.029907 | -0.0025059 | 0.059582 | 0.068086 | -0.00038451 | -0.0024866 | -0.0020443 | -0.088776 | 0.1648 | 0.13072 | 0.0017602 | 0.059242 | 0.10479 | -0.0046399 | -0.28381 | 60.0266 | -62.851 | 59.9808 | -62.6312 | -62.9517 | 60.0952 | 0.4303 | 60.022 | -62.7182 | 60.0449 | 60.141 | 59.9396 | 0.25177 | -0.10986 | -0.05951 | -0.10529 | 0.10986 | 122.8363 | -0.21057 | 122.9462 | -0.10071 | 0.022888 | -0.064087 | -0.041199 | 122.8821 | 62.9929 | 122.6807 | 62.97 | 122.6578 | 0.21973 | 122.8317 | 122.8592 | 122.7631 | 122.8775 | 122.7402 | 122.7676 | 122.7631 | -122.937 | -122.8043 | 122.7219 | 122.7859 | 62.4573 | 63.1714
1274.8906 | 123.0789 | -62.6907 | 60.0357 | -0.1062 | -0.0010105 | 0.061718 | 0.067018 | -0.00038451 | -0.00035036 | -0.0014035 | -0.049103 | 0.16608 | 0.13072 | -0.0052892 | 0.055824 | 0.10521 | -0.0037855 | -0.26093 | 59.9808 | -62.8235 | 60.054 | -62.5122 | -62.883 | 60.1639 | 0.50812 | 59.9579 | -62.7228 | 60.1547 | 60.2371 | 60.1181 | 0.32044 | -0.13275 | -0.054932 | 0.01831 | 0.17853 | 122.8546 | -0.19226 | 122.9874 | -0.05951 | -0.032043 | -0.07782 | 0.11902 | 122.9279 | 63.0112 | 122.8088 | 63.0432 | 122.8409 | 0.31128 | 122.8775 | 122.9599 | 122.8775 | 122.8043 | 122.6807 | 122.6715 | 122.6486 | -122.8592 | -122.7585 | 122.7448 | 122.8455 | 62.4298 | 63.1989
1275.8281 | 123.0103 | -62.7045 | 60.0861 | -0.022278 | 0.0013393 | 0.062786 | 0.069581 | 0.00025629 | -0.002273 | 9.193e-05 | -0.11929 | 0.16459 | 0.12858 | -0.0018712 | 0.054969 | 0.10415 | -0.0010083 | -0.23804 | 60.0174 | -62.8555 | 59.9945 | -62.5854 | -62.9333 | 60.1227 | 0.44403 | 60.0266 | -62.7365 | 60.1044 | 60.1776 | 59.9808 | 0.26093 | -0.15106 | -0.068665 | -0.091553 | 0.11902 | 122.8271 | -0.22888 | 122.9782 | -0.07782 | -0.032043 | -0.05951 | 0.01831 | 122.8821 | 62.9654 | 122.6852 | 62.9974 | 122.7173 | 0.27008 | 122.85 | 122.9141 | 122.8409 | 122.8729 | 122.7631 | 122.7219 | 122.731 | -122.9416 | -122.8226 | 122.699 | 122.8088 | 62.4664 | 63.1485
1276.8906 | 123.1018 | -62.7136 | 60.054 | -0.098572 | 0.0013393 | 0.061718 | 0.0683 | 0.0038879 | -0.00099116 | -0.0035397 | -0.036896 | 0.16544 | 0.12944 | -0.00037605 | 0.056465 | 0.10393 | -0.0018629 | -0.27008 | 59.9716 | -62.8372 | 60.0586 | -62.5168 | -62.8784 | 60.173 | 0.50812 | 59.967 | -62.7228 | 60.1364 | 60.2554 | 60.0815 | 0.30212 | -0.1236 | -0.082397 | 0.004578 | 0.19684 | 122.8867 | -0.1648 | 123.0103 | -0.041199 | -0.009155 | -0.086975 | 0.082398 | 122.9691 | 63.0157 | 122.7951 | 63.0249 | 122.8043 | 0.32043 | 122.8958 | 122.9782 | 122.8592 | 122.8088 | 122.6898 | 122.6852 | 122.6807 | -122.8912 | -122.7768 | 122.7722 | 122.85 | 62.4435 | 63.2217
1277.8281 | 123.0377 | -62.7045 | 60.0861 | -0.060425 | 0.00069854 | 0.063854 | 0.068727 | -0.0020935 | -0.00077756 | 0.0013735 | -0.12845 | 0.16566 | 0.13008 | -0.0025122 | 0.058174 | 0.10607 | -0.0025037 | -0.24719 | 60.0357 | -62.8418 | 59.9991 | -62.5946 | -62.9425 | 60.1318 | 0.45776 | 60.0082 | -62.7274 | 60.0815 | 60.1868 | 59.9899 | 0.27008 | -0.13733 | -0.050354 | -0.086976 | 0.10986 | 122.8363 | -0.23804 | 122.9736 | -0.10071 | -0.022888 | -0.07782 | -0.004578 | 122.8912 | 62.9745 | 122.6944 | 62.9974 | 122.7173 | 0.24719 | 122.8409 | 122.9141 | 122.8088 | 122.8775 | 122.7356 | 122.7402 | 122.7127 | -122.9279 | -122.8134 | 122.7036 | 122.7859 | 62.4573 | 63.1622
1278.8906 | 123.0515 | -62.6907 | 60.054 | -0.052796 | 0.0019803 | 0.06535 | 0.065523 | -0.0010253 | -0.0031274 | 9.193e-05 | -0.046051 | 0.16437 | 0.12709 | -0.00058965 | 0.058815 | 0.10308 | -0.00036747 | -0.15564 | 60.0266 | -62.7731 | 59.9945 | -62.4802 | -62.8006 | 60.1639 | 0.55389 | 59.9945 | -62.709 | 60.1318 | 60.2463 | 60.0677 | 0.32501 | -0.082397 | -0.027466 | -0.059509 | 0.21057 | 122.8546 | -0.10986 | 122.937 | -0.027466 | -0.01831 | -0.059509 | 0.07782 | 122.937 | 63.0157 | 122.7585 | 63.0341 | 122.7768 | 0.29297 | 122.7676 | 122.9553 | 122.8409 | 122.7997 | 122.7036 | 122.7173 | 122.6852 | -122.8271 | -122.7631 | 122.6852 | 122.8226 | 62.5351 | 63.2446
1279.8438 | 123.0743 | -62.7228 | 60.0174 | -0.1062 | 0.0011257 | 0.062786 | 0.070009 | 0.0036743 | -0.0014184 | -0.00033547 | -0.097931 | 0.16373 | 0.12837 | -0.0040076 | 0.059242 | 0.10628 | -0.0050671 | -0.28839 | 59.9304 | -62.8647 | 60.0449 | -62.5442 | -62.915 | 60.1181 | 0.4303 | 59.9442 | -62.7319 | 59.9899 | 60.4477 | 60.1135 | 0.19684 | -0.14191 | -0.086975 | 0.027466 | 0.17853 | 122.8409 | -0.19226 | 122.9828 | -0.050354 | -0.009156 | -0.073242 | -0.027466 | 123.1705 | 62.9196 | 122.8363 | 62.9288 | 122.8455 | 0.32044 | 122.9095 | 123.1796 | 122.7219 | 122.7951 | 122.6761 | 122.6532 | 122.6669 | -122.8821 | -122.7493 | 122.7676 | 122.7127 | 62.4344 | 63.1531
1280.8281 | 122.9691 | -62.7411 | 60.0998 | -0.029907 | 0.0015529 | 0.061504 | 0.066804 | -0.0016663 | -0.0029138 | -0.0024717 | -0.055206 | 0.16566 | 0.12986 | 0.0015466 | 0.058174 | 0.10479 | -0.0039991 | -0.24261 | 60.0403 | -62.8372 | 60.0037 | -62.5763 | -62.9425 | 60.1181 | 0.43945 | 60.0449 | -62.7319 | 60.0357 | 60.1547 | 59.9808 | 0.25635 | -0.09613 | -0.059509 | -0.09613 | 0.1648 | 122.8592 | -0.20142 | 122.9553 | -0.10529 | 0.009155 | -0.054931 | -0.064086 | 122.8958 | 62.9974 | 122.7219 | 62.9883 | 122.7127 | 0.26093 | 122.8409 | 122.8867 | 122.7676 | 122.8775 | 122.7768 | 122.7814 | 122.7859 | -122.937 | -122.8317 | 122.7448 | 122.7768 | 62.4985 | 63.1805
1281.8906 | 123.0515 | -62.7365 | 60.0311 | -0.11383 | 0.0013393 | 0.061718 | 0.068941 | 0.0049561 | -0.0031274 | -0.0031125 | -0.07962 | 0.16267 | 0.12922 | -0.0042212 | 0.057533 | 0.1035 | -0.0029309 | -0.31586 | 59.9762 | -62.8555 | 60.0037 | -62.558 | -62.9517 | 60.1135 | 0.37994 | 59.9442 | -62.7457 | 60.0769 | 60.1547 | 60.0037 | 0.17395 | -0.11902 | -0.054932 | -0.027466 | 0.17853 | 122.85 | -0.21515 | 122.9691 | -0.09613 | -0.009156 | -0.086975 | 0.045776 | 122.8912 | 62.9105 | 122.7402 | 62.9196 | 122.7493 | 0.29755 | 122.8592 | 122.9004 | 122.8226 | 122.8317 | 122.6898 | 122.7127 | 122.6807 | -122.8867 | -122.7768 | 122.7402 | 122.8134 | 62.4207 | 63.1165
1282.8281 | 122.9416 | -62.6587 | 60.0952 | -0.037537 | 0.00069854 | 0.060009 | 0.066804 | 0.0011109 | -0.0031274 | 0.00094633 | -0.10098 | 0.16651 | 0.12794 | 0.00090575 | 0.057319 | 0.10692 | 0.00070073 | -0.27924 | 60.0677 | -62.8693 | 59.9625 | -62.6175 | -62.9562 | 60.0952 | 0.42572 | 60.0357 | -62.7365 | 60.0357 | 60.173 | 60.1089 | 0.48523 | -0.21057 | -0.027466 | -0.13275 | 0.041198 | 122.7539 | -0.29755 | 122.9645 | -0.086975 | -0.07782 | -0.059509 | -0.059509 | 122.8317 | 63.1439 | 122.7676 | 63.2217 | 122.8455 | 0.25177 | 122.8317 | 122.9095 | 122.7722 | 122.937 | 122.7722 | 122.7264 | 122.6944 | -122.9645 | -122.8317 | 122.6212 | 122.6944 | 62.3795 | 63.0844
1283.8906 | 123.0789 | -62.7182 | 59.9945 | -0.15198 | 0.0028347 | 0.063427 | 0.069581 | 0.0019653 | -0.0018458 | -0.0041807 | -0.12234 | 0.16523 | 0.12687 | 5.1352e-05 | 0.05796 | 0.10692 | 0.00027333 | -0.28381 | 59.9487 | -62.8601 | 59.9899 | -62.7869 | -62.7869 | 60.2783 | 0.48981 | 59.9487 | -62.7274 | 60.1135 | 60.2051 | 60.0128 | 0.1831 | -0.14191 | -0.045777 | -0.004578 | -0.068664 | 122.9965 | -0.068664 | 123.1384 | 0.073242 | -0.009155 | -0.045777 | 0.11902 | 122.9233 | 62.9013 | 122.731 | 62.9105 | 122.7402 | 0.073242 | 122.85 | 122.9324 | 122.8409 | 122.8088 | 122.6761 | 122.6669 | 122.6669 | -122.8546 | -122.7219 | 122.7081 | 122.8317 | 62.4344 | 63.208
1284.8438 | 123.0743 | -62.7136 | 59.9808 | -0.083313 | 0.0015529 | 0.063 | 0.069581 | 0.00089729 | -0.00505 | -0.0014035 | -0.1254 | 0.16395 | 0.13093 | -0.002085 | 0.058174 | 0.10436 | 0.00027333 | -0.31128 | 59.9991 | -62.9059 | 60.0037 | -62.59 | -62.9562 | 60.1044 | 0.37537 | 59.9213 | -62.7319 | 60.1089 | 60.173 | 60.0128 | 0.17853 | -0.19226 | 0.01831 | 0.022888 | 0.1236 | 122.818 | -0.24262 | 123.0103 | -0.050354 | -0.018311 | -0.059509 | 0.12817 | 122.8867 | 62.8922 | 122.7264 | 62.9105 | 122.7448 | 0.31586 | 122.9095 | 122.905 | 122.8409 | 122.905 | 122.6532 | 122.7127 | 122.6349 | -122.8867 | -122.7127 | 122.7173 | 122.8226 | 62.4023 | 63.089
1285.8906 | 123.0469 | -62.7182 | 59.9945 | -0.12146 | 0.0017667 | 0.062572 | 0.066163 | 0.0032471 | 0.00029044 | -0.0016171 | -0.082672 | 0.16437 | 0.12901 | -0.0022986 | 0.059242 | 0.10842 | -0.00036747 | -0.28839 | 59.9716 | -62.8326 | 60.0357 | -62.5351 | -62.9242 | 60.1135 | 0.43945 | 59.9121 | -62.7274 | 60.1044 | 60.1776 | 60.0082 | 0.19226 | -0.11444 | -0.022888 | 0.041199 | 0.18311 | 122.8317 | -0.20599 | 122.9462 | -0.091552 | -0.009155 | -0.082398 | 0.10986 | 122.8958 | 62.9105 | 122.7264 | 62.9196 | 122.7356 | 0.29755 | 122.8683 | 122.905 | 122.8317 | 122.8043 | 122.6395 | 122.6898 | 122.6303 | -122.8271 | -122.7219 | 122.7539 | 122.8226 | 62.4298 | 63.1577
1286.8281 | 122.9782 | -62.7319 | 60.0677 | -0.052796 | 0.00091214 | 0.061077 | 0.068941 | -0.0016663 | -0.0020594 | 9.193e-05 | -0.10709 | 0.16608 | 0.12965 | -0.0016576 | 0.059883 | 0.10607 | -0.0044263 | -0.28381 | 60.0357 | -62.851 | 59.967 | -62.5992 | -62.9562 | 60.0769 | 0.4303 | 60.0266 | -62.7365 | 59.9625 | 60.1685 | 59.8846 | 0.20599 | -0.11902 | -0.032043 | -0.10071 | 0.13275 | 122.8088 | -0.2243 | 122.9279 | -0.10529 | -0.004577 | -0.041199 | -0.10529 | 122.9004 | 62.9379 | 122.6166 | 62.9425 | 122.6212 | 0.25177 | 122.818 | 122.905 | 122.699 | 122.8867 | 122.7631 | 122.7676 | 122.7585 | -122.9187 | -122.8043 | 122.699 | 122.6944 | 62.4481 | 63.1622
1287.8281 | 123.024 | -62.6907 | 60.1273 | -0.068054 | -0.0014377 | 0.062145 | 0.069795 | 0.0036743 | -0.0016322 | 0.00030553 | -0.07962 | 0.16608 | 0.13179 | -0.0042212 | 0.058387 | 0.10329 | -0.0033581 | -0.27466 | 60.0266 | -62.851 | 59.967 | -62.6083 | -62.9425 | 60.1135 | 0.43488 | 60.0311 | -62.7319 | 60.0403 | 60.1364 | 59.8846 | 0.33417 | -0.16022 | -0.10071 | -0.16022 | 0.082398 | 122.8043 | -0.25177 | 122.9645 | -0.091553 | -0.041199 | -0.09613 | -0.086975 | 122.8271 | 63.0249 | 122.5754 | 63.0661 | 122.6166 | 0.24262 | 122.818 | 122.8683 | 122.7722 | 122.8775 | 122.7631 | 122.7173 | 122.7219 | -122.9782 | -122.8592 | 122.6578 | 122.731 | 62.4161 | 63.1256
1288.8906 | 123.0469 | -62.6678 | 60.022 | -0.060425 | 0.0019803 | 0.061504 | 0.068513 | -0.0027343 | -0.0018458 | -0.0039671 | -0.052155 | 0.16416 | 0.13072 | -0.0050756 | 0.059883 | 0.10415 | 0.0013415 | -0.26093 | 59.9945 | -62.8281 | 60.054 | -62.5259 | -62.8738 | 60.1501 | 0.50354 | 59.9716 | -62.709 | 60.1364 | 60.2463 | 60.0769 | 0.3067 | -0.16022 | -0.027466 | 0.032043 | 0.14191 | 122.818 | -0.20599 | 122.9782 | -0.045776 | -0.041198 | -0.050354 | 0.11444 | 122.9141 | 62.9745 | 122.7448 | 63.0157 | 122.7859 | 0.30212 | 122.8821 | 122.9553 | 122.8455 | 122.8226 | 122.6807 | 122.6624 | 122.6395 | -122.85 | -122.731 | 122.7219 | 122.8043 | 62.4069 | 63.1714
1289.8438 | 123.0194 | -62.7411 | 60.0449 | -0.16724 | 0.0015529 | 0.060863 | 0.071504 | -0.0012391 | -0.0024866 | -0.0024717 | -0.15897 | 0.16758 | 0.12773 | -0.0016576 | 0.058387 | 0.10521 | -0.0020765 | -0.33875 | 60.0082 | -62.8967 | 59.9304 | -62.6678 | -63.0569 | 60.0449 | 0.29755 | 59.967 | -62.7686 | 60.0357 | 60.1044 | 59.9167 | 0.11444 | -0.15564 | -0.036621 | -0.11444 | 0.073242 | 122.7859 | -0.31586 | 122.9416 | -0.16022 | -0.027466 | -0.07782 | -0.009155 | 122.8455 | 62.8555 | 122.6578 | 62.883 | 122.6852 | 0.22888 | 122.8271 | 122.8729 | 122.8043 | 122.905 | 122.7356 | 122.7493 | 122.7081 | -122.9416 | -122.8134 | 122.6715 | 122.7768 | 62.4023 | 63.0386
1290.8906 | 123.0698 | -62.7045 | 60.0357 | -0.090943 | 0.0026211 | 0.061718 | 0.0683 | -0.0014527 | -0.0014184 | -0.0011899 | -0.046051 | 0.16651 | 0.13072 | -0.0074254 | 0.058174 | 0.10521 | -0.0042127 | -0.3067 | 59.9716 | -62.8601 | 59.9899 | -62.5717 | -62.9333 | 60.1089 | 0.3891 | 59.9487 | -62.7365 | 60.0906 | 60.1547 | 59.9945 | 0.20142 | -0.15564 | -0.064087 | -0.045777 | 0.13275 | 122.8134 | -0.22888 | 122.9691 | -0.073243 | -0.032043 | -0.086976 | 0.054931 | 122.8592 | 62.9059 | 122.699 | 62.9379 | 122.731 | 0.28839 | 122.85 | 122.8912 | 122.8271 | 122.8317 | 122.6852 | 122.6761 | 122.6532 | -122.8958 | -122.7722 | 122.6944 | 122.7951 | 62.3978 | 63.0936
1291.8281 | 123.0194 | -62.7136 | 60.0769 | -0.052796 | 0.0028347 | 0.061932 | 0.068941 | 0.0030335 | -0.00505 | -0.00054907 | -0.13455 | 0.16416 | 0.1305 | 0.00047855 | 0.058601 | 0.10628 | -0.0037855 | -0.22888 | 60.0266 | -62.8555 | 60.0037 | -62.5854 | -62.9379 | 60.1135 | 0.46692 | 60.0037 | -62.7457 | 60.0861 | 60.173 | 59.9945 | 0.26093 | -0.14191 | -0.050354 | -0.073242 | 0.12817 | 122.8271 | -0.2243 | 122.9691 | -0.082397 | -0.032044 | -0.073242 | 0.009156 | 122.8867 | 62.9745 | 122.7081 | 63.0066 | 122.7402 | 0.27008 | 122.8592 | 122.9187 | 122.8317 | 122.8821 | 122.7493 | 122.7402 | 122.7173 | -122.9324 | -122.8226 | 122.7173 | 122.7997 | 62.4847 | 63.1805
1292.8906 | 123.0331 | -62.7228 | 60.0174 | -0.15198 | 0.0024075 | 0.062572 | 0.068941 | 0.00025629 | -0.0052638 | -0.0024717 | -0.073517 | 0.16395 | 0.12794 | -0.00016245 | 0.060096 | 0.10393 | -0.0020765 | -0.32959 | 59.9808 | -62.8784 | 59.9945 | -62.5763 | -62.9379 | 60.1181 | 0.37537 | 59.9533 | -62.7365 | 60.0769 | 60.173 | 59.9991 | 0.19226 | -0.15564 | -0.036621 | -0.022888 | 0.14648 | 122.8409 | -0.21515 | 122.9965 | -0.059509 | -0.013733 | -0.064087 | 0.059509 | 122.8958 | 62.915 | 122.7219 | 62.9288 | 122.7356 | 0.30212 | 122.8729 | 122.9095 | 122.8134 | 122.8592 | 122.6898 | 122.7036 | 122.6761 | -122.8958 | -122.7539 | 122.7173 | 122.7997 | 62.3932 | 63.0981
1293.8281 | 122.9645 | -62.709 | 60.0769 | -0.1825 | 0.0026211 | 0.060436 | 0.067872 | -0.00059811 | -0.0018458 | -0.0037533 | -0.1254 | 0.16544 | 0.13157 | 5.1352e-05 | 0.058815 | 0.10692 | -0.0035719 | -0.27466 | 60.0449 | -62.8647 | 59.9716 | -62.5946 | -62.97 | 60.0769 | 0.40283 | 60.0037 | -62.7136 | 60.054 | 60.1364 | 59.9625 | 0.24719 | -0.15564 | -0.032043 | -0.10529 | 0.11444 | 122.7859 | -0.26093 | 122.9416 | -0.10529 | -0.004578 | -0.073242 | -0.022888 | 122.8455 | 62.9562 | 122.6715 | 62.9608 | 122.6761 | 0.27008 | 122.8363 | 122.85 | 122.7676 | 122.9095 | 122.7173 | 122.7539 | 122.7127 | -122.9416 | -122.7905 | 122.6807 | 122.7631 | 62.4344 | 63.1119
1294.9062 | 122.9782 | -62.7182 | 60.0449 | -0.090943 | 0.0017667 | 0.061504 | 0.067659 | -0.00017091 | -0.0020594 | -0.00054907 | -0.16507 | 0.16672 | 0.12965 | -0.0035802 | 0.059456 | 0.10692 | 0.00091433 | -0.27008 | 59.9854 | -62.8647 | 59.9762 | -62.5992 | -62.9791 | 60.0586 | 0.40283 | 60.0082 | -62.7731 | 60.054 | 60.1135 | 59.9121 | 0.16937 | -0.14648 | -0.059509 | -0.068665 | 0.11902 | 122.7768 | -0.26093 | 122.9233 | -0.11444 | -0.054931 | -0.036621 | 0.009155 | 122.8317 | 62.8876 | 122.6303 | 62.9425 | 122.6852 | 0.2655 | 122.8409 | 122.8867 | 122.8271 | 122.85 | 122.7814 | 122.7036 | 122.7264 | -122.9095 | -122.818 | 122.6944 | 122.7722 | 62.4481 | 63.121
1295.8281 | 122.9828 | -62.6999 | 60.0815 | -0.060425 | 0.0017667 | 0.061077 | 0.068086 | -0.0044433 | -0.0024866 | -0.0014035 | -0.085724 | 0.16651 | 0.13157 | -0.010203 | 0.058387 | 0.105 | -0.0018629 | -0.27008 | 60.0494 | -62.8555 | 59.9487 | -62.5854 | -63.0524 | 60.0815 | 0.40283 | 59.9899 | -62.7365 | 60.022 | 60.1273 | 59.9625 | 0.25635 | -0.15564 | -0.032044 | -0.13275 | 0.11444 | 122.7814 | -0.35248 | 122.937 | -0.19684 | -0.036621 | -0.091553 | -0.059509 | 122.8271 | 62.9562 | 122.6624 | 62.9929 | 122.699 | 0.27008 | 122.8043 | 122.8638 | 122.7585 | 122.905 | 122.7264 | 122.7493 | 122.6898 | -122.937 | -122.818 | 122.6486 | 122.7219 | 62.4298 | 63.1027
1296.8906 | 122.9874 | -62.7411 | 60.0677 | -0.052796 | 0.00091214 | 0.060436 | 0.067659 | -0.00038451 | -0.00077756 | -0.0028989 | -0.12234 | 0.16416 | 0.12922 | -0.0012304 | 0.059669 | 0.10628 | 0.0017687 | -0.25635 | 60.0449 | -62.8281 | 59.9854 | -62.6129 | -62.9333 | 60.0906 | 0.45776 | 60.0266 | -62.7319 | 60.0632 | 60.1959 | 59.9716 | 0.27008 | -0.086975 | -0.022888 | -0.082397 | 0.12817 | 122.8317 | -0.19226 | 122.9187 | -0.10529 | 0.009155 | -0.041199 | -0.004578 | 122.937 | 63.0112 | 122.7127 | 63.002 | 122.7036 | 0.21515 | 122.8134 | 122.9279 | 122.7951 | 122.8729 | 122.7585 | 122.7859 | 122.7676 | -122.8958 | -122.7997 | 122.7264 | 122.8043 | 62.4847 | 63.1989
1297.8281 | 123.0286 | -62.709 | 60.1044 | -0.014649 | 0.0013393 | 0.059368 | 0.067872 | -0.0029479 | -0.0020594 | -0.0024717 | -0.091827 | 0.16544 | 0.1288 | -0.0044348 | 0.059242 | 0.10521 | -0.0018629 | -0.25177 | 60.0403 | -62.8464 | 59.9716 | -62.6175 | -62.9379 | 60.1044 | 0.4303 | 60.022 | -62.7411 | 60.054 | 60.1685 | 59.967 | 0.26093 | -0.13733 | -0.064087 | -0.13275 | 0.091552 | 122.8134 | -0.22888 | 122.9507 | -0.091552 | -0.032044 | -0.082397 | -0.050354 | 122.8775 | 62.97 | 122.6761 | 63.002 | 122.7081 | 0.22888 | 122.818 | 122.9095 | 122.7951 | 122.8867 | 122.7631 | 122.7493 | 122.731 | -122.9507 | -122.8455 | 122.6807 | 122.7631 | 62.4573 | 63.1393
1298.8906 | 123.0743 | -62.6953 | 60.0311 | -0.13672 | 0.0015529 | 0.061504 | 0.067018 | 0.00068369 | -0.0016322 | -0.0039671 | -0.033844 | 0.16352 | 0.12944 | -0.011057 | 0.059456 | 0.1035 | -0.00036747 | -0.27924 | 59.9991 | -62.8326 | 60.0128 | -62.5259 | -62.9013 | 60.141 | 0.4715 | 59.9442 | -62.7274 | 60.1318 | 60.2417 | 60.0586 | 0.26093 | -0.13733 | -0.032044 | -0.018311 | 0.16937 | 122.8363 | -0.20599 | 122.9736 | -0.068664 | -0.032044 | -0.086975 | 0.10071 | 122.937 | 62.9562 | 122.7539 | 62.9883 | 122.7859 | 0.3067 | 122.8455 | 122.9691 | 122.8592 | 122.8317 | 122.6715 | 122.6944 | 122.6395 | -122.8638 | -122.7585 | 122.7081 | 122.8271 | 62.4161 | 63.1668
1299.8438 | 123.0377 | -62.7045 | 60.0128 | -0.16724 | 0.0036893 | 0.062359 | 0.066591 | -0.0029479 | -0.0029138 | -0.0011899 | -0.088776 | 0.16544 | 0.12837 | -0.004862 | 0.057319 | 0.10585 | -0.0018629 | -0.2655 | 59.9396 | -62.8464 | 60.0449 | -62.5122 | -62.9333 | 60.1135 | 0.43488 | 59.9213 | -62.7365 | 60.0952 | 60.173 | 59.9945 | 0.1831 | -0.14191 | -0.073242 | 0.032044 | 0.19226 | 122.818 | -0.22888 | 122.9599 | -0.086975 | -0.032043 | -0.091552 | 0.082398 | 122.8775 | 62.8876 | 122.699 | 62.9196 | 122.731 | 0.33417 | 122.8912 | 122.9095 | 122.8317 | 122.7859 | 122.6578 | 122.644 | 122.6257 | -122.8592 | -122.7493 | 122.7493 | 122.7997 | 62.439 | 63.1393
1300.8906 | 123.0469 | -62.7136 | 60.0449 | -0.068054 | 0.0013393 | 0.060863 | 0.068086 | -0.0031617 | -0.0029138 | -0.0024717 | -0.046051 | 0.16544 | 0.12773 | -0.0052892 | 0.057533 | 0.10393 | -0.0042127 | -0.2655 | 59.9808 | -62.8281 | 60.0128 | -62.5397 | -62.8922 | 60.141 | 0.46692 | 59.9762 | -62.7319 | 60.1135 | 60.2234 | 60.0494 | 0.2655 | -0.11444 | -0.064087 | -0.032044 | 0.17395 | 122.8546 | -0.17853 | 122.9691 | -0.064087 | -0.018311 | -0.068665 | 0.068664 | 122.937 | 62.9791 | 122.7631 | 62.9974 | 122.7814 | 0.28839 | 122.8409 | 122.9553 | 122.8455 | 122.8088 | 122.7081 | 122.6944 | 122.6898 | -122.8729 | -122.7768 | 122.7264 | 122.8271 | 62.4481 | 63.1805
1301.8281 | 122.9507 | -62.7319 | 60.0861 | -0.098572 | 0.00091214 | 0.059368 | 0.068727 | -0.0059387 | -0.0031274 | -0.0018307 | -0.11624 | 0.16587 | 0.13008 | 0.0021876 | 0.055824 | 0.10671 | 0.0017687 | -0.27008 | 60.0357 | -62.8555 | 59.9533 | -62.6129 | -62.9608 | 60.0906 | 0.43488 | 60.0311 | -62.7228 | 59.9396 | 60.1135 | 59.935 | 0.21515 | -0.1236 | -0.050354 | -0.13275 | 0.11902 | 122.8226 | -0.22888 | 122.9462 | -0.10528 | 0.009156 | -0.054932 | -0.14649 | 122.8455 | 62.9471 | 122.6669 | 62.9379 | 122.6578 | 0.24262 | 122.8088 | 122.8363 | 122.6624 | 122.8912 | 122.7539 | 122.7676 | 122.7631 | -122.9416 | -122.8088 | 122.6852 | 122.6715 | 62.4619 | 63.1668
1302.8906 | 123.0469 | -62.7182 | 60.0403 | -0.12146 | 0.0028347 | 0.061932 | 0.071504 | 0.00046989 | -0.00056396 | 9.193e-05 | -0.067413 | 0.16437 | 0.12815 | 0.0017602 | 0.059456 | 0.10628 | 0.0041187 | -0.30212 | 59.9625 | -62.8555 | 60.0082 | -62.5442 | -62.9517 | 60.1181 | 0.39825 | 59.9442 | -62.7457 | 60.0723 | 60.1456 | 59.9762 | 0.16022 | -0.13733 | -0.07782 | -0.032043 | 0.17395 | 122.8363 | -0.23346 | 122.9736 | -0.09613 | -0.027466 | -0.09613 | 0.032044 | 122.8638 | 62.8784 | 122.6944 | 62.9059 | 122.7219 | 0.31128 | 122.8638 | 122.8912 | 122.818 | 122.818 | 122.6898 | 122.6807 | 122.6624 | -122.8958 | -122.7859 | 122.7264 | 122.7905 | 62.4161 | 63.1165
1303.8281 | 123.0286 | -62.709 | 60.0449 | -0.045166 | 0.0013393 | 0.061718 | 0.070222 | -0.0027343 | -0.00099116 | -0.0011899 | -0.14676 | 0.16694 | 0.12602 | -0.0052892 | 0.058601 | 0.10692 | -0.0012219 | -0.24261 | 60.0174 | -62.851 | 60.0174 | -62.5534 | -62.9425 | 60.0815 | 0.44861 | 59.9945 | -62.7136 | 60.0632 | 60.173 | 59.9808 | 0.21057 | -0.14191 | -0.027466 | -0.027466 | 0.15564 | 122.7905 | -0.23346 | 122.9324 | -0.091553 | -0.004578 | -0.050354 | 0.01831 | 122.8821 | 62.9196 | 122.6898 | 62.9242 | 122.6944 | 0.29755 | 122.8683 | 122.8867 | 122.7768 | 122.8683 | 122.7081 | 122.7264 | 122.7036 | -122.8958 | -122.7585 | 122.7264 | 122.7722 | 62.4664 | 63.1577
1304.8281 | 122.9279 | -62.709 | 60.0906 | -0.068054 | 0.00069854 | 0.061291 | 0.067872 | 4.2692e-05 | -0.0012048 | -0.00097627 | -0.088776 | 0.16502 | 0.13072 | 0.00069215 | 0.060096 | 0.10372 | -0.0014355 | -0.27924 | 60.054 | -62.851 | 59.9579 | -62.5946 | -62.9654 | 60.0906 | 0.43488 | 60.0266 | -62.7274 | 60.0357 | 60.1227 | 59.9487 | 0.2243 | -0.14191 | -0.036621 | -0.13275 | 0.11444 | 122.7997 | -0.25635 | 122.9416 | -0.11444 | -0.018311 | -0.064087 | -0.054931 | 122.8317 | 62.9333 | 122.6578 | 62.9517 | 122.6761 | 0.25635 | 122.8088 | 122.85 | 122.7631 | 122.905 | 122.7539 | 122.7631 | 122.7356 | -122.9416 | -122.818 | 122.6669 | 122.7448 | 62.4298 | 63.1439
1305.8906 | 123.0927 | -62.6907 | 60.054 | -0.090943 | 0.0015529 | 0.060009 | 0.068086 | -0.0044433 | -0.0016322 | -0.0014035 | -0.046051 | 0.16587 | 0.12837 | -0.00080325 | 0.057106 | 0.10457 | 0.00048713 | -0.21515 | 59.9625 | -62.8098 | 60.0861 | -62.4344 | -62.8052 | 60.2051 | 0.55847 | 59.9487 | -62.7274 | 60.1593 | 60.2783 | 60.0906 | 0.31586 | -0.11902 | -0.091553 | 0.032044 | 0.25635 | 122.8958 | -0.11444 | 123.0148 | 0.004577 | -0.036621 | -0.10529 | 0.10529 | 122.9691 | 63.0066 | 122.7814 | 63.0432 | 122.818 | 0.37537 | 122.8958 | 123.0057 | 122.8867 | 122.7722 | 122.6761 | 122.6532 | 122.6395 | -122.8638 | -122.7814 | 122.7768 | 122.85 | 62.4756 | 63.2492
1306.8281 | 122.9507 | -62.7274 | 60.0723 | -0.052796 | 0.0015529 | 0.062786 | 0.068727 | 0.00089729 | -0.0018458 | -0.0035397 | -0.088776 | 0.16395 | 0.12944 | -0.0063574 | 0.059883 | 0.10308 | -0.00015387 | -0.24719 | 60.022 | -62.8464 | 59.9716 | -62.5992 | -62.9425 | 60.0906 | 0.44861 | 60.0311 | -62.7548 | 60.022 | 60.1456 | 59.9533 | 0.24261 | -0.11902 | -0.050354 | -0.10071 | 0.12817 | 122.818 | -0.21515 | 122.937 | -0.09613 | -0.027466 | -0.041199 | -0.050354 | 122.8729 | 62.97 | 122.6807 | 62.9974 | 122.7081 | 0.24719 | 122.818 | 122.9004 | 122.7768 | 122.8683 | 122.7859 | 122.7493 | 122.7585 | -122.9187 | -122.8271 | 122.699 | 122.7493 | 62.4802 | 63.176
1307.8906 | 123.0377 | -62.7045 | 60.0266 | -0.090943 | 0.00091214 | 0.061718 | 0.070009 | -0.0016663 | -0.0024866 | -0.0022581 | -0.046051 | 0.16502 | 0.13115 | -0.0078528 | 0.058174 | 0.10585 | -0.0025037 | -0.31128 | 59.967 | -62.8143 | 59.9899 | -62.5763 | -62.9288 | 60.1044 | 0.39368 | 59.9533 | -62.7136 | 60.0998 | 60.1593 | 59.9808 | 0.21515 | -0.10986 | -0.059509 | -0.036621 | 0.12817 | 122.8088 | -0.2243 | 122.9187 | -0.11444 | -0.009155 | -0.073242 | 0.073242 | 122.8638 | 62.9196 | 122.6852 | 62.9288 | 122.6944 | 0.23804 | 122.8043 | 122.8729 | 122.8134 | 122.7814 | 122.6669 | 122.6715 | 122.6578 | -122.8409 | -122.7402 | 122.6944 | 122.8043 | 62.3932 | 63.0981
1308.8281 | 123.0377 | -62.6816 | 60.054 | -0.037537 | 0.0030483 | 0.062786 | 0.068513 | 0.0015381 | -0.0012048 | -0.0028989 | -0.088776 | 0.16138 | 0.13157 | -0.00058965 | 0.05796 | 0.10479 | -0.0020765 | -0.27924 | 59.9579 | -62.8235 | 60.0677 | -62.4893 | -62.851 | 60.1639 | 0.54016 | 59.9899 | -62.6953 | 60.1089 | 60.2325 | 60.0494 | 0.31128 | -0.14191 | -0.09613 | 0.013733 | 0.19226 | 122.8455 | -0.16937 | 122.9874 | -0.027466 | -0.013732 | -0.064087 | 0.054932 | 122.9141 | 62.9929 | 122.731 | 63.0066 | 122.7448 | 0.33417 | 122.8912 | 122.9279 | 122.8043 | 122.7814 | 122.6852 | 122.6395 | 122.6715 | -122.8775 | -122.7493 | 122.7493 | 122.7905 | 62.4023 | 63.2217
1309.8906 | 123.0606 | -62.7045 | 60.0311 | -0.098572 | 0.0017667 | 0.061718 | 0.069154 | 0.00025629 | -0.0041956 | -0.00076267 | -0.07962 | 0.16309 | 0.12944 | -0.0052892 | 0.056465 | 0.10543 | -0.0050671 | -0.29755 | 59.9396 | -62.8555 | 60.1776 | -62.5488 | -62.8922 | 60.1868 | 0.44861 | 59.9167 | -62.7411 | 60.1273 | 60.1959 | 60.0174 | 0.17853 | -0.15106 | -0.091553 | 0.14648 | 0.15564 | 122.8912 | -0.18768 | 123.0423 | -0.036621 | -0.036621 | -0.11444 | 0.09613 | 122.9004 | 62.883 | 122.7219 | 62.9196 | 122.7585 | 0.3067 | 123.0331 | 122.937 | 122.8683 | 122.7951 | 122.6578 | 122.644 | 122.6212 | -122.8867 | -122.7722 | 122.8821 | 122.8317 | 62.4069 | 63.1531
1310.8281 | 122.9462 | -62.7045 | 60.1089 | -0.022278 | 0.0028347 | 0.060009 | 0.068086 | 0.0041015 | -0.0033412 | 9.193e-05 | -0.094879 | 0.16544 | 0.13221 | 0.0049646 | 0.058174 | 0.10585 | -0.0031445 | -0.2655 | 60.022 | -62.8601 | 59.9625 | -62.6129 | -62.9425 | 60.0906 | 0.44403 | 60.0174 | -62.7182 | 60.0357 | 60.1135 | 59.9442 | 0.24261 | -0.15564 | -0.086975 | -0.14648 | 0.091553 | 122.7951 | -0.23804 | 122.9507 | -0.082398 | -0.013733 | -0.091553 | -0.073242 | 122.818 | 62.9471 | 122.6486 | 62.9608 | 122.6624 | 0.24719 | 122.8226 | 122.8317 | 122.7539 | 122.8821 | 122.7356 | 122.7264 | 122.7219 | -122.9691 | -122.8271 | 122.6669 | 122.7402 | 62.439 | 63.1485
1311.8906 | 123.0743 | -62.7228 | 59.9899 | -0.1062 | 0.0017667 | 0.061504 | 0.070222 | 0.0028199 | -0.00056396 | -0.00054907 | -0.13455 | 0.16566 | 0.13072 | 0.00090575 | 0.058174 | 0.10436 | -0.00079467 | -0.32501 | 59.967 | -62.8693 | 60.0037 | -62.5946 | -62.9745 | 60.0677 | 0.37994 | 59.9396 | -62.7365 | 60.1089 | 60.1868 | 59.9899 | 0.1831 | -0.14648 | -0.022888 | 0.013733 | 0.12817 | 122.7905 | -0.25177 | 122.937 | -0.10529 | -0.013733 | -0.050354 | 0.11902 | 122.9095 | 62.9059 | 122.7127 | 62.9196 | 122.7264 | 0.27466 | 122.8729 | 122.9233 | 122.8455 | 122.8363 | 122.6761 | 122.6898 | 122.6624 | -122.8592 | -122.7264 | 122.7264 | 122.8317 | 62.3978 | 63.1027
1312.8281 | 122.9462 | -62.7182 | 60.0677 | -0.052796 | 0.0015529 | 0.060009 | 0.069368 | -0.00081171 | -0.0014184 | -0.0026853 | -0.082672 | 0.16459 | 0.13093 | -0.0018712 | 0.059242 | 0.10607 | -0.0048535 | -0.22888 | 60.0311 | -62.8235 | 59.9899 | -62.5763 | -62.9333 | 60.0998 | 0.44403 | 60.0082 | -62.7182 | 60.0403 | 60.1273 | 59.9579 | 0.25177 | -0.10529 | -0.036621 | -0.07782 | 0.14191 | 122.818 | -0.21515 | 122.9233 | -0.10986 | 0 | -0.059509 | -0.027466 | 122.8455 | 62.97 | 122.6761 | 62.97 | 122.6761 | 0.24719 | 122.8134 | 122.8455 | 122.7585 | 122.8546 | 122.7264 | 122.7493 | 122.7264 | -122.8912 | -122.7859 | 122.7081 | 122.7585 | 62.4893 | 63.1622
1313.8906 | 123.0469 | -62.6862 | 60.054 | -0.083313 | 0.0032619 | 0.060223 | 0.068727 | -0.00059811 | -0.00077756 | -0.0033261 | -0.033844 | 0.16373 | 0.12922 | -0.0027258 | 0.05796 | 0.10585 | -0.0048535 | -0.27466 | 59.9625 | -62.8555 | 60.0037 | -62.5442 | -62.9105 | 60.141 | 0.44403 | 59.9625 | -62.7182 | 60.1089 | 60.2005 | 60.0403 | 0.25177 | -0.16937 | -0.091553 | -0.050354 | 0.14191 | 122.8271 | -0.2243 | 122.9965 | -0.054931 | -0.032044 | -0.091553 | 0.054932 | 122.8867 | 62.9379 | 122.7264 | 62.97 | 122.7585 | 0.31128 | 122.8592 | 122.9187 | 122.8271 | 122.818 | 122.6807 | 122.6486 | 122.6486 | -122.9095 | -122.7722 | 122.6898 | 122.7951 | 62.4115 | 63.1302
1314.8281 | 122.9965 | -62.6953 | 60.0769 | -0.060425 | 0.0011257 | 0.062145 | 0.067445 | -0.0014527 | -0.0012048 | -0.0014035 | -0.14676 | 0.16544 | 0.13093 | -0.003153 | 0.05561 | 0.10521 | -0.0014355 | -0.24261 | 60.0357 | -62.8693 | 60.0037 | -62.5717 | -62.9333 | 60.1044 | 0.46234 | 60.0037 | -62.7319 | 60.0632 | 60.173 | 59.9899 | 0.24719 | -0.17395 | -0.041198 | -0.073242 | 0.1236 | 122.7997 | -0.23804 | 122.9736 | -0.064087 | -0.036622 | -0.073242 | -0.013733 | 122.8683 | 62.9425 | 122.6852 | 62.9791 | 122.7219 | 0.29755 | 122.8729 | 122.905 | 122.7951 | 122.905 | 122.7356 | 122.731 | 122.699 | -122.9462 | -122.8088 | 122.699 | 122.7585 | 62.4527 | 63.1577
1315.8281 | 122.9324 | -62.7136 | 60.0861 | -0.12909 | 0.00091214 | 0.060863 | 0.069795 | -0.00017091 | -0.003982 | 0.00030553 | -0.07962 | 0.16608 | 0.13093 | -0.0063574 | 0.059669 | 0.10607 | -0.0039991 | -0.24719 | 60.0266 | -62.8876 | 59.967 | -62.6038 | -62.9562 | 60.0815 | 0.43488 | 60.0403 | -62.7411 | 60.0494 | 60.1456 | 59.9442 | 0.23804 | -0.17395 | -0.05951 | -0.11902 | 0.10986 | 122.7951 | -0.24262 | 122.9691 | -0.068665 | -0.027466 | -0.045777 | -0.036622 | 122.8592 | 62.9517 | 122.6578 | 62.9791 | 122.6852 | 0.28381 | 122.8546 | 122.8867 | 122.7905 | 122.9141 | 122.7814 | 122.7402 | 122.7539 | -122.9736 | -122.8271 | 122.6807 | 122.7631 | 62.4664 | 63.1485
1316.8906 | 123.0377 | -63.6108 | 59.0652 | -0.22827 | 0.070981 | 0.13029 | 0.069795 | 0.0028199 | -0.00099116 | -0.0024717 | -0.10403 | 0.16373 | 0.12965 | 0.00047855 | 0.057533 | 0.10543 | 0.00070073 | -0.27466 | 59.0103 | -63.7848 | 59.079 | 59.1614 | -63.826 | 59.1614 | 0.42572 | 58.9966 | -63.6841 | 59.1751 | 59.2346 | 59.0424 | 0.16937 | -0.17395 | -0.054932 | 0.013732 | 122.7722 | 122.7722 | -0.21515 | 122.9462 | -0.041199 | -0.073242 | -0.068665 | 0.10986 | 122.8455 | 63.7802 | 122.6532 | 63.8535 | 122.7264 | 122.9462 | 122.8638 | 122.9187 | 122.8592 | 122.7951 | 122.6807 | 122.6212 | 122.6074 | -122.85 | -122.7493 | 122.6898 | 122.7859 | 63.3362 | 64.0366
1317.8281 | 123.0103 | -63.6475 | 59.1019 | -0.15961 | 0.071621 | 0.12944 | 0.070222 | -0.00017091 | -0.0012048 | 0.0018009 | -0.15591 | 0.16502 | 0.1273 | 0.0028284 | 0.059456 | 0.10778 | -0.0039991 | -0.23346 | 59.0424 | -63.7802 | 59.079 | 59.1293 | -63.8626 | 59.1431 | 0.47607 | 59.0652 | -63.6612 | 59.1339 | 59.2209 | 59.0424 | 0.25635 | -0.13275 | -0.05951 | -0.022889 | 122.7768 | 122.7905 | -0.21515 | 122.9233 | -0.082398 | -0.013733 | -0.036621 | 0.032043 | 122.8683 | 63.9038 | 122.6898 | 63.9175 | 122.7036 | 122.9095 | 122.8592 | 122.8821 | 122.7951 | 122.8226 | 122.7264 | 122.6898 | 122.7127 | -122.8821 | -122.7631 | 122.7264 | 122.7814 | 63.414 | 64.1235
1318.8906 | 123.1247 | -63.6475 | 59.0698 | -0.15198 | 0.06799 | 0.12858 | 0.068727 | -0.0031617 | 7.6842e-05 | -0.0016171 | -0.027741 | 0.16608 | 0.12858 | -0.0093482 | 0.060096 | 0.10436 | -0.0033581 | -0.20599 | 59.0469 | -63.7665 | 59.1293 | 59.23 | -63.7573 | 59.2209 | 0.55389 | 59.0195 | -63.6292 | 59.317 | 59.4955 | 58.8089 | 0.12817 | -0.11902 | -0.022888 | 0.059509 | 122.8775 | 122.8683 | -0.10986 | 122.9874 | 0.009155 | 0.018311 | -0.050354 | 0.24719 | 123.143 | 63.7756 | 122.4564 | 63.7573 | 122.438 | 122.9965 | 122.8958 | 123.1247 | 122.9462 | 122.8134 | 122.6486 | 122.6944 | 122.6669 | -122.8363 | -122.699 | 122.7768 | 122.9645 | 63.4415 | 64.2014
1319.8281 | 122.9553 | -63.652 | 59.1293 | 0.076904 | 0.066708 | 0.1288 | 0.069581 | 0.00089729 | -0.0012048 | 0.00073273 | -0.11319 | 0.16373 | 0.12751 | -0.003153 | 0.057533 | 0.105 | -0.0039991 | -0.32044 | 59.1202 | -63.7848 | 58.9966 | 59.0378 | -63.8626 | 59.1339 | 0.42572 | 59.0836 | -63.6841 | 59.1019 | 59.1934 | 59.024 | 0.25177 | -0.13275 | -0.009155 | -0.13275 | 122.6898 | 122.7859 | -0.21057 | 122.9187 | -0.07782 | -0.032043 | -0.045776 | -0.027465 | 122.8455 | 63.9038 | 122.6761 | 63.9359 | 122.7081 | 122.8226 | 122.7814 | 122.8775 | 122.7859 | 122.905 | 122.7676 | 122.7722 | 122.7356 | -122.9141 | -122.8134 | 122.6486 | 122.7539 | 63.3316 | 64.0778
1320.8906 | 123.0194 | -63.6429 | 59.0744 | -0.15961 | 0.069485 | 0.12901 | 0.0683 | -0.0010253 | -0.0018458 | -0.0014035 | -0.049103 | 0.16331 | 0.12794 | -0.0061438 | 0.058601 | 0.10479 | -0.00079467 | -0.28839 | 59.0424 | -63.7482 | 59.0652 | 59.166 | -63.8077 | 59.1797 | 0.46692 | 59.0103 | -63.6612 | 59.1705 | 59.285 | 59.1019 | 0.26093 | -0.10529 | -0.032044 | -0.009155 | 122.8088 | 122.8226 | -0.1648 | 122.9279 | -0.059509 | -0.018311 | -0.064087 | 0.09613 | 122.9279 | 63.9038 | 122.7448 | 63.9221 | 122.7631 | 122.9141 | 122.8134 | 122.9462 | 122.8317 | 122.7905 | 122.6715 | 122.6852 | 122.6532 | -122.8226 | -122.7356 | 122.7081 | 122.8134 | 63.3545 | 64.1098
1321.8281 | 122.9782 | -63.6703 | 59.1385 | -0.11383 | 0.071408 | 0.12773 | 0.068086 | 0.00068369 | -0.003982 | 9.193e-05 | -0.1254 | 0.16651 | 0.13243 | -0.0012304 | 0.057319 | 0.10564 | -0.00036747 | -0.26093 | 59.0744 | -63.7985 | 59.0149 | 59.0927 | -63.8763 | 59.1248 | 0.41657 | 59.0561 | -63.652 | 59.1156 | 59.198 | 59.0149 | 0.24719 | -0.12817 | -0.064087 | -0.1236 | 122.7631 | 122.7951 | -0.20599 | 122.9233 | -0.07782 | 0.01831 | -0.082398 | -0.022888 | 122.8683 | 63.9175 | 122.6852 | 63.8992 | 122.6669 | 122.8912 | 122.8134 | 122.85 | 122.7676 | 122.8729 | 122.7081 | 122.7448 | 122.7264 | -122.937 | -122.7905 | 122.6852 | 122.7859 | 63.4094 | 64.0869
1322.8906 | 123.0789 | -63.6475 | 59.0744 | -0.13672 | 0.070767 | 0.12858 | 0.068513 | 0.0011109 | -0.0037684 | -0.0020443 | -0.039948 | 0.16373 | 0.12922 | -0.0044348 | 0.059456 | 0.10372 | -0.0044263 | -0.20142 | 59.0286 | -63.7436 | 59.1385 | 59.2484 | -63.7527 | 59.2209 | 0.5722 | 58.992 | -63.62 | 59.2758 | 59.5688 | 58.8409 | 0.1236 | -0.09613 | -0.045777 | 0.064087 | 122.8958 | 122.8683 | -0.10529 | 122.9645 | -0.009156 | 0.027466 | -0.082398 | 0.20142 | 123.2162 | 63.7711 | 122.4884 | 63.7436 | 122.4609 | 122.9919 | 122.8821 | 123.1888 | 122.8958 | 122.7722 | 122.612 | 122.6761 | 122.6395 | -122.818 | -122.6944 | 122.7859 | 122.9233 | 63.446 | 64.2197
1323.8281 | 122.9324 | -63.6429 | 59.1248 | -0.11383 | 0.068844 | 0.12858 | 0.067659 | 0.0013245 | -0.0031274 | -0.0022581 | -0.10403 | 0.16373 | 0.13029 | -0.0042212 | 0.058601 | 0.10628 | -0.0018629 | -0.24719 | 59.079 | -63.7665 | 59.0195 | 59.0973 | -63.8718 | 59.1385 | 0.4303 | 59.0607 | -63.6429 | 59.0836 | 59.1843 | 59.0012 | 0.24719 | -0.1236 | -0.045777 | -0.10529 | 122.7402 | 122.7814 | -0.22888 | 122.905 | -0.10529 | 0 | -0.064087 | -0.041199 | 122.8271 | 63.8901 | 122.644 | 63.8901 | 122.644 | 122.8638 | 122.7859 | 122.8271 | 122.7264 | 122.8455 | 122.7036 | 122.7219 | 122.7036 | -122.8912 | -122.7676 | 122.6624 | 122.7264 | 63.3957 | 64.0732
1324.8906 | 123.0011 | -63.6337 | 59.0652 | -0.16724 | 0.070767 | 0.12986 | 0.067018 | 0.0019653 | -0.00099116 | 9.193e-05 | -0.14371 | 0.16138 | 0.12901 | -0.0022986 | 0.057106 | 0.10671 | -0.0018629 | -0.28839 | 59.0012 | -63.7711 | 59.0744 | 59.1797 | -63.8397 | 59.1797 | 0.41657 | 58.9645 | -63.6658 | 59.0103 | 59.111 | 59.2987 | 0.32501 | -0.13733 | -0.064087 | 0.009155 | 122.8134 | 122.8134 | -0.20599 | 122.9507 | -0.068665 | -0.032043 | -0.10071 | -0.054932 | 122.7448 | 63.9587 | 122.9324 | 63.9908 | 122.9645 | 122.9507 | 122.8455 | 122.7768 | 122.6761 | 122.7722 | 122.6303 | 122.6349 | 122.5983 | -122.8363 | -122.731 | 122.7081 | 122.644 | 63.3453 | 64.0503
1325.8281 | 122.9462 | -63.6566 | 59.1568 | -0.075684 | 0.068417 | 0.12944 | 0.068727 | 0.0032471 | -0.0020594 | -0.0020443 | -0.1254 | 0.16395 | 0.12687 | 0.0028284 | 0.059028 | 0.10393 | -0.00058107 | -0.26093 | 59.0698 | -63.8077 | 59.0103 | 59.0927 | -63.8855 | 59.1202 | 0.41657 | 59.0652 | -63.6795 | 59.0973 | 59.2026 | 59.0057 | 0.24261 | -0.15106 | -0.086975 | -0.14648 | 122.7493 | 122.7768 | -0.22888 | 122.9279 | -0.07782 | -0.022888 | -0.091552 | -0.059509 | 122.8592 | 63.8992 | 122.6624 | 63.9221 | 122.6852 | 122.9004 | 122.818 | 122.8821 | 122.7768 | 122.8775 | 122.7448 | 122.7264 | 122.7219 | -122.9645 | -122.8363 | 122.6669 | 122.7539 | 63.3957 | 64.0732
1326.8906 | 123.0103 | -63.62 | 59.0881 | -0.083313 | 0.069272 | 0.12986 | 0.068941 | -0.0018799 | -0.0033412 | -0.0033261 | -0.073517 | 0.16181 | 0.1288 | -0.0018712 | 0.059669 | 0.10372 | 5.9726e-05 | -0.32959 | 59.024 | -63.7344 | 59.0103 | 59.1431 | -63.8397 | 59.1568 | 0.40283 | 59.0012 | -63.6703 | 59.1476 | 59.2529 | 59.0652 | 0.19684 | -0.11444 | -0.064087 | -0.07782 | 122.7631 | 122.7768 | -0.21973 | 122.8912 | -0.10529 | -0.050354 | -0.086975 | 0.059509 | 122.8729 | 63.8168 | 122.6852 | 63.8672 | 122.7356 | 122.8775 | 122.7448 | 122.9233 | 122.818 | 122.7585 | 122.6715 | 122.644 | 122.6212 | -122.8226 | -122.7585 | 122.6303 | 122.7676 | 63.2904 | 64.0228
1327.8281 | 122.9095 | -63.6566 | 59.1248 | -0.15198 | 0.070553 | 0.1273 | 0.067445 | 0.00068369 | -0.0024866 | -0.00076267 | -0.091827 | 0.16224 | 0.13072 | -0.0042212 | 0.058601 | 0.10457 | -0.0012219 | -0.23346 | 59.0469 | -63.7482 | 59.0332 | 59.111 | -63.8214 | 59.1476 | 0.44403 | 59.0698 | -63.6475 | 59.0927 | 59.1797 | 58.9966 | 0.22888 | -0.091553 | -0.07782 | -0.091553 | 122.7676 | 122.8043 | -0.16479 | 122.8958 | -0.073242 | 0.009155 | -0.054932 | -0.032044 | 122.8363 | 63.8855 | 122.6532 | 63.8763 | 122.644 | 122.8592 | 122.7814 | 122.8271 | 122.7402 | 122.7951 | 122.7173 | 122.7036 | 122.7264 | -122.8729 | -122.7722 | 122.6898 | 122.7493 | 63.4232 | 64.1006
1328.8906 | 123.0057 | -63.6108 | 59.0836 | -0.16724 | 0.066281 | 0.12815 | 0.068513 | 0.0019653 | -0.003982 | -0.00033547 | -0.052155 | 0.16267 | 0.13157 | -0.00016245 | 0.056678 | 0.10457 | -0.0039991 | -0.28381 | 59.0332 | -63.7619 | 59.0607 | 59.1385 | -63.8443 | 59.1797 | 0.43945 | 59.0012 | -63.6612 | 59.166 | 59.2438 | 59.0927 | 0.24719 | -0.15106 | -0.050354 | -0.022888 | 122.7493 | 122.7905 | -0.23346 | 122.9416 | -0.082397 | -0.050354 | -0.082397 | 0.082398 | 122.8546 | 63.858 | 122.7036 | 63.9084 | 122.7539 | 122.9004 | 122.8226 | 122.905 | 122.8271 | 122.7951 | 122.6624 | 122.644 | 122.612 | -122.8455 | -122.7448 | 122.6715 | 122.7768 | 63.327 | 64.0503
1329.8281 | 123.0423 | -63.6063 | 59.1064 | -0.1825 | 0.069485 | 0.12773 | 0.068086 | 0.00068369 | -0.002273 | -0.0084531 | -0.0002747 | 0.1648 | 0.12922 | -0.0033666 | 0.058815 | 0.10564 | -0.0014355 | -0.21057 | 59.0286 | -63.7253 | 59.2621 | 59.5367 | -64.0274 | 59.0149 | 0.44861 | 58.9966 | -63.6429 | 59.1888 | 59.3033 | 59.1248 | 0.30212 | -0.11902 | -0.07782 | 0.15564 | 123.143 | 122.6212 | -0.42114 | 122.7402 | -0.30212 | -0.036621 | -0.10986 | 0.082398 | 122.9095 | 63.9084 | 122.731 | 63.945 | 122.7676 | 123.262 | 122.9874 | 122.9462 | 122.8317 | 122.7539 | 122.6395 | 122.6349 | 122.6028 | -122.8317 | -122.7493 | 122.8683 | 122.7951 | 63.3957 | 64.0549
1330.8906 | 123.0057 | -63.62 | 59.0836 | -0.14435 | 0.069912 | 0.13179 | 0.069795 | -0.0010253 | -0.0035548 | -0.0016171 | -0.076569 | 0.16459 | 0.12516 | -0.0059302 | 0.056038 | 0.10393 | -0.0054945 | -0.3067 | 58.992 | -63.7527 | 59.024 | 59.1248 | -63.858 | 59.1293 | 0.39825 | 59.0149 | -63.6658 | 59.1339 | 59.2255 | 59.0149 | 0.1831 | -0.13275 | -0.091553 | -0.059509 | 122.7448 | 122.7493 | -0.23804 | 122.8821 | -0.10529 | -0.045776 | -0.068664 | 0.050354 | 122.8455 | 63.8031 | 122.6349 | 63.8489 | 122.6807 | 122.8775 | 122.7768 | 122.8912 | 122.7997 | 122.7448 | 122.6807 | 122.612 | 122.6349 | -122.8363 | -122.7493 | 122.644 | 122.7539 | 63.3133 | 64.0182
1331.8281 | 122.9599 | -63.6337 | 59.0927 | -0.16724 | 0.068631 | 0.13008 | 0.067018 | 0.0013245 | -0.0014184 | -0.00076267 | -0.076569 | 0.16395 | 0.12815 | -0.0089208 | 0.058601 | 0.10393 | -0.0025037 | -0.2243 | 59.0424 | -63.7436 | 59.0744 | 59.1843 | -63.8031 | 59.1843 | 0.49896 | 59.0469 | -63.6429 | 59.0973 | 59.2026 | 59.024 | 0.25635 | -0.10986 | -0.050354 | -0.01831 | 122.818 | 122.818 | -0.16937 | 122.9279 | -0.05951 | -0.009155 | -0.045776 | 0.004578 | 122.8363 | 63.8901 | 122.6578 | 63.8992 | 122.6669 | 122.9279 | 122.818 | 122.8455 | 122.7402 | 122.7859 | 122.6898 | 122.6761 | 122.6807 | -122.8363 | -122.7356 | 122.7081 | 122.731 | 63.4094 | 64.1327
1332.8906 | 123.0057 | -63.6383 | 59.079 | -0.15961 | 0.069485 | 0.12858 | 0.0683 | -0.00038451 | -0.0020594 | -0.0024717 | -0.097931 | 0.16352 | 0.12965 | -0.0033666 | 0.05796 | 0.10521 | -0.0014355 | -0.32044 | 58.9737 | -63.7802 | 59.0332 | 59.1293 | -63.8718 | 59.1248 | 0.36621 | 58.992 | -63.6566 | 59.1339 | 59.2117 | 59.0149 | 0.16022 | -0.14191 | -0.10528 | -0.045776 | 122.7676 | 122.7631 | -0.23346 | 122.905 | -0.091553 | -0.01831 | -0.086975 | 0.054932 | 122.85 | 63.7985 | 122.6532 | 63.8168 | 122.6715 | 122.9095 | 122.8134 | 122.8683 | 122.7905 | 122.7539 | 122.6486 | 122.612 | 122.6303 | -122.8592 | -122.7356 | 122.6715 | 122.7722 | 63.3179 | 64.0045
1333.8281 | 123.0331 | -63.5971 | 59.0927 | -0.12146 | 0.068844 | 0.1273 | 0.068513 | 0.0013245 | -0.00077756 | -0.0020443 | -0.067413 | 0.16331 | 0.12687 | -0.0035802 | 0.058815 | 0.10628 | 0.00027333 | -0.23346 | 59.0195 | -63.7299 | 59.1293 | 59.2621 | -63.7436 | 59.2438 | 0.54932 | 59.024 | -63.6383 | 59.198 | 59.3308 | 59.1202 | 0.3067 | -0.13275 | -0.073242 | 0.036621 | 122.8592 | 122.8409 | -0.14648 | 122.9736 | -0.013733 | -0.041199 | -0.068664 | 0.10529 | 122.9279 | 63.9038 | 122.7173 | 63.945 | 122.7585 | 122.9919 | 122.8592 | 122.9691 | 122.8363 | 122.7493 | 122.6624 | 122.6166 | 122.6212 | -122.8226 | -122.731 | 122.7264 | 122.7951 | 63.3636 | 64.1464
1334.8906 | 122.9507 | -63.6932 | 59.0561 | -0.19012 | 0.067349 | 0.13179 | 0.070863 | 0.00089729 | -0.00056396 | -0.00033547 | -0.15897 | 0.16416 | 0.12986 | -0.0016576 | 0.057747 | 0.10885 | -0.0031445 | -0.35706 | 59.0057 | -63.8031 | 58.9691 | 59.0469 | -63.9587 | 59.0652 | 0.30212 | 59.0332 | -63.6841 | 59.0927 | 59.1522 | 58.9554 | 0.10986 | -0.10986 | -0.050354 | -0.086975 | 122.7402 | 122.7585 | -0.2655 | 122.8683 | -0.15564 | 0.009155 | -0.022888 | 0.036621 | 122.8455 | 63.8031 | 122.6486 | 63.7939 | 122.6395 | 122.85 | 122.7722 | 122.8363 | 122.7768 | 122.8088 | 122.7173 | 122.699 | 122.7264 | -122.8592 | -122.7402 | 122.6624 | 122.7859 | 63.3362 | 63.9954
1335.8281 | 123.0194 | -63.6292 | 59.0744 | -0.22064 | 0.070553 | 0.12709 | 0.068727 | -0.0012391 | -0.0016322 | -0.0016171 | -0.064362 | 0.1648 | 0.12495 | 0.003042 | 0.05796 | 0.10564 | -0.0020765 | -0.29755 | 59.0103 | -63.7711 | 59.0332 | 59.1476 | -63.8443 | 59.1476 | 0.42572 | 58.992 | -63.6566 | 59.1385 | 59.23 | 59.0836 | 0.2243 | -0.14191 | -0.064087 | -0.041199 | 122.7768 | 122.7768 | -0.21515 | 122.9187 | -0.073242 | -0.027466 | -0.082398 | 0.064087 | 122.8592 | 63.8535 | 122.7127 | 63.8809 | 122.7402 | 122.9187 | 122.8043 | 122.8867 | 122.7951 | 122.7814 | 122.6486 | 122.6395 | 122.6212 | -122.8455 | -122.731 | 122.6624 | 122.7676 | 63.3316 | 64.0549
1336.8906 | 122.8912 | -63.6932 | 59.1064 | -0.12909 | 0.070126 | 0.12944 | 0.070863 | 0.0036743 | -0.0031274 | -0.0016171 | -0.15591 | 0.16566 | 0.12666 | -0.00037605 | 0.058815 | 0.10671 | -0.0012219 | -0.32044 | 59.0149 | -63.8123 | 58.9828 | 59.0469 | -63.9313 | 59.0652 | 0.29297 | 59.0378 | -63.6978 | 59.0332 | 59.1293 | 58.9096 | 0.11902 | -0.11902 | -0.091552 | -0.1236 | 122.7402 | 122.7585 | -0.23804 | 122.8775 | -0.11902 | -0.004578 | -0.068664 | -0.073242 | 122.8226 | 63.8123 | 122.6028 | 63.8168 | 122.6074 | 122.8592 | 122.7951 | 122.8271 | 122.731 | 122.8271 | 122.7356 | 122.7081 | 122.731 | -122.9187 | -122.8043 | 122.6761 | 122.7264 | 63.3728 | 63.9862
1337.8281 | 123.024 | -63.6292 | 59.0607 | -0.2359 | 0.066922 | 0.12965 | 0.067872 | 0.0043151 | -0.002273 | -0.00076267 | -0.055206 | 0.16288 | 0.12773 | 0.00026495 | 0.058174 | 0.10543 | 0.0011279 | -0.28839 | 59.0195 | -63.7802 | 59.0424 | 59.1476 | -63.8397 | 59.1476 | 0.41199 | 59.0012 | -63.6475 | 59.1385 | 59.2529 | 59.079 | 0.23346 | -0.15106 | -0.041199 | -0.018311 | 122.7768 | 122.7768 | -0.21057 | 122.9279 | -0.05951 | -0.018311 | -0.059509 | 0.07782 | 122.8821 | 63.8626 | 122.7081 | 63.8809 | 122.7264 | 122.9279 | 122.8226 | 122.9004 | 122.7859 | 122.7997 | 122.6486 | 122.6486 | 122.6303 | -122.8409 | -122.7081 | 122.6715 | 122.7676 | 63.3408 | 64.0411
1338.8906 | 122.9874 | -63.6566 | 59.0286 | -0.19012 | 0.068203 | 0.12922 | 0.067445 | -0.0012391 | -0.0018458 | 0.0018009 | -0.082672 | 0.16288 | 0.13115 | -0.0061438 | 0.057747 | 0.10543 | -0.0050671 | -0.30212 | 58.9828 | -63.7665 | 59.0424 | 59.1751 | -63.8443 | 59.1614 | 0.41199 | 58.9783 | -63.6658 | 59.1248 | 59.2072 | 59.0332 | 0.16022 | -0.10986 | -0.045776 | 0.013733 | 122.8317 | 122.818 | -0.18768 | 122.9279 | -0.07782 | -0.009155 | -0.050354 | 0.096131 | 122.8638 | 63.8168 | 122.6898 | 63.826 | 122.699 | 122.9416 | 122.8088 | 122.8729 | 122.7905 | 122.7493 | 122.644 | 122.6395 | 122.6349 | -122.7951 | -122.6944 | 122.699 | 122.7814 | 63.3545 | 64.0686
1339.8281 | 123.0011 | -63.652 | 59.0561 | -0.20538 | 0.068631 | 0.1305 | 0.06595 | 0.00089729 | 0.00093144 | -0.00012167 | -0.07962 | 0.16416 | 0.12815 | -0.0074254 | 0.057319 | 0.10628 | -0.0020765 | -0.28381 | 59.0057 | -63.7573 | 59.0424 | 59.1339 | -63.8214 | 59.166 | 0.41657 | 59.0149 | -63.652 | 59.1385 | 59.2575 | 59.0744 | 0.23804 | -0.10528 | -0.050354 | -0.013733 | 122.7859 | 122.818 | -0.16937 | 122.9233 | -0.064087 | 0 | -0.041198 | 0.082398 | 122.9095 | 63.8901 | 122.7264 | 63.8901 | 122.7264 | 122.8912 | 122.7997 | 122.9095 | 122.7905 | 122.7631 | 122.6669 | 122.6578 | 122.6669 | -122.8134 | -122.7081 | 122.6944 | 122.7905 | 63.3682 | 64.0686
1340.8906 | 122.9507 | -63.6566 | 59.0698 | -0.1825 | 0.068844 | 0.12815 | 0.069154 | 0.0038879 | -0.002273 | -0.0022581 | -0.17117 | 0.16437 | 0.13029 | -0.001444 | 0.05796 | 0.10628 | 0.00070073 | -0.36621 | 59.0195 | -63.826 | 58.9645 | 59.0469 | -63.9542 | 59.0744 | 0.29297 | 59.0103 | -63.6932 | 59.1019 | 59.1476 | 58.9645 | 0.11444 | -0.16937 | -0.050354 | -0.10528 | 122.7036 | 122.731 | -0.29755 | 122.9004 | -0.12817 | -0.036621 | -0.059509 | 0.032044 | 122.8043 | 63.7711 | 122.6212 | 63.8077 | 122.6578 | 122.8729 | 122.7905 | 122.8409 | 122.7951 | 122.8455 | 122.7036 | 122.6761 | 122.6669 | -122.8958 | -122.7631 | 122.6212 | 122.7585 | 63.2904 | 63.9496
1341.8281 | 122.9919 | -63.6246 | 59.0561 | -0.22064 | 0.069699 | 0.12858 | 0.068727 | -0.0012391 | -0.002273 | -0.0037533 | -0.06131 | 0.16224 | 0.12773 | -0.0042212 | 0.05796 | 0.1035 | 0.0017687 | -0.3067 | 59.0012 | -63.7665 | 59.0424 | 59.1431 | -63.8351 | 59.1385 | 0.40741 | 59.0103 | -63.6566 | 59.1476 | 59.2484 | 59.0515 | 0.23346 | -0.14191 | -0.054931 | -0.013733 | 122.7676 | 122.7631 | -0.21057 | 122.905 | -0.068665 | -0.032043 | -0.045776 | 0.091553 | 122.8729 | 63.858 | 122.6761 | 63.8901 | 122.7081 | 122.9095 | 122.8088 | 122.905 | 122.8043 | 122.7676 | 122.6669 | 122.6257 | 122.6349 | -122.8226 | -122.7127 | 122.6669 | 122.7722 | 63.3179 | 64.032
1342.8906 | 122.9462 | -63.6566 | 59.0607 | -0.17487 | 0.067563 | 0.12773 | 0.07129 | 0.00046989 | -0.0014184 | -0.00097627 | -0.16202 | 0.1648 | 0.12815 | 0.001974 | 0.058174 | 0.10564 | -0.0029309 | -0.36163 | 59.0103 | -63.8397 | 58.9462 | 59.0424 | -63.9313 | 59.0607 | 0.30212 | 59.024 | -63.7115 | 59.0973 | 59.1476 | 58.9554 | 0.10986 | -0.18311 | -0.050354 | -0.11444 | 122.699 | 122.7173 | -0.27466 | 122.9004 | -0.091552 | -0.054932 | -0.036621 | 0.036621 | 122.8043 | 63.7665 | 122.612 | 63.8214 | 122.6669 | 122.8821 | 122.7859 | 122.8592 | 122.8088 | 122.85 | 122.7356 | 122.6669 | 122.6807 | -122.9004 | -122.7722 | 122.6028 | 122.7539 | 63.295 | 63.9587
1343.8281 | 123.0103 | -63.6292 | 59.0286 | -0.15961 | 0.068844 | 0.12922 | 0.066804 | -0.0010253 | -0.0024866 | 0.00094633 | -0.073517 | 0.16459 | 0.1273 | -0.0061438 | 0.056892 | 0.10521 | -0.0035719 | -0.28839 | 58.9737 | -63.7756 | 58.9691 | 59.4269 | -63.7207 | 59.111 | 0.39368 | 58.96 | -63.6383 | 59.1705 | 59.2529 | 59.0652 | 0.19684 | -0.14648 | -0.054931 | -0.059509 | 123.056 | 122.7402 | -0.091553 | 122.8867 | 0.054932 | -0.009156 | -0.068664 | 0.14191 | 122.8821 | 63.826 | 122.6944 | 63.8351 | 122.7036 | 123.2025 | 122.7448 | 122.8912 | 122.8088 | 122.7493 | 122.5983 | 122.6028 | 122.5891 | -122.8043 | -122.6669 | 122.5983 | 122.7997 | 63.3408 | 64.0228
1344.8281 | 122.9874 | -63.6566 | 59.0378 | -0.1825 | 0.069912 | 0.12986 | 0.069154 | 0.0015381 | -0.0027002 | -0.0020443 | -0.085724 | 0.16267 | 0.12794 | -0.0046484 | 0.059028 | 0.10543 | 0.0013415 | -0.32501 | 58.9828 | -63.7802 | 59.024 | 59.1431 | -63.8626 | 59.1385 | 0.38452 | 58.9966 | -63.6658 | 59.1156 | 59.2026 | 59.0378 | 0.16022 | -0.1236 | -0.054932 | -0.013733 | 122.7997 | 122.7951 | -0.20599 | 122.9187 | -0.082398 | -0.009155 | -0.041199 | 0.07782 | 122.8592 | 63.8168 | 122.6944 | 63.826 | 122.7036 | 122.9233 | 122.8043 | 122.8683 | 122.7814 | 122.7631 | 122.6624 | 122.6395 | 122.6532 | -122.818 | -122.7036 | 122.6807 | 122.7722 | 63.3316 | 64.0411
1345.8906 | 122.905 | -63.6566 | 59.0698 | -0.12146 | 0.068203 | 0.12858 | 0.070222 | 0.00025629 | -0.005691 | -0.00012167 | -0.18338 | 0.16224 | 0.12709 | -0.00016245 | 0.059883 | 0.10393 | -0.0044263 | -0.32959 | 59.0195 | -63.826 | 58.9645 | 59.0012 | -63.9496 | 59.0424 | 0.28381 | 59.0286 | -63.6887 | 59.0332 | 59.0836 | 58.905 | 0.09613 | -0.16937 | -0.050354 | -0.10528 | 122.6578 | 122.699 | -0.29297 | 122.8683 | -0.1236 | -0.032044 | -0.041199 | -0.036621 | 122.7402 | 63.7527 | 122.5616 | 63.7848 | 122.5937 | 122.8271 | 122.7905 | 122.7722 | 122.7219 | 122.8455 | 122.7173 | 122.6761 | 122.6852 | -122.8958 | -122.7585 | 122.6212 | 122.6898 | 63.327 | 63.9404
1346.8281 | 123.0286 | -63.6337 | 59.0286 | -0.22064 | 0.069912 | 0.12858 | 0.0683 | 0.00025629 | -0.00056396 | -0.0026853 | -0.10709 | 0.16437 | 0.12858 | 0.0017602 | 0.057319 | 0.10628 | -0.0014355 | -0.3067 | 58.9874 | -63.7848 | 59.0561 | 59.1797 | -63.826 | 59.1431 | 0.42114 | 58.9691 | -63.6383 | 59.1522 | 59.23 | 59.0515 | 0.17853 | -0.15106 | -0.041198 | 0.027466 | 122.8134 | 122.7768 | -0.19226 | 122.9279 | -0.041199 | -0.004578 | -0.059509 | 0.1236 | 122.8638 | 63.8123 | 122.6852 | 63.8168 | 122.6898 | 122.9645 | 122.8409 | 122.8683 | 122.7905 | 122.7722 | 122.6074 | 122.6212 | 122.6028 | -122.8134 | -122.6669 | 122.6898 | 122.7859 | 63.327 | 64.0549
1347.8906 | 122.8088 | -63.6383 | 59.1019 | -0.13672 | 0.067776 | 0.12559 | 0.067659 | -0.00017091 | -0.0033412 | 0.0013735 | -0.12234 | 0.16437 | 0.1305 | -0.0057166 | 0.057319 | 0.10692 | 0.00027333 | -0.28381 | 59.0744 | -63.7619 | 58.9966 | 59.0881 | -63.8535 | 59.1202 | 0.41199 | 59.0652 | -63.6612 | 58.9737 | 59.3628 | 59.1751 | 0.28839 | -0.1236 | -0.027466 | -0.10529 | 122.7264 | 122.7585 | -0.21515 | 122.8821 | -0.091553 | -0.022888 | -0.036621 | -0.12817 | 123.0011 | 63.9267 | 122.8134 | 63.9496 | 122.8363 | 122.85 | 122.7585 | 123.024 | 122.6349 | 122.8363 | 122.7264 | 122.7127 | 122.7036 | -122.8638 | -122.7631 | 122.6349 | 122.612 | 63.3545 | 64.0503
1348.8281 | 122.9095 | -63.6887 | 59.0744 | -0.15198 | 0.069058 | 0.12709 | 0.069368 | -0.0023071 | -0.0031274 | -0.00076267 | -0.14066 | 0.16566 | 0.12858 | 0.0026148 | 0.060524 | 0.10393 | 0.0015551 | -0.37079 | 59.0286 | -63.8443 | 58.9005 | 59.111 | -63.8992 | 59.024 | 0.25177 | 59.0607 | -63.707 | 59.0607 | 59.111 | 58.9554 | 0.10529 | -0.15564 | -0.045777 | -0.17395 | 122.7997 | 122.7127 | -0.21057 | 122.8683 | -0.054932 | -0.01831 | -0.013733 | -0.013733 | 122.7997 | 63.7939 | 122.644 | 63.8123 | 122.6624 | 122.9553 | 122.7448 | 122.818 | 122.7676 | 122.8729 | 122.7676 | 122.7173 | 122.7493 | -122.9187 | -122.7814 | 122.5891 | 122.7493 | 63.3179 | 63.9404
1349.8906 | 123.0103 | -63.6017 | 59.0836 | -0.052796 | 0.069699 | 0.12901 | 0.067445 | 0.0021789 | -0.0054774 | -0.0024717 | -0.058258 | 0.16331 | 0.12837 | -0.0042212 | 0.059883 | 0.10521 | 0.0030505 | -0.41657 | 59.0195 | -63.7436 | 59.0744 | 59.2255 | -63.7207 | 59.2026 | 0.54016 | 59.0057 | -63.62 | 59.1705 | 59.2804 | 59.0927 | 0.29755 | -0.14191 | -0.064087 | -0.009155 | 122.8271 | 122.8043 | -0.11902 | 122.9462 | 0.022888 | -0.01831 | -0.07782 | 0.086975 | 122.8821 | 63.8992 | 122.6944 | 63.9175 | 122.7127 | 122.9691 | 122.818 | 122.9004 | 122.7905 | 122.7631 | 122.6257 | 122.6212 | 122.6074 | -122.8271 | -122.7036 | 122.6761 | 122.7722 | 63.1851 | 64.1418
1350.8281 | 122.905 | -63.6795 | 59.0927 | -0.15961 | 0.067135 | 0.12709 | 0.070436 | 0.0015381 | -0.002273 | -0.0028989 | -0.15286 | 0.16587 | 0.12687 | 0.0015466 | 0.058174 | 0.105 | 0.00048713 | -0.39825 | 58.992 | -63.8489 | 59.0378 | 59.0332 | -64.0137 | 59.0836 | 0.28839 | 59.0286 | -63.707 | 59.0515 | 59.1385 | 58.9462 | 0.10071 | -0.16937 | -0.10071 | -0.054931 | 122.7127 | 122.7631 | -0.33417 | 122.9324 | -0.16479 | -0.027466 | -0.064087 | -0.041198 | 122.818 | 63.7802 | 122.6257 | 63.8077 | 122.6532 | 122.8821 | 122.8867 | 122.8455 | 122.7585 | 122.8409 | 122.7356 | 122.6715 | 122.7081 | -122.9416 | -122.7997 | 122.7173 | 122.731 | 63.2812 | 63.9679
1351.8906 | 122.9324 | -63.652 | 59.1156 | -0.1062 | 0.06799 | 0.12815 | 0.068941 | 0.00046989 | -0.003982 | -0.00012167 | -0.11624 | 0.16373 | 0.12986 | -0.003794 | 0.058387 | 0.10479 | -0.0057081 | -0.2655 | 59.0652 | -63.7573 | 58.9828 | 59.0836 | -63.8626 | 59.1293 | 0.41657 | 59.0561 | -63.6703 | 59.1019 | 59.1843 | 59.0149 | 0.2243 | -0.10528 | -0.050354 | -0.13275 | 122.7356 | 122.7814 | -0.21057 | 122.8867 | -0.10529 | -0.01831 | -0.05951 | -0.013733 | 122.8363 | 63.8763 | 122.6669 | 63.8947 | 122.6852 | 122.8409 | 122.7402 | 122.8546 | 122.7722 | 122.8226 | 122.7264 | 122.7173 | 122.7081 | -122.8729 | -122.7859 | 122.6349 | 122.7539 | 63.3865 | 64.0686
1352.8281 | 122.9279 | -63.6383 | 59.0652 | 0.023498 | 0.066708 | 0.12602 | 0.068086 | -0.0029479 | -0.0014184 | -0.0014035 | -0.14676 | 0.16566 | 0.12858 | 0.00069215 | 0.058601 | 0.1065 | -0.00058107 | -0.4303 | 59.024 | -63.8031 | 58.9279 | 59.024 | -63.9175 | 59.0607 | 0.28839 | 58.9966 | -63.6566 | 59.079 | 59.1248 | 58.9325 | 0.10529 | -0.16479 | -0.041199 | -0.13733 | 122.6624 | 122.699 | -0.27924 | 122.8638 | -0.11444 | -0.01831 | -0.068665 | 0.013732 | 122.7631 | 63.7436 | 122.5708 | 63.7619 | 122.5891 | 122.8271 | 122.731 | 122.7814 | 122.7356 | 122.8271 | 122.6532 | 122.6624 | 122.6349 | -122.8683 | -122.7219 | 122.5662 | 122.7173 | 63.208 | 63.9267
1353.8906 | 122.9462 | -63.6383 | 59.0744 | -0.12146 | 0.06799 | 0.12773 | 0.070436 | 0.00046989 | -0.0020594 | -0.0022581 | -0.11319 | 0.1648 | 0.12965 | -0.0027258 | 0.059669 | 0.1065 | -0.0018629 | -0.24261 | 59.0286 | -63.7482 | 59.024 | 59.1202 | -63.8397 | 59.1202 | 0.45319 | 59.0469 | -63.652 | 59.1248 | 59.2117 | 59.0149 | 0.24261 | -0.10986 | -0.045777 | -0.050354 | 122.7585 | 122.7585 | -0.20142 | 122.8683 | -0.091553 | -0.013733 | -0.027466 | 0.050354 | 122.85 | 63.8809 | 122.6532 | 63.8947 | 122.6669 | 122.8683 | 122.7722 | 122.8638 | 122.7768 | 122.7768 | 122.699 | 122.6669 | 122.6852 | -122.8226 | -122.7264 | 122.6624 | 122.7631 | 63.3957 | 64.0915
1354.8281 | 122.9141 | -63.6749 | 59.079 | -0.090943 | 0.067135 | 0.12666 | 0.069795 | 0.00025629 | -0.0037684 | -0.0020443 | -0.15286 | 0.16395 | 0.12687 | -0.0029394 | 0.057747 | 0.10628 | 0.0032641 | -0.31128 | 59.0378 | -63.7985 | 58.9691 | 59.0698 | -63.9313 | 59.0424 | 0.30212 | 59.0149 | -63.6703 | 59.0469 | 59.111 | 58.9417 | 0.13733 | -0.1236 | -0.041198 | -0.10986 | 122.7448 | 122.7173 | -0.25635 | 122.8409 | -0.13275 | 0.004578 | -0.064086 | -0.032043 | 122.7859 | 63.8123 | 122.6166 | 63.8077 | 122.612 | 122.8683 | 122.7676 | 122.7814 | 122.7173 | 122.8363 | 122.6852 | 122.7127 | 122.6898 | -122.8775 | -122.7493 | 122.644 | 122.7219 | 63.3636 | 63.9771
1355.8906 | 122.9279 | -63.6154 | 59.1202 | -0.15961 | 0.069912 | 0.12837 | 0.067018 | -0.00081171 | -0.0016322 | -0.0022581 | -0.046051 | 0.16288 | 0.12623 | -0.0078528 | 0.059028 | 0.10543 | 0.0011279 | -0.21515 | 59.024 | -63.7344 | 59.0744 | 59.2026 | -63.7665 | 59.1751 | 0.50812 | 59.0332 | -63.6475 | 59.1385 | 59.2484 | 59.0515 | 0.27924 | -0.11902 | -0.09613 | -0.045776 | 122.818 | 122.7905 | -0.15106 | 122.9095 | -0.032043 | -0.032044 | -0.086975 | 0.018311 | 122.8638 | 63.8947 | 122.6669 | 63.9267 | 122.699 | 122.937 | 122.8088 | 122.8958 | 122.7859 | 122.7585 | 122.6807 | 122.6395 | 122.6486 | -122.8546 | -122.7676 | 122.6898 | 122.7539 | 63.4003 | 64.1235
1356.8281 | 122.9507 | -63.6292 | 59.0927 | -0.13672 | 0.070126 | 0.12815 | 0.070222 | -0.00017091 | -0.0024866 | -0.0016171 | -0.12234 | 0.16309 | 0.12858 | 0.00069215 | 0.058387 | 0.10735 | -0.0012219 | -0.24719 | 59.0286 | -63.7756 | 59.0332 | 59.1293 | -63.8672 | 59.1156 | 0.44861 | 59.0149 | -63.6749 | 59.1339 | 59.1934 | 59.0103 | 0.21057 | -0.14648 | -0.064087 | -0.059509 | 122.7585 | 122.7448 | -0.23804 | 122.8912 | -0.091552 | -0.045777 | -0.077819 | 0.041199 | 122.8226 | 63.8397 | 122.6395 | 63.8855 | 122.6852 | 122.905 | 122.8088 | 122.8683 | 122.8088 | 122.8043 | 122.6898 | 122.6578 | 122.644 | -122.8683 | -122.7676 | 122.6624 | 122.7631 | 63.382 | 64.0778
1357.8906 | 123.0423 | -63.6154 | 59.0698 | -0.17487 | 0.070126 | 0.12794 | 0.068727 | -0.0010253 | -0.0020594 | 9.193e-05 | -0.021637 | 0.16288 | 0.12922 | -0.0063574 | 0.055824 | 0.105 | -0.0012219 | -0.25635 | 59.0286 | -63.7299 | 59.0515 | 59.1934 | -63.7802 | 59.1705 | 0.4715 | 58.96 | -63.6429 | 59.166 | 59.2758 | 59.0881 | 0.27466 | -0.11444 | -0.041199 | -0.01831 | 122.8088 | 122.7859 | -0.16479 | 122.9004 | -0.050354 | -0.027466 | -0.10986 | 0.096131 | 122.8912 | 63.8901 | 122.7036 | 63.9175 | 122.731 | 122.9233 | 122.7814 | 122.9187 | 122.8088 | 122.7585 | 122.6028 | 122.644 | 122.5754 | -122.7997 | -122.7127 | 122.6669 | 122.7814 | 63.3591 | 64.0869
1358.8281 | 122.9004 | -63.6475 | 59.1019 | -0.14435 | 0.069699 | 0.12751 | 0.071504 | -0.00017091 | 0.00071784 | 0.00094633 | -0.12845 | 0.16566 | 0.12815 | 0.0051782 | 0.05796 | 0.10372 | -0.00015387 | -0.28839 | 59.024 | -63.7756 | 58.9783 | 59.079 | -63.9221 | 59.0652 | 0.35706 | 59.0195 | -63.6658 | 59.0607 | 59.1202 | 58.9279 | 0.13275 | -0.12817 | -0.07782 | -0.1236 | 122.7264 | 122.7127 | -0.27466 | 122.8409 | -0.14648 | -0.01831 | -0.082398 | -0.041199 | 122.7676 | 63.7802 | 122.5754 | 63.7985 | 122.5937 | 122.8546 | 122.7539 | 122.7859 | 122.7264 | 122.7997 | 122.6852 | 122.6715 | 122.6669 | -122.8775 | -122.7676 | 122.6257 | 122.7081 | 63.3591 | 64.0045
1359.8906 | 122.937 | -63.62 | 59.0836 | -0.12146 | 0.069272 | 0.12901 | 0.070009 | 0.00068369 | -0.0012048 | 0.00073273 | -0.10709 | 0.16331 | 0.1273 | 0.00090575 | 0.058601 | 0.10585 | 0.00027333 | -0.24261 | 59.0607 | -63.7665 | 59.0149 | 59.1385 | -63.8306 | 59.1248 | 0.45776 | 59.0469 | -63.6475 | 59.1293 | 59.2026 | 59.024 | 0.23346 | -0.14648 | -0.022888 | -0.068664 | 122.7585 | 122.7448 | -0.21057 | 122.8912 | -0.064087 | -0.027466 | -0.036621 | 0.045776 | 122.8226 | 63.8535 | 122.644 | 63.8809 | 122.6715 | 122.905 | 122.7814 | 122.85 | 122.7768 | 122.8271 | 122.6944 | 122.6807 | 122.6669 | -122.85 | -122.731 | 122.6349 | 122.7493 | 63.3774 | 64.0778
1360.8281 | 122.9141 | -63.6658 | 59.0881 | -0.083313 | 0.067776 | 0.1273 | 0.069368 | 0.00025629 | -0.0033412 | -0.00033547 | -0.1376 | 0.16245 | 0.12815 | 0.0026148 | 0.059669 | 0.10564 | 0.0024097 | -0.3067 | 59.0378 | -63.7848 | 58.96 | 59.0561 | -63.9267 | 59.0515 | 0.31128 | 59.0378 | -63.6841 | 59.0469 | 59.0973 | 58.9142 | 0.12817 | -0.11902 | -0.050354 | -0.12817 | 122.7219 | 122.7173 | -0.26093 | 122.8363 | -0.14191 | -0.018311 | -0.050354 | -0.041199 | 122.7631 | 63.7939 | 122.58 | 63.8123 | 122.5983 | 122.8409 | 122.7448 | 122.7814 | 122.731 | 122.8226 | 122.7219 | 122.7036 | 122.7036 | -122.8729 | -122.7722 | 122.6257 | 122.7127 | 63.3591 | 63.977
1361.8906 | 123.0148 | -63.588 | 59.0973 | -0.15198 | 0.070553 | 0.12815 | 0.066591 | -0.0025207 | -0.0027002 | -0.00097627 | -0.11014 | 0.16352 | 0.12645 | -0.012339 | 0.058174 | 0.10479 | 0.00027333 | -0.19684 | 59.0195 | -63.7436 | 59.1019 | 59.3216 | -63.3682 | 59.1614 | 0.59052 | 58.9691 | -63.6383 | 59.198 | 59.2941 | 59.1156 | 0.31586 | -0.15564 | -0.07782 | 0.004578 | 122.9095 | 122.7493 | 0.21973 | 122.905 | 0.37537 | -0.050354 | -0.12817 | 0.10071 | 122.8821 | 63.9038 | 122.7036 | 63.9542 | 122.7539 | 123.0652 | 122.8455 | 122.9324 | 122.8363 | 122.7631 | 122.6074 | 122.6074 | 122.5571 | -122.8409 | -122.7356 | 122.6898 | 122.7859 | 63.3911 | 64.1785
1362.8281 | 122.8775 | -63.6658 | 59.079 | -0.12909 | 0.069272 | 0.12858 | 0.069368 | 0.00046989 | -0.0029138 | -0.0020443 | -0.1376 | 0.16437 | 0.12922 | -0.0025122 | 0.056465 | 0.10564 | -0.0031445 | -0.32044 | 59.0378 | -63.8306 | 58.9188 | 59.0057 | -63.9313 | 59.0652 | 0.27466 | 59.0332 | -63.6978 | 59.024 | 59.0881 | 58.905 | 0.10986 | -0.16479 | -0.041198 | -0.16022 | 122.6715 | 122.731 | -0.2655 | 122.8958 | -0.10071 | -0.032044 | -0.045776 | -0.054931 | 122.7539 | 63.7756 | 122.5708 | 63.8077 | 122.6028 | 122.8363 | 122.7493 | 122.7859 | 122.7219 | 122.8683 | 122.731 | 122.7036 | 122.699 | -122.9095 | -122.7768 | 122.5845 | 122.6898 | 63.3453 | 63.9404
1363.8281 | 122.9095 | -63.6429 | 59.079 | -0.12909 | 0.067776 | 0.12901 | 0.068941 | 0.0017517 | -0.00099116 | 0.0011599 | -0.1254 | 0.1648 | 0.13029 | -0.0035802 | 0.060951 | 0.105 | -0.00015387 | -0.27924 | 59.0378 | -63.7756 | 59.0012 | 59.111 | -63.8718 | 59.0836 | 0.39368 | 59.024 | -63.652 | 59.0836 | 59.1614 | 58.9462 | 0.16479 | -0.13275 | -0.041198 | -0.077819 | 122.7539 | 122.7264 | -0.22888 | 122.8592 | -0.09613 | -0.009156 | -0.054931 | 0.004578 | 122.8043 | 63.8077 | 122.5891 | 63.8168 | 122.5983 | 122.8867 | 122.7768 | 122.8134 | 122.7356 | 122.8134 | 122.6761 | 122.6807 | 122.6669 | -122.8546 | -122.731 | 122.644 | 122.7264 | 63.3636 | 64.0366
1364.8906 | 122.9141 | -63.62 | 59.1339 | -0.14435 | 0.068203 | 0.12751 | 0.069154 | -0.0010253 | -0.0031274 | -0.0026853 | -0.064362 | 0.16416 | 0.12944 | -0.002085 | 0.05796 | 0.10308 | 0.0011279 | -0.27924 | 59.0652 | -63.7573 | 58.9828 | 59.0973 | -63.8535 | 59.1339 | 0.4303 | 59.0469 | -63.6383 | 59.0652 | 59.1705 | 58.9783 | 0.23346 | -0.13733 | -0.068664 | -0.15106 | 122.7173 | 122.7539 | -0.23346 | 122.8912 | -0.096131 | -0.018311 | -0.086975 | -0.068664 | 122.7905 | 63.8535 | 122.5983 | 63.8718 | 122.6166 | 122.8546 | 122.7402 | 122.8088 | 122.7036 | 122.8226 | 122.6852 | 122.6852 | 122.6669 | -122.8912 | -122.7722 | 122.6028 | 122.6852 | 63.3408 | 64.0503
1365.8438 | 123.0103 | -63.62 | 59.0881 | -0.13672 | 0.067563 | 0.12794 | 0.067445 | 0.0013245 | -0.0014184 | 0.00051913 | 0.011932 | 0.16437 | 0.13008 | -0.0067846 | 0.058815 | 0.10479 | -0.00036747 | -0.31128 | 59.0012 | -63.7619 | 59.0286 | 59.166 | -63.8168 | 59.166 | 0.45319 | 58.992 | -63.6337 | 59.1568 | 59.2392 | 59.0698 | 0.24719 | -0.14191 | -0.086975 | -0.05951 | 122.7859 | 122.7859 | -0.19684 | 122.9279 | -0.054931 | -0.013733 | -0.096131 | 0.068664 | 122.8592 | 63.8672 | 122.6898 | 63.8809 | 122.7036 | 122.9279 | 122.7905 | 122.8729 | 122.7905 | 122.7631 | 122.6257 | 122.6212 | 122.612 | -122.85 | -122.7219 | 122.6486 | 122.7768 | 63.3087 | 64.0732
1366.8906 | 122.9279 | -63.6658 | 59.1431 | -0.14435 | 0.068417 | 0.12837 | 0.066377 | -0.0029479 | -0.0033412 | -0.0041807 | -0.064362 | 0.16352 | 0.1288 | -0.0022986 | 0.060524 | 0.10308 | 0.0013415 | -0.23804 | 59.0515 | -63.7299 | 59.0332 | 59.1293 | -63.7985 | 59.1293 | 0.46234 | 59.0469 | -63.652 | 59.079 | 59.166 | 58.9966 | 0.24261 | -0.064087 | -0.091552 | -0.10986 | 122.7951 | 122.7951 | -0.13275 | 122.8592 | -0.068665 | 0.013732 | -0.09613 | -0.064087 | 122.8317 | 63.9084 | 122.6624 | 63.8947 | 122.6486 | 122.8592 | 122.7631 | 122.818 | 122.731 | 122.7814 | 122.699 | 122.7173 | 122.7127 | -122.8729 | -122.7951 | 122.699 | 122.7447 | 63.4277 | 64.1281
1367.8281 | 123.0057 | -63.6749 | 59.1248 | -0.12909 | 0.066922 | 0.12837 | 0.068941 | 0.0017517 | -0.002273 | -0.0014035 | -0.14371 | 0.16395 | 0.12965 | -0.0022986 | 0.058387 | 0.10607 | 0.0011279 | -0.35706 | 59.0332 | -63.8123 | 58.9417 | 59.0103 | -63.9587 | 59.0378 | 0.29297 | 59.0515 | -63.6978 | 59.1293 | 58.8272 | 58.7173 | -0.013733 | -0.13733 | -0.091553 | -0.18311 | 122.6852 | 122.7127 | -0.28381 | 122.85 | -0.14648 | -0.022888 | -0.073242 | 0.004577 | 122.5021 | 63.6612 | 122.3923 | 63.6841 | 122.4152 | 122.8226 | 122.7539 | 122.525 | 122.8271 | 122.8455 | 122.7493 | 122.7081 | 122.7264 | -122.937 | -122.8226 | 122.6166 | 122.8043 | 63.3179 | 63.9679
1368.8906 | 122.9279 | -63.652 | 59.1156 | -0.1062 | 0.068844 | 0.1258 | 0.069581 | 4.2692e-05 | -0.003982 | -0.0035397 | -0.10403 | 0.16523 | 0.13008 | -0.0055028 | 0.058815 | 0.10735 | -0.0018629 | -0.31586 | 59.0744 | -63.7115 | 58.9462 | 59.0149 | -63.8077 | 59.1019 | 0.41199 | 59.0378 | -63.6612 | 59.079 | 59.1522 | 58.9874 | 0.24261 | -0.059509 | -0.041199 | -0.16937 | 122.6669 | 122.7539 | -0.15564 | 122.8134 | -0.09613 | -0.009155 | -0.07782 | -0.036622 | 122.8043 | 63.8947 | 122.6395 | 63.9038 | 122.6486 | 122.7264 | 122.6578 | 122.8134 | 122.7402 | 122.7859 | 122.699 | 122.7264 | 122.6898 | -122.8271 | -122.7768 | 122.5983 | 122.731 | 63.3362 | 64.064
1369.8281 | 122.9187 | -63.6429 | 59.0836 | -0.13672 | 0.067135 | 0.12794 | 0.070649 | -0.00017091 | -0.0033412 | 0.00030553 | -0.14676 | 0.16395 | 0.1288 | -0.0029394 | 0.056892 | 0.10564 | -0.0018629 | -0.27466 | 59.0012 | -63.7619 | 58.9874 | 59.0698 | -63.8992 | 59.0698 | 0.36621 | 59.0332 | -63.6612 | 59.0652 | 59.1293 | 58.9462 | 0.13733 | -0.11902 | -0.082397 | -0.09613 | 122.7127 | 122.7127 | -0.25635 | 122.8317 | -0.13733 | -0.018311 | -0.050354 | -0.01831 | 122.7722 | 63.7802 | 122.5891 | 63.7985 | 122.6074 | 122.8317 | 122.7493 | 122.7905 | 122.7264 | 122.7631 | 122.6944 | 122.644 | 122.6761 | -122.8455 | -122.7448 | 122.6303 | 122.7081 | 63.3682 | 64.0091
1370.9062 | 123.0103 | -63.652 | 59.024 | -0.16724 | 0.069272 | 0.1258 | 0.0683 | 0.0013245 | -0.0020594 | -0.00076267 | -0.046051 | 0.16331 | 0.12837 | -0.0059302 | 0.058387 | 0.1035 | -0.0018629 | -0.27924 | 58.96 | -63.7344 | 59.0424 | 59.1797 | -63.8214 | 59.1476 | 0.43488 | 58.9737 | -63.6429 | 59.1431 | 59.2163 | 59.0149 | 0.17395 | -0.082397 | -0.064087 | 0.01831 | 122.8317 | 122.7997 | -0.16937 | 122.8821 | -0.086975 | 0.009156 | -0.050354 | 0.11902 | 122.8683 | 63.826 | 122.6669 | 63.8168 | 122.6578 | 122.9141 | 122.7768 | 122.8592 | 122.7859 | 122.6944 | 122.6166 | 122.612 | 122.6257 | -122.7585 | -122.6669 | 122.6944 | 122.7951 | 63.3728 | 64.0869
1371.8281 | 122.8912 | -63.652 | 59.079 | -0.1062 | 0.068203 | 0.1288 | 0.068513 | -0.00017091 | -0.0014184 | -0.0033261 | -0.13455 | 0.16288 | 0.12944 | 0.0011194 | 0.058815 | 0.10543 | -0.0014355 | -0.28381 | 59.024 | -63.8031 | 59.0057 | 59.111 | -63.8672 | 59.0973 | 0.41199 | 59.0103 | -63.6749 | 59.0881 | 59.1339 | 58.9737 | 0.16479 | -0.15106 | -0.054931 | -0.073242 | 122.7631 | 122.7493 | -0.21515 | 122.9004 | -0.064086 | -0.022888 | -0.068664 | 0.009156 | 122.7859 | 63.8168 | 122.6257 | 63.8397 | 122.6486 | 122.9141 | 122.8088 | 122.8088 | 122.7631 | 122.8271 | 122.6852 | 122.6761 | 122.6624 | -122.8821 | -122.7539 | 122.6578 | 122.7402 | 63.3682 | 64.064
1372.8906 | 123.024 | -63.6017 | 59.0698 | -0.15198 | 0.066708 | 0.12623 | 0.065523 | -0.0044433 | 0.001145 | 0.0011599 | -0.0094299 | 0.16267 | 0.12837 | -0.0069982 | 0.058601 | 0.1018 | 0.00091433 | -0.24719 | 59.024 | -63.7527 | 59.0881 | 59.2392 | -63.7207 | 59.2392 | 0.59052 | 59.0057 | -63.5971 | 59.1614 | 59.3033 | 59.1156 | 0.29755 | -0.15106 | -0.045776 | 0.018311 | 122.8409 | 122.8409 | -0.11902 | 122.9919 | 0.032044 | 0.004578 | -0.064087 | 0.091553 | 122.905 | 63.8992 | 122.7173 | 63.8947 | 122.7127 | 122.9919 | 122.8409 | 122.9004 | 122.7585 | 122.7768 | 122.6028 | 122.6257 | 122.6074 | -122.8226 | -122.6669 | 122.6898 | 122.7631 | 63.3545 | 64.1922
1373.8281 | 122.905 | -63.6658 | 59.0881 | -0.19012 | 0.07034 | 0.12837 | 0.070222 | 0.0026063 | -0.0048364 | 0.00094633 | -0.14066 | 0.16587 | 0.12922 | 0.0015466 | 0.057533 | 0.10393 | 0.0041187 | -0.36163 | 59.0195 | -63.826 | 58.9096 | 58.9783 | -63.9771 | 59.0195 | 0.30212 | 59.024 | -63.6795 | 59.0469 | 59.1019 | 58.9142 | 0.10529 | -0.16022 | -0.068665 | -0.17853 | 122.644 | 122.6852 | -0.31128 | 122.8455 | -0.15106 | -0.013733 | -0.064087 | -0.041199 | 122.7676 | 63.7711 | 122.58 | 63.7848 | 122.5937 | 122.8043 | 122.7356 | 122.7814 | 122.7264 | 122.8455 | 122.7036 | 122.6852 | 122.6898 | -122.9141 | -122.7676 | 122.5754 | 122.7127 | 63.3041 | 63.9679
1374.8906 | 123.0423 | -63.6108 | 59.0652 | -0.13672 | 0.069912 | 0.12687 | 0.066163 | -0.0010253 | -0.0020594 | 0.0020145 | -0.012482 | 0.16416 | 0.12922 | -0.010843 | 0.058174 | 0.10457 | -0.0018629 | -0.24261 | 59.024 | -63.7299 | 59.0652 | 59.2163 | -63.7482 | 59.1843 | 0.54474 | 58.9783 | -63.588 | 59.1888 | 59.317 | 59.1431 | 0.30212 | -0.11902 | -0.041199 | 0 | 122.8271 | 122.7951 | -0.13733 | 122.9141 | -0.018311 | 0.022888 | -0.086976 | 0.1236 | 122.9279 | 63.913 | 122.7539 | 63.8901 | 122.731 | 122.9462 | 122.7951 | 122.905 | 122.7768 | 122.7539 | 122.5662 | 122.6349 | 122.5891 | -122.7951 | -122.6532 | 122.6761 | 122.7997 | 63.3682 | 64.1556
1375.8438 | 122.9919 | -63.652 | 59.0652 | -0.19012 | 0.069058 | 0.12858 | 0.067659 | -0.0018799 | 0.001145 | -0.00097627 | -0.073517 | 0.16181 | 0.13093 | -0.0052892 | 0.057747 | 0.10415 | 0.0011279 | -0.31128 | 58.9645 | -63.7665 | 59.0103 | 59.1522 | -63.858 | 59.1248 | 0.40741 | 58.9691 | -63.6795 | 59.1064 | 59.1888 | 59.0012 | 0.15106 | -0.11444 | -0.10071 | -0.054932 | 122.8043 | 122.7768 | -0.20599 | 122.8912 | -0.091553 | -0.027465 | -0.096131 | 0.041198 | 122.8409 | 63.8031 | 122.6532 | 63.8306 | 122.6807 | 122.9187 | 122.7768 | 122.8683 | 122.7859 | 122.731 | 122.6486 | 122.6166 | 122.6212 | -122.8317 | -122.7448 | 122.6624 | 122.7585 | 63.3408 | 64.0594
1376.8906 | 122.9965 | -63.62 | 59.0927 | -0.14435 | 0.067776 | 0.12944 | 0.067232 | -0.0020935 | -0.0014184 | -0.0022581 | -0.070465 | 0.16288 | 0.12687 | -0.0063574 | 0.05796 | 0.10564 | -0.00079467 | -0.23804 | 58.9966 | -63.7253 | 59.1064 | 59.2072 | -63.7436 | 59.1797 | 0.5722 | 59.0286 | -63.62 | 59.1431 | 59.2575 | 59.0698 | 0.31128 | -0.10529 | -0.09613 | 0.013733 | 122.8271 | 122.7997 | -0.1236 | 122.905 | -0.01831 | 0 | -0.064087 | 0.050354 | 122.8775 | 63.9313 | 122.6898 | 63.9313 | 122.6898 | 122.9324 | 122.8317 | 122.8775 | 122.7631 | 122.7219 | 122.6486 | 122.6166 | 122.6486 | -122.818 | -122.7127 | 122.7264 | 122.7631 | 63.382 | 64.1922
1377.8281 | 122.9416 | -63.6292 | 59.1019 | -0.19012 | 0.068631 | 0.12709 | 0.07129 | -0.0029479 | -0.0041956 | -0.00097627 | -0.17117 | 0.16373 | 0.13179 | 0.0011194 | 0.057747 | 0.10863 | -0.0020765 | -0.24261 | 59.0286 | -63.7802 | 59.0378 | 59.1339 | -63.8535 | 59.1202 | 0.48523 | 59.0378 | -63.6749 | 59.0515 | 59.1339 | 58.8959 | 0.14191 | -0.15106 | -0.073243 | -0.064087 | 122.7631 | 122.7493 | -0.2243 | 122.9004 | -0.073243 | -0.045777 | -0.064087 | -0.050354 | 122.7631 | 63.7711 | 122.525 | 63.8168 | 122.5708 | 122.9141 | 122.818 | 122.8088 | 122.7264 | 122.8088 | 122.7127 | 122.6578 | 122.6669 | -122.8821 | -122.7768 | 122.6669 | 122.6807 | 63.3865 | 64.1144
1378.8906 | 122.9736 | -63.6108 | 59.0973 | -0.052796 | 0.068631 | 0.12965 | 0.067018 | -0.0020935 | -0.00013676 | -0.0037533 | -0.027741 | 0.16523 | 0.12794 | -0.0022986 | 0.058815 | 0.105 | -0.0010083 | -0.40741 | 59.0332 | -63.7436 | 59.0652 | 59.23 | -63.7253 | 59.1934 | 0.55847 | 59.0012 | -63.5971 | 59.1568 | 59.2667 | 59.0927 | 0.30212 | -0.13275 | -0.064087 | -0.032043 | 122.8409 | 122.8043 | -0.11444 | 122.937 | 0.01831 | 0.013733 | -0.09613 | 0.059509 | 122.8775 | 63.913 | 122.7036 | 63.8992 | 122.6898 | 122.9736 | 122.8088 | 122.8638 | 122.7539 | 122.7768 | 122.5983 | 122.644 | 122.612 | -122.8409 | -122.6944 | 122.6761 | 122.7676 | 63.2034 | 64.1693
1379.8281 | 122.8592 | -63.6703 | 59.0927 | -0.14435 | 0.066922 | 0.12944 | 0.072999 | 0.0034607 | -0.0031274 | 0.0035099 | -0.15897 | 0.16437 | 0.12751 | -0.00058965 | 0.056038 | 0.10714 | 0.0011279 | -0.30212 | 59.0286 | -63.8031 | 58.9645 | 59.0698 | -63.9084 | 59.0607 | 0.33875 | 59.0332 | -63.6703 | 59.0378 | 59.0973 | 58.9233 | 0.11902 | -0.13275 | -0.064087 | -0.12817 | 122.7402 | 122.731 | -0.23804 | 122.8638 | -0.10529 | 0 | -0.059509 | -0.054931 | 122.7676 | 63.7894 | 122.5937 | 63.7894 | 122.5937 | 122.8729 | 122.7676 | 122.7676 | 122.7081 | 122.8317 | 122.7036 | 122.699 | 122.7036 | -122.8958 | -122.7631 | 122.6349 | 122.7081 | 63.3682 | 64.0091
1380.8906 | 122.7585 | -63.6749 | 59.0103 | -0.21301 | 0.067563 | 0.12815 | 0.069154 | 0.0041015 | -0.00013676 | -0.00076267 | -0.14066 | 0.16523 | 0.1288 | 0.0021876 | 0.056465 | 0.10329 | 0.00091433 | -0.36163 | 59.0286 | -63.8123 | 58.9096 | 58.9874 | -63.9771 | 59.0103 | 0.29755 | 59.0149 | -63.6978 | 59.0332 | 59.0927 | 58.9096 | 0.21057 | -0.13733 | 0.01831 | -0.10071 | 122.6624 | 122.6852 | -0.30212 | 122.8226 | -0.1648 | -0.022888 | 0.004578 | 0.022888 | 122.7676 | 63.8855 | 122.5845 | 63.9084 | 122.6074 | 122.7997 | 122.7219 | 122.7905 | 122.731 | 122.8409 | 122.7127 | 122.7036 | 122.6898 | -122.8226 | -122.7081 | 122.5845 | 122.7081 | 63.3133 | 63.9725
1381.8281 | 122.905 | -63.6658 | 59.0973 | -0.19775 | 0.068203 | 0.12858 | 0.069368 | 0.0017517 | -0.0012048 | 0.0022281 | -0.14371 | 0.16245 | 0.1273 | 0.0015466 | 0.058174 | 0.10607 | 0.00027333 | -0.33875 | 59.0286 | -63.7939 | 58.9142 | 58.9828 | -63.9725 | 59.0057 | 0.28381 | 58.9966 | -63.6749 | 59.0515 | 59.0881 | 58.9005 | 0.091553 | -0.12817 | -0.068665 | -0.1831 | 122.6486 | 122.6715 | -0.3067 | 122.7997 | -0.17853 | -0.009156 | -0.10071 | -0.045776 | 122.7539 | 63.7573 | 122.5662 | 63.7665 | 122.5754 | 122.7768 | 122.7081 | 122.7631 | 122.7264 | 122.8226 | 122.6715 | 122.6944 | 122.6624 | -122.8912 | -122.7722 | 122.58 | 122.7173 | 63.327 | 63.9496
1382.8906 | 122.8821 | -63.6566 | 59.111 | -0.12146 | 0.066281 | 0.12687 | 0.069154 | -0.0044433 | -0.0029138 | -0.0035397 | -0.076569 | 0.1648 | 0.12922 | -0.0076392 | 0.056892 | 0.10671 | 5.9726e-05 | -0.25177 | 59.0469 | -63.7344 | 58.9874 | 59.1064 | -63.858 | 59.1202 | 0.43945 | 59.0607 | -63.6383 | 59.0652 | 59.166 | 58.9783 | 0.24719 | -0.07782 | -0.064087 | -0.1236 | 122.7631 | 122.7768 | -0.20142 | 122.8546 | -0.1236 | 0.01831 | -0.050354 | -0.045776 | 122.8226 | 63.9038 | 122.6349 | 63.8855 | 122.6166 | 122.8409 | 122.7219 | 122.8043 | 122.7036 | 122.7814 | 122.699 | 122.7036 | 122.7173 | -122.8455 | -122.7493 | 122.644 | 122.7219 | 63.4048 | 64.0961
1383.8281 | 122.9141 | -63.6703 | 59.0836 | -0.12146 | 0.068417 | 0.12922 | 0.070009 | 0.0026063 | -0.003982 | -0.00054907 | -0.1315 | 0.16544 | 0.12858 | -0.0016576 | 0.059883 | 0.10585 | -0.0020765 | -0.28839 | 59.0149 | -63.8031 | 58.992 | 59.0561 | -63.9038 | 59.0652 | 0.37079 | 59.0286 | -63.6932 | 59.0698 | 59.1248 | 58.9233 | 0.14648 | -0.13275 | -0.068664 | -0.091553 | 122.7264 | 122.7356 | -0.23346 | 122.8683 | -0.10071 | -0.022888 | -0.054932 | -0.013733 | 122.7951 | 63.8168 | 122.5937 | 63.8397 | 122.6166 | 122.8592 | 122.7951 | 122.818 | 122.7631 | 122.818 | 122.7219 | 122.6852 | 122.699 | -122.8867 | -122.7768 | 122.6624 | 122.7402 | 63.382 | 64.0411
1384.8906 | 122.9416 | -63.6337 | 59.0927 | -0.11383 | 0.068203 | 0.12815 | 0.067445 | 0.0015381 | -0.0033412 | 0.0013735 | -0.030792 | 0.16459 | 0.12687 | -0.01298 | 0.058601 | 0.10372 | -0.0014355 | -0.21515 | 59.0378 | -63.7207 | 59.0561 | 59.1888 | -63.7436 | 59.1751 | 0.53101 | 59.0103 | -63.6063 | 59.1202 | 59.2346 | 59.0561 | 0.28839 | -0.086975 | -0.054931 | -0.036621 | 122.8226 | 122.8088 | -0.10986 | 122.8958 | -0.022888 | 0.027466 | -0.082397 | 0.027466 | 122.8683 | 63.9221 | 122.6898 | 63.8947 | 122.6624 | 122.9095 | 122.7768 | 122.8409 | 122.7264 | 122.7585 | 122.6166 | 122.6715 | 122.644 | -122.8134 | -122.699 | 122.6898 | 122.7539 | 63.4186 | 64.1647
1385.8281 | 122.905 | -63.6475 | 59.1019 | -0.14435 | 0.064999 | 0.1288 | 0.072572 | 0.0019653 | -0.0020594 | -0.0011899 | -0.16202 | 0.16502 | 0.12773 | -0.0025122 | 0.056892 | 0.105 | 0.0030505 | -0.29297 | 59.024 | -63.7711 | 58.9737 | 59.079 | -63.9038 | 59.0744 | 0.37537 | 59.0103 | -63.6703 | 59.0607 | 59.1339 | 58.9325 | 0.15564 | -0.1236 | -0.07782 | -0.12817 | 122.7264 | 122.7219 | -0.25635 | 122.8455 | -0.13275 | -0.022888 | -0.091553 | -0.041199 | 122.7814 | 63.8031 | 122.58 | 63.826 | 122.6028 | 122.85 | 122.7448 | 122.8043 | 122.731 | 122.7951 | 122.6807 | 122.6715 | 122.6578 | -122.8729 | -122.7722 | 122.6212 | 122.7081 | 63.3545 | 64.0228
1386.8906 | 122.9462 | -63.5834 | 59.0927 | -0.16724 | 0.069058 | 0.1258 | 0.066804 | -0.0010253 | 0.00093144 | 0.00030553 | -0.058258 | 0.16288 | 0.12709 | -0.0022986 | 0.056251 | 0.10564 | -0.0020765 | -0.20599 | 59.0012 | -63.6978 | 59.0836 | 59.2117 | -63.7482 | 59.1705 | 0.53101 | 59.0103 | -63.6337 | 59.1248 | 59.2529 | 59.0836 | 0.29755 | -0.11444 | -0.091552 | -0.009155 | 122.7951 | 122.7539 | -0.16479 | 122.8683 | -0.050354 | -0.050354 | -0.082397 | 0.032044 | 122.8363 | 63.8809 | 122.6669 | 63.9313 | 122.7173 | 122.9095 | 122.7814 | 122.8867 | 122.7585 | 122.699 | 122.644 | 122.5845 | 122.5937 | -122.7905 | -122.7264 | 122.6669 | 122.7081 | 63.3774 | 64.1144
1387.8281 | 122.8775 | -63.6475 | 59.0973 | -0.1825 | 0.066281 | 0.12773 | 0.0683 | -0.0018799 | -0.0020594 | -0.0026853 | -0.16812 | 0.16309 | 0.12815 | 0.0017602 | 0.058174 | 0.10479 | 0.0017687 | -0.35248 | 58.992 | -63.826 | 58.9691 | 58.6761 | -64.0182 | 59.3079 | 0.37994 | 58.992 | -63.6566 | 59.0424 | 59.111 | 58.8959 | 0.11444 | -0.17853 | -0.10529 | -0.12817 | 122.3236 | 122.9553 | -0.37079 | 123.1338 | -0.19226 | -0.009155 | -0.10529 | -0.054932 | 122.7585 | 63.7619 | 122.5433 | 63.7711 | 122.5525 | 122.5021 | 122.7951 | 122.7676 | 122.699 | 122.818 | 122.6486 | 122.6395 | 122.6395 | -122.9233 | -122.7539 | 122.6166 | 122.6898 | 63.295 | 64.0274
1388.8906 | 122.9691 | -63.62 | 59.0652 | -0.24353 | 0.066922 | 0.12687 | 0.069368 | 4.2692e-05 | -0.0014184 | -0.0016171 | -0.049103 | 0.16267 | 0.12751 | -0.0055028 | 0.058174 | 0.10479 | -0.00036747 | -0.29297 | 59.0149 | -63.7344 | 59.0836 | 59.1156 | -63.8397 | 59.1797 | 0.39368 | 58.9783 | -63.6566 | 59.2987 | 59.1934 | 59.0424 | 0.23804 | -0.11444 | -0.050354 | 0.01831 | 122.7356 | 122.7997 | -0.21973 | 122.9141 | -0.10529 | -0.036621 | -0.086976 | 0.23346 | 122.8134 | 63.858 | 122.6624 | 63.8947 | 122.699 | 122.85 | 122.818 | 122.85 | 122.9553 | 122.7493 | 122.6349 | 122.6349 | 122.5983 | -122.7997 | -122.7219 | 122.7036 | 122.9187 | 63.327 | 64.0137
1389.8281 | 122.9279 | -63.6658 | 59.079 | -0.20538 | 0.068631 | 0.12666 | 0.071077 | 0.0060241 | -0.0012048 | -0.00076267 | -0.14676 | 0.16502 | 0.1288 | 0.001974 | 0.058387 | 0.10329 | -0.00015387 | -0.37537 | 59.024 | -63.8031 | 58.9737 | 59.0103 | -63.8947 | 59.2209 | 0.30212 | 58.9966 | -63.7115 | 59.1431 | 59.2346 | 58.9462 | 0.16479 | -0.13733 | -0.054931 | -0.10528 | 122.6761 | 122.8867 | -0.22888 | 123.024 | -0.091552 | -0.045777 | -0.082397 | 0.064087 | 122.9004 | 63.8306 | 122.612 | 63.8763 | 122.6578 | 122.8134 | 122.7768 | 122.9462 | 122.8546 | 122.8271 | 122.7081 | 122.6898 | 122.6624 | -122.8821 | -122.7905 | 122.6395 | 122.8088 | 63.2904 | 63.9679
1390.8906 | 123.0331 | -63.6292 | 59.0332 | -0.17487 | 0.067776 | 0.12538 | 0.067018 | -0.0012391 | -0.0027002 | 0.00051913 | -0.012482 | 0.16459 | 0.12815 | -0.0035802 | 0.057533 | 0.10436 | 0.00048713 | -0.27008 | 59.0057 | -63.7665 | 59.1476 | 59.1797 | -63.7482 | 59.1888 | 0.53558 | 58.9828 | -63.6475 | 59.6786 | 59.2575 | 59.1705 | 0.26093 | -0.13733 | -0.027466 | 0.11444 | 122.8088 | 122.818 | -0.11902 | 122.9553 | 0.01831 | -0.018311 | -0.050354 | 0.64545 | 122.8867 | 63.8901 | 122.7997 | 63.9084 | 122.818 | 122.9462 | 122.9141 | 122.905 | 123.3261 | 122.7722 | 122.6303 | 122.6349 | 122.612 | -122.7997 | -122.6807 | 122.7768 | 123.3078 | 63.3591 | 64.1647
1391.8281 | 122.8317 | -63.6932 | 59.0424 | -0.26642 | 0.066495 | 0.12687 | 0.069154 | 0.0028199 | -0.0020594 | 0.0022281 | -0.1376 | 0.16544 | 0.12794 | -0.00080325 | 0.056678 | 0.105 | -0.00079467 | -0.36163 | 59.0149 | -63.8168 | 58.9096 | 58.992 | -63.9862 | 59.0149 | 0.29297 | 59.024 | -63.6887 | 59.0469 | 59.0881 | 58.9554 | -0.041199 | -0.1236 | -0.027465 | -0.13275 | 122.6852 | 122.7081 | -0.29297 | 122.8317 | -0.16937 | 0.004577 | -0.01831 | 0.004578 | 122.7814 | 63.652 | 122.6486 | 63.6475 | 122.644 | 122.8088 | 122.7264 | 122.7768 | 122.7356 | 122.8317 | 122.7127 | 122.7081 | 122.7173 | -122.8592 | -122.731 | 122.6028 | 122.7402 | 63.3316 | 63.9862
1392.8906 | 123.056 | -63.5834 | 59.079 | -0.21301 | 0.06799 | 0.12666 | 0.067872 | -0.0012391 | -0.0014184 | -0.0033261 | -0.027741 | 0.16416 | 0.12751 | -0.0040076 | 0.057533 | 0.10415 | -0.0012219 | -0.23346 | 59.0195 | -63.7253 | 59.0744 | 59.2346 | -63.739 | 59.2072 | 0.58594 | 58.9783 | -63.6108 | 59.198 | 59.317 | 59.1339 | 0.30212 | -0.14191 | -0.059509 | -0.004577 | 122.818 | 122.7905 | -0.15564 | 122.9324 | -0.013733 | -0.027466 | -0.10071 | 0.11902 | 122.9004 | 63.8855 | 122.7173 | 63.913 | 122.7448 | 122.9599 | 122.7997 | 122.9279 | 122.8088 | 122.7448 | 122.5891 | 122.6028 | 122.5616 | -122.8043 | -122.6898 | 122.6578 | 122.7814 | 63.3499 | 64.1693
1393.8281 | 122.8638 | -63.6429 | 59.0698 | -0.19012 | 0.069912 | 0.12815 | 0.070649 | 0.0043151 | -0.0018458 | -0.00054907 | -0.1376 | 0.16331 | 0.12709 | 0.0011194 | 0.056038 | 0.10543 | 0.00070073 | -0.33417 | 59.0286 | -63.8077 | 58.9233 | 58.9966 | -63.945 | 59.0149 | 0.27008 | 58.9966 | -63.6612 | 59.0332 | 59.0881 | 58.8959 | 0.09613 | -0.1648 | -0.041199 | -0.14648 | 122.6395 | 122.6578 | -0.30212 | 122.8226 | -0.13733 | -0.018311 | -0.073242 | -0.036621 | 122.731 | 63.739 | 122.5388 | 63.7573 | 122.5571 | 122.8043 | 122.731 | 122.7493 | 122.6944 | 122.8363 | 122.6578 | 122.6715 | 122.6395 | -122.8775 | -122.731 | 122.5662 | 122.6761 | 63.3087 | 63.913
1394.8906 | 122.9691 | -63.6292 | 59.0332 | -0.20538 | 0.067776 | 0.13093 | 0.067232 | -0.00059811 | -0.00056396 | -0.0028989 | -0.067413 | 0.16331 | 0.12965 | -0.003153 | 0.056465 | 0.10479 | -0.0033581 | -0.31128 | 58.9691 | -63.7482 | 59.0149 | 59.1385 | -63.8397 | 59.1293 | 0.3891 | 58.9783 | -63.6703 | 59.0973 | 59.1705 | 59.0012 | 0.16022 | -0.11902 | -0.064087 | -0.01831 | 122.7676 | 122.7585 | -0.21057 | 122.8775 | -0.091553 | -0.041199 | -0.054932 | 0.064087 | 122.7997 | 63.7894 | 122.6303 | 63.8306 | 122.6715 | 122.8867 | 122.7631 | 122.8409 | 122.7676 | 122.7173 | 122.6486 | 122.5983 | 122.6074 | -122.7814 | -122.7036 | 122.644 | 122.7264 | 63.3179 | 64.0182
1395.8281 | 122.9462 | -63.6566 | 59.0744 | -0.16724 | 0.065854 | 0.12666 | 0.070863 | -0.00038451 | -0.0027002 | -0.0018307 | -0.11929 | 0.16373 | 0.12687 | 0.0026148 | 0.055397 | 0.10585 | 0.00070073 | -0.35248 | 58.992 | -63.8031 | 58.9508 | 59.0561 | -63.9175 | 59.0515 | 0.35248 | 58.9828 | -63.6978 | 59.111 | 59.1385 | 58.96 | 0.13275 | -0.14648 | -0.082398 | -0.1236 | 122.7127 | 122.7081 | -0.26093 | 122.8546 | -0.11444 | -0.041199 | -0.091553 | 0.036621 | 122.7951 | 63.7894 | 122.6166 | 63.8306 | 122.6578 | 122.8592 | 122.7539 | 122.8363 | 122.8088 | 122.7951 | 122.6807 | 122.6486 | 122.6395 | -122.8775 | -122.7722 | 122.6074 | 122.7676 | 63.3041 | 64.0091
1396.8906 | 122.9736 | -63.6063 | 59.0607 | -0.13672 | 0.069272 | 0.12815 | 0.068513 | -0.0010253 | -0.0016322 | -0.00033547 | -0.036896 | 0.16138 | 0.12901 | -0.011484 | 0.060737 | 0.10521 | -0.0020765 | -0.29297 | 58.9966 | -63.7665 | 59.0378 | 59.0973 | -63.8489 | 59.1293 | 0.41657 | 58.9737 | -63.6475 | 59.1064 | 59.2117 | 59.0195 | 0.22888 | -0.16022 | -0.064087 | -0.022888 | 122.7036 | 122.7356 | -0.24262 | 122.8958 | -0.082398 | -0.041199 | -0.086975 | 0.045776 | 122.818 | 63.8351 | 122.6257 | 63.8763 | 122.6669 | 122.8638 | 122.8043 | 122.8592 | 122.7539 | 122.7631 | 122.6212 | 122.6028 | 122.58 | -122.8271 | -122.7081 | 122.644 | 122.7127 | 63.3133 | 64.0228
1397.8281 | 122.9095 | -63.6154 | 59.0881 | -0.15198 | 0.067349 | 0.12709 | 0.069368 | 0.00089729 | 7.6842e-05 | -0.0022581 | -0.14066 | 0.1648 | 0.12773 | 0.0024012 | 0.058387 | 0.10735 | -0.0037855 | -0.37079 | 59.0012 | -63.7939 | 59.0057 | 59.1156 | -63.858 | 59.1202 | 0.43488 | 59.0286 | -63.6475 | 59.0881 | 59.1705 | 58.96 | 0.19226 | -0.17853 | -0.086975 | -0.082398 | 122.731 | 122.7356 | -0.24262 | 122.9141 | -0.064087 | -0.032044 | -0.05951 | 0 | 122.7859 | 63.8077 | 122.5754 | 63.8397 | 122.6074 | 122.9095 | 122.7997 | 122.818 | 122.7356 | 122.7951 | 122.6761 | 122.6166 | 122.644 | -122.8821 | -122.7356 | 122.6212 | 122.7036 | 63.2446 | 64.0503
1398.8906 | 122.8958 | -63.62 | 59.0973 | -0.11383 | 0.067563 | 0.12645 | 0.067018 | 0.00089729 | -0.0031274 | -0.0014035 | -0.088776 | 0.16502 | 0.12815 | -0.00016245 | 0.059456 | 0.10457 | -0.0035719 | -0.25635 | 59.0698 | -63.7665 | 58.9783 | 59.079 | -63.8397 | 59.111 | 0.44861 | 59.0424 | -63.6337 | 59.0652 | 59.1705 | 58.9737 | 0.23346 | -0.14648 | -0.027466 | -0.11902 | 122.699 | 122.731 | -0.21973 | 122.8775 | -0.073243 | -0.013733 | -0.054932 | -0.032043 | 122.7905 | 63.8535 | 122.5937 | 63.8672 | 122.6074 | 122.8455 | 122.7447 | 122.8043 | 122.699 | 122.8363 | 122.6761 | 122.6898 | 122.6624 | -122.8638 | -122.731 | 122.5983 | 122.6852 | 63.3636 | 64.0686
1399.8281 | 122.8867 | -63.6337 | 59.0836 | -0.13672 | 0.067135 | 0.12623 | 0.072145 | 0.0021789 | -0.00077756 | 9.193e-05 | -0.1254 | 0.16544 | 0.12901 | -0.00016245 | 0.058387 | 0.10543 | -0.0039991 | -0.27924 | 58.992 | -63.7848 | 58.9874 | 59.0927 | -63.8626 | 59.0652 | 0.41657 | 59.0057 | -63.6475 | 59.0607 | 59.1522 | 58.9417 | 0.16022 | -0.15106 | -0.091553 | -0.09613 | 122.7264 | 122.699 | -0.22888 | 122.85 | -0.07782 | -0.013733 | -0.07782 | -0.022888 | 122.7859 | 63.7939 | 122.5754 | 63.8077 | 122.5891 | 122.8775 | 122.7722 | 122.7997 | 122.7081 | 122.7768 | 122.6532 | 122.6257 | 122.6395 | -122.8683 | -122.731 | 122.6212 | 122.6944 | 63.3545 | 64.0503
1400.8906 | 122.9095 | -63.6337 | 59.1019 | -0.098572 | 0.065426 | 0.12773 | 0.069368 | 0.00089729 | -0.0012048 | -0.0016171 | -0.11014 | 0.16587 | 0.12666 | -0.0025122 | 0.057747 | 0.10521 | -0.0014355 | -0.24719 | 59.0515 | -63.7802 | 59.0149 | 59.1156 | -63.8489 | 59.1202 | 0.47607 | 59.0195 | -63.6703 | 59.0836 | 59.198 | 59.0012 | 0.24719 | -0.14648 | -0.050354 | -0.086975 | 122.7493 | 122.7539 | -0.21515 | 122.9004 | -0.068665 | -0.036621 | -0.082398 | -0.018311 | 122.8317 | 63.8809 | 122.6349 | 63.9175 | 122.6715 | 122.8958 | 122.7951 | 122.8683 | 122.7539 | 122.8317 | 122.6898 | 122.6852 | 122.6532 | -122.8821 | -122.7722 | 122.6486 | 122.7173 | 63.3865 | 64.1098
1401.8281 | 122.9187 | -63.6703 | 59.0469 | -0.50293 | 0.070126 | 0.1258 | 0.068513 | -0.00059811 | -0.0033412 | 0.0011599 | -0.1376 | 0.16352 | 0.12666 | 0.0026148 | 0.057319 | 0.10436 | -0.0014355 | -0.37994 | 58.9645 | -63.7848 | 58.8959 | 59.0698 | -63.945 | 59.024 | 0.27924 | 58.9966 | -63.6978 | 59.0607 | 59.1202 | 58.9279 | 0.10986 | -0.11444 | -0.082397 | -0.15106 | 122.7402 | 122.6944 | -0.27466 | 122.8088 | -0.16022 | -0.027466 | -0.050354 | 0.013733 | 122.7905 | 63.7802 | 122.5983 | 63.8077 | 122.6257 | 122.8546 | 122.6807 | 122.818 | 122.7585 | 122.7493 | 122.6944 | 122.6349 | 122.6669 | -122.8317 | -122.7448 | 122.5662 | 122.731 | 63.2904 | 63.9496
1402.8906 | 122.9645 | -63.5925 | 59.0378 | -0.12909 | 0.067349 | 0.12687 | 0.067445 | -0.0040161 | -0.00505 | -0.0028989 | -0.046051 | 0.16309 | 0.12922 | -0.0063574 | 0.057319 | 0.10564 | -0.0037855 | -0.20142 | 59.0103 | -63.739 | 59.0927 | 59.23 | -63.7299 | 59.2117 | 0.58136 | 58.992 | -63.6154 | 59.1019 | 59.5825 | 59.1064 | 0.18768 | -0.14648 | -0.027466 | 0.054931 | 122.8226 | 122.8043 | -0.13733 | 122.9507 | 0.009156 | -0.022888 | -0.045777 | 0.064087 | 123.175 | 63.7802 | 122.699 | 63.8031 | 122.7219 | 122.9691 | 122.8317 | 123.1979 | 122.7173 | 122.7493 | 122.6074 | 122.6028 | 122.5845 | -122.7768 | -122.6532 | 122.6852 | 122.6944 | 63.3911 | 64.1739
1403.8281 | 122.9324 | -63.6337 | 59.0652 | -0.11383 | 0.068631 | 0.12794 | 0.069368 | -0.00059811 | -0.0065454 | -0.0014035 | -0.14371 | 0.16395 | 0.12709 | -0.0072118 | 0.058174 | 0.10543 | -0.0031445 | -0.28839 | 59.024 | -63.7711 | 59.0195 | 59.1156 | -63.858 | 59.0836 | 0.43488 | 59.0103 | -63.6475 | 59.0698 | 59.1522 | 58.96 | 0.17395 | -0.13733 | -0.041199 | -0.045777 | 122.7493 | 122.7173 | -0.2243 | 122.8546 | -0.086975 | -0.013733 | -0.054932 | 0.004577 | 122.7859 | 63.8077 | 122.5937 | 63.8214 | 122.6074 | 122.8867 | 122.7905 | 122.7997 | 122.7173 | 122.7951 | 122.6578 | 122.6578 | 122.644 | -122.8363 | -122.7127 | 122.6532 | 122.7036 | 63.3453 | 64.0686
1404.8906 | 122.9416 | -63.588 | 59.0561 | -0.15961 | 0.068203 | 0.12687 | 0.067659 | -0.0031617 | -0.00099116 | -0.0014035 | -0.058258 | 0.16352 | 0.12751 | -0.0040076 | 0.05796 | 0.1065 | -0.0014355 | -0.31586 | 58.9737 | -63.7436 | 59.0057 | 59.1156 | -63.8626 | 59.111 | 0.39368 | 58.9645 | -63.652 | 59.0698 | 59.1934 | 59.0378 | 0.16479 | -0.15564 | -0.082397 | -0.050354 | 122.7036 | 122.699 | -0.27466 | 122.8546 | -0.11902 | -0.064087 | -0.091552 | 0.013733 | 122.7814 | 63.7527 | 122.6257 | 63.8168 | 122.6898 | 122.8592 | 122.7493 | 122.8455 | 122.7219 | 122.7173 | 122.6166 | 122.5616 | 122.5525 | -122.7997 | -122.7081 | 122.5937 | 122.6578 | 63.2721 | 63.9816
1405.8281 | 122.9324 | -63.6292 | 59.0881 | -0.098572 | 0.066922 | 0.12773 | 0.069154 | 0.0028199 | -0.0033412 | -0.00012167 | -0.14676 | 0.16395 | 0.13008 | -0.0033666 | 0.056465 | 0.10564 | 0.00027333 | -0.24261 | 59.0332 | -63.7711 | 59.0149 | 59.1339 | -63.8443 | 59.1019 | 0.45776 | 59.0332 | -63.6566 | 59.0332 | 59.0561 | 59.024 | 0.25635 | -0.14191 | -0.054932 | -0.073242 | 122.7631 | 122.731 | -0.21515 | 122.8729 | -0.073242 | -0.027466 | -0.054932 | -0.054932 | 122.6852 | 63.8855 | 122.6532 | 63.913 | 122.6807 | 122.905 | 122.7859 | 122.7127 | 122.6898 | 122.8043 | 122.6898 | 122.6624 | 122.6624 | -122.8592 | -122.7448 | 122.644 | 122.6624 | 63.3865 | 64.0869
1406.8906 | 122.9416 | -63.62 | 59.1202 | -0.12146 | 0.069485 | 0.12666 | 0.069154 | -0.00059811 | -0.003982 | -0.0031125 | -0.052155 | 0.16267 | 0.12602 | -0.0084936 | 0.057747 | 0.10543 | -0.00079467 | -0.21973 | 59.0149 | -63.7115 | 59.0469 | 59.1751 | -63.7894 | 59.1568 | 0.52643 | 59.0332 | -63.6337 | 59.0881 | 59.2072 | 59.0424 | 0.29755 | -0.091553 | -0.10529 | -0.073242 | 122.7951 | 122.7768 | -0.16937 | 122.8683 | -0.07782 | -0.013733 | -0.086975 | -0.032043 | 122.8271 | 63.9175 | 122.6624 | 63.9313 | 122.6761 | 122.8867 | 122.7585 | 122.8409 | 122.7219 | 122.7264 | 122.6669 | 122.6349 | 122.6532 | -122.8317 | -122.7539 | 122.6669 | 122.7081 | 63.4003 | 64.1464
1407.8281 | 122.9324 | -63.6383 | 59.0836 | -0.15961 | 0.066067 | 0.12687 | 0.068727 | 4.2692e-05 | -0.0044092 | -0.00033547 | -0.11929 | 0.16395 | 0.12773 | 0.0011194 | 0.057106 | 0.10671 | -0.0029309 | -0.26093 | 59.0332 | -63.7573 | 59.0103 | 59.1156 | -63.8397 | 59.0927 | 0.39825 | 59.0149 | -63.6566 | 59.1064 | 59.1843 | 58.9645 | 0.22888 | -0.11902 | -0.050354 | -0.073242 | 122.7539 | 122.731 | -0.20142 | 122.85 | -0.082398 | -0.01831 | -0.068664 | 0.022888 | 122.8226 | 63.8672 | 122.6028 | 63.8855 | 122.6212 | 122.8729 | 122.7676 | 122.8409 | 122.7631 | 122.7905 | 122.6715 | 122.6715 | 122.6532 | -122.8409 | -122.7402 | 122.6486 | 122.7448 | 63.3774 | 64.0366
1408.8281 | 122.8958 | -63.6246 | 59.1202 | -0.075684 | 0.066281 | 0.12815 | 0.066804 | -0.0010253 | -0.0037684 | -0.0024717 | -0.097931 | 0.16544 | 0.12944 | -0.0069982 | 0.058174 | 0.10628 | -0.0010083 | -0.24719 | 59.0561 | -63.7344 | 58.9279 | 59.0012 | -63.8031 | 59.0836 | 0.45319 | 59.0332 | -63.6566 | 59.0652 | 59.1568 | 58.9828 | 0.24719 | -0.10986 | -0.064087 | -0.19226 | 122.6257 | 122.7081 | -0.17853 | 122.818 | -0.068665 | -0.032043 | -0.086975 | -0.054931 | 122.7814 | 63.8718 | 122.6074 | 63.9038 | 122.6395 | 122.7356 | 122.6624 | 122.8134 | 122.7219 | 122.7905 | 122.6898 | 122.6807 | 122.6578 | -122.8546 | -122.7768 | 122.5525 | 122.6898 | 63.3774 | 64.0778
1409.8281 | 122.9324 | -63.6383 | 59.079 | -0.15198 | 0.068417 | 0.12602 | 0.068941 | 0.0011109 | -0.005691 | -0.0011899 | -0.12845 | 0.16352 | 0.1288 | -0.0027258 | 0.058174 | 0.10692 | -0.0037855 | -0.23346 | 59.0286 | -63.739 | 59.024 | 59.1248 | -63.8077 | 59.1293 | 0.48523 | 59.0103 | -63.6566 | 59.0927 | 59.1934 | 58.9828 | 0.2655 | -0.10071 | -0.050354 | -0.054931 | 122.7631 | 122.7676 | -0.16937 | 122.8683 | -0.068664 | -0.01831 | -0.068664 | 0.013733 | 122.8317 | 63.9038 | 122.6212 | 63.9221 | 122.6395 | 122.8638 | 122.7631 | 122.85 | 122.7493 | 122.7676 | 122.6669 | 122.6669 | 122.6486 | -122.818 | -122.7356 | 122.6624 | 122.731 | 63.4048 | 64.1235
1410.8906 | 123.0057 | -63.6246 | 59.0515 | -0.16724 | 0.067776 | 0.13008 | 0.067872 | 0.0017517 | -0.0037684 | -0.0014035 | -0.039948 | 0.16181 | 0.12687 | -0.0022986 | 0.056678 | 0.10543 | -0.0014355 | -0.28381 | 58.9508 | -63.7573 | 59.0378 | 59.0698 | -64.1006 | 59.23 | 0.42572 | 58.96 | -63.6429 | 59.1431 | 59.2438 | 59.0378 | 0.16022 | -0.13275 | -0.10071 | -0.013733 | 122.6944 | 122.8546 | -0.47607 | 122.9874 | -0.34332 | -0.01831 | -0.091553 | 0.091552 | 122.8683 | 63.7848 | 122.6624 | 63.8031 | 122.6807 | 122.8271 | 122.7951 | 122.8867 | 122.7859 | 122.7081 | 122.6028 | 122.5754 | 122.5845 | -122.8088 | -122.6944 | 122.6624 | 122.7676 | 63.3408 | 64.0503
1411.8281 | 122.8592 | -63.6246 | 59.1202 | -0.098572 | 0.064999 | 0.12516 | 0.071077 | -0.0027343 | -0.003982 | -0.0031125 | -0.088776 | 0.16694 | 0.12602 | -0.0052892 | 0.058601 | 0.10692 | 0.0045459 | -0.2655 | 59.0607 | -63.7756 | 58.9645 | 59.0744 | -63.8351 | 59.2941 | 0.37994 | 59.0195 | -63.6429 | 59.0424 | 59.1888 | 58.9691 | 0.24719 | -0.15106 | -0.059509 | -0.15564 | 122.699 | 122.9187 | -0.21057 | 123.0698 | -0.059509 | -0.01831 | -0.10071 | -0.07782 | 122.8134 | 63.8718 | 122.5937 | 63.8901 | 122.612 | 122.85 | 122.7402 | 122.8317 | 122.6852 | 122.8363 | 122.6624 | 122.6852 | 122.644 | -122.8958 | -122.7631 | 122.5891 | 122.6669 | 63.3591 | 64.0045
1412.8906 | 122.9736 | -63.6246 | 59.0652 | -0.19012 | 0.06799 | 0.12645 | 0.068727 | -0.00038451 | -0.0061182 | -0.0035397 | -0.036896 | 0.16459 | 0.12687 | -0.00080325 | 0.056892 | 0.10436 | -0.0025037 | -0.32501 | 58.992 | -63.7527 | 58.9874 | 59.1064 | -63.8306 | 59.111 | 0.40283 | 58.9783 | -63.6337 | 59.0836 | 59.2072 | 59.0057 | 0.20142 | -0.12817 | -0.073243 | -0.07782 | 122.731 | 122.7356 | -0.20599 | 122.8638 | -0.077819 | -0.009155 | -0.086976 | 0.01831 | 122.8317 | 63.826 | 122.6303 | 63.8351 | 122.6395 | 122.8592 | 122.7402 | 122.8409 | 122.7173 | 122.7448 | 122.612 | 122.6166 | 122.6028 | -122.818 | -122.699 | 122.612 | 122.7081 | 63.2996 | 64.0274
1413.8281 | 122.8958 | -63.6383 | 59.0927 | -0.075684 | 0.069058 | 0.12666 | 0.069368 | 0.0023925 | -0.002273 | 0.00030553 | -0.11624 | 0.16587 | 0.12901 | 0.0011194 | 0.057533 | 0.1035 | 0.00048713 | -0.24719 | 59.0515 | -63.7573 | 58.9966 | 59.0927 | -63.8351 | 59.1019 | 0.46692 | 59.0332 | -63.652 | 59.0973 | 59.1888 | 59.0103 | 0.26093 | -0.11902 | -0.041198 | -0.09613 | 122.731 | 122.7402 | -0.19684 | 122.8592 | -0.07782 | -0.013733 | -0.059509 | 0.004578 | 122.8271 | 63.8992 | 122.6486 | 63.913 | 122.6624 | 122.85 | 122.7539 | 122.8409 | 122.7493 | 122.8088 | 122.6852 | 122.6898 | 122.6715 | -122.85 | -122.7448 | 122.6349 | 122.7356 | 63.3911 | 64.1052
1414.8906 | 123.0469 | -63.5788 | 59.0881 | -0.21301 | 0.067563 | 0.12666 | 0.070009 | 0.0015381 | -0.0031274 | -0.0033261 | -0.024689 | 0.16224 | 0.12858 | -0.0076392 | 0.056465 | 0.10607 | -0.0010083 | -0.23346 | 58.9966 | -63.7115 | 59.0515 | 59.2255 | -63.7344 | 59.2209 | 0.59967 | 58.9783 | -63.6154 | 59.166 | 59.285 | 59.111 | 0.31586 | -0.13275 | -0.091553 | -0.036621 | 122.8043 | 122.7997 | -0.15564 | 122.9324 | -0.022888 | -0.036621 | -0.10986 | 0.07782 | 122.8638 | 63.8947 | 122.6898 | 63.9313 | 122.7264 | 122.937 | 122.7631 | 122.9004 | 122.7814 | 122.7081 | 122.5937 | 122.5754 | 122.5571 | -122.7997 | -122.7036 | 122.6303 | 122.7448 | 63.3453 | 64.1785
1415.8281 | 122.9233 | -63.588 | 59.0927 | -0.15961 | 0.06799 | 0.12709 | 0.070436 | 0.00068369 | -0.0029138 | -0.0018307 | -0.11319 | 0.1648 | 0.12709 | -0.0080664 | 0.057533 | 0.10372 | -0.0022901 | -0.25177 | 59.0286 | -63.7985 | 58.992 | 59.1019 | -63.826 | 59.111 | 0.46692 | 59.0515 | -63.6337 | 59.1019 | 59.2072 | 59.0103 | 0.22888 | -0.21057 | -0.064087 | -0.10071 | 122.6898 | 122.699 | -0.23804 | 122.9095 | -0.027466 | -0.045776 | -0.041198 | 0.009156 | 122.7951 | 63.8168 | 122.5983 | 63.8626 | 122.644 | 122.9004 | 122.7905 | 122.8409 | 122.7356 | 122.8271 | 122.6852 | 122.6166 | 122.6395 | -122.8912 | -122.7264 | 122.58 | 122.6898 | 63.3362 | 64.0549
1416.8906 | 122.9599 | -63.6337 | 59.0332 | -0.16724 | 0.066281 | 0.12794 | 0.067659 | 0.0015381 | -0.0020594 | -0.0022581 | -0.070465 | 0.16267 | 0.12986 | 5.1352e-05 | 0.057747 | 0.10585 | -0.00058107 | -0.31128 | 58.9737 | -63.7527 | 59.0012 | 59.1019 | -63.8443 | 59.111 | 0.40741 | 58.9737 | -63.652 | 59.0973 | 59.1568 | 59.0332 | 0.16937 | -0.11902 | -0.059509 | -0.032043 | 122.7356 | 122.7448 | -0.21057 | 122.8638 | -0.091552 | -0.018311 | -0.059509 | 0.064087 | 122.7905 | 63.8031 | 122.6669 | 63.8214 | 122.6852 | 122.8546 | 122.7539 | 122.8088 | 122.7493 | 122.7264 | 122.6257 | 122.6074 | 122.6074 | -122.7859 | -122.6852 | 122.6349 | 122.731 | 63.3224 | 64.0411
1417.8281 | 122.8821 | -63.6292 | 59.0927 | -0.27405 | 0.067349 | 0.12367 | 0.069368 | 0.0015381 | -0.0052638 | 0.00030553 | -0.12234 | 0.16373 | 0.12794 | -0.0035802 | 0.057106 | 0.10393 | -0.0029309 | -0.23804 | 59.0469 | -63.7802 | 58.9874 | 59.0698 | -63.8672 | 59.0973 | 0.43488 | 59.0561 | -63.6566 | 59.0607 | 59.1705 | 58.9828 | 0.23804 | -0.15106 | -0.045776 | -0.10529 | 122.699 | 122.7264 | -0.23804 | 122.8775 | -0.086975 | -0.027466 | -0.036621 | -0.032043 | 122.7997 | 63.8672 | 122.612 | 63.8947 | 122.6395 | 122.85 | 122.7676 | 122.8271 | 122.7173 | 122.8271 | 122.7127 | 122.6761 | 122.6852 | -122.8729 | -122.7493 | 122.6166 | 122.6898 | 63.3911 | 64.064
1418.8906 | 123.0286 | -63.588 | 59.0561 | -0.15198 | 0.066281 | 0.1273 | 0.066377 | 0.0023925 | -0.0027002 | -0.0016171 | -0.049103 | 0.16352 | 0.12837 | -0.0061438 | 0.058815 | 0.105 | -0.00058107 | -0.24261 | 59.0012 | -63.7482 | 59.1156 | 59.23 | -63.7299 | 59.2255 | 0.6134 | 59.0149 | -63.6108 | 59.1934 | 59.2987 | 59.1248 | 0.30212 | -0.16022 | -0.054931 | 0.05951 | 122.818 | 122.8134 | -0.14191 | 122.9736 | 0.018311 | -0.022888 | -0.041198 | 0.13733 | 122.8867 | 63.8901 | 122.7127 | 63.913 | 122.7356 | 122.9782 | 122.8638 | 122.9095 | 122.8043 | 122.7493 | 122.6257 | 122.5891 | 122.6028 | -122.8043 | -122.6669 | 122.7036 | 122.7814 | 63.3453 | 64.2014
1419.8281 | 122.9553 | -63.5834 | 59.1751 | -0.075684 | 0.066708 | 0.12474 | 0.068941 | 0.0028199 | -0.0024866 | -0.0024717 | -0.085724 | 0.16309 | 0.12815 | -0.001444 | 0.059669 | 0.10479 | -0.0012219 | -0.25177 | 59.0652 | -63.7344 | 58.9737 | 59.0836 | -63.8306 | 59.1522 | 0.43945 | 59.0424 | -63.6475 | 59.079 | 59.166 | 58.9874 | 0.18768 | -0.15106 | -0.10986 | -0.20142 | 122.6669 | 122.7356 | -0.24719 | 122.8867 | -0.09613 | -0.064087 | -0.13275 | -0.096131 | 122.7493 | 63.7711 | 122.5708 | 63.8351 | 122.6349 | 122.818 | 122.7081 | 122.8134 | 122.7264 | 122.7997 | 122.6898 | 122.6486 | 122.6257 | -122.9095 | -122.8226 | 122.5571 | 122.6624 | 63.3316 | 64.0228
1420.8906 | 122.9782 | -63.6292 | 59.0652 | -0.17487 | 0.067776 | 0.12709 | 0.0683 | 0.0034607 | -0.0020594 | 9.193e-05 | -0.088776 | 0.16416 | 0.12751 | 0.0028284 | 0.056678 | 0.1035 | -0.0044263 | -0.31586 | 58.9691 | -63.7527 | 59.024 | 59.1156 | -63.8351 | 59.1248 | 0.41199 | 58.9691 | -63.6337 | 59.111 | 59.1751 | 59.0286 | 0.23804 | -0.1236 | -0.096131 | -0.041199 | 122.7448 | 122.7539 | -0.20599 | 122.8775 | -0.082397 | -0.004578 | -0.096131 | 0.045776 | 122.8043 | 63.8672 | 122.6578 | 63.8718 | 122.6624 | 122.8683 | 122.7768 | 122.8088 | 122.7448 | 122.7219 | 122.6028 | 122.5983 | 122.5983 | -122.818 | -122.699 | 122.6532 | 122.7402 | 63.3133 | 64.0411
1421.8281 | 122.8958 | -63.6017 | 59.0927 | -0.083313 | 0.069912 | 0.12773 | 0.070222 | -0.00081171 | -0.0016322 | 9.193e-05 | -0.070465 | 0.1648 | 0.1273 | -0.00058965 | 0.057533 | 0.10308 | -0.0016493 | -0.21057 | 59.0469 | -63.7344 | 59.0469 | 59.1476 | -63.7711 | 59.1843 | 0.49439 | 59.0332 | -63.62 | 59.1156 | 59.23 | 59.0561 | 0.34332 | -0.13275 | -0.045776 | -0.045776 | 122.7493 | 122.786 | -0.16937 | 122.9187 | -0.036621 | -0.01831 | -0.059509 | 0.022889 | 122.8317 | 63.945 | 122.6578 | 63.9633 | 122.6761 | 122.8821 | 122.7814 | 122.85 | 122.7356 | 122.7814 | 122.6532 | 122.6486 | 122.6349 | -122.8271 | -122.7127 | 122.6486 | 122.7173 | 63.3911 | 64.0961
1422.8906 | 122.8546 | -63.652 | 59.0561 | -0.15198 | 0.065854 | 0.12666 | 0.070436 | 0.0021789 | -0.0027002 | -0.00012167 | -0.16812 | 0.16395 | 0.12773 | 0.00047855 | 0.057319 | 0.10628 | 0.0013415 | -0.3067 | 59.0012 | -63.7848 | 58.9462 | 59.0469 | -63.8992 | 59.0378 | 0.34332 | 59.0149 | -63.6703 | 59.0332 | 59.0881 | 58.8959 | 0.13275 | -0.13275 | -0.054931 | -0.10986 | 122.699 | 122.6898 | -0.24719 | 122.8226 | -0.11444 | -0.01831 | -0.041198 | -0.022888 | 122.7402 | 63.7848 | 122.5479 | 63.8031 | 122.5662 | 122.8317 | 122.731 | 122.7585 | 122.7036 | 122.7859 | 122.6852 | 122.6532 | 122.6669 | -122.8409 | -122.7264 | 122.5983 | 122.6852 | 63.3453 | 63.9954
1423.8281 | 122.9919 | -63.5834 | 59.0881 | -0.22064 | 0.066708 | 0.12431 | 0.068727 | -0.0016663 | -0.002273 | -0.0016171 | -0.027741 | 0.16288 | 0.12922 | -0.0084936 | 0.056678 | 0.10372 | 5.9726e-05 | -0.20142 | 59.0332 | -63.7207 | 59.0881 | 59.2072 | -63.7482 | 59.1843 | 0.55847 | 58.9966 | -63.6017 | 59.1431 | 59.2575 | 59.0927 | 0.31586 | -0.13733 | -0.054932 | 0 | 122.7905 | 122.7676 | -0.16479 | 122.905 | -0.027466 | -0.018311 | -0.091553 | 0.054931 | 122.8409 | 63.8992 | 122.6761 | 63.9175 | 122.6944 | 122.9279 | 122.8088 | 122.8592 | 122.7448 | 122.7539 | 122.5983 | 122.6166 | 122.58 | -122.8088 | -122.6898 | 122.6715 | 122.7264 | 63.382 | 64.1418
1424.8906 | 122.8912 | -63.652 | 59.0607 | -0.15198 | 0.067349 | 0.1273 | 0.071077 | 0.0021789 | -0.0029138 | -0.0014035 | -0.14676 | 0.16502 | 0.12687 | -0.00016245 | 0.056465 | 0.10564 | -0.0012219 | -0.28839 | 59.0286 | -63.7756 | 58.9966 | 59.0973 | -63.8718 | 59.0836 | 0.43488 | 59.0149 | -63.6612 | 59.0698 | 59.1385 | 58.9508 | 0.17853 | -0.1236 | -0.032044 | -0.064087 | 122.7493 | 122.7356 | -0.21973 | 122.8592 | -0.09613 | -0.009155 | -0.045776 | 0.009155 | 122.7905 | 63.8306 | 122.6028 | 63.8397 | 122.612 | 122.8729 | 122.7722 | 122.7997 | 122.731 | 122.8043 | 122.6761 | 122.6807 | 122.6669 | -122.8363 | -122.7219 | 122.6486 | 122.7219 | 63.3636 | 64.0869
1425.8281 | 123.0011 | -63.6017 | 59.0652 | -0.14435 | 0.067563 | 0.12559 | 0.069154 | -0.00059811 | -0.0018458 | -0.00054907 | -0.033844 | 0.16224 | 0.12794 | -0.0091344 | 0.058174 | 0.1035 | 0.0017687 | -0.26093 | 58.9828 | -63.7253 | 59.0515 | 59.1843 | -63.7619 | 59.166 | 0.54016 | 59.0012 | -63.6154 | 59.1614 | 59.2987 | 59.1064 | 0.31128 | -0.1236 | -0.082398 | -0.013733 | 122.786 | 122.7676 | -0.16022 | 122.8912 | -0.036621 | -0.013732 | -0.064087 | 0.09613 | 122.9004 | 63.913 | 122.7081 | 63.9267 | 122.7219 | 122.9095 | 122.7768 | 122.9141 | 122.7768 | 122.7081 | 122.6166 | 122.5845 | 122.6028 | -122.7905 | -122.6807 | 122.6532 | 122.7631 | 63.3408 | 64.1418
1426.8906 | 122.9691 | -63.62 | 59.0332 | -0.20538 | 0.068631 | 0.12773 | 0.068513 | 0.00089729 | -0.00013676 | -0.0058897 | -0.082672 | 0.16352 | 0.12559 | 0.001333 | 0.056678 | 0.10479 | -0.00015387 | -0.29755 | 58.9691 | -63.7756 | 59.0378 | 59.1293 | -63.8397 | 59.1293 | 0.41657 | 58.9691 | -63.6383 | 59.1202 | 59.1751 | 59.0195 | 0.16022 | -0.15564 | -0.064087 | 0.004578 | 122.7493 | 122.7493 | -0.21973 | 122.905 | -0.064087 | -0.018311 | -0.064087 | 0.086975 | 122.7951 | 63.7802 | 122.6395 | 63.7985 | 122.6578 | 122.905 | 122.8134 | 122.8134 | 122.7585 | 122.7448 | 122.6074 | 122.5891 | 122.5891 | -122.8088 | -122.6715 | 122.6578 | 122.7402 | 63.3224 | 64.0366
1427.8281 | 123.0103 | -63.5925 | 59.0515 | -0.13672 | 0.068203 | 0.1273 | 0.068513 | -0.0012391 | -0.0014184 | -0.0014035 | -0.21695 | 0.16352 | 0.12602 | -0.0050756 | 0.056251 | 0.10415 | -0.0018629 | -0.14648 | 59.0103 | -63.7115 | 59.1293 | 59.1522 | -63.2263 | 59.3353 | 0.78278 | 58.96 | -63.6383 | 59.1705 | 59.2758 | 59.111 | 0.34332 | -0.11902 | -0.041199 | 0.077819 | 122.7448 | 122.9279 | 0.36621 | 123.0469 | 0.48523 | -0.045777 | -0.091553 | 0.11902 | 122.8683 | 63.9359 | 122.7036 | 63.9816 | 122.7493 | 122.8638 | 122.8409 | 122.9141 | 122.8088 | 122.7219 | 122.5983 | 122.6028 | 122.5525 | -122.7631 | -122.6898 | 122.7219 | 122.7631 | 63.446 | 64.3753
1428.8906 | 122.9919 | -63.6246 | 59.024 | -0.19775 | 0.067776 | 0.12474 | 0.070863 | 0.0015381 | -0.0020594 | -0.0026853 | -0.14371 | 0.16331 | 0.12687 | -0.0010168 | 0.055397 | 0.10564 | -0.0016493 | -0.31128 | 59.0103 | -63.8031 | 58.9645 | 59.0652 | -63.8672 | 59.1888 | 0.46234 | 58.9737 | -63.6749 | 59.1843 | 59.1705 | 58.9966 | 0.26093 | -0.17853 | -0.013733 | -0.059509 | 122.6898 | 122.8134 | -0.24261 | 122.9919 | -0.064086 | -0.050354 | -0.050354 | 0.16022 | 122.7951 | 63.8855 | 122.6212 | 63.9359 | 122.6715 | 122.8683 | 122.7676 | 122.8455 | 122.8592 | 122.8134 | 122.6486 | 122.6349 | 122.5983 | -122.8271 | -122.699 | 122.5891 | 122.8088 | 63.3133 | 64.0869
1429.8281 | 123.143 | -63.588 | 59.0515 | -0.12146 | 0.067563 | 0.12559 | 0.068941 | -0.0046569 | 0.00071784 | -0.0016171 | -0.06131 | 0.16309 | 0.12709 | -0.0018712 | 0.056251 | 0.10393 | 0.0024097 | -0.20599 | 59.0012 | -63.7207 | 59.0744 | 59.2392 | -63.6795 | 59.2438 | 0.73242 | 58.992 | -63.6017 | 59.3948 | 59.2712 | 59.0927 | 0.43488 | -0.13275 | -0.050354 | 0.022888 | 122.8271 | 122.8317 | -0.091552 | 122.9645 | 0.041199 | -0.013733 | -0.05951 | 0.34332 | 122.8592 | 64.0228 | 122.6807 | 64.0366 | 122.6944 | 122.9599 | 122.7951 | 122.8729 | 122.9965 | 122.7219 | 122.5937 | 122.5891 | 122.58 | -122.7722 | -122.6532 | 122.6624 | 122.9828 | 63.382 | 64.3204
1430.8906 | 122.9645 | -63.6383 | 59.0378 | -0.19775 | 0.067776 | 0.1288 | 0.070222 | 0.0021789 | -0.00013676 | -0.0024717 | -0.091827 | 0.16096 | 0.12687 | 0.00090575 | 0.05561 | 0.10628 | -0.0039991 | -0.21973 | 58.9508 | -63.7619 | 59.0927 | 59.1705 | -63.8123 | 59.1797 | 0.52185 | 58.9508 | -63.62 | 59.2941 | 59.2026 | 59.0561 | 0.23804 | -0.1236 | -0.086975 | 0.054931 | 122.8088 | 122.818 | -0.17395 | 122.9416 | -0.050354 | 0.018311 | -0.086975 | 0.25635 | 122.8409 | 63.8763 | 122.6944 | 63.858 | 122.6761 | 122.9324 | 122.8546 | 122.8226 | 122.9141 | 122.7127 | 122.5708 | 122.5891 | 122.5891 | -122.7997 | -122.6578 | 122.731 | 122.9324 | 63.4186 | 64.1602
1431.8281 | 123.0835 | -63.5788 | 59.0607 | -0.14435 | 0.066708 | 0.12623 | 0.068941 | -0.0033753 | -0.0012048 | -0.00054907 | -0.058258 | 0.16224 | 0.12709 | -0.0052892 | 0.058387 | 0.10521 | -0.0022901 | -0.10529 | 58.992 | -63.7115 | 59.2072 | 59.2438 | -63.7207 | 59.3308 | 0.60883 | 59.0012 | -63.6154 | 59.4772 | 59.2941 | 59.1293 | 0.32044 | -0.13275 | -0.068665 | 0.14648 | 122.8226 | 122.9095 | -0.14191 | 123.0423 | -0.009155 | -0.036621 | -0.059509 | 0.41657 | 122.8729 | 63.8992 | 122.7081 | 63.9359 | 122.7448 | 122.9553 | 122.9187 | 122.9095 | 123.0927 | 122.7036 | 122.6166 | 122.5708 | 122.58 | -122.7722 | -122.6761 | 122.7859 | 123.056 | 63.4735 | 64.1876
1432.8906 | 123.0286 | -63.6337 | 59.0286 | -0.15961 | 0.066708 | 0.12495 | 0.068941 | -0.00038451 | -0.0024866 | -0.0018307 | -0.15286 | 0.16202 | 0.12794 | -0.0012304 | 0.057747 | 0.105 | -0.0029309 | -0.25177 | 58.9783 | -63.7848 | 59.0515 | 59.111 | -63.8489 | 59.2026 | 0.4303 | 58.9508 | -63.6383 | 59.2575 | 59.2117 | 59.0286 | 0.20142 | -0.15106 | -0.050354 | 0.022889 | 122.7448 | 122.8363 | -0.21515 | 122.9874 | -0.064087 | -0.004578 | -0.077819 | 0.22888 | 122.8455 | 63.8351 | 122.6624 | 63.8397 | 122.6669 | 122.8958 | 122.8363 | 122.85 | 122.8958 | 122.7631 | 122.5891 | 122.612 | 122.5845 | -122.8134 | -122.6669 | 122.6852 | 122.8912 | 63.382 | 64.064
1433.8281 | 122.9553 | -63.6154 | 59.0515 | -0.17487 | 0.068203 | 0.12773 | 0.067659 | 0.00068369 | -0.0027002 | -0.0024717 | -0.073517 | 0.16395 | 0.12773 | -0.0035802 | 0.059028 | 0.10308 | 0.0015551 | -0.3067 | 58.9828 | -63.7482 | 58.992 | 59.111 | -63.8397 | 59.1751 | 0.40283 | 58.9691 | -63.6475 | 59.1293 | 59.1934 | 59.0103 | 0.1831 | -0.13275 | -0.068665 | -0.05951 | 122.7264 | 122.7905 | -0.22431 | 122.9233 | -0.091553 | -0.032044 | -0.082398 | 0.077819 | 122.8088 | 63.7985 | 122.6257 | 63.8306 | 122.6578 | 122.8592 | 122.7402 | 122.8409 | 122.7768 | 122.731 | 122.6166 | 122.5983 | 122.5845 | -122.7997 | -122.699 | 122.6074 | 122.7448 | 63.3087 | 64.0182
1434.8906 | 123.1155 | -63.5925 | 59.0149 | -0.15198 | 0.06799 | 0.12645 | 0.068513 | 0.0023925 | 0.00071784 | 0.00073273 | -0.14981 | 0.16288 | 0.1288 | -0.0063574 | 0.05561 | 0.10585 | -0.0035719 | -0.27924 | 58.96 | -63.7711 | 59.0332 | 59.1705 | -63.7848 | 59.1888 | 0.42572 | 58.9462 | -63.6475 | 59.1888 | 59.2163 | 59.0424 | 0.19226 | -0.17853 | -0.054932 | 0.01831 | 122.7631 | 122.7814 | -0.19226 | 122.9599 | -0.013733 | -0.054932 | -0.068665 | 0.17395 | 122.8088 | 63.7848 | 122.6349 | 63.8397 | 122.6898 | 122.9416 | 122.8043 | 122.8638 | 122.8363 | 122.731 | 122.5937 | 122.5525 | 122.5388 | -122.7859 | -122.6624 | 122.6257 | 122.7814 | 63.3133 | 64.0182
1435.8281 | 123.0515 | -64.476 | 57.7515 | -0.81574 | 0.060086 | 0.12303 | 2.1071 | 0.0028199 | 0.66615 | -0.0014035 | -0.018585 | 0.16437 | 0.12751 | -0.0087072 | 0.057106 | 0.10286 | 0.0030505 | 0.56763 | 57.9575 | -64.5035 | 58.0444 | 58.0994 | 57.6965 | 58.2092 | 0.58594 | 57.2021 | -63.8489 | 58.2504 | 58.168 | 57.9666 | 0.3067 | -0.027466 | 0.20599 | 0.29297 | 122.5754 | 122.6852 | 122.1725 | 122.7127 | 122.2 | 0.62714 | -0.54932 | 0.49896 | 122.644 | 64.7827 | 122.4426 | 64.1556 | 121.8155 | 122.6028 | 122.5479 | 122.0169 | 122.0993 | 122.4609 | 121.051 | 122.4335 | 121.6782 | -122.2549 | -121.6003 | 122.5204 | 122.7264 | 65.0436 | 65.0619
1436.8906 | 122.8729 | -64.1464 | 57.8934 | -0.44189 | 0.033383 | 0.10572 | 1.7252 | 0.035504 | 0.35384 | 0.043885 | -0.32681 | 0.025947 | 0.014934 | 0.038076 | 0.24744 | 0.010792 | 0.031249 | 0.29755 | 44.6228 | -63.8947 | 45.1584 | 55.5313 | 45.1355 | 57.6553 | 0.14191 | 42.7368 | -48.7701 | 58.4244 | 44.3527 | 42.0959 | 0.091553 | 0.25177 | -13.2706 | -12.735 | 119.6777 | 121.8018 | 109.2819 | 121.55 | 109.0302 | 15.3763 | -15.1566 | 0.53101 | 108.4991 | 64.238 | 106.2424 | 48.8617 | 90.8661 | 119.426 | 109.053 | 93.1229 | 107.1945 | 108.5175 | 91.507 | 108.7692 | 106.8832 | -121.788 | -106.6635 | 109.3048 | 122.5708 | 64.444 | 64.2883
1437.8281 | 122.9187 | -64.2838 | 58.2916 | -0.82336 | 0.061795 | 0.11726 | 2.1041 | -0.0016663 | 0.68816 | 0.0013735 | -0.036896 | 0.16309 | 0.12367 | -0.0059302 | 0.05796 | 0.10222 | 0.00070073 | 0.38452 | 58.1497 | -64.3662 | 44.4626 | 58.2962 | 44.426 | 58.2962 | 0.4303 | 57.8384 | -63.7573 | 58.3282 | 58.4244 | 58.2504 | 0.19226 | -0.082398 | -0.14191 | -13.829 | 122.58 | 122.58 | 108.7097 | 122.6624 | 108.7921 | 0.52643 | -0.45319 | 0.036621 | 122.7081 | 64.476 | 122.5342 | 63.9496 | 122.0078 | 122.6624 | 108.8287 | 122.1817 | 122.0856 | 122.5159 | 121.5958 | 122.4335 | 122.1222 | -122.6578 | -122.0489 | 108.7463 | 122.612 | 64.6683 | 64.7141
1438.8906 | 122.7402 | -64.2975 | 58.1772 | -0.43427 | 0.032742 | 0.11149 | 1.8407 | 0.03529 | 0.6967 | 0.043885 | -0.32376 | 0.025733 | 0.12986 | 0.038717 | 0.24979 | 0.011219 | -0.018953 | 0.40741 | 55.3482 | -63.8535 | 43.3594 | 57.9483 | 40.5075 | 57.6828 | 0.27466 | 58.136 | -57.0099 | 57.9895 | 58.374 | 48.6923 | 0.073242 | 0.44403 | -2.829 | -14.8178 | 122.2458 | 121.9803 | 104.805 | 121.5363 | 104.361 | 7.2876 | -0.041199 | -0.18768 | 122.6715 | 64.3707 | 112.9898 | 57.0831 | 105.7022 | 121.8018 | 107.2128 | 115.3839 | 114.9994 | 119.2017 | 115.1459 | 119.6457 | 122.4335 | -122.0306 | -115.1871 | 107.6569 | 122.287 | 64.7049 | 64.5721
1439.8281 | 122.7722 | -64.2792 | 58.2779 | -0.83862 | 0.061795 | 0.11555 | 2.0855 | 0.0032471 | 0.67427 | -0.0028989 | -0.049103 | 0.16309 | 0.12687 | -0.0029394 | 0.059028 | 0.105 | 0.00027333 | 0.71411 | 58.1223 | -64.183 | 42.3065 | 58.3511 | 42.1463 | 58.3374 | 0.43488 | 57.8979 | -63.707 | 58.3649 | 58.4198 | 58.2321 | 0.14191 | 0.096131 | -0.15564 | -15.9714 | 122.6303 | 122.6166 | 106.4255 | 122.5204 | 106.3293 | 0.5722 | -0.37994 | 0.086975 | 122.699 | 64.4211 | 122.5113 | 63.8489 | 121.9391 | 122.5342 | 106.4896 | 122.1268 | 122.0718 | 122.3053 | 121.6049 | 122.4014 | 122.1771 | -122.4609 | -121.9849 | 106.5857 | 122.644 | 64.9933 | 64.7141
1440.8281 | 122.8409 | -64.2334 | 58.3282 | -0.91492 | 0.060727 | 0.11299 | 2.0791 | -0.0018799 | 0.66765 | 0.0020145 | -0.07962 | 0.16352 | 0.1288 | -0.0044348 | 0.058387 | 0.10543 | -0.0054945 | -0.73242 | 58.2092 | -64.1647 | 38.6307 | 58.1726 | 42.691 | 58.0673 | 0.39825 | 58.0215 | -63.8855 | 58.4198 | 58.4518 | 58.1451 | 0.16937 | 0.068664 | -0.11902 | -19.6976 | 122.406 | 122.3007 | 106.9244 | 122.2321 | 106.8558 | 0.3479 | -0.3067 | 0.091553 | 122.6852 | 64.4028 | 122.3785 | 64.0549 | 122.0306 | 122.3373 | 102.7954 | 122.3373 | 122.3053 | 122.374 | 121.907 | 122.4426 | 122.2549 | -122.493 | -122.2137 | 102.8641 | 122.6532 | 63.501 | 64.6317
1441.8281 | 122.8821 | -64.2563 | 57.8064 | -0.80048 | 0.060299 | 0.11641 | 3.4369 | -0.0018799 | 0.6779 | 9.193e-05 | -0.049103 | 0.16373 | 0.1273 | -0.0063574 | 0.059028 | 0.10372 | 0.0019823 | 0.46234 | 58.1406 | -64.2059 | 43.9545 | 58.0261 | 44.2612 | 58.2962 | 0.37994 | 57.4173 | -63.5651 | 58.3008 | 58.287 | 58.1039 | 0.15106 | 0.050354 | 0.33417 | -13.8519 | 122.2824 | 122.5525 | 108.5175 | 122.5021 | 108.4671 | 0.69122 | -0.3891 | 0.49439 | 122.5433 | 64.4073 | 122.3602 | 63.7161 | 121.669 | 122.2321 | 108.1604 | 121.8521 | 121.8658 | 122.3465 | 120.9824 | 122.3969 | 121.6736 | -122.0123 | -121.3715 | 108.2108 | 122.5571 | 64.7186 | 64.6362
1442.8906 | 122.5159 | -63.6932 | 58.2596 | -0.44189 | 0.032956 | 0.1053 | 2.7271 | 0.03529 | 0.45125 | 0.043671 | -0.32681 | 0.025733 | 0.12132 | 0.040853 | 0.2468 | 0.011006 | 0.031035 | 0.1236 | 40.21 | -64.7278 | 36.2595 | 39.4547 | 26.1108 | 58.4793 | 0.16479 | 43.1442 | -49.4156 | 54.2084 | 44.0323 | 42.2791 | 0.082397 | -1.0345 | -18.0496 | -22.0001 | 103.1479 | 122.1725 | 89.8041 | 123.2071 | 90.8386 | 14.2776 | -15.1154 | -4.0512 | 107.7255 | 63.7756 | 105.9723 | 49.498 | 91.6946 | 104.1824 | 100.9872 | 93.4479 | 103.624 | 104.9377 | 92.5598 | 103.9032 | 106.8375 | -122.9874 | -107.6752 | 99.9527 | 117.9016 | 63.8168 | 63.858
1443.8281 | 122.7997 | -64.2792 | 58.1497 | -0.82336 | 0.054532 | 0.11534 | 3.4077 | 0.00025629 | 0.67363 | 0.00094633 | -0.046051 | 0.1663 | 0.1305 | -0.0033666 | 0.05796 | 0.10457 | 0.00048713 | 0.27466 | 58.1543 | -64.0228 | 44.5908 | 58.1589 | 42.9474 | 58.3145 | 0.38452 | 57.7881 | -63.6841 | 58.3511 | 58.4015 | 58.2184 | 0.23804 | 0.25635 | 0.004578 | -13.559 | 122.4381 | 122.5937 | 107.2266 | 122.3373 | 106.9702 | 0.59509 | -0.36163 | 0.20142 | 122.6807 | 64.5172 | 122.4976 | 63.9221 | 121.9025 | 122.1817 | 108.6136 | 122.0856 | 122.0352 | 122.1771 | 121.4722 | 122.4335 | 122.0673 | -122.1725 | -121.8338 | 108.8699 | 122.6303 | 64.5538 | 64.6637
1444.8906 | 121.8567 | -63.9084 | 58.0124 | -1.3116 | 0.047268 | 0.11299 | 3.3726 | -0.0044433 | 0.66209 | -0.0067441 | -0.19559 | 0.16074 | 0.1273 | -0.0040076 | 0.059242 | 0.10415 | 5.9726e-05 | 0.71869 | 57.431 | -63.5834 | 43.9178 | 57.8201 | 42.7597 | 57.5592 | 0.37079 | 57.4493 | -63.945 | 58.255 | 57.7652 | 57.4356 | -0.07782 | 0.32501 | -0.58136 | -14.0945 | 121.7285 | 121.4676 | 106.6681 | 121.1426 | 106.3431 | -0.036621 | -0.56305 | 0.24261 | 121.6736 | 63.8306 | 121.344 | 63.8672 | 121.3806 | 121.4035 | 107.5012 | 121.7102 | 122.2 | 121.0144 | 121.3943 | 121.3394 | 121.3577 | -121.5958 | -121.9574 | 107.8262 | 122.1634 | 64.6271 | 64.2792
1445.8281 | 122.8226 | -64.0274 | 58.1406 | -0.94543 | 0.057309 | 0.10893 | 3.3938 | -0.0044433 | 0.65376 | 0.0011599 | -0.064362 | 0.16416 | 0.13008 | -0.0069982 | 0.058174 | 0.10201 | -0.0010083 | 0.34332 | 58.3054 | -63.7756 | 32.872 | 58.1406 | 33.4076 | 58.2962 | 0.41199 | 57.5638 | -63.3774 | 58.493 | 58.4656 | 58.3008 | 0.16479 | 0.25177 | 0.1648 | -25.2686 | 122.168 | 122.3236 | 97.435 | 122.0718 | 97.1832 | 0.65002 | -0.57678 | 0.35248 | 122.493 | 64.1922 | 122.3282 | 63.5422 | 121.6782 | 121.9162 | 96.6476 | 121.843 | 121.8704 | 122.081 | 120.9412 | 122.3328 | 121.5912 | -121.9162 | -121.5179 | 96.8994 | 122.5204 | 64.3707 | 64.4394
1446.8906 | 122.7859 | -63.7344 | 54.4785 | -0.42664 | 0.032528 | 0.10572 | 2.9507 | 0.035077 | 0.22054 | 0.043457 | -0.33292 | 0.025733 | 0.016857 | 0.03829 | 0.24766 | 0.011006 | 0.031249 | 0.24719 | 41.716 | -63.8168 | 32.0709 | 42.2562 | 32.4463 | 58.3969 | 0.13275 | 35.9573 | -43.2266 | 46.3852 | 38.8779 | 37.2162 | 0.082397 | -0.082397 | -12.7625 | -22.4075 | 105.9906 | 122.1313 | 96.1807 | 122.2137 | 96.2631 | 20.5078 | -18.5211 | -8.0933 | 102.6123 | 63.8168 | 100.9506 | 43.309 | 80.4428 | 106.073 | 95.8878 | 82.1045 | 89.6118 | 105.5328 | 79.184 | 105.4504 | 99.6918 | -118.2953 | -97.7051 | 95.8054 | 110.1196 | 63.9816 | 63.8672
1447.8281 | 122.8226 | -64.2426 | 58.0902 | -0.99884 | 0.05325 | 0.11427 | 3.3837 | 0.0011109 | 0.66936 | -0.00076267 | -0.073517 | 0.16459 | 0.1288 | -0.00058965 | 0.058815 | 0.10628 | 0.00070073 | -0.3479 | 57.6187 | -63.7253 | 44.0277 | 57.4402 | 43.9636 | 57.5455 | 0.32501 | 57.5912 | -63.9679 | 58.1726 | 57.7972 | 57.5272 | -0.064087 | 0.51727 | -0.4715 | -14.0625 | 121.6827 | 121.788 | 108.2062 | 121.2708 | 107.6889 | 0.27466 | -0.49896 | 0.082397 | 122.0398 | 64.1785 | 121.7697 | 63.9038 | 121.4951 | 121.1655 | 107.753 | 121.7651 | 122.1405 | 121.344 | 121.5591 | 121.8613 | 121.8338 | -121.8155 | -122.0581 | 108.2703 | 122.4152 | 63.8947 | 64.5676
1448.8906 | 122.3648 | -64.064 | 57.6599 | -0.44952 | 0.032315 | 0.1053 | 2.7531 | 0.038068 | 0.57643 | 0.043885 | -0.32681 | 0.025733 | 0.10167 | 0.037863 | 0.24723 | 0.010792 | 0.031035 | 0.43488 | 38.6398 | -64.4531 | 35.5133 | 43.9865 | 35.5316 | 54.744 | 0.14191 | 48.381 | -50.9399 | 57.8934 | 51.5442 | 44.7052 | 0.09613 | -0.3891 | -19.0201 | -22.1466 | 108.0505 | 118.808 | 99.5956 | 119.1971 | 99.9847 | 13.1241 | -9.2789 | 0.23346 | 115.6082 | 64.1602 | 108.7692 | 51.0361 | 95.6451 | 108.4396 | 99.9664 | 102.4841 | 108.8333 | 103.093 | 99.321 | 102.7039 | 112.4451 | -122.113 | -108.5999 | 99.5773 | 121.9574 | 64.4989 | 64.2059
1449.8281 | 122.8455 | -64.2197 | 58.0261 | -0.8844 | 0.05795 | 0.11705 | 3.649 | -0.0029479 | 0.67448 | -0.00076267 | -0.055206 | 0.16544 | 0.12815 | -0.0089208 | 0.057319 | 0.10564 | -0.0014355 | 0.53101 | 58.0994 | -64.2014 | 45.5475 | 58.2184 | 45.1126 | 58.223 | 0.37079 | 57.6141 | -63.6108 | 58.2733 | 58.342 | 58.1818 | 0.16479 | 0.018311 | 0.073242 | -12.4786 | 122.4381 | 122.4426 | 109.3323 | 122.4243 | 109.314 | 0.60883 | -0.41199 | 0.24719 | 122.5616 | 64.3845 | 122.4014 | 63.7756 | 121.7926 | 122.4197 | 109.7488 | 121.9528 | 121.8842 | 122.3007 | 121.225 | 122.319 | 121.8338 | -122.2275 | -121.637 | 109.7672 | 122.493 | 64.7507 | 64.5905
1450.8906 | 122.7951 | -63.9175 | 58.0078 | -0.43427 | 0.043423 | 0.10337 | 3.5484 | -0.0052979 | 0.56831 | -0.010162 | -0.30545 | 0.14835 | 0.11149 | -0.0033666 | 0.045784 | 0.093037 | -0.012971 | 0.737 | 58.5434 | -63.9633 | 32.634 | 52.565 | 32.3181 | 57.811 | 0.29755 | 44.0735 | -51.7502 | 44.6045 | 43.9133 | 43.6157 | 0.086975 | -0.045776 | 0.53558 | -25.3738 | 116.4825 | 121.7285 | 96.2357 | 121.7743 | 96.2814 | 12.1674 | -13.9343 | -13.4033 | 107.8308 | 64.0045 | 107.5333 | 51.8372 | 95.3659 | 116.5283 | 96.5973 | 95.6635 | 96.3547 | 122.5067 | 95.8237 | 122.4609 | 107.991 | -121.9711 | -109.758 | 96.5515 | 108.522 | 64.6545 | 64.2151
1451.8438 | 122.9279 | -64.3845 | 57.8293 | -0.83862 | 0.057736 | 0.12281 | 3.6911 | 4.2692e-05 | 0.69478 | -0.0016171 | -0.036896 | 0.16224 | 0.12794 | -0.004862 | 0.05796 | 0.10393 | -0.0027173 | 0.63629 | 57.9117 | -64.4852 | 58.0124 | 58.0856 | 57.7057 | 58.1039 | 0.55847 | 57.4127 | -63.6795 | 58.1543 | 58.049 | 57.8293 | 0.2655 | -0.10071 | 0.082397 | 0.18311 | 122.4701 | 122.4884 | 122.0901 | 122.5891 | 122.1909 | 0.70496 | -0.41656 | 0.32501 | 122.4335 | 64.65 | 122.2137 | 63.945 | 121.5088 | 122.5708 | 122.4976 | 121.7285 | 121.8338 | 122.3969 | 121.0922 | 122.2961 | 121.7972 | -122.3145 | -121.5088 | 122.3969 | 122.5388 | 65.0208 | 64.9429
1452.8281 | 122.7722 | -64.2654 | 58.1955 | -1.0141 | 0.042355 | 0.10957 | 3.6324 | 0.0015381 | 0.66017 | -0.0024717 | -0.19864 | 0.15967 | 0.12538 | -0.0029394 | 0.059028 | 0.10457 | 5.9726e-05 | 0.37079 | 57.3395 | -63.945 | 45.2362 | 57.3669 | 45.0256 | 57.5684 | 0.29297 | 57.486 | -64.0549 | 57.7972 | 57.5684 | 57.6004 | -0.25635 | 0.32043 | -0.85602 | -12.9593 | 121.6324 | 121.8338 | 109.2911 | 121.5134 | 108.9706 | 0.21057 | -0.70953 | -0.39825 | 121.8338 | 64.0091 | 121.8658 | 63.7985 | 121.6553 | 121.3119 | 109.1812 | 121.6232 | 121.8521 | 121.2845 | 121.5408 | 121.6049 | 121.7514 | -122.1405 | -122.2504 | 109.5016 | 122.0627 | 64.6362 | 64.5584
1453.8906 | 122.8088 | -64.4348 | 57.6691 | -1.2201 | 0.044705 | 0.11213 | 3.689 | -0.0057251 | 0.72789 | -0.0073849 | -0.32681 | 0.14664 | 0.11235 | -0.011698 | 0.037239 | 0.088124 | -0.013826 | 0.46234 | 57.3441 | -64.0045 | 57.3441 | 57.5592 | 57.8842 | 57.2205 | 0.33417 | 57.7652 | -64.2609 | 57.4631 | 55.0232 | 47.0261 | 0.091553 | 0.4303 | -0.32501 | -0.32501 | 121.994 | 121.6553 | 122.319 | 121.225 | 121.8887 | 0.17395 | 0.096131 | -0.20599 | 119.458 | 64.5264 | 111.4609 | 64.3524 | 111.2869 | 121.5637 | 121.3486 | 119.2841 | 121.7239 | 121.3486 | 122.0261 | 121.7789 | 122.2 | -121.6736 | -121.9299 | 121.7789 | 121.8979 | 64.8972 | 64.769
1454.8281 | 122.7219 | -64.4989 | 58.049 | -0.45715 | 0.032956 | 0.1226 | 3.7247 | -0.0029479 | 0.74349 | -0.012298 | -0.31155 | 0.15925 | 0.11705 | -0.011698 | 0.039589 | 0.091542 | -0.016603 | 0.32959 | 53.9612 | -63.9908 | 57.9666 | 57.9117 | 57.7972 | 57.28 | 0.14648 | 57.6782 | -64.6225 | 57.5455 | 57.6324 | 55.4901 | 0.036621 | 0.50812 | -4.0878 | -0.082397 | 122.4106 | 121.7789 | 122.2961 | 121.2708 | 121.788 | -0.1236 | -0.37079 | -0.50354 | 122.1313 | 64.5355 | 119.989 | 64.6591 | 120.1126 | 121.9025 | 121.9574 | 122.2549 | 122.168 | 117.952 | 122.3007 | 118.4601 | 122.1771 | -122.0398 | -122.6715 | 122.4655 | 122.0444 | 64.8285 | 64.6454
1455.8906 | 122.406 | -64.4897 | 57.9712 | -1.3651 | 0.048977 | 0.10765 | 3.7025 | -0.012134 | 0.71828 | -0.020843 | -0.32681 | 0.16309 | 0.11448 | -0.013193 | 0.041298 | 0.030446 | 0.033385 | 0.37537 | 57.4539 | -63.7436 | 58.1772 | 58.1497 | 57.9437 | 57.518 | 0.30212 | 57.9758 | -62.7182 | 57.4951 | 58.2047 | 50.0519 | 0.11444 | 0.74615 | -0.51727 | 0.20599 | 122.6395 | 122.0078 | 122.4335 | 121.2616 | 121.6873 | 1.7715 | 0.004578 | -0.47607 | 122.6944 | 64.6042 | 114.5416 | 62.8326 | 112.7701 | 121.8933 | 121.9208 | 120.9229 | 120.2133 | 121.1975 | 120.694 | 121.9437 | 122.4655 | -121.7148 | -120.6894 | 122.6669 | 121.9849 | 64.8651 | 64.7919
1456.8281 | 122.8134 | -64.4669 | 58.0078 | -0.87677 | 0.059872 | 0.12367 | 3.7125 | 0.0043151 | 0.73686 | 0.0015871 | -0.015534 | 0.16395 | 0.12965 | -0.0046484 | 0.058387 | 0.105 | 0.0024097 | 0.48065 | 57.8888 | -64.4165 | 57.9025 | 58.0353 | 57.7423 | 58.0215 | 0.39368 | 57.8293 | -64.1556 | 58.049 | 58.1451 | 57.9666 | 0.17853 | 0.050354 | -0.11902 | -0.10529 | 122.5021 | 122.4884 | 122.2092 | 122.438 | 122.1588 | 0.31128 | -0.17853 | 0.041199 | 122.612 | 64.6454 | 122.4335 | 64.3341 | 122.1222 | 122.4518 | 122.319 | 122.3007 | 122.2046 | 122.3053 | 121.9849 | 122.3557 | 122.2961 | -122.4243 | -122.1634 | 122.3694 | 122.5159 | 64.9475 | 64.8605
1457.8906 | 121.9666 | -64.3799 | 58.0536 | -0.45715 | 0.032315 | 0.1179 | 3.0851 | 0.034863 | 0.75502 | 0.044098 | -0.32376 | 0.025519 | 0.12666 | -0.01298 | 0.044502 | 0.011006 | -0.015107 | 0.42114 | 52.2995 | -63.9771 | 57.4036 | 57.8705 | 57.8156 | 57.8796 | 0.27466 | 57.3074 | -64.0915 | 57.5409 | 57.3166 | 57.8842 | -0.1236 | 0.40283 | -5.7541 | -0.65002 | 122.2504 | 122.2595 | 122.1954 | 121.8567 | 121.7926 | 0.28839 | -0.74616 | -0.5127 | 121.6965 | 64.2563 | 122.2641 | 63.9679 | 121.9757 | 121.8475 | 121.3806 | 121.4081 | 121.6324 | 116.2766 | 121.3989 | 116.6794 | 121.6873 | -122.0306 | -122.1451 | 121.7834 | 121.9208 | 64.801 | 64.6545
1458.8281 | 122.2961 | -64.4806 | 58.0032 | -1.1514 | 0.054318 | 0.12068 | 3.6815 | 0.00068369 | 0.7249 | -0.0018307 | -0.14066 | 0.16288 | 0.12815 | -0.0035802 | 0.057747 | 0.10671 | 0.0011279 | 0.42114 | 57.193 | -63.8855 | 57.3624 | 57.3715 | 57.0419 | 57.3074 | 0.32044 | 57.4997 | -63.9816 | 57.9987 | 57.8384 | 57.4219 | 0.004578 | 0.59509 | -0.81024 | -0.64087 | 121.8521 | 121.788 | 121.5225 | 121.1929 | 120.9274 | 0.49896 | -0.50354 | -0.004578 | 122.319 | 64.4852 | 121.9025 | 63.9862 | 121.4035 | 121.257 | 121.2479 | 121.8201 | 121.9803 | 121.0785 | 121.4813 | 121.6736 | 121.9803 | -121.8887 | -121.9849 | 121.843 | 122.4792 | 64.9017 | 64.801
1459.8906 | 122.2778 | -64.4531 | 57.9025 | -0.85388 | 0.059445 | 0.12474 | 3.6999 | 0.0028199 | 0.73174 | -0.0016171 | -0.042999 | 0.1648 | 0.12815 | -0.003794 | 0.059242 | 0.10521 | 0.0028369 | 0.57678 | 57.9346 | -64.0594 | 57.962 | 57.9071 | 57.5912 | 57.7835 | 0.49896 | 57.6599 | -63.9084 | 58.049 | 58.1314 | 57.724 | 0.23346 | 0.39368 | 0.032043 | 0.059509 | 122.3602 | 122.2366 | 122.0444 | 121.843 | 121.6507 | 0.54474 | -0.24262 | 0.14648 | 122.5845 | 64.6866 | 122.1771 | 64.1418 | 121.6324 | 121.9666 | 122.0215 | 122.0398 | 121.9574 | 121.994 | 121.5683 | 122.3877 | 122.113 | -121.962 | -121.8109 | 122.4152 | 122.5021 | 65.0299 | 64.9521
1460.8281 | 122.7676 | -64.1327 | 58.0444 | -0.44952 | 0.032315 | 0.14183 | 3.2656 | 0.034863 | 0.7516 | 0.046448 | -0.17728 | 0.023597 | 0.12944 | -0.01597 | 0.037666 | 0.09731 | -0.016603 | 0.43945 | 57.9712 | -64.064 | 57.2617 | 57.2433 | 57.1838 | 57.4356 | 0.28839 | 57.5455 | -63.8947 | 57.486 | 57.5043 | 57.0648 | -0.11902 | 0.068664 | -0.073243 | -0.78278 | 121.376 | 121.5683 | 121.3165 | 121.4996 | 121.2479 | 0.23804 | -0.49896 | -0.55847 | 121.637 | 64.0137 | 121.1975 | 63.7756 | 120.9595 | 121.3074 | 121.3257 | 121.3989 | 121.3806 | 122.0352 | 121.4401 | 122.1039 | 121.6782 | -122.1085 | -121.9391 | 121.3943 | 121.6187 | 64.5721 | 64.4211
1461.8438 | 122.2412 | -64.4714 | 57.9987 | -0.84625 | 0.059231 | 0.12474 | 3.6975 | 0.0011109 | 0.72597 | -0.0043943 | -0.039948 | 0.16502 | 0.12687 | -0.0067846 | 0.057747 | 0.10393 | 0.00027333 | 0.58136 | 57.9025 | -64.1098 | 57.9666 | 57.9758 | 57.637 | 57.811 | 0.5127 | 57.7881 | -64.0457 | 58.0353 | 58.1543 | 57.8384 | 0.2655 | 0.36163 | -0.09613 | -0.032043 | 122.4472 | 122.2824 | 122.1085 | 121.9208 | 121.7468 | 0.42572 | -0.21057 | 0.036621 | 122.6257 | 64.7369 | 122.3099 | 64.3112 | 121.8842 | 122.0856 | 122.0764 | 122.2 | 122.081 | 122.0123 | 121.8338 | 122.374 | 122.2595 | -122.1085 | -122.0444 | 122.4381 | 122.5067 | 65.0528 | 64.9841
1462.8906 | 121.9254 | -64.2654 | 58.0032 | -0.96832 | 0.046414 | 0.11299 | 3.6593 | -0.0085021 | 0.70931 | -0.0050351 | -0.082672 | 0.15583 | 0.12495 | 0.0024012 | 0.058601 | 0.1035 | -0.00058107 | 0.44403 | 57.4631 | -64.1098 | 57.4265 | 57.5546 | 56.7444 | 57.1976 | 0.1831 | 57.7148 | -64.151 | 57.7881 | 57.8018 | 57.4539 | 0.064087 | 0.15564 | -0.54016 | -0.57678 | 121.8201 | 121.463 | 121.0098 | 121.3074 | 120.8542 | 0.11444 | -0.28839 | -0.21515 | 122.0673 | 64.3295 | 121.7194 | 64.2151 | 121.6049 | 121.6644 | 121.5363 | 121.9528 | 121.9391 | 121.5729 | 121.8658 | 121.7285 | 121.9803 | -122.113 | -122.1542 | 121.6919 | 122.0535 | 64.7095 | 64.4485
1463.8281 | 122.612 | -64.4531 | 57.9529 | -0.89966 | 0.05859 | 0.12516 | 3.6886 | 0.00089729 | 0.72298 | 0.0024417 | -0.076569 | 0.1648 | 0.1273 | -0.0057166 | 0.056465 | 0.10585 | -0.0020765 | 0.50354 | 57.8613 | -64.2563 | 57.9391 | 58.0444 | 57.756 | 57.8934 | 0.28839 | 57.8339 | -64.3524 | 58.0902 | 58.2047 | 57.9803 | 0.16937 | 0.19684 | -0.091553 | -0.013733 | 122.4976 | 122.3465 | 122.2092 | 122.1497 | 122.0123 | 0.10071 | -0.11902 | 0.13733 | 122.6578 | 64.6225 | 122.4335 | 64.5218 | 122.3328 | 122.3007 | 122.1954 | 122.5571 | 122.4426 | 122.1176 | 122.1863 | 122.3145 | 122.287 | -122.2092 | -122.3053 | 122.3923 | 122.5433 | 64.9567 | 64.7415
1464.8906 | 120.8633 | -64.0091 | 57.5821 | -0.93018 | 0.05325 | 0.11555 | 3.115 | -0.0065795 | 0.73537 | 0.043457 | -0.22 | 0.026374 | 0.1288 | -0.014902 | 0.034034 | 0.012074 | -0.015321 | 0.37994 | 54.538 | -64.0091 | 57.3578 | 57.3441 | 56.9366 | 57.2113 | 0.23346 | 57.4951 | -63.9771 | 57.4951 | 57.6279 | 57.2205 | -0.004578 | 0 | -3.0441 | -0.2243 | 121.3531 | 121.2204 | 120.9457 | 121.2204 | 120.9457 | 0.032043 | -0.086975 | -0.086975 | 121.637 | 64.0045 | 121.2296 | 63.9725 | 121.1975 | 121.3531 | 121.3669 | 121.6049 | 121.4722 | 118.5471 | 121.4722 | 118.5471 | 121.5042 | -121.5912 | -121.5591 | 121.3669 | 121.5042 | 64.389 | 64.2426
1465.8281 | 122.7081 | -64.4302 | 57.93 | -0.89203 | 0.060299 | 0.12303 | 3.683 | -0.0023071 | 0.71764 | 0.00094633 | -0.073517 | 0.16331 | 0.12837 | -0.0089208 | 0.058815 | 0.10521 | -0.0042127 | 0.49439 | 57.8796 | -64.3616 | 57.9391 | 58.0444 | 57.7652 | 58.0032 | 0.4303 | 57.9117 | -64.4028 | 58.0582 | 58.1268 | 57.9803 | 0.16479 | 0.068665 | -0.050354 | 0.009155 | 122.4747 | 122.4335 | 122.1954 | 122.3648 | 122.1268 | 0.027466 | -0.018311 | 0.12817 | 122.5571 | 64.595 | 122.4106 | 64.5676 | 122.3831 | 122.406 | 122.3007 | 122.5296 | 122.4609 | 122.2412 | 122.3145 | 122.3099 | 122.3419 | -122.2916 | -122.3328 | 122.3694 | 122.4884 | 64.9246 | 64.8605
1466.8906 | 122.4609 | -64.4485 | 57.843 | -0.90729 | 0.05859 | 0.12345 | 3.6813 | 0.0023925 | 0.71465 | -0.00097627 | -0.085724 | 0.16459 | 0.12666 | 0.0011194 | 0.059028 | 0.10564 | -0.0018629 | 0.48981 | 57.7103 | -64.3021 | 57.9346 | 58.0444 | 57.7423 | 57.8522 | 0.41657 | 57.8934 | -64.4348 | 58.0948 | 58.1772 | 57.9895 | 0.17853 | 0.14648 | -0.13275 | 0.091552 | 122.493 | 122.3007 | 122.1909 | 122.1542 | 122.0444 | 0.013733 | 0.050354 | 0.25177 | 122.6257 | 64.6271 | 122.438 | 64.6133 | 122.4243 | 122.3465 | 122.2366 | 122.612 | 122.5296 | 122.0123 | 122.3282 | 122.1588 | 122.3419 | -122.1451 | -122.2778 | 122.3831 | 122.5433 | 64.9384 | 64.8651
1467.8281 | 122.3969 | -64.4577 | 57.7103 | -0.86151 | 0.057736 | 0.12239 | 3.6796 | 0.00068369 | 0.71614 | -0.00076267 | -0.12845 | 0.16245 | 0.12687 | -0.0040076 | 0.057747 | 0.10543 | 0.00048713 | 0.47607 | 57.843 | -64.3707 | 57.93 | 58.0032 | 57.6782 | 57.8156 | 0.41657 | 57.9071 | -64.4485 | 58.0811 | 58.1497 | 57.9803 | 0.19226 | 0.086975 | 0.13275 | 0.21973 | 122.4609 | 122.2733 | 122.1359 | 122.1863 | 122.049 | 0.009156 | 0.19684 | 0.37079 | 122.6074 | 64.65 | 122.4381 | 64.6408 | 122.4289 | 122.374 | 122.3007 | 122.5983 | 122.5296 | 122.2137 | 122.3557 | 122.3007 | 122.3648 | -122.081 | -122.1588 | 122.3877 | 122.5388 | 64.9338 | 64.8743
1468.8906 | 121.8338 | -64.1739 | 57.4356 | -1.2964 | 0.052182 | 0.12004 | 3.6367 | 0.0047425 | 0.71272 | -0.00076267 | -0.25967 | 0.15925 | 0.1258 | -0.0046484 | 0.05796 | 0.10244 | -0.00015387 | 0.35248 | 57.193 | -64.1281 | 57.9529 | 57.7881 | 57.2845 | 57.5592 | 0.30212 | 57.7286 | -64.238 | 57.9758 | 58.0399 | 57.7469 | 0.10986 | 0.045776 | -0.24262 | 0.51727 | 121.962 | 121.7331 | 121.4584 | 121.6873 | 121.4127 | -0.064087 | 0.29297 | 0.54016 | 122.2137 | 64.2838 | 121.9208 | 64.3478 | 121.9849 | 121.9162 | 122.081 | 122.2778 | 122.2137 | 121.3211 | 121.9666 | 121.3669 | 121.9025 | -121.5637 | -121.6736 | 122.1268 | 122.1497 | 64.5264 | 64.476
1469.8281 | 122.6715 | -64.4623 | 57.7469 | -0.87677 | 0.059231 | 0.1241 | 3.6738 | -0.0033753 | 0.71123 | -0.0016171 | -0.064362 | 0.16309 | 0.12751 | -0.0069982 | 0.058387 | 0.10543 | -0.0042127 | 0.46692 | 57.8613 | -64.444 | 57.93 | 58.0399 | 57.756 | 58.0124 | 0.42114 | 57.9025 | -64.4623 | 58.049 | 58.136 | 57.9666 | 0.17395 | 0.01831 | 0.11444 | 0.18311 | 122.5021 | 122.4747 | 122.2183 | 122.4564 | 122.2 | 0 | 0.15564 | 0.30212 | 122.5983 | 64.6362 | 122.4289 | 64.6362 | 122.4289 | 122.4838 | 122.374 | 122.5983 | 122.5113 | 122.3053 | 122.3648 | 122.3236 | 122.3648 | -122.1909 | -122.2092 | 122.3923 | 122.5113 | 64.9292 | 64.8834
1470.8281 | 122.4243 | -64.4531 | 57.7927 | -0.86914 | 0.060727 | 0.12495 | 3.6715 | 0.0021789 | 0.7108 | -0.00033547 | -0.088776 | 0.16267 | 0.1305 | 5.1352e-05 | 0.057747 | 0.10415 | 0.0017687 | 0.46692 | 57.5958 | -64.325 | 57.9117 | 58.0307 | 57.6874 | 57.8796 | 0.41199 | 57.8888 | -64.4531 | 58.0811 | 58.1589 | 57.9712 | 0.20142 | 0.12817 | -0.19684 | 0.11902 | 122.4838 | 122.3328 | 122.1405 | 122.2046 | 122.0123 | 0 | 0.09613 | 0.28839 | 122.612 | 64.6545 | 122.4243 | 64.6545 | 122.4243 | 122.3557 | 122.2366 | 122.612 | 122.5342 | 121.9208 | 122.3419 | 122.0489 | 122.3419 | -122.1176 | -122.2458 | 122.3648 | 122.5342 | 64.92 | 64.8651
1471.9062 | 122.6212 | -64.4211 | 57.7332 | -0.79285 | 0.061581 | 0.12452 | 3.6713 | 0.00025629 | 0.70931 | 0.00073273 | -0.070465 | 0.16437 | 0.12773 | -0.00016245 | 0.058601 | 0.10265 | -0.00015387 | 0.49439 | 57.843 | -64.5126 | 57.9391 | 58.0811 | 57.7698 | 58.0124 | 0.4303 | 57.8796 | -64.4577 | 58.0719 | 58.1635 | 57.9758 | 0.20142 | -0.091552 | 0.10986 | 0.20599 | 122.5021 | 122.4335 | 122.1909 | 122.525 | 122.2824 | -0.036621 | 0.14648 | 0.33875 | 122.5845 | 64.6225 | 122.3969 | 64.6591 | 122.4335 | 122.5937 | 122.4518 | 122.6212 | 122.5296 | 122.3557 | 122.3373 | 122.2641 | 122.3007 | -122.2458 | -122.1909 | 122.3602 | 122.493 | 64.9155 | 64.8514
1472.8281 | 122.58 | -64.4485 | 57.7194 | -0.84625 | 0.059872 | 0.1258 | 3.6698 | -0.00038451 | 0.70653 | 0.00051913 | 0.021088 | 0.16331 | 0.12645 | -0.0018712 | 0.057533 | 0.10436 | -0.0027173 | 0.50354 | 57.8156 | -64.4714 | 57.93 | 58.0719 | 57.5317 | 57.8613 | 0.3479 | 57.9163 | -64.4394 | 58.0765 | 58.1451 | 57.9803 | 0.18768 | -0.022889 | 0.096131 | 0.21057 | 122.5204 | 122.3099 | 121.9803 | 122.3328 | 122.0032 | 0.009155 | 0.19684 | 0.35706 | 122.5937 | 64.6362 | 122.4289 | 64.6271 | 122.4197 | 122.5433 | 122.4014 | 122.5845 | 122.5159 | 122.287 | 122.3557 | 122.2641 | 122.3648 | -122.1909 | -122.1588 | 122.3785 | 122.525 | 64.9521 | 64.7964
1473.8906 | 121.9116 | -64.1647 | 57.486 | -1.4948 | 0.047909 | 0.11619 | 3.6315 | -0.00081171 | 0.7029 | -0.00054907 | -0.20169 | 0.15668 | 0.12623 | 0.0021876 | 0.058387 | 0.10415 | -0.0014355 | 0.37994 | 57.2433 | -64.2426 | 57.7423 | 58.2321 | 57.5409 | 57.6553 | 0.24719 | 57.8201 | -64.357 | 57.9712 | 58.0399 | 57.8659 | 0.10529 | -0.07782 | -0.24262 | 0.25635 | 122.3969 | 121.8201 | 121.7056 | 121.8979 | 121.7834 | -0.19226 | 0.33417 | 0.48523 | 122.2046 | 64.27 | 122.0306 | 64.4623 | 122.2229 | 122.4747 | 121.9849 | 122.3969 | 122.3282 | 121.4859 | 122.1771 | 121.4081 | 121.9849 | -121.7285 | -121.843 | 121.907 | 122.1359 | 64.5447 | 64.4119
1474.8281 | 122.438 | -64.4531 | 57.55 | -0.90729 | 0.061154 | 0.12431 | 3.6638 | 0.0045289 | 0.70332 | 0.00030553 | -0.11014 | 0.16352 | 0.1273 | -0.00037605 | 0.056465 | 0.10521 | -0.0031445 | 0.46234 | 57.8247 | -64.3433 | 57.9346 | 57.9803 | 57.6828 | 58.0078 | 0.41199 | 57.843 | -64.4714 | 58.0856 | 58.1497 | 57.9758 | 0.18768 | 0.10986 | 0.27466 | 0.38452 | 122.4335 | 122.4609 | 122.1359 | 122.3511 | 122.0261 | -0.018311 | 0.29297 | 0.53558 | 122.6028 | 64.6408 | 122.4289 | 64.6591 | 122.4472 | 122.3236 | 122.2778 | 122.6212 | 122.5571 | 122.168 | 122.3145 | 122.2778 | 122.2961 | -121.8933 | -122.0215 | 122.3877 | 122.5388 | 64.9155 | 64.8651
1475.8906 | 122.5525 | -63.8718 | 57.2617 | -1.5024 | 0.0462 | 0.10658 | 3.191 | -0.0059387 | 0.69627 | 0.043885 | -0.24747 | 0.023383 | 0.12132 | -0.011912 | 0.040229 | 0.0099376 | -0.0099805 | 0.26093 | 53.9703 | -64.0594 | 57.6233 | 57.7835 | 57.4036 | 57.55 | 0.19226 | 57.4036 | -64.0366 | 57.6416 | 57.9437 | 57.6599 | 0.15106 | -0.18768 | -3.2913 | 0.36163 | 121.6553 | 121.4218 | 121.2753 | 121.6095 | 121.463 | -0.16479 | 0.14191 | 0.37994 | 121.8155 | 64.0228 | 121.5317 | 64.1876 | 121.6965 | 121.843 | 121.6827 | 121.9803 | 121.6782 | 118.0298 | 121.4401 | 117.8421 | 121.2753 | -121.3211 | -121.2982 | 121.4951 | 121.5134 | 64.1327 | 64.064
1476.8281 | 122.6395 | -64.4348 | 57.7927 | -0.89203 | 0.059018 | 0.12538 | 3.6593 | 0.0030335 | 0.70076 | -0.00076267 | 0.0088807 | 0.16288 | 0.12901 | -0.0018712 | 0.056678 | 0.10585 | -0.0012219 | 0.48981 | 57.843 | -64.2517 | 57.93 | 58.1177 | 57.486 | 57.8888 | 0.34332 | 57.756 | -64.3158 | 58.0811 | 58.1406 | 57.9712 | 0.19684 | 0.1831 | 0.050354 | 0.13733 | 122.5525 | 122.3236 | 121.9208 | 122.1405 | 121.7377 | 0.11902 | -0.036622 | 0.28839 | 122.5754 | 64.6317 | 122.406 | 64.5126 | 122.287 | 122.3694 | 122.1817 | 122.4564 | 122.3969 | 122.0947 | 122.0718 | 122.2778 | 122.1909 | -122.0444 | -122.1085 | 122.3648 | 122.5159 | 64.9246 | 64.7781
1477.8906 | 121.8704 | -64.0778 | 58.0261 | -1.1133 | 0.054104 | 0.10615 | 3.5869 | -0.0025207 | 0.68089 | -0.015716 | -0.33292 | 0.14686 | 0.11619 | -0.0074254 | 0.05326 | 0.092823 | -0.0061353 | 0.42114 | 57.4356 | -64.0137 | 57.5638 | 57.7515 | 57.4768 | 57.6141 | 0.21515 | 57.486 | -64.0869 | 57.6828 | 57.9987 | 57.8018 | 0.11444 | 0.064087 | -0.59051 | -0.46234 | 121.8292 | 121.6919 | 121.5546 | 121.6278 | 121.4905 | -0.009155 | -0.54016 | -0.34332 | 122.0764 | 64.1922 | 121.8796 | 64.2014 | 121.8887 | 121.7651 | 121.5775 | 122.0856 | 121.7697 | 121.4493 | 121.5729 | 121.5134 | 121.5637 | -122.0398 | -122.113 | 121.6415 | 121.7606 | 64.4989 | 64.2929
1478.8281 | 122.731 | -64.4531 | 57.9987 | -0.81574 | 0.059018 | 0.1226 | 3.6559 | -0.00038451 | 0.69414 | -0.00076267 | -0.07962 | 0.16459 | 0.12901 | -0.0022986 | 0.05796 | 0.10308 | 0.00048713 | 0.48065 | 57.8613 | -64.3982 | 57.9117 | 58.0536 | 57.7469 | 57.9941 | 0.42114 | 57.9071 | -64.4119 | 58.0307 | 58.1314 | 57.9575 | 0.15106 | 0.054932 | -0.13733 | -0.086975 | 122.5067 | 122.4472 | 122.2 | 122.3923 | 122.1451 | 0.041199 | -0.091553 | 0.032044 | 122.5845 | 64.6042 | 122.4106 | 64.563 | 122.3694 | 122.4518 | 122.3099 | 122.5433 | 122.4426 | 122.2595 | 122.319 | 122.3145 | 122.3602 | -122.3969 | -122.4106 | 122.3648 | 122.4838 | 64.9338 | 64.8743
1479.8906 | 122.1817 | -64.3478 | 57.8796 | -1.3345 | 0.053463 | 0.11961 | 3.62 | -0.0014527 | 0.69542 | 0.00051913 | -0.11929 | 0.16138 | 0.12751 | -0.004862 | 0.057747 | 0.10543 | 0.00027333 | 0.43488 | 57.0877 | -64.1464 | 58.017 | 58.0719 | 57.55 | 57.8934 | 0.29297 | 57.724 | -64.1968 | 57.9758 | 58.0444 | 57.8613 | 0.11444 | 0.20142 | -0.79193 | 0.13733 | 122.4197 | 122.2412 | 121.8979 | 122.0398 | 121.6965 | 0.15106 | -0.15564 | 0.09613 | 122.3923 | 64.4623 | 122.2092 | 64.3112 | 122.0581 | 122.2183 | 122.1634 | 122.2412 | 122.1725 | 121.2341 | 121.9208 | 121.4355 | 122.0718 | -122.0261 | -122.0764 | 122.3648 | 122.3236 | 64.7827 | 64.6408
1480.8281 | 122.7722 | -64.4348 | 57.8567 | -0.86151 | 0.05859 | 0.12367 | 3.6516 | 0.0047425 | 0.69392 | 0.00051913 | 0.011932 | 0.16395 | 0.12623 | -0.0078528 | 0.057747 | 0.10329 | -0.0018629 | 0.49896 | 57.8613 | -64.3616 | 57.9529 | 58.1131 | 57.486 | 57.8796 | 0.36163 | 57.8522 | -64.3387 | 58.0673 | 58.136 | 57.9529 | 0.17853 | 0.073242 | 0.004578 | 0.096131 | 122.5479 | 122.3145 | 121.9208 | 122.2412 | 121.8475 | 0.09613 | -0.004577 | 0.21057 | 122.5708 | 64.6133 | 122.3877 | 64.5172 | 122.2916 | 122.4747 | 122.3145 | 122.4747 | 122.406 | 122.2229 | 122.1909 | 122.2961 | 122.287 | -122.2183 | -122.1954 | 122.3877 | 122.5021 | 64.9338 | 64.7964
1481.8906 | 122.0078 | -63.9999 | 57.3669 | -1.0522 | 0.047482 | 0.11256 | 3.6431 | -0.0074341 | 0.6747 | -0.015075 | -0.29935 | 0.14942 | 0.11213 | -0.01832 | 0.04792 | 0.11419 | -0.0072035 | 0.46234 | 57.1426 | -64.151 | 57.6782 | 57.8796 | 57.6187 | 57.8247 | 0.35706 | 57.5317 | -63.9633 | 57.7377 | 57.9987 | 57.7606 | 0.25635 | -0.15106 | -0.2243 | 0.31128 | 121.8796 | 121.8246 | 121.6187 | 121.9757 | 121.7697 | 0.036621 | 0.16479 | 0.37079 | 121.9986 | 64.2563 | 121.7606 | 64.2197 | 121.7239 | 122.0306 | 121.8292 | 121.962 | 121.7011 | 121.2936 | 121.4951 | 121.1426 | 121.5317 | -121.5179 | -121.3303 | 121.6782 | 121.7377 | 64.4623 | 64.357
1482.8281 | 122.731 | -64.4211 | 57.9849 | -0.82336 | 0.060086 | 0.12345 | 3.6482 | 0.0011109 | 0.69222 | -0.0022581 | -0.049103 | 0.16202 | 0.12901 | -0.0067846 | 0.05796 | 0.1065 | -0.0020765 | 0.48523 | 57.8522 | -64.4806 | 57.9071 | 58.0444 | 57.7652 | 58.0078 | 0.43488 | 57.9071 | -64.4348 | 58.0353 | 58.1177 | 57.9346 | 0.16479 | -0.059509 | -0.13275 | -0.07782 | 122.4655 | 122.4289 | 122.1863 | 122.4884 | 122.2458 | -0.013732 | -0.07782 | 0.050354 | 122.5388 | 64.5859 | 122.3557 | 64.5996 | 122.3694 | 122.525 | 122.3877 | 122.5525 | 122.4701 | 122.3328 | 122.3419 | 122.2733 | 122.3282 | -122.4655 | -122.4197 | 122.3282 | 122.4564 | 64.9063 | 64.856
1483.8281 | 122.7219 | -64.4211 | 57.9758 | -0.78522 | 0.05795 | 0.12239 | 3.6473 | 0.0015381 | 0.68965 | 0.0011599 | -0.036896 | 0.16181 | 0.12794 | -0.0063574 | 0.056251 | 0.105 | -0.0020765 | 0.47607 | 57.8522 | -64.4852 | 57.8888 | 57.9987 | 57.7744 | 58.0261 | 0.43488 | 57.9208 | -64.4623 | 58.049 | 58.1543 | 57.9758 | 0.2243 | -0.064086 | -0.1236 | -0.086975 | 122.4197 | 122.4472 | 122.1954 | 122.5113 | 122.2595 | -0.041198 | -0.054932 | 0.073242 | 122.5754 | 64.6454 | 122.3969 | 64.6866 | 122.438 | 122.4838 | 122.374 | 122.6166 | 122.5113 | 122.3373 | 122.3831 | 122.2733 | 122.3419 | -122.4609 | -122.438 | 122.3099 | 122.4701 | 64.8972 | 64.856
1484.8906 | 121.994 | -64.1647 | 58.0124 | -1.1667 | 0.053677 | 0.1226 | 3.6226 | -0.0033753 | 0.68025 | -0.00033547 | -0.15897 | 0.15775 | 0.12324 | -0.0012304 | 0.056892 | 0.10009 | -0.0025037 | 0.52643 | 57.3486 | -64.3341 | 57.8751 | 57.9437 | 57.756 | 57.962 | 0.43945 | 57.8979 | -64.27 | 58.0124 | 58.1085 | 57.9163 | 0.27466 | -0.16937 | -0.66376 | -0.13733 | 122.1085 | 122.1268 | 121.9208 | 122.2961 | 122.0901 | -0.10529 | -0.11444 | 0 | 122.2733 | 64.4394 | 122.081 | 64.5447 | 122.1863 | 122.2778 | 122.2092 | 122.3785 | 122.2824 | 121.6827 | 122.168 | 121.5134 | 122.0627 | -122.3465 | -122.2824 | 122.0398 | 122.1771 | 64.6912 | 64.6042
1485.8281 | 122.7081 | -64.4257 | 57.9987 | -0.83099 | 0.05795 | 0.12452 | 3.6443 | -0.00081171 | 0.68602 | -0.00076267 | -0.033844 | 0.16502 | 0.12901 | -0.002085 | 0.056465 | 0.1035 | -0.0020765 | 0.59967 | 57.8934 | -64.4897 | 57.8934 | 57.9941 | 57.7652 | 57.9941 | 0.4303 | 57.9071 | -64.476 | 58.0719 | 58.1406 | 57.9849 | 0.24261 | -0.064087 | -0.10529 | -0.10529 | 122.4197 | 122.4197 | 122.1909 | 122.4838 | 122.2549 | -0.050354 | -0.091553 | 0.073242 | 122.5662 | 64.6683 | 122.4106 | 64.7186 | 122.4609 | 122.4838 | 122.3831 | 122.6166 | 122.5479 | 122.3831 | 122.3831 | 122.319 | 122.3328 | -122.4884 | -122.4747 | 122.319 | 122.4976 | 65.0253 | 64.856
1486.8906 | 122.7127 | -64.4302 | 57.9666 | -0.82336 | 0.058377 | 0.12431 | 3.6411 | 0.0043151 | 0.68474 | 0.0020145 | -0.10403 | 0.1648 | 0.12687 | -0.00037605 | 0.056038 | 0.10436 | -0.0031445 | 0.43488 | 57.843 | -64.4989 | 57.9117 | 58.0261 | 57.7927 | 58.0124 | 0.44403 | 57.8888 | -64.4623 | 58.0673 | 58.1451 | 57.9666 | 0.17853 | -0.068664 | -0.1236 | -0.054932 | 122.4564 | 122.4426 | 122.2229 | 122.5113 | 122.2916 | -0.032043 | -0.07782 | 0.10071 | 122.5754 | 64.6088 | 122.3969 | 64.6408 | 122.4289 | 122.525 | 122.4106 | 122.6074 | 122.5296 | 122.3419 | 122.3511 | 122.2733 | 122.319 | -122.4655 | -122.4289 | 122.3419 | 122.4976 | 64.8651 | 64.8743
1487.8281 | 122.8729 | -64.3936 | 58.0536 | -0.77759 | 0.057309 | 0.12046 | 3.6411 | -0.0016663 | 0.68346 | -0.0016171 | -0.058258 | 0.16288 | 0.12794 | -0.0035802 | 0.057533 | 0.10372 | -0.0012219 | 0.5722 | 57.8522 | -64.4485 | 58.0078 | 58.1131 | 57.8705 | 58.0536 | 0.5722 | 57.8934 | -64.4119 | 58.0856 | 58.2321 | 58.049 | 0.19226 | -0.054931 | -0.20142 | -0.045777 | 122.5067 | 122.4472 | 122.2641 | 122.5021 | 122.319 | -0.01831 | -0.16022 | 0.032043 | 122.6257 | 64.5859 | 122.4426 | 64.6042 | 122.4609 | 122.5616 | 122.4564 | 122.644 | 122.4976 | 122.3007 | 122.3053 | 122.2458 | 122.287 | -122.5021 | -122.4655 | 122.4014 | 122.4792 | 64.9658 | 64.9658
1488.8906 | 122.4518 | -64.4257 | 58.0032 | -1.098 | 0.040646 | 0.11726 | 3.6181 | -0.0029479 | 0.67427 | -0.0058897 | -0.23526 | 0.15732 | 0.12538 | -0.0055028 | 0.059669 | 0.10543 | 0.0024097 | 0.43488 | 57.2159 | -64.5447 | 57.7652 | 57.9575 | 57.7194 | 57.8888 | 0.30212 | 57.9391 | -64.4531 | 57.9712 | 58.0399 | 57.8384 | 0.11902 | -0.11902 | -0.78735 | -0.23804 | 122.3831 | 122.3145 | 122.1451 | 122.4335 | 122.2641 | -0.027466 | -0.064087 | -0.032044 | 122.4655 | 64.5447 | 122.2641 | 64.5721 | 122.2916 | 122.5021 | 122.3099 | 122.493 | 122.4243 | 121.7606 | 122.3923 | 121.6415 | 122.3648 | -122.5479 | -122.4564 | 122.1909 | 122.3969 | 64.8605 | 64.7278
1489.8281 | 122.7219 | -64.4073 | 57.9803 | -0.81574 | 0.056027 | 0.12345 | 3.6371 | -0.00038451 | 0.68004 | 0.0011599 | -0.042999 | 0.16395 | 0.12645 | -0.013407 | 0.058387 | 0.10372 | 0.00091433 | 0.51727 | 57.8659 | -64.4669 | 57.93 | 58.049 | 57.8522 | 58.0582 | 0.5127 | 57.9025 | -64.4257 | 58.0811 | 58.1772 | 58.0307 | 0.28839 | -0.059509 | -0.11444 | -0.050354 | 122.4564 | 122.4655 | 122.2595 | 122.525 | 122.319 | -0.01831 | -0.07782 | 0.10071 | 122.5845 | 64.6957 | 122.4381 | 64.7141 | 122.4564 | 122.5159 | 122.3969 | 122.6028 | 122.5067 | 122.3328 | 122.3282 | 122.2733 | 122.3099 | -122.4472 | -122.406 | 122.3373 | 122.4884 | 64.9246 | 64.92
1490.8281 | 122.7356 | -64.4165 | 57.9803 | -0.83862 | 0.058377 | 0.12645 | 3.636 | -0.0016663 | 0.67769 | 9.193e-05 | -0.076569 | 0.16267 | 0.12773 | -0.0059302 | 0.05796 | 0.10265 | -0.0048535 | 0.59509 | 57.8796 | -64.4669 | 57.8934 | 57.9987 | 57.7789 | 58.0032 | 0.43488 | 57.9117 | -64.4531 | 58.049 | 58.1314 | 57.962 | 0.23804 | -0.050354 | -0.10071 | -0.086975 | 122.4152 | 122.4197 | 122.1954 | 122.4701 | 122.2458 | -0.036621 | -0.068665 | 0.068664 | 122.5479 | 64.6545 | 122.3785 | 64.6912 | 122.4152 | 122.4655 | 122.3602 | 122.5845 | 122.5021 | 122.3465 | 122.3648 | 122.2961 | 122.3282 | -122.4472 | -122.4335 | 122.3099 | 122.4655 | 65.0116 | 64.8514
1491.8906 | 122.1451 | -64.1418 | 58.0078 | -0.92255 | 0.044064 | 0.11277 | 3.6025 | -0.012134 | 0.66017 | -0.018707 | -0.38174 | 0.17313 | 0.10914 | -0.0091344 | 0.049842 | 0.10436 | -0.0091261 | 0.53101 | 57.1793 | -64.4852 | 57.9025 | 57.9803 | 57.7789 | 57.9529 | 0.5127 | 57.9254 | -64.3066 | 58.0261 | 58.1223 | 57.9117 | 0.27008 | -0.34332 | -0.82855 | -0.10529 | 122.1222 | 122.0947 | 121.9208 | 122.438 | 122.2641 | -0.16479 | -0.082397 | 0.018311 | 122.2641 | 64.4119 | 122.0535 | 64.5767 | 122.2183 | 122.4655 | 122.3877 | 122.4289 | 122.3328 | 121.6644 | 122.2321 | 121.3211 | 122.0673 | -122.493 | -122.3145 | 122.0444 | 122.168 | 64.6729 | 64.6545
1492.8281 | 122.6852 | -64.4257 | 57.962 | -0.83862 | 0.05859 | 0.12239 | 3.6337 | -0.0016663 | 0.67705 | 0.00094633 | -0.064362 | 0.16245 | 0.1273 | -0.0040076 | 0.05796 | 0.105 | -0.0022901 | 0.4715 | 57.8705 | -64.5126 | 57.8705 | 57.962 | 57.7789 | 57.9849 | 0.38452 | 57.9163 | -64.4531 | 58.017 | 58.0994 | 57.9254 | 0.19226 | -0.086975 | -0.091553 | -0.091553 | 122.3877 | 122.4106 | 122.2046 | 122.4976 | 122.2916 | -0.027466 | -0.045776 | 0.054932 | 122.525 | 64.6179 | 122.3511 | 64.6454 | 122.3785 | 122.4747 | 122.3831 | 122.5525 | 122.4701 | 122.3831 | 122.3694 | 122.2961 | 122.3419 | -122.4747 | -122.4152 | 122.2961 | 122.4426 | 64.8972 | 64.8102
1493.8906 | 122.1497 | -64.2014 | 57.8156 | -1.449 | 0.05795 | 0.10594 | 3.5956 | -0.011066 | 0.65761 | 0.043885 | -0.397 | 0.021247 | 0.11769 | -0.018107 | 0.045784 | 0.011647 | -0.01233 | 0.54932 | 57.0923 | -64.3295 | 57.9071 | 57.9803 | 57.7744 | 57.9483 | 0.40741 | 57.7606 | -64.2517 | 58.0307 | 58.017 | 57.8384 | 0.17853 | -0.12817 | -0.72327 | 0.091552 | 122.1817 | 122.1497 | 121.9757 | 122.2778 | 122.1039 | -0.050354 | -0.054932 | 0.21515 | 122.2183 | 64.3799 | 122.0398 | 64.4302 | 122.0901 | 122.3099 | 122.2366 | 122.2687 | 122.2824 | 121.4218 | 122.0123 | 121.2936 | 121.962 | -122.1451 | -122.0673 | 122.1085 | 122.2321 | 64.7507 | 64.6088
1494.8281 | 122.6898 | -64.4394 | 57.962 | -0.80811 | 0.060513 | 0.12559 | 3.6303 | 0.0013245 | 0.67342 | -0.0033261 | -0.082672 | 0.16352 | 0.12709 | -0.0044348 | 0.058174 | 0.10393 | 0.00091433 | 0.50812 | 57.8522 | -64.476 | 57.9208 | 58.0353 | 57.7744 | 57.9987 | 0.44861 | 57.8659 | -64.4577 | 58.0582 | 58.1223 | 57.9529 | 0.18768 | -0.036621 | -0.10986 | -0.041199 | 122.4747 | 122.438 | 122.2137 | 122.4747 | 122.2504 | -0.018311 | -0.09613 | 0.096131 | 122.5616 | 64.6271 | 122.3923 | 64.6454 | 122.4106 | 122.5113 | 122.3969 | 122.58 | 122.5159 | 122.3282 | 122.3236 | 122.2916 | 122.3053 | -122.438 | -122.4197 | 122.3602 | 122.4976 | 64.9475 | 64.888
1495.8906 | 122.7081 | -64.4119 | 57.9712 | -0.86914 | 0.060299 | 0.12431 | 3.6309 | -0.00081171 | 0.67278 | 0.0024417 | -0.11014 | 0.16459 | 0.12709 | 5.1352e-05 | 0.055824 | 0.10436 | -0.0014355 | 0.49439 | 57.843 | -64.4989 | 57.9254 | 58.0261 | 57.7789 | 58.0078 | 0.43945 | 57.8751 | -64.4028 | 58.1543 | 58.0444 | 58.0353 | 0.24261 | -0.086975 | -0.12817 | -0.045776 | 122.438 | 122.4197 | 122.1909 | 122.5067 | 122.2778 | 0.009155 | -0.09613 | 0.18311 | 122.4564 | 64.6545 | 122.4472 | 64.6454 | 122.438 | 122.525 | 122.4243 | 122.4472 | 122.5571 | 122.3419 | 122.2778 | 122.2549 | 122.287 | -122.4701 | -122.374 | 122.3373 | 122.5662 | 64.9063 | 64.8514
1496.8281 | 122.7448 | -64.4073 | 57.9712 | -0.86914 | 0.057736 | 0.12132 | 3.6279 | -0.0018799 | 0.67448 | 0.00030553 | -0.070465 | 0.16502 | 0.12815 | -0.009989 | 0.05796 | 0.10564 | -0.0022901 | 0.46692 | 57.8705 | -64.4806 | 57.8796 | 57.9758 | 57.7744 | 57.9666 | 0.39825 | 57.9071 | -64.4257 | 58.0261 | 58.1177 | 58.0124 | 0.27008 | -0.073242 | -0.10071 | -0.091552 | 122.3831 | 122.374 | 122.1817 | 122.4472 | 122.2549 | -0.01831 | -0.064087 | 0.054932 | 122.525 | 64.6774 | 122.4197 | 64.6957 | 122.438 | 122.4564 | 122.3602 | 122.5433 | 122.4518 | 122.3511 | 122.3328 | 122.2778 | 122.3145 | -122.4518 | -122.3969 | 122.287 | 122.4335 | 64.8743 | 64.8056
1497.8906 | 122.6898 | -64.4394 | 57.9117 | -0.8844 | 0.060086 | 0.12516 | 3.6264 | -0.0012391 | 0.67171 | -0.0016171 | -0.097931 | 0.16267 | 0.12794 | 0.00069215 | 0.053474 | 0.10521 | 0.00070073 | 0.49896 | 57.8247 | -64.5035 | 57.9208 | 58.0124 | 57.7789 | 57.9895 | 0.43488 | 57.8751 | -64.4531 | 58.0673 | 58.1406 | 57.9712 | 0.16022 | -0.064087 | -0.086975 | 0.009155 | 122.4518 | 122.4289 | 122.2183 | 122.493 | 122.2824 | -0.013733 | -0.036621 | 0.15564 | 122.58 | 64.5996 | 122.4106 | 64.6133 | 122.4243 | 122.5159 | 122.4243 | 122.5937 | 122.5204 | 122.3282 | 122.3282 | 122.2641 | 122.3145 | -122.4152 | -122.3648 | 122.3602 | 122.5067 | 64.9384 | 64.8743
1498.8281 | 122.6807 | -64.4119 | 57.9483 | -0.7547 | 0.054959 | 0.12281 | 3.6236 | 0.0019653 | 0.67043 | -0.0018307 | -0.064362 | 0.16395 | 0.12687 | -0.003794 | 0.058174 | 0.10329 | -0.0044263 | 0.50812 | 57.8751 | -64.4669 | 57.8934 | 57.9803 | 57.7789 | 57.9941 | 0.44403 | 57.8934 | -64.444 | 58.0353 | 58.1314 | 57.9483 | 0.22888 | -0.054932 | -0.073242 | -0.054931 | 122.3923 | 122.406 | 122.1909 | 122.4609 | 122.2458 | -0.032044 | -0.054931 | 0.086975 | 122.5433 | 64.6408 | 122.3602 | 64.6729 | 122.3923 | 122.4472 | 122.3602 | 122.5754 | 122.4792 | 122.3419 | 122.3373 | 122.287 | 122.3053 | -122.4152 | -122.3923 | 122.3053 | 122.4472 | 64.92 | 64.856
1499.8906 | 122.7036 | -64.4211 | 57.9391 | -0.82336 | 0.058163 | 0.1226 | 3.6217 | -0.0023071 | 0.66957 | 0.00051913 | -0.094879 | 0.16459 | 0.12773 | -0.003153 | 0.057106 | 0.10692 | -0.0031445 | 0.49439 | 57.8339 | -64.5035 | 57.8751 | 58.0902 | 57.8384 | 57.9758 | 0.42114 | 57.8888 | -64.4211 | 58.0536 | 58.1406 | 57.9483 | 0.19684 | -0.082397 | -0.10529 | -0.064087 | 122.5113 | 122.3969 | 122.2595 | 122.4792 | 122.3419 | 0 | -0.050354 | 0.11444 | 122.5616 | 64.6179 | 122.3694 | 64.6179 | 122.3694 | 122.5937 | 122.3785 | 122.5616 | 122.4747 | 122.3373 | 122.3099 | 122.2549 | 122.3099 | -122.4426 | -122.3602 | 122.2961 | 122.4747 | 64.9155 | 64.8422
1500.8281 | 122.6486 | -64.4302 | 57.962 | -0.83862 | 0.056881 | 0.12431 | 3.623 | 4.2692e-05 | 0.66744 | 0.0011599 | -0.10709 | 0.16502 | 0.12794 | -0.011912 | 0.057106 | 0.10244 | -0.0010083 | 0.46692 | 57.8522 | -64.4852 | 57.8934 | 57.9712 | 57.7972 | 58.1177 | 0.45319 | 57.9071 | -64.4531 | 58.017 | 58.1085 | 57.9529 | 0.21973 | -0.054931 | -0.10986 | -0.068664 | 122.4014 | 122.5479 | 122.2275 | 122.6028 | 122.2824 | -0.022888 | -0.054932 | 0.054932 | 122.5388 | 64.65 | 122.3831 | 64.6729 | 122.406 | 122.4564 | 122.3785 | 122.5616 | 122.4701 | 122.3373 | 122.3602 | 122.2824 | 122.3373 | -122.4472 | -122.4152 | 122.3236 | 122.4472 | 64.8972 | 64.8834
1501.8906 | 122.6212 | -64.4302 | 57.9849 | -1.2811 | 0.053036 | 0.12345 | 3.6044 | 0.00089729 | 0.66658 | 9.193e-05 | -0.15897 | 0.16331 | 0.1273 | 0.001333 | 0.058601 | 0.10393 | 0.0011279 | 0.45319 | 57.4173 | -64.5721 | 57.811 | 57.8888 | 57.6874 | 57.9071 | 0.33417 | 57.9163 | -64.4897 | 57.9803 | 58.0444 | 57.8522 | 0.11902 | -0.14191 | -0.56763 | -0.17395 | 122.319 | 122.3373 | 122.1176 | 122.4792 | 122.2595 | -0.059509 | -0.068664 | -0.004577 | 122.4747 | 64.5493 | 122.2824 | 64.6088 | 122.3419 | 122.4609 | 122.3831 | 122.5342 | 122.4701 | 121.9894 | 122.406 | 121.8475 | 122.3465 | -122.5571 | -122.4747 | 122.2412 | 122.4106 | 64.8834 | 64.7644
1502.8281 | 122.6715 | -64.4165 | 57.9483 | -0.86151 | 0.058377 | 0.12239 | 3.6191 | 0.0021789 | 0.66338 | -0.00076267 | -0.082672 | 0.16224 | 0.12559 | -0.0022986 | 0.057747 | 0.10436 | 0.0013415 | 0.46234 | 57.8339 | -64.5081 | 57.8796 | 57.9803 | 57.7515 | 57.9712 | 0.40283 | 57.8705 | -64.444 | 58.0215 | 58.1039 | 57.9025 | 0.16937 | -0.091553 | -0.11444 | -0.068664 | 122.3969 | 122.3877 | 122.168 | 122.4792 | 122.2595 | -0.027466 | -0.07782 | 0.073242 | 122.5204 | 64.5859 | 122.319 | 64.6133 | 122.3465 | 122.4884 | 122.3877 | 122.5479 | 122.4655 | 122.3419 | 122.3145 | 122.2504 | 122.287 | -122.4564 | -122.3923 | 122.2961 | 122.438 | 64.8788 | 64.8193
1503.8906 | 122.6807 | -64.4257 | 57.9391 | -0.8844 | 0.057522 | 0.12217 | 3.6172 | 0.0026063 | 0.66637 | -0.00054907 | -0.091827 | 0.16502 | 0.12666 | -0.0061438 | 0.056678 | 0.10585 | -0.0020765 | 0.48523 | 57.8201 | -64.4989 | 57.9117 | 58.0307 | 57.7652 | 57.9895 | 0.4303 | 57.8705 | -64.4394 | 58.0444 | 58.1131 | 57.9483 | 0.17853 | -0.073242 | -0.11902 | -0.027466 | 122.4564 | 122.4152 | 122.1909 | 122.4884 | 122.2641 | -0.013733 | -0.068665 | 0.10529 | 122.5388 | 64.6042 | 122.374 | 64.6179 | 122.3877 | 122.5296 | 122.4106 | 122.5525 | 122.4838 | 122.319 | 122.3099 | 122.2458 | 122.2961 | -122.438 | -122.3785 | 122.3373 | 122.4701 | 64.9109 | 64.856
1504.8281 | 122.6578 | -64.4119 | 57.9346 | -0.86914 | 0.059659 | 0.12303 | 3.6162 | 0.0011109 | 0.66316 | -0.0024717 | -0.076569 | 0.16416 | 0.12666 | -0.0018712 | 0.058174 | 0.10286 | 0.0034777 | 0.46234 | 57.8659 | -64.5035 | 57.8888 | 57.9575 | 57.7744 | 57.9666 | 0.39825 | 57.9025 | -64.4394 | 58.017 | 58.0856 | 57.93 | 0.19684 | -0.091553 | -0.068664 | -0.045776 | 122.3694 | 122.3785 | 122.1863 | 122.4701 | 122.2778 | -0.027466 | -0.032043 | 0.082398 | 122.4976 | 64.6088 | 122.3419 | 64.6362 | 122.3694 | 122.4609 | 122.3923 | 122.525 | 122.4564 | 122.3694 | 122.3419 | 122.2778 | 122.3145 | -122.438 | -122.374 | 122.3007 | 122.4289 | 64.8743 | 64.8102
1505.8281 | 122.7219 | -64.3936 | 57.9895 | -0.80048 | 0.057736 | 0.12303 | 3.6151 | -0.0016663 | 0.66423 | -0.0024717 | -0.073517 | 0.16395 | 0.1273 | -0.00828 | 0.05796 | 0.105 | -0.0031445 | 0.50812 | 57.8339 | -64.4897 | 57.9163 | 58.0307 | 57.8156 | 58.0307 | 0.52643 | 57.9025 | -64.4165 | 58.0673 | 58.1635 | 57.9803 | 0.28381 | -0.09613 | -0.15564 | -0.073242 | 122.4243 | 122.4243 | 122.2092 | 122.5204 | 122.3053 | -0.022888 | -0.086975 | 0.07782 | 122.5571 | 64.6774 | 122.374 | 64.7003 | 122.3969 | 122.5204 | 122.406 | 122.58 | 122.4838 | 122.3236 | 122.319 | 122.2275 | 122.2961 | -122.4792 | -122.406 | 122.3099 | 122.4609 | 64.9017 | 64.92
1506.8906 | 122.7036 | -64.3982 | 57.9437 | -1.0828 | 0.058804 | 0.12516 | 3.6149 | 0.0066651 | 0.66209 | -0.0011899 | -0.1315 | 0.16373 | 0.12794 | 0.0011194 | 0.056465 | 0.10372 | 0.00027333 | 0.48523 | 57.6736 | -64.5264 | 57.9025 | 58.0124 | 57.7469 | 57.9666 | 0.4303 | 57.8796 | -64.444 | 58.0536 | 58.1223 | 57.9254 | 0.19684 | -0.12817 | -0.27008 | -0.041199 | 122.4106 | 122.3648 | 122.1451 | 122.493 | 122.2733 | -0.045777 | -0.064087 | 0.10986 | 122.5204 | 64.595 | 122.3236 | 64.6408 | 122.3694 | 122.5388 | 122.4289 | 122.5662 | 122.4976 | 122.2 | 122.3236 | 122.0718 | 122.2778 | -122.4701 | -122.3877 | 122.3007 | 122.4518 | 64.8834 | 64.8285
1507.8281 | 122.7356 | -64.3845 | 57.9529 | -0.85388 | 0.058804 | 0.12281 | 3.6134 | 0.0023925 | 0.65697 | 0.0013735 | -0.073517 | 0.16288 | 0.1273 | -0.0033666 | 0.057747 | 0.10457 | -0.0012219 | 0.53558 | 57.8888 | -64.4577 | 57.9346 | 58.0536 | 57.8888 | 58.0902 | 0.59052 | 57.9117 | -64.3982 | 58.1039 | 58.2092 | 58.0353 | 0.33875 | -0.073243 | -0.064087 | -0.018311 | 122.438 | 122.4747 | 122.2733 | 122.5479 | 122.3465 | -0.013733 | -0.041199 | 0.15106 | 122.5937 | 64.7232 | 122.4197 | 64.7369 | 122.4335 | 122.5113 | 122.3923 | 122.6074 | 122.5021 | 122.3465 | 122.3099 | 122.2733 | 122.2961 | -122.4106 | -122.3511 | 122.319 | 122.4884 | 64.92 | 64.975
1508.8906 | 122.4838 | -64.4348 | 57.9712 | -0.42664 | 0.058377 | 0.10978 | 3.586 | -0.013629 | 0.63966 | -0.014434 | -0.32071 | 0.14707 | 0.11769 | -0.010843 | 0.057533 | 0.095387 | -0.0033581 | 0.45776 | 57.1289 | -64.5447 | 57.7881 | 57.8293 | 57.637 | 57.8522 | 0.29297 | 57.9391 | -64.4806 | 57.9391 | 57.9849 | 57.8156 | 0.1236 | -0.10986 | -0.84228 | -0.1831 | 122.2641 | 122.287 | 122.0718 | 122.3969 | 122.1817 | -0.045777 | -0.032043 | -0.032043 | 122.4197 | 64.5584 | 122.2504 | 64.6042 | 122.2961 | 122.374 | 122.3328 | 122.4655 | 122.4197 | 121.6736 | 122.4197 | 121.5637 | 122.374 | -122.5159 | -122.4518 | 122.2229 | 122.374 | 64.8926 | 64.7278
1509.8281 | 122.7036 | -64.3753 | 57.9575 | -0.78522 | 0.058377 | 0.1226 | 3.6091 | 0.0017517 | 0.65675 | -0.0022581 | -0.07962 | 0.16502 | 0.12837 | -0.0022986 | 0.058601 | 0.10543 | 0.00048713 | 0.52643 | 57.8796 | -64.4577 | 57.93 | 58.0353 | 57.8293 | 58.0353 | 0.52185 | 57.8751 | -64.4302 | 58.0719 | 58.1863 | 58.0261 | 0.32044 | -0.082398 | -0.077819 | -0.027465 | 122.4106 | 122.4106 | 122.2046 | 122.493 | 122.287 | -0.054932 | -0.082397 | 0.11444 | 122.5616 | 64.6957 | 122.4014 | 64.7507 | 122.4564 | 122.493 | 122.3877 | 122.6166 | 122.5021 | 122.3373 | 122.3053 | 122.2549 | 122.2504 | -122.4152 | -122.3877 | 122.3053 | 122.4472 | 64.9017 | 64.8972
1510.8906 | 122.6624 | -64.389 | 57.9071 | -0.83862 | 0.059872 | 0.12345 | 3.6097 | -0.0016663 | 0.65825 | 9.193e-05 | -0.11624 | 0.16267 | 0.12751 | -0.00080325 | 0.055183 | 0.10393 | -0.0046399 | 0.48981 | 57.8156 | -64.4989 | 57.9483 | 57.962 | 57.8888 | 57.9895 | 0.46692 | 57.8705 | -64.4211 | 58.0582 | 58.1314 | 57.9391 | 0.1831 | -0.10986 | -0.091552 | 0.041199 | 122.3511 | 122.3785 | 122.2778 | 122.4884 | 122.3877 | -0.032044 | -0.036621 | 0.15106 | 122.5204 | 64.5721 | 122.3282 | 64.6042 | 122.3602 | 122.4609 | 122.4472 | 122.5525 | 122.4792 | 122.3145 | 122.2916 | 122.2046 | 122.2595 | -122.406 | -122.3282 | 122.3373 | 122.4472 | 64.8788 | 64.856
1511.8281 | 122.6944 | -64.3799 | 57.9529 | -0.79285 | 0.06094 | 0.12239 | 3.608 | -0.0033753 | 0.65526 | -0.00097627 | -0.058258 | 0.16395 | 0.12687 | -0.0057166 | 0.057747 | 0.10521 | -0.0016493 | 0.56763 | 57.8613 | -64.476 | 57.9483 | 58.0673 | 57.8476 | 58.049 | 0.58594 | 57.8842 | -64.4119 | 58.0948 | 58.2001 | 58.0399 | 0.31128 | -0.09613 | -0.091553 | -0.004578 | 122.4472 | 122.4289 | 122.2275 | 122.525 | 122.3236 | -0.032043 | -0.068665 | 0.14191 | 122.58 | 64.6912 | 122.4197 | 64.7232 | 122.4518 | 122.5433 | 122.4243 | 122.612 | 122.5067 | 122.3373 | 122.2961 | 122.2412 | 122.2641 | -122.4289 | -122.3648 | 122.3282 | 122.4747 | 64.9475 | 64.9658
1512.8906 | 122.5983 | -64.4394 | 57.9529 | -1.1896 | 0.0462 | 0.11876 | 3.5886 | -0.0010253 | 0.64565 | -0.0031125 | -0.16202 | 0.16459 | 0.12901 | -0.002085 | 0.058387 | 0.10671 | -0.0025037 | 0.48065 | 57.5317 | -64.5218 | 57.8064 | 57.8705 | 57.6691 | 57.8842 | 0.35706 | 57.9071 | -64.4531 | 57.962 | 58.0261 | 57.8018 | 0.11902 | -0.082398 | -0.42114 | -0.14648 | 122.3099 | 122.3236 | 122.1085 | 122.406 | 122.1909 | -0.013733 | -0.045777 | 0.009155 | 122.4655 | 64.5584 | 122.2412 | 64.5721 | 122.2549 | 122.3923 | 122.3282 | 122.4792 | 122.4152 | 122.0535 | 122.3602 | 121.9711 | 122.3465 | -122.4747 | -122.406 | 122.2458 | 122.4014 | 64.92 | 64.7964
1513.8281 | 122.6578 | -64.4119 | 57.9163 | -0.86914 | 0.056881 | 0.12217 | 3.6044 | 0.0028199 | 0.65312 | 0.00073273 | -0.049103 | 0.1648 | 0.12837 | -0.00058965 | 0.058174 | 0.10479 | -0.0027173 | 0.49439 | 57.8705 | -64.4623 | 57.8659 | 57.9712 | 57.7698 | 57.9895 | 0.44861 | 57.9071 | -64.444 | 58.017 | 58.1268 | 57.9529 | 0.22888 | -0.050354 | -0.045777 | -0.050354 | 122.3831 | 122.4014 | 122.1817 | 122.4518 | 122.2321 | -0.032044 | -0.009156 | 0.10071 | 122.5388 | 64.6408 | 122.3648 | 64.6729 | 122.3969 | 122.4335 | 122.3282 | 122.5708 | 122.4609 | 122.3328 | 122.3511 | 122.2824 | 122.319 | -122.3785 | -122.3602 | 122.2778 | 122.4289 | 64.9063 | 64.8605
1514.8906 | 122.6257 | -64.4302 | 57.9391 | -1.1133 | 0.061368 | 0.12495 | 3.5927 | 0.0028199 | 0.65163 | -0.00076267 | -0.14371 | 0.1663 | 0.1273 | -0.0080664 | 0.056465 | 0.105 | 0.00091433 | 0.42114 | 57.3303 | -64.5126 | 57.8156 | 57.9117 | 57.692 | 57.9254 | 0.34332 | 57.9025 | -64.476 | 57.9987 | 58.049 | 57.8705 | 0.13733 | -0.082397 | -0.60883 | -0.1236 | 122.3419 | 122.3557 | 122.1222 | 122.438 | 122.2046 | -0.045776 | -0.036621 | 0.059509 | 122.4792 | 64.5676 | 122.3007 | 64.6133 | 122.3465 | 122.4243 | 122.3282 | 122.525 | 122.4747 | 121.843 | 122.3785 | 121.7606 | 122.3328 | -122.4518 | -122.4152 | 122.2458 | 122.4289 | 64.8514 | 64.7736
1515.8281 | 122.644 | -64.4165 | 57.9391 | -0.77759 | 0.059018 | 0.12367 | 3.6038 | -0.0014527 | 0.65334 | -0.0018307 | -0.082672 | 0.16544 | 0.1288 | -0.003153 | 0.058601 | 0.10585 | -0.00079467 | 0.46234 | 57.8522 | -64.476 | 57.8751 | 57.9758 | 57.7835 | 57.9803 | 0.37537 | 57.8934 | -64.4302 | 58.0124 | 58.0902 | 57.9254 | 0.21057 | -0.059509 | -0.086975 | -0.064087 | 122.3923 | 122.3969 | 122.2 | 122.4564 | 122.2595 | -0.013733 | -0.045776 | 0.073242 | 122.5067 | 64.6271 | 122.3419 | 64.6408 | 122.3557 | 122.4518 | 122.3511 | 122.5204 | 122.4426 | 122.3282 | 122.3236 | 122.2687 | 122.3099 | -122.4152 | -122.3694 | 122.2916 | 122.4289 | 64.8788 | 64.7919
1516.8906 | 122.4792 | -64.476 | 57.9346 | -1.3956 | 0.048977 | 0.11512 | 3.5734 | -0.013843 | 0.63539 | -0.018066 | -0.20779 | 0.15348 | 0.12046 | 0.00047855 | 0.05796 | 0.09795 | 0.0030505 | 0.43945 | 57.0465 | -64.476 | 57.7881 | 57.8384 | 57.637 | 57.8384 | 0.30212 | 57.9025 | -64.476 | 57.93 | 57.9803 | 57.8659 | 0.032043 | 0 | -0.88806 | -0.14648 | 122.3145 | 122.3145 | 122.113 | 122.3145 | 122.113 | 0 | -0.032043 | -0.004577 | 122.4564 | 64.5081 | 122.3419 | 64.5081 | 122.3419 | 122.3145 | 122.2641 | 122.4564 | 122.406 | 121.5225 | 122.3785 | 121.5225 | 122.3785 | -122.4106 | -122.4106 | 122.2641 | 122.406 | 64.9155 | 64.7781
1517.8281 | 122.6807 | -64.389 | 57.9346 | -0.81574 | 0.059659 | 0.12132 | 3.6012 | 4.2692e-05 | 0.64864 | 0.0013735 | -0.049103 | 0.16523 | 0.12773 | 0.0028284 | 0.058815 | 0.10286 | 0.00027333 | 0.52643 | 57.8476 | -64.4577 | 57.93 | 58.0261 | 57.8247 | 58.0261 | 0.53101 | 57.9071 | -64.3936 | 58.0811 | 58.2001 | 58.0032 | 0.31128 | -0.068665 | -0.086975 | -0.004577 | 122.4152 | 122.4152 | 122.2137 | 122.4838 | 122.2824 | -0.004578 | -0.027466 | 0.14648 | 122.5891 | 64.7003 | 122.3923 | 64.7049 | 122.3969 | 122.4838 | 122.3877 | 122.5937 | 122.4747 | 122.3053 | 122.3007 | 122.2366 | 122.2961 | -122.3923 | -122.3282 | 122.319 | 122.4701 | 64.9155 | 64.92
1518.8906 | 122.4197 | -64.4165 | 57.9895 | -1.0065 | 0.054959 | 0.12025 | 3.5627 | -0.012988 | 0.63689 | -0.016143 | -0.15286 | 0.15391 | 0.11662 | -0.01298 | 0.051979 | 0.093892 | -0.0042127 | 0.54932 | 57.2342 | -64.476 | 57.8659 | 57.9575 | 57.756 | 57.962 | 0.48523 | 57.8659 | -64.3616 | 58.0307 | 58.0765 | 57.9025 | 0.26093 | -0.059509 | -0.75531 | -0.1236 | 122.374 | 122.3785 | 122.1725 | 122.438 | 122.2321 | 0.054932 | -0.1236 | 0.041199 | 122.493 | 64.6774 | 122.319 | 64.6225 | 122.2641 | 122.4335 | 122.3419 | 122.438 | 122.3923 | 121.7102 | 122.2275 | 121.6507 | 122.2824 | -122.4655 | -122.3511 | 122.2824 | 122.4472 | 64.9658 | 64.9017
1519.8281 | 122.6349 | -64.4073 | 57.9163 | -0.78522 | 0.059018 | 0.12217 | 3.5991 | 0.0019653 | 0.64607 | 9.193e-05 | -0.064362 | 0.16437 | 0.12794 | -0.0063574 | 0.056251 | 0.1035 | 0.00070073 | 0.46234 | 57.843 | -64.476 | 57.8705 | 57.9758 | 57.7606 | 57.9803 | 0.57678 | 57.9391 | -64.4257 | 58.0078 | 58.1131 | 57.8934 | 0.21515 | -0.068664 | -0.073242 | -0.045777 | 122.3831 | 122.3877 | 122.168 | 122.4564 | 122.2366 | -0.01831 | 0.022888 | 0.091552 | 122.5204 | 64.6225 | 122.3007 | 64.6408 | 122.319 | 122.4518 | 122.3465 | 122.5388 | 122.4335 | 122.319 | 122.3648 | 122.2504 | 122.3465 | -122.3923 | -122.3419 | 122.2778 | 122.4152 | 64.8697 | 64.9841
1520.8906 | 122.5708 | -64.4028 | 58.0078 | -0.80048 | 0.053891 | 0.12153 | 3.5726 | -0.0046569 | 0.63646 | -0.0041807 | -0.1254 | 0.16053 | 0.1241 | -0.0069982 | 0.059242 | 0.09731 | -0.0025037 | 0.52185 | 57.6782 | -64.4943 | 57.8522 | 57.9208 | 57.756 | 57.9575 | 0.44861 | 57.9346 | -64.4302 | 57.9666 | 58.1039 | 57.8888 | 0.27466 | -0.091553 | -0.32959 | -0.15564 | 122.3236 | 122.3602 | 122.1588 | 122.4518 | 122.2504 | -0.027466 | -0.073242 | -0.041198 | 122.5067 | 64.6774 | 122.2916 | 64.7049 | 122.319 | 122.4152 | 122.3465 | 122.5342 | 122.3969 | 122.1725 | 122.3648 | 122.081 | 122.3373 | -122.5021 | -122.438 | 122.2549 | 122.3694 | 64.9246 | 64.8514
1521.8281 | 122.7081 | -64.3662 | 57.9437 | -0.81574 | 0.060727 | 0.12068 | 3.5969 | -0.00038451 | 0.64565 | -0.00097627 | -0.042999 | 0.16373 | 0.12751 | -0.004862 | 0.05796 | 0.10543 | 0.00070073 | 0.5127 | 57.8476 | -64.444 | 57.9254 | 58.0307 | 57.8339 | 58.0261 | 0.52185 | 57.8567 | -64.4073 | 58.0627 | 58.1635 | 57.9895 | 0.29755 | -0.07782 | -0.096131 | -0.018311 | 122.3969 | 122.3923 | 122.2 | 122.4701 | 122.2778 | -0.041199 | -0.086976 | 0.11902 | 122.5296 | 64.6637 | 122.3557 | 64.7049 | 122.3969 | 122.4747 | 122.3694 | 122.5708 | 122.4701 | 122.2916 | 122.2641 | 122.2137 | 122.2229 | -122.3877 | -122.3511 | 122.2916 | 122.4289 | 64.8788 | 64.888
1522.8906 | 122.5937 | -64.444 | 57.962 | -1.2506 | 0.050046 | 0.1194 | 3.5604 | -0.0074341 | 0.63432 | -0.015075 | -0.15897 | 0.16202 | 0.12367 | 0.0026148 | 0.058815 | 0.10479 | -0.0029309 | 0.44861 | 57.2525 | -64.5355 | 57.7744 | 57.8522 | 57.6416 | 57.8659 | 0.11902 | 57.8751 | -64.4989 | 58.0032 | 57.9895 | 57.7972 | 0.15106 | -0.091552 | -0.70953 | -0.18768 | 122.2961 | 122.3099 | 122.0856 | 122.4014 | 122.1771 | -0.054931 | -0.086975 | 0.041199 | 122.4335 | 64.595 | 122.2412 | 64.65 | 122.2961 | 122.3877 | 122.3099 | 122.4884 | 122.5021 | 121.788 | 122.374 | 121.6965 | 122.319 | -122.4976 | -122.4609 | 122.2183 | 122.4472 | 64.8926 | 64.563
1523.8281 | 122.6486 | -64.4028 | 57.9391 | -0.81574 | 0.059659 | 0.12217 | 3.5976 | 0.0028199 | 0.645 | -0.00033547 | -0.07962 | 0.16694 | 0.12559 | -0.0033666 | 0.056678 | 0.10372 | 0.0015551 | 0.54474 | 57.8156 | -64.4531 | 57.8934 | 58.017 | 57.7698 | 57.9895 | 0.46234 | 57.8613 | -64.4348 | 58.0399 | 58.1223 | 57.9254 | 0.19684 | -0.050354 | -0.1236 | -0.045776 | 122.4197 | 122.3923 | 122.1725 | 122.4426 | 122.2229 | -0.032043 | -0.07782 | 0.10071 | 122.525 | 64.5996 | 122.3282 | 64.6317 | 122.3602 | 122.4701 | 122.3465 | 122.5571 | 122.4747 | 122.2687 | 122.2961 | 122.2183 | 122.2641 | -122.3923 | -122.374 | 122.2961 | 122.4426 | 64.9475 | 64.8651
1524.8906 | 122.58 | -64.4257 | 57.9483 | -0.81574 | 0.05795 | 0.1226 | 3.5709 | 0.0019653 | 0.64159 | -0.0018307 | -0.16507 | 0.16502 | 0.12645 | -0.0018712 | 0.056678 | 0.10457 | -0.0020765 | 0.47607 | 57.4631 | -64.5447 | 57.8476 | 57.9437 | 57.6279 | 57.8979 | 0.3067 | 57.9208 | -64.4485 | 57.9529 | 58.017 | 57.8156 | 0.1236 | -0.11902 | -0.48523 | -0.10071 | 122.3694 | 122.3236 | 122.0535 | 122.4426 | 122.1725 | -0.022888 | -0.027466 | 0.004578 | 122.4426 | 64.5493 | 122.2412 | 64.5721 | 122.2641 | 122.4884 | 122.3923 | 122.4655 | 122.4014 | 122.0078 | 122.3694 | 121.8887 | 122.3465 | -122.493 | -122.3969 | 122.2733 | 122.3785 | 64.9017 | 64.7324
1525.8281 | 122.612 | -64.3982 | 57.93 | -0.78522 | 0.059659 | 0.12281 | 3.5929 | 0.00068369 | 0.64415 | -0.00054907 | -0.046051 | 0.16373 | 0.1288 | -0.0046484 | 0.057319 | 0.10415 | -0.0016493 | 0.45319 | 57.8384 | -64.4852 | 57.8476 | 57.9529 | 57.7469 | 57.962 | 0.3891 | 57.8751 | -64.4119 | 58.0032 | 58.0811 | 57.8934 | 0.16937 | -0.086975 | -0.091553 | -0.082398 | 122.3511 | 122.3602 | 122.1451 | 122.4472 | 122.2321 | -0.013733 | -0.054932 | 0.073242 | 122.4792 | 64.5676 | 122.2916 | 64.5813 | 122.3053 | 122.438 | 122.3328 | 122.493 | 122.4152 | 122.3236 | 122.287 | 122.2366 | 122.2733 | -122.4152 | -122.3419 | 122.2458 | 122.4014 | 64.8514 | 64.7873
1526.8906 | 122.5662 | -62.7136 | 59.729 | -0.2359 | -0.0052829 | -0.0062143 | 2.9133 | -0.0010253 | 0.0013586 | -0.0014035 | -0.16202 | 0.16544 | 0.12645 | -0.0046484 | 0.056678 | 0.10222 | 0.0021961 | -0.050354 | 0.11902 | -0.16022 | -0.11902 | -0.027466 | -0.13733 | -0.059509 | 0.3479 | 59.6512 | -62.6495 | 59.6558 | 59.7519 | 59.5642 | 0.13733 | 62.5534 | -59.61 | -59.848 | 62.6862 | 62.6541 | 62.5763 | 0.10071 | 0.022888 | 0.064087 | -0.07782 | -0.073242 | 122.4655 | 62.851 | 122.2778 | 62.7869 | 122.2137 | 0.13275 | 0.041198 | 122.4014 | 122.3053 | 0.27924 | 122.3007 | 62.8326 | 122.3648 | -59.8892 | -122.3785 | 62.5946 | 122.3694 | 62.6633 | 63.0615
1527.8281 | 122.6852 | -62.6999 | 59.6878 | -0.022278 | -0.0022923 | -0.0081369 | 2.9078 | 0.0023925 | 0.002213 | -0.0018307 | -0.082672 | 0.16245 | 0.12602 | -0.0087072 | 0.057106 | 0.10564 | -0.00058107 | -0.059509 | 0.045776 | -0.16479 | -0.082397 | 0.032043 | -0.082397 | -0.018311 | 0.42572 | 59.6054 | -62.6999 | 59.7565 | 59.8251 | 59.6695 | 0.18768 | 62.5351 | -59.642 | -59.7702 | 62.7319 | 62.6816 | 62.6175 | 0.14648 | 0.082398 | 0 | -0.082397 | 0.068665 | 122.525 | 62.8876 | 122.3694 | 62.8876 | 122.3694 | 0.19684 | 0.082398 | 122.525 | 122.4564 | 0.21057 | 122.3053 | 62.7457 | 122.3053 | -59.8526 | -122.3877 | 62.6175 | 122.4564 | 62.6404 | 63.1256
1528.8906 | 122.5983 | -62.7136 | 59.7427 | 0.038757 | -0.00079686 | -0.0096323 | 2.9099 | -0.0014527 | -0.00077756 | -0.0035397 | -0.10709 | 0.16138 | 0.12751 | -0.0074254 | 0.059028 | 0.10073 | -0.00036747 | -0.004578 | 0.19226 | -0.07782 | -0.032043 | 0.07782 | 0.009155 | 0.041199 | 0.48065 | 59.729 | -62.709 | 59.7382 | 59.6283 | 59.6649 | 0.29755 | 62.6358 | -59.5505 | -59.7748 | 62.7914 | 62.7548 | 62.7228 | 0.11902 | 0.086975 | 0.004578 | -0.013733 | -0.004578 | 122.3419 | 63.0112 | 122.3785 | 63.0066 | 122.374 | 0.15564 | 0.045777 | 122.3373 | 122.4472 | 0.27008 | 122.438 | 62.9059 | 122.4426 | -59.8206 | -122.4518 | 62.6816 | 122.4518 | 62.709 | 63.1943
1529.8281 | 122.7219 | -62.6816 | 59.729 | -0.060425 | -0.0029331 | -0.0087777 | 2.9084 | 0.0023925 | 7.6842e-05 | -0.0033261 | -0.06131 | 0.16181 | 0.12751 | 5.1352e-05 | 0.056038 | 0.10222 | -0.0014355 | -0.068665 | 0.032043 | -0.1236 | -0.068665 | 0.009155 | -0.082397 | 0 | 0.40741 | 59.6466 | -62.7045 | 59.7519 | 59.8389 | 59.6695 | 0.18768 | 62.558 | -59.697 | -59.7977 | 62.6907 | 62.6816 | 62.5992 | 0.1236 | 0.041199 | -0.022888 | -0.082398 | 0.022888 | 122.5204 | 62.8693 | 122.3511 | 62.8922 | 122.374 | 0.13275 | 0.054931 | 122.5433 | 122.4564 | 0.15564 | 122.3511 | 62.7136 | 122.3282 | -59.8526 | -122.4335 | 62.6129 | 122.4335 | 62.6129 | 63.089
1530.8906 | 122.5616 | -62.709 | 59.7702 | 0.00061049 | -0.0010105 | -0.0070687 | 2.9095 | 0.0051697 | 0.002213 | -0.0018307 | -0.16507 | 0.16181 | 0.12709 | -0.012125 | 0.056678 | 0.09731 | -0.0044263 | -0.059509 | 0.086975 | -0.16022 | -0.1236 | -0.041199 | -0.14648 | -0.068665 | 0.37537 | 59.6832 | -62.7319 | 59.697 | 59.7519 | 59.5825 | 0.13275 | 62.5488 | -59.6832 | -59.8938 | 62.6678 | 62.6404 | 62.5626 | 0.091552 | 0.013733 | -0.022889 | -0.086975 | -0.073243 | 122.4609 | 62.8418 | 122.2916 | 62.8647 | 122.3145 | 0.11902 | 0.036621 | 122.4838 | 122.4289 | 0.24719 | 122.4152 | 62.796 | 122.3923 | -59.9304 | -122.5021 | 62.5854 | 122.406 | 62.6495 | 63.0844
1531.8281 | 122.6852 | -62.6953 | 59.7198 | -0.037537 | -0.0022923 | -0.0081369 | 2.9091 | -0.0046569 | 0.00093144 | -0.0067441 | -0.076569 | 0.16224 | 0.12538 | -0.0033666 | 0.056678 | 0.10415 | -0.0037855 | -0.050354 | 0.013733 | -0.14648 | -0.07782 | 0.041199 | -0.091553 | -0.009155 | 0.43945 | 59.642 | -62.7274 | 59.7794 | 59.8526 | 59.6786 | 0.16937 | 62.5488 | -59.7061 | -59.7977 | 62.7365 | 62.6862 | 62.6038 | 0.13733 | 0.054931 | -0.032044 | -0.07782 | 0.059509 | 122.5479 | 62.8647 | 122.374 | 62.8967 | 122.406 | 0.18768 | 0.068664 | 122.58 | 122.5067 | 0.16022 | 122.3694 | 62.709 | 122.3373 | -59.8663 | -122.4472 | 62.6175 | 122.4747 | 62.645 | 63.1348
1532.8906 | 122.6807 | -62.7136 | 59.7656 | 0.015869 | -0.0027195 | -0.0089913 | 2.9097 | 0.0015381 | 0.0015722 | -0.0026853 | -0.14066 | 0.1648 | 0.12815 | -0.0087072 | 0.057106 | 0.10585 | -0.0035719 | 0.004578 | 0.16479 | -0.1236 | -0.027466 | 0.032043 | -0.018311 | 0.022888 | 0.46234 | 59.7473 | -62.7274 | 59.7427 | 59.8572 | 59.6741 | 0.25177 | 62.59 | -59.6008 | -59.7931 | 62.7457 | 62.7365 | 62.6953 | 0.14648 | 0.10528 | -0.013733 | -0.018311 | -0.022888 | 122.5708 | 62.9654 | 122.3877 | 62.9791 | 122.4014 | 0.15564 | 0.09613 | 122.5845 | 122.4701 | 0.28839 | 122.4747 | 62.8784 | 122.4609 | -59.8892 | -122.493 | 62.6862 | 122.4564 | 62.7182 | 63.176
1533.8281 | 122.731 | -62.7182 | 59.7244 | -0.029907 | -0.00036966 | -0.0060007 | 2.9069 | -0.0012391 | 0.00071784 | -0.0014035 | -0.07962 | 0.16202 | 0.12986 | -0.0074254 | 0.057747 | 0.10436 | -0.00036747 | -0.045776 | 0.022888 | -0.13733 | -0.036621 | 0.050354 | -0.054932 | -0.013733 | 0.4715 | 59.6512 | -62.7274 | 59.7977 | 59.8846 | 59.6924 | 0.1831 | 62.5809 | -59.7015 | -59.761 | 62.7686 | 62.7045 | 62.6633 | 0.1236 | 0.082397 | -0.009155 | -0.073242 | 0.073242 | 122.6028 | 62.9013 | 122.4106 | 62.9105 | 122.4197 | 0.18768 | 0.10071 | 122.612 | 122.525 | 0.16022 | 122.3785 | 62.7411 | 122.3694 | -59.8618 | -122.4518 | 62.6816 | 122.5159 | 62.6724 | 63.1897
1534.8906 | 122.7036 | -62.7136 | 59.7885 | 0.015869 | 5.7742e-05 | -0.0077097 | 2.908 | -0.00017091 | -0.00035036 | -0.0024717 | -0.067413 | 0.16181 | 0.12666 | -0.0010168 | 0.057533 | 0.10521 | -0.0016493 | 0.054932 | 0.13733 | -0.050354 | 0.022888 | 0.13275 | 0.054932 | 0.091553 | 0.55847 | 59.7153 | -62.7319 | 59.7702 | 59.8846 | 59.697 | 0.27008 | 62.6633 | -59.6512 | -59.7656 | 62.8464 | 62.8052 | 62.7686 | 0.14191 | 0.10529 | -0.018311 | -0.073242 | -0.01831 | 122.5983 | 62.9837 | 122.4106 | 63.002 | 122.4289 | 0.18311 | 0.073242 | 122.6166 | 122.5021 | 0.18768 | 122.4472 | 62.851 | 122.4289 | -59.8389 | -122.5204 | 62.7365 | 122.4838 | 62.7686 | 63.2721
1535.8281 | 122.7493 | -62.709 | 59.7565 | -0.060425 | -0.0022923 | -0.0092051 | 2.9082 | 0.00046989 | 0.0017858 | -0.0037533 | -0.064362 | 0.16331 | 0.12794 | -0.0061438 | 0.056465 | 0.1065 | -0.0010083 | -0.050354 | 0.013733 | -0.15106 | -0.068665 | 0.032043 | -0.073242 | -0.022888 | 0.41199 | 59.6649 | -62.7365 | 59.7839 | 59.8663 | 59.697 | 0.19684 | 62.558 | -59.7427 | -59.8251 | 62.7411 | 62.6862 | 62.6358 | 0.12817 | 0.07782 | -0.027466 | -0.091553 | 0.027466 | 122.5754 | 62.9059 | 122.406 | 62.9333 | 122.4335 | 0.18311 | 0.082397 | 122.6028 | 122.5204 | 0.16479 | 122.4014 | 62.7228 | 122.374 | -59.9075 | -122.493 | 62.6404 | 122.493 | 62.6587 | 63.121
1536.8906 | 122.699 | -62.7182 | 59.7794 | 0.015869 | -0.0027195 | -0.0087777 | 2.9073 | -0.0016663 | -0.0024866 | -0.0031125 | -0.1254 | 0.16459 | 0.12687 | -0.0012304 | 0.058815 | 0.099232 | -0.0012219 | 0.018311 | 0.19226 | -0.059509 | -0.036621 | 0.041199 | 0.004578 | 0.041199 | 0.48065 | 59.7382 | -62.7502 | 59.7839 | 59.8709 | 59.6924 | 0.27924 | 62.6587 | -59.5871 | -59.816 | 62.7594 | 62.7594 | 62.7228 | 0.10071 | 0.064087 | -0.032043 | -0.041199 | 0.004578 | 122.5891 | 62.9974 | 122.4106 | 63.0295 | 122.4426 | 0.10071 | 0.022888 | 122.6212 | 122.5342 | 0.25177 | 122.4884 | 62.9105 | 122.4564 | -59.8389 | -122.5296 | 62.6816 | 122.5021 | 62.7365 | 63.1989
1537.8438 | 122.6898 | -62.7274 | 59.8022 | 0.031128 | -0.0014377 | -0.0083505 | 2.9084 | -0.00038451 | 0.00071784 | -0.0014035 | -0.094879 | 0.1648 | 0.13008 | -0.0029394 | 0.057106 | 0.10393 | -0.0025037 | 0.004578 | 0.19684 | -0.045776 | -0.059509 | 0.53558 | 0.2655 | -0.19684 | 0.40741 | 59.7336 | -62.7594 | 59.7565 | 59.8389 | 59.6603 | 0.26093 | 62.6816 | -59.6054 | -59.8618 | 63.2629 | 62.5305 | 62.9929 | -0.15106 | 0.31128 | -0.032043 | -0.068664 | -0.045776 | 122.5662 | 62.9883 | 122.3877 | 63.0203 | 122.4197 | 0.58136 | -0.013733 | 122.5983 | 122.5159 | 0.24261 | 122.493 | 62.9242 | 122.4609 | -59.848 | -122.5616 | 62.6678 | 122.4838 | 62.7319 | 63.1348
1538.8906 | 122.7219 | -62.7457 | 59.8068 | -0.060425 | -0.0025059 | -0.0081369 | 2.9067 | -0.0048705 | 0.00071784 | -0.00033547 | -0.15591 | 0.1616 | 0.12837 | 0.001974 | 0.058815 | 0.093892 | -0.0027173 | 0.009155 | 0.12817 | -0.086975 | -0.027466 | 0.068665 | -0.036621 | 0.009155 | 0.52643 | 59.7061 | -62.7594 | 59.8114 | 59.8984 | 59.6924 | 0.2655 | 62.6587 | -59.6786 | -59.8343 | 62.8143 | 62.7548 | 62.709 | 0.09613 | 0.050354 | -0.013732 | -0.10071 | 0.004577 | 122.644 | 63.0112 | 122.4381 | 63.0249 | 122.4518 | 0.15564 | 0.059509 | 122.6578 | 122.5708 | 0.21515 | 122.4655 | 62.8738 | 122.4518 | -59.8938 | -122.5662 | 62.7182 | 122.5571 | 62.7548 | 63.2721
1539.8281 | 122.7722 | -62.7274 | 59.7519 | -0.029907 | -0.0014377 | -0.0083505 | 2.9071 | 0.0019653 | 0.0013586 | -0.0022581 | -0.076569 | 0.16267 | 0.1258 | -0.0072118 | 0.059028 | 0.105 | 0.0011279 | -0.032043 | 0.018311 | -0.14648 | -0.068665 | 0.050354 | -0.086975 | -0.013733 | 0.43488 | 59.6466 | -62.764 | 59.7977 | 59.8846 | 59.7015 | 0.1831 | 62.5809 | -59.7336 | -59.8206 | 62.7777 | 62.7136 | 62.6404 | 0.13275 | 0.059509 | -0.036621 | -0.10529 | 0.045776 | 122.612 | 62.9105 | 122.4289 | 62.9471 | 122.4655 | 0.19684 | 0.077819 | 122.6486 | 122.5616 | 0.16479 | 122.4106 | 62.7457 | 122.374 | -59.8984 | -122.5159 | 62.6587 | 122.525 | 62.6953 | 63.1622
1540.8906 | 122.6715 | -62.7457 | 59.7977 | -0.007019 | -0.00036966 | -0.0087777 | 2.9082 | -0.0040161 | -0.00099116 | -0.00097627 | -0.094879 | 0.16181 | 0.12751 | -0.0067846 | 0.056892 | 0.10543 | 0.0041187 | 0 | 0.1831 | -0.068665 | -0.032043 | 0.050354 | -0.009155 | 0.032043 | 0.44861 | 59.7656 | -62.764 | 59.6512 | 59.8251 | 59.6603 | 0.26093 | 62.677 | -59.6146 | -59.8297 | 62.796 | 62.7777 | 62.7365 | 0.10071 | 0.05951 | -0.01831 | -0.032043 | -0.14648 | 122.5708 | 63.0066 | 122.406 | 63.0249 | 122.4243 | 0.11902 | 0.036622 | 122.5891 | 122.4152 | 0.25177 | 122.5296 | 62.9288 | 122.5113 | -59.8663 | -122.5616 | 62.7136 | 122.3969 | 62.7457 | 63.1943
1541.8281 | 122.8271 | -62.7136 | 59.7565 | -0.037537 | -0.0018649 | -0.0077097 | 2.9063 | -0.00059811 | 0.001145 | -0.0026853 | -0.018585 | 0.16117 | 0.12901 | -0.0076392 | 0.058815 | 0.10329 | 0.00048713 | 0.009155 | 0.082397 | -0.086975 | -0.009155 | 0.11444 | 0.018311 | 0.082397 | 0.55389 | 59.6741 | -62.7457 | 59.8572 | 59.9762 | 59.7977 | 0.33417 | 62.6266 | -59.6741 | -59.7656 | 62.8281 | 62.796 | 62.7319 | 0.16937 | 0.10529 | -0.032044 | -0.082398 | 0.10071 | 122.6898 | 63.0478 | 122.5113 | 63.0798 | 122.5433 | 0.20142 | 0.07782 | 122.7219 | 122.6028 | 0.16937 | 122.4197 | 62.796 | 122.3877 | -59.8434 | -122.5021 | 62.7045 | 122.5708 | 62.7228 | 63.2675
1542.9062 | 122.7997 | -62.6999 | 59.7702 | -0.068054 | -0.0016513 | -0.0083505 | 2.9067 | -0.0018799 | 0.001145 | -0.0052487 | -0.06131 | 0.16373 | 0.12858 | -0.003153 | 0.055397 | 0.10436 | -0.00058107 | 0.013733 | 0.086975 | -0.068665 | 0.036621 | 0.15564 | 0.059509 | 0.086975 | 0.57678 | 59.6878 | -62.7411 | 59.8755 | 59.9762 | 59.8297 | 0.33417 | 62.6312 | -59.6832 | -59.7336 | 62.8555 | 62.7869 | 62.7594 | 0.15564 | 0.12817 | -0.041199 | -0.082398 | 0.10528 | 122.6761 | 63.0341 | 122.5296 | 63.0753 | 122.5708 | 0.22431 | 0.10529 | 122.7173 | 122.6166 | 0.15564 | 122.4289 | 62.7869 | 122.3877 | -59.8389 | -122.5113 | 62.7365 | 122.5754 | 62.7136 | 63.2767
1543.8281 | 122.7493 | -62.7182 | 59.7565 | -0.037537 | 0.00027134 | -0.0068551 | 2.9069 | -0.00081171 | -0.0027002 | -0.0018307 | -0.11014 | 0.16288 | 0.12602 | -0.0042212 | 0.057319 | 0.10286 | 0.0019823 | -0.032043 | 0.018311 | -0.14191 | -0.041199 | 0.041199 | -0.07782 | -0.032043 | 0.48523 | 59.6832 | -62.7548 | 59.8251 | 59.8938 | 59.7244 | 0.17853 | 62.5763 | -59.7382 | -59.7977 | 62.7594 | 62.6862 | 62.6404 | 0.10986 | 0.064087 | -0.036621 | -0.073242 | 0.068664 | 122.612 | 62.8967 | 122.4426 | 62.9333 | 122.4792 | 0.18311 | 0.10071 | 122.6486 | 122.58 | 0.16022 | 122.4381 | 62.7365 | 122.4014 | -59.8984 | -122.5113 | 62.677 | 122.5433 | 62.6862 | 63.2034
1544.8906 | 122.7356 | -62.7548 | 59.8251 | -0.14435 | -0.0018649 | -0.0074961 | 2.9084 | -0.0033753 | 0.001145 | -0.00097627 | -0.1254 | 0.16502 | 0.12645 | -0.0022986 | 0.057319 | 0.105 | -0.0027173 | 0.018311 | 0.2243 | -0.009155 | -0.032043 | 0.032043 | -0.041199 | 0.018311 | 0.45776 | 59.7382 | -62.7548 | 59.7748 | 59.8526 | 59.6832 | 0.26093 | 62.7457 | -59.6008 | -59.8572 | 62.7869 | 62.7731 | 62.7136 | 0.027466 | -0.032044 | 0 | -0.086975 | -0.050354 | 122.6074 | 63.0157 | 122.4381 | 63.0157 | 122.4381 | 0.041198 | -0.022888 | 122.6074 | 122.5296 | 0.23346 | 122.493 | 62.9791 | 122.493 | -59.8343 | -122.58 | 62.7228 | 122.5296 | 62.7731 | 63.2126
1545.8281 | 122.7631 | -62.7274 | 59.7748 | -0.075684 | 0.00027134 | -0.0079233 | 2.9069 | -0.0012391 | -0.00035036 | -0.00033547 | -0.06131 | 0.16032 | 0.12986 | -0.0044348 | 0.056678 | 0.10436 | -0.00058107 | -0.059509 | 0.022888 | -0.12817 | -0.086975 | 0.018311 | -0.086975 | -0.032043 | 0.41657 | 59.6741 | -62.7823 | 59.8022 | 59.8801 | 59.7198 | 0.17395 | 62.5992 | -59.7519 | -59.8618 | 62.7457 | 62.6953 | 62.6404 | 0.096131 | 0.041199 | -0.054932 | -0.10071 | 0.027466 | 122.6074 | 62.9013 | 122.4472 | 62.9562 | 122.5021 | 0.14649 | 0.041199 | 122.6624 | 122.5845 | 0.15106 | 122.4564 | 62.7502 | 122.4014 | -59.903 | -122.5571 | 62.6404 | 122.5296 | 62.6678 | 63.1439
1546.8906 | 122.7585 | -62.7319 | 59.7931 | 0.046386 | -0.00058326 | -0.0087777 | 2.9069 | 0.0011109 | -0.00099116 | -0.0011899 | -0.14676 | 0.16437 | 0.1273 | -0.0055028 | 0.057106 | 0.098378 | -0.0037855 | 0 | 0.17395 | -0.050354 | -0.009155 | 0.054932 | 0.004578 | 0.022888 | 0.50812 | 59.7473 | -62.7502 | 59.816 | 59.9075 | 59.7015 | 0.30212 | 62.6816 | -59.6191 | -59.8022 | 62.7869 | 62.7548 | 62.7365 | 0.073242 | 0.054932 | -0.01831 | -0.045777 | 0.022888 | 122.6395 | 63.0341 | 122.4335 | 63.0524 | 122.4518 | 0.10529 | 0.041199 | 122.6578 | 122.5662 | 0.2243 | 122.4976 | 62.9059 | 122.4792 | -59.8434 | -122.5433 | 62.7228 | 122.5479 | 62.7319 | 63.2401
1547.8438 | 122.7585 | -62.7228 | 59.816 | -0.045166 | -0.0010105 | -0.0092051 | 2.9073 | -0.0016663 | -0.00077756 | -0.0020443 | -0.067413 | 0.16117 | 0.12623 | -0.0076392 | 0.05796 | 0.10393 | -0.0012219 | 0.073242 | 0.10071 | -0.054932 | 0.022888 | 0.1236 | 0.064087 | 0.091553 | 0.55389 | 59.729 | -62.7411 | 59.8251 | 59.9213 | 59.7336 | 0.3067 | 62.6678 | -59.7153 | -59.7931 | 62.8464 | 62.8143 | 62.7869 | 0.14649 | 0.11902 | -0.018311 | -0.086975 | 0.009155 | 122.644 | 63.0295 | 122.4564 | 63.0478 | 122.4747 | 0.17853 | 0.07782 | 122.6624 | 122.5662 | 0.15564 | 122.4701 | 62.8235 | 122.4518 | -59.8709 | -122.5571 | 62.7457 | 122.5479 | 62.796 | 63.2767
1548.8281 | 122.8455 | -62.7136 | 59.7565 | -0.022278 | -0.0020785 | -0.0087777 | 2.9091 | 0.0013245 | 0.00029044 | -0.0011899 | -0.12234 | 0.16267 | 0.12687 | 0.001333 | 0.058387 | 0.10521 | 0.0032641 | -0.045776 | -0.032043 | -0.16479 | -0.054932 | 0.032043 | -0.07782 | -0.036621 | 0.46234 | 59.6649 | -62.7594 | 59.8572 | 59.935 | 59.761 | 0.19226 | 62.5488 | -59.7885 | -59.8114 | 62.7457 | 62.677 | 62.6358 | 0.12817 | 0.086975 | -0.045776 | -0.091553 | 0.10071 | 122.6486 | 62.9059 | 122.4747 | 62.9517 | 122.5204 | 0.19684 | 0.10986 | 122.6944 | 122.6166 | 0.13275 | 122.4243 | 62.6816 | 122.3785 | -59.9213 | -122.5159 | 62.6587 | 122.5708 | 62.6678 | 63.176
1549.8906 | 122.7448 | -62.7594 | 59.8068 | 0.00824 | -0.0022923 | -0.0081369 | 2.908 | -0.0016663 | 0.001145 | 0.00073273 | -0.1315 | 0.16331 | 0.12687 | -0.003794 | 0.056892 | 0.10051 | -0.0014355 | 0.009155 | 0.16022 | -0.045776 | -0.027466 | 0.064087 | 0.013733 | 0.022888 | 0.47607 | 59.7565 | -62.7594 | 59.8206 | 59.903 | 59.7153 | 0.28381 | 62.7136 | -59.6466 | -59.8343 | 62.8235 | 62.7823 | 62.7731 | 0.068664 | 0.059509 | 0 | -0.050354 | 0.013733 | 122.6624 | 63.0432 | 122.4747 | 63.0432 | 122.4747 | 0.10986 | 0.01831 | 122.6624 | 122.58 | 0.20599 | 122.5159 | 62.9196 | 122.5159 | -59.8526 | -122.5662 | 62.7319 | 122.58 | 62.7686 | 63.2355
1550.8281 | 122.8134 | -62.7365 | 59.7519 | -0.052796 | -0.0031467 | -0.0074961 | 2.9071 | 0.0038879 | 0.00071784 | -0.0026853 | -0.10098 | 0.16288 | 0.12559 | -0.0093482 | 0.057533 | 0.10457 | -0.0050671 | 0.082397 | -0.027466 | -0.16022 | -0.022888 | 0.050354 | -0.064087 | 0.009155 | 0.48065 | 59.6832 | -62.7548 | 59.8434 | 59.9396 | 59.7336 | 0.19226 | 62.5763 | -59.7794 | -59.7748 | 62.7869 | 62.7457 | 62.6724 | 0.16937 | 0.09613 | -0.018311 | -0.068664 | 0.091553 | 122.6761 | 62.9288 | 122.4701 | 62.9471 | 122.4884 | 0.21057 | 0.13733 | 122.6944 | 122.5983 | 0.13275 | 122.4381 | 62.709 | 122.4197 | -59.9121 | -122.5067 | 62.7136 | 122.58 | 62.8189 | 63.2172
1551.8906 | 122.7081 | -62.7914 | 59.7931 | -0.060425 | 0.00048494 | -0.0096323 | 2.8977 | -0.0025207 | -0.00035036 | -0.0041807 | -0.17117 | 0.16331 | 0.12452 | -0.0063574 | 0.05561 | 0.096241 | -0.0022901 | -0.064087 | 0.082397 | -0.10986 | -0.11444 | -0.041199 | -0.1236 | -0.059509 | 0.3891 | 59.7473 | -62.7777 | 59.7519 | 59.8389 | 59.6146 | 0.1236 | 62.6816 | -59.7107 | -59.9075 | 62.7502 | 62.7319 | 62.6678 | 0.050354 | -0.013733 | 0.013733 | -0.045777 | -0.041199 | 122.6303 | 62.915 | 122.406 | 62.9013 | 122.3923 | 0.068664 | -0.004578 | 122.6166 | 122.5296 | 0.19226 | 122.525 | 62.8738 | 122.5388 | -59.903 | -122.5708 | 62.677 | 122.5433 | 62.7274 | 63.1805
1552.8281 | 122.8592 | -62.7365 | 59.7748 | -0.037537 | -0.0025059 | -0.0072825 | 2.9054 | 0.0023925 | -0.0012048 | -0.0020443 | -0.058258 | 0.1616 | 0.12751 | -0.011912 | 0.058174 | 0.10671 | -0.00036747 | 0.045776 | 0.11444 | -0.059509 | 0.064087 | 0.18768 | 0.073242 | 0.10529 | 0.60883 | 59.7107 | -62.7457 | 59.7656 | 60.0998 | 59.7336 | 0.25177 | 62.677 | -59.6603 | -59.7107 | 62.9242 | 62.8418 | 62.8098 | 0.16479 | 0.13275 | -0.009156 | -0.064087 | -0.009155 | 122.8363 | 62.9883 | 122.4701 | 62.9974 | 122.4792 | 0.24719 | 0.1236 | 122.8455 | 122.5113 | 0.17395 | 122.4564 | 62.851 | 122.4472 | -59.8343 | -122.5204 | 62.8006 | 122.5021 | 62.7823 | 63.3453
1553.8906 | 122.7951 | -62.7228 | 59.816 | 0.046386 | -0.0020785 | -0.0072825 | 2.9012 | -0.0018799 | 0.00071784 | 0.0035099 | -0.15286 | 0.16395 | 0.12751 | -0.0042212 | 0.057533 | 0.091755 | 0.0026233 | -0.009155 | 0.12817 | -0.091553 | -0.032043 | 0.059509 | -0.018311 | 0.013733 | 0.53101 | 59.7473 | -62.764 | 59.816 | 59.903 | 59.7107 | 0.25635 | 62.6312 | -59.6878 | -59.848 | 62.7823 | 62.7365 | 62.7045 | 0.10529 | 0.073242 | -0.041199 | -0.068665 | 0 | 122.6257 | 62.9791 | 122.4335 | 63.0203 | 122.4747 | 0.15106 | 0.05951 | 122.6669 | 122.58 | 0.21973 | 122.5113 | 62.851 | 122.4701 | -59.9075 | -122.58 | 62.6907 | 122.5388 | 62.7136 | 63.2538
1554.8281 | 122.8409 | -62.7274 | 59.7656 | 0.023498 | -0.0020785 | -0.0074961 | 2.9063 | 0.0030335 | -0.00099116 | -0.0020443 | -0.076569 | 0.16416 | 0.12559 | -0.0074254 | 0.057106 | 0.10372 | 0.00091433 | -0.068665 | -0.032043 | -0.17395 | -0.045776 | 0.041199 | -0.050354 | -0.004578 | 0.46692 | 59.7107 | -62.7731 | 59.8755 | 59.9213 | 59.7427 | 0.17853 | 62.5534 | -59.7977 | -59.8114 | 62.7686 | 62.7228 | 62.677 | 0.16937 | 0.1236 | -0.045776 | -0.054932 | 0.10986 | 122.6486 | 62.9059 | 122.4701 | 62.9517 | 122.5159 | 0.21515 | 0.12817 | 122.6944 | 122.6486 | 0.14191 | 122.4838 | 62.6953 | 122.438 | -59.9396 | -122.5388 | 62.6816 | 122.6028 | 62.6587 | 63.1943
1555.8906 | 122.7219 | -62.7457 | 59.8343 | 0.023498 | -0.0035739 | -0.0098459 | 2.9069 | -0.0042297 | 0.001145 | -0.00097627 | -0.11014 | 0.16737 | 0.12559 | -0.0044348 | 0.057319 | 0.10628 | 0.0013415 | 0 | 0.16937 | -0.059509 | -0.091553 | 0.086975 | -0.16479 | -0.041199 | 0.44403 | 59.761 | -62.7686 | 59.7794 | 59.8801 | 59.697 | 0.27466 | 62.6862 | -59.6649 | -59.9258 | 62.8326 | 62.7045 | 62.5809 | 0.01831 | -0.10529 | -0.022888 | -0.073243 | -0.054932 | 122.6257 | 63.0203 | 122.4426 | 63.0432 | 122.4655 | 0.14648 | -0.032044 | 122.6486 | 122.5479 | 0.22888 | 122.5296 | 62.915 | 122.5067 | -59.8938 | -122.6028 | 62.6541 | 122.525 | 62.7457 | 63.1897
1556.8281 | 122.85 | -62.7502 | 59.761 | -0.037537 | -0.0016513 | -0.0051461 | 2.9048 | 0.0032471 | 0.0019994 | -0.0037533 | -0.10403 | 0.16117 | 0.12602 | -0.001444 | 0.057106 | 0.10457 | -0.0037855 | -0.045776 | -0.022888 | -0.15564 | -0.054932 | 0.041199 | -0.068665 | -0.009155 | 0.46234 | 59.6832 | -62.7869 | 59.8938 | 59.6832 | 59.7748 | 0.28839 | 62.5946 | -59.7839 | -59.816 | 62.7914 | 62.7411 | 62.6816 | 0.14649 | 0.086975 | -0.036621 | -0.077819 | 0.13275 | 122.4335 | 63.0386 | 122.525 | 63.0753 | 122.5616 | 0.19684 | 0.10071 | 122.4701 | 122.6807 | 0.13275 | 122.4701 | 62.7274 | 122.4335 | -59.9167 | -122.5479 | 62.6953 | 122.644 | 62.7045 | 63.2126
1557.9062 | 122.8363 | -62.7365 | 59.7656 | -0.007019 | -0.0025059 | -0.0096323 | 2.9039 | -0.0010253 | -0.0020594 | -0.0043943 | -0.042999 | 0.16437 | 0.12773 | -0.0063574 | 0.057533 | 0.105 | 0.00091433 | 0.054932 | 0.086975 | -0.07782 | -0.050354 | 0.041199 | -0.032043 | 0.018311 | 0.45319 | 59.7061 | -62.7777 | 59.8526 | 59.9258 | 59.7565 | 0.22888 | 62.6587 | -59.6786 | -59.816 | 62.7777 | 62.7548 | 62.7045 | 0.096131 | 0.045777 | -0.041199 | -0.059509 | 0.086975 | 122.6624 | 62.9654 | 122.493 | 63.0066 | 122.5342 | 0.11902 | 0.027466 | 122.7036 | 122.6303 | 0.16479 | 122.4838 | 62.8235 | 122.4426 | -59.8434 | -122.5433 | 62.6862 | 122.5891 | 62.7914 | 63.1897
1558.8281 | 122.8226 | -62.7411 | 59.761 | -0.022278 | -0.0025059 | -0.010487 | 2.9041 | -0.00081171 | 0.0019994 | 9.193e-05 | -0.058258 | 0.16245 | 0.12666 | -0.0029394 | 0.057533 | 0.10521 | -0.0042127 | -0.018311 | 0.064087 | -0.10529 | -0.1236 | 0.050354 | -0.082397 | 0.018311 | 0.45319 | 59.697 | -62.7594 | 59.8297 | 59.9258 | 59.7656 | 0.23346 | 62.6358 | -59.697 | -59.8846 | 62.7914 | 62.7594 | 62.6587 | 0.1236 | 0.022889 | -0.01831 | -0.064087 | 0.068665 | 122.6669 | 62.9745 | 122.5067 | 62.9929 | 122.525 | 0.15564 | -0.01831 | 122.6852 | 122.5891 | 0.16937 | 122.4564 | 62.8052 | 122.438 | -59.8663 | -122.5204 | 62.6175 | 122.5708 | 62.7228 | 63.1943
1559.8906 | 122.7768 | -62.7686 | 59.8022 | 0.023498 | -0.0018649 | -0.0083505 | 2.8926 | -0.0035889 | -0.0014184 | -0.0093075 | -0.11014 | 0.16032 | 0.12687 | -0.0057166 | 0.053688 | 0.1018 | 5.9726e-05 | -0.004578 | 0.10071 | -0.10071 | -0.050354 | 0.036621 | -0.1831 | -0.16022 | 0.48523 | 59.7519 | -62.7869 | 59.8206 | 59.8892 | 59.7107 | 0.2243 | 62.6678 | -59.7015 | -59.8526 | 62.8052 | 62.6083 | 62.5855 | -0.059509 | -0.082397 | -0.01831 | -0.050354 | 0.018311 | 122.6578 | 62.9929 | 122.4792 | 63.0112 | 122.4976 | 0.13733 | 0.050354 | 122.6761 | 122.6074 | 0.20142 | 122.5388 | 62.8693 | 122.5204 | -59.903 | -122.5891 | 62.7182 | 122.5891 | 62.764 | 63.2538
1560.8281 | 122.818 | -62.7686 | 59.7977 | -0.022278 | -0.00058326 | -0.0087777 | 2.9063 | 0.0015381 | 0.00071784 | -0.0016171 | -0.052155 | 0.16138 | 0.1305 | -0.014689 | 0.058601 | 0.10393 | -0.00036747 | -0.041199 | 0.050354 | -0.1236 | -0.073242 | 0.018311 | -0.059509 | 0.004578 | 0.43488 | 59.7198 | -62.7869 | 59.8297 | 59.9213 | 59.7382 | 0.21515 | 62.645 | -59.7473 | -59.8709 | 62.7869 | 62.7731 | 62.709 | 0.12817 | 0.064087 | -0.01831 | -0.077819 | 0.032044 | 122.6898 | 62.9837 | 122.5067 | 63.002 | 122.525 | 0.14191 | 0.050354 | 122.7081 | 122.6166 | 0.17395 | 122.5067 | 62.8189 | 122.4884 | -59.9213 | -122.5845 | 62.6953 | 122.5983 | 62.7274 | 63.2034
1561.8906 | 122.7448 | -62.7869 | 59.8068 | 0.00824 | -0.0016513 | -0.0087777 | 2.8973 | -0.0040161 | 0.00029044 | -0.0065305 | -0.16507 | 0.1616 | 0.12709 | -0.0095618 | 0.053474 | 0.092183 | -0.0044263 | -0.018311 | 0.07782 | -0.10986 | 0 | 0.045776 | -0.059509 | -0.004578 | 0.48981 | 59.7382 | -62.7914 | 59.8251 | 59.8755 | 59.6924 | 0.21057 | 62.677 | -59.729 | -59.8068 | 62.8326 | 62.7823 | 62.7274 | 0.10529 | 0.050354 | -0.004578 | -0.068665 | 0.01831 | 122.6624 | 62.9974 | 122.4792 | 63.002 | 122.4838 | 0.15564 | 0.10986 | 122.6669 | 122.6166 | 0.18768 | 122.5296 | 62.8647 | 122.525 | -59.9167 | -122.5983 | 62.7869 | 122.612 | 62.7686 | 63.2767
1562.8281 | 122.8592 | -62.7228 | 59.7702 | -0.037537 | -0.0025059 | -0.0074961 | 2.9063 | 0.00089729 | 7.6842e-05 | -0.00097627 | -0.039948 | 0.1648 | 0.12901 | 0.00090575 | 0.056465 | 0.10457 | -0.0014355 | -0.027466 | 0.07782 | -0.086975 | -0.041199 | 0.054932 | -0.022888 | 0.036621 | 0.48523 | 59.7198 | -62.7686 | 59.8526 | 59.9625 | 59.7931 | 0.27008 | 62.6358 | -59.6924 | -59.8114 | 62.7777 | 62.7594 | 62.6999 | 0.1236 | 0.064087 | -0.045777 | -0.050354 | 0.082397 | 122.6852 | 62.9929 | 122.5159 | 63.0386 | 122.5616 | 0.14191 | 0.045776 | 122.731 | 122.6212 | 0.16479 | 122.4884 | 62.8006 | 122.4426 | -59.8572 | -122.5388 | 62.6816 | 122.5754 | 62.6953 | 63.208
1563.8906 | 122.7722 | -62.7411 | 59.7977 | -0.029907 | 0.00048494 | -0.0072825 | 2.9014 | 0.00068369 | -0.0014184 | -0.0018307 | -0.13455 | 0.1616 | 0.12623 | -0.009989 | 0.056678 | 0.089833 | -0.00079467 | 0.013733 | 0.12817 | -0.073242 | -0.027466 | 0.059509 | -0.036621 | 0.013733 | 0.5127 | 59.7473 | -62.7777 | 59.8434 | 59.903 | 59.7107 | 0.27008 | 62.6678 | -59.6695 | -59.8251 | 62.8006 | 62.7548 | 62.7045 | 0.086975 | 0.036621 | -0.036621 | -0.050354 | 0.045777 | 122.644 | 63.0112 | 122.4518 | 63.0478 | 122.4884 | 0.13275 | 0.045776 | 122.6807 | 122.6212 | 0.20142 | 122.525 | 62.8693 | 122.4884 | -59.8709 | -122.5754 | 62.7136 | 122.5845 | 62.7548 | 63.2538
1564.8281 | 122.818 | -62.7594 | 59.7977 | -0.052796 | -0.0037875 | -0.0049325 | 2.9052 | -0.0014527 | -0.00077756 | -0.00097627 | -0.039948 | 0.16138 | 0.12474 | -0.0027258 | 0.056251 | 0.10372 | -0.0029309 | -0.045776 | 0.054932 | -0.11444 | -0.059509 | 0.041199 | -0.036621 | 0.018311 | 0.46692 | 59.7015 | -62.7548 | 59.8251 | 59.9258 | 59.7656 | 0.2243 | 62.645 | -59.7427 | -59.8572 | 62.8006 | 62.7777 | 62.7228 | 0.13275 | 0.07782 | 0.004577 | -0.09613 | 0.027466 | 122.6852 | 62.9837 | 122.525 | 62.9791 | 122.5204 | 0.15564 | 0.054932 | 122.6807 | 122.58 | 0.16937 | 122.4564 | 62.8143 | 122.4609 | -59.9121 | -122.5525 | 62.6999 | 122.5845 | 62.7136 | 63.2263
1565.8906 | 122.7859 | -62.7777 | 59.7977 | -0.022278 | 0.00091214 | -0.0068551 | 2.9052 | -0.00059811 | -0.00077756 | -0.00012167 | -0.15897 | 0.16224 | 0.12559 | -0.0016576 | 0.055824 | 0.10564 | -0.0016493 | -0.09613 | 0.045776 | -0.16937 | -0.14648 | -0.068665 | -0.1831 | -0.10529 | 0.37079 | 59.7336 | -62.8418 | 59.7931 | 59.8755 | 59.6695 | 0.14648 | 62.6083 | -59.7519 | -59.9442 | 62.709 | 62.6724 | 62.5946 | 0.064087 | -0.013732 | -0.064087 | -0.064086 | -0.004577 | 122.6532 | 62.9242 | 122.4472 | 62.9883 | 122.5113 | 0.10071 | 0.022889 | 122.7173 | 122.6349 | 0.21515 | 122.5754 | 62.8235 | 122.5113 | -59.967 | -122.6395 | 62.6312 | 122.5708 | 62.6816 | 63.1485
1566.8281 | 122.8821 | -62.7502 | 59.8022 | -0.037537 | -0.0022923 | -0.0083505 | 2.9048 | -0.00081171 | -0.00099116 | -0.0033261 | -0.033844 | 0.16288 | 0.12709 | -0.00080325 | 0.056465 | 0.10372 | -0.0027173 | 0.041199 | 0.091553 | -0.059509 | 0.064087 | 0.16937 | 0.068665 | 0.11444 | 0.6134 | 59.7198 | -62.7502 | 59.9121 | 60.022 | 59.8297 | 0.32501 | 62.6907 | -59.7107 | -59.7382 | 62.9196 | 62.8647 | 62.8189 | 0.17395 | 0.12817 | 0 | -0.082397 | 0.10986 | 122.7722 | 63.0753 | 122.58 | 63.0753 | 122.58 | 0.22888 | 0.1236 | 122.7722 | 122.6624 | 0.15106 | 122.4701 | 62.8418 | 122.4701 | -59.8618 | -122.5525 | 62.8143 | 122.6624 | 62.7914 | 63.3636
1567.8906 | 122.8638 | -62.7777 | 59.761 | -0.083313 | -0.00058326 | -0.0098459 | 2.9067 | -0.00081171 | 0.002854 | -0.0037533 | -0.070465 | 0.16267 | 0.1273 | -0.00016245 | 0.055824 | 0.10457 | -0.0050671 | -0.022888 | -0.013733 | -0.14191 | -0.068665 | 0.15564 | -0.032043 | -0.013733 | 0.45776 | 59.7061 | -62.7594 | 59.8663 | 59.9396 | 59.7702 | 0.18768 | 62.6358 | -59.7748 | -59.8297 | 62.9333 | 62.764 | 62.7457 | 0.12817 | 0.10986 | 0.018311 | -0.054931 | 0.10529 | 122.7173 | 62.9654 | 122.5479 | 62.9471 | 122.5296 | 0.29755 | 0.073242 | 122.699 | 122.6257 | 0.12817 | 122.4655 | 62.764 | 122.4838 | -59.903 | -122.5204 | 62.709 | 122.644 | 62.7548 | 63.2355
1568.8281 | 122.8775 | -62.7411 | 59.7977 | -0.022278 | -0.00079686 | -0.0094187 | 2.9029 | 0.00025629 | -0.00099116 | -0.0016171 | -0.042999 | 0.1648 | 0.12666 | -0.0050756 | 0.057533 | 0.10329 | -0.0012219 | 0.009155 | 0.07782 | -0.07782 | -0.009155 | 0.09613 | 0.013733 | 0.068665 | 0.54932 | 59.7382 | -62.7548 | 59.8801 | 59.9991 | 59.7794 | 0.3067 | 62.6633 | -59.7198 | -59.8068 | 62.8372 | 62.8098 | 62.7548 | 0.14649 | 0.091553 | -0.013733 | -0.059509 | 0.082398 | 122.7402 | 63.0478 | 122.5204 | 63.0615 | 122.5342 | 0.17395 | 0.068665 | 122.7539 | 122.6349 | 0.15564 | 122.493 | 62.8189 | 122.4792 | -59.8755 | -122.5525 | 62.7319 | 122.6212 | 62.7502 | 63.2904
1569.8906 | 122.8226 | -62.7823 | 59.7885 | -0.083313 | -0.0020785 | -0.0089913 | 2.9067 | 0.0034607 | 0.00093144 | -0.0031125 | -0.15591 | 0.16202 | 0.1258 | 0.0056056 | 0.057106 | 0.10564 | 0.0013415 | -0.091553 | 0.041199 | -0.16479 | -0.15106 | -0.068665 | -0.16479 | -0.09613 | 0.37537 | 59.7107 | -62.796 | 59.8206 | 59.8801 | 59.6924 | 0.16479 | 62.6175 | -59.7473 | -59.9396 | 62.7136 | 62.6862 | 62.6175 | 0.068665 | 0 | -0.013733 | -0.07782 | 0.032044 | 122.6624 | 62.9471 | 122.4747 | 62.9608 | 122.4884 | 0.09613 | 0.013733 | 122.6761 | 122.6166 | 0.20599 | 122.5067 | 62.8235 | 122.493 | -59.9533 | -122.5845 | 62.6312 | 122.6028 | 62.6907 | 63.1577
1570.8281 | 122.8638 | -62.7411 | 59.7839 | -0.045166 | -0.0042149 | -0.0092051 | 2.9056 | -0.0027343 | -0.00035036 | -0.0014035 | -0.052155 | 0.16117 | 0.12516 | -0.00828 | 0.058174 | 0.10201 | -0.00036747 | 0.013733 | 0.068665 | -0.086975 | 0 | 0.09613 | 0.018311 | 0.064087 | 0.52185 | 59.7153 | -62.7548 | 59.8846 | 59.9854 | 59.7931 | 0.31128 | 62.6541 | -59.7153 | -59.7839 | 62.8372 | 62.8052 | 62.7594 | 0.15106 | 0.10529 | -0.013733 | -0.068665 | 0.10071 | 122.7264 | 63.0524 | 122.5342 | 63.0661 | 122.5479 | 0.1831 | 0.086975 | 122.7402 | 122.6395 | 0.15564 | 122.4701 | 62.8098 | 122.4564 | -59.8709 | -122.5388 | 62.7411 | 122.6257 | 62.7548 | 63.2629
1571.8906 | 122.7951 | -62.7548 | 59.7656 | 0.00061049 | -0.00015586 | -0.0098459 | 2.9059 | 0.0026063 | 0.0015722 | -0.0014035 | -0.17422 | 0.16352 | 0.12666 | 0.0024012 | 0.059028 | 0.10607 | -0.0014355 | -0.091553 | 0.041199 | -0.17395 | -0.14191 | -0.064087 | -0.15564 | -0.091553 | 0.38452 | 59.7473 | -62.7914 | 59.8251 | 59.8709 | 59.7015 | 0.15106 | 62.5809 | -59.7244 | -59.9075 | 62.6907 | 62.6633 | 62.5992 | 0.082397 | 0.01831 | -0.036621 | -0.018311 | 0.059509 | 122.6257 | 62.9059 | 122.4564 | 62.9425 | 122.493 | 0.10986 | 0.032043 | 122.6624 | 122.6166 | 0.21515 | 122.5388 | 62.796 | 122.5021 | -59.9396 | -122.5571 | 62.6129 | 122.58 | 62.6633 | 63.1393
1572.8281 | 122.8958 | -62.7319 | 59.7885 | -0.052796 | -0.00079686 | -0.010059 | 2.9056 | -0.0023071 | -0.00056396 | -0.0026853 | -0.049103 | 0.16309 | 0.12794 | -0.003153 | 0.058387 | 0.10415 | 0.0026233 | 0.041199 | 0.086975 | -0.054932 | 0.059509 | 0.16937 | 0.064087 | 0.11444 | 0.63629 | 59.7336 | -62.7411 | 59.9075 | 60.0174 | 59.8297 | 0.33417 | 62.677 | -59.7015 | -59.729 | 62.9013 | 62.8464 | 62.796 | 0.16937 | 0.11902 | -0.009155 | -0.054931 | 0.11902 | 122.7493 | 63.0661 | 122.5616 | 63.0753 | 122.5708 | 0.22431 | 0.11444 | 122.7585 | 122.6486 | 0.14191 | 122.4747 | 62.8189 | 122.4655 | -59.8434 | -122.5296 | 62.7914 | 122.6395 | 62.7731 | 63.3682
1573.8906 | 122.8043 | -62.7914 | 59.7839 | -0.022278 | -0.0014377 | -0.0062143 | 2.9071 | 0.0023925 | -0.00077756 | -0.0022581 | -0.14981 | 0.16502 | 0.12815 | -0.002085 | 0.056678 | 0.10671 | -0.00079467 | -0.09613 | 0.045776 | -0.17395 | -0.14648 | -0.068665 | -0.17395 | -0.10071 | 0.38452 | 59.761 | -62.8189 | 59.8297 | 59.8846 | 59.6878 | 0.14191 | 62.6175 | -59.7382 | -59.9304 | 62.7228 | 62.6907 | 62.6175 | 0.073242 | 0 | -0.027466 | -0.022889 | 0.045776 | 122.6761 | 62.9334 | 122.4792 | 62.9608 | 122.5067 | 0.10528 | 0.027466 | 122.7036 | 122.6486 | 0.21973 | 122.58 | 62.8372 | 122.5525 | -59.9579 | -122.6028 | 62.645 | 122.6212 | 62.6953 | 63.176
1574.8281 | 122.8867 | -62.7457 | 59.7977 | -0.014649 | -0.0012241 | -0.0085641 | 2.9039 | 0.00025629 | -0.0027002 | -0.0020443 | -0.027741 | 0.16331 | 0.12709 | -0.00058965 | 0.058387 | 0.10415 | -0.0029309 | 0.041199 | 0.068665 | -0.064087 | 0.036621 | 0.19684 | 0.086975 | 0.10529 | 0.61798 | 59.7198 | -62.7731 | 59.9304 | 60.0174 | 59.8618 | 0.3479 | 62.6816 | -59.729 | -59.761 | 62.9425 | 62.851 | 62.8326 | 0.16937 | 0.15106 | -0.027465 | -0.077819 | 0.13275 | 122.7631 | 63.0936 | 122.6074 | 63.121 | 122.6349 | 0.26093 | 0.10071 | 122.7905 | 122.7036 | 0.13275 | 122.493 | 62.8143 | 122.4655 | -59.8618 | -122.5708 | 62.7823 | 122.6761 | 62.7869 | 63.3636
1575.8906 | 122.8455 | -62.7457 | 59.7702 | -0.029907 | -0.0014377 | -0.0068551 | 2.9046 | 0.0034607 | -0.00035036 | -0.0035397 | -0.11929 | 0.15797 | 0.13115 | -0.0016576 | 0.057106 | 0.10436 | -0.0039991 | -0.027466 | -0.018311 | -0.14191 | -0.045776 | 0.050354 | -0.068665 | -0.018311 | 0.24719 | 59.6649 | -62.7777 | 59.8984 | 59.9487 | 59.8022 | 0.22888 | 62.6038 | -59.7885 | -59.816 | 62.796 | 62.7274 | 62.677 | 0.1236 | 0.073242 | -0.032043 | -0.10529 | 0.12817 | 122.6944 | 62.9745 | 122.5479 | 63.0066 | 122.58 | 0.19226 | 0.096131 | 122.7264 | 122.6761 | 0.1236 | 122.4426 | 62.7274 | 122.4106 | -59.9121 | -122.5479 | 62.6999 | 122.644 | 62.7182 | 62.9929
1576.8281 | 122.8821 | -62.7411 | 59.7885 | 0.00061049 | -0.0020785 | -0.0081369 | 2.9033 | -0.0018799 | 0.0015722 | -0.0026853 | -0.027741 | 0.16331 | 0.12623 | -0.012125 | 0.057319 | 0.10521 | -0.0010083 | 0.022888 | 0.059509 | -0.07782 | 0.032043 | 0.14191 | 0.036621 | 0.11444 | 0.59509 | 59.7382 | -62.764 | 59.9258 | 60.0082 | 59.8389 | 0.32501 | 62.6633 | -59.729 | -59.7565 | 62.883 | 62.8555 | 62.7777 | 0.19226 | 0.11444 | -0.022888 | -0.050354 | 0.13733 | 122.7493 | 63.0661 | 122.58 | 63.089 | 122.6028 | 0.21973 | 0.10986 | 122.7722 | 122.6898 | 0.13733 | 122.5021 | 62.8006 | 122.4792 | -59.8663 | -122.5525 | 62.7731 | 122.6669 | 62.764 | 63.3362
1577.8906 | 122.8271 | -62.7686 | 59.7702 | -0.037537 | -0.00015586 | -0.0077097 | 2.9037 | -0.00059811 | 0.00071784 | -0.0016171 | -0.085724 | 0.16672 | 0.1258 | -0.0027258 | 0.05796 | 0.10201 | 0.0021961 | -0.041199 | 0.045776 | -0.11902 | -0.068665 | 0.036621 | -0.054932 | 0.009155 | 0.62256 | 59.761 | -62.7914 | 59.848 | 59.9258 | 59.7473 | 0.19684 | 62.6495 | -59.7244 | -59.8389 | 62.8052 | 62.7777 | 62.7136 | 0.12817 | 0.064087 | -0.022888 | -0.009156 | 0.077819 | 122.6944 | 62.9654 | 122.5159 | 62.9883 | 122.5388 | 0.15564 | 0.050354 | 122.7173 | 122.6395 | 0.16479 | 122.5525 | 62.8143 | 122.5296 | -59.8892 | -122.5616 | 62.6999 | 122.6166 | 62.7274 | 63.3911
1578.8281 | 122.85 | -62.7686 | 59.7977 | -0.090943 | 0.00069854 | -0.0094187 | 2.9052 | -0.0038025 | -0.002273 | -0.0024717 | -0.076569 | 0.16138 | 0.12837 | -0.0012304 | 0.059883 | 0.10308 | -0.0018629 | -0.041199 | 0.082397 | -0.091553 | -0.045776 | 0.050354 | -0.036621 | 0.032043 | 0.48981 | 59.729 | -62.7731 | 59.8572 | 59.9625 | 59.7794 | 0.27466 | 62.677 | -59.7153 | -59.8434 | 62.8189 | 62.8006 | 62.7319 | 0.1236 | 0.054932 | -0.004577 | -0.068664 | 0.05951 | 122.731 | 63.0432 | 122.5479 | 63.0478 | 122.5525 | 0.14191 | 0.045777 | 122.7356 | 122.6303 | 0.17395 | 122.5021 | 62.851 | 122.4976 | -59.8892 | -122.5708 | 62.7228 | 122.6257 | 62.7274 | 63.2584
1579.8906 | 122.8134 | -62.7457 | 59.8068 | -0.007019 | -0.00079686 | -0.0087777 | 2.9044 | -0.00038451 | 0.001145 | -0.00097627 | -0.067413 | 0.16224 | 0.1288 | 0.00090575 | 0.058174 | 0.10521 | -0.0025037 | -0.045776 | 0.027466 | -0.11444 | -0.054932 | 0.018311 | -0.059509 | 0.004578 | 0.43488 | 59.7198 | -62.7869 | 59.8389 | 60.0128 | 59.8206 | 0.33875 | 62.6312 | -59.7794 | -59.8618 | 62.764 | 62.7502 | 62.6862 | 0.11902 | 0.054932 | -0.041198 | -0.086975 | 0.032043 | 122.7585 | 63.0844 | 122.5662 | 63.1256 | 122.6074 | 0.13275 | 0.059509 | 122.7997 | 122.6257 | 0.14191 | 122.5067 | 62.7731 | 122.4655 | -59.9213 | -122.5937 | 62.6907 | 122.5845 | 62.6999 | 63.1805
1580.8281 | 122.8821 | -62.7365 | 59.7794 | -0.045166 | -0.00079686 | -0.0089913 | 2.9033 | 0.0034607 | 7.6842e-05 | 0.00051913 | -0.070465 | 0.1601 | 0.12516 | -0.0044348 | 0.056892 | 0.10543 | -0.0031445 | 0.086975 | 0.091553 | -0.050354 | 0.073242 | 0.19226 | 0.064087 | 0.10986 | 0.63629 | 59.7336 | -62.7686 | 59.9075 | 60.0357 | 59.8434 | 0.32959 | 62.6862 | -59.6878 | -59.7061 | 62.9288 | 62.8464 | 62.8006 | 0.16022 | 0.11444 | -0.032044 | -0.045776 | 0.12817 | 122.7722 | 63.0661 | 122.58 | 63.0981 | 122.612 | 0.24261 | 0.1236 | 122.8043 | 122.6761 | 0.14191 | 122.5021 | 62.8281 | 122.4701 | -59.8297 | -122.5479 | 62.8098 | 122.644 | 62.8235 | 63.3728
1581.8281 | 122.7951 | -62.7731 | 59.8389 | -0.014649 | -0.00036966 | -0.0062143 | 2.9044 | 0.0045289 | -0.0016322 | -0.0054623 | -0.094879 | 0.16331 | 0.12709 | -0.0078528 | 0.05796 | 0.10521 | -0.00058107 | 0.050354 | 0.12817 | -0.032043 | 0.050354 | 0.13275 | 0.032043 | 0.082397 | 0.57678 | 59.7839 | -62.7502 | 59.848 | 59.9304 | 59.761 | 0.30212 | 62.7411 | -59.7107 | -59.7885 | 62.9059 | 62.8555 | 62.8052 | 0.11444 | 0.064086 | 0.022888 | -0.054931 | 0.009155 | 122.7036 | 63.0753 | 122.5342 | 63.0524 | 122.5113 | 0.16479 | 0.082397 | 122.6807 | 122.5983 | 0.16022 | 122.5342 | 62.9013 | 122.5571 | -59.8709 | -122.5891 | 62.8235 | 122.6212 | 62.8235 | 63.3499
1582.8281 | 122.9187 | -62.7365 | 59.8022 | 0.00824 | -0.0014377 | -0.0072825 | 2.9031 | 0.00068369 | -0.0016322 | -0.00076267 | -0.091827 | 0.16309 | 0.12901 | -0.006571 | 0.059669 | 0.10393 | 0.0021961 | 0.041199 | 0.082397 | -0.068665 | 0.059509 | 0.17395 | 0.068665 | 0.09613 | 0.61798 | 59.729 | -62.7594 | 59.9396 | 60.0403 | 59.8755 | 0.32501 | 62.6678 | -59.7198 | -59.7427 | 62.9105 | 62.8326 | 62.8052 | 0.16479 | 0.13733 | -0.022888 | -0.073242 | 0.13733 | 122.7768 | 63.0615 | 122.612 | 63.0844 | 122.6349 | 0.24261 | 0.12817 | 122.7997 | 122.699 | 0.15106 | 122.4884 | 62.8189 | 122.4655 | -59.8709 | -122.5616 | 62.796 | 122.6761 | 62.7777 | 63.3545
1583.8906 | 122.8455 | -62.7594 | 59.7794 | -0.060425 | -0.0020785 | -0.0047189 | 2.9033 | 0.0073059 | -0.00099116 | -0.0016171 | -0.10403 | 0.1648 | 0.1273 | -0.0016576 | 0.059456 | 0.10415 | 0.0011279 | -0.022888 | 0.009155 | -0.11902 | -0.027466 | 0.050354 | -0.064087 | 0.013733 | 0.49439 | 59.7244 | -62.8006 | 59.8572 | 59.9258 | 59.761 | 0.18768 | 62.6404 | -59.7702 | -59.8068 | 62.8098 | 62.7731 | 62.6953 | 0.13275 | 0.054932 | -0.041199 | -0.054932 | 0.07782 | 122.6852 | 62.9471 | 122.5204 | 62.9883 | 122.5616 | 0.16937 | 0.091553 | 122.7264 | 122.6578 | 0.12817 | 122.525 | 62.7686 | 122.4838 | -59.8984 | -122.58 | 62.7319 | 122.6166 | 62.7365 | 63.2538
1584.8281 | 122.9095 | -62.7411 | 59.7931 | -0.037537 | -0.0027195 | -0.0083505 | 2.9035 | 0.0011109 | -0.0029138 | -0.0016171 | -0.094879 | 0.16224 | 0.12773 | -0.0052892 | 0.056038 | 0.10457 | -0.0044263 | 0.032043 | 0.07782 | -0.073242 | 0.045776 | 0.15564 | 0.050354 | 0.11902 | 0.61798 | 59.7336 | -62.7731 | 59.9258 | 60.0174 | 59.848 | 0.33875 | 62.6678 | -59.7153 | -59.7473 | 62.8967 | 62.8601 | 62.7914 | 0.19226 | 0.1236 | -0.032043 | -0.059509 | 0.13275 | 122.7585 | 63.0798 | 122.5891 | 63.1119 | 122.6212 | 0.22888 | 0.11902 | 122.7905 | 122.699 | 0.15106 | 122.5067 | 62.8189 | 122.4747 | -59.8663 | -122.5662 | 62.7869 | 122.6669 | 62.7731 | 63.3591
1585.8906 | 122.8683 | -62.7777 | 59.8114 | -0.083313 | -0.0018649 | -0.0074961 | 2.9033 | 0.0017517 | 0.00071784 | -0.0022581 | -0.039948 | 0.16437 | 0.12709 | -0.0025122 | 0.057747 | 0.10457 | -0.0033581 | -0.036621 | 0.059509 | -0.11444 | -0.045776 | 0.041199 | -0.041199 | 0.027466 | 0.40283 | 59.729 | -62.8006 | 59.8434 | 59.935 | 59.7519 | 0.23804 | 62.6633 | -59.7519 | -59.8572 | 62.8189 | 62.8052 | 62.7365 | 0.14191 | 0.073242 | -0.022888 | -0.082397 | 0.032044 | 122.7127 | 63.0157 | 122.5296 | 63.0386 | 122.5525 | 0.15564 | 0.068665 | 122.7356 | 122.644 | 0.17395 | 122.5296 | 62.8372 | 122.5067 | -59.9258 | -122.612 | 62.7319 | 122.6212 | 62.7411 | 63.1805
1586.8281 | 122.9233 | -62.7365 | 59.8022 | -0.052796 | -0.00079686 | -0.0077097 | 2.9035 | -0.00081171 | -0.00035036 | -0.0033261 | -0.082672 | 0.16309 | 0.13029 | -0.0042212 | 0.056465 | 0.10799 | -0.0016493 | 0.082397 | 0.091553 | -0.041199 | 0.068665 | 0.18768 | 0.086975 | 0.13275 | 0.6134 | 59.7473 | -62.7777 | 59.7931 | 60.1273 | 59.7427 | 0.24719 | 62.6953 | -59.7107 | -59.7336 | 62.9242 | 62.8693 | 62.8235 | 0.17395 | 0.12817 | -0.041199 | -0.054932 | -0.009155 | 122.8638 | 62.9837 | 122.4792 | 63.0249 | 122.5204 | 0.22888 | 0.10986 | 122.905 | 122.5708 | 0.13275 | 122.525 | 62.8281 | 122.4838 | -59.8434 | -122.58 | 62.8052 | 122.5296 | 62.8189 | 63.3499
1587.8906 | 122.85 | -62.7731 | 59.7794 | -0.029907 | -0.0016513 | -0.0081369 | 2.9048 | -0.00081171 | 0.00071784 | 0.0018009 | -0.088776 | 0.16331 | 0.1273 | 0.0034692 | 0.058387 | 0.10393 | -0.0022901 | -0.041199 | 0.050354 | -0.11902 | -0.054932 | 0.032043 | -0.050354 | 0.018311 | 0.45776 | 59.7473 | -62.7823 | 59.8389 | 59.9258 | 59.7565 | 0.2243 | 62.6541 | -59.729 | -59.8343 | 62.8052 | 62.7914 | 62.7228 | 0.13733 | 0.068665 | -0.009156 | -0.032044 | 0.059509 | 122.699 | 62.9974 | 122.5296 | 63.0066 | 122.5388 | 0.15106 | 0.064087 | 122.7081 | 122.6212 | 0.16937 | 122.5296 | 62.8235 | 122.5204 | -59.8984 | -122.5616 | 62.7182 | 122.612 | 62.7319 | 63.2309
1588.8281 | 122.85 | -62.7594 | 59.8206 | 0.015869 | -0.00015586 | -0.0074961 | 2.905 | -0.0038025 | 0.00029044 | -0.0016171 | -0.11624 | 0.16437 | 0.12858 | -0.0040076 | 0.057533 | 0.10521 | -0.0044263 | 0.041199 | 0.064087 | -0.064087 | 0.073242 | 0.15106 | 0.068665 | 0.11902 | 0.60883 | 59.7656 | -62.7731 | 59.8801 | 59.9899 | 59.7931 | 0.33875 | 62.6953 | -59.7565 | -59.7473 | 62.9105 | 62.8784 | 62.8281 | 0.18311 | 0.13275 | -0.013733 | -0.054932 | 0.059509 | 122.7493 | 63.0981 | 122.5525 | 63.1119 | 122.5662 | 0.21515 | 0.13733 | 122.7631 | 122.6532 | 0.12817 | 122.5388 | 62.8235 | 122.525 | -59.8846 | -122.5937 | 62.8326 | 122.6395 | 62.8006 | 63.3682
1589.8906 | 122.8867 | -62.7869 | 59.7885 | -0.15198 | -0.0027195 | -0.0092051 | 2.9037 | 0.0023925 | 7.6842e-05 | -0.00054907 | -0.13455 | 0.16202 | 0.12623 | 0.0017602 | 0.056892 | 0.10415 | -0.0042127 | 0.26093 | -0.064087 | -0.16479 | 0.009155 | 0.086975 | -0.09613 | -0.004578 | 0.48065 | 59.7244 | -62.7823 | 59.8892 | 59.9579 | 59.7794 | 0.20142 | 62.6221 | -59.8526 | -59.7794 | 62.8738 | 62.7823 | 62.6907 | 0.16022 | 0.068665 | 0.004577 | -0.064087 | 0.10071 | 122.7448 | 62.9883 | 122.5662 | 62.9837 | 122.5616 | 0.25177 | 0.17395 | 122.7402 | 122.6715 | 0.10071 | 122.5067 | 62.7228 | 122.5113 | -59.9533 | -122.5708 | 62.796 | 122.6761 | 63.0478 | 63.2675
1590.8281 | 122.8592 | -62.764 | 59.816 | 0.25238 | -0.00036966 | -0.0055735 | 2.9029 | -0.0010253 | -0.00013676 | -0.0020443 | -0.10098 | 0.1616 | 0.12815 | -0.0027258 | 0.058387 | 0.10607 | -0.0029309 | -0.24719 | 0.13275 | -0.009155 | 0.07782 | 0.11444 | 0.091553 | 0.13275 | 0.6134 | 59.761 | -62.7686 | 59.8984 | 60.0128 | 59.8206 | 0.34332 | 62.7548 | -59.6832 | -59.7382 | 62.8784 | 62.8967 | 62.8555 | 0.14191 | 0.10071 | -0.004578 | -0.054932 | 0.082397 | 122.7768 | 63.1073 | 122.5845 | 63.1119 | 122.5891 | 0.1236 | 0.086975 | 122.7814 | 122.6669 | 0.14191 | 122.5296 | 62.8967 | 122.525 | -59.8251 | -122.5845 | 62.8418 | 122.6624 | 62.5168 | 63.3774
1591.8906 | 122.8775 | -62.7686 | 59.7794 | -0.075684 | -0.0010105 | -0.0077097 | 2.9035 | 0.0015381 | 0.0017858 | -0.0028989 | -0.11929 | 0.16288 | 0.12559 | -0.0042212 | 0.057747 | 0.10671 | -0.0046399 | -0.013733 | -0.022888 | -0.11444 | 0.22888 | 0.31128 | -0.13733 | 0.018311 | 0.49896 | 59.697 | -62.8052 | 59.8892 | 59.9762 | 59.7839 | 0.20599 | 62.6541 | -59.8022 | -59.5505 | 63.0798 | 62.7869 | 62.6312 | 0.13275 | -0.022888 | -0.036621 | -0.082398 | 0.10986 | 122.7448 | 62.9745 | 122.5525 | 63.0112 | 122.5891 | 0.42572 | 0.34332 | 122.7814 | 122.6944 | 0.091553 | 122.5021 | 62.7457 | 122.4655 | -59.8938 | -122.5845 | 62.9974 | 122.6578 | 62.7548 | 63.2675
1592.8281 | 122.9095 | -62.7365 | 59.761 | -0.052796 | -0.0016513 | -0.0072825 | 2.9027 | -0.0038025 | -0.0018458 | -0.0052487 | -0.067413 | 0.16352 | 0.1241 | -0.0061438 | 0.056892 | 0.10479 | -0.0029309 | -0.009155 | 0.064087 | -0.064087 | 0.018311 | 0.09613 | 0.009155 | 0.064087 | 0.52643 | 59.7244 | -62.7914 | 59.8938 | 59.9945 | 59.8114 | 0.29755 | 62.6724 | -59.697 | -59.7427 | 62.8326 | 62.8006 | 62.7457 | 0.12817 | 0.073242 | -0.054932 | -0.036621 | 0.13275 | 122.731 | 63.0341 | 122.5479 | 63.089 | 122.6028 | 0.16022 | 0.082398 | 122.7859 | 122.6852 | 0.12817 | 122.5159 | 62.8006 | 122.4609 | -59.8251 | -122.5525 | 62.7548 | 122.6303 | 62.7274 | 63.2629
1593.8906 | 122.8226 | -62.796 | 59.7885 | -0.060425 | -0.0031467 | -0.0081369 | 2.9052 | -0.00038451 | 7.6842e-05 | -0.00076267 | -0.19559 | 0.16053 | 0.12794 | 0.00047855 | 0.058601 | 0.1065 | -0.0033581 | -0.1236 | 0.073242 | -0.13733 | -0.13733 | -0.064087 | -0.17395 | -0.09613 | 0.37994 | 59.7656 | -62.8281 | 59.8251 | 59.8663 | 59.6741 | 0.14648 | 62.6587 | -59.7153 | -59.9258 | 62.7319 | 62.6999 | 62.6221 | 0.041199 | -0.036621 | -0.032043 | -0.022888 | 0.036621 | 122.6624 | 62.9425 | 122.4701 | 62.9745 | 122.5021 | 0.073242 | 0 | 122.6944 | 122.6532 | 0.21057 | 122.5937 | 62.8693 | 122.5616 | -59.9258 | -122.6166 | 62.6587 | 122.6212 | 62.6724 | 63.176
1594.8281 | 122.8546 | -62.7731 | 59.816 | 0.00061049 | -0.0012241 | -0.0081369 | 2.9029 | 0.00025629 | -0.0018458 | -0.0014035 | -0.082672 | 0.16181 | 0.12751 | -0.0091344 | 0.057319 | 0.10585 | 5.9726e-05 | 0.054932 | 0.068665 | -0.059509 | 0.045776 | 0.14648 | 0.073242 | 0.10071 | 0.5722 | 59.7656 | -62.7869 | 59.8663 | 59.9762 | 59.7885 | 0.32501 | 62.7136 | -59.7473 | -59.7702 | 62.9196 | 62.8738 | 62.8464 | 0.16022 | 0.13275 | -0.013733 | -0.050354 | 0.050354 | 122.7493 | 63.0981 | 122.5616 | 63.1119 | 122.5754 | 0.20599 | 0.10528 | 122.7631 | 122.6532 | 0.12817 | 122.5525 | 62.8418 | 122.5388 | -59.8755 | -122.6028 | 62.8189 | 122.6395 | 62.8281 | 63.3453
1595.8906 | 122.8546 | -62.7823 | 59.7839 | -0.052796 | -0.0020785 | -0.0068551 | 2.9007 | 0.0023925 | -0.00077756 | -0.00076267 | -0.073517 | 0.16331 | 0.12944 | 0.00090575 | 0.059242 | 0.10521 | -0.0010083 | -0.041199 | 0.036621 | -0.11902 | -0.050354 | 0.041199 | -0.054932 | 0.027466 | 0.44861 | 59.7519 | -62.796 | 59.8618 | 59.9396 | 59.7519 | 0.24719 | 62.6633 | -59.7473 | -59.8343 | 62.8235 | 62.8098 | 62.7274 | 0.14649 | 0.064087 | -0.013733 | -0.032044 | 0.077819 | 122.7219 | 63.0295 | 122.5342 | 63.0432 | 122.5479 | 0.16022 | 0.068665 | 122.7356 | 122.6578 | 0.15564 | 122.5479 | 62.8189 | 122.5342 | -59.903 | -122.58 | 62.7319 | 122.644 | 62.7411 | 63.2309
1596.8281 | 122.8683 | -62.7548 | 59.8114 | -0.090943 | -0.00015586 | -0.0079233 | 2.9009 | -0.00038451 | -0.00013676 | -0.0031125 | -0.07962 | 0.16224 | 0.12709 | 5.1352e-05 | 0.055397 | 0.105 | -0.00079467 | 0.068665 | 0.082397 | -0.064087 | 0.050354 | 0.17853 | 0.064087 | 0.09613 | 0.59052 | 59.7702 | -62.7777 | 59.8892 | 59.9945 | 59.8114 | 0.33875 | 62.6907 | -59.729 | -59.761 | 62.9333 | 62.851 | 62.8189 | 0.16022 | 0.12817 | -0.022888 | -0.041198 | 0.07782 | 122.7493 | 63.0936 | 122.5662 | 63.1165 | 122.5891 | 0.24261 | 0.11444 | 122.7722 | 122.6669 | 0.14648 | 122.5479 | 62.8372 | 122.525 | -59.8755 | -122.5891 | 62.8052 | 122.644 | 62.8235 | 63.3453
1597.8906 | 122.8638 | -62.7914 | 59.7931 | -0.007019 | -0.00079686 | -0.0064279 | 2.9018 | -0.0027343 | 0.001145 | 0.00051913 | -0.10709 | 0.16395 | 0.12837 | -0.0035802 | 0.056678 | 0.10415 | -0.0016493 | -0.036621 | -0.009155 | -0.14191 | -0.050354 | 0.045776 | -0.082397 | -0.018311 | 0.46234 | 59.729 | -62.8006 | 59.8526 | 59.9304 | 59.7656 | 0.17395 | 62.6495 | -59.8022 | -59.8434 | 62.8372 | 62.7731 | 62.709 | 0.1236 | 0.05951 | -0.009155 | -0.064087 | 0.059509 | 122.7219 | 62.9654 | 122.5571 | 62.9745 | 122.5662 | 0.18768 | 0.091553 | 122.731 | 122.6532 | 0.13275 | 122.5296 | 62.7823 | 122.5204 | -59.935 | -122.5937 | 62.7411 | 122.644 | 62.7548 | 63.2538
1598.8281 | 122.9095 | -62.7502 | 59.8068 | 0.015869 | 0.00069854 | -0.0089913 | 2.902 | -0.0040161 | 0.00093144 | -0.0020443 | -0.091827 | 0.16181 | 0.12645 | -0.001444 | 0.056678 | 0.10521 | -0.00036747 | 0 | 0.050354 | -0.10529 | -0.009155 | 0.091553 | 0.004578 | 0.068665 | 0.53101 | 59.7427 | -62.7731 | 59.8892 | 60.0082 | 59.8389 | 0.28381 | 62.645 | -59.7565 | -59.816 | 62.8418 | 62.8189 | 62.7548 | 0.17395 | 0.10986 | -0.022888 | -0.064087 | 0.082397 | 122.7585 | 63.0341 | 122.5891 | 63.0569 | 122.612 | 0.19684 | 0.096131 | 122.7814 | 122.6624 | 0.15564 | 122.5159 | 62.8006 | 122.493 | -59.9121 | -122.58 | 62.7411 | 122.6395 | 62.7502 | 63.2812
1599.8906 | 122.8409 | -62.7823 | 59.8068 | -0.060425 | -0.0014377 | -0.0083505 | 2.9024 | 0.0030335 | 0.0013586 | -0.0026853 | -0.11319 | 0.16352 | 0.12538 | -0.0042212 | 0.056678 | 0.10479 | -0.0035719 | -0.041199 | 0.004578 | -0.1236 | -0.064087 | 0.009155 | -0.073242 | 0 | 0.43488 | 59.7519 | -62.8052 | 59.8389 | 59.9304 | 59.7473 | 0.19684 | 62.6587 | -59.8022 | -59.8709 | 62.7914 | 62.7823 | 62.709 | 0.1236 | 0.050354 | -0.022888 | -0.054932 | 0.032043 | 122.7127 | 62.9791 | 122.5296 | 63.002 | 122.5525 | 0.13275 | 0.059509 | 122.7356 | 122.644 | 0.12817 | 122.5571 | 62.7869 | 122.5342 | -59.9304 | -122.612 | 62.7182 | 122.6212 | 62.7411 | 63.2172
1600.8281 | 122.9553 | -62.764 | 59.8022 | -0.014649 | -0.0037875 | -0.0094187 | 2.9027 | 0.0038879 | -0.0018458 | -0.0035397 | -0.067413 | 0.16224 | 0.12687 | -0.0084936 | 0.055824 | 0.098164 | -0.0012219 | 0.086975 | 0.086975 | -0.054932 | 0.054932 | 0.17395 | 0.073242 | 0.1236 | 0.61798 | 59.7473 | -62.7869 | 60.0632 | 60.0861 | 59.5688 | 0.19226 | 62.709 | -59.7153 | -59.7473 | 62.9379 | 62.8876 | 62.8372 | 0.17853 | 0.12817 | -0.022888 | -0.054932 | 0.26093 | 122.85 | 62.9562 | 122.3328 | 62.9791 | 122.3557 | 0.22888 | 0.10986 | 122.8729 | 122.85 | 0.14191 | 122.5342 | 62.851 | 122.5113 | -59.8572 | -122.5891 | 62.8189 | 122.8271 | 62.851 | 63.382
1601.8906 | 122.7676 | -62.7914 | 59.8251 | -0.037537 | -0.0014377 | -0.0094187 | 2.9027 | -0.0080749 | -0.00077756 | -0.010589 | -0.20779 | 0.16074 | 0.12773 | 0.0034692 | 0.056038 | 0.097523 | -0.00036747 | -0.082397 | 0.068665 | -0.14648 | -0.13733 | -0.086975 | -0.16479 | -0.14191 | 0.34332 | 59.7794 | -62.8098 | 59.7794 | 59.8206 | 59.6191 | 0.13733 | 62.645 | -59.7565 | -59.9625 | 62.7045 | 62.6495 | 62.6266 | 0.004577 | -0.018311 | -0.01831 | -0.045776 | -0.045776 | 122.612 | 62.9288 | 122.4106 | 62.9471 | 122.4289 | 0.059509 | 0.009155 | 122.6303 | 122.5891 | 0.21515 | 122.5891 | 62.8601 | 122.5708 | -59.9716 | -122.6349 | 62.6541 | 122.5708 | 62.709 | 63.1348
1602.8281 | 122.9233 | -62.7686 | 59.8206 | -0.045166 | -0.0025059 | -0.0092051 | 2.9029 | -0.0018799 | -0.00056396 | 0.0013735 | -0.070465 | 0.16267 | 0.12858 | -0.0018712 | 0.057533 | 0.10521 | -0.0010083 | 0.036621 | 0.07782 | -0.054932 | 0.059509 | 0.14648 | 0.068665 | 0.11902 | 0.63629 | 59.7565 | -62.7594 | 59.9487 | 60.0449 | 59.8572 | 0.32959 | 62.7136 | -59.7427 | -59.761 | 62.915 | 62.8876 | 62.8372 | 0.17395 | 0.1236 | 0.009156 | -0.064087 | 0.12817 | 122.8134 | 63.0981 | 122.6257 | 63.089 | 122.6166 | 0.20142 | 0.11444 | 122.8043 | 122.7081 | 0.13275 | 122.5159 | 62.8464 | 122.525 | -59.8755 | -122.58 | 62.8281 | 122.7173 | 62.8052 | 63.4048
1603.8906 | 122.9004 | -62.764 | 59.7839 | -0.098572 | -0.00079686 | -0.0057871 | 2.9024 | 0.0011109 | -0.0012048 | -0.0050351 | -0.15591 | 0.16395 | 0.1273 | -0.0027258 | 0.057747 | 0.10756 | 0.00048713 | -0.086975 | 0.027466 | -0.16022 | -0.091553 | -0.022888 | -0.13275 | -0.064087 | 0.43945 | 59.7336 | -62.8235 | 59.8938 | 59.9579 | 59.7656 | 0.21515 | 62.6038 | -59.7565 | -59.8755 | 62.7411 | 62.6999 | 62.6312 | 0.09613 | 0.027466 | -0.059509 | -0.050354 | 0.10986 | 122.7219 | 62.9791 | 122.5296 | 63.0386 | 122.5891 | 0.13733 | 0.068664 | 122.7814 | 122.7173 | 0.18768 | 122.5571 | 62.7914 | 122.4976 | -59.9442 | -122.6074 | 62.6724 | 122.6578 | 62.677 | 63.2034
1604.8281 | 122.8088 | -62.7502 | 59.7977 | -0.037537 | -0.00015586 | -0.0077097 | 2.9033 | -0.0033753 | -0.0031274 | -0.0043943 | -0.058258 | 0.16138 | 0.12751 | -0.00058965 | 0.056892 | 0.10393 | -0.0018629 | 0.059509 | 0.091553 | -0.036621 | 0.068665 | 0.19226 | 0.073242 | 0.12817 | 0.63171 | 59.7656 | -62.7777 | 59.8801 | 60.1822 | 60.0723 | 0.53101 | 62.7136 | -59.7061 | -59.729 | 62.9425 | 62.8784 | 62.8235 | 0.1648 | 0.10986 | -0.027466 | -0.032043 | 0.082398 | 122.9324 | 63.2812 | 122.8226 | 63.3087 | 122.85 | 0.22888 | 0.10529 | 122.9599 | 122.6578 | 0.12817 | 122.5433 | 62.8418 | 122.5159 | -59.8343 | -122.5754 | 62.8189 | 122.6303 | 62.8098 | 63.382
1605.8906 | 122.8455 | -62.8052 | 59.8114 | -0.045166 | -0.00015586 | -0.0077097 | 2.9022 | 0.0028199 | -0.00035036 | 9.193e-05 | -0.14371 | 0.16331 | 0.12965 | 0.0015466 | 0.057106 | 0.10756 | -0.0035719 | -0.091553 | 0.041199 | -0.16022 | -0.13733 | -0.064087 | -0.15564 | -0.09613 | 0.39825 | 59.7519 | -62.8052 | 59.8389 | 59.9075 | 59.7244 | 0.16022 | 62.645 | -59.7702 | -59.9487 | 62.7411 | 62.709 | 62.6495 | 0.064087 | 0.004577 | 0 | -0.059509 | 0.027466 | 122.7127 | 62.9654 | 122.5296 | 62.9654 | 122.5296 | 0.09613 | 0.022888 | 122.7127 | 122.644 | 0.20142 | 122.5571 | 62.8464 | 122.5571 | -59.9716 | -122.6166 | 62.6678 | 122.644 | 62.7136 | 63.2034
1606.8281 | 122.9004 | -62.7869 | 59.8343 | -0.052796 | -0.0018649 | -0.0072825 | 2.902 | -0.0033753 | -0.0012048 | -0.0018307 | -0.082672 | 0.16224 | 0.1288 | -0.0052892 | 0.057106 | 0.10436 | 0.00070073 | -0.013733 | 0.059509 | -0.086975 | -0.022888 | 0.086975 | 0.013733 | 0.064087 | 0.53101 | 59.729 | -62.7914 | 59.8984 | 59.9945 | 59.8251 | 0.28839 | 62.6999 | -59.7748 | -59.8572 | 62.8738 | 62.851 | 62.8006 | 0.15106 | 0.10071 | -0.004578 | -0.10529 | 0.064086 | 122.7814 | 63.0753 | 122.612 | 63.0798 | 122.6166 | 0.17395 | 0.064087 | 122.7859 | 122.6898 | 0.14648 | 122.5204 | 62.8464 | 122.5159 | -59.9213 | -122.6257 | 62.764 | 122.6852 | 62.7731 | 63.3179
1607.8906 | 122.7905 | -62.796 | 59.8297 | -0.045166 | -0.0010105 | -0.0072825 | 2.9046 | 0.0028199 | -0.0012048 | 0.0018009 | -0.18033 | 0.16309 | 0.12751 | -0.004862 | 0.05796 | 0.10393 | -0.0042127 | -0.10529 | 0.050354 | -0.15564 | -0.1831 | -0.13733 | -0.1831 | -0.11902 | 0.3479 | 59.7702 | -62.851 | 59.7977 | 59.8343 | 59.6603 | 0.11902 | 62.6404 | -59.7794 | -60.0128 | 62.6587 | 62.677 | 62.6129 | 0.036621 | -0.027465 | -0.054931 | -0.059509 | -0.032044 | 122.6303 | 62.915 | 122.4564 | 62.97 | 122.5113 | 0.018311 | -0.027465 | 122.6852 | 122.6486 | 0.20599 | 122.6212 | 62.8464 | 122.5662 | -59.9854 | -122.6807 | 62.6129 | 122.5937 | 62.6907 | 63.1439
1608.8281 | 122.937 | -62.7457 | 59.7885 | 0.023498 | -0.0020785 | -0.0079233 | 2.8999 | -0.0010253 | -0.0018458 | -0.00097627 | -0.052155 | 0.16416 | 0.13008 | 5.1352e-05 | 0.057747 | 0.10372 | -0.0035719 | 0.009155 | 0.082397 | -0.064087 | 0.013733 | 0.12817 | 0.036621 | 0.086975 | 0.56763 | 59.7382 | -62.796 | 59.8892 | 60.0403 | 59.8618 | 0.32501 | 62.6816 | -59.7061 | -59.7748 | 62.8738 | 62.8326 | 62.7823 | 0.15106 | 0.10071 | -0.050354 | -0.050354 | 0.10071 | 122.7859 | 63.0707 | 122.6074 | 63.121 | 122.6578 | 0.19226 | 0.07782 | 122.8363 | 122.6852 | 0.14648 | 122.5342 | 62.8281 | 122.4838 | -59.8526 | -122.5845 | 62.7594 | 122.6349 | 62.7548 | 63.3133
1609.8906 | 122.8912 | -62.7823 | 59.7794 | -0.068054 | 0.00069854 | -0.0070687 | 2.9014 | -0.0018799 | -0.00013676 | -0.0035397 | -0.097931 | 0.16437 | 0.12773 | -0.0050756 | 0.057319 | 0.10564 | -0.0012219 | -0.018311 | -0.032043 | -0.13733 | -0.068665 | 0.027466 | 0.064087 | 0.032043 | 0.48065 | 59.7061 | -62.796 | 59.8984 | 59.9716 | 59.7839 | 0.21515 | 62.645 | -59.8114 | -59.848 | 62.8098 | 62.8143 | 62.8464 | 0.16937 | 0.20142 | -0.013733 | -0.073242 | 0.11902 | 122.7539 | 62.9974 | 122.5662 | 63.0112 | 122.58 | 0.16479 | 0.068664 | 122.7676 | 122.6944 | 0.10529 | 122.5021 | 62.7502 | 122.4884 | -59.9167 | -122.5754 | 62.7136 | 122.6807 | 62.764 | 63.2629
1610.8281 | 122.905 | -62.796 | 59.8206 | -0.029907 | -0.0020785 | -0.0074961 | 2.9009 | -0.00081171 | 0.00050424 | 9.193e-05 | -0.064362 | 0.16267 | 0.12922 | -0.0029394 | 0.056465 | 0.10436 | 0.00027333 | 0.004578 | 0.068665 | -0.082397 | -0.004578 | 0.10529 | 0.013733 | 0.064087 | 0.52643 | 59.7427 | -62.8006 | 59.8938 | 59.9899 | 59.8389 | 0.29755 | 62.7136 | -59.7519 | -59.8251 | 62.9013 | 62.8601 | 62.8098 | 0.14648 | 0.09613 | -0.004577 | -0.07782 | 0.073242 | 122.7859 | 63.0936 | 122.6349 | 63.0981 | 122.6395 | 0.18768 | 0.077819 | 122.7905 | 122.6944 | 0.15106 | 122.5433 | 62.8647 | 122.5388 | -59.903 | -122.6212 | 62.7914 | 122.6898 | 62.8006 | 63.3224
1611.8281 | 122.8546 | -62.7548 | 59.8526 | -0.014649 | -0.0020785 | -0.0087777 | 2.9009 | 0.0023925 | -0.0027002 | -0.0026853 | -0.076569 | 0.1616 | 0.12944 | -0.0050756 | 0.058387 | 0.10372 | -0.0010083 | 0.054932 | 0.082397 | -0.045776 | 0.041199 | 0.13733 | 0.054932 | 0.10071 | 0.59967 | 59.7748 | -62.7777 | 59.8663 | 59.9716 | 59.7931 | 0.32501 | 62.709 | -59.7702 | -59.8114 | 62.8922 | 62.8555 | 62.8098 | 0.14648 | 0.10071 | -0.022888 | -0.07782 | 0.013733 | 122.7264 | 63.0798 | 122.5479 | 63.1027 | 122.5708 | 0.18311 | 0.086975 | 122.7493 | 122.644 | 0.12817 | 122.5525 | 62.8372 | 122.5296 | -59.8984 | -122.6303 | 62.796 | 122.6212 | 62.8098 | 63.3545
1612.8281 | 122.9095 | -62.796 | 59.8251 | -0.014649 | 0.00027134 | -0.0074961 | 2.9007 | 0.00089729 | -0.0014184 | -0.0014035 | -0.085724 | 0.16352 | 0.12645 | -0.0025122 | 0.057747 | 0.10244 | 0.00070073 | -0.045776 | 0.036621 | -0.10071 | -0.054932 | 0.022888 | -0.054932 | 0.009155 | 0.43945 | 59.7519 | -62.8006 | 59.8663 | 59.9396 | 59.761 | 0.21973 | 62.6953 | -59.7885 | -59.8801 | 62.8189 | 62.8052 | 62.7411 | 0.10986 | 0.045776 | -0.004577 | -0.073242 | 0.041199 | 122.7356 | 63.0157 | 122.5571 | 63.0203 | 122.5616 | 0.1236 | 0.045776 | 122.7402 | 122.6669 | 0.13733 | 122.5525 | 62.8326 | 122.5479 | -59.9258 | -122.6257 | 62.7411 | 122.6624 | 62.7502 | 63.2355
1613.8906 | 122.9004 | -62.7823 | 59.7656 | -0.098572 | -0.0018649 | -0.0066415 | 2.9016 | -0.0012391 | 0.001145 | -0.0028989 | -0.094879 | 0.16373 | 0.1288 | -0.0025122 | 0.057106 | 0.10479 | -0.0054945 | 0.068665 | -0.032043 | -0.13275 | -0.059509 | 0.068665 | -0.064087 | -0.018311 | 0.47607 | 59.7153 | -62.8098 | 59.903 | 59.9808 | 59.7794 | 0.21057 | 62.6495 | -59.7977 | -59.8251 | 62.851 | 62.764 | 62.7182 | 0.11444 | 0.068664 | -0.027465 | -0.050354 | 0.13733 | 122.7631 | 62.9929 | 122.5616 | 63.0203 | 122.5891 | 0.20142 | 0.073242 | 122.7905 | 122.7127 | 0.10071 | 122.525 | 62.7502 | 122.4976 | -59.8984 | -122.5754 | 62.7228 | 122.6852 | 62.851 | 63.2584
1614.8281 | 122.9233 | -62.7548 | 59.8068 | -0.007019 | -0.0016513 | -0.0072825 | 2.9016 | -0.0010253 | 0.0032812 | -0.0024717 | -0.070465 | 0.16373 | 0.12944 | -0.003794 | 0.056465 | 0.10543 | -0.0037855 | 0.004578 | 0.054932 | -0.082397 | 0.022888 | 0.13275 | 0.027466 | 0.073242 | 0.54016 | 59.7748 | -62.8098 | 59.9121 | 60.022 | 59.848 | 0.29755 | 62.6724 | -59.7519 | -59.7839 | 62.8876 | 62.8281 | 62.7823 | 0.15564 | 0.10986 | -0.054931 | -0.032044 | 0.10529 | 122.7768 | 63.0524 | 122.6028 | 63.1073 | 122.6578 | 0.21515 | 0.10528 | 122.8317 | 122.7219 | 0.13733 | 122.5845 | 62.8098 | 122.5296 | -59.8892 | -122.6166 | 62.7777 | 122.6669 | 62.7594 | 63.295
1615.8906 | 122.8958 | -62.8006 | 59.7931 | -0.052796 | -0.0012241 | -0.0068551 | 2.8999 | 0.0017517 | 0.00071784 | -0.0022581 | -0.11624 | 0.16459 | 0.1273 | -0.0035802 | 0.057106 | 0.105 | -0.0057081 | -0.032043 | -0.009155 | -0.13275 | -0.045776 | 0.059509 | -0.091553 | -0.027466 | 0.48065 | 59.7473 | -62.8189 | 59.8618 | 59.9487 | 59.7519 | 0.1831 | 62.6678 | -59.8022 | -59.8389 | 62.8601 | 62.7731 | 62.709 | 0.10529 | 0.041198 | -0.018311 | -0.045777 | 0.068664 | 122.7493 | 62.9837 | 122.5525 | 63.002 | 122.5708 | 0.19226 | 0.086975 | 122.7676 | 122.6807 | 0.1236 | 122.5662 | 62.7914 | 122.5479 | -59.9258 | -122.612 | 62.7548 | 122.6624 | 62.7686 | 63.2812
1616.8281 | 122.9279 | -62.7914 | 59.8206 | -0.007019 | -0.0014377 | -0.0074961 | 2.9005 | -0.0031617 | -0.00099116 | -0.0035397 | -0.067413 | 0.16267 | 0.12773 | -0.0022986 | 0.059242 | 0.10457 | 5.9726e-05 | -0.013733 | 0.050354 | -0.086975 | 0 | 0.09613 | 0 | 0.054932 | 0.52185 | 59.7519 | -62.8006 | 59.8938 | 60.0174 | 59.8206 | 0.29755 | 62.7045 | -59.7702 | -59.8206 | 62.8876 | 62.8464 | 62.7914 | 0.14191 | 0.086975 | -0.009155 | -0.068665 | 0.073242 | 122.8088 | 63.089 | 122.612 | 63.0981 | 122.6212 | 0.1831 | 0.086975 | 122.818 | 122.6944 | 0.13733 | 122.5525 | 62.8418 | 122.5433 | -59.9075 | -122.6212 | 62.7914 | 122.6852 | 62.7777 | 63.3133
1617.8906 | 122.8775 | -62.7914 | 59.8068 | -0.060425 | -0.0012241 | -0.0074961 | 2.9001 | -0.0029479 | 0.0019994 | -0.0020443 | -0.088776 | 0.16117 | 0.12602 | -0.0057166 | 0.056892 | 0.10436 | -0.0050671 | -0.059509 | 0.022888 | -0.10986 | -0.050354 | 0.018311 | -0.091553 | -0.004578 | 0.44861 | 59.7427 | -62.8006 | 59.8572 | 59.9396 | 59.7519 | 0.20599 | 62.6816 | -59.7839 | -59.8572 | 62.8098 | 62.7869 | 62.6999 | 0.10529 | 0.01831 | -0.009155 | -0.064087 | 0.050354 | 122.731 | 62.9974 | 122.5433 | 63.0066 | 122.5525 | 0.12817 | 0.059509 | 122.7402 | 122.6578 | 0.13275 | 122.5433 | 62.8143 | 122.5342 | -59.9167 | -122.6074 | 62.7411 | 122.6486 | 62.7319 | 63.2401
1618.8281 | 122.9233 | -62.764 | 59.8251 | -0.022278 | -0.00036966 | -0.0068551 | 2.9018 | 0.00089729 | 0.00071784 | 0.00094633 | -0.07962 | 0.16245 | 0.12794 | -0.0029394 | 0.056465 | 0.10479 | -0.00015387 | 0.050354 | 0.086975 | -0.036621 | 0.073242 | 0.16479 | 0.082397 | 0.09613 | 0.89722 | 59.8114 | -62.7502 | 59.9442 | 60.0266 | 59.8297 | 0.32959 | 62.7274 | -59.7382 | -59.7519 | 62.9288 | 62.8601 | 62.8464 | 0.13275 | 0.11902 | 0.013733 | -0.013733 | 0.11902 | 122.7905 | 63.0936 | 122.5937 | 63.0798 | 122.58 | 0.20142 | 0.10986 | 122.7768 | 122.6944 | 0.1236 | 122.5616 | 62.851 | 122.5754 | -59.8618 | -122.5754 | 62.8372 | 122.7081 | 62.8143 | 63.6612
1619.8906 | 122.7768 | -62.8006 | 59.8434 | -0.029907 | -0.00036966 | -0.0077097 | 2.8988 | -0.0029479 | -0.003982 | -0.0088803 | -0.2139 | 0.15967 | 0.12751 | -0.003794 | 0.061165 | 0.089619 | -0.0016493 | -0.041199 | 0.059509 | -0.1236 | -0.09613 | -0.032043 | -0.14191 | -0.07782 | 0.37994 | 59.7794 | -62.8052 | 59.8068 | 59.8709 | 59.6741 | 0.14191 | 62.677 | -59.7839 | -59.9396 | 62.7686 | 62.7228 | 62.6587 | 0.045776 | -0.018311 | -0.004578 | -0.064087 | -0.036621 | 122.6715 | 62.9425 | 122.4747 | 62.9471 | 122.4792 | 0.091553 | 0.027466 | 122.6761 | 122.612 | 0.1831 | 122.5845 | 62.8601 | 122.58 | -59.967 | -122.6486 | 62.7045 | 122.6074 | 62.7594 | 63.1805
1620.8281 | 122.9095 | -62.7502 | 59.7977 | -0.060425 | -0.0025059 | -0.0081369 | 2.9012 | 0.00068369 | -0.0012048 | -0.0026853 | -0.058258 | 0.16202 | 0.12858 | -0.0050756 | 0.058174 | 0.10436 | -0.0027173 | -0.036621 | 0.054932 | -0.086975 | -0.041199 | 0.059509 | -0.018311 | 0.041199 | 0.49896 | 59.7565 | -62.8189 | 59.8938 | 59.9762 | 59.8206 | 0.27008 | 62.6633 | -59.7427 | -59.8389 | 62.8098 | 62.7914 | 62.7319 | 0.12817 | 0.068664 | -0.068665 | -0.041198 | 0.096131 | 122.7264 | 63.0203 | 122.5708 | 63.089 | 122.6395 | 0.14648 | 0.045776 | 122.7951 | 122.7127 | 0.14191 | 122.5754 | 62.8052 | 122.5067 | -59.8846 | -122.6166 | 62.709 | 122.644 | 62.7136 | 63.2492
1621.8906 | 122.8729 | -62.7823 | 59.8114 | -0.029907 | -0.0010105 | -0.0079233 | 2.9018 | -0.0016663 | 0.00050424 | -0.0028989 | -0.067413 | 0.16267 | 0.1305 | -0.0089208 | 0.05796 | 0.105 | -0.0022901 | -0.036621 | 0.050354 | -0.10071 | -0.059509 | 0.032043 | -0.045776 | 0 | 0.48065 | 59.7565 | -62.8235 | 59.8618 | 59.9487 | 59.7656 | 0.22888 | 62.6816 | -59.761 | -59.8709 | 62.8143 | 62.7823 | 62.7365 | 0.10071 | 0.054932 | -0.041198 | -0.054931 | 0.050354 | 122.731 | 63.0112 | 122.5479 | 63.0524 | 122.5891 | 0.13275 | 0.041199 | 122.7722 | 122.6852 | 0.15106 | 122.58 | 62.8326 | 122.5388 | -59.9121 | -122.6349 | 62.7228 | 122.644 | 62.7457 | 63.2629
1622.8281 | 122.937 | -62.7823 | 59.8022 | -0.014649 | -0.00036966 | -0.0081369 | 2.9016 | -0.0010253 | 0.00050424 | -0.0028989 | -0.076569 | 0.16331 | 0.12516 | -0.003153 | 0.057319 | 0.10393 | 0.00027333 | 0.018311 | 0.064087 | -0.073242 | 0.027466 | 0.1236 | 0.050354 | 0.10071 | 0.59509 | 59.7427 | -62.7823 | 59.9533 | 60.0403 | 59.8618 | 0.30212 | 62.709 | -59.7382 | -59.7748 | 62.9059 | 62.883 | 62.8326 | 0.17395 | 0.1236 | 0 | -0.059509 | 0.15106 | 122.8226 | 63.0844 | 122.644 | 63.0844 | 122.644 | 0.19684 | 0.10071 | 122.8226 | 122.7356 | 0.13733 | 122.525 | 62.8464 | 122.525 | -59.8755 | -122.5845 | 62.8098 | 122.7356 | 62.8006 | 63.3774
1623.9062 | 122.8455 | -62.7777 | 59.8206 | -0.090943 | -0.0018649 | -0.0079233 | 2.9033 | -0.0038025 | 0.001145 | -0.0058897 | -0.17728 | 0.1601 | 0.12858 | 0.0024012 | 0.059883 | 0.087056 | 0.00027333 | 0.027466 | 0.1236 | -0.091553 | -0.013733 | 0.073242 | -0.027466 | 0.018311 | 0.52643 | 59.7931 | -62.8052 | 59.8938 | 59.8114 | 59.7977 | 0.31586 | 62.6862 | -59.697 | -59.8343 | 62.851 | 62.796 | 62.7502 | 0.10986 | 0.064087 | -0.027466 | -0.027466 | 0.073242 | 122.5891 | 63.0936 | 122.5754 | 63.121 | 122.6028 | 0.16479 | 0.07782 | 122.6166 | 122.699 | 0.21515 | 122.5983 | 62.9013 | 122.5708 | -59.9121 | -122.6257 | 62.764 | 122.6715 | 62.8052 | 63.3041
1624.8281 | 122.9462 | -62.7594 | 59.7977 | -0.052796 | -0.0020785 | -0.0077097 | 2.8997 | -0.00017091 | -0.0012048 | -0.0016171 | -0.082672 | 0.16224 | 0.12666 | -0.0095618 | 0.058174 | 0.10201 | -0.0016493 | 0.027466 | 0.059509 | -0.059509 | 0.022888 | 0.13275 | 0.045776 | 0.10529 | 0.59967 | 59.761 | -62.8098 | 59.9487 | 60.0357 | 59.8618 | 0.33875 | 62.6999 | -59.7382 | -59.7748 | 62.8922 | 62.8647 | 62.8052 | 0.16479 | 0.10528 | -0.050354 | -0.036621 | 0.15106 | 122.7951 | 63.0981 | 122.6212 | 63.1485 | 122.6715 | 0.19226 | 0.082397 | 122.8455 | 122.7585 | 0.11902 | 122.5708 | 62.8189 | 122.5204 | -59.8572 | -122.6074 | 62.7823 | 122.7081 | 62.7869 | 63.3591
1625.8906 | 122.7951 | -62.8143 | 59.8572 | -0.037537 | -0.0025059 | -0.0081369 | 2.9012 | -0.0055115 | -0.0035548 | -0.0056759 | -0.15591 | 0.1663 | 0.12645 | -0.0025122 | 0.056892 | 0.094532 | -0.00058107 | -0.018311 | 0.068665 | -0.10986 | -0.09613 | -0.013733 | -0.12817 | -0.07782 | 0.40741 | 59.7977 | -62.8098 | 59.8022 | 59.8663 | 59.6878 | 0.16937 | 62.7045 | -59.7885 | -59.9533 | 62.8006 | 62.7365 | 62.6862 | 0.032043 | -0.018311 | 0.004578 | -0.05951 | -0.054932 | 122.6807 | 62.9837 | 122.5021 | 62.9791 | 122.4976 | 0.09613 | 0.013733 | 122.6761 | 122.612 | 0.17853 | 122.6074 | 62.883 | 122.612 | -59.967 | -122.6669 | 62.7182 | 122.6166 | 62.796 | 63.2217
1626.8281 | 122.9324 | -62.7548 | 59.816 | 0.031128 | -0.0033603 | -0.010273 | 2.8997 | -0.0023071 | 0.001145 | -0.0020443 | -0.058258 | 0.15861 | 0.12495 | -0.0080664 | 0.059028 | 0.10457 | 0.00048713 | 0.059509 | 0.09613 | -0.041199 | 0.059509 | 0.19684 | 0.091553 | 0.10986 | 0.90179 | 59.8206 | -62.7686 | 59.903 | 60.0723 | 59.8251 | 0.29755 | 62.7136 | -59.7198 | -59.7565 | 62.9517 | 62.8647 | 62.8464 | 0.15106 | 0.13275 | -0.013733 | 0.004578 | 0.086975 | 122.8271 | 63.0524 | 122.58 | 63.0661 | 122.5937 | 0.23804 | 0.10071 | 122.8409 | 122.6715 | 0.13733 | 122.5891 | 62.851 | 122.5754 | -59.8572 | -122.5845 | 62.8143 | 122.6578 | 62.8143 | 63.6566
1627.8906 | 122.8958 | -62.7777 | 59.8022 | -0.029907 | 0.00027134 | -0.0077097 | 2.902 | 0.0032471 | -0.0014184 | -0.0020443 | -0.052155 | 0.16395 | 0.12751 | 0.0011194 | 0.058174 | 0.10137 | -0.0039991 | -0.045776 | -0.018311 | -0.10529 | -0.07782 | 0.032043 | -0.073242 | -0.027466 | 0.43488 | 59.7336 | -62.8098 | 59.8709 | 59.9396 | 59.7656 | 0.20142 | 62.6724 | -59.8206 | -59.8801 | 62.8098 | 62.7502 | 62.7045 | 0.07782 | 0.032044 | -0.032043 | -0.068664 | 0.068665 | 122.7173 | 62.9791 | 122.5433 | 63.0112 | 122.5754 | 0.13733 | 0.027466 | 122.7493 | 122.6807 | 0.086975 | 122.5433 | 62.7594 | 122.5113 | -59.9075 | -122.612 | 62.6999 | 122.6486 | 62.7319 | 63.2126
1628.8438 | 122.7722 | -62.8601 | 59.8251 | -0.090943 | -0.0018649 | -0.0079233 | 2.9037 | 0.00046989 | 0.00050424 | 0.00094633 | -0.19254 | 0.16523 | 0.12602 | -0.00037605 | 0.057106 | 0.10585 | 0.0013415 | -0.09613 | 0.054932 | -0.16479 | -0.16022 | -0.10986 | -0.1831 | -0.10071 | 0.3479 | 59.7931 | -62.8555 | 59.8114 | 59.8526 | 59.4498 | -0.068665 | 62.6953 | -59.7702 | -59.9854 | 62.7502 | 62.7594 | 62.677 | 0.064087 | -0.01831 | 0.004577 | -0.032043 | -0.013733 | 122.7127 | 62.7914 | 122.3099 | 62.7869 | 122.3053 | 0.054932 | 0.004578 | 122.7081 | 122.6669 | 0.21973 | 122.6486 | 62.915 | 122.6532 | -59.9899 | -122.6807 | 62.6999 | 122.6715 | 62.764 | 63.208
1629.8906 | 122.8958 | -62.7869 | 59.7931 | -0.007019 | -0.0018649 | -0.0077097 | 2.899 | 0.0013245 | 0.00071784 | -0.0026853 | -0.036896 | 0.16288 | 0.12837 | -0.0061438 | 0.057106 | 0.10415 | 0.00048713 | -0.013733 | 0.041199 | -0.09613 | -0.045776 | 0.13275 | 0.19684 | 0.032043 | 0.44403 | 59.7427 | -62.8098 | 59.8801 | 59.9625 | 59.7839 | 0.25177 | 62.6907 | -59.7519 | -59.8389 | 62.9196 | 62.8189 | 62.9837 | 0.12817 | 0.29297 | -0.022888 | -0.050354 | 0.086975 | 122.7493 | 63.0386 | 122.5708 | 63.0615 | 122.5937 | 0.22888 | 0.050354 | 122.7722 | 122.6898 | 0.13733 | 122.5525 | 62.8281 | 122.5296 | -59.8892 | -122.6028 | 62.7411 | 122.6669 | 62.7731 | 63.2309
1630.8281 | 122.9462 | -62.7777 | 59.816 | -0.029907 | -0.0029331 | -0.0085641 | 2.8999 | 0.0011109 | 0.00050424 | 9.193e-05 | -0.14676 | 0.16117 | 0.12538 | -0.0027258 | 0.057747 | 0.10222 | -0.00058107 | 0.050354 | 0.086975 | -0.036621 | 0.059509 | 0.15106 | 0.69122 | 0.28839 | 0.70038 | 59.7565 | -62.7686 | 59.9487 | 60.0357 | 59.8618 | 0.3479 | 62.7411 | -59.729 | -59.7565 | 62.9288 | 63.0661 | 63.4689 | 0.32501 | 0.72784 | 0.009155 | -0.059509 | 0.13275 | 122.8134 | 63.1256 | 122.6395 | 63.1165 | 122.6303 | 0.18768 | 0.09613 | 122.8043 | 122.7173 | 0.1236 | 122.525 | 62.8647 | 122.5342 | -59.8526 | -122.5845 | 62.8372 | 122.7264 | 62.8281 | 63.4781
1631.8906 | 122.8546 | -62.8098 | 59.8068 | -0.060425 | -0.0020785 | -0.0089913 | 2.9024 | 0.0030335 | -0.0024866 | -0.0043943 | -0.15591 | 0.16352 | 0.12709 | -0.0018712 | 0.056465 | 0.10457 | 0.00070073 | -0.09613 | 0.050354 | -0.14191 | -0.14648 | -0.082397 | -0.16937 | -0.11444 | 0.38452 | 59.7748 | -62.8326 | 59.8251 | 59.8892 | 59.7015 | 0.15106 | 62.6678 | -59.7565 | -59.9533 | 62.7274 | 62.6953 | 62.6404 | 0.027466 | -0.027466 | -0.022889 | -0.032044 | 0.01831 | 122.699 | 62.9608 | 122.5113 | 62.9837 | 122.5342 | 0.05951 | -0.004577 | 122.7219 | 122.6578 | 0.19226 | 122.6074 | 62.8601 | 122.5845 | -59.9487 | -122.6395 | 62.6633 | 122.6349 | 62.7136 | 63.1943
1632.8281 | 122.85 | -62.7731 | 59.8389 | -0.022278 | 0.00048494 | -0.010487 | 2.9003 | -0.00081171 | 7.6842e-05 | -0.0028989 | -0.064362 | 0.16202 | 0.12623 | -0.0069982 | 0.059242 | 0.10521 | -0.0057081 | 0.064087 | 0.10071 | -0.045776 | 0.041199 | 0.15564 | 0.054932 | 0.10071 | 0.58136 | 59.7794 | -62.7731 | 59.8709 | 59.9716 | 59.7748 | 0.3067 | 62.7274 | -59.7382 | -59.7977 | 62.9288 | 62.8738 | 62.8281 | 0.14648 | 0.10071 | 0 | -0.059509 | 0.032044 | 122.7448 | 63.0798 | 122.5479 | 63.0798 | 122.5479 | 0.20142 | 0.086975 | 122.7448 | 122.644 | 0.14648 | 122.5525 | 62.8738 | 122.5525 | -59.8846 | -122.612 | 62.8143 | 122.644 | 62.8372 | 63.3545
1633.9062 | 122.8729 | -62.7914 | 59.7885 | -0.007019 | -0.0020785 | -0.0068551 | 2.9022 | 0.0023925 | -0.0020594 | -0.00097627 | -0.14066 | 0.16331 | 0.12709 | 0.00026495 | 0.057106 | 0.10607 | -0.0022901 | -0.091553 | 0.009155 | -0.16937 | -0.13275 | -0.059509 | -0.16479 | -0.07782 | 0.39368 | 59.7382 | -62.8143 | 59.8572 | 59.9304 | 59.7244 | 0.17395 | 62.6221 | -59.7794 | -59.9213 | 62.7319 | 62.7136 | 62.6266 | 0.091553 | 0.004578 | -0.022888 | -0.050354 | 0.068665 | 122.7219 | 62.9654 | 122.5159 | 62.9883 | 122.5388 | 0.10986 | 0.036622 | 122.7448 | 122.6715 | 0.17853 | 122.5525 | 62.8006 | 122.5296 | -59.9579 | -122.6028 | 62.6587 | 122.6486 | 62.6999 | 63.1851
1634.8281 | 122.8638 | -62.7777 | 59.8343 | 0.00824 | -0.0022923 | -0.0094187 | 2.9003 | -0.00038451 | -0.00056396 | -0.0011899 | -0.06131 | 0.16331 | 0.12815 | -0.00058965 | 0.056465 | 0.10415 | 0.0030505 | 0.050354 | 0.10071 | -0.036621 | 0.032043 | 0.13733 | 0.059509 | 0.091553 | 0.58594 | 59.7702 | -62.7914 | 59.8709 | 59.9716 | 59.7794 | 0.32044 | 62.7411 | -59.7336 | -59.8022 | 62.915 | 62.8693 | 62.8372 | 0.12817 | 0.09613 | -0.013733 | -0.064087 | 0.036621 | 122.7493 | 63.0981 | 122.5571 | 63.1119 | 122.5708 | 0.17395 | 0.068664 | 122.7631 | 122.6624 | 0.13733 | 122.5616 | 62.8784 | 122.5479 | -59.8709 | -122.6257 | 62.8098 | 122.6486 | 62.8281 | 63.3636
1635.8906 | 122.9004 | -62.8006 | 59.816 | -0.014649 | -0.0010105 | -0.0068551 | 2.8997 | -0.0016663 | -0.00056396 | 0.00030553 | -0.064362 | 0.16181 | 0.1273 | -0.0074254 | 0.057106 | 0.10543 | -0.0016493 | -0.013733 | 0.041199 | -0.086975 | -0.064087 | 0.018311 | -0.050354 | 0.009155 | 0.46692 | 59.7382 | -62.8052 | 59.8709 | 59.9625 | 59.7839 | 0.23804 | 62.7136 | -59.7748 | -59.8801 | 62.8189 | 62.8098 | 62.7502 | 0.09613 | 0.036621 | -0.004578 | -0.07782 | 0.054932 | 122.7631 | 63.0386 | 122.5845 | 63.0432 | 122.5891 | 0.10529 | 0.022888 | 122.7676 | 122.6761 | 0.12817 | 122.5433 | 62.8418 | 122.5388 | -59.903 | -122.6212 | 62.7365 | 122.6715 | 62.7869 | 63.2675
1636.8281 | 122.8134 | -62.8006 | 59.8801 | 0.00824 | -0.0029331 | -0.0079233 | 2.8999 | 0.00025629 | -0.00056396 | -0.0037533 | -0.10098 | 0.16459 | 0.12559 | 0.003042 | 0.06031 | 0.10564 | 0.0021961 | -0.009155 | 0.13275 | -0.059509 | -0.009155 | 0.064087 | -0.027466 | 0.054932 | 0.50812 | 59.8114 | -62.8052 | 59.8251 | 59.9121 | 59.7382 | 0.27924 | 62.7411 | -59.7473 | -59.8892 | 62.8647 | 62.8555 | 62.7731 | 0.11444 | 0.032043 | -0.004578 | -0.068665 | -0.054932 | 122.7127 | 63.0798 | 122.5388 | 63.0844 | 122.5433 | 0.1236 | 0.050354 | 122.7173 | 122.6303 | 0.19226 | 122.6166 | 62.9333 | 122.612 | -59.9396 | -122.6852 | 62.7914 | 122.6257 | 62.7914 | 63.3087
1637.8906 | 122.8867 | -62.7823 | 59.816 | 0.046386 | -0.0033603 | -0.0081369 | 2.8997 | 4.2692e-05 | -0.00013676 | -0.0056759 | -0.082672 | 0.1616 | 0.12837 | -0.0029394 | 0.056892 | 0.10158 | -0.00015387 | -0.032043 | 0.045776 | -0.09613 | 0.16022 | 0.13275 | -0.16479 | -0.018311 | 0.47607 | 59.7931 | -62.7823 | 59.8846 | 59.9762 | 59.8022 | 0.25635 | 62.6862 | -59.7702 | -59.6558 | 62.915 | 62.764 | 62.6175 | 0.077819 | -0.068665 | 0 | -0.022888 | 0.068665 | 122.7585 | 63.0386 | 122.5845 | 63.0386 | 122.5845 | 0.22888 | 0.25635 | 122.7585 | 122.6669 | 0.14191 | 122.5754 | 62.8281 | 122.5754 | -59.9121 | -122.5983 | 62.9425 | 122.6669 | 62.7502 | 63.2584
1638.8281 | 122.8271 | -62.8143 | 59.8526 | 0.00824 | -0.0025059 | -0.0074961 | 2.9014 | 0.00068369 | -0.0024866 | -0.00097627 | -0.097931 | 0.16309 | 0.12687 | 0.001974 | 0.056892 | 0.10222 | 0.00070073 | 0.022888 | 0.13275 | -0.054932 | -0.027466 | 0.050354 | -0.013733 | 0.045776 | 0.52643 | 59.8343 | -62.7869 | 59.816 | 59.9075 | 59.7336 | 0.28381 | 62.7594 | -59.7198 | -59.8801 | 62.8647 | 62.8601 | 62.8006 | 0.10071 | 0.041199 | 0.027466 | -0.01831 | -0.036621 | 122.7219 | 63.0981 | 122.5479 | 63.0707 | 122.5204 | 0.10529 | 0.027466 | 122.6944 | 122.6028 | 0.18768 | 122.6212 | 62.9471 | 122.6486 | -59.9075 | -122.6395 | 62.7869 | 122.6303 | 62.8372 | 63.3408
1639.8906 | 122.905 | -62.7823 | 59.8114 | -0.052796 | 0.0019803 | -0.0068551 | 2.9001 | -0.00038451 | 7.6842e-05 | -0.0011899 | -0.07962 | 0.16138 | 0.12815 | -0.0035802 | 0.056038 | 0.10628 | 0.0013415 | -0.050354 | -0.013733 | -0.11444 | -0.068665 | 0.009155 | -0.09613 | -0.027466 | 0.44403 | 59.7473 | -62.8052 | 59.8572 | 59.9442 | 59.7702 | 0.19684 | 62.6678 | -59.8251 | -59.8801 | 62.7914 | 62.7548 | 62.6862 | 0.086975 | 0.018311 | -0.022888 | -0.064087 | 0.045777 | 122.7264 | 62.9791 | 122.5525 | 63.002 | 122.5754 | 0.1236 | 0.045776 | 122.7493 | 122.6624 | 0.10071 | 122.5525 | 62.7686 | 122.5296 | -59.9258 | -122.6166 | 62.7136 | 122.6395 | 62.7319 | 63.2263
1640.8281 | 122.9645 | -62.7777 | 59.8297 | -0.014649 | -0.0012241 | -0.0072825 | 2.8997 | 0.00025629 | -0.00035036 | -0.0020443 | -0.052155 | 0.16202 | 0.12516 | -0.0084936 | 0.059242 | 0.10479 | -0.0010083 | 0.073242 | 0.082397 | -0.018311 | 0.068665 | 0.17853 | 0.07782 | 0.13733 | 0.65002 | 59.7336 | -62.7731 | 59.9533 | 60.0494 | 59.761 | 0.30212 | 62.7594 | -59.7473 | -59.761 | 62.9562 | 62.915 | 62.8555 | 0.15564 | 0.096131 | 0.004578 | -0.09613 | 0.1236 | 122.8271 | 63.0798 | 122.5388 | 63.0753 | 122.5342 | 0.19684 | 0.086976 | 122.8226 | 122.7264 | 0.10071 | 122.5067 | 62.8601 | 122.5113 | -59.848 | -122.6028 | 62.8464 | 122.731 | 62.851 | 63.4277
1641.8906 | 122.8775 | -62.8143 | 59.8389 | -0.029907 | -0.0012241 | -0.0066415 | 2.8975 | 0.00046989 | -0.0014184 | -0.0026853 | -0.076569 | 0.1616 | 0.12645 | -0.00080325 | 0.058174 | 0.10521 | 0.0026233 | -0.022888 | 0.036621 | -0.09613 | -0.041199 | 0.041199 | -0.059509 | 0.009155 | 0.45776 | 59.7565 | -62.8189 | 59.8663 | 59.9487 | 59.7931 | 0.25177 | 62.7182 | -59.8022 | -59.8801 | 62.8555 | 62.8235 | 62.7548 | 0.10528 | 0.036621 | -0.004578 | -0.082397 | 0.027466 | 122.7631 | 63.0661 | 122.6074 | 63.0707 | 122.612 | 0.13733 | 0.054931 | 122.7676 | 122.6852 | 0.13275 | 122.5754 | 62.851 | 122.5708 | -59.935 | -122.6578 | 62.7731 | 122.6807 | 62.7914 | 63.2721
1642.8281 | 122.7814 | -62.8052 | 59.8572 | 0.00824 | -0.0033603 | -0.0081369 | 2.9022 | 0.0021789 | -0.00035036 | -0.00076267 | -0.13455 | 0.16331 | 0.1288 | 0.0015466 | 0.057533 | 0.10415 | 0.0013415 | 0.018311 | 0.16479 | -0.032043 | -0.022888 | 0.036621 | -0.009155 | 0.045776 | 0.44403 | 59.8206 | -62.7914 | 59.7931 | 59.8801 | 59.7427 | 0.27466 | 62.7731 | -59.6924 | -59.8801 | 62.8418 | 62.851 | 62.796 | 0.077819 | 0.022888 | 0.013733 | -0.036621 | -0.064087 | 122.6852 | 63.0798 | 122.5479 | 63.0661 | 122.5342 | 0.068664 | 0.009155 | 122.6715 | 122.5845 | 0.19684 | 122.612 | 62.97 | 122.6257 | -59.8892 | -122.6486 | 62.7823 | 122.5983 | 62.8235 | 63.2492
1643.8906 | 122.9141 | -62.7869 | 59.8114 | -0.075684 | -0.0022923 | -0.0081369 | 2.8992 | -0.00017091 | 0.0024268 | -0.0035397 | -0.052155 | 0.16138 | 0.1258 | -0.0035802 | 0.058174 | 0.10393 | -0.0039991 | -0.032043 | 0.073242 | -0.091553 | -0.018311 | 0.050354 | -0.018311 | 0.036621 | 0.50812 | 59.7656 | -62.8235 | 59.903 | 59.9945 | 59.8206 | 0.29755 | 62.6953 | -59.7382 | -59.8297 | 62.8372 | 62.8235 | 62.7686 | 0.12817 | 0.073242 | -0.036621 | -0.045776 | 0.091553 | 122.7814 | 63.0844 | 122.6074 | 63.121 | 122.644 | 0.14191 | 0.073242 | 122.818 | 122.7264 | 0.16479 | 122.5891 | 62.8601 | 122.5525 | -59.903 | -122.6349 | 62.7686 | 122.6898 | 62.7548 | 63.295
1644.8281 | 122.85 | -62.8143 | 59.8572 | 0.023498 | -0.0010105 | -0.0085641 | 2.9022 | -0.00017091 | -0.00035036 | 9.193e-05 | -0.085724 | 0.16288 | 0.1273 | -0.0022986 | 0.057106 | 0.1065 | 0.0024097 | 0.054932 | 0.10986 | -0.041199 | 0.013733 | 0.11444 | 0.027466 | 0.068665 | 0.54932 | 59.8022 | -62.8189 | 59.848 | 59.967 | 59.7656 | 0.27466 | 62.7731 | -59.7473 | -59.8434 | 62.9288 | 62.883 | 62.8418 | 0.10986 | 0.068665 | -0.004578 | -0.054932 | -0.009156 | 122.7814 | 63.089 | 122.58 | 63.0936 | 122.5845 | 0.15564 | 0.054932 | 122.7859 | 122.6669 | 0.15106 | 122.6212 | 62.9242 | 122.6166 | -59.8984 | -122.6761 | 62.8281 | 122.6624 | 62.8693 | 63.3636
1645.8281 | 122.8775 | -62.8189 | 59.8618 | 0.00824 | -0.0016513 | -0.0092051 | 2.9022 | 0.00068369 | -0.0027002 | -0.0024717 | -0.15897 | 0.16437 | 0.12751 | 0.0017602 | 0.057533 | 0.1003 | -0.0035719 | 0.013733 | 0.14648 | -0.054932 | -0.027466 | 0.045776 | -0.013733 | 0.027466 | 0.53101 | 59.816 | -62.8372 | 59.8801 | 59.9579 | 59.7702 | 0.29297 | 62.764 | -59.7153 | -59.8892 | 62.8647 | 62.8464 | 62.8052 | 0.082398 | 0.041199 | -0.01831 | -0.045776 | 0.018311 | 122.7768 | 63.1119 | 122.5891 | 63.1302 | 122.6074 | 0.10071 | 0.027466 | 122.7951 | 122.7173 | 0.20142 | 122.6532 | 62.9654 | 122.6349 | -59.9167 | -122.699 | 62.7914 | 122.699 | 62.8326 | 63.3499
1646.8906 | 122.9324 | -62.7731 | 59.8068 | -0.037537 | -0.00058326 | -0.0066415 | 2.9009 | 0.00068369 | -0.00035036 | -0.0031125 | -0.064362 | 0.16138 | 0.12773 | -0.0072118 | 0.058601 | 0.10393 | -0.0027173 | 0.16022 | 0.059509 | -0.073242 | -0.036621 | 0.045776 | -0.041199 | 0.004578 | 0.48065 | 59.7565 | -62.8464 | 59.8892 | 59.9716 | 59.8022 | 0.24719 | 62.6999 | -59.7473 | -59.8434 | 62.8189 | 62.7777 | 62.7319 | 0.07782 | 0.032043 | -0.073243 | -0.050354 | 0.082397 | 122.7448 | 63.0203 | 122.5754 | 63.0936 | 122.6486 | 0.11902 | 0.036621 | 122.818 | 122.7356 | 0.13275 | 122.6028 | 62.8326 | 122.5296 | -59.8801 | -122.6532 | 62.7365 | 122.6624 | 62.9333 | 63.2538
1647.8281 | 122.8729 | -62.8281 | 59.8526 | 0.023498 | -0.00079686 | -0.0066415 | 2.9007 | -0.0010253 | -0.00099116 | -0.0024717 | -0.14066 | 0.16331 | 0.12751 | 0.00069215 | 0.054756 | 0.10372 | 0.0017687 | 0 | 0.15106 | -0.041199 | -0.013733 | 0.059509 | -0.004578 | 0.032043 | 0.52643 | 59.7977 | -62.8189 | 59.8846 | 59.9258 | 59.7839 | 0.31128 | 62.7869 | -59.7015 | -59.8663 | 62.8876 | 62.8601 | 62.8235 | 0.073242 | 0.036621 | 0.009155 | -0.054932 | 0.032044 | 122.7539 | 63.1393 | 122.612 | 63.1302 | 122.6028 | 0.10071 | 0.027466 | 122.7448 | 122.7036 | 0.19226 | 122.6166 | 62.9791 | 122.6257 | -59.8938 | -122.6715 | 62.8143 | 122.7127 | 62.8281 | 63.3545
1648.8906 | 122.9507 | -62.7914 | 59.8114 | -0.029907 | -0.0014377 | -0.0092051 | 2.8988 | 0.0011109 | -0.0029138 | -0.0033261 | -0.058258 | 0.16224 | 0.1273 | -0.0027258 | 0.058387 | 0.10521 | 0.0013415 | 0.009155 | 0.059509 | -0.09613 | 0 | 0.10529 | 0.013733 | 0.073242 | 0.55389 | 59.7427 | -62.7914 | 59.9167 | 60.0266 | 59.8434 | 0.32501 | 62.6953 | -59.7519 | -59.8114 | 62.8967 | 62.8647 | 62.8052 | 0.16937 | 0.10986 | 0 | -0.068664 | 0.10529 | 122.818 | 63.1165 | 122.6349 | 63.1165 | 122.6349 | 0.20142 | 0.09613 | 122.818 | 122.7081 | 0.15564 | 122.5342 | 62.851 | 122.5342 | -59.9075 | -122.6028 | 62.7914 | 122.7081 | 62.8006 | 63.3453
1649.8281 | 122.8638 | -62.8052 | 59.8572 | 0.031128 | -0.0012241 | -0.0079233 | 2.9018 | -0.00081171 | -0.00099116 | -0.00054907 | -0.16202 | 0.16437 | 0.12495 | -0.00037605 | 0.055824 | 0.099446 | 0.0011279 | 0.073242 | 0.054932 | -0.11902 | -0.027466 | 0.054932 | -0.064087 | -0.032043 | 0.49439 | 59.8206 | -62.8372 | 59.8755 | 59.9167 | 59.7244 | 0.2243 | 62.6862 | -59.8022 | -59.8846 | 62.8601 | 62.7731 | 62.7411 | 0.086976 | 0.054932 | -0.032043 | -0.036621 | 0.01831 | 122.7219 | 63.0295 | 122.5296 | 63.0615 | 122.5616 | 0.17395 | 0.091553 | 122.7539 | 122.7127 | 0.17395 | 122.6578 | 62.8601 | 122.6257 | -59.9762 | -122.6944 | 62.7777 | 122.6807 | 62.8784 | 63.2996
1650.8906 | 122.9645 | -62.764 | 59.8434 | -0.022278 | 0.00048494 | -0.0098459 | 2.899 | 4.2692e-05 | -0.0012048 | -0.0024717 | -0.036896 | 0.16181 | 0.12645 | -0.0080664 | 0.058174 | 0.10457 | -0.0016493 | 0.022888 | 0.050354 | -0.054932 | 0.032043 | 0.16937 | 0.07782 | 0.11444 | 0.63629 | 59.761 | -62.7869 | 59.9533 | 60.054 | 59.8755 | 0.33875 | 62.709 | -59.7931 | -59.8114 | 62.9333 | 62.8784 | 62.8418 | 0.16937 | 0.13275 | -0.022888 | -0.082398 | 0.10986 | 122.818 | 63.1027 | 122.6395 | 63.1256 | 122.6624 | 0.22431 | 0.086975 | 122.8409 | 122.7402 | 0.10529 | 122.5479 | 62.8143 | 122.525 | -59.8984 | -122.6303 | 62.796 | 122.7173 | 62.7869 | 63.4003
1651.8281 | 122.8683 | -62.8052 | 59.8663 | 0.00061049 | -0.0018649 | -0.0057871 | 2.9014 | -0.0014527 | -0.00099116 | -0.0024717 | -0.13455 | 0.16267 | 0.12666 | -0.0072118 | 0.056892 | 0.10308 | -0.00058107 | 0.027466 | 0.10071 | -0.059509 | -0.009155 | 0.054932 | -0.022888 | 0.018311 | 0.54474 | 59.8068 | -62.8326 | 59.8801 | 59.9533 | 59.7519 | 0.27924 | 62.7457 | -59.7656 | -59.8755 | 62.8601 | 62.8235 | 62.7823 | 0.07782 | 0.036621 | -0.027466 | -0.059509 | 0.013733 | 122.7585 | 63.0844 | 122.5571 | 63.1119 | 122.5845 | 0.11444 | 0.050354 | 122.7859 | 122.7127 | 0.16022 | 122.6395 | 62.9059 | 122.612 | -59.9258 | -122.699 | 62.796 | 122.6852 | 62.8326 | 63.3499
1652.9062 | 122.8317 | -62.7914 | 59.8755 | 0.023498 | -0.0035739 | -0.0092051 | 2.9018 | 0.0026063 | -0.0014184 | -0.00054907 | -0.1376 | 0.16437 | 0.12623 | -0.0042212 | 0.057106 | 0.10436 | 0.0028369 | 0 | 0.17853 | -0.032043 | -0.050354 | -0.09613 | -0.050354 | 0.018311 | 0.50812 | 59.8343 | -62.8464 | 59.8343 | 59.9121 | 59.7336 | 0.27924 | 62.7594 | -59.697 | -59.9258 | 62.6953 | 62.8098 | 62.7411 | 0.050354 | -0.018311 | -0.054932 | -0.041198 | -0.041198 | 122.7036 | 63.0707 | 122.525 | 63.1256 | 122.58 | -0.064087 | -0.018311 | 122.7585 | 122.6807 | 0.21057 | 122.6807 | 62.97 | 122.6257 | -59.9075 | -122.7219 | 62.7411 | 122.6257 | 62.7914 | 63.2996
1653.8281 | 122.8546 | -62.7869 | 59.8343 | -0.007019 | -0.0025059 | -0.0070687 | 2.9014 | 0.0021789 | -0.00035036 | -0.0026853 | -0.14371 | 0.16245 | 0.12751 | 0.0028284 | 0.056678 | 0.1035 | -0.0016493 | 0 | 0.10529 | -0.082397 | -0.073242 | -0.13733 | -0.16022 | 0.09613 | 0.51727 | 59.7931 | -62.8052 | 59.8618 | 59.935 | 59.7427 | 0.25177 | 62.7045 | -59.729 | -59.9075 | 62.6495 | 62.883 | 62.6266 | 0.17853 | -0.07782 | -0.018311 | -0.041199 | 0.027465 | 122.7219 | 63.0386 | 122.5296 | 63.0569 | 122.5479 | -0.054932 | 0.009155 | 122.7402 | 122.6669 | 0.18768 | 122.5983 | 62.8922 | 122.58 | -59.9167 | -122.6395 | 62.7136 | 122.6486 | 62.7869 | 63.3041
1654.8281 | 122.8226 | -62.8281 | 59.8846 | -0.052796 | 0.00091214 | -0.0087777 | 2.8994 | -0.0031617 | -0.0014184 | -0.0016171 | -0.064362 | 0.16202 | 0.12623 | -0.0059302 | 0.056678 | 0.10265 | -0.0010083 | 0.045776 | 0.10986 | -0.041199 | 0.013733 | 0.10071 | 0.018311 | 0.068665 | 0.54016 | 59.8068 | -62.8235 | 59.848 | 59.9121 | 59.7565 | 0.2655 | 62.7869 | -59.7748 | -59.8709 | 62.9288 | 62.8967 | 62.8464 | 0.10986 | 0.05951 | 0.004578 | -0.07782 | -0.036622 | 122.7402 | 63.0936 | 122.5845 | 63.089 | 122.58 | 0.14191 | 0.054932 | 122.7356 | 122.6715 | 0.15106 | 122.6303 | 62.9379 | 122.6349 | -59.9258 | -122.7081 | 62.8418 | 122.6761 | 62.8738 | 63.3682
1655.8906 | 122.9645 | -62.7777 | 59.8434 | -0.029907 | 0.00069854 | -0.0089913 | 2.8977 | -0.0014527 | -0.00013676 | -0.0043943 | -0.021637 | 0.16202 | 0.12645 | -0.0084936 | 0.05796 | 0.10479 | 0.00048713 | 0.018311 | 0.073242 | -0.073242 | 0.009155 | 0.13733 | 0.041199 | 0.10071 | 0.59052 | 59.7519 | -62.7777 | 59.9442 | 60.0494 | 59.8709 | 0.32044 | 62.7045 | -59.7702 | -59.8343 | 62.915 | 62.8784 | 62.8189 | 0.17395 | 0.11444 | 0 | -0.091553 | 0.10071 | 122.8271 | 63.0981 | 122.6486 | 63.0981 | 122.6486 | 0.21057 | 0.082397 | 122.8271 | 122.7219 | 0.14648 | 122.5296 | 62.851 | 122.5296 | -59.9167 | -122.6212 | 62.7869 | 122.7219 | 62.796 | 63.3682
1656.8281 | 122.85 | -62.8189 | 59.8663 | -0.007019 | -0.00036966 | -0.0098459 | 2.9012 | 0.0015381 | -0.00077756 | -0.0024717 | -0.14066 | 0.16267 | 0.12965 | -0.0027258 | 0.056678 | 0.10372 | -0.00058107 | -0.050354 | 0.15106 | -0.027466 | -0.059509 | 0.045776 | -0.041199 | 0.018311 | 0.49896 | 59.8251 | -62.8189 | 59.8297 | 59.9304 | 59.7473 | 0.28381 | 62.7914 | -59.7153 | -59.9258 | 62.8647 | 62.8372 | 62.7777 | 0.045777 | -0.013733 | 0 | -0.041199 | -0.036621 | 122.7493 | 63.1027 | 122.5662 | 63.1027 | 122.5662 | 0.073242 | -0.032043 | 122.7493 | 122.6486 | 0.17853 | 122.644 | 62.97 | 122.644 | -59.8938 | -122.6852 | 62.7594 | 122.6486 | 62.7686 | 63.3179
1657.8906 | 122.8912 | -62.7319 | 59.8801 | -0.052796 | -0.0025059 | -0.0094187 | 2.8994 | 0.00025629 | 0.0017858 | -0.0048215 | -0.036896 | 0.16181 | 0.12666 | -0.0042212 | 0.056678 | 0.10479 | -0.0042127 | 0.050354 | 0.07782 | -0.041199 | 0.059509 | 0.20599 | 0.082397 | 0.10986 | 0.61798 | 59.7702 | -62.7869 | 59.9396 | 60.0494 | 59.8618 | 0.35248 | 62.6907 | -59.8022 | -59.8206 | 62.9379 | 62.8418 | 62.8143 | 0.15106 | 0.1236 | -0.054931 | -0.10986 | 0.059509 | 122.7814 | 63.0844 | 122.5937 | 63.1393 | 122.6486 | 0.24719 | 0.10071 | 122.8363 | 122.7264 | 0.11902 | 122.5571 | 62.8098 | 122.5021 | -59.9213 | -122.6669 | 62.7914 | 122.6715 | 62.7823 | 63.3499
1658.8281 | 122.8912 | -62.8006 | 59.8618 | 0.031128 | -0.0020785 | -0.0094187 | 2.9003 | 0.0038879 | -0.0029138 | 0.00094633 | -0.1376 | 0.16352 | 0.1288 | -0.0035802 | 0.056465 | 0.10671 | -0.0014355 | 0.022888 | 0.14191 | -0.032043 | -0.013733 | 0.059509 | 0.004578 | 0.032043 | 0.54016 | 59.7977 | -62.8281 | 59.8572 | 59.9442 | 59.761 | 0.31128 | 62.7686 | -59.7198 | -59.8755 | 62.8601 | 62.8326 | 62.8052 | 0.064086 | 0.036621 | -0.027466 | -0.064087 | -0.004577 | 122.7448 | 63.1119 | 122.5616 | 63.1393 | 122.5891 | 0.091552 | 0.01831 | 122.7722 | 122.6852 | 0.17395 | 122.6257 | 62.9425 | 122.5983 | -59.8938 | -122.6898 | 62.7869 | 122.6578 | 62.8235 | 63.3408
1659.8906 | 122.9553 | -62.7548 | 59.8251 | -0.014649 | -0.0016513 | -0.0092051 | 2.8997 | -0.00017091 | 0.0013586 | 0.0026553 | -0.021637 | 0.16437 | 0.12623 | -0.0059302 | 0.057747 | 0.10329 | -0.0031445 | 0.054932 | 0.07782 | -0.045776 | 0.050354 | 0.1831 | 0.068665 | 0.12817 | 0.66376 | 59.7519 | -62.7823 | 59.9167 | 60.0403 | 59.8618 | 0.33875 | 62.709 | -59.7473 | -59.7748 | 62.9379 | 62.883 | 62.8235 | 0.17395 | 0.11444 | -0.027466 | -0.073242 | 0.091553 | 122.7951 | 63.0936 | 122.6166 | 63.121 | 122.644 | 0.22888 | 0.09613 | 122.8226 | 122.699 | 0.1236 | 122.5342 | 62.8326 | 122.5067 | -59.8709 | -122.6074 | 62.8052 | 122.6715 | 62.8098 | 63.4186
1660.8281 | 122.8867 | -62.8098 | 59.8709 | 0.00824 | -0.0012241 | -0.0096323 | 2.9035 | 0.0017517 | -0.0033412 | -0.00076267 | -0.15591 | 0.16587 | 0.12944 | -0.0044348 | 0.055183 | 0.10585 | -0.0012219 | 0.018311 | 0.10986 | -0.073242 | -0.041199 | 0.064087 | -0.027466 | 0.009155 | 0.54474 | 59.7931 | -62.8281 | 59.8846 | 59.9579 | 59.7656 | 0.29297 | 62.7365 | -59.761 | -59.9121 | 62.8738 | 62.8189 | 62.7823 | 0.082397 | 0.045776 | -0.018311 | -0.07782 | 0.013733 | 122.7676 | 63.1027 | 122.5754 | 63.121 | 122.5937 | 0.13733 | 0.032043 | 122.7859 | 122.7127 | 0.18311 | 122.6212 | 62.9196 | 122.6028 | -59.9442 | -122.699 | 62.7686 | 122.6944 | 62.8281 | 63.3545
1661.8906 | 122.9553 | -62.7777 | 59.8389 | -0.045166 | 0.00069854 | -0.0077097 | 2.8992 | 4.2692e-05 | -0.0012048 | -0.0014035 | -0.039948 | 0.16416 | 0.12965 | -0.0055028 | 0.057747 | 0.10308 | 5.9726e-05 | 0.064087 | 0.073242 | -0.022888 | 0.064087 | 0.16479 | 0.11444 | 0.53101 | 0.54474 | 59.7519 | -62.8006 | 59.8938 | 60.0586 | 59.8709 | 0.34332 | 62.7548 | -59.7656 | -59.7748 | 62.9425 | 63.3087 | 62.8922 | 0.55389 | 0.13733 | -0.022888 | -0.086975 | 0.054932 | 122.8363 | 63.121 | 122.6486 | 63.1439 | 122.6715 | 0.18768 | 0.086975 | 122.8592 | 122.6944 | 0.09613 | 122.5525 | 62.851 | 122.5296 | -59.8618 | -122.6395 | 62.8418 | 122.6715 | 62.8418 | 63.3224
1662.8438 | 122.9416 | -62.7823 | 59.8068 | 0.099792 | 0.00069854 | -0.0045053 | 2.8997 | 0.00068369 | -0.00077756 | 9.193e-05 | -0.070465 | 0.15989 | 0.12623 | 0.0024012 | 0.056465 | 0.10265 | -0.0016493 | -0.091553 | -0.064087 | -0.16022 | -0.073242 | 0.041199 | -0.050354 | -0.009155 | 0.52185 | 59.7382 | -62.8235 | 59.9304 | 59.9808 | 59.8068 | 0.21057 | 62.6221 | -59.8709 | -59.8801 | 62.8235 | 62.7731 | 62.7319 | 0.15106 | 0.10986 | -0.041198 | -0.068665 | 0.1236 | 122.7631 | 62.9929 | 122.5891 | 63.0341 | 122.6303 | 0.20142 | 0.086975 | 122.8043 | 122.7539 | 0.09613 | 122.5616 | 62.7182 | 122.5204 | -59.967 | -122.6303 | 62.709 | 122.7127 | 62.6907 | 63.3041
1663.8906 | 122.9553 | -62.7731 | 59.8251 | -0.022278 | -0.0022923 | -0.0079233 | 2.8982 | -0.0023071 | 0.00029044 | 0.0018009 | -0.015534 | 0.16245 | 0.12559 | -0.0052892 | 0.056678 | 0.099873 | 0.0024097 | 0.07782 | 0.068665 | -0.032043 | 0.059509 | 0.19226 | 0.086975 | 0.11902 | 0.63171 | 59.761 | -62.8006 | 60.1456 | 59.7244 | 59.7794 | 0.36621 | 62.7411 | -59.7565 | -59.7656 | 62.9654 | 62.8922 | 62.8601 | 0.15106 | 0.11902 | -0.027466 | -0.064087 | 0.32044 | 122.4976 | 63.1393 | 122.5525 | 63.1668 | 122.58 | 0.2243 | 0.091552 | 122.525 | 122.9462 | 0.10071 | 122.5616 | 62.8418 | 122.5342 | -59.8572 | -122.6257 | 62.8326 | 122.9187 | 62.851 | 63.4048
1664.8281 | 122.8317 | -62.8372 | 59.8801 | 0.054016 | -0.00079686 | -0.0083505 | 2.8997 | -0.00059811 | -0.00077756 | 9.193e-05 | -0.10098 | 0.16288 | 0.1288 | -0.0057166 | 0.057533 | 0.10585 | -0.0033581 | -0.004578 | 0.15106 | -0.068665 | -0.032043 | 0.064087 | -0.009155 | 0.050354 | 0.50354 | 59.8434 | -62.8189 | 59.8297 | 59.9075 | 59.7244 | 0.26093 | 62.7686 | -59.729 | -59.9121 | 62.9013 | 62.8876 | 62.8281 | 0.11902 | 0.05951 | 0.01831 | -0.036621 | -0.050354 | 122.7448 | 63.0981 | 122.5616 | 63.0798 | 122.5433 | 0.13275 | 0.036622 | 122.7264 | 122.6486 | 0.21973 | 122.6624 | 62.9883 | 122.6807 | -59.9487 | -122.699 | 62.8052 | 122.6669 | 62.8326 | 63.3408
1665.8906 | 122.9233 | -62.796 | 59.8114 | -0.068054 | -0.0010105 | -0.0055735 | 2.8982 | 0.0036743 | 0.00093144 | -0.00097627 | -0.073517 | 0.16352 | 0.12645 | -0.0050756 | 0.056465 | 0.10372 | 0.0021961 | -0.027466 | 0 | -0.11444 | -0.054932 | 0.045776 | -0.073242 | -0.004578 | 0.51727 | 59.7427 | -62.8235 | 59.8846 | 59.9716 | 59.7931 | 0.20599 | 62.6816 | -59.8114 | -59.8663 | 62.8418 | 62.7914 | 62.7228 | 0.10986 | 0.041199 | -0.027465 | -0.068664 | 0.073243 | 122.7676 | 63.002 | 122.5891 | 63.0295 | 122.6166 | 0.16022 | 0.059509 | 122.7951 | 122.7081 | 0.11444 | 122.5662 | 62.796 | 122.5388 | -59.9258 | -122.6349 | 62.7411 | 122.6807 | 62.7686 | 63.3133
1666.8281 | 122.8729 | -62.8006 | 59.8801 | 0.031128 | 5.7742e-05 | -0.0081369 | 2.8984 | 0.00089729 | 0.0013586 | 0.0015871 | -0.13455 | 0.16459 | 0.1273 | 0.0032556 | 0.056678 | 0.10543 | -0.0031445 | 0.009155 | 0.13733 | -0.064087 | -0.032043 | 0.018311 | -0.013733 | 0.032043 | 0.49896 | 59.8343 | -62.8235 | 59.8709 | 59.9716 | 59.7656 | 0.29755 | 62.7365 | -59.7427 | -59.9121 | 62.8189 | 62.8326 | 62.7869 | 0.09613 | 0.050354 | -0.022888 | -0.045776 | -0.009155 | 122.7722 | 63.0981 | 122.5662 | 63.121 | 122.5891 | 0.082398 | 0.032044 | 122.7951 | 122.6944 | 0.20142 | 122.6578 | 62.9379 | 122.6349 | -59.9442 | -122.7036 | 62.7686 | 122.6715 | 62.8098 | 63.2996
1667.9062 | 122.9599 | -62.8098 | 59.8343 | -0.007019 | -0.00058326 | -0.0085641 | 2.8969 | 0.0023925 | -0.00056396 | -0.0035397 | -0.046051 | 0.16181 | 0.12815 | -0.0076392 | 0.057533 | 0.10521 | -0.0031445 | -0.018311 | 0.045776 | -0.068665 | -0.022888 | 0.07782 | 0.004578 | 0.059509 | 0.53558 | 59.7519 | -62.8143 | 59.9167 | 60.0266 | 59.848 | 0.28839 | 62.7411 | -59.7885 | -59.8572 | 62.8876 | 62.8693 | 62.8143 | 0.12817 | 0.073243 | -0.004578 | -0.082398 | 0.082397 | 122.8363 | 63.0981 | 122.6578 | 63.1027 | 122.6624 | 0.14649 | 0.045777 | 122.8409 | 122.731 | 0.11444 | 122.5662 | 62.8555 | 122.5616 | -59.903 | -122.6486 | 62.7869 | 122.7264 | 62.7914 | 63.3453
1668.8281 | 122.8226 | -62.8006 | 59.8984 | -0.022278 | -0.0018649 | -0.0096323 | 2.8994 | -0.0018799 | 7.6842e-05 | -0.0024717 | -0.082672 | 0.16331 | 0.12645 | -0.0044348 | 0.056038 | 0.10329 | -0.0022901 | 0.022888 | 0.13275 | -0.041199 | -0.022888 | 0.059509 | 0 | 0.041199 | 0.50354 | 59.8068 | -62.8098 | 59.8251 | 59.9167 | 59.7382 | 0.27466 | 62.7594 | -59.7656 | -59.9213 | 62.8601 | 62.8418 | 62.8006 | 0.082398 | 0.041199 | -0.009155 | -0.091552 | -0.073242 | 122.7173 | 63.0753 | 122.5388 | 63.0844 | 122.5479 | 0.10071 | 0.018311 | 122.7264 | 122.6349 | 0.17395 | 122.6166 | 62.9333 | 122.6074 | -59.9396 | -122.7081 | 62.7777 | 122.6257 | 62.8235 | 63.3041
1669.8906 | 122.8592 | -62.796 | 59.8801 | -0.029907 | -0.0016513 | -0.0092051 | 2.9005 | 0.0034607 | -0.0016322 | -0.0028989 | -0.049103 | 0.16074 | 0.12751 | -0.00058965 | 0.059669 | 0.1065 | -0.0018629 | 0.073242 | 0.10529 | -0.027466 | 0.027466 | 0.12817 | 0.041199 | 0.07782 | 0.59052 | 59.7931 | -62.8143 | 59.8709 | 59.9396 | 59.7748 | 0.29755 | 62.7686 | -59.7748 | -59.8526 | 62.9242 | 62.8738 | 62.8372 | 0.10529 | 0.068665 | -0.01831 | -0.086975 | -0.009155 | 122.7356 | 63.0936 | 122.5708 | 63.1119 | 122.5891 | 0.15564 | 0.054932 | 122.7539 | 122.6852 | 0.13275 | 122.6074 | 62.9013 | 122.5891 | -59.9075 | -122.6944 | 62.8235 | 122.6669 | 62.8693 | 63.3865
1670.8281 | 122.8455 | -62.8326 | 59.8755 | 0.00824 | -0.0018649 | -0.011128 | 2.8988 | 4.2692e-05 | -0.0027002 | -0.0050351 | -0.12845 | 0.16587 | 0.12858 | -0.0029394 | 0.057106 | 0.10436 | -0.0022901 | 0 | 0.16022 | -0.032043 | -0.032043 | 0.050354 | -0.004578 | 0.37537 | 0.41199 | 59.8297 | -62.8143 | 59.8114 | 59.935 | 59.7382 | 0.28381 | 62.8006 | -59.7153 | -59.9075 | 62.883 | 63.208 | 62.8281 | 0.40741 | 0.027465 | 0.018311 | -0.045776 | -0.064087 | 122.7676 | 63.1165 | 122.5708 | 63.0981 | 122.5525 | 0.082397 | 0 | 122.7493 | 122.6257 | 0.19226 | 122.644 | 62.9929 | 122.6624 | -59.9075 | -122.6898 | 62.8006 | 122.644 | 62.8326 | 63.2446
1671.8906 | 122.9416 | -62.8098 | 59.8343 | -0.052796 | -0.0020785 | -0.0079233 | 2.8988 | -0.0020935 | -0.0014184 | -0.00097627 | -0.058258 | 0.16245 | 0.1288 | -0.0010168 | 0.057533 | 0.10436 | 0.0017687 | -0.027466 | 0.059509 | -0.09613 | -0.032043 | 0.050354 | -0.032043 | 0.022888 | 0.50354 | 59.7794 | -62.8235 | 59.8984 | 59.9991 | 59.8251 | 0.28381 | 62.7136 | -59.7748 | -59.8663 | 62.8601 | 62.8326 | 62.7777 | 0.11902 | 0.064087 | -0.013733 | -0.054932 | 0.064086 | 122.8088 | 63.0936 | 122.6349 | 63.1073 | 122.6486 | 0.14648 | 0.064087 | 122.8226 | 122.7219 | 0.15564 | 122.6028 | 62.8693 | 122.5891 | -59.9304 | -122.6578 | 62.7777 | 122.7081 | 62.7823 | 63.3133
1672.8438 | 122.8729 | -62.8098 | 59.8434 | 0.031128 | -0.0014377 | -0.0083505 | 2.9007 | 0.0017517 | 0.00050424 | -0.0022581 | -0.15286 | 0.16459 | 0.12388 | 0.0051782 | 0.056892 | 0.105 | 0.00070073 | 0.022888 | 0.11902 | -0.064087 | -0.018311 | 0.082397 | -0.004578 | 0.027466 | 0.54474 | 59.8297 | -62.8235 | 59.8663 | 59.9625 | 59.7656 | 0.28839 | 62.7457 | -59.7244 | -59.8618 | 62.8922 | 62.8372 | 62.8052 | 0.091553 | 0.059509 | -0.013733 | -0.013733 | 0.022888 | 122.7722 | 63.0981 | 122.5754 | 63.1119 | 122.5891 | 0.14648 | 0.045776 | 122.7859 | 122.6898 | 0.18311 | 122.6532 | 62.9288 | 122.6395 | -59.9075 | -122.6669 | 62.7914 | 122.6761 | 62.8326 | 63.3545
1673.8281 | 122.8729 | -62.796 | 59.8618 | 0.015869 | -0.0022923 | -0.0081369 | 2.9014 | 0.0021789 | 0.001145 | -0.0028989 | -0.16507 | 0.16502 | 0.12623 | -0.0074254 | 0.058815 | 0.10265 | -0.0012219 | 0.027466 | 0.11444 | -0.07782 | -0.018311 | 0.068665 | -0.018311 | 0.013733 | 0.52643 | 59.8114 | -62.8464 | 59.8709 | 59.9579 | 59.7748 | 0.26093 | 62.7182 | -59.7473 | -59.8801 | 62.8647 | 62.8098 | 62.7777 | 0.091553 | 0.059509 | -0.050354 | -0.050354 | 0.009156 | 122.7539 | 63.0569 | 122.5708 | 63.1073 | 122.6212 | 0.14649 | 0.059509 | 122.8043 | 122.7173 | 0.19226 | 122.6578 | 62.9105 | 122.6074 | -59.9396 | -122.7081 | 62.7777 | 122.6669 | 62.8235 | 63.3224
1674.8906 | 122.8821 | -62.7823 | 59.8618 | -0.068054 | -0.0040013 | -0.0096323 | 2.8969 | -0.00059811 | -0.0035548 | -0.0028989 | -0.06131 | 0.16309 | 0.1273 | -0.0042212 | 0.057319 | 0.10329 | 0.0021961 | 0.054932 | 0.10071 | -0.045776 | 0.036621 | 0.13733 | 0.064087 | 0.091553 | 0.58594 | 59.7977 | -62.796 | 59.8938 | 59.9808 | 59.7885 | 0.32959 | 62.7365 | -59.761 | -59.8251 | 62.9196 | 62.8738 | 62.8464 | 0.13733 | 0.10986 | -0.013733 | -0.064087 | 0.032044 | 122.7631 | 63.1119 | 122.5708 | 63.1256 | 122.5845 | 0.18311 | 0.082397 | 122.7768 | 122.6898 | 0.14648 | 122.5937 | 62.883 | 122.58 | -59.9075 | -122.6578 | 62.8189 | 122.6761 | 62.8372 | 63.3682
1675.8438 | 122.85 | -62.8052 | 59.8709 | -0.022278 | -0.0016513 | -0.0081369 | 2.8992 | 0.00068369 | 0.001145 | -0.0022581 | -0.14371 | 0.16373 | 0.1258 | -0.00058965 | 0.058174 | 0.10543 | -0.0018629 | -0.022888 | 0.07782 | -0.11444 | -0.09613 | -0.009155 | -0.09613 | -0.068665 | 0.44403 | 59.7977 | -62.8555 | 59.8251 | 59.9121 | 59.7153 | 0.19226 | 62.6907 | -59.7931 | -59.967 | 62.796 | 62.7365 | 62.709 | 0.045776 | 0.018311 | -0.050354 | -0.073243 | -0.045777 | 122.7173 | 62.9974 | 122.5204 | 63.0478 | 122.5708 | 0.10529 | 0.018311 | 122.7676 | 122.6807 | 0.19226 | 122.6532 | 62.883 | 122.6028 | -59.9854 | -122.7264 | 62.709 | 122.6303 | 62.7823 | 63.2492
1676.8906 | 122.8455 | -62.8052 | 59.9075 | 0.00061049 | 0.00027134 | -0.010273 | 2.8994 | 0.0015381 | 0.00029044 | -0.0031125 | -0.052155 | 0.16074 | 0.12623 | -0.0025122 | 0.056251 | 0.10372 | 0.00027333 | 0.036621 | 0.1236 | -0.045776 | -0.027466 | 0.068665 | -0.013733 | 0.027466 | 0.5127 | 59.8206 | -62.8189 | 59.8297 | 59.9258 | 59.7519 | 0.28381 | 62.7594 | -59.7839 | -59.935 | 62.8738 | 62.8326 | 62.7914 | 0.073242 | 0.032043 | -0.013733 | -0.086975 | -0.07782 | 122.731 | 63.089 | 122.5571 | 63.1027 | 122.5708 | 0.11444 | 0.01831 | 122.7448 | 122.6486 | 0.16937 | 122.6395 | 62.9288 | 122.6257 | -59.9533 | -122.7264 | 62.7777 | 122.6349 | 62.8418 | 63.3179
1677.8594 | 122.8546 | -62.8281 | 59.8663 | -0.075684 | -0.00058326 | -0.0092051 | 2.9007 | 0.0021789 | -0.00013676 | -0.0035397 | -0.13455 | 0.16437 | 0.12815 | 0.00090575 | 0.056892 | 0.10778 | -0.0042127 | -0.013733 | 0.073242 | -0.11444 | -0.086975 | -0.009155 | -0.09613 | -0.045776 | 0.44861 | 59.8022 | -62.8464 | 59.8389 | 59.9167 | 59.7153 | 0.1831 | 62.7136 | -59.7931 | -59.9533 | 62.8189 | 62.7823 | 62.7319 | 0.068665 | 0.018311 | -0.018311 | -0.064087 | -0.027466 | 122.7448 | 63.0112 | 122.5433 | 63.0295 | 122.5616 | 0.10529 | 0.027466 | 122.7631 | 122.6852 | 0.18768 | 122.6486 | 62.9013 | 122.6303 | -59.9808 | -122.7127 | 62.7411 | 122.6669 | 62.8143 | 63.2767
1678.8906 | 122.9141 | -62.7914 | 59.8022 | -0.037537 | 5.7742e-05 | -0.0077097 | 2.898 | 0.0013245 | -0.0012048 | -0.00076267 | -0.067413 | 0.16224 | 0.12709 | -0.0025122 | 0.055397 | 0.10479 | 0.00027333 | -0.036621 | 0.009155 | -0.10986 | -0.054932 | 0.073242 | -0.07782 | -0.013733 | 0.48981 | 59.7382 | -62.8464 | 59.8892 | 59.9625 | 59.7839 | 0.21057 | 62.6816 | -59.7931 | -59.8572 | 62.8647 | 62.7777 | 62.7136 | 0.09613 | 0.032043 | -0.054932 | -0.064087 | 0.086975 | 122.7539 | 63.002 | 122.5754 | 63.0569 | 122.6303 | 0.18311 | 0.054931 | 122.8088 | 122.7356 | 0.11902 | 122.5845 | 62.8006 | 122.5296 | -59.9121 | -122.6486 | 62.7365 | 122.6807 | 62.7548 | 63.2812
1679.8281 | 122.8729 | -62.8555 | 59.8526 | -0.022278 | -0.00079686 | -0.0066415 | 2.8992 | 0.0045289 | 0.00071784 | -0.0039671 | -0.1376 | 0.1648 | 0.1288 | -0.0018712 | 0.056678 | 0.10585 | -0.0014355 | -0.10071 | 0.032043 | -0.16937 | 0.26093 | 0.082397 | -0.25635 | -0.004578 | 0.39368 | 59.7977 | -62.851 | 59.8206 | 59.8938 | 59.6832 | 0.13733 | 62.6862 | -59.8206 | -59.5917 | 62.9379 | 62.851 | 62.5992 | 0.16479 | -0.086975 | 0.004578 | -0.054932 | -0.032043 | 122.7493 | 62.9929 | 122.5388 | 62.9883 | 122.5342 | 0.25177 | 0.4303 | 122.7448 | 122.6715 | 0.20142 | 122.6486 | 62.8876 | 122.6532 | -60.022 | -122.7036 | 63.1165 | 122.6761 | 62.7548 | 63.2492
1680.8906 | 122.9462 | -62.8281 | 59.7977 | -0.052796 | 5.7742e-05 | -0.0070687 | 2.899 | -0.0035889 | 0.00029044 | -0.0028989 | -0.094879 | 0.16181 | 0.12495 | -0.0063574 | 0.056678 | 0.10521 | -0.0029309 | -0.018311 | -0.022888 | -0.15106 | -0.068665 | 0.022888 | -0.073242 | -0.045776 | 0.48981 | 59.7427 | -62.8372 | 59.935 | 59.9579 | 59.6695 | 0.027466 | 62.677 | -59.8206 | -59.8663 | 62.851 | 62.7823 | 62.7548 | 0.10529 | 0.07782 | -0.009155 | -0.054931 | 0.13733 | 122.7859 | 62.8555 | 122.4976 | 62.8647 | 122.5067 | 0.17395 | 0.082397 | 122.7951 | 122.7722 | 0.12817 | 122.58 | 62.8052 | 122.5708 | -59.9487 | -122.6349 | 62.7594 | 122.7631 | 62.8098 | 63.3179
1681.8281 | 122.8867 | -62.796 | 59.8663 | 0.00061049 | -0.0022923 | -0.0094187 | 2.9014 | -0.0025207 | -0.00077756 | -0.0016171 | -0.088776 | 0.16395 | 0.12773 | -0.0010168 | 0.056678 | 0.105 | -0.0016493 | -0.022888 | 0.1236 | -0.082397 | -0.054932 | 0.054932 | 0.009155 | 0.022888 | 0.48523 | 59.8068 | -62.8235 | 59.8389 | 59.935 | 59.761 | 0.29755 | 62.7136 | -59.7427 | -59.9213 | 62.851 | 62.8189 | 62.8052 | 0.10528 | 0.091552 | -0.027465 | -0.059509 | -0.027466 | 122.731 | 63.0936 | 122.5571 | 63.121 | 122.5845 | 0.13733 | 0.027465 | 122.7585 | 122.6624 | 0.20599 | 122.6303 | 62.9196 | 122.6028 | -59.9487 | -122.6898 | 62.7411 | 122.6349 | 62.7731 | 63.2812
1682.9219 | 122.8683 | -62.8189 | 59.8618 | -0.029907 | -0.0020785 | -0.0083505 | 2.898 | 0.0011109 | -0.00013676 | -0.0026853 | -0.046051 | 0.16331 | 0.12645 | -0.0035802 | 0.057533 | 0.10308 | -0.0063489 | 0.045776 | 0.10529 | -0.032043 | 0.041199 | 0.14191 | 0.059509 | 0.082397 | 0.5722 | 59.7931 | -62.8052 | 59.8801 | 59.9762 | 59.7839 | 0.32044 | 62.7869 | -59.7565 | -59.8206 | 62.9608 | 62.9013 | 62.8784 | 0.11444 | 0.091552 | 0.013733 | -0.068664 | 0.018311 | 122.7951 | 63.1393 | 122.6028 | 63.1256 | 122.5891 | 0.17395 | 0.073242 | 122.7814 | 122.6852 | 0.13733 | 122.5983 | 62.9242 | 122.612 | -59.8938 | -122.6669 | 62.8601 | 122.699 | 62.8647 | 63.3911
1683.8281 | 122.8912 | -62.8235 | 59.8709 | -0.068054 | 0.00027134 | -0.0070687 | 2.8992 | 0.00025629 | 0.00029044 | -0.00076267 | -0.15897 | 0.16309 | 0.12666 | -0.0025122 | 0.059669 | 0.10479 | -0.0052809 | 0.018311 | 0.09613 | -0.068665 | -0.036621 | 0.068665 | -0.050354 | 0 | 0.53558 | 59.8022 | -62.8372 | 59.8938 | 59.9396 | 59.7565 | 0.25177 | 62.7548 | -59.7748 | -59.9075 | 62.8922 | 62.8235 | 62.7731 | 0.068665 | 0.018311 | -0.013733 | -0.068665 | 0.022888 | 122.7631 | 63.0753 | 122.58 | 63.089 | 122.5937 | 0.13733 | 0.032044 | 122.7768 | 122.731 | 0.16479 | 122.6395 | 62.9196 | 122.6257 | -59.9396 | -122.7081 | 62.7869 | 122.7173 | 62.8418 | 63.3591
1684.8906 | 122.9416 | -62.764 | 59.8526 | -0.037537 | -0.0025059 | -0.0072825 | 2.899 | 0.00089729 | -0.00099116 | -0.0037533 | -0.030792 | 0.1616 | 0.12516 | -0.011271 | 0.058815 | 0.10479 | -0.0010083 | 0.050354 | 0.064087 | -0.032043 | 0.07782 | 0.19226 | 0.091553 | 0.10986 | 0.62256 | 59.7656 | -62.8098 | 59.9304 | 60.0586 | 59.8846 | 0.35706 | 62.7319 | -59.7885 | -59.7748 | 62.9562 | 62.8738 | 62.8555 | 0.14191 | 0.1236 | -0.045776 | -0.086975 | 0.07782 | 122.8226 | 63.121 | 122.6486 | 63.1668 | 122.6944 | 0.2243 | 0.10986 | 122.8683 | 122.7402 | 0.09613 | 122.5754 | 62.8281 | 122.5296 | -59.8846 | -122.6624 | 62.8418 | 122.6944 | 62.8143 | 63.3865
1685.8281 | 122.8317 | -62.8189 | 59.8572 | 0.00824 | -0.00015586 | -0.0060007 | 2.8988 | 0.0019653 | -0.00099116 | -0.00033547 | -0.12845 | 0.16309 | 0.12986 | 0.0015466 | 0.057533 | 0.105 | -0.0065625 | 0 | 0.054932 | -0.10529 | -0.050354 | 0.032043 | -0.07782 | -0.027466 | 0.49439 | 59.816 | -62.8098 | 59.8343 | 59.9258 | 59.7382 | 0.21515 | 62.7136 | -59.8022 | -59.9075 | 62.851 | 62.7914 | 62.7411 | 0.07782 | 0.027466 | 0.009156 | -0.041199 | -0.022888 | 122.7448 | 63.0341 | 122.5571 | 63.0249 | 122.5479 | 0.13733 | 0.054932 | 122.7356 | 122.644 | 0.16022 | 122.6257 | 62.8738 | 122.6349 | -59.9625 | -122.6669 | 62.7686 | 122.6532 | 62.8189 | 63.3133
1686.8281 | 122.8729 | -62.8464 | 59.8389 | -0.045166 | 5.7742e-05 | -0.0079233 | 2.9005 | 0.0019653 | -0.0018458 | -0.0056759 | -0.14676 | 0.16288 | 0.12858 | -0.0059302 | 0.057533 | 0.10393 | -0.0031445 | -0.10071 | 0.027466 | -0.17395 | 0.20599 | -0.041199 | -0.20599 | 0.032043 | 0.39368 | 59.7931 | -62.8464 | 59.8206 | 59.8846 | 59.697 | 0.14648 | 62.6724 | -59.8114 | -59.6329 | 62.8052 | 62.8784 | 62.6404 | 0.20599 | -0.032044 | 0 | -0.045776 | -0.01831 | 122.731 | 62.9929 | 122.5433 | 62.9929 | 122.5433 | 0.13275 | 0.37994 | 122.731 | 122.6669 | 0.20142 | 122.6395 | 62.8738 | 122.6395 | -60.0128 | -122.6852 | 63.0524 | 122.6669 | 62.7457 | 63.2401
1687.8906 | 122.9919 | -62.7731 | 59.8251 | -0.037537 | -0.00036966 | -0.0064279 | 2.8956 | 4.2692e-05 | -0.00013676 | -0.0033261 | -0.039948 | 0.16181 | 0.12944 | -0.0027258 | 0.057319 | 0.10372 | -0.0012219 | 0.036621 | 0.050354 | -0.059509 | 0.041199 | 0.17395 | 0.086975 | 0.09613 | 0.63629 | 59.7565 | -62.796 | 59.967 | 60.0677 | 59.9075 | 0.3479 | 62.7136 | -59.7748 | -59.7839 | 62.9471 | 62.8693 | 62.8601 | 0.15564 | 0.14648 | -0.022889 | -0.068664 | 0.14191 | 122.8409 | 63.121 | 122.6807 | 63.1439 | 122.7036 | 0.23346 | 0.10071 | 122.8638 | 122.7631 | 0.10986 | 122.5525 | 62.8235 | 122.5296 | -59.8846 | -122.6212 | 62.8143 | 122.7402 | 62.8098 | 63.4094
1688.8281 | 122.9416 | -62.7869 | 59.848 | 0.031128 | 5.7742e-05 | -0.0083505 | 2.8986 | 0.0019653 | 0.00050424 | -0.0041807 | -0.042999 | 0.16181 | 0.12687 | -0.0044348 | 0.056678 | 0.10372 | -0.00058107 | 0.009155 | 0.064087 | -0.054932 | 0.045776 | 0.14191 | 0.064087 | 0.10071 | 0.60425 | 59.7702 | -62.8464 | 59.903 | 60.0174 | 59.8297 | 0.33417 | 62.7319 | -59.7839 | -59.8022 | 62.9288 | 62.8876 | 62.851 | 0.15564 | 0.11902 | -0.05951 | -0.077819 | 0.054932 | 122.8043 | 63.121 | 122.6166 | 63.1805 | 122.6761 | 0.19684 | 0.10071 | 122.8638 | 122.7493 | 0.11902 | 122.6166 | 62.851 | 122.5571 | -59.903 | -122.6944 | 62.8326 | 122.6898 | 62.796 | 63.3911
1689.8906 | 122.9462 | -62.796 | 59.848 | -0.037537 | -0.00015586 | -0.0092051 | 2.8984 | 0.0011109 | -0.0024866 | -0.0039671 | -0.049103 | 0.16117 | 0.12687 | -0.0087072 | 0.05561 | 0.10393 | -0.0027173 | -0.032043 | 0.050354 | -0.082397 | -0.032043 | 0.068665 | -0.022888 | 0.036621 | 0.51727 | 59.7977 | -62.8281 | 59.8984 | 59.9991 | 59.8251 | 0.29755 | 62.7136 | -59.7977 | -59.8801 | 62.8647 | 62.8326 | 62.7731 | 0.11902 | 0.059509 | -0.032043 | -0.050354 | 0.050354 | 122.7951 | 63.0936 | 122.6212 | 63.1256 | 122.6532 | 0.15106 | 0.050354 | 122.8271 | 122.7264 | 0.13275 | 122.6257 | 62.8464 | 122.5937 | -59.9304 | -122.6761 | 62.764 | 122.6944 | 62.764 | 63.3133
1690.8281 | 122.8683 | -62.7869 | 59.9396 | 0.015869 | -0.0018649 | -0.0096323 | 2.8975 | 0.0023925 | 0.00071784 | 9.193e-05 | -0.088776 | 0.16587 | 0.12901 | 0.0062464 | 0.057106 | 0.10201 | 0.0013415 | 0.004578 | 0.15106 | -0.054932 | -0.009155 | 0.068665 | -0.004578 | 0.027466 | 0.50354 | 59.8297 | -62.8418 | 59.816 | 59.9258 | 59.729 | 0.28381 | 62.7319 | -59.7885 | -59.9487 | 62.8555 | 62.8143 | 62.7823 | 0.082398 | 0.050354 | -0.054932 | -0.10986 | -0.1236 | 122.7127 | 63.0707 | 122.5159 | 63.1256 | 122.5708 | 0.1236 | 0.045777 | 122.7676 | 122.6578 | 0.20599 | 122.6715 | 62.9379 | 122.6166 | -59.9945 | -122.7814 | 62.7777 | 122.6028 | 62.7914 | 63.2904
1691.8906 | 122.8638 | -62.8189 | 59.8846 | 0.00061049 | 0.00069854 | -0.0077097 | 2.8986 | -0.0010253 | 7.6842e-05 | -0.00076267 | -0.088776 | 0.16224 | 0.12687 | 0.0028284 | 0.057533 | 0.10415 | -0.0012219 | 0.050354 | 0.11902 | -0.045776 | -0.022888 | 0.073242 | -0.004578 | 0.032043 | 0.55389 | 59.816 | -62.8281 | 59.8343 | 59.9396 | 59.7519 | 0.28381 | 62.7731 | -59.7656 | -59.9075 | 62.8922 | 62.851 | 62.8143 | 0.077819 | 0.041198 | -0.009155 | -0.068665 | -0.050354 | 122.7585 | 63.1027 | 122.5708 | 63.1119 | 122.58 | 0.11902 | 0.022888 | 122.7676 | 122.6624 | 0.16479 | 122.644 | 62.9379 | 122.6349 | -59.9304 | -122.7127 | 62.796 | 122.6532 | 62.8693 | 63.3728
1692.8438 | 122.8317 | -62.8418 | 59.8663 | -0.037537 | -0.00079686 | -0.0079233 | 2.8988 | 0.0032471 | -0.0018458 | 0.0032961 | -0.16202 | 0.16309 | 0.12815 | 5.1352e-05 | 0.055183 | 0.10607 | -0.0050671 | -0.054932 | 0.068665 | -0.11902 | -0.11444 | -0.064087 | -0.15564 | -0.10529 | 0.37537 | 59.8068 | -62.8418 | 59.8022 | 59.8572 | 59.6649 | 0.13733 | 62.7228 | -59.7977 | -59.9808 | 62.7777 | 62.7365 | 62.6862 | 0.013733 | -0.036621 | 0 | -0.059509 | -0.064087 | 122.699 | 62.9791 | 122.5067 | 62.9791 | 122.5067 | 0.054932 | 0.004578 | 122.699 | 122.644 | 0.18768 | 122.6486 | 62.9105 | 122.6486 | -59.9854 | -122.7081 | 62.7274 | 122.644 | 62.7869 | 63.2172
1693.8438 | 122.9736 | -62.7502 | 59.8343 | -0.014649 | -0.00036966 | -0.0074961 | 2.896 | 0.0013245 | 0.00071784 | -0.0026853 | -0.030792 | 0.16267 | 0.12324 | -0.010203 | 0.056892 | 0.10415 | 5.9726e-05 | 0.013733 | 0.059509 | -0.086975 | -0.004578 | 0.10986 | 0.045776 | 0.086975 | 0.55847 | 59.7656 | -62.8281 | 59.9258 | 60.0266 | 59.8801 | 0.32044 | 62.6633 | -59.7748 | -59.8389 | 62.8601 | 62.8372 | 62.796 | 0.17395 | 0.13275 | -0.07782 | -0.068665 | 0.091552 | 122.7768 | 63.0707 | 122.6303 | 63.1485 | 122.7081 | 0.19684 | 0.082397 | 122.8546 | 122.7539 | 0.14648 | 122.5937 | 62.8098 | 122.5159 | -59.9213 | -122.6624 | 62.7457 | 122.6761 | 62.764 | 63.3087
1694.8906 | 122.8683 | -62.796 | 59.8572 | -0.014649 | -0.00058326 | -0.0092051 | 2.8986 | 0.0013245 | -0.00035036 | -0.00097627 | -0.07962 | 0.16138 | 0.12837 | -0.0052892 | 0.057106 | 0.10201 | -0.00058107 | 0.059509 | 0.091553 | -0.041199 | 0.032043 | 0.11444 | 0.027466 | 0.07782 | 0.58136 | 59.8251 | -62.8326 | 59.8663 | 59.9533 | 59.7656 | 0.27008 | 62.7548 | -59.7656 | -59.8251 | 62.9105 | 62.8738 | 62.8235 | 0.11902 | 0.068665 | -0.036621 | -0.032044 | 0.009155 | 122.7493 | 63.0661 | 122.5616 | 63.1027 | 122.5983 | 0.15564 | 0.073242 | 122.7859 | 122.699 | 0.13275 | 122.6578 | 62.8876 | 122.6212 | -59.8984 | -122.6898 | 62.8281 | 122.6624 | 62.8555 | 63.3774
1695.8281 | 122.8546 | -62.8464 | 59.8755 | -0.022278 | -0.0027195 | -0.0087777 | 2.8975 | 0.00089729 | -0.0012048 | -0.0024717 | -0.10098 | 0.16202 | 0.12773 | 0.003042 | 0.058387 | 0.10286 | 0.0019823 | -0.013733 | 0.16479 | -0.041199 | -0.045776 | 0.49896 | 0.32959 | -0.17853 | 0.44861 | 59.8251 | -62.8738 | 59.8434 | 59.9167 | 59.761 | 0.28839 | 62.8052 | -59.7107 | -59.9213 | 63.3453 | 62.6678 | 63.176 | -0.13733 | 0.37079 | -0.027465 | -0.050354 | -0.032043 | 122.7631 | 63.1348 | 122.6074 | 63.1622 | 122.6349 | 0.54016 | -0.004577 | 122.7905 | 122.7173 | 0.20599 | 122.699 | 63.0112 | 122.6715 | -59.9167 | -122.7493 | 62.8006 | 122.6898 | 62.8326 | 63.295
1696.8281 | 122.8775 | -62.8235 | 59.8709 | 0.023498 | 0.00048494 | -0.0081369 | 2.8997 | 0.0021789 | -0.0016322 | -0.0018307 | -0.049103 | 0.16502 | 0.13029 | -0.0063574 | 0.05796 | 0.10628 | -0.0012219 | 0 | 0.1831 | -0.022888 | -0.022888 | 0.059509 | -0.009155 | 0.17395 | 0.35706 | 59.8343 | -62.8372 | 59.8022 | 59.9304 | 59.7473 | 0.29297 | 62.8006 | -59.6878 | -59.8938 | 62.883 | 62.9974 | 62.8143 | 0.19684 | 0.013733 | -0.013733 | -0.036621 | -0.068665 | 122.7539 | 63.1165 | 122.5708 | 63.1302 | 122.5845 | 0.082397 | 0 | 122.7676 | 122.6395 | 0.20599 | 122.6715 | 63.0066 | 122.6578 | -59.8938 | -122.7081 | 62.8006 | 122.6257 | 62.8235 | 63.1805
1697.9062 | 122.8821 | -62.8235 | 59.8755 | 0.031128 | -0.00079686 | -0.0081369 | 2.8958 | 0.0026063 | -0.0037684 | -0.0043943 | -0.1376 | 0.16202 | 0.12602 | 0.0032556 | 0.055824 | 0.10415 | -0.0050671 | 0.018311 | 0.10986 | -0.064087 | -0.036621 | 0.068665 | -0.027466 | 0.004578 | 0.54932 | 59.8114 | -62.8372 | 59.8892 | 59.9533 | 59.7519 | 0.27466 | 62.7594 | -59.7656 | -59.9121 | 62.8922 | 62.8281 | 62.796 | 0.068665 | 0.036621 | -0.013733 | -0.064087 | 0.013733 | 122.7768 | 63.0981 | 122.5754 | 63.1119 | 122.5891 | 0.13275 | 0.027466 | 122.7905 | 122.7264 | 0.17395 | 122.6486 | 62.9333 | 122.6349 | -59.9396 | -122.7127 | 62.7869 | 122.7127 | 62.8418 | 63.3728
1698.8281 | 122.8912 | -62.8418 | 59.8892 | 0.00824 | -0.00058326 | -0.0089913 | 2.8967 | 0.0023925 | -0.0016322 | -0.0033261 | -0.091827 | 0.16587 | 0.13093 | -0.011698 | 0.056465 | 0.10735 | 0.0034777 | 0.004578 | 0.15564 | -0.045776 | -0.032043 | 0.059509 | -0.018311 | 0.032043 | 0.50354 | 59.8251 | -62.8281 | 59.7336 | 60.0082 | 59.6741 | 0.23804 | 62.796 | -59.7336 | -59.9213 | 62.9013 | 62.8738 | 62.8235 | 0.077819 | 0.027465 | 0.013733 | -0.064087 | -0.15564 | 122.85 | 63.0798 | 122.5159 | 63.0661 | 122.5021 | 0.10528 | 0.013733 | 122.8363 | 122.5616 | 0.20142 | 122.6532 | 62.9974 | 122.6669 | -59.935 | -122.7173 | 62.8098 | 122.5754 | 62.8464 | 63.3453
1699.8906 | 122.9553 | -62.796 | 59.8389 | 0.00061049 | 0.0015529 | -0.0068551 | 2.8969 | 0.0043151 | 0.00093144 | -0.00054907 | -0.049103 | 0.16288 | 0.12986 | 0.00026495 | 0.057106 | 0.10564 | -0.00079467 | -0.022888 | 0.050354 | -0.091553 | -0.036621 | 0.054932 | -0.009155 | 0.050354 | 0.5127 | 59.7565 | -62.8143 | 59.8938 | 59.9945 | 59.8389 | 0.27466 | 62.7045 | -59.7885 | -59.8755 | 62.851 | 62.8464 | 62.7869 | 0.14191 | 0.082398 | -0.01831 | -0.082397 | 0.054932 | 122.7905 | 63.0707 | 122.6349 | 63.089 | 122.6532 | 0.14649 | 0.054932 | 122.8088 | 122.7081 | 0.14191 | 122.5708 | 62.8464 | 122.5525 | -59.9304 | -122.6532 | 62.7594 | 122.6898 | 62.7731 | 63.3087
1700.8281 | 122.9004 | -62.7914 | 59.9258 | 0.023498 | -0.00036966 | -0.0096323 | 2.8986 | 0.00046989 | -0.0027002 | -0.0018307 | -0.11014 | 0.16373 | 0.12901 | 0.0024012 | 0.057319 | 0.1035 | -0.0010083 | 0.009155 | 0.16479 | -0.050354 | -0.032043 | 0.064087 | 0 | 0.059509 | 0.50812 | 59.8297 | -62.8555 | 59.8251 | 59.935 | 59.7198 | 0.28839 | 62.7411 | -59.761 | -59.9579 | 62.8555 | 62.851 | 62.7914 | 0.10986 | 0.050354 | -0.064087 | -0.09613 | -0.10071 | 122.7264 | 63.0798 | 122.5113 | 63.1439 | 122.5754 | 0.11444 | 0.018311 | 122.7905 | 122.6807 | 0.21515 | 122.6852 | 62.9562 | 122.6212 | -59.9762 | -122.7814 | 62.7594 | 122.6166 | 62.8006 | 63.2996
1701.8906 | 123.0789 | -62.7457 | 59.9167 | -0.068054 | -0.0012241 | -0.0092051 | 2.8975 | -0.0014527 | -0.0014184 | 0.00094633 | -0.049103 | 0.16181 | 0.12837 | -0.0044348 | 0.054756 | 0.10479 | -0.0022901 | 0.064087 | 0.064087 | -0.027466 | 0.054932 | 0.17395 | 0.082397 | 0.11444 | 0.63629 | 59.7702 | -62.8052 | 59.9258 | 60.0677 | 59.8663 | 0.31586 | 62.7182 | -59.8526 | -59.8618 | 62.9196 | 62.8601 | 62.8281 | 0.14191 | 0.10986 | -0.059509 | -0.14648 | 0.009155 | 122.8134 | 63.0615 | 122.612 | 63.121 | 122.6715 | 0.20142 | 0.082398 | 122.8729 | 122.731 | 0.091553 | 122.5754 | 62.8098 | 122.5159 | -59.9442 | -122.7219 | 62.8006 | 122.6715 | 62.8098 | 63.382
1702.8281 | 122.8592 | -62.8372 | 59.8526 | 0.17609 | -0.00036966 | -0.010273 | 2.8977 | 0.0017517 | -0.002273 | -0.0014035 | -0.15591 | 0.16352 | 0.12751 | 0.0024012 | 0.055397 | 0.10607 | -0.0039991 | -0.14648 | -0.018311 | -0.16022 | -0.14648 | -0.11902 | -0.17853 | -0.10071 | 0.37537 | 59.7931 | -62.8647 | 59.8434 | 59.8801 | 59.7015 | 0.14648 | 62.677 | -59.8709 | -59.9991 | 62.7182 | 62.7365 | 62.6587 | 0.059509 | -0.018311 | -0.027466 | -0.059509 | -0.009155 | 122.7173 | 62.9837 | 122.5388 | 63.0112 | 122.5662 | 0.041198 | 0.013733 | 122.7448 | 122.7081 | 0.14191 | 122.6578 | 62.8189 | 122.6303 | -60.0128 | -122.7173 | 62.6907 | 122.6807 | 62.6907 | 63.2126
1703.8906 | 122.9782 | -62.8006 | 59.8251 | -0.014649 | -0.0020785 | -0.0051461 | 2.8956 | 0.00046989 | 0.002213 | -0.0020443 | -0.030792 | 0.16309 | 0.12773 | -0.014902 | 0.057747 | 0.10607 | -0.00015387 | -0.018311 | 0.036621 | -0.07782 | -0.013733 | 0.09613 | 0.022888 | 0.068665 | 0.54474 | 59.7839 | -62.8281 | 59.9213 | 60.0266 | 59.8389 | 0.31128 | 62.7228 | -59.7885 | -59.8389 | 62.8967 | 62.8693 | 62.8235 | 0.14649 | 0.10071 | -0.027466 | -0.041198 | 0.096131 | 122.8271 | 63.1119 | 122.6395 | 63.1393 | 122.6669 | 0.17395 | 0.064087 | 122.8546 | 122.7493 | 0.11444 | 122.612 | 62.8372 | 122.5845 | -59.903 | -122.6532 | 62.7869 | 122.7219 | 62.7823 | 63.3453
1704.8438 | 122.8729 | -62.8372 | 59.848 | 0.054016 | -0.0016513 | -0.0068551 | 2.8999 | 0.0032471 | -0.0018458 | -0.00054907 | -0.14066 | 0.16245 | 0.1273 | -0.0044348 | 0.055824 | 0.105 | -0.0018629 | -0.18768 | 0 | -0.17853 | -0.19226 | -0.10529 | -0.17853 | -0.10986 | 0.40741 | 59.8068 | -62.8647 | 59.8297 | 59.8892 | 59.7061 | 0.14191 | 62.6587 | -59.848 | -60.0403 | 62.7319 | 62.7274 | 62.6587 | 0.068665 | 0 | -0.027466 | -0.041198 | -0.01831 | 122.7264 | 62.9791 | 122.5433 | 63.0066 | 122.5708 | 0.073242 | -0.013733 | 122.7539 | 122.6944 | 0.17853 | 122.6715 | 62.8372 | 122.644 | -60.0266 | -122.7127 | 62.645 | 122.6669 | 62.6495 | 63.2446
1705.8906 | 122.9874 | -62.8143 | 59.8526 | -0.068054 | -0.00079686 | -0.0072825 | 2.8969 | 0.0032471 | 0.001145 | -0.0033261 | -0.036896 | 0.16352 | 0.12687 | -0.0050756 | 0.058387 | 0.10415 | -0.00079467 | -0.009155 | 0.050354 | -0.082397 | -0.022888 | 0.073242 | -0.009155 | 0.036621 | 0.52643 | 59.7885 | -62.8418 | 59.9075 | 60.0128 | 59.848 | 0.30212 | 62.7319 | -59.8022 | -59.8755 | 62.8876 | 62.851 | 62.8052 | 0.11902 | 0.073242 | -0.027466 | -0.064087 | 0.054932 | 122.8271 | 63.1165 | 122.6624 | 63.1439 | 122.6898 | 0.15564 | 0.059509 | 122.8546 | 122.7493 | 0.13275 | 122.6303 | 62.8647 | 122.6028 | -59.935 | -122.6944 | 62.7914 | 122.7219 | 62.8052 | 63.3408
1706.8281 | 122.8317 | -62.8464 | 59.8618 | -0.007019 | -0.0014377 | -0.0096323 | 2.8973 | 0.0013245 | -0.0037684 | -0.0014035 | -0.10709 | 0.16437 | 0.12773 | 0.00069215 | 0.056465 | 0.105 | -0.0020765 | 0 | 0.15564 | -0.045776 | -0.032043 | 0.041199 | -0.018311 | 0.032043 | 0.49439 | 59.8297 | -62.8464 | 59.7473 | 59.8663 | 59.7656 | 0.27466 | 62.8006 | -59.7061 | -59.8938 | 62.8876 | 62.8784 | 62.8281 | 0.077819 | 0.027465 | 0 | -0.032043 | -0.11444 | 122.7127 | 63.121 | 122.612 | 63.121 | 122.612 | 0.086975 | 0.013733 | 122.7127 | 122.5937 | 0.20142 | 122.6761 | 63.002 | 122.6761 | -59.9075 | -122.7081 | 62.8143 | 122.5937 | 62.8464 | 63.3408
1707.9062 | 122.9141 | -62.8052 | 59.8755 | -0.014649 | -0.00079686 | -0.0092051 | 2.8997 | -0.00038451 | -0.0024866 | -0.00054907 | -0.15286 | 0.16331 | 0.12709 | -0.0029394 | 0.055183 | 0.10628 | -0.0010083 | 0.004578 | 0.13275 | -0.07782 | -0.018311 | 0.073242 | -0.036621 | 0.009155 | 0.53101 | 59.8068 | -62.8372 | 59.8984 | 59.9579 | 59.761 | 0.30212 | 62.7274 | -59.7427 | -59.8938 | 62.8784 | 62.8143 | 62.7686 | 0.086975 | 0.041199 | -0.032043 | -0.068664 | 0.022888 | 122.7631 | 63.1073 | 122.5662 | 63.1393 | 122.5983 | 0.15106 | 0.059509 | 122.7951 | 122.7356 | 0.21057 | 122.644 | 62.9379 | 122.612 | -59.9533 | -122.7127 | 62.7869 | 122.7036 | 62.8098 | 63.3362
1708.8281 | 122.85 | -62.8418 | 59.8892 | 0.00061049 | -0.0018649 | -0.0087777 | 2.8992 | -0.0010253 | -0.0044092 | 0.00051913 | -0.094879 | 0.16352 | 0.12901 | -0.0025122 | 0.059456 | 0.10457 | -0.0022901 | 0 | 0.15106 | -0.050354 | -0.036621 | 0.054932 | -0.009155 | 0.054932 | 0.5127 | 59.848 | -62.8326 | 59.8251 | 59.9304 | 59.7473 | 0.28839 | 62.7914 | -59.7382 | -59.9258 | 62.8967 | 62.8967 | 62.8326 | 0.10529 | 0.041199 | 0.009155 | -0.041199 | -0.064087 | 122.7722 | 63.1302 | 122.5891 | 63.121 | 122.58 | 0.10529 | 0.013733 | 122.7631 | 122.6578 | 0.20142 | 122.6807 | 62.9929 | 122.6898 | -59.9396 | -122.7219 | 62.8052 | 122.6669 | 62.8418 | 63.3545
1709.9062 | 122.8867 | -62.8098 | 59.8801 | 0.046386 | 0.00069854 | -0.0074961 | 2.8975 | 0.0013245 | -0.0041956 | -0.0033261 | -0.15286 | 0.16437 | 0.13157 | 0.0015466 | 0.056465 | 0.10671 | 0.00070073 | 0.018311 | 0.082397 | -0.091553 | -0.054932 | 0.050354 | -0.050354 | -0.009155 | 0.42572 | 59.7794 | -62.8693 | 59.8709 | 59.9487 | 59.7794 | 0.28381 | 62.7182 | -59.7977 | -59.935 | 62.8601 | 62.8006 | 62.7594 | 0.082398 | 0.041199 | -0.05951 | -0.10071 | -0.009155 | 122.7585 | 63.0936 | 122.5891 | 63.1531 | 122.6486 | 0.14191 | 0.036621 | 122.818 | 122.7402 | 0.17395 | 122.6486 | 62.8922 | 122.5891 | -59.9716 | -122.7493 | 62.7548 | 122.6807 | 62.8281 | 63.2355
1710.8281 | 122.8638 | -62.8464 | 59.8846 | -0.007019 | -0.0020785 | -0.0074961 | 2.8967 | -0.00017091 | -0.0018458 | 0.00030553 | -0.085724 | 0.16459 | 0.12666 | -0.011057 | 0.056678 | 0.10457 | -0.00015387 | 0 | 0.12817 | -0.059509 | -0.032043 | 0.068665 | 0 | 0.045776 | 0.5127 | 59.816 | -62.8372 | 59.8297 | 59.935 | 59.7702 | 0.28381 | 62.7869 | -59.7565 | -59.9167 | 62.915 | 62.8922 | 62.8464 | 0.10528 | 0.059509 | 0.009156 | -0.068665 | -0.054932 | 122.7814 | 63.1302 | 122.6166 | 63.121 | 122.6074 | 0.12817 | 0.027466 | 122.7722 | 122.6669 | 0.18768 | 122.6532 | 62.9745 | 122.6624 | -59.9442 | -122.7219 | 62.8143 | 122.6761 | 62.8464 | 63.3591
1711.8906 | 122.9416 | -62.7869 | 59.8526 | -0.068054 | 0.00091214 | -0.0085641 | 2.8973 | 0.00089729 | 0.00050424 | -0.00012167 | -0.049103 | 0.16352 | 0.12794 | -0.0091344 | 0.057106 | 0.10308 | 0.0013415 | -0.009155 | 0.045776 | -0.082397 | -0.013733 | 0.10986 | -0.004578 | 0.054932 | 0.55847 | 59.7794 | -62.8281 | 59.9167 | 60.0403 | 59.8572 | 0.31128 | 62.7045 | -59.8068 | -59.8663 | 62.8967 | 62.8418 | 62.7823 | 0.13733 | 0.077819 | -0.041199 | -0.073242 | 0.064087 | 122.8271 | 63.0981 | 122.644 | 63.1393 | 122.6852 | 0.19226 | 0.068664 | 122.8683 | 122.7448 | 0.12817 | 122.6074 | 62.8326 | 122.5662 | -59.935 | -122.6807 | 62.7731 | 122.7036 | 62.7777 | 63.3453
1712.8438 | 122.9462 | -62.8281 | 59.8343 | 0.023498 | 5.7742e-05 | -0.0087777 | 2.8958 | -0.0018799 | 0.00093144 | -0.0018307 | -0.049103 | 0.16459 | 0.12709 | -0.0022986 | 0.058174 | 0.1035 | -0.0012219 | -0.054932 | 0.022888 | -0.091553 | -0.054932 | 0.036621 | -0.041199 | 0.022888 | 0.60425 | 59.7839 | -62.8098 | 59.8938 | 59.9945 | 59.7885 | 0.24261 | 62.7365 | -59.8114 | -59.8892 | 62.8647 | 62.851 | 62.7869 | 0.11444 | 0.050354 | 0.018311 | -0.050354 | 0.059509 | 122.8226 | 63.0707 | 122.6166 | 63.0524 | 122.5983 | 0.12817 | 0.036621 | 122.8043 | 122.7036 | 0.11444 | 122.5937 | 62.851 | 122.612 | -59.9258 | -122.644 | 62.7731 | 122.7219 | 62.7731 | 63.4323
1713.8906 | 122.9462 | -62.8052 | 59.8343 | -0.014649 | -0.00058326 | -0.0060007 | 2.898 | 0.00025629 | 0.001145 | -0.0052487 | -0.085724 | 0.16437 | 0.12815 | -0.0025122 | 0.056465 | 0.10607 | -0.00036747 | -0.041199 | -0.018311 | -0.10529 | -0.064087 | 0.045776 | -0.07782 | -0.018311 | 0.46692 | 59.7565 | -62.8235 | 59.8663 | 59.9442 | 59.8022 | 0.21515 | 62.6999 | -59.8526 | -59.8984 | 62.851 | 62.7869 | 62.7274 | 0.086975 | 0.027466 | -0.01831 | -0.07782 | 0.032043 | 122.7493 | 63.0203 | 122.6074 | 63.0386 | 122.6257 | 0.15106 | 0.041199 | 122.7676 | 122.6898 | 0.086975 | 122.58 | 62.7869 | 122.5616 | -59.9396 | -122.6578 | 62.7411 | 122.6715 | 62.764 | 63.2721
1714.8438 | 122.8546 | -62.8555 | 59.848 | -0.068054 | -0.0014377 | -0.0053599 | 2.8984 | -0.0018799 | 0.00093144 | -0.00012167 | -0.1315 | 0.16331 | 0.12858 | -0.004862 | 0.056251 | 0.10393 | -0.0031445 | -0.09613 | 0.036621 | -0.16937 | -0.28381 | -0.027466 | 0.009155 | -0.086975 | 0.35706 | 59.8206 | -62.8555 | 59.8343 | 59.8709 | 59.697 | 0.15564 | 62.6862 | -59.8114 | -60.1318 | 62.8281 | 62.7686 | 62.8647 | 0.082398 | 0.17853 | 0 | -0.027465 | -0.013732 | 122.7264 | 63.0112 | 122.5525 | 63.0112 | 122.5525 | 0.14191 | -0.11444 | 122.7264 | 122.6898 | 0.20599 | 122.6761 | 62.8922 | 122.6761 | -60.0174 | -122.7036 | 62.5717 | 122.6898 | 62.7594 | 63.2126
1715.8906 | 122.8592 | -62.8143 | 59.8526 | -0.022278 | -0.0031467 | -0.010059 | 2.8988 | -0.0027343 | -0.00099116 | -0.0037533 | -0.19864 | 0.16309 | 0.1288 | -0.0029394 | 0.058601 | 0.105 | -0.0020765 | -0.009155 | 0.16479 | -0.032043 | -0.041199 | 0.013733 | 0.54474 | 0.31128 | 0.53101 | 59.8206 | -62.8418 | 59.8434 | 59.9258 | 59.7427 | 0.27924 | 62.7823 | -59.6878 | -59.8938 | 62.8281 | 63.1256 | 63.3591 | 0.34332 | 0.57678 | -0.027466 | -0.032043 | -0.009155 | 122.7402 | 63.0936 | 122.5571 | 63.121 | 122.5845 | 0.045776 | -0.009156 | 122.7676 | 122.6852 | 0.19684 | 122.6624 | 62.9791 | 122.6349 | -59.8846 | -122.6944 | 62.7731 | 122.6578 | 62.8052 | 63.3453
1716.8281 | 122.8775 | -62.796 | 59.8938 | -0.007019 | -0.0025059 | -0.0085641 | 2.8988 | -0.0038025 | -0.0012048 | -0.0020443 | -0.067413 | 0.16331 | 0.12709 | 0.0034692 | 0.056251 | 0.10286 | -0.0022901 | 0.059509 | 0.10529 | -0.027466 | 0.004578 | 0.10986 | 0.022888 | 0.073242 | 0.56763 | 59.8297 | -62.8326 | 59.8663 | 59.9625 | 59.7656 | 0.28381 | 62.7686 | -59.7885 | -59.8892 | 62.9059 | 62.8693 | 62.8189 | 0.10071 | 0.050354 | -0.036621 | -0.064087 | -0.027466 | 122.7585 | 63.0798 | 122.5616 | 63.1165 | 122.5983 | 0.13733 | 0.032044 | 122.7951 | 122.699 | 0.13275 | 122.6624 | 62.9013 | 122.6257 | -59.9213 | -122.7264 | 62.8006 | 122.6624 | 62.8555 | 63.3636
1717.8906 | 122.9828 | -62.7777 | 59.8343 | -0.029907 | -0.00015586 | -0.0087777 | 2.8954 | -0.0025207 | -0.002273 | -0.00076267 | -0.033844 | 0.16309 | 0.1305 | -0.0029394 | 0.05796 | 0.10329 | -0.0018629 | 0.022888 | 0.059509 | -0.068665 | 0 | 0.1236 | 0.032043 | 0.10071 | 0.60883 | 59.7565 | -62.8281 | 59.9533 | 60.0632 | 59.8755 | 0.34332 | 62.709 | -59.7748 | -59.8343 | 62.9013 | 62.8784 | 62.8098 | 0.16937 | 0.10071 | -0.050354 | -0.07782 | 0.11902 | 122.8409 | 63.121 | 122.6532 | 63.1714 | 122.7036 | 0.19226 | 0.068665 | 122.8912 | 122.7814 | 0.12817 | 122.5845 | 62.8372 | 122.5342 | -59.903 | -122.6624 | 62.7777 | 122.731 | 62.8006 | 63.3865
1718.8281 | 122.8958 | -62.8235 | 59.8801 | 0.015869 | -0.00058326 | -0.0066415 | 2.9005 | 0.0011109 | -0.0029138 | -0.0026853 | -0.13455 | 0.16395 | 0.12837 | -0.0046484 | 0.056465 | 0.10607 | -0.0054945 | -0.022888 | 0.19226 | -0.018311 | -0.041199 | 0.013733 | -0.022888 | 0.032043 | 0.49439 | 59.8297 | -62.8235 | 59.8526 | 59.9396 | 59.7336 | 0.27466 | 62.8052 | -59.6878 | -59.9213 | 62.8372 | 62.8555 | 62.8006 | 0.050354 | -0.004577 | 0 | -0.050354 | -0.027466 | 122.7631 | 63.0981 | 122.5571 | 63.0981 | 122.5571 | 0.032044 | -0.022888 | 122.7631 | 122.6761 | 0.21057 | 122.6532 | 63.0157 | 122.6532 | -59.8984 | -122.7036 | 62.7823 | 122.6761 | 62.8006 | 63.3179
1719.9062 | 122.9507 | -62.8326 | 59.8343 | -0.007019 | -0.0016513 | -0.0074961 | 2.8982 | 0.0023925 | -0.0018458 | -0.0026853 | -0.14676 | 0.16331 | 0.12623 | -0.0046484 | 0.055183 | 0.10607 | -0.0035719 | -0.10529 | 0.009155 | -0.1831 | -0.16022 | -0.045776 | -0.15564 | -0.082397 | 0.39825 | 59.7839 | -62.8418 | 59.903 | 59.9579 | 59.7702 | 0.18768 | 62.6495 | -59.8251 | -59.9945 | 62.7869 | 62.7502 | 62.677 | 0.10071 | 0.027465 | -0.009155 | -0.050354 | 0.068664 | 122.7905 | 63.0203 | 122.6028 | 63.0295 | 122.612 | 0.13733 | 0.022888 | 122.7997 | 122.7448 | 0.19226 | 122.6257 | 62.8418 | 122.6166 | -60.0174 | -122.6761 | 62.6724 | 122.7356 | 62.7274 | 63.2309
1720.8281 | 122.9233 | -62.8235 | 59.8663 | 0.038757 | -0.0033603 | -0.0096323 | 2.8986 | -0.0010253 | 0.0013586 | -0.0020443 | -0.14066 | 0.16309 | 0.12751 | 5.1352e-05 | 0.055183 | 0.10564 | -0.0014355 | 0.041199 | 0.15106 | -0.041199 | -0.018311 | 0.07782 | -0.009155 | 0.018311 | 0.53558 | 59.8526 | -62.8372 | 59.8709 | 59.967 | 59.7885 | 0.3067 | 62.7823 | -59.7153 | -59.8846 | 62.9013 | 62.8418 | 62.8143 | 0.05951 | 0.032044 | -0.013733 | -0.013733 | 0.004578 | 122.7905 | 63.1302 | 122.612 | 63.1439 | 122.6257 | 0.11902 | 0.022888 | 122.8043 | 122.7081 | 0.19226 | 122.6898 | 62.9745 | 122.6761 | -59.9075 | -122.7036 | 62.8052 | 122.6944 | 62.8647 | 63.3591
1721.8281 | 122.8729 | -62.8189 | 59.8343 | 0.00824 | -0.00058326 | -0.0074961 | 2.898 | 0.0030335 | -0.0018458 | -0.0022581 | -0.1315 | 0.16416 | 0.12602 | -0.0022986 | 0.058601 | 0.1065 | 0.0011279 | 0.027466 | 0.086975 | -0.073242 | -0.032043 | 0.064087 | -0.032043 | 0.022888 | 0.54016 | 59.816 | -62.8601 | 59.8892 | 59.9442 | 59.7794 | 0.27466 | 62.7457 | -59.7473 | -59.8663 | 62.883 | 62.8418 | 62.7869 | 0.09613 | 0.041199 | -0.041198 | -0.018311 | 0.054931 | 122.7631 | 63.0936 | 122.5983 | 63.1348 | 122.6395 | 0.13733 | 0.041199 | 122.8043 | 122.7493 | 0.16022 | 122.6761 | 62.9059 | 122.6349 | -59.9075 | -122.6944 | 62.7869 | 122.7081 | 62.8464 | 63.3591
1722.9062 | 122.9095 | -62.8464 | 59.8846 | 0.00061049 | 5.7742e-05 | -0.0060007 | 2.8986 | 4.2692e-05 | -0.0016322 | -0.0011899 | -0.14371 | 0.16416 | 0.12922 | -0.00058965 | 0.058174 | 0.10457 | -0.00015387 | 0.013733 | 0.082397 | -0.082397 | -0.041199 | 0.054932 | -0.054932 | -0.004578 | 0.59052 | 59.8114 | -62.8464 | 59.8938 | 59.9579 | 59.7702 | 0.25635 | 62.764 | -59.8022 | -59.9258 | 62.9013 | 62.8418 | 62.7914 | 0.077819 | 0.027465 | 0 | -0.073243 | 0.009155 | 122.8043 | 63.1027 | 122.6166 | 63.1027 | 122.6166 | 0.13733 | 0.041198 | 122.8043 | 122.7402 | 0.16479 | 122.6578 | 62.9288 | 122.6578 | -59.967 | -122.731 | 62.8052 | 122.7402 | 62.8601 | 63.4369
1723.8281 | 122.905 | -62.8189 | 59.8526 | 0.031128 | 5.7742e-05 | -0.0062143 | 2.8977 | 0.0062379 | -0.0012048 | -0.00097627 | -0.12845 | 0.16224 | 0.12815 | -0.004862 | 0.057747 | 0.10521 | -0.00079467 | 0.032043 | 0.082397 | -0.07782 | -0.036621 | 0.064087 | -0.032043 | 0.009155 | 0.55389 | 59.816 | -62.8418 | 59.8709 | 59.967 | 59.7702 | 0.27008 | 62.7411 | -59.7702 | -59.8892 | 62.883 | 62.8281 | 62.7869 | 0.086975 | 0.045777 | -0.022888 | -0.036621 | 0.018311 | 122.7859 | 63.089 | 122.5891 | 63.1119 | 122.612 | 0.14191 | 0.041199 | 122.8088 | 122.7127 | 0.16022 | 122.6578 | 62.9013 | 122.6349 | -59.9304 | -122.6944 | 62.7823 | 122.6898 | 62.851 | 63.3728
1724.9062 | 122.9233 | -62.8189 | 59.8434 | -0.007019 | -0.0022923 | -0.0068551 | 2.8984 | 0.0028199 | 7.6842e-05 | -0.0028989 | -0.11014 | 0.16395 | 0.13008 | -0.0076392 | 0.058387 | 0.10564 | -0.0020765 | -0.11444 | 0.036621 | -0.14191 | -0.15564 | -0.073242 | -0.16022 | -0.082397 | 0.3891 | 59.7931 | -62.8647 | 59.8846 | 59.9442 | 59.7519 | 0.16022 | 62.677 | -59.8068 | -59.9991 | 62.7457 | 62.7365 | 62.6587 | 0.05951 | -0.01831 | -0.045776 | -0.050354 | 0.041199 | 122.7631 | 62.9791 | 122.5708 | 63.0249 | 122.6166 | 0.068665 | -0.013733 | 122.8088 | 122.7493 | 0.17853 | 122.6578 | 62.8555 | 122.612 | -59.9854 | -122.7081 | 62.6633 | 122.7036 | 62.7045 | 63.208
1725.8281 | 122.8683 | -62.851 | 59.8709 | -0.007019 | -0.0014377 | -0.0077097 | 2.898 | -0.0035889 | -0.0014184 | -0.0022581 | -0.13455 | 0.16352 | 0.1273 | 0.00090575 | 0.058387 | 0.10457 | -0.00036747 | -0.054932 | 0.064087 | -0.11902 | -0.13275 | -0.045776 | -0.15106 | -0.07782 | 0.38452 | 59.8068 | -62.8601 | 59.8068 | 59.8801 | 59.7061 | 0.17853 | 62.7319 | -59.8068 | -60.0037 | 62.8052 | 62.7731 | 62.6999 | 0.041199 | -0.032043 | -0.009155 | -0.064087 | -0.064087 | 122.731 | 63.0295 | 122.5571 | 63.0386 | 122.5662 | 0.073243 | -0.013732 | 122.7402 | 122.6669 | 0.18311 | 122.6669 | 62.915 | 122.6578 | -59.9899 | -122.731 | 62.7182 | 122.6578 | 62.796 | 63.2355
1726.8906 | 122.9416 | -62.8281 | 59.7977 | -0.068054 | -0.0014377 | -0.0055735 | 2.8962 | 0.0034607 | 0.00071784 | -0.0031125 | -0.052155 | 0.16331 | 0.12944 | -0.0074254 | 0.058601 | 0.10286 | -0.00036747 | -0.045776 | 0.004578 | -0.10986 | -0.059509 | 0.059509 | -0.054932 | 0.009155 | 0.49439 | 59.729 | -62.8464 | 59.9075 | 59.967 | 59.8114 | 0.2243 | 62.7182 | -59.7931 | -59.8572 | 62.8876 | 62.8372 | 62.7731 | 0.11902 | 0.054931 | -0.018311 | -0.068664 | 0.10986 | 122.7951 | 63.0524 | 122.6395 | 63.0707 | 122.6578 | 0.16937 | 0.050354 | 122.8134 | 122.7539 | 0.11444 | 122.5754 | 62.8326 | 122.5571 | -59.9075 | -122.644 | 62.7686 | 122.7356 | 62.7823 | 63.3224
1727.8438 | 122.9553 | -62.8281 | 59.8022 | -0.060425 | 0.00091214 | -0.0081369 | 2.8967 | 0.0015381 | 0.0013586 | -0.0039671 | -0.064362 | 0.16053 | 0.12645 | -0.0050756 | 0.056251 | 0.1035 | -0.0022901 | -0.054932 | 0 | -0.1236 | -0.064087 | 0.064087 | -0.073242 | -0.009155 | 0.48523 | 59.7519 | -62.8189 | 59.9075 | 59.9762 | 59.7977 | 0.2243 | 62.7045 | -59.8022 | -59.8663 | 62.8922 | 62.8189 | 62.7548 | 0.11444 | 0.050354 | 0.009155 | -0.050354 | 0.10529 | 122.8043 | 63.0524 | 122.6257 | 63.0432 | 122.6166 | 0.18768 | 0.059509 | 122.7951 | 122.7264 | 0.1236 | 122.5708 | 62.8281 | 122.58 | -59.9258 | -122.6212 | 62.764 | 122.7356 | 62.7731 | 63.3133
1728.8906 | 122.9919 | -62.796 | 59.8663 | -0.24353 | -0.00036966 | -0.0072825 | 2.8975 | 0.00046989 | 7.6842e-05 | -0.0028989 | -0.039948 | 0.16181 | 0.12709 | -0.011057 | 0.056678 | 0.10329 | -0.00058107 | 0.16937 | 0.1236 | -0.018311 | 0.086975 | 0.17853 | 0.059509 | 0.10986 | 0.62714 | 59.7748 | -62.8281 | 59.9213 | 60.0449 | 59.8572 | 0.35706 | 62.7777 | -59.7427 | -59.7794 | 62.9745 | 62.9059 | 62.8555 | 0.12817 | 0.07782 | -0.032043 | -0.091553 | 0.054932 | 122.8409 | 63.1531 | 122.6532 | 63.1851 | 122.6852 | 0.19684 | 0.10529 | 122.8729 | 122.7493 | 0.14191 | 122.6028 | 62.9196 | 122.5708 | -59.8846 | -122.6944 | 62.883 | 122.7173 | 62.9654 | 63.4232
1729.8281 | 122.8683 | -62.8189 | 59.8663 | -0.014649 | -0.00015586 | -0.0081369 | 2.898 | 0.0034607 | -0.002273 | -0.0016171 | -0.14371 | 0.16395 | 0.12645 | -0.003153 | 0.056251 | 0.10479 | -0.00058107 | -0.009155 | 0.054932 | -0.091553 | -0.068665 | 0.022888 | -0.07782 | -0.027466 | 0.49896 | 59.8389 | -62.8281 | 59.8526 | 59.9213 | 59.7473 | 0.21973 | 62.7274 | -59.8114 | -59.935 | 62.8418 | 62.7914 | 62.7411 | 0.064087 | 0.013733 | -0.009155 | -0.027466 | -0.013733 | 122.7402 | 63.0386 | 122.5662 | 63.0478 | 122.5754 | 0.11444 | 0.022888 | 122.7493 | 122.6807 | 0.14649 | 122.6669 | 62.8738 | 122.6578 | -59.9579 | -122.6944 | 62.7502 | 122.6715 | 62.8098 | 63.3179
1730.8906 | 122.9416 | -62.7869 | 59.8663 | 0.061645 | 0.00048494 | -0.0083505 | 2.896 | 0.0026063 | -0.0020594 | -0.00097627 | -0.033844 | 0.16416 | 0.12559 | -0.0089208 | 0.057319 | 0.10479 | -0.0031445 | -0.13275 | 0.10529 | -0.036621 | 0.068665 | 0.14648 | 0.082397 | 0.10986 | 0.60883 | 59.7931 | -62.8235 | 59.9304 | 60.0357 | 59.8801 | 0.36621 | 62.7502 | -59.761 | -59.7977 | 62.9333 | 62.8967 | 62.8693 | 0.14648 | 0.11902 | -0.036621 | -0.073242 | 0.064087 | 122.8226 | 63.1531 | 122.6669 | 63.1897 | 122.7036 | 0.18311 | 0.10529 | 122.8592 | 122.7539 | 0.14191 | 122.6166 | 62.8922 | 122.58 | -59.903 | -122.6898 | 62.8555 | 122.7173 | 62.6541 | 63.3957
1731.8281 | 122.8775 | -62.851 | 59.8709 | 0.00061049 | -0.00079686 | -0.0089913 | 2.8986 | -0.0012391 | -0.00035036 | -0.0014035 | -0.14676 | 0.16373 | 0.13243 | -0.0033666 | 0.057747 | 0.10372 | 0.0015551 | -0.10529 | 0.036621 | -0.16022 | -0.17395 | -0.10071 | -0.17853 | -0.12817 | 0.13733 | 59.7748 | -62.9059 | 59.8938 | 59.8343 | 59.7061 | 0.17853 | 62.6907 | -59.8343 | -60.0449 | 62.7502 | 62.7228 | 62.6724 | 0.032043 | -0.018311 | -0.054932 | -0.096131 | 0.022888 | 122.6852 | 63.0295 | 122.5571 | 63.0844 | 122.612 | 0.059509 | -0.013733 | 122.7402 | 122.7997 | 0.19684 | 122.6807 | 62.8876 | 122.6257 | -60.0311 | -122.7768 | 62.677 | 122.7448 | 62.7457 | 62.9883
1732.9062 | 122.9462 | -62.7914 | 59.8022 | -0.068054 | -0.0010105 | -0.010059 | 2.8969 | -0.00038451 | 0.0015722 | -0.0014035 | -0.1315 | 0.16267 | 0.12773 | 0.00069215 | 0.05561 | 0.105 | 0.00048713 | -0.10986 | 0.027466 | -0.16937 | -0.12817 | -0.054932 | -0.15106 | -0.082397 | 0.40741 | 59.7656 | -62.8555 | 59.903 | 59.967 | 59.761 | 0.21057 | 62.6221 | -59.7748 | -59.9304 | 62.7365 | 62.709 | 62.6404 | 0.086976 | 0.018311 | -0.064087 | -0.036621 | 0.10071 | 122.7585 | 63.002 | 122.5525 | 63.0661 | 122.6166 | 0.11444 | 0.041199 | 122.8226 | 122.7585 | 0.19684 | 122.6212 | 62.8189 | 122.5571 | -59.9716 | -122.6578 | 62.6633 | 122.6944 | 62.6816 | 63.1989
1733.8281 | 122.8409 | -62.8326 | 59.8755 | 0.015869 | -0.0010105 | -0.0089913 | 2.8971 | -0.00017091 | -0.0012048 | -0.00033547 | -0.13455 | 0.16502 | 0.12858 | 0.00047855 | 0.056251 | 0.10735 | -0.0010083 | -0.07782 | 0.036621 | -0.12817 | -0.13275 | -0.059509 | -0.16937 | -0.11444 | 0.3479 | 59.8114 | -62.8784 | 59.7931 | 59.8663 | 59.6786 | 0.15564 | 62.7045 | -59.8389 | -60.0082 | 62.7731 | 62.7182 | 62.6633 | 0.013733 | -0.041199 | -0.045776 | -0.064087 | -0.082397 | 122.699 | 62.9883 | 122.5113 | 63.0341 | 122.5571 | 0.068665 | -0.004577 | 122.7448 | 122.6715 | 0.1648 | 122.6898 | 62.8693 | 122.644 | -60.0037 | -122.7539 | 62.6999 | 122.6257 | 62.7548 | 63.1805
1734.8906 | 122.9462 | -62.7869 | 59.8343 | -0.007019 | -0.0025059 | -0.010059 | 2.8954 | -0.00059811 | -0.00099116 | -0.0035397 | -0.052155 | 0.16309 | 0.12815 | -0.0072118 | 0.057319 | 0.1018 | 0.0013415 | -0.032043 | 0.054932 | -0.086975 | -0.050354 | 0.064087 | -0.027466 | 0.036621 | 0.49896 | 59.7794 | -62.8418 | 59.9075 | 60.0174 | 59.8251 | 0.28381 | 62.6999 | -59.7794 | -59.8846 | 62.851 | 62.8235 | 62.7594 | 0.1236 | 0.059509 | -0.054932 | -0.054932 | 0.073242 | 122.8043 | 63.0707 | 122.612 | 63.1256 | 122.6669 | 0.15106 | 0.036621 | 122.8592 | 122.7493 | 0.14191 | 122.6212 | 62.8418 | 122.5662 | -59.9213 | -122.6761 | 62.7365 | 122.6944 | 62.7548 | 63.2858
1735.8281 | 122.9004 | -62.8464 | 59.8526 | -0.029907 | -0.0029331 | -0.0085641 | 2.8982 | 0.0034607 | 0.003922 | -0.0043943 | -0.10709 | 0.16331 | 0.12687 | 0.00047855 | 0.058387 | 0.10393 | -0.0025037 | -0.10529 | 0.032043 | -0.16479 | -0.39825 | 0.38452 | 0.032043 | -0.1831 | 0.32959 | 59.8068 | -62.8738 | 59.8389 | 59.8846 | 59.7061 | 0.16937 | 62.6816 | -59.8206 | -60.2509 | 63.2309 | 62.6633 | 62.8784 | -0.01831 | 0.19684 | -0.027465 | -0.045776 | -0.013733 | 122.731 | 63.0157 | 122.5525 | 63.0432 | 122.58 | 0.54932 | -0.23346 | 122.7585 | 122.7127 | 0.19684 | 122.6807 | 62.8784 | 122.6532 | -60.0174 | -122.7264 | 62.4481 | 122.6852 | 62.7411 | 63.176
1736.8281 | 122.9095 | -62.8189 | 59.8572 | 0.015869 | -0.0016513 | -0.0083505 | 2.8962 | -0.0014527 | -0.0014184 | -0.0024717 | -0.12234 | 0.1616 | 0.12922 | -0.0016576 | 0.05561 | 0.10628 | -0.00036747 | 0.022888 | 0.11902 | -0.059509 | -0.018311 | 0.036621 | -0.009155 | 0.041199 | 0.55389 | 59.848 | -62.8464 | 59.903 | 59.9716 | 59.7839 | 0.29755 | 62.7594 | -59.7382 | -59.8755 | 62.8555 | 62.8601 | 62.8098 | 0.10071 | 0.050354 | -0.027466 | -0.009156 | 0.045776 | 122.7905 | 63.1165 | 122.6028 | 63.1439 | 122.6303 | 0.09613 | 0.041198 | 122.818 | 122.7493 | 0.17853 | 122.6944 | 62.9379 | 122.6669 | -59.9167 | -122.7036 | 62.8006 | 122.7219 | 62.8418 | 63.3728
1737.8906 | 122.8546 | -62.8372 | 59.8755 | -0.014649 | 0.00027134 | -0.0083505 | 2.8971 | 0.0015381 | -0.00013676 | -0.0033261 | -0.049103 | 0.16395 | 0.12837 | -0.00016245 | 0.057106 | 0.10286 | 0.0032641 | 0.027466 | 0.11444 | -0.041199 | -0.032043 | 0.068665 | 0.036621 | 0.050354 | 0.52185 | 59.8297 | -62.8098 | 59.8389 | 59.9442 | 59.7794 | 0.29755 | 62.796 | -59.761 | -59.9075 | 62.9059 | 62.8876 | 62.8738 | 0.091553 | 0.07782 | 0.027466 | -0.045776 | -0.036621 | 122.7814 | 63.1348 | 122.6166 | 63.1073 | 122.5891 | 0.10986 | 0.009156 | 122.7539 | 122.6486 | 0.15564 | 122.6395 | 62.9517 | 122.6669 | -59.9167 | -122.6852 | 62.8052 | 122.6761 | 62.8647 | 63.3591
1738.8281 | 122.8592 | -62.8418 | 59.8434 | 0.015869 | -0.00036966 | -0.0083505 | 2.8982 | 0.0015381 | -0.0029138 | -0.00054907 | -0.1376 | 0.1663 | 0.12773 | 0.00090575 | 0.056251 | 0.10543 | 0.0015551 | -0.022888 | 0.082397 | -0.10071 | -0.09613 | 0.004578 | -0.10071 | -0.041199 | 0.44403 | 59.8251 | -62.8693 | 59.8434 | 59.9075 | 59.7336 | 0.20599 | 62.7411 | -59.761 | -59.9396 | 62.8464 | 62.8006 | 62.7411 | 0.059509 | 0 | -0.027466 | -0.018311 | 0 | 122.7493 | 63.0478 | 122.5754 | 63.0753 | 122.6028 | 0.10529 | 0.004578 | 122.7768 | 122.7127 | 0.18311 | 122.6944 | 62.9242 | 122.6669 | -59.9442 | -122.7127 | 62.7457 | 122.6852 | 62.8189 | 63.2858
1739.8906 | 122.8867 | -62.8189 | 59.8755 | 0.038757 | 5.7742e-05 | -0.0081369 | 2.8971 | 0.0026063 | -0.0014184 | -0.00097627 | -0.11014 | 0.16608 | 0.12944 | -0.0033666 | 0.055397 | 0.10543 | -0.0012219 | 0.022888 | 0.12817 | -0.059509 | -0.050354 | 0.045776 | -0.032043 | 0.032043 | 0.48523 | 59.8251 | -62.851 | 59.8618 | 59.9579 | 59.7839 | 0.31586 | 62.7594 | -59.7473 | -59.9258 | 62.8647 | 62.851 | 62.7869 | 0.091552 | 0.027466 | -0.032043 | -0.050354 | -0.013733 | 122.7768 | 63.1348 | 122.6028 | 63.1668 | 122.6349 | 0.10528 | 0.009155 | 122.8088 | 122.7127 | 0.18768 | 122.6761 | 62.9471 | 122.644 | -59.935 | -122.7264 | 62.7686 | 122.6807 | 62.8418 | 63.3041
1740.8281 | 122.8821 | -62.8601 | 59.8297 | 0.00824 | -0.0022923 | -0.0079233 | 2.9001 | 0.0036743 | -0.00099116 | 9.193e-05 | -0.091827 | 0.16352 | 0.12709 | -0.0022986 | 0.057533 | 0.10436 | -0.0031445 | -0.10529 | 0.036621 | -0.16479 | -0.10529 | -0.37079 | -0.65918 | 0.018311 | 0.33875 | 59.8251 | -62.8693 | 59.8206 | 59.8846 | 59.697 | 0.15106 | 62.6953 | -59.7931 | -59.935 | 62.4893 | 62.8784 | 62.2009 | 0.18311 | -0.49438 | -0.009156 | -0.004578 | -0.009155 | 122.7448 | 63.0112 | 122.5571 | 63.0203 | 122.5662 | -0.20599 | 0.059509 | 122.7539 | 122.6898 | 0.20142 | 122.6944 | 62.8967 | 122.6852 | -59.9945 | -122.699 | 62.7548 | 122.6807 | 62.7548 | 63.1989
1741.8906 | 122.8958 | -62.8372 | 59.8709 | 0.00061049 | -0.0010105 | -0.0074961 | 2.898 | 0.0028199 | 0.001145 | -0.0016171 | -0.091827 | 0.16395 | 0.1273 | -0.0033666 | 0.059883 | 0.10479 | 0.0045459 | -0.004578 | 0.15564 | -0.041199 | -0.045776 | 0.054932 | -0.018311 | 0.027466 | 0.737 | 59.8572 | -62.8143 | 59.8251 | 59.967 | 59.7244 | 0.2655 | 62.796 | -59.7153 | -59.9167 | 62.8922 | 62.8647 | 62.8189 | 0.068665 | 0.022888 | 0.022888 | -0.013733 | -0.045777 | 122.8043 | 63.1027 | 122.5616 | 63.0798 | 122.5388 | 0.096131 | -0.004577 | 122.7814 | 122.6395 | 0.19684 | 122.6715 | 62.9929 | 122.6944 | -59.9121 | -122.6852 | 62.7914 | 122.6624 | 62.8326 | 63.5742
1742.8438 | 122.9324 | -62.796 | 59.8389 | -0.022278 | -0.0016513 | -0.0085641 | 2.8956 | 0.0017517 | -0.00099116 | -0.00033547 | -0.046051 | 0.16202 | 0.1288 | -0.0078528 | 0.058601 | 0.10543 | -0.0020765 | -0.045776 | 0.004578 | -0.11902 | -0.068665 | 0.036621 | -0.073242 | -0.004578 | 0.45319 | 59.7885 | -62.8601 | 59.8709 | 59.9762 | 59.8022 | 0.23346 | 62.677 | -59.8343 | -59.9075 | 62.8326 | 62.7914 | 62.7228 | 0.11444 | 0.045777 | -0.064086 | -0.050354 | 0.032044 | 122.7722 | 63.0295 | 122.5983 | 63.0936 | 122.6624 | 0.15564 | 0.050354 | 122.8363 | 122.731 | 0.1236 | 122.6486 | 62.8006 | 122.5845 | -59.9579 | -122.699 | 62.7274 | 122.6669 | 62.7502 | 63.2492
1743.8906 | 122.905 | -62.8189 | 59.848 | -0.029907 | -0.0014377 | -0.0077097 | 2.8975 | -0.00017091 | -0.0037684 | -0.0024717 | -0.14371 | 0.16267 | 0.12794 | -0.0025122 | 0.054115 | 0.10415 | -0.0031445 | 0 | 0.073242 | -0.07782 | -0.050354 | -0.045776 | -0.27466 | -0.032043 | 0.52643 | 59.8022 | -62.8418 | 59.8801 | 59.9533 | 59.7656 | 0.24719 | 62.7411 | -59.7748 | -59.8984 | 62.7731 | 62.7869 | 62.5443 | 0.045777 | -0.19684 | -0.022888 | -0.045776 | 0.032044 | 122.7722 | 63.0661 | 122.5845 | 63.089 | 122.6074 | 0.032044 | 0.027466 | 122.7951 | 122.7219 | 0.15106 | 122.644 | 62.8922 | 122.6212 | -59.9258 | -122.6898 | 62.7686 | 122.699 | 62.8189 | 63.3453
1744.8281 | 122.8455 | -62.851 | 59.8526 | -0.075684 | -0.00079686 | -0.0077097 | 2.8962 | 0.0015381 | 0.00029044 | -0.0022581 | -0.14981 | 0.16352 | 0.12837 | -0.0025122 | 0.055824 | 0.10436 | -0.0016493 | -0.045776 | 0.07782 | -0.11902 | -0.12817 | -0.073242 | -0.15106 | -0.086975 | 0.37079 | 59.8114 | -62.8738 | 59.8114 | 59.8526 | 59.6832 | 0.16937 | 62.7319 | -59.7748 | -59.9808 | 62.7777 | 62.764 | 62.6999 | 0.032044 | -0.032043 | -0.022888 | -0.041199 | -0.041199 | 122.7036 | 63.0203 | 122.5342 | 63.0432 | 122.5571 | 0.045777 | -0.009155 | 122.7264 | 122.6852 | 0.19684 | 122.6852 | 62.9288 | 122.6624 | -59.9716 | -122.7264 | 62.7228 | 122.6624 | 62.8052 | 63.2217
1745.8906 | 122.8729 | -62.8326 | 59.8709 | 0.023498 | -0.0022923 | -0.011128 | 2.8958 | 0.0036743 | -0.00077756 | -0.0035397 | -0.10098 | 0.16352 | 0.12602 | -0.0016576 | 0.058601 | 0.10244 | -0.0022901 | 0.022888 | 0.11902 | -0.091553 | -0.032043 | 0.054932 | -0.032043 | 0.032043 | 0.48523 | 59.8297 | -62.851 | 59.8526 | 59.967 | 59.7794 | 0.29755 | 62.7411 | -59.7519 | -59.903 | 62.8876 | 62.8647 | 62.8006 | 0.1236 | 0.05951 | -0.01831 | -0.041199 | -0.018311 | 122.7997 | 63.1302 | 122.612 | 63.1485 | 122.6303 | 0.14649 | 0.05951 | 122.818 | 122.7036 | 0.21057 | 122.6807 | 62.9517 | 122.6624 | -59.9625 | -122.7219 | 62.8006 | 122.6852 | 62.8555 | 63.3179
1746.8281 | 122.8409 | -62.8418 | 59.8846 | -0.014649 | -0.0022923 | -0.0053599 | 2.898 | 0.0026063 | -0.0027002 | -0.0020443 | -0.13455 | 0.16566 | 0.12538 | -0.00037605 | 0.057533 | 0.10671 | -0.0025037 | -0.064087 | 0.064087 | -0.11902 | -0.14648 | -0.064087 | -0.15106 | -0.086975 | 0.36163 | 59.8068 | -62.8693 | 59.8022 | 59.8572 | 59.6786 | 0.16937 | 62.7228 | -59.8206 | -60.0311 | 62.7777 | 62.7548 | 62.6907 | 0.032044 | -0.032043 | -0.027466 | -0.07782 | -0.082398 | 122.699 | 63.0112 | 122.5204 | 63.0386 | 122.5479 | 0.054932 | -0.027465 | 122.7264 | 122.6715 | 0.18311 | 122.6761 | 62.9059 | 122.6486 | -60.0037 | -122.7539 | 62.6953 | 122.644 | 62.7777 | 63.2034
1747.8906 | 122.8592 | -62.8464 | 59.8938 | -0.022278 | -0.0033603 | -0.0074961 | 2.8967 | -0.0010253 | -0.002273 | -0.00033547 | -0.055206 | 0.16181 | 0.12815 | -0.0059302 | 0.057319 | 0.10479 | -0.0033581 | 0.036621 | 0.10986 | -0.032043 | -0.009155 | 0.10071 | 0.027466 | 0.068665 | 0.53558 | 59.8297 | -62.8418 | 59.8389 | 59.9533 | 59.7702 | 0.29297 | 62.8143 | -59.7839 | -59.903 | 62.9471 | 62.915 | 62.8738 | 0.10071 | 0.059509 | 0.004578 | -0.064087 | -0.054932 | 122.7997 | 63.1393 | 122.6166 | 63.1348 | 122.612 | 0.13275 | 0.022888 | 122.7951 | 122.6807 | 0.14191 | 122.6715 | 62.9562 | 122.6761 | -59.9258 | -122.7356 | 62.8372 | 122.6852 | 62.883 | 63.382
1748.8281 | 122.9965 | -62.8052 | 59.8343 | -0.075684 | -0.0010105 | -0.0074961 | 2.8977 | 0.0011109 | -0.0012048 | 0.00051913 | -0.082672 | 0.16309 | 0.12367 | -0.0059302 | 0.056678 | 0.10393 | -0.00058107 | -0.032043 | -0.041199 | -0.14191 | -0.36621 | -0.33875 | 0.25177 | 0.21973 | 0.54016 | 59.7656 | -62.8326 | 59.9258 | 60.0037 | 59.816 | 0.24261 | 62.6633 | -59.8755 | -60.2005 | 62.4664 | 63.0249 | 63.0569 | 0.36163 | 0.39368 | -0.027466 | -0.068665 | 0.091552 | 122.8088 | 63.0478 | 122.6212 | 63.0753 | 122.6486 | -0.19684 | -0.2243 | 122.8363 | 122.7585 | 0.10071 | 122.5983 | 62.764 | 122.5708 | -59.9762 | -122.6669 | 62.439 | 122.731 | 62.7731 | 63.3453
1749.8906 | 122.937 | -62.8372 | 59.8755 | -0.045166 | -0.00015586 | -0.0089913 | 2.8973 | 0.0021789 | 0.00029044 | -0.0026853 | -0.10098 | 0.16288 | 0.12773 | -0.0042212 | 0.056678 | 0.10564 | -0.0035719 | 0.041199 | 0.13733 | -0.050354 | -0.022888 | 0.07782 | -0.018311 | 0.032043 | 0.55389 | 59.8434 | -62.8601 | 59.8892 | 59.9716 | 59.7839 | 0.29755 | 62.7869 | -59.7382 | -59.8984 | 62.915 | 62.8693 | 62.8189 | 0.082397 | 0.032043 | -0.022888 | -0.032043 | 0.013733 | 122.8088 | 63.1348 | 122.6212 | 63.1577 | 122.644 | 0.12817 | 0.027466 | 122.8317 | 122.7493 | 0.18768 | 122.7036 | 62.9745 | 122.6807 | -59.9258 | -122.7356 | 62.8143 | 122.7264 | 62.8784 | 63.3911
1750.8281 | 122.8592 | -62.8464 | 59.8618 | -0.060425 | -0.0012241 | -0.010273 | 2.898 | 0.00068369 | -0.0012048 | -0.00012167 | -0.16202 | 0.16245 | 0.12709 | -0.001444 | 0.056038 | 0.10628 | -0.00079467 | -0.073242 | 0.050354 | -0.11902 | -0.13275 | -0.054932 | -0.14648 | -0.086975 | 0.36621 | 59.816 | -62.883 | 59.8022 | 59.8709 | 59.6649 | 0.15564 | 62.7274 | -59.8114 | -59.9945 | 62.7914 | 62.7594 | 62.6999 | 0.032044 | -0.027465 | -0.036621 | -0.045776 | -0.059509 | 122.7173 | 63.002 | 122.5113 | 63.0386 | 122.5479 | 0.064087 | -0.013732 | 122.7539 | 122.6852 | 0.16937 | 122.699 | 62.8967 | 122.6624 | -59.9808 | -122.7448 | 62.7136 | 122.6486 | 62.7731 | 63.2126
1751.8281 | 122.9416 | -62.8281 | 59.8206 | -0.037537 | -0.0016513 | -0.0081369 | 2.8956 | 0.0049561 | -0.0014184 | -0.00097627 | -0.11014 | 0.16373 | 0.12474 | 0.0024012 | 0.056892 | 0.10543 | 0.0019823 | -0.10071 | 0.036621 | -0.15106 | -0.15564 | -0.050354 | -0.16479 | -0.082397 | 0.38452 | 59.7977 | -62.8693 | 59.8755 | 59.9396 | 59.7427 | 0.19226 | 62.677 | -59.7839 | -59.9762 | 62.7777 | 62.7457 | 62.6633 | 0.068665 | -0.013733 | -0.041199 | -0.022889 | 0.054931 | 122.7676 | 63.0203 | 122.5708 | 63.0615 | 122.612 | 0.10071 | -0.004578 | 122.8088 | 122.7448 | 0.18768 | 122.6669 | 62.8647 | 122.6257 | -59.9716 | -122.6898 | 62.6724 | 122.7036 | 62.7274 | 63.2126
1752.8906 | 122.9233 | -62.8418 | 59.8434 | 0.023498 | -0.00058326 | -0.0094187 | 2.8971 | 0.00046989 | -0.0031274 | -0.0035397 | -0.10098 | 0.16267 | 0.1273 | 0.0017602 | 0.057319 | 0.1035 | -0.0016493 | 0.009155 | 0.12817 | -0.064087 | -0.022888 | 0.068665 | -0.027466 | 0.009155 | 0.53101 | 59.7931 | -62.8418 | 59.8846 | 59.9716 | 59.7839 | 0.29297 | 62.7777 | -59.7153 | -59.8663 | 62.9105 | 62.851 | 62.8143 | 0.073242 | 0.036621 | 0 | -0.050354 | 0.041199 | 122.8134 | 63.1348 | 122.6257 | 63.1348 | 122.6257 | 0.13275 | 0.041199 | 122.8134 | 122.7264 | 0.19226 | 122.6349 | 62.97 | 122.6349 | -59.9075 | -122.6852 | 62.8189 | 122.7264 | 62.851 | 63.3728
1753.8281 | 122.9782 | -62.7823 | 59.8251 | -0.060425 | -0.0010105 | -0.0070687 | 2.8971 | 0.0028199 | 0.002854 | -0.00097627 | -0.033844 | 0.1601 | 0.12452 | -0.003153 | 0.056038 | 0.10372 | -0.0016493 | -0.054932 | -0.027466 | -0.1236 | 0.073242 | 0.38452 | -0.10529 | -0.032043 | 0.49439 | 59.7427 | -62.8281 | 59.9304 | 60.0128 | 59.8297 | 0.2243 | 62.6587 | -59.8526 | -59.7519 | 63.1668 | 62.7502 | 62.677 | 0.091553 | 0.01831 | -0.045776 | -0.082397 | 0.10529 | 122.7951 | 63.0066 | 122.612 | 63.0524 | 122.6578 | 0.50812 | 0.19684 | 122.8409 | 122.7585 | 0.09613 | 122.5708 | 62.7548 | 122.525 | -59.9487 | -122.6532 | 62.8555 | 122.7127 | 62.7274 | 63.2767
1754.8906 | 122.9095 | -62.8418 | 59.8618 | 0.00824 | -0.0018649 | -0.0079233 | 2.8982 | 0.00068369 | -0.00099116 | -0.0016171 | -0.091827 | 0.16331 | 0.12687 | -0.0016576 | 0.056251 | 0.10543 | -0.0010083 | -0.018311 | 0.07782 | -0.09613 | -0.064087 | 0.054932 | -0.21515 | -0.16479 | 0.5127 | 59.8206 | -62.8372 | 59.8846 | 59.9442 | 59.7702 | 0.25177 | 62.7457 | -59.7839 | -59.9258 | 62.8967 | 62.677 | 62.6266 | -0.068665 | -0.11902 | 0.004578 | -0.041198 | 0.022889 | 122.7859 | 63.0936 | 122.612 | 63.089 | 122.6074 | 0.15106 | 0.032043 | 122.7814 | 122.7219 | 0.17395 | 122.6578 | 62.9196 | 122.6624 | -59.9579 | -122.699 | 62.7777 | 122.7264 | 62.8235 | 63.3545
1755.8281 | 122.9828 | -62.8143 | 59.848 | -0.014649 | -0.0014377 | -0.0085641 | 2.8956 | 0.00068369 | -0.00035036 | 0.0015871 | -0.10709 | 0.1616 | 0.12666 | -0.00016245 | 0.056892 | 0.10436 | -0.0039991 | -0.064087 | -0.027466 | -0.15106 | -0.041199 | 0.018311 | -0.10986 | -0.022888 | 0.48981 | 59.7702 | -62.8418 | 59.9442 | 60.0082 | 59.8206 | 0.23346 | 62.6633 | -59.8755 | -59.8892 | 62.8326 | 62.7914 | 62.7045 | 0.12817 | 0.041199 | -0.027466 | -0.077819 | 0.096131 | 122.8226 | 63.0478 | 122.6349 | 63.0753 | 122.6624 | 0.16937 | 0.10986 | 122.85 | 122.7859 | 0.1236 | 122.612 | 62.7869 | 122.5845 | -59.9991 | -122.6898 | 62.7731 | 122.7585 | 62.7502 | 63.3041
1756.8906 | 122.8912 | -62.8738 | 59.8389 | -0.014649 | -0.0016513 | -0.0079233 | 2.9009 | 0.0064515 | 0.001145 | -0.0048215 | -0.12845 | 0.16224 | 0.12815 | -0.0016576 | 0.057319 | 0.10628 | -0.00036747 | -0.10071 | 0.022888 | -0.17395 | 0.2243 | -0.018311 | -0.2243 | 0.018311 | 0.38452 | 59.7931 | -62.8601 | 59.8297 | 59.8984 | 59.697 | 0.16022 | 62.6999 | -59.816 | -59.6146 | 62.8555 | 62.8922 | 62.6495 | 0.19226 | -0.050354 | 0.013733 | -0.045776 | -0.009155 | 122.7722 | 63.0341 | 122.5708 | 63.0203 | 122.5571 | 0.15564 | 0.39825 | 122.7585 | 122.6898 | 0.19684 | 122.6532 | 62.8967 | 122.6669 | -60.0128 | -122.699 | 63.0981 | 122.7036 | 62.7731 | 63.2584
1757.8438 | 122.9919 | -62.8189 | 59.8251 | -0.029907 | -0.0029331 | -0.0096323 | 2.8965 | 0.00025629 | 0.00029044 | -0.0020443 | -0.0094299 | 0.16309 | 0.12559 | -0.011484 | 0.057533 | 0.10479 | -0.0031445 | 0.004578 | 0.050354 | -0.059509 | -0.009155 | 0.1236 | 0.022888 | 0.082397 | 0.56305 | 59.7748 | -62.8235 | 59.9579 | 60.0449 | 59.8663 | 0.32959 | 62.7594 | -59.7748 | -59.8343 | 62.9425 | 62.9013 | 62.8418 | 0.14191 | 0.082397 | -0.004577 | -0.050354 | 0.13275 | 122.8638 | 63.1485 | 122.6852 | 63.1531 | 122.6898 | 0.1831 | 0.050354 | 122.8683 | 122.7814 | 0.10986 | 122.5983 | 62.8693 | 122.5937 | -59.8846 | -122.6486 | 62.8098 | 122.7768 | 62.8235 | 63.382
1758.8906 | 122.8867 | -62.8418 | 59.8801 | -0.007019 | -0.0018649 | -0.0087777 | 2.8982 | 0.0013245 | -0.00099116 | -0.00097627 | -0.14676 | 0.16267 | 0.12922 | 0.00069215 | 0.054969 | 0.10372 | -0.0018629 | 0.004578 | 0.082397 | -0.091553 | -0.045776 | 0.032043 | -0.050354 | -0.013733 | 0.55847 | 59.8206 | -62.851 | 59.9075 | 59.9579 | 59.7656 | 0.25635 | 62.7502 | -59.7977 | -59.9258 | 62.8738 | 62.8281 | 62.7914 | 0.07782 | 0.041199 | -0.009155 | -0.059509 | 0.027466 | 122.7997 | 63.0981 | 122.6074 | 63.1073 | 122.6166 | 0.1236 | 0.045777 | 122.8088 | 122.7585 | 0.17395 | 122.6715 | 62.9242 | 122.6624 | -59.9716 | -122.731 | 62.796 | 122.7493 | 62.8464 | 63.4003
1759.8281 | 123.0011 | -62.8143 | 59.8297 | -0.12909 | 0.00027134 | -0.0062143 | 2.8962 | 0.0017517 | -0.00013676 | -0.0031125 | -0.052155 | 0.16074 | 0.12858 | -0.0025122 | 0.05561 | 0.10265 | 0.00048713 | -0.059509 | -0.027466 | -0.1236 | -0.054932 | 0.050354 | -0.086975 | -0.032043 | 0.48065 | 59.7656 | -62.8693 | 59.9716 | 60.0174 | 59.8251 | 0.22888 | 62.6907 | -59.8572 | -59.8846 | 62.8647 | 62.7823 | 62.7274 | 0.091553 | 0.036621 | -0.054932 | -0.064087 | 0.14191 | 122.8317 | 63.0432 | 122.6395 | 63.0981 | 122.6944 | 0.17395 | 0.068664 | 122.8867 | 122.8409 | 0.09613 | 122.6349 | 62.7869 | 122.58 | -59.9533 | -122.699 | 62.7594 | 122.7859 | 62.7548 | 63.295
1760.8906 | 122.9279 | -62.8235 | 59.8709 | 0.00824 | -0.0010105 | -0.0070687 | 2.898 | -0.00081171 | -0.00013676 | 0.00051913 | -0.12234 | 0.16309 | 0.12431 | -0.0016576 | 0.057747 | 0.10906 | -0.0059217 | 0.013733 | 0.10529 | -0.068665 | -0.027466 | 0.059509 | -0.059509 | 0.004578 | 0.53101 | 59.8343 | -62.8555 | 59.7839 | 60.0632 | 59.7656 | 0.26093 | 62.7548 | -59.7656 | -59.8984 | 62.883 | 62.8281 | 62.764 | 0.073243 | 0.009156 | -0.032044 | -0.036621 | -0.086975 | 122.8867 | 63.0844 | 122.5891 | 63.1165 | 122.6212 | 0.12817 | 0.041199 | 122.9187 | 122.6395 | 0.17395 | 122.6898 | 62.9288 | 122.6578 | -59.9396 | -122.7264 | 62.796 | 122.6074 | 62.8372 | 63.3545
1761.8281 | 122.9416 | -62.8189 | 59.8251 | -0.045166 | -0.00079686 | -0.0057871 | 2.8962 | 0.00025629 | 0.00029044 | -0.0016171 | -0.06131 | 0.16181 | 0.12687 | -0.0035802 | 0.055397 | 0.10628 | 0.00027333 | -0.054932 | -0.045776 | -0.13733 | -0.059509 | 0.041199 | -0.073242 | -0.022888 | 0.49896 | 59.7656 | -62.851 | 59.8022 | 60.0266 | 60.0082 | 0.3479 | 62.6816 | -59.8709 | -59.8846 | 62.8601 | 62.796 | 62.7457 | 0.11444 | 0.064087 | -0.032043 | -0.059509 | -0.022888 | 122.8455 | 63.1668 | 122.8271 | 63.1989 | 122.8592 | 0.17853 | 0.07782 | 122.8775 | 122.6532 | 0.091553 | 122.6166 | 62.7731 | 122.5845 | -59.9625 | -122.6761 | 62.7594 | 122.6212 | 62.764 | 63.3179
1762.9062 | 122.9599 | -62.8098 | 59.8251 | -0.014649 | -0.00058326 | -0.0083505 | 2.8952 | -0.0025207 | -0.0037684 | -0.00033547 | -0.015534 | 0.16224 | 0.12837 | 0.00026495 | 0.058387 | 0.10286 | -0.00058107 | -0.054932 | 0.013733 | -0.086975 | 0.07782 | -0.064087 | -0.091553 | -0.018311 | 0.48981 | 59.7885 | -62.851 | 59.9075 | 59.9854 | 59.8251 | 0.2655 | 62.7228 | -59.8114 | -59.7473 | 62.7457 | 62.7914 | 62.7182 | 0.068664 | -0.004578 | -0.041199 | -0.036621 | 0.082398 | 122.7951 | 63.0753 | 122.6349 | 63.1165 | 122.6761 | 0.022888 | 0.16479 | 122.8363 | 122.7585 | 0.10071 | 122.6395 | 62.8235 | 122.5983 | -59.9121 | -122.6761 | 62.8876 | 122.7173 | 62.7548 | 63.2996
1763.8281 | 122.9828 | -62.8143 | 59.8068 | -0.083313 | -0.0020785 | -0.010273 | 2.8965 | 0.0026063 | -0.00056396 | -0.0028989 | -0.11929 | 0.16437 | 0.12837 | 5.1352e-05 | 0.056892 | 0.10521 | -0.0025037 | -0.036621 | -0.059509 | -0.14648 | -0.050354 | 0.045776 | -0.07782 | -0.045776 | 0.47607 | 59.7748 | -62.8464 | 59.9442 | 59.9945 | 59.8251 | 0.22888 | 62.6678 | -59.8663 | -59.8572 | 62.8601 | 62.7686 | 62.7365 | 0.10071 | 0.068664 | -0.032044 | -0.032044 | 0.13733 | 122.8088 | 63.0432 | 122.6395 | 63.0753 | 122.6715 | 0.19226 | 0.09613 | 122.8409 | 122.7905 | 0.086975 | 122.6212 | 62.7548 | 122.5891 | -59.9533 | -122.6532 | 62.764 | 122.7585 | 62.7777 | 63.2904
1764.8906 | 122.8958 | -62.8601 | 59.8526 | -0.060425 | -0.0031467 | -0.0083505 | 2.8977 | -0.0010253 | -0.00013676 | -0.00097627 | -0.14371 | 0.1648 | 0.1273 | 0.00047855 | 0.057747 | 0.105 | -0.0018629 | 0.022888 | 0.022888 | -0.15106 | -0.15564 | -0.073242 | -0.17853 | -0.10529 | 0.37994 | 59.8022 | -62.8922 | 59.848 | 59.9075 | 59.7427 | 0.16022 | 62.709 | -59.8297 | -60.0082 | 62.7869 | 62.7548 | 62.6816 | 0.045776 | -0.027466 | -0.032044 | -0.050354 | -0.004578 | 122.7676 | 63.0203 | 122.6028 | 63.0524 | 122.6349 | 0.07782 | -0.004578 | 122.7997 | 122.7402 | 0.17395 | 122.6944 | 62.883 | 122.6624 | -60.0037 | -122.7448 | 62.7045 | 122.7081 | 62.883 | 63.2401
1765.8281 | 122.9324 | -62.8281 | 59.8206 | -0.037537 | -0.0010105 | -0.0092051 | 2.8943 | -0.0016663 | -0.00077756 | -0.0011899 | -0.06131 | 0.16138 | 0.12858 | -0.0061438 | 0.057319 | 0.10479 | -0.0022901 | -0.059509 | -0.013733 | -0.12817 | -0.073242 | 0.036621 | -0.073242 | -0.004578 | 0.46692 | 59.7656 | -62.8326 | 59.8938 | 59.9808 | 59.7839 | 0.19226 | 62.6999 | -59.8343 | -59.8938 | 62.8647 | 62.8235 | 62.7548 | 0.1236 | 0.054932 | -0.004578 | -0.054932 | 0.073242 | 122.8088 | 63.0203 | 122.612 | 63.0249 | 122.6166 | 0.1648 | 0.054932 | 122.8134 | 122.7264 | 0.11444 | 122.5983 | 62.8143 | 122.5937 | -59.9487 | -122.6532 | 62.7548 | 122.7219 | 62.7686 | 63.295
1766.8906 | 122.937 | -62.8418 | 59.8938 | 0.015869 | -0.0020785 | -0.0087777 | 2.8969 | 0.0011109 | 0.00029044 | 9.193e-05 | -0.12234 | 0.16267 | 0.12709 | 0.0043238 | 0.056251 | 0.10799 | -0.0039991 | 0.018311 | 0.12817 | -0.064087 | -0.013733 | 0.027466 | -0.018311 | 0.022888 | 0.48981 | 59.8572 | -62.8464 | 59.8755 | 59.9625 | 59.7656 | 0.31128 | 62.7777 | -59.7656 | -59.9075 | 62.8693 | 62.8647 | 62.8235 | 0.086975 | 0.045776 | -0.004578 | -0.036621 | -0.018311 | 122.8043 | 63.1531 | 122.6074 | 63.1577 | 122.612 | 0.091553 | 0.050354 | 122.8088 | 122.7219 | 0.19226 | 122.7036 | 62.97 | 122.699 | -59.9579 | -122.7402 | 62.8281 | 122.7173 | 62.8601 | 63.3316
1767.8438 | 122.9736 | -62.8006 | 59.8938 | -0.12909 | -0.00015586 | -0.0072825 | 2.8937 | 4.2692e-05 | 0.0019994 | -0.0039671 | -0.055206 | 0.16267 | 0.12495 | -0.001444 | 0.055824 | 0.10329 | -0.0020765 | 0.09613 | 0.07782 | -0.054932 | 0.050354 | 0.15564 | 0.054932 | 0.09613 | 0.61798 | 59.8022 | -62.8189 | 59.9258 | 60.0357 | 59.8572 | 0.36621 | 62.7457 | -59.816 | -59.8434 | 62.9562 | 62.8967 | 62.8555 | 0.15106 | 0.10986 | -0.018311 | -0.091553 | 0.032043 | 122.8363 | 63.1668 | 122.6578 | 63.1851 | 122.6761 | 0.21057 | 0.10529 | 122.8546 | 122.7448 | 0.13275 | 122.6212 | 62.8784 | 122.6028 | -59.9487 | -122.7127 | 62.851 | 122.7264 | 62.8967 | 63.4186
1768.8906 | 122.9004 | -62.8143 | 59.8846 | 0.00061049 | -0.0014377 | -0.0087777 | 2.8969 | -0.0033753 | 0.00029044 | 0.00030553 | -0.097931 | 0.16309 | 0.12751 | -0.0029394 | 0.057533 | 0.10778 | -0.0020765 | 0 | 0.073242 | -0.082397 | -0.041199 | 0.054932 | -0.059509 | -0.018311 | 0.45319 | 59.8251 | -62.8647 | 59.8846 | 59.9762 | 59.761 | 0.27008 | 62.7319 | -59.8114 | -59.9258 | 62.8693 | 62.796 | 62.7548 | 0.064086 | 0.022888 | -0.050354 | -0.05951 | 0 | 122.7905 | 63.0844 | 122.5754 | 63.1348 | 122.6257 | 0.13733 | 0.041198 | 122.8409 | 122.7493 | 0.15564 | 122.6898 | 62.8876 | 122.6395 | -59.967 | -122.7493 | 62.7731 | 122.699 | 62.8143 | 63.2675
1769.8281 | 122.9599 | -62.8235 | 59.8434 | -0.037537 | -0.0020785 | -0.0087777 | 2.8952 | -0.0025207 | 7.6842e-05 | -0.00097627 | -0.07962 | 0.16352 | 0.12815 | -0.0044348 | 0.05796 | 0.10521 | 0.0041187 | -0.041199 | 0.004578 | -0.11444 | -0.059509 | 0.064087 | -0.064087 | -0.027466 | 0.48981 | 59.7656 | -62.883 | 59.8984 | 59.9762 | 59.8114 | 0.20599 | 62.709 | -59.8389 | -59.903 | 62.8876 | 62.796 | 62.7594 | 0.086975 | 0.050354 | -0.05951 | -0.07782 | 0.054931 | 122.7997 | 63.0295 | 122.6349 | 63.089 | 122.6944 | 0.17853 | 0.054932 | 122.8592 | 122.7814 | 0.11902 | 122.6486 | 62.8281 | 122.5891 | -59.9579 | -122.7264 | 62.764 | 122.7219 | 62.7823 | 63.3133
1770.8906 | 122.85 | -62.8418 | 59.8618 | -0.029907 | -0.00058326 | -0.0087777 | 2.8986 | -0.0010253 | -0.0029138 | -0.0022581 | -0.14981 | 0.16395 | 0.12794 | -0.0091344 | 0.056465 | 0.10714 | 0.00091433 | -0.07782 | 0.054932 | -0.10986 | -0.1236 | -0.045776 | -0.21057 | -0.13733 | 0.37537 | 59.8206 | -62.8922 | 59.8022 | 59.8709 | 59.6878 | 0.16022 | 62.7319 | -59.8068 | -59.9854 | 62.796 | 62.7045 | 62.6312 | -0.027466 | -0.10071 | -0.050354 | -0.041198 | -0.059509 | 122.7127 | 63.002 | 122.5296 | 63.0524 | 122.58 | 0.064087 | -0.013733 | 122.7631 | 122.6944 | 0.16479 | 122.7127 | 62.8967 | 122.6624 | -59.9716 | -122.7539 | 62.7182 | 122.644 | 62.764 | 63.2172
1771.8281 | 122.9828 | -62.8052 | 59.816 | -0.11383 | -0.0010105 | -0.0064279 | 2.8945 | 0.0041015 | -0.0020594 | -0.0020443 | -0.10098 | 0.16373 | 0.12687 | -0.0025122 | 0.058387 | 0.10585 | 0.00048713 | -0.032043 | -0.050354 | -0.11902 | -0.059509 | 0.054932 | -0.07782 | -0.036621 | 0.48523 | 59.761 | -62.8464 | 59.9213 | 60.0952 | 59.816 | 0.20599 | 62.6862 | -59.8663 | -59.8755 | 62.8601 | 62.7686 | 62.7274 | 0.082398 | 0.041199 | -0.041199 | -0.054932 | 0.10529 | 122.9004 | 63.0112 | 122.6212 | 63.0524 | 122.6624 | 0.17395 | 0.05951 | 122.9416 | 122.7676 | 0.068665 | 122.6074 | 62.7548 | 122.5662 | -59.935 | -122.6624 | 62.7457 | 122.7264 | 62.7731 | 63.2904
1772.9219 | 122.8958 | -62.8647 | 59.8526 | -0.029907 | -0.00079686 | -0.0074961 | 2.8971 | -0.0016663 | -0.00013676 | 0.00051913 | -0.14676 | 0.16566 | 0.12666 | 0.00026495 | 0.059669 | 0.10329 | -0.0012219 | -0.11444 | 0.022888 | -0.15106 | -0.22888 | -0.12817 | 0.027466 | -0.050354 | 0.35706 | 59.8434 | -62.8738 | 59.8618 | 59.8892 | 59.7198 | 0.16022 | 62.7136 | -59.8297 | -60.0815 | 62.7365 | 62.8143 | 62.8922 | 0.10071 | 0.17853 | -0.009155 | -0.009155 | 0.009155 | 122.7539 | 63.0249 | 122.5845 | 63.0341 | 122.5937 | 0.022888 | -0.07782 | 122.7631 | 122.7356 | 0.17395 | 122.7173 | 62.8876 | 122.7081 | -60.0037 | -122.7264 | 62.6358 | 122.7264 | 62.7502 | 63.2217
1773.8438 | 122.9507 | -62.8189 | 59.816 | -0.068054 | -0.00015586 | -0.0083505 | 2.8937 | -0.00038451 | -0.0012048 | 9.193e-05 | -0.021637 | 0.15967 | 0.12751 | 0.00069215 | 0.058387 | 0.10393 | 0.00091433 | -0.054932 | 0.041199 | -0.091553 | -0.054932 | 0.050354 | -0.045776 | 0.018311 | 0.45319 | 59.7885 | -62.8464 | 59.903 | 59.9762 | 59.8206 | 0.25177 | 62.7274 | -59.7748 | -59.8709 | 62.8693 | 62.8372 | 62.7731 | 0.10986 | 0.045777 | -0.027466 | -0.027466 | 0.086975 | 122.7951 | 63.0707 | 122.6395 | 63.0981 | 122.6669 | 0.14191 | 0.036621 | 122.8226 | 122.7493 | 0.13275 | 122.6349 | 62.8601 | 122.6074 | -59.9075 | -122.6624 | 62.764 | 122.7219 | 62.764 | 63.2721
1774.8906 | 122.9095 | -62.8418 | 59.848 | -0.029907 | -0.0022923 | -0.0083505 | 2.8973 | 0.00025629 | -0.0012048 | -0.0022581 | -0.14371 | 0.16245 | 0.12773 | 5.1352e-05 | 0.056465 | 0.10521 | -0.0022901 | -0.10071 | 0.064087 | -0.13275 | -0.16022 | -0.086975 | -0.16937 | -0.10986 | 0.39368 | 59.7977 | -62.8738 | 59.8709 | 59.9258 | 59.7427 | 0.16937 | 62.709 | -59.7839 | -60.0082 | 62.7548 | 62.7319 | 62.6724 | 0.022888 | -0.036622 | -0.032043 | -0.050354 | 0.022889 | 122.7676 | 63.0112 | 122.5845 | 63.0432 | 122.6166 | 0.045776 | -0.027466 | 122.7997 | 122.7448 | 0.19684 | 122.6715 | 62.9059 | 122.6395 | -59.9808 | -122.7219 | 62.6816 | 122.7127 | 62.7411 | 63.2355
1775.8281 | 122.9416 | -62.8189 | 59.8434 | -0.075684 | -0.0016513 | -0.0077097 | 2.8952 | -0.0035889 | -0.0014184 | -0.0014035 | -0.067413 | 0.16373 | 0.12452 | -0.0022986 | 0.055824 | 0.10308 | -0.0027173 | -0.07782 | -0.018311 | -0.1236 | -0.073242 | 0.036621 | -0.086975 | 0 | 0.4303 | 59.7794 | -62.851 | 59.8938 | 59.9808 | 59.7885 | 0.22888 | 62.6953 | -59.8618 | -59.9167 | 62.8555 | 62.8189 | 62.7319 | 0.1236 | 0.036621 | -0.032043 | -0.064087 | 0.050354 | 122.7997 | 63.0478 | 122.6074 | 63.0798 | 122.6395 | 0.16022 | 0.050354 | 122.8317 | 122.7448 | 0.10528 | 122.6303 | 62.8006 | 122.5983 | -59.967 | -122.6944 | 62.7457 | 122.7127 | 62.7411 | 63.2492
1776.8906 | 122.8729 | -62.8235 | 59.8801 | -0.029907 | -0.00079686 | -0.0089913 | 2.8967 | -0.0055115 | -0.00056396 | -0.0031125 | -0.10403 | 0.16181 | 0.12794 | -0.0012304 | 0.056892 | 0.10436 | -0.0033581 | 0.018311 | 0.16937 | -0.045776 | -0.32959 | -0.045776 | -0.004578 | -0.064087 | 0.44861 | 59.8297 | -62.8647 | 59.8434 | 59.9167 | 59.7748 | 0.30212 | 62.7777 | -59.7107 | -60.2097 | 62.7777 | 62.7594 | 62.8189 | -0.018311 | 0.041198 | -0.041199 | -0.050354 | -0.036621 | 122.7402 | 63.1256 | 122.5983 | 63.1668 | 122.6395 | 0 | -0.28381 | 122.7814 | 122.7081 | 0.21515 | 122.6944 | 62.9929 | 122.6532 | -59.9258 | -122.7448 | 62.4939 | 122.6669 | 62.8418 | 63.2721
1777.8438 | 122.9782 | -62.8098 | 59.8434 | -0.045166 | -0.0020785 | -0.0083505 | 2.8958 | 0.0017517 | -0.0016322 | -0.0054623 | -0.06131 | 0.16138 | 0.12815 | 0.0026148 | 0.057106 | 0.10286 | -0.0022901 | 0.054932 | 0.064087 | -0.041199 | 0.082397 | 0.19226 | 0.068665 | 0.1236 | 0.50812 | 59.8068 | -62.7823 | 60.0037 | 59.967 | 59.903 | 0.40741 | 62.7686 | -59.7794 | -59.761 | 63.002 | 62.9333 | 62.8784 | 0.16479 | 0.10986 | 0.027465 | -0.036621 | 0.16022 | 122.7768 | 63.2172 | 122.7127 | 63.1897 | 122.6852 | 0.23346 | 0.1236 | 122.7493 | 122.7859 | 0.10529 | 122.5891 | 62.8738 | 122.6166 | -59.8846 | -122.6257 | 62.8922 | 122.8134 | 62.8647 | 63.3179
1778.8906 | 122.9187 | -62.8326 | 59.8709 | -0.014649 | -0.0010105 | -0.0072825 | 2.8954 | 0.0030335 | -0.0029138 | -0.00076267 | -0.13455 | 0.16416 | 0.1273 | 0.0034692 | 0.056465 | 0.10671 | -0.0039991 | -0.022888 | 0.073242 | -0.07782 | 0.041199 | 0.054932 | -0.018311 | 0.009155 | 0.52643 | 59.8297 | -62.8464 | 59.8755 | 59.9533 | 59.7794 | 0.25177 | 62.7548 | -59.7977 | -59.8297 | 62.8876 | 62.8418 | 62.8143 | 0.086975 | 0.059509 | -0.013733 | -0.041199 | 0.004577 | 122.7859 | 63.0844 | 122.612 | 63.0981 | 122.6257 | 0.13275 | 0.11902 | 122.7997 | 122.7219 | 0.15106 | 122.6761 | 62.9059 | 122.6624 | -59.9487 | -122.7173 | 62.8738 | 122.7081 | 62.8098 | 63.3591
1779.8281 | 122.937 | -62.8189 | 59.8251 | -0.029907 | -0.0010105 | -0.010487 | 2.8947 | 0.0026063 | -0.00099116 | 0.00073273 | -0.085724 | 0.16373 | 0.12837 | -0.003794 | 0.057106 | 0.10393 | 0.00091433 | -0.050354 | -0.027466 | -0.10071 | -0.050354 | 0.073242 | -0.073242 | -0.009155 | 0.48065 | 59.761 | -62.851 | 59.9075 | 59.9808 | 59.8068 | 0.20142 | 62.7182 | -59.8526 | -59.8755 | 62.8922 | 62.8098 | 62.7457 | 0.091553 | 0.027466 | -0.032043 | -0.064087 | 0.082398 | 122.7997 | 63.0203 | 122.6257 | 63.0524 | 122.6578 | 0.17395 | 0.050354 | 122.8317 | 122.7585 | 0.073242 | 122.612 | 62.7914 | 122.58 | -59.9258 | -122.6761 | 62.7686 | 122.7264 | 62.7686 | 63.2996
1780.8906 | 122.8912 | -62.8281 | 59.8801 | 0.00824 | -0.0020785 | -0.0072825 | 2.8965 | -0.0014527 | -0.0014184 | -0.00012167 | -0.17422 | 0.16309 | 0.12538 | 0.00090575 | 0.054969 | 0.10628 | -0.0025037 | -0.036621 | 0.073242 | -0.09613 | -0.082397 | 0.009155 | -0.11444 | -0.07782 | 0.44403 | 59.8343 | -62.8647 | 59.8526 | 59.9213 | 59.7473 | 0.20599 | 62.7319 | -59.8068 | -59.9625 | 62.8372 | 62.7502 | 62.7136 | 0.01831 | -0.018311 | -0.036621 | -0.045776 | -0.027466 | 122.7493 | 63.0341 | 122.5754 | 63.0707 | 122.612 | 0.10528 | 0.013733 | 122.7859 | 122.7173 | 0.16937 | 122.699 | 62.9013 | 122.6624 | -59.9762 | -122.7448 | 62.7457 | 122.6807 | 62.7914 | 63.2721
1781.8281 | 122.9599 | -62.8052 | 59.8434 | 0.00824 | -0.0029331 | -0.0072825 | 2.8945 | 0.00025629 | 0.001145 | -0.0014035 | -0.049103 | 0.16245 | 0.12623 | -0.0069982 | 0.056038 | 0.10201 | -0.0014355 | -0.041199 | 0.036621 | -0.10529 | -0.013733 | 0.20142 | 0.091553 | -0.064087 | 0.45319 | 59.7839 | -62.8464 | 59.903 | 59.9945 | 59.8114 | 0.2655 | 62.6999 | -59.8068 | -59.8572 | 63.0066 | 62.7411 | 62.8967 | 0.041199 | 0.19684 | -0.041199 | -0.059509 | 0.059509 | 122.7997 | 63.0707 | 122.6166 | 63.1119 | 122.6578 | 0.3067 | 0.091553 | 122.8409 | 122.7493 | 0.14191 | 122.6303 | 62.8418 | 122.5891 | -59.9487 | -122.6898 | 62.7914 | 122.7081 | 62.764 | 63.2584
1782.9062 | 122.8546 | -62.8647 | 59.8801 | -0.068054 | -0.0020785 | -0.0064279 | 2.8975 | 0.0011109 | 7.6842e-05 | -0.0020443 | -0.15897 | 0.16373 | 0.12794 | -0.00080325 | 0.05796 | 0.10521 | -0.0035719 | -0.091553 | 0.064087 | -0.11444 | -0.15564 | -0.09613 | -0.17395 | -0.11902 | 0.3479 | 59.8343 | -62.8967 | 59.8022 | 59.8709 | 59.6878 | 0.16937 | 62.7502 | -59.816 | -60.0357 | 62.7686 | 62.7457 | 62.6907 | -0.004578 | -0.059509 | -0.032044 | -0.045776 | -0.07782 | 122.7356 | 63.0341 | 122.5525 | 63.0661 | 122.5845 | 0.018311 | -0.041199 | 122.7676 | 122.699 | 0.17853 | 122.731 | 62.9288 | 122.699 | -59.9945 | -122.7768 | 62.709 | 122.6669 | 62.7731 | 63.2126
1783.8281 | 122.9782 | -62.8235 | 59.816 | 0.10742 | -0.0014377 | -0.0053599 | 2.8965 | -0.00059811 | 7.6842e-05 | -0.0037533 | -0.085724 | 0.16309 | 0.12815 | -0.0055028 | 0.057319 | 0.10372 | -0.00015387 | -0.11902 | -0.050354 | -0.15564 | -0.054932 | 0.045776 | -0.059509 | -0.004578 | 0.51727 | 59.7656 | -62.8098 | 59.9396 | 59.9945 | 59.8343 | 0.23346 | 62.6678 | -59.8663 | -59.8709 | 62.8693 | 62.8189 | 62.764 | 0.15106 | 0.096131 | 0.013733 | -0.050354 | 0.1236 | 122.818 | 63.0569 | 122.6578 | 63.0432 | 122.644 | 0.20142 | 0.10071 | 122.8043 | 122.7493 | 0.10529 | 122.5754 | 62.7731 | 122.5891 | -59.9716 | -122.6257 | 62.7686 | 122.7631 | 62.7045 | 63.3408
1784.8281 | 122.9416 | -62.8052 | 59.8251 | -0.029907 | 5.7742e-05 | -0.0068551 | 2.8918 | 0.0015381 | 7.6842e-05 | -0.0014035 | -0.091827 | 0.16074 | 0.12666 | -0.0046484 | 0.057106 | 0.10585 | 5.9726e-05 | -0.054932 | -0.004578 | -0.11902 | -0.059509 | 0.036621 | -0.082397 | -0.009155 | 0.4715 | 59.761 | -62.8647 | 59.9167 | 59.9762 | 59.8114 | 0.21515 | 62.6862 | -59.8297 | -59.8846 | 62.8418 | 62.796 | 62.7228 | 0.10986 | 0.036622 | -0.059509 | -0.064087 | 0.091553 | 122.7814 | 63.0203 | 122.6166 | 63.0798 | 122.6761 | 0.15564 | 0.05951 | 122.8409 | 122.7814 | 0.11444 | 122.6257 | 62.8006 | 122.5662 | -59.9442 | -122.6898 | 62.7457 | 122.7219 | 62.7502 | 63.2767
1785.8906 | 122.8775 | -62.8647 | 59.8801 | 0.00824 | -0.0012241 | -0.0062143 | 2.8954 | 0.0045289 | 7.6842e-05 | -0.0035397 | -0.17117 | 0.16459 | 0.12709 | -0.0016576 | 0.057747 | 0.10585 | -0.0031445 | -0.086975 | 0.059509 | -0.13733 | -0.11902 | -0.091553 | -0.19684 | -0.1236 | 0.36163 | 59.8343 | -62.8738 | 59.8114 | 59.8663 | 59.6695 | 0.17395 | 62.7274 | -59.8206 | -59.9991 | 62.7731 | 62.7411 | 62.6678 | 0.013733 | -0.059509 | -0.009155 | -0.045776 | -0.068665 | 122.731 | 63.0386 | 122.5342 | 63.0478 | 122.5433 | 0.045776 | 0.01831 | 122.7402 | 122.6852 | 0.19684 | 122.7081 | 62.9242 | 122.699 | -60.0174 | -122.7539 | 62.7457 | 122.6761 | 62.7777 | 63.2263
1786.8281 | 123.0286 | -62.7823 | 59.8434 | -0.045166 | -0.0014377 | -0.0062143 | 2.896 | 0.00025629 | -0.00035036 | 9.193e-05 | -0.10098 | 0.16053 | 0.12559 | 0.001974 | 0.056892 | 0.10372 | -0.0027173 | -0.036621 | -0.032043 | -0.13733 | -0.054932 | 0.045776 | -0.07782 | -0.009155 | 0.49439 | 59.761 | -62.851 | 60.0494 | 60.0586 | 59.7931 | 0.23346 | 62.645 | -59.8755 | -59.8984 | 62.8281 | 62.7731 | 62.7045 | 0.12817 | 0.059509 | -0.068664 | -0.082398 | 0.20599 | 122.8409 | 63.0157 | 122.5754 | 63.0844 | 122.644 | 0.18311 | 0.082397 | 122.9095 | 122.9004 | 0.10529 | 122.612 | 62.7502 | 122.5433 | -59.9808 | -122.6944 | 62.7274 | 122.8317 | 62.7457 | 63.2767
1787.9062 | 122.9828 | -62.7914 | 59.8434 | 0.00824 | 0.00069854 | -0.0068551 | 2.8975 | 0.0011109 | -0.00013676 | 9.193e-05 | -0.073517 | 0.16074 | 0.12773 | -0.0063574 | 0.054969 | 0.10308 | -0.0018629 | 0.064087 | 0.07782 | -0.013733 | 0.1236 | -0.004578 | -0.036621 | 0.1236 | 0.63171 | 59.7839 | -62.8189 | 59.9579 | 60.0494 | 59.8709 | 0.38452 | 62.7777 | -59.7656 | -59.7198 | 62.7869 | 62.915 | 62.7548 | 0.13733 | -0.022888 | -0.027466 | -0.059509 | 0.11444 | 122.8409 | 63.176 | 122.6624 | 63.2034 | 122.6898 | 0.009155 | 0.13733 | 122.8683 | 122.7768 | 0.091553 | 122.6028 | 62.8693 | 122.5754 | -59.8572 | -122.6624 | 62.915 | 122.7493 | 62.8555 | 63.4232
1788.8281 | 122.9736 | -62.8006 | 59.8251 | -0.068054 | -0.0016513 | -0.0085641 | 2.8947 | -0.0025207 | -0.002273 | -0.0020443 | -0.07962 | 0.16437 | 0.1273 | -0.0012304 | 0.056678 | 0.10265 | 0.0019823 | -0.032043 | -0.013733 | -0.13275 | -0.1236 | 0.064087 | 0.045776 | 0.004578 | 0.49439 | 59.7702 | -62.8326 | 59.9396 | 60.0128 | 59.8251 | 0.25177 | 62.6678 | -59.8389 | -59.9487 | 62.8647 | 62.8052 | 62.8464 | 0.13733 | 0.17853 | -0.032044 | -0.054931 | 0.11444 | 122.8134 | 63.0524 | 122.6257 | 63.0844 | 122.6578 | 0.19684 | 0.009155 | 122.8455 | 122.7722 | 0.11902 | 122.6028 | 62.7869 | 122.5708 | -59.9579 | -122.6578 | 62.677 | 122.7402 | 62.7686 | 63.295
1789.8906 | 122.9095 | -62.8693 | 59.8755 | -0.029907 | -0.0010105 | -0.0079233 | 2.8971 | 0.0028199 | -0.0018458 | 0.0013735 | -0.17117 | 0.16245 | 0.12666 | -0.0016576 | 0.055824 | 0.10585 | -0.0033581 | -0.11444 | 0.032043 | -0.16479 | -0.13275 | -0.63629 | -0.41657 | 0.23804 | 0.43488 | 59.8434 | -62.883 | 59.8434 | 59.8984 | 59.7107 | 0.16937 | 62.7045 | -59.8434 | -60.0082 | 62.233 | 63.1073 | 62.4527 | 0.40283 | -0.25177 | -0.013733 | -0.032043 | -0.032043 | 122.7676 | 63.0386 | 122.58 | 63.0524 | 122.5937 | -0.4715 | 0.032044 | 122.7814 | 122.7264 | 0.19684 | 122.7264 | 62.9013 | 122.7127 | -60.0403 | -122.7585 | 62.7365 | 122.7127 | 62.7548 | 63.3041
1790.8438 | 122.905 | -62.8235 | 59.903 | -0.022278 | -0.00015586 | -0.0072825 | 2.8933 | -0.00038451 | -0.0037684 | -0.0024717 | -0.06131 | 0.16117 | 0.12751 | -0.0042212 | 0.056038 | 0.10521 | -0.0033581 | 0.059509 | 0.086975 | -0.027466 | 0.032043 | 0.13275 | 0.041199 | 0.091553 | 0.58136 | 59.816 | -62.8235 | 59.8938 | 59.9945 | 59.8114 | 0.32501 | 62.796 | -59.816 | -59.8709 | 62.9562 | 62.915 | 62.8647 | 0.11902 | 0.068665 | 0 | -0.086975 | -0.009155 | 122.818 | 63.1485 | 122.6349 | 63.1485 | 122.6349 | 0.16022 | 0.059509 | 122.818 | 122.7173 | 0.11444 | 122.6395 | 62.9105 | 122.6395 | -59.9304 | -122.7264 | 62.8555 | 122.7173 | 62.883 | 63.4048
1791.8906 | 122.937 | -62.8464 | 59.8434 | -0.007019 | -0.0014377 | -0.0079233 | 2.8958 | 0.00089729 | -0.00077756 | -0.0011899 | -0.14676 | 0.16202 | 0.12773 | -0.00058965 | 0.059456 | 0.10585 | 0.0043323 | -0.10986 | 0.027466 | -0.14648 | -0.15106 | -0.082397 | -0.16937 | -0.11444 | 0.3891 | 59.816 | -62.883 | 59.8526 | 59.9167 | 59.7427 | 0.17853 | 62.6999 | -59.816 | -59.9945 | 62.764 | 62.7319 | 62.677 | 0.032043 | -0.022889 | -0.036621 | -0.027466 | 0.009155 | 122.7631 | 63.0249 | 122.5891 | 63.0615 | 122.6257 | 0.064087 | -0.004578 | 122.7997 | 122.7356 | 0.17395 | 122.699 | 62.8738 | 122.6624 | -59.9899 | -122.7264 | 62.6953 | 122.699 | 62.7365 | 63.2355
1792.8438 | 122.9416 | -62.8052 | 59.8389 | -0.1062 | -0.0010105 | -0.0085641 | 2.8933 | -0.0031617 | -0.00099116 | -0.0020443 | -0.073517 | 0.16309 | 0.12623 | -0.01298 | 0.056465 | 0.10457 | 0.0015551 | 0.068665 | 0.059509 | -0.045776 | 0.059509 | 0.14191 | 0.064087 | 0.091553 | 0.60425 | 59.816 | -62.8281 | 59.9121 | 60.0449 | 59.848 | 0.35706 | 62.7594 | -59.7794 | -59.7794 | 62.9471 | 62.8967 | 62.8693 | 0.13733 | 0.10986 | -0.022888 | -0.022888 | 0.073242 | 122.85 | 63.1622 | 122.6532 | 63.1851 | 122.6761 | 0.18768 | 0.10528 | 122.8729 | 122.7402 | 0.10528 | 122.644 | 62.8647 | 122.6212 | -59.8846 | -122.6669 | 62.8647 | 122.7173 | 62.8738 | 63.4094
1793.9062 | 123.0057 | -62.8281 | 59.8206 | -0.060425 | -0.0014377 | -0.0085641 | 2.8943 | 0.00089729 | -0.0018458 | 0.00030553 | -0.10098 | 0.16459 | 0.12837 | -0.002085 | 0.057106 | 0.10457 | -0.0016493 | -0.018311 | -0.036621 | -0.15564 | -0.050354 | 0.036621 | -0.082397 | -0.050354 | 0.48981 | 59.7794 | -62.8601 | 59.9487 | 60.0174 | 59.8297 | 0.25177 | 62.6724 | -59.8572 | -59.8709 | 62.8647 | 62.7777 | 62.7457 | 0.10529 | 0.073243 | -0.032043 | -0.041199 | 0.12817 | 122.8455 | 63.0798 | 122.6578 | 63.1119 | 122.6898 | 0.19226 | 0.10529 | 122.8775 | 122.8088 | 0.11902 | 122.6395 | 62.7914 | 122.6074 | -59.9762 | -122.6807 | 62.7777 | 122.7768 | 62.8098 | 63.3179
1794.8281 | 122.9874 | -62.8006 | 59.8343 | -0.075684 | 5.7742e-05 | -0.0079233 | 2.8958 | 0.0019653 | -0.002273 | -0.0014035 | -0.12234 | 0.16267 | 0.13008 | -0.006571 | 0.056251 | 0.10628 | -0.0050671 | -0.091553 | 0 | -0.16022 | -0.10529 | -0.018311 | -0.12817 | -0.064087 | 0.46234 | 59.7702 | -62.8601 | 59.9396 | 59.9945 | 59.8114 | 0.24261 | 62.6404 | -59.8343 | -59.9396 | 62.7823 | 62.7365 | 62.6724 | 0.09613 | 0.032043 | -0.059509 | -0.064087 | 0.10528 | 122.7951 | 63.0432 | 122.612 | 63.1027 | 122.6715 | 0.14191 | 0.054931 | 122.8546 | 122.7997 | 0.16022 | 122.6303 | 62.8006 | 122.5708 | -59.9945 | -122.6944 | 62.6953 | 122.7402 | 62.709 | 63.2629
1795.8438 | 122.9187 | -62.8052 | 59.8938 | 0.038757 | 5.7742e-05 | -0.0077097 | 2.8965 | 4.2692e-05 | 0.00029044 | -0.0041807 | -0.058258 | 0.16267 | 0.12666 | -0.0050756 | 0.05796 | 0.10436 | 0.00070073 | 0.050354 | 0.082397 | -0.018311 | 0.032043 | 0.13733 | 0.059509 | 0.07782 | 0.58136 | 59.8206 | -62.8281 | 59.9167 | 59.9945 | 59.8343 | 0.3479 | 62.7869 | -59.8114 | -59.8618 | 62.9425 | 62.883 | 62.8647 | 0.096131 | 0.07782 | -0.022888 | -0.073242 | 0.022888 | 122.7997 | 63.1531 | 122.6395 | 63.176 | 122.6624 | 0.15564 | 0.050354 | 122.8226 | 122.7448 | 0.10071 | 122.6486 | 62.8876 | 122.6257 | -59.9121 | -122.7219 | 62.8372 | 122.7219 | 62.8555 | 63.3865
1796.9062 | 122.9736 | -62.8326 | 59.8434 | -0.045166 | -0.0018649 | -0.0047189 | 2.8975 | -0.0023071 | -0.00035036 | 9.193e-05 | -0.14676 | 0.16395 | 0.12773 | -0.0033666 | 0.055397 | 0.10436 | -0.00015387 | -0.10529 | 0 | -0.16937 | -0.11444 | -0.027466 | -0.12817 | -0.059509 | 0.43945 | 59.7977 | -62.883 | 59.9304 | 60.0082 | 59.8022 | 0.23346 | 62.6633 | -59.8434 | -59.9579 | 62.8052 | 62.7731 | 62.7045 | 0.10986 | 0.041199 | -0.050354 | -0.045777 | 0.086975 | 122.8409 | 63.0661 | 122.6349 | 63.1165 | 122.6852 | 0.14191 | 0.054932 | 122.8912 | 122.8134 | 0.16937 | 122.6807 | 62.8326 | 122.6303 | -60.0128 | -122.7264 | 62.7182 | 122.7631 | 62.7274 | 63.2721
1797.8281 | 123.0057 | -62.7914 | 59.8572 | -0.029907 | -0.0018649 | -0.0079233 | 2.8962 | -0.0031617 | 0.00071784 | -0.0018307 | -0.049103 | 0.16352 | 0.12666 | 5.1352e-05 | 0.056251 | 0.10543 | 0.0030505 | -0.013733 | 0.041199 | -0.07782 | 0 | 0.091553 | 0.022888 | 0.068665 | 0.55389 | 59.7839 | -62.8281 | 59.9396 | 60.0449 | 59.8892 | 0.33875 | 62.7136 | -59.816 | -59.8572 | 62.883 | 62.8601 | 62.8143 | 0.14649 | 0.10071 | -0.036621 | -0.073242 | 0.082397 | 122.8363 | 63.1302 | 122.6807 | 63.1668 | 122.7173 | 0.16937 | 0.07782 | 122.8729 | 122.7676 | 0.11902 | 122.612 | 62.8326 | 122.5754 | -59.935 | -122.6852 | 62.7914 | 122.731 | 62.7777 | 63.3453
1798.9062 | 122.9874 | -62.8006 | 59.816 | -0.068054 | 5.7742e-05 | -0.010059 | 2.895 | 0.0034607 | -0.0016322 | -0.00054907 | -0.11624 | 0.16224 | 0.12837 | -0.0012304 | 0.053047 | 0.10564 | 0.00091433 | -0.054932 | -0.032043 | -0.15564 | -0.041199 | 0.041199 | -0.11444 | -0.041199 | 0.48981 | 59.7702 | -62.851 | 59.9442 | 60.0128 | 59.8297 | 0.23346 | 62.645 | -59.848 | -59.8572 | 62.8418 | 62.7594 | 62.6862 | 0.11444 | 0.041199 | -0.050354 | -0.045776 | 0.12817 | 122.8134 | 63.0341 | 122.6303 | 63.0844 | 122.6807 | 0.19684 | 0.11444 | 122.8638 | 122.7951 | 0.1236 | 122.6212 | 62.7686 | 122.5708 | -59.9716 | -122.6669 | 62.7594 | 122.7448 | 62.7457 | 63.2904
1799.8281 | 122.9141 | -62.8601 | 59.8389 | -0.26642 | 0.00069854 | -0.013477 | 2.8956 | -0.00059811 | -0.00056396 | -0.0028989 | -0.16812 | 0.16267 | 0.1273 | -0.00037605 | 0.057106 | 0.10521 | 0.0019823 | 0.23804 | -0.036621 | -0.17395 | -0.17395 | -0.032043 | -0.19226 | -0.15106 | 0.36621 | 59.8343 | -62.8967 | 59.8618 | 59.8984 | 59.7198 | 0.16022 | 62.6862 | -59.8755 | -60.0128 | 62.8281 | 62.709 | 62.6678 | 0.022888 | -0.018311 | -0.036622 | -0.004577 | 0.022888 | 122.7585 | 63.0203 | 122.58 | 63.0569 | 122.6166 | 0.14191 | 0 | 122.7951 | 122.7585 | 0.13733 | 122.731 | 62.8235 | 122.6944 | -60.0128 | -122.7356 | 62.6862 | 122.7219 | 63.0981 | 63.2263
1800.9062 | 122.8546 | -62.8555 | 59.8892 | -0.007019 | -0.0012241 | -0.0096323 | 2.8935 | 0.00046989 | 0.00029044 | 0.00073273 | -0.085724 | 0.16224 | 0.12837 | -0.0055028 | 0.057747 | 0.10329 | -0.00036747 | 0.027466 | 0.13275 | -0.059509 | -0.022888 | 0.050354 | 0.004578 | 0.036621 | 0.52185 | 59.848 | -62.8601 | 59.8618 | 59.9442 | 59.7702 | 0.29755 | 62.796 | -59.7565 | -59.9121 | 62.9059 | 62.8922 | 62.8601 | 0.09613 | 0.064087 | -0.004577 | -0.041199 | -0.027466 | 122.7997 | 63.1531 | 122.6257 | 63.1577 | 122.6303 | 0.10986 | 0.036621 | 122.8043 | 122.7219 | 0.19226 | 122.7081 | 62.9883 | 122.7036 | -59.9487 | -122.7493 | 62.8326 | 122.7173 | 62.883 | 63.3774
1801.8281 | 122.9828 | -62.8143 | 59.8297 | -0.075684 | -0.0020785 | -0.0068551 | 2.8937 | 0.0034607 | -0.0016322 | 0.00073273 | -0.13455 | 0.16053 | 0.1241 | -0.0040076 | 0.056892 | 0.10372 | -0.0031445 | -0.036621 | -0.050354 | -0.13275 | -0.22888 | -0.39368 | 0.059509 | 0.2243 | 0.55389 | 59.7702 | -62.8464 | 59.9258 | 60.0266 | 59.8297 | 0.25177 | 62.6816 | -59.8801 | -60.0586 | 62.4207 | 63.0386 | 62.8738 | 0.35706 | 0.19226 | -0.032044 | -0.059509 | 0.09613 | 122.8409 | 63.0661 | 122.644 | 63.0981 | 122.6761 | -0.26093 | -0.096131 | 122.8729 | 122.7722 | 0.082397 | 122.6166 | 62.764 | 122.5845 | -59.9625 | -122.6761 | 62.5854 | 122.7402 | 62.7777 | 63.3682
1802.9062 | 122.8592 | -62.8372 | 59.9121 | -0.022278 | 0.00027134 | -0.0072825 | 2.8941 | 0.00025629 | 0.0034948 | -0.0039671 | -0.11624 | 0.16416 | 0.12794 | -0.0069982 | 0.056251 | 0.10244 | -0.0018629 | 0.009155 | 0.16022 | -0.022888 | -0.013733 | 0.050354 | -0.027466 | 0.036621 | 0.48523 | 59.8389 | -62.8464 | 59.7931 | 59.8434 | 59.8068 | 0.31586 | 62.8143 | -59.7519 | -59.9258 | 62.8876 | 62.8738 | 62.8098 | 0.059509 | -0.004578 | -0.009156 | -0.073242 | -0.11902 | 122.6807 | 63.1531 | 122.644 | 63.1622 | 122.6532 | 0.073242 | 0.009155 | 122.6898 | 122.6395 | 0.1831 | 122.6852 | 62.9974 | 122.6761 | -59.935 | -122.7585 | 62.8235 | 122.6303 | 62.8464 | 63.3224
1803.8281 | 123.0057 | -62.8098 | 59.848 | -0.022278 | 0.0011257 | -0.0060007 | 2.8958 | 0.0011109 | -0.0018458 | 0.0015871 | -0.11319 | 0.16224 | 0.12922 | 0.00026495 | 0.057319 | 0.10201 | -0.0042127 | -0.054932 | -0.032043 | -0.13275 | -0.068665 | 0.032043 | -0.091553 | -0.041199 | 0.49439 | 59.7473 | -62.851 | 59.9396 | 60.0266 | 59.8389 | 0.23346 | 62.677 | -59.8801 | -59.9167 | 62.8418 | 62.7686 | 62.7182 | 0.091552 | 0.041198 | -0.041199 | -0.10071 | 0.091553 | 122.8363 | 63.0432 | 122.6486 | 63.0844 | 122.6898 | 0.16479 | 0.064086 | 122.8775 | 122.7905 | 0.10071 | 122.5983 | 62.7777 | 122.5571 | -59.9808 | -122.699 | 62.7411 | 122.7493 | 62.7548 | 63.3041
1804.8906 | 122.8729 | -62.8647 | 59.8618 | -0.014649 | -0.0012241 | -0.0055735 | 2.8971 | 0.00068369 | -0.0044092 | -0.0024717 | -0.14676 | 0.16373 | 0.12794 | 0.0034692 | 0.056251 | 0.10564 | -0.0022901 | -0.041199 | 0.07782 | -0.10986 | -0.10071 | -0.022888 | -0.10071 | -0.068665 | 0.4303 | 59.8343 | -62.8784 | 59.8618 | 59.903 | 59.7198 | 0.20142 | 62.7548 | -59.7839 | -59.9625 | 62.8418 | 62.796 | 62.764 | 0.041198 | 0.009155 | -0.013733 | -0.027465 | 0 | 122.7676 | 63.0661 | 122.5845 | 63.0798 | 122.5983 | 0.086975 | 0.009155 | 122.7814 | 122.7402 | 0.18768 | 122.7127 | 62.9425 | 122.699 | -59.9716 | -122.7402 | 62.764 | 122.7264 | 62.8235 | 63.295
1805.8438 | 123.024 | -62.8143 | 59.8526 | -0.098572 | -0.0022923 | -0.0094187 | 2.8939 | 4.2692e-05 | 0.00071784 | -0.0014035 | -0.049103 | 0.16331 | 0.12944 | -0.0042212 | 0.055824 | 0.10436 | 0.0011279 | 0.059509 | 0.064087 | -0.032043 | 0.050354 | 0.17853 | 0.086975 | 0.12817 | 0.63171 | 59.8068 | -62.8326 | 59.967 | 60.0815 | 59.9167 | 0.37994 | 62.7823 | -59.7885 | -59.8022 | 62.9929 | 62.9425 | 62.9013 | 0.16022 | 0.11902 | -0.018311 | -0.045776 | 0.11444 | 122.8958 | 63.1943 | 122.731 | 63.2126 | 122.7493 | 0.21057 | 0.082397 | 122.9141 | 122.7997 | 0.09613 | 122.6395 | 62.8784 | 122.6212 | -59.8846 | -122.6852 | 62.8647 | 122.7814 | 62.8738 | 63.446
1806.8906 | 122.9095 | -62.8555 | 59.8709 | 0.031128 | -0.0010105 | -0.0060007 | 2.8952 | 0.0045289 | -0.0020594 | -0.00054907 | -0.16812 | 0.16395 | 0.12858 | 0.00026495 | 0.056251 | 0.10521 | 0.00070073 | -0.004578 | 0.064087 | -0.086975 | -0.064087 | 0.027466 | -0.07782 | -0.032043 | 0.49439 | 59.8068 | -62.8464 | 59.8801 | 59.9213 | 59.7565 | 0.23804 | 62.7686 | -59.8068 | -59.935 | 62.883 | 62.8235 | 62.7777 | 0.054932 | 0.009155 | 0.009155 | -0.064087 | 0.009155 | 122.7768 | 63.0936 | 122.612 | 63.0844 | 122.6028 | 0.11444 | 0.022888 | 122.7676 | 122.7264 | 0.15106 | 122.6532 | 62.9196 | 122.6624 | -59.9579 | -122.7173 | 62.7914 | 122.7356 | 62.851 | 63.3499
1807.8438 | 122.9828 | -62.8555 | 59.8297 | -0.12146 | -0.00015586 | -0.0079233 | 2.8956 | 0.0021789 | -0.00099116 | -0.0011899 | -0.088776 | 0.16309 | 0.12986 | -0.0050756 | 0.056038 | 0.10564 | -0.0025037 | 0.032043 | -0.041199 | -0.11902 | -0.041199 | 0.059509 | -0.068665 | 0.013733 | 0.51727 | 59.7702 | -62.8601 | 59.9258 | 60.0037 | 59.8434 | 0.25177 | 62.7365 | -59.8709 | -59.8709 | 62.915 | 62.8693 | 62.7869 | 0.13275 | 0.050354 | -0.004577 | -0.059509 | 0.09613 | 122.8592 | 63.1073 | 122.699 | 63.1119 | 122.7036 | 0.17853 | 0.07782 | 122.8638 | 122.7859 | 0.07782 | 122.6303 | 62.8143 | 122.6257 | -59.9487 | -122.6898 | 62.8143 | 122.7814 | 62.8876 | 63.3728
1808.8906 | 122.9691 | -62.8647 | 59.848 | -0.045166 | 0.00027134 | -0.0077097 | 2.8947 | 0.00068369 | 0.00029044 | -0.00076267 | -0.16812 | 0.16267 | 0.12901 | -0.0063574 | 0.056038 | 0.10585 | -0.0012219 | -0.10986 | 0.027466 | -0.15106 | -0.13733 | -0.041199 | -0.16479 | -0.10071 | 0.40741 | 59.8114 | -62.8601 | 59.8892 | 59.935 | 59.7702 | 0.20599 | 62.7136 | -59.8206 | -59.9854 | 62.8235 | 62.764 | 62.6999 | 0.050354 | -0.013733 | 0.004578 | -0.036621 | 0.041199 | 122.7997 | 63.0707 | 122.6349 | 63.0661 | 122.6303 | 0.10986 | 0.013733 | 122.7951 | 122.7493 | 0.17853 | 122.6715 | 62.8922 | 122.6761 | -59.9991 | -122.7081 | 62.7274 | 122.7539 | 62.7548 | 63.2721
1809.8281 | 122.9187 | -62.8601 | 59.8572 | 0.023498 | -0.00036966 | -0.0089913 | 2.8967 | 0.0021789 | 7.6842e-05 | -0.00033547 | -0.12234 | 0.16267 | 0.12751 | -0.003153 | 0.057533 | 0.10393 | -0.0031445 | -0.1236 | 0.041199 | -0.14191 | -0.16022 | -0.068665 | -0.17395 | -0.11444 | 0.39368 | 59.8022 | -62.883 | 59.8801 | 59.9258 | 59.7656 | 0.1831 | 62.7182 | -59.816 | -60.0174 | 62.7914 | 62.7457 | 62.6862 | 0.027466 | -0.032043 | -0.022889 | -0.054932 | 0.022888 | 122.7859 | 63.0432 | 122.6257 | 63.0661 | 122.6486 | 0.073242 | -0.01831 | 122.8088 | 122.7631 | 0.18311 | 122.6852 | 62.9013 | 122.6624 | -59.9991 | -122.7402 | 62.6999 | 122.7402 | 62.7365 | 63.2538
1810.9062 | 122.9919 | -62.8235 | 59.8343 | -0.037537 | -0.0018649 | -0.0077097 | 2.895 | 0.0053833 | -0.0018458 | 0.0018009 | -0.097931 | 0.16117 | 0.12666 | -0.0012304 | 0.057533 | 0.10393 | -0.00036747 | -0.091553 | -0.027466 | -0.15106 | -0.082397 | 0.022888 | -0.086975 | -0.059509 | 0.48065 | 59.7839 | -62.8738 | 59.9533 | 60.0174 | 59.8251 | 0.24261 | 62.6724 | -59.8618 | -59.9167 | 62.8464 | 62.764 | 62.7365 | 0.091553 | 0.064087 | -0.050354 | -0.050354 | 0.11902 | 122.8409 | 63.0661 | 122.6486 | 63.1165 | 122.699 | 0.17395 | 0.068665 | 122.8912 | 122.8271 | 0.1236 | 122.6578 | 62.796 | 122.6074 | -59.9854 | -122.7081 | 62.7411 | 122.7768 | 62.7319 | 63.3041
1811.8281 | 122.9279 | -62.8647 | 59.8663 | -0.068054 | -0.0027195 | -0.0081369 | 2.8954 | 0.0030335 | -0.00056396 | -0.0014035 | -0.15591 | 0.16502 | 0.12709 | -0.0050756 | 0.05796 | 0.10329 | -0.00036747 | 0.25635 | -0.004578 | -0.1831 | -0.10529 | -0.054932 | -0.21973 | -0.10986 | 0.37994 | 59.8114 | -62.8738 | 59.8526 | 59.9121 | 59.729 | 0.16479 | 62.6816 | -59.8709 | -59.9716 | 62.8098 | 62.7548 | 62.645 | 0.073242 | -0.036622 | -0.009155 | -0.054932 | -0.013733 | 122.7768 | 63.0295 | 122.5937 | 63.0386 | 122.6028 | 0.12817 | 0.077819 | 122.7859 | 122.7264 | 0.17853 | 122.6852 | 62.8601 | 122.6761 | -60.0494 | -122.7402 | 62.7594 | 122.7173 | 63.121 | 63.2446
1812.9062 | 122.9279 | -62.8601 | 59.8389 | 0.031128 | -0.0014377 | -0.0089913 | 2.8967 | -0.0031617 | -0.0016322 | -0.0020443 | -0.11929 | 0.1648 | 0.12709 | -0.00080325 | 0.056465 | 0.10564 | 0.0017687 | -0.13275 | 0.045776 | -0.14191 | -0.17395 | -0.073242 | -0.16479 | -0.11444 | 0.37994 | 59.7885 | -62.8784 | 59.8709 | 59.9167 | 59.7244 | 0.17395 | 62.7182 | -59.7931 | -60.0128 | 62.7869 | 62.7457 | 62.6953 | 0.027466 | -0.022888 | -0.018311 | -0.050354 | 0.032044 | 122.7768 | 63.0341 | 122.5845 | 63.0524 | 122.6028 | 0.068665 | -0.032043 | 122.7951 | 122.7493 | 0.18768 | 122.6669 | 62.9059 | 122.6486 | -59.9808 | -122.7173 | 62.6862 | 122.731 | 62.7274 | 63.2401
1813.8281 | 122.8821 | -62.883 | 59.8709 | -0.098572 | -0.0018649 | -0.0057871 | 2.8945 | 0.0011109 | -0.0016322 | 0.00051913 | -0.097931 | 0.16502 | 0.12837 | -0.0022986 | 0.055824 | 0.10607 | -0.0010083 | -0.11444 | 0.036621 | -0.15564 | -0.13733 | -0.27466 | -0.72327 | -0.086975 | 0.32501 | 59.816 | -62.8738 | 59.8343 | 59.8938 | 59.7153 | 0.16479 | 62.7274 | -59.8343 | -60.0082 | 62.6083 | 62.796 | 62.1597 | 0.068665 | -0.56763 | 0.009156 | -0.054932 | -0.036621 | 122.7768 | 63.0478 | 122.5983 | 63.0386 | 122.5891 | -0.11902 | 0.018311 | 122.7676 | 122.7081 | 0.19226 | 122.6898 | 62.9196 | 122.699 | -60.0266 | -122.7448 | 62.7457 | 122.7173 | 62.7686 | 63.208
1814.8281 | 122.8912 | -62.8372 | 59.8618 | -0.029907 | -0.00036966 | -0.0060007 | 2.8954 | 0.0021789 | 7.6842e-05 | -0.0026853 | -0.12845 | 0.16459 | 0.12623 | 0.0021876 | 0.056678 | 0.1065 | 0.00027333 | -0.064087 | 0.059509 | -0.14191 | -0.14191 | -0.041199 | -0.1236 | -0.091553 | 0.37079 | 59.8389 | -62.883 | 59.8206 | 59.8892 | 59.7015 | 0.17395 | 62.6953 | -59.8022 | -60.0037 | 62.796 | 62.7457 | 62.7136 | 0.050354 | 0.018311 | -0.045777 | -0.022888 | -0.041198 | 122.7264 | 63.0112 | 122.5388 | 63.0569 | 122.5845 | 0.10071 | 0 | 122.7722 | 122.7036 | 0.20142 | 122.7219 | 62.8967 | 122.6761 | -60.0037 | -122.7448 | 62.6953 | 122.6578 | 62.7731 | 63.208
1815.9062 | 122.9965 | -62.8326 | 59.8297 | -0.060425 | -0.0014377 | -0.0077097 | 2.8945 | 0.0017517 | -0.00077756 | -0.00076267 | -0.088776 | 0.16288 | 0.1273 | -0.0040076 | 0.060524 | 0.10521 | -0.0020765 | -0.086975 | -0.045776 | -0.14648 | -0.086975 | 0.022888 | -0.09613 | -0.041199 | 0.4715 | 59.7565 | -62.8647 | 59.9442 | 60.0174 | 59.848 | 0.25177 | 62.6862 | -59.8755 | -59.9167 | 62.8555 | 62.7914 | 62.7365 | 0.10529 | 0.050354 | -0.032043 | -0.073242 | 0.11444 | 122.85 | 63.0844 | 122.6807 | 63.1165 | 122.7127 | 0.16937 | 0.059509 | 122.8821 | 122.8088 | 0.10071 | 122.6212 | 62.7869 | 122.5891 | -59.9762 | -122.6944 | 62.7457 | 122.7768 | 62.7457 | 63.3041
1816.8281 | 122.8729 | -62.8601 | 59.8709 | -0.007019 | -0.0020785 | -0.0096323 | 2.898 | 0.00025629 | 0.001145 | -0.0020443 | -0.15286 | 0.16245 | 0.1273 | -0.002085 | 0.055824 | 0.10479 | 0.00091433 | -0.054932 | 0.073242 | -0.09613 | -0.10529 | -0.045776 | -0.13275 | -0.07782 | 0.41199 | 59.8206 | -62.8784 | 59.8251 | 59.903 | 59.6924 | 0.17853 | 62.764 | -59.7977 | -59.9762 | 62.8143 | 62.7823 | 62.7274 | 0.01831 | -0.036621 | -0.018311 | -0.050354 | -0.045777 | 122.7631 | 63.0386 | 122.5525 | 63.0569 | 122.5708 | 0.050354 | -0.009156 | 122.7814 | 122.7036 | 0.16937 | 122.699 | 62.9333 | 122.6807 | -59.967 | -122.7493 | 62.7548 | 122.6852 | 62.8052 | 63.2721
1817.9062 | 122.9874 | -62.8098 | 59.8434 | -0.098572 | 5.7742e-05 | -0.0081369 | 2.8954 | 0.0032471 | -0.0027002 | -0.0046079 | -0.10403 | 0.16267 | 0.12645 | -0.0012304 | 0.057106 | 0.10393 | -0.0029309 | -0.086975 | -0.004578 | -0.13733 | -0.10529 | 0 | -0.10071 | -0.045776 | 0.49439 | 59.761 | -62.851 | 59.9396 | 60.0128 | 59.8251 | 0.25177 | 62.6724 | -59.848 | -59.9487 | 62.8098 | 62.764 | 62.709 | 0.091553 | 0.036621 | -0.041199 | -0.082398 | 0.09613 | 122.8226 | 63.0615 | 122.6349 | 63.1027 | 122.6761 | 0.13733 | 0.032043 | 122.8638 | 122.7905 | 0.13275 | 122.612 | 62.8052 | 122.5708 | -59.9808 | -122.6944 | 62.7045 | 122.7493 | 62.7228 | 63.3041
1818.8281 | 122.8546 | -62.8876 | 59.8618 | -0.045166 | 0.00091214 | -0.0077097 | 2.8973 | 0.0013245 | 0.0015722 | -0.0033261 | -0.14371 | 0.16331 | 0.12751 | -0.0022986 | 0.057533 | 0.10671 | -0.0014355 | -0.086975 | 0.045776 | -0.1236 | -0.20142 | -0.10529 | -0.20142 | -0.1236 | 0.33875 | 59.8389 | -62.9013 | 59.8114 | 59.8801 | 59.7061 | 0.17395 | 62.764 | -59.816 | -60.0632 | 62.7823 | 62.764 | 62.6862 | 0 | -0.07782 | -0.013733 | -0.022888 | -0.050354 | 122.7676 | 63.0615 | 122.5937 | 63.0753 | 122.6074 | 0.01831 | -0.07782 | 122.7814 | 122.7127 | 0.16937 | 122.7402 | 62.9333 | 122.7264 | -59.9854 | -122.7631 | 62.6862 | 122.699 | 62.8006 | 63.2263
1819.8906 | 122.9416 | -62.8464 | 59.8846 | 0.015869 | -0.0010105 | -0.0070687 | 2.8947 | 0.0021789 | -0.0014184 | -0.0024717 | -0.082672 | 0.16181 | 0.12901 | -0.0057166 | 0.056678 | 0.10479 | 0.0032641 | 0.032043 | 0.11902 | -0.068665 | -0.050354 | 0.045776 | -0.036621 | 0.013733 | 0.50354 | 59.848 | -62.8464 | 59.903 | 59.9762 | 59.7794 | 0.32501 | 62.7777 | -59.7656 | -59.935 | 62.8922 | 62.8601 | 62.8098 | 0.082398 | 0.032044 | 0 | -0.036622 | 0.01831 | 122.8226 | 63.1714 | 122.6257 | 63.1714 | 122.6257 | 0.11444 | 0.018311 | 122.8226 | 122.7493 | 0.18768 | 122.6944 | 62.9654 | 122.6944 | -59.9533 | -122.731 | 62.796 | 122.7493 | 62.8784 | 63.3499
1820.8281 | 122.9095 | -62.8418 | 59.8938 | -0.060425 | -0.0012241 | -0.0083505 | 2.8947 | 0.0073059 | -0.002273 | -0.0033261 | -0.1315 | 0.16502 | 0.12837 | -0.0027258 | 0.05561 | 0.10479 | 0.00070073 | -0.018311 | 0.082397 | -0.07782 | -0.054932 | 0.022888 | -0.086975 | -0.032043 | 0.50354 | 59.8297 | -62.8555 | 59.8709 | 59.9396 | 59.7565 | 0.24719 | 62.764 | -59.8114 | -59.9487 | 62.8647 | 62.8098 | 62.7548 | 0.045777 | -0.009155 | -0.013733 | -0.064087 | -0.022888 | 122.7814 | 63.089 | 122.5983 | 63.1027 | 122.612 | 0.10071 | 0.022888 | 122.7951 | 122.7264 | 0.16022 | 122.6852 | 62.9242 | 122.6715 | -59.9716 | -122.7493 | 62.7869 | 122.7127 | 62.8235 | 63.3453
1821.8906 | 122.905 | -62.8647 | 59.8984 | -0.014649 | -0.00036966 | -0.0077097 | 2.8941 | 0.0038879 | 0.0015722 | -0.0018307 | -0.1315 | 0.16331 | 0.12751 | -0.0033666 | 0.056465 | 0.10393 | -0.0025037 | -0.022888 | 0.091553 | -0.10986 | -0.068665 | 0.036621 | -0.07782 | -0.054932 | 0.48981 | 59.8068 | -62.851 | 59.8618 | 59.9396 | 59.7565 | 0.23804 | 62.7548 | -59.8068 | -59.967 | 62.9013 | 62.8098 | 62.7869 | 0.054931 | 0.032043 | 0.013733 | -0.091552 | -0.036621 | 122.8043 | 63.1027 | 122.6212 | 63.089 | 122.6074 | 0.14648 | 0.041198 | 122.7905 | 122.7127 | 0.20142 | 122.6578 | 62.9562 | 122.6715 | -60.0082 | -122.7493 | 62.796 | 122.7264 | 62.8418 | 63.3545
1822.8281 | 122.9874 | -62.851 | 59.8434 | -0.022278 | -0.00058326 | -0.0072825 | 2.8965 | 0.0015381 | -0.0031274 | -0.00033547 | -0.097931 | 0.1616 | 0.12858 | -0.0042212 | 0.056465 | 0.10692 | 0.0041187 | -0.10529 | 0.004578 | -0.16937 | -0.11902 | -0.032043 | -0.13733 | -0.068665 | 0.44861 | 59.8068 | -62.8693 | 59.9213 | 59.9579 | 59.8297 | 0.24261 | 62.6816 | -59.8389 | -59.9625 | 62.8189 | 62.7823 | 62.7136 | 0.10071 | 0.032044 | -0.018311 | -0.036621 | 0.07782 | 122.8088 | 63.0936 | 122.6807 | 63.1119 | 122.699 | 0.13733 | 0.050354 | 122.8271 | 122.7905 | 0.17395 | 122.6761 | 62.8555 | 122.6578 | -60.0128 | -122.7127 | 62.7319 | 122.7722 | 62.7457 | 63.2996
1823.8906 | 122.9279 | -62.8464 | 59.8984 | 0.023498 | -0.0010105 | -0.0087777 | 2.8947 | 0.0011109 | -0.0014184 | -0.00076267 | -0.10403 | 0.16416 | 0.12709 | -0.00058965 | 0.055397 | 0.10628 | -0.0018629 | 0 | 0.09613 | -0.068665 | -0.041199 | 0.073242 | -0.018311 | 0.018311 | 0.54474 | 59.8114 | -62.8693 | 59.8846 | 59.9487 | 59.7931 | 0.31586 | 62.7777 | -59.8022 | -59.9396 | 62.9196 | 62.8647 | 62.8281 | 0.086976 | 0.050354 | -0.022888 | -0.086975 | -0.013732 | 122.7951 | 63.1622 | 122.6395 | 63.1851 | 122.6624 | 0.14191 | 0.027466 | 122.818 | 122.7539 | 0.16479 | 122.6807 | 62.9425 | 122.6578 | -59.967 | -122.7676 | 62.8052 | 122.731 | 62.8464 | 63.3911
1824.8281 | 122.9828 | -62.8418 | 59.8251 | -0.075684 | 5.7742e-05 | -0.0079233 | 2.8947 | 0.0028199 | 0.0015722 | -0.0016171 | -0.11624 | 0.16288 | 0.12751 | -0.0057166 | 0.056678 | 0.10479 | -0.00036747 | -0.09613 | 0.009155 | -0.14191 | -0.14648 | -0.045776 | -0.16479 | -0.10071 | 0.41199 | 59.7885 | -62.883 | 59.8938 | 59.9487 | 59.7748 | 0.20142 | 62.6999 | -59.816 | -59.9716 | 62.796 | 62.7411 | 62.677 | 0.041199 | -0.022888 | -0.041199 | -0.036621 | 0.068665 | 122.7905 | 63.0432 | 122.6166 | 63.0844 | 122.6578 | 0.096131 | -0.004577 | 122.8317 | 122.7768 | 0.15106 | 122.6715 | 62.851 | 122.6303 | -59.967 | -122.7081 | 62.6953 | 122.7356 | 62.7457 | 63.2538
1825.8906 | 122.9324 | -62.8555 | 59.8846 | -0.014649 | -0.0012241 | -0.0074961 | 2.8971 | 0.0041015 | -0.0014184 | -0.00097627 | -0.12234 | 0.16288 | 0.12709 | -0.0042212 | 0.057319 | 0.10607 | -0.0029309 | 0.004578 | 0.082397 | -0.082397 | -0.07782 | -0.022888 | -0.33417 | -0.050354 | 0.52643 | 59.8068 | -62.8601 | 59.8938 | 59.9625 | 59.7748 | 0.27924 | 62.7731 | -59.8022 | -59.9625 | 62.8326 | 62.8052 | 62.5214 | 0.032043 | -0.25177 | -0.004577 | -0.07782 | 0.009155 | 122.818 | 63.1348 | 122.6303 | 63.1393 | 122.6349 | 0.059509 | 0.004577 | 122.8226 | 122.7539 | 0.16479 | 122.6669 | 62.9379 | 122.6624 | -59.967 | -122.7448 | 62.7777 | 122.7493 | 62.8601 | 63.382
1826.8281 | 122.9187 | -62.8418 | 59.9121 | -0.014649 | -0.0033603 | -0.0083505 | 2.8954 | 0.00089729 | 7.6842e-05 | -0.0048215 | -0.11319 | 0.16352 | 0.12751 | -0.0033666 | 0.057106 | 0.105 | 0.0013415 | -0.009155 | 0.064087 | -0.09613 | -0.07782 | 0.032043 | -0.07782 | -0.036621 | 0.5127 | 59.8389 | -62.8693 | 59.8709 | 59.9258 | 59.7473 | 0.25635 | 62.7457 | -59.848 | -59.9899 | 62.8738 | 62.8052 | 62.764 | 0.059509 | 0.01831 | -0.027466 | -0.073242 | -0.041198 | 122.7676 | 63.0981 | 122.5891 | 63.1256 | 122.6166 | 0.12817 | 0.01831 | 122.7951 | 122.7402 | 0.16022 | 122.7081 | 62.9059 | 122.6807 | -60.0082 | -122.7814 | 62.764 | 122.7127 | 62.8326 | 63.3545
1827.9062 | 123.0057 | -62.8235 | 59.8618 | -0.037537 | -0.0016513 | -0.0081369 | 2.893 | -0.00038451 | 0.0017858 | -0.0031125 | -0.018585 | 0.16181 | 0.12666 | -0.0025122 | 0.057533 | 0.1035 | -0.0014355 | 0 | 0.068665 | -0.041199 | -0.004578 | 0.12817 | 0.041199 | 0.082397 | 0.60883 | 59.7931 | -62.8464 | 59.9625 | 60.0723 | 59.8846 | 0.37079 | 62.7823 | -59.7931 | -59.8663 | 62.9517 | 62.9059 | 62.8647 | 0.1236 | 0.082398 | -0.022889 | -0.068664 | 0.10071 | 122.8958 | 63.1943 | 122.7081 | 63.2172 | 122.731 | 0.16937 | 0.036621 | 122.9187 | 122.8088 | 0.10986 | 122.6395 | 62.8922 | 122.6166 | -59.903 | -122.7081 | 62.8189 | 122.7859 | 62.8235 | 63.4323
1828.8281 | 123.0148 | -62.8784 | 59.8389 | -0.037537 | 0.00069854 | -0.0062143 | 2.8971 | 0.00025629 | 7.6842e-05 | -0.0033261 | -0.1315 | 0.16502 | 0.12666 | 0.00047855 | 0.056465 | 0.10436 | -0.00058107 | -0.091553 | 0.045776 | -0.14191 | -0.18768 | -0.10986 | -0.19226 | -0.11444 | 0.36621 | 59.8022 | -62.8967 | 59.8297 | 59.8892 | 59.7015 | 0.17853 | 62.7365 | -59.7931 | -60.0266 | 62.7686 | 62.764 | 62.6862 | 0.027466 | -0.050354 | -0.018311 | -0.036621 | -0.009155 | 122.7676 | 63.0569 | 122.58 | 63.0753 | 122.5983 | 0.032044 | -0.045776 | 122.7859 | 122.7264 | 0.18768 | 122.699 | 62.9242 | 122.6807 | -59.9808 | -122.7356 | 62.6907 | 122.7081 | 62.7869 | 63.2446
1829.8906 | 122.8821 | -62.8189 | 59.903 | 0.00061049 | -0.00058326 | -0.0089913 | 2.8943 | -0.0029479 | -0.0016322 | -0.0028989 | -0.073517 | 0.16267 | 0.12773 | -0.006571 | 0.057747 | 0.10521 | 0.0017687 | 0.004578 | 0.1236 | -0.041199 | -0.041199 | 0.032043 | -0.018311 | 0.050354 | 0.50812 | 59.8434 | -62.8647 | 59.848 | 59.9442 | 59.7702 | 0.29297 | 62.7777 | -59.7794 | -59.9442 | 62.851 | 62.8693 | 62.8006 | 0.091553 | 0.022888 | -0.045776 | -0.059509 | -0.054932 | 122.7631 | 63.1119 | 122.5891 | 63.1577 | 122.6349 | 0.073242 | 0 | 122.8088 | 122.7127 | 0.16479 | 122.7081 | 62.9425 | 122.6624 | -59.9442 | -122.7676 | 62.7777 | 122.6669 | 62.8235 | 63.327
1830.8281 | 122.8729 | -62.8738 | 59.8755 | -0.037537 | 0.00027134 | -0.0074961 | 2.8965 | -0.00038451 | -0.0016322 | -0.0033261 | -0.097931 | 0.16437 | 0.1288 | 0.00069215 | 0.056465 | 0.10457 | 0.0017687 | -0.09613 | 0.050354 | -0.13275 | -0.17853 | -0.10071 | -0.17853 | -0.11902 | 0.3479 | 59.8297 | -62.8738 | 59.8297 | 59.8663 | 59.7153 | 0.18768 | 62.7411 | -59.8251 | -60.054 | 62.7731 | 62.7548 | 62.6953 | 0.013732 | -0.045777 | 0 | -0.045776 | -0.045776 | 122.7402 | 63.0615 | 122.5891 | 63.0615 | 122.5891 | 0.032043 | -0.045777 | 122.7402 | 122.7036 | 0.18311 | 122.7036 | 62.9242 | 122.7036 | -60.0082 | -122.7493 | 62.6953 | 122.7036 | 62.7777 | 63.2217
1831.8906 | 122.9645 | -62.8006 | 59.8892 | -0.029907 | -0.0012241 | -0.0079233 | 2.895 | 0.0013245 | -0.00056396 | -0.00033547 | -0.10403 | 0.16416 | 0.12944 | -0.0059302 | 0.056892 | 0.10393 | -0.0027173 | 0.018311 | 0.10071 | -0.073242 | -0.036621 | 0.068665 | -0.027466 | 0.013733 | 0.54474 | 59.8297 | -62.8601 | 59.9075 | 59.9762 | 59.7977 | 0.31128 | 62.7274 | -59.7885 | -59.9258 | 62.8693 | 62.8143 | 62.7731 | 0.086975 | 0.045776 | -0.059509 | -0.059509 | 0.018311 | 122.7768 | 63.1119 | 122.5983 | 63.1714 | 122.6578 | 0.14191 | 0.036621 | 122.8363 | 122.7676 | 0.17395 | 122.6898 | 62.9013 | 122.6303 | -59.9625 | -122.7493 | 62.764 | 122.7081 | 62.8189 | 63.3453
1832.8438 | 123.0194 | -62.8143 | 59.8709 | -0.1062 | -0.0018649 | -0.0066415 | 2.8941 | 0.0017517 | -0.00056396 | -0.0014035 | -0.036896 | 0.16373 | 0.12666 | -0.0052892 | 0.057319 | 0.10479 | 0.0017687 | -0.045776 | 0.018311 | -0.10529 | -0.068665 | 0.041199 | -0.064087 | -0.004578 | 0.46692 | 59.7885 | -62.851 | 59.8938 | 59.9945 | 59.8206 | 0.36163 | 62.709 | -59.8526 | -59.9396 | 62.8555 | 62.8098 | 62.7502 | 0.10071 | 0.041199 | -0.036621 | -0.082398 | 0.022888 | 122.8088 | 63.176 | 122.6349 | 63.2126 | 122.6715 | 0.14649 | 0.036621 | 122.8455 | 122.7448 | 0.1236 | 122.6395 | 62.8326 | 122.6028 | -59.9762 | -122.7219 | 62.7457 | 122.7081 | 62.7686 | 63.2812
1833.8906 | 122.9462 | -62.8326 | 59.8755 | -0.029907 | 0.00048494 | -0.0068551 | 2.8943 | 4.2692e-05 | -0.002273 | -0.00033547 | -0.11014 | 0.16288 | 0.12986 | 0.0053918 | 0.056678 | 0.10585 | 5.9726e-05 | 0 | 0.059509 | -0.091553 | 0.036621 | 0.059509 | -0.018311 | 0 | 0.52643 | 59.8251 | -62.8738 | 59.8846 | 59.9579 | 59.7748 | 0.25177 | 62.7411 | -59.816 | -59.8389 | 62.8922 | 62.8326 | 62.8143 | 0.091553 | 0.073242 | -0.041198 | -0.050354 | 0.009156 | 122.7905 | 63.0844 | 122.6074 | 63.1256 | 122.6486 | 0.15106 | 0.12817 | 122.8317 | 122.7585 | 0.15106 | 122.699 | 62.8922 | 122.6578 | -59.967 | -122.7493 | 62.8693 | 122.7173 | 62.8326 | 63.3591
1834.8281 | 122.9141 | -62.8281 | 59.8755 | 0.00061049 | -0.0020785 | -0.0081369 | 2.8954 | 0.00046989 | -0.00077756 | -0.0016171 | -0.1315 | 0.16523 | 0.12815 | -0.0012304 | 0.056465 | 0.10436 | -0.00058107 | -0.018311 | 0.064087 | -0.091553 | -0.07782 | 0.009155 | -0.09613 | -0.032043 | 0.4715 | 59.8526 | -62.8876 | 59.8618 | 59.935 | 59.7565 | 0.23346 | 62.7365 | -59.8114 | -59.9533 | 62.8372 | 62.796 | 62.7319 | 0.05951 | -0.004577 | -0.059509 | -0.022888 | -0.013733 | 122.7631 | 63.0615 | 122.5845 | 63.121 | 122.644 | 0.10071 | 0.013733 | 122.8226 | 122.7493 | 0.15564 | 122.7402 | 62.8922 | 122.6807 | -59.967 | -122.7631 | 62.7502 | 122.6898 | 62.8098 | 63.2996
1835.8906 | 122.8821 | -62.8555 | 59.8572 | -0.052796 | 0.00069854 | -0.0098459 | 2.895 | -0.00017091 | -0.00035036 | -0.00076267 | -0.11624 | 0.16373 | 0.12709 | 0.0028284 | 0.057319 | 0.1035 | -0.0018629 | -0.027466 | 0.045776 | -0.10986 | -0.10071 | -0.009155 | -0.11444 | -0.073242 | 0.43488 | 59.8297 | -62.8784 | 59.8526 | 59.9167 | 59.7107 | 0.21515 | 62.7457 | -59.8114 | -59.9579 | 62.8464 | 62.7823 | 62.7411 | 0.036621 | -0.004578 | -0.022888 | -0.027466 | -0.004578 | 122.7722 | 63.0707 | 122.5662 | 63.0936 | 122.5891 | 0.10071 | 0.009155 | 122.7951 | 122.731 | 0.15564 | 122.7081 | 62.9013 | 122.6852 | -59.967 | -122.7356 | 62.7548 | 122.7081 | 62.8281 | 63.2904
1836.8281 | 122.8867 | -62.851 | 59.8755 | -0.052796 | -0.00036966 | -0.0083505 | 2.8971 | 0.0019653 | -0.00099116 | -0.0014035 | -0.094879 | 0.16544 | 0.1288 | 0.0026148 | 0.057533 | 0.10692 | -0.0014355 | -0.009155 | 0.082397 | -0.09613 | -0.07782 | 0.009155 | -0.09613 | -0.018311 | 0.46234 | 59.8251 | -62.8738 | 59.8709 | 59.9213 | 59.7565 | 0.23346 | 62.7548 | -59.7931 | -59.9533 | 62.8601 | 62.8326 | 62.7548 | 0.077819 | 0 | -0.022888 | -0.050354 | -0.004577 | 122.7722 | 63.0844 | 122.6074 | 63.1073 | 122.6303 | 0.10528 | 0.01831 | 122.7951 | 122.7448 | 0.17853 | 122.699 | 62.9333 | 122.6761 | -59.9716 | -122.7493 | 62.7731 | 122.7219 | 62.8418 | 63.3133
1837.9062 | 122.9507 | -62.8326 | 59.8663 | -0.052796 | 0.00091214 | -0.0096323 | 2.8922 | -0.0018799 | -0.00056396 | -0.0054623 | -0.030792 | 0.16267 | 0.12901 | -0.016184 | 0.054756 | 0.10393 | 0.0015551 | -0.036621 | 0.022888 | -0.07782 | -0.073242 | 0.032043 | -0.073242 | 0 | 0.46692 | 59.7748 | -62.8418 | 59.8526 | 60.0128 | 59.8068 | 0.26093 | 62.7548 | -59.8434 | -59.9396 | 62.8647 | 62.8326 | 62.7594 | 0.07782 | 0.004578 | -0.009155 | -0.091553 | -0.013733 | 122.8455 | 63.0936 | 122.6395 | 63.1027 | 122.6486 | 0.10986 | 0.004578 | 122.8546 | 122.6944 | 0.10071 | 122.6166 | 62.8555 | 122.6074 | -59.9442 | -122.7081 | 62.7594 | 122.6852 | 62.796 | 63.2996
1838.8281 | 122.8729 | -62.8922 | 59.8846 | -0.060425 | 0.00048494 | -0.0089913 | 2.8962 | 0.00025629 | 0.001145 | -0.0024717 | -0.14676 | 0.16459 | 0.1273 | -0.00058965 | 0.055183 | 0.105 | -0.0035719 | -0.068665 | 0.054932 | -0.11444 | -0.12817 | -0.07782 | -0.16479 | -0.07782 | 0.39825 | 59.8206 | -62.883 | 59.7977 | 59.8846 | 59.6878 | 0.16479 | 62.7777 | -59.8297 | -60.0128 | 62.8143 | 62.8143 | 62.7274 | 0.036621 | -0.050354 | 0.009155 | -0.064087 | -0.086976 | 122.7768 | 63.0569 | 122.58 | 63.0478 | 122.5708 | 0.036621 | -0.013733 | 122.7676 | 122.6807 | 0.16937 | 122.7036 | 62.9471 | 122.7127 | -59.9991 | -122.7676 | 62.764 | 122.6898 | 62.8235 | 63.2904
1839.8906 | 122.9233 | -62.8143 | 59.9258 | 0.00824 | -0.0029331 | -0.0077097 | 2.895 | 0.0023925 | 0.00050424 | -0.0020443 | -0.10403 | 0.16437 | 0.12986 | -0.0033666 | 0.056038 | 0.10415 | -0.0035719 | 0.032043 | 0.11444 | -0.054932 | -0.036621 | 0.082397 | -0.004578 | 0.013733 | 0.5722 | 59.8297 | -62.8601 | 59.8801 | 59.9762 | 59.8022 | 0.32044 | 62.7594 | -59.8114 | -59.9625 | 62.8967 | 62.8281 | 62.8098 | 0.068665 | 0.050354 | -0.045776 | -0.09613 | -0.045776 | 122.7905 | 63.1348 | 122.6166 | 63.1805 | 122.6624 | 0.13733 | 0.018311 | 122.8363 | 122.7402 | 0.16937 | 122.6898 | 62.9288 | 122.644 | -59.9808 | -122.7859 | 62.7777 | 122.6944 | 62.8464 | 63.3865
1840.8281 | 122.9187 | -62.8418 | 59.8755 | -0.052796 | -0.0029331 | -0.0072825 | 2.896 | 0.0017517 | -0.0012048 | -0.0024717 | -0.091827 | 0.16331 | 0.12452 | 0.00026495 | 0.056678 | 0.105 | 0.00070073 | -0.018311 | 0.068665 | -0.073242 | -0.086975 | 0.027466 | -0.07782 | -0.032043 | 0.48065 | 59.8114 | -62.8464 | 59.8663 | 59.9121 | 59.7244 | 0.23804 | 62.7686 | -59.8068 | -59.9625 | 62.8693 | 62.8098 | 62.764 | 0.041199 | -0.004578 | -0.004578 | -0.064087 | -0.009155 | 122.7539 | 63.0798 | 122.5662 | 63.0844 | 122.5708 | 0.10071 | -0.013733 | 122.7585 | 122.7127 | 0.14191 | 122.6578 | 62.9105 | 122.6532 | -59.9487 | -122.7219 | 62.7548 | 122.7081 | 62.8235 | 63.3224
1841.8906 | 122.9004 | -62.8464 | 59.8938 | -0.029907 | -0.0018649 | -0.0072825 | 2.8958 | -0.00038451 | -0.00077756 | -0.0020443 | -0.11624 | 0.16437 | 0.12666 | -0.0069982 | 0.054969 | 0.10735 | -0.00079467 | -0.022888 | 0.073242 | -0.09613 | -0.10529 | -0.013733 | -0.1236 | -0.054932 | 0.43945 | 59.8297 | -62.8647 | 59.8526 | 59.9167 | 59.7336 | 0.2243 | 62.7502 | -59.8206 | -59.9991 | 62.8326 | 62.7914 | 62.7228 | 0.041198 | -0.027466 | -0.01831 | -0.064087 | -0.041199 | 122.7631 | 63.0707 | 122.58 | 63.089 | 122.5983 | 0.082397 | -0.009156 | 122.7814 | 122.7173 | 0.16937 | 122.6944 | 62.9196 | 122.6761 | -59.9899 | -122.7585 | 62.7411 | 122.699 | 62.8235 | 63.2858
1842.8281 | 123.0286 | -62.8326 | 59.8572 | -0.083313 | -0.0042149 | -0.0074961 | 2.893 | 0.0026063 | 0.0032812 | -0.0024717 | -0.027741 | 0.16395 | 0.12666 | -0.0040076 | 0.056038 | 0.1035 | -0.0035719 | -0.036621 | -0.018311 | -0.12817 | -0.39825 | 0.21515 | 0.21057 | -0.013733 | 0.48981 | 59.7977 | -62.8647 | 59.9213 | 60.0082 | 59.8526 | 0.25177 | 62.7045 | -59.8755 | -60.2554 | 63.0478 | 62.8189 | 63.0432 | 0.11444 | 0.33875 | -0.032043 | -0.05951 | 0.064087 | 122.8409 | 63.0844 | 122.6852 | 63.1165 | 122.7173 | 0.34332 | -0.27008 | 122.8729 | 122.7859 | 0.10986 | 122.6624 | 62.8143 | 122.6303 | -59.9854 | -122.7219 | 62.4344 | 122.7539 | 62.796 | 63.3224
1843.9062 | 122.9782 | -62.851 | 59.8434 | -0.052796 | -0.0020785 | -0.0081369 | 2.8943 | 0.0034607 | -0.00013676 | -0.0033261 | -0.085724 | 0.16395 | 0.12559 | -0.003794 | 0.055824 | 0.10457 | -0.0012219 | -0.10071 | 0.009155 | -0.16479 | -0.15106 | -0.045776 | -0.15106 | -0.10071 | 0.41657 | 59.8114 | -62.8693 | 59.9121 | 59.9579 | 59.7839 | 0.21515 | 62.6862 | -59.8343 | -59.9945 | 62.8052 | 62.7502 | 62.6999 | 0.064087 | 0.013733 | -0.018311 | -0.032044 | 0.068664 | 122.8088 | 63.0661 | 122.6349 | 63.0844 | 122.6532 | 0.11902 | 0.013733 | 122.8271 | 122.7814 | 0.17395 | 122.6807 | 62.8601 | 122.6624 | -60.0082 | -122.7127 | 62.6999 | 122.7631 | 62.7502 | 63.2675
1844.8281 | 123.0011 | -62.8235 | 59.8114 | -0.075684 | -0.0020785 | -0.0079233 | 2.8947 | 0.0038879 | -0.0014184 | -0.0016171 | -0.085724 | 0.16544 | 0.1273 | -0.0035802 | 0.056892 | 0.10521 | -0.0014355 | -0.09613 | -0.018311 | -0.13275 | -0.086975 | 0.041199 | -0.17395 | -0.1236 | 0.46692 | 59.7931 | -62.8601 | 59.9442 | 60.0311 | 59.8206 | 0.25177 | 62.6907 | -59.8297 | -59.8984 | 62.8647 | 62.6999 | 62.6495 | 0.009155 | -0.041199 | -0.036621 | -0.01831 | 0.13275 | 122.8546 | 63.0753 | 122.644 | 63.1119 | 122.6807 | 0.17395 | 0.045776 | 122.8912 | 122.8043 | 0.11444 | 122.6532 | 62.8052 | 122.6166 | -59.9442 | -122.6715 | 62.7365 | 122.7676 | 62.7274 | 63.2904
1845.8906 | 122.9004 | -62.8281 | 59.8755 | 0.00824 | -0.0010105 | -0.0087777 | 2.8937 | 0.00089729 | -0.00056396 | -0.0041807 | -0.1315 | 0.16288 | 0.12687 | 0.0015466 | 0.055824 | 0.10457 | 0.00048713 | -0.018311 | 0.082397 | -0.091553 | -0.086975 | 0 | -0.10529 | -0.068665 | 0.46234 | 59.8343 | -62.8784 | 59.8572 | 59.9167 | 59.7519 | 0.2243 | 62.7365 | -59.7931 | -59.9625 | 62.8281 | 62.7594 | 62.7228 | 0.022888 | -0.013733 | -0.050354 | -0.041198 | -0.01831 | 122.7448 | 63.0524 | 122.58 | 63.1027 | 122.6303 | 0.091553 | 0.004578 | 122.7951 | 122.7356 | 0.17395 | 122.7127 | 62.9105 | 122.6624 | -59.967 | -122.7539 | 62.7411 | 122.6852 | 62.8098 | 63.2904
1846.8281 | 122.8363 | -62.8555 | 59.8755 | -0.037537 | -0.0012241 | -0.0070687 | 2.8935 | -0.0016663 | 0.00029044 | -0.00033547 | -0.12234 | 0.16202 | 0.1273 | -0.0033666 | 0.054756 | 0.10585 | -0.0039991 | -0.1236 | 0.041199 | -0.15564 | -0.16479 | -0.09613 | -0.19226 | -0.1236 | 0.36621 | 59.8343 | -62.8922 | 59.729 | 59.6695 | 60.0403 | 0.36621 | 62.6999 | -59.8343 | -60.0403 | 62.7594 | 62.7319 | 62.6633 | 0.032044 | -0.036621 | -0.036621 | -0.041198 | -0.14648 | 122.525 | 63.2217 | 122.8958 | 63.2584 | 122.9324 | 0.05951 | -0.009155 | 122.5616 | 122.6212 | 0.19684 | 122.7264 | 62.8967 | 122.6898 | -60.0311 | -122.7676 | 62.6907 | 122.5845 | 62.7319 | 63.2217
1847.8281 | 122.9279 | -62.8372 | 59.848 | -0.098572 | -0.0025059 | -0.0087777 | 2.8958 | 0.00089729 | -0.00077756 | -0.0018307 | -0.10403 | 0.16331 | 0.12773 | 0.00026495 | 0.056038 | 0.10308 | -0.0018629 | -0.091553 | 0.045776 | -0.12817 | -0.16022 | -0.07782 | -0.16479 | -0.11902 | 0.39368 | 59.7977 | -62.9013 | 59.8755 | 59.9304 | 59.7565 | 0.1831 | 62.709 | -59.8022 | -60.0082 | 62.7594 | 62.7182 | 62.6724 | 0.009155 | -0.036621 | -0.064087 | -0.050354 | 0.027466 | 122.7676 | 63.0203 | 122.5937 | 63.0844 | 122.6578 | 0.050354 | -0.032043 | 122.8317 | 122.7768 | 0.17395 | 122.699 | 62.883 | 122.6349 | -59.9762 | -122.7493 | 62.677 | 122.7127 | 62.7457 | 63.2309
1848.9062 | 122.9645 | -62.8464 | 59.848 | -0.045166 | -0.00036966 | -0.0081369 | 2.8954 | -0.0018799 | -0.00056396 | 0.00051913 | -0.10098 | 0.16373 | 0.12944 | -0.011912 | 0.056465 | 0.10479 | -0.0033581 | -0.11444 | 0.022888 | -0.16022 | -0.16022 | -0.054932 | -0.16937 | -0.10071 | 0.39825 | 59.7839 | -62.8922 | 59.8801 | 59.935 | 59.7519 | 0.18768 | 62.6862 | -59.8251 | -60.0082 | 62.7914 | 62.7457 | 62.677 | 0.059509 | -0.009156 | -0.045776 | -0.064086 | 0.032044 | 122.7814 | 63.0341 | 122.5983 | 63.0798 | 122.644 | 0.10528 | 0 | 122.8271 | 122.7722 | 0.1831 | 122.6761 | 62.8693 | 122.6303 | -60.0082 | -122.7402 | 62.6862 | 122.7264 | 62.7319 | 63.2446
1849.8281 | 122.9874 | -62.8098 | 59.8389 | -0.098572 | -0.0010105 | -0.0089913 | 2.8945 | -0.0018799 | -0.0020594 | -0.0043943 | -0.049103 | 0.16245 | 0.1288 | -0.002085 | 0.058387 | 0.10222 | -0.0031445 | -0.050354 | 0.004578 | -0.09613 | -0.073242 | 0.041199 | -0.059509 | -0.009155 | 0.50354 | 59.7702 | -62.8601 | 59.9258 | 59.9945 | 59.8251 | 0.24719 | 62.7136 | -59.8343 | -59.9121 | 62.851 | 62.8006 | 62.7502 | 0.086975 | 0.036621 | -0.050354 | -0.068664 | 0.086975 | 122.8043 | 63.0569 | 122.6349 | 63.1073 | 122.6852 | 0.13733 | 0.022888 | 122.8546 | 122.7859 | 0.10071 | 122.6303 | 62.8143 | 122.58 | -59.935 | -122.699 | 62.7365 | 122.7356 | 62.7594 | 63.3133
1850.8906 | 122.9691 | -62.8143 | 59.8343 | -0.12909 | -0.0025059 | -0.0066415 | 2.8941 | 0.0081605 | -0.0012048 | -0.0028989 | -0.076569 | 0.16352 | 0.12645 | -0.0010168 | 0.056038 | 0.10457 | -0.0010083 | -0.082397 | -0.045776 | -0.12817 | -0.050354 | 0.036621 | -0.073242 | -0.018311 | 0.49439 | 59.7656 | -62.883 | 59.8846 | 59.8618 | 60.1089 | 0.38452 | 62.6862 | -59.8801 | -59.8846 | 62.851 | 62.796 | 62.7411 | 0.10986 | 0.054932 | -0.068665 | -0.068665 | 0.050354 | 122.6761 | 63.1989 | 122.9233 | 63.2675 | 122.9919 | 0.1648 | 0.07782 | 122.7448 | 122.7676 | 0.082398 | 122.6486 | 62.7686 | 122.58 | -59.9625 | -122.7173 | 62.764 | 122.699 | 62.7319 | 63.3087
1851.8281 | 122.9828 | -62.8555 | 59.8434 | -0.075684 | 0.00069854 | -0.0070687 | 2.8935 | 0.0038879 | 0.00050424 | -0.0031125 | -0.073517 | 0.16309 | 0.12773 | -0.004862 | 0.054115 | 0.10457 | -0.00036747 | -0.050354 | -0.036621 | -0.13275 | -0.054932 | 0.032043 | -0.10071 | -0.009155 | 0.50354 | 59.7702 | -62.8693 | 59.9533 | 60.022 | 59.6512 | 0.050354 | 62.7228 | -59.8801 | -59.8984 | 62.8876 | 62.8464 | 62.7548 | 0.1236 | 0.032043 | -0.013733 | -0.073242 | 0.10986 | 122.8775 | 62.9059 | 122.5067 | 62.9196 | 122.5204 | 0.16479 | 0.077819 | 122.8912 | 122.8226 | 0.09613 | 122.6395 | 62.8189 | 122.6257 | -59.9762 | -122.7127 | 62.8006 | 122.8088 | 62.8052 | 63.3591
1852.9062 | 122.9233 | -62.8464 | 59.8892 | 0.054016 | -0.0016513 | -0.010487 | 2.8952 | -0.0020935 | -0.0014184 | -0.0024717 | -0.10403 | 0.16331 | 0.1288 | -0.0033666 | 0.058387 | 0.105 | -0.0010083 | -0.10529 | 0.16479 | -0.009155 | -0.054932 | 0.009155 | -0.009155 | 0.009155 | 0.50812 | 59.8526 | -62.8693 | 59.8663 | 59.9487 | 59.7656 | 0.30212 | 62.8372 | -59.7244 | -59.9442 | 62.8555 | 62.8555 | 62.8372 | 0.01831 | 0 | -0.022888 | -0.036621 | -0.022888 | 122.7951 | 63.1485 | 122.612 | 63.1714 | 122.6349 | 0.01831 | -0.045777 | 122.818 | 122.7356 | 0.17395 | 122.7219 | 63.0112 | 122.699 | -59.8984 | -122.7585 | 62.7914 | 122.7127 | 62.7411 | 63.3545
1853.8281 | 123.0011 | -62.8281 | 59.8343 | 0.038757 | -0.0020785 | -0.0077097 | 2.8943 | -0.0029479 | -0.0020594 | -0.0026853 | -0.082672 | 0.16224 | 0.12773 | -0.0057166 | 0.056465 | 0.1035 | -0.0025037 | -0.13733 | -0.050354 | -0.14191 | -0.068665 | 0.041199 | -0.045776 | -0.009155 | 0.52643 | 59.7885 | -62.8326 | 59.9396 | 60.0037 | 59.848 | 0.26093 | 62.6862 | -59.8846 | -59.903 | 62.8693 | 62.8189 | 62.7823 | 0.13275 | 0.096131 | -0.004578 | -0.045777 | 0.10528 | 122.8317 | 63.089 | 122.6761 | 63.0936 | 122.6807 | 0.18311 | 0.073242 | 122.8363 | 122.7722 | 0.091553 | 122.6212 | 62.7777 | 122.6166 | -59.9762 | -122.6669 | 62.7594 | 122.7676 | 62.6907 | 63.3545
1854.8906 | 122.8821 | -62.8738 | 59.8618 | -0.014649 | -0.00079686 | -0.0089913 | 2.895 | 0.00068369 | -0.0031274 | 0.0015871 | -0.16507 | 0.16437 | 0.12965 | -0.0012304 | 0.05561 | 0.10436 | -0.0033581 | -0.10071 | 0.054932 | -0.14648 | -0.19684 | -0.1236 | -0.19684 | -0.1236 | 0.37079 | 59.8526 | -62.8738 | 59.8434 | 59.8938 | 59.7015 | 0.16937 | 62.7274 | -59.8068 | -60.0586 | 62.7502 | 62.7502 | 62.677 | 0.022888 | -0.050354 | 0 | -0.009155 | -0.01831 | 122.7676 | 63.0432 | 122.5754 | 63.0432 | 122.5754 | 0.022888 | -0.050354 | 122.7676 | 122.7173 | 0.20142 | 122.7264 | 62.9288 | 122.7264 | -60.0082 | -122.7356 | 62.677 | 122.7173 | 62.7731 | 63.2446
1855.8281 | 122.9919 | -62.8189 | 59.816 | -0.045166 | 0.00027134 | -0.0068551 | 2.8937 | 0.0032471 | -0.00077756 | -0.0024717 | -0.085724 | 0.16245 | 0.12452 | 0.0017602 | 0.056892 | 0.10457 | -0.0018629 | -0.073242 | -0.027466 | -0.13733 | -0.073242 | 0.022888 | -0.091553 | -0.032043 | 0.47607 | 59.7748 | -62.8601 | 59.9487 | 60.0128 | 59.8572 | 0.25177 | 62.6816 | -59.8434 | -59.8892 | 62.8418 | 62.7869 | 62.7274 | 0.10529 | 0.045776 | -0.041198 | -0.041199 | 0.13275 | 122.8317 | 63.0707 | 122.6761 | 63.1119 | 122.7173 | 0.16022 | 0.064087 | 122.8729 | 122.8088 | 0.10986 | 122.6349 | 62.7914 | 122.5937 | -59.9533 | -122.6761 | 62.7457 | 122.7676 | 62.7457 | 63.295
1856.8906 | 122.9279 | -62.8372 | 59.8892 | -0.022278 | -0.0020785 | -0.0083505 | 2.8943 | 0.0026063 | 0.00050424 | -0.0014035 | -0.1254 | 0.16224 | 0.12687 | -0.00016245 | 0.057319 | 0.10564 | -0.0029309 | 0.018311 | 0.11444 | -0.059509 | -0.032043 | 0.054932 | 0.009155 | 0.032043 | 0.55847 | 59.848 | -62.851 | 59.9213 | 59.9762 | 59.7977 | 0.31586 | 62.7777 | -59.7748 | -59.9213 | 62.8922 | 62.8693 | 62.8464 | 0.091552 | 0.068664 | -0.013733 | -0.041199 | 0.032044 | 122.8134 | 63.1531 | 122.6349 | 63.1668 | 122.6486 | 0.11444 | 0.027466 | 122.8271 | 122.7722 | 0.17395 | 122.699 | 62.9517 | 122.6852 | -59.9487 | -122.7402 | 62.8052 | 122.7585 | 62.8555 | 63.3957
1857.8438 | 122.9874 | -62.8006 | 59.8618 | -0.037537 | -0.0010105 | -0.0098459 | 2.8928 | 0.0013245 | -0.0014184 | -0.0022581 | -0.042999 | 0.16373 | 0.12815 | -0.0022986 | 0.056038 | 0.10308 | -0.0018629 | -0.032043 | 0.045776 | -0.082397 | -0.07782 | 0.022888 | -0.050354 | 0.032043 | 0.48981 | 59.8114 | -62.8555 | 59.9167 | 60.0128 | 59.8343 | 0.28839 | 62.7182 | -59.816 | -59.9396 | 62.8235 | 62.8326 | 62.7502 | 0.11444 | 0.032043 | -0.054932 | -0.050354 | 0.054932 | 122.8134 | 63.089 | 122.6349 | 63.1439 | 122.6898 | 0.10528 | 0.004577 | 122.8683 | 122.7722 | 0.12817 | 122.6669 | 62.8464 | 122.612 | -59.9442 | -122.7173 | 62.7228 | 122.7173 | 62.7686 | 63.2904
1858.8906 | 122.8821 | -62.8647 | 59.8663 | -0.052796 | -0.0014377 | -0.0079233 | 2.8954 | -0.0016663 | 0.00029044 | -0.00054907 | -0.14981 | 0.16331 | 0.12602 | -0.00016245 | 0.054329 | 0.10479 | -0.0010083 | -0.064087 | 0.045776 | -0.13733 | -0.13275 | -0.059509 | -0.14191 | -0.09613 | 0.37994 | 59.8526 | -62.8647 | 59.8389 | 59.8984 | 59.7015 | 0.18768 | 62.7274 | -59.8206 | -59.9991 | 62.8052 | 62.7686 | 62.7228 | 0.041199 | -0.004578 | 0 | -0.013733 | -0.027466 | 122.7631 | 63.0524 | 122.5662 | 63.0524 | 122.5662 | 0.07782 | 0.004578 | 122.7631 | 122.7036 | 0.18311 | 122.7173 | 62.9105 | 122.7173 | -60.0037 | -122.731 | 62.7319 | 122.7036 | 62.8006 | 63.2446
1859.8281 | 122.9828 | -62.8464 | 59.8251 | -0.029907 | -0.0020785 | -0.0107 | 2.8933 | 4.2692e-05 | -0.0016322 | -0.00054907 | -0.10403 | 0.16224 | 0.1288 | 0.0068872 | 0.05796 | 0.10521 | -0.0010083 | -0.10986 | -0.013733 | -0.16022 | -0.12817 | -0.032043 | -0.13733 | -0.073242 | 0.45319 | 59.7931 | -62.8647 | 59.9396 | 59.9716 | 59.7794 | 0.21973 | 62.6862 | -59.8389 | -59.9533 | 62.8143 | 62.7731 | 62.709 | 0.086975 | 0.022888 | -0.01831 | -0.032043 | 0.11444 | 122.818 | 63.0661 | 122.6257 | 63.0844 | 122.644 | 0.12817 | 0.032043 | 122.8363 | 122.8043 | 0.14648 | 122.6578 | 62.8326 | 122.6395 | -59.9854 | -122.6898 | 62.7182 | 122.7859 | 62.7365 | 63.2996
1860.8906 | 122.9141 | -62.8464 | 59.8251 | -0.022278 | -0.0033603 | -0.0092051 | 2.8965 | 0.00089729 | -0.00099116 | -0.0046079 | -0.13455 | 0.16267 | 0.12773 | -0.0052892 | 0.056038 | 0.10393 | 0.0032641 | -0.004578 | 0.041199 | -0.14191 | -0.16479 | -0.091553 | -0.1831 | -0.09613 | 0.37537 | 59.8251 | -62.915 | 59.8618 | 59.9213 | 59.7473 | 0.1831 | 62.7045 | -59.7839 | -59.9899 | 62.7548 | 62.7502 | 62.6633 | 0.045777 | -0.041198 | -0.068664 | 0 | 0.036621 | 122.7676 | 63.0295 | 122.5937 | 63.0981 | 122.6624 | 0.050354 | -0.022888 | 122.8363 | 122.7768 | 0.18311 | 122.7402 | 62.8876 | 122.6715 | -59.967 | -122.7402 | 62.6816 | 122.7081 | 62.8418 | 63.2217
1861.8281 | 122.8958 | -62.8738 | 59.8801 | -0.014649 | 0.00069854 | -0.0068551 | 2.8954 | -0.0012391 | 0.0013586 | -0.00076267 | 0.0027771 | 0.16288 | 0.12815 | -0.00058965 | 0.057533 | 0.10607 | -0.0016493 | -0.10529 | 0.018311 | -0.14648 | -0.17853 | -0.11444 | -0.57678 | -0.54016 | 0.29755 | 59.8343 | -62.8876 | 59.8526 | 59.8846 | 59.7244 | 0.18768 | 62.7274 | -59.8618 | -60.0586 | 62.7594 | 62.3337 | 62.2971 | -0.39368 | -0.4303 | -0.013733 | -0.045776 | -0.027466 | 122.7585 | 63.0615 | 122.5983 | 63.0753 | 122.612 | 0.032043 | -0.032044 | 122.7722 | 122.7402 | 0.16479 | 122.7219 | 62.8922 | 122.7081 | -60.0266 | -122.7676 | 62.6953 | 122.7264 | 62.7686 | 63.1714
1862.8906 | 122.905 | -62.8601 | 59.8755 | 0.023498 | -0.0016513 | -0.0089913 | 2.8952 | 0.0030335 | -0.0027002 | -0.0022581 | -0.12234 | 0.16245 | 0.12815 | -0.0033666 | 0.055183 | 0.10607 | 0.0024097 | -0.032043 | 0.073242 | -0.10071 | -0.086975 | 0 | -0.10986 | -0.059509 | 0.46234 | 59.8434 | -62.8922 | 59.8618 | 59.9075 | 59.7382 | 0.21057 | 62.7594 | -59.8022 | -59.9625 | 62.8601 | 62.8006 | 62.7502 | 0.041199 | -0.009155 | -0.032044 | -0.032043 | -0.013733 | 122.7676 | 63.0707 | 122.5983 | 63.1027 | 122.6303 | 0.10071 | 0.013733 | 122.7997 | 122.7539 | 0.17395 | 122.7356 | 62.9333 | 122.7036 | -59.9762 | -122.7676 | 62.7731 | 122.7219 | 62.8281 | 63.3224
1863.8281 | 123.0286 | -62.8464 | 59.8297 | -0.045166 | -0.00079686 | -0.010487 | 2.8952 | 4.2692e-05 | -0.00056396 | -0.0020443 | -0.10403 | 0.16309 | 0.1273 | -0.0061438 | 0.058601 | 0.10521 | -0.0039991 | -0.10986 | 0.013733 | -0.14648 | -0.1236 | -0.022888 | -0.11444 | -0.054932 | 0.49439 | 59.7885 | -62.8784 | 59.9304 | 60.0128 | 59.816 | 0.25177 | 62.6999 | -59.816 | -59.9533 | 62.8235 | 62.7914 | 62.7319 | 0.091552 | 0.032043 | -0.032043 | -0.041199 | 0.10071 | 122.8592 | 63.0981 | 122.6624 | 63.1302 | 122.6944 | 0.1236 | 0.022888 | 122.8912 | 122.8088 | 0.16022 | 122.6669 | 62.8601 | 122.6349 | -59.9762 | -122.7081 | 62.7228 | 122.7768 | 62.7365 | 63.3408
1864.8906 | 122.8821 | -62.8601 | 59.903 | -0.022278 | -0.0012241 | -0.0098459 | 2.893 | 0.00025629 | 0.00029044 | -0.0031125 | -0.097931 | 0.16138 | 0.12538 | -0.0033666 | 0.056678 | 0.105 | 0.0024097 | 0.48523 | 0.19226 | 0.013733 | -0.1236 | 0.036621 | -0.082397 | -0.013733 | 0.48523 | 59.8389 | -62.8647 | 59.8572 | 59.9579 | 59.7656 | 0.32501 | 62.8738 | -59.7107 | -60.0266 | 62.8967 | 62.8464 | 62.7777 | -0.027466 | -0.09613 | -0.004578 | -0.064087 | -0.045776 | 122.818 | 63.1851 | 122.6257 | 63.1897 | 122.6303 | 0.022888 | -0.13733 | 122.8226 | 122.7219 | 0.17853 | 122.7036 | 63.0524 | 122.699 | -59.8892 | -122.7676 | 62.7365 | 122.7173 | 63.3453 | 63.3453
1865.8281 | 123.0194 | -62.8372 | 59.8297 | -0.068054 | 0.0019803 | -0.0066415 | 2.8952 | 0.00025629 | -0.00013676 | -0.0016171 | -0.06131 | 0.16202 | 0.12623 | -0.0061438 | 0.057106 | 0.10479 | 0.00027333 | 0.15564 | -0.068665 | -0.16022 | -0.009155 | 0.050354 | -0.082397 | 0.004578 | 0.52185 | 59.7565 | -62.8738 | 59.9442 | 60.0174 | 59.8343 | 0.23804 | 62.677 | -59.8984 | -59.8389 | 62.8876 | 62.8418 | 62.7548 | 0.16479 | 0.07782 | -0.036621 | -0.073242 | 0.11444 | 122.8546 | 63.0753 | 122.6715 | 63.1119 | 122.7081 | 0.21057 | 0.15106 | 122.8912 | 122.818 | 0.091552 | 122.6303 | 62.7686 | 122.5937 | -59.9899 | -122.7036 | 62.8281 | 122.7814 | 62.9929 | 63.3591
1866.8906 | 122.8867 | -62.8784 | 59.8709 | -0.068054 | -0.0012241 | -0.0089913 | 2.896 | 0.0060241 | 0.00029044 | -0.00054907 | -0.1315 | 0.16523 | 0.12709 | -0.0012304 | 0.056038 | 0.10479 | 0.0011279 | -0.11444 | 0.054932 | -0.1236 | -0.16479 | -0.086975 | -0.19226 | -0.13733 | 0.35706 | 59.8389 | -62.8876 | 59.848 | 59.8892 | 59.6924 | 0.19226 | 62.7548 | -59.816 | -60.0357 | 62.7914 | 62.7411 | 62.6862 | -0.013733 | -0.068665 | -0.009155 | -0.032044 | -0.022889 | 122.7676 | 63.0707 | 122.5708 | 63.0798 | 122.58 | 0.036621 | -0.041199 | 122.7768 | 122.7356 | 0.17853 | 122.7264 | 62.9334 | 122.7173 | -59.9945 | -122.7585 | 62.7136 | 122.7264 | 62.764 | 63.2355
1867.8438 | 122.9919 | -62.8189 | 59.8572 | -0.022278 | -0.0020785 | -0.0083505 | 2.892 | -0.0055115 | 0.0024268 | 0.0013735 | -0.027741 | 0.16224 | 0.1273 | -0.0061438 | 0.057319 | 0.10158 | 0.0013415 | -0.073242 | 0.045776 | -0.07782 | -0.073242 | 0.050354 | -0.041199 | -0.004578 | 0.48523 | 59.8022 | -62.8418 | 59.9213 | 59.9945 | 59.8389 | 0.29755 | 62.7411 | -59.8114 | -59.9304 | 62.8693 | 62.8143 | 62.7777 | 0.073242 | 0.036621 | -0.022888 | -0.054932 | 0.064087 | 122.8134 | 63.1165 | 122.6578 | 63.1393 | 122.6807 | 0.12817 | 0.004578 | 122.8363 | 122.7631 | 0.1236 | 122.644 | 62.8647 | 122.6212 | -59.935 | -122.699 | 62.7457 | 122.7402 | 62.7457 | 63.3041
1868.8906 | 122.9187 | -62.8464 | 59.8938 | -0.022278 | -0.00079686 | -0.0049325 | 2.8937 | 0.0026063 | -0.0037684 | -0.00054907 | -0.14981 | 0.16694 | 0.13029 | -0.0029394 | 0.055397 | 0.105 | -0.0027173 | -0.11444 | 0.036621 | -0.16022 | -0.17395 | -0.10071 | -0.20142 | -0.1236 | 0.086975 | 59.7794 | -62.915 | 59.8434 | 59.8755 | 59.761 | 0.19684 | 62.6862 | -59.8572 | -60.0677 | 62.7457 | 62.7228 | 62.645 | 0.036621 | -0.041199 | -0.068664 | -0.11444 | -0.050354 | 122.7219 | 63.0432 | 122.6074 | 63.1119 | 122.6761 | 0.059509 | -0.013733 | 122.7905 | 122.7585 | 0.19684 | 122.6944 | 62.883 | 122.6257 | -60.054 | -122.8088 | 62.6724 | 122.6898 | 62.7319 | 62.9334
1869.8281 | 123.0331 | -62.8372 | 59.848 | 0.038757 | -0.0018649 | -0.0077097 | 2.8973 | 0.0026063 | -0.0012048 | -0.0020443 | -0.10709 | 0.16459 | 0.12837 | -0.0046484 | 0.056465 | 0.10308 | 0.0015551 | -0.10529 | 0 | -0.15106 | -0.13275 | -0.022888 | -0.12817 | -0.073242 | 0.44861 | 59.7839 | -62.883 | 59.9579 | 59.9625 | 59.7656 | 0.20599 | 62.6862 | -59.848 | -59.9808 | 62.8143 | 62.764 | 62.709 | 0.07782 | 0.022888 | -0.045777 | -0.064086 | 0.10986 | 122.7997 | 63.0432 | 122.6028 | 63.089 | 122.6486 | 0.12817 | 0.018311 | 122.8455 | 122.8409 | 0.15106 | 122.6669 | 62.8372 | 122.6212 | -59.9991 | -122.731 | 62.7045 | 122.7951 | 62.7319 | 63.2858
1870.8906 | 122.8134 | -62.8784 | 59.8297 | -0.022278 | 0.0015529 | -0.0098459 | 2.8962 | 0.0019653 | 0.00071784 | -0.0024717 | -0.14981 | 0.16395 | 0.1273 | 5.1352e-05 | 0.056251 | 0.10329 | -0.0067761 | -0.10071 | 0.027466 | -0.15106 | -0.16022 | -0.11444 | -0.18768 | -0.11902 | 0.37079 | 59.8114 | -62.8784 | 59.8434 | 59.8755 | 59.6695 | 0.22888 | 62.7274 | -59.8022 | -59.9899 | 62.764 | 62.7594 | 62.6907 | 0.032043 | -0.036621 | 0 | -0.018311 | 0.013733 | 122.7539 | 63.1073 | 122.5479 | 63.1073 | 122.5479 | 0.036621 | -0.009155 | 122.7539 | 122.7219 | 0.17853 | 122.6898 | 62.9059 | 122.6898 | -59.9808 | -122.7081 | 62.7182 | 122.7219 | 62.7777 | 63.2492
1871.8438 | 122.8912 | -62.8326 | 59.8663 | -0.029907 | -0.0010105 | -0.0068551 | 2.895 | -0.0012391 | 0.0030676 | -0.0031125 | -0.039948 | 0.16352 | 0.1273 | -0.0033666 | 0.059028 | 0.10265 | -0.0020765 | -0.059509 | 0.009155 | -0.086975 | -0.082397 | 0.013733 | -0.064087 | 0.004578 | 0.45776 | 59.8022 | -62.8464 | 59.8984 | 59.9991 | 59.816 | 0.27008 | 62.7457 | -59.8572 | -59.9487 | 62.8464 | 62.8372 | 62.7686 | 0.091553 | 0.022888 | -0.013733 | -0.064087 | 0.032043 | 122.8317 | 63.1027 | 122.6486 | 63.1165 | 122.6624 | 0.10071 | 0.004578 | 122.8455 | 122.7448 | 0.09613 | 122.6486 | 62.8418 | 122.6349 | -59.9533 | -122.7127 | 62.7502 | 122.731 | 62.7731 | 63.2904
1872.8906 | 122.9416 | -62.8601 | 59.9121 | -0.022278 | -0.0040013 | -0.010059 | 2.8945 | 0.0011109 | -0.00077756 | 0.0011599 | -0.12234 | 0.16202 | 0.1288 | -0.0069982 | 0.057319 | 0.105 | -0.0029309 | 0.022888 | 0.14191 | -0.064087 | -0.022888 | 0.032043 | -0.022888 | 0.018311 | 0.5127 | 59.8572 | -62.8784 | 59.8801 | 59.9716 | 59.7931 | 0.32501 | 62.796 | -59.7702 | -59.935 | 62.8922 | 62.8784 | 62.8372 | 0.082398 | 0.041199 | -0.018311 | -0.054931 | -0.032043 | 122.8317 | 63.1851 | 122.6532 | 63.2034 | 122.6715 | 0.09613 | 0.041199 | 122.85 | 122.7585 | 0.20599 | 122.7356 | 63.002 | 122.7173 | -59.9762 | -122.7905 | 62.8372 | 122.7402 | 62.883 | 63.3728
1873.8281 | 123.0286 | -62.8189 | 59.8297 | -0.068054 | 0.00027134 | -0.0085641 | 2.8947 | 0.00046989 | -0.002273 | -0.0014035 | -0.15286 | 0.1601 | 0.12559 | -0.0010168 | 0.05796 | 0.10393 | -0.0031445 | -0.050354 | -0.036621 | -0.10986 | -0.054932 | 0.041199 | -0.082397 | -0.064087 | 0.67749 | 59.7931 | -62.851 | 59.967 | 60.0311 | 59.8206 | 0.23804 | 62.709 | -59.8663 | -59.8846 | 62.8601 | 62.7548 | 62.7365 | 0.045776 | 0.027466 | -0.032043 | -0.036621 | 0.13733 | 122.85 | 63.0569 | 122.6395 | 63.089 | 122.6715 | 0.15106 | 0.054931 | 122.8821 | 122.818 | 0.073242 | 122.644 | 62.7823 | 122.612 | -59.9396 | -122.6807 | 62.764 | 122.7859 | 62.7686 | 63.4964
1874.8906 | 122.937 | -62.8464 | 59.8984 | -0.014649 | 0.0013393 | -0.0077097 | 2.896 | 0.0041015 | -0.00099116 | -0.0014035 | -0.15286 | 0.16373 | 0.12623 | 0.0062464 | 0.054969 | 0.10393 | 0.0058275 | 0.013733 | 0.086975 | -0.082397 | -0.022888 | 0.050354 | -0.050354 | 0.004578 | 0.56305 | 59.8297 | -62.8464 | 59.8526 | 59.9625 | 59.8572 | 0.28839 | 62.764 | -59.8114 | -59.9213 | 62.8967 | 62.851 | 62.796 | 0.086975 | 0.032043 | 0 | -0.068664 | -0.045776 | 122.8088 | 63.1348 | 122.7036 | 63.1348 | 122.7036 | 0.13275 | 0.059509 | 122.8088 | 122.699 | 0.16937 | 122.6761 | 62.9334 | 122.6761 | -59.9808 | -122.7448 | 62.8235 | 122.699 | 62.8601 | 63.4094
1875.8281 | 122.9462 | -62.8464 | 59.8709 | 0.023498 | -0.0025059 | -0.0064279 | 2.8965 | -0.00017091 | 0.001145 | -0.00097627 | -0.13455 | 0.16202 | 0.12986 | -0.0044348 | 0.057106 | 0.10521 | -0.0010083 | 0.086975 | -0.022888 | -0.17853 | -0.10986 | -0.09613 | -0.21515 | -0.11902 | 0.39368 | 59.8068 | -62.8922 | 59.8618 | 59.9075 | 59.7244 | 0.1831 | 62.6678 | -59.8938 | -59.9808 | 62.7502 | 62.7274 | 62.6312 | 0.059509 | -0.036621 | -0.045776 | -0.064087 | -0.009156 | 122.7539 | 63.0295 | 122.5708 | 63.0753 | 122.6166 | 0.082398 | 0.068665 | 122.7997 | 122.7539 | 0.15564 | 122.699 | 62.8235 | 122.6532 | -60.0494 | -122.7631 | 62.7365 | 122.7081 | 62.9334 | 63.2401
1876.8438 | 122.9645 | -62.8143 | 59.8618 | -0.068054 | -0.0016513 | -0.0083505 | 2.8935 | -0.0014527 | -0.0018458 | -0.0043943 | -0.067413 | 0.16352 | 0.1273 | -0.0046484 | 0.058601 | 0.10436 | -0.00015387 | -0.064087 | -0.013733 | -0.10529 | -0.073242 | 0.036621 | -0.091553 | -0.022888 | 0.4715 | 59.7656 | -62.8693 | 59.9075 | 59.9808 | 59.8114 | 0.23804 | 62.709 | -59.8755 | -59.935 | 62.851 | 62.7914 | 62.7228 | 0.082398 | 0.013733 | -0.054932 | -0.09613 | 0.045777 | 122.7951 | 63.0524 | 122.6257 | 63.1073 | 122.6807 | 0.14191 | 0.032044 | 122.85 | 122.7768 | 0.091553 | 122.6349 | 62.8006 | 122.58 | -59.967 | -122.731 | 62.7411 | 122.7219 | 62.7502 | 63.2858
1877.8906 | 122.8775 | -62.851 | 59.8572 | -0.075684 | -0.0014377 | -0.0083505 | 2.898 | 0.0015381 | -0.00099116 | 0.0020145 | -0.14066 | 0.16288 | 0.12687 | -0.0027258 | 0.055397 | 0.10628 | -0.0010083 | -0.041199 | 0.059509 | -0.091553 | -0.10529 | -0.027466 | -0.11902 | -0.082397 | 0.45319 | 59.8755 | -62.8784 | 59.8618 | 59.9075 | 59.7107 | 0.21515 | 62.7594 | -59.7977 | -59.9625 | 62.8235 | 62.7686 | 62.7319 | 0.009156 | -0.027466 | -0.027466 | 0.01831 | 0.004577 | 122.7585 | 63.0661 | 122.5616 | 63.0936 | 122.5891 | 0.064087 | -0.013733 | 122.786 | 122.7402 | 0.15106 | 122.7539 | 62.9105 | 122.7264 | -59.9487 | -122.7356 | 62.7457 | 122.7127 | 62.8098 | 63.3041
1878.8281 | 122.9279 | -62.8738 | 59.8572 | -0.014649 | -0.0020785 | -0.0098459 | 2.8982 | 0.0011109 | -0.0014184 | -0.00012167 | -0.26883 | 0.16459 | 0.12645 | -0.0027258 | 0.058387 | 0.10308 | -0.0016493 | -0.11444 | 0.041199 | -0.15106 | -0.16937 | -0.09613 | -0.18768 | -0.12817 | 0.65002 | 59.8251 | -62.8647 | 59.848 | 59.9213 | 59.697 | 0.16479 | 62.7228 | -59.816 | -60.0266 | 62.7777 | 62.7457 | 62.6862 | 0.022888 | -0.036621 | 0.009155 | -0.032044 | -0.009156 | 122.7951 | 63.0386 | 122.5708 | 63.0295 | 122.5616 | 0.054932 | -0.018311 | 122.7859 | 122.7127 | 0.19226 | 122.6898 | 62.915 | 122.699 | -60.0082 | -122.7219 | 62.7045 | 122.7219 | 62.7594 | 63.5239
1879.8906 | 122.9462 | -62.8418 | 59.8663 | -0.037537 | -0.0027195 | -0.0096323 | 2.8943 | -0.0027343 | -0.00077756 | -0.0031125 | -0.11014 | 0.16437 | 0.12623 | -0.0012304 | 0.056678 | 0.10244 | -0.0016493 | 0.013733 | 0.13275 | -0.041199 | -0.041199 | 0.073242 | -0.027466 | 0.009155 | 0.56763 | 59.8526 | -62.8647 | 59.9167 | 59.9762 | 59.8022 | 0.34332 | 62.8006 | -59.7336 | -59.9075 | 62.915 | 62.851 | 62.8143 | 0.050354 | 0.013733 | -0.022888 | -0.013733 | 0.050354 | 122.818 | 63.1851 | 122.644 | 63.208 | 122.6669 | 0.11444 | 0 | 122.8409 | 122.7814 | 0.17395 | 122.7173 | 62.9745 | 122.6944 | -59.9075 | -122.731 | 62.8006 | 122.7585 | 62.8555 | 63.4094
1880.8281 | 122.937 | -62.8693 | 59.848 | 0.054016 | -0.0031467 | -0.0089913 | 2.8962 | 0.00025629 | -0.00077756 | -0.0046079 | -0.10709 | 0.16459 | 0.12858 | -0.0027258 | 0.058601 | 0.10585 | -0.00079467 | -0.14648 | 0.041199 | -0.12817 | -0.17395 | -0.086975 | -0.17395 | -0.11444 | 0.40283 | 59.848 | -62.8967 | 59.8618 | 59.9258 | 59.7427 | 0.1831 | 62.7411 | -59.8068 | -60.022 | 62.7823 | 62.7548 | 62.6953 | 0.013733 | -0.045776 | -0.027466 | 0 | 0.013733 | 122.7951 | 63.0524 | 122.612 | 63.0798 | 122.6395 | 0.041199 | -0.045776 | 122.8226 | 122.7585 | 0.16937 | 122.7448 | 62.9105 | 122.7173 | -59.9762 | -122.7448 | 62.6953 | 122.731 | 62.7228 | 63.2721
1881.9062 | 122.9828 | -62.8326 | 59.8297 | -0.083313 | -0.00036966 | -0.0085641 | 2.895 | 0.00089729 | -0.0012048 | -0.0043943 | -0.058258 | 0.16309 | 0.12773 | -0.0091344 | 0.057533 | 0.1035 | 0.0013415 | -0.059509 | 0.004578 | -0.082397 | -0.068665 | 0.045776 | -0.050354 | -0.027466 | 0.5127 | 59.7748 | -62.8693 | 59.9167 | 59.9945 | 59.8206 | 0.24719 | 62.7502 | -59.8251 | -59.8984 | 62.8784 | 62.8052 | 62.7823 | 0.054931 | 0.032043 | -0.036621 | -0.054932 | 0.086975 | 122.8271 | 63.0798 | 122.6532 | 63.1165 | 122.6898 | 0.12817 | 0.013732 | 122.8638 | 122.7859 | 0.086975 | 122.644 | 62.8372 | 122.6074 | -59.9121 | -122.699 | 62.764 | 122.7493 | 62.7731 | 63.3453
1882.8281 | 123.0057 | -62.8464 | 59.8434 | -0.022278 | -0.0022923 | -0.0040781 | 2.8933 | -0.0010253 | -0.0020594 | -0.0022581 | -0.085724 | 0.1616 | 0.12687 | -0.0018712 | 0.05796 | 0.10479 | -0.0016493 | -0.42114 | -0.073242 | -0.15106 | -0.068665 | 0.054932 | -0.018311 | -0.004578 | 0.52643 | 59.7794 | -62.8601 | 59.9487 | 60.0174 | 59.848 | 0.26093 | 62.6953 | -59.9167 | -59.9121 | 62.9013 | 62.8418 | 62.8281 | 0.14648 | 0.13275 | -0.013732 | -0.064087 | 0.10528 | 122.8638 | 63.1073 | 122.6944 | 63.121 | 122.7081 | 0.20599 | 0.082397 | 122.8775 | 122.8088 | 0.07782 | 122.6395 | 62.7731 | 122.6257 | -59.9945 | -122.7036 | 62.7777 | 122.7951 | 62.4252 | 63.3728
1883.8906 | 122.9233 | -62.8693 | 59.8938 | -0.029907 | -0.0018649 | -0.0092051 | 2.8952 | 0.00089729 | -0.0020594 | -0.0018307 | -0.073517 | 0.16523 | 0.12837 | 0.00090575 | 0.05561 | 0.10521 | -0.00079467 | -0.004578 | 0.073242 | -0.073242 | -0.054932 | 0.045776 | -0.21515 | -0.19226 | 0.51727 | 59.8389 | -62.8693 | 59.8984 | 59.9533 | 59.7839 | 0.29297 | 62.796 | -59.8206 | -59.9487 | 62.915 | 62.677 | 62.6541 | -0.11902 | -0.14191 | 0 | -0.054932 | 0.004577 | 122.8226 | 63.1622 | 122.6532 | 63.1622 | 122.6532 | 0.11902 | 0.01831 | 122.8226 | 122.7676 | 0.14648 | 122.7081 | 62.9425 | 122.7081 | -59.967 | -122.7631 | 62.8143 | 122.7676 | 62.8647 | 63.3865
1884.8281 | 122.937 | -62.8693 | 59.8572 | -0.037537 | -0.0016513 | -0.0060007 | 2.8971 | 0.0011109 | -0.00099116 | -0.0022581 | -0.12845 | 0.16331 | 0.12495 | -0.0018712 | 0.057106 | 0.10521 | 0.0032641 | -0.12817 | 0.041199 | -0.12817 | -0.14648 | -0.064087 | -0.17395 | -0.10529 | 0.39825 | 59.8114 | -62.9013 | 59.8755 | 59.9396 | 59.7565 | 0.17395 | 62.7411 | -59.816 | -60.0037 | 62.8052 | 62.764 | 62.6953 | 0.022888 | -0.045776 | -0.032043 | -0.045777 | 0.01831 | 122.8088 | 63.0432 | 122.6257 | 63.0753 | 122.6578 | 0.064087 | -0.01831 | 122.8409 | 122.7768 | 0.16937 | 122.7127 | 62.9105 | 122.6807 | -59.9854 | -122.7585 | 62.7228 | 122.7448 | 62.7411 | 63.2675
1885.8906 | 123.0515 | -62.8235 | 59.8755 | 0.023498 | 0.00069854 | -0.0085641 | 2.8918 | -0.0033753 | -0.0024866 | -0.0016171 | -0.033844 | 0.1616 | 0.12773 | -0.0044348 | 0.057106 | 0.10329 | -0.0037855 | 0.027466 | 0.068665 | -0.054932 | 0.032043 | 0.19226 | 0.091553 | 0.091553 | 0.66834 | 59.7931 | -62.8372 | 59.9945 | 60.1089 | 59.9304 | 0.37537 | 62.7686 | -59.8068 | -59.8434 | 63.0157 | 62.915 | 62.915 | 0.14649 | 0.14649 | -0.013733 | -0.082397 | 0.11902 | 122.9324 | 63.1989 | 122.7539 | 63.2126 | 122.7676 | 0.24719 | 0.086975 | 122.9462 | 122.8317 | 0.1236 | 122.6303 | 62.8922 | 122.6166 | -59.9304 | -122.7127 | 62.8555 | 122.818 | 62.851 | 63.4918
1886.8438 | 122.9965 | -62.8555 | 59.8526 | -0.037537 | -0.0010105 | -0.0081369 | 2.893 | 0.0019653 | -0.0012048 | -0.0037533 | -0.046051 | 0.16138 | 0.12602 | -0.0022986 | 0.054756 | 0.10564 | 0.00027333 | -0.091553 | 0.004578 | -0.11902 | -0.082397 | 0.027466 | -0.073242 | -0.032043 | 0.48065 | 59.7977 | -62.8647 | 59.9075 | 59.9762 | 59.8068 | 0.23804 | 62.7365 | -59.848 | -59.935 | 62.883 | 62.8235 | 62.7823 | 0.086976 | 0.045777 | -0.009155 | -0.054932 | 0.054932 | 122.8317 | 63.0936 | 122.6624 | 63.1027 | 122.6715 | 0.14649 | 0.036622 | 122.8409 | 122.7722 | 0.1236 | 122.6624 | 62.8601 | 122.6532 | -59.9716 | -122.7173 | 62.7731 | 122.7631 | 62.764 | 63.3362
1887.8906 | 122.8958 | -62.8784 | 59.8984 | 0.031128 | -0.0027195 | -0.0066415 | 2.896 | 0.0038879 | -0.00013676 | -0.0011899 | -0.15286 | 0.16395 | 0.12516 | 0.003683 | 0.05561 | 0.10543 | -0.0020765 | -0.045776 | 0.050354 | -0.11444 | -0.086975 | -0.004578 | -0.11444 | -0.054932 | 0.46234 | 59.8114 | -62.883 | 59.8618 | 59.9213 | 59.7198 | 0.21973 | 62.764 | -59.848 | -59.9854 | 62.8738 | 62.8235 | 62.764 | 0.059509 | 0 | -0.004578 | -0.086975 | -0.036621 | 122.7997 | 63.0981 | 122.5983 | 63.1027 | 122.6028 | 0.10986 | 0.027466 | 122.8043 | 122.7448 | 0.16479 | 122.6944 | 62.9288 | 122.6898 | -60.0128 | -122.7814 | 62.7914 | 122.7402 | 62.8326 | 63.3408
1888.8281 | 122.8867 | -62.8464 | 59.8709 | 0.00061049 | -0.00036966 | -0.0081369 | 2.8954 | -0.0014527 | -0.00077756 | 0.0030825 | -0.1376 | 0.16416 | 0.12687 | -0.001444 | 0.053901 | 0.10521 | -0.0033581 | 0.018311 | 0.082397 | -0.073242 | -0.022888 | 0.064087 | -0.045776 | 0.018311 | 0.54932 | 59.8343 | -62.8647 | 59.9121 | 59.9808 | 59.7885 | 0.23346 | 62.7731 | -59.7885 | -59.8938 | 62.9105 | 62.8647 | 62.8006 | 0.091553 | 0.027466 | -0.01831 | -0.036621 | 0.041198 | 122.8271 | 63.0798 | 122.6349 | 63.0981 | 122.6532 | 0.13733 | 0.050354 | 122.8455 | 122.7768 | 0.15564 | 122.699 | 62.9288 | 122.6807 | -59.9442 | -122.7356 | 62.8235 | 122.7585 | 62.8647 | 63.3957
1889.8281 | 122.9782 | -62.883 | 59.848 | -0.083313 | -0.0014377 | -0.0081369 | 2.8977 | 0.00025629 | 0.00050424 | -0.0039671 | -0.14676 | 0.16309 | 0.12837 | -0.0029394 | 0.057747 | 0.10457 | -0.0052809 | -0.10071 | 0.045776 | -0.16022 | -0.17395 | -0.091553 | -0.1831 | -0.10529 | 0.38452 | 59.8251 | -62.8967 | 59.8526 | 59.8801 | 59.6924 | 0.17395 | 62.7228 | -59.8022 | -60.022 | 62.7914 | 62.7777 | 62.6999 | 0.054931 | -0.022888 | -0.013733 | -0.022888 | 0.004578 | 122.7631 | 63.0569 | 122.5754 | 63.0707 | 122.5891 | 0.068664 | -0.013733 | 122.7768 | 122.7493 | 0.20599 | 122.7219 | 62.9288 | 122.7081 | -60.0082 | -122.7448 | 62.709 | 122.7356 | 62.7823 | 63.2675
1890.8906 | 123.0148 | -62.8281 | 59.8434 | -0.098572 | 0.00048494 | -0.0081369 | 2.8952 | 0.00046989 | 0.0015722 | -0.0028989 | -0.036896 | 0.16053 | 0.1273 | -0.0052892 | 0.058174 | 0.10479 | 0.0013415 | 0.041199 | 0.073242 | -0.041199 | 0.054932 | 0.19226 | 0.073242 | 0.10986 | 0.90179 | 59.848 | -62.8098 | 59.9304 | 60.1089 | 59.8709 | 0.36621 | 62.7869 | -59.7702 | -59.7885 | 63.0203 | 62.9379 | 62.9013 | 0.15106 | 0.11444 | 0.018311 | 0.004577 | 0.086975 | 122.937 | 63.1943 | 122.699 | 63.176 | 122.6807 | 0.23346 | 0.096131 | 122.9187 | 122.7402 | 0.11444 | 122.6578 | 62.9013 | 122.6761 | -59.8846 | -122.6532 | 62.883 | 122.7585 | 62.8693 | 63.7299
1891.8438 | 123.0194 | -62.8189 | 59.8343 | -0.037537 | -0.0025059 | -0.0092051 | 2.8937 | 0.00046989 | 0.00093144 | 0.00073273 | -0.027741 | 0.16416 | 0.132 | -0.0059302 | 0.057747 | 0.10436 | -0.0037855 | 0.022888 | 0.054932 | -0.059509 | 0.018311 | 0.13733 | 0.045776 | 0.091553 | 0.6134 | 59.8068 | -62.8418 | 59.9945 | 60.0723 | 59.903 | 0.38452 | 62.7594 | -59.7794 | -59.816 | 62.9562 | 62.9105 | 62.8647 | 0.15106 | 0.10528 | -0.022888 | -0.027466 | 0.16022 | 122.8912 | 63.2034 | 122.7219 | 63.2263 | 122.7448 | 0.19684 | 0.07782 | 122.9141 | 122.8363 | 0.11444 | 122.6486 | 62.8738 | 122.6257 | -59.8938 | -122.6761 | 62.8372 | 122.8134 | 62.8418 | 63.4323
1892.9062 | 122.9736 | -62.8326 | 59.8343 | -0.022278 | 0.00091214 | -0.0066415 | 2.89 | 0.0043151 | -0.0020594 | -0.0018307 | -0.067413 | 0.16309 | 0.12709 | -0.0035802 | 0.056678 | 0.10543 | -0.0033581 | -0.041199 | -0.022888 | -0.13275 | -0.064087 | 0.022888 | -0.10986 | -0.013733 | 0.49896 | 59.7839 | -62.8555 | 59.903 | 59.9762 | 59.8206 | 0.23346 | 62.6999 | -59.8572 | -59.8984 | 62.8555 | 62.8189 | 62.7228 | 0.11902 | 0.022888 | -0.022888 | -0.050354 | 0.068664 | 122.8088 | 63.0661 | 122.6532 | 63.089 | 122.6761 | 0.15564 | 0.068664 | 122.8317 | 122.7585 | 0.10986 | 122.6395 | 62.8098 | 122.6166 | -59.967 | -122.6898 | 62.7686 | 122.7356 | 62.7914 | 63.3316
1893.8281 | 123.0057 | -62.851 | 59.8389 | -0.007019 | -0.0018649 | -0.0079233 | 2.8952 | 0.0034607 | -0.0012048 | -0.0024717 | -0.1376 | 0.16331 | 0.12666 | 0.00026495 | 0.054969 | 0.10436 | 0.0024097 | -0.10529 | 0.022888 | -0.16022 | -0.11444 | -0.045776 | -0.13733 | -0.082397 | 0.44861 | 59.7931 | -62.883 | 59.9304 | 59.9854 | 59.8114 | 0.24261 | 62.6907 | -59.816 | -59.9533 | 62.8052 | 62.7686 | 62.7136 | 0.07782 | 0.022888 | -0.032044 | -0.045776 | 0.091553 | 122.8363 | 63.0936 | 122.6624 | 63.1256 | 122.6944 | 0.11444 | 0.045776 | 122.8683 | 122.8134 | 0.1831 | 122.6761 | 62.8738 | 122.644 | -59.9991 | -122.7219 | 62.7365 | 122.7814 | 62.7457 | 63.2996
1894.8906 | 123.0423 | -62.8143 | 59.8572 | -0.037537 | -0.0012241 | -0.0094187 | 2.8926 | -0.00038451 | -0.00099116 | 9.193e-05 | -0.052155 | 0.16181 | 0.12709 | -0.003153 | 0.056038 | 0.10265 | -0.0014355 | 0.009155 | 0.050354 | -0.064087 | 0.022888 | 0.15106 | 0.045776 | 0.10529 | 0.6134 | 59.7885 | -62.851 | 59.9945 | 60.0677 | 59.9167 | 0.37079 | 62.7502 | -59.8068 | -59.8343 | 62.9654 | 62.9196 | 62.8601 | 0.16937 | 0.10986 | -0.036621 | -0.068665 | 0.13733 | 122.8821 | 63.1851 | 122.731 | 63.2217 | 122.7676 | 0.21515 | 0.086975 | 122.9187 | 122.8455 | 0.11444 | 122.6395 | 62.8647 | 122.6028 | -59.9213 | -122.7081 | 62.8372 | 122.8088 | 62.8235 | 63.4277
1895.8281 | 122.8912 | -62.8418 | 59.8572 | -0.098572 | -0.00079686 | -0.0064279 | 2.8943 | 0.00025629 | 7.6842e-05 | -0.0026853 | -0.16812 | 0.16309 | 0.12858 | 0.0021876 | 0.054542 | 0.10628 | -0.0063489 | -0.068665 | 0.041199 | -0.1236 | -0.11902 | -0.036621 | -0.14191 | -0.11902 | 0.39368 | 59.8572 | -62.9059 | 59.8434 | 59.8709 | 59.7153 | 0.20599 | 62.7182 | -59.816 | -59.9762 | 62.8052 | 62.7228 | 62.6999 | 0.004577 | -0.018311 | -0.064087 | 0 | -0.013733 | 122.7127 | 63.0478 | 122.5571 | 63.1119 | 122.6212 | 0.086975 | 0.004577 | 122.7768 | 122.7493 | 0.16479 | 122.7631 | 62.883 | 122.699 | -59.9808 | -122.7631 | 62.7228 | 122.6852 | 62.7731 | 63.2355
1896.8281 | 122.8821 | -62.8738 | 59.9075 | -0.007019 | -0.0020785 | -0.0072825 | 2.895 | -0.0018799 | -0.0018458 | -0.0014035 | -0.16202 | 0.16395 | 0.12516 | 0.00047855 | 0.05561 | 0.10415 | -0.00079467 | -0.045776 | 0.064087 | -0.10986 | -0.091553 | -0.022888 | -0.13733 | -0.086975 | 0.44403 | 59.8343 | -62.8876 | 59.8572 | 59.9075 | 59.697 | 0.21057 | 62.764 | -59.8434 | -59.9991 | 62.851 | 62.7869 | 62.7365 | 0.022888 | -0.027466 | -0.013733 | -0.073242 | -0.050354 | 122.7814 | 63.0844 | 122.5708 | 63.0981 | 122.5845 | 0.086975 | 0.01831 | 122.7951 | 122.7448 | 0.17395 | 122.7219 | 62.9379 | 122.7081 | -60.0174 | -122.7951 | 62.7823 | 122.731 | 62.8281 | 63.3179
1897.8906 | 122.9233 | -62.8464 | 59.8846 | 0.015869 | -0.0014377 | -0.0094187 | 2.8939 | 0.00046989 | 0.00050424 | -0.0037533 | -0.055206 | 0.1648 | 0.12837 | -0.0059302 | 0.058174 | 0.10372 | 0.0026233 | 0.004578 | 0.16479 | -0.041199 | 0.31128 | 0.52643 | -0.28381 | -0.21057 | 0.46692 | 59.8572 | -62.8738 | 59.8526 | 59.9487 | 59.761 | 0.32959 | 62.8052 | -59.7198 | -59.5734 | 63.3728 | 62.6358 | 62.5626 | -0.16937 | -0.24261 | -0.027465 | -0.027466 | -0.032044 | 122.7951 | 63.176 | 122.6074 | 63.2034 | 122.6349 | 0.56763 | 0.35248 | 122.8226 | 122.7264 | 0.20599 | 122.731 | 63.0112 | 122.7036 | -59.9258 | -122.7585 | 63.1577 | 122.699 | 62.851 | 63.3133
1898.8281 | 122.9416 | -62.8372 | 59.9167 | -0.075684 | 5.7742e-05 | -0.0085641 | 2.8933 | 0.00089729 | -0.00099116 | -0.0024717 | -0.16507 | 0.16117 | 0.12602 | -0.0018712 | 0.057533 | 0.1065 | -0.0054945 | 0.013733 | 0.086975 | -0.073242 | -0.036621 | 0.041199 | -0.050354 | 0.004578 | 0.55389 | 59.848 | -62.851 | 59.8251 | 60.0723 | 59.7794 | 0.29755 | 62.764 | -59.8297 | -59.9533 | 62.8784 | 62.8418 | 62.7869 | 0.07782 | 0.022888 | -0.013733 | -0.068665 | -0.091553 | 122.9095 | 63.1348 | 122.6166 | 63.1485 | 122.6303 | 0.11444 | 0.036621 | 122.9233 | 122.6761 | 0.16022 | 122.699 | 62.9242 | 122.6852 | -59.9899 | -122.7676 | 62.8006 | 122.6624 | 62.851 | 63.3911
1899.8906 | 122.905 | -62.8235 | 59.9121 | -0.037537 | -0.00079686 | -0.0096323 | 2.8928 | -0.0025207 | 0.00093144 | -0.0016171 | -0.094879 | 0.16373 | 0.12687 | -0.0063574 | 0.056892 | 0.10521 | -0.0016493 | -0.013733 | 0.14191 | -0.022888 | -0.032043 | 0.064087 | -0.013733 | 0.032043 | 0.50812 | 59.8709 | -62.883 | 59.8618 | 59.9442 | 59.7748 | 0.30212 | 62.8006 | -59.7702 | -59.9442 | 62.8876 | 62.8555 | 62.8098 | 0.054931 | 0.009155 | -0.05951 | -0.041198 | -0.050354 | 122.7676 | 63.1256 | 122.5983 | 63.1851 | 122.6578 | 0.086975 | -0.009155 | 122.8271 | 122.7448 | 0.16479 | 122.7539 | 62.9654 | 122.6944 | -59.935 | -122.7951 | 62.7914 | 122.6852 | 62.8098 | 63.3316
1900.8281 | 122.9187 | -62.8967 | 59.8663 | -0.022278 | -0.00036966 | -0.0072825 | 2.8967 | 0.0043151 | -0.00099116 | -0.0024717 | -0.14676 | 0.16352 | 0.12837 | 0.00026495 | 0.056465 | 0.10521 | 0.0013415 | -0.082397 | 0.059509 | -0.11444 | -0.16479 | -0.10529 | -0.19684 | -0.13275 | 0.37994 | 59.8206 | -62.9013 | 59.8343 | 59.903 | 59.7153 | 0.18768 | 62.7823 | -59.8068 | -60.0311 | 62.7914 | 62.764 | 62.6999 | -0.01831 | -0.082397 | -0.004577 | -0.045776 | -0.032043 | 122.7997 | 63.0844 | 122.612 | 63.089 | 122.6166 | 0.009155 | -0.050354 | 122.8043 | 122.7356 | 0.17395 | 122.7219 | 62.9562 | 122.7173 | -59.9808 | -122.7676 | 62.7319 | 122.731 | 62.8143 | 63.2767
1901.9062 | 122.9141 | -62.8464 | 59.8984 | -0.029907 | -0.0014377 | -0.0072825 | 2.8947 | 0.00089729 | -0.00099116 | -0.0020443 | -0.14371 | 0.16245 | 0.12751 | -0.002085 | 0.056038 | 0.10799 | -0.0014355 | -0.036621 | 0.068665 | -0.10986 | -0.10071 | -0.004578 | -0.1236 | -0.073242 | 0.45319 | 59.8343 | -62.883 | 59.8618 | 59.9121 | 59.7153 | 0.21515 | 62.7365 | -59.8297 | -59.9991 | 62.8418 | 62.7731 | 62.7228 | 0.036621 | -0.013733 | -0.036621 | -0.064086 | -0.036621 | 122.7585 | 63.0615 | 122.5616 | 63.0981 | 122.5983 | 0.10529 | 0.009155 | 122.7951 | 122.7448 | 0.17853 | 122.7173 | 62.915 | 122.6807 | -60.0082 | -122.7814 | 62.7457 | 122.7081 | 62.8098 | 63.2996
1902.8281 | 122.9095 | -62.8647 | 59.8938 | -0.037537 | -0.00079686 | -0.0094187 | 2.8956 | 0.0015381 | -0.00056396 | -0.00012167 | -0.1376 | 0.16352 | 0.12837 | -0.0067846 | 0.057106 | 0.10628 | -0.0020765 | -0.054932 | 0.068665 | -0.10986 | -0.11902 | -0.041199 | -0.16022 | -0.09613 | 0.41199 | 59.8297 | -62.8555 | 59.8434 | 59.8938 | 59.7061 | 0.20142 | 62.7548 | -59.8251 | -60.0128 | 62.8235 | 62.7686 | 62.7045 | 0.013733 | -0.050354 | 0.009155 | -0.064087 | -0.050354 | 122.7585 | 63.0661 | 122.5708 | 63.0569 | 122.5616 | 0.068664 | -0.009156 | 122.7493 | 122.699 | 0.17853 | 122.6852 | 62.9334 | 122.6944 | -60.0037 | -122.7493 | 62.7457 | 122.7081 | 62.8098 | 63.2767
1903.8906 | 122.905 | -62.8555 | 59.9121 | -0.014649 | -0.0012241 | -0.0094187 | 2.8928 | -0.0029479 | -0.0012048 | -0.0028989 | -0.058258 | 0.1648 | 0.12602 | -0.0059302 | 0.056038 | 0.10244 | 0.0034777 | 0.004578 | 0.11444 | -0.059509 | -0.050354 | 0.059509 | 0.004578 | 0.032043 | 0.54016 | 59.8526 | -62.8784 | 59.848 | 59.9442 | 59.7931 | 0.33417 | 62.796 | -59.7977 | -59.9625 | 62.915 | 62.8876 | 62.8601 | 0.091552 | 0.064087 | -0.022888 | -0.059509 | -0.064087 | 122.7997 | 63.1897 | 122.6486 | 63.2126 | 122.6715 | 0.11902 | 0.009155 | 122.8226 | 122.7264 | 0.17395 | 122.731 | 62.97 | 122.7081 | -59.9716 | -122.7905 | 62.8052 | 122.7036 | 62.8601 | 63.3957
1904.8281 | 122.9095 | -62.8464 | 59.8846 | -0.037537 | 0.00048494 | -0.0087777 | 2.8933 | -0.0027343 | -0.0031274 | -0.0018307 | -0.13455 | 0.16309 | 0.13008 | -0.0052892 | 0.057106 | 0.10415 | -0.0072035 | -0.009155 | 0.073242 | -0.091553 | -0.064087 | 0.027466 | -0.091553 | -0.027466 | 0.50812 | 59.8434 | -62.883 | 59.8846 | 59.9396 | 59.761 | 0.23804 | 62.7548 | -59.8114 | -59.9487 | 62.8738 | 62.8189 | 62.7548 | 0.064087 | 0 | -0.036621 | -0.041199 | 0 | 122.7859 | 63.0844 | 122.6074 | 63.121 | 122.644 | 0.11902 | 0.027466 | 122.8226 | 122.7676 | 0.16479 | 122.7264 | 62.9196 | 122.6898 | -59.9762 | -122.7676 | 62.7823 | 122.731 | 62.8372 | 63.3545
1905.8906 | 122.9965 | -62.8326 | 59.8892 | 0.00824 | -0.00058326 | -0.0087777 | 2.8928 | 0.0021789 | -0.00077756 | -0.00097627 | -0.10403 | 0.16544 | 0.12709 | -0.003794 | 0.056465 | 0.105 | -0.0022901 | 0.018311 | 0.13275 | -0.045776 | -0.018311 | 0.064087 | -0.013733 | 0.022888 | 0.54016 | 59.8663 | -62.8601 | 59.9213 | 59.9854 | 59.816 | 0.3479 | 62.7869 | -59.7565 | -59.9075 | 62.8967 | 62.8555 | 62.8189 | 0.068664 | 0.032043 | -0.027465 | -0.022888 | 0.032044 | 122.818 | 63.1805 | 122.6486 | 63.208 | 122.6761 | 0.10986 | 0.027465 | 122.8455 | 122.7814 | 0.17853 | 122.7264 | 62.9654 | 122.699 | -59.935 | -122.7493 | 62.8143 | 122.7539 | 62.851 | 63.3728
1906.8281 | 122.9782 | -62.8281 | 59.8938 | 0.00061049 | -0.0018649 | -0.0070687 | 2.8943 | -0.00081171 | -0.0012048 | -0.0048215 | -0.07962 | 0.1648 | 0.12709 | -0.0010168 | 0.05796 | 0.105 | -0.0037855 | 0.045776 | 0.15564 | -0.032043 | -0.022888 | 0.059509 | -0.018311 | 0.013733 | 0.56305 | 59.8526 | -62.8693 | 59.9121 | 59.9808 | 59.7885 | 0.34332 | 62.796 | -59.7382 | -59.9167 | 62.8876 | 62.8418 | 62.8098 | 0.045776 | 0.013732 | -0.041199 | -0.041199 | 0.01831 | 122.8088 | 63.1714 | 122.6166 | 63.2126 | 122.6578 | 0.091552 | 0.009155 | 122.85 | 122.7814 | 0.18768 | 122.7219 | 62.9837 | 122.6807 | -59.9258 | -122.7631 | 62.8052 | 122.7402 | 62.8738 | 63.3911
1907.8906 | 122.9324 | -62.8281 | 59.8892 | 0.054016 | 0.00048494 | -0.0070687 | 2.8937 | -0.0016663 | 0.0013586 | 9.193e-05 | -0.036896 | 0.16202 | 0.12858 | -0.0076392 | 0.056038 | 0.10415 | -0.00058107 | 0.059509 | 0.091553 | -0.032043 | 0.009155 | 0.14648 | 0.041199 | 0.091553 | 0.61798 | 59.848 | -62.8372 | 59.8846 | 59.9991 | 59.8206 | 0.36163 | 62.796 | -59.7977 | -59.8801 | 62.9745 | 62.9196 | 62.8693 | 0.1236 | 0.073242 | -0.009155 | -0.041199 | -0.004577 | 122.8271 | 63.1897 | 122.6486 | 63.1989 | 122.6578 | 0.17853 | 0.041198 | 122.8363 | 122.7219 | 0.1236 | 122.6852 | 62.9196 | 122.6761 | -59.9213 | -122.7264 | 62.8372 | 122.7127 | 62.8876 | 63.446
1908.8281 | 122.9553 | -62.8326 | 59.8846 | 0.015869 | 0.0017667 | -0.0077097 | 2.8947 | 0.0034607 | -0.0029138 | -0.0037533 | -0.1254 | 0.16181 | 0.12773 | 5.1352e-05 | 0.056892 | 0.10692 | 0.0021961 | 0.013733 | 0.086975 | -0.07782 | -0.050354 | 0.041199 | -0.054932 | -0.022888 | 0.42114 | 59.8343 | -62.8693 | 59.8892 | 59.9899 | 59.8068 | 0.31586 | 62.7548 | -59.7977 | -59.935 | 62.8738 | 62.8098 | 62.7777 | 0.054932 | 0.022888 | -0.036621 | -0.050354 | 0.004577 | 122.8226 | 63.1485 | 122.6395 | 63.1851 | 122.6761 | 0.11902 | 0.027466 | 122.8592 | 122.7585 | 0.16479 | 122.7036 | 62.9196 | 122.6669 | -59.9625 | -122.7539 | 62.7823 | 122.7219 | 62.8464 | 63.2538
1909.8906 | 123.0331 | -62.8189 | 59.8663 | -0.052796 | -0.0020785 | -0.0092051 | 2.8945 | -0.00081171 | 0.0013586 | 0.00073273 | -0.0063781 | 0.16224 | 0.12773 | -0.0089208 | 0.056678 | 0.10201 | 5.9726e-05 | 0.009155 | 0.036621 | -0.059509 | 0 | 0.10071 | 0.009155 | 0.073242 | 0.59052 | 59.7931 | -62.8326 | 59.9533 | 60.0403 | 59.8938 | 0.37079 | 62.7594 | -59.8297 | -59.8663 | 62.9196 | 62.8922 | 62.8281 | 0.13275 | 0.068664 | -0.013733 | -0.073242 | 0.086975 | 122.8592 | 63.1897 | 122.7127 | 63.2034 | 122.7264 | 0.16022 | 0.059509 | 122.8729 | 122.7859 | 0.09613 | 122.6257 | 62.8555 | 122.612 | -59.9258 | -122.699 | 62.8189 | 122.7722 | 62.8281 | 63.4094
1910.8281 | 122.9233 | -62.8326 | 59.9167 | 0.00824 | -0.0014377 | -0.0098459 | 2.8941 | -0.00081171 | -0.0014184 | -0.0048215 | -0.042999 | 0.16309 | 0.12922 | 0.0015466 | 0.055183 | 0.1018 | -0.0020765 | 0.041199 | 0.10529 | -0.032043 | 0.004578 | 0.091553 | 0.018311 | 0.054932 | 0.54932 | 59.8618 | -62.8281 | 59.8846 | 59.9533 | 59.7885 | 0.32959 | 62.8006 | -59.8114 | -59.9121 | 62.9242 | 62.8876 | 62.851 | 0.086975 | 0.050354 | 0.004578 | -0.054932 | -0.032043 | 122.7859 | 63.1622 | 122.6212 | 63.1577 | 122.6166 | 0.1236 | 0.036621 | 122.7814 | 122.7127 | 0.13733 | 122.6898 | 62.9379 | 122.6944 | -59.9487 | -122.7448 | 62.8372 | 122.7173 | 62.8738 | 63.382
1911.8281 | 122.9599 | -62.8647 | 59.9167 | 0.00061049 | 0.00069854 | -0.0077097 | 2.8926 | 0.0028199 | 0.00071784 | -0.0018307 | -0.11319 | 0.16416 | 0.12666 | -0.003794 | 0.055397 | 0.10607 | -0.0052809 | 0.022888 | 0.11902 | -0.041199 | -0.018311 | 0.073242 | -0.018311 | 0.018311 | 0.55389 | 59.8526 | -62.8464 | 59.9121 | 59.9899 | 59.816 | 0.37079 | 62.8235 | -59.7977 | -59.935 | 62.9379 | 62.883 | 62.8464 | 0.05951 | 0.022888 | 0.01831 | -0.064087 | -0.004578 | 122.8546 | 63.2355 | 122.6807 | 63.2172 | 122.6624 | 0.11444 | 0.022888 | 122.8363 | 122.7585 | 0.16022 | 122.699 | 62.9837 | 122.7173 | -59.9579 | -122.7631 | 62.8464 | 122.7768 | 62.8876 | 63.4186
1912.8906 | 122.9736 | -62.8326 | 59.8938 | 0.023498 | -0.0010105 | -0.0094187 | 2.893 | -0.0012391 | -0.0031274 | -0.0026853 | -0.042999 | 0.16331 | 0.12944 | -0.0029394 | 0.056892 | 0.10393 | 0.0015551 | 0.073242 | 0.091553 | -0.018311 | 0.027466 | 0.14191 | 0.036621 | 0.082397 | 0.62714 | 59.8297 | -62.8418 | 59.9258 | 60.0082 | 59.848 | 0.37079 | 62.8143 | -59.8022 | -59.8663 | 62.9745 | 62.915 | 62.8693 | 0.10071 | 0.054932 | -0.009155 | -0.064087 | 0.032043 | 122.8409 | 63.2034 | 122.6807 | 63.2126 | 122.6898 | 0.16022 | 0.045777 | 122.85 | 122.7676 | 0.10986 | 122.6715 | 62.9242 | 122.6624 | -59.9121 | -122.7356 | 62.8601 | 122.7585 | 62.9059 | 63.4598
1913.8281 | 122.9691 | -62.8418 | 59.8938 | 0.046386 | 0.00069854 | -0.0081369 | 2.895 | 4.2692e-05 | -0.00056396 | -0.0028989 | -0.085724 | 0.16309 | 0.13008 | -0.0016576 | 0.057319 | 0.10479 | 0.0013415 | -0.10529 | 0.16937 | -0.004578 | -0.045776 | 0.018311 | -0.009155 | 0.018311 | 0.5127 | 59.8297 | -62.8922 | 59.8663 | 59.9625 | 59.7885 | 0.32044 | 62.8372 | -59.7244 | -59.9396 | 62.8601 | 62.8601 | 62.8326 | 0.022889 | -0.004577 | -0.050354 | -0.064087 | -0.027466 | 122.8043 | 63.1622 | 122.6303 | 63.2126 | 122.6807 | 0.022889 | -0.041198 | 122.8546 | 122.7585 | 0.17395 | 122.7219 | 63.0112 | 122.6715 | -59.8984 | -122.7859 | 62.796 | 122.7081 | 62.7365 | 63.3545
1914.8906 | 123.0103 | -62.8281 | 59.8618 | -0.045166 | -0.0010105 | -0.0083505 | 2.8935 | 0.0032471 | -0.002273 | -0.0020443 | -0.052155 | 0.16267 | 0.12666 | 0.00026495 | 0.055397 | 0.10585 | -0.0025037 | -0.032043 | 0.032043 | -0.07782 | -0.050354 | 0.036621 | -0.050354 | 0.009155 | 0.60883 | 59.7977 | -62.8418 | 59.9075 | 60.0082 | 59.8251 | 0.27466 | 62.7502 | -59.8297 | -59.9121 | 62.8647 | 62.8372 | 62.7777 | 0.086975 | 0.027466 | -0.013733 | -0.064087 | 0.045777 | 122.8363 | 63.1027 | 122.6532 | 63.1165 | 122.6669 | 0.11444 | 0.027466 | 122.85 | 122.7493 | 0.10986 | 122.6395 | 62.8601 | 122.6257 | -59.9396 | -122.7036 | 62.7777 | 122.7356 | 62.796 | 63.4369
1915.8281 | 122.9416 | -62.8647 | 59.9213 | -0.029907 | 5.7742e-05 | -0.0077097 | 2.8933 | 0.00046989 | -0.0031274 | -0.0026853 | -0.094879 | 0.16224 | 0.1273 | 0.003042 | 0.057106 | 0.10543 | -0.0025037 | -0.036621 | 0.12817 | -0.059509 | -0.045776 | 0.027466 | -0.027466 | 0.013733 | 0.50812 | 59.8526 | -62.851 | 59.8755 | 59.9716 | 59.7931 | 0.33417 | 62.8052 | -59.7931 | -59.967 | 62.8922 | 62.8784 | 62.8372 | 0.073242 | 0.032043 | 0.013733 | -0.068665 | -0.045777 | 122.8363 | 63.1989 | 122.6578 | 63.1851 | 122.644 | 0.086975 | 0.013733 | 122.8226 | 122.7264 | 0.18768 | 122.7036 | 62.9929 | 122.7173 | -59.9808 | -122.7722 | 62.8189 | 122.7402 | 62.8281 | 63.3728
1916.8906 | 122.9599 | -62.8555 | 59.8663 | -0.068054 | -0.0040013 | -0.0081369 | 2.8962 | 0.0034607 | 0.0024268 | -0.0026853 | -0.14981 | 0.16459 | 0.12837 | -0.0063574 | 0.056251 | 0.10393 | -0.0014355 | -0.07782 | 0.045776 | -0.13275 | -0.14191 | -0.054932 | -0.17853 | -0.11444 | 0.40283 | 59.8206 | -62.8876 | 59.8709 | 59.9213 | 59.7565 | 0.21057 | 62.7228 | -59.8206 | -60.0082 | 62.8006 | 62.7411 | 62.677 | 0.01831 | -0.045777 | -0.032043 | -0.045776 | 0.004578 | 122.7768 | 63.0661 | 122.612 | 63.0981 | 122.644 | 0.077819 | -0.009156 | 122.8088 | 122.7585 | 0.17853 | 122.7081 | 62.9013 | 122.6761 | -59.9991 | -122.7539 | 62.7136 | 122.7264 | 62.7777 | 63.2584
1917.8281 | 122.9187 | -62.8693 | 59.9075 | 0.046386 | 5.7742e-05 | -0.0096323 | 2.8937 | 4.2692e-05 | -0.0020594 | -0.00097627 | -0.1254 | 0.16373 | 0.12773 | 0.0015466 | 0.055824 | 0.10393 | 0.00070073 | 0.013733 | 0.11902 | -0.082397 | -0.041199 | 0.054932 | -0.013733 | 0.009155 | 0.51727 | 59.8618 | -62.8555 | 59.8801 | 59.9899 | 59.7885 | 0.32501 | 62.7869 | -59.7885 | -59.9487 | 62.9242 | 62.8784 | 62.8555 | 0.091552 | 0.068664 | 0.013733 | -0.045777 | -0.027466 | 122.8592 | 63.1943 | 122.6578 | 63.1805 | 122.644 | 0.13733 | 0.041198 | 122.8455 | 122.7356 | 0.20142 | 122.7173 | 62.9883 | 122.731 | -59.9899 | -122.7631 | 62.8281 | 122.7493 | 62.883 | 63.3865
1918.8906 | 123.0011 | -62.8464 | 59.8755 | -0.014649 | -0.0016513 | -0.0079233 | 2.8958 | -0.0033753 | 0.0017858 | -0.0037533 | -0.042999 | 0.16202 | 0.12858 | -0.002085 | 0.056678 | 0.1035 | 0.0015551 | -0.018311 | 0.045776 | -0.091553 | -0.14191 | 0.036621 | -0.073242 | -0.004578 | 0.49896 | 59.816 | -62.8647 | 59.935 | 60.0082 | 59.848 | 0.30212 | 62.7548 | -59.8297 | -60.0174 | 62.883 | 62.8418 | 62.7731 | 0.086975 | 0.018311 | -0.01831 | -0.059509 | 0.05951 | 122.8546 | 63.1485 | 122.6944 | 63.1668 | 122.7127 | 0.12817 | -0.050354 | 122.8729 | 122.7997 | 0.13733 | 122.6807 | 62.8922 | 122.6624 | -59.967 | -122.7402 | 62.7045 | 122.7814 | 62.8281 | 63.3453
1919.8281 | 122.9279 | -62.8647 | 59.935 | 0.015869 | -0.00036966 | -0.0055735 | 2.8937 | 0.0011109 | -0.00056396 | -0.0041807 | -0.091827 | 0.16331 | 0.12666 | 5.1352e-05 | 0.054969 | 0.10415 | -0.0012219 | 0.018311 | 0.16022 | -0.027466 | -0.041199 | 0.050354 | -0.013733 | 0.045776 | 0.6958 | 59.8938 | -62.8235 | 59.8297 | 59.9808 | 59.7656 | 0.32501 | 62.8372 | -59.7748 | -59.9762 | 62.915 | 62.9105 | 62.851 | 0.073242 | 0.013733 | 0.041199 | -0.041199 | -0.10529 | 122.8455 | 63.1897 | 122.6303 | 63.1485 | 122.5891 | 0.07782 | -0.013733 | 122.8043 | 122.6532 | 0.18768 | 122.7173 | 63.0249 | 122.7585 | -59.9625 | -122.7585 | 62.8235 | 122.6944 | 62.883 | 63.5605
1920.8906 | 123.0331 | -62.8372 | 59.8389 | -0.052796 | 0.00048494 | -0.0064279 | 2.8926 | 0.0041015 | -0.00013676 | -0.0031125 | -0.082672 | 0.1648 | 0.12815 | -0.0016576 | 0.054756 | 0.10436 | -0.0027173 | -0.027466 | -0.036621 | -0.11444 | -0.022888 | -0.33417 | -0.29755 | 0.20599 | 0.5722 | 59.7977 | -62.8601 | 59.9487 | 60.0357 | 59.8343 | 0.26093 | 62.7228 | -59.8755 | -59.8618 | 62.5031 | 63.0432 | 62.5397 | 0.32044 | -0.1831 | -0.022888 | -0.041199 | 0.10986 | 122.8729 | 63.0981 | 122.6715 | 63.121 | 122.6944 | -0.21973 | 0.091553 | 122.8958 | 122.8088 | 0.07782 | 122.6578 | 62.8006 | 122.6349 | -59.9533 | -122.699 | 62.8143 | 122.7859 | 62.8098 | 63.4094
1921.8281 | 122.9004 | -62.8738 | 59.9258 | -0.022278 | -0.0010105 | -0.0085641 | 2.8945 | 0.00089729 | -0.0020594 | -0.0022581 | -0.091827 | 0.16074 | 0.12666 | -0.0033666 | 0.057106 | 0.10393 | -0.0025037 | 0.018311 | 0.10986 | -0.050354 | 0.013733 | 0.14648 | -0.036621 | 0 | 0.53558 | 59.8663 | -62.8647 | 59.8572 | 59.9487 | 59.7839 | 0.31128 | 62.8235 | -59.816 | -59.9121 | 63.0203 | 62.8738 | 62.8372 | 0.050354 | 0.013733 | 0.009155 | -0.059509 | -0.068664 | 122.8226 | 63.1851 | 122.6578 | 63.176 | 122.6486 | 0.19684 | 0.064087 | 122.8134 | 122.7219 | 0.16022 | 122.731 | 62.9837 | 122.7402 | -59.9762 | -122.7905 | 62.8876 | 122.731 | 62.8922 | 63.4094
1922.8906 | 123.024 | -62.8647 | 59.8251 | -0.075684 | -0.0020785 | -0.0060007 | 2.8947 | -0.0052979 | -0.00035036 | -0.00076267 | -0.021637 | 0.16224 | 0.12602 | -0.0059302 | 0.056892 | 0.1035 | -0.00036747 | -0.059509 | 0.054932 | -0.064087 | -0.041199 | 0.054932 | -0.009155 | 0.018311 | 0.51727 | 59.8114 | -62.8647 | 59.9258 | 60.022 | 59.8572 | 0.32501 | 62.8006 | -59.7702 | -59.8663 | 62.9196 | 62.883 | 62.8555 | 0.082398 | 0.054932 | 0 | -0.013733 | 0.10071 | 122.8867 | 63.1897 | 122.7219 | 63.1897 | 122.7219 | 0.11902 | 0.022888 | 122.8867 | 122.7905 | 0.11902 | 122.6761 | 62.9196 | 122.6761 | -59.8892 | -122.6898 | 62.8235 | 122.7905 | 62.8052 | 63.382
1923.8281 | 122.9095 | -62.8784 | 59.9442 | 0.061645 | 0.0013393 | -0.0087777 | 2.8928 | 0.0023925 | -0.0012048 | 0.00030553 | -0.10709 | 0.16224 | 0.12709 | -0.0052892 | 0.056251 | 0.10543 | -0.0027173 | -0.004578 | 0.11902 | -0.041199 | -0.032043 | 0.045776 | -0.018311 | 0.018311 | 0.53558 | 59.8618 | -62.8601 | 59.8709 | 59.967 | 59.7565 | 0.32959 | 62.8372 | -59.8251 | -59.9762 | 62.9242 | 62.8967 | 62.8601 | 0.05951 | 0.022888 | 0.018311 | -0.082398 | -0.073242 | 122.8455 | 63.208 | 122.6349 | 63.1897 | 122.6166 | 0.086975 | 0.009156 | 122.8271 | 122.731 | 0.16022 | 122.7219 | 62.9974 | 122.7402 | -59.9854 | -122.8043 | 62.8464 | 122.7493 | 62.8738 | 63.414
1924.8906 | 123.056 | -62.8555 | 59.8572 | -0.060425 | -0.0018649 | -0.0092051 | 2.8935 | 0.00089729 | 0.00071784 | -0.0020443 | -0.052155 | 0.16117 | 0.1273 | 0.00090575 | 0.056678 | 0.10457 | -0.0014355 | -0.054932 | 0.013733 | -0.086975 | -0.059509 | 0.036621 | -0.068665 | -0.009155 | 0.4715 | 59.816 | -62.8647 | 59.9121 | 59.9945 | 59.816 | 0.21973 | 62.7686 | -59.8434 | -59.9167 | 62.8922 | 62.8464 | 62.7869 | 0.07782 | 0.01831 | -0.009155 | -0.041199 | 0.054931 | 122.85 | 63.0753 | 122.6715 | 63.0844 | 122.6807 | 0.1236 | 0.027466 | 122.8592 | 122.7768 | 0.10071 | 122.6807 | 62.8693 | 122.6715 | -59.9442 | -122.7219 | 62.796 | 122.7676 | 62.8006 | 63.327
1925.8281 | 122.905 | -62.8555 | 59.9258 | 0.00824 | -0.00036966 | -0.011768 | 2.8937 | 0.00068369 | -0.0014184 | -0.0014035 | -0.10709 | 0.16352 | 0.12602 | 0.00090575 | 0.05561 | 0.10415 | -0.0012219 | 0.004578 | 0.1236 | -0.032043 | -0.018311 | 0.050354 | -0.022888 | 0.027466 | 0.54474 | 59.8663 | -62.8876 | 59.8709 | 59.9533 | 59.7656 | 0.32044 | 62.8235 | -59.8022 | -59.9442 | 62.9059 | 62.883 | 62.8326 | 0.059509 | 0.009155 | -0.032043 | -0.059509 | -0.054931 | 122.8088 | 63.176 | 122.6212 | 63.208 | 122.6532 | 0.082397 | 0.013732 | 122.8409 | 122.7585 | 0.15564 | 122.7539 | 62.9791 | 122.7219 | -59.9579 | -122.8134 | 62.8372 | 122.7264 | 62.8601 | 63.4003
1926.8906 | 123.0423 | -62.8372 | 59.848 | -0.022278 | -0.00058326 | -0.0066415 | 2.8933 | 0.0043151 | -0.00099116 | -0.0016171 | -0.1315 | 0.16309 | 0.12623 | -0.0040076 | 0.056038 | 0.10457 | -0.00079467 | -0.10529 | 0.004578 | -0.14191 | -0.10529 | -0.054932 | -0.13733 | -0.091553 | 0.45776 | 59.816 | -62.8876 | 59.9533 | 59.9808 | 59.8068 | 0.24261 | 62.6953 | -59.8434 | -59.9533 | 62.7823 | 62.7457 | 62.6999 | 0.050354 | 0.004578 | -0.050354 | -0.032043 | 0.10529 | 122.818 | 63.0798 | 122.644 | 63.1302 | 122.6944 | 0.086975 | 0.036621 | 122.8683 | 122.8409 | 0.14649 | 122.7036 | 62.8418 | 122.6532 | -59.9899 | -122.7356 | 62.7319 | 122.7905 | 62.7319 | 63.295
1927.8281 | 122.937 | -62.8464 | 59.903 | 0.00824 | 0.0015529 | -0.0094187 | 2.8945 | 0.0062379 | -0.00056396 | -0.00097627 | -0.14981 | 0.16352 | 0.12709 | -0.0035802 | 0.057533 | 0.10308 | -0.0022901 | 0.009155 | 0.17395 | -0.045776 | -0.013733 | 0.036621 | -0.027466 | 0.018311 | 0.50354 | 59.8618 | -62.8693 | 59.8938 | 59.967 | 59.7931 | 0.32044 | 62.8006 | -59.729 | -59.9167 | 62.883 | 62.8647 | 62.8189 | 0.064087 | 0.01831 | -0.022888 | -0.041199 | -0.009155 | 122.8134 | 63.1668 | 122.6395 | 63.1897 | 122.6624 | 0.082397 | 0.032043 | 122.8363 | 122.7631 | 0.21973 | 122.731 | 63.0203 | 122.7081 | -59.9487 | -122.7722 | 62.8326 | 122.7402 | 62.8555 | 63.3499
1928.8906 | 122.9324 | -62.8464 | 59.8663 | -0.098572 | -0.00036966 | -0.0074961 | 2.8947 | -0.0014527 | -0.00077756 | -0.00097627 | -0.14981 | 0.16181 | 0.1273 | 0.0017602 | 0.056465 | 0.10628 | -0.0044263 | 0.068665 | 0.041199 | -0.10071 | -0.050354 | 0.041199 | -0.068665 | -0.027466 | 0.51727 | 59.8572 | -62.8784 | 59.903 | 59.9442 | 59.7565 | 0.27924 | 62.7457 | -59.8251 | -59.9167 | 62.8876 | 62.8189 | 62.7777 | 0.073242 | 0.032043 | -0.032043 | -0.009155 | 0.036621 | 122.7905 | 63.1256 | 122.6028 | 63.1577 | 122.6349 | 0.14191 | 0.050354 | 122.8226 | 122.7814 | 0.14191 | 122.7356 | 62.8876 | 122.7036 | -59.967 | -122.7448 | 62.796 | 122.7493 | 62.915 | 63.3636
1929.8281 | 123.0515 | -62.8189 | 59.8526 | -0.075684 | -0.0014377 | -0.0070687 | 2.8933 | 0.0011109 | -0.00077756 | -0.0028989 | -0.039948 | 0.16202 | 0.12559 | -0.0091344 | 0.058601 | 0.10521 | -0.0012219 | 0.009155 | 0.059509 | -0.036621 | 0.004578 | 0.13275 | 0.027466 | 0.068665 | 0.6134 | 59.7885 | -62.8418 | 59.967 | 60.0815 | 59.9396 | 0.37537 | 62.7823 | -59.7931 | -59.848 | 62.9517 | 62.8876 | 62.8464 | 0.10529 | 0.064087 | -0.022888 | -0.064087 | 0.11444 | 122.9004 | 63.1943 | 122.7585 | 63.2172 | 122.7814 | 0.16937 | 0.041199 | 122.9233 | 122.8088 | 0.09613 | 122.6303 | 62.8784 | 122.6074 | -59.8892 | -122.6944 | 62.8235 | 122.7859 | 62.8281 | 63.4323
1930.8906 | 123.0011 | -62.8372 | 59.8526 | -0.11383 | -0.0031467 | -0.0072825 | 2.8926 | 0.0015381 | -0.0059046 | 9.193e-05 | -0.11319 | 0.16074 | 0.12837 | -0.0046484 | 0.054756 | 0.105 | -0.0039991 | -0.050354 | -0.036621 | -0.13275 | 0.18768 | 0.041199 | -0.050354 | 0.082397 | 0.54474 | 59.7702 | -62.851 | 59.9533 | 60.022 | 59.8526 | 0.27008 | 62.7045 | -59.8892 | -59.6649 | 62.8784 | 62.9196 | 62.7869 | 0.21515 | 0.082397 | -0.013733 | -0.082397 | 0.10071 | 122.8592 | 63.1073 | 122.6898 | 63.121 | 122.7036 | 0.17395 | 0.32043 | 122.8729 | 122.8043 | 0.09613 | 122.6212 | 62.8006 | 122.6074 | -59.9854 | -122.7036 | 63.0249 | 122.7905 | 62.7869 | 63.382
1931.8281 | 123.024 | -62.8555 | 59.8663 | -0.052796 | -0.0010105 | -0.0079233 | 2.8939 | 0.00046989 | -0.00035036 | 0.00030553 | -0.064362 | 0.16373 | 0.12666 | -0.0072118 | 0.055824 | 0.10479 | -0.0057081 | -0.013733 | 0.041199 | -0.07782 | -0.027466 | 0.068665 | -0.009155 | 0.050354 | 0.54016 | 59.8114 | -62.8601 | 59.9487 | 60.0449 | 59.8755 | 0.34332 | 62.7777 | -59.8251 | -59.8938 | 62.9242 | 62.9059 | 62.8464 | 0.12817 | 0.068665 | -0.004577 | -0.054932 | 0.082397 | 122.9004 | 63.1989 | 122.731 | 63.2034 | 122.7356 | 0.14649 | 0.050354 | 122.905 | 122.8088 | 0.11902 | 122.6715 | 62.8967 | 122.6669 | -59.9442 | -122.7264 | 62.8281 | 122.8043 | 62.8418 | 63.3957
1932.8906 | 122.9782 | -62.8189 | 59.8618 | 0.00061049 | -0.0012241 | -0.0094187 | 2.8943 | -0.0025207 | 7.6842e-05 | -0.0026853 | -0.042999 | 0.16352 | 0.12538 | -0.0052892 | 0.055397 | 0.10222 | 0.0051867 | 0.059509 | 0.073242 | -0.032043 | 0.068665 | 0.17853 | 0.068665 | 0.11902 | 0.66376 | 59.8206 | -62.851 | 59.9304 | 59.903 | 59.9579 | 0.46692 | 62.7869 | -59.7885 | -59.7931 | 62.9974 | 62.9379 | 62.8876 | 0.15106 | 0.10071 | -0.032043 | -0.041198 | 0.068665 | 122.7219 | 63.2858 | 122.7768 | 63.3179 | 122.8088 | 0.21057 | 0.10071 | 122.7539 | 122.7814 | 0.10529 | 122.6715 | 62.8922 | 122.6395 | -59.8938 | -122.7127 | 62.8876 | 122.7493 | 62.8784 | 63.4827
1933.8281 | 123.0515 | -62.7823 | 59.903 | 0.00061049 | 0.00069854 | -0.0089913 | 2.8941 | 0.0011109 | -0.0016322 | -0.0041807 | -0.06131 | 0.16117 | 0.12815 | -0.0055028 | 0.055183 | 0.10265 | -0.0012219 | 0.027466 | 0.068665 | -0.045776 | 0.064087 | 0.1831 | 0.07782 | 0.14191 | 0.65918 | 59.8022 | -62.8326 | 59.9808 | 60.0723 | 59.9075 | 0.3891 | 62.7365 | -59.8343 | -59.8389 | 62.9654 | 62.9242 | 62.8601 | 0.18768 | 0.1236 | -0.050354 | -0.10071 | 0.07782 | 122.8546 | 63.1714 | 122.6898 | 63.2217 | 122.7402 | 0.22888 | 0.10986 | 122.905 | 122.8134 | 0.11444 | 122.6349 | 62.851 | 122.5845 | -59.9487 | -122.7356 | 62.8464 | 122.7631 | 62.8098 | 63.4415
1934.8906 | 122.905 | -62.8784 | 59.903 | -0.075684 | -0.0025059 | -0.0070687 | 2.8958 | -0.00017091 | -0.0029138 | -0.0031125 | -0.18033 | 0.16822 | 0.12944 | 0.0038966 | 0.053901 | 0.10329 | -0.0025037 | -0.10071 | 0.041199 | -0.14648 | -0.16022 | -0.10986 | -0.20599 | -0.12817 | 0.10986 | 59.7794 | -62.9196 | 59.8801 | 59.8755 | 59.7565 | 0.2243 | 62.7319 | -59.8618 | -60.0632 | 62.7686 | 62.7502 | 62.6724 | 0.01831 | -0.05951 | -0.041199 | -0.1236 | -0.022888 | 122.7539 | 63.1027 | 122.6349 | 63.1439 | 122.6761 | 0.036621 | -0.013733 | 122.7951 | 122.7997 | 0.18768 | 122.699 | 62.9196 | 122.6578 | -60.0494 | -122.8226 | 62.7182 | 122.7585 | 62.7777 | 62.9883
1935.8281 | 123.0469 | -62.8189 | 59.8709 | -0.068054 | 0.00048494 | -0.0087777 | 2.8939 | -0.0033753 | 7.6842e-05 | -0.0037533 | -0.058258 | 0.16331 | 0.12815 | -0.0069982 | 0.056678 | 0.10286 | -0.0027173 | 0.022888 | 0.054932 | -0.041199 | 0.032043 | 0.15564 | 0.07782 | 0.11444 | 0.66376 | 59.8389 | -62.8647 | 60.0082 | 60.0998 | 59.9258 | 0.39825 | 62.7777 | -59.816 | -59.8389 | 62.9745 | 62.9333 | 62.8967 | 0.15564 | 0.11902 | -0.045776 | -0.032044 | 0.13733 | 122.9187 | 63.2172 | 122.7448 | 63.2629 | 122.7905 | 0.19684 | 0.073242 | 122.9645 | 122.8729 | 0.096131 | 122.7036 | 62.8738 | 122.6578 | -59.9121 | -122.7356 | 62.851 | 122.8271 | 62.8418 | 63.4827
1936.8906 | 123.0011 | -62.8555 | 59.848 | -0.090943 | -0.00015586 | -0.0094187 | 2.8937 | 0.00068369 | 0.00093144 | -0.00012167 | -0.12845 | 0.16138 | 0.12516 | -0.0022986 | 0.055397 | 0.1065 | 0.0021961 | -0.041199 | -0.036621 | -0.15106 | -0.073242 | 0.036621 | -0.082397 | -0.022888 | 0.52643 | 59.7794 | -62.8555 | 59.8297 | 60.1135 | 59.9945 | 0.36163 | 62.7045 | -59.8846 | -59.9213 | 62.8922 | 62.8326 | 62.7731 | 0.12817 | 0.068665 | 0 | -0.068664 | -0.01831 | 122.9691 | 63.2172 | 122.85 | 63.2172 | 122.85 | 0.18768 | 0.07782 | 122.9691 | 122.6852 | 0.11444 | 122.6349 | 62.8189 | 122.6349 | -59.9991 | -122.7036 | 62.7823 | 122.6852 | 62.8143 | 63.382
1937.8281 | 123.0194 | -62.8235 | 59.8709 | -0.13672 | -0.00036966 | -0.0087777 | 2.8939 | 0.00089729 | -0.00077756 | -0.0026853 | -0.085724 | 0.16138 | 0.12538 | 0.0011194 | 0.057533 | 0.10393 | 0.0011279 | -0.054932 | 0.068665 | -0.068665 | -0.050354 | 0.068665 | -0.041199 | 0.022888 | 0.52185 | 59.8068 | -62.8693 | 59.9167 | 60.0174 | 59.8526 | 0.32959 | 62.7548 | -59.8022 | -59.9213 | 62.8922 | 62.8464 | 62.7823 | 0.091553 | 0.027466 | -0.045777 | -0.064087 | 0.045776 | 122.8409 | 63.1531 | 122.6761 | 63.1989 | 122.7219 | 0.13733 | 0.018311 | 122.8867 | 122.7859 | 0.13733 | 122.6761 | 62.8922 | 122.6303 | -59.9396 | -122.7402 | 62.7731 | 122.7402 | 62.7686 | 63.3453
1938.8906 | 122.9874 | -62.8693 | 59.848 | -0.052796 | -0.0020785 | -0.0087777 | 2.8918 | 0.00068369 | -0.00056396 | -0.00054907 | -0.17422 | 0.16416 | 0.12687 | -0.00016245 | 0.056465 | 0.10457 | -0.0018629 | -0.11902 | 0.004578 | -0.15106 | -0.13275 | -0.045776 | -0.16022 | -0.086975 | 0.43488 | 59.8297 | -62.8922 | 59.9167 | 59.9625 | 59.7794 | 0.20599 | 62.7182 | -59.8434 | -59.9808 | 62.8235 | 62.7823 | 62.709 | 0.064087 | -0.009155 | -0.022888 | -0.01831 | 0.068665 | 122.8317 | 63.0753 | 122.6486 | 63.0981 | 122.6715 | 0.10529 | 0.018311 | 122.8546 | 122.8088 | 0.15564 | 122.7219 | 62.8738 | 122.699 | -59.9991 | -122.7402 | 62.7365 | 122.7859 | 62.7502 | 63.3041
1939.8281 | 123.0423 | -62.8189 | 59.8389 | 0.00824 | -0.0027195 | -0.0074961 | 2.8926 | 0.00046989 | -0.0020594 | -0.0011899 | -0.058258 | 0.16245 | 0.12773 | -0.0059302 | 0.057533 | 0.1035 | -0.0022901 | -0.027466 | 0.032043 | -0.064087 | -0.018311 | 0.09613 | 0.018311 | 0.068665 | 0.5722 | 59.816 | -62.8372 | 59.967 | 60.0586 | 59.8801 | 0.35706 | 62.7548 | -59.8068 | -59.8572 | 62.915 | 62.8876 | 62.8372 | 0.13275 | 0.082398 | -0.01831 | -0.022888 | 0.12817 | 122.8775 | 63.176 | 122.699 | 63.1943 | 122.7173 | 0.16022 | 0.045776 | 122.8958 | 122.8043 | 0.09613 | 122.6532 | 62.851 | 122.6349 | -59.903 | -122.6761 | 62.8006 | 122.7859 | 62.7914 | 63.3911
1940.8906 | 122.9004 | -62.851 | 59.9075 | -0.045166 | -0.0014377 | -0.0094187 | 2.8945 | 0.0013245 | -0.00035036 | -0.0014035 | -0.18033 | 0.16331 | 0.12687 | -0.0027258 | 0.056678 | 0.10564 | -0.0029309 | -0.054932 | 0.036621 | -0.09613 | -0.10986 | -0.041199 | -0.13275 | -0.07782 | 0.42572 | 59.8526 | -62.8922 | 59.848 | 59.9167 | 59.7198 | 0.21057 | 62.7548 | -59.8709 | -60.0174 | 62.8098 | 62.7731 | 62.7182 | 0.01831 | -0.036621 | -0.041199 | -0.054932 | -0.05951 | 122.7676 | 63.0615 | 122.5708 | 63.1027 | 122.612 | 0.054931 | -0.013733 | 122.8088 | 122.7402 | 0.13275 | 122.7448 | 62.8876 | 122.7036 | -60.0037 | -122.7997 | 62.7411 | 122.699 | 62.796 | 63.2767
1941.8281 | 122.9919 | -62.8281 | 59.8618 | -0.060425 | -0.0031467 | -0.0087777 | 2.8928 | -0.0040161 | -0.0029138 | -0.00054907 | -0.064362 | 0.1616 | 0.12901 | -0.0087072 | 0.055824 | 0.10393 | -0.0014355 | -0.027466 | 0.018311 | -0.091553 | -0.036621 | 0.064087 | -0.027466 | 0.022888 | 0.52643 | 59.816 | -62.8601 | 59.9625 | 60.0311 | 59.8755 | 0.34332 | 62.7365 | -59.8434 | -59.8984 | 62.8922 | 62.851 | 62.8006 | 0.11444 | 0.064087 | -0.032043 | -0.045776 | 0.10071 | 122.8592 | 63.1714 | 122.7036 | 63.2034 | 122.7356 | 0.15564 | 0.054932 | 122.8912 | 122.8226 | 0.10986 | 122.6761 | 62.8464 | 122.644 | -59.9533 | -122.7219 | 62.7914 | 122.7905 | 62.8006 | 63.3545
1942.9062 | 123.0011 | -62.851 | 59.8801 | -0.037537 | -0.0018649 | -0.0081369 | 2.8937 | -0.0014527 | 0.00093144 | -0.0016171 | -0.10403 | 0.16331 | 0.12815 | -0.0069982 | 0.056465 | 0.10286 | 0.00027333 | -0.041199 | 0.009155 | -0.10071 | -0.064087 | 0.027466 | -0.054932 | 0.004578 | 0.49439 | 59.7977 | -62.8464 | 59.8709 | 60.0311 | 59.8068 | 0.27924 | 62.7502 | -59.8709 | -59.9442 | 62.8784 | 62.8555 | 62.796 | 0.10529 | 0.045776 | 0.004577 | -0.082398 | -0.009155 | 122.8821 | 63.1302 | 122.6578 | 63.1256 | 122.6532 | 0.12817 | 0.036621 | 122.8775 | 122.7173 | 0.10986 | 122.644 | 62.8601 | 122.6486 | -59.9808 | -122.7264 | 62.7869 | 122.7219 | 62.8098 | 63.3453
1943.8281 | 123.024 | -62.8418 | 59.8801 | -0.029907 | -0.0010105 | -0.0087777 | 2.893 | -0.00017091 | 0.0026404 | -0.0026853 | -0.094879 | 0.1616 | 0.12602 | -0.0061438 | 0.054115 | 0.105 | -0.0025037 | -0.022888 | 0.032043 | -0.082397 | -0.073242 | 0.032043 | -0.059509 | 0.004578 | 0.49439 | 59.8022 | -62.8693 | 59.935 | 60.0266 | 59.848 | 0.32044 | 62.7594 | -59.848 | -59.9533 | 62.8738 | 62.8464 | 62.7823 | 0.086975 | 0.022888 | -0.027466 | -0.07782 | 0.054932 | 122.8683 | 63.1622 | 122.6898 | 63.1897 | 122.7173 | 0.11444 | 0.009155 | 122.8958 | 122.8043 | 0.11444 | 122.6715 | 62.8738 | 122.644 | -59.9625 | -122.7493 | 62.7686 | 122.7768 | 62.8189 | 63.3362
1944.8906 | 123.024 | -62.8189 | 59.8434 | -0.045166 | -0.0022923 | -0.0083505 | 2.8952 | 0.0049561 | -0.00099116 | -0.00097627 | -0.15591 | 0.16245 | 0.1273 | 0.001333 | 0.055824 | 0.10543 | -0.00058107 | -0.086975 | -0.027466 | -0.14648 | -0.073242 | 0.027466 | -0.10529 | -0.041199 | 0.48981 | 59.7748 | -62.8876 | 59.9762 | 60.0266 | 59.8343 | 0.27466 | 62.6724 | -59.8709 | -59.9167 | 62.8464 | 62.7777 | 62.7136 | 0.10529 | 0.041198 | -0.068664 | -0.068665 | 0.13275 | 122.8455 | 63.0936 | 122.6532 | 63.1622 | 122.7219 | 0.17395 | 0.073242 | 122.9141 | 122.8638 | 0.11902 | 122.6624 | 62.7914 | 122.5937 | -59.9899 | -122.731 | 62.7457 | 122.7951 | 62.7319 | 63.3087
1945.8281 | 122.9828 | -62.8555 | 59.8572 | -0.1062 | -0.0018649 | -0.0094187 | 2.8926 | -0.0025207 | -0.00013676 | -0.00033547 | -0.064362 | 0.16267 | 0.1288 | -0.0069982 | 0.055397 | 0.10286 | -0.0012219 | -0.045776 | 0.027466 | -0.091553 | -0.054932 | 0.027466 | -0.054932 | 0 | 0.49439 | 59.8297 | -62.8693 | 59.9304 | 59.9899 | 59.8297 | 0.3067 | 62.764 | -59.8297 | -59.9121 | 62.883 | 62.8555 | 62.8006 | 0.091553 | 0.036621 | -0.013733 | -0.027466 | 0.073242 | 122.8455 | 63.1622 | 122.6852 | 63.176 | 122.699 | 0.11902 | 0.036621 | 122.8592 | 122.7997 | 0.11902 | 122.699 | 62.883 | 122.6852 | -59.9487 | -122.7264 | 62.8006 | 122.7859 | 62.8098 | 63.3499
1946.8906 | 122.937 | -62.8601 | 59.848 | -0.052796 | -0.0018649 | -0.010059 | 2.8943 | -0.00017091 | -0.00035036 | 0.00051913 | -0.17728 | 0.16416 | 0.12602 | -0.0022986 | 0.05561 | 0.10393 | 0.0013415 | -0.004578 | 0.004578 | -0.16479 | -0.16937 | -0.068665 | -0.17853 | -0.11444 | 0.40741 | 59.8709 | -62.8922 | 59.8846 | 59.9258 | 59.7473 | 0.21057 | 62.6953 | -59.8434 | -60.0174 | 62.7914 | 62.7457 | 62.6816 | 0.050354 | -0.013733 | -0.032044 | 0.022889 | 0.036622 | 122.7859 | 63.0707 | 122.6074 | 63.1027 | 122.6395 | 0.09613 | -0.004578 | 122.818 | 122.7768 | 0.16937 | 122.7631 | 62.8647 | 122.731 | -60.0128 | -122.7402 | 62.6907 | 122.7448 | 62.8555 | 63.2675
1947.8281 | 123.0057 | -62.851 | 59.8618 | -0.068054 | 0.00069854 | -0.0092051 | 2.8918 | 0.0011109 | -0.0020594 | 0.00073273 | -0.042999 | 0.16288 | 0.12709 | -0.0022986 | 0.057533 | 0.10479 | -0.0035719 | -0.054932 | 0.054932 | -0.07782 | -0.032043 | 0.059509 | -0.041199 | 0.027466 | 0.52185 | 59.8389 | -62.8784 | 59.9442 | 60.0266 | 59.8572 | 0.33875 | 62.7731 | -59.8068 | -59.8938 | 62.9105 | 62.8784 | 62.8098 | 0.10529 | 0.036621 | -0.027466 | -0.022888 | 0.082398 | 122.8775 | 63.1897 | 122.7081 | 63.2172 | 122.7356 | 0.13733 | 0.045777 | 122.905 | 122.8226 | 0.13275 | 122.7173 | 62.9059 | 122.6898 | -59.9396 | -122.7402 | 62.8189 | 122.7951 | 62.796 | 63.3728
1948.8906 | 122.9874 | -62.8601 | 59.8618 | -0.045166 | -0.00015586 | -0.0094187 | 2.8941 | -0.0012391 | -0.00035036 | 0.00094633 | -0.14066 | 0.16224 | 0.12709 | -0.0018712 | 0.053901 | 0.10521 | -0.0042127 | -0.10529 | 0.004578 | -0.13733 | -0.11902 | -0.059509 | -0.16937 | -0.10529 | 0.41199 | 59.816 | -62.8876 | 59.9396 | 59.9716 | 59.7794 | 0.21973 | 62.7228 | -59.8572 | -59.9808 | 62.8006 | 62.7548 | 62.6907 | 0.032043 | -0.032044 | -0.027466 | -0.045776 | 0.07782 | 122.8317 | 63.0798 | 122.6395 | 63.1073 | 122.6669 | 0.07782 | 0.01831 | 122.8592 | 122.8271 | 0.14191 | 122.7036 | 62.8647 | 122.6761 | -59.9991 | -122.7493 | 62.7411 | 122.7997 | 62.7548 | 63.2721
1949.8281 | 123.056 | -62.8372 | 59.8572 | -0.060425 | -0.0022923 | -0.010487 | 2.8926 | 0.0034607 | -0.0029138 | -0.0031125 | -0.049103 | 0.16202 | 0.12751 | -0.0016576 | 0.057747 | 0.105 | -0.0035719 | 0 | 0.045776 | -0.068665 | 0.009155 | 0.10071 | 0.022888 | 0.064087 | 0.57678 | 59.8114 | -62.8418 | 59.9716 | 60.0632 | 59.8938 | 0.36163 | 62.7686 | -59.8114 | -59.848 | 62.9379 | 62.9013 | 62.8601 | 0.13275 | 0.091553 | -0.004578 | -0.045777 | 0.11444 | 122.9004 | 63.1989 | 122.731 | 63.2034 | 122.7356 | 0.16937 | 0.07782 | 122.905 | 122.8134 | 0.11444 | 122.6532 | 62.883 | 122.6486 | -59.9258 | -122.699 | 62.8464 | 122.8088 | 62.8372 | 63.414
1950.8906 | 122.9782 | -62.8326 | 59.8846 | 0.00061049 | 0.00048494 | -0.0098459 | 2.8913 | 0.0030335 | -0.00013676 | 9.193e-05 | -0.16507 | 0.16309 | 0.12474 | -0.0063574 | 0.055824 | 0.10735 | -0.0018629 | 0.032043 | 0.14648 | -0.041199 | -0.013733 | 0.068665 | 0.009155 | 0.032043 | 0.54932 | 59.8801 | -62.8693 | 59.9075 | 59.9991 | 59.8206 | 0.35706 | 62.7914 | -59.7382 | -59.8984 | 62.9013 | 62.8647 | 62.8418 | 0.073242 | 0.050354 | -0.036621 | -0.004578 | 0.022888 | 122.8317 | 63.1897 | 122.6532 | 63.2263 | 122.6898 | 0.10986 | 0.027466 | 122.8683 | 122.7768 | 0.18768 | 122.7493 | 62.9791 | 122.7127 | -59.9258 | -122.7539 | 62.8189 | 122.7402 | 62.8647 | 63.382
1951.8281 | 123.0011 | -62.8464 | 59.848 | -0.060425 | -0.0020785 | -0.0087777 | 2.8926 | -0.0050843 | -0.00035036 | -0.0028989 | -0.055206 | 0.16288 | 0.12431 | -0.003153 | 0.058174 | 0.10308 | 0.0024097 | -0.045776 | 0.032043 | -0.091553 | -0.068665 | 0.018311 | -0.064087 | -0.009155 | 0.48065 | 59.8206 | -62.8281 | 59.9258 | 60.0082 | 59.7748 | 0.39368 | 62.7548 | -59.816 | -59.9167 | 62.8647 | 62.8372 | 62.7823 | 0.082398 | 0.027466 | 0.018311 | -0.027465 | 0.07782 | 122.8546 | 63.2401 | 122.6212 | 63.2217 | 122.6028 | 0.10986 | 0.022888 | 122.8363 | 122.7539 | 0.1236 | 122.6486 | 62.8784 | 122.6669 | -59.9396 | -122.6761 | 62.7777 | 122.7722 | 62.8006 | 63.327
1952.8281 | 122.9095 | -62.8052 | 59.8663 | 0.015869 | -0.0016513 | -0.0092051 | 2.892 | -0.0038025 | -0.00035036 | -0.00012167 | -0.076569 | 0.16331 | 0.12773 | -0.0067846 | 0.058601 | 0.10543 | -0.0033581 | 0.059509 | 0.082397 | -0.027466 | 0.059509 | 0.17395 | 0.073242 | 0.10529 | 0.67291 | 59.8114 | -62.8372 | 59.9854 | 60.1501 | 60.1593 | 0.66834 | 62.7777 | -59.7839 | -59.8068 | 62.9791 | 62.9105 | 62.8784 | 0.13275 | 0.10071 | -0.032043 | -0.054932 | 0.11902 | 122.9553 | 63.4735 | 122.9645 | 63.5056 | 122.9965 | 0.20142 | 0.086975 | 122.9874 | 122.8226 | 0.10986 | 122.6486 | 62.8876 | 122.6166 | -59.8938 | -122.7036 | 62.8647 | 122.7905 | 62.8647 | 63.4781
1953.8281 | 123.0194 | -62.8281 | 59.8984 | -0.045166 | -0.0020785 | -0.0085641 | 2.8918 | -0.0010253 | -0.0041956 | -0.0031125 | -0.07962 | 0.16074 | 0.12602 | -0.001444 | 0.054329 | 0.10436 | 5.9726e-05 | -0.022888 | 0.032043 | -0.082397 | 0.1236 | -0.059509 | -0.10071 | -0.009155 | 0.50812 | 59.816 | -62.8738 | 59.935 | 60.0082 | 59.8434 | 0.32044 | 62.7457 | -59.8663 | -59.7748 | 62.7686 | 62.8189 | 62.7274 | 0.073242 | -0.018311 | -0.045776 | -0.082397 | 0.036622 | 122.8363 | 63.1485 | 122.6715 | 63.1943 | 122.7173 | 0.022888 | 0.20599 | 122.8821 | 122.8088 | 0.11444 | 122.6898 | 62.8601 | 122.644 | -59.9808 | -122.7722 | 62.9517 | 122.7631 | 62.8052 | 63.3362
1954.8906 | 122.9187 | -62.8647 | 59.903 | -0.045166 | -0.0018649 | -0.0079233 | 2.8947 | 0.0049561 | -0.0016322 | 0.0022281 | -0.19254 | 0.16437 | 0.12709 | 5.1352e-05 | 0.056892 | 0.10735 | -0.00079467 | -0.054932 | 0.045776 | -0.11902 | -0.10986 | -0.018311 | -0.14648 | -0.10071 | 0.40283 | 59.8526 | -62.8876 | 59.8526 | 59.9258 | 59.7198 | 0.20142 | 62.7457 | -59.8572 | -60.0128 | 62.8464 | 62.764 | 62.7182 | 0.018311 | -0.027465 | -0.022888 | -0.050354 | -0.050354 | 122.7905 | 63.0661 | 122.5845 | 63.089 | 122.6074 | 0.10071 | 0.009156 | 122.8134 | 122.7402 | 0.16479 | 122.7402 | 62.9105 | 122.7173 | -60.022 | -122.7905 | 62.7548 | 122.7173 | 62.8098 | 63.2675
1955.8281 | 122.9828 | -62.8464 | 59.8709 | -0.045166 | -0.0031467 | -0.0070687 | 2.8928 | 0.0019653 | 7.6842e-05 | -0.0014035 | -0.064362 | 0.16373 | 0.12751 | -0.0046484 | 0.058174 | 0.10372 | -0.0022901 | -0.045776 | 0.013733 | -0.09613 | -0.045776 | 0.022888 | -0.073242 | -0.004578 | 0.48065 | 59.8114 | -62.8922 | 59.9304 | 60.0037 | 59.8251 | 0.26093 | 62.7502 | -59.8572 | -59.9167 | 62.8693 | 62.8418 | 62.7731 | 0.091552 | 0.022888 | -0.045776 | -0.05951 | 0.059509 | 122.85 | 63.1073 | 122.6715 | 63.1531 | 122.7173 | 0.11902 | 0.050354 | 122.8958 | 122.8226 | 0.10986 | 122.7036 | 62.8601 | 122.6578 | -59.967 | -122.7631 | 62.8006 | 122.7768 | 62.8006 | 63.327
1956.8906 | 122.9553 | -62.8326 | 59.9121 | -0.007019 | -0.0010105 | -0.0085641 | 2.8939 | 0.00089729 | -0.0020594 | -0.0031125 | -0.17117 | 0.16416 | 0.1273 | -0.00016245 | 0.054329 | 0.10778 | -0.0033581 | 0 | 0.082397 | -0.073242 | -0.036621 | 0.036621 | -0.064087 | -0.022888 | 0.51727 | 59.8709 | -62.9059 | 59.9304 | 59.9762 | 59.7931 | 0.3067 | 62.7594 | -59.8297 | -59.9487 | 62.8693 | 62.8098 | 62.7686 | 0.050354 | 0.009155 | -0.073242 | -0.041198 | 0.018311 | 122.8088 | 63.1393 | 122.6257 | 63.2126 | 122.699 | 0.10986 | 0.036621 | 122.8821 | 122.8363 | 0.15564 | 122.7768 | 62.915 | 122.7036 | -59.9854 | -122.818 | 62.796 | 122.7631 | 62.8326 | 63.3499
1957.8281 | 122.9782 | -62.8555 | 59.8663 | -0.029907 | -0.0014377 | -0.0077097 | 2.8941 | 0.00068369 | -0.00035036 | -0.0018307 | -0.073517 | 0.16224 | 0.12837 | -0.0061438 | 0.057747 | 0.10265 | -0.0022901 | -0.068665 | -0.022888 | -0.10986 | -0.073242 | 0.027466 | -0.091553 | -0.032043 | 0.47607 | 59.7794 | -62.8738 | 59.9213 | 60.0082 | 59.8251 | 0.26093 | 62.7457 | -59.8892 | -59.9396 | 62.883 | 62.8235 | 62.764 | 0.07782 | 0.01831 | -0.01831 | -0.086975 | 0.054932 | 122.8638 | 63.1165 | 122.6807 | 63.1348 | 122.699 | 0.13733 | 0.036621 | 122.8821 | 122.7951 | 0.086975 | 122.6532 | 62.8326 | 122.6349 | -59.9762 | -122.7402 | 62.7823 | 122.7768 | 62.7869 | 63.3316
1958.8906 | 122.9187 | -62.8464 | 59.9304 | -0.007019 | -0.0022923 | -0.0096323 | 2.8926 | 0.0026063 | -0.0020594 | -0.0020443 | -0.21695 | 0.16459 | 0.12815 | -0.0067846 | 0.05796 | 0.10308 | -0.00015387 | 0.013733 | 0.14648 | -0.027466 | -0.018311 | 0.009155 | 0.48065 | 0.37537 | 0.54932 | 59.8663 | -62.915 | 59.8892 | 59.9762 | 59.7748 | 0.32044 | 62.8189 | -59.7839 | -59.9487 | 62.8555 | 63.2217 | 63.327 | 0.40283 | 0.50812 | -0.068664 | -0.064087 | -0.041199 | 122.8226 | 63.1668 | 122.6212 | 63.2355 | 122.6898 | 0.036621 | 0.009155 | 122.8912 | 122.8043 | 0.17395 | 122.7814 | 62.9929 | 122.7127 | -59.9579 | -122.8455 | 62.8281 | 122.7356 | 62.8601 | 63.3957
1959.8281 | 123.0057 | -62.8601 | 59.8434 | -0.11383 | -0.0018649 | -0.0085641 | 2.8896 | -0.0016663 | -0.0016322 | -0.0026853 | -0.082672 | 0.16074 | 0.12858 | -0.0067846 | 0.057106 | 0.10393 | 0.0032641 | -0.041199 | -0.004578 | -0.10986 | -0.050354 | 0.054932 | -0.073242 | -0.018311 | 0.52643 | 59.7885 | -62.8693 | 59.9258 | 59.9991 | 59.8434 | 0.24719 | 62.7502 | -59.848 | -59.8938 | 62.915 | 62.8418 | 62.7869 | 0.091552 | 0.036621 | -0.009156 | -0.054932 | 0.082397 | 122.8592 | 63.1073 | 122.7036 | 63.1165 | 122.7127 | 0.16479 | 0.059509 | 122.8683 | 122.7951 | 0.10529 | 122.6578 | 62.8555 | 122.6486 | -59.9533 | -122.7127 | 62.8098 | 122.7859 | 62.8189 | 63.3865
1960.8906 | 122.9187 | -62.851 | 59.8938 | 0.015869 | -0.0018649 | -0.0089913 | 2.8952 | 0.0041015 | -0.0027002 | -0.0039671 | -0.18338 | 0.16373 | 0.12922 | 0.0034692 | 0.056892 | 0.10521 | -0.0033581 | -0.10529 | 0.027466 | -0.14191 | -0.16022 | -0.11444 | -0.19684 | -0.11444 | 0.36163 | 59.8389 | -62.9242 | 59.9991 | 59.9167 | 59.7153 | 0.20142 | 62.709 | -59.8663 | -60.054 | 62.7365 | 62.7365 | 62.6541 | 0.027466 | -0.054931 | -0.073242 | -0.054932 | 0.10529 | 122.7676 | 63.0524 | 122.5662 | 63.1256 | 122.6395 | 0.027466 | -0.01831 | 122.8409 | 122.9233 | 0.16937 | 122.7631 | 62.8784 | 122.6898 | -60.0357 | -122.818 | 62.6907 | 122.85 | 62.7457 | 63.2126
1961.8281 | 123.0057 | -62.851 | 59.8434 | -0.075684 | -0.00079686 | -0.0066415 | 2.8909 | -0.00081171 | -0.00099116 | -0.0016171 | -0.076569 | 0.16202 | 0.12815 | -0.0046484 | 0.056251 | 0.10222 | 0.0026233 | -0.059509 | -0.018311 | -0.10071 | -0.059509 | 0.041199 | -0.086975 | -0.022888 | 0.48065 | 59.7839 | -62.9013 | 59.9213 | 59.9899 | 59.7885 | 0.23804 | 62.7502 | -59.8618 | -59.903 | 62.8922 | 62.8281 | 62.764 | 0.07782 | 0.013733 | -0.050354 | -0.059509 | 0.07782 | 122.8409 | 63.089 | 122.6395 | 63.1393 | 122.6898 | 0.14191 | 0.041199 | 122.8912 | 122.8226 | 0.082397 | 122.6852 | 62.8326 | 122.6349 | -59.9442 | -122.7448 | 62.7914 | 122.7722 | 62.7914 | 63.3316
1962.8906 | 123.0286 | -62.8372 | 59.8846 | -0.075684 | -0.0046421 | -0.0081369 | 2.8933 | -0.00059811 | -0.00099116 | 9.193e-05 | -0.042999 | 0.1616 | 0.12666 | -0.0072118 | 0.056465 | 0.1035 | -0.0035719 | -0.009155 | 0.032043 | -0.091553 | 0.004578 | 0.09613 | 0.009155 | 0.068665 | 0.58136 | 59.8068 | -62.851 | 59.9716 | 60.0494 | 59.8892 | 0.36163 | 62.7457 | -59.8526 | -59.8801 | 62.9333 | 62.9059 | 62.8464 | 0.16022 | 0.10071 | -0.013733 | -0.07782 | 0.086975 | 122.8867 | 63.1989 | 122.7264 | 63.2126 | 122.7402 | 0.18768 | 0.096131 | 122.9004 | 122.8226 | 0.1236 | 122.6578 | 62.8693 | 122.644 | -59.9762 | -122.7356 | 62.8418 | 122.8088 | 62.8281 | 63.4186
1963.8281 | 122.9919 | -62.851 | 59.8663 | -0.090943 | -0.0031467 | -0.0096323 | 2.893 | 0.0011109 | -0.0018458 | -0.0018307 | -0.091827 | 0.16117 | 0.12751 | -0.0033666 | 0.056465 | 0.105 | 0.00091433 | -0.068665 | -0.022888 | -0.10986 | -0.059509 | 0.032043 | -0.091553 | -0.032043 | 0.48523 | 59.7931 | -62.8784 | 59.9167 | 59.9991 | 59.8022 | 0.26093 | 62.7411 | -59.8892 | -59.9258 | 62.883 | 62.8189 | 62.7594 | 0.07782 | 0.01831 | -0.027466 | -0.073242 | 0.050354 | 122.85 | 63.1119 | 122.6532 | 63.1393 | 122.6807 | 0.14191 | 0.050354 | 122.8775 | 122.7951 | 0.086975 | 122.6715 | 62.8281 | 122.644 | -59.9762 | -122.7448 | 62.7914 | 122.7676 | 62.7823 | 63.3362
1964.8906 | 122.905 | -62.8784 | 59.8801 | -0.075684 | 0.00027134 | -0.0087777 | 2.8943 | 0.0060241 | -0.0014184 | -0.00097627 | -0.16202 | 0.16267 | 0.1273 | -0.0016576 | 0.055397 | 0.105 | -0.0020765 | -0.07782 | 0.036621 | -0.11902 | -0.13733 | -0.07782 | -0.16479 | -0.10071 | 0.37079 | 59.848 | -62.9105 | 59.8572 | 59.8663 | 59.6924 | 0.16479 | 62.7594 | -59.8434 | -60.0174 | 62.8006 | 62.7777 | 62.7136 | 0.018311 | -0.045776 | -0.032043 | -0.032044 | -0.022888 | 122.7448 | 63.0432 | 122.5708 | 63.0753 | 122.6028 | 0.041199 | -0.01831 | 122.7768 | 122.7676 | 0.15564 | 122.7585 | 62.915 | 122.7264 | -59.9991 | -122.7905 | 62.7411 | 122.7356 | 62.8006 | 63.2492
1965.8281 | 122.9874 | -62.8418 | 59.8572 | -0.068054 | -0.0018649 | -0.0085641 | 2.892 | -0.00059811 | 0.00050424 | -0.0039671 | -0.076569 | 0.16331 | 0.1273 | -0.0059302 | 0.05796 | 0.10393 | -0.0031445 | -0.059509 | -0.027466 | -0.10986 | -0.068665 | 0.018311 | -0.09613 | -0.009155 | 0.46692 | 59.8022 | -62.8967 | 59.9304 | 59.9854 | 59.8206 | 0.25635 | 62.7319 | -59.8846 | -59.9258 | 62.8601 | 62.8326 | 62.7457 | 0.10071 | 0.013733 | -0.054932 | -0.054932 | 0.073242 | 122.8271 | 63.0981 | 122.6624 | 63.1531 | 122.7173 | 0.12817 | 0.041198 | 122.8821 | 122.8271 | 0.082397 | 122.699 | 62.8143 | 122.644 | -59.967 | -122.7539 | 62.7731 | 122.7722 | 62.7823 | 63.3087
1966.8906 | 122.9553 | -62.8693 | 59.8846 | 0.00061049 | 5.7742e-05 | -0.0087777 | 2.8945 | 0.00089729 | -0.0018458 | -0.0035397 | -0.14676 | 0.1616 | 0.12687 | 0.00026495 | 0.057106 | 0.105 | -0.0018629 | 0.018311 | 0.11902 | -0.036621 | -0.013733 | 0.059509 | -0.027466 | 0.032043 | 0.57678 | 59.8709 | -62.8555 | 59.9258 | 59.9991 | 59.8114 | 0.3479 | 62.8326 | -59.7656 | -59.8984 | 62.9288 | 62.9013 | 62.8418 | 0.068664 | 0.009155 | 0.013733 | -0.013733 | 0.041198 | 122.8683 | 63.2172 | 122.6807 | 63.2034 | 122.6669 | 0.09613 | 0.022888 | 122.8546 | 122.7814 | 0.15564 | 122.7264 | 62.9883 | 122.7402 | -59.9213 | -122.7402 | 62.8555 | 122.7951 | 62.8876 | 63.446
1967.8438 | 122.9828 | -62.8326 | 59.8892 | 0.00824 | -0.0027195 | -0.0092051 | 2.8926 | -0.00017091 | -0.0012048 | 0.00030553 | -0.070465 | 0.16416 | 0.12965 | -0.0069982 | 0.058174 | 0.10436 | -0.0031445 | 0.064087 | 0.086975 | -0.027466 | 0.045776 | 0.13275 | 0.054932 | 0.07782 | 0.60425 | 59.8434 | -62.8555 | 59.9304 | 60.0174 | 59.8434 | 0.37994 | 62.8052 | -59.8022 | -59.8434 | 62.9654 | 62.9105 | 62.8876 | 0.10529 | 0.082398 | -0.022888 | -0.045776 | 0.041199 | 122.85 | 63.2126 | 122.6761 | 63.2355 | 122.699 | 0.16022 | 0.073242 | 122.8729 | 122.7859 | 0.11444 | 122.699 | 62.9196 | 122.6761 | -59.9167 | -122.7448 | 62.8784 | 122.7631 | 62.8967 | 63.4369
1968.8906 | 122.9187 | -62.8601 | 59.9121 | 0.00061049 | -0.0016513 | -0.0068551 | 2.8939 | 4.2692e-05 | -0.0016322 | -0.0018307 | -0.17117 | 0.16416 | 0.12602 | 0.0038966 | 0.056251 | 0.10628 | -0.00058107 | -0.036621 | 0.050354 | -0.09613 | -0.082397 | -0.013733 | -0.11444 | -0.064087 | 0.46692 | 59.848 | -62.8967 | 59.8755 | 59.9258 | 59.7519 | 0.24719 | 62.764 | -59.8618 | -59.9945 | 62.8464 | 62.796 | 62.7457 | 0.032043 | -0.018311 | -0.036622 | -0.064087 | -0.036621 | 122.7859 | 63.1073 | 122.612 | 63.1439 | 122.6486 | 0.082397 | 0.013733 | 122.8226 | 122.7722 | 0.14648 | 122.7448 | 62.9105 | 122.7081 | -60.0082 | -122.8088 | 62.7777 | 122.7356 | 62.8235 | 63.327
1969.8281 | 123.0377 | -62.8372 | 59.8526 | -0.068054 | -0.0010105 | -0.0066415 | 2.8943 | 0.0017517 | -0.0027002 | -0.0011899 | -0.12845 | 0.16245 | 0.12687 | -0.00080325 | 0.054969 | 0.10564 | -0.0037855 | -0.091553 | 0.004578 | -0.14648 | -0.10529 | -0.032043 | -0.15106 | -0.073242 | 0.46234 | 59.7977 | -62.8922 | 59.9442 | 60.0174 | 59.8297 | 0.26093 | 62.6907 | -59.848 | -59.9579 | 62.8052 | 62.764 | 62.6862 | 0.073242 | -0.004578 | -0.054932 | -0.054932 | 0.091553 | 122.8546 | 63.0981 | 122.6669 | 63.1531 | 122.7219 | 0.11444 | 0.041198 | 122.9095 | 122.8363 | 0.15106 | 122.6898 | 62.8418 | 122.6349 | -59.9991 | -122.7448 | 62.7319 | 122.7814 | 62.7457 | 63.2996
1970.8906 | 122.9782 | -62.851 | 59.8755 | 0.00061049 | 0.00048494 | -0.0079233 | 2.895 | 0.00089729 | -0.00077756 | -0.0022581 | -0.12845 | 0.16331 | 0.12837 | -0.004862 | 0.056465 | 0.10628 | -0.0020765 | 0.045776 | 0.09613 | -0.064087 | -0.022888 | 0.073242 | -0.041199 | 0.013733 | 0.55847 | 59.8801 | -62.8647 | 59.9213 | 60.0037 | 59.8022 | 0.33875 | 62.7869 | -59.7794 | -59.8984 | 62.9242 | 62.8647 | 62.8098 | 0.07782 | 0.022888 | -0.013733 | 0.004578 | 0.045777 | 122.8546 | 63.1897 | 122.6532 | 63.2034 | 122.6669 | 0.13733 | 0.041199 | 122.8683 | 122.7859 | 0.16022 | 122.7448 | 62.9471 | 122.731 | -59.9396 | -122.7402 | 62.8281 | 122.7722 | 62.8967 | 63.4094
1971.8281 | 123.0652 | -62.8372 | 59.8343 | -0.098572 | -0.0014377 | -0.0070687 | 2.8928 | 4.2692e-05 | -0.0018458 | -0.00033547 | -0.097931 | 0.16224 | 0.12559 | -0.0044348 | 0.057533 | 0.1065 | -0.0012219 | -0.086975 | -0.004578 | -0.14191 | -0.11902 | -0.041199 | -0.10529 | -0.022888 | 0.49896 | 59.7931 | -62.8876 | 59.9579 | 60.0266 | 59.848 | 0.27008 | 62.6953 | -59.8389 | -59.9533 | 62.796 | 62.8143 | 62.7319 | 0.11902 | 0.036621 | -0.050354 | -0.041199 | 0.1236 | 122.8638 | 63.1073 | 122.6852 | 63.1577 | 122.7356 | 0.10071 | 0.022888 | 122.9141 | 122.8455 | 0.13733 | 122.6807 | 62.8326 | 122.6303 | -59.9762 | -122.7219 | 62.7182 | 122.7951 | 62.7502 | 63.3362
1972.8438 | 123.0515 | -62.8098 | 59.8572 | -0.075684 | 0.00069854 | -0.0098459 | 2.892 | -0.0012391 | -0.00035036 | -0.0031125 | -0.027741 | 0.16331 | 0.1273 | -0.0078528 | 0.05796 | 0.10201 | 0.0013415 | 0.041199 | 0.054932 | -0.036621 | 0.041199 | 0.16022 | 0.041199 | 0.11444 | 0.66834 | 59.7885 | -62.851 | 60.0082 | 60.1044 | 59.9442 | 0.40283 | 62.7731 | -59.8022 | -59.816 | 62.97 | 62.9242 | 62.851 | 0.15106 | 0.07782 | -0.041199 | -0.068665 | 0.15106 | 122.9141 | 63.2126 | 122.7539 | 63.2538 | 122.7951 | 0.19684 | 0.07782 | 122.9553 | 122.8592 | 0.091553 | 122.6395 | 62.8647 | 122.5983 | -59.8938 | -122.7081 | 62.851 | 122.818 | 62.851 | 63.4781
1973.8906 | 122.905 | -62.851 | 59.9121 | -0.075684 | -0.00015586 | -0.0081369 | 2.8954 | 0.0030335 | -0.0018458 | 0.00030553 | -0.16202 | 0.16395 | 0.12815 | -0.002085 | 0.056678 | 0.1065 | -0.0029309 | -0.050354 | 0.068665 | -0.10986 | -0.086975 | -0.022888 | -0.13275 | -0.07782 | 0.45319 | 59.848 | -62.8876 | 59.8572 | 59.9121 | 59.7382 | 0.23804 | 62.7411 | -59.8434 | -59.9991 | 62.8281 | 62.7731 | 62.7182 | 0.032043 | -0.022888 | -0.036621 | -0.064087 | -0.054931 | 122.7631 | 63.089 | 122.5891 | 63.1256 | 122.6257 | 0.086975 | 0.022888 | 122.7997 | 122.7448 | 0.17853 | 122.7356 | 62.9196 | 122.699 | -60.022 | -122.7997 | 62.764 | 122.7081 | 62.8006 | 63.3041
1974.8281 | 122.9324 | -62.8738 | 59.8938 | -0.045166 | -0.0025059 | -0.0081369 | 2.8926 | 0.0023925 | -0.0027002 | 0.0013735 | -0.14066 | 0.16373 | 0.12773 | -0.0029394 | 0.054969 | 0.10692 | -0.0020765 | -0.068665 | 0.054932 | -0.11902 | -0.10071 | -0.045776 | -0.14648 | -0.091553 | 0.39825 | 59.848 | -62.883 | 59.8434 | 59.9121 | 59.7198 | 0.21973 | 62.7548 | -59.8389 | -59.9945 | 62.8281 | 62.7823 | 62.7274 | 0.027466 | -0.027465 | -0.009156 | -0.045777 | -0.050354 | 122.7859 | 63.0936 | 122.5937 | 63.1027 | 122.6028 | 0.073243 | 0.018311 | 122.7951 | 122.7264 | 0.17395 | 122.731 | 62.9288 | 122.7219 | -60.0128 | -122.7768 | 62.7731 | 122.7173 | 62.8052 | 63.2721
1975.8906 | 122.9279 | -62.851 | 59.9121 | 0.031128 | -0.00036966 | -0.0077097 | 2.8941 | 0.0017517 | -0.00077756 | -0.0011899 | -0.097931 | 0.16459 | 0.12837 | -0.0022986 | 0.057106 | 0.10415 | -0.0029309 | 0.009155 | 0.12817 | -0.032043 | -0.018311 | 0.064087 | 0 | 0.027466 | 0.54932 | 59.8709 | -62.8738 | 59.9213 | 59.9945 | 59.816 | 0.3479 | 62.8189 | -59.7839 | -59.9304 | 62.915 | 62.8784 | 62.851 | 0.059509 | 0.032043 | -0.022888 | -0.041198 | 0.009156 | 122.8455 | 63.1989 | 122.6669 | 63.2217 | 122.6898 | 0.09613 | 0.013732 | 122.8683 | 122.7951 | 0.16022 | 122.7448 | 62.9791 | 122.7219 | -59.9442 | -122.7859 | 62.8326 | 122.7722 | 62.8601 | 63.4003
1976.8281 | 122.8867 | -62.8876 | 59.9075 | -0.068054 | -0.0020785 | -0.0085641 | 2.8945 | 0.0041015 | -0.00077756 | -0.00097627 | -0.12234 | 0.16502 | 0.12709 | 0.003042 | 0.054969 | 0.10628 | -0.00079467 | -0.07782 | 0.054932 | -0.11902 | -0.13275 | -0.07782 | -0.16937 | -0.10071 | 0.37994 | 59.848 | -62.8784 | 59.8251 | 59.8709 | 59.6924 | 0.19684 | 62.7686 | -59.8526 | -60.0403 | 62.8098 | 62.7869 | 62.7182 | 0.018311 | -0.050354 | 0.009155 | -0.05951 | -0.082398 | 122.7585 | 63.0844 | 122.58 | 63.0753 | 122.5708 | 0.041199 | -0.013732 | 122.7493 | 122.7036 | 0.17395 | 122.7264 | 62.9425 | 122.7356 | -60.0266 | -122.786 | 62.7548 | 122.7127 | 62.8098 | 63.2675
1977.8906 | 122.9141 | -62.8601 | 59.9167 | 0.00061049 | -0.0010105 | -0.0081369 | 2.893 | 4.2692e-05 | -0.00035036 | -0.00033547 | -0.12234 | 0.16224 | 0.12965 | -0.0040076 | 0.056251 | 0.10543 | 0.0011279 | -0.064087 | 0.050354 | -0.10529 | -0.10986 | -0.032043 | -0.15564 | -0.11444 | 0.37994 | 59.8251 | -62.9242 | 59.8251 | 59.8846 | 59.7244 | 0.21057 | 62.7548 | -59.8663 | -60.0266 | 62.8281 | 62.7457 | 62.7045 | -0.009155 | -0.050354 | -0.064087 | -0.091553 | -0.091553 | 122.7448 | 63.0707 | 122.5845 | 63.1348 | 122.6486 | 0.073243 | -0.004577 | 122.8088 | 122.7493 | 0.15564 | 122.7493 | 62.9105 | 122.6852 | -60.022 | -122.8409 | 62.7502 | 122.6852 | 62.796 | 63.2401
1978.8281 | 122.9782 | -62.8464 | 59.9075 | 0.031128 | 5.7742e-05 | -0.0079233 | 2.8928 | -0.0010253 | -0.0012048 | -0.0022581 | -0.091827 | 0.16544 | 0.12944 | -0.0067846 | 0.055824 | 0.10607 | -0.0014355 | 0.018311 | 0.10986 | -0.059509 | -0.036621 | 0.064087 | -0.009155 | 0.036621 | 0.5722 | 59.8618 | -62.8784 | 59.9121 | 59.9899 | 59.8206 | 0.36621 | 62.7869 | -59.7977 | -59.9442 | 62.9105 | 62.883 | 62.8372 | 0.09613 | 0.050354 | -0.032043 | -0.045777 | 0.004577 | 122.8363 | 63.2126 | 122.6669 | 63.2446 | 122.699 | 0.1236 | 0.022888 | 122.8683 | 122.7905 | 0.16937 | 122.7402 | 62.9562 | 122.7081 | -59.967 | -122.786 | 62.8098 | 122.7585 | 62.8647 | 63.4186
1979.8906 | 122.9141 | -62.8647 | 59.9258 | -0.014649 | -0.0014377 | -0.0085641 | 2.8913 | -0.0044433 | -0.0014184 | -0.0024717 | -0.046051 | 0.16181 | 0.12922 | -0.0093482 | 0.05796 | 0.10372 | -0.00015387 | 0.050354 | 0.091553 | -0.018311 | 0 | 0.11444 | 0.022888 | 0.073242 | 0.5722 | 59.8526 | -62.8601 | 59.8801 | 59.9762 | 59.8068 | 0.35706 | 62.8464 | -59.8343 | -59.9258 | 62.9791 | 62.9379 | 62.8876 | 0.091553 | 0.041199 | 0.004578 | -0.073242 | -0.045776 | 122.8409 | 63.2217 | 122.6715 | 63.2172 | 122.6669 | 0.13275 | 0.018311 | 122.8363 | 122.7402 | 0.10986 | 122.7127 | 62.9562 | 122.7173 | -59.9442 | -122.7859 | 62.8647 | 122.7448 | 62.915 | 63.4369
1980.8281 | 122.9507 | -62.8464 | 59.9121 | -0.060425 | -0.0016513 | -0.0087777 | 2.893 | 0.0015381 | -0.00035036 | -0.0039671 | -0.10709 | 0.16373 | 0.12858 | -0.0059302 | 0.057747 | 0.105 | 0.00048713 | -0.24261 | 0.059509 | -0.11444 | -0.045776 | 0.054932 | -0.050354 | -0.004578 | 0.54016 | 59.848 | -62.8601 | 59.8984 | 59.9762 | 59.7885 | 0.29755 | 62.7319 | -59.8526 | -59.9579 | 62.9013 | 62.8418 | 62.796 | 0.10986 | 0.064087 | -0.013732 | -0.064087 | -0.013733 | 122.8226 | 63.1439 | 122.6349 | 63.1577 | 122.6486 | 0.16937 | 0.068665 | 122.8363 | 122.7585 | 0.17395 | 122.7081 | 62.9059 | 122.6944 | -60.0266 | -122.7722 | 62.8006 | 122.7448 | 62.6038 | 63.3865
1981.8906 | 123.0469 | -62.8326 | 59.8663 | -0.052796 | -0.00015586 | -0.0077097 | 2.8913 | -0.0010253 | 0.00029044 | -0.0024717 | -0.027741 | 0.16437 | 0.12858 | -0.0093482 | 0.05796 | 0.1035 | -0.0029309 | 0.009155 | 0.059509 | -0.041199 | 0 | 0.11902 | 0.045776 | 0.09613 | 0.62256 | 59.7977 | -62.8647 | 59.9808 | 60.0861 | 59.9075 | 0.39368 | 62.7914 | -59.8068 | -59.8663 | 62.9517 | 62.9288 | 62.8784 | 0.13733 | 0.086975 | -0.032043 | -0.068665 | 0.11444 | 122.9187 | 63.2263 | 122.7402 | 63.2584 | 122.7722 | 0.16022 | 0.041199 | 122.9507 | 122.8455 | 0.10071 | 122.6624 | 62.8922 | 122.6303 | -59.9075 | -122.731 | 62.8326 | 122.8134 | 62.8418 | 63.4552
1982.8281 | 122.9553 | -62.851 | 59.9167 | 0.015869 | -0.0010105 | -0.0085641 | 2.8918 | -0.0010253 | 7.6842e-05 | -0.00033547 | -0.11929 | 0.16373 | 0.12773 | -0.0059302 | 0.054542 | 0.10692 | -0.0046399 | 0.041199 | 0.07782 | -0.054932 | -0.022888 | 0.054932 | -0.041199 | -0.013733 | 0.57678 | 59.8434 | -62.8738 | 59.9167 | 59.9808 | 59.8114 | 0.32044 | 62.796 | -59.8389 | -59.9396 | 62.9059 | 62.8372 | 62.8098 | 0.041199 | 0.013733 | -0.022888 | -0.073242 | 0 | 122.8317 | 63.1714 | 122.6624 | 63.1943 | 122.6852 | 0.10986 | 0.032044 | 122.8546 | 122.7905 | 0.13275 | 122.7173 | 62.9288 | 122.6944 | -59.9716 | -122.7905 | 62.8281 | 122.7676 | 62.8922 | 63.4277
1983.8906 | 122.937 | -62.8601 | 59.935 | -0.060425 | -0.0029331 | -0.0074961 | 2.892 | -0.00017091 | 0.00029044 | -0.0031125 | -0.049103 | 0.16437 | 0.12901 | -0.0097754 | 0.058387 | 0.10201 | -0.0016493 | 0.009155 | 0.11902 | -0.036621 | -0.036621 | 0.068665 | -0.004578 | 0.032043 | 0.53101 | 59.8618 | -62.8876 | 59.8618 | 59.9487 | 59.8022 | 0.32501 | 62.8235 | -59.816 | -59.9716 | 62.9288 | 62.8922 | 62.8555 | 0.068664 | 0.032043 | -0.027466 | -0.073243 | -0.073243 | 122.8088 | 63.1851 | 122.6624 | 63.2126 | 122.6898 | 0.10529 | 0 | 122.8363 | 122.7493 | 0.15564 | 122.7493 | 62.9791 | 122.7219 | -59.9716 | -122.8226 | 62.8235 | 122.7219 | 62.8693 | 63.3911
1984.8281 | 122.9691 | -62.8372 | 59.9304 | -0.014649 | -0.00015586 | -0.0092051 | 2.8905 | 0.0034607 | -0.0014184 | 9.193e-05 | -0.094879 | 0.16331 | 0.13008 | -0.0040076 | 0.055397 | 0.10415 | -0.0022901 | 0.032043 | 0.14648 | -0.036621 | -0.018311 | 0.045776 | -0.022888 | 0.022888 | 0.56305 | 59.848 | -62.8967 | 59.9213 | 60.0037 | 59.8068 | 0.36621 | 62.8006 | -59.7839 | -59.9487 | 62.883 | 62.8601 | 62.8143 | 0.059509 | 0.013733 | -0.05951 | -0.082398 | -0.009155 | 122.8409 | 63.2034 | 122.644 | 63.2629 | 122.7036 | 0.082397 | 0.01831 | 122.9004 | 122.818 | 0.18311 | 122.7448 | 62.9837 | 122.6852 | -59.967 | -122.8271 | 62.8189 | 122.7585 | 62.8693 | 63.4003
1985.8906 | 122.9782 | -62.8418 | 59.967 | -0.045166 | 0.0011257 | -0.0092051 | 2.8935 | 0.00046989 | -0.0027002 | -0.0022581 | -0.094879 | 0.16544 | 0.12751 | -0.0040076 | 0.057106 | 0.10415 | 0.00070073 | 0.009155 | 0.13733 | -0.050354 | -0.027466 | 0.036621 | -0.009155 | 0.036621 | 0.53101 | 59.8663 | -62.8693 | 59.8663 | 59.967 | 59.7794 | 0.2655 | 62.7914 | -59.8297 | -59.9945 | 62.8784 | 62.8784 | 62.8326 | 0.086975 | 0.041199 | -0.027466 | -0.10071 | -0.10071 | 122.8088 | 63.1073 | 122.6212 | 63.1348 | 122.6486 | 0.086975 | 0.022888 | 122.8363 | 122.7356 | 0.18768 | 122.7356 | 62.9791 | 122.7081 | -60.0174 | -122.8363 | 62.8143 | 122.7081 | 62.851 | 63.3728
1986.8281 | 122.9599 | -62.8281 | 59.935 | -0.022278 | -0.0018649 | -0.0092051 | 2.8896 | 0.00046989 | -0.00077756 | -0.0016171 | -0.10403 | 0.16373 | 0.12965 | -0.003794 | 0.058174 | 0.10308 | -0.0016493 | 0.013733 | 0.11444 | -0.045776 | -0.036621 | 0.054932 | -0.022888 | 0.018311 | 0.52185 | 59.8755 | -62.8784 | 59.8846 | 59.9716 | 59.7885 | 0.36621 | 62.7823 | -59.8206 | -59.9716 | 62.883 | 62.8464 | 62.8052 | 0.064087 | 0.022888 | -0.050354 | -0.05951 | -0.050354 | 122.7997 | 63.1943 | 122.6166 | 63.2446 | 122.6669 | 0.10071 | 0.009155 | 122.85 | 122.7631 | 0.16022 | 122.7539 | 62.9425 | 122.7036 | -59.9808 | -122.8134 | 62.7914 | 122.7127 | 62.8418 | 63.3499
1987.8281 | 122.9324 | -62.8555 | 59.9075 | -0.060425 | -0.0012241 | -0.0079233 | 2.8943 | 0.0043151 | -0.0016322 | -0.0024717 | -0.14371 | 0.16202 | 0.12858 | -0.0052892 | 0.057319 | 0.10372 | -0.00079467 | -0.013733 | 0.082397 | -0.086975 | -0.073242 | 0.027466 | -0.082397 | -0.041199 | 0.50354 | 59.8526 | -62.8784 | 59.8709 | 59.9396 | 59.7702 | 0.2655 | 62.7686 | -59.8251 | -59.9808 | 62.883 | 62.8143 | 62.7731 | 0.045776 | 0.004578 | -0.022888 | -0.054932 | -0.036621 | 122.7951 | 63.121 | 122.6257 | 63.1439 | 122.6486 | 0.11444 | 0.013733 | 122.818 | 122.7493 | 0.16937 | 122.731 | 62.9379 | 122.7081 | -59.9945 | -122.786 | 62.7823 | 122.7264 | 62.8418 | 63.3591
1988.8281 | 122.9782 | -62.8418 | 59.935 | 0.038757 | -0.00058326 | -0.0087777 | 2.893 | -0.0040161 | -0.0020594 | -0.0035397 | -0.11624 | 0.16309 | 0.13008 | -0.0012304 | 0.054969 | 0.10521 | -0.00036747 | 0.027466 | 0.14648 | -0.041199 | -0.032043 | 0.059509 | 0.004578 | 0.032043 | 0.52643 | 59.8709 | -62.8464 | 59.8984 | 59.9899 | 59.8068 | 0.37079 | 62.8006 | -59.7885 | -59.967 | 62.9013 | 62.8738 | 62.8464 | 0.073242 | 0.045777 | -0.004578 | -0.064087 | -0.036622 | 122.8317 | 63.2126 | 122.6486 | 63.2172 | 122.6532 | 0.10071 | 0.009156 | 122.8363 | 122.7448 | 0.18768 | 122.7173 | 62.9883 | 122.7127 | -59.9762 | -122.7814 | 62.8098 | 122.7402 | 62.8693 | 63.3682
1989.8906 | 123.0148 | -62.8601 | 59.8801 | 0.054016 | -0.0010105 | -0.0081369 | 2.8933 | 0.0017517 | -0.00077756 | -0.00076267 | -0.058258 | 0.16352 | 0.12773 | -0.002085 | 0.056251 | 0.10479 | -0.0020765 | -0.09613 | -0.064087 | -0.15106 | -0.050354 | 0.045776 | -0.064087 | 0.004578 | 0.52185 | 59.7977 | -62.8784 | 59.9625 | 60.0128 | 59.8389 | 0.27924 | 62.709 | -59.9442 | -59.9304 | 62.9059 | 62.8647 | 62.796 | 0.15564 | 0.086975 | -0.018311 | -0.082398 | 0.082397 | 122.8729 | 63.1393 | 122.699 | 63.1577 | 122.7173 | 0.19684 | 0.10071 | 122.8912 | 122.8409 | 0.086975 | 122.6761 | 62.796 | 122.6578 | -60.0311 | -122.7585 | 62.8098 | 122.8226 | 62.764 | 63.382
1990.8281 | 122.9416 | -62.8464 | 59.9304 | -0.14435 | -0.0029331 | -0.0094187 | 2.8941 | 0.0043151 | -0.00035036 | -0.00097627 | -0.088776 | 0.16395 | 0.12794 | -0.00037605 | 0.056892 | 0.10436 | 0.00091433 | 0.059509 | 0.1831 | 0 | -0.032043 | 0.032043 | -0.041199 | 0.027466 | 0.52643 | 59.8618 | -62.8784 | 59.8663 | 59.9625 | 59.7794 | 0.33417 | 62.8464 | -59.7473 | -59.9625 | 62.8784 | 62.8738 | 62.8052 | 0.027466 | -0.041199 | -0.032043 | -0.068665 | -0.064087 | 122.8088 | 63.1805 | 122.6257 | 63.2126 | 122.6578 | 0.032043 | -0.032043 | 122.8409 | 122.7448 | 0.1831 | 122.7402 | 63.0295 | 122.7081 | -59.9304 | -122.8088 | 62.8143 | 122.7127 | 62.9059 | 63.3728
1991.8906 | 123.0057 | -62.8647 | 59.8572 | -0.037537 | -0.0020785 | -0.0094187 | 2.8918 | -0.0050843 | 0.00093144 | -0.0050351 | 0.036346 | 0.16202 | 0.12965 | -0.0076392 | 0.05561 | 0.1035 | -0.0012219 | -0.050354 | 0.045776 | -0.07782 | -0.073242 | 0.032043 | -0.054932 | 0.004578 | 0.40283 | 59.816 | -62.8601 | 59.903 | 59.9945 | 59.8297 | 0.3067 | 62.7869 | -59.8114 | -59.9304 | 62.8967 | 62.8693 | 62.8098 | 0.082398 | 0.022888 | 0.004578 | -0.041199 | 0.045776 | 122.8592 | 63.1714 | 122.6944 | 63.1668 | 122.6898 | 0.10986 | 0.004578 | 122.8546 | 122.7631 | 0.1236 | 122.6761 | 62.9105 | 122.6807 | -59.935 | -122.7173 | 62.7914 | 122.7676 | 62.8143 | 63.2675
1992.8281 | 122.9553 | -62.8372 | 59.9304 | 0.023498 | -0.0010105 | -0.0098459 | 2.8941 | -0.0010253 | -0.00013676 | -0.0041807 | -0.064362 | 0.16224 | 0.12901 | -0.0018712 | 0.056892 | 0.10415 | -0.0020765 | 0.050354 | 0.086975 | -0.013733 | 0.027466 | 0.11902 | 0.022888 | 0.068665 | 0.58136 | 59.8572 | -62.8326 | 59.8801 | 60.0037 | 59.7839 | 0.32959 | 62.8235 | -59.8434 | -59.903 | 62.9562 | 62.9059 | 62.8601 | 0.082398 | 0.036621 | 0.004577 | -0.073242 | -0.050354 | 122.8409 | 63.1668 | 122.6212 | 63.1622 | 122.6166 | 0.13275 | 0.041199 | 122.8363 | 122.7127 | 0.10071 | 122.6898 | 62.9242 | 122.6944 | -59.9442 | -122.7631 | 62.8647 | 122.7173 | 62.8876 | 63.4186
1993.8906 | 123.056 | -62.8052 | 59.9121 | -0.045166 | -0.0012241 | -0.0092051 | 2.8933 | -0.0031617 | -0.002273 | -0.0050351 | -0.024689 | 0.16416 | 0.12837 | -0.0033666 | 0.056465 | 0.10158 | 0.00070073 | 0.050354 | 0.059509 | -0.027466 | 0.082397 | 0.17853 | 0.09613 | 0.13275 | 0.66376 | 59.8206 | -62.8235 | 59.9899 | 60.0769 | 59.935 | 0.40283 | 62.7777 | -59.8526 | -59.8297 | 62.9837 | 62.9379 | 62.9013 | 0.16022 | 0.1236 | -0.01831 | -0.091552 | 0.07782 | 122.8821 | 63.208 | 122.7402 | 63.2263 | 122.7585 | 0.20599 | 0.10986 | 122.9004 | 122.8134 | 0.086975 | 122.644 | 62.8647 | 122.6257 | -59.9396 | -122.7356 | 62.8876 | 122.7951 | 62.8555 | 63.4689
1994.8281 | 122.9599 | -62.8372 | 59.9258 | -0.022278 | 0.0017667 | -0.010059 | 2.8941 | 0.0013245 | 0.0013586 | -0.0035397 | -0.11929 | 0.1616 | 0.12944 | -0.00016245 | 0.054329 | 0.10521 | -0.0020765 | 0.036621 | 0.13275 | -0.041199 | -0.036621 | 0.027466 | -0.036621 | 0.045776 | 0.53101 | 59.8846 | -62.8784 | 59.8984 | 59.9808 | 59.7931 | 0.36621 | 62.796 | -59.7931 | -59.9625 | 62.8647 | 62.883 | 62.8006 | 0.086975 | 0.004578 | -0.041199 | -0.041198 | -0.027466 | 122.818 | 63.2034 | 122.6303 | 63.2446 | 122.6715 | 0.068665 | 0.004578 | 122.8592 | 122.7768 | 0.17395 | 122.7631 | 62.97 | 122.7219 | -59.967 | -122.8043 | 62.8006 | 122.7356 | 62.8738 | 63.3682
1995.8906 | 123.0469 | -62.8281 | 59.8709 | -0.045166 | -0.0027195 | -0.0085641 | 2.8915 | 0.00025629 | -0.0018458 | 0.00030553 | -0.033844 | 0.16138 | 0.12858 | -0.0078528 | 0.059028 | 0.10286 | 0.00091433 | 0.013733 | 0.050354 | -0.054932 | 0.022888 | 0.13733 | 0.022888 | 0.082397 | 0.61798 | 59.8206 | -62.8372 | 59.9716 | 60.0906 | 59.9121 | 0.40283 | 62.7731 | -59.8206 | -59.848 | 62.9654 | 62.9105 | 62.851 | 0.13733 | 0.07782 | -0.009155 | -0.050354 | 0.10071 | 122.9187 | 63.2309 | 122.7402 | 63.2401 | 122.7493 | 0.19226 | 0.07782 | 122.9279 | 122.8088 | 0.10529 | 122.6578 | 62.8784 | 122.6486 | -59.9258 | -122.7081 | 62.851 | 122.7997 | 62.8418 | 63.446
1996.8281 | 122.905 | -62.8418 | 59.9442 | -0.068054 | -0.0029331 | -0.0098459 | 2.8913 | 0.0015381 | 0.0019994 | 0.00051913 | -0.085724 | 0.16267 | 0.13008 | -0.0040076 | 0.05561 | 0.1035 | -0.0029309 | 0.050354 | 0.12817 | -0.036621 | -0.045776 | 0.054932 | -0.027466 | 0.036621 | 0.54016 | 59.8572 | -62.851 | 59.8663 | 59.9533 | 59.7977 | 0.32501 | 62.8052 | -59.816 | -59.9899 | 62.8967 | 62.8784 | 62.8143 | 0.073242 | 0.009155 | -0.009155 | -0.086975 | -0.07782 | 122.7951 | 63.1668 | 122.6395 | 63.176 | 122.6486 | 0.091553 | -0.009155 | 122.8043 | 122.7173 | 0.1648 | 122.7081 | 62.97 | 122.699 | -59.9808 | -122.7951 | 62.796 | 122.7081 | 62.8922 | 63.382
1997.8906 | 123.0377 | -62.8464 | 59.8572 | -0.029907 | -0.00079686 | -0.010914 | 2.8956 | 0.00025629 | -0.0014184 | -0.0033261 | -0.1315 | 0.16544 | 0.12901 | 0.011587 | 0.055824 | 0.10457 | 0.0028369 | -0.10529 | 0 | -0.14648 | -0.10071 | -0.032043 | -0.14648 | -0.059509 | 0.45319 | 59.8251 | -62.8967 | 59.9487 | 59.9945 | 59.8206 | 0.27008 | 62.6999 | -59.8572 | -59.9579 | 62.8143 | 62.7869 | 62.6999 | 0.086975 | 0 | -0.050354 | -0.032044 | 0.091552 | 122.8409 | 63.1165 | 122.6669 | 63.1668 | 122.7173 | 0.11444 | 0.045776 | 122.8912 | 122.8455 | 0.14648 | 122.7219 | 62.8464 | 122.6715 | -60.0037 | -122.7539 | 62.7457 | 122.7951 | 62.7411 | 63.2996
1998.8281 | 122.9462 | -62.883 | 59.9487 | -0.037537 | -0.0014377 | -0.0092051 | 2.8915 | -0.0035889 | -0.00013676 | -0.0052487 | -0.070465 | 0.16181 | 0.12773 | -0.0050756 | 0.056465 | 0.10457 | -0.0063489 | 0.059509 | 0.11444 | -0.013733 | 0.009155 | 0.09613 | 0.027466 | 0.054932 | 0.58594 | 59.8526 | -62.8647 | 59.8755 | 59.9808 | 59.8022 | 0.3479 | 62.8693 | -59.8343 | -59.9396 | 62.9791 | 62.9379 | 62.9105 | 0.068665 | 0.041199 | 0.018311 | -0.09613 | -0.073242 | 122.8638 | 63.2309 | 122.6852 | 63.2126 | 122.6669 | 0.10986 | 0.022888 | 122.8455 | 122.7402 | 0.12817 | 122.7173 | 62.9974 | 122.7356 | -59.9625 | -122.8134 | 62.8922 | 122.7585 | 62.9425 | 63.4689
1999.8906 | 123.0103 | -62.8281 | 59.8801 | -0.022278 | 0.00027134 | -0.0092051 | 2.8911 | -0.0020935 | -0.0016322 | -0.0026853 | -0.046051 | 0.16267 | 0.12815 | -0.0033666 | 0.056251 | 0.10286 | 0.0015551 | -0.022888 | 0.027466 | -0.091553 | -0.064087 | -0.004578 | -0.064087 | 0 | 0.50354 | 59.8251 | -62.8647 | 59.9213 | 60.0128 | 59.8389 | 0.31128 | 62.7365 | -59.8526 | -59.9442 | 62.8235 | 62.8281 | 62.764 | 0.091553 | 0.027466 | -0.036621 | -0.054932 | 0.041199 | 122.8409 | 63.1393 | 122.6669 | 63.176 | 122.7036 | 0.086975 | 0.027466 | 122.8775 | 122.7859 | 0.11902 | 122.6898 | 62.8555 | 122.6532 | -59.9716 | -122.7448 | 62.764 | 122.7493 | 62.8052 | 63.3316
2000.8281 | 122.937 | -62.8693 | 59.9167 | 0.00824 | -0.0016513 | -0.010273 | 2.8915 | -0.0020935 | -0.00099116 | -0.0022581 | -0.07962 | 0.16224 | 0.1273 | -0.0084936 | 0.057533 | 0.105 | -0.00079467 | 0.032043 | 0.10529 | -0.041199 | -0.013733 | 0.032043 | 0 | 0.10529 | 0.58136 | 59.8618 | -62.8555 | 59.8526 | 59.9899 | 59.7885 | 0.33875 | 62.8281 | -59.8114 | -59.9304 | 62.9013 | 62.9745 | 62.8693 | 0.14649 | 0.041199 | 0.013733 | -0.054932 | -0.064087 | 122.8592 | 63.208 | 122.6578 | 63.1943 | 122.644 | 0.073242 | 0.027466 | 122.8455 | 122.7081 | 0.14649 | 122.7173 | 62.9745 | 122.731 | -59.9579 | -122.7722 | 62.8555 | 122.7219 | 62.9013 | 63.4506
2001.8906 | 122.9965 | -62.8464 | 59.8663 | -0.075684 | -0.0012241 | -0.0072825 | 2.8926 | 0.00068369 | -0.0012048 | -0.0026853 | -0.094879 | 0.16331 | 0.12645 | -0.003153 | 0.055824 | 0.10308 | -0.00058107 | -0.054932 | 0.004578 | -0.12817 | -0.050354 | 0.041199 | -0.07782 | -0.013733 | 0.48523 | 59.7977 | -62.8876 | 59.9121 | 59.9762 | 59.8114 | 0.23804 | 62.7182 | -59.8618 | -59.9167 | 62.8876 | 62.8326 | 62.7686 | 0.11444 | 0.050354 | -0.041198 | -0.068665 | 0.045776 | 122.8226 | 63.0844 | 122.6578 | 63.1256 | 122.699 | 0.16937 | 0.07782 | 122.8638 | 122.7997 | 0.13275 | 122.6852 | 62.851 | 122.644 | -59.9945 | -122.7539 | 62.796 | 122.7585 | 62.7914 | 63.3316
2002.8281 | 122.9507 | -62.8418 | 59.9258 | -0.068054 | -0.00036966 | -0.0094187 | 2.892 | 0.0015381 | -0.0016322 | -0.0031125 | -0.07962 | 0.16288 | 0.12751 | 0.001974 | 0.053901 | 0.10543 | -0.0010083 | 0.073242 | 0.09613 | -0.027466 | 0.041199 | 0.13275 | 0.032043 | 0.064087 | 0.60425 | 59.8251 | -62.851 | 59.8938 | 60.0082 | 59.8389 | 0.36621 | 62.8143 | -59.8297 | -59.8846 | 62.9745 | 62.9059 | 62.8738 | 0.091553 | 0.059509 | -0.009155 | -0.10071 | -0.032043 | 122.85 | 63.208 | 122.6807 | 63.2172 | 122.6898 | 0.16022 | 0.068665 | 122.8592 | 122.7448 | 0.1236 | 122.6761 | 62.9379 | 122.6669 | -59.9533 | -122.7768 | 62.883 | 122.7356 | 62.915 | 63.446
2003.8906 | 122.9874 | -62.8601 | 59.8801 | -0.052796 | -0.00036966 | -0.0074961 | 2.8926 | 0.0017517 | -0.0018458 | -0.0048215 | -0.082672 | 0.16352 | 0.12837 | -0.003153 | 0.057106 | 0.10393 | -0.0033581 | -0.07782 | -0.027466 | -0.09613 | -0.068665 | 0.013733 | -0.10529 | -0.050354 | 0.4715 | 59.8114 | -62.8647 | 59.9213 | 59.9945 | 59.8068 | 0.27924 | 62.764 | -59.9075 | -59.9487 | 62.8738 | 62.8098 | 62.7548 | 0.045776 | -0.009156 | -0.004578 | -0.068665 | 0.041199 | 122.8546 | 63.1393 | 122.6669 | 63.1439 | 122.6715 | 0.10986 | 0.027465 | 122.8592 | 122.7859 | 0.068664 | 122.6761 | 62.8326 | 122.6715 | -59.9762 | -122.7448 | 62.7914 | 122.7814 | 62.7823 | 63.3316
2004.8281 | 122.9965 | -62.8143 | 59.8846 | -0.037537 | -0.0020785 | -0.0081369 | 2.8937 | 4.2692e-05 | 7.6842e-05 | -0.00076267 | -0.097931 | 0.16053 | 0.12773 | -0.003794 | 0.054756 | 0.10286 | 0.0011279 | 0.059509 | 0.068665 | -0.041199 | 0.045776 | 0.16937 | 0.068665 | 0.09613 | 0.63629 | 59.8526 | -62.851 | 59.9442 | 60.0494 | 59.8755 | 0.39825 | 62.7731 | -59.816 | -59.8389 | 62.9837 | 62.9105 | 62.883 | 0.13733 | 0.10986 | -0.036621 | -0.032044 | 0.059509 | 122.8638 | 63.2126 | 122.6898 | 63.2492 | 122.7264 | 0.21057 | 0.086975 | 122.9004 | 122.7951 | 0.10986 | 122.7036 | 62.883 | 122.6669 | -59.9258 | -122.7356 | 62.8601 | 122.7585 | 62.8738 | 63.4506
2005.8906 | 123.0286 | -62.8555 | 59.8755 | -0.052796 | -0.0018649 | -0.0081369 | 2.8905 | -0.0027343 | -0.0018458 | -0.0020443 | -0.076569 | 0.16309 | 0.12794 | -0.0052892 | 0.056678 | 0.1035 | -0.0020765 | -0.022888 | 0.041199 | -0.091553 | -0.022888 | 0.050354 | -0.027466 | 0.032043 | 0.52643 | 59.8251 | -62.8601 | 59.9487 | 60.0494 | 59.8618 | 0.33875 | 62.764 | -59.8343 | -59.8984 | 62.9059 | 62.8876 | 62.8281 | 0.1236 | 0.064087 | -0.004577 | -0.050354 | 0.073242 | 122.905 | 63.1943 | 122.7173 | 63.1989 | 122.7219 | 0.14191 | 0.068665 | 122.9095 | 122.8088 | 0.13275 | 122.6852 | 62.8967 | 122.6807 | -59.967 | -122.7356 | 62.8326 | 122.8043 | 62.8326 | 63.382
2006.8281 | 123.0423 | -62.8418 | 59.903 | -0.007019 | -0.00036966 | -0.0083505 | 2.8922 | 0.0017517 | -0.002273 | -0.0037533 | -0.10098 | 0.16395 | 0.1273 | -0.0061438 | 0.056251 | 0.1035 | 0.00027333 | 0.050354 | 0.07782 | -0.004578 | 0.1236 | 0.17853 | -0.1236 | 0.054932 | 0.66376 | 59.8068 | -62.8418 | 59.9762 | 60.0861 | 59.9121 | 0.40741 | 62.8372 | -59.8251 | -59.7794 | 63.0203 | 62.8967 | 62.7182 | 0.05951 | -0.11902 | 0 | -0.09613 | 0.073242 | 122.9279 | 63.2492 | 122.7539 | 63.2492 | 122.7539 | 0.18311 | 0.12817 | 122.9279 | 122.818 | 0.082398 | 122.6486 | 62.9196 | 122.6486 | -59.9075 | -122.7448 | 62.9654 | 122.818 | 62.8922 | 63.5056
2007.8906 | 122.9919 | -62.8647 | 59.8892 | -0.037537 | -0.0010105 | -0.011341 | 2.8913 | -0.0012391 | 0.0013586 | -0.0024717 | -0.076569 | 0.16245 | 0.12794 | 0.0024012 | 0.055183 | 0.10436 | -0.0020765 | -0.036621 | 0.045776 | -0.068665 | 0.036621 | 0.27008 | -0.12817 | -0.054932 | 0.50812 | 59.8251 | -62.8601 | 59.9258 | 60.0128 | 59.8389 | 0.31586 | 62.796 | -59.8434 | -59.8526 | 63.1348 | 62.8098 | 62.7365 | 0.013733 | -0.059509 | 0.004578 | -0.064087 | 0.036621 | 122.8775 | 63.1805 | 122.7036 | 63.176 | 122.699 | 0.33875 | 0.10529 | 122.8729 | 122.7859 | 0.11444 | 122.6852 | 62.9105 | 122.6898 | -59.9579 | -122.7493 | 62.9013 | 122.7905 | 62.8281 | 63.3728
2008.8281 | 123.0057 | -62.8555 | 59.9075 | 0.015869 | -0.00058326 | -0.010487 | 2.8928 | 4.2692e-05 | -0.00013676 | -0.0016171 | -0.11624 | 0.16416 | 0.12602 | -0.0010168 | 0.05561 | 0.10393 | -0.0022901 | 0.064087 | 0.050354 | -0.041199 | 0.064087 | 0.15106 | 0.059509 | 0.10529 | 0.64087 | 59.8389 | -62.8784 | 59.9487 | 60.0403 | 59.8755 | 0.40283 | 62.8143 | -59.8572 | -59.8434 | 63.0066 | 62.9608 | 62.915 | 0.14649 | 0.10071 | -0.022888 | -0.068665 | 0.041198 | 122.8958 | 63.2584 | 122.731 | 63.2812 | 122.7539 | 0.19226 | 0.10529 | 122.9187 | 122.8271 | 0.091553 | 122.7173 | 62.9059 | 122.6944 | -59.9487 | -122.786 | 62.9196 | 122.8043 | 62.9196 | 63.4964
2009.8906 | 123.0652 | -62.8189 | 59.8526 | -0.007019 | 5.7742e-05 | -0.010273 | 2.8922 | 4.2692e-05 | -0.0027002 | -0.0041807 | -0.082672 | 0.16288 | 0.1258 | -0.010416 | 0.055397 | 0.10372 | 0.00091433 | 0.022888 | 0.054932 | -0.064087 | 0.050354 | 0.14191 | 0.041199 | 0.091553 | 0.65002 | 59.8251 | -62.8281 | 59.9899 | 60.0952 | 59.9121 | 0.41199 | 62.7548 | -59.7977 | -59.8022 | 62.9608 | 62.9105 | 62.8601 | 0.15564 | 0.10529 | -0.009155 | -0.027466 | 0.13733 | 122.9141 | 63.2309 | 122.731 | 63.2401 | 122.7402 | 0.20599 | 0.11444 | 122.9233 | 122.818 | 0.11902 | 122.6532 | 62.8738 | 122.644 | -59.9167 | -122.6807 | 62.8693 | 122.8088 | 62.8418 | 63.4689
2010.8281 | 123.0286 | -62.8326 | 59.8984 | 0.00824 | -0.00015586 | -0.012837 | 2.8939 | -0.0020935 | -0.0016322 | 9.193e-05 | -0.085724 | 0.16331 | 0.12773 | -0.0040076 | 0.056038 | 0.1018 | -0.0042127 | 0.49439 | 0.11902 | 0.004578 | -0.018311 | 0.1831 | 0.041199 | 0.059509 | 0.65918 | 59.8343 | -62.8372 | 59.9625 | 60.0815 | 59.8892 | 0.40283 | 62.8372 | -59.7794 | -59.9167 | 63.0157 | 62.8922 | 62.8738 | 0.054931 | 0.036621 | -0.004577 | -0.064086 | 0.064087 | 122.9141 | 63.2355 | 122.7219 | 63.2401 | 122.7264 | 0.17853 | -0.022889 | 122.9187 | 122.7997 | 0.11444 | 122.6715 | 62.9517 | 122.6669 | -59.8938 | -122.7356 | 62.8143 | 122.7951 | 63.327 | 63.4918
2011.8906 | 122.9919 | -62.8418 | 59.9121 | -0.052796 | -0.0014377 | -0.0079233 | 2.8883 | -0.00059811 | 7.6842e-05 | -0.00012167 | -0.097931 | 0.16352 | 0.12794 | -0.00037605 | 0.05561 | 0.1035 | -0.0012219 | -0.009155 | 0.032043 | -0.086975 | -0.11444 | 0.027466 | -0.09613 | 0.018311 | 0.49896 | 59.7977 | -62.8784 | 59.9487 | 60.0174 | 59.848 | 0.31128 | 62.7548 | -59.8801 | -60.0266 | 62.8693 | 62.8601 | 62.7457 | 0.10529 | -0.009155 | -0.036621 | -0.11444 | 0.036621 | 122.8592 | 63.1531 | 122.6898 | 63.1897 | 122.7264 | 0.11444 | -0.027466 | 122.8958 | 122.8271 | 0.11902 | 122.6761 | 62.8738 | 122.6395 | -59.9991 | -122.7905 | 62.7274 | 122.7905 | 62.8326 | 63.3408
2012.8281 | 122.9233 | -62.8876 | 59.8892 | -0.029907 | -0.0014377 | -0.0079233 | 2.8952 | 0.0021789 | -0.00035036 | -0.0011899 | -0.18338 | 0.16437 | 0.12602 | -0.00058965 | 0.055183 | 0.105 | -0.0027173 | -0.059509 | 0.054932 | -0.10986 | -0.14191 | -0.10071 | -0.21515 | -0.13275 | 0.37537 | 59.8572 | -62.9105 | 59.8389 | 59.8663 | 59.7107 | 0.2243 | 62.7777 | -59.8343 | -60.0311 | 62.7869 | 62.7548 | 62.6724 | -0.022888 | -0.10529 | -0.022888 | -0.032043 | -0.050354 | 122.7539 | 63.1119 | 122.5983 | 63.1348 | 122.6212 | 0.009155 | -0.032044 | 122.7768 | 122.7493 | 0.16479 | 122.7676 | 62.9425 | 122.7448 | -59.9991 | -122.7997 | 62.7457 | 122.7264 | 62.8281 | 63.2629
2013.8906 | 123.0194 | -62.8555 | 59.8526 | -0.045166 | 0.00027134 | -0.0087777 | 2.8924 | 0.00068369 | -0.0012048 | -0.0011899 | -0.11319 | 0.16181 | 0.12687 | -0.0018712 | 0.05796 | 0.10436 | 0.0011279 | -0.050354 | -0.018311 | -0.10986 | -0.050354 | 0.050354 | -0.082397 | -0.022888 | 0.4715 | 59.8114 | -62.8876 | 59.9121 | 59.9854 | 59.816 | 0.25177 | 62.7457 | -59.8709 | -59.903 | 62.9059 | 62.8326 | 62.7731 | 0.086975 | 0.027466 | -0.032043 | -0.041199 | 0.059509 | 122.8409 | 63.1073 | 122.6715 | 63.1393 | 122.7036 | 0.16022 | 0.059509 | 122.8729 | 122.7997 | 0.091552 | 122.699 | 62.8372 | 122.6669 | -59.9625 | -122.7402 | 62.8052 | 122.7676 | 62.8052 | 63.327
2014.8281 | 123.0469 | -62.8098 | 59.8755 | 0.015869 | -0.0018649 | -0.0085641 | 2.8913 | -0.0020935 | -0.00035036 | -0.0046079 | -0.10098 | 0.16331 | 0.12751 | -0.002085 | 0.055397 | 0.10457 | -0.0027173 | 0.050354 | 0.050354 | -0.032043 | 0.064087 | 0.17395 | 0.064087 | 0.11902 | 0.69122 | 59.8389 | -62.8418 | 59.9854 | 60.0906 | 59.9213 | 0.40283 | 62.7777 | -59.8251 | -59.8114 | 62.9837 | 62.9288 | 62.8738 | 0.15106 | 0.09613 | -0.032044 | -0.036621 | 0.10986 | 122.9004 | 63.2126 | 122.731 | 63.2446 | 122.7631 | 0.20599 | 0.09613 | 122.9324 | 122.8271 | 0.082397 | 122.6807 | 62.8601 | 122.6486 | -59.9075 | -122.7173 | 62.8738 | 122.7951 | 62.8601 | 63.501
2015.8906 | 123.0286 | -62.8418 | 59.8755 | -0.060425 | -0.0018649 | -0.0094187 | 2.8937 | 0.0021789 | -0.0035548 | -0.0014035 | -0.085724 | 0.16245 | 0.12751 | -0.003794 | 0.058174 | 0.10244 | -0.0029309 | -0.027466 | 0.036621 | -0.082397 | 0.018311 | -0.082397 | -0.064087 | -0.013733 | 0.5127 | 59.8389 | -62.8647 | 59.9258 | 60.0037 | 59.8297 | 0.31128 | 62.7594 | -59.8389 | -59.8572 | 62.7594 | 62.8281 | 62.7777 | 0.068664 | 0.01831 | -0.022888 | -0.036621 | 0.050354 | 122.8455 | 63.1531 | 122.6715 | 63.176 | 122.6944 | 0 | 0.10071 | 122.8683 | 122.7905 | 0.11902 | 122.7036 | 62.8784 | 122.6807 | -59.9579 | -122.7402 | 62.8601 | 122.7676 | 62.8143 | 63.3545
2016.8281 | 123.0286 | -62.8235 | 59.8526 | 0.031128 | -0.0022923 | -0.0062143 | 2.8918 | 0.00089729 | -0.00056396 | -0.0026853 | -0.094879 | 0.1648 | 0.12751 | -0.00828 | 0.054329 | 0.1065 | -0.0020765 | 0.059509 | 0.054932 | -0.032043 | 0.07782 | 0.17853 | 0.07782 | 0.11444 | 0.66834 | 59.8206 | -62.8601 | 59.8434 | 60.1593 | 59.8892 | 0.38452 | 62.7914 | -59.7977 | -59.7748 | 63.002 | 62.9379 | 62.9013 | 0.14648 | 0.10986 | -0.036621 | -0.032043 | -0.009155 | 122.9828 | 63.208 | 122.7127 | 63.2446 | 122.7493 | 0.21057 | 0.10986 | 123.0194 | 122.7036 | 0.086975 | 122.6807 | 62.8784 | 122.644 | -59.8846 | -122.7127 | 62.9013 | 122.6669 | 62.883 | 63.4918
2017.8281 | 122.937 | -62.8555 | 59.9487 | -0.068054 | -0.00036966 | -0.0094187 | 2.8928 | 0.0017517 | -0.0033412 | -0.0022581 | -0.11929 | 0.16502 | 0.12666 | -0.0046484 | 0.056251 | 0.10436 | -0.0022901 | 0.032043 | 0.10986 | -0.036621 | 0.013733 | 0.09613 | 0.013733 | 0.054932 | 0.5722 | 59.8572 | -62.851 | 59.8709 | 59.9762 | 59.7931 | 0.3479 | 62.8189 | -59.8389 | -59.935 | 62.9517 | 62.9105 | 62.8693 | 0.091553 | 0.050354 | 0.004578 | -0.091552 | -0.077819 | 122.8317 | 63.2034 | 122.6486 | 63.1989 | 122.644 | 0.13275 | 0.050354 | 122.8271 | 122.7219 | 0.14648 | 122.7081 | 62.9654 | 122.7127 | -59.9854 | -122.7997 | 62.8693 | 122.7264 | 62.8876 | 63.4277
2018.8281 | 123.0377 | -62.8326 | 59.8846 | -0.014649 | -0.00079686 | -0.0089913 | 2.8939 | 0.0026063 | -0.002273 | -0.0041807 | -0.070465 | 0.16288 | 0.1288 | 0.00069215 | 0.057533 | 0.10286 | -0.0050671 | 0.054932 | 0.059509 | -0.027466 | 0.082397 | 0.20142 | 0.086975 | 0.1236 | 0.64545 | 59.8343 | -62.8464 | 59.9854 | 60.1089 | 59.9075 | 0.40741 | 62.8052 | -59.8251 | -59.8022 | 63.0341 | 62.9562 | 62.9196 | 0.15106 | 0.11444 | -0.013733 | -0.050354 | 0.10071 | 122.9416 | 63.2401 | 122.7402 | 63.2538 | 122.7539 | 0.22888 | 0.10986 | 122.9553 | 122.8317 | 0.086975 | 122.6807 | 62.8922 | 122.6669 | -59.9121 | -122.731 | 62.915 | 122.818 | 62.8876 | 63.4781
2019.8906 | 123.0148 | -62.8418 | 59.8709 | -0.052796 | -0.0029331 | -0.0083505 | 2.8933 | 0.0023925 | -0.0037684 | -0.0014035 | -0.094879 | 0.16331 | 0.12474 | -0.0027258 | 0.057106 | 0.10479 | -0.00015387 | -0.054932 | 0.018311 | -0.11444 | -0.059509 | 0.013733 | -0.054932 | -0.018311 | 0.48981 | 59.8297 | -62.8738 | 59.9167 | 59.9991 | 59.816 | 0.27924 | 62.7274 | -59.8526 | -59.9304 | 62.8555 | 62.8235 | 62.7869 | 0.09613 | 0.059509 | -0.032043 | -0.041199 | 0.045776 | 122.8409 | 63.121 | 122.6578 | 63.1531 | 122.6898 | 0.12817 | 0.054932 | 122.8729 | 122.7905 | 0.13275 | 122.7036 | 62.8601 | 122.6715 | -59.9854 | -122.7448 | 62.7823 | 122.7585 | 62.7869 | 63.3316
2020.8281 | 123.056 | -62.8281 | 59.903 | -0.029907 | -0.0012241 | -0.0089913 | 2.8952 | -0.0014527 | -0.0031274 | -0.0033261 | -0.088776 | 0.16309 | 0.12837 | -0.0063574 | 0.056678 | 0.10585 | -0.0012219 | 0.041199 | 0.050354 | -0.050354 | 0.050354 | 0.18768 | 0.054932 | 0.11444 | 0.6546 | 59.8068 | -62.8738 | 60.0082 | 60.0998 | 59.9258 | 0.43488 | 62.7777 | -59.8526 | -59.8526 | 63.0157 | 62.9425 | 62.883 | 0.16479 | 0.10529 | -0.045776 | -0.09613 | 0.10529 | 122.9279 | 63.2629 | 122.7539 | 63.3087 | 122.7997 | 0.23804 | 0.10071 | 122.9736 | 122.8821 | 0.10071 | 122.6807 | 62.8784 | 122.6349 | -59.9533 | -122.7768 | 62.8784 | 122.8363 | 62.8693 | 63.4827
2021.8906 | 123.0469 | -62.8326 | 59.8434 | -0.068054 | -0.0012241 | -0.0081369 | 2.8943 | 0.0011109 | -0.0020594 | -0.00012167 | -0.18643 | 0.16395 | 0.12794 | -0.0061438 | 0.055397 | 0.10521 | -0.0025037 | -0.073242 | -0.018311 | -0.14191 | -0.091553 | -0.018311 | -0.15106 | -0.07782 | 0.48981 | 59.7977 | -62.8738 | 59.9579 | 60.0174 | 59.8343 | 0.2655 | 62.6907 | -59.8618 | -59.935 | 62.8143 | 62.7548 | 62.6816 | 0.064087 | -0.009155 | -0.041198 | -0.045777 | 0.11444 | 122.85 | 63.0981 | 122.6669 | 63.1393 | 122.7081 | 0.1236 | 0.050354 | 122.8912 | 122.8317 | 0.1236 | 122.6715 | 62.8143 | 122.6303 | -59.9854 | -122.7173 | 62.7411 | 122.7905 | 62.7594 | 63.3224
2022.8281 | 122.9965 | -62.8143 | 59.9075 | -0.022278 | -0.00015586 | -0.0087777 | 2.8918 | -0.00059811 | -0.003982 | -0.0024717 | -0.091827 | 0.16096 | 0.12837 | -0.00080325 | 0.054969 | 0.10329 | 0.0011279 | 0.059509 | 0.045776 | -0.041199 | 0.045776 | 0.14648 | 0.045776 | 0.086975 | 0.62256 | 59.8343 | -62.8372 | 59.9533 | 60.0632 | 59.8572 | 0.41199 | 62.7731 | -59.8618 | -59.8618 | 62.9608 | 62.9013 | 62.8601 | 0.12817 | 0.086975 | -0.022888 | -0.073242 | 0.045776 | 122.8775 | 63.2263 | 122.6715 | 63.2492 | 122.6944 | 0.18768 | 0.086975 | 122.9004 | 122.7905 | 0.086975 | 122.6715 | 62.8601 | 122.6486 | -59.9487 | -122.7448 | 62.8601 | 122.7676 | 62.8738 | 63.4369
2023.8906 | 123.024 | -62.8601 | 59.8663 | -0.037537 | -0.0020785 | -0.010059 | 2.8905 | 0.00025629 | -0.00035036 | -0.00097627 | -0.10709 | 0.16267 | 0.1273 | 0.00026495 | 0.055397 | 0.105 | 0.00091433 | -0.059509 | -0.013733 | -0.09613 | -0.059509 | 0.041199 | -0.082397 | -0.022888 | 0.47607 | 59.7977 | -62.9013 | 59.9121 | 59.9762 | 59.816 | 0.28839 | 62.764 | -59.8801 | -59.9258 | 62.9013 | 62.8372 | 62.7777 | 0.073242 | 0.013733 | -0.041199 | -0.068665 | 0.045776 | 122.8363 | 63.1485 | 122.6761 | 63.1897 | 122.7173 | 0.13733 | 0.036621 | 122.8775 | 122.8134 | 0.082397 | 122.699 | 62.8464 | 122.6578 | -59.9625 | -122.7676 | 62.8006 | 122.7722 | 62.8006 | 63.3362
2024.8281 | 123.0423 | -62.8372 | 59.8938 | -0.022278 | -0.0010105 | -0.0083505 | 2.8933 | -0.0029479 | -0.0016322 | 0.00030553 | -0.07962 | 0.16202 | 0.12815 | -0.0059302 | 0.056251 | 0.10393 | -0.0025037 | 0.041199 | 0.064087 | -0.041199 | 0.064087 | 0.21057 | 0.091553 | 0.1236 | 0.66834 | 59.816 | -62.8464 | 59.9899 | 60.0998 | 59.9258 | 0.42572 | 62.796 | -59.8297 | -59.8297 | 63.0478 | 62.9608 | 62.9288 | 0.16479 | 0.13275 | -0.009156 | -0.07782 | 0.09613 | 122.937 | 63.2629 | 122.7631 | 63.2721 | 122.7722 | 0.25177 | 0.10529 | 122.9462 | 122.8363 | 0.10529 | 122.6624 | 62.9013 | 122.6532 | -59.935 | -122.7402 | 62.9013 | 122.8271 | 62.8784 | 63.5056
2025.8906 | 123.0377 | -62.851 | 59.8389 | -0.029907 | 5.7742e-05 | -0.0062143 | 2.8947 | 0.0043151 | 0.00029044 | -0.00033547 | -0.10098 | 0.16096 | 0.12709 | -0.002085 | 0.056678 | 0.10372 | -0.0035719 | -0.045776 | -0.018311 | -0.11444 | -0.38452 | 0.082397 | 0.23804 | 0.050354 | 0.51727 | 59.8114 | -62.8784 | 59.9625 | 60.0174 | 59.8434 | 0.29755 | 62.7365 | -59.8572 | -60.2234 | 62.9333 | 62.9013 | 63.089 | 0.16479 | 0.35248 | -0.027466 | -0.027466 | 0.1236 | 122.8683 | 63.1485 | 122.6944 | 63.176 | 122.7219 | 0.19684 | -0.27008 | 122.8958 | 122.8409 | 0.09613 | 122.6898 | 62.8326 | 122.6624 | -59.9533 | -122.7173 | 62.4664 | 122.8134 | 62.8052 | 63.3682
2026.8281 | 123.0835 | -62.8098 | 59.8663 | -0.045166 | -0.00015586 | -0.010487 | 2.8926 | -0.0010253 | -0.0016322 | -0.0022581 | -0.07962 | 0.16331 | 0.12901 | -0.0035802 | 0.056251 | 0.10393 | -0.0054945 | 0.032043 | 0.064087 | -0.045776 | 0.050354 | 0.15564 | 0.059509 | 0.11444 | 0.66376 | 59.8068 | -62.8372 | 60.0082 | 60.1364 | 59.9167 | 0.41657 | 62.764 | -59.8022 | -59.816 | 62.9654 | 62.9242 | 62.8693 | 0.16022 | 0.10528 | -0.027466 | -0.059509 | 0.14191 | 122.9462 | 63.2263 | 122.7264 | 63.2538 | 122.7539 | 0.20142 | 0.09613 | 122.9736 | 122.8455 | 0.10986 | 122.644 | 62.8738 | 122.6166 | -59.9121 | -122.7036 | 62.8601 | 122.818 | 62.8418 | 63.4735
2027.8906 | 123.0423 | -62.8235 | 59.8938 | -0.014649 | -0.0020785 | -0.010059 | 2.8939 | 0.0015381 | -0.00077756 | -0.0011899 | -0.14066 | 0.16267 | 0.12602 | -0.0016576 | 0.055824 | 0.105 | -0.0037855 | -0.041199 | -0.045776 | -0.1236 | -0.041199 | 0.059509 | -0.064087 | -0.018311 | 0.6134 | 59.7748 | -62.915 | 60.0082 | 60.0357 | 59.8297 | 0.28839 | 62.6999 | -59.9396 | -59.935 | 62.883 | 62.8052 | 62.7594 | 0.10528 | 0.059509 | -0.091553 | -0.11902 | 0.11444 | 122.8592 | 63.1119 | 122.6532 | 63.2034 | 122.7448 | 0.1831 | 0.082397 | 122.9507 | 122.9233 | 0.07782 | 122.6898 | 62.7777 | 122.5983 | -60.0174 | -122.8088 | 62.7823 | 122.8317 | 62.7823 | 63.4369
2028.8281 | 123.0652 | -62.8281 | 59.8846 | -0.098572 | -0.0014377 | -0.0085641 | 2.8937 | -0.0014527 | -0.00099116 | -0.00076267 | -0.070465 | 0.1616 | 0.13029 | -0.0059302 | 0.056678 | 0.10244 | 0.0015551 | 0.032043 | 0.054932 | -0.045776 | 0.032043 | 0.14648 | 0.054932 | 0.10071 | 0.6546 | 59.8206 | -62.8647 | 59.9945 | 60.1044 | 59.9258 | 0.39825 | 62.7823 | -59.8297 | -59.8526 | 62.9745 | 62.9288 | 62.883 | 0.14648 | 0.10071 | -0.036621 | -0.064087 | 0.10986 | 122.9324 | 63.2263 | 122.7539 | 63.2629 | 122.7905 | 0.19226 | 0.077819 | 122.9691 | 122.8592 | 0.10071 | 122.6852 | 62.883 | 122.6486 | -59.9304 | -122.7493 | 62.8601 | 122.8226 | 62.8601 | 63.4827
2029.8906 | 123.0148 | -62.8784 | 59.8755 | -0.068054 | -0.0012241 | -0.0085641 | 2.893 | -0.0027343 | -0.00013676 | -0.00076267 | -0.076569 | 0.16331 | 0.12815 | -0.0022986 | 0.057747 | 0.10222 | -0.0020765 | -0.041199 | 0.027466 | -0.11444 | -0.036621 | 0.036621 | -0.045776 | 0 | 0.47607 | 59.8343 | -62.8693 | 59.9258 | 60.0266 | 59.8297 | 0.31586 | 62.764 | -59.848 | -59.9121 | 62.915 | 62.8784 | 62.8326 | 0.11444 | 0.068665 | 0.009155 | -0.041198 | 0.050354 | 122.905 | 63.1943 | 122.7081 | 63.1851 | 122.699 | 0.15106 | 0.07782 | 122.8958 | 122.7951 | 0.14191 | 122.7036 | 62.9059 | 122.7127 | -59.9899 | -122.7448 | 62.8418 | 122.8043 | 62.8372 | 63.3545
2030.8281 | 122.9324 | -62.8006 | 59.8663 | -0.029907 | -0.00036966 | -0.0094187 | 2.8918 | -0.0027343 | -0.0012048 | -0.0016171 | -0.06131 | 0.16096 | 0.12858 | -0.0050756 | 0.053688 | 0.10585 | -0.0022901 | 0.07782 | 0.068665 | -0.018311 | 0.073242 | 0.18768 | 0.091553 | 0.11902 | 0.66834 | 59.8343 | -62.8418 | 59.9213 | 60.3378 | 60.0952 | 0.54474 | 62.7823 | -59.7977 | -59.7931 | 62.9883 | 62.9196 | 62.8922 | 0.13733 | 0.10986 | -0.041199 | -0.032043 | 0.054932 | 123.1384 | 63.3453 | 122.8958 | 63.3865 | 122.937 | 0.20599 | 0.091553 | 123.1796 | 122.7631 | 0.086976 | 122.6761 | 62.8693 | 122.6349 | -59.8846 | -122.7081 | 62.8738 | 122.7219 | 62.8784 | 63.4689
2031.8906 | 122.8958 | -62.8784 | 59.9075 | -0.052796 | 0.00048494 | -0.0079233 | 2.893 | 0.0043151 | -0.00077756 | -0.0054623 | -0.18643 | 0.16288 | 0.12773 | -0.0012304 | 0.055397 | 0.10457 | -0.0035719 | -0.064087 | 0.064087 | -0.13275 | -0.16479 | -0.10529 | -0.1831 | -0.11902 | 0.35706 | 59.816 | -62.9288 | 59.8526 | 59.9075 | 59.7153 | 0.2243 | 62.7457 | -59.8434 | -60.0723 | 62.7731 | 62.7594 | 62.6953 | 0.013732 | -0.050354 | -0.050354 | -0.091553 | -0.054932 | 122.786 | 63.1027 | 122.5937 | 63.1531 | 122.644 | 0.027465 | -0.032044 | 122.8363 | 122.7814 | 0.19684 | 122.7448 | 62.9425 | 122.6944 | -60.0403 | -122.8363 | 62.7136 | 122.731 | 62.8143 | 63.2355
2032.8281 | 123.0652 | -62.8189 | 59.8755 | -0.007019 | -0.0014377 | -0.0083505 | 2.8905 | -0.00081171 | -0.0012048 | 0.0022281 | -0.058258 | 0.16267 | 0.12773 | -0.0044348 | 0.056038 | 0.10415 | 0.00091433 | 0.032043 | 0.045776 | -0.027466 | 0.068665 | 0.19684 | 0.09613 | 0.12817 | 0.65918 | 59.8434 | -62.8464 | 59.9899 | 60.1089 | 59.9304 | 0.42572 | 62.7914 | -59.8297 | -59.8068 | 63.0157 | 62.9471 | 62.915 | 0.15564 | 0.1236 | -0.027466 | -0.032043 | 0.11444 | 122.9279 | 63.2446 | 122.7493 | 63.2721 | 122.7768 | 0.2243 | 0.096131 | 122.9553 | 122.8363 | 0.073242 | 122.6898 | 62.8647 | 122.6624 | -59.903 | -122.7219 | 62.8876 | 122.8088 | 62.851 | 63.4781
2033.8906 | 122.9965 | -62.8418 | 59.8618 | -0.075684 | -0.00079686 | -0.0074961 | 2.8918 | -0.0018799 | 7.6842e-05 | -0.0016171 | -0.094879 | 0.16245 | 0.13115 | -0.0061438 | 0.05561 | 0.10244 | -0.0029309 | -0.064087 | -0.004578 | -0.11444 | -0.068665 | 0.022888 | -0.064087 | 0.004578 | 0.48065 | 59.8343 | -62.883 | 59.9304 | 60.022 | 59.8251 | 0.3067 | 62.7274 | -59.8663 | -59.9304 | 62.8647 | 62.8464 | 62.7777 | 0.11902 | 0.050354 | -0.041199 | -0.027465 | 0.068665 | 122.8638 | 63.1485 | 122.6669 | 63.1897 | 122.7081 | 0.13733 | 0.045776 | 122.905 | 122.8134 | 0.10986 | 122.7173 | 62.8372 | 122.6761 | -59.9762 | -122.7448 | 62.7731 | 122.7722 | 62.7777 | 63.3224
2034.8281 | 122.9965 | -62.8281 | 59.8846 | -0.022278 | -0.0010105 | -0.0087777 | 2.8943 | -0.0070069 | -0.00035036 | -0.00012167 | -0.13455 | 0.16395 | 0.12773 | -0.0050756 | 0.055183 | 0.10393 | -0.0010083 | 0.045776 | 0.064087 | -0.009155 | 0.009155 | -0.27466 | 0.041199 | 0.1236 | 0.66834 | 59.8343 | -62.851 | 59.9625 | 60.0769 | 59.8984 | 0.41199 | 62.8189 | -59.8206 | -59.8755 | 62.5534 | 62.9517 | 62.8693 | 0.13275 | 0.050354 | -0.022888 | -0.050354 | 0.077819 | 122.905 | 63.2401 | 122.7264 | 63.2629 | 122.7493 | -0.2655 | 0.01831 | 122.9279 | 122.8134 | 0.073242 | 122.6852 | 62.8922 | 122.6624 | -59.8938 | -122.7356 | 62.8372 | 122.7905 | 62.8738 | 63.4964
2035.8906 | 123.0331 | -62.8281 | 59.8572 | 0.00061049 | 5.7742e-05 | -0.0087777 | 2.893 | -0.00059811 | -0.0027002 | -0.0018307 | -0.073517 | 0.16352 | 0.12773 | -0.0076392 | 0.056251 | 0.10628 | 0.0013415 | 0.009155 | 0.036621 | -0.064087 | 0.009155 | 0.09613 | 0.018311 | 0.082397 | 0.59967 | 59.7977 | -62.8418 | 59.9625 | 60.0723 | 59.8892 | 0.39368 | 62.764 | -59.8206 | -59.848 | 62.9242 | 62.9105 | 62.8464 | 0.14648 | 0.082398 | -0.013733 | -0.05951 | 0.10529 | 122.9004 | 63.2217 | 122.7173 | 63.2355 | 122.731 | 0.16022 | 0.073242 | 122.9141 | 122.8043 | 0.10071 | 122.6395 | 62.8647 | 122.6257 | -59.9213 | -122.699 | 62.8372 | 122.7905 | 62.8372 | 63.4277
2036.8281 | 123.0515 | -62.8281 | 59.8801 | 0.00824 | -0.0027195 | -0.0072825 | 2.8935 | 0.0036743 | -0.00013676 | -0.0016171 | -0.0002747 | 0.16395 | 0.12986 | -0.0035802 | 0.055183 | 0.10265 | -0.0031445 | 0.064087 | 0.068665 | -0.022888 | 0.07782 | 0.18768 | 0.059509 | 0.10071 | 0.76904 | 59.8709 | -62.8418 | 59.9899 | 60.0677 | 59.9121 | 0.41199 | 62.8052 | -59.8114 | -59.8022 | 63.0157 | 62.9288 | 62.8876 | 0.1236 | 0.082397 | -0.013733 | -0.009155 | 0.10986 | 122.8958 | 63.2401 | 122.7402 | 63.2538 | 122.7539 | 0.21057 | 0.10071 | 122.9095 | 122.8317 | 0.091553 | 122.7127 | 62.8967 | 122.699 | -59.903 | -122.7219 | 62.9059 | 122.818 | 62.8922 | 63.5971
2037.8906 | 123.0103 | -62.8418 | 59.8663 | -0.090943 | -0.00036966 | -0.0074961 | 2.8941 | 0.0041015 | -0.0024866 | -0.0016171 | -0.11319 | 0.16331 | 0.12709 | -0.0022986 | 0.056678 | 0.10329 | -0.0016493 | -0.036621 | 0.013733 | -0.07782 | -0.041199 | 0.045776 | -0.068665 | -0.027466 | 0.52643 | 59.8251 | -62.8693 | 59.9579 | 60.022 | 59.8251 | 0.27924 | 62.764 | -59.8526 | -59.9075 | 62.8876 | 62.8143 | 62.7731 | 0.050354 | 0.009155 | -0.027466 | -0.041199 | 0.091553 | 122.8638 | 63.121 | 122.6669 | 63.1485 | 122.6944 | 0.1236 | 0.036621 | 122.8912 | 122.8271 | 0.091553 | 122.6944 | 62.8555 | 122.6669 | -59.9442 | -122.7356 | 62.8006 | 122.7997 | 62.8052 | 63.3682
2038.8281 | 122.9965 | -62.851 | 59.8892 | 0.038757 | -0.00058326 | -0.0064279 | 2.8939 | 0.00068369 | -0.0018458 | -0.0024717 | -0.10403 | 0.16288 | 0.12709 | -0.0035802 | 0.054542 | 0.10137 | -0.0033581 | 0.064087 | 0.050354 | -0.032043 | 0.064087 | 0.16022 | 0.050354 | 0.091553 | 0.63171 | 59.8389 | -62.8418 | 59.9442 | 60.0449 | 59.8618 | 0.40283 | 62.8189 | -59.8389 | -59.8251 | 63.0112 | 62.9425 | 62.9013 | 0.1236 | 0.082397 | 0.009155 | -0.050354 | 0.054932 | 122.8958 | 63.2538 | 122.7127 | 63.2446 | 122.7036 | 0.19226 | 0.09613 | 122.8867 | 122.7859 | 0.082397 | 122.6807 | 62.9013 | 122.6898 | -59.9213 | -122.731 | 62.915 | 122.7951 | 62.915 | 63.4827
2039.8906 | 122.9279 | -62.8922 | 59.8801 | -0.060425 | -0.00079686 | -0.0085641 | 2.8947 | 0.0055969 | -0.0016322 | -0.0014035 | -0.19559 | 0.16459 | 0.1273 | -0.00037605 | 0.056678 | 0.10585 | -0.0044263 | -0.073242 | 0.050354 | -0.1236 | -0.14191 | -0.091553 | -0.17853 | -0.12817 | 0.38452 | 59.8618 | -62.9196 | 59.8663 | 59.8892 | 59.7061 | 0.20142 | 62.7686 | -59.8297 | -60.022 | 62.8006 | 62.764 | 62.7136 | -0.004578 | -0.054932 | -0.027466 | -0.018311 | -0.013733 | 122.7814 | 63.0936 | 122.5983 | 63.121 | 122.6257 | 0.032043 | -0.018311 | 122.8088 | 122.7859 | 0.17395 | 122.7814 | 62.9425 | 122.7539 | -60.0037 | -122.7997 | 62.7502 | 122.7585 | 62.8189 | 63.2767
2040.8281 | 123.0652 | -62.8281 | 59.8938 | -0.037537 | -0.0012241 | -0.0089913 | 2.8907 | 0.00089729 | -0.0029138 | -0.0035397 | -0.067413 | 0.16224 | 0.12773 | -0.0022986 | 0.057533 | 0.10415 | -0.0031445 | 0.004578 | 0.064087 | -0.054932 | 0.009155 | 0.12817 | 0.018311 | 0.073242 | 0.59967 | 59.816 | -62.8601 | 59.9808 | 60.0677 | 59.9533 | 0.40741 | 62.7731 | -59.8297 | -59.8846 | 62.9562 | 62.9013 | 62.8464 | 0.12817 | 0.073243 | -0.032043 | -0.07782 | 0.086975 | 122.8958 | 63.2355 | 122.7814 | 63.2675 | 122.8134 | 0.18311 | 0.064087 | 122.9279 | 122.8409 | 0.11902 | 122.6761 | 62.8922 | 122.644 | -59.9487 | -122.7539 | 62.8372 | 122.8088 | 62.8326 | 63.4277
2041.8906 | 123.0057 | -62.8326 | 59.8618 | -0.1062 | 0.00027134 | -0.0094187 | 2.8935 | -0.0020935 | 0.00029044 | 0.0011599 | -0.082672 | 0.16309 | 0.12602 | -0.0016576 | 0.057106 | 0.10607 | 0.00070073 | -0.050354 | -0.022888 | -0.13733 | -0.059509 | 0.032043 | -0.091553 | -0.013733 | 0.50354 | 59.7885 | -62.8967 | 59.9167 | 59.9945 | 59.8022 | 0.25635 | 62.6953 | -59.8846 | -59.9213 | 62.8647 | 62.8189 | 62.7411 | 0.1236 | 0.045776 | -0.064087 | -0.073242 | 0.054932 | 122.8271 | 63.089 | 122.6349 | 63.1531 | 122.699 | 0.16937 | 0.07782 | 122.8912 | 122.8134 | 0.11444 | 122.6852 | 62.8098 | 122.6212 | -59.9991 | -122.7585 | 62.7731 | 122.7493 | 62.7823 | 63.3362
2042.8281 | 123.0423 | -62.8235 | 59.8663 | 0.069275 | -0.0018649 | -0.0057871 | 2.893 | -0.00081171 | -0.00056396 | -0.0022581 | -0.088776 | 0.16288 | 0.12773 | -0.0069982 | 0.055397 | 0.10329 | -0.0012219 | -0.34332 | 0.09613 | 0 | 0.018311 | 0.13733 | 0.10071 | 0.11902 | 0.66834 | 59.8206 | -62.851 | 59.967 | 60.0769 | 59.8709 | 0.42572 | 62.8235 | -59.7702 | -59.848 | 62.9608 | 62.9425 | 62.9242 | 0.11902 | 0.10071 | -0.027466 | -0.045776 | 0.10071 | 122.9004 | 63.2492 | 122.6944 | 63.2767 | 122.7219 | 0.13733 | 0.018311 | 122.9279 | 122.818 | 0.09613 | 122.6715 | 62.9196 | 122.644 | -59.8663 | -122.7173 | 62.8418 | 122.7905 | 62.4802 | 63.4918
2043.8906 | 122.9416 | -62.8601 | 59.9304 | -0.022278 | -0.0010105 | -0.010059 | 2.8941 | 0.0049561 | -0.0012048 | -0.0014035 | -0.14066 | 0.16309 | 0.12901 | 0.0096644 | 0.054969 | 0.10436 | -0.0037855 | -0.027466 | 0.17853 | -0.041199 | -0.041199 | 0.045776 | -0.022888 | 0.018311 | 0.53101 | 59.8846 | -62.8784 | 59.8801 | 59.967 | 59.7885 | 0.3479 | 62.8189 | -59.7519 | -59.9716 | 62.9059 | 62.8784 | 62.8372 | 0.05951 | 0.018311 | -0.018311 | -0.045776 | -0.050354 | 122.8271 | 63.208 | 122.6486 | 63.2263 | 122.6669 | 0.086975 | 0 | 122.8455 | 122.7585 | 0.21973 | 122.7631 | 63.0386 | 122.7448 | -59.9716 | -122.8088 | 62.8189 | 122.7402 | 62.8326 | 63.3911
2044.8281 | 123.0148 | -62.8189 | 59.8801 | 0.00061049 | -0.0044285 | -0.0085641 | 2.8907 | -0.0010253 | 0.00050424 | -0.00033547 | -0.067413 | 0.16331 | 0.12687 | -0.0033666 | 0.05561 | 0.10308 | -0.0020765 | 0.064087 | 0.086975 | -0.009155 | -0.22888 | 0.22888 | -0.004578 | -0.045776 | 0.64545 | 59.8297 | -62.8555 | 59.9808 | 60.0769 | 59.9121 | 0.42114 | 62.8098 | -59.7931 | -60.1089 | 63.0478 | 62.7731 | 62.8143 | -0.036621 | 0.004577 | -0.036621 | -0.050354 | 0.10071 | 122.8958 | 63.2401 | 122.731 | 63.2767 | 122.7676 | 0.23804 | -0.21973 | 122.9324 | 122.8363 | 0.09613 | 122.6852 | 62.9059 | 122.6486 | -59.8892 | -122.7356 | 62.59 | 122.7997 | 62.883 | 63.4644
2045.8906 | 123.0423 | -62.851 | 59.8526 | -0.075684 | -0.0012241 | -0.0077097 | 2.8956 | 0.0053833 | -0.002273 | -0.0022581 | -0.27188 | 0.16352 | 0.12431 | -0.00058965 | 0.053688 | 0.10521 | -0.00058107 | -0.032043 | -0.022888 | -0.12817 | -0.050354 | 0.064087 | -0.064087 | -0.018311 | 0.66376 | 59.7656 | -62.8693 | 59.9762 | 60.0449 | 59.8343 | 0.27466 | 62.7228 | -59.8755 | -59.903 | 62.915 | 62.8326 | 62.7869 | 0.10986 | 0.064087 | -0.018311 | -0.086975 | 0.1236 | 122.8958 | 63.1256 | 122.6852 | 63.1439 | 122.7036 | 0.19226 | 0.07782 | 122.9141 | 122.8455 | 0.10529 | 122.6349 | 62.8281 | 122.6166 | -59.9808 | -122.7219 | 62.8006 | 122.8271 | 62.8189 | 63.5147
2046.8281 | 123.0286 | -62.8143 | 59.8663 | -0.083313 | -0.00015586 | -0.0070687 | 2.8918 | -0.0012391 | -0.0018458 | -0.0031125 | 0.0088807 | 0.16202 | 0.12922 | -0.0050756 | 0.05796 | 0.10436 | 0.0015551 | 0.050354 | 0.073242 | -0.041199 | 0.068665 | 0.17395 | 0.068665 | 0.17395 | 0.43945 | 59.848 | -62.8738 | 59.9716 | 60.0815 | 59.9487 | 0.42572 | 62.7731 | -59.7931 | -59.7977 | 62.9883 | 62.9883 | 62.883 | 0.21515 | 0.10986 | -0.059509 | -0.018311 | 0.10529 | 122.8958 | 63.2401 | 122.7631 | 63.2996 | 122.8226 | 0.21515 | 0.10986 | 122.9553 | 122.8455 | 0.11444 | 122.7219 | 62.8876 | 122.6624 | -59.9075 | -122.7402 | 62.883 | 122.7859 | 62.8647 | 63.2538
2047.8906 | 122.9691 | -62.8784 | 59.8984 | 0.046386 | -0.0016513 | -0.0077097 | 2.8933 | -0.00038451 | -0.0027002 | 9.193e-05 | -0.15591 | 0.1648 | 0.12751 | -0.0046484 | 0.05561 | 0.10543 | -0.0022901 | -0.12817 | 0.045776 | -0.1236 | -0.15564 | -0.086975 | -0.16937 | -0.09613 | 0.42114 | 59.848 | -62.8967 | 59.8892 | 59.9304 | 59.7565 | 0.2243 | 62.7548 | -59.8526 | -60.054 | 62.7914 | 62.7823 | 62.709 | 0.027466 | -0.045777 | -0.018311 | -0.050354 | -0.009155 | 122.8088 | 63.1027 | 122.6349 | 63.121 | 122.6532 | 0.036621 | -0.032044 | 122.8271 | 122.7859 | 0.16937 | 122.7448 | 62.9242 | 122.7264 | -60.022 | -122.7951 | 62.7228 | 122.7676 | 62.7502 | 63.2996
2048.8438 | 123.0377 | -62.8281 | 59.8114 | -0.045166 | -0.0010105 | -0.0087777 | 2.8937 | 0.0021789 | 0.002213 | -0.00076267 | -0.14066 | 0.16331 | 0.12944 | -0.0044348 | 0.058174 | 0.10756 | -0.0018629 | -0.10071 | -0.009155 | -0.15106 | -0.1236 | -0.018311 | -0.13275 | -0.082397 | 0.4715 | 59.8251 | -62.8876 | 59.9442 | 60.0174 | 59.8297 | 0.27008 | 62.677 | -59.8206 | -59.935 | 62.8098 | 62.7457 | 62.6953 | 0.068665 | 0.018311 | -0.059509 | 0.013733 | 0.13275 | 122.8455 | 63.0981 | 122.6578 | 63.1577 | 122.7173 | 0.13275 | 0.027466 | 122.905 | 122.8317 | 0.14191 | 122.7127 | 62.8189 | 122.6532 | -59.9625 | -122.699 | 62.7045 | 122.7722 | 62.7274 | 63.2996
2049.8906 | 123.0331 | -62.8555 | 59.8663 | -0.022278 | -0.00079686 | -0.0092051 | 2.8918 | 0.0011109 | -0.0012048 | -0.0052487 | -0.076569 | 0.16288 | 0.1288 | -0.0074254 | 0.056892 | 0.10415 | -0.0010083 | -0.018311 | 0.045776 | -0.082397 | -0.018311 | 0.09613 | -0.004578 | 0.050354 | 0.55389 | 59.8114 | -62.851 | 59.9533 | 60.0449 | 59.8755 | 0.37537 | 62.7731 | -59.8206 | -59.8846 | 62.9517 | 62.9059 | 62.851 | 0.13275 | 0.077819 | 0.004578 | -0.054932 | 0.086975 | 122.9004 | 63.2309 | 122.731 | 63.2263 | 122.7264 | 0.17853 | 0.064086 | 122.8958 | 122.8043 | 0.12817 | 122.6624 | 62.9013 | 122.6669 | -59.9487 | -122.7173 | 62.8372 | 122.8088 | 62.8372 | 63.4094
2050.8281 | 123.0103 | -62.8235 | 59.8984 | -0.052796 | -0.0014377 | -0.0074961 | 2.8928 | 0.0011109 | -0.0012048 | -0.00033547 | -0.091827 | 0.16138 | 0.12965 | -0.0091344 | 0.057319 | 0.10479 | -0.0039991 | 0.054932 | 0.045776 | -0.054932 | 0.059509 | 0.15106 | 0.068665 | 0.091553 | 0.64545 | 59.8206 | -62.8464 | 59.935 | 60.0586 | 59.8755 | 0.42572 | 62.7686 | -59.8526 | -59.8389 | 62.9745 | 62.915 | 62.8922 | 0.14649 | 0.1236 | -0.022889 | -0.077819 | 0.036622 | 122.8821 | 63.2492 | 122.699 | 63.2721 | 122.7219 | 0.20599 | 0.11444 | 122.905 | 122.7814 | 0.10071 | 122.6669 | 62.8693 | 122.644 | -59.9533 | -122.7448 | 62.883 | 122.7585 | 62.8784 | 63.4689
2051.8281 | 122.9782 | -62.8555 | 59.935 | 0.015869 | -0.0020785 | -0.0096323 | 2.8939 | 0.00068369 | -0.0027002 | 0.00073273 | -0.14981 | 0.16224 | 0.1288 | -0.0025122 | 0.056038 | 0.10479 | -0.0039991 | 0.022888 | 0.11902 | -0.059509 | -0.027466 | 0.045776 | -0.018311 | 0.036621 | 0.52643 | 59.8663 | -62.8693 | 59.9075 | 59.9899 | 59.7977 | 0.38452 | 62.796 | -59.816 | -59.9625 | 62.9013 | 62.8922 | 62.8372 | 0.09613 | 0.041198 | -0.013733 | -0.068665 | -0.027466 | 122.8455 | 63.2401 | 122.6532 | 63.2538 | 122.6669 | 0.10528 | 0.032043 | 122.8592 | 122.7768 | 0.17853 | 122.7356 | 62.9745 | 122.7219 | -59.9945 | -122.8043 | 62.8281 | 122.7631 | 62.8784 | 63.382
2052.8906 | 122.9919 | -62.8601 | 59.8755 | -0.029907 | -0.0016513 | -0.0085641 | 2.8915 | 0.0034607 | 0.00071784 | -0.00097627 | -0.076569 | 0.16267 | 0.1288 | -0.011271 | 0.057747 | 0.10265 | 0.0036913 | -0.041199 | 0.004578 | -0.091553 | -0.068665 | 0.027466 | -0.045776 | -0.013733 | 0.49896 | 59.8114 | -62.8922 | 60.0174 | 59.935 | 59.8343 | 0.32959 | 62.7686 | -59.8709 | -59.9442 | 62.8876 | 62.8464 | 62.8143 | 0.07782 | 0.045777 | -0.032044 | -0.064087 | 0.14191 | 122.7951 | 63.1897 | 122.6944 | 63.2217 | 122.7264 | 0.11902 | 0.022888 | 122.8271 | 122.9095 | 0.096131 | 122.7036 | 62.8647 | 122.6715 | -59.967 | -122.7676 | 62.7914 | 122.8775 | 62.8189 | 63.3591
2053.8438 | 123.024 | -62.8464 | 59.8618 | -0.1062 | -0.0012241 | -0.0107 | 2.8941 | 0.0047425 | -0.00056396 | -0.00012167 | -0.1315 | 0.16416 | 0.12538 | 5.1352e-05 | 0.055824 | 0.10415 | -0.0022901 | -0.091553 | -0.009155 | -0.15106 | -0.11902 | -0.050354 | -0.14648 | -0.068665 | 0.45776 | 59.8389 | -62.8922 | 59.9258 | 60.0037 | 59.8114 | 0.2655 | 62.6953 | -59.8709 | -59.9808 | 62.796 | 62.7777 | 62.6999 | 0.082397 | 0.004578 | -0.045776 | -0.022888 | 0.064087 | 122.85 | 63.1119 | 122.6578 | 63.1577 | 122.7036 | 0.10071 | 0.032043 | 122.8958 | 122.818 | 0.14191 | 122.731 | 62.8372 | 122.6852 | -60.0128 | -122.7539 | 62.7274 | 122.7722 | 62.7548 | 63.3041
2054.8906 | 123.0286 | -62.8372 | 59.8618 | -0.045166 | -0.00015586 | -0.0083505 | 2.892 | -0.0025207 | -0.0016322 | -0.00012167 | -0.06131 | 0.16331 | 0.12837 | -0.0040076 | 0.057106 | 0.1035 | 0.0017687 | -0.022888 | 0.018311 | -0.091553 | -0.032043 | 0.086975 | -0.018311 | 0.050354 | 0.56305 | 59.8297 | -62.8418 | 59.9579 | 60.0677 | 59.8709 | 0.37537 | 62.7457 | -59.8434 | -59.8938 | 62.9242 | 62.8876 | 62.8189 | 0.14191 | 0.073242 | -0.004578 | -0.032043 | 0.096131 | 122.905 | 63.2126 | 122.7081 | 63.2172 | 122.7127 | 0.17853 | 0.05951 | 122.9095 | 122.7997 | 0.10986 | 122.6715 | 62.8555 | 122.6669 | -59.9533 | -122.7036 | 62.8052 | 122.7951 | 62.8143 | 63.4003
2055.8281 | 122.9736 | -62.8464 | 59.9304 | 0.00061049 | 5.7742e-05 | -0.010914 | 2.8943 | -0.00059811 | -0.003982 | -0.0014035 | -0.1315 | 0.16437 | 0.12602 | -0.0044348 | 0.055183 | 0.10607 | -0.0027173 | 0.032043 | 0.10986 | -0.045776 | -0.018311 | 0.036621 | -0.036621 | 0.009155 | 0.53558 | 59.8755 | -62.8784 | 59.9075 | 60.0037 | 59.8206 | 0.37537 | 62.8006 | -59.8206 | -59.9487 | 62.883 | 62.8555 | 62.8098 | 0.054931 | 0.009155 | -0.032043 | -0.054932 | -0.022888 | 122.85 | 63.2217 | 122.6669 | 63.2538 | 122.699 | 0.082397 | 0.027465 | 122.8821 | 122.786 | 0.15564 | 122.7539 | 62.9562 | 122.7219 | -59.9762 | -122.8088 | 62.8281 | 122.7539 | 62.8784 | 63.382
2056.8906 | 123.0194 | -62.8647 | 59.8618 | -0.12909 | -0.0012241 | -0.0070687 | 2.8939 | -0.0010253 | 0.00093144 | -0.0028989 | -0.076569 | 0.16267 | 0.12858 | -0.002085 | 0.056251 | 0.10457 | 0.00091433 | -0.073242 | -0.013733 | -0.10986 | -0.073242 | 0.022888 | -0.086975 | 0 | 0.4715 | 59.8114 | -62.9105 | 59.9258 | 59.9945 | 59.8206 | 0.28381 | 62.7548 | -59.8755 | -59.935 | 62.8876 | 62.8647 | 62.7777 | 0.10986 | 0.022888 | -0.045776 | -0.050354 | 0.064087 | 122.8592 | 63.1485 | 122.6852 | 63.1943 | 122.731 | 0.13275 | 0.036621 | 122.905 | 122.8363 | 0.09613 | 122.7219 | 62.851 | 122.6761 | -59.9716 | -122.7722 | 62.7914 | 122.7905 | 62.7914 | 63.3362
2057.8281 | 122.9599 | -62.851 | 59.9075 | -0.014649 | -0.00036966 | -0.0081369 | 2.893 | 0.0023925 | -0.00056396 | -0.0014035 | -0.16507 | 0.16566 | 0.1288 | 0.0021876 | 0.056678 | 0.10564 | 0.0039049 | -0.12817 | 0.064087 | -0.09613 | -0.032043 | 0.045776 | -0.054932 | 0.004578 | 0.54016 | 59.8389 | -62.8967 | 59.903 | 59.9762 | 59.7885 | 0.32959 | 62.7548 | -59.8434 | -59.9396 | 62.8967 | 62.8555 | 62.796 | 0.10071 | 0.041198 | -0.045777 | -0.068665 | -0.004578 | 122.8271 | 63.1805 | 122.6395 | 63.2263 | 122.6852 | 0.14191 | 0.064087 | 122.8729 | 122.7997 | 0.16022 | 122.7356 | 62.915 | 122.6898 | -60.0037 | -122.8043 | 62.8189 | 122.7539 | 62.7228 | 63.3911
2058.9062 | 122.9736 | -62.8784 | 59.8709 | -0.060425 | 0.00048494 | -0.0081369 | 2.893 | 0.00046989 | -0.0024866 | -0.0024717 | -0.13455 | 0.16309 | 0.12858 | -0.0057166 | 0.05561 | 0.10415 | 0.00070073 | -0.11444 | 0.022888 | -0.15106 | -0.13733 | -0.050354 | -0.1831 | -0.11444 | 0.42114 | 59.8572 | -62.8967 | 59.9075 | 59.9533 | 59.761 | 0.23346 | 62.7274 | -59.848 | -60.0082 | 62.8281 | 62.764 | 62.6953 | 0.036621 | -0.032043 | -0.018311 | -0.013733 | 0.036621 | 122.8317 | 63.1119 | 122.6395 | 63.1302 | 122.6578 | 0.10071 | 0.013733 | 122.85 | 122.8043 | 0.17395 | 122.7539 | 62.9013 | 122.7356 | -60.022 | -122.7676 | 62.7411 | 122.786 | 62.764 | 63.2996
2059.8281 | 122.9736 | -62.8601 | 59.903 | 0.00061049 | 5.7742e-05 | -0.0070687 | 2.8947 | -0.00081171 | -0.0018458 | 0.00094633 | -0.1315 | 0.16395 | 0.12794 | -0.0035802 | 0.059028 | 0.10564 | 0.0013415 | 0.018311 | 0.10986 | -0.064087 | -0.041199 | 0.050354 | -0.032043 | 0.009155 | 0.56763 | 59.8572 | -62.883 | 59.9442 | 60.0082 | 59.8114 | 0.33875 | 62.796 | -59.7931 | -59.9442 | 62.9105 | 62.8693 | 62.8281 | 0.073242 | 0.032044 | -0.022889 | -0.045776 | 0.041199 | 122.8683 | 63.1989 | 122.6715 | 63.2217 | 122.6944 | 0.11444 | 0.022888 | 122.8912 | 122.8271 | 0.17395 | 122.7402 | 62.97 | 122.7173 | -59.967 | -122.7859 | 62.8189 | 122.8043 | 62.8784 | 63.4277
2060.8281 | 122.9233 | -62.8693 | 59.9213 | 0.00061049 | -0.0031467 | -0.0083505 | 2.8933 | -0.00038451 | -0.0020594 | -0.0014035 | -0.07962 | 0.1616 | 0.1273 | -0.0072118 | 0.057106 | 0.10607 | -0.0029309 | 0.022888 | 0.1236 | -0.022888 | -0.036621 | 0.064087 | -0.018311 | 0.022888 | 0.54474 | 59.8709 | -62.8922 | 59.8709 | 59.967 | 59.7885 | 0.34332 | 62.8464 | -59.7977 | -59.9579 | 62.9333 | 62.8922 | 62.851 | 0.045776 | 0.004577 | -0.022888 | -0.050354 | -0.050354 | 122.8363 | 63.2126 | 122.6578 | 63.2355 | 122.6807 | 0.086975 | -0.013733 | 122.8592 | 122.7631 | 0.14648 | 122.7631 | 62.9929 | 122.7402 | -59.9442 | -122.8134 | 62.8326 | 122.7402 | 62.8922 | 63.414
2061.8906 | 123.0148 | -62.8326 | 59.8572 | -0.11383 | -0.0037875 | -0.0085641 | 2.8915 | 0.0026063 | -0.0014184 | -0.0016171 | -0.073517 | 0.16352 | 0.1288 | -0.0016576 | 0.057533 | 0.10329 | 5.9726e-05 | -0.036621 | 0.018311 | -0.086975 | -0.059509 | 0.064087 | -0.082397 | -0.018311 | 0.54016 | 59.7931 | -62.8922 | 59.9442 | 60.0128 | 59.8434 | 0.28381 | 62.7457 | -59.8389 | -59.9167 | 62.8967 | 62.8143 | 62.7502 | 0.068664 | 0.004578 | -0.059509 | -0.064087 | 0.086975 | 122.8455 | 63.1165 | 122.6761 | 63.176 | 122.7356 | 0.15106 | 0.027466 | 122.905 | 122.8363 | 0.10529 | 122.6852 | 62.851 | 122.6257 | -59.9442 | -122.7493 | 62.7731 | 122.7768 | 62.796 | 63.3728
2062.8281 | 122.9187 | -62.8372 | 59.9213 | 0.00824 | -0.00079686 | -0.0107 | 2.8915 | 0.00025629 | -0.0035548 | -0.00054907 | -0.088776 | 0.1648 | 0.12751 | -0.0033666 | 0.05796 | 0.10244 | 0.0011279 | 0.004578 | 0.12817 | -0.045776 | -0.032043 | 0.064087 | -0.018311 | 0.013733 | 0.53558 | 59.8938 | -62.8922 | 59.8755 | 59.9579 | 59.7885 | 0.34332 | 62.7914 | -59.7931 | -59.9533 | 62.9013 | 62.851 | 62.8189 | 0.059509 | 0.027465 | -0.054932 | -0.027466 | -0.045777 | 122.7951 | 63.1805 | 122.6257 | 63.2355 | 122.6807 | 0.10986 | 0.013733 | 122.85 | 122.7676 | 0.17395 | 122.7859 | 62.9654 | 122.731 | -59.967 | -122.8134 | 62.8052 | 122.7127 | 62.8418 | 63.3728
2063.9062 | 122.8958 | -62.883 | 59.9167 | -0.068054 | -0.0020785 | -0.0066415 | 2.8926 | 4.2692e-05 | -0.0018458 | 0.00073273 | -0.1315 | 0.16331 | 0.12901 | -0.0010168 | 0.055397 | 0.105 | 0.00070073 | -0.082397 | 0.064087 | -0.11444 | -0.15564 | -0.09613 | -0.16022 | -0.10529 | 0.39825 | 59.8709 | -62.9105 | 59.8297 | 59.8755 | 59.6924 | 0.20599 | 62.7686 | -59.8526 | -60.0723 | 62.7869 | 62.7777 | 62.7228 | 0.009155 | -0.045776 | -0.027465 | -0.045776 | -0.086975 | 122.7585 | 63.089 | 122.5754 | 63.1165 | 122.6028 | 0.018311 | -0.041199 | 122.7859 | 122.7402 | 0.17853 | 122.7814 | 62.9471 | 122.7539 | -60.0311 | -122.8271 | 62.7274 | 122.7127 | 62.8006 | 63.2812
2064.8281 | 122.9874 | -62.8372 | 59.9121 | 0.023498 | -0.0014377 | -0.0096323 | 2.8915 | -0.0027343 | -0.0024866 | -0.0028989 | -0.12845 | 0.16267 | 0.12901 | -0.0076392 | 0.056038 | 0.10457 | -0.00058107 | 0.009155 | 0.14191 | -0.041199 | -0.009155 | 0.064087 | 0 | 0.018311 | 0.56763 | 59.8709 | -62.8647 | 59.9213 | 60.0037 | 59.8068 | 0.37537 | 62.796 | -59.7702 | -59.9213 | 62.9013 | 62.8555 | 62.8372 | 0.05951 | 0.041199 | -0.027466 | -0.041198 | 0.009156 | 122.8409 | 63.2126 | 122.644 | 63.2401 | 122.6715 | 0.10529 | 0.032044 | 122.8683 | 122.7859 | 0.18311 | 122.7356 | 62.9791 | 122.7081 | -59.9533 | -122.7768 | 62.8281 | 122.7585 | 62.8464 | 63.4048
2065.8906 | 122.9874 | -62.8098 | 59.9487 | -0.068054 | -0.0020785 | -0.0077097 | 2.8935 | 0.0011109 | 0.0024268 | -0.0020443 | -0.033844 | 0.16331 | 0.12751 | -0.0067846 | 0.054115 | 0.10521 | 0.0011279 | 0.054932 | 0.073242 | -0.059509 | 0.064087 | 0.21515 | 0.086975 | 0.10071 | 0.65918 | 59.8068 | -62.8693 | 59.9716 | 60.1044 | 59.8984 | 0.44861 | 62.7502 | -59.8755 | -59.8846 | 63.0249 | 62.9105 | 62.8967 | 0.16022 | 0.14648 | -0.05951 | -0.14191 | 0.022889 | 122.9141 | 63.2584 | 122.7081 | 63.3179 | 122.7676 | 0.27466 | 0.1236 | 122.9736 | 122.8409 | 0.13275 | 122.6761 | 62.883 | 122.6166 | -60.0082 | -122.818 | 62.8738 | 122.7814 | 62.8647 | 63.4689
2066.8281 | 122.937 | -62.8647 | 59.9258 | 0.054016 | 5.7742e-05 | -0.010059 | 2.8915 | 0.00068369 | 0.0015722 | -0.0033261 | -0.10709 | 0.16267 | 0.12623 | -0.00037605 | 0.057319 | 0.10521 | 5.9726e-05 | -0.064087 | 0.17395 | -0.009155 | -0.059509 | 0.045776 | -0.027466 | 0.009155 | 0.52643 | 59.8801 | -62.8738 | 59.8755 | 59.9625 | 59.7977 | 0.36163 | 62.8555 | -59.7519 | -59.9854 | 62.9105 | 62.8738 | 62.8372 | 0.01831 | -0.018311 | -0.009155 | -0.045776 | -0.050354 | 122.8271 | 63.2263 | 122.6624 | 63.2355 | 122.6715 | 0.054931 | -0.050354 | 122.8363 | 122.7493 | 0.1831 | 122.7539 | 63.0386 | 122.7448 | -59.935 | -122.7997 | 62.8052 | 122.7402 | 62.8006 | 63.3911
2067.8906 | 123.0057 | -62.851 | 59.8709 | -0.029907 | -0.0012241 | -0.0077097 | 2.8937 | -0.00038451 | -0.00013676 | -0.0014035 | -0.030792 | 0.16224 | 0.12773 | -0.0029394 | 0.056678 | 0.10415 | 0.0011279 | -0.059509 | 0.027466 | -0.086975 | -0.064087 | 0.022888 | -0.059509 | 0 | 0.48523 | 59.8114 | -62.8601 | 59.9075 | 59.9899 | 59.8251 | 0.31128 | 62.764 | -59.8434 | -59.935 | 62.8738 | 62.851 | 62.7914 | 0.086975 | 0.027466 | -0.009155 | -0.05951 | 0.036621 | 122.8409 | 63.1622 | 122.6761 | 63.1714 | 122.6852 | 0.10986 | 0.022888 | 122.85 | 122.7676 | 0.11444 | 122.6715 | 62.8784 | 122.6624 | -59.9579 | -122.731 | 62.7869 | 122.7585 | 62.7914 | 63.3362
2068.8281 | 122.9279 | -62.8601 | 59.9121 | -0.045166 | -0.00036966 | -0.0092051 | 2.8939 | 0.0034607 | -0.0061182 | -0.00097627 | -0.14371 | 0.1616 | 0.12965 | -0.0044348 | 0.057319 | 0.10628 | 0.00070073 | -0.022888 | 0.073242 | -0.073242 | -0.091553 | -0.009155 | -0.10071 | -0.054932 | 0.50354 | 59.8389 | -62.883 | 59.8755 | 59.935 | 59.7473 | 0.2655 | 62.7869 | -59.8389 | -60.0037 | 62.851 | 62.8052 | 62.7594 | 0.01831 | -0.027466 | -0.022889 | -0.073242 | -0.036621 | 122.7951 | 63.1256 | 122.6074 | 63.1485 | 122.6303 | 0.064087 | -0.018311 | 122.818 | 122.7585 | 0.14648 | 122.7219 | 62.9333 | 122.699 | -59.9854 | -122.7951 | 62.7686 | 122.7356 | 62.8372 | 63.3636
2069.8906 | 122.9416 | -62.8738 | 59.9304 | -0.007019 | -0.00036966 | -0.0087777 | 2.8926 | -0.0033753 | -0.0046228 | -0.00033547 | -0.067413 | 0.16544 | 0.12901 | 0.00026495 | 0.057319 | 0.10393 | -0.0014355 | 0.036621 | 0.14191 | -0.032043 | 0 | 0.064087 | -0.032043 | 0.018311 | 0.54932 | 59.8801 | -62.883 | 59.8709 | 59.9625 | 59.7931 | 0.36163 | 62.8418 | -59.7885 | -59.9304 | 62.9379 | 62.8922 | 62.8418 | 0.050354 | 0 | -0.009156 | -0.050354 | -0.059509 | 122.8363 | 63.2355 | 122.6669 | 63.2446 | 122.6761 | 0.09613 | 0.032043 | 122.8455 | 122.7539 | 0.17395 | 122.7631 | 63.0157 | 122.7539 | -59.9625 | -122.8134 | 62.8738 | 122.7448 | 62.9105 | 63.4232
2070.8281 | 122.9782 | -62.8647 | 59.8801 | -0.014649 | -0.00015586 | -0.0098459 | 2.8924 | 0.0030335 | -0.00077756 | -0.0016171 | -0.1376 | 0.16416 | 0.12815 | 0.0011194 | 0.054756 | 0.10457 | 0.0030505 | 0.009155 | 0.10986 | -0.054932 | -0.009155 | 0.082397 | -0.032043 | 0.018311 | 0.57678 | 59.8663 | -62.8738 | 59.9213 | 60.0128 | 59.8251 | 0.37079 | 62.8098 | -59.7702 | -59.8892 | 62.9471 | 62.883 | 62.8326 | 0.073243 | 0.022889 | -0.009155 | -0.013733 | 0.041199 | 122.8775 | 63.2355 | 122.6898 | 63.2446 | 122.699 | 0.13733 | 0.045777 | 122.8867 | 122.7951 | 0.16479 | 122.7402 | 62.9745 | 122.731 | -59.935 | -122.7539 | 62.8555 | 122.7859 | 62.8738 | 63.4415
2071.8906 | 123.0423 | -62.8326 | 59.9075 | -0.052796 | 0.00091214 | -0.010273 | 2.8922 | 0.00089729 | -0.0020594 | -0.0016171 | -0.06131 | 0.16224 | 0.12794 | -0.0059302 | 0.055183 | 0.10436 | -0.0020765 | 0.059509 | 0.091553 | -0.036621 | -0.027466 | 0.45776 | 0.54016 | -0.018311 | 0.66376 | 59.816 | -62.8601 | 59.9762 | 60.0952 | 59.8984 | 0.43488 | 62.796 | -59.816 | -59.935 | 63.2904 | 62.8143 | 63.3728 | 0.01831 | 0.57678 | -0.027465 | -0.091553 | 0.068664 | 122.9279 | 63.2675 | 122.731 | 63.295 | 122.7585 | 0.49439 | 0.009155 | 122.9553 | 122.8363 | 0.12817 | 122.6761 | 62.9242 | 122.6486 | -59.9442 | -122.7676 | 62.8052 | 122.8088 | 62.8922 | 63.4964
2072.8438 | 123.0103 | -62.8693 | 59.848 | -0.014649 | -0.0016513 | -0.0092051 | 2.8937 | 0.00046989 | -0.0014184 | -0.0046079 | -0.064362 | 0.16395 | 0.12516 | -0.002085 | 0.054756 | 0.10479 | 0.00027333 | -0.045776 | 0.022888 | -0.10071 | -0.07782 | 0.045776 | -0.036621 | 0 | 0.64087 | 59.848 | -62.8738 | 59.9258 | 60.022 | 59.8297 | 0.31586 | 62.7686 | -59.8251 | -59.9258 | 62.915 | 62.8693 | 62.8326 | 0.10071 | 0.064087 | -0.004577 | 0 | 0.07782 | 122.8912 | 63.1851 | 122.699 | 63.1897 | 122.7036 | 0.14648 | 0.022888 | 122.8958 | 122.7997 | 0.1236 | 122.7219 | 62.8922 | 122.7173 | -59.9487 | -122.7219 | 62.7914 | 122.7951 | 62.8235 | 63.5101
2073.8906 | 123.0286 | -62.8235 | 59.8938 | -0.037537 | -0.0031467 | -0.0092051 | 2.889 | 0.00089729 | -0.002273 | 9.193e-05 | -0.039948 | 0.16202 | 0.12452 | 0.00090575 | 0.054969 | 0.10222 | -0.0027173 | 0.068665 | 0.07782 | -0.022888 | -0.3067 | -0.10529 | 0.16022 | 0.045776 | 0.6546 | 59.8251 | -62.851 | 59.9762 | 60.0769 | 59.903 | 0.4303 | 62.8006 | -59.816 | -60.2005 | 62.7182 | 62.8693 | 62.9837 | 0.068664 | 0.1831 | -0.027466 | -0.068665 | 0.082397 | 122.9004 | 63.2538 | 122.7264 | 63.2812 | 122.7539 | -0.082398 | -0.28381 | 122.9279 | 122.8271 | 0.10071 | 122.6761 | 62.9013 | 122.6486 | -59.9167 | -122.7448 | 62.5168 | 122.7997 | 62.8922 | 63.4781
2074.8281 | 122.9141 | -62.8784 | 59.8846 | -0.045166 | 0.00091214 | -0.0072825 | 2.8926 | 0.0032471 | -0.0018458 | -0.0020443 | -0.16812 | 0.16331 | 0.12709 | 0.00069215 | 0.056251 | 0.1035 | -0.0046399 | -0.064087 | 0.059509 | -0.10071 | -0.10071 | -0.032043 | -0.13733 | -0.059509 | 0.46234 | 59.8663 | -62.8738 | 59.8755 | 59.9213 | 59.7382 | 0.24261 | 62.7777 | -59.8251 | -59.9854 | 62.8464 | 62.8189 | 62.7411 | 0.041199 | -0.036621 | 0.004578 | -0.018311 | -0.009156 | 122.7997 | 63.121 | 122.6166 | 63.1165 | 122.612 | 0.068665 | 0 | 122.7951 | 122.7493 | 0.16022 | 122.7402 | 62.9379 | 122.7448 | -59.9854 | -122.7585 | 62.7777 | 122.7539 | 62.8143 | 63.3408
2075.8906 | 122.9233 | -62.851 | 59.9121 | -0.060425 | -0.00036966 | -0.0094187 | 2.893 | -0.00017091 | -0.0027002 | -0.0046079 | -0.094879 | 0.16416 | 0.12965 | -0.0012304 | 0.057319 | 0.10329 | -0.0037855 | -0.018311 | 0.14648 | -0.036621 | -0.041199 | 0.068665 | -0.018311 | 0.032043 | 0.53101 | 59.8938 | -62.8876 | 59.8846 | 59.9442 | 59.7931 | 0.35706 | 62.8143 | -59.7656 | -59.9533 | 62.9196 | 62.883 | 62.8326 | 0.068664 | 0.01831 | -0.036621 | -0.01831 | -0.027465 | 122.7951 | 63.208 | 122.644 | 63.2446 | 122.6807 | 0.10529 | -0.004578 | 122.8317 | 122.7722 | 0.18311 | 122.7814 | 62.9974 | 122.7448 | -59.9487 | -122.7997 | 62.8098 | 122.7356 | 62.8326 | 63.382
2076.8281 | 122.9553 | -62.8555 | 59.8984 | -0.045166 | 0.0019803 | -0.0094187 | 2.8941 | 0.0055969 | -0.0029138 | -0.0016171 | -0.11929 | 0.16202 | 0.12559 | -0.003153 | 0.056465 | 0.10607 | 0.0015551 | -0.018311 | 0.09613 | -0.082397 | -0.036621 | 0.054932 | -0.036621 | 0.009155 | 0.5722 | 59.8618 | -62.883 | 59.9167 | 59.9991 | 59.8114 | 0.3479 | 62.7731 | -59.8022 | -59.935 | 62.9105 | 62.8647 | 62.8189 | 0.091552 | 0.045776 | -0.027466 | -0.036621 | 0.018311 | 122.8546 | 63.2034 | 122.6669 | 63.2309 | 122.6944 | 0.13733 | 0.045776 | 122.8821 | 122.7997 | 0.17853 | 122.7448 | 62.9517 | 122.7173 | -59.9808 | -122.7814 | 62.8189 | 122.7722 | 62.8372 | 63.4277
2077.8906 | 122.9691 | -62.8693 | 59.903 | -0.014649 | -0.00079686 | -0.0083505 | 2.8935 | -0.00038451 | -0.00099116 | -0.0037533 | -0.10403 | 0.16416 | 0.1305 | 0.001974 | 0.05561 | 0.10735 | -0.0029309 | -0.050354 | 0.15564 | -0.022888 | -0.064087 | 0.054932 | -0.013733 | 0.018311 | 0.52643 | 59.8846 | -62.8967 | 59.8801 | 59.9579 | 59.7977 | 0.35706 | 62.8464 | -59.7473 | -59.967 | 62.9242 | 62.8876 | 62.8555 | 0.041199 | 0.009155 | -0.027466 | -0.01831 | -0.022888 | 122.8271 | 63.2263 | 122.6669 | 63.2538 | 122.6944 | 0.07782 | -0.041199 | 122.8546 | 122.7768 | 0.17853 | 122.7814 | 63.0249 | 122.7539 | -59.9258 | -122.7997 | 62.8052 | 122.7493 | 62.8189 | 63.3957
2078.8281 | 122.9507 | -62.8922 | 59.8984 | -0.052796 | -0.0014377 | -0.010487 | 2.8933 | 0.0021789 | -0.00056396 | -0.0033261 | -0.15897 | 0.16395 | 0.12645 | -0.0035802 | 0.057747 | 0.105 | 0.00027333 | 0.013733 | 0.045776 | -0.086975 | -0.068665 | 0.022888 | -0.064087 | -0.013733 | 0.51727 | 59.8618 | -62.8784 | 59.8892 | 59.9716 | 59.7656 | 0.31586 | 62.8052 | -59.8526 | -59.967 | 62.915 | 62.8784 | 62.8281 | 0.073242 | 0.022888 | 0.013733 | -0.036621 | -0.009155 | 122.8638 | 63.208 | 122.6578 | 63.1943 | 122.644 | 0.10986 | 0.01831 | 122.85 | 122.7676 | 0.13275 | 122.7402 | 62.9379 | 122.7539 | -59.9854 | -122.7768 | 62.8235 | 122.7814 | 62.9059 | 63.4094
2079.8281 | 122.9736 | -62.8876 | 59.8846 | -0.045166 | -0.0022923 | -0.010487 | 2.8922 | 0.00046989 | 0.0017858 | -0.00054907 | -0.11319 | 0.16395 | 0.1273 | -0.0040076 | 0.056251 | 0.105 | 0.00048713 | -0.13275 | 0.041199 | -0.11902 | -0.15564 | -0.059509 | -0.16479 | -0.10071 | 0.40741 | 59.816 | -62.8922 | 59.8801 | 59.935 | 59.7656 | 0.23346 | 62.7686 | -59.8434 | -60.0403 | 62.8281 | 62.7869 | 62.7228 | 0.018311 | -0.045776 | -0.004578 | -0.068665 | -0.004578 | 122.8226 | 63.121 | 122.6532 | 63.1256 | 122.6578 | 0.05951 | -0.036621 | 122.8271 | 122.7722 | 0.16022 | 122.7081 | 62.9288 | 122.7036 | -60.0037 | -122.7768 | 62.7319 | 122.7676 | 62.7548 | 63.295
2080.8906 | 122.937 | -62.8693 | 59.9075 | -0.037537 | -0.0012241 | -0.0087777 | 2.8933 | 0.00046989 | -0.0014184 | -0.0026853 | -0.033844 | 0.16202 | 0.12709 | -0.0010168 | 0.056251 | 0.10372 | -0.0029309 | 0.041199 | 0.09613 | -0.027466 | 0.004578 | 0.11444 | 0.027466 | 0.073242 | 0.59967 | 59.8572 | -62.8693 | 59.8755 | 60.022 | 59.848 | 0.37079 | 62.8418 | -59.8114 | -59.903 | 62.9837 | 62.9425 | 62.8967 | 0.10071 | 0.054932 | 0 | -0.050354 | -0.032044 | 122.8912 | 63.2401 | 122.7173 | 63.2401 | 122.7173 | 0.14191 | 0.032044 | 122.8912 | 122.7448 | 0.1236 | 122.7264 | 62.9654 | 122.7264 | -59.935 | -122.7768 | 62.8738 | 122.7448 | 62.9105 | 63.4689
2081.8281 | 122.8821 | -62.8784 | 59.8938 | -0.060425 | -0.0014377 | -0.0096323 | 2.8922 | 0.0021789 | -0.0033412 | -0.0026853 | -0.15286 | 0.16331 | 0.12837 | -0.0027258 | 0.057319 | 0.10286 | -0.00058107 | -0.13275 | 0.032043 | -0.16022 | -0.16937 | -0.091553 | -0.18768 | -0.11902 | 0.37994 | 59.848 | -62.9196 | 59.7565 | 59.7794 | 60.0266 | 0.39825 | 62.7182 | -59.8618 | -60.0632 | 62.7869 | 62.7594 | 62.6907 | 0.041198 | -0.027466 | -0.041199 | -0.045777 | -0.13733 | 122.6578 | 63.2767 | 122.905 | 63.3179 | 122.9462 | 0.068664 | -0.009156 | 122.699 | 122.6761 | 0.19226 | 122.7676 | 62.9105 | 122.7264 | -60.054 | -122.8134 | 62.709 | 122.6349 | 62.7457 | 63.2584
2082.8281 | 122.9645 | -62.883 | 59.8938 | -0.060425 | -0.0018649 | -0.0089913 | 2.8939 | 0.00046989 | 7.6842e-05 | -0.0022581 | -0.1254 | 0.16373 | 0.12837 | -0.0087072 | 0.055824 | 0.10436 | -0.0016493 | -0.018311 | 0.059509 | -0.086975 | -0.068665 | 0.018311 | -0.07782 | -0.036621 | 0.52643 | 59.848 | -62.9013 | 59.8801 | 59.9487 | 59.7656 | 0.28839 | 62.796 | -59.8343 | -59.9625 | 62.9013 | 62.8464 | 62.8052 | 0.050354 | 0.009155 | -0.01831 | -0.045777 | -0.013733 | 122.8317 | 63.1714 | 122.6486 | 63.1897 | 122.6669 | 0.10529 | 0.01831 | 122.85 | 122.7814 | 0.14648 | 122.7493 | 62.9425 | 122.731 | -59.9808 | -122.7951 | 62.8143 | 122.7631 | 62.8647 | 63.4094
2083.8906 | 122.9965 | -62.8601 | 59.8984 | 0.015869 | -0.0020785 | -0.0094187 | 2.8922 | -0.00017091 | 0.00029044 | -0.0033261 | -0.082672 | 0.16416 | 0.12794 | -0.0074254 | 0.055397 | 0.105 | -0.0016493 | -0.009155 | 0.10986 | -0.054932 | -0.050354 | 0.050354 | -0.022888 | 0.027466 | 0.56763 | 59.8709 | -62.883 | 60.1593 | 59.9808 | 59.8297 | 0.37994 | 62.8052 | -59.7885 | -59.9487 | 62.9105 | 62.8876 | 62.8372 | 0.082398 | 0.032044 | -0.022889 | -0.027465 | 0.26093 | 122.8409 | 63.2401 | 122.6898 | 63.2629 | 122.7127 | 0.10529 | 0.004578 | 122.8638 | 123.0423 | 0.16479 | 122.7539 | 62.97 | 122.731 | -59.9533 | -122.7814 | 62.8098 | 123.0194 | 62.851 | 63.4277
2084.8281 | 122.9874 | -62.8647 | 59.9213 | -0.014649 | -0.0025059 | -0.0083505 | 2.8928 | 0.00046989 | -0.00035036 | -0.0024717 | -0.11319 | 0.16224 | 0.12965 | -0.00016245 | 0.055397 | 0.10585 | -0.0025037 | -0.032043 | 0.050354 | -0.11444 | -0.045776 | -0.050354 | -0.1236 | -0.013733 | 0.49439 | 59.8663 | -62.915 | 59.9945 | 59.8938 | 59.761 | 0.23346 | 62.7502 | -59.8709 | -59.967 | 62.8143 | 62.851 | 62.7411 | 0.10071 | -0.009155 | -0.050354 | -0.054932 | 0.073242 | 122.7585 | 63.0981 | 122.6257 | 63.1485 | 122.6761 | 0.064087 | 0.068665 | 122.8088 | 122.9095 | 0.16479 | 122.7814 | 62.915 | 122.731 | -60.0357 | -122.8363 | 62.8189 | 122.8592 | 62.8326 | 63.3591
2085.8906 | 122.9782 | -62.8418 | 59.9213 | -0.037537 | -0.00058326 | -0.0089913 | 2.8924 | 0.0013245 | 0.00050424 | -0.0026853 | -0.091827 | 0.16331 | 0.1273 | -0.0018712 | 0.055183 | 0.10393 | -0.0020765 | 0.027466 | 0.12817 | -0.036621 | -0.027466 | 0.068665 | -0.041199 | 0.018311 | 0.56763 | 59.8709 | -62.883 | 59.9258 | 60.0174 | 59.8297 | 0.37994 | 62.8052 | -59.7931 | -59.9487 | 62.9105 | 62.8601 | 62.8006 | 0.054932 | -0.004578 | -0.041199 | -0.050354 | 0.004577 | 122.8592 | 63.2217 | 122.6715 | 63.2629 | 122.7127 | 0.10529 | 0.009155 | 122.9004 | 122.8088 | 0.1648 | 122.7539 | 62.97 | 122.7127 | -59.9579 | -122.8043 | 62.8143 | 122.7676 | 62.8693 | 63.4094
2086.8281 | 122.9645 | -62.8601 | 59.8984 | -0.060425 | -0.0014377 | -0.0081369 | 2.8926 | 0.0015381 | -0.00056396 | -0.0039671 | -0.11929 | 0.16437 | 0.12837 | -0.003794 | 0.055824 | 0.10671 | 0.0026233 | -0.11444 | 0.027466 | -0.14648 | -0.17853 | -0.10986 | -0.20142 | -0.1236 | 0.41199 | 59.848 | -62.9379 | 59.8206 | 60.0174 | 59.7198 | 0.21973 | 62.7136 | -59.8709 | -60.0769 | 62.7502 | 62.7365 | 62.6587 | 0.022888 | -0.054932 | -0.07782 | -0.050354 | -0.077819 | 122.8775 | 63.0798 | 122.58 | 63.1577 | 122.6578 | 0.036621 | -0.032044 | 122.9553 | 122.7585 | 0.17395 | 122.7859 | 62.8876 | 122.7081 | -60.0449 | -122.8363 | 62.6816 | 122.6807 | 62.7457 | 63.2721
2087.8906 | 122.9691 | -62.8418 | 59.903 | -0.045166 | -0.0020785 | -0.0077097 | 2.8903 | -0.0020935 | -0.003982 | 9.193e-05 | -0.10709 | 0.16288 | 0.12922 | -0.0069982 | 0.056892 | 0.10543 | 0.0032641 | 0.018311 | 0.11902 | -0.045776 | -0.041199 | 0.059509 | -0.018311 | 0.045776 | 0.58136 | 59.8709 | -62.8876 | 59.9121 | 59.9991 | 59.8114 | 0.36163 | 62.796 | -59.7839 | -59.9442 | 62.9013 | 62.8876 | 62.8235 | 0.091552 | 0.027465 | -0.045776 | -0.032043 | 0.009155 | 122.8409 | 63.2034 | 122.6532 | 63.2492 | 122.699 | 0.10528 | 0.004577 | 122.8867 | 122.7997 | 0.16479 | 122.7585 | 62.9608 | 122.7127 | -59.9487 | -122.7905 | 62.8006 | 122.7539 | 62.8601 | 63.4232
2088.8281 | 122.9324 | -62.8922 | 59.8663 | -0.068054 | -0.0016513 | -0.0089913 | 2.893 | 0.00068369 | -0.0041956 | -0.0022581 | -0.10709 | 0.16437 | 0.13328 | -0.0025122 | 0.056465 | 0.10692 | 0.0015551 | -0.11444 | 0.013733 | -0.15564 | -0.16937 | -0.09613 | -0.20142 | -0.11902 | 0.17853 | 59.8068 | -62.9608 | 59.8938 | 59.8984 | 59.7473 | 0.25635 | 62.7365 | -59.8526 | -60.0357 | 62.796 | 62.7731 | 62.6907 | 0.036621 | -0.045776 | -0.068664 | -0.059509 | 0.027466 | 122.7905 | 63.1485 | 122.6395 | 63.2172 | 122.7081 | 0.05951 | -0.013733 | 122.8592 | 122.8546 | 0.16937 | 122.7676 | 62.9059 | 122.699 | -60.022 | -122.8271 | 62.7228 | 122.7859 | 62.7777 | 63.0707
2089.8906 | 123.1293 | -62.8281 | 59.8892 | -0.1062 | 0.00048494 | -0.0094187 | 2.8928 | -0.00059811 | -0.00056396 | -0.0018307 | -0.0063781 | 0.16309 | 0.12709 | -0.003794 | 0.057106 | 0.10329 | -0.00079467 | 0.07782 | 0.068665 | -0.045776 | 0.064087 | 0.17853 | 0.054932 | 0.36621 | 0.70038 | 59.8434 | -62.8464 | 60.0174 | 60.0769 | 59.9487 | 0.43945 | 62.7823 | -59.8206 | -59.8251 | 63.0066 | 63.1943 | 62.883 | 0.41199 | 0.10071 | -0.018311 | -0.045776 | 0.12817 | 122.905 | 63.2675 | 122.7768 | 63.2858 | 122.7951 | 0.2243 | 0.10986 | 122.9233 | 122.8638 | 0.11444 | 122.6898 | 62.8967 | 122.6715 | -59.935 | -122.7356 | 62.8922 | 122.8455 | 62.9059 | 63.5284
2090.8281 | 123.0011 | -62.883 | 59.8846 | -0.052796 | -0.0012241 | -0.0083505 | 2.8924 | -0.00059811 | -0.0020594 | -0.0033261 | -0.11014 | 0.16331 | 0.12773 | -0.0029394 | 0.054542 | 0.10329 | -0.00079467 | -0.059509 | 0.036621 | -0.15106 | -0.1236 | -0.07782 | -0.16937 | -0.082397 | 0.41657 | 59.8389 | -62.8967 | 60.0403 | 59.9899 | 59.816 | 0.35248 | 62.7319 | -59.848 | -60.0082 | 62.8052 | 62.8006 | 62.7136 | 0.068665 | -0.018311 | -0.013733 | -0.045777 | 0.15564 | 122.8729 | 63.2355 | 122.699 | 63.2492 | 122.7127 | 0.073242 | 0.027466 | 122.8867 | 122.937 | 0.18768 | 122.7356 | 62.9196 | 122.7219 | -60.0357 | -122.7814 | 62.7594 | 122.9233 | 62.8235 | 63.2996
2091.8281 | 123.0789 | -62.851 | 59.8572 | -0.029907 | -0.0014377 | -0.0072825 | 2.8937 | 0.0028199 | -0.0027002 | 0.00051913 | -0.088776 | 0.16352 | 0.12837 | -0.0052892 | 0.054115 | 0.10457 | -0.0046399 | 0.018311 | -0.018311 | -0.16479 | -0.050354 | -0.068665 | -0.10071 | 0.041199 | 0.55847 | 59.8022 | -62.8738 | 59.9945 | 60.0082 | 59.8892 | 0.3479 | 62.6862 | -59.8755 | -59.9075 | 62.7823 | 62.8922 | 62.7502 | 0.20599 | 0.064087 | -0.022888 | -0.054932 | 0.13733 | 122.8592 | 63.1989 | 122.7402 | 63.2217 | 122.7631 | 0.09613 | 0.11444 | 122.8821 | 122.8683 | 0.14648 | 122.6761 | 62.8326 | 122.6532 | -60.022 | -122.731 | 62.8006 | 122.8455 | 62.8693 | 63.4094
2092.8906 | 123.0606 | -62.8555 | 59.9121 | 0.00824 | -0.0014377 | -0.0092051 | 2.8928 | 4.2692e-05 | -0.003982 | -0.00097627 | -0.064362 | 0.1616 | 0.13072 | -0.0059302 | 0.055824 | 0.10372 | -0.00058107 | 0.050354 | 0.10986 | -0.027466 | 0.009155 | 0.20142 | 0.14191 | 0.41199 | 0.97504 | 59.8572 | -62.8693 | 60.2554 | 59.9945 | 59.7794 | 0.80109 | 62.8281 | -59.8022 | -59.903 | 63.0569 | 63.2675 | 62.9974 | 0.43945 | 0.16937 | -0.013733 | -0.054931 | 0.34332 | 122.85 | 63.6566 | 122.6349 | 63.6703 | 122.6486 | 0.22888 | 0.036621 | 122.8638 | 123.1247 | 0.13733 | 122.7264 | 62.9654 | 122.7127 | -59.9396 | -122.7814 | 62.8647 | 123.111 | 62.9059 | 63.8306
2093.8281 | 123.1201 | -62.8647 | 59.8663 | -0.075684 | -0.0010105 | -0.0070687 | 2.8933 | 0.0011109 | -0.00035036 | -0.00097627 | -0.082672 | 0.16267 | 0.12709 | -0.0042212 | 0.055397 | 0.10628 | -0.0014355 | 0.027466 | -0.013733 | -0.15106 | -0.07782 | 0.018311 | -0.054932 | 0.059509 | 0.52185 | 59.8022 | -62.8876 | 60.2692 | 60.0357 | 60.0998 | 0.30212 | 62.7136 | -59.8801 | -59.9442 | 62.883 | 62.9242 | 62.8098 | 0.21057 | 0.09613 | -0.022888 | -0.064087 | 0.40283 | 122.9004 | 63.1668 | 122.9645 | 63.1897 | 122.9874 | 0.16937 | 0.073242 | 122.9233 | 123.1567 | 0.13733 | 122.6898 | 62.851 | 122.6669 | -60.0174 | -122.7539 | 62.7869 | 123.1338 | 62.8922 | 63.3865
2094.8906 | 123.0652 | -62.8326 | 59.903 | -0.060425 | -0.0010105 | -0.0070687 | 2.892 | 0.0011109 | 0.0013586 | -0.0018307 | -0.12845 | 0.16502 | 0.1258 | -0.00058965 | 0.055824 | 0.1035 | -0.0025037 | 0.16022 | 0.068665 | -0.068665 | -0.2655 | 0.032043 | 0.09613 | 0.20142 | 0.54474 | 59.8618 | -62.8738 | 60.3973 | 59.9945 | 59.967 | 0.39825 | 62.764 | -59.8343 | -60.1685 | 62.8647 | 63.0341 | 62.9288 | 0.27008 | 0.16479 | -0.041198 | -0.041199 | 0.49439 | 122.8271 | 63.2309 | 122.7997 | 63.2721 | 122.8409 | 0.10071 | -0.19684 | 122.8683 | 123.2712 | 0.13733 | 122.7356 | 62.9013 | 122.6944 | -59.9716 | -122.7768 | 62.5671 | 123.23 | 62.9929 | 63.3774
2095.8281 | 123.143 | -62.8326 | 59.8755 | -0.052796 | -0.0029331 | -0.0079233 | 2.8922 | -0.0023071 | -0.0018458 | 9.193e-05 | -0.06131 | 0.16309 | 0.12794 | -0.0033666 | 0.056892 | 0.10372 | 0.0021961 | -0.036621 | -0.036621 | -0.11444 | 0.018311 | 0.07782 | 0.032043 | 0.022888 | 0.55389 | 59.8114 | -62.8647 | 60.054 | 60.0266 | 59.9304 | 0.36163 | 62.7182 | -59.9121 | -59.8572 | 62.9105 | 62.8555 | 62.8647 | 0.13733 | 0.14648 | -0.032043 | -0.064087 | 0.17853 | 122.8592 | 63.1943 | 122.7631 | 63.2263 | 122.7951 | 0.19226 | 0.13275 | 122.8912 | 122.9187 | 0.07782 | 122.6761 | 62.796 | 122.644 | -59.9899 | -122.7402 | 62.851 | 122.8867 | 62.796 | 63.3865
2096.8906 | 122.9965 | -62.8601 | 59.9258 | -0.029907 | -0.00015586 | -0.011341 | 2.8922 | -0.00038451 | -0.0016322 | -0.0031125 | -0.06131 | 0.16224 | 0.12709 | -0.0044348 | 0.055824 | 0.10479 | -0.0020765 | 0 | 0.12817 | -0.022888 | -0.004578 | 0.032043 | -0.032043 | 0.041199 | 0.81024 | 59.9121 | -62.851 | 60.2692 | 59.967 | 59.761 | 0.36163 | 62.8372 | -59.7977 | -59.9304 | 62.8922 | 62.9013 | 62.8281 | 0.064087 | -0.009155 | 0.009155 | -0.013733 | 0.34332 | 122.8271 | 63.2217 | 122.6212 | 63.2126 | 122.612 | 0.054931 | 0.01831 | 122.818 | 123.1201 | 0.15106 | 122.7631 | 62.9883 | 122.7722 | -59.9487 | -122.7768 | 62.8555 | 123.1293 | 62.8601 | 63.6703
2097.8281 | 123.0011 | -62.8418 | 59.8526 | -0.068054 | -0.0029331 | -0.0089913 | 2.8911 | 0.00025629 | 0.0013586 | -0.0026853 | -0.052155 | 0.16096 | 0.12687 | -0.0093482 | 0.056465 | 0.10415 | 0.0015551 | -0.013733 | -0.013733 | -0.12817 | -0.004578 | 0.082397 | -0.086975 | 0.018311 | 0.63171 | 59.8068 | -62.8738 | 60.1273 | 60.0082 | 59.9625 | 0.40741 | 62.7136 | -59.8663 | -59.8572 | 62.9242 | 62.8601 | 62.7548 | 0.14649 | 0.041199 | -0.032043 | -0.045776 | 0.27466 | 122.85 | 63.2492 | 122.8043 | 63.2812 | 122.8363 | 0.21057 | 0.1236 | 122.8821 | 123.0011 | 0.11444 | 122.6807 | 62.8281 | 122.6486 | -59.9808 | -122.7264 | 62.8372 | 122.9691 | 62.8281 | 63.4735
2098.8281 | 123.1338 | -62.8738 | 59.8846 | -0.083313 | -0.0029331 | -0.0081369 | 2.8937 | 0.0021789 | -0.0012048 | -0.00012167 | -0.12845 | 0.16459 | 0.1273 | -0.002085 | 0.054329 | 0.10521 | 0.00048713 | -0.009155 | 0.009155 | -0.15564 | -0.068665 | -0.036621 | 0.032043 | 0.032043 | 0.48523 | 59.8343 | -62.9196 | 60.0861 | 60.0311 | 59.9075 | 0.36621 | 62.7182 | -59.8755 | -59.9533 | 62.8372 | 62.9059 | 62.9059 | 0.18768 | 0.18768 | -0.045777 | -0.050354 | 0.20142 | 122.905 | 63.2401 | 122.7814 | 63.2858 | 122.8271 | 0.11902 | 0.086975 | 122.9507 | 123.0057 | 0.16479 | 122.7539 | 62.883 | 122.7081 | -60.0403 | -122.8043 | 62.8052 | 122.9599 | 62.8647 | 63.3591
2099.8906 | 123.0881 | -62.8281 | 59.9121 | -0.014649 | -0.0022923 | -0.0094187 | 2.8907 | 0.0045289 | -0.0016322 | -0.0039671 | -0.055206 | 0.16181 | 0.12709 | 0.00047855 | 0.05561 | 0.10329 | -0.0035719 | 0.059509 | 0.059509 | -0.064087 | 0.073242 | 0.14648 | 0.050354 | 0.2243 | 0.65918 | 59.8434 | -62.8601 | 60.022 | 60.054 | 59.9075 | 0.48981 | 62.764 | -59.8526 | -59.8389 | 62.9745 | 63.0524 | 62.8784 | 0.28839 | 0.11444 | -0.032043 | -0.068664 | 0.10986 | 122.8821 | 63.3179 | 122.7356 | 63.3499 | 122.7676 | 0.21057 | 0.13733 | 122.9141 | 122.8821 | 0.1236 | 122.7036 | 62.8876 | 122.6715 | -59.9762 | -122.7722 | 62.9013 | 122.85 | 62.8876 | 63.4872
2100.8281 | 123.0011 | -62.8601 | 59.8663 | -0.052796 | -0.0029331 | -0.0074961 | 2.8918 | 0.0055969 | -0.00013676 | -0.00097627 | -0.1254 | 0.16544 | 0.12687 | -0.0052892 | 0.056465 | 0.10415 | -0.0072035 | -0.11444 | 0.013733 | -0.15564 | -0.13275 | -0.041199 | -0.16937 | -0.09613 | 0.42114 | 59.8389 | -62.8967 | 59.9121 | 59.9579 | 59.7977 | 0.26093 | 62.7045 | -59.8526 | -59.9991 | 62.8189 | 62.764 | 62.6907 | 0.05951 | -0.013733 | -0.036622 | -0.027466 | 0.045776 | 122.818 | 63.121 | 122.6578 | 63.1577 | 122.6944 | 0.11444 | 0.022889 | 122.8546 | 122.8088 | 0.16937 | 122.7356 | 62.8738 | 122.699 | -60.022 | -122.7631 | 62.7274 | 122.7722 | 62.7457 | 63.2812
2101.8906 | 122.9691 | -62.8693 | 59.8984 | -0.022278 | 0.00091214 | -0.0072825 | 2.893 | -0.00038451 | -0.0012048 | -0.0033261 | -0.13455 | 0.16331 | 0.1305 | -0.003153 | 0.05326 | 0.10628 | -0.0027173 | -0.013733 | 0.07782 | -0.082397 | -0.027466 | 0.073242 | -0.041199 | 0.009155 | 0.53558 | 59.8801 | -62.883 | 59.9213 | 59.967 | 59.7885 | 0.32959 | 62.7869 | -59.8206 | -59.9258 | 62.9425 | 62.8784 | 62.8281 | 0.091552 | 0.041198 | -0.013733 | -0.01831 | 0.022889 | 122.8363 | 63.1989 | 122.6578 | 63.2126 | 122.6715 | 0.15564 | 0.054931 | 122.85 | 122.8043 | 0.16022 | 122.7631 | 62.9471 | 122.7493 | -59.9808 | -122.7814 | 62.8418 | 122.7905 | 62.8555 | 63.4048
2102.8281 | 123.0148 | -62.883 | 59.8572 | -0.068054 | -0.00036966 | -0.0074961 | 2.8939 | 0.0030335 | 0.0015722 | -0.0039671 | -0.1254 | 0.16202 | 0.12687 | -0.0040076 | 0.055824 | 0.10393 | -0.0010083 | -0.11444 | 0.022888 | -0.16022 | -0.12817 | -0.050354 | -0.16479 | -0.10986 | 0.41657 | 59.8251 | -62.9196 | 59.9213 | 59.9762 | 59.7931 | 0.25177 | 62.7228 | -59.8343 | -59.9854 | 62.8326 | 62.7731 | 62.7182 | 0.050354 | -0.004578 | -0.036621 | -0.032044 | 0.064087 | 122.8592 | 63.1348 | 122.6761 | 63.1714 | 122.7127 | 0.10986 | 0.032043 | 122.8958 | 122.8409 | 0.1831 | 122.7448 | 62.9059 | 122.7081 | -60.0174 | -122.7768 | 62.7548 | 122.8043 | 62.7686 | 63.2996
2103.8906 | 122.9782 | -62.8876 | 59.8709 | 0.061645 | -0.0010105 | -0.0087777 | 2.8935 | -0.0033753 | -0.0020594 | -0.00033547 | -0.1254 | 0.16544 | 0.12944 | -0.002085 | 0.055183 | 0.10479 | 0.0030505 | -0.15564 | -0.022888 | -0.15564 | -0.18768 | -0.09613 | -0.17853 | -0.10529 | 0.39368 | 59.8297 | -62.9059 | 59.8801 | 59.9304 | 59.7382 | 0.23346 | 62.7319 | -59.8938 | -60.0586 | 62.7914 | 62.7823 | 62.709 | 0.050354 | -0.022888 | -0.018311 | -0.041199 | 0.009155 | 122.818 | 63.121 | 122.6257 | 63.1393 | 122.644 | 0.05951 | -0.032043 | 122.8363 | 122.7859 | 0.13275 | 122.7356 | 62.8647 | 122.7173 | -60.0266 | -122.7768 | 62.6999 | 122.7676 | 62.7319 | 63.2812
2104.8281 | 123.0103 | -62.8876 | 59.8618 | -0.014649 | -0.0012241 | -0.0087777 | 2.8911 | 0.0023925 | 7.6842e-05 | 9.193e-05 | -0.11929 | 0.16416 | 0.12794 | -0.0035802 | 0.055397 | 0.10244 | -0.0012219 | -0.10986 | 0.018311 | -0.16022 | -0.15106 | -0.054932 | -0.16022 | -0.09613 | 0.43945 | 59.8068 | -62.8967 | 59.9121 | 59.9899 | 59.7931 | 0.28381 | 62.7274 | -59.8434 | -60.0128 | 62.8326 | 62.7914 | 62.7274 | 0.064087 | 0 | -0.009156 | -0.054931 | 0.050354 | 122.8775 | 63.1714 | 122.6807 | 63.1805 | 122.6898 | 0.10528 | 0.009155 | 122.8867 | 122.8088 | 0.17853 | 122.7036 | 62.9059 | 122.6944 | -60.022 | -122.7585 | 62.7365 | 122.7997 | 62.7777 | 63.327
2105.8906 | 122.9324 | -62.8555 | 59.935 | -0.014649 | -0.00058326 | -0.0089913 | 2.8947 | -0.0025207 | -0.0012048 | 0.0013735 | -0.17117 | 0.16331 | 0.12944 | -0.0046484 | 0.055397 | 0.10415 | 0.0032641 | 0.013733 | 0.16937 | -0.041199 | -0.050354 | -0.041199 | 0.39825 | 0.41657 | 0.58136 | 59.8709 | -62.9059 | 59.8709 | 59.967 | 59.7931 | 0.36163 | 62.8143 | -59.7656 | -59.9854 | 62.8143 | 63.2721 | 63.2538 | 0.45776 | 0.43945 | -0.050354 | -0.064087 | -0.064087 | 122.8226 | 63.2172 | 122.6486 | 63.2675 | 122.699 | 0 | -0.009155 | 122.8729 | 122.7768 | 0.21057 | 122.7768 | 63.0249 | 122.7264 | -59.9762 | -122.8409 | 62.8052 | 122.7264 | 62.8693 | 63.4369
2106.8281 | 123.0652 | -62.851 | 59.8526 | -0.014649 | -0.0014377 | -0.0083505 | 2.8926 | -0.00059811 | 0.00050424 | -0.0026853 | -0.076569 | 0.16224 | 0.1258 | -0.00037605 | 0.053474 | 0.1035 | -0.0016493 | -0.041199 | -0.032043 | -0.15106 | -0.07782 | 0.032043 | -0.10986 | -0.036621 | 0.49439 | 59.8022 | -62.8967 | 59.9625 | 60.0311 | 59.848 | 0.31128 | 62.6999 | -59.8846 | -59.9304 | 62.883 | 62.8143 | 62.7411 | 0.11444 | 0.041199 | -0.045777 | -0.050354 | 0.10986 | 122.8821 | 63.1622 | 122.699 | 63.208 | 122.7448 | 0.18311 | 0.073242 | 122.9279 | 122.8592 | 0.11902 | 122.699 | 62.8189 | 122.6532 | -60.0037 | -122.7493 | 62.7731 | 122.8134 | 62.8098 | 63.3453
2107.8906 | 122.9874 | -62.9059 | 59.8846 | -0.045166 | -0.0014377 | -0.011768 | 2.8922 | -0.0023071 | -0.0012048 | -0.0031125 | -0.11929 | 0.16395 | 0.1273 | -0.0035802 | 0.056892 | 0.10564 | -0.0037855 | 0.045776 | 0.027466 | -0.15106 | -0.16022 | -0.068665 | -0.19684 | -0.1236 | 0.41657 | 59.8663 | -62.915 | 59.8801 | 59.9213 | 59.7565 | 0.23346 | 62.7548 | -59.8572 | -60.0449 | 62.8372 | 62.7823 | 62.709 | 0.027466 | -0.045776 | -0.009155 | -0.018311 | -0.004578 | 122.8271 | 63.1393 | 122.6624 | 63.1485 | 122.6715 | 0.082397 | -0.009155 | 122.8363 | 122.7951 | 0.17853 | 122.7814 | 62.9333 | 122.7722 | -60.0357 | -122.7997 | 62.7457 | 122.7859 | 62.9517 | 63.3224
2108.8281 | 123.0469 | -62.8372 | 59.8434 | -0.12909 | -0.0044285 | -0.0085641 | 2.8922 | 0.0015381 | -0.0033412 | -0.0016171 | -0.082672 | 0.16416 | 0.12623 | -0.0076392 | 0.056892 | 0.10436 | 0.0011279 | 0.10986 | -0.064087 | -0.12817 | -0.013733 | 0.045776 | -0.086975 | -0.018311 | 0.52643 | 59.7977 | -62.8601 | 59.9579 | 60.022 | 59.8297 | 0.29755 | 62.709 | -59.9075 | -59.8572 | 62.883 | 62.8189 | 62.7502 | 0.10986 | 0.041199 | -0.022888 | -0.045777 | 0.11444 | 122.8592 | 63.1348 | 122.6669 | 63.1577 | 122.6898 | 0.17395 | 0.11444 | 122.8821 | 122.818 | 0.064087 | 122.6578 | 62.7731 | 122.6349 | -59.9716 | -122.7036 | 62.8235 | 122.7951 | 62.9471 | 63.3636
2109.8906 | 122.818 | -62.9105 | 59.848 | -0.029907 | -0.0018649 | -0.0062143 | 2.8947 | 0.00046989 | -0.0016322 | -0.0043943 | -0.14981 | 0.16544 | 0.12773 | -0.003153 | 0.056251 | 0.10372 | -0.0020765 | -0.11902 | 0.027466 | -0.15106 | -0.19226 | -0.11902 | -0.16937 | -0.11444 | 0.37537 | 59.8526 | -62.9059 | 59.8618 | 59.9075 | 59.7153 | 0.27924 | 62.7594 | -59.8206 | -60.0403 | 62.7914 | 62.796 | 62.7411 | 0.036621 | -0.018311 | 0.004577 | 0.004578 | 0.013733 | 122.818 | 63.1897 | 122.6257 | 63.1851 | 122.6212 | 0.032043 | -0.041199 | 122.8134 | 122.7676 | 0.17853 | 122.7585 | 62.9379 | 122.7631 | -59.9991 | -122.7539 | 62.7182 | 122.7722 | 62.7914 | 63.2858
2110.8281 | 123.0469 | -62.8647 | 59.848 | -0.090943 | 5.7742e-05 | -0.0077097 | 2.8943 | 0.0019653 | 7.6842e-05 | -0.00076267 | -0.11014 | 0.16416 | 0.1273 | -0.0012304 | 0.054756 | 0.10479 | -0.00079467 | -0.054932 | -0.032043 | -0.13733 | -0.059509 | 0.027466 | -0.091553 | -0.041199 | 0.50354 | 59.8022 | -62.8922 | 59.967 | 60.0494 | 59.8434 | 0.3067 | 62.7274 | -59.8801 | -59.9075 | 62.8922 | 62.8235 | 62.7731 | 0.09613 | 0.045776 | -0.027466 | -0.045776 | 0.11902 | 122.9141 | 63.1714 | 122.7081 | 63.1989 | 122.7356 | 0.16479 | 0.07782 | 122.9416 | 122.8592 | 0.10529 | 122.6944 | 62.8326 | 122.6669 | -59.9854 | -122.7402 | 62.8052 | 122.8317 | 62.8098 | 63.3682
2111.8906 | 122.9645 | -62.8647 | 59.8984 | -0.022278 | -0.00036966 | -0.0098459 | 2.8926 | -0.0020935 | -0.0014184 | -0.0020443 | -0.15286 | 0.16288 | 0.12837 | -0.0050756 | 0.056251 | 0.10564 | 0.00027333 | 0.009155 | 0.082397 | -0.054932 | -0.027466 | 0.068665 | -0.036621 | 0.013733 | 0.57678 | 59.8709 | -62.8601 | 59.9304 | 59.9762 | 59.7977 | 0.34332 | 62.8098 | -59.816 | -59.9258 | 62.9334 | 62.8784 | 62.8281 | 0.068665 | 0.018311 | 0.004578 | -0.027465 | 0.032044 | 122.8409 | 63.208 | 122.6624 | 63.2034 | 122.6578 | 0.1236 | 0.027466 | 122.8363 | 122.7905 | 0.13733 | 122.731 | 62.9471 | 122.7356 | -59.9533 | -122.7585 | 62.8372 | 122.7951 | 62.8738 | 63.4415
2112.8281 | 123.024 | -62.8601 | 59.8709 | -0.075684 | -0.0037875 | -0.0107 | 2.8918 | -0.0033753 | -0.002273 | -0.0022581 | -0.064362 | 0.16331 | 0.12815 | -0.0063574 | 0.057533 | 0.10244 | 0.0011279 | -0.068665 | -0.013733 | -0.10986 | -0.059509 | 0.045776 | -0.091553 | -0.022888 | 0.48065 | 59.8251 | -62.883 | 59.9167 | 59.9991 | 59.816 | 0.28839 | 62.7502 | -59.8846 | -59.9304 | 62.9059 | 62.8372 | 62.7686 | 0.086975 | 0.01831 | -0.022889 | -0.045777 | 0.045776 | 122.8592 | 63.1485 | 122.6761 | 63.1714 | 122.699 | 0.15564 | 0.050354 | 122.8821 | 122.7997 | 0.09613 | 122.7081 | 62.8464 | 122.6852 | -59.9808 | -122.7539 | 62.8006 | 122.7768 | 62.7914 | 63.3408
2113.8906 | 122.9279 | -62.8922 | 59.9213 | -0.014649 | -0.00079686 | -0.0083505 | 2.8939 | 0.0011109 | -0.0018458 | -0.00076267 | -0.16507 | 0.16331 | 0.12815 | 0.0032556 | 0.056678 | 0.10585 | -0.0027173 | -0.059509 | 0.045776 | -0.12817 | -0.1236 | -0.045776 | -0.14191 | -0.09613 | 0.42572 | 59.8663 | -62.9105 | 59.8572 | 59.9075 | 59.7061 | 0.24261 | 62.764 | -59.8755 | -60.0449 | 62.8464 | 62.796 | 62.7502 | 0.032044 | -0.013733 | -0.01831 | -0.054932 | -0.064087 | 122.7997 | 63.1348 | 122.5983 | 63.1531 | 122.6166 | 0.082398 | 0.004578 | 122.818 | 122.7676 | 0.17395 | 122.7768 | 62.9379 | 122.7585 | -60.0494 | -122.8317 | 62.7686 | 122.7493 | 62.8326 | 63.3179
2114.8281 | 123.0194 | -62.8418 | 59.8526 | -0.090943 | -0.0016513 | -0.0092051 | 2.8922 | 0.0023925 | -0.00056396 | -0.0031125 | -0.070465 | 0.16352 | 0.12645 | -0.010203 | 0.057106 | 0.10286 | -0.00015387 | -0.032043 | -0.018311 | -0.086975 | -0.068665 | 0.054932 | -0.050354 | 0.18768 | 0.75989 | 59.7977 | -62.8967 | 60.5118 | 60.0677 | 59.8755 | 0.37537 | 62.7548 | -59.8709 | -59.9213 | 62.8967 | 63.0295 | 62.7914 | 0.27466 | 0.036621 | -0.054932 | -0.054932 | 0.65918 | 122.9095 | 63.2172 | 122.7173 | 63.2721 | 122.7722 | 0.14191 | 0.01831 | 122.9645 | 123.4085 | 0.068664 | 122.6944 | 62.8235 | 122.6395 | -59.9396 | -122.7493 | 62.7731 | 123.3536 | 62.8098 | 63.6017
2115.8906 | 123.1522 | -62.8922 | 59.9075 | -0.052796 | -0.0016513 | -0.0079233 | 2.8939 | 0.0011109 | -0.0031274 | -0.0020443 | -0.24136 | 0.16181 | 0.12623 | -0.0010168 | 0.055824 | 0.10692 | -0.0012219 | -0.09613 | 0.013733 | -0.14191 | -0.082397 | -0.10529 | -0.1831 | -0.16479 | 0.74616 | 59.8572 | -62.883 | 60.4111 | 59.9579 | 59.8114 | 0.21057 | 62.7502 | -59.8938 | -59.9899 | 62.7869 | 62.7274 | 62.709 | -0.022888 | -0.041198 | 0.009155 | -0.050354 | 0.50354 | 122.85 | 63.1027 | 122.7036 | 63.0936 | 122.6944 | 0.036621 | 0.05951 | 122.8409 | 123.2941 | 0.15564 | 122.7402 | 62.9059 | 122.7493 | -60.0494 | -122.7905 | 62.8098 | 123.3032 | 62.796 | 63.6383
2116.8281 | 123.0972 | -62.8555 | 59.8755 | 0.023498 | -0.0022923 | -0.0098459 | 2.8926 | -0.0048705 | -0.0048364 | -0.00076267 | -0.055206 | 0.16181 | 0.12516 | -0.011271 | 0.056678 | 0.105 | 0.0019823 | -0.041199 | 0.027466 | -0.068665 | 0.013733 | -0.036621 | -0.013733 | 0.068665 | 0.54474 | 59.8114 | -62.8784 | 60.0677 | 60.022 | 59.9213 | 0.5127 | 62.7869 | -59.848 | -59.8618 | 62.8189 | 62.9242 | 62.8418 | 0.13733 | 0.054932 | -0.022888 | -0.064087 | 0.19226 | 122.8775 | 63.3682 | 122.7768 | 63.3911 | 122.7997 | 0.032044 | 0.082398 | 122.9004 | 122.9462 | 0.096131 | 122.6898 | 62.883 | 122.6669 | -59.9442 | -122.7539 | 62.8693 | 122.9233 | 62.8143 | 63.4003
2117.8906 | 123.4268 | -62.8281 | 59.8755 | -0.11383 | -0.00036966 | -0.0089913 | 2.8937 | 0.0019653 | 0.0026404 | -0.0063169 | -0.094879 | 0.16309 | 0.1258 | -0.0078528 | 0.057106 | 0.10372 | -0.0014355 | 0.14648 | -0.032043 | -0.15564 | -0.018311 | 0.068665 | -0.073242 | 0.13733 | 0.64087 | 59.8022 | -62.9059 | 60.1501 | 60.022 | 59.8984 | 0.4715 | 62.6724 | -59.9075 | -59.8938 | 62.8967 | 62.9654 | 62.7548 | 0.29297 | 0.082398 | -0.07782 | -0.073242 | 0.27466 | 122.85 | 63.2996 | 122.7264 | 63.3774 | 122.8043 | 0.22431 | 0.13733 | 122.9279 | 123.056 | 0.1236 | 122.7081 | 62.796 | 122.6303 | -60.0311 | -122.7814 | 62.8098 | 122.9782 | 62.9745 | 63.4689
2118.8281 | 123.0331 | -62.8555 | 59.8755 | -0.022278 | -0.00015586 | -0.010273 | 2.8943 | 0.0013245 | 0.001145 | -0.0043943 | -0.085724 | 0.16309 | 0.12645 | -0.0052892 | 0.056038 | 0.10372 | -0.0033581 | -0.073242 | -0.022888 | -0.1236 | -0.054932 | 0.050354 | -0.086975 | -0.009155 | 0.50354 | 59.7931 | -62.8876 | 59.9304 | 59.9899 | 59.8343 | 0.29297 | 62.7319 | -59.8984 | -59.9304 | 62.9059 | 62.8464 | 62.7686 | 0.11444 | 0.036621 | -0.032043 | -0.082397 | 0.054932 | 122.8455 | 63.1485 | 122.6898 | 63.1805 | 122.7219 | 0.17395 | 0.068664 | 122.8775 | 122.818 | 0.10071 | 122.6807 | 62.8326 | 122.6486 | -59.9991 | -122.7631 | 62.8006 | 122.7859 | 62.7823 | 63.3591
2119.8906 | 123.0011 | -62.8784 | 59.8572 | -0.075684 | -0.0012241 | -0.0077097 | 2.8922 | -0.0042297 | -0.00099116 | 0.00030553 | -0.070465 | 0.16502 | 0.12709 | -0.0018712 | 0.057106 | 0.10286 | -0.0027173 | -0.073242 | -0.022888 | -0.1236 | -0.064087 | 0.036621 | -0.09613 | -0.032043 | 0.48981 | 59.8068 | -62.9059 | 59.9167 | 59.9991 | 59.816 | 0.2655 | 62.7548 | -59.8801 | -59.9213 | 62.915 | 62.8464 | 62.7823 | 0.091553 | 0.027466 | -0.027466 | -0.050354 | 0.059509 | 122.8775 | 63.1439 | 122.6944 | 63.1714 | 122.7219 | 0.16022 | 0.059509 | 122.905 | 122.8226 | 0.10071 | 122.7127 | 62.8555 | 122.6852 | -59.9808 | -122.7631 | 62.8143 | 122.7951 | 62.8052 | 63.3682
2120.8281 | 123.0194 | -62.8693 | 59.8618 | 0.00824 | 5.7742e-05 | -0.0092051 | 2.8939 | -0.0033753 | -0.00056396 | -0.00076267 | -0.067413 | 0.16566 | 0.1258 | -0.0080664 | 0.053901 | 0.10415 | -0.0029309 | -0.07782 | 0.013733 | -0.11444 | -0.054932 | 0.018311 | -0.059509 | -0.013733 | 0.48523 | 59.8343 | -62.9013 | 59.9258 | 59.9899 | 59.8251 | 0.31586 | 62.7548 | -59.848 | -59.9167 | 62.8876 | 62.8555 | 62.8098 | 0.10071 | 0.054932 | -0.032043 | -0.027465 | 0.064087 | 122.8592 | 63.1851 | 122.6944 | 63.2172 | 122.7264 | 0.13275 | 0.059509 | 122.8912 | 122.8271 | 0.12817 | 122.7356 | 62.883 | 122.7036 | -59.9762 | -122.7631 | 62.8143 | 122.7951 | 62.7914 | 63.3545
2121.8906 | 122.9599 | -62.8647 | 59.8846 | -0.007019 | -0.00058326 | -0.0079233 | 2.8943 | -0.0016663 | -0.0020594 | -0.0031125 | -0.18948 | 0.16459 | 0.1273 | -0.0027258 | 0.05561 | 0.10521 | -0.0016493 | -0.050354 | 0.064087 | -0.11444 | -0.091553 | -0.022888 | -0.13275 | -0.068665 | 0.4715 | 59.8663 | -62.883 | 59.8846 | 59.9304 | 59.7336 | 0.2655 | 62.7502 | -59.8206 | -59.9762 | 62.8418 | 62.796 | 62.7319 | 0.045776 | -0.01831 | -0.018311 | -0.018311 | 0 | 122.7951 | 63.1302 | 122.5983 | 63.1485 | 122.6166 | 0.091553 | 0.022888 | 122.8134 | 122.7676 | 0.17853 | 122.7493 | 62.9288 | 122.731 | -59.9991 | -122.7676 | 62.7731 | 122.7493 | 62.8143 | 63.3362
2122.8281 | 123.024 | -62.8464 | 59.8755 | -0.052796 | -0.0014377 | -0.0068551 | 2.8924 | 0.0036743 | -0.0018458 | -0.00097627 | -0.058258 | 0.16245 | 0.12901 | -0.010843 | 0.057747 | 0.10436 | -0.0014355 | -0.032043 | 0.050354 | -0.073242 | -0.022888 | 0.059509 | -0.045776 | 0.027466 | 0.53558 | 59.7977 | -62.8967 | 59.9533 | 60.0403 | 59.8938 | 0.36621 | 62.7731 | -59.8251 | -59.8984 | 62.9059 | 62.8738 | 62.8006 | 0.10071 | 0.027466 | -0.050354 | -0.07782 | 0.07782 | 122.8867 | 63.2126 | 122.7402 | 63.2629 | 122.7905 | 0.13275 | 0.050354 | 122.937 | 122.85 | 0.1236 | 122.6944 | 62.8967 | 122.644 | -59.9487 | -122.7722 | 62.8235 | 122.7997 | 62.8143 | 63.382
2123.8906 | 123.0331 | -62.8464 | 59.8618 | -0.075684 | -0.0010105 | -0.0070687 | 2.8939 | 0.0028199 | -0.00056396 | -0.00076267 | -0.14981 | 0.16267 | 0.12751 | -0.00080325 | 0.054969 | 0.10671 | -0.0025037 | -0.10071 | 0 | -0.14191 | -0.10529 | -0.032043 | -0.13733 | -0.073242 | 0.48065 | 59.7931 | -62.9059 | 59.9442 | 60.0174 | 59.848 | 0.32044 | 62.7045 | -59.8618 | -59.967 | 62.8143 | 62.7731 | 62.709 | 0.068665 | 0.004578 | -0.059509 | -0.068664 | 0.082398 | 122.8638 | 63.1668 | 122.6944 | 63.2263 | 122.7539 | 0.10986 | 0.036621 | 122.9233 | 122.85 | 0.14191 | 122.699 | 62.8464 | 122.6395 | -60.0037 | -122.7676 | 62.7411 | 122.7905 | 62.7457 | 63.327
2124.8281 | 123.0652 | -62.851 | 59.8846 | 0.00824 | -0.00015586 | -0.011128 | 2.8928 | -0.0025207 | 0.0013586 | -0.0026853 | -0.055206 | 0.16181 | 0.12794 | -0.0027258 | 0.055183 | 0.10265 | 0.0021961 | -0.059509 | 0.018311 | -0.10071 | -0.068665 | 0.022888 | -0.064087 | -0.009155 | 0.48065 | 59.8297 | -62.8876 | 59.935 | 60.0128 | 59.8434 | 0.19226 | 62.7502 | -59.8663 | -59.9533 | 62.8738 | 62.8418 | 62.7869 | 0.091553 | 0.036621 | -0.036621 | -0.054932 | 0.050354 | 122.8638 | 63.0432 | 122.6944 | 63.0798 | 122.731 | 0.1236 | 0.032043 | 122.9004 | 122.8226 | 0.11902 | 122.7173 | 62.8693 | 122.6807 | -59.9854 | -122.7722 | 62.7823 | 122.7859 | 62.7914 | 63.3316
2125.8906 | 122.9782 | -62.8738 | 59.8618 | -0.083313 | -0.0016513 | -0.010487 | 2.8939 | 0.0030335 | -0.0020594 | -0.0026853 | -0.17422 | 0.16395 | 0.12773 | -0.0057166 | 0.057106 | 0.10607 | -0.0014355 | -0.027466 | 0.032043 | -0.15106 | -0.14648 | -0.07782 | -0.18768 | -0.11444 | 0.42114 | 59.8343 | -62.915 | 59.8892 | 59.9304 | 59.7656 | 0.22888 | 62.7228 | -59.8297 | -60.0082 | 62.796 | 62.7594 | 62.6862 | 0.036621 | -0.036621 | -0.041199 | -0.027465 | 0.027466 | 122.8043 | 63.1027 | 122.6395 | 63.1439 | 122.6807 | 0.073242 | 0.004578 | 122.8455 | 122.8043 | 0.18311 | 122.7493 | 62.9059 | 122.7081 | -60.0128 | -122.7768 | 62.7274 | 122.7631 | 62.8464 | 63.295
2126.8281 | 123.0881 | -62.8372 | 59.8709 | -0.083313 | -0.00079686 | -0.0094187 | 2.8935 | -0.0048705 | -0.0014184 | -0.0014035 | -0.049103 | 0.16074 | 0.12986 | -0.00016245 | 0.05561 | 0.10286 | -0.0012219 | 0.018311 | 0.054932 | -0.045776 | 0.036621 | 0.14648 | 0.027466 | 0.082397 | 0.65002 | 59.8389 | -62.8555 | 60.0037 | 60.1044 | 59.935 | 0.43945 | 62.7914 | -59.816 | -59.8343 | 62.9837 | 62.9196 | 62.8647 | 0.12817 | 0.073242 | -0.018311 | -0.032044 | 0.13275 | 122.9416 | 63.2767 | 122.7722 | 63.295 | 122.7905 | 0.19226 | 0.082397 | 122.9599 | 122.8592 | 0.10071 | 122.6944 | 62.8922 | 122.6761 | -59.9167 | -122.7264 | 62.8738 | 122.8409 | 62.8555 | 63.4872
2127.8281 | 123.0515 | -62.8326 | 59.8755 | -0.037537 | -0.0018649 | -0.010059 | 2.893 | 0.0013245 | -0.0018458 | -0.00076267 | 0.024139 | 0.16245 | 0.12623 | -0.001444 | 0.057106 | 0.10415 | -0.0016493 | 0.050354 | 0.068665 | -0.027466 | 0.07782 | 0.17395 | 0.064087 | 0.10529 | 0.77362 | 59.8984 | -62.8372 | 59.9854 | 60.0677 | 59.9075 | 0.45319 | 62.8052 | -59.8068 | -59.7977 | 63.0066 | 62.9379 | 62.8967 | 0.13275 | 0.091553 | -0.004577 | 0.022888 | 0.10986 | 122.9004 | 63.2858 | 122.7402 | 63.2904 | 122.7448 | 0.20142 | 0.10529 | 122.905 | 122.8226 | 0.096131 | 122.7356 | 62.9013 | 122.731 | -59.903 | -122.7127 | 62.9105 | 122.818 | 62.883 | 63.6063
2128.8906 | 122.9828 | -62.8601 | 59.8892 | -0.022278 | -0.0020785 | -0.0072825 | 2.8941 | 0.00089729 | 0.00093144 | -0.0037533 | -0.17117 | 0.16395 | 0.12666 | 0.00069215 | 0.054756 | 0.10393 | -0.0025037 | -0.082397 | 0.050354 | -0.13275 | -0.14191 | -0.059509 | -0.1831 | -0.091553 | 0.4303 | 59.8343 | -62.8967 | 59.8984 | 59.9487 | 59.761 | 0.24719 | 62.7274 | -59.8389 | -60.0311 | 62.8006 | 62.7686 | 62.677 | 0.041198 | -0.050354 | -0.036622 | -0.054931 | 0.009155 | 122.8088 | 63.1073 | 122.6212 | 63.1439 | 122.6578 | 0.073242 | -0.009156 | 122.8455 | 122.7951 | 0.18311 | 122.731 | 62.9105 | 122.6944 | -60.022 | -122.7859 | 62.7182 | 122.7585 | 62.7777 | 63.2904
2129.8438 | 122.9736 | -62.8738 | 59.8709 | -0.052796 | -0.00036966 | -0.0085641 | 2.8945 | 0.0011109 | -0.0018458 | -0.0011899 | -0.1376 | 0.16245 | 0.12858 | 0.0011194 | 0.058174 | 0.10415 | -0.0031445 | -0.1236 | 0.054932 | -0.1236 | -0.15106 | -0.059509 | -0.17853 | -0.1236 | 0.41657 | 59.8618 | -62.9059 | 59.9121 | 59.9487 | 59.7748 | 0.26093 | 62.7502 | -59.816 | -60.022 | 62.8143 | 62.7502 | 62.6953 | 0 | -0.054932 | -0.032044 | -0.009156 | 0.041198 | 122.8226 | 63.1348 | 122.6486 | 63.1668 | 122.6807 | 0.064087 | -0.027466 | 122.8546 | 122.818 | 0.17853 | 122.7676 | 62.9288 | 122.7356 | -59.9945 | -122.7768 | 62.7228 | 122.7859 | 62.7502 | 63.2904
2130.8906 | 123.0423 | -62.8372 | 59.8755 | -0.022278 | -0.0016513 | -0.0079233 | 2.8905 | 0.0021789 | -0.00077756 | -0.0028989 | -0.076569 | 0.16117 | 0.12516 | -0.0069982 | 0.059242 | 0.10308 | -0.0033581 | -0.059509 | 0 | -0.10529 | -0.073242 | 0.027466 | -0.082397 | 0 | 0.46234 | 59.816 | -62.8876 | 59.9213 | 60.0037 | 59.8251 | 0.31128 | 62.7319 | -59.8755 | -59.9487 | 62.8647 | 62.8372 | 62.7548 | 0.10529 | 0.022889 | -0.050354 | -0.059509 | 0.045777 | 122.8409 | 63.1485 | 122.6624 | 63.1989 | 122.7127 | 0.13275 | 0.032044 | 122.8912 | 122.8088 | 0.10529 | 122.7036 | 62.8372 | 122.6532 | -59.9808 | -122.7631 | 62.764 | 122.7585 | 62.7777 | 63.2996
2131.8281 | 123.0515 | -62.8189 | 59.8938 | -0.014649 | -0.0014377 | -0.0079233 | 2.8898 | -0.00017091 | -0.0037684 | -0.0031125 | -0.11929 | 0.16245 | 0.1273 | -0.00828 | 0.056678 | 0.10308 | -0.00015387 | 0.059509 | 0.082397 | -0.032043 | 0.38452 | -0.16937 | -0.25177 | 0.12817 | 0.66376 | 59.8251 | -62.8693 | 59.9854 | 60.0952 | 59.903 | 0.44403 | 62.7869 | -59.8114 | -59.5093 | 62.6495 | 62.9471 | 62.5671 | 0.16022 | -0.21973 | -0.050354 | -0.068665 | 0.091553 | 122.9141 | 63.2629 | 122.7219 | 63.3133 | 122.7722 | -0.13733 | 0.41656 | 122.9645 | 122.8546 | 0.11444 | 122.6944 | 62.9013 | 122.644 | -59.9258 | -122.7631 | 63.2034 | 122.8043 | 62.8784 | 63.4827
2132.9062 | 122.9828 | -62.8555 | 59.903 | -0.045166 | -0.0010105 | -0.010059 | 2.8954 | 0.0015381 | -0.0041956 | -0.0031125 | -0.14066 | 0.16373 | 0.12645 | 0.0021876 | 0.055824 | 0.10799 | -0.0031445 | 0.032043 | 0.14191 | -0.050354 | -0.018311 | 0.064087 | -0.022888 | 0.009155 | 0.59509 | 59.8938 | -62.8876 | 59.9304 | 60.0128 | 59.8206 | 0.39825 | 62.8052 | -59.761 | -59.9213 | 62.9196 | 62.8647 | 62.8326 | 0.059509 | 0.027466 | -0.032043 | -0.009155 | 0.027466 | 122.8683 | 63.2538 | 122.6761 | 63.2858 | 122.7081 | 0.11444 | 0.032043 | 122.9004 | 122.818 | 0.19226 | 122.7814 | 62.9974 | 122.7493 | -59.9533 | -122.7905 | 62.8372 | 122.7859 | 62.8876 | 63.4506
2133.8281 | 122.9553 | -62.8418 | 59.9304 | 0.054016 | 5.7742e-05 | -0.0092051 | 2.8913 | 0.0026063 | -0.00056396 | -0.00054907 | -0.13455 | 0.16309 | 0.12794 | -0.0063574 | 0.056678 | 0.10671 | 0.0024097 | -0.17395 | 0.19684 | 0.022888 | -0.082397 | 0.036621 | -0.027466 | -0.004578 | 0.5127 | 59.8846 | -62.9013 | 59.8938 | 59.9762 | 59.7931 | 0.37079 | 62.8647 | -59.7336 | -60.0128 | 62.8784 | 62.8372 | 62.8143 | -0.027466 | -0.050354 | -0.059509 | -0.045776 | -0.036621 | 122.818 | 63.2126 | 122.6349 | 63.2721 | 122.6944 | 0.013733 | -0.10528 | 122.8775 | 122.7951 | 0.17395 | 122.7859 | 63.0386 | 122.7264 | -59.9075 | -122.8317 | 62.7594 | 122.7356 | 62.6678 | 63.3545
2134.8906 | 123.0835 | -62.8006 | 59.9167 | -0.022278 | 0.00027134 | -0.0098459 | 2.8898 | 0.00046989 | -0.00035036 | -0.0035397 | -0.042999 | 0.16437 | 0.1273 | -0.001444 | 0.056038 | 0.10329 | 5.9726e-05 | 0.036621 | 0.064087 | -0.045776 | 0.068665 | 0.20142 | 0.082397 | 0.10529 | 0.66376 | 59.8206 | -62.8555 | 59.9945 | 60.0906 | 59.9258 | 0.45319 | 62.7548 | -59.8526 | -59.848 | 63.002 | 62.9059 | 62.883 | 0.15106 | 0.12817 | -0.054932 | -0.09613 | 0.07782 | 122.8912 | 63.2538 | 122.7264 | 63.3087 | 122.7814 | 0.24719 | 0.11444 | 122.9462 | 122.85 | 0.10986 | 122.6761 | 62.8647 | 122.6212 | -59.9625 | -122.7722 | 62.8693 | 122.7951 | 62.8372 | 63.4644
2135.8281 | 123.0057 | -62.8372 | 59.9258 | 0.00824 | -0.0031467 | -0.0083505 | 2.8915 | -0.0012391 | 0.00050424 | -0.0026853 | -0.085724 | 0.16245 | 0.1273 | 0.0011194 | 0.054969 | 0.10564 | 0.0013415 | 0.068665 | 0.082397 | -0.032043 | 0.032043 | 0.14648 | 0.050354 | 0.1236 | 0.62714 | 59.8343 | -62.8555 | 59.9899 | 60.0082 | 59.8755 | 0.42114 | 62.8052 | -59.8434 | -59.8938 | 62.9837 | 62.9608 | 62.8876 | 0.15564 | 0.082397 | -0.018311 | -0.091552 | 0.064087 | 122.8455 | 63.2584 | 122.7127 | 63.2767 | 122.731 | 0.17853 | 0.064086 | 122.8638 | 122.8455 | 0.11444 | 122.6898 | 62.9196 | 122.6715 | -59.9579 | -122.7814 | 62.8693 | 122.8271 | 62.9059 | 63.4644
2136.8906 | 123.0606 | -62.8326 | 59.8801 | -0.029907 | -0.0029331 | -0.011555 | 2.8909 | 0.0030335 | -0.0024866 | -0.0041807 | -0.067413 | 0.16224 | 0.12815 | -0.0012304 | 0.054969 | 0.10479 | 0.00048713 | -0.004578 | 0.050354 | -0.07782 | -0.036621 | 0.022888 | -0.064087 | 0.064087 | 0.56763 | 59.8251 | -62.8922 | 59.967 | 60.0357 | 59.8846 | 0.3479 | 62.7548 | -59.8297 | -59.9167 | 62.8555 | 62.8967 | 62.7686 | 0.14191 | 0.013733 | -0.059509 | -0.054932 | 0.086975 | 122.8683 | 63.1805 | 122.7173 | 63.2401 | 122.7768 | 0.10071 | 0.041199 | 122.9279 | 122.8592 | 0.12817 | 122.7173 | 62.883 | 122.6578 | -59.9579 | -122.7722 | 62.796 | 122.7997 | 62.8281 | 63.4003
2137.8281 | 122.9462 | -62.8418 | 59.9258 | -0.014649 | -0.0016513 | -0.0092051 | 2.892 | 0.0015381 | -0.0014184 | -0.0014035 | -0.10403 | 0.16352 | 0.13072 | 0.00026495 | 0.056251 | 0.10457 | -0.0018629 | 0.045776 | 0.12817 | -0.041199 | -0.022888 | 0.068665 | -0.013733 | 0.07782 | 0.60425 | 59.8892 | -62.9013 | 59.8892 | 59.9854 | 59.8022 | 0.37537 | 62.8006 | -59.7977 | -59.9487 | 62.9105 | 62.9196 | 62.8281 | 0.11902 | 0.027466 | -0.059509 | -0.036621 | -0.036621 | 122.8271 | 63.2172 | 122.644 | 63.2767 | 122.7036 | 0.10986 | 0.018311 | 122.8867 | 122.7905 | 0.16937 | 122.7905 | 62.97 | 122.731 | -59.967 | -122.8271 | 62.8189 | 122.731 | 62.8876 | 63.446
2138.8906 | 123.0469 | -62.851 | 59.8892 | -0.022278 | -0.0020785 | -0.0070687 | 2.8903 | 0.0015381 | -0.0024866 | -0.0028989 | -0.082672 | 0.16352 | 0.12709 | -0.00080325 | 0.056892 | 0.10415 | -0.0022901 | -0.064087 | 0.009155 | -0.11902 | -0.073242 | 0.041199 | -0.07782 | 0 | 0.48981 | 59.8206 | -62.8784 | 60.0723 | 59.9945 | 59.8663 | 0.31586 | 62.7319 | -59.8801 | -59.9625 | 62.8922 | 62.851 | 62.7731 | 0.11902 | 0.041199 | -0.027466 | -0.068664 | 0.18311 | 122.8455 | 63.1668 | 122.7173 | 63.1943 | 122.7448 | 0.16022 | 0.045777 | 122.8729 | 122.9507 | 0.12817 | 122.699 | 62.8601 | 122.6715 | -60.0082 | -122.7676 | 62.7777 | 122.9233 | 62.7869 | 63.3408
2139.8438 | 122.9141 | -62.8693 | 59.935 | -0.029907 | -0.0020785 | -0.0081369 | 2.8943 | 0.0034607 | -0.00099116 | -0.0022581 | -0.20169 | 0.1648 | 0.12751 | -0.0044348 | 0.054969 | 0.10457 | 0.00070073 | -0.045776 | 0.059509 | -0.11902 | -0.10071 | -0.036621 | -0.13275 | -0.059509 | 0.45319 | 59.8618 | -62.9013 | 59.9808 | 59.9213 | 59.7382 | 0.32501 | 62.7502 | -59.8755 | -60.0357 | 62.8326 | 62.8098 | 62.7365 | 0.05951 | -0.013732 | -0.032043 | -0.073243 | 0.045776 | 122.7905 | 63.1943 | 122.6074 | 63.2263 | 122.6395 | 0.082398 | 0.018311 | 122.8226 | 122.8821 | 0.17853 | 122.7631 | 62.9288 | 122.731 | -60.054 | -122.8363 | 62.7686 | 122.85 | 62.8235 | 63.3224
2140.8906 | 123.0515 | -62.8418 | 59.8755 | -0.068054 | 0.00048494 | -0.011768 | 2.8928 | 0.0062379 | -0.0016322 | -0.0028989 | -0.015534 | 0.16459 | 0.12773 | -0.0050756 | 0.055824 | 0.10436 | -0.00036747 | -0.013733 | 0.018311 | -0.09613 | -0.036621 | 0.059509 | -0.027466 | 0.10529 | 0.48981 | 59.8251 | -62.8693 | 59.935 | 60.022 | 59.8618 | 0.36163 | 62.7457 | -59.8572 | -59.9121 | 62.9013 | 62.9471 | 62.8143 | 0.20142 | 0.068664 | -0.027466 | -0.050354 | 0.05951 | 122.8638 | 63.2034 | 122.7036 | 63.2309 | 122.731 | 0.15564 | 0.059509 | 122.8912 | 122.8043 | 0.11444 | 122.6944 | 62.8601 | 122.6669 | -59.9716 | -122.7448 | 62.8052 | 122.7768 | 62.8281 | 63.3316
2141.8281 | 122.9828 | -62.8464 | 59.9442 | -0.014649 | -0.0016513 | -0.0094187 | 2.8918 | 0.0021789 | -0.002273 | 9.193e-05 | -0.10709 | 0.16437 | 0.12773 | -0.002085 | 0.054115 | 0.10457 | -0.0044263 | 0.15106 | 0.16479 | -0.022888 | 0.032043 | 0.054932 | -0.009155 | 0.41199 | 0.44403 | 59.8984 | -62.9013 | 59.9396 | 59.9854 | 59.816 | 0.44403 | 62.8235 | -59.7794 | -59.9121 | 62.9013 | 63.2584 | 62.8372 | 0.43488 | 0.013733 | -0.054931 | -0.045777 | -0.004578 | 122.8317 | 63.2904 | 122.6624 | 63.3453 | 122.7173 | 0.07782 | 0.054931 | 122.8867 | 122.8409 | 0.18768 | 122.7997 | 63.0112 | 122.7448 | -59.967 | -122.8455 | 62.8784 | 122.7859 | 62.9974 | 63.2904
2142.8906 | 123.0377 | -62.8967 | 59.8572 | -0.068054 | -0.0022923 | -0.0085641 | 2.8918 | 0.00068369 | -0.0024866 | -0.0016171 | -0.097931 | 0.16117 | 0.12965 | -0.00058965 | 0.054969 | 0.10137 | -0.0033581 | 0.009155 | -0.018311 | -0.10529 | 0.004578 | 0.082397 | -0.068665 | 0.059509 | 0.62714 | 59.7839 | -62.8922 | 60.0266 | 60.0311 | 59.8663 | 0.34332 | 62.7914 | -59.8755 | -59.8526 | 62.9791 | 62.9562 | 62.8281 | 0.16479 | 0.036621 | 0.004578 | -0.073242 | 0.16937 | 122.9279 | 63.2401 | 122.7631 | 63.2355 | 122.7585 | 0.18768 | 0.10986 | 122.9233 | 122.9187 | 0.086975 | 122.6761 | 62.8784 | 122.6807 | -59.9625 | -122.7493 | 62.9013 | 122.9233 | 62.9059 | 63.5239
2143.8281 | 122.9462 | -62.8555 | 59.8984 | -0.007019 | -0.0014377 | -0.0081369 | 2.8922 | -0.0012391 | -0.00013676 | -0.00097627 | -0.091827 | 0.16202 | 0.12773 | -0.001444 | 0.05561 | 0.10372 | -0.0020765 | 0.050354 | 0.10071 | -0.045776 | 0.032043 | 0.10071 | 0.004578 | 0.050354 | 0.57678 | 59.8709 | -62.8647 | 59.8984 | 59.9808 | 59.7931 | 0.39825 | 62.8098 | -59.7977 | -59.8663 | 62.9562 | 62.9059 | 62.8601 | 0.09613 | 0.050354 | -0.009155 | -0.027465 | 0 | 122.8363 | 63.2538 | 122.6486 | 63.2629 | 122.6578 | 0.14648 | 0.077819 | 122.8455 | 122.7631 | 0.14648 | 122.7356 | 62.9562 | 122.7264 | -59.9442 | -122.7631 | 62.8876 | 122.7539 | 62.9059 | 63.4323
2144.8906 | 123.0331 | -62.8555 | 59.9121 | -0.068054 | -0.0016513 | -0.0079233 | 2.8915 | -0.00017091 | -0.00056396 | -0.0011899 | -0.07962 | 0.16309 | 0.12815 | 0.00047855 | 0.056038 | 0.10436 | -0.0054945 | 0.059509 | 0.073242 | -0.032043 | 0.059509 | 0.15106 | 0.091553 | 0.15564 | 0.64087 | 59.8618 | -62.8738 | 60.1089 | 60.0449 | 59.9121 | 0.4715 | 62.8235 | -59.8389 | -59.8526 | 63.0066 | 63.0112 | 62.9471 | 0.18768 | 0.1236 | -0.01831 | -0.050354 | 0.19684 | 122.9004 | 63.327 | 122.7676 | 63.3453 | 122.7859 | 0.18311 | 0.091552 | 122.9187 | 122.9828 | 0.10529 | 122.7356 | 62.9288 | 122.7173 | -59.9442 | -122.7859 | 62.915 | 122.9645 | 62.915 | 63.4964
2145.8281 | 122.9599 | -62.8555 | 59.9396 | -0.060425 | -0.0020785 | -0.010273 | 2.8915 | -0.0035889 | -0.0016322 | -0.0035397 | -0.076569 | 0.16224 | 0.1273 | -0.01063 | 0.054115 | 0.10479 | -0.0022901 | 0.036621 | 0.10529 | -0.032043 | 0.009155 | 0.10529 | 0.027466 | 0.045776 | 0.59052 | 59.8892 | -62.8693 | 59.8846 | 59.9808 | 59.816 | 0.37994 | 62.8235 | -59.8343 | -59.9304 | 62.9608 | 62.9013 | 62.883 | 0.077819 | 0.059509 | -0.013733 | -0.050354 | -0.054931 | 122.8363 | 63.2355 | 122.6715 | 63.2492 | 122.6852 | 0.13733 | 0.041198 | 122.85 | 122.7539 | 0.13733 | 122.7585 | 62.9608 | 122.7448 | -59.9716 | -122.8088 | 62.8647 | 122.7402 | 62.8922 | 63.446
2146.8906 | 123.0698 | -62.8006 | 59.8892 | 0.00061049 | -0.00079686 | -0.0094187 | 2.8926 | 0.0023925 | -0.00056396 | 0.0020145 | -0.058258 | 0.16202 | 0.12901 | -0.0055028 | 0.055824 | 0.10415 | -0.0033581 | 0.018311 | 0.050354 | -0.050354 | 0.027466 | 0.14191 | 0.036621 | 0.082397 | 0.63629 | 59.8206 | -62.8738 | 59.9945 | 60.0861 | 59.935 | 0.44861 | 62.7502 | -59.8389 | -59.8618 | 62.9425 | 62.883 | 62.8372 | 0.13275 | 0.086975 | -0.073242 | -0.068664 | 0.10529 | 122.8867 | 63.2492 | 122.7356 | 63.3224 | 122.8088 | 0.19226 | 0.07782 | 122.9599 | 122.8683 | 0.10071 | 122.6944 | 62.851 | 122.6212 | -59.9396 | -122.7631 | 62.8281 | 122.7951 | 62.8189 | 63.4369
2147.8281 | 122.9416 | -62.8967 | 59.9396 | -0.007019 | -0.0010105 | -0.0085641 | 2.8933 | 0.0011109 | -0.0029138 | 0.0011599 | -0.11929 | 0.16416 | 0.12858 | 0.003042 | 0.055824 | 0.10628 | -0.0029309 | 0.009155 | 0.13733 | -0.032043 | -0.013733 | 0.059509 | -0.022888 | 0.027466 | 0.53558 | 59.8801 | -62.8876 | 59.8572 | 60.1776 | 59.5917 | 0.24719 | 62.8647 | -59.8022 | -59.9533 | 62.9562 | 62.9242 | 62.8738 | 0.059509 | 0.009155 | 0.009156 | -0.059509 | -0.082397 | 123.0743 | 63.1439 | 122.4884 | 63.1348 | 122.4792 | 0.091552 | 0.01831 | 123.0652 | 122.7448 | 0.16937 | 122.7676 | 63.0341 | 122.7768 | -59.9716 | -122.8271 | 62.883 | 122.7539 | 62.9059 | 63.4323
2148.8906 | 123.0515 | -62.8555 | 59.8938 | -0.098572 | -0.0014377 | -0.0087777 | 2.8918 | -0.0018799 | -0.0018458 | -0.00033547 | -0.064362 | 0.16181 | 0.12709 | -0.0012304 | 0.057533 | 0.10286 | -0.0057081 | -0.045776 | 0.054932 | -0.086975 | -0.032043 | 0.064087 | -0.032043 | 0.018311 | 0.53558 | 59.8434 | -62.883 | 59.9533 | 60.0403 | 59.8709 | 0.37994 | 62.7686 | -59.8389 | -59.9258 | 62.9196 | 62.8738 | 62.8235 | 0.10529 | 0.054932 | -0.027466 | -0.050354 | 0.059509 | 122.8958 | 63.2355 | 122.7264 | 63.2629 | 122.7539 | 0.15106 | 0.054932 | 122.9233 | 122.8363 | 0.14191 | 122.7264 | 62.9105 | 122.699 | -59.9808 | -122.7768 | 62.8235 | 122.8088 | 62.8098 | 63.3911
2149.8281 | 122.9874 | -62.8372 | 59.8938 | 0.023498 | -0.00015586 | -0.0094187 | 2.8939 | 4.2692e-05 | -0.00099116 | -0.0020443 | -0.14066 | 0.16523 | 0.13008 | -0.00037605 | 0.056465 | 0.105 | -0.0022901 | 0.027466 | 0.11444 | -0.036621 | -0.013733 | 0.054932 | -0.036621 | 0.027466 | 0.59509 | 59.8709 | -62.883 | 59.935 | 59.9991 | 59.8068 | 0.39368 | 62.8006 | -59.7794 | -59.9075 | 62.8922 | 62.8647 | 62.8006 | 0.064087 | 0 | -0.045777 | -0.022888 | 0.041199 | 122.8363 | 63.2309 | 122.644 | 63.2767 | 122.6898 | 0.091553 | 0.022888 | 122.8821 | 122.818 | 0.15106 | 122.7539 | 62.9517 | 122.7081 | -59.9304 | -122.7768 | 62.8235 | 122.7722 | 62.8647 | 63.4323
2150.8906 | 123.0515 | -62.8326 | 59.8709 | -0.045166 | -0.0016513 | -0.0062143 | 2.8928 | -0.00081171 | -0.00056396 | -0.00012167 | -0.15286 | 0.16224 | 0.12751 | -0.004862 | 0.056892 | 0.10457 | -0.0010083 | -0.050354 | -0.041199 | -0.14648 | -0.064087 | 0.022888 | -0.10529 | -0.032043 | 0.52185 | 59.8206 | -62.915 | 59.9808 | 60.0586 | 59.848 | 0.31586 | 62.6862 | -59.9121 | -59.935 | 62.8555 | 62.8006 | 62.7274 | 0.11444 | 0.041198 | -0.082397 | -0.050354 | 0.10986 | 122.8912 | 63.1485 | 122.6807 | 63.2309 | 122.7631 | 0.16937 | 0.082397 | 122.9736 | 122.8958 | 0.10529 | 122.7356 | 62.7914 | 122.6532 | -60.0174 | -122.7859 | 62.7686 | 122.8134 | 62.7823 | 63.3545
2151.8281 | 122.9782 | -62.8693 | 59.9258 | -0.12909 | -0.0022923 | -0.0072825 | 2.8933 | 0.00046989 | -0.00099116 | -0.0020443 | -0.10403 | 0.16566 | 0.1288 | -0.0025122 | 0.056251 | 0.10372 | 0.00070073 | 0.045776 | 0.20142 | -0.004578 | -0.027466 | 0.041199 | -0.059509 | 0.013733 | 0.51727 | 59.8755 | -62.8738 | 59.8755 | 59.9762 | 59.7748 | 0.3891 | 62.8647 | -59.7244 | -59.9533 | 62.9105 | 62.883 | 62.8098 | 0.018311 | -0.054931 | -0.004577 | -0.050354 | -0.050354 | 122.8455 | 63.2584 | 122.644 | 63.2629 | 122.6486 | 0.045777 | -0.022888 | 122.85 | 122.7493 | 0.20599 | 122.7493 | 63.0707 | 122.7448 | -59.9304 | -122.7997 | 62.8418 | 122.7448 | 62.915 | 63.3865
2152.8906 | 123.0377 | -62.851 | 59.8755 | -0.060425 | -0.0014377 | -0.0072825 | 2.893 | -0.00059811 | -0.0016322 | -0.0020443 | -0.052155 | 0.16309 | 0.12986 | -0.006571 | 0.055824 | 0.10265 | 0.00070073 | -0.09613 | 0.045776 | -0.073242 | -0.064087 | 0.059509 | -0.059509 | 0.004578 | 0.51727 | 59.848 | -62.883 | 59.9487 | 60.0266 | 59.8663 | 0.36163 | 62.7777 | -59.8297 | -59.9396 | 62.9105 | 62.8555 | 62.7914 | 0.07782 | 0.013733 | -0.032044 | -0.027466 | 0.073242 | 122.8775 | 63.2126 | 122.7173 | 63.2446 | 122.7493 | 0.13275 | 0.009155 | 122.9095 | 122.8317 | 0.11902 | 122.731 | 62.8967 | 122.699 | -59.9487 | -122.7585 | 62.7869 | 122.7997 | 62.7548 | 63.3682
2153.8281 | 122.9279 | -62.8601 | 59.9304 | 0.00061049 | -0.0012241 | -0.012196 | 2.8922 | 0.0032471 | 0.0015722 | -0.0024717 | -0.11929 | 0.16437 | 0.12773 | -0.0025122 | 0.055397 | 0.10436 | -0.00015387 | 0.50812 | 0.19684 | 0.032043 | -0.091553 | 0.036621 | -0.086975 | -0.018311 | 0.54016 | 59.903 | -62.9059 | 59.8938 | 59.9716 | 59.7839 | 0.37994 | 62.8922 | -59.7336 | -60.022 | 62.8967 | 62.8418 | 62.7731 | -0.050354 | -0.11902 | -0.045777 | -0.027466 | -0.036621 | 122.8317 | 63.2401 | 122.644 | 63.2858 | 122.6898 | 0.004578 | -0.1236 | 122.8775 | 122.7997 | 0.1648 | 122.8088 | 63.0569 | 122.7631 | -59.8984 | -122.8363 | 62.7686 | 122.7539 | 63.3682 | 63.4003
2154.9062 | 122.9462 | -62.883 | 59.8984 | -0.052796 | -0.00015586 | -0.0070687 | 2.893 | 0.0036743 | -0.0016322 | -0.0014035 | -0.16507 | 0.16331 | 0.12901 | -0.0010168 | 0.05561 | 0.1065 | -0.0025037 | -0.059509 | 0.064087 | -0.1236 | -0.12817 | -0.059509 | -0.15564 | -0.11902 | 0.4303 | 59.8709 | -62.9288 | 59.8526 | 59.9167 | 59.7198 | 0.25177 | 62.7594 | -59.8343 | -60.0266 | 62.8235 | 62.764 | 62.7274 | 0.004577 | -0.032044 | -0.045776 | -0.027465 | -0.045776 | 122.7997 | 63.1348 | 122.6028 | 63.1805 | 122.6486 | 0.064087 | -0.004578 | 122.8455 | 122.7814 | 0.18768 | 122.7997 | 62.9471 | 122.7539 | -60.022 | -122.8271 | 62.7548 | 122.7356 | 62.8235 | 63.3133
2155.8281 | 122.9324 | -62.8693 | 59.9396 | -0.022278 | -0.0018649 | -0.0087777 | 2.8894 | -0.0010253 | -0.002273 | -0.0028989 | -0.14066 | 0.16437 | 0.1288 | -0.001444 | 0.057747 | 0.10393 | -0.0050671 | 0.004578 | 0.16479 | -0.032043 | 0.43945 | 0.17395 | -0.39368 | -0.091553 | 0.52643 | 59.8663 | -62.8967 | 59.8892 | 59.9579 | 59.7794 | 0.37079 | 62.8372 | -59.7748 | -59.5001 | 63.0432 | 62.7777 | 62.4756 | -0.05951 | -0.36163 | -0.027466 | -0.073242 | -0.050354 | 122.8271 | 63.2401 | 122.6486 | 63.2675 | 122.6761 | 0.20599 | 0.4715 | 122.8546 | 122.7859 | 0.19684 | 122.7631 | 63.0341 | 122.7356 | -59.9716 | -122.8363 | 63.3087 | 122.7585 | 62.8738 | 63.3957
2156.8906 | 123.0789 | -62.8326 | 59.903 | -0.029907 | -0.0010105 | -0.0070687 | 2.8915 | 0.00068369 | 0.00093144 | -0.0035397 | -0.015534 | 0.16288 | 0.12837 | -0.0050756 | 0.056038 | 0.10628 | -0.00079467 | 0.022888 | 0.07782 | -0.054932 | 0 | 0.16937 | 0.086975 | 0.091553 | 0.65918 | 59.8251 | -62.8693 | 60.0037 | 60.1181 | 59.9396 | 0.46234 | 62.7777 | -59.8251 | -59.903 | 63.002 | 62.9242 | 62.9196 | 0.14649 | 0.14191 | -0.036621 | -0.07782 | 0.10071 | 122.9507 | 63.295 | 122.7722 | 63.3316 | 122.8088 | 0.22431 | 0.054932 | 122.9874 | 122.8729 | 0.13275 | 122.6944 | 62.9105 | 122.6578 | -59.9579 | -122.7722 | 62.8326 | 122.8363 | 62.8555 | 63.4918
2157.8281 | 122.9782 | -62.8601 | 59.9579 | 0.015869 | 0.00027134 | -0.0098459 | 2.8937 | -0.00017091 | -0.0016322 | 0.0024417 | -0.11014 | 0.16459 | 0.12773 | 0.00047855 | 0.056251 | 0.10436 | -0.00036747 | 0.018311 | 0.11444 | -0.073242 | -0.022888 | 0.045776 | -0.013733 | 0.027466 | 0.53558 | 59.9075 | -62.8876 | 59.8938 | 59.9762 | 59.816 | 0.39368 | 62.7869 | -59.8434 | -59.9808 | 62.9059 | 62.8876 | 62.8464 | 0.10071 | 0.059509 | -0.027466 | -0.050354 | -0.064087 | 122.8363 | 63.2538 | 122.6761 | 63.2812 | 122.7036 | 0.11902 | 0.050354 | 122.8638 | 122.7814 | 0.18768 | 122.7951 | 62.9745 | 122.7676 | -60.0311 | -122.8455 | 62.8372 | 122.7539 | 62.8784 | 63.3957
2158.8906 | 123.0515 | -62.8418 | 59.8938 | -0.052796 | -0.00079686 | -0.0092051 | 2.8918 | -0.00038451 | -0.0020594 | -0.00033547 | -0.058258 | 0.16224 | 0.1288 | -0.010203 | 0.056678 | 0.10329 | 0.0015551 | -0.032043 | 0.041199 | -0.054932 | -0.036621 | 0.073242 | -0.041199 | 0.018311 | 0.52185 | 59.8618 | -62.883 | 59.9625 | 60.0082 | 59.8755 | 0.37994 | 62.7869 | -59.8526 | -59.9304 | 62.915 | 62.8601 | 62.8006 | 0.073243 | 0.013733 | -0.041199 | -0.032044 | 0.068664 | 122.85 | 63.2217 | 122.7173 | 63.2629 | 122.7585 | 0.12817 | 0.018311 | 122.8912 | 122.8455 | 0.096131 | 122.7448 | 62.883 | 122.7036 | -59.9487 | -122.7768 | 62.8052 | 122.8043 | 62.8098 | 63.3636
2159.8281 | 122.9507 | -62.8876 | 59.9487 | 0.015869 | -0.0012241 | -0.010487 | 2.8918 | 0.0060241 | -0.0029138 | -0.0018307 | -0.088776 | 0.16288 | 0.13072 | -0.0012304 | 0.053688 | 0.10244 | -0.0014355 | -0.009155 | 0.15564 | -0.027466 | -0.036621 | 0.045776 | -0.013733 | 0.027466 | 0.54474 | 59.8663 | -62.8876 | 59.8663 | 59.9625 | 59.7839 | 0.37537 | 62.8601 | -59.7931 | -59.9854 | 62.9333 | 62.915 | 62.8738 | 0.054932 | 0.013733 | 0 | -0.082397 | -0.082397 | 122.85 | 63.2629 | 122.6715 | 63.2629 | 122.6715 | 0.073242 | -0.009155 | 122.85 | 122.7539 | 0.18311 | 122.7539 | 63.0432 | 122.7539 | -59.9762 | -122.8363 | 62.851 | 122.7539 | 62.8784 | 63.4323
2160.8906 | 123.0286 | -62.8693 | 59.8663 | -0.083313 | -0.0020785 | -0.0092051 | 2.8911 | -0.0027343 | -0.0012048 | -0.0041807 | -0.064362 | 0.16267 | 0.12837 | -0.0027258 | 0.056251 | 0.10479 | 0.0032641 | -0.064087 | 0.018311 | -0.10529 | -0.036621 | 0.032043 | -0.07782 | -0.013733 | 0.48065 | 59.8251 | -62.8693 | 59.9075 | 60.0082 | 59.8297 | 0.32501 | 62.764 | -59.848 | -59.903 | 62.9013 | 62.8555 | 62.7914 | 0.091553 | 0.027466 | 0 | -0.041199 | 0.041199 | 122.8775 | 63.1943 | 122.699 | 63.1943 | 122.699 | 0.13733 | 0.068665 | 122.8775 | 122.7768 | 0.1236 | 122.6944 | 62.8876 | 122.6944 | -59.9716 | -122.7356 | 62.8326 | 122.7768 | 62.8052 | 63.3499
2161.8281 | 122.9553 | -62.8693 | 59.9167 | -0.090943 | -0.0027195 | -0.0092051 | 2.8926 | 0.0032471 | -0.0014184 | -0.00054907 | -0.1376 | 0.1648 | 0.12666 | -0.00058965 | 0.054969 | 0.10521 | 0.0026233 | 0.009155 | 0.16022 | -0.027466 | -0.21973 | -0.25635 | 0.036621 | 0 | 0.52643 | 59.8709 | -62.8967 | 59.8892 | 59.9487 | 59.7794 | 0.37994 | 62.8418 | -59.7565 | -60.1364 | 62.6129 | 62.8693 | 62.9059 | 0.027466 | 0.064087 | -0.027466 | -0.045776 | -0.027466 | 122.818 | 63.2492 | 122.6486 | 63.2767 | 122.6761 | -0.22888 | -0.19226 | 122.8455 | 122.7859 | 0.18768 | 122.7676 | 63.0295 | 122.7402 | -59.9442 | -122.8134 | 62.6495 | 122.7585 | 62.8784 | 63.3957
2162.8906 | 123.0286 | -62.8647 | 59.8984 | -0.052796 | -0.0014377 | -0.0081369 | 2.8928 | 0.0013245 | 0.00050424 | -0.0011899 | -0.067413 | 0.16202 | 0.12388 | -0.0050756 | 0.056678 | 0.10372 | -0.0035719 | -0.054932 | 0.041199 | -0.09613 | -0.045776 | 0.032043 | -0.041199 | 0.009155 | 0.5127 | 59.8434 | -62.883 | 59.9258 | 60.0082 | 59.8297 | 0.34332 | 62.7686 | -59.8572 | -59.9442 | 62.8967 | 62.8738 | 62.8235 | 0.10528 | 0.054931 | -0.018311 | -0.054931 | 0.027466 | 122.8729 | 63.208 | 122.6944 | 63.2263 | 122.7127 | 0.12817 | 0.050354 | 122.8912 | 122.8088 | 0.13733 | 122.7264 | 62.9059 | 122.7081 | -59.9945 | -122.7814 | 62.8189 | 122.7905 | 62.8098 | 63.3774
2163.8281 | 122.9416 | -62.8693 | 59.8984 | 0.046386 | 5.7742e-05 | -0.0089913 | 2.8935 | 0.0015381 | -0.0016322 | 0.00073273 | -0.082672 | 0.16523 | 0.12858 | 0.00047855 | 0.056678 | 0.10265 | 0.0021961 | 0.022888 | 0.15564 | -0.032043 | -0.036621 | 0.036621 | -0.027466 | 0.032043 | 0.43488 | 59.8984 | -62.851 | 59.8846 | 59.903 | 59.8068 | 0.40283 | 62.8372 | -59.7427 | -59.935 | 62.9059 | 62.9013 | 62.8418 | 0.064086 | 0.004577 | 0.018311 | 0 | -0.013732 | 122.7722 | 63.2721 | 122.6761 | 63.2538 | 122.6578 | 0.068664 | -0.004578 | 122.7539 | 122.7356 | 0.18768 | 122.7493 | 63.0249 | 122.7676 | -59.9304 | -122.7493 | 62.8326 | 122.7539 | 62.8922 | 63.3041
2164.8906 | 123.056 | -62.8372 | 59.8801 | -0.060425 | -0.0010105 | -0.0083505 | 2.8903 | 0.00025629 | -0.0018458 | -0.0052487 | -0.052155 | 0.16309 | 0.1288 | -0.00080325 | 0.054115 | 0.10415 | -0.0037855 | 0.022888 | 0.068665 | -0.050354 | 0.036621 | 0.13733 | 0.027466 | 0.086975 | 0.6546 | 59.8251 | -62.8738 | 59.9945 | 60.0861 | 59.935 | 0.43488 | 62.7869 | -59.8114 | -59.8434 | 62.9745 | 62.9242 | 62.8647 | 0.13733 | 0.07782 | -0.036621 | -0.054932 | 0.11444 | 122.9233 | 63.2721 | 122.7722 | 63.3087 | 122.8088 | 0.18768 | 0.086975 | 122.9599 | 122.8683 | 0.11902 | 122.699 | 62.9059 | 122.6624 | -59.9304 | -122.7539 | 62.8738 | 122.8317 | 62.8601 | 63.4918
2165.8281 | 122.9874 | -62.8555 | 59.8984 | -0.022278 | -0.0010105 | -0.0094187 | 2.8939 | 0.0036743 | -0.00056396 | -0.00033547 | -0.17728 | 0.16544 | 0.12751 | 0.00090575 | 0.05561 | 0.10222 | -0.0042127 | 0.041199 | 0.14191 | -0.041199 | -0.009155 | 0.059509 | -0.013733 | 0.018311 | 0.59509 | 59.8892 | -62.8922 | 59.935 | 60.0082 | 59.8022 | 0.38452 | 62.8143 | -59.7565 | -59.9075 | 62.915 | 62.8738 | 62.8418 | 0.05951 | 0.027466 | -0.036621 | -0.009155 | 0.036622 | 122.8638 | 63.2401 | 122.6578 | 63.2767 | 122.6944 | 0.10071 | 0.032044 | 122.9004 | 122.8271 | 0.18311 | 122.7814 | 62.9974 | 122.7448 | -59.9396 | -122.7905 | 62.8464 | 122.7905 | 62.8967 | 63.4506
2166.8906 | 123.056 | -62.8372 | 59.8755 | -0.090943 | -0.00058326 | -0.0077097 | 2.8911 | 0.0019653 | -0.00077756 | -0.0035397 | -0.052155 | 0.16202 | 0.12773 | -0.01063 | 0.05796 | 0.10436 | -0.00015387 | 0.21515 | 0.050354 | -0.064087 | -0.036621 | 0.059509 | -0.073242 | 0.004578 | 0.52185 | 59.8251 | -62.8647 | 59.935 | 60.0311 | 59.8572 | 0.37537 | 62.7731 | -59.8251 | -59.9121 | 62.8967 | 62.8418 | 62.764 | 0.068665 | -0.009155 | -0.027466 | -0.050354 | 0.05951 | 122.8683 | 63.2126 | 122.6944 | 63.2401 | 122.7219 | 0.1236 | 0.027466 | 122.8958 | 122.7997 | 0.11444 | 122.6898 | 62.8876 | 122.6624 | -59.9396 | -122.7402 | 62.8006 | 122.7722 | 63.0524 | 63.3591
2167.8281 | 122.9874 | -62.8693 | 59.9304 | 0.015869 | 0.00027134 | -0.0077097 | 2.8928 | 0.0026063 | 7.6842e-05 | 0.0011599 | -0.15897 | 0.16352 | 0.12858 | -0.0016576 | 0.056678 | 0.10436 | -0.0031445 | 0.027466 | 0.14648 | -0.041199 | -0.004578 | 0.045776 | -0.009155 | 0.018311 | 0.57678 | 59.8846 | -62.851 | 59.9304 | 59.9991 | 59.8297 | 0.40283 | 62.8281 | -59.7839 | -59.935 | 62.915 | 62.8876 | 62.8601 | 0.05951 | 0.032044 | 0.018311 | -0.045776 | 0 | 122.8683 | 63.2721 | 122.699 | 63.2538 | 122.6807 | 0.086975 | 0.036621 | 122.85 | 122.7814 | 0.18768 | 122.7356 | 63.0157 | 122.7539 | -59.9716 | -122.7814 | 62.8647 | 122.7997 | 62.8967 | 63.446
2168.8906 | 123.056 | -62.8326 | 59.8709 | -0.007019 | -0.0029331 | -0.010487 | 2.893 | -0.0027343 | -0.00013676 | -0.0035397 | -0.052155 | 0.16117 | 0.12645 | -0.0040076 | 0.055824 | 0.10244 | -0.0035719 | 0 | 0.045776 | -0.068665 | -0.004578 | 0.10071 | 0.004578 | 0.07782 | 0.59967 | 59.8251 | -62.8647 | 59.9945 | 60.0723 | 59.903 | 0.4303 | 62.764 | -59.8251 | -59.8755 | 62.9333 | 62.9105 | 62.8372 | 0.14649 | 0.073243 | -0.032043 | -0.045777 | 0.1236 | 122.905 | 63.2629 | 122.7356 | 63.295 | 122.7676 | 0.16937 | 0.064087 | 122.937 | 122.8592 | 0.11444 | 122.6898 | 62.8784 | 122.6578 | -59.9396 | -122.7356 | 62.8281 | 122.8271 | 62.8326 | 63.4323
2169.8281 | 122.9553 | -62.8738 | 59.9487 | -0.037537 | -0.0022923 | -0.0089913 | 2.8939 | 0.0013245 | -0.0012048 | 0.0013735 | -0.14066 | 0.16373 | 0.12901 | -0.0016576 | 0.056251 | 0.10222 | -0.0020765 | 0.022888 | 0.16022 | -0.032043 | -0.29297 | 0.068665 | -0.036621 | -0.091553 | 0.50354 | 59.8892 | -62.9059 | 59.8938 | 59.967 | 59.7931 | 0.37994 | 62.8418 | -59.7885 | -60.2417 | 62.9425 | 62.7823 | 62.8372 | -0.05951 | -0.004578 | -0.032044 | -0.059509 | -0.054931 | 122.8409 | 63.2538 | 122.6669 | 63.2858 | 122.699 | 0.10071 | -0.26093 | 122.8729 | 122.7997 | 0.19226 | 122.7951 | 63.0341 | 122.7631 | -59.9808 | -122.8546 | 62.5809 | 122.7676 | 62.8967 | 63.3774
2170.8906 | 123.0515 | -62.851 | 59.8709 | -0.068054 | -0.00079686 | -0.0092051 | 2.8947 | 0.0015381 | -0.0018458 | -0.0026853 | -0.06131 | 0.16373 | 0.12794 | -0.0069982 | 0.057319 | 0.10329 | -0.0014355 | -0.045776 | 0.018311 | -0.11444 | -0.050354 | 0.041199 | -0.032043 | 0.14191 | 0.54474 | 59.8343 | -62.883 | 59.9258 | 60.022 | 59.8434 | 0.35706 | 62.7365 | -59.8526 | -59.9213 | 62.8922 | 62.9929 | 62.8189 | 0.25635 | 0.082398 | -0.032044 | -0.036621 | 0.054931 | 122.8729 | 63.208 | 122.6944 | 63.2401 | 122.7264 | 0.15564 | 0.064087 | 122.905 | 122.8088 | 0.13275 | 122.7173 | 62.8693 | 122.6852 | -59.9854 | -122.7539 | 62.8006 | 122.7768 | 62.8052 | 63.3957
2171.8281 | 122.9736 | -62.8647 | 59.9167 | 0.023498 | -0.0020785 | -0.0083505 | 2.8941 | 0.0047425 | 7.6842e-05 | 0.0018009 | -0.15286 | 0.16608 | 0.12858 | 0.00026495 | 0.054115 | 0.10436 | -0.0012219 | 0.013733 | 0.11444 | -0.07782 | -0.018311 | 0.07782 | -0.036621 | 0 | 0.59509 | 59.8892 | -62.9013 | 59.9213 | 60.0082 | 59.8022 | 0.37994 | 62.7869 | -59.8022 | -59.935 | 62.9425 | 62.8647 | 62.8281 | 0.07782 | 0.041199 | -0.036621 | -0.027466 | 0.004578 | 122.8729 | 63.2446 | 122.6669 | 63.2812 | 122.7036 | 0.15564 | 0.059509 | 122.9095 | 122.8226 | 0.19226 | 122.7905 | 62.9791 | 122.7539 | -59.9945 | -122.818 | 62.8464 | 122.7859 | 62.8784 | 63.4598
2172.8906 | 123.0469 | -62.8143 | 59.9075 | -0.068054 | -0.0025059 | -0.0092051 | 2.8911 | -0.0023071 | -0.0016322 | 0.0015871 | -0.055206 | 0.16202 | 0.1273 | -0.006571 | 0.056038 | 0.10201 | -0.0016493 | 0.032043 | 0.073242 | -0.009155 | -0.32959 | 0.13275 | 0.09613 | -0.036621 | 0.62256 | 59.8389 | -62.8647 | 59.967 | 60.0769 | 59.8984 | 0.45319 | 62.8052 | -59.8343 | -60.2371 | 62.9471 | 62.7777 | 62.9105 | -0.027466 | 0.10528 | -0.050354 | -0.068665 | 0.059509 | 122.8912 | 63.2675 | 122.7127 | 63.3179 | 122.7631 | 0.14191 | -0.32043 | 122.9416 | 122.8317 | 0.082397 | 122.7036 | 62.8876 | 122.6532 | -59.9167 | -122.7722 | 62.4847 | 122.7814 | 62.8464 | 63.4369
2173.8281 | 122.9919 | -62.8418 | 59.9396 | -0.022278 | -0.0014377 | -0.0098459 | 2.8918 | 0.0021789 | 0.0013586 | 0.00073273 | -0.10403 | 0.16566 | 0.12709 | 5.1352e-05 | 0.054969 | 0.1035 | -0.0012219 | 0.022888 | 0.1236 | -0.045776 | -0.027466 | 0.064087 | -0.036621 | 0.004578 | 0.54016 | 59.8984 | -62.8876 | 59.9213 | 60.0082 | 59.8251 | 0.40283 | 62.796 | -59.816 | -59.967 | 62.9059 | 62.8464 | 62.8052 | 0.050354 | 0.009155 | -0.045776 | -0.041199 | -0.01831 | 122.85 | 63.2446 | 122.6669 | 63.2904 | 122.7127 | 0.10986 | 0.01831 | 122.8958 | 122.8088 | 0.16937 | 122.7859 | 62.9654 | 122.7402 | -59.9854 | -122.8271 | 62.8143 | 122.7631 | 62.8647 | 63.382
2174.8906 | 123.0469 | -62.8281 | 59.8618 | -0.083313 | -0.00036966 | -0.010487 | 2.8915 | 0.0011109 | -0.0024866 | 0.0011599 | -0.11929 | 0.16331 | 0.12944 | -0.00016245 | 0.05561 | 0.10329 | -0.0022901 | 0.064087 | 0.09613 | -0.022888 | 0.050354 | -0.31128 | 0.045776 | 0.14648 | 0.70038 | 59.8389 | -62.8693 | 59.9854 | 60.0815 | 59.9075 | 0.45319 | 62.8052 | -59.7656 | -59.8114 | 62.5168 | 62.9745 | 62.8738 | 0.16937 | 0.068664 | -0.041199 | -0.022888 | 0.1236 | 122.9095 | 63.2812 | 122.7356 | 63.3224 | 122.7768 | -0.28839 | 0.073242 | 122.9507 | 122.8546 | 0.11902 | 122.7081 | 62.9242 | 122.6669 | -59.8846 | -122.731 | 62.8784 | 122.8134 | 62.8922 | 63.5284
2175.8281 | 122.9874 | -62.8647 | 59.9258 | -0.045166 | 0.0011257 | -0.0085641 | 2.8905 | 0.0023925 | -0.00077756 | -0.00054907 | -0.1254 | 0.16288 | 0.1288 | 0.0026148 | 0.055824 | 0.10521 | -0.0035719 | 0.027466 | 0.12817 | -0.036621 | -0.027466 | 0.032043 | -0.009155 | 0.018311 | 0.54932 | 59.8709 | -62.9196 | 59.9258 | 60.0082 | 59.8068 | 0.39825 | 62.8281 | -59.7977 | -59.9533 | 62.8967 | 62.883 | 62.8555 | 0.054932 | 0.027466 | -0.054932 | -0.054931 | 0 | 122.8729 | 63.2629 | 122.6715 | 63.3179 | 122.7264 | 0.068664 | 0.009155 | 122.9279 | 122.8455 | 0.1648 | 122.7905 | 62.9929 | 122.7356 | -59.9625 | -122.8455 | 62.8372 | 122.7905 | 62.8922 | 63.414
2176.8906 | 123.024 | -62.8738 | 59.848 | -0.060425 | -0.00079686 | -0.010273 | 2.892 | 0.0017517 | -0.00077756 | -0.0037533 | -0.042999 | 0.1616 | 0.12687 | -0.0072118 | 0.057106 | 0.10308 | 0.0017687 | -0.041199 | 0.013733 | -0.086975 | -0.050354 | 0.032043 | -0.054932 | 0.018311 | 0.61798 | 59.8434 | -62.8967 | 59.9304 | 60.0128 | 59.8343 | 0.34332 | 62.7869 | -59.8343 | -59.8984 | 62.9059 | 62.8922 | 62.8189 | 0.10529 | 0.032043 | -0.022889 | -0.004577 | 0.082398 | 122.8867 | 63.2172 | 122.7081 | 63.2401 | 122.731 | 0.11902 | 0.036621 | 122.9095 | 122.8271 | 0.10071 | 122.7402 | 62.8876 | 122.7173 | -59.935 | -122.7448 | 62.8235 | 122.8043 | 62.8326 | 63.4918
2177.8281 | 123.0011 | -62.8738 | 59.8892 | -0.045166 | -0.0014377 | -0.010059 | 2.8924 | 0.00068369 | 0.0026404 | 0.00094633 | -0.18033 | 0.16202 | 0.12516 | -0.00037605 | 0.054329 | 0.10457 | -0.0020765 | 0.032043 | 0.09613 | -0.068665 | -0.009155 | 0.059509 | -0.050354 | -0.004578 | 0.57678 | 59.8663 | -62.883 | 59.935 | 59.9899 | 59.8206 | 0.3891 | 62.8052 | -59.7931 | -59.8984 | 62.9333 | 62.8693 | 62.8235 | 0.064087 | 0.018311 | -0.009156 | -0.022888 | 0.045777 | 122.8638 | 63.2629 | 122.6944 | 63.2721 | 122.7036 | 0.12817 | 0.05951 | 122.8729 | 122.818 | 0.16479 | 122.7493 | 62.97 | 122.7402 | -59.9579 | -122.7722 | 62.8647 | 122.8088 | 62.9059 | 63.4506
2178.8906 | 123.0881 | -62.8006 | 59.8755 | -0.037537 | -0.0027195 | -0.0096323 | 2.8911 | 0.00068369 | -0.0016322 | -0.0020443 | -0.06131 | 0.16331 | 0.12773 | -0.011698 | 0.057106 | 0.10329 | -0.00058107 | 0.022888 | 0.050354 | -0.041199 | 0.059509 | 0.16479 | 0.068665 | 0.12817 | 0.67749 | 59.8297 | -62.8418 | 60.0037 | 60.1089 | 59.9213 | 0.44403 | 62.7594 | -59.8251 | -59.816 | 62.9654 | 62.9288 | 62.8693 | 0.16937 | 0.10986 | -0.041199 | -0.045776 | 0.12817 | 122.9095 | 63.2446 | 122.7219 | 63.2858 | 122.7631 | 0.20599 | 0.10071 | 122.9507 | 122.8455 | 0.091553 | 122.6715 | 62.851 | 122.6303 | -59.9167 | -122.7173 | 62.8601 | 122.8043 | 62.8235 | 63.4781
2179.8281 | 122.9874 | -62.8555 | 59.9396 | -0.022278 | -0.0018649 | -0.010059 | 2.8935 | -0.0010253 | -0.0031274 | -0.0037533 | -0.1376 | 0.1648 | 0.12901 | -0.00080325 | 0.054329 | 0.10521 | -0.0016493 | 0.027466 | 0.13733 | -0.018311 | -0.041199 | 0.041199 | -0.013733 | 0.032043 | 0.54932 | 59.8846 | -62.8738 | 59.9121 | 59.9945 | 59.8206 | 0.41657 | 62.8372 | -59.8022 | -59.9808 | 62.8967 | 62.8876 | 62.8418 | 0.050354 | 0.004578 | -0.01831 | -0.054931 | -0.027466 | 122.85 | 63.2721 | 122.6761 | 63.2904 | 122.6944 | 0.05951 | -0.022888 | 122.8683 | 122.7859 | 0.15564 | 122.7585 | 62.9929 | 122.7402 | -59.9579 | -122.8134 | 62.8143 | 122.7676 | 62.883 | 63.4048
2180.8906 | 123.0652 | -62.8098 | 59.8984 | -0.083313 | 0.00069854 | -0.0087777 | 2.8918 | 0.0019653 | -0.0012048 | -0.0024717 | -0.033844 | 0.16245 | 0.12944 | -0.0029394 | 0.057319 | 0.10329 | -0.00036747 | 0.054932 | 0.050354 | -0.050354 | 0.059509 | 0.1831 | 0.064087 | 0.11902 | 0.70038 | 59.8251 | -62.8693 | 60.0037 | 60.0952 | 59.9213 | 0.45776 | 62.7594 | -59.848 | -59.8389 | 62.9929 | 62.9288 | 62.8738 | 0.16937 | 0.11444 | -0.05951 | -0.073242 | 0.10529 | 122.905 | 63.2675 | 122.731 | 63.327 | 122.7905 | 0.23346 | 0.10986 | 122.9645 | 122.8729 | 0.10071 | 122.6944 | 62.8601 | 122.6349 | -59.9487 | -122.7676 | 62.8693 | 122.8134 | 62.8647 | 63.5101
2181.8281 | 122.9874 | -62.8647 | 59.9167 | 0.00824 | 0.00048494 | -0.0098459 | 2.893 | 0.0011109 | -0.002273 | -0.00012167 | -0.1376 | 0.16352 | 0.12944 | -0.0052892 | 0.056678 | 0.10585 | -0.0035719 | 0.013733 | 0.091553 | -0.068665 | -0.032043 | 0.064087 | -0.027466 | 0.009155 | 0.56305 | 59.8526 | -62.8784 | 59.9304 | 59.9945 | 59.8206 | 0.37079 | 62.796 | -59.8251 | -59.9487 | 62.9288 | 62.8738 | 62.8372 | 0.07782 | 0.041199 | -0.013733 | -0.064087 | 0.013733 | 122.8592 | 63.2355 | 122.6852 | 63.2492 | 122.699 | 0.13275 | 0.036622 | 122.8729 | 122.8088 | 0.16022 | 122.731 | 62.9562 | 122.7173 | -59.9854 | -122.7951 | 62.8326 | 122.7951 | 62.8784 | 63.4277
2182.8906 | 123.0194 | -62.8647 | 59.8892 | -0.090943 | -0.0012241 | -0.0087777 | 2.8926 | -0.0042297 | -0.0012048 | -0.0011899 | -0.064362 | 0.16096 | 0.12858 | 0.0017602 | 0.056892 | 0.10393 | -0.00015387 | -0.073242 | 0 | -0.091553 | -0.10986 | 0.018311 | -0.032043 | -0.009155 | 0.48981 | 59.816 | -62.8922 | 59.9167 | 59.9991 | 59.8297 | 0.32501 | 62.7731 | -59.8892 | -59.9991 | 62.883 | 62.8555 | 62.8326 | 0.082398 | 0.05951 | -0.027466 | -0.073242 | 0.027466 | 122.8638 | 63.1897 | 122.6944 | 63.2172 | 122.7219 | 0.10986 | -0.01831 | 122.8912 | 122.8088 | 0.091553 | 122.7081 | 62.8647 | 122.6807 | -59.9808 | -122.7814 | 62.7548 | 122.7814 | 62.7914 | 63.3545
2183.8281 | 122.9782 | -62.8555 | 59.903 | 0.00061049 | 5.7742e-05 | -0.010914 | 2.8939 | -0.00017091 | -0.00013676 | -0.0016171 | -0.13455 | 0.16373 | 0.12666 | 0.0024012 | 0.056038 | 0.10479 | -0.00036747 | 0.018311 | 0.082397 | -0.054932 | -0.032043 | 0.068665 | -0.045776 | 0.022888 | 0.60425 | 59.8709 | -62.9013 | 59.9533 | 59.9991 | 59.8068 | 0.37994 | 62.8006 | -59.8206 | -59.935 | 62.9242 | 62.8784 | 62.8098 | 0.07782 | 0.009156 | -0.045776 | -0.032043 | 0.050354 | 122.8546 | 63.2355 | 122.6624 | 63.2812 | 122.7081 | 0.1236 | 0.022889 | 122.9004 | 122.8546 | 0.13733 | 122.7722 | 62.9379 | 122.7264 | -59.9579 | -122.8043 | 62.8235 | 122.8088 | 62.8738 | 63.4598
2184.8906 | 123.056 | -62.8372 | 59.8892 | -0.022278 | -0.00036966 | -0.0068551 | 2.8928 | 0.00068369 | 0.0026404 | 9.193e-05 | -0.027741 | 0.16544 | 0.12794 | -0.0074254 | 0.055183 | 0.10265 | -0.00036747 | 0.041199 | 0.082397 | -0.009155 | 0.013733 | 0.26093 | -0.13275 | -0.013733 | 0.6546 | 59.8389 | -62.8418 | 59.9716 | 60.0861 | 59.903 | 0.44403 | 62.8281 | -59.8068 | -59.8755 | 63.0981 | 62.8235 | 62.7045 | -0.004578 | -0.1236 | -0.004578 | -0.050354 | 0.082398 | 122.9233 | 63.2812 | 122.7402 | 63.2858 | 122.7448 | 0.27008 | 0.022888 | 122.9279 | 122.8134 | 0.091552 | 122.6807 | 62.9196 | 122.6761 | -59.8984 | -122.731 | 62.851 | 122.8088 | 62.8784 | 63.4918
2185.8281 | 122.9919 | -62.8738 | 59.9167 | 0.046386 | -0.00058326 | -0.0087777 | 2.8933 | 0.0043151 | -0.00013676 | -0.00033547 | -0.1315 | 0.16587 | 0.12751 | 0.0053918 | 0.05561 | 0.10607 | -0.0018629 | 0.032043 | 0.10071 | -0.059509 | -0.022888 | 0.064087 | -0.036621 | 0 | 0.59052 | 59.8618 | -62.8738 | 59.935 | 60.0128 | 59.816 | 0.38452 | 62.8143 | -59.816 | -59.9396 | 62.9379 | 62.8738 | 62.8372 | 0.059509 | 0.022888 | 0 | -0.054932 | 0.018311 | 122.8867 | 63.2584 | 122.6898 | 63.2584 | 122.6898 | 0.1236 | 0.036621 | 122.8867 | 122.8088 | 0.16022 | 122.7356 | 62.9745 | 122.7356 | -59.9762 | -122.7905 | 62.851 | 122.8088 | 62.9059 | 63.4644
2186.8906 | 122.9416 | -62.8601 | 59.9396 | 0.023498 | -0.0027195 | -0.0094187 | 2.8926 | 0.00068369 | -0.00099116 | -0.0022581 | -0.088776 | 0.1616 | 0.12751 | 5.1352e-05 | 0.05796 | 0.10372 | 0.0013415 | 0.027466 | 0.14648 | -0.036621 | -0.032043 | 0.064087 | -0.022888 | 0.032043 | 0.52643 | 59.8892 | -62.8876 | 59.8892 | 59.9533 | 59.7702 | 0.38452 | 62.8235 | -59.7931 | -59.9716 | 62.9242 | 62.8922 | 62.8372 | 0.068664 | 0.013733 | -0.027466 | -0.050354 | -0.050354 | 122.8134 | 63.2446 | 122.6303 | 63.2721 | 122.6578 | 0.10071 | 0.004578 | 122.8409 | 122.7768 | 0.18311 | 122.7768 | 63.0066 | 122.7493 | -59.9762 | -122.8271 | 62.8281 | 122.7493 | 62.8876 | 63.3865
2187.8281 | 123.0148 | -62.8647 | 59.9213 | -0.045166 | 5.7742e-05 | -0.0064279 | 2.8935 | -0.00059811 | -0.0044092 | -0.0033261 | -0.1315 | 0.16309 | 0.1258 | 0.0015466 | 0.055824 | 0.10372 | -0.0035719 | 0.013733 | 0.11902 | -0.054932 | -0.032043 | 0.068665 | -0.027466 | 0.032043 | 0.59052 | 59.8755 | -62.883 | 59.9304 | 59.9991 | 59.816 | 0.39825 | 62.8098 | -59.8022 | -59.9533 | 62.9334 | 62.8967 | 62.8372 | 0.086975 | 0.027466 | -0.018311 | -0.045777 | 0.009155 | 122.8638 | 63.2629 | 122.6807 | 63.2812 | 122.699 | 0.1236 | 0.022889 | 122.8821 | 122.8134 | 0.17395 | 122.7585 | 62.9837 | 122.7402 | -59.9762 | -122.8043 | 62.8326 | 122.7951 | 62.8784 | 63.4552
2188.8906 | 123.0377 | -62.8143 | 59.9167 | -0.029907 | -0.0012241 | -0.0087777 | 2.8918 | -0.0033753 | -0.0029138 | -0.0016171 | -0.046051 | 0.1616 | 0.12922 | -0.0052892 | 0.056038 | 0.10329 | -0.0022901 | 0.054932 | 0.073242 | -0.036621 | 0.027466 | 0.13733 | 0.073242 | 0.091553 | 0.64087 | 59.8801 | -62.8693 | 59.9442 | 60.0494 | 59.8709 | 0.43488 | 62.7777 | -59.8434 | -59.8892 | 62.9517 | 62.9059 | 62.8876 | 0.12817 | 0.10986 | -0.054932 | -0.036621 | 0.027466 | 122.8638 | 63.2492 | 122.6852 | 63.3041 | 122.7402 | 0.17395 | 0.064087 | 122.9187 | 122.8134 | 0.10986 | 122.7493 | 62.8876 | 122.6944 | -59.9533 | -122.7859 | 62.8418 | 122.7585 | 62.8693 | 63.4552
2189.8281 | 122.9782 | -62.8464 | 59.9167 | -0.090943 | 0.00091214 | -0.0089913 | 2.8935 | 0.0015381 | 0.00071784 | 0.00073273 | -0.1315 | 0.16523 | 0.13243 | -0.0033666 | 0.056038 | 0.10692 | -0.00058107 | 0.009155 | 0.073242 | -0.091553 | -0.041199 | 0.041199 | -0.068665 | -0.009155 | 0.43488 | 59.8434 | -62.8967 | 59.9258 | 59.9762 | 59.8114 | 0.36163 | 62.7548 | -59.8434 | -59.9579 | 62.8876 | 62.8372 | 62.7777 | 0.082398 | 0.022888 | -0.050354 | -0.073242 | 0.009155 | 122.8226 | 63.208 | 122.6578 | 63.2584 | 122.7081 | 0.13275 | 0.050354 | 122.8729 | 122.8226 | 0.16479 | 122.7402 | 62.9196 | 122.6898 | -60.0082 | -122.8134 | 62.8052 | 122.7722 | 62.8555 | 63.2812
2190.8281 | 122.9828 | -62.8601 | 59.9304 | 0.00824 | -0.0027195 | -0.0089913 | 2.8937 | 0.0019653 | -0.0018458 | -0.00097627 | -0.10098 | 0.16373 | 0.12837 | -0.0052892 | 0.055824 | 0.10436 | -0.00058107 | -0.027466 | 0.16022 | -0.036621 | -0.064087 | 0.045776 | -0.050354 | 0.004578 | 0.53101 | 59.8846 | -62.8967 | 59.8892 | 59.967 | 59.7931 | 0.39825 | 62.8235 | -59.7702 | -59.9945 | 62.9059 | 62.8647 | 62.8098 | 0.041199 | -0.013733 | -0.036622 | -0.045776 | -0.041199 | 122.8271 | 63.2584 | 122.6532 | 63.295 | 122.6898 | 0.082397 | -0.027466 | 122.8638 | 122.7859 | 0.19684 | 122.7814 | 63.0203 | 122.7448 | -59.967 | -122.8271 | 62.796 | 122.7493 | 62.8326 | 63.3911
2191.8906 | 123.0194 | -62.851 | 59.8984 | -0.022278 | 0.00027134 | -0.0079233 | 2.8898 | 0.00046989 | -0.0020594 | -0.0024717 | -0.036896 | 0.16032 | 0.12645 | 5.1352e-05 | 0.054969 | 0.10372 | 0.00070073 | 0.004578 | 0.091553 | -0.036621 | 0.036621 | 0.17395 | 0.068665 | 0.091553 | 0.63629 | 59.8389 | -62.8647 | 59.9625 | 60.0677 | 59.903 | 0.46234 | 62.8143 | -59.8068 | -59.8618 | 63.0249 | 62.9425 | 62.9196 | 0.12817 | 0.10529 | -0.013733 | -0.059509 | 0.064087 | 122.9187 | 63.3133 | 122.7539 | 63.327 | 122.7676 | 0.21057 | 0.073242 | 122.9324 | 122.8271 | 0.12817 | 122.7036 | 62.9425 | 122.6898 | -59.935 | -122.7631 | 62.8876 | 122.8134 | 62.8555 | 63.4872
2192.8281 | 122.9462 | -62.8922 | 59.9213 | -0.068054 | -0.0016513 | -0.0087777 | 2.8943 | 4.2692e-05 | -0.0016322 | -0.0022581 | -0.14981 | 0.16309 | 0.12815 | -0.0069982 | 0.058174 | 0.10906 | -0.0027173 | -0.11902 | 0.032043 | -0.14191 | -0.16479 | -0.091553 | -0.19684 | -0.11902 | 0.38452 | 59.8526 | -62.883 | 59.6695 | 60.2417 | 59.761 | 0.21515 | 62.7502 | -59.8892 | -60.0861 | 62.8006 | 62.7731 | 62.6953 | 0.022888 | -0.054931 | 0.009155 | -0.068665 | -0.25177 | 123.1338 | 63.1073 | 122.6532 | 63.0981 | 122.644 | 0.050354 | -0.022888 | 123.1247 | 122.5525 | 0.17395 | 122.7356 | 62.9242 | 122.7448 | -60.0632 | -122.8043 | 62.7274 | 122.5616 | 62.7731 | 63.2767
2193.8906 | 123.0652 | -62.8281 | 59.903 | -0.022278 | -0.0010105 | -0.0070687 | 2.8918 | 0.0030335 | -0.0024866 | -0.00033547 | -0.058258 | 0.16138 | 0.12815 | -0.0076392 | 0.056038 | 0.10436 | -0.0014355 | -0.022888 | 0.086975 | -0.009155 | 0 | -0.036621 | 0.054932 | 0.10986 | 0.67749 | 59.8389 | -62.8693 | 59.9762 | 60.0769 | 59.8984 | 0.44861 | 62.8189 | -59.816 | -59.903 | 62.7914 | 62.9379 | 62.883 | 0.11902 | 0.064087 | -0.041199 | -0.064087 | 0.073242 | 122.905 | 63.2767 | 122.7264 | 63.3179 | 122.7676 | -0.027466 | 0.009155 | 122.9462 | 122.8455 | 0.09613 | 122.7081 | 62.915 | 122.6669 | -59.9121 | -122.7722 | 62.8281 | 122.8043 | 62.8052 | 63.5056
2194.8281 | 122.9645 | -62.8738 | 59.935 | 0.00061049 | -0.0040013 | -0.0089913 | 2.8926 | 0.00089729 | -0.0024866 | -0.0050351 | -0.10098 | 0.16117 | 0.12944 | -0.0033666 | 0.056038 | 0.10457 | 0.0013415 | 0.009155 | 0.15564 | -0.027466 | -0.11444 | 0.37994 | 0.43945 | -0.086975 | 0.48981 | 59.8846 | -62.9242 | 59.8892 | 59.9487 | 59.7977 | 0.40283 | 62.8464 | -59.7794 | -60.0494 | 63.2538 | 62.7869 | 63.3133 | -0.059509 | 0.46692 | -0.050354 | -0.050354 | -0.045777 | 122.8226 | 63.2767 | 122.6715 | 63.327 | 122.7219 | 0.40741 | -0.086975 | 122.8729 | 122.8134 | 0.18311 | 122.8088 | 63.0295 | 122.7585 | -59.9625 | -122.8592 | 62.7594 | 122.7631 | 62.883 | 63.3636
2195.8906 | 123.0652 | -62.8281 | 59.903 | -0.037537 | 5.7742e-05 | -0.0081369 | 2.8937 | -0.0016663 | -0.00056396 | -0.0026853 | -0.18948 | 0.16288 | 0.12687 | -0.00080325 | 0.056678 | 0.10329 | -0.0018629 | 0.050354 | 0.07782 | -0.032043 | 0.059509 | 0.17395 | 0.65918 | 0.43488 | 0.75989 | 59.8343 | -62.8922 | 59.9762 | 60.1089 | 59.9167 | 0.46692 | 62.796 | -59.8251 | -59.8434 | 63.002 | 63.2629 | 63.4872 | 0.46692 | 0.69122 | -0.064087 | -0.068664 | 0.073242 | 122.937 | 63.295 | 122.7448 | 63.3591 | 122.8088 | 0.20599 | 0.091552 | 123.0011 | 122.8683 | 0.10986 | 122.7264 | 62.9059 | 122.6624 | -59.935 | -122.7951 | 62.8876 | 122.8043 | 62.8784 | 63.588
2196.8281 | 122.9782 | -62.8784 | 59.9533 | 0.00824 | -0.00015586 | -0.0092051 | 2.8939 | -0.00081171 | -0.002273 | -0.0050351 | -0.10098 | 0.16437 | 0.12687 | -0.0046484 | 0.05326 | 0.10479 | -0.0014355 | 0.022888 | 0.1236 | -0.073242 | -0.022888 | 0.045776 | -0.018311 | 0.036621 | 0.52643 | 59.8846 | -62.8922 | 59.9167 | 59.9808 | 59.8022 | 0.39368 | 62.8052 | -59.8297 | -59.9762 | 62.9242 | 62.915 | 62.8601 | 0.10986 | 0.054931 | -0.013733 | -0.068664 | -0.036621 | 122.8592 | 63.2721 | 122.6807 | 63.2858 | 122.6944 | 0.11902 | 0.050354 | 122.8729 | 122.8088 | 0.19684 | 122.7768 | 63.002 | 122.7631 | -60.0266 | -122.8455 | 62.8555 | 122.7951 | 62.9013 | 63.4048
2197.8906 | 123.0148 | -62.8418 | 59.9121 | -0.052796 | -0.00079686 | -0.0079233 | 2.8945 | 0.00089729 | -0.0018458 | -0.0016171 | -0.058258 | 0.16459 | 0.12965 | -0.0052892 | 0.056251 | 0.10286 | -0.0027173 | 0.068665 | 0.054932 | -0.041199 | 0.041199 | 0.17395 | 0.041199 | 0.091553 | 0.63171 | 59.8572 | -62.883 | 59.9396 | 60.0357 | 59.8892 | 0.44861 | 62.8006 | -59.8572 | -59.8709 | 63.0157 | 62.9333 | 62.883 | 0.13275 | 0.082398 | -0.041199 | -0.054931 | 0.027466 | 122.8775 | 63.2904 | 122.731 | 63.3316 | 122.7722 | 0.21515 | 0.082398 | 122.9187 | 122.8226 | 0.096131 | 122.7402 | 62.8967 | 122.699 | -59.9533 | -122.7951 | 62.883 | 122.7814 | 62.9105 | 63.4735
2198.8281 | 122.9782 | -62.8693 | 59.9487 | -0.052796 | -0.0016513 | -0.0066415 | 2.8922 | 0.0013245 | -0.002273 | -0.00097627 | -0.11319 | 0.16416 | 0.12858 | -0.0027258 | 0.055397 | 0.10372 | 0.00027333 | -0.013733 | 0.16022 | -0.022888 | -0.032043 | 0.027466 | -0.027466 | 0.027466 | 0.54474 | 59.8892 | -62.9013 | 59.8663 | 59.9945 | 59.7885 | 0.39825 | 62.8464 | -59.7885 | -59.9808 | 62.8967 | 62.8967 | 62.8418 | 0.050354 | -0.004578 | -0.032043 | -0.059509 | -0.082397 | 122.8638 | 63.2675 | 122.6578 | 63.2996 | 122.6898 | 0.050354 | -0.009155 | 122.8958 | 122.7676 | 0.1831 | 122.7905 | 63.0295 | 122.7585 | -59.9716 | -122.85 | 62.8372 | 122.7356 | 62.8555 | 63.414
2199.8906 | 122.9599 | -62.8647 | 59.9487 | 0.015869 | -0.00058326 | -0.010273 | 2.8933 | 0.00046989 | -0.00099116 | -0.00054907 | -0.070465 | 0.16352 | 0.1288 | -0.0055028 | 0.056251 | 0.10457 | -0.0018629 | 0.041199 | 0.10071 | -0.027466 | -0.013733 | 0.10071 | 0.009155 | 0.045776 | 0.57678 | 59.8892 | -62.8784 | 59.8938 | 59.9762 | 59.8068 | 0.39825 | 62.8372 | -59.848 | -59.9625 | 62.9654 | 62.9105 | 62.8738 | 0.073242 | 0.036621 | -0.013733 | -0.059509 | -0.054931 | 122.8409 | 63.2629 | 122.6715 | 63.2767 | 122.6852 | 0.12817 | 0.013733 | 122.8546 | 122.7722 | 0.12817 | 122.7676 | 62.9654 | 122.7539 | -59.9762 | -122.8271 | 62.851 | 122.7585 | 62.9059 | 63.4415
2200.8281 | 122.9691 | -62.8555 | 59.903 | -0.014649 | -0.00079686 | -0.0083505 | 2.893 | 0.0036743 | 0.00029044 | -0.0020443 | -0.14676 | 0.1648 | 0.12645 | -0.0016576 | 0.05561 | 0.10329 | -0.0037855 | 0.009155 | 0.082397 | -0.07782 | -0.032043 | 0.07782 | -0.027466 | -0.018311 | 0.58136 | 59.8755 | -62.8784 | 59.9396 | 59.9762 | 59.7382 | 0.20599 | 62.7777 | -59.8206 | -59.935 | 62.9334 | 62.8372 | 62.8281 | 0.059509 | 0.050354 | -0.022888 | -0.027466 | 0.036621 | 122.8317 | 63.0615 | 122.5937 | 63.0844 | 122.6166 | 0.15564 | 0.045777 | 122.8546 | 122.818 | 0.16022 | 122.7539 | 62.9379 | 122.731 | -59.9808 | -122.7814 | 62.8235 | 122.7951 | 62.8647 | 63.4369
2201.8906 | 123.0423 | -62.8693 | 59.8892 | -0.052796 | -0.0037875 | -0.0087777 | 2.8898 | -0.00017091 | 0.0024268 | 0.0011599 | -0.033844 | 0.16587 | 0.12794 | -0.0091344 | 0.056678 | 0.10436 | -0.0020765 | -0.036621 | 0.041199 | -0.086975 | -0.050354 | -0.11902 | -0.073242 | -0.013733 | 0.50354 | 59.8389 | -62.9288 | 59.9442 | 60.0128 | 59.8618 | 0.37079 | 62.7823 | -59.848 | -59.9396 | 62.7502 | 62.8555 | 62.796 | 0.073242 | 0.013733 | -0.059509 | -0.050354 | 0.054932 | 122.8821 | 63.2401 | 122.731 | 63.2996 | 122.7905 | -0.032044 | 0.036621 | 122.9416 | 122.8729 | 0.12817 | 122.7676 | 62.9105 | 122.7081 | -59.9762 | -122.818 | 62.8189 | 122.8134 | 62.8326 | 63.3728
2202.8281 | 122.9874 | -62.8555 | 59.9075 | -0.022278 | -0.00058326 | -0.0066415 | 2.8933 | 0.00046989 | -0.0035548 | -0.00033547 | -0.15286 | 0.16437 | 0.12837 | -0.0027258 | 0.055397 | 0.10436 | -0.00036747 | 0.027466 | 0.091553 | -0.064087 | -0.032043 | 0.054932 | -0.036621 | 0.013733 | 0.58594 | 59.8846 | -62.8967 | 59.9304 | 59.9945 | 59.7931 | 0.37994 | 62.7914 | -59.816 | -59.9396 | 62.9105 | 62.8693 | 62.8189 | 0.07782 | 0.027466 | -0.041199 | -0.022888 | 0.022888 | 122.85 | 63.2355 | 122.6486 | 63.2767 | 122.6898 | 0.11902 | 0.032044 | 122.8912 | 122.8271 | 0.15564 | 122.7814 | 62.9471 | 122.7402 | -59.9716 | -122.8043 | 62.8235 | 122.7859 | 62.883 | 63.4415
2203.8906 | 122.9965 | -62.8693 | 59.9213 | -0.060425 | 0.00027134 | -0.0089913 | 2.8935 | 0.00089729 | -0.0014184 | -0.0037533 | -0.058258 | 0.16288 | 0.12559 | -0.00080325 | 0.055397 | 0.10393 | -0.0039991 | 0.059509 | 0.068665 | -0.018311 | 0.036621 | 0.14191 | 0.050354 | 0.10529 | 0.61798 | 59.8755 | -62.8922 | 59.9213 | 60.0082 | 59.8526 | 0.43488 | 62.851 | -59.8526 | -59.8846 | 63.0112 | 62.9745 | 62.9196 | 0.1236 | 0.068665 | -0.022888 | -0.045777 | 0 | 122.8775 | 63.3041 | 122.7219 | 63.327 | 122.7448 | 0.16022 | 0.054932 | 122.9004 | 122.8134 | 0.086976 | 122.7676 | 62.9379 | 122.7448 | -59.9396 | -122.8134 | 62.9059 | 122.7905 | 62.9288 | 63.4872
2204.8281 | 122.9919 | -62.851 | 59.9121 | -0.045166 | 5.7742e-05 | -0.0077097 | 2.8922 | 0.0030335 | -0.0012048 | -0.00012167 | -0.15591 | 0.16117 | 0.12773 | -0.0042212 | 0.056038 | 0.10393 | -0.0039991 | 0.041199 | 0.1236 | -0.045776 | -0.027466 | 0.09613 | 0.013733 | 0.027466 | 0.59052 | 59.8801 | -62.8922 | 59.9213 | 60.0082 | 59.816 | 0.42114 | 62.8052 | -59.7885 | -59.9396 | 62.9471 | 62.8784 | 62.8647 | 0.073242 | 0.059509 | -0.041199 | -0.032043 | 0.009156 | 122.8592 | 63.2721 | 122.6669 | 63.3133 | 122.7081 | 0.14191 | 0.01831 | 122.9004 | 122.8134 | 0.16937 | 122.7722 | 62.9745 | 122.731 | -59.9579 | -122.8043 | 62.8235 | 122.7722 | 62.8922 | 63.4415
2205.8906 | 123.0194 | -62.8418 | 59.935 | 0.031128 | -0.0022923 | -0.0092051 | 2.8909 | -0.0016663 | -0.0012048 | 0.00030553 | -0.058258 | 0.16288 | 0.12495 | -0.0072118 | 0.055397 | 0.10201 | -0.0048535 | 0.07782 | 0.068665 | -0.045776 | 0.050354 | 0.15564 | 0.073242 | 0.10529 | 0.66376 | 59.8434 | -62.8647 | 59.935 | 60.0769 | 59.8846 | 0.45776 | 62.796 | -59.8663 | -59.8846 | 62.9974 | 62.9471 | 62.915 | 0.15106 | 0.11902 | -0.022888 | -0.091553 | 0 | 122.9187 | 63.2996 | 122.7264 | 63.3224 | 122.7493 | 0.20142 | 0.09613 | 122.9416 | 122.7997 | 0.11444 | 122.7081 | 62.9105 | 122.6852 | -59.9808 | -122.7997 | 62.8922 | 122.7768 | 62.9196 | 63.5056
2206.8281 | 122.9919 | -62.8555 | 59.9258 | -0.014649 | -0.0022923 | -0.0096323 | 2.8926 | 0.0017517 | -0.0024866 | -0.0031125 | -0.14981 | 0.16309 | 0.12858 | 0.0043238 | 0.05561 | 0.1035 | -0.0014355 | 0.027466 | 0.14191 | -0.022888 | -0.018311 | 0.045776 | -0.022888 | 0.018311 | 0.59052 | 59.8801 | -62.883 | 59.935 | 60.0174 | 59.8251 | 0.40283 | 62.8326 | -59.7839 | -59.9442 | 62.9013 | 62.8738 | 62.8326 | 0.041199 | 0 | -0.027466 | -0.045776 | 0.009156 | 122.8729 | 63.2584 | 122.6807 | 63.2858 | 122.7081 | 0.068664 | 0.004577 | 122.9004 | 122.818 | 0.16479 | 122.7631 | 62.9974 | 122.7356 | -59.9487 | -122.8088 | 62.8372 | 122.7905 | 62.883 | 63.446
2207.8281 | 122.9874 | -62.8922 | 59.9075 | -0.052796 | -0.0010105 | -0.0070687 | 2.8941 | 0.0019653 | -0.0016322 | -0.0016171 | -0.13455 | 0.1616 | 0.1273 | -0.0016576 | 0.056251 | 0.10457 | 0.00048713 | 0.004578 | 0.059509 | -0.10071 | -0.045776 | 0.022888 | -0.059509 | -0.027466 | 0.53558 | 59.8755 | -62.915 | 59.9213 | 59.9579 | 59.7748 | 0.33875 | 62.7914 | -59.848 | -59.9533 | 62.915 | 62.8647 | 62.8326 | 0.073242 | 0.041199 | -0.022888 | -0.032044 | 0.013733 | 122.85 | 63.2309 | 122.6669 | 63.2538 | 122.6898 | 0.1236 | 0.054932 | 122.8729 | 122.8363 | 0.16022 | 122.7905 | 62.9517 | 122.7676 | -60.0082 | -122.8226 | 62.8464 | 122.8134 | 62.8967 | 63.4277
2208.8281 | 122.9736 | -62.8464 | 59.9167 | 0.015869 | -0.0016513 | -0.0074961 | 2.8943 | -0.00059811 | -0.0016322 | -0.0028989 | -0.1254 | 0.16587 | 0.12837 | -0.0080664 | 0.054756 | 0.10671 | -0.0018629 | 0.036621 | 0.10071 | -0.064087 | -0.036621 | 0.073242 | -0.032043 | 0.004578 | 0.59509 | 59.8526 | -62.8967 | 59.9121 | 59.9991 | 59.8251 | 0.39368 | 62.7823 | -59.816 | -59.9533 | 62.9196 | 62.851 | 62.8143 | 0.068665 | 0.032044 | -0.050354 | -0.064087 | -0.004578 | 122.8455 | 63.2401 | 122.6715 | 63.2904 | 122.7219 | 0.13733 | 0.027466 | 122.8958 | 122.8088 | 0.1648 | 122.7493 | 62.9471 | 122.699 | -59.9808 | -122.8134 | 62.8098 | 122.7585 | 62.883 | 63.4415
2209.8281 | 122.9462 | -62.8876 | 59.9167 | 0.023498 | -0.0018649 | -0.0070687 | 2.8933 | 0.0019653 | 0.00071784 | 9.193e-05 | -0.1315 | 0.1663 | 0.13115 | -0.0029394 | 0.056251 | 0.10671 | -0.00036747 | -0.041199 | 0.07782 | -0.091553 | -0.10071 | -0.013733 | -0.13275 | -0.073242 | 0.43945 | 59.8618 | -62.9059 | 59.8572 | 59.9258 | 59.7382 | 0.29297 | 62.796 | -59.8389 | -60.0174 | 62.8738 | 62.8143 | 62.7548 | 0.018311 | -0.041198 | -0.018311 | -0.054932 | -0.059509 | 122.8134 | 63.1805 | 122.6257 | 63.1989 | 122.644 | 0.07782 | -0.009155 | 122.8317 | 122.7631 | 0.16937 | 122.7676 | 62.9654 | 122.7493 | -60.0082 | -122.8226 | 62.7869 | 122.7448 | 62.8464 | 63.327
2210.9062 | 123.0194 | -62.8601 | 59.8709 | -0.068054 | 5.7742e-05 | -0.0074961 | 2.8926 | 0.0011109 | -0.00099116 | 0.00073273 | -0.036896 | 0.16331 | 0.12986 | -0.0029394 | 0.054756 | 0.10436 | -0.0050671 | -0.073242 | -0.032043 | -0.10071 | -0.068665 | 0.068665 | -0.086975 | -0.018311 | 0.44861 | 59.7931 | -62.8876 | 59.9487 | 60.0311 | 59.8526 | 0.3479 | 62.7594 | -59.903 | -59.9396 | 62.9288 | 62.8418 | 62.7731 | 0.082397 | 0.013733 | -0.027466 | -0.07782 | 0.077819 | 122.8912 | 63.208 | 122.7127 | 63.2355 | 122.7402 | 0.16937 | 0.032043 | 122.9187 | 122.8363 | 0.068665 | 122.6807 | 62.8281 | 122.6532 | -59.9716 | -122.7585 | 62.7914 | 122.8088 | 62.7869 | 63.3087
2211.8281 | 122.9828 | -62.8738 | 59.9258 | -0.075684 | -0.00058326 | -0.0081369 | 2.8941 | 0.0011109 | -0.0016322 | -0.00054907 | -0.12234 | 0.16288 | 0.1288 | -0.0040076 | 0.056678 | 0.1097 | -0.00015387 | -0.004578 | 0.09613 | -0.064087 | -0.032043 | 0.064087 | -0.041199 | 0.009155 | 0.5722 | 59.8801 | -62.8876 | 59.8206 | 59.9945 | 59.8618 | 0.36621 | 62.8098 | -59.8297 | -59.9579 | 62.9379 | 62.883 | 62.8326 | 0.073242 | 0.022888 | -0.013733 | -0.045776 | -0.10529 | 122.8683 | 63.2401 | 122.7356 | 63.2538 | 122.7493 | 0.12817 | 0.032044 | 122.8821 | 122.7081 | 0.16022 | 122.7676 | 62.97 | 122.7539 | -59.9899 | -122.8134 | 62.8418 | 122.6944 | 62.8693 | 63.446
2212.8906 | 123.0148 | -62.8555 | 59.8572 | -0.052796 | -0.0025059 | -0.0083505 | 2.8918 | -0.0040161 | -0.0018458 | -0.00097627 | -0.027741 | 0.16267 | 0.12922 | -0.0063574 | 0.057533 | 0.10286 | -0.0031445 | -0.036621 | 0.041199 | -0.10071 | 0.054932 | 0.3067 | -0.16022 | -0.068665 | 0.52185 | 59.8389 | -62.8876 | 59.9258 | 60.0174 | 59.8434 | 0.35706 | 62.7548 | -59.816 | -59.8022 | 63.1622 | 62.7869 | 62.6953 | 0.032043 | -0.059509 | -0.032043 | -0.018311 | 0.068664 | 122.8729 | 63.2126 | 122.699 | 63.2446 | 122.731 | 0.40741 | 0.15564 | 122.905 | 122.8134 | 0.14191 | 122.7264 | 62.8967 | 122.6944 | -59.9579 | -122.7448 | 62.9105 | 122.7814 | 62.8189 | 63.3774
2213.8281 | 122.9462 | -62.883 | 59.9121 | -0.014649 | -0.0018649 | -0.0089913 | 2.8939 | 0.0017517 | -0.0016322 | -0.0024717 | -0.13455 | 0.1616 | 0.12837 | -0.0012304 | 0.054969 | 0.10372 | -0.00036747 | -0.059509 | 0.045776 | -0.1236 | -0.11444 | -0.013733 | -0.12817 | -0.07782 | 0.43945 | 59.8755 | -62.883 | 59.8709 | 59.8938 | 59.7565 | 0.30212 | 62.7594 | -59.8663 | -60.0266 | 62.8693 | 62.8052 | 62.7548 | 0.045776 | -0.004578 | 0 | -0.036621 | -0.041198 | 122.7768 | 63.1851 | 122.6395 | 63.1851 | 122.6395 | 0.10986 | 0.009155 | 122.7768 | 122.7539 | 0.16937 | 122.7585 | 62.9288 | 122.7585 | -60.0357 | -122.7951 | 62.7686 | 122.7539 | 62.8235 | 63.3224
2214.8906 | 123.0927 | -62.8418 | 59.8984 | 0.00061049 | -0.0020785 | -0.0092051 | 2.8915 | 0.0028199 | 0.00071784 | -0.0031125 | -0.018585 | 0.16202 | 0.12687 | -0.0063574 | 0.057533 | 0.10308 | 0.0011279 | 0.041199 | 0.07782 | -0.045776 | 0.045776 | 0.1831 | 0.073242 | 0.11444 | 0.62714 | 59.816 | -62.8372 | 60.0266 | 60.054 | 59.8572 | 0.43945 | 62.796 | -59.8206 | -59.8526 | 63.0249 | 62.9562 | 62.915 | 0.16022 | 0.11902 | 0.004578 | -0.082397 | 0.12817 | 122.8958 | 63.2812 | 122.699 | 63.2767 | 122.6944 | 0.22888 | 0.091552 | 122.8912 | 122.8638 | 0.1236 | 122.6532 | 62.9196 | 122.6578 | -59.9442 | -122.7356 | 62.8876 | 122.8683 | 62.883 | 63.4689
2215.8438 | 123.0927 | -62.8464 | 59.8572 | -0.052796 | -0.00079686 | -0.0072825 | 2.893 | 0.0021789 | -0.0018458 | -0.0016171 | -0.076569 | 0.16459 | 0.12773 | -0.0035802 | 0.05561 | 0.1035 | -0.0025037 | -0.068665 | -0.004578 | -0.15106 | -0.073242 | 0.059509 | -0.091553 | -0.054932 | 0.52185 | 59.8022 | -62.9105 | 59.9716 | 60.0128 | 59.8572 | 0.33417 | 62.6953 | -59.8618 | -59.9304 | 62.9059 | 62.7914 | 62.7548 | 0.09613 | 0.059509 | -0.064086 | -0.054932 | 0.11444 | 122.8592 | 63.1805 | 122.7036 | 63.2446 | 122.7676 | 0.21057 | 0.07782 | 122.9233 | 122.8821 | 0.14648 | 122.7127 | 62.8418 | 122.6486 | -60.0082 | -122.7676 | 62.7731 | 122.818 | 62.7777 | 63.3682
2216.8906 | 123.0515 | -62.796 | 59.8846 | 0.00061049 | 0.0013393 | -0.016254 | 2.8933 | 0.0011109 | -0.0029138 | -0.0016171 | -0.039948 | 0.16267 | 0.1305 | -0.0055028 | 0.05561 | 0.10286 | -0.0014355 | 0.43488 | 0.10071 | 0.009155 | -0.09613 | 0.13733 | 0.050354 | 0.045776 | 0.66376 | 59.8434 | -62.8738 | 59.967 | 60.0769 | 59.8984 | 0.46692 | 62.8052 | -59.7839 | -59.9808 | 62.9334 | 62.8418 | 62.8464 | 0.036621 | 0.041199 | -0.077819 | -0.041199 | 0.082397 | 122.8729 | 63.2629 | 122.6944 | 63.3408 | 122.7722 | 0.12817 | -0.10528 | 122.9507 | 122.8409 | 0.091553 | 122.7173 | 62.8967 | 122.6395 | -59.8755 | -122.7585 | 62.6999 | 122.7631 | 63.2309 | 63.4598
2217.8281 | 122.9828 | -62.8693 | 59.9167 | -0.022278 | -0.00015586 | -0.0079233 | 2.8918 | 0.0036743 | -0.0052638 | 9.193e-05 | -0.13455 | 0.16352 | 0.12709 | 0.0015466 | 0.052833 | 0.1065 | -0.0020765 | -0.009155 | 0.059509 | -0.09613 | 0.050354 | 0.054932 | -0.041199 | -0.004578 | 0.54932 | 59.8801 | -62.9013 | 59.9121 | 59.9762 | 59.7702 | 0.36163 | 62.7731 | -59.8572 | -59.8663 | 62.9242 | 62.8647 | 62.8281 | 0.091552 | 0.054931 | -0.032043 | -0.036621 | -0.004578 | 122.8455 | 63.2309 | 122.6395 | 63.2629 | 122.6715 | 0.15106 | 0.14648 | 122.8775 | 122.8134 | 0.15564 | 122.7814 | 62.9288 | 122.7493 | -60.0128 | -122.818 | 62.9196 | 122.7814 | 62.8601 | 63.4186
2218.8906 | 123.0789 | -62.8326 | 59.8755 | -0.060425 | -0.00058326 | -0.0096323 | 2.89 | -0.00081171 | 7.6842e-05 | -0.0020443 | -0.018585 | 0.16245 | 0.12645 | -0.0044348 | 0.054115 | 0.10479 | -0.00036747 | 0.022888 | 0.064087 | -0.041199 | 0.032043 | 0.12817 | 0.032043 | 0.091553 | 0.65002 | 59.8297 | -62.8693 | 60.0037 | 60.1044 | 59.9213 | 0.46234 | 62.7914 | -59.8114 | -59.8434 | 62.9608 | 62.9242 | 62.8647 | 0.13275 | 0.073242 | -0.036621 | -0.045776 | 0.12817 | 122.937 | 63.295 | 122.7539 | 63.3316 | 122.7905 | 0.16937 | 0.073242 | 122.9736 | 122.8729 | 0.10529 | 122.699 | 62.8967 | 122.6624 | -59.9167 | -122.7448 | 62.8647 | 122.8363 | 62.8555 | 63.4827
2219.8281 | 122.9828 | -62.8693 | 59.9075 | -0.052796 | -0.00058326 | -0.0094187 | 2.893 | 0.0019653 | -0.0037684 | -0.0016171 | -0.14981 | 0.16309 | 0.12794 | -0.002085 | 0.054969 | 0.10436 | -0.0018629 | 0.004578 | 0.059509 | -0.082397 | -0.018311 | 0.054932 | -0.036621 | -0.013733 | 0.050354 | 59.8572 | -62.9013 | 59.9121 | 59.8846 | 59.903 | 0.39368 | 62.7869 | -59.848 | -59.9258 | 62.9242 | 62.8555 | 62.8326 | 0.068664 | 0.045776 | -0.032043 | -0.050354 | 0.004577 | 122.7539 | 63.2629 | 122.7722 | 63.295 | 122.8043 | 0.13733 | 0.064086 | 122.7859 | 122.8134 | 0.14191 | 122.7585 | 62.9288 | 122.7264 | -59.9899 | -122.8088 | 62.851 | 122.7814 | 62.8738 | 62.9196
2220.8438 | 123.0606 | -62.8555 | 59.8938 | -0.068054 | -0.0016513 | -0.0089913 | 2.8905 | -0.0029479 | -0.002273 | -0.0028989 | -0.036896 | 0.16224 | 0.12751 | -0.0093482 | 0.057106 | 0.10329 | 0.00048713 | -0.018311 | 0.050354 | -0.073242 | -0.082397 | 0.24719 | 0.027466 | -0.059509 | 0.33417 | 59.8114 | -62.8647 | 59.935 | 60.0128 | 59.8618 | 0.35706 | 62.7823 | -59.8434 | -59.9762 | 63.1027 | 62.796 | 62.883 | 0.013733 | 0.10071 | -0.009155 | -0.082398 | 0.041199 | 122.8683 | 63.2126 | 122.7173 | 63.2217 | 122.7264 | 0.32043 | -0.009155 | 122.8775 | 122.7997 | 0.1236 | 122.6761 | 62.9059 | 122.6669 | -59.967 | -122.7585 | 62.7731 | 122.7905 | 62.8372 | 63.1897
2221.8281 | 122.9782 | -62.3749 | 60.4156 | -0.022278 | -0.00079686 | -0.0098459 | 2.8945 | -0.0010253 | -0.0027002 | -0.0031125 | -0.14371 | 0.16288 | 0.12837 | -0.00058965 | 0.054542 | 0.10585 | 0.0032641 | 0.032043 | 0.10071 | -0.064087 | -0.022888 | 0.036621 | -0.045776 | -0.004578 | -58.1451 | 60.379 | -62.3886 | 60.434 | 60.5072 | 60.3012 | 0.39825 | 62.3108 | -60.3149 | -60.4385 | 62.4115 | 62.3703 | 62.3291 | 0.059509 | 0.018311 | -0.013733 | -0.036621 | 0.018311 | 122.8821 | 62.7731 | 122.6761 | 62.7869 | 122.6898 | 0.10071 | 0.041199 | 122.8958 | 122.8226 | 0.1648 | 122.7676 | 62.4756 | 122.7539 | -60.4797 | -122.8043 | 62.352 | 122.8088 | 62.4069 | 4.2297
2222.8906 | 122.9507 | -62.3886 | 60.434 | -0.007019 | -0.0033603 | -0.010487 | 2.8924 | 0.0036743 | -0.0018458 | -0.0063169 | -0.12234 | 0.16437 | 0.12452 | -0.0027258 | 0.057319 | 0.10479 | 0.00070073 | 0.013733 | 0.16022 | -0.032043 | -0.018311 | 0.045776 | -0.16937 | -0.013733 | -58.1268 | 60.379 | -62.3978 | 60.3836 | 60.466 | 60.2783 | 0.39825 | 62.3566 | -60.2737 | -60.4523 | 62.4344 | 62.3749 | 62.2192 | 0.01831 | -0.13733 | -0.009155 | -0.054932 | -0.050354 | 122.8546 | 62.7869 | 122.6669 | 62.796 | 122.6761 | 0.077819 | 0.013732 | 122.8638 | 122.7814 | 0.19226 | 122.7768 | 62.5488 | 122.7676 | -60.466 | -122.8317 | 62.3703 | 122.7722 | 62.4023 | 4.2618
2223.8281 | 122.937 | -62.3566 | 60.4294 | -0.029907 | -0.00036966 | -0.0083505 | 2.8943 | 0.0019653 | 7.6842e-05 | 0.00073273 | -0.16202 | 0.16352 | 0.12794 | -0.0044348 | 0.055824 | 0.10479 | -0.0018629 | -0.050354 | 0.054932 | -0.10071 | -0.10986 | -0.004578 | -0.1236 | -0.064087 | -58.5342 | 60.379 | -62.4069 | 60.3836 | 60.4385 | 60.2463 | 0.29755 | 62.2559 | -60.3744 | -60.5392 | 62.352 | 62.2925 | 62.233 | 0.036621 | -0.022888 | -0.050354 | -0.050354 | -0.045776 | 122.7951 | 62.6541 | 122.6028 | 62.7045 | 122.6532 | 0.09613 | -0.009155 | 122.8455 | 122.7905 | 0.15564 | 122.7859 | 62.4115 | 122.7356 | -60.5301 | -122.8363 | 62.2467 | 122.7402 | 62.3062 | 3.8223
2224.8906 | 123.0515 | -62.3291 | 60.4019 | -0.029907 | -0.00036966 | -0.0096323 | 2.8911 | -0.00038451 | 7.6842e-05 | -0.0031125 | 0.17062 | 0.16416 | 0.13072 | -0.0097754 | 0.055824 | 0.10308 | -0.0027173 | 0.050354 | 0.082397 | -0.027466 | 0.068665 | 0.17853 | 0.059509 | 0.10986 | -58.7997 | 60.3516 | -62.3428 | 60.5026 | 60.553 | 60.4248 | 0.49439 | 62.3016 | -60.3195 | -60.3333 | 62.5076 | 62.439 | 62.3886 | 0.13733 | 0.086975 | -0.013732 | -0.050355 | 0.10071 | 122.8821 | 62.8235 | 122.7539 | 62.8372 | 122.7676 | 0.20599 | 0.096131 | 122.8958 | 122.8455 | 0.10986 | 122.6944 | 62.4115 | 122.6807 | -60.4294 | -122.7448 | 62.3978 | 122.8317 | 62.3795 | 3.5294
2225.8438 | 123.0194 | -62.3566 | 60.4111 | -0.045166 | -0.0012241 | -0.0087777 | 2.8924 | 0.00046989 | -0.0012048 | -0.0041807 | -0.07962 | 0.16267 | 0.12709 | -0.00080325 | 0.057319 | 0.10671 | 0.0017687 | -0.064087 | -0.027466 | -0.1236 | -0.07782 | 0.036621 | -0.10071 | -0.022888 | -58.4839 | 60.3195 | -62.4115 | 60.434 | 60.5026 | 60.3149 | 0.3067 | 62.233 | -60.4385 | -60.4889 | 62.3932 | 62.3337 | 62.2559 | 0.10071 | 0.022888 | -0.054932 | -0.091553 | 0.022888 | 122.8592 | 62.6633 | 122.6715 | 62.7182 | 122.7264 | 0.16022 | 0.045776 | 122.9141 | 122.8455 | 0.09613 | 122.731 | 62.3291 | 122.6761 | -60.5347 | -122.8226 | 62.2787 | 122.7905 | 62.2925 | 3.8727
2226.8906 | 123.0743 | -62.3474 | 60.3836 | -0.022278 | 5.7742e-05 | -0.0092051 | 2.8928 | 0.00046989 | -0.002273 | -0.0046079 | -0.046051 | 0.1616 | 0.132 | -0.002085 | 0.054756 | 0.10457 | -0.00015387 | 0.032043 | 0.068665 | -0.054932 | 0.032043 | 0.13275 | 0.068665 | 0.11444 | -58.0032 | 60.3287 | -62.3611 | 60.4889 | 60.5942 | 60.4477 | 0.47607 | 62.2925 | -60.3149 | -60.3516 | 62.4802 | 62.4619 | 62.4161 | 0.16937 | 0.1236 | -0.013733 | -0.054932 | 0.10529 | 122.9416 | 62.8235 | 122.7951 | 62.8372 | 122.8088 | 0.18768 | 0.086975 | 122.9553 | 122.85 | 0.1236 | 122.6898 | 62.4161 | 122.6761 | -60.4385 | -122.7448 | 62.3795 | 122.8363 | 62.3795 | 4.3442
2227.8281 | 122.9599 | -62.3795 | 60.4248 | -0.022278 | -0.0016513 | -0.0083505 | 2.8947 | 0.00089729 | -0.00099116 | -0.0018307 | -0.15286 | 0.16459 | 0.12773 | 0.0015466 | 0.053474 | 0.10543 | -0.0010083 | -0.041199 | 0.073242 | -0.10529 | -0.086975 | -0.018311 | -0.11902 | -0.07782 | -58.0765 | 60.3607 | -62.384 | 60.379 | 60.4294 | 60.2554 | 0.3067 | 62.2742 | -60.3516 | -60.5118 | 62.3611 | 62.3016 | 62.2604 | 0.027466 | -0.013733 | -0.004577 | -0.064087 | -0.045777 | 122.8088 | 62.6862 | 122.6349 | 62.6907 | 122.6395 | 0.086975 | 0.018311 | 122.8134 | 122.7631 | 0.17853 | 122.7448 | 62.4527 | 122.7402 | -60.5301 | -122.8088 | 62.2925 | 122.7585 | 62.3383 | 4.303
2228.8906 | 122.9462 | -62.3749 | 60.434 | -0.014649 | -0.0012241 | -0.0096323 | 2.8918 | -0.00081171 | -0.0035548 | -0.0014035 | -0.091827 | 0.16288 | 0.12986 | -0.0044348 | 0.056038 | 0.10265 | -0.0035719 | -0.004578 | 0.1236 | -0.050354 | -0.013733 | 0.054932 | -0.036621 | 0.036621 | -57.7332 | 60.3882 | -62.3978 | 60.379 | 60.4706 | 60.2921 | 0.39368 | 62.3245 | -60.3104 | -60.4477 | 62.4298 | 62.4115 | 62.3383 | 0.086975 | 0.013733 | -0.022888 | -0.045776 | -0.054932 | 122.8455 | 62.7686 | 122.6669 | 62.7914 | 122.6898 | 0.10529 | 0.036621 | 122.8683 | 122.7768 | 0.17395 | 122.7859 | 62.4985 | 122.7631 | -60.4843 | -122.8317 | 62.3611 | 122.7539 | 62.3703 | 4.6417
2229.8281 | 122.9965 | -62.3795 | 60.3882 | -0.083313 | -0.0012241 | -0.0060007 | 2.8909 | 0.0058105 | 0.00071784 | -0.0024717 | -0.13455 | 0.16373 | 0.12986 | 5.1352e-05 | 0.055183 | 0.10265 | -0.0029309 | -0.013733 | 0.082397 | -0.10071 | -0.022888 | 0.050354 | -0.054932 | -0.018311 | -57.6324 | 60.3607 | -62.3978 | 60.4294 | 60.4706 | 60.2875 | 0.35706 | 62.2787 | -60.3058 | -60.4111 | 62.4298 | 62.3611 | 62.3245 | 0.082397 | 0.045776 | -0.01831 | -0.027466 | 0.041198 | 122.85 | 62.7365 | 122.6669 | 62.7548 | 122.6852 | 0.15106 | 0.07782 | 122.8683 | 122.8271 | 0.18311 | 122.7585 | 62.4619 | 122.7402 | -60.4889 | -122.7859 | 62.3566 | 122.8088 | 62.3657 | 4.747
2230.9062 | 123.0103 | -62.3795 | 60.3653 | -0.060425 | -0.0020785 | -0.0098459 | 2.8928 | 0.0023925 | -0.0020594 | -0.0028989 | -0.15897 | 0.16181 | 0.12794 | -0.00080325 | 0.055183 | 0.10585 | 0.00027333 | -0.11444 | 0.022888 | -0.16022 | -0.16022 | -0.054932 | -0.17853 | -0.10071 | -57.6599 | 60.3149 | -62.4069 | 60.3928 | 60.4523 | 60.2783 | 0.28839 | 62.2192 | -60.3424 | -60.5255 | 62.3245 | 62.2787 | 62.2009 | 0.059509 | -0.018311 | -0.027465 | -0.050354 | 0.027466 | 122.8317 | 62.6678 | 122.6578 | 62.6953 | 122.6852 | 0.10528 | 0 | 122.8592 | 122.7997 | 0.1831 | 122.7219 | 62.4023 | 122.6944 | -60.5255 | -122.7722 | 62.2192 | 122.7722 | 62.265 | 4.7195
2231.8281 | 122.9462 | -62.3703 | 60.4065 | -0.075684 | -0.0014377 | -0.0068551 | 2.8935 | 0.0062379 | -0.00013676 | -0.00097627 | -0.13455 | 0.16352 | 0.13072 | 0.00090575 | 0.055824 | 0.10564 | -0.00036747 | -0.018311 | 0.059509 | -0.086975 | -0.064087 | 0.036621 | -0.073242 | -0.041199 | -57.5546 | 60.347 | -62.4161 | 60.3928 | 60.4523 | 60.2737 | 0.32959 | 62.2833 | -60.347 | -60.4706 | 62.4069 | 62.3291 | 62.2971 | 0.045776 | 0.013733 | -0.045777 | -0.059509 | -0.013733 | 122.8226 | 62.6999 | 122.644 | 62.7457 | 122.6898 | 0.1236 | 0.022888 | 122.8683 | 122.8088 | 0.14648 | 122.7631 | 62.4298 | 122.7173 | -60.4935 | -122.8226 | 62.3062 | 122.7631 | 62.352 | 4.8157
2232.8906 | 123.0103 | -62.3337 | 60.3836 | -0.12909 | -0.0031467 | -0.0094187 | 2.8915 | 0.00089729 | 0.0013586 | -0.0046079 | -0.033844 | 0.16096 | 0.12645 | -0.010843 | 0.056465 | 0.10308 | 0.00091433 | 0.07782 | 0.073242 | -0.045776 | 0.050354 | 0.16937 | 0.064087 | 0.09613 | -57.4127 | 60.3424 | -62.3657 | 60.4477 | 60.553 | 60.3836 | 0.45776 | 62.2879 | -60.3104 | -60.3333 | 62.5031 | 62.4298 | 62.3978 | 0.14191 | 0.10986 | -0.032044 | -0.041199 | 0.064087 | 122.8867 | 62.7914 | 122.7173 | 62.8235 | 122.7493 | 0.21515 | 0.09613 | 122.9187 | 122.8134 | 0.11902 | 122.7081 | 62.4069 | 122.6761 | -60.4294 | -122.7493 | 62.384 | 122.7814 | 62.4115 | 4.921
2233.8281 | 122.9462 | -62.4115 | 60.3928 | -0.068054 | -0.0012241 | -0.0077097 | 2.8922 | 0.0011109 | -0.0020594 | -0.00076267 | -0.030792 | 0.1648 | 0.12901 | -0.00080325 | 0.056678 | 0.10308 | 0.0034777 | -0.10986 | 0.045776 | -0.15106 | -0.17395 | -0.018311 | -0.79193 | -0.40283 | -57.7927 | 60.3653 | -62.4161 | 60.3561 | 60.3973 | 60.2371 | 0.28381 | 62.2604 | -60.347 | -60.5667 | 62.3932 | 62.0087 | 61.6196 | -0.25177 | -0.64087 | -0.004578 | -0.027466 | -0.036621 | 122.8088 | 62.6953 | 122.6486 | 62.6999 | 122.6532 | 0.13275 | -0.022888 | 122.8134 | 122.7722 | 0.19684 | 122.7814 | 62.4573 | 122.7768 | -60.5438 | -122.8088 | 62.2375 | 122.7676 | 62.3016 | 4.6188
2234.8906 | 123.0377 | -62.3566 | 60.3745 | -0.029907 | 0.00048494 | -0.0094187 | 2.8896 | 0.00025629 | -0.0012048 | -0.0031125 | -0.052155 | 0.16245 | 0.12922 | 0.0015466 | 0.05561 | 0.1035 | -0.0044263 | 0.045776 | 0.064087 | -0.032043 | 0.054932 | 0.1831 | 0.073242 | 0.10529 | -57.5729 | 60.3561 | -62.3383 | 60.4477 | 60.5713 | 60.4523 | 0.49439 | 62.3245 | -60.3104 | -60.3195 | 62.5397 | 62.4619 | 62.4298 | 0.13733 | 0.10529 | 0.01831 | -0.018311 | 0.073242 | 122.9279 | 62.851 | 122.8088 | 62.8326 | 122.7905 | 0.21515 | 0.086975 | 122.9095 | 122.7859 | 0.09613 | 122.6944 | 62.4207 | 122.7127 | -60.4065 | -122.7127 | 62.4115 | 122.8043 | 62.4023 | 4.7836
2235.8281 | 122.9507 | -62.3932 | 60.4156 | -0.045166 | 5.7742e-05 | -0.0092051 | 2.8935 | 0.0019653 | 7.6842e-05 | -0.0016171 | -0.14981 | 0.16544 | 0.12986 | -0.0016576 | 0.053901 | 0.10521 | -0.0018629 | -0.10071 | 0.054932 | -0.14191 | -0.15564 | -0.10529 | -0.20142 | -0.13733 | -58.0444 | 60.3607 | -62.4161 | 60.3607 | 60.3882 | 60.2051 | 0.24719 | 62.2513 | -60.3607 | -60.5713 | 62.2879 | 62.2559 | 62.1918 | 0.004578 | -0.059509 | -0.022889 | -0.054931 | -0.054931 | 122.7814 | 62.6404 | 122.5983 | 62.6633 | 122.6212 | 0.036621 | -0.013733 | 122.8043 | 122.7768 | 0.19684 | 122.7768 | 62.4481 | 122.7539 | -60.5576 | -122.8317 | 62.2375 | 122.7539 | 62.2925 | 4.3488
2236.8906 | 123.0103 | -62.3474 | 60.434 | 0.015869 | -0.0016513 | -0.0087777 | 2.8935 | 0.00089729 | -0.0016322 | -0.00033547 | -0.11319 | 0.16416 | 0.13029 | -0.0025122 | 0.056892 | 0.105 | -0.0035719 | 0.018311 | 0.13275 | -0.059509 | -0.027466 | 0.054932 | -0.027466 | 0.004578 | -57.9208 | 60.3699 | -62.3932 | 60.4156 | 60.5347 | 60.3195 | 0.42114 | 62.2879 | -60.3012 | -60.4614 | 62.4023 | 62.352 | 62.3199 | 0.064087 | 0.032043 | -0.045776 | -0.064087 | -0.018311 | 122.8821 | 62.7686 | 122.6669 | 62.8143 | 122.7127 | 0.11444 | 0.032043 | 122.9279 | 122.8088 | 0.19226 | 122.7631 | 62.4802 | 122.7173 | -60.4935 | -122.8271 | 62.3199 | 122.7631 | 62.3657 | 4.4266
2237.8281 | 123.0423 | -62.3611 | 60.3241 | -0.045166 | 5.7742e-05 | -0.0081369 | 2.8918 | 0.0045289 | -0.0033412 | -0.0065305 | -0.1254 | 0.16416 | 0.1273 | -0.0052892 | 0.055824 | 0.10457 | -0.0016493 | -0.086975 | -0.004578 | -0.12817 | -0.11444 | -0.013733 | -0.1236 | -0.059509 | -57.93 | 60.3104 | -62.4161 | 60.4752 | 60.5209 | 60.3699 | 0.34332 | 62.233 | -60.3287 | -60.4385 | 62.3474 | 62.3016 | 62.2375 | 0.068665 | 0.004578 | -0.054932 | -0.013733 | 0.15106 | 122.8821 | 62.7045 | 122.731 | 62.7594 | 122.7859 | 0.11444 | 0.013733 | 122.937 | 122.8912 | 0.1236 | 122.7264 | 62.3566 | 122.6715 | -60.4523 | -122.7402 | 62.2467 | 122.8363 | 62.2742 | 4.4312
2238.8906 | 122.9782 | -62.3566 | 60.4294 | 0.046386 | -0.00079686 | -0.0098459 | 2.8937 | 0.0011109 | -0.00035036 | -0.0011899 | -0.097931 | 0.16224 | 0.12901 | -0.00037605 | 0.052833 | 0.10415 | -0.0027173 | -0.032043 | 0.11902 | -0.082397 | -0.036621 | 0.036621 | -0.009155 | 0.009155 | -58.2321 | 60.3928 | -62.4069 | 60.3973 | 60.4935 | 60.2875 | 0.40741 | 62.2742 | -60.3104 | -60.466 | 62.3932 | 62.3657 | 62.3474 | 0.091552 | 0.073242 | -0.050354 | -0.036621 | -0.032043 | 122.85 | 62.764 | 122.644 | 62.8143 | 122.6944 | 0.11902 | 0.045776 | 122.9004 | 122.8043 | 0.20142 | 122.7997 | 62.4756 | 122.7493 | -60.5118 | -122.8363 | 62.3199 | 122.7539 | 62.3245 | 4.1244
2239.8281 | 123.0057 | -62.3657 | 60.3745 | -0.045166 | -0.0016513 | -0.0079233 | 2.8922 | -0.0014527 | -0.0016322 | -0.0020443 | -0.11014 | 0.16267 | 0.12986 | -0.0010168 | 0.055397 | 0.10244 | -0.00036747 | -0.10986 | 0.018311 | -0.15564 | -0.15106 | -0.045776 | -0.17395 | -0.091553 | -58.2733 | 60.3195 | -62.4344 | 60.4111 | 60.4797 | 60.2966 | 0.3067 | 62.2101 | -60.3561 | -60.5255 | 62.3199 | 62.2742 | 62.1918 | 0.064087 | -0.01831 | -0.068664 | -0.054932 | 0.036621 | 122.8455 | 62.6724 | 122.6624 | 62.7411 | 122.731 | 0.10986 | 0.004578 | 122.9141 | 122.8455 | 0.17395 | 122.7539 | 62.384 | 122.6852 | -60.5301 | -122.8088 | 62.2147 | 122.7768 | 62.2559 | 4.0924
2240.8906 | 122.9462 | -62.3611 | 60.4202 | 0.031128 | -0.00058326 | -0.0092051 | 2.8941 | -0.0010253 | -0.0048364 | -0.0052487 | -0.067413 | 0.16288 | 0.12858 | -0.013621 | 0.055183 | 0.10393 | -0.0035719 | 0.009155 | 0.15106 | -0.041199 | -0.045776 | 0.56763 | 0.19226 | -0.22888 | -58.2687 | 60.3928 | -62.4023 | 60.3973 | 60.4752 | 60.2875 | 0.40741 | 62.3199 | -60.2692 | -60.466 | 62.9288 | 62.1323 | 62.5534 | -0.18768 | 0.23346 | -0.041199 | -0.027466 | -0.022888 | 122.8363 | 62.7686 | 122.6486 | 62.8098 | 122.6898 | 0.60883 | -0.004577 | 122.8775 | 122.7997 | 0.19226 | 122.7951 | 62.5122 | 122.7539 | -60.4614 | -122.8226 | 62.3154 | 122.7585 | 62.3703 | 4.0924
2241.8281 | 123.0103 | -62.3749 | 60.347 | -0.1062 | 0.00048494 | -0.0085641 | 2.8933 | 0.0036743 | -0.0020594 | -0.0031125 | -0.07962 | 0.16138 | 0.12837 | -0.003153 | 0.054969 | 0.10286 | -0.0057081 | -0.064087 | -0.041199 | -0.14191 | -0.064087 | 0.041199 | -0.10071 | -0.022888 | -57.9987 | 60.2966 | -62.3886 | 60.4797 | 60.5347 | 60.1868 | 0.14648 | 62.233 | -60.3882 | -60.4111 | 62.4161 | 62.352 | 62.2742 | 0.11902 | 0.041199 | -0.013733 | -0.050354 | 0.13275 | 122.9095 | 62.5214 | 122.5616 | 62.5351 | 122.5754 | 0.18311 | 0.07782 | 122.9233 | 122.8683 | 0.10071 | 122.6852 | 62.3337 | 122.6715 | -60.4889 | -122.7356 | 62.3108 | 122.8546 | 62.3108 | 4.3762
2242.8906 | 122.9782 | -62.3566 | 60.4111 | -0.045166 | -0.0020785 | -0.0089913 | 2.8937 | 0.0015381 | -0.00035036 | -0.0011899 | -0.11624 | 0.16373 | 0.12858 | -0.0025122 | 0.056251 | 0.10393 | -0.0044263 | 0 | 0.10071 | -0.054932 | -0.022888 | 0.059509 | -0.054932 | 0 | -58.0948 | 60.3516 | -62.4069 | 60.3378 | 60.4111 | 60.4065 | 0.3891 | 62.3016 | -60.3104 | -60.434 | 62.4161 | 62.3566 | 62.3016 | 0.054932 | 0 | -0.050354 | -0.05951 | -0.073242 | 122.7676 | 62.7457 | 122.7631 | 62.796 | 122.8134 | 0.11444 | 0.032044 | 122.818 | 122.7448 | 0.15564 | 122.7585 | 62.4573 | 122.7081 | -60.466 | -122.818 | 62.3337 | 122.6944 | 62.3566 | 4.2618
2243.8281 | 123.0652 | -62.352 | 60.347 | -0.1062 | -0.0010105 | -0.0074961 | 2.8933 | 0.0028199 | 0.001145 | -0.0037533 | -0.11319 | 0.16267 | 0.12687 | -0.0061438 | 0.054969 | 0.10393 | -0.0016493 | -0.086975 | 0.004578 | -0.14648 | -0.09613 | -0.013733 | -0.11902 | -0.059509 | -58.0765 | 60.2966 | -62.384 | 60.4523 | 60.5301 | 60.3424 | 0.35248 | 62.2055 | -60.3424 | -60.4431 | 62.3383 | 62.2925 | 62.233 | 0.086975 | 0.027465 | -0.032043 | -0.050354 | 0.10529 | 122.8821 | 62.7045 | 122.6944 | 62.7365 | 122.7264 | 0.13275 | 0.050354 | 122.9141 | 122.8363 | 0.15106 | 122.6807 | 62.3566 | 122.6486 | -60.4935 | -122.731 | 62.2559 | 122.8043 | 62.265 | 4.2755
2244.8906 | 122.9187 | -62.4023 | 60.4065 | -0.029907 | -0.0029331 | -0.0085641 | 2.8924 | -0.00081171 | -0.0031274 | -0.0022581 | -0.13455 | 0.16288 | 0.1273 | 0.00069215 | 0.05561 | 0.10479 | 0.00048713 | -0.07782 | 0.045776 | -0.12817 | -0.14648 | -0.07782 | -0.19684 | -0.13733 | -58.1543 | 60.3607 | -62.4435 | 60.347 | 60.3699 | 60.2188 | 0.27008 | 62.2742 | -60.3607 | -60.553 | 62.3245 | 62.265 | 62.2055 | -0.009155 | -0.068664 | -0.041198 | -0.045776 | -0.059509 | 122.7722 | 62.6724 | 122.6212 | 62.7136 | 122.6624 | 0.050354 | -0.01831 | 122.8134 | 122.7905 | 0.17395 | 122.8043 | 62.4481 | 122.7631 | -60.5347 | -122.85 | 62.2559 | 122.7493 | 62.3245 | 4.248
2245.8281 | 123.0469 | -62.3611 | 60.3424 | -0.1062 | -0.00079686 | -0.0079233 | 2.8935 | -0.00081171 | -0.00077756 | -0.0026853 | -0.049103 | 0.16267 | 0.12901 | -0.0072118 | 0.055183 | 0.10543 | -0.00036747 | -0.050354 | -0.041199 | -0.13733 | -0.4303 | -0.036621 | 0.3067 | 0.082397 | -58.049 | 60.2966 | -62.3795 | 60.4431 | 60.5255 | 60.3378 | 0.35248 | 62.2238 | -60.3836 | -60.7727 | 62.3245 | 62.4435 | 62.6678 | 0.21973 | 0.44403 | -0.018311 | -0.045776 | 0.10071 | 122.8867 | 62.7136 | 122.699 | 62.7319 | 122.7173 | 0.10071 | -0.29297 | 122.905 | 122.8226 | 0.09613 | 122.6761 | 62.3199 | 122.6578 | -60.4797 | -122.7219 | 61.9308 | 122.8043 | 62.3108 | 4.3121
2246.8906 | 123.0011 | -62.3611 | 60.4248 | 0.00824 | -0.00058326 | -0.010487 | 2.8924 | 0.0017517 | -0.002273 | -0.0031125 | -0.14066 | 0.16352 | 0.1258 | -0.0057166 | 0.055183 | 0.10329 | -0.0050671 | 0.027466 | 0.11444 | -0.045776 | -0.032043 | 0.07782 | -0.018311 | 0.022888 | -58.7723 | 60.3882 | -62.384 | 60.4431 | 60.5072 | 60.3333 | 0.41657 | 62.3154 | -60.3104 | -60.4568 | 62.439 | 62.384 | 62.3428 | 0.068664 | 0.027465 | -0.022888 | -0.036621 | 0.01831 | 122.8683 | 62.7777 | 122.6944 | 62.8006 | 122.7173 | 0.1236 | 0.013733 | 122.8912 | 122.8271 | 0.16022 | 122.7722 | 62.4756 | 122.7493 | -60.4706 | -122.8088 | 62.3291 | 122.8043 | 62.3886 | 3.5889
2247.8281 | 123.0652 | -62.3428 | 60.3653 | -0.007019 | 5.7742e-05 | -0.0045053 | 2.8926 | 4.2692e-05 | 0.001145 | -0.0022581 | -0.070465 | 0.16331 | 0.12773 | -0.0042212 | 0.053474 | 0.10372 | -0.0027173 | -0.045776 | -0.045776 | -0.13275 | 0.018311 | 0.14191 | -0.082397 | 0 | -58.8867 | 60.3149 | -62.4115 | 60.466 | 60.5347 | 60.347 | 0.34332 | 62.2101 | -60.4111 | -60.347 | 62.4847 | 62.3428 | 62.2604 | 0.13275 | 0.050354 | -0.068665 | -0.050354 | 0.10071 | 122.8775 | 62.6862 | 122.6898 | 62.7548 | 122.7585 | 0.27466 | 0.15106 | 122.9462 | 122.8775 | 0.086975 | 122.7264 | 62.2971 | 122.6578 | -60.498 | -122.7768 | 62.3611 | 122.8088 | 62.2971 | 3.4561
2248.8906 | 122.9507 | -62.3795 | 60.4202 | -0.045166 | 0.00048494 | -0.0079233 | 2.893 | 0.0015381 | -0.0029138 | -0.0016171 | -0.13455 | 0.16267 | 0.12858 | 0.0066736 | 0.057533 | 0.10436 | -0.00079467 | -0.10986 | 0.045776 | -0.13275 | -0.16937 | -0.1236 | -0.19226 | -0.14648 | -59.4223 | 60.3561 | -62.3932 | 60.3607 | 60.4111 | 60.2234 | 0.2655 | 62.2467 | -60.3745 | -60.5896 | 62.2559 | 62.233 | 62.1872 | -0.013733 | -0.05951 | -0.013732 | -0.064087 | -0.059509 | 122.7905 | 62.645 | 122.6028 | 62.6587 | 122.6166 | 0.009155 | -0.036622 | 122.8043 | 122.7539 | 0.17853 | 122.7493 | 62.4252 | 122.7356 | -60.553 | -122.8134 | 62.2101 | 122.7402 | 62.2696 | 2.9572
2249.8281 | 123.0331 | -62.3428 | 60.3607 | -0.060425 | -0.0020785 | -0.0094187 | 2.8907 | -0.0031617 | -0.0020594 | -0.0016171 | -0.067413 | 0.16224 | 0.12751 | -0.0033666 | 0.056038 | 0.10415 | -0.00058107 | -0.059509 | -0.022888 | -0.10529 | -0.073242 | 0.032043 | -0.09613 | -0.022888 | -59.2712 | 60.3241 | -62.3703 | 60.4294 | 60.5072 | 60.3424 | 0.32501 | 62.2375 | -60.3836 | -60.434 | 62.3749 | 62.3199 | 62.2467 | 0.082398 | 0.009156 | -0.027466 | -0.036621 | 0.068664 | 122.85 | 62.6678 | 122.6852 | 62.6953 | 122.7127 | 0.13733 | 0.032044 | 122.8775 | 122.7997 | 0.082398 | 122.6944 | 62.3199 | 122.6669 | -60.466 | -122.731 | 62.2696 | 122.7722 | 62.2833 | 3.0716
2250.8906 | 122.9416 | -62.3703 | 60.4248 | -0.007019 | -0.00058326 | -0.0064279 | 2.893 | 0.0045289 | 7.6842e-05 | 0.0013735 | -0.13455 | 0.16437 | 0.12815 | 0.0015466 | 0.054756 | 0.10543 | -0.0025037 | -0.041199 | 0.054932 | -0.11444 | -0.10071 | -0.027466 | -0.13275 | -0.091553 | -59.404 | 60.3653 | -62.4023 | 60.3745 | 60.434 | 60.2325 | 0.31128 | 62.2559 | -60.3699 | -60.5255 | 62.3428 | 62.2787 | 62.2375 | 0.022888 | -0.01831 | -0.032044 | -0.05951 | -0.050354 | 122.8043 | 62.6816 | 122.6028 | 62.7136 | 122.6349 | 0.086975 | 0.013733 | 122.8363 | 122.7768 | 0.16937 | 122.7676 | 62.4252 | 122.7356 | -60.5392 | -122.8271 | 62.2696 | 122.7448 | 62.3291 | 2.9663
2251.8281 | 123.024 | -62.3245 | 60.3882 | -0.045166 | 5.7742e-05 | -0.0087777 | 2.8909 | 0.0038879 | 7.6842e-05 | -0.0043943 | -0.030792 | 0.16502 | 0.12794 | -0.0089208 | 0.05561 | 0.10436 | -0.0012219 | -0.059509 | 0.027466 | -0.10071 | -0.073242 | 0.027466 | -0.068665 | -0.013733 | -59.3353 | 60.3378 | -62.3611 | 60.5072 | 60.5759 | 60.2554 | 0.36621 | 62.2238 | -60.3607 | -60.4614 | 62.352 | 62.3108 | 62.2559 | 0.086975 | 0.032043 | -0.036621 | -0.050354 | 0.11902 | 122.9004 | 62.6907 | 122.58 | 62.7274 | 122.6166 | 0.12817 | 0.027466 | 122.937 | 122.8683 | 0.12817 | 122.699 | 62.352 | 122.6624 | -60.4889 | -122.7493 | 62.2513 | 122.8317 | 62.265 | 2.9892
2252.9062 | 123.0194 | -62.3657 | 60.3516 | -0.090943 | -0.0010105 | -0.0085641 | 2.8926 | -0.0055115 | -0.0046228 | -0.00097627 | -0.06131 | 0.16224 | 0.12986 | 0.00069215 | 0.054542 | 0.10457 | -0.0035719 | -0.082397 | -0.022888 | -0.09613 | -0.068665 | 0.027466 | -0.11902 | -0.036621 | -59.2575 | 60.3424 | -62.3657 | 60.4294 | 60.5026 | 60.3378 | 0.3479 | 62.2696 | -60.3745 | -60.4202 | 62.3932 | 62.3291 | 62.2467 | 0.059509 | -0.022889 | 0 | -0.009155 | 0.07782 | 122.8683 | 62.7136 | 122.7036 | 62.7136 | 122.7036 | 0.1236 | 0.027465 | 122.8683 | 122.7951 | 0.073242 | 122.7081 | 62.3428 | 122.7081 | -60.4477 | -122.7173 | 62.2971 | 122.7951 | 62.2833 | 3.1082
2253.8281 | 123.0469 | -62.3428 | 60.3745 | -0.098572 | -0.0014377 | -0.0094187 | 2.8909 | -0.0018799 | -0.002273 | -0.0033261 | -0.052155 | 0.16587 | 0.12709 | -0.0025122 | 0.053901 | 0.10329 | 0.00070073 | -0.073242 | -0.027466 | -0.12817 | -0.073242 | 0.027466 | -0.091553 | -0.018311 | -59.5367 | 60.3241 | -62.3932 | 60.4202 | 60.5301 | 60.3378 | 0.32044 | 62.2147 | -60.4019 | -60.4477 | 62.3703 | 62.3245 | 62.2513 | 0.10986 | 0.036621 | -0.050354 | -0.050354 | 0.045776 | 122.8729 | 62.6633 | 122.6807 | 62.7136 | 122.731 | 0.15564 | 0.054932 | 122.9233 | 122.8134 | 0.10071 | 122.7173 | 62.3154 | 122.6669 | -60.5026 | -122.7676 | 62.2696 | 122.7631 | 62.2696 | 2.8061
2254.8281 | 123.0606 | -62.3566 | 60.3516 | -0.060425 | -0.0020785 | -0.0072825 | 2.8928 | 0.00025629 | 7.6842e-05 | -0.0043943 | -0.07962 | 0.1616 | 0.12602 | -0.00080325 | 0.054756 | 0.10372 | -0.00036747 | -0.068665 | -0.022888 | -0.09613 | -0.050354 | 0.073242 | -0.068665 | -0.004578 | -58.6121 | 60.3149 | -62.3703 | 60.466 | 60.5255 | 60.3378 | 0.35248 | 62.2604 | -60.3745 | -60.4019 | 62.4298 | 62.352 | 62.2879 | 0.091552 | 0.027465 | -0.013733 | -0.036621 | 0.11444 | 122.8821 | 62.709 | 122.6944 | 62.7228 | 122.7081 | 0.16937 | 0.045776 | 122.8958 | 122.8363 | 0.073242 | 122.6852 | 62.3337 | 122.6715 | -60.4477 | -122.7219 | 62.3062 | 122.8226 | 62.2879 | 3.7445
2255.8906 | 122.9233 | -62.3795 | 60.434 | -0.052796 | -0.0016513 | -0.0081369 | 2.8926 | 0.0019653 | -0.0078272 | -0.0033261 | -0.16507 | 0.16566 | 0.12815 | -0.003794 | 0.053901 | 0.10201 | -0.00036747 | -0.11444 | 0.027466 | -0.13275 | -0.15106 | -0.10986 | -0.17853 | -0.11444 | -59.3582 | 60.3745 | -62.4252 | 60.2325 | 60.498 | 60.466 | 0.37994 | 62.2467 | -60.4065 | -60.585 | 62.2696 | 62.265 | 62.2009 | 0.01831 | -0.045777 | -0.045776 | -0.059509 | -0.20142 | 122.8775 | 62.7594 | 122.8455 | 62.8052 | 122.8912 | 0.022888 | -0.018311 | 122.9233 | 122.6578 | 0.16022 | 122.7997 | 62.4069 | 122.7539 | -60.5667 | -122.8592 | 62.2284 | 122.612 | 62.265 | 3.0212
2256.8281 | 123.056 | -62.3657 | 60.3882 | -0.12146 | -0.00036966 | -0.0087777 | 2.8915 | -0.0016663 | -0.00035036 | -0.0016171 | -0.097931 | 0.16395 | 0.12559 | -0.0076392 | 0.053474 | 0.10308 | -0.0022901 | 0.004578 | -0.027466 | -0.09613 | -0.036621 | 0.064087 | -0.086975 | -0.009155 | -59.3765 | 60.3149 | -62.3795 | 60.4889 | 60.5392 | 60.3699 | 0.33875 | 62.2696 | -60.4156 | -60.4248 | 62.4298 | 62.3566 | 62.2787 | 0.086975 | 0.009155 | -0.013733 | -0.073243 | 0.10071 | 122.905 | 62.7045 | 122.7356 | 62.7182 | 122.7493 | 0.16022 | 0.059509 | 122.9187 | 122.8683 | 0.068664 | 122.6944 | 62.3383 | 122.6807 | -60.4843 | -122.7676 | 62.3291 | 122.8546 | 62.3703 | 2.9892
2257.8906 | 122.9919 | -62.3657 | 60.4248 | -0.075684 | -0.0022923 | -0.0077097 | 2.8941 | 0.00025629 | -0.0037684 | -0.0020443 | -0.16202 | 0.16523 | 0.12559 | -0.00080325 | 0.056678 | 0.10714 | -0.0033581 | -0.11444 | 0.018311 | -0.13275 | -0.16022 | -0.10071 | -0.1831 | -0.13733 | -59.6237 | 60.3836 | -62.4161 | 60.4202 | 60.6216 | 60.173 | 0.20142 | 62.233 | -60.4065 | -60.585 | 62.265 | 62.2284 | 62.1826 | -0.004578 | -0.050354 | -0.050354 | -0.041199 | -0.004578 | 122.9874 | 62.5671 | 122.5388 | 62.6175 | 122.5891 | 0.032043 | -0.027466 | 123.0377 | 122.8363 | 0.15106 | 122.7997 | 62.384 | 122.7493 | -60.5576 | -122.8409 | 62.2055 | 122.7859 | 62.2513 | 2.742
2258.8281 | 123.0103 | -62.352 | 60.3882 | -0.1062 | 0.0013393 | -0.0107 | 2.8924 | -0.0016663 | -0.0033412 | -0.0014035 | -0.07962 | 0.16331 | 0.12773 | -0.00058965 | 0.057533 | 0.10521 | 0.0024097 | -0.064087 | -0.018311 | -0.11444 | -0.073242 | 0.036621 | -0.068665 | -0.027466 | -59.4635 | 60.347 | -62.3795 | 60.4385 | 60.5301 | 60.3516 | 0.33875 | 62.2375 | -60.4065 | -60.4614 | 62.3886 | 62.3245 | 62.2833 | 0.086975 | 0.045776 | -0.027466 | -0.041199 | 0.050354 | 122.8821 | 62.6907 | 122.7036 | 62.7182 | 122.731 | 0.15106 | 0.041199 | 122.9095 | 122.818 | 0.09613 | 122.7264 | 62.3337 | 122.699 | -60.5026 | -122.7676 | 62.2787 | 122.7905 | 62.2879 | 2.8885
2259.8906 | 122.9782 | -62.3749 | 60.4111 | -0.022278 | -0.0012241 | -0.0068551 | 2.8924 | 4.2692e-05 | -0.00077756 | -0.0033261 | -0.16812 | 0.1616 | 0.12602 | 0.0032556 | 0.055824 | 0.099873 | -0.00036747 | -0.091553 | 0.032043 | -0.14648 | -0.16937 | -0.11444 | -0.18768 | -0.12817 | -59.6283 | 60.3745 | -62.4298 | 60.5301 | 60.3836 | 60.2509 | 0.31586 | 62.2284 | -60.379 | -60.5804 | 62.2604 | 62.2467 | 62.1872 | 0.01831 | -0.041199 | -0.054932 | -0.036621 | 0.11902 | 122.7585 | 62.6907 | 122.6257 | 62.7457 | 122.6807 | 0.032043 | -0.022889 | 122.8134 | 122.9599 | 0.17853 | 122.8043 | 62.4069 | 122.7493 | -60.5576 | -122.8409 | 62.2055 | 122.905 | 62.2833 | 2.7466
2260.8281 | 123.0652 | -62.3383 | 60.3607 | -0.052796 | 0.00027134 | -0.0070687 | 2.8924 | 0.0026063 | 0.00071784 | 0.0011599 | -0.085724 | 0.16288 | 0.12666 | -0.002085 | 0.054756 | 0.10457 | -0.00079467 | -0.07782 | -0.009155 | -0.10986 | -0.045776 | 0.064087 | -0.082397 | -0.018311 | -59.7656 | 60.3287 | -62.3749 | 60.466 | 60.5255 | 60.3561 | 0.35248 | 62.2284 | -60.3699 | -60.4065 | 62.4023 | 62.3199 | 62.2559 | 0.091552 | 0.027466 | -0.036621 | -0.032044 | 0.10529 | 122.8638 | 62.6907 | 122.6944 | 62.7274 | 122.731 | 0.17395 | 0.064087 | 122.9004 | 122.8409 | 0.10071 | 122.7036 | 62.3291 | 122.6669 | -60.4706 | -122.7356 | 62.2925 | 122.8043 | 62.2604 | 2.5726
2261.8906 | 122.9919 | -62.3337 | 60.4385 | -0.014649 | -0.0037875 | -0.0087777 | 2.8909 | 0.00046989 | -0.00013676 | -0.0031125 | -0.12845 | 0.16437 | 0.12794 | 5.1352e-05 | 0.055397 | 0.10436 | -0.0018629 | 0.009155 | 0.14191 | -0.036621 | -0.027466 | 0.059509 | -0.004578 | 0.032043 | -59.7427 | 60.4065 | -62.384 | 60.4294 | 60.5301 | 60.3378 | 0.43945 | 62.2971 | -60.2966 | -60.466 | 62.3932 | 62.3657 | 62.3291 | 0.068664 | 0.032043 | -0.050354 | -0.032044 | -0.009156 | 122.8638 | 62.7731 | 122.6715 | 62.8235 | 122.7219 | 0.09613 | 0.009155 | 122.9141 | 122.8134 | 0.17853 | 122.7905 | 62.4756 | 122.7402 | -60.4752 | -122.8226 | 62.3062 | 122.7631 | 62.3428 | 2.5909
2262.8281 | 123.0148 | -62.3703 | 60.3928 | -0.1062 | -0.0014377 | -0.0079233 | 2.8924 | 0.0021789 | -0.00099116 | -0.00097627 | -0.064362 | 0.16202 | 0.12965 | -0.0027258 | 0.054329 | 0.10329 | 0.00048713 | -0.068665 | -0.004578 | -0.10071 | -0.068665 | 0.004578 | -0.09613 | -0.032043 | -59.8434 | 60.3241 | -62.384 | 60.4385 | 60.5209 | 60.347 | 0.33875 | 62.2696 | -60.3973 | -60.4614 | 62.3749 | 62.3383 | 62.2742 | 0.068665 | 0.004578 | -0.013733 | -0.068664 | 0.045777 | 122.8912 | 62.709 | 122.7173 | 62.7228 | 122.731 | 0.10529 | 0.032043 | 122.905 | 122.8226 | 0.09613 | 122.7081 | 62.3657 | 122.6944 | -60.4935 | -122.7768 | 62.3016 | 122.8088 | 62.3016 | 2.5269
2263.8281 | 123.0698 | -62.3474 | 60.4019 | -0.022278 | -0.0014377 | -0.010059 | 2.892 | 0.0021789 | -0.0037684 | -0.0033261 | -0.06131 | 0.1601 | 0.12858 | -0.003794 | 0.057106 | 0.10543 | -0.0020765 | -0.022888 | 0.036621 | -0.073242 | -0.018311 | 0.10071 | -0.004578 | 0.045776 | -59.697 | 60.3424 | -62.3474 | 60.498 | 60.5759 | 60.4156 | 0.43488 | 62.2742 | -60.3653 | -60.4202 | 62.4481 | 62.3932 | 62.3428 | 0.11902 | 0.068664 | 0 | -0.05951 | 0.09613 | 122.9233 | 62.7823 | 122.7631 | 62.7823 | 122.7631 | 0.17395 | 0.054931 | 122.9233 | 122.8455 | 0.10986 | 122.6898 | 62.384 | 122.6898 | -60.4752 | -122.7493 | 62.3291 | 122.8455 | 62.3245 | 2.6505
2264.8906 | 123.0835 | -62.3474 | 60.379 | -0.075684 | -0.00079686 | -0.010059 | 2.8922 | -0.0012391 | 0.00029044 | 0.0020145 | -0.1315 | 0.16309 | 0.12623 | -0.0029394 | 0.05561 | 0.105 | 0.0043323 | -0.10071 | -0.013733 | -0.14191 | -0.09613 | 0.022888 | -0.082397 | -0.041199 | -59.6649 | 60.3378 | -62.384 | 60.4889 | 60.5438 | 60.3607 | 0.37537 | 62.2055 | -60.3928 | -60.4752 | 62.3703 | 62.3062 | 62.265 | 0.10071 | 0.05951 | -0.036621 | -0.041198 | 0.10986 | 122.8912 | 62.7228 | 122.7081 | 62.7594 | 122.7448 | 0.16479 | 0.045777 | 122.9279 | 122.8729 | 0.12817 | 122.7219 | 62.3337 | 122.6852 | -60.5209 | -122.7631 | 62.2513 | 122.8363 | 62.2467 | 2.6825
2265.8281 | 123.0515 | -62.3428 | 60.4156 | -0.007019 | -0.0027195 | -0.010059 | 2.8915 | -0.0031617 | -0.0029138 | -0.00033547 | -0.082672 | 0.16288 | 0.12559 | -0.00058965 | 0.056251 | 0.10479 | 0.0015551 | 0.041199 | 0.068665 | -0.036621 | -0.29755 | -0.21515 | 0.17395 | 0.073242 | -60.2509 | 60.3653 | -62.3566 | 60.5164 | 60.5988 | 60.4111 | 0.48523 | 62.3062 | -60.347 | -60.7132 | 62.1277 | 62.4161 | 62.5168 | 0.10986 | 0.21057 | -0.013733 | -0.050354 | 0.10071 | 122.9416 | 62.8281 | 122.7539 | 62.8418 | 122.7676 | -0.17853 | -0.26092 | 122.9553 | 122.8729 | 0.10529 | 122.7219 | 62.4115 | 122.7081 | -60.4523 | -122.7722 | 62.0453 | 122.8592 | 62.384 | 2.092
2266.8906 | 122.9645 | -62.3383 | 60.4156 | -0.037537 | -0.00036966 | -0.0085641 | 2.8939 | 0.00089729 | -0.0014184 | -0.0033261 | -0.17422 | 0.16437 | 0.12815 | -0.0027258 | 0.054969 | 0.10671 | -0.0042127 | -0.013733 | 0.073242 | -0.07782 | -0.050354 | 0.036621 | -0.09613 | -0.036621 | -60.3287 | 60.4065 | -62.3886 | 60.434 | 60.4843 | 60.2783 | 0.33417 | 62.2604 | -60.3424 | -60.466 | 62.3749 | 62.3016 | 62.2421 | 0.041199 | -0.01831 | -0.050354 | -0.009155 | 0.018311 | 122.8226 | 62.6724 | 122.6166 | 62.7228 | 122.6669 | 0.11444 | 0.027466 | 122.8729 | 122.8226 | 0.15106 | 122.7951 | 62.4115 | 122.7448 | -60.4935 | -122.8043 | 62.2879 | 122.7722 | 62.3245 | 2.0096
2267.8281 | 123.0652 | -62.3062 | 60.4202 | -0.060425 | -0.0027195 | -0.0096323 | 2.892 | 0.00046989 | -0.0024866 | -0.0024717 | -0.055206 | 0.16395 | 0.12559 | -0.0025122 | 0.056251 | 0.10521 | 5.9726e-05 | -0.013733 | 0.041199 | -0.07782 | 0.009155 | 0.10071 | -0.004578 | 0.050354 | -60.8871 | 60.3607 | -62.3657 | 60.5026 | 60.6079 | 60.4248 | 0.44861 | 62.2284 | -60.379 | -60.4111 | 62.4069 | 62.3566 | 62.3016 | 0.12817 | 0.073242 | -0.05951 | -0.059509 | 0.082398 | 122.9141 | 62.7548 | 122.731 | 62.8143 | 122.7905 | 0.17853 | 0.086975 | 122.9736 | 122.8683 | 0.11902 | 122.7264 | 62.3474 | 122.6669 | -60.498 | -122.7859 | 62.3154 | 122.8088 | 62.2925 | 1.4191
2268.8906 | 123.0743 | -62.3291 | 60.379 | -0.060425 | -0.0033603 | -0.0072825 | 2.8943 | -0.0025207 | 0.00029044 | 0.00051913 | -0.13455 | 0.16352 | 0.12666 | -0.0044348 | 0.054756 | 0.10543 | -0.0029309 | -0.10529 | -0.018311 | -0.13733 | -0.11444 | -0.086975 | -0.10986 | -0.018311 | -60.5621 | 60.3333 | -62.3795 | 60.498 | 60.5576 | 60.3653 | 0.35248 | 62.1918 | -60.3973 | -60.4935 | 62.2421 | 62.3108 | 62.2192 | 0.11902 | 0.027466 | -0.050354 | -0.045776 | 0.11902 | 122.8867 | 62.6816 | 122.6944 | 62.7319 | 122.7448 | 0.050354 | 0.022888 | 122.937 | 122.8775 | 0.11902 | 122.7127 | 62.3108 | 122.6624 | -60.5164 | -122.7585 | 62.2147 | 122.8271 | 62.2238 | 1.767
2269.8281 | 123.0881 | -62.3199 | 60.4111 | -0.052796 | -0.0010105 | -0.0098459 | 2.8907 | -0.0014527 | -0.0020594 | -0.0035397 | -0.052155 | 0.16288 | 0.1258 | 5.1352e-05 | 0.055397 | 0.10286 | -0.0014355 | 0.022888 | 0.045776 | -0.059509 | 0.050354 | 0.17395 | 0.09613 | 0.12817 | -60.7224 | 60.347 | -62.352 | 60.5347 | 60.6445 | 60.4797 | 0.4715 | 62.2604 | -60.3653 | -60.3607 | 62.4939 | 62.4481 | 62.4161 | 0.18768 | 0.15564 | -0.032044 | -0.064087 | 0.1236 | 122.9645 | 62.7914 | 122.7997 | 62.8235 | 122.8317 | 0.23346 | 0.10986 | 122.9965 | 122.8867 | 0.10528 | 122.699 | 62.3657 | 122.6669 | -60.4706 | -122.7631 | 62.3703 | 122.8546 | 62.3428 | 1.5976
2270.8906 | 123.056 | -62.3337 | 60.3836 | -0.083313 | 0.00069854 | -0.0098459 | 2.8941 | 0.0032471 | -0.00013676 | -0.0016171 | -0.12234 | 0.16181 | 0.12944 | -0.0027258 | 0.056251 | 0.10415 | -0.0050671 | -0.041199 | -0.027466 | -0.1236 | -0.059509 | 0.054932 | -0.09613 | -0.013733 | -61.0657 | 60.3104 | -62.4023 | 60.5347 | 60.5392 | 60.3882 | 0.35248 | 62.2101 | -60.4111 | -60.4431 | 62.3886 | 62.3199 | 62.2375 | 0.10986 | 0.027466 | -0.068665 | -0.073242 | 0.15106 | 122.8729 | 62.6862 | 122.7219 | 62.7548 | 122.7905 | 0.17853 | 0.064087 | 122.9416 | 122.937 | 0.09613 | 122.7127 | 62.3062 | 122.644 | -60.5072 | -122.7859 | 62.2742 | 122.8683 | 62.2925 | 1.268
2271.8281 | 123.111 | -62.3199 | 60.4248 | -0.045166 | -0.0016513 | -0.010059 | 2.8926 | 0.00025629 | -0.0014184 | -0.0039671 | -0.052155 | 0.16224 | 0.12751 | 5.1352e-05 | 0.054756 | 0.10244 | -0.0018629 | 0.013733 | 0.068665 | -0.068665 | 0.027466 | 0.13733 | 0.009155 | 0.07782 | -60.9604 | 60.3607 | -62.3474 | 60.5301 | 60.6354 | 60.466 | 0.48523 | 62.2513 | -60.3561 | -60.3973 | 62.4573 | 62.3978 | 62.3291 | 0.14649 | 0.07782 | -0.027466 | -0.064087 | 0.10529 | 122.9553 | 62.8052 | 122.7859 | 62.8326 | 122.8134 | 0.20599 | 0.096131 | 122.9828 | 122.8775 | 0.13733 | 122.7081 | 62.3886 | 122.6807 | -60.4935 | -122.7722 | 62.3474 | 122.85 | 62.3337 | 1.3596
2272.8906 | 122.9965 | -62.3611 | 60.4202 | -0.029907 | -0.00036966 | -0.0096323 | 2.893 | 0.0019653 | -0.0033412 | -0.0026853 | -0.16507 | 0.16373 | 0.12687 | 0.0021876 | 0.054115 | 0.10479 | -0.0031445 | 0.022888 | 0.1236 | -0.064087 | -0.009155 | 0.068665 | -0.041199 | 0.009155 | -61.1114 | 60.4156 | -62.3566 | 60.4523 | 60.5301 | 60.3333 | 0.41199 | 62.2971 | -60.2966 | -60.4294 | 62.4298 | 62.3703 | 62.3199 | 0.073242 | 0.022888 | 0.004578 | -0.004578 | 0.032044 | 122.8912 | 62.7731 | 122.6944 | 62.7686 | 122.6898 | 0.13275 | 0.054932 | 122.8867 | 122.8088 | 0.18768 | 122.7722 | 62.4847 | 122.7768 | -60.4843 | -122.7768 | 62.352 | 122.8134 | 62.384 | 1.2497
2273.8281 | 123.0698 | -62.2879 | 60.4248 | -0.022278 | 5.7742e-05 | -0.0085641 | 2.892 | -0.0016663 | -0.00035036 | -0.0039671 | -0.058258 | 0.1648 | 0.12559 | -0.010843 | 0.057106 | 0.10372 | -0.0035719 | 0.013733 | 0.064087 | -0.054932 | 0.009155 | 0.12817 | 0.027466 | 0.086975 | -61.4273 | 60.3561 | -62.3474 | 60.5209 | 60.6354 | 60.4614 | 0.46234 | 62.233 | -60.3607 | -60.4156 | 62.4161 | 62.3749 | 62.3154 | 0.14191 | 0.082398 | -0.059509 | -0.068665 | 0.09613 | 122.9233 | 62.7502 | 122.7493 | 62.8098 | 122.8088 | 0.18311 | 0.064087 | 122.9828 | 122.8683 | 0.11902 | 122.7036 | 62.352 | 122.644 | -60.4797 | -122.7722 | 62.2971 | 122.8088 | 62.3016 | 0.8606
2274.8906 | 123.0652 | -62.3245 | 60.3836 | -0.098572 | -0.00058326 | -0.0094187 | 2.8935 | 0.0023925 | -0.0014184 | 0.0015871 | -0.14981 | 0.16331 | 0.12538 | 0.0083826 | 0.054115 | 0.10436 | -0.00079467 | -0.032043 | -0.045776 | -0.15564 | -0.064087 | 0.022888 | -0.091553 | -0.050354 | -61.7935 | 60.3333 | -62.3795 | 60.5118 | 60.585 | 60.4065 | 0.35248 | 62.1689 | -60.4294 | -60.4477 | 62.3474 | 62.2742 | 62.233 | 0.10529 | 0.064087 | -0.054932 | -0.050354 | 0.12817 | 122.9095 | 62.677 | 122.731 | 62.7319 | 122.7859 | 0.17853 | 0.091553 | 122.9645 | 122.8912 | 0.10986 | 122.7127 | 62.2787 | 122.6578 | -60.5392 | -122.7631 | 62.2604 | 122.8363 | 62.2925 | 0.53101
2275.8281 | 123.1018 | -62.3245 | 60.3882 | -0.014649 | -0.0016513 | -0.0070687 | 2.8915 | -0.0016663 | -0.00035036 | -0.0035397 | -0.046051 | 0.16288 | 0.12602 | -0.0069982 | 0.055824 | 0.10329 | -0.0025037 | 0.018311 | 0.054932 | -0.054932 | 0 | 0.11444 | 0.018311 | 0.073242 | -61.496 | 60.3516 | -62.3703 | 60.4935 | 60.6216 | 60.4202 | 0.46234 | 62.2696 | -60.3333 | -60.3882 | 62.439 | 62.3978 | 62.3428 | 0.12817 | 0.073243 | -0.045776 | -0.036622 | 0.10528 | 122.9462 | 62.7869 | 122.7448 | 62.8326 | 122.7905 | 0.16937 | 0.054932 | 122.9919 | 122.8638 | 0.10986 | 122.7219 | 62.3795 | 122.6761 | -60.4431 | -122.7585 | 62.3245 | 122.818 | 62.3428 | 0.82855
2276.8906 | 123.0972 | -62.3108 | 60.3836 | -0.052796 | -0.0027195 | -0.0072825 | 2.8933 | 0.0032471 | -0.0033412 | -0.0022581 | -0.12845 | 0.16523 | 0.12516 | -0.0018712 | 0.055183 | 0.10479 | -0.0050671 | -0.082397 | -0.018311 | -0.16022 | -0.054932 | 0.032043 | -0.09613 | -0.050354 | -61.7569 | 60.3333 | -62.3611 | 60.5255 | 60.5667 | 60.3836 | 0.37079 | 62.1506 | -60.4019 | -60.4385 | 62.3428 | 62.2604 | 62.2147 | 0.10986 | 0.064087 | -0.050354 | -0.050354 | 0.14191 | 122.8775 | 62.6816 | 122.6944 | 62.7319 | 122.7448 | 0.19226 | 0.10528 | 122.9279 | 122.8867 | 0.14191 | 122.6944 | 62.2925 | 122.644 | -60.5438 | -122.7448 | 62.2559 | 122.8363 | 62.2284 | 0.55389
2277.8281 | 123.0606 | -62.3016 | 60.4019 | -0.007019 | -0.0025059 | -0.0092051 | 2.8924 | 0.0013245 | -0.0024866 | -0.0039671 | -0.049103 | 0.1616 | 0.12645 | -0.0067846 | 0.057319 | 0.10222 | -0.0014355 | -0.036621 | 0.032043 | -0.086975 | -0.013733 | 0.09613 | -0.004578 | 0.050354 | -62.1231 | 60.379 | -62.3657 | 60.5164 | 60.6125 | 60.4385 | 0.43945 | 62.2147 | -60.3699 | -60.4156 | 62.3978 | 62.352 | 62.2971 | 0.13733 | 0.082397 | -0.064087 | -0.022889 | 0.11444 | 122.9141 | 62.7411 | 122.7402 | 62.8052 | 122.8043 | 0.1831 | 0.073242 | 122.9782 | 122.8821 | 0.11902 | 122.7448 | 62.3337 | 122.6807 | -60.4889 | -122.7676 | 62.2879 | 122.818 | 62.265 | 0.17853
2278.8906 | 123.056 | -62.3199 | 60.3745 | -0.052796 | -0.0010105 | -0.0062143 | 2.8943 | -0.0014527 | -0.00035036 | -0.0024717 | -0.14371 | 0.16459 | 0.12944 | -0.00080325 | 0.054756 | 0.10479 | -0.0020765 | -0.086975 | -0.009155 | -0.14191 | -0.11444 | -0.018311 | -0.14648 | -0.073242 | -62.1094 | 60.3561 | -62.3703 | 60.498 | 60.5621 | 60.3745 | 0.36163 | 62.178 | -60.3836 | -60.4889 | 62.3016 | 62.2467 | 62.1735 | 0.068665 | -0.004577 | -0.050354 | -0.018311 | 0.1236 | 122.8821 | 62.6816 | 122.6944 | 62.7319 | 122.7448 | 0.1236 | 0.027466 | 122.9324 | 122.8683 | 0.13275 | 122.7264 | 62.3108 | 122.6761 | -60.5164 | -122.7448 | 62.2055 | 122.818 | 62.233 | 0.21057
2279.8281 | 123.0835 | -62.3245 | 60.3836 | -0.045166 | -0.0025059 | -0.0089913 | 2.8911 | -0.0010253 | -0.00013676 | -0.0046079 | -0.085724 | 0.16352 | 0.12858 | -0.0033666 | 0.057533 | 0.105 | -0.00036747 | 0.054932 | 0.059509 | -0.022888 | 0.050354 | 0.17853 | 0.07782 | 0.10071 | -62.1094 | 60.3745 | -62.3337 | 60.4935 | 60.6628 | 60.3378 | 0.43488 | 62.3016 | -60.3241 | -60.3333 | 62.5031 | 62.4252 | 62.4023 | 0.1236 | 0.10071 | -0.009155 | -0.009155 | 0.10986 | 122.9874 | 62.7594 | 122.6624 | 62.7686 | 122.6715 | 0.20142 | 0.073242 | 122.9965 | 122.8271 | 0.082397 | 122.7081 | 62.384 | 122.699 | -60.4065 | -122.7173 | 62.3749 | 122.818 | 62.3795 | 0.21515
2280.8906 | 122.9782 | -62.3428 | 60.4523 | -0.083313 | 0.0017667 | -0.0074961 | 2.8937 | -0.00017091 | -0.00505 | -0.0014035 | -0.16507 | 0.1648 | 0.12794 | 0.0011194 | 0.055397 | 0.10628 | -0.0044263 | -0.55847 | 0 | -0.20599 | -0.036621 | -0.091553 | -0.17853 | -0.068665 | -62.4619 | 60.4156 | -62.384 | 60.4248 | 60.4706 | 60.2829 | 0.29755 | 62.1368 | -60.4523 | -60.4889 | 62.2513 | 62.2742 | 62.1643 | 0.13733 | 0.027466 | -0.041199 | -0.036622 | -0.027466 | 122.8134 | 62.6404 | 122.6257 | 62.6816 | 122.6669 | 0.11444 | 0.16937 | 122.8546 | 122.8088 | 0.20599 | 122.7997 | 62.3428 | 122.7585 | -60.6583 | -122.8363 | 62.3062 | 122.7676 | 61.7844 | -0.11902
2281.8281 | 123.0789 | -62.2971 | 60.4111 | -0.007019 | -0.0020785 | -0.010914 | 2.8926 | -0.0033753 | -0.00099116 | -0.0024717 | -0.058258 | 0.16288 | 0.1273 | -0.0074254 | 0.056251 | 0.10415 | -0.0027173 | -0.009155 | 0.064087 | -0.064087 | 0.009155 | 0.10529 | 0.004578 | 0.07782 | -62.3291 | 60.3973 | -62.352 | 60.5255 | 60.6125 | 60.4431 | 0.46692 | 62.233 | -60.347 | -60.4019 | 62.4023 | 62.3749 | 62.3016 | 0.14191 | 0.068665 | -0.054932 | -0.013733 | 0.11444 | 122.9095 | 62.764 | 122.7402 | 62.8189 | 122.7951 | 0.16937 | 0.073242 | 122.9645 | 122.8775 | 0.12817 | 122.7493 | 62.3611 | 122.6944 | -60.4752 | -122.7631 | 62.3062 | 122.8226 | 62.2879 | -0.032044
2282.8281 | 123.0331 | -62.3337 | 60.4202 | -0.083313 | -0.0025059 | -0.0087777 | 2.8913 | 0.0032471 | 0.0017858 | -0.0016171 | -0.07962 | 0.1616 | 0.12751 | -0.0093482 | 0.05326 | 0.10244 | -0.0027173 | -0.045776 | 0.018311 | -0.086975 | 0.14191 | -0.018311 | -0.17395 | -0.018311 | -62.3795 | 60.3607 | -62.3611 | 60.4797 | 60.5484 | 60.3836 | 0.3891 | 62.2467 | -60.4019 | -60.2783 | 62.3154 | 62.3154 | 62.1597 | 0.068664 | -0.086975 | -0.027466 | -0.059509 | 0.059509 | 122.8821 | 62.7228 | 122.7173 | 62.7502 | 122.7448 | 0.068664 | 0.22888 | 122.9095 | 122.8409 | 0.10529 | 122.7219 | 62.352 | 122.6944 | -60.5072 | -122.7814 | 62.4756 | 122.8134 | 62.2879 | -0.045777
2283.8906 | 122.9416 | -62.352 | 60.434 | -0.014649 | 0.00027134 | -0.010059 | 2.8952 | 0.0036743 | -0.0035548 | -0.00097627 | -0.18033 | 0.1648 | 0.1258 | 0.00047855 | 0.053688 | 0.105 | 0.0011279 | -0.12817 | 0.032043 | -0.16937 | -0.16937 | -0.091553 | -0.20599 | -0.13275 | -62.5031 | 60.3836 | -62.3703 | 60.379 | 60.4614 | 60.347 | 0.32501 | 62.1826 | -60.4019 | -60.6033 | 62.2604 | 62.2192 | 62.146 | 0.036622 | -0.036621 | -0.01831 | -0.050354 | -0.054932 | 122.8134 | 62.677 | 122.699 | 62.6953 | 122.7173 | 0.07782 | 0 | 122.8317 | 122.7493 | 0.20142 | 122.7539 | 62.384 | 122.7356 | -60.6033 | -122.8043 | 62.1826 | 122.731 | 62.2238 | -0.15106
2284.8281 | 123.0331 | -62.3337 | 60.434 | -0.045166 | 5.7742e-05 | -0.0077097 | 2.8907 | 0.0011109 | -0.00035036 | -0.00012167 | -0.091827 | 0.16181 | 0.12837 | -0.0018712 | 0.056678 | 0.10372 | -0.00015387 | -0.068665 | -0.036621 | -0.10529 | -0.068665 | 0.036621 | -0.10529 | -0.018311 | -62.471 | 60.3378 | -62.3566 | 60.4523 | 60.5301 | 60.3745 | 0.32501 | 62.2284 | -60.4706 | -60.5026 | 62.3703 | 62.3154 | 62.2284 | 0.086975 | 0 | -0.022888 | -0.09613 | 0.018311 | 122.8638 | 62.6587 | 122.7081 | 62.6816 | 122.731 | 0.14191 | 0.036621 | 122.8867 | 122.8088 | 0.068665 | 122.6944 | 62.2971 | 122.6715 | -60.5392 | -122.7905 | 62.265 | 122.7859 | 62.265 | -0.13733
2285.8906 | 123.0927 | -62.3199 | 60.4065 | -0.075684 | -0.0027195 | -0.0077097 | 2.8922 | 0.0026063 | -0.0014184 | 0.00051913 | -0.13455 | 0.16267 | 0.12773 | 0.00047855 | 0.054756 | 0.10543 | -0.0042127 | -0.054932 | -0.022888 | -0.12817 | -0.045776 | 0.036621 | -0.10071 | -0.027466 | -62.4207 | 60.3378 | -62.3474 | 60.6216 | 60.3149 | 60.3745 | 0.42572 | 62.1918 | -60.4294 | -60.4523 | 62.3566 | 62.2925 | 62.2192 | 0.10071 | 0.027466 | -0.027466 | -0.068664 | 0.21515 | 122.6349 | 62.7457 | 122.6944 | 62.7731 | 122.7219 | 0.1648 | 0.082398 | 122.6624 | 122.9691 | 0.10529 | 122.6852 | 62.2971 | 122.6578 | -60.5347 | -122.7539 | 62.2742 | 122.9416 | 62.265 | -0.10071
2286.8281 | 123.0194 | -62.3291 | 60.4111 | -0.022278 | -0.00036966 | -0.011341 | 2.8905 | 4.2692e-05 | -0.00013676 | -0.0035397 | -0.097931 | 0.16138 | 0.12773 | -0.003794 | 0.056038 | 0.10244 | 5.9726e-05 | -0.07782 | 0 | -0.10529 | -0.054932 | 0.022888 | -0.07782 | -0.009155 | -62.4893 | 60.3699 | -62.3703 | 60.466 | 60.5667 | 60.3653 | 0.35706 | 62.2238 | -60.4111 | -60.466 | 62.352 | 62.3199 | 62.2513 | 0.096131 | 0.027466 | -0.041198 | -0.041199 | 0.054931 | 122.8958 | 62.6862 | 122.6944 | 62.7274 | 122.7356 | 0.12817 | 0.050354 | 122.937 | 122.8363 | 0.10529 | 122.7402 | 62.3291 | 122.699 | -60.5164 | -122.7814 | 62.2742 | 122.7951 | 62.2513 | -0.16022
2287.8906 | 123.0698 | -62.3245 | 60.3836 | -0.1062 | -0.0012241 | -0.0083505 | 2.8939 | 0.0017517 | -0.0027002 | -0.00054907 | -0.15286 | 0.16416 | 0.12815 | -0.0050756 | 0.054542 | 0.10457 | -0.0010083 | -0.073242 | -0.022888 | -0.13733 | -0.032043 | 0.032043 | -0.11444 | -0.050354 | -62.4252 | 60.3607 | -62.3657 | 60.5164 | 60.5759 | 60.3973 | 0.37994 | 62.1872 | -60.4065 | -60.4156 | 62.3566 | 62.2742 | 62.2101 | 0.086975 | 0.022888 | -0.041199 | -0.022888 | 0.13275 | 122.9004 | 62.7045 | 122.7219 | 62.7457 | 122.7631 | 0.16937 | 0.10529 | 122.9416 | 122.8821 | 0.11444 | 122.7264 | 62.3016 | 122.6852 | -60.5209 | -122.7493 | 62.2925 | 122.8409 | 62.2513 | -0.10071
2288.8281 | 123.024 | -62.3291 | 60.4248 | -0.052796 | -0.00015586 | -0.0089913 | 2.8907 | 0.00068369 | -0.002273 | -0.0026853 | -0.088776 | 0.16331 | 0.12922 | -0.00058965 | 0.058387 | 0.10265 | 0.00070073 | -0.073242 | 0 | -0.11444 | -0.07782 | 0.022888 | -0.07782 | -0.018311 | -62.4939 | 60.3607 | -62.3703 | 60.4797 | 60.5392 | 60.347 | 0.3479 | 62.2147 | -60.4248 | -60.5026 | 62.352 | 62.3108 | 62.2513 | 0.09613 | 0.036621 | -0.041198 | -0.064087 | 0.054931 | 122.8683 | 62.677 | 122.6761 | 62.7182 | 122.7173 | 0.13733 | 0.036621 | 122.9095 | 122.85 | 0.11444 | 122.731 | 62.3291 | 122.6898 | -60.5392 | -122.7951 | 62.2513 | 122.8088 | 62.2559 | -0.16479
2289.8906 | 123.0057 | -62.3199 | 60.4156 | 0.00061049 | -0.0018649 | -0.0085641 | 2.893 | 0.0013245 | -0.0027002 | -0.0035397 | -0.18643 | 0.16523 | 0.12709 | 0.00090575 | 0.054756 | 0.10479 | -0.0016493 | 0.009155 | 0.10529 | -0.059509 | -0.022888 | 0.054932 | -0.050354 | 0.004578 | -62.4573 | 60.4111 | -62.3566 | 60.466 | 60.5347 | 60.3378 | 0.41657 | 62.2604 | -60.3104 | -60.4385 | 62.3749 | 62.3245 | 62.2696 | 0.064087 | 0.009155 | -0.036621 | -0.004577 | 0.050354 | 122.8546 | 62.7365 | 122.6578 | 62.7731 | 122.6944 | 0.11444 | 0.036621 | 122.8912 | 122.8226 | 0.16479 | 122.7676 | 62.4252 | 122.731 | -60.4752 | -122.7722 | 62.2971 | 122.7859 | 62.3291 | -0.13733
2290.8281 | 123.0148 | -62.3291 | 60.3973 | -0.052796 | -0.0010105 | -0.0085641 | 2.8924 | 0.0013245 | -0.002273 | -0.00076267 | -0.088776 | 0.16224 | 0.1273 | 0.00026495 | 0.057106 | 0.10393 | -0.0016493 | -0.054932 | -0.022888 | -0.10071 | -0.059509 | 0.045776 | -0.086975 | -0.032043 | -62.4481 | 60.3516 | -62.3566 | 60.4706 | 60.5392 | 60.3699 | 0.33417 | 62.2284 | -60.4202 | -60.4568 | 62.3749 | 62.2971 | 62.2421 | 0.068665 | 0.013733 | -0.027465 | -0.045777 | 0.073242 | 122.8683 | 62.6633 | 122.699 | 62.6907 | 122.7264 | 0.14648 | 0.041199 | 122.8958 | 122.8271 | 0.07782 | 122.7081 | 62.3062 | 122.6807 | -60.498 | -122.7539 | 62.2696 | 122.7997 | 62.2742 | -0.11902
2291.9062 | 123.0103 | -62.2971 | 60.4385 | -0.029907 | -0.0020785 | -0.0098459 | 2.893 | 4.2692e-05 | -0.0027002 | -0.0020443 | -0.082672 | 0.16288 | 0.1305 | -0.00016245 | 0.055824 | 0.10393 | 0.0021961 | 0.050354 | 0.082397 | -0.041199 | 0.050354 | 0.13275 | 0.050354 | 0.091553 | -62.4069 | 60.3882 | -62.3199 | 60.4889 | 60.5942 | 60.3973 | 0.47607 | 62.2559 | -60.3561 | -60.3882 | 62.4298 | 62.3886 | 62.3474 | 0.13275 | 0.091553 | -0.022888 | -0.050354 | 0.050354 | 122.8912 | 62.7731 | 122.6944 | 62.796 | 122.7173 | 0.17395 | 0.091553 | 122.9141 | 122.8088 | 0.1236 | 122.7081 | 62.3795 | 122.6852 | -60.4797 | -122.7585 | 62.3474 | 122.7859 | 62.3474 | -0.10986
2292.8281 | 123.0331 | -62.3154 | 60.4065 | -0.052796 | -0.0016513 | -0.0081369 | 2.8909 | 0.0023925 | 7.6842e-05 | -0.00033547 | -0.07962 | 0.16202 | 0.12709 | 0.00069215 | 0.056892 | 0.10415 | 5.9726e-05 | -0.068665 | 0.018311 | -0.09613 | -0.091553 | 0.036621 | -0.068665 | -0.027466 | -62.4847 | 60.379 | -62.3932 | 60.466 | 60.5392 | 60.3699 | 0.36163 | 62.2192 | -60.3882 | -60.498 | 62.352 | 62.2879 | 62.2467 | 0.068664 | 0.027465 | -0.077819 | -0.027466 | 0.059509 | 122.8546 | 62.677 | 122.6852 | 62.7548 | 122.7631 | 0.13275 | 0.004577 | 122.9324 | 122.8592 | 0.11444 | 122.7722 | 62.3337 | 122.6944 | -60.5026 | -122.7997 | 62.2238 | 122.7814 | 62.2467 | -0.16937
2293.8906 | 122.9736 | -62.3383 | 60.4385 | -0.068054 | -0.0018649 | -0.010487 | 2.8924 | 0.00089729 | -0.0012048 | 0.0011599 | -0.16812 | 0.16331 | 0.12751 | 0.003683 | 0.05561 | 0.10265 | -0.0012219 | -0.10071 | 0.032043 | -0.14191 | -0.16022 | -0.10986 | -0.1831 | -0.10529 | -62.8052 | 60.3516 | -62.4298 | 60.4752 | 60.4065 | 60.2783 | 0.30212 | 62.1963 | -60.4065 | -60.5988 | 62.2284 | 62.233 | 62.1552 | 0.036621 | -0.041198 | -0.091553 | -0.086976 | 0.036621 | 122.7448 | 62.6404 | 122.6166 | 62.7319 | 122.7081 | 0.032044 | -0.01831 | 122.8363 | 122.905 | 0.17395 | 122.7814 | 62.3703 | 122.6898 | -60.5804 | -122.8683 | 62.178 | 122.8134 | 62.2375 | -0.46692
2294.8281 | 123.0194 | -62.3337 | 60.4019 | -0.075684 | 0.00027134 | -0.0098459 | 2.8911 | -0.00059811 | -0.0033412 | -0.0035397 | -0.094879 | 0.16416 | 0.12837 | -0.0061438 | 0.056251 | 0.10286 | -0.00015387 | -0.086975 | -0.013733 | -0.12817 | -0.07782 | 0.013733 | -0.082397 | -0.032043 | -62.4802 | 60.3378 | -62.3703 | 60.4752 | 60.5438 | 60.3653 | 0.33417 | 62.2055 | -60.4156 | -60.4797 | 62.3474 | 62.3016 | 62.2513 | 0.096131 | 0.045777 | -0.036621 | -0.064087 | 0.073242 | 122.8775 | 62.6678 | 122.699 | 62.7045 | 122.7356 | 0.14191 | 0.050354 | 122.9141 | 122.8455 | 0.11444 | 122.7081 | 62.3199 | 122.6715 | -60.5301 | -122.7722 | 62.2559 | 122.8088 | 62.2467 | -0.14649
2295.8281 | 123.0606 | -62.3245 | 60.434 | -0.022278 | -0.0027195 | -0.010273 | 2.8913 | 0.00025629 | -0.00077756 | -0.0014035 | -0.076569 | 0.16309 | 0.1288 | -0.0078528 | 0.055397 | 0.10286 | -0.0031445 | -0.041199 | 0.032043 | -0.073242 | -0.032043 | 0.059509 | -0.036621 | 0.004578 | -62.4619 | 60.3607 | -62.352 | 60.5072 | 60.585 | 60.4156 | 0.4303 | 62.2513 | -60.4019 | -60.466 | 62.384 | 62.3291 | 62.2879 | 0.07782 | 0.036621 | -0.027466 | -0.073242 | 0.073242 | 122.9095 | 62.7548 | 122.7402 | 62.7823 | 122.7676 | 0.13275 | 0.041199 | 122.937 | 122.8592 | 0.10529 | 122.7127 | 62.3566 | 122.6852 | -60.5072 | -122.7859 | 62.2925 | 122.8317 | 62.2833 | -0.13733
2296.9062 | 123.0057 | -62.3291 | 60.4523 | -0.060425 | -0.0016513 | -0.0092051 | 2.893 | -0.0023071 | -0.002273 | -0.0024717 | -0.11929 | 0.1648 | 0.12602 | -0.00058965 | 0.053688 | 0.10265 | -0.00079467 | 0.059509 | 0.068665 | -0.018311 | 0.036621 | 0.14648 | 0.041199 | 0.086975 | -62.4298 | 60.3973 | -62.3291 | 60.498 | 60.5667 | 60.4156 | 0.48065 | 62.3108 | -60.3836 | -60.4157 | 62.4756 | 62.4161 | 62.3703 | 0.10529 | 0.05951 | 0 | -0.054932 | 0.045776 | 122.8958 | 62.8098 | 122.7448 | 62.8098 | 122.7448 | 0.16479 | 0.054932 | 122.8958 | 122.8271 | 0.086976 | 122.7264 | 62.3978 | 122.7264 | -60.4706 | -122.7814 | 62.3657 | 122.8271 | 62.3886 | -0.10071
2297.8281 | 123.0743 | -62.2971 | 60.4248 | -0.007019 | -0.0025059 | -0.0089913 | 2.893 | 0.0045289 | -0.0014184 | -0.0050351 | -0.070465 | 0.16096 | 0.12751 | -0.00828 | 0.056892 | 0.10457 | -0.00015387 | 0.027466 | 0.068665 | -0.041199 | 0.054932 | 0.18768 | 0.068665 | 0.11902 | -62.3337 | 60.3653 | -62.3428 | 60.5392 | 60.6354 | 60.466 | 0.50354 | 62.2559 | -60.3561 | -60.3699 | 62.4847 | 62.4161 | 62.3657 | 0.16022 | 0.10986 | -0.045776 | -0.05951 | 0.11444 | 122.9324 | 62.8006 | 122.7631 | 62.8464 | 122.8088 | 0.22888 | 0.096131 | 122.9782 | 122.8821 | 0.10986 | 122.7081 | 62.3657 | 122.6624 | -60.466 | -122.7676 | 62.352 | 122.8363 | 62.3245 | -0.036621
2298.8906 | 122.9553 | -62.3337 | 60.4523 | -0.014649 | -0.0014377 | -0.0077097 | 2.8935 | 0.0030335 | -0.0027002 | -0.0028989 | -0.20474 | 0.16566 | 0.12858 | 0.0017602 | 0.054329 | 0.10286 | -0.0020765 | -0.10529 | 0.018311 | -0.15106 | -0.15106 | -0.10071 | -0.20142 | -0.1236 | -62.5717 | 60.4019 | -62.3795 | 60.4935 | 60.4019 | 60.3745 | 0.36621 | 62.1826 | -60.434 | -60.6033 | 62.233 | 62.2101 | 62.1323 | 0.027466 | -0.050354 | -0.045777 | -0.050354 | 0.041198 | 122.7356 | 62.6999 | 122.7081 | 62.7457 | 122.7539 | 0.050354 | 0 | 122.7814 | 122.8729 | 0.16937 | 122.7814 | 62.352 | 122.7356 | -60.6033 | -122.8317 | 62.1826 | 122.8271 | 62.2284 | -0.23804
2299.8281 | 123.1064 | -62.3108 | 60.4202 | -0.045166 | -0.0029331 | -0.0079233 | 2.8909 | -0.0016663 | -0.0037684 | -0.0035397 | -0.058258 | 0.16523 | 0.12901 | -0.0018712 | 0.055183 | 0.10222 | -0.0020765 | 0.004578 | 0.068665 | -0.036621 | 0.018311 | 0.13733 | 0.036621 | 0.09613 | -62.3611 | 60.3928 | -62.3199 | 60.553 | 60.64 | 60.4614 | 0.49439 | 62.2742 | -60.3516 | -60.4019 | 62.4481 | 62.4069 | 62.3474 | 0.13275 | 0.073242 | -0.009155 | -0.027466 | 0.13275 | 122.9507 | 62.8052 | 122.7722 | 62.8143 | 122.7814 | 0.17395 | 0.054932 | 122.9599 | 122.8729 | 0.10529 | 122.7127 | 62.3795 | 122.7036 | -60.4568 | -122.7402 | 62.3291 | 122.8638 | 62.3154 | -0.050354
2300.8906 | 122.9553 | -62.3611 | 60.4523 | -0.083313 | 0.00048494 | -0.0089913 | 2.8958 | 0.0028199 | -0.00035036 | 0.0024417 | -0.17422 | 0.16373 | 0.12645 | 0.00069215 | 0.055397 | 0.10479 | 5.9726e-05 | -0.050354 | 0.032043 | -0.11902 | -0.07782 | -0.013733 | -0.13275 | -0.064087 | -62.5351 | 60.4019 | -62.3749 | 60.4248 | 60.4477 | 60.2875 | 0.32044 | 62.2421 | -60.4202 | -60.5301 | 62.3474 | 62.2971 | 62.2284 | 0.054932 | -0.013732 | -0.013733 | -0.050354 | -0.027466 | 122.8088 | 62.6816 | 122.6486 | 62.6953 | 122.6624 | 0.10529 | 0.041199 | 122.8226 | 122.7997 | 0.15106 | 122.7768 | 62.3932 | 122.7631 | -60.5713 | -122.8271 | 62.2833 | 122.7859 | 62.3108 | -0.17395
2301.8438 | 122.9782 | -62.3245 | 60.4797 | -0.045166 | -0.0025059 | -0.0094187 | 2.8935 | 4.2692e-05 | -0.0020594 | 0.00073273 | -0.13455 | 0.16502 | 0.12965 | -0.0033666 | 0.057533 | 0.10735 | -0.00036747 | 0.018311 | 0.11902 | -0.068665 | -0.032043 | 0.050354 | -0.022888 | 0.022888 | -62.5214 | 60.4111 | -62.3566 | 60.4431 | 60.5347 | 60.3287 | 0.4303 | 62.2559 | -60.3607 | -60.5118 | 62.3749 | 62.3474 | 62.3016 | 0.091553 | 0.045777 | -0.032043 | -0.068664 | -0.036621 | 122.8592 | 62.7548 | 122.6532 | 62.7869 | 122.6852 | 0.11902 | 0.036622 | 122.8912 | 122.7997 | 0.18768 | 122.7676 | 62.4435 | 122.7356 | -60.5484 | -122.8363 | 62.2925 | 122.7676 | 62.3428 | -0.19684
2302.8281 | 123.0377 | -62.3154 | 60.4019 | -0.075684 | -0.00036966 | -0.010914 | 2.8915 | 0.0017517 | -0.0012048 | -0.0014035 | -0.055206 | 0.1616 | 0.12645 | -0.00016245 | 0.056892 | 0.10308 | -0.0050671 | -0.086975 | 0.013733 | -0.10986 | -0.086975 | 0.022888 | -0.10986 | -0.045776 | -62.4985 | 60.3745 | -62.3703 | 60.4568 | 60.553 | 60.3607 | 0.36621 | 62.2055 | -60.3882 | -60.4889 | 62.3383 | 62.2696 | 62.2055 | 0.064087 | 0 | -0.054931 | -0.027466 | 0.054931 | 122.8683 | 62.6816 | 122.6761 | 62.7365 | 122.731 | 0.13275 | 0.022888 | 122.9233 | 122.8271 | 0.1236 | 122.7448 | 62.3291 | 122.6898 | -60.5118 | -122.7722 | 62.2284 | 122.7722 | 62.2284 | -0.18311
2303.8906 | 122.9736 | -62.352 | 60.466 | -0.045166 | 5.7742e-05 | -0.0077097 | 2.8939 | 0.0026063 | -0.00099116 | -0.0046079 | -0.18643 | 0.16523 | 0.1273 | -0.00037605 | 0.05561 | 0.10671 | -0.0031445 | -0.059509 | 0.059509 | -0.11902 | -0.11444 | -0.041199 | -0.14648 | -0.082397 | -62.5626 | 60.4248 | -62.4161 | 60.3973 | 60.4477 | 60.2646 | 0.32501 | 62.233 | -60.4065 | -60.5804 | 62.3108 | 62.2696 | 62.2055 | 0.036622 | -0.027465 | -0.064087 | -0.041198 | -0.068664 | 122.7997 | 62.677 | 122.6166 | 62.7411 | 122.6807 | 0.07782 | 0.004578 | 122.8638 | 122.8134 | 0.17853 | 122.8409 | 62.4115 | 122.7768 | -60.585 | -122.8821 | 62.2375 | 122.7493 | 62.2925 | -0.21057
2304.8281 | 123.0331 | -62.3245 | 60.4523 | -0.014649 | -0.00079686 | -0.0074961 | 2.8911 | -0.0010253 | 0.00029044 | -0.0050351 | -0.036896 | 0.16566 | 0.12751 | -0.0063574 | 0.052833 | 0.1035 | 0.0015551 | -0.059509 | 0.018311 | -0.09613 | -0.068665 | 0.022888 | -0.068665 | 0.004578 | -62.4756 | 60.3607 | -62.3703 | 60.466 | 60.5576 | 60.3607 | 0.3891 | 62.2284 | -60.434 | -60.5209 | 62.3474 | 62.3291 | 62.2559 | 0.10071 | 0.027465 | -0.045776 | -0.091553 | 0.013732 | 122.8821 | 62.7136 | 122.6852 | 62.7594 | 122.731 | 0.11902 | 0.027465 | 122.9279 | 122.8363 | 0.11444 | 122.731 | 62.3428 | 122.6852 | -60.5484 | -122.8226 | 62.2559 | 122.7905 | 62.265 | -0.15106
2305.8906 | 123.0606 | -62.3108 | 60.4156 | -0.31982 | 0.0015529 | -0.0072825 | 2.8907 | 0.00089729 | 0.001145 | -0.0016171 | -0.12234 | 0.1616 | 0.12773 | -0.00828 | 0.054115 | 0.10415 | 5.9726e-05 | -0.009155 | -0.07782 | -0.15106 | -0.041199 | 0.1236 | -0.073242 | -0.045776 | -62.4252 | 60.3333 | -62.3337 | 60.5118 | 60.5759 | 60.3928 | 0.37079 | 62.1597 | -60.4935 | -60.4568 | 62.4344 | 62.265 | 62.2375 | 0.10529 | 0.07782 | -0.022888 | -0.082397 | 0.096131 | 122.8867 | 62.6816 | 122.7036 | 62.7045 | 122.7264 | 0.27466 | 0.10986 | 122.9095 | 122.8455 | 0.073242 | 122.6669 | 62.233 | 122.644 | -60.5667 | -122.7493 | 62.2696 | 122.8226 | 62.3016 | -0.11444
2306.8438 | 123.0698 | -62.3154 | 60.4477 | -0.022278 | -0.0016513 | -0.0107 | 2.8924 | 0.00068369 | -0.0035548 | -0.0011899 | -0.10098 | 0.16544 | 0.12837 | -0.0095618 | 0.054756 | 0.10308 | -0.0012219 | 0.032043 | 0.068665 | -0.013733 | 0.16022 | 0.054932 | -0.082397 | 0.10986 | -62.3657 | 60.3882 | -62.3383 | 60.5255 | 60.6079 | 60.4477 | 0.48065 | 62.3016 | -60.379 | -60.2875 | 62.3703 | 62.4252 | 62.233 | 0.1236 | -0.068664 | -0.022888 | -0.059509 | 0.07782 | 122.9233 | 62.796 | 122.7631 | 62.8189 | 122.7859 | 0.068665 | 0.17395 | 122.9462 | 122.8638 | 0.082398 | 122.7264 | 62.384 | 122.7036 | -60.4614 | -122.7859 | 62.4756 | 122.8409 | 62.3474 | -0.050354
2307.8906 | 123.0469 | -62.3474 | 60.466 | -0.15198 | 0.00069854 | -0.0085641 | 2.8965 | 0.0028199 | -0.0020594 | -0.0020443 | -0.18033 | 0.16566 | 0.12858 | -0.0057166 | 0.054329 | 0.10457 | -0.0010083 | -0.13275 | 0.045776 | -0.16479 | -0.15106 | -0.10071 | -0.16937 | -0.11444 | -62.5717 | 60.3836 | -62.3932 | 60.498 | 60.1547 | 60.0998 | 0.25635 | 62.1826 | -60.4202 | -60.6171 | 62.2467 | 62.233 | 62.178 | 0.050354 | -0.004578 | -0.045776 | -0.082397 | 0.032044 | 122.5021 | 62.6038 | 122.4472 | 62.6495 | 122.493 | 0.064087 | 0.013733 | 122.5479 | 122.8912 | 0.21057 | 122.7768 | 62.3932 | 122.731 | -60.6308 | -122.8592 | 62.1963 | 122.8455 | 62.2147 | -0.2243
2308.8281 | 123.0698 | -62.3154 | 60.3928 | -0.075684 | -0.0014377 | -0.0068551 | 2.8924 | 0.0019653 | 0.0013586 | -0.0018307 | -0.10709 | 0.16331 | 0.12858 | 0.0026148 | 0.053901 | 0.10415 | -0.0059217 | -0.036621 | -0.041199 | -0.14648 | 0.041199 | 0.11902 | -0.068665 | 0.013733 | -62.4161 | 60.3378 | -62.3383 | 60.5164 | 60.5667 | 60.379 | 0.36163 | 62.1689 | -60.434 | -60.3516 | 62.4344 | 62.3291 | 62.2467 | 0.16022 | 0.077819 | -0.022888 | -0.054931 | 0.1236 | 122.8821 | 62.677 | 122.6944 | 62.6999 | 122.7173 | 0.2655 | 0.18768 | 122.905 | 122.8546 | 0.10529 | 122.6761 | 62.2742 | 122.6532 | -60.5392 | -122.731 | 62.3566 | 122.8317 | 62.2787 | -0.10071
2309.8906 | 122.9324 | -62.3749 | 60.4248 | -0.029907 | 0.00069854 | -0.0085641 | 2.8911 | 0.0013245 | -0.0012048 | -0.00054907 | -0.16507 | 0.16437 | 0.12687 | -0.0010168 | 0.054115 | 0.10671 | 5.9726e-05 | -0.082397 | 0.041199 | -0.13733 | -0.13275 | -0.064087 | -0.19684 | -0.14191 | -62.5809 | 60.4111 | -62.384 | 60.3973 | 60.4248 | 60.2417 | 0.3067 | 62.2375 | -60.3836 | -60.5576 | 62.3108 | 62.233 | 62.178 | -0.004578 | -0.059509 | -0.009155 | -0.013733 | -0.027466 | 122.7997 | 62.6816 | 122.6166 | 62.6907 | 122.6257 | 0.073242 | 0.004578 | 122.8088 | 122.7814 | 0.17853 | 122.7951 | 62.4161 | 122.7859 | -60.5621 | -122.8088 | 62.2421 | 122.7722 | 62.2925 | -0.20599
2310.8281 | 123.0194 | -62.3108 | 60.4019 | -0.13672 | -0.0014377 | -0.0081369 | 2.8928 | 0.00089729 | -0.0014184 | -0.0016171 | -0.088776 | 0.16416 | 0.1273 | -0.00016245 | 0.054969 | 0.10393 | -0.00036747 | -0.045776 | 0.018311 | -0.09613 | -0.054932 | 0.054932 | -0.073242 | -0.018311 | -62.4435 | 60.3424 | -62.3566 | 60.5072 | 60.5438 | 60.3745 | 0.35248 | 62.2147 | -60.3836 | -60.4568 | 62.3657 | 62.2925 | 62.2375 | 0.077819 | 0.022888 | -0.045776 | -0.05951 | 0.10529 | 122.8546 | 62.6633 | 122.6852 | 62.709 | 122.731 | 0.15106 | 0.041198 | 122.9004 | 122.8638 | 0.11444 | 122.699 | 62.3291 | 122.6532 | -60.498 | -122.7585 | 62.2559 | 122.818 | 62.265 | -0.13275
2311.8906 | 123.0606 | -62.3154 | 60.3928 | -0.12909 | -0.00036966 | -0.0092051 | 2.8943 | 0.0023925 | -0.0018458 | -0.0016171 | -0.091827 | 0.16224 | 0.12666 | 0.0034692 | 0.054115 | 0.10521 | -0.0018629 | -0.068665 | -0.022888 | -0.1236 | -0.054932 | 0.054932 | -0.07782 | -0.018311 | -62.5763 | 60.3241 | -62.3886 | 60.5484 | 60.5484 | 60.4156 | 0.40741 | 62.1918 | -60.4156 | -60.4477 | 62.3703 | 62.2971 | 62.2375 | 0.10528 | 0.045776 | -0.073242 | -0.068664 | 0.15564 | 122.8638 | 62.7228 | 122.731 | 62.796 | 122.8043 | 0.17853 | 0.068664 | 122.937 | 122.937 | 0.10071 | 122.7127 | 62.2925 | 122.6395 | -60.5164 | -122.7814 | 62.2604 | 122.8638 | 62.2467 | -0.26093
2312.8281 | 122.9828 | -62.3062 | 60.4706 | -0.007019 | 0.00027134 | -0.0087777 | 2.8924 | 0.0026063 | -0.002273 | 0.00094633 | -0.11929 | 0.16267 | 0.12773 | -0.0018712 | 0.055183 | 0.10393 | 0.0013415 | 0.013733 | 0.11444 | -0.054932 | -0.032043 | 0.054932 | -0.018311 | 0.032043 | -62.5397 | 60.434 | -62.384 | 60.4477 | 60.5255 | 60.3378 | 0.42572 | 62.2513 | -60.3561 | -60.5026 | 62.3611 | 62.3383 | 62.2879 | 0.086975 | 0.036621 | -0.07782 | -0.036621 | -0.022888 | 122.8317 | 62.7319 | 122.644 | 62.8098 | 122.7219 | 0.10986 | 0.022889 | 122.9095 | 122.8317 | 0.16937 | 122.818 | 62.4207 | 122.7402 | -60.5255 | -122.8546 | 62.2742 | 122.7539 | 62.3199 | -0.23346
2313.8906 | 122.9874 | -62.3245 | 60.4294 | -0.060425 | -0.00036966 | -0.0085641 | 2.8943 | 0.00089729 | -0.0024866 | -0.0020443 | -0.14981 | 0.16502 | 0.12965 | -0.0029394 | 0.056251 | 0.10521 | -0.0059217 | -0.036621 | 0.073242 | -0.086975 | -0.091553 | -0.004578 | -0.1236 | -0.054932 | -62.5305 | 60.4248 | -62.3657 | 60.4248 | 60.4706 | 60.2692 | 0.33417 | 62.2375 | -60.3561 | -60.5209 | 62.3199 | 62.2696 | 62.2009 | 0.032043 | -0.036621 | -0.041199 | -0.004577 | -0.004577 | 122.7951 | 62.6587 | 122.5937 | 62.6999 | 122.6349 | 0.082397 | -0.004578 | 122.8363 | 122.7905 | 0.16022 | 122.7905 | 62.3978 | 122.7493 | -60.5164 | -122.7951 | 62.233 | 122.7493 | 62.2879 | -0.20599
2314.8281 | 123.0469 | -62.3016 | 60.3928 | -0.045166 | 0.00048494 | -0.0087777 | 2.892 | -0.0010253 | 0.0013586 | -0.0011899 | -0.064362 | 0.16309 | 0.13029 | -0.001444 | 0.056251 | 0.10265 | -0.0050671 | -0.059509 | -0.045776 | -0.12817 | -0.054932 | 0.041199 | -0.068665 | -0.013733 | -62.59 | 60.3104 | -62.3703 | 60.5438 | 60.5438 | 60.4156 | 0.3891 | 62.1735 | -60.4385 | -60.4477 | 62.3428 | 62.2879 | 62.233 | 0.11444 | 0.059509 | -0.068664 | -0.082397 | 0.15106 | 122.8455 | 62.6907 | 122.7173 | 62.7594 | 122.7859 | 0.16937 | 0.073242 | 122.9141 | 122.9141 | 0.082398 | 122.6807 | 62.2559 | 122.612 | -60.5209 | -122.7631 | 62.2467 | 122.8455 | 62.2421 | -0.28839
2315.8906 | 122.9919 | -62.3474 | 60.4477 | -0.060425 | -0.00079686 | -0.0081369 | 2.8937 | -0.00017091 | -0.00077756 | -0.0035397 | -0.13455 | 0.16416 | 0.12666 | 0.003683 | 0.054969 | 0.10158 | -0.0010083 | -0.10071 | 0.013733 | -0.15106 | -0.17395 | -0.10071 | -0.21515 | -0.1236 | -62.5671 | 60.379 | -62.3932 | 60.5667 | 60.4111 | 60.2875 | 0.32501 | 62.1963 | -60.434 | -60.6216 | 62.2467 | 62.2238 | 62.1323 | 0.027466 | -0.064087 | -0.045776 | -0.068665 | 0.11902 | 122.7585 | 62.6724 | 122.6349 | 62.7182 | 122.6807 | 0.050354 | -0.022888 | 122.8043 | 122.9599 | 0.16479 | 122.7722 | 62.3611 | 122.7264 | -60.5988 | -122.8409 | 62.1735 | 122.9141 | 62.2467 | -0.21973
2316.8281 | 123.0698 | -62.3108 | 60.3973 | -0.11383 | -0.00079686 | -0.0083505 | 2.8915 | 0.0019653 | 0.0015722 | -0.0037533 | -0.10709 | 0.16267 | 0.12623 | -0.0069982 | 0.054542 | 0.10585 | -0.0018629 | -0.041199 | -0.050354 | -0.13733 | -0.086975 | 0.027466 | -0.086975 | -0.041199 | -62.439 | 60.3561 | -62.3428 | 60.5301 | 60.5713 | 60.3928 | 0.37994 | 62.1735 | -60.4477 | -60.4843 | 62.3383 | 62.2696 | 62.2238 | 0.09613 | 0.050354 | -0.032043 | -0.041199 | 0.13275 | 122.8821 | 62.6907 | 122.7036 | 62.7228 | 122.7356 | 0.16479 | 0.050354 | 122.9141 | 122.8729 | 0.086975 | 122.699 | 62.2604 | 122.6669 | -60.5347 | -122.7402 | 62.2238 | 122.8409 | 62.2696 | -0.12817
2317.8281 | 123.0698 | -62.3016 | 60.4385 | -0.022278 | -0.0044285 | -0.011555 | 2.8928 | -0.00081171 | -0.0012048 | -0.0048215 | -0.055206 | 0.16309 | 0.12773 | -0.0035802 | 0.055183 | 0.10244 | -0.0022901 | 0.53101 | 0.12817 | 0.018311 | -0.022888 | 0.20142 | 0.018311 | 0.068665 | -62.4115 | 60.3928 | -62.3428 | 60.5301 | 60.6033 | 60.4385 | 0.52185 | 62.3199 | -60.3104 | -60.4614 | 62.5031 | 62.3703 | 62.3199 | 0.050354 | 0 | -0.041198 | -0.045777 | 0.091552 | 122.905 | 62.8235 | 122.7402 | 62.8647 | 122.7814 | 0.18311 | -0.041199 | 122.9462 | 122.8729 | 0.10986 | 122.7356 | 62.4298 | 122.6944 | -60.4202 | -122.7814 | 62.2787 | 122.8317 | 62.8326 | -0.10986
2318.8906 | 123.0148 | -62.352 | 60.3836 | -0.052796 | -0.0014377 | -0.0083505 | 2.8926 | 0.0041015 | -0.0020594 | -0.0018307 | -0.1376 | 0.16459 | 0.12751 | -0.0018712 | 0.054542 | 0.10756 | -0.0018629 | -0.11444 | 0.022888 | -0.14648 | -0.13275 | -0.059509 | -0.17853 | -0.091553 | -62.5031 | 60.3424 | -62.384 | 60.4843 | 60.5347 | 60.3561 | 0.3479 | 62.2055 | -60.3607 | -60.5164 | 62.2925 | 62.2604 | 62.1735 | 0.054931 | -0.032044 | -0.032043 | -0.041199 | 0.10071 | 122.8867 | 62.6999 | 122.7081 | 62.7319 | 122.7402 | 0.086975 | 0.013733 | 122.9187 | 122.8683 | 0.16937 | 122.7264 | 62.3749 | 122.6944 | -60.5301 | -122.7676 | 62.2192 | 122.8363 | 62.2375 | -0.15106
2319.8281 | 123.0469 | -62.3383 | 60.4111 | -0.045166 | -0.00058326 | -0.0096323 | 2.8907 | -0.0038025 | -0.00056396 | -0.00097627 | -0.064362 | 0.16245 | 0.1273 | -0.004862 | 0.053688 | 0.10286 | 0.00048713 | -0.068665 | -0.009155 | -0.10529 | -0.10071 | -0.004578 | -0.045776 | -0.009155 | -62.4802 | 60.3607 | -62.3474 | 60.4797 | 60.5484 | 60.3699 | 0.37079 | 62.233 | -60.4202 | -60.5118 | 62.3337 | 62.3291 | 62.2925 | 0.096131 | 0.05951 | -0.009155 | -0.050354 | 0.068664 | 122.8867 | 62.709 | 122.7081 | 62.7182 | 122.7173 | 0.10071 | 0.004578 | 122.8958 | 122.8271 | 0.096131 | 122.7081 | 62.3291 | 122.699 | -60.5164 | -122.7585 | 62.2375 | 122.818 | 62.2696 | -0.14191
2320.8906 | 122.9874 | -62.3474 | 60.466 | 0.038757 | -0.0042149 | -0.0092051 | 2.8913 | 0.0030335 | -0.0014184 | -0.0033261 | -0.12234 | 0.16267 | 0.13072 | -0.0010168 | 0.05326 | 0.1065 | 0.0017687 | 0.17395 | 0.21973 | 0.032043 | -0.032043 | -0.018311 | -0.07782 | 0.004578 | -62.5305 | 60.4294 | -62.3703 | 60.4294 | 60.498 | 60.3378 | 0.43488 | 62.3795 | -60.2463 | -60.498 | 62.3291 | 62.352 | 62.2696 | -0.027465 | -0.10986 | -0.022888 | -0.036621 | -0.036621 | 122.8455 | 62.7823 | 122.6852 | 62.8052 | 122.7081 | -0.050354 | -0.064086 | 122.8683 | 122.7997 | 0.18768 | 122.7997 | 62.5671 | 122.7768 | -60.434 | -122.8363 | 62.3154 | 122.7768 | 62.5214 | -0.18311
2321.8281 | 123.0148 | -62.3199 | 60.4477 | -0.068054 | -0.0012241 | -0.0079233 | 2.8926 | -0.00017091 | -0.0027002 | -0.0011899 | -0.058258 | 0.16309 | 0.12687 | -0.0095618 | 0.054329 | 0.10415 | 0.0017687 | -0.041199 | 0.041199 | -0.086975 | -0.064087 | 0.022888 | -0.054932 | 0.022888 | -62.471 | 60.3745 | -62.3383 | 60.4568 | 60.5713 | 60.379 | 0.39825 | 62.233 | -60.4065 | -60.5118 | 62.3428 | 62.3428 | 62.265 | 0.10986 | 0.032043 | -0.018311 | -0.073242 | 0.009155 | 122.8912 | 62.7182 | 122.699 | 62.7365 | 122.7173 | 0.10986 | 0.022888 | 122.9095 | 122.7951 | 0.12817 | 122.7127 | 62.3611 | 122.6944 | -60.5347 | -122.7859 | 62.2559 | 122.7768 | 62.2787 | -0.15106
2322.8906 | 122.9095 | -62.3428 | 60.4523 | -0.098572 | -0.00079686 | -0.0077097 | 2.8945 | 0.0030335 | -0.00099116 | -0.0022581 | -0.17422 | 0.16267 | 0.12709 | -0.00080325 | 0.054542 | 0.10393 | 0.00091433 | -0.11902 | 0.041199 | -0.16937 | -0.14648 | -0.091553 | -0.1831 | -0.11902 | -62.5763 | 60.4065 | -62.384 | 60.3653 | 60.2051 | 60.5484 | 0.48523 | 62.1735 | -60.4111 | -60.5988 | 62.2513 | 62.2238 | 62.1597 | 0.050354 | -0.013732 | -0.041199 | -0.045777 | -0.086976 | 122.5479 | 62.8281 | 122.8912 | 62.8693 | 122.9324 | 0.07782 | 0.022889 | 122.5891 | 122.7493 | 0.21057 | 122.7905 | 62.384 | 122.7493 | -60.6216 | -122.8363 | 62.1964 | 122.7081 | 62.2238 | -0.23346
2323.8281 | 123.0515 | -62.3245 | 60.4111 | -0.1062 | -0.0025059 | -0.0081369 | 2.8911 | -0.0033753 | -0.0054774 | -0.0084531 | -0.058258 | 0.16437 | 0.13008 | -0.0052892 | 0.055824 | 0.1035 | -0.00079467 | -0.050354 | 0.032043 | -0.10529 | -0.07782 | 0.036621 | -0.045776 | 0.018311 | -62.4893 | 60.3882 | -62.3703 | 60.4523 | 60.553 | 60.3699 | 0.37994 | 62.2192 | -60.379 | -60.4889 | 62.3611 | 62.3428 | 62.2787 | 0.1236 | 0.05951 | -0.045776 | -0.022888 | 0.041199 | 122.8775 | 62.7045 | 122.6944 | 62.7502 | 122.7402 | 0.14191 | 0.027466 | 122.9233 | 122.8226 | 0.13733 | 122.7585 | 62.3566 | 122.7127 | -60.5164 | -122.7814 | 62.2467 | 122.7768 | 62.2742 | -0.1648
2324.8906 | 122.9507 | -62.3337 | 60.4568 | -0.075684 | -0.0016513 | -0.0089913 | 2.8941 | 0.0013245 | -0.0033412 | -0.0011899 | -0.17117 | 0.16502 | 0.1258 | -0.00037605 | 0.052833 | 0.10372 | -0.0018629 | -0.059509 | 0.073242 | -0.12817 | -0.086975 | -0.050354 | -0.15106 | -0.10529 | -62.5626 | 60.4156 | -62.4023 | 60.4065 | 60.4431 | 60.2371 | 0.32501 | 62.2055 | -60.3836 | -60.5438 | 62.2833 | 62.2284 | 62.1826 | 0.022888 | -0.022888 | -0.068665 | -0.041199 | -0.050354 | 122.7768 | 62.6587 | 122.5708 | 62.7274 | 122.6395 | 0.07782 | 0.041199 | 122.8455 | 122.8088 | 0.20142 | 122.818 | 62.4069 | 122.7493 | -60.585 | -122.8592 | 62.2467 | 122.7402 | 62.2742 | -0.22888
2325.8281 | 123.0148 | -62.3245 | 60.4111 | -0.022278 | -0.0018649 | -0.0087777 | 2.892 | -0.00059811 | -0.00013676 | -0.0033261 | -0.085724 | 0.1616 | 0.12773 | -0.0022986 | 0.056678 | 0.10372 | -0.0016493 | -0.073242 | -0.013733 | -0.11902 | -0.07782 | 0.004578 | -0.082397 | -0.032043 | -62.4664 | 60.379 | -62.3932 | 60.4706 | 60.5301 | 60.3699 | 0.36163 | 62.2055 | -60.4248 | -60.4889 | 62.3291 | 62.2925 | 62.2421 | 0.086976 | 0.036622 | -0.068664 | -0.032044 | 0.059509 | 122.8546 | 62.6862 | 122.6944 | 62.7548 | 122.7631 | 0.1236 | 0.041199 | 122.9233 | 122.8638 | 0.10529 | 122.7722 | 62.3108 | 122.7036 | -60.5301 | -122.8043 | 62.2467 | 122.7951 | 62.2513 | -0.14191
2326.8906 | 122.9919 | -62.3428 | 60.4385 | -0.037537 | -0.00015586 | -0.0092051 | 2.8943 | -0.0012391 | -0.0041956 | -0.0024717 | -0.14371 | 0.16331 | 0.12858 | -0.003153 | 0.054756 | 0.105 | -0.0025037 | -0.013733 | 0.082397 | -0.091553 | -0.045776 | 0.022888 | -0.086975 | -0.045776 | -62.5076 | 60.4111 | -62.3611 | 60.4523 | 60.4797 | 60.2921 | 0.3479 | 62.2513 | -60.3561 | -60.4843 | 62.3657 | 62.2971 | 62.2559 | 0.045777 | 0.004578 | -0.018311 | -0.027466 | 0.013733 | 122.8226 | 62.6907 | 122.6349 | 62.709 | 122.6532 | 0.11444 | 0.045777 | 122.8409 | 122.8134 | 0.17395 | 122.7722 | 62.4252 | 122.7539 | -60.5301 | -122.7997 | 62.2971 | 122.7951 | 62.3291 | -0.16479
2327.8281 | 123.056 | -62.2925 | 60.4065 | -0.007019 | -0.00036966 | -0.011555 | 2.8913 | -0.0023071 | -0.002273 | -0.0024717 | -0.018585 | 0.16416 | 0.12709 | -0.0044348 | 0.056465 | 0.10265 | -0.0037855 | 0 | 0.027466 | -0.068665 | -0.018311 | 0.11902 | 0.018311 | 0.064087 | -62.4207 | 60.3653 | -62.3245 | 60.5255 | 60.6125 | 60.4431 | 0.4715 | 62.2238 | -60.379 | -60.4248 | 62.4115 | 62.3566 | 62.3108 | 0.13275 | 0.086976 | -0.032044 | -0.041199 | 0.11902 | 122.905 | 62.764 | 122.7356 | 62.796 | 122.7676 | 0.18768 | 0.050354 | 122.937 | 122.85 | 0.096131 | 122.6898 | 62.3199 | 122.6578 | -60.4752 | -122.731 | 62.2742 | 122.818 | 62.2925 | -0.12817
2328.8906 | 123.0377 | -62.3291 | 60.4065 | -0.1062 | -0.00036966 | -0.0079233 | 2.8937 | -0.0010253 | -0.00056396 | -0.0048215 | -0.14371 | 0.1648 | 0.12751 | -0.0035802 | 0.057533 | 0.10521 | -0.0018629 | -0.10529 | 0.032043 | -0.16479 | -0.13275 | -0.050354 | -0.16479 | -0.09613 | -62.5076 | 60.3561 | -62.3703 | 60.4889 | 60.5255 | 60.3424 | 0.3479 | 62.1643 | -60.3745 | -60.5392 | 62.2787 | 62.233 | 62.1643 | 0.068665 | 0 | -0.041198 | -0.050354 | 0.082398 | 122.8546 | 62.677 | 122.6715 | 62.7182 | 122.7127 | 0.11444 | 0.032044 | 122.8958 | 122.8592 | 0.19684 | 122.7264 | 62.3611 | 122.6852 | -60.5713 | -122.7768 | 62.1964 | 122.818 | 62.2238 | -0.17853
2329.8281 | 123.0423 | -62.3245 | 60.4202 | -0.014649 | -0.0027195 | -0.0083505 | 2.8933 | 0.0011109 | -0.00099116 | -0.0033261 | -0.052155 | 0.1648 | 0.12858 | -0.0061438 | 0.057533 | 0.10457 | -0.00015387 | 0.11444 | 0.059509 | -0.086975 | -0.054932 | 0.050354 | -0.036621 | 0 | -62.4664 | 60.3699 | -62.352 | 60.4843 | 60.585 | 60.4156 | 0.42572 | 62.2375 | -60.3607 | -60.4752 | 62.3749 | 62.3245 | 62.2879 | 0.086975 | 0.050354 | -0.027466 | -0.050354 | 0.064087 | 122.9095 | 62.7502 | 122.7402 | 62.7777 | 122.7676 | 0.13733 | 0.032043 | 122.937 | 122.8363 | 0.14648 | 122.7219 | 62.384 | 122.6944 | -60.5072 | -122.7722 | 62.2696 | 122.8088 | 62.439 | -0.14191
2330.8906 | 122.9645 | -62.384 | 60.434 | -0.014649 | 0.0015529 | -0.0079233 | 2.8935 | 0.0023925 | -0.0033412 | -0.0018307 | -0.18033 | 0.1663 | 0.12709 | -0.0035802 | 0.054329 | 0.10585 | 0.0026233 | -0.55389 | -0.009155 | -0.19226 | -0.10986 | -0.12817 | -0.12817 | -0.091553 | -62.5488 | 60.4156 | -62.384 | 60.4294 | 60.4614 | 60.2737 | 0.30212 | 62.1918 | -60.4431 | -60.5438 | 62.2559 | 62.2925 | 62.2559 | 0.10071 | 0.064087 | 0 | -0.018311 | -0.004578 | 122.8455 | 62.6862 | 122.6578 | 62.6862 | 122.6578 | 0.064087 | 0.082398 | 122.8455 | 122.8134 | 0.18311 | 122.7997 | 62.3749 | 122.7997 | -60.6262 | -122.818 | 62.2742 | 122.8134 | 61.8301 | -0.16479
2331.8281 | 123.0789 | -62.3062 | 60.3928 | -0.075684 | -0.0014377 | -0.0087777 | 2.89 | -0.0020935 | -0.00099116 | -0.0011899 | -0.064362 | 0.16331 | 0.1273 | -0.0072118 | 0.054329 | 0.10521 | -0.0020765 | 0.050354 | 0.073242 | -0.036621 | 0.07782 | 0.1831 | 0.073242 | 0.10529 | -62.384 | 60.3607 | -62.3154 | 60.4156 | 60.7498 | 60.3699 | 0.43488 | 62.2696 | -60.3195 | -60.3149 | 62.4893 | 62.4115 | 62.3795 | 0.14191 | 0.10986 | -0.009156 | -0.032043 | 0.022888 | 123.056 | 62.7411 | 122.6761 | 62.7502 | 122.6852 | 0.21973 | 0.11444 | 123.0652 | 122.731 | 0.10986 | 122.6761 | 62.3795 | 122.6669 | -60.4294 | -122.7081 | 62.384 | 122.7219 | 62.3566 | -0.07782
2332.8906 | 123.0286 | -62.3337 | 60.4019 | -0.090943 | -0.0027195 | -0.0079233 | 2.8924 | 0.00025629 | -0.0024866 | -0.00097627 | -0.07962 | 0.16245 | 0.12944 | -0.00080325 | 0.054329 | 0.10308 | 0.0021961 | -0.032043 | 0 | -0.10986 | -0.059509 | 0.073242 | -0.082397 | 0 | -62.4252 | 60.3378 | -62.3428 | 60.498 | 60.5484 | 60.3745 | 0.35248 | 62.2238 | -60.4019 | -60.4614 | 62.4069 | 62.3337 | 62.2513 | 0.10986 | 0.027466 | -0.009155 | -0.064087 | 0.09613 | 122.8821 | 62.6862 | 122.7081 | 62.6953 | 122.7173 | 0.18311 | 0.050354 | 122.8912 | 122.8409 | 0.10986 | 122.6807 | 62.3337 | 122.6715 | -60.5118 | -122.7448 | 62.2742 | 122.8317 | 62.3016 | -0.091553
2333.8281 | 123.1018 | -62.3062 | 60.4294 | 0.00824 | -0.00079686 | -0.0096323 | 2.8918 | -0.0016663 | -0.002273 | -0.0020443 | -0.042999 | 0.16395 | 0.12794 | -0.0074254 | 0.05561 | 0.10393 | 0.0017687 | 0.041199 | 0.064087 | -0.036621 | 0.013733 | 0.16479 | 0.086975 | 0.09613 | -62.3383 | 60.3561 | -62.3428 | 60.5621 | 60.6537 | 60.466 | 0.49439 | 62.2696 | -60.3653 | -60.4156 | 62.471 | 62.4023 | 62.3932 | 0.13275 | 0.1236 | -0.036621 | -0.073242 | 0.13275 | 122.9599 | 62.8006 | 122.7722 | 62.8372 | 122.8088 | 0.20142 | 0.050354 | 122.9965 | 122.905 | 0.10071 | 122.699 | 62.3703 | 122.6624 | -60.466 | -122.7722 | 62.3199 | 122.8683 | 62.3474 | -0.032044
2334.8906 | 123.0835 | -62.3154 | 60.3882 | -0.098572 | -0.00079686 | -0.0068551 | 2.8928 | 0.0041015 | 0.00050424 | -0.00076267 | -0.14676 | 0.16416 | 0.12666 | -0.0022986 | 0.054969 | 0.10436 | -0.0020765 | -0.073242 | -0.032043 | -0.13733 | -0.059509 | 0.032043 | -0.10986 | -0.041199 | -62.4207 | 60.3607 | -62.3795 | 60.5164 | 60.5759 | 60.379 | 0.37994 | 62.178 | -60.4202 | -60.4477 | 62.3474 | 62.2742 | 62.2055 | 0.09613 | 0.027466 | -0.064087 | -0.027466 | 0.12817 | 122.8912 | 62.6953 | 122.6944 | 62.7594 | 122.7585 | 0.16937 | 0.07782 | 122.9553 | 122.8958 | 0.10529 | 122.7402 | 62.2833 | 122.6761 | -60.5255 | -122.7676 | 62.2559 | 122.8317 | 62.2421 | -0.10529
2335.8281 | 123.0652 | -62.3154 | 60.4294 | -0.007019 | -0.0020785 | -0.0092051 | 2.8915 | -0.00038451 | -0.0027002 | -0.0035397 | -0.058258 | 0.16245 | 0.12559 | -0.0033666 | 0.05326 | 0.10393 | -0.00058107 | 0.022888 | 0.064087 | -0.045776 | 0.059509 | 0.19226 | 0.082397 | 0.12817 | -62.3337 | 60.3836 | -62.3291 | 60.5164 | 60.6445 | 60.466 | 0.53101 | 62.2696 | -60.3653 | -60.3699 | 62.5076 | 62.4435 | 62.3978 | 0.17395 | 0.12817 | -0.013733 | -0.045776 | 0.086975 | 122.9599 | 62.8464 | 122.7814 | 62.8601 | 122.7951 | 0.23804 | 0.10528 | 122.9736 | 122.8455 | 0.10986 | 122.7127 | 62.3795 | 122.699 | -60.4752 | -122.7585 | 62.3749 | 122.8317 | 62.3383 | -0.01831
2336.8906 | 123.0789 | -62.3154 | 60.4065 | -0.060425 | 0.00048494 | -0.0074961 | 2.8922 | 0.0049561 | -0.0018458 | -0.0024717 | -0.12845 | 0.16309 | 0.13029 | -0.00058965 | 0.054756 | 0.10308 | -0.00058107 | -0.059509 | -0.022888 | -0.13733 | -0.059509 | 0.022888 | -0.10071 | -0.045776 | -62.4069 | 60.3104 | -62.352 | 60.5255 | 60.5759 | 60.3973 | 0.37537 | 62.178 | -60.4294 | -60.466 | 62.3383 | 62.2696 | 62.2147 | 0.091553 | 0.036621 | -0.036621 | -0.09613 | 0.11902 | 122.8912 | 62.6907 | 122.7127 | 62.7274 | 122.7493 | 0.16022 | 0.07782 | 122.9279 | 122.8775 | 0.11444 | 122.6624 | 62.2925 | 122.6257 | -60.5438 | -122.7585 | 62.2559 | 122.8409 | 62.2559 | -0.091552
2337.8281 | 123.143 | -62.3016 | 60.4248 | -0.075684 | -0.00036966 | -0.0083505 | 2.8892 | -0.0012391 | -0.0024866 | -0.0018307 | -0.082672 | 0.16288 | 0.12751 | -0.0052892 | 0.054329 | 0.1003 | -0.0016493 | 0.068665 | 0.068665 | -0.045776 | 0.045776 | 0.18768 | 0.068665 | 0.10529 | -62.3657 | 60.347 | -62.3245 | 60.6857 | 60.6079 | 60.2051 | 0.37994 | 62.2559 | -60.3561 | -60.379 | 62.4893 | 62.4069 | 62.3703 | 0.15106 | 0.11444 | -0.022888 | -0.07782 | 0.26093 | 122.9095 | 62.6816 | 122.5067 | 62.7045 | 122.5296 | 0.23346 | 0.091552 | 122.9324 | 123.0103 | 0.11444 | 122.6715 | 62.3703 | 122.6486 | -60.4706 | -122.7493 | 62.3474 | 122.9874 | 62.3703 | -0.064087
2338.8906 | 123.0286 | -62.3428 | 60.4385 | -0.045166 | -0.00015586 | -0.0083505 | 2.893 | 0.0041015 | -0.00505 | 0.00030553 | -0.021637 | 0.16395 | 0.12794 | -0.0084936 | 0.054542 | 0.1035 | -0.0020765 | -0.050354 | 0.022888 | -0.09613 | -0.050354 | 0.050354 | -0.045776 | 0.073242 | -62.5076 | 60.3653 | -62.3474 | 60.4752 | 60.5621 | 60.3653 | 0.40741 | 62.2467 | -60.4156 | -60.4889 | 62.3932 | 62.4161 | 62.2971 | 0.16937 | 0.050354 | -0.004578 | -0.073243 | 0.036621 | 122.905 | 62.7502 | 122.7081 | 62.7548 | 122.7127 | 0.14648 | 0.045776 | 122.9095 | 122.8226 | 0.11902 | 122.7127 | 62.3657 | 122.7081 | -60.5347 | -122.7859 | 62.2925 | 122.818 | 62.2925 | -0.16479
2339.8281 | 123.0103 | -62.3154 | 60.4568 | 0.015869 | -0.00036966 | -0.0083505 | 2.8937 | -0.0033753 | -0.00077756 | -0.0041807 | -0.10098 | 0.16181 | 0.12837 | -0.0063574 | 0.054756 | 0.10436 | -0.0012219 | 0.064087 | 0.07782 | -0.041199 | 0.050354 | 0.12817 | 0.064087 | 0.091553 | -62.4115 | 60.3973 | -62.3383 | 60.498 | 60.5713 | 60.4156 | 0.48981 | 62.2742 | -60.379 | -60.4065 | 62.4435 | 62.4069 | 62.3795 | 0.13275 | 0.10529 | -0.022888 | -0.059509 | 0.041199 | 122.8867 | 62.8052 | 122.731 | 62.8281 | 122.7539 | 0.16937 | 0.091553 | 122.9095 | 122.8363 | 0.11902 | 122.7356 | 62.3932 | 122.7127 | -60.498 | -122.7951 | 62.3657 | 122.8134 | 62.3795 | -0.09613
2340.8906 | 123.0789 | -62.3383 | 60.4065 | -0.037537 | -0.00036966 | -0.0085641 | 2.8939 | 0.0021789 | 0.00029044 | -0.0026853 | -0.17117 | 0.16288 | 0.12623 | 0.00069215 | 0.053688 | 0.10543 | -0.0025037 | -0.086975 | -0.009155 | -0.14191 | -0.073242 | 0.009155 | -0.091553 | -0.064087 | -62.4115 | 60.3607 | -62.3795 | 60.5255 | 60.5667 | 60.379 | 0.37537 | 62.1963 | -60.4156 | -60.4797 | 62.3474 | 62.2742 | 62.2467 | 0.07782 | 0.050354 | -0.041199 | -0.045776 | 0.11902 | 122.905 | 62.7136 | 122.7173 | 62.7548 | 122.7585 | 0.15106 | 0.068665 | 122.9462 | 122.905 | 0.13275 | 122.7402 | 62.3291 | 122.699 | -60.5484 | -122.7859 | 62.265 | 122.8638 | 62.2513 | -0.073242
2341.8281 | 123.0057 | -62.3199 | 60.4477 | -0.037537 | -0.0014377 | -0.0083505 | 2.8907 | -0.0012391 | -0.00013676 | -0.0024717 | -0.10709 | 0.16395 | 0.12751 | -0.0040076 | 0.055397 | 0.10137 | -0.00079467 | 0.073242 | 0.10986 | -0.022888 | 0.032043 | 0.12817 | 0.045776 | 0.07782 | -62.439 | 60.4065 | -62.352 | 60.4614 | 60.5667 | 60.3836 | 0.48065 | 62.2971 | -60.3378 | -60.4156 | 62.4481 | 62.3978 | 62.3657 | 0.10071 | 0.068664 | -0.032044 | -0.041199 | 0.013733 | 122.8867 | 62.8006 | 122.7036 | 62.8326 | 122.7356 | 0.15106 | 0.054931 | 122.9187 | 122.8134 | 0.13275 | 122.7585 | 62.4298 | 122.7264 | -60.4706 | -122.7997 | 62.352 | 122.7814 | 62.3932 | -0.11902
2342.8906 | 123.0743 | -62.3154 | 60.3836 | -0.075684 | -0.0012241 | -0.0068551 | 2.8922 | 0.0019653 | -0.00056396 | -0.00012167 | -0.10403 | 0.16309 | 0.12666 | -0.002085 | 0.054756 | 0.10457 | -0.0035719 | -0.045776 | -0.009155 | -0.12817 | -0.10529 | 0.032043 | 0.022888 | -0.004578 | -62.4161 | 60.3561 | -62.3337 | 60.5072 | 60.5713 | 60.3882 | 0.37079 | 62.1872 | -60.3928 | -60.4889 | 62.3474 | 62.3108 | 62.3383 | 0.1236 | 0.15106 | -0.01831 | -0.027466 | 0.1236 | 122.8867 | 62.6862 | 122.7036 | 62.7045 | 122.7219 | 0.16022 | 0.022888 | 122.905 | 122.8409 | 0.11902 | 122.6898 | 62.3062 | 122.6715 | -60.5118 | -122.7173 | 62.2101 | 122.8226 | 62.2696 | -0.10071
2343.8281 | 123.0103 | -62.3291 | 60.5118 | -0.022278 | -0.00058326 | -0.0098459 | 2.8939 | 0.0019653 | -0.0020594 | -0.0022581 | -0.085724 | 0.16267 | 0.12815 | 0.0041102 | 0.056251 | 0.105 | -0.0020765 | 0.059509 | 0.10071 | -0.032043 | 0.022888 | 0.11444 | 0.018311 | 0.068665 | -62.4344 | 60.4248 | -62.3566 | 60.466 | 60.5347 | 60.347 | 0.41199 | 62.2971 | -60.4111 | -60.4889 | 62.4435 | 62.3978 | 62.3474 | 0.10071 | 0.050354 | -0.027465 | -0.086975 | -0.045777 | 122.8638 | 62.7411 | 122.6761 | 62.7686 | 122.7036 | 0.14648 | 0.054931 | 122.8912 | 122.8226 | 0.13275 | 122.7814 | 62.4298 | 122.7539 | -60.5438 | -122.8683 | 62.352 | 122.7951 | 62.3886 | -0.10529
2344.8906 | 123.0698 | -62.3428 | 60.4019 | -0.083313 | 0.00048494 | -0.0079233 | 2.8918 | 0.0019653 | 0.00050424 | -0.00012167 | -0.13455 | 0.16309 | 0.1273 | -0.0035802 | 0.053474 | 0.10479 | -0.0022901 | -0.018311 | -0.013733 | -0.16479 | -0.064087 | 0.041199 | -0.091553 | -0.073242 | -62.4115 | 60.347 | -62.3657 | 60.5118 | 60.5713 | 60.3928 | 0.37537 | 62.178 | -60.4156 | -60.466 | 62.384 | 62.2696 | 62.2513 | 0.091553 | 0.073242 | -0.022889 | -0.054932 | 0.10986 | 122.9141 | 62.7182 | 122.7356 | 62.7411 | 122.7585 | 0.20599 | 0.10071 | 122.937 | 122.8775 | 0.15106 | 122.7127 | 62.3291 | 122.6898 | -60.5667 | -122.7676 | 62.2787 | 122.8546 | 62.3245 | -0.068665
2345.8281 | 122.9691 | -62.3428 | 60.4752 | 0.00824 | -0.00079686 | -0.0087777 | 2.8939 | 0.0023925 | -0.0046228 | -0.00012167 | -0.19254 | 0.16331 | 0.12858 | -0.00058965 | 0.055183 | 0.10543 | -0.00058107 | -0.009155 | 0.068665 | -0.091553 | -0.050354 | 0.027466 | -0.07782 | -0.027466 | -62.4664 | 60.4156 | -62.3932 | 60.4523 | 60.5026 | 60.3195 | 0.3891 | 62.2513 | -60.4065 | -60.5255 | 62.3703 | 62.3154 | 62.265 | 0.064087 | 0.013733 | -0.050354 | -0.05951 | -0.022888 | 122.8455 | 62.7319 | 122.6624 | 62.7823 | 122.7127 | 0.11902 | 0.041199 | 122.8958 | 122.8455 | 0.16022 | 122.8088 | 62.4115 | 122.7585 | -60.5667 | -122.8683 | 62.2925 | 122.7951 | 62.3337 | -0.1236
2346.8906 | 123.0515 | -62.3291 | 60.434 | -0.045166 | -0.00015586 | -0.0094187 | 2.8915 | 0.00025629 | -0.0016322 | -0.0011899 | -0.055206 | 0.16459 | 0.12922 | -0.006571 | 0.056892 | 0.10436 | -0.0025037 | -0.022888 | 0.041199 | -0.086975 | -0.041199 | 0.059509 | -0.022888 | 0.022888 | -62.4664 | 60.3561 | -62.3428 | 60.5026 | 60.585 | 60.4111 | 0.45319 | 62.2421 | -60.3928 | -60.4752 | 62.3886 | 62.352 | 62.3062 | 0.10986 | 0.064087 | -0.013732 | -0.07782 | 0.068665 | 122.9141 | 62.7823 | 122.7402 | 62.796 | 122.7539 | 0.14648 | 0.045776 | 122.9279 | 122.8455 | 0.12817 | 122.699 | 62.3703 | 122.6852 | -60.5209 | -122.7768 | 62.2879 | 122.8317 | 62.3062 | -0.13733
2347.8281 | 122.8867 | -62.3291 | 60.466 | -0.037537 | -0.00058326 | -0.012409 | 2.8918 | -0.0027343 | -0.002273 | -0.0063169 | -0.097931 | 0.16416 | 0.12944 | 0.0021876 | 0.058601 | 0.10564 | 0.00048713 | 0.009155 | 0.14191 | -0.032043 | -0.041199 | 0.054932 | -0.013733 | 0.036621 | -62.5259 | 60.4385 | -62.3611 | 60.3561 | 60.6766 | 60.4568 | 0.45319 | 62.2971 | -60.3241 | -60.5072 | 62.384 | 62.3657 | 62.3154 | 0.068664 | 0.01831 | -0.032043 | -0.027465 | -0.10986 | 123.0057 | 62.7823 | 122.7859 | 62.8143 | 122.818 | 0.086975 | -0.009156 | 123.0377 | 122.7173 | 0.17395 | 122.7997 | 62.471 | 122.7676 | -60.498 | -122.8271 | 62.2879 | 122.6852 | 62.3383 | -0.19684
2348.8906 | 123.056 | -62.3016 | 60.4294 | -0.11383 | -0.0012241 | -0.0066415 | 2.8937 | 0.0023925 | -0.00099116 | -0.0041807 | -0.06131 | 0.16202 | 0.12623 | -0.00080325 | 0.056678 | 0.10158 | 0.00091433 | -0.050354 | 0.068665 | -0.073242 | -0.036621 | 0.059509 | -0.036621 | 0.004578 | -62.4481 | 60.379 | -62.3611 | 60.498 | 60.5896 | 60.3973 | 0.42114 | 62.2284 | -60.3607 | -60.466 | 62.3611 | 62.3062 | 62.265 | 0.07782 | 0.036621 | -0.059509 | -0.050354 | 0.068665 | 122.8912 | 62.7228 | 122.699 | 62.7823 | 122.7585 | 0.13275 | 0.036621 | 122.9507 | 122.8592 | 0.14191 | 122.7402 | 62.3703 | 122.6807 | -60.5026 | -122.7905 | 62.265 | 122.7997 | 62.2513 | -0.14648
2349.8281 | 122.9691 | -62.3383 | 60.4706 | -0.007019 | -0.0020785 | -0.010914 | 2.8905 | -0.00081171 | -0.0012048 | -0.0026853 | -0.12234 | 0.16245 | 0.12687 | 0.00090575 | 0.05561 | 0.10415 | -0.0016493 | 0.018311 | 0.14648 | -0.041199 | -0.027466 | 0.068665 | -0.004578 | 0.032043 | -62.5214 | 60.4248 | -62.3566 | 60.434 | 60.498 | 60.3378 | 0.4303 | 62.2971 | -60.3241 | -60.498 | 62.4069 | 62.3703 | 62.3337 | 0.073242 | 0.036621 | -0.01831 | -0.045776 | -0.036621 | 122.8363 | 62.7686 | 122.6761 | 62.7869 | 122.6944 | 0.10986 | 0.013733 | 122.8546 | 122.7905 | 0.18768 | 122.7814 | 62.4847 | 122.7631 | -60.5118 | -122.8271 | 62.3108 | 122.7722 | 62.3566 | -0.18311
2350.8906 | 123.0469 | -62.3199 | 60.4111 | -0.068054 | -0.0020785 | -0.0064279 | 2.8915 | 0.0041015 | 0.00093144 | -0.0022581 | -0.064362 | 0.16267 | 0.12815 | -0.0040076 | 0.055824 | 0.10201 | 0.00070073 | 0.15106 | 0.054932 | -0.064087 | -0.041199 | 0.041199 | -0.059509 | 0 | -62.4664 | 60.3607 | -62.3611 | 60.4843 | 60.553 | 60.3882 | 0.42114 | 62.2559 | -60.3561 | -60.4523 | 62.3611 | 62.3199 | 62.2604 | 0.064087 | 0.004578 | -0.041199 | -0.050354 | 0.073242 | 122.8729 | 62.7411 | 122.7081 | 62.7823 | 122.7493 | 0.10529 | 0.022888 | 122.9141 | 122.8455 | 0.11902 | 122.7219 | 62.3749 | 122.6807 | -60.4752 | -122.7722 | 62.2787 | 122.8043 | 62.471 | -0.14648
2351.8281 | 122.9599 | -62.3474 | 60.4568 | -0.045166 | 0.00027134 | -0.0089913 | 2.8943 | 0.0011109 | -0.0048364 | -0.0016171 | -0.17422 | 0.16373 | 0.1273 | -0.0042212 | 0.053688 | 0.10671 | -0.0054945 | -0.041199 | 0.059509 | -0.09613 | -0.082397 | -0.013733 | -0.12817 | -0.064087 | -62.5214 | 60.4065 | -62.3749 | 60.4385 | 60.466 | 60.2829 | 0.34332 | 62.2513 | -60.3973 | -60.5392 | 62.3337 | 62.2833 | 62.2192 | 0.032043 | -0.032044 | -0.027466 | -0.050354 | -0.01831 | 122.8134 | 62.6907 | 122.6303 | 62.7182 | 122.6578 | 0.082397 | 0.013733 | 122.8409 | 122.8134 | 0.15564 | 122.7814 | 62.4069 | 122.7539 | -60.553 | -122.8317 | 62.265 | 122.7859 | 62.3062 | -0.17395
2352.8906 | 123.0515 | -62.2879 | 60.4294 | -0.052796 | 0.00048494 | -0.0089913 | 2.8915 | 0.0015381 | 0.001145 | -0.0033261 | -0.076569 | 0.16309 | 0.12773 | -0.006571 | 0.057319 | 0.10286 | 0.0017687 | 0.059509 | 0.073242 | -0.032043 | 0.054932 | 0.19684 | 0.091553 | 0.1236 | -62.3291 | 60.3836 | -62.3199 | 60.5484 | 60.6354 | 60.4477 | 0.51727 | 62.2559 | -60.3561 | -60.3744 | 62.4847 | 62.4115 | 62.3795 | 0.15564 | 0.1236 | -0.032043 | -0.045776 | 0.11902 | 122.9233 | 62.8052 | 122.7356 | 62.8372 | 122.7676 | 0.22888 | 0.086975 | 122.9553 | 122.8683 | 0.10529 | 122.7036 | 62.3611 | 122.6715 | -60.4614 | -122.7493 | 62.3428 | 122.8363 | 62.3474 | -0.041199
2353.8281 | 122.9736 | -62.3428 | 60.466 | -0.029907 | -0.0033603 | -0.010914 | 2.8941 | 0.0026063 | -0.0016322 | -0.0011899 | -0.15286 | 0.16395 | 0.13008 | -0.00016245 | 0.056251 | 0.1035 | 0.0024097 | 0.013733 | 0.15106 | -0.032043 | 0.022888 | 0.027466 | -0.16022 | -0.018311 | -62.5031 | 60.4568 | -62.3795 | 60.4248 | 60.5026 | 60.3241 | 0.45319 | 62.3108 | -60.3149 | -60.4431 | 62.3703 | 62.3245 | 62.1826 | 0.013732 | -0.12817 | -0.036622 | -0.009155 | -0.041198 | 122.8455 | 62.796 | 122.6669 | 62.8326 | 122.7036 | 0.059509 | 0.054931 | 122.8821 | 122.8043 | 0.18311 | 122.8363 | 62.4939 | 122.7997 | -60.498 | -122.8455 | 62.3657 | 122.7676 | 62.3566 | -0.16022
2354.8906 | 123.0469 | -62.3383 | 60.4248 | -0.022278 | -0.0027195 | -0.0087777 | 2.8924 | 0.0017517 | -0.00077756 | -0.0020443 | -0.097931 | 0.16117 | 0.12773 | -0.0027258 | 0.054115 | 0.10329 | -0.0031445 | -0.045776 | 0.041199 | -0.10071 | -0.045776 | 0.036621 | -0.013733 | 0.24719 | -62.4481 | 60.3745 | -62.3749 | 60.4706 | 60.5438 | 60.379 | 0.42114 | 62.2375 | -60.3836 | -60.4706 | 62.3749 | 62.5854 | 62.3245 | 0.3479 | 0.086975 | -0.036621 | -0.050354 | 0.045776 | 122.8821 | 62.7594 | 122.7173 | 62.796 | 122.7539 | 0.13733 | 0.054932 | 122.9187 | 122.8455 | 0.14191 | 122.7493 | 62.3795 | 122.7127 | -60.5255 | -122.7997 | 62.2925 | 122.8088 | 62.2925 | -0.10986
2355.8281 | 123.0103 | -62.3154 | 60.4614 | -0.014649 | -0.00015586 | -0.0094187 | 2.8937 | 0.0017517 | -0.0033412 | -0.0043943 | -0.14676 | 0.16224 | 0.12687 | -0.0018712 | 0.054115 | 0.10564 | 0.0024097 | 0.032043 | 0.15106 | -0.064087 | -0.022888 | 0.032043 | -0.032043 | 0.018311 | -62.4893 | 60.4477 | -62.3657 | 60.4568 | 60.5484 | 60.3424 | 0.45319 | 62.2513 | -60.3104 | -60.4843 | 62.3474 | 62.3337 | 62.2833 | 0.082398 | 0.032044 | -0.050354 | -0.013733 | -0.004578 | 122.8638 | 62.7686 | 122.6578 | 62.8189 | 122.7081 | 0.09613 | 0.041199 | 122.9141 | 122.8226 | 0.21515 | 122.8134 | 62.4664 | 122.7631 | -60.5255 | -122.8271 | 62.2925 | 122.7722 | 62.3474 | -0.17395
2356.8906 | 123.0103 | -62.3062 | 60.3973 | -0.045166 | 0.00027134 | -0.0068551 | 2.8911 | 4.2692e-05 | 0.0015722 | -0.0031125 | -0.073517 | 0.16373 | 0.12965 | -0.010843 | 0.056251 | 0.1035 | -0.00015387 | -0.068665 | -0.009155 | -0.1236 | -0.059509 | 0.041199 | -0.10529 | -0.018311 | -62.4664 | 60.3607 | -62.3886 | 60.4752 | 60.5392 | 60.3699 | 0.35706 | 62.1826 | -60.4065 | -60.4568 | 62.3474 | 62.2879 | 62.2009 | 0.10528 | 0.01831 | -0.082398 | -0.036621 | 0.07782 | 122.8455 | 62.6633 | 122.6761 | 62.7457 | 122.7585 | 0.16479 | 0.064087 | 122.9279 | 122.8638 | 0.11444 | 122.7493 | 62.2971 | 122.6669 | -60.5209 | -122.7859 | 62.2467 | 122.7814 | 62.2375 | -0.16022
2357.8281 | 122.9462 | -62.3383 | 60.4797 | 0.00061049 | -0.00079686 | -0.0081369 | 2.8911 | 0.00046989 | -0.00056396 | -0.0016171 | -0.10098 | 0.16608 | 0.12751 | -0.001444 | 0.054969 | 0.10329 | -0.00015387 | 0.009155 | 0.15106 | -0.032043 | -0.027466 | 0.054932 | -0.013733 | 0.027466 | -62.5626 | 60.434 | -62.3383 | 60.4568 | 60.4294 | 60.3378 | 0.4715 | 62.3062 | -60.3287 | -60.5072 | 62.3932 | 62.3657 | 62.3245 | 0.059509 | 0.01831 | 0 | -0.045776 | -0.022888 | 122.7676 | 62.8098 | 122.6761 | 62.8098 | 122.6761 | 0.086975 | 0.004577 | 122.7676 | 122.7951 | 0.18311 | 122.7722 | 62.4893 | 122.7722 | -60.5118 | -122.818 | 62.3108 | 122.7951 | 62.3474 | -0.2243
2358.8906 | 123.0927 | -62.3154 | 60.4294 | -0.15198 | -0.0022923 | -0.0077097 | 2.892 | 0.0017517 | -0.0012048 | -0.0024717 | -0.076569 | 0.16267 | 0.12815 | -0.0027258 | 0.056038 | 0.10521 | -0.0033581 | -0.027466 | 0.036621 | -0.086975 | -0.036621 | 0.068665 | -0.032043 | 0.022888 | -62.439 | 60.379 | -62.3611 | 60.4889 | 60.5896 | 60.4065 | 0.45776 | 62.2284 | -60.3928 | -60.466 | 62.384 | 62.3383 | 62.2833 | 0.10986 | 0.054932 | -0.045776 | -0.050354 | 0.05951 | 122.905 | 62.7731 | 122.7219 | 62.8189 | 122.7676 | 0.15564 | 0.050354 | 122.9507 | 122.85 | 0.1236 | 122.7402 | 62.352 | 122.6944 | -60.5164 | -122.7905 | 62.2787 | 122.8043 | 62.2879 | -0.1236
2359.8281 | 122.9553 | -62.3474 | 60.466 | -0.007019 | -0.0016513 | -0.0107 | 2.8943 | -0.00017091 | -0.00077756 | -0.0026853 | -0.097931 | 0.16502 | 0.12901 | -0.004862 | 0.056038 | 0.10051 | -0.0016493 | 0.009155 | 0.15564 | -0.064087 | -0.032043 | 0.054932 | -0.018311 | 0.041199 | -62.5168 | 60.434 | -62.384 | 60.585 | 60.26 | 60.3058 | 0.4715 | 62.2833 | -60.3104 | -60.498 | 62.4023 | 62.3886 | 62.3291 | 0.10529 | 0.045776 | -0.036621 | -0.032043 | 0.11902 | 122.6074 | 62.8189 | 122.6532 | 62.8555 | 122.6898 | 0.11902 | 0.032044 | 122.644 | 122.9691 | 0.21973 | 122.818 | 62.5031 | 122.7814 | -60.5301 | -122.85 | 62.3154 | 122.9324 | 62.3566 | -0.16937
2360.8281 | 123.0743 | -62.2971 | 60.4568 | -0.029907 | 5.7742e-05 | -0.0094187 | 2.8941 | 0.0017517 | -0.00077756 | -0.0018307 | -0.067413 | 0.16309 | 0.12773 | -0.0063574 | 0.056465 | 0.10479 | 0.00070073 | -0.21973 | 0.1236 | -0.013733 | 0.013733 | 0.16479 | 0.10071 | 0.09613 | -62.4023 | 60.3516 | -62.3383 | 60.5347 | 60.6171 | 60.434 | 0.50812 | 62.2833 | -60.3333 | -60.4431 | 62.4619 | 62.3932 | 62.3978 | 0.10986 | 0.11444 | -0.041199 | -0.10529 | 0.07782 | 122.9141 | 62.8052 | 122.731 | 62.8464 | 122.7722 | 0.17853 | 0.027466 | 122.9553 | 122.8729 | 0.13733 | 122.6898 | 62.4207 | 122.6486 | -60.4706 | -122.7951 | 62.3108 | 122.8317 | 62.0773 | -0.10529
2361.8906 | 123.0652 | -62.3016 | 60.434 | -0.12909 | 5.7742e-05 | -0.0094187 | 2.8928 | 4.2692e-05 | -0.0016322 | -0.0022581 | -0.067413 | 0.1648 | 0.12986 | -0.0057166 | 0.054329 | 0.10265 | 0.00027333 | -0.045776 | 0.054932 | -0.059509 | -0.036621 | 0.064087 | -0.027466 | 0.013733 | -62.4573 | 60.3745 | -62.3657 | 60.5072 | 60.585 | 60.4294 | 0.44403 | 62.2421 | -60.379 | -60.4706 | 62.3657 | 62.3154 | 62.2742 | 0.073242 | 0.032043 | -0.064087 | -0.059509 | 0.073242 | 122.8867 | 62.7457 | 122.731 | 62.8098 | 122.7951 | 0.1236 | 0.022888 | 122.9507 | 122.8729 | 0.11444 | 122.7402 | 62.3566 | 122.6761 | -60.4935 | -122.7997 | 62.265 | 122.8088 | 62.2559 | -0.15564
2362.8281 | 122.9736 | -62.3291 | 60.4843 | -0.022278 | 0.00091214 | -0.0098459 | 2.8933 | 0.0011109 | -0.0018458 | -0.0031125 | -0.091827 | 0.16288 | 0.12538 | -0.0018712 | 0.053047 | 0.10479 | -0.0037855 | 0.050354 | 0.11902 | -0.018311 | 0.018311 | 0.1236 | 0.032043 | 0.07782 | -62.4435 | 60.4294 | -62.3428 | 60.4523 | 60.5301 | 60.3699 | 0.4715 | 62.3108 | -60.3653 | -60.466 | 62.4527 | 62.4069 | 62.3611 | 0.096131 | 0.050354 | -0.013732 | -0.054932 | -0.032043 | 122.8592 | 62.8006 | 122.699 | 62.8143 | 122.7127 | 0.14191 | 0.036622 | 122.8729 | 122.7951 | 0.13733 | 122.7722 | 62.4481 | 122.7585 | -60.5026 | -122.8271 | 62.3474 | 122.7814 | 62.3795 | -0.11444
2363.8906 | 123.0789 | -62.3154 | 60.4202 | -0.060425 | 0.00048494 | -0.0070687 | 2.8945 | 0.0021789 | -0.0018458 | -0.0016171 | -0.082672 | 0.16245 | 0.12815 | -0.001444 | 0.054542 | 0.10415 | -0.0012219 | -0.050354 | -0.032043 | -0.11902 | -0.29297 | 0.32044 | 0.14648 | -0.041199 | -62.4207 | 60.3607 | -62.3474 | 60.5164 | 60.5804 | 60.4111 | 0.38452 | 62.1963 | -60.4523 | -60.7132 | 62.6358 | 62.2742 | 62.4619 | 0.07782 | 0.2655 | -0.032043 | -0.059509 | 0.09613 | 122.8958 | 62.6999 | 122.7264 | 62.7319 | 122.7585 | 0.43945 | -0.17395 | 122.9279 | 122.8638 | 0.086976 | 122.7081 | 62.2833 | 122.6761 | -60.5392 | -122.7676 | 62.0224 | 122.8317 | 62.265 | -0.10529
2364.8281 | 123.0743 | -62.3108 | 60.4385 | 0.00824 | -0.00058326 | -0.0087777 | 2.8939 | -0.0042297 | -0.00035036 | -0.0014035 | -0.070465 | 0.16352 | 0.12666 | -0.0016576 | 0.054542 | 0.10543 | -0.0029309 | 0.050354 | 0.086975 | -0.036621 | -0.13275 | 0.29297 | -0.054932 | -0.041199 | -62.3886 | 60.3745 | -62.3199 | 60.5164 | 60.6216 | 60.4523 | 0.5127 | 62.2742 | -60.3516 | -60.5713 | 62.6038 | 62.2696 | 62.2559 | -0.004578 | -0.018311 | -0.009155 | -0.064087 | 0.077819 | 122.9324 | 62.8235 | 122.7631 | 62.8326 | 122.7722 | 0.32959 | -0.09613 | 122.9416 | 122.8363 | 0.1236 | 122.6944 | 62.3978 | 122.6852 | -60.4752 | -122.7585 | 62.178 | 122.8271 | 62.3611 | -0.07782
2365.8906 | 123.0469 | -62.3016 | 60.3928 | -0.083313 | -0.0010105 | -0.0074961 | 2.8943 | 0.0036743 | -0.00077756 | -0.0016171 | -0.039948 | 0.16288 | 0.12922 | -0.0012304 | 0.05262 | 0.10286 | -0.0027173 | -0.045776 | -0.027466 | -0.1236 | -0.054932 | 0.12817 | -0.49896 | -0.31586 | -62.439 | 60.3653 | -62.3611 | 60.5026 | 60.5621 | 60.3928 | 0.3891 | 62.178 | -60.4202 | -60.4477 | 62.4298 | 61.9858 | 61.8027 | -0.19226 | -0.37537 | -0.059509 | -0.027466 | 0.10986 | 122.8638 | 62.6907 | 122.6944 | 62.7502 | 122.7539 | 0.25177 | 0.068664 | 122.9233 | 122.8638 | 0.09613 | 122.7264 | 62.2742 | 122.6669 | -60.5164 | -122.7539 | 62.2467 | 122.8043 | 62.2559 | -0.13733
2366.8281 | 123.0698 | -62.2925 | 60.4111 | -0.060425 | -0.00036966 | -0.0066415 | 2.8922 | -0.0016663 | -0.0037684 | -0.0020443 | -0.12234 | 0.16395 | 0.12687 | 0.00026495 | 0.054969 | 0.10329 | -0.0027173 | 0.050354 | 0.091553 | -0.036621 | 0.44861 | -0.082397 | -0.3479 | 0.1236 | -62.3611 | 60.379 | -62.3383 | 60.5255 | 60.6445 | 60.4431 | 0.52643 | 62.2559 | -60.3195 | -59.9625 | 62.2101 | 62.4161 | 61.9446 | 0.16022 | -0.31128 | -0.045777 | -0.032044 | 0.11444 | 122.937 | 62.8189 | 122.7356 | 62.8647 | 122.7814 | -0.045776 | 0.48523 | 122.9828 | 122.8638 | 0.12817 | 122.7173 | 62.384 | 122.6715 | -60.4477 | -122.7493 | 62.7411 | 122.818 | 62.3428 | -0.068665
2367.8906 | 123.1018 | -62.3108 | 60.4202 | -0.045166 | -0.00079686 | -0.0074961 | 2.8926 | -0.00017091 | 0.00050424 | -0.0035397 | -0.082672 | 0.16288 | 0.12751 | -0.0029394 | 0.054115 | 0.10415 | -0.00079467 | 0.050354 | 0.07782 | -0.013733 | 0.073242 | 0.20599 | 0.073242 | 0.11444 | -62.3383 | 60.3882 | -62.3428 | 60.5347 | 60.6308 | 60.4477 | 0.53101 | 62.2971 | -60.3424 | -60.347 | 62.5168 | 62.4252 | 62.384 | 0.12817 | 0.086975 | -0.032043 | -0.032043 | 0.11444 | 122.9416 | 62.8418 | 122.7585 | 62.8738 | 122.7905 | 0.21973 | 0.086975 | 122.9736 | 122.8775 | 0.091553 | 122.731 | 62.3886 | 122.699 | -60.434 | -122.7631 | 62.384 | 122.8455 | 62.3611 | -0.027466
2368.8281 | 122.9828 | -62.3474 | 60.4752 | 0.00824 | -0.00079686 | -0.010914 | 2.8918 | 0.00068369 | -0.003982 | -0.0020443 | -0.10403 | 0.16267 | 0.12922 | -0.00058965 | 0.055824 | 0.10393 | -0.0044263 | 0.050354 | 0.13733 | -0.041199 | -0.027466 | 0.059509 | -0.018311 | 0.018311 | -62.4939 | 60.4385 | -62.352 | 60.4248 | 60.5209 | 60.3333 | 0.44403 | 62.3062 | -60.3378 | -60.5026 | 62.4069 | 62.3657 | 62.3291 | 0.05951 | 0.022888 | -0.004578 | -0.036621 | -0.050354 | 122.8683 | 62.7914 | 122.6807 | 62.796 | 122.6852 | 0.10071 | 0.013733 | 122.8729 | 122.7768 | 0.17853 | 122.7905 | 62.4847 | 122.7859 | -60.5164 | -122.8271 | 62.3199 | 122.7722 | 62.3978 | -0.14648
2369.8906 | 123.0789 | -62.3108 | 60.4431 | -0.090943 | -0.0020785 | -0.0077097 | 2.8915 | 0.0030335 | -0.00056396 | -0.00033547 | -0.06131 | 0.1648 | 0.12773 | -0.0046484 | 0.056251 | 0.10308 | -0.00036747 | 0.004578 | 0.045776 | -0.054932 | 0.004578 | 0.10529 | 0.009155 | 0.07782 | -62.4161 | 60.3928 | -62.3428 | 60.5301 | 60.6079 | 60.466 | 0.48981 | 62.2559 | -60.3973 | -60.4385 | 62.4161 | 62.3886 | 62.3199 | 0.13275 | 0.064087 | -0.032043 | -0.050354 | 0.086975 | 122.9187 | 62.8006 | 122.7768 | 62.8326 | 122.8088 | 0.16022 | 0.05951 | 122.9507 | 122.8729 | 0.10071 | 122.7356 | 62.3566 | 122.7036 | -60.498 | -122.7859 | 62.3154 | 122.8409 | 62.3154 | -0.10529
2370.8281 | 122.9691 | -62.3566 | 60.4889 | -0.083313 | -0.0020785 | -0.010914 | 2.8913 | -0.0025207 | -0.00099116 | -0.0024717 | -0.11624 | 0.16416 | 0.12965 | -0.0084936 | 0.056892 | 0.10244 | -0.0044263 | 0.045776 | 0.13275 | -0.045776 | -0.027466 | 0.059509 | -0.018311 | 0.032043 | -62.5214 | 60.4477 | -62.3657 | 60.4156 | 60.498 | 60.3195 | 0.4303 | 62.3108 | -60.3561 | -60.5164 | 62.4161 | 62.3886 | 62.3383 | 0.077819 | 0.027465 | -0.009156 | -0.041199 | -0.073243 | 122.8546 | 62.7869 | 122.6761 | 62.796 | 122.6852 | 0.10528 | 0.01831 | 122.8638 | 122.7814 | 0.17853 | 122.8134 | 62.4893 | 122.8043 | -60.5347 | -122.8546 | 62.3291 | 122.7722 | 62.4023 | -0.1648
2371.8906 | 122.9782 | -62.3611 | 60.4294 | -0.075684 | -0.0029331 | -0.0092051 | 2.8935 | 0.0011109 | -0.00077756 | -0.0022581 | -0.16202 | 0.16523 | 0.12858 | -0.004862 | 0.055183 | 0.1065 | -0.0027173 | -0.1236 | 0.050354 | -0.13733 | -0.14191 | -0.068665 | -0.1831 | -0.10529 | -62.5305 | 60.3928 | -62.3978 | 60.434 | 60.4935 | 60.2921 | 0.31586 | 62.2238 | -60.379 | -60.5713 | 62.2925 | 62.2559 | 62.178 | 0.032043 | -0.045776 | -0.036621 | -0.036621 | 0.004578 | 122.8546 | 62.677 | 122.6532 | 62.7136 | 122.6898 | 0.068664 | -0.004578 | 122.8912 | 122.8317 | 0.18768 | 122.7905 | 62.4115 | 122.7539 | -60.5667 | -122.8271 | 62.2192 | 122.7951 | 62.2375 | -0.16937
2372.8281 | 122.9507 | -62.3428 | 60.4385 | -0.060425 | -0.0010105 | -0.0094187 | 2.893 | 4.2692e-05 | -0.00099116 | -0.00054907 | -0.15897 | 0.16395 | 0.12922 | 0.00069215 | 0.056678 | 0.10628 | -0.00058107 | 0.022888 | 0.10529 | -0.07782 | -0.022888 | 0.064087 | -0.036621 | -0.013733 | -62.4435 | 60.4248 | -62.3703 | 60.4797 | 60.5576 | 60.3149 | 0.37994 | 62.265 | -60.3333 | -60.4614 | 62.4069 | 62.3291 | 62.3062 | 0.064087 | 0.041199 | -0.027466 | -0.013733 | 0.041198 | 122.9004 | 62.7228 | 122.6578 | 62.7502 | 122.6852 | 0.14191 | 0.054932 | 122.9279 | 122.85 | 0.18311 | 122.7951 | 62.4481 | 122.7676 | -60.5164 | -122.8088 | 62.3199 | 122.8226 | 62.3657 | -0.10071
2373.8906 | 123.0606 | -62.3199 | 60.3928 | -0.068054 | 5.7742e-05 | -0.0079233 | 2.8924 | 0.0038879 | -0.0016322 | -0.0028989 | -0.067413 | 0.16309 | 0.12794 | 0.00090575 | 0.055397 | 0.105 | -0.0010083 | -0.041199 | -0.045776 | -0.13733 | -0.059509 | -0.09613 | -0.51727 | 0.032043 | -62.4023 | 60.3561 | -62.3383 | 60.5118 | 60.5804 | 60.3973 | 0.39368 | 62.1826 | -60.4385 | -60.4523 | 62.2238 | 62.352 | 61.8027 | 0.16937 | -0.37994 | -0.018311 | -0.036621 | 0.11902 | 122.9004 | 62.7136 | 122.7173 | 62.7319 | 122.7356 | 0.041199 | 0.07782 | 122.9187 | 122.85 | 0.091553 | 122.6944 | 62.2742 | 122.6761 | -60.5301 | -122.731 | 62.2604 | 122.8317 | 62.2787 | -0.082398
2374.8281 | 122.9691 | -62.3383 | 60.4477 | -0.16724 | -0.00015586 | -0.0092051 | 2.893 | 0.00089729 | -0.0031274 | -0.0033261 | -0.11929 | 0.16416 | 0.13072 | -0.0027258 | 0.056678 | 0.1035 | -0.0022901 | 0.041199 | 0.21057 | 0.009155 | -0.036621 | 0.068665 | -0.045776 | 0.009155 | -62.5259 | 60.4294 | -62.3795 | 60.4294 | 60.5301 | 60.3241 | 0.44403 | 62.3474 | -60.2371 | -60.4843 | 62.4069 | 62.3474 | 62.2925 | 0 | -0.054931 | -0.041199 | -0.018311 | -0.018311 | 122.8683 | 62.7823 | 122.6624 | 62.8235 | 122.7036 | 0.05951 | -0.045776 | 122.9095 | 122.8088 | 0.20142 | 122.8088 | 62.5488 | 122.7676 | -60.4385 | -122.8271 | 62.3016 | 122.7676 | 62.3795 | -0.18768
2375.8906 | 123.0194 | -62.3428 | 60.4156 | -0.068054 | -0.0027195 | -0.0092051 | 2.8926 | -0.0010253 | -0.0035548 | -0.0028989 | -0.073517 | 0.16202 | 0.12858 | -0.003794 | 0.055397 | 0.10393 | -0.0022901 | -0.091553 | 0.013733 | -0.10071 | -0.073242 | 0.013733 | -0.082397 | -0.013733 | -62.4847 | 60.3607 | -62.3657 | 60.466 | 60.5484 | 60.3653 | 0.39368 | 62.2421 | -60.4019 | -60.4889 | 62.3566 | 62.3291 | 62.2604 | 0.086975 | 0.018311 | -0.022889 | -0.054931 | 0.050354 | 122.8912 | 62.7365 | 122.7081 | 62.7594 | 122.731 | 0.11444 | 0.027466 | 122.9141 | 122.8317 | 0.11444 | 122.7264 | 62.3566 | 122.7036 | -60.5164 | -122.7814 | 62.2696 | 122.8088 | 62.2513 | -0.14191
2376.8281 | 123.0057 | -62.3291 | 60.5255 | 0.061645 | -0.0018649 | -0.0094187 | 2.8913 | -0.0018799 | -0.0024866 | -0.0041807 | -0.10098 | 0.16416 | 0.12687 | 0.0011194 | 0.057106 | 0.1035 | -0.0022901 | 0.004578 | 0.13733 | -0.032043 | -0.022888 | 0.07782 | -0.027466 | 0.045776 | -62.5168 | 60.4385 | -62.3611 | 60.4202 | 60.498 | 60.3241 | 0.44861 | 62.2971 | -60.3882 | -60.5484 | 62.4069 | 62.3749 | 62.3016 | 0.077819 | 0.004577 | -0.032043 | -0.086975 | -0.10529 | 122.8271 | 62.7777 | 122.6532 | 62.8098 | 122.6852 | 0.10986 | 0.009155 | 122.8592 | 122.7814 | 0.16937 | 122.7997 | 62.4664 | 122.7676 | -60.5576 | -122.8867 | 62.3062 | 122.7493 | 62.3337 | -0.18768
2377.8906 | 123.0606 | -62.3108 | 60.4431 | -0.037537 | -0.00036966 | -0.010487 | 2.8903 | 0.00089729 | -0.002273 | -0.0048215 | -0.042999 | 0.16352 | 0.12815 | -0.0033666 | 0.05326 | 0.098164 | 0.00070073 | 0.054932 | 0.064087 | -0.041199 | 0.054932 | 0.16479 | 0.073242 | 0.10986 | -62.3611 | 60.3699 | -62.3383 | 60.6079 | 60.3516 | 60.5301 | 0.60425 | 62.2696 | -60.379 | -60.3882 | 62.4756 | 62.4207 | 62.384 | 0.15106 | 0.11444 | -0.027466 | -0.073242 | 0.16479 | 122.6624 | 62.915 | 122.8409 | 62.9425 | 122.8683 | 0.20599 | 0.096131 | 122.6898 | 122.9462 | 0.10529 | 122.7081 | 62.3749 | 122.6807 | -60.4843 | -122.7814 | 62.3657 | 122.9187 | 62.3657 | -0.050354
2378.8281 | 122.9965 | -62.3428 | 60.4614 | 0.023498 | -0.0014377 | -0.010487 | 2.8918 | 0.0028199 | 0.001145 | -0.0039671 | -0.1315 | 0.16502 | 0.12794 | -0.0016576 | 0.056251 | 0.10521 | -0.0014355 | 0.009155 | 0.1236 | -0.068665 | -0.018311 | 0.041199 | -0.027466 | 0.027466 | -62.5168 | 60.434 | -62.3428 | 60.4385 | 60.5164 | 60.3607 | 0.45319 | 62.2742 | -60.3378 | -60.4797 | 62.384 | 62.3703 | 62.3154 | 0.096131 | 0.041199 | 0 | -0.027466 | -0.022888 | 122.8592 | 62.796 | 122.7036 | 62.796 | 122.7036 | 0.10986 | 0.050354 | 122.8592 | 122.7814 | 0.19226 | 122.7768 | 62.4664 | 122.7768 | -60.5301 | -122.8043 | 62.3245 | 122.7814 | 62.352 | -0.17395
2379.8906 | 123.111 | -62.265 | 60.434 | -0.014649 | 5.7742e-05 | -0.010059 | 2.893 | 0.0026063 | -0.00056396 | -0.0052487 | -0.085724 | 0.16651 | 0.12709 | -0.0059302 | 0.056465 | 0.10457 | -0.0029309 | 0.059509 | 0.07782 | -0.041199 | 0.068665 | 0.17395 | 0.059509 | 0.10986 | -62.1002 | 60.4385 | -62.3016 | 60.5072 | 60.6766 | 60.4385 | 0.48065 | 62.2238 | -60.3561 | -60.3653 | 62.439 | 62.3749 | 62.3245 | 0.15106 | 0.10071 | -0.036621 | 0.004578 | 0.073242 | 122.9416 | 62.7457 | 122.7036 | 62.7823 | 122.7402 | 0.21515 | 0.10986 | 122.9782 | 122.8088 | 0.11902 | 122.7402 | 62.3428 | 122.7036 | -60.4752 | -122.7356 | 62.3337 | 122.7722 | 62.3245 | 0.16479
2380.8281 | 122.9553 | -62.352 | 60.4843 | -0.007019 | -0.0029331 | -0.0094187 | 2.893 | -0.0023071 | -0.0024866 | -0.0041807 | -0.11014 | 0.16694 | 0.12815 | -0.00016245 | 0.056038 | 0.105 | 0.00027333 | 0.018311 | 0.16022 | -0.022888 | -0.027466 | 0.068665 | -0.013733 | 0.036621 | -62.4298 | 60.4614 | -62.3062 | 60.3928 | 60.5164 | 60.3149 | 0.42572 | 62.3291 | -60.3241 | -60.5118 | 62.4207 | 62.3886 | 62.3383 | 0.059509 | 0.009155 | 0.045777 | -0.022888 | -0.091553 | 122.8683 | 62.7777 | 122.6669 | 62.7319 | 122.6212 | 0.091553 | -0.004578 | 122.8226 | 122.699 | 0.1831 | 122.7676 | 62.5122 | 122.8134 | -60.5072 | -122.7905 | 62.3245 | 122.7448 | 62.3703 | -0.07782
2381.8906 | 123.0057 | -62.3428 | 60.4706 | -0.045166 | 0.00048494 | -0.0079233 | 2.89 | -0.0014527 | 7.6842e-05 | -0.0014035 | -0.06131 | 0.16245 | 0.12773 | -0.0097754 | 0.05561 | 0.10372 | -0.0042127 | 0.054932 | 0.073242 | -0.018311 | 0.050354 | 0.14191 | 0.054932 | 0.086975 | -62.4115 | 60.4019 | -62.3154 | 60.4843 | 60.5667 | 60.3928 | 0.48981 | 62.3245 | -60.3973 | -60.4202 | 62.4847 | 62.4298 | 62.3978 | 0.10529 | 0.073243 | 0.027465 | -0.068664 | 0.013733 | 122.9095 | 62.8326 | 122.7356 | 62.8052 | 122.7081 | 0.16022 | 0.068665 | 122.8821 | 122.7997 | 0.091553 | 122.7173 | 62.4161 | 122.7448 | -60.4889 | -122.7859 | 62.3932 | 122.8271 | 62.3978 | -0.068665
2382.8438 | 123.0423 | -62.3291 | 60.4294 | -0.052796 | -0.00036966 | -0.0074961 | 2.8913 | -0.00038451 | -0.00013676 | -0.0033261 | -0.06131 | 0.16416 | 0.12687 | -0.0016576 | 0.057319 | 0.10222 | 5.9726e-05 | -0.064087 | 0 | -0.13275 | -0.064087 | 0.022888 | -0.09613 | -0.013733 | -62.4527 | 60.379 | -62.3657 | 60.4614 | 60.553 | 60.3653 | 0.37537 | 62.1964 | -60.4294 | -60.4935 | 62.352 | 62.3154 | 62.233 | 0.11902 | 0.036621 | -0.036621 | -0.050354 | 0.032044 | 122.8821 | 62.7045 | 122.6944 | 62.7411 | 122.731 | 0.15564 | 0.068664 | 122.9187 | 122.8271 | 0.13275 | 122.7448 | 62.3291 | 122.7081 | -60.5621 | -122.7951 | 62.265 | 122.7905 | 62.265 | -0.1236
2383.8906 | 123.0652 | -62.3016 | 60.4294 | -0.052796 | -0.0031467 | -0.010914 | 2.8926 | -0.0055115 | -0.0029138 | -0.0035397 | -0.14371 | 0.16224 | 0.12751 | -0.0089208 | 0.055824 | 0.10329 | -0.0029309 | 0.041199 | 0.073242 | -0.027466 | 0.1236 | -0.32044 | -0.036621 | 0.14648 | -62.3383 | 60.3607 | -62.352 | 60.5438 | 60.6308 | 60.4431 | 0.54016 | 62.2742 | -60.3561 | -60.3058 | 61.9812 | 62.4481 | 62.265 | 0.17395 | -0.009155 | -0.050354 | -0.068664 | 0.11444 | 122.9324 | 62.8418 | 122.7448 | 62.8922 | 122.7951 | -0.29297 | 0.15106 | 122.9828 | 122.8958 | 0.10071 | 122.7127 | 62.3749 | 122.6624 | -60.4568 | -122.7814 | 62.4252 | 122.8455 | 62.3428 | -0.036621
2384.8281 | 123.0011 | -62.3154 | 60.4843 | -0.052796 | 0.00048494 | -0.0092051 | 2.8945 | -0.00059811 | -0.0018458 | -0.00076267 | -0.1315 | 0.16459 | 0.12922 | -0.002085 | 0.055183 | 0.1035 | -0.00036747 | 0.022888 | 0.14191 | -0.032043 | -0.036621 | 0.036621 | -0.013733 | 0.022888 | -62.4847 | 60.4431 | -62.3657 | 60.4523 | 60.5392 | 60.3699 | 0.4715 | 62.2833 | -60.3424 | -60.5209 | 62.352 | 62.3383 | 62.3016 | 0.054931 | 0.01831 | -0.050354 | -0.041199 | -0.032043 | 122.8546 | 62.7869 | 122.6852 | 62.8372 | 122.7356 | 0.068664 | -0.004578 | 122.905 | 122.818 | 0.17395 | 122.8088 | 62.4573 | 122.7585 | -60.5164 | -122.85 | 62.2787 | 122.7676 | 62.3383 | -0.16937
2385.8906 | 122.9553 | -62.3566 | 60.4935 | 0.046386 | -0.0022923 | -0.0074961 | 2.892 | -0.0018799 | -0.002273 | -0.0014035 | -0.082672 | 0.16352 | 0.12687 | -0.003794 | 0.057106 | 0.10286 | -0.0035719 | -0.036621 | 0.13275 | -0.036621 | -0.041199 | 0.059509 | -0.022888 | 0.032043 | -62.5076 | 60.4385 | -62.3795 | 60.4156 | 60.5164 | 60.3333 | 0.46234 | 62.3199 | -60.3607 | -60.5347 | 62.4161 | 62.3886 | 62.3337 | 0.068664 | 0.013733 | -0.022889 | -0.054931 | -0.07782 | 122.8729 | 62.8189 | 122.6898 | 62.8418 | 122.7127 | 0.09613 | -0.004578 | 122.8958 | 122.7951 | 0.16937 | 122.818 | 62.4893 | 122.7951 | -60.5301 | -122.8729 | 62.3154 | 122.7722 | 62.3199 | -0.15106
2386.8281 | 123.0011 | -62.3474 | 60.4614 | 0.00061049 | -0.0025059 | -0.0092051 | 2.8956 | 0.0019653 | -0.0012048 | -0.0031125 | -0.1376 | 0.16267 | 0.12602 | -0.0084936 | 0.056251 | 0.10628 | -0.0010083 | 0.032043 | 0.14648 | -0.064087 | -0.045776 | 0.036621 | -0.036621 | 0.009155 | -62.5076 | 60.4111 | -62.3886 | 60.4752 | 60.5438 | 60.3561 | 0.48065 | 62.2833 | -60.3149 | -60.5072 | 62.384 | 62.3566 | 62.3108 | 0.073242 | 0.027466 | -0.041199 | -0.050354 | 0.013733 | 122.8912 | 62.8281 | 122.7036 | 62.8693 | 122.7448 | 0.10071 | 0.018311 | 122.9324 | 122.8638 | 0.21057 | 122.7997 | 62.4939 | 122.7585 | -60.5255 | -122.85 | 62.3016 | 122.8226 | 62.3795 | -0.16022
2387.9062 | 122.9736 | -62.3245 | 60.4752 | -0.045166 | -0.0012241 | -0.0092051 | 2.8924 | 0.0047425 | -0.0029138 | -0.0022581 | -0.16507 | 0.16416 | 0.12666 | 0.001333 | 0.055824 | 0.10457 | -0.0035719 | 0.009155 | 0.073242 | -0.082397 | -0.045776 | 0.022888 | -0.086975 | -0.036621 | -62.4756 | 60.4065 | -62.3474 | 60.4523 | 60.5072 | 60.3058 | 0.37994 | 62.2421 | -60.4019 | -60.5209 | 62.3474 | 62.2879 | 62.2375 | 0.045776 | -0.004578 | -0.022888 | -0.068665 | -0.022888 | 122.8317 | 62.7045 | 122.6303 | 62.7274 | 122.6532 | 0.10528 | 0.036621 | 122.8546 | 122.7997 | 0.15564 | 122.7539 | 62.3978 | 122.731 | -60.5576 | -122.8226 | 62.2787 | 122.7768 | 62.3337 | -0.15106
2388.8281 | 123.0103 | -62.3383 | 60.4477 | -0.014649 | -0.00036966 | -0.010273 | 2.8945 | 0.0032471 | 0.0015722 | -0.0033261 | -0.11319 | 0.16352 | 0.12602 | -0.0010168 | 0.054969 | 0.105 | -0.0046399 | 0.032043 | 0.13275 | -0.068665 | -0.054932 | 0.054932 | -0.032043 | 0 | -62.4573 | 60.4202 | -62.3383 | 60.4843 | 60.5392 | 60.3699 | 0.46692 | 62.2696 | -60.3149 | -60.5026 | 62.3932 | 62.3383 | 62.3062 | 0.068665 | 0.036622 | 0 | -0.027466 | 0.036621 | 122.8775 | 62.8052 | 122.7081 | 62.8052 | 122.7081 | 0.1236 | 0.013733 | 122.8775 | 122.8226 | 0.20142 | 122.7585 | 62.471 | 122.7585 | -60.5164 | -122.7859 | 62.2833 | 122.8226 | 62.3703 | -0.11902
2389.8906 | 122.9507 | -62.3657 | 60.4706 | -0.014649 | -0.00058326 | -0.0094187 | 2.892 | -0.0012391 | 7.6842e-05 | -0.0039671 | -0.070465 | 0.16459 | 0.12944 | -0.0069982 | 0.056678 | 0.10201 | 0.0011279 | 0.004578 | 0.12817 | -0.027466 | -0.041199 | 0.059509 | -0.022888 | 0.027466 | -62.5214 | 60.4111 | -62.3657 | 60.4065 | 60.5026 | 60.3516 | 0.45319 | 62.3383 | -60.3424 | -60.5118 | 62.4252 | 62.3932 | 62.3428 | 0.054932 | 0.004578 | 0 | -0.059509 | -0.064087 | 122.8683 | 62.8189 | 122.7173 | 62.8189 | 122.7173 | 0.086975 | -0.013733 | 122.8683 | 122.7722 | 0.15564 | 122.7768 | 62.4939 | 122.7768 | -60.498 | -122.8363 | 62.3245 | 122.7722 | 62.3703 | -0.15564
2390.8281 | 123.0103 | -62.3245 | 60.4568 | -0.022278 | -0.00058326 | -0.0060007 | 2.8926 | 0.00025629 | -0.0024866 | -0.0061033 | -0.1254 | 0.16267 | 0.12965 | 0.003042 | 0.054756 | 0.10372 | 0.0017687 | 0.018311 | 0.10529 | -0.054932 | -0.018311 | 0.068665 | -0.027466 | 0.054932 | -62.4664 | 60.4019 | -62.3383 | 60.4614 | 60.5347 | 60.3699 | 0.4715 | 62.2696 | -60.3516 | -60.4752 | 62.3932 | 62.3795 | 62.2971 | 0.10986 | 0.027466 | -0.013733 | -0.054931 | 0.004578 | 122.8592 | 62.796 | 122.6944 | 62.8098 | 122.7081 | 0.1236 | 0.036621 | 122.8729 | 122.7997 | 0.16022 | 122.7402 | 62.4298 | 122.7264 | -60.5118 | -122.7951 | 62.3062 | 122.7859 | 62.3428 | -0.14191
2391.8906 | 123.0972 | -62.2971 | 60.4385 | -0.1062 | -0.0014377 | -0.0089913 | 2.8915 | -0.0025207 | -0.0027002 | -0.00076267 | -0.036896 | 0.16416 | 0.12815 | -0.012766 | 0.055183 | 0.10201 | 0.0030505 | 0.004578 | 0.045776 | -0.059509 | 0.009155 | 0.14648 | 0.032043 | 0.091553 | -62.3795 | 60.3699 | -62.3337 | 60.5484 | 60.6308 | 60.466 | 0.50812 | 62.2375 | -60.3928 | -60.4294 | 62.4435 | 62.3886 | 62.3291 | 0.15106 | 0.091552 | -0.036621 | -0.068665 | 0.10986 | 122.9279 | 62.8052 | 122.7631 | 62.8418 | 122.7997 | 0.20599 | 0.068664 | 122.9645 | 122.8821 | 0.10528 | 122.7036 | 62.3428 | 122.6669 | -60.498 | -122.7722 | 62.3062 | 122.8455 | 62.3016 | -0.082398
2392.8281 | 123.0148 | -62.3108 | 60.4614 | -0.075684 | -0.0018649 | -0.0057871 | 2.8933 | 0.0019653 | -0.0016322 | -0.0033261 | -0.11929 | 0.16373 | 0.12687 | -0.00016245 | 0.054969 | 0.10372 | -0.0010083 | 0.041199 | 0.14648 | -0.050354 | -0.018311 | 0.054932 | -0.018311 | 0.018311 | -62.4619 | 60.4156 | -62.3474 | 60.4706 | 60.5438 | 60.3561 | 0.48065 | 62.2604 | -60.3149 | -60.4797 | 62.3657 | 62.3291 | 62.2925 | 0.068665 | 0.032043 | -0.036621 | -0.045777 | 0.009155 | 122.8546 | 62.7914 | 122.6669 | 62.8281 | 122.7036 | 0.10529 | 0.032043 | 122.8912 | 122.818 | 0.19684 | 122.7631 | 62.4573 | 122.7264 | -60.5118 | -122.8088 | 62.2925 | 122.7814 | 62.352 | -0.15106
2393.8281 | 122.9507 | -62.3749 | 60.4477 | -0.052796 | -0.0018649 | -0.0074961 | 2.893 | 0.0030335 | -0.0016322 | -0.0028989 | -0.14371 | 0.1648 | 0.12559 | 0.0017602 | 0.057106 | 0.10585 | 0.0013415 | -0.073242 | 0.041199 | -0.1236 | -0.14191 | -0.045776 | -0.15106 | -0.09613 | -62.5763 | 60.4065 | -62.3657 | 60.4111 | 60.4614 | 60.2509 | 0.31586 | 62.2513 | -60.4065 | -60.5896 | 62.3291 | 62.2787 | 62.2238 | 0.027466 | -0.027466 | 0.009155 | -0.041199 | -0.036621 | 122.8363 | 62.6907 | 122.6257 | 62.6816 | 122.6166 | 0.07782 | -0.018311 | 122.8271 | 122.7768 | 0.16479 | 122.7722 | 62.4161 | 122.7814 | -60.5713 | -122.8134 | 62.233 | 122.7859 | 62.3016 | -0.20142
2394.8281 | 123.0148 | -62.3108 | 60.4614 | -0.029907 | 0.00027134 | -0.0064279 | 2.8924 | 4.2692e-05 | -0.0012048 | -0.0016171 | -0.12234 | 0.1663 | 0.12986 | -0.0076392 | 0.056251 | 0.10521 | -0.0018629 | 0.013733 | 0.13275 | -0.041199 | -0.041199 | 0.073242 | 0 | 0.036621 | -62.5031 | 60.4156 | -62.3657 | 60.466 | 60.5438 | 60.3745 | 0.46692 | 62.2696 | -60.3287 | -60.5026 | 62.384 | 62.3474 | 62.3108 | 0.07782 | 0.041199 | -0.054932 | -0.045777 | 0.004577 | 122.8546 | 62.7777 | 122.6852 | 62.8326 | 122.7402 | 0.11444 | 0 | 122.9095 | 122.8317 | 0.17395 | 122.7814 | 62.4435 | 122.7264 | -60.5026 | -122.8271 | 62.2696 | 122.7768 | 62.3245 | -0.19226
2395.8906 | 123.0286 | -62.3428 | 60.434 | -0.075684 | 0.00027134 | -0.010059 | 2.8926 | -0.00059811 | -0.0020594 | -0.0031125 | -0.052155 | 0.16395 | 0.12944 | -0.0044348 | 0.055824 | 0.10436 | 0.0015551 | -0.091553 | 0.009155 | -0.11444 | -0.09613 | -0.018311 | -0.11444 | 0 | -62.4756 | 60.3699 | -62.3611 | 60.4523 | 60.5484 | 60.379 | 0.39825 | 62.2284 | -60.4248 | -60.5301 | 62.3245 | 62.3428 | 62.2284 | 0.11444 | 0 | -0.018311 | -0.064087 | 0.018311 | 122.8912 | 62.7411 | 122.7219 | 62.7594 | 122.7402 | 0.09613 | 0.018311 | 122.9095 | 122.8134 | 0.1236 | 122.731 | 62.352 | 122.7127 | -60.5484 | -122.7951 | 62.2467 | 122.7951 | 62.2513 | -0.13275
2396.8281 | 122.9736 | -62.3154 | 60.4431 | -0.007019 | -0.00079686 | -0.0094187 | 2.8918 | 4.2692e-05 | -0.003982 | -0.00012167 | -0.14981 | 0.1648 | 0.1288 | -0.0027258 | 0.056465 | 0.10415 | -0.0016493 | -0.018311 | 0.073242 | -0.09613 | -0.050354 | 0.082397 | -0.041199 | -0.018311 | -62.4664 | 60.4065 | -62.3703 | 60.4523 | 60.5209 | 60.3287 | 0.41199 | 62.2192 | -60.3699 | -60.4935 | 62.3978 | 62.2971 | 62.2742 | 0.077819 | 0.054931 | -0.054931 | -0.036621 | 0.009156 | 122.8363 | 62.7274 | 122.644 | 62.7823 | 122.699 | 0.17853 | 0.045776 | 122.8912 | 122.8226 | 0.16937 | 122.7768 | 62.3886 | 122.7219 | -60.5392 | -122.8134 | 62.265 | 122.7676 | 62.2971 | -0.15106
2397.8906 | 123.0194 | -62.3383 | 60.466 | -0.052796 | -0.00079686 | -0.0092051 | 2.8924 | 0.00068369 | -0.00013676 | -0.0048215 | -0.046051 | 0.16331 | 0.1273 | -0.012339 | 0.054969 | 0.10393 | -0.0016493 | 0.054932 | 0.082397 | -0.041199 | 0.032043 | 0.13733 | 0.054932 | 0.082397 | -62.4298 | 60.3973 | -62.3474 | 60.4797 | 60.5713 | 60.4156 | 0.51727 | 62.2971 | -60.3836 | -60.434 | 62.4756 | 62.4207 | 62.3932 | 0.1236 | 0.096131 | -0.009155 | -0.068664 | 0.013733 | 122.9095 | 62.8555 | 122.7539 | 62.8647 | 122.7631 | 0.17853 | 0.073242 | 122.9187 | 122.8271 | 0.1236 | 122.7448 | 62.4207 | 122.7356 | -60.5072 | -122.8134 | 62.3703 | 122.818 | 62.3932 | -0.091553
2398.8281 | 123.0103 | -62.3383 | 60.4568 | -0.060425 | -0.0014377 | -0.0089913 | 2.8937 | -0.00017091 | -0.0027002 | -0.0024717 | -0.1376 | 0.1663 | 0.12751 | 0.0017602 | 0.054756 | 0.10372 | -0.0022901 | 0.004578 | 0.064087 | -0.07782 | -0.064087 | 0.041199 | -0.068665 | -0.004578 | -62.4985 | 60.379 | -62.3886 | 60.4614 | 60.5301 | 60.3333 | 0.4303 | 62.2604 | -60.3928 | -60.5209 | 62.3795 | 62.3337 | 62.2696 | 0.073242 | 0.009155 | -0.050354 | -0.07782 | 0.004578 | 122.8683 | 62.7686 | 122.6715 | 62.8189 | 122.7219 | 0.11902 | 0.013733 | 122.9187 | 122.85 | 0.14191 | 122.7676 | 62.4023 | 122.7173 | -60.5347 | -122.8455 | 62.2742 | 122.7997 | 62.3428 | -0.16022
2399.8906 | 122.9691 | -62.3474 | 60.4935 | -0.060425 | -0.0020785 | -0.0107 | 2.8924 | -0.0020935 | -0.0031274 | -0.0035397 | -0.070465 | 0.16459 | 0.12965 | -0.0055028 | 0.05561 | 0.10585 | 0.00091433 | 0.004578 | 0.16022 | -0.036621 | -0.032043 | 0.045776 | -0.022888 | 0.036621 | -62.4985 | 60.4614 | -62.3245 | 60.3973 | 60.5118 | 60.3378 | 0.46234 | 62.3108 | -60.3333 | -60.5255 | 62.3932 | 62.384 | 62.3245 | 0.073242 | 0.013733 | 0.022888 | -0.032043 | -0.09613 | 122.8592 | 62.8098 | 122.6852 | 62.7869 | 122.6624 | 0.082397 | 0.004578 | 122.8363 | 122.7219 | 0.19684 | 122.7859 | 62.5076 | 122.8088 | -60.5301 | -122.818 | 62.3154 | 122.7448 | 62.352 | -0.15106
2400.8281 | 123.0469 | -62.352 | 60.4706 | -0.052796 | -0.0020785 | -0.010273 | 2.8926 | -0.00038451 | -0.0027002 | -0.00033547 | -0.13455 | 0.16523 | 0.12858 | -0.0022986 | 0.057106 | 0.105 | -0.0022901 | 0.018311 | 0.07782 | -0.068665 | -0.036621 | 0.050354 | -0.050354 | -0.013733 | -62.4664 | 60.3928 | -62.3703 | 60.466 | 60.4568 | 60.2463 | 0.33417 | 62.2833 | -60.3928 | -60.5072 | 62.4023 | 62.3383 | 62.3016 | 0.054932 | 0.018311 | -0.01831 | -0.07782 | -0.004578 | 122.8088 | 62.6862 | 122.5983 | 62.7045 | 122.6166 | 0.11902 | 0.032044 | 122.8271 | 122.8363 | 0.14649 | 122.7631 | 62.4298 | 122.7448 | -60.5392 | -122.8409 | 62.3154 | 122.818 | 62.3703 | -0.11444
2401.8906 | 123.0377 | -62.3062 | 60.4431 | -0.045166 | 0.00048494 | -0.0081369 | 2.8913 | -0.00017091 | -0.002273 | -0.0014035 | -0.036896 | 0.16202 | 0.12751 | -0.0057166 | 0.057106 | 0.10329 | -0.00036747 | -0.022888 | 0.082397 | -0.004578 | -0.064087 | -0.009155 | 0.09613 | 0.09613 | -62.3795 | 60.3745 | -62.3154 | 60.5209 | 60.6262 | 60.4568 | 0.52643 | 62.3016 | -60.3607 | -60.5072 | 62.2971 | 62.4023 | 62.4023 | 0.10071 | 0.10071 | -0.009156 | -0.068664 | 0.07782 | 122.9324 | 62.8326 | 122.7631 | 62.8418 | 122.7722 | -0.004577 | -0.059509 | 122.9416 | 122.8363 | 0.086975 | 122.6898 | 62.3886 | 122.6807 | -60.4477 | -122.7585 | 62.2421 | 122.8271 | 62.2833 | -0.073243
2402.8281 | 123.0103 | -62.3474 | 60.4568 | -0.068054 | 5.7742e-05 | -0.0096323 | 2.8939 | 0.00089729 | -0.0024866 | -0.0024717 | -0.14371 | 0.16566 | 0.12602 | -0.0061438 | 0.056251 | 0.10457 | -0.0025037 | -0.018311 | 0.064087 | -0.073242 | -0.036621 | 0.073242 | -0.045776 | -0.018311 | -62.4756 | 60.4111 | -62.3749 | 60.4568 | 60.5118 | 60.3424 | 0.41657 | 62.2742 | -60.3928 | -60.4935 | 62.4207 | 62.3291 | 62.3016 | 0.054931 | 0.027466 | -0.027466 | -0.045776 | 0 | 122.8592 | 62.764 | 122.6898 | 62.7914 | 122.7173 | 0.14648 | 0.036621 | 122.8867 | 122.8317 | 0.13733 | 122.7859 | 62.4115 | 122.7585 | -60.5301 | -122.8317 | 62.3108 | 122.8043 | 62.3291 | -0.12817
2403.8906 | 122.9507 | -62.3566 | 60.4797 | -0.007019 | -0.00015586 | -0.0087777 | 2.8941 | -0.00038451 | -0.0059046 | -0.0073849 | -0.10709 | 0.16373 | 0.12815 | -0.0063574 | 0.053474 | 0.10265 | 0.00048713 | 0.013733 | 0.15564 | -0.027466 | 0.36163 | -0.11902 | -0.28381 | 0.004578 | -62.5076 | 60.4523 | -62.3657 | 60.4385 | 60.5072 | 60.3333 | 0.45319 | 62.3291 | -60.3241 | -60.1181 | 62.2375 | 62.3611 | 62.0728 | 0.032044 | -0.25635 | -0.009156 | -0.027465 | -0.041198 | 122.8638 | 62.8098 | 122.6898 | 62.8189 | 122.699 | -0.091553 | 0.3891 | 122.8729 | 122.8043 | 0.18311 | 122.818 | 62.5122 | 122.8088 | -60.5072 | -122.8455 | 62.7182 | 122.7951 | 62.3703 | -0.15106
2404.8281 | 122.9874 | -62.3337 | 60.4614 | 0.015869 | -0.0014377 | -0.0098459 | 2.8952 | 0.0066651 | -0.002273 | -0.0035397 | -0.14066 | 0.16245 | 0.12901 | -0.0044348 | 0.051979 | 0.1035 | -0.0035719 | -0.032043 | 0.068665 | -0.086975 | -0.10529 | 0.004578 | -0.11902 | -0.054932 | -62.5076 | 60.3973 | -62.3657 | 60.4202 | 60.4843 | 60.3104 | 0.3891 | 62.2467 | -60.3928 | -60.5667 | 62.3383 | 62.2787 | 62.2147 | 0.032043 | -0.032044 | -0.032044 | -0.064087 | -0.041199 | 122.818 | 62.7228 | 122.644 | 62.7548 | 122.6761 | 0.091553 | -0.018311 | 122.85 | 122.7859 | 0.15564 | 122.7631 | 62.4023 | 122.731 | -60.5484 | -122.8271 | 62.2284 | 122.7539 | 62.3016 | -0.17395
2405.8906 | 123.0423 | -62.3245 | 60.4385 | -0.12146 | 0.00091214 | -0.0092051 | 2.8928 | 0.0013245 | -0.0014184 | -0.0028989 | -0.024689 | 0.16224 | 0.12559 | -0.00058965 | 0.055183 | 0.1035 | 0.0011279 | 0.032043 | 0.064087 | -0.054932 | 0.036621 | 0.16479 | 0.050354 | 0.086975 | -62.4023 | 60.3745 | -62.3291 | 60.5026 | 60.5942 | 60.4385 | 0.52185 | 62.2696 | -60.3745 | -60.4019 | 62.4893 | 62.4115 | 62.3749 | 0.14191 | 0.10529 | -0.004578 | -0.064087 | 0.064087 | 122.9187 | 62.8464 | 122.7631 | 62.851 | 122.7676 | 0.21973 | 0.091553 | 122.9233 | 122.8317 | 0.11902 | 122.7036 | 62.3886 | 122.699 | -60.4935 | -122.7676 | 62.3611 | 122.8271 | 62.3566 | -0.07782
2406.8281 | 123.0057 | -62.3474 | 60.4523 | -0.022278 | -0.0010105 | -0.0087777 | 2.8935 | 0.0017517 | -0.0016322 | -0.0033261 | -0.11929 | 0.16566 | 0.12773 | 0.001974 | 0.054115 | 0.10372 | -0.00015387 | 0.013733 | 0.086975 | -0.068665 | -0.032043 | 0.054932 | -0.050354 | 0.009155 | -62.4664 | 60.3882 | -62.3474 | 60.4752 | 60.5255 | 60.3607 | 0.45776 | 62.2787 | -60.3653 | -60.4843 | 62.4023 | 62.3566 | 62.2971 | 0.07782 | 0.018311 | 0 | -0.064087 | 0.022888 | 122.8729 | 62.8052 | 122.7081 | 62.8052 | 122.7081 | 0.1236 | 0.036622 | 122.8729 | 122.8226 | 0.15564 | 122.7356 | 62.4344 | 122.7356 | -60.5209 | -122.7997 | 62.3154 | 122.8226 | 62.3611 | -0.11902
2407.8906 | 122.9874 | -62.3154 | 60.466 | -0.007019 | 0.0011257 | -0.0094187 | 2.8935 | -0.0025207 | -0.00013676 | -0.0022581 | -0.10709 | 0.16309 | 0.12538 | -0.00828 | 0.055397 | 0.10244 | -0.0016493 | -0.082397 | 0.19684 | 0.009155 | -0.07782 | 0.041199 | -0.045776 | 0 | -62.5351 | 60.4111 | -62.352 | 60.4294 | 60.5209 | 60.3195 | 0.46234 | 62.3245 | -60.2692 | -60.5438 | 62.3566 | 62.3154 | 62.2696 | -0.009155 | -0.054931 | -0.036621 | -0.054931 | -0.036621 | 122.8363 | 62.7777 | 122.6349 | 62.8143 | 122.6715 | 0.032044 | -0.086975 | 122.8729 | 122.7814 | 0.18768 | 122.7631 | 62.5122 | 122.7264 | -60.4568 | -122.818 | 62.2375 | 122.7448 | 62.233 | -0.21973
2408.8281 | 123.0148 | -62.3291 | 60.4568 | -0.052796 | -0.00079686 | -0.0083505 | 2.8945 | 0.0028199 | -0.0035548 | -0.0031125 | -0.1254 | 0.16416 | 0.12815 | -0.0067846 | 0.054329 | 0.10415 | 0.00070073 | 0.027466 | 0.10986 | -0.064087 | -0.050354 | 0.054932 | -0.027466 | 0.009155 | -62.4664 | 60.4156 | -62.3657 | 60.466 | 60.5347 | 60.3607 | 0.44403 | 62.265 | -60.347 | -60.5072 | 62.384 | 62.3383 | 62.3016 | 0.073242 | 0.036621 | -0.036621 | -0.041199 | 0.009155 | 122.8638 | 62.7731 | 122.6898 | 62.8098 | 122.7264 | 0.11902 | 0.013733 | 122.9004 | 122.8317 | 0.17395 | 122.7814 | 62.439 | 122.7448 | -60.5209 | -122.8226 | 62.2787 | 122.7951 | 62.3566 | -0.13733
2409.8906 | 123.0835 | -62.3108 | 60.4156 | -0.045166 | 0.00048494 | -0.0081369 | 2.892 | -0.00081171 | 0.0015722 | -0.0028989 | 0.16452 | 0.1616 | 0.12965 | -0.0033666 | 0.054969 | 0.10329 | -0.0016493 | 0.054932 | 0.09613 | -0.022888 | 0.059509 | 0.1831 | 0.064087 | 0.091553 | -62.5992 | 60.4065 | -62.3291 | 60.5301 | 60.5713 | 60.4614 | 0.54474 | 62.2879 | -60.3195 | -60.3561 | 62.4939 | 62.4023 | 62.3749 | 0.11444 | 0.086975 | -0.018311 | -0.009155 | 0.11444 | 122.8821 | 62.8555 | 122.7722 | 62.8738 | 122.7905 | 0.20599 | 0.082397 | 122.9004 | 122.8592 | 0.11902 | 122.7356 | 62.4069 | 122.7173 | -60.4385 | -122.7448 | 62.3703 | 122.8409 | 62.3657 | -0.28839
2410.8281 | 122.9919 | -62.3245 | 60.4706 | 0.00061049 | -0.00015586 | -0.0089913 | 2.8939 | 0.0017517 | 0.001145 | -0.0020443 | -0.13455 | 0.16437 | 0.12773 | -0.0018712 | 0.056892 | 0.10607 | 0.00048713 | 0.013733 | 0.09613 | -0.09613 | -0.064087 | 0.045776 | -0.064087 | -0.009155 | -62.5854 | 60.3882 | -62.3657 | 60.466 | 60.5209 | 60.3378 | 0.44861 | 62.2284 | -60.3745 | -60.5347 | 62.3703 | 62.3154 | 62.2604 | 0.086975 | 0.032043 | -0.041199 | -0.082397 | -0.004578 | 122.8455 | 62.7731 | 122.6624 | 62.8143 | 122.7036 | 0.14191 | 0.032043 | 122.8867 | 122.8317 | 0.19226 | 122.7539 | 62.4207 | 122.7127 | -60.5667 | -122.8363 | 62.2604 | 122.7905 | 62.3383 | -0.26093
2411.8906 | 123.0331 | -62.3062 | 60.4706 | -0.037537 | 0.00027134 | -0.0092051 | 2.8935 | -0.0027343 | -0.0063318 | -0.0011899 | -0.030792 | 0.16309 | 0.13115 | -0.0091344 | 0.056251 | 0.10308 | 0.00091433 | 0.018311 | 0.064087 | -0.064087 | 0.027466 | 0.13733 | 0.036621 | 0.09613 | -62.4252 | 60.3928 | -62.3428 | 60.498 | 60.5942 | 60.4202 | 0.54016 | 62.2421 | -60.4065 | -60.4431 | 62.4435 | 62.4023 | 62.3428 | 0.16022 | 0.10071 | -0.036621 | -0.07782 | 0.027466 | 122.9004 | 62.8464 | 122.7264 | 62.883 | 122.7631 | 0.20142 | 0.091553 | 122.937 | 122.8409 | 0.12817 | 122.7356 | 62.3703 | 122.699 | -60.5347 | -122.8134 | 62.3337 | 122.8043 | 62.3245 | -0.11902
2412.8281 | 123.0148 | -62.3337 | 60.4523 | -0.037537 | 0.0019803 | -0.0096323 | 2.8941 | 0.0036743 | -0.0014184 | -0.0022581 | -0.11929 | 0.16437 | 0.12773 | -0.004862 | 0.054969 | 0.10393 | -0.00058107 | 0.013733 | 0.086975 | -0.082397 | -0.036621 | 0.041199 | -0.050354 | 0.004578 | -62.4435 | 60.4156 | -62.3428 | 60.4568 | 60.498 | 60.2463 | 0.36621 | 62.2513 | -60.3653 | -60.4889 | 62.3749 | 62.3383 | 62.2833 | 0.086975 | 0.032043 | -0.009155 | -0.036622 | 0.004577 | 122.8317 | 62.6999 | 122.58 | 62.709 | 122.5891 | 0.1236 | 0.045776 | 122.8409 | 122.7997 | 0.16937 | 122.7585 | 62.4207 | 122.7493 | -60.5347 | -122.7951 | 62.2971 | 122.7905 | 62.3474 | -0.10986
2413.8906 | 123.0789 | -62.3199 | 60.4202 | 0.10742 | 5.7742e-05 | -0.0055735 | 2.893 | -0.00038451 | 0.0017858 | -0.0031125 | -0.049103 | 0.16459 | 0.12858 | -0.0080664 | 0.057106 | 0.10436 | -0.0042127 | -0.35248 | 0.11902 | 0.009155 | 0.018311 | 0.10986 | 0.091553 | 0.10071 | -62.3886 | 60.3928 | -62.3657 | 60.5209 | 60.6125 | 60.4431 | 0.52643 | 62.3291 | -60.3012 | -60.4019 | 62.4298 | 62.4207 | 62.4115 | 0.091553 | 0.082398 | -0.045777 | -0.027466 | 0.10071 | 122.9324 | 62.8464 | 122.7631 | 62.8922 | 122.8088 | 0.10071 | 0.009156 | 122.9782 | 122.8867 | 0.10986 | 122.7585 | 62.439 | 122.7127 | -60.4111 | -122.7859 | 62.3383 | 122.8409 | 61.9675 | -0.068665
2414.8281 | 122.9691 | -62.3383 | 60.466 | 0.00061049 | -0.0020785 | -0.0085641 | 2.8935 | 0.0036743 | -0.00035036 | -0.00097627 | -0.14676 | 0.16331 | 0.12623 | -0.0042212 | 0.056465 | 0.10479 | -0.0016493 | -0.013733 | 0.045776 | -0.10529 | -0.059509 | 0.050354 | -0.073242 | -0.036621 | -62.471 | 60.4156 | -62.3657 | 60.4431 | 60.5072 | 60.3104 | 0.41199 | 62.233 | -60.4202 | -60.5255 | 62.3886 | 62.3016 | 62.265 | 0.068665 | 0.032044 | -0.027466 | -0.050354 | -0.022888 | 122.8455 | 62.7502 | 122.6486 | 62.7777 | 122.6761 | 0.15564 | 0.045777 | 122.8729 | 122.8088 | 0.15106 | 122.7814 | 62.384 | 122.7539 | -60.5713 | -122.8317 | 62.2787 | 122.7814 | 62.3245 | -0.13275
2415.8906 | 123.0377 | -62.3428 | 60.4385 | -0.029907 | -0.0018649 | -0.0094187 | 2.8915 | -0.00059811 | 0.00071784 | -0.0020443 | -0.082672 | 0.16267 | 0.12751 | -0.0084936 | 0.056465 | 0.10244 | 0.0017687 | -0.041199 | 0.036621 | -0.073242 | -0.059509 | 0.041199 | -0.013733 | 0.23804 | -62.4619 | 60.379 | -62.352 | 60.4614 | 60.5438 | 60.3882 | 0.42572 | 62.2696 | -60.4019 | -60.498 | 62.384 | 62.5809 | 62.3291 | 0.31128 | 0.059509 | -0.009156 | -0.05951 | 0.022888 | 122.8867 | 62.7686 | 122.731 | 62.7777 | 122.7402 | 0.11444 | 0.013733 | 122.8958 | 122.8134 | 0.10986 | 122.731 | 62.3795 | 122.7219 | -60.5118 | -122.7905 | 62.2833 | 122.8043 | 62.3016 | -0.11902
2416.8281 | 123.0148 | -62.352 | 60.4477 | -0.007019 | -0.0033603 | -0.0089913 | 2.895 | 0.0055969 | 0.00029044 | -0.0024717 | -0.1254 | 0.16416 | 0.12623 | -0.00080325 | 0.054969 | 0.10543 | -0.00036747 | -0.018311 | 0.073242 | -0.10529 | -0.018311 | 0.045776 | -0.050354 | -0.032043 | -62.4573 | 60.4156 | -62.3566 | 60.4752 | 60.5118 | 60.3424 | 0.42114 | 62.2467 | -60.3745 | -60.466 | 62.3978 | 62.3199 | 62.3016 | 0.073243 | 0.054932 | -0.004577 | -0.032044 | 0.027466 | 122.8638 | 62.7731 | 122.6944 | 62.7777 | 122.699 | 0.15106 | 0.086975 | 122.8683 | 122.8317 | 0.17853 | 122.7722 | 62.4252 | 122.7676 | -60.553 | -122.8043 | 62.3337 | 122.8271 | 62.3337 | -0.10529
2417.8906 | 122.9691 | -62.3383 | 60.4568 | -0.11383 | 0.00069854 | -0.0089913 | 2.8907 | -0.0023071 | -0.0016322 | -0.0039671 | -0.058258 | 0.16288 | 0.1273 | 0.00090575 | 0.05561 | 0.1035 | 0.0013415 | 0.032043 | 0.12817 | -0.050354 | -0.027466 | 0.045776 | -0.027466 | 0.018311 | -62.5168 | 60.4385 | -62.3657 | 60.4202 | 60.5209 | 60.3149 | 0.46234 | 62.2879 | -60.3287 | -60.4843 | 62.384 | 62.3566 | 62.3108 | 0.068665 | 0.022888 | -0.027466 | -0.01831 | -0.036621 | 122.8592 | 62.8006 | 122.6532 | 62.8281 | 122.6807 | 0.09613 | 0.022888 | 122.8867 | 122.7859 | 0.17853 | 122.8043 | 62.4664 | 122.7768 | -60.5072 | -122.8226 | 62.3108 | 122.7585 | 62.3703 | -0.17853
2418.8281 | 122.9736 | -62.3566 | 60.4797 | -0.083313 | -0.0010105 | -0.0087777 | 2.8947 | 0.0041015 | 0.0032812 | -0.0041807 | -0.1254 | 0.16459 | 0.12687 | -0.0035802 | 0.055397 | 0.10372 | 0.0019823 | -0.013733 | 0.07782 | -0.09613 | -0.13275 | 0.21057 | -0.036621 | 0.004578 | -62.4619 | 60.4202 | -62.3474 | 60.4568 | 60.5209 | 60.3333 | 0.42114 | 62.2604 | -60.4019 | -60.6125 | 62.5671 | 62.3611 | 62.3199 | 0.10071 | 0.059509 | 0.009155 | -0.059509 | -0.022888 | 122.8775 | 62.7777 | 122.6898 | 62.7686 | 122.6807 | 0.3067 | -0.036621 | 122.8683 | 122.8043 | 0.17395 | 122.7676 | 62.4344 | 122.7768 | -60.5759 | -122.8271 | 62.2238 | 122.8134 | 62.3428 | -0.10529
2419.8906 | 123.0103 | -62.3383 | 60.4706 | -0.083313 | -0.0018649 | -0.0083505 | 2.8918 | 0.0049561 | -0.00056396 | -0.0039671 | -0.052155 | 0.16331 | 0.12965 | -0.0055028 | 0.056465 | 0.10222 | -0.0029309 | 0.059509 | 0.064087 | -0.032043 | 0.027466 | 0.14191 | 0.050354 | 0.09613 | -62.4344 | 60.3928 | -62.3611 | 60.5072 | 60.5896 | 60.3973 | 0.51727 | 62.3062 | -60.4065 | -60.4431 | 62.4802 | 62.4344 | 62.3886 | 0.12817 | 0.082397 | -0.022888 | -0.07782 | 0.036621 | 122.9279 | 62.8555 | 122.7356 | 62.8784 | 122.7585 | 0.17395 | 0.059509 | 122.9507 | 122.8683 | 0.09613 | 122.7539 | 62.4023 | 122.731 | -60.5026 | -122.8317 | 62.3657 | 122.8455 | 62.3978 | -0.09613
2420.8281 | 122.9599 | -62.3428 | 60.466 | -0.007019 | -0.0022923 | -0.0094187 | 2.8943 | 0.0028199 | -0.0031274 | -0.0018307 | -0.17117 | 0.16566 | 0.12815 | 0.0032556 | 0.054756 | 0.10479 | -0.0042127 | -0.050354 | 0.07782 | -0.11902 | -0.091553 | -0.009155 | -0.12817 | -0.064087 | -62.5168 | 60.4111 | -62.352 | 60.4248 | 60.4706 | 60.2875 | 0.35706 | 62.2238 | -60.3882 | -60.5576 | 62.3337 | 62.2787 | 62.2147 | 0.054932 | -0.009155 | -0.009156 | -0.054931 | -0.041198 | 122.8134 | 62.6999 | 122.6303 | 62.709 | 122.6395 | 0.10986 | 0.027466 | 122.8226 | 122.7768 | 0.19684 | 122.7631 | 62.4207 | 122.7539 | -60.585 | -122.818 | 62.2513 | 122.7676 | 62.2925 | -0.17395
2421.8906 | 122.9782 | -62.3657 | 60.498 | -0.037537 | -0.0010105 | -0.010914 | 2.8935 | 0.00025629 | -0.0018458 | -0.0016171 | -0.073517 | 0.16416 | 0.12645 | -0.0089208 | 0.056892 | 0.10137 | 0.00091433 | 0.013733 | 0.10986 | -0.041199 | 0.045776 | 0.1236 | -0.064087 | 0.013733 | -62.5076 | 60.4294 | -62.3886 | 60.4065 | 60.5164 | 60.3378 | 0.48523 | 62.3245 | -60.3882 | -60.4523 | 62.4893 | 62.3795 | 62.3016 | 0.054932 | -0.022888 | -0.022888 | -0.068665 | -0.091553 | 122.8821 | 62.851 | 122.7036 | 62.8738 | 122.7264 | 0.16479 | 0.086975 | 122.905 | 122.7951 | 0.15106 | 122.818 | 62.4756 | 122.7951 | -60.5392 | -122.8867 | 62.4115 | 122.7722 | 62.3795 | -0.14191
2422.8281 | 123.0011 | -62.3337 | 60.4752 | -0.052796 | -0.0020785 | -0.0092051 | 2.8945 | 0.0021789 | 7.6842e-05 | -0.0024717 | -0.11319 | 0.16352 | 0.12815 | -0.004862 | 0.05561 | 0.10585 | -0.0012219 | 0 | 0.073242 | -0.073242 | -0.068665 | 0.064087 | -0.073242 | -0.14648 | -62.4893 | 60.4156 | -62.3932 | 60.4752 | 60.5209 | 60.3516 | 0.44403 | 62.2604 | -60.4019 | -60.5438 | 62.3978 | 62.1872 | 62.2604 | -0.073242 | 0 | -0.059509 | -0.05951 | 0 | 122.8546 | 62.7777 | 122.6852 | 62.8372 | 122.7448 | 0.13733 | 0.004577 | 122.9141 | 122.8683 | 0.14648 | 122.8088 | 62.4069 | 122.7493 | -60.5484 | -122.8683 | 62.265 | 122.8088 | 62.3337 | -0.15564
2423.8281 | 122.9736 | -62.352 | 60.4385 | -0.022278 | -0.0018649 | -0.0085641 | 2.8941 | 0.0023925 | 0.0015722 | -0.00033547 | -0.058258 | 0.16373 | 0.12965 | -0.0061438 | 0.056251 | 0.10479 | 0.0021961 | -0.10071 | 0.022888 | -0.14648 | -0.32501 | 0.39825 | -0.041199 | -0.17853 | -62.59 | 60.4019 | -62.3795 | 60.4156 | 60.4523 | 60.2646 | 0.32959 | 62.2055 | -60.4156 | -60.7636 | 62.7502 | 62.1735 | 62.3108 | -0.032044 | 0.10529 | -0.027466 | -0.036621 | -0.022889 | 122.8043 | 62.6816 | 122.6166 | 62.709 | 122.644 | 0.54474 | -0.17853 | 122.8317 | 122.7951 | 0.16937 | 122.7814 | 62.3749 | 122.7539 | -60.585 | -122.818 | 62.027 | 122.7676 | 62.2513 | -0.23804
2424.8281 | 122.9919 | -62.3199 | 60.4385 | 0.00061049 | -0.0012241 | -0.0081369 | 2.8947 | 0.0013245 | -0.0014184 | -0.0016171 | -0.13455 | 0.16459 | 0.12773 | 0.0024012 | 0.057319 | 0.10607 | -0.0031445 | -0.027466 | 0.068665 | -0.10986 | -0.07782 | 0.009155 | -0.10986 | -0.054932 | -62.5031 | 60.4202 | -62.384 | 60.434 | 60.498 | 60.2921 | 0.39368 | 62.2101 | -60.3699 | -60.5164 | 62.3291 | 62.265 | 62.2101 | 0.054931 | 0 | -0.064087 | -0.018311 | -0.004578 | 122.818 | 62.7136 | 122.612 | 62.7777 | 122.6761 | 0.11902 | 0.032043 | 122.8821 | 122.818 | 0.17853 | 122.8043 | 62.3886 | 122.7402 | -60.5484 | -122.8226 | 62.2421 | 122.7539 | 62.2925 | -0.18311
2425.8906 | 122.9782 | -62.3428 | 60.4706 | 0.00824 | -0.0014377 | -0.0087777 | 2.8905 | 0.00089729 | -0.00077756 | -0.0043943 | -0.027741 | 0.16288 | 0.12602 | -0.0087072 | 0.056038 | 0.10329 | -0.0048535 | 0.027466 | 0.10986 | -0.036621 | -0.018311 | 0.091553 | 0.004578 | 0.045776 | -62.4893 | 60.434 | -62.3566 | 60.4431 | 60.498 | 60.3516 | 0.48981 | 62.3062 | -60.3607 | -60.4889 | 62.4344 | 62.3886 | 62.3474 | 0.082397 | 0.041199 | -0.013733 | -0.036621 | -0.027466 | 122.8409 | 62.8326 | 122.6944 | 62.8464 | 122.7081 | 0.12817 | 0.01831 | 122.8546 | 122.7997 | 0.14648 | 122.7905 | 62.4527 | 122.7768 | -60.5072 | -122.8271 | 62.3245 | 122.7859 | 62.3703 | -0.14648
2426.8281 | 122.9736 | -62.3383 | 60.4523 | -0.060425 | -0.00036966 | -0.0094187 | 2.893 | 0.00025629 | 0.00029044 | -0.0011899 | -0.12845 | 0.16352 | 0.12794 | -0.0057166 | 0.05561 | 0.10564 | -0.0029309 | -0.022888 | 0.073242 | -0.09613 | -0.068665 | 0.036621 | -0.086975 | -0.036621 | -62.4939 | 60.4111 | -62.384 | 60.4431 | 60.4935 | 60.3012 | 0.40283 | 62.2421 | -60.379 | -60.5209 | 62.3749 | 62.3016 | 62.2513 | 0.059509 | 0.009155 | -0.045776 | -0.041199 | -0.009156 | 122.8317 | 62.7411 | 122.6395 | 62.7869 | 122.6852 | 0.13275 | 0.027465 | 122.8775 | 122.8271 | 0.16937 | 122.7951 | 62.4115 | 122.7493 | -60.5484 | -122.8363 | 62.2696 | 122.7814 | 62.3154 | -0.15564
2427.8906 | 123.0881 | -62.2879 | 60.4248 | -0.052796 | -0.00036966 | -0.0094187 | 2.8945 | 0.0047425 | -0.0016322 | -0.0039671 | -0.027741 | 0.16331 | 0.12837 | -0.011698 | 0.053901 | 0.10137 | -0.0012219 | 0.050354 | 0.059509 | -0.036621 | 0.054932 | 0.19226 | 0.07782 | 0.10529 | -62.352 | 60.3561 | -62.3383 | 60.5255 | 60.6445 | 60.4614 | 0.54474 | 62.2513 | -60.3653 | -60.3699 | 62.4802 | 62.3932 | 62.3657 | 0.14191 | 0.11444 | -0.050354 | -0.068665 | 0.10071 | 122.9324 | 62.8326 | 122.7493 | 62.883 | 122.7997 | 0.22888 | 0.091553 | 122.9828 | 122.8638 | 0.09613 | 122.6944 | 62.3474 | 122.644 | -60.4614 | -122.7631 | 62.3428 | 122.8134 | 62.3383 | -0.064087
2428.8281 | 122.9919 | -62.3428 | 60.4614 | -0.029907 | -0.00058326 | -0.0083505 | 2.8933 | 0.0058105 | -0.0016322 | -0.0022581 | -0.1376 | 0.16309 | 0.1288 | -0.0063574 | 0.05326 | 0.10393 | 0.00027333 | -0.004578 | 0.073242 | -0.09613 | -0.059509 | 0.022888 | -0.082397 | -0.032043 | -62.4756 | 60.4111 | -62.3703 | 60.4431 | 60.4889 | 60.3104 | 0.40283 | 62.2467 | -60.3882 | -60.5209 | 62.3657 | 62.3108 | 62.2604 | 0.064087 | 0.013733 | -0.027466 | -0.050354 | -0.018311 | 122.8317 | 62.7457 | 122.6532 | 62.7731 | 122.6807 | 0.11902 | 0.036621 | 122.8592 | 122.8134 | 0.16937 | 122.7814 | 62.4161 | 122.7539 | -60.5576 | -122.8317 | 62.2833 | 122.7859 | 62.3383 | -0.13275
2429.8906 | 122.9645 | -62.3383 | 60.4614 | -0.022278 | -0.0020785 | -0.0081369 | 2.892 | 0.00089729 | -0.0020594 | -0.00097627 | -0.042999 | 0.16331 | 0.12623 | -0.0061438 | 0.056251 | 0.10329 | 0.0015551 | 0.004578 | 0.15564 | -0.032043 | -0.036621 | 0.064087 | -0.022888 | 0.054932 | -62.5214 | 60.4202 | -62.3703 | 60.4294 | 60.5072 | 60.3287 | 0.47607 | 62.3062 | -60.3058 | -60.498 | 62.4023 | 62.3932 | 62.3154 | 0.086975 | 0.009155 | -0.032043 | -0.041199 | -0.032044 | 122.8455 | 62.8143 | 122.6669 | 62.8464 | 122.699 | 0.09613 | -0.004578 | 122.8775 | 122.7997 | 0.18768 | 122.7905 | 62.4939 | 122.7585 | -60.4935 | -122.8317 | 62.3016 | 122.7676 | 62.3428 | -0.18311
2430.8281 | 122.9874 | -62.3611 | 60.466 | -0.045166 | -0.0014377 | -0.0085641 | 2.8941 | 0.0023925 | -0.0018458 | -0.0011899 | -0.14676 | 0.16245 | 0.12666 | -0.00016245 | 0.054969 | 0.10543 | -0.0014355 | -0.036621 | 0.064087 | -0.11902 | -0.10529 | -0.018311 | -0.1236 | -0.082397 | -62.5259 | 60.4248 | -62.3749 | 60.4019 | 60.4568 | 60.2783 | 0.36163 | 62.2421 | -60.4019 | -60.5713 | 62.3428 | 62.2787 | 62.2375 | 0.036622 | -0.004577 | -0.013733 | -0.041198 | -0.064086 | 122.818 | 62.7228 | 122.6395 | 62.7365 | 122.6532 | 0.10071 | 0.013733 | 122.8317 | 122.7768 | 0.18311 | 122.7997 | 62.4252 | 122.7859 | -60.585 | -122.8409 | 62.2559 | 122.7631 | 62.3245 | -0.16479
2431.8906 | 122.9919 | -62.3383 | 60.466 | -0.052796 | -0.0016513 | -0.010059 | 2.8909 | -0.00017091 | -0.00013676 | -0.0018307 | -0.097931 | 0.16288 | 0.12687 | -0.00016245 | 0.054542 | 0.10393 | 0.0013415 | 0.027466 | 0.13733 | -0.041199 | -0.041199 | 0.050354 | -0.022888 | 0.027466 | -62.5076 | 60.4065 | -62.3657 | 60.4752 | 60.5301 | 60.3699 | 0.49439 | 62.2971 | -60.3287 | -60.5072 | 62.3886 | 62.3657 | 62.3154 | 0.068665 | 0.018311 | -0.027466 | -0.059509 | 0.009156 | 122.8683 | 62.8326 | 122.7081 | 62.8601 | 122.7356 | 0.091553 | 0 | 122.8958 | 122.8409 | 0.17853 | 122.7722 | 62.4756 | 122.7448 | -60.5072 | -122.8317 | 62.2971 | 122.8134 | 62.3657 | -0.16937
2432.8281 | 122.9599 | -62.352 | 60.4614 | -0.037537 | 5.7742e-05 | -0.0092051 | 2.8907 | 0.0023925 | -0.002273 | 0.00094633 | -0.14066 | 0.16331 | 0.13008 | -0.0061438 | 0.055183 | 0.10265 | 0.0013415 | -0.022888 | 0.068665 | -0.082397 | -0.10071 | -0.009155 | -0.1236 | -0.073242 | -62.5168 | 60.3928 | -62.3749 | 60.4294 | 60.4752 | 60.3149 | 0.37537 | 62.2696 | -60.3928 | -60.5621 | 62.3428 | 62.2787 | 62.2284 | 0.009155 | -0.041199 | -0.022888 | -0.068665 | -0.032044 | 122.8271 | 62.7274 | 122.6669 | 62.7502 | 122.6898 | 0.073242 | -0.018311 | 122.85 | 122.8043 | 0.15106 | 122.7676 | 62.4207 | 122.7448 | -60.5438 | -122.8363 | 62.2513 | 122.7814 | 62.3291 | -0.16479
2433.8906 | 122.9965 | -62.3291 | 60.4935 | 0.00061049 | -0.00079686 | -0.0079233 | 2.8935 | -0.0016663 | -0.0012048 | -0.0052487 | -0.07962 | 0.16395 | 0.12944 | -0.0040076 | 0.054756 | 0.10543 | -0.00058107 | 0.022888 | 0.12817 | -0.050354 | -0.050354 | 0.036621 | -0.036621 | 0.004578 | -62.5122 | 60.4385 | -62.384 | 60.4431 | 60.5392 | 60.3607 | 0.47607 | 62.2787 | -60.3653 | -60.5438 | 62.3657 | 62.3337 | 62.2925 | 0.054932 | 0.013733 | -0.054931 | -0.054931 | -0.050354 | 122.8683 | 62.8052 | 122.6898 | 62.8601 | 122.7448 | 0.086975 | 0 | 122.9233 | 122.8271 | 0.17853 | 122.8226 | 62.4573 | 122.7676 | -60.5438 | -122.8775 | 62.2787 | 122.7722 | 62.352 | -0.1831
2434.8281 | 122.9645 | -62.3566 | 60.4568 | -0.045166 | 0.00027134 | -0.0077097 | 2.896 | 0.0026063 | -0.0048364 | -0.00076267 | -0.12234 | 0.16416 | 0.12709 | -0.004862 | 0.057319 | 0.10521 | -0.0025037 | -0.059509 | 0.068665 | -0.11444 | -0.15106 | -0.064087 | -0.13733 | -0.082397 | -62.5809 | 60.4019 | -62.3886 | 60.3836 | 60.4477 | 60.2829 | 0.33417 | 62.2421 | -60.3882 | -60.6079 | 62.2925 | 62.2742 | 62.2192 | 0.032044 | -0.022888 | -0.032044 | -0.054931 | -0.073242 | 122.8043 | 62.6907 | 122.6395 | 62.7228 | 122.6715 | 0.050354 | -0.036621 | 122.8363 | 122.7722 | 0.18311 | 122.7905 | 62.4252 | 122.7585 | -60.5713 | -122.8455 | 62.2055 | 122.7402 | 62.2971 | -0.22431
2435.8906 | 122.9965 | -62.3337 | 60.498 | -0.014649 | -0.0016513 | -0.0089913 | 2.892 | 4.2692e-05 | -0.0035548 | -0.0031125 | -0.064362 | 0.16245 | 0.13008 | -0.003794 | 0.056038 | 0.10158 | 0.00070073 | -0.004578 | 0.14191 | -0.059509 | -0.050354 | 0.054932 | -0.027466 | 0.027466 | -62.5351 | 60.434 | -62.3611 | 60.4202 | 60.4935 | 60.3287 | 0.68207 | 62.2742 | -60.3561 | -60.5484 | 62.3886 | 62.3611 | 62.3062 | 0.086975 | 0.032043 | -0.027466 | -0.064087 | -0.07782 | 122.8271 | 63.0157 | 122.6624 | 63.0432 | 122.6898 | 0.11444 | 0.009155 | 122.8546 | 122.7814 | 0.20142 | 122.7951 | 62.4756 | 122.7676 | -60.5576 | -122.8592 | 62.2833 | 122.7539 | 62.3291 | -0.20142
2436.8281 | 122.9919 | -62.3337 | 60.4752 | -0.11383 | 0.00048494 | -0.0079233 | 2.8933 | 0.0049561 | -0.0027002 | -0.0011899 | -0.1376 | 0.16416 | 0.12751 | -0.003794 | 0.055824 | 0.10415 | 0.00070073 | -0.14191 | 0.050354 | -0.10529 | -0.068665 | 0.054932 | -0.059509 | -0.009155 | -62.4664 | 60.4385 | -62.3383 | 60.4294 | 60.5118 | 60.3241 | 0.43488 | 62.2284 | -60.4248 | -60.5438 | 62.3886 | 62.3245 | 62.2742 | 0.096131 | 0.045777 | -0.004578 | -0.036621 | -0.045777 | 122.8455 | 62.7686 | 122.6578 | 62.7731 | 122.6624 | 0.16022 | 0.036621 | 122.85 | 122.7676 | 0.15564 | 122.7768 | 62.384 | 122.7722 | -60.5804 | -122.8134 | 62.265 | 122.7631 | 62.1918 | -0.13275
2437.8906 | 123.0011 | -62.3245 | 60.4568 | -0.037537 | 0.00069854 | -0.0081369 | 2.8933 | 4.2692e-05 | -0.003982 | -0.0024717 | -0.10709 | 0.16352 | 0.12495 | -0.0035802 | 0.055183 | 0.10415 | -0.0012219 | 0.018311 | 0.09613 | -0.050354 | -0.036621 | 0.064087 | -0.045776 | -0.009155 | -62.4756 | 60.3928 | -62.3474 | 60.4614 | 60.5438 | 60.3516 | 0.45776 | 62.2742 | -60.3607 | -60.4935 | 62.3886 | 62.3154 | 62.2787 | 0.041199 | 0.004578 | -0.022888 | -0.064087 | 0.004578 | 122.8683 | 62.7823 | 122.6761 | 62.8052 | 122.699 | 0.11444 | 0.013733 | 122.8912 | 122.8088 | 0.14648 | 122.7402 | 62.4207 | 122.7173 | -60.5072 | -122.8043 | 62.2879 | 122.7859 | 62.3428 | -0.15106
2438.8281 | 122.9828 | -62.3383 | 60.4614 | -0.037537 | -0.0014377 | -0.0089913 | 2.8933 | 0.0038879 | -0.0031274 | -0.0016171 | -0.10098 | 0.16416 | 0.12709 | -0.0025122 | 0.056892 | 0.1035 | -0.0018629 | -0.041199 | 0.073242 | -0.091553 | -0.10529 | 0 | -0.10529 | -0.054932 | -62.5351 | 60.4202 | -62.3886 | 60.4294 | 60.4935 | 60.2829 | 0.3891 | 62.2467 | -60.3882 | -60.5667 | 62.3383 | 62.2833 | 62.233 | 0.036621 | -0.013733 | -0.050354 | -0.041199 | -0.032044 | 122.8317 | 62.7274 | 122.6212 | 62.7777 | 122.6715 | 0.091553 | -0.013733 | 122.8821 | 122.818 | 0.16479 | 122.8088 | 62.4115 | 122.7585 | -60.553 | -122.85 | 62.233 | 122.7676 | 62.2971 | -0.19684
2439.8906 | 123.111 | -62.2833 | 60.4294 | -0.022278 | -0.0037875 | -0.0077097 | 2.8905 | -0.0020935 | -0.0027002 | -0.0022581 | 0.018036 | 0.16416 | 0.1305 | -0.0033666 | 0.056892 | 0.10115 | -0.00058107 | 0.004578 | 0.059509 | -0.059509 | -0.004578 | 0.13275 | 0.045776 | 0.082397 | -62.3978 | 60.3745 | -62.3474 | 60.5164 | 60.6308 | 60.4797 | 0.54016 | 62.2238 | -60.3699 | -60.434 | 62.4161 | 62.3657 | 62.3291 | 0.14191 | 0.10528 | -0.064087 | -0.054931 | 0.086975 | 122.9141 | 62.8235 | 122.7631 | 62.8876 | 122.8271 | 0.19226 | 0.054931 | 122.9782 | 122.8638 | 0.11902 | 122.7219 | 62.3428 | 122.6578 | -60.4889 | -122.7768 | 62.2787 | 122.7997 | 62.2879 | -0.11444
2440.8281 | 122.937 | -62.3886 | 60.4614 | -0.029907 | -0.0012241 | -0.0089913 | 2.8952 | 0.0017517 | -0.0035548 | -0.0033261 | -0.1376 | 0.16459 | 0.1273 | 0.0028284 | 0.055397 | 0.10415 | -0.0014355 | -0.059509 | 0.059509 | -0.1236 | -0.1236 | -0.068665 | -0.13275 | -0.091553 | -62.5671 | 60.4065 | -62.3749 | 60.379 | 60.4385 | 60.2509 | 0.35706 | 62.265 | -60.4019 | -60.585 | 62.3199 | 62.2971 | 62.2559 | 0.032043 | -0.009155 | 0.013733 | -0.054932 | -0.082398 | 122.8271 | 62.7457 | 122.6395 | 62.7319 | 122.6257 | 0.054931 | 0 | 122.8134 | 122.7539 | 0.1831 | 122.7814 | 62.4481 | 122.7951 | -60.585 | -122.8363 | 62.265 | 122.7676 | 62.3291 | -0.17853
2441.8906 | 123.0194 | -62.3291 | 60.4614 | -0.037537 | -0.0029331 | -0.0094187 | 2.8922 | 0.00046989 | 0.001145 | -0.0011899 | -0.11624 | 0.16245 | 0.12602 | -0.003153 | 0.056892 | 0.10329 | -0.00036747 | 0.032043 | 0.13733 | -0.045776 | -0.041199 | 0.068665 | -0.022888 | 0.018311 | -62.4481 | 60.4431 | -62.3611 | 60.466 | 60.5438 | 60.3516 | 0.48523 | 62.2833 | -60.3241 | -60.5026 | 62.3978 | 62.3474 | 62.3062 | 0.064087 | 0.022888 | -0.032043 | -0.018311 | 0.004577 | 122.8729 | 62.8143 | 122.6807 | 62.8464 | 122.7127 | 0.11444 | 0.004577 | 122.905 | 122.8271 | 0.18311 | 122.8043 | 62.4664 | 122.7722 | -60.5072 | -122.8226 | 62.2879 | 122.7951 | 62.3611 | -0.11902
2442.8281 | 122.9965 | -62.3383 | 60.4614 | 0.038757 | -0.00036966 | -0.0092051 | 2.8935 | 0.0013245 | 0.0026404 | 0.0018009 | -0.1254 | 0.16373 | 0.12815 | 0.00069215 | 0.057533 | 0.105 | -0.0016493 | 0.054932 | 0.050354 | -0.10529 | -0.045776 | 0.050354 | -0.073242 | -0.036621 | -62.4802 | 60.4111 | -62.3703 | 60.4477 | 60.5026 | 60.3104 | 0.43488 | 62.233 | -60.4111 | -60.5072 | 62.3886 | 62.3016 | 62.265 | 0.068665 | 0.032044 | -0.032043 | -0.050354 | -0.013733 | 122.8409 | 62.7731 | 122.6486 | 62.8052 | 122.6807 | 0.15564 | 0.05951 | 122.8729 | 122.818 | 0.15564 | 122.7814 | 62.3886 | 122.7493 | -60.5667 | -122.8317 | 62.2925 | 122.7859 | 62.3932 | -0.14191
2443.8906 | 122.9736 | -62.3795 | 60.4248 | -0.045166 | -0.00058326 | -0.0092051 | 2.8924 | 0.0017517 | -0.0035548 | -0.0014035 | -0.097931 | 0.16245 | 0.1273 | -0.0027258 | 0.055824 | 0.10393 | -0.0042127 | -0.004578 | 0.10071 | -0.068665 | -0.050354 | 0.064087 | -0.045776 | -0.009155 | -62.4619 | 60.4111 | -62.3657 | 60.4797 | 60.5255 | 60.3516 | 0.45776 | 62.3108 | -60.3241 | -60.4752 | 62.4435 | 62.3703 | 62.3337 | 0.05951 | 0.022889 | 0.013733 | -0.013733 | 0.054931 | 122.905 | 62.8372 | 122.731 | 62.8235 | 122.7173 | 0.13275 | 0.018311 | 122.8912 | 122.8455 | 0.16937 | 122.7768 | 62.4802 | 122.7905 | -60.4935 | -122.7905 | 62.3291 | 122.8592 | 62.3749 | -0.082397
2444.8281 | 122.9599 | -62.3657 | 60.4568 | -0.045166 | -0.0016513 | -0.0085641 | 2.8943 | 0.0023925 | -0.00099116 | -0.0026853 | -0.097931 | 0.16566 | 0.12965 | 0.0021876 | 0.054969 | 0.10286 | -0.0046399 | -0.036621 | 0.073242 | -0.091553 | -0.10071 | -0.009155 | -0.1236 | -0.073242 | -62.5305 | 60.3973 | -62.3795 | 60.4019 | 60.4752 | 60.2875 | 0.38452 | 62.2742 | -60.3836 | -60.5576 | 62.3566 | 62.2925 | 62.2421 | 0.018311 | -0.032043 | -0.013733 | -0.059509 | -0.054931 | 122.8409 | 62.7502 | 122.6532 | 62.764 | 122.6669 | 0.082398 | -0.009155 | 122.8546 | 122.7814 | 0.16479 | 122.7768 | 62.439 | 122.7631 | -60.5484 | -122.8363 | 62.265 | 122.7676 | 62.3291 | -0.16479
2445.8906 | 123.056 | -62.3199 | 60.4523 | -0.052796 | -0.0012241 | -0.0089913 | 2.8915 | 0.00068369 | -0.00035036 | -0.0018307 | -0.027741 | 0.16181 | 0.12345 | -0.003794 | 0.056465 | 0.10308 | -0.0027173 | 0.045776 | 0.082397 | -0.022888 | 0.045776 | 0.1831 | 0.068665 | 0.11902 | -62.2925 | 60.3882 | -62.3291 | 60.4889 | 60.6354 | 60.4752 | 0.54474 | 62.2971 | -60.3699 | -60.4065 | 62.5031 | 62.439 | 62.3886 | 0.14191 | 0.091553 | -0.009156 | -0.064087 | 0.036621 | 122.9553 | 62.8647 | 122.7951 | 62.8738 | 122.8043 | 0.20599 | 0.068664 | 122.9645 | 122.818 | 0.10528 | 122.7173 | 62.4023 | 122.7081 | -60.4752 | -122.7814 | 62.3657 | 122.8088 | 62.3657 | 0.027466
2446.8281 | 122.9828 | -62.3703 | 60.4523 | -0.037537 | 0.00091214 | -0.0098459 | 2.8943 | 0.00046989 | 0.00071784 | -0.0028989 | -0.06131 | 0.16224 | 0.12837 | -0.003794 | 0.05561 | 0.105 | 5.9726e-05 | -0.11444 | 0.036621 | -0.15564 | -0.57678 | 0.17853 | 0.22888 | -0.11902 | -62.5671 | 60.4202 | -62.3795 | 60.4019 | 60.4431 | 60.2783 | 0.33875 | 62.2147 | -60.4157 | -61.0291 | 62.5488 | 62.2513 | 62.5992 | 0.036621 | 0.38452 | -0.009156 | -0.032044 | -0.050354 | 122.8134 | 62.709 | 122.6486 | 62.7182 | 122.6578 | 0.33417 | -0.42114 | 122.8226 | 122.7814 | 0.19226 | 122.7997 | 62.4069 | 122.7905 | -60.6079 | -122.8317 | 61.7935 | 122.7722 | 62.2559 | -0.19684
2447.8906 | 122.9691 | -62.3337 | 60.466 | -0.007019 | 5.7742e-05 | -0.0087777 | 2.8911 | 0.00089729 | -0.0037684 | -0.0022581 | -0.070465 | 0.16267 | 0.12922 | -0.0052892 | 0.056465 | 0.10265 | 0.00048713 | 0.032043 | 0.091553 | -0.045776 | -0.027466 | 0.068665 | -0.013733 | 0.009155 | -62.4664 | 60.4523 | -62.3383 | 60.4156 | 60.5209 | 60.347 | 0.47607 | 62.2879 | -60.3745 | -60.4935 | 62.4023 | 62.3428 | 62.3199 | 0.054931 | 0.032043 | -0.004578 | -0.013732 | -0.050354 | 122.8546 | 62.8098 | 122.6807 | 62.8143 | 122.6852 | 0.11444 | 0.01831 | 122.8592 | 122.7539 | 0.13733 | 122.7905 | 62.4252 | 122.7859 | -60.5118 | -122.8043 | 62.3062 | 122.7493 | 62.3657 | -0.13275
2448.8438 | 123.0835 | -62.2925 | 60.4248 | -0.014649 | -0.00015586 | -0.0096323 | 2.892 | 4.2692e-05 | 7.6842e-05 | -0.0039671 | -0.015534 | 0.16459 | 0.12751 | -0.0067846 | 0.056465 | 0.10201 | -0.0020765 | 0.004578 | 0.054932 | -0.054932 | -0.004578 | 0.11444 | 0.022888 | 0.082397 | -62.3978 | 60.3882 | -62.3383 | 60.5301 | 60.6491 | 60.4614 | 0.52643 | 62.2375 | -60.3699 | -60.4294 | 62.4069 | 62.3749 | 62.3154 | 0.13733 | 0.07782 | -0.045777 | -0.036621 | 0.10529 | 122.9416 | 62.8189 | 122.7539 | 62.8647 | 122.7997 | 0.16937 | 0.050354 | 122.9874 | 122.8683 | 0.10986 | 122.7264 | 62.3474 | 122.6807 | -60.4797 | -122.7631 | 62.2879 | 122.8226 | 62.2971 | -0.10529
2449.8906 | 122.9691 | -62.3611 | 60.4935 | -0.007019 | -0.00079686 | -0.010914 | 2.8926 | -0.0012391 | -0.0029138 | -0.0043943 | -0.11014 | 0.16224 | 0.13093 | -0.012766 | 0.053474 | 0.10457 | 5.9726e-05 | 0.009155 | 0.17395 | -0.054932 | -0.045776 | 0.041199 | -0.027466 | 0.036621 | -62.4664 | 60.4797 | -62.3611 | 60.4156 | 60.4752 | 60.3287 | 0.47607 | 62.3062 | -60.3195 | -60.5392 | 62.4023 | 62.3978 | 62.3337 | 0.091553 | 0.027466 | 0 | -0.013733 | -0.07782 | 122.8363 | 62.8372 | 122.6898 | 62.8372 | 122.6898 | 0.096131 | 0.009156 | 122.8363 | 122.7768 | 0.22888 | 122.8409 | 62.5351 | 122.8409 | -60.5484 | -122.8546 | 62.3154 | 122.7768 | 62.3703 | -0.10529
2450.8281 | 122.9279 | -62.3474 | 60.4477 | -0.007019 | -0.0014377 | -0.0070687 | 2.8922 | 0.00025629 | -0.00056396 | -0.0037533 | -0.13455 | 0.16566 | 0.1288 | 0.0021876 | 0.056038 | 0.10201 | -0.0016493 | -0.068665 | 0.059509 | -0.11902 | -0.10986 | -0.054932 | -0.18768 | -0.13733 | -62.5809 | 60.4111 | -62.3932 | 60.3928 | 60.4294 | 60.2509 | 0.35248 | 62.2284 | -60.3882 | -60.5576 | 62.2925 | 62.2101 | 62.1597 | -0.01831 | -0.068664 | -0.045776 | -0.036621 | -0.054932 | 122.7768 | 62.6999 | 122.5983 | 62.7457 | 122.644 | 0.064087 | 0.009156 | 122.8226 | 122.7859 | 0.17853 | 122.8043 | 62.4069 | 122.7585 | -60.5667 | -122.8409 | 62.2375 | 122.7402 | 62.2787 | -0.23346
2451.8906 | 122.9645 | -62.3428 | 60.4797 | -0.007019 | 0.00069854 | -0.0072825 | 2.8926 | -0.0025207 | -0.0024866 | -0.00012167 | -0.070465 | 0.16416 | 0.12751 | -0.0025122 | 0.056251 | 0.10201 | -0.0012219 | 0.036621 | 0.11444 | -0.041199 | -0.009155 | 0.082397 | -0.032043 | 0.022888 | -62.4756 | 60.4385 | -62.3703 | 60.4111 | 60.5118 | 60.3561 | 0.47607 | 62.3016 | -60.3653 | -60.4889 | 62.4252 | 62.3657 | 62.3108 | 0.064087 | 0.009156 | -0.027466 | -0.041198 | -0.068664 | 122.8546 | 62.8189 | 122.699 | 62.8464 | 122.7264 | 0.1236 | 0.032044 | 122.8821 | 122.7814 | 0.15564 | 122.8088 | 62.4573 | 122.7814 | -60.5209 | -122.85 | 62.3337 | 122.7539 | 62.3795 | -0.13275
2452.8281 | 122.9919 | -62.3703 | 60.4523 | -0.052796 | 0.00048494 | -0.0098459 | 2.8941 | -0.00017091 | -0.00077756 | 0.0022281 | -0.11929 | 0.16138 | 0.12837 | -0.0067846 | 0.056678 | 0.10244 | 0.0015551 | -0.10529 | 0.050354 | -0.15106 | -0.64545 | -0.3891 | 0.3891 | 0.086975 | -62.5442 | 60.4294 | -62.3749 | 60.4065 | 60.4477 | 60.2737 | 0.34332 | 62.2192 | -60.4019 | -61.0977 | 61.9812 | 62.4573 | 62.7594 | 0.23804 | 0.54016 | -0.004578 | -0.022889 | -0.045777 | 122.818 | 62.7136 | 122.644 | 62.7182 | 122.6486 | -0.23804 | -0.49438 | 122.8226 | 122.7814 | 0.20142 | 122.8043 | 62.4207 | 122.7997 | -60.6033 | -122.8271 | 61.7249 | 122.7768 | 62.265 | -0.17395
2453.9062 | 123.0927 | -62.3199 | 60.4065 | -0.075684 | 5.7742e-05 | -0.0077097 | 2.892 | -0.0033753 | -0.003982 | -0.0020443 | -0.10098 | 0.16459 | 0.12901 | -0.0091344 | 0.054542 | 0.1035 | 0.00048713 | -0.10529 | 0.009155 | -0.14648 | -0.1236 | -0.041199 | -0.15106 | -0.082397 | -62.4893 | 60.3882 | -62.3932 | 60.498 | 60.5347 | 60.3607 | 0.40283 | 62.1735 | -60.3973 | -60.5301 | 62.2787 | 62.2375 | 62.1689 | 0.064087 | -0.004578 | -0.073242 | -0.01831 | 0.091553 | 122.8546 | 62.7228 | 122.6807 | 62.796 | 122.7539 | 0.10529 | 0.022888 | 122.9279 | 122.8912 | 0.15564 | 122.7814 | 62.3291 | 122.7081 | -60.553 | -122.7997 | 62.1964 | 122.818 | 62.2147 | -0.16937
2454.8281 | 122.9736 | -62.3886 | 60.434 | -0.045166 | 0.0024075 | -0.0070687 | 2.8937 | 0.0049561 | -0.00056396 | -0.0024717 | -0.10403 | 0.16352 | 0.12687 | -0.0025122 | 0.056892 | 0.10479 | -0.0031445 | -0.11902 | 0.050354 | -0.16479 | 0.20599 | 0.29755 | -0.3067 | -0.10071 | -62.5671 | 60.4202 | -62.3932 | 60.3928 | 60.4523 | 60.2829 | 0.3479 | 62.2238 | -60.3836 | -60.228 | 62.6862 | 62.2879 | 62.0819 | 0.064087 | -0.14191 | -0.004577 | -0.013733 | -0.041199 | 122.8409 | 62.7365 | 122.6715 | 62.7411 | 122.6761 | 0.46234 | 0.37079 | 122.8455 | 122.7859 | 0.21515 | 122.8134 | 62.439 | 122.8088 | -60.5988 | -122.8271 | 62.5946 | 122.7814 | 62.2696 | -0.17853
2455.8906 | 122.9965 | -62.3474 | 60.4935 | -0.022278 | 5.7742e-05 | -0.011341 | 2.8926 | -0.0010253 | -0.003982 | -0.0018307 | -0.11319 | 0.16373 | 0.12858 | -0.002085 | 0.054542 | 0.105 | -0.0014355 | 0.013733 | 0.14191 | -0.054932 | -0.041199 | 0.022888 | -0.036621 | 0.036621 | -62.5305 | 60.4385 | -62.3657 | 60.4523 | 60.5438 | 60.3516 | 0.50354 | 62.2925 | -60.3516 | -60.5347 | 62.3703 | 62.384 | 62.3108 | 0.091553 | 0.018311 | -0.018311 | -0.054931 | -0.041198 | 122.8912 | 62.851 | 122.699 | 62.8693 | 122.7173 | 0.07782 | 0.013733 | 122.9095 | 122.818 | 0.19684 | 122.8043 | 62.4893 | 122.7859 | -60.5484 | -122.8592 | 62.3062 | 122.7997 | 62.3611 | -0.18311
2456.8281 | 122.937 | -62.352 | 60.434 | -0.052796 | -0.0020785 | -0.0070687 | 2.8945 | -0.0018799 | 0.001145 | -0.00076267 | -0.15591 | 0.16502 | 0.1288 | -0.0033666 | 0.055183 | 0.10415 | -0.0042127 | -0.091553 | 0.054932 | -0.12817 | -0.14648 | -0.086975 | -0.19684 | -0.1236 | -62.5809 | 60.4065 | -62.4023 | 60.4065 | 60.4385 | 60.2509 | 0.36621 | 62.2238 | -60.379 | -60.5804 | 62.265 | 62.2284 | 62.1552 | 0.004578 | -0.068664 | -0.050354 | -0.027466 | -0.027466 | 122.7905 | 62.7182 | 122.6028 | 62.7686 | 122.6532 | 0.041199 | -0.01831 | 122.8409 | 122.8088 | 0.18311 | 122.8088 | 62.4069 | 122.7585 | -60.5621 | -122.8363 | 62.2055 | 122.7585 | 62.2604 | -0.22888
2457.8281 | 123.0331 | -62.3566 | 60.4019 | -0.029907 | -0.0012241 | -0.0087777 | 2.8939 | -0.0014527 | 0.0013586 | -0.0039671 | -0.11014 | 0.16416 | 0.12751 | -0.0044348 | 0.055183 | 0.10201 | -0.00036747 | -0.10986 | 0.018311 | -0.16022 | -0.14191 | -0.050354 | -0.16937 | -0.086975 | -62.5122 | 60.3882 | -62.384 | 60.4614 | 60.5209 | 60.347 | 0.37994 | 62.1963 | -60.3836 | -60.5438 | 62.3062 | 62.2696 | 62.1872 | 0.073242 | -0.009156 | -0.027466 | -0.013733 | 0.059509 | 122.8775 | 62.7365 | 122.7036 | 62.764 | 122.731 | 0.10986 | 0.01831 | 122.905 | 122.8455 | 0.17853 | 122.7722 | 62.3749 | 122.7448 | -60.5621 | -122.7859 | 62.2147 | 122.818 | 62.2467 | -0.15564
2459.0312 | 123.0515 | -62.3154 | 60.379 | -0.037537 | -0.0035739 | -0.0072825 | 2.8913 | -0.00017091 | -0.00077756 | -0.00033547 | -0.064362 | 0.16395 | 0.12837 | -0.006571 | 0.054329 | 0.10158 | -0.0012219 | -0.054932 | -0.027466 | -0.11444 | -0.050354 | 0.054932 | -0.068665 | -0.009155 | -62.4298 | 60.3653 | -62.3795 | 60.5072 | 60.585 | 60.3973 | 0.40741 | 62.2009 | -60.4065 | -60.4294 | 62.3703 | 62.3062 | 62.2467 | 0.10529 | 0.045776 | -0.064087 | -0.013733 | 0.12817 | 122.9004 | 62.7228 | 122.7127 | 62.7869 | 122.7768 | 0.16937 | 0.064087 | 122.9645 | 122.8867 | 0.086975 | 122.7448 | 62.2879 | 122.6807 | -60.4935 | -122.7585 | 62.265 | 122.8226 | 62.2604 | -0.11444
2459.9375 | 123.0423 | -62.3199 | 60.4614 | -0.045166 | 0.0011257 | -0.0081369 | 2.8905 | -0.0023071 | -0.00077756 | -0.0014035 | -0.036896 | 0.16224 | 0.12773 | -0.002085 | 0.05561 | 0.10329 | -0.0037855 | 0.041199 | 0.086975 | -0.032043 | 0.054932 | 0.16022 | 0.059509 | 0.086975 | -62.4207 | 60.4019 | -62.3337 | 60.4706 | 60.5804 | 60.4065 | 0.53558 | 62.2879 | -60.3745 | -60.4065 | 62.4802 | 62.4069 | 62.3795 | 0.11902 | 0.091552 | -0.013733 | -0.059509 | 0.009155 | 122.9004 | 62.8555 | 122.7264 | 62.8693 | 122.7402 | 0.19226 | 0.086975 | 122.9141 | 122.8043 | 0.11902 | 122.7356 | 62.4069 | 122.7219 | -60.4935 | -122.7951 | 62.3749 | 122.7905 | 62.3611 | -0.10071
2461.375 | 123.0469 | -62.3016 | 60.4568 | -0.022278 | 0.00027134 | -0.0096323 | 2.895 | 0.0023925 | -0.0020594 | -0.0031125 | -0.06131 | 0.16267 | 0.12794 | -0.003794 | 0.053688 | 0.10436 | -0.0016493 | 0.054932 | 0.059509 | -0.050354 | 0.045776 | 0.16022 | 0.050354 | 0.09613 | -62.4161 | 60.3928 | -62.3428 | 60.5072 | 60.5988 | 60.4294 | 0.54016 | 62.2513 | -60.3973 | -60.4111 | 62.4619 | 62.3978 | 62.352 | 0.14648 | 0.10071 | -0.041198 | -0.064087 | 0.050354 | 122.9004 | 62.8418 | 122.731 | 62.883 | 122.7722 | 0.21057 | 0.09613 | 122.9416 | 122.85 | 0.10986 | 122.7356 | 62.3611 | 122.6944 | -60.5072 | -122.7997 | 62.3474 | 122.8088 | 62.3566 | -0.11444
2462.5312 | 122.9919 | -62.3337 | 60.4202 | -0.014649 | -0.00058326 | -0.0087777 | 2.8941 | 0.0047425 | -0.0014184 | -0.0016171 | -0.14981 | 0.16331 | 0.12687 | -0.0059302 | 0.056892 | 0.105 | -0.0033581 | -0.091553 | 0.022888 | -0.12817 | -0.16937 | -0.10071 | -0.17853 | -0.10529 | -62.5534 | 60.4065 | -62.384 | 60.4385 | 60.466 | 60.2783 | 0.35706 | 62.2055 | -60.3973 | -60.5896 | 62.233 | 62.2284 | 62.1552 | 0.022888 | -0.050354 | -0.050354 | -0.013733 | 0.018311 | 122.7997 | 62.6907 | 122.612 | 62.7411 | 122.6624 | 0.027466 | -0.041199 | 122.85 | 122.8226 | 0.15106 | 122.7905 | 62.3566 | 122.7402 | -60.5484 | -122.8043 | 62.1643 | 122.7722 | 62.2421 | -0.21973
2463.4531 | 122.9599 | -62.3657 | 60.4385 | -0.060425 | -0.0014377 | -0.0087777 | 2.8922 | 0.0028199 | -0.00056396 | -0.00033547 | -0.088776 | 0.16352 | 0.12901 | -0.0072118 | 0.055397 | 0.10201 | -0.0031445 | -0.10529 | 0.036621 | -0.17853 | -0.17395 | -0.11902 | -0.27466 | -0.59509 | -62.5397 | 60.4111 | -62.384 | 60.4385 | 60.4248 | 60.2554 | 0.35248 | 62.1872 | -60.4019 | -60.6125 | 62.2467 | 61.7706 | 62.0911 | -0.41656 | -0.09613 | -0.01831 | -0.027466 | 0 | 122.7905 | 62.7182 | 122.6212 | 62.7365 | 122.6395 | 0.059509 | 0.004578 | 122.8088 | 122.8226 | 0.21515 | 122.7951 | 62.4023 | 122.7768 | -60.6171 | -122.8226 | 62.1918 | 122.8043 | 62.2604 | -0.17395
2465.5312 | 123.0331 | -62.3657 | 60.4431 | -0.090943 | -0.00036966 | -0.0072825 | 2.8941 | -0.0018799 | -0.002273 | -0.0039671 | -0.055206 | 0.1601 | 0.12623 | -0.0046484 | 0.054115 | 0.10158 | -0.00036747 | -0.059509 | 0.018311 | -0.10529 | -0.059509 | 0.022888 | -0.082397 | -0.004578 | -62.4893 | 60.3516 | -62.3657 | 60.4752 | 60.5484 | 60.3607 | 0.42114 | 62.2604 | -60.4248 | -60.5026 | 62.3886 | 62.3611 | 62.2833 | 0.10071 | 0.022889 | 0 | -0.091553 | 0.032044 | 122.9141 | 62.7869 | 122.7264 | 62.7869 | 122.7264 | 0.12817 | 0.045777 | 122.9141 | 122.8409 | 0.1236 | 122.7173 | 62.384 | 122.7173 | -60.5484 | -122.8088 | 62.3062 | 122.8409 | 62.3062 | -0.1236
2466.6562 | 123.0515 | -62.3062 | 60.4294 | 0.00061049 | 0.0011257 | -0.0085641 | 2.8915 | -0.0010253 | -0.0014184 | -0.0039671 | -0.024689 | 0.16267 | 0.12944 | -0.003153 | 0.055397 | 0.1035 | -0.0046399 | -0.041199 | 0.036621 | -0.086975 | -0.064087 | 0.041199 | -0.054932 | 0.013733 | -62.5168 | 60.4019 | -62.3611 | 60.4935 | 60.5438 | 60.3653 | 0.4303 | 62.2192 | -60.3928 | -60.4935 | 62.3474 | 62.3199 | 62.2513 | 0.10071 | 0.032043 | -0.054932 | -0.027465 | 0.064087 | 122.85 | 62.7365 | 122.6715 | 62.7914 | 122.7264 | 0.12817 | 0.022888 | 122.905 | 122.8546 | 0.1236 | 122.7631 | 62.3428 | 122.7081 | -60.5164 | -122.7905 | 62.2421 | 122.7997 | 62.265 | -0.21057
2467.3906 | 123.0103 | -62.3703 | 60.4385 | -0.068054 | -0.0020785 | -0.0074961 | 2.8956 | 0.0011109 | -0.00077756 | -0.00097627 | -0.17117 | 0.16288 | 0.13179 | -0.00080325 | 0.052833 | 0.10137 | -0.00036747 | -0.07782 | 0.041199 | -0.13275 | -0.16022 | -0.064087 | -0.16479 | -0.09613 | -62.5488 | 60.3928 | -62.3978 | 60.4477 | 60.4706 | 60.3149 | 0.3479 | 62.2375 | -60.3973 | -60.5988 | 62.3062 | 62.2742 | 62.2055 | 0.036621 | -0.032044 | -0.027466 | -0.045777 | 0.009155 | 122.8409 | 62.7182 | 122.6852 | 62.7457 | 122.7127 | 0.068664 | -0.027466 | 122.8683 | 122.8455 | 0.17395 | 122.7905 | 62.4115 | 122.7631 | -60.5713 | -122.8363 | 62.2101 | 122.818 | 62.2925 | -0.17853
2471.9531 | 122.9462 | -62.3657 | 60.4431 | -0.037537 | 0.0013393 | -0.0060007 | 2.8937 | 0.0049561 | 0.0013586 | -0.0026853 | -0.16202 | 0.16331 | 0.12815 | -0.003153 | 0.055397 | 0.10308 | -0.00058107 | -0.091553 | 0.036621 | -0.15564 | -0.17853 | -0.10071 | -0.19684 | -0.11444 | -62.7777 | 60.3561 | -62.4069 | 60.4156 | 60.4523 | 60.3012 | 0.36621 | 62.2101 | -60.4065 | -60.6216 | 62.265 | 62.2513 | 62.1689 | 0.041199 | -0.041198 | -0.041198 | -0.086975 | -0.027466 | 122.818 | 62.7319 | 122.6669 | 62.7731 | 122.7081 | 0.054932 | -0.022888 | 122.8592 | 122.8226 | 0.19226 | 122.7631 | 62.4023 | 122.7219 | -60.5988 | -122.85 | 62.1872 | 122.7814 | 62.2742 | -0.41199
2472.5938 | 122.9645 | -62.3245 | 60.4752 | -0.022278 | -0.0014377 | -0.010273 | 2.892 | -0.0020935 | -0.0014184 | -0.00012167 | -0.088776 | 0.16395 | 0.1273 | -0.0018712 | 0.054969 | 0.10393 | -0.0020765 | 0.004578 | 0.14648 | -0.027466 | -0.027466 | 0.059509 | -0.009155 | 0.041199 | -62.5305 | 60.434 | -62.3657 | 60.4294 | 60.5072 | 60.3287 | 0.47607 | 62.2971 | -60.3287 | -60.5026 | 62.384 | 62.3657 | 62.3154 | 0.068665 | 0.018311 | -0.041199 | -0.041199 | -0.045777 | 122.8317 | 62.8006 | 122.6532 | 62.8418 | 122.6944 | 0.086975 | 0 | 122.8729 | 122.7951 | 0.17395 | 122.7997 | 62.471 | 122.7585 | -60.5026 | -122.8409 | 62.2971 | 122.7539 | 62.3291 | -0.20599
2473.4531 | 123.0011 | -62.3383 | 60.4248 | -0.045166 | -0.0010105 | -0.0085641 | 2.8945 | 0.0013245 | -0.0016322 | 0.00073273 | -0.1254 | 0.16352 | 0.13008 | 0.0026148 | 0.056465 | 0.10457 | -0.0033581 | 0.032043 | 0.13275 | -0.07782 | -0.041199 | 0.059509 | -0.032043 | -0.013733 | -62.4527 | 60.4202 | -62.3657 | 60.466 | 60.5621 | 60.379 | 0.4715 | 62.2604 | -60.2921 | -60.466 | 62.3978 | 62.3245 | 62.3062 | 0.064087 | 0.045777 | -0.027466 | -0.004578 | 0.041198 | 122.9004 | 62.8098 | 122.7173 | 62.8372 | 122.7448 | 0.13733 | 0.036621 | 122.9279 | 122.8317 | 0.21057 | 122.7859 | 62.471 | 122.7585 | -60.5026 | -122.7905 | 62.2971 | 122.8043 | 62.3703 | -0.11444
2474.0156 | 123.0972 | -62.2925 | 60.4248 | -0.014649 | -0.00015586 | -0.0072825 | 2.8903 | -0.0020935 | 0.0024268 | -0.0054623 | -0.049103 | 0.16096 | 0.12602 | -0.0076392 | 0.056251 | 0.10329 | -0.0010083 | 0.032043 | 0.064087 | -0.054932 | 0.059509 | 0.16479 | 0.059509 | 0.11444 | -62.3703 | 60.3928 | -62.3245 | 60.5576 | 60.6628 | 60.4706 | 0.54932 | 62.2375 | -60.3607 | -60.3653 | 62.4573 | 62.4069 | 62.352 | 0.16937 | 0.11444 | -0.032044 | -0.032044 | 0.13275 | 122.9553 | 62.8418 | 122.7631 | 62.8738 | 122.7951 | 0.21973 | 0.11444 | 122.9874 | 122.8821 | 0.11902 | 122.7173 | 62.3566 | 122.6852 | -60.4797 | -122.7493 | 62.352 | 122.85 | 62.3245 | -0.07782
2474.8281 | 123.0331 | -62.3383 | 60.4019 | -0.007019 | -0.0014377 | -0.0094187 | 2.8924 | -0.0010253 | -0.0018458 | -0.0022581 | -0.076569 | 0.16032 | 0.12623 | 0.00047855 | 0.054329 | 0.10286 | 0.00070073 | -0.050354 | -0.022888 | -0.1236 | -0.073242 | 0.032043 | -0.091553 | -0.022888 | -62.471 | 60.347 | -62.3703 | 60.4843 | 60.5255 | 60.3516 | 0.3891 | 62.2147 | -60.4248 | -60.4752 | 62.3703 | 62.3154 | 62.2467 | 0.10071 | 0.032043 | -0.032043 | -0.054932 | 0.082397 | 122.8638 | 62.7274 | 122.6898 | 62.7594 | 122.7219 | 0.15564 | 0.050354 | 122.8958 | 122.8546 | 0.10071 | 122.7173 | 62.3154 | 122.6852 | -60.5255 | -122.7722 | 62.265 | 122.8226 | 62.2879 | -0.13275
2475.8281 | 123.111 | -62.3016 | 60.434 | -0.083313 | -0.0014377 | -0.0085641 | 2.8937 | -0.0040161 | -0.0012048 | -0.0024717 | -0.046051 | 0.16309 | 0.12922 | -0.0069982 | 0.05262 | 0.10329 | 0.00048713 | 0.022888 | 0.068665 | -0.041199 | 0.054932 | 0.17395 | 0.054932 | 0.09613 | -62.3703 | 60.379 | -62.3428 | 60.5576 | 60.6491 | 60.4843 | 0.54474 | 62.2604 | -60.3653 | -60.379 | 62.4756 | 62.3978 | 62.3566 | 0.13733 | 0.096131 | -0.041198 | -0.054932 | 0.1236 | 122.9507 | 62.8464 | 122.7859 | 62.8876 | 122.8271 | 0.21515 | 0.096131 | 122.9919 | 122.9004 | 0.10986 | 122.7219 | 62.3703 | 122.6807 | -60.4752 | -122.7768 | 62.3566 | 122.8592 | 62.3245 | -0.068664
2476.8281 | 123.0698 | -62.2925 | 60.4477 | -0.037537 | -0.00036966 | -0.011128 | 2.8915 | 0.0021789 | -0.0014184 | -0.0026853 | -0.06131 | 0.16267 | 0.12709 | -0.0080664 | 0.053474 | 0.10115 | -0.0029309 | 0.036621 | 0.068665 | -0.041199 | 0.059509 | 0.19684 | 0.068665 | 0.10986 | -62.3566 | 60.3836 | -62.3062 | 60.5484 | 60.64 | 60.4614 | 0.56305 | 62.2513 | -60.379 | -60.3882 | 62.4893 | 62.4023 | 62.3611 | 0.15106 | 0.10986 | -0.013733 | -0.064087 | 0.10071 | 122.9324 | 62.8555 | 122.7539 | 62.8693 | 122.7676 | 0.23804 | 0.10071 | 122.9462 | 122.8546 | 0.10986 | 122.6898 | 62.3611 | 122.6761 | -60.4889 | -122.7539 | 62.352 | 122.8409 | 62.3291 | -0.064087
2477.8906 | 123.0469 | -62.3474 | 60.4385 | -0.045166 | -0.00079686 | -0.0092051 | 2.8922 | 0.0019653 | -0.00099116 | -0.0018307 | -0.052155 | 0.1648 | 0.12709 | -0.0044348 | 0.054969 | 0.10308 | 0.0011279 | -0.054932 | 0.032043 | -0.082397 | -0.059509 | 0.036621 | -0.045776 | 0.009155 | -62.3383 | 60.3928 | -62.3383 | 60.4843 | 60.5621 | 60.3836 | 0.43488 | 62.265 | -60.4065 | -60.498 | 62.384 | 62.3566 | 62.3016 | 0.091552 | 0.036621 | 0.009155 | -0.045777 | 0.045776 | 122.9095 | 62.7823 | 122.731 | 62.7731 | 122.7219 | 0.11902 | 0.022888 | 122.9004 | 122.8226 | 0.11444 | 122.731 | 62.3795 | 122.7402 | -60.5209 | -122.7768 | 62.2879 | 122.8317 | 62.2925 | 0.009155
2478.8281 | 123.1064 | -62.2833 | 60.4431 | -0.090943 | -0.0016513 | -0.0083505 | 2.893 | -0.0012391 | 0.00093144 | -0.0031125 | -0.070465 | 0.16267 | 0.12687 | 0.00090575 | 0.054542 | 0.10222 | 0.00027333 | 0.009155 | 0.059509 | -0.041199 | 0.041199 | 0.17395 | 0.050354 | 0.11444 | -62.3474 | 60.3928 | -62.3291 | 60.5621 | 60.64 | 60.4523 | 0.55389 | 62.2421 | -60.3836 | -60.4019 | 62.4573 | 62.3978 | 62.3337 | 0.15564 | 0.091553 | -0.045777 | -0.050354 | 0.11902 | 122.9233 | 62.8372 | 122.7356 | 62.883 | 122.7814 | 0.21515 | 0.082398 | 122.9691 | 122.8912 | 0.10071 | 122.7219 | 62.3428 | 122.6761 | -60.4843 | -122.7722 | 62.3245 | 122.8455 | 62.2925 | -0.064087
2479.8906 | 123.1201 | -62.2925 | 60.434 | -0.045166 | 0.00027134 | -0.0083505 | 2.8933 | -0.0010253 | -0.0020594 | -0.0035397 | -0.067413 | 0.16288 | 0.12687 | -0.00037605 | 0.05561 | 0.10415 | -0.0025037 | 0.022888 | 0.073242 | -0.054932 | 0.045776 | 0.13733 | 0.036621 | 0.11902 | -62.3566 | 60.3699 | -62.3199 | 60.5576 | 60.6445 | 60.4843 | 0.55389 | 62.2375 | -60.3607 | -60.3882 | 62.4298 | 62.4115 | 62.3291 | 0.17395 | 0.091553 | -0.027466 | -0.064087 | 0.1236 | 122.937 | 62.8464 | 122.7768 | 62.8738 | 122.8043 | 0.19226 | 0.10071 | 122.9645 | 122.8775 | 0.12817 | 122.6898 | 62.3657 | 122.6624 | -60.4889 | -122.7539 | 62.3383 | 122.85 | 62.3154 | -0.064087
2480.8281 | 123.0835 | -62.2971 | 60.4706 | -0.060425 | 0.00027134 | -0.0085641 | 2.8937 | -0.0046569 | 0.0019994 | -0.00076267 | -0.088776 | 0.15967 | 0.12751 | -0.0076392 | 0.055183 | 0.10415 | -0.0020765 | 0.068665 | 0.068665 | -0.027466 | 0.064087 | 0.16937 | 0.068665 | 0.09613 | -62.1689 | 60.4568 | -62.3291 | 60.5301 | 60.6308 | 60.4248 | 0.52643 | 62.2696 | -60.4019 | -60.4065 | 62.4664 | 62.3932 | 62.3657 | 0.1236 | 0.096131 | -0.032044 | -0.013733 | 0.059509 | 122.9279 | 62.8235 | 122.7219 | 62.8555 | 122.7539 | 0.19684 | 0.091553 | 122.9599 | 122.8592 | 0.096131 | 122.7859 | 62.3657 | 122.7539 | -60.498 | -122.7997 | 62.3611 | 122.8271 | 62.3657 | 0.12817
2481.8906 | 123.0331 | -62.3337 | 60.3928 | -0.075684 | 0.00048494 | -0.0096323 | 2.8933 | 0.0021789 | -0.002273 | -0.00012167 | -0.11014 | 0.16352 | 0.1273 | 0.001333 | 0.05561 | 0.10457 | 0.00091433 | -0.054932 | 0.004578 | -0.11444 | -0.059509 | 0.036621 | -0.091553 | -0.022888 | -62.4527 | 60.3653 | -62.3657 | 60.5026 | 60.5255 | 60.347 | 0.39825 | 62.2192 | -60.3882 | -60.4523 | 62.3703 | 62.3108 | 62.2421 | 0.091553 | 0.022888 | -0.032044 | -0.027466 | 0.10986 | 122.8592 | 62.7319 | 122.6807 | 62.764 | 122.7127 | 0.15106 | 0.054932 | 122.8912 | 122.8683 | 0.11902 | 122.731 | 62.3383 | 122.699 | -60.5072 | -122.7585 | 62.2742 | 122.8363 | 62.2787 | -0.11902
2482.8281 | 123.0652 | -62.3199 | 60.466 | -0.007019 | -0.0014377 | -0.0070687 | 2.8939 | -0.0023071 | -0.00035036 | -0.0016171 | -0.10098 | 0.16245 | 0.12773 | -0.0076392 | 0.054329 | 0.10244 | -0.0054945 | 0.07782 | 0.050354 | -0.045776 | 0.054932 | 0.14648 | 0.054932 | 0.091553 | -62.4023 | 60.3882 | -62.3383 | 60.5164 | 60.5804 | 60.4202 | 0.55847 | 62.2742 | -60.4156 | -60.4111 | 62.4664 | 62.4115 | 62.3749 | 0.13733 | 0.10071 | -0.018311 | -0.077819 | 0.050354 | 122.9004 | 62.8784 | 122.7402 | 62.8967 | 122.7585 | 0.19226 | 0.10071 | 122.9187 | 122.8546 | 0.09613 | 122.7264 | 62.3703 | 122.7081 | -60.5118 | -122.8043 | 62.3749 | 122.8363 | 62.3978 | -0.082398
2483.8281 | 122.9645 | -62.3291 | 60.4843 | 0.015869 | -0.0018649 | -0.0098459 | 2.8939 | 4.2692e-05 | -0.002273 | -0.00076267 | -0.14371 | 0.16416 | 0.12773 | -0.003153 | 0.054756 | 0.10692 | -0.0025037 | -0.018311 | 0.1236 | -0.041199 | -0.032043 | 0.050354 | -0.018311 | 0.022888 | -62.5122 | 60.434 | -62.3703 | 60.4294 | 60.5118 | 60.3333 | 0.4715 | 62.2879 | -60.3607 | -60.5164 | 62.3795 | 62.352 | 62.3108 | 0.064087 | 0.022888 | -0.041198 | -0.050354 | -0.054932 | 122.8409 | 62.8006 | 122.6624 | 62.8418 | 122.7036 | 0.091553 | 0.009156 | 122.8821 | 122.7997 | 0.16479 | 122.8043 | 62.4527 | 122.7631 | -60.5255 | -122.8546 | 62.2971 | 122.7585 | 62.3108 | -0.1831
2484.8281 | 123.056 | -62.3016 | 60.466 | -0.12146 | -0.0018649 | -0.0079233 | 2.893 | 0.0017517 | -0.0027002 | -0.0073849 | -0.088776 | 0.16224 | 0.1273 | -0.0016576 | 0.053688 | 0.10329 | -0.0065625 | 0.045776 | 0.1236 | -0.013733 | 0.036621 | 0.17853 | 0.050354 | 0.09613 | -62.3978 | 60.379 | -62.3383 | 60.5164 | 60.6216 | 60.4568 | 0.55389 | 62.2879 | -60.3424 | -60.4294 | 62.4802 | 62.3978 | 62.352 | 0.10986 | 0.064087 | -0.036621 | -0.086975 | 0.050354 | 122.9233 | 62.8555 | 122.7585 | 62.8922 | 122.7951 | 0.19226 | 0.050354 | 122.9599 | 122.8546 | 0.13733 | 122.7173 | 62.4252 | 122.6807 | -60.4797 | -122.8043 | 62.3383 | 122.818 | 62.3474 | -0.09613
2485.8281 | 123.0148 | -62.3337 | 60.4935 | 0.015869 | -0.0020785 | -0.0077097 | 2.893 | 0.0013245 | -0.0033412 | -0.0020443 | -0.15897 | 0.16523 | 0.12815 | -0.0016576 | 0.054329 | 0.10436 | -0.00036747 | 0.059509 | 0.10529 | -0.068665 | -0.022888 | 0.068665 | -0.059509 | 0.009155 | -62.4481 | 60.4019 | -62.3657 | 60.4843 | 60.5255 | 60.3516 | 0.4715 | 62.265 | -60.3882 | -60.5164 | 62.4023 | 62.3428 | 62.2742 | 0.07782 | 0.009156 | -0.032044 | -0.091552 | -0.009155 | 122.8592 | 62.8052 | 122.6852 | 62.8372 | 122.7173 | 0.13733 | 0.045777 | 122.8912 | 122.85 | 0.17395 | 122.7676 | 62.439 | 122.7356 | -60.5621 | -122.8592 | 62.3108 | 122.818 | 62.3932 | -0.11444
2486.8281 | 123.0103 | -62.3291 | 60.4523 | -0.083313 | 5.7742e-05 | -0.0083505 | 2.8937 | 0.0021789 | -0.0020594 | 0.0020145 | -0.16202 | 0.16459 | 0.12858 | -0.0069982 | 0.056892 | 0.10457 | -0.0027173 | 0.022888 | 0.15106 | -0.059509 | -0.018311 | 0.068665 | -0.013733 | 0.022888 | -62.4573 | 60.4477 | -62.3795 | 60.4935 | 60.585 | 60.3745 | 0.49896 | 62.2696 | -60.3012 | -60.4706 | 62.3978 | 62.352 | 62.3154 | 0.082397 | 0.045776 | -0.050354 | -0.004578 | 0.041198 | 122.9141 | 62.8281 | 122.7036 | 62.8784 | 122.7539 | 0.12817 | 0.041198 | 122.9645 | 122.8729 | 0.21057 | 122.8271 | 62.4802 | 122.7768 | -60.5118 | -122.8317 | 62.3108 | 122.8226 | 62.352 | -0.12817
2487.8281 | 123.0194 | -62.3428 | 60.4706 | -0.045166 | -0.0010105 | -0.0085641 | 2.8945 | 0.00068369 | -0.0027002 | -0.0022581 | -0.1376 | 0.16416 | 0.12794 | 0.0038966 | 0.056038 | 0.10308 | -0.0035719 | 0.018311 | 0.1236 | -0.045776 | -0.022888 | 0.091553 | -0.050354 | 0.032043 | -62.471 | 60.4248 | -62.3611 | 60.4752 | 60.5576 | 60.3561 | 0.48065 | 62.2971 | -60.347 | -60.4935 | 62.4344 | 62.3749 | 62.2925 | 0.077819 | -0.004578 | -0.018311 | -0.045776 | 0.004578 | 122.9004 | 62.8235 | 122.699 | 62.8418 | 122.7173 | 0.13733 | 0.022888 | 122.9187 | 122.8363 | 0.16937 | 122.7859 | 62.4664 | 122.7676 | -60.5164 | -122.8317 | 62.3199 | 122.818 | 62.3611 | -0.12817
2488.8281 | 123.0194 | -62.3291 | 60.4706 | -0.007019 | 0.00091214 | -0.0079233 | 2.8907 | 0.00068369 | -0.0016322 | -0.0024717 | -0.12234 | 0.16395 | 0.1305 | 0.00069215 | 0.056038 | 0.10372 | -0.0010083 | 0.036621 | 0.1236 | -0.054932 | -0.050354 | 0.041199 | -0.013733 | 0.018311 | -62.5031 | 60.4523 | -62.3474 | 60.4568 | 60.5484 | 60.3653 | 0.50354 | 62.2742 | -60.347 | -60.5209 | 62.3703 | 62.3474 | 62.3154 | 0.073243 | 0.041199 | -0.01831 | -0.01831 | -0.013733 | 122.8775 | 62.8326 | 122.6944 | 62.851 | 122.7127 | 0.096131 | 0.004578 | 122.8958 | 122.8043 | 0.17853 | 122.7997 | 62.4527 | 122.7814 | -60.5255 | -122.818 | 62.2787 | 122.7859 | 62.3657 | -0.17395
2489.8906 | 123.0698 | -62.3016 | 60.4843 | -0.12146 | 0.00069854 | -0.0089913 | 2.8939 | 0.0030335 | -0.00077756 | -0.0016171 | -0.058258 | 0.16267 | 0.12709 | -0.0040076 | 0.056892 | 0.10329 | 0.0017687 | -0.013733 | 0.10986 | -0.013733 | 0.032043 | 0.18768 | 0.086975 | 0.10071 | -62.4069 | 60.3973 | -62.352 | 60.5301 | 60.6308 | 60.4477 | 0.55847 | 62.2879 | -60.3745 | -60.4523 | 62.4893 | 62.4023 | 62.3886 | 0.11444 | 0.10071 | -0.050354 | -0.086975 | 0.045776 | 122.9324 | 62.8601 | 122.7493 | 62.9105 | 122.7997 | 0.20142 | 0.045776 | 122.9828 | 122.8821 | 0.1236 | 122.7493 | 62.4115 | 122.699 | -60.498 | -122.8363 | 62.3337 | 122.8317 | 62.2879 | -0.10528
2490.8281 | 123.0011 | -62.3199 | 60.4614 | -0.037537 | 0.00027134 | -0.0068551 | 2.8937 | 0.0013245 | 7.6842e-05 | -0.0024717 | -0.1254 | 0.16566 | 0.12623 | -0.00058965 | 0.055397 | 0.10735 | 0.00048713 | -0.004578 | 0.07782 | -0.086975 | -0.041199 | 0.050354 | -0.064087 | -0.018311 | -62.471 | 60.4385 | -62.3795 | 60.4752 | 60.5164 | 60.3653 | 0.46234 | 62.233 | -60.3836 | -60.5026 | 62.3703 | 62.3016 | 62.2559 | 0.068664 | 0.022888 | -0.05951 | -0.022888 | 0.013733 | 122.8363 | 62.7823 | 122.6852 | 62.8418 | 122.7448 | 0.13733 | 0.045776 | 122.8958 | 122.8546 | 0.16479 | 122.818 | 62.3978 | 122.7585 | -60.5484 | -122.8409 | 62.2787 | 122.7951 | 62.3154 | -0.15106
2491.8906 | 122.9965 | -62.3154 | 60.4477 | -0.014649 | -0.00036966 | -0.0081369 | 2.8918 | 4.2692e-05 | -0.0012048 | -0.0046079 | -0.076569 | 0.16352 | 0.12666 | -0.0093482 | 0.054969 | 0.10585 | -0.0014355 | 0.068665 | 0.091553 | -0.041199 | 0.032043 | 0.12817 | 0.032043 | 0.086975 | -62.439 | 60.4019 | -62.3474 | 60.4797 | 60.5667 | 60.3973 | 0.53101 | 62.2742 | -60.3561 | -60.4156 | 62.4435 | 62.4023 | 62.3474 | 0.12817 | 0.073242 | -0.032043 | -0.045776 | 0.032043 | 122.8821 | 62.8464 | 122.7127 | 62.8784 | 122.7448 | 0.16937 | 0.073242 | 122.9141 | 122.8271 | 0.13275 | 122.7493 | 62.4069 | 122.7173 | -60.4889 | -122.7951 | 62.3474 | 122.7951 | 62.384 | -0.1236
2492.8281 | 123.024 | -62.3428 | 60.4797 | -0.060425 | -0.00079686 | -0.0089913 | 2.8928 | -0.00081171 | -0.0012048 | -0.0014035 | -0.16202 | 0.16416 | 0.12922 | -0.0029394 | 0.053688 | 0.10479 | -0.0027173 | -0.004578 | 0.10071 | -0.07782 | -0.045776 | 0.059509 | -0.032043 | 0 | -62.4481 | 60.4111 | -62.3657 | 60.4752 | 60.5438 | 60.3699 | 0.48523 | 62.265 | -60.379 | -60.5255 | 62.4023 | 62.3428 | 62.3108 | 0.07782 | 0.045777 | -0.022889 | -0.068664 | -0.004577 | 122.8867 | 62.8281 | 122.7127 | 62.851 | 122.7356 | 0.13733 | 0.032044 | 122.9095 | 122.8409 | 0.17853 | 122.7768 | 62.4435 | 122.7539 | -60.5576 | -122.8455 | 62.2971 | 122.818 | 62.3383 | -0.10529
2493.8906 | 122.9462 | -62.3383 | 60.4706 | 0.015869 | 5.7742e-05 | -0.0081369 | 2.8928 | -0.00081171 | -0.0012048 | -0.0039671 | -0.10098 | 0.16416 | 0.13029 | -0.003153 | 0.056251 | 0.10564 | 0.0028369 | 0.009155 | 0.16022 | -0.050354 | -0.041199 | 0.07782 | -0.013733 | 0.041199 | -62.3199 | 60.4889 | -62.352 | 60.4065 | 60.5484 | 60.3058 | 0.46692 | 62.2879 | -60.3104 | -60.5118 | 62.4161 | 62.3795 | 62.3245 | 0.091553 | 0.036621 | -0.013733 | 0.018311 | -0.064087 | 122.8867 | 62.8052 | 122.644 | 62.8189 | 122.6578 | 0.12817 | 0.009155 | 122.9004 | 122.7585 | 0.21057 | 122.8409 | 62.4985 | 122.8271 | -60.5209 | -122.8226 | 62.2971 | 122.7448 | 62.3474 | 0.018311
2494.8281 | 123.0011 | -62.3245 | 60.466 | -0.037537 | 0.0015529 | -0.0081369 | 2.8941 | -0.0016663 | -0.0012048 | -0.0052487 | -0.14371 | 0.16352 | 0.12645 | -0.004862 | 0.056038 | 0.10372 | 0.0021961 | -0.004578 | 0.10071 | -0.059509 | -0.21973 | -0.1831 | 0.068665 | 0.045776 | -62.4802 | 60.4294 | -62.3657 | 60.4706 | 60.5118 | 60.3424 | 0.46234 | 62.265 | -60.3653 | -60.6857 | 62.1414 | 62.3703 | 62.3932 | 0.10528 | 0.12817 | -0.041199 | -0.036621 | 0.004578 | 122.8363 | 62.7869 | 122.6669 | 62.8281 | 122.7081 | -0.1236 | -0.16022 | 122.8775 | 122.8363 | 0.16022 | 122.7951 | 62.4252 | 122.7539 | -60.5255 | -122.8317 | 62.1048 | 122.7951 | 62.3199 | -0.15564
2495.8906 | 122.9965 | -62.3383 | 60.434 | -0.068054 | 0.0011257 | -0.0089913 | 2.892 | 0.0028199 | -0.0033412 | -0.0011899 | -0.13455 | 0.16523 | 0.12965 | -0.003794 | 0.056251 | 0.10436 | -0.0020765 | -0.004578 | 0.091553 | -0.086975 | -0.054932 | 0.059509 | -0.050354 | -0.004578 | -62.4619 | 60.4065 | -62.384 | 60.498 | 60.5118 | 60.3836 | 0.47607 | 62.2513 | -60.3424 | -60.4889 | 62.3978 | 62.3337 | 62.2879 | 0.082397 | 0.036621 | -0.045776 | -0.027466 | 0.064087 | 122.85 | 62.8143 | 122.7219 | 62.8601 | 122.7676 | 0.14648 | 0.032043 | 122.8958 | 122.8821 | 0.17853 | 122.7905 | 62.4298 | 122.7448 | -60.5209 | -122.818 | 62.2833 | 122.8363 | 62.3337 | -0.1236
2496.8281 | 122.9645 | -62.3749 | 60.4477 | -0.052796 | -0.0025059 | -0.0085641 | 2.8941 | 0.0015381 | -0.0029138 | -0.0043943 | -0.14371 | 0.16437 | 0.12922 | 0.0021876 | 0.056465 | 0.10436 | 0.00070073 | -0.064087 | 0.045776 | -0.10529 | -0.14191 | -0.050354 | -0.13275 | -0.13275 | -62.5854 | 60.4111 | -62.3932 | 60.4019 | 60.4614 | 60.2554 | 0.36163 | 62.2696 | -60.4019 | -60.5896 | 62.3245 | 62.2421 | 62.2421 | -0.027465 | -0.027465 | -0.01831 | -0.036621 | -0.045776 | 122.8363 | 62.7365 | 122.6303 | 62.7548 | 122.6486 | 0.054932 | -0.036621 | 122.8546 | 122.7951 | 0.15106 | 122.8043 | 62.4207 | 122.7859 | -60.553 | -122.8409 | 62.233 | 122.7768 | 62.3108 | -0.21057
2497.8281 | 122.9874 | -62.352 | 60.434 | -0.060425 | -0.00058326 | -0.0098459 | 2.8907 | 0.0030335 | -0.0012048 | -0.0026853 | -0.091827 | 0.16309 | 0.12944 | 0.00090575 | 0.054969 | 0.10521 | 0.00048713 | -0.036621 | 0.022888 | -0.1831 | -0.045776 | 0.059509 | -0.20142 | -0.10529 | -62.5763 | 60.3882 | -62.3932 | 60.4294 | 60.4706 | 60.2875 | 0.35706 | 62.1689 | -60.4111 | -60.4797 | 62.4115 | 62.2467 | 62.1506 | 0.077819 | -0.018311 | -0.041198 | -0.045776 | -0.004578 | 122.8226 | 62.709 | 122.6395 | 62.7502 | 122.6807 | 0.24261 | 0.13733 | 122.8638 | 122.8226 | 0.20599 | 122.7814 | 62.3749 | 122.7402 | -60.6171 | -122.8271 | 62.3062 | 122.7814 | 62.3154 | -0.2243
2498.8906 | 123.024 | -62.3657 | 60.4385 | -0.029907 | -0.0020785 | -0.0098459 | 2.8926 | 0.0011109 | -0.0018458 | -0.0014035 | -0.11014 | 0.16416 | 0.13008 | -0.003794 | 0.054756 | 0.10308 | -0.0014355 | 0 | 0.07782 | -0.07782 | -0.036621 | 0.064087 | -0.054932 | -0.004578 | -62.4756 | 60.4156 | -62.352 | 60.3516 | 60.6171 | 60.3516 | 0.46234 | 62.2879 | -60.3607 | -60.4752 | 62.4298 | 62.3611 | 62.3108 | 0.073242 | 0.022888 | 0.013733 | -0.022889 | -0.086976 | 122.9828 | 62.8281 | 122.7173 | 62.8143 | 122.7036 | 0.14191 | 0.041199 | 122.9691 | 122.7036 | 0.15564 | 122.7676 | 62.4435 | 122.7814 | -60.5164 | -122.7905 | 62.3291 | 122.7173 | 62.3657 | -0.10986
2499.8281 | 123.0606 | -62.3154 | 60.4156 | -0.083313 | -0.0014377 | -0.0089913 | 2.8937 | 0.0028199 | -0.0014184 | -0.00076267 | -0.11624 | 0.1648 | 0.12709 | -0.0055028 | 0.055824 | 0.1035 | -0.0012219 | -0.091553 | -0.022888 | -0.13733 | -0.11444 | -0.027466 | -0.082397 | -0.022888 | -62.4435 | 60.3561 | -62.3657 | 60.5164 | 60.5667 | 60.3882 | 0.42572 | 62.178 | -60.4385 | -60.5301 | 62.2879 | 62.2925 | 62.233 | 0.11444 | 0.054932 | -0.050354 | -0.059509 | 0.10071 | 122.8821 | 62.7411 | 122.7036 | 62.7914 | 122.7539 | 0.10986 | 0.022888 | 122.9324 | 122.8821 | 0.11444 | 122.7219 | 62.2925 | 122.6715 | -60.553 | -122.7814 | 62.2009 | 122.8317 | 62.2238 | -0.12817
2500.8906 | 122.9828 | -62.352 | 60.4889 | -0.014649 | -0.0016513 | -0.0083505 | 2.8905 | 0.0011109 | -0.0029138 | 0.00030553 | -0.082672 | 0.16651 | 0.1258 | -0.0025122 | 0.056465 | 0.10607 | -0.0033581 | 0.004578 | 0.16479 | -0.045776 | -0.059509 | 0.059509 | -0.013733 | 0.38452 | -62.5854 | 60.4156 | -62.3795 | 60.4111 | 60.5347 | 60.3378 | 0.5127 | 62.3062 | -60.3241 | -60.5484 | 62.4115 | 62.7365 | 62.3383 | 0.4303 | 0.032043 | -0.027466 | -0.073243 | -0.07782 | 122.8867 | 62.8647 | 122.6898 | 62.8922 | 122.7173 | 0.10528 | -0.013733 | 122.9141 | 122.7905 | 0.21057 | 122.7951 | 62.5168 | 122.7676 | -60.5347 | -122.8683 | 62.2925 | 122.7631 | 62.3566 | -0.23346
2501.8281 | 123.0469 | -62.3245 | 60.3973 | -0.052796 | 0.00091214 | -0.0092051 | 2.8924 | -0.0014527 | -0.00099116 | 0.00030553 | -0.064362 | 0.16523 | 0.12709 | -0.0044348 | 0.056678 | 0.10286 | -0.0029309 | -0.022888 | -0.018311 | -0.1236 | -0.054932 | 0.073242 | -0.07782 | -0.027466 | -62.4298 | 60.347 | -62.3749 | 60.4935 | 60.5484 | 60.4019 | 0.43488 | 62.2009 | -60.4156 | -60.4523 | 62.3978 | 62.2971 | 62.2467 | 0.09613 | 0.045776 | -0.050354 | -0.050354 | 0.09613 | 122.8729 | 62.7594 | 122.7264 | 62.8098 | 122.7768 | 0.19684 | 0.068664 | 122.9233 | 122.8683 | 0.10528 | 122.7219 | 62.3062 | 122.6715 | -60.5209 | -122.7722 | 62.2696 | 122.818 | 62.3016 | -0.10529
2502.8906 | 122.9095 | -62.3199 | 60.4568 | 0.031128 | -0.0016513 | -0.0098459 | 2.8939 | 0.0017517 | -0.0018458 | -0.0039671 | -0.064362 | 0.16288 | 0.12837 | -0.003794 | 0.054756 | 0.10265 | -0.0014355 | -0.004578 | 0.16479 | -0.059509 | -0.036621 | 0.054932 | -0.018311 | 0.050354 | -62.5214 | 60.4065 | -62.3566 | 60.4248 | 60.5164 | 60.466 | 0.70496 | 62.2604 | -60.2921 | -60.4935 | 62.3749 | 62.3703 | 62.3016 | 0.10986 | 0.041198 | -0.036621 | -0.050354 | -0.032043 | 122.8363 | 63.0249 | 122.7859 | 63.0615 | 122.8226 | 0.11444 | 0.022888 | 122.8729 | 122.7814 | 0.2243 | 122.7631 | 62.4847 | 122.7264 | -60.5164 | -122.8134 | 62.2833 | 122.7448 | 62.3154 | -0.20142
2503.8281 | 123.0652 | -62.3199 | 60.4431 | -0.022278 | -0.0018649 | -0.0083505 | 2.8922 | -0.0033753 | -0.0014184 | -0.0043943 | -0.030792 | 0.16202 | 0.12815 | -0.0084936 | 0.055824 | 0.10286 | -0.0010083 | -0.07782 | 0.059509 | -0.064087 | -0.064087 | 0.041199 | -0.022888 | 0.009155 | -62.471 | 60.3928 | -62.3657 | 60.4843 | 60.5942 | 60.4202 | 0.50812 | 62.2559 | -60.3836 | -60.5072 | 62.3611 | 62.3291 | 62.2971 | 0.073242 | 0.041199 | -0.045777 | -0.050354 | 0.041199 | 122.9141 | 62.8281 | 122.7402 | 62.8738 | 122.7859 | 0.10529 | 0 | 122.9599 | 122.85 | 0.1236 | 122.7585 | 62.3795 | 122.7127 | -60.5072 | -122.8088 | 62.2559 | 122.8043 | 62.2421 | -0.15106
2504.8281 | 123.0789 | -62.3383 | 60.4202 | -0.075684 | 0.00027134 | -0.0083505 | 2.8933 | 0.00089729 | -0.0031274 | -0.0026853 | -0.11014 | 0.16138 | 0.12623 | -0.004862 | 0.053474 | 0.10457 | -0.0012219 | -0.10529 | 0.009155 | -0.15564 | -0.11444 | -0.036621 | -0.15106 | -0.082397 | -62.4985 | 60.379 | -62.3795 | 60.4935 | 60.5301 | 60.3516 | 0.42114 | 62.1826 | -60.4111 | -60.5347 | 62.3016 | 62.2559 | 62.1872 | 0.073243 | 0.004578 | -0.041199 | -0.041199 | 0.073242 | 122.8683 | 62.7594 | 122.6898 | 62.8006 | 122.731 | 0.11902 | 0.041199 | 122.9095 | 122.8729 | 0.16479 | 122.7585 | 62.3474 | 122.7173 | -60.5759 | -122.7997 | 62.2238 | 122.8317 | 62.233 | -0.16022
2505.8906 | 122.9324 | -62.352 | 60.4111 | -0.045166 | -0.00036966 | -0.0092051 | 2.8943 | 0.0038879 | 0.001145 | -0.0016171 | -0.1315 | 0.16523 | 0.12794 | 5.1352e-05 | 0.056678 | 0.10457 | -0.00015387 | -0.068665 | 0.059509 | -0.14191 | -0.15106 | -0.07782 | -0.16937 | -0.11902 | -62.5992 | 60.4156 | -62.3978 | 60.3836 | 60.4248 | 60.2417 | 0.36621 | 62.2101 | -60.3516 | -60.5621 | 62.2742 | 62.233 | 62.1826 | 0.022888 | -0.027466 | -0.045776 | 0.004577 | -0.027466 | 122.7768 | 62.7182 | 122.5937 | 62.764 | 122.6395 | 0.064087 | -0.009155 | 122.8226 | 122.7814 | 0.20142 | 122.8134 | 62.4115 | 122.7676 | -60.553 | -122.8088 | 62.2009 | 122.7356 | 62.2833 | -0.24719
2506.8281 | 123.0515 | -62.3428 | 60.4111 | -0.11383 | -0.0031467 | -0.0081369 | 2.8941 | -0.00081171 | -0.00035036 | -0.00097627 | -0.11014 | 0.16181 | 0.12559 | -0.0050756 | 0.053688 | 0.10286 | -0.00015387 | -0.43488 | -0.068665 | -0.16022 | 0.018311 | 0.045776 | -0.036621 | 0.009155 | -62.4298 | 60.3653 | -62.3703 | 60.5118 | 60.5804 | 60.4019 | 0.43488 | 62.1826 | -60.4797 | -60.3928 | 62.3886 | 62.352 | 62.3062 | 0.16937 | 0.1236 | -0.027466 | -0.045777 | 0.10071 | 122.9233 | 62.7777 | 122.7448 | 62.8052 | 122.7722 | 0.20599 | 0.17853 | 122.9507 | 122.8821 | 0.091552 | 122.7356 | 62.2742 | 122.7081 | -60.5713 | -122.7814 | 62.3611 | 122.8546 | 61.908 | -0.086976
2507.8906 | 123.0011 | -62.3428 | 60.4797 | -0.022278 | -0.00079686 | -0.012837 | 2.8943 | -0.0016663 | -0.00035036 | -0.00076267 | -0.10403 | 0.16416 | 0.12623 | -0.0050756 | 0.056678 | 0.10393 | 0.00070073 | 0.45319 | 0.21515 | 0.027466 | -0.059509 | 0.041199 | -0.10529 | 0.004578 | -62.5442 | 60.4248 | -62.3611 | 60.4202 | 60.5164 | 60.3333 | 0.50354 | 62.3703 | -60.2646 | -60.5392 | 62.384 | 62.3474 | 62.2375 | -0.022888 | -0.13275 | -0.018311 | -0.054931 | -0.059509 | 122.8592 | 62.8464 | 122.6761 | 62.8647 | 122.6944 | 0.013733 | -0.086975 | 122.8775 | 122.7814 | 0.18768 | 122.7859 | 62.558 | 122.7676 | -60.4523 | -122.8409 | 62.2833 | 122.7631 | 62.796 | -0.20142
2508.8281 | 123.0423 | -62.3428 | 60.4156 | -0.098572 | -0.00079686 | -0.010487 | 2.892 | 0.00025629 | -0.0016322 | -0.0022581 | -0.070465 | 0.16373 | 0.12751 | -0.003794 | 0.056038 | 0.10436 | -0.00015387 | -0.059509 | -0.009155 | -0.09613 | -0.073242 | 0.059509 | -0.068665 | -0.027466 | -62.4435 | 60.3745 | -62.3566 | 60.4889 | 60.5392 | 60.3836 | 0.3891 | 62.2467 | -60.4248 | -60.4889 | 62.4023 | 62.3154 | 62.2742 | 0.068664 | 0.027465 | -0.013733 | -0.041198 | 0.073243 | 122.8821 | 62.7319 | 122.7264 | 62.7457 | 122.7402 | 0.15564 | 0.022888 | 122.8958 | 122.8455 | 0.086975 | 122.731 | 62.3337 | 122.7173 | -60.5118 | -122.7722 | 62.2696 | 122.8317 | 62.2833 | -0.10071
2509.8906 | 123.0743 | -62.3154 | 60.4156 | -0.083313 | -0.00036966 | -0.010059 | 2.8943 | 0.00068369 | -0.00099116 | -0.0035397 | -0.097931 | 0.16245 | 0.1273 | -0.0095618 | 0.05262 | 0.10308 | -0.0012219 | -0.050354 | -0.032043 | -0.14191 | -0.050354 | 0.054932 | -0.082397 | -0.036621 | -62.4207 | 60.3607 | -62.3428 | 60.5255 | 60.6033 | 60.434 | 0.43488 | 62.1735 | -60.4477 | -60.466 | 62.3703 | 62.2787 | 62.233 | 0.10529 | 0.05951 | -0.027465 | -0.054931 | 0.10986 | 122.9187 | 62.7502 | 122.7493 | 62.7777 | 122.7768 | 0.19684 | 0.091553 | 122.9462 | 122.8683 | 0.10986 | 122.7036 | 62.2833 | 122.6761 | -60.5576 | -122.7585 | 62.265 | 122.8409 | 62.265 | -0.10529
2510.8438 | 122.9919 | -62.3566 | 60.4706 | -0.045166 | -0.00058326 | -0.0098459 | 2.8924 | 0.0019653 | 0.00029044 | -0.0016171 | -0.16812 | 0.16224 | 0.12837 | -0.0044348 | 0.057319 | 0.10457 | -0.0039991 | 0 | 0.10529 | -0.073242 | -0.050354 | 0.045776 | -0.073242 | -0.004578 | -62.4619 | 60.4156 | -62.3383 | 60.5164 | 60.5164 | 60.3424 | 0.47607 | 62.2833 | -60.3653 | -60.5209 | 62.4023 | 62.352 | 62.2833 | 0.068664 | 0 | 0.01831 | -0.054932 | 0.045776 | 122.8729 | 62.8326 | 122.699 | 62.8143 | 122.6807 | 0.11902 | 0.022888 | 122.8546 | 122.8546 | 0.17853 | 122.7539 | 62.4619 | 122.7722 | -60.5438 | -122.8088 | 62.3062 | 122.8729 | 62.3566 | -0.10529
2511.8906 | 123.0835 | -62.3566 | 60.3973 | -0.083313 | -0.0010105 | -0.0074961 | 2.8933 | -0.0018799 | -0.0035548 | -0.0018307 | -0.10709 | 0.16373 | 0.12516 | -0.0033666 | 0.054115 | 0.1035 | -0.0031445 | -0.10071 | 0.013733 | -0.13275 | -0.11902 | -0.036621 | -0.15106 | -0.082397 | -62.471 | 60.3607 | -62.3703 | 60.4843 | 60.5759 | 60.379 | 0.43945 | 62.2238 | -60.3836 | -60.5164 | 62.3199 | 62.2742 | 62.2055 | 0.050354 | -0.018311 | -0.013733 | -0.036621 | 0.086975 | 122.9324 | 62.796 | 122.7356 | 62.8098 | 122.7493 | 0.09613 | 0.013732 | 122.9462 | 122.8546 | 0.14648 | 122.731 | 62.3703 | 122.7173 | -60.5301 | -122.7676 | 62.2375 | 122.8409 | 62.2559 | -0.11444
2512.8281 | 123.0515 | -62.3337 | 60.4202 | -0.083313 | -0.0016513 | -0.0092051 | 2.89 | -0.00081171 | -0.00035036 | -0.0026853 | -0.018585 | 0.16416 | 0.12944 | -0.0057166 | 0.056038 | 0.10329 | -0.00058107 | -0.036621 | 0.032043 | -0.09613 | -0.054932 | 0.045776 | -0.050354 | 0.073242 | -62.4847 | 60.3836 | -62.3566 | 60.498 | 60.5576 | 60.3699 | 0.4715 | 62.2375 | -60.3882 | -60.4752 | 62.3795 | 62.4069 | 62.2833 | 0.16937 | 0.045776 | -0.022888 | -0.036621 | 0.07782 | 122.8912 | 62.8052 | 122.7036 | 62.8281 | 122.7264 | 0.14191 | 0.041198 | 122.9141 | 122.8546 | 0.12817 | 122.7402 | 62.3657 | 122.7173 | -60.5164 | -122.7768 | 62.2787 | 122.8317 | 62.2971 | -0.15106
2513.8906 | 123.0606 | -62.3154 | 60.4202 | -0.029907 | -0.0016513 | -0.0081369 | 2.8945 | 0.00046989 | 0.00050424 | -0.0031125 | -0.058258 | 0.16224 | 0.12837 | -0.002085 | 0.05561 | 0.10201 | -0.0037855 | -0.054932 | 0.041199 | -0.082397 | -0.054932 | 0.041199 | -0.050354 | 0.013733 | -62.4802 | 60.3653 | -62.3428 | 60.4843 | 60.553 | 60.3836 | 0.45319 | 62.233 | -60.379 | -60.4752 | 62.3566 | 62.3291 | 62.265 | 0.09613 | 0.032043 | -0.027465 | -0.054932 | 0.064087 | 122.8683 | 62.7686 | 122.699 | 62.796 | 122.7264 | 0.1236 | 0.027465 | 122.8958 | 122.8271 | 0.1236 | 122.7081 | 62.3566 | 122.6807 | -60.5026 | -122.7631 | 62.2604 | 122.7997 | 62.2604 | -0.1648
2514.8281 | 123.1293 | -62.3199 | 60.4523 | 0.023498 | -0.0014377 | -0.0096323 | 2.8928 | 0.0017517 | -0.0029138 | -0.0018307 | -0.055206 | 0.16352 | 0.1288 | 0.004751 | 0.054542 | 0.10479 | -0.0067761 | 0.036621 | 0.050354 | -0.054932 | 0.059509 | 0.15564 | 0.054932 | 0.11902 | -62.352 | 60.379 | -62.3337 | 60.5713 | 60.6674 | 60.498 | 0.55847 | 62.265 | -60.4019 | -60.3928 | 62.4756 | 62.439 | 62.3749 | 0.17395 | 0.10986 | -0.013733 | -0.073243 | 0.11902 | 122.9874 | 62.8784 | 122.818 | 62.8922 | 122.8317 | 0.21057 | 0.11444 | 123.0011 | 122.905 | 0.10529 | 122.7127 | 62.3703 | 122.699 | -60.5072 | -122.7859 | 62.3795 | 122.8912 | 62.3566 | -0.032044
2515.9062 | 122.9919 | -61.322 | 61.4777 | -0.037537 | -0.00036966 | -0.0074961 | 2.8947 | -0.0025207 | -0.0044092 | -0.0011899 | -0.073517 | 0.010993 | 0.0078848 | -0.0052892 | -0.012963 | 0.0058788 | -0.0022901 | 0.027466 | 0.10986 | -0.064087 | -0.027466 | 0.054932 | -0.064087 | -0.004578 | 0.022888 | 0.20142 | -0.10529 | 0.027466 | 0.10071 | -0.022888 | 0.059509 | 61.2579 | -61.3678 | -61.5051 | 61.377 | 61.3174 | 61.2579 | 0.059509 | 0 | 61.2167 | -61.2762 | -61.4502 | 61.4227 | 61.3815 | 61.2991 | 0.16479 | 0.082398 | 0.11902 | 0.036621 | 0.20599 | 0.13275 | 0.17395 | 0.3067 | 61.4319 | 61.5234 | -61.5417 | -61.5829 | 61.2946 | 61.3495 | 61.3495 | 61.3449
2516.8281 | 123.0698 | -61.2854 | 61.496 | -0.037537 | -0.00079686 | -0.0092051 | 2.8898 | -0.00081171 | -0.0031274 | -0.0052487 | 0.021088 | 0.009925 | 0.007244 | -0.0059302 | -0.010186 | 0.0024608 | -0.0039991 | 0.059509 | 0.07782 | -0.036621 | 0.045776 | 0.16022 | 0.14191 | 0.55847 | -0.032043 | 0.24719 | -0.036621 | 0.054932 | 0.25635 | 0.15106 | 0.16937 | 61.2488 | -61.4182 | -61.4502 | 61.4456 | 61.8439 | 61.4273 | 0.59509 | 0.17853 | 61.2488 | -61.2488 | -61.441 | 61.5417 | 61.4548 | 61.4365 | 0.20599 | 0.18768 | 0.19684 | 0.082397 | 0.29297 | 0.091553 | 0.11444 | 0.28381 | 61.3632 | 61.5326 | -61.5326 | -61.5326 | 61.3312 | 61.3403 | 61.3449 | 61.2534
2517.8906 | 123.0881 | -61.29 | 61.4639 | -0.098572 | 0.00027134 | -0.0074961 | 2.8926 | 0.0055969 | -0.0020594 | -0.0022581 | -0.012482 | 0.01142 | 0.0059622 | -0.0016576 | -0.0091174 | 0.0041698 | -0.0018629 | -0.041199 | -0.036621 | -0.15106 | -0.050354 | 0.027466 | -0.09613 | -0.027466 | -0.013733 | 0.064087 | -0.19684 | -0.018311 | 0.050354 | -0.027466 | 0.054932 | 61.1389 | -61.5005 | -61.5143 | 61.3174 | 61.2625 | 61.1938 | 0.1236 | 0.054932 | 61.0931 | -61.3998 | -61.4822 | 61.3403 | 61.3449 | 61.2625 | 0.25177 | 0.16937 | 0.17853 | 0.10071 | 0.24719 | 0.17853 | 0.11444 | 0.26093 | 61.2534 | 61.3541 | -61.615 | -61.6608 | 61.2396 | 61.2717 | 61.2488 | 61.2762
2518.8281 | 122.9645 | -61.3358 | 61.5417 | -0.014649 | -0.0025059 | -0.010059 | 2.8939 | 0.00046989 | -0.0016322 | -0.0018307 | 0.033295 | 0.010566 | 0.0068168 | -0.0089208 | -0.0091174 | 0.0026746 | -0.0014355 | 0.009155 | 0.11444 | -0.041199 | -0.082397 | 0.082397 | -0.004578 | 0.018311 | 0 | 0.28839 | -0.064087 | 0.027466 | 0.13275 | 0.036621 | 0.082397 | 61.2946 | -61.4273 | -61.6241 | 61.4182 | 61.3541 | 61.3312 | 0.05951 | 0.036621 | 61.2717 | -61.2534 | -61.5143 | 61.4685 | 61.4182 | 61.3724 | 0.14648 | 0.10071 | 0.1236 | -0.041198 | 0.19684 | 0.091553 | 0.15564 | 0.35248 | 61.4502 | 61.6241 | -61.5829 | -61.6058 | 61.2534 | 61.3632 | 61.3449 | 61.3358
2519.8906 | 123.1018 | -61.2991 | 61.4685 | -0.060425 | -0.0014377 | -0.0083505 | 2.8939 | 0.0011109 | -0.00077756 | -0.0028989 | 0.04245 | 0.009925 | 0.0053214 | -0.0057166 | -0.0084766 | 0.0033154 | -0.0069897 | -0.032043 | 0.041199 | -0.073242 | -0.036621 | 0.050354 | -0.036621 | 0.022888 | 0.013733 | 0.15564 | -0.13275 | 0.050354 | 0.16022 | 0.068665 | 0.11902 | 61.2259 | -61.4273 | -61.5051 | 61.3495 | 61.322 | 61.2625 | 0.09613 | 0.036621 | 61.1664 | -61.3129 | -61.4182 | 61.4594 | 61.4182 | 61.3678 | 0.25177 | 0.20142 | 0.1236 | 0.036621 | 0.29297 | 0.18311 | 0.11444 | 0.28839 | 61.3403 | 61.4548 | -61.5417 | -61.6013 | 61.2625 | 61.3495 | 61.2671 | 61.3129
2520.8281 | 122.9965 | -61.3449 | 61.5143 | -0.029907 | 0.00069854 | -0.010273 | 2.895 | -0.0018799 | -0.0029138 | -0.0014035 | -0.06131 | 0.013129 | 0.0070304 | 0.004751 | -0.009972 | 0.0063062 | -0.0012219 | -0.050354 | 0.059509 | -0.11444 | -0.10071 | -0.032043 | -0.14648 | -0.07782 | -0.091553 | 0.16479 | -0.16479 | -0.073242 | -0.027466 | -0.12817 | -0.032043 | 61.2305 | -61.4548 | -61.615 | 61.3129 | 61.2671 | 61.1984 | 0.036621 | -0.032043 | 61.1801 | -61.3495 | -61.5875 | 61.3174 | 61.3129 | 61.2167 | 0.13275 | 0.036621 | 0.082398 | 0.013733 | 0.13733 | 0.091553 | 0.17395 | 0.32959 | 61.4044 | 61.5097 | -61.6287 | -61.6791 | 61.2442 | 61.2717 | 61.2946 | 61.2534
2521.8906 | 123.1293 | -61.2717 | 61.4822 | -0.083313 | 0.0011257 | -0.0092051 | 2.892 | 0.00089729 | -0.0018458 | -0.0043943 | 0.057709 | 0.010566 | 0.0053214 | 0.00026495 | -0.0074084 | 0.0058788 | -0.0033581 | 0.018311 | 0.068665 | -0.054932 | 0.013733 | 0.13275 | 0.027466 | 0.082397 | 0.11444 | 0.17395 | -0.091553 | 0.091553 | 0.27008 | 0.15106 | 0.17395 | 61.2167 | -61.4136 | -61.4685 | 61.4044 | 61.3541 | 61.2991 | 0.13733 | 0.082398 | 61.1801 | -61.3083 | -61.3907 | 61.5417 | 61.4456 | 61.4227 | 0.2655 | 0.24261 | 0.18768 | 0.068665 | 0.36163 | 0.18311 | 0.1236 | 0.2655 | 61.3403 | 61.4456 | -61.5372 | -61.5738 | 61.2854 | 61.3632 | 61.29 | 61.3861
2522.8281 | 123.0377 | -61.3129 | 61.4914 | -0.075684 | -0.00036966 | -0.0072825 | 2.8945 | 0.0021789 | -0.00077756 | -0.0033261 | -0.052155 | 0.013129 | 0.0091666 | -0.0018712 | -0.0095448 | 0.0043836 | 5.9726e-05 | 0.054932 | 0.10986 | -0.064087 | -0.045776 | 0.064087 | -0.054932 | 0.004578 | 0.022888 | 0.2243 | -0.09613 | 0.018311 | 0.11902 | 0.013733 | 0.082397 | 61.2488 | -61.3815 | -61.5372 | 61.377 | 61.3174 | 61.2579 | 0.068665 | 0.009155 | 61.2167 | -61.2671 | -61.4731 | 61.4319 | 61.3953 | 61.3266 | 0.17853 | 0.10986 | 0.12817 | 0.018311 | 0.21515 | 0.11444 | 0.17395 | 0.32043 | 61.4227 | 61.5372 | -61.5555 | -61.5875 | 61.2671 | 61.3312 | 61.3678 | 61.3358
2523.8906 | 123.0972 | -61.3266 | 61.5005 | -0.068054 | -0.0048557 | -0.0085641 | 2.8903 | -0.0014527 | -0.0012048 | -0.0035397 | 0.057709 | 0.010993 | 0.0031852 | -0.010416 | -0.0084766 | 0.0037426 | -0.0037855 | 0.13733 | 0.064087 | -0.064087 | -0.054932 | 0.041199 | -0.059509 | 0 | 0.004578 | 0.16479 | -0.13275 | 0.027466 | 0.14191 | 0.059509 | 0.10986 | 61.2625 | -61.4365 | -61.5555 | 61.3678 | 61.3266 | 61.2671 | 0.064087 | 0.004578 | 61.1938 | -61.3358 | -61.4731 | 61.4685 | 61.4365 | 61.3861 | 0.24261 | 0.19226 | 0.10529 | 0.009155 | 0.27466 | 0.16022 | 0.12817 | 0.29755 | 61.3907 | 61.4914 | -61.5646 | -61.6333 | 61.2717 | 61.3541 | 61.4639 | 61.3312
2524.8281 | 123.0377 | -61.3312 | 61.5372 | -0.014649 | -0.00079686 | -0.0079233 | 2.8937 | 0.0019653 | -0.0024866 | -0.0014035 | -0.052155 | 0.01142 | 0.0070304 | -0.0027258 | -0.010399 | 0.0063062 | -0.0052809 | -0.013733 | 0.064087 | -0.082397 | -0.045776 | -0.022888 | -0.28381 | 0.036621 | 0.041199 | 0.16479 | -0.13733 | 0.013733 | 0.064087 | -0.027466 | 0.059509 | 61.2488 | -61.4731 | -61.5829 | 61.3083 | 61.3678 | 61.0474 | 0.11902 | -0.20142 | 61.1938 | -61.3724 | -61.5234 | 61.3953 | 61.3907 | 61.3037 | 0.19684 | 0.10986 | 0.059509 | 0.036621 | 0.20142 | 0.15106 | 0.14648 | 0.30212 | 61.3953 | 61.496 | -61.6196 | -61.6745 | 61.2854 | 61.3449 | 61.3174 | 61.3724
2525.9062 | 123.1384 | -61.3083 | 61.4777 | -0.060425 | -0.0014377 | -0.0083505 | 2.8935 | -0.0012391 | -0.00056396 | -0.0033261 | -0.015534 | 0.011634 | 0.0061758 | -0.0044348 | -0.0091174 | 0.0060924 | -0.00079467 | -0.064087 | -0.004578 | -0.13733 | -0.059509 | 0.036621 | -0.091553 | -0.050354 | -0.036621 | 0.07782 | -0.21057 | 0.009155 | 0.059509 | -0.032043 | 0.068665 | 61.171 | -61.4822 | -61.5372 | 61.3449 | 61.2579 | 61.2167 | 0.086975 | 0.045776 | 61.0977 | -61.3998 | -61.4685 | 61.3678 | 61.377 | 61.2762 | 0.27924 | 0.17853 | 0.17395 | 0.07782 | 0.27008 | 0.21973 | 0.13275 | 0.28839 | 61.3037 | 61.3861 | -61.615 | -61.6882 | 61.2488 | 61.3174 | 61.2442 | 61.2717
2526.8281 | 123.0469 | -61.3403 | 61.5097 | -0.037537 | -0.00036966 | -0.0089913 | 2.8937 | 0.0028199 | -0.002273 | -0.0033261 | -0.055206 | 0.010566 | 0.0087394 | -0.0072118 | -0.010399 | 0.0056652 | -0.0037855 | -0.009155 | 0.082397 | -0.09613 | -0.036621 | 0.059509 | -0.064087 | -0.009155 | 0 | 0.20599 | -0.12817 | 0.045776 | 0.082397 | -0.004578 | 0.068665 | 61.2442 | -61.4273 | -61.5463 | 61.3998 | 61.3312 | 61.2762 | 0.086975 | 0.032043 | 61.2122 | -61.3037 | -61.4639 | 61.4227 | 61.409 | 61.3358 | 0.19684 | 0.1236 | 0.15564 | 0.059509 | 0.21057 | 0.17395 | 0.17853 | 0.33417 | 61.4227 | 61.5463 | -61.6058 | -61.6379 | 61.3037 | 61.3861 | 61.3312 | 61.3403
2527.8906 | 123.0103 | -61.3449 | 61.5097 | -0.075684 | -0.0025059 | -0.0089913 | 2.8924 | 0.00089729 | 0.00050424 | -0.0035397 | -0.033844 | 0.012061 | 0.0074576 | 0.0011194 | -0.0091174 | 0.0056652 | 0.00027333 | -0.064087 | 0.054932 | -0.11902 | -0.13275 | -0.041199 | -0.15564 | -0.10986 | -0.1236 | 0.16937 | -0.16022 | -0.10529 | -0.027466 | -0.16022 | -0.07782 | 61.2259 | -61.4548 | -61.6425 | 61.3037 | 61.235 | 61.1893 | 0.009156 | -0.036621 | 61.1847 | -61.3403 | -61.615 | 61.3174 | 61.2671 | 61.1847 | 0.082397 | 0 | 0.07782 | -0.013732 | 0.13275 | 0.054931 | 0.17395 | 0.32959 | 61.3998 | 61.5143 | -61.6287 | -61.6699 | 61.2122 | 61.2396 | 61.2808 | 61.2213
2528.8281 | 123.0011 | -61.3678 | 61.5326 | -0.068054 | -0.00015586 | -0.0060007 | 2.8922 | 0.00089729 | 0.0013586 | -0.0018307 | -0.039948 | 0.012488 | 0.0046806 | 5.1352e-05 | -0.0091174 | 0.003529 | -0.00079467 | -0.082397 | 0.064087 | -0.13733 | -0.14648 | -0.045776 | -0.15106 | -0.10529 | -0.12817 | 0.17853 | -0.17395 | -0.07782 | -0.068665 | -0.13733 | -0.050354 | 61.2305 | -61.4685 | -61.6791 | 61.322 | 61.2625 | 61.2167 | 0.032043 | -0.013733 | 61.1938 | -61.3541 | -61.6104 | 61.2991 | 61.3174 | 61.2305 | 0.1236 | 0.036621 | 0.091553 | -0.009155 | 0.10528 | 0.09613 | 0.20142 | 0.35248 | 61.4319 | 61.5463 | -61.6699 | -61.7065 | 61.2213 | 61.29 | 61.2854 | 61.2396
2529.8906 | 123.0286 | -61.3586 | 61.5372 | -0.022278 | -0.0046421 | -0.0074961 | 2.8937 | -0.0018799 | -0.0031274 | -0.0035397 | 0.04245 | 0.012488 | 0.0093802 | -0.0029394 | -0.0078358 | 0.003529 | -0.00079467 | 0.022888 | 0.1236 | -0.041199 | -0.050354 | 0.082397 | 0.068665 | 0.073242 | 0.009155 | 0.29297 | -0.059509 | 0.032043 | 0.14648 | 0.054932 | 0.073242 | 61.3174 | -61.4136 | -61.5875 | 61.441 | 61.4319 | 61.4273 | 0.11444 | 0.10986 | 61.2991 | -61.2442 | -61.5051 | 61.5051 | 61.4319 | 61.4136 | 0.13275 | 0.11444 | 0.1236 | -0.009155 | 0.20599 | 0.091552 | 0.16479 | 0.35248 | 61.4822 | 61.6516 | -61.5784 | -61.5967 | 61.3083 | 61.3907 | 61.3815 | 61.3678
2530.8281 | 123.056 | -61.3495 | 61.5051 | 0.13794 | -0.0067783 | -0.0068551 | 2.8937 | -0.00017091 | -0.0016322 | 0.00073273 | -0.039948 | 0.012488 | 0.0093802 | 0.00047855 | -0.0091174 | 0.0060924 | -0.0022901 | -0.17395 | -0.009155 | -0.19684 | -0.16479 | -0.11444 | -0.1831 | -0.11902 | -0.12817 | 0.14191 | -0.1831 | -0.09613 | -0.032043 | -0.10986 | -0.018311 | 61.1526 | -61.5143 | -61.6699 | 61.235 | 61.2305 | 61.1664 | 0.077819 | 0.013733 | 61.1664 | -61.3632 | -61.6013 | 61.3174 | 61.3312 | 61.2396 | 0.16479 | 0.073242 | 0.082397 | 0.032043 | 0.15106 | 0.086975 | 0.18768 | 0.32501 | 61.3403 | 61.4914 | -61.702 | -61.6882 | 61.1847 | 61.2534 | 61.1755 | 61.2213
2531.8906 | 123.0377 | -61.3449 | 61.5189 | -0.014649 | -0.0027195 | -0.0094187 | 2.8926 | 0.0011109 | -0.002273 | -0.0022581 | 0.014984 | 0.012702 | 0.005535 | -0.0057166 | -0.011681 | 0.0043836 | -0.0039991 | 0.022888 | 0.11902 | -0.059509 | -0.045776 | 0.054932 | -0.027466 | 0.022888 | -0.050354 | 0.23346 | -0.082397 | 0.036621 | 0.11902 | 0.027466 | 0.09613 | 61.2854 | -61.3998 | -61.5646 | 61.3998 | 61.3678 | 61.3174 | 0.082397 | 0.032043 | 61.2625 | -61.2854 | -61.4822 | 61.4639 | 61.441 | 61.3724 | 0.17853 | 0.10986 | 0.11444 | 0.013733 | 0.20142 | 0.11902 | 0.17853 | 0.31586 | 61.4639 | 61.5784 | -61.5784 | -61.6013 | 61.2991 | 61.3815 | 61.3678 | 61.2946
2532.8281 | 123.0743 | -61.3358 | 61.5051 | -0.068054 | -0.0033603 | -0.0077097 | 2.8907 | -0.0029479 | 7.6842e-05 | -0.0037533 | -0.0094299 | 0.011848 | 0.005535 | -0.0050756 | -0.0084766 | 0.0054516 | -0.0014355 | -0.10529 | 0.022888 | -0.14191 | -0.13733 | -0.054932 | -0.16022 | -0.10986 | -0.10529 | 0.11444 | -0.19684 | -0.045776 | 0.018311 | -0.086975 | 0.013733 | 61.1938 | -61.4822 | -61.6425 | 61.2808 | 61.2259 | 61.1755 | 0.032044 | -0.01831 | 61.1389 | -61.3907 | -61.5509 | 61.3541 | 61.3495 | 61.2488 | 0.21057 | 0.10986 | 0.086975 | 0.004578 | 0.21515 | 0.15106 | 0.16479 | 0.31128 | 61.3586 | 61.4502 | -61.647 | -61.702 | 61.1984 | 61.29 | 61.2305 | 61.2305
2533.8281 | 123.0377 | -61.3083 | 61.4502 | -0.12146 | -0.0010105 | -0.0092051 | 2.8943 | -0.0046569 | -0.0027002 | -0.0024717 | -0.0002747 | 0.012488 | 0.0085258 | -0.002085 | -0.010186 | 0.005238 | -0.0037855 | -0.068665 | -0.032043 | -0.1236 | -0.073242 | 0.036621 | -0.091553 | -0.032043 | -0.032043 | 0.068665 | -0.17853 | -0.018311 | 0.064087 | -0.018311 | 0.045776 | 61.1847 | -61.4822 | -61.5234 | 61.3449 | 61.2762 | 61.2167 | 0.091553 | 0.032043 | 61.1298 | -61.3815 | -61.4685 | 61.3724 | 61.3541 | 61.29 | 0.2243 | 0.16022 | 0.16022 | 0.050354 | 0.24261 | 0.16022 | 0.091553 | 0.24719 | 61.2762 | 61.377 | -61.5738 | -61.6287 | 61.235 | 61.29 | 61.2396 | 61.2762
2534.8906 | 123.111 | -61.322 | 61.5051 | -0.20538 | -0.0035739 | -0.0089913 | 2.892 | -0.0018799 | -0.0014184 | -0.0041807 | 0.072967 | 0.012061 | 0.0076712 | -0.00828 | -0.010186 | 0.00182 | 0.0013415 | 0.28381 | 0.12817 | 0.022888 | 0.10071 | 0.1236 | 0.009155 | 0.10529 | 0.10986 | 0.1831 | -0.07782 | 0.10071 | 0.20599 | 0.13733 | 0.16937 | 61.3449 | -61.377 | -61.4044 | 61.4456 | 61.4273 | 61.3312 | 0.082398 | -0.013733 | 61.2442 | -61.322 | -61.4044 | 61.528 | 61.4914 | 61.4594 | 0.24719 | 0.21515 | 0.10071 | 0.07782 | 0.28381 | 0.17853 | 0.10529 | 0.26092 | 61.4502 | 61.5051 | -61.4822 | -61.5829 | 61.4227 | 61.4227 | 61.6058 | 61.4319
2535.8281 | 123.0881 | -61.322 | 61.5097 | -0.083313 | -0.0020785 | -0.010273 | 2.8928 | 0.0032471 | -0.002273 | -0.0020443 | 0.06076 | 0.009925 | 0.0098074 | -0.0010168 | -0.010399 | 0.0024608 | -0.0033581 | -0.07782 | 0.018311 | -0.10071 | -0.068665 | 0.027466 | -0.07782 | -0.013733 | -0.041199 | 0.13275 | -0.15106 | 0.004578 | 0.086975 | 0.018311 | 0.07782 | 61.2213 | -61.4914 | -61.5784 | 61.3495 | 61.3083 | 61.2442 | 0.086975 | 0.022888 | 61.171 | -61.377 | -61.5051 | 61.409 | 61.3998 | 61.3403 | 0.22888 | 0.16937 | 0.12817 | 0.032043 | 0.23804 | 0.15564 | 0.11902 | 0.28381 | 61.3403 | 61.4548 | -61.6104 | -61.6608 | 61.2534 | 61.3266 | 61.2442 | 61.2808
2536.8906 | 123.0698 | -61.322 | 61.5234 | -0.045166 | 0.00069854 | -0.010059 | 2.8945 | 0.00025629 | -0.0018458 | -0.0018307 | -0.042999 | 0.013557 | 0.0087394 | 0.0034692 | -0.0089038 | 0.0054516 | 0.00027333 | 0.009155 | 0.086975 | -0.064087 | -0.041199 | 0.073242 | -0.059509 | 0.004578 | 0.018311 | 0.21057 | -0.09613 | 0.013733 | 0.086975 | 0 | 0.082397 | 61.2579 | -61.4365 | -61.5646 | 61.3953 | 61.3266 | 61.2625 | 0.068665 | 0.004578 | 61.2259 | -61.3129 | -61.5097 | 61.409 | 61.4044 | 61.322 | 0.17853 | 0.09613 | 0.13733 | 0.022888 | 0.1831 | 0.10986 | 0.15106 | 0.3067 | 61.409 | 61.5326 | -61.5875 | -61.6196 | 61.2808 | 61.3358 | 61.3312 | 61.3403
2537.8281 | 123.1293 | -61.3083 | 61.5051 | -0.090943 | -0.00015586 | -0.0096323 | 2.893 | -0.0010253 | 0.0015722 | -0.0050351 | 0.051605 | 0.010139 | 0.0066032 | -0.0050756 | -0.0095448 | 0.0016064 | -0.0018629 | -0.068665 | 0.009155 | -0.10986 | -0.09613 | 0.018311 | -0.09613 | -0.041199 | -0.054932 | 0.11902 | -0.16479 | -0.004578 | 0.073242 | 0.004578 | 0.059509 | 61.1984 | -61.496 | -61.6013 | 61.3266 | 61.2671 | 61.2122 | 0.068664 | 0.013733 | 61.1435 | -61.3861 | -61.5097 | 61.3815 | 61.3678 | 61.3129 | 0.2243 | 0.16937 | 0.12817 | 0.013733 | 0.23804 | 0.16022 | 0.11902 | 0.28381 | 61.3174 | 61.4273 | -61.615 | -61.6699 | 61.2122 | 61.3037 | 61.2396 | 61.2534
2538.8906 | 123.1293 | -61.3266 | 61.4822 | -0.11383 | 0.00027134 | -0.0077097 | 2.8926 | 0.0026063 | -0.0018458 | -0.0031125 | 0.030243 | 0.011634 | 0.0066032 | -0.0050756 | -0.0095448 | 0.0045972 | -0.00015387 | -0.018311 | -0.004578 | -0.09613 | -0.032043 | 0.073242 | -0.073242 | -0.018311 | -0.009155 | 0.09613 | -0.17395 | -0.004578 | 0.064087 | -0.004578 | 0.050354 | 61.2305 | -61.4868 | -61.5143 | 61.3998 | 61.3083 | 61.2534 | 0.077819 | 0.022888 | 61.1526 | -61.3861 | -61.4868 | 61.3907 | 61.377 | 61.322 | 0.2243 | 0.16937 | 0.16937 | 0.064087 | 0.23804 | 0.16937 | 0.091552 | 0.27008 | 61.322 | 61.4227 | -61.5784 | -61.6562 | 61.2946 | 61.322 | 61.3083 | 61.3174
2539.8281 | 123.1522 | -61.322 | 61.496 | -0.014649 | -0.0014377 | -0.0096323 | 2.8924 | -0.00017091 | -0.0044092 | -0.0043943 | 0.06076 | 0.01377 | 0.0085258 | -0.0095618 | -0.009331 | 0.0031018 | -0.0035719 | -0.022888 | 0.041199 | -0.073242 | -0.032043 | 0.073242 | -0.013733 | 0.041199 | 0.027466 | 0.16022 | -0.09613 | 0.064087 | 0.17395 | 0.082397 | 0.13733 | 61.2488 | -61.4548 | -61.528 | 61.3953 | 61.3632 | 61.3083 | 0.11444 | 0.059509 | 61.2259 | -61.3358 | -61.4319 | 61.496 | 61.4594 | 61.4044 | 0.23346 | 0.17853 | 0.14648 | 0.041199 | 0.27008 | 0.16022 | 0.11444 | 0.25635 | 61.3632 | 61.4822 | -61.5692 | -61.5921 | 61.29 | 61.3861 | 61.2991 | 61.3495
2540.8906 | 123.0972 | -61.3449 | 61.5234 | -0.090943 | -0.0016513 | -0.0083505 | 2.8937 | 0.0019653 | -0.0027002 | -0.0031125 | -0.070465 | 0.010139 | 0.0059622 | -0.00016245 | -0.011254 | 0.0060924 | -0.0033581 | 0 | 0.082397 | -0.064087 | -0.045776 | 0.045776 | -0.050354 | 0.004578 | -0.036621 | 0.19226 | -0.10986 | 0.059509 | 0.07782 | -0.013733 | 0.068665 | 61.2808 | -61.441 | -61.5692 | 61.3907 | 61.3495 | 61.2946 | 0.068665 | 0.013733 | 61.235 | -61.3312 | -61.4639 | 61.4227 | 61.4136 | 61.3312 | 0.17853 | 0.09613 | 0.10986 | 0.018311 | 0.18768 | 0.16937 | 0.14648 | 0.30212 | 61.4273 | 61.5372 | -61.5875 | -61.6333 | 61.2991 | 61.4044 | 61.3449 | 61.3083
2541.8281 | 123.1796 | -61.2991 | 61.4685 | -0.060425 | -0.00079686 | -0.0089913 | 2.8924 | -0.00081171 | -0.0037684 | -0.0024717 | 0.039398 | 0.012916 | 0.0074576 | -0.0016576 | -0.0097584 | 0.0041698 | -0.0014355 | -0.009155 | 0.07782 | -0.050354 | 0.013733 | 0.14191 | 0.027466 | 0.073242 | 0.073242 | 0.16479 | -0.07782 | 0.11444 | 0.20142 | 0.10986 | 0.17853 | 61.2488 | -61.3907 | -61.4548 | 61.441 | 61.3724 | 61.3266 | 0.1236 | 0.07782 | 61.2213 | -61.3037 | -61.3541 | 61.5005 | 61.4777 | 61.409 | 0.25635 | 0.18768 | 0.19226 | 0.064087 | 0.27924 | 0.19226 | 0.12817 | 0.24261 | 61.377 | 61.4639 | -61.5189 | -61.5463 | 61.3129 | 61.4136 | 61.29 | 61.3724
2542.8906 | 123.1659 | -61.3266 | 61.4914 | -0.060425 | 0.00027134 | -0.010487 | 2.8928 | -0.0025207 | -0.0031274 | 0.00073273 | -0.030792 | 0.013557 | 0.0078848 | -0.0025122 | -0.0086902 | 0.0063062 | -0.00058107 | -0.086975 | 0.009155 | -0.15564 | -0.11444 | -0.013733 | -0.11902 | -0.059509 | -0.054932 | 0.09613 | -0.16937 | -0.013733 | 0.07782 | -0.050354 | 0.054932 | 61.171 | -61.4822 | -61.6058 | 61.3129 | 61.2671 | 61.2076 | 0.096131 | 0.036621 | 61.1572 | -61.3953 | -61.5051 | 61.4044 | 61.3815 | 61.2762 | 0.22431 | 0.11902 | 0.14191 | 0.041199 | 0.24719 | 0.15564 | 0.16479 | 0.2655 | 61.3358 | 61.4227 | -61.647 | -61.6608 | 61.2122 | 61.3129 | 61.2396 | 61.2717
2543.8281 | 123.1613 | -61.3129 | 61.528 | -0.083313 | -0.0020785 | -0.0085641 | 2.8924 | -0.0044433 | -0.00013676 | -0.0048215 | 0.063812 | 0.010352 | 0.0061758 | -0.002085 | -0.010826 | 0.0028882 | -0.00058107 | 0.050354 | 0.059509 | -0.036621 | 0.050354 | 0.17853 | 0.068665 | 0.11902 | 0.16479 | 0.20142 | -0.064087 | 0.10529 | 0.21515 | 0.13275 | 0.16937 | 61.2762 | -61.4685 | -61.4777 | 61.4914 | 61.4319 | 61.3815 | 0.15564 | 0.10529 | 61.2488 | -61.3266 | -61.4227 | 61.528 | 61.4822 | 61.4456 | 0.23346 | 0.19684 | 0.21515 | 0.086975 | 0.27924 | 0.16937 | 0.09613 | 0.2655 | 61.3724 | 61.5143 | -61.5646 | -61.5921 | 61.3632 | 61.4182 | 61.3632 | 61.4777
2544.8906 | 123.1476 | -61.3083 | 61.5005 | -0.1062 | -0.0012241 | -0.0079233 | 2.892 | 0.0019653 | -0.0037684 | -0.0022581 | 0.0027771 | 0.011848 | 0.0046806 | 0.00026495 | -0.009331 | 0.0050244 | -0.00058107 | 0 | 0 | -0.10071 | -0.041199 | 0.082397 | -0.091553 | -0.022888 | 0.009155 | 0.07782 | -0.15564 | -0.013733 | 0.068665 | -0.018311 | 0.068665 | 61.2076 | -61.5005 | -61.5417 | 61.3907 | 61.2854 | 61.2167 | 0.07782 | 0.009155 | 61.1526 | -61.4227 | -61.5143 | 61.377 | 61.377 | 61.29 | 0.22431 | 0.13733 | 0.18311 | 0.059509 | 0.22431 | 0.14191 | 0.10071 | 0.23346 | 61.3083 | 61.3861 | -61.6013 | -61.6562 | 61.2671 | 61.2946 | 61.3083 | 61.3174
2545.8281 | 123.0927 | -61.3449 | 61.5417 | -0.052796 | -0.0018649 | -0.0087777 | 2.8939 | -0.0059387 | -0.0016322 | -0.0037533 | 0.024139 | 0.012061 | 0.0087394 | -0.0063574 | -0.0078358 | 0.0037426 | -0.0046399 | 0.054932 | 0.07782 | -0.032043 | 0.036621 | 0.15564 | 0.041199 | 0.091553 | 0.082397 | 0.20599 | -0.059509 | 0.091553 | 0.1831 | 0.09613 | 0.15564 | 61.3129 | -61.4639 | -61.5051 | 61.5005 | 61.4365 | 61.3861 | 0.1236 | 0.073242 | 61.2854 | -61.3358 | -61.4502 | 61.528 | 61.5005 | 61.441 | 0.21515 | 0.15564 | 0.18768 | 0.068664 | 0.24261 | 0.15106 | 0.10986 | 0.2655 | 61.4227 | 61.5509 | -61.5738 | -61.6013 | 61.3815 | 61.4365 | 61.3998 | 61.4273
2546.8906 | 123.1155 | -61.3312 | 61.5051 | -0.052796 | -0.00079686 | -0.0089913 | 2.8935 | 0.0013245 | 0.00050424 | -0.0024717 | 0.018036 | 0.010352 | 0.0070304 | -0.0040076 | -0.0091174 | 0.0041698 | -0.00015387 | -0.07782 | -0.009155 | -0.11902 | -0.059509 | 0.059509 | -0.082397 | -0.018311 | -0.018311 | 0.082397 | -0.17395 | -0.018311 | 0.068665 | -0.018311 | 0.050354 | 61.2122 | -61.5143 | -61.5646 | 61.3907 | 61.3129 | 61.2488 | 0.10071 | 0.036622 | 61.1572 | -61.4227 | -61.5234 | 61.3998 | 61.3815 | 61.3129 | 0.2243 | 0.15564 | 0.17853 | 0.05951 | 0.24261 | 0.15564 | 0.10986 | 0.25635 | 61.322 | 61.4136 | -61.6241 | -61.6791 | 61.2717 | 61.3129 | 61.2534 | 61.3129
2547.8281 | 123.056 | -61.3495 | 61.5509 | -0.098572 | 0.00069854 | -0.0081369 | 2.8924 | -0.0027343 | -0.0027002 | -0.0033261 | -0.0063781 | 0.01142 | 0.0076712 | 0.0041102 | -0.0095448 | 0.0033154 | -0.0022901 | 0.045776 | 0.10986 | -0.036621 | 0.004578 | 0.086975 | 0 | 0.064087 | 0.045776 | 0.2655 | -0.050354 | 0.027466 | 0.14191 | 0.041199 | 0.082397 | 61.3129 | -61.441 | -61.5463 | 61.4365 | 61.4136 | 61.3495 | 0.10071 | 0.036621 | 61.2991 | -61.2854 | -61.5234 | 61.4914 | 61.4319 | 61.3907 | 0.13275 | 0.091553 | 0.1236 | 0.041199 | 0.19226 | 0.07782 | 0.14648 | 0.31586 | 61.4594 | 61.615 | -61.5875 | -61.6013 | 61.3541 | 61.377 | 61.3953 | 61.3953
2548.8906 | 123.1338 | -61.3358 | 61.5234 | -0.090943 | -0.00015586 | -0.0098459 | 2.893 | -0.0025207 | -0.0024866 | -0.0043943 | 0.033295 | 0.010779 | 0.0061758 | 0.003042 | -0.010613 | 0.0031018 | -0.0029309 | -0.045776 | 0.041199 | -0.07782 | -0.064087 | -0.004578 | 0.2655 | 0.10529 | -0.050354 | 0.16022 | -0.11444 | 0.013733 | 0.10071 | 0.041199 | 0.086975 | 61.2579 | -61.4822 | -61.5875 | 61.3312 | 61.441 | 61.6013 | 0.18311 | 0.34332 | 61.2213 | -61.3632 | -61.5097 | 61.4365 | 61.4227 | 61.377 | 0.20142 | 0.15564 | 0.073242 | 0.013733 | 0.21515 | 0.12817 | 0.11902 | 0.27466 | 61.377 | 61.496 | -61.6013 | -61.6379 | 61.2717 | 61.3495 | 61.29 | 61.2854
2549.8281 | 123.0469 | -61.3586 | 61.5646 | -0.037537 | -0.0016513 | -0.010914 | 2.8926 | 0.0015381 | -0.0027002 | -0.0028989 | -0.0063781 | 0.013984 | 0.0078848 | -0.001444 | -0.0074084 | 0.0024608 | 0.0017687 | -0.013733 | 0.13733 | -0.041199 | -0.032043 | 0.041199 | -0.027466 | 0.018311 | 0.009155 | 0.27008 | -0.059509 | 0.022888 | 0.12817 | 0.009155 | 0.086975 | 61.3174 | -61.4273 | -61.5967 | 61.3998 | 61.377 | 61.3312 | 0.05951 | 0.013733 | 61.2991 | -61.2946 | -61.5417 | 61.4868 | 61.4456 | 61.3678 | 0.14648 | 0.068664 | 0.082398 | 0.009156 | 0.18768 | 0.082397 | 0.17853 | 0.32959 | 61.496 | 61.6287 | -61.6058 | -61.6241 | 61.3266 | 61.3815 | 61.3449 | 61.3678
2550.8906 | 123.143 | -61.3358 | 61.5143 | -0.098572 | -0.0022923 | -0.010059 | 2.8918 | -0.0014527 | -0.0031274 | -0.0026853 | 0.027191 | 0.014197 | 0.0098074 | -0.0061438 | -0.009331 | 0.0037426 | -0.0018629 | -0.036621 | 0.045776 | -0.082397 | -0.036621 | 0.045776 | -0.045776 | 0.018311 | 0.027466 | 0.15106 | -0.10986 | 0.054932 | 0.14648 | 0.059509 | 0.10986 | 61.2534 | -61.4685 | -61.5509 | 61.3815 | 61.3541 | 61.29 | 0.10071 | 0.036621 | 61.2259 | -61.3632 | -61.4594 | 61.4822 | 61.4456 | 61.3953 | 0.21973 | 0.16937 | 0.12817 | 0.045776 | 0.25635 | 0.16479 | 0.12817 | 0.26093 | 61.3815 | 61.4868 | -61.5967 | -61.6241 | 61.2991 | 61.3907 | 61.2991 | 61.3632
2551.8281 | 123.0377 | -61.3632 | 61.5601 | -0.052796 | -0.0020785 | -0.010059 | 2.893 | -0.0016663 | -0.0016322 | -0.0075985 | 0.033295 | 0.012916 | 0.010448 | -0.0042212 | -0.0089038 | 0.00182 | -0.0010083 | 0.022888 | 0.16022 | -0.045776 | -0.036621 | 0.041199 | -0.013733 | -0.022888 | -0.36163 | 0.32501 | -0.022888 | -0.018311 | 0.068665 | 0.032043 | 0.10529 | 61.3174 | -61.3998 | -61.5967 | 61.4044 | 61.3403 | 61.3495 | 0.022888 | 0.032043 | 61.3403 | -61.235 | -61.5784 | 61.4319 | 61.4685 | 61.3953 | 0.12817 | 0.054931 | 0.086975 | 0.009155 | 0.091553 | 0.004577 | 0.20599 | 0.3479 | 61.5234 | 61.6882 | -61.6058 | -61.5829 | 61.3266 | 61.3449 | 61.3861 | 61.0016
2552.8906 | 123.1247 | -61.3541 | 61.5097 | -0.052796 | -0.00058326 | -0.0089913 | 2.8928 | -0.00081171 | -0.0027002 | -0.0014035 | 0.021088 | 0.009284 | 0.0053214 | -0.004862 | -0.010613 | 0.0048108 | -0.0016493 | -0.091553 | 0.009155 | -0.11444 | -0.073242 | 0.009155 | -0.07782 | -0.013733 | -0.022888 | 0.10071 | -0.14191 | -0.013733 | 0.082397 | 0.009155 | 0.086975 | 61.2396 | -61.5005 | -61.5829 | 61.3632 | 61.3403 | 61.2762 | 0.10071 | 0.036621 | 61.2122 | -61.409 | -61.5234 | 61.4365 | 61.441 | 61.3632 | 0.22888 | 0.15106 | 0.1236 | 0.041199 | 0.2243 | 0.12817 | 0.1236 | 0.24262 | 61.3632 | 61.4548 | -61.6241 | -61.6516 | 61.2808 | 61.3403 | 61.2625 | 61.3312
2553.8281 | 123.1064 | -61.3266 | 61.5463 | -0.075684 | -0.00015586 | -0.010273 | 2.8941 | 0.0041015 | -0.0027002 | -0.00033547 | -0.058258 | 0.013984 | 0.0080984 | 0.00090575 | -0.0091174 | 0.0067334 | 0.0015551 | 0.041199 | 0.15106 | -0.050354 | -0.013733 | 0.050354 | -0.027466 | 0.013733 | 0.027466 | 0.23804 | -0.059509 | 0.045776 | 0.12817 | 0.054932 | 0.086975 | 61.2762 | -61.3953 | -61.5601 | 61.377 | 61.3403 | 61.2991 | 0.064087 | 0.022888 | 61.2671 | -61.3083 | -61.5006 | 61.4548 | 61.4136 | 61.3815 | 0.14648 | 0.11444 | 0.10071 | 0.036621 | 0.18768 | 0.10528 | 0.20142 | 0.29755 | 61.4777 | 61.5646 | -61.5967 | -61.6058 | 61.3129 | 61.3724 | 61.3678 | 61.3541
2554.8906 | 123.0606 | -61.3495 | 61.5555 | -0.037537 | -0.0010105 | -0.0107 | 2.8943 | 0.0019653 | -0.0033412 | -0.0037533 | 0.021088 | 0.01377 | 0.0063896 | -0.0040076 | -0.011467 | 0.0026746 | 0.0013415 | 0.036621 | 0.12817 | -0.050354 | -0.036621 | 0.064087 | -0.027466 | 0.050354 | -0.004578 | 0.2655 | -0.050354 | 0.036621 | 0.1236 | 0.054932 | 0.10071 | 61.2991 | -61.4273 | -61.5921 | 61.4136 | 61.3998 | 61.322 | 0.10071 | 0.022888 | 61.2991 | -61.29 | -61.5189 | 61.4731 | 61.4502 | 61.4044 | 0.15106 | 0.10529 | 0.11444 | 0.013733 | 0.17395 | 0.086975 | 0.17853 | 0.31586 | 61.4777 | 61.615 | -61.6058 | -61.6058 | 61.3129 | 61.3861 | 61.3861 | 61.3449
2555.8281 | 123.0652 | -61.377 | 61.5509 | -0.045166 | -0.00036966 | -0.0087777 | 2.8956 | -0.00059811 | -0.0016322 | -0.0018307 | -0.067413 | 0.012275 | 0.0078848 | -0.0018712 | -0.0086902 | 0.0037426 | -0.0010083 | -0.036621 | 0.07782 | -0.10529 | -0.10071 | 0.009155 | -0.13275 | -0.064087 | -0.059509 | 0.17395 | -0.16022 | -0.045776 | 0.022888 | -0.082397 | 0.004578 | 61.2717 | -61.4731 | -61.6516 | 61.3861 | 61.3129 | 61.2442 | 0.041199 | -0.027465 | 61.2167 | -61.377 | -61.5967 | 61.3998 | 61.3815 | 61.2946 | 0.16479 | 0.07782 | 0.11444 | 0.004578 | 0.1831 | 0.11444 | 0.18311 | 0.33417 | 61.4548 | 61.5509 | -61.6562 | -61.7111 | 61.2762 | 61.3312 | 61.3403 | 61.3174
2556.8906 | 123.1705 | -61.322 | 61.528 | -0.068054 | -0.00036966 | -0.0092051 | 2.893 | 0.0038879 | -0.00099116 | -0.0024717 | 0.063812 | 0.011207 | 0.0085258 | -0.0080664 | -0.010613 | 0.0065198 | -0.00036747 | 0.054932 | 0.064087 | -0.009155 | 0.041199 | 0.26093 | -0.14648 | 0 | 0.10071 | 0.17853 | -0.09613 | 0.091553 | 0.21515 | 0.12817 | 0.17395 | 61.3129 | -61.4639 | -61.4868 | 61.5829 | 61.322 | 61.1755 | 0.009155 | -0.13733 | 61.2259 | -61.3495 | -61.4365 | 61.5372 | 61.496 | 61.4502 | 0.27008 | 0.2243 | 0.27008 | 0.050354 | 0.31128 | 0.18768 | 0.073242 | 0.27466 | 61.3861 | 61.5005 | -61.5372 | -61.6241 | 61.3632 | 61.4136 | 61.377 | 61.4227
2557.8281 | 123.1155 | -61.3495 | 61.528 | 0.00061049 | 0.0013393 | -0.012196 | 2.8915 | 0.0060241 | -0.0018458 | -0.0020443 | -0.036896 | 0.013984 | 0.0063896 | 0.003042 | -0.0069812 | 0.0048108 | -0.0069897 | 0.036621 | 0.10071 | -0.059509 | -0.036621 | 0.050354 | -0.050354 | 0.009155 | 0.036621 | 0.21515 | -0.09613 | 0.013733 | 0.068665 | 0 | 0.068665 | 61.29 | -61.4273 | -61.5646 | 61.3998 | 61.3586 | 61.2991 | 0.068664 | 0.009155 | 61.2534 | -61.3129 | -61.5143 | 61.4182 | 61.4182 | 61.3495 | 0.16479 | 0.09613 | 0.10986 | 0.022888 | 0.16479 | 0.10986 | 0.16022 | 0.31128 | 61.4502 | 61.5646 | -61.5875 | -61.6241 | 61.3129 | 61.3632 | 61.3861 | 61.3861
2558.8906 | 123.0698 | -61.3358 | 61.5601 | -0.037537 | 0.00048494 | -0.0079233 | 2.893 | 0.0028199 | -0.0037684 | -0.0043943 | 0.021088 | 0.013343 | 0.0074576 | -0.0033666 | -0.0074084 | 0.0028882 | -0.00015387 | 0.032043 | 0.11444 | -0.018311 | -0.009155 | 0.10986 | 0.009155 | 0.050354 | 0.054932 | 0.24261 | -0.050354 | 0.036621 | 0.14191 | 0.050354 | 0.082397 | 61.3174 | -61.4456 | -61.5692 | 61.4456 | 61.3861 | 61.3449 | 0.068665 | 0.027466 | 61.2854 | -61.3174 | -61.5234 | 61.4777 | 61.4182 | 61.3861 | 0.13275 | 0.10071 | 0.12817 | 0.009156 | 0.19226 | 0.086975 | 0.13275 | 0.29297 | 61.4502 | 61.5784 | -61.5784 | -61.6104 | 61.3266 | 61.3724 | 61.3678 | 61.3907
2559.8281 | 123.0835 | -61.3632 | 61.5463 | -0.022278 | -0.00058326 | -0.010914 | 2.8945 | 0.0036743 | -0.0014184 | -0.00076267 | -0.052155 | 0.010993 | 0.0093802 | -0.00037605 | -0.010186 | 0.0058788 | -0.00036747 | 0.009155 | 0.086975 | -0.07782 | -0.045776 | 0.059509 | -0.045776 | -0.022888 | 0.036621 | 0.18768 | -0.11444 | 0.054932 | 0.07782 | 0 | 0.064087 | 61.2854 | -61.4594 | -61.5921 | 61.4227 | 61.3403 | 61.3174 | 0.054932 | 0.032044 | 61.2488 | -61.3586 | -61.4914 | 61.441 | 61.4273 | 61.3632 | 0.17853 | 0.11444 | 0.13733 | 0.032044 | 0.19226 | 0.16937 | 0.16479 | 0.30212 | 61.4502 | 61.5509 | -61.6241 | -61.6608 | 61.3174 | 61.4182 | 61.3724 | 61.3998
2560.8906 | 123.0606 | -61.3586 | 61.5601 | -0.068054 | -0.0016513 | -0.0096323 | 2.8915 | 0.0011109 | -0.0012048 | -0.0031125 | 0.0088807 | 0.012275 | 0.008953 | -0.0069982 | -0.0084766 | 0.0048108 | 0.00048713 | 0.022888 | 0.1236 | -0.045776 | -0.027466 | 0.036621 | -0.022888 | 0.027466 | 0.018311 | 0.27466 | -0.059509 | 0.018311 | 0.11902 | 0.050354 | 0.086975 | 61.3129 | -61.4365 | -61.5875 | 61.3953 | 61.3861 | 61.3358 | 0.073242 | 0.022888 | 61.2991 | -61.2854 | -61.5417 | 61.4777 | 61.4456 | 61.409 | 0.14648 | 0.10986 | 0.082397 | 0.01831 | 0.17853 | 0.07782 | 0.16937 | 0.33417 | 61.4822 | 61.6333 | -61.6058 | -61.6196 | 61.3312 | 61.377 | 61.3815 | 61.377
2561.8281 | 123.0515 | -61.3541 | 61.5555 | -0.1062 | 0.0011257 | -0.0081369 | 2.8922 | 0.0017517 | 0.00071784 | -0.0020443 | -0.033844 | 0.012916 | 0.010235 | 0.0024012 | -0.0097584 | 0.0056652 | -0.0022901 | -0.059509 | 0.064087 | -0.091553 | -0.10986 | -0.018311 | -0.13733 | -0.082397 | -0.073242 | 0.16937 | -0.15564 | -0.054932 | 0 | -0.11902 | -0.018311 | 61.2625 | -61.4914 | -61.6653 | 61.3358 | 61.2717 | 61.2167 | 0.009156 | -0.045776 | 61.1984 | -61.3861 | -61.6104 | 61.3541 | 61.3358 | 61.235 | 0.13733 | 0.036621 | 0.073242 | -0.01831 | 0.15564 | 0.10071 | 0.15564 | 0.32501 | 61.4182 | 61.5234 | -61.647 | -61.7111 | 61.2442 | 61.2991 | 61.2946 | 61.2808
2562.8906 | 123.1796 | -61.3312 | 61.528 | -0.075684 | -0.0020785 | -0.0083505 | 2.893 | -0.00081171 | -0.00077756 | -0.0031125 | 0.088226 | 0.011634 | 0.0066032 | -0.0074254 | -0.010826 | 0.0041698 | -0.0016493 | -0.027466 | 0.022888 | -0.073242 | -0.013733 | 0.10071 | 0 | 0.054932 | 0.068665 | 0.16022 | -0.10529 | 0.073242 | 0.1831 | 0.091553 | 0.13733 | 61.2579 | -61.5051 | -61.5417 | 61.4319 | 61.3861 | 61.3312 | 0.12817 | 0.073242 | 61.2259 | -61.3678 | -61.4548 | 61.5143 | 61.4685 | 61.4227 | 0.24262 | 0.19684 | 0.17395 | 0.059509 | 0.28839 | 0.17853 | 0.09613 | 0.2655 | 61.3541 | 61.4914 | -61.6013 | -61.6333 | 61.3174 | 61.4044 | 61.3037 | 61.3998
2563.8281 | 123.0743 | -61.3678 | 61.5509 | -0.037537 | -0.00058326 | -0.0083505 | 2.8926 | 0.0032471 | -0.0029138 | -0.0028989 | -0.049103 | 0.010779 | 0.0083122 | 0.0028284 | -0.0076222 | 0.0041698 | -0.00079467 | -0.068665 | 0.050354 | -0.10986 | -0.11444 | -0.036621 | -0.15564 | -0.10529 | -0.09613 | 0.16479 | -0.16937 | -0.086975 | -0.013733 | -0.11444 | -0.032043 | 61.2579 | -61.5005 | -61.6653 | 61.3312 | 61.2625 | 61.2122 | 0.004577 | -0.045777 | 61.1984 | -61.3861 | -61.6379 | 61.3541 | 61.3358 | 61.2534 | 0.13733 | 0.054932 | 0.073242 | -0.004578 | 0.15564 | 0.082398 | 0.16022 | 0.33417 | 61.4182 | 61.5326 | -61.6608 | -61.7203 | 61.2534 | 61.2808 | 61.2991 | 61.2717
2564.8906 | 123.0881 | -61.3632 | 61.5692 | -0.045166 | -0.0010105 | -0.010273 | 2.8922 | -0.00081171 | 0.00029044 | -0.0031125 | 0.04245 | 0.012061 | 0.0083122 | -0.002085 | -0.0095448 | 0.0031018 | -0.0012219 | 0.045776 | 0.11444 | -0.041199 | -0.009155 | 0.10071 | 0.009155 | 0.059509 | 0.045776 | 0.25635 | -0.050354 | 0.013733 | 0.10986 | 0.064087 | 0.11444 | 61.322 | -61.4548 | -61.5784 | 61.4639 | 61.4227 | 61.3724 | 0.10071 | 0.050354 | 61.3129 | -61.3129 | -61.5555 | 61.4731 | 61.4777 | 61.4273 | 0.16479 | 0.11444 | 0.14191 | 0.032044 | 0.16022 | 0.064087 | 0.15564 | 0.3067 | 61.4777 | 61.6196 | -61.6104 | -61.6196 | 61.3541 | 61.377 | 61.409 | 61.409
2565.8281 | 123.0743 | -61.377 | 61.5189 | -0.037537 | -0.0027195 | -0.0087777 | 2.8913 | 0.0060241 | -0.002273 | -0.00033547 | -0.094879 | 0.015266 | 0.0085258 | 0.0017602 | -0.011467 | 0.0039562 | -0.0033581 | -0.10071 | 0.018311 | -0.13275 | -0.17853 | -0.086975 | -0.1831 | -0.11902 | -0.37537 | 0.064087 | -0.24719 | -0.10529 | -0.018311 | -0.07782 | -0.041199 | 61.2442 | -61.5005 | -61.6974 | 61.29 | 61.2579 | 61.1938 | 0.013732 | -0.050354 | 61.1298 | -61.4548 | -61.6241 | 61.3586 | 61.3358 | 61.2991 | 0.20599 | 0.16937 | 0.045776 | -0.045777 | 0.22888 | 0.14191 | 0.15106 | 0.31128 | 61.3953 | 61.441 | -61.6516 | -61.7661 | 61.1984 | 61.2717 | 61.2762 | 61.0016
2566.8906 | 123.0835 | -61.3815 | 61.5463 | -0.007019 | -0.0029331 | -0.012196 | 2.892 | 0.0021789 | -0.0033412 | -0.0020443 | -0.06131 | 0.011848 | 0.008953 | 0.0011194 | -0.010186 | 0.0060924 | -0.0010083 | 0.009155 | 0.17853 | -0.050354 | -0.041199 | 0.054932 | 0.082397 | 0.46234 | -0.059509 | 0.31128 | -0.022888 | -0.013733 | 0.13275 | 0.032043 | 0.07782 | 61.3312 | -61.3678 | -61.5875 | 61.4365 | 61.8439 | 61.4639 | 0.5127 | 0.13275 | 61.3586 | -61.235 | -61.5601 | 61.5143 | 61.4594 | 61.4136 | 0.10071 | 0.054931 | 0.10529 | 0.009155 | 0.15564 | 0.009155 | 0.22888 | 0.33417 | 61.5601 | 61.6928 | -61.5967 | -61.5692 | 61.3403 | 61.3678 | 61.3907 | 61.322
2567.8281 | 123.0469 | -61.3998 | 61.5555 | -0.068054 | 0.0039029 | -0.0092051 | 2.8943 | 0.0019653 | -0.0014184 | 0.0020145 | -0.024689 | 0.012275 | 0.0087394 | -0.0022986 | -0.0089038 | 0.0048108 | 0.00027333 | -0.10071 | 0.027466 | -0.12817 | -0.16479 | -0.10071 | -0.19226 | -0.14191 | -0.19226 | 0.13275 | -0.18768 | -0.10071 | -0.041199 | -0.1236 | -0.045776 | 61.2717 | -61.528 | -61.7203 | 61.2991 | 61.2579 | 61.2076 | -0.013733 | -0.064087 | 61.2122 | -61.4227 | -61.6562 | 61.3586 | 61.3541 | 61.2762 | 0.14191 | 0.064087 | 0.027466 | -0.036621 | 0.14648 | 0.086975 | 0.15564 | 0.32043 | 61.4273 | 61.5326 | -61.6837 | -61.7432 | 61.235 | 61.2991 | 61.2991 | 61.2076
2568.8906 | 123.175 | -61.3174 | 61.528 | -0.029907 | -0.0025059 | -0.010059 | 2.8905 | -0.00017091 | -0.00013676 | -0.0031125 | 0.024139 | 0.012061 | 0.0061758 | -0.0033666 | -0.0097584 | 0.0024608 | 0.00091433 | 0.064087 | 0.073242 | -0.022888 | 0.41199 | -0.13275 | -0.32044 | 0.10529 | 0.1236 | 0.19684 | -0.068665 | 0.10529 | 0.22888 | 0.14191 | 0.16937 | 61.2946 | -61.4548 | -61.116 | 61.1847 | 61.4227 | 60.997 | 0.12817 | -0.29755 | 61.2488 | -61.3312 | -61.4227 | 61.5463 | 61.4868 | 61.4594 | 0.23804 | 0.21057 | -0.10986 | 0.43488 | 0.29755 | 0.17395 | 0.09613 | 0.2655 | 61.3907 | 61.5143 | -61.5509 | -61.5967 | 61.7294 | 61.4227 | 61.3815 | 61.441
2569.8281 | 123.1201 | -61.3861 | 61.5509 | -0.1062 | 0.00069854 | -0.0072825 | 2.8928 | 0.0032471 | 0.00050424 | -0.00097627 | -0.049103 | 0.011207 | 0.0085258 | -0.00037605 | -0.0091174 | 0.0058788 | 0.0036913 | -0.059509 | 0.054932 | -0.15564 | -0.16479 | -0.073242 | -0.1831 | -0.10986 | -0.11902 | 0.12817 | -0.18768 | -0.086975 | -0.018311 | -0.10986 | -0.009155 | 61.2305 | -61.496 | -61.7157 | 61.3129 | 61.2762 | 61.203 | 0.045777 | -0.027465 | 61.1984 | -61.4227 | -61.6379 | 61.3678 | 61.377 | 61.2762 | 0.17853 | 0.07782 | 0.082398 | -0.009155 | 0.16937 | 0.10071 | 0.21057 | 0.31586 | 61.441 | 61.5143 | -61.7065 | -61.7386 | 61.2213 | 61.2991 | 61.3266 | 61.2671
2570.8906 | 123.0881 | -61.3632 | 61.5509 | -0.090943 | 0.00027134 | -0.010914 | 2.8926 | 0.0019653 | -0.0029138 | -0.0018307 | -0.0002747 | 0.010352 | 0.0074576 | -0.0091344 | -0.0095448 | 0.0043836 | -0.0035719 | 0.009155 | 0.13733 | -0.068665 | -0.054932 | 0.041199 | -0.013733 | 0.022888 | -0.022888 | 0.2655 | -0.068665 | 0.032043 | 0.1236 | 0.013733 | 0.07782 | 61.2946 | -61.4136 | -61.6058 | 61.4044 | 61.3861 | 61.3495 | 0.091553 | 0.054932 | 61.2946 | -61.2854 | -61.5189 | 61.4868 | 61.441 | 61.377 | 0.14649 | 0.082398 | 0.10986 | 0.013733 | 0.19226 | 0.10071 | 0.20599 | 0.33417 | 61.5005 | 61.6287 | -61.6196 | -61.6196 | 61.3083 | 61.3953 | 61.3724 | 61.3403
2571.8281 | 123.2025 | -61.3541 | 61.5005 | -0.1062 | 0.0017667 | -0.0092051 | 2.8922 | 0.0030335 | -0.002273 | -0.0028989 | 0.036346 | 0.010779 | 0.0076712 | -0.0012304 | -0.0095448 | 0.0028882 | 0.0032641 | -0.07782 | -0.013733 | -0.13733 | -0.045776 | 0.022888 | -0.11902 | -0.036621 | -0.013733 | 0.068665 | -0.19684 | 0 | 0.064087 | -0.022888 | 0.068665 | 61.2167 | -61.5143 | -61.5463 | 61.377 | 61.3174 | 61.235 | 0.10071 | 0.01831 | 61.1572 | -61.4319 | -61.5005 | 61.4182 | 61.4227 | 61.3312 | 0.2655 | 0.17395 | 0.16022 | 0.091553 | 0.26093 | 0.19684 | 0.1236 | 0.2655 | 61.3403 | 61.4227 | -61.6379 | -61.6974 | 61.3083 | 61.3541 | 61.2762 | 61.3403
2572.8906 | 123.111 | -61.3586 | 61.5463 | -0.11383 | -0.0022923 | -0.0077097 | 2.8933 | 0.0030335 | 7.6842e-05 | 0.00073273 | -0.033844 | 0.012488 | 0.0095938 | -0.001444 | -0.0095448 | 0.0063062 | -0.0014355 | -0.018311 | 0.082397 | -0.086975 | -0.068665 | 0.086975 | -0.059509 | -0.018311 | -0.009155 | 0.20142 | -0.10986 | -0.009155 | 0.064087 | -0.032043 | 0.059509 | 61.2717 | -61.4639 | -61.615 | 61.4456 | 61.3403 | 61.2991 | 0.068664 | 0.027466 | 61.2488 | -61.3449 | -61.5555 | 61.4227 | 61.4182 | 61.3266 | 0.16937 | 0.07782 | 0.17395 | 0.01831 | 0.17395 | 0.10071 | 0.16937 | 0.31128 | 61.441 | 61.5601 | -61.6333 | -61.6562 | 61.29 | 61.3495 | 61.3403 | 61.3495
2573.8281 | 123.1979 | -61.3495 | 61.5143 | -0.14435 | -0.00015586 | -0.0089913 | 2.8911 | 0.0015381 | -0.0035548 | -0.0056759 | 0.0088807 | 0.010566 | 0.0074576 | -0.0059302 | -0.010613 | 0.0022472 | -0.0033581 | -0.082397 | -0.050354 | -0.15564 | -0.073242 | 0.041199 | -0.073242 | -0.018311 | -0.013733 | 0.041199 | -0.17395 | -0.009155 | 0.059509 | -0.027466 | 0.054932 | 61.1938 | -61.5646 | -61.5875 | 61.3907 | 61.3312 | 61.2762 | 0.13733 | 0.082398 | 61.1755 | -61.4731 | -61.5234 | 61.409 | 61.4044 | 61.322 | 0.22888 | 0.14648 | 0.19684 | 0.082398 | 0.23346 | 0.16479 | 0.10529 | 0.21515 | 61.2991 | 61.3907 | -61.6699 | -61.6882 | 61.2762 | 61.3403 | 61.2671 | 61.3358
2574.8906 | 123.0927 | -61.3815 | 61.5509 | -0.1062 | -0.0010105 | -0.0064279 | 2.8935 | 0.0019653 | -0.0029138 | 9.193e-05 | -0.030792 | 0.013129 | 0.0053214 | -0.0087072 | -0.0086902 | 0.0037426 | -0.0029309 | -0.059509 | 0.073242 | -0.11444 | -0.11902 | -0.050354 | -0.15564 | -0.09613 | -0.14648 | 0.16479 | -0.15564 | -0.091553 | -0.050354 | -0.11902 | -0.036621 | 61.2671 | -61.4777 | -61.6699 | 61.3312 | 61.2854 | 61.2259 | 0.018311 | -0.041199 | 61.2259 | -61.3861 | -61.6425 | 61.3312 | 61.3449 | 61.2625 | 0.11902 | 0.036621 | 0.064087 | -0.004578 | 0.10529 | 0.064087 | 0.18768 | 0.32044 | 61.4548 | 61.5463 | -61.6653 | -61.7065 | 61.2625 | 61.29 | 61.322 | 61.235
2575.8281 | 123.1934 | -61.3586 | 61.5051 | -0.11383 | 0.0011257 | -0.0087777 | 2.892 | -0.0012391 | 7.6842e-05 | -0.0052487 | 0.033295 | 0.011634 | 0.005535 | -0.0078528 | -0.010399 | 0.0028882 | -0.0016493 | -0.050354 | -0.032043 | -0.12817 | -0.07782 | 0.045776 | -0.073242 | -0.036621 | -0.013733 | 0.059509 | -0.16022 | 0.068665 | 0.013733 | 0.086975 | 0.14648 | 61.2305 | -61.5372 | -61.5829 | 61.4044 | 61.322 | 61.2854 | 0.091553 | 0.054932 | 61.1984 | -61.4456 | -61.4365 | 61.3724 | 61.5051 | 61.4456 | 0.3067 | 0.24719 | 0.17395 | 0.050354 | 0.17395 | 0.22888 | 0.096131 | 0.21973 | 61.3266 | 61.4182 | -61.6333 | -61.6653 | 61.2808 | 61.4273 | 61.3083 | 61.3449
2576.8906 | 123.0835 | -61.3724 | 61.5738 | -0.052796 | -0.0022923 | -0.010487 | 2.893 | 4.2692e-05 | -0.0018458 | -0.0046079 | 0.057709 | 0.012275 | 0.0063896 | -0.0057166 | -0.009972 | 0.0031018 | -0.00058107 | 0.036621 | 0.10529 | -0.018311 | 0.004578 | 0.10529 | 0.009155 | 0.073242 | 0.050354 | 0.23346 | -0.064087 | -0.018311 | 0.1831 | 0.16479 | 0.15564 | 61.3541 | -61.4685 | -61.5692 | 61.4777 | 61.4456 | 61.3815 | 0.091553 | 0.027466 | 61.3083 | -61.3403 | -61.5921 | 61.5555 | 61.528 | 61.5372 | 0.21973 | 0.22888 | 0.1236 | 0.022889 | 0.24719 | 0.045776 | 0.1236 | 0.29755 | 61.4777 | 61.6058 | -61.5921 | -61.6379 | 61.377 | 61.3541 | 61.409 | 61.4227
2577.8281 | 123.1338 | -61.3312 | 61.5189 | -0.1062 | -0.0016513 | -0.0081369 | 2.8956 | 0.00046989 | -0.00099116 | -0.0011899 | 0.04245 | 0.011848 | 0.0070304 | -0.0097754 | -0.0095448 | 0.0037426 | 0.0013415 | -0.050354 | -0.009155 | -0.10529 | -0.073242 | 0.064087 | -0.082397 | -0.041199 | -0.032043 | 0.073242 | -0.16937 | -0.018311 | 0.036621 | -0.027466 | 0.045776 | 61.2259 | -61.528 | -61.5921 | 61.3953 | 61.29 | 61.2488 | 0.064087 | 0.022889 | 61.1618 | -61.4456 | -61.5372 | 61.3678 | 61.377 | 61.3037 | 0.21515 | 0.14191 | 0.16937 | 0.032044 | 0.20599 | 0.15106 | 0.096131 | 0.24261 | 61.322 | 61.4044 | -61.6241 | -61.6882 | 61.2579 | 61.3129 | 61.2808 | 61.2991
2578.8906 | 123.1384 | -61.3678 | 61.5692 | -0.014649 | -0.0022923 | -0.0096323 | 2.8935 | 0.0021789 | -0.002273 | -0.0056759 | -0.039948 | 0.011848 | 0.0076712 | 0.0011194 | -0.0097584 | 0.0024608 | -0.0022901 | 0.013733 | 0.10986 | -0.073242 | -0.032043 | 0.068665 | -0.045776 | 0 | 0.009155 | 0.21057 | -0.11444 | 0.022888 | 0.086975 | 0.022888 | 0.082397 | 61.2946 | -61.4594 | -61.6013 | 61.4365 | 61.3678 | 61.322 | 0.073242 | 0.027466 | 61.2534 | -61.3586 | -61.5463 | 61.4548 | 61.4502 | 61.3907 | 0.19684 | 0.13733 | 0.14191 | 0.041199 | 0.20142 | 0.13733 | 0.18311 | 0.32501 | 61.4777 | 61.5784 | -61.6425 | -61.6837 | 61.3358 | 61.3907 | 61.3815 | 61.377
2579.8281 | 123.1613 | -61.3449 | 61.5326 | -0.068054 | -0.0022923 | -0.0085641 | 2.8935 | -0.0014527 | -0.0020594 | -0.0035397 | 0.054657 | 0.012061 | 0.0070304 | -0.003153 | -0.0095448 | 0.0033154 | 0.0026233 | -0.064087 | 0 | -0.1236 | -0.086975 | 0.027466 | -0.091553 | -0.018311 | -0.050354 | 0.09613 | -0.15564 | -0.004578 | 0.068665 | -0.022888 | 0.068665 | 61.2213 | -61.5326 | -61.6196 | 61.3724 | 61.3266 | 61.2534 | 0.10528 | 0.032043 | 61.1893 | -61.4365 | -61.5372 | 61.4136 | 61.4136 | 61.322 | 0.22431 | 0.13275 | 0.15106 | 0.036621 | 0.22431 | 0.15106 | 0.1236 | 0.25177 | 61.3449 | 61.441 | -61.6562 | -61.6882 | 61.2579 | 61.3403 | 61.2808 | 61.2946
2580.8906 | 123.0789 | -61.3724 | 61.5555 | -0.060425 | 0.00069854 | -0.0072825 | 2.8933 | 0.0023925 | -0.0018458 | -0.00097627 | -0.033844 | 0.012488 | 0.005535 | -0.003794 | -0.010186 | 0.0050244 | 0.00027333 | -0.10986 | 0.045776 | -0.16022 | -0.17395 | -0.10071 | -0.20599 | -0.11902 | -0.15106 | 0.13275 | -0.21057 | -0.20142 | 0.054932 | 0.041199 | 0.022888 | 61.2122 | -61.5097 | -61.7294 | 61.2717 | 61.2534 | 61.1664 | 0.041198 | -0.045777 | 61.1618 | -61.4227 | -61.7569 | 61.4273 | 61.3953 | 61.4136 | 0.23346 | 0.25177 | 0.059509 | -0.013733 | 0.2655 | 0.009155 | 0.20599 | 0.34332 | 61.4182 | 61.5051 | -61.7157 | -61.7661 | 61.1984 | 61.171 | 61.2625 | 61.2213
2581.8281 | 123.1522 | -61.3632 | 61.5234 | -0.068054 | -0.0022923 | -0.0087777 | 2.8918 | -0.0010253 | -0.0018458 | -0.00054907 | 0.06076 | 0.009925 | 0.005535 | -0.0033666 | -0.009972 | 0.0033154 | -0.0031445 | -0.068665 | 0 | -0.11902 | -0.07782 | 0.027466 | -0.082397 | -0.018311 | -0.050354 | 0.10986 | -0.15106 | 0 | 0.082397 | 0 | 0.064087 | 61.2442 | -61.5234 | -61.6013 | 61.3907 | 61.3449 | 61.2808 | 0.10071 | 0.036622 | 61.2122 | -61.4136 | -61.5234 | 61.4456 | 61.4273 | 61.3632 | 0.21515 | 0.15106 | 0.14649 | 0.041199 | 0.23346 | 0.15106 | 0.11902 | 0.26093 | 61.3632 | 61.4731 | -61.6425 | -61.6745 | 61.2854 | 61.3632 | 61.2946 | 61.3129
2582.8906 | 123.1018 | -61.3678 | 61.5646 | 0.015869 | -0.0016513 | -0.011555 | 2.8939 | 0.0036743 | -0.0020594 | -0.0020443 | 0.011932 | 0.012275 | 0.0061758 | 0.0038966 | -0.0097584 | 0.0033154 | 0.00048713 | -0.009155 | 0.16479 | -0.022888 | -0.041199 | 0.054932 | -0.027466 | 0.032043 | 0 | 0.27008 | -0.045776 | 0.073242 | 0.036621 | -0.07782 | 0.064087 | 61.3449 | -61.3998 | -61.6058 | 61.4227 | 61.3998 | 61.3403 | 0.054931 | -0.004578 | 61.322 | -61.2946 | -61.4914 | 61.4044 | 61.4319 | 61.29 | 0.10986 | -0.032044 | 0.07782 | -0.018311 | 0.082397 | 0.11902 | 0.18768 | 0.31586 | 61.5326 | 61.6379 | -61.5875 | -61.6104 | 61.3266 | 61.441 | 61.3586 | 61.3678
2583.8281 | 123.1979 | -61.3632 | 61.5372 | -0.068054 | -0.0020785 | -0.0077097 | 2.8928 | -0.0010253 | -0.0027002 | -0.0041807 | 0.063812 | 0.011634 | 0.007244 | -0.0022986 | -0.008263 | 0.0039562 | 0.0011279 | -0.045776 | 0.059509 | -0.086975 | -0.036621 | 0.054932 | -0.036621 | 0.022888 | 0 | 0.14648 | -0.11902 | 0.050354 | 0.14648 | 0.068665 | 0.14648 | 61.2762 | -61.4777 | -61.5738 | 61.4182 | 61.3861 | 61.3266 | 0.10986 | 0.050354 | 61.2442 | -61.3907 | -61.4868 | 61.5097 | 61.5097 | 61.4319 | 0.2655 | 0.18768 | 0.14191 | 0.050354 | 0.2655 | 0.16937 | 0.14648 | 0.2655 | 61.4227 | 61.5097 | -61.6241 | -61.6562 | 61.3266 | 61.4136 | 61.3174 | 61.3632
2584.8906 | 123.0743 | -61.3632 | 61.5601 | -0.068054 | -0.0012241 | -0.0085641 | 2.8943 | 0.00089729 | -0.00077756 | -0.00076267 | -0.07962 | 0.014197 | 0.0083122 | 0.001333 | -0.010826 | 0.008015 | 0.0011279 | -0.11902 | 0.027466 | -0.14191 | -0.15564 | -0.07782 | -0.21057 | -0.12817 | -0.15564 | 0.13733 | -0.19226 | -0.5722 | 0.064087 | 0.35248 | 0.15106 | 61.2213 | -61.5326 | -61.7157 | 61.2854 | 61.235 | 61.1526 | 0.013733 | -0.068664 | 61.171 | -61.4227 | -62.1323 | 61.4273 | 61.5143 | 61.7157 | 0.34332 | 0.54474 | 0.064087 | -0.013733 | 0.25635 | -0.37994 | 0.16937 | 0.32959 | 61.3907 | 61.5005 | -61.702 | -61.7523 | 61.2076 | 60.791 | 61.2442 | 61.2076
2585.8281 | 123.1888 | -61.3403 | 61.5234 | -0.098572 | -0.0018649 | -0.010059 | 2.8922 | -0.0023071 | -0.002273 | -0.0022581 | -0.024689 | 0.012061 | 0.0076712 | -0.0033666 | -0.0074084 | 0.0031018 | 0.0030505 | -0.041199 | 0.041199 | -0.091553 | -0.064087 | 0.050354 | 0.1236 | 0.20599 | -0.032043 | 0.16937 | -0.09613 | 0.013733 | 0.091553 | 0.022888 | 0.091553 | 61.2488 | -61.4822 | -61.5875 | 61.3907 | 61.5463 | 61.4639 | 0.29755 | 0.21515 | 61.2442 | -61.3541 | -61.5097 | 61.4319 | 61.4319 | 61.3632 | 0.18768 | 0.11902 | 0.14191 | 0.027466 | 0.18768 | 0.10986 | 0.13275 | 0.2655 | 61.3815 | 61.5097 | -61.615 | -61.6196 | 61.2762 | 61.3541 | 61.2991 | 61.3083
2586.8281 | 123.1476 | -61.3907 | 61.5372 | -0.098572 | -0.00079686 | -0.0085641 | 2.892 | 0.00046989 | 0.00029044 | -0.0022581 | 0.030243 | 0.014197 | 0.0076712 | -0.0093482 | -0.010399 | 0.0048108 | 0.00027333 | -0.073242 | 0.018311 | -0.10529 | -0.068665 | 0.032043 | -0.091553 | -0.009155 | -0.027466 | 0.11902 | -0.15564 | -0.013733 | 0.068665 | -0.009155 | 0.073242 | 61.2854 | -61.5189 | -61.6058 | 61.4227 | 61.3815 | 61.2991 | 0.096131 | 0.013733 | 61.235 | -61.4182 | -61.5509 | 61.4594 | 61.4639 | 61.3815 | 0.22888 | 0.14649 | 0.13733 | 0.036621 | 0.22431 | 0.14191 | 0.1236 | 0.27466 | 61.409 | 61.5097 | -61.6425 | -61.6928 | 61.322 | 61.377 | 61.3174 | 61.3632
2587.8906 | 123.0835 | -61.377 | 61.5555 | -0.045166 | -0.0016513 | -0.0096323 | 2.8937 | 0.0038879 | -0.002273 | -0.0024717 | -0.076569 | 0.011848 | 0.0074576 | 5.1352e-05 | -0.012108 | 0.0041698 | -0.00079467 | -0.032043 | 0.059509 | -0.09613 | -0.091553 | -0.022888 | -0.11902 | -0.059509 | -0.068665 | 0.16479 | -0.14648 | -0.050354 | 0.004578 | -0.082397 | 0.013733 | 61.2808 | -61.496 | -61.647 | 61.3541 | 61.3174 | 61.2579 | 0.036621 | -0.022889 | 61.2305 | -61.3907 | -61.6058 | 61.3815 | 61.3907 | 61.2946 | 0.16022 | 0.064087 | 0.073242 | 0.004577 | 0.15106 | 0.09613 | 0.15564 | 0.31128 | 61.4365 | 61.5417 | -61.6516 | -61.702 | 61.2854 | 61.3266 | 61.3449 | 61.3083
2588.8281 | 123.143 | -61.3586 | 61.5326 | -0.090943 | -0.0016513 | -0.0094187 | 2.8922 | -0.00017091 | 0.0013586 | -0.0041807 | 0.036346 | 0.012916 | 0.0068168 | -0.006571 | -0.0084766 | 0.0041698 | -0.0010083 | -0.054932 | 0.009155 | -0.09613 | -0.07782 | 0.022888 | -0.082397 | -0.013733 | -0.054932 | 0.1236 | -0.1236 | -0.004578 | 0.091553 | 0.022888 | 0.045776 | 61.2625 | -61.5234 | -61.6104 | 61.3815 | 61.3449 | 61.2762 | 0.082397 | 0.013733 | 61.235 | -61.409 | -61.5372 | 61.4502 | 61.4044 | 61.3815 | 0.16937 | 0.14648 | 0.11902 | 0.01831 | 0.21515 | 0.11902 | 0.10528 | 0.24719 | 61.3678 | 61.4822 | -61.6287 | -61.6562 | 61.2808 | 61.3541 | 61.3037 | 61.3037
2589.8906 | 123.2162 | -61.3449 | 61.5051 | -0.11383 | -0.0016513 | -0.0096323 | 2.8943 | 0.0013245 | -0.0012048 | -0.00076267 | -0.042999 | 0.0097114 | 0.0068168 | -0.0072118 | -0.009972 | 0.0041698 | -0.0012219 | -0.10986 | 0 | -0.14191 | -0.10986 | -0.032043 | -0.15564 | -0.064087 | -0.041199 | 0.082397 | -0.17853 | -0.013733 | 0.059509 | -0.032043 | 0.045776 | 61.203 | -61.5051 | -61.615 | 61.3129 | 61.2808 | 61.1893 | 0.07782 | -0.013733 | 61.1664 | -61.4227 | -61.5189 | 61.4044 | 61.3907 | 61.3129 | 0.2243 | 0.14648 | 0.10986 | 0.032044 | 0.23804 | 0.16479 | 0.14191 | 0.26092 | 61.3449 | 61.4273 | -61.647 | -61.6837 | 61.235 | 61.3312 | 61.235 | 61.3037
2590.8281 | 123.1705 | -61.3358 | 61.5189 | -0.075684 | -0.00036966 | -0.0083505 | 2.8939 | -0.0014527 | -0.0012048 | -0.0037533 | 0.063812 | 0.012702 | 0.0085258 | -0.0059302 | -0.008263 | 0.003529 | -0.00036747 | -0.054932 | 0.032043 | -0.10529 | -0.064087 | 0.027466 | -0.068665 | 0.009155 | 0.20142 | 0.15106 | -0.10986 | 0.018311 | 0.10529 | 0.018311 | 0.082397 | 61.2305 | -61.4868 | -61.5829 | 61.3632 | 61.3449 | 61.2671 | 0.11444 | 0.036621 | 61.2259 | -61.3678 | -61.5005 | 61.441 | 61.4182 | 61.3541 | 0.19226 | 0.12817 | 0.13275 | 0.041199 | 0.21515 | 0.12817 | 0.13733 | 0.26093 | 61.3678 | 61.4868 | -61.6241 | -61.6287 | 61.2717 | 61.3541 | 61.2808 | 61.5372
2591.8906 | 123.2254 | -61.3403 | 61.5143 | -0.037537 | -0.0010105 | -0.0068551 | 2.8937 | 0.0017517 | 7.6842e-05 | -0.0014035 | -0.030792 | 0.01142 | 0.0048942 | 0.0011194 | -0.01104 | 0.0041698 | -0.0020765 | -0.086975 | -0.027466 | -0.15106 | -0.10529 | 0.022888 | -0.10529 | -0.059509 | -0.032043 | 0.07782 | -0.1831 | -0.004578 | 0.073242 | -0.027466 | 0.059509 | 61.1893 | -61.5417 | -61.6196 | 61.3632 | 61.2808 | 61.235 | 0.091553 | 0.045776 | 61.1572 | -61.4365 | -61.5189 | 61.4136 | 61.3998 | 61.3129 | 0.24261 | 0.15564 | 0.17395 | 0.045776 | 0.25635 | 0.17853 | 0.1236 | 0.26092 | 61.3129 | 61.4182 | -61.6653 | -61.6974 | 61.235 | 61.3358 | 61.2534 | 61.3083
2592.8281 | 123.2162 | -61.3403 | 61.528 | -0.029907 | 5.7742e-05 | -0.0074961 | 2.893 | -0.00017091 | -0.00013676 | -0.0028989 | 0.045502 | 0.011634 | 0.0063896 | -0.00828 | -0.009331 | 0.003529 | -0.0020765 | -0.009155 | 0.050354 | -0.064087 | -0.009155 | 0.11444 | 0.004578 | 0.068665 | 0.059509 | 0.15106 | -0.09613 | 0.091553 | 0.19226 | 0.10986 | 0.13733 | 61.2762 | -61.4777 | -61.5372 | 61.4548 | 61.409 | 61.3449 | 0.13275 | 0.068665 | 61.2442 | -61.377 | -61.4365 | 61.5326 | 61.4777 | 61.4502 | 0.23346 | 0.20599 | 0.17853 | 0.054932 | 0.28839 | 0.18768 | 0.11444 | 0.24719 | 61.3907 | 61.4914 | -61.5921 | -61.6241 | 61.3312 | 61.4319 | 61.3312 | 61.3998
2593.8906 | 123.1064 | -61.3724 | 61.5646 | -0.037537 | -0.0010105 | -0.0072825 | 2.8939 | -0.00059811 | -0.0012048 | -0.0020443 | -0.073517 | 0.012702 | 0.0087394 | -0.003153 | -0.0084766 | 0.0050244 | -0.0031445 | -0.032043 | 0.068665 | -0.086975 | -0.09613 | 0 | -0.12817 | -0.082397 | -0.068665 | 0.16022 | -0.13275 | -0.059509 | 0.018311 | -0.073242 | 0.009155 | 61.2854 | -61.496 | -61.6608 | 61.3724 | 61.29 | 61.2442 | 0.004578 | -0.041199 | 61.2396 | -61.4044 | -61.6241 | 61.3907 | 61.3815 | 61.2991 | 0.14191 | 0.059509 | 0.086975 | -0.009155 | 0.15106 | 0.073242 | 0.15564 | 0.29297 | 61.441 | 61.5326 | -61.6516 | -61.6974 | 61.2762 | 61.3129 | 61.3403 | 61.3037
2594.8281 | 123.2025 | -61.3403 | 61.5326 | -0.029907 | 0.00048494 | -0.0064279 | 2.8947 | -0.00081171 | -0.00056396 | -0.0024717 | 0.054657 | 0.012916 | 0.0061758 | -0.0033666 | -0.009972 | 0.0041698 | 0.0013415 | -0.036621 | 0.045776 | -0.09613 | -0.050354 | 0.068665 | -0.036621 | 0.018311 | 0 | 0.13733 | -0.13275 | 0.054932 | 0.15564 | 0.082397 | 0.13275 | 61.2442 | -61.4868 | -61.5829 | 61.409 | 61.3586 | 61.3037 | 0.11444 | 0.059509 | 61.2076 | -61.3953 | -61.4777 | 61.496 | 61.4731 | 61.4227 | 0.2655 | 0.21515 | 0.16479 | 0.045776 | 0.28839 | 0.18768 | 0.14191 | 0.27008 | 61.3861 | 61.4777 | -61.6287 | -61.6653 | 61.29 | 61.3953 | 61.3037 | 61.3403
2595.8906 | 123.2346 | -61.3266 | 61.528 | -0.090943 | 0.00027134 | -0.0070687 | 2.8943 | 0.0021789 | 7.6842e-05 | -0.00097627 | -0.024689 | 0.011848 | 0.0068168 | -0.0027258 | -0.0095448 | 0.0058788 | -0.0031445 | -0.045776 | -0.032043 | -0.13275 | -0.050354 | 0.054932 | -0.086975 | -0.027466 | 0.07782 | 0.059509 | -0.17853 | 0 | 0.20142 | 0 | 0.059509 | 61.1938 | -61.5601 | -61.5784 | 61.3815 | 61.2991 | 61.2396 | 0.10529 | 0.045776 | 61.1481 | -61.4685 | -61.528 | 61.528 | 61.3861 | 61.3266 | 0.23804 | 0.17853 | 0.18768 | 0.082397 | 0.37994 | 0.17853 | 0.10071 | 0.23804 | 61.2946 | 61.3861 | -61.6608 | -61.7065 | 61.2762 | 61.3266 | 61.2808 | 61.4044
2596.8281 | 123.1338 | -61.3541 | 61.5738 | -0.029907 | -0.0014377 | -0.0096323 | 2.8926 | -0.0018799 | -0.0016322 | -0.0014035 | -0.027741 | 0.013557 | 0.0063896 | 0.001333 | -0.009972 | 0.0039562 | -0.0018629 | 0.027466 | 0.15106 | -0.036621 | -0.022888 | 0.059509 | -0.013733 | 0.018311 | 0.018311 | 0.24261 | -0.073242 | 0.022888 | 0.1236 | 0.032043 | 0.09613 | 61.3174 | -61.4227 | -61.5967 | 61.4136 | 61.3724 | 61.3403 | 0.054932 | 0.022888 | 61.2808 | -61.3312 | -61.5509 | 61.4777 | 61.4502 | 61.3861 | 0.16937 | 0.10529 | 0.09613 | 0.013733 | 0.19684 | 0.09613 | 0.18768 | 0.31586 | 61.5051 | 61.5967 | -61.6104 | -61.647 | 61.3312 | 61.377 | 61.3815 | 61.3724
2597.8906 | 123.2071 | -61.3632 | 61.5097 | -0.1062 | -0.00058326 | -0.0072825 | 2.8945 | 0.0017517 | -0.0016322 | 0.00094633 | 0.045502 | 0.010566 | 0.007244 | -0.0027258 | -0.011254 | 0.005238 | -0.00036747 | -0.045776 | -0.032043 | -0.14191 | -0.29755 | 0.32959 | 0.11444 | -0.054932 | -0.009155 | 0.054932 | -0.16022 | 0.009155 | 0.07782 | -0.004578 | 0.068665 | 61.2213 | -61.5417 | -61.8073 | 61.6928 | 61.3083 | 61.4777 | 0.086975 | 0.25635 | 61.203 | -61.4548 | -61.5005 | 61.441 | 61.4319 | 61.3586 | 0.22888 | 0.15564 | 0.4715 | -0.15564 | 0.23804 | 0.16937 | 0.10986 | 0.21515 | 61.3312 | 61.4182 | -61.6516 | -61.6699 | 61.0657 | 61.3724 | 61.3174 | 61.3541
2598.8281 | 123.2117 | -61.3037 | 61.5234 | -0.014649 | -0.0012241 | -0.0085641 | 2.8939 | -0.00038451 | -0.0014184 | -0.0020443 | 0.039398 | 0.011634 | 0.0074576 | -0.0035802 | -0.008263 | 0.0020336 | -0.0042127 | 0.073242 | 0.054932 | -0.059509 | 0.073242 | 0.20142 | 0.073242 | 0.1236 | 0.15564 | 0.17395 | -0.045776 | 0.11902 | 0.21973 | 0.13275 | 0.17395 | 61.2442 | -61.4685 | -61.4502 | 61.5051 | 61.4273 | 61.377 | 0.1831 | 0.13275 | 61.2579 | -61.3495 | -61.4044 | 61.5234 | 61.4777 | 61.4365 | 0.21973 | 0.17853 | 0.26093 | 0.13275 | 0.2655 | 0.16479 | 0.11444 | 0.21973 | 61.3586 | 61.4777 | -61.5829 | -61.5692 | 61.377 | 61.4227 | 61.377 | 61.4594
2599.8906 | 123.2529 | -61.3541 | 61.5463 | -0.068054 | -0.00036966 | -0.010059 | 2.8926 | -0.00059811 | -0.0020594 | -0.0018307 | 0.030243 | 0.012702 | 0.0070304 | -0.0080664 | -0.0089038 | 0.0043836 | 0.0019823 | -0.068665 | 0.018311 | -0.10986 | -0.073242 | 0.018311 | -0.064087 | -0.027466 | -0.018311 | 0.14191 | -0.14191 | 0.009155 | 0.09613 | -0.022888 | 0.050354 | 61.2442 | -61.528 | -61.6196 | 61.3724 | 61.3266 | 61.29 | 0.082397 | 0.045776 | 61.2122 | -61.4044 | -61.5372 | 61.4502 | 61.4044 | 61.3312 | 0.19226 | 0.11902 | 0.12817 | 0.036621 | 0.23804 | 0.15106 | 0.12817 | 0.28381 | 61.3724 | 61.496 | -61.6562 | -61.6882 | 61.2808 | 61.3632 | 61.2854 | 61.3358
2600.8281 | 123.1842 | -61.3312 | 61.5509 | -0.12909 | 0.0011257 | -0.0074961 | 2.8922 | -0.0046569 | -0.0016322 | -0.0016171 | 0.021088 | 0.0094976 | 0.011303 | -0.0027258 | -0.011254 | 0.0054516 | -0.0039991 | 0.07782 | 0.091553 | -0.054932 | 0.059509 | 0.17395 | 0.050354 | 0.07782 | 0.11444 | 0.19684 | -0.059509 | 0.09613 | 0.19684 | 0.12817 | 0.17853 | 61.2762 | -61.4594 | -61.4914 | 61.5051 | 61.409 | 61.3815 | 0.13275 | 0.10529 | 61.2717 | -61.3541 | -61.4548 | 61.528 | 61.5097 | 61.4594 | 0.23804 | 0.18768 | 0.22888 | 0.11444 | 0.25635 | 0.15564 | 0.14649 | 0.25635 | 61.4227 | 61.528 | -61.6058 | -61.6104 | 61.3907 | 61.4273 | 61.409 | 61.4456
2601.9062 | 123.1659 | -61.3541 | 61.5921 | 0.00824 | 0.0011257 | -0.010487 | 2.8939 | -0.00017091 | -0.0020594 | -0.0037533 | -0.027741 | 0.012916 | 0.010021 | -0.0025122 | -0.010826 | 0.0060924 | -0.0048535 | 0.022888 | 0.14648 | -0.054932 | -0.009155 | 0.059509 | -0.018311 | 0.041199 | 0.027466 | 0.22888 | -0.068665 | 0.041199 | 0.11444 | 0.036621 | 0.07782 | 61.2991 | -61.4456 | -61.6013 | 61.4136 | 61.3953 | 61.3358 | 0.096131 | 0.036621 | 61.2854 | -61.3632 | -61.5509 | 61.4685 | 61.4319 | 61.3907 | 0.14649 | 0.10529 | 0.11444 | 0.045777 | 0.18311 | 0.10986 | 0.20142 | 0.29755 | 61.5005 | 61.5829 | -61.647 | -61.6608 | 61.3449 | 61.3953 | 61.377 | 61.3815
2602.8281 | 123.1842 | -61.377 | 61.5601 | -0.052796 | -0.00015586 | -0.0096323 | 2.8915 | -0.0040161 | -0.0035548 | -0.0016171 | 0.039398 | 0.010352 | 0.0076712 | -0.010203 | -0.0078358 | 0.0031018 | -0.0018629 | 0.050354 | 0.073242 | -0.054932 | 0.059509 | 0.14648 | 0.050354 | 0.086975 | 0.10986 | 0.21057 | -0.041199 | 0.068665 | 0.19684 | 0.10529 | 0.13733 | 61.322 | -61.4868 | -61.5006 | 61.5234 | 61.4639 | 61.4273 | 0.14191 | 0.10529 | 61.3358 | -61.3495 | -61.4914 | 61.5738 | 61.5143 | 61.4822 | 0.17853 | 0.14649 | 0.20142 | 0.11444 | 0.23804 | 0.10986 | 0.12817 | 0.25177 | 61.4502 | 61.5875 | -61.615 | -61.6013 | 61.4365 | 61.4456 | 61.4273 | 61.4868
2603.8906 | 123.2391 | -61.3358 | 61.528 | -0.075684 | 0.0015529 | -0.0068551 | 2.8926 | 0.00025629 | -0.00013676 | -0.0014035 | -0.0002747 | 0.0097114 | 0.0057486 | 0.0017602 | -0.0097584 | 0.0056652 | 0.0013415 | -0.045776 | -0.027466 | -0.1236 | -0.036621 | 0.032043 | -0.10529 | -0.027466 | 0.022888 | 0.041199 | -0.19684 | 0.073242 | 0.1831 | 0.013733 | 0.07782 | 61.2122 | -61.5555 | -61.5646 | 61.3678 | 61.3083 | 61.2305 | 0.09613 | 0.01831 | 61.1389 | -61.4868 | -61.4548 | 61.5189 | 61.4136 | 61.3495 | 0.27466 | 0.21057 | 0.15564 | 0.086975 | 0.37994 | 0.27008 | 0.09613 | 0.23804 | 61.3083 | 61.377 | -61.6516 | -61.7249 | 61.2991 | 61.409 | 61.29 | 61.3586
2604.8281 | 123.1384 | -61.3586 | 61.5784 | -0.075684 | -0.0010105 | -0.0096323 | 2.8935 | 0.0011109 | -0.0016322 | -0.0033261 | 0.014984 | 0.010779 | 0.0078848 | -0.003794 | -0.0089038 | 0.0050244 | -0.00036747 | 0.054932 | 0.091553 | -0.041199 | 0.027466 | 0.1236 | 0.054932 | 0.07782 | 0.10529 | 0.24261 | -0.054932 | 0.064087 | 0.17395 | 0.07782 | 0.15564 | 61.3174 | -61.4868 | -61.5509 | 61.4822 | 61.4365 | 61.4136 | 0.11902 | 0.096131 | 61.3037 | -61.3358 | -61.5143 | 61.5326 | 61.5143 | 61.4365 | 0.21057 | 0.13275 | 0.16479 | 0.068665 | 0.22888 | 0.11902 | 0.13275 | 0.29755 | 61.4502 | 61.6013 | -61.6196 | -61.6333 | 61.3861 | 61.4227 | 61.4136 | 61.4639
2605.8906 | 123.2346 | -61.3632 | 61.5143 | -0.068054 | -0.0031467 | -0.0081369 | 2.8943 | 0.0049561 | -0.0018458 | -0.0014035 | 0.036346 | 0.01142 | 0.0053214 | -0.0016576 | -0.0084766 | 0.0056652 | -0.0014355 | -0.041199 | -0.027466 | -0.10529 | -0.050354 | -0.068665 | -0.55847 | -0.064087 | 0.004578 | 0.032043 | -0.1831 | -0.013733 | 0.07782 | -0.018311 | 0.059509 | 61.2579 | -61.5417 | -61.5646 | 61.2946 | 61.2991 | 60.8047 | 0.041199 | -0.45319 | 61.1801 | -61.4822 | -61.528 | 61.441 | 61.4227 | 61.3449 | 0.24261 | 0.16479 | 0.036621 | 0.054932 | 0.26092 | 0.16937 | 0.07782 | 0.21515 | 61.3358 | 61.3953 | -61.6196 | -61.6974 | 61.3129 | 61.3495 | 61.322 | 61.3678
2606.8438 | 123.1018 | -61.377 | 61.528 | -0.014649 | -0.00058326 | -0.0089913 | 2.8947 | 0.00068369 | -0.0033412 | -0.0031125 | -0.046051 | 0.016334 | 0.0063896 | -0.0010168 | -0.010399 | 0.0065198 | -0.0029309 | -0.10529 | 0.045776 | -0.13733 | -0.16937 | -0.086975 | -0.17853 | -0.11444 | -0.53101 | 0.064087 | -0.24719 | -0.091553 | -0.036621 | -0.068665 | -0.013733 | 61.2396 | -61.4822 | -61.6974 | 61.29 | 61.2625 | 61.1984 | 0.022888 | -0.041199 | 61.1298 | -61.4639 | -61.6196 | 61.3403 | 61.3632 | 61.3083 | 0.23346 | 0.17853 | 0.050354 | -0.032044 | 0.21057 | 0.15564 | 0.18311 | 0.31128 | 61.4227 | 61.441 | -61.6653 | -61.7752 | 61.2076 | 61.2854 | 61.2717 | 60.8459
2607.8906 | 123.2483 | -61.3403 | 61.5372 | -0.037537 | -0.0018649 | -0.0089913 | 2.8896 | -0.0018799 | -0.0016322 | -0.0018307 | 0.063812 | 0.012488 | 0.0076712 | -0.0091344 | -0.010186 | 0.0028882 | -0.0048535 | 0.009155 | 0.068665 | -0.050354 | 0.009155 | 0.15106 | 0.027466 | 0.086975 | 0.11444 | 0.16937 | -0.068665 | 0.11444 | 0.21973 | 0.14648 | 0.19226 | 61.29 | -61.4685 | -61.528 | 61.4914 | 61.4273 | 61.3678 | 0.13733 | 0.07782 | 61.2717 | -61.3678 | -61.4227 | 61.5601 | 61.5326 | 61.4868 | 0.26093 | 0.21515 | 0.20142 | 0.059509 | 0.28839 | 0.18311 | 0.11902 | 0.23804 | 61.409 | 61.5097 | -61.5875 | -61.6058 | 61.3495 | 61.4548 | 61.3495 | 61.4548
2608.8281 | 122.9965 | -61.3632 | 61.5738 | 0.031128 | -0.0016513 | -0.0092051 | 2.893 | 4.2692e-05 | -0.0024866 | -0.0018307 | -0.0094299 | 0.011207 | 0.0068168 | -0.0040076 | -0.0076222 | 0.0048108 | -0.0016493 | -0.004578 | 0.16479 | -0.036621 | -0.032043 | 0.068665 | -0.027466 | 0.032043 | 0.004578 | 0.26093 | -0.054932 | 0.013733 | 0.16479 | 0.56305 | 0.39825 | 61.3266 | -61.409 | -61.6058 | 61.4319 | 61.3953 | 61.3358 | 0.068664 | 0.009155 | 61.3083 | -61.3129 | -61.5601 | 61.528 | 61.7615 | 61.9263 | 0.45319 | 0.61798 | 0.10529 | 0.004578 | 0.21973 | 0.068665 | 0.20142 | 0.31586 | 61.528 | 61.6241 | -61.6104 | -61.6287 | 61.3312 | 61.377 | 61.3586 | 61.3678
2609.8906 | 123.2529 | -61.3586 | 61.5601 | -0.060425 | -0.00015586 | -0.0092051 | 2.8935 | 0.00046989 | 0.00050424 | -0.0020443 | 0.039398 | 0.013343 | 0.0063896 | 0.0034692 | -0.0086902 | 0.00182 | -0.0016493 | 0.045776 | 0.082397 | -0.032043 | 0.059509 | 0.1831 | 0.082397 | 0.091553 | 0.14191 | 0.1831 | -0.027466 | 0.20142 | 0.1236 | -0.018311 | 0.12817 | 61.3266 | -61.4777 | -61.5006 | 61.5417 | 61.4502 | 61.441 | 0.1236 | 0.11444 | 61.3312 | -61.377 | -61.3586 | 61.4822 | 61.4868 | 61.3403 | 0.15564 | 0.009155 | 0.21515 | 0.091552 | 0.15106 | 0.22888 | 0.11444 | 0.21057 | 61.441 | 61.5417 | -61.5921 | -61.5875 | 61.4182 | 61.5601 | 61.4044 | 61.5006
2610.8281 | 123.1338 | -61.4136 | 61.5921 | 0.00061049 | -0.00015586 | -0.010059 | 2.8945 | 0.00025629 | -0.002273 | -0.0022581 | -0.027741 | 0.012061 | 0.0070304 | 0.00069215 | -0.0095448 | 0.0078014 | -0.0039991 | 0.018311 | 0.16022 | -0.032043 | -0.045776 | 0.050354 | -0.013733 | 0.027466 | 0.009155 | 0.24719 | -0.059509 | -0.16022 | 0.21515 | -0.064087 | -0.045776 | 61.3815 | -61.4319 | -61.6379 | 61.4639 | 61.441 | 61.3998 | 0.059509 | 0.01831 | 61.3541 | -61.3449 | -61.7523 | 61.6287 | 61.3678 | 61.3495 | 0.013733 | -0.004578 | 0.082397 | -0.013733 | 0.27466 | -0.10071 | 0.19226 | 0.3067 | 61.5738 | 61.6608 | -61.6241 | -61.6516 | 61.3678 | 61.2534 | 61.4319 | 61.4227
2611.8906 | 123.1888 | -61.3632 | 61.5234 | -0.090943 | -0.0010105 | -0.0085641 | 2.8922 | -0.0029479 | -0.0029138 | -0.0052487 | 0.030243 | 0.011207 | 0.0066032 | -0.0091344 | -0.009331 | 0.0067334 | -0.0016493 | -0.022888 | 0.045776 | -0.068665 | -0.004578 | 0.09613 | -0.004578 | 0.032043 | 0.027466 | 0.16479 | -0.086975 | 0.068665 | 0.16937 | 0.086975 | 0.14191 | 61.2946 | -61.4777 | -61.528 | 61.4594 | 61.3953 | 61.3586 | 0.10071 | 0.064087 | 61.2762 | -61.3586 | -61.4548 | 61.5326 | 61.5051 | 61.4502 | 0.22888 | 0.17395 | 0.16479 | 0.064087 | 0.25635 | 0.15564 | 0.11444 | 0.25177 | 61.409 | 61.528 | -61.5921 | -61.6104 | 61.3586 | 61.4319 | 61.3403 | 61.3907
2612.8281 | 123.1293 | -61.3861 | 61.5646 | 0.00824 | -0.0012241 | -0.010059 | 2.8915 | -0.00017091 | -0.0033412 | -0.0018307 | -0.015534 | 0.012061 | 0.0070304 | 5.1352e-05 | -0.009331 | 0.0028882 | -0.0014355 | 0.013733 | 0.16022 | -0.027466 | -0.032043 | 0.050354 | -0.013733 | 0.050354 | 0.009155 | 0.26093 | -0.050354 | 0.022888 | 0.10529 | 0.018311 | 0.09613 | 61.3586 | -61.4044 | -61.5967 | 61.4365 | 61.4365 | 61.3724 | 0.07782 | 0.013733 | 61.3358 | -61.3037 | -61.5417 | 61.4914 | 61.4822 | 61.4044 | 0.14648 | 0.068665 | 0.07782 | -0.004577 | 0.15564 | 0.073242 | 0.18768 | 0.31128 | 61.5463 | 61.647 | -61.5921 | -61.615 | 61.3541 | 61.409 | 61.3998 | 61.3953

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.4021 | 20.6617 | 20.0607 | 20.2051
0.5979 | 20.6657 | 20.0577 | 20.2078
1.5979 | 20.6511 | 20.0653 | 20.2084
2.5979 | 20.6747 | 20.0653 | 20.2063
3.5979 | 20.9894 | 20.069 | 20.2015
4.5979 | 22.0463 | 20.0762 | 20.2016
5.5979 | 23.8932 | 20.0863 | 20.215
6.5979 | 26.4844 | 20.0923 | 20.2198
7.5979 | 29.6147 | 20.1419 | 20.2347
8.5979 | 33.2105 | 20.1734 | 20.2589
9.5979 | 37.1817 | 20.2283 | 20.2811
10.5979 | 41.4752 | 20.2935 | 20.3155
11.5979 | 45.9787 | 20.3587 | 20.3557
12.5979 | 50.6856 | 20.4328 | 20.4052
13.5979 | 55.6048 | 20.5395 | 20.4661
14.5979 | 60.6447 | 20.6571 | 20.54
15.5979 | 65.7994 | 20.7914 | 20.6175
16.5979 | 71.0856 | 20.949 | 20.7262
17.5979 | 76.5494 | 21.1015 | 20.8305
18.5979 | 82.1316 | 21.269 | 20.9728
19.5979 | 87.7064 | 21.4696 | 21.1189
20.5979 | 93.3652 | 21.6947 | 21.2702
21.5979 | 99.1423 | 21.9525 | 21.4464
22.5979 | 105.0046 | 22.2569 | 21.6275
23.5979 | 110.907 | 22.5614 | 21.8305
24.5979 | 116.8376 | 22.8791 | 22.0559
25.5979 | 122.7875 | 23.2107 | 22.2963
26.5979 | 128.7418 | 23.5452 | 22.5717
27.5979 | 134.6876 | 23.9137 | 22.8612
28.5979 | 140.6454 | 24.3058 | 23.1676
29.5979 | 146.6373 | 24.7225 | 23.4766
30.5979 | 152.6287 | 25.1466 | 23.8246
31.5979 | 158.5632 | 25.6367 | 24.1799
32.5979 | 164.5321 | 26.141 | 24.5658
33.5979 | 170.5075 | 26.6814 | 24.9826
34.5979 | 176.4547 | 27.2256 | 25.4086
35.5979 | 182.3527 | 27.8143 | 25.8577
36.5979 | 188.1519 | 28.4189 | 26.3323
37.5979 | 194.0864 | 29.0375 | 26.8212
38.5979 | 199.9765 | 29.7155 | 27.3225
39.5979 | 205.8016 | 30.3738 | 27.8532
40.5979 | 211.6389 | 31.0505 | 28.4144
41.5979 | 217.5464 | 31.7545 | 29.0006
42.5979 | 223.4198 | 32.4806 | 29.6188
43.5979 | 229.3789 | 33.2633 | 30.2645
44.5979 | 235.417 | 34.0895 | 30.9344
45.5979 | 241.2308 | 34.9206 | 31.619
46.5979 | 246.9659 | 35.769 | 32.3349
47.5979 | 252.8418 | 36.623 | 33.066
48.5979 | 258.6408 | 37.5178 | 33.8146
49.5979 | 264.3768 | 38.4451 | 34.5907
50.5979 | 269.9596 | 39.3839 | 35.3986
51.5979 | 275.5824 | 40.3484 | 36.2408
52.5979 | 281.2621 | 41.3517 | 37.1049
53.5979 | 286.8876 | 42.3782 | 38.0058
54.5979 | 292.3901 | 43.4633 | 38.9426
55.5979 | 298.0075 | 44.6166 | 39.9027
56.5979 | 303.539 | 45.8429 | 40.8861
57.5979 | 308.8934 | 47.099 | 41.891
58.5979 | 314.1259 | 48.3566 | 42.9429
59.5979 | 319.3897 | 49.6299 | 44.0332
60.5979 | 324.2246 | 50.9304 | 45.1847
61.5979 | 328.5588 | 52.2895 | 46.3452
62.5979 | 332.5357 | 53.6049 | 47.5019
63.5979 | 336.3677 | 54.9162 | 48.675
64.5979 | 339.9615 | 56.2343 | 49.8411
65.5979 | 343.1927 | 57.5222 | 51.0136
66.5979 | 346.1754 | 58.7733 | 52.2019
67.5979 | 349.1957 | 60.0611 | 53.3926
68.5979 | 351.5871 | 61.3104 | 54.587
69.5979 | 353.8785 | 62.5444 | 55.7862
70.5979 | 356.0559 | 63.7571 | 56.9816
71.5979 | 357.7834 | 64.9797 | 58.1713
72.5979 | 359.1826 | 66.1641 | 59.3484
73.5979 | 360.5911 | 67.3052 | 60.496
74.5979 | 361.8255 | 68.4265 | 61.6497
75.5979 | 362.8051 | 69.5451 | 62.792
76.5979 | 363.53 | 70.6312 | 63.9114
77.5979 | 363.8191 | 71.6823 | 65.0037
78.5979 | 364.1506 | 72.6973 | 66.0752
79.5979 | 364.4164 | 73.7097 | 67.1385
80.5979 | 364.4889 | 74.7111 | 68.1949
81.5979 | 364.5069 | 75.6749 | 69.2281
82.5979 | 364.3672 | 76.6338 | 70.2409
83.5979 | 364.1492 | 77.569 | 71.2794
84.5979 | 363.9344 | 78.4589 | 72.2778
85.5979 | 363.7239 | 79.3271 | 73.2526
86.5979 | 363.5561 | 80.1971 | 74.2222
87.5979 | 363.2997 | 81.035 | 75.1445
88.5979 | 362.7548 | 81.868 | 76.0759
89.5979 | 362.2665 | 82.6838 | 76.966
90.5979 | 361.9178 | 83.4933 | 77.8581
91.5979 | 361.4886 | 84.2819 | 78.7252
92.5979 | 360.9999 | 85.0609 | 79.563
93.5979 | 360.5582 | 85.8333 | 80.4122
94.5979 | 360.0856 | 86.6052 | 81.2327
95.5979 | 359.8152 | 87.4138 | 82.06
96.5979 | 359.5792 | 88.1885 | 82.8746
97.5979 | 359.2577 | 88.9114 | 83.6826
98.5979 | 358.8551 | 89.6762 | 84.4595
99.5979 | 358.3128 | 90.422 | 85.2318
100.5979 | 358.0741 | 91.1603 | 86.0123
101.5979 | 357.8651 | 91.8909 | 86.7689
102.5979 | 357.6048 | 92.6402 | 87.5297
103.5979 | 357.1273 | 93.3851 | 88.2832
104.5979 | 356.8011 | 94.0943 | 89.0261
105.5979 | 356.683 | 94.8019 | 89.7629
106.5979 | 356.5222 | 95.5335 | 90.5071
107.5979 | 356.2773 | 96.2522 | 91.2621
108.5979 | 356.2106 | 96.9714 | 92.0036
109.5979 | 356.0975 | 97.6896 | 92.755
110.5979 | 356.1868 | 98.4043 | 93.4989
111.5979 | 356.3804 | 99.1583 | 94.2512
112.5979 | 356.569 | 99.9137 | 95.0214
113.5979 | 356.7047 | 100.6417 | 95.7805
114.5979 | 356.8781 | 101.3492 | 96.5096
115.5979 | 357.0629 | 102.0481 | 97.2519
116.5979 | 357.3212 | 102.7437 | 97.9691
117.5979 | 357.522 | 103.4573 | 98.6675
118.5979 | 357.6638 | 104.2179 | 99.3982
119.5979 | 357.7813 | 104.972 | 100.1322
120.5979 | 357.6935 | 105.738 | 100.8528
121.5979 | 357.7874 | 106.4445 | 101.567
122.5979 | 357.8951 | 107.118 | 102.2789
123.5979 | 358.1182 | 107.804 | 102.9625
124.5979 | 358.2666 | 108.4791 | 103.6478
125.5979 | 358.2944 | 109.1775 | 104.3322
126.5979 | 358.3246 | 109.9413 | 105.0145
127.5979 | 358.4898 | 110.6798 | 105.7088
128.5979 | 358.5733 | 111.3868 | 106.3991
129.5979 | 358.6316 | 112.066 | 107.0741
130.5979 | 358.7592 | 112.7117 | 107.7592
131.5979 | 358.9507 | 113.3726 | 108.4533
132.5979 | 358.9135 | 114.0293 | 109.1277
133.5979 | 359.059 | 114.683 | 109.8126
134.5979 | 359.1711 | 115.385 | 110.5275
135.5979 | 359.1261 | 116.118 | 111.2941
136.5979 | 359.0589 | 116.8142 | 112.0567
137.5979 | 359.1332 | 117.4868 | 112.7881
138.5979 | 359.3002 | 118.1546 | 113.4959
139.5979 | 359.3627 | 118.8497 | 114.1836
140.5979 | 359.3065 | 119.5815 | 114.8631
141.5979 | 359.3239 | 120.2988 | 115.5552
142.5979 | 359.5739 | 120.9949 | 116.2206
143.5979 | 359.706 | 121.6409 | 116.8663
144.5979 | 359.9311 | 122.3017 | 117.5071
145.5979 | 360.044 | 122.9284 | 118.1477
146.5979 | 360.0507 | 123.5623 | 118.793
147.5979 | 360.1109 | 124.1994 | 119.4297
148.5979 | 360.1747 | 124.8271 | 120.0656
149.5979 | 360.165 | 125.484 | 120.7215
150.5979 | 360.3346 | 126.1919 | 121.3871
151.5979 | 360.4756 | 126.8772 | 122.0523
152.5979 | 360.5583 | 127.5508 | 122.6921
153.5979 | 360.373 | 128.2232 | 123.3452
154.5979 | 360.3504 | 128.9137 | 123.9978
155.5979 | 360.3759 | 129.5973 | 124.6463
156.5979 | 360.3495 | 130.2702 | 125.3101
157.5979 | 360.3171 | 130.9795 | 125.9814
158.5979 | 360.2163 | 131.6451 | 126.6433
159.5979 | 360.184 | 132.3201 | 127.3034
160.5979 | 360.1063 | 132.9984 | 127.9768
161.5979 | 360.1234 | 133.7236 | 128.6583
162.5979 | 360.0376 | 134.4357 | 129.3655
163.5979 | 359.8991 | 135.1338 | 130.083
164.5979 | 359.9879 | 135.8337 | 130.8
165.5979 | 360.1551 | 136.5547 | 131.5112
166.5979 | 360.1609 | 137.2808 | 132.2048
167.5979 | 360.0122 | 137.9891 | 132.9075
168.5979 | 360.0081 | 138.5785 | 133.5934
169.5979 | 359.9554 | 139.1751 | 134.2413
170.5979 | 359.9107 | 139.7507 | 134.877
171.5979 | 360.0507 | 140.3414 | 135.4867
172.5979 | 360.1753 | 140.939 | 136.1024
173.5979 | 360.1222 | 141.5683 | 136.7153
174.5979 | 360.1251 | 142.1847 | 137.3208
175.5979 | 359.8367 | 142.761 | 137.921
176.5979 | 359.5985 | 143.3604 | 138.499
177.5979 | 359.4684 | 144.0049 | 139.0953
178.5979 | 359.3032 | 144.5597 | 139.6764
179.5979 | 359.0259 | 145.1216 | 140.2451
180.5979 | 358.9072 | 145.6846 | 140.8045
181.5979 | 358.7764 | 146.3448 | 141.3559
182.5979 | 358.6494 | 146.9824 | 141.9274
183.5979 | 358.6294 | 147.5854 | 142.4927
184.5979 | 358.6545 | 148.127 | 143.0531
185.5979 | 358.5629 | 148.6855 | 143.5997
186.5979 | 358.4405 | 149.2623 | 144.128
187.5979 | 358.3257 | 149.8448 | 144.6795
188.5979 | 358.2897 | 150.3796 | 145.2181
189.5979 | 358.3556 | 150.9606 | 145.7449
190.5979 | 358.5157 | 151.5447 | 146.2777
191.5979 | 358.5215 | 152.1317 | 146.817
192.5979 | 358.6607 | 152.7114 | 147.3714
193.5979 | 358.8726 | 153.327 | 147.9111
194.5979 | 358.8591 | 153.9324 | 148.4878
195.5979 | 358.8342 | 154.5518 | 149.0618
196.5979 | 358.8057 | 155.1614 | 149.6436
197.5979 | 358.6753 | 155.7582 | 150.25
198.5979 | 358.5776 | 156.3323 | 150.8226
199.5979 | 358.4507 | 156.9214 | 151.3677
200.5979 | 358.5013 | 157.4541 | 151.9206
201.5979 | 358.4797 | 157.9601 | 152.4703
202.5979 | 358.4529 | 158.5121 | 152.9992
203.5979 | 358.5933 | 159.0765 | 153.5315
204.5979 | 358.6699 | 159.7005 | 154.059
205.5979 | 358.7243 | 160.342 | 154.6163
206.5979 | 358.8779 | 160.8921 | 155.1728
207.5979 | 358.8939 | 161.4518 | 155.7288
208.5979 | 358.7312 | 161.85 | 156.2914
209.5979 | 358.6788 | 162.3018 | 156.8455
210.5979 | 358.6431 | 162.8457 | 157.3857
211.5979 | 358.6611 | 163.4256 | 157.9607
212.5979 | 358.6715 | 164.0436 | 158.5378
213.5979 | 358.8257 | 164.6512 | 159.1148
214.5979 | 358.9492 | 165.2698 | 159.7019
215.5979 | 359.0888 | 165.8697 | 160.2719
216.5979 | 359.1008 | 166.4029 | 160.8079
217.5979 | 359.1339 | 166.9545 | 161.3224
218.5979 | 359.2703 | 167.4765 | 161.8315
219.5979 | 359.2285 | 167.992 | 162.3317
220.5979 | 359.2124 | 168.3706 | 162.843
221.5979 | 359.1384 | 168.7679 | 163.3621
222.5979 | 359.1272 | 169.3023 | 163.8702
223.5979 | 359.1739 | 169.881 | 164.4086
224.5979 | 359.2799 | 170.4721 | 164.9611
225.5979 | 359.3809 | 171.0598 | 165.5112
226.5979 | 359.3947 | 171.6481 | 166.0689
227.5979 | 359.4121 | 172.2505 | 166.6404
228.5979 | 359.3775 | 172.8764 | 167.2136
229.5979 | 359.2905 | 173.4087 | 167.7869
230.5979 | 359.2141 | 173.8857 | 168.3509
231.5979 | 359.1352 | 174.425 | 168.9195
232.5979 | 359.0431 | 174.9841 | 169.5014
233.5979 | 358.9136 | 175.5327 | 170.0599
234.5979 | 358.931 | 176.0668 | 170.6134
235.5979 | 359.072 | 176.5438 | 171.1485
236.5979 | 358.8988 | 177.0242 | 171.6562
237.5979 | 358.8189 | 177.5116 | 172.1559
238.5979 | 358.6839 | 177.9518 | 172.6593
239.5979 | 358.5886 | 178.381 | 173.1596
240.5979 | 358.5226 | 178.7642 | 173.6582
241.5979 | 358.4948 | 179.2482 | 174.159
242.5979 | 358.5227 | 179.8162 | 174.6668
243.5979 | 358.6503 | 180.3859 | 175.1791
244.5979 | 358.6493 | 180.9764 | 175.6808
245.5979 | 358.6287 | 181.5215 | 176.1585
246.5979 | 358.6789 | 182.0443 | 176.6634
247.5979 | 358.5893 | 182.457 | 177.154
248.5979 | 358.4375 | 182.924 | 177.607
249.5979 | 358.357 | 183.4402 | 178.0749
250.5979 | 358.2698 | 184.0145 | 178.5744
251.5979 | 358.2285 | 184.5891 | 179.1183
252.5979 | 358.1589 | 185.1485 | 179.6497
253.5979 | 358.1336 | 185.6855 | 180.1616
254.5979 | 358.0593 | 186.221 | 180.656
255.5979 | 358.082 | 186.7716 | 181.1792
256.5979 | 358.049 | 187.2805 | 181.7031
257.5979 | 357.9653 | 187.7698 | 182.2241
258.5979 | 357.9484 | 188.1755 | 182.738
259.5979 | 357.9418 | 188.66 | 183.2222
260.5979 | 357.8807 | 189.1701 | 183.688
261.5979 | 357.7836 | 189.6998 | 184.1519
262.5979 | 357.6063 | 190.2016 | 184.6302
263.5979 | 357.5557 | 190.6922 | 185.1044
264.5979 | 357.5639 | 191.1102 | 185.5738
265.5979 | 357.4481 | 191.5883 | 186.048
266.5979 | 357.3791 | 192.0498 | 186.5201
267.5979 | 357.3758 | 192.3776 | 186.9815
268.5979 | 357.3279 | 192.8209 | 187.4309
269.5979 | 357.3074 | 193.2771 | 187.8877
270.5979 | 357.3655 | 193.7407 | 188.3303
271.5979 | 357.4556 | 194.1966 | 188.7672
272.5979 | 357.5234 | 194.6435 | 189.2015
273.5979 | 357.4331 | 195.128 | 189.6267
274.5979 | 357.4759 | 195.5947 | 190.065
275.5979 | 357.3608 | 196.0711 | 190.52
276.5979 | 357.3488 | 196.5536 | 190.9516
277.5979 | 357.3117 | 196.9816 | 191.3677
278.5979 | 357.2345 | 197.4612 | 191.7739
279.5979 | 357.247 | 197.9376 | 192.1826
280.5979 | 357.1523 | 198.3929 | 192.615
281.5979 | 357.2089 | 198.8521 | 193.0633
282.5979 | 357.3974 | 199.3141 | 193.508
283.5979 | 357.4819 | 199.7558 | 193.9641
284.5979 | 357.5053 | 200.2625 | 194.4027
285.5979 | 357.4951 | 200.7347 | 194.8166
286.5979 | 357.4834 | 201.193 | 195.2206
287.5979 | 357.4398 | 201.6221 | 195.6184
288.5979 | 357.4253 | 202.1106 | 196.0499
289.5979 | 357.3969 | 202.5756 | 196.4676
290.5979 | 357.5127 | 203.0267 | 196.8709
291.5979 | 357.444 | 203.4295 | 197.2387
292.5979 | 357.318 | 203.836 | 197.6065
293.5979 | 357.4134 | 204.2666 | 197.9908
294.5979 | 357.4757 | 204.7131 | 198.3898
295.5979 | 357.4214 | 205.1557 | 198.8193
296.5979 | 357.4552 | 205.573 | 199.2324
297.5979 | 357.5212 | 205.9289 | 199.6428
298.5979 | 357.5857 | 206.2927 | 200.0347
299.5979 | 357.5337 | 206.7086 | 200.417
300.5979 | 357.41 | 207.0722 | 200.8119
301.5979 | 357.416 | 207.4498 | 201.2154
302.5979 | 357.3579 | 207.8499 | 201.613
303.5979 | 357.3306 | 208.2711 | 202.0058
304.5979 | 357.2741 | 208.659 | 202.3772
305.5979 | 357.302 | 208.9537 | 202.6972
306.5979 | 357.4035 | 209.0844 | 203.0146
307.5979 | 357.3766 | 209.3705 | 203.3371
308.5979 | 357.3234 | 209.541 | 203.6884
309.5979 | 357.2726 | 209.8523 | 204.0613
310.5979 | 357.4388 | 210.2244 | 204.4587
311.5979 | 357.6818 | 210.6461 | 204.8579
312.5979 | 357.8752 | 211.0472 | 205.2526
313.5979 | 358.0331 | 211.4291 | 205.6553
314.5979 | 358.2164 | 211.8507 | 206.0554
315.5979 | 358.3108 | 212.3055 | 206.4503
316.5979 | 358.4421 | 212.7144 | 206.8358
317.5979 | 358.4938 | 213.0514 | 207.2123
318.5979 | 358.6161 | 213.4368 | 207.5912
319.5979 | 358.6657 | 213.8537 | 207.9583
320.5979 | 358.6459 | 214.105 | 208.305
321.5979 | 358.557 | 214.3909 | 208.6501
322.5979 | 358.5116 | 214.5477 | 208.9986
323.5979 | 358.4299 | 214.8118 | 209.3335
324.5979 | 358.4079 | 215.1673 | 209.6513
325.5979 | 358.2971 | 215.5832 | 209.9725
326.5979 | 358.2612 | 216.0082 | 210.2957
327.5979 | 358.1533 | 216.3805 | 210.6393
328.5979 | 358.045 | 216.7626 | 210.9971
329.5979 | 358.0533 | 217.0857 | 211.3743
330.5979 | 358.1204 | 217.3951 | 211.7444
331.5979 | 358.0031 | 217.7276 | 212.1285
332.5979 | 357.9963 | 217.928 | 212.517
333.6135 | 358.0095 | 218.2725 | 212.8846
334.5979 | 357.9491 | 218.6773 | 213.229
335.5979 | 357.9831 | 219.1318 | 213.5732
336.5979 | 358.0806 | 219.4145 | 213.9063
337.5979 | 358.1211 | 219.6504 | 214.2558
338.5979 | 358.0282 | 220.041 | 214.5904
339.5979 | 357.9964 | 220.3952 | 214.9438
340.6292 | 357.9189 | 220.7999 | 215.2929
341.5979 | 357.8984 | 221.1123 | 215.6315
342.5979 | 357.8647 | 221.4042 | 215.9674
343.5979 | 357.8701 | 221.7563 | 216.2797
344.5979 | 357.847 | 222.1183 | 216.6199
345.5979 | 357.9269 | 222.3819 | 216.9433
346.5979 | 357.8582 | 222.7297 | 217.2685
347.5979 | 357.6327 | 223.1143 | 217.583
348.5979 | 357.5272 | 223.5278 | 217.8892
349.5979 | 357.4127 | 223.9278 | 218.2133
350.5979 | 357.2689 | 224.3172 | 218.5338
351.5979 | 357.3112 | 224.625 | 218.857
352.5979 | 357.3648 | 225.0013 | 219.1714
353.5979 | 357.4401 | 225.3322 | 219.4557
354.5979 | 357.5784 | 225.5968 | 219.7579
355.5979 | 357.6342 | 225.9377 | 220.0423
356.5979 | 357.5948 | 226.2723 | 220.3088
357.5979 | 357.6771 | 226.6426 | 220.5705
358.5979 | 357.7631 | 226.8544 | 220.8442
359.5979 | 357.746 | 226.9532 | 221.1189
360.5979 | 357.7303 | 227.0514 | 221.3662
361.5979 | 357.8808 | 227.1299 | 221.5989
362.5979 | 357.8536 | 227.2868 | 221.8188
363.6135 | 357.7969 | 227.6145 | 222.0506
364.5979 | 357.7371 | 227.9246 | 222.2848
365.5979 | 357.7032 | 228.163 | 222.5213
366.5979 | 357.7274 | 228.3579 | 222.7794
367.5979 | 357.819 | 228.6888 | 223.0617
368.5979 | 357.8342 | 229.0047 | 223.3223
369.5979 | 357.8641 | 229.4019 | 223.5603
370.5979 | 357.7866 | 229.7917 | 223.7979
371.5979 | 357.6736 | 230.1812 | 224.0489
372.5979 | 357.6866 | 230.5533 | 224.3495
373.5979 | 357.7288 | 230.83 | 224.6613
374.5979 | 357.8578 | 231.1298 | 224.9691
375.5979 | 357.9505 | 231.4185 | 225.2663
376.5979 | 357.8853 | 231.6278 | 225.5564
377.5979 | 357.8841 | 231.9534 | 225.853
378.5979 | 357.8838 | 232.2811 | 226.161
379.5979 | 357.7623 | 232.6223 | 226.4512
380.5979 | 357.6947 | 232.934 | 226.74
381.5979 | 357.7021 | 233.165 | 227.0067
382.5979 | 357.7121 | 233.4567 | 227.2711
383.5979 | 357.6742 | 233.7826 | 227.535
384.5979 | 357.4886 | 234.1189 | 227.8255
385.5979 | 357.3681 | 234.4404 | 228.1276
386.5979 | 357.273 | 234.6718 | 228.4389
387.5979 | 357.2528 | 234.7261 | 228.7245
388.5979 | 357.2089 | 234.9527 | 228.99
389.5979 | 357.1921 | 235.2574 | 229.2273
390.5979 | 357.2158 | 235.5886 | 229.4616
391.5979 | 357.2626 | 235.9202 | 229.7309
392.5979 | 357.3589 | 236.1968 | 230.0015
393.5979 | 357.4538 | 236.4837 | 230.2811
394.5979 | 357.5834 | 236.7976 | 230.557
395.5979 | 357.6698 | 237.1684 | 230.8266
396.5979 | 357.7064 | 237.4588 | 231.0864
397.5979 | 357.7475 | 237.7655 | 231.3633
398.5979 | 357.7112 | 238.0537 | 231.6452
399.5979 | 357.6928 | 238.3454 | 231.9331
400.5979 | 357.603 | 238.6184 | 232.2168
401.5979 | 357.6189 | 238.8841 | 232.4988
402.5979 | 357.6512 | 239.1377 | 232.7798
403.5979 | 357.5818 | 239.3049 | 233.0527
404.5979 | 357.5869 | 239.4715 | 233.3183
405.5979 | 357.4437 | 239.6285 | 233.5605
406.5979 | 357.2874 | 239.748 | 233.7941
407.5979 | 357.1959 | 239.978 | 234.0556
408.5979 | 357.1707 | 240.1318 | 234.3106
409.5979 | 357.1295 | 240.3721 | 234.5728
410.5979 | 357.0279 | 240.5851 | 234.8337
411.5979 | 357.0592 | 240.8485 | 235.09
412.5979 | 357.1579 | 241.0611 | 235.3477
413.5979 | 357.1349 | 241.1964 | 235.6089
414.5979 | 357.1861 | 241.2057 | 235.8412
415.5979 | 357.0135 | 241.3911 | 236.0565
416.5979 | 356.8373 | 241.6145 | 236.2802
417.5979 | 356.6085 | 241.8367 | 236.5011
418.5979 | 356.6179 | 241.9546 | 236.7225
419.5979 | 356.7536 | 242.1433 | 236.9392
420.5979 | 356.8178 | 242.2438 | 237.1753
421.5979 | 356.8052 | 242.468 | 237.4009
422.5979 | 356.8444 | 242.7515 | 237.6132
423.5979 | 356.7116 | 242.9551 | 237.8375
424.5979 | 356.7194 | 243.1615 | 238.0566
425.5979 | 356.8857 | 243.4157 | 238.2904
426.5979 | 356.9769 | 243.5526 | 238.5164
427.5979 | 356.9695 | 243.8195 | 238.745
428.5979 | 356.9356 | 243.9356 | 238.9707
429.5979 | 356.883 | 244.1874 | 239.1977
430.5979 | 356.8412 | 244.497 | 239.4297
431.5979 | 356.8966 | 244.7564 | 239.6685
432.5979 | 356.8963 | 244.9318 | 239.9222
433.5979 | 356.9331 | 245.0898 | 240.1513
434.5979 | 356.9023 | 245.2418 | 240.3816
435.5979 | 356.9041 | 245.483 | 240.6037
436.5979 | 356.8069 | 245.6961 | 240.8307
437.5979 | 356.7893 | 245.9363 | 241.0716
438.5979 | 356.7915 | 246.1637 | 241.3028
439.5979 | 356.7113 | 246.4481 | 241.5092
440.5979 | 356.6411 | 246.7803 | 241.7176
441.5979 | 356.5529 | 247.0945 | 241.9256
442.5979 | 356.5629 | 247.3528 | 242.1516
443.5979 | 356.4866 | 247.6067 | 242.3662
444.5979 | 356.5274 | 247.7953 | 242.5831
445.5979 | 356.5523 | 247.8822 | 242.7897
446.5979 | 356.4237 | 248.0391 | 242.9815
447.5979 | 356.3905 | 248.2601 | 243.1715
448.5979 | 356.4446 | 248.4482 | 243.3747
449.5979 | 356.4608 | 248.7007 | 243.5685
450.5979 | 356.4314 | 248.9062 | 243.7805
451.5979 | 356.3913 | 249.1278 | 243.9549
452.5979 | 356.3487 | 249.2568 | 244.1333
453.5979 | 356.2863 | 249.3757 | 244.3089
454.5979 | 356.2963 | 249.6417 | 244.4901
455.5979 | 356.3064 | 249.8295 | 244.6855
456.5979 | 356.3016 | 250.0495 | 244.8794
457.5979 | 356.328 | 250.1727 | 245.0779
458.5979 | 356.3138 | 250.3591 | 245.2672
459.5979 | 356.2686 | 250.5818 | 245.4571
460.5979 | 356.2058 | 250.7685 | 245.6501
461.5979 | 356.1378 | 250.9497 | 245.8433
462.5979 | 356.163 | 251.0954 | 246.0409
463.5979 | 356.2629 | 251.3183 | 246.2371
464.5979 | 356.3033 | 251.5888 | 246.4328
465.5979 | 356.2047 | 251.8118 | 246.6444
466.5979 | 356.0732 | 252.0433 | 246.8367
467.5979 | 356.1628 | 252.2427 | 247.0319
468.5979 | 356.0326 | 252.3177 | 247.2068
469.5979 | 355.9478 | 252.4154 | 247.379
470.5979 | 355.9061 | 252.5271 | 247.5546
471.5979 | 355.9777 | 252.4936 | 247.7218
472.5979 | 355.9976 | 252.5737 | 247.9145
473.5979 | 355.9584 | 252.7227 | 248.0854
474.5979 | 356.0713 | 252.9183 | 248.2476
475.5979 | 356.098 | 253.1519 | 248.4113
476.5979 | 356.0712 | 253.3924 | 248.5934
477.5979 | 356.0885 | 253.6396 | 248.7733
478.5979 | 356.1806 | 253.8126 | 248.9491
479.5979 | 356.2727 | 254.0278 | 249.1267
480.5979 | 356.3881 | 254.2681 | 249.3063
481.5979 | 356.4653 | 254.4618 | 249.4772
482.5979 | 356.5142 | 254.6307 | 249.6514
483.5979 | 356.5075 | 254.7153 | 249.8129
484.5979 | 356.4985 | 254.7777 | 249.9627
485.5979 | 356.5939 | 254.8138 | 250.1159
486.5979 | 356.5711 | 254.952 | 250.2701
487.5979 | 356.4277 | 255.0331 | 250.4236
488.5979 | 356.5345 | 255.2116 | 250.5882
489.5979 | 356.4938 | 255.4367 | 250.7472
490.5979 | 356.3506 | 255.6997 | 250.9115
491.5979 | 356.3095 | 255.9407 | 251.0614
492.5979 | 356.3333 | 255.9802 | 251.2079
493.5979 | 356.2799 | 256.0295 | 251.3443
494.5979 | 356.1862 | 256.1342 | 251.4825
495.5979 | 356.2332 | 256.3506 | 251.6188
496.5979 | 356.4266 | 256.5543 | 251.7568
497.5979 | 356.6005 | 256.7459 | 251.8963
498.5979 | 356.7919 | 256.939 | 252.0476
499.5979 | 356.9162 | 257.0153 | 252.2129
500.5979 | 356.9742 | 257.1911 | 252.3743
501.5979 | 356.9396 | 257.3623 | 252.5335
502.5979 | 356.917 | 257.5028 | 252.6998
503.5979 | 356.9832 | 257.6942 | 252.8591
504.5979 | 357.0774 | 257.9049 | 253.014
505.5979 | 357.0988 | 257.9752 | 253.1615
506.5979 | 357.0449 | 258.1285 | 253.3271
507.5979 | 356.9796 | 258.0859 | 253.5041
508.5979 | 356.9238 | 257.9696 | 253.6644
509.5979 | 356.8576 | 257.8145 | 253.8334
510.5979 | 356.7653 | 257.988 | 253.9667
511.5979 | 356.6377 | 258.1582 | 254.0845
512.5979 | 356.6608 | 258.3485 | 254.1856
513.5979 | 356.5828 | 258.5396 | 254.2822
514.5979 | 356.4098 | 258.7345 | 254.3939
515.5979 | 356.4211 | 258.8399 | 254.5201
516.5979 | 356.3523 | 258.9583 | 254.6504
517.5979 | 356.2284 | 259.0325 | 254.7936
518.5979 | 356.132 | 259.1604 | 254.9383
519.5979 | 356.1202 | 259.0662 | 255.0832
520.5979 | 356.1028 | 259.1453 | 255.2158
521.5979 | 356.1167 | 259.312 | 255.3599
522.5979 | 356.0673 | 259.5139 | 255.4945
523.5979 | 356.1436 | 259.6984 | 255.6255
524.5979 | 356.0811 | 259.8419 | 255.7727
525.5979 | 356.0932 | 259.9818 | 255.9143
526.5979 | 356.0585 | 260.0859 | 256.0549
527.5979 | 355.9545 | 260.2001 | 256.1955
528.5979 | 355.8942 | 260.293 | 256.3169
529.5979 | 355.824 | 260.2707 | 256.4394
530.5979 | 355.8741 | 260.3898 | 256.5755
531.5979 | 355.9522 | 260.5835 | 256.7052
532.5979 | 355.996 | 260.7555 | 256.8475
533.5979 | 356.1052 | 260.9399 | 256.9839
534.5979 | 356.0997 | 261.1289 | 257.1237
535.5979 | 356.1304 | 261.3216 | 257.2557
536.5979 | 356.1652 | 261.481 | 257.3892
537.5979 | 356.3281 | 261.6484 | 257.5267
538.5979 | 356.5205 | 261.8301 | 257.6617
539.5979 | 356.6155 | 262.0062 | 257.8003
540.6135 | 356.7694 | 262.1624 | 257.9411
541.5979 | 356.8307 | 262.3648 | 258.0612
542.5979 | 356.7734 | 262.5595 | 258.1945
543.5979 | 356.7087 | 262.7775 | 258.329
544.5979 | 356.7211 | 262.9646 | 258.4644
545.5979 | 356.6187 | 263.0608 | 258.5882
546.5979 | 356.6823 | 263.1908 | 258.7095
547.5979 | 356.8584 | 263.3725 | 258.8442
548.5979 | 356.8235 | 263.41 | 258.9579
549.5979 | 356.7701 | 263.5948 | 259.073
550.5979 | 356.8091 | 263.7707 | 259.1892
551.5979 | 356.8753 | 263.9782 | 259.3012
552.5979 | 356.9125 | 264.1279 | 259.4297
553.5979 | 356.9478 | 264.3055 | 259.5328
554.5979 | 356.895 | 264.533 | 259.6613
555.5979 | 356.8556 | 264.7939 | 259.7712
556.5979 | 356.7037 | 265.0567 | 259.8569
557.5979 | 356.7045 | 265.3553 | 259.9443
558.5979 | 356.7341 | 265.5958 | 260.0252
559.5979 | 356.6252 | 265.8106 | 260.1232
560.5979 | 356.6523 | 266.074 | 260.2261
561.5979 | 356.583 | 266.2201 | 260.3353
562.5979 | 356.4718 | 266.3053 | 260.4492
563.5979 | 356.4841 | 266.4273 | 260.5517
564.5979 | 356.468 | 266.5693 | 260.6557
565.5979 | 356.3892 | 266.7417 | 260.7457
566.5979 | 356.4618 | 266.8339 | 260.8463
567.5979 | 356.4877 | 266.9514 | 260.9601
568.5979 | 356.5761 | 267.0645 | 261.0765
569.5979 | 356.6054 | 267.1884 | 261.2004
570.5979 | 356.5385 | 267.4217 | 261.3266
571.5979 | 356.5641 | 267.5758 | 261.4489
572.5979 | 356.6159 | 267.55 | 261.5704
573.5979 | 356.6147 | 267.6345 | 261.6759
574.5979 | 356.5283 | 267.8037 | 261.7867
575.5979 | 356.5293 | 267.8582 | 261.8994
576.5979 | 356.5328 | 267.9782 | 261.9999
577.5979 | 356.4386 | 268.0694 | 262.1236
578.5979 | 356.3485 | 268.2723 | 262.2281
579.5979 | 356.3013 | 268.4866 | 262.3533
580.5979 | 356.2376 | 268.6394 | 262.4583
581.5979 | 356.1442 | 268.8989 | 262.5974
582.5979 | 356.1813 | 269.1289 | 262.7302
583.5979 | 356.1525 | 269.3903 | 262.8373
584.5979 | 356.0918 | 269.5456 | 262.9641
585.5979 | 355.9641 | 269.6566 | 263.083
586.5979 | 355.9148 | 269.6858 | 263.2097
587.5979 | 355.8708 | 269.7442 | 263.3123
588.5979 | 355.9517 | 269.8621 | 263.4018
589.5979 | 355.8777 | 270.0418 | 263.4904
590.5979 | 355.906 | 270.1045 | 263.5871
591.5979 | 355.7079 | 269.832 | 263.7056
592.5979 | 355.5601 | 269.7804 | 263.7787
593.5979 | 355.4476 | 269.8313 | 263.8345
594.5979 | 355.2998 | 269.6834 | 263.8985
595.5979 | 355.1462 | 269.7413 | 263.973
596.5979 | 355.0135 | 269.8822 | 264.0635
597.5979 | 355.0088 | 269.9695 | 264.1597
598.5979 | 354.9817 | 269.6926 | 264.2484
599.5979 | 354.8637 | 269.6284 | 264.3134
600.5979 | 354.7079 | 269.7427 | 264.3865
601.5979 | 354.7157 | 269.7805 | 264.4381
602.5979 | 354.9613 | 269.6418 | 264.4848
603.5979 | 354.9351 | 269.691 | 264.5223
604.5979 | 354.9772 | 269.8742 | 264.5514
605.5979 | 354.9882 | 270.0329 | 264.6195
606.5979 | 355.0613 | 270.1193 | 264.6959
607.5979 | 355.1351 | 270.0913 | 264.7785
608.5979 | 355.134 | 270.0177 | 264.8409
609.5979 | 355.1461 | 270.2037 | 264.9112
610.5979 | 355.2921 | 270.4531 | 264.9951
611.5979 | 355.3776 | 270.3268 | 265.0826
612.5979 | 355.4141 | 270.446 | 265.1837
613.5979 | 355.5431 | 270.6904 | 265.276
614.5979 | 355.6638 | 270.9619 | 265.3809
615.5979 | 355.7885 | 271.2375 | 265.494
616.5979 | 355.8254 | 271.4331 | 265.6072
617.5979 | 355.8683 | 271.6121 | 265.7186
618.5979 | 356.0215 | 271.767 | 265.8264
619.5979 | 356.1439 | 271.9058 | 265.9396
620.5979 | 356.184 | 271.9611 | 266.0575
621.5979 | 356.2714 | 271.9644 | 266.1668
622.5979 | 356.3999 | 272.0878 | 266.2731
623.5979 | 356.3096 | 271.8779 | 266.3832
624.5979 | 356.3741 | 271.6953 | 266.4847
625.5979 | 356.4589 | 271.6321 | 266.5763
626.5979 | 356.479 | 271.5336 | 266.6679
627.5979 | 356.4282 | 271.7656 | 266.7584
628.5979 | 356.477 | 271.8311 | 266.8645
629.5979 | 356.4348 | 271.9802 | 266.9338
630.5979 | 356.3372 | 271.9672 | 266.9979
631.5979 | 356.2282 | 272.0659 | 267.0572
632.5979 | 356.2631 | 272.3683 | 267.1221
633.6135 | 356.3005 | 272.6101 | 267.2144
634.5979 | 356.252 | 272.7464 | 267.2891
635.5979 | 356.1917 | 272.8588 | 267.3653
636.5979 | 356.1473 | 273.006 | 267.4382
637.5979 | 356.1096 | 273.1641 | 267.4978
638.5979 | 356.0854 | 273.2742 | 267.5688
639.5979 | 355.9902 | 273.2115 | 267.6392
640.5979 | 355.8667 | 273.1303 | 267.7358
641.5979 | 355.8516 | 272.886 | 267.8458
642.5979 | 355.8668 | 272.8789 | 267.9548
643.5979 | 355.9423 | 272.816 | 268.0612
644.5979 | 355.9005 | 272.9265 | 268.1743
645.5979 | 355.8163 | 273.1448 | 268.2746
646.5979 | 355.7121 | 273.3453 | 268.378
647.5979 | 355.7185 | 273.5254 | 268.4708
648.5979 | 355.7771 | 273.7827 | 268.5627
649.5979 | 355.7919 | 273.9693 | 268.6447
650.5979 | 355.8159 | 274.0808 | 268.7426
651.5979 | 355.8244 | 274.2005 | 268.8498
652.5979 | 355.8733 | 274.3908 | 268.9666
653.5979 | 355.8736 | 274.6759 | 269.0724
654.5979 | 355.7976 | 275.008 | 269.1645
655.5979 | 355.7466 | 275.205 | 269.2742
656.5979 | 355.7836 | 275.3208 | 269.3819
657.5979 | 355.7734 | 275.5187 | 269.5003
658.5979 | 355.7723 | 275.698 | 269.6008
659.5979 | 355.7856 | 275.7851 | 269.7106
660.5979 | 355.8151 | 276.0904 | 269.8155
661.5979 | 355.7612 | 276.2446 | 269.938
662.5979 | 355.7801 | 276.4035 | 270.0493
663.5979 | 355.6586 | 276.4615 | 270.1802
664.5979 | 355.6877 | 276.3551 | 270.3016
665.5979 | 355.7164 | 276.5178 | 270.4218
666.5979 | 355.7431 | 276.6409 | 270.5529
667.5979 | 355.8122 | 276.7801 | 270.6721
668.5979 | 355.8399 | 276.9561 | 270.7938
669.5979 | 355.8973 | 276.815 | 270.9099
670.5979 | 355.9654 | 276.9186 | 271.026
671.5979 | 356.002 | 277.1483 | 271.1469
672.5979 | 356.0332 | 277.4251 | 271.2514
673.5979 | 356.0332 | 277.4666 | 271.3618
674.5979 | 355.9955 | 277.529 | 271.482
675.5979 | 356.0509 | 277.6792 | 271.6063
676.5979 | 356.0412 | 277.8555 | 271.7225
677.5979 | 356.0529 | 277.9443 | 271.8338
678.5979 | 356.0601 | 277.9516 | 271.9417
679.5979 | 356.061 | 278.1055 | 272.0454
680.5979 | 356.1723 | 278.3126 | 272.1479
681.5979 | 356.2524 | 278.6253 | 272.2574
682.5979 | 356.2969 | 278.8038 | 272.3594
683.5979 | 356.4712 | 278.9502 | 272.4574
684.5979 | 356.493 | 279.1204 | 272.5391
685.5979 | 356.3458 | 278.9755 | 272.6443
686.5979 | 356.2427 | 278.9672 | 272.7438
687.5979 | 356.2115 | 278.8752 | 272.8427
688.5979 | 356.1491 | 279.0587 | 272.9096
689.5979 | 356.0725 | 279.1693 | 272.9777
690.5979 | 355.983 | 278.958 | 273.0421
691.5979 | 355.8341 | 279.0242 | 273.1052
692.5979 | 355.6493 | 278.9757 | 273.1788
693.5979 | 355.7299 | 279.0674 | 273.2496
694.5979 | 355.8895 | 278.991 | 273.3302
695.5979 | 355.7554 | 279.0207 | 273.4007
696.5979 | 355.7697 | 279.0804 | 273.473
697.5979 | 355.8655 | 279.1376 | 273.5448
698.5979 | 355.9267 | 279.3499 | 273.6192
699.5979 | 356.0008 | 279.5576 | 273.7068
700.5979 | 356.0375 | 279.6886 | 273.8017
701.5979 | 356.0795 | 279.8246 | 273.9
702.5979 | 356.1065 | 280.0191 | 273.9946
703.5979 | 356.1366 | 280.1041 | 274.0921
704.5979 | 355.9913 | 279.9735 | 274.1918
705.5979 | 355.9648 | 280.0215 | 274.2997
706.5979 | 356.0428 | 280.3185 | 274.3925
707.5979 | 356.1262 | 280.5568 | 274.4828
708.5979 | 356.2228 | 280.6405 | 274.5806
709.5979 | 356.1765 | 280.6241 | 274.6714
710.5979 | 356.062 | 280.6762 | 274.7611
711.5979 | 356.1233 | 280.7268 | 274.8581
712.5979 | 356.1712 | 280.7047 | 274.9474
713.5979 | 356.2409 | 280.853 | 275.0429
714.5979 | 356.2088 | 280.9797 | 275.1344
715.5979 | 356.0766 | 281.1326 | 275.2185
716.5979 | 356.0191 | 281.2834 | 275.2991
717.5979 | 356.0146 | 281.4374 | 275.3791
718.5979 | 356.0594 | 281.5235 | 275.45
719.5979 | 355.9685 | 281.672 | 275.5267
720.5979 | 355.8066 | 281.9095 | 275.6037
721.5979 | 355.8587 | 282.1855 | 275.6623
722.5979 | 355.8121 | 282.2269 | 275.7289
723.5979 | 355.789 | 282.2002 | 275.8031
724.5979 | 355.717 | 282.2157 | 275.8806
725.5979 | 355.6141 | 282.2387 | 275.9777
726.5979 | 355.6119 | 282.455 | 276.0637
727.5979 | 355.5696 | 282.6018 | 276.1779
728.5979 | 355.6396 | 282.9105 | 276.2739
729.5979 | 355.7856 | 282.9289 | 276.3667
730.5979 | 355.7842 | 282.7877 | 276.4578
731.5979 | 355.7626 | 282.7149 | 276.5613
732.5979 | 355.779 | 282.8265 | 276.6653
733.5979 | 355.732 | 282.903 | 276.7733
734.5979 | 355.6308 | 283.0253 | 276.8813
735.5979 | 355.5132 | 283.0591 | 276.9875
736.5979 | 355.5206 | 283.1448 | 277.0895
737.5979 | 355.4926 | 283.1546 | 277.1825
738.5979 | 355.4734 | 283.1967 | 277.2674
739.5979 | 355.5295 | 283.2342 | 277.3625
740.5979 | 355.4575 | 283.3798 | 277.4495
741.5979 | 355.5101 | 283.6214 | 277.5375
742.5979 | 355.5254 | 283.7255 | 277.6347
743.5979 | 355.5283 | 283.7339 | 277.7278
744.5979 | 355.5552 | 283.5627 | 277.8246
745.5979 | 355.4805 | 283.5849 | 277.9176
746.5979 | 355.4476 | 283.5936 | 278.009
747.5979 | 355.5552 | 283.4869 | 278.0818
748.5979 | 355.6361 | 283.5998 | 278.16
749.5979 | 355.6523 | 283.5947 | 278.2325
750.5979 | 355.7075 | 283.709 | 278.3088
751.5979 | 355.6446 | 283.7098 | 278.3821
752.5979 | 355.5852 | 283.7465 | 278.4525
753.5979 | 355.4788 | 283.8114 | 278.5174
754.5979 | 355.5318 | 283.8916 | 278.5727
755.5979 | 355.5757 | 284.0123 | 278.6297
756.5979 | 355.6061 | 284.3179 | 278.6888
757.5979 | 355.6915 | 284.5668 | 278.7439
758.5979 | 355.7357 | 284.7009 | 278.8086
759.5979 | 355.6108 | 284.7812 | 278.8872
760.5979 | 355.6318 | 284.4931 | 278.9607
761.5979 | 355.7704 | 284.4489 | 279.0366
762.5979 | 355.8006 | 284.6505 | 279.1144
763.5979 | 355.7244 | 284.7624 | 279.1923
764.5979 | 355.7058 | 285.0506 | 279.2633
765.5979 | 355.7582 | 285.1964 | 279.3278
766.5979 | 355.8253 | 285.3762 | 279.3902
767.5979 | 355.8079 | 285.5357 | 279.461
768.5979 | 355.7848 | 285.7072 | 279.5287
769.5979 | 355.7406 | 285.8387 | 279.6058
770.5979 | 355.7393 | 285.9569 | 279.671
771.5979 | 355.8022 | 285.8009 | 279.754
772.5979 | 355.8941 | 285.5496 | 279.8274
773.5979 | 355.8415 | 285.5916 | 279.9128
774.5979 | 355.6896 | 285.7474 | 279.9955
775.5979 | 355.6492 | 285.8388 | 280.0709
776.5979 | 355.7532 | 285.9823 | 280.1469
777.5979 | 355.7994 | 286.0305 | 280.2151
778.5979 | 355.6963 | 286.1409 | 280.2841
779.5979 | 355.6242 | 286.2672 | 280.3569
780.5979 | 355.6254 | 286.2712 | 280.4278
781.5979 | 355.554 | 286.4041 | 280.4918
782.5979 | 355.4619 | 286.5459 | 280.5473
783.5979 | 355.3431 | 286.5822 | 280.604
784.5979 | 355.2628 | 286.6623 | 280.6542
785.5979 | 355.2657 | 286.6622 | 280.7042
786.5979 | 355.2231 | 286.7053 | 280.7634
787.5979 | 355.1613 | 286.5582 | 280.8237
788.5979 | 355.1661 | 286.4761 | 280.8812
789.5979 | 355.3036 | 286.588 | 280.9392
790.5979 | 355.3652 | 286.6222 | 280.9994
791.5979 | 355.3747 | 286.7043 | 281.059
792.5979 | 355.369 | 286.7037 | 281.1243
793.5979 | 355.3595 | 286.7055 | 281.1693
794.5979 | 355.3142 | 286.9505 | 281.2155
795.5979 | 355.2495 | 287.1533 | 281.2525
796.5979 | 355.2445 | 287.3166 | 281.2971
797.5979 | 355.243 | 287.5621 | 281.3351
798.5979 | 355.1813 | 287.6273 | 281.396
799.5979 | 355.1272 | 287.6404 | 281.4429
800.5979 | 355.1401 | 287.584 | 281.5054
801.5979 | 355.1366 | 287.5853 | 281.5696
802.5979 | 355.2069 | 287.7774 | 281.6349
803.5979 | 355.3374 | 287.8184 | 281.6978
804.5979 | 355.4279 | 287.8531 | 281.7614
805.5979 | 355.5242 | 287.6446 | 281.8363
806.5979 | 355.4849 | 287.6175 | 281.9106
807.5979 | 355.4138 | 287.276 | 281.9707
808.5979 | 355.4629 | 287.2118 | 282.0521
809.5979 | 355.5306 | 287.3555 | 282.1303
810.5979 | 355.7291 | 287.3736 | 282.2059
811.5979 | 355.7987 | 287.4818 | 282.262
812.5979 | 355.8556 | 287.5313 | 282.3123
813.5979 | 355.8448 | 287.5283 | 282.3646
814.5979 | 355.8175 | 287.7031 | 282.4219
815.5979 | 355.7823 | 287.7724 | 282.4708
816.5979 | 355.793 | 287.6988 | 282.5266
817.5979 | 355.8315 | 287.7476 | 282.5735
818.5979 | 355.9304 | 287.6616 | 282.6245
819.5979 | 355.9717 | 287.8116 | 282.6809
820.5979 | 356.0067 | 287.9283 | 282.7298
821.5979 | 356.0298 | 288.082 | 282.775
822.5979 | 355.9625 | 287.8667 | 282.8282
823.5979 | 355.8788 | 287.8784 | 282.8892
824.5979 | 355.9808 | 288.0001 | 282.9567
825.5979 | 355.9414 | 288.0424 | 283.0249
826.5979 | 356.034 | 287.9378 | 283.0707
827.5979 | 356.1634 | 287.9108 | 283.1299
828.5979 | 356.1745 | 287.9176 | 283.1798
829.5979 | 356.0658 | 287.9657 | 283.2294
830.5979 | 356.1409 | 288.0491 | 283.2835
831.5979 | 356.2387 | 288.0774 | 283.3389
832.5979 | 356.1596 | 288.0809 | 283.3935
833.5979 | 355.987 | 288.0595 | 283.454
834.5979 | 355.9845 | 288.0214 | 283.5279
835.5979 | 356.0467 | 288.1098 | 283.5837
836.5979 | 356.0587 | 288.2363 | 283.642
837.5979 | 356.1028 | 288.217 | 283.6946
838.5979 | 356.0591 | 288.2896 | 283.7586
839.5979 | 356.1213 | 288.3459 | 283.8247
840.5979 | 356.1312 | 288.3561 | 283.8909
841.5979 | 356.0706 | 288.3607 | 283.9531
842.5979 | 356.0712 | 288.5325 | 284.0058
843.5979 | 356.0868 | 288.605 | 284.0657
844.5979 | 356.0156 | 288.7143 | 284.1162
845.5979 | 355.8866 | 288.8599 | 284.1695
846.5979 | 355.8752 | 289.0565 | 284.219
847.5979 | 355.7774 | 289.1139 | 284.2746
848.5979 | 355.7317 | 289.1889 | 284.3449
849.5979 | 355.7104 | 289.3404 | 284.3792
850.5979 | 355.6522 | 289.4878 | 284.4359
851.5979 | 355.7047 | 289.4925 | 284.4678
852.5979 | 355.8371 | 289.3958 | 284.4967
853.5979 | 355.8489 | 289.374 | 284.534
854.5979 | 355.8206 | 289.5054 | 284.5757
855.5979 | 355.862 | 289.7077 | 284.5976
856.5979 | 355.8616 | 289.8776 | 284.6151
857.5979 | 355.767 | 290.0202 | 284.6346
858.5979 | 355.5977 | 289.9858 | 284.6526
859.5979 | 355.6276 | 289.972 | 284.6889
860.5979 | 355.68 | 290.0539 | 284.716
861.5979 | 355.6422 | 290.0702 | 284.7504
862.5979 | 355.5652 | 289.9258 | 284.7888
863.5979 | 355.6007 | 289.7703 | 284.8207
864.5979 | 355.6311 | 289.6716 | 284.8562
865.5979 | 355.6306 | 289.193 | 284.9084
866.5979 | 355.5985 | 288.7959 | 284.9602
867.5979 | 355.5599 | 288.7556 | 285.0114
868.5979 | 355.5565 | 288.7382 | 285.0608
869.5979 | 355.5795 | 288.8096 | 285.1168
870.5979 | 355.5216 | 289.0097 | 285.1776
871.5979 | 355.5914 | 289.1631 | 285.2278
872.5979 | 355.6181 | 289.1509 | 285.2771
873.5979 | 355.6396 | 289.1615 | 285.3258
874.5979 | 355.7844 | 289.0641 | 285.376
875.5979 | 355.756 | 289.0487 | 285.4297
876.5979 | 355.7272 | 289.1369 | 285.4695
877.5979 | 355.8285 | 289.2917 | 285.5002
878.5979 | 355.7829 | 289.2324 | 285.5222
879.5979 | 355.734 | 289.0861 | 285.559
880.5979 | 355.7628 | 288.8477 | 285.569
881.5979 | 355.7872 | 288.9005 | 285.5817
882.5979 | 355.8318 | 288.9346 | 285.6239
883.5979 | 355.7884 | 289.1443 | 285.6411
884.5979 | 355.809 | 289.2707 | 285.6844
885.5979 | 355.7581 | 289.2976 | 285.732
886.5979 | 355.7578 | 289.553 | 285.764
887.5979 | 355.7866 | 289.6879 | 285.792
888.5979 | 355.901 | 289.6151 | 285.8174
889.5979 | 355.8875 | 289.5281 | 285.8441
890.5979 | 355.7408 | 289.4427 | 285.8589
891.5979 | 355.6763 | 288.8873 | 285.8889
892.5979 | 355.6019 | 288.3967 | 285.9171
893.5979 | 355.5868 | 288.2715 | 285.9526
894.5979 | 355.5571 | 288.2895 | 285.9785
895.5979 | 355.5211 | 288.3755 | 286.0078
896.5979 | 355.4138 | 288.4114 | 286.0333
897.5979 | 355.3782 | 288.2193 | 286.0752
898.5979 | 355.2894 | 288.1463 | 286.1084
899.5979 | 355.2091 | 287.8424 | 286.1419
900.5979 | 355.3841 | 287.8433 | 286.1532
901.5979 | 355.4764 | 287.87 | 286.1592
902.5979 | 355.4774 | 287.6027 | 286.1625
903.5979 | 355.5422 | 287.5924 | 286.1799
904.5979 | 355.5739 | 287.6118 | 286.211
905.5979 | 355.5744 | 287.6407 | 286.2347
906.5979 | 355.4887 | 287.7846 | 286.2715
907.5979 | 355.4425 | 287.6346 | 286.31
908.5979 | 355.3217 | 287.5721 | 286.3547
909.5979 | 355.2983 | 287.3937 | 286.4031
910.5979 | 355.4014 | 287.4875 | 286.4445
911.5979 | 355.4516 | 287.544 | 286.475
912.5979 | 355.3711 | 287.6835 | 286.5082
913.5979 | 355.2908 | 287.7342 | 286.5315
914.5979 | 355.3345 | 287.8796 | 286.545
915.5979 | 355.3481 | 287.9013 | 286.5658
916.5979 | 355.3433 | 288.0717 | 286.5863
917.5979 | 355.3691 | 288.0739 | 286.6132
918.5979 | 355.4291 | 288.2547 | 286.6356
919.5979 | 355.4266 | 288.6159 | 286.6588
920.5979 | 355.4208 | 288.6773 | 286.6881
921.5979 | 355.3808 | 288.9038 | 286.7213
922.5979 | 355.3711 | 289.1244 | 286.7539
923.5979 | 355.441 | 289.2356 | 286.7713
924.5979 | 355.447 | 289.2896 | 286.7813
925.5979 | 355.4705 | 288.8257 | 286.7904
926.5979 | 355.464 | 288.8358 | 286.7887
927.5979 | 355.4077 | 288.9576 | 286.7937
928.5979 | 355.437 | 288.8007 | 286.8137
929.5979 | 355.5397 | 288.9852 | 286.8276
930.5979 | 355.5215 | 289.1457 | 286.8502
931.5979 | 355.6927 | 288.8303 | 286.8789
932.5979 | 355.8645 | 288.7681 | 286.8929
933.5979 | 355.8904 | 288.384 | 286.9131
934.5979 | 355.9421 | 288.5 | 286.9405
935.5979 | 355.9593 | 288.5179 | 286.9484
936.5979 | 355.9293 | 288.4955 | 286.9724
937.5979 | 355.975 | 288.6722 | 287.0104
938.5979 | 355.9414 | 288.8362 | 287.0322
939.5979 | 356.0905 | 288.9603 | 287.0661
940.5979 | 356.1817 | 288.9856 | 287.09
941.5979 | 356.1584 | 288.8513 | 287.1215
942.5979 | 356.1093 | 289.0301 | 287.1535
943.5979 | 356.1711 | 289.0755 | 287.1906
944.5979 | 356.1925 | 289.1116 | 287.2304
945.5979 | 356.1828 | 289.2011 | 287.2676
946.5979 | 355.9804 | 289.131 | 287.3011
947.5979 | 355.9793 | 289.2419 | 287.3389
948.5979 | 355.9665 | 289.2696 | 287.3715
949.5979 | 355.9197 | 289.3313 | 287.395
950.5979 | 355.9426 | 289.3712 | 287.4116
951.5979 | 355.979 | 289.4662 | 287.4271
952.5979 | 355.9818 | 289.5053 | 287.4366
953.5979 | 355.9569 | 289.4213 | 287.453
954.5979 | 355.8752 | 289.6684 | 287.4679
955.5979 | 355.844 | 289.7998 | 287.4971
956.5979 | 355.7744 | 289.9469 | 287.5259
957.5979 | 355.8206 | 290.1118 | 287.553
958.5979 | 355.7944 | 290.0752 | 287.578
959.5979 | 355.7562 | 289.9384 | 287.6088
960.5979 | 355.7145 | 289.9711 | 287.6454
961.5979 | 355.6994 | 289.9495 | 287.686
962.5979 | 355.7198 | 289.9436 | 287.7097
963.5979 | 355.7199 | 290.1917 | 287.7321
964.5979 | 355.7396 | 290.4258 | 287.7721
965.5979 | 355.7772 | 290.6262 | 287.8124
966.5979 | 355.7303 | 290.4772 | 287.8457
967.5979 | 355.5974 | 290.4176 | 287.8829
968.5979 | 355.542 | 290.3558 | 287.8996
969.5979 | 355.6088 | 290.4096 | 287.9179
970.5979 | 355.6119 | 290.5402 | 287.9391
971.5979 | 355.5556 | 290.6695 | 287.9505
972.5979 | 355.5343 | 290.7524 | 287.9651
973.5979 | 355.5358 | 290.7584 | 287.9887
974.5979 | 355.4678 | 290.7197 | 288.0061
975.5979 | 355.4134 | 290.5519 | 288.0196
976.5979 | 355.4202 | 290.487 | 288.0433
977.5979 | 355.5476 | 290.2869 | 288.0525
978.5979 | 355.6995 | 290.0989 | 288.0813
979.5979 | 355.77 | 290.2558 | 288.0955
980.5979 | 355.8155 | 290.2486 | 288.1212
981.5979 | 355.7351 | 290.1848 | 288.1555
982.5979 | 355.6485 | 290.2386 | 288.1835
983.5979 | 355.6827 | 290.3895 | 288.2096
984.5979 | 355.7022 | 290.423 | 288.2348
985.5979 | 355.6414 | 290.4524 | 288.2752
986.5979 | 355.6478 | 290.5904 | 288.3159
987.5979 | 355.7031 | 290.5782 | 288.346
988.5979 | 355.8172 | 290.6596 | 288.3734
989.5979 | 355.8864 | 290.9694 | 288.4085
990.5979 | 355.9104 | 290.9809 | 288.4541
991.5979 | 355.7951 | 290.8495 | 288.4889
992.5979 | 355.8358 | 290.9569 | 288.5366
993.5979 | 355.8999 | 290.9777 | 288.5699
994.5979 | 355.918 | 290.8973 | 288.615
995.5979 | 355.9122 | 291.0444 | 288.6585
996.5979 | 355.8638 | 291.3708 | 288.6899
997.5979 | 355.7835 | 291.5682 | 288.7155
998.5979 | 355.6164 | 291.5643 | 288.7368
999.5979 | 355.4908 | 291.4711 | 288.7518
1000.5979 | 355.556 | 291.449 | 288.771
1001.5979 | 355.6878 | 291.4712 | 288.7988
1002.5979 | 355.5897 | 291.5648 | 288.8192
1003.5979 | 355.5797 | 291.6089 | 288.8417
1004.5979 | 355.6216 | 291.4472 | 288.8782
1005.5979 | 355.6449 | 291.1494 | 288.9038
1006.5979 | 355.6768 | 291.2167 | 288.9273
1007.5979 | 355.6011 | 291.3106 | 288.9497
1008.5979 | 355.5691 | 291.5131 | 288.9564
1009.5979 | 355.5472 | 291.6148 | 288.9808
1010.5979 | 355.4751 | 291.6452 | 288.998
1011.5979 | 355.3883 | 291.7687 | 289.0229
1012.5979 | 355.3713 | 291.7568 | 289.0392
1013.5979 | 355.3583 | 291.6547 | 289.0549
1014.5979 | 355.3492 | 291.6972 | 289.0651
1015.5979 | 355.3872 | 291.7693 | 289.0967
1016.5979 | 355.454 | 291.6632 | 289.1123
1017.5979 | 355.5443 | 291.238 | 289.1317
1018.5979 | 355.4799 | 291.1932 | 289.1545
1019.5979 | 355.4448 | 291.3331 | 289.1916
1020.5979 | 355.5919 | 291.4991 | 289.2277
1021.5979 | 355.6538 | 291.4922 | 289.2624
1022.5979 | 355.6044 | 291.5906 | 289.3084
1023.5979 | 355.584 | 291.7448 | 289.3314
1024.5979 | 355.5031 | 292.0757 | 289.3535
1025.5979 | 355.4524 | 292.3975 | 289.3448
1026.5979 | 355.3743 | 292.6547 | 289.3237
1027.5979 | 355.4272 | 292.7722 | 289.3173
1028.5979 | 355.4332 | 292.6609 | 289.3147
1029.5979 | 355.3604 | 292.4889 | 289.3202
1030.5979 | 355.1699 | 292.5034 | 289.3142
1031.5979 | 355.0592 | 292.607 | 289.3272
1032.5979 | 355.1198 | 292.7754 | 289.349
1033.5979 | 355.0881 | 292.8563 | 289.3684
1034.5979 | 355.0299 | 292.9627 | 289.3966
1035.5979 | 355.0424 | 293.1061 | 289.4195
1036.5979 | 355.005 | 293.2217 | 289.4263
1037.5979 | 354.9359 | 293.3722 | 289.4336
1038.5979 | 354.9364 | 293.1997 | 289.4532
1039.5979 | 354.9524 | 293.3066 | 289.4769
1040.5979 | 354.9589 | 293.4765 | 289.4922
1041.5979 | 354.942 | 293.4256 | 289.516
1042.5979 | 354.8933 | 293.1473 | 289.5424
1043.5979 | 354.8809 | 293.0049 | 289.5783
1044.5979 | 354.9305 | 292.9965 | 289.6018
1045.5979 | 354.8149 | 293.0562 | 289.6359
1046.5979 | 354.7445 | 293.0772 | 289.6689
1047.5979 | 354.7643 | 293.2561 | 289.689
1048.5979 | 354.7662 | 293.315 | 289.7251
1049.5979 | 354.7395 | 293.2898 | 289.7406
1050.5979 | 354.6774 | 293.4088 | 289.7588
1051.5979 | 354.7233 | 293.4352 | 289.7631
1052.5979 | 354.7714 | 293.3365 | 289.7786
1053.5979 | 354.7153 | 293.4232 | 289.7827
1054.5979 | 354.7325 | 293.529 | 289.7954
1055.5979 | 354.8203 | 293.4527 | 289.7928
1056.5979 | 354.9336 | 293.3256 | 289.7925
1057.5979 | 354.9784 | 293.2905 | 289.795
1058.5979 | 354.9684 | 293.2398 | 289.7976
1059.5979 | 354.9053 | 293.2916 | 289.7987
1060.5979 | 354.9462 | 293.2244 | 289.7824
1061.5979 | 354.8992 | 293.2693 | 289.7775
1062.5979 | 354.8808 | 293.42 | 289.7807
1063.5979 | 354.9786 | 293.301 | 289.8009
1064.5979 | 355.1698 | 293.3939 | 289.8048
1065.5979 | 355.2058 | 293.411 | 289.8157
1066.5979 | 355.2536 | 293.2709 | 289.8347
1067.5979 | 355.2338 | 293.3244 | 289.8495
1068.5979 | 355.1511 | 293.3738 | 289.8683
1069.5979 | 355.1588 | 293.3284 | 289.8918
1070.5979 | 355.238 | 292.9519 | 289.9204
1071.5979 | 355.3188 | 293.048 | 289.9508
1072.5979 | 355.331 | 293.2015 | 289.9776
1073.5979 | 355.299 | 293.3056 | 290.0181
1074.5979 | 355.2788 | 292.8645 | 290.046
1075.5979 | 355.2525 | 292.8321 | 290.0714
1076.5979 | 355.3391 | 292.4689 | 290.0939
1077.5979 | 355.4105 | 292.4777 | 290.1166
1078.5979 | 355.5087 | 292.5846 | 290.1297
1079.5979 | 355.5861 | 292.7295 | 290.1398
1080.5979 | 355.6256 | 292.2966 | 290.1473
1081.5979 | 355.4808 | 291.8825 | 290.1555
1082.5979 | 355.4113 | 291.5832 | 290.162
1083.5979 | 355.3845 | 291.4519 | 290.1484
1084.5979 | 355.4704 | 291.5697 | 290.1363
1085.5979 | 355.5542 | 291.5858 | 290.113
1086.5979 | 355.6838 | 291.7535 | 290.0989
1087.5979 | 355.8469 | 291.8353 | 290.09
1088.5979 | 355.9612 | 291.7934 | 290.0762
1089.5979 | 355.9022 | 291.7396 | 290.0662
1090.5979 | 355.9675 | 291.7282 | 290.0731
1091.5979 | 355.9815 | 291.676 | 290.0682
1092.5979 | 355.8953 | 291.738 | 290.0711
1093.5979 | 355.8633 | 291.8655 | 290.0554
1094.5979 | 355.9732 | 291.9399 | 290.0412
1095.5979 | 356.0459 | 291.9883 | 290.0294
1096.5979 | 356.1175 | 291.6744 | 290.0194
1097.5979 | 356.1889 | 291.7041 | 290.0148
1098.5979 | 356.0942 | 291.7878 | 290.0298
1099.5979 | 355.9848 | 291.9383 | 290.0387
1100.5979 | 355.9066 | 292.0701 | 290.0586
1101.5979 | 355.9638 | 292.2477 | 290.0781
1102.5979 | 355.8774 | 292.1801 | 290.0919
1103.5979 | 355.8511 | 292.1489 | 290.113
1104.5979 | 355.7725 | 292.0837 | 290.1237
1105.5979 | 355.7437 | 292.1164 | 290.15
1106.5979 | 355.7143 | 292.1484 | 290.1702
1107.5979 | 355.8081 | 292.0493 | 290.1749
1108.5979 | 355.8863 | 292.0844 | 290.1897
1109.5979 | 355.7849 | 292.1381 | 290.211
1110.5979 | 355.7054 | 292.2517 | 290.2311
1111.5979 | 355.6512 | 292.4978 | 290.2502
1112.5979 | 355.5852 | 292.6585 | 290.2669
1113.5979 | 355.5628 | 292.9081 | 290.2704
1114.5979 | 355.5879 | 292.9037 | 290.2818
1115.5979 | 355.6432 | 293.0057 | 290.2888
1116.5979 | 355.7286 | 292.6153 | 290.2884
1117.5979 | 355.6822 | 292.596 | 290.2946
1118.5979 | 355.6271 | 292.7599 | 290.3124
1119.5979 | 355.5972 | 292.9812 | 290.3355
1120.5979 | 355.6307 | 292.9161 | 290.3494
1121.5979 | 355.6152 | 293.1428 | 290.3661
1122.5979 | 355.5746 | 293.2156 | 290.3949
1123.5979 | 355.4033 | 293.3299 | 290.4041
1124.5979 | 355.3638 | 293.3324 | 290.4239
1125.5979 | 355.4659 | 293.4992 | 290.4321
1126.5979 | 355.4886 | 293.2126 | 290.4574
1127.5979 | 355.5115 | 293.2101 | 290.4884
1128.5979 | 355.5636 | 293.0316 | 290.5107
1129.5979 | 355.5854 | 293.0318 | 290.5347
1130.5979 | 355.5252 | 292.8955 | 290.5508
1131.5979 | 355.3754 | 292.81 | 290.5725
1132.5979 | 355.3109 | 292.7558 | 290.5919
1133.5979 | 355.2181 | 292.6191 | 290.619
1134.5979 | 355.2203 | 292.6204 | 290.6468
1135.5979 | 355.3162 | 292.5952 | 290.6683
1136.5979 | 355.5349 | 292.4342 | 290.6879
1137.5979 | 355.4744 | 292.4569 | 290.6943
1138.5979 | 355.3497 | 292.51 | 290.6834
1139.5979 | 355.2977 | 292.6825 | 290.6891
1140.5979 | 355.2517 | 292.7044 | 290.7019
1141.5979 | 355.2731 | 292.1716 | 290.7183
1142.5979 | 355.2997 | 291.9808 | 290.7479
1143.5979 | 355.2591 | 291.9674 | 290.7626
1144.5979 | 355.1563 | 292.1499 | 290.7674
1145.5979 | 355.1745 | 292.1951 | 290.7662
1146.5979 | 355.1171 | 292.3381 | 290.7731
1147.5979 | 355.0168 | 292.4795 | 290.7706
1148.5979 | 355.0504 | 292.662 | 290.7758
1149.5979 | 355.1303 | 292.5421 | 290.7767
1150.5979 | 355.1338 | 291.9918 | 290.797
1151.5979 | 355.1468 | 292.0037 | 290.8029
1152.5979 | 355.1741 | 291.9441 | 290.8109
1153.5979 | 355.2159 | 292.1691 | 290.8122
1154.5979 | 355.2619 | 292.2533 | 290.8312
1155.5979 | 355.2809 | 292.0774 | 290.8492
1156.5979 | 355.1908 | 292.1684 | 290.8676
1157.5979 | 355.1715 | 292.1567 | 290.88
1158.5979 | 355.1275 | 291.5895 | 290.8992
1159.5979 | 355.2371 | 291.6946 | 290.9139
1160.5979 | 355.2959 | 291.839 | 290.9374
1161.5979 | 355.2849 | 291.6055 | 290.9528
1162.5979 | 355.2242 | 291.1648 | 290.9658
1163.5979 | 355.146 | 291.465 | 290.9638
1164.5979 | 355.0719 | 291.3003 | 290.9521
1165.5979 | 355.0701 | 290.7813 | 290.9291
1166.5979 | 355.1457 | 290.3151 | 290.8967
1167.5979 | 355.1589 | 290.5734 | 290.8725
1168.5979 | 355.1252 | 290.6903 | 290.8473
1169.5979 | 355.1342 | 290.6501 | 290.8211
1170.5979 | 355.1333 | 290.7731 | 290.7908
1171.5979 | 355.2627 | 290.9346 | 290.7736
1172.5979 | 355.3124 | 291.0778 | 290.76
1173.5979 | 355.3926 | 291.3854 | 290.7587
1174.5979 | 355.4174 | 291.4957 | 290.7658
1175.5979 | 355.4714 | 291.3478 | 290.7772
1176.5979 | 355.5746 | 291.2878 | 290.7964
1177.5979 | 355.6491 | 291.4373 | 290.8138
1178.5979 | 355.6838 | 291.3363 | 290.8355
1179.5979 | 355.7255 | 291.2689 | 290.8443
1180.5979 | 355.7686 | 291.4459 | 290.8471
1181.5979 | 355.7105 | 291.5467 | 290.8459
1182.5979 | 355.7721 | 291.5497 | 290.8494
1183.5979 | 355.7049 | 291.7594 | 290.8439
1184.5979 | 355.6457 | 291.7963 | 290.8439
1185.5979 | 355.6077 | 291.8569 | 290.8542
1186.5979 | 355.6662 | 291.8708 | 290.8589
1187.5979 | 355.694 | 291.9263 | 290.8831
1188.5979 | 355.6509 | 292.1183 | 290.8996
1189.5979 | 355.6568 | 292.4976 | 290.9198
1190.5979 | 355.612 | 292.6732 | 290.9384
1191.5979 | 355.4898 | 292.8594 | 290.9313
1192.5979 | 355.3488 | 292.8306 | 290.9286
1193.5979 | 355.407 | 293.0166 | 290.9238
1194.5979 | 355.4092 | 293.139 | 290.9332
1195.5979 | 355.4472 | 293.226 | 290.9434
1196.5979 | 355.4634 | 293.3995 | 290.9539
1197.5979 | 355.4849 | 293.5148 | 290.9676
1198.5979 | 355.5057 | 293.2841 | 290.982
1199.5979 | 355.5282 | 293.2357 | 291.0022
1200.5979 | 355.5852 | 293.3875 | 291.0185
1201.5979 | 355.581 | 293.4033 | 291.0364
1202.5979 | 355.5489 | 293.6948 | 291.0451
1203.5979 | 355.5287 | 293.9502 | 291.0513
1204.5979 | 355.4522 | 294.2149 | 291.0564
1205.5979 | 355.5242 | 294.2474 | 291.0727
1206.5979 | 355.6585 | 294.2675 | 291.0913
1207.5979 | 355.7131 | 294.3547 | 291.1231
1208.5979 | 355.5747 | 294.0929 | 291.1566
1209.5979 | 355.4732 | 294.087 | 291.1805
1210.5979 | 355.4718 | 294.0679 | 291.2124
1211.5979 | 355.413 | 294.0632 | 291.2471
1212.5979 | 355.4821 | 294.171 | 291.2741
1213.5979 | 355.4203 | 294.2256 | 291.2947
1214.5979 | 355.3218 | 293.952 | 291.3243
1215.5979 | 355.2417 | 293.7595 | 291.3531
1216.5979 | 355.1929 | 293.614 | 291.3737
1217.5979 | 355.1314 | 293.6425 | 291.3744
1218.5979 | 355.0631 | 293.5977 | 291.3713
1219.5979 | 355.0209 | 293.3594 | 291.3722
1220.5979 | 354.9608 | 293.3431 | 291.3598
1221.5979 | 354.9859 | 293.2671 | 291.3511
1222.5979 | 354.9463 | 293.3161 | 291.3279
1223.5979 | 354.9141 | 293.2947 | 291.3186
1224.5979 | 354.9048 | 293.0387 | 291.3
1225.5979 | 354.9347 | 292.967 | 291.2941
1226.5979 | 354.9934 | 293.0215 | 291.2913
1227.5979 | 355.0164 | 293.0537 | 291.3037
1228.5979 | 354.9973 | 293.1098 | 291.2916
1229.5979 | 354.9394 | 293.235 | 291.301
1230.5979 | 354.9549 | 293.3133 | 291.3221
1231.5979 | 354.8621 | 293.334 | 291.3445
1232.5979 | 354.8554 | 293.2649 | 291.3585
1233.5979 | 354.7546 | 293.0751 | 291.3763
1234.5979 | 354.6136 | 293.0727 | 291.3885
1235.5979 | 354.5963 | 292.9148 | 291.3802
1236.5979 | 354.5928 | 293.0503 | 291.3658
1237.5979 | 354.7221 | 292.8271 | 291.3427
1238.5979 | 354.8934 | 292.5133 | 291.328
1239.5979 | 355.0762 | 292.5846 | 291.3204
1240.5979 | 355.23 | 292.6469 | 291.3073
1241.5979 | 355.2785 | 292.608 | 291.2959
1242.5979 | 355.2185 | 292.6851 | 291.2858
1243.5979 | 355.3378 | 292.5775 | 291.293
1244.5979 | 355.4309 | 292.5369 | 291.3041
1245.5979 | 355.5302 | 292.3434 | 291.3125
1246.5979 | 355.6291 | 292.024 | 291.3343
1247.5979 | 355.6462 | 291.9423 | 291.3331
1248.5979 | 355.7688 | 292.1183 | 291.3337
1249.5979 | 355.768 | 292.2177 | 291.3409
1250.5979 | 355.8557 | 292.3108 | 291.3355
1251.5979 | 355.9419 | 292.4388 | 291.3194
1252.5979 | 355.8415 | 292.4885 | 291.3053
1253.5979 | 355.8348 | 292.4063 | 291.2924
1254.5979 | 355.8315 | 292.2217 | 291.2843
1255.5979 | 355.7645 | 291.8983 | 291.2865
1256.5979 | 355.7603 | 291.8873 | 291.2732
1257.5979 | 355.8078 | 291.1913 | 291.2551
1258.5979 | 355.7974 | 290.7309 | 291.2197
1259.5979 | 355.7869 | 290.3916 | 291.1882
1260.5979 | 355.763 | 290.5622 | 291.1468
1261.5979 | 355.6899 | 290.8293 | 291.1118
1262.5979 | 355.665 | 291.2361 | 291.0692
1263.5979 | 355.6209 | 291.2094 | 291.0236
1264.5979 | 355.7145 | 291.3016 | 290.9882
1265.5979 | 355.723 | 291.4179 | 290.9684
1266.5979 | 355.789 | 291.3033 | 290.955
1267.5979 | 355.738 | 291.3374 | 290.9306
1268.5979 | 355.7317 | 291.5678 | 290.9019
1269.5979 | 355.8089 | 291.7902 | 290.8639
1270.5979 | 355.9183 | 291.5628 | 290.8275
1271.5979 | 355.9032 | 291.6982 | 290.8159
1272.5979 | 355.9509 | 291.8056 | 290.808
1273.5979 | 355.8852 | 291.929 | 290.808
1274.5979 | 355.8128 | 291.8901 | 290.7966
1275.5979 | 355.7321 | 291.9751 | 290.7699
1276.5979 | 355.7143 | 292.1369 | 290.7282
1277.5979 | 355.7468 | 292.2194 | 290.6883
1278.5979 | 355.7172 | 292.4192 | 290.6605
1279.5979 | 355.7395 | 292.3907 | 290.6307
1280.5979 | 355.7892 | 292.4442 | 290.6245
1281.5979 | 355.7817 | 292.4604 | 290.6126
1282.5979 | 355.7263 | 292.3678 | 290.6109
1283.5979 | 355.6539 | 292.1092 | 290.6114
1284.5979 | 355.7508 | 291.9993 | 290.6019
1285.5979 | 355.7222 | 291.7904 | 290.5853
1286.5979 | 355.7817 | 291.4138 | 290.5443
1287.5979 | 355.7248 | 291.0787 | 290.5068
1288.5979 | 355.6595 | 290.7916 | 290.4714
1289.5979 | 355.6048 | 290.9348 | 290.4138
1290.5979 | 355.5527 | 291.245 | 290.3681
1291.5979 | 355.5469 | 291.361 | 290.3344
1292.5979 | 355.4907 | 290.9565 | 290.3071
1293.5979 | 355.4017 | 290.9511 | 290.2832
1294.5979 | 355.2781 | 290.7469 | 290.2688
1295.5979 | 355.2429 | 290.8366 | 290.2535
1296.5979 | 355.3265 | 291.0737 | 290.2246
1297.5979 | 355.3897 | 291.1158 | 290.2088
1298.5979 | 355.4787 | 291.2843 | 290.1969
1299.5979 | 355.417 | 291.3825 | 290.2026
1300.5979 | 355.3634 | 291.5764 | 290.2049
1301.5979 | 355.3745 | 291.5714 | 290.2014
1302.5979 | 355.3849 | 291.3994 | 290.2105
1303.5979 | 355.3548 | 291.5241 | 290.2151
1304.5979 | 355.2917 | 291.0154 | 290.2261
1305.5979 | 355.3164 | 290.9458 | 290.2294
1306.5979 | 355.4587 | 291.0124 | 290.2462
1307.5979 | 355.4641 | 291.2016 | 290.2806
1308.5979 | 355.5128 | 291.6098 | 290.3223
1309.5979 | 355.4708 | 291.8678 | 290.3485
1310.5979 | 355.4456 | 291.9655 | 290.3805
1311.5979 | 355.4344 | 291.8428 | 290.4068
1312.5979 | 355.3228 | 291.9157 | 290.4301
1313.5979 | 355.4449 | 291.9973 | 290.4462
1314.5979 | 355.4771 | 292.0797 | 290.4671
1315.5979 | 355.4429 | 292.0035 | 290.4978
1316.5979 | 355.455 | 292.1557 | 290.5309
1317.5979 | 355.3852 | 292.0536 | 290.5537
1318.5979 | 355.2826 | 292.0785 | 290.5833
1319.5979 | 355.2579 | 292.3761 | 290.6111
1320.5979 | 355.1918 | 292.4557 | 290.6383
1321.5979 | 355.2556 | 292.535 | 290.6697
1322.5979 | 355.1963 | 292.6286 | 290.6993
1323.5979 | 355.2107 | 292.3801 | 290.7277
1324.5979 | 355.1844 | 292.425 | 290.7558
1325.5979 | 355.1954 | 292.4207 | 290.7847
1326.5979 | 355.2039 | 292.4084 | 290.8093
1327.5979 | 355.1029 | 292.5989 | 290.8416
1328.5979 | 355.026 | 292.5918 | 290.8587
1329.5979 | 354.9723 | 292.5499 | 290.8925
1330.5979 | 354.9335 | 292.4646 | 290.9293
1331.5979 | 355.0836 | 292.7554 | 290.957
1332.5979 | 355.1311 | 292.6419 | 290.9754
1333.5979 | 355.138 | 292.7501 | 290.9799
1334.5979 | 355.2681 | 292.7253 | 290.9829
1335.5979 | 355.331 | 292.7627 | 290.9982
1336.5979 | 355.3341 | 292.4727 | 291.0114
1337.5979 | 355.2602 | 292.3257 | 291.0348
1338.5979 | 355.2199 | 291.919 | 291.0472
1339.5979 | 355.2532 | 291.7865 | 291.0499
1340.5979 | 355.3096 | 291.6597 | 291.042
1341.5979 | 355.4034 | 291.0269 | 291.0294
1342.5979 | 355.5819 | 290.6556 | 290.9978
1343.5979 | 355.6154 | 290.6096 | 290.9712
1344.5979 | 355.5838 | 290.5137 | 290.9577
1345.5979 | 355.5508 | 290.6312 | 290.9442
1346.5979 | 355.5667 | 290.6972 | 290.9435
1347.5979 | 355.5514 | 290.9268 | 290.9493
1348.5979 | 355.5272 | 290.9866 | 290.933
1349.5979 | 355.6101 | 291.098 | 290.9209
1350.5979 | 355.7388 | 291.3397 | 290.8853
1351.5979 | 355.6935 | 291.4914 | 290.8873
1352.5979 | 355.8106 | 291.6545 | 290.8958
1353.5979 | 355.9461 | 291.9035 | 290.9182
1354.5979 | 356.0502 | 291.9357 | 290.9476
1355.5979 | 356.1496 | 292.151 | 290.9718
1356.5979 | 356.2631 | 292.2185 | 291.0014
1357.5979 | 356.3325 | 292.3321 | 291.0265
1358.5979 | 356.4861 | 292.4023 | 291.0503
1359.5979 | 356.4356 | 292.189 | 291.0706
1360.5979 | 356.4257 | 292.266 | 291.1001
1361.5979 | 356.4327 | 292.2586 | 291.1237
1362.5979 | 356.4436 | 292.3008 | 291.1426
1363.5979 | 356.502 | 292.4868 | 291.176
1364.5979 | 356.5642 | 292.5375 | 291.1896
1365.5979 | 356.4635 | 292.2853 | 291.2127
1366.5979 | 356.2903 | 292.0595 | 291.2496
1367.5979 | 356.1747 | 292.1682 | 291.2741
1368.5979 | 356.2843 | 292.3611 | 291.2793
1369.5979 | 356.2708 | 292.2362 | 291.2733
1370.5979 | 356.2583 | 291.959 | 291.2891
1371.5979 | 356.3651 | 291.6845 | 291.3054
1372.5979 | 356.3932 | 291.5634 | 291.3216
1373.5979 | 356.3697 | 291.7021 | 291.3322
1374.5979 | 356.2561 | 292.0059 | 291.3256
1375.5979 | 356.2583 | 292.2816 | 291.3209
1376.5979 | 356.2314 | 292.534 | 291.3162
1377.5979 | 356.2148 | 292.7336 | 291.3115
1378.5979 | 356.0778 | 292.8108 | 291.3073
1379.5979 | 355.9608 | 292.6421 | 291.308
1380.5979 | 355.8339 | 292.4668 | 291.3114
1381.5979 | 355.7826 | 292.5923 | 291.3274
1382.5979 | 355.7988 | 292.642 | 291.351
1383.5979 | 355.7592 | 292.6314 | 291.3707
1384.5979 | 355.7036 | 292.5952 | 291.3887
1385.5979 | 355.7195 | 292.8007 | 291.3903
1386.5979 | 355.8323 | 292.6532 | 291.38
1387.5979 | 355.8932 | 292.6207 | 291.3672
1388.5979 | 355.935 | 292.7888 | 291.3372
1389.5979 | 355.9975 | 292.8293 | 291.3316
1390.5979 | 356.0573 | 292.4548 | 291.3039
1391.5979 | 356.2257 | 292.2746 | 291.2735
1392.5979 | 356.4156 | 292.427 | 291.2329
1393.5979 | 356.5136 | 292.027 | 291.2028
1394.5979 | 356.4461 | 291.6555 | 291.1785
1395.5979 | 356.4489 | 291.4988 | 291.1437
1396.5979 | 356.4302 | 291.6911 | 291.1164
1397.5979 | 356.3283 | 291.9103 | 291.0818
1398.5979 | 356.3063 | 292.0215 | 291.0579
1399.5979 | 356.2948 | 292.2743 | 291.0219
1400.5979 | 356.2713 | 291.6807 | 291.0065
1401.5979 | 356.2714 | 291.7086 | 290.9934
1402.5979 | 356.2741 | 291.8399 | 290.9878
1403.5979 | 356.3863 | 291.9683 | 291.0028
1404.5979 | 356.6007 | 291.9869 | 291.0155
1405.5979 | 356.6366 | 291.991 | 291.0375
1406.5979 | 356.5276 | 292.1439 | 291.0558
1407.5979 | 356.4078 | 292.0981 | 291.0757
1408.5979 | 356.4421 | 292.2791 | 291.1031
1409.5979 | 356.4247 | 292.4424 | 291.1274
1410.5979 | 356.2222 | 292.6652 | 291.1388
1411.5979 | 356.2119 | 292.754 | 291.154
1412.5979 | 356.2522 | 292.8871 | 291.1795
1413.5979 | 356.2553 | 292.9083 | 291.2071
1414.5979 | 356.1855 | 292.8341 | 291.2475
1415.5979 | 356.2432 | 292.9311 | 291.2839
1416.5979 | 356.2732 | 293.098 | 291.3196
1417.5979 | 356.1561 | 293.0141 | 291.3561
1418.5979 | 356.0071 | 292.632 | 291.3985
1419.5979 | 355.9381 | 292.4675 | 291.4286
1420.5979 | 355.8853 | 292.4009 | 291.4529
1421.5979 | 355.8429 | 292.3376 | 291.4782
1422.5979 | 355.7345 | 292.5262 | 291.4827
1423.5979 | 355.6714 | 292.6193 | 291.4882
1424.5979 | 355.5375 | 292.594 | 291.5026
1425.5979 | 355.4248 | 292.4027 | 291.5069
1426.5979 | 355.3893 | 292.5914 | 291.5081
1427.5979 | 355.3531 | 292.8345 | 291.5118
1428.5979 | 355.3826 | 292.7041 | 291.523
1429.5979 | 355.4505 | 292.8508 | 291.5295
1430.5979 | 355.5286 | 292.566 | 291.5306
1431.5979 | 355.6734 | 292.6357 | 291.5381
1432.5979 | 355.6408 | 292.6695 | 291.5571
1433.5979 | 355.7681 | 292.9363 | 291.5803
1434.5979 | 355.893 | 292.8967 | 291.5944
1435.5979 | 355.7407 | 292.7519 | 291.6177
1436.5979 | 355.6996 | 292.7503 | 291.6507
1437.5979 | 355.685 | 292.6466 | 291.6644
1438.5979 | 355.6503 | 292.6136 | 291.68
1439.5979 | 355.6922 | 292.7816 | 291.6986
1440.5979 | 355.8265 | 292.9223 | 291.73
1441.5979 | 355.847 | 293.0583 | 291.7612
1442.5979 | 355.7962 | 292.6948 | 291.7783
1443.5979 | 355.5753 | 292.5761 | 291.798
1444.6135 | 355.5017 | 292.5706 | 291.7975
1445.5979 | 355.5435 | 292.5419 | 291.7954
1446.5979 | 355.4145 | 292.6397 | 291.7984
1447.5979 | 355.4143 | 292.4904 | 291.7867
1448.5979 | 355.4263 | 292.61 | 291.7754
1449.5979 | 355.4641 | 292.7061 | 291.7839
1450.5979 | 355.4814 | 292.282 | 291.781
1451.5979 | 355.4666 | 291.9559 | 291.7724
1452.5979 | 355.4865 | 292.2168 | 291.7712
1453.5979 | 355.5721 | 292.4716 | 291.7569
1454.5979 | 355.5454 | 292.6478 | 291.7469
1455.5979 | 355.6553 | 292.7668 | 291.7419
1456.5979 | 355.661 | 292.9 | 291.7382
1457.5979 | 355.6147 | 292.8479 | 291.7536
1458.5979 | 355.637 | 292.5659 | 291.7642
1459.5979 | 355.7567 | 292.307 | 291.774
1460.5979 | 355.7305 | 292.2412 | 291.7792
1461.5979 | 355.6512 | 292.3373 | 291.7685
1462.5979 | 355.6909 | 292.6522 | 291.7548
1463.5979 | 355.7998 | 292.8025 | 291.7476
1464.5979 | 355.8956 | 292.7686 | 291.7541
1465.5979 | 355.9864 | 292.7137 | 291.7767
1466.5979 | 355.9752 | 292.7888 | 291.796
1467.5979 | 355.9237 | 292.6307 | 291.8175
1468.5979 | 355.9489 | 292.4389 | 291.829
1469.5979 | 355.9186 | 292.2371 | 291.847
1470.5979 | 355.8054 | 292.1642 | 291.8752
1471.5979 | 355.8026 | 292.3641 | 291.8846
1472.5979 | 355.8287 | 292.4624 | 291.9024
1473.5979 | 355.8819 | 292.5673 | 291.9264
1474.6135 | 355.9498 | 292.508 | 291.9482
1475.5979 | 356.0125 | 292.1917 | 291.9786
1476.5979 | 356.0643 | 292.3187 | 292.0048
1477.5979 | 356.2546 | 292.4367 | 292.0384
1478.5979 | 356.3768 | 292.5425 | 292.0557
1479.5979 | 356.3164 | 292.7565 | 292.0709
1480.5979 | 356.2576 | 293.0747 | 292.0873
1481.5979 | 356.1815 | 293.1303 | 292.1092
1482.5979 | 356.1441 | 293.2811 | 292.1148
1483.5979 | 356.065 | 293.282 | 292.1088
1484.5979 | 356.0234 | 293.3925 | 292.1034
1485.5979 | 355.8866 | 293.3928 | 292.1071
1486.5979 | 355.7557 | 293.5113 | 292.1159
1487.5979 | 355.7064 | 293.5317 | 292.1282
1488.5979 | 355.7465 | 293.5087 | 292.1393
1489.5979 | 355.7725 | 293.3679 | 292.1673
1490.5979 | 355.779 | 293.2456 | 292.205
1491.5979 | 355.8263 | 293.2724 | 292.2253
1492.5979 | 355.8567 | 293.0774 | 292.2489
1493.5979 | 355.8773 | 293.1843 | 292.2726
1494.5979 | 355.9446 | 293.1428 | 292.3024
1495.5979 | 355.9172 | 293.1766 | 292.3201
1496.5979 | 355.915 | 293.4743 | 292.3418
1497.5979 | 355.8464 | 293.7052 | 292.3671
1498.5979 | 355.8544 | 293.9245 | 292.3842
1499.5979 | 355.8487 | 293.8419 | 292.4171
1500.5979 | 355.6929 | 293.8651 | 292.4399
1501.5979 | 355.5349 | 293.902 | 292.4747
1502.5979 | 355.4092 | 293.8167 | 292.4867
1503.5979 | 355.4711 | 293.7862 | 292.4908
1504.5979 | 355.5899 | 293.8879 | 292.4768
1505.5979 | 355.6354 | 293.92 | 292.4466
1506.5979 | 355.7698 | 293.6846 | 292.4103
1507.5979 | 355.742 | 293.4236 | 292.393
1508.5979 | 355.7032 | 293.577 | 292.3788
1509.5979 | 355.6782 | 293.8127 | 292.3405
1510.5979 | 355.6144 | 293.5544 | 292.3149
1511.5979 | 355.5232 | 293.4017 | 292.2763
1512.5979 | 355.5252 | 293.4894 | 292.2579
1513.5979 | 355.5179 | 293.2787 | 292.2496
1514.5979 | 355.4592 | 292.6352 | 292.2503
1515.5979 | 355.4536 | 292.3693 | 292.2595
1516.5979 | 355.5463 | 292.5023 | 292.2443
1517.5979 | 355.5482 | 292.6421 | 292.2393
1518.5979 | 355.4808 | 292.7035 | 292.2114
1519.5979 | 355.4709 | 292.8519 | 292.1832
1520.5979 | 355.6011 | 292.905 | 292.162
1521.5979 | 355.641 | 292.8675 | 292.1372
1522.5979 | 355.6222 | 292.2006 | 292.1047
1523.5979 | 355.5775 | 292.2559 | 292.0741
1524.5979 | 355.5971 | 292.039 | 292.056
1525.5979 | 355.7048 | 292.1397 | 292.0335
1526.5979 | 355.7533 | 291.9121 | 292.0096
1527.5979 | 355.7403 | 291.9932 | 291.9863
1528.5979 | 355.7292 | 292.0394 | 291.9586
1529.5979 | 355.6217 | 292.1601 | 291.9417
1530.5979 | 355.5956 | 292.4254 | 291.9259
1531.5979 | 355.5515 | 292.5317 | 291.9216
1532.5979 | 355.5372 | 292.7874 | 291.9129
1533.5979 | 355.4687 | 292.991 | 291.9244
1534.5979 | 355.5479 | 292.8313 | 291.9093
1535.5979 | 355.5155 | 292.6203 | 291.9021
1536.5979 | 355.5737 | 292.929 | 291.8862
1537.5979 | 355.7371 | 292.9339 | 291.8809
1538.5979 | 355.666 | 292.8269 | 291.8807
1539.5979 | 355.5752 | 292.8914 | 291.885
1540.5979 | 355.5632 | 292.799 | 291.8874
1541.5979 | 355.5882 | 292.8487 | 291.8866
1542.5979 | 355.6285 | 292.9847 | 291.9023
1543.5979 | 355.6207 | 292.9859 | 291.9269
1544.5979 | 355.7414 | 293.0458 | 291.9368
1545.5979 | 355.6967 | 293.1311 | 291.9533
1546.5979 | 355.6144 | 292.9789 | 291.9578
1547.5979 | 355.4769 | 292.8547 | 291.9599
1548.5979 | 355.4302 | 292.713 | 291.9342
1549.5979 | 355.3921 | 292.7953 | 291.8991
1550.5979 | 355.4056 | 292.9313 | 291.8635
1551.5979 | 355.4707 | 292.9997 | 291.8388
1552.5979 | 355.5893 | 293.0179 | 291.8143
1553.5979 | 355.6338 | 293.3735 | 291.8078
1554.5979 | 355.5129 | 293.533 | 291.8114
1555.5979 | 355.3988 | 293.7361 | 291.8181
1556.5979 | 355.4643 | 293.9199 | 291.8187
1557.5979 | 355.4429 | 294.0851 | 291.8307
1558.5979 | 355.4051 | 294.1008 | 291.8413
1559.5979 | 355.391 | 294.1343 | 291.8461
1560.5979 | 355.3293 | 294.1251 | 291.8545
1561.5979 | 355.1589 | 294.0252 | 291.8763
1562.5979 | 355.1576 | 294.1055 | 291.8952
1563.5979 | 355.2501 | 294.1998 | 291.9122
1564.5979 | 355.2842 | 293.9578 | 291.9392
1565.5979 | 355.3707 | 293.9412 | 291.9545
1566.5979 | 355.3694 | 293.6619 | 291.9796
1567.5979 | 355.3559 | 293.6655 | 292.0047
1568.5979 | 355.2775 | 293.8113 | 292.0325
1569.5979 | 355.2748 | 293.8578 | 292.0483
1570.5979 | 355.2005 | 293.8037 | 292.0503
1571.5979 | 355.1644 | 293.8867 | 292.0448
1572.5979 | 355.0691 | 294.0507 | 292.0539
1573.5979 | 354.9753 | 294.0283 | 292.0574
1574.5979 | 354.9469 | 293.9154 | 292.0698
1575.5979 | 354.9282 | 293.8883 | 292.0885
1576.5979 | 354.9452 | 293.4959 | 292.0924
1577.5979 | 354.9755 | 293.4683 | 292.092
1578.5979 | 355.0494 | 293.3302 | 292.0956
1579.5979 | 355.148 | 293.4159 | 292.0995
1580.5979 | 355.3018 | 293.3806 | 292.1092
1581.5979 | 355.4304 | 293.0312 | 292.1156
1582.5979 | 355.4074 | 292.7639 | 292.1228
1583.5979 | 355.3958 | 292.5167 | 292.123
1584.5979 | 355.561 | 292.3883 | 292.1159
1585.5979 | 355.6621 | 292.398 | 292.094
1586.5979 | 355.6963 | 292.1289 | 292.0638
1587.5979 | 355.7819 | 292.2467 | 292.0247
1588.5979 | 355.8428 | 292.3185 | 291.9843
1589.5979 | 355.8803 | 292.4059 | 291.9412
1590.5979 | 355.8623 | 292.5682 | 291.9176
1591.5979 | 355.8552 | 292.8161 | 291.9008
1592.5979 | 356.0147 | 292.6903 | 291.9004
1593.5979 | 356.1853 | 292.5294 | 291.9166
1594.5979 | 356.2431 | 292.2111 | 291.9242
1595.5979 | 356.1958 | 292.0521 | 291.9245
1596.5979 | 356.1163 | 292.0946 | 291.9368
1597.5979 | 356.0964 | 292.156 | 291.9373
1598.5979 | 355.9645 | 292.1544 | 291.9343
1599.5979 | 355.9763 | 292.2923 | 291.9417
1600.5979 | 356.0667 | 292.5337 | 291.9669
1601.5979 | 356.0903 | 292.3775 | 291.9806
1602.5979 | 356.0384 | 292.4508 | 291.9944
1603.5979 | 355.9569 | 292.4061 | 291.9974
1604.5979 | 355.9016 | 292.448 | 291.9988
1605.5979 | 355.7489 | 292.5398 | 291.9995
1606.5979 | 355.699 | 292.4914 | 292.0114
1607.5979 | 355.667 | 292.6466 | 292.0144
1608.5979 | 355.6588 | 292.7878 | 292.0101
1609.5979 | 355.5599 | 292.9354 | 291.9991
1610.5979 | 355.4904 | 293.1141 | 291.9729
1611.5979 | 355.4373 | 293.0757 | 291.9485
1612.5979 | 355.4016 | 293.0279 | 291.9321
1613.5979 | 355.3261 | 292.8215 | 291.9173
1614.5979 | 355.1534 | 292.5518 | 291.9125
1615.5979 | 355.1926 | 292.8057 | 291.9155
1616.5979 | 355.1792 | 292.9246 | 291.9224
1617.5979 | 355.1776 | 292.7747 | 291.9288
1618.5979 | 355.1239 | 292.8308 | 291.9467
1619.5979 | 354.9471 | 293.0563 | 291.9619
1620.5979 | 354.8891 | 293.3435 | 291.9863
1621.5979 | 354.9231 | 293.1983 | 292.0011
1622.5979 | 354.8997 | 293.2181 | 292.004
1623.5979 | 354.8712 | 293.1269 | 291.9878
1624.5979 | 354.8837 | 293.2743 | 291.9544
1625.5979 | 354.8488 | 293.2693 | 291.9069
1626.5979 | 354.8711 | 293.2778 | 291.876
1627.5979 | 354.8884 | 293.137 | 291.865
1628.5979 | 354.8815 | 293.2865 | 291.8658
1629.5979 | 355.0242 | 293.3272 | 291.8706
1630.5979 | 355.1203 | 293.4335 | 291.8768
1631.5979 | 355.1848 | 293.5009 | 291.8787
1632.5979 | 355.2453 | 293.4018 | 291.8809
1633.5979 | 355.2717 | 293.3905 | 291.8893
1634.5979 | 355.1739 | 293.5006 | 291.8806
1635.5979 | 355.1648 | 293.5032 | 291.8813
1636.5979 | 355.2213 | 293.5925 | 291.8675
1637.5979 | 355.3323 | 293.3462 | 291.8605
1638.5979 | 355.3851 | 293.1211 | 291.8525
1639.5979 | 355.3934 | 293.1722 | 291.8566
1640.5979 | 355.4395 | 293.3729 | 291.8706
1641.5979 | 355.5515 | 293.3285 | 291.8855
1642.5979 | 355.6694 | 293.2362 | 291.8976
1643.5979 | 355.5855 | 293.1749 | 291.9114
1644.5979 | 355.6149 | 293.3095 | 291.9387
1645.5979 | 355.6416 | 293.1955 | 291.9575
1646.5979 | 355.7485 | 293.3468 | 291.9771
1647.5979 | 355.8275 | 293.4359 | 292.0015
1648.5979 | 355.9384 | 293.1493 | 292.024
1649.5979 | 355.9648 | 293.2806 | 292.0564
1650.5979 | 355.9055 | 293.3577 | 292.0902
1651.5979 | 355.8978 | 293.437 | 292.1165
1652.5979 | 355.8304 | 293.3233 | 292.1425
1653.5979 | 355.8278 | 293.5586 | 292.1589
1654.5979 | 355.8512 | 293.514 | 292.168
1655.5979 | 355.8725 | 293.4191 | 292.1816
1656.5979 | 355.8752 | 293.3041 | 292.1871
1657.5979 | 355.8896 | 293.5008 | 292.1808
1658.5979 | 355.8325 | 293.5936 | 292.1848
1659.5979 | 355.7931 | 293.5359 | 292.2014
1660.5979 | 355.857 | 293.7242 | 292.2125
1661.5979 | 355.9508 | 293.8623 | 292.2219
1662.5979 | 355.9548 | 293.6316 | 292.2489
1663.5979 | 355.9944 | 293.5602 | 292.2725
1664.5979 | 356.0848 | 293.2253 | 292.3049
1665.5979 | 355.9968 | 293.1551 | 292.3372
1666.5979 | 356.0094 | 293.0664 | 292.3671
1667.5979 | 355.8895 | 293.4008 | 292.3957
1668.5979 | 355.8959 | 293.4668 | 292.4171
1669.5979 | 355.8603 | 293.6875 | 292.4211
1670.5979 | 355.851 | 293.734 | 292.4277
1671.5979 | 355.8665 | 293.7308 | 292.4192
1672.5979 | 355.7923 | 293.5155 | 292.4082
1673.5979 | 355.8556 | 293.3399 | 292.3863
1674.5979 | 355.892 | 293.36 | 292.3718
1675.5979 | 355.7932 | 293.3519 | 292.3683
1676.5979 | 355.6718 | 293.1894 | 292.3637
1677.5979 | 355.6302 | 292.6951 | 292.3656
1678.5979 | 355.559 | 292.6412 | 292.3686
1679.5979 | 355.5463 | 292.5185 | 292.3746
1680.5979 | 355.5597 | 292.4292 | 292.3785
1681.5979 | 355.4936 | 291.9249 | 292.3766
1682.5979 | 355.5333 | 291.6797 | 292.3607
1683.5979 | 355.5603 | 291.7352 | 292.3449
1684.5979 | 355.5593 | 291.6911 | 292.3348
1685.5979 | 355.6109 | 291.792 | 292.3169
1686.5979 | 355.6233 | 291.9205 | 292.3149
1687.5979 | 355.5733 | 292.2482 | 292.3183
1688.5979 | 355.6083 | 292.2561 | 292.3347
1689.5979 | 355.6769 | 292.4627 | 292.3543
1690.5979 | 355.6216 | 292.4613 | 292.3642
1691.5979 | 355.4799 | 292.5954 | 292.3749
1692.5979 | 355.4668 | 292.9065 | 292.3859
1693.5979 | 355.46 | 293.1468 | 292.3901
1694.5979 | 355.4945 | 293.1457 | 292.4115
1695.5979 | 355.5218 | 293.0779 | 292.4182
1696.5979 | 355.5039 | 293.1517 | 292.4298
1697.5979 | 355.4952 | 293.2504 | 292.4288
1698.5979 | 355.481 | 293.2007 | 292.4186
1699.5979 | 355.3215 | 293.1178 | 292.4072
1700.5979 | 355.2571 | 293.3094 | 292.3779
1701.5979 | 355.0909 | 293.1303 | 292.3408
1702.5979 | 355.1941 | 292.8933 | 292.302
1703.5979 | 355.2705 | 292.9179 | 292.2552
1704.5979 | 355.2801 | 292.968 | 292.2128
1705.5979 | 355.3492 | 293.1636 | 292.1845
1706.5979 | 355.4009 | 293.1972 | 292.1517
1707.5979 | 355.3136 | 293.3704 | 292.111
1708.5979 | 355.1935 | 293.3875 | 292.0758
1709.5979 | 355.056 | 293.6111 | 292.0425
1710.5979 | 355.0675 | 293.4372 | 292.0293
1711.5979 | 355.1072 | 293.4539 | 292.028
1712.5979 | 355.1294 | 293.259 | 292.0319
1713.5979 | 355.1524 | 293.2751 | 292.0452
1714.5979 | 355.0799 | 293.0288 | 292.066
1715.5979 | 354.9546 | 292.7455 | 292.0751
1716.5979 | 354.8534 | 292.4313 | 292.0805
1717.5979 | 354.8305 | 292.4512 | 292.0815
1718.5979 | 354.7747 | 292.1592 | 292.0662
1719.5979 | 354.783 | 292.2574 | 292.0569
1720.5979 | 354.839 | 292.3526 | 292.0343
1721.5979 | 354.8355 | 292.4958 | 292.034
1722.5979 | 354.8358 | 292.506 | 292.0367
1723.5979 | 354.8513 | 292.6597 | 292.0426
1724.5979 | 354.8185 | 292.5382 | 292.047
1725.5979 | 354.7163 | 292.5404 | 292.0337
1726.5979 | 354.8043 | 292.358 | 292.036
1727.5979 | 354.8617 | 292.6321 | 292.0214
1728.5979 | 354.9428 | 292.6686 | 292.0185
1729.5979 | 354.911 | 292.6511 | 291.9911
1730.5979 | 354.9706 | 292.7632 | 291.9851
1731.5979 | 354.9671 | 292.8557 | 291.9833
1732.5979 | 354.9081 | 292.9875 | 291.9996
1733.5979 | 354.9925 | 293.1323 | 292.0213
1734.5979 | 354.9968 | 292.9259 | 292.033
1735.5979 | 355.0051 | 292.94 | 292.0482
1736.5979 | 355.0191 | 293.0798 | 292.0652
1737.5979 | 355.1741 | 293.2659 | 292.0851
1738.5979 | 355.1419 | 293.2836 | 292.1053
1739.5979 | 355.2036 | 293.4455 | 292.128
1740.5979 | 355.197 | 293.7063 | 292.1115
1741.5979 | 355.215 | 293.6942 | 292.1008
1742.5979 | 355.264 | 293.7404 | 292.0923
1743.5979 | 355.2398 | 293.5601 | 292.0969
1744.5979 | 355.2606 | 293.1861 | 292.091
1745.5979 | 355.2811 | 292.7911 | 292.0967
1746.5979 | 355.3306 | 293.0731 | 292.1081
1747.5979 | 355.4263 | 293.2762 | 292.1212
1748.5979 | 355.5309 | 293.3348 | 292.1462
1749.5979 | 355.553 | 293.3275 | 292.1767
1750.5979 | 355.5221 | 293.459 | 292.2086
1751.5979 | 355.4116 | 293.5687 | 292.2303
1752.5979 | 355.3333 | 293.405 | 292.2545
1753.5979 | 355.2637 | 293.1241 | 292.268
1754.5979 | 355.126 | 292.905 | 292.3045
1755.5979 | 355.0835 | 292.9487 | 292.348
1756.5979 | 355.1962 | 293.0619 | 292.375
1757.5979 | 355.3521 | 293.1721 | 292.3994
1758.5979 | 355.3831 | 293.2308 | 292.4217
1759.5979 | 355.3578 | 293.2621 | 292.468
1760.5979 | 355.3128 | 293.3692 | 292.5076
1761.5979 | 355.4409 | 293.4266 | 292.5657
1762.5979 | 355.5205 | 293.4285 | 292.6112
1763.5979 | 355.5119 | 293.4797 | 292.6505
1764.5979 | 355.4226 | 293.6364 | 292.6764
1765.5979 | 355.4206 | 293.7888 | 292.6989
1766.5979 | 355.3838 | 293.7691 | 292.7172
1767.5979 | 355.5252 | 293.3823 | 292.7506
1768.5979 | 355.6359 | 293.3754 | 292.7663
1769.5979 | 355.6236 | 293.4155 | 292.7926
1770.5979 | 355.6061 | 293.4274 | 292.8132
1771.5979 | 355.6167 | 293.5521 | 292.8213
1772.5979 | 355.6668 | 293.4878 | 292.8354
1773.5979 | 355.6831 | 293.664 | 292.8341
1774.5979 | 355.6124 | 293.565 | 292.8367
1775.5979 | 355.5782 | 293.5822 | 292.8394
1776.5979 | 355.5568 | 293.082 | 292.8499
1777.5979 | 355.4447 | 293.1428 | 292.862
1778.5979 | 355.4513 | 293.3245 | 292.8672
1779.5979 | 355.4697 | 293.1957 | 292.8734
1780.5979 | 355.3493 | 292.9226 | 292.8864
1781.5979 | 355.2843 | 292.9146 | 292.9021
1782.5979 | 355.3254 | 292.8109 | 292.9156
1783.5979 | 355.3998 | 292.8015 | 292.9283
1784.5979 | 355.2576 | 293.0119 | 292.9388
1785.5979 | 355.1689 | 293.29 | 292.9267
1786.5979 | 355.082 | 293.5155 | 292.911
1787.5979 | 355.0431 | 293.6271 | 292.8892
1788.5979 | 355.0874 | 293.7909 | 292.852
1789.5979 | 355.2622 | 294.0052 | 292.8141
1790.5979 | 355.2912 | 294.0021 | 292.7582
1791.5979 | 355.2814 | 293.9664 | 292.7059
1792.5979 | 355.3089 | 294.049 | 292.687
1793.5979 | 355.232 | 294.263 | 292.6869
1794.5979 | 355.2233 | 294.3752 | 292.6786
1795.5979 | 355.2368 | 294.4259 | 292.6612
1796.5979 | 355.2178 | 294.4848 | 292.6509
1797.5979 | 355.2155 | 294.6045 | 292.648
1798.5979 | 355.1627 | 294.5393 | 292.6506
1799.5979 | 355.1721 | 294.523 | 292.6667
1800.5979 | 355.0878 | 294.5754 | 292.6742
1801.5979 | 354.9421 | 294.5755 | 292.687
1802.5979 | 354.7964 | 294.6059 | 292.7114
1803.5979 | 354.74 | 294.5252 | 292.7324
1804.5979 | 354.6477 | 294.3724 | 292.7542
1805.5979 | 354.676 | 294.6907 | 292.7642
1806.5979 | 354.6544 | 294.4684 | 292.7708
1807.5979 | 354.5764 | 294.5138 | 292.7793
1808.5979 | 354.5808 | 294.5072 | 292.7886
1809.5979 | 354.6717 | 294.1043 | 292.7959
1810.5979 | 354.6344 | 294.2041 | 292.8111
1811.5979 | 354.5768 | 294.3124 | 292.8245
1812.5979 | 354.5835 | 294.5199 | 292.8271
1813.5979 | 354.6551 | 294.397 | 292.8307
1814.5979 | 354.7692 | 294.2526 | 292.8334
1815.5979 | 354.8743 | 294.5385 | 292.8391
1816.5979 | 354.8768 | 294.5668 | 292.839
1817.5979 | 354.9545 | 294.7615 | 292.8409
1818.5979 | 354.9838 | 294.6394 | 292.8436
1819.5979 | 354.921 | 294.6623 | 292.8557
1820.5979 | 354.7614 | 294.5017 | 292.8677
1821.5979 | 354.7237 | 294.4289 | 292.867
1822.5979 | 354.7292 | 294.3717 | 292.8748
1823.5979 | 354.6222 | 294.3415 | 292.8871
1824.5979 | 354.7181 | 294.3863 | 292.8984
1825.5979 | 354.9152 | 294.2983 | 292.9111
1826.5979 | 355.0329 | 294.3528 | 292.9225
1827.5979 | 355.0959 | 294.3578 | 292.922
1828.5979 | 355.0963 | 294.4364 | 292.9177
1829.5979 | 355.028 | 294.4426 | 292.904
1830.5979 | 354.995 | 294.1706 | 292.8843
1831.5979 | 355.0785 | 294.0351 | 292.8714
1832.5979 | 354.9694 | 293.5127 | 292.8548
1833.5979 | 354.9258 | 292.8619 | 292.8373
1834.5979 | 354.7683 | 292.6953 | 292.8263
1835.5979 | 354.6999 | 292.6056 | 292.8164
1836.5979 | 354.7096 | 292.5931 | 292.8075
1837.5979 | 354.6906 | 292.7452 | 292.7884
1838.5979 | 354.7085 | 292.8222 | 292.7634
1839.5979 | 354.7256 | 292.9663 | 292.7427
1840.5979 | 354.7655 | 292.8089 | 292.7328
1841.5979 | 354.7706 | 292.9382 | 292.7263
1842.5979 | 354.8365 | 293.1923 | 292.7077
1843.5979 | 355.0111 | 293.5099 | 292.6857
1844.5979 | 355.112 | 293.4276 | 292.6659
1845.5979 | 355.2217 | 293.1668 | 292.6542
1846.5979 | 355.2414 | 293.2485 | 292.6419
1847.5979 | 355.099 | 293.1965 | 292.6295
1848.5979 | 355.1392 | 293.1872 | 292.6174
1849.5979 | 355.1842 | 293.2983 | 292.59
1850.5979 | 355.1704 | 293.2014 | 292.5729
1851.5979 | 355.2497 | 293.4312 | 292.5622
1852.5979 | 355.2507 | 293.6894 | 292.574
1853.5979 | 355.255 | 294.024 | 292.5714
1854.5979 | 355.2285 | 293.9272 | 292.5867
1855.5979 | 355.2007 | 293.781 | 292.6076
1856.5979 | 355.0821 | 293.8147 | 292.6369
1857.5979 | 355.1405 | 293.8905 | 292.665
1858.5979 | 355.1606 | 293.7517 | 292.6937
1859.5979 | 355.0864 | 293.8593 | 292.7311
1860.5979 | 355.0603 | 293.5964 | 292.7579
1861.5979 | 354.9899 | 293.8144 | 292.7632
1862.5979 | 354.8999 | 293.9339 | 292.7593
1863.5979 | 354.9571 | 293.5617 | 292.7458
1864.5979 | 354.9352 | 293.4332 | 292.7399
1865.5979 | 354.8695 | 293.4479 | 292.7468
1866.5979 | 354.9229 | 293.4514 | 292.7552
1867.5979 | 354.9467 | 293.5211 | 292.7764
1868.5979 | 355.0586 | 293.3808 | 292.7812
1869.5979 | 355.1192 | 293.4444 | 292.7947
1870.5979 | 355.0108 | 293.5122 | 292.8051
1871.5979 | 354.9957 | 293.4787 | 292.8219
1872.5979 | 354.9869 | 293.2824 | 292.8271
1873.5979 | 354.9659 | 293.3813 | 292.8372
1874.5979 | 355.091 | 293.5292 | 292.853
1875.5979 | 355.0968 | 293.521 | 292.8658
1876.5979 | 355.0377 | 293.646 | 292.8636
1877.5979 | 354.9845 | 293.2777 | 292.8553
1878.5979 | 355.0177 | 293.0637 | 292.8437
1879.5979 | 355.1455 | 292.8585 | 292.8334
1880.5979 | 355.2123 | 292.7708 | 292.8261
1881.5979 | 355.1967 | 292.4355 | 292.8222
1882.5979 | 355.1699 | 292.6861 | 292.8263
1883.5979 | 355.1443 | 292.7882 | 292.8304
1884.5979 | 355.1871 | 292.869 | 292.8282
1885.5979 | 355.1474 | 293.0459 | 292.8283
1886.5979 | 355.0605 | 293.0285 | 292.8237
1887.5979 | 355.0453 | 292.9898 | 292.801
1888.5979 | 355.1512 | 293.0101 | 292.7576
1889.5979 | 355.1963 | 293.1316 | 292.7141
1890.5979 | 355.301 | 293.2665 | 292.6894
1891.5979 | 355.3803 | 293.1158 | 292.6634
1892.5979 | 355.3004 | 293.0858 | 292.6402
1893.5979 | 355.3158 | 293.107 | 292.6161
1894.5979 | 355.2757 | 293.0408 | 292.5745
1895.5979 | 355.3082 | 292.971 | 292.5385
1896.5979 | 355.2219 | 292.788 | 292.4962
1897.5979 | 355.0705 | 292.8591 | 292.4429
1898.5979 | 355.1594 | 292.9178 | 292.4008
1899.5979 | 355.096 | 292.6598 | 292.375
1900.5979 | 355.0815 | 292.7296 | 292.3551
1901.5979 | 355.0699 | 292.781 | 292.3225
1902.5979 | 355.1679 | 292.8357 | 292.2921
1903.5979 | 355.1545 | 292.981 | 292.2694
1904.5979 | 355.1186 | 292.9296 | 292.2498
1905.5979 | 355.0793 | 292.8141 | 292.2233
1906.5979 | 355.0105 | 292.7104 | 292.1909
1907.5979 | 354.9801 | 292.3924 | 292.1657
1908.5979 | 354.9766 | 292.5228 | 292.1339
1909.5979 | 354.9183 | 292.5305 | 292.1086
1910.5979 | 355.0054 | 292.6512 | 292.0938
1911.5979 | 355.0487 | 292.8762 | 292.0635
1912.5979 | 355.0923 | 292.4416 | 292.0557
1913.5979 | 355.061 | 292.3661 | 292.036
1914.5979 | 354.9071 | 292.5889 | 292.0163
1915.5979 | 354.8213 | 292.4831 | 291.9934
1916.5979 | 354.8225 | 292.2411 | 291.9728
1917.5979 | 354.7436 | 292.4086 | 291.9383
1918.5979 | 354.7211 | 292.3524 | 291.9222
1919.5979 | 354.7915 | 292.4252 | 291.9041
1920.5979 | 354.744 | 292.4996 | 291.8974
1921.5979 | 354.7743 | 292.4225 | 291.892
1922.5979 | 354.8562 | 292.4421 | 291.8943
1923.5979 | 354.8892 | 292.6059 | 291.9
1924.5979 | 354.8528 | 292.7702 | 291.9023
1925.5979 | 354.7919 | 293.0392 | 291.9093
1926.5979 | 354.6785 | 292.8291 | 291.9223
1927.5979 | 354.6547 | 292.5757 | 291.9299
1928.5979 | 354.5667 | 292.4711 | 291.9279
1929.5979 | 354.4004 | 292.197 | 291.916
1930.5979 | 354.3667 | 292.252 | 291.8938
1931.5979 | 354.3211 | 292.4867 | 291.8905
1932.5979 | 354.266 | 292.5718 | 291.8917
1933.5979 | 354.4134 | 292.6433 | 291.8894
1934.5979 | 354.4892 | 292.605 | 291.8962
1935.5979 | 354.4446 | 292.098 | 291.9141
1936.5979 | 354.4061 | 292.1139 | 291.9198
1937.5979 | 354.2988 | 292.2757 | 291.9237
1938.5979 | 354.3404 | 292.4359 | 291.9347
1939.5979 | 354.4794 | 292.4545 | 291.9454
1940.5979 | 354.534 | 292.2076 | 291.9651
1941.5979 | 354.5047 | 292.0236 | 291.9769
1942.5979 | 354.4774 | 291.921 | 291.9889
1943.5979 | 354.54 | 292.227 | 292
1944.5979 | 354.5586 | 292.3769 | 292.0039
1945.5979 | 354.5471 | 292.5308 | 292.0047
1946.5979 | 354.5091 | 292.7206 | 291.9985
1947.5979 | 354.5237 | 292.5611 | 291.9914
1948.5979 | 354.5893 | 292.399 | 291.9988
1949.5979 | 354.6176 | 292.2628 | 292.0068
1950.5979 | 354.6344 | 292.154 | 292.0277
1951.5979 | 354.6395 | 292.2057 | 292.0522
1952.5979 | 354.6469 | 292.3435 | 292.0708
1953.5979 | 354.6632 | 292.4848 | 292.0893
1954.5979 | 354.6466 | 292.6354 | 292.1086
1955.5979 | 354.6334 | 292.7398 | 292.1229
1956.5979 | 354.56 | 292.8114 | 292.144
1957.5979 | 354.5003 | 292.3458 | 292.1732
1958.5979 | 354.5694 | 292.3198 | 292.192
1959.5979 | 354.5821 | 292.372 | 292.2066
1960.5979 | 354.6086 | 292.068 | 292.2098
1961.5979 | 354.6288 | 292.0964 | 292.2172
1962.5979 | 354.5025 | 292.1993 | 292.2068
1963.5979 | 354.4368 | 292.0728 | 292.2003
1964.5979 | 354.3872 | 291.916 | 292.1904
1965.5979 | 354.3985 | 292.1451 | 292.1732
1966.5979 | 354.4169 | 292.457 | 292.1682
1967.5979 | 354.3892 | 292.564 | 292.148
1968.5979 | 354.3813 | 292.5251 | 292.1295
1969.5979 | 354.4455 | 292.3436 | 292.115
1970.5979 | 354.4467 | 292.301 | 292.0869
1971.5979 | 354.5913 | 292.3903 | 292.0632
1972.5979 | 354.5417 | 292.4774 | 292.023
1973.5979 | 354.4942 | 292.5492 | 291.9784
1974.5979 | 354.5622 | 292.5719 | 291.9167
1975.5979 | 354.7111 | 292.2445 | 291.8429
1976.5979 | 354.7613 | 291.9684 | 291.7707
1977.5979 | 354.6673 | 291.9064 | 291.6989
1978.5979 | 354.6671 | 291.4245 | 291.6272
1979.5979 | 354.6574 | 291.145 | 291.5359
1980.5979 | 354.7394 | 291.2448 | 291.4569
1981.5979 | 354.7806 | 291.3842 | 291.3849
1982.5979 | 354.7975 | 291.3907 | 291.3257
1983.5979 | 354.7591 | 291.6099 | 291.2649
1984.5979 | 354.8933 | 291.6866 | 291.2168
1985.5979 | 354.9859 | 291.9069 | 291.1817
1986.5979 | 354.9685 | 291.7415 | 291.137
1987.5979 | 354.9565 | 291.6023 | 291.1077
1988.5979 | 355.0092 | 291.7492 | 291.062
1989.5979 | 355.0731 | 291.9789 | 291.036
1990.5979 | 355.1621 | 291.7605 | 291.0102
1991.5979 | 355.1954 | 291.7838 | 290.9858
1992.5979 | 355.2556 | 291.9636 | 290.9452
1993.5979 | 355.3906 | 292.0289 | 290.9093
1994.5979 | 355.4602 | 292.1913 | 290.8936
1995.5979 | 355.4199 | 292.1669 | 290.8916
1996.5979 | 355.4184 | 292.2146 | 290.9001
1997.5979 | 355.4146 | 292.4077 | 290.9138
1998.5979 | 355.4734 | 292.3443 | 290.9353
1999.5979 | 355.4681 | 292.2983 | 290.9506
2000.5979 | 355.4901 | 292.2921 | 290.9412
2001.5979 | 355.4769 | 292.5484 | 290.9328
2002.5979 | 355.5492 | 292.2974 | 290.9156
2003.5979 | 355.6145 | 292.051 | 290.9148
2004.5979 | 355.572 | 291.8841 | 290.9171
2005.5979 | 355.6042 | 291.5703 | 290.9295
2006.5979 | 355.8847 | 291.8137 | 290.9464
2007.5979 | 355.9074 | 291.9013 | 290.9651
2008.5979 | 355.9228 | 291.4348 | 290.9952
2009.5979 | 355.9752 | 291.3801 | 291.0249
2010.5979 | 355.9468 | 291.735 | 291.056
2011.5979 | 355.9725 | 292.0028 | 291.0892
2012.5979 | 355.9401 | 292.1895 | 291.1233
2013.5979 | 355.9565 | 292.4304 | 291.1677
2014.5979 | 356.1388 | 292.6091 | 291.2069
2015.5979 | 356.254 | 292.8543 | 291.2465
2016.5979 | 356.2201 | 292.9163 | 291.2846
2017.5979 | 356.1567 | 292.9687 | 291.3293
2018.5979 | 356.167 | 293.2244 | 291.3787
2019.5979 | 356.0967 | 293.3364 | 291.4331
2020.5979 | 356.1138 | 293.5218 | 291.4902
2021.5979 | 356.1954 | 293.5747 | 291.5459
2022.5979 | 356.2003 | 293.5895 | 291.5877
2023.5979 | 356.1982 | 293.5913 | 291.6276
2024.5979 | 356.1245 | 293.7313 | 291.6678
2025.5979 | 355.9872 | 293.724 | 291.6877
2026.5979 | 355.9551 | 293.8827 | 291.7012
2027.5979 | 355.9704 | 294.016 | 291.7179
2028.5979 | 355.9126 | 293.6997 | 291.743
2029.5979 | 355.9582 | 293.6971 | 291.7683
2030.5979 | 355.7706 | 293.8942 | 291.789
2031.5979 | 355.651 | 294.1922 | 291.8179
2032.5979 | 355.5092 | 294.3108 | 291.8556
2033.5979 | 355.4848 | 294.0651 | 291.8919
2034.5979 | 355.4873 | 294.0428 | 291.9299
2035.5979 | 355.3697 | 294.0181 | 291.9453
2036.5979 | 355.3742 | 293.822 | 291.9588
2037.5979 | 355.4181 | 293.8034 | 291.9575
2038.5979 | 355.3359 | 293.8554 | 291.9555
2039.5979 | 355.2535 | 293.8068 | 291.9613
2040.5979 | 355.2326 | 293.7035 | 291.9761
2041.5979 | 355.1724 | 293.27 | 291.9852
2042.5979 | 354.9962 | 292.9131 | 291.9874
2043.5979 | 354.8963 | 292.5141 | 291.9889
2044.5979 | 354.8932 | 292.473 | 292.0016
2045.5979 | 354.84 | 292.0723 | 292.0217
2046.5979 | 354.7236 | 292.2772 | 292.0333
2047.5979 | 354.6313 | 292.5984 | 292.0597
2048.5979 | 354.627 | 292.839 | 292.0833
2049.5979 | 354.5339 | 293.1705 | 292.1012
2050.5979 | 354.5528 | 293.0623 | 292.1205
2051.5979 | 354.6128 | 293.0379 | 292.1335
2052.5979 | 354.5204 | 293.2306 | 292.1519
2053.5979 | 354.2923 | 293.0773 | 292.1713
2054.5979 | 354.2672 | 293.2637 | 292.1806
2055.5979 | 354.2614 | 292.9071 | 292.1925
2056.5979 | 354.4013 | 292.7949 | 292.2165
2057.5979 | 354.5123 | 292.9971 | 292.231
2058.5979 | 354.4106 | 292.8838 | 292.2356
2059.5979 | 354.4464 | 292.8054 | 292.2264
2060.5979 | 354.3857 | 292.9371 | 292.2179
2061.5979 | 354.3003 | 292.9914 | 292.2103
2062.5979 | 354.3298 | 292.6661 | 292.206
2063.5979 | 354.5133 | 292.2445 | 292.1925
2064.5979 | 354.5898 | 292.1307 | 292.1754
2065.5979 | 354.6364 | 292.0713 | 292.148
2066.5979 | 354.6409 | 292.0572 | 292.1374
2067.5979 | 354.6461 | 292.2062 | 292.1192
2068.5979 | 354.691 | 292.4857 | 292.1003
2069.5979 | 354.7173 | 292.5499 | 292.0775
2070.5979 | 354.7319 | 292.1127 | 292.0519
2071.5979 | 354.7022 | 292.174 | 292.054
2072.5979 | 354.6305 | 292.2053 | 292.0525
2073.5979 | 354.5589 | 292.3386 | 292.0567
2074.5979 | 354.6564 | 292.3806 | 292.0699
2075.5979 | 354.6238 | 292.3514 | 292.0736
2076.5979 | 354.5743 | 292.4005 | 292.0868
2077.5979 | 354.5474 | 292.3391 | 292.1036
2078.5979 | 354.6343 | 292.5622 | 292.1259
2079.5979 | 354.606 | 292.9273 | 292.135
2080.5979 | 354.5553 | 293.1344 | 292.1384
2081.5979 | 354.593 | 293.291 | 292.1353
2082.5979 | 354.5656 | 293.4572 | 292.132
2083.5979 | 354.6157 | 293.4087 | 292.1492
2084.5979 | 354.6607 | 293.077 | 292.1647
2085.5979 | 354.6258 | 293.0215 | 292.1828
2086.5979 | 354.5459 | 293.1702 | 292.1918
2087.5979 | 354.3754 | 293.0434 | 292.1868
2088.5979 | 354.3206 | 292.8182 | 292.1856
2089.5979 | 354.3111 | 292.8994 | 292.1688
2090.5979 | 354.3895 | 292.9573 | 292.1437
2091.5979 | 354.3547 | 292.8489 | 292.1215
2092.5979 | 354.2422 | 292.2987 | 292.0971
2093.5979 | 354.1748 | 292.2485 | 292.072
2094.5979 | 354.2415 | 291.8459 | 292.0675
2095.5979 | 354.3915 | 291.4692 | 292.0406
2096.5979 | 354.6388 | 291.5855 | 292.0123
2097.5979 | 354.8283 | 291.6764 | 291.9897
2098.5979 | 354.901 | 291.8858 | 291.9708
2099.5979 | 354.9813 | 292.1728 | 291.9576
2100.5979 | 354.9901 | 292.3186 | 291.9642
2101.5979 | 355.0086 | 292.0005 | 291.9637
2102.5979 | 355.1031 | 291.9755 | 291.986
2103.5979 | 355.1346 | 292.0655 | 292.0066
2104.5979 | 355.213 | 292.3231 | 292.0241
2105.5979 | 355.15 | 292.585 | 292.0404
2106.5979 | 355.1064 | 292.7812 | 292.046
2107.5979 | 355.1681 | 292.8557 | 292.0527
2108.5979 | 355.1579 | 293.0325 | 292.0508
2109.5979 | 355.1265 | 292.7914 | 292.0675
2110.5979 | 355.1706 | 292.6678 | 292.07
2111.5979 | 355.2223 | 292.9005 | 292.0516
2112.5979 | 355.2387 | 293.1358 | 292.0257
2113.5979 | 355.358 | 293.3234 | 292.0097
2114.5979 | 355.4155 | 293.5592 | 292.0018
2115.5979 | 355.5122 | 293.7301 | 291.9835
2116.5979 | 355.5933 | 293.8024 | 291.9789
2117.5979 | 355.6655 | 293.6924 | 291.9654
2118.5979 | 355.6834 | 293.5491 | 291.9726
2119.5979 | 355.7105 | 293.6534 | 291.9958
2120.5979 | 355.7118 | 293.9069 | 292.016
2121.5979 | 355.5864 | 293.8671 | 292.0198
2122.5979 | 355.6685 | 294.0232 | 292.0187
2123.5979 | 355.6593 | 294.3361 | 292.0194
2124.5979 | 355.566 | 294.6415 | 292.0178
2125.5979 | 355.3952 | 294.7243 | 292.0118
2126.5979 | 355.2811 | 294.7692 | 292.0317
2127.5979 | 355.2517 | 294.6225 | 292.0366
2128.5979 | 355.1777 | 294.2716 | 292.0512
2129.5979 | 355.2117 | 294.1454 | 292.0384
2130.5979 | 355.2525 | 293.9465 | 292.0349
2131.5979 | 355.1299 | 293.9184 | 292.0103
2132.5979 | 355.1231 | 293.9908 | 291.9718
2133.5979 | 355.1339 | 293.6827 | 291.9388
2134.5979 | 355.1157 | 293.7527 | 291.9011
2135.5979 | 355.1701 | 293.4496 | 291.8864
2136.5979 | 355.1283 | 292.8986 | 291.8723
2137.5979 | 355.0624 | 292.3236 | 291.8623
2138.5979 | 354.9517 | 291.8116 | 291.8484
2139.5979 | 354.963 | 291.8228 | 291.8368
2140.5979 | 354.9896 | 291.7036 | 291.8091
2141.5979 | 355.0077 | 291.4928 | 291.7845
2142.5979 | 355.0858 | 291.2731 | 291.7731
2143.5979 | 355.1705 | 291.28 | 291.7514
2144.5979 | 355.1815 | 291.5263 | 291.7337
2145.5979 | 355.2973 | 291.7815 | 291.7016
2146.5979 | 355.304 | 291.9425 | 291.6677
2147.5979 | 355.2193 | 292.1285 | 291.6611
2148.5979 | 355.2003 | 292.3005 | 291.6638
2149.5979 | 355.2703 | 292.424 | 291.6575
2150.5979 | 355.3521 | 292.4859 | 291.6634
2151.5979 | 355.4119 | 292.4171 | 291.6645
2152.5979 | 355.4027 | 292.4084 | 291.6619
2153.5979 | 355.568 | 292.6435 | 291.6639
2154.5979 | 355.5763 | 292.7031 | 291.671
2155.5979 | 355.5025 | 292.4653 | 291.6861
2156.5979 | 355.3903 | 292.1202 | 291.7042
2157.5979 | 355.1829 | 291.7154 | 291.7142
2158.5979 | 355.1097 | 291.8037 | 291.7188
2159.5979 | 355.1397 | 291.246 | 291.7291
2160.5979 | 355.2396 | 291.1771 | 291.7359
2161.5979 | 355.2843 | 291.5816 | 291.755
2162.5979 | 355.3623 | 291.6833 | 291.7798
2163.5979 | 355.5078 | 291.8883 | 291.8072
2164.5979 | 355.7069 | 291.8578 | 291.8282
2165.5979 | 355.8 | 291.7079 | 291.8487
2166.5979 | 355.8182 | 291.7582 | 291.8761
2167.5979 | 355.8402 | 291.9329 | 291.9014
2168.5979 | 356.0367 | 292.1408 | 291.9173
2169.5979 | 355.9872 | 292.3467 | 291.9267
2170.5979 | 356.0914 | 292.3719 | 291.9009
2171.5979 | 356.0707 | 292.4562 | 291.8817
2172.5979 | 356.1635 | 292.7129 | 291.8704
2173.5979 | 356.2155 | 292.74 | 291.8756
2174.5979 | 356.1985 | 292.6643 | 291.8806
2175.5979 | 356.0791 | 292.8183 | 291.8921
2176.5979 | 355.9518 | 292.6391 | 291.9055
2177.5979 | 355.9138 | 292.8565 | 291.9267
2178.5979 | 355.8861 | 292.9754 | 291.9594
2179.5979 | 355.8381 | 293.0285 | 291.9984
2180.5979 | 355.682 | 293.0174 | 292.0498
2181.5979 | 355.6088 | 293.1065 | 292.1048
2182.5979 | 355.6334 | 293.0854 | 292.16
2183.5979 | 355.5666 | 292.9915 | 292.223
2184.5979 | 355.4272 | 293.3042 | 292.2802
2185.5979 | 355.4139 | 293.4802 | 292.3331
2186.5979 | 355.4885 | 293.5212 | 292.378
2187.5979 | 355.4726 | 293.4367 | 292.4141
2188.5979 | 355.5562 | 293.3331 | 292.4408
2189.5979 | 355.5647 | 293.3114 | 292.4647
2190.5979 | 355.4837 | 293.3341 | 292.4939
2191.5979 | 355.3959 | 293.1931 | 292.5168
2192.5979 | 355.3422 | 293.1774 | 292.5292
2193.5979 | 355.3151 | 293.4509 | 292.5349
2194.5979 | 355.2894 | 293.3282 | 292.5472
2195.5979 | 355.1624 | 293.5234 | 292.559
2196.5979 | 355.028 | 293.9342 | 292.5503
2197.5979 | 355.0087 | 294.0637 | 292.5279
2198.5979 | 355.0241 | 294.2012 | 292.5033
2199.5979 | 354.9766 | 294.2557 | 292.485
2200.5979 | 354.9005 | 294.1627 | 292.4499
2201.5979 | 354.8948 | 294.2374 | 292.4146
2202.5979 | 354.8864 | 294.2367 | 292.3954
2203.5979 | 354.8613 | 294.323 | 292.3667
2204.5979 | 354.7966 | 294.1885 | 292.3511
2205.5979 | 354.8943 | 294.1578 | 292.3377
2206.5979 | 354.9906 | 294.292 | 292.3272
2207.5979 | 355.0375 | 294.1744 | 292.3336
2208.5979 | 355.114 | 294.0569 | 292.3545
2209.5979 | 355.2364 | 293.6668 | 292.3666
2210.5979 | 355.3316 | 293.6981 | 292.3857
2211.5979 | 355.4267 | 293.8397 | 292.4013
2212.5979 | 355.4978 | 293.915 | 292.4097
2213.5979 | 355.5078 | 293.7675 | 292.4216
2214.5979 | 355.5812 | 293.7166 | 292.4259
2215.5979 | 355.7627 | 293.7803 | 292.4339
2216.5979 | 355.7746 | 293.8893 | 292.4493
2217.5979 | 355.8086 | 293.8399 | 292.4718
2218.5979 | 355.8242 | 293.8046 | 292.4974
2219.5979 | 355.9573 | 293.7938 | 292.5251
2220.5979 | 355.9255 | 293.666 | 292.5428
2221.5979 | 355.8382 | 293.8849 | 292.5697
2222.5979 | 355.7899 | 294.1094 | 292.5957
2223.5979 | 355.7957 | 294.077 | 292.6106
2224.5979 | 355.7505 | 294.036 | 292.6236
2225.5979 | 355.7156 | 293.8682 | 292.6226
2226.5979 | 355.6149 | 293.9153 | 292.6075
2227.5979 | 355.554 | 293.7771 | 292.5926
2228.5979 | 355.4776 | 293.3236 | 292.5816
2229.5979 | 355.5493 | 293.2377 | 292.5612
2230.5979 | 355.5786 | 293.1959 | 292.5464
2231.5979 | 355.6384 | 293.3502 | 292.5377
2232.5979 | 355.6783 | 293.2028 | 292.5298
2233.5979 | 355.7069 | 293.0739 | 292.5265
2234.5979 | 355.7536 | 293.2692 | 292.527
2235.5979 | 355.7127 | 293.55 | 292.5095
2236.5979 | 355.6488 | 293.7548 | 292.4732
2237.5979 | 355.5907 | 293.8041 | 292.4323
2238.5979 | 355.4803 | 293.8603 | 292.4035
2239.5979 | 355.4052 | 293.9299 | 292.3806
2240.5979 | 355.4063 | 294.0236 | 292.3566
2241.5979 | 355.5143 | 294.0377 | 292.3358
2242.5979 | 355.5514 | 293.9587 | 292.3188
2243.5979 | 355.5642 | 293.9599 | 292.3023
2244.5979 | 355.4618 | 293.9449 | 292.3061
2245.5979 | 355.386 | 293.905 | 292.3025
2246.5979 | 355.2865 | 294.0308 | 292.3123
2247.5979 | 355.268 | 293.9208 | 292.3297
2248.5979 | 355.3372 | 294.0074 | 292.3325
2249.5979 | 355.4058 | 294.1612 | 292.3369
2250.5979 | 355.4452 | 294.374 | 292.3365
2251.5979 | 355.4584 | 294.5072 | 292.3273
2252.5979 | 355.4081 | 294.488 | 292.316
2253.5979 | 355.4425 | 294.2287 | 292.3194
2254.5979 | 355.4968 | 293.8276 | 292.329
2255.5979 | 355.545 | 293.9369 | 292.3342
2256.5979 | 355.5498 | 293.6974 | 292.3361
2257.5979 | 355.5832 | 293.7525 | 292.3556
2258.5979 | 355.7392 | 293.6868 | 292.3736
2259.5979 | 355.7239 | 293.6656 | 292.4077
2260.5979 | 355.7916 | 293.8332 | 292.4446
2261.5979 | 355.8545 | 294.0104 | 292.4713
2262.5979 | 355.9888 | 294.159 | 292.5074
2263.5979 | 356.0618 | 294.2705 | 292.5342
2264.5979 | 356.0817 | 294.3163 | 292.5631
2265.5979 | 356.038 | 294.3299 | 292.6176
2266.5979 | 356.0935 | 294.6447 | 292.6497
2267.5979 | 356.1363 | 294.8561 | 292.6784
2268.5979 | 356.1821 | 294.9505 | 292.7185
2269.5979 | 356.1615 | 295.0031 | 292.7461
2270.5979 | 356.1443 | 294.7241 | 292.7815
2271.5979 | 356.1325 | 294.8109 | 292.7981
2272.5979 | 356.0975 | 294.8352 | 292.8078
2273.5979 | 355.9664 | 294.643 | 292.8209
2274.5979 | 355.8857 | 294.5114 | 292.8423
2275.5979 | 355.781 | 294.4158 | 292.8611
2276.5979 | 355.8269 | 294.2698 | 292.8517
2277.5979 | 355.73 | 294.3991 | 292.861
2278.5979 | 355.6358 | 294.48 | 292.8513
2279.5979 | 355.6617 | 294.5683 | 292.8642
2280.5979 | 355.6567 | 294.6336 | 292.8721
2281.5979 | 355.7375 | 294.5216 | 292.8841
2282.5979 | 355.7446 | 294.4458 | 292.8971
2283.5979 | 355.6985 | 294.4622 | 292.9031
2284.5979 | 355.6435 | 294.4625 | 292.9239
2285.5979 | 355.5396 | 294.1128 | 292.9114
2286.5979 | 355.3953 | 293.9094 | 292.891
2287.5979 | 355.3752 | 293.8333 | 292.8808
2288.5979 | 355.3479 | 293.9298 | 292.872
2289.5979 | 355.4205 | 293.6547 | 292.8518
2290.5979 | 355.3915 | 293.4231 | 292.8334
2291.5979 | 355.2885 | 293.4703 | 292.8125
2292.5979 | 355.1719 | 293.3691 | 292.7934
2293.5979 | 355.1396 | 293.2774 | 292.7782
2294.5979 | 355.1218 | 293.3662 | 292.7732
2295.5979 | 355.0504 | 293.2665 | 292.78
2296.5979 | 355.065 | 293.3462 | 292.7901
2297.5979 | 355.1789 | 293.4163 | 292.7961
2298.5979 | 355.2081 | 293.2841 | 292.8025
2299.5979 | 355.3575 | 293.3747 | 292.8048
2300.5979 | 355.4011 | 293.5267 | 292.8088
2301.5979 | 355.3871 | 293.7267 | 292.7946
2302.5979 | 355.3525 | 293.9271 | 292.7599
2303.5979 | 355.3242 | 293.6616 | 292.7318
2304.5979 | 355.213 | 293.6093 | 292.7123
2305.5979 | 355.1873 | 293.7284 | 292.7011
2306.5979 | 355.1576 | 293.8338 | 292.6749
2307.5979 | 355.166 | 293.92 | 292.6675
2308.5979 | 355.294 | 293.7894 | 292.6648
2309.5979 | 355.223 | 293.9153 | 292.6653
2310.5979 | 355.2573 | 294.0594 | 292.6626
2311.5979 | 355.3471 | 294.106 | 292.6742
2312.5979 | 355.3382 | 294.0595 | 292.6828
2313.5979 | 355.3201 | 293.9199 | 292.6711
2314.5979 | 355.3571 | 294.0429 | 292.6547
2315.5979 | 355.342 | 293.8707 | 292.6454
2316.5979 | 355.3846 | 293.8124 | 292.6516
2317.5979 | 355.3269 | 293.866 | 292.6379
2318.5979 | 355.2545 | 293.8079 | 292.6437
2319.5979 | 355.2829 | 293.8032 | 292.6546
2320.5979 | 355.2621 | 293.9159 | 292.6489
2321.5979 | 355.1724 | 293.7588 | 292.6399
2322.5979 | 355.1764 | 293.7654 | 292.6484
2323.5979 | 355.2486 | 293.8562 | 292.6551
2324.5979 | 355.2988 | 293.8878 | 292.663
2325.5979 | 355.3364 | 293.7608 | 292.6743
2326.5979 | 355.2474 | 293.8083 | 292.6911
2327.5979 | 355.2239 | 293.9867 | 292.7057
2328.5979 | 355.2221 | 294.0219 | 292.7307
2329.5979 | 355.2477 | 294.0243 | 292.7402
2330.5979 | 355.2148 | 293.8077 | 292.7655
2331.5979 | 355.1712 | 293.7237 | 292.7838
2332.5979 | 355.1953 | 293.8909 | 292.8192
2333.5979 | 355.1628 | 294.06 | 292.8477
2334.5979 | 355.0807 | 294.0893 | 292.8711
2335.5979 | 355.0101 | 294.0676 | 292.8938
2336.5979 | 354.8737 | 294.3949 | 292.9049
2337.5979 | 354.7362 | 294.6681 | 292.905
2338.5979 | 354.6644 | 294.8066 | 292.8991
2339.5979 | 354.5801 | 294.9506 | 292.8811
2340.5979 | 354.5606 | 294.9803 | 292.874
2341.5979 | 354.4417 | 294.8571 | 292.8763
2342.5979 | 354.3687 | 294.6486 | 292.8918
2343.5979 | 354.3562 | 294.6379 | 292.9032
2344.5979 | 354.3478 | 294.6512 | 292.9225
2345.5979 | 354.4291 | 294.5703 | 292.944
2346.5979 | 354.44 | 294.5226 | 292.937
2347.5979 | 354.4663 | 294.2808 | 292.9189
2348.5979 | 354.5047 | 294.2307 | 292.9065
2349.5979 | 354.5141 | 294.3924 | 292.8877
2350.5979 | 354.5378 | 293.9811 | 292.8741
2351.5979 | 354.6953 | 293.3929 | 292.8613
2352.5979 | 354.8193 | 293.2031 | 292.822
2353.5979 | 354.9943 | 293.0918 | 292.7568
2354.5979 | 355.0786 | 293.1165 | 292.683
2355.5979 | 355.0855 | 292.8872 | 292.6261
2356.5979 | 355.1009 | 292.8631 | 292.5789
2357.5979 | 355.2279 | 292.9632 | 292.5502
2358.5979 | 355.2045 | 293.0663 | 292.5281
2359.5979 | 355.167 | 292.8383 | 292.5094
2360.5979 | 355.1766 | 292.8088 | 292.5016
2361.5979 | 355.1901 | 292.6435 | 292.5035
2362.5979 | 355.2726 | 292.5711 | 292.4918
2363.5979 | 355.3245 | 292.6399 | 292.4877
2364.5979 | 355.3131 | 292.4582 | 292.4835
2365.5979 | 355.1721 | 292.6849 | 292.463
2366.5979 | 355.1595 | 292.5754 | 292.4426
2367.5979 | 355.1087 | 292.3426 | 292.4317
2368.5979 | 354.9749 | 292.4388 | 292.4069
2369.5979 | 354.9686 | 292.2687 | 292.3618
2370.5979 | 354.9871 | 292.4906 | 292.3099
2371.5979 | 354.9785 | 292.55 | 292.2375
2372.5979 | 354.9441 | 292.8001 | 292.1587
2373.5979 | 354.9424 | 292.9407 | 292.0835
2374.5979 | 355.0158 | 292.6741 | 291.996
2375.5979 | 355.0565 | 292.4747 | 291.9192
2376.5979 | 355.0405 | 292.3749 | 291.8464
2377.5979 | 355.0132 | 292.5269 | 291.7867
2378.5979 | 354.9968 | 292.7991 | 291.7262
2379.5979 | 355.127 | 293.0012 | 291.6532
2380.5979 | 355.1776 | 292.985 | 291.5947
2381.5979 | 355.2712 | 293.0036 | 291.5624
2382.5979 | 355.3607 | 293.3296 | 291.529
2383.5979 | 355.4168 | 293.4986 | 291.5025
2384.5979 | 355.5644 | 293.4805 | 291.4876
2385.5979 | 355.7611 | 293.4552 | 291.4741
2386.5979 | 355.8388 | 293.0872 | 291.4788
2387.5979 | 355.7912 | 292.5479 | 291.503
2388.5979 | 355.9266 | 292.5567 | 291.5333
2389.5979 | 356.0481 | 292.676 | 291.5714
2390.5979 | 356.0831 | 292.7968 | 291.6138
2391.5979 | 356.2225 | 292.8143 | 291.6618
2392.5979 | 356.2781 | 292.9842 | 291.7116
2393.5979 | 356.2396 | 293.0688 | 291.7612
2394.5979 | 356.2157 | 293.3537 | 291.8183
2395.5979 | 356.1138 | 293.7741 | 291.8425
2396.5979 | 356.047 | 294.0233 | 291.8613
2397.5979 | 355.8492 | 294.1937 | 291.8704
2398.5979 | 355.8214 | 294.1613 | 291.8711
2399.5979 | 355.9661 | 293.969 | 291.859
2400.5979 | 356.0161 | 293.7319 | 291.8395
2401.5979 | 355.8913 | 293.6783 | 291.8382
2402.5979 | 355.9257 | 293.8554 | 291.831
2403.5979 | 355.8877 | 294.0001 | 291.8434
2404.5979 | 355.8321 | 293.879 | 291.8509
2405.5979 | 355.8017 | 293.9502 | 291.8587
2406.5979 | 355.792 | 293.9748 | 291.8655
2407.5979 | 355.7011 | 293.9148 | 291.8581
2408.5979 | 355.6366 | 293.8008 | 291.8609
2409.5979 | 355.5003 | 293.7921 | 291.8633
2410.5979 | 355.4996 | 293.6956 | 291.879
2411.5979 | 355.4156 | 293.766 | 291.9013
2412.5979 | 355.2302 | 293.9099 | 291.9212
2413.5979 | 355.1947 | 294.0906 | 291.9424
2414.5979 | 355.2445 | 293.9188 | 291.9724
2415.5979 | 355.2388 | 293.7134 | 292.0085
2416.5979 | 355.3116 | 293.9237 | 292.0407
2417.5979 | 355.301 | 293.9861 | 292.0748
2418.5979 | 355.1272 | 294.017 | 292.1198
2419.5979 | 355.147 | 293.7243 | 292.1606
2420.5979 | 355.1524 | 293.8789 | 292.1906
2421.5979 | 355.0947 | 293.2545 | 292.2134
2422.5979 | 355.0382 | 293.3273 | 292.2434
2423.5979 | 355.1104 | 293.5445 | 292.2747
2424.5979 | 355.1464 | 293.6648 | 292.314
2425.5979 | 355.0903 | 293.6959 | 292.3589
2426.5979 | 355.1582 | 293.8583 | 292.3976
2427.5979 | 355.2118 | 293.8789 | 292.4398
2428.5979 | 355.2065 | 293.922 | 292.4665
2429.5979 | 355.2259 | 294.0364 | 292.4759
2430.5979 | 355.2106 | 294.3081 | 292.4719
2431.5979 | 355.0898 | 294.3513 | 292.4623
2432.5979 | 355.181 | 294.4609 | 292.4563
2433.5979 | 355.0991 | 294.7264 | 292.4626
2434.5979 | 355.1335 | 294.7759 | 292.4743
2435.5979 | 355.0927 | 294.7214 | 292.4873
2436.5979 | 355.1019 | 294.7422 | 292.5093
2437.5979 | 355.1949 | 294.8453 | 292.5276
2438.5979 | 355.1306 | 295.0472 | 292.5491
2439.5979 | 355.2208 | 295.2004 | 292.5539
2440.5979 | 355.2238 | 295.0488 | 292.5512
2441.5979 | 355.1282 | 294.8026 | 292.557
2442.5979 | 355.0952 | 294.7451 | 292.5751
2443.5979 | 355.1638 | 294.4877 | 292.6033
2444.5979 | 355.2803 | 294.4793 | 292.6175
2445.5979 | 355.2753 | 294.6094 | 292.6109
2446.5979 | 355.2277 | 294.5903 | 292.6059
2447.5979 | 355.1486 | 294.675 | 292.6046
2448.5979 | 355.1826 | 294.6428 | 292.5684
2449.5979 | 355.2032 | 294.5261 | 292.5404
2450.5979 | 355.1602 | 293.9068 | 292.4846
2451.5979 | 355.1216 | 293.9077 | 292.4447
2452.5979 | 355.1897 | 293.9094 | 292.3873
2453.5979 | 355.283 | 294.0988 | 292.3093
2454.5979 | 355.4192 | 294.1483 | 292.2389
2455.5979 | 355.5167 | 294.2796 | 292.1778
2456.5979 | 355.5669 | 294.3614 | 292.1277
2457.5979 | 355.5103 | 294.1508 | 292.092
2458.5979 | 355.5145 | 294.214 | 292.0482
2459.5979 | 355.6187 | 294.1286 | 292.0033
2460.5979 | 355.7909 | 294.0726 | 291.9676
2461.5979 | 355.8506 | 293.9753 | 291.9066
2462.5979 | 355.9067 | 293.919 | 291.8349
2463.5979 | 356.0204 | 293.9345 | 291.783
2464.5979 | 356.1729 | 293.8193 | 291.727
2465.5979 | 356.3067 | 293.8959 | 291.6883
2466.5979 | 356.4212 | 293.8432 | 291.6452
2467.5979 | 356.6605 | 293.9698 | 291.6193
2468.5979 | 356.7345 | 294.2522 | 291.5884
2469.5979 | 356.7661 | 294.1735 | 291.5681
2470.5979 | 356.7071 | 293.8916 | 291.5594
2471.5979 | 356.6014 | 293.8013 | 291.5562
2472.5979 | 356.5918 | 293.6113 | 291.5869
2473.5979 | 356.5017 | 293.7606 | 291.6136
2474.5979 | 356.4423 | 293.8278 | 291.6564
2475.5979 | 356.4603 | 293.8505 | 291.6916
2476.5979 | 356.5337 | 293.8166 | 291.7135
2477.5979 | 356.4634 | 293.5549 | 291.7295
2478.5979 | 356.4349 | 293.0251 | 291.7371
2479.5979 | 356.4286 | 292.1442 | 291.7418
2480.5979 | 356.3796 | 291.6155 | 291.7475
2481.5979 | 356.4182 | 291.6222 | 291.7229
2482.5979 | 356.4555 | 291.93 | 291.6787
2483.5979 | 356.4588 | 292.2173 | 291.6212
2484.5979 | 356.5509 | 292.4197 | 291.5939
2485.5979 | 356.4596 | 292.6608 | 291.5719
2486.5979 | 356.4314 | 292.8836 | 291.563
2487.5979 | 356.2998 | 292.9722 | 291.5577
2488.5979 | 356.1695 | 293.2744 | 291.5644
2489.5979 | 356.0656 | 293.3729 | 291.5799
2490.5979 | 355.8605 | 293.4278 | 291.6049
2491.5979 | 355.7664 | 293.3217 | 291.6311
2492.5979 | 355.6594 | 293.0485 | 291.6489
2493.5979 | 355.6482 | 292.8078 | 291.6544
2494.5979 | 355.598 | 293 | 291.6344
2495.5979 | 355.6045 | 292.8551 | 291.6193
2496.5979 | 355.4736 | 293.0669 | 291.5881
2497.5979 | 355.4655 | 293.3292 | 291.5689
2498.5979 | 355.4239 | 293.2581 | 291.5582
2499.5979 | 355.5052 | 293.2001 | 291.5484
2500.5979 | 355.5502 | 293.0047 | 291.5536
2501.5979 | 355.4486 | 292.6814 | 291.5576
2502.5979 | 355.4772 | 292.8008 | 291.5676
2503.5979 | 355.4866 | 292.6081 | 291.5718
2504.5979 | 355.4767 | 292.3494 | 291.5817
2505.5979 | 355.4481 | 292.023 | 291.5814
2506.5979 | 355.3984 | 292.26 | 291.5848
2507.5979 | 355.2575 | 292.4443 | 291.583
2508.5979 | 355.178 | 292.6499 | 291.5857
2509.5979 | 355.1431 | 292.8218 | 291.5906
2510.5979 | 355.2101 | 292.9824 | 291.5972
2511.5979 | 355.1484 | 293.2572 | 291.609
2512.5979 | 355.0821 | 293.4576 | 291.6402
2513.5979 | 354.936 | 293.4753 | 291.6821
2514.5979 | 354.8705 | 293.2979 | 291.7247
2515.5979 | 354.8923 | 293.4022 | 291.7649
2516.5979 | 354.8827 | 293.7673 | 291.7956
2517.5979 | 354.982 | 293.8448 | 291.8171
2518.5979 | 355.1078 | 293.7531 | 291.8392
2519.5979 | 355.1095 | 293.6647 | 291.8733
2520.5979 | 355.0901 | 293.6593 | 291.8983
2521.5979 | 355.0062 | 293.577 | 291.9394
2522.5979 | 354.8668 | 293.5529 | 291.9785
2523.5979 | 354.8753 | 293.7518 | 291.9994
2524.5979 | 354.8662 | 293.9964 | 292.0021
2525.5979 | 354.9439 | 293.8217 | 291.9815
2526.5979 | 355.023 | 293.8705 | 291.9706
2527.5979 | 354.9919 | 293.5255 | 291.9879
2528.5979 | 354.9261 | 293.5553 | 292.0164
2529.5979 | 354.7708 | 293.6139 | 292.0614
2530.5979 | 354.7635 | 293.788 | 292.1007
2531.5979 | 354.7844 | 293.6856 | 292.15
2532.5979 | 354.7031 | 293.3689 | 292.1821
2533.5979 | 354.6415 | 292.9626 | 292.2092
2534.5979 | 354.54 | 292.899 | 292.227
2535.5979 | 354.5526 | 292.877 | 292.2431
2536.5979 | 354.5927 | 292.6496 | 292.2563
2537.5979 | 354.5875 | 292.683 | 292.278
2538.5979 | 354.5176 | 292.6164 | 292.2919
2539.5979 | 354.4461 | 292.7386 | 292.2958
2540.5979 | 354.4624 | 292.3941 | 292.2914
2541.5979 | 354.4461 | 292.04 | 292.2959
2542.5979 | 354.4788 | 292.2499 | 292.2754
2543.5979 | 354.5638 | 291.9115 | 292.2523
2544.5979 | 354.6012 | 291.8196 | 292.2318
2545.5979 | 354.618 | 291.9669 | 292.1916
2546.5979 | 354.5814 | 291.9422 | 292.1391
2547.5979 | 354.6125 | 292.0057 | 292.0746
2548.5979 | 354.6628 | 292.1482 | 292.0178
2549.5979 | 354.6544 | 292.403 | 291.9668
2550.5979 | 354.7287 | 292.5652 | 291.9365
2551.5979 | 354.6714 | 292.5318 | 291.9067
2552.5979 | 354.7261 | 292.5295 | 291.876
2553.5979 | 354.7543 | 292.4124 | 291.8124
2554.5979 | 354.7568 | 292.4838 | 291.7692
2555.5979 | 354.8129 | 292.3371 | 291.7514
2556.5979 | 354.8645 | 292.266 | 291.7253
2557.5979 | 354.9909 | 292.4009 | 291.7177
2558.5979 | 354.9424 | 292.6742 | 291.7166
2559.5979 | 355.0642 | 292.9188 | 291.7343
2560.5979 | 355.1703 | 293.0803 | 291.7704
2561.5979 | 355.1528 | 292.9358 | 291.803
2562.5979 | 355.2444 | 292.9346 | 291.8329
2563.5979 | 355.2353 | 292.9066 | 291.8448
2564.5979 | 355.2763 | 292.6818 | 291.869
2565.5979 | 355.2741 | 292.4766 | 291.8718
2566.5979 | 355.4103 | 292.3014 | 291.8495
2567.5979 | 355.364 | 292.4204 | 291.8133
2568.5979 | 355.3481 | 292.6278 | 291.7769
2569.5979 | 355.4215 | 292.804 | 291.7265
2570.5979 | 355.376 | 292.7208 | 291.6875
2571.5979 | 355.4618 | 292.8015 | 291.6621
2572.5979 | 355.5077 | 292.9257 | 291.6422
2573.5979 | 355.5438 | 292.5873 | 291.6338
2574.5979 | 355.4822 | 292.0424 | 291.6442
2575.5979 | 355.4943 | 292.1969 | 291.6509
2576.5979 | 355.5357 | 292.1935 | 291.6698
2577.5979 | 355.5866 | 292.124 | 291.652
2578.5979 | 355.6631 | 292.2908 | 291.67
2579.5979 | 355.6233 | 292.4891 | 291.6765
2580.5979 | 355.3994 | 292.7792 | 291.6837
2581.5979 | 355.3108 | 293.1771 | 291.7099
2582.5979 | 355.449 | 293.5015 | 291.7186
2583.5979 | 355.5268 | 293.4043 | 291.7368
2584.5979 | 355.5556 | 293.3213 | 291.7506
2585.5979 | 355.6097 | 292.8978 | 291.774
2586.5979 | 355.596 | 292.895 | 291.7937
2587.5979 | 355.4472 | 292.983 | 291.775
2588.5979 | 355.4707 | 292.2991 | 291.7572
2589.5979 | 355.6049 | 292.0079 | 291.7501
2590.5979 | 355.7697 | 291.5982 | 291.7533
2591.5979 | 355.8294 | 291.6049 | 291.7576
2592.5979 | 355.7711 | 291.8412 | 291.7749
2593.5979 | 355.7735 | 292.1537 | 291.7995
2594.5979 | 355.8186 | 292.2352 | 291.8276
2595.5979 | 355.827 | 292.0083 | 291.8571
2596.5979 | 355.8753 | 291.8925 | 291.8739
2597.5979 | 355.9256 | 291.9553 | 291.8726
2598.5979 | 355.8854 | 292.1567 | 291.867
2599.5979 | 355.8357 | 292.1021 | 291.8728
2600.5979 | 355.7924 | 292.0196 | 291.8898
2601.5979 | 355.8524 | 291.6684 | 291.8908
2602.5979 | 355.9677 | 291.5467 | 291.9022
2603.5979 | 355.9322 | 291.3044 | 291.9174
2604.5979 | 355.8789 | 291.5446 | 291.9241
2605.5979 | 355.9438 | 291.586 | 291.9293
2606.5979 | 355.9744 | 291.2552 | 291.9166
2607.5979 | 355.8818 | 291.1569 | 291.9018
2608.5979 | 355.864 | 291.2642 | 291.8792
2609.5979 | 355.8605 | 291.4939 | 291.8594
2610.5979 | 355.8004 | 291.4845 | 291.85
2611.5979 | 355.7646 | 291.6495 | 291.8639
2612.5979 | 355.7626 | 291.6576 | 291.8743