## Test Conditions
DESIREE-FIRE Test Number 34 - Circuit Simulator Data Only
Test Date: | 2009-08-11
DCSim DAQ Start Time | 11:03
DCSim Time for Synchronization | 11:32
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 11:30
Fire Time | 11:34
Offset | 0:30 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1830 | seconds
Heat Source Offset | 0:04 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 214 | seconds
Heat Source Stop Time | 12:04
Test Duration | 0:30 | hour:minutes:seconds
| 1830 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4, TC25 in the Temperature Data File
SOV 2 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the top and bottom of the conduit, respectively. Channel 5 represents the cable temperature within the conduit. | Channel 4, TC25 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.20312 | 123.349 | -66.7511 | 56.282 | 0.0018314 | -0.00092939 | 0.00082041 | 0.066481 | -0.00034394 | 0.064078 | -0.001755 | 0.00025007 | 0.00046581 | 0.062084 | 0.0037457 | 0.06356 | -66.7885 | 0.0243 | -66.7506 | 56.2518 | 55.9731 | 56.2527 | -66.8284 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3214 | 55.8438 | -67.0195 | -0.077257 | -0.030204 | -0.037376 | 0.000516 | 0.077773 | -0.30891 | -0.029303 | -0.26836 | -0.12013 | -0.028337 | -0.058263 | 0.2101 | 0.039317 | -0.43823 | 123.0029 | 122.7242 | 123.0038 | 66.7754 | -123.1104 | 122.913 | 123.0725 | 122.5949 | 66.7789 | -123.3015
0.79688 | 123.3032 | -66.7831 | 56.3232 | -0.0057996 | -0.00092939 | 0.00060681 | 0.066481 | -0.00034394 | 0.064505 | -0.001755 | 0.00025007 | 0.00025221 | 0.062298 | 0.0041731 | 0.064201 | -66.7931 | 0.028878 | -66.7552 | 56.2381 | 55.9777 | 56.2253 | -66.8238 | -66.7886 | 0.023253 | -66.8094 | 56.1528 | 56.3214 | 55.798 | -67.0286 | -0.040635 | -0.085138 | -0.009911 | 0.027981 | 0.068616 | -0.34553 | -0.097974 | -0.24547 | -0.17048 | -0.005451 | -0.02622 | 0.21925 | -0.001882 | -0.52522 | 123.0212 | 122.7609 | 123.0084 | 66.812 | -123.147 | 122.9359 | 123.1045 | 122.5812 | 66.8064 | -123.3519
1.7969 | 123.3444 | -66.7648 | 56.2912 | -0.013431 | -0.0011432 | 0.0010342 | 0.066695 | -0.00034394 | 0.064291 | -0.0093855 | 0.00025007 | 3.8406e-05 | 0.062084 | 0.0041731 | 0.063987 | -66.7839 | 0.033457 | -66.7689 | 56.2473 | 55.9869 | 56.2161 | -66.723 | -66.7794 | 0.023253 | -66.8139 | 56.1665 | 56.3076 | 55.766 | -67.0195 | 0.041791 | -0.043939 | -0.019064 | -0.004064 | -0.045855 | -0.30433 | -0.075088 | -0.25463 | -0.1247 | -0.014604 | -0.049109 | 0.20552 | 0.016425 | -0.52523 | 123.0121 | 122.7517 | 122.9809 | 66.7983 | -123.0142 | 122.9313 | 123.0725 | 122.5308 | 66.7881 | -123.3107
2.7969 | 123.3078 | -66.7831 | 56.2958 | -0.021062 | -0.00092939 | 0.00060681 | 0.066695 | -0.00055774 | 0.064078 | -0.001755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0039593 | 0.063773 | -66.7885 | 0.0243 | -66.7597 | 56.2335 | 56.0143 | 56.2482 | -66.8467 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3214 | 55.885 | -67.0195 | -0.06353 | -0.062251 | -0.005333 | 0.023402 | 0.086932 | -0.28143 | -0.047615 | -0.23632 | -0.13386 | 0.003706 | -0.02622 | 0.2101 | 0.025584 | -0.41076 | 123.0167 | 122.7975 | 123.0313 | 66.8074 | -123.1424 | 122.9451 | 123.1045 | 122.6682 | 66.811 | -123.3152
3.7969 | 123.3582 | -66.7465 | 56.2958 | 0.0018314 | -0.0011432 | 0.00082041 | 0.066481 | -0.00077134 | 0.063864 | 0.0058755 | 0.00025007 | 0.00025221 | 0.062511 | 0.0039593 | 0.063773 | -66.7931 | 0.0243 | -66.7552 | 56.2473 | 55.9548 | 56.2482 | -66.8467 | -66.7794 | 0.027831 | -66.8139 | 56.1619 | 56.3122 | 55.7706 | -67.0195 | -0.10015 | -0.048516 | -0.046532 | -0.00864 | 0.091511 | -0.34096 | -0.047615 | -0.27294 | -0.13386 | -0.032915 | -0.06742 | 0.20552 | 0.016427 | -0.52522 | 122.9938 | 122.7013 | 122.9947 | 66.7708 | -123.1424 | 122.9084 | 123.0587 | 122.5171 | 66.7744 | -123.3152
4.7969 | 123.3398 | -66.7511 | 56.2729 | -0.013431 | -0.00071579 | 0.00060681 | 0.066481 | -0.00055774 | 0.064078 | -0.017016 | 0.00025007 | 0.00046581 | 0.062298 | 0.0041731 | 0.063987 | -66.7931 | 0.028878 | -66.746 | 56.2427 | 55.9823 | 56.2527 | -66.8421 | -66.7794 | 0.03241 | -66.8139 | 56.1619 | 56.3168 | 55.8118 | -67.0103 | -0.090994 | -0.030206 | -0.041954 | 0.005094 | 0.096088 | -0.2906 | -0.020148 | -0.2592 | -0.11097 | -0.028337 | -0.062842 | 0.19636 | 0.043894 | -0.46113 | 122.9938 | 122.7334 | 123.0038 | 66.78 | -123.115 | 122.913 | 123.0679 | 122.5629 | 66.7835 | -123.2832
5.7969 | 123.2117 | -66.806 | 56.337 | -0.013431 | -0.00050219 | 0.00060681 | 0.066481 | -0.00077134 | 0.064078 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.062298 | 0.0037457 | 0.063987 | -66.7931 | 0.028878 | -66.7552 | 56.2381 | 56.0418 | 56.239 | -66.8329 | -66.784 | 0.027831 | -66.8139 | 56.1619 | 56.3168 | 55.766 | -67.0286 | -0.026905 | -0.098871 | 0.012977 | 0.050869 | 0.077774 | -0.29516 | -0.097971 | -0.22259 | -0.17506 | 0.022016 | -0.007911 | 0.21467 | -0.020193 | -0.571 | 123.0441 | 122.8478 | 123.045 | 66.8349 | -123.1699 | 122.9679 | 123.1228 | 122.572 | 66.8339 | -123.3656
6.7969 | 123.3261 | -66.7557 | 56.2958 | 0.0018314 | -0.00092939 | 0.00060681 | 0.066695 | -0.00055774 | 0.064291 | -0.001755 | 0.00025007 | 0.00046581 | 0.062725 | 0.0041731 | 0.063987 | -66.7885 | 0.0243 | -66.7506 | 56.2427 | 55.964 | 56.2527 | -66.778 | -66.784 | 0.03241 | -66.8139 | 56.1573 | 56.3214 | 55.798 | -67.024 | -0.022312 | -0.053094 | -0.032799 | 0.005093 | 0.027405 | -0.3318 | -0.043036 | -0.26836 | -0.13844 | -0.028338 | -0.058265 | 0.2101 | 0.025584 | -0.49775 | 122.9984 | 122.7197 | 123.0084 | 66.78 | -123.0738 | 122.913 | 123.077 | 122.5537 | 66.7881 | -123.3198
7.7969 | 123.3536 | -66.7603 | 56.3004 | -0.0057996 | -0.00071579 | 0.0010342 | 0.066908 | -0.00055774 | 0.064078 | -0.017016 | 0.00025007 | 0.00025221 | 0.062298 | 0.0041731 | 0.063987 | -66.7885 | 0.028878 | -66.7552 | 56.2473 | 56.0006 | 56.2482 | -66.8421 | -66.7794 | 0.03241 | -66.8094 | 56.1619 | 56.3122 | 55.8118 | -67.024 | -0.081839 | -0.053094 | -0.028221 | 0.005093 | 0.086932 | -0.29975 | -0.052193 | -0.26378 | -0.13844 | -0.019182 | -0.049108 | 0.21468 | 0.011849 | -0.4886 | 123.0075 | 122.7609 | 123.0084 | 66.7891 | -123.1424 | 122.9222 | 123.0725 | 122.572 | 66.7927 | -123.3244
8.7969 | 123.3719 | -66.7511 | 56.2866 | -0.0057996 | -0.00092939 | 0.00060681 | 0.066267 | -0.00055774 | 0.063864 | -0.0093855 | 0.00046367 | 0.00025221 | 0.062084 | 0.0046005 | 0.06356 | -66.7931 | 0.028878 | -66.7552 | 56.2518 | 56.0143 | 56.2436 | -66.8421 | -66.784 | 0.018674 | -66.8185 | 56.1619 | 56.3168 | 55.766 | -67.024 | -0.090994 | -0.034782 | -0.041954 | -0.004062 | 0.086932 | -0.27228 | -0.043038 | -0.27294 | -0.1247 | -0.032915 | -0.06742 | 0.20552 | 0.030161 | -0.52065 | 123.0029 | 122.7654 | 122.9947 | 66.78 | -123.1287 | 122.913 | 123.0679 | 122.5171 | 66.7698 | -123.3107
9.7969 | 123.2849 | -66.7603 | 56.282 | -0.0057996 | -0.00092939 | 0.0010342 | 0.066267 | -0.00055774 | 0.064291 | -0.001755 | 0.00025007 | 0.00025221 | 0.06187 | 0.0039593 | 0.063773 | -66.7839 | 0.019721 | -66.7643 | 56.2656 | 56.1883 | 56.2619 | -66.8604 | -66.784 | 0.03241 | -66.8185 | 56.1619 | 56.3214 | 56.2376 | -67.0195 | -0.10015 | -0.016469 | -0.023642 | -0.004064 | 0.09609 | -0.093701 | -0.020146 | -0.2592 | -0.12013 | -0.02376 | -0.058265 | 0.20094 | 0.039317 | -0.044475 | 123.0258 | 122.9486 | 123.0222 | 66.78 | -123.1425 | 122.9222 | 123.0816 | 122.9978 | 66.7927 | -123.3015
10.7969 | 123.3536 | -66.7694 | 56.2683 | 0.0018314 | -0.0011432 | 0.00082041 | 0.066267 | -0.00055774 | 0.064291 | -0.0093855 | 0.00046367 | 0.00025221 | 0.062298 | 0.0041731 | 0.063987 | -66.7931 | 0.033457 | -66.7643 | 56.2473 | 56.0143 | 56.2573 | -66.8329 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3168 | 55.8896 | -67.0195 | -0.063526 | -0.021051 | -0.023644 | 0.005091 | 0.068617 | -0.25397 | -0.010993 | -0.25005 | -0.10639 | -0.010027 | -0.039953 | 0.2101 | 0.048471 | -0.37872 | 123.0167 | 122.7838 | 123.0267 | 66.8029 | -123.1012 | 122.9313 | 123.0862 | 122.659 | 66.7972 | -123.2878
11.7969 | 123.2162 | -66.7969 | 56.3232 | 0.0018314 | -0.00071579 | 0.00060681 | 0.066481 | -0.00055774 | 0.064291 | -0.001755 | 0.00025007 | 0.00046581 | 0.062084 | 0.0041731 | 0.063773 | -66.7885 | 0.028878 | -66.7506 | 56.2473 | 56.0235 | 56.2527 | -66.8375 | -66.7794 | 0.03241 | -66.8185 | 56.1665 | 56.3214 | 55.9079 | -67.0195 | -0.040639 | -0.075982 | 0.0084 | 0.046292 | 0.086931 | -0.29974 | -0.070502 | -0.22258 | -0.15675 | 0.017439 | -0.021644 | 0.20094 | -0.001882 | -0.41533 | 123.0441 | 122.8204 | 123.0496 | 66.8258 | -123.1608 | 122.9634 | 123.1182 | 122.7048 | 66.8293 | -123.3427
12.7969 | 123.3719 | -66.7419 | 56.2683 | -0.0057996 | -0.0011432 | 0.00082041 | 0.066695 | -0.00077134 | 0.064078 | 0.0058755 | 0.00025007 | 0.00025221 | 0.062084 | 0.0039593 | 0.063987 | -66.7885 | 0.028878 | -66.7506 | 56.2473 | 56.0235 | 56.2527 | -66.8375 | -66.7749 | 0.03241 | -66.8139 | 56.1711 | 56.3214 | 55.9491 | -67.024 | -0.095571 | -0.021051 | -0.046532 | -0.00864 | 0.086931 | -0.24481 | -0.015571 | -0.28209 | -0.097237 | -0.032914 | -0.071998 | 0.2101 | 0.053049 | -0.3192 | 122.9892 | 122.7654 | 122.9947 | 66.7708 | -123.1058 | 122.913 | 123.0633 | 122.6911 | 66.7744 | -123.2923
13.7969 | 123.262 | -66.7557 | 56.3141 | -0.0057996 | -0.00092939 | 0.00060681 | 0.066481 | -0.00055774 | 0.064078 | -0.0093855 | 0.00025007 | 0.00025221 | 0.062084 | 0.0039593 | 0.063987 | -66.7885 | 0.028878 | -66.7552 | 56.2473 | 56.051 | 56.2619 | -66.8329 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3214 | 55.9171 | -67.0195 | -0.077259 | -0.066827 | -0.032799 | 0.000515 | 0.077774 | -0.26311 | -0.05219 | -0.26378 | -0.15217 | -0.02376 | -0.053686 | 0.2101 | 0.007273 | -0.39702 | 123.0029 | 122.8066 | 123.0176 | 66.7846 | -123.147 | 122.9176 | 123.077 | 122.6727 | 66.7835 | -123.3335
14.7969 | 123.3307 | -66.7603 | 56.2729 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066695 | -0.00098494 | 0.064078 | -0.0093855 | 0.00046367 | 0.00025221 | 0.062298 | 0.0043867 | 0.063773 | -66.7839 | 0.028878 | -66.7552 | 56.2564 | 56.0281 | 56.2527 | -66.8329 | -66.7794 | 0.018674 | -66.8094 | 56.1573 | 56.3214 | 55.9262 | -67.0286 | -0.072681 | -0.016471 | -0.023642 | 0.005093 | 0.077774 | -0.24481 | -0.020148 | -0.26836 | -0.11555 | -0.019182 | -0.049108 | 0.21925 | 0.048472 | -0.34667 | 123.0167 | 122.7883 | 123.013 | 66.7891 | -123.1058 | 122.9176 | 123.0816 | 122.6865 | 66.7789 | -123.3015
15.7969 | 123.2803 | -66.7923 | 56.3049 | 0.0018314 | -0.0011432 | 0.00082041 | 0.066267 | -0.00055774 | 0.064078 | -0.0093855 | 0.00046367 | 0.00067941 | 0.062084 | 0.0041731 | 0.063773 | -66.7839 | 0.0243 | -66.7552 | 56.261 | 56.0876 | 56.2711 | -66.8421 | -66.7794 | 0.027831 | -66.8185 | 56.1619 | 56.3214 | 55.9308 | -67.024 | -0.049796 | -0.043937 | 0.008401 | 0.037136 | 0.086932 | -0.21733 | -0.033878 | -0.23174 | -0.14301 | 0.012861 | -0.026222 | 0.20552 | 0.016428 | -0.37413 | 123.0533 | 122.8799 | 123.0634 | 66.8166 | -123.147 | 122.9542 | 123.1137 | 122.7231 | 66.8201 | -123.329
16.7969 | 123.3673 | -66.7419 | 56.2958 | 0.0018314 | -0.0011432 | 0.0010342 | 0.066695 | -0.00034394 | 0.064291 | -0.001755 | -0.00017733 | 0.00067941 | 0.062084 | 0.0046005 | 0.063773 | -66.7839 | 0.033457 | -66.746 | 56.2564 | 56.0784 | 56.2665 | -66.7963 | -66.7749 | 0.036989 | -66.8139 | 56.1619 | 56.3259 | 55.9445 | -67.024 | -0.054361 | -0.039359 | -0.041953 | -0.004062 | 0.050299 | -0.21733 | -0.0293 | -0.28209 | -0.13386 | -0.032914 | -0.071998 | 0.2101 | 0.030163 | -0.35124 | 122.9984 | 122.8204 | 123.0084 | 66.7754 | -123.0921 | 122.9039 | 123.0679 | 122.6865 | 66.7789 | -123.3198
17.7969 | 123.2346 | -66.8015 | 56.337 | 0.0094624 | -0.0011432 | 0.00060681 | 0.066267 | -0.00055774 | 0.064078 | -0.0093855 | 0.00046367 | 0.00025221 | 0.062298 | 0.0041731 | 0.06356 | -66.7931 | 0.028878 | -66.7506 | 56.2564 | 56.0418 | 56.2665 | -66.8375 | -66.784 | 0.03241 | -66.8139 | 56.1665 | 56.3168 | 55.9445 | -67.0195 | -0.036061 | -0.080558 | 0.0084 | 0.05087 | 0.086931 | -0.29516 | -0.070499 | -0.21801 | -0.17048 | 0.017439 | -0.012488 | 0.20552 | -0.020193 | -0.39244 | 123.0579 | 122.8433 | 123.0679 | 66.8303 | -123.1745 | 122.9679 | 123.1182 | 122.746 | 66.8339 | -123.3564
18.7969 | 123.317 | -66.7831 | 56.2912 | -0.013431 | -0.00092939 | 0.0010342 | 0.066481 | -0.00055774 | 0.063864 | -0.001755 | 0.00046367 | 0.00046581 | 0.06187 | 0.0041731 | 0.06356 | -66.7839 | 0.033457 | -66.7506 | 56.2518 | 56.0327 | 56.2665 | -66.7643 | -66.7749 | 0.027831 | -66.8185 | 56.1619 | 56.3259 | 55.9308 | -67.0286 | 0.018891 | -0.03936 | -0.000754 | 0.032559 | 0.013668 | -0.25854 | -0.024723 | -0.24547 | -0.12928 | 0.008285 | -0.035377 | 0.2101 | 0.03474 | -0.3604 | 123.035 | 122.8158 | 123.0496 | 66.8166 | -123.0555 | 122.9451 | 123.1091 | 122.7139 | 66.811 | -123.3198
19.7969 | 123.23 | -66.806 | 56.3416 | 0.0018314 | -0.00071579 | 0.00082041 | 0.066267 | -0.00098494 | 0.064291 | -0.0093855 | 0.00067727 | 0.00046581 | 0.062084 | 0.0043867 | 0.063773 | -66.7885 | 0.033457 | -66.7643 | 56.261 | 56.0556 | 56.2665 | -66.8146 | -66.784 | 0.03241 | -66.8185 | 56.1619 | 56.3214 | 55.9491 | -67.024 | -0.008589 | -0.080558 | 0.017555 | 0.041712 | 0.050301 | -0.286 | -0.075077 | -0.21801 | -0.17964 | 0.022016 | -0.012489 | 0.20552 | -0.020193 | -0.39244 | 123.067 | 122.8616 | 123.0725 | 66.8395 | -123.1562 | 122.9679 | 123.1274 | 122.7551 | 66.8384 | -123.3656
20.7969 | 123.3536 | -66.7465 | 56.2866 | 0.0018314 | -0.00071579 | 0.00082041 | 0.066481 | -0.00055774 | 0.064078 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.06187 | 0.0041731 | 0.063987 | -66.7839 | 0.033457 | -66.7552 | 56.2518 | 56.0418 | 56.239 | -66.8238 | -66.7703 | 0.023253 | -66.8094 | 56.1665 | 56.3168 | 55.9445 | -67.0195 | -0.077256 | -0.034782 | -0.037375 | -0.00864 | 0.068616 | -0.2448 | -0.047617 | -0.27294 | -0.12012 | -0.023757 | -0.062841 | 0.2101 | 0.030161 | -0.34208 | 122.9984 | 122.7883 | 122.9855 | 66.78 | -123.1104 | 122.913 | 123.0633 | 122.6911 | 66.7698 | -123.3061
21.7969 | 123.2391 | -66.7648 | 56.2958 | -0.0057996 | -0.0011432 | 0.0010342 | 0.066695 | -0.00055774 | 0.064078 | -0.0093855 | 0.00046367 | 0.00046581 | 0.06187 | 0.0046005 | 0.063987 | -66.7839 | 0.028878 | -66.7552 | 56.261 | 56.0418 | 56.2756 | -66.8375 | -66.784 | 0.027831 | -66.8048 | 56.1619 | 56.3214 | 55.94 | -67.0332 | -0.072682 | -0.034781 | -0.019064 | 0.009671 | 0.082353 | -0.25396 | -0.020143 | -0.26836 | -0.13386 | -0.019182 | -0.039951 | 0.22841 | 0.025584 | -0.35582 | 123.0258 | 122.8066 | 123.0405 | 66.7937 | -123.1333 | 122.9267 | 123.0862 | 122.7048 | 66.7927 | -123.329
22.7969 | 123.3261 | -66.7648 | 56.2775 | 0.0018314 | -0.00050219 | 0.00039321 | 0.066054 | -0.00077134 | 0.06365 | -0.0093855 | 0.00046367 | 0.00025221 | 0.06187 | 0.0041731 | 0.063346 | -66.7839 | 0.028878 | -66.746 | 56.2564 | 56.0189 | 56.2711 | -66.8375 | -66.784 | 0.03241 | -66.8139 | 56.1711 | 56.3214 | 55.94 | -67.024 | -0.072682 | -0.021049 | -0.019064 | 0.018827 | 0.091509 | -0.25854 | -0.006412 | -0.25921 | -0.10639 | -0.019182 | -0.049109 | 0.2101 | 0.043894 | -0.33751 | 123.0212 | 122.7838 | 123.0359 | 66.7937 | -123.115 | 122.9359 | 123.0862 | 122.7048 | 66.7972 | -123.3015
23.7969 | 123.2849 | -66.7694 | 56.3004 | 0.0018314 | -0.00092939 | 0.00082041 | 0.066695 | -0.00077134 | 0.064291 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0041731 | 0.063773 | -66.7931 | 0.038035 | -66.7506 | 56.2564 | 56.0418 | 56.2482 | -66.81 | -66.7794 | 0.027831 | -66.8139 | 56.1665 | 56.3259 | 55.9445 | -67.0332 | -0.040631 | -0.043937 | -0.023644 | 0.018826 | 0.059457 | -0.25854 | -0.052193 | -0.26379 | -0.13386 | -0.010027 | -0.044532 | 0.21925 | 0.025585 | -0.35582 | 123.0258 | 122.8112 | 123.0176 | 66.8074 | -123.1104 | 122.9359 | 123.0953 | 122.7139 | 66.7972 | -123.3335
24.7969 | 123.3398 | -66.7328 | 56.2729 | 0.0094624 | -0.00092939 | 0.00082041 | 0.066054 | -0.00077134 | 0.064078 | -0.001755 | 0.00046367 | 0.00046581 | 0.062084 | 0.0046005 | 0.063773 | -66.7793 | 0.0243 | -66.7552 | 56.2564 | 56.0693 | 56.2665 | -66.8329 | -66.7794 | 0.03241 | -66.8048 | 56.1619 | 56.3214 | 55.94 | -67.0332 | -0.10015 | -0.016471 | -0.04653 | -0.022373 | 0.077774 | -0.2036 | -0.006412 | -0.30041 | -0.11097 | -0.046648 | -0.071995 | 0.22841 | 0.048472 | -0.33293 | 122.9892 | 122.8021 | 122.9993 | 66.7571 | -123.1058 | 122.8947 | 123.0541 | 122.6727 | 66.7652 | -123.3061
25.7969 | 123.2254 | -66.7969 | 56.3324 | -0.0057996 | -0.0011432 | 0.0010342 | 0.066481 | -0.00055774 | 0.064078 | -0.0093855 | 0.00025007 | 3.8406e-05 | 0.062084 | 0.0043867 | 0.063773 | -66.7885 | 0.028878 | -66.7597 | 56.2564 | 56.0327 | 56.2482 | -66.8329 | -66.7794 | 0.03241 | -66.8094 | 56.1528 | 56.3214 | 55.9537 | -67.0195 | -0.03606 | -0.07598 | 0.0084 | 0.037135 | 0.073195 | -0.29974 | -0.084236 | -0.22258 | -0.17964 | 0.017439 | -0.012487 | 0.2101 | -0.011037 | -0.3787 | 123.0533 | 122.8295 | 123.045 | 66.8258 | -123.1653 | 122.9496 | 123.1182 | 122.7506 | 66.8293 | -123.3519
26.7969 | 123.3353 | -66.7557 | 56.2912 | -0.013431 | -0.00092939 | 0.00082041 | 0.066481 | -0.00034394 | 0.064078 | -0.001755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0041731 | 0.063987 | -66.7885 | 0.028878 | -66.7506 | 56.2564 | 56.0327 | 56.2711 | -66.8329 | -66.7794 | 0.023253 | -66.8185 | 56.1573 | 56.3168 | 55.9445 | -67.024 | -0.077259 | -0.034782 | -0.032799 | 0.005093 | 0.082352 | -0.25854 | -0.020145 | -0.26836 | -0.13386 | -0.02376 | -0.062843 | 0.20552 | 0.025583 | -0.34666 | 123.0121 | 122.7883 | 123.0267 | 66.7846 | -123.1241 | 122.913 | 123.0725 | 122.7002 | 66.7789 | -123.3152
27.7969 | 123.3398 | -66.7786 | 56.2729 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066481 | -0.00077134 | 0.063864 | 0.0058755 | 0.00025007 | 0.00046581 | 0.062084 | 0.0043867 | 0.063773 | -66.7885 | 0.0243 | -66.7506 | 56.2564 | 56.0693 | 56.2619 | -66.8146 | -66.7794 | 0.023253 | -66.8185 | 56.1619 | 56.3259 | 55.9491 | -67.0195 | -0.036055 | -0.016471 | -0.009911 | 0.027981 | 0.064036 | -0.2036 | -0.010991 | -0.24089 | -0.11097 | -0.000872 | -0.039955 | 0.20094 | 0.053051 | -0.32377 | 123.035 | 122.8479 | 123.0405 | 66.8029 | -123.0875 | 122.9405 | 123.1045 | 122.7277 | 66.8018 | -123.2923
28.7969 | 123.3307 | -66.774 | 56.2866 | -0.0057996 | -0.0011432 | 0.00060681 | 0.066481 | -0.00055774 | 0.063864 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.06187 | 0.0041731 | 0.064201 | -66.7839 | 0.033457 | -66.7597 | 56.2564 | 56.0556 | 56.2573 | -66.8146 | -66.7794 | 0.03241 | -66.8094 | 56.1711 | 56.3259 | 55.9445 | -67.0286 | -0.040632 | -0.030204 | -0.009909 | 0.014247 | 0.054879 | -0.23107 | -0.029303 | -0.25463 | -0.11555 | -0.005449 | -0.035375 | 0.21925 | 0.039318 | -0.34208 | 123.0304 | 122.8295 | 123.0313 | 66.8074 | -123.1012 | 122.9451 | 123.0999 | 122.7185 | 66.8064 | -123.3152
29.7969 | 123.2986 | -66.7694 | 56.2912 | 0.0018314 | -0.0013568 | 0.00060681 | 0.066267 | -0.00055774 | 0.064291 | -0.001755 | 0.00025007 | 0.00067941 | 0.062511 | 0.0043867 | 0.063773 | -66.7793 | 0.028878 | -66.7597 | 56.261 | 56.0739 | 56.2665 | -66.8284 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3214 | 55.94 | -67.024 | -0.058947 | -0.030204 | -0.009909 | 0.009669 | 0.068616 | -0.21733 | -0.024723 | -0.25463 | -0.12928 | -0.010027 | -0.039953 | 0.21468 | 0.030161 | -0.35124 | 123.0304 | 122.8433 | 123.0359 | 66.7983 | -123.1196 | 122.9313 | 123.0908 | 122.7094 | 66.7972 | -123.3152
30.7969 | 123.3582 | -66.7603 | 56.2912 | -0.0057996 | -0.00092939 | 0.00082041 | 0.066481 | -0.00055774 | 0.063864 | 0.0058755 | 0.00046367 | 0.00046581 | 0.06187 | 0.0043867 | 0.063773 | -66.7885 | 0.033457 | -66.7552 | 56.2564 | 56.0556 | 56.2711 | -66.8421 | -66.7886 | 0.027831 | -66.8139 | 56.1665 | 56.3305 | 55.9445 | -67.0332 | -0.081839 | -0.034782 | -0.028221 | 0.005093 | 0.086932 | -0.23565 | -0.020145 | -0.27294 | -0.1247 | -0.028339 | -0.053687 | 0.21925 | 0.039318 | -0.34666 | 123.0167 | 122.8158 | 123.0313 | 66.7937 | -123.1333 | 122.9267 | 123.0908 | 122.7048 | 66.7881 | -123.3244
31.7969 | 123.2895 | -66.7877 | 56.3324 | 0.0018314 | -0.00092939 | 0.00082041 | 0.066481 | -0.00055774 | 0.064078 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.06187 | 0.0046005 | 0.063773 | -66.7793 | 0.028878 | -66.7414 | 56.261 | 56.0189 | 56.2665 | -66.8375 | -66.7794 | 0.036989 | -66.8094 | 56.1619 | 56.3168 | 55.9445 | -67.024 | -0.049794 | -0.071402 | 0.008402 | 0.046293 | 0.096087 | -0.31347 | -0.065921 | -0.23632 | -0.17048 | 0.008284 | -0.021642 | 0.21468 | -0.015615 | -0.38786 | 123.0487 | 122.8066 | 123.0542 | 66.8166 | -123.1699 | 122.9496 | 123.1045 | 122.7323 | 66.8247 | -123.3564
32.7969 | 123.3353 | -66.7465 | 56.2912 | -0.013431 | -0.00071579 | 0.00060681 | 0.066481 | -0.00034394 | 0.06365 | -0.001755 | 0.00046367 | 0.00067941 | 0.062084 | 0.0043867 | 0.063987 | -66.7885 | 0.0243 | -66.7552 | 56.2564 | 56.0601 | 56.2619 | -66.8375 | -66.7749 | 0.023253 | -66.8139 | 56.1665 | 56.3168 | 55.9445 | -67.0286 | -0.090993 | -0.034782 | -0.041954 | -0.00864 | 0.082353 | -0.23107 | -0.029302 | -0.28209 | -0.1247 | -0.028336 | -0.06742 | 0.21467 | 0.025583 | -0.34666 | 123.0029 | 122.8067 | 123.0084 | 66.7708 | -123.1287 | 122.913 | 123.0633 | 122.6911 | 66.7698 | -123.3198
33.7969 | 123.3215 | -66.7603 | 56.2775 | -0.0057996 | -0.00092939 | 0.00082041 | 0.066267 | -0.00055774 | 0.063864 | -0.0093855 | 0.00025007 | 0.00025221 | 0.062298 | 0.0043867 | 0.063987 | -66.7885 | 0.033457 | -66.7597 | 56.2518 | 56.0418 | 56.2711 | -66.8375 | -66.7794 | 0.03241 | -66.8139 | 56.1619 | 56.3168 | 55.9629 | -67.0286 | -0.07726 | -0.025627 | -0.028221 | 0.000514 | 0.077774 | -0.23565 | -0.006412 | -0.26836 | -0.11555 | -0.019182 | -0.053687 | 0.21467 | 0.039316 | -0.31461 | 123.0121 | 122.8021 | 123.0313 | 66.7937 | -123.115 | 122.9222 | 123.077 | 122.7231 | 66.7927 | -123.3061
34.7969 | 123.317 | -66.7282 | 56.2958 | -0.0057996 | -0.0013568 | 0.0012478 | 0.066267 | -0.00077134 | 0.064078 | -0.0093855 | 0.00025007 | 0.00046581 | 0.06187 | 0.0046005 | 0.063773 | -66.7793 | 0.038035 | -66.7506 | 56.2564 | 56.0052 | 56.2665 | -66.7963 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3214 | 55.9354 | -67.0286 | -0.068094 | -0.039359 | -0.051108 | -0.022373 | 0.045721 | -0.29059 | -0.0293 | -0.30041 | -0.13386 | -0.051226 | -0.081152 | 0.21925 | 0.025584 | -0.3604 | 122.9846 | 122.7334 | 122.9947 | 66.7662 | -123.0921 | 122.8901 | 123.0496 | 122.6636 | 66.756 | -123.3244
35.7969 | 123.2849 | -66.7923 | 56.2958 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066481 | -0.00077134 | 0.064078 | -0.001755 | -0.00017733 | 0.00046581 | 0.062084 | 0.0043867 | 0.063987 | -66.7885 | 0.033457 | -66.7552 | 56.2518 | 56.0281 | 56.239 | -66.8192 | -66.7749 | 0.03241 | -66.8094 | 56.1711 | 56.3168 | 55.94 | -67.024 | -0.026901 | -0.043937 | 0.003822 | 0.037136 | 0.064037 | -0.2677 | -0.056772 | -0.23174 | -0.1247 | 0.01744 | -0.017065 | 0.21468 | 0.021006 | -0.35582 | 123.0441 | 122.8204 | 123.0313 | 66.8258 | -123.115 | 122.9634 | 123.1091 | 122.7323 | 66.8247 | -123.3198
36.7969 | 123.3536 | -66.7648 | 56.3095 | 0.0018314 | -0.0013568 | 0.00060681 | 0.066481 | -0.00034394 | 0.064078 | 0.0058755 | 0.00067727 | 0.00025221 | 0.062298 | 0.0043867 | 0.063773 | -66.7885 | 0.033457 | -66.7552 | 56.261 | 56.0784 | 56.2711 | -66.8375 | -66.7794 | 0.027831 | -66.8094 | 56.1665 | 56.3214 | 55.9491 | -67.0332 | -0.072682 | -0.048514 | -0.023643 | 0.009671 | 0.082353 | -0.23106 | -0.038455 | -0.26836 | -0.14301 | -0.014604 | -0.04453 | 0.22383 | 0.011851 | -0.36039 | 123.0258 | 122.8433 | 123.0359 | 66.7983 | -123.147 | 122.9313 | 123.0862 | 122.7139 | 66.7927 | -123.3427
37.7969 | 123.2666 | -66.7831 | 56.2958 | -0.0057996 | -0.0011432 | 0.00082041 | 0.066481 | -0.00055774 | 0.06365 | 0.0058755 | 0.00025007 | 0.00025221 | 0.062084 | 0.0046005 | 0.06356 | -66.7885 | 0.033457 | -66.7506 | 56.2518 | 56.0235 | 56.2711 | -66.8375 | -66.7749 | 0.036989 | -66.8048 | 56.1665 | 56.3214 | 55.94 | -67.0286 | -0.054372 | -0.043937 | -0.005333 | 0.032559 | 0.086931 | -0.27227 | -0.024722 | -0.24547 | -0.12928 | 0.008285 | -0.021641 | 0.22383 | 0.025584 | -0.35582 | 123.035 | 122.8066 | 123.0542 | 66.8166 | -123.1333 | 122.9496 | 123.1045 | 122.7231 | 66.8201 | -123.3244
38.7969 | 123.3582 | -66.7511 | 56.282 | 0.0018314 | -0.0013568 | 0.0010342 | 0.066267 | -0.00098494 | 0.063864 | -0.017016 | 0.00025007 | 0.00067941 | 0.062298 | 0.0046005 | 0.06356 | -66.7839 | 0.0243 | -66.7506 | 56.2473 | 56.0281 | 56.2436 | -66.8284 | -66.7749 | 0.036989 | -66.8139 | 56.1573 | 56.3168 | 55.9445 | -67.0195 | -0.077257 | -0.034783 | -0.032797 | 0.000516 | 0.077773 | -0.25396 | -0.03846 | -0.26836 | -0.1247 | -0.023758 | -0.062842 | 0.20552 | 0.034739 | -0.33751 | 122.9984 | 122.7792 | 122.9947 | 66.7754 | -123.1104 | 122.9084 | 123.0679 | 122.6956 | 66.7881 | -123.3015
39.7969 | 123.2254 | -66.8152 | 56.3278 | -0.0057996 | -0.0011432 | 0.00060681 | 0.066267 | -0.00098494 | 0.063864 | -0.0093855 | 0.00025007 | 0.00046581 | 0.062298 | 0.0048141 | 0.063773 | -66.7885 | 0.033457 | -66.7368 | 56.2564 | 56.0693 | 56.2711 | -66.7963 | -66.7703 | 0.027831 | -66.8139 | 56.1619 | 56.3122 | 55.9445 | -67.0286 | 0.018882 | -0.071403 | 0.026711 | 0.078338 | 0.059456 | -0.25853 | -0.056766 | -0.21343 | -0.1659 | 0.044908 | 0.001245 | 0.21467 | -0.015617 | -0.38328 | 123.0716 | 122.8845 | 123.0862 | 66.8486 | -123.1241 | 122.9771 | 123.1274 | 122.7597 | 66.843 | -123.3564
40.7969 | 123.3536 | -66.7557 | 56.2683 | 0.0094624 | -0.0011432 | 0.0010342 | 0.066481 | -0.00098494 | 0.063864 | -0.001755 | 0.00025007 | 0.00046581 | 0.06187 | 0.0041731 | 0.063773 | -66.7839 | 0.038035 | -66.7552 | 56.2564 | 56.0693 | 56.2711 | -66.8421 | -66.7794 | 0.027831 | -66.8139 | 56.1573 | 56.3122 | 55.9629 | -67.0286 | -0.086417 | -0.011894 | -0.02822 | 0.000515 | 0.086932 | -0.19902 | 0.002743 | -0.27294 | -0.11097 | -0.02376 | -0.058265 | 0.21467 | 0.043892 | -0.30546 | 123.0121 | 122.825 | 123.0267 | 66.7937 | -123.1104 | 122.913 | 123.0679 | 122.7185 | 66.7835 | -123.2969
41.7969 | 123.2895 | -66.774 | 56.3004 | 0.0018314 | -0.0011432 | 0.00082041 | 0.066267 | -0.00034394 | 0.06365 | -0.017016 | 0.00046367 | 3.8406e-05 | 0.062298 | 0.0041731 | 0.06356 | -66.7885 | 0.038035 | -66.7506 | 56.2473 | 56.051 | 56.2665 | -66.8421 | -66.7749 | 0.03241 | -66.8048 | 56.1665 | 56.3076 | 55.9354 | -67.0286 | -0.068106 | -0.053094 | -0.014488 | 0.023404 | 0.09151 | -0.24938 | -0.033878 | -0.25463 | -0.13386 | -0.00087 | -0.030796 | 0.22383 | 0.00727 | -0.36497 | 123.0212 | 122.825 | 123.0405 | 66.812 | -123.1424 | 122.9405 | 123.0816 | 122.7094 | 66.8064 | -123.329
42.7969 | 123.3353 | -66.7282 | 56.282 | -0.0057996 | -0.0011432 | 0.00060681 | 0.066481 | -0.00034394 | 0.063864 | -0.001755 | 0.00025007 | 0.00067941 | 0.062084 | 0.0043867 | 0.063773 | -66.7793 | 0.0243 | -66.746 | 56.2564 | 56.0327 | 56.2711 | -66.8375 | -66.7749 | 0.023253 | -66.8094 | 56.1619 | 56.3122 | 55.9537 | -67.0286 | -0.1093 | -0.025626 | -0.051108 | -0.017795 | 0.091509 | -0.24938 | -0.010989 | -0.30041 | -0.12013 | -0.046647 | -0.081152 | 0.21925 | 0.03016 | -0.32835 | 122.9846 | 122.7609 | 122.9993 | 66.7525 | -123.1196 | 122.8901 | 123.0404 | 122.6819 | 66.7515 | -123.3107
43.7969 | 123.262 | -66.7877 | 56.3049 | 0.0094624 | -0.0011432 | 0.00082041 | 0.066054 | -0.00034394 | 0.063864 | -0.0093855 | -0.00017733 | 0.00046581 | 0.062298 | 0.0046005 | 0.063987 | -66.7885 | 0.033457 | -66.7506 | 56.2564 | 56.0556 | 56.2573 | -66.8421 | -66.7749 | 0.027831 | -66.8139 | 56.1619 | 56.3168 | 55.9354 | -67.0195 | -0.054373 | -0.048515 | -0.000755 | 0.037137 | 0.09151 | -0.24938 | -0.047614 | -0.23174 | -0.14301 | 0.012863 | -0.026221 | 0.20552 | 0.01185 | -0.36955 | 123.0441 | 122.8433 | 123.045 | 66.8212 | -123.147 | 122.9496 | 123.1045 | 122.7231 | 66.8156 | -123.3244
44.7969 | 123.3582 | -66.7648 | 56.2775 | 0.0018314 | -0.0013568 | 0.0010342 | 0.066481 | -0.00077134 | 0.064078 | -0.0093855 | 0.00025007 | 0.00046581 | 0.062084 | 0.0043867 | 0.063987 | -66.7793 | 0.038035 | -66.7506 | 56.2564 | 56.0693 | 56.2619 | -66.8284 | -66.7886 | 0.03241 | -66.8139 | 56.1665 | 56.3214 | 55.972 | -67.0286 | -0.063524 | -0.021049 | -0.014486 | 0.014249 | 0.077773 | -0.20818 | -0.015569 | -0.26378 | -0.11097 | -0.023761 | -0.049109 | 0.21467 | 0.043894 | -0.30546 | 123.0212 | 122.8341 | 123.0267 | 66.8029 | -123.1058 | 122.9313 | 123.0862 | 122.7368 | 66.7972 | -123.3061
45.7969 | 123.2346 | -66.7969 | 56.3278 | -0.0057996 | -0.0011432 | 0.0014616 | 0.066481 | -0.00055774 | 0.064078 | -0.001755 | 0.00046367 | 0.00046581 | 0.062511 | 0.0046005 | 0.063773 | -66.7793 | 0.038035 | -66.7506 | 56.2564 | 55.996 | 56.2711 | -66.8421 | -66.7703 | 0.027831 | -66.8048 | 56.1573 | 56.3168 | 55.9537 | -67.0195 | -0.045218 | -0.071403 | 0.017557 | 0.046292 | 0.09151 | -0.33179 | -0.056766 | -0.22258 | -0.17048 | 0.026597 | -0.007908 | 0.21468 | -0.011038 | -0.37412 | 123.0533 | 122.7929 | 123.0679 | 66.8349 | -123.1699 | 122.9542 | 123.1137 | 122.7506 | 66.8247 | -123.3473
46.7969 | 123.3444 | -66.774 | 56.3049 | -0.013431 | -0.0011432 | 0.00082041 | 0.066267 | -0.00098494 | 0.063864 | -0.001755 | 0.00025007 | 0.00067941 | 0.06187 | 0.0046005 | 0.063773 | -66.7839 | 0.038035 | -66.7506 | 56.261 | 56.0556 | 56.2711 | -66.8238 | -66.7703 | 0.023253 | -66.8094 | 56.1665 | 56.3168 | 55.9354 | -67.0149 | -0.04979 | -0.043937 | -0.009909 | 0.023404 | 0.073194 | -0.24938 | -0.033878 | -0.24089 | -0.13844 | 0.003709 | -0.035375 | 0.20552 | 0.01185 | -0.36955 | 123.035 | 122.8295 | 123.045 | 66.812 | -123.1287 | 122.9405 | 123.0908 | 122.7094 | 66.7972 | -123.3198
47.7969 | 123.3124 | -66.7786 | 56.3049 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066267 | -0.00055774 | 0.063864 | -0.001755 | 0.00046367 | 0.00025221 | 0.062084 | 0.0046005 | 0.063987 | -66.7839 | 0.0243 | -66.7552 | 56.2564 | 56.0052 | 56.2527 | -66.8329 | -66.7749 | 0.036989 | -66.8094 | 56.1619 | 56.3122 | 55.94 | -67.0195 | -0.054371 | -0.048515 | -0.005332 | 0.023403 | 0.077774 | -0.29975 | -0.052192 | -0.24089 | -0.14301 | 0.003707 | -0.030798 | 0.2101 | 0.007271 | -0.36497 | 123.035 | 122.7837 | 123.0313 | 66.8029 | -123.1379 | 122.9405 | 123.0908 | 122.7185 | 66.8156 | -123.3244
48.7969 | 123.3398 | -66.7603 | 56.2775 | -0.0057996 | -0.00071579 | 0.00082041 | 0.066481 | -0.00055774 | 0.063864 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.06187 | 0.0048141 | 0.063773 | -66.7839 | 0.033457 | -66.746 | 56.2564 | 56.0464 | 56.2711 | -66.8375 | -66.7703 | 0.03241 | -66.8094 | 56.1573 | 56.3214 | 55.9354 | -67.0332 | -0.07726 | -0.021049 | -0.023642 | 0.014249 | 0.091509 | -0.23107 | -0.006412 | -0.27294 | -0.12013 | -0.010024 | -0.049108 | 0.22383 | 0.043894 | -0.34209 | 123.0167 | 122.8066 | 123.0313 | 66.7937 | -123.115 | 122.9176 | 123.0816 | 122.6956 | 66.7927 | -123.3107
49.7969 | 123.2666 | -66.7603 | 56.3232 | -0.021062 | -0.0011432 | 0.00082041 | 0.066267 | -0.00055774 | 0.064078 | 0.0058755 | 0.00046367 | 0.00025221 | 0.062084 | 0.0046005 | 0.063773 | -66.7839 | 0.028878 | -66.7506 | 56.2518 | 56.0143 | 56.2665 | -66.8421 | -66.7703 | 0.03241 | -66.8048 | 56.1619 | 56.3168 | 55.9491 | -67.024 | -0.081839 | -0.071403 | -0.023642 | 0.009671 | 0.09151 | -0.3089 | -0.056766 | -0.26378 | -0.16132 | -0.010024 | -0.044529 | 0.21925 | -0.00646 | -0.37413 | 123.0121 | 122.7746 | 123.0267 | 66.7891 | -123.1653 | 122.9222 | 123.077 | 122.7094 | 66.7927 | -123.3473
50.7969 | 123.3444 | -66.7557 | 56.282 | -0.0057996 | -0.00092939 | 0.00060681 | 0.066481 | -0.00055774 | 0.063864 | 0.0058755 | 0.00025007 | 0.00025221 | 0.062084 | 0.0046005 | 0.063773 | -66.7885 | 0.033457 | -66.746 | 56.2518 | 56.0784 | 56.2665 | -66.8421 | -66.7749 | 0.03241 | -66.8048 | 56.1573 | 56.3214 | 55.94 | -67.024 | -0.086417 | -0.030204 | -0.032799 | 0.009671 | 0.096088 | -0.20359 | -0.015567 | -0.26836 | -0.1247 | -0.019181 | -0.049107 | 0.21925 | 0.039317 | -0.34208 | 123.0075 | 122.8341 | 123.0222 | 66.7891 | -123.1241 | 122.913 | 123.077 | 122.6956 | 66.7881 | -123.3061
51.7969 | 123.2666 | -66.7877 | 56.3095 | -0.0057996 | -0.0011432 | 0.00060681 | 0.066267 | -0.00055774 | 0.064291 | -0.017016 | 0.00025007 | 0.00046581 | 0.06187 | 0.0048141 | 0.063773 | -66.7885 | 0.033457 | -66.7506 | 56.2564 | 56.0281 | 56.2665 | -66.8421 | -66.7749 | 0.03241 | -66.8048 | 56.1573 | 56.3168 | 55.9354 | -67.024 | -0.054373 | -0.053092 | -0.000755 | 0.037137 | 0.09151 | -0.28143 | -0.043033 | -0.23632 | -0.15217 | 0.012863 | -0.017063 | 0.21925 | 0.007273 | -0.37413 | 123.0441 | 122.8158 | 123.0542 | 66.8212 | -123.1516 | 122.9451 | 123.1045 | 122.7231 | 66.8201 | -123.3335
52.7969 | 123.3719 | -66.7694 | 56.282 | 0.0018314 | -0.0013568 | 0.00039321 | 0.066054 | -0.00055774 | 0.064078 | 0.0058755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0048141 | 0.063987 | -66.7839 | 0.0243 | -66.7506 | 56.2473 | 56.0464 | 56.2711 | -66.8375 | -66.7749 | 0.03241 | -66.8139 | 56.1573 | 56.3259 | 55.94 | -67.0195 | -0.068105 | -0.034783 | -0.014487 | 0.018826 | 0.086931 | -0.23565 | -0.010989 | -0.25005 | -0.1247 | -0.005448 | -0.044532 | 0.20552 | 0.043896 | -0.34208 | 123.0167 | 122.8158 | 123.0405 | 66.7937 | -123.1196 | 122.9267 | 123.0953 | 122.7094 | 66.8018 | -123.3015
53.7969 | 123.2208 | -66.806 | 56.3278 | 0.0018314 | -0.00092939 | 0.00082041 | 0.066267 | -0.00055774 | 0.063864 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.062084 | 0.0048141 | 0.06356 | -66.7885 | 0.028878 | -66.746 | 56.2564 | 56.0327 | 56.2665 | -66.8421 | -66.7703 | 0.03241 | -66.8094 | 56.1619 | 56.3122 | 55.9262 | -67.0286 | -0.036063 | -0.071403 | 0.017555 | 0.060025 | 0.096088 | -0.29516 | -0.061344 | -0.22259 | -0.1659 | 0.035752 | -0.003332 | 0.21925 | -0.015617 | -0.4016 | 123.0624 | 122.8387 | 123.0725 | 66.8349 | -123.1699 | 122.9679 | 123.1182 | 122.7323 | 66.8384 | -123.3564
54.7969 | 123.3673 | -66.7374 | 56.2912 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066054 | -0.00055774 | 0.064291 | -0.001755 | 0.00025007 | 0.00046581 | 0.06187 | 0.0046005 | 0.063987 | -66.7885 | 0.028878 | -66.746 | 56.2473 | 56.0647 | 56.2711 | -66.8329 | -66.7657 | 0.03241 | -66.8139 | 56.1619 | 56.3214 | 55.94 | -67.0332 | -0.095569 | -0.043939 | -0.051109 | -0.008639 | 0.08693 | -0.22649 | -0.020145 | -0.29583 | -0.12928 | -0.028333 | -0.076575 | 0.21925 | 0.030161 | -0.35124 | 122.9846 | 122.8021 | 123.0084 | 66.7662 | -123.1241 | 122.8993 | 123.0587 | 122.6773 | 66.7698 | -123.3244
55.7969 | 123.3032 | -66.774 | 56.3095 | -0.0057996 | -0.0011432 | 0.00082041 | 0.066267 | -0.00055774 | 0.06365 | 0.0058755 | 0.00046367 | 0.00046581 | 0.062298 | 0.0048141 | 0.06356 | -66.7747 | 0.028878 | -66.746 | 56.2564 | 56.0372 | 56.2665 | -66.8329 | -66.7749 | 0.023253 | -66.8094 | 56.1573 | 56.3122 | 55.9537 | -67.0332 | -0.058948 | -0.053092 | -0.000752 | 0.027982 | 0.08693 | -0.27227 | -0.043033 | -0.25921 | -0.15217 | -0.00087 | -0.035375 | 0.22383 | 0.002694 | -0.35581 | 123.0304 | 122.8112 | 123.0405 | 66.8029 | -123.1424 | 122.9313 | 123.0862 | 122.7277 | 66.7972 | -123.3427
56.7969 | 123.3353 | -66.7465 | 56.3095 | -0.013431 | -0.0013568 | 0.00082041 | 0.066481 | -0.00077134 | 0.063864 | -0.0093855 | 0.00046367 | 0.00046581 | 0.06187 | 0.0048141 | 0.063773 | -66.7885 | 0.028878 | -66.746 | 56.2564 | 56.0647 | 56.2573 | -66.8375 | -66.7794 | 0.023253 | -66.8048 | 56.1573 | 56.3168 | 55.94 | -67.024 | -0.090993 | -0.053092 | -0.041954 | 0.000516 | 0.091509 | -0.2448 | -0.052191 | -0.27752 | -0.15217 | -0.032915 | -0.058262 | 0.21925 | 0.007273 | -0.36955 | 123.0029 | 122.8112 | 123.0038 | 66.7754 | -123.147 | 122.9039 | 123.0633 | 122.6865 | 66.7698 | -123.3335
57.7969 | 123.2574 | -66.7969 | 56.3004 | 0.0018314 | -0.0011432 | 0.00082041 | 0.066481 | -0.00098494 | 0.063864 | -0.0093855 | 0.00025007 | 0.00067941 | 0.06187 | 0.0046005 | 0.063346 | -66.7747 | 0.033457 | -66.746 | 56.2564 | 55.9731 | 56.2665 | -66.8284 | -66.7657 | 0.023253 | -66.8048 | 56.1619 | 56.3214 | 55.94 | -67.024 | -0.031481 | -0.043937 | 0.022136 | 0.05087 | 0.082351 | -0.32722 | -0.033878 | -0.22716 | -0.13844 | 0.031176 | -0.007908 | 0.21925 | 0.021006 | -0.36039 | 123.0533 | 122.77 | 123.0634 | 66.8303 | -123.1287 | 122.9588 | 123.1182 | 122.7368 | 66.8201 | -123.3244
58.8594 | 123.262 | -66.7374 | 56.3232 | 0.0018314 | -0.0013568 | 0.0012478 | 0.066481 | -0.00077134 | 0.06365 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.06187 | 0.0046005 | 0.063987 | -66.7839 | 0.060928 | -66.6544 | 56.2564 | 56.0327 | 56.2711 | -66.8375 | -66.697 | 0.041567 | -66.7682 | 56.1573 | 56.3168 | 55.9537 | -67.0286 | -0.10015 | -0.066825 | -0.04653 | 0.082927 | 0.18308 | -0.29058 | -0.052188 | -0.29125 | -0.1659 | 0.040347 | -0.030788 | 0.26046 | -0.00646 | -0.36955 | 122.9938 | 122.77 | 123.0084 | 66.7983 | -123.1608 | 122.8947 | 123.0541 | 122.6911 | 66.7789 | -123.3519
59.7969 | 123.2712 | -66.8106 | 56.3095 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066481 | -0.00055774 | 0.063864 | 0.0058755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0050277 | 0.06356 | -66.7747 | 0.070086 | -66.7323 | 56.2564 | 55.996 | 56.2711 | -66.8421 | -66.7657 | 0.03241 | -66.7865 | 56.1665 | 56.3168 | 55.94 | -67.024 | -0.031485 | -0.053092 | 0.035869 | 0.078338 | 0.10982 | -0.31348 | -0.038455 | -0.21343 | -0.14301 | 0.044909 | 0.024139 | 0.23757 | 0.007273 | -0.36955 | 123.067 | 122.8066 | 123.0817 | 66.8807 | -123.1516 | 122.9771 | 123.1274 | 122.7506 | 66.843 | -123.3335
60.7969 | 123.3307 | -66.7374 | 56.2729 | -0.013431 | -0.00092939 | 0.00060681 | 0.066267 | -0.00055774 | 0.06365 | -0.017016 | 0.00067727 | 0.00046581 | 0.061443 | 0.0046005 | 0.063773 | -66.7747 | 0.038035 | -66.746 | 56.2564 | 56.0189 | 56.2665 | -66.8375 | -66.7703 | 0.03241 | -66.8094 | 56.1619 | 56.3168 | 55.9354 | -67.0286 | -0.10015 | -0.016471 | -0.037373 | -0.008639 | 0.091509 | -0.25397 | -0.006412 | -0.29125 | -0.11097 | -0.032912 | -0.071996 | 0.21925 | 0.043894 | -0.33751 | 122.9938 | 122.7563 | 123.0038 | 66.7754 | -123.1104 | 122.8993 | 123.0541 | 122.6727 | 66.7698 | -123.3015
61.7969 | 123.3215 | -66.7557 | 56.282 | -0.013431 | -0.0011432 | 0.00082041 | 0.066267 | -0.00098494 | 0.063864 | -0.017016 | 0.00046367 | 0.00025221 | 0.06187 | 0.0046005 | 0.06356 | -66.7839 | 0.033457 | -66.7414 | 56.261 | 56.0281 | 56.2756 | -66.8146 | -66.7703 | 0.03241 | -66.8139 | 56.1573 | 56.3122 | 55.9262 | -67.0195 | -0.058943 | -0.021048 | -0.02822 | 0.014249 | 0.073192 | -0.25396 | -0.00641 | -0.26378 | -0.1247 | -0.014602 | -0.058265 | 0.20552 | 0.03016 | -0.35582 | 123.0167 | 122.7838 | 123.0313 | 66.7891 | -123.0967 | 122.913 | 123.0679 | 122.6819 | 66.7881 | -123.3015
62.7969 | 123.3032 | -66.7465 | 56.2775 | -0.0057996 | -0.00071579 | 0.00082041 | 0.066267 | -0.00077134 | 0.063864 | -0.001755 | 0.00046367 | 0.00025221 | 0.062084 | 0.0046005 | 0.063773 | -66.7793 | 0.033457 | -66.746 | 56.2564 | 56.0464 | 56.2802 | -66.8467 | -66.7749 | 0.027831 | -66.8048 | 56.1528 | 56.3168 | 55.9308 | -67.024 | -0.10015 | -0.021049 | -0.032797 | 0.000516 | 0.10067 | -0.23107 | 0.002745 | -0.27752 | -0.12471 | -0.028336 | -0.058262 | 0.21925 | 0.039316 | -0.34666 | 123.0029 | 122.7929 | 123.0267 | 66.78 | -123.1241 | 122.8993 | 123.0633 | 122.6773 | 66.7744 | -123.3015
63.7969 | 123.262 | -66.7648 | 56.3095 | -0.013431 | -0.0013568 | 0.0010342 | 0.066054 | -0.00034394 | 0.063864 | 0.0058755 | 0.00046367 | 0.00067941 | 0.06187 | 0.0048141 | 0.06356 | -66.7747 | 0.028878 | -66.746 | 56.2564 | 56.0556 | 56.2848 | -66.8146 | -66.7749 | 0.03241 | -66.8048 | 56.1619 | 56.3214 | 55.9354 | -67.0195 | -0.049787 | -0.053092 | -0.009907 | 0.018827 | 0.068614 | -0.25396 | -0.024719 | -0.25463 | -0.14759 | -0.010025 | -0.039951 | 0.21468 | 0.011851 | -0.37413 | 123.0212 | 122.8204 | 123.0496 | 66.7937 | -123.1241 | 122.9267 | 123.0862 | 122.7002 | 66.7972 | -123.329
64.7969 | 123.2346 | -66.7694 | 56.3644 | -0.0057996 | -0.0015706 | 0.00082041 | 0.066267 | -0.00034394 | 0.063864 | 0.013506 | 0.00025007 | 0.00025221 | 0.061657 | 0.0046005 | 0.06356 | -66.7793 | 0.033457 | -66.746 | 56.2518 | 56.0464 | 56.2756 | -66.8284 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3168 | 55.9354 | -67.0286 | -0.058947 | -0.1126 | -0.009909 | 0.023404 | 0.082351 | -0.31805 | -0.088808 | -0.25921 | -0.20252 | -0.010027 | -0.039953 | 0.21925 | -0.047659 | -0.42906 | 123.0212 | 122.8158 | 123.045 | 66.8029 | -123.1928 | 122.9313 | 123.0862 | 122.7048 | 66.7972 | -123.3931
65.7969 | 123.2803 | -66.7786 | 56.2958 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066267 | -0.0011987 | 0.064078 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.06187 | 0.0048141 | 0.063987 | -66.7885 | 0.033457 | -66.7506 | 56.2564 | 56.0464 | 56.2756 | -66.8329 | -66.7749 | 0.023253 | -66.8094 | 56.1619 | 56.3122 | 55.9354 | -67.0286 | -0.054371 | -0.039359 | -0.009911 | 0.027981 | 0.082352 | -0.24938 | -0.020143 | -0.25005 | -0.13386 | 0.003707 | -0.030798 | 0.21925 | 0.016427 | -0.3604 | 123.035 | 122.825 | 123.0542 | 66.812 | -123.1287 | 122.9405 | 123.0908 | 122.7139 | 66.8018 | -123.3244
66.7969 | 123.3215 | -66.7419 | 56.282 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066267 | -0.00077134 | 0.063437 | -0.001755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0052415 | 0.063773 | -66.7747 | 0.0243 | -66.746 | 56.2564 | 56.0647 | 56.2711 | -66.8375 | -66.7794 | 0.018674 | -66.8094 | 56.1573 | 56.3168 | 55.94 | -67.0286 | -0.095571 | -0.025626 | -0.032796 | -0.004062 | 0.091509 | -0.21733 | -0.010989 | -0.28667 | -0.1247 | -0.037493 | -0.067419 | 0.21925 | 0.034739 | -0.34208 | 122.9984 | 122.8067 | 123.013 | 66.7662 | -123.1196 | 122.8993 | 123.0587 | 122.6819 | 66.7606 | -123.3107
67.7969 | 123.2666 | -66.7969 | 56.3187 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066054 | -0.00055774 | 0.06365 | -0.001755 | 3.6274e-05 | 3.8406e-05 | 0.06187 | 0.0050277 | 0.063773 | -66.7793 | 0.033457 | -66.746 | 56.2564 | 56.0601 | 56.2573 | -66.8421 | -66.7703 | 0.027831 | -66.8048 | 56.1573 | 56.3168 | 55.9445 | -67.024 | -0.045218 | -0.062248 | 0.017557 | 0.05087 | 0.096088 | -0.25853 | -0.061347 | -0.22716 | -0.16133 | 0.026597 | -0.007908 | 0.21925 | -0.001883 | -0.37413 | 123.0533 | 122.857 | 123.0542 | 66.8303 | -123.1608 | 122.9542 | 123.1137 | 122.7414 | 66.8247 | -123.3427
68.7969 | 123.3627 | -66.7557 | 56.2592 | -0.0057996 | -0.0015706 | 0.00082041 | 0.066054 | -0.00077134 | 0.06365 | -0.0093855 | 0.00025007 | 0.00046581 | 0.062298 | 0.0048141 | 0.063987 | -66.7747 | 0.028878 | -66.7414 | 56.2564 | 56.051 | 56.2619 | -66.8284 | -66.7611 | 0.023253 | -66.8048 | 56.1573 | 56.3214 | 55.9445 | -67.024 | -0.07268 | -0.002738 | -0.019063 | 0.014249 | 0.086929 | -0.20818 | 0.002742 | -0.26836 | -0.10182 | -0.005445 | -0.049107 | 0.21925 | 0.062205 | -0.31462 | 123.0121 | 122.8066 | 123.0176 | 66.7846 | -123.0875 | 122.913 | 123.077 | 122.7002 | 66.7789 | -123.2832
69.7969 | 123.349 | -66.7419 | 56.3004 | 0.0018314 | -0.00092939 | 0.0010342 | 0.066481 | -0.00055774 | 0.06365 | -0.001755 | 0.00025007 | 0.00025221 | 0.061443 | 0.0046005 | 0.06356 | -66.7793 | 0.0243 | -66.746 | 56.2473 | 56.0189 | 56.2619 | -66.8375 | -66.7749 | 0.027831 | -66.8094 | 56.1619 | 56.3168 | 55.9308 | -67.0286 | -0.095571 | -0.053094 | -0.037375 | -0.004062 | 0.091509 | -0.28143 | -0.038457 | -0.28667 | -0.13844 | -0.032914 | -0.067419 | 0.21925 | 0.016428 | -0.36955 | 122.9892 | 122.7609 | 123.0038 | 66.7662 | -123.1379 | 122.9039 | 123.0587 | 122.6727 | 66.7698 | -123.329
70.7969 | 123.3215 | -66.7374 | 56.2775 | 0.0018314 | -0.0011432 | 0.0010342 | 0.066267 | -0.00077134 | 0.063864 | -0.001755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0050277 | 0.063773 | -66.7747 | 0.0243 | -66.7506 | 56.2518 | 56.0235 | 56.2619 | -66.8009 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3168 | 55.9354 | -67.024 | -0.063516 | -0.025627 | -0.037373 | -0.013217 | 0.050299 | -0.25396 | -0.015569 | -0.28667 | -0.11555 | -0.04207 | -0.071996 | 0.21468 | 0.039316 | -0.34209 | 122.9892 | 122.7609 | 122.9993 | 66.7617 | -123.0783 | 122.8993 | 123.0541 | 122.6727 | 66.7652 | -123.3015
71.7969 | 123.2346 | -66.7831 | 56.3141 | -0.0057996 | -0.0013568 | 0.00060681 | 0.066267 | -0.00055774 | 0.06365 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0043867 | 0.063987 | -66.7839 | 0.042614 | -66.7506 | 56.2518 | 56.0052 | 56.2665 | -66.8329 | -66.7749 | 0.027831 | -66.8002 | 56.1573 | 56.3122 | 55.94 | -67.0286 | -0.049793 | -0.062248 | -0.000754 | 0.032559 | 0.082352 | -0.3089 | -0.047611 | -0.24547 | -0.15675 | 0.008285 | -0.017063 | 0.22841 | -0.001884 | -0.37413 | 123.035 | 122.7883 | 123.0496 | 66.8258 | -123.147 | 122.9405 | 123.0953 | 122.7231 | 66.811 | -123.3427
72.7969 | 123.3444 | -66.7557 | 56.2775 | 0.0018314 | -0.0013568 | 0.00082041 | 0.066267 | -0.00055774 | 0.063437 | -0.0093855 | 0.00025007 | 0.00025221 | 0.061443 | 0.0048141 | 0.063773 | -66.7793 | 0.028878 | -66.7414 | 56.261 | 56.0464 | 56.2619 | -66.8329 | -66.7703 | 0.023253 | -66.8048 | 56.1528 | 56.3122 | 55.94 | -67.0286 | -0.077259 | -0.016471 | -0.023642 | 0.014249 | 0.091508 | -0.23107 | -0.015569 | -0.27294 | -0.12471 | -0.014602 | -0.049107 | 0.22383 | 0.034737 | -0.33751 | 123.0167 | 122.8021 | 123.0176 | 66.7846 | -123.1104 | 122.9084 | 123.0679 | 122.6956 | 66.7789 | -123.3061
73.7969 | 123.1934 | -66.806 | 56.3141 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066054 | -0.00077134 | 0.063437 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0050277 | 0.06356 | -66.7793 | 0.038035 | -66.746 | 56.2518 | 56.0601 | 56.2711 | -66.8146 | -66.7703 | 0.027831 | -66.8002 | 56.1619 | 56.3122 | 55.9354 | -67.0286 | -0.008589 | -0.062248 | 0.026712 | 0.060025 | 0.068614 | -0.25395 | -0.043033 | -0.22259 | -0.15217 | 0.035752 | 0.005825 | 0.22841 | -0.001884 | -0.37871 | 123.0579 | 122.8662 | 123.0771 | 66.8441 | -123.1287 | 122.9679 | 123.1182 | 122.7414 | 66.8339 | -123.3427
74.7969 | 123.3673 | -66.7145 | 56.3049 | -0.0057996 | -0.0011432 | 0.0010342 | 0.066054 | -0.00077134 | 0.063864 | 0.013506 | 0.00046367 | 3.8406e-05 | 0.06187 | 0.0046005 | 0.063773 | -66.7747 | 0.028878 | -66.7506 | 56.261 | 56.0693 | 56.2711 | -66.8375 | -66.7749 | 0.027831 | -66.8094 | 56.1573 | 56.3168 | 55.9354 | -67.0286 | -0.12304 | -0.043937 | -0.060261 | -0.036105 | 0.086931 | -0.23564 | -0.033878 | -0.31414 | -0.14759 | -0.060379 | -0.094884 | 0.21925 | 0.01185 | -0.36955 | 122.9755 | 122.7838 | 122.9855 | 66.7434 | -123.1424 | 122.8718 | 123.0313 | 122.6499 | 66.7423 | -123.3335
75.7969 | 123.2712 | -66.7969 | 56.3004 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066054 | -0.00098494 | 0.06365 | -0.0093855 | 0.00046367 | 0.00046581 | 0.061657 | 0.0046005 | 0.063346 | -66.7793 | 0.033457 | -66.746 | 56.2564 | 56.0464 | 56.2711 | -66.8284 | -66.784 | 0.023253 | -66.8094 | 56.1573 | 56.3214 | 55.9537 | -67.0286 | -0.031481 | -0.043937 | 0.017557 | 0.05087 | 0.082351 | -0.25396 | -0.0293 | -0.23174 | -0.14301 | 0.012861 | -0.012487 | 0.21925 | 0.021006 | -0.34666 | 123.0533 | 122.8433 | 123.0679 | 66.8303 | -123.1287 | 122.9542 | 123.1182 | 122.7506 | 66.8201 | -123.329
76.7969 | 123.3582 | -66.7465 | 56.2637 | -0.013431 | -0.0013568 | 0.00060681 | 0.066908 | -0.00077134 | 0.064291 | -0.0093855 | -0.00017733 | 0.00046581 | 0.06187 | 0.0048141 | 0.06356 | -66.7747 | 0.028878 | -66.746 | 56.2518 | 56.0372 | 56.2756 | -66.7597 | -66.7611 | 0.023253 | -66.8048 | 56.1528 | 56.3214 | 55.9445 | -67.0286 | -0.013151 | -0.011894 | -0.028218 | 0.000516 | 0.013667 | -0.22649 | 0.0119 | -0.28209 | -0.11097 | -0.0146 | -0.058262 | 0.22383 | 0.057627 | -0.3192 | 122.9984 | 122.7838 | 123.0222 | 66.7754 | -123.0234 | 122.8993 | 123.0679 | 122.6911 | 66.7698 | -123.2923
77.7969 | 123.2391 | -66.7831 | 56.3232 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066267 | -0.00055774 | 0.063864 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.062298 | 0.0054551 | 0.063346 | -66.7793 | 0.028878 | -66.746 | 56.2564 | 56.0235 | 56.2619 | -66.8375 | -66.7703 | 0.027831 | -66.8002 | 56.1528 | 56.3214 | 55.94 | -67.024 | -0.054372 | -0.066825 | 0.003824 | 0.037137 | 0.091509 | -0.29974 | -0.061345 | -0.2409 | -0.17048 | 0.012864 | -0.017063 | 0.22383 | -0.001882 | -0.38328 | 123.0396 | 122.8066 | 123.045 | 66.812 | -123.1608 | 122.9359 | 123.1045 | 122.7231 | 66.811 | -123.3473
78.7969 | 123.381 | -66.7374 | 56.2866 | -0.0057996 | -0.0015706 | 0.00082041 | 0.066695 | -0.00055774 | 0.063864 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0048141 | 0.06356 | -66.7747 | 0.038035 | -66.746 | 56.2564 | 56.0739 | 56.2665 | -66.8284 | -66.7703 | 0.041567 | -66.8048 | 56.1573 | 56.3076 | 55.9354 | -67.024 | -0.09099 | -0.030204 | -0.037373 | -0.008639 | 0.082351 | -0.21275 | -0.020145 | -0.28667 | -0.12928 | -0.032912 | -0.067417 | 0.21925 | 0.021003 | -0.35124 | 122.9938 | 122.8112 | 123.0038 | 66.7754 | -123.115 | 122.8947 | 123.045 | 122.6727 | 66.7789 | -123.3107
79.7969 | 123.2986 | -66.7419 | 56.3004 | 0.0018314 | -0.0013568 | 0.0010342 | 0.066267 | -0.00077134 | 0.063437 | -0.017016 | 0.00046367 | 0.00046581 | 0.062084 | 0.0050277 | 0.063346 | -66.7793 | 0.033457 | -66.7414 | 56.2564 | 56.0647 | 56.2665 | -66.8329 | -66.7794 | 0.027831 | -66.8094 | 56.1619 | 56.3122 | 55.9354 | -67.024 | -0.090992 | -0.043937 | -0.037375 | 0.000516 | 0.091508 | -0.23564 | -0.033878 | -0.28209 | -0.13844 | -0.037493 | -0.067419 | 0.21468 | 0.011849 | -0.36497 | 122.9984 | 122.8067 | 123.0084 | 66.7754 | -123.1333 | 122.9039 | 123.0541 | 122.6773 | 66.7698 | -123.3244
80.7969 | 123.2529 | -66.7877 | 56.3049 | -0.0057996 | -0.0013568 | 0.00082041 | 0.066481 | -0.00055774 | 0.063864 | -0.0093855 | 0.00046367 | 3.8406e-05 | 0.061443 | 0.0048141 | 0.063773 | -66.7702 | 0.033457 | -66.7506 | 56.2564 | 56.0556 | 56.2619 | -66.8329 | -66.7794 | 0.03241 | -66.8002 | 56.1619 | 56.3168 | 55.9354 | -67.0286 | -0.045215 | -0.048515 | 0.017559 | 0.037137 | 0.082352 | -0.24938 | -0.043035 | -0.2409 | -0.14301 | 0.008284 | -0.012485 | 0.22841 | 0.01185 | -0.36955 | 123.0441 | 122.8433 | 123.0496 | 66.8212 | -123.1379 | 122.9496 | 123.1045 | 122.7231 | 66.8201 | -123.3335
81.7969 | 123.2071 | -66.774 | 56.3416 | -0.0057996 | -0.0013568 | 0.00060681 | 0.057293 | -0.00055774 | 0.064078 | -0.001755 | 0.00025007 | 0.00025221 | 0.061443 | 0.0052415 | 0.063987 | -66.7747 | 0.028878 | -66.7506 | 56.2564 | 56.0739 | 56.2711 | -66.8421 | -66.7703 | 0.03241 | -66.8048 | 56.1573 | 56.3214 | 55.9308 | -67.0286 | -0.068106 | -0.085136 | -0.000752 | 0.023404 | 0.09151 | -0.26768 | -0.070499 | -0.25463 | -0.18421 | 0.003709 | -0.030796 | 0.22383 | -0.020193 | -0.41075 | 123.0304 | 122.8479 | 123.045 | 66.8029 | -123.1836 | 122.9313 | 123.0953 | 122.7048 | 66.8064 | -123.3702
82.7969 | 123.3444 | -66.7465 | 56.2775 | -0.013431 | -0.0011432 | 0.00060681 | 0.057079 | -0.00077134 | 0.06365 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0052415 | 0.06356 | -66.7747 | 0.033457 | -66.746 | 56.2518 | 56.0784 | 56.2756 | -66.8284 | -66.7703 | 0.03241 | -66.7956 | 56.1573 | 56.3168 | 55.94 | -67.0332 | -0.081835 | -0.025627 | -0.028218 | 0.000516 | 0.082351 | -0.19902 | -0.001833 | -0.28667 | -0.12013 | -0.023757 | -0.049105 | 0.23757 | 0.039316 | -0.33751 | 122.9984 | 122.825 | 123.0222 | 66.78 | -123.1058 | 122.9039 | 123.0633 | 122.6865 | 66.7789 | -123.3107
83.7969 | 123.1796 | -66.7969 | 56.3416 | 0.0018314 | -0.0015706 | 0.0010342 | 0.057079 | -0.00077134 | 0.06365 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.062084 | 0.0054551 | 0.06356 | -66.7747 | 0.033457 | -66.7414 | 56.2564 | 56.0098 | 56.2756 | -66.8421 | -66.7749 | 0.03241 | -66.8002 | 56.1528 | 56.3168 | 55.9308 | -67.0286 | -0.045218 | -0.085136 | 0.022136 | 0.055448 | 0.10067 | -0.33179 | -0.06592 | -0.23174 | -0.18879 | 0.022018 | -0.00333 | 0.22841 | -0.024771 | -0.41075 | 123.0533 | 122.8066 | 123.0725 | 66.8303 | -123.1836 | 122.9496 | 123.1137 | 122.7277 | 66.8293 | -123.3702
84.7969 | 123.2529 | -66.7465 | 56.337 | 0.0018314 | -0.0015706 | 0.00082041 | 0.057293 | -0.00077134 | 0.06365 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0054551 | 0.06356 | -66.7793 | 0.033457 | -66.746 | 56.2564 | 56.0784 | 56.2756 | -66.8329 | -66.7703 | 0.023253 | -66.8048 | 56.1619 | 56.3214 | 55.9354 | -67.024 | -0.086414 | -0.080558 | -0.032797 | 0.000516 | 0.08693 | -0.25853 | -0.061342 | -0.27752 | -0.17506 | -0.023757 | -0.058262 | 0.21925 | -0.015615 | -0.4016 | 123.0029 | 122.825 | 123.0222 | 66.78 | -123.1699 | 122.9084 | 123.0679 | 122.6819 | 66.7698 | -123.361
85.7969 | 123.2117 | -66.7923 | 56.3278 | -0.0057996 | -0.0017842 | 0.00082041 | 0.057079 | -0.00034394 | 0.064078 | -0.0093855 | 0.00025007 | 0.00067941 | 0.06187 | 0.0052415 | 0.06356 | -66.7793 | 0.028878 | -66.7506 | 56.2564 | 56.0281 | 56.2756 | -66.8009 | -66.7749 | 0.027831 | -66.8094 | 56.1619 | 56.3259 | 55.94 | -67.0286 | -0.008585 | -0.071403 | 0.012979 | 0.041714 | 0.050299 | -0.29974 | -0.052187 | -0.23632 | -0.1659 | 0.01744 | -0.017065 | 0.21925 | -0.001881 | -0.38786 | 123.0487 | 122.8204 | 123.0679 | 66.8212 | -123.1287 | 122.9542 | 123.1182 | 122.7323 | 66.8201 | -123.3564
86.7969 | 123.3215 | -66.7694 | 56.2775 | -0.0057996 | -0.0013568 | 0.0010342 | 0.057293 | -0.00077134 | 0.063437 | -0.001755 | -0.00017733 | 0.00025221 | 0.061657 | 0.0048141 | 0.06356 | -66.7747 | 0.033457 | -66.7506 | 56.2473 | 56.0647 | 56.2711 | -66.8192 | -66.7749 | 0.027831 | -66.8002 | 56.1619 | 56.3214 | 55.9308 | -67.024 | -0.049789 | -0.030206 | -0.00533 | 0.018826 | 0.068615 | -0.21275 | -0.006412 | -0.25463 | -0.11555 | -0.005448 | -0.030796 | 0.22383 | 0.043894 | -0.34666 | 123.0167 | 122.8341 | 123.0405 | 66.8029 | -123.0967 | 122.9313 | 123.0908 | 122.7002 | 66.7972 | -123.3015
87.7969 | 123.23 | -66.7831 | 56.3461 | -0.013431 | -0.0017842 | 0.0010342 | 0.057079 | -0.00098494 | 0.063864 | -0.0093855 | 0.00046367 | 0.00046581 | 0.061657 | 0.0052415 | 0.063773 | -66.7747 | 0.033457 | -66.746 | 56.2564 | 56.0098 | 56.2756 | -66.8375 | -66.784 | 0.03241 | -66.8094 | 56.1573 | 56.3259 | 55.9354 | -67.024 | -0.054372 | -0.089713 | 0.008403 | 0.037137 | 0.091509 | -0.33637 | -0.070497 | -0.2409 | -0.18879 | -0.000872 | -0.02622 | 0.21468 | -0.020191 | -0.41075 | 123.0396 | 122.7929 | 123.0588 | 66.8166 | -123.1836 | 122.9405 | 123.1091 | 122.7185 | 66.8156 | -123.3702
88.7969 | 123.3353 | -66.7511 | 56.2866 | 0.0018314 | -0.0013568 | 0.00082041 | 0.057293 | -0.00077134 | 0.06365 | -0.0093855 | 0.00025007 | 0.00067941 | 0.061657 | 0.0052415 | 0.063346 | -66.7747 | 0.033457 | -66.7506 | 56.2518 | 56.0647 | 56.2711 | -66.8329 | -66.7794 | 0.03241 | -66.8094 | 56.1482 | 56.3305 | 55.94 | -67.0286 | -0.081836 | -0.034782 | -0.02364 | 0.000516 | 0.082352 | -0.22191 | -0.015567 | -0.27752 | -0.13844 | -0.028337 | -0.058263 | 0.21925 | 0.043896 | -0.34666 | 123.0029 | 122.8158 | 123.0222 | 66.7846 | -123.1196 | 122.8993 | 123.0816 | 122.6911 | 66.7835 | -123.3152
89.7969 | 123.2025 | -66.7786 | 56.3049 | -0.0057996 | -0.00092939 | 0.00082041 | 0.056865 | -0.00098494 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.06187 | 0.0050277 | 0.063773 | -66.7793 | 0.033457 | -66.7506 | 56.2518 | 56.0601 | 56.2711 | -66.8375 | -66.7749 | 0.036989 | -66.8002 | 56.1665 | 56.3259 | 55.9354 | -67.024 | -0.05895 | -0.053093 | -0.000754 | 0.027981 | 0.086931 | -0.2448 | -0.033878 | -0.24547 | -0.13844 | 0.003707 | -0.021641 | 0.22383 | 0.021007 | -0.36955 | 123.0304 | 122.8387 | 123.0496 | 66.812 | -123.1424 | 122.9451 | 123.1045 | 122.7139 | 66.8156 | -123.329
90.7969 | 123.3032 | -66.7786 | 56.3049 | -0.0057996 | -0.0013568 | 0.00082041 | 0.057293 | -0.0011987 | 0.063864 | -0.001755 | 0.00025007 | 0.00025221 | 0.061443 | 0.0054551 | 0.063773 | -66.7747 | 0.038035 | -66.7552 | 56.2473 | 56.0601 | 56.2756 | -66.8375 | -66.7749 | 0.027831 | -66.8002 | 56.1573 | 56.3259 | 55.9308 | -67.0286 | -0.05895 | -0.057672 | 0.003825 | 0.023403 | 0.082353 | -0.2448 | -0.029299 | -0.25005 | -0.14759 | 0.003707 | -0.021641 | 0.22841 | 0.021007 | -0.37413 | 123.0258 | 122.8387 | 123.0542 | 66.8166 | -123.1424 | 122.9359 | 123.1045 | 122.7094 | 66.8064 | -123.3335
91.7969 | 123.1979 | -66.7877 | 56.3187 | 0.0018314 | -0.0017842 | 0.0010342 | 0.057293 | -0.00055774 | 0.063864 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0050277 | 0.06356 | -66.7793 | 0.033457 | -66.746 | 56.2518 | 56.0647 | 56.2848 | -66.8513 | -66.7749 | 0.027831 | -66.8002 | 56.1573 | 56.3214 | 55.9308 | -67.0286 | -0.063531 | -0.066826 | 0.008402 | 0.041715 | 0.10525 | -0.25395 | -0.033875 | -0.2409 | -0.16133 | 0.012863 | -0.012485 | 0.22841 | 0.002695 | -0.38786 | 123.0396 | 122.8524 | 123.0725 | 66.8212 | -123.1699 | 122.9451 | 123.1091 | 122.7185 | 66.8156 | -123.3473
92.7969 | 123.2391 | -66.7831 | 56.3141 | -0.013431 | -0.0011432 | 0.0010342 | 0.057079 | -0.00098494 | 0.063437 | -0.001755 | -0.00017733 | 0.00025221 | 0.06187 | 0.0052415 | 0.06356 | -66.7793 | 0.0243 | -66.7414 | 56.2473 | 56.0556 | 56.2711 | -66.8375 | -66.7657 | 0.027831 | -66.8094 | 56.1528 | 56.3168 | 55.9308 | -67.0378 | -0.054372 | -0.066827 | 0.003824 | 0.041715 | 0.096087 | -0.25853 | -0.043033 | -0.25463 | -0.16133 | 0.017443 | -0.02622 | 0.22841 | 0.002695 | -0.38329 | 123.0304 | 122.8387 | 123.0542 | 66.8074 | -123.1516 | 122.9359 | 123.0999 | 122.7139 | 66.811 | -123.3519
93.7969 | 123.1979 | -66.7877 | 56.3324 | 0.0018314 | -0.0015706 | 0.0010342 | 0.057079 | -0.00098494 | 0.06365 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0054551 | 0.06356 | -66.7747 | 0.0243 | -66.746 | 56.2564 | 56.051 | 56.2756 | -66.8329 | -66.7703 | 0.036989 | -66.8002 | 56.1573 | 56.3168 | 55.94 | -67.0378 | -0.045215 | -0.07598 | 0.012981 | 0.041715 | 0.08693 | -0.28142 | -0.056764 | -0.25005 | -0.17506 | 0.017442 | -0.012485 | 0.23757 | -0.015615 | -0.39244 | 123.0441 | 122.8387 | 123.0634 | 66.812 | -123.1653 | 122.9451 | 123.1045 | 122.7277 | 66.8247 | -123.3702
94.7969 | 123.2208 | -66.774 | 56.3141 | -0.013431 | -0.0017842 | 0.00060681 | 0.057293 | -0.00077134 | 0.06365 | 0.0058755 | 3.6274e-05 | 3.8406e-05 | 0.06187 | 0.0052415 | 0.063346 | -66.7793 | 0.028878 | -66.7414 | 56.2564 | 56.0922 | 56.2711 | -66.8467 | -66.7794 | 0.036989 | -66.8002 | 56.1619 | 56.3168 | 55.9674 | -67.0286 | -0.072685 | -0.05767 | -0.005331 | 0.03256 | 0.10524 | -0.2219 | -0.043033 | -0.25463 | -0.15217 | -0.005449 | -0.026218 | 0.22841 | 0.002695 | -0.34666 | 123.0304 | 122.8662 | 123.045 | 66.8029 | -123.1608 | 122.9359 | 123.0908 | 122.7414 | 66.811 | -123.3427
95.7969 | 123.1934 | -66.774 | 56.3278 | -0.0057996 | -0.0017842 | 0.0010342 | 0.057506 | -0.00098494 | 0.063864 | 0.0058755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0050277 | 0.06356 | -66.7747 | 0.042614 | -66.7643 | 56.2885 | 56.225 | 56.3123 | -66.9016 | -66.7794 | 0.041567 | -66.8002 | 56.1619 | 56.3168 | 56.2834 | -67.024 | -0.12763 | -0.039354 | -0.000752 | 0.009669 | 0.1373 | -0.10285 | -0.015558 | -0.25005 | -0.1659 | -0.005449 | -0.026218 | 0.22383 | -0.011038 | -0.044466 | 123.0625 | 122.999 | 123.0862 | 66.8166 | -123.2294 | 122.9359 | 123.0908 | 123.0573 | 66.8156 | -123.3519
96.7969 | 123.3124 | -66.7419 | 56.2912 | -0.013431 | -0.0015706 | 0.0010342 | 0.057506 | -0.00055774 | 0.063437 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.06187 | 0.0050277 | 0.063346 | -66.7793 | 0.042614 | -66.7552 | 56.2793 | 56.2204 | 56.3031 | -66.897 | -66.7749 | 0.041567 | -66.8048 | 56.1619 | 56.3122 | 56.3017 | -67.024 | -0.1551 | -0.01189 | -0.037375 | -0.013218 | 0.14188 | -0.070804 | 0.011905 | -0.28209 | -0.12928 | -0.032914 | -0.06284 | 0.21925 | 0.021004 | 0.01047 | 123.0213 | 122.9623 | 123.045 | 66.7846 | -123.1882 | 122.9039 | 123.0541 | 123.0436 | 66.7835 | -123.3152
97.7969 | 123.2346 | -66.8152 | 56.337 | -0.0057996 | -0.0015706 | 0.00060681 | 0.057293 | -0.00077134 | 0.06365 | -0.001755 | 3.6274e-05 | 3.8406e-05 | 0.06187 | 0.0054551 | 0.063346 | -66.7793 | 0.047193 | -66.7552 | 56.2839 | 56.2296 | 56.3031 | -66.897 | -66.7794 | 0.041567 | -66.8002 | 56.1619 | 56.3214 | 56.2879 | -67.0195 | -0.081854 | -0.053088 | 0.035868 | 0.060025 | 0.14188 | -0.10742 | -0.033871 | -0.20427 | -0.17506 | 0.03575 | 0.014981 | 0.21925 | -0.015615 | -0.049042 | 123.0991 | 123.0447 | 123.1183 | 66.8624 | -123.234 | 122.9771 | 123.1365 | 123.1031 | 66.8568 | -123.3564
98.7969 | 123.3032 | -66.7694 | 56.2912 | -0.0057996 | -0.0013568 | 0.00082041 | 0.057506 | -0.00077134 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0054551 | 0.063346 | -66.7839 | 0.038035 | -66.7506 | 56.2885 | 56.2296 | 56.3077 | -66.9016 | -66.784 | 0.046146 | -66.8002 | 56.1573 | 56.3122 | 56.2925 | -67.0286 | -0.13221 | -0.002733 | -0.014487 | 0.018826 | 0.15104 | -0.061647 | 0.016484 | -0.25921 | -0.13386 | -0.014605 | -0.030796 | 0.22841 | 0.021004 | 0.001312 | 123.0579 | 122.999 | 123.0771 | 66.8074 | -123.1928 | 122.9267 | 123.0816 | 123.0619 | 66.8156 | -123.3198
99.7969 | 123.2025 | -66.7694 | 56.3324 | -0.013431 | -0.0015706 | 0.0010342 | 0.057506 | -0.00077134 | 0.06365 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061657 | 0.0054551 | 0.06356 | -66.7702 | 0.038035 | -66.7643 | 56.2839 | 56.2204 | 56.3031 | -66.9062 | -66.7794 | 0.046146 | -66.8048 | 56.1528 | 56.3168 | 56.2925 | -67.024 | -0.13679 | -0.04851 | -0.000752 | 0.005091 | 0.14188 | -0.112 | -0.029293 | -0.25463 | -0.17964 | -0.010027 | -0.035374 | 0.21925 | -0.015615 | -0.039886 | 123.0533 | 122.9898 | 123.0725 | 66.8074 | -123.2386 | 122.9222 | 123.0862 | 123.0619 | 66.8156 | -123.3564
100.7969 | 123.262 | -66.7831 | 56.2912 | -0.013431 | -0.0015706 | 0.00060681 | 0.057506 | -0.00098494 | 0.063864 | -0.001755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0054551 | 0.06356 | -66.7747 | 0.047193 | -66.7643 | 56.293 | 56.2296 | 56.3168 | -66.9016 | -66.7886 | 0.046146 | -66.8002 | 56.1482 | 56.3259 | 56.3017 | -67.0286 | -0.11848 | 0.001845 | 0.008403 | 0.018824 | 0.1373 | -0.061647 | 0.025641 | -0.24547 | -0.14302 | -0.005451 | -0.017063 | 0.22841 | 0.03474 | 0.01047 | 123.0762 | 123.0127 | 123.1 | 66.8303 | -123.1928 | 122.9313 | 123.1091 | 123.0848 | 66.8293 | -123.3198
101.7969 | 123.3307 | -66.774 | 56.3507 | -0.0057996 | -0.0015706 | 0.0010342 | 0.05772 | -0.00077134 | 0.064505 | -0.001755 | -0.00017733 | -0.00017519 | 0.06187 | 0.0054551 | 0.063346 | -66.7747 | 0.042614 | -66.7735 | 56.3022 | 56.2433 | 56.3123 | -66.9062 | -66.7932 | 0.046146 | -66.8048 | 56.1619 | 56.3214 | 56.3154 | -67.0286 | -0.13221 | -0.048507 | -0.000752 | 0.000513 | 0.13272 | -0.10742 | -0.038446 | -0.25463 | -0.18879 | -0.019185 | -0.030796 | 0.22383 | -0.029348 | -0.035304 | 123.0762 | 123.0173 | 123.0862 | 66.8166 | -123.2569 | 122.9359 | 123.0953 | 123.0894 | 66.8201 | -123.3793
102.7969 | 123.2574 | -66.7969 | 56.282 | 0.0018314 | -0.0019978 | 0.0010342 | 0.057079 | -0.0011987 | 0.063864 | 0.0058755 | 0.00025007 | 0.00025221 | 0.06187 | 0.0054551 | 0.06356 | -66.7747 | 0.047193 | -66.7689 | 56.3022 | 56.2387 | 56.3214 | -66.9062 | -66.7886 | 0.046146 | -66.8048 | 56.1573 | 56.3214 | 56.2421 | -67.0286 | -0.10932 | 0.020158 | 0.022136 | 0.027979 | 0.1373 | -0.043333 | 0.039376 | -0.23174 | -0.1247 | 0.008282 | -0.007908 | 0.22383 | 0.039317 | -0.039896 | 123.0991 | 123.0356 | 123.1183 | 66.8441 | -123.1882 | 122.9542 | 123.1182 | 123.039 | 66.843 | -123.3107
103.7969 | 123.1888 | -66.8015 | 56.3187 | -0.0057996 | -0.0019978 | 0.0016752 | 0.057293 | -0.0011987 | 0.064078 | 0.013506 | 3.6274e-05 | 3.8406e-05 | 0.06187 | 0.0056687 | 0.06356 | -66.7747 | 0.051771 | -66.7781 | 56.3022 | 56.2433 | 56.326 | -66.9154 | -66.7977 | 0.055303 | -66.8048 | 56.1619 | 56.3214 | 56.146 | -67.024 | -0.1139 | -0.016464 | 0.026714 | 0.0234 | 0.1373 | -0.075376 | 0.007332 | -0.22258 | -0.15675 | 0.003703 | -0.00333 | 0.21925 | 0.002695 | -0.17267 | 123.1037 | 123.0447 | 123.1274 | 66.8532 | -123.234 | 122.9634 | 123.1228 | 122.9474 | 66.8568 | -123.3427
104.7969 | 123.2941 | -66.7603 | 56.2958 | -0.0057996 | -0.0015706 | 0.00082041 | 0.057506 | -0.00077134 | 0.063864 | -0.0093855 | 0.00025007 | 0.00025221 | 0.061443 | 0.0054551 | 0.063132 | -66.7747 | 0.042614 | -66.7689 | 56.2976 | 56.2341 | 56.3123 | -66.9016 | -66.7886 | 0.046146 | -66.8094 | 56.1619 | 56.3214 | 56.3062 | -67.0332 | -0.14136 | 0.001847 | -0.014485 | -0.008642 | 0.13272 | -0.061645 | 0.016486 | -0.27294 | -0.13386 | -0.028339 | -0.049108 | 0.22383 | 0.025584 | 0.010471 | 123.0579 | 122.9944 | 123.0725 | 66.8029 | -123.1974 | 122.9222 | 123.0816 | 123.0665 | 66.8064 | -123.329
105.7969 | 123.1842 | -66.7877 | 56.3141 | -0.013431 | -0.0017842 | 0.0010342 | 0.057506 | -0.00077134 | 0.06365 | -0.017016 | 0.00025007 | 3.8406e-05 | 0.061443 | 0.0052415 | 0.063132 | -66.7702 | 0.038035 | -66.746 | 56.2793 | 56.1517 | 56.3031 | -66.8925 | -66.7703 | 0.046146 | -66.8002 | 56.1665 | 56.3259 | 56.2879 | -67.0286 | -0.10474 | -0.034778 | 0.017559 | 0.041715 | 0.14646 | -0.16238 | -0.010983 | -0.2409 | -0.14759 | 0.017442 | -0.012485 | 0.22841 | 0.011852 | -0.026154 | 123.067 | 122.9394 | 123.0908 | 66.8258 | -123.2065 | 122.9542 | 123.1137 | 123.0757 | 66.8339 | -123.3427
106.7969 | 123.2162 | -66.7465 | 56.3004 | 0.0018314 | -0.0015706 | 0.00060681 | 0.057293 | -0.00077134 | 0.063864 | -0.001755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0052415 | 0.063346 | -66.7793 | 0.038035 | -66.7368 | 56.2656 | 56.1197 | 56.2894 | -66.8741 | -66.7657 | 0.036989 | -66.8002 | 56.1619 | 56.3168 | 56.2788 | -67.0286 | -0.12762 | -0.03478 | -0.032797 | 0.009673 | 0.1373 | -0.1807 | -0.010985 | -0.28209 | -0.13844 | -0.019178 | -0.053684 | 0.22841 | 0.016428 | -0.021578 | 123.0121 | 122.8662 | 123.0359 | 66.7846 | -123.1745 | 122.9084 | 123.0633 | 123.0253 | 66.7835 | -123.329
107.7969 | 123.0515 | -66.7969 | 56.2775 | -0.0057996 | -0.0013568 | 0.00060681 | 0.058147 | -0.00077134 | 0.06365 | 0.0058755 | 0.00025007 | 0.00025221 | 0.062084 | 0.0054551 | 0.063346 | -66.7793 | 0.028878 | -66.746 | 56.2518 | 56.1288 | 56.2756 | -66.865 | -66.7657 | 0.027831 | -66.8002 | 56.1573 | 56.3168 | 56.2696 | -67.0286 | -0.068112 | -0.025627 | 0.017557 | 0.05087 | 0.11898 | -0.14865 | -0.001833 | -0.23174 | -0.12013 | 0.031176 | -0.00333 | 0.22841 | 0.039316 | -0.007848 | 123.0487 | 122.9257 | 123.0725 | 66.8258 | -123.1425 | 122.9542 | 123.1137 | 123.0665 | 66.8247 | -123.3061
108.7969 | 123.1934 | -66.7694 | 56.3141 | -0.013431 | -0.0013568 | 0.00082041 | 0.057293 | -0.00077134 | 0.06365 | 0.0058755 | 0.00046367 | 0.00025221 | 0.06187 | 0.0052415 | 0.063773 | -66.7747 | 0.0243 | -66.7414 | 56.2518 | 56.1242 | 56.2711 | -66.865 | -66.7657 | 0.036989 | -66.8048 | 56.1528 | 56.3214 | 56.2238 | -67.0378 | -0.095578 | -0.062248 | -0.00533 | 0.027982 | 0.12356 | -0.18985 | -0.043033 | -0.26837 | -0.16133 | 0.00371 | -0.035374 | 0.23299 | 0.007273 | -0.090255 | 123.0212 | 122.8936 | 123.0405 | 66.7937 | -123.1791 | 122.9222 | 123.0908 | 122.9932 | 66.8064 | -123.3519
109.7969 | 123.2162 | -66.7603 | 56.3278 | -0.0057996 | -0.0015706 | 0.0010342 | 0.057506 | -0.00098494 | 0.06365 | -0.001755 | 0.00046367 | 0.00046581 | 0.061443 | 0.0054551 | 0.06356 | -66.7793 | 0.033457 | -66.7368 | 56.2473 | 56.1197 | 56.2711 | -66.8513 | -66.7703 | 0.03241 | -66.7956 | 56.1573 | 56.3214 | 56.233 | -67.024 | -0.090997 | -0.08056 | -0.019064 | 0.023406 | 0.1144 | -0.20816 | -0.056766 | -0.26378 | -0.17048 | -0.010024 | -0.035372 | 0.22841 | -0.00646 | -0.09483 | 123.0075 | 122.8799 | 123.0313 | 66.7937 | -123.1791 | 122.9176 | 123.0816 | 122.9932 | 66.7927 | -123.3519
110.7969 | 123.3215 | -66.7648 | 56.2775 | -0.013431 | -0.0015706 | 0.00082041 | 0.05772 | -0.00055774 | 0.063864 | 0.0058755 | 0.00025007 | 3.8406e-05 | 0.06187 | 0.0058825 | 0.063346 | -66.7747 | 0.033457 | -66.7368 | 56.2518 | 56.1563 | 56.2619 | -66.8421 | -66.7703 | 0.03241 | -66.8048 | 56.1573 | 56.3259 | 56.2193 | -67.024 | -0.077261 | -0.025627 | -0.009907 | 0.027984 | 0.10525 | -0.12118 | -0.015569 | -0.25921 | -0.12013 | -0.005446 | -0.039951 | 0.21925 | 0.048473 | -0.058212 | 123.0167 | 122.9211 | 123.0267 | 66.7983 | -123.1196 | 122.9222 | 123.0908 | 122.9841 | 66.7972 | -123.3015
111.7969 | 123.23 | -66.7511 | 56.3324 | 0.0018314 | -0.0015706 | 0.00060681 | 0.057506 | -0.00098494 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.06187 | 0.0054551 | 0.06356 | -66.7793 | 0.0243 | -66.746 | 56.2518 | 56.1517 | 56.2711 | -66.7734 | -66.7703 | 0.027831 | -66.8048 | 56.1573 | 56.3168 | 56.059 | -67.024 | -0.02231 | -0.080558 | -0.028219 | 0.005094 | 0.027404 | -0.18069 | -0.061343 | -0.27294 | -0.17506 | -0.019179 | -0.053684 | 0.21925 | -0.015615 | -0.27339 | 123.0029 | 122.9028 | 123.0222 | 66.7754 | -123.1058 | 122.9084 | 123.0679 | 122.8101 | 66.7789 | -123.3564
112.7969 | 123.2162 | -66.7877 | 56.3004 | -0.013431 | -0.0015706 | 0.00060681 | 0.05772 | -0.00077134 | 0.06365 | -0.001755 | -0.00017733 | 0.00046581 | 0.061657 | 0.0054551 | 0.06356 | -66.7747 | 0.0243 | -66.746 | 56.2427 | 56.1517 | 56.2756 | -66.8467 | -66.7749 | 0.03241 | -66.7956 | 56.1528 | 56.3122 | 56.0041 | -67.0286 | -0.058952 | -0.057672 | 0.012981 | 0.041715 | 0.10067 | -0.14864 | -0.024721 | -0.2409 | -0.14759 | 0.012863 | -0.007906 | 0.23299 | 0.011849 | -0.2963 | 123.0304 | 122.9394 | 123.0634 | 66.812 | -123.147 | 122.9405 | 123.0999 | 122.7918 | 66.8201 | -123.329
113.7969 | 123.2574 | -66.7831 | 56.3187 | 0.0018314 | -0.0015706 | 0.00060681 | 0.057293 | -0.0011987 | 0.063437 | -0.001755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0054551 | 0.063132 | -66.7747 | 0.038035 | -66.7506 | 56.2427 | 56.1471 | 56.2711 | -66.8467 | -66.7749 | 0.027831 | -66.8002 | 56.1573 | 56.3122 | 56.0544 | -67.0286 | -0.06353 | -0.075983 | 0.008403 | 0.032559 | 0.096089 | -0.17153 | -0.047611 | -0.24547 | -0.16133 | 0.008285 | -0.017063 | 0.22841 | -0.006462 | -0.26424 | 123.0258 | 122.9303 | 123.0542 | 66.8212 | -123.1653 | 122.9405 | 123.0953 | 122.8376 | 66.811 | -123.3473
114.7969 | 123.1934 | -66.7923 | 56.3141 | -0.0057996 | -0.0017842 | 0.00060681 | 0.057506 | -0.00077134 | 0.063864 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061657 | 0.0052415 | 0.06356 | -66.7747 | 0.028878 | -66.746 | 56.2427 | 56.138 | 56.2756 | -66.8467 | -66.7749 | 0.036989 | -66.7956 | 56.1619 | 56.3168 | 56.0544 | -67.0286 | -0.054375 | -0.071405 | 0.017558 | 0.046292 | 0.10067 | -0.17611 | -0.038454 | -0.23632 | -0.15217 | 0.01744 | -0.003329 | 0.23299 | 0.002695 | -0.25966 | 123.035 | 122.9303 | 123.0679 | 66.8212 | -123.1608 | 122.9542 | 123.1091 | 122.8467 | 66.8293 | -123.3427
115.7969 | 123.2529 | -66.7831 | 56.3416 | 0.0018314 | -0.0013568 | 0.00082041 | 0.057293 | -0.00098494 | 0.06365 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061657 | 0.0054551 | 0.06356 | -66.7793 | 0.028878 | -66.746 | 56.2473 | 56.1517 | 56.2711 | -66.8558 | -66.7749 | 0.027831 | -66.8002 | 56.1528 | 56.3214 | 56.1323 | -67.0286 | -0.072688 | -0.094293 | 0.003824 | 0.037137 | 0.10983 | -0.18984 | -0.070499 | -0.24547 | -0.18879 | 0.008285 | -0.017063 | 0.22841 | -0.020193 | -0.20929 | 123.0304 | 122.9349 | 123.0542 | 66.812 | -123.1974 | 122.9359 | 123.1045 | 122.9154 | 66.811 | -123.3702
116.7969 | 123.2117 | -66.7603 | 56.3095 | -0.0057996 | -0.0015706 | 0.00082041 | 0.057506 | -0.00098494 | 0.063864 | -0.001755 | 0.00025007 | 0.00046581 | 0.06187 | 0.0054551 | 0.063346 | -66.7839 | 0.033457 | -66.7506 | 56.2427 | 56.138 | 56.2711 | -66.8513 | -66.7657 | 0.027831 | -66.8002 | 56.1619 | 56.3168 | 56.1597 | -67.0286 | -0.090997 | -0.066827 | -0.023642 | 0.009671 | 0.10067 | -0.17153 | -0.038455 | -0.26836 | -0.14759 | -0.005445 | -0.039951 | 0.22841 | 0.007273 | -0.14978 | 123.0029 | 122.8982 | 123.0313 | 66.7937 | -123.1608 | 122.9222 | 123.077 | 122.92 | 66.7881 | -123.3381
117.7969 | 123.2574 | -66.7374 | 56.3278 | 0.0018314 | -0.0017842 | 0.00082041 | 0.057079 | -0.00098494 | 0.06365 | -0.0093855 | -0.00017733 | 3.8406e-05 | 0.061657 | 0.0052415 | 0.063346 | -66.7793 | 0.033457 | -66.746 | 56.2473 | 56.1517 | 56.2756 | -66.8604 | -66.7703 | 0.03241 | -66.8002 | 56.1619 | 56.3076 | 56.0911 | -67.0286 | -0.12304 | -0.08056 | -0.041952 | -0.008639 | 0.1144 | -0.17611 | -0.052187 | -0.29125 | -0.1659 | -0.032912 | -0.062839 | 0.22841 | -0.020196 | -0.23677 | 122.9846 | 122.8891 | 123.013 | 66.7708 | -123.1882 | 122.8993 | 123.045 | 122.8284 | 66.7698 | -123.3564
118.7969 | 123.2117 | -66.7923 | 56.3324 | -0.013431 | -0.0019978 | 0.00082041 | 0.057293 | -0.00077134 | 0.063437 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.061443 | 0.0056687 | 0.06356 | -66.7793 | 0.033457 | -66.746 | 56.2335 | 56.1471 | 56.2665 | -66.8513 | -66.7749 | 0.027831 | -66.8048 | 56.1573 | 56.3214 | 56.1231 | -67.024 | -0.058954 | -0.098872 | 0.012979 | 0.046292 | 0.10525 | -0.18527 | -0.065921 | -0.23174 | -0.17506 | 0.01744 | -0.012486 | 0.21925 | -0.011037 | -0.20929 | 123.0258 | 122.9394 | 123.0588 | 66.8258 | -123.1836 | 122.9496 | 123.1137 | 122.9154 | 66.8201 | -123.3564
119.7969 | 123.2574 | -66.7648 | 56.3416 | -0.0057996 | -0.00071579 | 0.00082041 | 0.057079 | -0.0011987 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0054551 | 0.063132 | -66.7747 | 0.028878 | -66.746 | 56.2427 | 56.1471 | 56.2756 | -66.8513 | -66.7749 | 0.036989 | -66.8002 | 56.1619 | 56.3214 | 56.1826 | -67.0332 | -0.086419 | -0.098871 | -0.009907 | 0.018827 | 0.10525 | -0.19442 | -0.06592 | -0.26836 | -0.17964 | -0.010025 | -0.035373 | 0.23299 | -0.020193 | -0.15893 | 123.0075 | 122.912 | 123.0405 | 66.7937 | -123.1928 | 122.9267 | 123.0862 | 122.9475 | 66.8018 | -123.3747
120.7969 | 123.2162 | -66.7786 | 56.3049 | 0.0094624 | -0.0019978 | 0.00060681 | 0.057293 | -0.00034394 | 0.06365 | -0.001755 | 3.6274e-05 | 3.8406e-05 | 0.061229 | 0.0050277 | 0.063346 | -66.7793 | 0.033457 | -66.746 | 56.2518 | 56.1471 | 56.2665 | -66.8513 | -66.7749 | 0.041567 | -66.8002 | 56.1619 | 56.3214 | 56.1414 | -67.0286 | -0.072687 | -0.053093 | -0.000754 | 0.032559 | 0.10525 | -0.1578 | -0.038456 | -0.25005 | -0.14301 | 0.003707 | -0.021641 | 0.22841 | 0.016428 | -0.16351 | 123.0304 | 122.9257 | 123.045 | 66.812 | -123.1562 | 122.9405 | 123.0999 | 122.92 | 66.8201 | -123.3335
121.7969 | 123.2071 | -66.7557 | 56.3232 | 0.0018314 | -0.0017842 | 0.00060681 | 0.057506 | -0.0011987 | 0.063223 | 0.0058755 | 0.00067727 | 0.00067941 | 0.061657 | 0.0054551 | 0.063132 | -66.7793 | 0.033457 | -66.746 | 56.2381 | 56.1609 | 56.2756 | -66.8513 | -66.7703 | 0.023253 | -66.8002 | 56.1573 | 56.3122 | 56.0727 | -67.0286 | -0.095575 | -0.085138 | -0.023642 | 0.009671 | 0.10525 | -0.16237 | -0.047609 | -0.27294 | -0.1659 | -0.014602 | -0.044529 | 0.22841 | -0.011039 | -0.2505 | 122.9938 | 122.9165 | 123.0313 | 66.7891 | -123.1745 | 122.913 | 123.0679 | 122.8284 | 66.7789 | -123.3519
122.7969 | 123.2529 | -66.7557 | 56.3278 | 0.0018314 | -0.0015706 | 0.0012478 | 0.057506 | -0.00098494 | 0.063864 | -0.0093855 | 0.00025007 | 0.00025221 | 0.061657 | 0.0054551 | 0.06356 | -66.7747 | 0.033457 | -66.746 | 56.2518 | 56.1426 | 56.2665 | -66.8513 | -66.7749 | 0.03241 | -66.8048 | 56.1528 | 56.3214 | 56.0865 | -67.0286 | -0.095575 | -0.075981 | -0.019063 | 0.009671 | 0.10525 | -0.18527 | -0.061344 | -0.27294 | -0.17506 | -0.019181 | -0.049107 | 0.22383 | -0.00646 | -0.24135 | 123.0075 | 122.8982 | 123.0222 | 66.7891 | -123.1791 | 122.9084 | 123.077 | 122.8422 | 66.7881 | -123.3564
123.7969 | 123.2666 | -66.7511 | 56.3416 | 0.0018314 | -0.0015706 | 0.00082041 | 0.05772 | -0.00098494 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0058825 | 0.06356 | -66.7793 | 0.038035 | -66.7506 | 56.2473 | 56.1471 | 56.2711 | -66.8467 | -66.7749 | 0.027831 | -66.8002 | 56.1619 | 56.3168 | 56.0865 | -67.0332 | -0.095573 | -0.094293 | -0.028219 | 0.000516 | 0.096089 | -0.19442 | -0.070499 | -0.2821 | -0.17964 | -0.023758 | -0.049106 | 0.23299 | -0.024771 | -0.25508 | 122.9984 | 122.8982 | 123.0222 | 66.7891 | -123.1882 | 122.913 | 123.0679 | 122.8376 | 66.7789 | -123.3747
124.7969 | 123.262 | -66.7694 | 56.3095 | 0.0094624 | -0.0015706 | 0.00082041 | 0.057506 | -0.00098494 | 0.06365 | -0.001755 | 0.00046367 | 3.8406e-05 | 0.061657 | 0.0054551 | 0.06356 | -66.7747 | 0.033457 | -66.7414 | 56.2473 | 56.1654 | 56.2802 | -66.8467 | -66.7657 | 0.03241 | -66.7956 | 56.1619 | 56.3168 | 56.0407 | -67.0286 | -0.077263 | -0.062249 | -0.00533 | 0.027982 | 0.10524 | -0.14406 | -0.029298 | -0.25921 | -0.14759 | 0.00371 | -0.026217 | 0.23299 | 0.007273 | -0.26882 | 123.0167 | 122.9349 | 123.0496 | 66.8029 | -123.1562 | 122.9313 | 123.0862 | 122.8101 | 66.8018 | -123.3381
125.7969 | 123.2208 | -66.7694 | 56.3278 | 0.0094624 | -0.0017842 | 0.00060681 | 0.057506 | -0.00098494 | 0.06365 | 0.0058755 | -0.00017733 | 0.00046581 | 0.061443 | 0.0054551 | 0.063346 | -66.7702 | 0.0243 | -66.7368 | 56.2381 | 56.1471 | 56.2665 | -66.8467 | -66.7703 | 0.027831 | -66.8048 | 56.1573 | 56.3168 | 56.0773 | -67.024 | -0.077263 | -0.089716 | -0.000752 | 0.032561 | 0.10982 | -0.18069 | -0.061344 | -0.25463 | -0.17048 | -0.000869 | -0.035374 | 0.21925 | -0.011038 | -0.2505 | 123.0075 | 122.9165 | 123.0359 | 66.7937 | -123.1745 | 122.9267 | 123.0862 | 122.8467 | 66.7972 | -123.3519
126.7969 | 123.2483 | -66.7511 | 56.3095 | 0.0018314 | -0.0017842 | 0.00082041 | 0.05772 | -0.00098494 | 0.063864 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061657 | 0.0056687 | 0.063132 | -66.7702 | 0.033457 | -66.7552 | 56.2473 | 56.1563 | 56.2756 | -66.8467 | -66.7703 | 0.03241 | -66.7956 | 56.1573 | 56.3214 | 56.0544 | -67.0332 | -0.095573 | -0.062249 | -0.019062 | -0.004062 | 0.091511 | -0.15322 | -0.033876 | -0.2821 | -0.15217 | -0.019179 | -0.044527 | 0.23757 | 0.011851 | -0.25509 | 122.9984 | 122.9074 | 123.0267 | 66.7846 | -123.1562 | 122.9084 | 123.0725 | 122.8055 | 66.7835 | -123.3427
127.7969 | 123.2071 | -66.7511 | 56.3324 | 0.0094624 | -0.0017842 | 0.0010342 | 0.057506 | -0.00077134 | 0.063864 | 0.013506 | 3.6274e-05 | -0.00017519 | 0.061443 | 0.0056687 | 0.063132 | -66.7656 | 0.028878 | -66.7506 | 56.2473 | 56.1471 | 56.2711 | -66.8421 | -66.7657 | 0.027831 | -66.791 | 56.1573 | 56.3168 | 56.0636 | -67.0332 | -0.090994 | -0.085137 | -0.014484 | 0.000516 | 0.09151 | -0.18527 | -0.061343 | -0.2821 | -0.17506 | -0.0146 | -0.039948 | 0.24215 | -0.015615 | -0.26882 | 122.9984 | 122.8982 | 123.0222 | 66.78 | -123.1745 | 122.9084 | 123.0679 | 122.8147 | 66.7789 | -123.3656
128.7969 | 123.2574 | -66.7511 | 56.3141 | 0.0018314 | -0.0015706 | 0.00082041 | 0.057293 | -0.00077134 | 0.06365 | 0.0058755 | 0.00025007 | 0.00067941 | 0.061443 | 0.0056687 | 0.063132 | -66.7702 | 0.0243 | -66.7368 | 56.2518 | 56.1563 | 56.2802 | -66.8009 | -66.7749 | 0.03241 | -66.8048 | 56.1528 | 56.3168 | 56.1002 | -67.0286 | -0.049783 | -0.062248 | -0.019062 | 0.014251 | 0.064034 | -0.1578 | -0.033876 | -0.27752 | -0.16133 | -0.023758 | -0.053684 | 0.22383 | 0.002695 | -0.21388 | 123.0029 | 122.9074 | 123.0313 | 66.7754 | -123.115 | 122.9039 | 123.0679 | 122.8513 | 66.7835 | -123.3427
129.7969 | 123.1979 | -66.7419 | 56.3507 | 0.0018314 | -0.0015706 | 0.0010342 | 0.05772 | -0.00055774 | 0.063437 | -0.0093855 | 0.00025007 | 0.00046581 | 0.061657 | 0.0056687 | 0.063346 | -66.7793 | 0.028878 | -66.7506 | 56.2427 | 56.1563 | 56.2756 | -66.7459 | -66.7703 | 0.023253 | -66.8048 | 56.1573 | 56.3168 | 56.0407 | -67.0286 | -0.003992 | -0.10803 | -0.037375 | -0.00864 | -0.004648 | -0.19442 | -0.075075 | -0.28667 | -0.19337 | -0.028335 | -0.06284 | 0.22383 | -0.033926 | -0.31002 | 122.9846 | 122.8982 | 123.0176 | 66.7708 | -123.0966 | 122.8993 | 123.0587 | 122.7826 | 66.7652 | -123.3793
130.7969 | 123.2162 | -66.7419 | 56.3278 | 0.0094624 | -0.0015706 | 0.00082041 | 0.05772 | -0.00055774 | 0.063864 | -0.001755 | -0.00017733 | 0.00046581 | 0.061443 | 0.0058825 | 0.06356 | -66.7702 | 0.019721 | -66.7414 | 56.2473 | 56.1517 | 56.2711 | -66.7963 | -66.7703 | 0.03241 | -66.7956 | 56.1573 | 56.3214 | 56.1139 | -67.0286 | -0.054361 | -0.08056 | -0.028218 | 0.000516 | 0.054877 | -0.17611 | -0.056766 | -0.28667 | -0.17048 | -0.028335 | -0.053683 | 0.23299 | -0.00646 | -0.21387 | 122.9892 | 122.8937 | 123.013 | 66.7617 | -123.1241 | 122.8993 | 123.0633 | 122.8559 | 66.7744 | -123.3564
131.7969 | 123.2254 | -66.7557 | 56.337 | 0.0018314 | -0.0017842 | 0.00082041 | 0.057506 | -0.00077134 | 0.063437 | 0.021136 | 3.6274e-05 | 0.00046581 | 0.06187 | 0.0058825 | 0.063346 | -66.7747 | 0.033457 | -66.746 | 56.2564 | 56.1471 | 56.2711 | -66.7597 | -66.7749 | 0.027831 | -66.8094 | 56.1573 | 56.3122 | 56.0682 | -67.0286 | -0.003996 | -0.080558 | -0.019063 | 0.009671 | 0.013667 | -0.18984 | -0.065921 | -0.27294 | -0.17964 | -0.019181 | -0.053686 | 0.21925 | -0.024772 | -0.26882 | 123.0121 | 122.9028 | 123.0267 | 66.7891 | -123.0966 | 122.913 | 123.0679 | 122.8238 | 66.7835 | -123.3656
132.7969 | 123.23 | -66.7603 | 56.3278 | 0.0018314 | -0.0015706 | 0.00060681 | 0.057934 | -0.00098494 | 0.063437 | 0.013506 | 0.00025007 | 3.8406e-05 | 0.061229 | 0.0058825 | 0.063346 | -66.7747 | 0.0243 | -66.746 | 56.2518 | 56.1563 | 56.2756 | -66.8192 | -66.7703 | 0.03241 | -66.8048 | 56.1528 | 56.3214 | 56.1139 | -67.0286 | -0.058944 | -0.075981 | -0.014485 | 0.014249 | 0.073193 | -0.17153 | -0.052187 | -0.26836 | -0.17506 | -0.010024 | -0.044529 | 0.22383 | -0.00646 | -0.21387 | 123.0121 | 122.9165 | 123.0359 | 66.7846 | -123.147 | 122.913 | 123.0816 | 122.8742 | 66.7927 | -123.3564
133.7969 | 123.3032 | -66.7465 | 56.3187 | 0.0094624 | -0.0019978 | 0.00082041 | 0.058147 | -0.00077134 | 0.063864 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061657 | 0.0054551 | 0.063132 | -66.7702 | 0.028878 | -66.746 | 56.2564 | 56.1563 | 56.2711 | -66.8284 | -66.7657 | 0.03241 | -66.8002 | 56.1528 | 56.3168 | 56.1552 | -67.0286 | -0.081835 | -0.062248 | -0.02364 | 0.000516 | 0.082351 | -0.16238 | -0.047611 | -0.28209 | -0.16591 | -0.019178 | -0.053684 | 0.22841 | -0.001883 | -0.16351 | 123.0029 | 122.9028 | 123.0176 | 66.7754 | -123.147 | 122.8993 | 123.0633 | 122.9017 | 66.7789 | -123.3473
134.7969 | 123.2025 | -66.7419 | 56.3416 | 0.0018314 | -0.0017842 | 0.00082041 | 0.05772 | -0.00055774 | 0.063864 | 0.0058755 | 0.00046367 | 0.00025221 | 0.061443 | 0.0054551 | 0.063346 | -66.7656 | 0.028878 | -66.746 | 56.2564 | 56.1609 | 56.2802 | -66.8375 | -66.7657 | 0.023253 | -66.7956 | 56.1528 | 56.3122 | 56.2009 | -67.024 | -0.095571 | -0.085136 | -0.02364 | -0.004062 | 0.091509 | -0.18068 | -0.061342 | -0.28209 | -0.18879 | -0.023756 | -0.053683 | 0.22841 | -0.02935 | -0.14061 | 122.9984 | 122.9028 | 123.0222 | 66.7708 | -123.1791 | 122.8947 | 123.0541 | 122.9429 | 66.7652 | -123.3656
135.7969 | 123.4268 | -66.7282 | 56.2592 | -0.013431 | -0.0017842 | 0.00082041 | 0.05772 | -0.00055774 | 0.063223 | -0.001755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0058825 | 0.063132 | -66.7747 | 0.038035 | -66.7506 | 56.2564 | 56.1609 | 56.2756 | -66.8284 | -66.7657 | 0.023253 | -66.7956 | 56.1528 | 56.3122 | 56.1964 | -67.0286 | -0.10015 | -0.002738 | -0.046529 | -0.022373 | 0.077773 | -0.098287 | 0.016478 | -0.30041 | -0.10639 | -0.037489 | -0.067416 | 0.23299 | 0.053048 | -0.062794 | 122.9846 | 122.8891 | 123.0038 | 66.7662 | -123.0875 | 122.881 | 123.0404 | 122.9246 | 66.7515 | -123.2878
136.7969 | 123.1705 | -66.7419 | 56.3965 | 0.0018314 | -0.0015706 | 0.00082041 | 0.05772 | -0.00077134 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0058825 | 0.063346 | -66.7793 | 0.0243 | -66.7368 | 56.2564 | 56.1517 | 56.2756 | -66.8421 | -66.7611 | 0.027831 | -66.8002 | 56.1573 | 56.3122 | 56.2193 | -67.024 | -0.10015 | -0.14007 | -0.037375 | 0.005095 | 0.10525 | -0.24477 | -0.12085 | -0.28209 | -0.23915 | -0.019178 | -0.058262 | 0.22383 | -0.084281 | -0.17723 | 122.9984 | 122.8937 | 123.0176 | 66.7662 | -123.2386 | 122.8993 | 123.0541 | 122.9612 | 66.7698 | -123.4205
137.7969 | 123.3261 | -66.7191 | 56.3049 | 0.0018314 | -0.0015706 | 0.00082041 | 0.057934 | -0.00098494 | 0.063223 | -0.001755 | 0.00025007 | 0.00067941 | 0.061443 | 0.0058825 | 0.06356 | -66.7656 | 0.038035 | -66.746 | 56.2564 | 56.1563 | 56.2711 | -66.8421 | -66.7657 | 0.036989 | -66.7956 | 56.1573 | 56.3122 | 56.2193 | -67.0332 | -0.12304 | -0.048515 | -0.046528 | -0.02695 | 0.096088 | -0.14864 | -0.033878 | -0.31414 | -0.14759 | -0.046644 | -0.076571 | 0.23757 | 0.007271 | -0.085678 | 122.9755 | 122.8753 | 122.9901 | 66.7571 | -123.147 | 122.8764 | 123.0313 | 122.9383 | 66.756 | -123.3381
138.7969 | 123.2391 | -66.7511 | 56.3324 | 0.0018314 | -0.0019978 | 0.00082041 | 0.057293 | -0.00098494 | 0.063864 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0058825 | 0.063346 | -66.7702 | 0.038035 | -66.746 | 56.261 | 56.1654 | 56.2711 | -66.8467 | -66.7794 | 0.036989 | -66.791 | 56.1573 | 56.3122 | 56.2055 | -67.0286 | -0.095573 | -0.071402 | -0.019062 | 0.005094 | 0.10067 | -0.16695 | -0.061343 | -0.27752 | -0.17506 | -0.028337 | -0.039948 | 0.23757 | -0.020194 | -0.12688 | 123.0121 | 122.9165 | 123.0222 | 66.7891 | -123.1791 | 122.9084 | 123.0633 | 122.9566 | 66.7881 | -123.361
139.7969 | 123.349 | -66.6916 | 56.2912 | 0.0094624 | -0.0015706 | 0.0010342 | 0.05772 | -0.00055774 | 0.063437 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061443 | 0.0058825 | 0.062919 | -66.7793 | 0.028878 | -66.7368 | 56.2564 | 56.1609 | 56.2756 | -66.8375 | -66.7703 | 0.03241 | -66.8002 | 56.1573 | 56.3076 | 56.1826 | -67.0286 | -0.14593 | -0.034782 | -0.087729 | -0.045259 | 0.10067 | -0.13033 | -0.015566 | -0.33703 | -0.13386 | -0.078689 | -0.10862 | 0.22841 | 0.016425 | -0.10857 | 122.948 | 122.8525 | 122.9672 | 66.7205 | -123.1287 | 122.8489 | 122.9992 | 122.8742 | 66.724 | -123.3198
140.7969 | 123.2574 | -66.7328 | 56.3187 | 0.0094624 | -0.0017842 | 0.00082041 | 0.05772 | -0.00055774 | 0.063223 | -0.001755 | 0.00046367 | 0.00046581 | 0.061443 | 0.0058825 | 0.063346 | -66.7747 | 0.0243 | -66.7414 | 56.2564 | 56.1609 | 56.2711 | -66.8329 | -66.7611 | 0.027831 | -66.7956 | 56.1528 | 56.3214 | 56.1323 | -67.0332 | -0.10015 | -0.062248 | -0.041951 | -0.008639 | 0.091508 | -0.1578 | -0.047611 | -0.30041 | -0.16591 | -0.028333 | -0.062838 | 0.23757 | 0.002695 | -0.18641 | 122.9892 | 122.8937 | 123.0038 | 66.7571 | -123.1516 | 122.8855 | 123.0541 | 122.865 | 66.7606 | -123.3519
141.7969 | 123.3582 | -66.687 | 56.3004 | -0.0057996 | -0.0017842 | 0.0010342 | 0.05772 | -0.00098494 | 0.06365 | 0.013506 | 0.00046367 | 0.00025221 | 0.061229 | 0.0058825 | 0.063346 | -66.7747 | 0.0243 | -66.7414 | 56.2473 | 56.1609 | 56.2711 | -66.8375 | -66.7749 | 0.03241 | -66.7956 | 56.1573 | 56.3168 | 56.146 | -67.0286 | -0.1505 | -0.053094 | -0.087727 | -0.054415 | 0.096087 | -0.13949 | -0.0293 | -0.3416 | -0.14301 | -0.087845 | -0.10861 | 0.23299 | 0.016428 | -0.15436 | 122.9343 | 122.8479 | 122.9581 | 66.7113 | -123.1379 | 122.8444 | 123.0038 | 122.833 | 66.7194 | -123.329
142.7969 | 123.3582 | -66.7374 | 56.3141 | 0.0094624 | -0.0019978 | 0.0010342 | 0.057506 | -0.00077134 | 0.06365 | -0.0093855 | 0.00025007 | 0.00046581 | 0.061443 | 0.0056687 | 0.062919 | -66.7702 | 0.028878 | -66.7414 | 56.2564 | 56.1654 | 56.2756 | -66.8284 | -66.7657 | 0.023253 | -66.8002 | 56.1436 | 56.3168 | 56.2101 | -67.0286 | -0.09099 | -0.05767 | -0.032795 | -0.004061 | 0.086929 | -0.14864 | -0.038454 | -0.29125 | -0.17048 | -0.028333 | -0.062839 | 0.22841 | 0.002695 | -0.10399 | 122.9938 | 122.9028 | 123.013 | 66.7662 | -123.1424 | 122.881 | 123.0541 | 122.9475 | 66.7606 | -123.3427
143.7969 | 123.3261 | -66.7282 | 56.2912 | 0.0094624 | -0.0017842 | 0.00082041 | 0.058147 | -0.00098494 | 0.063864 | 0.0058755 | 0.00046367 | 0.00046581 | 0.061657 | 0.0056687 | 0.063346 | -66.7702 | 0.038035 | -66.746 | 56.2518 | 56.1517 | 56.2756 | -66.8375 | -66.7657 | 0.027831 | -66.7956 | 56.1573 | 56.3168 | 56.1552 | -67.0332 | -0.1093 | -0.03936 | -0.041951 | -0.017795 | 0.091509 | -0.13949 | -0.015566 | -0.30499 | -0.13386 | -0.037489 | -0.067416 | 0.23757 | 0.025583 | -0.13605 | 122.98 | 122.8799 | 123.0038 | 66.7662 | -123.1287 | 122.8855 | 123.045 | 122.8834 | 66.756 | -123.3244
144.7969 | 123.1888 | -66.7465 | 56.3599 | -0.013431 | -0.0017842 | 0.00039321 | 0.057506 | -0.00098494 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061443 | 0.0058825 | 0.063132 | -66.7702 | 0.028878 | -66.7414 | 56.261 | 56.1609 | 56.2802 | -66.8375 | -66.7657 | 0.036989 | -66.7956 | 56.1528 | 56.3168 | 56.1826 | -67.0286 | -0.090993 | -0.098868 | -0.02364 | 0.005094 | 0.096087 | -0.19899 | -0.079652 | -0.28209 | -0.2071 | -0.019178 | -0.049105 | 0.23299 | -0.043081 | -0.17724 | 123.0075 | 122.9074 | 123.0267 | 66.7754 | -123.1974 | 122.8993 | 123.0633 | 122.9291 | 66.7835 | -123.3885
145.7969 | 123.317 | -66.7145 | 56.2912 | 0.0094624 | -0.0019978 | 0.0010342 | 0.058147 | -0.00098494 | 0.06365 | 0.0058755 | 0.00025007 | 0.00067941 | 0.061443 | 0.0056687 | 0.063346 | -66.7747 | 0.0243 | -66.7368 | 56.2564 | 56.1609 | 56.2665 | -66.8467 | -66.7703 | 0.023253 | -66.7956 | 56.1619 | 56.3168 | 56.1231 | -67.0332 | -0.13219 | -0.034782 | -0.060261 | -0.02237 | 0.10982 | -0.13033 | -0.024723 | -0.31872 | -0.12928 | -0.0558 | -0.081148 | 0.23757 | 0.025583 | -0.1681 | 122.9709 | 122.8753 | 122.981 | 66.7388 | -123.1379 | 122.8764 | 123.0313 | 122.8376 | 66.7377 | -123.3244
146.7969 | 123.3307 | -66.7191 | 56.3141 | 0.0018314 | -0.0017842 | 0.00060681 | 0.05772 | -0.00098494 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0060961 | 0.063132 | -66.7656 | 0.0243 | -66.746 | 56.2518 | 56.1609 | 56.2756 | -66.8238 | -66.7657 | 0.036989 | -66.7956 | 56.1573 | 56.3122 | 56.0865 | -67.0332 | -0.10472 | -0.062248 | -0.046528 | -0.02695 | 0.077772 | -0.15322 | -0.038454 | -0.31414 | -0.15675 | -0.046644 | -0.076571 | 0.23757 | -0.001884 | -0.22761 | 122.9709 | 122.8799 | 122.9947 | 66.7434 | -123.1379 | 122.8764 | 123.0313 | 122.8055 | 66.756 | -123.3473
147.7969 | 123.2895 | -66.7465 | 56.3187 | -0.0057996 | -0.0015706 | 0.0010342 | 0.058147 | -0.00055774 | 0.063437 | -0.001755 | 0.00046367 | 0.00067941 | 0.061443 | 0.0056687 | 0.063132 | -66.7747 | 0.0243 | -66.7414 | 56.2564 | 56.1563 | 56.2665 | -66.8375 | -66.7703 | 0.027831 | -66.7956 | 56.1482 | 56.3168 | 56.1643 | -67.0332 | -0.090993 | -0.062248 | -0.028218 | 0.005094 | 0.096087 | -0.16238 | -0.052189 | -0.28667 | -0.17048 | -0.023757 | -0.049105 | 0.23757 | -0.001883 | -0.15435 | 123.0029 | 122.9028 | 123.013 | 66.7708 | -123.1562 | 122.8947 | 123.0633 | 122.9108 | 66.7744 | -123.3519
148.7969 | 123.317 | -66.7007 | 56.3324 | 0.0018314 | -0.0015706 | 0.0010342 | 0.05772 | -0.00055774 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0060961 | 0.063346 | -66.7656 | 0.033457 | -66.7368 | 56.2518 | 56.1517 | 56.2711 | -66.81 | -66.7611 | 0.027831 | -66.8002 | 56.1528 | 56.3122 | 56.0544 | -67.0332 | -0.1093 | -0.080558 | -0.064838 | -0.036103 | 0.073192 | -0.18069 | -0.061343 | -0.33245 | -0.17964 | -0.060376 | -0.09946 | 0.23299 | -0.020194 | -0.27797 | 122.9526 | 122.8525 | 122.9718 | 66.7342 | -123.1424 | 122.8535 | 123.0129 | 122.7552 | 66.7286 | -123.3656
149.7969 | 123.2849 | -66.7465 | 56.2866 | 0.0018314 | -0.0019978 | 0.0012478 | 0.057934 | -0.00077134 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0056687 | 0.063132 | -66.7793 | 0.0243 | -66.7368 | 56.2427 | 56.1426 | 56.2711 | -66.7093 | -66.7703 | 0.014095 | -66.8002 | 56.1528 | 56.3122 | 56.0315 | -67.0286 | 0.037217 | -0.043939 | -0.032797 | 0.009673 | -0.027544 | -0.14407 | -0.015567 | -0.28209 | -0.13386 | -0.023757 | -0.053684 | 0.22841 | 0.025582 | -0.25509 | 122.9892 | 122.8891 | 123.0176 | 66.7708 | -122.9959 | 122.8993 | 123.0587 | 122.7781 | 66.7606 | -123.3152
150.7969 | 123.317 | -66.7282 | 56.3004 | -0.0057996 | -0.0019978 | 0.0010342 | 0.057934 | -0.00077134 | 0.063864 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.061443 | 0.0060961 | 0.063346 | -66.7656 | 0.019721 | -66.746 | 56.2518 | 56.1471 | 56.2711 | -66.723 | -66.7657 | 0.027831 | -66.8002 | 56.1528 | 56.3214 | 56.0682 | -67.0286 | 0.005169 | -0.048515 | -0.037373 | -0.017795 | -0.022964 | -0.15322 | -0.0293 | -0.30041 | -0.14759 | -0.037489 | -0.071995 | 0.22841 | 0.021006 | -0.23219 | 122.98 | 122.8753 | 122.9993 | 66.7479 | -123.0234 | 122.881 | 123.0496 | 122.7964 | 66.756 | -123.329
151.7969 | 123.3078 | -66.7419 | 56.2866 | 0.0094624 | -0.0015706 | 0.0012478 | 0.057934 | -0.00077134 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0056687 | 0.063346 | -66.7702 | 0.033457 | -66.746 | 56.2473 | 56.1609 | 56.2711 | -66.7459 | -66.7565 | 0.036989 | -66.791 | 56.1573 | 56.3168 | 56.0865 | -67.0332 | -0.003992 | -0.039361 | -0.028218 | -0.004062 | -7e-05 | -0.12575 | -0.015567 | -0.29125 | -0.12928 | -0.014599 | -0.049104 | 0.24215 | 0.030161 | -0.20015 | 122.9892 | 122.9028 | 123.013 | 66.7754 | -123.0326 | 122.8993 | 123.0587 | 122.8284 | 66.7789 | -123.3198
152.7969 | 123.3353 | -66.7099 | 56.3049 | -0.0057996 | -0.0015706 | 0.00060681 | 0.057934 | -0.00077134 | 0.06365 | 0.0058755 | 0.00025007 | 0.00025221 | 0.061443 | 0.0054551 | 0.063346 | -66.7702 | 0.033457 | -66.7414 | 56.2518 | 56.1517 | 56.2711 | -66.7322 | -66.7703 | 0.03241 | -66.7956 | 56.1573 | 56.3122 | 56.0544 | -67.0378 | -0.022299 | -0.053093 | -0.060261 | -0.031527 | -0.009228 | -0.15322 | -0.033878 | -0.32787 | -0.14759 | -0.060378 | -0.085726 | 0.24215 | 0.007271 | -0.25051 | 122.9617 | 122.8616 | 122.981 | 66.7434 | -123.0371 | 122.8672 | 123.0221 | 122.7643 | 66.7423 | -123.3427
153.7969 | 123.2941 | -66.7419 | 56.3004 | 0.017093 | -0.0017842 | 0.00082041 | 0.058147 | -0.00098494 | 0.063437 | 0.013506 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0056687 | 0.063132 | -66.7702 | 0.033457 | -66.7506 | 56.2473 | 56.1517 | 56.2756 | -66.7139 | -66.7703 | 0.023253 | -66.8048 | 56.1619 | 56.3168 | 56.0498 | -67.0332 | 0.02806 | -0.053094 | -0.028218 | -0.00864 | -0.0367 | -0.14864 | -0.024721 | -0.29125 | -0.13844 | -0.028335 | -0.06284 | 0.22841 | 0.016428 | -0.25051 | 122.9892 | 122.8937 | 123.0176 | 66.7754 | -123.0142 | 122.9039 | 123.0587 | 122.7918 | 66.7652 | -123.3335
154.7969 | 123.3627 | -66.7145 | 56.2958 | 0.0018314 | -0.0015706 | 0.00082041 | 0.057934 | -0.00098494 | 0.064078 | 0.0058755 | 3.6274e-05 | 3.8406e-05 | 0.061657 | 0.0058825 | 0.063132 | -66.7702 | 0.033457 | -66.7552 | 56.2564 | 56.1517 | 56.2756 | -66.7368 | -66.7703 | 0.027831 | -66.791 | 56.1619 | 56.3168 | 56.0911 | -67.0332 | -0.0223 | -0.039359 | -0.055683 | -0.040683 | -0.018383 | -0.14406 | -0.020143 | -0.31872 | -0.13386 | -0.0558 | -0.076569 | 0.24215 | 0.021006 | -0.20472 | 122.9709 | 122.8662 | 122.9901 | 66.7479 | -123.0326 | 122.8764 | 123.0313 | 122.8055 | 66.7423 | -123.329
155.7969 | 123.2986 | -66.774 | 56.3004 | -0.0057996 | -0.0019978 | 0.00060681 | 0.057506 | -0.0014123 | 0.06365 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.061229 | 0.0058825 | 0.063132 | -66.7702 | 0.0243 | -66.7414 | 56.2427 | 56.1471 | 56.2665 | -66.8009 | -66.7657 | 0.027831 | -66.7956 | 56.1619 | 56.3122 | 56.0132 | -67.0286 | -0.026895 | -0.057672 | 0.003826 | 0.03256 | 0.059455 | -0.15322 | -0.033878 | -0.25463 | -0.13844 | 0.008288 | -0.021639 | 0.23299 | 0.011849 | -0.28714 | 123.0167 | 122.9211 | 123.0405 | 66.7983 | -123.1012 | 122.9359 | 123.0862 | 122.7872 | 66.8018 | -123.329
156.7969 | 123.3078 | -66.7465 | 56.2958 | -0.013431 | -0.0017842 | 0.00060681 | 0.05772 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0056687 | 0.063132 | -66.7747 | 0.028878 | -66.7506 | 56.2518 | 56.1517 | 56.2711 | -66.7368 | -66.7703 | 0.03241 | -66.8048 | 56.1619 | 56.3168 | 56.059 | -67.0286 | 0.009743 | -0.043937 | -0.028218 | -0.004062 | -0.013805 | -0.14406 | -0.024722 | -0.28209 | -0.13386 | -0.023757 | -0.058262 | 0.22383 | 0.021006 | -0.23677 | 122.9984 | 122.8982 | 123.0176 | 66.7754 | -123.0326 | 122.9084 | 123.0633 | 122.8055 | 66.7789 | -123.3244
157.7969 | 123.3124 | -66.7465 | 56.3095 | -0.0057996 | -0.0017842 | 0.00060681 | 0.057934 | -0.0011987 | 0.063437 | -0.0093855 | 0.00025007 | 0.00046581 | 0.061657 | 0.0063099 | 0.063132 | -66.7702 | 0.028878 | -66.746 | 56.2427 | 56.1471 | 56.2665 | -66.7643 | -66.7657 | 0.03241 | -66.8002 | 56.1573 | 56.3168 | 56.0453 | -67.024 | -0.01773 | -0.066827 | -0.02364 | 0.000516 | 0.018246 | -0.16238 | -0.043033 | -0.27752 | -0.15217 | -0.019178 | -0.053684 | 0.22383 | 0.007273 | -0.26424 | 122.9892 | 122.8937 | 123.013 | 66.7754 | -123.0738 | 122.9039 | 123.0633 | 122.7918 | 66.7789 | -123.3335
158.7969 | 123.262 | -66.6779 | 56.3599 | -0.0057996 | -0.0019978 | 0.0010342 | 0.057934 | -0.00098494 | 0.06365 | 0.013506 | 0.00025007 | 0.00046581 | 0.061443 | 0.0063099 | 0.063132 | -66.7702 | 0.033457 | -66.7414 | 56.2427 | 56.1471 | 56.2665 | -66.7597 | -66.7703 | 0.018674 | -66.791 | 56.1619 | 56.3214 | 56.059 | -67.0286 | -0.081816 | -0.11718 | -0.092305 | -0.063571 | 0.018245 | -0.21273 | -0.093387 | -0.35076 | -0.19795 | -0.092422 | -0.11319 | 0.23757 | -0.038503 | -0.30086 | 122.9205 | 122.825 | 122.9443 | 66.7113 | -123.1195 | 122.8398 | 122.9992 | 122.7369 | 66.6965 | -123.3885
159.7969 | 123.2666 | -66.7328 | 56.2958 | -0.0057996 | -0.0019978 | 0.00082041 | 0.058147 | -0.0011987 | 0.06365 | -0.0093855 | 0.00025007 | 3.8406e-05 | 0.061443 | 0.0058825 | 0.06356 | -66.7656 | 0.033457 | -66.7414 | 56.2427 | 56.1654 | 56.2756 | -66.7643 | -66.7611 | 0.023253 | -66.8002 | 56.1482 | 56.3168 | 56.0727 | -67.024 | -0.031463 | -0.053094 | -0.032795 | -0.008639 | 0.022824 | -0.13033 | -0.020143 | -0.29125 | -0.14759 | -0.028333 | -0.067417 | 0.22383 | 0.021006 | -0.22304 | 122.9755 | 122.8982 | 123.0084 | 66.7662 | -123.06 | 122.881 | 123.0496 | 122.8055 | 66.756 | -123.3198
160.7969 | 123.3307 | -66.7145 | 56.3095 | 0.0094624 | -0.0017842 | 0.0010342 | 0.058147 | -0.00098494 | 0.063437 | -0.001755 | 0.00067727 | 0.00046581 | 0.061657 | 0.0060961 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2711 | -66.7643 | -66.7611 | 0.03241 | -66.791 | 56.1482 | 56.3168 | 56.0178 | -67.024 | -0.049773 | -0.066827 | -0.051105 | -0.026949 | 0.022824 | -0.1578 | -0.038455 | -0.30956 | -0.16133 | -0.046643 | -0.076569 | 0.23299 | 0.007273 | -0.29171 | 122.9572 | 122.8662 | 122.9855 | 66.7434 | -123.0738 | 122.8627 | 123.0313 | 122.7323 | 66.7469 | -123.3335
161.7969 | 123.2529 | -66.7511 | 56.3095 | -0.0057996 | -0.0017842 | 0.00082041 | 0.057934 | -0.00077134 | 0.063437 | -0.001755 | -0.00017733 | 0.00046581 | 0.061443 | 0.0058825 | 0.063132 | -66.7747 | 0.033457 | -66.7414 | 56.2473 | 56.1426 | 56.2711 | -66.7826 | -66.7703 | 0.023253 | -66.7956 | 56.1528 | 56.3168 | 56.0498 | -67.0378 | -0.031468 | -0.062249 | -0.02364 | 0.009672 | 0.04114 | -0.16696 | -0.038455 | -0.28668 | -0.15675 | -0.019179 | -0.044527 | 0.24215 | 0.007273 | -0.25966 | 122.9984 | 122.8937 | 123.0222 | 66.7846 | -123.0921 | 122.9039 | 123.0679 | 122.8009 | 66.7744 | -123.3473
162.7969 | 123.3078 | -66.6916 | 56.3095 | -0.0057996 | -0.0019978 | 0.00082041 | 0.058147 | -0.00098494 | 0.063437 | -0.001755 | 0.00025007 | 0.00089321 | 0.061443 | 0.0060961 | 0.063346 | -66.7702 | 0.028878 | -66.7506 | 56.2427 | 56.1471 | 56.2711 | -66.7597 | -66.7657 | 0.03241 | -66.791 | 56.1573 | 56.3122 | 56.0911 | -67.0378 | -0.068083 | -0.066827 | -0.078572 | -0.058994 | 0.009089 | -0.16238 | -0.038455 | -0.34619 | -0.15217 | -0.07411 | -0.099458 | 0.24673 | 0.002694 | -0.21846 | 122.9343 | 122.8387 | 122.9626 | 66.7205 | -123.0692 | 122.8489 | 123.0038 | 122.7826 | 66.724 | -123.3473
163.7969 | 123.2895 | -66.7191 | 56.2866 | 0.0018314 | -0.0017842 | 0.0010342 | 0.05772 | -0.00077134 | 0.063437 | 0.013506 | 0.00025007 | 0.00025221 | 0.061443 | 0.0063099 | 0.063346 | -66.7656 | 0.019721 | -66.7368 | 56.2427 | 56.1471 | 56.2619 | -66.7414 | -66.7611 | 0.027831 | -66.7956 | 56.1619 | 56.3122 | 56.0041 | -67.0286 | -0.022301 | -0.043939 | -0.046528 | -0.017793 | 0.004508 | -0.13949 | -0.024724 | -0.30956 | -0.1247 | -0.042066 | -0.076571 | 0.23299 | 0.025582 | -0.28256 | 122.9617 | 122.8662 | 122.981 | 66.7388 | -123.028 | 122.881 | 123.0313 | 122.7231 | 66.7469 | -123.3152
164.7969 | 123.3215 | -66.7191 | 56.3049 | 0.0018314 | -0.0017842 | 0.00060681 | 0.057934 | -0.00077134 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061443 | 0.0058825 | 0.063132 | -66.7702 | 0.019721 | -66.746 | 56.2473 | 56.1426 | 56.2802 | -66.7551 | -66.7703 | 0.03241 | -66.8002 | 56.1482 | 56.3122 | 56.0315 | -67.0286 | -0.036038 | -0.057672 | -0.051106 | -0.02695 | 0.009088 | -0.16238 | -0.024721 | -0.30956 | -0.15675 | -0.051223 | -0.08115 | 0.22841 | 0.007271 | -0.2734 | 122.9663 | 122.8616 | 122.9993 | 66.7388 | -123.06 | 122.8672 | 123.0313 | 122.7506 | 66.7515 | -123.3335
165.7969 | 123.2895 | -66.7419 | 56.3049 | -0.0057996 | -0.0019978 | 0.00082041 | 0.05772 | -0.00098494 | 0.063223 | -0.0093855 | 0.00025007 | 0.00046581 | 0.061443 | 0.0058825 | 0.062919 | -66.7702 | 0.028878 | -66.7368 | 56.2427 | 56.1563 | 56.2711 | -66.7643 | -66.7611 | 0.03241 | -66.7956 | 56.1619 | 56.3122 | 56.0086 | -67.024 | -0.022308 | -0.06225 | -0.028218 | 0.005095 | 0.027403 | -0.14864 | -0.033878 | -0.28209 | -0.14301 | -0.019178 | -0.053683 | 0.22841 | 0.007271 | -0.29629 | 122.9846 | 122.8982 | 123.013 | 66.7708 | -123.0692 | 122.9039 | 123.0541 | 122.7506 | 66.7744 | -123.329
166.7969 | 123.349 | -66.7099 | 56.3004 | 0.0094624 | -0.0019978 | 0.0010342 | 0.057934 | -0.00077134 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0063099 | 0.06356 | -66.7656 | 0.033457 | -66.7414 | 56.2473 | 56.1471 | 56.2711 | -66.7505 | -66.7657 | 0.027831 | -66.8002 | 56.1573 | 56.3076 | 56.0407 | -67.024 | -0.040614 | -0.053094 | -0.055683 | -0.031527 | 0.009087 | -0.15322 | -0.0293 | -0.31414 | -0.14301 | -0.055799 | -0.090305 | 0.22383 | 0.00727 | -0.25967 | 122.9572 | 122.857 | 122.981 | 66.7434 | -123.0509 | 122.8672 | 123.0175 | 122.7506 | 66.7377 | -123.3244
167.7969 | 123.2941 | -66.7419 | 56.2958 | 0.0094624 | -0.0022116 | 0.0012478 | 0.057934 | -0.0011987 | 0.063437 | -0.001755 | 0.00046367 | 3.8406e-05 | 0.061229 | 0.0060961 | 0.063132 | -66.7702 | 0.0243 | -66.7414 | 56.2518 | 56.1471 | 56.2665 | -66.7551 | -66.7657 | 0.023253 | -66.8048 | 56.1573 | 56.3168 | 56.0636 | -67.0332 | -0.01315 | -0.043937 | -0.028218 | 0.000516 | 0.013666 | -0.14864 | -0.0293 | -0.29125 | -0.13844 | -0.023756 | -0.06284 | 0.22841 | 0.021006 | -0.23219 | 122.9938 | 122.8891 | 123.0084 | 66.7662 | -123.0509 | 122.8993 | 123.0587 | 122.8055 | 66.7652 | -123.329
168.7969 | 123.349 | -66.6962 | 56.3095 | 0.0018314 | -0.0022116 | 0.00060681 | 0.057506 | -0.00098494 | 0.06365 | -0.001755 | 0.00025007 | 0.00067941 | 0.061229 | 0.0063099 | 0.063346 | -66.7793 | 0.0243 | -66.7368 | 56.2381 | 56.1563 | 56.2711 | -66.6864 | -66.7794 | 0.023253 | -66.7956 | 56.1619 | 56.3122 | 56.0224 | -67.0378 | 0.009758 | -0.071405 | -0.083151 | -0.040681 | -0.050439 | -0.15322 | -0.038455 | -0.34161 | -0.14759 | -0.083269 | -0.099459 | 0.24215 | 0.002694 | -0.28713 | 122.9343 | 122.8525 | 122.9672 | 66.7205 | -122.9959 | 122.8581 | 123.0084 | 122.7185 | 66.7194 | -123.3473
169.7969 | 123.2895 | -66.7236 | 56.2912 | 0.0018314 | -0.0024252 | 0.00082041 | 0.05772 | -0.00077134 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061657 | 0.0058825 | 0.062919 | -66.7702 | 0.033457 | -66.7414 | 56.2381 | 56.1563 | 56.2711 | -66.7276 | -66.7611 | 0.03241 | -66.7956 | 56.1619 | 56.3168 | 56.0911 | -67.0332 | -0.003987 | -0.053095 | -0.046528 | -0.017794 | -0.013807 | -0.13491 | -0.020145 | -0.30956 | -0.12928 | -0.037488 | -0.071993 | 0.23757 | 0.025583 | -0.20015 | 122.9617 | 122.8799 | 122.9947 | 66.7571 | -123.0188 | 122.8856 | 123.0404 | 122.8147 | 66.756 | -123.3244
170.7969 | 123.2254 | -66.7648 | 56.2958 | -0.0057996 | -0.0022116 | 0.0010342 | 0.057293 | -0.0011987 | 0.06365 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0060961 | 0.063132 | -66.7702 | 0.028878 | -66.746 | 56.2473 | 56.1517 | 56.2802 | -66.7322 | -66.7703 | 0.036989 | -66.7865 | 56.1528 | 56.3168 | 56.0819 | -67.0286 | 0.032633 | -0.048516 | -0.005329 | 0.018827 | -0.013806 | -0.14406 | -0.015565 | -0.26378 | -0.14302 | -0.005446 | -0.021637 | 0.24215 | 0.021006 | -0.21388 | 123.0121 | 122.9165 | 123.045 | 66.7937 | -123.028 | 122.9176 | 123.0816 | 122.8467 | 66.8018 | -123.3244
171.7969 | 123.3215 | -66.7603 | 56.3049 | 0.0018314 | -0.0019978 | 0.00082041 | 0.057934 | -0.00077134 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0063099 | 0.063132 | -66.761 | 0.0243 | -66.7414 | 56.2473 | 56.1471 | 56.2711 | -66.7734 | -66.7611 | 0.03241 | -66.8002 | 56.1573 | 56.3168 | 55.9995 | -67.024 | -0.013155 | -0.057672 | -0.00075 | 0.018827 | 0.031982 | -0.1578 | -0.033878 | -0.26378 | -0.14759 | -0.000867 | -0.039951 | 0.22383 | 0.01185 | -0.30545 | 123.0075 | 122.9074 | 123.0313 | 66.7846 | -123.0783 | 122.9176 | 123.077 | 122.7597 | 66.7927 | -123.329
172.7969 | 123.2986 | -66.7236 | 56.3232 | 0.0094624 | -0.0017842 | 0.00060681 | 0.057934 | -0.00077134 | 0.06365 | -0.0093855 | 0.00025007 | 0.00067941 | 0.061443 | 0.0058825 | 0.06356 | -66.7702 | 0.0243 | -66.7414 | 56.2518 | 56.1563 | 56.2711 | -66.7139 | -66.7657 | 0.023253 | -66.7956 | 56.1573 | 56.3168 | 56.0315 | -67.024 | 0.00975 | -0.071403 | -0.046528 | -0.017794 | -0.027544 | -0.16695 | -0.052188 | -0.3004 | -0.1659 | -0.042066 | -0.071993 | 0.22841 | -0.00646 | -0.29171 | 122.9755 | 122.8799 | 122.9947 | 66.7479 | -123.0371 | 122.881 | 123.0404 | 122.7552 | 66.7469 | -123.3473
173.7969 | 123.2941 | -66.7374 | 56.2866 | 0.0018314 | -0.0017842 | 0.00082041 | 0.057934 | -0.00077134 | 0.063437 | -0.001755 | 0.00046367 | 0.00046581 | 0.061016 | 0.0060961 | 0.063132 | -66.761 | 0.019721 | -66.7414 | 56.2427 | 56.1563 | 56.2802 | -66.8192 | -66.7565 | 0.027831 | -66.7956 | 56.1619 | 56.3168 | 56.0041 | -67.0332 | -0.081832 | -0.043939 | -0.023638 | -0.004061 | 0.077771 | -0.13033 | -0.00641 | -0.29583 | -0.1247 | -0.019176 | -0.05826 | 0.23757 | 0.030161 | -0.28256 | 122.98 | 122.8937 | 123.0176 | 66.7571 | -123.1058 | 122.8993 | 123.0541 | 122.7414 | 66.7652 | -123.3198
174.7969 | 123.3994 | -66.7053 | 56.2729 | 0.0018314 | -0.0017842 | 0.00082041 | 0.05772 | -0.00098494 | 0.063223 | -0.0093855 | 0.00025007 | 0.00025221 | 0.061443 | 0.0060961 | 0.063132 | -66.761 | 0.0243 | -66.746 | 56.2473 | 56.1471 | 56.2711 | -66.7963 | -66.7611 | 0.03241 | -66.791 | 56.1528 | 56.3122 | 56.0727 | -67.0332 | -0.090982 | -0.025628 | -0.055682 | -0.040683 | 0.050299 | -0.12576 | -0.001834 | -0.32787 | -0.12013 | -0.055799 | -0.085725 | 0.24215 | 0.039315 | -0.20015 | 122.9526 | 122.8525 | 122.9764 | 66.7296 | -123.0692 | 122.8581 | 123.0175 | 122.7781 | 66.7377 | -123.3061
175.7969 | 123.2071 | -66.7603 | 56.3416 | 0.0094624 | -0.0019978 | 0.00060681 | 0.057293 | -0.0014123 | 0.06365 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0063099 | 0.063132 | -66.7564 | 0.028878 | -66.746 | 56.2427 | 56.1517 | 56.2711 | -66.8421 | -66.7657 | 0.027831 | -66.791 | 56.1573 | 56.3168 | 56.0178 | -67.0332 | -0.081839 | -0.098871 | 0.003828 | 0.014249 | 0.096088 | -0.18984 | -0.070499 | -0.27294 | -0.18421 | -0.005445 | -0.030793 | 0.24215 | -0.024771 | -0.32376 | 123.0029 | 122.912 | 123.0313 | 66.7891 | -123.1836 | 122.9176 | 123.077 | 122.778 | 66.7881 | -123.3747
176.7969 | 123.317 | -66.687 | 56.337 | 0.0018314 | -0.0017842 | 0.00082041 | 0.057934 | -0.00077134 | 0.06365 | 0.013506 | 0.00025007 | 0.00046581 | 0.061229 | 0.0060961 | 0.062705 | -66.7747 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2756 | -66.8375 | -66.7657 | 0.018674 | -66.8002 | 56.1573 | 56.3214 | 56.0636 | -67.024 | -0.1505 | -0.094293 | -0.087727 | -0.054415 | 0.096087 | -0.18526 | -0.061342 | -0.33703 | -0.17964 | -0.078687 | -0.11319 | 0.22383 | -0.015615 | -0.27339 | 122.9297 | 122.8387 | 122.9626 | 66.7159 | -123.1745 | 122.8444 | 123.0084 | 122.7506 | 66.7057 | -123.361
177.7969 | 123.2666 | -66.7511 | 56.2912 | -0.0057996 | -0.0022116 | 0.0012478 | 0.057934 | -0.00055774 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0060961 | 0.062919 | -66.7747 | 0.0243 | -66.746 | 56.2381 | 56.138 | 56.2711 | -66.8421 | -66.7611 | 0.018674 | -66.7956 | 56.1573 | 56.3214 | 56.0636 | -67.0332 | -0.090994 | -0.053095 | -0.02364 | 0.005094 | 0.096088 | -0.15322 | -0.020145 | -0.2821 | -0.13386 | -0.010022 | -0.044527 | 0.23757 | 0.030161 | -0.22762 | 122.9892 | 122.8891 | 123.0222 | 66.7754 | -123.1333 | 122.9084 | 123.0725 | 122.8147 | 66.7698 | -123.3244
178.7969 | 123.3398 | -66.6824 | 56.2866 | 0.0094624 | -0.0024252 | 0.00082041 | 0.057934 | -0.00077134 | 0.063437 | -0.001755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0063099 | 0.062919 | -66.7656 | 0.033457 | -66.746 | 56.2427 | 56.1471 | 56.2711 | -66.8467 | -66.7703 | 0.023253 | -66.7956 | 56.1528 | 56.3168 | 56.0911 | -67.0332 | -0.16424 | -0.043939 | -0.083149 | -0.063571 | 0.10067 | -0.13949 | -0.015567 | -0.35076 | -0.13386 | -0.087844 | -0.11319 | 0.23757 | 0.030161 | -0.19557 | 122.9251 | 122.8296 | 122.9535 | 66.7159 | -123.1333 | 122.8352 | 122.9992 | 122.7735 | 66.7057 | -123.3198
179.7969 | 123.3261 | -66.7374 | 56.3278 | 0.0018314 | -0.0019978 | 0.0010342 | 0.057934 | -0.0011987 | 0.06365 | -0.001755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0063099 | 0.063132 | -66.7702 | 0.0243 | -66.7414 | 56.2335 | 56.1471 | 56.2756 | -66.8375 | -66.7703 | 0.027831 | -66.7956 | 56.1619 | 56.3168 | 56.059 | -67.0332 | -0.10015 | -0.094295 | -0.032795 | -0.004061 | 0.096087 | -0.18069 | -0.052187 | -0.29583 | -0.1659 | -0.032912 | -0.05826 | 0.23757 | -0.011038 | -0.26882 | 122.9709 | 122.8845 | 123.013 | 66.7617 | -123.1653 | 122.8993 | 123.0541 | 122.7964 | 66.7652 | -123.361
180.7969 | 123.1842 | -66.7648 | 56.3095 | 0.0018314 | -0.0022116 | 0.00082041 | 0.057293 | -0.00098494 | 0.063223 | -0.0093855 | -0.00017733 | 0.00046581 | 0.061229 | 0.0063099 | 0.062705 | -66.7656 | 0.028878 | -66.746 | 56.2427 | 56.1563 | 56.2711 | -66.8467 | -66.7657 | 0.023253 | -66.791 | 56.1573 | 56.3168 | 56.0956 | -67.0332 | -0.08184 | -0.066827 | -0.000751 | 0.018827 | 0.10067 | -0.15322 | -0.038455 | -0.26836 | -0.15217 | -0.000867 | -0.026215 | 0.24215 | 0.007273 | -0.21388 | 123.0075 | 122.9211 | 123.0359 | 66.7937 | -123.1562 | 122.9222 | 123.0816 | 122.8605 | 66.7881 | -123.3427
181.7969 | 123.3398 | -66.7419 | 56.2958 | 0.0018314 | -0.0022116 | 0.0010342 | 0.05772 | -0.0011987 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061657 | 0.0060961 | 0.062919 | -66.7702 | 0.0243 | -66.7368 | 56.2473 | 56.1517 | 56.2711 | -66.8329 | -66.7611 | 0.023253 | -66.8002 | 56.1528 | 56.3214 | 56.0498 | -67.0332 | -0.090992 | -0.048516 | -0.028218 | 0.005095 | 0.096087 | -0.14406 | -0.024722 | -0.29125 | -0.14302 | -0.019178 | -0.058262 | 0.23299 | 0.025584 | -0.24593 | 122.9892 | 122.8937 | 123.013 | 66.7662 | -123.1287 | 122.8947 | 123.0633 | 122.7918 | 66.7652 | -123.329
182.7969 | 123.349 | -66.7099 | 56.3232 | -0.0057996 | -0.0019978 | 0.00060681 | 0.057506 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.061443 | 0.0060961 | 0.063346 | -66.7656 | 0.0243 | -66.7414 | 56.2427 | 56.1654 | 56.2711 | -66.8467 | -66.7657 | 0.03241 | -66.791 | 56.1482 | 56.3168 | 56.0865 | -67.0286 | -0.13677 | -0.08056 | -0.055683 | -0.031527 | 0.10524 | -0.1578 | -0.052188 | -0.31872 | -0.17506 | -0.055799 | -0.081147 | 0.23757 | -0.00646 | -0.23677 | 122.9526 | 122.8753 | 122.981 | 66.7342 | -123.1699 | 122.8581 | 123.0267 | 122.7964 | 66.7423 | -123.3519
183.7969 | 123.2712 | -66.7191 | 56.2912 | 0.017093 | -0.0022116 | 0.00060681 | 0.05772 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.06187 | 0.0065235 | 0.063132 | -66.7564 | 0.028878 | -66.7414 | 56.2473 | 56.1471 | 56.2665 | -66.8421 | -66.7565 | 0.027831 | -66.7956 | 56.1619 | 56.3214 | 56.0727 | -67.0286 | -0.12304 | -0.043939 | -0.037371 | -0.022372 | 0.10067 | -0.14407 | -0.024723 | -0.30956 | -0.12928 | -0.037487 | -0.076571 | 0.23299 | 0.030161 | -0.21846 | 122.9663 | 122.8662 | 122.9855 | 66.7479 | -123.1333 | 122.881 | 123.0404 | 122.7918 | 66.7469 | -123.3198
184.7969 | 123.3124 | -66.7191 | 56.3187 | -0.0057996 | -0.0022116 | 0.00060681 | 0.058147 | -0.00077134 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.06187 | 0.0065235 | 0.062919 | -66.7793 | 0.0243 | -66.7552 | 56.2427 | 56.1471 | 56.2802 | -66.8421 | -66.7657 | 0.03241 | -66.8002 | 56.1619 | 56.3214 | 56.0773 | -67.0378 | -0.12304 | -0.075983 | -0.060263 | -0.036106 | 0.086932 | -0.17153 | -0.038454 | -0.31872 | -0.15675 | -0.046644 | -0.08115 | 0.23757 | 0.002695 | -0.24135 | 122.9617 | 122.8662 | 122.9993 | 66.7434 | -123.1608 | 122.881 | 123.0404 | 122.7964 | 66.7515 | -123.3564
185.7969 | 123.2437 | -66.7557 | 56.3324 | -0.0057996 | -0.0022116 | 0.00060681 | 0.057506 | -0.0011987 | 0.063437 | 0.0058755 | 0.00025007 | 0.00067941 | 0.061443 | 0.0063099 | 0.062919 | -66.7702 | 0.033457 | -66.7414 | 56.2518 | 56.1517 | 56.2711 | -66.8467 | -66.7657 | 0.027831 | -66.7956 | 56.1573 | 56.3214 | 56.0086 | -67.0332 | -0.090996 | -0.080558 | -0.014485 | 0.014249 | 0.10524 | -0.18069 | -0.061343 | -0.27752 | -0.17506 | -0.010023 | -0.03995 | 0.23757 | -0.011037 | -0.32376 | 123.0075 | 122.9074 | 123.0267 | 66.7891 | -123.1791 | 122.913 | 123.077 | 122.7643 | 66.7835 | -123.3656
186.7969 | 123.317 | -66.7236 | 56.3278 | 0.0018314 | -0.0022116 | 0.0012478 | 0.057934 | -0.00098494 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.061657 | 0.0065235 | 0.063132 | -66.7656 | 0.0243 | -66.746 | 56.2473 | 56.1471 | 56.2665 | -66.8467 | -66.7565 | 0.027831 | -66.8002 | 56.1528 | 56.3214 | 56.0178 | -67.0378 | -0.12304 | -0.08056 | -0.04195 | -0.022372 | 0.10067 | -0.18069 | -0.061344 | -0.31414 | -0.17506 | -0.032909 | -0.076572 | 0.23757 | -0.00646 | -0.31003 | 122.9709 | 122.8708 | 122.9901 | 66.7479 | -123.1745 | 122.8764 | 123.045 | 122.7414 | 66.7515 | -123.3656
187.7969 | 123.3353 | -66.7328 | 56.3004 | -0.013431 | -0.0024252 | 0.00082041 | 0.057506 | -0.00077134 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0063099 | 0.063132 | -66.7702 | 0.0243 | -66.7506 | 56.2473 | 56.1471 | 56.2848 | -66.8421 | -66.7611 | 0.03241 | -66.7956 | 56.1528 | 56.3214 | 56.0224 | -67.0332 | -0.10931 | -0.053094 | -0.037373 | -0.017795 | 0.09151 | -0.15322 | -0.015564 | -0.30041 | -0.14759 | -0.028333 | -0.062838 | 0.23757 | 0.021006 | -0.27798 | 122.98 | 122.8799 | 123.0176 | 66.7571 | -123.1424 | 122.8855 | 123.0541 | 122.7552 | 66.7652 | -123.3335
188.7969 | 123.3032 | -66.7007 | 56.3004 | 0.0018314 | -0.0019978 | 0.00082041 | 0.05772 | -0.00077134 | 0.063437 | -0.001755 | -0.00017733 | 0.00046581 | 0.061229 | 0.0065235 | 0.06356 | -66.7656 | 0.0243 | -66.746 | 56.2473 | 56.1471 | 56.2802 | -66.8421 | -66.7611 | 0.023253 | -66.791 | 56.1573 | 56.3168 | 56.0682 | -67.0286 | -0.14135 | -0.053094 | -0.064838 | -0.04526 | 0.096088 | -0.15322 | -0.020143 | -0.32787 | -0.14301 | -0.060376 | -0.090302 | 0.23757 | 0.016428 | -0.23219 | 122.948 | 122.8479 | 122.981 | 66.725 | -123.1424 | 122.8581 | 123.0175 | 122.7689 | 66.724 | -123.329
189.7969 | 123.3353 | -66.7191 | 56.2912 | -0.0057996 | -0.0022116 | 0.00060681 | 0.058147 | -0.0011987 | 0.063864 | 0.013506 | 0.00046367 | 0.00046581 | 0.061443 | 0.0060961 | 0.062919 | -66.7656 | 0.0243 | -66.746 | 56.2473 | 56.1517 | 56.2756 | -66.8375 | -66.7611 | 0.023253 | -66.7865 | 56.1573 | 56.3259 | 56.059 | -67.0286 | -0.11846 | -0.043939 | -0.046528 | -0.02695 | 0.091509 | -0.13949 | -0.015566 | -0.30956 | -0.13386 | -0.042066 | -0.067414 | 0.24215 | 0.03474 | -0.2322 | 122.9663 | 122.8708 | 122.9947 | 66.7434 | -123.1287 | 122.8764 | 123.045 | 122.7781 | 66.7423 | -123.3198
190.7969 | 123.2346 | -66.7328 | 56.3278 | -0.0057996 | -0.0024252 | 0.00082041 | 0.057293 | -0.00098494 | 0.063437 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0067371 | 0.062919 | -66.761 | 0.028878 | -66.746 | 56.2473 | 56.1517 | 56.2756 | -66.8467 | -66.7749 | 0.027831 | -66.791 | 56.1573 | 56.3168 | 56.0453 | -67.0286 | -0.11388 | -0.08056 | -0.028216 | -0.013217 | 0.10067 | -0.17611 | -0.052187 | -0.29583 | -0.17048 | -0.042069 | -0.058259 | 0.23757 | -0.011038 | -0.28255 | 122.98 | 122.8845 | 123.0084 | 66.7617 | -123.1745 | 122.8901 | 123.0496 | 122.7781 | 66.7606 | -123.3564
191.7969 | 123.3307 | -66.7236 | 56.2775 | 0.0018314 | -0.0019978 | 0.00082041 | 0.057506 | -0.00098494 | 0.063437 | -0.0093855 | 3.6274e-05 | 3.8406e-05 | 0.061229 | 0.0065235 | 0.062919 | -66.761 | 0.0243 | -66.746 | 56.2427 | 56.1517 | 56.2756 | -66.8421 | -66.7657 | 0.027831 | -66.7956 | 56.1573 | 56.3214 | 56.0727 | -67.0332 | -0.11846 | -0.034784 | -0.037371 | -0.022372 | 0.096088 | -0.12575 | -0.001833 | -0.30956 | -0.12013 | -0.042066 | -0.071993 | 0.23757 | 0.043894 | -0.20473 | 122.9663 | 122.8753 | 122.9993 | 66.7479 | -123.1196 | 122.881 | 123.045 | 122.7964 | 66.7515 | -123.3107
192.7969 | 123.2941 | -66.6962 | 56.3095 | 0.0018314 | -0.0019978 | 0.0010342 | 0.057934 | -0.00077134 | 0.063437 | 0.0058755 | -0.00017733 | 0.00067941 | 0.061229 | 0.0063099 | 0.062919 | -66.7702 | 0.033457 | -66.746 | 56.2518 | 56.1517 | 56.2711 | -66.8421 | -66.7657 | 0.023253 | -66.7865 | 56.1573 | 56.3214 | 56.0086 | -67.0286 | -0.14593 | -0.05767 | -0.073994 | -0.049838 | 0.096088 | -0.1578 | -0.038455 | -0.33245 | -0.15217 | -0.069532 | -0.090302 | 0.24215 | 0.011851 | -0.30087 | 122.948 | 122.8479 | 122.9672 | 66.7296 | -123.1516 | 122.8535 | 123.0175 | 122.7048 | 66.7194 | -123.3381
193.7969 | 123.2941 | -66.7099 | 56.2729 | 0.0018314 | -0.0024252 | 0.0010342 | 0.057293 | -0.00098494 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0067371 | 0.063132 | -66.7702 | 0.028878 | -66.7368 | 56.2473 | 56.1517 | 56.2711 | -66.8467 | -66.7611 | 0.027831 | -66.7956 | 56.1573 | 56.3076 | 56.0682 | -67.0378 | -0.13677 | -0.025628 | -0.060261 | -0.026948 | 0.10982 | -0.12118 | -0.001834 | -0.32787 | -0.11555 | -0.051221 | -0.085726 | 0.24215 | 0.034736 | -0.20473 | 122.9572 | 122.8616 | 122.981 | 66.7388 | -123.1196 | 122.8672 | 123.0175 | 122.7781 | 66.7377 | -123.3107
194.7969 | 123.2437 | -66.7236 | 56.337 | 0.0018314 | -0.0022116 | 0.0010342 | 0.05772 | -0.00098494 | 0.063437 | -0.001755 | 0.00025007 | 0.00025221 | 0.06187 | 0.0063099 | 0.063132 | -66.761 | 0.019721 | -66.7506 | 56.2473 | 56.1471 | 56.2711 | -66.8421 | -66.7703 | 0.027831 | -66.7865 | 56.1573 | 56.3122 | 56.0727 | -67.0378 | -0.11846 | -0.089715 | -0.037371 | -0.02695 | 0.09151 | -0.18984 | -0.065921 | -0.31414 | -0.17964 | -0.046645 | -0.062836 | 0.25131 | -0.024772 | -0.26424 | 122.9709 | 122.8708 | 122.9947 | 66.7434 | -123.1791 | 122.881 | 123.0358 | 122.7964 | 66.7515 | -123.3747
195.7969 | 123.3902 | -66.7145 | 56.2958 | -0.021062 | -0.0022116 | 0.00082041 | 0.057506 | -0.00077134 | 0.063437 | 0.013506 | 0.00046367 | 0.00046581 | 0.061229 | 0.0063099 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2473 | 56.1517 | 56.2802 | -66.8375 | -66.7657 | 0.03241 | -66.8002 | 56.1573 | 56.3122 | 56.0315 | -67.0378 | -0.12304 | -0.048516 | -0.051105 | -0.026949 | 0.096087 | -0.14406 | -0.015565 | -0.3233 | -0.13844 | -0.051221 | -0.085727 | 0.23757 | 0.016427 | -0.26424 | 122.9617 | 122.8662 | 122.9947 | 66.7434 | -123.1333 | 122.8718 | 123.0267 | 122.746 | 66.7469 | -123.3336
196.7969 | 123.2666 | -66.7282 | 56.3324 | 0.0018314 | -0.0022116 | 0.0010342 | 0.057506 | -0.00098494 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0065235 | 0.063132 | -66.7656 | 0.033457 | -66.7414 | 56.2381 | 56.1471 | 56.2756 | -66.8467 | -66.7611 | 0.027831 | -66.791 | 56.1528 | 56.3168 | 56.0224 | -67.0286 | -0.11846 | -0.094293 | -0.037373 | -0.013217 | 0.10524 | -0.18527 | -0.056764 | -0.30041 | -0.17964 | -0.032911 | -0.062837 | 0.23757 | -0.015615 | -0.31002 | 122.9663 | 122.8753 | 123.0038 | 66.7617 | -123.1791 | 122.881 | 123.045 | 122.7506 | 66.756 | -123.361
197.7969 | 123.3307 | -66.7145 | 56.2866 | 0.0018314 | -0.0022116 | 0.0010342 | 0.05772 | -0.00098494 | 0.063223 | 0.0058755 | 0.00046367 | 0.00046581 | 0.06187 | 0.0067371 | 0.063132 | -66.761 | 0.028878 | -66.746 | 56.2473 | 56.1517 | 56.2711 | -66.8375 | -66.7703 | 0.027831 | -66.7956 | 56.1619 | 56.3168 | 56.0361 | -67.0332 | -0.12304 | -0.039361 | -0.046526 | -0.031527 | 0.091509 | -0.13491 | -0.015567 | -0.31872 | -0.1247 | -0.0558 | -0.081148 | 0.23757 | 0.030161 | -0.25051 | 122.9617 | 122.8662 | 122.9855 | 66.7434 | -123.1241 | 122.8764 | 123.0313 | 122.7506 | 66.7423 | -123.3198
198.7969 | 123.2391 | -66.7419 | 56.3278 | 0.0094624 | -0.0022116 | 0.00082041 | 0.05772 | -0.00077134 | 0.063223 | 0.013506 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0063099 | 0.062705 | -66.7564 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2756 | -66.8421 | -66.7565 | 0.036989 | -66.7819 | 56.1528 | 56.3076 | 56.0407 | -67.0378 | -0.10015 | -0.085138 | -0.014483 | 0.000516 | 0.10067 | -0.17611 | -0.052187 | -0.29583 | -0.17506 | -0.014599 | -0.039947 | 0.25588 | -0.020196 | -0.28713 | 122.9846 | 122.8937 | 123.0176 | 66.7708 | -123.1699 | 122.8947 | 123.0496 | 122.7826 | 66.7789 | -123.3656
199.7969 | 123.3124 | -66.7053 | 56.2912 | 0.0018314 | -0.0022116 | 0.00060681 | 0.057079 | -0.00098494 | 0.063437 | 0.0058755 | 0.00046367 | 0.00025221 | 0.061229 | 0.0065235 | 0.062919 | -66.7702 | 0.0243 | -66.7277 | 56.2427 | 56.1563 | 56.2756 | -66.8375 | -66.7657 | 0.036989 | -66.791 | 56.1482 | 56.3168 | 56.0773 | -67.0332 | -0.13219 | -0.048517 | -0.064839 | -0.02237 | 0.10982 | -0.13491 | -0.015566 | -0.32787 | -0.14302 | -0.060377 | -0.085725 | 0.24215 | 0.025583 | -0.21388 | 122.948 | 122.8616 | 122.981 | 66.7296 | -123.1287 | 122.8535 | 123.0221 | 122.7826 | 66.7423 | -123.3244
200.7969 | 123.2666 | -66.7053 | 56.3828 | 0.0018314 | -0.0024252 | 0.0012478 | 0.05772 | -0.0011987 | 0.063437 | -0.001755 | -0.00017733 | 0.00025221 | 0.061229 | 0.0065235 | 0.062919 | -66.7747 | 0.0243 | -66.746 | 56.2473 | 56.1517 | 56.2665 | -66.8421 | -66.7611 | 0.027831 | -66.7956 | 56.1528 | 56.3168 | 56.0819 | -67.0332 | -0.13677 | -0.13549 | -0.069417 | -0.040683 | 0.096088 | -0.23104 | -0.11628 | -0.32787 | -0.22999 | -0.055799 | -0.090304 | 0.23757 | -0.065969 | -0.30085 | 122.9526 | 122.857 | 122.9718 | 66.7296 | -123.2248 | 122.8581 | 123.0221 | 122.7872 | 66.7332 | -123.4159
201.7969 | 123.3215 | -66.7374 | 56.3095 | 0.0094624 | -0.0022116 | 0.00082041 | 0.057934 | -0.00077134 | 0.06365 | 0.0058755 | 0.00025007 | 0.00089321 | 0.061016 | 0.0067371 | 0.063132 | -66.761 | 0.028878 | -66.7323 | 56.2473 | 56.1563 | 56.2711 | -66.8421 | -66.7657 | 0.027831 | -66.7865 | 56.1573 | 56.3122 | 56.0315 | -67.0286 | -0.10473 | -0.062249 | -0.023638 | 0.005096 | 0.10982 | -0.15322 | -0.038455 | -0.29125 | -0.15217 | -0.028333 | -0.049103 | 0.24215 | 0.002694 | -0.27798 | 122.9846 | 122.8937 | 123.0084 | 66.7662 | -123.1516 | 122.8947 | 123.0496 | 122.7689 | 66.7652 | -123.3381
202.7969 | 123.2254 | -66.7419 | 56.3644 | -0.0057996 | -0.0019978 | 0.0010342 | 0.057506 | -0.00098494 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0065235 | 0.062919 | -66.7656 | 0.028878 | -66.7506 | 56.2473 | 56.1563 | 56.2756 | -66.8467 | -66.7657 | 0.036989 | -66.7956 | 56.1619 | 56.3076 | 55.9949 | -67.0286 | -0.10473 | -0.11718 | -0.02364 | -0.00864 | 0.096089 | -0.20815 | -0.088808 | -0.28667 | -0.20252 | -0.023756 | -0.053683 | 0.23299 | -0.056817 | -0.36954 | 122.9892 | 122.8982 | 123.0176 | 66.7708 | -123.2111 | 122.9039 | 123.0496 | 122.7368 | 66.7789 | -123.3931
203.7969 | 123.3353 | -66.7053 | 56.3095 | -0.0057996 | -0.0017842 | 0.00082041 | 0.057934 | -0.00077134 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0067371 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2473 | 56.1563 | 56.2711 | -66.8284 | -66.7611 | 0.027831 | -66.791 | 56.1573 | 56.3122 | 56.0407 | -67.0332 | -0.12303 | -0.062249 | -0.060261 | -0.036105 | 0.086929 | -0.15322 | -0.038455 | -0.32787 | -0.15217 | -0.055799 | -0.085725 | 0.24215 | 0.002694 | -0.26882 | 122.9526 | 122.8616 | 122.9764 | 66.7342 | -123.1379 | 122.8627 | 123.0175 | 122.746 | 66.7332 | -123.3427
204.7969 | 123.2849 | -66.7236 | 56.3187 | -0.0057996 | -0.0026388 | 0.00082041 | 0.057506 | -0.00077134 | 0.063223 | 0.013506 | 0.00046367 | 0.00067941 | 0.061443 | 0.0069509 | 0.062705 | -66.7656 | 0.028878 | -66.7414 | 56.2473 | 56.1471 | 56.2756 | -66.8375 | -66.7657 | 0.03241 | -66.791 | 56.1619 | 56.3076 | 56.0315 | -67.0286 | -0.11388 | -0.071405 | -0.04195 | -0.017794 | 0.096087 | -0.17153 | -0.043032 | -0.30498 | -0.15675 | -0.042066 | -0.067414 | 0.23757 | -0.011041 | -0.28713 | 122.9709 | 122.8708 | 122.9993 | 66.7525 | -123.1562 | 122.8856 | 123.0313 | 122.7552 | 66.756 | -123.3473
205.7969 | 123.3353 | -66.7191 | 56.3095 | -0.013431 | -0.0022116 | 0.00082041 | 0.057506 | -0.00077134 | 0.063437 | 0.0058755 | 0.00025007 | 0.00067941 | 0.061229 | 0.0065235 | 0.062705 | -66.7702 | 0.0243 | -66.7368 | 56.2518 | 56.1563 | 56.2756 | -66.8467 | -66.7565 | 0.027831 | -66.791 | 56.1528 | 56.3168 | 55.9995 | -67.0378 | -0.12762 | -0.05767 | -0.051106 | -0.017793 | 0.10982 | -0.15322 | -0.033876 | -0.31872 | -0.15675 | -0.037487 | -0.071992 | 0.24673 | 0.007273 | -0.31003 | 122.9709 | 122.8753 | 122.9947 | 66.7434 | -123.1562 | 122.8718 | 123.0358 | 122.7185 | 66.7469 | -123.3473
206.7969 | 123.2071 | -66.7511 | 56.3461 | 0.0094624 | -0.0022116 | 0.00039321 | 0.05772 | -0.00055774 | 0.063223 | 0.0058755 | 0.00046367 | 0.00067941 | 0.061229 | 0.0065235 | 0.062705 | -66.7656 | 0.033457 | -66.7414 | 56.2427 | 56.1609 | 56.2756 | -66.8375 | -66.7611 | 0.023253 | -66.7865 | 56.1528 | 56.3122 | 56.0178 | -67.0286 | -0.086415 | -0.10345 | -0.014484 | 0.009672 | 0.096087 | -0.18526 | -0.070497 | -0.27752 | -0.19337 | -0.010022 | -0.03537 | 0.24215 | -0.033927 | -0.32834 | 122.9938 | 122.912 | 123.0267 | 66.7846 | -123.1836 | 122.9039 | 123.0633 | 122.7689 | 66.7744 | -123.3747
207.7969 | 123.2025 | -66.7328 | 56.3416 | -0.0057996 | -0.0022116 | 0.00082041 | 0.057293 | -0.0011987 | 0.063437 | 0.013506 | 0.00025007 | 0.00025221 | 0.061229 | 0.0065235 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2756 | -66.8467 | -66.7611 | 0.027831 | -66.7956 | 56.1528 | 56.3076 | 56.0819 | -67.0332 | -0.11388 | -0.098871 | -0.032795 | -0.008639 | 0.10524 | -0.18984 | -0.06592 | -0.30041 | -0.18879 | -0.028333 | -0.062838 | 0.23757 | -0.033929 | -0.25966 | 122.9755 | 122.8845 | 123.0084 | 66.7617 | -123.1882 | 122.8855 | 123.0404 | 122.8147 | 66.7606 | -123.3747
208.7969 | 123.2071 | -66.7603 | 56.3278 | 0.0018314 | -0.0022116 | 0.00060681 | 0.057506 | -0.00077134 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0065235 | 0.062919 | -66.761 | 0.033457 | -66.7414 | 56.2473 | 56.1517 | 56.2711 | -66.8421 | -66.7657 | 0.027831 | -66.7865 | 56.1528 | 56.3122 | 56.027 | -67.0286 | -0.081839 | -0.08056 | -0.00075 | 0.018827 | 0.10067 | -0.17611 | -0.056766 | -0.26836 | -0.17506 | -0.005445 | -0.026215 | 0.24215 | -0.015617 | -0.30087 | 123.0075 | 122.912 | 123.0313 | 66.7937 | -123.1699 | 122.913 | 123.0725 | 122.7872 | 66.7881 | -123.3564
209.7969 | 123.2162 | -66.7557 | 56.3599 | 0.0018314 | -0.0024252 | 0.00082041 | 0.05772 | -0.00098494 | 0.063223 | -0.001755 | -0.00017733 | 3.8406e-05 | 0.061229 | 0.0065235 | 0.062705 | -66.7702 | 0.028878 | -66.7414 | 56.2381 | 56.1609 | 56.2756 | -66.8421 | -66.7611 | 0.03241 | -66.791 | 56.1528 | 56.3122 | 56.0086 | -67.0286 | -0.086417 | -0.12176 | -0.014485 | 0.014249 | 0.10067 | -0.19899 | -0.08423 | -0.27294 | -0.2071 | -0.005445 | -0.035371 | 0.23757 | -0.04766 | -0.35122 | 122.9938 | 122.9165 | 123.0313 | 66.7846 | -123.202 | 122.9084 | 123.0679 | 122.7643 | 66.7881 | -123.3885
210.7969 | 123.2162 | -66.7557 | 56.3553 | 0.0094624 | -0.0024252 | 0.00082041 | 0.057293 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0065235 | 0.062705 | -66.761 | 0.028878 | -66.7368 | 56.2427 | 56.1517 | 56.2802 | -66.8467 | -66.7611 | 0.027831 | -66.7956 | 56.1528 | 56.3214 | 56.0773 | -67.0332 | -0.090996 | -0.1126 | -0.005328 | 0.018828 | 0.10982 | -0.20358 | -0.075075 | -0.27752 | -0.20253 | -0.005445 | -0.03995 | 0.23757 | -0.033926 | -0.27797 | 122.9984 | 122.9074 | 123.0359 | 66.7846 | -123.202 | 122.9084 | 123.077 | 122.833 | 66.7835 | -123.3885
211.7969 | 123.2986 | -66.7007 | 56.3049 | -0.0057996 | -0.0022116 | 0.0010342 | 0.057506 | -0.0011987 | 0.06365 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0067371 | 0.062919 | -66.7564 | 0.033457 | -66.7368 | 56.2427 | 56.1471 | 56.2619 | -66.8375 | -66.7657 | 0.036989 | -66.791 | 56.1528 | 56.3168 | 56.0086 | -67.0286 | -0.13677 | -0.06225 | -0.055681 | -0.036103 | 0.10067 | -0.1578 | -0.043035 | -0.32787 | -0.15217 | -0.064954 | -0.090302 | 0.23757 | 0.01185 | -0.29629 | 122.9434 | 122.8479 | 122.9626 | 66.7342 | -123.1424 | 122.8535 | 123.0175 | 122.7094 | 66.7377 | -123.3335
212.7969 | 123.2529 | -66.7603 | 56.3278 | 0.0094624 | -0.0022116 | 0.00082041 | 0.057293 | -0.00098494 | 0.06365 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0067371 | 0.062705 | -66.761 | 0.028878 | -66.7368 | 56.2427 | 56.1517 | 56.2756 | -66.8421 | -66.7611 | 0.03241 | -66.7865 | 56.1573 | 56.3168 | 56.027 | -67.0332 | -0.081839 | -0.085138 | -0.00075 | 0.023406 | 0.10525 | -0.17611 | -0.052187 | -0.27294 | -0.17048 | -0.000867 | -0.026215 | 0.24673 | -0.011038 | -0.30087 | 123.0029 | 122.912 | 123.0359 | 66.7891 | -123.1699 | 122.9176 | 123.077 | 122.7872 | 66.7927 | -123.361
213.7969 | 123.2025 | -66.7648 | 56.3507 | 0.0094624 | -0.0022116 | 0.00082041 | 0.05772 | -0.00077134 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0067371 | 0.062919 | -66.7656 | 0.028878 | -66.7368 | 56.2473 | 56.1471 | 56.2756 | -66.8421 | -66.752 | 0.023253 | -66.791 | 56.1528 | 56.3214 | 56.0727 | -67.0378 | -0.077261 | -0.10345 | -0.000751 | 0.027984 | 0.10525 | -0.20358 | -0.075075 | -0.27294 | -0.19795 | 0.012869 | -0.026215 | 0.24673 | -0.029348 | -0.27797 | 123.0121 | 122.912 | 123.0405 | 66.7937 | -123.1928 | 122.9176 | 123.0862 | 122.8376 | 66.7881 | -123.3885
214.7969 | 123.262 | -66.7374 | 56.3232 | 0.0094624 | -0.0024252 | 0.0010342 | 0.057506 | -0.00098494 | 0.063437 | 0.013506 | 0.00025007 | 0.00046581 | 0.060802 | 0.0067371 | 0.062491 | -66.761 | 0.028878 | -66.7414 | 56.2473 | 56.1563 | 56.2711 | -66.8375 | -66.7611 | 0.027831 | -66.7956 | 56.1528 | 56.3168 | 56.0727 | -67.0332 | -0.10015 | -0.075982 | -0.023638 | -0.004061 | 0.096087 | -0.16695 | -0.052188 | -0.29583 | -0.17048 | -0.023755 | -0.05826 | 0.23757 | -0.00646 | -0.2505 | 122.9846 | 122.8937 | 123.0084 | 66.7662 | -123.1608 | 122.8901 | 123.0541 | 122.8101 | 66.7652 | -123.3564
215.7969 | 123.2117 | -66.7648 | 56.3324 | -0.0057996 | -0.0024252 | 0.00082041 | 0.057506 | -0.00098494 | 0.063223 | 0.0058755 | -0.00017733 | 0.00046581 | 0.061229 | 0.0065235 | 0.062919 | -66.761 | 0.033457 | -66.7414 | 56.2473 | 56.1563 | 56.2756 | -66.8421 | -66.7565 | 0.027831 | -66.7865 | 56.1573 | 56.3214 | 56.0361 | -67.0286 | -0.077261 | -0.085137 | 0.003828 | 0.023405 | 0.10067 | -0.17611 | -0.056764 | -0.26378 | -0.17506 | 0.00829 | -0.021637 | 0.24215 | -0.011037 | -0.29629 | 123.0121 | 122.9211 | 123.0405 | 66.7983 | -123.1745 | 122.9222 | 123.0862 | 122.8009 | 66.7927 | -123.361
216.7969 | 123.2208 | -66.7374 | 56.3141 | -0.0057996 | -0.0024252 | 0.00082041 | 0.05772 | -0.00098494 | 0.063437 | 0.0058755 | 0.00025007 | 0.00025221 | 0.061657 | 0.0067371 | 0.062919 | -66.761 | 0.028878 | -66.7414 | 56.2473 | 56.1563 | 56.2848 | -66.8467 | -66.7611 | 0.036989 | -66.791 | 56.1528 | 56.3168 | 56.0544 | -67.0286 | -0.10931 | -0.066827 | -0.023638 | -0.004061 | 0.10524 | -0.1578 | -0.029297 | -0.29125 | -0.16133 | -0.023755 | -0.053681 | 0.23757 | 0.002695 | -0.25966 | 122.9846 | 122.8937 | 123.0222 | 66.7662 | -123.1608 | 122.8901 | 123.0541 | 122.7918 | 66.7744 | -123.3427
217.7969 | 123.1888 | -66.7374 | 56.3187 | 0.0018314 | -0.0026388 | 0.00082041 | 0.057293 | -0.0011987 | 0.063437 | 0.013506 | 0.00046367 | 0.00046581 | 0.061229 | 0.0060961 | 0.062705 | -66.761 | 0.028878 | -66.7368 | 56.2427 | 56.1563 | 56.2802 | -66.8009 | -66.7657 | 0.03241 | -66.791 | 56.1528 | 56.3168 | 56.0682 | -67.0424 | -0.063516 | -0.075983 | -0.023638 | 0.000518 | 0.064034 | -0.16238 | -0.038454 | -0.30499 | -0.16591 | -0.028333 | -0.053681 | 0.25131 | -0.001883 | -0.25051 | 122.98 | 122.8937 | 123.0176 | 66.7662 | -123.1195 | 122.8901 | 123.0541 | 122.8055 | 66.7698 | -123.361
218.7969 | 123.23 | -66.7511 | 56.337 | -0.013431 | -0.0022116 | 0.00039321 | 0.057506 | -0.0011987 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.061229 | 0.0067371 | 0.062705 | -66.7564 | 0.033457 | -66.746 | 56.2473 | 56.1517 | 56.2756 | -66.8284 | -66.7565 | 0.036989 | -66.791 | 56.1528 | 56.3122 | 56.0407 | -67.0378 | -0.077257 | -0.089715 | -0.005327 | 0.005094 | 0.082351 | -0.18526 | -0.061342 | -0.28668 | -0.18422 | -0.005443 | -0.039948 | 0.24673 | -0.024772 | -0.29629 | 122.9984 | 122.9028 | 123.0267 | 66.7846 | -123.1653 | 122.9039 | 123.0633 | 122.7918 | 66.7881 | -123.3747
219.7969 | 123.1842 | -66.7557 | 56.3278 | -0.0057996 | -0.0024252 | 0.00039321 | 0.057506 | -0.0011987 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0069509 | 0.062919 | -66.761 | 0.0243 | -66.7368 | 56.2518 | 56.1609 | 56.2802 | -66.7734 | -66.7565 | 0.027831 | -66.791 | 56.1573 | 56.3122 | 56.0498 | -67.0332 | -0.017733 | -0.075981 | -0.005328 | 0.018828 | 0.036561 | -0.16695 | -0.047609 | -0.27752 | -0.17048 | -0.000866 | -0.035371 | 0.24215 | -0.015617 | -0.27798 | 123.0075 | 122.9165 | 123.0359 | 66.78 | -123.1012 | 122.913 | 123.0679 | 122.8055 | 66.7835 | -123.361
220.7969 | 123.2346 | -66.7603 | 56.3416 | -0.0057996 | -0.0022116 | 0.0010342 | 0.057506 | -0.00098494 | 0.063223 | -0.001755 | 0.00025007 | 0.00025221 | 0.061016 | 0.0065235 | 0.062705 | -66.761 | 0.033457 | -66.746 | 56.2427 | 56.1654 | 56.2848 | -66.7322 | -66.7565 | 0.03241 | -66.7956 | 56.1436 | 56.3168 | 56.0041 | -67.0332 | 0.028055 | -0.098871 | -0.00075 | 0.014249 | -0.013806 | -0.17611 | -0.056763 | -0.27294 | -0.19795 | 0.003712 | -0.035372 | 0.23757 | -0.024771 | -0.33749 | 123.0029 | 122.9257 | 123.045 | 66.7937 | -123.0738 | 122.9039 | 123.077 | 122.7643 | 66.7927 | -123.3747
221.7969 | 123.23 | -66.7419 | 56.3232 | 0.0018314 | -0.0022116 | 0.00082041 | 0.05772 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0063099 | 0.063346 | -66.761 | 0.028878 | -66.7368 | 56.2381 | 56.1609 | 56.2802 | -66.7688 | -66.7611 | 0.027831 | -66.791 | 56.1573 | 56.3122 | 56.1094 | -67.0378 | -0.026887 | -0.085138 | -0.019061 | 0.005095 | 0.031982 | -0.16237 | -0.043031 | -0.29583 | -0.1659 | -0.019178 | -0.049104 | 0.24673 | -0.011039 | -0.21388 | 122.98 | 122.9028 | 123.0222 | 66.7708 | -123.0921 | 122.8993 | 123.0541 | 122.8513 | 66.7698 | -123.361
222.7969 | 123.2071 | -66.774 | 56.3095 | 0.0018314 | -0.0026388 | 0.00060681 | 0.057293 | -0.00098494 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0067371 | 0.062919 | -66.761 | 0.038035 | -66.746 | 56.2473 | 56.1563 | 56.2802 | -66.6956 | -66.7611 | 0.03241 | -66.791 | 56.1528 | 56.3076 | 56.0361 | -67.0332 | 0.07842 | -0.062249 | 0.012983 | 0.027982 | -0.050438 | -0.15322 | -0.029298 | -0.25921 | -0.15675 | 0.012866 | -0.01706 | 0.24215 | -0.001885 | -0.2734 | 123.0212 | 122.9303 | 123.0542 | 66.812 | -123.0051 | 122.9267 | 123.0816 | 122.8101 | 66.8064 | -123.3427
223.7969 | 123.2391 | -66.7374 | 56.3324 | 0.0094624 | -0.0022116 | 0.00082041 | 0.057506 | -0.00098494 | 0.063223 | -0.001755 | 0.00025007 | 0.00025221 | 0.061229 | 0.0067371 | 0.062919 | -66.761 | 0.033457 | -66.7323 | 56.2427 | 56.1654 | 56.2802 | -66.7185 | -66.7565 | 0.03241 | -66.7956 | 56.1619 | 56.3168 | 56.0086 | -67.0332 | 0.018904 | -0.089715 | -0.023638 | 0.005096 | -0.013808 | -0.16695 | -0.052186 | -0.29583 | -0.17048 | -0.019176 | -0.05826 | 0.23757 | -0.015615 | -0.32376 | 122.98 | 122.9028 | 123.0176 | 66.7708 | -123.0509 | 122.8993 | 123.0541 | 122.746 | 66.7698 | -123.3656
224.7969 | 123.2162 | -66.7648 | 56.3232 | -0.013431 | -0.0026388 | 0.00082041 | 0.057506 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061443 | 0.0069509 | 0.062919 | -66.761 | 0.028878 | -66.7414 | 56.2518 | 56.1563 | 56.2802 | -66.7643 | -66.7657 | 0.027831 | -66.791 | 56.1573 | 56.3214 | 56.0773 | -67.0424 | 0.000581 | -0.071403 | 0.003828 | 0.023405 | 0.022824 | -0.16695 | -0.043031 | -0.27752 | -0.1659 | -0.000867 | -0.026215 | 0.25131 | -0.001882 | -0.24592 | 123.0167 | 122.9211 | 123.045 | 66.7937 | -123.0875 | 122.9222 | 123.0862 | 122.8421 | 66.7927 | -123.3656
225.7969 | 123.2071 | -66.7557 | 56.3416 | -0.0057996 | -0.0022116 | 0.00060681 | 0.057079 | -0.00098494 | 0.063437 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0065235 | 0.062919 | -66.7656 | 0.033457 | -66.7368 | 56.2427 | 56.1563 | 56.2848 | -66.8284 | -66.7657 | 0.03241 | -66.7865 | 56.1528 | 56.3168 | 56.0453 | -67.0286 | -0.07268 | -0.098871 | -0.009907 | 0.018828 | 0.091508 | -0.18526 | -0.056763 | -0.27294 | -0.18879 | -0.010023 | -0.030793 | 0.24215 | -0.024771 | -0.29629 | 122.9984 | 122.912 | 123.0405 | 66.7891 | -123.1699 | 122.9084 | 123.0725 | 122.8009 | 66.7881 | -123.3702
226.7969 | 123.2208 | -66.7557 | 56.3095 | 0.0018314 | -0.0026388 | 0.00082041 | 0.057506 | -0.0011987 | 0.06365 | -0.0093855 | -0.00017733 | 0.00025221 | 0.061229 | 0.0067371 | 0.062919 | -66.7656 | 0.0243 | -66.7368 | 56.2518 | 56.1563 | 56.2802 | -66.8146 | -66.7657 | 0.03241 | -66.7956 | 56.1619 | 56.3122 | 56.0315 | -67.0286 | -0.058943 | -0.05767 | -0.009907 | 0.018828 | 0.077771 | -0.15322 | -0.029298 | -0.27294 | -0.14759 | -0.010023 | -0.03995 | 0.23299 | 0.002694 | -0.27798 | 123.0075 | 122.912 | 123.0359 | 66.78 | -123.1241 | 122.9176 | 123.0679 | 122.7872 | 66.7881 | -123.3381
227.7969 | 123.1934 | -66.7557 | 56.3232 | 0.0018314 | -0.0028526 | 0.00060681 | 0.057293 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060802 | 0.0067371 | 0.063132 | -66.7564 | 0.028878 | -66.7414 | 56.2473 | 56.1609 | 56.2848 | -66.7688 | -66.7565 | 0.03241 | -66.791 | 56.1528 | 56.3168 | 55.9995 | -67.0332 | -0.013154 | -0.075982 | -0.00075 | 0.014249 | 0.027403 | -0.16237 | -0.038452 | -0.27752 | -0.17048 | -0.000866 | -0.035371 | 0.24215 | -0.00646 | -0.32376 | 123.0029 | 122.9165 | 123.0405 | 66.7846 | -123.0921 | 122.9084 | 123.0725 | 122.7552 | 66.7881 | -123.3564
228.7969 | 123.1842 | -66.7877 | 56.282 | -0.0057996 | -0.0022116 | 0.00082041 | 0.05772 | -0.00098494 | 0.063437 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.061229 | 0.0069509 | 0.063132 | -66.7564 | 0.0243 | -66.7414 | 56.2427 | 56.1517 | 56.2848 | -66.7001 | -66.7565 | 0.03241 | -66.791 | 56.1573 | 56.3168 | 56.0086 | -67.0378 | 0.087574 | -0.039361 | 0.031294 | 0.046293 | -0.041281 | -0.13033 | 0.002747 | -0.25005 | -0.1247 | 0.031178 | -0.003327 | 0.24673 | 0.034739 | -0.27341 | 123.0304 | 122.9394 | 123.0725 | 66.812 | -122.9822 | 122.9451 | 123.1045 | 122.7964 | 66.8201 | -123.3198
229.7969 | 123.2071 | -66.7511 | 56.2958 | 0.0018314 | -0.0024252 | 0.00060681 | 0.05772 | -0.00077134 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0067371 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2473 | 56.1609 | 56.2848 | -66.8055 | -66.7657 | 0.023253 | -66.7865 | 56.1528 | 56.3168 | 55.9949 | -67.0332 | -0.054362 | -0.048516 | -0.014484 | 0.009672 | 0.064034 | -0.13491 | -0.010986 | -0.2821 | -0.14302 | -0.0146 | -0.03537 | 0.24673 | 0.021006 | -0.30087 | 122.9984 | 122.912 | 123.0359 | 66.78 | -123.1012 | 122.9039 | 123.0679 | 122.746 | 66.7744 | -123.329
230.7969 | 123.1979 | -66.7831 | 56.3141 | 0.0018314 | -0.0026388 | 0.00060681 | 0.057293 | -0.00055774 | 0.063223 | -0.0093855 | 0.00025007 | 0.00046581 | 0.061443 | 0.0069509 | 0.063132 | -66.7656 | 0.028878 | -66.7414 | 56.2473 | 56.1563 | 56.2756 | -66.7688 | -66.752 | 0.03241 | -66.7819 | 56.1619 | 56.3076 | 56.0498 | -67.024 | 0.014312 | -0.066827 | 0.017559 | 0.041715 | 0.027403 | -0.1578 | -0.038454 | -0.2409 | -0.15217 | 0.031179 | 0.001252 | 0.24215 | -0.006463 | -0.26424 | 123.0304 | 122.9394 | 123.0588 | 66.812 | -123.0829 | 122.9451 | 123.0908 | 122.833 | 66.8156 | -123.3381
231.7969 | 123.2391 | -66.7374 | 56.3232 | -0.0057996 | -0.0024252 | 0.00039321 | 0.057506 | -0.0011987 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0071645 | 0.063132 | -66.761 | 0.033457 | -66.746 | 56.2473 | 56.1563 | 56.2894 | -66.8009 | -66.7565 | 0.027831 | -66.791 | 56.1528 | 56.3214 | 56.0819 | -67.0378 | -0.063516 | -0.075982 | -0.023638 | -0.008639 | 0.054877 | -0.16695 | -0.033873 | -0.30041 | -0.17048 | -0.019176 | -0.053681 | 0.24673 | -0.001882 | -0.24135 | 122.9846 | 122.8937 | 123.0267 | 66.7708 | -123.1241 | 122.8901 | 123.0587 | 122.8193 | 66.7652 | -123.361
232.7969 | 123.23 | -66.7648 | 56.3095 | 0.0018314 | -0.0026388 | 0.0012478 | 0.057293 | -0.00098494 | 0.063437 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0067371 | 0.062705 | -66.761 | 0.033457 | -66.7414 | 56.2518 | 56.1654 | 56.2802 | -66.8375 | -66.7611 | 0.027831 | -66.7865 | 56.1528 | 56.3122 | 56.0956 | -67.0378 | -0.072682 | -0.05767 | 0.003828 | 0.023405 | 0.096087 | -0.14406 | -0.029298 | -0.27294 | -0.15675 | 0.003711 | -0.021637 | 0.25131 | 0.002694 | -0.21388 | 123.0167 | 122.9303 | 123.045 | 66.7983 | -123.147 | 122.9176 | 123.077 | 122.8605 | 66.7927 | -123.3473
233.7969 | 123.2346 | -66.7419 | 56.3232 | 0.0018314 | -0.0026388 | 0.00082041 | 0.057506 | -0.00098494 | 0.063009 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0067371 | 0.062919 | -66.7564 | 0.028878 | -66.7368 | 56.2473 | 56.1654 | 56.2894 | -66.8467 | -66.7565 | 0.03241 | -66.791 | 56.1573 | 56.303 | 56.0636 | -67.0332 | -0.10473 | -0.075982 | -0.014483 | 0.005095 | 0.10982 | -0.1578 | -0.033873 | -0.29125 | -0.1659 | -0.014599 | -0.049104 | 0.24215 | -0.020196 | -0.25966 | 122.9892 | 122.9074 | 123.0313 | 66.7708 | -123.1699 | 122.8993 | 123.045 | 122.8055 | 66.7744 | -123.3564
234.7969 | 123.2529 | -66.7831 | 56.3095 | 0.0018314 | -0.0030662 | 0.0010342 | 0.057506 | -0.00077134 | 0.063437 | -0.017016 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0073781 | 0.062705 | -66.761 | 0.0243 | -66.7414 | 56.2427 | 56.1471 | 56.2756 | -66.8421 | -66.7565 | 0.027831 | -66.7865 | 56.1573 | 56.3122 | 56.0956 | -67.0378 | -0.058951 | -0.066827 | 0.022138 | 0.041715 | 0.10067 | -0.16238 | -0.033876 | -0.25463 | -0.15217 | 0.0266 | -0.003327 | 0.25131 | 0.002694 | -0.21388 | 123.0258 | 122.9303 | 123.0588 | 66.8074 | -123.1516 | 122.9405 | 123.0953 | 122.8788 | 66.811 | -123.3473
235.7969 | 123.2483 | -66.7511 | 56.3141 | -0.0057996 | -0.0024252 | 0.00082041 | 0.057293 | -0.00077134 | 0.063223 | 0.0058755 | -0.00017733 | 0.00025221 | 0.061016 | 0.0069509 | 0.062491 | -66.7518 | 0.028878 | -66.7368 | 56.2518 | 56.1563 | 56.2848 | -66.8421 | -66.7611 | 0.03241 | -66.791 | 56.1573 | 56.3122 | 56.0819 | -67.0332 | -0.090994 | -0.062248 | -0.000748 | 0.014251 | 0.10525 | -0.1578 | -0.029297 | -0.2821 | -0.15675 | -0.010022 | -0.039948 | 0.24215 | -0.001884 | -0.23219 | 123.0029 | 122.9074 | 123.0359 | 66.78 | -123.1562 | 122.9084 | 123.0633 | 122.833 | 66.7835 | -123.3473
236.7969 | 123.1796 | -66.7831 | 56.3004 | 0.0018314 | -0.0028526 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | 0.013506 | 0.00025007 | 0.00046581 | 0.061016 | 0.0067371 | 0.062919 | -66.761 | 0.038035 | -66.7414 | 56.2427 | 56.1563 | 56.2756 | -66.8421 | -66.7611 | 0.027831 | -66.791 | 56.1528 | 56.3168 | 56.0636 | -67.0378 | -0.058951 | -0.057672 | 0.022138 | 0.041715 | 0.10067 | -0.14406 | -0.024721 | -0.25463 | -0.14759 | 0.022021 | -0.007905 | 0.24673 | 0.016428 | -0.23677 | 123.0258 | 122.9394 | 123.0588 | 66.8212 | -123.1424 | 122.9359 | 123.0999 | 122.8467 | 66.811 | -123.3381
237.7969 | 123.2254 | -66.7694 | 56.3004 | -0.0057996 | -0.0026388 | 0.0012478 | 0.057079 | -0.00077134 | 0.063437 | -0.001755 | 0.00025007 | 0.00067941 | 0.061016 | 0.0069509 | 0.062919 | -66.7518 | 0.033457 | -66.746 | 56.2473 | 56.1563 | 56.2848 | -66.8467 | -66.7565 | 0.027831 | -66.791 | 56.1528 | 56.3076 | 56.0361 | -67.0332 | -0.077263 | -0.053094 | 0.017562 | 0.023404 | 0.10067 | -0.14406 | -0.015564 | -0.26379 | -0.14759 | 0.012867 | -0.021638 | 0.24215 | 0.00727 | -0.26424 | 123.0167 | 122.9257 | 123.0542 | 66.8029 | -123.147 | 122.9222 | 123.077 | 122.8055 | 66.7972 | -123.3335
238.7969 | 123.1613 | -66.7877 | 56.2958 | -0.013431 | -0.0022116 | 0.00082041 | 0.057293 | -0.0014123 | 0.063223 | -0.001755 | 0.00025007 | 0.00067941 | 0.061016 | 0.0071645 | 0.062705 | -66.7564 | 0.033457 | -66.7414 | 56.2427 | 56.1563 | 56.2894 | -66.8421 | -66.7611 | 0.03241 | -66.7865 | 56.1573 | 56.3214 | 56.0453 | -67.0378 | -0.054373 | -0.053094 | 0.031294 | 0.046293 | 0.10067 | -0.13949 | -0.006407 | -0.25005 | -0.13844 | 0.026599 | 0.001251 | 0.25131 | 0.025584 | -0.25051 | 123.0304 | 122.944 | 123.0771 | 66.8212 | -123.1379 | 122.9451 | 123.1091 | 122.833 | 66.8201 | -123.3336
239.7969 | 123.1888 | -66.7831 | 56.3049 | -0.0057996 | -0.0026388 | 0.0010342 | 0.05772 | -0.0011987 | 0.063437 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0069509 | 0.062919 | -66.7564 | 0.0243 | -66.7414 | 56.2427 | 56.1471 | 56.2756 | -66.8421 | -66.7565 | 0.03241 | -66.791 | 56.1528 | 56.3168 | 56.0361 | -67.0378 | -0.058951 | -0.06225 | 0.026716 | 0.041715 | 0.10067 | -0.1578 | -0.029299 | -0.25463 | -0.15217 | 0.0266 | -0.007905 | 0.24673 | 0.01185 | -0.26882 | 123.0258 | 122.9303 | 123.0588 | 66.8074 | -123.147 | 122.9359 | 123.0999 | 122.8193 | 66.8156 | -123.3427
240.7969 | 123.0377 | -66.806 | 56.2866 | -0.013431 | -0.0024252 | 0.00082041 | 0.057506 | -0.0011987 | 0.063223 | -0.0093855 | -0.00017733 | 0.00046581 | 0.061443 | 0.0071645 | 0.063132 | -66.761 | 0.028878 | -66.7414 | 56.2473 | 56.1563 | 56.2802 | -66.8421 | -66.7611 | 0.036989 | -66.791 | 56.1573 | 56.3168 | 56.0086 | -67.0378 | -0.036063 | -0.039361 | 0.045026 | 0.064603 | 0.10067 | -0.13033 | -0.00641 | -0.23174 | -0.12928 | 0.044909 | 0.014983 | 0.24673 | 0.030161 | -0.27798 | 123.0533 | 122.9623 | 123.0862 | 66.8349 | -123.1287 | 122.9634 | 123.1228 | 122.8147 | 66.843 | -123.3244
241.7969 | 123.2391 | -66.7465 | 56.3049 | -0.0057996 | -0.0028526 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | 0.0058755 | -0.00017733 | 0.00046581 | 0.061229 | 0.0073781 | 0.062919 | -66.761 | 0.033457 | -66.7368 | 56.2473 | 56.1563 | 56.2802 | -66.8421 | -66.7611 | 0.03241 | -66.791 | 56.1482 | 56.3122 | 56.0315 | -67.0424 | -0.095572 | -0.057672 | -0.014483 | 0.009673 | 0.10525 | -0.14864 | -0.024721 | -0.29583 | -0.15675 | -0.0146 | -0.044526 | 0.25131 | 0.007271 | -0.2734 | 122.9938 | 122.9028 | 123.0267 | 66.78 | -123.147 | 122.8947 | 123.0587 | 122.7781 | 66.7789 | -123.3473
242.7969 | 123.2117 | -66.7786 | 56.2866 | -0.0057996 | -0.0022116 | 0.00039321 | 0.057293 | -0.0011987 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.061016 | 0.0071645 | 0.062919 | -66.7564 | 0.028878 | -66.7368 | 56.2473 | 56.1654 | 56.2802 | -66.8375 | -66.7565 | 0.036989 | -66.791 | 56.1528 | 56.3168 | 56.0727 | -67.0469 | -0.05895 | -0.039361 | 0.022138 | 0.041716 | 0.10067 | -0.12117 | -0.00641 | -0.26837 | -0.13386 | 0.022022 | -0.012483 | 0.25588 | 0.030161 | -0.21388 | 123.0258 | 122.944 | 123.0588 | 66.8074 | -123.1241 | 122.9313 | 123.0953 | 122.8513 | 66.8156 | -123.3336
243.7969 | 123.2941 | -66.7603 | 56.3187 | -0.0057996 | -0.0026388 | 0.00082041 | 0.057293 | -0.00098494 | 0.063437 | 0.0058755 | 3.6274e-05 | 3.8406e-05 | 0.061016 | 0.0071645 | 0.062491 | -66.7564 | 0.028878 | -66.746 | 56.2473 | 56.1517 | 56.2848 | -66.8421 | -66.7611 | 0.027831 | -66.7865 | 56.1573 | 56.3168 | 56.0544 | -67.0378 | -0.081839 | -0.071405 | 0.003828 | 0.014249 | 0.096088 | -0.16695 | -0.033875 | -0.27752 | -0.16133 | -0.000867 | -0.026215 | 0.25131 | -0.001883 | -0.26424 | 123.0075 | 122.912 | 123.045 | 66.7891 | -123.1608 | 122.9176 | 123.077 | 122.8147 | 66.7881 | -123.3564
244.7969 | 123.2117 | -66.7877 | 56.2866 | -0.0057996 | -0.0028526 | 0.00082041 | 0.057506 | -0.0011987 | 0.06365 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.061229 | 0.0071645 | 0.062705 | -66.7656 | 0.033457 | -66.7368 | 56.2473 | 56.1609 | 56.2848 | -66.8421 | -66.7657 | 0.027831 | -66.7865 | 56.1573 | 56.3168 | 56.0178 | -67.0332 | -0.054373 | -0.039361 | 0.022137 | 0.050872 | 0.10525 | -0.12575 | -0.001831 | -0.24548 | -0.12928 | 0.022021 | 0.001251 | 0.24673 | 0.030161 | -0.26883 | 123.035 | 122.9486 | 123.0725 | 66.8212 | -123.1287 | 122.9451 | 123.1045 | 122.8055 | 66.8156 | -123.3198
245.7969 | 123.2346 | -66.7603 | 56.2912 | 0.0018314 | -0.0026388 | 0.00082041 | 0.05772 | -0.00077134 | 0.063223 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0071645 | 0.062705 | -66.761 | 0.028878 | -66.7368 | 56.2518 | 56.1563 | 56.2756 | -66.8421 | -66.7474 | 0.027831 | -66.7865 | 56.1482 | 56.3168 | 55.9903 | -67.0469 | -0.081839 | -0.03936 | -0.00075 | 0.023406 | 0.10525 | -0.13491 | -0.015566 | -0.28668 | -0.14302 | 0.012869 | -0.026215 | 0.26046 | 0.025583 | -0.30087 | 123.0121 | 122.9165 | 123.0359 | 66.7891 | -123.1333 | 122.9084 | 123.077 | 122.7506 | 66.7881 | -123.3381
246.7969 | 123.1934 | -66.7557 | 56.2866 | -0.0057996 | -0.0024252 | 0.00082041 | 0.057293 | -0.0014123 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0073781 | 0.063132 | -66.7518 | 0.033457 | -66.746 | 56.2473 | 56.1471 | 56.2848 | -66.8421 | -66.752 | 0.027831 | -66.7819 | 56.1573 | 56.3168 | 56.0544 | -67.0378 | -0.086417 | -0.039361 | 0.003829 | 0.009671 | 0.096088 | -0.13949 | -0.001831 | -0.2821 | -0.12928 | 0.003713 | -0.026214 | 0.25588 | 0.030161 | -0.2322 | 123.0029 | 122.9028 | 123.0405 | 66.7891 | -123.1287 | 122.913 | 123.0725 | 122.8101 | 66.7835 | -123.3244
247.7969 | 123.2254 | -66.7374 | 56.3095 | 0.0018314 | -0.0024252 | 0.00082041 | 0.057293 | -0.0014123 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061229 | 0.0071645 | 0.062919 | -66.7656 | 0.033457 | -66.7368 | 56.2427 | 56.1609 | 56.2802 | -66.8467 | -66.7611 | 0.036989 | -66.791 | 56.1528 | 56.3214 | 56.0544 | -67.0424 | -0.10931 | -0.066827 | -0.028217 | 0.000518 | 0.10982 | -0.14864 | -0.029298 | -0.30499 | -0.15675 | -0.023755 | -0.053681 | 0.25131 | 0.011851 | -0.25509 | 122.98 | 122.8982 | 123.0176 | 66.7708 | -123.1562 | 122.8901 | 123.0587 | 122.7918 | 66.7744 | -123.3519
248.7969 | 123.1842 | -66.7694 | 56.3278 | -0.0057996 | -0.0028526 | 0.00060681 | 0.057506 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0071645 | 0.062919 | -66.7518 | 0.028878 | -66.7323 | 56.2427 | 56.1563 | 56.2802 | -66.8513 | -66.7565 | 0.027831 | -66.791 | 56.1619 | 56.3168 | 56.0041 | -67.0378 | -0.081842 | -0.085138 | 0.017562 | 0.037139 | 0.11898 | -0.17153 | -0.047609 | -0.26837 | -0.1659 | 0.012867 | -0.021638 | 0.24673 | -0.011038 | -0.32376 | 123.0121 | 122.9257 | 123.0496 | 66.7983 | -123.1791 | 122.9313 | 123.0862 | 122.7735 | 66.7972 | -123.3656
249.7969 | 123.2071 | -66.7648 | 56.3187 | 0.0094624 | -0.0024252 | 0.00082041 | 0.057506 | -0.00077134 | 0.063437 | 0.0058755 | 0.00025007 | 0.00025221 | 0.061016 | 0.0069509 | 0.062919 | -66.761 | 0.033457 | -66.7368 | 56.2473 | 56.1563 | 56.2802 | -66.8192 | -66.752 | 0.03241 | -66.7865 | 56.1528 | 56.3122 | 56.059 | -67.0332 | -0.054366 | -0.071405 | 0.003828 | 0.027984 | 0.08235 | -0.16238 | -0.038454 | -0.26836 | -0.16591 | 0.012869 | -0.021637 | 0.24673 | -0.006462 | -0.25966 | 123.0121 | 122.9211 | 123.045 | 66.7983 | -123.1379 | 122.9176 | 123.077 | 122.8238 | 66.7972 | -123.3519
251.25 | 123.2025 | -66.7511 | 56.2866 | -0.0057996 | -0.0028526 | 0.0010342 | 0.057293 | -0.00098494 | 0.063223 | 0.0058755 | 0.00046367 | 0.00025221 | 0.061443 | 0.0067371 | 0.062705 | -66.7518 | 0.028878 | -66.7323 | 56.2473 | 56.1654 | 56.2894 | -66.8421 | -66.752 | 0.041567 | -66.791 | 56.1573 | 56.3168 | 56.0453 | -67.0424 | -0.090994 | -0.039361 | -0.000748 | 0.018829 | 0.10982 | -0.12117 | 0.002748 | -0.29125 | -0.12928 | -0.000864 | -0.039948 | 0.25131 | 0.030161 | -0.24135 | 122.9984 | 122.9165 | 123.0405 | 66.78 | -123.1287 | 122.9084 | 123.0679 | 122.7964 | 66.7927 | -123.329
251.8281 | 123.1934 | -66.7374 | 56.337 | -0.0057996 | -0.0028526 | 0.00082041 | 0.057079 | -0.00098494 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0069509 | 0.062919 | -66.761 | 0.019721 | -66.7368 | 56.2473 | 56.1609 | 56.2756 | -66.8009 | -66.7565 | 0.03241 | -66.791 | 56.1573 | 56.3168 | 56.0773 | -67.0378 | -0.063516 | -0.089715 | -0.023638 | 0.000518 | 0.064034 | -0.17611 | -0.061342 | -0.30041 | -0.17964 | -0.019176 | -0.053681 | 0.24673 | -0.020193 | -0.25966 | 122.9846 | 122.8982 | 123.013 | 66.7571 | -123.1379 | 122.8947 | 123.0541 | 122.8147 | 66.7698 | -123.3747
252.7969 | 123.23 | -66.7648 | 56.3507 | -0.021062 | -0.0028526 | 0.00082041 | 0.057506 | -0.00098494 | 0.063223 | -0.001755 | 0.00025007 | 3.8406e-05 | 0.061016 | 0.0071645 | 0.062919 | -66.7564 | 0.028878 | -66.7414 | 56.2427 | 56.1609 | 56.2802 | -66.8055 | -66.7611 | 0.027831 | -66.7819 | 56.1573 | 56.3122 | 55.9949 | -67.0378 | -0.040629 | -0.10803 | 0.008406 | 0.023405 | 0.064034 | -0.18984 | -0.070497 | -0.27294 | -0.19337 | 0.003711 | -0.017058 | 0.25588 | -0.038505 | -0.35581 | 123.0075 | 122.9257 | 123.045 | 66.7937 | -123.1562 | 122.9222 | 123.077 | 122.7597 | 66.7927 | -123.3885
253.7969 | 123.2025 | -66.7099 | 56.337 | 0.0018314 | -0.0026388 | 0.0012478 | 0.057506 | -0.0014123 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061229 | 0.0073781 | 0.062919 | -66.761 | 0.038035 | -66.7368 | 56.2427 | 56.1471 | 56.2894 | -66.8375 | -66.752 | 0.027831 | -66.7819 | 56.1528 | 56.3214 | 56.0544 | -67.0332 | -0.12761 | -0.094293 | -0.051104 | -0.026948 | 0.10067 | -0.18984 | -0.047606 | -0.3233 | -0.18422 | -0.042063 | -0.07199 | 0.25131 | -0.015615 | -0.28255 | 122.9526 | 122.857 | 122.9993 | 66.7479 | -123.1745 | 122.8627 | 123.0313 | 122.7643 | 66.7377 | -123.3702
254.7969 | 123.1934 | -66.7603 | 56.3507 | 0.0094624 | -0.0022116 | 0.00082041 | 0.05772 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061443 | 0.0073781 | 0.062919 | -66.761 | 0.028878 | -66.7368 | 56.2473 | 56.1563 | 56.2848 | -66.8421 | -66.7565 | 0.03241 | -66.7865 | 56.1528 | 56.3168 | 56.0636 | -67.0286 | -0.081839 | -0.10345 | -0.00075 | 0.023406 | 0.10525 | -0.19442 | -0.065918 | -0.26836 | -0.19795 | 0.003712 | -0.026215 | 0.24215 | -0.033926 | -0.28713 | 123.0075 | 122.9165 | 123.045 | 66.7891 | -123.1928 | 122.913 | 123.077 | 122.8238 | 66.7927 | -123.3793
255.7969 | 123.1796 | -66.7328 | 56.3416 | -0.0057996 | -0.0028526 | 0.00082041 | 0.057293 | -0.0014123 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0071645 | 0.062491 | -66.761 | 0.033457 | -66.7277 | 56.2473 | 56.1563 | 56.2848 | -66.8329 | -66.7565 | 0.027831 | -66.7865 | 56.1573 | 56.3168 | 56.0773 | -67.0332 | -0.10015 | -0.094293 | -0.028216 | 0.005096 | 0.10524 | -0.18526 | -0.056763 | -0.30041 | -0.18421 | -0.023754 | -0.053681 | 0.24673 | -0.024771 | -0.26424 | 122.98 | 122.8891 | 123.0176 | 66.7662 | -123.1745 | 122.8901 | 123.0496 | 122.8101 | 66.7606 | -123.3747
256.7969 | 123.1888 | -66.7786 | 56.3187 | -0.013431 | -0.0024252 | 0.00060681 | 0.057079 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0071645 | 0.062705 | -66.761 | 0.0243 | -66.7414 | 56.2427 | 56.1563 | 56.2802 | -66.8375 | -66.7565 | 0.036989 | -66.7819 | 56.1573 | 56.303 | 56.027 | -67.0378 | -0.05895 | -0.075983 | 0.01756 | 0.037137 | 0.096087 | -0.16238 | -0.038454 | -0.25921 | -0.16133 | 0.022022 | -0.003326 | 0.25588 | -0.015619 | -0.29171 | 123.0212 | 122.9349 | 123.0588 | 66.8029 | -123.1562 | 122.9359 | 123.0816 | 122.8055 | 66.8156 | -123.3564
257.7969 | 123.2941 | -66.7328 | 56.3095 | 0.0018314 | -0.0026388 | 0.00082041 | 0.057506 | -0.00077134 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0067371 | 0.062278 | -66.761 | 0.0243 | -66.7277 | 56.2427 | 56.1517 | 56.2848 | -66.8513 | -66.7565 | 0.023253 | -66.7819 | 56.1528 | 56.3168 | 56.0727 | -67.0424 | -0.11846 | -0.066827 | -0.028216 | 0.005096 | 0.12356 | -0.1578 | -0.024719 | -0.30957 | -0.15675 | -0.023754 | -0.049102 | 0.26046 | 0.007273 | -0.23677 | 122.9755 | 122.8845 | 123.0176 | 66.7571 | -123.1608 | 122.8855 | 123.0496 | 122.8055 | 66.756 | -123.3519
258.7969 | 123.1979 | -66.7282 | 56.3278 | -0.0057996 | -0.0024252 | 0.0010342 | 0.057506 | -0.00098494 | 0.063223 | 0.0058755 | 0.00025007 | 0.00067941 | 0.061016 | 0.0067371 | 0.062919 | -66.7564 | 0.0243 | -66.7368 | 56.2427 | 56.1563 | 56.2756 | -66.8467 | -66.752 | 0.03241 | -66.7865 | 56.1482 | 56.3122 | 56.0178 | -67.0378 | -0.11846 | -0.085138 | -0.028216 | -0.008638 | 0.10982 | -0.17153 | -0.052187 | -0.30956 | -0.17964 | -0.023753 | -0.058259 | 0.25131 | -0.015617 | -0.31003 | 122.9709 | 122.8845 | 123.0038 | 66.7525 | -123.1745 | 122.8764 | 123.0404 | 122.746 | 66.7606 | -123.3656
259.7969 | 123.3124 | -66.7053 | 56.3004 | 0.0018314 | -0.0028526 | 0.00060681 | 0.057293 | -0.00098494 | 0.063437 | -0.001755 | 0.00025007 | 0.00046581 | 0.061229 | 0.0069509 | 0.062919 | -66.7564 | 0.028878 | -66.7323 | 56.2427 | 56.1563 | 56.2802 | -66.8375 | -66.752 | 0.03241 | -66.791 | 56.1573 | 56.3122 | 55.9995 | -67.0424 | -0.13219 | -0.057672 | -0.051104 | -0.026948 | 0.10524 | -0.14406 | -0.020143 | -0.33703 | -0.14301 | -0.046641 | -0.085725 | 0.25131 | 0.011849 | -0.30087 | 122.948 | 122.8616 | 122.9855 | 66.7342 | -123.1379 | 122.8627 | 123.0175 | 122.7048 | 66.7377 | -123.3427
260.7969 | 123.1934 | -66.7557 | 56.3507 | 0.0018314 | -0.0026388 | 0.0012478 | 0.057293 | -0.00098494 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061229 | 0.0069509 | 0.062705 | -66.761 | 0.028878 | -66.7368 | 56.2381 | 56.1563 | 56.2802 | -66.8421 | -66.7565 | 0.027831 | -66.791 | 56.1573 | 56.3168 | 55.9995 | -67.0424 | -0.086417 | -0.1126 | -0.005328 | 0.018828 | 0.10525 | -0.19442 | -0.070497 | -0.28668 | -0.19337 | -0.000866 | -0.035371 | 0.25131 | -0.033926 | -0.35123 | 122.9938 | 122.912 | 123.0359 | 66.7846 | -123.1928 | 122.913 | 123.0725 | 122.7552 | 66.7835 | -123.3931
261.7969 | 123.2346 | -66.7557 | 56.3187 | -0.0057996 | -0.0026388 | 0.0010342 | 0.057506 | -0.00098494 | 0.063223 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060802 | 0.0073781 | 0.062919 | -66.7518 | 0.033457 | -66.7368 | 56.2427 | 56.1654 | 56.2848 | -66.8375 | -66.7565 | 0.03241 | -66.7865 | 56.1573 | 56.3122 | 56.0407 | -67.0378 | -0.081838 | -0.075983 | 0.003829 | 0.018828 | 0.10067 | -0.15322 | -0.033875 | -0.2821 | -0.16133 | -0.000866 | -0.030793 | 0.25131 | -0.006462 | -0.27798 | 122.9984 | 122.9211 | 123.0405 | 66.7891 | -123.1562 | 122.913 | 123.0679 | 122.7964 | 66.7881 | -123.3564
262.7969 | 123.1796 | -66.7694 | 56.3324 | 0.0018314 | -0.0028526 | 0.0010342 | 0.057506 | -0.0011987 | 0.063223 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0071645 | 0.062491 | -66.7656 | 0.028878 | -66.7414 | 56.2381 | 56.1609 | 56.2848 | -66.8375 | -66.7565 | 0.027831 | -66.7865 | 56.1482 | 56.3168 | 56.0178 | -67.0332 | -0.068105 | -0.094293 | 0.003826 | 0.027982 | 0.096087 | -0.17153 | -0.047607 | -0.26379 | -0.18422 | 0.012867 | -0.01706 | 0.24673 | -0.015615 | -0.3146 | 123.0075 | 122.9303 | 123.0542 | 66.7983 | -123.1699 | 122.9176 | 123.0862 | 122.7872 | 66.7972 | -123.3656
263.7969 | 123.3124 | -66.7053 | 56.2866 | 0.0018314 | -0.0026388 | 0.0010342 | 0.05772 | -0.00098494 | 0.063437 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061229 | 0.0069509 | 0.063132 | -66.7564 | 0.028878 | -66.7368 | 56.2427 | 56.1471 | 56.2848 | -66.8375 | -66.7657 | 0.018674 | -66.7819 | 56.1528 | 56.3168 | 56.0498 | -67.0469 | -0.13219 | -0.043939 | -0.051104 | -0.031526 | 0.10067 | -0.13949 | -0.001831 | -0.34161 | -0.13386 | -0.060377 | -0.076568 | 0.26504 | 0.030161 | -0.23678 | 122.948 | 122.8525 | 122.9901 | 66.7342 | -123.1241 | 122.8581 | 123.0221 | 122.7552 | 66.724 | -123.3336
264.7969 | 123.2162 | -66.7374 | 56.3507 | 0.0018314 | -0.0026388 | 0.0010342 | 0.05772 | -0.0014123 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.061016 | 0.0069509 | 0.062491 | -66.7564 | 0.028878 | -66.7323 | 56.2427 | 56.1563 | 56.2802 | -66.8467 | -66.7474 | 0.027831 | -66.7819 | 56.1528 | 56.3214 | 56.0361 | -67.0332 | -0.10931 | -0.10803 | -0.01906 | 0.005096 | 0.1144 | -0.19442 | -0.070497 | -0.29583 | -0.19795 | -0.010019 | -0.044524 | 0.25131 | -0.029348 | -0.3146 | 122.98 | 122.8937 | 123.0176 | 66.7662 | -123.1974 | 122.8901 | 123.0587 | 122.7735 | 66.7652 | -123.3839
265.7969 | 123.3307 | -66.6824 | 56.2912 | 0.0094624 | -0.0026388 | 0.0010342 | 0.057506 | -0.0011987 | 0.063437 | -0.001755 | 0.00025007 | 0.00025221 | 0.060802 | 0.0075919 | 0.062705 | -66.7518 | 0.028878 | -66.7323 | 56.2473 | 56.1471 | 56.2711 | -66.8375 | -66.7565 | 0.023253 | -66.791 | 56.1619 | 56.3168 | 55.972 | -67.0332 | -0.15508 | -0.043939 | -0.069413 | -0.049836 | 0.10524 | -0.14407 | -0.020145 | -0.35076 | -0.12928 | -0.074108 | -0.10861 | 0.24215 | 0.025583 | -0.31919 | 122.9297 | 122.8296 | 122.9535 | 66.7113 | -123.1287 | 122.8444 | 122.9992 | 122.6544 | 66.7057 | -123.3244
266.7969 | 123.2712 | -66.7511 | 56.2683 | -0.0057996 | -0.0032798 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.017016 | 3.6274e-05 | 3.8406e-05 | 0.061016 | 0.0073781 | 0.062491 | -66.7564 | 0.038035 | -66.7323 | 56.2427 | 56.1517 | 56.2802 | -66.8375 | -66.7565 | 0.027831 | -66.7819 | 56.1528 | 56.3122 | 56.0407 | -67.0424 | -0.086415 | -0.025629 | -0.005327 | 0.018829 | 0.10524 | -0.1166 | 0.0119 | -0.29125 | -0.11555 | -0.005443 | -0.030791 | 0.26046 | 0.043892 | -0.22762 | 122.9938 | 122.9028 | 123.0313 | 66.7891 | -123.1058 | 122.9039 | 123.0633 | 122.7918 | 66.7789 | -123.3107
267.7969 | 123.3078 | -66.7145 | 56.2866 | -0.0057996 | -0.0022116 | 0.00060681 | 0.057934 | -0.00098494 | 0.062796 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0073781 | 0.062705 | -66.761 | 0.0243 | -66.7368 | 56.2381 | 56.1563 | 56.2802 | -66.8375 | -66.7565 | 0.03241 | -66.7865 | 56.1528 | 56.3122 | 56.0086 | -67.0424 | -0.12304 | -0.048517 | -0.046526 | -0.02237 | 0.10067 | -0.13033 | -0.00641 | -0.32788 | -0.13386 | -0.042064 | -0.071991 | 0.25588 | 0.025582 | -0.27798 | 122.9526 | 122.8708 | 122.9947 | 66.7388 | -123.1241 | 122.8672 | 123.0267 | 122.7231 | 66.7469 | -123.329
268.7969 | 123.3032 | -66.7282 | 56.2958 | 0.0018314 | -0.0026388 | 0.0012478 | 0.057506 | -0.0011987 | 0.063009 | -0.0093855 | 0.00046367 | 0.00025221 | 0.061229 | 0.0073781 | 0.062705 | -66.7564 | 0.0243 | -66.7323 | 56.2473 | 56.1654 | 56.2802 | -66.8329 | -66.7611 | 0.027831 | -66.791 | 56.1573 | 56.3168 | 56.0224 | -67.0424 | -0.10473 | -0.048516 | -0.028216 | -0.00406 | 0.10067 | -0.13033 | -0.015565 | -0.31414 | -0.13844 | -0.032911 | -0.062837 | 0.25131 | 0.021006 | -0.2734 | 122.9755 | 122.8937 | 123.0084 | 66.7525 | -123.1287 | 122.8855 | 123.045 | 122.7506 | 66.756 | -123.3381
269.7969 | 123.3124 | -66.7007 | 56.2866 | 0.0094624 | -0.0028526 | 0.00082041 | 0.057934 | -0.0011987 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061443 | 0.0073781 | 0.062919 | -66.7518 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2848 | -66.8467 | -66.752 | 0.023253 | -66.7865 | 56.1528 | 56.3214 | 56.0636 | -67.0378 | -0.14593 | -0.043939 | -0.051102 | -0.040682 | 0.10524 | -0.13491 | -0.001831 | -0.33703 | -0.13386 | -0.051218 | -0.085724 | 0.25131 | 0.034739 | -0.22304 | 122.9434 | 122.8525 | 122.9855 | 66.7296 | -123.1333 | 122.8535 | 123.0221 | 122.7643 | 66.724 | -123.3244
270.7969 | 123.2941 | -66.7099 | 56.3095 | -0.0057996 | -0.0026388 | 0.00082041 | 0.057506 | -0.0011987 | 0.063223 | 0.013506 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0071645 | 0.062491 | -66.761 | 0.033457 | -66.7414 | 56.2427 | 56.1609 | 56.2894 | -66.8421 | -66.7565 | 0.03241 | -66.7773 | 56.1573 | 56.3214 | 56.0132 | -67.0378 | -0.13219 | -0.066827 | -0.051104 | -0.031527 | 0.10067 | -0.14864 | -0.02014 | -0.32787 | -0.15217 | -0.046642 | -0.067411 | 0.26046 | 0.011851 | -0.29629 | 122.9526 | 122.8708 | 122.9993 | 66.7434 | -123.1516 | 122.8672 | 123.0313 | 122.7231 | 66.7423 | -123.3473
271.7969 | 123.2071 | -66.7236 | 56.3416 | 0.017093 | -0.0026388 | 0.00060681 | 0.057293 | -0.0011987 | 0.06365 | -0.001755 | 3.6274e-05 | 3.8406e-05 | 0.061016 | 0.0078055 | 0.062705 | -66.7564 | 0.033457 | -66.746 | 56.2473 | 56.1563 | 56.2848 | -66.8375 | -66.7611 | 0.03241 | -66.7865 | 56.1528 | 56.3214 | 56.0315 | -67.0378 | -0.11388 | -0.094293 | -0.032793 | -0.022372 | 0.091509 | -0.18526 | -0.056763 | -0.31414 | -0.18879 | -0.037488 | -0.062836 | 0.25131 | -0.020193 | -0.31002 | 122.9709 | 122.8799 | 123.0084 | 66.7571 | -123.1791 | 122.8764 | 123.045 | 122.7552 | 66.756 | -123.3793
272.7969 | 123.3307 | -66.6962 | 56.2958 | 0.0018314 | -0.0028526 | 0.0012478 | 0.057506 | -0.0014123 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0073781 | 0.062705 | -66.7564 | 0.038035 | -66.7368 | 56.2381 | 56.1609 | 56.2802 | -66.8421 | -66.7565 | 0.03241 | -66.7865 | 56.1528 | 56.3122 | 56.0361 | -67.0378 | -0.14593 | -0.057672 | -0.060259 | -0.040681 | 0.10525 | -0.13491 | -0.015565 | -0.34161 | -0.14302 | -0.060375 | -0.090302 | 0.25131 | 0.016427 | -0.25967 | 122.9343 | 122.857 | 122.9764 | 66.7342 | -123.1379 | 122.8489 | 123.0084 | 122.7323 | 66.7286 | -123.3336
273.7969 | 123.2758 | -66.7145 | 56.2866 | 0.0018314 | -0.0026388 | 0.00082041 | 0.057934 | -0.00098494 | 0.063223 | 0.013506 | 3.6274e-05 | 3.8406e-05 | 0.061016 | 0.0075919 | 0.062705 | -66.761 | 0.0243 | -66.7368 | 56.2335 | 56.1471 | 56.2802 | -66.8467 | -66.7611 | 0.027831 | -66.7865 | 56.1528 | 56.3214 | 56.0224 | -67.0378 | -0.13219 | -0.053096 | -0.046526 | -0.02237 | 0.10982 | -0.13949 | -0.00641 | -0.3233 | -0.13386 | -0.046643 | -0.071991 | 0.25131 | 0.034739 | -0.26425 | 122.948 | 122.8616 | 122.9947 | 66.7388 | -123.1333 | 122.8672 | 123.0358 | 122.7369 | 66.7423 | -123.3244
274.7969 | 123.2849 | -66.7007 | 56.3095 | -0.013431 | -0.0028526 | 0.00082041 | 0.057293 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0073781 | 0.062705 | -66.7518 | 0.0243 | -66.7368 | 56.2381 | 56.1471 | 56.2848 | -66.8375 | -66.7611 | 0.027831 | -66.7773 | 56.1573 | 56.3122 | 56.0636 | -67.0378 | -0.13677 | -0.071405 | -0.051102 | -0.036103 | 0.10067 | -0.16238 | -0.024719 | -0.33703 | -0.15217 | -0.060376 | -0.076566 | 0.26046 | 0.002694 | -0.24593 | 122.9388 | 122.8479 | 122.9855 | 66.725 | -123.147 | 122.8581 | 123.0129 | 122.7643 | 66.7286 | -123.3473
275.7969 | 123.3307 | -66.7236 | 56.2866 | 0.0018314 | -0.0026388 | 0.0010342 | 0.057293 | -0.00098494 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0073781 | 0.063132 | -66.7564 | 0.028878 | -66.7323 | 56.2335 | 56.1471 | 56.2848 | -66.8329 | -66.7565 | 0.027831 | -66.7819 | 56.1482 | 56.3214 | 56.0544 | -67.0378 | -0.1093 | -0.053096 | -0.032793 | -0.008637 | 0.10067 | -0.13949 | -0.001831 | -0.31414 | -0.13844 | -0.032909 | -0.058257 | 0.25588 | 0.034739 | -0.2322 | 122.9572 | 122.8708 | 123.0084 | 66.7525 | -123.1196 | 122.8718 | 123.045 | 122.7781 | 66.7515 | -123.3244
276.7969 | 123.1888 | -66.7374 | 56.3278 | 0.0094624 | -0.0032798 | 0.0010342 | 0.057293 | -0.0011987 | 0.063223 | 0.013506 | 3.6274e-05 | 3.8406e-05 | 0.060802 | 0.0075919 | 0.062705 | -66.7564 | 0.038035 | -66.7368 | 56.2473 | 56.1654 | 56.2894 | -66.8375 | -66.7611 | 0.036989 | -66.7773 | 56.1482 | 56.3122 | 56.0819 | -67.0378 | -0.10015 | -0.08056 | -0.01906 | 0.000518 | 0.10067 | -0.16237 | -0.038451 | -0.30041 | -0.17964 | -0.023755 | -0.039945 | 0.26046 | -0.015617 | -0.24592 | 122.9846 | 122.9028 | 123.0267 | 66.7754 | -123.1653 | 122.8855 | 123.0496 | 122.8193 | 66.7744 | -123.3656
277.7969 | 123.317 | -66.6916 | 56.2912 | -0.0057996 | -0.0030662 | 0.0010342 | 0.057506 | -0.00098494 | 0.063223 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0073781 | 0.062919 | -66.761 | 0.033457 | -66.7323 | 56.2381 | 56.1517 | 56.2802 | -66.8421 | -66.752 | 0.027831 | -66.7865 | 56.1619 | 56.3168 | 56.059 | -67.0424 | -0.1505 | -0.053095 | -0.069415 | -0.040681 | 0.10982 | -0.13949 | -0.010988 | -0.35076 | -0.12928 | -0.060374 | -0.09488 | 0.25588 | 0.025583 | -0.2322 | 122.9297 | 122.8433 | 122.9718 | 66.725 | -123.1333 | 122.8535 | 123.0084 | 122.7506 | 66.7194 | -123.3336
278.7969 | 123.317 | -66.7099 | 56.3095 | -0.0057996 | -0.0030662 | 0.00082041 | 0.05772 | -0.00077134 | 0.063009 | 0.0058755 | 0.00046367 | 0.00067941 | 0.061016 | 0.0080191 | 0.062278 | -66.7473 | 0.0243 | -66.7368 | 56.2381 | 56.1609 | 56.2848 | -66.8421 | -66.7611 | 0.027831 | -66.7865 | 56.1528 | 56.3168 | 56.0544 | -67.0378 | -0.13219 | -0.071405 | -0.037369 | -0.026948 | 0.10525 | -0.14864 | -0.024719 | -0.32787 | -0.15675 | -0.051221 | -0.076569 | 0.25131 | 0.007273 | -0.25509 | 122.948 | 122.8708 | 122.9947 | 66.7342 | -123.1516 | 122.8627 | 123.0267 | 122.7643 | 66.7377 | -123.3473
279.7969 | 123.3124 | -66.7007 | 56.3004 | 0.0018314 | -0.0028526 | 0.00060681 | 0.05772 | -0.0011987 | 0.063009 | 0.013506 | 0.00025007 | 0.00067941 | 0.060588 | 0.0071645 | 0.062705 | -66.7564 | 0.028878 | -66.7368 | 56.2473 | 56.1563 | 56.2894 | -66.8375 | -66.7611 | 0.03241 | -66.7865 | 56.1528 | 56.3168 | 56.059 | -67.0332 | -0.13677 | -0.053094 | -0.055681 | -0.036103 | 0.10067 | -0.14406 | -0.010985 | -0.33245 | -0.14759 | -0.060376 | -0.085724 | 0.24673 | 0.016428 | -0.24135 | 122.948 | 122.857 | 122.9901 | 66.7296 | -123.1379 | 122.8535 | 123.0175 | 122.7597 | 66.7332 | -123.3335
280.7969 | 123.2346 | -66.6824 | 56.3049 | -0.0057996 | -0.0030662 | 0.00082041 | 0.05772 | -0.00098494 | 0.063223 | -0.001755 | -0.00017733 | 0.00046581 | 0.060802 | 0.0073781 | 0.062919 | -66.7518 | 0.0243 | -66.7323 | 56.2427 | 56.1563 | 56.2848 | -66.8421 | -66.752 | 0.027831 | -66.7773 | 56.1436 | 56.3168 | 56.0178 | -67.0378 | -0.15966 | -0.06225 | -0.069413 | -0.049836 | 0.10982 | -0.14864 | -0.020142 | -0.35534 | -0.16133 | -0.069529 | -0.094877 | 0.26046 | 0.01185 | -0.28714 | 122.9251 | 122.8387 | 122.9672 | 66.7067 | -123.147 | 122.826 | 122.9992 | 122.7002 | 66.7103 | -123.3427
281.7969 | 123.2574 | -66.7099 | 56.2775 | 0.0018314 | -0.0032798 | 0.00060681 | 0.057506 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061443 | 0.0075919 | 0.062919 | -66.7564 | 0.0243 | -66.7368 | 56.2473 | 56.1426 | 56.2756 | -66.8329 | -66.752 | 0.023253 | -66.791 | 56.1528 | 56.3214 | 56.0865 | -67.0332 | -0.12304 | -0.030206 | -0.046526 | -0.026948 | 0.096087 | -0.13491 | -0.001833 | -0.3233 | -0.12471 | -0.042063 | -0.081147 | 0.24215 | 0.043894 | -0.19099 | 122.9572 | 122.8525 | 122.9855 | 66.7342 | -123.1104 | 122.8627 | 123.0313 | 122.7964 | 66.7332 | -123.3107
282.7969 | 123.3078 | -66.6916 | 56.3004 | 0.0018314 | -0.0028526 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0073781 | 0.062705 | -66.7564 | 0.033457 | -66.7414 | 56.2381 | 56.1426 | 56.2711 | -66.8375 | -66.752 | 0.023253 | -66.7819 | 56.1619 | 56.3259 | 56.0773 | -67.0424 | -0.14593 | -0.06225 | -0.064837 | -0.049838 | 0.096087 | -0.1578 | -0.0293 | -0.35076 | -0.13844 | -0.060374 | -0.090301 | 0.26046 | 0.025585 | -0.22304 | 122.9297 | 122.8341 | 122.9626 | 66.725 | -123.1379 | 122.8535 | 123.0175 | 122.7689 | 66.7148 | -123.3427
283.7969 | 123.262 | -66.7282 | 56.3278 | 0.0094624 | -0.0030662 | 0.00082041 | 0.057506 | -0.0011987 | 0.063223 | -0.001755 | 0.00046367 | 0.00067941 | 0.060802 | 0.0075919 | 0.062919 | -66.7564 | 0.028878 | -66.7323 | 56.2427 | 56.1471 | 56.2802 | -66.8329 | -66.752 | 0.027831 | -66.7865 | 56.1573 | 56.3168 | 56.0911 | -67.0424 | -0.10473 | -0.085138 | -0.028216 | -0.00406 | 0.10067 | -0.18069 | -0.047609 | -0.31414 | -0.17048 | -0.023753 | -0.058259 | 0.25588 | -0.011038 | -0.23677 | 122.9709 | 122.8753 | 123.0084 | 66.7571 | -123.1608 | 122.8855 | 123.045 | 122.8193 | 66.756 | -123.3702
284.7969 | 123.2986 | -66.6779 | 56.2775 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057293 | -0.0011987 | 0.063223 | -0.001755 | -0.00039093 | 0.00046581 | 0.060375 | 0.0075919 | 0.062919 | -66.7564 | 0.0243 | -66.7414 | 56.2427 | 56.1563 | 56.2756 | -66.8375 | -66.7657 | 0.03241 | -66.7819 | 56.1482 | 56.3122 | 56.0819 | -67.0378 | -0.15966 | -0.034784 | -0.07857 | -0.063571 | 0.096087 | -0.12118 | -0.001833 | -0.35992 | -0.12928 | -0.087843 | -0.10403 | 0.25588 | 0.034737 | -0.19557 | 122.9205 | 122.8341 | 122.9535 | 66.7022 | -123.115 | 122.826 | 122.9901 | 122.7598 | 66.7103 | -123.3152
285.7969 | 123.2437 | -66.7282 | 56.3004 | 0.0018314 | -0.0028526 | 0.00060681 | 0.057079 | -0.0011987 | 0.063223 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060802 | 0.0073781 | 0.062705 | -66.7518 | 0.028878 | -66.7368 | 56.2381 | 56.1242 | 56.2848 | -66.8375 | -66.7611 | 0.03241 | -66.7865 | 56.1528 | 56.3214 | 56.1872 | -67.0378 | -0.1093 | -0.06225 | -0.023637 | -0.008638 | 0.10067 | -0.17612 | -0.015564 | -0.30956 | -0.14759 | -0.032911 | -0.058259 | 0.25131 | 0.021006 | -0.11315 | 122.9663 | 122.8524 | 123.013 | 66.7571 | -123.1379 | 122.881 | 123.0496 | 122.9154 | 66.7606 | -123.3381
286.7969 | 123.3215 | -66.7145 | 56.3004 | 0.0018314 | -0.0034936 | 0.00082041 | 0.057506 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061016 | 0.0075919 | 0.062705 | -66.761 | 0.033457 | -66.7368 | 56.2473 | 56.1242 | 56.2848 | -66.8284 | -66.7565 | 0.03241 | -66.7819 | 56.1528 | 56.3168 | 56.2009 | -67.0424 | -0.11388 | -0.053094 | -0.046526 | -0.02237 | 0.091508 | -0.17612 | -0.015564 | -0.32788 | -0.14759 | -0.042064 | -0.067412 | 0.26046 | 0.016428 | -0.099415 | 122.9617 | 122.8387 | 122.9993 | 66.7479 | -123.1287 | 122.8672 | 123.0313 | 122.9154 | 66.7469 | -123.3427
287.7969 | 123.262 | -66.7511 | 56.3141 | -0.0057996 | -0.0032798 | 0.00060681 | 0.057506 | -0.00077134 | 0.063437 | 0.0058755 | 0.00046367 | 3.8406e-05 | 0.061229 | 0.0075919 | 0.062705 | -66.7518 | 0.033457 | -66.7323 | 56.2427 | 56.1242 | 56.2848 | -66.8284 | -66.752 | 0.023253 | -66.7819 | 56.1573 | 56.3076 | 56.1872 | -67.0332 | -0.077257 | -0.071405 | -0.000748 | 0.018829 | 0.096086 | -0.18985 | -0.029297 | -0.2821 | -0.15675 | -0.000864 | -0.030791 | 0.25131 | -0.006463 | -0.12688 | 122.9938 | 122.8753 | 123.0359 | 66.7846 | -123.1424 | 122.9084 | 123.0587 | 122.9383 | 66.7744 | -123.3473
288.7969 | 123.2986 | -66.7236 | 56.2866 | 0.0018314 | -0.0030662 | 0.0010342 | 0.057506 | -0.0014123 | 0.063009 | -0.001755 | -0.00039093 | 0.00067941 | 0.060802 | 0.0080191 | 0.062705 | -66.7656 | 0.028878 | -66.7323 | 56.2381 | 56.1288 | 56.2756 | -66.8329 | -66.7565 | 0.027831 | -66.7865 | 56.1482 | 56.3259 | 56.1964 | -67.0378 | -0.1093 | -0.048517 | -0.04195 | -0.008637 | 0.10067 | -0.1578 | -0.010988 | -0.31414 | -0.13844 | -0.032909 | -0.062836 | 0.25131 | 0.039318 | -0.09026 | 122.9617 | 122.8524 | 122.9993 | 66.7525 | -123.1196 | 122.8718 | 123.0496 | 122.92 | 66.7515 | -123.3244
289.7969 | 123.2254 | -66.7465 | 56.282 | 0.0094624 | -0.0032798 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060588 | 0.0075919 | 0.062705 | -66.761 | 0.038035 | -66.7323 | 56.2473 | 56.1013 | 56.2802 | -66.8329 | -66.7565 | 0.03241 | -66.7819 | 56.1573 | 56.3122 | 56.146 | -67.0332 | -0.086414 | -0.034783 | -0.014483 | 0.014251 | 0.10067 | -0.1807 | -0.001832 | -0.28667 | -0.1247 | -0.010021 | -0.035369 | 0.25131 | 0.03016 | -0.13605 | 122.9938 | 122.8479 | 123.0267 | 66.7846 | -123.115 | 122.9039 | 123.0587 | 122.8925 | 66.7789 | -123.3152
290.7969 | 123.2849 | -66.7145 | 56.2866 | 0.0018314 | -0.0030662 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | -0.001755 | 0.00025007 | 0.00025221 | 0.060802 | 0.0075919 | 0.062705 | -66.7518 | 0.028878 | -66.7414 | 56.2381 | 56.1151 | 56.2711 | -66.8375 | -66.7474 | 0.027831 | -66.7819 | 56.1573 | 56.3168 | 56.2009 | -67.0424 | -0.12304 | -0.048517 | -0.037369 | -0.026949 | 0.096087 | -0.17154 | -0.015567 | -0.32788 | -0.12928 | -0.032907 | -0.067412 | 0.26046 | 0.030161 | -0.085682 | 122.9526 | 122.8296 | 122.9855 | 66.7434 | -123.1241 | 122.8718 | 123.0313 | 122.9154 | 66.7423 | -123.329
291.7969 | 123.262 | -66.7511 | 56.2775 | -0.013431 | -0.0030662 | 0.00082041 | 0.057506 | -0.00077134 | 0.063223 | -0.0093855 | 0.00025007 | 0.00067941 | 0.061016 | 0.0078055 | 0.063132 | -66.7518 | 0.033457 | -66.7414 | 56.2427 | 56.1105 | 56.2802 | -66.8421 | -66.7428 | 0.027831 | -66.7865 | 56.1528 | 56.3168 | 56.1918 | -67.0378 | -0.090994 | -0.034784 | -0.000748 | 0.009672 | 0.10067 | -0.16697 | 0.002745 | -0.28668 | -0.12471 | 0.008293 | -0.03537 | 0.25131 | 0.039316 | -0.085684 | 122.9938 | 122.8616 | 123.0313 | 66.7846 | -123.1196 | 122.9039 | 123.0679 | 122.9429 | 66.7789 | -123.3152
292.7969 | 123.2666 | -66.7007 | 56.2912 | 0.0094624 | -0.0030662 | 0.00039321 | 0.05772 | -0.00077134 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0075919 | 0.062491 | -66.761 | 0.028878 | -66.7368 | 56.2335 | 56.1334 | 56.2894 | -66.8375 | -66.752 | 0.023253 | -66.7819 | 56.1619 | 56.3214 | 56.1964 | -67.0332 | -0.13677 | -0.057674 | -0.060259 | -0.036103 | 0.10067 | -0.1578 | -0.00183 | -0.33245 | -0.12928 | -0.051218 | -0.081145 | 0.25131 | 0.030161 | -0.094838 | 122.9343 | 122.8341 | 122.9901 | 66.7296 | -123.1287 | 122.8627 | 123.0221 | 122.8971 | 66.724 | -123.3244
293.7969 | 123.3856 | -66.7053 | 56.3278 | 0.0018314 | -0.0032798 | 0.0012478 | 0.057079 | -0.00098494 | 0.063009 | -0.001755 | 0.00025007 | 0.00025221 | 0.061016 | 0.0078055 | 0.062705 | -66.7564 | 0.028878 | -66.746 | 56.2381 | 56.1197 | 56.2802 | -66.8375 | -66.7565 | 0.027831 | -66.7819 | 56.1619 | 56.3259 | 56.1918 | -67.0378 | -0.13219 | -0.089716 | -0.051104 | -0.040683 | 0.091509 | -0.20816 | -0.047609 | -0.33245 | -0.1659 | -0.05122 | -0.076568 | 0.25588 | -0.001881 | -0.13604 | 122.9434 | 122.825 | 122.9855 | 66.7342 | -123.1653 | 122.8672 | 123.0313 | 122.8971 | 66.7332 | -123.3656
294.7969 | 123.2895 | -66.7236 | 56.3049 | 0.0094624 | -0.0032798 | 0.00060681 | 0.057506 | -0.00077134 | 0.062796 | -0.0093855 | 0.00025007 | 0.00089321 | 0.060802 | 0.0075919 | 0.062705 | -66.7564 | 0.028878 | -66.7414 | 56.2335 | 56.1151 | 56.2756 | -66.8329 | -66.7474 | 0.03241 | -66.7865 | 56.1482 | 56.3214 | 56.146 | -67.0332 | -0.1093 | -0.071407 | -0.032793 | -0.017794 | 0.091508 | -0.18985 | -0.029299 | -0.30956 | -0.15675 | -0.023752 | -0.062836 | 0.24673 | 0.016428 | -0.15894 | 122.9572 | 122.8387 | 122.9993 | 66.7525 | -123.1379 | 122.8718 | 123.045 | 122.8696 | 66.756 | -123.3381
295.7969 | 123.2803 | -66.7053 | 56.2912 | -0.013431 | -0.0030662 | 0.00060681 | 0.057293 | -0.00077134 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.061229 | 0.0075919 | 0.062491 | -66.7518 | 0.028878 | -66.7323 | 56.2427 | 56.1105 | 56.2848 | -66.8421 | -66.7565 | 0.027831 | -66.7819 | 56.1528 | 56.3214 | 56.1826 | -67.0378 | -0.13677 | -0.048517 | -0.046525 | -0.026948 | 0.10982 | -0.1807 | -0.006409 | -0.33245 | -0.13844 | -0.05122 | -0.076568 | 0.25588 | 0.030161 | -0.10857 | 122.948 | 122.8158 | 122.9901 | 66.7342 | -123.1333 | 122.8581 | 123.0267 | 122.8879 | 66.7332 | -123.329
296.7969 | 123.2803 | -66.7282 | 56.3278 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | 0.013506 | 0.00025007 | 0.00046581 | 0.060802 | 0.0075919 | 0.062278 | -66.7518 | 0.038035 | -66.7323 | 56.2427 | 56.1288 | 56.2894 | -66.8375 | -66.7611 | 0.036989 | -66.7819 | 56.1482 | 56.3122 | 56.178 | -67.0332 | -0.1093 | -0.085138 | -0.023637 | -0.00406 | 0.10524 | -0.199 | -0.038451 | -0.30499 | -0.17964 | -0.032911 | -0.05368 | 0.25131 | -0.015617 | -0.14977 | 122.9709 | 122.857 | 123.0176 | 66.7662 | -123.1653 | 122.8764 | 123.0404 | 122.9063 | 66.7652 | -123.361
297.7969 | 123.2529 | -66.7419 | 56.2729 | -0.0057996 | -0.0030662 | 0.00082041 | 0.057506 | -0.0011987 | 0.063437 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.060802 | 0.0075919 | 0.062491 | -66.7518 | 0.033457 | -66.7414 | 56.2473 | 56.1105 | 56.2802 | -66.8375 | -66.7474 | 0.027831 | -66.7819 | 56.1528 | 56.3305 | 56.1368 | -67.0332 | -0.095571 | -0.025628 | -0.009904 | 0.000516 | 0.096087 | -0.16239 | 0.007323 | -0.29125 | -0.12013 | -0.005442 | -0.039947 | 0.25131 | 0.057629 | -0.13605 | 122.9892 | 122.8524 | 123.0222 | 66.7754 | -123.1104 | 122.8947 | 123.0725 | 122.8788 | 66.7698 | -123.3061
298.7969 | 123.2849 | -66.7236 | 56.2958 | -0.0057996 | -0.0030662 | 0.0010342 | 0.057293 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061016 | 0.0080191 | 0.062491 | -66.7473 | 0.028878 | -66.7323 | 56.2473 | 56.1242 | 56.2802 | -66.8375 | -66.7474 | 0.027831 | -66.7819 | 56.1573 | 56.3214 | 56.1689 | -67.0378 | -0.11388 | -0.048516 | -0.023636 | -0.008637 | 0.10524 | -0.17154 | -0.015565 | -0.31414 | -0.13844 | -0.023752 | -0.058257 | 0.25588 | 0.025584 | -0.12689 | 122.9709 | 122.8479 | 123.0038 | 66.7525 | -123.1333 | 122.881 | 123.045 | 122.8925 | 66.7515 | -123.3336
299.7969 | 123.3032 | -66.7191 | 56.2729 | -0.0057996 | -0.0028526 | 0.00082041 | 0.057506 | -0.0011987 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0078055 | 0.062491 | -66.7518 | 0.033457 | -66.7368 | 56.2381 | 56.1105 | 56.2756 | -66.8329 | -66.752 | 0.03241 | -66.7773 | 56.1573 | 56.3259 | 56.1964 | -67.0378 | -0.11388 | -0.034784 | -0.032792 | -0.017793 | 0.096087 | -0.16239 | 0.002745 | -0.31872 | -0.11555 | -0.032908 | -0.058256 | 0.26046 | 0.053051 | -0.076527 | 122.9572 | 122.8296 | 122.9947 | 66.7525 | -123.1058 | 122.8764 | 123.045 | 122.9154 | 66.7515 | -123.3107
300.7969 | 123.2712 | -66.7419 | 56.2912 | 0.0018314 | -0.0032798 | 0.00060681 | 0.057293 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0075919 | 0.062705 | -66.7564 | 0.028878 | -66.7368 | 56.2381 | 56.1059 | 56.2756 | -66.8284 | -66.752 | 0.036989 | -66.7865 | 56.1482 | 56.3168 | 56.1964 | -67.0424 | -0.086413 | -0.053095 | -0.014483 | 0.005095 | 0.091508 | -0.18528 | -0.015566 | -0.30041 | -0.14302 | -0.01002 | -0.044526 | 0.25588 | 0.025583 | -0.094838 | 122.98 | 122.8479 | 123.0176 | 66.7708 | -123.1196 | 122.8901 | 123.0587 | 122.9383 | 66.7789 | -123.3336
301.7969 | 123.2941 | -66.7099 | 56.282 | -0.0057996 | -0.0034936 | 0.00039321 | 0.057506 | -0.00077134 | 0.063009 | -0.001755 | 0.00025007 | 0.00025221 | 0.060802 | 0.0078055 | 0.062705 | -66.7518 | 0.028878 | -66.7368 | 56.2381 | 56.1151 | 56.2711 | -66.8329 | -66.7565 | 0.03241 | -66.7773 | 56.1573 | 56.3214 | 56.1368 | -67.0332 | -0.12304 | -0.043939 | -0.041947 | -0.026948 | 0.096087 | -0.16696 | -0.010989 | -0.3233 | -0.1247 | -0.046642 | -0.067411 | 0.25588 | 0.039317 | -0.1452 | 122.948 | 122.825 | 122.981 | 66.7388 | -123.115 | 122.8672 | 123.0313 | 122.8467 | 66.7423 | -123.3152
302.7969 | 123.2529 | -66.7236 | 56.2866 | 0.0018314 | -0.0034936 | 0.0010342 | 0.057506 | -0.00098494 | 0.063437 | -0.017016 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0073781 | 0.062919 | -66.7564 | 0.0243 | -66.7368 | 56.2381 | 56.1197 | 56.2756 | -66.8329 | -66.752 | 0.027831 | -66.7819 | 56.1482 | 56.3259 | 56.178 | -67.0469 | -0.1093 | -0.048517 | -0.032793 | -0.013215 | 0.096087 | -0.16696 | -0.010988 | -0.3233 | -0.13844 | -0.02833 | -0.058257 | 0.26504 | 0.039318 | -0.10857 | 122.9617 | 122.8433 | 122.9993 | 66.7479 | -123.1196 | 122.8718 | 123.0496 | 122.9017 | 66.7515 | -123.3336
303.7969 | 123.2941 | -66.7145 | 56.25 | 0.0018314 | -0.0030662 | 0.0010342 | 0.057079 | -0.00098494 | 0.062796 | -0.001755 | 0.00025007 | 0.00046581 | 0.060588 | 0.0075919 | 0.062705 | -66.7473 | 0.028878 | -66.7368 | 56.2335 | 56.1197 | 56.2802 | -66.8329 | -66.7428 | 0.036989 | -66.7865 | 56.1482 | 56.3259 | 56.146 | -67.0378 | -0.11846 | -0.016475 | -0.032791 | -0.02237 | 0.096087 | -0.13034 | 0.030211 | -0.3233 | -0.10182 | -0.028328 | -0.071991 | 0.25131 | 0.075939 | -0.104 | 122.948 | 122.8341 | 122.9947 | 66.7434 | -123.0829 | 122.8627 | 123.0404 | 122.8605 | 66.7515 | -123.2878
304.7969 | 123.262 | -66.7236 | 56.3004 | 0.0018314 | -0.0030662 | 0.00082041 | 0.057506 | -0.0014123 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.061016 | 0.0078055 | 0.062491 | -66.7473 | 0.0243 | -66.7277 | 56.2427 | 56.1151 | 56.2756 | -66.8284 | -66.752 | 0.03241 | -66.7773 | 56.1436 | 56.3214 | 56.1597 | -67.0378 | -0.10472 | -0.057672 | -0.023636 | -0.004059 | 0.10066 | -0.18527 | -0.024721 | -0.31414 | -0.15675 | -0.02833 | -0.053678 | 0.26046 | 0.021006 | -0.14062 | 122.9663 | 122.8387 | 122.9993 | 66.7479 | -123.1287 | 122.8672 | 123.045 | 122.8834 | 66.756 | -123.3381
305.7969 | 123.2849 | -66.7236 | 56.2729 | -0.0057996 | -0.0032798 | 0.00082041 | 0.057079 | -0.00098494 | 0.063223 | 0.0058755 | 0.00025007 | 0.00025221 | 0.060802 | 0.0078055 | 0.062278 | -66.7564 | 0.033457 | -66.7277 | 56.2381 | 56.1242 | 56.2756 | -66.8329 | -66.7565 | 0.027831 | -66.7865 | 56.139 | 56.3214 | 56.1964 | -67.0378 | -0.1093 | -0.034784 | -0.032793 | -0.004059 | 0.10524 | -0.14865 | 0.002745 | -0.31414 | -0.13386 | -0.032909 | -0.062836 | 0.25131 | 0.048472 | -0.076527 | 122.9617 | 122.8479 | 122.9993 | 66.7571 | -123.1058 | 122.8627 | 123.045 | 122.92 | 66.7515 | -123.3107
306.7969 | 123.2483 | -66.7282 | 56.2958 | -0.013431 | -0.0030662 | 0.00039321 | 0.057079 | -0.0014123 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0078055 | 0.062705 | -66.7427 | 0.033457 | -66.7414 | 56.2381 | 56.1105 | 56.2848 | -66.8375 | -66.7474 | 0.03241 | -66.7865 | 56.1528 | 56.3168 | 56.1918 | -67.0378 | -0.1093 | -0.057672 | -0.014481 | -0.013217 | 0.096087 | -0.18528 | -0.010986 | -0.30956 | -0.14302 | -0.019175 | -0.058259 | 0.25131 | 0.021006 | -0.10399 | 122.9663 | 122.8387 | 123.013 | 66.7617 | -123.1333 | 122.881 | 123.045 | 122.92 | 66.7606 | -123.3336
307.7969 | 123.2941 | -66.7099 | 56.2637 | -0.0057996 | -0.0030662 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060588 | 0.0075919 | 0.062705 | -66.7564 | 0.038035 | -66.7368 | 56.2381 | 56.1059 | 56.2756 | -66.8329 | -66.7474 | 0.03241 | -66.7819 | 56.1436 | 56.3122 | 56.1918 | -67.0378 | -0.12304 | -0.025629 | -0.046526 | -0.026948 | 0.096087 | -0.15781 | 0.0119 | -0.32787 | -0.12013 | -0.037485 | -0.07199 | 0.25588 | 0.04847 | -0.071951 | 122.948 | 122.8158 | 122.9855 | 66.7479 | -123.0967 | 122.8535 | 123.0221 | 122.9017 | 66.7423 | -123.3015
308.7969 | 123.262 | -66.7282 | 56.2637 | 0.0094624 | -0.0028526 | 0.00060681 | 0.057293 | -0.0011987 | 0.062796 | -0.0093855 | 0.00067727 | 0.00025221 | 0.061016 | 0.0075919 | 0.062705 | -66.7564 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2802 | -66.8375 | -66.7474 | 0.027831 | -66.7819 | 56.1573 | 56.3122 | 56.1552 | -67.0378 | -0.1093 | -0.025629 | -0.028216 | -0.008638 | 0.10067 | -0.15323 | 0.016478 | -0.30956 | -0.10639 | -0.019175 | -0.05368 | 0.25588 | 0.04847 | -0.10858 | 122.9663 | 122.8387 | 123.0084 | 66.7571 | -123.1012 | 122.8855 | 123.0404 | 122.8834 | 66.756 | -123.3015
309.7969 | 123.2529 | -66.7328 | 56.3141 | 0.0018314 | -0.0028526 | 0.00060681 | 0.057293 | -0.0011987 | 0.063009 | 0.013506 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.0080191 | 0.062278 | -66.7518 | 0.028878 | -66.7277 | 56.2381 | 56.1105 | 56.2848 | -66.8375 | -66.752 | 0.027831 | -66.7773 | 56.1482 | 56.3122 | 56.0407 | -67.0469 | -0.10473 | -0.075983 | -0.019059 | 0.005096 | 0.10982 | -0.20359 | -0.029297 | -0.31414 | -0.16591 | -0.019175 | -0.044523 | 0.26962 | -0.001884 | -0.2734 | 122.9709 | 122.8433 | 123.0176 | 66.7617 | -123.1516 | 122.881 | 123.045 | 122.7735 | 66.7606 | -123.361
310.7969 | 123.2712 | -66.7328 | 56.2912 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.061016 | 0.0078055 | 0.062278 | -66.7564 | 0.0243 | -66.7277 | 56.2381 | 56.1197 | 56.2802 | -66.8192 | -66.7428 | 0.036989 | -66.7819 | 56.1528 | 56.3122 | 56.0407 | -67.0378 | -0.08641 | -0.053095 | -0.023638 | 0.005096 | 0.091506 | -0.17154 | -0.010988 | -0.30499 | -0.13844 | -0.010018 | -0.049102 | 0.25588 | 0.021004 | -0.25051 | 122.9709 | 122.8524 | 123.013 | 66.7571 | -123.1104 | 122.8855 | 123.045 | 122.7735 | 66.7698 | -123.329
311.7969 | 123.2437 | -66.7328 | 56.2408 | -0.013431 | -0.0034936 | 0.00082041 | 0.057506 | -0.0011987 | 0.063009 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0080191 | 0.062491 | -66.7473 | 0.033457 | -66.7323 | 56.2473 | 56.1105 | 56.2894 | -66.7688 | -66.7565 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.0361 | -67.0424 | -0.036042 | 0.006415 | -0.014481 | 0.000518 | 0.03656 | -0.13034 | 0.048524 | -0.30957 | -0.092663 | -0.023754 | -0.039944 | 0.26962 | 0.080515 | -0.20473 | 122.98 | 122.8433 | 123.0222 | 66.7662 | -123.0097 | 122.881 | 123.0541 | 122.7689 | 66.7606 | -123.2832
312.7969 | 123.2758 | -66.7328 | 56.2729 | -0.0057996 | -0.0032798 | 0.00060681 | 0.057506 | -0.00077134 | 0.063009 | -0.001755 | -0.00017733 | 0.00046581 | 0.060802 | 0.0075919 | 0.062491 | -66.7518 | 0.033457 | -66.7368 | 56.2381 | 56.1105 | 56.2756 | -66.7185 | -66.752 | 0.03241 | -66.7773 | 56.1482 | 56.3122 | 56.0178 | -67.0378 | 0.014326 | -0.034784 | -0.019059 | -0.00406 | -0.018386 | -0.16239 | 0.002745 | -0.30499 | -0.12471 | -0.019175 | -0.044523 | 0.26046 | 0.039315 | -0.25509 | 122.9709 | 122.8433 | 123.0084 | 66.7662 | -122.9914 | 122.881 | 123.045 | 122.7506 | 66.7652 | -123.3107
313.7969 | 123.2895 | -66.7191 | 56.2775 | 0.0094624 | -0.0032798 | 0.00082041 | 0.057293 | -0.00098494 | 0.063009 | -0.0093855 | 0.00025007 | 0.00046581 | 0.060588 | 0.0082329 | 0.062491 | -66.7518 | 0.038035 | -66.7368 | 56.2381 | 56.1105 | 56.2802 | -66.6864 | -66.752 | 0.03241 | -66.7773 | 56.1665 | 56.3122 | 56.0453 | -67.0469 | 0.032646 | -0.039362 | -0.032792 | -0.017793 | -0.050439 | -0.16697 | 0.002745 | -0.32788 | -0.11097 | -0.032908 | -0.058256 | 0.26962 | 0.034737 | -0.2322 | 122.9572 | 122.8296 | 122.9993 | 66.7571 | -122.9639 | 122.8856 | 123.0313 | 122.7643 | 66.7515 | -123.3244
314.8594 | 123.1705 | -66.7465 | 56.3049 | 0.0018314 | -0.0032798 | 0.00060681 | 0.057293 | -0.0014123 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060802 | 0.0075919 | 0.062491 | -66.7473 | 0.038035 | -66.7323 | 56.2473 | 56.1105 | 56.2802 | -66.7185 | -66.7428 | 0.03241 | -66.7819 | 56.1528 | 56.3214 | 56.0498 | -67.0424 | 0.028059 | -0.057672 | -0.000748 | 0.014251 | -0.013808 | -0.19443 | -0.024721 | -0.29583 | -0.15217 | 0.003715 | -0.035369 | 0.26046 | 0.016428 | -0.25509 | 122.9938 | 122.857 | 123.0267 | 66.7846 | -123.0234 | 122.8993 | 123.0679 | 122.7964 | 66.7789 | -123.3473
315.7969 | 123.2391 | -66.7557 | 56.2729 | 0.0018314 | -0.0034936 | 0.00082041 | 0.057293 | -0.00098494 | 0.063223 | 0.013506 | -0.00017733 | 0.00046581 | 0.061229 | 0.0080191 | 0.062491 | -66.7564 | 0.038035 | -66.7368 | 56.2427 | 56.1013 | 56.2802 | -66.723 | -66.7474 | 0.027831 | -66.7773 | 56.1482 | 56.3122 | 56.0453 | -67.0378 | 0.032635 | -0.030206 | -0.00075 | 0.018828 | -0.013807 | -0.17155 | 0.007323 | -0.2821 | -0.12471 | 0.008291 | -0.021635 | 0.26046 | 0.039315 | -0.22762 | 122.9984 | 122.857 | 123.0359 | 66.7937 | -122.9959 | 122.9039 | 123.0679 | 122.8009 | 66.7835 | -123.3107
316.7969 | 123.2895 | -66.7191 | 56.2592 | -0.013431 | -0.0030662 | 0.00082041 | 0.057506 | -0.00077134 | 0.063009 | -0.017016 | -0.00017733 | 0.00025221 | 0.060802 | 0.0078055 | 0.062705 | -66.7518 | 0.028878 | -66.7323 | 56.2427 | 56.1105 | 56.2848 | -66.7139 | -66.752 | 0.03241 | -66.7819 | 56.1482 | 56.3168 | 56.0544 | -67.0378 | 0.005172 | -0.016473 | -0.032792 | -0.013215 | -0.018387 | -0.14865 | 0.025635 | -0.31872 | -0.11097 | -0.032908 | -0.062835 | 0.25588 | 0.057627 | -0.20473 | 122.9617 | 122.8296 | 123.0038 | 66.7479 | -122.973 | 122.8672 | 123.0358 | 122.7735 | 66.7515 | -123.2969
317.7969 | 123.4177 | -66.7374 | 56.2729 | -0.013431 | -0.0028526 | 0.00060681 | 0.057506 | -0.0011987 | 0.063009 | -0.001755 | 0.00046367 | 0.00067941 | 0.060802 | 0.0078055 | 0.062705 | -66.7427 | 0.038035 | -66.7277 | 56.2427 | 56.1013 | 56.2848 | -66.7368 | -66.7428 | 0.03241 | -66.7865 | 56.1482 | 56.3214 | 56.0544 | -67.0378 | 0.000588 | -0.030206 | -0.005325 | 0.009674 | 0.009086 | -0.17155 | 0.011902 | -0.30041 | -0.12471 | -0.00544 | -0.049103 | 0.25131 | 0.048472 | -0.21846 | 122.98 | 122.8387 | 123.0222 | 66.7754 | -123.0097 | 122.8855 | 123.0587 | 122.7918 | 66.7698 | -123.3107
318.7969 | 123.2574 | -66.7236 | 56.2592 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057293 | -0.00098494 | 0.063009 | -0.017016 | -0.00017733 | 0.00046581 | 0.060802 | 0.0078055 | 0.062491 | -66.7518 | 0.033457 | -66.7323 | 56.2427 | 56.1288 | 56.2848 | -66.8329 | -66.7565 | 0.03241 | -66.7773 | 56.1528 | 56.3168 | 56.1552 | -67.0378 | -0.1093 | -0.016473 | -0.028214 | -0.008637 | 0.10067 | -0.13034 | 0.025635 | -0.31414 | -0.10639 | -0.032909 | -0.053678 | 0.26046 | 0.057627 | -0.104 | 122.9663 | 122.8524 | 123.0084 | 66.7571 | -123.0921 | 122.8764 | 123.0404 | 122.8788 | 66.756 | -123.2969
319.7969 | 123.2803 | -66.7145 | 56.282 | -0.013431 | -0.0032798 | 0.0012478 | 0.057079 | -0.0014123 | 0.063223 | -0.017016 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0078055 | 0.062491 | -66.7518 | 0.033457 | -66.7368 | 56.2381 | 56.1197 | 56.2894 | -66.8375 | -66.7474 | 0.03241 | -66.7819 | 56.1573 | 56.3122 | 56.1277 | -67.0424 | -0.12304 | -0.043939 | -0.037369 | -0.02237 | 0.10067 | -0.16239 | 0.007326 | -0.32788 | -0.1247 | -0.032907 | -0.067412 | 0.26046 | 0.03016 | -0.15436 | 122.9526 | 122.8341 | 123.0038 | 66.7479 | -123.1196 | 122.8718 | 123.0267 | 122.8422 | 66.7469 | -123.3244
320.7969 | 123.2941 | -66.7328 | 56.2637 | -0.0057996 | -0.0032798 | 0.00082041 | 0.057506 | -0.00098494 | 0.063223 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060802 | 0.0075919 | 0.062491 | -66.7518 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2802 | -66.8329 | -66.752 | 0.027831 | -66.7773 | 56.1573 | 56.3214 | 56.146 | -67.0424 | -0.10015 | -0.025629 | -0.019059 | -0.00406 | 0.096087 | -0.15323 | 0.016478 | -0.30957 | -0.10639 | -0.019175 | -0.044523 | 0.26504 | 0.057627 | -0.11774 | 122.9709 | 122.8433 | 123.013 | 66.7617 | -123.0967 | 122.8901 | 123.0541 | 122.8788 | 66.7606 | -123.3061
321.7969 | 123.2941 | -66.7191 | 56.2958 | -0.013431 | -0.0034936 | 0.0010342 | 0.057293 | -0.00098494 | 0.063437 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060588 | 0.0078055 | 0.062278 | -66.7564 | 0.033457 | -66.7323 | 56.2473 | 56.1151 | 56.2894 | -66.8421 | -66.7474 | 0.027831 | -66.7865 | 56.1573 | 56.3214 | 56.1597 | -67.0378 | -0.12304 | -0.048516 | -0.037371 | -0.013215 | 0.10982 | -0.1807 | -0.006407 | -0.31872 | -0.13844 | -0.02833 | -0.067414 | 0.25131 | 0.025584 | -0.13604 | 122.9663 | 122.8341 | 123.0084 | 66.7525 | -123.1379 | 122.8764 | 123.0404 | 122.8788 | 66.7469 | -123.3336
322.7969 | 123.3124 | -66.7053 | 56.2866 | -0.0057996 | -0.0030662 | 0.0010342 | 0.057079 | -0.0011987 | 0.063009 | -0.0093855 | 0.00046367 | 0.00046581 | 0.060375 | 0.0082329 | 0.062705 | -66.7427 | 0.028878 | -66.7277 | 56.2381 | 56.1105 | 56.2848 | -66.8421 | -66.7611 | 0.036989 | -66.7819 | 56.1573 | 56.3214 | 56.1918 | -67.0378 | -0.13677 | -0.048517 | -0.037369 | -0.02237 | 0.1144 | -0.17612 | -0.001831 | -0.33245 | -0.12928 | -0.055799 | -0.076568 | 0.25588 | 0.034739 | -0.094839 | 122.9434 | 122.8158 | 122.9901 | 66.7342 | -123.1287 | 122.8627 | 123.0267 | 122.8971 | 66.7423 | -123.3244
323.7969 | 123.2758 | -66.7145 | 56.2408 | 0.0018314 | -0.0032798 | 0.00082041 | 0.056865 | -0.0011987 | 0.063223 | -0.001755 | 0.00025007 | 0.00046581 | 0.061016 | 0.0078055 | 0.062491 | -66.7427 | 0.028878 | -66.7368 | 56.2381 | 56.1151 | 56.2756 | -66.8329 | -66.752 | 0.027831 | -66.7819 | 56.1528 | 56.3168 | 56.1872 | -67.0378 | -0.11846 | -0.002741 | -0.028213 | -0.02237 | 0.096087 | -0.12577 | 0.034788 | -0.3233 | -0.088085 | -0.037485 | -0.067412 | 0.25588 | 0.075937 | -0.053641 | 122.9526 | 122.8296 | 122.9901 | 66.7434 | -123.0738 | 122.8672 | 123.0313 | 122.9017 | 66.7423 | -123.2786
324.7969 | 123.2346 | -66.7053 | 56.2775 | -0.0057996 | -0.0032798 | 0.00060681 | 0.057506 | -0.00098494 | 0.062796 | 0.0058755 | -0.00017733 | 0.00025221 | 0.060588 | 0.0080191 | 0.062491 | -66.7518 | 0.019721 | -66.7368 | 56.2427 | 56.1242 | 56.2848 | -66.8329 | -66.7565 | 0.027831 | -66.7819 | 56.1573 | 56.3214 | 56.178 | -67.0469 | -0.12761 | -0.034784 | -0.046525 | -0.031526 | 0.096087 | -0.15323 | 0.007324 | -0.34161 | -0.12013 | -0.05122 | -0.076568 | 0.26504 | 0.043894 | -0.09942 | 122.948 | 122.8296 | 122.9901 | 66.725 | -123.1104 | 122.8627 | 123.0267 | 122.8834 | 66.7332 | -123.3244
325.7969 | 123.2849 | -66.7328 | 56.3004 | -0.0057996 | -0.0030662 | 0.00082041 | 0.057293 | -0.0014123 | 0.062796 | -0.001755 | -0.00017733 | 0.00046581 | 0.060588 | 0.0082329 | 0.062491 | -66.7518 | 0.038035 | -66.7277 | 56.2381 | 56.1151 | 56.2802 | -66.8375 | -66.7565 | 0.027831 | -66.7773 | 56.1528 | 56.3259 | 56.178 | -67.0469 | -0.10473 | -0.06225 | -0.019059 | 0.005096 | 0.10982 | -0.18527 | -0.020143 | -0.31414 | -0.14759 | -0.023754 | -0.044523 | 0.26962 | 0.025585 | -0.12231 | 122.9709 | 122.8479 | 123.013 | 66.7708 | -123.1379 | 122.8855 | 123.0587 | 122.9108 | 66.7606 | -123.3473
326.7969 | 123.2483 | -66.7236 | 56.2408 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057293 | -0.0014123 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061229 | 0.0080191 | 0.062278 | -66.7473 | 0.028878 | -66.7323 | 56.2473 | 56.1151 | 56.2802 | -66.8329 | -66.752 | 0.023253 | -66.7773 | 56.1482 | 56.3214 | 56.1872 | -67.0332 | -0.1093 | 0.006415 | -0.023636 | -0.008637 | 0.10067 | -0.12577 | 0.039366 | -0.30956 | -0.092663 | -0.02833 | -0.053678 | 0.25588 | 0.080515 | -0.053641 | 122.9709 | 122.8387 | 123.0038 | 66.7525 | -123.0738 | 122.8718 | 123.045 | 122.9108 | 66.7469 | -123.274
327.7969 | 123.3078 | -66.7191 | 56.2637 | -0.0057996 | -0.0034936 | 0.0012478 | 0.057293 | -0.0011987 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0078055 | 0.062491 | -66.7518 | 0.028878 | -66.7368 | 56.2518 | 56.1105 | 56.2802 | -66.8375 | -66.7474 | 0.023253 | -66.7773 | 56.1528 | 56.3259 | 56.1964 | -67.0515 | -0.11846 | -0.011894 | -0.032792 | -0.017793 | 0.10067 | -0.15323 | 0.016478 | -0.33245 | -0.11097 | -0.02833 | -0.058256 | 0.2742 | 0.062206 | -0.067372 | 122.9709 | 122.8296 | 122.9993 | 66.7479 | -123.1012 | 122.8718 | 123.045 | 122.9154 | 66.7423 | -123.3152
328.7969 | 123.2712 | -66.7145 | 56.2729 | 0.0018314 | -0.0034936 | 0.0012478 | 0.057079 | -0.00098494 | 0.062796 | 0.013506 | -0.00017733 | 0.00046581 | 0.060588 | 0.0082329 | 0.062278 | -66.7564 | 0.019721 | -66.7323 | 56.2427 | 56.1105 | 56.2848 | -66.8375 | -66.7474 | 0.036989 | -66.7865 | 56.1482 | 56.3214 | 56.2009 | -67.0378 | -0.12304 | -0.030206 | -0.041948 | -0.017792 | 0.10524 | -0.16239 | 0.011902 | -0.3233 | -0.12471 | -0.032907 | -0.071991 | 0.25131 | 0.048472 | -0.071949 | 122.9572 | 122.825 | 122.9993 | 66.7342 | -123.1104 | 122.8627 | 123.0358 | 122.9154 | 66.7515 | -123.3107
329.7969 | 123.1888 | -66.7465 | 56.2912 | -0.0057996 | -0.0032798 | 0.0010342 | 0.057293 | -0.0014123 | 0.063223 | -0.001755 | -0.00039093 | 0.00067941 | 0.060802 | 0.0075919 | 0.062278 | -66.7564 | 0.028878 | -66.7323 | 56.2381 | 56.1151 | 56.2756 | -66.8329 | -66.7474 | 0.03241 | -66.7865 | 56.1573 | 56.3214 | 56.1964 | -67.0424 | -0.086414 | -0.053095 | -0.009905 | 0.014251 | 0.10067 | -0.17612 | -0.015566 | -0.29583 | -0.13386 | -0.000864 | -0.039948 | 0.25588 | 0.030161 | -0.094838 | 122.9846 | 122.8616 | 123.0222 | 66.7754 | -123.1241 | 122.9039 | 123.0679 | 122.9429 | 66.7789 | -123.3336
330.7969 | 123.2895 | -66.7374 | 56.282 | 0.0018314 | -0.0034936 | 0.0010342 | 0.057293 | -0.0014123 | 0.063223 | 0.013506 | 0.00025007 | 0.00067941 | 0.061016 | 0.0078055 | 0.062491 | -66.7427 | 0.033457 | -66.7368 | 56.2427 | 56.1105 | 56.2756 | -66.8375 | -66.752 | 0.03241 | -66.7819 | 56.1573 | 56.3122 | 56.178 | -67.0378 | -0.10015 | -0.039361 | -0.005325 | 0.000518 | 0.10067 | -0.17154 | -0.00641 | -0.30041 | -0.1247 | -0.014597 | -0.044524 | 0.25588 | 0.03016 | -0.104 | 122.98 | 122.8479 | 123.013 | 66.7708 | -123.1196 | 122.8947 | 123.0496 | 122.9154 | 66.7698 | -123.3198
331.7969 | 123.2849 | -66.7236 | 56.2592 | -0.0057996 | -0.0037072 | 0.0010342 | 0.057293 | -0.0014123 | 0.063223 | -0.017016 | 0.00025007 | 0.00046581 | 0.060802 | 0.0082329 | 0.062491 | -66.7473 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2756 | -66.8329 | -66.752 | 0.03241 | -66.7819 | 56.1528 | 56.3168 | 56.2009 | -67.0424 | -0.1093 | -0.021051 | -0.023636 | -0.013215 | 0.096087 | -0.14865 | 0.016478 | -0.31872 | -0.10639 | -0.02833 | -0.058257 | 0.26046 | 0.057627 | -0.058216 | 122.9617 | 122.8341 | 122.9993 | 66.7525 | -123.0921 | 122.8764 | 123.0404 | 122.9246 | 66.756 | -123.3015
332.7969 | 123.2758 | -66.7191 | 56.282 | 0.0018314 | -0.0032798 | 0.00082041 | 0.057293 | -0.0014123 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.060802 | 0.0082329 | 0.062278 | -66.7518 | 0.033457 | -66.7368 | 56.2381 | 56.1059 | 56.2848 | -66.8329 | -66.752 | 0.03241 | -66.7819 | 56.1528 | 56.3259 | 56.1689 | -67.0469 | -0.11388 | -0.043939 | -0.032792 | -0.017793 | 0.096087 | -0.17612 | 0.002747 | -0.32788 | -0.12928 | -0.032908 | -0.062835 | 0.26504 | 0.043896 | -0.11315 | 122.9572 | 122.825 | 123.0038 | 66.7525 | -123.115 | 122.8718 | 123.045 | 122.8879 | 66.7515 | -123.329
333.7969 | 123.2346 | -66.7328 | 56.3095 | -0.0057996 | -0.0037072 | 0.00082041 | 0.057079 | -0.0011987 | 0.063223 | -0.0093855 | 0.00025007 | 0.00067941 | 0.060161 | 0.0082329 | 0.062705 | -66.7427 | 0.038035 | -66.7368 | 56.2473 | 56.1013 | 56.2894 | -66.8284 | -66.7474 | 0.036989 | -66.7819 | 56.1528 | 56.3214 | 56.1918 | -67.0424 | -0.095568 | -0.062249 | -0.009903 | -0.00406 | 0.091508 | -0.20817 | -0.02014 | -0.30957 | -0.15675 | -0.014597 | -0.049102 | 0.26046 | 0.011851 | -0.11773 | 122.98 | 122.8341 | 123.0222 | 66.7708 | -123.1379 | 122.8855 | 123.0541 | 122.9246 | 66.7698 | -123.3519
334.7969 | 123.2437 | -66.7053 | 56.2775 | 0.0018314 | -0.0034936 | 0.0010342 | 0.057079 | -0.00098494 | 0.063437 | -0.001755 | -0.00017733 | 0.00046581 | 0.060802 | 0.0082329 | 0.062491 | -66.7473 | 0.033457 | -66.7323 | 56.2381 | 56.1197 | 56.2802 | -66.8329 | -66.7428 | 0.023253 | -66.7773 | 56.1436 | 56.3214 | 56.1918 | -67.0378 | -0.12761 | -0.039362 | -0.041947 | -0.026948 | 0.10067 | -0.15781 | 0.002745 | -0.33245 | -0.13386 | -0.037484 | -0.071989 | 0.26046 | 0.043894 | -0.085684 | 122.9434 | 122.825 | 122.9855 | 66.7388 | -123.1104 | 122.8489 | 123.0267 | 122.8971 | 66.7286 | -123.3152
335.7969 | 123.2941 | -66.7007 | 56.282 | 0.0018314 | -0.0034936 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.001755 | -0.00017733 | 0.00067941 | 0.060802 | 0.0084465 | 0.062705 | -66.7427 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2802 | -66.8329 | -66.7565 | 0.027831 | -66.7819 | 56.1528 | 56.3168 | 56.1964 | -67.0424 | -0.13219 | -0.043939 | -0.041946 | -0.036103 | 0.096087 | -0.17154 | -0.001832 | -0.34161 | -0.12928 | -0.055797 | -0.081145 | 0.26046 | 0.034739 | -0.085682 | 122.9388 | 122.8112 | 122.981 | 66.7296 | -123.115 | 122.8535 | 123.0175 | 122.8971 | 66.7286 | -123.3244
336.7969 | 123.2941 | -66.7099 | 56.2546 | -0.0057996 | -0.0034936 | 0.00082041 | 0.057293 | -0.00098494 | 0.063009 | -0.001755 | 0.00025007 | 0.00067941 | 0.060802 | 0.0080191 | 0.062491 | -66.7518 | 0.028878 | -66.7368 | 56.2381 | 56.1105 | 56.2802 | -66.8238 | -66.7474 | 0.03241 | -66.7819 | 56.1573 | 56.3214 | 56.1597 | -67.0469 | -0.11388 | -0.016474 | -0.041947 | -0.026948 | 0.086929 | -0.14408 | 0.025633 | -0.33703 | -0.097239 | -0.037485 | -0.07199 | 0.26504 | 0.066782 | -0.094846 | 122.948 | 122.8204 | 122.9901 | 66.7388 | -123.0784 | 122.8672 | 123.0313 | 122.8696 | 66.7423 | -123.3015
337.7969 | 123.2574 | -66.7099 | 56.2866 | -0.0057996 | -0.0034936 | 0.00082041 | 0.057506 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0078055 | 0.062705 | -66.7564 | 0.038035 | -66.7323 | 56.2427 | 56.1105 | 56.2802 | -66.8375 | -66.7565 | 0.036989 | -66.7865 | 56.1528 | 56.3122 | 56.1826 | -67.0378 | -0.12761 | -0.043939 | -0.046526 | -0.02237 | 0.10524 | -0.17612 | -0.00641 | -0.32787 | -0.13386 | -0.046642 | -0.076569 | 0.25131 | 0.025582 | -0.104 | 122.9526 | 122.8204 | 122.9901 | 66.7479 | -123.1241 | 122.8627 | 123.0221 | 122.8925 | 66.7469 | -123.3244
338.7969 | 123.2849 | -66.7191 | 56.2546 | 0.0094624 | -0.0032798 | 0.00082041 | 0.057506 | -0.0014123 | 0.063009 | -0.001755 | -0.00017733 | 0.00025221 | 0.060802 | 0.0082329 | 0.062278 | -66.7473 | 0.033457 | -66.7414 | 56.2335 | 56.1105 | 56.2848 | -66.8375 | -66.7474 | 0.027831 | -66.7773 | 56.1482 | 56.3168 | 56.1277 | -67.0378 | -0.11846 | -0.021053 | -0.028214 | -0.022372 | 0.096087 | -0.14408 | 0.030212 | -0.31872 | -0.1064 | -0.02833 | -0.058256 | 0.26046 | 0.062204 | -0.1269 | 122.9526 | 122.8296 | 123.0038 | 66.7525 | -123.0921 | 122.8672 | 123.0358 | 122.8467 | 66.7469 | -123.2924
339.7969 | 123.23 | -66.7419 | 56.3232 | 0.0018314 | -0.0034936 | 0.00060681 | 0.057293 | -0.0014123 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0084465 | 0.062278 | -66.7427 | 0.033457 | -66.7368 | 56.2381 | 56.1151 | 56.2939 | -66.8329 | -66.752 | 0.027831 | -66.7773 | 56.1573 | 56.3122 | 56.1368 | -67.0469 | -0.090992 | -0.085138 | -0.000748 | 0.005095 | 0.096087 | -0.20816 | -0.029295 | -0.30499 | -0.1659 | -0.01002 | -0.035368 | 0.26962 | -0.011039 | -0.1864 | 122.98 | 122.857 | 123.0359 | 66.7754 | -123.1562 | 122.8993 | 123.0541 | 122.8788 | 66.7698 | -123.3702
340.7969 | 123.2666 | -66.6962 | 56.2683 | 0.0018314 | -0.0034936 | 0.00082041 | 0.057293 | -0.00098494 | 0.063223 | 0.0058755 | 0.00025007 | 0.00089321 | 0.060588 | 0.0084465 | 0.062278 | -66.7518 | 0.033457 | -66.7323 | 56.2381 | 56.1105 | 56.2848 | -66.8284 | -66.7474 | 0.027831 | -66.7819 | 56.1528 | 56.3168 | 56.1735 | -67.0378 | -0.13219 | -0.030207 | -0.05568 | -0.036103 | 0.096086 | -0.15781 | 0.016479 | -0.34161 | -0.11555 | -0.051218 | -0.085723 | 0.25588 | 0.048471 | -0.094843 | 122.9343 | 122.8067 | 122.981 | 66.7296 | -123.0967 | 122.8489 | 123.0129 | 122.8696 | 66.724 | -123.3061
341.7969 | 123.2895 | -66.7282 | 56.2866 | -0.0057996 | -0.0030662 | 0.00082041 | 0.057293 | -0.0011987 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.0078055 | 0.062064 | -66.7335 | 0.033457 | -66.7323 | 56.2381 | 56.1197 | 56.2985 | -66.8329 | -66.7474 | 0.03241 | -66.7727 | 56.1528 | 56.3168 | 56.1964 | -67.0378 | -0.10473 | -0.048517 | -0.005324 | -0.00406 | 0.10067 | -0.16696 | 0.011905 | -0.30956 | -0.13386 | -0.019175 | -0.044522 | 0.26504 | 0.030161 | -0.09026 | 122.9663 | 122.8479 | 123.0267 | 66.7617 | -123.1196 | 122.881 | 123.045 | 122.9246 | 66.7606 | -123.3244
342.7969 | 123.2941 | -66.7007 | 56.2729 | -0.0057996 | -0.0032798 | 0.00082041 | 0.057293 | -0.0014123 | 0.063009 | -0.017016 | 0.00046367 | 0.00025221 | 0.060588 | 0.0080191 | 0.062919 | -66.7427 | 0.033457 | -66.7323 | 56.2427 | 56.1151 | 56.2848 | -66.8284 | -66.7565 | 0.03241 | -66.7819 | 56.1573 | 56.3076 | 56.1048 | -67.0378 | -0.12761 | -0.030206 | -0.041946 | -0.031525 | 0.096086 | -0.15781 | 0.011902 | -0.33703 | -0.11555 | -0.055797 | -0.081145 | 0.25588 | 0.034736 | -0.1681 | 122.9434 | 122.8158 | 122.9855 | 66.7342 | -123.1012 | 122.8581 | 123.0084 | 122.8055 | 66.7332 | -123.3107
343.7969 | 123.1888 | -66.7511 | 56.3187 | -0.0057996 | -0.003921 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061016 | 0.0084465 | 0.062064 | -66.7381 | 0.028878 | -66.7323 | 56.2427 | 56.1242 | 56.2802 | -66.8329 | -66.7565 | 0.027831 | -66.7819 | 56.1528 | 56.3076 | 56.1231 | -67.0424 | -0.081836 | -0.075983 | 0.012987 | 0.018829 | 0.10067 | -0.19443 | -0.038454 | -0.29125 | -0.16591 | -0.005443 | -0.030791 | 0.26046 | -0.011041 | -0.19556 | 122.9938 | 122.8753 | 123.0313 | 66.78 | -123.1516 | 122.9039 | 123.0587 | 122.8742 | 66.7789 | -123.361
344.7969 | 123.2803 | -66.7191 | 56.282 | -0.0057996 | -0.0037072 | 0.0012478 | 0.057506 | -0.0011987 | 0.062796 | -0.001755 | -0.00017733 | 0.00025221 | 0.061016 | 0.0080191 | 0.062064 | -66.7473 | 0.038035 | -66.7323 | 56.2289 | 56.1105 | 56.2848 | -66.8375 | -66.752 | 0.03241 | -66.7682 | 56.1573 | 56.3168 | 56.1094 | -67.0378 | -0.11846 | -0.053096 | -0.028214 | -0.013215 | 0.10524 | -0.17154 | 0.002747 | -0.31872 | -0.1247 | -0.032908 | -0.049099 | 0.26962 | 0.034739 | -0.17268 | 122.948 | 122.8296 | 123.0038 | 66.7571 | -123.1196 | 122.8764 | 123.0358 | 122.8284 | 66.7515 | -123.3198
345.7969 | 123.2162 | -66.7557 | 56.2912 | -0.013431 | -0.0032798 | 0.00082041 | 0.057293 | -0.0014123 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0084465 | 0.062278 | -66.7473 | 0.033457 | -66.7368 | 56.2427 | 56.1151 | 56.2939 | -66.8329 | -66.7565 | 0.03241 | -66.7819 | 56.1528 | 56.3122 | 56.1826 | -67.0424 | -0.077259 | -0.048517 | 0.008407 | 0.018828 | 0.096087 | -0.17612 | 0.002748 | -0.28668 | -0.13844 | -0.000866 | -0.026214 | 0.26046 | 0.021004 | -0.10857 | 122.9984 | 122.8708 | 123.0496 | 66.7891 | -123.1241 | 122.9084 | 123.0679 | 122.9383 | 66.7881 | -123.3336
346.7969 | 123.2895 | -66.7053 | 56.25 | 0.0018314 | -0.003921 | 0.0012478 | 0.05772 | -0.0011987 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0084465 | 0.062064 | -66.7473 | 0.028878 | -66.7368 | 56.2427 | 56.1105 | 56.2848 | -66.8375 | -66.752 | 0.027831 | -66.7682 | 56.1528 | 56.3122 | 56.1139 | -67.0378 | -0.13219 | -0.007318 | -0.041947 | -0.031526 | 0.10067 | -0.1395 | 0.03479 | -0.33245 | -0.09724 | -0.046641 | -0.062832 | 0.26962 | 0.062203 | -0.13605 | 122.948 | 122.8158 | 122.9901 | 66.7342 | -123.0875 | 122.8581 | 123.0175 | 122.8193 | 66.7332 | -123.2878
347.7969 | 123.2346 | -66.7465 | 56.3004 | 0.0018314 | -0.0034936 | 0.00060681 | 0.057079 | -0.0011987 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0082329 | 0.062064 | -66.7518 | 0.028878 | -66.7414 | 56.2427 | 56.1105 | 56.2939 | -66.8329 | -66.7565 | 0.027831 | -66.7727 | 56.1436 | 56.3168 | 56.1414 | -67.0378 | -0.086414 | -0.057672 | -0.005326 | 0.005094 | 0.091508 | -0.18985 | -0.006407 | -0.29125 | -0.15675 | -0.010021 | -0.026211 | 0.26504 | 0.016428 | -0.15894 | 122.9892 | 122.857 | 123.0405 | 66.7754 | -123.1333 | 122.8901 | 123.0633 | 122.8879 | 66.7744 | -123.3381
348.7969 | 123.2849 | -66.7236 | 56.2683 | -0.0057996 | -0.0034936 | 0.0010342 | 0.057079 | -0.00077134 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.060802 | 0.0086603 | 0.062278 | -66.7518 | 0.028878 | -66.7323 | 56.2427 | 56.1059 | 56.2848 | -66.8284 | -66.752 | 0.03241 | -66.7773 | 56.1528 | 56.3168 | 56.1964 | -67.0424 | -0.10472 | -0.025629 | -0.028214 | -0.008637 | 0.096086 | -0.16239 | 0.016479 | -0.31872 | -0.11555 | -0.02833 | -0.053678 | 0.26504 | 0.048471 | -0.07195 | 122.9663 | 122.8296 | 123.0084 | 66.7525 | -123.0967 | 122.8764 | 123.0404 | 122.92 | 66.756 | -123.3107
349.7969 | 123.2162 | -66.7557 | 56.3004 | 0.0018314 | -0.0037072 | 0.0010342 | 0.056652 | -0.0011987 | 0.063009 | -0.001755 | 0.00025007 | 0.00067941 | 0.060588 | 0.0086603 | 0.062705 | -66.7518 | 0.028878 | -66.7414 | 56.2427 | 56.1151 | 56.2848 | -66.8329 | -66.7565 | 0.036989 | -66.7727 | 56.1573 | 56.3168 | 56.2009 | -67.0424 | -0.077259 | -0.057672 | 0.003829 | 0.014249 | 0.091508 | -0.18527 | -0.015564 | -0.28668 | -0.14301 | -0.000866 | -0.017056 | 0.26962 | 0.016428 | -0.099415 | 122.9984 | 122.8708 | 123.0405 | 66.7846 | -123.1333 | 122.913 | 123.0725 | 122.9566 | 66.7927 | -123.3427
350.7969 | 123.2895 | -66.7282 | 56.2637 | -0.0057996 | -0.003921 | 0.0010342 | 0.057506 | -0.0016259 | 0.063223 | -0.001755 | 0.00046367 | 0.00025221 | 0.060588 | 0.0080191 | 0.06185 | -66.7518 | 0.042614 | -66.7323 | 56.2381 | 56.1242 | 56.2848 | -66.8238 | -66.752 | 0.027831 | -66.7773 | 56.1482 | 56.3122 | 56.1964 | -67.0424 | -0.095567 | -0.025629 | -0.023637 | -0.00406 | 0.091507 | -0.1395 | 0.021057 | -0.31414 | -0.11555 | -0.023753 | -0.049101 | 0.26504 | 0.04847 | -0.067372 | 122.9663 | 122.8524 | 123.013 | 66.7708 | -123.0875 | 122.8764 | 123.0404 | 122.9246 | 66.756 | -123.3061
351.7969 | 123.2391 | -66.7465 | 56.2729 | -0.021062 | -0.0037072 | 0.0010342 | 0.057079 | -0.0011987 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0084465 | 0.062705 | -66.7427 | 0.033457 | -66.7277 | 56.2381 | 56.1151 | 56.2894 | -66.8284 | -66.752 | 0.03241 | -66.7773 | 56.1573 | 56.3168 | 56.1918 | -67.0424 | -0.081835 | -0.034784 | 0.00383 | 0.018829 | 0.10066 | -0.15781 | 0.016481 | -0.29583 | -0.11555 | -0.005442 | -0.03079 | 0.26504 | 0.043894 | -0.081106 | 122.9846 | 122.8616 | 123.0359 | 66.78 | -123.1012 | 122.9039 | 123.0633 | 122.9383 | 66.7789 | -123.3152
352.7969 | 123.317 | -66.7053 | 56.2683 | 0.0094624 | -0.0034936 | 0.0010342 | 0.056865 | -0.0016259 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0084465 | 0.062278 | -66.7381 | 0.028878 | -66.7277 | 56.2289 | 56.1105 | 56.2848 | -66.8284 | -66.7565 | 0.027831 | -66.7773 | 56.1528 | 56.3122 | 56.1872 | -67.0378 | -0.12303 | -0.039364 | -0.03279 | -0.02237 | 0.10066 | -0.15781 | 0.016479 | -0.33245 | -0.11555 | -0.05122 | -0.071989 | 0.26046 | 0.043892 | -0.081107 | 122.9343 | 122.8158 | 122.9901 | 66.7342 | -123.0967 | 122.8581 | 123.0175 | 122.8925 | 66.7332 | -123.3061
353.7969 | 123.2391 | -66.7374 | 56.2958 | -0.013431 | -0.0037072 | 0.00060681 | 0.057079 | -0.0014123 | 0.062796 | -0.001755 | 0.00046367 | 0.00067941 | 0.061016 | 0.0086603 | 0.062278 | -66.7518 | 0.033457 | -66.7277 | 56.2427 | 56.1197 | 56.2894 | -66.8284 | -66.7565 | 0.03241 | -66.7819 | 56.1528 | 56.3122 | 56.2009 | -67.0424 | -0.09099 | -0.053094 | -0.014481 | 0.009674 | 0.10066 | -0.17612 | -0.006407 | -0.30499 | -0.14302 | -0.019176 | -0.044524 | 0.26046 | 0.016427 | -0.094837 | 122.98 | 122.857 | 123.0267 | 66.7708 | -123.1241 | 122.8901 | 123.0496 | 122.9383 | 66.7698 | -123.3381
354.7969 | 123.2986 | -66.7328 | 56.2637 | -0.0057996 | -0.0034936 | 0.0010342 | 0.057079 | -0.0011987 | 0.062796 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060802 | 0.0086603 | 0.062278 | -66.7518 | 0.033457 | -66.7323 | 56.2335 | 56.1288 | 56.2894 | -66.8284 | -66.752 | 0.018674 | -66.7865 | 56.1528 | 56.3214 | 56.1918 | -67.0469 | -0.095568 | -0.030208 | -0.019059 | 0.000518 | 0.096086 | -0.13492 | 0.025636 | -0.31414 | -0.11097 | -0.019175 | -0.053681 | 0.26046 | 0.057627 | -0.071951 | 122.9663 | 122.8616 | 123.0222 | 66.7662 | -123.0921 | 122.8855 | 123.0541 | 122.9246 | 66.7515 | -123.3107
355.7969 | 123.3673 | -66.7145 | 56.2363 | -0.0057996 | -0.0034936 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.001755 | 0.00025007 | 0.00025221 | 0.060588 | 0.0086603 | 0.062064 | -66.7381 | 0.028878 | -66.7323 | 56.2427 | 56.1197 | 56.2802 | -66.8329 | -66.7474 | 0.027831 | -66.7682 | 56.1482 | 56.3168 | 56.1918 | -67.0378 | -0.11846 | 0.006415 | -0.023634 | -0.017792 | 0.10067 | -0.11661 | 0.043944 | -0.3233 | -0.088085 | -0.032907 | -0.053676 | 0.26962 | 0.080515 | -0.044485 | 122.9572 | 122.8341 | 122.9947 | 66.7434 | -123.0692 | 122.8627 | 123.0313 | 122.9063 | 66.7423 | -123.274
356.7969 | 123.2941 | -66.7191 | 56.282 | -0.0057996 | -0.0034936 | 0.0010342 | 0.057293 | -0.0014123 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0084465 | 0.062278 | -66.7473 | 0.028878 | -66.7277 | 56.2473 | 56.1151 | 56.2802 | -66.8375 | -66.752 | 0.036989 | -66.7819 | 56.1573 | 56.3214 | 56.2009 | -67.0378 | -0.11846 | -0.034783 | -0.028214 | -0.008637 | 0.10982 | -0.16696 | -0.001832 | -0.31872 | -0.1247 | -0.032908 | -0.062835 | 0.25588 | 0.039317 | -0.081104 | 122.9663 | 122.8341 | 122.9993 | 66.7479 | -123.1196 | 122.8764 | 123.0404 | 122.92 | 66.756 | -123.3198
357.7969 | 123.2254 | -66.7557 | 56.3095 | -0.028693 | -0.0037072 | 0.0010342 | 0.057079 | -0.0011987 | 0.062796 | -0.017016 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0086603 | 0.062064 | -66.7518 | 0.038035 | -66.7323 | 56.2427 | 56.1197 | 56.2939 | -66.8284 | -66.7428 | 0.03241 | -66.7727 | 56.1528 | 56.3259 | 56.1918 | -67.0424 | -0.07268 | -0.066827 | 0.003829 | 0.023406 | 0.096086 | -0.18985 | -0.015562 | -0.28668 | -0.15675 | 0.01287 | -0.017056 | 0.26962 | 0.01643 | -0.11773 | 122.9984 | 122.8753 | 123.0496 | 66.7937 | -123.1379 | 122.9084 | 123.0816 | 122.9475 | 66.7881 | -123.3519
358.7969 | 123.2758 | -66.7465 | 56.2546 | 0.0094624 | -0.0034936 | 0.00082041 | 0.057079 | -0.0011987 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.060802 | 0.0082329 | 0.062491 | -66.7473 | 0.019721 | -66.7368 | 56.2381 | 56.1059 | 56.2756 | -66.8375 | -66.752 | 0.023253 | -66.7773 | 56.1436 | 56.3214 | 56.1964 | -67.0424 | -0.090993 | -0.016474 | -0.000748 | 0.009673 | 0.10067 | -0.14866 | 0.021055 | -0.29583 | -0.11098 | -0.005442 | -0.03079 | 0.26504 | 0.066782 | -0.058217 | 122.9846 | 122.8524 | 123.0222 | 66.7662 | -123.0921 | 122.8901 | 123.0679 | 122.9429 | 66.7698 | -123.2969
359.7969 | 123.2666 | -66.7282 | 56.3004 | 0.0018314 | -0.0037072 | 0.0010342 | 0.057079 | -0.0014123 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0082329 | 0.062919 | -66.7335 | 0.033457 | -66.7368 | 56.2381 | 56.1013 | 56.2756 | -66.8284 | -66.7474 | 0.03241 | -66.7727 | 56.1528 | 56.3168 | 56.1918 | -67.0424 | -0.10015 | -0.06225 | -0.005324 | -0.008638 | 0.091508 | -0.19901 | -0.024721 | -0.31414 | -0.14759 | -0.019175 | -0.044522 | 0.26962 | 0.016428 | -0.10857 | 122.9663 | 122.8296 | 123.0038 | 66.7617 | -123.1287 | 122.881 | 123.045 | 122.92 | 66.7606 | -123.3427
360.7969 | 123.3078 | -66.7145 | 56.2637 | 0.0018314 | -0.0034936 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | -0.0093855 | 0.00025007 | 0.00067941 | 0.060802 | 0.0082329 | 0.062064 | -66.7473 | 0.033457 | -66.7277 | 56.2427 | 56.1151 | 56.2848 | -66.8329 | -66.7474 | 0.03241 | -66.7819 | 56.1573 | 56.3259 | 56.1872 | -67.0469 | -0.11846 | -0.021051 | -0.032791 | -0.013214 | 0.10524 | -0.14865 | 0.021057 | -0.33245 | -0.10639 | -0.032907 | -0.067412 | 0.26504 | 0.062206 | -0.076529 | 122.9572 | 122.8296 | 122.9993 | 66.7479 | -123.0967 | 122.8718 | 123.0404 | 122.9017 | 66.7469 | -123.3107
361.7969 | 123.23 | -66.7511 | 56.2912 | -0.0057996 | -0.0037072 | 0.0012478 | 0.057293 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.061016 | 0.0084465 | 0.06185 | -66.7473 | 0.028878 | -66.7323 | 56.2427 | 56.1151 | 56.2939 | -66.8375 | -66.7428 | 0.027831 | -66.7727 | 56.1436 | 56.3214 | 56.1552 | -67.0332 | -0.086415 | -0.048517 | 0.00383 | 0.018829 | 0.10524 | -0.17612 | 0.002748 | -0.2821 | -0.1476 | 0.008293 | -0.021633 | 0.26046 | 0.030161 | -0.13605 | 122.9938 | 122.8662 | 123.045 | 66.78 | -123.1287 | 122.8947 | 123.0725 | 122.9063 | 66.7789 | -123.3244
362.7969 | 123.1613 | -66.7465 | 56.337 | -0.0057996 | -0.0034936 | 0.0010342 | 0.057293 | -0.0011987 | 0.063009 | 0.0058755 | 0.00025007 | 0.0011068 | 0.061016 | 0.0084465 | 0.062278 | -66.7473 | 0.033457 | -66.7368 | 56.2335 | 56.1105 | 56.2756 | -66.8375 | -66.752 | 0.03241 | -66.7727 | 56.1528 | 56.3168 | 56.2055 | -67.0378 | -0.090993 | -0.10345 | -0.000748 | 0.009673 | 0.10067 | -0.22648 | -0.061342 | -0.29125 | -0.18422 | -0.005442 | -0.026211 | 0.26504 | -0.020193 | -0.13146 | 122.98 | 122.857 | 123.0222 | 66.78 | -123.1745 | 122.8993 | 123.0633 | 122.952 | 66.7789 | -123.3747
363.7969 | 123.2117 | -66.7465 | 56.2958 | -0.0057996 | -0.0037072 | 0.0012478 | 0.057079 | -0.00098494 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0082329 | 0.062278 | -66.7427 | 0.033457 | -66.7323 | 56.2427 | 56.1151 | 56.2894 | -66.8329 | -66.752 | 0.03241 | -66.7682 | 56.1482 | 56.3122 | 56.1918 | -67.0469 | -0.086414 | -0.053094 | 0.00383 | 0.014251 | 0.10067 | -0.1807 | -0.006407 | -0.30041 | -0.14759 | -0.005442 | -0.021633 | 0.27878 | 0.016427 | -0.10399 | 122.9892 | 122.8616 | 123.0359 | 66.78 | -123.1287 | 122.8947 | 123.0587 | 122.9383 | 66.7789 | -123.3427
364.7969 | 123.2803 | -66.7236 | 56.2546 | 0.0018314 | -0.0041346 | 0.00082041 | 0.057079 | -0.0011987 | 0.062796 | -0.001755 | 0.00025007 | 0.00046581 | 0.060802 | 0.0082329 | 0.062278 | -66.7473 | 0.028878 | -66.7277 | 56.2381 | 56.0968 | 56.2848 | -66.8329 | -66.7474 | 0.027831 | -66.7773 | 56.1573 | 56.3168 | 56.2009 | -67.0515 | -0.1093 | -0.016474 | -0.023636 | -0.004059 | 0.10524 | -0.15781 | 0.030212 | -0.32788 | -0.097239 | -0.023752 | -0.053678 | 0.2742 | 0.062204 | -0.053639 | 122.9617 | 122.8204 | 123.0084 | 66.7525 | -123.0875 | 122.881 | 123.0404 | 122.9246 | 66.7515 | -123.3061
365.7969 | 123.2666 | -66.7236 | 56.2729 | -0.0057996 | -0.003921 | 0.00060681 | 0.057293 | -0.0011987 | 0.063009 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060588 | 0.0082329 | 0.062064 | -66.7473 | 0.028878 | -66.7277 | 56.2427 | 56.1013 | 56.2802 | -66.8238 | -66.7474 | 0.027831 | -66.7819 | 56.1528 | 56.3122 | 56.1964 | -67.0378 | -0.10014 | -0.030206 | -0.023636 | -0.004059 | 0.096085 | -0.17155 | 0.007323 | -0.31414 | -0.12013 | -0.023752 | -0.058257 | 0.25588 | 0.039315 | -0.076527 | 122.9663 | 122.825 | 123.0038 | 66.7525 | -123.0967 | 122.8764 | 123.0358 | 122.92 | 66.7515 | -123.3107
366.7969 | 123.2666 | -66.7236 | 56.3004 | 0.0094624 | -0.0034936 | 0.00082041 | 0.057293 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0084465 | 0.062491 | -66.7427 | 0.028878 | -66.7323 | 56.2381 | 56.1059 | 56.2848 | -66.8329 | -66.7382 | 0.027831 | -66.7773 | 56.1528 | 56.3259 | 56.178 | -67.0515 | -0.1093 | -0.06225 | -0.019058 | -0.008637 | 0.10067 | -0.19443 | -0.015564 | -0.32788 | -0.14759 | -0.014594 | -0.053678 | 0.2742 | 0.025585 | -0.12231 | 122.9617 | 122.8296 | 123.0084 | 66.7525 | -123.1333 | 122.8764 | 123.0496 | 122.9017 | 66.7515 | -123.3519
367.7969 | 123.317 | -66.7236 | 56.3095 | 0.0094624 | -0.0037072 | 0.00060681 | 0.057293 | -0.0014123 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060375 | 0.0084465 | 0.062064 | -66.7427 | 0.033457 | -66.7323 | 56.2335 | 56.1197 | 56.2848 | -66.8284 | -66.7474 | 0.027831 | -66.7773 | 56.1528 | 56.3168 | 56.1964 | -67.0424 | -0.10472 | -0.075984 | -0.019058 | -0.008637 | 0.096086 | -0.18985 | -0.024719 | -0.31872 | -0.15675 | -0.023752 | -0.053678 | 0.26504 | 0.007273 | -0.11315 | 122.9572 | 122.8433 | 123.0084 | 66.7571 | -123.1379 | 122.8764 | 123.0404 | 122.92 | 66.7515 | -123.3519
368.7969 | 123.2895 | -66.6962 | 56.2729 | -0.013431 | -0.0037072 | 0.00082041 | 0.057506 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0084465 | 0.062278 | -66.7381 | 0.033457 | -66.7277 | 56.2381 | 56.1288 | 56.2802 | -66.8329 | -66.7474 | 0.03241 | -66.7773 | 56.1528 | 56.3168 | 56.1826 | -67.0469 | -0.13677 | -0.034784 | -0.041945 | -0.031525 | 0.10524 | -0.14407 | 0.007323 | -0.35076 | -0.12013 | -0.051218 | -0.081144 | 0.26962 | 0.043894 | -0.090263 | 122.9343 | 122.825 | 122.9764 | 66.7296 | -123.1058 | 122.8489 | 123.0129 | 122.8788 | 66.7286 | -123.3198
369.7969 | 123.4085 | -66.7236 | 56.282 | -0.0057996 | -0.0034936 | 0.0010342 | 0.057079 | -0.0011987 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.0090875 | 0.062278 | -66.7427 | 0.038035 | -66.7277 | 56.2427 | 56.1105 | 56.2756 | -66.8284 | -66.7474 | 0.027831 | -66.7636 | 56.1528 | 56.3259 | 56.2009 | -67.0469 | -0.10472 | -0.039361 | -0.019058 | -0.004059 | 0.10066 | -0.17154 | -0.00641 | -0.3233 | -0.12928 | -0.023752 | -0.039942 | 0.28336 | 0.043896 | -0.081104 | 122.9663 | 122.8341 | 122.9993 | 66.7617 | -123.1104 | 122.8764 | 123.0496 | 122.9246 | 66.7515 | -123.329
370.7969 | 123.2941 | -66.7236 | 56.2454 | -0.0057996 | -0.003921 | 0.00060681 | 0.057506 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.061016 | 0.0084465 | 0.062278 | -66.7473 | 0.033457 | -66.7277 | 56.2335 | 56.1105 | 56.2894 | -66.8329 | -66.7428 | 0.027831 | -66.7819 | 56.1482 | 56.3122 | 56.2009 | -67.0469 | -0.1093 | -0.011897 | -0.023636 | -0.004059 | 0.10524 | -0.13492 | 0.043947 | -0.3233 | -0.09724 | -0.019173 | -0.058257 | 0.26504 | 0.066781 | -0.044483 | 122.9572 | 122.8341 | 123.013 | 66.7571 | -123.0784 | 122.8718 | 123.0358 | 122.9246 | 66.7515 | -123.2924
371.7969 | 123.2483 | -66.7511 | 56.3187 | -0.013431 | -0.0037072 | 0.0010342 | 0.057293 | -0.0014123 | 0.063009 | -0.017016 | 0.00025007 | 0.00025221 | 0.060802 | 0.0086603 | 0.06185 | -66.7427 | 0.033457 | -66.7323 | 56.2518 | 56.1197 | 56.2894 | -66.8421 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3259 | 56.1826 | -67.0469 | -0.090994 | -0.066826 | 0.008408 | 0.018829 | 0.10982 | -0.19901 | -0.029296 | -0.29583 | -0.17048 | 0.003714 | -0.021633 | 0.2742 | 0.007274 | -0.13604 | 123.0029 | 122.8708 | 123.0405 | 66.7846 | -123.1608 | 122.8993 | 123.077 | 122.9337 | 66.7789 | -123.3656
372.7969 | 123.2025 | -66.7191 | 56.3416 | 0.0018314 | -0.0037072 | 0.00082041 | 0.057293 | -0.0011987 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.061016 | 0.0084465 | 0.062278 | -66.7473 | 0.028878 | -66.7231 | 56.2427 | 56.1197 | 56.2894 | -66.8421 | -66.7474 | 0.03241 | -66.7819 | 56.1482 | 56.3214 | 56.1872 | -67.0469 | -0.12304 | -0.098871 | -0.028214 | -0.004058 | 0.11898 | -0.22189 | -0.052184 | -0.32788 | -0.19337 | -0.02833 | -0.062835 | 0.26504 | -0.020193 | -0.15435 | 122.9617 | 122.8387 | 123.0084 | 66.7479 | -123.1836 | 122.8672 | 123.0404 | 122.9063 | 66.7515 | -123.3885
373.7969 | 123.2758 | -66.7145 | 56.25 | -0.0057996 | -0.003921 | 0.0012478 | 0.056865 | -0.0011987 | 0.063009 | -0.017016 | -0.00017733 | 0.00046581 | 0.060588 | 0.0086603 | 0.062278 | -66.7381 | 0.028878 | -66.7323 | 56.2381 | 56.1105 | 56.2848 | -66.8375 | -66.7474 | 0.027831 | -66.7682 | 56.1482 | 56.3214 | 56.1826 | -67.0424 | -0.12304 | -0.011896 | -0.023634 | -0.017792 | 0.10524 | -0.1395 | 0.03479 | -0.32788 | -0.10182 | -0.032907 | -0.053676 | 0.2742 | 0.07136 | -0.067375 | 122.9526 | 122.825 | 122.9993 | 66.7434 | -123.0875 | 122.8627 | 123.0358 | 122.8971 | 66.7423 | -123.2924
374.7969 | 123.2895 | -66.7053 | 56.2592 | -0.0057996 | -0.0032798 | 0.00082041 | 0.057293 | -0.0014123 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.061016 | 0.0086603 | 0.062064 | -66.7427 | 0.028878 | -66.7323 | 56.2335 | 56.1105 | 56.2848 | -66.8329 | -66.752 | 0.027831 | -66.7819 | 56.1482 | 56.3122 | 56.2009 | -67.0515 | -0.12761 | -0.02563 | -0.037369 | -0.026948 | 0.10067 | -0.14865 | 0.025635 | -0.34619 | -0.11097 | -0.046641 | -0.076568 | 0.26962 | 0.053048 | -0.058216 | 122.9388 | 122.8158 | 122.9901 | 66.7342 | -123.0921 | 122.8535 | 123.0175 | 122.9063 | 66.7332 | -123.3107
375.7969 | 123.2529 | -66.7419 | 56.2546 | -0.013431 | -0.0034936 | 0.0010342 | 0.057293 | -0.0011987 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0086603 | 0.062491 | -66.7473 | 0.033457 | -66.7277 | 56.2381 | 56.1242 | 56.2939 | -66.8284 | -66.7428 | 0.036989 | -66.7773 | 56.1528 | 56.3168 | 56.1368 | -67.0424 | -0.086413 | -0.016474 | -0.005326 | 0.014251 | 0.10066 | -0.13034 | 0.039369 | -0.30041 | -0.10182 | -0.000863 | -0.035368 | 0.26504 | 0.062204 | -0.11774 | 122.98 | 122.8662 | 123.0359 | 66.7754 | -123.0829 | 122.8947 | 123.0587 | 122.8788 | 66.7789 | -123.2969
376.7969 | 123.23 | -66.7191 | 56.3187 | -0.013431 | -0.0037072 | 0.0010342 | 0.057506 | -0.0011987 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0086603 | 0.062064 | -66.7427 | 0.028878 | -66.7323 | 56.2335 | 56.1197 | 56.2802 | -66.8284 | -66.752 | 0.027831 | -66.7773 | 56.1528 | 56.3122 | 56.1964 | -67.0469 | -0.1093 | -0.08514 | -0.023636 | -0.013215 | 0.096086 | -0.19901 | -0.038454 | -0.32788 | -0.16591 | -0.032908 | -0.058256 | 0.26962 | -0.006462 | -0.1223 | 122.9526 | 122.8387 | 122.9993 | 66.7479 | -123.147 | 122.8718 | 123.0313 | 122.9154 | 66.7469 | -123.3656
377.7969 | 123.262 | -66.7007 | 56.3232 | 0.0018314 | -0.0034936 | 0.00060681 | 0.057506 | -0.0014123 | 0.063009 | -0.001755 | 0.00025007 | 3.8406e-05 | 0.060588 | 0.0084465 | 0.062064 | -66.7427 | 0.033457 | -66.7277 | 56.2381 | 56.1197 | 56.2894 | -66.8329 | -66.7382 | 0.03241 | -66.7727 | 56.1436 | 56.3305 | 56.1231 | -67.0424 | -0.13219 | -0.085138 | -0.041946 | -0.026947 | 0.10524 | -0.20358 | -0.033873 | -0.34161 | -0.17964 | -0.037482 | -0.071987 | 0.26962 | 0.007275 | -0.20014 | 122.9388 | 122.8204 | 122.9901 | 66.7342 | -123.1562 | 122.8443 | 123.0313 | 122.8238 | 66.7332 | -123.3656
378.7969 | 123.2346 | -66.7099 | 56.2958 | 0.0018314 | -0.0037072 | 0.00082041 | 0.057506 | -0.0011987 | 0.062796 | -0.017016 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0084465 | 0.062064 | -66.7427 | 0.028878 | -66.7323 | 56.2335 | 56.1059 | 56.2848 | -66.8329 | -66.752 | 0.027831 | -66.7773 | 56.1573 | 56.3214 | 56.1048 | -67.0424 | -0.12304 | -0.062251 | -0.032791 | -0.02237 | 0.10067 | -0.18985 | -0.010986 | -0.33245 | -0.13844 | -0.042063 | -0.067411 | 0.26504 | 0.025584 | -0.19099 | 122.9434 | 122.8158 | 122.9947 | 66.7388 | -123.1287 | 122.8672 | 123.0313 | 122.8147 | 66.7377 | -123.3381
379.7969 | 123.262 | -66.6962 | 56.2775 | 0.0018314 | -0.0041346 | 0.00082041 | 0.057293 | -0.0014123 | 0.063009 | -0.001755 | 0.00025007 | 0.00067941 | 0.060588 | 0.0086603 | 0.062278 | -66.7427 | 0.033457 | -66.7323 | 56.2335 | 56.1197 | 56.2894 | -66.8375 | -66.7428 | 0.036989 | -66.7727 | 56.1528 | 56.3122 | 56.1506 | -67.0469 | -0.14135 | -0.043941 | -0.046524 | -0.036103 | 0.10524 | -0.15781 | 0.011903 | -0.35076 | -0.12471 | -0.046639 | -0.076565 | 0.2742 | 0.034737 | -0.12689 | 122.9297 | 122.8158 | 122.9855 | 66.7296 | -123.115 | 122.8489 | 123.0084 | 122.8467 | 66.7332 | -123.3244
380.7969 | 123.3032 | -66.7236 | 56.3004 | -0.0057996 | -0.0037072 | 0.0012478 | 0.05772 | -0.0014123 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060802 | 0.0086603 | 0.062491 | -66.7381 | 0.028878 | -66.7368 | 56.2381 | 56.1197 | 56.2848 | -66.8329 | -66.7428 | 0.027831 | -66.7727 | 56.1619 | 56.3122 | 56.146 | -67.0515 | -0.1093 | -0.06225 | -0.014479 | -0.013215 | 0.096087 | -0.1807 | -0.015564 | -0.32788 | -0.13844 | -0.019173 | -0.049099 | 0.27878 | 0.011849 | -0.15436 | 122.9617 | 122.8433 | 123.0084 | 66.7525 | -123.1333 | 122.8856 | 123.0358 | 122.8696 | 66.7515 | -123.3519
381.7969 | 123.3124 | -66.7099 | 56.2729 | -0.0057996 | -0.0037072 | 0.00082041 | 0.057293 | -0.00098494 | 0.062368 | -0.0093855 | 0.00046367 | 0.00046581 | 0.060802 | 0.0084465 | 0.062491 | -66.7473 | 0.042614 | -66.7368 | 56.2518 | 56.1013 | 56.2802 | -66.8421 | -66.7474 | 0.036989 | -66.7682 | 56.1528 | 56.3259 | 56.1139 | -67.0469 | -0.13219 | -0.021049 | -0.037369 | -0.026948 | 0.10525 | -0.17155 | 0.007323 | -0.33703 | -0.12013 | -0.037485 | -0.058254 | 0.27878 | 0.053051 | -0.15894 | 122.9617 | 122.8112 | 122.9901 | 66.7525 | -123.115 | 122.8627 | 123.0358 | 122.8238 | 66.7469 | -123.3198
382.7969 | 123.2712 | -66.6962 | 56.3324 | 0.0018314 | -0.003921 | 0.0010342 | 0.057293 | -0.0014123 | 0.063009 | 0.013506 | 3.6274e-05 | 0.00089321 | 0.061016 | 0.0084465 | 0.062278 | -66.7427 | 0.038035 | -66.7277 | 56.2427 | 56.1059 | 56.2848 | -66.8238 | -66.7382 | 0.03241 | -66.7727 | 56.1482 | 56.3168 | 56.2009 | -67.0469 | -0.12761 | -0.089715 | -0.046524 | -0.031525 | 0.096085 | -0.22648 | -0.047607 | -0.35076 | -0.18422 | -0.04206 | -0.076565 | 0.2742 | -0.015615 | -0.13146 | 122.9388 | 122.8021 | 122.981 | 66.7342 | -123.1562 | 122.8443 | 123.0129 | 122.8971 | 66.7286 | -123.3793
383.7969 | 123.2666 | -66.7099 | 56.2683 | -0.0057996 | -0.0037072 | 0.0012478 | 0.057506 | -0.0011987 | 0.062796 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060802 | 0.0082329 | 0.062278 | -66.7381 | 0.033457 | -66.7323 | 56.2381 | 56.1242 | 56.2894 | -66.8329 | -66.7428 | 0.036989 | -66.7773 | 56.1482 | 56.3122 | 56.2009 | -67.0515 | -0.12304 | -0.030207 | -0.028212 | -0.02237 | 0.10067 | -0.14407 | 0.021058 | -0.34161 | -0.12013 | -0.032906 | -0.067411 | 0.2742 | 0.043892 | -0.067372 | 122.948 | 122.8341 | 122.9993 | 66.7434 | -123.1012 | 122.8581 | 123.0221 | 122.9108 | 66.7469 | -123.3198
384.7969 | 123.2758 | -66.7282 | 56.2775 | -0.0057996 | -0.003921 | 0.00082041 | 0.057506 | -0.0011987 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0086603 | 0.062278 | -66.7518 | 0.028878 | -66.7323 | 56.2381 | 56.1105 | 56.2939 | -66.8329 | -66.7428 | 0.023253 | -66.7727 | 56.1528 | 56.3076 | 56.1826 | -67.0469 | -0.10473 | -0.039362 | -0.023637 | -0.00406 | 0.10067 | -0.16697 | 0.016481 | -0.31872 | -0.12471 | -0.014596 | -0.044522 | 0.2742 | 0.030158 | -0.094841 | 122.9663 | 122.8387 | 123.0222 | 66.7571 | -123.1104 | 122.881 | 123.0358 | 122.9108 | 66.7515 | -123.3244
385.7969 | 123.2803 | -66.7191 | 56.2866 | -0.0057996 | -0.0034936 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0084465 | 0.06185 | -66.7381 | 0.0243 | -66.7231 | 56.2335 | 56.1105 | 56.2894 | -66.8375 | -66.7474 | 0.036989 | -66.7773 | 56.1482 | 56.3168 | 56.2009 | -67.0424 | -0.11846 | -0.053096 | -0.019057 | -0.004058 | 0.1144 | -0.17612 | 0.002748 | -0.3233 | -0.13844 | -0.02833 | -0.058256 | 0.26504 | 0.030161 | -0.085682 | 122.9526 | 122.8296 | 123.0084 | 66.7434 | -123.1241 | 122.8672 | 123.0358 | 122.92 | 66.756 | -123.329
386.7969 | 123.2346 | -66.7099 | 56.3004 | -0.0057996 | -0.0037072 | 0.00082041 | 0.057079 | -0.0011987 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0086603 | 0.062064 | -66.7473 | 0.028878 | -66.7185 | 56.2335 | 56.1242 | 56.2894 | -66.8375 | -66.7474 | 0.023253 | -66.7727 | 56.1436 | 56.3122 | 56.1735 | -67.0424 | -0.12761 | -0.066829 | -0.037369 | -0.008635 | 0.11898 | -0.17612 | -0.010985 | -0.33245 | -0.15675 | -0.037485 | -0.062832 | 0.26962 | 0.011849 | -0.12689 | 122.9434 | 122.8341 | 122.9993 | 66.7388 | -123.1379 | 122.8535 | 123.0221 | 122.8834 | 66.7332 | -123.3427
387.7969 | 123.1567 | -66.7145 | 56.3416 | 0.0018314 | -0.003921 | 0.00082041 | 0.056652 | -0.0014123 | 0.062796 | -0.001755 | 0.00025007 | 0.00046581 | 0.060588 | 0.0088739 | 0.062278 | -66.7427 | 0.0243 | -66.7323 | 56.2473 | 56.1059 | 56.2848 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.2009 | -67.0469 | -0.11846 | -0.094293 | -0.028213 | -0.017792 | 0.10067 | -0.23563 | -0.056763 | -0.33245 | -0.19337 | -0.028328 | -0.049097 | 0.28336 | -0.020193 | -0.14061 | 122.9617 | 122.8204 | 122.9993 | 66.7388 | -123.1745 | 122.8627 | 123.0358 | 122.9154 | 66.7469 | -123.3885
388.7969 | 123.2346 | -66.7282 | 56.2592 | 0.017093 | -0.0037072 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0084465 | 0.062278 | -66.7335 | 0.028878 | -66.7368 | 56.2381 | 56.1242 | 56.2985 | -66.8284 | -66.7382 | 0.027831 | -66.7727 | 56.1528 | 56.3168 | 56.1964 | -67.0469 | -0.10015 | -0.021051 | -0.005324 | -0.008638 | 0.091508 | -0.13492 | 0.039371 | -0.31872 | -0.10639 | -0.010017 | -0.044522 | 0.2742 | 0.057627 | -0.062794 | 122.9663 | 122.8524 | 123.0267 | 66.7571 | -123.0875 | 122.881 | 123.045 | 122.9246 | 66.756 | -123.3061
389.7969 | 123.2803 | -66.7099 | 56.2637 | -0.0057996 | -0.0043482 | 0.0010342 | 0.057293 | -0.00098494 | 0.063223 | 0.0058755 | 3.6274e-05 | 0.00025221 | 0.060802 | 0.0086603 | 0.062491 | -66.7381 | 0.033457 | -66.7368 | 56.2473 | 56.1059 | 56.2848 | -66.8329 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0469 | -0.12304 | -0.016473 | -0.028212 | -0.026948 | 0.096087 | -0.15781 | 0.021057 | -0.33703 | -0.11555 | -0.037485 | -0.062832 | 0.2742 | 0.057627 | -0.071951 | 122.9572 | 122.8158 | 122.9947 | 66.7434 | -123.0967 | 122.8581 | 123.0313 | 122.9017 | 66.7377 | -123.3107
390.7969 | 123.2758 | -66.7053 | 56.3095 | 0.0018314 | -0.0041346 | 0.00082041 | 0.057293 | -0.00077134 | 0.063009 | -0.0093855 | 0.00046367 | 0.00046581 | 0.060588 | 0.0090875 | 0.062064 | -66.7518 | 0.028878 | -66.7323 | 56.2427 | 56.1105 | 56.2939 | -66.8284 | -66.7428 | 0.027831 | -66.7819 | 56.1482 | 56.3214 | 56.1643 | -67.0515 | -0.12303 | -0.066827 | -0.046525 | -0.026948 | 0.096086 | -0.19901 | -0.015562 | -0.34619 | -0.16133 | -0.037484 | -0.076568 | 0.26962 | 0.011851 | -0.1452 | 122.948 | 122.8158 | 122.9993 | 66.7342 | -123.1379 | 122.8535 | 123.0267 | 122.8696 | 66.7332 | -123.361
391.7969 | 123.2574 | -66.7191 | 56.3049 | 0.0018314 | -0.003921 | 0.0010342 | 0.056865 | -0.0011987 | 0.063009 | -0.017016 | 0.00025007 | 0.00089321 | 0.060375 | 0.0088739 | 0.062064 | -66.7381 | 0.042614 | -66.7323 | 56.2427 | 56.1151 | 56.2894 | -66.8284 | -66.7428 | 0.027831 | -66.7727 | 56.1528 | 56.3214 | 56.1552 | -67.0469 | -0.1093 | -0.06225 | -0.019057 | -0.013215 | 0.096086 | -0.18985 | -0.015563 | -0.32788 | -0.15217 | -0.023751 | -0.053677 | 0.2742 | 0.016428 | -0.14978 | 122.9617 | 122.8341 | 123.0084 | 66.7617 | -123.1333 | 122.8718 | 123.0404 | 122.8742 | 66.7469 | -123.3519
392.7969 | 123.2986 | -66.7099 | 56.2592 | 0.0094624 | -0.0043482 | 0.00060681 | 0.057506 | -0.0014123 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.060588 | 0.0088739 | 0.062064 | -66.7427 | 0.028878 | -66.7277 | 56.2381 | 56.1151 | 56.2802 | -66.8329 | -66.752 | 0.027831 | -66.7727 | 56.1573 | 56.3214 | 56.1964 | -67.0515 | -0.12304 | -0.021051 | -0.032791 | -0.017792 | 0.10524 | -0.14408 | 0.021056 | -0.34161 | -0.10182 | -0.042063 | -0.062832 | 0.27878 | 0.062205 | -0.062794 | 122.948 | 122.825 | 122.9901 | 66.7388 | -123.0921 | 122.8672 | 123.0313 | 122.9063 | 66.7377 | -123.3107
393.7969 | 123.2941 | -66.7282 | 56.282 | 0.0094624 | -0.0034936 | 0.0010342 | 0.057293 | -0.00098494 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.060802 | 0.0088739 | 0.061637 | -66.7381 | 0.038035 | -66.7277 | 56.2427 | 56.1242 | 56.3077 | -66.8284 | -66.7474 | 0.03241 | -66.7819 | 56.1482 | 56.3168 | 56.2009 | -67.0515 | -0.10015 | -0.039361 | -0.009902 | 0.000518 | 0.10066 | -0.15781 | 0.02564 | -0.3233 | -0.13386 | -0.019175 | -0.05368 | 0.26962 | 0.034739 | -0.081104 | 122.9709 | 122.8524 | 123.0359 | 66.7662 | -123.1104 | 122.8764 | 123.045 | 122.9291 | 66.7606 | -123.3336
394.7969 | 123.2849 | -66.6916 | 56.2592 | -0.0057996 | -0.003921 | 0.00082041 | 0.057293 | -0.0011987 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0090875 | 0.062278 | -66.7427 | 0.033457 | -66.7277 | 56.2427 | 56.1197 | 56.2894 | -66.8329 | -66.7382 | 0.027831 | -66.7636 | 56.1482 | 56.3168 | 56.1918 | -67.0424 | -0.14135 | -0.016473 | -0.051102 | -0.036103 | 0.10524 | -0.1395 | 0.030214 | -0.35076 | -0.11097 | -0.046638 | -0.071986 | 0.27878 | 0.057627 | -0.067373 | 122.9343 | 122.8112 | 122.981 | 66.725 | -123.0921 | 122.8398 | 123.0084 | 122.8834 | 66.7194 | -123.3015
395.7969 | 123.1842 | -66.7236 | 56.282 | -0.013431 | -0.0037072 | 0.0012478 | 0.057293 | -0.00098494 | 0.062796 | 0.013506 | 0.00025007 | 0.00089321 | 0.060588 | 0.0088739 | 0.06185 | -66.7427 | 0.028878 | -66.7231 | 56.2427 | 56.1105 | 56.2756 | -66.8375 | -66.7428 | 0.027831 | -66.7773 | 56.1482 | 56.3168 | 56.1826 | -67.0469 | -0.11388 | -0.039361 | -0.019058 | 0.00052 | 0.1144 | -0.17154 | -0.00641 | -0.3233 | -0.13386 | -0.019173 | -0.053678 | 0.26962 | 0.034739 | -0.099418 | 122.9663 | 122.8341 | 122.9993 | 66.7525 | -123.1196 | 122.8718 | 123.0404 | 122.9063 | 66.7515 | -123.329
396.7969 | 123.2941 | -66.7145 | 56.2729 | -0.0057996 | -0.003921 | 0.0012478 | 0.056865 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060802 | 0.0086603 | 0.06185 | -66.7473 | 0.028878 | -66.7323 | 56.2427 | 56.1197 | 56.2939 | -66.8329 | -66.7474 | 0.03241 | -66.7773 | 56.1482 | 56.3259 | 56.1918 | -67.0424 | -0.11846 | -0.030206 | -0.032791 | -0.017792 | 0.10067 | -0.15323 | 0.021059 | -0.32788 | -0.12471 | -0.032907 | -0.062833 | 0.26504 | 0.053051 | -0.081106 | 122.9572 | 122.8341 | 123.0084 | 66.7434 | -123.1058 | 122.8627 | 123.0404 | 122.9063 | 66.7469 | -123.3152
397.7969 | 123.2574 | -66.7328 | 56.2546 | -0.013431 | -0.0037072 | 0.0010342 | 0.056865 | -0.0014123 | 0.063223 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060375 | 0.0088739 | 0.06185 | -66.7381 | 0.0243 | -66.7277 | 56.2427 | 56.1197 | 56.2894 | -66.8329 | -66.7474 | 0.036989 | -66.7727 | 56.1482 | 56.3214 | 56.1964 | -67.0561 | -0.10015 | -0.011896 | -0.005324 | 0.005096 | 0.10524 | -0.13492 | 0.034791 | -0.3233 | -0.1064 | -0.014597 | -0.039944 | 0.28336 | 0.066782 | -0.058217 | 122.9755 | 122.8524 | 123.0222 | 66.7571 | -123.0875 | 122.881 | 123.0541 | 122.9291 | 66.7698 | -123.3107
398.7969 | 123.2803 | -66.6916 | 56.282 | -0.0057996 | -0.0037072 | 0.0010342 | 0.057293 | -0.0011987 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060588 | 0.0088739 | 0.061423 | -66.7381 | 0.033457 | -66.7277 | 56.2473 | 56.1288 | 56.2848 | -66.8329 | -66.7474 | 0.041567 | -66.7682 | 56.1436 | 56.3305 | 56.1964 | -67.0378 | -0.14135 | -0.034783 | -0.046523 | -0.036103 | 0.10524 | -0.15323 | 0.002747 | -0.34619 | -0.13844 | -0.055796 | -0.076565 | 0.26962 | 0.048474 | -0.085682 | 122.9388 | 122.8204 | 122.9764 | 66.725 | -123.115 | 122.8352 | 123.0221 | 122.8879 | 66.7332 | -123.3198
399.7969 | 123.2346 | -66.7603 | 56.2775 | -0.0057996 | -0.003921 | 0.00082041 | 0.057293 | -0.00098494 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0088739 | 0.062491 | -66.7381 | 0.028878 | -66.7323 | 56.2427 | 56.1197 | 56.2802 | -66.8421 | -66.7428 | 0.03241 | -66.7727 | 56.1573 | 56.3214 | 56.2009 | -67.0424 | -0.081839 | -0.034784 | 0.022142 | 0.027984 | 0.10982 | -0.15781 | 0.002745 | -0.2821 | -0.12013 | 0.017448 | -0.012478 | 0.26962 | 0.043894 | -0.076527 | 123.0029 | 122.8799 | 123.0405 | 66.7891 | -123.1196 | 122.9176 | 123.0816 | 122.9612 | 66.7927 | -123.3198
400.7969 | 123.2758 | -66.7236 | 56.2546 | 0.0018314 | -0.003921 | 0.0010342 | 0.057293 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0088739 | 0.06185 | -66.7381 | 0.0243 | -66.7323 | 56.2335 | 56.1151 | 56.2848 | -66.8329 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3168 | 56.1872 | -67.0515 | -0.1093 | -0.021053 | -0.014479 | -0.008637 | 0.10067 | -0.1395 | 0.030212 | -0.32788 | -0.1064 | -0.023752 | -0.049099 | 0.27878 | 0.062204 | -0.067374 | 122.9572 | 122.8387 | 123.0084 | 66.7479 | -123.0875 | 122.8718 | 123.0404 | 122.9108 | 66.7515 | -123.3061
401.7969 | 123.1705 | -66.7511 | 56.282 | 0.0018314 | -0.0041346 | 0.0010342 | 0.057079 | -0.0011987 | 0.063009 | -0.0093855 | 0.00025007 | 0.00067941 | 0.060802 | 0.0088739 | 0.062278 | -66.7427 | 0.038035 | -66.7368 | 56.2335 | 56.1242 | 56.2985 | -66.8284 | -66.752 | 0.03241 | -66.7773 | 56.1528 | 56.3168 | 56.1918 | -67.0424 | -0.077257 | -0.048518 | 0.008408 | 0.014251 | 0.091508 | -0.15781 | 0.016483 | -0.29125 | -0.12928 | -0.000864 | -0.026212 | 0.26504 | 0.034739 | -0.090261 | 122.9846 | 122.8753 | 123.0496 | 66.7891 | -123.1104 | 122.9039 | 123.0679 | 122.9429 | 66.7835 | -123.3244
402.7969 | 123.3307 | -66.6916 | 56.2546 | -0.0057996 | -0.0041346 | 0.0010342 | 0.057079 | -0.0011987 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0086603 | 0.06185 | -66.7473 | 0.033457 | -66.7277 | 56.2427 | 56.1197 | 56.2894 | -66.8284 | -66.7382 | 0.027831 | -66.7773 | 56.1528 | 56.3259 | 56.1826 | -67.0469 | -0.13677 | -0.011896 | -0.05568 | -0.036103 | 0.10066 | -0.13492 | 0.034791 | -0.35534 | -0.10182 | -0.046638 | -0.085722 | 0.26962 | 0.071361 | -0.071953 | 122.9343 | 122.8112 | 122.981 | 66.725 | -123.0829 | 122.8443 | 123.0175 | 122.8742 | 66.7194 | -123.3015
403.7969 | 123.2117 | -66.7419 | 56.3095 | -0.013431 | -0.0043482 | 0.00060681 | 0.057079 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0090875 | 0.062278 | -66.7427 | 0.033457 | -66.7277 | 56.2427 | 56.1242 | 56.2894 | -66.8284 | -66.7382 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0469 | -0.086413 | -0.066827 | -0.000748 | 0.014251 | 0.10066 | -0.18527 | -0.02014 | -0.30499 | -0.16133 | 0.003716 | -0.030789 | 0.2742 | 0.011851 | -0.11773 | 122.9846 | 122.8662 | 123.0313 | 66.7754 | -123.1379 | 122.8901 | 123.0633 | 122.9337 | 66.7698 | -123.3564
404.7969 | 123.2986 | -66.7145 | 56.2912 | -0.0057996 | -0.0043482 | 0.0012478 | 0.057293 | -0.0011987 | 0.063009 | -0.001755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0088739 | 0.06185 | -66.7473 | 0.033457 | -66.7231 | 56.2381 | 56.1242 | 56.2939 | -66.8329 | -66.7474 | 0.03241 | -66.7727 | 56.1528 | 56.3214 | 56.1918 | -67.0469 | -0.11846 | -0.053095 | -0.032791 | -0.008635 | 0.10982 | -0.16696 | 0.002748 | -0.33245 | -0.13844 | -0.032907 | -0.058254 | 0.2742 | 0.030161 | -0.099417 | 122.9526 | 122.8387 | 123.0084 | 66.7479 | -123.1241 | 122.8672 | 123.0358 | 122.9063 | 66.7469 | -123.3381
405.7969 | 123.1613 | -66.7511 | 56.3461 | 0.0018314 | -0.0043482 | 0.0010342 | 0.057079 | -0.0011987 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0088739 | 0.06185 | -66.7381 | 0.028878 | -66.7277 | 56.2427 | 56.1242 | 56.2985 | -66.8284 | -66.7428 | 0.03241 | -66.7727 | 56.1573 | 56.3259 | 56.1918 | -67.0424 | -0.077257 | -0.10345 | 0.012987 | 0.023407 | 0.10066 | -0.22189 | -0.047604 | -0.29125 | -0.18879 | 0.008293 | -0.021633 | 0.26962 | -0.020191 | -0.15435 | 122.9938 | 122.8753 | 123.0496 | 66.78 | -123.1745 | 122.9084 | 123.077 | 122.9429 | 66.7835 | -123.3885
406.7969 | 123.2162 | -66.7374 | 56.2866 | -0.0057996 | -0.003921 | 0.0010342 | 0.056865 | -0.0016259 | 0.063009 | -0.001755 | -0.00017733 | 0.00067941 | 0.060802 | 0.0088739 | 0.062278 | -66.7381 | 0.028878 | -66.7323 | 56.2381 | 56.1197 | 56.2894 | -66.8329 | -66.7474 | 0.03241 | -66.7727 | 56.1573 | 56.3168 | 56.2009 | -67.0469 | -0.095569 | -0.048517 | -0.000746 | 0.005096 | 0.10067 | -0.16696 | 0.002748 | -0.30957 | -0.12928 | -0.010019 | -0.035366 | 0.2742 | 0.030161 | -0.085682 | 122.9755 | 122.857 | 123.0267 | 66.7662 | -123.1196 | 122.8947 | 123.0541 | 122.9383 | 66.7698 | -123.3336
407.7969 | 123.175 | -66.7694 | 56.3232 | 0.0018314 | -0.004562 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060375 | 0.0088739 | 0.06185 | -66.7427 | 0.0243 | -66.7323 | 56.2381 | 56.1105 | 56.2894 | -66.8375 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3122 | 56.1918 | -67.0469 | -0.068105 | -0.085138 | 0.026718 | 0.037139 | 0.10524 | -0.21274 | -0.033873 | -0.27752 | -0.17506 | 0.022024 | -0.003323 | 0.2742 | -0.011039 | -0.13146 | 123.0075 | 122.8799 | 123.0588 | 66.7937 | -123.1608 | 122.9176 | 123.0816 | 122.9612 | 66.7972 | -123.3702
408.7969 | 123.2254 | -66.7145 | 56.2637 | -0.0057996 | -0.003921 | 0.00060681 | 0.056865 | -0.0016259 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0090875 | 0.062491 | -66.7381 | 0.0243 | -66.7277 | 56.2381 | 56.1197 | 56.2894 | -66.8284 | -66.7474 | 0.03241 | -66.7819 | 56.1482 | 56.3168 | 56.1643 | -67.0424 | -0.11388 | -0.025629 | -0.023634 | -0.013214 | 0.10066 | -0.14408 | 0.025636 | -0.32788 | -0.11555 | -0.032907 | -0.067412 | 0.26046 | 0.053049 | -0.099422 | 122.9526 | 122.8341 | 123.0038 | 66.7388 | -123.0921 | 122.8627 | 123.0313 | 122.8788 | 66.7469 | -123.3061
409.7969 | 122.9599 | -66.774 | 56.2408 | -0.0057996 | -0.0041346 | 0.0010342 | 0.056865 | -0.00098494 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.0090875 | 0.062064 | -66.7427 | 0.028878 | -66.7277 | 56.2381 | 56.1151 | 56.2939 | -66.8329 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0469 | -0.058948 | -0.002741 | 0.031296 | 0.046295 | 0.10524 | -0.12577 | 0.053102 | -0.27294 | -0.092663 | 0.026602 | 0.001255 | 0.2742 | 0.080515 | -0.049063 | 123.0121 | 122.8891 | 123.0679 | 66.8029 | -123.0738 | 122.9222 | 123.0953 | 122.9658 | 66.8018 | -123.2878
410.7969 | 123.2117 | -66.7557 | 56.2775 | -0.0057996 | -0.003921 | 0.0010342 | 0.056438 | -0.0011987 | 0.063009 | -0.001755 | -0.00017733 | 0.00046581 | 0.060588 | 0.0090875 | 0.06185 | -66.7381 | 0.033457 | -66.7368 | 56.2335 | 56.1197 | 56.2848 | -66.8329 | -66.7428 | 0.036989 | -66.7727 | 56.1436 | 56.3122 | 56.2055 | -67.0515 | -0.077259 | -0.043941 | 0.017564 | 0.018828 | 0.096087 | -0.15781 | 0.007324 | -0.29583 | -0.13386 | 0.01287 | -0.017056 | 0.27878 | 0.034737 | -0.071948 | 122.9892 | 122.8753 | 123.0405 | 66.7891 | -123.1104 | 122.8993 | 123.0679 | 122.9612 | 66.7927 | -123.329
411.7969 | 123.1567 | -66.7419 | 56.3324 | -0.0057996 | -0.0041346 | 0.0010342 | 0.057079 | -0.0014123 | 0.063223 | -0.001755 | -0.00017733 | 0.00025221 | 0.060588 | 0.0088739 | 0.061637 | -66.7427 | 0.033457 | -66.7277 | 56.2473 | 56.1151 | 56.2939 | -66.8329 | -66.7428 | 0.03241 | -66.7727 | 56.1528 | 56.3168 | 56.1964 | -67.0424 | -0.090992 | -0.085137 | -0.000748 | 0.014251 | 0.10524 | -0.21732 | -0.03845 | -0.30041 | -0.17964 | -0.000863 | -0.030789 | 0.26962 | -0.015615 | -0.13604 | 122.9892 | 122.857 | 123.0359 | 66.7754 | -123.1653 | 122.8947 | 123.0587 | 122.9383 | 66.7744 | -123.3748
412.7969 | 123.1796 | -66.7465 | 56.2958 | -0.013431 | -0.0041346 | 0.0012478 | 0.057506 | -0.0014123 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060588 | 0.0088739 | 0.061637 | -66.729 | 0.033457 | -66.7231 | 56.2335 | 56.1105 | 56.2848 | -66.8421 | -66.7474 | 0.027831 | -66.7773 | 56.1528 | 56.3122 | 56.1964 | -67.0424 | -0.095572 | -0.062251 | 0.017565 | 0.023408 | 0.11898 | -0.18528 | -0.010986 | -0.29583 | -0.14302 | -0.000864 | -0.03079 | 0.26504 | 0.016427 | -0.099415 | 122.98 | 122.857 | 123.0313 | 66.78 | -123.1379 | 122.8993 | 123.0587 | 122.9429 | 66.7744 | -123.3381
413.7969 | 123.1659 | -66.774 | 56.2683 | 0.0094624 | -0.0043482 | 0.0012478 | 0.056865 | -0.0014123 | 0.063009 | 0.013506 | 0.00025007 | 0.00046581 | 0.060802 | 0.0088739 | 0.062064 | -66.7473 | 0.033457 | -66.7277 | 56.2427 | 56.1151 | 56.2939 | -66.8375 | -66.752 | 0.03241 | -66.7773 | 56.1482 | 56.3214 | 56.1643 | -67.0424 | -0.063527 | -0.025629 | 0.026718 | 0.046295 | 0.10982 | -0.15323 | 0.025636 | -0.26837 | -0.12013 | 0.022024 | -0.003324 | 0.26504 | 0.053049 | -0.104 | 123.0167 | 122.8891 | 123.0679 | 66.8074 | -123.1058 | 122.9222 | 123.0953 | 122.9383 | 66.8064 | -123.3107
414.7969 | 123.23 | -66.7465 | 56.2866 | -0.013431 | -0.003921 | 0.00082041 | 0.057079 | -0.00098494 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060588 | 0.0086603 | 0.06185 | -66.7427 | 0.028878 | -66.7277 | 56.2427 | 56.1105 | 56.2894 | -66.8375 | -66.7428 | 0.027831 | -66.7819 | 56.1436 | 56.3214 | 56.1552 | -67.0515 | -0.090993 | -0.043939 | 0.00383 | 0.018829 | 0.10982 | -0.17612 | 0.002748 | -0.30499 | -0.14302 | 0.003715 | -0.035369 | 0.26962 | 0.034739 | -0.13147 | 122.9892 | 122.857 | 123.0359 | 66.7754 | -123.1241 | 122.8901 | 123.0679 | 122.9017 | 66.7744 | -123.3381
415.7969 | 123.1796 | -66.7465 | 56.282 | 0.0094624 | -0.0037072 | 0.00060681 | 0.057293 | -0.0011987 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.0090875 | 0.06185 | -66.7427 | 0.033457 | -66.7277 | 56.2473 | 56.1242 | 56.2939 | -66.8421 | -66.7428 | 0.03241 | -66.7636 | 56.1573 | 56.3259 | 56.1002 | -67.0469 | -0.095572 | -0.034783 | 0.00383 | 0.018829 | 0.1144 | -0.15781 | 0.011904 | -0.30041 | -0.1247 | 0.003715 | -0.017054 | 0.28336 | 0.043896 | -0.18183 | 122.9938 | 122.8708 | 123.0405 | 66.78 | -123.1241 | 122.9039 | 123.0725 | 122.8467 | 66.7789 | -123.329
416.7969 | 123.1888 | -66.7511 | 56.2592 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0011987 | 0.063009 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0090875 | 0.062064 | -66.7381 | 0.028878 | -66.7277 | 56.2381 | 56.1151 | 56.2939 | -66.8375 | -66.7474 | 0.03241 | -66.7682 | 56.1482 | 56.3259 | 56.2009 | -67.0515 | -0.086415 | -0.021051 | 0.012987 | 0.023407 | 0.10982 | -0.14408 | 0.034792 | -0.30041 | -0.11097 | 0.003714 | -0.017055 | 0.28336 | 0.066784 | -0.058216 | 122.9892 | 122.8662 | 123.045 | 66.78 | -123.0967 | 122.8993 | 123.077 | 122.952 | 66.7835 | -123.3107
417.7969 | 123.1522 | -66.7557 | 56.3004 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0011987 | 0.062796 | 0.0058755 | 0.00025007 | 0.00025221 | 0.060588 | 0.0093013 | 0.06185 | -66.7427 | 0.033457 | -66.7231 | 56.2473 | 56.1059 | 56.2939 | -66.8375 | -66.752 | 0.03241 | -66.7773 | 56.1528 | 56.3168 | 56.1918 | -67.0515 | -0.081838 | -0.053094 | 0.012985 | 0.032563 | 0.1144 | -0.19443 | -0.006407 | -0.29583 | -0.14759 | 0.003713 | -0.021635 | 0.2742 | 0.016428 | -0.10857 | 123.0029 | 122.8616 | 123.0496 | 66.7891 | -123.1379 | 122.9084 | 123.0725 | 122.9475 | 66.7881 | -123.3519
418.7969 | 123.175 | -66.7511 | 56.2683 | 0.0018314 | -0.0041346 | 0.00060681 | 0.056865 | -0.0011987 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0093013 | 0.062064 | -66.7381 | 0.028878 | -66.7368 | 56.2427 | 56.1105 | 56.2939 | -66.8238 | -66.752 | 0.03241 | -66.7682 | 56.1482 | 56.3076 | 56.1872 | -67.0469 | -0.072678 | -0.025629 | 0.012987 | 0.014251 | 0.086929 | -0.15781 | 0.025636 | -0.29583 | -0.12013 | -0.000864 | -0.017055 | 0.27878 | 0.039313 | -0.081107 | 122.9938 | 122.8616 | 123.045 | 66.78 | -123.0921 | 122.8993 | 123.0587 | 122.9383 | 66.7835 | -123.3152
419.7969 | 123.1842 | -66.7328 | 56.282 | -0.0057996 | -0.0041346 | 0.0010342 | 0.057079 | -0.0014123 | 0.063009 | 0.0058755 | -0.00039093 | 0.00046581 | 0.060588 | 0.0093013 | 0.062278 | -66.7335 | 0.033457 | -66.7323 | 56.2427 | 56.1288 | 56.2985 | -66.8284 | -66.7428 | 0.03241 | -66.7773 | 56.1573 | 56.3122 | 56.1964 | -67.0515 | -0.095568 | -0.039361 | -0.000746 | 0.000518 | 0.096086 | -0.15323 | 0.016483 | -0.31872 | -0.1247 | -0.010018 | -0.044523 | 0.2742 | 0.03016 | -0.085682 | 122.9755 | 122.8616 | 123.0313 | 66.7662 | -123.1104 | 122.8901 | 123.045 | 122.9291 | 66.7652 | -123.3336
420.7969 | 123.23 | -66.7236 | 56.2866 | -0.013431 | -0.0043482 | 0.00082041 | 0.056865 | -0.00077134 | 0.062796 | -0.0093855 | 0.00025007 | 0.00067941 | 0.060588 | 0.0088739 | 0.062064 | -66.7381 | 0.028878 | -66.7277 | 56.2335 | 56.1151 | 56.2939 | -66.8375 | -66.7565 | 0.03241 | -66.7727 | 56.1528 | 56.3122 | 56.1872 | -67.0515 | -0.11388 | -0.053096 | -0.014479 | -0.004059 | 0.10982 | -0.17154 | 0.007326 | -0.32788 | -0.13386 | -0.032909 | -0.049099 | 0.27878 | 0.025582 | -0.099417 | 122.9572 | 122.8387 | 123.0176 | 66.7525 | -123.1241 | 122.8764 | 123.0358 | 122.9108 | 66.756 | -123.3381
421.7969 | 123.1476 | -66.7557 | 56.3141 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0016259 | 0.063009 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060375 | 0.0095149 | 0.062064 | -66.7381 | 0.033457 | -66.7414 | 56.2427 | 56.1288 | 56.2939 | -66.8329 | -66.7428 | 0.027831 | -66.7727 | 56.1482 | 56.3122 | 56.1872 | -67.0561 | -0.077259 | -0.071405 | 0.017564 | 0.014249 | 0.091508 | -0.18527 | -0.02014 | -0.30041 | -0.16591 | 0.01287 | -0.017056 | 0.28336 | -0.001884 | -0.12688 | 122.9984 | 122.8845 | 123.0496 | 66.7891 | -123.147 | 122.9039 | 123.0679 | 122.9429 | 66.7835 | -123.3702
422.7969 | 123.1796 | -66.7694 | 56.2958 | 0.0018314 | -0.0043482 | 0.00082041 | 0.056652 | -0.0014123 | 0.063009 | -0.017016 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.0088739 | 0.062064 | -66.7381 | 0.033457 | -66.7323 | 56.2335 | 56.138 | 56.2939 | -66.8375 | -66.752 | 0.03241 | -66.7636 | 56.1573 | 56.3122 | 56.1918 | -67.0515 | -0.068105 | -0.062251 | 0.031297 | 0.037139 | 0.10524 | -0.1578 | -0.001829 | -0.2821 | -0.13844 | 0.017446 | 0.005834 | 0.28793 | 0.016427 | -0.10399 | 123.0029 | 122.9074 | 123.0634 | 66.8029 | -123.1333 | 122.9267 | 123.0816 | 122.9612 | 66.8018 | -123.3473
423.7969 | 123.1979 | -66.7374 | 56.2866 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0014123 | 0.062796 | 0.013506 | 0.00025007 | 0.00089321 | 0.060375 | 0.0093013 | 0.062064 | -66.7381 | 0.033457 | -66.7323 | 56.2427 | 56.1471 | 56.2894 | -66.8329 | -66.752 | 0.036989 | -66.7682 | 56.1482 | 56.3168 | 56.1918 | -67.0561 | -0.095569 | -0.043939 | -0.000746 | 0.005096 | 0.10067 | -0.13949 | 0.002748 | -0.31872 | -0.13844 | -0.014597 | -0.030788 | 0.28794 | 0.030161 | -0.094839 | 122.98 | 122.8845 | 123.0267 | 66.7708 | -123.1196 | 122.8855 | 123.0541 | 122.9291 | 66.7744 | -123.3427
424.7969 | 123.1842 | -66.7603 | 56.2729 | -0.013431 | -0.003921 | 0.00082041 | 0.057079 | -0.0014123 | 0.063223 | -0.0093855 | -0.00017733 | 0.00025221 | 0.060375 | 0.0090875 | 0.061637 | -66.7427 | 0.028878 | -66.7277 | 56.2335 | 56.138 | 56.2848 | -66.8329 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3168 | 56.1964 | -67.0515 | -0.072681 | -0.039363 | 0.017563 | 0.032562 | 0.10524 | -0.13491 | 0.011902 | -0.29126 | -0.12471 | 0.012869 | -0.012478 | 0.27878 | 0.043894 | -0.076527 | 122.9938 | 122.8982 | 123.045 | 66.7891 | -123.1058 | 122.9084 | 123.077 | 122.9566 | 66.7881 | -123.3244
425.7969 | 123.2254 | -66.7282 | 56.3004 | 0.0018314 | -0.0043482 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0090875 | 0.06185 | -66.7427 | 0.038035 | -66.7368 | 56.2381 | 56.1426 | 56.3031 | -66.8329 | -66.7474 | 0.03241 | -66.7727 | 56.1482 | 56.3168 | 56.1872 | -67.0561 | -0.10473 | -0.06225 | -0.014481 | -0.008638 | 0.096087 | -0.1578 | 0.00275 | -0.32788 | -0.15217 | -0.019175 | -0.044522 | 0.28336 | 0.016428 | -0.11315 | 122.9663 | 122.8708 | 123.0313 | 66.7662 | -123.1333 | 122.8764 | 123.045 | 122.9154 | 66.7606 | -123.3564
426.7969 | 123.143 | -66.7557 | 56.3095 | 0.0018314 | -0.0041346 | 0.00060681 | 0.057079 | -0.0016259 | 0.063009 | -0.017016 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0093013 | 0.06185 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.138 | 56.2985 | -66.8329 | -66.7474 | 0.027831 | -66.7727 | 56.1436 | 56.3122 | 56.1872 | -67.0515 | -0.077259 | -0.071405 | 0.022142 | 0.027984 | 0.10524 | -0.17153 | -0.010983 | -0.29583 | -0.16591 | 0.008291 | -0.017056 | 0.27878 | 0.002694 | -0.1223 | 122.9938 | 122.8936 | 123.0542 | 66.7891 | -123.1424 | 122.8993 | 123.0679 | 122.9429 | 66.7835 | -123.361
427.7969 | 123.1888 | -66.7465 | 56.3004 | -0.0057996 | -0.004562 | 0.0010342 | 0.056865 | -0.0014123 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0088739 | 0.061637 | -66.7427 | 0.033457 | -66.7277 | 56.2427 | 56.1334 | 56.2939 | -66.8238 | -66.7428 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0424 | -0.077256 | -0.057672 | 0.00383 | 0.018829 | 0.096085 | -0.16696 | -0.006407 | -0.29583 | -0.15217 | 0.003715 | -0.026211 | 0.26962 | 0.021006 | -0.10857 | 122.9892 | 122.8799 | 123.0405 | 66.78 | -123.1241 | 122.8947 | 123.0679 | 122.9383 | 66.7744 | -123.3427
428.7969 | 123.1613 | -66.7648 | 56.3049 | -0.0057996 | -0.0043482 | 0.0012478 | 0.056865 | -0.0014123 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.0093013 | 0.061637 | -66.7381 | 0.033457 | -66.7323 | 56.2335 | 56.1197 | 56.2939 | -66.8375 | -66.7474 | 0.027831 | -66.7727 | 56.1482 | 56.3122 | 56.1964 | -67.0469 | -0.072682 | -0.071407 | 0.02672 | 0.032562 | 0.10524 | -0.18527 | -0.010985 | -0.2821 | -0.15675 | 0.017447 | -0.0079 | 0.2742 | 0.007271 | -0.10857 | 122.9984 | 122.8845 | 123.0588 | 66.7983 | -123.1424 | 122.913 | 123.077 | 122.9612 | 66.7927 | -123.3519
429.7969 | 123.1796 | -66.7603 | 56.282 | -0.0057996 | -0.0043482 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0090875 | 0.061637 | -66.7381 | 0.038035 | -66.7323 | 56.2381 | 56.138 | 56.2985 | -66.8329 | -66.752 | 0.03241 | -66.7727 | 56.1573 | 56.3214 | 56.1918 | -67.0515 | -0.072681 | -0.043939 | 0.022142 | 0.027984 | 0.10067 | -0.14407 | 0.016483 | -0.29126 | -0.1247 | 0.008291 | -0.012478 | 0.27878 | 0.039317 | -0.090261 | 122.9984 | 122.8982 | 123.0588 | 66.7983 | -123.115 | 122.9176 | 123.0816 | 122.952 | 66.7927 | -123.3336
430.7969 | 123.143 | -66.7603 | 56.2912 | 0.0018314 | -0.004562 | 0.0010342 | 0.056865 | -0.0016259 | 0.063009 | -0.001755 | -0.00039093 | 0.00067941 | 0.060375 | 0.0093013 | 0.062064 | -66.7427 | 0.033457 | -66.7231 | 56.2381 | 56.1288 | 56.2939 | -66.8329 | -66.7428 | 0.027831 | -66.7773 | 56.1528 | 56.3168 | 56.1826 | -67.0515 | -0.072681 | -0.053095 | 0.017563 | 0.037141 | 0.10982 | -0.16238 | 0.002748 | -0.29126 | -0.13844 | 0.017448 | -0.017057 | 0.2742 | 0.025583 | -0.10857 | 122.9984 | 122.8891 | 123.0542 | 66.7937 | -123.1241 | 122.913 | 123.077 | 122.9429 | 66.7881 | -123.3427
431.7969 | 123.1979 | -66.7694 | 56.3187 | 0.0094624 | -0.0043482 | 0.0010342 | 0.056865 | -0.0011987 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.060588 | 0.0093013 | 0.06185 | -66.7381 | 0.033457 | -66.7368 | 56.2381 | 56.1334 | 56.2939 | -66.8375 | -66.7428 | 0.03241 | -66.7682 | 56.1482 | 56.3122 | 56.1918 | -67.0469 | -0.068105 | -0.080561 | 0.031297 | 0.032561 | 0.10067 | -0.18527 | -0.024718 | -0.27752 | -0.17048 | 0.026603 | 0.001255 | 0.27878 | -0.006462 | -0.12688 | 123.0075 | 122.9028 | 123.0634 | 66.8029 | -123.1562 | 122.9176 | 123.0816 | 122.9612 | 66.8018 | -123.3656
432.7969 | 123.1613 | -66.7419 | 56.2958 | 0.0018314 | -0.0043482 | 0.0012478 | 0.056865 | -0.0014123 | 0.063009 | -0.001755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0090875 | 0.061423 | -66.7381 | 0.038035 | -66.7185 | 56.2427 | 56.1288 | 56.2894 | -66.8238 | -66.7428 | 0.027831 | -66.7682 | 56.1436 | 56.3168 | 56.1964 | -67.0561 | -0.081834 | -0.053094 | 0.003831 | 0.023408 | 0.10524 | -0.16696 | -0.006407 | -0.31415 | -0.15217 | -0.000863 | -0.026211 | 0.28794 | 0.021006 | -0.099415 | 122.9846 | 122.8708 | 123.0313 | 66.78 | -123.1196 | 122.8855 | 123.0587 | 122.9383 | 66.7698 | -123.3519
433.7969 | 123.2803 | -66.7648 | 56.2775 | 0.0018314 | -0.0043482 | 0.0010342 | 0.057079 | -0.0018397 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060375 | 0.0093013 | 0.061637 | -66.7381 | 0.033457 | -66.7277 | 56.2427 | 56.138 | 56.2985 | -66.8329 | -66.752 | 0.027831 | -66.7682 | 56.1482 | 56.3168 | 56.1964 | -67.0515 | -0.068103 | -0.034784 | 0.02672 | 0.03714 | 0.10524 | -0.13949 | 0.02106 | -0.28668 | -0.12928 | 0.012869 | -0.003322 | 0.28336 | 0.039316 | -0.081105 | 123.0075 | 122.9028 | 123.0634 | 66.7983 | -123.1104 | 122.913 | 123.0816 | 122.9612 | 66.7927 | -123.329
434.7969 | 123.2803 | -66.7648 | 56.3095 | 0.0018314 | -0.0043482 | 0.0010342 | 0.057079 | -0.0016259 | 0.063223 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.0090875 | 0.061423 | -66.7427 | 0.033457 | -66.7323 | 56.2518 | 56.1242 | 56.2985 | -66.8238 | -66.7382 | 0.027831 | -66.7727 | 56.139 | 56.3168 | 56.1918 | -67.0469 | -0.058945 | -0.05767 | 0.022141 | 0.032562 | 0.091507 | -0.18527 | -0.010983 | -0.2821 | -0.17048 | 0.026605 | -0.0079 | 0.2742 | 0.007273 | -0.11773 | 123.0167 | 122.8891 | 123.0634 | 66.7983 | -123.1333 | 122.9039 | 123.0816 | 122.9566 | 66.7927 | -123.3564
435.7969 | 123.2025 | -66.7419 | 56.2958 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0014123 | 0.063223 | -0.001755 | -0.00039093 | 0.00046581 | 0.060375 | 0.0095149 | 0.062278 | -66.7381 | 0.033457 | -66.7323 | 56.2427 | 56.1242 | 56.2894 | -66.8375 | -66.7428 | 0.03241 | -66.7727 | 56.1482 | 56.3214 | 56.1872 | -67.0561 | -0.095571 | -0.053094 | 0.003831 | 0.009673 | 0.10524 | -0.17154 | -0.006407 | -0.31415 | -0.14759 | -0.000863 | -0.030789 | 0.28336 | 0.025584 | -0.10857 | 122.9846 | 122.8662 | 123.0313 | 66.7754 | -123.1333 | 122.8901 | 123.0633 | 122.9291 | 66.7744 | -123.3519
436.7969 | 123.1476 | -66.7877 | 56.2958 | -0.0057996 | -0.004562 | 0.0010342 | 0.057079 | -0.0011987 | 0.063009 | -0.001755 | -0.00017733 | 0.00089321 | 0.060375 | 0.0095149 | 0.061637 | -66.7381 | 0.038035 | -66.7323 | 56.2473 | 56.1105 | 56.2939 | -66.8375 | -66.7474 | 0.03241 | -66.7682 | 56.1528 | 56.3168 | 56.1643 | -67.0515 | -0.049794 | -0.048516 | 0.049608 | 0.05545 | 0.10524 | -0.18528 | -0.001829 | -0.26379 | -0.14302 | 0.040335 | 0.019566 | 0.28336 | 0.021006 | -0.13146 | 123.035 | 122.8982 | 123.0817 | 66.8258 | -123.1333 | 122.9405 | 123.1045 | 122.952 | 66.8201 | -123.3473
437.7969 | 123.2071 | -66.7419 | 56.2912 | 0.0018314 | -0.0043482 | 0.0012478 | 0.056865 | -0.0016259 | 0.062582 | 0.013506 | 0.00046367 | 0.00067941 | 0.060588 | 0.0088739 | 0.06185 | -66.7427 | 0.033457 | -66.7414 | 56.2381 | 56.1242 | 56.2985 | -66.8284 | -66.7428 | 0.027831 | -66.759 | 56.1528 | 56.3214 | 56.1552 | -67.0515 | -0.086413 | -0.053095 | -0.000748 | 0.000516 | 0.086929 | -0.16696 | 0.007327 | -0.30957 | -0.13844 | -0.000863 | -0.017053 | 0.29251 | 0.030161 | -0.13605 | 122.98 | 122.8662 | 123.0405 | 66.7754 | -123.1196 | 122.8947 | 123.0633 | 122.8971 | 66.7698 | -123.3427
438.7969 | 123.1613 | -66.7603 | 56.2683 | -0.013431 | -0.004562 | 0.0010342 | 0.057079 | -0.0016259 | 0.063009 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060588 | 0.0095149 | 0.061423 | -66.7381 | 0.028878 | -66.7368 | 56.2381 | 56.1151 | 56.2939 | -66.8375 | -66.7382 | 0.036989 | -66.7682 | 56.1482 | 56.3122 | 56.1277 | -67.0652 | -0.07726 | -0.030207 | 0.022142 | 0.023406 | 0.10067 | -0.15323 | 0.025636 | -0.30499 | -0.12013 | 0.022027 | -0.0079 | 0.29709 | 0.043892 | -0.14063 | 122.9984 | 122.8753 | 123.0542 | 66.7891 | -123.1058 | 122.9084 | 123.0725 | 122.8879 | 66.7972 | -123.3336
439.7969 | 123.262 | -66.7465 | 56.3049 | -0.0057996 | -0.0043482 | 0.00082041 | 0.057079 | -0.0016259 | 0.063009 | -0.001755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0097285 | 0.062278 | -66.7335 | 0.028878 | -66.7323 | 56.2427 | 56.1197 | 56.2985 | -66.8329 | -66.752 | 0.03241 | -66.7727 | 56.1436 | 56.3214 | 56.1643 | -67.0561 | -0.086414 | -0.06225 | 0.012987 | 0.014251 | 0.10067 | -0.18527 | -0.006406 | -0.30957 | -0.16133 | -0.005442 | -0.026211 | 0.28336 | 0.016428 | -0.14062 | 122.9892 | 122.8662 | 123.045 | 66.7754 | -123.1379 | 122.8901 | 123.0679 | 122.9108 | 66.7789 | -123.361
440.7969 | 123.1384 | -66.7603 | 56.3049 | 0.0018314 | -0.0043482 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0093013 | 0.061637 | -66.7335 | 0.033457 | -66.7277 | 56.2473 | 56.1151 | 56.2939 | -66.8421 | -66.7428 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 56.0911 | -67.0469 | -0.081839 | -0.057672 | 0.02672 | 0.032562 | 0.1144 | -0.18985 | -0.010985 | -0.28668 | -0.15675 | 0.017448 | -0.0079 | 0.27878 | 0.016428 | -0.21388 | 123.0075 | 122.8753 | 123.0542 | 66.7937 | -123.147 | 122.9084 | 123.0816 | 122.8513 | 66.7927 | -123.3519
441.7969 | 123.1934 | -66.7557 | 56.3232 | -0.0057996 | -0.0043482 | 0.00082041 | 0.056865 | -0.0018397 | 0.063009 | -0.001755 | -0.00017733 | 0.00025221 | 0.060375 | 0.0095149 | 0.06185 | -66.7381 | 0.033457 | -66.7277 | 56.2381 | 56.1151 | 56.2939 | -66.8238 | -66.7428 | 0.03241 | -66.7727 | 56.1573 | 56.3214 | 56.1414 | -67.0515 | -0.068101 | -0.085138 | 0.017564 | 0.027984 | 0.096085 | -0.20816 | -0.029295 | -0.29583 | -0.1659 | 0.01287 | -0.017056 | 0.27878 | -0.001882 | -0.18182 | 122.9938 | 122.8708 | 123.0496 | 66.7891 | -123.147 | 122.913 | 123.077 | 122.8971 | 66.7881 | -123.3748
442.7969 | 122.9782 | -66.7923 | 56.25 | -0.0057996 | -0.004562 | 0.00060681 | 0.056865 | -0.0016259 | 0.062796 | -0.0093855 | -0.00039093 | 0.00046581 | 0.060375 | 0.0093013 | 0.062064 | -66.7335 | 0.033457 | -66.7323 | 56.2427 | 56.1151 | 56.2939 | -66.8375 | -66.7382 | 0.027831 | -66.7636 | 56.1482 | 56.3214 | 56.1048 | -67.0561 | -0.045217 | -0.007318 | 0.058763 | 0.060027 | 0.10524 | -0.13492 | 0.043947 | -0.26379 | -0.10182 | 0.05407 | 0.028722 | 0.29251 | 0.07136 | -0.14521 | 123.035 | 122.9074 | 123.0862 | 66.8258 | -123.0875 | 122.9405 | 123.1137 | 122.8971 | 66.8201 | -123.3061
443.7969 | 123.2117 | -66.7236 | 56.2912 | 0.0018314 | -0.004562 | 0.00082041 | 0.057293 | -0.0011987 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0095149 | 0.06185 | -66.7427 | 0.0243 | -66.7277 | 56.2427 | 56.1197 | 56.2985 | -66.8421 | -66.7428 | 0.036989 | -66.7682 | 56.139 | 56.3259 | 56.146 | -67.0515 | -0.11846 | -0.048517 | -0.019058 | -0.004059 | 0.1144 | -0.17154 | 0.007327 | -0.32788 | -0.15217 | -0.019173 | -0.044521 | 0.28336 | 0.03474 | -0.1452 | 122.9663 | 122.8433 | 123.0222 | 66.7479 | -123.1333 | 122.8627 | 123.0496 | 122.8696 | 66.7606 | -123.3427
444.7969 | 123.1796 | -66.7557 | 56.2866 | -0.013431 | -0.0041346 | 0.0012478 | 0.057293 | -0.0016259 | 0.063223 | 0.013506 | -0.00017733 | 0.00046581 | 0.060588 | 0.0093013 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2473 | 56.1197 | 56.2939 | -66.8284 | -66.7428 | 0.03241 | -66.7727 | 56.1573 | 56.3168 | 56.1552 | -67.0515 | -0.07268 | -0.039361 | 0.022142 | 0.027984 | 0.10066 | -0.16696 | 0.007326 | -0.29583 | -0.12928 | 0.01287 | -0.017056 | 0.27878 | 0.030161 | -0.13147 | 123.0029 | 122.8753 | 123.0496 | 66.7937 | -123.115 | 122.913 | 123.0725 | 122.9108 | 66.7881 | -123.3381
445.7969 | 123.2071 | -66.7694 | 56.2866 | -0.0057996 | -0.0047756 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | -0.001755 | 0.00025007 | 0.00025221 | 0.060588 | 0.0095149 | 0.061637 | -66.7381 | 0.038035 | -66.7323 | 56.2427 | 56.1197 | 56.2939 | -66.8284 | -66.7474 | 0.03241 | -66.7727 | 56.1482 | 56.3214 | 56.1048 | -67.0561 | -0.058947 | -0.043939 | 0.031297 | 0.037139 | 0.096086 | -0.16696 | 0.007326 | -0.28668 | -0.13844 | 0.022024 | -0.003323 | 0.28336 | 0.034739 | -0.18183 | 123.0121 | 122.8891 | 123.0634 | 66.8074 | -123.115 | 122.9176 | 123.0908 | 122.8742 | 66.8018 | -123.3427
446.7969 | 123.1659 | -66.7419 | 56.2683 | 0.0018314 | -0.004562 | 0.00082041 | 0.056865 | -0.0014123 | 0.062796 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060375 | 0.0095149 | 0.061637 | -66.7381 | 0.028878 | -66.7231 | 56.2427 | 56.1197 | 56.3031 | -66.8329 | -66.7382 | 0.036989 | -66.7682 | 56.1528 | 56.3168 | 56.1002 | -67.0515 | -0.090992 | -0.025629 | 0.003831 | 0.01883 | 0.10982 | -0.14865 | 0.034793 | -0.30957 | -0.11555 | 0.003716 | -0.026211 | 0.28336 | 0.048471 | -0.1681 | 122.9846 | 122.8616 | 123.045 | 66.7708 | -123.1012 | 122.8947 | 123.0587 | 122.8422 | 66.7789 | -123.3198
447.7969 | 123.1842 | -66.7648 | 56.2866 | 0.0018314 | -0.0043482 | 0.0010342 | 0.057079 | -0.0016259 | 0.063223 | -0.017016 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0095149 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2473 | 56.1242 | 56.2985 | -66.8329 | -66.7474 | 0.036989 | -66.7727 | 56.1482 | 56.3122 | 56.059 | -67.0515 | -0.068103 | -0.039361 | 0.031298 | 0.03714 | 0.10524 | -0.16238 | 0.011905 | -0.28668 | -0.13844 | 0.017447 | -0.0079 | 0.27878 | 0.025582 | -0.22762 | 123.0121 | 122.8891 | 123.0634 | 66.8029 | -123.1196 | 122.913 | 123.077 | 122.8238 | 66.8018 | -123.3381
448.7969 | 123.1613 | -66.7694 | 56.2958 | 0.0094624 | -0.0047756 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060588 | 0.0095149 | 0.062064 | -66.7335 | 0.033457 | -66.7277 | 56.2427 | 56.1151 | 56.2939 | -66.8421 | -66.7428 | 0.027831 | -66.7727 | 56.1482 | 56.3168 | 56.1689 | -67.0469 | -0.072684 | -0.053094 | 0.035875 | 0.041717 | 0.1144 | -0.1807 | -0.001829 | -0.27752 | -0.14759 | 0.026603 | -0.003323 | 0.2742 | 0.021006 | -0.12689 | 123.0121 | 122.8845 | 123.0634 | 66.8029 | -123.1379 | 122.9176 | 123.0862 | 122.9383 | 66.7972 | -123.3427
449.7969 | 123.1659 | -66.7236 | 56.2958 | -0.013431 | -0.0047756 | 0.00060681 | 0.056652 | -0.0014123 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0097285 | 0.062064 | -66.7335 | 0.028878 | -66.7277 | 56.2427 | 56.1105 | 56.2939 | -66.8421 | -66.7428 | 0.036989 | -66.7636 | 56.1482 | 56.3122 | 56.178 | -67.0515 | -0.11846 | -0.053094 | -0.009901 | -0.004059 | 0.1144 | -0.18528 | -0.001829 | -0.32788 | -0.14759 | -0.019173 | -0.039942 | 0.28793 | 0.016427 | -0.11773 | 122.9663 | 122.8341 | 123.0176 | 66.7525 | -123.1379 | 122.8718 | 123.0358 | 122.9017 | 66.7606 | -123.3473
450.7969 | 123.0881 | -66.7603 | 56.3187 | 0.0018314 | -0.0041346 | 0.0010342 | 0.057079 | -0.0011987 | 0.063223 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.0090875 | 0.062064 | -66.7335 | 0.033457 | -66.7323 | 56.2518 | 56.1105 | 56.2939 | -66.8238 | -66.7474 | 0.03241 | -66.7727 | 56.1528 | 56.3259 | 56.1872 | -67.0515 | -0.063523 | -0.066826 | 0.02672 | 0.027984 | 0.091507 | -0.20817 | -0.024718 | -0.29126 | -0.16591 | 0.012869 | -0.012478 | 0.27878 | 0.007274 | -0.13146 | 123.0121 | 122.8708 | 123.0542 | 66.7937 | -123.1424 | 122.913 | 123.0862 | 122.9475 | 66.7927 | -123.3702
451.7969 | 123.2117 | -66.7419 | 56.3004 | 0.0094624 | -0.0043482 | 0.00082041 | 0.057079 | -0.0014123 | 0.063223 | 0.0058755 | 0.00025007 | 0.00046581 | 0.060588 | 0.0095149 | 0.06185 | -66.7381 | 0.038035 | -66.7323 | 56.2473 | 56.1151 | 56.2939 | -66.8329 | -66.7474 | 0.03241 | -66.7682 | 56.1528 | 56.3214 | 56.1918 | -67.0515 | -0.090992 | -0.053094 | 0.003831 | 0.009673 | 0.10067 | -0.18527 | -0.006407 | -0.30957 | -0.14759 | -0.005442 | -0.026211 | 0.28336 | 0.021006 | -0.10857 | 122.9892 | 122.857 | 123.0359 | 66.78 | -123.1333 | 122.8947 | 123.0633 | 122.9337 | 66.7744 | -123.3519
452.7969 | 123.1522 | -66.7694 | 56.2912 | 0.0018314 | -0.0041346 | 0.00082041 | 0.056865 | -0.0014123 | 0.063009 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060375 | 0.0093013 | 0.061637 | -66.7473 | 0.0243 | -66.7231 | 56.2427 | 56.1105 | 56.2939 | -66.8284 | -66.7428 | 0.036989 | -66.7682 | 56.1528 | 56.3214 | 56.1552 | -67.0561 | -0.058947 | -0.048517 | 0.02214 | 0.046296 | 0.10524 | -0.1807 | 0.002748 | -0.28668 | -0.13844 | 0.026603 | 0.001255 | 0.28794 | 0.030161 | -0.13605 | 123.0121 | 122.8799 | 123.0634 | 66.7937 | -123.1196 | 122.9222 | 123.0908 | 122.9246 | 66.8064 | -123.3473
453.7969 | 123.1934 | -66.7191 | 56.3049 | 0.0094624 | -0.0043482 | 0.00082041 | 0.056865 | -0.0011987 | 0.062796 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060375 | 0.0095149 | 0.06185 | -66.7381 | 0.033457 | -66.7368 | 56.2473 | 56.1151 | 56.2939 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3122 | 56.1826 | -67.0469 | -0.11388 | -0.057672 | -0.019057 | -0.017793 | 0.096087 | -0.18985 | -0.010985 | -0.32788 | -0.15675 | -0.023751 | -0.04452 | 0.28336 | 0.007271 | -0.12231 | 122.9663 | 122.8341 | 123.013 | 66.7525 | -123.1379 | 122.8672 | 123.0313 | 122.9017 | 66.7515 | -123.3519
454.7969 | 123.143 | -66.7603 | 56.2958 | -0.0057996 | -0.0047756 | 0.0010342 | 0.057079 | -0.0016259 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.0095149 | 0.06185 | -66.7335 | 0.033457 | -66.7323 | 56.2427 | 56.1105 | 56.2939 | -66.8329 | -66.7474 | 0.03241 | -66.7727 | 56.1528 | 56.3214 | 56.1964 | -67.0469 | -0.072681 | -0.053094 | 0.02672 | 0.027984 | 0.10067 | -0.18528 | -0.001829 | -0.28668 | -0.14302 | 0.012869 | -0.012478 | 0.2742 | 0.025584 | -0.099415 | 123.0029 | 122.8708 | 123.0542 | 66.7937 | -123.1287 | 122.913 | 123.0816 | 122.9566 | 66.7927 | -123.3427
455.7969 | 123.1705 | -66.7557 | 56.3187 | -0.0057996 | -0.004562 | 0.0010342 | 0.056865 | -0.0016259 | 0.062796 | -0.001755 | -0.00017733 | 0.00046581 | 0.060375 | 0.0099423 | 0.06185 | -66.7381 | 0.038035 | -66.7277 | 56.2473 | 56.1288 | 56.2939 | -66.8329 | -66.7474 | 0.023253 | -66.7682 | 56.1482 | 56.3259 | 56.1964 | -67.0515 | -0.077259 | -0.071405 | 0.017564 | 0.027984 | 0.10524 | -0.18985 | -0.024718 | -0.29583 | -0.17048 | 0.008291 | -0.012478 | 0.28336 | 0.007274 | -0.1223 | 123.0029 | 122.8845 | 123.0496 | 66.7937 | -123.1516 | 122.9039 | 123.0816 | 122.952 | 66.7789 | -123.3702
456.7969 | 123.1613 | -66.7786 | 56.3049 | -0.013431 | -0.0043482 | 0.00060681 | 0.057079 | -0.0014123 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.0095149 | 0.06185 | -66.7335 | 0.033457 | -66.7368 | 56.2381 | 56.1151 | 56.2939 | -66.8238 | -66.7382 | 0.03241 | -66.7636 | 56.1436 | 56.3259 | 56.2009 | -67.0515 | -0.045213 | -0.066828 | 0.04503 | 0.041716 | 0.086929 | -0.18985 | -0.010985 | -0.27295 | -0.16133 | 0.040337 | 0.014989 | 0.28793 | 0.021007 | -0.10399 | 123.0167 | 122.8936 | 123.0725 | 66.812 | -123.1287 | 122.9222 | 123.1045 | 122.9795 | 66.811 | -123.3564
457.7969 | 123.1979 | -66.7328 | 56.2866 | -0.0057996 | -0.004562 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.0095149 | 0.061637 | -66.7381 | 0.038035 | -66.7368 | 56.2427 | 56.1197 | 56.2985 | -66.8329 | -66.7474 | 0.027831 | -66.7636 | 56.1528 | 56.3214 | 56.1323 | -67.0561 | -0.10015 | -0.043939 | -0.005324 | -0.00406 | 0.096087 | -0.16696 | 0.011905 | -0.3233 | -0.13386 | -0.014597 | -0.030787 | 0.29251 | 0.034739 | -0.15436 | 122.9755 | 122.8524 | 123.0313 | 66.7708 | -123.1196 | 122.8855 | 123.0541 | 122.865 | 66.7606 | -123.3427
458.7969 | 123.1659 | -66.7648 | 56.2866 | 0.0018314 | -0.0043482 | 0.00082041 | 0.056652 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00025221 | 0.060375 | 0.0097285 | 0.061423 | -66.7335 | 0.028878 | -66.7277 | 56.2335 | 56.1105 | 56.2985 | -66.8329 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3168 | 56.1918 | -67.0469 | -0.068103 | -0.053096 | 0.031298 | 0.03714 | 0.10524 | -0.17612 | 0.011905 | -0.2821 | -0.13844 | 0.026605 | -0.003322 | 0.27878 | 0.030161 | -0.094839 | 122.9984 | 122.8753 | 123.0634 | 66.7937 | -123.1196 | 122.913 | 123.0816 | 122.9566 | 66.7972 | -123.3336
459.7969 | 123.1659 | -66.7511 | 56.2912 | 0.0018314 | -0.0047756 | 0.00082041 | 0.057079 | -0.0014123 | 0.063009 | 0.013506 | -0.00039093 | 0.00025221 | 0.060375 | 0.0095149 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2473 | 56.1105 | 56.3031 | -66.8421 | -66.7428 | 0.036989 | -66.7636 | 56.1482 | 56.3214 | 56.2009 | -67.0515 | -0.090994 | -0.043939 | 0.017565 | 0.023407 | 0.1144 | -0.1807 | 0.011905 | -0.30041 | -0.14302 | 0.008293 | -0.012476 | 0.28793 | 0.030161 | -0.09026 | 122.9984 | 122.8616 | 123.0542 | 66.7891 | -123.1333 | 122.8993 | 123.0725 | 122.952 | 66.7881 | -123.3427
460.7969 | 123.1796 | -66.7877 | 56.2912 | 0.0018314 | -0.0043482 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.0097285 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2427 | 56.1197 | 56.2985 | -66.8284 | -66.7428 | 0.03241 | -66.7682 | 56.1436 | 56.3214 | 56.1964 | -67.0561 | -0.040636 | -0.048517 | 0.054186 | 0.060028 | 0.10066 | -0.17154 | 0.007327 | -0.26837 | -0.1476 | 0.044914 | 0.019566 | 0.28794 | 0.030161 | -0.094838 | 123.0304 | 122.9074 | 123.0862 | 66.8258 | -123.1196 | 122.9313 | 123.1091 | 122.9841 | 66.8201 | -123.3473
461.7969 | 123.1567 | -66.7511 | 56.3141 | -0.0057996 | -0.004562 | 0.00039321 | 0.057079 | -0.0014123 | 0.062796 | -0.001755 | -0.00017733 | 0.00046581 | 0.060161 | 0.0095149 | 0.061423 | -66.7381 | 0.038035 | -66.7277 | 56.2518 | 56.1197 | 56.2939 | -66.8375 | -66.7428 | 0.03241 | -66.7682 | 56.1528 | 56.3214 | 56.1368 | -67.0561 | -0.086415 | -0.062248 | 0.012987 | 0.023407 | 0.10982 | -0.19443 | -0.02014 | -0.30499 | -0.16133 | 0.008293 | -0.017055 | 0.28794 | 0.007273 | -0.17725 | 123.0029 | 122.8708 | 123.045 | 66.7891 | -123.1516 | 122.9039 | 123.0725 | 122.8879 | 66.7835 | -123.3702
462.7969 | 123.2071 | -66.7191 | 56.2225 | -0.0057996 | -0.004562 | 0.00082041 | 0.057079 | -0.0016259 | 0.063009 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.0097285 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2427 | 56.1151 | 56.2848 | -66.8375 | -66.752 | 0.03241 | -66.7682 | 56.1528 | 56.3168 | 56.1826 | -67.0515 | -0.11846 | 0.020148 | -0.014479 | -0.008637 | 0.10982 | -0.10746 | 0.062256 | -0.33245 | -0.069774 | -0.032908 | -0.049099 | 0.28336 | 0.094248 | -0.039909 | 122.9617 | 122.8341 | 123.0038 | 66.7571 | -123.06 | 122.8718 | 123.0358 | 122.9017 | 66.7515 | -123.274
463.7969 | 123.175 | -66.7374 | 56.3232 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056652 | -0.0016259 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.0097285 | 0.06185 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1197 | 56.2939 | -66.8421 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.2009 | -67.0561 | -0.10473 | -0.085138 | 0.00841 | 0.009674 | 0.1144 | -0.20358 | -0.029295 | -0.31872 | -0.17506 | -0.00544 | -0.026209 | 0.29251 | -0.00646 | -0.1223 | 122.9755 | 122.857 | 123.0313 | 66.7708 | -123.1653 | 122.8855 | 123.0541 | 122.9383 | 66.7698 | -123.3793
464.7969 | 123.1522 | -66.7648 | 56.2958 | -0.013431 | -0.004562 | 0.00082041 | 0.057293 | -0.0016259 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0095149 | 0.06185 | -66.7335 | 0.033457 | -66.7277 | 56.2427 | 56.1151 | 56.2939 | -66.8329 | -66.7291 | 0.027831 | -66.7636 | 56.1528 | 56.3122 | 56.1918 | -67.0515 | -0.068103 | -0.053094 | 0.031298 | 0.03714 | 0.10524 | -0.1807 | -0.001829 | -0.28668 | -0.14302 | 0.035762 | 0.001257 | 0.28793 | 0.016427 | -0.10399 | 123.0075 | 122.8799 | 123.0588 | 66.7983 | -123.1287 | 122.9176 | 123.077 | 122.9566 | 66.7927 | -123.3473
465.7969 | 123.1567 | -66.7465 | 56.2958 | 0.0094624 | -0.0047756 | 0.0012478 | 0.056865 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0093013 | 0.061423 | -66.7381 | 0.028878 | -66.7231 | 56.2381 | 56.1197 | 56.2985 | -66.8375 | -66.7428 | 0.036989 | -66.7636 | 56.1528 | 56.3168 | 56.1552 | -67.0515 | -0.090993 | -0.057672 | 0.008409 | 0.023408 | 0.1144 | -0.17612 | 0.00275 | -0.30499 | -0.14302 | 0.003715 | -0.017054 | 0.28793 | 0.021006 | -0.14062 | 122.9846 | 122.8662 | 123.045 | 66.7754 | -123.1333 | 122.8993 | 123.0633 | 122.9017 | 66.7835 | -123.3473
466.7969 | 123.143 | -66.7648 | 56.3232 | -0.013431 | -0.004562 | 0.00082041 | 0.057079 | -0.0016259 | 0.062582 | -0.017016 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0097285 | 0.061423 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.1197 | 56.2985 | -66.8284 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3168 | 56.1918 | -67.0515 | -0.063524 | -0.085138 | 0.031298 | 0.03714 | 0.10066 | -0.20358 | -0.024716 | -0.28668 | -0.17506 | 0.026605 | -0.003322 | 0.28336 | -0.00646 | -0.13146 | 123.0029 | 122.8845 | 123.0634 | 66.7983 | -123.1516 | 122.913 | 123.0816 | 122.9566 | 66.7972 | -123.3748
467.7969 | 123.2162 | -66.7328 | 56.3232 | -0.0057996 | -0.0049892 | 0.00082041 | 0.056652 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.0097285 | 0.061637 | -66.7335 | 0.038035 | -66.7277 | 56.2381 | 56.1242 | 56.2939 | -66.8284 | -66.7474 | 0.03241 | -66.7636 | 56.1436 | 56.3168 | 56.1552 | -67.0561 | -0.095568 | -0.085138 | -0.000746 | 0.005096 | 0.10066 | -0.199 | -0.029295 | -0.3233 | -0.17964 | -0.014597 | -0.030787 | 0.29251 | -0.00646 | -0.16809 | 122.9709 | 122.857 | 123.0267 | 66.7708 | -123.1516 | 122.8764 | 123.0496 | 122.8879 | 66.7652 | -123.3793
468.7969 | 123.1613 | -66.7374 | 56.2866 | -0.0057996 | -0.0047756 | 0.00082041 | 0.056652 | -0.0011987 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.0097285 | 0.061637 | -66.7381 | 0.033457 | -66.7277 | 56.2427 | 56.1105 | 56.2939 | -66.8375 | -66.7382 | 0.023253 | -66.7636 | 56.1528 | 56.3214 | 56.146 | -67.0561 | -0.10015 | -0.043939 | -0.000746 | 0.009674 | 0.10982 | -0.17612 | 0.007326 | -0.31872 | -0.13386 | -0.000861 | -0.026209 | 0.29251 | 0.034739 | -0.14062 | 122.98 | 122.8479 | 123.0313 | 66.7708 | -123.1241 | 122.8901 | 123.0587 | 122.8834 | 66.7606 | -123.3427
469.7969 | 123.1979 | -66.7328 | 56.3187 | 0.0018314 | -0.004562 | 0.0010342 | 0.057293 | -0.0014123 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.0099423 | 0.061423 | -66.729 | 0.028878 | -66.7277 | 56.2427 | 56.1288 | 56.3031 | -66.8421 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.1918 | -67.0469 | -0.10931 | -0.075983 | 0.003832 | 0.005096 | 0.1144 | -0.18985 | -0.015561 | -0.31414 | -0.17048 | -0.010018 | -0.030787 | 0.28336 | -0.001883 | -0.12688 | 122.9755 | 122.8616 | 123.0359 | 66.7617 | -123.1608 | 122.881 | 123.0496 | 122.9246 | 66.7652 | -123.3656
470.7969 | 123.1888 | -66.7282 | 56.2866 | 0.0018314 | -0.0043482 | 0.00082041 | 0.056865 | -0.0016259 | 0.063009 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.0097285 | 0.061637 | -66.729 | 0.038035 | -66.7185 | 56.2427 | 56.1197 | 56.2939 | -66.8284 | -66.7428 | 0.03241 | -66.7682 | 56.1528 | 56.3214 | 56.1918 | -67.0561 | -0.10015 | -0.043939 | -0.000746 | 0.009675 | 0.10982 | -0.16696 | 0.007326 | -0.32788 | -0.13386 | -0.014596 | -0.039944 | 0.28794 | 0.034739 | -0.094839 | 122.9709 | 122.8479 | 123.0222 | 66.7662 | -123.115 | 122.881 | 123.0496 | 122.92 | 66.7606 | -123.3427
471.7969 | 123.2025 | -66.7282 | 56.2912 | 0.0018314 | -0.004562 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.0099423 | 0.061423 | -66.729 | 0.038035 | -66.7231 | 56.2381 | 56.1105 | 56.3031 | -66.8375 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3259 | 56.1918 | -67.0469 | -0.1093 | -0.053095 | -0.000746 | 0.005097 | 0.1144 | -0.1807 | 0.011905 | -0.31872 | -0.14302 | -0.014596 | -0.035365 | 0.28336 | 0.03474 | -0.099417 | 122.9663 | 122.8387 | 123.0313 | 66.7662 | -123.1287 | 122.8764 | 123.0541 | 122.92 | 66.7606 | -123.3381
472.7969 | 123.1705 | -66.7557 | 56.2866 | -0.0057996 | -0.0043482 | 0.0010342 | 0.057079 | -0.0014123 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060161 | 0.0097285 | 0.061637 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.1059 | 56.2985 | -66.8284 | -66.7428 | 0.023253 | -66.7636 | 56.1528 | 56.3168 | 56.1872 | -67.0561 | -0.07268 | -0.048517 | 0.022142 | 0.027984 | 0.10066 | -0.1807 | 0.011905 | -0.30041 | -0.13386 | 0.01287 | -0.007899 | 0.29251 | 0.030161 | -0.099417 | 122.9938 | 122.8616 | 123.0542 | 66.7891 | -123.115 | 122.9084 | 123.0725 | 122.9429 | 66.7789 | -123.3427
473.7969 | 123.2117 | -66.7053 | 56.2546 | -0.0057996 | -0.004562 | 0.00060681 | 0.057079 | -0.0011987 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.0097285 | 0.061637 | -66.7381 | 0.028878 | -66.7277 | 56.2427 | 56.1105 | 56.2894 | -66.8329 | -66.7428 | 0.036989 | -66.7727 | 56.1482 | 56.3214 | 56.146 | -67.0561 | -0.12761 | -0.011896 | -0.03279 | -0.02237 | 0.10524 | -0.14408 | 0.034791 | -0.35077 | -0.1064 | -0.037484 | -0.06741 | 0.28336 | 0.066782 | -0.10858 | 122.948 | 122.8158 | 122.9947 | 66.7342 | -123.0875 | 122.8535 | 123.0267 | 122.8513 | 66.7423 | -123.3107
474.7969 | 123.143 | -66.7465 | 56.3187 | -0.021062 | -0.0041346 | 0.00082041 | 0.057079 | -0.0016259 | 0.062796 | 0.0058755 | -0.00039093 | 0.00025221 | 0.059734 | 0.0099423 | 0.061423 | -66.7335 | 0.033457 | -66.7368 | 56.2381 | 56.1426 | 56.2894 | -66.8375 | -66.7428 | 0.027831 | -66.7727 | 56.1436 | 56.3168 | 56.1918 | -67.0469 | -0.090993 | -0.080561 | 0.012987 | 0.009673 | 0.10067 | -0.17611 | -0.029296 | -0.30041 | -0.17506 | 0.003715 | -0.026211 | 0.2742 | -0.001883 | -0.12688 | 122.9846 | 122.8891 | 123.0359 | 66.78 | -123.1562 | 122.8901 | 123.0633 | 122.9383 | 66.7744 | -123.3656
475.7969 | 123.1888 | -66.7282 | 56.2866 | 0.0018314 | -0.0047756 | 0.0010342 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | 0.00025007 | 0.00046581 | 0.060375 | 0.0097285 | 0.061209 | -66.7335 | 0.038035 | -66.7277 | 56.2427 | 56.1426 | 56.2985 | -66.8329 | -66.7428 | 0.027831 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0561 | -0.10473 | -0.043939 | -0.005324 | 0.000518 | 0.10524 | -0.14407 | 0.011905 | -0.32788 | -0.13844 | -0.014596 | -0.044522 | 0.28336 | 0.034739 | -0.094839 | 122.9709 | 122.8708 | 123.0267 | 66.7662 | -123.1196 | 122.8764 | 123.0496 | 122.92 | 66.756 | -123.3427
476.7969 | 123.0148 | -66.7786 | 56.25 | -0.013431 | -0.0049892 | 0.00082041 | 0.056865 | -0.0016259 | 0.063009 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060375 | 0.0099423 | 0.061209 | -66.7381 | 0.028878 | -66.7277 | 56.2381 | 56.1197 | 56.2985 | -66.8329 | -66.7428 | 0.027831 | -66.7682 | 56.1436 | 56.3168 | 56.1918 | -67.0561 | -0.054371 | -0.011896 | 0.040452 | 0.050872 | 0.10524 | -0.13034 | 0.048526 | -0.27752 | -0.1064 | 0.035758 | 0.01041 | 0.28794 | 0.066782 | -0.058218 | 123.0167 | 122.8982 | 123.0771 | 66.8074 | -123.0829 | 122.9222 | 123.0953 | 122.9703 | 66.8064 | -123.3061
477.7969 | 123.2162 | -66.7328 | 56.2958 | -0.013431 | -0.004562 | 0.0010342 | 0.056865 | -0.0016259 | 0.063009 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060375 | 0.010369 | 0.061423 | -66.7381 | 0.033457 | -66.7368 | 56.2427 | 56.1334 | 56.2939 | -66.8375 | -66.7428 | 0.036989 | -66.7682 | 56.1528 | 56.3305 | 56.1964 | -67.0607 | -0.10473 | -0.053094 | -0.005324 | -0.00406 | 0.10067 | -0.16238 | -0.001829 | -0.32788 | -0.14302 | -0.010018 | -0.035366 | 0.29251 | 0.034741 | -0.099415 | 122.9755 | 122.8662 | 123.0267 | 66.7662 | -123.1333 | 122.8855 | 123.0633 | 122.9291 | 66.7698 | -123.3564
478.7969 | 123.175 | -66.7099 | 56.2775 | 0.0018314 | -0.0041346 | 0.00060681 | 0.057079 | -0.0011987 | 0.062796 | -0.001755 | -0.00039093 | 0.00067941 | 0.060588 | 0.0093013 | 0.061637 | -66.7381 | 0.0243 | -66.7277 | 56.2427 | 56.1197 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7727 | 56.1482 | 56.3214 | 56.1918 | -67.0469 | -0.12304 | -0.034784 | -0.028212 | -0.017792 | 0.10524 | -0.15781 | 0.025638 | -0.33703 | -0.12928 | -0.028327 | -0.062832 | 0.2742 | 0.043894 | -0.085684 | 122.9526 | 122.8296 | 123.013 | 66.7342 | -123.1104 | 122.8581 | 123.0313 | 122.9017 | 66.7423 | -123.3244
479.7969 | 123.1934 | -66.7465 | 56.3232 | -0.0057996 | -0.0047756 | 0.00082041 | 0.057079 | -0.0016259 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0097285 | 0.061209 | -66.7335 | 0.033457 | -66.7277 | 56.2473 | 56.1288 | 56.2939 | -66.8375 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 56.2009 | -67.0607 | -0.090993 | -0.075982 | 0.012987 | 0.018829 | 0.10982 | -0.19443 | -0.029295 | -0.31415 | -0.17506 | 0.008294 | -0.021633 | 0.29251 | -0.001882 | -0.1223 | 122.9938 | 122.8753 | 123.0405 | 66.78 | -123.1608 | 122.8947 | 123.0679 | 122.9475 | 66.7789 | -123.3839
480.7969 | 122.937 | -66.7648 | 56.2454 | 0.0018314 | -0.004562 | 0.0010342 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060588 | 0.0099423 | 0.061423 | -66.7335 | 0.038035 | -66.7323 | 56.2381 | 56.1059 | 56.2894 | -66.8284 | -66.7428 | 0.03241 | -66.7682 | 56.1482 | 56.3168 | 56.1826 | -67.0561 | -0.063524 | -0.007318 | 0.031298 | 0.032562 | 0.096086 | -0.1395 | 0.043947 | -0.29126 | -0.09724 | 0.022026 | -0.003322 | 0.28794 | 0.07136 | -0.062797 | 123.0029 | 122.8708 | 123.0542 | 66.8029 | -123.0738 | 122.913 | 123.0816 | 122.9475 | 66.7972 | -123.3015
481.7969 | 123.2208 | -66.7191 | 56.2958 | -0.0057996 | -0.0043482 | 0.0010342 | 0.056865 | -0.0016259 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060375 | 0.0097285 | 0.061423 | -66.7427 | 0.033457 | -66.7323 | 56.2335 | 56.1105 | 56.3031 | -66.8375 | -66.7382 | 0.03241 | -66.759 | 56.1482 | 56.3214 | 56.1918 | -67.0515 | -0.11846 | -0.062251 | -0.023636 | -0.013215 | 0.10524 | -0.18528 | 0.007328 | -0.33245 | -0.14759 | -0.019172 | -0.039941 | 0.29251 | 0.025584 | -0.10399 | 122.9526 | 122.8296 | 123.0222 | 66.7525 | -123.1333 | 122.8672 | 123.0404 | 122.9108 | 66.7515 | -123.3473
482.7969 | 123.1659 | -66.7786 | 56.3095 | -0.013431 | -0.0043482 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | -0.0093855 | -0.00017733 | 0.00025221 | 0.060161 | 0.0095149 | 0.061637 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.1288 | 56.2939 | -66.8238 | -66.7474 | 0.027831 | -66.7682 | 56.1482 | 56.3259 | 56.1918 | -67.0515 | -0.045213 | -0.071405 | 0.04503 | 0.050872 | 0.096085 | -0.18069 | -0.015562 | -0.27295 | -0.16133 | 0.031179 | 0.01041 | 0.28336 | 0.01643 | -0.11773 | 123.0167 | 122.9074 | 123.0725 | 66.812 | -123.1333 | 122.9267 | 123.1045 | 122.9703 | 66.8064 | -123.361
483.7969 | 123.2483 | -66.7099 | 56.2546 | -0.0057996 | -0.004562 | 0.00082041 | 0.057079 | -0.0016259 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.0097285 | 0.061423 | -66.729 | 0.028878 | -66.7414 | 56.2381 | 56.1105 | 56.2939 | -66.8284 | -66.7382 | 0.036989 | -66.7727 | 56.1528 | 56.3214 | 56.1964 | -67.0561 | -0.11846 | -0.016474 | -0.019056 | -0.031527 | 0.086929 | -0.14408 | 0.039369 | -0.34619 | -0.10182 | -0.028327 | -0.062832 | 0.28336 | 0.066782 | -0.058217 | 122.948 | 122.8204 | 123.0038 | 66.7388 | -123.0829 | 122.8627 | 123.0313 | 122.9063 | 66.7469 | -123.3107
484.7969 | 123.1796 | -66.7328 | 56.3187 | 0.0018314 | -0.0049892 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.0099423 | 0.061637 | -66.729 | 0.033457 | -66.7323 | 56.2473 | 56.1242 | 56.2985 | -66.8329 | -66.7336 | 0.03241 | -66.7727 | 56.1482 | 56.3214 | 56.1689 | -67.0607 | -0.10015 | -0.071405 | 0.003832 | 0.000518 | 0.10067 | -0.19443 | -0.020139 | -0.32788 | -0.17048 | -0.000861 | -0.039944 | 0.28794 | 0.002695 | -0.14978 | 122.98 | 122.857 | 123.0313 | 66.7662 | -123.1516 | 122.881 | 123.0541 | 122.9017 | 66.7652 | -123.3793
485.7969 | 123.1842 | -66.7053 | 56.3049 | 0.0094624 | -0.0041346 | 0.0010342 | 0.056652 | -0.0014123 | 0.063009 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060161 | 0.010156 | 0.061637 | -66.7381 | 0.038035 | -66.7231 | 56.2427 | 56.1197 | 56.2985 | -66.8192 | -66.7336 | 0.027831 | -66.7682 | 56.1482 | 56.3168 | 56.1964 | -67.0561 | -0.11388 | -0.06225 | -0.03279 | -0.017791 | 0.096085 | -0.18527 | -0.006406 | -0.35077 | -0.15675 | -0.028327 | -0.062832 | 0.28794 | 0.01185 | -0.10857 | 122.948 | 122.825 | 123.0038 | 66.7434 | -123.1241 | 122.8535 | 123.0221 | 122.9017 | 66.7332 | -123.361
486.7969 | 123.1338 | -66.7831 | 56.2958 | 0.0018314 | -0.0047756 | 0.0012478 | 0.057079 | -0.0018397 | 0.063009 | -0.001755 | -0.00039093 | 0.00025221 | 0.060161 | 0.0099423 | 0.060996 | -66.7335 | 0.028878 | -66.7277 | 56.2427 | 56.1105 | 56.3031 | -66.8284 | -66.7428 | 0.03241 | -66.7727 | 56.1528 | 56.3122 | 56.2009 | -67.0561 | -0.045214 | -0.053094 | 0.049608 | 0.05545 | 0.10066 | -0.18528 | 0.007328 | -0.27295 | -0.14302 | 0.040336 | 0.01041 | 0.28336 | 0.016427 | -0.094837 | 123.0258 | 122.8936 | 123.0862 | 66.812 | -123.1241 | 122.9359 | 123.0953 | 122.9841 | 66.8156 | -123.3519
487.7969 | 123.2117 | -66.7328 | 56.3278 | 0.0094624 | -0.004562 | 0.00082041 | 0.056652 | -0.0016259 | 0.062796 | 0.013506 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.0099423 | 0.061209 | -66.7335 | 0.028878 | -66.7277 | 56.2335 | 56.1242 | 56.2985 | -66.8329 | -66.7382 | 0.027831 | -66.7636 | 56.1528 | 56.3168 | 56.1918 | -67.0561 | -0.10015 | -0.094295 | -0.000746 | 0.005096 | 0.10524 | -0.20358 | -0.029294 | -0.3233 | -0.17506 | -0.005439 | -0.030787 | 0.29251 | -0.011038 | -0.13604 | 122.9663 | 122.857 | 123.0313 | 66.7617 | -123.1608 | 122.8855 | 123.0496 | 122.9246 | 66.7606 | -123.3839
488.7969 | 123.2346 | -66.7236 | 56.2592 | 0.0018314 | -0.004562 | 0.00060681 | 0.057079 | -0.0016259 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0099423 | 0.061637 | -66.7381 | 0.028878 | -66.7277 | 56.2427 | 56.1105 | 56.2894 | -66.8238 | -66.7382 | 0.027831 | -66.759 | 56.1482 | 56.3214 | 56.178 | -67.0561 | -0.10014 | -0.016473 | -0.014479 | -0.004059 | 0.096085 | -0.14865 | 0.030214 | -0.33246 | -0.11097 | -0.014594 | -0.035363 | 0.29709 | 0.062205 | -0.081109 | 122.9663 | 122.8341 | 123.013 | 66.7525 | -123.0829 | 122.8718 | 123.045 | 122.9017 | 66.7515 | -123.3152
489.7969 | 123.2071 | -66.7145 | 56.3095 | 0.0018314 | -0.0047756 | 0.00082041 | 0.057079 | -0.0014123 | 0.063223 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.0097285 | 0.061209 | -66.7381 | 0.033457 | -66.7277 | 56.2473 | 56.1242 | 56.2939 | -66.8375 | -66.7336 | 0.03241 | -66.7727 | 56.1436 | 56.3168 | 56.1689 | -67.0652 | -0.12304 | -0.062249 | -0.023634 | -0.013214 | 0.10982 | -0.18527 | -0.015562 | -0.35077 | -0.16591 | -0.019171 | -0.058254 | 0.29251 | 0.007273 | -0.14062 | 122.9617 | 122.8387 | 123.0084 | 66.7479 | -123.147 | 122.8581 | 123.0313 | 122.8834 | 66.7469 | -123.3748
490.7969 | 123.143 | -66.7648 | 56.3095 | 0.0018314 | -0.004562 | 0.00082041 | 0.057079 | -0.0014123 | 0.063223 | -0.001755 | -0.00017733 | 0.00046581 | 0.060161 | 0.0097285 | 0.061423 | -66.7381 | 0.033457 | -66.7231 | 56.2518 | 56.1105 | 56.2939 | -66.8375 | -66.7428 | 0.036989 | -66.7682 | 56.1482 | 56.3214 | 56.146 | -67.0561 | -0.072682 | -0.05767 | 0.02672 | 0.041719 | 0.1144 | -0.19901 | -0.015562 | -0.29126 | -0.16133 | 0.022026 | -0.003322 | 0.28794 | 0.011851 | -0.16351 | 123.0167 | 122.8753 | 123.0588 | 66.7983 | -123.147 | 122.913 | 123.0862 | 122.9108 | 66.8018 | -123.3656
491.7969 | 123.2025 | -66.7465 | 56.3095 | -0.0057996 | -0.0049892 | 0.00060681 | 0.057506 | -0.0016259 | 0.063223 | -0.001755 | -0.00017733 | 0.00067941 | 0.060375 | 0.0099423 | 0.061637 | -66.7427 | 0.038035 | -66.7323 | 56.2427 | 56.1197 | 56.2848 | -66.8375 | -66.7336 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 56.1918 | -67.0561 | -0.090993 | -0.066827 | 0.00383 | 0.014251 | 0.10524 | -0.18985 | -0.024719 | -0.30957 | -0.16133 | 0.012872 | -0.021633 | 0.28794 | 0.011851 | -0.11773 | 122.9892 | 122.8662 | 123.0313 | 66.7846 | -123.147 | 122.8947 | 123.0679 | 122.9383 | 66.7789 | -123.3656
492.7969 | 123.1522 | -66.7603 | 56.3049 | 0.0018314 | -0.0047756 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | -0.001755 | 0.00046367 | 0.00067941 | 0.060161 | 0.010156 | 0.061637 | -66.7335 | 0.038035 | -66.7231 | 56.2381 | 56.1197 | 56.2939 | -66.8375 | -66.7382 | 0.03241 | -66.7636 | 56.1573 | 56.3168 | 56.1826 | -67.0561 | -0.07726 | -0.066828 | 0.02672 | 0.037141 | 0.1144 | -0.18527 | -0.010985 | -0.29583 | -0.14759 | 0.022027 | -0.003321 | 0.29251 | 0.01185 | -0.12231 | 122.9984 | 122.8799 | 123.0542 | 66.7983 | -123.1424 | 122.9176 | 123.077 | 122.9429 | 66.7927 | -123.361
493.7969 | 123.2346 | -66.7603 | 56.2775 | 0.0018314 | -0.0043482 | 0.00082041 | 0.057079 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.0097285 | 0.061423 | -66.7381 | 0.028878 | -66.7323 | 56.2381 | 56.1151 | 56.2939 | -66.8329 | -66.7428 | 0.027831 | -66.7636 | 56.1436 | 56.3214 | 56.1918 | -67.0607 | -0.072681 | -0.039362 | 0.022142 | 0.027984 | 0.10067 | -0.16239 | 0.016481 | -0.30041 | -0.13386 | 0.017448 | -0.003321 | 0.29709 | 0.043894 | -0.085684 | 122.9984 | 122.8753 | 123.0542 | 66.7891 | -123.1104 | 122.9039 | 123.0816 | 122.952 | 66.7881 | -123.3381
494.7969 | 123.1613 | -66.7511 | 56.2958 | -0.0057996 | -0.0047756 | 0.0010342 | 0.057079 | -0.00098494 | 0.062582 | 0.0058755 | 0.00025007 | 0.00067941 | 0.060375 | 0.0099423 | 0.061423 | -66.7198 | 0.033457 | -66.7277 | 56.2335 | 56.1151 | 56.2985 | -66.8329 | -66.7382 | 0.03241 | -66.7682 | 56.1436 | 56.3168 | 56.1964 | -67.0561 | -0.081836 | -0.062251 | 0.0313 | 0.023407 | 0.10524 | -0.1807 | 0.00275 | -0.30499 | -0.15217 | 0.012872 | -0.017055 | 0.28794 | 0.021006 | -0.099415 | 122.9846 | 122.8662 | 123.0496 | 66.7846 | -123.1287 | 122.8947 | 123.0679 | 122.9475 | 66.7835 | -123.3519
495.7969 | 123.1888 | -66.7191 | 56.3232 | -0.013431 | -0.0049892 | 0.0012478 | 0.057079 | -0.0018397 | 0.063009 | 0.013506 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0097285 | 0.061209 | -66.7381 | 0.033457 | -66.7231 | 56.2473 | 56.1105 | 56.2985 | -66.8329 | -66.7382 | 0.023253 | -66.7636 | 56.1528 | 56.3214 | 56.1918 | -67.0561 | -0.11388 | -0.075982 | -0.019057 | -0.004058 | 0.10982 | -0.21274 | -0.024716 | -0.33703 | -0.17048 | -0.019172 | -0.04452 | 0.29251 | -0.001882 | -0.13146 | 122.9663 | 122.8296 | 123.0176 | 66.7525 | -123.1562 | 122.8718 | 123.0404 | 122.9108 | 66.7423 | -123.3793
496.7969 | 123.2758 | -66.7557 | 56.3004 | -0.0057996 | -0.0047756 | 0.00082041 | 0.057079 | -0.0016259 | 0.063009 | -0.001755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010156 | 0.061209 | -66.7335 | 0.033457 | -66.7323 | 56.2473 | 56.1105 | 56.2894 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1573 | 56.3168 | 56.1552 | -67.0561 | -0.077259 | -0.053094 | 0.022142 | 0.023406 | 0.10067 | -0.18985 | -0.010985 | -0.30041 | -0.14301 | 0.017449 | -0.007899 | 0.29251 | 0.016428 | -0.1452 | 123.0029 | 122.8662 | 123.045 | 66.7891 | -123.1333 | 122.913 | 123.0725 | 122.9108 | 66.7881 | -123.3564
497.7969 | 123.2025 | -66.7099 | 56.3049 | -0.0057996 | -0.0043482 | 0.00082041 | 0.057079 | -0.0016259 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060588 | 0.0099423 | 0.061423 | -66.7335 | 0.038035 | -66.7277 | 56.2381 | 56.1197 | 56.3031 | -66.8329 | -66.7336 | 0.03241 | -66.7682 | 56.1436 | 56.3122 | 56.1918 | -67.0515 | -0.12304 | -0.066828 | -0.023634 | -0.017792 | 0.10524 | -0.18527 | -0.001828 | -0.34161 | -0.16133 | -0.023749 | -0.058254 | 0.28336 | 0.007271 | -0.11315 | 122.948 | 122.8296 | 123.013 | 66.7479 | -123.1379 | 122.8535 | 123.0221 | 122.9017 | 66.7423 | -123.3564
498.7969 | 123.1338 | -66.7557 | 56.3095 | 0.0018314 | -0.0047756 | 0.00039321 | 0.056865 | -0.0018397 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.010156 | 0.061423 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.1197 | 56.2894 | -66.8329 | -66.7382 | 0.03241 | -66.7682 | 56.1528 | 56.3168 | 56.0911 | -67.0561 | -0.077259 | -0.071405 | 0.022142 | 0.027984 | 0.10524 | -0.18985 | -0.02014 | -0.30041 | -0.15675 | 0.017449 | -0.012478 | 0.28794 | 0.007273 | -0.21846 | 122.9938 | 122.8753 | 123.045 | 66.7891 | -123.1424 | 122.9084 | 123.0725 | 122.8467 | 66.7881 | -123.3656
499.7969 | 123.2025 | -66.7236 | 56.2775 | -0.0057996 | -0.005203 | 0.00082041 | 0.056865 | -0.0014123 | 0.062582 | -0.001755 | -0.00039093 | 0.00046581 | 0.060375 | 0.0099423 | 0.061423 | -66.729 | 0.038035 | -66.7368 | 56.2473 | 56.1197 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7544 | 56.1482 | 56.3168 | 56.1185 | -67.0561 | -0.1093 | -0.030206 | -0.005323 | -0.013215 | 0.096087 | -0.15781 | 0.025638 | -0.33246 | -0.12928 | -0.014594 | -0.030785 | 0.30167 | 0.039316 | -0.15894 | 122.9709 | 122.8433 | 123.0267 | 66.7617 | -123.1104 | 122.8718 | 123.0404 | 122.8422 | 66.756 | -123.3336
500.7969 | 123.143 | -66.7557 | 56.2958 | 0.0018314 | -0.0047756 | 0.00060681 | 0.057079 | -0.0018397 | 0.063009 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060161 | 0.010156 | 0.061637 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1151 | 56.3031 | -66.8284 | -66.7474 | 0.03241 | -66.7682 | 56.1436 | 56.3259 | 56.1048 | -67.0561 | -0.07268 | -0.057672 | 0.02672 | 0.027984 | 0.10066 | -0.1807 | 0.007328 | -0.30041 | -0.15217 | 0.008291 | -0.012478 | 0.28794 | 0.030163 | -0.19099 | 122.9938 | 122.8708 | 123.0588 | 66.7891 | -123.1241 | 122.8993 | 123.0816 | 122.8605 | 66.7881 | -123.3519
501.7969 | 123.2071 | -66.7053 | 56.3049 | 0.0018314 | -0.0049892 | 0.00082041 | 0.057079 | -0.0014123 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.0097285 | 0.060996 | -66.7335 | 0.033457 | -66.7323 | 56.2473 | 56.1197 | 56.2985 | -66.8467 | -66.7428 | 0.027831 | -66.759 | 56.1436 | 56.3168 | 56.1185 | -67.0607 | -0.14135 | -0.057672 | -0.028212 | -0.026948 | 0.1144 | -0.18527 | -0.006406 | -0.35535 | -0.16133 | -0.037484 | -0.053674 | 0.30167 | 0.01185 | -0.18641 | 122.9526 | 122.825 | 123.0038 | 66.7388 | -123.1516 | 122.8489 | 123.0221 | 122.8238 | 66.7332 | -123.3656
502.7969 | 123.1567 | -66.7374 | 56.3187 | -0.0057996 | -0.0047756 | 0.00082041 | 0.056865 | -0.0018397 | 0.062582 | 0.0058755 | -0.00017733 | 0.00089321 | 0.060375 | 0.0099423 | 0.061637 | -66.7335 | 0.028878 | -66.7277 | 56.2381 | 56.1105 | 56.2985 | -66.8329 | -66.7428 | 0.046146 | -66.7682 | 56.1528 | 56.3122 | 56.0727 | -67.0607 | -0.095569 | -0.080561 | 0.003832 | 0.009674 | 0.10524 | -0.20817 | -0.020139 | -0.3233 | -0.16591 | -0.00544 | -0.030788 | 0.29251 | -0.006462 | -0.24593 | 122.9755 | 122.8479 | 123.0359 | 66.7662 | -123.1516 | 122.8901 | 123.0496 | 122.8101 | 66.7835 | -123.3793
503.7969 | 123.2071 | -66.7145 | 56.2912 | -0.0057996 | -0.0049892 | 0.0010342 | 0.056865 | -0.0016259 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.010156 | 0.061423 | -66.7427 | 0.033457 | -66.7368 | 56.2427 | 56.1151 | 56.2985 | -66.8375 | -66.7382 | 0.036989 | -66.7682 | 56.1482 | 56.3168 | 56.1185 | -67.0561 | -0.12304 | -0.048517 | -0.028213 | -0.02237 | 0.10067 | -0.17612 | 0.007327 | -0.34161 | -0.14302 | -0.023749 | -0.053676 | 0.28794 | 0.025583 | -0.17267 | 122.9572 | 122.8296 | 123.013 | 66.7479 | -123.1287 | 122.8627 | 123.0313 | 122.833 | 66.7515 | -123.3473
504.7969 | 123.0194 | -66.7877 | 56.2683 | 0.0018314 | -0.005203 | 0.00082041 | 0.056865 | -0.0016259 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.010156 | 0.061209 | -66.729 | 0.038035 | -66.7323 | 56.2427 | 56.1151 | 56.2985 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1436 | 56.3168 | 56.1185 | -67.0652 | -0.040636 | -0.025629 | 0.058764 | 0.05545 | 0.096086 | -0.15323 | 0.030215 | -0.27753 | -0.12471 | 0.049493 | 0.024145 | 0.30167 | 0.048471 | -0.14979 | 123.0304 | 122.9028 | 123.0862 | 66.8258 | -123.0967 | 122.9313 | 123.1045 | 122.9062 | 66.8247 | -123.3336
505.7969 | 123.2025 | -66.7282 | 56.2958 | -0.013431 | -0.0047756 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | 0.00025007 | 0.00067941 | 0.060375 | 0.0099423 | 0.061209 | -66.7381 | 0.028878 | -66.7323 | 56.2381 | 56.1197 | 56.3031 | -66.8375 | -66.7382 | 0.027831 | -66.7682 | 56.1573 | 56.3259 | 56.1231 | -67.0469 | -0.1093 | -0.057672 | -0.009902 | -0.00406 | 0.10524 | -0.17612 | 0.007328 | -0.31872 | -0.13844 | -0.010017 | -0.039944 | 0.27878 | 0.030163 | -0.17267 | 122.9663 | 122.8479 | 123.0313 | 66.7571 | -123.1333 | 122.8855 | 123.0541 | 122.8513 | 66.756 | -123.3427
506.7969 | 123.1522 | -66.7557 | 56.3141 | 0.0018314 | -0.0049892 | 0.00082041 | 0.057293 | -0.0014123 | 0.062796 | -0.001755 | -0.00039093 | 0.00046581 | 0.060375 | 0.010156 | 0.061423 | -66.7335 | 0.028878 | -66.7323 | 56.2381 | 56.1151 | 56.2939 | -66.8284 | -66.7382 | 0.036989 | -66.7727 | 56.1528 | 56.3168 | 56.1872 | -67.0607 | -0.07268 | -0.075983 | 0.022142 | 0.023406 | 0.096086 | -0.19901 | -0.02014 | -0.30499 | -0.16133 | 0.017449 | -0.017056 | 0.28794 | 0.002695 | -0.12688 | 122.9938 | 122.8708 | 123.0496 | 66.7846 | -123.1424 | 122.9084 | 123.0725 | 122.9429 | 66.7927 | -123.3748
507.7969 | 123.1705 | -66.7419 | 56.3324 | -0.0057996 | -0.004562 | 0.0010342 | 0.057079 | -0.0014123 | 0.063009 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010583 | 0.061209 | -66.7381 | 0.033457 | -66.7323 | 56.2427 | 56.1197 | 56.2939 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3122 | 56.1872 | -67.0561 | -0.090992 | -0.089715 | 0.003831 | 0.009673 | 0.10067 | -0.21274 | -0.03845 | -0.31415 | -0.18422 | 0.003716 | -0.021632 | 0.29251 | -0.020194 | -0.14519 | 122.9846 | 122.8616 | 123.0359 | 66.7754 | -123.1653 | 122.8901 | 123.0541 | 122.9291 | 66.7744 | -123.3885
508.7969 | 123.1705 | -66.7465 | 56.2958 | -0.013431 | -0.0047756 | 0.00082041 | 0.057079 | -0.0018397 | 0.063009 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060161 | 0.0099423 | 0.061209 | -66.7244 | 0.028878 | -66.7323 | 56.2427 | 56.1151 | 56.3031 | -66.8329 | -66.7428 | 0.027831 | -66.7636 | 56.1482 | 56.3305 | 56.1826 | -67.0561 | -0.086414 | -0.053094 | 0.022144 | 0.014251 | 0.10067 | -0.1807 | 0.007328 | -0.30957 | -0.14759 | 0.003715 | -0.017054 | 0.29251 | 0.034741 | -0.11315 | 122.9892 | 122.8616 | 123.0496 | 66.7754 | -123.1287 | 122.8947 | 123.077 | 122.9291 | 66.7744 | -123.3519
509.7969 | 123.1201 | -66.7374 | 56.3049 | 0.0018314 | -0.0049892 | 0.00082041 | 0.057079 | -0.0014123 | 0.062582 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010156 | 0.060996 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1151 | 56.2985 | -66.8238 | -66.7474 | 0.036989 | -66.759 | 56.1482 | 56.3214 | 56.1552 | -67.0561 | -0.086411 | -0.066828 | 0.00841 | 0.009674 | 0.096085 | -0.18985 | -0.006406 | -0.31872 | -0.15675 | -0.010019 | -0.02163 | 0.29709 | 0.016428 | -0.14978 | 122.9755 | 122.8524 | 123.0359 | 66.7708 | -123.1287 | 122.8855 | 123.0587 | 122.8925 | 66.7744 | -123.361
510.7969 | 123.0652 | -66.7603 | 56.3049 | -0.013431 | -0.004562 | 0.00082041 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.010369 | 0.061209 | -66.7335 | 0.038035 | -66.7231 | 56.2381 | 56.1151 | 56.2985 | -66.8329 | -66.7291 | 0.03241 | -66.7682 | 56.1436 | 56.3214 | 56.1826 | -67.0469 | -0.072681 | -0.066828 | 0.02672 | 0.037141 | 0.10982 | -0.18985 | -0.006406 | -0.28668 | -0.16133 | 0.031184 | -0.0079 | 0.27878 | 0.016428 | -0.12231 | 122.9984 | 122.8753 | 123.0588 | 66.7983 | -123.1379 | 122.9039 | 123.0816 | 122.9429 | 66.7927 | -123.3519
511.7969 | 123.2071 | -66.7191 | 56.3004 | 0.0094624 | -0.004562 | 0.0014616 | 0.057079 | -0.0014123 | 0.063009 | -0.001755 | -0.00017733 | 0.00025221 | 0.060161 | 0.010583 | 0.061423 | -66.7335 | 0.038035 | -66.7323 | 56.2381 | 56.1151 | 56.2985 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1619 | 56.3259 | 56.1918 | -67.0607 | -0.11388 | -0.06225 | -0.014479 | -0.013215 | 0.10067 | -0.18527 | -0.001828 | -0.34161 | -0.13844 | -0.019172 | -0.04452 | 0.29709 | 0.025585 | -0.10857 | 122.9572 | 122.8341 | 123.0176 | 66.7571 | -123.1333 | 122.881 | 123.045 | 122.9108 | 66.7515 | -123.361
512.7969 | 123.1293 | -66.7694 | 56.2866 | 0.0018314 | -0.005203 | 0.0012478 | 0.056865 | -0.0014123 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.010369 | 0.061423 | -66.729 | 0.038035 | -66.7277 | 56.2473 | 56.1151 | 56.3031 | -66.8192 | -66.7336 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 56.2009 | -67.0561 | -0.049789 | -0.039361 | 0.040453 | 0.041717 | 0.091506 | -0.17154 | 0.016483 | -0.28668 | -0.13386 | 0.03576 | 0.005834 | 0.29251 | 0.034739 | -0.085682 | 123.0167 | 122.8845 | 123.0725 | 66.8074 | -123.1058 | 122.9222 | 123.0908 | 122.9703 | 66.8018 | -123.3427
513.7969 | 123.1659 | -66.7511 | 56.2958 | -0.0057996 | -0.005203 | 0.0012478 | 0.056865 | -0.0016259 | 0.063223 | -0.001755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010156 | 0.061209 | -66.7244 | 0.033457 | -66.7323 | 56.2381 | 56.1197 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 56.1826 | -67.0607 | -0.081836 | -0.057672 | 0.026722 | 0.018829 | 0.10067 | -0.17612 | 0.007328 | -0.30957 | -0.14302 | 0.012872 | -0.012476 | 0.29709 | 0.025584 | -0.11315 | 122.9892 | 122.8708 | 123.0542 | 66.7846 | -123.1287 | 122.9039 | 123.0725 | 122.9337 | 66.7835 | -123.3564
514.7969 | 123.1705 | -66.7511 | 56.3004 | -0.013431 | -0.0054166 | 0.00082041 | 0.057079 | -0.0016259 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.010156 | 0.061209 | -66.7244 | 0.028878 | -66.7277 | 56.2335 | 56.1105 | 56.2985 | -66.8421 | -66.7428 | 0.027831 | -66.7682 | 56.139 | 56.3168 | 56.1872 | -67.0561 | -0.090994 | -0.066829 | 0.026722 | 0.023407 | 0.1144 | -0.18985 | -0.001828 | -0.30499 | -0.16133 | 0.008293 | -0.017055 | 0.28794 | 0.016428 | -0.11315 | 122.9846 | 122.8616 | 123.0496 | 66.78 | -123.1424 | 122.8901 | 123.0679 | 122.9383 | 66.7789 | -123.3564
515.7969 | 123.1888 | -66.7374 | 56.3004 | -0.013431 | -0.005203 | 0.00082041 | 0.056865 | -0.0014123 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.0099423 | 0.061209 | -66.729 | 0.028878 | -66.7277 | 56.2381 | 56.1242 | 56.3031 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.139 | 56.3214 | 56.1918 | -67.0607 | -0.095569 | -0.06225 | 0.00841 | 0.009674 | 0.10524 | -0.17612 | 0.00275 | -0.3233 | -0.16133 | -0.00544 | -0.026209 | 0.29709 | 0.021006 | -0.10857 | 122.9755 | 122.8616 | 123.0405 | 66.7662 | -123.1333 | 122.8764 | 123.0587 | 122.9291 | 66.7698 | -123.361
516.7969 | 123.1613 | -66.7648 | 56.3004 | -0.0057996 | -0.0047756 | 0.00060681 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 0.00025007 | 0.00067941 | 0.059947 | 0.010369 | 0.061637 | -66.7335 | 0.033457 | -66.7323 | 56.2427 | 56.138 | 56.3077 | -66.8375 | -66.7291 | 0.03241 | -66.7636 | 56.1482 | 56.3122 | 56.1826 | -67.0515 | -0.072682 | -0.057672 | 0.031298 | 0.032562 | 0.10524 | -0.16238 | 0.007329 | -0.28668 | -0.15217 | 0.035762 | 0.001257 | 0.28793 | 0.011849 | -0.11773 | 123.0075 | 122.9028 | 123.0725 | 66.7983 | -123.1379 | 122.913 | 123.077 | 122.9475 | 66.7972 | -123.3519
517.7969 | 123.1659 | -66.7191 | 56.2912 | -0.0057996 | -0.0049892 | 0.0012478 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.010156 | 0.061423 | -66.729 | 0.038035 | -66.7323 | 56.2427 | 56.1151 | 56.3077 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1482 | 56.3214 | 56.1964 | -67.0607 | -0.1093 | -0.048517 | -0.009901 | -0.013215 | 0.096086 | -0.17612 | 0.016484 | -0.34161 | -0.14302 | -0.019172 | -0.04452 | 0.29709 | 0.030161 | -0.094838 | 122.9617 | 122.8341 | 123.0267 | 66.7571 | -123.1196 | 122.8672 | 123.0404 | 122.9154 | 66.756 | -123.3519
518.7969 | 123.1476 | -66.7694 | 56.3049 | -0.0057996 | -0.0047756 | 0.0010342 | 0.057079 | -0.0016259 | 0.062368 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060375 | 0.010369 | 0.061423 | -66.7335 | 0.038035 | -66.7185 | 56.2381 | 56.1151 | 56.3031 | -66.8329 | -66.7382 | 0.027831 | -66.7727 | 56.1344 | 56.3122 | 56.1918 | -67.0561 | -0.063526 | -0.066828 | 0.035875 | 0.050874 | 0.1144 | -0.18985 | -0.001828 | -0.28668 | -0.17049 | 0.031182 | -0.003323 | 0.28336 | 0.007271 | -0.11315 | 123.0075 | 122.8845 | 123.0725 | 66.8074 | -123.1379 | 122.9039 | 123.0816 | 122.9612 | 66.7972 | -123.361
519.7969 | 123.1888 | -66.7191 | 56.3049 | -0.021062 | -0.005203 | 0.00082041 | 0.057079 | -0.0014123 | 0.062582 | -0.0093855 | 0.00025007 | 0.00067941 | 0.060375 | 0.010583 | 0.061209 | -66.7335 | 0.038035 | -66.7277 | 56.2473 | 56.1334 | 56.2985 | -66.8329 | -66.7428 | 0.03241 | -66.759 | 56.1528 | 56.3259 | 56.1918 | -67.0561 | -0.11388 | -0.057672 | -0.014479 | -0.008637 | 0.10524 | -0.17154 | -0.006406 | -0.33703 | -0.15217 | -0.023751 | -0.039941 | 0.29709 | 0.021007 | -0.11315 | 122.9663 | 122.8525 | 123.0176 | 66.7571 | -123.1379 | 122.8718 | 123.045 | 122.9108 | 66.7515 | -123.361
520.7969 | 123.1705 | -66.7465 | 56.2683 | -0.0057996 | -0.005203 | 0.0012478 | 0.057079 | -0.0018397 | 0.063009 | -0.001755 | -0.00039093 | 0.00067941 | 0.060588 | 0.010369 | 0.061209 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1242 | 56.3031 | -66.8238 | -66.7428 | 0.036989 | -66.7636 | 56.1528 | 56.3168 | 56.1964 | -67.0652 | -0.077256 | -0.030207 | 0.017565 | 0.018829 | 0.096085 | -0.14407 | 0.034793 | -0.31873 | -0.11555 | 0.003715 | -0.017054 | 0.30167 | 0.048471 | -0.07195 | 122.9846 | 122.8708 | 123.0496 | 66.78 | -123.0921 | 122.8993 | 123.0633 | 122.9429 | 66.7835 | -123.3336
521.7969 | 123.1384 | -66.7465 | 56.2912 | -0.0057996 | -0.005203 | 0.00082041 | 0.056652 | -0.0014123 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060588 | 0.010369 | 0.061423 | -66.729 | 0.0243 | -66.7323 | 56.2381 | 56.1288 | 56.2985 | -66.8375 | -66.7382 | 0.023253 | -66.7636 | 56.1528 | 56.3214 | 56.2009 | -67.0561 | -0.090993 | -0.053095 | 0.017565 | 0.014251 | 0.10524 | -0.16238 | 0.007327 | -0.30957 | -0.13844 | 0.008294 | -0.017054 | 0.29251 | 0.030161 | -0.09026 | 122.9846 | 122.8753 | 123.045 | 66.7708 | -123.1287 | 122.8993 | 123.0679 | 122.9475 | 66.7698 | -123.3473
522.7969 | 123.1384 | -66.7557 | 56.2958 | -0.0057996 | -0.0054166 | 0.0010342 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.060588 | 0.010156 | 0.061423 | -66.7335 | 0.033457 | -66.7277 | 56.2381 | 56.1426 | 56.3031 | -66.8329 | -66.7428 | 0.03241 | -66.7682 | 56.1528 | 56.3214 | 56.1964 | -67.0607 | -0.077259 | -0.057672 | 0.022142 | 0.027984 | 0.10524 | -0.15322 | 0.007328 | -0.30499 | -0.14302 | 0.01287 | -0.012478 | 0.29251 | 0.025584 | -0.099415 | 122.9938 | 122.8982 | 123.0588 | 66.7891 | -123.1287 | 122.9084 | 123.077 | 122.952 | 66.7881 | -123.3564
523.7969 | 123.1934 | -66.7328 | 56.2912 | -0.0057996 | -0.0049892 | 0.0012478 | 0.057079 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060161 | 0.0099423 | 0.061209 | -66.7335 | 0.033457 | -66.7231 | 56.2427 | 56.1197 | 56.2985 | -66.8329 | -66.7382 | 0.036989 | -66.7682 | 56.1482 | 56.3259 | 56.1872 | -67.0561 | -0.10015 | -0.048517 | -0.000746 | 0.009675 | 0.10982 | -0.17154 | 0.007327 | -0.3233 | -0.14302 | -0.005439 | -0.035366 | 0.28794 | 0.03474 | -0.10399 | 122.9755 | 122.8524 | 123.0313 | 66.7662 | -123.1241 | 122.881 | 123.0587 | 122.92 | 66.7698 | -123.3473
524.7969 | 123.2758 | -66.7191 | 56.2729 | -0.013431 | -0.0049892 | 0.0012478 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | -0.00039093 | 0.00046581 | 0.060161 | 0.010156 | 0.061209 | -66.729 | 0.038035 | -66.7323 | 56.2381 | 56.138 | 56.3077 | -66.8284 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3305 | 56.1872 | -67.0607 | -0.1093 | -0.034784 | -0.009901 | -0.013215 | 0.096086 | -0.13491 | 0.034795 | -0.34161 | -0.12471 | -0.019172 | -0.04452 | 0.29709 | 0.057629 | -0.085684 | 122.9572 | 122.857 | 123.0267 | 66.7571 | -123.1012 | 122.8672 | 123.0496 | 122.9063 | 66.7515 | -123.3336
525.7969 | 123.1659 | -66.7557 | 56.2912 | 0.0018314 | -0.0054166 | 0.00082041 | 0.056652 | -0.0014123 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.010369 | 0.061423 | -66.7335 | 0.0243 | -66.7368 | 56.2473 | 56.138 | 56.3077 | -66.8375 | -66.7336 | 0.027831 | -66.7636 | 56.1528 | 56.3259 | 56.1964 | -67.0515 | -0.081838 | -0.043939 | 0.022142 | 0.018828 | 0.10067 | -0.15322 | 0.016484 | -0.29583 | -0.13844 | 0.022027 | -0.007899 | 0.28793 | 0.03474 | -0.094838 | 123.0029 | 122.8936 | 123.0634 | 66.78 | -123.1287 | 122.9084 | 123.0816 | 122.952 | 66.7835 | -123.3427
526.7969 | 123.1613 | -66.7419 | 56.2775 | -0.013431 | -0.005203 | 0.00082041 | 0.056865 | -0.0018397 | 0.063009 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.010156 | 0.061209 | -66.7244 | 0.038035 | -66.7277 | 56.2473 | 56.1471 | 56.2985 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1872 | -67.0561 | -0.090992 | -0.030206 | 0.017566 | 0.014251 | 0.10524 | -0.13033 | 0.02106 | -0.31415 | -0.12928 | -0.000863 | -0.021632 | 0.29251 | 0.043894 | -0.090262 | 122.9892 | 122.8891 | 123.0405 | 66.78 | -123.1104 | 122.8901 | 123.0633 | 122.9291 | 66.7744 | -123.3336
527.7969 | 123.1476 | -66.7511 | 56.3141 | -0.0057996 | -0.005203 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059947 | 0.010156 | 0.060996 | -66.7244 | 0.033457 | -66.7277 | 56.2381 | 56.1471 | 56.2985 | -66.8329 | -66.7336 | 0.036989 | -66.7636 | 56.1482 | 56.3168 | 56.1872 | -67.0561 | -0.081836 | -0.075983 | 0.026722 | 0.023407 | 0.10524 | -0.16696 | -0.015561 | -0.30499 | -0.16591 | 0.01745 | -0.012476 | 0.29251 | 0.002695 | -0.12688 | 122.9892 | 122.8982 | 123.0496 | 66.7846 | -123.147 | 122.8993 | 123.0679 | 122.9383 | 66.7881 | -123.3702
528.7969 | 123.1705 | -66.7465 | 56.2866 | 0.0018314 | -0.0054166 | 0.00082041 | 0.056438 | -0.0011987 | 0.062582 | -0.001755 | -0.00017733 | 0.00025221 | 0.060588 | 0.010369 | 0.061423 | -66.729 | 0.033457 | -66.7277 | 56.2335 | 56.1426 | 56.2985 | -66.8238 | -66.7382 | 0.03241 | -66.7727 | 56.1528 | 56.3259 | 56.178 | -67.0652 | -0.077256 | -0.053096 | 0.017565 | 0.018829 | 0.096085 | -0.14407 | 0.011905 | -0.31873 | -0.13386 | 0.008294 | -0.026211 | 0.29251 | 0.039318 | -0.10857 | 122.98 | 122.8891 | 123.045 | 66.78 | -123.1104 | 122.8993 | 123.0725 | 122.9246 | 66.7789 | -123.3519
529.7969 | 123.1888 | -66.7419 | 56.2958 | 0.0018314 | -0.005203 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | -0.00039093 | 0.00025221 | 0.059947 | 0.010156 | 0.061209 | -66.729 | 0.028878 | -66.7323 | 56.2473 | 56.1242 | 56.3031 | -66.8284 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3168 | 56.2009 | -67.0607 | -0.086413 | -0.048516 | 0.012987 | 0.009673 | 0.096086 | -0.17154 | 0.007328 | -0.31873 | -0.14759 | 0.003716 | -0.026211 | 0.29251 | 0.021006 | -0.094837 | 122.9892 | 122.8662 | 123.045 | 66.7708 | -123.1241 | 122.8901 | 123.0587 | 122.9429 | 66.7744 | -123.3564
530.7969 | 123.0835 | -66.7831 | 56.3141 | 0.0018314 | -0.0047756 | 0.0010342 | 0.056652 | -0.0018397 | 0.063009 | -0.001755 | -0.00039093 | 0.00067941 | 0.060375 | 0.010797 | 0.061423 | -66.729 | 0.038035 | -66.7368 | 56.2381 | 56.1197 | 56.3077 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.1436 | 56.3168 | 56.1872 | -67.0607 | -0.049793 | -0.075983 | 0.054186 | 0.046294 | 0.096087 | -0.19443 | -0.006404 | -0.27753 | -0.17048 | 0.040336 | 0.019567 | 0.29709 | 0.002695 | -0.12688 | 123.0212 | 122.9028 | 123.0908 | 66.8212 | -123.147 | 122.9267 | 123.0999 | 122.9703 | 66.8156 | -123.3748
531.7969 | 123.1613 | -66.7419 | 56.282 | -0.0057996 | -0.005203 | 0.00082041 | 0.056865 | -0.0018397 | 0.062796 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059947 | 0.010369 | 0.061209 | -66.7335 | 0.033457 | -66.7277 | 56.2335 | 56.1334 | 56.2985 | -66.8329 | -66.7428 | 0.03241 | -66.759 | 56.1482 | 56.3168 | 56.1826 | -67.0561 | -0.090992 | -0.048518 | 0.008409 | 0.014251 | 0.10524 | -0.14865 | 0.016483 | -0.31415 | -0.13386 | -0.000863 | -0.017053 | 0.29709 | 0.034739 | -0.099418 | 122.9755 | 122.8753 | 123.0405 | 66.7754 | -123.115 | 122.8901 | 123.0587 | 122.9246 | 66.7744 | -123.3381
532.7969 | 123.1705 | -66.7694 | 56.282 | -0.0057996 | -0.005203 | 0.00082041 | 0.056652 | -0.0016259 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00025221 | 0.060161 | 0.010156 | 0.061209 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1242 | 56.3077 | -66.8238 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1918 | -67.0515 | -0.054368 | -0.043939 | 0.040453 | 0.041717 | 0.096085 | -0.15781 | 0.02564 | -0.2821 | -0.13386 | 0.031182 | 0.005834 | 0.28793 | 0.039317 | -0.090261 | 123.0075 | 122.8936 | 123.0771 | 66.8029 | -123.1058 | 122.9176 | 123.0908 | 122.9612 | 66.8018 | -123.3336
533.7969 | 123.1705 | -66.7145 | 56.2958 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060375 | 0.010369 | 0.061209 | -66.729 | 0.033457 | -66.7323 | 56.2381 | 56.1197 | 56.2894 | -66.8329 | -66.7382 | 0.027831 | -66.7636 | 56.1436 | 56.3168 | 56.2055 | -67.0652 | -0.11846 | -0.057672 | -0.014478 | -0.017792 | 0.10067 | -0.17612 | -0.006407 | -0.35077 | -0.15217 | -0.023749 | -0.049097 | 0.30167 | 0.021006 | -0.090258 | 122.9526 | 122.8341 | 123.0038 | 66.7479 | -123.1287 | 122.8581 | 123.0313 | 122.92 | 66.7423 | -123.361
534.7969 | 123.175 | -66.7557 | 56.2958 | -0.0057996 | -0.005203 | 0.00082041 | 0.057293 | -0.0018397 | 0.062796 | -0.017016 | 0.00025007 | 0.00089321 | 0.060161 | 0.010369 | 0.061209 | -66.729 | 0.028878 | -66.7277 | 56.2381 | 56.1197 | 56.2985 | -66.8284 | -66.7336 | 0.03241 | -66.7682 | 56.1619 | 56.3168 | 56.1964 | -67.0561 | -0.07268 | -0.057672 | 0.02672 | 0.027984 | 0.10066 | -0.17612 | 0.00275 | -0.30041 | -0.13386 | 0.022027 | -0.012478 | 0.28794 | 0.021006 | -0.099415 | 122.9938 | 122.8753 | 123.0542 | 66.7846 | -123.1241 | 122.9176 | 123.0725 | 122.952 | 66.7881 | -123.3519
535.7969 | 123.1384 | -66.7328 | 56.3004 | -0.013431 | -0.005203 | 0.0010342 | 0.056865 | -0.0014123 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060161 | 0.010369 | 0.060996 | -66.7244 | 0.038035 | -66.7323 | 56.2381 | 56.1288 | 56.3077 | -66.8238 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.1506 | -67.0561 | -0.090989 | -0.06225 | 0.008411 | 0.000518 | 0.091507 | -0.17154 | 0.007329 | -0.3233 | -0.15217 | -0.010018 | -0.030787 | 0.29251 | 0.016428 | -0.14978 | 122.9709 | 122.8616 | 123.0405 | 66.7708 | -123.1241 | 122.881 | 123.0496 | 122.8834 | 66.7652 | -123.3564
536.7969 | 123.1201 | -66.7419 | 56.3004 | 0.0018314 | -0.0054166 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.0093855 | -0.00039093 | 0.00089321 | 0.060161 | 0.010583 | 0.061209 | -66.7335 | 0.028878 | -66.7368 | 56.2427 | 56.138 | 56.3031 | -66.8329 | -66.7428 | 0.027831 | -66.759 | 56.1482 | 56.3122 | 56.2009 | -67.0561 | -0.090992 | -0.057672 | 0.008409 | 0.005095 | 0.096087 | -0.16238 | 0.00275 | -0.31415 | -0.15217 | -0.000863 | -0.017053 | 0.29709 | 0.011849 | -0.099415 | 122.9846 | 122.8799 | 123.045 | 66.7708 | -123.1333 | 122.8901 | 123.0541 | 122.9429 | 66.7698 | -123.3564
537.7969 | 123.1979 | -66.7191 | 56.3049 | 0.0094624 | -0.0054166 | 0.0010342 | 0.056865 | -0.0018397 | 0.063223 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010369 | 0.061209 | -66.729 | 0.038035 | -66.7323 | 56.2473 | 56.1151 | 56.3031 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1436 | 56.3168 | 56.1964 | -67.0652 | -0.1093 | -0.057672 | -0.009901 | -0.013215 | 0.096086 | -0.18985 | -0.001828 | -0.34619 | -0.16133 | -0.019172 | -0.04452 | 0.30167 | 0.01185 | -0.10857 | 122.9663 | 122.8341 | 123.0222 | 66.7571 | -123.1333 | 122.8627 | 123.0358 | 122.9154 | 66.756 | -123.3702
538.7969 | 123.1293 | -66.7648 | 56.282 | 0.0018314 | -0.005203 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | -0.00039093 | 0.00067941 | 0.060161 | 0.010583 | 0.061423 | -66.729 | 0.033457 | -66.7323 | 56.2381 | 56.1288 | 56.3031 | -66.8284 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.1918 | -67.0561 | -0.063524 | -0.043939 | 0.035876 | 0.032562 | 0.096086 | -0.15323 | 0.021061 | -0.29126 | -0.13386 | 0.022026 | 0.001257 | 0.29251 | 0.034739 | -0.090261 | 123.0029 | 122.8936 | 123.0679 | 66.7983 | -123.1104 | 122.913 | 123.0816 | 122.9566 | 66.7972 | -123.3381
539.7969 | 123.2025 | -66.7145 | 56.3095 | -0.0057996 | -0.0056302 | 0.00082041 | 0.056652 | -0.0022669 | 0.062796 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060161 | 0.010369 | 0.061423 | -66.7335 | 0.028878 | -66.7323 | 56.2381 | 56.1151 | 56.3077 | -66.8238 | -66.7382 | 0.03241 | -66.759 | 56.1528 | 56.3259 | 56.1368 | -67.0652 | -0.1093 | -0.071405 | -0.019056 | -0.017792 | 0.091507 | -0.19443 | -0.001826 | -0.35077 | -0.15675 | -0.023749 | -0.044518 | 0.30625 | 0.01643 | -0.17267 | 122.9526 | 122.8296 | 123.0222 | 66.7434 | -123.1333 | 122.8672 | 123.0404 | 122.8513 | 66.7469 | -123.3748
540.7969 | 123.1384 | -66.7419 | 56.2866 | 0.0018314 | -0.0054166 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060161 | 0.010156 | 0.060782 | -66.729 | 0.033457 | -66.7277 | 56.2473 | 56.1563 | 56.3031 | -66.8329 | -66.7336 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 55.9995 | -67.0515 | -0.090992 | -0.039361 | 0.012987 | 0.014251 | 0.10524 | -0.13033 | 0.016483 | -0.30957 | -0.13386 | 0.008294 | -0.021632 | 0.28793 | 0.034739 | -0.28714 | 122.9892 | 122.8982 | 123.045 | 66.7754 | -123.1196 | 122.8947 | 123.0633 | 122.7414 | 66.7744 | -123.3381
541.7969 | 123.2025 | -66.7191 | 56.3095 | 0.0094624 | -0.005203 | 0.00082041 | 0.057079 | -0.0016259 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.010583 | 0.061209 | -66.7244 | 0.038035 | -66.7277 | 56.2473 | 56.1517 | 56.3031 | -66.8375 | -66.7382 | 0.027831 | -66.759 | 56.1528 | 56.3259 | 56.0727 | -67.0561 | -0.11846 | -0.062249 | -0.005322 | -0.008637 | 0.10982 | -0.1578 | -0.006405 | -0.33703 | -0.15675 | -0.019172 | -0.039941 | 0.29709 | 0.01643 | -0.23677 | 122.9663 | 122.8708 | 123.0222 | 66.7571 | -123.147 | 122.8718 | 123.045 | 122.7918 | 66.7469 | -123.3656
542.7969 | 123.1384 | -66.7465 | 56.3004 | 0.0018314 | -0.0054166 | 0.0010342 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060375 | 0.010583 | 0.061209 | -66.7244 | 0.038035 | -66.7277 | 56.2381 | 56.1563 | 56.3031 | -66.8284 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 55.9995 | -67.0607 | -0.081835 | -0.06225 | 0.022144 | 0.018829 | 0.10066 | -0.14406 | 0.00275 | -0.31415 | -0.15217 | 0.008294 | -0.021633 | 0.29251 | 0.021006 | -0.30087 | 122.9846 | 122.9028 | 123.0496 | 66.7846 | -123.1287 | 122.8947 | 123.0679 | 122.746 | 66.7789 | -123.361
543.7969 | 123.1842 | -66.7419 | 56.3141 | -0.0057996 | -0.0049892 | 0.0010342 | 0.056865 | -0.0016259 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.010583 | 0.060996 | -66.729 | 0.038035 | -66.7277 | 56.2335 | 56.1609 | 56.2985 | -66.8329 | -66.7382 | 0.036989 | -66.7682 | 56.1528 | 56.3168 | 55.9995 | -67.0744 | -0.090992 | -0.080562 | 0.012987 | 0.014251 | 0.10524 | -0.15322 | -0.015561 | -0.33246 | -0.16133 | 0.003716 | -0.026211 | 0.30625 | 0.002695 | -0.31461 | 122.9755 | 122.9028 | 123.0405 | 66.78 | -123.147 | 122.8947 | 123.0587 | 122.7414 | 66.7789 | -123.3885
544.7969 | 123.1796 | -66.7328 | 56.2729 | 0.0018314 | -0.005203 | 0.00060681 | 0.056865 | -0.0018397 | 0.062796 | -0.001755 | -0.00017733 | 0.00089321 | 0.060161 | 0.010583 | 0.061209 | -66.7335 | 0.028878 | -66.7277 | 56.2427 | 56.1563 | 56.3031 | -66.8375 | -66.7382 | 0.03241 | -66.7636 | 56.1436 | 56.3259 | 56.0086 | -67.0561 | -0.10473 | -0.030206 | -0.000746 | 0.005096 | 0.10982 | -0.1166 | 0.030216 | -0.3233 | -0.12929 | -0.005439 | -0.030787 | 0.29251 | 0.053051 | -0.26425 | 122.9755 | 122.8891 | 123.0359 | 66.7617 | -123.1104 | 122.8764 | 123.0587 | 122.7414 | 66.7652 | -123.329
545.7969 | 123.2254 | -66.7282 | 56.3095 | -0.013431 | -0.005203 | 0.0010342 | 0.056865 | -0.0014123 | 0.062796 | -0.0093855 | -0.00017733 | 0.00025221 | 0.059947 | 0.010583 | 0.060996 | -66.7244 | 0.028878 | -66.7231 | 56.2427 | 56.1563 | 56.3031 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1482 | 56.3168 | 56.0498 | -67.0607 | -0.10015 | -0.066827 | 0.003833 | 0.005097 | 0.10524 | -0.15322 | -0.006405 | -0.33246 | -0.16133 | -0.010017 | -0.035365 | 0.29709 | 0.007273 | -0.25966 | 122.9709 | 122.8845 | 123.0313 | 66.7571 | -123.1379 | 122.8764 | 123.045 | 122.7781 | 66.7652 | -123.3702
546.7969 | 123.1796 | -66.7145 | 56.2775 | 0.0018314 | -0.005203 | 0.0010342 | 0.056652 | -0.0016259 | 0.063009 | -0.001755 | -0.00060453 | 0.00067941 | 0.060161 | 0.010369 | 0.061209 | -66.7381 | 0.033457 | -66.7368 | 56.2473 | 56.1563 | 56.3031 | -66.8421 | -66.7428 | 0.03241 | -66.759 | 56.1482 | 56.3168 | 56.0361 | -67.0561 | -0.12762 | -0.030206 | -0.023634 | -0.02237 | 0.10525 | -0.12118 | 0.025638 | -0.34161 | -0.12928 | -0.028328 | -0.044518 | 0.29709 | 0.039316 | -0.24136 | 122.9617 | 122.8708 | 123.0176 | 66.7479 | -123.1196 | 122.8627 | 123.0313 | 122.7506 | 66.7469 | -123.3336
547.7969 | 123.2254 | -66.7099 | 56.2866 | 0.0018314 | -0.005203 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.010583 | 0.061423 | -66.7244 | 0.038035 | -66.7231 | 56.2427 | 56.1609 | 56.2985 | -66.8329 | -66.7474 | 0.036989 | -66.7636 | 56.1482 | 56.3214 | 56.0224 | -67.0561 | -0.12304 | -0.043939 | -0.014477 | -0.013213 | 0.10982 | -0.12575 | 0.011905 | -0.34619 | -0.13844 | -0.037485 | -0.053675 | 0.29251 | 0.034739 | -0.26425 | 122.9526 | 122.8708 | 123.0084 | 66.7479 | -123.1196 | 122.8581 | 123.0313 | 122.7323 | 66.7469 | -123.3427
548.7969 | 123.1522 | -66.7511 | 56.2912 | -0.0057996 | -0.0056302 | 0.0010342 | 0.057079 | -0.0016259 | 0.063009 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.010583 | 0.060782 | -66.7335 | 0.0243 | -66.7231 | 56.2427 | 56.1654 | 56.3123 | -66.8329 | -66.7428 | 0.03241 | -66.7636 | 56.1528 | 56.3259 | 56.0865 | -67.0561 | -0.081836 | -0.048517 | 0.017565 | 0.027986 | 0.10982 | -0.12575 | 0.021063 | -0.30499 | -0.13844 | 0.008293 | -0.012476 | 0.29251 | 0.03474 | -0.20472 | 122.9938 | 122.9165 | 123.0634 | 66.7754 | -123.1241 | 122.9039 | 123.077 | 122.8376 | 66.7835 | -123.3473
549.7969 | 123.1659 | -66.7419 | 56.3416 | 0.0094624 | -0.0047756 | 0.00082041 | 0.056865 | -0.0014123 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.010583 | 0.060996 | -66.7381 | 0.028878 | -66.7231 | 56.2427 | 56.1563 | 56.3077 | -66.8284 | -66.7474 | 0.03241 | -66.7682 | 56.1482 | 56.3168 | 56.0682 | -67.0515 | -0.086413 | -0.098871 | 0.003831 | 0.01883 | 0.10524 | -0.18526 | -0.03387 | -0.30957 | -0.19337 | -0.005442 | -0.026211 | 0.28336 | -0.024771 | -0.27339 | 122.9846 | 122.8982 | 123.0496 | 66.7708 | -123.1699 | 122.8901 | 123.0587 | 122.8101 | 66.7744 | -123.3931
550.7969 | 123.2162 | -66.7328 | 56.3095 | 0.0018314 | -0.0054166 | 0.0010342 | 0.057079 | -0.0018397 | 0.062796 | -0.001755 | -0.00039093 | 0.00089321 | 0.060161 | 0.010369 | 0.060996 | -66.7244 | 0.033457 | -66.7185 | 56.2473 | 56.1654 | 56.2985 | -66.8284 | -66.7428 | 0.03241 | -66.7544 | 56.1436 | 56.3214 | 56.0636 | -67.0652 | -0.095568 | -0.062249 | 0.008411 | 0.014253 | 0.10982 | -0.14406 | -0.010983 | -0.33246 | -0.16591 | -0.010018 | -0.02163 | 0.31083 | 0.011851 | -0.24593 | 122.98 | 122.8982 | 123.0313 | 66.7662 | -123.1379 | 122.8764 | 123.0541 | 122.7964 | 66.7652 | -123.3748
551.7969 | 123.1613 | -66.7145 | 56.3187 | -0.0057996 | -0.0054166 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | 0.00025007 | 0.00046581 | 0.059947 | 0.010583 | 0.061423 | -66.7381 | 0.033457 | -66.7277 | 56.2381 | 56.1563 | 56.2985 | -66.8329 | -66.7428 | 0.036989 | -66.7636 | 56.1528 | 56.3259 | 56.0315 | -67.0607 | -0.11846 | -0.080561 | -0.023634 | -0.013214 | 0.10524 | -0.16238 | -0.020139 | -0.34619 | -0.16591 | -0.028328 | -0.049097 | 0.29709 | 0.007274 | -0.28713 | 122.9526 | 122.8708 | 123.013 | 66.7479 | -123.1516 | 122.8672 | 123.0404 | 122.746 | 66.7515 | -123.3793
552.7969 | 123.1796 | -66.7282 | 56.3004 | 0.0018314 | -0.0054166 | 0.00060681 | 0.057079 | -0.0018397 | 0.062796 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059947 | 0.010797 | 0.061209 | -66.729 | 0.033457 | -66.7231 | 56.2381 | 56.1471 | 56.2985 | -66.8284 | -66.7336 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 56.0636 | -67.0607 | -0.10015 | -0.06225 | -0.000746 | 0.005097 | 0.10524 | -0.15322 | -0.001828 | -0.33246 | -0.14759 | -0.005439 | -0.035365 | 0.29709 | 0.021006 | -0.23677 | 122.9663 | 122.8753 | 123.0267 | 66.7617 | -123.1287 | 122.881 | 123.0496 | 122.7918 | 66.7606 | -123.361
553.7969 | 123.1796 | -66.7053 | 56.3141 | 0.0094624 | -0.0054166 | 0.00060681 | 0.056865 | -0.0018397 | 0.063009 | 0.0058755 | -0.00017733 | 0.00025221 | 0.060161 | 0.010369 | 0.061209 | -66.729 | 0.033457 | -66.7277 | 56.2335 | 56.1563 | 56.3031 | -66.8329 | -66.7336 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1139 | -67.0652 | -0.12761 | -0.080562 | -0.023634 | -0.02237 | 0.10524 | -0.1578 | -0.010983 | -0.35993 | -0.16591 | -0.028327 | -0.058253 | 0.30167 | 0.007273 | -0.20014 | 122.9388 | 122.8616 | 123.0084 | 66.7388 | -123.147 | 122.8535 | 123.0267 | 122.8193 | 66.7377 | -123.3793
554.7969 | 123.1567 | -66.7419 | 56.3004 | 0.0018314 | -0.0054166 | 0.0010342 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | -0.00039093 | 0.00025221 | 0.059947 | 0.010369 | 0.061423 | -66.7335 | 0.0243 | -66.7323 | 56.2427 | 56.1609 | 56.3077 | -66.8329 | -66.7336 | 0.03241 | -66.7682 | 56.1482 | 56.3259 | 56.0636 | -67.0652 | -0.090992 | -0.057672 | 0.008409 | 0.009673 | 0.10067 | -0.13949 | 0.007329 | -0.3233 | -0.15217 | 0.008294 | -0.026211 | 0.29709 | 0.025585 | -0.23677 | 122.9846 | 122.9028 | 123.0496 | 66.7662 | -123.1333 | 122.8901 | 123.0679 | 122.8055 | 66.7744 | -123.3656
555.7969 | 123.1613 | -66.7328 | 56.3187 | -0.013431 | -0.005203 | 0.00082041 | 0.056224 | -0.0018397 | 0.062796 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059947 | 0.010583 | 0.060996 | -66.7244 | 0.038035 | -66.7323 | 56.2381 | 56.1517 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.759 | 56.1482 | 56.3214 | 56.0178 | -67.0561 | -0.10015 | -0.080561 | 0.008411 | 0.000518 | 0.10067 | -0.16695 | -0.015561 | -0.3233 | -0.17048 | -0.005439 | -0.026208 | 0.29709 | 0.002695 | -0.30087 | 122.9709 | 122.8845 | 123.0359 | 66.7708 | -123.1516 | 122.881 | 123.0541 | 122.7506 | 66.7652 | -123.3748
556.7969 | 123.1888 | -66.7419 | 56.3049 | -0.0057996 | -0.0056302 | 0.0010342 | 0.056865 | -0.0014123 | 0.062796 | 0.013506 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.010369 | 0.061209 | -66.729 | 0.033457 | -66.7231 | 56.2427 | 56.1609 | 56.3031 | -66.8284 | -66.7382 | 0.027831 | -66.759 | 56.1482 | 56.3214 | 56.1506 | -67.0652 | -0.086413 | -0.06225 | 0.012987 | 0.01883 | 0.10524 | -0.14406 | -0.001828 | -0.3233 | -0.15675 | 0.003716 | -0.017053 | 0.30625 | 0.016428 | -0.15436 | 122.9846 | 122.9028 | 123.045 | 66.7754 | -123.1333 | 122.8901 | 123.0633 | 122.8925 | 66.7698 | -123.3702
557.7969 | 123.175 | -66.7374 | 56.3141 | 0.0094624 | -0.0056302 | 0.00082041 | 0.056865 | -0.0014123 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.010797 | 0.061209 | -66.729 | 0.028878 | -66.7323 | 56.2335 | 56.1517 | 56.2985 | -66.8284 | -66.7428 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 56.0361 | -67.0652 | -0.09099 | -0.080562 | 0.00841 | 0.005096 | 0.096086 | -0.16238 | -0.015561 | -0.32788 | -0.16591 | -0.00544 | -0.030788 | 0.29709 | 0.007273 | -0.27798 | 122.9709 | 122.8891 | 123.0359 | 66.7662 | -123.1424 | 122.8855 | 123.0587 | 122.7735 | 66.7698 | -123.3793
558.7969 | 123.1842 | -66.7145 | 56.2912 | 0.017093 | -0.0056302 | 0.00082041 | 0.056865 | -0.0014123 | 0.062796 | 0.0058755 | -0.00039093 | 0.00089321 | 0.059734 | 0.010369 | 0.060996 | -66.7244 | 0.028878 | -66.7231 | 56.2427 | 56.1654 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7682 | 56.1482 | 56.3214 | 56.0911 | -67.0652 | -0.11846 | -0.048517 | -0.009899 | -0.008635 | 0.10982 | -0.12575 | 0.011905 | -0.35077 | -0.14302 | -0.023749 | -0.053676 | 0.29709 | 0.030161 | -0.20015 | 122.9572 | 122.8799 | 123.0176 | 66.7434 | -123.1241 | 122.8627 | 123.0358 | 122.8055 | 66.7469 | -123.3564
559.7969 | 123.1201 | -66.7236 | 56.3141 | 0.0018314 | -0.005203 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010583 | 0.060996 | -66.7335 | 0.038035 | -66.7277 | 56.2427 | 56.1609 | 56.3031 | -66.8284 | -66.7428 | 0.036989 | -66.7636 | 56.1573 | 56.3168 | 56.0956 | -67.0652 | -0.10472 | -0.071405 | -0.009901 | -0.004059 | 0.10066 | -0.15322 | -0.010983 | -0.34161 | -0.15675 | -0.019173 | -0.039942 | 0.30167 | 0.002695 | -0.21845 | 122.9663 | 122.8845 | 123.0267 | 66.7617 | -123.1424 | 122.881 | 123.0404 | 122.8193 | 66.7606 | -123.3793
560.7969 | 123.2025 | -66.7282 | 56.3278 | 0.0094624 | -0.0054166 | 0.0014616 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060375 | 0.010583 | 0.060996 | -66.7335 | 0.038035 | -66.7323 | 56.2473 | 56.1563 | 56.3123 | -66.8284 | -66.7382 | 0.027831 | -66.7636 | 56.1528 | 56.3214 | 56.1323 | -67.0607 | -0.10015 | -0.08056 | -0.005324 | -0.00406 | 0.096086 | -0.17153 | -0.015558 | -0.33246 | -0.17506 | -0.010017 | -0.035365 | 0.29709 | -0.00646 | -0.19556 | 122.9755 | 122.8845 | 123.0405 | 66.7662 | -123.1562 | 122.881 | 123.0496 | 122.8605 | 66.756 | -123.3885
561.7969 | 123.1659 | -66.7145 | 56.3095 | -0.0057996 | -0.0054166 | 0.0010342 | 0.057079 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.059947 | 0.010797 | 0.060996 | -66.7244 | 0.028878 | -66.7231 | 56.2427 | 56.1563 | 56.3077 | -66.8238 | -66.7382 | 0.027831 | -66.7636 | 56.1436 | 56.3168 | 56.0819 | -67.0607 | -0.1093 | -0.066827 | -0.009899 | -0.008635 | 0.10066 | -0.15322 | -0.001826 | -0.34619 | -0.16591 | -0.023749 | -0.049097 | 0.29709 | 0.007273 | -0.22761 | 122.9572 | 122.8708 | 123.0222 | 66.7434 | -123.1333 | 122.8581 | 123.0313 | 122.7964 | 66.7423 | -123.3702
562.7969 | 123.175 | -66.7191 | 56.337 | 0.0018314 | -0.0056302 | 0.0012478 | 0.056438 | -0.0014123 | 0.062582 | -0.001755 | -0.00039093 | 0.00067941 | 0.060375 | 0.010797 | 0.061209 | -66.7244 | 0.038035 | -66.7277 | 56.2473 | 56.1654 | 56.2939 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1528 | 56.3168 | 56.059 | -67.0652 | -0.1093 | -0.089715 | -0.005322 | -0.008637 | 0.10066 | -0.17153 | -0.043028 | -0.34619 | -0.18422 | -0.019172 | -0.04452 | 0.30167 | -0.020193 | -0.27797 | 122.9663 | 122.8845 | 123.013 | 66.7571 | -123.1653 | 122.8718 | 123.0358 | 122.7781 | 66.756 | -123.4022
563.7969 | 123.23 | -66.7007 | 56.3187 | 0.0018314 | -0.0054166 | 0.00060681 | 0.056652 | -0.0016259 | 0.062155 | -0.001755 | -0.00039093 | 0.00046581 | 0.059734 | 0.010797 | 0.061209 | -66.7244 | 0.028878 | -66.7231 | 56.2335 | 56.1471 | 56.3031 | -66.8375 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.059 | -67.0698 | -0.13677 | -0.08514 | -0.023632 | -0.022368 | 0.1144 | -0.17153 | -0.015561 | -0.36908 | -0.17048 | -0.037482 | -0.06283 | 0.30625 | -0.001883 | -0.25966 | 122.9343 | 122.8479 | 123.0038 | 66.7296 | -123.1562 | 122.8489 | 123.0175 | 122.7597 | 66.7332 | -123.3885
564.7969 | 123.1522 | -66.7282 | 56.3141 | 0.0094624 | -0.005203 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | 0.013506 | -0.00017733 | 0.00046581 | 0.060161 | 0.010797 | 0.060996 | -66.729 | 0.038035 | -66.7323 | 56.2427 | 56.1563 | 56.2985 | -66.8421 | -66.7336 | 0.036989 | -66.7544 | 56.1482 | 56.3214 | 55.9995 | -67.0561 | -0.11388 | -0.071405 | -0.000746 | -0.00406 | 0.10982 | -0.1578 | -0.015561 | -0.32788 | -0.16591 | -0.005439 | -0.026208 | 0.30167 | 0.007273 | -0.31461 | 122.9709 | 122.8845 | 123.0267 | 66.7662 | -123.1562 | 122.8764 | 123.0496 | 122.7277 | 66.7652 | -123.3702
565.7969 | 123.2162 | -66.6962 | 56.3049 | 0.0018314 | -0.0054166 | 0.00082041 | 0.057079 | -0.0020533 | 0.062582 | 0.013506 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.010583 | 0.060568 | -66.729 | 0.033457 | -66.7231 | 56.2427 | 56.1471 | 56.3031 | -66.8329 | -66.7382 | 0.036989 | -66.7636 | 56.1482 | 56.3259 | 56.027 | -67.0652 | -0.13677 | -0.06225 | -0.032789 | -0.026946 | 0.10982 | -0.1578 | -0.001828 | -0.36908 | -0.15675 | -0.04206 | -0.067408 | 0.30167 | 0.021007 | -0.27798 | 122.9388 | 122.8433 | 122.9993 | 66.7296 | -123.1379 | 122.8443 | 123.0221 | 122.7231 | 66.7332 | -123.3702
566.7969 | 123.1659 | -66.7191 | 56.2912 | 0.0018314 | -0.005203 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.0093855 | -0.00017733 | 0.00025221 | 0.059947 | 0.010797 | 0.061209 | -66.7335 | 0.033457 | -66.7231 | 56.2381 | 56.1563 | 56.3077 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.0544 | -67.0652 | -0.11388 | -0.053095 | -0.014479 | -0.004058 | 0.10982 | -0.13491 | 0.016484 | -0.34619 | -0.14302 | -0.019172 | -0.04452 | 0.30167 | 0.030161 | -0.23678 | 122.9572 | 122.8753 | 123.0267 | 66.7525 | -123.1241 | 122.8672 | 123.0404 | 122.7735 | 66.7515 | -123.3564
567.7969 | 123.3032 | -66.687 | 56.282 | 0.0094624 | -0.0056302 | 0.00060681 | 0.056865 | -0.0020533 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.010797 | 0.061209 | -66.729 | 0.028878 | -66.7277 | 56.2427 | 56.1517 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1002 | -67.0652 | -0.14592 | -0.039361 | -0.041944 | -0.04068 | 0.10524 | -0.13033 | 0.021061 | -0.37824 | -0.13386 | -0.051215 | -0.076563 | 0.30167 | 0.039317 | -0.18183 | 122.9297 | 122.8387 | 122.9901 | 66.7159 | -123.115 | 122.8352 | 123.0084 | 122.7872 | 66.7194 | -123.3473
568.7969 | 123.175 | -66.7374 | 56.3095 | -0.013431 | -0.0054166 | 0.00082041 | 0.056438 | -0.0016259 | 0.063009 | 0.0058755 | -0.00017733 | 0.00046581 | 0.060375 | 0.010797 | 0.060996 | -66.729 | 0.033457 | -66.7323 | 56.2427 | 56.1517 | 56.3031 | -66.8375 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3214 | 56.0636 | -67.0652 | -0.10015 | -0.066827 | 0.00841 | 0.005096 | 0.10524 | -0.1578 | -0.006405 | -0.32788 | -0.15675 | 0.003717 | -0.02163 | 0.30625 | 0.011851 | -0.24593 | 122.98 | 122.8891 | 123.0405 | 66.7708 | -123.147 | 122.8901 | 123.0587 | 122.8009 | 66.7698 | -123.3748
569.7969 | 123.2712 | -66.687 | 56.282 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056865 | -0.0018397 | 0.063009 | 0.0058755 | -0.00039093 | 0.00046581 | 0.060161 | 0.011224 | 0.061209 | -66.7244 | 0.0243 | -66.7277 | 56.2335 | 56.1609 | 56.3031 | -66.8329 | -66.7336 | 0.036989 | -66.7544 | 56.1482 | 56.3214 | 56.1185 | -67.0652 | -0.14592 | -0.048518 | -0.037365 | -0.04068 | 0.10524 | -0.12118 | 0.021061 | -0.37824 | -0.13386 | -0.046637 | -0.067406 | 0.31083 | 0.039317 | -0.16352 | 122.9205 | 122.8479 | 122.9901 | 66.7113 | -123.115 | 122.8352 | 123.0084 | 122.8055 | 66.724 | -123.3473
570.8594 | 123.2849 | -66.6824 | 56.3004 | -0.0057996 | -0.0054166 | 0.00082041 | 0.056438 | -0.0018397 | 0.062796 | -0.001755 | 0.00025007 | 0.00046581 | 0.059947 | 0.010797 | 0.060996 | -66.729 | 0.028878 | -66.7323 | 56.2381 | 56.1654 | 56.3031 | -66.8284 | -66.7382 | 0.027831 | -66.759 | 56.1573 | 56.3214 | 56.0315 | -67.0607 | -0.14592 | -0.06225 | -0.046522 | -0.049836 | 0.096086 | -0.13491 | 0.00275 | -0.37823 | -0.14301 | -0.055793 | -0.076562 | 0.30167 | 0.021006 | -0.26882 | 122.9205 | 122.8479 | 122.9855 | 66.7113 | -123.1287 | 122.8398 | 123.0038 | 122.714 | 66.7103 | -123.361
571.7969 | 123.3215 | -66.6916 | 56.2683 | 0.0018314 | -0.0047756 | 0.00060681 | 0.057079 | -0.0020533 | 0.062796 | 0.0058755 | -0.00039093 | 0.00067941 | 0.060161 | 0.010797 | 0.061209 | -66.7381 | 0.019721 | -66.7277 | 56.2335 | 56.1517 | 56.3031 | -66.8238 | -66.7245 | 0.036989 | -66.7636 | 56.1482 | 56.3305 | 56.0773 | -67.0652 | -0.13219 | -0.034786 | -0.046523 | -0.036103 | 0.096085 | -0.1166 | 0.034793 | -0.37366 | -0.12013 | -0.032902 | -0.071986 | 0.30167 | 0.062206 | -0.19099 | 122.9251 | 122.8433 | 122.9947 | 66.7113 | -123.0921 | 122.8398 | 123.0221 | 122.7689 | 66.7286 | -123.3336
572.7969 | 123.1567 | -66.7007 | 56.3553 | 0.0094624 | -0.005844 | 0.0010342 | 0.056865 | -0.0016259 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.010797 | 0.060996 | -66.7381 | 0.028878 | -66.7185 | 56.2427 | 56.1609 | 56.3031 | -66.8238 | -66.7382 | 0.027831 | -66.759 | 56.1573 | 56.3305 | 56.1277 | -67.0607 | -0.12303 | -0.1126 | -0.037367 | -0.01779 | 0.10524 | -0.19442 | -0.052182 | -0.35992 | -0.19795 | -0.037482 | -0.058251 | 0.30167 | -0.024769 | -0.2276 | 122.9434 | 122.8616 | 123.0038 | 66.7296 | -123.1791 | 122.8581 | 123.0313 | 122.8284 | 66.7286 | -123.416
573.7969 | 123.1201 | -66.655 | 56.282 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056652 | -0.0018397 | 0.062796 | 0.013506 | -0.00039093 | 0.00089321 | 0.060161 | 0.010797 | 0.060996 | -66.7381 | 0.028878 | -66.7277 | 56.2427 | 56.1609 | 56.3031 | -66.8329 | -66.7382 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 56.1368 | -67.0607 | -0.17797 | -0.039361 | -0.083144 | -0.072724 | 0.10524 | -0.12118 | 0.021061 | -0.4057 | -0.12928 | -0.083259 | -0.10861 | 0.29709 | 0.039317 | -0.1452 | 122.8976 | 122.8158 | 122.9581 | 66.6838 | -123.115 | 122.8077 | 122.9763 | 122.7918 | 66.6874 | -123.3427
574.7969 | 123.23 | -66.6962 | 56.3232 | 0.017093 | -0.0056302 | 0.00060681 | 0.056865 | -0.0016259 | 0.063009 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.010797 | 0.060782 | -66.7244 | 0.028878 | -66.7323 | 56.2473 | 56.1609 | 56.3031 | -66.8238 | -66.7336 | 0.03241 | -66.759 | 56.1573 | 56.3214 | 56.0498 | -67.0652 | -0.12761 | -0.075982 | -0.02821 | -0.036103 | 0.091507 | -0.16237 | -0.020138 | -0.36908 | -0.1659 | -0.037482 | -0.062829 | 0.30625 | -0.001882 | -0.2734 | 122.9434 | 122.857 | 122.9993 | 66.725 | -123.147 | 122.8535 | 123.0175 | 122.746 | 66.7286 | -123.3885
575.7969 | 123.2483 | -66.7007 | 56.2912 | 0.0018314 | -0.0056302 | 0.00039321 | 0.057079 | -0.0018397 | 0.062582 | -0.001755 | 0.00025007 | 0.00089321 | 0.059947 | 0.010369 | 0.061209 | -66.729 | 0.0243 | -66.7323 | 56.2381 | 56.1609 | 56.3031 | -66.8329 | -66.7245 | 0.03241 | -66.7682 | 56.1482 | 56.3259 | 56.0682 | -67.0698 | -0.13219 | -0.053095 | -0.028211 | -0.031525 | 0.10067 | -0.13033 | 0.011905 | -0.36908 | -0.14302 | -0.023746 | -0.067409 | 0.30167 | 0.03474 | -0.22304 | 122.9388 | 122.8616 | 123.0038 | 66.725 | -123.1241 | 122.8489 | 123.0267 | 122.7689 | 66.7332 | -123.361
576.7969 | 123.2758 | -66.6687 | 56.282 | 0.0018314 | -0.0054166 | 0.00060681 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.011011 | 0.061209 | -66.7152 | 0.033457 | -66.7277 | 56.2381 | 56.1563 | 56.3077 | -66.8284 | -66.7336 | 0.036989 | -66.7682 | 56.1436 | 56.3214 | 56.0636 | -67.0607 | -0.15966 | -0.043939 | -0.046519 | -0.058991 | 0.10066 | -0.12575 | 0.02564 | -0.39197 | -0.13844 | -0.064948 | -0.099453 | 0.29251 | 0.039317 | -0.21846 | 122.9068 | 122.825 | 122.9764 | 66.7022 | -123.1104 | 122.8123 | 122.9901 | 122.7323 | 66.7057 | -123.3427
577.7969 | 123.2346 | -66.6779 | 56.2912 | 0.0018314 | -0.0056302 | 0.0010342 | 0.057079 | -0.0018397 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.011011 | 0.060996 | -66.7381 | 0.033457 | -66.7231 | 56.2381 | 56.1471 | 56.3031 | -66.8238 | -66.7428 | 0.036989 | -66.759 | 56.1436 | 56.3214 | 56.1277 | -67.0652 | -0.14592 | -0.053095 | -0.060256 | -0.045257 | 0.10066 | -0.14407 | 0.011905 | -0.38739 | -0.1476 | -0.06495 | -0.08114 | 0.30625 | 0.030161 | -0.16352 | 122.916 | 122.825 | 122.981 | 66.7113 | -123.115 | 122.8215 | 122.9992 | 122.8055 | 66.7148 | -123.3564
578.7969 | 123.23 | -66.687 | 56.2775 | -0.013431 | -0.0056302 | 0.0010342 | 0.057079 | -0.0016259 | 0.062368 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059947 | 0.010797 | 0.060782 | -66.729 | 0.033457 | -66.7323 | 56.2381 | 56.1426 | 56.3077 | -66.8329 | -66.7382 | 0.027831 | -66.759 | 56.1528 | 56.3168 | 56.0727 | -67.0652 | -0.14592 | -0.039362 | -0.041944 | -0.045258 | 0.10067 | -0.13491 | 0.030217 | -0.37824 | -0.12471 | -0.051215 | -0.071984 | 0.30625 | 0.039316 | -0.20473 | 122.9251 | 122.8296 | 122.9947 | 66.7205 | -123.1104 | 122.8398 | 123.0038 | 122.7597 | 66.7148 | -123.3427
579.7969 | 123.1979 | -66.6962 | 56.3141 | -0.0057996 | -0.005844 | 0.0010342 | 0.056865 | -0.0018397 | 0.062155 | 0.021136 | -0.00017733 | 0.00067941 | 0.059734 | 0.010797 | 0.060782 | -66.7335 | 0.028878 | -66.7277 | 56.2381 | 56.1563 | 56.3031 | -66.8284 | -66.7291 | 0.036989 | -66.7636 | 56.1528 | 56.3168 | 56.0132 | -67.0607 | -0.13219 | -0.075983 | -0.037367 | -0.031525 | 0.10066 | -0.1578 | -0.010983 | -0.3645 | -0.16133 | -0.032903 | -0.067408 | 0.29709 | 0.002695 | -0.30087 | 122.9343 | 122.8525 | 122.9993 | 66.725 | -123.1424 | 122.8489 | 123.0129 | 122.7094 | 66.7332 | -123.3748
580.7969 | 123.2849 | -66.6779 | 56.2912 | 0.0018314 | -0.005203 | 0.00082041 | 0.057079 | -0.0018397 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.011011 | 0.060782 | -66.7244 | 0.033457 | -66.7231 | 56.2381 | 56.1471 | 56.2985 | -66.8329 | -66.7336 | 0.027831 | -66.7636 | 56.1482 | 56.3168 | 56.0407 | -67.0652 | -0.15508 | -0.053095 | -0.046521 | -0.045257 | 0.10982 | -0.14407 | 0.007327 | -0.38739 | -0.14302 | -0.055793 | -0.085719 | 0.30167 | 0.025583 | -0.25051 | 122.916 | 122.825 | 122.9764 | 66.7113 | -123.1241 | 122.826 | 122.9946 | 122.7185 | 66.7057 | -123.3564
581.7969 | 123.23 | -66.7145 | 56.2912 | 0.0094624 | -0.0054166 | 0.0010342 | 0.057079 | -0.0016259 | 0.062796 | -0.001755 | -0.00039093 | 0.00067941 | 0.059947 | 0.011011 | 0.060782 | -66.7244 | 0.033457 | -66.7277 | 56.2427 | 56.1471 | 56.3031 | -66.8238 | -66.7336 | 0.03241 | -66.759 | 56.1482 | 56.3168 | 56.0453 | -67.0652 | -0.1093 | -0.048517 | -0.009899 | -0.013214 | 0.096085 | -0.14407 | 0.011905 | -0.35077 | -0.14302 | -0.019171 | -0.044518 | 0.30625 | 0.025583 | -0.24593 | 122.9572 | 122.8616 | 123.0176 | 66.7479 | -123.115 | 122.8627 | 123.0313 | 122.7597 | 66.7469 | -123.3564
582.7969 | 123.2391 | -66.7007 | 56.2775 | 0.0094624 | -0.0054166 | 0.00060681 | 0.057293 | -0.0014123 | 0.062368 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060161 | 0.011011 | 0.060782 | -66.729 | 0.028878 | -66.7277 | 56.2427 | 56.1426 | 56.2985 | -66.8238 | -66.7382 | 0.03241 | -66.759 | 56.1528 | 56.3214 | 56.0453 | -67.0607 | -0.12303 | -0.034784 | -0.028211 | -0.026947 | 0.096085 | -0.13491 | 0.02106 | -0.35992 | -0.12471 | -0.037482 | -0.058251 | 0.30167 | 0.043894 | -0.2322 | 122.9434 | 122.8433 | 122.9993 | 66.7296 | -123.1012 | 122.8535 | 123.0221 | 122.746 | 66.7332 | -123.3381
583.7969 | 123.2346 | -66.7007 | 56.2775 | -0.0057996 | -0.0054166 | 0.00060681 | 0.057506 | -0.0014123 | 0.062368 | -0.0093855 | -0.00017733 | 0.00067941 | 0.060161 | 0.010797 | 0.060996 | -66.7335 | 0.033457 | -66.7231 | 56.2335 | 56.1563 | 56.2985 | -66.8284 | -66.7291 | 0.036989 | -66.759 | 56.139 | 56.3259 | 56.0407 | -67.0652 | -0.12761 | -0.043941 | -0.032789 | -0.022368 | 0.10524 | -0.12118 | 0.02106 | -0.3645 | -0.13844 | -0.028325 | -0.058251 | 0.30625 | 0.048473 | -0.23678 | 122.9343 | 122.857 | 122.9993 | 66.7342 | -123.1058 | 122.8398 | 123.0267 | 122.7414 | 66.7377 | -123.3427
584.7969 | 123.0698 | -66.7099 | 56.3004 | -0.0057996 | -0.0056302 | 0.00060681 | 0.056865 | -0.0022669 | 0.062582 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059947 | 0.010583 | 0.061209 | -66.7244 | 0.033457 | -66.7368 | 56.2427 | 56.1563 | 56.2985 | -66.8329 | -66.7382 | 0.036989 | -66.759 | 56.1528 | 56.3305 | 56.027 | -67.0607 | -0.12304 | -0.057672 | -0.014477 | -0.026948 | 0.096087 | -0.14406 | -0.001828 | -0.35077 | -0.14759 | -0.028327 | -0.049096 | 0.30167 | 0.030163 | -0.2734 | 122.9526 | 122.8662 | 123.0084 | 66.7434 | -123.1333 | 122.8627 | 123.0404 | 122.7369 | 66.7469 | -123.361
585.7969 | 123.23 | -66.7099 | 56.25 | -0.0057996 | -0.005844 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.010797 | 0.060996 | -66.7335 | 0.038035 | -66.7231 | 56.2335 | 56.1471 | 56.3031 | -66.8238 | -66.7336 | 0.03241 | -66.759 | 56.1482 | 56.3259 | 56.0453 | -67.0561 | -0.11388 | -0.016475 | -0.023634 | -0.013213 | 0.10066 | -0.10287 | 0.053104 | -0.34619 | -0.10182 | -0.023749 | -0.049096 | 0.29709 | 0.075939 | -0.20473 | 122.9434 | 122.857 | 123.013 | 66.7479 | -123.0738 | 122.8581 | 123.0358 | 122.7552 | 66.7423 | -123.3061
586.7969 | 123.2254 | -66.7191 | 56.282 | 0.0018314 | -0.0054166 | 0.0012478 | 0.057506 | -0.0016259 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.060161 | 0.011224 | 0.060996 | -66.7244 | 0.028878 | -66.7231 | 56.2473 | 56.1288 | 56.3031 | -66.8238 | -66.7291 | 0.036989 | -66.7682 | 56.1528 | 56.3259 | 56.0956 | -67.0561 | -0.10472 | -0.034783 | -0.005322 | -0.004058 | 0.10066 | -0.15323 | 0.021061 | -0.33703 | -0.12928 | -0.010015 | -0.049099 | 0.28794 | 0.043896 | -0.18641 | 122.9663 | 122.8479 | 123.0222 | 66.7479 | -123.1058 | 122.8718 | 123.045 | 122.8147 | 66.756 | -123.3381
587.7969 | 123.2574 | -66.7099 | 56.2546 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056865 | -0.0020533 | 0.062582 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059947 | 0.010583 | 0.061209 | -66.7198 | 0.033457 | -66.7277 | 56.2427 | 56.1426 | 56.3031 | -66.8329 | -66.7291 | 0.03241 | -66.759 | 56.1482 | 56.3259 | 56.0498 | -67.0652 | -0.12304 | -0.011896 | -0.009899 | -0.017792 | 0.10524 | -0.11203 | 0.048526 | -0.35535 | -0.1064 | -0.01917 | -0.049096 | 0.30625 | 0.071361 | -0.20473 | 122.9526 | 122.8525 | 123.013 | 66.7434 | -123.0875 | 122.8581 | 123.0358 | 122.7597 | 66.7423 | -123.3198
588.7969 | 123.2712 | -66.6962 | 56.2729 | 0.0018314 | -0.0054166 | 0.00039321 | 0.056865 | -0.0018397 | 0.062796 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.010797 | 0.060996 | -66.7335 | 0.033457 | -66.7231 | 56.2381 | 56.1426 | 56.2985 | -66.8329 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3259 | 56.0086 | -67.0607 | -0.13677 | -0.034784 | -0.037367 | -0.026946 | 0.10982 | -0.13034 | 0.025638 | -0.3645 | -0.12013 | -0.037482 | -0.062829 | 0.30167 | 0.053051 | -0.26425 | 122.9343 | 122.8387 | 122.9947 | 66.7296 | -123.1058 | 122.8489 | 123.0221 | 122.7048 | 66.7286 | -123.3336
589.7969 | 123.2803 | -66.6962 | 56.3049 | -0.0057996 | -0.0054166 | 0.00060681 | 0.057079 | -0.0018397 | 0.063009 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059734 | 0.011224 | 0.060996 | -66.729 | 0.038035 | -66.7414 | 56.2381 | 56.1609 | 56.2939 | -66.8284 | -66.7382 | 0.036989 | -66.759 | 56.1528 | 56.3305 | 56.0865 | -67.0561 | -0.13219 | -0.066828 | -0.032789 | -0.04526 | 0.086929 | -0.14406 | -0.010985 | -0.35992 | -0.15217 | -0.04206 | -0.062829 | 0.29709 | 0.025585 | -0.21846 | 122.9343 | 122.857 | 122.9901 | 66.7342 | -123.1333 | 122.8489 | 123.0267 | 122.7826 | 66.7332 | -123.361
590.7969 | 123.262 | -66.7282 | 56.2637 | -0.0057996 | -0.005844 | 0.00082041 | 0.057079 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059734 | 0.010797 | 0.060782 | -66.729 | 0.028878 | -66.7277 | 56.2381 | 56.1471 | 56.3031 | -66.8238 | -66.7336 | 0.03241 | -66.7544 | 56.1528 | 56.3259 | 56.0178 | -67.0515 | -0.095567 | -0.025629 | -0.000746 | 0.000518 | 0.096085 | -0.1166 | 0.039371 | -0.3233 | -0.11097 | -0.005439 | -0.026208 | 0.29709 | 0.062206 | -0.24594 | 122.9663 | 122.8753 | 123.0313 | 66.7571 | -123.0875 | 122.881 | 123.0541 | 122.746 | 66.7606 | -123.3152
591.7969 | 123.1613 | -66.7465 | 56.3141 | -0.013431 | -0.005844 | 0.00060681 | 0.057079 | -0.0016259 | 0.063009 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059947 | 0.011224 | 0.060568 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1471 | 56.2985 | -66.8284 | -66.7291 | 0.03241 | -66.7544 | 56.1528 | 56.3259 | 56.1002 | -67.0607 | -0.081835 | -0.071405 | 0.022144 | 0.014251 | 0.096086 | -0.16696 | -0.015561 | -0.31415 | -0.16133 | 0.017451 | -0.007897 | 0.30625 | 0.011852 | -0.21388 | 122.9892 | 122.8937 | 123.045 | 66.7846 | -123.1424 | 122.8993 | 123.0725 | 122.8467 | 66.7789 | -123.3748
592.7969 | 123.2346 | -66.7099 | 56.2546 | 0.0018314 | -0.0060576 | 0.0010342 | 0.056865 | -0.0018397 | 0.062582 | -0.001755 | -0.00017733 | 0.00046581 | 0.059947 | 0.011224 | 0.060996 | -66.729 | 0.038035 | -66.7368 | 56.2335 | 56.17 | 56.3077 | -66.8284 | -66.7336 | 0.036989 | -66.759 | 56.1482 | 56.3305 | 56.0865 | -67.0698 | -0.11846 | -0.021053 | -0.019056 | -0.026948 | 0.091508 | -0.084552 | 0.053105 | -0.35993 | -0.1064 | -0.023749 | -0.049096 | 0.31083 | 0.075939 | -0.1681 | 122.9434 | 122.8799 | 123.0176 | 66.7479 | -123.0829 | 122.8581 | 123.0404 | 122.7964 | 66.7469 | -123.3244
593.7969 | 123.1247 | -66.7465 | 56.3095 | 0.0018314 | -0.0056302 | 0.00060681 | 0.056865 | -0.0014123 | 0.062796 | -0.0093855 | 0.00025007 | 0.00067941 | 0.059947 | 0.011011 | 0.061209 | -66.7335 | 0.038035 | -66.7323 | 56.2473 | 56.1563 | 56.3031 | -66.8284 | -66.7291 | 0.03241 | -66.7636 | 56.139 | 56.3305 | 56.0544 | -67.0652 | -0.081835 | -0.062249 | 0.012987 | 0.014251 | 0.096086 | -0.15322 | -0.006405 | -0.31873 | -0.17048 | 0.017451 | -0.017054 | 0.30167 | 0.021008 | -0.25509 | 122.9938 | 122.9028 | 123.0496 | 66.7846 | -123.1379 | 122.8855 | 123.077 | 122.8009 | 66.7789 | -123.3748
594.7969 | 123.2574 | -66.7145 | 56.2683 | -0.013431 | -0.0056302 | 0.00082041 | 0.056865 | -0.0014123 | 0.062582 | -0.001755 | -0.00017733 | 0.00089321 | 0.059734 | 0.011011 | 0.060996 | -66.7244 | 0.033457 | -66.7277 | 56.2335 | 56.1609 | 56.2985 | -66.8238 | -66.7336 | 0.027831 | -66.7544 | 56.1573 | 56.3259 | 56.1002 | -67.0652 | -0.1093 | -0.034786 | -0.009899 | -0.013214 | 0.096085 | -0.10744 | 0.030215 | -0.35077 | -0.11097 | -0.019171 | -0.03994 | 0.31083 | 0.057628 | -0.1681 | 122.948 | 122.8753 | 123.013 | 66.7479 | -123.0921 | 122.8718 | 123.0404 | 122.8147 | 66.7423 | -123.3336
595.7969 | 123.1522 | -66.774 | 56.2958 | 0.0018314 | -0.0060576 | 0.00082041 | 0.056865 | -0.0016259 | 0.062796 | -0.001755 | -0.00017733 | 0.00046581 | 0.059947 | 0.011438 | 0.061209 | -66.7244 | 0.038035 | -66.7368 | 56.2335 | 56.1563 | 56.2939 | -66.8238 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1506 | -67.0744 | -0.04979 | -0.062251 | 0.04961 | 0.037139 | 0.086929 | -0.13949 | -0.001829 | -0.30042 | -0.14759 | 0.031181 | 0.010412 | 0.31083 | 0.025584 | -0.1452 | 123.0075 | 122.9303 | 123.0679 | 66.812 | -123.1196 | 122.9222 | 123.0953 | 122.9246 | 66.8064 | -123.3702
596.7969 | 123.2574 | -66.7099 | 56.2637 | 0.0018314 | -0.005844 | 0.00082041 | 0.056652 | -0.0014123 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.011011 | 0.060782 | -66.729 | 0.028878 | -66.7414 | 56.2427 | 56.1517 | 56.2985 | -66.8238 | -66.7428 | 0.03241 | -66.7498 | 56.1436 | 56.3259 | 56.1689 | -67.0607 | -0.11388 | -0.021051 | -0.019056 | -0.031527 | 0.08235 | -0.11202 | 0.034793 | -0.35077 | -0.12013 | -0.032906 | -0.039939 | 0.31083 | 0.062206 | -0.094844 | 122.9526 | 122.8616 | 123.0084 | 66.7388 | -123.0875 | 122.8535 | 123.0358 | 122.8788 | 66.7423 | -123.3244
597.7969 | 123.111 | -66.7374 | 56.2683 | 0.017093 | -0.005844 | 0.0010342 | 0.056652 | -0.0018397 | 0.062582 | -0.001755 | -0.00039093 | 0.00089321 | 0.060375 | 0.011224 | 0.060782 | -66.729 | 0.042614 | -66.7277 | 56.2335 | 56.17 | 56.3077 | -66.8284 | -66.7382 | 0.036989 | -66.7636 | 56.1573 | 56.3305 | 56.1506 | -67.0607 | -0.09099 | -0.034786 | 0.00841 | 0.009674 | 0.10066 | -0.098285 | 0.039372 | -0.3233 | -0.11097 | -0.000861 | -0.026209 | 0.29709 | 0.062206 | -0.11774 | 122.9709 | 122.9074 | 123.045 | 66.78 | -123.0967 | 122.8947 | 123.0679 | 122.8879 | 66.7744 | -123.329
598.7969 | 123.1293 | -66.7557 | 56.2866 | -0.0057996 | -0.0060576 | 0.00060681 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | 0.00025007 | 0.00067941 | 0.059947 | 0.011224 | 0.060996 | -66.729 | 0.033457 | -66.7368 | 56.2381 | 56.1517 | 56.3077 | -66.8284 | -66.7336 | 0.036989 | -66.759 | 56.1482 | 56.3214 | 56.1277 | -67.0652 | -0.07268 | -0.048517 | 0.02672 | 0.018828 | 0.091508 | -0.13491 | 0.021062 | -0.30957 | -0.13844 | 0.022027 | -0.00332 | 0.30625 | 0.034739 | -0.15894 | 122.9938 | 122.9074 | 123.0634 | 66.7891 | -123.115 | 122.9039 | 123.077 | 122.8834 | 66.7927 | -123.3519
599.7969 | 123.2162 | -66.7236 | 56.2866 | 0.0094624 | -0.005844 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.011011 | 0.060996 | -66.7335 | 0.033457 | -66.7368 | 56.2335 | 56.1517 | 56.3077 | -66.8284 | -66.7428 | 0.03241 | -66.7636 | 56.1482 | 56.3259 | 56.0865 | -67.0607 | -0.10472 | -0.053096 | -0.009901 | -0.013215 | 0.091508 | -0.13491 | 0.021062 | -0.33704 | -0.13844 | -0.019173 | -0.039942 | 0.29709 | 0.039318 | -0.20015 | 122.9572 | 122.8753 | 123.0313 | 66.7571 | -123.115 | 122.8718 | 123.0496 | 122.8101 | 66.756 | -123.3473
600.7969 | 123.1338 | -66.7328 | 56.2912 | 0.0094624 | -0.005844 | 0.00082041 | 0.056652 | -0.0020533 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.060161 | 0.011011 | 0.060782 | -66.7198 | 0.038035 | -66.7368 | 56.2427 | 56.1654 | 56.3077 | -66.8284 | -66.7336 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.1735 | -67.0607 | -0.095568 | -0.048517 | 0.012989 | -0.00406 | 0.091508 | -0.12575 | 0.016484 | -0.32788 | -0.14302 | -0.000861 | -0.030787 | 0.29709 | 0.030161 | -0.11773 | 122.9755 | 122.8982 | 123.0405 | 66.7708 | -123.1196 | 122.881 | 123.0541 | 122.9063 | 66.7652 | -123.3519
601.7969 | 123.1705 | -66.7099 | 56.3004 | -0.013431 | -0.005844 | 0.0010342 | 0.056652 | -0.0018397 | 0.062796 | 0.0058755 | -0.00017733 | 0.00089321 | 0.060161 | 0.011224 | 0.060996 | -66.729 | 0.033457 | -66.746 | 56.2518 | 56.1563 | 56.3168 | -66.8284 | -66.7336 | 0.03241 | -66.7636 | 56.1528 | 56.3214 | 56.1918 | -67.0698 | -0.11846 | -0.048515 | -0.019056 | -0.036105 | 0.082351 | -0.14406 | 0.016486 | -0.35993 | -0.14759 | -0.023749 | -0.053675 | 0.30625 | 0.021006 | -0.10857 | 122.9617 | 122.8662 | 123.0267 | 66.7434 | -123.1287 | 122.8627 | 123.0313 | 122.9017 | 66.7423 | -123.3702
602.7969 | 123.1338 | -66.7648 | 56.282 | -0.013431 | -0.0054166 | 0.00082041 | 0.056438 | -0.0014123 | 0.062368 | -0.001755 | -0.00017733 | 0.00046581 | 0.059947 | 0.011438 | 0.060782 | -66.7244 | 0.033457 | -66.7414 | 56.2427 | 56.1471 | 56.2985 | -66.8284 | -66.7382 | 0.03241 | -66.7498 | 56.1528 | 56.3168 | 56.1323 | -67.0607 | -0.063524 | -0.039361 | 0.040455 | 0.023405 | 0.086929 | -0.13491 | 0.016483 | -0.29584 | -0.12928 | 0.026605 | 0.014993 | 0.31083 | 0.034739 | -0.14978 | 123.0075 | 122.912 | 123.0634 | 66.7983 | -123.1104 | 122.9176 | 123.0816 | 122.8971 | 66.7972 | -123.3427
603.7969 | 123.1567 | -66.7419 | 56.2775 | 0.0018314 | -0.0056302 | 0.00060681 | 0.056438 | -0.0020533 | 0.062796 | -0.001755 | -0.00039093 | 0.00067941 | 0.060375 | 0.011224 | 0.060782 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1517 | 56.3077 | -66.8375 | -66.7382 | 0.027831 | -66.7498 | 56.1528 | 56.3214 | 56.0865 | -67.0607 | -0.095571 | -0.034784 | 0.017566 | 0.009673 | 0.10524 | -0.12575 | 0.030217 | -0.31873 | -0.12471 | 0.003716 | -0.007896 | 0.31083 | 0.043894 | -0.19099 | 122.9846 | 122.8937 | 123.0496 | 66.78 | -123.115 | 122.8947 | 123.0633 | 122.8284 | 66.7698 | -123.3381
604.7969 | 123.0469 | -66.7419 | 56.3095 | 0.0018314 | -0.0054166 | 0.00060681 | 0.056652 | -0.0016259 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.059734 | 0.011438 | 0.060782 | -66.7198 | 0.038035 | -66.7323 | 56.2473 | 56.1609 | 56.3077 | -66.8284 | -66.7336 | 0.036989 | -66.7544 | 56.1482 | 56.3397 | 56.1185 | -67.0652 | -0.086413 | -0.062249 | 0.022144 | 0.009673 | 0.096086 | -0.14864 | -0.001826 | -0.3233 | -0.16133 | 0.008294 | -0.012475 | 0.31083 | 0.030166 | -0.19098 | 122.9892 | 122.9028 | 123.0496 | 66.78 | -123.1379 | 122.8901 | 123.0816 | 122.8605 | 66.7789 | -123.3748
605.7969 | 123.1934 | -66.7374 | 56.3049 | 0.0094624 | -0.0056302 | 0.0010342 | 0.056652 | -0.0020533 | 0.062582 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059947 | 0.011224 | 0.060996 | -66.7244 | 0.038035 | -66.7368 | 56.2381 | 56.1563 | 56.3123 | -66.8284 | -66.7382 | 0.03241 | -66.7544 | 56.1482 | 56.3214 | 56.1506 | -67.0652 | -0.09099 | -0.066828 | 0.012989 | 0.000518 | 0.091508 | -0.14864 | 0.00733 | -0.32788 | -0.15675 | -0.000861 | -0.017052 | 0.31083 | 0.016428 | -0.15436 | 122.9755 | 122.8937 | 123.0496 | 66.7754 | -123.1333 | 122.8855 | 123.0587 | 122.8879 | 66.7698 | -123.3702
606.7969 | 123.1293 | -66.7465 | 56.3095 | -0.0057996 | -0.0056302 | 0.0010342 | 0.056652 | -0.0020533 | 0.062582 | -0.0093855 | -0.00017733 | 0.00046581 | 0.060588 | 0.011011 | 0.060996 | -66.7198 | 0.033457 | -66.7414 | 56.2473 | 56.1654 | 56.3077 | -66.8284 | -66.7291 | 0.027831 | -66.759 | 56.1436 | 56.3259 | 55.9812 | -67.0652 | -0.081835 | -0.062249 | 0.026722 | 0.005094 | 0.086929 | -0.14406 | -0.001826 | -0.31873 | -0.16591 | 0.017451 | -0.012475 | 0.30625 | 0.01643 | -0.32834 | 122.9938 | 122.912 | 123.0542 | 66.78 | -123.1379 | 122.8901 | 123.0725 | 122.7277 | 66.7744 | -123.3748
607.7969 | 123.1934 | -66.7145 | 56.3095 | 0.0094624 | -0.005844 | 0.0010342 | 0.056438 | -0.0016259 | 0.062368 | -0.0093855 | -0.00039093 | 0.00046581 | 0.060375 | 0.011438 | 0.060996 | -66.729 | 0.033457 | -66.7277 | 56.2427 | 56.1654 | 56.2985 | -66.8284 | -66.7291 | 0.036989 | -66.7636 | 56.1528 | 56.3259 | 55.9949 | -67.0652 | -0.11388 | -0.066827 | -0.014478 | -0.013214 | 0.10066 | -0.14406 | -0.010983 | -0.35077 | -0.15675 | -0.014592 | -0.049097 | 0.30167 | 0.01643 | -0.31461 | 122.9572 | 122.8799 | 123.013 | 66.7479 | -123.1379 | 122.8672 | 123.0404 | 122.7094 | 66.7515 | -123.3748
608.7969 | 123.1476 | -66.7419 | 56.3095 | 0.0018314 | -0.005844 | 0.00082041 | 0.056438 | -0.0016259 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.011224 | 0.060996 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1426 | 56.3123 | -66.8329 | -66.7336 | 0.036989 | -66.759 | 56.1436 | 56.3214 | 56.0361 | -67.0698 | -0.090992 | -0.066827 | 0.017566 | 0.009673 | 0.10067 | -0.16696 | 0.002753 | -0.32788 | -0.16591 | 0.008294 | -0.017053 | 0.31083 | 0.011851 | -0.2734 | 122.9846 | 122.8845 | 123.0542 | 66.78 | -123.1424 | 122.8855 | 123.0633 | 122.7781 | 66.7789 | -123.3793
609.7969 | 123.2208 | -66.7053 | 56.3049 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056652 | -0.0018397 | 0.062796 | -0.001755 | -0.00017733 | 0.00046581 | 0.059947 | 0.011224 | 0.060782 | -66.7106 | 0.038035 | -66.7323 | 56.2427 | 56.1471 | 56.3077 | -66.8329 | -66.7336 | 0.027831 | -66.7636 | 56.1482 | 56.3168 | 56.0361 | -67.0652 | -0.12761 | -0.06225 | -0.00532 | -0.026948 | 0.10067 | -0.1578 | 0.002751 | -0.35993 | -0.15675 | -0.028327 | -0.058253 | 0.30167 | 0.01185 | -0.26882 | 122.948 | 122.8525 | 123.013 | 66.7434 | -123.1379 | 122.8535 | 123.0221 | 122.7414 | 66.7332 | -123.3702
610.7969 | 123.1567 | -66.7694 | 56.3278 | -0.013431 | -0.005844 | 0.0010342 | 0.057079 | -0.0016259 | 0.062368 | -0.001755 | 0.00025007 | 0.00067941 | 0.060161 | 0.011224 | 0.060996 | -66.7244 | 0.038035 | -66.7231 | 56.2427 | 56.1563 | 56.3077 | -66.8284 | -66.7336 | 0.03241 | -66.759 | 56.1573 | 56.3214 | 55.972 | -67.0652 | -0.058947 | -0.085138 | 0.045032 | 0.046296 | 0.10524 | -0.17153 | -0.020137 | -0.29584 | -0.17048 | 0.03576 | 0.010413 | 0.30625 | -0.00646 | -0.35581 | 123.0121 | 122.9257 | 123.0771 | 66.8074 | -123.1562 | 122.9267 | 123.0908 | 122.7414 | 66.8018 | -123.3931
611.7969 | 123.1888 | -66.7236 | 56.3049 | -0.0057996 | -0.005844 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | 0.0058755 | -0.00039093 | 0.00089321 | 0.059947 | 0.011011 | 0.060782 | -66.7244 | 0.033457 | -66.7323 | 56.2473 | 56.1609 | 56.3031 | -66.8284 | -66.7291 | 0.036989 | -66.7544 | 56.1482 | 56.3259 | 55.9857 | -67.0561 | -0.10472 | -0.057672 | -0.000744 | -0.008637 | 0.096086 | -0.14406 | -0.001828 | -0.33246 | -0.15675 | -0.005437 | -0.030785 | 0.30167 | 0.021007 | -0.31919 | 122.9709 | 122.8845 | 123.0267 | 66.7571 | -123.1333 | 122.8718 | 123.0496 | 122.7094 | 66.7606 | -123.361
612.7969 | 123.1842 | -66.7145 | 56.3095 | 0.0094624 | -0.005844 | 0.00060681 | 0.056865 | -0.0016259 | 0.062582 | 0.013506 | -0.00017733 | 0.00067941 | 0.05952 | 0.011438 | 0.060568 | -66.7198 | 0.033457 | -66.7323 | 56.2381 | 56.1563 | 56.3031 | -66.8375 | -66.7336 | 0.027831 | -66.7727 | 56.1482 | 56.3259 | 56.0453 | -67.0607 | -0.12304 | -0.071405 | -0.005321 | -0.017792 | 0.10524 | -0.15322 | -0.006405 | -0.34619 | -0.16133 | -0.019171 | -0.058254 | 0.28794 | 0.01643 | -0.26424 | 122.9526 | 122.8708 | 123.0176 | 66.7479 | -123.147 | 122.8627 | 123.0404 | 122.7597 | 66.7423 | -123.3702
613.7969 | 123.1567 | -66.7191 | 56.3004 | -0.0057996 | -0.005844 | 0.00082041 | 0.056652 | -0.0018397 | 0.062582 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059947 | 0.011438 | 0.060782 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1426 | 56.3077 | -66.8375 | -66.7336 | 0.036989 | -66.759 | 56.1436 | 56.3214 | 56.059 | -67.0652 | -0.11846 | -0.057672 | -0.005322 | -0.013215 | 0.10524 | -0.1578 | 0.007329 | -0.34619 | -0.15675 | -0.014594 | -0.039941 | 0.30625 | 0.021006 | -0.24135 | 122.9617 | 122.8616 | 123.0267 | 66.7571 | -123.1379 | 122.8627 | 123.0404 | 122.7781 | 66.756 | -123.3656
614.7969 | 123.1888 | -66.7282 | 56.2958 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | 0.00025007 | 0.00067941 | 0.059947 | 0.011438 | 0.060996 | -66.7335 | 0.033457 | -66.7368 | 56.2473 | 56.1563 | 56.3123 | -66.8375 | -66.7382 | 0.027831 | -66.759 | 56.1528 | 56.3305 | 55.972 | -67.0607 | -0.1093 | -0.048516 | -0.005324 | -0.008638 | 0.10067 | -0.13949 | 0.016486 | -0.33246 | -0.14302 | -0.010017 | -0.030786 | 0.30167 | 0.034741 | -0.32377 | 122.9755 | 122.8845 | 123.0405 | 66.7617 | -123.1333 | 122.881 | 123.0587 | 122.7002 | 66.756 | -123.3564
615.7969 | 123.1705 | -66.7465 | 56.3278 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056652 | -0.0016259 | 0.062368 | 0.013506 | 3.6274e-05 | 0.00089321 | 0.060375 | 0.011652 | 0.060782 | -66.7244 | 0.038035 | -66.7368 | 56.2427 | 56.1426 | 56.3123 | -66.8284 | -66.7336 | 0.036989 | -66.7682 | 56.1436 | 56.3214 | 56.0636 | -67.0652 | -0.081835 | -0.085138 | 0.022144 | 0.009673 | 0.091508 | -0.18527 | -0.015558 | -0.31873 | -0.18422 | 0.012872 | -0.021633 | 0.29709 | -0.00646 | -0.26424 | 122.9892 | 122.8891 | 123.0588 | 66.7846 | -123.1562 | 122.8901 | 123.0679 | 122.8101 | 66.7835 | -123.3931
616.7969 | 123.2666 | -66.7007 | 56.2592 | 0.0018314 | -0.0060576 | 0.00082041 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059947 | 0.011438 | 0.060782 | -66.729 | 0.033457 | -66.7277 | 56.2518 | 56.1471 | 56.3123 | -66.8238 | -66.7291 | 0.027831 | -66.7636 | 56.1528 | 56.3214 | 56.0727 | -67.0698 | -0.12303 | -0.007316 | -0.028211 | -0.026947 | 0.096085 | -0.11202 | 0.053107 | -0.36908 | -0.10639 | -0.028325 | -0.06283 | 0.30625 | 0.062205 | -0.18642 | 122.9526 | 122.8479 | 123.013 | 66.7342 | -123.0829 | 122.8535 | 123.0221 | 122.7735 | 66.7286 | -123.329
617.7969 | 123.2025 | -66.7053 | 56.3187 | 0.0018314 | -0.005844 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059947 | 0.011652 | 0.060782 | -66.7244 | 0.033457 | -66.7414 | 56.2335 | 56.1517 | 56.3077 | -66.8238 | -66.7382 | 0.03241 | -66.759 | 56.1528 | 56.3214 | 56.0773 | -67.0652 | -0.11846 | -0.08514 | -0.019055 | -0.036105 | 0.08235 | -0.16695 | -0.010982 | -0.35993 | -0.16591 | -0.032905 | -0.053674 | 0.30625 | 0.002695 | -0.24135 | 122.9388 | 122.857 | 123.013 | 66.7388 | -123.1424 | 122.8581 | 123.0267 | 122.7826 | 66.7377 | -123.3839
618.7969 | 123.1659 | -66.7557 | 56.3004 | 0.0018314 | -0.0056302 | 0.0012478 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059734 | 0.011011 | 0.060996 | -66.7244 | 0.038035 | -66.7323 | 56.2473 | 56.138 | 56.3077 | -66.8284 | -66.7291 | 0.03241 | -66.759 | 56.1436 | 56.3351 | 56.059 | -67.0561 | -0.07268 | -0.053094 | 0.031299 | 0.023406 | 0.096086 | -0.16238 | 0.007329 | -0.30041 | -0.15675 | 0.026606 | -0.00332 | 0.29709 | 0.034742 | -0.24135 | 123.0029 | 122.8936 | 123.0634 | 66.7937 | -123.1287 | 122.8993 | 123.0908 | 122.8147 | 66.7881 | -123.3564
619.7969 | 123.1384 | -66.7191 | 56.3095 | -0.013431 | -0.0056302 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | -0.0093855 | -0.00017733 | 0.00025221 | 0.059734 | 0.011224 | 0.060996 | -66.7198 | 0.028878 | -66.7323 | 56.2473 | 56.1563 | 56.3123 | -66.8329 | -66.7382 | 0.03241 | -66.759 | 56.1482 | 56.3214 | 56.0361 | -67.0607 | -0.11388 | -0.062249 | -0.000744 | -0.013215 | 0.10067 | -0.15322 | 0.002753 | -0.34161 | -0.16133 | -0.019172 | -0.039941 | 0.30167 | 0.011851 | -0.2734 | 122.9663 | 122.8753 | 123.0313 | 66.7479 | -123.1424 | 122.8672 | 123.0404 | 122.7552 | 66.7515 | -123.3702
620.7969 | 123.1293 | -66.7603 | 56.3187 | 0.0018314 | -0.005844 | 0.00082041 | 0.056865 | -0.0022669 | 0.062582 | -0.017016 | -0.00017733 | 0.00046581 | 0.059947 | 0.011865 | 0.060782 | -66.729 | 0.038035 | -66.7368 | 56.2381 | 56.1563 | 56.3031 | -66.8329 | -66.7336 | 0.027831 | -66.7544 | 56.1528 | 56.3305 | 56.0361 | -67.0607 | -0.072681 | -0.080561 | 0.031298 | 0.023406 | 0.096087 | -0.16238 | -0.015561 | -0.30041 | -0.16591 | 0.026605 | 0.005836 | 0.30625 | 0.011852 | -0.28256 | 122.9984 | 122.9165 | 123.0634 | 66.7983 | -123.1516 | 122.913 | 123.0908 | 122.7964 | 66.7881 | -123.3793
621.7969 | 123.2758 | -66.7099 | 56.25 | 0.0018314 | -0.005844 | 0.0014616 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.059734 | 0.011652 | 0.060996 | -66.7244 | 0.028878 | -66.7323 | 56.2381 | 56.1517 | 56.3031 | -66.8329 | -66.7291 | 0.03241 | -66.759 | 56.1528 | 56.3305 | 56.0224 | -67.0561 | -0.12304 | -0.011896 | -0.014477 | -0.02237 | 0.10067 | -0.098289 | 0.053104 | -0.34619 | -0.09724 | -0.01917 | -0.049096 | 0.29709 | 0.080517 | -0.22763 | 122.948 | 122.8616 | 123.013 | 66.7388 | -123.0829 | 122.8627 | 123.0404 | 122.7323 | 66.7423 | -123.3061
622.7969 | 123.1888 | -66.7465 | 56.3049 | 0.0018314 | -0.005844 | 0.00082041 | 0.056865 | -0.0014123 | 0.062582 | -0.0093855 | -0.00081813 | 0.00067941 | 0.059734 | 0.011438 | 0.060782 | -66.7244 | 0.033457 | -66.7368 | 56.2518 | 56.1654 | 56.3077 | -66.8284 | -66.7291 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.0086 | -67.0652 | -0.081835 | -0.053093 | 0.022144 | 0.009673 | 0.091508 | -0.13949 | 0.002751 | -0.31873 | -0.15675 | 0.017451 | -0.017054 | 0.30167 | 0.016428 | -0.29629 | 122.9984 | 122.912 | 123.0542 | 66.78 | -123.1333 | 122.8947 | 123.0679 | 122.7552 | 66.7789 | -123.3702
623.7969 | 123.1384 | -66.7236 | 56.2958 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056438 | -0.0020533 | 0.062796 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.059734 | 0.011652 | 0.060782 | -66.729 | 0.033457 | -66.7368 | 56.2427 | 56.1609 | 56.3077 | -66.8329 | -66.7336 | 0.027831 | -66.759 | 56.1482 | 56.3305 | 56.1368 | -67.0652 | -0.1093 | -0.053094 | -0.005323 | -0.013215 | 0.096087 | -0.13491 | 0.011907 | -0.34161 | -0.14759 | -0.010016 | -0.035363 | 0.30625 | 0.034741 | -0.15894 | 122.9663 | 122.8845 | 123.0313 | 66.7571 | -123.1287 | 122.8718 | 123.0542 | 122.8605 | 66.7515 | -123.361
624.7969 | 123.1567 | -66.7191 | 56.2866 | -0.0057996 | -0.0054166 | 0.0010342 | 0.056438 | -0.0018397 | 0.062582 | 0.0058755 | 0.00025007 | 0.00089321 | 0.059947 | 0.011224 | 0.061209 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1654 | 56.3077 | -66.8284 | -66.7382 | 0.036989 | -66.7498 | 56.1436 | 56.3305 | 56.1185 | -67.0607 | -0.1093 | -0.043939 | -0.005322 | -0.013215 | 0.096086 | -0.12117 | 0.021062 | -0.34161 | -0.14302 | -0.019172 | -0.030784 | 0.31083 | 0.043896 | -0.1681 | 122.9617 | 122.8845 | 123.0267 | 66.7571 | -123.115 | 122.8627 | 123.0496 | 122.8376 | 66.756 | -123.3473
625.7969 | 123.1934 | -66.7328 | 56.3324 | 0.0094624 | -0.0062714 | 0.0010342 | 0.056865 | -0.0018397 | 0.062796 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.011652 | 0.061209 | -66.729 | 0.033457 | -66.7277 | 56.2427 | 56.1563 | 56.3031 | -66.8284 | -66.7382 | 0.018674 | -66.7636 | 56.1482 | 56.3214 | 56.1231 | -67.0607 | -0.095568 | -0.089715 | 0.003832 | 0.005096 | 0.10066 | -0.17611 | -0.029293 | -0.32788 | -0.18422 | -0.005439 | -0.030787 | 0.29709 | -0.011037 | -0.20929 | 122.9755 | 122.8891 | 123.0359 | 66.7662 | -123.1608 | 122.881 | 123.0541 | 122.8559 | 66.7515 | -123.3931
626.7969 | 123.1979 | -66.7191 | 56.2546 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056865 | -0.0018397 | 0.062582 | -0.0093855 | 0.00025007 | 0.00089321 | 0.059307 | 0.011224 | 0.060996 | -66.7244 | 0.038035 | -66.7277 | 56.2427 | 56.1517 | 56.3077 | -66.8238 | -66.7291 | 0.03241 | -66.759 | 56.1573 | 56.3259 | 56.0315 | -67.0607 | -0.10472 | -0.011896 | -0.005322 | -0.008637 | 0.096085 | -0.10287 | 0.053105 | -0.34161 | -0.097239 | -0.010015 | -0.039941 | 0.30167 | 0.071361 | -0.22305 | 122.9617 | 122.8708 | 123.0267 | 66.7571 | -123.0784 | 122.8764 | 123.045 | 122.7506 | 66.7515 | -123.3152
627.7969 | 123.1979 | -66.7099 | 56.3187 | 0.0094624 | -0.005844 | 0.00060681 | 0.056438 | -0.0018397 | 0.062796 | -0.0093855 | -0.00017733 | 0.00046581 | 0.059947 | 0.011652 | 0.061423 | -66.7152 | 0.028878 | -66.7368 | 56.2335 | 56.1517 | 56.3077 | -66.8329 | -66.7382 | 0.027831 | -66.759 | 56.1528 | 56.3259 | 56.1094 | -67.0607 | -0.12304 | -0.08514 | -0.00532 | -0.026948 | 0.096087 | -0.16695 | -0.010982 | -0.35077 | -0.16591 | -0.028327 | -0.049096 | 0.30167 | 0.007274 | -0.2093 | 122.9434 | 122.8616 | 123.0176 | 66.7388 | -123.1516 | 122.8627 | 123.0358 | 122.8193 | 66.7377 | -123.3793
628.7969 | 123.1155 | -66.7511 | 56.3004 | -0.0057996 | -0.005844 | 0.0010342 | 0.056438 | -0.0016259 | 0.062368 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.059947 | 0.011652 | 0.060568 | -66.7244 | 0.033457 | -66.7368 | 56.2427 | 56.1517 | 56.3077 | -66.8238 | -66.7291 | 0.036989 | -66.7636 | 56.1436 | 56.3214 | 56.1048 | -67.0607 | -0.072678 | -0.057672 | 0.026722 | 0.014251 | 0.086929 | -0.14864 | 0.007329 | -0.30957 | -0.15675 | 0.022029 | -0.012476 | 0.29709 | 0.021006 | -0.19557 | 122.9938 | 122.9028 | 123.0588 | 66.7846 | -123.1241 | 122.8947 | 123.0725 | 122.8559 | 66.7881 | -123.361
629.7969 | 123.1888 | -66.7328 | 56.3049 | 0.0018314 | -0.0060576 | 0.00082041 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.011865 | 0.060782 | -66.7198 | 0.0243 | -66.7323 | 56.2381 | 56.1654 | 56.3123 | -66.8284 | -66.7336 | 0.027831 | -66.759 | 56.1528 | 56.3259 | 56.0361 | -67.0652 | -0.095568 | -0.066828 | 0.012989 | 0.000518 | 0.096086 | -0.13949 | 0.00733 | -0.33246 | -0.15217 | -0.000861 | -0.026208 | 0.30625 | 0.021007 | -0.26882 | 122.9709 | 122.8982 | 123.0451 | 66.7571 | -123.1333 | 122.8855 | 123.0587 | 122.7689 | 66.7606 | -123.3702
630.7969 | 123.143 | -66.7282 | 56.2866 | -0.0057996 | -0.005844 | 0.0010342 | 0.056224 | -0.0020533 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059734 | 0.011438 | 0.060568 | -66.729 | 0.028878 | -66.7277 | 56.2473 | 56.1563 | 56.3031 | -66.8238 | -66.7336 | 0.03241 | -66.7544 | 56.1482 | 56.3259 | 56.1002 | -67.0607 | -0.095567 | -0.039361 | -0.000746 | 0.000518 | 0.096085 | -0.13033 | 0.016483 | -0.33246 | -0.13844 | -0.005439 | -0.026208 | 0.30625 | 0.039318 | -0.18641 | 122.9755 | 122.8845 | 123.0313 | 66.7571 | -123.1104 | 122.8764 | 123.0541 | 122.8284 | 66.7606 | -123.3473
631.8125 | 123.143 | -66.7099 | 56.3416 | 0.0018314 | -0.0060576 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.059947 | 0.011438 | 0.060782 | -66.7244 | 0.033457 | -66.7323 | 56.2381 | 56.1654 | 56.3077 | -66.8238 | -66.7336 | 0.041567 | -66.7544 | 56.1482 | 56.3259 | 56.1552 | -67.0652 | -0.11388 | -0.10345 | -0.014477 | -0.02237 | 0.091507 | -0.17611 | -0.03387 | -0.35535 | -0.19337 | -0.023749 | -0.044518 | 0.31083 | -0.015614 | -0.1864 | 122.948 | 122.8753 | 123.0176 | 66.7434 | -123.1653 | 122.8581 | 123.0358 | 122.8651 | 66.7515 | -123.4068
632.7969 | 123.1888 | -66.7099 | 56.3187 | 0.0094624 | -0.0060576 | 0.00082041 | 0.056652 | -0.0016259 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060161 | 0.011438 | 0.060782 | -66.7244 | 0.028878 | -66.7368 | 56.2381 | 56.17 | 56.3077 | -66.8284 | -66.7382 | 0.041567 | -66.7636 | 56.1528 | 56.3259 | 56.0911 | -67.0607 | -0.11846 | -0.080561 | -0.014477 | -0.026948 | 0.091508 | -0.14864 | -0.010982 | -0.35077 | -0.16591 | -0.028327 | -0.053675 | 0.29709 | 0.007274 | -0.22761 | 122.948 | 122.8799 | 123.0176 | 66.7388 | -123.147 | 122.8627 | 123.0358 | 122.801 | 66.7515 | -123.3793
633.7969 | 123.1796 | -66.7191 | 56.3049 | 0.0018314 | -0.0056302 | 0.00082041 | 0.056865 | -0.0018397 | 0.062368 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059947 | 0.011438 | 0.060782 | -66.729 | 0.033457 | -66.7323 | 56.2427 | 56.1609 | 56.3031 | -66.8284 | -66.7382 | 0.027831 | -66.7544 | 56.1573 | 56.3214 | 56.1139 | -67.0652 | -0.1093 | -0.06225 | -0.009901 | -0.013215 | 0.096086 | -0.14406 | -0.001828 | -0.34619 | -0.14759 | -0.019172 | -0.035363 | 0.31083 | 0.016428 | -0.19099 | 122.9617 | 122.8799 | 123.0222 | 66.7525 | -123.1333 | 122.8764 | 123.0404 | 122.833 | 66.7469 | -123.3702
634.7969 | 123.1705 | -66.7191 | 56.2912 | 0.0018314 | -0.0060576 | 0.0010342 | 0.056438 | -0.0022669 | 0.062582 | -0.001755 | -0.00017733 | 0.00089321 | 0.059947 | 0.011438 | 0.060568 | -66.729 | 0.033457 | -66.7323 | 56.2381 | 56.1609 | 56.3123 | -66.8329 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3214 | 56.1139 | -67.0698 | -0.11388 | -0.053095 | -0.009901 | -0.013215 | 0.10067 | -0.13033 | 0.021063 | -0.35077 | -0.13844 | -0.014594 | -0.039941 | 0.31083 | 0.030161 | -0.17725 | 122.9572 | 122.8799 | 123.0313 | 66.7525 | -123.1241 | 122.8718 | 123.0404 | 122.833 | 66.7515 | -123.361
635.7969 | 123.1338 | -66.7603 | 56.3141 | -0.013431 | -0.005844 | 0.00082041 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.059947 | 0.011652 | 0.060782 | -66.7198 | 0.033457 | -66.7323 | 56.2427 | 56.1517 | 56.3123 | -66.8284 | -66.7336 | 0.03241 | -66.7636 | 56.1482 | 56.3214 | 56.0407 | -67.0652 | -0.068102 | -0.071405 | 0.040455 | 0.027984 | 0.096086 | -0.16238 | -0.001825 | -0.30499 | -0.16591 | 0.026605 | -0.003321 | 0.30167 | 0.007273 | -0.2734 | 123.0029 | 122.912 | 123.0725 | 66.7937 | -123.1424 | 122.9084 | 123.0816 | 122.8009 | 66.7927 | -123.3793
636.8125 | 123.1796 | -66.7282 | 56.3187 | 0.0018314 | -0.0062714 | 0.00060681 | 0.056652 | -0.0016259 | 0.062796 | -0.001755 | -0.00039093 | 0.00067941 | 0.059734 | 0.011438 | 0.060782 | -66.7198 | 0.028878 | -66.7231 | 56.2427 | 56.1563 | 56.3077 | -66.8238 | -66.7336 | 0.027831 | -66.759 | 56.1528 | 56.3214 | 56.027 | -67.0652 | -0.095567 | -0.075983 | 0.008411 | 0.005097 | 0.10066 | -0.16238 | -0.010982 | -0.33704 | -0.16591 | -0.005439 | -0.030786 | 0.30625 | 0.002695 | -0.29171 | 122.9709 | 122.8845 | 123.0359 | 66.7571 | -123.1424 | 122.881 | 123.0496 | 122.7552 | 66.756 | -123.3839
637.7969 | 123.1842 | -66.7282 | 56.3141 | -0.0057996 | -0.005844 | 0.00082041 | 0.057079 | -0.0018397 | 0.062368 | 0.0058755 | -0.00039093 | 0.00046581 | 0.059947 | 0.011438 | 0.060568 | -66.7244 | 0.033457 | -66.7323 | 56.2381 | 56.1517 | 56.3123 | -66.8284 | -66.7291 | 0.027831 | -66.7544 | 56.1482 | 56.3259 | 56.0865 | -67.0652 | -0.10015 | -0.075983 | 0.003833 | -0.00406 | 0.096086 | -0.16238 | -0.001825 | -0.33704 | -0.16591 | -0.00086 | -0.026208 | 0.31083 | 0.011852 | -0.22761 | 122.9663 | 122.8799 | 123.0405 | 66.7617 | -123.1424 | 122.8764 | 123.0541 | 122.8147 | 66.756 | -123.3793
638.7969 | 123.1705 | -66.7282 | 56.2637 | 0.0018314 | -0.005844 | 0.0010342 | 0.056438 | -0.0018397 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.059947 | 0.011438 | 0.060782 | -66.729 | 0.033457 | -66.7323 | 56.2427 | 56.1426 | 56.3077 | -66.8238 | -66.7291 | 0.036989 | -66.7636 | 56.1482 | 56.3168 | 56.0727 | -67.0652 | -0.095567 | -0.021051 | -0.000746 | -0.00406 | 0.091507 | -0.12118 | 0.04395 | -0.33704 | -0.11555 | -0.00086 | -0.035365 | 0.30167 | 0.053049 | -0.191 | 122.9709 | 122.8708 | 123.0359 | 66.7617 | -123.0875 | 122.8764 | 123.045 | 122.8009 | 66.7652 | -123.329
639.7969 | 123.1842 | -66.7007 | 56.2912 | 0.0094624 | -0.0060576 | 0.00082041 | 0.056652 | -0.0016259 | 0.062368 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059734 | 0.011652 | 0.060996 | -66.7244 | 0.028878 | -66.7323 | 56.2473 | 56.1654 | 56.3077 | -66.8329 | -66.7245 | 0.027831 | -66.759 | 56.1482 | 56.3214 | 55.9995 | -67.0652 | -0.13219 | -0.043939 | -0.023632 | -0.031525 | 0.10067 | -0.12575 | 0.016484 | -0.3645 | -0.14302 | -0.023746 | -0.058251 | 0.30625 | 0.030161 | -0.29172 | 122.948 | 122.8662 | 123.0084 | 66.7296 | -123.1241 | 122.8489 | 123.0221 | 122.7002 | 66.7286 | -123.3564
640.7969 | 123.1979 | -66.7465 | 56.3049 | 0.0018314 | -0.0060576 | 0.00060681 | 0.056652 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059734 | 0.011438 | 0.061209 | -66.7198 | 0.038035 | -66.7414 | 56.2427 | 56.1563 | 56.3123 | -66.8375 | -66.7382 | 0.036989 | -66.7636 | 56.1573 | 56.3259 | 56.0453 | -67.0652 | -0.090993 | -0.06225 | 0.026722 | 0.005094 | 0.096087 | -0.14864 | 0.00733 | -0.31873 | -0.14759 | 0.008294 | -0.017054 | 0.30167 | 0.021007 | -0.25966 | 122.9892 | 122.9028 | 123.0588 | 66.7846 | -123.1424 | 122.9039 | 123.0725 | 122.7918 | 66.7835 | -123.3702
641.8125 | 123.1567 | -66.6916 | 56.3232 | 0.0094624 | -0.005844 | 0.00082041 | 0.056438 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059734 | 0.011652 | 0.060782 | -66.7198 | 0.033457 | -66.7277 | 56.2518 | 56.1517 | 56.3077 | -66.8238 | -66.7291 | 0.03241 | -66.7544 | 56.1528 | 56.3214 | 56.0498 | -67.0607 | -0.13219 | -0.071403 | -0.02821 | -0.036103 | 0.096085 | -0.17153 | -0.015559 | -0.36908 | -0.17048 | -0.037481 | -0.062829 | 0.30625 | -0.001882 | -0.2734 | 122.9434 | 122.8433 | 122.9993 | 66.725 | -123.147 | 122.8443 | 123.0129 | 122.7414 | 66.724 | -123.3839
642.7969 | 123.175 | -66.7374 | 56.3141 | -0.0057996 | -0.0066986 | 0.0010342 | 0.056865 | -0.0020533 | 0.062368 | -0.001755 | -0.00039093 | 0.00046581 | 0.05952 | 0.011652 | 0.060996 | -66.7244 | 0.033457 | -66.7323 | 56.2427 | 56.1517 | 56.3123 | -66.8329 | -66.7291 | 0.018674 | -66.759 | 56.1528 | 56.3122 | 56.027 | -67.0652 | -0.095569 | -0.071405 | 0.012989 | 0.005096 | 0.10067 | -0.16238 | -0.001825 | -0.32788 | -0.16133 | 0.008296 | -0.02163 | 0.30625 | -0.001884 | -0.28713 | 122.98 | 122.8891 | 123.0496 | 66.7708 | -123.147 | 122.8901 | 123.0496 | 122.7643 | 66.756 | -123.3793
643.7969 | 123.2071 | -66.7191 | 56.3049 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056865 | -0.0018397 | 0.062582 | -0.001755 | -0.00039093 | 0.00089321 | 0.059734 | 0.011865 | 0.060568 | -66.7198 | 0.033457 | -66.7368 | 56.2427 | 56.1471 | 56.3077 | -66.8284 | -66.7336 | 0.041567 | -66.759 | 56.1619 | 56.3259 | 55.9812 | -67.0652 | -0.1093 | -0.06225 | -0.000744 | -0.017793 | 0.091508 | -0.1578 | 0.002751 | -0.34619 | -0.14301 | -0.014594 | -0.039941 | 0.30625 | 0.021007 | -0.32377 | 122.9617 | 122.8662 | 123.0267 | 66.7525 | -123.1333 | 122.881 | 123.045 | 122.7002 | 66.7606 | -123.3702
644.7969 | 123.2071 | -66.7099 | 56.3187 | -0.0057996 | -0.005844 | 0.00082041 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059734 | 0.012079 | 0.060568 | -66.7244 | 0.0243 | -66.7323 | 56.2473 | 56.1471 | 56.3168 | -66.8284 | -66.7291 | 0.036989 | -66.7544 | 56.1482 | 56.3259 | 56.0453 | -67.0652 | -0.11846 | -0.071405 | -0.014477 | -0.02237 | 0.096086 | -0.17153 | -0.001825 | -0.35535 | -0.17048 | -0.01917 | -0.044518 | 0.31083 | 0.007274 | -0.2734 | 122.9572 | 122.857 | 123.0267 | 66.7342 | -123.147 | 122.8581 | 123.0358 | 122.7552 | 66.7469 | -123.3839
645.7969 | 123.1567 | -66.7236 | 56.3416 | 0.0018314 | -0.0060576 | 0.0012478 | 0.056865 | -0.0016259 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059947 | 0.011865 | 0.060355 | -66.7152 | 0.028878 | -66.7277 | 56.2381 | 56.1426 | 56.3031 | -66.8192 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3259 | 55.9949 | -67.0607 | -0.095565 | -0.10345 | 0.008413 | -0.004059 | 0.091506 | -0.199 | -0.038449 | -0.33704 | -0.18879 | -0.010016 | -0.035363 | 0.30167 | -0.015614 | -0.34665 | 122.9617 | 122.8662 | 123.0267 | 66.7525 | -123.1608 | 122.8764 | 123.0496 | 122.7185 | 66.756 | -123.4022
646.8125 | 123.2208 | -66.7282 | 56.2729 | 0.0018314 | -0.0060576 | 0.00082041 | 0.057079 | -0.0018397 | 0.062582 | 0.013506 | -0.00039093 | 0.00025221 | 0.059734 | 0.011652 | 0.060782 | -66.7198 | 0.033457 | -66.7277 | 56.2381 | 56.1288 | 56.3077 | -66.8238 | -66.7291 | 0.027831 | -66.7544 | 56.1482 | 56.3305 | 56.0178 | -67.0652 | -0.095567 | -0.034784 | 0.008411 | 0.000518 | 0.096085 | -0.14407 | 0.034795 | -0.33704 | -0.12471 | -0.00086 | -0.026208 | 0.31083 | 0.057629 | -0.25509 | 122.9663 | 122.857 | 123.0359 | 66.7617 | -123.0967 | 122.8764 | 123.0587 | 122.746 | 66.756 | -123.3381
647.7969 | 123.1705 | -66.7053 | 56.3141 | -0.0057996 | -0.0060576 | 0.0010342 | 0.056652 | -0.0016259 | 0.062155 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.011438 | 0.060782 | -66.7198 | 0.028878 | -66.7277 | 56.2427 | 56.1471 | 56.3123 | -66.8238 | -66.7291 | 0.027831 | -66.759 | 56.1482 | 56.3259 | 56.0727 | -67.0652 | -0.11846 | -0.071405 | -0.014477 | -0.02237 | 0.096085 | -0.16696 | -0.001825 | -0.35993 | -0.16591 | -0.023748 | -0.053674 | 0.30625 | 0.011852 | -0.24135 | 122.948 | 122.8525 | 123.0176 | 66.7342 | -123.1379 | 122.8535 | 123.0313 | 122.7781 | 66.7332 | -123.3793
648.7969 | 123.1567 | -66.7191 | 56.3278 | 0.0018314 | -0.005844 | 0.0010342 | 0.056652 | -0.0018397 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.011438 | 0.060782 | -66.7152 | 0.033457 | -66.7231 | 56.2381 | 56.1426 | 56.3077 | -66.8284 | -66.7382 | 0.027831 | -66.759 | 56.1528 | 56.3305 | 56.0315 | -67.0607 | -0.1093 | -0.089716 | 0.003835 | -0.004058 | 0.10524 | -0.18527 | -0.020137 | -0.34161 | -0.17506 | -0.019172 | -0.039941 | 0.30167 | 0.002697 | -0.29629 | 122.9572 | 122.8616 | 123.0267 | 66.7525 | -123.1562 | 122.8718 | 123.0496 | 122.7506 | 66.7469 | -123.3885
649.7969 | 123.1888 | -66.7236 | 56.3141 | 0.0094624 | -0.005844 | 0.0010342 | 0.056865 | -0.0016259 | 0.062582 | 0.013506 | -0.00017733 | 0.00067941 | 0.05952 | 0.011438 | 0.060568 | -66.7244 | 0.028878 | -66.7323 | 56.2381 | 56.1517 | 56.3168 | -66.8284 | -66.7291 | 0.03241 | -66.7544 | 56.1528 | 56.3259 | 56.0132 | -67.0561 | -0.10472 | -0.075983 | -0.000744 | -0.008637 | 0.096086 | -0.16238 | 0.002753 | -0.33246 | -0.16133 | -0.005437 | -0.030785 | 0.30167 | 0.011852 | -0.30087 | 122.9617 | 122.8753 | 123.0405 | 66.7525 | -123.1424 | 122.8764 | 123.0496 | 122.7369 | 66.756 | -123.3702
650.7969 | 123.2025 | -66.7053 | 56.3049 | 0.0018314 | -0.006485 | 0.0010342 | 0.056652 | -0.0022669 | 0.062368 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059947 | 0.011865 | 0.060568 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1609 | 56.3031 | -66.8329 | -66.7291 | 0.041567 | -66.7544 | 56.1528 | 56.3351 | 56.059 | -67.0607 | -0.12761 | -0.06225 | -0.019055 | -0.026948 | 0.10067 | -0.14406 | -0.001828 | -0.35535 | -0.15217 | -0.023748 | -0.049096 | 0.30625 | 0.030164 | -0.24593 | 122.948 | 122.8662 | 123.0084 | 66.7434 | -123.1379 | 122.8581 | 123.0404 | 122.7643 | 66.7469 | -123.3656
651.8125 | 123.1979 | -66.687 | 56.282 | -0.0057996 | -0.005844 | 0.0010342 | 0.057079 | -0.0018397 | 0.062582 | -0.001755 | -0.00017733 | 0.00089321 | 0.05952 | 0.011652 | 0.060782 | -66.7198 | 0.033457 | -66.7277 | 56.2335 | 56.1609 | 56.3077 | -66.8329 | -66.7291 | 0.023253 | -66.759 | 56.1528 | 56.3305 | 56.0773 | -67.0607 | -0.14592 | -0.048518 | -0.032787 | -0.04068 | 0.10524 | -0.12118 | 0.02564 | -0.37366 | -0.12928 | -0.042058 | -0.071984 | 0.30167 | 0.048474 | -0.20473 | 122.9205 | 122.8479 | 122.9947 | 66.7205 | -123.115 | 122.8398 | 123.0175 | 122.7643 | 66.7103 | -123.3427
652.7969 | 123.143 | -66.7191 | 56.337 | -0.0057996 | -0.0066986 | 0.00060681 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | -0.00039093 | 0.00067941 | 0.059734 | 0.011865 | 0.060782 | -66.7244 | 0.038035 | -66.7277 | 56.2381 | 56.1609 | 56.3077 | -66.8329 | -66.7336 | 0.03241 | -66.7544 | 56.1482 | 56.3259 | 56.0956 | -67.0652 | -0.11388 | -0.098871 | -0.005322 | -0.008637 | 0.10524 | -0.17611 | -0.029292 | -0.34619 | -0.18879 | -0.014594 | -0.035363 | 0.31083 | -0.011036 | -0.24134 | 122.9572 | 122.8799 | 123.0267 | 66.7571 | -123.1699 | 122.8672 | 123.045 | 122.8147 | 66.7515 | -123.4022
653.7969 | 123.2895 | -66.687 | 56.2775 | -0.0057996 | -0.0062714 | 0.00082041 | 0.056865 | -0.0014123 | 0.062155 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.011438 | 0.060996 | -66.729 | 0.033457 | -66.7323 | 56.2427 | 56.1517 | 56.3077 | -66.8329 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3305 | 56.0727 | -67.0652 | -0.14592 | -0.034784 | -0.041944 | -0.045258 | 0.10067 | -0.12575 | 0.030217 | -0.37824 | -0.12471 | -0.046637 | -0.071984 | 0.30625 | 0.053051 | -0.20473 | 122.9297 | 122.8387 | 122.9947 | 66.7205 | -123.1104 | 122.8398 | 123.0175 | 122.7597 | 66.7194 | -123.3427
654.7969 | 123.2574 | -66.6916 | 56.2958 | 0.0018314 | -0.0066986 | 0.00082041 | 0.057079 | -0.0018397 | 0.062582 | -0.001755 | -0.00060453 | 0.00089321 | 0.059947 | 0.011865 | 0.060996 | -66.7244 | 0.028878 | -66.7368 | 56.2335 | 56.1517 | 56.3031 | -66.8284 | -66.7336 | 0.03241 | -66.759 | 56.1482 | 56.3259 | 56.0865 | -67.0698 | -0.13677 | -0.062251 | -0.032788 | -0.045259 | 0.091508 | -0.14406 | 0.007328 | -0.37824 | -0.14759 | -0.04206 | -0.067407 | 0.31083 | 0.030163 | -0.2093 | 122.9251 | 122.8433 | 122.9947 | 66.7205 | -123.1241 | 122.8398 | 123.0175 | 122.7781 | 66.724 | -123.3656
655.7969 | 123.2071 | -66.687 | 56.3095 | 0.0018314 | -0.0062714 | 0.0010342 | 0.056652 | -0.0018397 | 0.062155 | 0.021136 | 3.6274e-05 | 0.00067941 | 0.059734 | 0.011865 | 0.060782 | -66.7198 | 0.028878 | -66.7368 | 56.2381 | 56.1609 | 56.3123 | -66.8329 | -66.7336 | 0.027831 | -66.759 | 56.1573 | 56.3305 | 56.0911 | -67.0652 | -0.14592 | -0.071405 | -0.032787 | -0.049836 | 0.096087 | -0.14864 | 0.002753 | -0.37824 | -0.15217 | -0.046637 | -0.071984 | 0.30625 | 0.021008 | -0.21846 | 122.9251 | 122.8479 | 122.9993 | 66.7159 | -123.1424 | 122.8444 | 123.0175 | 122.7781 | 66.7148 | -123.3748
656.7969 | 123.1705 | -66.7191 | 56.3416 | 0.0018314 | -0.0060576 | 0.0010342 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | -0.00060453 | 0.0011068 | 0.05952 | 0.011865 | 0.060355 | -66.7244 | 0.038035 | -66.7323 | 56.2427 | 56.1609 | 56.3077 | -66.8329 | -66.7336 | 0.03241 | -66.7544 | 56.1528 | 56.3259 | 56.1048 | -67.0698 | -0.11388 | -0.098871 | -0.005322 | -0.013215 | 0.10067 | -0.18068 | -0.03387 | -0.35077 | -0.18879 | -0.014594 | -0.035363 | 0.31541 | -0.015614 | -0.23676 | 122.9617 | 122.8799 | 123.0267 | 66.7571 | -123.1745 | 122.8718 | 123.045 | 122.8238 | 66.7515 | -123.4114
657.7969 | 123.2391 | -66.6824 | 56.2454 | 0.0094624 | -0.0060576 | 0.0010342 | 0.056865 | -0.0020533 | 0.062582 | -0.0093855 | 0.00025007 | 0.0013204 | 0.059734 | 0.011438 | 0.060782 | -66.7198 | 0.038035 | -66.7323 | 56.2427 | 56.1609 | 56.3077 | -66.8329 | -66.7291 | 0.03241 | -66.7544 | 56.1482 | 56.3259 | 56.0682 | -67.0607 | -0.1505 | -0.00274 | -0.037365 | -0.049836 | 0.10067 | -0.084554 | 0.062261 | -0.37823 | -0.09724 | -0.046636 | -0.071984 | 0.30625 | 0.080517 | -0.17726 | 122.9251 | 122.8433 | 122.9901 | 66.7205 | -123.0784 | 122.8306 | 123.0084 | 122.7506 | 66.7148 | -123.3061
658.7969 | 123.2758 | -66.655 | 56.2912 | 0.0018314 | -0.0062714 | 0.0010342 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.060375 | 0.011652 | 0.060782 | -66.7244 | 0.033457 | -66.7277 | 56.2381 | 56.1471 | 56.3077 | -66.8238 | -66.7291 | 0.023253 | -66.7498 | 56.1482 | 56.3214 | 56.1414 | -67.0698 | -0.16881 | -0.053095 | -0.069409 | -0.072724 | 0.096085 | -0.14407 | 0.016484 | -0.41486 | -0.14302 | -0.074102 | -0.094871 | 0.31999 | 0.030161 | -0.14978 | 122.8931 | 122.8021 | 122.9627 | 66.6884 | -123.115 | 122.8031 | 122.9763 | 122.7964 | 66.6782 | -123.361
659.7969 | 123.2803 | -66.687 | 56.282 | -0.0057996 | -0.0062714 | 0.00082041 | 0.056865 | -0.0018397 | 0.062368 | 0.0058755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012079 | 0.060568 | -66.729 | 0.033457 | -66.7277 | 56.2335 | 56.1609 | 56.3123 | -66.8284 | -66.7336 | 0.03241 | -66.7636 | 56.1482 | 56.3259 | 56.1506 | -67.0561 | -0.14134 | -0.048518 | -0.041944 | -0.04068 | 0.10066 | -0.12118 | 0.030219 | -0.36908 | -0.13386 | -0.046637 | -0.076563 | 0.29251 | 0.043896 | -0.13147 | 122.9205 | 122.8479 | 122.9993 | 66.7205 | -123.1104 | 122.8352 | 123.013 | 122.8376 | 66.7194 | -123.3381
660.7969 | 123.2437 | -66.6779 | 56.2775 | -0.0057996 | -0.0062714 | 0.0010342 | 0.057079 | -0.0016259 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.060161 | 0.012079 | 0.060568 | -66.729 | 0.0243 | -66.7231 | 56.2381 | 56.1609 | 56.3123 | -66.8192 | -66.7336 | 0.027831 | -66.759 | 56.1482 | 56.3214 | 56.0498 | -67.0652 | -0.14134 | -0.039362 | -0.0511 | -0.045257 | 0.096085 | -0.1166 | 0.034796 | -0.38739 | -0.12928 | -0.055793 | -0.08114 | 0.30625 | 0.043894 | -0.22762 | 122.916 | 122.8387 | 122.9901 | 66.7022 | -123.0967 | 122.826 | 122.9992 | 122.7277 | 66.7057 | -123.3427
661.7969 | 123.1476 | -66.6962 | 56.3553 | 0.0094624 | -0.0060576 | 0.0012478 | 0.056438 | -0.0018397 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.059734 | 0.011652 | 0.060355 | -66.7198 | 0.028878 | -66.7368 | 56.2427 | 56.1517 | 56.3168 | -66.8284 | -66.7336 | 0.027831 | -66.759 | 56.1482 | 56.3259 | 56.1094 | -67.0652 | -0.13219 | -0.1126 | -0.023632 | -0.040681 | 0.091508 | -0.20358 | -0.038446 | -0.36908 | -0.2071 | -0.037482 | -0.062829 | 0.30625 | -0.029347 | -0.24592 | 122.9388 | 122.8479 | 123.013 | 66.725 | -123.1836 | 122.8443 | 123.0221 | 122.8055 | 66.724 | -123.4205
662.7969 | 123.23 | -66.687 | 56.2866 | 0.0094624 | -0.006485 | 0.00082041 | 0.056865 | -0.0020533 | 0.063009 | -0.0093855 | -0.00017733 | 0.00089321 | 0.059734 | 0.011652 | 0.060568 | -66.7244 | 0.028878 | -66.7323 | 56.2427 | 56.1517 | 56.3077 | -66.8284 | -66.7291 | 0.03241 | -66.7544 | 56.1482 | 56.3214 | 56.1094 | -67.0652 | -0.14134 | -0.043939 | -0.037365 | -0.045258 | 0.096086 | -0.13491 | 0.021062 | -0.37824 | -0.13844 | -0.042058 | -0.067406 | 0.31083 | 0.034739 | -0.17725 | 122.9297 | 122.8387 | 122.9947 | 66.7159 | -123.115 | 122.8352 | 123.0084 | 122.7964 | 66.7194 | -123.3519
663.7969 | 123.2117 | -66.6779 | 56.2775 | -0.0057996 | -0.0062714 | 0.0010342 | 0.056652 | -0.0020533 | 0.062582 | -0.001755 | -0.00039093 | 0.00089321 | 0.059734 | 0.011652 | 0.060355 | -66.7198 | 0.028878 | -66.7277 | 56.2427 | 56.1563 | 56.3123 | -66.8238 | -66.7291 | 0.03241 | -66.7636 | 56.139 | 56.3214 | 56.0453 | -67.0652 | -0.14592 | -0.034784 | -0.041943 | -0.049836 | 0.096085 | -0.12118 | 0.034796 | -0.38739 | -0.13844 | -0.051214 | -0.085719 | 0.30167 | 0.043894 | -0.2322 | 122.9205 | 122.8341 | 122.9901 | 66.7067 | -123.1012 | 122.8169 | 122.9992 | 122.7231 | 66.7103 | -123.3427
664.7969 | 123.2529 | -66.655 | 56.282 | 0.0094624 | -0.0062714 | 0.00082041 | 0.057079 | -0.0018397 | 0.062368 | -0.0093855 | -0.00017733 | 0.00067941 | 0.059947 | 0.011865 | 0.060568 | -66.7198 | 0.028878 | -66.7185 | 56.2381 | 56.1563 | 56.3077 | -66.8284 | -66.7336 | 0.036989 | -66.759 | 56.1482 | 56.3305 | 56.1185 | -67.0607 | -0.17339 | -0.043939 | -0.064831 | -0.063567 | 0.10982 | -0.12575 | 0.02564 | -0.4057 | -0.13386 | -0.078681 | -0.10403 | 0.30167 | 0.048474 | -0.16352 | 122.8931 | 122.8113 | 122.9627 | 66.6838 | -123.1104 | 122.8031 | 122.9855 | 122.7735 | 66.692 | -123.3427
665.7969 | 123.1201 | -66.6779 | 56.2866 | 0.0018314 | -0.0066986 | 0.00060681 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.060375 | 0.012079 | 0.060355 | -66.7198 | 0.033457 | -66.7323 | 56.2427 | 56.1471 | 56.3031 | -66.8284 | -66.7336 | 0.03241 | -66.759 | 56.1528 | 56.3259 | 56.1231 | -67.0652 | -0.1505 | -0.043939 | -0.041943 | -0.054414 | 0.096086 | -0.13949 | 0.016483 | -0.38739 | -0.13386 | -0.055793 | -0.08114 | 0.30625 | 0.039318 | -0.16352 | 122.9205 | 122.825 | 122.981 | 66.7113 | -123.115 | 122.8306 | 123.0038 | 122.801 | 66.7103 | -123.3519
666.7969 | 123.1567 | -66.7053 | 56.3599 | 0.0094624 | -0.0062714 | 0.0010342 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.060375 | 0.011865 | 0.060782 | -66.7244 | 0.028878 | -66.7323 | 56.2427 | 56.1517 | 56.3123 | -66.8284 | -66.7291 | 0.036989 | -66.7636 | 56.1482 | 56.3214 | 56.059 | -67.0652 | -0.12303 | -0.11718 | -0.019055 | -0.026948 | 0.096086 | -0.20815 | -0.047601 | -0.35993 | -0.21168 | -0.023748 | -0.058253 | 0.30167 | -0.038503 | -0.30086 | 122.948 | 122.857 | 123.0176 | 66.7342 | -123.1882 | 122.8535 | 123.0267 | 122.7643 | 66.7423 | -123.4251
667.7969 | 123.2437 | -66.7236 | 56.2454 | -0.0057996 | -0.0062714 | 0.00082041 | 0.057079 | -0.0016259 | 0.062368 | 0.013506 | 3.6274e-05 | 0.00067941 | 0.059947 | 0.011865 | 0.060568 | -66.7152 | 0.028878 | -66.7277 | 56.2381 | 56.1563 | 56.3031 | -66.8284 | -66.7245 | 0.041567 | -66.759 | 56.1482 | 56.3259 | 56.0544 | -67.0607 | -0.10472 | -0.007318 | 0.008413 | -0.004059 | 0.10066 | -0.089132 | 0.057682 | -0.33704 | -0.09724 | -0.000858 | -0.035363 | 0.30167 | 0.080517 | -0.191 | 122.9617 | 122.8799 | 123.0267 | 66.7525 | -123.0738 | 122.8718 | 123.0496 | 122.7781 | 66.7652 | -123.3061
668.7969 | 123.1979 | -66.7007 | 56.2592 | 0.0018314 | -0.0062714 | 0.0010342 | 0.057293 | -0.0018397 | 0.062796 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.011865 | 0.060782 | -66.7152 | 0.028878 | -66.7277 | 56.2381 | 56.1563 | 56.3077 | -66.8238 | -66.7336 | 0.03241 | -66.7544 | 56.1528 | 56.3214 | 56.0636 | -67.0652 | -0.12303 | -0.021051 | -0.014475 | -0.026947 | 0.096085 | -0.10287 | 0.048528 | -0.3645 | -0.10639 | -0.032904 | -0.053673 | 0.31083 | 0.062205 | -0.19557 | 122.9388 | 122.857 | 123.0084 | 66.7296 | -123.0829 | 122.8535 | 123.0221 | 122.7643 | 66.7332 | -123.3244
669.7969 | 123.2712 | -66.7007 | 56.2683 | 0.0018314 | -0.0066986 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.0093855 | -0.00017733 | 0.00067941 | 0.059734 | 0.011865 | 0.060782 | -66.7152 | 0.028878 | -66.7277 | 56.2335 | 56.1563 | 56.3077 | -66.8329 | -66.7336 | 0.03241 | -66.7636 | 56.1482 | 56.3168 | 56.1277 | -67.0652 | -0.13219 | -0.034786 | -0.014475 | -0.026947 | 0.10524 | -0.11202 | 0.039372 | -0.3645 | -0.12013 | -0.032904 | -0.06283 | 0.30167 | 0.048471 | -0.14063 | 122.9343 | 122.857 | 123.0084 | 66.7296 | -123.1012 | 122.8489 | 123.0175 | 122.8284 | 66.7332 | -123.3336
670.7969 | 123.2254 | -66.7282 | 56.2729 | 0.0018314 | -0.006485 | 0.00082041 | 0.056652 | -0.0016259 | 0.062155 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.011865 | 0.060568 | -66.7198 | 0.038035 | -66.7277 | 56.2427 | 56.1609 | 56.3123 | -66.8375 | -66.7245 | 0.027831 | -66.759 | 56.1573 | 56.3305 | 56.1139 | -67.0607 | -0.1093 | -0.030206 | 0.008411 | 0.000518 | 0.10982 | -0.11202 | 0.039374 | -0.33246 | -0.11555 | 0.003719 | -0.030786 | 0.30167 | 0.057629 | -0.15894 | 122.9709 | 122.8891 | 123.0405 | 66.7662 | -123.1104 | 122.8855 | 123.0587 | 122.8422 | 66.756 | -123.3336
671.7969 | 123.2025 | -66.6779 | 56.3141 | 0.0018314 | -0.006485 | 0.00082041 | 0.056652 | -0.0014123 | 0.062368 | -0.001755 | -0.00060453 | 0.00067941 | 0.059734 | 0.011652 | 0.060996 | -66.7244 | 0.038035 | -66.7368 | 56.2427 | 56.17 | 56.3123 | -66.8375 | -66.7291 | 0.03241 | -66.7544 | 56.1528 | 56.3214 | 56.059 | -67.0652 | -0.15966 | -0.071405 | -0.046521 | -0.058992 | 0.10067 | -0.14406 | -0.001825 | -0.38739 | -0.16133 | -0.051214 | -0.076562 | 0.31083 | 0.007273 | -0.25508 | 122.9205 | 122.8479 | 122.9901 | 66.7159 | -123.1516 | 122.8306 | 122.9992 | 122.7369 | 66.7103 | -123.3793
672.7969 | 123.2162 | -66.7099 | 56.2775 | -0.0057996 | -0.0060576 | 0.00060681 | 0.057079 | -0.0016259 | 0.062368 | -0.001755 | -0.00039093 | 0.00089321 | 0.059734 | 0.012079 | 0.060568 | -66.7244 | 0.028878 | -66.7277 | 56.2427 | 56.1563 | 56.3031 | -66.8238 | -66.7336 | 0.023253 | -66.759 | 56.1573 | 56.3259 | 56.1231 | -67.0607 | -0.11388 | -0.034784 | -0.014477 | -0.017792 | 0.096085 | -0.12118 | 0.025638 | -0.35077 | -0.12013 | -0.023749 | -0.049096 | 0.30167 | 0.048473 | -0.15436 | 122.9526 | 122.8662 | 123.013 | 66.7388 | -123.1012 | 122.8672 | 123.0358 | 122.833 | 66.7332 | -123.3381
673.7969 | 123.2117 | -66.7282 | 56.2866 | 0.0018314 | -0.0062714 | 0.00060681 | 0.057079 | -0.0018397 | 0.062368 | -0.001755 | -0.00039093 | 0.00089321 | 0.05952 | 0.011652 | 0.060355 | -66.7198 | 0.028878 | -66.7277 | 56.2427 | 56.1563 | 56.3168 | -66.8238 | -66.7291 | 0.036989 | -66.7498 | 56.1482 | 56.3259 | 56.0682 | -67.0652 | -0.095567 | -0.043939 | 0.008411 | 0.000518 | 0.096085 | -0.13033 | 0.030219 | -0.33704 | -0.13844 | -0.00086 | -0.021629 | 0.31541 | 0.039318 | -0.21846 | 122.9709 | 122.8845 | 123.0451 | 66.7571 | -123.1104 | 122.8764 | 123.0541 | 122.7964 | 66.7652 | -123.3519
674.7969 | 123.2803 | -66.7007 | 56.2683 | -0.0057996 | -0.0062714 | 0.00082041 | 0.056865 | -0.0018397 | 0.062155 | 0.0058755 | 0.00025007 | 0.00089321 | 0.05952 | 0.012079 | 0.060141 | -66.7198 | 0.028878 | -66.7323 | 56.2473 | 56.1609 | 56.3168 | -66.8284 | -66.7245 | 0.03241 | -66.7544 | 56.1528 | 56.3305 | 56.0865 | -67.0607 | -0.12761 | -0.021051 | -0.019054 | -0.031525 | 0.096086 | -0.10744 | 0.048529 | -0.35992 | -0.11555 | -0.023746 | -0.053673 | 0.30625 | 0.062206 | -0.18184 | 122.948 | 122.8616 | 123.0176 | 66.7296 | -123.0967 | 122.8535 | 123.0313 | 122.7872 | 66.7332 | -123.329
675.7969 | 123.2437 | -66.7374 | 56.2225 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056865 | -0.0020533 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.05952 | 0.011865 | 0.060355 | -66.7244 | 0.028878 | -66.7323 | 56.2427 | 56.1563 | 56.3077 | -66.8284 | -66.7291 | 0.027831 | -66.7636 | 56.1573 | 56.3259 | 56.0727 | -67.0607 | -0.09099 | 0.020148 | 0.012989 | 0.005096 | 0.096086 | -0.066244 | 0.085149 | -0.3233 | -0.065195 | 0.008296 | -0.026209 | 0.29709 | 0.1034 | -0.1498 | 122.98 | 122.8937 | 123.045 | 66.7662 | -123.0509 | 122.8947 | 123.0633 | 122.8101 | 66.7652 | -123.2832
676.7969 | 123.3261 | -66.6779 | 56.2637 | 0.0018314 | -0.006485 | 0.0010342 | 0.056865 | -0.0018397 | 0.062368 | 0.013506 | -0.00017733 | 0.00089321 | 0.059947 | 0.012079 | 0.060568 | -66.7198 | 0.028878 | -66.7277 | 56.2381 | 56.1517 | 56.3123 | -66.8375 | -66.7382 | 0.023253 | -66.7544 | 56.1528 | 56.3305 | 56.0086 | -67.0698 | -0.15966 | -0.025629 | -0.041943 | -0.049836 | 0.10982 | -0.11202 | 0.048529 | -0.39197 | -0.11097 | -0.060371 | -0.076562 | 0.31541 | 0.066784 | -0.2551 | 122.916 | 122.8296 | 122.9901 | 66.7067 | -123.1012 | 122.8306 | 123.0084 | 122.6865 | 66.7011 | -123.3336
677.7969 | 123.2758 | -66.6824 | 56.2546 | -0.013431 | -0.006485 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00046581 | 0.05952 | 0.011865 | 0.060355 | -66.7198 | 0.038035 | -66.7231 | 56.2427 | 56.1517 | 56.3077 | -66.8238 | -66.7291 | 0.03241 | -66.7636 | 56.1528 | 56.3305 | 56.0911 | -67.0652 | -0.14134 | -0.011896 | -0.037365 | -0.040679 | 0.10066 | -0.10287 | 0.053105 | -0.38281 | -0.10182 | -0.046636 | -0.081141 | 0.30167 | 0.075939 | -0.16352 | 122.9251 | 122.8341 | 122.9901 | 66.7205 | -123.0784 | 122.8352 | 123.013 | 122.7735 | 66.7148 | -123.3198
678.7969 | 123.2849 | -66.7145 | 56.2546 | -0.0057996 | -0.0062714 | 0.00082041 | 0.056652 | -0.0016259 | 0.062155 | -0.001755 | -0.00017733 | 0.0011068 | 0.05952 | 0.012079 | 0.060782 | -66.7198 | 0.038035 | -66.7277 | 56.2427 | 56.1563 | 56.3123 | -66.8238 | -66.7291 | 0.027831 | -66.7544 | 56.1436 | 56.3305 | 56.1094 | -67.0607 | -0.1093 | -0.011896 | -0.005321 | -0.013214 | 0.096085 | -0.098288 | 0.057684 | -0.34619 | -0.11098 | -0.014592 | -0.03994 | 0.30625 | 0.075939 | -0.14521 | 122.9572 | 122.8708 | 123.0267 | 66.7525 | -123.0784 | 122.8581 | 123.045 | 122.8238 | 66.7423 | -123.3152
679.7969 | 123.2529 | -66.7007 | 56.2775 | 0.0094624 | -0.0066986 | 0.00082041 | 0.056438 | -0.0016259 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.059947 | 0.012079 | 0.060355 | -66.7061 | 0.028878 | -66.7231 | 56.2381 | 56.1609 | 56.3123 | -66.8284 | -66.7291 | 0.03241 | -66.759 | 56.1573 | 56.3259 | 56.0361 | -67.0698 | -0.12761 | -0.039362 | -0.005319 | -0.022368 | 0.10524 | -0.1166 | 0.034796 | -0.36908 | -0.12013 | -0.028325 | -0.058251 | 0.31083 | 0.048473 | -0.24136 | 122.9388 | 122.8616 | 123.013 | 66.7296 | -123.1058 | 122.8581 | 123.0267 | 122.7369 | 66.7332 | -123.3473
680.7969 | 123.23 | -66.6916 | 56.282 | 0.017093 | -0.006485 | 0.00082041 | 0.056652 | -0.0016259 | 0.062155 | -0.0093855 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.011652 | 0.060568 | -66.729 | 0.033457 | -66.7277 | 56.2381 | 56.1563 | 56.3077 | -66.8238 | -66.7336 | 0.027831 | -66.7544 | 56.1528 | 56.3351 | 56.0407 | -67.0607 | -0.13219 | -0.043939 | -0.037367 | -0.036103 | 0.096085 | -0.12575 | 0.02564 | -0.36908 | -0.12928 | -0.04206 | -0.062829 | 0.30625 | 0.053053 | -0.24135 | 122.9297 | 122.8479 | 122.9993 | 66.725 | -123.1058 | 122.8443 | 123.0267 | 122.7323 | 66.7194 | -123.3427
681.7969 | 123.2254 | -66.6733 | 56.2958 | 0.0094624 | -0.0066986 | 0.00082041 | 0.056652 | -0.0018397 | 0.062582 | 0.013506 | 3.6274e-05 | 0.00067941 | 0.059734 | 0.012079 | 0.060355 | -66.7198 | 0.033457 | -66.7277 | 56.2381 | 56.1609 | 56.3077 | -66.8329 | -66.7291 | 0.036989 | -66.759 | 56.1482 | 56.3305 | 56.027 | -67.0744 | -0.15966 | -0.057672 | -0.04652 | -0.054413 | 0.10524 | -0.13491 | 0.011907 | -0.40113 | -0.14759 | -0.055791 | -0.085717 | 0.31541 | 0.034741 | -0.26882 | 122.9114 | 122.8341 | 122.981 | 66.7067 | -123.1287 | 122.8215 | 123.0038 | 122.7002 | 66.7103 | -123.3702
682.7969 | 123.2346 | -66.6733 | 56.3049 | 0.0018314 | -0.006485 | 0.00082041 | 0.056652 | -0.0020533 | 0.062368 | 0.013506 | 0.00025007 | 0.00067941 | 0.059734 | 0.011865 | 0.060782 | -66.7198 | 0.038035 | -66.7231 | 56.2427 | 56.1654 | 56.3031 | -66.8284 | -66.7382 | 0.023253 | -66.759 | 56.1482 | 56.3305 | 56.1048 | -67.0698 | -0.15508 | -0.06225 | -0.04652 | -0.049834 | 0.10524 | -0.13949 | -0.001828 | -0.39655 | -0.15675 | -0.064948 | -0.085717 | 0.31083 | 0.025585 | -0.20014 | 122.916 | 122.8387 | 122.9764 | 66.7113 | -123.1333 | 122.8215 | 123.0038 | 122.7781 | 66.6965 | -123.3748
683.7969 | 123.2346 | -66.7007 | 56.2729 | 0.0018314 | -0.0062714 | 0.00082041 | 0.056652 | -0.0020533 | 0.062368 | -0.0093855 | 3.6274e-05 | 0.00046581 | 0.059734 | 0.012079 | 0.060568 | -66.7244 | 0.028878 | -66.7231 | 56.2381 | 56.1609 | 56.3077 | -66.8192 | -66.7291 | 0.03241 | -66.7544 | 56.1528 | 56.3305 | 56.059 | -67.0652 | -0.11845 | -0.034784 | -0.023632 | -0.022368 | 0.096085 | -0.11202 | 0.034795 | -0.3645 | -0.12013 | -0.028325 | -0.053673 | 0.31083 | 0.057629 | -0.21389 | 122.9388 | 122.8616 | 123.0084 | 66.7296 | -123.0921 | 122.8535 | 123.0313 | 122.7597 | 66.7332 | -123.3381
684.7969 | 123.2574 | -66.6962 | 56.2546 | -0.0057996 | -0.006485 | 0.00060681 | 0.056865 | -0.0016259 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059734 | 0.012079 | 0.060355 | -66.7106 | 0.028878 | -66.7277 | 56.2427 | 56.1654 | 56.3031 | -66.8146 | -66.7336 | 0.027831 | -66.759 | 56.1528 | 56.3305 | 56.1048 | -67.0698 | -0.11845 | -0.011896 | -0.014475 | -0.031525 | 0.086927 | -0.089131 | 0.048526 | -0.37366 | -0.10182 | -0.037482 | -0.062829 | 0.31083 | 0.075939 | -0.14979 | 122.9388 | 122.8616 | 122.9993 | 66.725 | -123.0692 | 122.8489 | 123.0267 | 122.801 | 66.724 | -123.3244
685.7969 | 123.2758 | -66.6779 | 56.2637 | 0.0018314 | -0.006485 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | 0.0058755 | 0.00046367 | 0.00089321 | 0.059734 | 0.011865 | 0.060568 | -66.7198 | 0.028878 | -66.7323 | 56.2335 | 56.1517 | 56.3077 | -66.8238 | -66.7291 | 0.023253 | -66.7498 | 56.1482 | 56.3305 | 56.1277 | -67.0698 | -0.14592 | -0.030208 | -0.041943 | -0.054414 | 0.091507 | -0.11202 | 0.04395 | -0.39197 | -0.11555 | -0.051214 | -0.071983 | 0.31999 | 0.066784 | -0.13605 | 122.9114 | 122.8296 | 122.9855 | 66.7067 | -123.0875 | 122.826 | 123.0084 | 122.8055 | 66.7011 | -123.3336
686.7969 | 123.2025 | -66.7099 | 56.282 | 0.0094624 | -0.006485 | 0.00082041 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.012293 | 0.060782 | -66.7198 | 0.028878 | -66.7277 | 56.2335 | 56.1654 | 56.3168 | -66.8238 | -66.7291 | 0.03241 | -66.7498 | 56.1573 | 56.3259 | 56.0361 | -67.0652 | -0.11388 | -0.048518 | -0.009899 | -0.017792 | 0.096085 | -0.1166 | 0.034797 | -0.35535 | -0.1247 | -0.01917 | -0.039939 | 0.31541 | 0.043896 | -0.24593 | 122.9434 | 122.8753 | 123.0267 | 66.7388 | -123.1058 | 122.8672 | 123.0358 | 122.746 | 66.7423 | -123.3473
687.7969 | 123.1659 | -66.7145 | 56.3278 | 0.0018314 | -0.0066986 | 0.00082041 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | -0.00039093 | 0.00089321 | 0.059734 | 0.012293 | 0.060141 | -66.7198 | 0.033457 | -66.7323 | 56.2381 | 56.1609 | 56.3168 | -66.8284 | -66.7336 | 0.027831 | -66.759 | 56.1482 | 56.3305 | 56.0956 | -67.0652 | -0.11388 | -0.089716 | -0.005321 | -0.017792 | 0.096086 | -0.16695 | -0.01098 | -0.35077 | -0.17964 | -0.019171 | -0.044518 | 0.30625 | 0.002697 | -0.23219 | 122.9526 | 122.8753 | 123.0313 | 66.7479 | -123.1562 | 122.8627 | 123.045 | 122.8101 | 66.7423 | -123.3931
688.7969 | 123.1934 | -66.7145 | 56.2683 | 0.0018314 | -0.0066986 | 0.00082041 | 0.056652 | -0.0014123 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059307 | 0.012293 | 0.060568 | -66.7244 | 0.033457 | -66.7231 | 56.2427 | 56.1563 | 56.3031 | -66.8238 | -66.7291 | 0.03241 | -66.7498 | 56.1573 | 56.3305 | 56.1139 | -67.0652 | -0.1093 | -0.025629 | -0.009899 | -0.008635 | 0.10066 | -0.11202 | 0.034793 | -0.35077 | -0.11097 | -0.014592 | -0.035361 | 0.31541 | 0.062206 | -0.15436 | 122.9572 | 122.8708 | 123.0176 | 66.7479 | -123.0921 | 122.8718 | 123.045 | 122.8284 | 66.7469 | -123.3336
689.7969 | 123.2529 | -66.7099 | 56.2592 | -0.0057996 | -0.006485 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | -0.001755 | -0.00060453 | 0.00067941 | 0.05952 | 0.012293 | 0.060568 | -66.7198 | 0.038035 | -66.7231 | 56.2381 | 56.1471 | 56.3123 | -66.8329 | -66.7245 | 0.027831 | -66.7498 | 56.1573 | 56.3351 | 56.0956 | -67.0607 | -0.12304 | -0.021051 | -0.009899 | -0.013213 | 0.10982 | -0.11202 | 0.053107 | -0.35077 | -0.10182 | -0.014591 | -0.039939 | 0.31083 | 0.075941 | -0.16352 | 122.948 | 122.857 | 123.0222 | 66.7479 | -123.0921 | 122.8672 | 123.045 | 122.8055 | 66.7377 | -123.3198
690.7969 | 123.4085 | -66.6504 | 56.3004 | -0.0057996 | -0.0066986 | 0.0010342 | 0.057293 | -0.0016259 | 0.062368 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012293 | 0.060782 | -66.7198 | 0.028878 | -66.7277 | 56.2381 | 56.1471 | 56.3123 | -66.8284 | -66.7336 | 0.023253 | -66.759 | 56.1482 | 56.3259 | 56.0453 | -67.0652 | -0.17797 | -0.06225 | -0.069408 | -0.077301 | 0.10066 | -0.15322 | 0.011908 | -0.41486 | -0.15217 | -0.083258 | -0.1086 | 0.30625 | 0.025585 | -0.25509 | 122.8885 | 122.7975 | 122.9627 | 66.6793 | -123.1287 | 122.7986 | 122.9763 | 122.6957 | 66.6736 | -123.3656
691.7969 | 123.2162 | -66.7007 | 56.2866 | 0.0018314 | -0.006485 | 0.0012478 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | -0.00039093 | 0.00089321 | 0.05952 | 0.011865 | 0.060568 | -66.7198 | 0.038035 | -66.7231 | 56.2473 | 56.1426 | 56.2985 | -66.8192 | -66.7245 | 0.027831 | -66.7498 | 56.1528 | 56.3305 | 56.0453 | -67.0607 | -0.11845 | -0.039361 | -0.019054 | -0.022368 | 0.096085 | -0.14407 | 0.011905 | -0.35992 | -0.13386 | -0.023746 | -0.049094 | 0.31083 | 0.043896 | -0.24135 | 122.948 | 122.8433 | 122.9993 | 66.7388 | -123.1058 | 122.8535 | 123.0313 | 122.746 | 66.7286 | -123.3473
692.7969 | 123.2025 | -66.7419 | 56.2729 | -0.0057996 | -0.0060576 | 0.00082041 | 0.056438 | -0.0018397 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.012293 | 0.060782 | -66.7152 | 0.033457 | -66.7185 | 56.2381 | 56.1471 | 56.3168 | -66.8329 | -66.7245 | 0.03241 | -66.7453 | 56.1436 | 56.3351 | 56.0315 | -67.0698 | -0.090992 | -0.034784 | 0.026723 | 0.023408 | 0.1144 | -0.12576 | 0.043952 | -0.32788 | -0.12929 | 0.017452 | -0.003317 | 0.32457 | 0.062208 | -0.24136 | 122.98 | 122.8891 | 123.0588 | 66.7754 | -123.1058 | 122.8855 | 123.077 | 122.7735 | 66.7744 | -123.3427
693.7969 | 123.2391 | -66.7053 | 56.2592 | 0.0018314 | -0.006485 | 0.0010342 | 0.056438 | -0.0016259 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012293 | 0.060782 | -66.7198 | 0.033457 | -66.7277 | 56.2473 | 56.1609 | 56.3168 | -66.8238 | -66.7245 | 0.027831 | -66.7498 | 56.1482 | 56.3351 | 56.059 | -67.0698 | -0.11846 | -0.011895 | -0.014477 | -0.02237 | 0.096085 | -0.098287 | 0.057685 | -0.3645 | -0.11097 | -0.019169 | -0.044517 | 0.31999 | 0.075941 | -0.20015 | 122.9526 | 122.8662 | 123.0222 | 66.7388 | -123.0829 | 122.8535 | 123.0404 | 122.7643 | 66.7332 | -123.329
694.7969 | 123.2712 | -66.7465 | 56.3004 | -0.0057996 | -0.0066986 | 0.00060681 | 0.056438 | -0.0018397 | 0.062582 | -0.0093855 | -0.00017733 | 0.00089321 | 0.05952 | 0.012293 | 0.060782 | -66.7152 | 0.028878 | -66.7185 | 56.2381 | 56.1563 | 56.3168 | -66.8284 | -66.7291 | 0.03241 | -66.7544 | 56.1436 | 56.3305 | 56.0773 | -67.0698 | -0.081835 | -0.06225 | 0.031301 | 0.027986 | 0.10982 | -0.14406 | 0.016486 | -0.32331 | -0.15675 | 0.017451 | -0.007897 | 0.31541 | 0.030163 | -0.22304 | 122.9846 | 122.9028 | 123.0634 | 66.7754 | -123.1287 | 122.8901 | 123.077 | 122.8238 | 66.7789 | -123.3702
695.7969 | 123.1934 | -66.7007 | 56.2775 | -0.0057996 | -0.0066986 | 0.00082041 | 0.056865 | -0.0018397 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012079 | 0.060568 | -66.7152 | 0.028878 | -66.7277 | 56.2289 | 56.1563 | 56.3168 | -66.8192 | -66.7245 | 0.023253 | -66.7498 | 56.1528 | 56.3305 | 56.0361 | -67.0607 | -0.11845 | -0.048519 | -0.014475 | -0.026947 | 0.091506 | -0.12118 | 0.039374 | -0.35992 | -0.12471 | -0.023746 | -0.049094 | 0.31083 | 0.053051 | -0.24136 | 122.9297 | 122.857 | 123.0176 | 66.7296 | -123.0967 | 122.8535 | 123.0313 | 122.7369 | 66.724 | -123.3381
696.7969 | 123.2071 | -66.7099 | 56.2958 | 0.0018314 | -0.0069124 | 0.00082041 | 0.057079 | -0.0018397 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.012506 | 0.060355 | -66.7198 | 0.028878 | -66.7368 | 56.2427 | 56.1563 | 56.3123 | -66.8238 | -66.7291 | 0.027831 | -66.7544 | 56.1528 | 56.3305 | 56.0086 | -67.0698 | -0.11388 | -0.053094 | -0.009899 | -0.026948 | 0.086929 | -0.13949 | 0.016486 | -0.35993 | -0.14302 | -0.01917 | -0.044518 | 0.31541 | 0.034741 | -0.28714 | 122.9526 | 122.8662 | 123.0222 | 66.7388 | -123.1196 | 122.8627 | 123.0404 | 122.7185 | 66.7377 | -123.3656
697.7969 | 123.2071 | -66.7374 | 56.2866 | -0.0057996 | -0.0066986 | 0.00060681 | 0.056224 | -0.0016259 | 0.062155 | -0.0093855 | -0.00017733 | 0.00089321 | 0.059734 | 0.012293 | 0.060568 | -66.7152 | 0.033457 | -66.7277 | 56.2381 | 56.1609 | 56.3123 | -66.8238 | -66.7245 | 0.03241 | -66.759 | 56.1482 | 56.3259 | 56.0636 | -67.0698 | -0.086411 | -0.048517 | 0.022146 | 0.009674 | 0.096085 | -0.12575 | 0.025641 | -0.33246 | -0.13844 | 0.012875 | -0.02163 | 0.31083 | 0.039318 | -0.22304 | 122.9755 | 122.8982 | 123.0496 | 66.7708 | -123.1104 | 122.8855 | 123.0633 | 122.8009 | 66.7698 | -123.3564
698.7969 | 123.1018 | -66.7282 | 56.3141 | 0.0018314 | -0.0062714 | 0.00082041 | 0.056652 | -0.0016259 | 0.062582 | -0.001755 | -0.00017733 | 0.0011068 | 0.059734 | 0.011865 | 0.060568 | -66.7061 | 0.038035 | -66.7277 | 56.2427 | 56.1609 | 56.3077 | -66.8284 | -66.7245 | 0.036989 | -66.7453 | 56.1573 | 56.3305 | 56.0453 | -67.0744 | -0.10015 | -0.071405 | 0.022146 | 0.000518 | 0.10066 | -0.15322 | -0.006404 | -0.34619 | -0.15675 | 0.003719 | -0.01705 | 0.32914 | 0.01643 | -0.26882 | 122.9709 | 122.8891 | 123.0359 | 66.7662 | -123.1424 | 122.8855 | 123.0587 | 122.7735 | 66.7652 | -123.3885
699.7969 | 123.1567 | -66.7191 | 56.3141 | -0.0057996 | -0.0062714 | 0.0010342 | 0.056652 | -0.0018397 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.05952 | 0.012293 | 0.060355 | -66.7152 | 0.028878 | -66.7277 | 56.2381 | 56.17 | 56.3168 | -66.8284 | -66.7291 | 0.036989 | -66.7498 | 56.1436 | 56.3259 | 56.0636 | -67.0698 | -0.1093 | -0.075983 | 0.003835 | -0.008637 | 0.10066 | -0.14406 | 0.002753 | -0.35077 | -0.17048 | -0.010015 | -0.030784 | 0.31999 | 0.011852 | -0.25051 | 122.9572 | 122.8891 | 123.0359 | 66.7479 | -123.1424 | 122.8627 | 123.045 | 122.7826 | 66.756 | -123.3839
700.7969 | 123.1934 | -66.7053 | 56.2637 | 0.0094624 | -0.006485 | 0.0012478 | 0.056865 | -0.0016259 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059947 | 0.012079 | 0.060568 | -66.7244 | 0.0243 | -66.7231 | 56.2381 | 56.1609 | 56.3077 | -66.8192 | -66.7291 | 0.023253 | -66.7544 | 56.1528 | 56.3259 | 56.1323 | -67.0698 | -0.11388 | -0.025629 | -0.019055 | -0.017791 | 0.096085 | -0.10287 | 0.04395 | -0.3645 | -0.11097 | -0.023748 | -0.049096 | 0.31541 | 0.062206 | -0.13147 | 122.9434 | 122.8662 | 123.013 | 66.7296 | -123.0829 | 122.8581 | 123.0313 | 122.8376 | 66.7286 | -123.3336
701.7969 | 123.2803 | -66.6916 | 56.2683 | 0.0018314 | -0.0066986 | 0.00039321 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.01272 | 0.060355 | -66.7152 | 0.033457 | -66.7323 | 56.2473 | 56.1563 | 56.3168 | -66.8284 | -66.7291 | 0.023253 | -66.7544 | 56.1573 | 56.3305 | 56.1597 | -67.0698 | -0.13677 | -0.021051 | -0.023631 | -0.040681 | 0.096086 | -0.11202 | 0.048529 | -0.37824 | -0.11097 | -0.037481 | -0.062829 | 0.31541 | 0.062206 | -0.10858 | 122.9388 | 122.8479 | 123.0084 | 66.725 | -123.0967 | 122.8489 | 123.0221 | 122.8513 | 66.7148 | -123.3381
702.7969 | 123.143 | -66.7007 | 56.3004 | 0.0094624 | -0.006485 | 0.00082041 | 0.056224 | -0.0016259 | 0.062368 | 0.0058755 | -0.00039093 | 0.00046581 | 0.05952 | 0.012293 | 0.060568 | -66.7106 | 0.033457 | -66.7231 | 56.2427 | 56.1609 | 56.3168 | -66.8329 | -66.7291 | 0.03241 | -66.7544 | 56.1573 | 56.3351 | 56.0865 | -67.0652 | -0.13219 | -0.057672 | -0.009897 | -0.022368 | 0.10982 | -0.13949 | 0.016486 | -0.3645 | -0.14301 | -0.028325 | -0.053673 | 0.31083 | 0.034742 | -0.21388 | 122.9434 | 122.8616 | 123.0176 | 66.7342 | -123.1333 | 122.8581 | 123.0358 | 122.7872 | 66.7332 | -123.3656
703.7969 | 123.1338 | -66.7328 | 56.3004 | -0.0057996 | -0.0066986 | 0.0010342 | 0.056652 | -0.0020533 | 0.062582 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012293 | 0.060355 | -66.7198 | 0.038035 | -66.7323 | 56.2427 | 56.1609 | 56.3214 | -66.8238 | -66.7199 | 0.027831 | -66.7544 | 56.1573 | 56.3259 | 56.0682 | -67.0652 | -0.090989 | -0.057672 | 0.012989 | 0.000518 | 0.091507 | -0.13949 | 0.021065 | -0.33246 | -0.14301 | 0.012876 | -0.02163 | 0.31083 | 0.025585 | -0.23219 | 122.9755 | 122.8937 | 123.0542 | 66.7708 | -123.1241 | 122.8901 | 123.0587 | 122.8009 | 66.7606 | -123.3656
704.7969 | 123.1338 | -66.7603 | 56.2866 | 0.0094624 | -0.0069124 | 0.0012478 | 0.056438 | -0.0020533 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.059307 | 0.012293 | 0.060568 | -66.7198 | 0.038035 | -66.7323 | 56.2473 | 56.1426 | 56.3123 | -66.8238 | -66.7291 | 0.03241 | -66.7498 | 56.1482 | 56.3214 | 56.0132 | -67.0652 | -0.063523 | -0.039361 | 0.040455 | 0.027984 | 0.091507 | -0.14407 | 0.025641 | -0.30499 | -0.13844 | 0.031184 | 0.010415 | 0.31541 | 0.034739 | -0.2734 | 123.0075 | 122.9028 | 123.0725 | 66.7983 | -123.1104 | 122.9084 | 123.0816 | 122.7735 | 66.7927 | -123.3519
705.7969 | 123.1934 | -66.7007 | 56.2546 | 0.0018314 | -0.0066986 | 0.00060681 | 0.056865 | -0.0016259 | 0.061941 | -0.0093855 | -0.00017733 | 0.00089321 | 0.059734 | 0.012079 | 0.060355 | -66.7198 | 0.033457 | -66.7185 | 56.2427 | 56.17 | 56.3123 | -66.8284 | -66.7336 | 0.023253 | -66.7636 | 56.1528 | 56.3259 | 56.0407 | -67.0652 | -0.12761 | -0.011896 | -0.019054 | -0.01779 | 0.10982 | -0.084552 | 0.057684 | -0.3645 | -0.10182 | -0.032904 | -0.06283 | 0.30167 | 0.071361 | -0.21389 | 122.9434 | 122.8708 | 123.013 | 66.7342 | -123.0829 | 122.8535 | 123.0267 | 122.7414 | 66.724 | -123.3198
706.7969 | 123.2529 | -66.6779 | 56.2912 | 0.0018314 | -0.0069124 | 0.00060681 | 0.057079 | -0.0016259 | 0.062155 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.012506 | 0.060141 | -66.7198 | 0.0243 | -66.7277 | 56.2335 | 56.1517 | 56.3123 | -66.8329 | -66.7199 | 0.03241 | -66.759 | 56.1573 | 56.3305 | 56.027 | -67.0744 | -0.15508 | -0.057674 | -0.041943 | -0.049836 | 0.10524 | -0.13949 | 0.021063 | -0.39655 | -0.13386 | -0.042056 | -0.08114 | 0.31541 | 0.039318 | -0.26425 | 122.9114 | 122.8296 | 122.9901 | 66.7022 | -123.1241 | 122.8352 | 123.0084 | 122.7048 | 66.7103 | -123.3656
707.7969 | 123.1567 | -66.7145 | 56.3141 | -0.0057996 | -0.0066986 | 0.00082041 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059734 | 0.012506 | 0.060355 | -66.7152 | 0.033457 | -66.7277 | 56.2427 | 56.1471 | 56.3168 | -66.8284 | -66.7291 | 0.027831 | -66.7453 | 56.1528 | 56.3259 | 56.1277 | -67.0698 | -0.11388 | -0.071405 | -0.000742 | -0.013214 | 0.10066 | -0.16696 | 0.002753 | -0.35535 | -0.16133 | -0.014592 | -0.030782 | 0.32457 | 0.011852 | -0.18641 | 122.9572 | 122.8616 | 123.0313 | 66.7479 | -123.1424 | 122.8672 | 123.0404 | 122.8422 | 66.7423 | -123.3839
708.7969 | 123.0927 | -66.7191 | 56.2866 | -0.013431 | -0.0069124 | 0.00082041 | 0.056438 | -0.0016259 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059734 | 0.011865 | 0.060141 | -66.7106 | 0.028878 | -66.7323 | 56.2427 | 56.1471 | 56.3214 | -66.8329 | -66.7291 | 0.03241 | -66.7498 | 56.1528 | 56.3259 | 56.0544 | -67.0698 | -0.11388 | -0.043939 | 0.008413 | -0.013215 | 0.10067 | -0.13949 | 0.034798 | -0.35077 | -0.13386 | -0.010015 | -0.030784 | 0.31999 | 0.039318 | -0.2322 | 122.9617 | 122.8662 | 123.0405 | 66.7479 | -123.1196 | 122.8718 | 123.045 | 122.7735 | 66.7515 | -123.3564
709.7969 | 123.2025 | -66.7282 | 56.282 | -0.0057996 | -0.006485 | 0.00060681 | 0.056652 | -0.0018397 | 0.061941 | 0.0058755 | -0.00039093 | 0.00089321 | 0.059734 | 0.012079 | 0.060568 | -66.7198 | 0.033457 | -66.7231 | 56.2427 | 56.1609 | 56.3214 | -66.8284 | -66.7245 | 0.036989 | -66.7636 | 56.1528 | 56.3305 | 56.0224 | -67.0652 | -0.10015 | -0.039361 | 0.008411 | 0.005097 | 0.10524 | -0.12118 | 0.039376 | -0.33704 | -0.12928 | 0.003719 | -0.035365 | 0.30167 | 0.048474 | -0.25967 | 122.9709 | 122.8891 | 123.0496 | 66.7617 | -123.1104 | 122.881 | 123.0587 | 122.7506 | 66.7652 | -123.3473
710.7969 | 123.143 | -66.7236 | 56.3049 | -0.013431 | -0.0066986 | 0.0010342 | 0.056652 | -0.0018397 | 0.062155 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059734 | 0.012506 | 0.060355 | -66.7106 | 0.028878 | -66.7277 | 56.2473 | 56.1517 | 56.3123 | -66.8329 | -66.7245 | 0.023253 | -66.7544 | 56.139 | 56.3305 | 56.0315 | -67.0744 | -0.1093 | -0.057672 | 0.012991 | -0.004059 | 0.10524 | -0.15322 | 0.00733 | -0.35077 | -0.16591 | -0.000858 | -0.030785 | 0.31999 | 0.025585 | -0.2734 | 122.9709 | 122.8753 | 123.0359 | 66.7525 | -123.1379 | 122.8627 | 123.0542 | 122.7552 | 66.7469 | -123.3793
711.7969 | 123.2117 | -66.7374 | 56.2637 | 0.0018314 | -0.0066986 | 0.00060681 | 0.056652 | -0.0020533 | 0.062155 | 0.0058755 | -0.00039093 | 0.00089321 | 0.059734 | 0.012506 | 0.060355 | -66.7152 | 0.019721 | -66.7231 | 56.2381 | 56.1471 | 56.3214 | -66.8238 | -66.7291 | 0.023253 | -66.7544 | 56.1528 | 56.3305 | 56.0315 | -67.0744 | -0.086411 | -0.025629 | 0.022146 | 0.014253 | 0.10066 | -0.1166 | 0.057686 | -0.33704 | -0.11097 | 0.008296 | -0.017052 | 0.31999 | 0.066784 | -0.2322 | 122.9755 | 122.8845 | 123.0588 | 66.7571 | -123.0875 | 122.8901 | 123.0679 | 122.7689 | 66.7606 | -123.3381
712.7969 | 123.1888 | -66.7191 | 56.2912 | -0.0057996 | -0.0069124 | 0.00082041 | 0.056224 | -0.0018397 | 0.062155 | 0.013506 | -0.00039093 | 0.00089321 | 0.059947 | 0.012293 | 0.060141 | -66.7198 | 0.028878 | -66.7277 | 56.2427 | 56.1563 | 56.3168 | -66.8284 | -66.7336 | 0.023253 | -66.759 | 56.1528 | 56.3259 | 56.0407 | -67.0698 | -0.1093 | -0.048517 | -0.000744 | -0.008637 | 0.10066 | -0.13491 | 0.025641 | -0.35077 | -0.13844 | -0.014594 | -0.039941 | 0.31083 | 0.03474 | -0.25051 | 122.9617 | 122.8753 | 123.0359 | 66.7479 | -123.1196 | 122.8718 | 123.045 | 122.7597 | 66.7423 | -123.361
713.7969 | 123.1567 | -66.7282 | 56.2958 | -0.021062 | -0.007126 | 0.00082041 | 0.056652 | -0.0020533 | 0.062368 | -0.0093855 | -0.00017733 | 0.00046581 | 0.059307 | 0.012079 | 0.060141 | -66.7198 | 0.028878 | -66.7277 | 56.2381 | 56.1563 | 56.3214 | -66.8284 | -66.7336 | 0.027831 | -66.7544 | 56.1482 | 56.3305 | 56.0911 | -67.0652 | -0.10015 | -0.057672 | 0.008411 | 0.000518 | 0.10066 | -0.13949 | 0.025643 | -0.33704 | -0.14759 | -0.005439 | -0.026208 | 0.31083 | 0.034741 | -0.20472 | 122.9663 | 122.8845 | 123.0496 | 66.7571 | -123.1241 | 122.8764 | 123.0587 | 122.8193 | 66.756 | -123.361
714.7969 | 123.1659 | -66.7328 | 56.2912 | -0.013431 | -0.0069124 | 0.00082041 | 0.056438 | -0.0020533 | 0.062582 | 0.013506 | -0.00060453 | 0.00067941 | 0.059734 | 0.012079 | 0.060568 | -66.7152 | 0.033457 | -66.7277 | 56.2473 | 56.17 | 56.3168 | -66.8284 | -66.7336 | 0.027831 | -66.7498 | 56.1482 | 56.3305 | 56.0865 | -67.0698 | -0.095568 | -0.043939 | 0.017568 | 0.005096 | 0.10066 | -0.12117 | 0.025641 | -0.33704 | -0.14302 | -0.000861 | -0.017051 | 0.31999 | 0.039318 | -0.20472 | 122.98 | 122.9028 | 123.0496 | 66.7662 | -123.1196 | 122.881 | 123.0633 | 122.8193 | 66.7606 | -123.361
715.7969 | 123.1293 | -66.7328 | 56.3232 | -0.0057996 | -0.007126 | 0.00060681 | 0.056438 | -0.0020533 | 0.061941 | 0.013506 | -0.00017733 | 0.00089321 | 0.05952 | 0.01272 | 0.060568 | -66.7198 | 0.033457 | -66.7231 | 56.2381 | 56.1746 | 56.3168 | -66.8284 | -66.7291 | 0.03241 | -66.7544 | 56.1573 | 56.3259 | 56.1735 | -67.0698 | -0.095568 | -0.085138 | 0.012989 | 0.009675 | 0.10524 | -0.14864 | -0.006402 | -0.33704 | -0.1659 | 0.003718 | -0.02163 | 0.31541 | 0.002697 | -0.14977 | 122.9709 | 122.9074 | 123.0496 | 66.7662 | -123.1516 | 122.8901 | 123.0587 | 122.9063 | 66.7652 | -123.3931
716.7969 | 123.1293 | -66.7557 | 56.2775 | 0.0094624 | -0.0066986 | 0.00060681 | 0.056224 | -0.0018397 | 0.062582 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.012506 | 0.060355 | -66.7152 | 0.028878 | -66.7277 | 56.2381 | 56.1609 | 56.3123 | -66.8192 | -66.7336 | 0.023253 | -66.7498 | 56.1528 | 56.3259 | 56.059 | -67.0744 | -0.063522 | -0.039362 | 0.040456 | 0.027984 | 0.091506 | -0.1166 | 0.034796 | -0.31873 | -0.12471 | 0.022027 | 0.005837 | 0.32457 | 0.048473 | -0.21846 | 122.9938 | 122.9165 | 123.0679 | 66.7846 | -123.0967 | 122.9084 | 123.0816 | 122.8147 | 66.7789 | -123.3519
717.7969 | 123.1796 | -66.7191 | 56.282 | -0.0057996 | -0.0069124 | 0.00082041 | 0.056652 | -0.0020533 | 0.062582 | -0.001755 | 0.00025007 | 0.00046581 | 0.05952 | 0.012293 | 0.060355 | -66.7198 | 0.038035 | -66.7323 | 56.2518 | 56.1609 | 56.3123 | -66.8238 | -66.7245 | 0.03241 | -66.7498 | 56.1528 | 56.3259 | 56.1643 | -67.0652 | -0.10472 | -0.030204 | -0.000744 | -0.013215 | 0.091507 | -0.12118 | 0.030219 | -0.34619 | -0.12928 | -0.005436 | -0.030784 | 0.31541 | 0.043896 | -0.11773 | 122.9709 | 122.8799 | 123.0313 | 66.7571 | -123.1058 | 122.8718 | 123.045 | 122.8834 | 66.7515 | -123.3473
718.7969 | 123.1567 | -66.7419 | 56.337 | 0.0018314 | -0.006485 | 0.00060681 | 0.056438 | -0.0020533 | 0.062155 | 0.013506 | -0.00039093 | 0.00067941 | 0.059734 | 0.012506 | 0.060568 | -66.7198 | 0.033457 | -66.7368 | 56.2381 | 56.1563 | 56.3168 | -66.8238 | -66.7291 | 0.027831 | -66.7498 | 56.1436 | 56.3168 | 56.1094 | -67.0698 | -0.081834 | -0.098871 | 0.022144 | 0.005095 | 0.086929 | -0.18069 | -0.020135 | -0.32788 | -0.19337 | 0.012873 | -0.007896 | 0.31999 | -0.020193 | -0.22761 | 122.98 | 122.8982 | 123.0588 | 66.7754 | -123.1608 | 122.8855 | 123.0587 | 122.8513 | 66.7698 | -123.4068
719.7969 | 123.1522 | -66.6962 | 56.3004 | 0.0018314 | -0.0066986 | 0.00082041 | 0.056865 | -0.0016259 | 0.062368 | 0.0058755 | -0.00017733 | 0.0011068 | 0.059307 | 0.012506 | 0.060355 | -66.7106 | 0.028878 | -66.7277 | 56.2381 | 56.17 | 56.3168 | -66.8284 | -66.7245 | 0.023253 | -66.7453 | 56.1482 | 56.3259 | 56.0819 | -67.0698 | -0.13219 | -0.06225 | -0.014475 | -0.031525 | 0.10066 | -0.13033 | 0.016486 | -0.37366 | -0.15217 | -0.028324 | -0.049093 | 0.32457 | 0.025585 | -0.21846 | 122.9343 | 122.8662 | 123.013 | 66.725 | -123.1287 | 122.8443 | 123.0221 | 122.7781 | 66.7194 | -123.3702
720.7969 | 123.1384 | -66.7191 | 56.3278 | 0.0018314 | -0.0069124 | 0.00060681 | 0.056438 | -0.0020533 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.012506 | 0.059927 | -66.7152 | 0.0243 | -66.7277 | 56.2381 | 56.1609 | 56.3123 | -66.8329 | -66.7291 | 0.023253 | -66.7544 | 56.1528 | 56.3305 | 56.0682 | -67.0698 | -0.11388 | -0.089716 | 0.003835 | -0.008637 | 0.10524 | -0.16695 | -0.015558 | -0.35077 | -0.17506 | -0.010015 | -0.035363 | 0.31541 | 0.002697 | -0.25966 | 122.9572 | 122.8799 | 123.0313 | 66.7434 | -123.1608 | 122.8718 | 123.0496 | 122.7872 | 66.7423 | -123.3976
721.7969 | 123.2529 | -66.7236 | 56.2454 | -0.0057996 | -0.0062714 | 0.00082041 | 0.056865 | -0.0016259 | 0.061941 | -0.001755 | 3.6274e-05 | 0.0011068 | 0.05952 | 0.012506 | 0.060141 | -66.7152 | 0.0243 | -66.7277 | 56.2381 | 56.17 | 56.3123 | -66.8192 | -66.7245 | 0.027831 | -66.759 | 56.1619 | 56.3259 | 56.0819 | -67.0698 | -0.095565 | -0.007318 | 0.008413 | -0.004059 | 0.091506 | -0.075396 | 0.06684 | -0.34619 | -0.083505 | -0.000858 | -0.035363 | 0.31083 | 0.080517 | -0.16353 | 122.9617 | 122.8937 | 123.0359 | 66.7479 | -123.0646 | 122.8856 | 123.0496 | 122.8055 | 66.7515 | -123.3152
722.7969 | 123.1796 | -66.7236 | 56.3278 | -0.0057996 | -0.0069124 | 0.00060681 | 0.056652 | -0.0018397 | 0.062368 | 0.013506 | -0.00039093 | 0.00089321 | 0.059734 | 0.01272 | 0.060141 | -66.7152 | 0.033457 | -66.7277 | 56.2427 | 56.1609 | 56.3168 | -66.8284 | -66.7291 | 0.027831 | -66.7453 | 56.1482 | 56.3259 | 56.0819 | -67.0744 | -0.10472 | -0.085138 | 0.008413 | -0.004059 | 0.10066 | -0.16695 | -0.01098 | -0.35077 | -0.17964 | -0.005437 | -0.021627 | 0.32914 | -0.001881 | -0.24592 | 122.9663 | 122.8845 | 123.0405 | 66.7571 | -123.1562 | 122.8718 | 123.0496 | 122.8055 | 66.7515 | -123.4022
723.7969 | 123.2208 | -66.6779 | 56.2958 | 0.0018314 | -0.0069124 | 0.00060681 | 0.056652 | -0.0018397 | 0.062155 | 0.013506 | -0.00017733 | 0.00089321 | 0.05952 | 0.012506 | 0.060355 | -66.7106 | 0.028878 | -66.7231 | 56.2335 | 56.1792 | 56.3214 | -66.8284 | -66.7245 | 0.027831 | -66.759 | 56.1482 | 56.3305 | 56.1506 | -67.0698 | -0.1505 | -0.062251 | -0.032786 | -0.045257 | 0.10524 | -0.11659 | 0.025643 | -0.39197 | -0.14759 | -0.046635 | -0.08114 | 0.31083 | 0.034741 | -0.1452 | 122.9114 | 122.857 | 122.9993 | 66.7067 | -123.1241 | 122.826 | 123.0084 | 122.8284 | 66.7057 | -123.3656
724.7969 | 123.1293 | -66.7099 | 56.3416 | 0.0094624 | -0.0066986 | 0.00039321 | 0.056865 | -0.0018397 | 0.062155 | -0.001755 | -0.00017733 | 0.00089321 | 0.05952 | 0.01272 | 0.060355 | -66.7198 | 0.0243 | -66.7231 | 56.2381 | 56.17 | 56.3168 | -66.8375 | -66.7291 | 0.023253 | -66.7544 | 56.1573 | 56.3305 | 56.1094 | -67.079 | -0.12761 | -0.10345 | -0.009899 | -0.013213 | 0.1144 | -0.17153 | -0.024713 | -0.36908 | -0.18421 | -0.01917 | -0.044518 | 0.32456 | -0.011036 | -0.23219 | 122.948 | 122.8799 | 123.0267 | 66.7342 | -123.1791 | 122.8672 | 123.0404 | 122.8193 | 66.7332 | -123.4205
725.7969 | 123.1384 | -66.7145 | 56.3141 | -0.0057996 | -0.007126 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | 0.0058755 | -0.00039093 | 0.0011068 | 0.059307 | 0.012506 | 0.060141 | -66.7061 | 0.0243 | -66.7277 | 56.2427 | 56.17 | 56.3168 | -66.8329 | -66.7291 | 0.023253 | -66.7498 | 56.1436 | 56.3351 | 56.1368 | -67.0744 | -0.11846 | -0.071405 | 0.008414 | -0.013214 | 0.10524 | -0.14406 | 0.002753 | -0.35993 | -0.17048 | -0.014592 | -0.035361 | 0.32457 | 0.021009 | -0.17725 | 122.9572 | 122.8845 | 123.0313 | 66.7388 | -123.147 | 122.8581 | 123.0496 | 122.8513 | 66.7377 | -123.3885
726.7969 | 123.2574 | -66.6962 | 56.2729 | -0.013431 | -0.0066986 | 0.00060681 | 0.056438 | -0.0018397 | 0.062368 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.012079 | 0.060141 | -66.7106 | 0.0243 | -66.7231 | 56.2473 | 56.17 | 56.3214 | -66.8192 | -66.7245 | 0.023253 | -66.759 | 56.1528 | 56.3351 | 56.0636 | -67.0744 | -0.12303 | -0.025628 | -0.014475 | -0.026946 | 0.096085 | -0.10286 | 0.048531 | -0.37824 | -0.12013 | -0.028324 | -0.062829 | 0.31541 | 0.062208 | -0.20931 | 122.9434 | 122.8662 | 123.0176 | 66.7205 | -123.0921 | 122.8489 | 123.0313 | 122.7597 | 66.7194 | -123.3473
727.7969 | 123.1476 | -66.7053 | 56.3324 | 0.0094624 | -0.0066986 | 0.00082041 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.05952 | 0.012506 | 0.060141 | -66.7106 | 0.028878 | -66.7323 | 56.2473 | 56.1746 | 56.3123 | -66.8238 | -66.7382 | 0.027831 | -66.7453 | 56.1619 | 56.3351 | 56.059 | -67.0652 | -0.11846 | -0.085137 | -0.00532 | -0.026948 | 0.091507 | -0.15779 | -0.020135 | -0.35993 | -0.17048 | -0.032905 | -0.039938 | 0.31999 | 0.002699 | -0.27339 | 122.9526 | 122.8799 | 123.0176 | 66.7342 | -123.1562 | 122.8672 | 123.0404 | 122.7643 | 66.7332 | -123.3976
728.7969 | 123.143 | -66.6962 | 56.3095 | 0.0018314 | -0.007126 | 0.00082041 | 0.056438 | -0.0020533 | 0.062582 | 0.013506 | -0.00039093 | 0.00046581 | 0.059093 | 0.012506 | 0.060355 | -66.7152 | 0.0243 | -66.7277 | 56.2427 | 56.1654 | 56.3168 | -66.8284 | -66.7199 | 0.027831 | -66.7544 | 56.1482 | 56.3351 | 56.0727 | -67.0698 | -0.13219 | -0.066827 | -0.019053 | -0.031525 | 0.10066 | -0.14406 | 0.007331 | -0.37366 | -0.16133 | -0.023745 | -0.058251 | 0.31541 | 0.025587 | -0.23677 | 122.9388 | 122.8616 | 123.013 | 66.7205 | -123.1379 | 122.8443 | 123.0313 | 122.7689 | 66.724 | -123.3793
729.7969 | 123.143 | -66.7053 | 56.3232 | -0.0057996 | -0.007126 | 0.00082041 | 0.056011 | -0.0018397 | 0.062368 | 0.0058755 | -0.00039093 | 0.00046581 | 0.05952 | 0.012079 | 0.060141 | -66.7152 | 0.028878 | -66.7231 | 56.2427 | 56.1654 | 56.3123 | -66.8238 | -66.7245 | 0.027831 | -66.7498 | 56.1573 | 56.3305 | 56.1689 | -67.0744 | -0.11846 | -0.08056 | -0.009898 | -0.017791 | 0.10066 | -0.1578 | -0.01098 | -0.36908 | -0.1659 | -0.019169 | -0.044517 | 0.32457 | 0.007275 | -0.15435 | 122.948 | 122.8708 | 123.0176 | 66.7342 | -123.147 | 122.8627 | 123.0358 | 122.8742 | 66.7332 | -123.3976
730.7969 | 123.1247 | -66.7282 | 56.3278 | 0.0018314 | -0.007126 | 0.0010342 | 0.056652 | -0.0020533 | 0.062155 | -0.001755 | -0.00039093 | 0.00046581 | 0.05952 | 0.012293 | 0.060568 | -66.7061 | 0.033457 | -66.7323 | 56.2427 | 56.1654 | 56.3168 | -66.8284 | -66.7291 | 0.027831 | -66.7498 | 56.1528 | 56.3305 | 56.1139 | -67.0744 | -0.10015 | -0.085138 | 0.022146 | -0.00406 | 0.096086 | -0.16237 | -0.01098 | -0.34619 | -0.17506 | -0.00086 | -0.021629 | 0.32457 | 0.002697 | -0.21387 | 122.9709 | 122.8937 | 123.0451 | 66.7617 | -123.1562 | 122.881 | 123.0587 | 122.8422 | 66.756 | -123.4022
731.7969 | 123.175 | -66.7145 | 56.3049 | 0.0094624 | -0.0073396 | 0.00060681 | 0.056438 | -0.0020533 | 0.062582 | 0.0058755 | -0.00060453 | 0.00089321 | 0.05952 | 0.012506 | 0.060568 | -66.7152 | 0.0243 | -66.7277 | 56.2427 | 56.1609 | 56.3123 | -66.8329 | -66.7199 | 0.027831 | -66.759 | 56.1528 | 56.3351 | 56.0132 | -67.0698 | -0.11846 | -0.06225 | -0.000742 | -0.013214 | 0.10524 | -0.14406 | 0.00733 | -0.35535 | -0.15217 | -0.005434 | -0.044518 | 0.31083 | 0.030164 | -0.29172 | 122.9572 | 122.8753 | 123.0267 | 66.7388 | -123.1379 | 122.8672 | 123.0496 | 122.7277 | 66.7423 | -123.3748
732.7969 | 123.1567 | -66.7099 | 56.3095 | 0.0094624 | -0.007126 | 0.00082041 | 0.056652 | -0.0018397 | 0.062155 | 0.0058755 | -0.00017733 | 0.00046581 | 0.059734 | 0.012079 | 0.060141 | -66.7152 | 0.0243 | -66.7277 | 56.2427 | 56.17 | 56.3168 | -66.8238 | -66.7291 | 0.023253 | -66.7544 | 56.1528 | 56.3305 | 56.0865 | -67.0698 | -0.11388 | -0.066827 | -0.00532 | -0.017792 | 0.096085 | -0.13948 | 0.007331 | -0.35993 | -0.15675 | -0.01917 | -0.044518 | 0.31541 | 0.021008 | -0.22303 | 122.9526 | 122.8799 | 123.0267 | 66.7342 | -123.1333 | 122.8627 | 123.0404 | 122.7964 | 66.7332 | -123.3793
733.7969 | 123.1064 | -66.7191 | 56.3232 | 0.0018314 | -0.007126 | 0.00082041 | 0.056865 | -0.0020533 | 0.062582 | 0.0058755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012293 | 0.060355 | -66.7152 | 0.019721 | -66.7277 | 56.2381 | 56.1563 | 56.3168 | -66.8238 | -66.7291 | 0.023253 | -66.759 | 56.1528 | 56.3305 | 56.1643 | -67.0744 | -0.10472 | -0.085138 | 0.003835 | -0.008637 | 0.096085 | -0.16695 | -0.006402 | -0.35535 | -0.17048 | -0.010015 | -0.039941 | 0.31541 | 0.007275 | -0.15893 | 122.9572 | 122.8753 | 123.0359 | 66.7388 | -123.147 | 122.8718 | 123.0496 | 122.8834 | 66.7423 | -123.3976
734.7969 | 123.1659 | -66.7099 | 56.3278 | -0.0057996 | -0.0069124 | 0.00060681 | 0.056011 | -0.0020533 | 0.062368 | -0.001755 | -0.00039093 | 0.00067941 | 0.05952 | 0.01272 | 0.060568 | -66.7106 | 0.0243 | -66.7323 | 56.2427 | 56.1563 | 56.3168 | -66.8375 | -66.7291 | 0.023253 | -66.7453 | 56.1528 | 56.3214 | 56.1048 | -67.0698 | -0.12761 | -0.085138 | -0.000742 | -0.02237 | 0.10524 | -0.17153 | -0.01098 | -0.35993 | -0.17506 | -0.01917 | -0.03536 | 0.32457 | -0.00646 | -0.22303 | 122.9526 | 122.8662 | 123.0267 | 66.7342 | -123.1653 | 122.8627 | 123.0313 | 122.8147 | 66.7332 | -123.3976
735.7969 | 123.1567 | -66.7328 | 56.337 | 0.0018314 | -0.007126 | 0.00082041 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | -0.00017733 | 0.0013204 | 0.05952 | 0.01272 | 0.060355 | -66.7244 | 0.038035 | -66.7231 | 56.2473 | 56.1609 | 56.3123 | -66.8238 | -66.7245 | 0.018674 | -66.7544 | 56.1436 | 56.3305 | 56.1094 | -67.0744 | -0.090989 | -0.089715 | 0.008411 | 0.009675 | 0.10066 | -0.17611 | -0.024713 | -0.34162 | -0.19337 | 0.008297 | -0.02163 | 0.31999 | -0.006458 | -0.22761 | 122.98 | 122.8937 | 123.0451 | 66.7708 | -123.1608 | 122.8764 | 123.0633 | 122.8422 | 66.7515 | -123.4114
736.7969 | 123.1979 | -66.7099 | 56.3187 | 0.0018314 | -0.0069124 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | -0.00039093 | 0.00046581 | 0.059307 | 0.012293 | 0.060355 | -66.7152 | 0.0243 | -66.7277 | 56.2381 | 56.1609 | 56.3168 | -66.8238 | -66.7291 | 0.027831 | -66.7498 | 56.1528 | 56.3305 | 56.0453 | -67.0744 | -0.11388 | -0.080561 | -0.00532 | -0.017792 | 0.096085 | -0.1578 | -0.001825 | -0.3645 | -0.16591 | -0.01917 | -0.039939 | 0.32457 | 0.011852 | -0.2734 | 122.948 | 122.8708 | 123.0267 | 66.7342 | -123.1424 | 122.8627 | 123.0404 | 122.7552 | 66.7377 | -123.3931
737.7969 | 123.1384 | -66.7053 | 56.3278 | 0.0094624 | -0.006485 | 0.00082041 | 0.056011 | -0.0018397 | 0.062155 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.01272 | 0.060355 | -66.7198 | 0.028878 | -66.7277 | 56.2518 | 56.1563 | 56.3214 | -66.8238 | -66.7336 | 0.023253 | -66.759 | 56.1573 | 56.3259 | 56.0956 | -67.0744 | -0.11846 | -0.075981 | -0.014477 | -0.02237 | 0.096085 | -0.17153 | -0.006401 | -0.36908 | -0.17048 | -0.028327 | -0.053674 | 0.31541 | -0.001881 | -0.23219 | 122.9572 | 122.8616 | 123.0267 | 66.7342 | -123.1516 | 122.8627 | 123.0313 | 122.801 | 66.7286 | -123.4022
738.7969 | 123.1705 | -66.7053 | 56.337 | 0.0094624 | -0.0069124 | 0.00039321 | 0.056652 | -0.0018397 | 0.062582 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059307 | 0.012506 | 0.060141 | -66.7198 | 0.019721 | -66.7277 | 56.2427 | 56.1746 | 56.3214 | -66.8284 | -66.7199 | 0.027831 | -66.7498 | 56.1482 | 56.3305 | 56.0498 | -67.0698 | -0.12303 | -0.094293 | -0.014477 | -0.02237 | 0.10066 | -0.16237 | -0.015556 | -0.3645 | -0.18879 | -0.01459 | -0.044517 | 0.31999 | -0.006458 | -0.28713 | 122.948 | 122.8799 | 123.0267 | 66.725 | -123.1653 | 122.8535 | 123.0358 | 122.7552 | 66.7332 | -123.4068
739.7969 | 123.1705 | -66.687 | 56.3004 | 0.0018314 | -0.0069124 | 0.00082041 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | -0.00017733 | 0.00089321 | 0.059734 | 0.01272 | 0.060355 | -66.7152 | 0.019721 | -66.7277 | 56.2427 | 56.1609 | 56.3077 | -66.8238 | -66.7291 | 0.018674 | -66.7498 | 56.1436 | 56.3214 | 56.0682 | -67.0744 | -0.13677 | -0.057672 | -0.028208 | -0.04068 | 0.096085 | -0.13949 | 0.007329 | -0.38739 | -0.15675 | -0.042058 | -0.062827 | 0.32457 | 0.021006 | -0.23219 | 122.9297 | 122.8479 | 122.9947 | 66.7067 | -123.1241 | 122.8306 | 123.0084 | 122.7552 | 66.7057 | -123.3748
740.7969 | 123.1293 | -66.7099 | 56.3232 | -0.013431 | -0.007126 | 0.00060681 | 0.056224 | -0.0020533 | 0.061941 | -0.001755 | -0.00039093 | 0.0011068 | 0.059734 | 0.012506 | 0.059927 | -66.7198 | 0.0243 | -66.7277 | 56.2381 | 56.1654 | 56.3168 | -66.8284 | -66.7291 | 0.018674 | -66.7544 | 56.1573 | 56.3259 | 56.0911 | -67.0744 | -0.11846 | -0.085138 | -0.009899 | -0.017792 | 0.10066 | -0.1578 | -0.006402 | -0.3645 | -0.1659 | -0.01917 | -0.044518 | 0.31999 | 0.002697 | -0.23219 | 122.948 | 122.8753 | 123.0267 | 66.7342 | -123.1516 | 122.8672 | 123.0358 | 122.801 | 66.7286 | -123.3976
741.7969 | 123.111 | -66.7419 | 56.3141 | -0.013431 | -0.0069124 | 0.00060681 | 0.056438 | -0.0018397 | 0.062155 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059734 | 0.012506 | 0.060355 | -66.7106 | 0.028878 | -66.7231 | 56.2473 | 56.1654 | 56.326 | -66.8329 | -66.7336 | 0.023253 | -66.7453 | 56.1573 | 56.3305 | 56.0865 | -67.079 | -0.090992 | -0.066827 | 0.031301 | 0.01883 | 0.10982 | -0.14864 | 0.01191 | -0.33704 | -0.15675 | 0.008294 | -0.003317 | 0.33372 | 0.01643 | -0.22761 | 122.9892 | 122.9074 | 123.0679 | 66.7708 | -123.147 | 122.8993 | 123.0725 | 122.8284 | 66.7652 | -123.3931
742.7969 | 123.1293 | -66.7374 | 56.282 | -0.013431 | -0.0069124 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00046581 | 0.05952 | 0.01272 | 0.060355 | -66.7244 | 0.038035 | -66.7231 | 56.2427 | 56.1654 | 56.3123 | -66.8238 | -66.7291 | 0.018674 | -66.7498 | 56.1528 | 56.3305 | 56.0956 | -67.0698 | -0.086411 | -0.039361 | 0.012989 | 0.014253 | 0.10066 | -0.1166 | 0.030219 | -0.33246 | -0.12928 | 0.008296 | -0.012473 | 0.31999 | 0.048474 | -0.18641 | 122.98 | 122.9028 | 123.0496 | 66.7754 | -123.1058 | 122.8901 | 123.0679 | 122.833 | 66.756 | -123.3519
743.7969 | 123.2803 | -66.687 | 56.2683 | 0.0094624 | -0.0069124 | 0.00082041 | 0.056865 | -0.0018397 | 0.062582 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.059734 | 0.012506 | 0.060355 | -66.7198 | 0.0243 | -66.7231 | 56.2381 | 56.1609 | 56.3123 | -66.8238 | -66.7245 | 0.014095 | -66.7544 | 56.1573 | 56.3351 | 56.0636 | -67.0744 | -0.13677 | -0.030207 | -0.032787 | -0.036101 | 0.10066 | -0.10744 | 0.043951 | -0.38739 | -0.11097 | -0.037479 | -0.067406 | 0.31999 | 0.066785 | -0.20473 | 122.9251 | 122.8479 | 122.9993 | 66.7113 | -123.0921 | 122.8444 | 123.0221 | 122.7506 | 66.7011 | -123.3427
744.7969 | 123.262 | -66.6779 | 56.3095 | 0.0018314 | -0.007126 | 0.00082041 | 0.056652 | -0.0018397 | 0.062368 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059307 | 0.012506 | 0.060355 | -66.7152 | 0.028878 | -66.7231 | 56.2381 | 56.17 | 56.3168 | -66.8238 | -66.7245 | 0.018674 | -66.7453 | 56.1528 | 56.3351 | 56.0819 | -67.0698 | -0.14592 | -0.071405 | -0.037364 | -0.045257 | 0.10066 | -0.13948 | 0.007331 | -0.39197 | -0.15675 | -0.046635 | -0.067404 | 0.32457 | 0.025587 | -0.22761 | 122.916 | 122.8479 | 122.9947 | 66.7067 | -123.1333 | 122.8306 | 123.013 | 122.7598 | 66.6965 | -123.3793
745.7969 | 123.2208 | -66.6779 | 56.3232 | -0.0057996 | -0.0066986 | 0.00060681 | 0.056652 | -0.0018397 | 0.062582 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059307 | 0.012506 | 0.060141 | -66.7152 | 0.033457 | -66.7231 | 56.2335 | 56.1517 | 56.326 | -66.8284 | -66.7199 | 0.027831 | -66.7498 | 56.1573 | 56.3351 | 56.1323 | -67.0744 | -0.1505 | -0.089717 | -0.037364 | -0.045257 | 0.10524 | -0.17153 | 0.002755 | -0.39655 | -0.1659 | -0.042056 | -0.071983 | 0.32457 | 0.011854 | -0.19098 | 122.9114 | 122.8296 | 123.0039 | 66.7113 | -123.1516 | 122.8352 | 123.013 | 122.8101 | 66.7057 | -123.3976
746.7969 | 123.1476 | -66.7236 | 56.3141 | 0.0018314 | -0.0069124 | 0.00082041 | 0.056438 | -0.0020533 | 0.061941 | -0.0093855 | -0.00017733 | 0.00067941 | 0.05952 | 0.012506 | 0.060355 | -66.7152 | 0.0243 | -66.7185 | 56.2381 | 56.1563 | 56.3168 | -66.8192 | -66.7291 | 0.023253 | -66.7498 | 56.1482 | 56.3397 | 56.059 | -67.0744 | -0.095565 | -0.075983 | 0.008413 | 0.005098 | 0.10066 | -0.1578 | 0.002753 | -0.35077 | -0.16591 | -0.005437 | -0.026206 | 0.32457 | 0.025588 | -0.25508 | 122.9617 | 122.8799 | 123.0405 | 66.7479 | -123.1333 | 122.8718 | 123.0633 | 122.7826 | 66.7469 | -123.3885
747.7969 | 123.1293 | -66.7282 | 56.3232 | 0.0094624 | -0.007126 | 0.00060681 | 0.056438 | -0.0020533 | 0.062368 | -0.0093855 | 3.6274e-05 | 0.0011068 | 0.059307 | 0.012506 | 0.060141 | -66.7106 | 0.028878 | -66.7277 | 56.2518 | 56.17 | 56.3168 | -66.8238 | -66.7245 | 0.018674 | -66.7544 | 56.1573 | 56.3259 | 56.0453 | -67.0744 | -0.095567 | -0.071403 | 0.017568 | 0.000518 | 0.096085 | -0.15322 | -0.006402 | -0.34619 | -0.1659 | 0.003719 | -0.026208 | 0.31999 | 0.002697 | -0.27797 | 122.98 | 122.8982 | 123.0451 | 66.7571 | -123.147 | 122.8855 | 123.0541 | 122.7735 | 66.7469 | -123.3976
748.7969 | 123.2071 | -66.7007 | 56.2958 | 0.0094624 | -0.0069124 | 0.00082041 | 0.056224 | -0.0016259 | 0.062155 | 0.0058755 | -0.00060453 | 0.00067941 | 0.05952 | 0.01272 | 0.060355 | -66.7152 | 0.019721 | -66.7277 | 56.2427 | 56.1609 | 56.3214 | -66.8329 | -66.7245 | 0.018674 | -66.7453 | 56.1528 | 56.3351 | 56.1323 | -67.0652 | -0.13219 | -0.053094 | -0.014475 | -0.026947 | 0.10524 | -0.13491 | 0.025643 | -0.3645 | -0.14302 | -0.023746 | -0.044515 | 0.31999 | 0.03932 | -0.16352 | 122.9434 | 122.8616 | 123.0222 | 66.7205 | -123.1287 | 122.8535 | 123.0358 | 122.833 | 66.7194 | -123.361
749.7969 | 123.2346 | -66.6504 | 56.282 | 0.0094624 | -0.007126 | 0.00060681 | 0.056224 | -0.0018397 | 0.062368 | -0.001755 | -0.00017733 | 0.00046581 | 0.059734 | 0.012506 | 0.060141 | -66.7152 | 0.0243 | -66.7277 | 56.2381 | 56.1654 | 56.3168 | -66.8238 | -66.7336 | 0.018674 | -66.759 | 56.1573 | 56.3305 | 56.178 | -67.0698 | -0.17339 | -0.043939 | -0.064829 | -0.077301 | 0.096085 | -0.1166 | 0.034797 | -0.41944 | -0.1247 | -0.083258 | -0.1086 | 0.31083 | 0.048474 | -0.104 | 122.8885 | 122.8158 | 122.9672 | 66.6747 | -123.1058 | 122.8077 | 122.9809 | 122.8284 | 66.6691 | -123.3519
750.7969 | 123.2529 | -66.6641 | 56.2958 | -0.0057996 | -0.0069124 | 0.00060681 | 0.056652 | -0.0018397 | 0.062155 | 0.013506 | -0.00039093 | 0.00089321 | 0.05952 | 0.01272 | 0.060141 | -66.7244 | 0.019721 | -66.7231 | 56.2473 | 56.1563 | 56.3168 | -66.8238 | -66.7245 | 0.018674 | -66.7453 | 56.1528 | 56.3351 | 56.1048 | -67.0744 | -0.15965 | -0.048516 | -0.060253 | -0.058989 | 0.10066 | -0.13949 | 0.021064 | -0.41028 | -0.14302 | -0.060367 | -0.081136 | 0.32914 | 0.03932 | -0.19099 | 122.9114 | 122.8204 | 122.981 | 66.6838 | -123.1196 | 122.8169 | 122.9992 | 122.7689 | 66.6828 | -123.3702
751.7969 | 123.2346 | -66.6733 | 56.3049 | 0.0018314 | -0.0069124 | 0.00082041 | 0.056652 | -0.0020533 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.05952 | 0.012934 | 0.060141 | -66.7152 | 0.028878 | -66.7231 | 56.2427 | 56.1517 | 56.3168 | -66.8284 | -66.7291 | 0.023253 | -66.7498 | 56.1482 | 56.3305 | 56.0315 | -67.079 | -0.15508 | -0.06225 | -0.041941 | -0.049834 | 0.10524 | -0.15322 | 0.011908 | -0.4057 | -0.15675 | -0.055791 | -0.07656 | 0.32914 | 0.025585 | -0.2734 | 122.916 | 122.825 | 122.9901 | 66.7022 | -123.1333 | 122.8215 | 123.0038 | 122.7048 | 66.6965 | -123.3839
752.7969 | 123.2391 | -66.6595 | 56.3141 | 0.0018314 | -0.0069124 | 0.00039321 | 0.056652 | -0.0018397 | 0.062582 | -0.001755 | -0.00017733 | 0.00089321 | 0.059307 | 0.012934 | 0.060141 | -66.7061 | 0.028878 | -66.7277 | 56.2473 | 56.1654 | 56.3168 | -66.8284 | -66.7291 | 0.014095 | -66.7544 | 56.1528 | 56.3305 | 56.0956 | -67.0698 | -0.16881 | -0.066827 | -0.046518 | -0.068146 | 0.10066 | -0.14864 | 0.002753 | -0.41028 | -0.16133 | -0.069524 | -0.094872 | 0.31541 | 0.01643 | -0.21845 | 122.9068 | 122.825 | 122.9764 | 66.6884 | -123.1424 | 122.8123 | 122.9901 | 122.7552 | 66.6736 | -123.3839
753.7969 | 123.3353 | -66.655 | 56.3736 | 0.017093 | -0.0066986 | 0.0010342 | 0.056224 | -0.0018397 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.01272 | 0.060141 | -66.7152 | 0.028878 | -66.7277 | 56.2427 | 56.1654 | 56.3168 | -66.8284 | -66.7245 | 0.018674 | -66.7636 | 56.1619 | 56.3351 | 56.0453 | -67.0698 | -0.17339 | -0.13091 | -0.060252 | -0.072724 | 0.10066 | -0.20815 | -0.056756 | -0.41486 | -0.21168 | -0.069523 | -0.10861 | 0.30625 | -0.0385 | -0.32833 | 122.8976 | 122.8204 | 122.9718 | 66.6838 | -123.202 | 122.8169 | 122.9901 | 122.7002 | 66.6736 | -123.4434
754.7969 | 123.2208 | -66.6687 | 56.3187 | 0.0018314 | -0.0069124 | 0.00039321 | 0.056438 | -0.0020533 | 0.062155 | 0.0058755 | -0.00039093 | 0.00046581 | 0.05952 | 0.01272 | 0.060141 | -66.7106 | 0.019721 | -66.7277 | 56.2427 | 56.1563 | 56.3214 | -66.8192 | -66.7245 | 0.023253 | -66.759 | 56.1528 | 56.3351 | 56.1506 | -67.0698 | -0.1505 | -0.075983 | -0.041941 | -0.058991 | 0.091506 | -0.16238 | 0.002754 | -0.40113 | -0.16591 | -0.05579 | -0.090295 | 0.31083 | 0.016431 | -0.16809 | 122.9114 | 122.825 | 122.9901 | 66.6884 | -123.1379 | 122.8215 | 123.0038 | 122.8193 | 66.692 | -123.3885
755.7969 | 123.1659 | -66.6824 | 56.3461 | 0.0094624 | -0.0069124 | 0.00082041 | 0.056438 | -0.0018397 | 0.062155 | 0.0058755 | -0.00039093 | 0.00089321 | 0.05952 | 0.012293 | 0.060355 | -66.7152 | 0.0243 | -66.714 | 56.2427 | 56.17 | 56.3123 | -66.8238 | -66.7291 | 0.018674 | -66.7453 | 56.1482 | 56.3351 | 56.1002 | -67.079 | -0.14134 | -0.10345 | -0.032786 | -0.031523 | 0.10982 | -0.1761 | -0.033868 | -0.39655 | -0.19795 | -0.046636 | -0.062826 | 0.33372 | -0.011034 | -0.24592 | 122.9251 | 122.8525 | 122.9947 | 66.7067 | -123.1699 | 122.8306 | 123.0175 | 122.7826 | 66.7011 | -123.4251
756.7969 | 123.2025 | -66.6824 | 56.3141 | 0.0094624 | -0.007126 | 0.0010342 | 0.056438 | -0.0020533 | 0.062155 | 0.0058755 | -0.00017733 | 0.00089321 | 0.05952 | 0.01272 | 0.060141 | -66.7152 | 0.0243 | -66.7323 | 56.2381 | 56.17 | 56.3123 | -66.8284 | -66.7291 | 0.018674 | -66.7498 | 56.1528 | 56.3305 | 56.1094 | -67.0744 | -0.14592 | -0.075983 | -0.032786 | -0.049836 | 0.096086 | -0.14406 | -0.001825 | -0.39197 | -0.16133 | -0.046636 | -0.067405 | 0.32457 | 0.01643 | -0.20472 | 122.9205 | 122.8525 | 122.9947 | 66.7067 | -123.1424 | 122.8352 | 123.013 | 122.7918 | 66.7011 | -123.3885
757.7969 | 123.2803 | -66.687 | 56.2958 | -0.0057996 | -0.007126 | 0.00060681 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059307 | 0.01272 | 0.060355 | -66.7198 | 0.028878 | -66.7277 | 56.2473 | 56.1517 | 56.3168 | -66.8192 | -66.7199 | 0.014095 | -66.7498 | 56.1528 | 56.3397 | 56.1139 | -67.0698 | -0.13219 | -0.048516 | -0.032787 | -0.04068 | 0.091506 | -0.14406 | 0.021064 | -0.38281 | -0.14302 | -0.0329 | -0.062827 | 0.31999 | 0.043899 | -0.18183 | 122.9343 | 122.8387 | 123.0039 | 66.7159 | -123.115 | 122.8398 | 123.0267 | 122.801 | 66.7011 | -123.3656
758.7969 | 123.2666 | -66.6687 | 56.2866 | 0.0018314 | -0.007126 | 0.00082041 | 0.056865 | -0.0020533 | 0.062155 | 0.0058755 | -0.00060453 | 0.00046581 | 0.05952 | 0.012934 | 0.060141 | -66.7106 | 0.028878 | -66.7368 | 56.2427 | 56.1654 | 56.3214 | -66.8284 | -66.7291 | 0.018674 | -66.7544 | 56.1528 | 56.3351 | 56.1552 | -67.0698 | -0.15966 | -0.043939 | -0.041941 | -0.068147 | 0.091508 | -0.12117 | 0.034798 | -0.40113 | -0.13386 | -0.060369 | -0.085717 | 0.31541 | 0.048475 | -0.13147 | 122.9114 | 122.8341 | 122.9901 | 66.6976 | -123.115 | 122.8215 | 123.0038 | 122.8239 | 66.6874 | -123.3564
759.7969 | 123.175 | -66.7053 | 56.282 | -0.0057996 | -0.007126 | 0.0010342 | 0.056652 | -0.0018397 | 0.062155 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.059307 | 0.01272 | 0.060568 | -66.7152 | 0.028878 | -66.7323 | 56.2473 | 56.1654 | 56.3214 | -66.8284 | -66.7291 | 0.018674 | -66.7498 | 56.1573 | 56.3397 | 56.1323 | -67.0744 | -0.12303 | -0.034783 | -0.009898 | -0.026948 | 0.096086 | -0.1166 | 0.039376 | -0.36908 | -0.1247 | -0.023748 | -0.044517 | 0.32457 | 0.057632 | -0.14978 | 122.9526 | 122.8708 | 123.0267 | 66.7342 | -123.1104 | 122.8627 | 123.045 | 122.8376 | 66.724 | -123.3564
760.7969 | 123.2483 | -66.6641 | 56.282 | 0.0094624 | -0.0073396 | 0.00082041 | 0.056865 | -0.0020533 | 0.062368 | -0.0093855 | -0.00039093 | 0.00067941 | 0.058879 | 0.01272 | 0.060355 | -66.7106 | 0.015142 | -66.7231 | 56.2381 | 56.1654 | 56.3214 | -66.8284 | -66.7291 | 0.018674 | -66.7544 | 56.1482 | 56.3351 | 56.1643 | -67.0698 | -0.16423 | -0.043939 | -0.046518 | -0.058989 | 0.10524 | -0.1166 | 0.039376 | -0.4057 | -0.13386 | -0.064946 | -0.090294 | 0.31541 | 0.053053 | -0.11773 | 122.9022 | 122.8296 | 122.9855 | 66.6793 | -123.1104 | 122.8123 | 122.9992 | 122.8284 | 66.6828 | -123.3519
761.7969 | 123.2483 | -66.6687 | 56.3095 | 0.0018314 | -0.007126 | 0.00082041 | 0.056865 | -0.0018397 | 0.062368 | -0.001755 | -0.00060453 | 0.0011068 | 0.05952 | 0.013147 | 0.060141 | -66.7152 | 0.0243 | -66.7277 | 56.2381 | 56.1609 | 56.3168 | -66.8238 | -66.7291 | 0.014095 | -66.7453 | 56.1528 | 56.3397 | 56.1139 | -67.0698 | -0.15508 | -0.071405 | -0.046519 | -0.058991 | 0.096085 | -0.14864 | 0.007331 | -0.40113 | -0.15675 | -0.060369 | -0.076559 | 0.32457 | 0.030166 | -0.19556 | 122.9068 | 122.8296 | 122.9855 | 66.693 | -123.1333 | 122.8215 | 123.0084 | 122.7826 | 66.6828 | -123.3793
762.7969 | 123.2437 | -66.655 | 56.3004 | 0.0018314 | -0.0069124 | 0.00060681 | 0.056652 | -0.0020533 | 0.061941 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059307 | 0.01272 | 0.060141 | -66.7106 | 0.015142 | -66.7323 | 56.2427 | 56.1563 | 56.3123 | -66.8284 | -66.7245 | 0.014095 | -66.7498 | 56.1528 | 56.3397 | 56.0865 | -67.0698 | -0.17339 | -0.057672 | -0.055674 | -0.077302 | 0.096086 | -0.14406 | 0.011908 | -0.41486 | -0.14759 | -0.069523 | -0.094871 | 0.31999 | 0.039321 | -0.21388 | 122.8976 | 122.8113 | 122.9672 | 66.6701 | -123.1287 | 122.8077 | 122.9946 | 122.7414 | 66.6691 | -123.3702
763.7969 | 123.2574 | -66.6595 | 56.3004 | 0.0018314 | -0.0069124 | 0.00082041 | 0.056438 | -0.0020533 | 0.061941 | -0.0093855 | 0.00025007 | 0.00067941 | 0.059307 | 0.013361 | 0.060141 | -66.7152 | 0.015142 | -66.7277 | 56.2381 | 56.1654 | 56.3214 | -66.8238 | -66.7291 | 0.014095 | -66.7453 | 56.1573 | 56.3351 | 56.1002 | -67.0652 | -0.16423 | -0.06225 | -0.055674 | -0.068146 | 0.096085 | -0.13491 | 0.021065 | -0.4057 | -0.14301 | -0.069524 | -0.085714 | 0.31999 | 0.034742 | -0.20014 | 122.8976 | 122.825 | 122.981 | 66.6747 | -123.1241 | 122.8169 | 122.9946 | 122.7598 | 66.6736 | -123.3656
764.7969 | 123.2346 | -66.6687 | 56.2958 | 0.0018314 | -0.0075534 | 0.0010342 | 0.056865 | -0.0018397 | 0.061941 | -0.001755 | -0.00017733 | 0.00067941 | 0.059734 | 0.013147 | 0.059927 | -66.7198 | 0.015142 | -66.7277 | 56.2381 | 56.17 | 56.3168 | -66.8284 | -66.7199 | 0.018674 | -66.7544 | 56.1528 | 56.3397 | 56.0773 | -67.0698 | -0.15966 | -0.057672 | -0.051098 | -0.058991 | 0.10066 | -0.12575 | 0.021064 | -0.40113 | -0.14302 | -0.051211 | -0.085717 | 0.31541 | 0.043899 | -0.21846 | 122.9068 | 122.8387 | 122.9855 | 66.6838 | -123.1241 | 122.8215 | 123.0084 | 122.746 | 66.6874 | -123.3656
765.7969 | 123.2117 | -66.7099 | 56.282 | -0.0057996 | -0.0073396 | 0.00082041 | 0.056865 | -0.0016259 | 0.062582 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.012934 | 0.059714 | -66.7106 | 0.028878 | -66.7185 | 56.2473 | 56.17 | 56.3214 | -66.8329 | -66.7245 | 0.018674 | -66.7544 | 56.1573 | 56.3351 | 56.0819 | -67.0744 | -0.12304 | -0.034783 | -0.000742 | -0.008635 | 0.1144 | -0.11202 | 0.039376 | -0.3645 | -0.1247 | -0.014591 | -0.044518 | 0.31999 | 0.053053 | -0.20015 | 122.9572 | 122.8799 | 123.0313 | 66.7388 | -123.115 | 122.8672 | 123.045 | 122.7918 | 66.7286 | -123.3564
766.7969 | 123.1659 | -66.6733 | 56.3782 | -0.0057996 | -0.007126 | 0.00060681 | 0.056224 | -0.0020533 | 0.062155 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.01272 | 0.060141 | -66.7152 | 0.0243 | -66.7185 | 56.2427 | 56.1563 | 56.326 | -66.8329 | -66.7245 | 0.014095 | -66.7544 | 56.1482 | 56.3351 | 56.1368 | -67.0652 | -0.15966 | -0.13549 | -0.041941 | -0.045256 | 0.1144 | -0.22188 | -0.052177 | -0.39197 | -0.22999 | -0.051212 | -0.081139 | 0.31083 | -0.043078 | -0.24133 | 122.916 | 122.8296 | 122.9993 | 66.6976 | -123.2111 | 122.8215 | 123.0084 | 122.8101 | 66.6874 | -123.4434
767.7969 | 123.2162 | -66.6962 | 56.282 | -0.0057996 | -0.0069124 | 0.00060681 | 0.056865 | -0.0018397 | 0.062155 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059734 | 0.01272 | 0.059927 | -66.7106 | 0.028878 | -66.7277 | 56.2427 | 56.1654 | 56.3168 | -66.8238 | -66.7199 | 0.023253 | -66.7498 | 56.1528 | 56.3305 | 56.0773 | -67.0744 | -0.12761 | -0.039361 | -0.014475 | -0.031525 | 0.096085 | -0.1166 | 0.034797 | -0.37824 | -0.12928 | -0.023745 | -0.053672 | 0.32457 | 0.048474 | -0.20473 | 122.9388 | 122.8616 | 123.013 | 66.725 | -123.1058 | 122.8489 | 123.0267 | 122.7735 | 66.7194 | -123.3564
768.7969 | 123.2529 | -66.6779 | 56.2866 | 0.0018314 | -0.007126 | 0.00060681 | 0.056865 | -0.0018397 | 0.061941 | -0.001755 | -0.00017733 | 0.00046581 | 0.059307 | 0.013361 | 0.060355 | -66.7244 | 0.019721 | -66.7231 | 56.2473 | 56.1654 | 56.3123 | -66.8192 | -66.7245 | 0.014095 | -66.7498 | 56.1528 | 56.3351 | 56.178 | -67.0652 | -0.14134 | -0.039361 | -0.046521 | -0.045257 | 0.096085 | -0.12117 | 0.025641 | -0.38739 | -0.13386 | -0.046635 | -0.071983 | 0.31541 | 0.048475 | -0.10857 | 122.9251 | 122.8433 | 122.9901 | 66.6976 | -123.1058 | 122.8306 | 123.013 | 122.8559 | 66.692 | -123.3519
769.7969 | 123.1979 | -66.6824 | 56.282 | -0.0057996 | -0.0073396 | 0.00060681 | 0.056865 | -0.0020533 | 0.061941 | -0.0093855 | -0.00017733 | 0.00067941 | 0.059307 | 0.01272 | 0.060355 | -66.7106 | 0.0243 | -66.7231 | 56.2427 | 56.1517 | 56.3168 | -66.8238 | -66.7245 | 0.023253 | -66.7498 | 56.1573 | 56.3305 | 56.0682 | -67.0698 | -0.14134 | -0.039361 | -0.028208 | -0.040679 | 0.10066 | -0.13033 | 0.034797 | -0.38739 | -0.1247 | -0.042057 | -0.067405 | 0.31999 | 0.048474 | -0.21388 | 122.9251 | 122.8341 | 122.9993 | 66.7067 | -123.1058 | 122.8398 | 123.013 | 122.7506 | 66.7057 | -123.3519
770.7969 | 123.2895 | -66.6824 | 56.3095 | 0.0018314 | -0.0069124 | 0.00060681 | 0.056865 | -0.0018397 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.01272 | 0.060568 | -66.7015 | 0.0243 | -66.7231 | 56.2381 | 56.1563 | 56.3123 | -66.8238 | -66.7245 | 0.018674 | -66.7453 | 56.1528 | 56.3351 | 56.1002 | -67.0698 | -0.14134 | -0.071405 | -0.019051 | -0.040679 | 0.10066 | -0.15322 | 0.002753 | -0.38739 | -0.15675 | -0.042057 | -0.062826 | 0.32457 | 0.025587 | -0.2093 | 122.9205 | 122.8387 | 122.9947 | 66.7067 | -123.1333 | 122.8352 | 123.0175 | 122.7826 | 66.7011 | -123.3793
771.7969 | 123.2803 | -66.6779 | 56.2958 | 0.0018314 | -0.0075534 | 0.00060681 | 0.056652 | -0.0018397 | 0.062155 | 0.0058755 | -0.00017733 | 0.00046581 | 0.05952 | 0.01272 | 0.060141 | -66.7152 | 0.0243 | -66.7231 | 56.2427 | 56.1517 | 56.3214 | -66.8192 | -66.7245 | 0.014095 | -66.7498 | 56.1528 | 56.3351 | 56.0132 | -67.0744 | -0.14134 | -0.053094 | -0.037364 | -0.045257 | 0.096085 | -0.14406 | 0.025643 | -0.39655 | -0.14302 | -0.046635 | -0.071983 | 0.32457 | 0.03932 | -0.28256 | 122.9205 | 122.8296 | 122.9993 | 66.7022 | -123.115 | 122.8306 | 123.013 | 122.6911 | 66.692 | -123.3702
772.7969 | 123.2117 | -66.6916 | 56.2912 | 0.0018314 | -0.007126 | 0.00082041 | 0.056438 | -0.0016259 | 0.061941 | -0.001755 | -0.00017733 | 0.00067941 | 0.059307 | 0.012934 | 0.060141 | -66.7106 | 0.0243 | -66.7277 | 56.2473 | 56.1471 | 56.3214 | -66.8284 | -66.7245 | 0.027831 | -66.7498 | 56.1528 | 56.3305 | 56.0727 | -67.0652 | -0.13677 | -0.043939 | -0.019053 | -0.036103 | 0.10066 | -0.14407 | 0.03022 | -0.37366 | -0.13844 | -0.032902 | -0.05825 | 0.31541 | 0.039318 | -0.21846 | 122.9388 | 122.8387 | 123.013 | 66.7159 | -123.1196 | 122.8443 | 123.0221 | 122.7643 | 66.7194 | -123.3564
773.7969 | 123.2117 | -66.7053 | 56.2729 | -0.0057996 | -0.007126 | 0.00060681 | 0.056865 | -0.0022669 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.012934 | 0.060141 | -66.7106 | 0.0243 | -66.7231 | 56.2473 | 56.1334 | 56.326 | -66.8238 | -66.7245 | 0.018674 | -66.7498 | 56.1573 | 56.3351 | 56.0086 | -67.0744 | -0.11846 | -0.025628 | -0.00532 | -0.017791 | 0.10066 | -0.13949 | 0.053109 | -0.36908 | -0.11555 | -0.019169 | -0.044517 | 0.32457 | 0.062208 | -0.26425 | 122.9526 | 122.8387 | 123.0313 | 66.7296 | -123.0967 | 122.8627 | 123.0404 | 122.714 | 66.724 | -123.3473
774.7969 | 123.2162 | -66.7053 | 56.2592 | -0.013431 | -0.007126 | 0.00082041 | 0.057079 | -0.0020533 | 0.062368 | -0.017016 | -0.00039093 | 0.00089321 | 0.05952 | 0.013361 | 0.059714 | -66.7152 | 0.0243 | -66.7277 | 56.2518 | 56.1334 | 56.3214 | -66.8192 | -66.7199 | 0.018674 | -66.7498 | 56.1573 | 56.3397 | 56.0636 | -67.0698 | -0.11388 | -0.007316 | -0.009898 | -0.02237 | 0.091506 | -0.12576 | 0.062264 | -0.3645 | -0.10182 | -0.01459 | -0.044517 | 0.31999 | 0.08052 | -0.19557 | 122.9572 | 122.8387 | 123.0267 | 66.7296 | -123.0784 | 122.8627 | 123.045 | 122.7689 | 66.724 | -123.329
775.7969 | 123.2071 | -66.687 | 56.2912 | -0.0057996 | -0.007126 | 0.0010342 | 0.057079 | -0.0018397 | 0.061941 | -0.001755 | -0.00017733 | 0.0011068 | 0.059307 | 0.01272 | 0.060141 | -66.7106 | 0.010564 | -66.7277 | 56.2381 | 56.1609 | 56.3168 | -66.8284 | -66.7245 | 0.027831 | -66.7544 | 56.1528 | 56.3351 | 55.972 | -67.0698 | -0.14134 | -0.053095 | -0.02363 | -0.04068 | 0.10066 | -0.13033 | 0.025641 | -0.38281 | -0.13844 | -0.037479 | -0.067406 | 0.31541 | 0.043897 | -0.31919 | 122.9251 | 122.8479 | 123.0039 | 66.6976 | -123.1196 | 122.8398 | 123.0221 | 122.659 | 66.7148 | -123.361
776.7969 | 123.2758 | -66.6733 | 56.3004 | 0.0094624 | -0.007126 | 0.0010342 | 0.056652 | -0.0024807 | 0.061941 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.05952 | 0.013147 | 0.060568 | -66.7106 | 0.0243 | -66.7277 | 56.2381 | 56.1517 | 56.3214 | -66.8192 | -66.7245 | 0.018674 | -66.7453 | 56.1619 | 56.3305 | 56.027 | -67.0698 | -0.14592 | -0.06225 | -0.037363 | -0.054413 | 0.091506 | -0.14864 | 0.021065 | -0.39655 | -0.13844 | -0.051212 | -0.071981 | 0.32457 | 0.030163 | -0.2734 | 122.9114 | 122.825 | 122.9947 | 66.6976 | -123.1196 | 122.8352 | 123.0038 | 122.7002 | 66.692 | -123.3702
777.7969 | 123.23 | -66.687 | 56.2729 | 0.0018314 | -0.007126 | 0.00060681 | 0.056865 | -0.0020533 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.05952 | 0.013147 | 0.060355 | -66.7061 | 0.0243 | -66.7185 | 56.2518 | 56.1654 | 56.3214 | -66.8238 | -66.7291 | 0.023253 | -66.7498 | 56.1528 | 56.3397 | 56.0773 | -67.0698 | -0.13677 | -0.021049 | -0.019052 | -0.031523 | 0.10524 | -0.10744 | 0.048531 | -0.38281 | -0.12013 | -0.042058 | -0.062827 | 0.31999 | 0.066787 | -0.19557 | 122.9389 | 122.8525 | 123.0084 | 66.7113 | -123.0967 | 122.8398 | 123.0267 | 122.7643 | 66.7103 | -123.3427
778.7969 | 123.2346 | -66.6824 | 56.2637 | -0.0057996 | -0.0073396 | 0.00060681 | 0.056652 | -0.0020533 | 0.062155 | -0.001755 | 3.6274e-05 | 0.0013204 | 0.05952 | 0.01272 | 0.060355 | -66.7106 | 0.019721 | -66.7277 | 56.2473 | 56.138 | 56.326 | -66.8238 | -66.7245 | 0.027831 | -66.7453 | 56.1436 | 56.3351 | 56.0544 | -67.0652 | -0.14134 | -0.016473 | -0.028208 | -0.045258 | 0.096085 | -0.12576 | 0.062264 | -0.38281 | -0.12013 | -0.042057 | -0.062826 | 0.31999 | 0.071363 | -0.20931 | 122.9297 | 122.8204 | 123.0084 | 66.7022 | -123.0875 | 122.826 | 123.0175 | 122.7369 | 66.7103 | -123.329
779.7969 | 123.23 | -66.6916 | 56.2454 | -0.0057996 | -0.007126 | 0.00060681 | 0.056865 | -0.0020533 | 0.062155 | -0.001755 | 0.00046367 | 0.00046581 | 0.059307 | 0.012934 | 0.059927 | -66.7106 | 0.0243 | -66.7323 | 56.2427 | 56.1609 | 56.3123 | -66.8284 | -66.7199 | 0.018674 | -66.7544 | 56.1528 | 56.3305 | 56.0407 | -67.0652 | -0.13677 | -0.00274 | -0.019053 | -0.040681 | 0.096086 | -0.084554 | 0.06684 | -0.37366 | -0.092662 | -0.028323 | -0.062829 | 0.31083 | 0.085095 | -0.20473 | 122.9343 | 122.8525 | 123.0039 | 66.7159 | -123.0738 | 122.8443 | 123.0221 | 122.7323 | 66.7103 | -123.3107
780.7969 | 123.2208 | -66.7053 | 56.25 | -0.0057996 | -0.0073396 | 0.00039321 | 0.056438 | -0.0020533 | 0.061514 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059307 | 0.013361 | 0.059927 | -66.7152 | 0.019721 | -66.7323 | 56.2427 | 56.1654 | 56.3214 | -66.8284 | -66.7153 | 0.023253 | -66.7453 | 56.1482 | 56.3351 | 56.0636 | -67.0698 | -0.12303 | -0.007318 | -0.009898 | -0.026948 | 0.096086 | -0.084553 | 0.071419 | -0.3645 | -0.10182 | -0.010012 | -0.039938 | 0.32457 | 0.085096 | -0.18642 | 122.948 | 122.8708 | 123.0267 | 66.725 | -123.0784 | 122.8535 | 123.0404 | 122.7689 | 66.7286 | -123.3198
781.7969 | 123.23 | -66.6962 | 56.2958 | 0.0018314 | -0.007126 | 0.00039321 | 0.056652 | -0.0020533 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058879 | 0.013361 | 0.060141 | -66.7061 | 0.019721 | -66.7185 | 56.2427 | 56.1654 | 56.3168 | -66.8284 | -66.7199 | 0.009516 | -66.7544 | 56.1573 | 56.3305 | 56.0682 | -67.0698 | -0.13219 | -0.053094 | -0.009897 | -0.022368 | 0.10982 | -0.13033 | 0.021064 | -0.37366 | -0.13844 | -0.023745 | -0.058251 | 0.31541 | 0.034741 | -0.22762 | 122.9388 | 122.8616 | 123.013 | 66.7159 | -123.1241 | 122.8535 | 123.0267 | 122.7643 | 66.7057 | -123.3656
782.7969 | 123.1888 | -66.687 | 56.3187 | 0.0018314 | -0.007126 | 0.00082041 | 0.056652 | -0.0020533 | 0.061941 | -0.001755 | -0.00017733 | 0.00046581 | 0.059307 | 0.01272 | 0.060355 | -66.7061 | 0.015142 | -66.7277 | 56.2381 | 56.1654 | 56.3214 | -66.8238 | -66.7199 | 0.018674 | -66.7544 | 56.1573 | 56.3351 | 56.0682 | -67.0652 | -0.13677 | -0.080561 | -0.019052 | -0.04068 | 0.096085 | -0.15322 | 0.002754 | -0.37824 | -0.16133 | -0.0329 | -0.067406 | 0.31083 | 0.016431 | -0.25051 | 122.9251 | 122.8525 | 123.0084 | 66.7022 | -123.1424 | 122.8444 | 123.0221 | 122.7552 | 66.7057 | -123.3839
783.7969 | 123.1567 | -66.687 | 56.2958 | -0.0057996 | -0.0073396 | 0.00060681 | 0.056438 | -0.0018397 | 0.061941 | 0.013506 | -0.00017733 | 0.00089321 | 0.059093 | 0.013147 | 0.059927 | -66.7106 | 0.0243 | -66.7231 | 56.2427 | 56.17 | 56.3123 | -66.8238 | -66.7245 | 0.018674 | -66.7498 | 56.1619 | 56.3305 | 56.0956 | -67.0652 | -0.13677 | -0.053094 | -0.02363 | -0.036101 | 0.10066 | -0.12575 | 0.016486 | -0.37824 | -0.13386 | -0.037479 | -0.062827 | 0.31541 | 0.034741 | -0.20014 | 122.9297 | 122.857 | 122.9993 | 66.7113 | -123.1196 | 122.8489 | 123.0175 | 122.7826 | 66.7057 | -123.361
784.7969 | 123.2346 | -66.6779 | 56.2592 | 0.0018314 | -0.007126 | 0.00060681 | 0.056224 | -0.0018397 | 0.061941 | 0.013506 | -0.00060453 | 0.00046581 | 0.059307 | 0.012934 | 0.060141 | -66.7106 | 0.0243 | -66.7323 | 56.2335 | 56.17 | 56.3214 | -66.8238 | -66.7245 | 0.018674 | -66.7498 | 56.1573 | 56.3351 | 56.1414 | -67.0698 | -0.14592 | -0.02563 | -0.032786 | -0.054414 | 0.091507 | -0.089129 | 0.062264 | -0.39197 | -0.10182 | -0.046635 | -0.071983 | 0.31999 | 0.075941 | -0.11774 | 122.9114 | 122.8479 | 122.9993 | 66.7022 | -123.0829 | 122.8352 | 123.013 | 122.8193 | 66.6965 | -123.329
785.7969 | 123.1934 | -66.7007 | 56.2775 | 0.0018314 | -0.0075534 | 0.00060681 | 0.056652 | -0.0022669 | 0.061727 | -0.001755 | -0.00081813 | 0.00067941 | 0.05952 | 0.013147 | 0.059927 | -66.7061 | 0.015142 | -66.7277 | 56.2335 | 56.1746 | 56.3306 | -66.8238 | -66.7245 | 0.03241 | -66.7453 | 56.1573 | 56.3351 | 56.1368 | -67.0652 | -0.12303 | -0.043941 | -0.005319 | -0.026947 | 0.096085 | -0.10286 | 0.05311 | -0.3645 | -0.12013 | -0.023746 | -0.044515 | 0.31999 | 0.05763 | -0.14063 | 122.9343 | 122.8753 | 123.0313 | 66.7159 | -123.1012 | 122.8581 | 123.0358 | 122.8376 | 66.7332 | -123.3427
786.7969 | 123.2529 | -66.6733 | 56.3049 | 0.0018314 | -0.0073396 | 0.00060681 | 0.056224 | -0.0016259 | 0.062155 | -0.001755 | -0.00039093 | 0.00089321 | 0.059093 | 0.013147 | 0.060141 | -66.7061 | 0.019721 | -66.7277 | 56.2381 | 56.1746 | 56.3168 | -66.8238 | -66.7245 | 0.027831 | -66.7498 | 56.1528 | 56.3305 | 56.1414 | -67.0698 | -0.1505 | -0.066828 | -0.032785 | -0.054413 | 0.096085 | -0.13033 | 0.011908 | -0.39655 | -0.15217 | -0.051212 | -0.07656 | 0.31999 | 0.025585 | -0.16351 | 122.9114 | 122.8479 | 122.9901 | 66.693 | -123.1287 | 122.826 | 123.0038 | 122.8147 | 66.7011 | -123.3748
787.7969 | 123.2117 | -66.6962 | 56.2592 | 0.0018314 | -0.0075534 | 0.00082041 | 0.056224 | -0.0020533 | 0.061941 | -0.017016 | -0.00039093 | 0.00089321 | 0.059307 | 0.01272 | 0.059927 | -66.7106 | 0.015142 | -66.7323 | 56.2427 | 56.17 | 56.3214 | -66.8238 | -66.7245 | 0.018674 | -66.7498 | 56.1619 | 56.3351 | 56.1872 | -67.0698 | -0.12761 | -0.016473 | -0.014475 | -0.036103 | 0.091507 | -0.089129 | 0.062264 | -0.37366 | -0.097238 | -0.028324 | -0.053672 | 0.31999 | 0.075941 | -0.071951 | 122.9388 | 122.8662 | 123.0176 | 66.7113 | -123.0829 | 122.8581 | 123.0313 | 122.8834 | 66.7148 | -123.329
788.7969 | 123.2391 | -66.7099 | 56.282 | -0.0057996 | -0.0073396 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059734 | 0.013361 | 0.060355 | -66.7061 | 0.019721 | -66.7277 | 56.2427 | 56.1654 | 56.3168 | -66.8146 | -66.7153 | 0.018674 | -66.7498 | 56.1482 | 56.3305 | 56.1552 | -67.0698 | -0.10472 | -0.039361 | 0.003836 | -0.017792 | 0.086927 | -0.1166 | 0.034797 | -0.35993 | -0.13386 | -0.005434 | -0.039939 | 0.31999 | 0.048474 | -0.12689 | 122.9526 | 122.8753 | 123.0267 | 66.7296 | -123.0967 | 122.8581 | 123.0404 | 122.8651 | 66.7286 | -123.3519
789.7969 | 123.2208 | -66.7007 | 56.2729 | 0.017093 | -0.007767 | 0.00082041 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | -0.00060453 | 0.00089321 | 0.05952 | 0.013147 | 0.059927 | -66.7198 | 0.010564 | -66.7323 | 56.2473 | 56.17 | 56.3214 | -66.8238 | -66.7245 | 0.023253 | -66.7544 | 56.1528 | 56.3305 | 56.1689 | -67.0698 | -0.12303 | -0.025628 | -0.019054 | -0.031525 | 0.091507 | -0.10286 | 0.048531 | -0.36908 | -0.12013 | -0.023746 | -0.053673 | 0.31541 | 0.057629 | -0.104 | 122.948 | 122.8708 | 123.0222 | 66.7113 | -123.0967 | 122.8535 | 123.0313 | 122.8696 | 66.724 | -123.3427
790.7969 | 123.1934 | -66.6962 | 56.2866 | -0.0057996 | -0.0073396 | 0.00060681 | 0.056865 | -0.0022669 | 0.062155 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059093 | 0.013361 | 0.060141 | -66.7106 | 0.019721 | -66.7323 | 56.2381 | 56.17 | 56.3214 | -66.8238 | -66.7245 | 0.023253 | -66.7361 | 56.1528 | 56.3397 | 56.1231 | -67.0698 | -0.12761 | -0.048517 | -0.014475 | -0.036103 | 0.091507 | -0.11659 | 0.034798 | -0.37366 | -0.13386 | -0.028324 | -0.039936 | 0.33372 | 0.053054 | -0.16352 | 122.9343 | 122.8662 | 123.0176 | 66.7159 | -123.1104 | 122.8489 | 123.0358 | 122.8193 | 66.7194 | -123.3564
791.7969 | 123.2254 | -66.7007 | 56.2729 | 0.0018314 | -0.0075534 | 0.00082041 | 0.056652 | -0.0024807 | 0.062368 | -0.001755 | -0.00017733 | 0.00089321 | 0.05952 | 0.013147 | 0.059927 | -66.7106 | 0.015142 | -66.7323 | 56.2289 | 56.1654 | 56.326 | -66.8192 | -66.7199 | 0.018674 | -66.7453 | 56.1573 | 56.3397 | 56.1872 | -67.0698 | -0.11845 | -0.043941 | -0.009897 | -0.031525 | 0.086928 | -0.10744 | 0.053109 | -0.36908 | -0.11555 | -0.019167 | -0.044515 | 0.32457 | 0.066787 | -0.085684 | 122.9297 | 122.8662 | 123.0267 | 66.7159 | -123.0921 | 122.8581 | 123.0404 | 122.8879 | 66.7194 | -123.3427
792.7969 | 123.2346 | -66.6916 | 56.2775 | -0.0057996 | -0.007767 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | -0.0093855 | -0.00017733 | 0.0011068 | 0.059734 | 0.013361 | 0.060141 | -66.7152 | 0.015142 | -66.7368 | 56.2381 | 56.1654 | 56.3214 | -66.8238 | -66.7245 | 0.027831 | -66.7453 | 56.1573 | 56.3351 | 56.1872 | -67.0652 | -0.13219 | -0.039362 | -0.023631 | -0.045259 | 0.086929 | -0.11202 | 0.043953 | -0.37366 | -0.12013 | -0.032902 | -0.053671 | 0.31999 | 0.05763 | -0.090262 | 122.9297 | 122.857 | 123.013 | 66.7067 | -123.1012 | 122.8489 | 123.0267 | 122.8788 | 66.7194 | -123.3427
793.7969 | 123.23 | -66.6962 | 56.2729 | -0.013431 | -0.0073396 | 0.00060681 | 0.056652 | -0.0020533 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.013575 | 0.060141 | -66.7152 | 0.019721 | -66.7323 | 56.2427 | 56.1654 | 56.3214 | -66.8192 | -66.7153 | 0.014095 | -66.7544 | 56.1573 | 56.3305 | 56.1918 | -67.0698 | -0.12303 | -0.030206 | -0.019053 | -0.036103 | 0.086928 | -0.10744 | 0.048531 | -0.37366 | -0.11555 | -0.019167 | -0.058251 | 0.31541 | 0.057629 | -0.081106 | 122.9388 | 122.8616 | 123.0176 | 66.7159 | -123.0921 | 122.8535 | 123.0267 | 122.8879 | 66.7103 | -123.3427
794.7969 | 123.1934 | -66.6779 | 56.3004 | 0.0018314 | -0.0073396 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059307 | 0.013361 | 0.059927 | -66.7106 | 0.019721 | -66.7323 | 56.2381 | 56.1609 | 56.3214 | -66.8238 | -66.7199 | 0.027831 | -66.7453 | 56.1573 | 56.3259 | 56.1689 | -67.0698 | -0.14592 | -0.06225 | -0.032786 | -0.054414 | 0.091507 | -0.13949 | 0.021065 | -0.39197 | -0.14301 | -0.042056 | -0.067404 | 0.32457 | 0.025585 | -0.13146 | 122.916 | 122.8387 | 122.9993 | 66.6976 | -123.1241 | 122.8352 | 123.0038 | 122.8467 | 66.7057 | -123.3702
795.7969 | 123.2162 | -66.6824 | 56.3004 | -0.0057996 | -0.0075534 | 0.00060681 | 0.056224 | -0.0022669 | 0.062155 | 0.0058755 | -0.00017733 | 0.00089321 | 0.05952 | 0.013361 | 0.060141 | -66.7106 | 0.015142 | -66.7231 | 56.2518 | 56.17 | 56.3214 | -66.8238 | -66.7199 | 0.023253 | -66.7407 | 56.1528 | 56.3351 | 56.1826 | -67.0652 | -0.14134 | -0.048515 | -0.028208 | -0.040679 | 0.10066 | -0.13033 | 0.021065 | -0.38281 | -0.14759 | -0.037478 | -0.058247 | 0.32457 | 0.034742 | -0.11773 | 122.9343 | 122.8525 | 123.0039 | 66.6976 | -123.1241 | 122.8352 | 123.0175 | 122.8651 | 66.7057 | -123.3656
796.7969 | 123.1567 | -66.7007 | 56.3004 | -0.0057996 | -0.0075534 | 0.00082041 | 0.056011 | -0.0022669 | 0.061941 | -0.001755 | -0.00039093 | 0.00067941 | 0.059093 | 0.013361 | 0.059927 | -66.7106 | 0.0243 | -66.7323 | 56.2427 | 56.17 | 56.3306 | -66.8329 | -66.7245 | 0.027831 | -66.7407 | 56.1619 | 56.3305 | 56.2009 | -67.0652 | -0.13219 | -0.057672 | -0.009897 | -0.031525 | 0.10067 | -0.13033 | 0.030222 | -0.3645 | -0.13844 | -0.023746 | -0.039936 | 0.32457 | 0.030163 | -0.099415 | 122.9434 | 122.8708 | 123.0313 | 66.725 | -123.1333 | 122.8627 | 123.0313 | 122.9017 | 66.7286 | -123.3656
797.7969 | 123.2574 | -66.6779 | 56.282 | -0.0057996 | -0.0075534 | 0.00039321 | 0.056652 | -0.0022669 | 0.062155 | 0.0058755 | -0.00039093 | 0.00067941 | 0.05952 | 0.013361 | 0.059927 | -66.7061 | 0.0243 | -66.7185 | 56.2473 | 56.17 | 56.326 | -66.8192 | -66.7245 | 0.023253 | -66.7453 | 56.1573 | 56.3351 | 56.146 | -67.0652 | -0.14134 | -0.034783 | -0.028208 | -0.040679 | 0.10066 | -0.11202 | 0.043954 | -0.38739 | -0.1247 | -0.046635 | -0.067404 | 0.31999 | 0.053053 | -0.13605 | 122.9251 | 122.8479 | 123.0039 | 66.7022 | -123.1012 | 122.8352 | 123.013 | 122.8239 | 66.7011 | -123.3473
798.7969 | 123.1705 | -66.6824 | 56.3095 | 0.0018314 | -0.0073396 | 0.00082041 | 0.056438 | -0.0024807 | 0.062155 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059093 | 0.013575 | 0.060141 | -66.7106 | 0.015142 | -66.7323 | 56.2427 | 56.1654 | 56.3123 | -66.8192 | -66.7199 | 0.014095 | -66.7498 | 56.1573 | 56.3305 | 56.1826 | -67.0744 | -0.13676 | -0.066827 | -0.028208 | -0.049836 | 0.086928 | -0.14406 | 0.002753 | -0.39197 | -0.15217 | -0.037478 | -0.067405 | 0.32457 | 0.021008 | -0.12688 | 122.9251 | 122.8479 | 122.9947 | 66.6976 | -123.1287 | 122.8398 | 123.013 | 122.8651 | 66.6965 | -123.3839
799.7969 | 123.2529 | -66.6641 | 56.2729 | 0.0018314 | -0.0073396 | 0.00082041 | 0.056438 | -0.0020533 | 0.062155 | -0.001755 | -0.00060453 | 0.00089321 | 0.05952 | 0.013361 | 0.059927 | -66.7198 | 0.0243 | -66.7277 | 56.2427 | 56.1654 | 56.3306 | -66.8238 | -66.7245 | 0.023253 | -66.7453 | 56.1573 | 56.3397 | 56.1323 | -67.0652 | -0.15965 | -0.030206 | -0.055675 | -0.063568 | 0.096085 | -0.10744 | 0.057688 | -0.40112 | -0.11555 | -0.060367 | -0.081136 | 0.31999 | 0.066787 | -0.14063 | 122.9068 | 122.8296 | 122.9947 | 66.6884 | -123.0967 | 122.8215 | 123.0038 | 122.7964 | 66.6874 | -123.3381
800.7969 | 123.1934 | -66.7053 | 56.2729 | -0.0057996 | -0.007126 | 0.00060681 | 0.056652 | -0.0020533 | 0.061941 | -0.0093855 | -0.00017733 | 0.00089321 | 0.05952 | 0.013575 | 0.060355 | -66.7015 | 0.015142 | -66.7277 | 56.2427 | 56.1609 | 56.326 | -66.8238 | -66.7245 | 0.023253 | -66.7544 | 56.1528 | 56.3259 | 56.178 | -67.0652 | -0.11846 | -0.030206 | 0.003837 | -0.02237 | 0.096085 | -0.11202 | 0.053109 | -0.35993 | -0.12013 | -0.019169 | -0.049096 | 0.31083 | 0.053051 | -0.094842 | 122.948 | 122.8662 | 123.0313 | 66.7205 | -123.0967 | 122.8581 | 123.0313 | 122.8834 | 66.7286 | -123.3381
801.7969 | 123.1796 | -66.7145 | 56.3232 | 0.0094624 | -0.0073396 | 0.0010342 | 0.056224 | -0.0020533 | 0.062155 | 0.013506 | -0.00039093 | 0.00067941 | 0.059734 | 0.013361 | 0.059927 | -66.7106 | 0.019721 | -66.7277 | 56.2427 | 56.1654 | 56.3214 | -66.8238 | -66.7199 | 0.023253 | -66.7498 | 56.1482 | 56.3305 | 56.1368 | -67.0607 | -0.1093 | -0.08056 | 0.003836 | -0.013214 | 0.096085 | -0.1578 | -0.001823 | -0.34619 | -0.17506 | -0.005434 | -0.035361 | 0.31083 | 0.007275 | -0.1864 | 122.9572 | 122.8799 | 123.0359 | 66.7342 | -123.147 | 122.8627 | 123.045 | 122.8513 | 66.7377 | -123.3839
802.7969 | 123.1384 | -66.7007 | 56.3461 | 0.0018314 | -0.007767 | 0.0012478 | 0.056011 | -0.0022669 | 0.062155 | -0.001755 | -0.00060453 | 0.00067941 | 0.059734 | 0.013361 | 0.059714 | -66.7061 | 0.015142 | -66.7323 | 56.2518 | 56.1746 | 56.326 | -66.8284 | -66.7245 | 0.023253 | -66.7453 | 56.1528 | 56.3351 | 56.0453 | -67.0607 | -0.12761 | -0.094291 | -0.005319 | -0.031525 | 0.096086 | -0.17153 | -0.020133 | -0.35992 | -0.19337 | -0.023746 | -0.044515 | 0.31541 | -0.011034 | -0.30086 | 122.9526 | 122.8753 | 123.0267 | 66.7159 | -123.1745 | 122.8535 | 123.0358 | 122.746 | 66.724 | -123.4068
803.7969 | 123.2346 | -66.6687 | 56.2912 | 0.0018314 | -0.0073396 | 0.00060681 | 0.056438 | -0.0020533 | 0.061941 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059093 | 0.013147 | 0.060141 | -66.7061 | 0.010564 | -66.7231 | 56.2473 | 56.1654 | 56.3214 | -66.8192 | -66.7199 | 0.018674 | -66.7407 | 56.1528 | 56.3397 | 56.0819 | -67.0652 | -0.1505 | -0.043939 | -0.037363 | -0.054412 | 0.096085 | -0.12575 | 0.03022 | -0.39655 | -0.13844 | -0.051211 | -0.07198 | 0.32457 | 0.048476 | -0.2093 | 122.916 | 122.8341 | 122.9901 | 66.6793 | -123.1104 | 122.8215 | 123.0084 | 122.7506 | 66.6874 | -123.3564
804.7969 | 123.2346 | -66.6962 | 56.2958 | -0.0057996 | -0.0075534 | 0.0012478 | 0.056652 | -0.0020533 | 0.061514 | -0.001755 | -0.00017733 | 0.00089321 | 0.059307 | 0.013575 | 0.059927 | -66.7106 | 0.010564 | -66.7231 | 56.2518 | 56.17 | 56.3306 | -66.8192 | -66.7199 | 0.023253 | -66.7498 | 56.1573 | 56.3351 | 56.0773 | -67.0698 | -0.12303 | -0.043937 | -0.014475 | -0.026946 | 0.096085 | -0.12575 | 0.0348 | -0.37366 | -0.13844 | -0.023745 | -0.053672 | 0.31999 | 0.03932 | -0.21846 | 122.948 | 122.8662 | 123.0267 | 66.7067 | -123.115 | 122.8535 | 123.0313 | 122.7735 | 66.7194 | -123.3656
805.7969 | 123.2208 | -66.6962 | 56.2912 | 0.0094624 | -0.007767 | 0.00060681 | 0.056652 | -0.0022669 | 0.062155 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059093 | 0.013575 | 0.059927 | -66.7106 | 0.0243 | -66.7185 | 56.2473 | 56.1609 | 56.3214 | -66.8192 | -66.7245 | 0.018674 | -66.7453 | 56.1619 | 56.3305 | 56.146 | -67.0652 | -0.12303 | -0.043939 | -0.014475 | -0.022368 | 0.10066 | -0.13033 | 0.03022 | -0.36908 | -0.12928 | -0.028324 | -0.049093 | 0.31999 | 0.039318 | -0.1452 | 122.9434 | 122.857 | 123.0176 | 66.7205 | -123.1104 | 122.8581 | 123.0267 | 122.8422 | 66.7148 | -123.3564
806.7969 | 123.1476 | -66.7191 | 56.3324 | 0.0018314 | -0.0075534 | 0.0010342 | 0.056011 | -0.0020533 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.013361 | 0.060141 | -66.7106 | 0.015142 | -66.7277 | 56.2518 | 56.1609 | 56.3306 | -66.8192 | -66.7199 | 0.014095 | -66.7453 | 56.1573 | 56.3259 | 56.0911 | -67.0607 | -0.10014 | -0.080558 | 0.008413 | -0.008637 | 0.091506 | -0.17153 | -0.001821 | -0.34161 | -0.17506 | -0.000857 | -0.026205 | 0.31541 | -0.006458 | -0.24134 | 122.9709 | 122.8799 | 123.0496 | 66.7342 | -123.1516 | 122.8764 | 123.045 | 122.8101 | 66.7331 | -123.3931
807.7969 | 123.2346 | -66.6779 | 56.2454 | -0.021062 | -0.0075534 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | -0.0093855 | -0.00081813 | 0.00089321 | 0.059307 | 0.013361 | 0.059927 | -66.7106 | 0.019721 | -66.7277 | 56.2473 | 56.1654 | 56.3214 | -66.8284 | -66.7199 | 0.018674 | -66.7453 | 56.1528 | 56.3351 | 56.1231 | -67.0561 | -0.1505 | 0.001838 | -0.032786 | -0.049836 | 0.10066 | -0.079975 | 0.075997 | -0.37823 | -0.092662 | -0.042056 | -0.067404 | 0.31083 | 0.089674 | -0.12232 | 122.9251 | 122.8433 | 122.9993 | 66.6976 | -123.0738 | 122.8306 | 123.013 | 122.801 | 66.6965 | -123.3015
808.7969 | 123.2346 | -66.6641 | 56.2912 | -0.0057996 | -0.007767 | 0.0012478 | 0.056652 | -0.0024807 | 0.062368 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059734 | 0.013361 | 0.059714 | -66.7061 | 0.019721 | -66.7277 | 56.2473 | 56.1654 | 56.326 | -66.8238 | -66.7291 | 0.014095 | -66.7453 | 56.1619 | 56.3397 | 56.027 | -67.0607 | -0.15965 | -0.043939 | -0.04194 | -0.063568 | 0.096085 | -0.12575 | 0.034798 | -0.39654 | -0.12928 | -0.064946 | -0.081136 | 0.31541 | 0.048476 | -0.26425 | 122.9114 | 122.8296 | 122.9901 | 66.6838 | -123.115 | 122.826 | 123.0038 | 122.6911 | 66.6782 | -123.3519
809.7969 | 123.2346 | -66.7236 | 56.2912 | -0.0057996 | -0.007767 | 0.0010342 | 0.056652 | -0.0024807 | 0.061941 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059307 | 0.013361 | 0.059927 | -66.6969 | 0.015142 | -66.7231 | 56.2518 | 56.1517 | 56.3214 | -66.8192 | -66.7108 | 0.018674 | -66.7453 | 56.1619 | 56.3305 | 56.0911 | -67.0561 | -0.095565 | -0.03936 | 0.026726 | 0.00052 | 0.096085 | -0.13949 | 0.03022 | -0.33246 | -0.12928 | 0.012878 | -0.021627 | 0.31083 | 0.039318 | -0.20015 | 122.9755 | 122.8753 | 123.0451 | 66.7388 | -123.1104 | 122.8856 | 123.0542 | 122.8147 | 66.7423 | -123.3473
810.7969 | 123.2346 | -66.6321 | 56.3095 | 0.0094624 | -0.0073396 | 0.00082041 | 0.056438 | -0.0018397 | 0.061941 | 0.0058755 | -0.00060453 | 0.00089321 | 0.059307 | 0.013147 | 0.059714 | -66.7061 | 0.019721 | -66.7231 | 56.2473 | 56.1471 | 56.326 | -66.8146 | -66.7199 | 0.027831 | -66.7453 | 56.1573 | 56.3397 | 56.0315 | -67.0607 | -0.18254 | -0.062249 | -0.073984 | -0.091033 | 0.091506 | -0.16238 | 0.016488 | -0.42859 | -0.15217 | -0.087832 | -0.11318 | 0.31541 | 0.030166 | -0.27798 | 122.8793 | 122.7792 | 122.9581 | 66.6518 | -123.1241 | 122.7894 | 122.9718 | 122.6636 | 66.6599 | -123.3702
811.7969 | 123.1567 | -66.7007 | 56.3187 | -0.0057996 | -0.007767 | 0.00082041 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059307 | 0.013361 | 0.060141 | -66.7061 | 0.019721 | -66.7277 | 56.2473 | 56.1563 | 56.3352 | -66.8238 | -66.7199 | 0.027831 | -66.7453 | 56.1665 | 56.3351 | 56.0773 | -67.0607 | -0.12303 | -0.071405 | -0.005319 | -0.026947 | 0.096085 | -0.16238 | 0.01649 | -0.35992 | -0.15217 | -0.019167 | -0.044515 | 0.31541 | 0.016431 | -0.24135 | 122.948 | 122.857 | 123.0359 | 66.7205 | -123.1424 | 122.8672 | 123.0358 | 122.7781 | 66.7286 | -123.3793
812.7969 | 123.1705 | -66.687 | 56.2729 | 0.0018314 | -0.0075534 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059307 | 0.013361 | 0.059927 | -66.7061 | 0.015142 | -66.7323 | 56.2473 | 56.1517 | 56.326 | -66.8146 | -66.7199 | 0.014095 | -66.7453 | 56.1528 | 56.3397 | 56.0865 | -67.0652 | -0.12761 | -0.025628 | -0.019052 | -0.045258 | 0.082349 | -0.12118 | 0.053109 | -0.37824 | -0.12013 | -0.0329 | -0.058248 | 0.31999 | 0.066787 | -0.18641 | 122.9343 | 122.8387 | 123.013 | 66.7022 | -123.0875 | 122.8398 | 123.0267 | 122.7735 | 66.7011 | -123.3381
813.7969 | 123.2437 | -66.6733 | 56.25 | 0.0018314 | -0.0073396 | 0.00060681 | 0.056652 | -0.0020533 | 0.061514 | 0.0058755 | -0.00017733 | 0.00067941 | 0.05952 | 0.013575 | 0.060141 | -66.7015 | 0.019721 | -66.7277 | 56.2473 | 56.1654 | 56.326 | -66.8146 | -66.7245 | 0.023253 | -66.7407 | 56.1573 | 56.3351 | 56.0453 | -67.0607 | -0.14134 | -0.00274 | -0.028206 | -0.054413 | 0.086927 | -0.084553 | 0.075997 | -0.38739 | -0.092661 | -0.051212 | -0.067402 | 0.31999 | 0.085096 | -0.20473 | 122.9205 | 122.8387 | 122.9993 | 66.693 | -123.0646 | 122.8306 | 123.0084 | 122.7185 | 66.6965 | -123.3107
814.7969 | 123.1979 | -66.687 | 56.282 | 0.0018314 | -0.007767 | 0.0010342 | 0.056865 | -0.0020533 | 0.061941 | -0.0093855 | -0.00039093 | 0.00046581 | 0.059307 | 0.013575 | 0.059714 | -66.7061 | 0.010564 | -66.7277 | 56.2473 | 56.1471 | 56.3214 | -66.8192 | -66.7199 | 0.014095 | -66.7453 | 56.1619 | 56.3443 | 56.1552 | -67.0607 | -0.13219 | -0.034783 | -0.019052 | -0.04068 | 0.091506 | -0.13491 | 0.039376 | -0.37366 | -0.12013 | -0.0329 | -0.058248 | 0.31541 | 0.06221 | -0.12689 | 122.9343 | 122.8341 | 123.0084 | 66.6976 | -123.1012 | 122.8489 | 123.0313 | 122.8422 | 66.7011 | -123.3427
815.7969 | 123.2162 | -66.7191 | 56.2775 | 0.0018314 | -0.0073396 | 0.00039321 | 0.056652 | -0.0020533 | 0.061941 | 0.0058755 | -0.00039093 | 0.0011068 | 0.05952 | 0.013361 | 0.059714 | -66.7061 | 0.015142 | -66.7277 | 56.2427 | 56.1654 | 56.326 | -66.8146 | -66.7153 | 0.018674 | -66.7407 | 56.1573 | 56.3488 | 56.0819 | -67.0652 | -0.095564 | -0.034784 | 0.012991 | -0.008637 | 0.086927 | -0.11202 | 0.048531 | -0.34619 | -0.12013 | 0.003721 | -0.021626 | 0.32457 | 0.071366 | -0.19557 | 122.9617 | 122.8845 | 123.0451 | 66.7342 | -123.0921 | 122.8764 | 123.0679 | 122.801 | 66.7377 | -123.3427
816.7969 | 123.2254 | -66.6824 | 56.3141 | -0.0057996 | -0.007767 | 0.00082041 | 0.056652 | -0.0022669 | 0.061941 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059307 | 0.013361 | 0.059927 | -66.7106 | 0.015142 | -66.7368 | 56.2473 | 56.1746 | 56.326 | -66.8146 | -66.7199 | 0.014095 | -66.7453 | 56.1619 | 56.3443 | 56.1597 | -67.0607 | -0.13218 | -0.066827 | -0.028208 | -0.054414 | 0.077771 | -0.13948 | 0.01191 | -0.37823 | -0.15217 | -0.037478 | -0.062826 | 0.31541 | 0.030166 | -0.15436 | 122.9297 | 122.857 | 123.0084 | 66.6976 | -123.1287 | 122.8444 | 123.0267 | 122.8422 | 66.6965 | -123.3748
817.7969 | 123.2574 | -66.6595 | 56.2592 | 0.0094624 | -0.0075534 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | -0.0093855 | -0.00060453 | 0.00067941 | 0.05952 | 0.013575 | 0.060355 | -66.7061 | 0.019721 | -66.7323 | 56.2473 | 56.17 | 56.326 | -66.8238 | -66.7199 | 0.023253 | -66.7498 | 56.1619 | 56.3443 | 56.1323 | -67.0698 | -0.16423 | -0.011895 | -0.046518 | -0.072724 | 0.091507 | -0.089129 | 0.066842 | -0.41028 | -0.097238 | -0.060366 | -0.090293 | 0.31999 | 0.085098 | -0.12689 | 122.9068 | 122.8296 | 122.9855 | 66.6793 | -123.0829 | 122.8215 | 123.0038 | 122.7918 | 66.6828 | -123.329
818.7969 | 123.2025 | -66.6962 | 56.2775 | 0.0018314 | -0.007767 | 0.00082041 | 0.056652 | -0.0022669 | 0.061941 | -0.001755 | -0.00017733 | 0.00067941 | 0.05952 | 0.013575 | 0.059714 | -66.7106 | 0.019721 | -66.7277 | 56.2427 | 56.1609 | 56.326 | -66.8192 | -66.7153 | 0.018674 | -66.7453 | 56.1528 | 56.3443 | 56.1277 | -67.0607 | -0.12303 | -0.034784 | -0.014475 | -0.031525 | 0.091506 | -0.1166 | 0.048531 | -0.3645 | -0.12471 | -0.019167 | -0.049093 | 0.31541 | 0.066787 | -0.14978 | 122.9388 | 122.857 | 123.0222 | 66.7159 | -123.0967 | 122.8489 | 123.0404 | 122.8238 | 66.7148 | -123.3381
819.7969 | 123.2529 | -66.6824 | 56.282 | -0.0057996 | -0.0073396 | 0.00060681 | 0.056224 | -0.0016259 | 0.061727 | -0.001755 | -0.00060453 | 0.00046581 | 0.059093 | 0.013575 | 0.059927 | -66.7106 | 0.010564 | -66.7277 | 56.2427 | 56.1654 | 56.3214 | -66.8146 | -66.7153 | 0.023253 | -66.7498 | 56.1573 | 56.3397 | 56.1689 | -67.0698 | -0.13218 | -0.039361 | -0.028208 | -0.045258 | 0.086927 | -0.1166 | 0.039376 | -0.38739 | -0.1247 | -0.0329 | -0.067405 | 0.31999 | 0.057632 | -0.11315 | 122.9251 | 122.8479 | 123.0039 | 66.693 | -123.0967 | 122.8398 | 123.0221 | 122.8513 | 66.7057 | -123.3519
820.7969 | 123.2025 | -66.7145 | 56.2775 | -0.0057996 | -0.0075534 | 0.00082041 | 0.056865 | -0.0022669 | 0.062582 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059093 | 0.013575 | 0.059927 | -66.7106 | 0.010564 | -66.7231 | 56.2473 | 56.1654 | 56.326 | -66.8192 | -66.7245 | 0.018674 | -66.7453 | 56.1573 | 56.3351 | 56.178 | -67.0652 | -0.10472 | -0.030206 | 0.003836 | -0.008635 | 0.096085 | -0.11202 | 0.048531 | -0.35077 | -0.12013 | -0.010013 | -0.030782 | 0.31999 | 0.05763 | -0.09942 | 122.9617 | 122.8799 | 123.0405 | 66.725 | -123.0967 | 122.8718 | 123.0496 | 122.8925 | 66.7332 | -123.3427
821.7969 | 123.2162 | -66.6916 | 56.2912 | 0.0018314 | -0.007767 | 0.00060681 | 0.056652 | -0.0020533 | 0.062155 | -0.001755 | -0.00017733 | 0.00089321 | 0.059093 | 0.013361 | 0.060141 | -66.7061 | 0.010564 | -66.7277 | 56.2473 | 56.1654 | 56.326 | -66.8284 | -66.7153 | 0.018674 | -66.7361 | 56.1619 | 56.3397 | 56.1094 | -67.0652 | -0.13677 | -0.043939 | -0.014475 | -0.036103 | 0.10066 | -0.12575 | 0.034798 | -0.37366 | -0.12928 | -0.023745 | -0.044514 | 0.32914 | 0.048476 | -0.18183 | 122.9388 | 122.857 | 123.0176 | 66.7022 | -123.1196 | 122.8535 | 123.0313 | 122.801 | 66.7103 | -123.3564
822.7969 | 123.2574 | -66.687 | 56.2637 | -0.0057996 | -0.007767 | 0.0012478 | 0.056438 | -0.0022669 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059307 | 0.013575 | 0.059714 | -66.7106 | 0.005985 | -66.7323 | 56.2518 | 56.1746 | 56.326 | -66.8146 | -66.7108 | 0.014095 | -66.7453 | 56.1619 | 56.3488 | 56.1323 | -67.0561 | -0.12761 | -0.011894 | -0.02363 | -0.045258 | 0.082349 | -0.089128 | 0.062264 | -0.36908 | -0.10182 | -0.023743 | -0.058248 | 0.31083 | 0.085099 | -0.13147 | 122.9389 | 122.8616 | 123.013 | 66.693 | -123.0784 | 122.8489 | 123.0358 | 122.8193 | 66.7011 | -123.3198
823.7969 | 123.2025 | -66.6916 | 56.2912 | 0.017093 | -0.007767 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | -0.001755 | 3.6274e-05 | 0.00067941 | 0.059307 | 0.013575 | 0.059927 | -66.7061 | 0.010564 | -66.7277 | 56.2427 | 56.1746 | 56.326 | -66.8146 | -66.7153 | 0.018674 | -66.7407 | 56.1573 | 56.3305 | 56.1964 | -67.0652 | -0.12303 | -0.048517 | -0.014475 | -0.036103 | 0.086927 | -0.11659 | 0.034798 | -0.37366 | -0.13386 | -0.023745 | -0.049092 | 0.32457 | 0.039318 | -0.094838 | 122.9343 | 122.8662 | 123.0176 | 66.7022 | -123.1058 | 122.8489 | 123.0221 | 122.8879 | 66.7103 | -123.3564
824.7969 | 123.2391 | -66.655 | 56.2912 | -0.0057996 | -0.0073396 | 0.00082041 | 0.056224 | -0.0022669 | 0.062155 | -0.0093855 | 3.6274e-05 | 0.00089321 | 0.059093 | 0.013361 | 0.060568 | -66.7061 | 0.015142 | -66.7323 | 56.2427 | 56.1792 | 56.326 | -66.81 | -66.7153 | 0.014095 | -66.7498 | 56.1573 | 56.3351 | 56.0819 | -67.0561 | -0.15507 | -0.048517 | -0.051096 | -0.077302 | 0.07777 | -0.11201 | 0.034798 | -0.40112 | -0.13386 | -0.060366 | -0.094871 | 0.30625 | 0.043897 | -0.2093 | 122.8976 | 122.8342 | 122.981 | 66.6701 | -123.1012 | 122.8123 | 122.9901 | 122.7369 | 66.6691 | -123.3473
825.7969 | 123.1064 | -66.7236 | 56.3187 | 0.0018314 | -0.0079808 | 0.00060681 | 0.056438 | -0.0022669 | 0.061941 | 0.0058755 | -0.00039093 | 0.00046581 | 0.059307 | 0.013361 | 0.0595 | -66.7015 | 0.019721 | -66.7277 | 56.2518 | 56.1746 | 56.326 | -66.8238 | -66.7153 | 0.018674 | -66.7453 | 56.1665 | 56.3351 | 56.1689 | -67.0652 | -0.10014 | -0.066826 | 0.022148 | -0.004059 | 0.096085 | -0.14406 | 0.007332 | -0.34161 | -0.15217 | 0.008299 | -0.021627 | 0.31999 | 0.016431 | -0.14978 | 122.9755 | 122.8982 | 123.0496 | 66.7434 | -123.1424 | 122.8901 | 123.0587 | 122.8925 | 66.7423 | -123.3839
826.7969 | 123.2208 | -66.6687 | 56.25 | -0.013431 | -0.007767 | 0.00039321 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | -0.00017733 | 0.00067941 | 0.059307 | 0.013575 | 0.060141 | -66.7061 | 0.015142 | -66.7323 | 56.2518 | 56.1746 | 56.326 | -66.8192 | -66.7199 | 0.018674 | -66.7453 | 56.1482 | 56.3351 | 56.1826 | -67.0698 | -0.1505 | 0.001839 | -0.037363 | -0.063569 | 0.086928 | -0.075395 | 0.075997 | -0.40113 | -0.10182 | -0.051211 | -0.076559 | 0.32457 | 0.085096 | -0.067375 | 122.9205 | 122.8433 | 122.9947 | 66.6838 | -123.0692 | 122.8169 | 123.0038 | 122.8513 | 66.6874 | -123.3198
827.7969 | 123.2208 | -66.7007 | 56.2729 | -0.0057996 | -0.0075534 | 0.00082041 | 0.056652 | -0.0018397 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.059093 | 0.013575 | 0.059927 | -66.6969 | 0.015142 | -66.7323 | 56.2473 | 56.1654 | 56.326 | -66.8238 | -66.7199 | 0.018674 | -66.7453 | 56.1573 | 56.3397 | 56.0956 | -67.0561 | -0.12303 | -0.025628 | 0.003838 | -0.031525 | 0.091507 | -0.10744 | 0.053109 | -0.35534 | -0.11555 | -0.019167 | -0.044515 | 0.31083 | 0.066787 | -0.17726 | 122.948 | 122.8662 | 123.0267 | 66.7159 | -123.0967 | 122.8581 | 123.0404 | 122.7964 | 66.7194 | -123.329
828.7969 | 123.2346 | -66.6641 | 56.2729 | -0.013431 | -0.0079808 | 0.00060681 | 0.056224 | -0.0020533 | 0.062368 | -0.001755 | -0.00039093 | 0.00046581 | 0.059093 | 0.013575 | 0.060141 | -66.7061 | 0.010564 | -66.7277 | 56.2427 | 56.1654 | 56.3352 | -66.8146 | -66.7153 | 0.018674 | -66.7407 | 56.1619 | 56.3397 | 56.1323 | -67.0652 | -0.15049 | -0.030206 | -0.04194 | -0.063568 | 0.086927 | -0.10744 | 0.062267 | -0.40112 | -0.11097 | -0.05121 | -0.076557 | 0.32457 | 0.066787 | -0.14063 | 122.9068 | 122.8296 | 122.9993 | 66.6747 | -123.0875 | 122.826 | 123.0038 | 122.7964 | 66.6828 | -123.3381
829.7969 | 123.2391 | -66.6916 | 56.2866 | -0.013431 | -0.007767 | 0.00060681 | 0.056224 | -0.0022669 | 0.061941 | -0.001755 | -0.00017733 | 0.00067941 | 0.059307 | 0.013361 | 0.059927 | -66.7061 | 0.019721 | -66.7231 | 56.2427 | 56.1746 | 56.326 | -66.8238 | -66.7199 | 0.018674 | -66.7361 | 56.1619 | 56.3443 | 56.0773 | -67.0561 | -0.13219 | -0.043939 | -0.014475 | -0.031524 | 0.10066 | -0.11202 | 0.039376 | -0.3645 | -0.1247 | -0.028323 | -0.044514 | 0.31999 | 0.057632 | -0.2093 | 122.9343 | 122.8662 | 123.0176 | 66.7113 | -123.1104 | 122.8535 | 123.0358 | 122.7689 | 66.7103 | -123.3427
830.7969 | 123.1613 | -66.7007 | 56.2683 | 0.0018314 | -0.0081944 | 0.00082041 | 0.056652 | -0.0020533 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059307 | 0.014002 | 0.059927 | -66.7061 | 0.005985 | -66.7368 | 56.2473 | 56.17 | 56.3306 | -66.8146 | -66.7153 | 0.014095 | -66.7407 | 56.1573 | 56.3397 | 56.1414 | -67.0607 | -0.11387 | -0.021051 | -0.005319 | -0.036103 | 0.077771 | -0.098285 | 0.062265 | -0.35992 | -0.11097 | -0.014589 | -0.039936 | 0.31999 | 0.071364 | -0.12689 | 122.948 | 122.8708 | 123.0313 | 66.7067 | -123.0829 | 122.8581 | 123.0404 | 122.8422 | 66.7148 | -123.329
831.7969 | 123.2117 | -66.687 | 56.282 | 0.0018314 | -0.0075534 | 0.00082041 | 0.056438 | -0.0022669 | 0.061727 | -0.017016 | -0.00039093 | 0.00067941 | 0.059734 | 0.013788 | 0.0595 | -66.7015 | 0.010564 | -66.7277 | 56.2473 | 56.17 | 56.3306 | -66.8192 | -66.7199 | 0.018674 | -66.7315 | 56.1573 | 56.3443 | 56.1368 | -67.0607 | -0.13219 | -0.034783 | -0.014473 | -0.04068 | 0.091506 | -0.11202 | 0.048533 | -0.37366 | -0.1247 | -0.0329 | -0.044512 | 0.32914 | 0.06221 | -0.1452 | 122.9343 | 122.857 | 123.0176 | 66.6976 | -123.1012 | 122.8444 | 123.0313 | 122.8239 | 66.7057 | -123.3427
832.7969 | 123.2117 | -66.6962 | 56.2775 | 0.0018314 | -0.007767 | 0.00082041 | 0.056438 | -0.0020533 | 0.061941 | -0.001755 | -0.00017733 | 0.00089321 | 0.059734 | 0.013575 | 0.0595 | -66.7015 | 0.019721 | -66.7185 | 56.2518 | 56.17 | 56.326 | -66.8146 | -66.7153 | 0.023253 | -66.7361 | 56.1619 | 56.3488 | 56.2009 | -67.0607 | -0.11845 | -0.025627 | -0.005318 | -0.022368 | 0.096084 | -0.10744 | 0.048531 | -0.3645 | -0.11555 | -0.019167 | -0.039936 | 0.32457 | 0.071366 | -0.076527 | 122.948 | 122.8662 | 123.0222 | 66.7159 | -123.0921 | 122.8581 | 123.045 | 122.8971 | 66.7194 | -123.3381
833.7969 | 123.1384 | -66.7511 | 56.2912 | 0.0018314 | -0.007767 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059093 | 0.013788 | 0.059714 | -66.7061 | 0.019721 | -66.7277 | 56.2473 | 56.1746 | 56.3306 | -66.8238 | -66.7199 | 0.018674 | -66.7361 | 56.1619 | 56.3397 | 56.1552 | -67.0652 | -0.072678 | -0.043939 | 0.045035 | 0.023407 | 0.096085 | -0.11659 | 0.039377 | -0.31415 | -0.12928 | 0.031187 | 0.014996 | 0.32914 | 0.048476 | -0.13605 | 122.9984 | 122.9257 | 123.0817 | 66.7708 | -123.115 | 122.913 | 123.0908 | 122.9063 | 66.7698 | -123.3564
834.7969 | 123.23 | -66.7007 | 56.2546 | -0.021062 | -0.007767 | 0.00082041 | 0.056438 | -0.0022669 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.05952 | 0.014002 | 0.059714 | -66.7015 | 0.019721 | -66.7323 | 56.2427 | 56.17 | 56.326 | -66.8238 | -66.7108 | 0.009516 | -66.7407 | 56.1665 | 56.3397 | 56.1643 | -67.0469 | -0.12303 | -0.011896 | -0.00074 | -0.031525 | 0.091507 | -0.084552 | 0.071419 | -0.34619 | -0.088082 | -0.01001 | -0.039936 | 0.30625 | 0.085097 | -0.090267 | 122.9434 | 122.8708 | 123.0267 | 66.7205 | -123.0784 | 122.8672 | 123.0404 | 122.8651 | 66.7103 | -123.3015
835.7969 | 123.23 | -66.7007 | 56.2637 | 0.0018314 | -0.0079808 | 0.0010342 | 0.056224 | -0.0026943 | 0.061941 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059307 | 0.013575 | 0.060141 | -66.7106 | 0.015142 | -66.7231 | 56.2427 | 56.1746 | 56.3306 | -66.8146 | -66.7199 | 0.014095 | -66.7453 | 56.1573 | 56.3443 | 56.1964 | -67.0561 | -0.11387 | -0.021051 | -0.009897 | -0.022368 | 0.091506 | -0.089128 | 0.066843 | -0.35534 | -0.10639 | -0.019167 | -0.044515 | 0.31083 | 0.08052 | -0.067372 | 122.9434 | 122.8753 | 123.0313 | 66.7159 | -123.0784 | 122.8581 | 123.045 | 122.8971 | 66.7148 | -123.3198
836.7969 | 123.2574 | -66.6824 | 56.2637 | -0.0057996 | -0.007767 | 0.00082041 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00039093 | 0.00089321 | 0.05952 | 0.013361 | 0.059714 | -66.7061 | 0.019721 | -66.7277 | 56.2427 | 56.17 | 56.3306 | -66.8192 | -66.7153 | 0.009516 | -66.7498 | 56.1619 | 56.3488 | 56.1872 | -67.0561 | -0.13676 | -0.021051 | -0.02363 | -0.045258 | 0.091506 | -0.093707 | 0.066843 | -0.37365 | -0.10182 | -0.0329 | -0.067405 | 0.30625 | 0.085099 | -0.076529 | 122.9251 | 122.8525 | 123.013 | 66.7022 | -123.0829 | 122.8444 | 123.0313 | 122.8696 | 66.692 | -123.3198
837.7969 | 123.2254 | -66.6962 | 56.2729 | -0.013431 | -0.007767 | 0.00082041 | 0.056438 | -0.0024807 | 0.062368 | -0.0093855 | -0.00060453 | 0.00089321 | 0.059307 | 0.013788 | 0.059927 | -66.7015 | 0.015142 | -66.7323 | 56.2473 | 56.1746 | 56.3306 | -66.8146 | -66.7153 | 0.014095 | -66.7407 | 56.1619 | 56.3443 | 56.2101 | -67.0607 | -0.11845 | -0.025628 | -0.005318 | -0.036103 | 0.082349 | -0.098283 | 0.057688 | -0.3645 | -0.11097 | -0.019167 | -0.044514 | 0.31999 | 0.071365 | -0.062791 | 122.9434 | 122.8708 | 123.0267 | 66.7113 | -123.0875 | 122.8581 | 123.0404 | 122.9063 | 66.7103 | -123.3336
838.7969 | 123.2071 | -66.6916 | 56.2683 | -0.0057996 | -0.007767 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.00089321 | 0.058879 | 0.013361 | 0.059927 | -66.7015 | 0.015142 | -66.7231 | 56.2518 | 56.1838 | 56.3352 | -66.8192 | -66.7153 | 0.014095 | -66.7453 | 56.1665 | 56.3443 | 56.1597 | -67.0607 | -0.12761 | -0.016472 | -0.009896 | -0.031524 | 0.096085 | -0.084548 | 0.066844 | -0.36908 | -0.10181 | -0.023745 | -0.053671 | 0.31541 | 0.075942 | -0.10858 | 122.9434 | 122.8754 | 123.0267 | 66.7067 | -123.0875 | 122.8581 | 123.0358 | 122.8513 | 66.7057 | -123.329
839.7969 | 123.2162 | -66.6962 | 56.2775 | 0.0018314 | -0.0081944 | 0.00060681 | 0.056224 | -0.0022669 | 0.061941 | -0.001755 | -0.00081813 | 0.00067941 | 0.059307 | 0.014002 | 0.059927 | -66.7106 | 0.0243 | -66.7231 | 56.2518 | 56.1746 | 56.326 | -66.8238 | -66.7245 | 0.018674 | -66.7453 | 56.1573 | 56.3443 | 56.146 | -67.0561 | -0.12761 | -0.025627 | -0.014475 | -0.026946 | 0.10066 | -0.10286 | 0.048531 | -0.35992 | -0.12013 | -0.028324 | -0.049093 | 0.31083 | 0.066787 | -0.13147 | 122.948 | 122.8708 | 123.0222 | 66.7205 | -123.1012 | 122.8535 | 123.0404 | 122.8422 | 66.7148 | -123.3336
840.7969 | 123.143 | -66.7374 | 56.282 | 0.0018314 | -0.007767 | 0.0012478 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.013575 | 0.059714 | -66.7015 | 0.010564 | -66.7277 | 56.2518 | 56.1654 | 56.3306 | -66.8192 | -66.7153 | 0.014095 | -66.7453 | 56.1619 | 56.3397 | 56.1414 | -67.0561 | -0.081832 | -0.030204 | 0.035881 | 0.009674 | 0.091506 | -0.1166 | 0.048533 | -0.31872 | -0.12013 | 0.022032 | -0.007894 | 0.31083 | 0.057632 | -0.14062 | 122.9892 | 122.9028 | 123.0679 | 66.7479 | -123.1012 | 122.8993 | 123.077 | 122.8788 | 66.7515 | -123.3381
841.7969 | 123.2025 | -66.7053 | 56.282 | 0.0018314 | -0.007767 | 0.0010342 | 0.056438 | -0.0024807 | 0.061727 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.014002 | 0.059927 | -66.7061 | 0.015142 | -66.7277 | 56.2518 | 56.1609 | 56.326 | -66.8146 | -66.7153 | 0.018674 | -66.7361 | 56.1665 | 56.3534 | 56.1689 | -67.0607 | -0.1093 | -0.030204 | -0.000742 | -0.02237 | 0.086927 | -0.12118 | 0.043954 | -0.35535 | -0.11555 | -0.010012 | -0.030781 | 0.32457 | 0.071367 | -0.11315 | 122.9572 | 122.8662 | 123.0313 | 66.7205 | -123.0967 | 122.8718 | 123.0587 | 122.8742 | 66.724 | -123.3427
842.7969 | 123.1705 | -66.7282 | 56.3049 | -0.0057996 | -0.0081944 | 0.0010342 | 0.056224 | -0.0024807 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059093 | 0.014002 | 0.059927 | -66.6969 | 0.015142 | -66.7277 | 56.2473 | 56.1883 | 56.326 | -66.8238 | -66.7199 | 0.014095 | -66.7453 | 56.1619 | 56.3443 | 56.1597 | -67.0561 | -0.095567 | -0.057672 | 0.031303 | 0.000518 | 0.096085 | -0.11659 | 0.021065 | -0.32788 | -0.14301 | 0.008298 | -0.01705 | 0.31083 | 0.039321 | -0.1452 | 122.9755 | 122.9166 | 123.0542 | 66.7434 | -123.1287 | 122.8901 | 123.0725 | 122.8879 | 66.7423 | -123.361
843.7969 | 123.2025 | -66.6962 | 56.2637 | 0.0018314 | -0.0079808 | 0.00082041 | 0.056438 | -0.0020533 | 0.061514 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059093 | 0.014002 | 0.059714 | -66.7061 | 0.019721 | -66.7277 | 56.2518 | 56.1746 | 56.3352 | -66.8192 | -66.7153 | 0.018674 | -66.7361 | 56.1573 | 56.3443 | 56.1139 | -67.0561 | -0.12303 | -0.011894 | -0.009897 | -0.031525 | 0.091506 | -0.089128 | 0.071422 | -0.35992 | -0.10639 | -0.019167 | -0.039936 | 0.31999 | 0.08052 | -0.14979 | 122.948 | 122.8708 | 123.0313 | 66.7159 | -123.0829 | 122.8535 | 123.0404 | 122.8101 | 66.7148 | -123.3198
844.7969 | 123.1567 | -66.7099 | 56.2775 | 0.0018314 | -0.0079808 | 0.00060681 | 0.056224 | -0.0020533 | 0.062155 | -0.001755 | -0.00039093 | 0.00089321 | 0.059734 | 0.013788 | 0.059927 | -66.7015 | 0.015142 | -66.7185 | 56.2564 | 56.17 | 56.3306 | -66.8192 | -66.7153 | 0.018674 | -66.7361 | 56.1619 | 56.3443 | 56.1094 | -67.0561 | -0.1093 | -0.021049 | 0.008415 | -0.008635 | 0.10066 | -0.10744 | 0.05311 | -0.34619 | -0.11555 | -0.005434 | -0.026203 | 0.31999 | 0.066787 | -0.1681 | 122.9663 | 122.8799 | 123.0405 | 66.725 | -123.0967 | 122.8718 | 123.0542 | 122.8193 | 66.7286 | -123.3336
845.7969 | 123.1338 | -66.7282 | 56.337 | -0.013431 | -0.0079808 | 0.00082041 | 0.056438 | -0.0026943 | 0.061514 | -0.001755 | -0.00060453 | 0.00089321 | 0.059734 | 0.014002 | 0.059927 | -66.6969 | 0.015142 | -66.7323 | 56.2564 | 56.1792 | 56.3306 | -66.8192 | -66.7108 | 0.014095 | -66.7315 | 56.1619 | 56.3488 | 56.1231 | -67.0607 | -0.090988 | -0.080558 | 0.031303 | -0.00406 | 0.086928 | -0.15779 | -0.006399 | -0.33246 | -0.17506 | 0.017455 | -0.003314 | 0.32914 | 0.011857 | -0.21387 | 122.9846 | 122.9074 | 123.0588 | 66.7434 | -123.1562 | 122.8901 | 123.077 | 122.8513 | 66.7423 | -123.3976
846.7969 | 123.2346 | -66.6962 | 56.25 | -0.013431 | -0.0079808 | 0.0010342 | 0.056438 | -0.0018397 | 0.062155 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059093 | 0.014216 | 0.059927 | -66.7015 | 0.019721 | -66.7231 | 56.2473 | 56.17 | 56.3306 | -66.8192 | -66.7199 | 0.014095 | -66.7407 | 56.1573 | 56.3397 | 56.1964 | -67.0561 | -0.12303 | -0.00274 | -0.005318 | -0.026946 | 0.096085 | -0.079974 | 0.080576 | -0.35992 | -0.092661 | -0.023745 | -0.044514 | 0.31541 | 0.089675 | -0.053639 | 122.9434 | 122.8662 | 123.0267 | 66.7159 | -123.0692 | 122.8535 | 123.0358 | 122.8925 | 66.7103 | -123.3061
847.7969 | 123.1338 | -66.7374 | 56.282 | -0.0057996 | -0.0079808 | 0.00082041 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.013575 | 0.059714 | -66.6969 | 0.019721 | -66.7277 | 56.2473 | 56.17 | 56.3352 | -66.8146 | -66.7108 | 0.014095 | -66.7361 | 56.1665 | 56.3397 | 56.1185 | -67.0561 | -0.077253 | -0.034783 | 0.040459 | 0.009674 | 0.086927 | -0.11202 | 0.053112 | -0.31872 | -0.11555 | 0.026611 | 0.001263 | 0.31999 | 0.057632 | -0.16352 | 122.9846 | 122.9074 | 123.0725 | 66.7571 | -123.0967 | 122.9039 | 123.077 | 122.8559 | 66.7515 | -123.3381
848.7969 | 123.1613 | -66.7236 | 56.2683 | -0.0057996 | -0.007767 | 0.00060681 | 0.055797 | -0.0022669 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.059307 | 0.013575 | 0.059927 | -66.6923 | 0.019721 | -66.7277 | 56.2518 | 56.1746 | 56.3306 | -66.8146 | -66.7153 | 0.018674 | -66.7361 | 56.1573 | 56.3443 | 56.1506 | -67.0607 | -0.090986 | -0.016472 | 0.031305 | -0.004059 | 0.086927 | -0.093706 | 0.062265 | -0.33704 | -0.11097 | 0.008299 | -0.01247 | 0.32457 | 0.075942 | -0.11774 | 122.9755 | 122.8982 | 123.0542 | 66.7434 | -123.0829 | 122.881 | 123.0679 | 122.8742 | 66.7423 | -123.329
849.7969 | 123.1338 | -66.7145 | 56.3004 | 0.0018314 | -0.0081944 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | -0.001755 | -0.00060453 | 0.00089321 | 0.059093 | 0.013788 | 0.060141 | -66.7061 | 0.019721 | -66.7277 | 56.2564 | 56.1792 | 56.3306 | -66.8146 | -66.7108 | 0.014095 | -66.7361 | 56.1619 | 56.3397 | 56.178 | -67.0607 | -0.10014 | -0.043937 | 0.008414 | -0.013214 | 0.086927 | -0.12117 | 0.030222 | -0.34619 | -0.13844 | 0.003723 | -0.021625 | 0.32457 | 0.039321 | -0.12231 | 122.9709 | 122.8937 | 123.0451 | 66.7342 | -123.115 | 122.8764 | 123.0542 | 122.8925 | 66.7286 | -123.361
850.7969 | 123.1979 | -66.7007 | 56.2912 | -0.0057996 | -0.0081944 | 0.00060681 | 0.056224 | -0.0022669 | 0.062155 | -0.017016 | -0.00060453 | 0.00067941 | 0.059093 | 0.013575 | 0.0595 | -66.7015 | 0.019721 | -66.7277 | 56.2518 | 56.1517 | 56.3397 | -66.8146 | -66.7108 | 0.014095 | -66.7407 | 56.1665 | 56.3443 | 56.1002 | -67.0652 | -0.11387 | -0.03936 | -0.00074 | -0.026947 | 0.086927 | -0.13949 | 0.048534 | -0.3645 | -0.1247 | -0.01001 | -0.039936 | 0.32457 | 0.053054 | -0.19099 | 122.9526 | 122.8525 | 123.0405 | 66.7205 | -123.1058 | 122.8672 | 123.045 | 122.801 | 66.7148 | -123.3564
851.7969 | 123.2117 | -66.7053 | 56.2592 | -0.0057996 | -0.0081944 | 0.0010342 | 0.056438 | -0.0022669 | 0.061941 | 0.0058755 | -0.00060453 | 0.00089321 | 0.058879 | 0.014002 | 0.059714 | -66.7015 | 0.015142 | -66.7185 | 56.2564 | 56.138 | 56.3306 | -66.8192 | -66.7108 | 0.009516 | -66.7407 | 56.1619 | 56.3488 | 56.059 | -67.0561 | -0.11388 | -0.002738 | 0.003837 | -0.013213 | 0.10066 | -0.12118 | 0.071421 | -0.35077 | -0.097238 | -0.005433 | -0.035359 | 0.31541 | 0.089677 | -0.20015 | 122.9617 | 122.8433 | 123.0359 | 66.7205 | -123.0784 | 122.8672 | 123.0542 | 122.7643 | 66.7148 | -123.3152
852.7969 | 123.1201 | -66.7328 | 56.3004 | -0.0057996 | -0.0079808 | 0.00060681 | 0.056224 | -0.0020533 | 0.062155 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059093 | 0.013575 | 0.0595 | -66.7015 | 0.015142 | -66.7185 | 56.2473 | 56.1609 | 56.326 | -66.8192 | -66.7199 | 0.018674 | -66.7361 | 56.1665 | 56.3397 | 56.0773 | -67.0607 | -0.08641 | -0.053094 | 0.031303 | 0.014253 | 0.10066 | -0.13949 | 0.025643 | -0.32788 | -0.13386 | 0.012876 | -0.003315 | 0.32457 | 0.039321 | -0.22304 | 122.98 | 122.8937 | 123.0588 | 66.7479 | -123.1196 | 122.8993 | 123.0725 | 122.8101 | 66.7515 | -123.361
853.7969 | 123.1842 | -66.7053 | 56.2958 | -0.0057996 | -0.0081944 | 0.00039321 | 0.056224 | -0.0024807 | 0.061727 | -0.0093855 | -0.00081813 | 0.00067941 | 0.059093 | 0.013788 | 0.059714 | -66.6969 | 0.015142 | -66.7231 | 56.2564 | 56.1563 | 56.3352 | -66.8284 | -66.7153 | 0.014095 | -66.7407 | 56.1665 | 56.3397 | 56.1139 | -67.0652 | -0.12303 | -0.039359 | 0.008415 | -0.017791 | 0.10524 | -0.13949 | 0.039379 | -0.35993 | -0.12928 | -0.010012 | -0.035359 | 0.32457 | 0.043899 | -0.18183 | 122.9617 | 122.8616 | 123.0405 | 66.7205 | -123.1241 | 122.8718 | 123.045 | 122.8193 | 66.7194 | -123.361
854.7969 | 123.1338 | -66.7374 | 56.2866 | -0.0057996 | -0.007767 | 0.00082041 | 0.056652 | -0.0022669 | 0.061727 | 0.0058755 | -0.00017733 | 0.00089321 | 0.059093 | 0.014002 | 0.059714 | -66.7015 | 0.019721 | -66.7323 | 56.2518 | 56.1563 | 56.3306 | -66.8192 | -66.7108 | 0.014095 | -66.7361 | 56.1665 | 56.3443 | 56.0727 | -67.0607 | -0.081832 | -0.034782 | 0.035881 | 0.005096 | 0.086928 | -0.13033 | 0.043955 | -0.3233 | -0.12012 | 0.026611 | 0.001263 | 0.32457 | 0.057632 | -0.21388 | 122.9892 | 122.8937 | 123.0679 | 66.7571 | -123.1058 | 122.9039 | 123.0816 | 122.8101 | 66.7515 | -123.3473
855.7969 | 123.0515 | -66.7511 | 56.2592 | 0.0018314 | -0.0081944 | 0.00082041 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.059307 | 0.013788 | 0.059714 | -66.6923 | 0.015142 | -66.7231 | 56.2518 | 56.1654 | 56.3397 | -66.8238 | -66.7108 | 0.014095 | -66.7361 | 56.1665 | 56.3443 | 56.0956 | -67.0607 | -0.072678 | -0.007316 | 0.058771 | 0.027986 | 0.10066 | -0.093708 | 0.080578 | -0.30957 | -0.092659 | 0.040344 | 0.014996 | 0.32457 | 0.085098 | -0.16352 | 123.0029 | 122.9165 | 123.0908 | 66.7662 | -123.0829 | 122.9176 | 123.0954 | 122.8467 | 66.7652 | -123.3198
856.8125 | 123.0331 | -66.7374 | 56.3095 | 0.0018314 | -0.0079808 | 0.00082041 | 0.056224 | -0.0024807 | 0.062155 | 0.013506 | -0.00017733 | 0.00046581 | 0.058879 | 0.013788 | 0.059927 | -66.6969 | 0.015142 | -66.7185 | 56.2656 | 56.1609 | 56.3352 | -66.8284 | -66.7153 | 0.014095 | -66.7407 | 56.1573 | 56.3443 | 56.0086 | -67.0469 | -0.09099 | -0.043935 | 0.040459 | 0.018831 | 0.10982 | -0.14864 | 0.025646 | -0.30957 | -0.15217 | 0.022032 | -0.003315 | 0.30625 | 0.034744 | -0.30087 | 123.0029 | 122.8982 | 123.0725 | 66.7525 | -123.1379 | 122.8947 | 123.0816 | 122.746 | 66.7515 | -123.3564
857.7969 | 123.1064 | -66.7374 | 56.3004 | -0.013431 | -0.0079808 | 0.00082041 | 0.056865 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.059307 | 0.014002 | 0.059714 | -66.7015 | 0.015142 | -66.7231 | 56.2518 | 56.1746 | 56.3306 | -66.8238 | -66.7108 | 0.014095 | -66.7361 | 56.1711 | 56.3488 | 56.1185 | -67.0561 | -0.086411 | -0.048515 | 0.035881 | 0.014253 | 0.10066 | -0.12575 | 0.030222 | -0.31872 | -0.12928 | 0.026611 | 0.001263 | 0.31999 | 0.048478 | -0.18183 | 122.9892 | 122.912 | 123.0679 | 66.7525 | -123.1241 | 122.9084 | 123.0862 | 122.8559 | 66.7515 | -123.3564
858.7969 | 123.143 | -66.7191 | 56.282 | -0.013431 | -0.007767 | 0.00082041 | 0.056224 | -0.0022669 | 0.062155 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058879 | 0.014216 | 0.060141 | -66.6923 | 0.019721 | -66.7277 | 56.2518 | 56.1792 | 56.3306 | -66.8146 | -66.7108 | 0.014095 | -66.7361 | 56.1619 | 56.3488 | 56.146 | -67.0561 | -0.095564 | -0.030204 | 0.026727 | -0.008637 | 0.086927 | -0.10286 | 0.048533 | -0.33703 | -0.12013 | 0.0083 | -0.017048 | 0.31999 | 0.066789 | -0.13605 | 122.9709 | 122.8982 | 123.0496 | 66.7388 | -123.0967 | 122.881 | 123.0679 | 122.8651 | 66.7331 | -123.3381
859.7969 | 123.111 | -66.7282 | 56.2912 | -0.0057996 | -0.0079808 | 0.0010342 | 0.056011 | -0.0020533 | 0.062155 | -0.0093855 | -0.00017733 | 0.00046581 | 0.058879 | 0.013788 | 0.059927 | -66.7015 | 0.019721 | -66.7231 | 56.2518 | 56.1746 | 56.3352 | -66.8192 | -66.7199 | 0.018674 | -66.7315 | 56.1665 | 56.3488 | 56.2009 | -67.0561 | -0.090988 | -0.03936 | 0.026725 | 0.005097 | 0.096085 | -0.11659 | 0.043956 | -0.32788 | -0.1247 | 0.008298 | -0.003314 | 0.32457 | 0.057633 | -0.09026 | 122.98 | 122.9028 | 123.0634 | 66.7479 | -123.1104 | 122.8947 | 123.077 | 122.9291 | 66.7469 | -123.3473
860.7969 | 123.1338 | -66.7191 | 56.3095 | -0.0057996 | -0.0081944 | 0.0010342 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.059307 | 0.013575 | 0.059287 | -66.6969 | 0.015142 | -66.7277 | 56.2564 | 56.1746 | 56.3352 | -66.8146 | -66.7153 | 0.018674 | -66.7269 | 56.1619 | 56.3443 | 56.1643 | -67.0607 | -0.095564 | -0.053092 | 0.022148 | -0.008637 | 0.086927 | -0.1349 | 0.025646 | -0.34161 | -0.14759 | 0.003721 | -0.00789 | 0.33372 | 0.034744 | -0.1452 | 122.9755 | 122.8937 | 123.0542 | 66.7342 | -123.1241 | 122.881 | 123.0633 | 122.8834 | 66.7377 | -123.3702
861.7969 | 123.1384 | -66.7328 | 56.2866 | 0.0018314 | -0.007767 | 0.0010342 | 0.055797 | -0.0018397 | 0.061727 | -0.001755 | -0.00060453 | 0.00046581 | 0.059307 | 0.014002 | 0.059927 | -66.7061 | 0.015142 | -66.7231 | 56.2564 | 56.1792 | 56.3352 | -66.8192 | -66.7062 | 0.018674 | -66.7407 | 56.1665 | 56.3443 | 56.2147 | -67.0515 | -0.08641 | -0.030204 | 0.026724 | 0.009675 | 0.096085 | -0.10744 | 0.048534 | -0.31872 | -0.12012 | 0.026612 | -0.007893 | 0.31083 | 0.057632 | -0.071946 | 122.9892 | 122.912 | 123.0679 | 66.7479 | -123.1058 | 122.8993 | 123.077 | 122.9475 | 66.7515 | -123.3381
862.7969 | 123.2208 | -66.7145 | 56.2912 | 0.0018314 | -0.0081944 | 0.00060681 | 0.056652 | -0.0024807 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.014216 | 0.059714 | -66.7015 | 0.010564 | -66.7185 | 56.2518 | 56.1654 | 56.3352 | -66.81 | -66.7153 | 0.014095 | -66.7407 | 56.1619 | 56.3534 | 56.1689 | -67.0607 | -0.095562 | -0.03936 | 0.012993 | -0.004057 | 0.091505 | -0.12575 | 0.043956 | -0.34619 | -0.12928 | -0.000856 | -0.026203 | 0.31999 | 0.062211 | -0.12231 | 122.9663 | 122.8799 | 123.0496 | 66.725 | -123.1012 | 122.8764 | 123.0679 | 122.8834 | 66.7286 | -123.3519
863.7969 | 123.1293 | -66.7191 | 56.3232 | -0.013431 | -0.007767 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.00089321 | 0.059093 | 0.014216 | 0.059714 | -66.6923 | 0.010564 | -66.7231 | 56.2564 | 56.1792 | 56.3352 | -66.8192 | -66.7153 | 0.014095 | -66.7315 | 56.1619 | 56.3443 | 56.1231 | -67.0652 | -0.10014 | -0.066825 | 0.026727 | -0.004058 | 0.096085 | -0.14406 | 0.011913 | -0.34619 | -0.16132 | 0.003721 | -0.012469 | 0.33372 | 0.021011 | -0.20014 | 122.9755 | 122.8982 | 123.0542 | 66.7296 | -123.1424 | 122.881 | 123.0633 | 122.8422 | 66.7331 | -123.3885
864.7969 | 123.1201 | -66.7465 | 56.3278 | -0.021062 | -0.0081944 | 0.0012478 | 0.056224 | -0.0020533 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014002 | 0.059927 | -66.6969 | 0.019721 | -66.7277 | 56.2564 | 56.1883 | 56.3397 | -66.8192 | -66.7153 | 0.014095 | -66.7315 | 56.1757 | 56.3443 | 56.1094 | -67.0515 | -0.072677 | -0.071403 | 0.049614 | 0.018829 | 0.091506 | -0.13948 | 0.011913 | -0.30499 | -0.15217 | 0.031187 | 0.014997 | 0.31999 | 0.016433 | -0.21845 | 123.0029 | 122.9349 | 123.0863 | 66.7662 | -123.147 | 122.9222 | 123.0908 | 122.8559 | 66.7606 | -123.3793
865.7969 | 123.0835 | -66.7191 | 56.3461 | -0.013431 | -0.0081944 | 0.0010342 | 0.055797 | -0.0026943 | 0.061941 | -0.0093855 | -0.00039093 | 3.8406e-05 | 0.059307 | 0.013575 | 0.059927 | -66.6923 | 0.019721 | -66.7231 | 56.2473 | 56.1746 | 56.3397 | -66.8238 | -66.7062 | 0.018674 | -66.7453 | 56.1573 | 56.3443 | 56.1689 | -67.0515 | -0.10472 | -0.09887 | 0.026727 | -0.004058 | 0.10066 | -0.17153 | -0.006397 | -0.33245 | -0.18879 | 0.012879 | -0.026205 | 0.30625 | -0.001877 | -0.17724 | 122.9663 | 122.8937 | 123.0588 | 66.7388 | -123.1699 | 122.8764 | 123.0633 | 122.8879 | 66.7377 | -123.3976
866.7969 | 123.2208 | -66.6824 | 56.2592 | 0.0018314 | -0.0079808 | 0.00060681 | 0.056224 | -0.0020533 | 0.062155 | -0.001755 | -0.00060453 | 0.00046581 | 0.059307 | 0.014002 | 0.059714 | -66.6969 | 0.010564 | -66.7185 | 56.2518 | 56.1746 | 56.3352 | -66.8146 | -66.7153 | 0.018674 | -66.7361 | 56.1665 | 56.3443 | 56.1277 | -67.0607 | -0.13218 | -0.007316 | -0.014473 | -0.036101 | 0.096084 | -0.08455 | 0.076 | -0.37823 | -0.092659 | -0.0329 | -0.053669 | 0.32457 | 0.085098 | -0.13147 | 122.9343 | 122.857 | 123.0176 | 66.693 | -123.0738 | 122.8489 | 123.0267 | 122.8101 | 66.7011 | -123.3198
867.7969 | 123.1842 | -66.687 | 56.3278 | -0.0057996 | -0.0081944 | 0.00082041 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | -0.00060453 | 0.00089321 | 0.059307 | 0.013788 | 0.059714 | -66.6969 | 0.010564 | -66.7185 | 56.2564 | 56.1746 | 56.3397 | -66.8192 | -66.7199 | 0.014095 | -66.7361 | 56.1711 | 56.3397 | 56.1826 | -67.0515 | -0.13219 | -0.071403 | -0.009895 | -0.031523 | 0.10066 | -0.15322 | 0.011913 | -0.3645 | -0.15675 | -0.0329 | -0.049091 | 0.31541 | 0.011855 | -0.1452 | 122.9434 | 122.8616 | 123.0267 | 66.6976 | -123.147 | 122.8581 | 123.0267 | 122.8696 | 66.7011 | -123.3793
868.7969 | 123.1201 | -66.7328 | 56.3187 | 0.0018314 | -0.008408 | 0.0012478 | 0.056224 | -0.0020533 | 0.062155 | 0.0058755 | -0.00017733 | 0.00067941 | 0.059307 | 0.014002 | 0.0595 | -66.6969 | 0.010564 | -66.7277 | 56.2564 | 56.1746 | 56.3397 | -66.8192 | -66.7153 | 0.009516 | -66.7407 | 56.1665 | 56.3397 | 56.2055 | -67.0515 | -0.08641 | -0.062248 | 0.035881 | 0.005096 | 0.091506 | -0.14406 | 0.021068 | -0.31872 | -0.15217 | 0.017454 | -0.007893 | 0.31083 | 0.02101 | -0.11315 | 122.9892 | 122.9074 | 123.0725 | 66.7434 | -123.1379 | 122.8993 | 123.0725 | 122.9383 | 66.7423 | -123.3702
869.7969 | 123.1522 | -66.7145 | 56.3141 | -0.0057996 | -0.0079808 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | 0.013506 | -0.00081813 | 0.00067941 | 0.058666 | 0.014216 | 0.0595 | -66.7015 | 0.019721 | -66.7231 | 56.2564 | 56.1746 | 56.3352 | -66.8192 | -66.7108 | 0.018674 | -66.7315 | 56.1711 | 56.3397 | 56.1964 | -67.0515 | -0.10472 | -0.05767 | 0.012993 | -0.008635 | 0.096085 | -0.13948 | 0.021068 | -0.33703 | -0.14301 | 0.003723 | -0.017046 | 0.31999 | 0.025588 | -0.11773 | 122.9709 | 122.8891 | 123.0496 | 66.7342 | -123.1333 | 122.8856 | 123.0542 | 122.9108 | 66.7332 | -123.3656
870.7969 | 123.2712 | -66.655 | 56.2729 | 0.0018314 | -0.0081944 | 0.0012478 | 0.056224 | -0.0022669 | 0.061941 | -0.001755 | -0.00017733 | 0.00089321 | 0.058879 | 0.014002 | 0.059287 | -66.6923 | 0.019721 | -66.7277 | 56.2518 | 56.1746 | 56.3352 | -66.8192 | -66.7062 | 0.009516 | -66.7361 | 56.1619 | 56.3443 | 56.1597 | -67.0561 | -0.16423 | -0.021049 | -0.03736 | -0.072724 | 0.091506 | -0.098283 | 0.062267 | -0.40112 | -0.11097 | -0.051208 | -0.081135 | 0.31999 | 0.071365 | -0.11316 | 122.9068 | 122.8296 | 122.9901 | 66.6747 | -123.0921 | 122.8169 | 122.9992 | 122.8147 | 66.6645 | -123.329
871.7969 | 123.2346 | -66.6824 | 56.25 | 0.0018314 | -0.0079808 | 0.0012478 | 0.056438 | -0.0020533 | 0.061941 | -0.001755 | -0.00017733 | 0.00067941 | 0.058879 | 0.014002 | 0.059714 | -66.6923 | 0.015142 | -66.7231 | 56.2564 | 56.1792 | 56.3306 | -66.8146 | -66.7153 | 0.014095 | -66.7361 | 56.1619 | 56.3488 | 56.1643 | -67.0561 | -0.13218 | 0.006417 | -0.009894 | -0.040679 | 0.091506 | -0.070816 | 0.080576 | -0.37365 | -0.088083 | -0.0329 | -0.053669 | 0.31999 | 0.098832 | -0.085689 | 122.9389 | 122.8616 | 123.013 | 66.6976 | -123.0646 | 122.8444 | 123.0313 | 122.8467 | 66.6965 | -123.3061
872.7969 | 123.2254 | -66.6962 | 56.2637 | -0.0057996 | -0.0079808 | 0.00082041 | 0.056438 | -0.0022669 | 0.061727 | -0.0093855 | -0.00060453 | 0.00089321 | 0.059093 | 0.014216 | 0.0595 | -66.6923 | 0.015142 | -66.7231 | 56.2564 | 56.1838 | 56.3306 | -66.8192 | -66.7062 | 0.009516 | -66.7361 | 56.1619 | 56.3488 | 56.1826 | -67.0515 | -0.12303 | -0.007316 | 0.003839 | -0.026946 | 0.096085 | -0.07997 | 0.066843 | -0.35534 | -0.10182 | -0.010009 | -0.039936 | 0.31541 | 0.085099 | -0.081108 | 122.9526 | 122.8799 | 123.0267 | 66.7113 | -123.0829 | 122.8581 | 123.045 | 122.8788 | 66.7057 | -123.3152
873.7969 | 123.1338 | -66.7282 | 56.3232 | -0.0057996 | -0.0081944 | 0.00060681 | 0.056011 | -0.0018397 | 0.061941 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059307 | 0.014216 | 0.059714 | -66.6969 | 0.019721 | -66.7277 | 56.2564 | 56.1929 | 56.3443 | -66.8284 | -66.7153 | 0.018674 | -66.7361 | 56.1619 | 56.3397 | 56.1506 | -67.0561 | -0.10015 | -0.066825 | 0.031303 | 0.000518 | 0.10066 | -0.13032 | 0.02107 | -0.32788 | -0.16132 | 0.012876 | -0.007893 | 0.31999 | 0.016433 | -0.17267 | 122.9846 | 122.9211 | 123.0725 | 66.7479 | -123.1516 | 122.8901 | 123.0679 | 122.8788 | 66.7469 | -123.3793
874.7969 | 123.111 | -66.7282 | 56.2958 | -0.013431 | -0.0079808 | 0.00060681 | 0.056011 | -0.0029079 | 0.062155 | -0.001755 | -0.00017733 | 0.00067941 | 0.059093 | 0.014002 | 0.059714 | -66.7015 | 0.015142 | -66.7277 | 56.261 | 56.1883 | 56.3352 | -66.81 | -66.7062 | 0.018674 | -66.7315 | 56.1665 | 56.3443 | 56.146 | -67.0607 | -0.08183 | -0.034781 | 0.026725 | 0.000518 | 0.082348 | -0.10743 | 0.039379 | -0.33246 | -0.12928 | 0.022034 | -0.003314 | 0.32914 | 0.048477 | -0.14978 | 122.9892 | 122.9166 | 123.0634 | 66.7434 | -123.1058 | 122.8947 | 123.0725 | 122.8742 | 66.7469 | -123.3564
875.7969 | 123.1659 | -66.7419 | 56.3049 | 0.0094624 | -0.008408 | 0.00082041 | 0.055583 | -0.0020533 | 0.061941 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014216 | 0.0595 | -66.6969 | 0.019721 | -66.7185 | 56.2564 | 56.1746 | 56.3397 | -66.81 | -66.7108 | 0.014095 | -66.7315 | 56.1619 | 56.3443 | 56.1506 | -67.0561 | -0.068097 | -0.048515 | 0.045036 | 0.023408 | 0.091505 | -0.13033 | 0.034801 | -0.31415 | -0.14301 | 0.031188 | 0.010419 | 0.32457 | 0.039321 | -0.15436 | 122.9984 | 122.9165 | 123.0817 | 66.7617 | -123.115 | 122.9039 | 123.0862 | 122.8925 | 66.756 | -123.361
876.7969 | 123.2437 | -66.6824 | 56.2729 | -0.0057996 | -0.0079808 | 0.00082041 | 0.056652 | -0.0024807 | 0.061941 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014429 | 0.059714 | -66.6923 | 0.019721 | -66.7231 | 56.2427 | 56.1838 | 56.3352 | -66.81 | -66.7153 | 0.014095 | -66.7361 | 56.1665 | 56.3443 | 56.2101 | -67.0515 | -0.12761 | -0.030206 | -0.009894 | -0.040679 | 0.086927 | -0.089125 | 0.062267 | -0.36908 | -0.10639 | -0.0329 | -0.053669 | 0.31541 | 0.071365 | -0.062791 | 122.9251 | 122.8662 | 123.0176 | 66.7022 | -123.0829 | 122.8489 | 123.0267 | 122.8925 | 66.6965 | -123.3244
877.7969 | 123.1293 | -66.7419 | 56.3049 | 0.0018314 | -0.0081944 | 0.00060681 | 0.056224 | -0.0020533 | 0.061941 | 0.013506 | -0.00060453 | 0.00089321 | 0.058879 | 0.014429 | 0.059927 | -66.7061 | 0.010564 | -66.7231 | 56.2518 | 56.1792 | 56.3443 | -66.8192 | -66.7153 | 0.014095 | -66.7315 | 56.1711 | 56.3397 | 56.146 | -67.0515 | -0.077255 | -0.053093 | 0.035879 | 0.01883 | 0.096085 | -0.12575 | 0.03938 | -0.30957 | -0.13386 | 0.026609 | 0.010419 | 0.31999 | 0.034743 | -0.15894 | 122.9938 | 122.9211 | 123.0863 | 66.7525 | -123.1241 | 122.913 | 123.0816 | 122.8879 | 66.756 | -123.3564
878.7969 | 123.2437 | -66.7191 | 56.2866 | 0.0018314 | -0.008408 | 0.00039321 | 0.055797 | -0.0026943 | 0.061941 | -0.0093855 | -0.00081813 | 0.00089321 | 0.059093 | 0.014216 | 0.0595 | -66.6923 | 0.019721 | -66.7185 | 56.261 | 56.1746 | 56.3397 | -66.8146 | -66.7108 | 0.014095 | -66.7361 | 56.1619 | 56.3397 | 56.2055 | -67.0561 | -0.095564 | -0.025626 | 0.026727 | 0.00052 | 0.096084 | -0.11202 | 0.053112 | -0.33703 | -0.1247 | 0.0083 | -0.017048 | 0.31999 | 0.053054 | -0.081103 | 122.9801 | 122.8937 | 123.0588 | 66.7388 | -123.1012 | 122.881 | 123.0587 | 122.9246 | 66.7331 | -123.3427
879.7969 | 123.0972 | -66.7191 | 56.3324 | 0.017093 | -0.008408 | 0.00082041 | 0.056011 | -0.0020533 | 0.061941 | 0.0058755 | -0.00039093 | 0.00046581 | 0.059093 | 0.014429 | 0.0595 | -66.7015 | 0.010564 | -66.7231 | 56.2564 | 56.1838 | 56.3397 | -66.8146 | -66.7062 | 0.018674 | -66.7315 | 56.1711 | 56.3443 | 56.1048 | -67.0515 | -0.095564 | -0.07598 | 0.01757 | -0.004058 | 0.091506 | -0.14863 | 0.007336 | -0.33245 | -0.16132 | 0.012879 | -0.012469 | 0.31999 | 0.011856 | -0.22761 | 122.9755 | 122.9028 | 123.0588 | 66.7296 | -123.147 | 122.8901 | 123.0633 | 122.8238 | 66.7377 | -123.3839
880.7969 | 123.1842 | -66.7236 | 56.282 | -0.0057996 | -0.007767 | 0.0010342 | 0.056011 | -0.0020533 | 0.062155 | -0.001755 | -0.00017733 | 0.00025221 | 0.059093 | 0.014002 | 0.059714 | -66.6969 | 0.010564 | -66.7185 | 56.2518 | 56.17 | 56.3397 | -66.81 | -66.7108 | 0.009516 | -66.7315 | 56.1665 | 56.3534 | 56.1002 | -67.0561 | -0.086407 | -0.030204 | 0.026726 | 0.005098 | 0.091505 | -0.11202 | 0.05769 | -0.33246 | -0.11555 | 0.012878 | -0.007891 | 0.32457 | 0.071367 | -0.18183 | 122.9755 | 122.8937 | 123.0634 | 66.7342 | -123.0921 | 122.8901 | 123.077 | 122.8238 | 66.7331 | -123.3381
881.7969 | 123.1338 | -66.6962 | 56.3141 | 0.0018314 | -0.0081944 | 0.00060681 | 0.056224 | -0.0022669 | 0.061941 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059093 | 0.014002 | 0.059714 | -66.7015 | 0.015142 | -66.7231 | 56.2564 | 56.1746 | 56.3443 | -66.8192 | -66.7108 | 0.014095 | -66.7407 | 56.1665 | 56.3443 | 56.1048 | -67.0561 | -0.12303 | -0.05767 | -0.005318 | -0.026946 | 0.096085 | -0.13948 | 0.030225 | -0.35992 | -0.14759 | -0.014588 | -0.044514 | 0.31541 | 0.030166 | -0.2093 | 122.9526 | 122.8708 | 123.0405 | 66.7113 | -123.1333 | 122.8627 | 123.0404 | 122.801 | 66.7103 | -123.3702
882.7969 | 123.1659 | -66.7053 | 56.2866 | 0.0018314 | -0.0081944 | 0.00082041 | 0.056438 | -0.0022669 | 0.062155 | -0.0093855 | -0.00017733 | 0.00089321 | 0.059093 | 0.014216 | 0.0595 | -66.6969 | 0.015142 | -66.7185 | 56.2518 | 56.1746 | 56.3397 | -66.8146 | -66.7062 | 0.009516 | -66.7315 | 56.1711 | 56.3397 | 56.1964 | -67.0561 | -0.1093 | -0.034782 | 0.008415 | -0.013213 | 0.096084 | -0.11202 | 0.053112 | -0.35077 | -0.11555 | -0.000854 | -0.026202 | 0.32457 | 0.053054 | -0.09026 | 122.9572 | 122.8799 | 123.0451 | 66.7205 | -123.1012 | 122.8764 | 123.045 | 122.9017 | 66.7148 | -123.3427
883.7969 | 123.1613 | -66.7053 | 56.3004 | -0.013431 | -0.0079808 | 0.00082041 | 0.056224 | -0.0029079 | 0.061941 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059307 | 0.014216 | 0.059927 | -66.6969 | 0.015142 | -66.7277 | 56.2473 | 56.1883 | 56.3397 | -66.8192 | -66.7153 | 0.018674 | -66.7315 | 56.1619 | 56.3488 | 56.1826 | -67.0561 | -0.11388 | -0.053094 | 0.008415 | -0.02237 | 0.091506 | -0.11201 | 0.039379 | -0.35077 | -0.13844 | -0.010012 | -0.026202 | 0.32457 | 0.048478 | -0.11773 | 122.9526 | 122.8937 | 123.0451 | 66.7205 | -123.1196 | 122.8672 | 123.0542 | 122.8879 | 66.724 | -123.3564
884.7969 | 123.2437 | -66.6779 | 56.2775 | -0.0057996 | -0.008408 | 0.0010342 | 0.056224 | -0.0024807 | 0.062155 | -0.017016 | -0.00039093 | 0.0011068 | 0.059093 | 0.014002 | 0.059927 | -66.6969 | 0.015142 | -66.7185 | 56.2518 | 56.1654 | 56.3352 | -66.8192 | -66.7108 | 0.014095 | -66.7361 | 56.1711 | 56.3488 | 56.178 | -67.0561 | -0.14134 | -0.025627 | -0.019051 | -0.040679 | 0.10066 | -0.11202 | 0.057689 | -0.37823 | -0.10639 | -0.032899 | -0.058247 | 0.31999 | 0.071366 | -0.09942 | 122.9297 | 122.8433 | 123.013 | 66.693 | -123.0967 | 122.8489 | 123.0267 | 122.8559 | 66.692 | -123.3336
885.8438 | 123.0698 | -66.7648 | 56.3049 | 0.0018314 | -0.0086218 | 0.00082041 | 0.056224 | -0.0024807 | 0.062155 | -0.001755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014857 | 0.0595 | -66.6969 | 0.019721 | -66.7231 | 56.261 | 56.1792 | 56.3443 | -66.8146 | -66.7153 | 0.014095 | -66.7315 | 56.1665 | 56.3443 | 56.1368 | -67.0469 | -0.049787 | -0.043937 | 0.067925 | 0.041719 | 0.091506 | -0.12575 | 0.03938 | -0.2821 | -0.13844 | 0.049498 | 0.033308 | 0.31541 | 0.039321 | -0.16809 | 123.0258 | 122.944 | 123.1091 | 66.7846 | -123.1196 | 122.9313 | 123.1091 | 122.9017 | 66.7789 | -123.3519
886.7969 | 123.1247 | -66.7328 | 56.2912 | -0.0057996 | -0.008408 | 0.00060681 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058879 | 0.014002 | 0.059714 | -66.6969 | 0.019721 | -66.7185 | 56.2564 | 56.1746 | 56.3397 | -66.8146 | -66.7153 | 0.014095 | -66.7361 | 56.1619 | 56.3397 | 56.2009 | -67.0515 | -0.081831 | -0.034782 | 0.035881 | 0.014253 | 0.096084 | -0.11659 | 0.048534 | -0.31872 | -0.12928 | 0.017454 | -0.003315 | 0.31541 | 0.048476 | -0.09026 | 122.9892 | 122.9074 | 123.0725 | 66.7525 | -123.1058 | 122.8947 | 123.0725 | 122.9337 | 66.7469 | -123.3427
887.7969 | 123.1796 | -66.7145 | 56.2408 | -0.0057996 | -0.0081944 | 0.00082041 | 0.056438 | -0.0024807 | 0.061941 | 0.0058755 | -0.00039093 | 0.00046581 | 0.059093 | 0.014216 | 0.059714 | -66.6969 | 0.015142 | -66.7185 | 56.2564 | 56.17 | 56.3352 | -66.8146 | -66.7108 | 0.009516 | -66.7315 | 56.1665 | 56.3488 | 56.1002 | -67.0515 | -0.10014 | 0.015572 | 0.017571 | -0.004057 | 0.096084 | -0.070819 | 0.09431 | -0.33703 | -0.074349 | 0.003723 | -0.017046 | 0.31999 | 0.10799 | -0.14064 | 122.9709 | 122.8845 | 123.0496 | 66.7296 | -123.0555 | 122.881 | 123.0633 | 122.8147 | 66.724 | -123.2924
888.7969 | 123.1201 | -66.6916 | 56.3461 | -0.0057996 | -0.008408 | 0.00060681 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014429 | 0.060141 | -66.6923 | 0.015142 | -66.7185 | 56.2564 | 56.1792 | 56.3352 | -66.8146 | -66.7108 | 0.018674 | -66.7453 | 56.1665 | 56.3397 | 56.2009 | -67.0515 | -0.12303 | -0.089713 | -0.000739 | -0.026946 | 0.096084 | -0.16695 | -0.010975 | -0.35992 | -0.17963 | -0.019166 | -0.053671 | 0.30625 | -0.006455 | -0.14519 | 122.948 | 122.8708 | 123.0267 | 66.7067 | -123.1607 | 122.8581 | 123.0313 | 122.8925 | 66.7103 | -123.3976
889.7969 | 123.1613 | -66.7099 | 56.3232 | 0.0018314 | -0.0086218 | 0.00082041 | 0.055797 | -0.0024807 | 0.061941 | -0.001755 | -0.00017733 | 0.00046581 | 0.058879 | 0.014216 | 0.0595 | -66.6969 | 0.015142 | -66.7277 | 56.2564 | 56.1792 | 56.3397 | -66.8192 | -66.7108 | 0.023253 | -66.7361 | 56.1665 | 56.3488 | 56.2147 | -67.0469 | -0.1093 | -0.066825 | 0.012993 | -0.017792 | 0.091506 | -0.14406 | 0.016491 | -0.33703 | -0.15675 | -0.000855 | -0.026203 | 0.31083 | 0.02559 | -0.10857 | 122.9663 | 122.8891 | 123.0496 | 66.725 | -123.1424 | 122.8764 | 123.0587 | 122.9246 | 66.7332 | -123.3702
890.7969 | 123.1247 | -66.7053 | 56.3141 | 0.0094624 | -0.0079808 | 0.00082041 | 0.056011 | -0.0024807 | 0.061941 | -0.001755 | -0.00060453 | 0.00089321 | 0.05952 | 0.014429 | 0.059714 | -66.6923 | 0.015142 | -66.7231 | 56.2564 | 56.1792 | 56.3352 | -66.8146 | -66.7016 | 0.018674 | -66.7269 | 56.1711 | 56.3443 | 56.2147 | -67.0561 | -0.1093 | -0.05767 | 0.012994 | -0.017791 | 0.091506 | -0.1349 | 0.021068 | -0.35077 | -0.14301 | 0.003724 | -0.021623 | 0.32914 | 0.030166 | -0.099412 | 122.9617 | 122.8845 | 123.0405 | 66.7205 | -123.1287 | 122.8764 | 123.0496 | 122.92 | 66.724 | -123.3702
891.7969 | 123.1522 | -66.7099 | 56.3278 | 0.0094624 | -0.008408 | 0.0014616 | 0.056224 | -0.0024807 | 0.061941 | -0.001755 | -0.00081813 | 0.00067941 | 0.059093 | 0.014216 | 0.0595 | -66.6923 | 0.010564 | -66.7277 | 56.261 | 56.1792 | 56.3443 | -66.8146 | -66.7108 | 0.014095 | -66.7315 | 56.1665 | 56.3534 | 56.1597 | -67.0515 | -0.10472 | -0.066825 | 0.017572 | -0.017792 | 0.086927 | -0.14864 | 0.016492 | -0.34161 | -0.16132 | -0.000855 | -0.021624 | 0.31999 | 0.02559 | -0.16809 | 122.9709 | 122.8891 | 123.0542 | 66.7205 | -123.1424 | 122.8764 | 123.0633 | 122.8696 | 66.724 | -123.3793
892.7969 | 123.2849 | -66.6641 | 56.2866 | 0.0018314 | -0.0086218 | 0.0010342 | 0.056438 | -0.0022669 | 0.061727 | -0.001755 | -0.00060453 | 0.00089321 | 0.058666 | 0.014216 | 0.0595 | -66.6923 | 0.015142 | -66.714 | 56.2564 | 56.1883 | 56.3352 | -66.8146 | -66.7062 | 0.004938 | -66.7269 | 56.1665 | 56.3534 | 56.1964 | -67.0515 | -0.15049 | -0.030204 | -0.028204 | -0.049833 | 0.10066 | -0.098279 | 0.048534 | -0.38739 | -0.12012 | -0.042052 | -0.062821 | 0.32456 | 0.066789 | -0.09026 | 122.9205 | 122.8525 | 122.9993 | 66.6793 | -123.1012 | 122.8306 | 123.0175 | 122.8605 | 66.6691 | -123.3381
893.7969 | 123.0057 | -66.7236 | 56.2912 | 0.0094624 | -0.008408 | 0.00082041 | 0.056224 | -0.0024807 | 0.061727 | -0.0093855 | -0.00060453 | 0.00046581 | 0.059093 | 0.014429 | 0.0595 | -66.6877 | 0.019721 | -66.7185 | 56.2518 | 56.1883 | 56.3397 | -66.8192 | -66.7108 | 0.014095 | -66.7269 | 56.1711 | 56.3443 | 56.178 | -67.0561 | -0.095565 | -0.03936 | 0.035883 | 0.005098 | 0.10066 | -0.10286 | 0.048534 | -0.33246 | -0.12013 | 0.012878 | -0.003312 | 0.32914 | 0.053054 | -0.11315 | 122.9755 | 122.912 | 123.0634 | 66.7434 | -123.1104 | 122.8947 | 123.0679 | 122.9017 | 66.7377 | -123.3473
894.7969 | 123.1338 | -66.7099 | 56.3232 | 0.0018314 | -0.008408 | 0.0010342 | 0.056224 | -0.0022669 | 0.062155 | 0.013506 | -0.00039093 | 0.00089321 | 0.058879 | 0.014643 | 0.0595 | -66.6923 | 0.019721 | -66.7185 | 56.2564 | 56.17 | 56.3443 | -66.8192 | -66.7108 | 0.018674 | -66.7315 | 56.1665 | 56.3443 | 56.2009 | -67.0469 | -0.1093 | -0.066825 | 0.017572 | -0.008635 | 0.10066 | -0.15322 | 0.02107 | -0.33703 | -0.15675 | -0.000855 | -0.021624 | 0.31541 | 0.021011 | -0.1223 | 122.9663 | 122.8799 | 123.0542 | 66.7296 | -123.1424 | 122.8764 | 123.0542 | 122.9108 | 66.7286 | -123.3702
895.7969 | 123.1613 | -66.7236 | 56.2729 | -0.0057996 | -0.0081944 | 0.0010342 | 0.056011 | -0.0024807 | 0.061514 | -0.001755 | -0.00060453 | 0.00089321 | 0.059093 | 0.014002 | 0.059927 | -66.6877 | 0.019721 | -66.7185 | 56.2564 | 56.1838 | 56.3397 | -66.8146 | -66.7062 | 0.014095 | -66.7315 | 56.1619 | 56.3534 | 56.1872 | -67.0561 | -0.090986 | -0.016471 | 0.035883 | 0.005098 | 0.096084 | -0.089125 | 0.066845 | -0.33246 | -0.11097 | 0.017457 | -0.007891 | 0.32457 | 0.080522 | -0.085684 | 122.9801 | 122.9074 | 123.0634 | 66.7434 | -123.0875 | 122.8856 | 123.077 | 122.9108 | 66.7377 | -123.329
896.7969 | 123.1247 | -66.7328 | 56.2912 | 0.0018314 | -0.0086218 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.0093855 | -0.00017733 | 0.00046581 | 0.058879 | 0.014429 | 0.0595 | -66.6877 | 0.015142 | -66.7277 | 56.2518 | 56.1883 | 56.3352 | -66.8192 | -66.7153 | 0.018674 | -66.7315 | 56.1665 | 56.3443 | 56.2009 | -67.0561 | -0.08641 | -0.03936 | 0.045038 | 0.005096 | 0.091506 | -0.10286 | 0.043956 | -0.3233 | -0.1247 | 0.017454 | 0.001264 | 0.32457 | 0.053054 | -0.09026 | 122.9846 | 122.9211 | 123.0679 | 66.7479 | -123.1104 | 122.8993 | 123.077 | 122.9337 | 66.7515 | -123.3473
897.7969 | 123.2391 | -66.6733 | 56.2683 | 0.0018314 | -0.008408 | 0.00082041 | 0.056652 | -0.0024807 | 0.061727 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058879 | 0.014216 | 0.060141 | -66.6969 | 0.010564 | -66.7231 | 56.2518 | 56.1929 | 56.3443 | -66.8146 | -66.7108 | 0.009516 | -66.7269 | 56.1665 | 56.3443 | 56.1552 | -67.0469 | -0.14134 | -0.016472 | -0.023628 | -0.049834 | 0.091506 | -0.07539 | 0.076001 | -0.37365 | -0.10181 | -0.037476 | -0.053666 | 0.31999 | 0.075942 | -0.11316 | 122.9251 | 122.8662 | 123.0176 | 66.6838 | -123.0829 | 122.8398 | 123.0175 | 122.8284 | 66.6828 | -123.3152
898.7969 | 123.1567 | -66.7053 | 56.3232 | -0.013431 | -0.008408 | 0.00082041 | 0.056011 | -0.0022669 | 0.062155 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058879 | 0.014429 | 0.059714 | -66.6923 | 0.015142 | -66.7185 | 56.2564 | 56.1654 | 56.3489 | -66.8192 | -66.7108 | 0.014095 | -66.7269 | 56.1711 | 56.3443 | 56.2009 | -67.0515 | -0.11388 | -0.066825 | 0.012994 | -0.013213 | 0.10066 | -0.1578 | 0.025648 | -0.34619 | -0.15217 | -0.005433 | -0.021623 | 0.32456 | 0.021011 | -0.1223 | 122.9617 | 122.8708 | 123.0542 | 66.7205 | -123.1424 | 122.8764 | 123.0496 | 122.9063 | 66.7194 | -123.3748
899.7969 | 123.1567 | -66.6916 | 56.3278 | 0.0018314 | -0.0086218 | 0.0010342 | 0.056011 | -0.0024807 | 0.062155 | -0.0093855 | -0.00017733 | 0.00067941 | 0.058879 | 0.014216 | 0.059927 | -66.6969 | 0.010564 | -66.7277 | 56.2564 | 56.1838 | 56.3397 | -66.8192 | -66.7108 | 0.014095 | -66.7269 | 56.1619 | 56.3488 | 56.2147 | -67.0469 | -0.12761 | -0.071403 | -0.005318 | -0.036103 | 0.091506 | -0.14406 | 0.011913 | -0.35534 | -0.1659 | -0.019166 | -0.035356 | 0.31999 | 0.021012 | -0.11315 | 122.948 | 122.8754 | 123.0313 | 66.7022 | -123.147 | 122.8535 | 123.0404 | 122.9063 | 66.7057 | -123.3748
900.7969 | 123.1064 | -66.7328 | 56.25 | -0.013431 | -0.008408 | 0.00082041 | 0.055797 | -0.0022669 | 0.062155 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059093 | 0.014429 | 0.059714 | -66.6969 | 0.019721 | -66.714 | 56.2564 | 56.1838 | 56.3352 | -66.8192 | -66.7062 | 0.014095 | -66.7315 | 56.1665 | 56.3488 | 56.2009 | -67.0469 | -0.08641 | 0.006417 | 0.035881 | 0.018831 | 0.10524 | -0.066237 | 0.085155 | -0.31414 | -0.083504 | 0.026612 | 0.001264 | 0.31541 | 0.098832 | -0.049061 | 122.9892 | 122.9166 | 123.0679 | 66.7525 | -123.0692 | 122.8993 | 123.0816 | 122.9337 | 66.7469 | -123.2969
901.7969 | 123.1934 | -66.6962 | 56.3278 | -0.0057996 | -0.0081944 | 0.00060681 | 0.055797 | -0.0024807 | 0.062155 | 0.0058755 | -0.00017733 | 0.0011068 | 0.059093 | 0.014643 | 0.0595 | -66.6877 | 0.010564 | -66.7185 | 56.261 | 56.1838 | 56.3397 | -66.8192 | -66.7062 | 0.009516 | -66.7269 | 56.1619 | 56.3397 | 56.1368 | -67.0515 | -0.12303 | -0.066825 | 0.008417 | -0.022368 | 0.10066 | -0.14406 | 0.011913 | -0.35534 | -0.1659 | -0.010009 | -0.030778 | 0.32456 | 0.011855 | -0.19098 | 122.9572 | 122.8799 | 123.0359 | 66.7067 | -123.147 | 122.8581 | 123.0358 | 122.833 | 66.7057 | -123.3793
902.7969 | 123.1842 | -66.7007 | 56.2912 | 0.0094624 | -0.0086218 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | -0.017016 | -0.00017733 | 0.00067941 | 0.058666 | 0.014216 | 0.059714 | -66.6923 | 0.019721 | -66.7185 | 56.2564 | 56.1838 | 56.3397 | -66.81 | -66.7108 | 0.018674 | -66.7315 | 56.1711 | 56.3443 | 56.1872 | -67.0561 | -0.1093 | -0.034782 | 0.008417 | -0.01779 | 0.091505 | -0.10744 | 0.048534 | -0.35534 | -0.12013 | -0.01001 | -0.030779 | 0.32457 | 0.053054 | -0.10399 | 122.9572 | 122.8845 | 123.0405 | 66.7205 | -123.1012 | 122.8718 | 123.045 | 122.8879 | 66.7194 | -123.3473
903.7969 | 123.143 | -66.7191 | 56.3187 | 0.0018314 | -0.0086218 | 0.0010342 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00046581 | 0.059093 | 0.014429 | 0.059714 | -66.6923 | 0.015142 | -66.7185 | 56.2564 | 56.1883 | 56.3489 | -66.8192 | -66.7108 | 0.009516 | -66.7224 | 56.1573 | 56.3443 | 56.2009 | -67.0469 | -0.10014 | -0.062248 | 0.026727 | 0.00052 | 0.10066 | -0.13032 | 0.030225 | -0.32788 | -0.16133 | 0.0083 | -0.003312 | 0.32456 | 0.025588 | -0.11773 | 122.9755 | 122.9074 | 123.0679 | 66.7342 | -123.1379 | 122.8764 | 123.0633 | 122.92 | 66.7286 | -123.3656
904.7969 | 123.143 | -66.7465 | 56.3095 | 0.0018314 | -0.0086218 | 0.00082041 | 0.056011 | -0.0020533 | 0.061727 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058879 | 0.014216 | 0.0595 | -66.6969 | 0.015142 | -66.7231 | 56.2564 | 56.1929 | 56.3443 | -66.8238 | -66.7062 | 0.014095 | -66.7315 | 56.1665 | 56.3488 | 56.178 | -67.0469 | -0.077256 | -0.053092 | 0.049614 | 0.023408 | 0.10066 | -0.11659 | 0.034803 | -0.30041 | -0.14301 | 0.040345 | 0.014997 | 0.31541 | 0.039323 | -0.13146 | 123.0029 | 122.9394 | 123.0908 | 66.7617 | -123.1333 | 122.913 | 123.0954 | 122.9246 | 66.7606 | -123.3564
905.7969 | 123.1293 | -66.7099 | 56.3187 | -0.0057996 | -0.0081944 | 0.00060681 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00060453 | 0.00046581 | 0.058879 | 0.014857 | 0.059927 | -66.6877 | 0.019721 | -66.7231 | 56.261 | 56.1792 | 56.3397 | -66.8192 | -66.7062 | 0.018674 | -66.7224 | 56.1665 | 56.3443 | 56.178 | -67.0515 | -0.1093 | -0.05767 | 0.02215 | -0.013213 | 0.096085 | -0.13948 | 0.021068 | -0.34161 | -0.15217 | 0.003724 | -0.012467 | 0.32914 | 0.025588 | -0.14062 | 122.9709 | 122.8891 | 123.0496 | 66.7296 | -123.1379 | 122.8764 | 123.0542 | 122.8879 | 66.7286 | -123.3702
906.7969 | 123.1064 | -66.7145 | 56.3095 | -0.0057996 | -0.0086218 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | 0.0058755 | -0.00017733 | 0.00046581 | 0.058879 | 0.014429 | 0.0595 | -66.6877 | 0.019721 | -66.714 | 56.2564 | 56.1792 | 56.3489 | -66.8146 | -66.7108 | 0.023253 | -66.7269 | 56.1665 | 56.3488 | 56.1552 | -67.0469 | -0.10014 | -0.053092 | 0.026728 | 0.000521 | 0.10066 | -0.13032 | 0.039381 | -0.33245 | -0.14301 | 0.003723 | -0.012467 | 0.31999 | 0.039323 | -0.15436 | 122.9709 | 122.8937 | 123.0634 | 66.7342 | -123.1241 | 122.881 | 123.0633 | 122.8696 | 66.7377 | -123.3564
907.7969 | 123.2117 | -66.6962 | 56.2866 | 0.0018314 | -0.008408 | 0.00060681 | 0.056438 | -0.0026943 | 0.061727 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059307 | 0.014002 | 0.0595 | -66.6969 | 0.010564 | -66.714 | 56.2518 | 56.1746 | 56.3443 | -66.81 | -66.7016 | 0.018674 | -66.7315 | 56.1665 | 56.3443 | 56.1277 | -67.0515 | -0.11387 | -0.034782 | -0.00074 | -0.01779 | 0.096083 | -0.11202 | 0.057691 | -0.35534 | -0.12012 | -0.005431 | -0.035357 | 0.31999 | 0.057632 | -0.15894 | 122.948 | 122.8708 | 123.0405 | 66.7067 | -123.0967 | 122.8627 | 123.0404 | 122.8238 | 66.7148 | -123.3381
908.7969 | 123.1567 | -66.7053 | 56.3141 | -0.0057996 | -0.0088354 | 0.00060681 | 0.056438 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014643 | 0.0595 | -66.6923 | 0.015142 | -66.7094 | 56.261 | 56.1654 | 56.3443 | -66.8146 | -66.7062 | 0.018674 | -66.7315 | 56.1665 | 56.3488 | 56.178 | -67.0469 | -0.1093 | -0.053092 | 0.012994 | -0.004057 | 0.10524 | -0.14864 | 0.030225 | -0.34161 | -0.14759 | -0.000854 | -0.026202 | 0.31541 | 0.034745 | -0.13604 | 122.9663 | 122.8708 | 123.0496 | 66.7205 | -123.1287 | 122.8718 | 123.0542 | 122.8834 | 66.724 | -123.361
909.7969 | 123.1888 | -66.687 | 56.3324 | -0.0057996 | -0.008408 | 0.00060681 | 0.055797 | -0.0022669 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014643 | 0.0595 | -66.6877 | 0.019721 | -66.7185 | 56.261 | 56.1883 | 56.3489 | -66.81 | -66.7108 | 0.023253 | -66.7269 | 56.1711 | 56.3443 | 56.1872 | -67.0607 | -0.12303 | -0.071402 | -0.000738 | -0.031523 | 0.091505 | -0.14406 | 0.016493 | -0.37366 | -0.16132 | -0.023743 | -0.039933 | 0.33372 | 0.011856 | -0.14519 | 122.948 | 122.8754 | 123.0359 | 66.7067 | -123.1424 | 122.8581 | 123.0313 | 122.8742 | 66.7103 | -123.3931
910.7969 | 123.1293 | -66.7145 | 56.3187 | -0.0057996 | -0.009049 | 0.00082041 | 0.056011 | -0.0022669 | 0.061941 | 0.0058755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014643 | 0.0595 | -66.6969 | 0.019721 | -66.7185 | 56.2564 | 56.1883 | 56.3443 | -66.81 | -66.7062 | 0.023253 | -66.7315 | 56.1802 | 56.3534 | 56.1323 | -67.0469 | -0.095562 | -0.062248 | 0.017571 | -0.004057 | 0.091505 | -0.13032 | 0.025647 | -0.33245 | -0.13843 | 0.008302 | -0.017046 | 0.31541 | 0.034745 | -0.18641 | 122.9709 | 122.9028 | 123.0588 | 66.7342 | -123.1287 | 122.8947 | 123.0679 | 122.8467 | 66.7377 | -123.3656
911.7969 | 123.175 | -66.6962 | 56.3141 | -0.0057996 | -0.0086218 | 0.00060681 | 0.056011 | -0.0022669 | 0.061514 | 0.0058755 | -0.00060453 | 0.0011068 | 0.059093 | 0.014643 | 0.059714 | -66.6923 | 0.010564 | -66.7185 | 56.2564 | 56.1883 | 56.3489 | -66.81 | -66.7062 | 0.014095 | -66.7315 | 56.1619 | 56.3443 | 56.2101 | -67.0469 | -0.11387 | -0.05767 | 0.003839 | -0.022368 | 0.091505 | -0.12575 | 0.034803 | -0.35076 | -0.15217 | -0.010009 | -0.035357 | 0.31541 | 0.030166 | -0.10399 | 122.9526 | 122.8845 | 123.0451 | 66.7067 | -123.1241 | 122.8581 | 123.0404 | 122.9063 | 66.7103 | -123.361
912.7969 | 123.2346 | -66.6962 | 56.2454 | 0.0018314 | -0.0086218 | 0.00060681 | 0.055797 | -0.0022669 | 0.062155 | -0.001755 | -0.00060453 | 0.00067941 | 0.058879 | 0.014429 | 0.059714 | -66.6969 | 0.019721 | -66.7094 | 56.2518 | 56.1792 | 56.3397 | -66.81 | -66.7016 | 0.014095 | -66.7315 | 56.1757 | 56.3443 | 56.1643 | -67.0561 | -0.11387 | 0.006417 | -0.00074 | -0.013212 | 0.10066 | -0.066238 | 0.094311 | -0.35992 | -0.069769 | -0.005431 | -0.035357 | 0.32457 | 0.098831 | -0.081111 | 122.948 | 122.8754 | 123.0359 | 66.7159 | -123.0555 | 122.8718 | 123.0404 | 122.8605 | 66.7103 | -123.3015
913.7969 | 123.1979 | -66.6779 | 56.337 | 0.0094624 | -0.008408 | 0.00082041 | 0.056011 | -0.0022669 | 0.061941 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014643 | 0.059287 | -66.7015 | 0.019721 | -66.7185 | 56.2473 | 56.1929 | 56.3397 | -66.8238 | -66.7108 | 0.018674 | -66.7269 | 56.1711 | 56.3443 | 56.178 | -67.0561 | -0.14592 | -0.089715 | -0.023629 | -0.040679 | 0.10524 | -0.14405 | 0.002758 | -0.37823 | -0.1659 | -0.032899 | -0.049089 | 0.32914 | 0.007278 | -0.15893 | 122.9251 | 122.8708 | 123.0176 | 66.6976 | -123.1608 | 122.8489 | 123.0221 | 122.8559 | 66.6965 | -123.3931
914.7969 | 123.1155 | -66.7099 | 56.3187 | -0.013431 | -0.009049 | 0.00082041 | 0.056438 | -0.0022669 | 0.061727 | -0.0093855 | -0.00060453 | 0.0011068 | 0.058879 | 0.014429 | 0.059714 | -66.6969 | 0.010564 | -66.7185 | 56.2564 | 56.1883 | 56.3397 | -66.8192 | -66.7062 | 0.018674 | -66.7269 | 56.1619 | 56.3488 | 56.2009 | -67.0561 | -0.1093 | -0.062248 | 0.012993 | -0.008635 | 0.10066 | -0.13032 | 0.021068 | -0.34619 | -0.15675 | 0.003724 | -0.017045 | 0.32914 | 0.030167 | -0.11773 | 122.9663 | 122.8982 | 123.0496 | 66.7205 | -123.1379 | 122.8718 | 123.0587 | 122.9108 | 66.7286 | -123.3748
915.7969 | 123.1567 | -66.7236 | 56.3324 | 0.0018314 | -0.0088354 | 0.0010342 | 0.055583 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058879 | 0.014643 | 0.0595 | -66.7015 | 0.015142 | -66.714 | 56.2564 | 56.1792 | 56.3443 | -66.8055 | -66.7016 | 0.023253 | -66.7269 | 56.1711 | 56.3397 | 56.2147 | -67.0561 | -0.081828 | -0.07598 | 0.022148 | 0.009676 | 0.091504 | -0.15321 | 0.011915 | -0.33246 | -0.16132 | 0.022035 | -0.003312 | 0.32914 | 0.007278 | -0.11772 | 122.9801 | 122.9028 | 123.0679 | 66.7388 | -123.1379 | 122.8947 | 123.0633 | 122.9383 | 66.7469 | -123.3885
916.7969 | 123.1522 | -66.7145 | 56.3004 | 0.0018314 | -0.0086218 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058879 | 0.014216 | 0.059287 | -66.6923 | 0.010564 | -66.714 | 56.2656 | 56.1883 | 56.3443 | -66.8146 | -66.7108 | 0.027831 | -66.7315 | 56.1665 | 56.3443 | 56.1826 | -67.0515 | -0.10014 | -0.03478 | 0.02215 | 0.000521 | 0.10066 | -0.11201 | 0.043958 | -0.33703 | -0.13386 | 0.003723 | -0.017046 | 0.31999 | 0.043899 | -0.11773 | 122.9801 | 122.9028 | 123.0588 | 66.725 | -123.115 | 122.881 | 123.0587 | 122.8971 | 66.7423 | -123.3519
917.7969 | 123.1705 | -66.6962 | 56.3141 | 0.0018314 | -0.0086218 | 0.00060681 | 0.056011 | -0.0022669 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.059093 | 0.014857 | 0.059287 | -66.6923 | 0.0243 | -66.7277 | 56.2564 | 56.17 | 56.3489 | -66.8192 | -66.7108 | 0.018674 | -66.7315 | 56.1711 | 56.3534 | 56.1506 | -67.0469 | -0.12303 | -0.05767 | 0.003839 | -0.031525 | 0.091506 | -0.14406 | 0.034803 | -0.35076 | -0.14301 | -0.014588 | -0.035357 | 0.31541 | 0.039323 | -0.16351 | 122.9526 | 122.8662 | 123.0451 | 66.7205 | -123.1333 | 122.8672 | 123.0496 | 122.8467 | 66.7148 | -123.361
918.7969 | 123.1384 | -66.7099 | 56.3278 | 0.0018314 | -0.0086218 | 0.0010342 | 0.056224 | -0.0024807 | 0.062155 | -0.001755 | -0.00081813 | 0.00046581 | 0.059093 | 0.014216 | 0.059287 | -66.6923 | 0.010564 | -66.7231 | 56.261 | 56.1792 | 56.3443 | -66.8146 | -66.7062 | 0.023253 | -66.7269 | 56.1619 | 56.3534 | 56.1735 | -67.0515 | -0.10472 | -0.066825 | 0.017572 | -0.013213 | 0.091506 | -0.14864 | 0.016492 | -0.34161 | -0.1659 | 0.003724 | -0.017045 | 0.32456 | 0.02559 | -0.15435 | 122.9709 | 122.8891 | 123.0542 | 66.7205 | -123.1424 | 122.8718 | 123.0633 | 122.8834 | 66.7332 | -123.3793
919.7969 | 123.1567 | -66.6962 | 56.3187 | -0.0057996 | -0.0088354 | 0.00060681 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058879 | 0.014429 | 0.059287 | -66.6923 | 0.019721 | -66.7185 | 56.2564 | 56.1746 | 56.3489 | -66.81 | -66.7062 | 0.018674 | -66.7315 | 56.1619 | 56.3534 | 56.2238 | -67.0469 | -0.11387 | -0.062248 | 0.003839 | -0.022368 | 0.091505 | -0.14406 | 0.030225 | -0.35076 | -0.15675 | -0.010009 | -0.035357 | 0.31541 | 0.034745 | -0.094833 | 122.9526 | 122.8708 | 123.0451 | 66.7159 | -123.1287 | 122.8581 | 123.0496 | 122.92 | 66.7148 | -123.3656
920.7969 | 123.1338 | -66.7053 | 56.3049 | -0.0057996 | -0.008408 | 0.00060681 | 0.056438 | -0.0024807 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.014643 | 0.0595 | -66.6832 | 0.015142 | -66.7185 | 56.261 | 56.1792 | 56.3443 | -66.81 | -66.7016 | 0.023253 | -66.7315 | 56.1665 | 56.3534 | 56.1414 | -67.0561 | -0.10472 | -0.043937 | 0.02215 | -0.013213 | 0.091505 | -0.12575 | 0.03938 | -0.35077 | -0.13844 | 0.003724 | -0.026202 | 0.32457 | 0.048478 | -0.16351 | 122.9663 | 122.8845 | 123.0496 | 66.7205 | -123.115 | 122.8718 | 123.0587 | 122.8467 | 66.7286 | -123.361
921.7969 | 123.1613 | -66.7007 | 56.337 | 0.0018314 | -0.008408 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | -0.001755 | -0.00060453 | 0.0011068 | 0.059093 | 0.014643 | 0.0595 | -66.6877 | 0.019721 | -66.714 | 56.2564 | 56.1654 | 56.358 | -66.8146 | -66.7062 | 0.023253 | -66.7178 | 56.1711 | 56.3534 | 56.146 | -67.0515 | -0.11387 | -0.080558 | 0.012995 | -0.013212 | 0.10066 | -0.17153 | 0.021073 | -0.35076 | -0.1659 | -0.005431 | -0.017043 | 0.33372 | 0.016435 | -0.19098 | 122.9572 | 122.8662 | 123.0588 | 66.7205 | -123.1516 | 122.8718 | 123.0542 | 122.8467 | 66.724 | -123.3885
922.7969 | 123.1705 | -66.6916 | 56.3049 | 0.0018314 | -0.008408 | 0.0010342 | 0.056011 | -0.0022669 | 0.061941 | 0.0058755 | -0.00060453 | 0.00046581 | 0.059093 | 0.014643 | 0.0595 | -66.6969 | 0.0243 | -66.7185 | 56.261 | 56.1792 | 56.3535 | -66.81 | -66.7062 | 0.023253 | -66.7224 | 56.1711 | 56.3488 | 56.1552 | -67.0515 | -0.11845 | -0.043937 | -0.005318 | -0.026946 | 0.091505 | -0.12575 | 0.048537 | -0.35992 | -0.13386 | -0.014587 | -0.030778 | 0.32914 | 0.0439 | -0.14978 | 122.9526 | 122.8708 | 123.0451 | 66.7159 | -123.115 | 122.8627 | 123.0404 | 122.8467 | 66.7148 | -123.3564
923.7969 | 123.1796 | -66.6962 | 56.3278 | -0.0057996 | -0.0086218 | 0.00082041 | 0.055797 | -0.0022669 | 0.061941 | -0.001755 | -0.00060453 | 0.00067941 | 0.058879 | 0.014643 | 0.059714 | -66.6923 | 0.015142 | -66.7094 | 56.2518 | 56.1746 | 56.3489 | -66.81 | -66.7062 | 0.014095 | -66.7269 | 56.1665 | 56.3488 | 56.1048 | -67.0515 | -0.11387 | -0.075981 | 0.003839 | -0.013212 | 0.10066 | -0.15322 | 0.02107 | -0.35534 | -0.16132 | -0.010009 | -0.030778 | 0.32456 | 0.021012 | -0.22303 | 122.948 | 122.8708 | 123.0451 | 66.7113 | -123.1379 | 122.8627 | 123.045 | 122.801 | 66.7103 | -123.3793
924.7969 | 123.1384 | -66.6916 | 56.3187 | 0.0018314 | -0.0088354 | 0.00082041 | 0.056438 | -0.0024807 | 0.061727 | -0.001755 | -0.00060453 | 0.00089321 | 0.059307 | 0.014643 | 0.0595 | -66.7015 | 0.019721 | -66.714 | 56.2656 | 56.1654 | 56.3443 | -66.8146 | -66.7062 | 0.023253 | -66.7269 | 56.1619 | 56.358 | 56.1368 | -67.0515 | -0.12303 | -0.053091 | -0.009896 | -0.022368 | 0.10066 | -0.15322 | 0.025647 | -0.35992 | -0.15675 | -0.014587 | -0.035356 | 0.32456 | 0.039324 | -0.18183 | 122.9572 | 122.857 | 123.0359 | 66.7113 | -123.1333 | 122.8535 | 123.0496 | 122.8284 | 66.7148 | -123.3702
925.7969 | 123.1659 | -66.7099 | 56.3599 | -0.0057996 | -0.0088354 | 0.00082041 | 0.056011 | -0.0022669 | 0.061727 | -0.0093855 | -0.00060453 | 0.00089321 | 0.058879 | 0.014429 | 0.059714 | -66.6923 | 0.015142 | -66.7231 | 56.2656 | 56.17 | 56.3443 | -66.8146 | -66.7108 | 0.014095 | -66.7269 | 56.1711 | 56.3443 | 56.1094 | -67.0515 | -0.10472 | -0.094289 | 0.017572 | -0.013213 | 0.091506 | -0.18984 | -0.015551 | -0.34161 | -0.18879 | -0.000855 | -0.017045 | 0.32456 | -0.01561 | -0.2505 | 122.9755 | 122.8799 | 123.0542 | 66.725 | -123.1745 | 122.881 | 123.0542 | 122.8193 | 66.724 | -123.4114
926.7969 | 123.1705 | -66.6824 | 56.3141 | -0.013431 | -0.0092628 | 0.00082041 | 0.056438 | -0.0024807 | 0.061514 | -0.001755 | -0.00060453 | 0.00067941 | 0.058879 | 0.014429 | 0.0595 | -66.6969 | 0.019721 | -66.7185 | 56.261 | 56.1563 | 56.3489 | -66.81 | -66.7062 | 0.027831 | -66.7269 | 56.1711 | 56.358 | 56.1323 | -67.0424 | -0.12761 | -0.053092 | -0.014473 | -0.036101 | 0.091505 | -0.1578 | 0.034803 | -0.35992 | -0.14301 | -0.023742 | -0.044511 | 0.31541 | 0.043902 | -0.18183 | 122.9434 | 122.8387 | 123.0313 | 66.7022 | -123.1241 | 122.8535 | 123.0404 | 122.8147 | 66.7103 | -123.3564
927.7969 | 123.175 | -66.6824 | 56.3324 | 0.0018314 | -0.008408 | 0.00060681 | 0.056224 | -0.0022669 | 0.062155 | -0.001755 | -0.00060453 | 0.00046581 | 0.058666 | 0.014857 | 0.059927 | -66.6877 | 0.015142 | -66.714 | 56.2656 | 56.17 | 56.358 | -66.81 | -66.7062 | 0.03241 | -66.7269 | 56.1711 | 56.3488 | 56.146 | -67.0561 | -0.12761 | -0.066823 | -0.005316 | -0.031523 | 0.096083 | -0.16237 | 0.025651 | -0.37365 | -0.16132 | -0.023742 | -0.044511 | 0.32914 | 0.016435 | -0.1864 | 122.948 | 122.8525 | 123.0405 | 66.6976 | -123.1424 | 122.8535 | 123.0313 | 122.8284 | 66.7148 | -123.3885
928.7969 | 123.175 | -66.7099 | 56.3324 | -0.013431 | -0.009049 | 0.00082041 | 0.056224 | -0.0024807 | 0.062155 | 0.0058755 | -0.00081813 | 0.00067941 | 0.059093 | 0.014429 | 0.059287 | -66.6877 | 0.019721 | -66.7094 | 56.261 | 56.1792 | 56.3489 | -66.81 | -66.7062 | 0.023253 | -66.7269 | 56.1757 | 56.3488 | 56.1735 | -67.0515 | -0.10014 | -0.071402 | 0.02215 | 0.000521 | 0.10066 | -0.15321 | 0.016493 | -0.34161 | -0.15674 | 0.003724 | -0.017045 | 0.32456 | 0.016435 | -0.15893 | 122.9709 | 122.8891 | 123.0588 | 66.7296 | -123.1424 | 122.8856 | 123.0587 | 122.8834 | 66.7332 | -123.3839
929.7969 | 123.1201 | -66.7099 | 56.3278 | 0.0094624 | -0.0088354 | 0.00082041 | 0.056224 | -0.0029079 | 0.061727 | 0.0058755 | -0.00060453 | 0.0011068 | 0.058666 | 0.014857 | 0.059073 | -66.6877 | 0.005985 | -66.714 | 56.261 | 56.17 | 56.3443 | -66.81 | -66.7016 | 0.023253 | -66.7315 | 56.1711 | 56.3534 | 56.1368 | -67.0469 | -0.10014 | -0.066825 | 0.02215 | -0.004057 | 0.096083 | -0.15779 | 0.016492 | -0.33703 | -0.15675 | 0.008302 | -0.021624 | 0.31541 | 0.02559 | -0.19098 | 122.9709 | 122.8799 | 123.0542 | 66.7159 | -123.1379 | 122.881 | 123.0633 | 122.8467 | 66.7332 | -123.3748
930.7969 | 123.1796 | -66.6916 | 56.3278 | -0.0057996 | -0.0086218 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | -0.0093855 | -0.00017733 | 0.0011068 | 0.058666 | 0.014857 | 0.059287 | -66.6877 | 0.015142 | -66.7231 | 56.261 | 56.17 | 56.3535 | -66.8146 | -66.7016 | 0.027831 | -66.7269 | 56.1711 | 56.3534 | 56.1735 | -67.0469 | -0.12303 | -0.066825 | 0.003839 | -0.031524 | 0.091506 | -0.15779 | 0.025649 | -0.35534 | -0.15675 | -0.010009 | -0.035356 | 0.31999 | 0.02559 | -0.15435 | 122.9526 | 122.8616 | 123.0451 | 66.7067 | -123.1424 | 122.8627 | 123.045 | 122.8651 | 66.7194 | -123.3748
931.7969 | 123.1522 | -66.6962 | 56.3187 | 0.0018314 | -0.0088354 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | 0.013506 | -0.00060453 | 0.00046581 | 0.059093 | 0.014857 | 0.059714 | -66.6923 | 0.010564 | -66.7094 | 56.261 | 56.1838 | 56.3397 | -66.8146 | -66.7016 | 0.023253 | -66.7224 | 56.1711 | 56.358 | 56.1552 | -67.0424 | -0.11845 | -0.05767 | 0.003839 | -0.013212 | 0.10524 | -0.1349 | 0.021068 | -0.34619 | -0.14759 | -0.005431 | -0.0262 | 0.31999 | 0.039324 | -0.16351 | 122.9572 | 122.8799 | 123.0359 | 66.7067 | -123.1333 | 122.8672 | 123.0542 | 122.8513 | 66.7194 | -123.361
932.7969 | 123.1567 | -66.7191 | 56.3004 | -0.0057996 | -0.0086218 | 0.00039321 | 0.056011 | -0.0024807 | 0.061514 | 0.0058755 | -0.00081813 | 0.00089321 | 0.058879 | 0.014857 | 0.0595 | -66.6832 | 0.019721 | -66.714 | 56.2656 | 56.1654 | 56.3489 | -66.81 | -66.7062 | 0.018674 | -66.7269 | 56.1711 | 56.3534 | 56.1597 | -67.0469 | -0.090985 | -0.03478 | 0.035883 | 0.005098 | 0.096083 | -0.13491 | 0.048536 | -0.32788 | -0.12928 | 0.012879 | -0.00789 | 0.31999 | 0.053056 | -0.14062 | 122.9846 | 122.8845 | 123.0679 | 66.7388 | -123.1104 | 122.8901 | 123.0725 | 122.8788 | 66.7377 | -123.3473
933.7969 | 123.1888 | -66.6687 | 56.3278 | 0.0018314 | -0.009049 | 0.00082041 | 0.056224 | -0.0026943 | 0.061727 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058879 | 0.014857 | 0.0595 | -66.6923 | 0.010564 | -66.7231 | 56.2564 | 56.1746 | 56.3535 | -66.8192 | -66.7062 | 0.023253 | -66.7224 | 56.1757 | 56.3488 | 56.1139 | -67.0469 | -0.1505 | -0.071403 | -0.023627 | -0.054412 | 0.096085 | -0.15322 | 0.025649 | -0.37823 | -0.15217 | -0.037475 | -0.053666 | 0.32456 | 0.021012 | -0.21387 | 122.9251 | 122.8433 | 123.0222 | 66.6793 | -123.147 | 122.8444 | 123.0175 | 122.7826 | 66.692 | -123.3748
934.7969 | 123.1522 | -66.7007 | 56.3232 | 0.0018314 | -0.009049 | 0.00060681 | 0.056224 | -0.0020533 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.059093 | 0.014643 | 0.059287 | -66.6877 | 0.015142 | -66.7048 | 56.2702 | 56.17 | 56.3489 | -66.8146 | -66.7016 | 0.018674 | -66.7224 | 56.1757 | 56.358 | 56.1735 | -67.0469 | -0.11387 | -0.05309 | 0.012995 | -0.004055 | 0.10982 | -0.15322 | 0.025648 | -0.34619 | -0.14759 | -0.000853 | -0.021622 | 0.32456 | 0.034747 | -0.14977 | 122.9709 | 122.8708 | 123.0496 | 66.7159 | -123.1379 | 122.8764 | 123.0587 | 122.8742 | 66.7194 | -123.3702
935.7969 | 123.1201 | -66.7099 | 56.3324 | -0.0057996 | -0.009049 | 0.00082041 | 0.056652 | -0.0020533 | 0.0613 | 0.0058755 | -0.00039093 | 0.0011068 | 0.058879 | 0.014857 | 0.059287 | -66.6877 | 0.010564 | -66.7094 | 56.261 | 56.1746 | 56.3489 | -66.8055 | -66.697 | 0.018674 | -66.7178 | 56.1711 | 56.3534 | 56.1552 | -67.0424 | -0.095561 | -0.071402 | 0.02215 | 0.000521 | 0.096082 | -0.15779 | 0.016493 | -0.33245 | -0.16132 | 0.012881 | -0.007888 | 0.32457 | 0.021013 | -0.17724 | 122.9709 | 122.8845 | 123.0588 | 66.7205 | -123.1379 | 122.881 | 123.0633 | 122.8651 | 66.7286 | -123.3748
936.7969 | 123.1567 | -66.6916 | 56.3141 | -0.0057996 | -0.009049 | 0.00082041 | 0.056011 | -0.0022669 | 0.061727 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059093 | 0.014857 | 0.059287 | -66.6877 | 0.019721 | -66.7185 | 56.261 | 56.17 | 56.3443 | -66.81 | -66.7016 | 0.014095 | -66.7224 | 56.1711 | 56.3626 | 56.233 | -67.0424 | -0.11845 | -0.053092 | 0.003839 | -0.026946 | 0.091505 | -0.14406 | 0.030225 | -0.35076 | -0.14301 | -0.010009 | -0.030778 | 0.31999 | 0.048481 | -0.081097 | 122.9526 | 122.8616 | 123.0359 | 66.7113 | -123.1241 | 122.8627 | 123.0542 | 122.9246 | 66.7057 | -123.3564
937.7969 | 123.1338 | -66.7145 | 56.3461 | -0.0057996 | -0.0088354 | 0.00082041 | 0.056224 | -0.0024807 | 0.061727 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059093 | 0.014643 | 0.059287 | -66.6832 | 0.010564 | -66.714 | 56.2656 | 56.1883 | 56.3535 | -66.81 | -66.7016 | 0.018674 | -66.7224 | 56.1757 | 56.358 | 56.2147 | -67.0424 | -0.095562 | -0.080556 | 0.031306 | 0.000521 | 0.096083 | -0.15779 | 0.007339 | -0.32788 | -0.17048 | 0.01288 | -0.007889 | 0.31999 | 0.011859 | -0.13146 | 122.9801 | 122.9028 | 123.0679 | 66.725 | -123.1562 | 122.8901 | 123.0725 | 122.9292 | 66.7332 | -123.3885
938.7969 | 123.175 | -66.6962 | 56.3049 | -0.0057996 | -0.0086218 | 0.0010342 | 0.056224 | -0.0020533 | 0.061514 | 0.0058755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014857 | 0.059287 | -66.6877 | 0.019721 | -66.714 | 56.2656 | 56.1838 | 56.3535 | -66.8055 | -66.6924 | 0.018674 | -66.7178 | 56.1757 | 56.358 | 56.1414 | -67.0469 | -0.10929 | -0.039358 | 0.008417 | -0.01779 | 0.091504 | -0.12117 | 0.048537 | -0.35076 | -0.12928 | 0.003727 | -0.021621 | 0.32914 | 0.053057 | -0.16351 | 122.9617 | 122.8799 | 123.0496 | 66.7159 | -123.1104 | 122.8718 | 123.0542 | 122.8376 | 66.7148 | -123.3519
939.7969 | 123.1247 | -66.6824 | 56.337 | -0.013431 | -0.0088354 | 0.00082041 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00017733 | 0.00067941 | 0.058666 | 0.014857 | 0.059287 | -66.674 | 0.010564 | -66.7094 | 56.261 | 56.1883 | 56.358 | -66.8009 | -66.6924 | 0.023253 | -66.7178 | 56.1757 | 56.358 | 56.2284 | -67.0424 | -0.11845 | -0.07598 | 0.008419 | -0.026945 | 0.091503 | -0.14863 | 0.021073 | -0.35992 | -0.16132 | -0.010006 | -0.035354 | 0.32457 | 0.021014 | -0.10856 | 122.9434 | 122.8708 | 123.0405 | 66.693 | -123.1379 | 122.8581 | 123.0404 | 122.9108 | 66.7057 | -123.3793
940.7969 | 123.1796 | -66.6824 | 56.3141 | -0.0057996 | -0.009049 | 0.00082041 | 0.056224 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014643 | 0.0595 | -66.6786 | 0.015142 | -66.7094 | 56.2702 | 56.1838 | 56.3489 | -66.8055 | -66.6879 | 0.018674 | -66.7178 | 56.1802 | 56.358 | 56.1918 | -67.0378 | -0.12303 | -0.043935 | 0.003841 | -0.026945 | 0.096082 | -0.13032 | 0.034803 | -0.35534 | -0.13386 | -0.005427 | -0.035354 | 0.31999 | 0.043902 | -0.1223 | 122.9526 | 122.8662 | 123.0313 | 66.6976 | -123.1195 | 122.8627 | 123.0404 | 122.8742 | 66.7011 | -123.3519
941.7969 | 123.1476 | -66.687 | 56.3553 | 0.0018314 | -0.009049 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.014857 | 0.0595 | -66.6877 | 0.015142 | -66.7048 | 56.2656 | 56.2021 | 56.3535 | -66.81 | -66.6879 | 0.014095 | -66.7178 | 56.1757 | 56.3717 | 56.2238 | -67.0469 | -0.12303 | -0.089712 | -0.000738 | -0.017788 | 0.10524 | -0.15321 | -0.001817 | -0.35992 | -0.17963 | -0.000849 | -0.030776 | 0.32914 | 0.016439 | -0.13145 | 122.9526 | 122.8891 | 123.0405 | 66.7022 | -123.1653 | 122.8627 | 123.0587 | 122.9108 | 66.7011 | -123.4022
942.7969 | 123.175 | -66.6916 | 56.3278 | 0.0094624 | -0.009049 | 0.00082041 | 0.056011 | -0.0022669 | 0.061727 | -0.001755 | -0.00039093 | 0.00046581 | 0.059093 | 0.014643 | 0.0595 | -66.6786 | 0.0243 | -66.714 | 56.2702 | 56.1929 | 56.358 | -66.8146 | -66.6924 | 0.014095 | -66.7086 | 56.1757 | 56.358 | 56.2055 | -67.0378 | -0.12303 | -0.057668 | 0.012996 | -0.022368 | 0.10066 | -0.1349 | 0.030228 | -0.34619 | -0.15217 | -0.000851 | -0.017041 | 0.32914 | 0.030169 | -0.1223 | 122.9617 | 122.8845 | 123.0496 | 66.7159 | -123.1424 | 122.8672 | 123.0496 | 122.8971 | 66.7057 | -123.3656
943.7969 | 123.1613 | -66.7007 | 56.3416 | 0.0094624 | -0.009049 | 0.00082041 | 0.056438 | -0.0022669 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059093 | 0.01507 | 0.0595 | -66.6832 | 0.015142 | -66.7094 | 56.2656 | 56.1929 | 56.358 | -66.8055 | -66.6879 | 0.014095 | -66.7132 | 56.1802 | 56.3534 | 56.2284 | -67.0424 | -0.10472 | -0.075979 | 0.017573 | -0.008634 | 0.096082 | -0.14863 | 0.016495 | -0.34161 | -0.16132 | 0.012884 | -0.012464 | 0.32914 | 0.011857 | -0.11314 | 122.9663 | 122.8937 | 123.0588 | 66.7159 | -123.147 | 122.881 | 123.0542 | 122.9292 | 66.7148 | -123.3839
944.7969 | 123.1796 | -66.687 | 56.3416 | 0.0094624 | -0.009049 | 0.00060681 | 0.056011 | -0.0022669 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014857 | 0.0595 | -66.6786 | 0.019721 | -66.7094 | 56.261 | 56.1838 | 56.358 | -66.8009 | -66.6879 | 0.014095 | -66.7178 | 56.1848 | 56.3626 | 56.2101 | -67.0424 | -0.11387 | -0.080558 | 0.008419 | -0.022367 | 0.091503 | -0.15779 | 0.016495 | -0.35534 | -0.15674 | -0.000849 | -0.030776 | 0.32457 | 0.021015 | -0.13146 | 122.948 | 122.8708 | 123.0451 | 66.7067 | -123.1424 | 122.8718 | 123.0496 | 122.8971 | 66.7011 | -123.3839
945.7969 | 123.143 | -66.7007 | 56.3553 | -0.0057996 | -0.009049 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059307 | 0.014643 | 0.059287 | -66.6786 | 0.010564 | -66.7094 | 56.261 | 56.2067 | 56.3535 | -66.8055 | -66.6833 | 0.009516 | -66.7132 | 56.1802 | 56.358 | 56.2376 | -67.0378 | -0.10472 | -0.094291 | 0.022152 | -0.008634 | 0.096082 | -0.14863 | -0.001817 | -0.33703 | -0.17506 | 0.017462 | -0.012464 | 0.32456 | 0.002703 | -0.11772 | 122.9617 | 122.9074 | 123.0542 | 66.7113 | -123.1607 | 122.881 | 123.0587 | 122.9383 | 66.7103 | -123.3931
946.7969 | 123.1567 | -66.6916 | 56.3187 | 0.0018314 | -0.0088354 | 0.00060681 | 0.056011 | -0.0024807 | 0.061941 | 0.013506 | -0.00039093 | 0.00089321 | 0.058879 | 0.014857 | 0.0595 | -66.674 | 0.019721 | -66.7002 | 56.2702 | 56.2021 | 56.3535 | -66.8055 | -66.6879 | 0.000359 | -66.7041 | 56.1757 | 56.3671 | 56.2055 | -67.0424 | -0.11387 | -0.048513 | 0.017574 | -0.008633 | 0.10524 | -0.11659 | 0.034804 | -0.35076 | -0.14301 | 0.003728 | -0.012463 | 0.3383 | 0.048481 | -0.11315 | 122.9617 | 122.8937 | 123.0451 | 66.7113 | -123.1241 | 122.8672 | 123.0587 | 122.8971 | 66.6919 | -123.361
947.7969 | 123.1796 | -66.6824 | 56.3324 | 0.0018314 | -0.0088354 | 0.0010342 | 0.056011 | -0.0026943 | 0.061941 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058879 | 0.01507 | 0.0595 | -66.6694 | 0.010564 | -66.7048 | 56.2702 | 56.2021 | 56.3626 | -66.8009 | -66.6879 | 0.004938 | -66.7041 | 56.1802 | 56.3626 | 56.2009 | -67.0332 | -0.11845 | -0.062245 | 0.012998 | -0.022366 | 0.096082 | -0.13032 | 0.030229 | -0.35076 | -0.15217 | -0.005427 | -0.021618 | 0.32914 | 0.030171 | -0.13146 | 122.9526 | 122.8845 | 123.0451 | 66.693 | -123.1333 | 122.8627 | 123.045 | 122.8834 | 66.6874 | -123.3656
948.7969 | 123.1613 | -66.6962 | 56.3324 | -0.0057996 | -0.009049 | 0.00060681 | 0.055797 | -0.0024807 | 0.061941 | 0.0058755 | -0.00039093 | 0.00089321 | 0.059307 | 0.01507 | 0.0595 | -66.6786 | 0.019721 | -66.714 | 56.2702 | 56.2021 | 56.3672 | -66.81 | -66.6787 | -0.00422 | -66.7132 | 56.1848 | 56.3626 | 56.2193 | -67.0378 | -0.11387 | -0.062245 | 0.017574 | -0.01779 | 0.096083 | -0.13032 | 0.034808 | -0.34161 | -0.14759 | 0.017463 | -0.017042 | 0.32456 | 0.030171 | -0.11314 | 122.9663 | 122.8982 | 123.0634 | 66.7159 | -123.1424 | 122.881 | 123.0587 | 122.9154 | 66.6919 | -123.3702
949.7969 | 123.143 | -66.6962 | 56.3644 | -0.0057996 | -0.009049 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | -0.001755 | -0.00060453 | 0.00089321 | 0.058666 | 0.01507 | 0.059287 | -66.6832 | 0.010564 | -66.7094 | 56.2702 | 56.2021 | 56.358 | -66.7963 | -66.6879 | -0.00422 | -66.7132 | 56.1848 | 56.3626 | 56.2376 | -67.0378 | -0.10014 | -0.094289 | 0.012995 | -0.013212 | 0.086925 | -0.16236 | -0.006393 | -0.34161 | -0.17963 | 0.008306 | -0.017042 | 0.32456 | -0.001873 | -0.12687 | 122.9663 | 122.8982 | 123.0542 | 66.7067 | -123.1607 | 122.881 | 123.0587 | 122.9337 | 66.6919 | -123.4022
950.7969 | 123.1979 | -66.6779 | 56.3599 | -0.0057996 | -0.009049 | 0.0010342 | 0.056224 | -0.0022669 | 0.061727 | 0.0058755 | -0.00017733 | 0.00089321 | 0.058879 | 0.014857 | 0.058646 | -66.6786 | 0.015142 | -66.714 | 56.2702 | 56.2021 | 56.3672 | -66.8055 | -66.6879 | -0.00422 | -66.7132 | 56.1848 | 56.3717 | 56.2284 | -67.0378 | -0.1276 | -0.089711 | -0.000737 | -0.036101 | 0.091504 | -0.15778 | 0.007342 | -0.35992 | -0.17505 | -0.010005 | -0.035353 | 0.32456 | 0.011862 | -0.13145 | 122.948 | 122.8799 | 123.0451 | 66.693 | -123.1653 | 122.8627 | 123.0496 | 122.9063 | 66.6736 | -123.3976
951.7969 | 123.1613 | -66.6733 | 56.3416 | 0.0094624 | -0.0088354 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | 0.013506 | -0.0010319 | 0.00067941 | 0.058879 | 0.014857 | 0.059287 | -66.6786 | 0.019721 | -66.7002 | 56.2747 | 56.2067 | 56.3626 | -66.7963 | -66.6879 | -0.013377 | -66.7132 | 56.1757 | 56.3671 | 56.2376 | -67.0378 | -0.12303 | -0.066822 | -0.005314 | -0.026943 | 0.096082 | -0.1349 | 0.021073 | -0.3645 | -0.1659 | -0.014582 | -0.03993 | 0.32456 | 0.025593 | -0.10398 | 122.948 | 122.8799 | 123.0359 | 66.693 | -123.1379 | 122.8489 | 123.0404 | 122.9108 | 66.6599 | -123.3793
952.7969 | 123.1659 | -66.6733 | 56.337 | -0.0057996 | -0.009049 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | 0.0058755 | -0.00060453 | 0.00067941 | 0.058879 | 0.01507 | 0.059287 | -66.6786 | 0.015142 | -66.7048 | 56.2793 | 56.1975 | 56.3626 | -66.8055 | -66.6833 | -0.022535 | -66.7086 | 56.1848 | 56.3671 | 56.2467 | -67.0378 | -0.13218 | -0.057666 | -0.005314 | -0.031521 | 0.10066 | -0.13948 | 0.025651 | -0.3645 | -0.15217 | -0.010004 | -0.035351 | 0.32914 | 0.030171 | -0.09025 | 122.9526 | 122.8708 | 123.0359 | 66.6884 | -123.1424 | 122.8581 | 123.0404 | 122.92 | 66.6507 | -123.3747
953.7969 | 123.1567 | -66.6733 | 56.3553 | -0.013431 | -0.009049 | 0.00039321 | 0.056224 | -0.0022669 | 0.062155 | -0.001755 | -0.00039093 | 0.0011068 | 0.059093 | 0.014857 | 0.059287 | -66.6786 | 0.019721 | -66.7048 | 56.2747 | 56.2021 | 56.358 | -66.8055 | -66.6741 | -0.017956 | -66.7178 | 56.1848 | 56.3671 | 56.2238 | -67.0378 | -0.13218 | -0.080555 | -0.005314 | -0.031521 | 0.10066 | -0.15321 | 0.002762 | -0.3645 | -0.17048 | -0.000846 | -0.044509 | 0.31999 | 0.01186 | -0.13145 | 122.948 | 122.8754 | 123.0313 | 66.693 | -123.1607 | 122.8581 | 123.0404 | 122.8971 | 66.6553 | -123.3931
954.7969 | 123.111 | -66.7191 | 56.337 | 0.0094624 | -0.0088354 | 0.00082041 | 0.056011 | -0.0024807 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015284 | 0.058859 | -66.674 | 0.015142 | -66.7048 | 56.2702 | 56.2067 | 56.3672 | -66.81 | -66.6833 | -0.036271 | -66.7178 | 56.1894 | 56.3671 | 56.233 | -67.0469 | -0.090985 | -0.066823 | 0.04504 | 0.014255 | 0.10524 | -0.13032 | 0.03023 | -0.32788 | -0.14759 | 0.035772 | 0.001267 | 0.32914 | 0.030171 | -0.10399 | 122.9892 | 122.9257 | 123.0863 | 66.7342 | -123.147 | 122.9084 | 123.0862 | 122.952 | 66.6828 | -123.3839
955.7969 | 123.1842 | -66.6824 | 56.3461 | -0.0057996 | -0.0092628 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.0093855 | -0.00060453 | 0.00089321 | 0.059093 | 0.01507 | 0.059287 | -66.674 | 0.019721 | -66.7048 | 56.2793 | 56.2021 | 56.358 | -66.8055 | -66.6879 | -0.036271 | -66.7041 | 56.1848 | 56.3671 | 56.233 | -67.0378 | -0.12303 | -0.066821 | 0.008419 | -0.022366 | 0.10066 | -0.14405 | 0.011918 | -0.35534 | -0.16132 | -0.005427 | -0.021618 | 0.33372 | 0.021016 | -0.11314 | 122.9617 | 122.8845 | 123.0405 | 66.7022 | -123.1516 | 122.8672 | 123.0496 | 122.9154 | 66.6462 | -123.3839
956.7969 | 123.1705 | -66.6779 | 56.337 | 0.0018314 | -0.009049 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.059093 | 0.014857 | 0.059287 | -66.674 | 0.019721 | -66.7094 | 56.2793 | 56.2067 | 56.3626 | -66.8055 | -66.6879 | -0.040849 | -66.7041 | 56.1848 | 56.3671 | 56.2238 | -67.0378 | -0.1276 | -0.057666 | 0.003841 | -0.031523 | 0.096082 | -0.13032 | 0.025651 | -0.35992 | -0.15217 | -0.010005 | -0.026196 | 0.33372 | 0.030171 | -0.11314 | 122.9572 | 122.8845 | 123.0405 | 66.6976 | -123.1424 | 122.8627 | 123.045 | 122.9017 | 66.637 | -123.3747
957.7969 | 123.1293 | -66.6779 | 56.3599 | 0.0018314 | -0.0088354 | 0.0010342 | 0.056011 | -0.0024807 | 0.061941 | 0.0058755 | -0.00060453 | 0.00067941 | 0.059093 | 0.014857 | 0.059287 | -66.6694 | 0.0243 | -66.7048 | 56.2656 | 56.2021 | 56.3535 | -66.8055 | -66.6787 | -0.054586 | -66.7086 | 56.1848 | 56.3671 | 56.2147 | -67.0378 | -0.1276 | -0.094289 | 0.00842 | -0.026944 | 0.10066 | -0.15778 | -0.006394 | -0.35992 | -0.17505 | -0.000848 | -0.030774 | 0.32914 | 0.007283 | -0.14519 | 122.9434 | 122.8799 | 123.0313 | 66.7022 | -123.1653 | 122.8627 | 123.045 | 122.8925 | 66.6233 | -123.3976
958.7969 | 123.1247 | -66.6733 | 56.3187 | -0.0057996 | -0.009049 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00060453 | 0.00067941 | 0.058879 | 0.014857 | 0.059287 | -66.674 | 0.015142 | -66.7048 | 56.2747 | 56.1975 | 56.3626 | -66.7963 | -66.6787 | -0.068322 | -66.7086 | 56.1894 | 56.3626 | 56.2421 | -67.0378 | -0.12303 | -0.043934 | -0.000736 | -0.031521 | 0.091504 | -0.12117 | 0.043961 | -0.3645 | -0.12928 | -0.005425 | -0.035351 | 0.32914 | 0.043903 | -0.076518 | 122.948 | 122.8708 | 123.0359 | 66.6884 | -123.115 | 122.8627 | 123.0358 | 122.9154 | 66.605 | -123.3564
959.7969 | 123.1522 | -66.6687 | 56.3232 | 0.0018314 | -0.0094764 | 0.00082041 | 0.055797 | -0.0026943 | 0.061514 | 0.013506 | -0.00017733 | 0.00046581 | 0.058879 | 0.01507 | 0.0595 | -66.6694 | 0.010564 | -66.7048 | 56.2793 | 56.2021 | 56.3626 | -66.8009 | -66.6787 | -0.077479 | -66.6995 | 56.1848 | 56.3671 | 56.2376 | -67.0378 | -0.13218 | -0.043933 | -0.000735 | -0.036099 | 0.096082 | -0.12116 | 0.039384 | -0.36907 | -0.13843 | -0.010003 | -0.030772 | 0.3383 | 0.043904 | -0.085674 | 122.948 | 122.8708 | 123.0313 | 66.6793 | -123.1241 | 122.8535 | 123.0358 | 122.9063 | 66.5912 | -123.361
960.7969 | 123.1293 | -66.6733 | 56.3416 | -0.0057996 | -0.0092628 | 0.00082041 | 0.056011 | -0.0024807 | 0.062368 | -0.001755 | -0.00060453 | 0.00067941 | 0.058879 | 0.01507 | 0.059287 | -66.6694 | 0.019721 | -66.7002 | 56.2793 | 56.1975 | 56.3626 | -66.8055 | -66.6695 | -0.077479 | -66.7041 | 56.1757 | 56.3626 | 56.2101 | -67.0378 | -0.13218 | -0.062244 | 0.003843 | -0.026943 | 0.10524 | -0.14405 | 0.021073 | -0.3645 | -0.1659 | 0.003732 | -0.030773 | 0.33372 | 0.021015 | -0.13146 | 122.9526 | 122.8708 | 123.0359 | 66.693 | -123.147 | 122.8489 | 123.0358 | 122.8834 | 66.5958 | -123.3793
961.7969 | 123.143 | -66.6779 | 56.3416 | -0.0057996 | -0.0092628 | 0.00060681 | 0.056011 | -0.0024807 | 0.061941 | -0.001755 | -0.00060453 | 0.00089321 | 0.059093 | 0.014857 | 0.059287 | -66.674 | 0.019721 | -66.7048 | 56.2747 | 56.1929 | 56.358 | -66.8009 | -66.6833 | -0.10037 | -66.7041 | 56.1848 | 56.3671 | 56.2284 | -67.0332 | -0.12303 | -0.066822 | 0.003841 | -0.026944 | 0.096082 | -0.14863 | 0.016495 | -0.35534 | -0.15674 | -0.005427 | -0.026196 | 0.32914 | 0.025593 | -0.11314 | 122.9526 | 122.8708 | 123.0359 | 66.6976 | -123.1424 | 122.8627 | 123.045 | 122.9063 | 66.5775 | -123.3747
962.7969 | 123.0972 | -66.7145 | 56.3416 | 0.0018314 | -0.009049 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | -0.00060453 | 0.00089321 | 0.058879 | 0.01507 | 0.059287 | -66.674 | 0.028878 | -66.6956 | 56.2793 | 56.1975 | 56.3626 | -66.8055 | -66.6787 | -0.10953 | -66.7041 | 56.1848 | 56.3671 | 56.2284 | -67.024 | -0.090983 | -0.062244 | 0.040463 | 0.018834 | 0.10982 | -0.14405 | 0.021073 | -0.30956 | -0.15674 | 0.035774 | 0.010426 | 0.31999 | 0.025593 | -0.11314 | 122.9938 | 122.912 | 123.0771 | 66.7434 | -123.147 | 122.8993 | 123.0816 | 122.9429 | 66.6049 | -123.3656
963.7969 | 123.175 | -66.6962 | 56.3278 | 0.0018314 | -0.0092628 | 0.00082041 | 0.056011 | -0.0029079 | 0.061941 | 0.0058755 | -0.00017733 | 0.00046581 | 0.058666 | 0.01507 | 0.059287 | -66.674 | 0.028878 | -66.7048 | 56.2793 | 56.2021 | 56.3626 | -66.8009 | -66.6787 | -0.12327 | -66.7086 | 56.1848 | 56.3626 | 56.2284 | -67.0332 | -0.10471 | -0.048511 | 0.022152 | -0.008633 | 0.096082 | -0.12574 | 0.034806 | -0.33703 | -0.14301 | 0.017463 | -0.012463 | 0.32457 | 0.034748 | -0.099409 | 122.9755 | 122.8982 | 123.0588 | 66.725 | -123.1287 | 122.881 | 123.0587 | 122.9246 | 66.5729 | -123.361
964.7969 | 123.1338 | -66.7099 | 56.3095 | 0.0018314 | -0.009049 | 0.00039321 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00081813 | 0.00067941 | 0.058879 | 0.01507 | 0.059073 | -66.674 | 0.019721 | -66.6956 | 56.2793 | 56.1838 | 56.3672 | -66.81 | -66.6787 | -0.15074 | -66.7041 | 56.1848 | 56.3717 | 56.233 | -67.0378 | -0.10014 | -0.0302 | 0.035885 | 0.014256 | 0.1144 | -0.12575 | 0.057696 | -0.32787 | -0.1247 | 0.031196 | 0.005848 | 0.33372 | 0.062216 | -0.076519 | 122.9892 | 122.8937 | 123.0771 | 66.7296 | -123.1195 | 122.8947 | 123.0816 | 122.9429 | 66.5592 | -123.3473
965.7969 | 123.1705 | -66.687 | 56.2912 | -0.0057996 | -0.0092628 | 0.00039321 | 0.056224 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.00025221 | 0.058879 | 0.015284 | 0.059073 | -66.6694 | 0.028878 | -66.7002 | 56.2839 | 56.2021 | 56.3672 | -66.8055 | -66.6833 | -0.17363 | -66.6949 | 56.1894 | 56.3626 | 56.146 | -67.0378 | -0.11845 | -0.007312 | 0.017576 | -0.01321 | 0.10524 | -0.08912 | 0.076006 | -0.35076 | -0.10181 | 0.003729 | -0.007882 | 0.34288 | 0.071369 | -0.1452 | 122.9709 | 122.8891 | 123.0542 | 66.7159 | -123.0967 | 122.8764 | 123.0496 | 122.833 | 66.5134 | -123.329
966.7969 | 123.1293 | -66.7099 | 56.3278 | -0.0057996 | -0.009049 | 0.00039321 | 0.056011 | -0.0026943 | 0.061514 | 0.0058755 | -0.00060453 | 0.00089321 | 0.058452 | 0.014857 | 0.0595 | -66.674 | 0.028878 | -66.7002 | 56.2702 | 56.2021 | 56.3626 | -66.8009 | -66.6695 | -0.18737 | -66.7041 | 56.1848 | 56.3626 | 56.1964 | -67.0378 | -0.090982 | -0.057668 | 0.035885 | 0.009678 | 0.10066 | -0.12574 | 0.034806 | -0.32787 | -0.14301 | 0.040353 | 0.005848 | 0.33372 | 0.034748 | -0.13146 | 122.9801 | 122.912 | 123.0725 | 66.7388 | -123.1287 | 122.8947 | 123.0725 | 122.9063 | 66.5225 | -123.3656
967.7969 | 123.143 | -66.687 | 56.3324 | -0.0057996 | -0.0094764 | 0.00039321 | 0.056011 | -0.0031215 | 0.061941 | -0.001755 | -0.00081813 | 0.00067941 | 0.059093 | 0.01507 | 0.059287 | -66.6694 | 0.0243 | -66.7002 | 56.2839 | 56.1883 | 56.3764 | -66.8055 | -66.6695 | -0.21026 | -66.7086 | 56.1894 | 56.3671 | 56.2284 | -67.0378 | -0.11845 | -0.04851 | 0.017576 | -0.01321 | 0.10524 | -0.14406 | 0.043965 | -0.35076 | -0.14301 | 0.017465 | -0.021618 | 0.32914 | 0.034749 | -0.10399 | 122.9709 | 122.8754 | 123.0634 | 66.7113 | -123.1379 | 122.8764 | 123.0542 | 122.9154 | 66.4767 | -123.3702
968.7969 | 123.143 | -66.7053 | 56.3232 | -0.013431 | -0.009049 | 0.00082041 | 0.055797 | -0.0026943 | 0.061514 | -0.0093855 | -0.00060453 | 0.00067941 | 0.058666 | 0.01507 | 0.059287 | -66.6694 | 0.019721 | -66.6956 | 56.2747 | 56.1746 | 56.358 | -66.7917 | -66.6741 | -0.23773 | -66.6995 | 56.1894 | 56.3717 | 56.1964 | -67.0424 | -0.086403 | -0.048511 | 0.035886 | 0.009678 | 0.096081 | -0.14864 | 0.034806 | -0.33703 | -0.13385 | 0.031197 | 0.005849 | 0.34288 | 0.048483 | -0.12688 | 122.9801 | 122.8799 | 123.0634 | 66.725 | -123.115 | 122.8947 | 123.077 | 122.9017 | 66.4676 | -123.3656
969.7969 | 123.1201 | -66.7191 | 56.3461 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058666 | 0.015284 | 0.059073 | -66.674 | 0.028878 | -66.7002 | 56.2747 | 56.1929 | 56.358 | -66.81 | -66.6741 | -0.26978 | -66.7041 | 56.1757 | 56.3671 | 56.1826 | -67.0332 | -0.090985 | -0.071399 | 0.04504 | 0.018833 | 0.10982 | -0.15321 | 0.011918 | -0.31414 | -0.17048 | 0.04493 | 0.015003 | 0.32914 | 0.021016 | -0.16351 | 122.9938 | 122.912 | 123.0771 | 66.7479 | -123.1562 | 122.8947 | 123.0862 | 122.9017 | 66.4493 | -123.3793
970.7969 | 123.111 | -66.6824 | 56.3187 | -0.013431 | -0.009049 | 0.0010342 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | -0.00039093 | 0.00067941 | 0.058879 | 0.015284 | 0.059287 | -66.6786 | 0.019721 | -66.7002 | 56.2702 | 56.1838 | 56.3764 | -66.7963 | -66.6695 | -0.29726 | -66.7086 | 56.1802 | 56.3671 | 56.0956 | -67.0378 | -0.11387 | -0.048513 | 0.003841 | -0.017788 | 0.096082 | -0.1349 | 0.057697 | -0.35534 | -0.13843 | 0.012887 | -0.026196 | 0.32914 | 0.048481 | -0.22303 | 122.9526 | 122.8662 | 123.0588 | 66.7022 | -123.115 | 122.8627 | 123.0496 | 122.7781 | 66.3852 | -123.3564
971.7969 | 123.1659 | -66.6916 | 56.3049 | 0.0018314 | -0.009049 | 0.00039321 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | -0.00060453 | 0.0011068 | 0.058666 | 0.015498 | 0.059073 | -66.6694 | 0.0243 | -66.7094 | 56.2702 | 56.1792 | 56.3672 | -66.8009 | -66.6741 | -0.33847 | -66.6995 | 56.1894 | 56.3671 | 56.1506 | -67.0378 | -0.10929 | -0.03478 | 0.022153 | -0.01779 | 0.091503 | -0.12575 | 0.062273 | -0.34619 | -0.11554 | 0.017464 | -0.007884 | 0.3383 | 0.062214 | -0.15436 | 122.9617 | 122.8708 | 123.0588 | 66.7159 | -123.1058 | 122.881 | 123.0587 | 122.8422 | 66.3531 | -123.3427
972.7969 | 123.2254 | -66.6779 | 56.2408 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | -0.001755 | -0.00060453 | 0.0011068 | 0.058879 | 0.015284 | 0.059073 | -66.6649 | 0.015142 | -66.7048 | 56.2747 | 56.1654 | 56.3626 | -66.8009 | -66.665 | -0.36594 | -66.7041 | 56.1894 | 56.3671 | 56.1597 | -67.0378 | -0.12303 | 0.033886 | 0.012998 | -0.026944 | 0.096082 | -0.075398 | 0.12178 | -0.35992 | -0.051457 | 0.012888 | -0.026196 | 0.33372 | 0.1263 | -0.081113 | 122.9526 | 122.8433 | 123.0405 | 66.693 | -123.0417 | 122.8672 | 123.045 | 122.8376 | 66.3119 | -123.2786
973.7969 | 123.1293 | -66.7191 | 56.3278 | 0.0018314 | -0.0092628 | 0.00082041 | 0.056438 | -0.0026943 | 0.061514 | -0.001755 | -0.00081813 | 0.00089321 | 0.058666 | 0.015284 | 0.059073 | -66.6649 | 0.028878 | -66.7048 | 56.2793 | 56.1792 | 56.3626 | -66.8055 | -66.6604 | -0.40257 | -66.6995 | 56.1802 | 56.3671 | 56.1689 | -67.0332 | -0.086406 | -0.048511 | 0.054197 | 0.014255 | 0.10066 | -0.14864 | 0.034806 | -0.31414 | -0.14759 | 0.058666 | 0.019582 | 0.33372 | 0.039326 | -0.15893 | 122.9984 | 122.8982 | 123.0817 | 66.7479 | -123.1333 | 122.8993 | 123.0862 | 122.8879 | 66.3165 | -123.361
974.7969 | 123.2574 | -66.6595 | 56.2866 | -0.013431 | -0.0092628 | 0.00060681 | 0.056652 | -0.0026943 | 0.061086 | 0.0058755 | -0.00060453 | 0.00046581 | 0.058666 | 0.01507 | 0.059287 | -66.6649 | 0.0243 | -66.7002 | 56.2702 | 56.17 | 56.358 | -66.7963 | -66.6558 | -0.4392 | -66.6995 | 56.1848 | 56.3671 | 56.178 | -67.0378 | -0.13676 | -0.016469 | -0.005312 | -0.040676 | 0.096082 | -0.11659 | 0.071427 | -0.37823 | -0.10181 | 0.003736 | -0.039927 | 0.3383 | 0.080525 | -0.10857 | 122.9297 | 122.8296 | 123.0176 | 66.6838 | -123.0829 | 122.8444 | 123.0267 | 122.8376 | 66.2203 | -123.3244
975.7969 | 123.1064 | -66.7145 | 56.3278 | -0.0057996 | -0.0092628 | 0.00060681 | 0.056011 | -0.0022669 | 0.061941 | -0.001755 | -0.00060453 | 0.00089321 | 0.058452 | 0.015498 | 0.059073 | -66.6649 | 0.0243 | -66.7002 | 56.2747 | 56.1838 | 56.3672 | -66.7963 | -66.6604 | -0.47583 | -66.6995 | 56.1894 | 56.3717 | 56.146 | -67.0378 | -0.081826 | -0.053089 | 0.04962 | 0.014256 | 0.096082 | -0.14406 | 0.039385 | -0.3233 | -0.13843 | 0.054089 | 0.015005 | 0.3383 | 0.043905 | -0.18182 | 122.9892 | 122.8982 | 123.0817 | 66.7388 | -123.1241 | 122.9039 | 123.0862 | 122.8605 | 66.2387 | -123.3656
976.7969 | 123.2208 | -66.655 | 56.2912 | -0.0057996 | -0.009049 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | 3.6274e-05 | 0.00067941 | 0.058879 | 0.01507 | 0.059073 | -66.6603 | 0.0243 | -66.6956 | 56.2747 | 56.1883 | 56.3626 | -66.7963 | -66.665 | -0.5033 | -66.6903 | 56.1848 | 56.3671 | 56.2101 | -67.0378 | -0.14134 | -0.016468 | -0.005312 | -0.040676 | 0.10066 | -0.10286 | 0.071427 | -0.38281 | -0.10639 | -0.01 | -0.035348 | 0.34746 | 0.075947 | -0.081102 | 122.9297 | 122.8433 | 123.0176 | 66.6793 | -123.0875 | 122.8398 | 123.0221 | 122.8651 | 66.1517 | -123.329
977.7969 | 123.0789 | -66.7053 | 56.3644 | -0.013431 | -0.009049 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058666 | 0.015284 | 0.058859 | -66.6649 | 0.0243 | -66.6956 | 56.2747 | 56.1929 | 56.3672 | -66.8009 | -66.6604 | -0.54451 | -66.6903 | 56.1802 | 56.3717 | 56.2193 | -67.0332 | -0.09556 | -0.08971 | 0.040464 | 0.009678 | 0.10524 | -0.17152 | 0.002764 | -0.32787 | -0.18421 | 0.044933 | 0.015006 | 0.34288 | 0.007284 | -0.14519 | 122.9801 | 122.8982 | 123.0725 | 66.7296 | -123.1653 | 122.8856 | 123.077 | 122.9246 | 66.1608 | -123.3976
978.7969 | 123.2071 | -66.6916 | 56.3141 | -0.013431 | -0.0092628 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00060453 | 0.0011068 | 0.058666 | 0.015498 | 0.059073 | -66.6603 | 0.0243 | -66.6956 | 56.2793 | 56.2067 | 56.3535 | -66.8009 | -66.6558 | -0.57656 | -66.6995 | 56.194 | 56.3763 | 56.2513 | -67.0332 | -0.10929 | -0.034778 | 0.031309 | -0.004055 | 0.10524 | -0.10743 | 0.039382 | -0.34161 | -0.12012 | 0.035779 | -0.007884 | 0.33372 | 0.062216 | -0.062783 | 122.9709 | 122.8982 | 123.0451 | 66.7159 | -123.115 | 122.8856 | 123.0679 | 122.9429 | 66.115 | -123.3473
979.7969 | 123.1247 | -66.7099 | 56.3507 | -0.0057996 | -0.0094764 | 0.00017941 | 0.056011 | -0.0029079 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058666 | 0.015284 | 0.059073 | -66.6603 | 0.0243 | -66.6956 | 56.2793 | 56.1975 | 56.3672 | -66.8009 | -66.6512 | -0.6315 | -66.6903 | 56.1894 | 56.3717 | 56.2147 | -67.0332 | -0.090982 | -0.071399 | 0.04962 | 0.014256 | 0.10524 | -0.15321 | 0.016497 | -0.3233 | -0.16132 | 0.058668 | 0.019584 | 0.34288 | 0.021017 | -0.13603 | 122.9892 | 122.9074 | 123.0771 | 66.7342 | -123.1516 | 122.8993 | 123.0816 | 122.9246 | 66.0784 | -123.3839
980.7969 | 123.1705 | -66.6779 | 56.2775 | -0.013431 | -0.0092628 | 0.00060681 | 0.056011 | -0.0029079 | 0.061727 | 0.0058755 | -0.00060453 | 0.00089321 | 0.058666 | 0.015711 | 0.0595 | -66.6649 | 0.0243 | -66.7002 | 56.2747 | 56.2067 | 56.3718 | -66.7917 | -66.6604 | -0.67271 | -66.6949 | 56.1894 | 56.3671 | 56.2193 | -67.024 | -0.11387 | -0.002735 | 0.012998 | -0.022366 | 0.091503 | -0.070808 | 0.094318 | -0.34618 | -0.088078 | 0.017467 | -0.017038 | 0.32914 | 0.08968 | -0.058212 | 122.9526 | 122.8845 | 123.0496 | 66.7022 | -123.0692 | 122.8672 | 123.045 | 122.8971 | 66.0051 | -123.3015
981.7969 | 123.1338 | -66.6916 | 56.3644 | 0.0018314 | -0.0092628 | 0.00082041 | 0.056224 | -0.0026943 | 0.061514 | -0.001755 | -0.00017733 | 0.00089321 | 0.058666 | 0.015498 | 0.059287 | -66.6603 | 0.0243 | -66.7002 | 56.2747 | 56.1883 | 56.3764 | -66.7917 | -66.6512 | -0.70934 | -66.6995 | 56.194 | 56.3671 | 56.2055 | -67.0332 | -0.10014 | -0.08971 | 0.031309 | -0.008633 | 0.091503 | -0.1761 | 0.011921 | -0.34161 | -0.17047 | 0.040357 | -0.007884 | 0.33372 | 0.002705 | -0.15892 | 122.9663 | 122.8799 | 123.068 | 66.7159 | -123.1562 | 122.8856 | 123.0587 | 122.8971 | 65.9822 | -123.3976
982.7969 | 123.23 | -66.655 | 56.2912 | 0.0018314 | -0.009049 | 0.00060681 | 0.056011 | -0.0022669 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.058879 | 0.015498 | 0.059073 | -66.6649 | 0.0243 | -66.6911 | 56.2793 | 56.1746 | 56.3718 | -66.7871 | -66.6512 | -0.75971 | -66.6903 | 56.1985 | 56.3809 | 56.2238 | -67.0286 | -0.13218 | -0.01189 | -0.00989 | -0.036097 | 0.096081 | -0.11659 | 0.080585 | -0.37365 | -0.092654 | 0.003736 | -0.035348 | 0.3383 | 0.089683 | -0.067367 | 122.9343 | 122.8296 | 123.0268 | 66.6793 | -123.0783 | 122.8535 | 123.0358 | 122.8788 | 65.8953 | -123.3198
983.7969 | 123.111 | -66.6824 | 56.3782 | -0.0057996 | -0.00969 | 0.00060681 | 0.056011 | -0.0022669 | 0.061727 | -0.0093855 | -0.00039093 | 0.00067941 | 0.059093 | 0.015498 | 0.059073 | -66.6511 | 0.0243 | -66.6956 | 56.2793 | 56.1929 | 56.3672 | -66.7917 | -66.6512 | -0.80092 | -66.6903 | 56.1985 | 56.3763 | 56.2284 | -67.0286 | -0.10929 | -0.098865 | 0.031311 | -0.01321 | 0.096081 | -0.18525 | -0.010969 | -0.34618 | -0.17963 | 0.031202 | -0.007882 | 0.3383 | -0.001871 | -0.14976 | 122.9617 | 122.8754 | 123.0496 | 66.7067 | -123.1699 | 122.881 | 123.0587 | 122.9108 | 65.8815 | -123.4068
984.7969 | 123.2483 | -66.6412 | 56.3187 | -0.013431 | -0.0094764 | 0.00082041 | 0.056224 | -0.0026943 | 0.061514 | -0.001755 | -0.00039093 | 0.00089321 | 0.059093 | 0.01507 | 0.058859 | -66.6557 | 0.019721 | -66.6911 | 56.2793 | 56.1929 | 56.3809 | -66.7917 | -66.6467 | -0.85128 | -66.6812 | 56.1894 | 56.3763 | 56.1597 | -67.0286 | -0.15049 | -0.039356 | -0.014466 | -0.04983 | 0.10066 | -0.12574 | 0.062276 | -0.38738 | -0.12928 | -0.005418 | -0.039923 | 0.34746 | 0.057638 | -0.15893 | 122.9205 | 122.8342 | 123.0222 | 66.661 | -123.1104 | 122.8306 | 123.0175 | 122.801 | 65.79 | -123.3473
985.7969 | 123.143 | -66.6916 | 56.3187 | -0.013431 | -0.0092628 | 0.0010342 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058666 | 0.01507 | 0.059287 | -66.6511 | 0.0243 | -66.6865 | 56.2885 | 56.1975 | 56.3718 | -66.7826 | -66.6375 | -0.89249 | -66.6903 | 56.1985 | 56.3763 | 56.2284 | -67.0286 | -0.090978 | -0.030199 | 0.040466 | 0.005102 | 0.09608 | -0.12117 | 0.053119 | -0.33703 | -0.12012 | 0.054093 | 0.001273 | 0.3383 | 0.057638 | -0.090254 | 122.9801 | 122.8891 | 123.0634 | 66.7159 | -123.1012 | 122.8901 | 123.0679 | 122.92 | 65.7991 | -123.3473
986.7969 | 123.2437 | -66.6595 | 56.2958 | -0.0057996 | -0.009049 | 0.00082041 | 0.056224 | -0.0024807 | 0.061727 | -0.0093855 | -0.00060453 | 0.00089321 | 0.058666 | 0.015284 | 0.059073 | -66.6557 | 0.019721 | -66.6911 | 56.2793 | 56.1883 | 56.3718 | -66.7826 | -66.6421 | -0.92454 | -66.6674 | 56.1985 | 56.3763 | 56.2147 | -67.0286 | -0.12302 | -0.016467 | 0.003845 | -0.031519 | 0.091502 | -0.10743 | 0.076008 | -0.36907 | -0.097231 | 0.017472 | -0.007876 | 0.36119 | 0.080527 | -0.081101 | 122.9389 | 122.8479 | 123.0313 | 66.6793 | -123.0783 | 122.8581 | 123.0358 | 122.8742 | 65.735 | -123.3244
987.7969 | 123.1293 | -66.6824 | 56.3324 | 0.0094624 | -0.0092628 | 0.00060681 | 0.056011 | -0.0022669 | 0.061727 | -0.0093855 | -0.00039093 | 0.00067941 | 0.058666 | 0.015284 | 0.059073 | -66.642 | 0.0243 | -66.6911 | 56.2885 | 56.2067 | 56.3764 | -66.7826 | -66.6421 | -0.96575 | -66.6766 | 56.1985 | 56.3809 | 56.265 | -67.024 | -0.10013 | -0.043931 | 0.040468 | -0.008631 | 0.091502 | -0.12574 | 0.043965 | -0.3416 | -0.13385 | 0.04036 | 0.005855 | 0.34746 | 0.048485 | -0.067357 | 122.9709 | 122.8891 | 123.0588 | 66.7067 | -123.115 | 122.881 | 123.0633 | 122.9475 | 65.7167 | -123.3564
988.7969 | 123.2254 | -66.6275 | 56.3141 | -0.0057996 | -0.0092628 | 0.00082041 | 0.056224 | -0.0024807 | 0.061514 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015498 | 0.059287 | -66.6511 | 0.019721 | -66.6911 | 56.2839 | 56.1975 | 56.3764 | -66.7826 | -66.6375 | -1.0299 | -66.6766 | 56.1985 | 56.3809 | 56.2513 | -67.0195 | -0.15506 | -0.0302 | -0.023621 | -0.063563 | 0.091502 | -0.11659 | 0.062275 | -0.39196 | -0.11554 | -0.009994 | -0.049077 | 0.34288 | 0.066795 | -0.062783 | 122.9114 | 122.825 | 123.0039 | 66.6472 | -123.0967 | 122.826 | 123.0084 | 122.8788 | 65.5977 | -123.3335
989.7969 | 123.175 | -66.6916 | 56.3232 | 0.0018314 | -0.0094764 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | -0.00060453 | 0.00089321 | 0.058879 | 0.015284 | 0.059287 | -66.6511 | 0.0243 | -66.6911 | 56.293 | 56.2158 | 56.3764 | -66.7826 | -66.6329 | -1.0436 | -66.6674 | 56.1894 | 56.3809 | 56.1918 | -67.0286 | -0.090978 | -0.030198 | 0.040466 | 0.000524 | 0.091502 | -0.10743 | 0.05312 | -0.33703 | -0.13385 | 0.058672 | 0.024167 | 0.36119 | 0.05764 | -0.13146 | 122.9846 | 122.9074 | 123.068 | 66.7159 | -123.1058 | 122.881 | 123.0725 | 122.8834 | 65.648 | -123.3519
990.7969 | 123.2529 | -66.6641 | 56.2912 | 0.0018314 | -0.0094764 | 0.0010342 | 0.056224 | -0.0026943 | 0.061941 | 0.0058755 | -0.00060453 | 0.0011068 | 0.058666 | 0.015498 | 0.059073 | -66.6465 | 0.015142 | -66.6865 | 56.2793 | 56.2067 | 56.3764 | -66.778 | -66.6283 | -1.0894 | -66.672 | 56.1985 | 56.3855 | 56.2147 | -67.0195 | -0.11386 | -0.01189 | 0.017579 | -0.022363 | 0.091501 | -0.084541 | 0.085163 | -0.35533 | -0.092654 | 0.035786 | -0.007877 | 0.34746 | 0.094262 | -0.076524 | 122.9434 | 122.8708 | 123.0405 | 66.6793 | -123.0692 | 122.8627 | 123.0496 | 122.8788 | 65.5747 | -123.3107
991.7969 | 123.1201 | -66.6687 | 56.3416 | 0.0018314 | -0.00969 | 0.00082041 | 0.055797 | -0.0026943 | 0.061514 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058879 | 0.01507 | 0.059287 | -66.642 | 0.015142 | -66.6865 | 56.293 | 56.2296 | 56.3901 | -66.7871 | -66.6238 | -1.1306 | -66.6674 | 56.2031 | 56.39 | 56.2513 | -67.0195 | -0.11845 | -0.048509 | 0.026735 | -0.017786 | 0.10066 | -0.112 | 0.048545 | -0.35076 | -0.13843 | 0.044942 | 0.001279 | 0.35204 | 0.048486 | -0.090249 | 122.9617 | 122.8983 | 123.0588 | 66.6838 | -123.1287 | 122.8718 | 123.0587 | 122.92 | 65.5381 | -123.361
992.7969 | 123.2391 | -66.6458 | 56.2866 | 0.0018314 | -0.0092628 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058452 | 0.015284 | 0.059073 | -66.642 | 0.015142 | -66.6819 | 56.2885 | 56.2204 | 56.3809 | -66.7826 | -66.6238 | -1.1764 | -66.6628 | 56.2077 | 56.39 | 56.2513 | -67.0195 | -0.13675 | 0.001845 | 0.003847 | -0.036096 | 0.10066 | -0.066226 | 0.09432 | -0.37365 | -0.078919 | 0.022054 | -0.01703 | 0.35662 | 0.10342 | -0.035317 | 122.9343 | 122.8662 | 123.0268 | 66.661 | -123.0692 | 122.8535 | 123.0359 | 122.8971 | 65.4694 | -123.3061
993.7969 | 123.23 | -66.5955 | 56.3644 | 0.0018314 | -0.0094764 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.058879 | 0.015711 | 0.059073 | -66.642 | 0.010564 | -66.6773 | 56.2839 | 56.2204 | 56.3764 | -66.7826 | -66.61 | -1.2176 | -66.6583 | 56.2169 | 56.39 | 56.2467 | -67.0195 | -0.18711 | -0.080554 | -0.046507 | -0.081872 | 0.10524 | -0.14405 | 0.011921 | -0.424 | -0.14758 | -0.014564 | -0.062806 | 0.36119 | 0.025598 | -0.11772 | 122.8793 | 122.8159 | 122.9718 | 66.606 | -123.147 | 122.8123 | 122.9855 | 122.8422 | 65.3779 | -123.3839
994.7969 | 123.2391 | -66.6367 | 56.3278 | -0.0057996 | -0.00969 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | -0.00060453 | 0.00089321 | 0.058238 | 0.01507 | 0.059287 | -66.6374 | 0.019721 | -66.6819 | 56.2976 | 56.2067 | 56.3855 | -66.778 | -66.6146 | -1.245 | -66.6674 | 56.2077 | 56.3992 | 56.2421 | -67.0149 | -0.14133 | -0.030197 | -0.00073 | -0.045251 | 0.096079 | -0.12116 | 0.057699 | -0.37822 | -0.12012 | 0.022056 | -0.030764 | 0.34746 | 0.071377 | -0.085673 | 122.9343 | 122.8433 | 123.0222 | 66.6564 | -123.1058 | 122.8444 | 123.0359 | 122.8788 | 65.3916 | -123.3427
995.7969 | 123.1979 | -66.6504 | 56.3004 | -0.0057996 | -0.0094764 | 0.0010342 | 0.056224 | -0.0024807 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.058879 | 0.015498 | 0.059073 | -66.6465 | 0.010564 | -66.6819 | 56.3022 | 56.2067 | 56.3947 | -66.7734 | -66.61 | -1.2863 | -66.6628 | 56.2077 | 56.3992 | 56.2513 | -67.0195 | -0.12302 | 0.001847 | 0.003846 | -0.031518 | 0.0915 | -0.093696 | 0.094323 | -0.36907 | -0.092652 | 0.040368 | -0.012452 | 0.35662 | 0.098843 | -0.04905 | 122.9526 | 122.857 | 123.0451 | 66.661 | -123.0738 | 122.8581 | 123.0496 | 122.9017 | 65.3641 | -123.3198
996.7969 | 123.2483 | -66.6321 | 56.3232 | -0.0057996 | -0.0092628 | 0.0010342 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.059093 | 0.015498 | 0.059073 | -66.6374 | 0.010564 | -66.6728 | 56.3068 | 56.2296 | 56.3809 | -66.7688 | -66.61 | -1.3137 | -66.6628 | 56.2077 | 56.39 | 56.2559 | -67.0149 | -0.13675 | -0.016463 | -0.005308 | -0.040672 | 0.096078 | -0.09369 | 0.057699 | -0.3828 | -0.11554 | 0.022057 | -0.030763 | 0.35204 | 0.066797 | -0.067359 | 122.9389 | 122.8616 | 123.013 | 66.6426 | -123.0921 | 122.8398 | 123.0221 | 122.888 | 65.3183 | -123.3381
997.7969 | 123.111 | -66.6458 | 56.3416 | -0.0057996 | -0.0094764 | 0.0010342 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015284 | 0.059287 | -66.6328 | 0.015142 | -66.6865 | 56.3022 | 56.2387 | 56.3947 | -66.7688 | -66.6054 | -1.3275 | -66.6583 | 56.2169 | 56.3992 | 56.2605 | -67.0149 | -0.12302 | -0.039352 | 0.013004 | -0.040674 | 0.082343 | -0.10284 | 0.053124 | -0.36907 | -0.12469 | 0.040368 | -0.012452 | 0.35662 | 0.057644 | -0.081092 | 122.948 | 122.8845 | 123.0405 | 66.661 | -123.1104 | 122.8627 | 123.045 | 122.9063 | 65.3183 | -123.3564
998.7969 | 123.2437 | -66.5955 | 56.3782 | -0.0057996 | -0.0094764 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | -0.00017733 | 0.00089321 | 0.058879 | 0.015284 | 0.058432 | -66.6328 | 0.005985 | -66.6728 | 56.2976 | 56.2296 | 56.3947 | -66.7688 | -66.6054 | -1.3549 | -66.6537 | 56.2214 | 56.4084 | 56.2696 | -67.0103 | -0.17337 | -0.080551 | -0.03735 | -0.077293 | 0.096078 | -0.14862 | 0.016503 | -0.41484 | -0.15674 | -0.009986 | -0.058227 | 0.35662 | 0.03018 | -0.10856 | 122.8931 | 122.825 | 122.9901 | 66.6014 | -123.147 | 122.8169 | 123.0038 | 122.8651 | 65.2405 | -123.3885
999.7969 | 123.1155 | -66.6595 | 56.3599 | -0.0057996 | -0.0094764 | 0.00060681 | 0.056224 | -0.0026943 | 0.061941 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058666 | 0.015284 | 0.058859 | -66.6282 | 0.005985 | -66.6636 | 56.3068 | 56.2296 | 56.3947 | -66.7688 | -66.5917 | -1.387 | -66.6491 | 56.2214 | 56.3992 | 56.2559 | -67.0011 | -0.10928 | -0.053084 | 0.031315 | -0.00405 | 0.10523 | -0.13031 | 0.034814 | -0.3416 | -0.13842 | 0.067837 | 0.010439 | 0.35204 | 0.039334 | -0.10398 | 122.9663 | 122.8891 | 123.0542 | 66.6655 | -123.1287 | 122.881 | 123.0587 | 122.9154 | 65.2726 | -123.361
1000.7969 | 123.2437 | -66.6229 | 56.3141 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056438 | -0.0024807 | 0.061514 | -0.0093855 | -0.00017733 | 0.00067941 | 0.058666 | 0.015711 | 0.0595 | -66.6237 | -0.007751 | -66.6682 | 56.3068 | 56.2296 | 56.3901 | -66.7643 | -66.5917 | -1.3961 | -66.6491 | 56.2123 | 56.4038 | 56.2696 | -67.0149 | -0.14133 | -0.007308 | -0.000728 | -0.045249 | 0.096077 | -0.084535 | 0.076011 | -0.39196 | -0.10181 | 0.031216 | -0.026182 | 0.36577 | 0.089688 | -0.044469 | 122.9297 | 122.8525 | 123.013 | 66.6152 | -123.0783 | 122.8352 | 123.0267 | 122.8925 | 65.2268 | -123.329
1001.7969 | 123.1522 | -66.6595 | 56.369 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.058879 | 0.015284 | 0.058859 | -66.6145 | -0.003172 | -66.6636 | 56.3022 | 56.2296 | 56.3947 | -66.7643 | -66.5871 | -1.4236 | -66.6445 | 56.226 | 56.4038 | 56.2513 | -67.0057 | -0.1047 | -0.066818 | 0.04505 | -0.00405 | 0.10066 | -0.13947 | 0.025658 | -0.34618 | -0.143 | 0.072416 | 0.015017 | 0.36119 | 0.034756 | -0.11772 | 122.9617 | 122.8891 | 123.0542 | 66.6564 | -123.1333 | 122.8856 | 123.0633 | 122.9109 | 65.2359 | -123.3747
1002.7969 | 123.2529 | -66.6183 | 56.3461 | -0.0057996 | -0.0092628 | 0.00082041 | 0.056011 | -0.0029079 | 0.061727 | -0.001755 | -0.00060453 | 0.00046581 | 0.058879 | 0.015498 | 0.059287 | -66.6191 | -0.003172 | -66.659 | 56.3022 | 56.2204 | 56.3993 | -66.7643 | -66.5734 | -1.4374 | -66.6354 | 56.2214 | 56.4129 | 56.2742 | -67.0057 | -0.1459 | -0.043929 | -0.000727 | -0.04067 | 0.10523 | -0.12573 | 0.053125 | -0.38738 | -0.12469 | 0.044953 | -0.017024 | 0.37035 | 0.066802 | -0.071933 | 122.9205 | 122.8387 | 123.0176 | 66.6152 | -123.1104 | 122.8398 | 123.0313 | 122.8925 | 65.181 | -123.3519
1003.7969 | 123.1796 | -66.6046 | 56.3873 | -0.0057996 | -0.0094764 | 0.00039321 | 0.056224 | -0.0024807 | 0.061514 | 0.0058755 | -0.00039093 | 0.0011068 | 0.058666 | 0.015711 | 0.059073 | -66.6191 | -0.012329 | -66.6636 | 56.3068 | 56.2204 | 56.4084 | -66.7643 | -66.5826 | -1.4602 | -66.6354 | 56.2352 | 56.4084 | 56.2605 | -67.0011 | -0.15964 | -0.08055 | -0.01446 | -0.058982 | 0.10066 | -0.16693 | 0.021083 | -0.39653 | -0.15216 | 0.022063 | -0.030757 | 0.36577 | 0.021025 | -0.12687 | 122.9114 | 122.825 | 123.013 | 66.5923 | -123.1516 | 122.8398 | 123.013 | 122.8651 | 65.1444 | -123.3885
1004.7969 | 123.2208 | -66.6229 | 56.3416 | -0.013431 | -0.0094764 | 0.00082041 | 0.056011 | -0.0026943 | 0.061941 | -0.001755 | -0.00081813 | 0.00089321 | 0.058666 | 0.015711 | 0.059073 | -66.6145 | -0.016908 | -66.659 | 56.3159 | 56.2021 | 56.4084 | -66.7597 | -66.578 | -1.4831 | -66.6399 | 56.2306 | 56.4084 | 56.2376 | -66.992 | -0.13675 | -0.025617 | 0.008429 | -0.036092 | 0.10065 | -0.13947 | 0.066859 | -0.36906 | -0.11096 | 0.044953 | -0.017025 | 0.35204 | 0.066801 | -0.10398 | 122.9389 | 122.825 | 123.0313 | 66.606 | -123.1012 | 122.8535 | 123.0313 | 122.8605 | 65.1398 | -123.3335
1005.7969 | 122.9507 | -66.6779 | 56.3416 | -0.013431 | -0.0092628 | 0.00039321 | 0.056224 | -0.0022669 | 0.061514 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058666 | 0.015498 | 0.058859 | -66.6145 | -0.030644 | -66.6499 | 56.3159 | 56.2158 | 56.4084 | -66.7597 | -66.5642 | -1.5015 | -66.6354 | 56.2352 | 56.4175 | 56.233 | -66.9966 | -0.081816 | -0.025617 | 0.06336 | 0.027995 | 0.10981 | -0.12574 | 0.066859 | -0.31871 | -0.10638 | 0.11362 | 0.042485 | 0.36119 | 0.075958 | -0.10856 | 122.9938 | 122.8937 | 123.0863 | 66.6472 | -123.1012 | 122.913 | 123.0954 | 122.9108 | 65.1764 | -123.3381
1006.7969 | 123.2437 | -66.6458 | 56.3004 | 0.0018314 | -0.0094764 | 0.00039321 | 0.056224 | -0.0024807 | 0.061727 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015711 | 0.058859 | -66.6099 | -0.030644 | -66.6544 | 56.3159 | 56.2204 | 56.4038 | -66.7505 | -66.5642 | -1.5289 | -66.6308 | 56.2352 | 56.4267 | 56.2376 | -66.992 | -0.1047 | 0.015582 | 0.035896 | -0.008626 | 0.096075 | -0.079959 | 0.10348 | -0.34617 | -0.065181 | 0.081577 | 0.015021 | 0.36119 | 0.12631 | -0.062786 | 122.9617 | 122.8662 | 123.0496 | 66.6152 | -123.0509 | 122.881 | 123.0725 | 122.8834 | 65.1169 | -123.2923
1007.7969 | 123.1247 | -66.655 | 56.3644 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056224 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058666 | 0.015284 | 0.059287 | -66.6099 | -0.030644 | -66.6453 | 56.3251 | 56.2204 | 56.4221 | -66.7551 | -66.5642 | -1.5335 | -66.6262 | 56.226 | 56.4175 | 56.233 | -66.9874 | -0.10013 | -0.039348 | 0.045051 | 0.009685 | 0.10981 | -0.14405 | 0.057707 | -0.33244 | -0.13842 | 0.090732 | 0.028754 | 0.36119 | 0.05307 | -0.13145 | 122.9801 | 122.8754 | 123.0771 | 66.6243 | -123.1195 | 122.881 | 123.0725 | 122.888 | 65.1215 | -123.3518
1008.7969 | 123.2025 | -66.6275 | 56.3782 | -0.0057996 | -0.0094764 | 0.00060681 | 0.056224 | -0.0026943 | 0.061727 | 0.0058755 | -0.00081813 | 0.0013204 | 0.058879 | 0.015711 | 0.0595 | -66.6008 | -0.035222 | -66.6453 | 56.3159 | 56.2204 | 56.4084 | -66.7505 | -66.5597 | -1.5747 | -66.6262 | 56.2352 | 56.4267 | 56.1964 | -66.9874 | -0.12301 | -0.062238 | 0.026741 | -0.017781 | 0.10523 | -0.15778 | 0.030238 | -0.3599 | -0.143 | 0.067844 | 0.001288 | 0.36119 | 0.048494 | -0.18181 | 122.9434 | 122.8479 | 123.0359 | 66.5923 | -123.1287 | 122.8627 | 123.0542 | 122.8239 | 65.0528 | -123.3656
1009.7969 | 123.1201 | -66.6687 | 56.3736 | -0.021062 | -0.00969 | 0.00082041 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | -0.00060453 | 0.00067941 | 0.058666 | 0.015925 | 0.059287 | -66.5962 | -0.048958 | -66.6499 | 56.3205 | 56.2341 | 56.4176 | -66.7505 | -66.5597 | -1.6068 | -66.6216 | 56.2352 | 56.4267 | 56.2513 | -66.992 | -0.081813 | -0.053082 | 0.072519 | 0.01884 | 0.10065 | -0.13947 | 0.043974 | -0.32328 | -0.13842 | 0.10904 | 0.047066 | 0.37035 | 0.053072 | -0.12229 | 122.9892 | 122.9028 | 123.0863 | 66.6197 | -123.1241 | 122.9039 | 123.0954 | 122.92 | 65.0619 | -123.3656
1010.7969 | 123.2574 | -66.5909 | 56.3553 | 0.0094624 | -0.0094764 | 0.00082041 | 0.056011 | -0.0024807 | 0.0613 | -0.001755 | -0.00081813 | 0.00089321 | 0.058452 | 0.015711 | 0.059073 | -66.5962 | -0.067272 | -66.6453 | 56.3251 | 56.2387 | 56.4176 | -66.7459 | -66.5459 | -1.6342 | -66.6171 | 56.2398 | 56.4221 | 56.2742 | -66.9874 | -0.15505 | -0.030193 | -0.005301 | -0.054402 | 0.10065 | -0.11658 | 0.062284 | -0.39653 | -0.11554 | 0.04496 | -0.026175 | 0.37035 | 0.066804 | -0.081089 | 122.916 | 122.8296 | 123.0085 | 66.5236 | -123.1012 | 122.8306 | 123.013 | 122.8651 | 64.9566 | -123.3427
1011.7969 | 123.143 | -66.6367 | 56.4102 | -0.0057996 | -0.00969 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058452 | 0.015498 | 0.059287 | -66.6008 | -0.058115 | -66.6453 | 56.3251 | 56.257 | 56.4313 | -66.7459 | -66.5459 | -1.6663 | -66.6033 | 56.2352 | 56.4358 | 56.2513 | -66.9782 | -0.10928 | -0.085124 | 0.035897 | -0.008625 | 0.10065 | -0.15319 | 0.021088 | -0.34159 | -0.17504 | 0.090737 | 0.033338 | 0.37493 | 0.025608 | -0.15891 | 122.9618 | 122.8937 | 123.068 | 66.5785 | -123.1562 | 122.8718 | 123.0725 | 122.888 | 64.9704 | -123.3885
1012.7969 | 123.1338 | -66.6367 | 56.3736 | 0.0094624 | -0.0092628 | 0.00060681 | 0.055797 | -0.0031215 | 0.061941 | -0.0093855 | -0.00060453 | 0.00089321 | 0.058666 | 0.015925 | 0.059073 | -66.5962 | -0.067272 | -66.6361 | 56.3388 | 56.2387 | 56.4267 | -66.7414 | -66.5459 | -1.6938 | -66.6079 | 56.2443 | 56.4312 | 56.2834 | -66.9782 | -0.1047 | -0.034768 | 0.040476 | 0.000532 | 0.10523 | -0.13489 | 0.053131 | -0.34159 | -0.12927 | 0.090737 | 0.028759 | 0.37035 | 0.057651 | -0.090242 | 122.9755 | 122.8754 | 123.0634 | 66.5694 | -123.115 | 122.881 | 123.0679 | 122.92 | 64.9429 | -123.3518
1013.7969 | 123.2254 | -66.6046 | 56.369 | 0.0094624 | -0.0094764 | 0.00039321 | 0.056011 | -0.0031215 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015925 | 0.058859 | -66.587 | -0.081008 | -66.6407 | 56.3342 | 56.2524 | 56.4359 | -66.7276 | -66.5368 | -1.7167 | -66.6033 | 56.2398 | 56.4404 | 56.2879 | -66.9737 | -0.12301 | -0.034769 | 0.017588 | -0.03609 | 0.086916 | -0.11657 | 0.066865 | -0.36906 | -0.12927 | 0.06785 | 0.001294 | 0.37035 | 0.071385 | -0.081086 | 122.9389 | 122.8571 | 123.0405 | 66.5236 | -123.0966 | 122.8444 | 123.045 | 122.8925 | 64.888 | -123.3427
1014.7969 | 123.2162 | -66.6321 | 56.3599 | 0.0018314 | -0.0094764 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00081813 | 0.00067941 | 0.058879 | 0.015925 | 0.059073 | -66.587 | -0.085587 | -66.6315 | 56.3434 | 56.2708 | 56.4221 | -66.7322 | -66.5322 | -1.767 | -66.5987 | 56.2489 | 56.4404 | 56.3062 | -66.9737 | -0.10012 | -0.016457 | 0.045054 | 0.000532 | 0.10065 | -0.0891 | 0.062285 | -0.34159 | -0.11095 | 0.099895 | 0.033339 | 0.37493 | 0.080541 | -0.053616 | 122.9755 | 122.9028 | 123.0542 | 66.5465 | -123.0921 | 122.881 | 123.0725 | 122.9383 | 64.8651 | -123.3335
1015.7969 | 123.1384 | -66.6092 | 56.4011 | -0.0057996 | -0.0094764 | 0.00082041 | 0.056011 | -0.0029079 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.058879 | 0.015711 | 0.059287 | -66.5779 | -0.099323 | -66.6315 | 56.3434 | 56.2662 | 56.4359 | -66.7368 | -66.5276 | -1.8082 | -66.5987 | 56.2581 | 56.4404 | 56.2605 | -66.9691 | -0.12759 | -0.057656 | 0.031323 | -0.022356 | 0.10523 | -0.13488 | 0.034822 | -0.3599 | -0.143 | 0.081585 | 0.010451 | 0.37035 | 0.039342 | -0.1406 | 122.9526 | 122.8754 | 123.0451 | 66.5099 | -123.1378 | 122.8673 | 123.0496 | 122.8697 | 64.801 | -123.3702
1016.7969 | 123.1705 | -66.6412 | 56.3919 | -0.0057996 | -0.0094764 | 0.00039321 | 0.056011 | -0.0022669 | 0.061514 | 0.013506 | -0.00039093 | 0.00089321 | 0.058452 | 0.015498 | 0.059073 | -66.5779 | -0.11764 | -66.6132 | 56.3388 | 56.2753 | 56.4405 | -66.723 | -66.5276 | -1.8586 | -66.585 | 56.2672 | 56.445 | 56.2788 | -66.9691 | -0.081806 | -0.053079 | 0.063366 | 0.028 | 0.10981 | -0.11657 | 0.048556 | -0.32786 | -0.12469 | 0.11363 | 0.05623 | 0.38409 | 0.053076 | -0.11313 | 122.9801 | 122.9166 | 123.0817 | 66.5236 | -123.1149 | 122.9085 | 123.0862 | 122.92 | 64.7826 | -123.361
1017.7969 | 123.1247 | -66.6 | 56.4239 | -0.0057996 | -0.00969 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058879 | 0.015711 | 0.058859 | -66.5733 | -0.12679 | -66.6132 | 56.348 | 56.2845 | 56.445 | -66.7185 | -66.5139 | -1.8906 | -66.5804 | 56.2672 | 56.4496 | 56.3062 | -66.9645 | -0.11843 | -0.075965 | 0.026747 | -0.013198 | 0.10523 | -0.13945 | 0.021091 | -0.36448 | -0.15673 | 0.086167 | 0.01961 | 0.38409 | 0.025611 | -0.1177 | 122.948 | 122.8845 | 123.0451 | 66.4732 | -123.1424 | 122.8673 | 123.0496 | 122.9063 | 64.7094 | -123.3885
1018.7969 | 123.2391 | -66.6092 | 56.3644 | -0.0057996 | -0.0099038 | 0.00060681 | 0.055797 | -0.0029079 | 0.061727 | 0.0058755 | -0.00039093 | 0.00067941 | 0.058452 | 0.015925 | 0.058859 | -66.5641 | -0.14969 | -66.6224 | 56.3617 | 56.2845 | 56.4496 | -66.7139 | -66.5093 | -1.9181 | -66.5713 | 56.2718 | 56.4633 | 56.3246 | -66.9599 | -0.10469 | -0.002721 | 0.045058 | -0.013199 | 0.091492 | -0.079942 | 0.085179 | -0.35074 | -0.09264 | 0.0999 | 0.037923 | 0.38867 | 0.098856 | -0.039879 | 122.9709 | 122.8937 | 123.0588 | 66.4595 | -123.0783 | 122.881 | 123.0725 | 122.9338 | 64.6911 | -123.3244
1019.7969 | 123.1613 | -66.5817 | 56.4148 | 0.0018314 | -0.0092628 | 0.00082041 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058452 | 0.015498 | 0.059073 | -66.555 | -0.16342 | -66.6132 | 56.3617 | 56.2662 | 56.4542 | -66.723 | -66.5047 | -1.941 | -66.5713 | 56.2718 | 56.4587 | 56.3337 | -66.9554 | -0.14131 | -0.053075 | 0.026749 | -0.031509 | 0.10981 | -0.14861 | 0.039403 | -0.37363 | -0.14299 | 0.077013 | 0.010457 | 0.38409 | 0.043923 | -0.081076 | 122.9434 | 122.8479 | 123.0359 | 66.4183 | -123.1378 | 122.8535 | 123.0404 | 122.9154 | 64.6407 | -123.3701
1020.7969 | 123.1201 | -66.6046 | 56.4194 | 0.0018314 | -0.0092628 | 0.00082041 | 0.056011 | -0.0026943 | 0.062155 | 0.0058755 | -0.00060453 | 0.00067941 | 0.058666 | 0.015498 | 0.0595 | -66.5596 | -0.19547 | -66.6178 | 56.3663 | 56.2937 | 56.4542 | -66.7139 | -66.5001 | -1.996 | -66.5667 | 56.2718 | 56.4633 | 56.3246 | -66.9462 | -0.10927 | -0.053075 | 0.045059 | -0.013199 | 0.09607 | -0.12572 | 0.034825 | -0.34158 | -0.14757 | 0.10448 | 0.037924 | 0.37951 | 0.043924 | -0.094811 | 122.9709 | 122.8983 | 123.0588 | 66.4091 | -123.1333 | 122.8764 | 123.0679 | 122.9292 | 64.6087 | -123.3656
1021.7969 | 123.1796 | -66.6092 | 56.4102 | 0.0018314 | -0.0094764 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | 0.0058755 | -0.00039093 | 0.0011068 | 0.058666 | 0.015925 | 0.059073 | -66.555 | -0.20005 | -66.6041 | 56.3709 | 56.3074 | 56.4634 | -66.7139 | -66.4956 | -2.0372 | -66.5575 | 56.2718 | 56.4587 | 56.3246 | -66.937 | -0.10469 | -0.03934 | 0.054215 | 0.005114 | 0.1098 | -0.10282 | 0.053139 | -0.32785 | -0.13842 | 0.11364 | 0.051659 | 0.37951 | 0.048501 | -0.085655 | 122.9801 | 122.9166 | 123.0725 | 66.4091 | -123.1241 | 122.881 | 123.0679 | 122.9338 | 64.572 | -123.3473
1022.7969 | 123.0881 | -66.6092 | 56.4423 | -0.013431 | -0.00969 | 0.00060681 | 0.055797 | -0.0026943 | 0.061941 | -0.0093855 | -0.00017733 | 0.00067941 | 0.058666 | 0.015925 | 0.059287 | -66.5412 | -0.24126 | -66.5949 | 56.3755 | 56.3028 | 56.4634 | -66.7093 | -66.4772 | -2.0738 | -66.5484 | 56.281 | 56.4725 | 56.3246 | -66.937 | -0.10011 | -0.066806 | 0.06795 | 0.01427 | 0.11438 | -0.13945 | 0.021095 | -0.32785 | -0.1613 | 0.13195 | 0.060816 | 0.38866 | 0.030193 | -0.1177 | 122.9846 | 122.912 | 123.0725 | 66.3679 | -123.1516 | 122.8901 | 123.0816 | 122.9338 | 64.5354 | -123.3793
1023.7969 | 123.1476 | -66.6 | 56.4468 | -0.0057996 | -0.00969 | 0.00039321 | 0.056224 | -0.0022669 | 0.061514 | -0.001755 | -0.00060453 | 0.00089321 | 0.058452 | 0.015711 | 0.059287 | -66.5458 | -0.27331 | -66.5903 | 56.3755 | 56.3028 | 56.4725 | -66.6956 | -66.4772 | -2.1471 | -66.5484 | 56.2947 | 56.477 | 56.3154 | -66.9416 | -0.09553 | -0.071383 | 0.054217 | 0.009694 | 0.10522 | -0.14402 | 0.025675 | -0.34158 | -0.15214 | 0.1228 | 0.051661 | 0.39324 | 0.030195 | -0.13143 | 122.9755 | 122.9029 | 123.0726 | 66.3267 | -123.1424 | 122.8947 | 123.0771 | 122.9154 | 64.453 | -123.3885
1024.7969 | 123.1384 | -66.5817 | 56.456 | -0.0057996 | -0.0092628 | 0.00060681 | 0.055797 | -0.0024807 | 0.061514 | -0.001755 | -0.00017733 | 0.0011068 | 0.058666 | 0.015925 | 0.058859 | -66.5275 | -0.30078 | -66.5858 | 56.3755 | 56.3074 | 56.4725 | -66.691 | -66.4635 | -2.1608 | -66.5392 | 56.2947 | 56.477 | 56.3383 | -66.9279 | -0.10926 | -0.080539 | 0.05422 | -0.004039 | 0.10522 | -0.1486 | 0.016519 | -0.34616 | -0.1613 | 0.11822 | 0.042508 | 0.38866 | 0.021039 | -0.1177 | 122.9572 | 122.8891 | 123.0542 | 66.2809 | -123.147 | 122.8764 | 123.0588 | 122.92 | 64.4209 | -123.3839
1025.7969 | 123.1613 | -66.5588 | 56.456 | 0.0094624 | -0.0092628 | 0.00039321 | 0.055797 | -0.0026943 | 0.061941 | -0.001755 | -0.00060453 | 0.00089321 | 0.058666 | 0.015711 | 0.058859 | -66.5275 | -0.34199 | -66.5812 | 56.3938 | 56.3028 | 56.4771 | -66.6864 | -66.4635 | -2.2157 | -66.5301 | 56.2901 | 56.4862 | 56.3062 | -66.9279 | -0.12757 | -0.062225 | 0.031332 | -0.022349 | 0.10522 | -0.15318 | 0.021097 | -0.36904 | -0.16588 | 0.095333 | 0.028777 | 0.39782 | 0.030196 | -0.14975 | 122.9526 | 122.8617 | 123.0359 | 66.2168 | -123.1424 | 122.849 | 123.045 | 122.8651 | 64.3431 | -123.3839
1026.7969 | 123.0972 | -66.5771 | 56.4423 | 0.0018314 | -0.010117 | 0.0010342 | 0.056011 | -0.0022669 | 0.0613 | -0.001755 | -0.00039093 | 0.00089321 | 0.058879 | 0.015498 | 0.059073 | -66.5183 | -0.37404 | -66.5766 | 56.3938 | 56.3166 | 56.4862 | -66.6864 | -66.4543 | -2.2798 | -66.5255 | 56.3038 | 56.4862 | 56.32 | -66.9187 | -0.10926 | -0.048492 | 0.058798 | 0.00054 | 0.1098 | -0.12571 | 0.043988 | -0.34158 | -0.13841 | 0.1228 | 0.051666 | 0.39324 | 0.043929 | -0.12228 | 122.9709 | 122.8937 | 123.0634 | 66.2031 | -123.1287 | 122.881 | 123.0633 | 122.8971 | 64.2973 | -123.361
1027.7969 | 123.1705 | -66.5543 | 56.4651 | 0.0018314 | -0.0092628 | 0.0010342 | 0.055797 | -0.0026943 | 0.061727 | 0.013506 | -0.00039093 | 0.0011068 | 0.058879 | 0.015925 | 0.059073 | -66.5138 | -0.41525 | -66.572 | 56.3983 | 56.3074 | 56.4908 | -66.6773 | -66.4543 | -2.321 | -66.5255 | 56.313 | 56.4862 | 56.3062 | -66.9096 | -0.12299 | -0.066802 | 0.040489 | -0.01777 | 0.10522 | -0.15775 | 0.025678 | -0.35531 | -0.15214 | 0.099913 | 0.028778 | 0.38408 | 0.021041 | -0.1589 | 122.9526 | 122.8617 | 123.0451 | 66.139 | -123.1424 | 122.8673 | 123.0404 | 122.8605 | 64.2332 | -123.3747
1028.7969 | 123.1201 | -66.5955 | 56.4285 | 0.0018314 | -0.00969 | 0.00082041 | 0.055797 | -0.0026943 | 0.061941 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015711 | 0.059287 | -66.5183 | -0.47019 | -66.5629 | 56.3983 | 56.3166 | 56.4954 | -66.6727 | -66.4406 | -2.3714 | -66.5072 | 56.3084 | 56.4953 | 56.265 | -66.9096 | -0.077214 | -0.030181 | 0.077109 | 0.032585 | 0.1098 | -0.11198 | 0.066878 | -0.31411 | -0.1201 | 0.15485 | 0.088292 | 0.4024 | 0.066819 | -0.16349 | 122.9938 | 122.912 | 123.0909 | 66.1253 | -123.1012 | 122.9039 | 123.0908 | 122.8605 | 64.224 | -123.3381
1029.7969 | 123.1476 | -66.5451 | 56.4697 | 0.0018314 | -0.0099038 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.017016 | -0.00017733 | 0.0011068 | 0.058452 | 0.015925 | 0.059073 | -66.5046 | -0.50224 | -66.5537 | 56.4075 | 56.3211 | 56.5046 | -66.6681 | -66.4315 | -2.4309 | -66.5072 | 56.3176 | 56.5091 | 56.2376 | -66.9096 | -0.12299 | -0.062223 | 0.04049 | -0.008612 | 0.11438 | -0.1486 | 0.034836 | -0.36446 | -0.15214 | 0.11365 | 0.037938 | 0.4024 | 0.039356 | -0.23216 | 122.9526 | 122.8662 | 123.0497 | 66.0429 | -123.1378 | 122.8627 | 123.0542 | 122.7827 | 64.1142 | -123.3793
1030.7969 | 123.1705 | -66.5771 | 56.5018 | -0.0057996 | -0.0094764 | 0.00039321 | 0.056438 | -0.0022669 | 0.061514 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058452 | 0.015711 | 0.059287 | -66.4955 | -0.54803 | -66.5537 | 56.4167 | 56.3211 | 56.5137 | -66.6635 | -66.4223 | -2.4813 | -66.5026 | 56.313 | 56.5045 | 56.3062 | -66.9096 | -0.086367 | -0.085109 | 0.08169 | 0.023431 | 0.1098 | -0.18064 | 0.01195 | -0.33242 | -0.18876 | 0.15485 | 0.07456 | 0.40698 | 0.002734 | -0.19552 | 122.9938 | 122.8983 | 123.0909 | 66.0291 | -123.1653 | 122.8902 | 123.0817 | 122.8834 | 64.0958 | -123.4113
1031.7969 | 123.143 | -66.5588 | 56.456 | 0.0018314 | -0.00969 | 0.00082041 | 0.056011 | -0.0026943 | 0.061941 | 0.0058755 | -0.00060453 | 0.00067941 | 0.058879 | 0.015925 | 0.058859 | -66.4863 | -0.61213 | -66.5446 | 56.4212 | 56.3303 | 56.5091 | -66.6635 | -66.4223 | -2.5271 | -66.5026 | 56.3222 | 56.5045 | 56.2879 | -66.8958 | -0.10468 | -0.034755 | 0.072537 | 0.014278 | 0.11895 | -0.1257 | 0.053148 | -0.33699 | -0.13383 | 0.13654 | 0.05625 | 0.39324 | 0.04851 | -0.16806 | 122.9801 | 122.8891 | 123.068 | 65.9467 | -123.1195 | 122.881 | 123.0633 | 122.8468 | 64.0317 | -123.3518
1032.7969 | 123.1201 | -66.5314 | 56.4743 | 0.0018314 | -0.00969 | 0.00060681 | 0.056011 | -0.0026943 | 0.0613 | -0.001755 | -0.00039093 | 0.00089321 | 0.058666 | 0.015498 | 0.059073 | -66.4771 | -0.65791 | -66.5354 | 56.4212 | 56.3394 | 56.5183 | -66.6452 | -66.4131 | -2.6232 | -66.4934 | 56.3359 | 56.5137 | 56.2421 | -66.8913 | -0.11383 | -0.053065 | 0.054228 | -0.004032 | 0.1098 | -0.13486 | 0.043995 | -0.35988 | -0.1384 | 0.11823 | 0.037941 | 0.39782 | 0.039358 | -0.23216 | 122.9526 | 122.8708 | 123.0497 | 65.8735 | -123.1195 | 122.8673 | 123.045 | 122.7735 | 63.9081 | -123.3656
1033.7969 | 123.1613 | -66.5131 | 56.4835 | 0.0018314 | -0.00969 | 0.00060681 | 0.056011 | -0.0026943 | 0.0613 | -0.001755 | -0.00060453 | 0.0011068 | 0.058879 | 0.015925 | 0.058859 | -66.4771 | -0.70828 | -66.5354 | 56.4304 | 56.3486 | 56.5229 | -66.6452 | -66.4086 | -2.6782 | -66.4843 | 56.3405 | 56.532 | 56.3383 | -66.8821 | -0.13214 | -0.053063 | 0.035918 | -0.022342 | 0.1098 | -0.13486 | 0.039418 | -0.36903 | -0.14298 | 0.1045 | 0.028788 | 0.39782 | 0.048517 | -0.14516 | 122.9435 | 122.8617 | 123.0359 | 65.8048 | -123.1287 | 122.8535 | 123.045 | 122.8514 | 63.8349 | -123.3656
1034.7969 | 123.0881 | -66.5451 | 56.5018 | -0.0057996 | -0.00969 | 0.00039321 | 0.056652 | -0.0022669 | 0.0613 | -0.001755 | -0.00060453 | 0.0011068 | 0.058666 | 0.016139 | 0.059073 | -66.468 | -0.7678 | -66.5308 | 56.4441 | 56.3349 | 56.5275 | -66.6452 | -66.3902 | -2.7286 | -66.4751 | 56.3451 | 56.5274 | 56.2696 | -66.8775 | -0.10009 | -0.057639 | 0.077118 | 0.014279 | 0.11437 | -0.1669 | 0.025686 | -0.33241 | -0.15671 | 0.15486 | 0.069989 | 0.4024 | 0.025627 | -0.23215 | 122.9892 | 122.88 | 123.0726 | 65.7773 | -123.147 | 122.8902 | 123.0725 | 122.8147 | 63.8166 | -123.3793
1035.7969 | 123.1522 | -66.5039 | 56.5063 | 0.0018314 | -0.00969 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0013204 | 0.058666 | 0.015498 | 0.059073 | -66.468 | -0.8319 | -66.5171 | 56.4396 | 56.3623 | 56.5412 | -66.6452 | -66.3902 | -2.7927 | -66.4705 | 56.3542 | 56.5411 | 56.3612 | -66.8729 | -0.14129 | -0.066795 | 0.035919 | -0.013185 | 0.12811 | -0.14401 | 0.034844 | -0.36903 | -0.15213 | 0.11366 | 0.033368 | 0.4024 | 0.034785 | -0.14516 | 122.9435 | 122.8662 | 123.0451 | 65.672 | -123.1515 | 122.8581 | 123.045 | 122.8651 | 63.7113 | -123.3793
1036.7969 | 123.1201 | -66.5451 | 56.5155 | -0.0057996 | -0.010117 | 0.00039321 | 0.056438 | -0.0026943 | 0.061514 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058879 | 0.016139 | 0.058859 | -66.4588 | -0.90516 | -66.5125 | 56.4441 | 56.3578 | 56.5412 | -66.6269 | -66.3719 | -2.8339 | -66.4614 | 56.3542 | 56.5503 | 56.32 | -66.8729 | -0.081778 | -0.071372 | 0.086274 | 0.032592 | 0.11437 | -0.15774 | 0.025689 | -0.32783 | -0.16129 | 0.17318 | 0.083725 | 0.41156 | 0.034787 | -0.19552 | 122.9892 | 122.9029 | 123.0863 | 65.6399 | -123.1424 | 122.8993 | 123.0954 | 122.8651 | 63.7112 | -123.3884
1037.7969 | 123.1567 | -66.4993 | 56.5384 | -0.013431 | -0.00969 | 0.00039321 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.058879 | 0.015498 | 0.058859 | -66.4497 | -0.97384 | -66.5034 | 56.4579 | 56.3623 | 56.5458 | -66.6177 | -66.3674 | -2.8934 | -66.4522 | 56.3634 | 56.5457 | 56.407 | -66.8638 | -0.1184 | -0.080525 | 0.049655 | -0.004027 | 0.11437 | -0.17605 | 0.007379 | -0.36445 | -0.17502 | 0.13198 | 0.047106 | 0.41156 | 0.007321 | -0.13141 | 122.9572 | 122.8617 | 123.0451 | 65.5255 | -123.1561 | 122.8627 | 123.045 | 122.9063 | 63.6059 | -123.4022
1038.7969 | 123.1796 | -66.5131 | 56.5018 | 0.0018314 | -0.0094764 | 0.00082041 | 0.055583 | -0.0024807 | 0.061514 | 0.0058755 | -0.00039093 | 0.0011068 | 0.058238 | 0.015711 | 0.058646 | -66.4359 | -1.0196 | -66.4942 | 56.4579 | 56.3761 | 56.5549 | -66.6131 | -66.3582 | -2.9621 | -66.4431 | 56.3725 | 56.5594 | 56.4024 | -66.8455 | -0.10008 | -0.043904 | 0.077123 | 0.018863 | 0.11895 | -0.12569 | 0.053158 | -0.3324 | -0.12924 | 0.15487 | 0.069997 | 0.4024 | 0.057678 | -0.099372 | 122.9709 | 122.8891 | 123.068 | 65.4934 | -123.1149 | 122.8856 | 123.0725 | 122.9155 | 63.551 | -123.3472
1039.7969 | 123.1567 | -66.4673 | 56.5201 | -0.0057996 | -0.00969 | 0.00082041 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.058452 | 0.015925 | 0.059073 | -66.4268 | -1.0883 | -66.4805 | 56.467 | 56.3715 | 56.5549 | -66.604 | -66.349 | -3.0353 | -66.4431 | 56.3771 | 56.564 | 56.4024 | -66.8455 | -0.1367 | -0.053058 | 0.040503 | -0.01318 | 0.12352 | -0.14858 | 0.034847 | -0.37818 | -0.14297 | 0.11825 | 0.02422 | 0.4024 | 0.043945 | -0.11768 | 122.9343 | 122.8388 | 123.0222 | 65.379 | -123.1241 | 122.8444 | 123.0313 | 122.8697 | 63.432 | -123.3655
1040.7969 | 123.1155 | -66.4948 | 56.5201 | -0.013431 | -0.0099038 | 0.0010342 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | -0.00039093 | 0.0011068 | 0.058666 | 0.015498 | 0.058646 | -66.4268 | -1.1478 | -66.4805 | 56.4716 | 56.3898 | 56.5687 | -66.604 | -66.3399 | -3.0857 | -66.4248 | 56.3817 | 56.564 | 56.2971 | -66.8363 | -0.10924 | -0.04848 | 0.067969 | 0.014286 | 0.12352 | -0.13027 | 0.048582 | -0.34155 | -0.1384 | 0.15487 | 0.070001 | 0.41156 | 0.043945 | -0.22299 | 122.9664 | 122.8846 | 123.0634 | 65.3469 | -123.1241 | 122.8764 | 123.0588 | 122.7918 | 63.4091 | -123.3564
1041.7969 | 123.1659 | -66.4673 | 56.5338 | -0.0057996 | -0.00969 | 0.0010342 | 0.055797 | -0.0024807 | 0.061514 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.015711 | 0.059073 | -66.4222 | -1.2302 | -66.4759 | 56.4762 | 56.399 | 56.5687 | -66.5994 | -66.3353 | -3.1406 | -66.4248 | 56.3908 | 56.5778 | 56.407 | -66.8363 | -0.13213 | -0.057633 | 0.045081 | -0.008601 | 0.12352 | -0.13484 | 0.03485 | -0.36902 | -0.14297 | 0.13198 | 0.042535 | 0.41156 | 0.043949 | -0.12684 | 122.9435 | 122.8663 | 123.0359 | 65.237 | -123.1332 | 122.8581 | 123.045 | 122.8743 | 63.3266 | -123.3701
1042.7969 | 123.1293 | -66.5176 | 56.5384 | -0.0057996 | -0.010117 | 0.00082041 | 0.055797 | -0.0024807 | 0.061514 | -0.001755 | -0.00060453 | 0.0011068 | 0.058666 | 0.015925 | 0.059287 | -66.4085 | -1.2943 | -66.4713 | 56.4853 | 56.399 | 56.5824 | -66.5994 | -66.3261 | -3.2002 | -66.411 | 56.3908 | 56.5823 | 56.352 | -66.8271 | -0.081771 | -0.053055 | 0.10917 | 0.046331 | 0.1281 | -0.13942 | 0.044008 | -0.30951 | -0.14755 | 0.1915 | 0.10663 | 0.41613 | 0.04395 | -0.18636 | 123.003 | 122.9166 | 123.1 | 65.2233 | -123.1378 | 122.9085 | 123.1 | 122.8697 | 63.3175 | -123.3655
1043.7969 | 123.1476 | -66.4948 | 56.5659 | 0.0018314 | -0.00969 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | 0.0058755 | -0.00017733 | 0.00089321 | 0.058238 | 0.015925 | 0.058859 | -66.3993 | -1.3676 | -66.4667 | 56.4945 | 56.4081 | 56.587 | -66.5903 | -66.3124 | -3.2505 | -66.4064 | 56.3908 | 56.5869 | 56.3887 | -66.8271 | -0.095501 | -0.071364 | 0.095439 | 0.028021 | 0.12352 | -0.15773 | 0.021121 | -0.3324 | -0.17502 | 0.18234 | 0.088315 | 0.42071 | 0.021062 | -0.1772 | 122.9892 | 122.9029 | 123.0817 | 65.1272 | -123.1561 | 122.8856 | 123.0817 | 122.8834 | 63.2442 | -123.393
1044.7969 | 123.111 | -66.5085 | 56.5704 | 0.0018314 | -0.010117 | 0.00082041 | 0.056011 | -0.0029079 | 0.061727 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058238 | 0.015711 | 0.058859 | -66.3856 | -1.4134 | -66.4438 | 56.4991 | 56.4127 | 56.6007 | -66.5765 | -66.3078 | -3.3375 | -66.3881 | 56.4092 | 56.5915 | 56.3887 | -66.8134 | -0.068031 | -0.071363 | 0.12291 | 0.064646 | 0.13268 | -0.15773 | 0.030279 | -0.30493 | -0.16128 | 0.20066 | 0.12036 | 0.42529 | 0.021063 | -0.18177 | 123.0076 | 122.9212 | 123.1092 | 65.0951 | -123.147 | 122.9176 | 123.1 | 122.8971 | 63.171 | -123.3838
1045.7969 | 123.1293 | -66.4444 | 56.5475 | 0.0094624 | -0.00969 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.015711 | 0.058859 | -66.3764 | -1.4912 | -66.4484 | 56.5082 | 56.4264 | 56.6007 | -66.5719 | -66.2987 | -3.4154 | -66.3927 | 56.4183 | 56.6007 | 56.4573 | -66.8088 | -0.12754 | -0.039318 | 0.067977 | -0.00402 | 0.12352 | -0.1211 | 0.053168 | -0.36444 | -0.12923 | 0.14573 | 0.051698 | 0.41613 | 0.053109 | -0.090205 | 122.9526 | 122.8708 | 123.0451 | 64.9532 | -123.1195 | 122.8627 | 123.0451 | 122.9017 | 63.029 | -123.3564
1046.7969 | 123.0881 | -66.4673 | 56.5659 | 0.0018314 | -0.0094764 | 0.00060681 | 0.055797 | -0.0022669 | 0.0613 | -0.001755 | -0.00017733 | 0.0011068 | 0.058666 | 0.015925 | 0.059287 | -66.3764 | -1.5553 | -66.4438 | 56.5174 | 56.4356 | 56.6007 | -66.5674 | -66.2804 | -3.4932 | -66.379 | 56.4275 | 56.6052 | 56.3749 | -66.7997 | -0.10007 | -0.048472 | 0.090865 | 0.023447 | 0.12352 | -0.13025 | 0.034857 | -0.33239 | -0.13839 | 0.18693 | 0.088322 | 0.42071 | 0.039377 | -0.19093 | 122.9847 | 122.9029 | 123.068 | 64.912 | -123.1332 | 122.8948 | 123.0725 | 122.8422 | 62.9741 | -123.3655
1047.7969 | 123.1384 | -66.4444 | 56.5704 | 0.0018314 | -0.0099038 | 0.00060681 | 0.055797 | -0.0024807 | 0.061941 | 0.013506 | -0.00039093 | 0.0011068 | 0.058452 | 0.015711 | 0.059073 | -66.3673 | -1.6057 | -66.4255 | 56.522 | 56.4493 | 56.6144 | -66.549 | -66.2712 | -3.5481 | -66.3744 | 56.432 | 56.6144 | 56.4253 | -66.7951 | -0.10465 | -0.048471 | 0.077134 | 0.018872 | 0.12352 | -0.12109 | 0.044014 | -0.3507 | -0.13839 | 0.1732 | 0.070012 | 0.42071 | 0.043956 | -0.14514 | 122.9664 | 122.8937 | 123.0588 | 64.8387 | -123.1195 | 122.8764 | 123.0588 | 122.8697 | 62.8963 | -123.3655
1048.7969 | 123.143 | -66.4352 | 56.5842 | 0.0018314 | -0.00969 | 0.00060681 | 0.056011 | -0.0029079 | 0.062155 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058452 | 0.015711 | 0.059073 | -66.3535 | -1.656 | -66.4209 | 56.5265 | 56.4448 | 56.619 | -66.5445 | -66.262 | -3.658 | -66.3652 | 56.4366 | 56.6144 | 56.4757 | -66.7859 | -0.10922 | -0.057625 | 0.081714 | 0.014295 | 0.12352 | -0.13941 | 0.034861 | -0.3507 | -0.14754 | 0.1732 | 0.070015 | 0.42071 | 0.030224 | -0.10851 | 122.9618 | 122.88 | 123.0543 | 64.7792 | -123.1286 | 122.8719 | 123.0496 | 122.9109 | 62.7772 | -123.3701
1049.7969 | 123.1201 | -66.4261 | 56.5842 | -0.0057996 | -0.010117 | 0.00060681 | 0.055797 | -0.0026943 | 0.061941 | -0.001755 | -0.00081813 | 0.00089321 | 0.058452 | 0.016352 | 0.059073 | -66.3489 | -1.711 | -66.4118 | 56.5357 | 56.4722 | 56.6282 | -66.5445 | -66.2575 | -3.7404 | -66.3561 | 56.4458 | 56.6281 | 56.4894 | -66.7768 | -0.11838 | -0.048468 | 0.077137 | 0.014296 | 0.13267 | -0.11193 | 0.044018 | -0.3507 | -0.13838 | 0.16862 | 0.070016 | 0.42071 | 0.04396 | -0.094776 | 122.9618 | 122.8983 | 123.0543 | 64.7151 | -123.1286 | 122.8719 | 123.0542 | 122.9155 | 62.6856 | -123.3609
1050.7969 | 123.143 | -66.4261 | 56.5704 | -0.0057996 | -0.00969 | 0.00082041 | 0.056224 | -0.0029079 | 0.061727 | -0.001755 | -0.00060453 | 0.00067941 | 0.058452 | 0.015925 | 0.058859 | -66.3352 | -1.743 | -66.3981 | 56.5449 | 56.4722 | 56.6328 | -66.5307 | -66.2483 | -3.832 | -66.3561 | 56.4595 | 56.6327 | 56.5031 | -66.7722 | -0.10464 | -0.025579 | 0.090872 | 0.028031 | 0.13267 | -0.0982 | 0.062329 | -0.34612 | -0.11092 | 0.17778 | 0.070016 | 0.41613 | 0.06227 | -0.067308 | 122.9709 | 122.8983 | 123.0589 | 64.683 | -123.1012 | 122.8856 | 123.0588 | 122.9292 | 62.5941 | -123.3426
1051.7969 | 123.143 | -66.4307 | 56.5933 | -0.021062 | -0.00969 | 0.00082041 | 0.056011 | -0.0026943 | 0.061514 | -0.0093855 | -0.00060453 | 0.0011068 | 0.058666 | 0.016139 | 0.058859 | -66.3352 | -1.8026 | -66.4026 | 56.5449 | 56.4768 | 56.6328 | -66.5353 | -66.2437 | -3.8687 | -66.3469 | 56.4504 | 56.6373 | 56.4985 | -66.763 | -0.10464 | -0.048467 | 0.09545 | 0.02803 | 0.13267 | -0.11651 | 0.039441 | -0.33238 | -0.14296 | 0.18694 | 0.083752 | 0.41613 | 0.043961 | -0.094774 | 122.9755 | 122.9075 | 123.0634 | 64.6281 | -123.1286 | 122.881 | 123.0679 | 122.9292 | 62.562 | -123.3564
1052.7969 | 123.143 | -66.4078 | 56.6025 | 0.0094624 | -0.0099038 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00017733 | 0.0011068 | 0.058452 | 0.015711 | 0.059073 | -66.3261 | -1.8712 | -66.3935 | 56.5494 | 56.4768 | 56.6511 | -66.5216 | -66.2391 | -3.9556 | -66.3332 | 56.4641 | 56.6464 | 56.4528 | -66.7585 | -0.11379 | -0.053044 | 0.081719 | 0.014299 | 0.12809 | -0.12566 | 0.0486 | -0.35069 | -0.13838 | 0.16863 | 0.0746 | 0.42529 | 0.043963 | -0.14972 | 122.9572 | 122.8846 | 123.0589 | 64.5365 | -123.124 | 122.8719 | 123.0542 | 122.8605 | 62.4521 | -123.3609
1053.7969 | 123.1842 | -66.3849 | 56.6254 | -0.0057996 | -0.0099038 | 0.00060681 | 0.056011 | -0.0024807 | 0.061514 | 0.0058755 | -0.00039093 | 0.0011068 | 0.058452 | 0.015925 | 0.059073 | -66.3123 | -1.8987 | -66.3843 | 56.5586 | 56.4951 | 56.6557 | -66.517 | -66.2254 | -4.0655 | -66.324 | 56.4687 | 56.651 | 56.5031 | -66.7585 | -0.1321 | -0.066775 | 0.072566 | 0.000567 | 0.13267 | -0.13024 | 0.030291 | -0.37358 | -0.15669 | 0.15948 | 0.060869 | 0.43445 | 0.025654 | -0.12224 | 122.9435 | 122.88 | 123.0405 | 64.4862 | -123.1424 | 122.8536 | 123.0359 | 122.888 | 62.3194 | -123.3838
1054.7969 | 123.1018 | -66.4124 | 56.6345 | -0.0057996 | -0.00969 | 0.00082041 | 0.056224 | -0.0031215 | 0.061727 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058238 | 0.016139 | 0.058859 | -66.2986 | -1.9262 | -66.366 | 56.5677 | 56.5089 | 56.6602 | -66.5078 | -66.2025 | -4.1067 | -66.3149 | 56.4687 | 56.6648 | 56.4985 | -66.7447 | -0.095477 | -0.066774 | 0.11377 | 0.046346 | 0.14182 | -0.12565 | 0.025714 | -0.33238 | -0.16584 | 0.20984 | 0.097493 | 0.42987 | 0.030234 | -0.13597 | 122.9801 | 122.9212 | 123.0726 | 64.4862 | -123.1424 | 122.881 | 123.0771 | 122.9109 | 62.3056 | -123.3793
1055.7969 | 123.1338 | -66.3757 | 56.6299 | -0.0057996 | -0.010117 | 0.00039321 | 0.055797 | -0.0024807 | 0.061086 | -0.001755 | -0.00060453 | 0.00089321 | 0.058452 | 0.016352 | 0.058859 | -66.2849 | -1.9857 | -66.3614 | 56.5723 | 56.5089 | 56.6694 | -66.5033 | -66.1888 | -4.1937 | -66.3149 | 56.4824 | 56.6648 | 56.4985 | -66.7402 | -0.12752 | -0.057618 | 0.09088 | 0.014303 | 0.14182 | -0.12108 | 0.039449 | -0.36442 | -0.14753 | 0.18695 | 0.060871 | 0.42529 | 0.034811 | -0.1314 | 122.9481 | 122.8846 | 123.0451 | 64.39 | -123.1332 | 122.8581 | 123.0405 | 122.8743 | 62.182 | -123.3701
1056.7969 | 123.1155 | -66.3757 | 56.6528 | -0.013431 | -0.0099038 | 0.00082041 | 0.055797 | -0.0026943 | 0.061941 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058452 | 0.016139 | 0.059073 | -66.2849 | -2.0086 | -66.3569 | 56.5815 | 56.4997 | 56.6786 | -66.4895 | -66.1842 | -4.2991 | -66.2965 | 56.4961 | 56.6785 | 56.5169 | -66.7356 | -0.11378 | -0.071349 | 0.09088 | 0.018881 | 0.13266 | -0.15312 | 0.025718 | -0.35984 | -0.15668 | 0.19153 | 0.079185 | 0.43903 | 0.025659 | -0.13597 | 122.9572 | 122.8754 | 123.0543 | 64.3671 | -123.1423 | 122.8719 | 123.0542 | 122.8926 | 62.0767 | -123.3884
1057.7969 | 123.1201 | -66.3849 | 56.6574 | 0.0018314 | -0.0099038 | 0.00039321 | 0.055797 | -0.0022669 | 0.0613 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.016352 | 0.058859 | -66.2665 | -2.0681 | -66.3431 | 56.5952 | 56.5226 | 56.6877 | -66.4895 | -66.1705 | -4.386 | -66.2874 | 56.5007 | 56.6831 | 56.5443 | -66.7218 | -0.10463 | -0.062192 | 0.11835 | 0.041772 | 0.1464 | -0.13481 | 0.030297 | -0.33695 | -0.15668 | 0.21442 | 0.097499 | 0.43445 | 0.02566 | -0.11308 | 122.9801 | 122.9075 | 123.0726 | 64.3168 | -123.1469 | 122.8856 | 123.068 | 122.9292 | 61.9988 | -123.3792
1058.7969 | 123.1384 | -66.3666 | 56.6299 | -0.0057996 | -0.0099038 | 0.00060681 | 0.055583 | -0.0026943 | 0.061514 | -0.0093855 | -0.00060453 | 0.0013204 | 0.058452 | 0.015925 | 0.059073 | -66.2711 | -2.1093 | -66.3294 | 56.5952 | 56.5226 | 56.6923 | -66.4712 | -66.1659 | -4.4639 | -66.2828 | 56.5145 | 56.6922 | 56.4802 | -66.7173 | -0.10462 | -0.034726 | 0.09546 | 0.037196 | 0.14182 | -0.10734 | 0.062342 | -0.35068 | -0.11548 | 0.20069 | 0.083767 | 0.43445 | 0.062283 | -0.14971 | 122.9618 | 122.8892 | 123.0589 | 64.2572 | -123.1011 | 122.881 | 123.0588 | 122.8468 | 61.9027 | -123.3472
1059.7969 | 123.1567 | -66.3849 | 56.6666 | 0.0094624 | -0.00969 | 0.00060681 | 0.055583 | -0.0026943 | 0.061727 | -0.001755 | -0.00060453 | 0.0011068 | 0.058666 | 0.015925 | 0.059073 | -66.2528 | -2.1505 | -66.3294 | 56.6044 | 56.5226 | 56.706 | -66.4758 | -66.1522 | -4.5188 | -66.2691 | 56.5099 | 56.6968 | 56.5214 | -66.7127 | -0.090891 | -0.06219 | 0.13209 | 0.055507 | 0.1464 | -0.14396 | 0.039456 | -0.32779 | -0.15668 | 0.23274 | 0.11581 | 0.4436 | 0.030241 | -0.14512 | 122.9893 | 122.9075 | 123.0909 | 64.2344 | -123.1423 | 122.8948 | 123.0817 | 122.9063 | 61.8661 | -123.3792
1060.7969 | 123.1018 | -66.3666 | 56.6757 | -0.013431 | -0.010117 | 0.00082041 | 0.056224 | -0.0022669 | 0.061514 | -0.001755 | -0.00060453 | 0.0011068 | 0.058238 | 0.015925 | 0.059073 | -66.2391 | -2.1597 | -66.3202 | 56.6135 | 56.5318 | 56.7152 | -66.4666 | -66.1476 | -4.6104 | -66.2645 | 56.5236 | 56.7151 | 56.4665 | -66.7081 | -0.10004 | -0.062189 | 0.12751 | 0.046352 | 0.1464 | -0.14396 | 0.039459 | -0.34152 | -0.1521 | 0.219 | 0.10208 | 0.4436 | 0.0394 | -0.20922 | 122.9801 | 122.8983 | 123.0818 | 64.2069 | -123.1423 | 122.8902 | 123.0817 | 122.8331 | 61.7562 | -123.3838
1061.7969 | 123.1201 | -66.3528 | 56.6849 | 0.0018314 | -0.00969 | 0.0010342 | 0.056011 | -0.0029079 | 0.061941 | -0.001755 | -0.00017733 | 0.0013204 | 0.058452 | 0.016139 | 0.058646 | -66.2345 | -2.233 | -66.3156 | 56.6227 | 56.518 | 56.7198 | -66.462 | -66.1293 | -4.6791 | -66.2553 | 56.5328 | 56.7105 | 56.5306 | -66.6944 | -0.1092 | -0.062187 | 0.11835 | 0.037198 | 0.1464 | -0.16685 | 0.034882 | -0.34152 | -0.1521 | 0.22358 | 0.097506 | 0.43903 | 0.025666 | -0.15428 | 122.9755 | 122.8709 | 123.0726 | 64.1199 | -123.1469 | 122.8856 | 123.0634 | 122.8834 | 61.6738 | -123.3792
1062.7969 | 123.111 | -66.3574 | 56.6483 | 0.0018314 | -0.00969 | 0.00017941 | 0.056224 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.0013204 | 0.058238 | 0.015711 | 0.059073 | -66.2299 | -2.265 | -66.3065 | 56.6181 | 56.5318 | 56.7106 | -66.4529 | -66.1293 | -4.7707 | -66.2508 | 56.5282 | 56.7197 | 56.4985 | -66.6944 | -0.095462 | -0.030144 | 0.12751 | 0.050932 | 0.14639 | -0.11649 | 0.062346 | -0.33694 | -0.12006 | 0.22816 | 0.10666 | 0.4436 | 0.071445 | -0.14971 | 122.9755 | 122.8892 | 123.068 | 64.0924 | -123.1011 | 122.8856 | 123.0771 | 122.856 | 61.5868 | -123.3426
1063.7969 | 123.1201 | -66.33 | 56.694 | -0.0057996 | -0.0099038 | 0.00082041 | 0.055797 | -0.0026943 | 0.061514 | 0.0058755 | -0.00017733 | 0.0011068 | 0.058452 | 0.016139 | 0.058859 | -66.2208 | -2.3016 | -66.2973 | 56.6364 | 56.5363 | 56.7289 | -66.4483 | -66.1109 | -4.8668 | -66.2462 | 56.5419 | 56.7243 | 56.5901 | -66.6898 | -0.11835 | -0.057608 | 0.1092 | 0.032623 | 0.15097 | -0.15769 | 0.034883 | -0.35983 | -0.1521 | 0.21901 | 0.083775 | 0.4436 | 0.030246 | -0.10391 | 122.9664 | 122.8663 | 123.0589 | 64.0283 | -123.1423 | 122.8719 | 123.0542 | 122.9201 | 61.4631 | -123.3838
1064.7969 | 123.3078 | -66.3071 | 56.6025 | -0.0057996 | -0.0094764 | 0.00060681 | 0.056652 | -0.0024807 | 0.061514 | -0.0093855 | -0.00039093 | 0.001534 | 0.058238 | 0.016352 | 0.058859 | -66.2116 | -2.3199 | -66.2882 | 56.6318 | 56.5363 | 56.7381 | -66.4254 | -66.1018 | -4.9309 | -66.2324 | 56.5419 | 56.7197 | 56.526 | -66.676 | -0.11834 | 0.029367 | 0.09547 | 0.018891 | 0.13723 | -0.066138 | 0.13559 | -0.36898 | -0.060546 | 0.20528 | 0.074623 | 0.4436 | 0.11722 | -0.076458 | 122.9389 | 122.8434 | 123.0451 | 63.9871 | -123.0279 | 122.849 | 123.0268 | 122.8331 | 61.3762 | -123.2785
1065.7969 | 123.111 | -66.3254 | 56.7215 | 0.0018314 | -0.0099038 | 0.00082041 | 0.056224 | -0.0024807 | 0.061514 | 0.0058755 | -0.00081813 | 0.0013204 | 0.058452 | 0.015925 | 0.058646 | -66.207 | -2.352 | -66.2744 | 56.6364 | 56.5592 | 56.7381 | -66.4346 | -66.0926 | -5.0179 | -66.2233 | 56.5511 | 56.7334 | 56.5535 | -66.6623 | -0.10919 | -0.085074 | 0.11836 | 0.050936 | 0.16013 | -0.16226 | 0.016575 | -0.33693 | -0.17041 | 0.23275 | 0.10209 | 0.43902 | 0.011937 | -0.16801 | 122.9618 | 122.8846 | 123.0635 | 63.9734 | -123.1561 | 122.8765 | 123.0588 | 122.8789 | 61.3075 | -123.3838
1066.7969 | 123.1567 | -66.3116 | 56.7032 | 0.0018314 | -0.0099038 | 0.00060681 | 0.056224 | -0.0026943 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.016139 | 0.059073 | -66.1979 | -2.4115 | -66.2653 | 56.6502 | 56.5455 | 56.7426 | -66.4208 | -66.0789 | -5.0912 | -66.205 | 56.5602 | 56.7426 | 56.5626 | -66.6577 | -0.10919 | -0.053028 | 0.11378 | 0.046361 | 0.15555 | -0.15769 | 0.039464 | -0.34609 | -0.14294 | 0.23275 | 0.10667 | 0.45276 | 0.039406 | -0.14054 | 122.9618 | 122.8571 | 123.0543 | 63.9001 | -123.124 | 122.8719 | 123.0542 | 122.8743 | 61.2205 | -123.3609
1067.7969 | 123.1613 | -66.3116 | 56.7352 | -0.0057996 | -0.010117 | 0.00060681 | 0.055797 | -0.0029079 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.058666 | 0.015925 | 0.059287 | -66.1841 | -2.4207 | -66.2699 | 56.6593 | 56.5684 | 56.7564 | -66.4208 | -66.0652 | -5.1827 | -66.2004 | 56.574 | 56.7517 | 56.5993 | -66.6577 | -0.10919 | -0.075914 | 0.12752 | 0.041782 | 0.15097 | -0.16684 | 0.021157 | -0.34609 | -0.16125 | 0.24649 | 0.11125 | 0.45734 | 0.01652 | -0.13595 | 122.971 | 122.88 | 123.068 | 63.891 | -123.1561 | 122.8856 | 123.0634 | 122.9109 | 61.1289 | -123.393
1068.7969 | 123.1476 | -66.3116 | 56.6895 | 0.0094624 | -0.0099038 | 0.00082041 | 0.055797 | -0.0022669 | 0.061514 | -0.0093855 | -0.00039093 | 0.001534 | 0.058452 | 0.016139 | 0.058859 | -66.175 | -2.4802 | -66.2561 | 56.6685 | 56.6004 | 56.761 | -66.4208 | -66.056 | -5.2789 | -66.1958 | 56.5831 | 56.7609 | 56.6176 | -66.6532 | -0.10919 | -0.020981 | 0.13667 | 0.055517 | 0.1647 | -0.089008 | 0.071512 | -0.34151 | -0.10631 | 0.25565 | 0.11583 | 0.45734 | 0.071453 | -0.071861 | 122.9801 | 122.9121 | 123.0726 | 63.8314 | -123.1103 | 122.8948 | 123.0726 | 122.9292 | 61.0328 | -123.3426
1069.7969 | 123.1018 | -66.2796 | 56.7261 | -0.0057996 | -0.010117 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | 0.0058755 | -0.00017733 | 0.0011068 | 0.058666 | 0.015925 | 0.059073 | -66.1521 | -2.4894 | -66.2378 | 56.6822 | 56.5821 | 56.7747 | -66.4025 | -66.0423 | -5.3659 | -66.1821 | 56.5831 | 56.7746 | 56.5077 | -66.644 | -0.12291 | -0.043867 | 0.12752 | 0.041786 | 0.1647 | -0.14394 | 0.048627 | -0.36439 | -0.14293 | 0.23734 | 0.097523 | 0.46192 | 0.048568 | -0.21837 | 122.9618 | 122.8617 | 123.0543 | 63.7902 | -123.1286 | 122.8627 | 123.0542 | 122.7873 | 60.9137 | -123.3701
1070.7969 | 123.1247 | -66.2888 | 56.7307 | 0.0018314 | -0.0099038 | 0.00039321 | 0.056011 | -0.0024807 | 0.061514 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058452 | 0.015711 | 0.059073 | -66.1567 | -2.5397 | -66.2424 | 56.6822 | 56.605 | 56.7793 | -66.3888 | -66.0285 | -5.4025 | -66.1729 | 56.5969 | 56.7792 | 56.5947 | -66.6257 | -0.10002 | -0.048445 | 0.1321 | 0.046363 | 0.14638 | -0.12563 | 0.048627 | -0.33692 | -0.13378 | 0.26023 | 0.11584 | 0.45276 | 0.048569 | -0.13595 | 122.971 | 122.8938 | 123.068 | 63.749 | -123.1194 | 122.8856 | 123.068 | 122.8835 | 60.8862 | -123.3563
1071.7969 | 123.143 | -66.2888 | 56.7535 | -0.0057996 | -0.0094764 | 0.00039321 | 0.055797 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058666 | 0.016139 | 0.059073 | -66.1383 | -2.5718 | -66.2287 | 56.7005 | 56.5913 | 56.7976 | -66.3934 | -66.0102 | -5.517 | -66.1592 | 56.5969 | 56.7792 | 56.6176 | -66.6257 | -0.1046 | -0.053019 | 0.15041 | 0.060098 | 0.1647 | -0.16225 | 0.044054 | -0.33692 | -0.15667 | 0.27855 | 0.12957 | 0.4665 | 0.025681 | -0.13595 | 122.9893 | 122.88 | 123.0864 | 63.717 | -123.1469 | 122.8856 | 123.068 | 122.9063 | 60.7718 | -123.3792
1072.7969 | 123.1934 | -66.2613 | 56.7169 | 0.0018314 | -0.00969 | 0.00082041 | 0.056438 | -0.0022669 | 0.061514 | -0.017016 | -0.00039093 | 0.00089321 | 0.058452 | 0.016139 | 0.058859 | -66.1338 | -2.6084 | -66.2195 | 56.6914 | 56.5913 | 56.7884 | -66.3842 | -66.0102 | -5.604 | -66.1546 | 56.606 | 56.7884 | 56.6267 | -66.6257 | -0.12291 | -0.025555 | 0.12753 | 0.041789 | 0.1647 | -0.12563 | 0.071517 | -0.36439 | -0.11089 | 0.25108 | 0.10668 | 0.47107 | 0.071459 | -0.09017 | 122.9527 | 122.8526 | 123.0497 | 63.6529 | -123.1011 | 122.8673 | 123.0497 | 122.888 | 60.6573 | -123.3426
1073.7969 | 123.1293 | -66.2521 | 56.7581 | -0.0057996 | -0.00969 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058025 | 0.016352 | 0.058859 | -66.1109 | -2.645 | -66.2058 | 56.7005 | 56.5959 | 56.8068 | -66.375 | -66.0056 | -5.7047 | -66.1409 | 56.6152 | 56.7975 | 56.5443 | -66.6074 | -0.12291 | -0.057597 | 0.14126 | 0.046368 | 0.16927 | -0.16225 | 0.048633 | -0.35523 | -0.14293 | 0.2465 | 0.11127 | 0.46649 | 0.039417 | -0.21378 | 122.9527 | 122.848 | 123.0589 | 63.6071 | -123.1332 | 122.8673 | 123.0497 | 122.7965 | 60.5474 | -123.3655
1074.7969 | 123.1567 | -66.2704 | 56.7627 | -0.013431 | -0.0099038 | 0.00039321 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.058452 | 0.015925 | 0.058859 | -66.1063 | -2.7229 | -66.2012 | 56.7143 | 56.6233 | 56.8022 | -66.3705 | -65.9827 | -5.8009 | -66.1363 | 56.6243 | 56.8067 | 56.5947 | -66.6028 | -0.10002 | -0.048439 | 0.16415 | 0.069258 | 0.16927 | -0.13936 | 0.039477 | -0.33234 | -0.13835 | 0.28771 | 0.13416 | 0.46649 | 0.043997 | -0.168 | 122.9847 | 122.8938 | 123.0726 | 63.5476 | -123.1332 | 122.8948 | 123.0771 | 122.8651 | 60.4696 | -123.3655
1075.7969 | 123.1155 | -66.2659 | 56.7993 | -0.0057996 | -0.010331 | 0.00060681 | 0.055797 | -0.0026943 | 0.061514 | -0.001755 | -0.00060453 | 0.00089321 | 0.058452 | 0.016352 | 0.058859 | -66.0926 | -2.7549 | -66.1966 | 56.7188 | 56.6233 | 56.8205 | -66.3521 | -65.969 | -5.8833 | -66.1226 | 56.6335 | 56.8204 | 56.6634 | -66.5982 | -0.086279 | -0.080482 | 0.17331 | 0.069258 | 0.15554 | -0.17598 | 0.021171 | -0.33234 | -0.16581 | 0.29686 | 0.14331 | 0.47565 | 0.021112 | -0.13594 | 122.9847 | 122.8892 | 123.0864 | 63.511 | -123.1515 | 122.8994 | 123.0863 | 122.9292 | 60.3826 | -123.3975
1076.7969 | 123.1476 | -66.2613 | 56.781 | -0.013431 | -0.010117 | 0.00060681 | 0.056438 | -0.0024807 | 0.061727 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058452 | 0.016139 | 0.059073 | -66.0788 | -2.7641 | -66.1875 | 56.7326 | 56.6371 | 56.8205 | -66.3476 | -65.9644 | -6.0023 | -66.1134 | 56.6335 | 56.8204 | 56.5901 | -66.5845 | -0.086277 | -0.048437 | 0.18247 | 0.073837 | 0.16011 | -0.14393 | 0.039481 | -0.32318 | -0.1475 | 0.29687 | 0.14789 | 0.47107 | 0.039422 | -0.19088 | 122.9939 | 122.8984 | 123.0818 | 63.4972 | -123.1286 | 122.8948 | 123.0817 | 122.8514 | 60.259 | -123.3655
1077.7969 | 123.1064 | -66.2155 | 56.7993 | 0.0018314 | -0.010331 | 0.00017941 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | -0.00081813 | 0.00089321 | 0.058666 | 0.016139 | 0.058859 | -66.0742 | -2.8007 | -66.1783 | 56.7326 | 56.6554 | 56.8342 | -66.343 | -65.9461 | -6.1214 | -66.1088 | 56.6427 | 56.825 | 56.6542 | -66.5845 | -0.12748 | -0.066747 | 0.14127 | 0.037217 | 0.16469 | -0.14392 | 0.034906 | -0.36896 | -0.15666 | 0.2694 | 0.1067 | 0.47565 | 0.025691 | -0.14509 | 122.9481 | 122.8709 | 123.0497 | 63.4148 | -123.1423 | 122.8582 | 123.0405 | 122.8697 | 60.0941 | -123.3838
1078.7969 | 123.23 | -66.2018 | 56.7398 | -0.021062 | -0.010117 | 0.00060681 | 0.056224 | -0.0024807 | 0.0613 | -0.001755 | -0.00039093 | 0.0013204 | 0.058238 | 0.016352 | 0.058859 | -66.0742 | -2.8419 | -66.1737 | 56.7326 | 56.66 | 56.8342 | -66.3338 | -65.9415 | -6.213 | -66.0951 | 56.6381 | 56.8296 | 56.6817 | -66.5799 | -0.13205 | -0.007238 | 0.12754 | 0.028062 | 0.16011 | -0.079836 | 0.094415 | -0.37811 | -0.10173 | 0.26025 | 0.1067 | 0.48481 | 0.089778 | -0.058114 | 122.9344 | 122.8618 | 123.036 | 63.3599 | -123.0736 | 122.8399 | 123.0314 | 122.8835 | 59.9888 | -123.3197
1079.7969 | 123.1155 | -66.2704 | 56.7947 | 0.0094624 | -0.010117 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | -0.00017733 | 0.0013204 | 0.058025 | 0.016566 | 0.059073 | -66.0514 | -2.8968 | -66.16 | 56.7463 | 56.6737 | 56.8525 | -66.3338 | -65.9232 | -6.2771 | -66.0951 | 56.661 | 56.8387 | 56.6954 | -66.5753 | -0.063385 | -0.048434 | 0.21909 | 0.11046 | 0.17385 | -0.12103 | 0.057798 | -0.30487 | -0.13377 | 0.34723 | 0.17536 | 0.48023 | 0.044003 | -0.099311 | 123.0168 | 122.9442 | 123.123 | 63.3736 | -123.1286 | 122.9314 | 123.1092 | 122.9659 | 59.9934 | -123.3701
1080.7969 | 123.1201 | -66.2109 | 56.7993 | -0.021062 | -0.0099038 | 0.00082041 | 0.055583 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058238 | 0.016352 | 0.058859 | -66.0514 | -2.8968 | -66.1554 | 56.7463 | 56.6829 | 56.848 | -66.3201 | -65.9141 | -6.3549 | -66.0768 | 56.6747 | 56.8479 | 56.7137 | -66.5616 | -0.10916 | -0.053011 | 0.15958 | 0.05553 | 0.16469 | -0.11645 | 0.048642 | -0.35064 | -0.12461 | 0.29688 | 0.13417 | 0.48481 | 0.048584 | -0.085573 | 122.9572 | 122.8938 | 123.0589 | 63.3141 | -123.1194 | 122.8856 | 123.0588 | 122.9247 | 59.856 | -123.3609
1081.7969 | 123.1613 | -66.1926 | 56.8222 | -0.0057996 | -0.0099038 | 0.00039321 | 0.056011 | -0.0024807 | 0.061514 | -0.001755 | -0.00081813 | 0.0011068 | 0.058452 | 0.016139 | 0.058859 | -66.0468 | -2.9472 | -66.1508 | 56.7692 | 56.6783 | 56.8617 | -66.3155 | -65.9095 | -6.4739 | -66.0768 | 56.6747 | 56.8525 | 56.7046 | -66.557 | -0.12289 | -0.053008 | 0.14585 | 0.041799 | 0.16469 | -0.14392 | 0.039489 | -0.36437 | -0.1475 | 0.28315 | 0.11586 | 0.48023 | 0.030273 | -0.11762 | 122.9618 | 122.8709 | 123.0543 | 63.2454 | -123.1377 | 122.8673 | 123.0451 | 122.8972 | 59.7187 | -123.3792
1082.8594 | 123.1155 | -66.1743 | 56.8405 | 0.0018314 | -0.010117 | 0.0010342 | 0.055797 | -0.0024807 | 0.061086 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058452 | 0.016566 | 0.059073 | -66.0193 | -2.9655 | -66.1279 | 56.7692 | 56.7012 | 56.8709 | -66.3064 | -65.882 | -6.6159 | -66.0493 | 56.6793 | 56.8616 | 56.6908 | -66.5478 | -0.13204 | -0.071318 | 0.15501 | 0.046379 | 0.17842 | -0.13933 | 0.030336 | -0.37352 | -0.16123 | 0.29231 | 0.12502 | 0.49854 | 0.02112 | -0.14967 | 122.9435 | 122.8755 | 123.0452 | 63.2088 | -123.1469 | 122.8536 | 123.036 | 122.8652 | 59.5584 | -123.3884
1083.7969 | 123.1064 | -66.2064 | 56.813 | 0.0018314 | -0.0099038 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058452 | 0.016566 | 0.059073 | -66.0193 | -3.0067 | -66.1279 | 56.7784 | 56.7058 | 56.8663 | -66.3018 | -65.882 | -6.7349 | -66.0539 | 56.6884 | 56.8662 | 56.7229 | -66.5341 | -0.09542 | -0.034696 | 0.18706 | 0.078423 | 0.17384 | -0.10729 | 0.053224 | -0.32774 | -0.12461 | 0.32435 | 0.15248 | 0.48023 | 0.053165 | -0.090149 | 122.9847 | 122.9121 | 123.0726 | 63.1996 | -123.1148 | 122.8948 | 123.0726 | 122.9293 | 59.4714 | -123.3472
1084.7969 | 123.1613 | -66.188 | 56.8176 | 0.0018314 | -0.010331 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058452 | 0.016139 | 0.059073 | -66.0056 | -3.0663 | -66.1142 | 56.7829 | 56.692 | 56.8846 | -66.2926 | -65.8683 | -6.8402 | -66.0447 | 56.693 | 56.8754 | 56.6863 | -66.5341 | -0.10457 | -0.034695 | 0.18248 | 0.073847 | 0.17842 | -0.1256 | 0.06696 | -0.34605 | -0.1246 | 0.31978 | 0.14333 | 0.48939 | 0.057744 | -0.13136 | 122.971 | 122.8801 | 123.0726 | 63.1218 | -123.1102 | 122.8811 | 123.0634 | 122.8743 | 59.3478 | -123.3517
1085.7969 | 123.0835 | -66.1789 | 56.8588 | -0.0057996 | -0.010331 | 0.00082041 | 0.056224 | -0.0026943 | 0.061727 | 0.0058755 | -0.00060453 | 0.0011068 | 0.058452 | 0.016352 | 0.059073 | -65.9918 | -3.1258 | -66.1096 | 56.7875 | 56.7012 | 56.8983 | -66.2789 | -65.85 | -6.9318 | -66.0264 | 56.7068 | 56.8891 | 56.6359 | -66.5341 | -0.099991 | -0.071316 | 0.18706 | 0.06927 | 0.16926 | -0.15764 | 0.039497 | -0.35521 | -0.15207 | 0.32894 | 0.15249 | 0.5077 | 0.030281 | -0.22292 | 122.9664 | 122.8801 | 123.0772 | 63.0531 | -123.1377 | 122.8857 | 123.068 | 122.8148 | 59.2471 | -123.3929
1086.7969 | 123.2391 | -66.1606 | 56.8222 | 0.0018314 | -0.010331 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00081813 | 0.00089321 | 0.058238 | 0.016352 | 0.059287 | -65.9918 | -3.1487 | -66.105 | 56.7921 | 56.7058 | 56.8892 | -66.2789 | -65.8362 | -7.0188 | -66.0218 | 56.7113 | 56.8937 | 56.6817 | -66.5158 | -0.1183 | -0.030117 | 0.16875 | 0.055537 | 0.17384 | -0.11644 | 0.066961 | -0.35521 | -0.11087 | 0.32436 | 0.13876 | 0.49397 | 0.071481 | -0.14051 | 122.9527 | 122.8663 | 123.0497 | 63.0119 | -123.1011 | 122.8719 | 123.0543 | 122.8423 | 59.1418 | -123.338
1087.7969 | 123.1247 | -66.156 | 56.8634 | 0.0018314 | -0.010117 | 0.00039321 | 0.055797 | -0.0024807 | 0.061514 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.01678 | 0.059073 | -65.9781 | -3.2128 | -66.0913 | 56.8104 | 56.7241 | 56.9029 | -66.2651 | -65.8316 | -7.147 | -66.0127 | 56.7251 | 56.8983 | 56.6954 | -66.5112 | -0.10914 | -0.053001 | 0.17791 | 0.064695 | 0.17384 | -0.13933 | 0.039498 | -0.3552 | -0.13833 | 0.32436 | 0.14334 | 0.49854 | 0.034861 | -0.16797 | 122.9664 | 122.8801 | 123.0589 | 62.9432 | -123.1286 | 122.8811 | 123.0543 | 122.8514 | 59.009 | -123.3746
1088.7969 | 123.1293 | -66.188 | 56.8817 | 0.0018314 | -0.0099038 | 0.00060681 | 0.055583 | -0.0026943 | 0.061727 | -0.001755 | -0.00017733 | 0.00089321 | 0.058666 | 0.01678 | 0.058859 | -65.9644 | -3.2219 | -66.0822 | 56.8196 | 56.7424 | 56.9166 | -66.2651 | -65.8133 | -7.2386 | -65.9944 | 56.7388 | 56.9166 | 56.7092 | -66.5066 | -0.077099 | -0.062155 | 0.22368 | 0.1059 | 0.18299 | -0.13932 | 0.034923 | -0.31858 | -0.14291 | 0.37472 | 0.1937 | 0.51228 | 0.034865 | -0.17255 | 123.0076 | 122.9304 | 123.1047 | 62.9661 | -123.1469 | 122.9269 | 123.1046 | 122.8972 | 58.9495 | -123.3883
1089.7969 | 123.1384 | -66.1652 | 56.8863 | 0.0018314 | -0.010117 | 0.00060681 | 0.055797 | -0.0026943 | 0.0613 | -0.001755 | -0.00039093 | 0.0013204 | 0.058452 | 0.016352 | 0.058859 | -65.9506 | -3.2586 | -66.0684 | 56.8196 | 56.7241 | 56.9258 | -66.2514 | -65.7904 | -7.3668 | -65.9852 | 56.7388 | 56.9257 | 56.7824 | -66.4975 | -0.086251 | -0.066733 | 0.21453 | 0.096742 | 0.18299 | -0.16222 | 0.039502 | -0.33231 | -0.14748 | 0.37473 | 0.17997 | 0.51228 | 0.039444 | -0.10387 | 122.9847 | 122.8892 | 123.091 | 62.9066 | -123.1377 | 122.904 | 123.0909 | 122.9476 | 58.7984 | -123.3838
1090.7969 | 123.1293 | -66.1423 | 56.8726 | 0.0018314 | -0.010331 | 0.00039321 | 0.056438 | -0.0026943 | 0.061727 | -0.0093855 | 3.6274e-05 | 0.00089321 | 0.058666 | 0.016566 | 0.059073 | -65.9461 | -3.2769 | -66.0593 | 56.8333 | 56.7332 | 56.9304 | -66.2468 | -65.7904 | -7.4813 | -65.9852 | 56.7342 | 56.9212 | 56.7733 | -66.4929 | -0.10456 | -0.039265 | 0.19622 | 0.08301 | 0.18757 | -0.13932 | 0.057814 | -0.35062 | -0.13833 | 0.35184 | 0.15708 | 0.5077 | 0.048598 | -0.099294 | 122.9756 | 122.8755 | 123.0726 | 62.8654 | -123.1194 | 122.8765 | 123.0634 | 122.9155 | 58.661 | -123.3655
1091.7969 | 123.1064 | -66.1377 | 56.9046 | -0.0057996 | -0.010117 | 0.00060681 | 0.056224 | -0.0022669 | 0.061514 | -0.0093855 | -0.00039093 | 0.0011068 | 0.058452 | 0.016566 | 0.059073 | -65.9277 | -3.3181 | -66.0501 | 56.8425 | 56.747 | 56.9395 | -66.2377 | -65.7767 | -7.5957 | -65.9623 | 56.748 | 56.9349 | 56.7595 | -66.47 | -0.09998 | -0.062151 | 0.20996 | 0.087589 | 0.18757 | -0.15763 | 0.034928 | -0.33231 | -0.15664 | 0.361 | 0.17539 | 0.5077 | 0.030291 | -0.14507 | 122.9801 | 122.8847 | 123.0772 | 62.8196 | -123.1423 | 122.8857 | 123.0726 | 122.8972 | 58.542 | -123.3746
1092.7969 | 123.2025 | -66.0782 | 56.8542 | -0.0057996 | -0.010117 | 0.00060681 | 0.055797 | -0.0024807 | 0.0613 | 0.0058755 | -0.00039093 | 0.001534 | 0.058452 | 0.016566 | 0.058859 | -65.9277 | -3.3501 | -66.0409 | 56.8516 | 56.7561 | 56.935 | -66.2239 | -65.7721 | -7.7331 | -65.9577 | 56.7525 | 56.9532 | 56.668 | -66.4746 | -0.14575 | -0.002641 | 0.15045 | 0.037236 | 0.18299 | -0.098119 | 0.080704 | -0.39639 | -0.1017 | 0.30607 | 0.12046 | 0.51686 | 0.098959 | -0.18629 | 122.9298 | 122.8343 | 123.0131 | 62.7281 | -123.0782 | 122.8307 | 123.0314 | 122.7461 | 58.3451 | -123.3288
1093.7969 | 123.1522 | -66.1102 | 56.9183 | 0.0018314 | -0.0099038 | 0.00039321 | 0.056011 | -0.0024807 | 0.0613 | -0.0093855 | -0.00060453 | 0.0011068 | 0.058452 | 0.016566 | 0.059287 | -65.914 | -3.4142 | -66.0318 | 56.8516 | 56.7561 | 56.9578 | -66.2285 | -65.7538 | -7.8384 | -65.9486 | 56.7663 | 56.9532 | 56.7595 | -66.4654 | -0.11829 | -0.066728 | 0.19623 | 0.078436 | 0.19672 | -0.16221 | 0.03951 | -0.35519 | -0.15206 | 0.35642 | 0.16166 | 0.51686 | 0.034872 | -0.15881 | 122.9618 | 122.8664 | 123.0681 | 62.696 | -123.1469 | 122.8765 | 123.0634 | 122.8698 | 58.2718 | -123.3838
1094.7969 | 123.1201 | -66.1148 | 56.8863 | -0.013431 | -0.010117 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00017733 | 0.0011068 | 0.058238 | 0.016139 | 0.059287 | -65.8957 | -3.4234 | -66.0226 | 56.8653 | 56.7653 | 56.9578 | -66.2148 | -65.7309 | -7.9666 | -65.9348 | 56.78 | 56.9624 | 56.7687 | -66.4563 | -0.099973 | -0.020949 | 0.21912 | 0.092171 | 0.19214 | -0.121 | 0.071553 | -0.34146 | -0.10628 | 0.3839 | 0.17998 | 0.52144 | 0.076073 | -0.11761 | 122.9802 | 122.8801 | 123.0727 | 62.6914 | -123.1011 | 122.8948 | 123.0772 | 122.8835 | 58.1482 | -123.3426
1095.7969 | 123.1338 | -66.0828 | 56.9229 | 0.0018314 | -0.010117 | 0.00060681 | 0.056011 | -0.0029079 | 0.061514 | 0.013506 | -0.00017733 | 0.0013204 | 0.058238 | 0.016566 | 0.059073 | -65.8911 | -3.4921 | -66.0089 | 56.8745 | 56.7928 | 56.9762 | -66.2056 | -65.7126 | -8.1177 | -65.9211 | 56.7892 | 56.9624 | 56.755 | -66.4517 | -0.12286 | -0.048414 | 0.19165 | 0.073862 | 0.19672 | -0.13015 | 0.053246 | -0.36892 | -0.13374 | 0.37017 | 0.16167 | 0.53059 | 0.039452 | -0.16796 | 122.9573 | 122.8755 | 123.0589 | 62.5907 | -123.1285 | 122.8719 | 123.0451 | 122.8377 | 57.9651 | -123.3746
1096.7969 | 123.1567 | -66.1057 | 56.8863 | -0.021062 | -0.010117 | 0.00060681 | 0.056224 | -0.0026943 | 0.061727 | -0.0093855 | -0.00039093 | 0.0013204 | 0.058238 | 0.016139 | 0.058859 | -65.8728 | -3.5333 | -65.9997 | 56.8837 | 56.8019 | 56.9807 | -66.2056 | -65.6989 | -8.2184 | -65.9119 | 56.7846 | 56.9807 | 56.8191 | -66.4334 | -0.09997 | -0.002636 | 0.23286 | 0.10591 | 0.20588 | -0.084374 | 0.094446 | -0.32772 | -0.1017 | 0.40679 | 0.19372 | 0.52143 | 0.094387 | -0.067241 | 122.9893 | 122.9076 | 123.0864 | 62.5724 | -123.0919 | 122.8902 | 123.0863 | 122.9247 | 57.8872 | -123.3197
1097.7969 | 123.1247 | -66.0873 | 56.9733 | 0.0018314 | -0.010331 | 0.00039321 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.00067941 | 0.058452 | 0.01678 | 0.059073 | -65.8591 | -3.6065 | -65.9906 | 56.8928 | 56.8065 | 56.9899 | -66.1781 | -65.6943 | -8.3924 | -65.9119 | 56.8029 | 56.9853 | 56.8145 | -66.4242 | -0.090808 | -0.080454 | 0.22828 | 0.096752 | 0.18756 | -0.16677 | 0.016628 | -0.33687 | -0.17036 | 0.39306 | 0.17541 | 0.51228 | 0.011991 | -0.15879 | 122.9802 | 122.8938 | 123.0772 | 62.4808 | -123.1514 | 122.8902 | 123.0726 | 122.9018 | 57.6949 | -123.3975
1098.7969 | 123.2208 | -66.0507 | 56.9046 | -0.0057996 | -0.010117 | 0.00060681 | 0.056224 | -0.0026943 | 0.061727 | -0.0093855 | -0.00060453 | 0.0011068 | 0.058452 | 0.016566 | 0.059287 | -65.8499 | -3.6569 | -65.9769 | 56.902 | 56.8248 | 56.9945 | -66.1781 | -65.6668 | -8.5206 | -65.8845 | 56.8075 | 56.999 | 56.7824 | -66.4105 | -0.12743 | -0.002632 | 0.20081 | 0.073866 | 0.2013 | -0.079789 | 0.089871 | -0.35976 | -0.097117 | 0.38391 | 0.16626 | 0.52601 | 0.094391 | -0.12218 | 122.9527 | 122.8755 | 123.0452 | 62.3938 | -123.0828 | 122.8582 | 123.0497 | 122.8331 | 57.5301 | -123.3151
1099.8594 | 123.2391 | -66.0233 | 56.9229 | -0.0057996 | -0.010331 | 0.00082041 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | 3.6274e-05 | 0.00089321 | 0.058238 | 0.016566 | 0.059073 | -65.8362 | -3.7073 | -65.9723 | 56.9111 | 56.834 | 57.0174 | -66.1553 | -65.6531 | -8.6626 | -65.8707 | 56.8304 | 57.0082 | 56.8648 | -66.4151 | -0.132 | -0.011786 | 0.18708 | 0.050979 | 0.18298 | -0.088943 | 0.094453 | -0.3918 | -0.092536 | 0.37018 | 0.15253 | 0.54433 | 0.085238 | -0.058076 | 122.9344 | 122.8572 | 123.0406 | 62.316 | -123.0782 | 122.8536 | 123.0314 | 122.8881 | 57.3607 | -123.338
1100.7969 | 123.1842 | -66.0324 | 56.9458 | -0.013431 | -0.010117 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | -0.00017733 | 0.0011068 | 0.058452 | 0.016352 | 0.059287 | -65.8316 | -3.7485 | -65.9585 | 56.9203 | 56.834 | 57.0174 | -66.1553 | -65.6485 | -8.8045 | -65.8661 | 56.8258 | 57.0127 | 56.8648 | -66.3967 | -0.12284 | -0.025518 | 0.20082 | 0.073869 | 0.19671 | -0.11183 | 0.071565 | -0.36433 | -0.12 | 0.38392 | 0.16626 | 0.53059 | 0.066928 | -0.080964 | 122.9527 | 122.8664 | 123.0498 | 62.2839 | -123.1011 | 122.8582 | 123.0451 | 122.8972 | 57.2279 | -123.3425
1101.7969 | 123.1155 | -66.0187 | 56.9916 | 0.0018314 | -0.010331 | 0.00082041 | 0.055583 | -0.0029079 | 0.061727 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.01678 | 0.059073 | -65.8087 | -3.808 | -65.9585 | 56.9294 | 56.8477 | 57.0265 | -66.1507 | -65.6439 | -8.919 | -65.8524 | 56.835 | 57.0219 | 56.8923 | -66.3967 | -0.132 | -0.062137 | 0.20998 | 0.060136 | 0.19213 | -0.14387 | 0.034947 | -0.37806 | -0.15662 | 0.37476 | 0.16626 | 0.54433 | 0.030309 | -0.099269 | 122.9481 | 122.8664 | 123.0452 | 62.2107 | -123.1423 | 122.8536 | 123.0406 | 122.911 | 57.0997 | -123.3883
1102.7969 | 123.1338 | -66.0553 | 56.9641 | -0.0057996 | -0.010117 | 0.00039321 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058452 | 0.01678 | 0.059073 | -65.8087 | -3.8492 | -65.9402 | 56.9294 | 56.8614 | 57.0311 | -66.1507 | -65.621 | -9.038 | -65.8387 | 56.8395 | 57.031 | 56.9015 | -66.3922 | -0.095377 | -0.034671 | 0.2466 | 0.11507 | 0.21045 | -0.10267 | 0.066991 | -0.33686 | -0.12458 | 0.43428 | 0.21662 | 0.55348 | 0.066933 | -0.062645 | 122.9847 | 122.9167 | 123.0864 | 62.2061 | -123.1148 | 122.8948 | 123.0863 | 122.9568 | 57.0173 | -123.3563
1103.7969 | 123.0789 | -66.037 | 56.9778 | -0.013431 | -0.010331 | 0.00039321 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | -0.00017733 | 0.00089321 | 0.058025 | 0.016566 | 0.058646 | -65.795 | -3.8858 | -65.9265 | 56.9432 | 56.8706 | 57.0357 | -66.1369 | -65.6073 | -9.1708 | -65.8295 | 56.8533 | 57.0356 | 56.8969 | -66.3738 | -0.099951 | -0.034669 | 0.24202 | 0.11049 | 0.21045 | -0.10724 | 0.057837 | -0.33686 | -0.12457 | 0.4297 | 0.20747 | 0.54433 | 0.057778 | -0.080957 | 122.9802 | 122.9076 | 123.0727 | 62.1512 | -123.1148 | 122.8903 | 123.0726 | 122.9339 | 56.8662 | -123.3517
1104.7969 | 123.2391 | -65.9592 | 56.9641 | 0.0018314 | -0.0099038 | 0.00082041 | 0.056438 | -0.0024807 | 0.061514 | 0.0058755 | -0.00039093 | 0.001534 | 0.058238 | 0.01678 | 0.059073 | -65.7767 | -3.9728 | -65.9219 | 56.9569 | 56.8706 | 57.0494 | -66.1278 | -65.589 | -9.3173 | -65.8158 | 56.8624 | 57.0494 | 56.8603 | -66.3693 | -0.16861 | -0.007201 | 0.18252 | 0.037253 | 0.20587 | -0.093509 | 0.085306 | -0.4101 | -0.10168 | 0.3702 | 0.14338 | 0.55348 | 0.085247 | -0.10385 | 122.9161 | 122.8298 | 123.0086 | 61.9863 | -123.0919 | 122.8216 | 123.0085 | 122.8194 | 56.6419 | -123.3334
1105.7969 | 123.1201 | -66.037 | 57.0053 | 0.0018314 | -0.010117 | 0.00039321 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.0011068 | 0.058452 | 0.016352 | 0.059073 | -65.7721 | -4.0094 | -65.9173 | 56.9615 | 56.8843 | 57.054 | -66.1232 | -65.5752 | -9.473 | -65.8158 | 56.8578 | 57.0494 | 56.9198 | -66.3555 | -0.086215 | -0.043821 | 0.26492 | 0.11965 | 0.20587 | -0.12097 | 0.048685 | -0.31854 | -0.14746 | 0.46175 | 0.2212 | 0.53975 | 0.044048 | -0.08553 | 122.9985 | 122.9213 | 123.091 | 62.0275 | -123.1285 | 122.8948 | 123.0863 | 122.9568 | 56.564 | -123.3608
1106.7969 | 123.2391 | -65.9683 | 56.9458 | 0.0018314 | -0.010331 | 0.00039321 | 0.056011 | -0.0022669 | 0.061727 | -0.017016 | -0.00060453 | 0.001534 | 0.058238 | 0.01678 | 0.059287 | -65.7538 | -4.069 | -65.9082 | 56.9615 | 56.8889 | 57.0677 | -66.1095 | -65.5661 | -9.6424 | -65.802 | 56.8762 | 57.0631 | 56.8511 | -66.351 | -0.14114 | 0.015688 | 0.21456 | 0.060144 | 0.20129 | -0.056884 | 0.12193 | -0.38263 | -0.069639 | 0.40225 | 0.16628 | 0.5489 | 0.11729 | -0.0947 | 122.9298 | 122.8572 | 123.0361 | 61.8994 | -123.0553 | 122.8445 | 123.0314 | 122.8194 | 56.3259 | -123.2968
1107.7969 | 123.1247 | -66.0049 | 57.0419 | 0.0018314 | -0.010545 | 0.00039321 | 0.055797 | -0.0022669 | 0.061514 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058666 | 0.016566 | 0.058859 | -65.7492 | -4.1376 | -65.8853 | 56.9752 | 56.8981 | 57.0723 | -66.1049 | -65.5432 | -9.7569 | -65.7792 | 56.8899 | 57.0723 | 56.9152 | -66.3418 | -0.099942 | -0.066707 | 0.25576 | 0.11966 | 0.2196 | -0.14386 | 0.030379 | -0.33685 | -0.15203 | 0.46176 | 0.22579 | 0.56264 | 0.03032 | -0.12673 | 122.9802 | 122.903 | 123.0773 | 61.8673 | -123.1468 | 122.8948 | 123.0772 | 122.9201 | 56.2481 | -123.3837
1108.7969 | 123.1567 | -65.9821 | 57.0328 | -0.013431 | -0.010331 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | -0.001755 | 3.6274e-05 | 0.001534 | 0.058238 | 0.016566 | 0.058859 | -65.7309 | -4.1972 | -65.8853 | 56.9798 | 56.8935 | 57.0769 | -66.0957 | -65.534 | -9.9309 | -65.7792 | 56.8899 | 57.0814 | 56.8786 | -66.3372 | -0.11367 | -0.052974 | 0.25119 | 0.096768 | 0.21044 | -0.13928 | 0.044112 | -0.35516 | -0.14288 | 0.44803 | 0.2029 | 0.55806 | 0.048632 | -0.1542 | 122.9619 | 122.8756 | 123.0589 | 61.7849 | -123.1285 | 122.872 | 123.0635 | 122.8606 | 56.0512 | -123.37
1109.7969 | 123.2208 | -65.9134 | 57.0419 | 0.0018314 | -0.010117 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0013204 | 0.058452 | 0.016993 | 0.058859 | -65.7263 | -4.2659 | -65.8716 | 56.989 | 56.8981 | 57.0815 | -66.0866 | -65.5157 | -10.0499 | -65.7654 | 56.8991 | 57.086 | 56.8694 | -66.3281 | -0.17318 | -0.052972 | 0.1871 | 0.041838 | 0.21502 | -0.14386 | 0.039536 | -0.41467 | -0.14288 | 0.39768 | 0.14798 | 0.56264 | 0.044056 | -0.17252 | 122.9024 | 122.8115 | 122.9949 | 61.6475 | -123.1285 | 122.8124 | 122.9994 | 122.7828 | 55.8635 | -123.37
1110.7969 | 123.2574 | -65.9317 | 57.0053 | 0.0018314 | -0.010331 | 0.00039321 | 0.056224 | -0.0029079 | 0.061941 | -0.0093855 | -0.00017733 | 0.001534 | 0.058452 | 0.01678 | 0.059073 | -65.7126 | -4.3345 | -65.867 | 56.989 | 56.9072 | 57.086 | -66.0774 | -65.5111 | -10.1781 | -65.7517 | 56.9082 | 57.0951 | 56.787 | -66.3235 | -0.14571 | -0.016351 | 0.21915 | 0.064727 | 0.21044 | -0.098077 | 0.080735 | -0.39178 | -0.097098 | 0.42057 | 0.18002 | 0.5718 | 0.089834 | -0.21831 | 122.9207 | 122.8389 | 123.0177 | 61.5972 | -123.0827 | 122.8399 | 123.0268 | 122.7187 | 55.7536 | -123.3288
1111.7969 | 123.1064 | -65.9637 | 57.0694 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0026943 | 0.061514 | -0.001755 | -0.00017733 | 0.0011068 | 0.058238 | 0.016352 | 0.059073 | -65.7034 | -4.4169 | -65.8532 | 57.0119 | 56.8981 | 57.1044 | -66.0774 | -65.4928 | -10.3384 | -65.7425 | 56.9128 | 57.0951 | 56.8877 | -66.3097 | -0.11367 | -0.057546 | 0.26035 | 0.11051 | 0.22417 | -0.17132 | 0.034963 | -0.346 | -0.15661 | 0.47093 | 0.22122 | 0.56722 | 0.025747 | -0.18167 | 122.9756 | 122.8618 | 123.0681 | 61.5468 | -123.1468 | 122.8765 | 123.0589 | 122.8515 | 55.6254 | -123.3791
1112.7969 | 123.2483 | -65.9317 | 57.0328 | 0.0018314 | -0.010117 | 0.00060681 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | -0.00039093 | 0.00089321 | 0.058238 | 0.016566 | 0.059073 | -65.6942 | -4.5085 | -65.8487 | 57.0119 | 56.9027 | 57.1044 | -66.0637 | -65.4837 | -10.4757 | -65.7288 | 56.9265 | 57.1135 | 56.9198 | -66.3097 | -0.13197 | -0.020925 | 0.23746 | 0.08304 | 0.21501 | -0.13012 | 0.071584 | -0.37804 | -0.10625 | 0.44804 | 0.20292 | 0.58096 | 0.080683 | -0.113 | 122.9436 | 122.8344 | 123.0361 | 61.4232 | -123.0965 | 122.8582 | 123.0452 | 122.8515 | 55.456 | -123.3425
1113.7969 | 123.1201 | -65.95 | 57.0465 | 0.0018314 | -0.010331 | 0.00060681 | 0.056224 | -0.0022669 | 0.0613 | -0.0093855 | -0.00017733 | 0.0013204 | 0.058238 | 0.016566 | 0.058859 | -65.6805 | -4.5864 | -65.8441 | 57.0256 | 56.9347 | 57.1135 | -66.0499 | -65.4699 | -10.636 | -65.7288 | 56.9311 | 57.1226 | 56.9518 | -66.296 | -0.099927 | -0.020923 | 0.26951 | 0.10593 | 0.20585 | -0.1118 | 0.067008 | -0.34599 | -0.11541 | 0.48009 | 0.22123 | 0.56722 | 0.076107 | -0.094679 | 122.9756 | 122.8847 | 123.0635 | 61.3637 | -123.0964 | 122.8811 | 123.0726 | 122.9018 | 55.314 | -123.3425
1114.7969 | 123.2666 | -65.8813 | 57.0648 | 0.0018314 | -0.010117 | 0.00082041 | 0.056438 | -0.0024807 | 0.061514 | -0.0093855 | -0.00039093 | 0.00089321 | 0.058025 | 0.016993 | 0.058859 | -65.6622 | -4.6779 | -65.8303 | 57.0256 | 56.9347 | 57.1227 | -66.0499 | -65.447 | -10.81 | -65.7059 | 56.9448 | 57.1272 | 56.8832 | -66.2823 | -0.16859 | -0.039233 | 0.21916 | 0.050999 | 0.21959 | -0.13011 | 0.057855 | -0.40092 | -0.11998 | 0.43432 | 0.17545 | 0.57638 | 0.062375 | -0.18167 | 122.9069 | 122.8161 | 123.004 | 61.2034 | -123.1148 | 122.8262 | 123.0085 | 122.7645 | 55.0714 | -123.3471
1115.7969 | 123.1293 | -65.9317 | 57.1014 | 0.0018314 | -0.010331 | 0.00060681 | 0.056011 | -0.0022669 | 0.061514 | -0.001755 | -0.00039093 | 0.0011068 | 0.058452 | 0.016566 | 0.058646 | -65.653 | -4.7512 | -65.8212 | 57.0393 | 56.953 | 57.1364 | -66.0454 | -65.4379 | -10.9519 | -65.6967 | 56.9448 | 57.1318 | 56.906 | -66.2868 | -0.11366 | -0.062119 | 0.27867 | 0.11051 | 0.22417 | -0.14842 | 0.03497 | -0.35515 | -0.1566 | 0.49383 | 0.23497 | 0.59011 | 0.030333 | -0.1954 | 122.971 | 122.8847 | 123.0681 | 61.1805 | -123.1468 | 122.8765 | 123.0635 | 122.8377 | 54.9798 | -123.3883
1116.7969 | 123.1384 | -65.9134 | 57.0923 | 0.0018314 | -0.010331 | 0.00039321 | 0.056011 | -0.0024807 | 0.061514 | -0.0093855 | -0.00017733 | 0.00089321 | 0.058666 | 0.01678 | 0.059073 | -65.653 | -4.797 | -65.812 | 57.0393 | 56.953 | 57.141 | -66.0362 | -65.4241 | -11.103 | -65.6784 | 56.954 | 57.1364 | 56.9198 | -66.2868 | -0.12281 | -0.052964 | 0.26036 | 0.10135 | 0.22417 | -0.13926 | 0.048704 | -0.37346 | -0.13829 | 0.48925 | 0.23497 | 0.60843 | 0.044067 | -0.1725 | 122.9527 | 122.8664 | 123.0544 | 61.1164 | -123.1285 | 122.8674 | 123.0497 | 122.8332 | 54.8104 | -123.3791
1117.7969 | 123.0835 | -65.9317 | 57.1106 | -0.0057996 | -0.010545 | 0.00060681 | 0.056011 | -0.0029079 | 0.061727 | -0.0093855 | -0.00039093 | 0.0013204 | 0.058452 | 0.016566 | 0.059073 | -65.6347 | -4.884 | -65.7983 | 57.0576 | 56.9622 | 57.1501 | -66.027 | -65.4012 | -11.277 | -65.6738 | 56.9677 | 57.1501 | 56.9381 | -66.264 | -0.095342 | -0.052961 | 0.29698 | 0.1334 | 0.22874 | -0.14842 | 0.03955 | -0.33225 | -0.14286 | 0.53046 | 0.25786 | 0.59011 | 0.039491 | -0.1725 | 122.9893 | 122.8939 | 123.0818 | 61.0477 | -123.1376 | 122.8994 | 123.0818 | 122.8698 | 54.6547 | -123.3745
1118.7969 | 123.2208 | -65.9088 | 57.0877 | -0.0057996 | -0.010117 | 0.00039321 | 0.056224 | -0.0026943 | 0.061514 | -0.001755 | -0.00017733 | 0.0013204 | 0.058025 | 0.01678 | 0.059073 | -65.6256 | -4.9618 | -65.7937 | 57.0622 | 56.9713 | 57.1547 | -66.0225 | -65.3921 | -11.4556 | -65.6647 | 56.9723 | 57.1638 | 57.0068 | -66.2594 | -0.11365 | -0.025495 | 0.28325 | 0.11509 | 0.22874 | -0.11637 | 0.067017 | -0.35056 | -0.1154 | 0.51673 | 0.24413 | 0.59469 | 0.076115 | -0.080935 | 122.971 | 122.8802 | 123.0635 | 60.947 | -123.1102 | 122.8811 | 123.0726 | 122.9156 | 54.4532 | -123.3471
1119.7969 | 123.1613 | -65.8676 | 57.1152 | 0.0094624 | -0.010545 | 0.00082041 | 0.056011 | -0.0024807 | 0.0613 | 0.013506 | -0.00017733 | 0.0013204 | 0.058025 | 0.01678 | 0.059073 | -65.6118 | -5.0351 | -65.78 | 57.0714 | 56.9759 | 57.173 | -65.995 | -65.3783 | -11.5838 | -65.6464 | 56.9769 | 57.1684 | 56.9793 | -66.2502 | -0.12738 | -0.043803 | 0.25579 | 0.087627 | 0.215 | -0.13926 | 0.057866 | -0.3826 | -0.13828 | 0.48927 | 0.22124 | 0.60385 | 0.053229 | -0.13587 | 122.939 | 122.8435 | 123.0407 | 60.8326 | -123.1102 | 122.8445 | 123.036 | 122.8469 | 54.2838 | -123.3654
1120.7969 | 123.2117 | -65.8539 | 57.0969 | -0.013431 | -0.010758 | 0.00039321 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.016993 | 0.058859 | -65.5935 | -5.1358 | -65.7754 | 57.0805 | 56.9713 | 57.1685 | -65.9996 | -65.3555 | -11.7395 | -65.6326 | 56.9952 | 57.1776 | 57.0068 | -66.2365 | -0.14569 | -0.016336 | 0.26037 | 0.078473 | 0.22416 | -0.12552 | 0.071597 | -0.3826 | -0.10166 | 0.49842 | 0.22125 | 0.60385 | 0.080696 | -0.09009 | 122.9344 | 122.8252 | 123.0223 | 60.7181 | -123.0964 | 122.8491 | 123.0314 | 122.8607 | 54.1144 | -123.3333
1121.7969 | 123.1247 | -65.8905 | 57.1564 | -0.0057996 | -0.010331 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00017733 | 0.0013204 | 0.058025 | 0.01678 | 0.058646 | -65.5798 | -5.2228 | -65.7617 | 57.0897 | 56.9988 | 57.1822 | -65.995 | -65.3509 | -11.9318 | -65.6235 | 56.986 | 57.1821 | 56.9381 | -66.2365 | -0.10449 | -0.066688 | 0.31072 | 0.12883 | 0.23332 | -0.15756 | 0.025824 | -0.34598 | -0.17033 | 0.53963 | 0.26703 | 0.61301 | 0.025766 | -0.21828 | 122.9802 | 122.8893 | 123.0727 | 60.6677 | -123.1514 | 122.8765 | 123.0726 | 122.8286 | 53.9587 | -123.3929
1122.7969 | 123.1476 | -65.8813 | 57.1198 | 0.0018314 | -0.010545 | 0.00039321 | 0.055797 | -0.0026943 | 0.061514 | -0.001755 | -0.00081813 | 0.0013204 | 0.058238 | 0.016566 | 0.059073 | -65.5752 | -5.2869 | -65.7525 | 57.0943 | 57.008 | 57.1868 | -65.9904 | -65.3371 | -12.1012 | -65.6097 | 56.9998 | 57.1959 | 56.9976 | -66.2319 | -0.10907 | -0.025489 | 0.30615 | 0.12883 | 0.2379 | -0.11178 | 0.067024 | -0.35055 | -0.11997 | 0.54421 | 0.27161 | 0.62216 | 0.076122 | -0.12214 | 122.9756 | 122.8893 | 123.0681 | 60.5945 | -123.1102 | 122.8811 | 123.0772 | 122.879 | 53.7802 | -123.3517
1123.7969 | 123.1155 | -65.8722 | 57.1564 | 0.0018314 | -0.010545 | 0.00060681 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | 0.00025007 | 0.0013204 | 0.058666 | 0.017207 | 0.059287 | -65.5569 | -5.3693 | -65.7388 | 57.0988 | 57.0171 | 57.2005 | -65.9813 | -65.3142 | -12.2614 | -65.6097 | 57.0135 | 57.2005 | 57.0617 | -66.2136 | -0.10906 | -0.057532 | 0.3153 | 0.13341 | 0.24247 | -0.13924 | 0.044139 | -0.3414 | -0.14285 | 0.55794 | 0.26245 | 0.60385 | 0.04408 | -0.094655 | 122.971 | 122.8893 | 123.0727 | 60.5029 | -123.1376 | 122.8857 | 123.0726 | 122.9339 | 53.6108 | -123.37
1124.7969 | 123.2483 | -65.8447 | 57.1335 | -0.0057996 | -0.010545 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | 0.0058755 | -0.00060453 | 0.0013204 | 0.058238 | 0.01678 | 0.059073 | -65.5432 | -5.4517 | -65.7296 | 57.108 | 57.008 | 57.2097 | -65.9675 | -65.3005 | -12.4766 | -65.596 | 57.0273 | 57.2096 | 57.0114 | -66.2136 | -0.12279 | -0.025487 | 0.30157 | 0.1151 | 0.23789 | -0.12551 | 0.076184 | -0.36886 | -0.10623 | 0.54422 | 0.24872 | 0.61758 | 0.076125 | -0.12213 | 122.9527 | 122.8527 | 123.0544 | 60.393 | -123.101 | 122.872 | 123.0543 | 122.8561 | 53.3681 | -123.3471
1125.7969 | 123.1659 | -65.8356 | 57.1335 | 0.0018314 | -0.010331 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.0093855 | -0.00017733 | 0.0011068 | 0.058666 | 0.01678 | 0.058859 | -65.5386 | -5.5524 | -65.725 | 57.1126 | 57.0263 | 57.2097 | -65.9629 | -65.2776 | -12.6186 | -65.5731 | 57.0227 | 57.2188 | 57.0022 | -66.2044 | -0.12737 | -0.020908 | 0.297 | 0.11052 | 0.23789 | -0.1072 | 0.076184 | -0.36886 | -0.11081 | 0.55795 | 0.26246 | 0.63132 | 0.085282 | -0.13129 | 122.9481 | 122.8619 | 123.0452 | 60.2831 | -123.0964 | 122.8582 | 123.0543 | 122.8378 | 53.217 | -123.3379
1126.7969 | 123.2437 | -65.7898 | 57.1381 | -0.013431 | -0.0099038 | 0.00039321 | 0.056224 | -0.0026943 | 0.0613 | -0.0093855 | -0.00017733 | 0.001534 | 0.058452 | 0.016993 | 0.059287 | -65.5157 | -5.612 | -65.7113 | 57.1263 | 57.0354 | 57.2142 | -65.9492 | -65.2685 | -12.7605 | -65.5777 | 57.0364 | 57.2188 | 57.0617 | -66.1953 | -0.15941 | -0.011751 | 0.27411 | 0.078482 | 0.23789 | -0.10262 | 0.076184 | -0.40548 | -0.10165 | 0.52133 | 0.21211 | 0.61758 | 0.080704 | -0.076345 | 122.9161 | 122.8252 | 123.004 | 60.1778 | -123.0873 | 122.8262 | 123.0086 | 122.8515 | 53.0293 | -123.3333
1127.7969 | 123.1247 | -65.8356 | 57.1747 | 0.0018314 | -0.010331 | 0.00082041 | 0.056011 | -0.0029079 | 0.0613 | -0.001755 | -0.00017733 | 0.0013204 | 0.058238 | 0.016566 | 0.059287 | -65.5157 | -5.7035 | -65.7067 | 57.1263 | 57.0492 | 57.2326 | -65.94 | -65.2547 | -12.9116 | -65.5502 | 57.0456 | 57.2233 | 57.08 | -66.1907 | -0.10447 | -0.048372 | 0.31989 | 0.12884 | 0.23331 | -0.1255 | 0.057878 | -0.35512 | -0.12912 | 0.58085 | 0.28535 | 0.64048 | 0.048662 | -0.094652 | 122.9619 | 122.8848 | 123.0681 | 60.132 | -123.1147 | 122.8811 | 123.0589 | 122.9156 | 52.924 | -123.3654
1128.7969 | 123.2666 | -65.7898 | 57.1747 | 0.0018314 | -0.010545 | 0.00082041 | 0.056011 | -0.0024807 | 0.061514 | -0.0093855 | -0.00039093 | 0.0013204 | 0.058452 | 0.017207 | 0.059287 | -65.4974 | -5.8088 | -65.6976 | 57.1355 | 57.0538 | 57.2371 | -65.94 | -65.2456 | -13.1451 | -65.5319 | 57.0456 | 57.2371 | 57.0892 | -66.1815 | -0.15025 | -0.039215 | 0.29243 | 0.092216 | 0.24247 | -0.12092 | 0.062456 | -0.39174 | -0.12912 | 0.54423 | 0.25789 | 0.64963 | 0.062398 | -0.085495 | 122.9253 | 122.8436 | 123.0269 | 59.981 | -123.1147 | 122.8354 | 123.0269 | 122.879 | 52.6447 | -123.3562
1129.7969 | 123.2437 | -65.8447 | 57.225 | 0.0018314 | -0.010331 | 0.00060681 | 0.055583 | -0.0026943 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.01678 | 0.058859 | -65.4791 | -5.8958 | -65.6838 | 57.1446 | 57.0767 | 57.2463 | -65.9355 | -65.2181 | -13.3466 | -65.5227 | 57.0547 | 57.2462 | 57.1075 | -66.1678 | -0.090739 | -0.080413 | 0.36567 | 0.16088 | 0.25162 | -0.14838 | 0.02126 | -0.32307 | -0.17031 | 0.62663 | 0.32198 | 0.64505 | 0.021201 | -0.11753 | 122.9894 | 122.9214 | 123.091 | 59.9489 | -123.1605 | 122.8995 | 123.091 | 122.9522 | 52.4981 | -123.3928
1130.7969 | 123.2529 | -65.7944 | 57.1381 | 0.0018314 | -0.010117 | 0.00060681 | 0.056224 | -0.0026943 | 0.061514 | 0.0058755 | -0.00039093 | 0.00089321 | 0.058238 | 0.016993 | 0.059287 | -65.4791 | -5.9141 | -65.6701 | 57.1492 | 57.0721 | 57.2509 | -65.9172 | -65.2181 | -13.5893 | -65.5136 | 57.073 | 57.2508 | 57.0983 | -66.1632 | -0.12278 | 0.011141 | 0.31532 | 0.12426 | 0.24704 | -0.065988 | 0.11281 | -0.36885 | -0.065024 | 0.57628 | 0.28079 | 0.64963 | 0.11275 | -0.039717 | 122.9436 | 122.8664 | 123.0452 | 59.8802 | -123.0552 | 122.8674 | 123.0452 | 122.8927 | 52.2051 | -123.3013
1131.7969 | 123.1155 | -65.8081 | 57.225 | -0.0057996 | -0.010117 | 0.00060681 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.016993 | 0.059287 | -65.4607 | -6.0195 | -65.6701 | 57.1584 | 57.0904 | 57.2692 | -65.9126 | -65.1998 | -13.7861 | -65.509 | 57.073 | 57.26 | 57.08 | -66.1541 | -0.10447 | -0.066678 | 0.34736 | 0.138 | 0.24246 | -0.13465 | 0.044153 | -0.34596 | -0.152 | 0.60832 | 0.2991 | 0.64505 | 0.034937 | -0.14501 | 122.9665 | 122.8985 | 123.0773 | 59.7886 | -123.1376 | 122.8811 | 123.0681 | 122.8881 | 52.022 | -123.3791
1132.7969 | 123.3124 | -65.7852 | 57.1472 | 0.0094624 | -0.010331 | 0.00060681 | 0.055583 | -0.0024807 | 0.061727 | -0.001755 | -0.00017733 | 0.0013204 | 0.058025 | 0.01678 | 0.058859 | -65.4562 | -6.1385 | -65.6518 | 57.1767 | 57.0904 | 57.2646 | -65.8988 | -65.1815 | -13.9601 | -65.4953 | 57.0776 | 57.2691 | 57.1167 | -66.1449 | -0.11362 | 0.029456 | 0.32905 | 0.13342 | 0.24704 | -0.056827 | 0.11739 | -0.35969 | -0.069601 | 0.60375 | 0.28995 | 0.64963 | 0.12191 | -0.030557 | 122.9619 | 122.8756 | 123.0498 | 59.6467 | -123.0461 | 122.8628 | 123.0543 | 122.9019 | 51.8251 | -123.2921
1133.7969 | 123.2574 | -65.7715 | 57.1838 | -0.0057996 | -0.010331 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | 3.6274e-05 | 0.001534 | 0.058025 | 0.017207 | 0.058859 | -65.447 | -6.2392 | -65.6564 | 57.1721 | 57.1041 | 57.2783 | -65.9034 | -65.1677 | -14.1204 | -65.4861 | 57.0959 | 57.2737 | 57.0434 | -66.1403 | -0.13193 | -0.011743 | 0.32448 | 0.11511 | 0.24704 | -0.079711 | 0.094509 | -0.36884 | -0.087908 | 0.60375 | 0.28537 | 0.65421 | 0.089872 | -0.14044 | 122.9436 | 122.8756 | 123.0498 | 59.5323 | -123.0873 | 122.8674 | 123.0452 | 122.8149 | 51.6511 | -123.3242
1134.7969 | 123.2437 | -65.744 | 57.2067 | 0.0094624 | -0.010545 | 0.00060681 | 0.056011 | -0.0024807 | 0.061727 | -0.017016 | -0.00060453 | 0.0013204 | 0.058452 | 0.016993 | 0.059073 | -65.4287 | -6.3354 | -65.6381 | 57.1904 | 57.1041 | 57.2783 | -65.8943 | -65.1494 | -14.3539 | -65.4678 | 57.0959 | 57.2829 | 57.0342 | -66.1403 | -0.15024 | -0.016318 | 0.31533 | 0.10596 | 0.25619 | -0.1026 | 0.071621 | -0.39631 | -0.1108 | 0.5946 | 0.27622 | 0.67253 | 0.076141 | -0.17248 | 122.9344 | 122.8481 | 123.0224 | 59.4086 | -123.101 | 122.8399 | 123.0269 | 122.7783 | 51.3901 | -123.3471
1135.7969 | 123.111 | -65.7944 | 57.225 | -0.0057996 | -0.010545 | 0.00082041 | 0.055583 | -0.0024807 | 0.061941 | -0.017016 | -0.00039093 | 0.0013204 | 0.058025 | 0.017207 | 0.059073 | -65.4287 | -6.4178 | -65.6381 | 57.1904 | 57.0995 | 57.2829 | -65.8988 | -65.1494 | -14.4867 | -65.4586 | 57.0959 | 57.2874 | 57.0892 | -66.1357 | -0.10446 | -0.034629 | 0.36568 | 0.15631 | 0.26077 | -0.12549 | 0.057888 | -0.34137 | -0.12911 | 0.64496 | 0.33573 | 0.6771 | 0.062408 | -0.13585 | 122.9848 | 122.8939 | 123.0773 | 59.3766 | -123.1239 | 122.8903 | 123.0818 | 122.8836 | 51.3077 | -123.3608
1136.7969 | 123.2071 | -65.7211 | 57.2388 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | 0.0058755 | -0.00017733 | 0.001534 | 0.058452 | 0.016993 | 0.058859 | -65.415 | -6.5323 | -65.6243 | 57.1996 | 57.1041 | 57.2921 | -65.8851 | -65.1265 | -14.6698 | -65.4449 | 57.1005 | 57.2829 | 57.0571 | -66.1357 | -0.16397 | -0.039205 | 0.30617 | 0.096804 | 0.26077 | -0.13464 | 0.053313 | -0.41462 | -0.13826 | 0.59461 | 0.27622 | 0.69084 | 0.044097 | -0.18163 | 122.9207 | 122.8253 | 123.0132 | 59.1889 | -123.1239 | 122.8216 | 123.004 | 122.7783 | 51.0513 | -123.3745
1137.7969 | 123.1155 | -65.7623 | 57.2571 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0026943 | 0.061514 | -0.001755 | -0.00039093 | 0.0013204 | 0.058238 | 0.01678 | 0.058859 | -65.4012 | -6.6055 | -65.6197 | 57.195 | 57.1133 | 57.3012 | -65.8805 | -65.1128 | -14.8896 | -65.4449 | 57.1051 | 57.2966 | 57.1167 | -66.122 | -0.11819 | -0.062093 | 0.36111 | 0.14258 | 0.26077 | -0.1438 | 0.04416 | -0.35968 | -0.15199 | 0.64954 | 0.31742 | 0.6771 | 0.039523 | -0.14042 | 122.9573 | 122.8756 | 123.0636 | 59.1568 | -123.1376 | 122.8674 | 123.0589 | 122.879 | 50.8727 | -123.3791
1138.7969 | 123.2529 | -65.6799 | 57.2388 | -0.013431 | -0.010545 | 0.00039321 | 0.055797 | -0.0022669 | 0.061514 | 0.0058755 | -0.00017733 | 0.001534 | 0.058025 | 0.01678 | 0.058859 | -65.3966 | -6.6742 | -65.6106 | 57.2087 | 57.1179 | 57.3058 | -65.8622 | -65.1036 | -15.1277 | -65.4357 | 57.1188 | 57.3103 | 57.1579 | -66.1129 | -0.18227 | -0.030048 | 0.28329 | 0.069341 | 0.25161 | -0.12091 | 0.067048 | -0.43292 | -0.11995 | 0.5763 | 0.24418 | 0.6771 | 0.071568 | -0.080903 | 122.8887 | 122.7978 | 122.9857 | 59.0057 | -123.101 | 122.7988 | 122.9903 | 122.8378 | 50.5522 | -123.3516
1139.7969 | 123.1064 | -65.7669 | 57.2617 | -0.0057996 | -0.010331 | 0.00060681 | 0.055797 | -0.0029079 | 0.061727 | -0.001755 | -0.00060453 | 0.0013204 | 0.058666 | 0.016993 | 0.059073 | -65.3783 | -6.7841 | -65.606 | 57.2179 | 57.1133 | 57.3104 | -65.8576 | -65.0899 | -15.2971 | -65.4174 | 57.1234 | 57.3103 | 57.1487 | -66.1037 | -0.090717 | -0.043779 | 0.38858 | 0.16089 | 0.25161 | -0.14837 | 0.048739 | -0.33679 | -0.13826 | 0.67701 | 0.34947 | 0.68626 | 0.04868 | -0.11295 | 122.9848 | 122.8802 | 123.0773 | 58.9828 | -123.1193 | 122.8903 | 123.0772 | 122.9156 | 50.4698 | -123.3654
1140.7969 | 123.2437 | -65.7303 | 57.2433 | -0.0057996 | -0.010331 | 0.00039321 | 0.056438 | -0.0026943 | 0.0613 | -0.001755 | -0.00017733 | 0.0011068 | 0.058666 | 0.017207 | 0.059073 | -65.3646 | -6.8482 | -65.5969 | 57.2225 | 57.127 | 57.3196 | -65.853 | -65.0807 | -15.5352 | -65.4083 | 57.1234 | 57.3195 | 57.0709 | -66.1037 | -0.12276 | -0.02089 | 0.36569 | 0.13343 | 0.25619 | -0.11633 | 0.076207 | -0.37341 | -0.11995 | 0.64955 | 0.32201 | 0.69542 | 0.076149 | -0.17247 | 122.9527 | 122.8573 | 123.0498 | 58.8821 | -123.0964 | 122.8537 | 123.0498 | 122.8012 | 50.1951 | -123.347
1141.7969 | 123.175 | -65.7211 | 57.2754 | 0.0094624 | -0.010545 | 0.00039321 | 0.056011 | -0.0024807 | 0.061727 | -0.0093855 | -0.00017733 | 0.0013204 | 0.058238 | 0.016993 | 0.059073 | -65.3509 | -6.9764 | -65.5877 | 57.2316 | 57.1316 | 57.3333 | -65.8439 | -65.0578 | -15.7412 | -65.39 | 57.1417 | 57.3287 | 57.0434 | -66.09 | -0.12276 | -0.043777 | 0.37027 | 0.13343 | 0.25619 | -0.14379 | 0.057899 | -0.36883 | -0.13368 | 0.66329 | 0.33117 | 0.7 | 0.053262 | -0.23199 | 122.9527 | 122.8527 | 123.0544 | 58.7447 | -123.1193 | 122.8628 | 123.0498 | 122.7645 | 49.9799 | -123.3653
1142.7969 | 123.2391 | -65.6982 | 57.2296 | -0.013431 | -0.010758 | 0.00060681 | 0.056011 | -0.0024807 | 0.061514 | -0.001755 | -0.00060453 | 0.0011068 | 0.058238 | 0.016993 | 0.059287 | -65.3463 | -7.0359 | -65.5694 | 57.2362 | 57.1362 | 57.3287 | -65.8393 | -65.0441 | -15.9198 | -65.3808 | 57.1417 | 57.3332 | 57.1533 | -66.0854 | -0.14107 | 0.006578 | 0.35196 | 0.12885 | 0.26992 | -0.093435 | 0.099097 | -0.38714 | -0.087899 | 0.65414 | 0.31744 | 0.70458 | 0.10362 | -0.076325 | 122.9344 | 122.8344 | 123.027 | 58.6623 | -123.0689 | 122.84 | 123.0315 | 122.8515 | 49.7784 | -123.315
1143.7969 | 123.1247 | -65.7394 | 57.3029 | -0.0057996 | -0.010972 | 0.00082041 | 0.056011 | -0.0024807 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.016993 | 0.059073 | -65.3325 | -7.1366 | -65.5694 | 57.2316 | 57.1499 | 57.3333 | -65.8393 | -65.0258 | -16.103 | -65.3716 | 57.1463 | 57.3332 | 57.1121 | -66.0808 | -0.099867 | -0.071242 | 0.40689 | 0.17005 | 0.26992 | -0.15294 | 0.030434 | -0.34136 | -0.15656 | 0.71365 | 0.36779 | 0.70915 | 0.030375 | -0.19077 | 122.9711 | 122.8894 | 123.0727 | 58.6028 | -123.1422 | 122.8857 | 123.0727 | 122.8515 | 49.6365 | -123.3837
1144.7969 | 123.2162 | -65.6982 | 57.2708 | 0.0018314 | -0.010545 | 0.00060681 | 0.055797 | -0.0022669 | 0.061727 | -0.001755 | -0.00017733 | 0.001534 | 0.058452 | 0.01678 | 0.0595 | -65.3188 | -7.2603 | -65.5465 | 57.2362 | 57.1499 | 57.3516 | -65.8347 | -65.0166 | -16.309 | -65.3579 | 57.1509 | 57.3424 | 57.1075 | -66.0716 | -0.13649 | -0.034621 | 0.37943 | 0.15175 | 0.28823 | -0.1209 | 0.080791 | -0.3734 | -0.11994 | 0.68161 | 0.34033 | 0.71373 | 0.071576 | -0.16331 | 122.9344 | 122.8482 | 123.0498 | 58.438 | -123.1055 | 122.8491 | 123.0406 | 122.8057 | 49.3892 | -123.3425
1145.7969 | 123.175 | -65.7166 | 57.28 | 0.0018314 | -0.010545 | 0.00039321 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | -0.00017733 | 0.0013204 | 0.058238 | 0.017207 | 0.058859 | -65.3051 | -7.3381 | -65.5511 | 57.2453 | 57.1453 | 57.3424 | -65.8393 | -65.0075 | -16.483 | -65.3488 | 57.1646 | 57.3515 | 57.0571 | -66.0762 | -0.12275 | -0.034619 | 0.41148 | 0.16548 | 0.28823 | -0.13463 | 0.062479 | -0.35967 | -0.11536 | 0.70908 | 0.3678 | 0.72747 | 0.071578 | -0.22283 | 122.9619 | 122.8619 | 123.059 | 58.3785 | -123.1193 | 122.8812 | 123.0681 | 122.7737 | 49.2336 | -123.3562
1146.7969 | 123.2208 | -65.6754 | 57.2617 | -0.0057996 | -0.010545 | 0.00082041 | 0.056011 | -0.0024807 | 0.0613 | -0.017016 | -0.00017733 | 0.001534 | 0.058452 | 0.017207 | 0.059073 | -65.3097 | -7.448 | -65.5328 | 57.2545 | 57.1637 | 57.3562 | -65.8164 | -64.9983 | -16.6936 | -65.335 | 57.1646 | 57.347 | 57.1899 | -66.0671 | -0.14106 | -0.007152 | 0.3657 | 0.14259 | 0.28365 | -0.098005 | 0.094525 | -0.39171 | -0.09705 | 0.67704 | 0.34034 | 0.73205 | 0.085309 | -0.07174 | 122.9299 | 122.839 | 123.0315 | 58.2274 | -123.0781 | 122.84 | 123.0223 | 122.8653 | 48.9817 | -123.3287
1147.7969 | 123.2437 | -65.6708 | 57.2754 | -0.0057996 | -0.010331 | 0.00039321 | 0.056011 | -0.0022669 | 0.061514 | -0.001755 | 3.6274e-05 | 0.001534 | 0.058238 | 0.016993 | 0.059073 | -65.2868 | -7.5487 | -65.5282 | 57.2637 | 57.182 | 57.3653 | -65.8073 | -64.9708 | -16.9088 | -65.3213 | 57.1738 | 57.3653 | 57.1991 | -66.0579 | -0.13648 | -0.011729 | 0.38401 | 0.14259 | 0.27907 | -0.093422 | 0.089949 | -0.38713 | -0.10163 | 0.69993 | 0.3495 | 0.73663 | 0.089891 | -0.076316 | 122.9344 | 122.8527 | 123.0361 | 58.1221 | -123.0826 | 122.8445 | 123.0361 | 122.8699 | 48.762 | -123.3333
1148.7969 | 123.3398 | -65.6387 | 57.3074 | -0.0057996 | -0.010331 | 0.00017941 | 0.056011 | -0.0024807 | 0.0613 | 0.0058755 | 3.6274e-05 | 0.001534 | 0.058452 | 0.017421 | 0.058859 | -65.2685 | -7.6678 | -65.519 | 57.2682 | 57.182 | 57.3745 | -65.8027 | -64.9525 | -17.0737 | -65.3075 | 57.1783 | 57.379 | 57.222 | -66.0533 | -0.16394 | -0.039193 | 0.37028 | 0.11971 | 0.28365 | -0.12546 | 0.067063 | -0.41459 | -0.12909 | 0.6862 | 0.33119 | 0.74578 | 0.071583 | -0.085466 | 122.907 | 122.8207 | 123.0132 | 57.971 | -123.1101 | 122.8171 | 123.0178 | 122.8607 | 48.5651 | -123.3608
1149.7969 | 123.1476 | -65.6891 | 57.312 | 0.0018314 | -0.010545 | 0.00082041 | 0.056011 | -0.0024807 | 0.061727 | 0.0058755 | -0.00060453 | 0.0013204 | 0.058238 | 0.016993 | 0.058646 | -65.2685 | -7.7456 | -65.5053 | 57.2774 | 57.2049 | 57.3837 | -65.8027 | -64.948 | -17.2156 | -65.2984 | 57.1829 | 57.379 | 57.1899 | -66.035 | -0.11359 | -0.034614 | 0.42064 | 0.1838 | 0.29739 | -0.10715 | 0.071643 | -0.34593 | -0.12909 | 0.74113 | 0.3907 | 0.73663 | 0.067005 | -0.12209 | 122.9665 | 122.894 | 123.0727 | 57.9435 | -123.1147 | 122.872 | 123.0681 | 122.879 | 48.4735 | -123.347
1150.7969 | 123.2483 | -65.6662 | 57.3074 | 0.0018314 | -0.010758 | 0.0010342 | 0.056011 | -0.0024807 | 0.061514 | 0.0058755 | -0.00017733 | 0.0011068 | 0.058452 | 0.017207 | 0.059287 | -65.2501 | -7.8738 | -65.4961 | 57.2866 | 57.2049 | 57.3791 | -65.7935 | -64.9251 | -17.4903 | -65.2755 | 57.1921 | 57.3836 | 57.2311 | -66.035 | -0.12732 | -0.02088 | 0.41606 | 0.17007 | 0.29739 | -0.10257 | 0.071642 | -0.36881 | -0.11536 | 0.74114 | 0.39071 | 0.75952 | 0.076162 | -0.076309 | 122.9528 | 122.8711 | 123.0453 | 57.7924 | -123.101 | 122.8583 | 123.0498 | 122.8973 | 48.1759 | -123.3424
1151.7969 | 123.2483 | -65.6158 | 57.3303 | -0.0057996 | -0.010758 | 0.00060681 | 0.056011 | -0.0026943 | 0.061514 | 0.013506 | -0.00017733 | 0.001534 | 0.058666 | 0.016993 | 0.058859 | -65.2318 | -7.9699 | -65.4916 | 57.3003 | 57.2094 | 57.3882 | -65.7889 | -64.9113 | -17.6551 | -65.2755 | 57.2012 | 57.3882 | 57.1441 | -66.0259 | -0.1731 | -0.030032 | 0.38402 | 0.12429 | 0.29738 | -0.12088 | 0.057911 | -0.41001 | -0.12909 | 0.70452 | 0.34035 | 0.75036 | 0.057853 | -0.18619 | 122.9161 | 122.8253 | 123.0041 | 57.6459 | -123.1193 | 122.8171 | 123.004 | 122.76 | 47.9607 | -123.3562
1152.7969 | 123.2071 | -65.6387 | 57.3029 | 0.0018314 | -0.010758 | 0.00060681 | 0.056224 | -0.0024807 | 0.061727 | -0.017016 | 3.6274e-05 | 0.001534 | 0.058452 | 0.017421 | 0.059073 | -65.2227 | -8.0844 | -65.4916 | 57.2911 | 57.2232 | 57.402 | -65.7752 | -64.893 | -17.8887 | -65.2572 | 57.2058 | 57.3973 | 57.1624 | -66.0213 | -0.13647 | -0.011723 | 0.41607 | 0.14718 | 0.28365 | -0.079677 | 0.099113 | -0.38254 | -0.097042 | 0.74573 | 0.38155 | 0.7641 | 0.094476 | -0.14041 | 122.9299 | 122.8619 | 123.0407 | 57.5543 | -123.0781 | 122.8445 | 123.0361 | 122.8012 | 47.7501 | -123.3241
1153.7969 | 123.2346 | -65.6708 | 57.3532 | -0.0057996 | -0.010545 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | 0.00025007 | 0.001534 | 0.058666 | 0.017207 | 0.059073 | -65.1998 | -8.1851 | -65.4732 | 57.3049 | 57.2232 | 57.4065 | -65.7752 | -64.8793 | -18.0718 | -65.2343 | 57.215 | 57.4111 | 57.2403 | -66.0075 | -0.10443 | -0.048342 | 0.471 | 0.19753 | 0.30196 | -0.13003 | 0.053338 | -0.33676 | -0.13824 | 0.79151 | 0.43649 | 0.77325 | 0.057858 | -0.11293 | 122.9756 | 122.894 | 123.0773 | 57.4856 | -123.1284 | 122.8857 | 123.0818 | 122.9111 | 47.599 | -123.3607
1154.7969 | 123.1979 | -65.6158 | 57.3578 | -0.0057996 | -0.010331 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00039093 | 0.001534 | 0.058025 | 0.017207 | 0.059073 | -65.1952 | -8.2904 | -65.4595 | 57.314 | 57.2323 | 57.4203 | -65.7615 | -64.8564 | -18.287 | -65.2206 | 57.2241 | 57.4202 | 57.2586 | -65.9984 | -0.14562 | -0.043763 | 0.42065 | 0.15634 | 0.30196 | -0.12545 | 0.062495 | -0.38254 | -0.13366 | 0.75947 | 0.39529 | 0.77783 | 0.062437 | -0.099191 | 122.9299 | 122.8482 | 123.0361 | 57.3254 | -123.1193 | 122.84 | 123.0361 | 122.8744 | 47.3288 | -123.3562
1155.7969 | 123.262 | -65.5975 | 57.3441 | 0.0018314 | -0.010545 | 0.00082041 | 0.056011 | -0.0026943 | 0.0613 | -0.017016 | 3.6274e-05 | 0.0013204 | 0.058452 | 0.017207 | 0.058859 | -65.1769 | -8.4324 | -65.4458 | 57.3232 | 57.2232 | 57.4249 | -65.7523 | -64.8335 | -18.4976 | -65.2114 | 57.2379 | 57.4294 | 57.1075 | -66.003 | -0.15478 | -0.020874 | 0.42065 | 0.15176 | 0.30654 | -0.12088 | 0.080807 | -0.40543 | -0.10619 | 0.76405 | 0.38614 | 0.79157 | 0.085327 | -0.23655 | 122.9207 | 122.8207 | 123.0224 | 57.1652 | -123.0964 | 122.8354 | 123.0269 | 122.705 | 47.0999 | -123.347
1156.7969 | 123.23 | -65.6067 | 57.3212 | 0.0018314 | -0.010331 | 0.00082041 | 0.056011 | -0.0022669 | 0.061514 | -0.001755 | -0.00017733 | 0.001534 | 0.058238 | 0.017207 | 0.058859 | -65.1677 | -8.5285 | -65.4458 | 57.3369 | 57.2415 | 57.4294 | -65.7523 | -64.8197 | -18.6716 | -65.1977 | 57.247 | 57.4385 | 57.2494 | -65.9892 | -0.14562 | 0.01575 | 0.43896 | 0.16092 | 0.30654 | -0.079672 | 0.10827 | -0.38254 | -0.074147 | 0.78694 | 0.40903 | 0.79157 | 0.11737 | -0.071728 | 122.9436 | 122.8482 | 123.0361 | 57.0782 | -123.0735 | 122.8537 | 123.0452 | 122.8561 | 46.9351 | -123.3104
1157.7969 | 123.1567 | -65.6021 | 57.3624 | -0.0057996 | -0.010758 | 0.00039321 | 0.056224 | -0.0024807 | 0.061727 | 0.0058755 | -0.00039093 | 0.001534 | 0.058025 | 0.016993 | 0.058859 | -65.1631 | -8.6201 | -65.432 | 57.3323 | 57.2278 | 57.434 | -65.7477 | -64.806 | -18.8731 | -65.1839 | 57.2424 | 57.4477 | 57.2265 | -65.9846 | -0.14562 | -0.030028 | 0.43897 | 0.17007 | 0.31569 | -0.13461 | 0.071653 | -0.38253 | -0.11992 | 0.7961 | 0.41819 | 0.80073 | 0.08533 | -0.13582 | 122.9344 | 122.8299 | 123.0361 | 56.982 | -123.1101 | 122.8446 | 123.0498 | 122.8287 | 46.729 | -123.347
1158.7969 | 123.1934 | -65.5792 | 57.3624 | -0.0057996 | -0.010331 | 0.0010342 | 0.056224 | -0.0026943 | 0.061727 | 0.0058755 | -0.00017733 | 0.0011068 | 0.058452 | 0.017207 | 0.059287 | -65.1403 | -8.7391 | -65.4183 | 57.3461 | 57.2598 | 57.4478 | -65.7294 | -64.7877 | -19.1295 | -65.1564 | 57.2562 | 57.4477 | 57.2311 | -65.9755 | -0.15019 | -0.016293 | 0.43897 | 0.16092 | 0.31111 | -0.10256 | 0.085389 | -0.39626 | -0.10619 | 0.79153 | 0.42278 | 0.81904 | 0.08533 | -0.13124 | 122.9253 | 122.839 | 123.027 | 56.8401 | -123.0918 | 122.8354 | 123.0269 | 122.8103 | 46.4497 | -123.3379
1159.7969 | 123.23 | -65.6113 | 57.3715 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0024807 | 0.062155 | -0.0093855 | -0.00017733 | 0.0013204 | 0.058452 | 0.017207 | 0.0595 | -65.1311 | -8.8445 | -65.4 | 57.3598 | 57.2552 | 57.4478 | -65.7203 | -64.7694 | -19.3126 | -65.1427 | 57.2699 | 57.4614 | 57.1808 | -65.9663 | -0.10899 | -0.011712 | 0.48017 | 0.21128 | 0.32027 | -0.11629 | 0.076234 | -0.35506 | -0.10161 | 0.84189 | 0.46855 | 0.82362 | 0.089911 | -0.19076 | 122.9711 | 122.8665 | 123.059 | 56.7668 | -123.0918 | 122.8812 | 123.0727 | 122.792 | 46.2986 | -123.3379
1160.7969 | 123.1979 | -65.5472 | 57.3853 | 0.0018314 | -0.010758 | 0.00060681 | 0.056011 | -0.0022669 | 0.061941 | -0.0093855 | -0.00081813 | 0.001534 | 0.058452 | 0.017421 | 0.059287 | -65.1036 | -8.9589 | -65.4 | 57.369 | 57.2598 | 57.4661 | -65.7111 | -64.7465 | -19.5233 | -65.1427 | 57.2745 | 57.466 | 57.2906 | -65.9572 | -0.16392 | -0.016289 | 0.44355 | 0.14719 | 0.31111 | -0.12544 | 0.080816 | -0.40999 | -0.11076 | 0.80069 | 0.40447 | 0.81446 | 0.080757 | -0.094607 | 122.9161 | 122.807 | 123.0132 | 56.5883 | -123.0964 | 122.8217 | 123.0132 | 122.8378 | 46.0239 | -123.3424
1161.7969 | 123.23 | -65.5655 | 57.4127 | -0.0057996 | -0.010545 | 0.00060681 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | -0.00060453 | 0.0017478 | 0.058025 | 0.017634 | 0.059287 | -65.0945 | -9.0963 | -65.3771 | 57.3735 | 57.2735 | 57.4752 | -65.6974 | -64.7236 | -19.7156 | -65.1152 | 57.2791 | 57.4706 | 57.2678 | -65.948 | -0.13187 | -0.039176 | 0.47102 | 0.18839 | 0.32026 | -0.13917 | 0.062507 | -0.38252 | -0.13365 | 0.8419 | 0.45025 | 0.83278 | 0.057869 | -0.14497 | 122.939 | 122.839 | 123.0407 | 56.4692 | -123.1101 | 122.8446 | 123.0361 | 122.8332 | 45.8499 | -123.3607
1162.7969 | 123.2025 | -65.5426 | 57.431 | 0.0094624 | -0.010545 | 0.00082041 | 0.055797 | -0.0024807 | 0.061727 | -0.0093855 | -0.00039093 | 0.001534 | 0.057811 | 0.017207 | 0.0595 | -65.0853 | -9.2062 | -65.3725 | 57.3873 | 57.2873 | 57.4798 | -65.7019 | -64.7099 | -19.9033 | -65.0969 | 57.2928 | 57.4797 | 57.254 | -65.9389 | -0.15934 | -0.043751 | 0.45729 | 0.17008 | 0.32942 | -0.14375 | 0.048775 | -0.39625 | -0.13822 | 0.83274 | 0.44568 | 0.84193 | 0.048717 | -0.17701 | 122.9299 | 122.8299 | 123.0224 | 56.3364 | -123.133 | 122.8354 | 123.0224 | 122.7966 | 45.6393 | -123.3699
1163.7969 | 123.1888 | -65.5609 | 57.4173 | 0.0018314 | -0.010972 | 0.00060681 | 0.055797 | -0.0024807 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.001534 | 0.058452 | 0.017421 | 0.059073 | -65.067 | -9.3435 | -65.3634 | 57.3919 | 57.301 | 57.4844 | -65.6882 | -64.6961 | -20.1002 | -65.0923 | 57.302 | 57.4889 | 57.1945 | -65.9297 | -0.12729 | -0.02544 | 0.49391 | 0.19755 | 0.32484 | -0.11628 | 0.067087 | -0.36879 | -0.11533 | 0.86479 | 0.46857 | 0.83735 | 0.071607 | -0.2228 | 122.9528 | 122.8619 | 123.0453 | 56.2174 | -123.1055 | 122.8629 | 123.0498 | 122.7554 | 45.4607 | -123.347
1164.7969 | 123.2529 | -65.5334 | 57.4081 | 0.0018314 | -0.010331 | 0.00060681 | 0.056438 | -0.0031215 | 0.061941 | 0.0058755 | -0.00017733 | 0.0013204 | 0.058238 | 0.017207 | 0.059073 | -65.0578 | -9.4763 | -65.3496 | 57.3919 | 57.3193 | 57.4981 | -65.679 | -64.6641 | -20.2604 | -65.0695 | 57.3157 | 57.4981 | 57.3593 | -65.9251 | -0.1456 | -0.016285 | 0.4756 | 0.18382 | 0.32942 | -0.088806 | 0.089978 | -0.39167 | -0.092444 | 0.86937 | 0.46399 | 0.85567 | 0.089919 | -0.048816 | 122.9253 | 122.8528 | 123.0316 | 56.0571 | -123.0872 | 122.8491 | 123.0315 | 122.8928 | 45.273 | -123.3333
1165.7969 | 123.2025 | -65.4877 | 57.4448 | -0.0057996 | -0.010545 | 0.00082041 | 0.056224 | -0.0024807 | 0.0613 | -0.001755 | -0.00017733 | 0.0011068 | 0.058238 | 0.017207 | 0.058859 | -65.0487 | -9.5679 | -65.3496 | 57.4056 | 57.3148 | 57.4981 | -65.6745 | -64.6595 | -20.4298 | -65.0603 | 57.3157 | 57.5118 | 57.3227 | -65.9205 | -0.1868 | -0.039171 | 0.43898 | 0.13804 | 0.32484 | -0.13001 | 0.053357 | -0.43287 | -0.12907 | 0.82818 | 0.42738 | 0.86025 | 0.067034 | -0.12207 | 122.8933 | 122.8024 | 122.9858 | 55.9198 | -123.1192 | 122.8034 | 122.9995 | 122.8104 | 45.0578 | -123.3653
1166.7969 | 123.1888 | -65.5289 | 57.4448 | -0.0057996 | -0.010758 | 0.00082041 | 0.056011 | -0.0026943 | 0.0613 | -0.001755 | -0.00017733 | 0.001534 | 0.058238 | 0.017207 | 0.0595 | -65.0304 | -9.7052 | -65.3267 | 57.4056 | 57.3193 | 57.5119 | -65.6653 | -64.6366 | -20.6405 | -65.0374 | 57.3249 | 57.5118 | 57.2861 | -65.9114 | -0.13644 | -0.039171 | 0.4985 | 0.20213 | 0.33857 | -0.12543 | 0.067093 | -0.38251 | -0.11991 | 0.89227 | 0.49147 | 0.87398 | 0.067034 | -0.1587 | 122.9345 | 122.8482 | 123.0407 | 55.8236 | -123.1101 | 122.8537 | 123.0407 | 122.8149 | 44.8884 | -123.3561
1167.7969 | 123.2574 | -65.506 | 57.4448 | 0.0018314 | -0.010758 | 0.00060681 | 0.056011 | -0.0024807 | 0.061514 | -0.0093855 | -0.00017733 | 0.001534 | 0.058452 | 0.017421 | 0.059073 | -65.0166 | -9.8151 | -65.3222 | 57.4193 | 57.3468 | 57.5164 | -65.6562 | -64.6137 | -20.8648 | -65.0237 | 57.334 | 57.5164 | 57.3319 | -65.9022 | -0.15017 | -0.025435 | 0.48934 | 0.18382 | 0.33399 | -0.097953 | 0.071671 | -0.39625 | -0.11075 | 0.89228 | 0.48232 | 0.87856 | 0.071613 | -0.11291 | 122.9253 | 122.8528 | 123.0224 | 55.6909 | -123.1009 | 122.84 | 123.0224 | 122.8378 | 44.6412 | -123.347
1168.7969 | 123.1064 | -65.5106 | 57.4905 | 0.0018314 | -0.010545 | 0.00082041 | 0.056011 | -0.0026943 | 0.061941 | 0.0058755 | -0.00017733 | 0.001534 | 0.058452 | 0.017848 | 0.059073 | -64.9937 | -9.9479 | -65.3038 | 57.4285 | 57.3422 | 57.5164 | -65.6378 | -64.5954 | -21.0571 | -65.0099 | 57.334 | 57.5301 | 57.3685 | -65.8885 | -0.12728 | -0.062056 | 0.51681 | 0.20671 | 0.33399 | -0.14831 | 0.025894 | -0.37793 | -0.15653 | 0.91517 | 0.50063 | 0.87856 | 0.039571 | -0.12206 | 122.939 | 122.8528 | 123.027 | 55.5627 | -123.1284 | 122.8446 | 123.0407 | 122.879 | 44.4534 | -123.379
1169.7969 | 123.175 | -65.4831 | 57.4585 | 0.0018314 | -0.010545 | 0.00082041 | 0.056224 | -0.0029079 | 0.061941 | -0.001755 | 3.6274e-05 | 0.0013204 | 0.058452 | 0.017207 | 0.059287 | -64.98 | -10.1173 | -65.2901 | 57.4331 | 57.3651 | 57.5347 | -65.6333 | -64.5771 | -21.2998 | -64.987 | 57.3477 | 57.5301 | 57.3685 | -65.8793 | -0.15016 | -0.025433 | 0.50308 | 0.19298 | 0.34315 | -0.09337 | 0.076253 | -0.39624 | -0.11075 | 0.90602 | 0.49606 | 0.8923 | 0.071615 | -0.090013 | 122.9162 | 122.8482 | 123.0178 | 55.3658 | -123.0918 | 122.8308 | 123.0132 | 122.8516 | 44.1833 | -123.3378
1170.7969 | 123.2025 | -65.4739 | 57.4722 | 0.0018314 | -0.010758 | 0.00082041 | 0.056011 | -0.0024807 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.0013204 | 0.058452 | 0.017421 | 0.059287 | -64.9617 | -10.273 | -65.2764 | 57.4468 | 57.3697 | 57.5485 | -65.6195 | -64.5496 | -21.4417 | -64.9687 | 57.3661 | 57.5484 | 57.3685 | -65.8702 | -0.14558 | -0.025431 | 0.51224 | 0.19756 | 0.34314 | -0.10252 | 0.076255 | -0.39624 | -0.10617 | 0.92433 | 0.50522 | 0.90145 | 0.076197 | -0.10375 | 122.9207 | 122.8436 | 123.0224 | 55.201 | -123.0917 | 122.84 | 123.0224 | 122.8424 | 44.0322 | -123.3424
1171.7969 | 123.2208 | -65.4831 | 57.4722 | 0.0018314 | -0.010331 | 0.00039321 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | 3.6274e-05 | 0.001534 | 0.058452 | 0.017207 | 0.059073 | -64.948 | -10.4149 | -65.2581 | 57.4605 | 57.3926 | 57.5576 | -65.6058 | -64.5313 | -21.6066 | -64.9367 | 57.3798 | 57.5622 | 57.4326 | -65.861 | -0.12269 | -0.011696 | 0.53513 | 0.22503 | 0.34772 | -0.07963 | 0.085413 | -0.37793 | -0.092432 | 0.9518 | 0.54642 | 0.92435 | 0.089933 | -0.039646 | 122.9436 | 122.8757 | 123.0407 | 55.0682 | -123.078 | 122.8629 | 123.0453 | 122.9157 | 43.8765 | -123.3332
1172.7969 | 123.2162 | -65.4373 | 57.5043 | 0.0094624 | -0.010758 | 0.00039321 | 0.056011 | -0.0029079 | 0.061727 | -0.001755 | 0.00025007 | 0.0011068 | 0.058666 | 0.017634 | 0.0595 | -64.9342 | -10.566 | -65.2489 | 57.4697 | 57.4109 | 57.5714 | -65.6012 | -64.5038 | -21.7348 | -64.9184 | 57.3844 | 57.5713 | 57.3181 | -65.8564 | -0.16389 | -0.034582 | 0.50309 | 0.18841 | 0.3523 | -0.093357 | 0.067105 | -0.41912 | -0.1199 | 0.9335 | 0.51896 | 0.93808 | 0.067047 | -0.18615 | 122.907 | 122.8482 | 123.0087 | 54.8713 | -123.1055 | 122.8217 | 123.0086 | 122.7554 | 43.7025 | -123.3607
1173.7969 | 123.2529 | -65.4236 | 57.518 | 0.0018314 | -0.010758 | 0.00082041 | 0.055797 | -0.0026943 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.0013204 | 0.058238 | 0.017421 | 0.059287 | -64.9159 | -10.7079 | -65.2352 | 57.488 | 57.4201 | 57.5897 | -65.592 | -64.4809 | -21.9088 | -64.8955 | 57.3981 | 57.5805 | 57.428 | -65.8381 | -0.16846 | -0.030002 | 0.50767 | 0.18841 | 0.35687 | -0.097932 | 0.071687 | -0.41454 | -0.11989 | 0.94266 | 0.52812 | 0.94266 | 0.062471 | -0.09 | 122.9116 | 122.8437 | 123.0133 | 54.7156 | -123.1101 | 122.8217 | 123.0041 | 122.8516 | 43.5148 | -123.3561
1174.7969 | 123.262 | -65.4144 | 57.5272 | 0.0018314 | -0.010758 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | -0.00039093 | 0.0013204 | 0.058452 | 0.017848 | 0.0595 | -64.9022 | -10.8041 | -65.2214 | 57.488 | 57.4201 | 57.5897 | -65.5829 | -64.4626 | -22.0828 | -64.8817 | 57.3981 | 57.5988 | 57.4143 | -65.829 | -0.16846 | -0.039158 | 0.51225 | 0.19299 | 0.36145 | -0.10709 | 0.062531 | -0.41454 | -0.12905 | 0.95182 | 0.5327 | 0.94724 | 0.071629 | -0.11289 | 122.9024 | 122.8345 | 123.0041 | 54.6103 | -123.1101 | 122.8125 | 123.0132 | 122.8287 | 43.3317 | -123.3561
1175.7969 | 123.23 | -65.4236 | 57.5226 | -0.013431 | -0.010545 | 0.0010342 | 0.056011 | -0.0024807 | 0.061727 | -0.001755 | -0.00039093 | 0.0013204 | 0.058452 | 0.017421 | 0.059287 | -64.8839 | -10.9094 | -65.2077 | 57.4972 | 57.4292 | 57.5897 | -65.5737 | -64.4351 | -22.243 | -64.8771 | 57.4164 | 57.5988 | 57.4097 | -65.8244 | -0.15015 | -0.025423 | 0.53972 | 0.21588 | 0.36603 | -0.093352 | 0.067109 | -0.4008 | -0.10616 | 0.98845 | 0.54644 | 0.94724 | 0.076207 | -0.11289 | 122.9207 | 122.8528 | 123.0133 | 54.5142 | -123.0963 | 122.84 | 123.0224 | 122.8333 | 43.1806 | -123.347
1176.7969 | 123.2391 | -65.4282 | 57.5546 | -0.0057996 | -0.010758 | 0.00060681 | 0.056011 | -0.0026943 | 0.061514 | -0.001755 | 3.6274e-05 | 0.0011068 | 0.058452 | 0.017634 | 0.059287 | -64.8793 | -11.0651 | -65.2077 | 57.5017 | 57.4201 | 57.5988 | -65.5829 | -64.4351 | -22.3483 | -64.8543 | 57.4118 | 57.6034 | 57.4509 | -65.829 | -0.15473 | -0.052887 | 0.54887 | 0.22046 | 0.37519 | -0.13455 | 0.044223 | -0.4008 | -0.14278 | 0.99303 | 0.57391 | 0.97471 | 0.048743 | -0.10373 | 122.9299 | 122.8482 | 123.027 | 54.3631 | -123.1375 | 122.84 | 123.0315 | 122.8791 | 43.0798 | -123.3836
1177.7969 | 123.2391 | -65.451 | 57.5134 | -0.0057996 | -0.010758 | 0.00060681 | 0.055797 | -0.0026943 | 0.061941 | -0.001755 | 3.6274e-05 | 0.0017478 | 0.058452 | 0.017634 | 0.059287 | -64.8793 | -11.2116 | -65.2031 | 57.4926 | 57.3972 | 57.5943 | -65.5875 | -64.4306 | -22.3804 | -64.8543 | 57.3981 | 57.5896 | 57.4646 | -65.829 | -0.13642 | -0.020846 | 0.57176 | 0.24793 | 0.38434 | -0.11625 | 0.080842 | -0.37792 | -0.11532 | 1.0205 | 0.5968 | 0.97471 | 0.076205 | -0.048794 | 122.9436 | 122.8482 | 123.0453 | 54.2395 | -123.1009 | 122.8492 | 123.0407 | 122.9157 | 43.0707 | -123.3424
1178.7969 | 123.2117 | -65.4419 | 57.4814 | -0.0057996 | -0.010545 | 0.00082041 | 0.056011 | -0.0026943 | 0.061727 | -0.0093855 | 0.00025007 | 0.0013204 | 0.058025 | 0.017421 | 0.059287 | -64.8884 | -11.3764 | -65.2123 | 57.4697 | 57.3926 | 57.5897 | -65.5966 | -64.4351 | -22.2796 | -64.8771 | 57.389 | 57.5851 | 57.3685 | -65.8473 | -0.15473 | -0.011694 | 0.55345 | 0.22961 | 0.38434 | -0.088785 | 0.10831 | -0.40539 | -0.09243 | 1.0068 | 0.56475 | 0.97013 | 0.10367 | -0.1129 | 122.9116 | 122.8345 | 123.0316 | 54.0655 | -123.078 | 122.8308 | 123.0269 | 122.8104 | 43.1623 | -123.3287
1179.7969 | 123.2437 | -65.4282 | 57.5043 | 0.0018314 | -0.010545 | 0.00082041 | 0.056011 | -0.0024807 | 0.061941 | -0.0093855 | 3.6274e-05 | 0.0017478 | 0.058238 | 0.017421 | 0.059287 | -64.8701 | -11.5092 | -65.2077 | 57.488 | 57.4018 | 57.5851 | -65.592 | -64.4168 | -22.298 | -64.8588 | 57.3981 | 57.5851 | 57.396 | -65.8427 | -0.16388 | -0.016269 | 0.55803 | 0.22046 | 0.38434 | -0.10251 | 0.080841 | -0.41454 | -0.10616 | 1.0113 | 0.56933 | 0.98387 | 0.080783 | -0.10832 | 122.9162 | 122.8299 | 123.0133 | 53.919 | -123.0963 | 122.8263 | 123.0132 | 122.8241 | 43.1302 | -123.347
1180.7969 | 123.2117 | -65.4144 | 57.5089 | 0.0018314 | -0.010758 | 0.0010342 | 0.056438 | -0.0026943 | 0.061941 | -0.001755 | -0.00017733 | 0.0019614 | 0.058452 | 0.017634 | 0.059287 | -64.8656 | -11.6695 | -65.1985 | 57.4972 | 57.3972 | 57.5943 | -65.5875 | -64.3985 | -22.3575 | -64.8359 | 57.4073 | 57.5942 | 57.4097 | -65.829 | -0.17304 | -0.01169 | 0.54888 | 0.21588 | 0.38892 | -0.11167 | 0.08542 | -0.41454 | -0.10158 | 1.0159 | 0.57849 | 0.99303 | 0.085362 | -0.09916 | 122.9116 | 122.8116 | 123.0087 | 53.745 | -123.0963 | 122.8217 | 123.0086 | 122.8241 | 43.0569 | -123.3378
1181.7969 | 123.2071 | -65.419 | 57.5226 | 0.0018314 | -0.010545 | 0.00060681 | 0.056652 | -0.0022669 | 0.061514 | -0.0093855 | -0.00017733 | 0.001534 | 0.058238 | 0.017634 | 0.059287 | -64.8472 | -11.816 | -65.1894 | 57.5017 | 57.4063 | 57.6034 | -65.5783 | -64.3802 | -22.3895 | -64.8222 | 57.4073 | 57.6034 | 57.3502 | -65.8244 | -0.1593 | -0.020844 | 0.57177 | 0.22962 | 0.38892 | -0.11625 | 0.080845 | -0.40538 | -0.11531 | 1.0388 | 0.5968 | 1.0022 | 0.080786 | -0.17241 | 122.9207 | 122.8253 | 123.0224 | 53.603 | -123.1009 | 122.8263 | 123.0224 | 122.7692 | 43.0295 | -123.347
1182.7969 | 123.2117 | -65.4419 | 57.5592 | -0.0057996 | -0.010972 | 0.00082041 | 0.056438 | -0.0026943 | 0.061727 | -0.001755 | -0.00039093 | 0.001534 | 0.058452 | 0.017634 | 0.059714 | -64.8289 | -11.9396 | -65.1757 | 57.5017 | 57.4018 | 57.6034 | -65.5646 | -64.3665 | -22.4674 | -64.8085 | 57.4256 | 57.6034 | 57.3547 | -65.8198 | -0.12268 | -0.057465 | 0.61297 | 0.26624 | 0.38892 | -0.15745 | 0.044224 | -0.37791 | -0.13362 | 1.0754 | 0.63343 | 1.0113 | 0.044165 | -0.20446 | 122.9436 | 122.8437 | 123.0453 | 53.5023 | -123.1238 | 122.8675 | 123.0453 | 122.7966 | 42.9745 | -123.379
1183.7969 | 123.2529 | -65.419 | 57.518 | -0.0057996 | -0.010545 | 0.00082041 | 0.056224 | -0.0026943 | 0.061727 | -0.001755 | 3.6274e-05 | 0.0013204 | 0.058666 | 0.017634 | 0.0595 | -64.8106 | -12.0998 | -65.1619 | 57.5201 | 57.4109 | 57.6172 | -65.5646 | -64.339 | -22.6093 | -64.8039 | 57.4118 | 57.6217 | 57.396 | -65.8061 | -0.14557 | 0.002047 | 0.6084 | 0.25709 | 0.40265 | -0.10709 | 0.099158 | -0.38707 | -0.10616 | 1.08 | 0.61512 | 1.0022 | 0.10368 | -0.12205 | 122.9391 | 122.8299 | 123.0362 | 53.3192 | -123.0826 | 122.8309 | 123.0407 | 122.815 | 42.8097 | -123.3241
1184.7969 | 123.2071 | -65.4099 | 57.5546 | 0.0018314 | -0.010758 | 0.00082041 | 0.056011 | -0.0026943 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.00089321 | 0.057811 | 0.017848 | 0.059714 | -64.8106 | -12.2921 | -65.1528 | 57.5155 | 57.4155 | 57.6172 | -65.56 | -64.3161 | -22.7375 | -64.781 | 57.4256 | 57.6125 | 57.3593 | -65.8015 | -0.15014 | -0.039152 | 0.59924 | 0.25709 | 0.40723 | -0.13913 | 0.062537 | -0.39164 | -0.12904 | 1.0938 | 0.62886 | 1.0205 | 0.0579 | -0.1953 | 122.9253 | 122.8253 | 123.027 | 53.1177 | -123.1146 | 122.8354 | 123.0224 | 122.7692 | 42.6723 | -123.3561
1185.7969 | 123.2346 | -65.3915 | 57.5455 | 0.0094624 | -0.010545 | 0.00082041 | 0.056011 | -0.0026943 | 0.061941 | -0.001755 | -0.00039093 | 0.001534 | 0.058238 | 0.017848 | 0.059287 | -64.7831 | -12.4387 | -65.139 | 57.5292 | 57.4384 | 57.6355 | -65.5371 | -64.2886 | -22.7879 | -64.7535 | 57.4439 | 57.6354 | 57.4051 | -65.7878 | -0.14556 | -0.016262 | 0.6084 | 0.25251 | 0.39807 | -0.10708 | 0.090007 | -0.39622 | -0.10157 | 1.1029 | 0.63802 | 1.0342 | 0.089948 | -0.14036 | 122.9207 | 122.8299 | 123.027 | 52.9529 | -123.0826 | 122.8354 | 123.027 | 122.7967 | 42.6037 | -123.3332
1186.7969 | 123.1567 | -65.4053 | 57.5775 | -0.0057996 | -0.010545 | 0.00060681 | 0.056011 | -0.0022669 | 0.061727 | -0.001755 | 3.6274e-05 | 0.001534 | 0.058452 | 0.017421 | 0.059714 | -64.7786 | -12.6126 | -65.1207 | 57.5384 | 57.443 | 57.6309 | -65.5417 | -64.2749 | -22.8795 | -64.7444 | 57.4439 | 57.6308 | 57.396 | -65.7832 | -0.13641 | -0.039149 | 0.62671 | 0.28456 | 0.42096 | -0.13455 | 0.053384 | -0.37791 | -0.13362 | 1.1304 | 0.66091 | 1.0388 | 0.053326 | -0.18156 | 122.9436 | 122.8482 | 123.0362 | 52.7926 | -123.1192 | 122.8492 | 123.0361 | 122.8012 | 42.5258 | -123.3607
1187.7969 | 123.2025 | -65.387 | 57.5867 | -0.013431 | -0.010758 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.0093855 | 3.6274e-05 | 0.0017478 | 0.058238 | 0.017421 | 0.059287 | -64.7557 | -12.7546 | -65.1161 | 57.5384 | 57.4659 | 57.6355 | -65.5325 | -64.2566 | -22.9985 | -64.7215 | 57.4576 | 57.6354 | 57.4555 | -65.7878 | -0.14556 | -0.048304 | 0.63129 | 0.27083 | 0.41638 | -0.12081 | 0.048808 | -0.40079 | -0.12904 | 1.1304 | 0.66549 | 1.0663 | 0.048749 | -0.13119 | 122.9253 | 122.8528 | 123.0224 | 52.6324 | -123.1192 | 122.8446 | 123.0224 | 122.8424 | 42.3885 | -123.3744
1188.7969 | 123.2254 | -65.3732 | 57.6141 | 0.0018314 | -0.010758 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | 0.00025007 | 0.001534 | 0.058238 | 0.017634 | 0.059287 | -64.7465 | -12.9286 | -65.107 | 57.5567 | 57.4659 | 57.6538 | -65.5142 | -64.2383 | -23.1175 | -64.6986 | 57.4576 | 57.6583 | 57.5242 | -65.7694 | -0.14097 | -0.057457 | 0.62672 | 0.26625 | 0.40723 | -0.14827 | 0.039656 | -0.39621 | -0.15651 | 1.135 | 0.67465 | 1.0709 | 0.044176 | -0.089981 | 122.9299 | 122.8391 | 123.027 | 52.4447 | -123.1283 | 122.8309 | 123.0315 | 122.8974 | 42.2557 | -123.3836
1189.7969 | 123.2025 | -65.3641 | 57.5775 | -0.0057996 | -0.010758 | 0.0010342 | 0.056438 | -0.0022669 | 0.061727 | -0.0093855 | 3.6274e-05 | 0.001534 | 0.058666 | 0.017848 | 0.059287 | -64.7236 | -13.098 | -65.0887 | 57.5567 | 57.475 | 57.6721 | -65.5142 | -64.2016 | -23.2229 | -64.6894 | 57.4759 | 57.6675 | 57.5104 | -65.7603 | -0.15013 | -0.020836 | 0.64045 | 0.27541 | 0.42554 | -0.10249 | 0.094592 | -0.39621 | -0.10157 | 1.1625 | 0.67466 | 1.0709 | 0.089954 | -0.067095 | 122.9208 | 122.8391 | 123.0362 | 52.2661 | -123.0917 | 122.84 | 123.0315 | 122.8745 | 42.1412 | -123.3378
1190.7969 | 123.2254 | -65.3732 | 57.6187 | -0.0057996 | -0.010545 | 0.0010342 | 0.056011 | -0.0026943 | 0.061727 | -0.001755 | 0.00025007 | 0.001534 | 0.058238 | 0.017634 | 0.059287 | -64.7099 | -13.2674 | -65.0704 | 57.575 | 57.4796 | 57.6721 | -65.505 | -64.1741 | -23.3327 | -64.6665 | 57.4897 | 57.6812 | 57.4921 | -65.7557 | -0.13182 | -0.04372 | 0.66334 | 0.30288 | 0.43469 | -0.13911 | 0.053394 | -0.38247 | -0.12903 | 1.1991 | 0.7067 | 1.0892 | 0.062492 | -0.12661 | 122.9482 | 122.8528 | 123.0453 | 52.1058 | -123.1238 | 122.8629 | 123.0544 | 122.8653 | 42.0405 | -123.3744
1191.7969 | 123.2574 | -65.3458 | 57.5912 | -0.013431 | -0.010758 | 0.0010342 | 0.056224 | -0.0022669 | 0.061514 | -0.0093855 | 3.6274e-05 | 0.0013204 | 0.058238 | 0.017634 | 0.059287 | -64.687 | -13.4322 | -65.0566 | 57.5842 | 57.5025 | 57.6813 | -65.4959 | -64.1513 | -23.4335 | -64.6391 | 57.4988 | 57.6858 | 57.5104 | -65.742 | -0.15013 | -0.007098 | 0.65877 | 0.28915 | 0.43927 | -0.088755 | 0.090016 | -0.3962 | -0.09241 | 1.1945 | 0.70671 | 1.1029 | 0.094536 | -0.080828 | 122.9299 | 122.8483 | 123.027 | 51.9136 | -123.0871 | 122.8446 | 123.0315 | 122.8562 | 41.9123 | -123.3332
1192.7969 | 123.2117 | -65.3183 | 57.6279 | -0.0057996 | -0.010972 | 0.0010342 | 0.056224 | -0.0026943 | 0.061727 | -0.0093855 | 3.6274e-05 | 0.001534 | 0.058238 | 0.017634 | 0.059287 | -64.6733 | -13.6108 | -65.0475 | 57.5979 | 57.5025 | 57.6904 | -65.4776 | -64.1238 | -23.5479 | -64.6253 | 57.5034 | 57.6995 | 57.5425 | -65.7374 | -0.15928 | -0.029984 | 0.64504 | 0.27084 | 0.43011 | -0.12538 | 0.062552 | -0.41909 | -0.12445 | 1.1945 | 0.69298 | 1.1121 | 0.071651 | -0.085399 | 122.9162 | 122.8208 | 123.0087 | 51.7075 | -123.1054 | 122.8217 | 123.0178 | 122.8608 | 41.7704 | -123.3653
1193.7969 | 123.1934 | -65.3 | 57.6508 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0024807 | 0.061514 | -0.001755 | -0.00017733 | 0.0017478 | 0.058025 | 0.017848 | 0.0595 | -64.6549 | -13.8351 | -65.0246 | 57.5979 | 57.5071 | 57.6996 | -65.4684 | -64.0963 | -23.7082 | -64.6024 | 57.5172 | 57.7041 | 57.4829 | -65.7145 | -0.16843 | -0.052872 | 0.64504 | 0.27542 | 0.44384 | -0.14368 | 0.048821 | -0.41451 | -0.1336 | 1.2037 | 0.69756 | 1.1121 | 0.053341 | -0.16781 | 122.8979 | 122.8071 | 122.9996 | 51.4649 | -123.1192 | 122.8171 | 123.0041 | 122.7829 | 41.5918 | -123.3653
1194.7969 | 123.2391 | -65.3 | 57.6416 | 0.0094624 | -0.010758 | 0.00082041 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | 0.00025007 | 0.0017478 | 0.058238 | 0.018062 | 0.0595 | -64.6458 | -14.0183 | -65.02 | 57.6162 | 57.5208 | 57.7087 | -65.4593 | -64.0688 | -23.8318 | -64.575 | 57.5217 | 57.7178 | 57.5013 | -65.7099 | -0.15927 | -0.025404 | 0.6542 | 0.27999 | 0.43927 | -0.12079 | 0.067133 | -0.40993 | -0.11987 | 1.2311 | 0.72504 | 1.135 | 0.076232 | -0.14034 | 122.9162 | 122.8208 | 123.0087 | 51.2817 | -123.1009 | 122.8217 | 123.0178 | 122.8012 | 41.4682 | -123.3515
1195.7969 | 123.1705 | -65.3091 | 57.6645 | -0.0057996 | -0.010545 | 0.00060681 | 0.056224 | -0.0022669 | 0.062155 | -0.001755 | 0.00025007 | 0.0017478 | 0.058452 | 0.017634 | 0.0595 | -64.6183 | -14.1968 | -65.0017 | 57.6254 | 57.5254 | 57.727 | -65.4547 | -64.0459 | -23.9509 | -64.5612 | 57.5263 | 57.7316 | 57.5379 | -65.7008 | -0.14554 | -0.039135 | 0.69082 | 0.30746 | 0.453 | -0.1391 | 0.06256 | -0.39162 | -0.13818 | 1.2632 | 0.74793 | 1.1395 | 0.06708 | -0.1266 | 122.9345 | 122.8345 | 123.0362 | 51.1123 | -123.1192 | 122.8355 | 123.0407 | 122.847 | 41.3583 | -123.3652
1196.7969 | 123.2483 | -65.2817 | 57.6599 | 0.0094624 | -0.010758 | 0.00060681 | 0.056224 | -0.0026943 | 0.061727 | 0.0058755 | -0.00017733 | 0.001534 | 0.058452 | 0.017634 | 0.0595 | -64.6 | -14.3846 | -64.9879 | 57.6345 | 57.5391 | 57.7362 | -65.4455 | -64.0139 | -24.1111 | -64.5292 | 57.54 | 57.7361 | 57.4143 | -65.6916 | -0.16384 | -0.0254 | 0.68167 | 0.29373 | 0.45758 | -0.12079 | 0.076295 | -0.40993 | -0.11987 | 1.2678 | 0.75251 | 1.1624 | 0.076236 | -0.24564 | 122.9162 | 122.8208 | 123.0179 | 50.8971 | -123.1054 | 122.8217 | 123.0178 | 122.6959 | 41.1706 | -123.3515
1197.7969 | 123.1796 | -65.2863 | 57.6645 | -0.013431 | -0.010545 | 0.00060681 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | -0.00017733 | 0.001534 | 0.058238 | 0.017848 | 0.0595 | -64.5863 | -14.5814 | -64.9696 | 57.6437 | 57.5437 | 57.7408 | -65.4409 | -63.9864 | -24.2485 | -64.5063 | 57.5538 | 57.7407 | 57.4555 | -65.6779 | -0.15469 | -0.020821 | 0.69998 | 0.31662 | 0.47131 | -0.12079 | 0.076296 | -0.39161 | -0.11071 | 1.2998 | 0.77998 | 1.1716 | 0.076237 | -0.20901 | 122.9299 | 122.83 | 123.027 | 50.7048 | -123.1054 | 122.84 | 123.027 | 122.7417 | 41.0378 | -123.3424
1198.7969 | 123.2574 | -65.2954 | 57.6965 | 0.0094624 | -0.010758 | 0.0010342 | 0.056224 | -0.0024807 | 0.061727 | -0.0093855 | 3.6274e-05 | 0.001534 | 0.058879 | 0.018062 | 0.0595 | -64.5725 | -14.7509 | -64.9651 | 57.6528 | 57.5529 | 57.7454 | -65.4364 | -63.9635 | -24.3492 | -64.4971 | 57.5584 | 57.7499 | 57.5654 | -65.6779 | -0.14095 | -0.043708 | 0.72288 | 0.33036 | 0.47131 | -0.14367 | 0.048831 | -0.38245 | -0.13818 | 1.3319 | 0.7983 | 1.1808 | 0.053351 | -0.13117 | 122.9482 | 122.8483 | 123.0408 | 50.5446 | -123.1329 | 122.8538 | 123.0453 | 122.8608 | 40.9462 | -123.3744
1199.7969 | 123.1979 | -65.2588 | 57.7011 | -0.0057996 | -0.010545 | 0.0010342 | 0.056438 | -0.0024807 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.001534 | 0.058025 | 0.017848 | 0.059073 | -64.568 | -14.934 | -64.9422 | 57.6482 | 57.5666 | 57.7591 | -65.4318 | -63.9452 | -24.4179 | -64.4834 | 57.5629 | 57.7545 | 57.5242 | -65.6733 | -0.173 | -0.052864 | 0.69083 | 0.31663 | 0.48962 | -0.13451 | 0.057989 | -0.4145 | -0.13817 | 1.3136 | 0.77541 | 1.1899 | 0.053352 | -0.17696 | 122.907 | 122.8254 | 123.0179 | 50.3248 | -123.1329 | 122.8217 | 123.0133 | 122.7829 | 40.8409 | -123.3744
1200.7969 | 123.1613 | -65.2908 | 57.7332 | 0.0018314 | -0.010758 | 0.00060681 | 0.056011 | -0.0029079 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.001534 | 0.058452 | 0.018062 | 0.0595 | -64.5451 | -15.1034 | -64.9376 | 57.6574 | 57.5803 | 57.7683 | -65.418 | -63.9177 | -24.5415 | -64.4467 | 57.5721 | 57.7636 | 57.5425 | -65.6733 | -0.12721 | -0.07575 | 0.74577 | 0.35325 | 0.48046 | -0.15282 | 0.035103 | -0.38245 | -0.16106 | 1.3731 | 0.84409 | 1.2265 | 0.030466 | -0.19068 | 122.9482 | 122.8712 | 123.0591 | 50.1874 | -123.1512 | 122.8629 | 123.0545 | 122.8333 | 40.7493 | -123.4064
1201.7969 | 123.2117 | -65.2359 | 57.7057 | -0.0057996 | -0.010758 | 0.00082041 | 0.056438 | -0.0024807 | 0.061941 | -0.001755 | 3.6274e-05 | 0.0017478 | 0.058452 | 0.018062 | 0.0595 | -64.5268 | -15.2911 | -64.9193 | 57.6803 | 57.5895 | 57.7774 | -65.3997 | -63.8857 | -24.6194 | -64.4239 | 57.5904 | 57.7819 | 57.6203 | -65.6412 | -0.16383 | -0.025392 | 0.70915 | 0.31663 | 0.48046 | -0.1162 | 0.071726 | -0.40533 | -0.11528 | 1.3502 | 0.81205 | 1.2174 | 0.076246 | -0.085382 | 122.9162 | 122.8254 | 123.0133 | 49.9448 | -123.1054 | 122.8263 | 123.0178 | 122.8562 | 40.6165 | -123.3469
1202.7969 | 123.2208 | -65.2313 | 57.7423 | 0.0094624 | -0.010972 | 0.0010342 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.0019614 | 0.058666 | 0.018062 | 0.059287 | -64.5039 | -15.4743 | -64.9055 | 57.6757 | 57.5941 | 57.7866 | -65.3997 | -63.8536 | -24.7247 | -64.401 | 57.595 | 57.7819 | 57.515 | -65.6458 | -0.16841 | -0.066593 | 0.72746 | 0.32579 | 0.4942 | -0.14824 | 0.044262 | -0.41449 | -0.14732 | 1.3777 | 0.83036 | 1.2449 | 0.039624 | -0.22731 | 122.907 | 122.8254 | 123.0179 | 49.7571 | -123.142 | 122.8263 | 123.0133 | 122.7463 | 40.5066 | -123.3881
1203.7969 | 123.2208 | -65.2222 | 57.7148 | 0.0094624 | -0.010758 | 0.00060681 | 0.056438 | -0.0026943 | 0.061727 | 0.0058755 | -0.00039093 | 0.0017478 | 0.058452 | 0.018062 | 0.059714 | -64.4947 | -15.6986 | -64.8964 | 57.6849 | 57.6032 | 57.7866 | -65.386 | -63.8353 | -24.7796 | -64.401 | 57.5996 | 57.7865 | 57.5883 | -65.6367 | -0.16383 | -0.02997 | 0.72747 | 0.32579 | 0.48962 | -0.11161 | 0.071728 | -0.41449 | -0.11528 | 1.3868 | 0.82121 | 1.2357 | 0.071669 | -0.12659 | 122.907 | 122.8254 | 123.0087 | 49.5235 | -123.1008 | 122.8217 | 123.0087 | 122.8104 | 40.4425 | -123.3515
1204.7969 | 123.1247 | -65.2176 | 57.7194 | 0.0018314 | -0.010972 | 0.00060681 | 0.056011 | -0.0026943 | 0.062155 | 0.0058755 | -0.00017733 | 0.0017478 | 0.058666 | 0.018062 | 0.059714 | -64.481 | -15.8955 | -64.8872 | 57.6849 | 57.6078 | 57.7866 | -65.3952 | -63.8124 | -24.8575 | -64.3735 | 57.5996 | 57.7819 | 57.5379 | -65.6321 | -0.17756 | -0.034547 | 0.73662 | 0.33037 | 0.50793 | -0.11161 | 0.067151 | -0.41449 | -0.11986 | 1.4052 | 0.8441 | 1.2586 | 0.062513 | -0.18153 | 122.9025 | 122.8254 | 123.0042 | 49.3221 | -123.1146 | 122.8172 | 122.9995 | 122.7555 | 40.3601 | -123.3515
1205.7969 | 123.1384 | -65.2588 | 57.7881 | 0.0018314 | -0.011186 | 0.0010342 | 0.055797 | -0.0026943 | 0.061941 | 0.0058755 | -0.00039093 | 0.001534 | 0.058666 | 0.018062 | 0.059714 | -64.4627 | -16.1153 | -64.8735 | 57.694 | 57.6124 | 57.8049 | -65.386 | -63.7895 | -24.9124 | -64.3552 | 57.6041 | 57.8002 | 57.6661 | -65.6321 | -0.12721 | -0.094055 | 0.79613 | 0.3853 | 0.51251 | -0.1757 | 0.0168 | -0.37329 | -0.18394 | 1.4693 | 0.90361 | 1.2769 | 0.012163 | -0.12199 | 122.9528 | 122.8712 | 123.0637 | 49.1435 | -123.1741 | 122.8629 | 123.059 | 122.9249 | 40.3464 | -123.4202
1206.7969 | 123.2346 | -65.1855 | 57.7423 | -0.0057996 | -0.010758 | 0.00082041 | 0.056011 | -0.0024807 | 0.061514 | 0.0058755 | 3.6274e-05 | 0.0019614 | 0.058238 | 0.018062 | 0.059927 | -64.4398 | -16.3488 | -64.8506 | 57.7078 | 57.6215 | 57.8095 | -65.3677 | -63.7529 | -25.0223 | -64.3277 | 57.6179 | 57.8048 | 57.6295 | -65.6183 | -0.18213 | -0.034544 | 0.74578 | 0.33495 | 0.51708 | -0.12077 | 0.067155 | -0.43279 | -0.12443 | 1.4326 | 0.85785 | 1.2906 | 0.062517 | -0.11285 | 122.8933 | 122.8071 | 122.995 | 48.8368 | -123.11 | 122.8034 | 122.9904 | 122.815 | 40.1633 | -123.3607
1207.7969 | 123.262 | -65.1993 | 57.7423 | 0.0018314 | -0.011186 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | -0.001755 | 3.6274e-05 | 0.001534 | 0.058238 | 0.018062 | 0.059287 | -64.4352 | -16.5365 | -64.8414 | 57.7078 | 57.6261 | 57.8095 | -65.3677 | -63.73 | -25.1093 | -64.3231 | 57.627 | 57.8048 | 57.6386 | -65.6138 | -0.1684 | -0.034544 | 0.7641 | 0.35784 | 0.52624 | -0.11619 | 0.067155 | -0.41448 | -0.11527 | 1.4693 | 0.87616 | 1.2906 | 0.062517 | -0.10369 | 122.907 | 122.8254 | 123.0087 | 48.6628 | -123.11 | 122.8263 | 123.0041 | 122.8379 | 40.09 | -123.3561
1208.7969 | 123.1522 | -65.2405 | 57.8156 | -0.013431 | -0.010972 | 0.00082041 | 0.055797 | -0.0022669 | 0.061941 | 0.0058755 | -0.00017733 | 0.001534 | 0.058666 | 0.017848 | 0.0595 | -64.4031 | -16.7563 | -64.8323 | 57.7169 | 57.6215 | 57.814 | -65.3585 | -63.6888 | -25.1276 | -64.2911 | 57.6225 | 57.8094 | 57.5974 | -65.6092 | -0.11804 | -0.098629 | 0.83734 | 0.40819 | 0.52624 | -0.19401 | -0.001509 | -0.3687 | -0.19309 | 1.5517 | 0.94941 | 1.3181 | -0.006146 | -0.21814 | 122.9574 | 122.862 | 123.0545 | 48.4842 | -123.1741 | 122.8629 | 123.0499 | 122.8379 | 40.1129 | -123.4247
1209.7969 | 123.2849 | -65.181 | 57.7515 | 0.0018314 | -0.010972 | 0.00060681 | 0.056438 | -0.0022669 | 0.061941 | -0.001755 | 3.6274e-05 | 0.0017478 | 0.058238 | 0.017848 | 0.059287 | -64.394 | -16.9348 | -64.8185 | 57.7215 | 57.6353 | 57.8324 | -65.3585 | -63.6659 | -25.2238 | -64.2636 | 57.6362 | 57.8277 | 57.5928 | -65.6 | -0.17755 | -0.029964 | 0.78699 | 0.36242 | 0.53997 | -0.11618 | 0.080893 | -0.41906 | -0.11527 | 1.5151 | 0.91737 | 1.3364 | 0.076255 | -0.15863 | 122.9025 | 122.8163 | 123.0133 | 48.2461 | -123.11 | 122.8172 | 123.0087 | 122.7738 | 39.9572 | -123.3515
1210.7969 | 123.1705 | -65.2176 | 57.7972 | 0.0094624 | -0.010758 | 0.00039321 | 0.056224 | -0.0024807 | 0.061941 | -0.001755 | -0.00017733 | 0.002175 | 0.058452 | 0.018062 | 0.059714 | -64.3711 | -17.1775 | -64.7957 | 57.7398 | 57.6399 | 57.8278 | -65.3402 | -63.6339 | -25.2604 | -64.2407 | 57.6454 | 57.8323 | 57.6432 | -65.5954 | -0.12262 | -0.057426 | 0.8465 | 0.42193 | 0.54455 | -0.15738 | 0.030538 | -0.37786 | -0.15189 | 1.5837 | 0.97688 | 1.3547 | 0.035058 | -0.15404 | 122.9574 | 122.8575 | 123.0454 | 48.0401 | -123.1374 | 122.8629 | 123.0499 | 122.8608 | 39.9572 | -123.3927
1211.7969 | 123.2117 | -65.181 | 57.7789 | 0.0094624 | -0.010758 | 0.00082041 | 0.056224 | -0.0031215 | 0.061941 | 0.013506 | -0.00017733 | 0.001534 | 0.058452 | 0.018062 | 0.059714 | -64.3482 | -17.4522 | -64.7865 | 57.749 | 57.6536 | 57.8461 | -65.331 | -63.5927 | -25.3428 | -64.2087 | 57.6545 | 57.8415 | 57.5883 | -65.5771 | -0.15008 | -0.029959 | 0.83277 | 0.39447 | 0.54455 | -0.12533 | 0.067163 | -0.39616 | -0.12442 | 1.5883 | 0.97231 | 1.3685 | 0.062525 | -0.19067 | 122.9299 | 122.8346 | 123.0271 | 47.7287 | -123.11 | 122.8355 | 123.0224 | 122.7692 | 39.8382 | -123.3561
1212.7969 | 123.2208 | -65.1535 | 57.8156 | -0.013431 | -0.011186 | 0.0010342 | 0.056011 | -0.0024807 | 0.061514 | -0.001755 | -0.00017733 | 0.0019614 | 0.058238 | 0.018275 | 0.059714 | -64.3345 | -17.6354 | -64.7682 | 57.7535 | 57.6719 | 57.8598 | -65.3265 | -63.5652 | -25.3886 | -64.1995 | 57.6637 | 57.8506 | 57.6707 | -65.5726 | -0.17297 | -0.062002 | 0.81904 | 0.38532 | 0.55828 | -0.14364 | 0.044277 | -0.41905 | -0.15189 | 1.5883 | 0.95401 | 1.3731 | 0.035062 | -0.14488 | 122.9071 | 122.8254 | 123.0133 | 47.5181 | -123.142 | 122.8172 | 123.0041 | 122.8242 | 39.7649 | -123.3881
1213.7969 | 123.23 | -65.1627 | 57.7789 | 0.0094624 | -0.010758 | 0.00060681 | 0.056011 | -0.0026943 | 0.062155 | -0.001755 | 0.00046367 | 0.0019614 | 0.058238 | 0.018489 | 0.059927 | -64.3161 | -17.8643 | -64.7636 | 57.749 | 57.6719 | 57.8598 | -65.3265 | -63.5377 | -25.4481 | -64.1766 | 57.6682 | 57.8598 | 57.6111 | -65.568 | -0.16381 | -0.029959 | 0.84651 | 0.39905 | 0.56286 | -0.10702 | 0.080898 | -0.40532 | -0.11069 | 1.625 | 0.98606 | 1.3914 | 0.08084 | -0.16778 | 122.9116 | 122.8346 | 123.0225 | 47.2984 | -123.1054 | 122.8309 | 123.0224 | 122.7738 | 39.7145 | -123.3469
1214.7969 | 123.1247 | -65.1627 | 57.8339 | 0.0094624 | -0.010545 | 0.0010342 | 0.056224 | -0.0022669 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.001534 | 0.058666 | 0.018062 | 0.059927 | -64.3024 | -18.107 | -64.7453 | 57.7673 | 57.6765 | 57.869 | -65.3173 | -63.5057 | -25.5122 | -64.1491 | 57.6682 | 57.8598 | 57.6569 | -65.5588 | -0.15465 | -0.066577 | 0.86025 | 0.41736 | 0.57202 | -0.15737 | 0.035125 | -0.39616 | -0.16562 | 1.657 | 1.0135 | 1.4097 | 0.025909 | -0.17693 | 122.9299 | 122.8392 | 123.0316 | 47.0557 | -123.1512 | 122.8309 | 123.0224 | 122.8196 | 39.6504 | -123.3927
1215.7969 | 123.23 | -65.2267 | 57.8247 | 0.0018314 | -0.010972 | 0.00082041 | 0.055797 | -0.0024807 | 0.062155 | -0.0093855 | 0.00025007 | 0.001534 | 0.058238 | 0.018275 | 0.059927 | -64.2749 | -18.3222 | -64.727 | 57.7719 | 57.6811 | 57.8736 | -65.3173 | -63.4644 | -25.5488 | -64.1262 | 57.6866 | 57.8643 | 57.6661 | -65.5497 | -0.090565 | -0.052844 | 0.95181 | 0.49976 | 0.59033 | -0.14364 | 0.048858 | -0.32291 | -0.13815 | 1.7623 | 1.1005 | 1.4234 | 0.039642 | -0.15861 | 122.9986 | 122.9078 | 123.1003 | 46.9046 | -123.142 | 122.9133 | 123.0911 | 122.8928 | 39.6779 | -123.3744
1216.7969 | 123.1201 | -65.1718 | 57.8705 | 0.0018314 | -0.010972 | 0.00060681 | 0.055797 | -0.0024807 | 0.061727 | -0.001755 | 0.00067727 | 0.0019614 | 0.058452 | 0.018275 | 0.060141 | -64.2566 | -18.5236 | -64.7178 | 57.7764 | 57.6948 | 57.8827 | -65.3127 | -63.4416 | -25.5855 | -64.1171 | 57.6866 | 57.8735 | 57.6615 | -65.5542 | -0.14092 | -0.094041 | 0.91519 | 0.45399 | 0.5949 | -0.17567 | 0.012239 | -0.38242 | -0.18393 | 1.7303 | 1.0547 | 1.4372 | 0.003024 | -0.20897 | 122.9483 | 122.8666 | 123.0545 | 46.6482 | -123.1832 | 122.8584 | 123.0453 | 122.8333 | 39.5863 | -123.4247
1217.7969 | 123.2162 | -65.1306 | 57.8384 | -0.0057996 | -0.010972 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | 0.00025007 | 0.0017478 | 0.058666 | 0.018703 | 0.059927 | -64.2429 | -18.7571 | -64.7087 | 57.7856 | 57.6902 | 57.8873 | -65.299 | -63.4141 | -25.5717 | -64.0896 | 57.6911 | 57.8827 | 57.6661 | -65.5497 | -0.16838 | -0.052841 | 0.88772 | 0.42195 | 0.59033 | -0.14821 | 0.048861 | -0.41904 | -0.14731 | 1.7165 | 1.041 | 1.46 | 0.044224 | -0.17235 | 122.9162 | 122.8208 | 123.0179 | 46.3735 | -123.1374 | 122.8217 | 123.0133 | 122.7967 | 39.5589 | -123.3881
1218.7969 | 123.143 | -65.1306 | 57.8751 | 0.017093 | -0.010972 | 0.0010342 | 0.056011 | -0.0024807 | 0.062155 | 0.0058755 | 0.00025007 | 0.0019614 | 0.058452 | 0.018275 | 0.059714 | -64.2337 | -18.9906 | -64.6812 | 57.7902 | 57.6948 | 57.8919 | -65.2853 | -63.3683 | -25.5717 | -64.0713 | 57.6957 | 57.8827 | 57.6844 | -65.5359 | -0.15464 | -0.084884 | 0.89688 | 0.44942 | 0.60406 | -0.18025 | 0.016819 | -0.40531 | -0.17935 | 1.7623 | 1.0593 | 1.4646 | 0.007603 | -0.19065 | 122.9208 | 122.8254 | 123.0225 | 46.14 | -123.1603 | 122.8263 | 123.0133 | 122.815 | 39.5589 | -123.411
1219.7969 | 123.2346 | -65.1077 | 57.8476 | 0.0018314 | -0.010545 | 0.00082041 | 0.056224 | -0.0022669 | 0.062368 | -0.001755 | 0.00046367 | 0.0017478 | 0.058666 | 0.018275 | 0.059073 | -64.2017 | -19.2196 | -64.6675 | 57.7993 | 57.704 | 57.8965 | -65.2853 | -63.3317 | -25.5763 | -64.0438 | 57.7049 | 57.9101 | 57.6615 | -65.5268 | -0.17753 | -0.048261 | 0.90604 | 0.44026 | 0.61779 | -0.14363 | 0.048863 | -0.41904 | -0.14272 | 1.7761 | 1.0639 | 1.4829 | 0.06254 | -0.18608 | 122.9071 | 122.8117 | 123.0042 | 45.8882 | -123.1329 | 122.8126 | 123.0179 | 122.7692 | 39.5314 | -123.3744
1220.7969 | 123.1293 | -65.1718 | 57.843 | -0.0057996 | -0.010758 | 0.0010342 | 0.056011 | -0.0024807 | 0.062368 | -0.001755 | 3.6274e-05 | 0.0017478 | 0.058238 | 0.018489 | 0.059927 | -64.1788 | -19.4393 | -64.6537 | 57.8085 | 57.7177 | 57.9102 | -65.2807 | -63.3042 | -25.5534 | -64.0163 | 57.7094 | 57.9147 | 57.6432 | -65.5222 | -0.10887 | -0.034527 | 0.99302 | 0.51808 | 0.62695 | -0.12532 | 0.067176 | -0.35037 | -0.13357 | 1.8676 | 1.1555 | 1.5058 | 0.071696 | -0.19982 | 122.9803 | 122.8895 | 123.082 | 45.7325 | -123.1237 | 122.8813 | 123.0865 | 122.815 | 39.6184 | -123.3652
1221.7969 | 123.2208 | -65.1077 | 57.8567 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0022669 | 0.061941 | 0.0058755 | 3.6274e-05 | 0.002175 | 0.058452 | 0.018275 | 0.059927 | -64.1696 | -19.6728 | -64.64 | 57.8039 | 57.7223 | 57.9102 | -65.2669 | -63.2538 | -25.6313 | -63.9843 | 57.7278 | 57.9147 | 57.7577 | -65.5176 | -0.15922 | -0.052838 | 0.93809 | 0.46773 | 0.62695 | -0.13447 | 0.053444 | -0.40988 | -0.12899 | 1.8539 | 1.1234 | 1.5333 | 0.057964 | -0.099086 | 122.9116 | 122.83 | 123.0179 | 45.4349 | -123.1237 | 122.8355 | 123.0224 | 122.8654 | 39.4765 | -123.3744
1222.7969 | 123.1201 | -65.1215 | 57.8888 | -0.0057996 | -0.010545 | 0.00060681 | 0.055797 | -0.0026943 | 0.061727 | -0.001755 | 0.00046367 | 0.0017478 | 0.058452 | 0.018703 | 0.060141 | -64.1422 | -19.9109 | -64.6263 | 57.8176 | 57.7131 | 57.9239 | -65.2715 | -63.2355 | -25.5763 | -63.9706 | 57.7278 | 57.9239 | 57.6752 | -65.513 | -0.15006 | -0.071147 | 0.97929 | 0.4952 | 0.64526 | -0.17567 | 0.035136 | -0.39157 | -0.16103 | 1.8859 | 1.1509 | 1.5425 | 0.035077 | -0.21354 | 122.9391 | 122.8346 | 123.0454 | 45.2105 | -123.1603 | 122.8492 | 123.0453 | 122.7967 | 39.5451 | -123.4018
1223.7969 | 123.1613 | -65.1077 | 57.8659 | 0.0018314 | -0.010972 | 0.0010342 | 0.056224 | -0.0022669 | 0.061727 | -0.001755 | 0.00067727 | 0.0019614 | 0.058238 | 0.018275 | 0.060141 | -64.1239 | -20.1536 | -64.6171 | 57.8085 | 57.7223 | 57.9148 | -65.2624 | -63.2035 | -25.558 | -63.9522 | 57.7278 | 57.9147 | 57.6524 | -65.513 | -0.15464 | -0.057415 | 0.98387 | 0.49062 | 0.64526 | -0.14362 | 0.048867 | -0.4053 | -0.13814 | 1.9043 | 1.1555 | 1.5608 | 0.048808 | -0.21355 | 122.9162 | 122.83 | 123.0225 | 44.9541 | -123.1283 | 122.8355 | 123.0224 | 122.7601 | 39.5497 | -123.3789
1224.7969 | 123.1293 | -65.1352 | 57.8888 | -0.0057996 | -0.010758 | 0.00082041 | 0.056011 | -0.0024807 | 0.061941 | 0.0058755 | 0.00046367 | 0.0017478 | 0.058666 | 0.018703 | 0.0595 | -64.1193 | -20.378 | -64.6079 | 57.8314 | 57.7314 | 57.9194 | -65.2578 | -63.1668 | -25.5259 | -63.9248 | 57.7323 | 57.9193 | 57.7073 | -65.5084 | -0.12259 | -0.057412 | 1.0159 | 0.52725 | 0.64984 | -0.15735 | 0.030557 | -0.37326 | -0.15645 | 1.9684 | 1.2104 | 1.5837 | 0.030499 | -0.18149 | 122.9666 | 122.8666 | 123.0545 | 44.7572 | -123.1466 | 122.8675 | 123.0545 | 122.8425 | 39.6092 | -123.3972
1225.7969 | 123.2254 | -65.0986 | 57.8659 | -0.021062 | -0.010758 | 0.00082041 | 0.056438 | -0.0022669 | 0.061514 | 0.0058755 | 0.00025007 | 0.002175 | 0.058452 | 0.018489 | 0.060141 | -64.0964 | -20.5886 | -64.5896 | 57.8268 | 57.7269 | 57.9239 | -65.2532 | -63.1302 | -25.5076 | -63.9065 | 57.7323 | 57.9239 | 57.7348 | -65.4993 | -0.15463 | -0.039102 | 1.0022 | 0.50894 | 0.66357 | -0.13905 | 0.058024 | -0.40072 | -0.13357 | 1.9684 | 1.1921 | 1.5928 | 0.057965 | -0.13114 | 122.9254 | 122.8254 | 123.0225 | 44.51 | -123.1191 | 122.8309 | 123.0224 | 122.8333 | 39.5909 | -123.3652
1226.7969 | 123.1247 | -65.1718 | 57.8796 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0024807 | 0.062155 | 0.0058755 | 0.00025007 | 0.0019614 | 0.058452 | 0.018275 | 0.060141 | -64.1147 | -21.0052 | -64.6171 | 57.7948 | 57.704 | 57.8965 | -65.299 | -63.1577 | -25.439 | -63.9156 | 57.6957 | 57.8872 | 57.6936 | -65.5359 | -0.12718 | -0.084884 | 1.0571 | 0.55471 | 0.68189 | -0.17567 | 0.016819 | -0.36411 | -0.18393 | 2.0141 | 1.2562 | 1.6203 | 0.007603 | -0.18607 | 122.9666 | 122.8758 | 123.0683 | 44.1666 | -123.1786 | 122.8675 | 123.0591 | 122.8654 | 39.7329 | -123.4156
1227.7969 | 123.2162 | -65.1077 | 57.8522 | -0.0057996 | -0.010758 | 0.00082041 | 0.056438 | -0.0024807 | 0.062155 | 0.0058755 | 0.00025007 | 0.0019614 | 0.058452 | 0.018275 | 0.059927 | -64.1055 | -21.2296 | -64.5942 | 57.7948 | 57.6994 | 57.8873 | -65.2898 | -63.1348 | -25.3886 | -63.8973 | 57.7003 | 57.8918 | 57.6936 | -65.5451 | -0.18211 | -0.057418 | 1.0022 | 0.51351 | 0.69562 | -0.15279 | 0.035128 | -0.43735 | -0.15188 | 1.9729 | 1.2104 | 1.6478 | 0.039648 | -0.15861 | 122.9025 | 122.8071 | 122.995 | 43.8782 | -123.142 | 122.808 | 122.9995 | 122.8013 | 39.7191 | -123.3973
1228.7969 | 123.1384 | -65.1627 | 57.8842 | -0.0057996 | -0.010758 | 0.00082041 | 0.056011 | -0.0024807 | 0.062155 | 0.0058755 | 0.00046367 | 0.0017478 | 0.058452 | 0.018916 | 0.059927 | -64.0826 | -21.4906 | -64.5851 | 57.7902 | 57.6948 | 57.8827 | -65.2898 | -63.1165 | -25.2375 | -63.8836 | 57.7049 | 57.8918 | 57.721 | -65.5313 | -0.12718 | -0.094039 | 1.08 | 0.5776 | 0.70478 | -0.18941 | -0.001494 | -0.36868 | -0.17935 | 2.0462 | 1.2791 | 1.6478 | 0.007605 | -0.16318 | 122.9528 | 122.8575 | 123.0454 | 43.6721 | -123.1741 | 122.8675 | 123.0545 | 122.8837 | 39.9252 | -123.4156
1229.7969 | 123.143 | -65.1535 | 57.8567 | 0.0018314 | -0.010758 | 0.00082041 | 0.056011 | -0.0022669 | 0.062155 | -0.001755 | 0.00046367 | 0.0019614 | 0.058666 | 0.018489 | 0.059927 | -64.0598 | -21.7653 | -64.5667 | 57.7948 | 57.7085 | 57.901 | -65.2853 | -63.0753 | -25.091 | -63.8698 | 57.7094 | 57.8964 | 57.6798 | -65.5268 | -0.13175 | -0.061995 | 1.0937 | 0.58676 | 0.71851 | -0.1482 | 0.044287 | -0.37326 | -0.1473 | 2.0782 | 1.2837 | 1.6569 | 0.03965 | -0.17692 | 122.9483 | 122.862 | 123.0545 | 43.3882 | -123.142 | 122.863 | 123.0499 | 122.8333 | 40.0625 | -123.3835
1230.7969 | 123.1247 | -65.1443 | 57.8613 | 0.0018314 | -0.010758 | 0.00082041 | 0.056011 | -0.0024807 | 0.062155 | 0.0058755 | 0.00046367 | 0.0017478 | 0.058452 | 0.018703 | 0.060141 | -64.0552 | -21.985 | -64.553 | 57.8039 | 57.736 | 57.9056 | -65.2761 | -63.0432 | -24.9399 | -63.8469 | 57.7094 | 57.901 | 57.7256 | -65.5268 | -0.13175 | -0.057416 | 1.0892 | 0.59134 | 0.72309 | -0.12531 | 0.044287 | -0.38242 | -0.15188 | 2.1011 | 1.2974 | 1.6798 | 0.03965 | -0.13571 | 122.9483 | 122.8804 | 123.05 | 43.1593 | -123.1374 | 122.8538 | 123.0453 | 122.87 | 40.2045 | -123.3881
1231.7969 | 123.175 | -65.1077 | 57.8613 | 0.0018314 | -0.010758 | 0.0012478 | 0.055797 | -0.0022669 | 0.062155 | 0.0058755 | 0.00025007 | 0.0019614 | 0.058666 | 0.018916 | 0.060141 | -64.0048 | -22.246 | -64.521 | 57.8222 | 57.7589 | 57.9239 | -65.2578 | -62.9883 | -24.9673 | -63.8011 | 57.7369 | 57.9239 | 57.7531 | -65.5039 | -0.15006 | -0.039102 | 1.1029 | 0.58677 | 0.73682 | -0.10242 | 0.062602 | -0.39614 | -0.12441 | 2.1195 | 1.3066 | 1.7027 | 0.062543 | -0.10824 | 122.93 | 122.8666 | 123.0317 | 42.8617 | -123.1191 | 122.8446 | 123.0316 | 122.8608 | 40.1404 | -123.3652
1232.7969 | 123.1293 | -65.126 | 57.9117 | 0.0094624 | -0.010758 | 0.0010342 | 0.056438 | -0.0024807 | 0.061941 | -0.001755 | 0.00046367 | 0.002175 | 0.058452 | 0.018916 | 0.060141 | -63.9865 | -22.507 | -64.5118 | 57.8222 | 57.7543 | 57.9285 | -65.2532 | -62.9562 | -24.8208 | -63.7828 | 57.7369 | 57.9239 | 57.7485 | -65.4993 | -0.12717 | -0.089456 | 1.1395 | 0.61423 | 0.7414 | -0.15735 | 0.016826 | -0.37325 | -0.17476 | 2.1698 | 1.3432 | 1.7165 | 0.012189 | -0.16318 | 122.9483 | 122.8804 | 123.0545 | 42.619 | -123.1649 | 122.863 | 123.0499 | 122.8745 | 40.3052 | -123.411
1233.7969 | 123.2666 | -65.0711 | 57.8751 | -0.0057996 | -0.010972 | 0.00082041 | 0.056224 | -0.0022669 | 0.061941 | -0.0093855 | 0.00067727 | 0.002175 | 0.058238 | 0.018916 | 0.059927 | -63.9728 | -22.7634 | -64.4889 | 57.8268 | 57.7543 | 57.9285 | -65.244 | -62.9104 | -24.6743 | -63.7691 | 57.7415 | 57.9284 | 57.7256 | -65.4947 | -0.17294 | -0.048257 | 1.0983 | 0.58219 | 0.75514 | -0.12073 | 0.053447 | -0.42361 | -0.13356 | 2.1607 | 1.302 | 1.7256 | 0.053389 | -0.14945 | 122.8979 | 122.8254 | 122.9996 | 42.3077 | -123.1191 | 122.8126 | 122.9996 | 122.7967 | 40.3968 | -123.3698
1234.7969 | 123.1705 | -65.1169 | 57.9346 | 0.0094624 | -0.010972 | 0.00082041 | 0.056438 | -0.0026943 | 0.062368 | 0.0058755 | 0.00046367 | 0.0017478 | 0.058666 | 0.01913 | 0.060568 | -63.9453 | -23.0198 | -64.4706 | 57.8451 | 57.7498 | 57.9377 | -65.2395 | -62.8692 | -24.5461 | -63.7325 | 57.7552 | 57.9422 | 57.7806 | -65.4856 | -0.12259 | -0.089452 | 1.1716 | 0.64628 | 0.76887 | -0.18482 | 0.003096 | -0.36867 | -0.17934 | 2.2477 | 1.3844 | 1.7531 | 0.007616 | -0.15401 | 122.962 | 122.8666 | 123.0545 | 42.0971 | -123.174 | 122.8721 | 123.0591 | 122.8974 | 40.5708 | -123.4201
1235.7969 | 123.2071 | -65.0482 | 57.8888 | 0.0018314 | -0.010758 | 0.0010342 | 0.056438 | -0.0022669 | 0.062368 | 0.021136 | 0.00067727 | 0.0017478 | 0.058452 | 0.019344 | 0.060355 | -63.9178 | -23.2854 | -64.4523 | 57.8451 | 57.7543 | 57.9468 | -65.2303 | -62.8326 | -24.4179 | -63.705 | 57.7552 | 57.933 | 57.7943 | -65.481 | -0.18209 | -0.043676 | 1.1304 | 0.59593 | 0.77802 | -0.13446 | 0.058029 | -0.43276 | -0.13356 | 2.2156 | 1.3432 | 1.776 | 0.044234 | -0.094501 | 122.8933 | 122.8026 | 122.995 | 41.7629 | -123.1191 | 122.8035 | 122.9812 | 122.8425 | 40.6303 | -123.3698
1236.7969 | 123.1476 | -65.0986 | 57.9163 | 0.0018314 | -0.010972 | 0.0010342 | 0.056224 | -0.0022669 | 0.062155 | -0.0093855 | 0.00067727 | 0.0019614 | 0.058238 | 0.018916 | 0.059927 | -63.8995 | -23.5509 | -64.4386 | 57.8497 | 57.7543 | 57.956 | -65.2303 | -62.7914 | -24.3355 | -63.6867 | 57.7552 | 57.9513 | 57.7577 | -65.4718 | -0.13174 | -0.066564 | 1.1991 | 0.66002 | 0.79176 | -0.16193 | 0.03972 | -0.37325 | -0.16103 | 2.3072 | 1.4119 | 1.7851 | 0.035083 | -0.1586 | 122.9483 | 122.8529 | 123.0546 | 41.5476 | -123.1466 | 122.8538 | 123.0499 | 122.8562 | 40.7631 | -123.3881
1237.7969 | 123.1338 | -65.0574 | 57.9254 | 0.0018314 | -0.010972 | 0.0010342 | 0.056224 | -0.0022669 | 0.062155 | -0.001755 | 0.00067727 | 0.0017478 | 0.058025 | 0.018916 | 0.059927 | -63.872 | -23.7753 | -64.4202 | 57.8589 | 57.7726 | 57.9606 | -65.2166 | -62.7364 | -24.1844 | -63.6638 | 57.7735 | 57.9697 | 57.7943 | -65.4627 | -0.1592 | -0.066562 | 1.1853 | 0.63714 | 0.79634 | -0.15277 | 0.035144 | -0.40529 | -0.15187 | 2.3209 | 1.3936 | 1.7989 | 0.044242 | -0.13112 | 122.9162 | 122.83 | 123.0179 | 41.2821 | -123.142 | 122.8309 | 123.027 | 122.8517 | 40.873 | -123.3881
1238.7969 | 123.1613 | -65.0436 | 57.9254 | -0.0057996 | -0.010972 | 0.0012478 | 0.056224 | -0.0026943 | 0.062582 | -0.0093855 | 0.00046367 | 0.0017478 | 0.058666 | 0.018703 | 0.059927 | -63.8492 | -24.0591 | -64.3928 | 57.868 | 57.7864 | 57.9789 | -65.212 | -62.6998 | -24.0241 | -63.6317 | 57.7735 | 57.9697 | 57.8218 | -65.4535 | -0.16836 | -0.057405 | 1.1945 | 0.65087 | 0.81923 | -0.13903 | 0.053458 | -0.40986 | -0.15187 | 2.3438 | 1.4119 | 1.8218 | 0.044242 | -0.10365 | 122.9116 | 122.83 | 123.0225 | 40.9845 | -123.1374 | 122.8172 | 123.0133 | 122.8654 | 41.0195 | -123.3789
1239.7969 | 123.2071 | -65.0482 | 57.9208 | -0.013431 | -0.010972 | 0.0010342 | 0.056438 | -0.0022669 | 0.061941 | -0.001755 | 0.00067727 | 0.0017478 | 0.058666 | 0.018489 | 0.060141 | -63.8171 | -24.2789 | -64.379 | 57.868 | 57.7864 | 57.9789 | -65.1983 | -62.654 | -23.8822 | -63.6043 | 57.7873 | 57.9834 | 57.7714 | -65.4489 | -0.15004 | -0.052827 | 1.2311 | 0.66918 | 0.81922 | -0.13445 | 0.058036 | -0.40071 | -0.13355 | 2.3942 | 1.444 | 1.8447 | 0.062556 | -0.14944 | 122.9162 | 122.8346 | 123.0271 | 40.7693 | -123.1191 | 122.8355 | 123.0316 | 122.8196 | 41.166 | -123.3698
1240.7969 | 123.1293 | -65.0665 | 57.9666 | 0.0018314 | -0.011186 | 0.0010342 | 0.056224 | -0.0020533 | 0.062155 | 0.0058755 | 0.00067727 | 0.002175 | 0.058452 | 0.018489 | 0.060355 | -63.7942 | -24.5491 | -64.347 | 57.8909 | 57.8001 | 57.9835 | -65.1845 | -62.6128 | -23.7494 | -63.5631 | 57.8056 | 57.9834 | 57.7851 | -65.4398 | -0.11799 | -0.075712 | 1.2723 | 0.71954 | 0.83754 | -0.16649 | 0.016838 | -0.37324 | -0.16102 | 2.4537 | 1.5035 | 1.8767 | 0.016779 | -0.18148 | 122.9574 | 122.8667 | 123.05 | 40.5175 | -123.1511 | 122.8721 | 123.0499 | 122.8517 | 41.3171 | -123.4064
1241.7969 | 123.1888 | -65.0162 | 57.962 | 0.0094624 | -0.011186 | 0.00082041 | 0.056224 | -0.0024807 | 0.061941 | 0.0058755 | 0.00089087 | 0.002175 | 0.058666 | 0.018703 | 0.060355 | -63.753 | -24.8009 | -64.3149 | 57.9046 | 57.8047 | 58.0155 | -65.1754 | -62.5533 | -23.5571 | -63.531 | 57.8148 | 57.9971 | 57.7943 | -65.426 | -0.15919 | -0.057399 | 1.2632 | 0.70124 | 0.86043 | -0.15733 | 0.053466 | -0.40986 | -0.14728 | 2.4629 | 1.4852 | 1.895 | 0.035093 | -0.16774 | 122.9208 | 122.8209 | 123.0317 | 40.2153 | -123.1374 | 122.8309 | 123.0133 | 122.8105 | 41.4591 | -123.3881
1242.7969 | 123.1522 | -65.0391 | 57.9803 | -0.0057996 | -0.011186 | 0.0012478 | 0.056224 | -0.0022669 | 0.062155 | -0.001755 | 0.00067727 | 0.002175 | 0.058666 | 0.018703 | 0.060355 | -63.7255 | -25.0802 | -64.2966 | 57.9184 | 57.823 | 58.0201 | -65.1754 | -62.5075 | -23.2549 | -63.499 | 57.8193 | 58.0109 | 57.8126 | -65.4077 | -0.1363 | -0.061975 | 1.3135 | 0.74244 | 0.87874 | -0.15733 | 0.039733 | -0.36865 | -0.16101 | 2.5316 | 1.5401 | 1.9088 | 0.030518 | -0.16774 | 122.9574 | 122.8621 | 123.0591 | 39.9589 | -123.1557 | 122.8584 | 123.0499 | 122.8517 | 41.7842 | -123.3881
1243.7969 | 123.143 | -65.0345 | 58.0032 | 0.0018314 | -0.011186 | 0.0010342 | 0.056438 | -0.0024807 | 0.062155 | 0.0058755 | 0.0011045 | 0.002175 | 0.058452 | 0.018916 | 0.060568 | -63.7072 | -25.3549 | -64.2783 | 57.9046 | 57.823 | 58.0063 | -65.1662 | -62.4663 | -23.0626 | -63.4623 | 57.8193 | 58.0109 | 57.7806 | -65.4077 | -0.13172 | -0.098598 | 1.3273 | 0.75617 | 0.88789 | -0.18022 | 0.00311 | -0.37323 | -0.1839 | 2.5682 | 1.5722 | 1.9454 | 0.00763 | -0.22268 | 122.9391 | 122.8575 | 123.0408 | 39.6796 | -123.1694 | 122.8538 | 123.0454 | 122.815 | 41.9719 | -123.4109
1244.7969 | 123.1659 | -65.0116 | 57.9758 | -0.013431 | -0.010758 | 0.0010342 | 0.056224 | -0.0022669 | 0.062368 | 0.013506 | 0.0011045 | 0.0019614 | 0.058452 | 0.018916 | 0.060355 | -63.6797 | -25.6388 | -64.26 | 57.9184 | 57.8184 | 58.0247 | -65.157 | -62.4251 | -22.8657 | -63.4303 | 57.8285 | 58.02 | 57.8813 | -65.4031 | -0.14545 | -0.057397 | 1.3318 | 0.7516 | 0.89705 | -0.15733 | 0.04889 | -0.39154 | -0.14728 | 2.5865 | 1.5813 | 1.9729 | 0.044253 | -0.094483 | 122.93 | 122.83 | 123.0363 | 39.3728 | -123.1328 | 122.8401 | 123.0316 | 122.8929 | 42.1459 | -123.3789
1245.7969 | 123.2529 | -64.9933 | 57.9666 | 0.0018314 | -0.010758 | 0.0012478 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | 0.0011045 | 0.0023888 | 0.058238 | 0.018703 | 0.060568 | -63.6614 | -25.886 | -64.2371 | 57.9184 | 57.8322 | 58.0201 | -65.1616 | -62.3747 | -22.6414 | -63.4028 | 57.8331 | 58.02 | 57.8218 | -65.394 | -0.16834 | -0.048242 | 1.3318 | 0.75618 | 0.92452 | -0.13444 | 0.053466 | -0.40069 | -0.13355 | 2.6186 | 1.5905 | 1.9912 | 0.053408 | -0.14485 | 122.9117 | 122.8255 | 123.0134 | 39.1073 | -123.1282 | 122.8264 | 123.0133 | 122.8151 | 42.3519 | -123.3606
1246.7969 | 123.1201 | -65.0299 | 58.0032 | -0.0057996 | -0.010545 | 0.0010342 | 0.056011 | -0.0024807 | 0.062155 | -0.001755 | 0.00089087 | 0.0019614 | 0.058666 | 0.018916 | 0.060355 | -63.634 | -26.1424 | -64.2142 | 57.9321 | 57.8368 | 58.0338 | -65.1525 | -62.3198 | -22.4445 | -63.3662 | 57.8422 | 58.0383 | 57.8447 | -65.394 | -0.12256 | -0.071128 | 1.3959 | 0.81569 | 0.93825 | -0.16648 | 0.030581 | -0.36407 | -0.16101 | 2.7101 | 1.6637 | 2.0278 | 0.035101 | -0.15858 | 122.962 | 122.8667 | 123.0637 | 38.8875 | -123.1557 | 122.8721 | 123.0682 | 122.8746 | 42.5854 | -123.3972
1247.7969 | 123.2254 | -64.9979 | 57.9941 | 0.0018314 | -0.010972 | 0.0010342 | 0.056438 | -0.0022669 | 0.062155 | 0.0058755 | 0.00089087 | 0.002175 | 0.058238 | 0.01913 | 0.060568 | -63.6248 | -26.3897 | -64.2051 | 57.923 | 57.8322 | 58.0338 | -65.1525 | -62.2877 | -22.2522 | -63.3433 | 57.8331 | 58.0292 | 57.808 | -65.4031 | -0.15461 | -0.07113 | 1.3731 | 0.79281 | 0.94741 | -0.1619 | 0.039736 | -0.40527 | -0.16101 | 2.7101 | 1.6546 | 2.0599 | 0.035099 | -0.18605 | 122.9208 | 122.83 | 123.0317 | 38.6082 | -123.1465 | 122.8309 | 123.027 | 122.8059 | 42.7457 | -123.3972
1248.7969 | 123.1613 | -65.0024 | 58.0078 | 0.0094624 | -0.010545 | 0.0012478 | 0.056224 | -0.0022669 | 0.062582 | -0.0093855 | 0.00089087 | 0.0019614 | 0.058452 | 0.01913 | 0.060568 | -63.5973 | -26.5957 | -64.1959 | 57.9321 | 57.8368 | 58.0338 | -65.1479 | -62.2419 | -22.0553 | -63.3066 | 57.8376 | 58.0246 | 57.8355 | -65.394 | -0.14545 | -0.075705 | 1.4051 | 0.80654 | 0.95199 | -0.17106 | 0.026004 | -0.39154 | -0.17017 | 2.7605 | 1.6958 | 2.0873 | 0.016788 | -0.17231 | 122.9345 | 122.8392 | 123.0363 | 38.4067 | -123.1557 | 122.8401 | 123.027 | 122.8379 | 42.9472 | -123.4018
1249.7969 | 123.1613 | -64.9979 | 57.9895 | 0.0094624 | -0.010758 | 0.0012478 | 0.056224 | -0.0022669 | 0.062368 | 0.013506 | 0.0015319 | 0.0017478 | 0.058452 | 0.01913 | 0.060355 | -63.5516 | -26.8796 | -64.1684 | 57.9367 | 57.8368 | 58.043 | -65.1479 | -62.1916 | -21.7989 | -63.27 | 57.8468 | 58.0246 | 57.7668 | -65.3986 | -0.15003 | -0.052817 | 1.4463 | 0.82943 | 0.97946 | -0.15275 | 0.053471 | -0.40069 | -0.1427 | 2.8063 | 1.7278 | 2.1285 | 0.035098 | -0.22268 | 122.9345 | 122.8346 | 123.0408 | 38.1183 | -123.1374 | 122.8447 | 123.0225 | 122.7647 | 43.199 | -123.3881
1250.7969 | 123.1384 | -64.9841 | 57.9895 | -0.0057996 | -0.010758 | 0.0010342 | 0.056438 | -0.0024807 | 0.062368 | 0.013506 | 0.0013183 | 0.0017478 | 0.058666 | 0.019344 | 0.060568 | -63.5424 | -27.0673 | -64.1455 | 57.9367 | 57.8459 | 58.0338 | -65.1433 | -62.1504 | -21.5516 | -63.2425 | 57.8422 | 58.0246 | 57.8447 | -65.3848 | -0.15918 | -0.052817 | 1.4417 | 0.83859 | 0.99777 | -0.14359 | 0.044314 | -0.40069 | -0.14728 | 2.8338 | 1.7416 | 2.1423 | 0.035098 | -0.14484 | 122.9208 | 122.83 | 123.0179 | 37.9168 | -123.1328 | 122.8264 | 123.0087 | 122.8288 | 43.4325 | -123.3743
1251.7969 | 123.2025 | -65.0024 | 58.0032 | -0.0057996 | -0.010758 | 0.0010342 | 0.056224 | -0.0022669 | 0.062582 | -0.001755 | 0.0013183 | 0.0019614 | 0.059093 | 0.01913 | 0.060782 | -63.5195 | -27.3237 | -64.1364 | 57.9367 | 57.8505 | 58.0384 | -65.1296 | -62.0954 | -21.3456 | -63.2059 | 57.8468 | 58.0383 | 57.7439 | -65.3894 | -0.12713 | -0.06655 | 1.4829 | 0.86606 | 0.99319 | -0.15274 | 0.03516 | -0.38696 | -0.15643 | 2.907 | 1.7965 | 2.1835 | 0.035101 | -0.25931 | 122.9391 | 122.8529 | 123.0408 | 37.6787 | -123.1328 | 122.8492 | 123.0408 | 122.7464 | 43.6569 | -123.3926
1252.7969 | 123.1567 | -64.9933 | 58.0124 | 0.0018314 | -0.010758 | 0.00082041 | 0.056011 | -0.0022669 | 0.062582 | 0.0058755 | 0.0013183 | 0.002175 | 0.058666 | 0.01913 | 0.060782 | -63.5012 | -27.5847 | -64.1181 | 57.9458 | 57.8505 | 58.0476 | -65.1433 | -62.0588 | -21.0388 | -63.1693 | 57.8468 | 58.0338 | 57.8034 | -65.3848 | -0.15003 | -0.066548 | 1.4921 | 0.87521 | 1.0252 | -0.1619 | 0.035162 | -0.39154 | -0.16559 | 2.9345 | 1.824 | 2.2155 | 0.021368 | -0.20894 | 122.9391 | 122.8438 | 123.0408 | 37.4086 | -123.1557 | 122.8401 | 123.027 | 122.7967 | 43.9545 | -123.3972
1253.7969 | 123.2529 | -64.9521 | 57.9895 | 0.0018314 | -0.010758 | 0.0010342 | 0.056438 | -0.0020533 | 0.061941 | 0.0058755 | 0.0013183 | 0.0023888 | 0.058238 | 0.018916 | 0.060782 | -63.4691 | -27.8182 | -64.0952 | 57.9504 | 57.8551 | 58.0521 | -65.125 | -62.013 | -20.8053 | -63.1281 | 57.8605 | 58.0521 | 57.863 | -65.3802 | -0.17291 | -0.039081 | 1.4829 | 0.85691 | 1.0298 | -0.13443 | 0.062629 | -0.42815 | -0.12896 | 2.9391 | 1.824 | 2.2522 | 0.06257 | -0.12653 | 122.9025 | 122.8072 | 123.0042 | 37.1339 | -123.1145 | 122.8126 | 123.0042 | 122.8151 | 44.1468 | -123.3697
1254.7969 | 123.1201 | -65.0024 | 58.0261 | -0.0057996 | -0.010758 | 0.0010342 | 0.056438 | -0.0018397 | 0.062155 | 0.0058755 | 0.0017455 | 0.002175 | 0.058238 | 0.019344 | 0.061209 | -63.4417 | -28.0746 | -64.0631 | 57.955 | 57.8688 | 58.0567 | -65.1204 | -61.9672 | -20.5352 | -63.1006 | 57.8605 | 58.0475 | 57.8447 | -65.3711 | -0.11798 | -0.071124 | 1.5608 | 0.93931 | 1.0573 | -0.15732 | 0.030586 | -0.36864 | -0.16558 | 3.0352 | 1.9018 | 2.2705 | 0.02137 | -0.18146 | 122.9574 | 122.8712 | 123.0592 | 36.9279 | -123.1465 | 122.863 | 123.0499 | 122.8471 | 44.4673 | -123.3972
1255.7969 | 123.2025 | -64.9521 | 58.0215 | 0.0018314 | -0.010758 | 0.0010342 | 0.056011 | -0.0022669 | 0.062155 | 0.0058755 | 0.0017455 | 0.002175 | 0.058452 | 0.019771 | 0.060782 | -63.405 | -28.3264 | -64.0402 | 57.9596 | 57.8825 | 58.0704 | -65.1158 | -61.9031 | -20.3474 | -63.0502 | 57.8697 | 58.0704 | 57.8218 | -65.3619 | -0.16375 | -0.061968 | 1.547 | 0.91185 | 1.0756 | -0.139 | 0.0489 | -0.40984 | -0.15185 | 3.049 | 1.9018 | 2.3117 | 0.048841 | -0.19978 | 122.9117 | 122.8346 | 123.0225 | 36.6257 | -123.1374 | 122.8218 | 123.0225 | 122.7739 | 44.6047 | -123.3835
1256.7969 | 123.1613 | -64.9933 | 58.0444 | 0.0018314 | -0.010972 | 0.0012478 | 0.056224 | -0.0022669 | 0.062155 | 0.0058755 | 0.0015319 | 0.0023888 | 0.058666 | 0.019344 | 0.060996 | -63.3959 | -28.592 | -64.0311 | 57.9642 | 57.8551 | 58.0613 | -65.1204 | -61.8756 | -19.9766 | -63.0228 | 57.8651 | 58.0521 | 57.8859 | -65.3802 | -0.12713 | -0.080278 | 1.5974 | 0.9622 | 1.0893 | -0.18936 | 0.016854 | -0.38696 | -0.17932 | 3.1176 | 1.9705 | 2.3575 | 0.007638 | -0.15857 | 122.9574 | 122.8484 | 123.0546 | 36.4013 | -123.1649 | 122.8584 | 123.0454 | 122.8792 | 45.0167 | -123.4247
1257.7969 | 123.1659 | -64.9887 | 58.0444 | -0.0057996 | -0.010972 | 0.0012478 | 0.056011 | -0.0020533 | 0.062582 | -0.0093855 | 0.0015319 | 0.002175 | 0.058666 | 0.019344 | 0.060355 | -63.3684 | -28.8575 | -64.0128 | 57.955 | 57.8688 | 58.0659 | -65.125 | -61.839 | -19.7476 | -62.9953 | 57.8651 | 58.0612 | 57.9133 | -65.3757 | -0.13629 | -0.089435 | 1.6203 | 0.97594 | 1.1122 | -0.17563 | 0.021432 | -0.38696 | -0.17932 | 3.1497 | 1.9934 | 2.3804 | 0.016795 | -0.1311 | 122.9437 | 122.8575 | 123.0546 | 36.1312 | -123.1694 | 122.8538 | 123.0499 | 122.902 | 45.2411 | -123.4201
1258.7969 | 123.1201 | -64.975 | 58.0307 | -0.021062 | -0.010758 | 0.0010342 | 0.056438 | -0.0022669 | 0.062368 | -0.0093855 | 0.0015319 | 0.002175 | 0.058666 | 0.019771 | 0.060782 | -63.3501 | -29.0956 | -63.999 | 57.955 | 57.878 | 58.0613 | -65.1296 | -61.7932 | -19.537 | -62.9541 | 57.8651 | 58.0475 | 57.895 | -65.3757 | -0.1546 | -0.075702 | 1.6249 | 0.97594 | 1.1305 | -0.15274 | 0.030587 | -0.40069 | -0.16558 | 3.1818 | 2.0209 | 2.4216 | 0.016792 | -0.13568 | 122.93 | 122.8529 | 123.0363 | 35.8794 | -123.1603 | 122.8401 | 123.0225 | 122.87 | 45.438 | -123.4064
1259.7969 | 123.2254 | -64.9612 | 58.0032 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0022669 | 0.062796 | 0.0058755 | 0.0017455 | 0.002175 | 0.058666 | 0.019557 | 0.060996 | -63.3318 | -29.3154 | -63.9807 | 57.9504 | 57.8825 | 58.0613 | -65.125 | -61.7612 | -19.2989 | -62.9312 | 57.8651 | 58.0567 | 57.895 | -65.3802 | -0.16375 | -0.052814 | 1.6295 | 0.98052 | 1.1443 | -0.12069 | 0.058053 | -0.419 | -0.13812 | 3.2001 | 2.03 | 2.449 | 0.053416 | -0.10821 | 122.9117 | 122.8438 | 123.0225 | 35.6459 | -123.1282 | 122.8264 | 123.0179 | 122.8563 | 45.6623 | -123.3835
1260.7969 | 123.1567 | -64.9887 | 58.0215 | 0.0094624 | -0.010972 | 0.0010342 | 0.056011 | -0.0018397 | 0.062368 | 0.0058755 | 0.0017455 | 0.002175 | 0.058666 | 0.019557 | 0.060782 | -63.2997 | -29.5352 | -63.9624 | 57.9504 | 57.8871 | 58.0659 | -65.1204 | -61.72 | -19.1478 | -62.8854 | 57.8605 | 58.0612 | 57.8721 | -65.3711 | -0.13171 | -0.071124 | 1.689 | 1.0263 | 1.158 | -0.13442 | 0.044321 | -0.38238 | -0.16101 | 3.2687 | 2.1033 | 2.4857 | 0.039684 | -0.14942 | 122.9391 | 122.8758 | 123.0546 | 35.4536 | -123.142 | 122.8492 | 123.0499 | 122.8608 | 45.8409 | -123.3926
1261.7969 | 123.1476 | -64.9704 | 58.0444 | 0.0018314 | -0.010545 | 0.00082041 | 0.056438 | -0.0020533 | 0.062368 | -0.001755 | 0.0017455 | 0.002175 | 0.058666 | 0.019557 | 0.060996 | -63.2769 | -29.732 | -63.9349 | 57.9642 | 57.8963 | 58.0613 | -65.1158 | -61.6696 | -18.9555 | -62.8488 | 57.8743 | 58.0704 | 57.9133 | -65.3619 | -0.14544 | -0.080278 | 1.6935 | 1.0355 | 1.1809 | -0.14815 | 0.016854 | -0.39153 | -0.17016 | 3.3008 | 2.1216 | 2.5131 | 0.025952 | -0.1311 | 122.9346 | 122.8667 | 123.0317 | 35.2384 | -123.1603 | 122.8447 | 123.0408 | 122.8837 | 46.0149 | -123.4064
1262.7969 | 123.1155 | -64.9933 | 58.017 | 0.0018314 | -0.010758 | 0.0010342 | 0.056224 | -0.0020533 | 0.062582 | -0.0093855 | 0.0019591 | 0.0019614 | 0.058452 | 0.019557 | 0.060782 | -63.254 | -29.9243 | -63.9258 | 57.9596 | 57.8596 | 58.0659 | -65.1296 | -61.6467 | -18.8593 | -62.8259 | 57.8651 | 58.0567 | 57.9179 | -65.3802 | -0.13629 | -0.057391 | 1.7393 | 1.0675 | 1.2038 | -0.15732 | 0.048898 | -0.38696 | -0.15185 | 3.3466 | 2.1674 | 2.5544 | 0.039683 | -0.099053 | 122.9529 | 122.8529 | 123.0592 | 35.0689 | -123.1465 | 122.8584 | 123.0499 | 122.9112 | 46.1339 | -123.3972
1263.7969 | 123.0881 | -64.9796 | 58.017 | 0.0018314 | -0.010758 | 0.0010342 | 0.056224 | -0.0022669 | 0.062368 | 0.0058755 | 0.0017455 | 0.0023888 | 0.058879 | 0.019557 | 0.060782 | -63.2402 | -30.1533 | -63.8983 | 57.955 | 57.8825 | 58.0613 | -65.1204 | -61.6055 | -18.6716 | -62.7938 | 57.8651 | 58.0612 | 57.9271 | -65.3711 | -0.14086 | -0.061969 | 1.7393 | 1.0812 | 1.2221 | -0.13442 | 0.04432 | -0.39153 | -0.15185 | 3.3741 | 2.1857 | 2.5772 | 0.044261 | -0.089895 | 122.9346 | 122.8621 | 123.0408 | 34.8263 | -123.1374 | 122.8447 | 123.0408 | 122.9066 | 46.3079 | -123.3881
1264.7969 | 123.1476 | -65.0803 | 57.9391 | 0.0018314 | -0.010972 | 0.0010342 | 0.056224 | -0.0022669 | 0.062368 | -0.001755 | 0.0019591 | 0.0023888 | 0.058452 | 0.019771 | 0.060782 | -63.3822 | -30.2494 | -63.999 | 57.8772 | 57.7864 | 57.9789 | -65.2074 | -61.6559 | -18.5755 | -62.8488 | 57.7827 | 57.9834 | 57.8309 | -65.4489 | -0.12716 | -0.061982 | 1.6981 | 1.0812 | 1.2084 | -0.15276 | 0.039725 | -0.36866 | -0.15644 | 3.4244 | 2.2315 | 2.6001 | 0.044245 | -0.10823 | 122.9574 | 122.8666 | 123.0591 | 34.8308 | -123.1466 | 122.863 | 123.0637 | 122.9112 | 46.5048 | -123.3881
1265.7969 | 123.1247 | -65.1077 | 57.9025 | 0.0094624 | -0.010758 | 0.00082041 | 0.056438 | -0.0020533 | 0.062582 | -0.001755 | 0.0019591 | 0.002175 | 0.058666 | 0.019771 | 0.061209 | -63.3913 | -30.4051 | -64.0082 | 57.868 | 57.7681 | 57.9697 | -65.212 | -61.633 | -18.3832 | -62.8259 | 57.7781 | 57.9651 | 57.7806 | -65.4672 | -0.10427 | -0.034517 | 1.7164 | 1.0995 | 1.2038 | -0.13446 | 0.067189 | -0.35951 | -0.1244 | 3.4748 | 2.2818 | 2.6414 | 0.062552 | -0.12197 | 122.9757 | 122.8758 | 123.0774 | 34.7026 | -123.1145 | 122.8859 | 123.0728 | 122.8883 | 46.7246 | -123.3698
1266.7969 | 123.1476 | -65.0894 | 57.93 | 0.0018314 | -0.010758 | 0.0010342 | 0.056224 | -0.0020533 | 0.062796 | 0.013506 | 0.0019591 | 0.002175 | 0.058879 | 0.019557 | 0.060996 | -63.3822 | -30.4692 | -64.0173 | 57.8543 | 57.7543 | 57.9514 | -65.2303 | -61.6101 | -18.2137 | -62.8076 | 57.769 | 57.9513 | 57.7439 | -65.481 | -0.14089 | -0.075719 | 1.7073 | 1.0721 | 1.213 | -0.17566 | 0.021408 | -0.39156 | -0.16102 | 3.4793 | 2.2818 | 2.6734 | 0.02135 | -0.18607 | 122.9437 | 122.8438 | 123.0408 | 34.6202 | -123.1603 | 122.8584 | 123.0408 | 122.8333 | 46.8757 | -123.411
1267.7969 | 123.1247 | -65.094 | 57.9208 | 0.0018314 | -0.010972 | 0.0010342 | 0.056224 | -0.0020533 | 0.062155 | 0.0058755 | 0.0019591 | 0.0023888 | 0.058452 | 0.019557 | 0.061209 | -63.3776 | -30.4921 | -64.0173 | 57.8405 | 57.7543 | 57.9468 | -65.2395 | -61.5872 | -18.0581 | -62.7801 | 57.7461 | 57.9468 | 57.7622 | -65.4856 | -0.14548 | -0.080298 | 1.7164 | 1.0766 | 1.2221 | -0.1665 | 0.025986 | -0.39156 | -0.17476 | 3.5068 | 2.3139 | 2.7055 | 0.025927 | -0.15859 | 122.9345 | 122.8483 | 123.0408 | 34.6019 | -123.1603 | 122.8401 | 123.0408 | 122.8562 | 47.0359 | -123.4064
1268.7969 | 123.175 | -65.1077 | 57.8934 | 0.0018314 | -0.010758 | 0.0010342 | 0.056438 | -0.0018397 | 0.062582 | 0.0058755 | 0.0019591 | 0.0019614 | 0.058452 | 0.020198 | 0.061209 | -63.3638 | -30.4371 | -64.0219 | 57.836 | 57.7452 | 57.9468 | -65.2486 | -61.546 | -17.9711 | -62.7572 | 57.7552 | 57.9376 | 57.7806 | -65.4947 | -0.1409 | -0.057411 | 1.7439 | 1.0858 | 1.2267 | -0.1482 | 0.053451 | -0.38699 | -0.13814 | 3.5618 | 2.3505 | 2.7375 | 0.044235 | -0.11281 | 122.9437 | 122.8529 | 123.0546 | 34.6706 | -123.142 | 122.863 | 123.0453 | 122.8883 | 47.1366 | -123.3881
1269.7969 | 123.1384 | -65.0848 | 57.9437 | 0.0094624 | -0.011186 | 0.0010342 | 0.056652 | -0.0020533 | 0.063009 | -0.001755 | 0.0023863 | 0.0023888 | 0.058452 | 0.019771 | 0.061423 | -63.3455 | -30.5104 | -64.0219 | 57.8451 | 57.7452 | 57.9422 | -65.2349 | -61.5093 | -17.8108 | -62.7297 | 57.7415 | 57.9468 | 57.7577 | -65.4856 | -0.15005 | -0.098608 | 1.7393 | 1.0629 | 1.213 | -0.19855 | -0.001482 | -0.40072 | -0.20223 | 3.5755 | 2.3551 | 2.7558 | 0.003038 | -0.18606 | 122.93 | 122.83 | 123.0271 | 34.5744 | -123.1786 | 122.8263 | 123.0316 | 122.8425 | 47.274 | -123.4293
1270.7969 | 123.1567 | -65.1215 | 57.9025 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0020533 | 0.062796 | 0.0058755 | 0.0023863 | 0.0023888 | 0.058666 | 0.019985 | 0.060782 | -63.3318 | -30.5196 | -64.0036 | 57.836 | 57.7498 | 57.9468 | -65.2395 | -61.4727 | -17.6826 | -62.7023 | 57.7507 | 57.9376 | 57.7439 | -65.4947 | -0.11801 | -0.066566 | 1.7897 | 1.1178 | 1.2359 | -0.15277 | 0.044296 | -0.37325 | -0.15187 | 3.6487 | 2.4192 | 2.7925 | 0.03508 | -0.1586 | 122.9574 | 122.8712 | 123.0683 | 34.6019 | -123.142 | 122.8721 | 123.0591 | 122.8654 | 47.4388 | -123.3972
1271.7969 | 123.0881 | -65.1169 | 57.9025 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0018397 | 0.062582 | 0.013506 | 0.0019591 | 0.0023888 | 0.058452 | 0.020198 | 0.061423 | -63.2906 | -30.5699 | -63.9853 | 57.8405 | 57.7589 | 57.956 | -65.2349 | -61.4315 | -17.5132 | -62.6611 | 57.7598 | 57.9468 | 57.6752 | -65.481 | -0.11801 | -0.061988 | 1.8263 | 1.1316 | 1.2496 | -0.14361 | 0.053453 | -0.36409 | -0.14272 | 3.6854 | 2.4558 | 2.8199 | 0.044237 | -0.22728 | 122.9574 | 122.8758 | 123.0729 | 34.547 | -123.1374 | 122.8767 | 123.0636 | 122.7921 | 47.6037 | -123.3835
1272.7969 | 123.1567 | -65.1489 | 57.8567 | -0.0057996 | -0.010972 | 0.0014616 | 0.056011 | -0.0022669 | 0.062368 | -0.001755 | 0.0021727 | 0.0023888 | 0.059093 | 0.019985 | 0.061423 | -63.3043 | -30.7073 | -64.0128 | 57.8085 | 57.7223 | 57.9194 | -65.2715 | -61.4452 | -17.4537 | -62.6702 | 57.7232 | 57.9101 | 57.689 | -65.5176 | -0.1226 | -0.048259 | 1.8446 | 1.1362 | 1.2588 | -0.13447 | 0.062601 | -0.36868 | -0.13357 | 3.7037 | 2.4787 | 2.8474 | 0.053385 | -0.16776 | 122.9574 | 122.8712 | 123.0683 | 34.4416 | -123.1283 | 122.8721 | 123.0591 | 122.8379 | 47.6952 | -123.3744
1273.7969 | 123.1293 | -65.1489 | 57.8888 | 0.0094624 | -0.010545 | 0.00082041 | 0.056438 | -0.0020533 | 0.062796 | -0.0093855 | 0.0023863 | 0.0023888 | 0.058879 | 0.020198 | 0.061209 | -63.286 | -30.6935 | -63.999 | 57.8085 | 57.7177 | 57.9194 | -65.2669 | -61.4178 | -17.3255 | -62.6427 | 57.7232 | 57.9193 | 57.6936 | -65.5222 | -0.11802 | -0.080303 | 1.8629 | 1.1499 | 1.2679 | -0.17109 | 0.030557 | -0.37326 | -0.16561 | 3.7312 | 2.5062 | 2.8794 | 0.030499 | -0.19523 | 122.9574 | 122.8666 | 123.0683 | 34.4554 | -123.1557 | 122.8721 | 123.0682 | 122.8425 | 47.8234 | -123.411
1274.7969 | 123.1659 | -65.1764 | 57.8659 | 0.0018314 | -0.010758 | 0.0012478 | 0.056224 | -0.0018397 | 0.062796 | -0.001755 | 0.0021727 | 0.0019614 | 0.058879 | 0.019557 | 0.061209 | -63.2769 | -30.7805 | -64.0036 | 57.7948 | 57.6994 | 57.8965 | -65.2853 | -61.3903 | -17.179 | -62.6473 | 57.7049 | 57.9056 | 57.7165 | -65.5359 | -0.10887 | -0.071151 | 1.8995 | 1.1728 | 1.2816 | -0.16652 | 0.030552 | -0.35953 | -0.16104 | 3.7861 | 2.5291 | 2.8886 | 0.039651 | -0.14945 | 122.9711 | 122.8758 | 123.0729 | 34.3959 | -123.1512 | 122.8813 | 123.0819 | 122.8928 | 47.9974 | -123.4018
1275.7969 | 123.1064 | -65.1031 | 57.9071 | 0.0018314 | -0.010758 | 0.00082041 | 0.056224 | -0.0022669 | 0.062368 | -0.0093855 | 0.0026001 | 0.0019614 | 0.058452 | 0.019985 | 0.061209 | -63.2082 | -30.8309 | -63.9441 | 57.8314 | 57.7452 | 57.9422 | -65.2395 | -61.3308 | -17.005 | -62.5786 | 57.7461 | 57.9422 | 57.6295 | -65.4856 | -0.13632 | -0.075722 | 1.895 | 1.1591 | 1.2954 | -0.16193 | 0.03514 | -0.38241 | -0.16103 | 3.7724 | 2.5245 | 2.9069 | 0.035082 | -0.27764 | 122.9345 | 122.8483 | 123.0454 | 34.2722 | -123.1466 | 122.8492 | 123.0453 | 122.7326 | 48.0982 | -123.3927
1276.7969 | 123.1247 | -65.0848 | 57.9117 | -0.0057996 | -0.010758 | 0.0012478 | 0.056224 | -0.0022669 | 0.062582 | -0.001755 | 0.0026001 | 0.0019614 | 0.058666 | 0.020198 | 0.061423 | -63.1578 | -30.8858 | -63.912 | 57.8634 | 57.7635 | 57.9651 | -65.2257 | -61.2758 | -16.9821 | -62.5237 | 57.7644 | 57.9559 | 57.7577 | -65.4718 | -0.14089 | -0.048251 | 1.927 | 1.1728 | 1.3137 | -0.14819 | 0.053455 | -0.38698 | -0.14729 | 3.809 | 2.5611 | 2.9481 | 0.044239 | -0.15402 | 122.9483 | 122.8483 | 123.05 | 34.199 | -123.1374 | 122.8492 | 123.0408 | 122.8425 | 48.1028 | -123.3835
1277.7969 | 123.1705 | -65.0803 | 57.9391 | 0.0094624 | -0.010758 | 0.0012478 | 0.056438 | -0.0018397 | 0.062582 | -0.001755 | 0.0021727 | 0.0026024 | 0.058879 | 0.020198 | 0.060996 | -63.112 | -30.9179 | -63.8754 | 57.8726 | 57.7772 | 57.9743 | -65.2074 | -61.2163 | -16.8997 | -62.4687 | 57.7735 | 57.9697 | 57.776 | -65.4581 | -0.12716 | -0.06656 | 1.9682 | 1.2048 | 1.332 | -0.16192 | 0.035146 | -0.37782 | -0.1656 | 3.864 | 2.6115 | 2.9893 | 0.030509 | -0.16317 | 122.9528 | 122.8575 | 123.0546 | 34.1624 | -123.1466 | 122.8538 | 123.0499 | 122.8562 | 48.1806 | -123.3972
1278.7969 | 123.1522 | -65.0711 | 57.9117 | 0.0018314 | -0.010758 | 0.0010342 | 0.056438 | -0.0018397 | 0.062796 | -0.001755 | 0.0026001 | 0.0026024 | 0.058879 | 0.020198 | 0.061423 | -63.0846 | -30.9042 | -63.848 | 57.8817 | 57.791 | 57.9835 | -65.1983 | -61.1705 | -16.8218 | -62.4321 | 57.7919 | 57.9834 | 57.7851 | -65.4443 | -0.12715 | -0.029937 | 1.9865 | 1.2232 | 1.3503 | -0.12072 | 0.07177 | -0.37324 | -0.11982 | 3.9006 | 2.639 | 3.0122 | 0.071711 | -0.12655 | 122.9529 | 122.8621 | 123.0546 | 34.1669 | -123.1099 | 122.863 | 123.0545 | 122.8562 | 48.2493 | -123.356
1279.7969 | 123.143 | -65.0757 | 57.9437 | 0.0018314 | -0.010758 | 0.0014616 | 0.056438 | -0.0020533 | 0.063009 | 0.0058755 | 0.0026001 | 0.0023888 | 0.058666 | 0.020412 | 0.061423 | -63.0617 | -30.9408 | -63.8342 | 57.8772 | 57.7864 | 57.9926 | -65.1983 | -61.143 | -16.8218 | -62.4092 | 57.7873 | 57.9742 | 57.7806 | -65.4581 | -0.12257 | -0.06656 | 2.014 | 1.2415 | 1.364 | -0.15734 | 0.048883 | -0.3824 | -0.15644 | 3.9326 | 2.6665 | 3.0489 | 0.03051 | -0.16317 | 122.9528 | 122.8621 | 123.0683 | 34.1349 | -123.142 | 122.863 | 123.0499 | 122.8562 | 48.2539 | -123.4018
1280.7969 | 123.1842 | -65.0528 | 57.9346 | 0.0094624 | -0.010758 | 0.0010342 | 0.056224 | -0.0022669 | 0.063009 | -0.001755 | 0.0028137 | 0.002175 | 0.058666 | 0.019985 | 0.061423 | -63.0342 | -30.982 | -63.8296 | 57.8817 | 57.791 | 57.988 | -65.2074 | -61.111 | -16.7943 | -62.4001 | 57.7827 | 57.9788 | 57.7851 | -65.4535 | -0.15462 | -0.052825 | 2.0186 | 1.2232 | 1.3778 | -0.1436 | 0.05346 | -0.40071 | -0.15187 | 3.9418 | 2.6527 | 3.0534 | 0.044244 | -0.14943 | 122.9345 | 122.8438 | 123.0408 | 34.0708 | -123.142 | 122.8355 | 123.0316 | 122.8379 | 48.2584 | -123.3881
1281.7969 | 123.143 | -65.0803 | 57.9437 | 0.017093 | -0.010758 | 0.0010342 | 0.056224 | -0.0020533 | 0.062368 | 0.0058755 | 0.0028137 | 0.002175 | 0.058666 | 0.020198 | 0.061423 | -63.0205 | -30.9545 | -63.8159 | 57.868 | 57.7864 | 57.9835 | -65.2028 | -61.0789 | -16.7806 | -62.3726 | 57.7827 | 57.9651 | 57.7622 | -65.4581 | -0.12258 | -0.075716 | 2.0598 | 1.2644 | 1.3869 | -0.15734 | 0.039726 | -0.37782 | -0.16102 | 4.0013 | 2.7077 | 3.0855 | 0.021353 | -0.18148 | 122.9483 | 122.8666 | 123.0637 | 34.1257 | -123.1466 | 122.863 | 123.0453 | 122.8425 | 48.2996 | -123.4018
1282.7969 | 123.1338 | -65.0894 | 57.9071 | -0.0057996 | -0.010972 | 0.0012478 | 0.056224 | -0.0022669 | 0.062582 | -0.001755 | 0.0028137 | 0.0026024 | 0.058666 | 0.020198 | 0.061637 | -62.9793 | -30.863 | -63.8067 | 57.8772 | 57.7955 | 57.9743 | -65.2074 | -61.0469 | -16.7577 | -62.3497 | 57.7735 | 57.9697 | 57.8401 | -65.4535 | -0.118 | -0.029938 | 2.1102 | 1.2827 | 1.4007 | -0.11156 | 0.06719 | -0.36409 | -0.13356 | 4.0425 | 2.7397 | 3.1038 | 0.062553 | -0.067025 | 122.9666 | 122.885 | 123.0637 | 34.2265 | -123.1145 | 122.863 | 123.0591 | 122.9295 | 48.3317 | -123.3606
1283.7969 | 123.1522 | -65.1169 | 57.9071 | 0.0018314 | -0.010758 | 0.0012478 | 0.056011 | -0.0018397 | 0.063009 | 0.013506 | 0.0028137 | 0.002816 | 0.058666 | 0.019985 | 0.061637 | -62.9747 | -30.8446 | -63.8067 | 57.8497 | 57.7681 | 57.9606 | -65.2257 | -61.0286 | -16.6936 | -62.3589 | 57.7598 | 57.9513 | 57.7851 | -65.4764 | -0.10885 | -0.057408 | 2.1422 | 1.3101 | 1.419 | -0.13903 | 0.053455 | -0.35952 | -0.14729 | 4.0883 | 2.758 | 3.1175 | 0.044239 | -0.12197 | 122.9666 | 122.885 | 123.0774 | 34.2722 | -123.1328 | 122.8767 | 123.0682 | 122.902 | 48.4233 | -123.3835
1284.7969 | 123.1064 | -65.1306 | 57.8842 | -0.0057996 | -0.010758 | 0.0012478 | 0.056438 | -0.0018397 | 0.062368 | -0.001755 | 0.0030273 | 0.0023888 | 0.058666 | 0.020412 | 0.061637 | -62.9472 | -30.8034 | -63.7884 | 57.8543 | 57.7543 | 57.9514 | -65.2349 | -61.0057 | -16.6524 | -62.336 | 57.7552 | 57.9422 | 57.7714 | -65.4856 | -0.10427 | -0.029942 | 2.1834 | 1.3422 | 1.4465 | -0.12988 | 0.067185 | -0.35494 | -0.12898 | 4.1249 | 2.7947 | 3.1496 | 0.05797 | -0.11282 | 122.9849 | 122.8849 | 123.082 | 34.3272 | -123.1191 | 122.8858 | 123.0728 | 122.902 | 48.4782 | -123.3698
1285.7969 | 123.1979 | -65.1031 | 57.8796 | 0.0018314 | -0.010758 | 0.0010342 | 0.056011 | -0.0020533 | 0.062796 | 0.0058755 | 0.0028137 | 0.0023888 | 0.058452 | 0.020412 | 0.061637 | -62.9152 | -30.7485 | -63.7655 | 57.8405 | 57.7635 | 57.956 | -65.2303 | -60.9691 | -16.6066 | -62.3176 | 57.7507 | 57.9422 | 57.7622 | -65.4764 | -0.12716 | -0.0391 | 2.188 | 1.3376 | 1.4648 | -0.11615 | 0.076341 | -0.37325 | -0.12898 | 4.1341 | 2.7855 | 3.1587 | 0.062547 | -0.1174 | 122.9437 | 122.8666 | 123.0591 | 34.3547 | -123.1099 | 122.8538 | 123.0453 | 122.8654 | 48.4965 | -123.356
1286.7969 | 123.1384 | -65.1215 | 57.8659 | -0.0057996 | -0.010545 | 0.0010342 | 0.056224 | -0.0020533 | 0.062796 | -0.0093855 | 0.0028137 | 0.002175 | 0.058879 | 0.020412 | 0.061423 | -62.8877 | -30.6432 | -63.7427 | 57.8497 | 57.7589 | 57.9514 | -65.2349 | -60.9416 | -16.5883 | -62.2948 | 57.7598 | 57.9468 | 57.776 | -65.4856 | -0.11343 | -0.01621 | 2.2338 | 1.3788 | 1.4922 | -0.10699 | 0.085495 | -0.3641 | -0.10609 | 4.1799 | 2.8267 | 3.1908 | 0.080858 | -0.089927 | 122.9712 | 122.8804 | 123.0729 | 34.4783 | -123.1008 | 122.8813 | 123.0682 | 122.8974 | 48.5332 | -123.3515
1287.7969 | 123.1247 | -65.1398 | 57.8888 | 0.0018314 | -0.010758 | 0.0012478 | 0.056224 | -0.0018397 | 0.063009 | 0.0058755 | 0.0030273 | 0.002175 | 0.058238 | 0.020198 | 0.06185 | -62.8602 | -30.5196 | -63.7518 | 57.836 | 57.7543 | 57.9422 | -65.244 | -60.9187 | -16.5975 | -62.2856 | 57.7461 | 57.9376 | 57.7668 | -65.4901 | -0.10428 | -0.052833 | 2.2796 | 1.388 | 1.4922 | -0.13446 | 0.05345 | -0.35036 | -0.14272 | 4.2211 | 2.8542 | 3.2045 | 0.048813 | -0.12197 | 122.9757 | 122.8941 | 123.082 | 34.6202 | -123.1328 | 122.8858 | 123.0774 | 122.9066 | 48.5423 | -123.3789
1288.7969 | 123.1705 | -65.1306 | 57.8613 | -0.013431 | -0.010331 | 0.0014616 | 0.056438 | -0.0018397 | 0.062796 | 0.0058755 | 0.0026001 | 0.002175 | 0.058666 | 0.020198 | 0.061423 | -62.8236 | -30.4188 | -63.7198 | 57.836 | 57.7406 | 57.9331 | -65.2486 | -60.8958 | -16.5517 | -62.2581 | 57.7461 | 57.933 | 57.6936 | -65.4947 | -0.11801 | -0.025367 | 2.307 | 1.4109 | 1.5289 | -0.12073 | 0.071759 | -0.3641 | -0.11525 | 4.2348 | 2.8725 | 3.2366 | 0.0717 | -0.16776 | 122.9666 | 122.8712 | 123.0637 | 34.7118 | -123.11 | 122.8767 | 123.0636 | 122.8242 | 48.5789 | -123.356
1289.7969 | 123.1796 | -65.1215 | 57.8751 | -0.0057996 | -0.010331 | 0.0012478 | 0.056438 | -0.0018397 | 0.063009 | -0.001755 | 0.0032409 | 0.0026024 | 0.058666 | 0.020626 | 0.061637 | -62.8007 | -30.3044 | -63.706 | 57.836 | 57.7452 | 57.9468 | -65.244 | -60.8729 | -16.5379 | -62.2444 | 57.7461 | 57.9284 | 57.7577 | -65.4993 | -0.12259 | -0.0391 | 2.3208 | 1.4154 | 1.538 | -0.12989 | 0.071762 | -0.37783 | -0.12899 | 4.2486 | 2.8771 | 3.2549 | 0.053389 | -0.1174 | 122.9574 | 122.8666 | 123.0683 | 34.8171 | -123.1191 | 122.8675 | 123.0499 | 122.8791 | 48.5835 | -123.3744
1290.7969 | 123.1384 | -65.1169 | 57.8842 | 0.0018314 | -0.010545 | 0.0014616 | 0.056224 | -0.0016259 | 0.063223 | -0.001755 | 0.0030273 | 0.0026024 | 0.058452 | 0.020198 | 0.061637 | -62.7595 | -30.1304 | -63.6831 | 57.836 | 57.7406 | 57.9422 | -65.2486 | -60.8363 | -16.515 | -62.2169 | 57.7415 | 57.933 | 57.7348 | -65.4901 | -0.13174 | -0.048255 | 2.3574 | 1.4337 | 1.5655 | -0.14362 | 0.058028 | -0.37325 | -0.14272 | 4.2806 | 2.9 | 3.2732 | 0.048812 | -0.14945 | 122.9528 | 122.8575 | 123.0591 | 34.9865 | -123.1328 | 122.8584 | 123.0499 | 122.8517 | 48.6018 | -123.3743
1291.7969 | 123.1293 | -65.1077 | 57.8888 | 0.0018314 | -0.010758 | 0.0014616 | 0.056011 | -0.0016259 | 0.062796 | 0.0058755 | 0.0032409 | 0.0026024 | 0.058666 | 0.020412 | 0.06185 | -62.732 | -29.9747 | -63.6557 | 57.8314 | 57.7543 | 57.9377 | -65.244 | -60.7905 | -16.515 | -62.194 | 57.7461 | 57.9376 | 57.7302 | -65.4901 | -0.13632 | -0.057412 | 2.3757 | 1.4521 | 1.5884 | -0.13446 | 0.048872 | -0.38241 | -0.14272 | 4.3172 | 2.9137 | 3.2961 | 0.048813 | -0.1586 | 122.9391 | 122.8621 | 123.0454 | 35.133 | -123.1328 | 122.8538 | 123.0453 | 122.8379 | 48.5927 | -123.3789
1292.7969 | 123.143 | -65.1398 | 57.8567 | 0.0018314 | -0.010758 | 0.0014616 | 0.056224 | -0.0020533 | 0.063009 | -0.001755 | 0.0032409 | 0.0026024 | 0.058666 | 0.019985 | 0.06185 | -62.6954 | -29.7916 | -63.6328 | 57.8268 | 57.7452 | 57.9331 | -65.2486 | -60.7767 | -16.515 | -62.1803 | 57.7369 | 57.9193 | 57.7348 | -65.4993 | -0.10886 | -0.029946 | 2.4444 | 1.507 | 1.6159 | -0.11157 | 0.076337 | -0.35952 | -0.11983 | 4.363 | 2.9595 | 3.319 | 0.062543 | -0.12198 | 122.9666 | 122.8849 | 123.0729 | 35.3482 | -123.1054 | 122.8767 | 123.0591 | 122.8745 | 48.6247 | -123.356
1293.7969 | 123.143 | -65.1077 | 57.8796 | 0.0018314 | -0.010758 | 0.0012478 | 0.056224 | -0.0018397 | 0.063009 | -0.001755 | 0.0032409 | 0.0026024 | 0.058452 | 0.019985 | 0.06185 | -62.6542 | -29.613 | -63.6099 | 57.8405 | 57.7452 | 57.9468 | -65.2486 | -60.7447 | -16.5013 | -62.1482 | 57.7415 | 57.933 | 57.7668 | -65.4947 | -0.1409 | -0.0391 | 2.4535 | 1.4978 | 1.6387 | -0.13446 | 0.067184 | -0.38699 | -0.13814 | 4.363 | 2.9595 | 3.3465 | 0.053389 | -0.11282 | 122.9483 | 122.8529 | 123.0546 | 35.4947 | -123.1283 | 122.8492 | 123.0408 | 122.8745 | 48.6064 | -123.3744
1294.7969 | 123.1613 | -65.1443 | 57.8567 | -0.013431 | -0.010545 | 0.0016752 | 0.056224 | -0.0016259 | 0.063223 | -0.001755 | 0.0030273 | 0.0026024 | 0.058879 | 0.020626 | 0.06185 | -62.613 | -29.4024 | -63.587 | 57.8405 | 57.7406 | 57.9377 | -65.2532 | -60.7218 | -16.4922 | -62.1391 | 57.7415 | 57.933 | 57.7394 | -65.5084 | -0.10886 | -0.016211 | 2.5314 | 1.5574 | 1.6662 | -0.11615 | 0.080916 | -0.3641 | -0.11525 | 4.4225 | 3.0053 | 3.3694 | 0.076278 | -0.1174 | 122.9849 | 122.8849 | 123.082 | 35.742 | -123.11 | 122.8858 | 123.0774 | 122.8837 | 48.6522 | -123.3652
1295.7969 | 123.1476 | -65.1306 | 57.8476 | 0.0018314 | -0.010331 | 0.0014616 | 0.056224 | -0.0020533 | 0.063437 | 0.0058755 | 0.0028137 | 0.0023888 | 0.058879 | 0.020626 | 0.06185 | -62.5992 | -29.2559 | -63.5778 | 57.8085 | 57.736 | 57.9148 | -65.2761 | -60.7081 | -16.5196 | -62.1345 | 57.7232 | 57.901 | 57.7531 | -65.5268 | -0.14549 | -0.039104 | 2.5314 | 1.5528 | 1.6983 | -0.11158 | 0.067178 | -0.39615 | -0.12441 | 4.4225 | 2.9961 | 3.3923 | 0.053383 | -0.094509 | 122.9391 | 122.8666 | 123.0454 | 35.8748 | -123.1237 | 122.8538 | 123.0316 | 122.8837 | 48.611 | -123.3744
1296.7969 | 123.1155 | -65.1627 | 57.843 | -0.0057996 | -0.010331 | 0.0014616 | 0.056011 | -0.0016259 | 0.06365 | -0.001755 | 0.0032409 | 0.002816 | 0.058666 | 0.020412 | 0.062064 | -62.5626 | -28.9949 | -63.5687 | 57.8039 | 57.7314 | 57.9102 | -65.2807 | -60.6898 | -16.5242 | -62.1116 | 57.7094 | 57.8964 | 57.7302 | -65.5313 | -0.11802 | -0.039106 | 2.6 | 1.594 | 1.712 | -0.11158 | 0.067176 | -0.36868 | -0.13357 | 4.4729 | 3.0511 | 3.4197 | 0.053382 | -0.11283 | 122.9666 | 122.8941 | 123.0729 | 36.1678 | -123.1237 | 122.8721 | 123.0591 | 122.8929 | 48.6385 | -123.3744
1297.7969 | 123.1384 | -65.1352 | 57.8567 | -0.0057996 | -0.010331 | 0.0014616 | 0.056011 | -0.0018397 | 0.063437 | 0.0058755 | 0.0030273 | 0.0026024 | 0.058879 | 0.020839 | 0.06185 | -62.526 | -28.8301 | -63.5504 | 57.7948 | 57.7269 | 57.9148 | -65.2807 | -60.6531 | -16.5105 | -62.1116 | 57.7094 | 57.8964 | 57.7622 | -65.5359 | -0.14549 | -0.061995 | 2.6092 | 1.5848 | 1.7303 | -0.12989 | 0.058023 | -0.40073 | -0.1473 | 4.4821 | 3.0236 | 3.4243 | 0.03965 | -0.094507 | 122.9299 | 122.8621 | 123.05 | 36.3051 | -123.1374 | 122.8446 | 123.0316 | 122.8974 | 48.6247 | -123.3927
1298.7969 | 123.0927 | -65.1855 | 57.843 | -0.0057996 | -0.010331 | 0.0012478 | 0.056865 | -0.0018397 | 0.063437 | -0.0093855 | 0.0032409 | 0.0026024 | 0.058452 | 0.020626 | 0.062064 | -62.4985 | -28.5508 | -63.5321 | 57.7993 | 57.7177 | 57.901 | -65.2944 | -60.6348 | -16.5013 | -62.0933 | 57.6957 | 57.8918 | 57.6981 | -65.5359 | -0.10887 | -0.043684 | 2.687 | 1.6535 | 1.7624 | -0.12532 | 0.058019 | -0.35037 | -0.14731 | 4.5507 | 3.0923 | 3.4426 | 0.048803 | -0.14488 | 122.9849 | 122.9032 | 123.0866 | 36.6348 | -123.1374 | 122.8813 | 123.0774 | 122.8837 | 48.6842 | -123.3789
1299.7969 | 123.175 | -65.1489 | 57.8476 | 0.0018314 | -0.010545 | 0.0014616 | 0.056438 | -0.0020533 | 0.06365 | -0.001755 | 0.0030273 | 0.002175 | 0.059093 | 0.021053 | 0.06185 | -62.4482 | -28.2989 | -63.5046 | 57.7948 | 57.7223 | 57.9102 | -65.2807 | -60.6028 | -16.5059 | -62.0658 | 57.714 | 57.8964 | 57.7256 | -65.5313 | -0.13175 | -0.05284 | 2.7008 | 1.6443 | 1.7761 | -0.12531 | 0.062599 | -0.38242 | -0.13357 | 4.5462 | 3.0831 | 3.4655 | 0.048805 | -0.12198 | 122.9437 | 122.8712 | 123.0591 | 36.85 | -123.1283 | 122.863 | 123.0453 | 122.8745 | 48.643 | -123.3789
1300.7969 | 123.0972 | -65.1993 | 57.8293 | -0.0057996 | -0.010758 | 0.0016752 | 0.056438 | -0.0018397 | 0.063009 | -0.001755 | 0.0034545 | 0.0026024 | 0.058879 | 0.020626 | 0.06185 | -62.4161 | -28.0013 | -63.4771 | 57.7856 | 57.7223 | 57.8965 | -65.2944 | -60.5753 | -16.5242 | -62.0429 | 57.6957 | 57.8918 | 57.7531 | -65.5451 | -0.095136 | -0.043686 | 2.7832 | 1.7222 | 1.8173 | -0.107 | 0.067173 | -0.3458 | -0.13357 | 4.624 | 3.1564 | 3.5022 | 0.062536 | -0.076199 | 122.9849 | 122.9216 | 123.0957 | 37.198 | -123.1237 | 122.895 | 123.0911 | 122.9524 | 48.6751 | -123.3744
1301.7969 | 123.1659 | -65.1901 | 57.8247 | 0.0018314 | -0.010117 | 0.0014616 | 0.056224 | -0.0020533 | 0.063437 | -0.001755 | 0.0030273 | 0.002816 | 0.059093 | 0.020839 | 0.062064 | -62.3749 | -27.722 | -63.4542 | 57.7856 | 57.7085 | 57.8919 | -65.2944 | -60.5524 | -16.5242 | -62.0292 | 57.6957 | 57.8827 | 57.6661 | -65.5497 | -0.10429 | -0.039108 | 2.8152 | 1.7359 | 1.8402 | -0.11616 | 0.067173 | -0.35953 | -0.12899 | 4.6377 | 3.1609 | 3.5205 | 0.057957 | -0.15861 | 122.9757 | 122.8987 | 123.082 | 37.4681 | -123.1191 | 122.8858 | 123.0728 | 122.8562 | 48.6659 | -123.3744
1302.7969 | 123.1476 | -65.1718 | 57.8156 | 0.0018314 | -0.010331 | 0.0016752 | 0.056652 | -0.0016259 | 0.063223 | 0.0058755 | 0.0036683 | 0.0026024 | 0.058879 | 0.020626 | 0.062064 | -62.3337 | -27.4244 | -63.4268 | 57.781 | 57.7131 | 57.8919 | -65.2944 | -60.5158 | -16.5425 | -62.02 | 57.6866 | 57.8781 | 57.7302 | -65.5451 | -0.1226 | -0.034532 | 2.8381 | 1.7451 | 1.8677 | -0.10243 | 0.076328 | -0.37327 | -0.129 | 4.6561 | 3.1518 | 3.525 | 0.062533 | -0.085359 | 122.9528 | 122.8849 | 123.0637 | 37.7474 | -123.11 | 122.8584 | 123.0499 | 122.902 | 48.6293 | -123.3606
1303.7969 | 123.1796 | -65.1627 | 57.8064 | 0.0018314 | -0.010117 | 0.0014616 | 0.056224 | -0.0018397 | 0.06365 | -0.001755 | 0.0036683 | 0.0026024 | 0.058666 | 0.020839 | 0.06185 | -62.2971 | -27.1039 | -63.3855 | 57.7948 | 57.6948 | 57.8919 | -65.299 | -60.4929 | -16.5471 | -61.9971 | 57.6866 | 57.8827 | 57.6798 | -65.5451 | -0.13634 | -0.011641 | 2.8656 | 1.7771 | 1.9134 | -0.11159 | 0.085484 | -0.38242 | -0.11984 | 4.6698 | 3.1655 | 3.5479 | 0.076268 | -0.12657 | 122.9574 | 122.8575 | 123.0545 | 38.0587 | -123.1054 | 122.8492 | 123.0453 | 122.8425 | 48.6156 | -123.3515
1304.7969 | 123.1567 | -65.2039 | 57.8476 | 0.0018314 | -0.010331 | 0.0014616 | 0.056438 | -0.0016259 | 0.06365 | 0.0058755 | 0.0036683 | 0.0026024 | 0.058879 | 0.020412 | 0.062491 | -62.2421 | -26.7834 | -63.3581 | 57.781 | 57.6902 | 57.8873 | -65.299 | -60.47 | -16.5471 | -61.9788 | 57.6866 | 57.8827 | 57.6478 | -65.5542 | -0.095138 | -0.066575 | 2.9617 | 1.8458 | 1.9409 | -0.15737 | 0.039706 | -0.35038 | -0.16104 | 4.7339 | 3.225 | 3.5754 | 0.035069 | -0.19982 | 122.9849 | 122.8941 | 123.0912 | 38.4204 | -123.1466 | 122.8904 | 123.0865 | 122.8516 | 48.6568 | -123.4018
1305.7969 | 123.1201 | -65.1718 | 57.8201 | 0.0018314 | -0.010331 | 0.0012478 | 0.056652 | -0.0018397 | 0.06365 | 0.0058755 | 0.0034545 | 0.0023888 | 0.058666 | 0.020626 | 0.062491 | -62.2101 | -26.4767 | -63.326 | 57.781 | 57.6948 | 57.8873 | -65.299 | -60.4379 | -16.5746 | -61.9559 | 57.6866 | 57.8781 | 57.6936 | -65.5497 | -0.12718 | -0.039109 | 2.9617 | 1.8458 | 1.973 | -0.12532 | 0.067172 | -0.37784 | -0.13357 | 4.7339 | 3.2159 | 3.5937 | 0.057956 | -0.12656 | 122.9528 | 122.8666 | 123.0591 | 38.6952 | -123.1191 | 122.8584 | 123.0499 | 122.8654 | 48.5972 | -123.3698
1306.7969 | 123.1842 | -65.1535 | 57.7698 | -0.0057996 | -0.0099038 | 0.0016752 | 0.057079 | -0.0014123 | 0.063223 | -0.0093855 | 0.0034545 | 0.002816 | 0.058879 | 0.020839 | 0.062278 | -62.1597 | -26.266 | -63.294 | 57.7627 | 57.6857 | 57.869 | -65.3036 | -60.4104 | -16.602 | -61.9514 | 57.6728 | 57.8689 | 57.6524 | -65.5588 | -0.15007 | -0.007068 | 2.9938 | 1.8595 | 2.0096 | -0.084125 | 0.099212 | -0.40531 | -0.096955 | 4.7431 | 3.2022 | 3.6075 | 0.099153 | -0.11742 | 122.9162 | 122.8392 | 123.0225 | 38.8875 | -123.0733 | 122.8263 | 123.0224 | 122.8059 | 48.5515 | -123.3286
1307.7969 | 123.1613 | -65.2039 | 57.8201 | 0.0018314 | -0.010117 | 0.0014616 | 0.056438 | -0.0018397 | 0.063864 | -0.001755 | 0.0036683 | 0.002816 | 0.058666 | 0.020626 | 0.062278 | -62.1277 | -26.0783 | -63.2802 | 57.7673 | 57.6719 | 57.869 | -65.3127 | -60.3876 | -16.6204 | -61.9239 | 57.6728 | 57.8689 | 57.6295 | -65.5634 | -0.10887 | -0.052844 | 3.0762 | 1.9236 | 2.0325 | -0.14822 | 0.048858 | -0.35954 | -0.14731 | 4.8163 | 3.28 | 3.6395 | 0.048799 | -0.19067 | 122.9711 | 122.8758 | 123.0728 | 39.1255 | -123.1329 | 122.8767 | 123.0728 | 122.8333 | 48.5835 | -123.3835
1308.7969 | 123.1155 | -65.213 | 57.8201 | 0.0094624 | -0.0099038 | 0.0012478 | 0.056652 | -0.0016259 | 0.06365 | -0.001755 | 0.0032409 | 0.0023888 | 0.058666 | 0.021267 | 0.062491 | -62.0819 | -25.7761 | -63.239 | 57.7673 | 57.6673 | 57.8736 | -65.3127 | -60.3738 | -16.6112 | -61.901 | 57.6728 | 57.8643 | 57.6569 | -65.5634 | -0.099719 | -0.052844 | 3.1311 | 1.974 | 2.0737 | -0.15279 | 0.053436 | -0.35038 | -0.14731 | 4.8392 | 3.312 | 3.6624 | 0.04422 | -0.16319 | 122.9803 | 122.8803 | 123.0866 | 39.4369 | -123.1329 | 122.8858 | 123.0774 | 122.8699 | 48.6018 | -123.3835
1309.7969 | 123.143 | -65.1855 | 57.8064 | -0.013431 | -0.0099038 | 0.0014616 | 0.056652 | -0.0018397 | 0.063864 | 0.0058755 | 0.0032409 | 0.0026024 | 0.058452 | 0.02148 | 0.062064 | -62.0453 | -25.5106 | -63.2116 | 57.7627 | 57.6673 | 57.869 | -65.3082 | -60.3418 | -16.6158 | -61.8964 | 57.6682 | 57.8643 | 57.7302 | -65.568 | -0.12261 | -0.043689 | 3.1403 | 1.974 | 2.0966 | -0.13906 | 0.062591 | -0.38243 | -0.13815 | 4.8438 | 3.2891 | 3.6716 | 0.057953 | -0.076203 | 122.9483 | 122.8529 | 123.0545 | 39.675 | -123.1145 | 122.8538 | 123.0499 | 122.9157 | 48.5698 | -123.3744
1310.7969 | 123.0972 | -65.2039 | 57.8018 | 0.0018314 | -0.0094764 | 0.0016752 | 0.056438 | -0.0016259 | 0.064078 | -0.0093855 | 0.0034545 | 0.0026024 | 0.059093 | 0.020839 | 0.062064 | -61.9903 | -25.1717 | -63.1749 | 57.7627 | 57.6811 | 57.8736 | -65.3082 | -60.296 | -16.6249 | -61.8598 | 57.6728 | 57.8643 | 57.6524 | -65.568 | -0.1043 | -0.039112 | 3.2135 | 2.0289 | 2.1332 | -0.12075 | 0.071746 | -0.36412 | -0.129 | 4.9079 | 3.3441 | 3.7082 | 0.06253 | -0.14946 | 122.9666 | 122.8849 | 123.0774 | 40.0321 | -123.11 | 122.8767 | 123.0682 | 122.8562 | 48.5789 | -123.3698
1311.7969 | 123.1842 | -65.1718 | 57.7652 | 0.0018314 | -0.0094764 | 0.0014616 | 0.056438 | -0.0014123 | 0.064078 | -0.0093855 | 0.0036683 | 0.0026024 | 0.058452 | 0.020839 | 0.062278 | -61.9445 | -24.7826 | -63.1337 | 57.7535 | 57.6628 | 57.8644 | -65.3173 | -60.2731 | -16.6433 | -61.846 | 57.6682 | 57.8643 | 57.6661 | -65.5726 | -0.1455 | -0.011648 | 3.2273 | 2.0381 | 2.1836 | -0.10244 | 0.09921 | -0.40074 | -0.096956 | 4.8987 | 3.3258 | 3.7265 | 0.099151 | -0.099106 | 122.9254 | 122.8346 | 123.0362 | 40.3892 | -123.0825 | 122.8401 | 123.0362 | 122.8379 | 48.5286 | -123.3377
1312.7969 | 123.1064 | -65.1993 | 57.7789 | -0.0057996 | -0.0094764 | 0.0014616 | 0.056652 | -0.0016259 | 0.063864 | -0.001755 | 0.0036683 | 0.002816 | 0.058666 | 0.020839 | 0.062278 | -61.9171 | -24.4163 | -63.1063 | 57.7581 | 57.6673 | 57.8644 | -65.3219 | -60.2502 | -16.6661 | -61.8369 | 57.6637 | 57.8552 | 57.6569 | -65.5863 | -0.12261 | -0.020803 | 3.2822 | 2.093 | 2.2156 | -0.1116 | 0.085477 | -0.38701 | -0.11527 | 4.9491 | 3.3624 | 3.7494 | 0.076261 | -0.122 | 122.9574 | 122.8666 | 123.0637 | 40.783 | -123.1008 | 122.8629 | 123.0545 | 122.8562 | 48.5331 | -123.3652
1313.7969 | 123.1018 | -65.1947 | 57.8064 | -0.0057996 | -0.00969 | 0.0014616 | 0.056011 | -0.0014123 | 0.064291 | -0.001755 | 0.0036683 | 0.0030296 | 0.058879 | 0.021053 | 0.062278 | -61.8713 | -23.9996 | -63.0696 | 57.7444 | 57.6536 | 57.8644 | -65.3356 | -60.2181 | -16.6753 | -61.8186 | 57.6591 | 57.846 | 57.6478 | -65.5817 | -0.14092 | -0.062003 | 3.3234 | 2.1251 | 2.266 | -0.1528 | 0.058012 | -0.38701 | -0.14731 | 4.9766 | 3.3761 | 3.7631 | 0.039639 | -0.15862 | 122.9391 | 122.8483 | 123.0591 | 41.1951 | -123.142 | 122.8538 | 123.0407 | 122.8425 | 48.5194 | -123.3881
1314.7969 | 123.1338 | -65.2176 | 57.7881 | -0.0057996 | -0.0094764 | 0.0018888 | 0.056224 | -0.0014123 | 0.064078 | -0.001755 | 0.0036683 | 0.002816 | 0.058879 | 0.020839 | 0.062491 | -61.8301 | -23.6791 | -63.0376 | 57.7535 | 57.6765 | 57.8553 | -65.3265 | -60.1861 | -16.6524 | -61.7957 | 57.6545 | 57.8552 | 57.6203 | -65.5863 | -0.10888 | -0.034536 | 3.3875 | 2.18 | 2.2889 | -0.11159 | 0.067165 | -0.3687 | -0.13358 | 5.0315 | 3.4219 | 3.7906 | 0.067106 | -0.16778 | 122.9711 | 122.8941 | 123.0728 | 41.5385 | -123.1146 | 122.8721 | 123.0728 | 122.8379 | 48.5652 | -123.3744
1315.7969 | 123.0835 | -65.2084 | 57.8156 | 0.0094624 | -0.0099038 | 0.0014616 | 0.056224 | -0.0011987 | 0.064078 | -0.0093855 | 0.0036683 | 0.002816 | 0.058879 | 0.021053 | 0.062491 | -61.7889 | -23.2487 | -63.0147 | 57.7444 | 57.649 | 57.8507 | -65.3402 | -60.1586 | -16.6616 | -61.7819 | 57.6545 | 57.846 | 57.7073 | -65.5863 | -0.13177 | -0.071159 | 3.4196 | 2.1937 | 2.3255 | -0.16653 | 0.03512 | -0.37785 | -0.16104 | 5.0498 | 3.4265 | 3.8043 | 0.030483 | -0.10825 | 122.9528 | 122.8575 | 123.0591 | 41.9597 | -123.1558 | 122.8629 | 123.0545 | 122.9157 | 48.5469 | -123.4018
1316.7969 | 123.2437 | -65.1398 | 57.7881 | -0.0057996 | -0.0094764 | 0.0012478 | 0.056438 | -0.00098494 | 0.063864 | -0.001755 | 0.0034545 | 0.002816 | 0.058666 | 0.020839 | 0.062278 | -61.7248 | -22.8458 | -62.9643 | 57.749 | 57.6811 | 57.8598 | -65.3173 | -60.1083 | -16.6707 | -61.7499 | 57.6682 | 57.8598 | 57.6478 | -65.5726 | -0.17754 | -0.039114 | 3.415 | 2.1754 | 2.353 | -0.10701 | 0.071743 | -0.43278 | -0.11984 | 5.0315 | 3.3899 | 3.8227 | 0.071685 | -0.14031 | 122.8887 | 122.8208 | 122.9996 | 42.294 | -123.1054 | 122.808 | 122.9995 | 122.7875 | 48.469 | -123.3606
1317.7969 | 123.0743 | -65.213 | 57.8064 | 0.0018314 | -0.0094764 | 0.0018888 | 0.056224 | -0.0014123 | 0.064078 | -0.0093855 | 0.0036683 | 0.002816 | 0.059093 | 0.021053 | 0.062705 | -61.6836 | -22.4566 | -62.9323 | 57.749 | 57.6719 | 57.8598 | -65.3173 | -60.0762 | -16.6661 | -61.7178 | 57.6682 | 57.8598 | 57.6844 | -65.5771 | -0.1043 | -0.057424 | 3.5294 | 2.2807 | 2.385 | -0.13448 | 0.053433 | -0.36412 | -0.13815 | 5.1368 | 3.4952 | 3.8593 | 0.053375 | -0.12199 | 122.962 | 122.8849 | 123.0728 | 42.7564 | -123.1237 | 122.8813 | 123.0728 | 122.8974 | 48.5469 | -123.3835
1318.7969 | 123.2254 | -65.1443 | 57.7606 | -0.0057996 | -0.0094764 | 0.0016752 | 0.056438 | -0.0014123 | 0.064291 | -0.001755 | 0.0040955 | 0.0026024 | 0.058879 | 0.020839 | 0.062491 | -61.6424 | -22.04 | -62.8865 | 57.749 | 57.6628 | 57.8598 | -65.3219 | -60.0442 | -16.6753 | -61.6995 | 57.6682 | 57.8506 | 57.6478 | -65.5771 | -0.17754 | -0.011648 | 3.502 | 2.2578 | 2.4354 | -0.097864 | 0.099209 | -0.43278 | -0.092378 | 5.1002 | 3.4448 | 3.8776 | 0.089994 | -0.11284 | 122.8933 | 122.8071 | 123.0042 | 43.1044 | -123.0825 | 122.8126 | 122.995 | 122.7921 | 48.469 | -123.3378
1319.7969 | 123.1064 | -65.2496 | 57.8064 | 0.0018314 | -0.0092628 | 0.0016752 | 0.056438 | -0.00098494 | 0.064078 | -0.001755 | 0.0038819 | 0.0026024 | 0.058666 | 0.021267 | 0.062919 | -61.6012 | -21.7241 | -62.859 | 57.7352 | 57.6582 | 57.8553 | -65.3219 | -60.0121 | -16.6799 | -61.6812 | 57.6591 | 57.8506 | 57.6936 | -65.5863 | -0.072256 | -0.07116 | 3.6485 | 2.3906 | 2.4628 | -0.14822 | 0.048855 | -0.33665 | -0.14731 | 5.2375 | 3.5684 | 3.9051 | 0.044218 | -0.11283 | 122.9849 | 122.9078 | 123.1049 | 43.5256 | -123.1283 | 122.9087 | 123.1002 | 122.9432 | 48.5698 | -123.3927
1320.7969 | 123.2346 | -65.181 | 57.7652 | 0.0018314 | -0.0092628 | 0.0016752 | 0.056011 | -0.00098494 | 0.064291 | 0.0058755 | 0.0036683 | 0.002816 | 0.058666 | 0.021053 | 0.062705 | -61.56 | -21.3578 | -62.8224 | 57.7444 | 57.6673 | 57.8507 | -65.331 | -59.9938 | -16.7119 | -61.6629 | 57.6454 | 57.8415 | 57.6981 | -65.5863 | -0.15008 | -0.020805 | 3.621 | 2.3586 | 2.5086 | -0.097863 | 0.085474 | -0.40532 | -0.11985 | 5.1872 | 3.5181 | 3.9234 | 0.076258 | -0.067056 | 122.9254 | 122.8483 | 123.0316 | 43.8232 | -123.0962 | 122.8263 | 123.0224 | 122.8791 | 48.469 | -123.3515
1321.7969 | 123.1567 | -65.213 | 57.7789 | 0.0018314 | -0.009049 | 0.0012478 | 0.057079 | -0.0014123 | 0.064291 | 0.013506 | 0.0036683 | 0.0030296 | 0.058879 | 0.021053 | 0.062491 | -61.5187 | -20.9823 | -62.7858 | 57.7398 | 57.6628 | 57.8507 | -65.331 | -59.9617 | -16.7257 | -61.6446 | 57.6545 | 57.8415 | 57.6798 | -65.5863 | -0.11803 | -0.039116 | 3.6943 | 2.4272 | 2.5453 | -0.11617 | 0.071741 | -0.37328 | -0.12442 | 5.2513 | 3.5684 | 3.9417 | 0.062525 | -0.099103 | 122.9528 | 122.8758 | 123.0637 | 44.2307 | -123.11 | 122.8675 | 123.0545 | 122.8928 | 48.4873 | -123.3652
1322.7969 | 123.1934 | -65.1718 | 57.7652 | -0.0057996 | -0.0088354 | 0.0014616 | 0.056438 | -0.0011987 | 0.064291 | 0.0058755 | 0.0038819 | 0.002816 | 0.058666 | 0.02148 | 0.062705 | -61.4867 | -20.6572 | -62.7629 | 57.7307 | 57.6536 | 57.8415 | -65.3448 | -59.9251 | -16.7669 | -61.6308 | 57.6454 | 57.8323 | 57.6981 | -65.6 | -0.17297 | -0.03454 | 3.6851 | 2.4089 | 2.5819 | -0.1116 | 0.076317 | -0.42821 | -0.11985 | 5.2467 | 3.541 | 3.9692 | 0.067101 | -0.067056 | 122.9025 | 122.8254 | 123.0133 | 44.5146 | -123.11 | 122.8172 | 123.0041 | 122.87 | 48.4049 | -123.3652
1323.7969 | 123.0972 | -65.2679 | 57.7835 | -0.0057996 | -0.0088354 | 0.0014616 | 0.056224 | -0.0011987 | 0.064719 | -0.0093855 | 0.0038819 | 0.0030296 | 0.058879 | 0.021267 | 0.062705 | -61.4638 | -20.3551 | -62.7354 | 57.7215 | 57.6353 | 57.8278 | -65.3494 | -59.8976 | -16.7669 | -61.6217 | 57.6316 | 57.8323 | 57.6661 | -65.6183 | -0.081419 | -0.062007 | 3.8041 | 2.5325 | 2.6139 | -0.14823 | 0.044271 | -0.3504 | -0.15189 | 5.3703 | 3.6463 | 3.9967 | 0.048791 | -0.11742 | 122.9894 | 122.9032 | 123.0957 | 44.9129 | -123.1329 | 122.8996 | 123.1002 | 122.934 | 48.5011 | -123.4018
1324.7969 | 123.2208 | -65.2359 | 57.7423 | -0.0057996 | -0.0092628 | 0.0016752 | 0.056652 | -0.0014123 | 0.064505 | 0.013506 | 0.0038819 | 0.0026024 | 0.058879 | 0.021267 | 0.062705 | -61.418 | -20.0712 | -62.708 | 57.7261 | 57.649 | 57.8324 | -65.3585 | -59.8702 | -16.776 | -61.5896 | 57.6362 | 57.8231 | 57.6752 | -65.6138 | -0.12262 | -0.01623 | 3.8179 | 2.5279 | 2.6506 | -0.093291 | 0.090048 | -0.37786 | -0.10612 | 5.3657 | 3.6463 | 4.0241 | 0.080832 | -0.067061 | 122.962 | 122.8849 | 123.0683 | 45.1647 | -123.1008 | 122.8721 | 123.059 | 122.9111 | 48.4599 | -123.3561
1325.7969 | 123.1842 | -65.2405 | 57.7332 | -0.013431 | -0.0088354 | 0.0016752 | 0.056652 | -0.0011987 | 0.064719 | -0.001755 | 0.0040955 | 0.002816 | 0.059093 | 0.02148 | 0.062705 | -61.386 | -19.7782 | -62.6805 | 57.7078 | 57.6353 | 57.814 | -65.3677 | -59.8473 | -16.7486 | -61.5713 | 57.6225 | 57.8323 | 57.6661 | -65.6138 | -0.1272 | -0.025388 | 3.8545 | 2.56 | 2.6872 | -0.097872 | 0.080889 | -0.37328 | -0.1107 | 5.3932 | 3.6692 | 4.0424 | 0.099145 | -0.067062 | 122.9482 | 122.8758 | 123.0545 | 45.4623 | -123.1008 | 122.8629 | 123.0728 | 122.9066 | 48.4919 | -123.3469
1326.7969 | 123.1522 | -65.2451 | 57.7606 | 0.0018314 | -0.0088354 | 0.0018888 | 0.056224 | -0.0014123 | 0.064932 | -0.001755 | 0.0040955 | 0.0030296 | 0.059093 | 0.021267 | 0.062705 | -61.3631 | -19.508 | -62.6484 | 57.7032 | 57.6399 | 57.8186 | -65.3677 | -59.8152 | -16.7715 | -61.5576 | 57.6225 | 57.814 | 57.6524 | -65.6229 | -0.12262 | -0.057432 | 3.882 | 2.5966 | 2.7192 | -0.12076 | 0.058002 | -0.37786 | -0.13816 | 5.4298 | 3.6875 | 4.0653 | 0.053365 | -0.10826 | 122.9482 | 122.8849 | 123.0637 | 45.737 | -123.1283 | 122.8675 | 123.059 | 122.8974 | 48.4736 | -123.3835
1327.7969 | 123.2071 | -65.2496 | 57.6965 | -0.0057996 | -0.0088354 | 0.0014616 | 0.056224 | -0.0011987 | 0.064719 | -0.0093855 | 0.0036683 | 0.0026024 | 0.058666 | 0.021267 | 0.062919 | -61.3127 | -19.2287 | -62.6164 | 57.7078 | 57.6307 | 57.8186 | -65.3631 | -59.7832 | -16.776 | -61.5301 | 57.6225 | 57.814 | 57.689 | -65.6229 | -0.11347 | 0.011233 | 3.9369 | 2.6332 | 2.7467 | -0.06583 | 0.12209 | -0.37328 | -0.074076 | 5.4665 | 3.7195 | 4.0928 | 0.11745 | -0.007548 | 122.9574 | 122.8803 | 123.0683 | 46.0209 | -123.0596 | 122.8721 | 123.0636 | 122.9386 | 48.4736 | -123.3195
1328.7969 | 123.2025 | -65.2222 | 57.7286 | -0.0057996 | -0.0092628 | 0.0018888 | 0.056652 | -0.00077134 | 0.064505 | 0.0058755 | 0.0038819 | 0.0032434 | 0.058879 | 0.021267 | 0.062919 | -61.2715 | -18.9632 | -62.5889 | 57.7078 | 57.6353 | 57.814 | -65.3631 | -59.742 | -16.7715 | -61.5118 | 57.6179 | 57.814 | 57.6569 | -65.6275 | -0.14093 | -0.020811 | 3.9507 | 2.6332 | 2.7742 | -0.093295 | 0.085466 | -0.40533 | -0.1107 | 5.4802 | 3.7104 | 4.1157 | 0.085408 | -0.071642 | 122.9299 | 122.8575 | 123.0362 | 46.259 | -123.0917 | 122.84 | 123.0362 | 122.8791 | 48.4507 | -123.3561
1329.7969 | 123.1338 | -65.2588 | 57.7698 | -0.021062 | -0.0088354 | 0.0018888 | 0.056652 | -0.00098494 | 0.064505 | -0.001755 | 0.0038819 | 0.0026024 | 0.058879 | 0.021267 | 0.062705 | -61.2212 | -18.7342 | -62.566 | 57.7078 | 57.6444 | 57.8186 | -65.3539 | -59.7053 | -16.7852 | -61.4843 | 57.6179 | 57.814 | 57.6752 | -65.6229 | -0.095153 | -0.062009 | 4.0376 | 2.6928 | 2.7879 | -0.12533 | 0.048847 | -0.36413 | -0.1519 | 5.5535 | 3.7745 | 4.1386 | 0.04421 | -0.094526 | 122.9666 | 122.9032 | 123.0774 | 46.5246 | -123.1237 | 122.8767 | 123.0728 | 122.934 | 48.4736 | -123.3927
1330.7969 | 123.2162 | -65.2267 | 57.7377 | -0.013431 | -0.0086218 | 0.0016752 | 0.056438 | -0.00098494 | 0.064932 | 0.0058755 | 0.0043091 | 0.002816 | 0.058666 | 0.021694 | 0.062919 | -61.1891 | -18.5236 | -62.5386 | 57.7032 | 57.617 | 57.8049 | -65.3768 | -59.6733 | -16.7989 | -61.4706 | 57.6087 | 57.7957 | 57.6432 | -65.6275 | -0.15009 | -0.034544 | 4.0376 | 2.6882 | 2.8383 | -0.12077 | 0.067154 | -0.40075 | -0.12901 | 5.5535 | 3.7562 | 4.1569 | 0.057938 | -0.094533 | 122.9299 | 122.8437 | 123.0316 | 46.7031 | -123.1146 | 122.8355 | 123.0224 | 122.8699 | 48.4278 | -123.3652
1331.7969 | 123.1613 | -65.2176 | 57.7011 | -0.021062 | -0.0088354 | 0.0018888 | 0.056652 | -0.00055774 | 0.064505 | 0.0058755 | 0.0038819 | 0.0030296 | 0.058879 | 0.021053 | 0.062919 | -61.1571 | -18.3267 | -62.5157 | 57.7032 | 57.6261 | 57.8049 | -65.3768 | -59.6458 | -16.8035 | -61.4431 | 57.6041 | 57.8094 | 57.6203 | -65.6321 | -0.15925 | 0.002077 | 4.0605 | 2.7019 | 2.8612 | -0.074987 | 0.10378 | -0.41449 | -0.096968 | 5.5718 | 3.7745 | 4.189 | 0.1083 | -0.080805 | 122.9208 | 122.8437 | 123.0225 | 46.8909 | -123.0779 | 122.8217 | 123.027 | 122.8379 | 48.4141 | -123.3332
1332.7969 | 123.1888 | -65.2267 | 57.7103 | -0.0057996 | -0.0088354 | 0.0014616 | 0.056652 | -0.00077134 | 0.064932 | -0.001755 | 0.0040955 | 0.0030296 | 0.058879 | 0.021694 | 0.063346 | -61.1067 | -18.1711 | -62.4882 | 57.6986 | 57.6353 | 57.8003 | -65.3723 | -59.6 | -16.8035 | -61.4111 | 57.6133 | 57.7957 | 57.6249 | -65.6321 | -0.14551 | -0.011657 | 4.1201 | 2.7385 | 2.8841 | -0.074984 | 0.090041 | -0.40533 | -0.096966 | 5.6267 | 3.8157 | 4.221 | 0.085404 | -0.085381 | 122.9254 | 122.862 | 123.0271 | 47.0557 | -123.0825 | 122.84 | 123.0224 | 122.8516 | 48.4232 | -123.3423
1333.7969 | 123.1979 | -65.2084 | 57.7286 | -0.0057996 | -0.0086218 | 0.0014616 | 0.056865 | -0.00098494 | 0.064932 | -0.001755 | 0.0045227 | 0.0032434 | 0.058879 | 0.021694 | 0.062919 | -61.093 | -18.0062 | -62.4699 | 57.6895 | 57.617 | 57.8095 | -65.3906 | -59.5863 | -16.8447 | -61.3973 | 57.595 | 57.7957 | 57.602 | -65.6412 | -0.18214 | -0.039125 | 4.1155 | 2.7385 | 2.9207 | -0.11161 | 0.080888 | -0.4328 | -0.13359 | 5.6222 | 3.8111 | 4.2439 | 0.067093 | -0.12658 | 122.8979 | 122.8254 | 123.0179 | 47.2022 | -123.1192 | 122.8034 | 123.0041 | 122.8104 | 48.3637 | -123.3698
1334.7969 | 123.1659 | -65.2405 | 57.6965 | 0.0018314 | -0.009049 | 0.0016752 | 0.056865 | -0.00055774 | 0.064932 | -0.001755 | 0.0040955 | 0.0030296 | 0.059093 | 0.021908 | 0.063132 | -61.0472 | -17.8735 | -62.447 | 57.694 | 57.6078 | 57.7957 | -65.3814 | -59.5497 | -16.8585 | -61.3699 | 57.5996 | 57.7911 | 57.6295 | -65.6458 | -0.14094 | -0.002502 | 4.1933 | 2.7935 | 2.9344 | -0.088724 | 0.099196 | -0.40533 | -0.096968 | 5.6908 | 3.8706 | 4.276 | 0.094559 | -0.06707 | 122.9345 | 122.8483 | 123.0362 | 47.367 | -123.0779 | 122.84 | 123.0316 | 122.8699 | 48.382 | -123.3423
1335.7969 | 123.1796 | -65.2725 | 57.7103 | -0.013431 | -0.0086218 | 0.0012478 | 0.056438 | -0.00098494 | 0.064719 | 0.0058755 | 0.0038819 | 0.0032434 | 0.058879 | 0.021694 | 0.062919 | -61.0151 | -17.7315 | -62.4333 | 57.6803 | 57.6124 | 57.7912 | -65.3906 | -59.5268 | -16.8905 | -61.3515 | 57.5996 | 57.7865 | 57.634 | -65.6458 | -0.11805 | -0.02997 | 4.2574 | 2.8393 | 2.9573 | -0.097878 | 0.080884 | -0.37329 | -0.1107 | 5.7458 | 3.921 | 4.2943 | 0.076247 | -0.076224 | 122.9528 | 122.8849 | 123.0637 | 47.541 | -123.1008 | 122.8721 | 123.059 | 122.9066 | 48.382 | -123.3561
1336.7969 | 123.2071 | -65.2267 | 57.6874 | 0.0018314 | -0.008408 | 0.0014616 | 0.056865 | -0.00055774 | 0.064932 | -0.0093855 | 0.0043091 | 0.0032434 | 0.059307 | 0.02148 | 0.063132 | -60.9831 | -17.6033 | -62.4012 | 57.6757 | 57.6124 | 57.7912 | -65.3952 | -59.4947 | -16.8997 | -61.3286 | 57.595 | 57.7819 | 57.6478 | -65.6458 | -0.16841 | -0.011661 | 4.2437 | 2.8255 | 2.9939 | -0.07499 | 0.10377 | -0.41907 | -0.092392 | 5.732 | 3.8981 | 4.3172 | 0.094556 | -0.0396 | 122.9025 | 122.8391 | 123.0179 | 47.6234 | -123.0825 | 122.8217 | 123.0087 | 122.8745 | 48.3271 | -123.3332
1337.7969 | 123.1979 | -65.2451 | 57.6782 | 0.0018314 | -0.008408 | 0.0018888 | 0.056652 | -0.00077134 | 0.064719 | -0.001755 | 0.0040955 | 0.0032434 | 0.059093 | 0.021694 | 0.062919 | -60.9419 | -17.4934 | -62.3783 | 57.6803 | 57.6124 | 57.7957 | -65.3906 | -59.4443 | -16.8997 | -61.3058 | 57.5904 | 57.7865 | 57.6524 | -65.655 | -0.14552 | 0.002073 | 4.3032 | 2.8667 | 3.0122 | -0.065835 | 0.11751 | -0.40991 | -0.087815 | 5.8007 | 3.9393 | 4.3492 | 0.10829 | -0.025867 | 122.9254 | 122.8574 | 123.0408 | 47.7516 | -123.0688 | 122.8355 | 123.0316 | 122.8974 | 48.3454 | -123.3332
1338.7969 | 123.2117 | -65.2542 | 57.6828 | 0.0018314 | -0.0086218 | 0.0018888 | 0.056652 | -0.00098494 | 0.06536 | -0.0093855 | 0.0045227 | 0.0030296 | 0.058666 | 0.021694 | 0.062919 | -60.9052 | -17.3835 | -62.3509 | 57.6757 | 57.6124 | 57.7957 | -65.3814 | -59.4031 | -16.9226 | -61.2737 | 57.5996 | 57.7865 | 57.6157 | -65.6458 | -0.12721 | -0.007083 | 4.349 | 2.9034 | 3.0306 | -0.070412 | 0.11293 | -0.3916 | -0.083235 | 5.8511 | 3.9805 | 4.3721 | 0.10371 | -0.067072 | 122.9299 | 122.8666 | 123.0499 | 47.8707 | -123.0642 | 122.8538 | 123.0407 | 122.8699 | 48.3317 | -123.3286
1339.7969 | 123.23 | -65.2267 | 57.6874 | -0.013431 | -0.008408 | 0.0016752 | 0.056652 | -0.00077134 | 0.06536 | -0.001755 | 0.0040955 | 0.0030296 | 0.059307 | 0.02148 | 0.062919 | -60.8732 | -17.3149 | -62.3417 | 57.6849 | 57.6078 | 57.7957 | -65.3814 | -59.3757 | -16.9271 | -61.2462 | 57.595 | 57.7865 | 57.634 | -65.6412 | -0.15467 | -0.002504 | 4.3535 | 2.885 | 3.0397 | -0.079569 | 0.10835 | -0.41449 | -0.092392 | 5.8511 | 3.9805 | 4.395 | 0.099135 | -0.053336 | 122.9116 | 122.8346 | 123.0225 | 47.9119 | -123.0688 | 122.8217 | 123.0133 | 122.8608 | 48.2996 | -123.3286
1340.8594 | 123.2483 | -65.2267 | 57.7194 | 0.0018314 | -0.0081944 | 0.0016752 | 0.056438 | -0.00077134 | 0.064719 | -0.017016 | 0.0043091 | 0.002816 | 0.058879 | 0.021694 | 0.063132 | -60.832 | -17.2462 | -62.3051 | 57.6803 | 57.6261 | 57.7957 | -65.3906 | -59.3253 | -16.9409 | -61.2142 | 57.5996 | 57.7865 | 57.6157 | -65.6504 | -0.16383 | -0.039125 | 4.3948 | 2.9217 | 3.0855 | -0.093297 | 0.076308 | -0.42365 | -0.11986 | 5.9015 | 4.0126 | 4.4362 | 0.067092 | -0.10369 | 122.907 | 122.8529 | 123.0225 | 47.9806 | -123.11 | 122.8263 | 123.0133 | 122.8425 | 48.2859 | -123.3698
1341.7969 | 123.2391 | -65.2176 | 57.692 | -0.013431 | -0.008408 | 0.0016752 | 0.056652 | -0.00077134 | 0.064932 | -0.001755 | 0.0043091 | 0.0030296 | 0.059093 | 0.021908 | 0.063346 | -60.7816 | -17.1729 | -62.2822 | 57.6895 | 57.6124 | 57.8003 | -65.3814 | -59.2887 | -16.9409 | -61.1959 | 57.595 | 57.7865 | 57.6432 | -65.6412 | -0.16383 | -0.002504 | 4.436 | 2.9354 | 3.0992 | -0.079568 | 0.10835 | -0.42364 | -0.09697 | 5.9289 | 4.0217 | 4.4454 | 0.094557 | -0.048757 | 122.907 | 122.83 | 123.0179 | 48.0447 | -123.0734 | 122.8126 | 123.0041 | 122.8608 | 48.2767 | -123.3332
1342.7969 | 123.1796 | -65.2359 | 57.6782 | -0.0057996 | -0.0086218 | 0.0018888 | 0.056652 | -0.00098494 | 0.064932 | -0.001755 | 0.0043091 | 0.0032434 | 0.059093 | 0.021694 | 0.062919 | -60.7633 | -17.1043 | -62.2684 | 57.6849 | 57.5987 | 57.7957 | -65.386 | -59.2566 | -16.9592 | -61.1684 | 57.595 | 57.7865 | 57.6295 | -65.6504 | -0.15009 | 0.006651 | 4.4726 | 2.9675 | 3.1175 | -0.079572 | 0.11751 | -0.41449 | -0.083237 | 5.9793 | 4.0675 | 4.482 | 0.10829 | -0.04876 | 122.9208 | 122.8346 | 123.0316 | 48.1316 | -123.0642 | 122.8309 | 123.0224 | 122.8654 | 48.2767 | -123.3286
1343.7969 | 123.2346 | -65.2405 | 57.7011 | -0.0057996 | -0.008408 | 0.0018888 | 0.056652 | -0.00055774 | 0.065146 | -0.001755 | 0.0043091 | 0.0030296 | 0.059307 | 0.022335 | 0.063132 | -60.7267 | -17.0539 | -62.241 | 57.6849 | 57.6124 | 57.7912 | -65.3814 | -59.22 | -16.9729 | -61.1363 | 57.5996 | 57.7911 | 57.6066 | -65.6458 | -0.14094 | -0.016237 | 4.5138 | 2.9995 | 3.1404 | -0.088723 | 0.090039 | -0.40533 | -0.10155 | 6.0205 | 4.1041 | 4.5095 | 0.089981 | -0.094541 | 122.9254 | 122.8529 | 123.0316 | 48.1866 | -123.0825 | 122.84 | 123.0316 | 122.847 | 48.2676 | -123.3469
1344.7969 | 123.1979 | -65.2359 | 57.724 | 0.0018314 | -0.008408 | 0.0018888 | 0.057293 | -0.00055774 | 0.065146 | -0.001755 | 0.0047365 | 0.0030296 | 0.058879 | 0.021908 | 0.063132 | -60.6901 | -17.0218 | -62.2181 | 57.6895 | 57.6124 | 57.7912 | -65.386 | -59.1742 | -16.9729 | -61.1089 | 57.595 | 57.7911 | 57.6478 | -65.6412 | -0.15009 | -0.034547 | 4.5458 | 3.0178 | 3.1679 | -0.11161 | 0.067151 | -0.40533 | -0.12901 | 6.0617 | 4.127 | 4.5324 | 0.067093 | -0.076221 | 122.9254 | 122.8483 | 123.0271 | 48.2141 | -123.11 | 122.8309 | 123.027 | 122.8837 | 48.263 | -123.3652
1345.7969 | 123.1796 | -65.2313 | 57.724 | 0.0018314 | -0.008408 | 0.0014616 | 0.056865 | -0.00055774 | 0.065573 | -0.001755 | 0.0045227 | 0.0032434 | 0.058879 | 0.021908 | 0.063346 | -60.6534 | -16.9348 | -62.1998 | 57.6895 | 57.5941 | 57.7957 | -65.3814 | -59.1284 | -17.005 | -61.0768 | 57.595 | 57.7911 | 57.6615 | -65.6458 | -0.15009 | -0.034547 | 4.5779 | 3.0316 | 3.1816 | -0.12993 | 0.07173 | -0.41449 | -0.12901 | 6.1029 | 4.1545 | 4.569 | 0.067093 | -0.062485 | 122.9208 | 122.8254 | 123.0271 | 48.2965 | -123.1054 | 122.8263 | 123.0224 | 122.8928 | 48.2264 | -123.3698
1346.7969 | 123.1934 | -65.2176 | 57.7377 | 0.0094624 | -0.0081944 | 0.0021026 | 0.056865 | -0.00098494 | 0.065146 | -0.001755 | 0.0049501 | 0.0032434 | 0.058666 | 0.021694 | 0.063132 | -60.6077 | -16.8799 | -62.1723 | 57.6895 | 57.6078 | 57.8049 | -65.3768 | -59.078 | -17.0691 | -61.0448 | 57.6087 | 57.7957 | 57.6249 | -65.6412 | -0.15925 | -0.04828 | 4.6099 | 3.0453 | 3.2045 | -0.12992 | 0.067154 | -0.42364 | -0.12901 | 6.1395 | 4.1728 | 4.5965 | 0.057938 | -0.11285 | 122.907 | 122.8254 | 123.0225 | 48.3377 | -123.1146 | 122.8263 | 123.0133 | 122.8425 | 48.1485 | -123.379
1347.7969 | 123.2117 | -65.2222 | 57.7103 | -0.0057996 | -0.008408 | 0.0018888 | 0.056865 | -0.00077134 | 0.065573 | -0.0093855 | 0.0047365 | 0.0030296 | 0.058666 | 0.021908 | 0.06356 | -60.571 | -16.7471 | -62.154 | 57.6986 | 57.5987 | 57.814 | -65.3723 | -59.0323 | -17.1103 | -61.0127 | 57.6133 | 57.8002 | 57.515 | -65.6321 | -0.15009 | -0.011657 | 4.6511 | 3.0682 | 3.2183 | -0.11162 | 0.10378 | -0.40991 | -0.096966 | 6.1899 | 4.2095 | 4.6194 | 0.089983 | -0.19527 | 122.9208 | 122.8208 | 123.0362 | 48.475 | -123.0825 | 122.8355 | 123.0224 | 122.7372 | 48.1119 | -123.3423
1348.7969 | 123.1796 | -65.2084 | 57.7698 | 0.0018314 | -0.0081944 | 0.0018888 | 0.057079 | -0.00034394 | 0.065146 | -0.0093855 | 0.0045227 | 0.003457 | 0.059093 | 0.021694 | 0.06356 | -60.5207 | -16.7151 | -62.1174 | 57.694 | 57.5987 | 57.814 | -65.3723 | -58.9865 | -17.0874 | -60.9669 | 57.6225 | 57.8094 | 57.6524 | -65.6275 | -0.16382 | -0.075744 | 4.6878 | 3.0911 | 3.2549 | -0.17112 | 0.044268 | -0.41906 | -0.14732 | 6.222 | 4.2415 | 4.6606 | 0.039631 | -0.11742 | 122.9025 | 122.8071 | 123.0225 | 48.4934 | -123.142 | 122.8309 | 123.0178 | 122.8608 | 48.121 | -123.3973
1349.7969 | 123.1888 | -65.2222 | 57.7194 | -0.0057996 | -0.0081944 | 0.0023162 | 0.056865 | -0.00055774 | 0.064932 | -0.0093855 | 0.0043091 | 0.0032434 | 0.059093 | 0.022122 | 0.063346 | -60.4932 | -16.7059 | -62.099 | 57.6986 | 57.6078 | 57.8003 | -65.3723 | -58.9407 | -17.1149 | -60.9349 | 57.6225 | 57.8048 | 57.5425 | -65.6321 | -0.15009 | -0.020812 | 4.729 | 3.1231 | 3.2732 | -0.11161 | 0.080886 | -0.40991 | -0.096964 | 6.2815 | 4.2873 | 4.6972 | 0.085406 | -0.17695 | 122.9208 | 122.83 | 123.0225 | 48.5163 | -123.0917 | 122.8446 | 123.027 | 122.7646 | 48.1073 | -123.3515
1350.7969 | 123.175 | -65.2084 | 57.7652 | 0.0018314 | -0.0081944 | 0.0018888 | 0.056865 | -0.00077134 | 0.065573 | -0.001755 | 0.0049501 | 0.0030296 | 0.058879 | 0.022122 | 0.06356 | -60.452 | -16.651 | -62.067 | 57.7078 | 57.6124 | 57.814 | -65.3585 | -58.9041 | -17.1606 | -60.8982 | 57.6225 | 57.814 | 57.5837 | -65.6229 | -0.15009 | -0.057432 | 4.7564 | 3.1414 | 3.2915 | -0.15281 | 0.048845 | -0.41448 | -0.14274 | 6.3044 | 4.3102 | 4.7247 | 0.048787 | -0.18152 | 122.9162 | 122.8208 | 123.0225 | 48.5575 | -123.1237 | 122.8309 | 123.0224 | 122.7921 | 48.0478 | -123.3881
1351.7969 | 123.2071 | -65.1947 | 57.724 | -0.013431 | -0.0079808 | 0.0018888 | 0.056652 | -0.00034394 | 0.065573 | -0.0093855 | 0.0043091 | 0.003457 | 0.058879 | 0.022122 | 0.063346 | -60.4154 | -16.6052 | -62.0487 | 57.7078 | 57.6078 | 57.814 | -65.3585 | -58.8583 | -17.179 | -60.857 | 57.627 | 57.8094 | 57.5883 | -65.6183 | -0.16382 | -0.016233 | 4.7793 | 3.146 | 3.3098 | -0.11619 | 0.090044 | -0.42364 | -0.096963 | 6.3364 | 4.3377 | 4.7613 | 0.085407 | -0.13574 | 122.9025 | 122.8025 | 123.0087 | 48.5895 | -123.0825 | 122.8217 | 123.0041 | 122.783 | 48.0157 | -123.3423
1352.7969 | 123.1567 | -65.2084 | 57.7469 | 0.0018314 | -0.008408 | 0.0016752 | 0.057079 | -0.00077134 | 0.06536 | 0.0058755 | 0.0045227 | 0.0030296 | 0.058666 | 0.022335 | 0.063346 | -60.3787 | -16.5411 | -62.0166 | 57.7169 | 57.6215 | 57.8369 | -65.3448 | -58.8125 | -17.179 | -60.8158 | 57.6316 | 57.8277 | 57.5791 | -65.6092 | -0.13635 | -0.029964 | 4.8297 | 3.1918 | 3.3281 | -0.12534 | 0.090049 | -0.40075 | -0.11527 | 6.396 | 4.3926 | 4.7934 | 0.080833 | -0.16779 | 122.9254 | 122.83 | 123.0454 | 48.6674 | -123.0917 | 122.84 | 123.0362 | 122.7875 | 48.0295 | -123.3561
1353.7969 | 123.1934 | -65.1901 | 57.7377 | -0.0057996 | -0.008408 | 0.0014616 | 0.056865 | -0.00055774 | 0.06536 | -0.001755 | 0.0047365 | 0.0032434 | 0.059093 | 0.021908 | 0.063346 | -60.3329 | -16.509 | -61.9937 | 57.7215 | 57.6307 | 57.8369 | -65.3494 | -58.7759 | -17.2064 | -60.7838 | 57.6362 | 57.8277 | 57.6844 | -65.6138 | -0.15924 | -0.016231 | 4.8572 | 3.1964 | 3.3556 | -0.10703 | 0.099204 | -0.42364 | -0.10154 | 6.4143 | 4.4063 | 4.83 | 0.089988 | -0.053325 | 122.9116 | 122.8208 | 123.0271 | 48.6811 | -123.0871 | 122.8263 | 123.0178 | 122.8745 | 47.9837 | -123.3515
1354.7969 | 123.2071 | -65.1718 | 57.7835 | -0.0057996 | -0.008408 | 0.0018888 | 0.057293 | -0.00055774 | 0.065573 | 0.0058755 | 0.0051637 | 0.002816 | 0.058879 | 0.022335 | 0.063773 | -60.3055 | -16.4861 | -61.9663 | 57.7307 | 57.6353 | 57.8324 | -65.3448 | -58.7392 | -17.2339 | -60.7517 | 57.6362 | 57.8277 | 57.6478 | -65.6092 | -0.17297 | -0.05285 | 4.8663 | 3.2055 | 3.3785 | -0.14823 | 0.04885 | -0.43737 | -0.14731 | 6.4326 | 4.4201 | 4.8575 | 0.044212 | -0.13573 | 122.9025 | 122.8071 | 123.0042 | 48.6857 | -123.1283 | 122.808 | 122.9995 | 122.8196 | 47.9379 | -123.3927
1355.7969 | 123.1934 | -65.1764 | 57.7606 | -0.0057996 | -0.0081944 | 0.0016752 | 0.056652 | -0.00034394 | 0.065787 | -0.0093855 | 0.0049501 | 0.0032434 | 0.058666 | 0.022122 | 0.063346 | -60.2734 | -16.4678 | -61.9434 | 57.7307 | 57.6444 | 57.8369 | -65.3448 | -58.6934 | -17.2431 | -60.7105 | 57.6499 | 57.8323 | 57.6157 | -65.6092 | -0.16839 | -0.029962 | 4.903 | 3.233 | 3.4014 | -0.11618 | 0.076316 | -0.43279 | -0.11069 | 6.483 | 4.4659 | 4.8987 | 0.071679 | -0.14489 | 122.907 | 122.8208 | 123.0133 | 48.7086 | -123.1054 | 122.8263 | 123.0087 | 122.7921 | 47.9333 | -123.3698
1356.7969 | 123.1705 | -65.1718 | 57.7881 | -0.0057996 | -0.0081944 | 0.0018888 | 0.056652 | -0.00055774 | 0.06536 | -0.001755 | 0.0045227 | 0.0032434 | 0.058879 | 0.022335 | 0.06356 | -60.2322 | -16.4404 | -61.9068 | 57.7352 | 57.649 | 57.8507 | -65.331 | -58.6248 | -17.2614 | -60.6602 | 57.6454 | 57.8415 | 57.6936 | -65.5954 | -0.15923 | -0.05285 | 4.9396 | 3.2651 | 3.4243 | -0.13907 | 0.062586 | -0.42363 | -0.14274 | 6.5471 | 4.5117 | 4.9353 | 0.05337 | -0.094522 | 122.907 | 122.8208 | 123.0225 | 48.7315 | -123.1191 | 122.8172 | 123.0133 | 122.8654 | 47.9104 | -123.3835
1357.7969 | 123.1659 | -65.1855 | 57.7789 | 0.0018314 | -0.008408 | 0.0018888 | 0.057293 | -0.00077134 | 0.065573 | -0.001755 | 0.0049501 | 0.0032434 | 0.058879 | 0.022122 | 0.06356 | -60.191 | -16.4404 | -61.893 | 57.7352 | 57.6628 | 57.8553 | -65.3219 | -58.5835 | -17.2751 | -60.6144 | 57.6591 | 57.8598 | 57.7027 | -65.5817 | -0.13634 | -0.043695 | 4.9945 | 3.2925 | 3.4289 | -0.11617 | 0.07632 | -0.39616 | -0.11985 | 6.602 | 4.5712 | 4.9673 | 0.08084 | -0.07621 | 122.9208 | 122.8483 | 123.0408 | 48.7452 | -123.1008 | 122.8446 | 123.0453 | 122.8883 | 47.9104 | -123.3606
1358.7969 | 123.2346 | -65.1215 | 57.7789 | 0.0018314 | -0.008408 | 0.0021026 | 0.057079 | -0.00013034 | 0.065573 | 0.021136 | 0.0053773 | 0.0038844 | 0.059093 | 0.022335 | 0.06356 | -60.159 | -16.3808 | -61.8564 | 57.7444 | 57.6582 | 57.8553 | -65.3219 | -58.5286 | -17.2888 | -60.5915 | 57.6591 | 57.8552 | 57.6203 | -65.5771 | -0.20043 | -0.034538 | 4.9625 | 3.2651 | 3.4655 | -0.12075 | 0.07632 | -0.45567 | -0.11985 | 6.5929 | 4.53 | 4.9857 | 0.076261 | -0.15863 | 122.8659 | 122.7796 | 122.9767 | 48.7406 | -123.1008 | 122.7805 | 122.9767 | 122.7418 | 47.8326 | -123.3561
1359.7969 | 123.1705 | -65.1535 | 57.7652 | -0.0057996 | -0.008408 | 0.0018888 | 0.057079 | -0.00055774 | 0.065573 | 0.0058755 | 0.0047365 | 0.0036706 | 0.05952 | 0.022122 | 0.06356 | -60.1178 | -16.2984 | -61.8335 | 57.7535 | 57.6628 | 57.8644 | -65.3127 | -58.4874 | -17.3438 | -60.5365 | 57.6728 | 57.8506 | 57.6844 | -65.5726 | -0.15923 | -0.011648 | 5.0357 | 3.32 | 3.4792 | -0.10244 | 0.09921 | -0.41905 | -0.092378 | 6.6661 | 4.617 | 5.036 | 0.085416 | -0.080791 | 122.9071 | 122.8163 | 123.0179 | 48.8551 | -123.0779 | 122.8263 | 123.0041 | 122.8379 | 47.8097 | -123.3377
1360.7969 | 123.2346 | -65.1489 | 57.8064 | 0.0018314 | -0.007767 | 0.0018888 | 0.056865 | -0.00055774 | 0.065787 | -0.001755 | 0.0049501 | 0.0038844 | 0.059093 | 0.022122 | 0.06356 | -60.0766 | -16.303 | -61.8015 | 57.7535 | 57.6628 | 57.8598 | -65.3127 | -58.4324 | -17.385 | -60.4999 | 57.6774 | 57.8598 | 57.7119 | -65.5726 | -0.16381 | -0.052846 | 5.0724 | 3.3475 | 3.5113 | -0.14364 | 0.053433 | -0.42363 | -0.129 | 6.7165 | 4.649 | 5.0727 | 0.053375 | -0.094518 | 122.9025 | 122.8117 | 123.0088 | 48.8459 | -123.1191 | 122.8263 | 123.0087 | 122.8608 | 47.7639 | -123.3789
1361.7969 | 123.1659 | -65.1535 | 57.7927 | 0.0018314 | -0.0081944 | 0.0021026 | 0.056652 | -0.00055774 | 0.065573 | -0.001755 | 0.0053773 | 0.003457 | 0.059307 | 0.022335 | 0.063987 | -60.0308 | -16.303 | -61.7694 | 57.7627 | 57.6811 | 57.8781 | -65.2944 | -58.3683 | -17.4079 | -60.4587 | 57.6774 | 57.8735 | 57.721 | -65.5634 | -0.14091 | -0.029957 | 5.1227 | 3.3841 | 3.525 | -0.11159 | 0.08548 | -0.40989 | -0.11527 | 6.7852 | 4.6948 | 5.1047 | 0.080843 | -0.071629 | 122.9162 | 122.8346 | 123.0316 | 48.8505 | -123.0871 | 122.8309 | 123.027 | 122.8745 | 47.7456 | -123.3561
1362.7969 | 123.23 | -65.1123 | 57.8201 | 0.0018314 | -0.0081944 | 0.0018888 | 0.057079 | -0.00077134 | 0.065573 | 0.013506 | 0.0051637 | 0.003457 | 0.059093 | 0.022549 | 0.06356 | -59.9987 | -16.3259 | -61.7465 | 57.781 | 57.6948 | 57.8919 | -65.2944 | -58.3134 | -17.4628 | -60.3992 | 57.6911 | 57.8918 | 57.721 | -65.5497 | -0.18211 | -0.039109 | 5.1136 | 3.3658 | 3.5479 | -0.12532 | 0.071751 | -0.43735 | -0.129 | 6.7989 | 4.7131 | 5.1505 | 0.071692 | -0.099094 | 122.8933 | 122.8071 | 123.0042 | 48.7864 | -123.1145 | 122.8034 | 123.0041 | 122.8333 | 47.6495 | -123.3698
1363.7969 | 123.2071 | -65.1398 | 57.8247 | 0.0018314 | -0.007767 | 0.0021026 | 0.057079 | -0.00055774 | 0.065573 | -0.001755 | 0.0051637 | 0.003457 | 0.059307 | 0.022763 | 0.063773 | -59.9575 | -16.2984 | -61.7145 | 57.7856 | 57.704 | 57.8965 | -65.2898 | -58.2676 | -17.4903 | -60.3625 | 57.7003 | 57.8918 | 57.721 | -65.5313 | -0.15007 | -0.039108 | 5.1823 | 3.4253 | 3.5754 | -0.12074 | 0.071751 | -0.39157 | -0.12442 | 6.8722 | 4.7772 | 5.1688 | 0.067114 | -0.10367 | 122.9254 | 122.8437 | 123.0362 | 48.8414 | -123.1145 | 122.8401 | 123.0316 | 122.8608 | 47.6495 | -123.3561
1364.7969 | 123.2208 | -65.1077 | 57.8384 | 0.0094624 | -0.0081944 | 0.0016752 | 0.056865 | -0.00055774 | 0.065787 | -0.0093855 | 0.0051637 | 0.003457 | 0.059093 | 0.022549 | 0.063773 | -59.9163 | -16.2709 | -61.6824 | 57.8085 | 57.736 | 57.9148 | -65.2669 | -58.2035 | -17.4903 | -60.303 | 57.714 | 57.9101 | 57.7394 | -65.5359 | -0.15922 | -0.029949 | 5.1914 | 3.4253 | 3.5845 | -0.10242 | 0.076333 | -0.4282 | -0.12441 | 6.9042 | 4.8047 | 5.2329 | 0.071695 | -0.09909 | 122.9162 | 122.8437 | 123.0225 | 48.8368 | -123.1054 | 122.8218 | 123.0179 | 122.8471 | 47.6174 | -123.3744
1365.7969 | 123.1705 | -65.1306 | 57.8384 | -0.013431 | -0.007767 | 0.0021026 | 0.056652 | -0.00034394 | 0.065787 | 0.0058755 | 0.0051637 | 0.003457 | 0.059093 | 0.022763 | 0.063773 | -59.8797 | -16.2984 | -61.6458 | 57.8085 | 57.7406 | 57.9148 | -65.2578 | -58.1394 | -17.4903 | -60.2572 | 57.7232 | 57.9101 | 57.7714 | -65.5222 | -0.12717 | -0.029949 | 5.2509 | 3.4848 | 3.612 | -0.097843 | 0.076333 | -0.39157 | -0.11526 | 6.9912 | 4.8734 | 5.265 | 0.071695 | -0.06704 | 122.9391 | 122.8712 | 123.0454 | 48.8322 | -123.0962 | 122.8538 | 123.0408 | 122.902 | 47.6403 | -123.3606
1366.7969 | 123.2162 | -65.1123 | 57.8522 | -0.0057996 | -0.0079808 | 0.0021026 | 0.056438 | -0.00077134 | 0.066001 | -0.001755 | 0.0051637 | 0.0036706 | 0.058879 | 0.022976 | 0.063773 | -59.8476 | -16.3076 | -61.6138 | 57.8085 | 57.736 | 57.9148 | -65.2624 | -58.0936 | -17.5361 | -60.2206 | 57.7232 | 57.9193 | 57.7622 | -65.5176 | -0.15006 | -0.043682 | 5.2647 | 3.4986 | 3.6486 | -0.11615 | 0.0626 | -0.4053 | -0.12899 | 7.0187 | 4.8917 | 5.297 | 0.06712 | -0.08993 | 122.9208 | 122.8483 | 123.0271 | 48.8047 | -123.1145 | 122.8355 | 123.0316 | 122.8745 | 47.5762 | -123.3698
1367.7969 | 123.1796 | -65.0894 | 57.8842 | 0.0094624 | -0.0079808 | 0.0018888 | 0.057079 | -0.00034394 | 0.065787 | -0.0093855 | 0.0051637 | 0.0038844 | 0.059307 | 0.022549 | 0.063773 | -59.8064 | -16.303 | -61.6 | 57.8131 | 57.7314 | 57.9331 | -65.244 | -58.0341 | -17.5727 | -60.1702 | 57.7323 | 57.9284 | 57.7989 | -65.513 | -0.15463 | -0.071147 | 5.283 | 3.4894 | 3.644 | -0.15278 | 0.048871 | -0.42361 | -0.15188 | 7.0553 | 4.9192 | 5.3428 | 0.044234 | -0.085344 | 122.9025 | 122.8209 | 123.0225 | 48.7864 | -123.1283 | 122.8218 | 123.0179 | 122.8883 | 47.5167 | -123.3972
1368.7969 | 123.2529 | -65.0803 | 57.8659 | 0.0018314 | -0.0079808 | 0.0021026 | 0.057079 | -0.00055774 | 0.065573 | -0.0093855 | 0.0053773 | 0.0036706 | 0.059734 | 0.02319 | 0.064201 | -59.7835 | -16.3259 | -61.5725 | 57.8268 | 57.7543 | 57.9285 | -65.2578 | -57.9837 | -17.6185 | -60.1336 | 57.7323 | 57.9239 | 57.7394 | -65.513 | -0.17752 | -0.039102 | 5.2967 | 3.5077 | 3.6852 | -0.11157 | 0.062602 | -0.43277 | -0.13357 | 7.0965 | 4.9467 | 5.3794 | 0.057965 | -0.12656 | 122.9071 | 122.8346 | 123.0088 | 48.7544 | -123.1237 | 122.8126 | 123.0041 | 122.8196 | 47.4617 | -123.3789
1369.7969 | 123.2208 | -65.094 | 57.8751 | 0.0094624 | -0.0079808 | 0.0021026 | 0.056652 | -0.00013034 | 0.065787 | -0.001755 | 0.0051637 | 0.0038844 | 0.05952 | 0.022976 | 0.063987 | -59.7378 | -16.3579 | -61.5497 | 57.8222 | 57.7498 | 57.9422 | -65.244 | -57.9151 | -17.6048 | -60.0878 | 57.7323 | 57.9284 | 57.7897 | -65.5084 | -0.15005 | -0.052835 | 5.3562 | 3.5443 | 3.6944 | -0.12531 | 0.067183 | -0.41446 | -0.14272 | 7.1789 | 5.0062 | 5.4206 | 0.053389 | -0.085347 | 122.9162 | 122.8437 | 123.0362 | 48.7361 | -123.1191 | 122.8263 | 123.0224 | 122.8837 | 47.4892 | -123.3835
1370.7969 | 123.23 | -65.0894 | 57.8705 | 0.017093 | -0.0079808 | 0.0021026 | 0.057079 | -0.00034394 | 0.066001 | -0.0093855 | 0.0051637 | 0.0036706 | 0.059307 | 0.022549 | 0.063773 | -59.7103 | -16.3717 | -61.513 | 57.836 | 57.7314 | 57.9422 | -65.2395 | -57.8738 | -17.6323 | -60.0374 | 57.7461 | 57.9422 | 57.7348 | -65.4993 | -0.15005 | -0.034522 | 5.3791 | 3.5764 | 3.7264 | -0.13904 | 0.071761 | -0.40987 | -0.12441 | 7.2156 | 5.052 | 5.4618 | 0.071703 | -0.13571 | 122.9254 | 122.8209 | 123.0317 | 48.7177 | -123.11 | 122.8355 | 123.0316 | 122.8242 | 47.4572 | -123.3698
1371.7969 | 123.1934 | -65.0757 | 57.8613 | -0.0057996 | -0.0079808 | 0.0018888 | 0.057079 | -0.00034394 | 0.066214 | -0.001755 | 0.0053773 | 0.0036706 | 0.059307 | 0.022976 | 0.064414 | -59.6737 | -16.3808 | -61.4947 | 57.836 | 57.7498 | 57.9377 | -65.2303 | -57.8143 | -17.6735 | -60.0054 | 57.7507 | 57.9422 | 57.7577 | -65.4901 | -0.15463 | -0.025367 | 5.402 | 3.581 | 3.7356 | -0.11157 | 0.076338 | -0.41445 | -0.11067 | 7.2614 | 5.0703 | 5.4847 | 0.080858 | -0.10366 | 122.9116 | 122.8254 | 123.0134 | 48.6949 | -123.0916 | 122.8263 | 123.0179 | 122.8333 | 47.4022 | -123.3515
1372.7969 | 123.2208 | -65.0757 | 57.8979 | 0.0018314 | -0.0079808 | 0.0021026 | 0.056865 | -0.00034394 | 0.065787 | -0.001755 | 0.0055909 | 0.003457 | 0.059734 | 0.022976 | 0.064201 | -59.6416 | -16.39 | -61.4627 | 57.836 | 57.7635 | 57.9422 | -65.2349 | -57.7548 | -17.6964 | -59.9733 | 57.7507 | 57.9422 | 57.776 | -65.4993 | -0.15921 | -0.061988 | 5.4341 | 3.613 | 3.7722 | -0.13446 | 0.044295 | -0.42361 | -0.14729 | 7.3209 | 5.1023 | 5.5259 | 0.044237 | -0.12197 | 122.9116 | 122.8392 | 123.0179 | 48.6857 | -123.1328 | 122.8263 | 123.0179 | 122.8517 | 47.3793 | -123.3972
1373.7969 | 123.2254 | -65.0528 | 57.8567 | 0.0018314 | -0.0079808 | 0.0021026 | 0.056865 | -0.00034394 | 0.066001 | -0.001755 | 0.0053773 | 0.0038844 | 0.059307 | 0.022549 | 0.064201 | -59.6096 | -16.39 | -61.426 | 57.836 | 57.7589 | 57.956 | -65.2257 | -57.7044 | -17.7101 | -59.9092 | 57.7644 | 57.9468 | 57.7714 | -65.4901 | -0.17294 | -0.020789 | 5.4432 | 3.6268 | 3.7997 | -0.097837 | 0.09923 | -0.43734 | -0.09236 | 7.3484 | 5.1435 | 5.5809 | 0.090014 | -0.08535 | 122.8888 | 122.8117 | 123.0088 | 48.6628 | -123.0825 | 122.8172 | 122.9996 | 122.8242 | 47.3427 | -123.3469
1374.7969 | 123.1979 | -65.0482 | 57.9391 | 0.0018314 | -0.0079808 | 0.0018888 | 0.056865 | -0.00013034 | 0.065787 | 0.0058755 | 0.0053773 | 0.0038844 | 0.059307 | 0.022763 | 0.063773 | -59.5546 | -16.4175 | -61.3986 | 57.8543 | 57.7818 | 57.9697 | -65.2074 | -57.6403 | -17.7513 | -59.8589 | 57.769 | 57.9605 | 57.8034 | -65.4718 | -0.1592 | -0.084874 | 5.4936 | 3.6496 | 3.8088 | -0.15734 | 0.030568 | -0.4236 | -0.17018 | 7.4079 | 5.1893 | 5.6129 | 0.021352 | -0.1357 | 122.9025 | 122.83 | 123.0179 | 48.6308 | -123.1466 | 122.8172 | 123.0087 | 122.8517 | 47.2969 | -123.411
1375.7969 | 123.2346 | -65.0299 | 57.9071 | 0.0018314 | -0.007767 | 0.0021026 | 0.057293 | -0.00055774 | 0.066001 | -0.0093855 | 0.0053773 | 0.004098 | 0.05952 | 0.022976 | 0.064201 | -59.5317 | -16.4449 | -61.3757 | 57.8589 | 57.7726 | 57.9697 | -65.2074 | -57.59 | -17.7788 | -59.8085 | 57.7735 | 57.9605 | 57.8218 | -65.4718 | -0.17751 | -0.048251 | 5.4982 | 3.6542 | 3.8317 | -0.13445 | 0.062612 | -0.44191 | -0.13356 | 7.4399 | 5.2214 | 5.6633 | 0.053396 | -0.085339 | 122.8888 | 122.8026 | 122.9996 | 48.585 | -123.1145 | 122.8035 | 122.9904 | 122.8517 | 47.2511 | -123.3789
1376.7969 | 123.1659 | -65.0208 | 57.9437 | -0.0057996 | -0.0073396 | 0.0023162 | 0.056865 | -0.00034394 | 0.066001 | -0.001755 | 0.0053773 | 0.004098 | 0.059734 | 0.02319 | 0.064201 | -59.4859 | -16.477 | -61.3482 | 57.868 | 57.7864 | 57.9697 | -65.2028 | -57.5304 | -17.7925 | -59.7536 | 57.7735 | 57.9742 | 57.8355 | -65.4581 | -0.18209 | -0.075716 | 5.5348 | 3.6725 | 3.8546 | -0.15734 | 0.02599 | -0.43733 | -0.17018 | 7.4903 | 5.2672 | 5.7045 | 0.03051 | -0.10823 | 122.8888 | 122.8071 | 122.9905 | 48.5438 | -123.1466 | 122.7943 | 122.995 | 122.8563 | 47.2282 | -123.4018
1377.7969 | 123.2208 | -65.0528 | 57.9163 | 0.0094624 | -0.007767 | 0.0016752 | 0.057293 | -0.00013034 | 0.065787 | 0.0058755 | 0.0053773 | 0.0038844 | 0.05952 | 0.02319 | 0.064414 | -59.4539 | -16.477 | -61.3299 | 57.868 | 57.791 | 57.9926 | -65.1983 | -57.4755 | -17.82 | -59.7169 | 57.7827 | 57.9742 | 57.7851 | -65.4672 | -0.14546 | -0.04825 | 5.5989 | 3.7229 | 3.8684 | -0.12529 | 0.076349 | -0.41445 | -0.13356 | 7.5773 | 5.3359 | 5.7503 | 0.057976 | -0.13112 | 122.9208 | 122.8438 | 123.0454 | 48.5758 | -123.1145 | 122.8355 | 123.027 | 122.8379 | 47.2328 | -123.3835
1378.7969 | 123.1613 | -65.0345 | 57.9346 | 0.0018314 | -0.0079808 | 0.0023162 | 0.056865 | -0.00034394 | 0.066214 | -0.001755 | 0.0055909 | 0.004098 | 0.059307 | 0.023404 | 0.064201 | -59.4127 | -16.4907 | -61.2933 | 57.8817 | 57.8047 | 57.9926 | -65.1937 | -57.4068 | -17.8612 | -59.6666 | 57.7964 | 57.988 | 57.7851 | -65.4535 | -0.15919 | -0.052825 | 5.6218 | 3.7412 | 3.9004 | -0.12987 | 0.058039 | -0.41902 | -0.13813 | 7.6277 | 5.3679 | 5.7869 | 0.053402 | -0.14943 | 122.9162 | 122.8392 | 123.0271 | 48.5438 | -123.1283 | 122.8309 | 123.0225 | 122.8196 | 47.1733 | -123.3881
1379.7969 | 123.2208 | -65.0024 | 57.8979 | 0.0094624 | -0.007767 | 0.0021026 | 0.057079 | -0.00055774 | 0.066428 | -0.001755 | 0.0055909 | 0.004098 | 0.05952 | 0.022976 | 0.064628 | -59.3715 | -16.4907 | -61.2521 | 57.8909 | 57.8047 | 58.0018 | -65.1708 | -57.3473 | -17.8612 | -59.6116 | 57.801 | 57.9926 | 57.8309 | -65.4352 | -0.16834 | -0.007047 | 5.631 | 3.7504 | 3.9187 | -0.093247 | 0.10382 | -0.43275 | -0.096931 | 7.6551 | 5.3908 | 5.8236 | 0.094601 | -0.067027 | 122.8933 | 122.8071 | 123.0042 | 48.5117 | -123.0687 | 122.8035 | 122.995 | 122.8334 | 47.1413 | -123.3331
1380.7969 | 123.1476 | -65.0208 | 58.0353 | -0.013431 | -0.007767 | 0.0021026 | 0.056652 | -0.00055774 | 0.066428 | -0.001755 | 0.0060183 | 0.0036706 | 0.05952 | 0.022976 | 0.064414 | -59.3211 | -16.5365 | -61.2154 | 57.9092 | 57.8322 | 58.0109 | -65.1708 | -57.2878 | -17.8749 | -59.5567 | 57.8148 | 58.0154 | 57.8721 | -65.426 | -0.15003 | -0.12606 | 5.6996 | 3.8053 | 3.9553 | -0.2031 | -0.024355 | -0.40528 | -0.22052 | 7.733 | 5.4641 | 5.8693 | -0.019835 | -0.16315 | 122.93 | 122.8529 | 123.0317 | 48.4842 | -123.2061 | 122.8355 | 123.0362 | 122.8929 | 47.1458 | -123.4613
1381.7969 | 123.2437 | -64.9841 | 57.962 | 0.0018314 | -0.007767 | 0.0021026 | 0.056438 | -0.00034394 | 0.066001 | -0.001755 | 0.0060183 | 0.0036706 | 0.05952 | 0.023404 | 0.064841 | -59.2845 | -16.5457 | -61.1742 | 57.923 | 57.8322 | 58.0247 | -65.157 | -57.2145 | -17.8703 | -59.5017 | 57.8331 | 58.0292 | 57.8172 | -65.4031 | -0.17292 | -0.039086 | 5.6996 | 3.8099 | 3.9828 | -0.12986 | 0.062623 | -0.419 | -0.12897 | 7.7696 | 5.4824 | 5.9014 | 0.067143 | -0.14485 | 122.9071 | 122.8163 | 123.0088 | 48.4385 | -123.1191 | 122.8172 | 123.0133 | 122.8013 | 47.1138 | -123.3652
1382.7969 | 122.9736 | -64.9841 | 58.0124 | 0.0018314 | -0.0079808 | 0.0021026 | 0.056438 | -0.00013034 | 0.066214 | 0.0058755 | 0.0055909 | 0.0038844 | 0.059307 | 0.02319 | 0.064414 | -59.2433 | -16.5731 | -61.1422 | 57.9184 | 57.8505 | 58.0338 | -65.1479 | -57.155 | -17.8932 | -59.4376 | 57.8285 | 58.0246 | 57.8904 | -65.4031 | -0.16376 | -0.094018 | 5.7408 | 3.8419 | 4.0057 | -0.1619 | 0.021426 | -0.419 | -0.1839 | 7.8291 | 5.5465 | 5.9655 | 0.01221 | -0.12195 | 122.9025 | 122.8346 | 123.0179 | 48.411 | -123.1603 | 122.8126 | 123.0087 | 122.8746 | 47.0909 | -123.4155
1383.7969 | 123.2483 | -64.9521 | 57.9758 | 0.0018314 | -0.0075534 | 0.0021026 | 0.057079 | -0.00034394 | 0.066428 | 0.0058755 | 0.0055909 | 0.0038844 | 0.05952 | 0.023617 | 0.065055 | -59.2021 | -16.6052 | -61.101 | 57.9367 | 57.8596 | 58.043 | -65.1342 | -57.0817 | -17.907 | -59.3827 | 57.8514 | 58.0383 | 57.8676 | -65.394 | -0.18207 | -0.039084 | 5.75 | 3.8511 | 4.0332 | -0.11612 | 0.067204 | -0.44189 | -0.12439 | 7.8704 | 5.5694 | 6.0113 | 0.062567 | -0.10822 | 122.8888 | 122.8117 | 122.9951 | 48.3469 | -123.1099 | 122.8035 | 122.9904 | 122.8196 | 47.0451 | -123.3697
1384.7969 | 123.1613 | -64.9475 | 58.0399 | -0.0057996 | -0.0075534 | 0.0018888 | 0.057079 | -0.00013034 | 0.066428 | 0.013506 | 0.0058047 | 0.0036706 | 0.05952 | 0.023617 | 0.064414 | -59.1517 | -16.6281 | -61.0552 | 57.9596 | 57.8963 | 58.0567 | -65.125 | -57.0222 | -17.9161 | -59.3278 | 57.8651 | 58.0521 | 57.895 | -65.3711 | -0.17749 | -0.080279 | 5.7958 | 3.8923 | 4.0698 | -0.14357 | 0.016853 | -0.42357 | -0.17474 | 7.9253 | 5.6198 | 6.0433 | 0.012216 | -0.14483 | 122.9071 | 122.8438 | 123.0042 | 48.3194 | -123.1649 | 122.8126 | 122.9996 | 122.8425 | 47.0314 | -123.4109
1385.7969 | 123.2162 | -64.9292 | 58.0124 | -0.0057996 | -0.007767 | 0.0023162 | 0.056865 | -0.00034394 | 0.066642 | -0.0093855 | 0.0058047 | 0.004098 | 0.059734 | 0.023617 | 0.064841 | -59.1014 | -16.6555 | -61.0094 | 57.9733 | 57.8734 | 58.075 | -65.0975 | -56.9215 | -17.907 | -59.2636 | 57.888 | 58.0795 | 57.8767 | -65.3619 | -0.16832 | -0.039077 | 5.8278 | 3.9198 | 4.0881 | -0.139 | 0.062634 | -0.43273 | -0.12438 | 8.0077 | 5.6656 | 6.0983 | 0.067154 | -0.13568 | 122.9025 | 122.8026 | 123.0042 | 48.2736 | -123.1099 | 122.8172 | 123.0087 | 122.8059 | 47.0222 | -123.3743
1386.7969 | 123.111 | -64.9658 | 58.0673 | -0.0057996 | -0.0073396 | 0.0023162 | 0.057079 | -0.00034394 | 0.066214 | 0.0058755 | 0.0060183 | 0.0038844 | 0.05952 | 0.023404 | 0.064628 | -59.0739 | -16.683 | -60.9819 | 57.9687 | 57.878 | 58.0842 | -65.0975 | -56.8986 | -17.9299 | -59.2133 | 57.8834 | 58.075 | 57.9225 | -65.3665 | -0.1317 | -0.098588 | 5.8919 | 3.9839 | 4.1156 | -0.18936 | 0.016859 | -0.40069 | -0.18389 | 8.0672 | 5.7525 | 6.1532 | 0.007643 | -0.14483 | 122.9346 | 122.8438 | 123.05 | 48.2828 | -123.1648 | 122.8493 | 123.0408 | 122.8883 | 47.036 | -123.4338
1387.7969 | 123.1201 | -64.9429 | 58.049 | 0.0018314 | -0.0075534 | 0.0023162 | 0.056865 | 8.3264e-05 | 0.066428 | 0.0058755 | 0.0060183 | 0.0038844 | 0.059734 | 0.02319 | 0.065269 | -59.0235 | -16.7105 | -60.9362 | 57.9962 | 57.9146 | 58.1025 | -65.07 | -56.8024 | -17.9253 | -59.14 | 57.9063 | 58.0979 | 57.9362 | -65.3345 | -0.12712 | -0.052807 | 5.9194 | 4.0068 | 4.1339 | -0.13441 | 0.053484 | -0.39152 | -0.14269 | 8.1405 | 5.8029 | 6.1944 | 0.048847 | -0.11278 | 122.9391 | 122.8575 | 123.0454 | 48.2324 | -123.1191 | 122.8493 | 123.0408 | 122.8792 | 47.0176 | -123.3835
1388.7969 | 123.111 | -64.9292 | 58.0536 | 0.0018314 | -0.0075534 | 0.0021026 | 0.056438 | -0.00034394 | 0.066642 | 0.0058755 | 0.0060183 | 0.004098 | 0.059307 | 0.023831 | 0.064628 | -58.9823 | -16.7517 | -60.8995 | 58.0054 | 57.9192 | 58.1071 | -65.07 | -56.7612 | -17.9619 | -59.0942 | 57.9201 | 58.107 | 57.9729 | -65.3299 | -0.14085 | -0.048228 | 5.9469 | 4.0297 | 4.1705 | -0.13441 | 0.053485 | -0.40068 | -0.13353 | 8.168 | 5.835 | 6.2356 | 0.053426 | -0.08073 | 122.9346 | 122.8484 | 123.0363 | 48.1775 | -123.1236 | 122.8493 | 123.0362 | 122.9021 | 46.9673 | -123.3835
1389.7969 | 123.1522 | -64.9109 | 58.0536 | 0.0018314 | -0.007767 | 0.00253 | 0.057079 | -0.00013034 | 0.066642 | -0.001755 | 0.0055909 | 0.0038844 | 0.05952 | 0.023831 | 0.064841 | -58.9503 | -16.7746 | -60.8629 | 58.0008 | 57.9329 | 58.1117 | -65.0655 | -56.688 | -17.9757 | -59.0439 | 57.9201 | 58.1116 | 57.9591 | -65.3253 | -0.15458 | -0.052806 | 5.9606 | 4.048 | 4.2026 | -0.12068 | 0.058063 | -0.41441 | -0.13353 | 8.2229 | 5.867 | 6.2814 | 0.058005 | -0.094466 | 122.9117 | 122.8438 | 123.0225 | 48.1363 | -123.1191 | 122.8309 | 123.0225 | 122.87 | 46.9352 | -123.3789
1390.7969 | 123.111 | -64.9246 | 58.0948 | 0.0018314 | -0.007767 | 0.0021026 | 0.056865 | 8.3264e-05 | 0.066214 | -0.001755 | 0.0055909 | 0.0038844 | 0.059734 | 0.023831 | 0.064841 | -58.8999 | -16.7975 | -60.8309 | 58.0145 | 57.9375 | 58.1345 | -65.0517 | -56.6422 | -17.994 | -58.9981 | 57.9292 | 58.1162 | 57.982 | -65.3161 | -0.12711 | -0.08027 | 6.0247 | 4.0938 | 4.2209 | -0.1573 | 0.039757 | -0.39152 | -0.16557 | 8.2824 | 5.9265 | 6.3181 | 0.021384 | -0.11277 | 122.9391 | 122.8621 | 123.0592 | 48.1271 | -123.1465 | 122.8538 | 123.0408 | 122.9066 | 46.9307 | -123.4109
1391.7969 | 123.2162 | -64.8743 | 58.0811 | 0.0094624 | -0.007767 | 0.0023162 | 0.056865 | 8.3264e-05 | 0.066428 | -0.001755 | 0.0060183 | 0.0036706 | 0.059734 | 0.023617 | 0.065055 | -58.8679 | -16.8204 | -60.7942 | 58.0237 | 57.9604 | 58.1391 | -65.0426 | -56.5643 | -18.0031 | -58.9386 | 57.943 | 58.1299 | 57.9912 | -65.307 | -0.16831 | -0.05738 | 6.0064 | 4.08 | 4.2483 | -0.12067 | 0.058069 | -0.43271 | -0.1381 | 8.3099 | 5.9357 | 6.3684 | 0.048853 | -0.089882 | 122.8979 | 122.8347 | 123.0134 | 48.0539 | -123.1236 | 122.8172 | 123.0042 | 122.8654 | 46.8711 | -123.388
1392.7969 | 123.1201 | -64.8834 | 58.1223 | -0.0057996 | -0.007126 | 0.0018888 | 0.056438 | 8.3264e-05 | 0.066642 | 0.0058755 | 0.0062319 | 0.004098 | 0.059734 | 0.024045 | 0.065269 | -58.8267 | -16.857 | -60.753 | 58.042 | 57.965 | 58.1437 | -65.038 | -56.5002 | -18.0535 | -58.879 | 57.9475 | 58.1391 | 58.0003 | -65.2978 | -0.15457 | -0.080265 | 6.0568 | 4.1304 | 4.285 | -0.15729 | 0.02145 | -0.4144 | -0.17472 | 8.3832 | 6.0044 | 6.4188 | 0.016812 | -0.12192 | 122.9254 | 122.8484 | 123.0271 | 48.0264 | -123.1603 | 122.831 | 123.0225 | 122.8838 | 46.8299 | -123.4201
1393.7969 | 123.1476 | -64.8514 | 58.1131 | 0.0094624 | -0.0073396 | 0.0023162 | 0.056865 | 8.3264e-05 | 0.066428 | 0.0058755 | 0.0062319 | 0.0038844 | 0.05952 | 0.023831 | 0.065269 | -58.7855 | -16.8753 | -60.7164 | 58.0466 | 57.9695 | 58.1437 | -65.0243 | -56.4041 | -18.0764 | -58.8287 | 57.9567 | 58.1391 | 58.0003 | -65.2932 | -0.17288 | -0.066531 | 6.0659 | 4.135 | 4.3079 | -0.14355 | 0.030605 | -0.44187 | -0.15641 | 8.4473 | 6.0227 | 6.4646 | 0.025967 | -0.11277 | 122.8979 | 122.8209 | 122.9951 | 47.9761 | -123.1374 | 122.8081 | 122.9904 | 122.8517 | 46.775 | -123.4063
1394.7969 | 123.1567 | -64.8697 | 58.1131 | 0.0018314 | -0.0075534 | 0.0021026 | 0.057079 | -0.00013034 | 0.066642 | -0.001755 | 0.0060183 | 0.0045252 | 0.059734 | 0.024045 | 0.065269 | -58.7305 | -16.912 | -60.6752 | 58.0603 | 57.9833 | 58.1712 | -65.0197 | -56.3491 | -18.1084 | -58.7508 | 57.9613 | 58.1574 | 57.9866 | -65.2703 | -0.14999 | -0.052796 | 6.1392 | 4.1945 | 4.3445 | -0.12982 | 0.058076 | -0.40066 | -0.15183 | 8.5206 | 6.1189 | 6.5195 | 0.044282 | -0.1265 | 122.93 | 122.853 | 123.0409 | 47.9577 | -123.1328 | 122.831 | 123.0271 | 122.8563 | 46.7613 | -123.3834
1395.7969 | 123.111 | -64.9063 | 58.1131 | 0.0094624 | -0.0075534 | 0.0023162 | 0.057293 | -0.00034394 | 0.066855 | -0.001755 | 0.0064455 | 0.0038844 | 0.059734 | 0.024045 | 0.065269 | -58.703 | -16.9532 | -60.6432 | 58.0557 | 57.9787 | 58.1666 | -65.0151 | -56.2988 | -18.1313 | -58.705 | 57.9658 | 58.1528 | 58.0095 | -65.2749 | -0.10879 | -0.057375 | 6.2033 | 4.2632 | 4.3719 | -0.1344 | 0.053498 | -0.36862 | -0.14725 | 8.6075 | 6.2013 | 6.5699 | 0.039703 | -0.10361 | 122.962 | 122.885 | 123.0729 | 47.9532 | -123.1282 | 122.8722 | 123.0591 | 122.9158 | 46.775 | -123.388
1396.7969 | 123.1613 | -64.8788 | 58.0765 | -0.0057996 | -0.0079808 | 0.0021026 | 0.056652 | -0.00013034 | 0.066642 | 0.0058755 | 0.0062319 | 0.004098 | 0.05952 | 0.024045 | 0.065696 | -58.6801 | -17.0081 | -60.6248 | 58.0466 | 57.9741 | 58.1574 | -65.0197 | -56.2667 | -18.1909 | -58.673 | 57.9613 | 58.1436 | 57.9683 | -65.2841 | -0.14084 | -0.02991 | 6.1987 | 4.254 | 4.3948 | -0.10235 | 0.080961 | -0.40524 | -0.11521 | 8.6121 | 6.2058 | 6.6111 | 0.067167 | -0.1082 | 122.9254 | 122.853 | 123.0363 | 47.8707 | -123.0962 | 122.8401 | 123.0225 | 122.8471 | 46.688 | -123.3606
1397.7969 | 123.1155 | -64.8697 | 58.1406 | -0.0057996 | -0.0073396 | 0.0023162 | 0.056652 | 0.00029706 | 0.066642 | -0.001755 | 0.0062319 | 0.004098 | 0.05952 | 0.023831 | 0.065055 | -58.6298 | -17.031 | -60.5791 | 58.0649 | 57.9833 | 58.1758 | -65.0059 | -56.198 | -18.1909 | -58.6043 | 57.9704 | 58.162 | 57.9729 | -65.2703 | -0.13625 | -0.075684 | 6.2399 | 4.2906 | 4.4269 | -0.15728 | 0.035189 | -0.40066 | -0.17014 | 8.6717 | 6.2654 | 6.666 | 0.021394 | -0.1677 | 122.9346 | 122.853 | 123.0454 | 47.8387 | -123.1465 | 122.8401 | 123.0316 | 122.8425 | 46.6788 | -123.4109
1398.7969 | 123.1338 | -64.8651 | 58.1406 | -0.0057996 | -0.0073396 | 0.00253 | 0.056652 | -0.00013034 | 0.066428 | 0.0058755 | 0.0064455 | 0.0043116 | 0.060161 | 0.024045 | 0.065269 | -58.5748 | -17.0356 | -60.5241 | 58.0878 | 58.0153 | 58.1941 | -64.983 | -56.1248 | -18.2092 | -58.5173 | 57.9933 | 58.1849 | 58.069 | -65.2475 | -0.11794 | -0.052792 | 6.2903 | 4.341 | 4.4589 | -0.12523 | 0.053503 | -0.38234 | -0.14725 | 8.7403 | 6.3478 | 6.7301 | 0.044287 | -0.071555 | 122.9529 | 122.8804 | 123.0592 | 47.8295 | -123.1236 | 122.8584 | 123.05 | 122.9341 | 46.6559 | -123.388
1399.7969 | 123.1064 | -64.8605 | 58.136 | -0.0057996 | -0.0073396 | 0.0023162 | 0.056652 | 8.3264e-05 | 0.066642 | 0.0058755 | 0.0062319 | 0.0043116 | 0.059734 | 0.024258 | 0.065696 | -58.5565 | -17.0768 | -60.4967 | 58.074 | 58.0016 | 58.1849 | -64.9922 | -56.0653 | -18.2275 | -58.4807 | 57.9933 | 58.1757 | 58.0324 | -65.252 | -0.13167 | -0.061949 | 6.304 | 4.3639 | 4.4956 | -0.13439 | 0.048924 | -0.3915 | -0.14267 | 8.7953 | 6.3798 | 6.7713 | 0.039708 | -0.10361 | 122.9346 | 122.8621 | 123.0454 | 47.7838 | -123.1282 | 122.8538 | 123.0362 | 122.8929 | 46.633 | -123.388
1400.7969 | 123.1384 | -64.8331 | 58.1726 | 0.0094624 | -0.0069124 | 0.0023162 | 0.057079 | 8.3264e-05 | 0.066642 | -0.001755 | 0.0064455 | 0.0043116 | 0.059734 | 0.024258 | 0.065482 | -58.5016 | -17.1043 | -60.4509 | 58.1015 | 58.0153 | 58.2078 | -64.9739 | -55.9966 | -18.2458 | -58.4029 | 58.0071 | 58.1986 | 58.0736 | -65.2337 | -0.14082 | -0.0711 | 6.3315 | 4.3822 | 4.523 | -0.15727 | 0.035196 | -0.40065 | -0.16556 | 8.8365 | 6.4302 | 6.8309 | 0.02598 | -0.099019 | 122.9346 | 122.8484 | 123.0409 | 47.7288 | -123.1465 | 122.8401 | 123.0317 | 122.9067 | 46.5873 | -123.4063
1401.7969 | 123.1476 | -64.8239 | 58.1543 | 0.017093 | -0.007126 | 0.00253 | 0.056865 | 8.3264e-05 | 0.067069 | 0.013506 | 0.0068727 | 0.004098 | 0.059734 | 0.024472 | 0.065269 | -58.4467 | -17.1455 | -60.4051 | 58.1152 | 58.0291 | 58.2215 | -64.9602 | -55.9142 | -18.2275 | -58.3342 | 58.0208 | 58.2077 | 58.0324 | -65.22 | -0.13624 | -0.039054 | 6.3773 | 4.4188 | 4.5551 | -0.12523 | 0.067242 | -0.39607 | -0.13351 | 8.9098 | 6.4897 | 6.8858 | 0.053448 | -0.12192 | 122.9392 | 122.853 | 123.0455 | 47.6785 | -123.1145 | 122.8447 | 123.0317 | 122.8563 | 46.5964 | -123.3743
1402.7969 | 123.111 | -64.8239 | 58.1726 | 0.0018314 | -0.007126 | 0.0023162 | 0.057293 | -0.00013034 | 0.066855 | 0.0058755 | 0.0064455 | 0.004098 | 0.05952 | 0.024899 | 0.065696 | -58.3917 | -17.2004 | -60.3685 | 58.1198 | 58.0245 | 58.2353 | -64.951 | -55.8501 | -18.2504 | -58.2838 | 58.0299 | 58.2215 | 58.0232 | -65.2154 | -0.12708 | -0.052786 | 6.4322 | 4.4555 | 4.5825 | -0.14812 | 0.062668 | -0.39149 | -0.14266 | 8.9739 | 6.5401 | 6.9316 | 0.048873 | -0.14938 | 122.9437 | 122.8484 | 123.0592 | 47.6235 | -123.1236 | 122.8539 | 123.0454 | 122.8471 | 46.5735 | -123.388
1403.7969 | 123.1247 | -64.8331 | 58.1635 | 0.0094624 | -0.0069124 | 0.0027436 | 0.056865 | 8.3264e-05 | 0.066642 | -0.001755 | 0.0066591 | 0.004098 | 0.059947 | 0.024472 | 0.065696 | -58.3505 | -17.2462 | -60.3318 | 58.129 | 58.0336 | 58.2307 | -64.9556 | -55.786 | -18.2733 | -58.2243 | 58.0254 | 58.2215 | 58.0873 | -65.2017 | -0.12251 | -0.034474 | 6.4826 | 4.5012 | 4.6237 | -0.1298 | 0.067244 | -0.3686 | -0.13809 | 9.0471 | 6.6088 | 6.9774 | 0.058028 | -0.076128 | 122.962 | 122.8667 | 123.0638 | 47.5869 | -123.119 | 122.8584 | 123.0545 | 122.9204 | 46.5598 | -123.3651
1404.7969 | 123.1522 | -64.7873 | 58.2184 | -0.013431 | -0.0073396 | 0.0027436 | 0.057079 | 0.00029706 | 0.066855 | -0.001755 | 0.0066591 | 0.0043116 | 0.059947 | 0.024472 | 0.06591 | -58.2773 | -17.2691 | -60.254 | 58.1748 | 58.0794 | 58.2765 | -64.9098 | -55.6852 | -18.2458 | -58.119 | 58.0712 | 58.2718 | 58.1011 | -65.1696 | -0.1225 | -0.043622 | 6.51 | 4.5333 | 4.6558 | -0.13895 | 0.058098 | -0.38232 | -0.14723 | 9.1021 | 6.6683 | 7.0506 | 0.053461 | -0.11733 | 122.9621 | 122.8667 | 123.0638 | 47.5182 | -123.1282 | 122.8584 | 123.0591 | 122.8884 | 46.5415 | -123.388
1405.7969 | 123.1796 | -64.7736 | 58.2458 | -0.0057996 | -0.0069124 | 0.00253 | 0.056865 | 8.3264e-05 | 0.066855 | 0.0058755 | 0.0066591 | 0.0045252 | 0.060161 | 0.024258 | 0.065482 | -58.2315 | -17.292 | -60.2128 | 58.1748 | 58.084 | 58.2765 | -64.9006 | -55.6165 | -18.255 | -58.0457 | 58.0849 | 58.2718 | 58.0415 | -65.1605 | -0.12707 | -0.071088 | 6.5421 | 4.5608 | 4.6878 | -0.16183 | 0.030632 | -0.3869 | -0.16096 | 9.157 | 6.7278 | 7.1147 | 0.025995 | -0.20431 | 122.9483 | 122.8576 | 123.05 | 47.4816 | -123.1465 | 122.8584 | 123.0454 | 122.8151 | 46.5186 | -123.4063
1406.7969 | 123.0835 | -64.7873 | 58.2138 | -0.0057996 | -0.007126 | 0.00253 | 0.057079 | 0.00051066 | 0.067069 | 0.013506 | 0.0068727 | 0.0038844 | 0.059947 | 0.024686 | 0.06591 | -58.1948 | -17.324 | -60.1716 | 58.1793 | 58.0886 | 58.2856 | -64.8869 | -55.5479 | -18.2779 | -57.9816 | 58.094 | 58.2764 | 58.0141 | -65.1513 | -0.0996 | -0.034466 | 6.5925 | 4.6157 | 4.7153 | -0.12521 | 0.071833 | -0.36401 | -0.11976 | 9.2394 | 6.8057 | 7.1697 | 0.062618 | -0.19974 | 122.9666 | 122.8759 | 123.0729 | 47.4633 | -123.1007 | 122.8813 | 123.0637 | 122.8014 | 46.5094 | -123.3651
1407.7969 | 123.1384 | -64.7324 | 58.2642 | 0.0094624 | -0.0075534 | 0.0027436 | 0.057079 | 0.00029706 | 0.066855 | -0.001755 | 0.0070865 | 0.004739 | 0.059734 | 0.024472 | 0.065696 | -58.1491 | -17.3744 | -60.1395 | 58.1885 | 58.0886 | 58.2948 | -64.8869 | -55.4929 | -18.2962 | -57.9129 | 58.094 | 58.2856 | 58.124 | -65.1513 | -0.15453 | -0.075663 | 6.5833 | 4.5928 | 4.7473 | -0.17556 | 0.030637 | -0.41894 | -0.17012 | 9.2394 | 6.8194 | 7.2384 | 0.021421 | -0.14021 | 122.9209 | 122.821 | 123.0272 | 47.358 | -123.1511 | 122.8264 | 123.0179 | 122.8563 | 46.4362 | -123.4155
1408.7969 | 123.0743 | -64.7827 | 58.2275 | 0.0018314 | -0.007126 | 0.0021026 | 0.057079 | 0.00029706 | 0.067283 | -0.0093855 | 0.0070865 | 0.0045252 | 0.059947 | 0.024686 | 0.06591 | -58.1033 | -17.4293 | -60.0846 | 58.1977 | 58.1023 | 58.304 | -64.8686 | -55.4288 | -18.2962 | -57.8671 | 58.1078 | 58.2947 | 58.0873 | -65.133 | -0.085861 | -0.029885 | 6.6794 | 4.6981 | 4.784 | -0.12521 | 0.076415 | -0.35027 | -0.11976 | 9.3539 | 6.9156 | 7.2658 | 0.067199 | -0.14021 | 122.9804 | 122.885 | 123.0867 | 47.3534 | -123.0961 | 122.8905 | 123.0775 | 122.87 | 46.4865 | -123.3605
1409.7969 | 123.1338 | -64.7461 | 58.2413 | 0.0018314 | -0.0069124 | 0.0023162 | 0.057079 | 0.00051066 | 0.066855 | -0.001755 | 0.0068727 | 0.0043116 | 0.060161 | 0.024472 | 0.06591 | -58.0529 | -17.4614 | -60.0434 | 58.2114 | 58.1161 | 58.3223 | -64.864 | -55.3601 | -18.2962 | -57.7893 | 58.1169 | 58.3085 | 58.1194 | -65.1192 | -0.1179 | -0.029883 | 6.6932 | 4.7027 | 4.8206 | -0.1252 | 0.080996 | -0.37315 | -0.12434 | 9.386 | 6.9568 | 7.3299 | 0.067202 | -0.1219 | 122.9575 | 122.8622 | 123.0684 | 47.2847 | -123.1053 | 122.863 | 123.0546 | 122.8655 | 46.4499 | -123.3605
1410.7969 | 123.0652 | -64.7507 | 58.2458 | 0.0094624 | -0.007126 | 0.0023162 | 0.057079 | 0.00029706 | 0.066855 | 0.013506 | 0.0068727 | 0.0043116 | 0.060161 | 0.024472 | 0.066123 | -58.0025 | -17.4934 | -59.9976 | 58.216 | 58.1206 | 58.3314 | -64.8594 | -55.3006 | -18.3145 | -57.7573 | 58.1215 | 58.3176 | 58.1652 | -65.1238 | -0.10875 | -0.029883 | 6.7481 | 4.7531 | 4.8618 | -0.1252 | 0.085575 | -0.37316 | -0.12434 | 9.4501 | 6.9934 | 7.3666 | 0.071781 | -0.08069 | 122.9666 | 122.8713 | 123.0821 | 47.2572 | -123.1053 | 122.8722 | 123.0683 | 122.9158 | 46.4362 | -123.3697
1411.7969 | 123.1384 | -64.7278 | 58.2779 | -0.0057996 | -0.007126 | 0.0023162 | 0.057293 | 8.3264e-05 | 0.067283 | 0.0058755 | 0.0073001 | 0.004739 | 0.059947 | 0.024899 | 0.066123 | -57.9659 | -17.553 | -59.9747 | 58.2114 | 58.1206 | 58.3223 | -64.8594 | -55.264 | -18.3328 | -57.6977 | 58.1124 | 58.3131 | 58.1743 | -65.1192 | -0.13164 | -0.066504 | 6.7619 | 4.7531 | 4.8847 | -0.15724 | 0.044375 | -0.39147 | -0.16554 | 9.4638 | 7.0301 | 7.4215 | 0.035159 | -0.10358 | 122.9392 | 122.8484 | 123.0501 | 47.1748 | -123.1373 | 122.8401 | 123.0408 | 122.9021 | 46.395 | -123.3971
1412.7969 | 123.2025 | -64.6637 | 58.2458 | -0.0057996 | -0.0069124 | 0.00253 | 0.057506 | 0.00051066 | 0.067069 | -0.001755 | 0.0068727 | 0.0043116 | 0.060161 | 0.024686 | 0.06591 | -57.9247 | -17.5804 | -59.9244 | 58.2068 | 58.1435 | 58.3314 | -64.8503 | -55.1907 | -18.3282 | -57.6474 | 58.1352 | 58.3222 | 58.124 | -65.1192 | -0.18657 | -0.03904 | 6.739 | 4.7393 | 4.9259 | -0.10231 | 0.085575 | -0.45555 | -0.1106 | 9.473 | 7.0163 | 7.4719 | 0.07636 | -0.1219 | 122.8705 | 122.8072 | 122.9951 | 47.0833 | -123.0961 | 122.7989 | 122.9859 | 122.7876 | 46.3355 | -123.3651
1413.7969 | 123.1018 | -64.7049 | 58.3145 | -0.013431 | -0.007126 | 0.00253 | 0.057079 | 0.00029706 | 0.067496 | -0.0093855 | 0.0073001 | 0.0045252 | 0.060161 | 0.024899 | 0.066123 | -57.8515 | -17.5942 | -59.8694 | 58.2434 | 58.1664 | 58.3543 | -64.8319 | -55.1083 | -18.3145 | -57.5695 | 58.1398 | 58.3359 | 58.1972 | -65.1009 | -0.12705 | -0.071077 | 6.8534 | 4.8355 | 4.9625 | -0.14808 | 0.039804 | -0.39604 | -0.17469 | 9.5966 | 7.1354 | 7.5314 | 0.021431 | -0.1173 | 122.9483 | 122.8713 | 123.0592 | 47.1107 | -123.1465 | 122.8447 | 123.0408 | 122.9021 | 46.3904 | -123.4154
1414.7969 | 123.1522 | -64.7049 | 58.255 | -0.0057996 | -0.0073396 | 0.0027436 | 0.056865 | 0.00051066 | 0.066855 | -0.0093855 | 0.0073001 | 0.0045252 | 0.060161 | 0.024686 | 0.066551 | -57.8057 | -17.6354 | -59.8236 | 58.248 | 58.1619 | 58.3543 | -64.8182 | -55.035 | -18.3282 | -57.4871 | 58.1536 | 58.3497 | 58.1423 | -65.0918 | -0.11331 | -0.006989 | 6.8992 | 4.8812 | 4.9946 | -0.093146 | 0.099313 | -0.38688 | -0.10144 | 9.6698 | 7.2178 | 7.6047 | 0.094676 | -0.11274 | 122.9529 | 122.8668 | 123.0592 | 47.0695 | -123.0732 | 122.8585 | 123.0546 | 122.8472 | 46.3767 | -123.3468
1415.7969 | 123.0927 | -64.7186 | 58.2642 | 0.0018314 | -0.007126 | 0.00253 | 0.057079 | 0.00051066 | 0.067069 | -0.017016 | 0.0070865 | 0.004739 | 0.059947 | 0.024899 | 0.066764 | -57.7691 | -17.6903 | -59.787 | 58.2434 | 58.171 | 58.3589 | -64.8182 | -54.9755 | -18.3648 | -57.423 | 58.1581 | 58.3405 | 58.2064 | -65.0872 | -0.09958 | -0.020723 | 6.9496 | 4.9316 | 5.0312 | -0.093144 | 0.094737 | -0.36857 | -0.10602 | 9.7431 | 7.2956 | 7.6642 | 0.076364 | -0.057793 | 122.9621 | 122.8896 | 123.0775 | 47.0283 | -123.0824 | 122.8768 | 123.0592 | 122.925 | 46.3538 | -123.3514
1416.7969 | 123.1796 | -64.682 | 58.255 | 0.0018314 | -0.0073396 | 0.00253 | 0.057079 | 0.00051066 | 0.067283 | -0.001755 | 0.0073001 | 0.0045252 | 0.059947 | 0.024686 | 0.066337 | -57.7233 | -17.7453 | -59.7504 | 58.248 | 58.171 | 58.3589 | -64.8228 | -54.9068 | -18.3694 | -57.3864 | 58.1673 | 58.3543 | 58.2155 | -65.078 | -0.14078 | -0.006989 | 6.9587 | 4.9316 | 5.0724 | -0.083989 | 0.10389 | -0.39603 | -0.087707 | 9.7752 | 7.2956 | 7.6917 | 0.099255 | -0.039481 | 122.93 | 122.853 | 123.0409 | 46.9368 | -123.0778 | 122.8493 | 123.0363 | 122.8975 | 46.3126 | -123.333
1417.7969 | 123.2483 | -64.595 | 58.3237 | 0.0094624 | -0.0066986 | 0.00253 | 0.057506 | 0.00051066 | 0.067283 | -0.0093855 | 0.0070865 | 0.0045252 | 0.059947 | 0.024899 | 0.066337 | -57.6409 | -17.7453 | -59.6726 | 58.2938 | 58.2122 | 58.4093 | -64.7678 | -54.8198 | -18.4015 | -57.2856 | 58.2085 | 58.3955 | 58.2567 | -65.0414 | -0.17281 | -0.029869 | 6.9542 | 4.9225 | 5.0953 | -0.11144 | 0.085593 | -0.44638 | -0.11517 | 9.7752 | 7.3094 | 7.7558 | 0.071798 | -0.066937 | 122.8888 | 122.8073 | 123.0043 | 46.8498 | -123.0915 | 122.8035 | 122.9905 | 122.8518 | 46.1936 | -123.3651
1418.7969 | 123.1293 | -64.6683 | 58.3237 | -0.0057996 | -0.007126 | 0.0029572 | 0.056865 | 0.00072426 | 0.067496 | -0.001755 | 0.0073001 | 0.0045252 | 0.060161 | 0.025113 | 0.066551 | -57.5905 | -17.7773 | -59.6359 | 58.2984 | 58.2076 | 58.4093 | -64.7678 | -54.7557 | -18.4289 | -57.2399 | 58.2085 | 58.3955 | 58.2476 | -65.0368 | -0.099566 | -0.025291 | 7.0778 | 5.0323 | 5.1319 | -0.11602 | 0.085593 | -0.36856 | -0.11517 | 9.9125 | 7.4284 | 7.797 | 0.071798 | -0.076094 | 122.9667 | 122.8759 | 123.0775 | 46.891 | -123.0915 | 122.8768 | 123.0637 | 122.9158 | 46.2393 | -123.3605
1419.7969 | 123.0835 | -64.6362 | 58.3649 | -0.0057996 | -0.0069124 | 0.0027436 | 0.057079 | 0.00051066 | 0.067496 | 0.0058755 | 0.0075137 | 0.0049526 | 0.060161 | 0.025327 | 0.066764 | -57.531 | -17.8048 | -59.581 | 58.3121 | 58.2351 | 58.4276 | -64.7633 | -54.6779 | -18.4747 | -57.1574 | 58.2222 | 58.4229 | 58.1881 | -65.0231 | -0.12703 | -0.052755 | 7.1053 | 5.0552 | 5.1823 | -0.12975 | 0.062708 | -0.38686 | -0.14263 | 9.9583 | 7.4788 | 7.8657 | 0.058071 | -0.17682 | 122.9483 | 122.8714 | 123.0638 | 46.8315 | -123.1281 | 122.8585 | 123.0592 | 122.8243 | 46.1615 | -123.388
1420.7969 | 123.1934 | -64.6088 | 58.3008 | -0.0057996 | -0.0069124 | 0.00253 | 0.057506 | 0.00051066 | 0.067924 | -0.001755 | 0.0075137 | 0.0051662 | 0.060375 | 0.024899 | 0.066978 | -57.5035 | -17.8506 | -59.5444 | 58.3167 | 58.2214 | 58.423 | -64.7541 | -54.623 | -18.5068 | -57.1071 | 58.2268 | 58.4184 | 58.2338 | -65.0231 | -0.14534 | 0.015911 | 7.1053 | 5.0644 | 5.2097 | -0.079396 | 0.12222 | -0.41433 | -0.073963 | 9.9858 | 7.5017 | 7.916 | 0.11758 | -0.066942 | 122.9255 | 122.8302 | 123.0318 | 46.7582 | -123.0549 | 122.8356 | 123.0271 | 122.8426 | 46.102 | -123.3239
1421.7969 | 123.1293 | -64.6408 | 58.3694 | -0.013431 | -0.007126 | 0.00253 | 0.057293 | 0.00093806 | 0.067283 | -0.001755 | 0.0073001 | 0.004739 | 0.060375 | 0.025327 | 0.066551 | -57.4257 | -17.8826 | -59.4894 | 58.3213 | 58.2351 | 58.4505 | -64.7358 | -54.5589 | -18.4747 | -57.0292 | 58.2406 | 58.4367 | 58.1835 | -65.0048 | -0.09498 | -0.048176 | 7.2151 | 5.1514 | 5.2464 | -0.13433 | 0.081023 | -0.36397 | -0.12889 | 10.0819 | 7.6116 | 7.9755 | 0.067229 | -0.18597 | 122.9621 | 122.8759 | 123.0913 | 46.7582 | -123.1052 | 122.8814 | 123.0775 | 122.8243 | 46.1661 | -123.3742
1422.7969 | 123.2117 | -64.5584 | 58.3786 | 0.0094624 | -0.0066986 | 0.00253 | 0.05772 | 0.00072426 | 0.067496 | 0.0058755 | 0.0075137 | 0.0049526 | 0.060161 | 0.02554 | 0.066764 | -57.3936 | -17.9284 | -59.4711 | 58.3258 | 58.2397 | 58.4413 | -64.7404 | -54.5222 | -18.5205 | -56.988 | 58.236 | 58.4367 | 58.1743 | -65.0048 | -0.18195 | -0.052753 | 7.1648 | 5.0873 | 5.2692 | -0.1389 | 0.062711 | -0.44637 | -0.14263 | 10.0362 | 7.5704 | 8.0168 | 0.058074 | -0.20428 | 122.8843 | 122.7981 | 122.9997 | 46.63 | -123.119 | 122.7944 | 122.9951 | 122.7327 | 46.0379 | -123.3834
1423.7969 | 123.1567 | -64.6042 | 58.3649 | -0.021062 | -0.0066986 | 0.00253 | 0.057293 | 0.00072426 | 0.067496 | -0.0093855 | 0.0077273 | 0.004739 | 0.060588 | 0.025327 | 0.066551 | -57.3387 | -17.9696 | -59.407 | 58.335 | 58.2397 | 58.4459 | -64.7312 | -54.4535 | -18.5617 | -56.9606 | 58.2451 | 58.4458 | 58.2567 | -65.0002 | -0.12702 | -0.029863 | 7.2655 | 5.1972 | 5.3242 | -0.12517 | 0.081022 | -0.39601 | -0.11974 | 10.1506 | 7.6436 | 8.0396 | 0.080964 | -0.10814 | 122.9392 | 122.8439 | 123.0501 | 46.6346 | -123.0961 | 122.8493 | 123.05 | 122.8609 | 46.0425 | -123.3651
1424.7969 | 123.1888 | -64.5676 | 58.374 | 0.0094624 | -0.0066986 | 0.0027436 | 0.05772 | 0.00093806 | 0.067924 | -0.001755 | 0.0077273 | 0.004739 | 0.060161 | 0.024899 | 0.066978 | -57.2792 | -18.02 | -59.3521 | 58.3533 | 58.2489 | 58.4596 | -64.7129 | -54.3986 | -18.5526 | -56.8873 | 58.2634 | 58.4504 | 58.1926 | -64.9819 | -0.14533 | -0.020704 | 7.2884 | 5.2155 | 5.3608 | -0.12517 | 0.085603 | -0.41432 | -0.11058 | 10.169 | 7.6803 | 8.0946 | 0.076387 | -0.18139 | 122.9209 | 122.8164 | 123.0272 | 46.5476 | -123.0869 | 122.831 | 123.018 | 122.7602 | 46.015 | -123.3559
1425.7969 | 123.0927 | -64.6042 | 58.4061 | 0.0018314 | -0.006485 | 0.0027436 | 0.057293 | 0.00072426 | 0.06771 | -0.0093855 | 0.0075137 | 0.0049526 | 0.060375 | 0.025327 | 0.066978 | -57.238 | -18.0703 | -59.3109 | 58.3533 | 58.2626 | 58.4688 | -64.7129 | -54.3345 | -18.5755 | -56.8369 | 58.2543 | 58.4596 | 58.3208 | -64.9727 | -0.10871 | -0.052748 | 7.3662 | 5.2933 | 5.402 | -0.14347 | 0.062716 | -0.36854 | -0.15178 | 10.2697 | 7.7673 | 8.1358 | 0.053501 | -0.085235 | 122.9575 | 122.8668 | 123.073 | 46.5338 | -123.119 | 122.8585 | 123.0638 | 122.925 | 46.0287 | -123.3788
1426.7969 | 123.2025 | -64.563 | 58.3511 | 0.0094624 | -0.006485 | 0.0027436 | 0.057506 | 0.00029706 | 0.067496 | -0.001755 | 0.0075137 | 0.0051662 | 0.060375 | 0.025327 | 0.066764 | -57.2059 | -18.1115 | -59.2926 | 58.3442 | 58.2626 | 58.455 | -64.7221 | -54.2704 | -18.6213 | -56.7957 | 58.2543 | 58.4458 | 58.3071 | -64.9865 | -0.15906 | -0.006973 | 7.3571 | 5.2704 | 5.4295 | -0.08854 | 0.10391 | -0.42348 | -0.096846 | 10.2926 | 7.7673 | 8.1907 | 0.094697 | -0.044038 | 122.9072 | 122.8256 | 123.018 | 46.4514 | -123.0732 | 122.8173 | 123.0088 | 122.8701 | 45.9417 | -123.3376
1427.7969 | 123.1613 | -64.5538 | 58.4381 | -0.0057996 | -0.0066986 | 0.00253 | 0.057506 | 0.00093806 | 0.067496 | -0.001755 | 0.0077273 | 0.0051662 | 0.060375 | 0.025327 | 0.066978 | -57.1464 | -18.1482 | -59.2285 | 58.3625 | 58.2763 | 58.4779 | -64.7037 | -54.1926 | -18.6213 | -56.7225 | 58.2726 | 58.4596 | 58.2934 | -64.9727 | -0.1499 | -0.075635 | 7.4074 | 5.3254 | 5.4753 | -0.16178 | 0.039831 | -0.41889 | -0.16551 | 10.3613 | 7.8314 | 8.2503 | 0.021458 | -0.14475 | 122.9163 | 122.8302 | 123.0318 | 46.4057 | -123.1418 | 122.8264 | 123.0134 | 122.8472 | 45.9326 | -123.4108
1428.7969 | 123.2666 | -64.5447 | 58.374 | 0.0018314 | -0.006485 | 0.00253 | 0.05772 | 0.00093806 | 0.06771 | 0.013506 | 0.0079409 | 0.0049526 | 0.060161 | 0.025754 | 0.067192 | -57.1006 | -18.2306 | -59.1735 | 58.3671 | 58.2901 | 58.4688 | -64.6992 | -54.1468 | -18.6579 | -56.6538 | 58.268 | 58.4687 | 58.3163 | -64.959 | -0.15448 | -0.006969 | 7.4441 | 5.3711 | 5.5256 | -0.083955 | 0.09476 | -0.41431 | -0.106 | 10.3979 | 7.8909 | 8.3052 | 0.094702 | -0.057769 | 122.9117 | 122.8347 | 123.0135 | 46.3141 | -123.0732 | 122.8127 | 123.0134 | 122.8609 | 45.8868 | -123.333
1429.7969 | 123.2162 | -64.5172 | 58.3923 | 0.0018314 | -0.006485 | 0.0027436 | 0.057506 | 0.00072426 | 0.067924 | 0.013506 | 0.0079409 | 0.0049526 | 0.060802 | 0.02554 | 0.067192 | -57.0411 | -18.2581 | -59.1277 | 58.3716 | 58.2992 | 58.4917 | -64.69 | -54.0781 | -18.6991 | -56.5988 | 58.2772 | 58.4779 | 58.2888 | -64.959 | -0.17279 | -0.020702 | 7.4761 | 5.3895 | 5.5623 | -0.093108 | 0.099342 | -0.44178 | -0.11515 | 10.4391 | 7.9184 | 8.3602 | 0.085548 | -0.10355 | 122.8888 | 122.8164 | 123.0089 | 46.2592 | -123.0823 | 122.7944 | 122.9951 | 122.806 | 45.8181 | -123.3513
1430.7969 | 123.111 | -64.5447 | 58.4335 | 0.0018314 | -0.006485 | 0.0027436 | 0.057293 | 0.00072426 | 0.068137 | 0.013506 | 0.0079409 | 0.0051662 | 0.060375 | 0.025327 | 0.067405 | -56.9953 | -18.3313 | -59.0865 | 58.3671 | 58.2992 | 58.4779 | -64.6946 | -54.0186 | -18.7037 | -56.5576 | 58.2818 | 58.4779 | 58.3437 | -64.959 | -0.1499 | -0.066479 | 7.5494 | 5.4581 | 5.608 | -0.13431 | 0.044408 | -0.41431 | -0.15177 | 10.5261 | 7.987 | 8.4014 | 0.044349 | -0.089808 | 122.9117 | 122.8439 | 123.0226 | 46.2134 | -123.1281 | 122.8264 | 123.0226 | 122.8884 | 45.841 | -123.3925
1431.7969 | 123.2071 | -64.5264 | 58.4015 | -0.013431 | -0.0069124 | 0.0027436 | 0.05772 | 0.0011517 | 0.06771 | -0.001755 | 0.0081547 | 0.0049526 | 0.060375 | 0.025327 | 0.067405 | -56.9404 | -18.3817 | -59.0362 | 58.3808 | 58.2855 | 58.4917 | -64.6763 | -53.9316 | -18.7266 | -56.4706 | 58.2955 | 58.487 | 58.3117 | -64.9407 | -0.14989 | -0.0207 | 7.586 | 5.4902 | 5.6401 | -0.116 | 0.090187 | -0.41431 | -0.10599 | 10.5948 | 8.0557 | 8.47 | 0.08555 | -0.089814 | 122.9072 | 122.8119 | 123.018 | 46.1447 | -123.0777 | 122.8219 | 123.0134 | 122.838 | 45.7998 | -123.3422
1432.7969 | 123.1979 | -64.5355 | 58.4061 | -0.013431 | -0.0066986 | 0.0027436 | 0.057506 | 0.0011517 | 0.068137 | 0.0058755 | 0.0081547 | 0.0049526 | 0.060375 | 0.025754 | 0.067405 | -56.9312 | -18.4595 | -59.027 | 58.3487 | 58.2672 | 58.4596 | -64.7221 | -53.9362 | -18.7998 | -56.4661 | 58.2543 | 58.4504 | 58.3117 | -64.9819 | -0.18653 | -0.057327 | 7.6043 | 5.5085 | 5.695 | -0.13889 | 0.053559 | -0.44636 | -0.15178 | 10.5994 | 8.0695 | 8.5158 | 0.044343 | -0.094392 | 122.8843 | 122.8027 | 122.9951 | 46.076 | -123.1281 | 122.7898 | 122.9859 | 122.8472 | 45.7357 | -123.388
1433.7969 | 123.2254 | -64.5493 | 58.3878 | -0.0057996 | -0.0066986 | 0.003171 | 0.05772 | 0.0011517 | 0.067924 | -0.0093855 | 0.0081547 | 0.004739 | 0.060161 | 0.025754 | 0.066978 | -56.8992 | -18.5282 | -58.9858 | 58.3396 | 58.2443 | 58.455 | -64.7221 | -53.8812 | -18.841 | -56.4157 | 58.2589 | 58.4504 | 58.3208 | -64.9865 | -0.1728 | -0.048172 | 7.6501 | 5.5634 | 5.7362 | -0.14348 | 0.067292 | -0.43721 | -0.12889 | 10.668 | 8.1336 | 8.5708 | 0.062654 | -0.066924 | 122.8888 | 122.7935 | 123.0043 | 46.0211 | -123.1098 | 122.8081 | 122.9997 | 122.8701 | 45.7082 | -123.3742
1434.7969 | 123.1476 | -64.5493 | 58.3969 | -0.0057996 | -0.006485 | 0.0029572 | 0.05772 | 0.0011517 | 0.068351 | -0.001755 | 0.0083683 | 0.0049526 | 0.060161 | 0.025754 | 0.067619 | -56.8442 | -18.5831 | -58.9355 | 58.3533 | 58.2672 | 58.455 | -64.7129 | -53.8217 | -18.9189 | -56.3516 | 58.268 | 58.455 | 58.2979 | -64.9865 | -0.16364 | -0.043593 | 7.705 | 5.6138 | 5.7774 | -0.12974 | 0.058136 | -0.43721 | -0.12889 | 10.7276 | 8.1977 | 8.6349 | 0.058077 | -0.098973 | 122.9026 | 122.8164 | 123.0043 | 45.9661 | -123.1098 | 122.8173 | 123.0042 | 122.8472 | 45.6304 | -123.3834
1435.7969 | 123.1522 | -64.563 | 58.4015 | -0.013431 | -0.0060576 | 0.0029572 | 0.057293 | 0.00093806 | 0.068137 | -0.001755 | 0.0083683 | 0.0051662 | 0.060375 | 0.025754 | 0.067405 | -56.7847 | -18.6243 | -58.8714 | 58.3579 | 58.2672 | 58.4688 | -64.6946 | -53.7484 | -18.9509 | -56.2783 | 58.2772 | 58.4687 | 58.3071 | -64.9681 | -0.13159 | -0.043592 | 7.7783 | 5.6916 | 5.8232 | -0.13432 | 0.067294 | -0.40516 | -0.12431 | 10.8146 | 8.2847 | 8.6898 | 0.067236 | -0.094392 | 122.9209 | 122.8302 | 123.0318 | 45.9386 | -123.0961 | 122.8402 | 123.0317 | 122.8701 | 45.6121 | -123.3696
1436.7969 | 123.2254 | -64.5447 | 58.4152 | 0.0094624 | -0.006485 | 0.0029572 | 0.058147 | 0.0013653 | 0.068137 | 0.0058755 | 0.0083683 | 0.0049526 | 0.060802 | 0.026181 | 0.067192 | -56.7389 | -18.6747 | -58.8347 | 58.3716 | 58.2901 | 58.4871 | -64.6854 | -53.6981 | -18.9967 | -56.228 | 58.2818 | 58.4733 | 58.33 | -64.959 | -0.14074 | -0.04359 | 7.8058 | 5.7099 | 5.8507 | -0.12515 | 0.071876 | -0.41431 | -0.13346 | 10.8466 | 8.3167 | 8.731 | 0.058081 | -0.085232 | 122.9163 | 122.8347 | 123.0318 | 45.87 | -123.1006 | 122.8264 | 123.018 | 122.8747 | 45.548 | -123.3742
1437.7969 | 123.1659 | -64.5813 | 58.3786 | 0.0094624 | -0.006485 | 0.0027436 | 0.057293 | 0.00051066 | 0.068351 | -0.0093855 | 0.0085819 | 0.0051662 | 0.060588 | 0.025754 | 0.067405 | -56.7206 | -18.7617 | -58.821 | 58.335 | 58.2626 | 58.4505 | -64.7312 | -53.6797 | -19.07 | -56.2051 | 58.2451 | 58.4321 | 58.2384 | -64.9956 | -0.14991 | -0.043596 | 7.8607 | 5.7603 | 5.9102 | -0.11601 | 0.071868 | -0.41432 | -0.13347 | 10.9016 | 8.3762 | 8.7906 | 0.053495 | -0.14018 | 122.9163 | 122.8439 | 123.0318 | 45.8196 | -123.1098 | 122.8264 | 123.0134 | 122.8197 | 45.5113 | -123.3742
1438.7969 | 123.1979 | -64.5401 | 58.4015 | 0.0018314 | -0.0062714 | 0.0029572 | 0.05772 | 0.00093806 | 0.068351 | 0.0058755 | 0.0081547 | 0.0051662 | 0.060588 | 0.025968 | 0.067833 | -56.6611 | -18.8258 | -58.7661 | 58.3442 | 58.2626 | 58.4596 | -64.7175 | -53.6156 | -19.1066 | -56.1135 | 58.268 | 58.4458 | 58.2888 | -64.991 | -0.17737 | -0.057327 | 7.879 | 5.774 | 5.9514 | -0.13889 | 0.058137 | -0.45094 | -0.13346 | 10.9245 | 8.4266 | 8.8775 | 0.044343 | -0.11271 | 122.8843 | 122.8027 | 122.9997 | 45.7143 | -123.119 | 122.8081 | 122.9859 | 122.8289 | 45.4335 | -123.3925
1439.7969 | 123.1979 | -64.5218 | 58.3649 | 0.0018314 | -0.006485 | 0.0029572 | 0.057506 | 0.0011517 | 0.068137 | -0.017016 | 0.0085819 | 0.0049526 | 0.060588 | 0.025754 | 0.067619 | -56.6061 | -18.8762 | -58.7111 | 58.3625 | 58.2718 | 58.4642 | -64.7037 | -53.5561 | -19.0883 | -56.0494 | 58.268 | 58.455 | 58.2888 | -64.9681 | -0.18194 | -0.002393 | 7.9156 | 5.8107 | 5.9926 | -0.093115 | 0.099337 | -0.44636 | -0.096843 | 10.9657 | 8.4724 | 8.9188 | 0.090121 | -0.076086 | 122.8843 | 122.7935 | 122.986 | 45.6456 | -123.0686 | 122.7898 | 122.9768 | 122.8106 | 45.4335 | -123.333
1440.7969 | 123.1705 | -64.5493 | 58.4015 | -0.0057996 | -0.006485 | 0.0027436 | 0.057934 | 0.0013653 | 0.068351 | -0.001755 | 0.0087955 | 0.0051662 | 0.060802 | 0.026181 | 0.067833 | -56.5604 | -18.9357 | -58.6699 | 58.3533 | 58.2718 | 58.4642 | -64.7083 | -53.492 | -19.1203 | -55.9944 | 58.268 | 58.455 | 58.2934 | -64.9727 | -0.15906 | -0.04817 | 7.9889 | 5.8793 | 6.0384 | -0.12974 | 0.062716 | -0.42347 | -0.13346 | 11.0572 | 8.5548 | 8.9783 | 0.0535 | -0.10813 | 122.9026 | 122.821 | 123.0135 | 45.6136 | -123.1098 | 122.8173 | 123.0042 | 122.8426 | 45.4289 | -123.3742
1441.7969 | 123.1705 | -64.5767 | 58.3603 | -0.013431 | -0.0062714 | 0.003171 | 0.057293 | 0.0011517 | 0.068137 | -0.001755 | 0.0090091 | 0.0051662 | 0.061016 | 0.026181 | 0.067405 | -56.5329 | -19.0135 | -58.6241 | 58.3396 | 58.2489 | 58.455 | -64.7129 | -53.4462 | -19.1432 | -55.9532 | 58.2497 | 58.4458 | 58.2476 | -64.991 | -0.13617 | -0.020707 | 8.0438 | 5.9526 | 6.0888 | -0.11143 | 0.094757 | -0.41432 | -0.11058 | 11.1305 | 8.6235 | 9.0378 | 0.085541 | -0.11272 | 122.9163 | 122.8256 | 123.0318 | 45.5632 | -123.0732 | 122.8264 | 123.0226 | 122.8243 | 45.4335 | -123.3513
1442.7969 | 123.1522 | -64.4943 | 58.429 | -0.013431 | -0.0060576 | 0.0029572 | 0.05772 | 0.0015789 | 0.068351 | -0.001755 | 0.0085819 | 0.0049526 | 0.060588 | 0.026395 | 0.06826 | -56.4459 | -19.0318 | -58.5555 | 58.3899 | 58.2901 | 58.5008 | -64.6808 | -53.3547 | -19.1432 | -55.8571 | 58.3001 | 58.4916 | 58.3163 | -64.9453 | -0.18652 | -0.039009 | 8.0484 | 5.9389 | 6.1254 | -0.13889 | 0.071879 | -0.45093 | -0.12888 | 11.1397 | 8.6372 | 9.0882 | 0.062663 | -0.1127 | 122.8843 | 122.7844 | 122.9952 | 45.4625 | -123.1098 | 122.7944 | 122.9859 | 122.8106 | 45.3511 | -123.3742
1443.7969 | 123.175 | -64.5447 | 58.4061 | 0.0018314 | -0.0060576 | 0.0033846 | 0.05772 | 0.0013653 | 0.068351 | -0.001755 | 0.0083683 | 0.00538 | 0.060802 | 0.025968 | 0.06826 | -56.4093 | -19.1005 | -58.5143 | 58.3716 | 58.2809 | 58.4779 | -64.6854 | -53.3135 | -19.2028 | -55.8021 | 58.2772 | 58.4779 | 58.2934 | -64.9544 | -0.14074 | -0.034435 | 8.1354 | 6.0304 | 6.1712 | -0.12516 | 0.071874 | -0.40973 | -0.12888 | 11.2312 | 8.7425 | 9.1523 | 0.071815 | -0.11271 | 122.9163 | 122.8256 | 123.0226 | 45.4442 | -123.0915 | 122.8219 | 123.0226 | 122.838 | 45.3419 | -123.3605
1444.7969 | 123.2758 | -64.5401 | 58.4015 | 0.0018314 | -0.005844 | 0.0029572 | 0.057293 | 0.0013653 | 0.068565 | 0.0058755 | 0.0090091 | 0.0051662 | 0.060802 | 0.026395 | 0.068046 | -56.3498 | -19.1417 | -58.4593 | 58.3762 | 58.2946 | 58.4917 | -64.6854 | -53.2493 | -19.2073 | -55.738 | 58.2863 | 58.487 | 58.3163 | -64.9453 | -0.14532 | -0.025278 | 8.1903 | 6.0808 | 6.2261 | -0.10684 | 0.090187 | -0.40515 | -0.11515 | 11.2908 | 8.8021 | 9.2072 | 0.08555 | -0.085235 | 122.9163 | 122.8347 | 123.0318 | 45.3984 | -123.0869 | 122.8264 | 123.0271 | 122.8564 | 45.3328 | -123.3467
1445.7969 | 123.23 | -64.5035 | 58.4427 | 0.0094624 | -0.0062714 | 0.0027436 | 0.058147 | 0.0013653 | 0.068351 | 0.0058755 | 0.0090091 | 0.0051662 | 0.060802 | 0.025968 | 0.068046 | -56.2765 | -19.1372 | -58.3861 | 58.4174 | 58.345 | 58.5375 | -64.6396 | -53.1532 | -19.1799 | -55.6327 | 58.3367 | 58.5191 | 58.3346 | -64.9132 | -0.13615 | -0.025272 | 8.227 | 6.1174 | 6.2536 | -0.097673 | 0.094774 | -0.40972 | -0.10599 | 11.3503 | 8.8707 | 9.2805 | 0.076401 | -0.10812 | 122.9209 | 122.8485 | 123.0409 | 45.3663 | -123.0823 | 122.8402 | 123.0226 | 122.838 | 45.3236 | -123.3559
1446.7969 | 123.2346 | -64.444 | 58.4885 | 0.0018314 | -0.0060576 | 0.003171 | 0.057934 | 0.0011517 | 0.068565 | -0.001755 | 0.0090091 | 0.00538 | 0.060588 | 0.026609 | 0.067833 | -56.1987 | -19.16 | -58.3082 | 58.4449 | 58.3633 | 58.5604 | -64.6122 | -53.057 | -19.1936 | -55.5549 | 58.3596 | 58.5557 | 58.3346 | -64.8812 | -0.16819 | -0.043578 | 8.2453 | 6.1357 | 6.3039 | -0.12513 | 0.071892 | -0.43718 | -0.12887 | 11.3869 | 8.8891 | 9.3263 | 0.067254 | -0.1539 | 122.8889 | 122.8073 | 123.0043 | 45.2839 | -123.1006 | 122.8036 | 122.9997 | 122.7785 | 45.2504 | -123.3696
1447.7969 | 123.2208 | -64.4531 | 58.4976 | 0.0018314 | -0.0062714 | 0.0027436 | 0.057934 | 0.0013653 | 0.068565 | -0.0093855 | 0.0087955 | 0.00538 | 0.060588 | 0.026609 | 0.06826 | -56.1437 | -19.1921 | -58.267 | 58.4403 | 58.3633 | 58.5558 | -64.6167 | -52.9929 | -19.2211 | -55.4954 | 58.3642 | 58.5511 | 58.3346 | -64.8857 | -0.16361 | -0.057312 | 8.3094 | 6.1861 | 6.3497 | -0.13429 | 0.058157 | -0.4326 | -0.13345 | 11.4602 | 8.9578 | 9.3904 | 0.05352 | -0.16305 | 122.8934 | 122.8165 | 123.0089 | 45.261 | -123.1144 | 122.8173 | 123.0043 | 122.7877 | 45.2321 | -123.3833
1448.7969 | 123.2437 | -64.444 | 58.4976 | 0.0094624 | -0.0060576 | 0.003171 | 0.057506 | 0.0015789 | 0.068778 | 0.0058755 | 0.0092229 | 0.0051662 | 0.060802 | 0.026609 | 0.068474 | -56.1025 | -19.2425 | -58.2212 | 58.454 | 58.3771 | 58.5741 | -64.6122 | -52.9288 | -19.2073 | -55.4267 | 58.3733 | 58.5511 | 58.4216 | -64.872 | -0.16819 | -0.043577 | 8.3415 | 6.2227 | 6.3909 | -0.12055 | 0.076471 | -0.42802 | -0.12429 | 11.5151 | 9.0173 | 9.4453 | 0.05352 | -0.076058 | 122.898 | 122.821 | 123.0181 | 45.2015 | -123.1098 | 122.8173 | 122.9951 | 122.8655 | 45.2366 | -123.3696
1449.7969 | 123.2025 | -64.4302 | 58.4839 | 0.0018314 | -0.0060576 | 0.003171 | 0.05772 | 0.0015789 | 0.068992 | 0.0058755 | 0.0090091 | 0.00538 | 0.060802 | 0.026609 | 0.068046 | -56.0338 | -19.3066 | -58.1617 | 58.4586 | 58.3816 | 58.5695 | -64.5938 | -52.8373 | -19.2394 | -55.3489 | 58.3733 | 58.5649 | 58.4078 | -64.8674 | -0.1636 | -0.025265 | 8.3964 | 6.2685 | 6.4321 | -0.10224 | 0.085626 | -0.43718 | -0.11056 | 11.593 | 9.0814 | 9.5186 | 0.080989 | -0.076061 | 122.8889 | 122.8119 | 122.9998 | 45.1237 | -123.0777 | 122.8036 | 122.9951 | 122.8381 | 45.1909 | -123.3513
1450.7969 | 123.2025 | -64.3982 | 58.5342 | 0.0094624 | -0.005844 | 0.0033846 | 0.05772 | 0.0015789 | 0.068565 | -0.0093855 | 0.0090091 | 0.0055936 | 0.061229 | 0.026822 | 0.06826 | -55.9652 | -19.3569 | -58.0885 | 58.4815 | 58.3816 | 58.5878 | -64.5801 | -52.764 | -19.2669 | -55.2802 | 58.3871 | 58.5878 | 58.4124 | -64.8491 | -0.18191 | -0.052727 | 8.433 | 6.3097 | 6.4916 | -0.15259 | 0.053586 | -0.45091 | -0.14718 | 11.6342 | 9.118 | 9.5689 | 0.053528 | -0.12184 | 122.8797 | 122.7798 | 122.986 | 45.0413 | -123.1143 | 122.7853 | 122.986 | 122.8106 | 45.1313 | -123.3833
1451.7969 | 123.2162 | -64.3845 | 58.5388 | -0.0057996 | -0.0060576 | 0.0035984 | 0.05772 | 0.0017927 | 0.068778 | 0.0058755 | 0.0092229 | 0.0058072 | 0.060802 | 0.026822 | 0.068687 | -55.8919 | -19.3615 | -58.029 | 58.4907 | 58.4183 | 58.6107 | -64.5664 | -52.6907 | -19.3081 | -55.2023 | 58.41 | 58.6061 | 58.4353 | -64.8354 | -0.18191 | -0.048148 | 8.4925 | 6.3555 | 6.5374 | -0.12054 | 0.071902 | -0.4509 | -0.12886 | 11.6937 | 9.1821 | 9.633 | 0.067265 | -0.10352 | 122.8751 | 122.8027 | 122.9952 | 45.023 | -123.1052 | 122.7944 | 122.9905 | 122.8198 | 45.0764 | -123.3742
1452.7969 | 123.2117 | -64.3524 | 58.5846 | 0.0018314 | -0.0056302 | 0.0029572 | 0.05772 | 0.0015789 | 0.068992 | 0.0058755 | 0.0094365 | 0.0051662 | 0.060802 | 0.026609 | 0.068474 | -55.8187 | -19.4027 | -57.9511 | 58.5319 | 58.4503 | 58.6473 | -64.5252 | -52.5717 | -19.2806 | -55.1016 | 58.442 | 58.6336 | 58.4124 | -64.8033 | -0.17274 | -0.052719 | 8.5338 | 6.4013 | 6.574 | -0.13426 | 0.062754 | -0.45089 | -0.14259 | 11.7807 | 9.2508 | 9.7017 | 0.04896 | -0.17219 | 122.8843 | 122.8027 | 122.9998 | 44.9497 | -123.1098 | 122.7944 | 122.986 | 122.7648 | 45.0718 | -123.3879
1453.7969 | 123.2071 | -64.3936 | 58.5754 | 0.0018314 | -0.005844 | 0.0027436 | 0.058147 | 0.0020063 | 0.068778 | 0.0058755 | 0.0092229 | 0.0055936 | 0.060802 | 0.026822 | 0.068687 | -55.7408 | -19.4164 | -57.8504 | 58.5639 | 58.487 | 58.6748 | -64.5023 | -52.4755 | -19.2394 | -55.0283 | 58.4649 | 58.6702 | 58.5086 | -64.7621 | -0.10865 | -0.011514 | 8.6528 | 6.5432 | 6.6519 | -0.088477 | 0.099382 | -0.36849 | -0.11054 | 11.9181 | 9.3653 | 9.7338 | 0.094744 | -0.066884 | 122.9575 | 122.8806 | 123.0684 | 44.9772 | -123.0777 | 122.8585 | 123.0638 | 122.9022 | 45.1542 | -123.3375
1454.7969 | 123.2025 | -64.3158 | 58.6304 | -0.0057996 | -0.0060576 | 0.003171 | 0.057934 | 0.0015789 | 0.069205 | -0.001755 | 0.0094365 | 0.00538 | 0.061229 | 0.027036 | 0.068474 | -55.6767 | -19.4485 | -57.8184 | 58.5593 | 58.4686 | 58.6748 | -64.4977 | -52.4343 | -19.331 | -54.9551 | 58.4695 | 58.6656 | 58.5131 | -64.7621 | -0.18189 | -0.071025 | 8.6391 | 6.4974 | 6.6793 | -0.16172 | 0.04445 | -0.44631 | -0.16089 | 11.8815 | 9.3607 | 9.807 | 0.035234 | -0.11724 | 122.8751 | 122.7844 | 122.9906 | 44.8673 | -123.1281 | 122.7853 | 122.9814 | 122.8289 | 44.9848 | -123.3925
1455.7969 | 123.1979 | -64.325 | 58.5846 | 0.0018314 | -0.005844 | 0.0029572 | 0.058147 | 0.0017927 | 0.068992 | 0.0058755 | 0.0094365 | 0.0051662 | 0.061016 | 0.027036 | 0.068901 | -55.6309 | -19.508 | -57.768 | 58.5502 | 58.4641 | 58.6565 | -64.5068 | -52.3886 | -19.3676 | -54.9047 | 58.4695 | 58.6519 | 58.5223 | -64.7713 | -0.18189 | -0.034406 | 8.694 | 6.557 | 6.7388 | -0.12053 | 0.071911 | -0.44631 | -0.11512 | 11.9364 | 9.4202 | 9.8665 | 0.067274 | -0.062304 | 122.8751 | 122.789 | 122.9815 | 44.8169 | -123.0914 | 122.7944 | 122.9768 | 122.8472 | 44.9574 | -123.3559
1456.7969 | 123.1064 | -64.3662 | 58.6899 | 0.0018314 | -0.0054166 | 0.0033846 | 0.05772 | 0.0017927 | 0.069205 | -0.001755 | 0.0094365 | 0.0058072 | 0.061016 | 0.027036 | 0.068901 | -55.5485 | -19.5401 | -57.6764 | 58.5822 | 58.4915 | 58.6931 | -64.4748 | -52.3016 | -19.3401 | -54.804 | 58.4878 | 58.6839 | 58.5589 | -64.7484 | -0.10864 | -0.10764 | 8.8176 | 6.6897 | 6.7984 | -0.19834 | 0.003255 | -0.38222 | -0.20209 | 12.0646 | 9.5622 | 9.9444 | -0.005961 | -0.13096 | 122.9484 | 122.8577 | 123.0593 | 44.8261 | -123.1647 | 122.8539 | 123.0501 | 122.9251 | 45.026 | -123.4382
1457.7969 | 123.1888 | -64.3112 | 58.6029 | 0.0018314 | -0.005844 | 0.0033846 | 0.057934 | 0.0013653 | 0.069419 | 0.0058755 | 0.0094365 | 0.00538 | 0.061443 | 0.027036 | 0.069115 | -55.5027 | -19.5859 | -57.6215 | 58.5822 | 58.487 | 58.6931 | -64.4931 | -52.2283 | -19.3493 | -54.7445 | 58.4924 | 58.6748 | 58.5177 | -64.7529 | -0.18189 | -0.020667 | 8.8085 | 6.6897 | 6.8716 | -0.11594 | 0.09023 | -0.44173 | -0.11053 | 12.0829 | 9.5668 | 10.0085 | 0.071857 | -0.085193 | 122.8935 | 122.7982 | 123.0044 | 44.7254 | -123.096 | 122.8036 | 122.986 | 122.8289 | 44.9619 | -123.3558
1458.7969 | 123.0927 | -64.3753 | 58.6578 | -0.0057996 | -0.0056302 | 0.003171 | 0.057506 | 0.0017927 | 0.069419 | 0.0058755 | 0.0096501 | 0.0055936 | 0.060802 | 0.027036 | 0.068901 | -55.4524 | -19.6087 | -57.5803 | 58.5822 | 58.4915 | 58.6977 | -64.4794 | -52.1871 | -19.3813 | -54.6849 | 58.4924 | 58.6885 | 58.5543 | -64.7484 | -0.10406 | -0.075599 | 8.9229 | 6.795 | 6.8991 | -0.1663 | 0.039877 | -0.37306 | -0.16547 | 12.1882 | 9.6904 | 10.0634 | 0.030661 | -0.1035 | 122.9575 | 122.8668 | 123.073 | 44.7666 | -123.1372 | 122.8677 | 123.0638 | 122.9296 | 44.994 | -123.4062
1459.7969 | 123.23 | -64.3066 | 58.58 | -0.0057996 | -0.0056302 | 0.0029572 | 0.057934 | 0.0017927 | 0.069419 | -0.001755 | 0.0096501 | 0.0058072 | 0.061229 | 0.027036 | 0.068901 | -55.3974 | -19.6637 | -57.5253 | 58.5731 | 58.4778 | 58.684 | -64.4885 | -52.1367 | -19.3996 | -54.63 | 58.4878 | 58.6748 | 58.5131 | -64.7621 | -0.18188 | -0.006936 | 8.9092 | 6.7813 | 6.9632 | -0.10221 | 0.10396 | -0.45546 | -0.092224 | 12.1699 | 9.6766 | 10.1321 | 0.094745 | -0.066883 | 122.8797 | 122.7844 | 122.9906 | 44.6429 | -123.0685 | 122.7944 | 122.9814 | 122.8198 | 44.907 | -123.3421
1460.7969 | 123.1476 | -64.3066 | 58.6578 | -0.0057996 | -0.0056302 | 0.0033846 | 0.05772 | 0.0020063 | 0.069419 | -0.001755 | 0.0098637 | 0.0055936 | 0.061229 | 0.026822 | 0.068901 | -55.3196 | -19.6683 | -57.4338 | 58.6143 | 58.5236 | 58.716 | -64.4611 | -52.0589 | -19.3584 | -54.5293 | 58.5153 | 58.7114 | 58.5681 | -64.7117 | -0.15441 | -0.04355 | 8.987 | 6.8729 | 7.0273 | -0.13424 | 0.058191 | -0.40509 | -0.14257 | 12.2478 | 9.7774 | 10.1825 | 0.053554 | -0.08976 | 122.9209 | 122.8302 | 123.0227 | 44.6384 | -123.1189 | 122.8219 | 123.018 | 122.8747 | 44.9482 | -123.3696
1461.7969 | 123.2162 | -64.2975 | 58.667 | 0.017093 | -0.0056302 | 0.003171 | 0.058147 | 0.0017927 | 0.069205 | -0.001755 | 0.0098637 | 0.0058072 | 0.060802 | 0.02725 | 0.069328 | -55.2693 | -19.7095 | -57.3834 | 58.596 | 58.5373 | 58.7206 | -64.4611 | -52.0085 | -19.363 | -54.4697 | 58.5198 | 58.7022 | 58.5543 | -64.7301 | -0.16357 | -0.071019 | 9.0282 | 6.9141 | 7.0776 | -0.12966 | 0.053615 | -0.43257 | -0.14715 | 12.289 | 9.8277 | 10.2603 | 0.035242 | -0.11265 | 122.8935 | 122.8348 | 123.0181 | 44.588 | -123.128 | 122.8173 | 122.9997 | 122.8518 | 44.9345 | -123.397
1462.7969 | 123.111 | -64.2975 | 58.7402 | -0.0057996 | -0.0054166 | 0.003171 | 0.058147 | 0.0022199 | 0.069419 | -0.001755 | 0.010077 | 0.006021 | 0.061229 | 0.027891 | 0.068901 | -55.196 | -19.7415 | -57.3331 | 58.6143 | 58.5419 | 58.7252 | -64.4427 | -51.9353 | -19.4271 | -54.3965 | 58.5198 | 58.716 | 58.5498 | -64.7209 | -0.14525 | -0.12595 | 9.1015 | 6.9644 | 7.1097 | -0.19833 | -0.015049 | -0.42341 | -0.22039 | 12.3622 | 9.901 | 10.3244 | -0.024265 | -0.19047 | 122.9118 | 122.8394 | 123.0227 | 44.556 | -123.183 | 122.8173 | 123.0135 | 122.8472 | 44.8704 | -123.4611
1463.7969 | 123.1567 | -64.2746 | 58.7219 | -0.0057996 | -0.0056302 | 0.003171 | 0.058147 | 0.0020063 | 0.069633 | -0.001755 | 0.0098637 | 0.00538 | 0.061016 | 0.027463 | 0.069115 | -55.1273 | -19.769 | -57.2461 | 58.6418 | 58.5648 | 58.7572 | -64.4244 | -51.8483 | -19.4271 | -54.3186 | 58.5519 | 58.7389 | 58.591 | -64.6843 | -0.14982 | -0.080167 | 9.1473 | 7.0285 | 7.1783 | -0.15712 | 0.035311 | -0.40967 | -0.17003 | 12.4263 | 9.956 | 10.3656 | 0.016938 | -0.13095 | 122.9164 | 122.8394 | 123.0318 | 44.5056 | -123.1463 | 122.8265 | 123.0135 | 122.8656 | 44.8475 | -123.4062
1464.7969 | 123.0972 | -64.2746 | 58.754 | 0.0018314 | -0.0054166 | 0.003171 | 0.057506 | 0.0020063 | 0.069846 | -0.001755 | 0.0098637 | 0.00538 | 0.061016 | 0.027036 | 0.069756 | -55.0632 | -19.8102 | -57.1774 | 58.6555 | 58.5785 | 58.7572 | -64.4107 | -51.7658 | -19.3996 | -54.2545 | 58.5656 | 58.7526 | 58.591 | -64.6751 | -0.13609 | -0.098475 | 9.2114 | 7.0972 | 7.2333 | -0.17543 | 0.003268 | -0.40051 | -0.18834 | 12.5088 | 10.0201 | 10.4206 | -0.001369 | -0.163 | 122.9301 | 122.8531 | 123.0318 | 44.4644 | -123.1647 | 122.8402 | 123.0272 | 122.8656 | 44.875 | -123.4291
1465.7969 | 123.143 | -64.238 | 58.7357 | -0.013431 | -0.0054166 | 0.0033846 | 0.057506 | 0.0020063 | 0.069419 | 0.0058755 | 0.010291 | 0.006021 | 0.061016 | 0.027463 | 0.069328 | -54.9808 | -19.8423 | -57.0813 | 58.6784 | 58.606 | 58.7893 | -64.3878 | -51.6697 | -19.4363 | -54.1721 | 58.5977 | 58.7892 | 58.591 | -64.6385 | -0.14981 | -0.057273 | 9.2572 | 7.1567 | 7.3065 | -0.12964 | 0.053629 | -0.4005 | -0.13798 | 12.5683 | 10.0659 | 10.4664 | 0.05357 | -0.14469 | 122.9164 | 122.844 | 123.0273 | 44.3957 | -123.1234 | 122.8357 | 123.0272 | 122.8289 | 44.8017 | -123.3741
1466.7969 | 123.0881 | -64.2838 | 58.7128 | 0.0018314 | -0.005203 | 0.0035984 | 0.057934 | 0.0022199 | 0.069846 | 0.0058755 | 0.010505 | 0.0058072 | 0.061229 | 0.027677 | 0.069115 | -54.9259 | -19.8789 | -57.0446 | 58.6692 | 58.6014 | 58.7893 | -64.3924 | -51.601 | -19.418 | -54.1172 | 58.5839 | 58.7801 | 58.6184 | -64.6522 | -0.10862 | -0.043542 | 9.3579 | 7.2391 | 7.3477 | -0.11133 | 0.076517 | -0.36846 | -0.12883 | 12.6827 | 10.1666 | 10.535 | 0.067301 | -0.094328 | 122.953 | 122.8852 | 123.073 | 44.4049 | -123.1051 | 122.8677 | 123.0638 | 122.9022 | 44.8658 | -123.365
1467.7969 | 123.1888 | -64.2197 | 58.7082 | 0.0018314 | -0.0054166 | 0.003812 | 0.05772 | 0.0024337 | 0.069633 | 0.0058755 | 0.010505 | 0.0055936 | 0.061016 | 0.027677 | 0.069542 | -54.8847 | -19.9292 | -57.0263 | 58.6601 | 58.6014 | 58.7664 | -64.4015 | -51.5598 | -19.4683 | -54.0714 | 58.5702 | 58.7663 | 58.623 | -64.6522 | -0.18186 | -0.04812 | 9.335 | 7.1934 | 7.3752 | -0.10676 | 0.058202 | -0.43254 | -0.13799 | 12.6599 | 10.1483 | 10.5808 | 0.058143 | -0.085171 | 122.8797 | 122.8211 | 122.9861 | 44.2904 | -123.1097 | 122.7899 | 122.986 | 122.8427 | 44.7514 | -123.3604
1468.7969 | 123.1018 | -64.2471 | 58.754 | -0.0057996 | -0.0056302 | 0.0035984 | 0.05772 | 0.0015789 | 0.07006 | -0.001755 | 0.010077 | 0.0058072 | 0.06187 | 0.028104 | 0.069542 | -54.8068 | -19.9613 | -56.9393 | 58.6784 | 58.6014 | 58.7847 | -64.3832 | -51.482 | -19.4729 | -53.9844 | 58.5885 | 58.7801 | 58.6368 | -64.6568 | -0.13608 | -0.075583 | 9.4403 | 7.3078 | 7.4439 | -0.15253 | 0.03074 | -0.40966 | -0.16545 | 12.7652 | 10.2627 | 10.6724 | 0.026103 | -0.11721 | 122.9255 | 122.8486 | 123.0318 | 44.2858 | -123.1372 | 122.8357 | 123.0272 | 122.8839 | 44.7742 | -123.4108
1469.7969 | 123.0927 | -64.1876 | 58.8455 | 0.0018314 | -0.005203 | 0.0035984 | 0.05772 | 0.0022199 | 0.069419 | -0.001755 | 0.0098637 | 0.0062346 | 0.061229 | 0.027891 | 0.069756 | -54.6832 | -19.9476 | -56.8066 | 58.7608 | 58.6701 | 58.8625 | -64.3191 | -51.3354 | -19.4088 | -53.8379 | 58.6618 | 58.8579 | 58.7237 | -64.5835 | -0.13148 | -0.084725 | 9.5044 | 7.3811 | 7.5125 | -0.1754 | 0.017023 | -0.39591 | -0.18375 | 12.8522 | 10.3497 | 10.7457 | 0.012386 | -0.12177 | 122.9484 | 122.8577 | 123.0502 | 44.2401 | -123.1646 | 122.8494 | 123.0455 | 122.9114 | 44.7788 | -123.429
1470.7969 | 123.111 | -64.2059 | 58.7769 | -0.0057996 | -0.005203 | 0.0035984 | 0.05772 | 0.0022199 | 0.070274 | 0.0058755 | 0.010077 | 0.006021 | 0.061443 | 0.027891 | 0.069969 | -54.6512 | -19.9979 | -56.7745 | 58.7242 | 58.6472 | 58.8305 | -64.3466 | -51.3034 | -19.4134 | -53.815 | 58.6251 | 58.8259 | 58.6505 | -64.6064 | -0.14065 | -0.052687 | 9.5548 | 7.4314 | 7.5721 | -0.12963 | 0.053638 | -0.40049 | -0.15171 | 12.9025 | 10.391 | 10.7914 | 0.049001 | -0.12636 | 122.9301 | 122.8532 | 123.0364 | 44.208 | -123.1234 | 122.8311 | 123.0318 | 122.8564 | 44.7926 | -123.3833
1471.7969 | 123.1155 | -64.1876 | 58.8181 | 0.0018314 | -0.0047756 | 0.0035984 | 0.057506 | 0.0022199 | 0.069846 | -0.001755 | 0.010718 | 0.0055936 | 0.061657 | 0.027891 | 0.069542 | -54.5596 | -20.0117 | -56.6829 | 58.7562 | 58.6747 | 58.8671 | -64.3099 | -51.2301 | -19.3859 | -53.7188 | 58.6618 | 58.8579 | 58.6963 | -64.5789 | -0.12233 | -0.061837 | 9.628 | 7.5047 | 7.627 | -0.14336 | 0.049068 | -0.39133 | -0.15628 | 12.9575 | 10.4688 | 10.8601 | 0.039852 | -0.12178 | 122.9438 | 122.8623 | 123.0547 | 44.176 | -123.128 | 122.8494 | 123.0455 | 122.8839 | 44.8017 | -123.397
1472.7969 | 123.111 | -64.1052 | 58.8547 | 0.0018314 | -0.005203 | 0.0033846 | 0.057934 | 0.0022199 | 0.069846 | -0.001755 | 0.010505 | 0.006021 | 0.061443 | 0.027891 | 0.069969 | -54.436 | -19.9979 | -56.596 | 58.8157 | 58.7342 | 58.9312 | -64.2504 | -51.0974 | -19.3538 | -53.586 | 58.7305 | 58.9174 | 58.7421 | -64.5103 | -0.1452 | -0.038939 | 9.6692 | 7.5093 | 7.6545 | -0.12045 | 0.076547 | -0.40504 | -0.12422 | 13.0079 | 10.5192 | 10.9242 | 0.062753 | -0.11261 | 122.921 | 122.8394 | 123.0364 | 44.1073 | -123.1051 | 122.8357 | 123.0227 | 122.8473 | 44.7514 | -123.3649
1473.7969 | 123.0743 | -64.1098 | 58.8867 | 0.0094624 | -0.005203 | 0.0033846 | 0.057506 | 0.0022199 | 0.07006 | 0.0058755 | 0.010291 | 0.0058072 | 0.061443 | 0.027891 | 0.069969 | -54.3398 | -20.0254 | -56.4952 | 58.8569 | 58.7663 | 58.9724 | -64.2138 | -50.992 | -19.331 | -53.4991 | 58.7625 | 58.9586 | 58.8199 | -64.4736 | -0.10399 | -0.029778 | 9.77 | 7.6146 | 7.7186 | -0.12044 | 0.085711 | -0.36383 | -0.12422 | 13.1178 | 10.6107 | 10.9746 | 0.071916 | -0.066819 | 122.9667 | 122.8761 | 123.0822 | 44.0844 | -123.1005 | 122.8723 | 123.0684 | 122.9297 | 44.7788 | -123.3604
1474.7969 | 123.1247 | -64.0823 | 58.8867 | 0.0094624 | -0.0049892 | 0.0035984 | 0.05772 | 0.0024337 | 0.070274 | -0.0093855 | 0.010718 | 0.0058072 | 0.061443 | 0.027891 | 0.070183 | -54.3078 | -20.0803 | -56.4632 | 58.834 | 58.7434 | 58.9495 | -64.2413 | -50.9554 | -19.3905 | -53.4578 | 58.7442 | 58.9312 | 58.797 | -64.492 | -0.15893 | -0.05267 | 9.7745 | 7.6191 | 7.7781 | -0.14334 | 0.062818 | -0.40962 | -0.14253 | 13.1269 | 10.6245 | 11.0341 | 0.044445 | -0.089712 | 122.9164 | 122.8257 | 123.0319 | 44.002 | -123.128 | 122.8265 | 123.0135 | 122.8793 | 44.6919 | -123.3787
1475.7969 | 123.1384 | -64.0869 | 58.8959 | 0.0018314 | -0.0049892 | 0.0033846 | 0.058361 | 0.0024337 | 0.07006 | -0.001755 | 0.010505 | 0.0064482 | 0.061443 | 0.027677 | 0.069969 | -54.2483 | -20.1124 | -56.4037 | 58.8386 | 58.7525 | 58.9541 | -64.2275 | -50.8959 | -19.3676 | -53.3983 | 58.7488 | 58.9312 | 58.8062 | -64.4874 | -0.14061 | -0.057246 | 9.8386 | 7.6832 | 7.8239 | -0.14333 | 0.058241 | -0.40046 | -0.14711 | 13.191 | 10.6886 | 11.0891 | 0.03529 | -0.08971 | 122.9255 | 122.8395 | 123.041 | 43.9745 | -123.1234 | 122.8357 | 123.0181 | 122.8931 | 44.7193 | -123.3832
1476.7969 | 123.1018 | -64.0457 | 58.9874 | -0.013431 | -0.004562 | 0.0033846 | 0.057934 | 0.0024337 | 0.070487 | -0.017016 | 0.011145 | 0.0058072 | 0.061657 | 0.028104 | 0.069969 | -54.1384 | -20.0849 | -56.2938 | 58.889 | 58.8121 | 59.0045 | -64.1817 | -50.7677 | -19.3401 | -53.2793 | 58.7991 | 58.9907 | 58.8474 | -64.437 | -0.13602 | -0.098437 | 9.9073 | 7.7519 | 7.8879 | -0.17536 | 0.017053 | -0.39129 | -0.1883 | 13.278 | 10.7664 | 11.1577 | 0.003259 | -0.14005 | 122.9347 | 122.8578 | 123.0502 | 43.9608 | -123.1692 | 122.8448 | 123.0364 | 122.8931 | 44.7056 | -123.4244
1477.7969 | 123.1018 | -64.0549 | 58.9188 | 0.0018314 | -0.004562 | 0.0035984 | 0.058147 | 0.0028609 | 0.070274 | -0.001755 | 0.010932 | 0.006021 | 0.061229 | 0.028104 | 0.070183 | -54.088 | -20.1216 | -56.2526 | 58.8798 | 58.7892 | 58.9953 | -64.1817 | -50.7127 | -19.3813 | -53.2335 | 58.7946 | 58.9907 | 58.8291 | -64.4507 | -0.12687 | -0.038929 | 9.9668 | 7.8023 | 7.9292 | -0.12959 | 0.076561 | -0.39587 | -0.12421 | 13.3421 | 10.8214 | 11.2173 | 0.071924 | -0.089705 | 122.9347 | 122.844 | 123.0502 | 43.9333 | -123.1005 | 122.8494 | 123.0456 | 122.8839 | 44.6736 | -123.3695
1478.7969 | 123.1064 | -63.9999 | 59.0149 | 0.0018314 | -0.004562 | 0.0035984 | 0.058147 | 0.0028609 | 0.070487 | -0.001755 | 0.010718 | 0.0062346 | 0.06187 | 0.028318 | 0.070183 | -53.9415 | -20.0712 | -56.1015 | 58.9714 | 58.8853 | 59.0823 | -64.0902 | -50.5662 | -19.2806 | -53.087 | 58.8861 | 59.0868 | 58.8474 | -64.3592 | -0.09022 | -0.043492 | 10.0584 | 7.8984 | 7.9887 | -0.12956 | 0.067423 | -0.35923 | -0.12877 | 13.4337 | 10.913 | 11.2722 | 0.071943 | -0.16752 | 122.9713 | 122.8853 | 123.0823 | 43.9288 | -123.1051 | 122.8861 | 123.0868 | 122.8473 | 44.7194 | -123.3741
1479.7969 | 123.0972 | -63.7711 | 59.2255 | -0.013431 | -0.0047756 | 0.0035984 | 0.058147 | 0.0026473 | 0.07006 | 0.0058755 | 0.010932 | 0.0062346 | 0.061443 | 0.028318 | 0.07061 | -53.708 | -19.9613 | -55.8817 | 59.1454 | 59.0593 | 59.2517 | -63.9207 | -50.3281 | -19.1203 | -52.858 | 59.0464 | 59.2425 | 59.0855 | -64.176 | -0.14968 | -0.080084 | 10.063 | 7.8893 | 8.039 | -0.16614 | 0.02626 | -0.40496 | -0.1791 | 13.4429 | 10.913 | 11.318 | 0.017045 | -0.14001 | 122.9164 | 122.8304 | 123.0228 | 43.8098 | -123.1462 | 122.8174 | 123.0136 | 122.8565 | 44.6507 | -123.4015
1480.7969 | 123.0743 | -63.8489 | 59.1614 | 0.0094624 | -0.0047756 | 0.0035984 | 0.058147 | 0.0030747 | 0.070487 | -0.001755 | 0.011145 | 0.006021 | 0.061657 | 0.028318 | 0.069969 | -53.6668 | -20.0162 | -55.836 | 59.1133 | 59.0273 | 59.2243 | -63.9528 | -50.2549 | -19.1249 | -52.8077 | 59.0281 | 59.2196 | 58.9847 | -64.2081 | -0.10391 | -0.048046 | 10.1821 | 8.0129 | 8.1168 | -0.1341 | 0.062876 | -0.35919 | -0.13332 | 13.594 | 11.0412 | 11.4004 | 0.058239 | -0.17665 | 122.9622 | 122.8762 | 123.0731 | 43.8326 | -123.1142 | 122.8769 | 123.0685 | 122.8336 | 44.724 | -123.3694
1481.7969 | 123.1018 | -63.7711 | 59.2072 | -0.013431 | -0.004562 | 0.003812 | 0.058147 | 0.0026473 | 0.070487 | -0.001755 | 0.010932 | 0.006021 | 0.061443 | 0.028318 | 0.070396 | -53.5569 | -19.9842 | -55.7261 | 59.1683 | 59.0914 | 59.2884 | -63.9024 | -50.1358 | -19.1158 | -52.7024 | 59.0738 | 59.27 | 59.09 | -64.1577 | -0.13137 | -0.038881 | 10.2141 | 8.045 | 8.1763 | -0.11577 | 0.0812 | -0.38664 | -0.13331 | 13.6352 | 11.0687 | 11.4553 | 0.062827 | -0.11711 | 122.9393 | 122.8624 | 123.0594 | 43.7869 | -123.1096 | 122.8449 | 123.041 | 122.8611 | 44.6553 | -123.3649
1482.7969 | 123.143 | -63.7299 | 59.2255 | -0.0057996 | -0.004562 | 0.003812 | 0.057934 | 0.0028609 | 0.070487 | 0.0058755 | 0.011573 | 0.006021 | 0.061657 | 0.028532 | 0.07061 | -53.4837 | -19.9659 | -55.6391 | 59.1957 | 59.1189 | 59.3112 | -63.8566 | -50.0214 | -19.0562 | -52.6016 | 59.1059 | 59.3066 | 59.1221 | -64.1256 | -0.12678 | -0.029722 | 10.2462 | 8.0908 | 8.2175 | -0.10661 | 0.085782 | -0.39579 | -0.11958 | 13.7085 | 11.1282 | 11.524 | 0.081145 | -0.10338 | 122.9256 | 122.8487 | 123.0411 | 43.764 | -123.0821 | 122.8357 | 123.0365 | 122.8519 | 44.6736 | -123.3511
1483.7969 | 123.0652 | -63.6337 | 59.3399 | -0.0057996 | -0.0041346 | 0.003812 | 0.058147 | 0.0028609 | 0.070701 | 0.0058755 | 0.011359 | 0.0064482 | 0.061657 | 0.028532 | 0.070824 | -53.2822 | -19.8606 | -55.4331 | 59.3468 | 59.2562 | 59.4623 | -63.7147 | -49.797 | -18.9051 | -52.3956 | 59.257 | 59.4577 | 59.2961 | -63.9745 | -0.080959 | 0.006924 | 10.3515 | 8.2007 | 8.2816 | -0.083684 | 0.12243 | -0.34082 | -0.082925 | 13.8367 | 11.2381 | 11.579 | 0.1178 | -0.04383 | 122.9806 | 122.8899 | 123.0961 | 43.7732 | -123.0546 | 122.8907 | 123.0914 | 122.9298 | 44.7286 | -123.3144
1484.7969 | 123.2025 | -63.6292 | 59.2987 | -0.0057996 | -0.004562 | 0.0035984 | 0.058361 | 0.0026473 | 0.070487 | 0.0058755 | 0.011573 | 0.0062346 | 0.061657 | 0.028532 | 0.071037 | -53.2685 | -19.9247 | -55.4056 | 59.3102 | 59.215 | 59.4211 | -63.7467 | -49.7787 | -18.9555 | -52.3681 | 59.2204 | 59.4165 | 59.2045 | -64.002 | -0.11759 | 0.011496 | 10.3607 | 8.2235 | 8.3411 | -0.083695 | 0.12243 | -0.37287 | -0.078354 | 13.8505 | 11.261 | 11.6339 | 0.11779 | -0.094203 | 122.9394 | 122.8442 | 123.0503 | 43.7045 | -123.0454 | 122.8495 | 123.0456 | 122.8337 | 44.6737 | -123.3007
1485.7969 | 123.0972 | -63.5605 | 59.4223 | -0.013431 | -0.0043482 | 0.003812 | 0.058789 | 0.0030747 | 0.070915 | -0.001755 | 0.010932 | 0.006021 | 0.06187 | 0.028318 | 0.071037 | -53.1449 | -19.8926 | -55.2728 | 59.3789 | 59.2883 | 59.4898 | -63.6735 | -49.6459 | -18.9006 | -52.2353 | 59.2982 | 59.4852 | 59.2915 | -63.9425 | -0.11299 | -0.043424 | 10.4156 | 8.2877 | 8.4006 | -0.13403 | 0.06751 | -0.38201 | -0.12412 | 13.9146 | 11.3252 | 11.7072 | 0.062873 | -0.13081 | 122.9394 | 122.8488 | 123.0503 | 43.6679 | -123.0958 | 122.8587 | 123.0457 | 122.852 | 44.6599 | -123.3648
1486.7969 | 123.2025 | -63.5605 | 59.3308 | 0.0094624 | -0.0041346 | 0.0035984 | 0.058575 | 0.0030747 | 0.070915 | -0.0093855 | 0.011359 | 0.0064482 | 0.061657 | 0.028532 | 0.071037 | -53.1083 | -19.943 | -55.2591 | 59.356 | 59.2516 | 59.4715 | -63.7101 | -49.6322 | -18.9601 | -52.2033 | 59.2524 | 59.4485 | 59.2869 | -63.9745 | -0.14962 | 0.025236 | 10.4522 | 8.3014 | 8.451 | -0.079107 | 0.14075 | -0.41406 | -0.078349 | 13.9283 | 11.3572 | 11.7713 | 0.1178 | -0.043833 | 122.9165 | 122.8121 | 123.032 | 43.6175 | -123.0409 | 122.8129 | 123.009 | 122.8474 | 44.6004 | -123.3053
1487.7969 | 123.0743 | -63.5651 | 59.3948 | -0.013431 | -0.0043482 | 0.003812 | 0.057934 | 0.0024337 | 0.071128 | -0.0093855 | 0.011573 | 0.0064482 | 0.062084 | 0.028745 | 0.071465 | -53.0258 | -19.975 | -55.1858 | 59.3606 | 59.2608 | 59.4669 | -63.7055 | -49.5635 | -18.9876 | -52.2124 | 59.2616 | 59.4577 | 59.3144 | -63.9745 | -0.14047 | -0.034272 | 10.5392 | 8.3792 | 8.5197 | -0.13404 | 0.072083 | -0.40948 | -0.13328 | 14.0016 | 11.3526 | 11.7621 | 0.062867 | -0.080447 | 122.9256 | 122.8259 | 123.032 | 43.59 | -123.1004 | 122.8266 | 123.0228 | 122.8795 | 44.5775 | -123.3694
1488.7969 | 123.1934 | -63.5559 | 59.3719 | 0.0018314 | -0.0041346 | 0.0040256 | 0.058361 | 0.0035019 | 0.071128 | -0.001755 | 0.011359 | 0.0064482 | 0.061443 | 0.028745 | 0.071251 | -52.9617 | -19.9796 | -55.1172 | 59.3743 | 59.2837 | 59.4898 | -63.6872 | -49.4719 | -18.9647 | -52.13 | 59.289 | 59.4852 | 59.3327 | -63.9471 | -0.13131 | 0.002351 | 10.5942 | 8.4387 | 8.57 | -0.088253 | 0.11786 | -0.39116 | -0.082919 | 14.084 | 11.4259 | 11.8171 | 0.11323 | -0.039245 | 122.9302 | 122.8396 | 123.0457 | 43.5763 | -123.0592 | 122.8449 | 123.0411 | 122.8886 | 44.5913 | -123.319
1489.7969 | 123.1384 | -63.6063 | 59.3811 | -0.0057996 | -0.0043482 | 0.003812 | 0.058147 | 0.0030747 | 0.071128 | -0.0093855 | 0.011786 | 0.0066618 | 0.06187 | 0.028745 | 0.071037 | -52.948 | -20.0529 | -55.1126 | 59.3239 | 59.2379 | 59.4394 | -63.7376 | -49.4582 | -19.0196 | -52.1254 | 59.2249 | 59.4302 | 59.2869 | -63.9974 | -0.13132 | -0.057167 | 10.6583 | 8.4937 | 8.625 | -0.1432 | 0.058343 | -0.39118 | -0.15617 | 14.1481 | 11.4808 | 11.872 | 0.049127 | -0.094187 | 122.9302 | 122.8442 | 123.0457 | 43.5534 | -123.1187 | 122.8312 | 123.0365 | 122.8932 | 44.5867 | -123.3785
1490.7969 | 123.1796 | -63.5513 | 59.404 | -0.0057996 | -0.0043482 | 0.0040256 | 0.058575 | 0.0028609 | 0.071128 | -0.001755 | 0.012 | 0.006021 | 0.061657 | 0.028959 | 0.071465 | -52.8519 | -20.0391 | -55.0256 | 59.356 | 59.2654 | 59.4623 | -63.7055 | -49.3529 | -18.9692 | -52.0705 | 59.2661 | 59.4577 | 59.2457 | -63.97 | -0.1542 | -0.048006 | 10.6995 | 8.5257 | 8.6799 | -0.13861 | 0.058348 | -0.41864 | -0.13786 | 14.1985 | 11.4808 | 11.8995 | 0.053711 | -0.15828 | 122.9073 | 122.8167 | 123.0137 | 43.5122 | -123.1095 | 122.8175 | 123.009 | 122.797 | 44.5821 | -123.374
1491.7969 | 123.1888 | -63.4827 | 59.4177 | -0.013431 | -0.0041346 | 0.003812 | 0.058361 | 0.0030747 | 0.071128 | 0.0058755 | 0.012 | 0.0064482 | 0.06187 | 0.028959 | 0.071251 | -52.7466 | -20.0346 | -54.9249 | 59.4109 | 59.3203 | 59.5173 | -63.6552 | -49.2338 | -18.8639 | -51.9469 | 59.3165 | 59.4989 | 59.3464 | -63.915 | -0.17249 | -0.006799 | 10.7361 | 8.5578 | 8.7303 | -0.097399 | 0.099558 | -0.43236 | -0.10122 | 14.2488 | 11.5358 | 11.9682 | 0.081185 | -0.071286 | 122.8936 | 122.803 | 122.9999 | 43.4481 | -123.0729 | 122.7992 | 122.9816 | 122.8291 | 44.6187 | -123.3327
1492.7969 | 123.1613 | -63.2538 | 59.6329 | 0.0094624 | -0.003921 | 0.0040256 | 0.058789 | 0.0030747 | 0.071128 | -0.001755 | 0.011786 | 0.0066618 | 0.061443 | 0.029173 | 0.071037 | -52.5039 | -19.888 | -54.6822 | 59.5803 | 59.4943 | 59.6913 | -63.4812 | -49.014 | -18.7449 | -51.7362 | 59.4859 | 59.6821 | 59.5525 | -63.741 | -0.22738 | -0.052547 | 10.7499 | 8.5715 | 8.7989 | -0.13855 | 0.058396 | -0.48724 | -0.14697 | 14.2397 | 11.5175 | 12.0048 | 0.049181 | -0.080398 | 122.8341 | 122.7481 | 122.9451 | 43.3657 | -123.114 | 122.7397 | 122.9358 | 122.8063 | 44.5089 | -123.3739
1493.7969 | 123.2025 | -63.3408 | 59.5871 | -0.013431 | -0.0041346 | 0.0040256 | 0.058361 | 0.0030747 | 0.071128 | 0.0058755 | 0.011786 | 0.0066618 | 0.061657 | 0.029173 | 0.071465 | -52.4581 | -19.9155 | -54.6365 | 59.5849 | 59.4897 | 59.6913 | -63.4857 | -48.9637 | -18.7678 | -51.6905 | 59.4813 | 59.6775 | 59.4563 | -63.7364 | -0.14498 | -0.002192 | 10.8826 | 8.7043 | 8.8493 | -0.09735 | 0.10417 | -0.39569 | -0.10577 | 14.3771 | 11.6503 | 12.046 | 0.090379 | -0.13077 | 122.9257 | 122.8305 | 123.032 | 43.4252 | -123.0728 | 122.8221 | 123.0182 | 122.7971 | 44.573 | -123.3235
1494.7969 | 123.1888 | -63.4048 | 59.523 | 0.0094624 | -0.0041346 | 0.0042394 | 0.058575 | 0.0032883 | 0.071556 | -0.0093855 | 0.012 | 0.0064482 | 0.061657 | 0.029386 | 0.071892 | -52.3986 | -19.9384 | -54.5952 | 59.5666 | 59.4669 | 59.6775 | -63.4949 | -48.9225 | -18.7357 | -51.6447 | 59.4722 | 59.6637 | 59.5021 | -63.7639 | -0.090053 | 0.043581 | 11.0062 | 8.8096 | 8.8997 | -0.056158 | 0.15452 | -0.35907 | -0.050841 | 14.4824 | 11.7602 | 12.1192 | 0.14073 | -0.020898 | 122.9714 | 122.8717 | 123.0824 | 43.4664 | -123.0179 | 122.877 | 123.0686 | 122.907 | 44.6691 | -123.2869
1495.7969 | 123.2025 | -63.3179 | 59.5963 | 0.0018314 | -0.0041346 | 0.0040256 | 0.058361 | 0.0035019 | 0.071128 | 0.0058755 | 0.012 | 0.006021 | 0.061657 | 0.029386 | 0.071892 | -52.3116 | -19.9476 | -54.522 | 59.5941 | 59.5081 | 59.7004 | -63.4674 | -48.8355 | -18.7449 | -51.5485 | 59.4996 | 59.7004 | 59.5433 | -63.7273 | -0.14955 | -0.00219 | 11.0063 | 8.7959 | 8.9454 | -0.08819 | 0.10418 | -0.40942 | -0.096612 | 14.4824 | 11.7693 | 12.1788 | 0.10412 | -0.052933 | 122.9119 | 122.8259 | 123.0183 | 43.3703 | -123.0637 | 122.8175 | 123.0182 | 122.8612 | 44.573 | -123.3235
1496.7969 | 123.1567 | -63.4232 | 59.5047 | 0.0094624 | -0.0037072 | 0.003812 | 0.058789 | 0.0035019 | 0.071769 | -0.001755 | 0.012 | 0.0068756 | 0.06187 | 0.029386 | 0.071678 | -52.3574 | -20.0483 | -54.5724 | 59.4933 | 59.4165 | 59.6089 | -63.5727 | -48.8813 | -18.809 | -51.5897 | 59.3989 | 59.5996 | 59.438 | -63.8326 | -0.14958 | -0.011363 | 11.0658 | 8.8508 | 9.0004 | -0.088216 | 0.10415 | -0.40944 | -0.10579 | 14.5419 | 11.8334 | 12.2429 | 0.09494 | -0.066689 | 122.9165 | 122.8396 | 123.032 | 43.3749 | -123.0774 | 122.8221 | 123.0228 | 122.8612 | 44.6142 | -123.3373
1497.7969 | 123.1522 | -63.4277 | 59.4818 | 0.0018314 | -0.0034936 | 0.0040256 | 0.058147 | 0.0030747 | 0.071128 | -0.001755 | 0.012214 | 0.0062346 | 0.06187 | 0.029173 | 0.071465 | -52.3208 | -20.117 | -54.5357 | 59.4613 | 59.3707 | 59.5814 | -63.5956 | -48.8217 | -18.8365 | -51.5531 | 59.376 | 59.5676 | 59.4151 | -63.8509 | -0.1679 | -0.020523 | 11.107 | 8.892 | 9.0599 | -0.11112 | 0.099572 | -0.42318 | -0.10579 | 14.606 | 11.8746 | 12.2978 | 0.085777 | -0.066694 | 122.889 | 122.7984 | 123.0091 | 43.3108 | -123.0774 | 122.8038 | 122.9953 | 122.8429 | 44.5913 | -123.3327
1498.7969 | 123.1796 | -63.4598 | 59.4864 | -0.0057996 | -0.0032798 | 0.003812 | 0.058575 | 0.0032883 | 0.071556 | 0.0058755 | 0.012427 | 0.0066618 | 0.06187 | 0.029173 | 0.071892 | -52.2887 | -20.149 | -54.5083 | 59.4338 | 59.3432 | 59.5402 | -63.614 | -48.7943 | -18.8456 | -51.5119 | 59.344 | 59.5401 | 59.3968 | -63.8875 | -0.15417 | -0.052571 | 11.1711 | 8.9515 | 9.1057 | -0.14317 | 0.053787 | -0.42777 | -0.14242 | 14.6655 | 11.9479 | 12.3757 | 0.053729 | -0.089585 | 122.8936 | 122.803 | 123 | 43.3108 | -123.1003 | 122.8037 | 122.9999 | 122.8566 | 44.6142 | -123.3739
1499.7969 | 123.1705 | -63.3408 | 59.5642 | -0.0057996 | -0.0034936 | 0.004453 | 0.058361 | 0.0032883 | 0.071983 | -0.001755 | 0.012214 | 0.0066618 | 0.062084 | 0.029386 | 0.072106 | -52.1468 | -20.0895 | -54.3663 | 59.53 | 59.4348 | 59.6272 | -63.5224 | -48.6432 | -18.7128 | -51.3608 | 59.431 | 59.6317 | 59.438 | -63.796 | -0.18161 | -0.034245 | 11.194 | 8.9744 | 9.156 | -0.12941 | 0.062961 | -0.45521 | -0.13325 | 14.6976 | 11.98 | 12.4352 | 0.067481 | -0.1262 | 122.8707 | 122.7756 | 122.9679 | 43.2513 | -123.0866 | 122.7717 | 122.9724 | 122.7788 | 44.6279 | -123.3602
1500.7969 | 123.1613 | -63.3316 | 59.5871 | -0.0057996 | -0.0034936 | 0.0042394 | 0.058575 | 0.0035019 | 0.071769 | -0.001755 | 0.012427 | 0.0066618 | 0.06187 | 0.029386 | 0.071892 | -52.0919 | -20.1261 | -54.3068 | 59.5162 | 59.4256 | 59.6226 | -63.5407 | -48.6157 | -18.7311 | -51.3013 | 59.4264 | 59.6317 | 59.4243 | -63.8051 | -0.20908 | -0.070868 | 11.2398 | 9.0248 | 9.2339 | -0.16145 | 0.035494 | -0.47353 | -0.16071 | 14.7159 | 12.0303 | 12.5039 | 0.044593 | -0.16282 | 122.8478 | 122.7572 | 122.9542 | 43.2055 | -123.1278 | 122.758 | 122.9633 | 122.7559 | 44.6005 | -123.3922
1501.7969 | 123.2117 | -63.414 | 59.5001 | -0.0057996 | -0.003921 | 0.0042394 | 0.059002 | 0.0041429 | 0.071556 | -0.017016 | 0.012855 | 0.0066618 | 0.061657 | 0.029173 | 0.071892 | -52.0461 | -20.1628 | -54.261 | 59.4933 | 59.4027 | 59.6089 | -63.559 | -48.5699 | -18.754 | -51.2646 | 59.3989 | 59.5951 | 59.4243 | -63.8326 | -0.145 | -0.006785 | 11.3679 | 9.153 | 9.298 | -0.097375 | 0.10873 | -0.4186 | -0.10121 | 14.8441 | 12.1494 | 12.568 | 0.094939 | -0.075846 | 122.9073 | 122.8167 | 123.0229 | 43.2512 | -123.0591 | 122.8129 | 123.0091 | 122.8383 | 44.66 | -123.3327
1502.7969 | 123.1522 | -63.3865 | 59.5642 | -0.0057996 | -0.0034936 | 0.0042394 | 0.058789 | 0.0035019 | 0.071769 | -0.001755 | 0.012427 | 0.0068756 | 0.062298 | 0.0296 | 0.071892 | -51.9591 | -20.1765 | -54.1832 | 59.5071 | 59.4256 | 59.618 | -63.5498 | -48.5104 | -18.7128 | -51.1868 | 59.4218 | 59.618 | 59.3922 | -63.8097 | -0.16331 | -0.057137 | 11.4275 | 9.2033 | 9.3666 | -0.13857 | 0.053804 | -0.42317 | -0.1424 | 14.8762 | 12.1997 | 12.6229 | 0.053745 | -0.17198 | 122.8936 | 122.8122 | 123.0045 | 43.21 | -123.1141 | 122.8083 | 123.0045 | 122.7788 | 44.6737 | -123.3739
1503.7969 | 123.1796 | -63.414 | 59.5413 | 0.0018314 | -0.003921 | 0.0042394 | 0.058789 | 0.0039293 | 0.071983 | 0.0058755 | 0.012641 | 0.0064482 | 0.062298 | 0.029173 | 0.071892 | -51.9224 | -20.2269 | -54.1466 | 59.475 | 59.389 | 59.5814 | -63.5819 | -48.4692 | -18.6716 | -51.1593 | 59.3852 | 59.5813 | 59.3831 | -63.8463 | -0.1679 | -0.066297 | 11.4916 | 9.2674 | 9.4353 | -0.15231 | 0.040063 | -0.43234 | -0.15614 | 14.9448 | 12.2547 | 12.687 | 0.040004 | -0.15825 | 122.889 | 122.803 | 122.9954 | 43.1871 | -123.1232 | 122.7992 | 122.9953 | 122.7971 | 44.7424 | -123.3877
1504.7969 | 123.2162 | -63.2538 | 59.6878 | 0.0018314 | -0.0034936 | 0.0040256 | 0.058789 | 0.0037157 | 0.071983 | -0.001755 | 0.012427 | 0.0068756 | 0.06187 | 0.0296 | 0.072319 | -51.7302 | -20.0987 | -53.9497 | 59.6215 | 59.5218 | 59.7279 | -63.4354 | -48.2814 | -18.5755 | -50.9441 | 59.5317 | 59.7187 | 59.4975 | -63.7044 | -0.18159 | -0.066273 | 11.5236 | 9.3041 | 9.4857 | -0.16601 | 0.040094 | -0.45061 | -0.15611 | 14.9723 | 12.3097 | 12.7603 | 0.030878 | -0.19027 | 122.8753 | 122.7756 | 122.9817 | 43.1551 | -123.1232 | 122.7855 | 122.9725 | 122.7513 | 44.6783 | -123.3922
1505.7969 | 123.1934 | -63.414 | 59.523 | 0.0018314 | -0.0037072 | 0.0040256 | 0.059002 | 0.0037157 | 0.072624 | 0.0058755 | 0.012641 | 0.0068756 | 0.062084 | 0.0296 | 0.072106 | -51.7943 | -20.2589 | -54.0092 | 59.4888 | 59.3982 | 59.6134 | -63.559 | -48.3227 | -18.6854 | -51.0311 | 59.4081 | 59.5996 | 59.4517 | -63.8189 | -0.145 | -0.034251 | 11.6197 | 9.4048 | 9.5498 | -0.12484 | 0.090424 | -0.40486 | -0.11494 | 15.0913 | 12.3829 | 12.7877 | 0.07663 | -0.071263 | 122.9028 | 122.8122 | 123.0274 | 43.1551 | -123.082 | 122.8221 | 123.0136 | 122.8657 | 44.7286 | -123.3419
1506.7969 | 123.2071 | -63.3133 | 59.5963 | 0.017093 | -0.0034936 | 0.0040256 | 0.059216 | 0.0037157 | 0.071983 | -0.001755 | 0.012641 | 0.0070892 | 0.062084 | 0.0296 | 0.072106 | -51.6523 | -20.1857 | -53.8719 | 59.5803 | 59.4806 | 59.6867 | -63.472 | -48.2311 | -18.5526 | -50.8846 | 59.4859 | 59.6821 | 59.5342 | -63.7502 | -0.15871 | -0.015925 | 11.661 | 9.4414 | 9.6001 | -0.11566 | 0.09044 | -0.43689 | -0.11035 | 15.0822 | 12.4287 | 12.8656 | 0.085803 | -0.06209 | 122.8936 | 122.7939 | 123 | 43.1276 | -123.0683 | 122.7992 | 122.9953 | 122.8475 | 44.7607 | -123.3464
1507.7969 | 123.1705 | -63.3774 | 59.5596 | -0.013431 | -0.0034936 | 0.0040256 | 0.058789 | 0.0039293 | 0.071983 | -0.001755 | 0.012855 | 0.0068756 | 0.062298 | 0.029814 | 0.072319 | -51.6432 | -20.2543 | -53.8765 | 59.5162 | 59.4485 | 59.6363 | -63.5361 | -48.2219 | -18.5617 | -50.8709 | 59.431 | 59.6225 | 59.4838 | -63.8006 | -0.15873 | -0.043402 | 11.7342 | 9.5009 | 9.6597 | -0.1111 | 0.076696 | -0.42317 | -0.12867 | 15.1555 | 12.5065 | 12.9297 | 0.062902 | -0.075834 | 122.8936 | 122.8259 | 123.0137 | 43.123 | -123.0957 | 122.8083 | 122.9999 | 122.8612 | 44.8156 | -123.3602
1508.7969 | 123.0972 | -63.3316 | 59.6146 | 0.0018314 | -0.0034936 | 0.0040256 | 0.059002 | 0.0037157 | 0.07241 | -0.001755 | 0.012855 | 0.0068756 | 0.06187 | 0.029814 | 0.072319 | -51.5196 | -20.2498 | -53.7757 | 59.5757 | 59.4714 | 59.6867 | -63.4903 | -48.1395 | -18.5251 | -50.7747 | 59.4813 | 59.6683 | 59.4609 | -63.7593 | -0.15872 | -0.038815 | 11.8121 | 9.5559 | 9.7146 | -0.14313 | 0.072129 | -0.42774 | -0.13324 | 15.1921 | 12.5569 | 12.9846 | 0.053756 | -0.15366 | 122.9074 | 122.803 | 123.0183 | 43.0819 | -123.1049 | 122.8129 | 122.9999 | 122.7925 | 44.8065 | -123.3739
1509.7969 | 123.1842 | -63.2172 | 59.6786 | 0.0094624 | -0.0032798 | 0.004453 | 0.059216 | 0.0039293 | 0.07241 | 0.0058755 | 0.013068 | 0.0070892 | 0.062084 | 0.029814 | 0.072533 | -51.46 | -20.2543 | -53.6933 | 59.5757 | 59.4989 | 59.6913 | -63.4766 | -48.0571 | -18.4015 | -50.6877 | 59.4905 | 59.6729 | 59.493 | -63.7364 | -0.25942 | -0.1029 | 11.7571 | 9.5238 | 9.7833 | -0.17975 | 0.01262 | -0.51928 | -0.18817 | 15.1601 | 12.5294 | 13.0487 | -0.005753 | -0.18569 | 122.7929 | 122.7161 | 122.9084 | 42.9628 | -123.1552 | 122.7076 | 122.8901 | 122.7101 | 44.8157 | -123.4151
1510.7969 | 123.1659 | -63.2172 | 59.7198 | -0.0057996 | -0.0037072 | 0.004453 | 0.058575 | 0.0037157 | 0.07241 | 0.013506 | 0.013282 | 0.0070892 | 0.062298 | 0.029814 | 0.072747 | -51.2906 | -20.1582 | -53.5377 | 59.6856 | 59.6088 | 59.792 | -63.3667 | -47.9106 | -18.3511 | -50.5229 | 59.5912 | 59.7828 | 59.5983 | -63.6357 | -0.14953 | -0.034219 | 11.9265 | 9.6795 | 9.829 | -0.11105 | 0.072151 | -0.41855 | -0.12864 | 15.3066 | 12.6943 | 13.1128 | 0.062935 | -0.12159 | 122.9028 | 122.826 | 123.0092 | 43.059 | -123.0865 | 122.8084 | 122.9999 | 122.8154 | 44.8661 | -123.3556
1511.7969 | 123.2025 | -63.2858 | 59.6191 | 0.0094624 | -0.0032798 | 0.004453 | 0.058789 | 0.0039293 | 0.07241 | 0.0058755 | 0.013068 | 0.0066618 | 0.062298 | 0.030241 | 0.072533 | -51.3318 | -20.2681 | -53.5697 | 59.5757 | 59.5035 | 59.6867 | -63.4857 | -47.9793 | -18.4747 | -50.5733 | 59.4859 | 59.6729 | 59.5433 | -63.7502 | -0.19991 | -0.043393 | 11.954 | 9.7161 | 9.916 | -0.11566 | 0.067551 | -0.46435 | -0.13324 | 15.3066 | 12.7126 | 13.1769 | 0.053756 | -0.075822 | 122.8616 | 122.7893 | 122.9725 | 43.0178 | -123.1049 | 122.7717 | 122.9587 | 122.8291 | 44.8111 | -123.3693
1512.7969 | 123.1018 | -63.446 | 59.5871 | 0.0094624 | -0.0030662 | 0.0040256 | 0.058789 | 0.0039293 | 0.072838 | 0.0058755 | 0.013495 | 0.0066618 | 0.062725 | 0.030027 | 0.072533 | -51.3685 | -20.4054 | -53.6201 | 59.4567 | 59.3982 | 59.5768 | -63.5911 | -48.0434 | -18.5251 | -50.6099 | 59.376 | 59.563 | 59.3876 | -63.8555 | -0.14501 | -0.13039 | 12.0776 | 9.826 | 9.971 | -0.18893 | -0.010292 | -0.40945 | -0.21108 | 15.4027 | 12.8362 | 13.2456 | -0.024086 | -0.19945 | 122.9028 | 122.8442 | 123.0229 | 43.0406 | -123.1782 | 122.8221 | 123.0091 | 122.8337 | 44.9209 | -123.4426
1513.7969 | 123.2071 | -63.3774 | 59.5322 | 0.0018314 | -0.0028526 | 0.0048804 | 0.058789 | 0.0037157 | 0.07241 | 0.0058755 | 0.013282 | 0.0070892 | 0.062084 | 0.030241 | 0.072533 | -51.3044 | -20.4192 | -53.5606 | 59.4704 | 59.3982 | 59.5814 | -63.5911 | -47.9793 | -18.5434 | -50.5687 | 59.3714 | 59.563 | 59.4151 | -63.8463 | -0.21368 | -0.061721 | 12.073 | 9.8168 | 10.0305 | -0.134 | 0.049218 | -0.46896 | -0.16072 | 15.3981 | 12.8087 | 13.2777 | 0.030845 | -0.11705 | 122.8478 | 122.7755 | 122.9588 | 42.9582 | -123.1232 | 122.7488 | 122.9404 | 122.7925 | 44.834 | -123.3785
1514.7969 | 123.0652 | -63.5834 | 59.3994 | 0.0018314 | -0.0030662 | 0.0042394 | 0.058361 | 0.0041429 | 0.073051 | 0.0058755 | 0.013282 | 0.0066618 | 0.062511 | 0.030455 | 0.072533 | -51.3776 | -20.5703 | -53.6155 | 59.3285 | 59.2562 | 59.444 | -63.7147 | -48.0617 | -18.6258 | -50.6099 | 59.2432 | 59.4302 | 59.1999 | -63.9929 | -0.13131 | -0.070899 | 12.2058 | 9.9679 | 10.0992 | -0.14319 | 0.044612 | -0.40949 | -0.15617 | 15.5217 | 12.9735 | 13.383 | 0.030817 | -0.19949 | 122.9119 | 122.8396 | 123.0274 | 43.0131 | -123.1141 | 122.8266 | 123.0136 | 122.7833 | 44.9575 | -123.3923
1515.7969 | 123.1705 | -63.5239 | 59.404 | 0.0094624 | -0.0030662 | 0.004453 | 0.059002 | 0.0041429 | 0.072624 | 0.013506 | 0.013495 | 0.0068756 | 0.062084 | 0.030027 | 0.072747 | -51.2723 | -20.529 | -53.5148 | 59.3789 | 59.2929 | 59.4944 | -63.6689 | -47.9609 | -18.5617 | -50.4954 | 59.2845 | 59.476 | 59.3235 | -63.9333 | -0.14503 | -0.025114 | 12.2515 | 10.0091 | 10.1541 | -0.11114 | 0.090398 | -0.40947 | -0.11954 | 15.5629 | 13.0284 | 13.4379 | 0.072025 | -0.080446 | 122.9027 | 122.8167 | 123.0183 | 42.9948 | -123.0729 | 122.8083 | 122.9999 | 122.8474 | 44.9621 | -123.3373
1516.7969 | 123.0881 | -63.5376 | 59.4727 | 0.0094624 | -0.0028526 | 0.0042394 | 0.059002 | 0.0041429 | 0.072838 | -0.001755 | 0.013282 | 0.0066618 | 0.062084 | 0.030455 | 0.072747 | -51.2174 | -20.5245 | -53.469 | 59.3606 | 59.27 | 59.4715 | -63.6872 | -47.9197 | -18.5892 | -50.4588 | 59.2707 | 59.4623 | 59.3281 | -63.9562 | -0.14962 | -0.11209 | 12.3202 | 10.0686 | 10.2182 | -0.2027 | -0.001159 | -0.41863 | -0.20194 | 15.6179 | 13.0788 | 13.4974 | -0.010374 | -0.14453 | 122.8982 | 122.8076 | 123.0091 | 43.0131 | -123.1599 | 122.8083 | 122.9999 | 122.8657 | 44.9484 | -123.4289
1517.7969 | 123.1567 | -63.5834 | 59.3903 | -0.0057996 | -0.0030662 | 0.0042394 | 0.059216 | 0.0041429 | 0.072838 | -0.001755 | 0.013923 | 0.0070892 | 0.062298 | 0.030668 | 0.073174 | -51.1899 | -20.5886 | -53.4369 | 59.3285 | 59.2471 | 59.444 | -63.7238 | -47.8648 | -18.5984 | -50.413 | 59.2432 | 59.4257 | 59.2045 | -63.9883 | -0.14047 | -0.061744 | 12.3935 | 10.1464 | 10.2869 | -0.14319 | 0.053767 | -0.40491 | -0.14702 | 15.7186 | 13.1704 | 13.5753 | 0.035394 | -0.18576 | 122.9119 | 122.8304 | 123.0274 | 42.9948 | -123.1141 | 122.8266 | 123.009 | 122.7879 | 44.985 | -123.3785
1518.7969 | 123.2025 | -63.4644 | 59.404 | -0.0057996 | -0.0028526 | 0.004453 | 0.059002 | 0.0043567 | 0.073051 | -0.001755 | 0.013495 | 0.0075166 | 0.062511 | 0.030241 | 0.07296 | -51.0342 | -20.5199 | -53.2996 | 59.4247 | 59.3295 | 59.531 | -63.6277 | -47.7137 | -18.5251 | -50.2711 | 59.3211 | 59.5218 | 59.264 | -63.8967 | -0.16333 | 0.020669 | 12.4301 | 10.1648 | 10.3281 | -0.074508 | 0.12703 | -0.43235 | -0.082913 | 15.7507 | 13.1933 | 13.6256 | 0.11781 | -0.13997 | 122.889 | 122.7938 | 122.9954 | 42.9445 | -123.0317 | 122.7854 | 122.9862 | 122.7284 | 44.9393 | -123.3007
1519.7969 | 123.0743 | -63.5696 | 59.4315 | 0.0018314 | -0.0026388 | 0.004453 | 0.058575 | 0.0045703 | 0.073265 | 0.0058755 | 0.013709 | 0.0070892 | 0.062725 | 0.030455 | 0.073388 | -51.0388 | -20.5703 | -53.3362 | 59.356 | 59.2654 | 59.4623 | -63.6964 | -47.7412 | -18.5434 | -50.2985 | 59.2661 | 59.4531 | 59.177 | -63.97 | -0.12673 | -0.075472 | 12.5308 | 10.2334 | 10.3602 | -0.16608 | 0.030882 | -0.40033 | -0.16532 | 15.8285 | 13.2711 | 13.6714 | 0.021666 | -0.25443 | 122.9256 | 122.835 | 123.032 | 42.9994 | -123.1278 | 122.8358 | 123.0228 | 122.7467 | 45.0262 | -123.4014
1520.7969 | 123.1293 | -63.5193 | 59.4818 | 0.0094624 | -0.0030662 | 0.004453 | 0.059002 | 0.0043567 | 0.072838 | -0.001755 | 0.013495 | 0.0068756 | 0.062725 | 0.030668 | 0.073174 | -50.9198 | -20.5748 | -53.2309 | 59.3926 | 59.2974 | 59.5035 | -63.6735 | -47.6725 | -18.5022 | -50.1886 | 59.2936 | 59.4852 | 59.2182 | -63.9288 | -0.15419 | -0.089199 | 12.5995 | 10.2884 | 10.4426 | -0.18438 | 0.021736 | -0.40947 | -0.1882 | 15.8468 | 13.3306 | 13.7401 | 0.003363 | -0.26357 | 122.9119 | 122.8167 | 123.0228 | 42.9445 | -123.1553 | 122.8129 | 123.0045 | 122.7375 | 45.0171 | -123.4106
1521.7969 | 123.0881 | -63.4323 | 59.5642 | 0.0094624 | -0.0026388 | 0.0046666 | 0.05943 | 0.0045703 | 0.073051 | -0.001755 | 0.013709 | 0.0070892 | 0.062511 | 0.030455 | 0.073174 | -50.7458 | -20.4787 | -53.0707 | 59.5025 | 59.4165 | 59.6134 | -63.5498 | -47.5031 | -18.4061 | -50.033 | 59.4081 | 59.5996 | 59.3739 | -63.8143 | -0.11753 | -0.061715 | 12.6865 | 10.3616 | 10.4792 | -0.14773 | 0.049225 | -0.38197 | -0.15614 | 15.9292 | 13.3993 | 13.7813 | 0.035431 | -0.1903 | 122.9348 | 122.8488 | 123.0457 | 42.9536 | -123.1141 | 122.8404 | 123.032 | 122.8062 | 45.0263 | -123.3785
1522.7969 | 123.1384 | -63.4186 | 59.5596 | 0.0018314 | -0.0028526 | 0.0046666 | 0.058575 | 0.0045703 | 0.073051 | -0.001755 | 0.014136 | 0.0066618 | 0.062298 | 0.030668 | 0.073601 | -50.6634 | -20.4283 | -52.9928 | 59.53 | 59.4531 | 59.6501 | -63.5132 | -47.4252 | -18.3236 | -49.9322 | 59.4401 | 59.6363 | 59.4472 | -63.7914 | -0.094636 | -0.029667 | 12.7552 | 10.4257 | 10.5204 | -0.10652 | 0.090432 | -0.37281 | -0.11951 | 15.9933 | 13.4863 | 13.8592 | 0.076637 | -0.11246 | 122.9485 | 122.8717 | 123.0686 | 42.9903 | -123.0728 | 122.8587 | 123.0548 | 122.8657 | 45.0949 | -123.351
1523.7969 | 123.1018 | -63.5284 | 59.436 | 0.0018314 | -0.0024252 | 0.0046666 | 0.059002 | 0.0045703 | 0.073265 | 0.0058755 | 0.014136 | 0.0070892 | 0.062725 | 0.030882 | 0.073601 | -50.7046 | -20.5474 | -53.0615 | 59.4155 | 59.3295 | 59.5264 | -63.6414 | -47.4939 | -18.3374 | -49.9872 | 59.3165 | 59.4989 | 59.2503 | -63.9059 | -0.11298 | -0.02053 | 12.8238 | 10.4669 | 10.5799 | -0.10655 | 0.090406 | -0.37742 | -0.11953 | 16.0345 | 13.5413 | 13.9187 | 0.062875 | -0.18575 | 122.9439 | 122.8579 | 123.0549 | 42.9811 | -123.0775 | 122.8449 | 123.0274 | 122.7787 | 45.1911 | -123.3419
1524.7969 | 123.111 | -63.5742 | 59.3857 | 0.0018314 | -0.0026388 | 0.004453 | 0.058789 | 0.0047839 | 0.073265 | -0.001755 | 0.014136 | 0.0068756 | 0.063152 | 0.030882 | 0.073388 | -50.7138 | -20.6252 | -53.0753 | 59.3422 | 59.2516 | 59.4532 | -63.7284 | -47.5122 | -18.3694 | -50.0101 | 59.2432 | 59.4257 | 59.2228 | -63.9883 | -0.1542 | -0.043431 | 12.8605 | 10.499 | 10.6532 | -0.13404 | 0.067502 | -0.41406 | -0.14244 | 16.062 | 13.5641 | 13.9782 | 0.039972 | -0.16286 | 122.9165 | 122.8259 | 123.0274 | 42.949 | -123.1141 | 122.8175 | 122.9999 | 122.797 | 45.2048 | -123.374
1525.7969 | 123.0789 | -63.5147 | 59.491 | -0.0057996 | -0.0026388 | 0.0046666 | 0.059002 | 0.0045703 | 0.073479 | -0.001755 | 0.013495 | 0.0073028 | 0.062939 | 0.031096 | 0.074029 | -50.5947 | -20.5657 | -52.9562 | 59.3926 | 59.3157 | 59.5127 | -63.6506 | -47.3932 | -18.2962 | -49.8681 | 59.3073 | 59.4989 | 59.3235 | -63.9288 | -0.13587 | -0.098354 | 12.92 | 10.5585 | 10.6944 | -0.17522 | 0.021738 | -0.41405 | -0.18362 | 16.1215 | 13.6466 | 14.0606 | 0.007943 | -0.16742 | 122.9073 | 122.8305 | 123.0274 | 42.949 | -123.1415 | 122.8221 | 123.0136 | 122.8383 | 45.2185 | -123.4197
1526.7969 | 123.1293 | -63.5376 | 59.4315 | -0.0057996 | -0.0028526 | 0.0048804 | 0.058789 | 0.0045703 | 0.073692 | 0.0058755 | 0.013709 | 0.0075166 | 0.062511 | 0.030668 | 0.073815 | -50.5306 | -20.584 | -52.9059 | 59.3926 | 59.3112 | 59.5081 | -63.6506 | -47.3428 | -18.2641 | -49.7995 | 59.3028 | 59.4989 | 59.3052 | -63.9288 | -0.11298 | -0.038845 | 13.007 | 10.6317 | 10.7447 | -0.12029 | 0.076668 | -0.39116 | -0.12869 | 16.1948 | 13.7381 | 14.1293 | 0.067452 | -0.12623 | 122.9302 | 122.8488 | 123.0457 | 42.9536 | -123.082 | 122.8404 | 123.0365 | 122.8428 | 45.2735 | -123.3602
1527.7969 | 123.0881 | -63.5193 | 59.4681 | 0.0018314 | -0.0019978 | 0.0048804 | 0.058789 | 0.0043567 | 0.073479 | -0.001755 | 0.013709 | 0.0070892 | 0.062725 | 0.030882 | 0.073815 | -50.4207 | -20.5245 | -52.8051 | 59.4476 | 59.357 | 59.5493 | -63.6231 | -47.265 | -18.2275 | -49.7033 | 59.3348 | 59.5401 | 59.3876 | -63.8875 | -0.10382 | -0.020526 | 13.0985 | 10.7141 | 10.818 | -0.11112 | 0.081255 | -0.36826 | -0.13327 | 16.2543 | 13.816 | 14.1842 | 0.072039 | -0.080432 | 122.9668 | 122.8762 | 123.0686 | 42.9948 | -123.0912 | 122.8541 | 123.0594 | 122.9069 | 45.2918 | -123.3556
1528.7969 | 123.1476 | -63.6063 | 59.3491 | 0.0018314 | -0.0022116 | 0.004453 | 0.059216 | 0.0049977 | 0.073692 | -0.0093855 | 0.01435 | 0.0075166 | 0.062725 | 0.031096 | 0.073601 | -50.4528 | -20.6618 | -52.8738 | 59.3056 | 59.215 | 59.4257 | -63.7467 | -47.352 | -18.3648 | -49.7766 | 59.2204 | 59.4028 | 59.2411 | -64.0066 | -0.14048 | -0.043437 | 13.1535 | 10.7324 | 10.8729 | -0.13405 | 0.076651 | -0.40033 | -0.12871 | 16.2543 | 13.8297 | 14.23 | 0.0537 | -0.10793 | 122.9119 | 122.8213 | 123.032 | 42.9444 | -123.0958 | 122.8266 | 123.009 | 122.8474 | 45.2414 | -123.3557
1529.7969 | 123.1384 | -63.5422 | 59.4269 | 0.0094624 | -0.0022116 | 0.0046666 | 0.058575 | 0.0049977 | 0.073906 | 0.0058755 | 0.014564 | 0.0073028 | 0.062939 | 0.030882 | 0.073815 | -50.2971 | -20.6023 | -52.7548 | 59.3789 | 59.2791 | 59.4761 | -63.6781 | -47.2421 | -18.2229 | -49.6575 | 59.2845 | 59.4806 | 59.2823 | -63.9379 | -0.13588 | -0.048002 | 13.2451 | 10.7874 | 10.9233 | -0.14776 | 0.049196 | -0.39574 | -0.14243 | 16.3001 | 13.8847 | 14.2804 | 0.053716 | -0.14454 | 122.9211 | 122.8213 | 123.0183 | 42.9399 | -123.1049 | 122.8266 | 123.0228 | 122.8245 | 45.3193 | -123.3648
1530.7969 | 123.1064 | -63.5696 | 59.3903 | 0.0018314 | -0.0019978 | 0.0046666 | 0.058789 | 0.0047839 | 0.073906 | -0.0093855 | 0.01435 | 0.0073028 | 0.062725 | 0.030882 | 0.073815 | -50.2788 | -20.6664 | -52.7365 | 59.3331 | 59.2471 | 59.4486 | -63.7284 | -47.2512 | -18.1771 | -49.6438 | 59.2432 | 59.444 | 59.2182 | -63.9837 | -0.15878 | -0.057165 | 13.2908 | 10.8332 | 10.992 | -0.14319 | 0.058345 | -0.41406 | -0.14702 | 16.3184 | 13.9259 | 14.3399 | 0.053708 | -0.17202 | 122.9027 | 122.8167 | 123.0182 | 42.9032 | -123.1187 | 122.8129 | 123.0136 | 122.7879 | 45.3925 | -123.374
1531.7969 | 123.1018 | -63.5651 | 59.436 | 0.017093 | -0.0017842 | 0.0048804 | 0.059002 | 0.0049977 | 0.073906 | 0.0058755 | 0.014564 | 0.0070892 | 0.062725 | 0.031096 | 0.074029 | -50.1918 | -20.6206 | -52.6449 | 59.3835 | 59.302 | 59.499 | -63.6689 | -47.1505 | -18.0993 | -49.5385 | 59.289 | 59.4806 | 59.2778 | -63.9288 | -0.10383 | -0.052579 | 13.3732 | 10.9202 | 11.024 | -0.13402 | 0.062934 | -0.36369 | -0.14701 | 16.4146 | 14.0266 | 14.3903 | 0.044561 | -0.15827 | 122.9485 | 122.8671 | 123.064 | 42.9444 | -123.1049 | 122.8541 | 123.0457 | 122.8428 | 45.4658 | -123.3648
1532.7969 | 123.0972 | -63.5605 | 59.4086 | -0.0057996 | -0.0022116 | 0.0046666 | 0.058789 | 0.0047839 | 0.073906 | -0.001755 | 0.014777 | 0.0073028 | 0.062939 | 0.031096 | 0.073601 | -50.1643 | -20.6298 | -52.6037 | 59.3697 | 59.2883 | 59.4807 | -63.6872 | -47.1322 | -18.0855 | -49.4881 | 59.2707 | 59.4714 | 59.3052 | -63.9517 | -0.12673 | -0.038848 | 13.3961 | 10.9568 | 11.0835 | -0.12029 | 0.072086 | -0.39117 | -0.13785 | 16.4283 | 14.0724 | 14.4635 | 0.06287 | -0.10334 | 122.9302 | 122.8488 | 123.0411 | 42.9307 | -123.0958 | 122.8312 | 123.0319 | 122.8657 | 45.4749 | -123.3602
1533.7969 | 123.1705 | -63.4506 | 59.4406 | 0.0018314 | -0.0017842 | 0.0053078 | 0.059216 | 0.0047839 | 0.073906 | -0.0093855 | 0.014564 | 0.0070892 | 0.062725 | 0.031096 | 0.073815 | -50.0041 | -20.5519 | -52.4343 | 59.4521 | 59.3661 | 59.5722 | -63.5911 | -46.9628 | -17.9848 | -49.337 | 59.3623 | 59.5584 | 59.3327 | -63.8647 | -0.14043 | 0.011519 | 13.4465 | 11.0163 | 11.1568 | -0.074497 | 0.13161 | -0.41403 | -0.078328 | 16.4878 | 14.1136 | 14.5276 | 0.11782 | -0.10791 | 122.9028 | 122.8167 | 123.0229 | 42.8987 | -123.0317 | 122.8129 | 123.0091 | 122.7833 | 45.4658 | -123.3053
1534.7969 | 123.0835 | -63.5239 | 59.4589 | -0.0057996 | -0.0017842 | 0.0048804 | 0.058789 | 0.0049977 | 0.073906 | 0.0058755 | 0.014777 | 0.0073028 | 0.062725 | 0.031309 | 0.074456 | -49.9812 | -20.5931 | -52.4068 | 59.4247 | 59.3295 | 59.5356 | -63.6323 | -46.9628 | -18.0214 | -49.3187 | 59.3211 | 59.5218 | 59.3373 | -63.9013 | -0.1084 | -0.034262 | 13.5427 | 11.117 | 11.2254 | -0.12944 | 0.076675 | -0.37742 | -0.13784 | 16.5611 | 14.2052 | 14.5826 | 0.06288 | -0.12164 | 122.9485 | 122.8533 | 123.0595 | 42.9307 | -123.0912 | 122.8449 | 123.0457 | 122.8611 | 45.5024 | -123.3602
1535.7969 | 123.1064 | -63.4644 | 59.5367 | 0.0094624 | -0.0017842 | 0.0048804 | 0.059216 | 0.0049977 | 0.074333 | -0.001755 | 0.01435 | 0.0073028 | 0.063152 | 0.031096 | 0.074242 | -49.9034 | -20.584 | -52.329 | 59.443 | 59.3615 | 59.5676 | -63.6185 | -46.9033 | -17.9802 | -49.2454 | 59.344 | 59.5401 | 59.406 | -63.8784 | -0.15418 | -0.093768 | 13.561 | 11.1354 | 11.2895 | -0.17521 | 0.030905 | -0.41404 | -0.19277 | 16.5611 | 14.2189 | 14.633 | 0.003375 | -0.13078 | 122.9073 | 122.8259 | 123.032 | 42.8804 | -123.1553 | 122.8083 | 123.0045 | 122.8703 | 45.4841 | -123.4151
1536.7969 | 123.1338 | -63.4369 | 59.523 | 0.0018314 | -0.0017842 | 0.005094 | 0.058575 | 0.0052113 | 0.07412 | 0.0058755 | 0.014564 | 0.0073028 | 0.062939 | 0.031096 | 0.07467 | -49.7981 | -20.5519 | -52.242 | 59.4659 | 59.3799 | 59.5768 | -63.5865 | -46.8437 | -17.9024 | -49.1584 | 59.376 | 59.5676 | 59.4289 | -63.8509 | -0.14959 | -0.057143 | 13.6388 | 11.1949 | 11.3445 | -0.14316 | 0.053795 | -0.41403 | -0.14699 | 16.5932 | 14.2785 | 14.6925 | 0.044579 | -0.094156 | 122.9028 | 122.8167 | 123.0137 | 42.885 | -123.1095 | 122.8129 | 123.0045 | 122.8657 | 45.5345 | -123.3739
1537.7969 | 123.143 | -63.4644 | 59.491 | 0.0018314 | -0.0015706 | 0.0046666 | 0.059216 | 0.0052113 | 0.073906 | 0.0058755 | 0.014564 | 0.0070892 | 0.063366 | 0.031737 | 0.074242 | -49.7202 | -20.5382 | -52.1596 | 59.4979 | 59.4073 | 59.5997 | -63.5636 | -46.7476 | -17.8429 | -49.0989 | 59.3989 | 59.5996 | 59.4655 | -63.8234 | -0.099228 | 0.006949 | 13.7441 | 11.3048 | 11.404 | -0.083641 | 0.10873 | -0.35909 | -0.092054 | 16.7168 | 14.3654 | 14.7245 | 0.10867 | -0.025484 | 122.9623 | 122.8717 | 123.0641 | 42.9262 | -123.0546 | 122.8633 | 123.064 | 122.9298 | 45.6215 | -123.3144
1538.7969 | 123.1979 | -63.3591 | 59.5596 | 0.0018314 | -0.0019978 | 0.0048804 | 0.059857 | 0.0049977 | 0.074333 | 0.0058755 | 0.014777 | 0.0073028 | 0.062939 | 0.031309 | 0.074242 | -49.6745 | -20.5474 | -52.123 | 59.4659 | 59.3753 | 59.5722 | -63.5773 | -46.7384 | -17.8932 | -49.0714 | 59.3806 | 59.5676 | 59.4197 | -63.8463 | -0.21825 | -0.093764 | 13.6846 | 11.2361 | 11.4543 | -0.18436 | 0.012596 | -0.48727 | -0.17903 | 16.6206 | 14.2876 | 14.7749 | 0.007958 | -0.13993 | 122.8249 | 122.7343 | 122.9313 | 42.8117 | -123.137 | 122.7397 | 122.9267 | 122.7788 | 45.4658 | -123.406
1539.7969 | 123.1338 | -63.5468 | 59.4269 | 0.0018314 | -0.0017842 | 0.0048804 | 0.059216 | 0.0052113 | 0.074761 | 0.0058755 | 0.014777 | 0.0075166 | 0.062725 | 0.031309 | 0.074456 | -49.6882 | -20.6115 | -52.1642 | 59.4018 | 59.3341 | 59.5219 | -63.646 | -46.7522 | -17.8795 | -49.0714 | 59.3119 | 59.5126 | 59.3556 | -63.9059 | -0.09925 | -0.02511 | 13.8586 | 11.3826 | 11.4818 | -0.092817 | 0.094982 | -0.35911 | -0.11496 | 16.7946 | 14.4753 | 14.8344 | 0.085766 | -0.071284 | 122.9485 | 122.8808 | 123.0686 | 42.9353 | -123.0729 | 122.8587 | 123.0594 | 122.9023 | 45.6673 | -123.3327
1540.7969 | 123.0515 | -63.9542 | 59.0561 | -0.013431 | -0.0013568 | 0.0053078 | 0.059216 | 0.0049977 | 0.07412 | -0.001755 | 0.014991 | 0.0077302 | 0.062725 | 0.031737 | 0.074456 | -50.0041 | -20.9274 | -52.4892 | 59.0126 | 58.9449 | 59.1235 | -64.0444 | -47.1047 | -18.2641 | -49.392 | 58.9273 | 59.1189 | 58.9389 | -64.2996 | -0.090207 | -0.043484 | 13.9501 | 11.4649 | 11.5551 | -0.11124 | 0.067433 | -0.34548 | -0.12876 | 16.8494 | 14.5622 | 14.9077 | 0.062795 | -0.11715 | 122.9668 | 122.899 | 123.0777 | 43.0268 | -123.1005 | 122.8815 | 123.073 | 122.8931 | 45.69 | -123.3557
1541.7969 | 123.1155 | -63.5422 | 59.4406 | 0.0018314 | -0.0015706 | 0.0053078 | 0.059002 | 0.0054249 | 0.074761 | -0.001755 | 0.014991 | 0.0070892 | 0.063366 | 0.031737 | 0.074242 | -49.5508 | -20.5657 | -52.0314 | 59.4155 | 59.3341 | 59.5356 | -63.646 | -46.7018 | -17.8612 | -48.9524 | 59.3348 | 59.5218 | 59.3831 | -63.8921 | -0.10383 | -0.025108 | 13.9913 | 11.5108 | 11.6146 | -0.10655 | 0.094985 | -0.34995 | -0.1058 | 16.8404 | 14.5898 | 14.9397 | 0.08119 | -0.057545 | 122.9577 | 122.8762 | 123.0778 | 42.9765 | -123.0866 | 122.877 | 123.064 | 122.9252 | 45.681 | -123.3327
1542.7969 | 123.0698 | -63.414 | 59.5734 | 0.0018314 | -0.0015706 | 0.005094 | 0.059002 | 0.0052113 | 0.074761 | 0.0058755 | 0.014991 | 0.0073028 | 0.063366 | 0.031737 | 0.074456 | -49.4089 | -20.4741 | -51.8941 | 59.5025 | 59.4211 | 59.6134 | -63.559 | -46.5873 | -17.7971 | -48.8196 | 59.4081 | 59.5996 | 59.4289 | -63.8097 | -0.145 | -0.07087 | 14.0051 | 11.5199 | 11.6649 | -0.1523 | 0.04007 | -0.39571 | -0.16529 | 16.8267 | 14.5944 | 14.9901 | 0.026276 | -0.14451 | 122.9165 | 122.8351 | 123.0274 | 42.9399 | -123.1324 | 122.8221 | 123.0136 | 122.8429 | 45.6169 | -123.3831
1543.7969 | 123.0927 | -63.3728 | 59.5825 | -0.0057996 | -0.0013568 | 0.005094 | 0.059002 | 0.0049977 | 0.074761 | -0.001755 | 0.015205 | 0.0073028 | 0.062939 | 0.031737 | 0.074456 | -49.2899 | -20.4192 | -51.7842 | 59.5574 | 59.4806 | 59.6821 | -63.4995 | -46.4774 | -17.6735 | -48.696 | 59.4676 | 59.6637 | 59.4975 | -63.7548 | -0.12668 | -0.025085 | 14.0829 | 11.5886 | 11.7153 | -0.10193 | 0.099593 | -0.38196 | -0.11493 | 16.8954 | 14.6768 | 15.0588 | 0.08122 | -0.084987 | 122.9302 | 122.8534 | 123.0549 | 42.9536 | -123.082 | 122.8404 | 123.0365 | 122.8703 | 45.6993 | -123.3373
1544.7969 | 123.0835 | -63.5834 | 59.4131 | -0.0057996 | -0.0013568 | 0.0053078 | 0.05943 | 0.0052113 | 0.074974 | -0.0093855 | 0.015205 | 0.0075166 | 0.063366 | 0.031737 | 0.07467 | -49.5188 | -20.6572 | -51.9948 | 59.2827 | 59.2013 | 59.4074 | -63.7651 | -46.7338 | -17.8841 | -48.902 | 59.1975 | 59.3844 | 59.2228 | -64.0158 | -0.18168 | -0.13042 | 14.0646 | 11.5886 | 11.7703 | -0.21187 | -0.00575 | -0.43238 | -0.21569 | 16.8495 | 14.6813 | 15.1137 | -0.028702 | -0.19033 | 122.8661 | 122.7846 | 122.9908 | 42.9261 | -123.1782 | 122.7808 | 122.9678 | 122.8062 | 45.6993 | -123.4289
1545.7969 | 123.1018 | -63.5605 | 59.3994 | 0.0094624 | -0.00092939 | 0.0055214 | 0.059002 | 0.0052113 | 0.074974 | -0.001755 | 0.015205 | 0.0075166 | 0.063152 | 0.031737 | 0.074883 | -49.3723 | -20.5748 | -51.8483 | 59.3697 | 59.2883 | 59.4898 | -63.6689 | -46.5965 | -17.8062 | -48.7418 | 59.289 | 59.476 | 59.319 | -63.9333 | -0.10841 | -0.029693 | 14.1882 | 11.7122 | 11.8206 | -0.11114 | 0.090398 | -0.37285 | -0.11039 | 16.964 | 14.8187 | 15.1916 | 0.076603 | -0.080446 | 122.9302 | 122.8488 | 123.0503 | 42.9857 | -123.0683 | 122.8495 | 123.0365 | 122.8795 | 45.7542 | -123.3328
1546.7969 | 123.056 | -63.5422 | 59.4177 | 0.0018314 | -0.0011432 | 0.0055214 | 0.059216 | 0.0052113 | 0.074547 | -0.001755 | 0.015632 | 0.0075166 | 0.062939 | 0.03195 | 0.07467 | -49.2807 | -20.5382 | -51.7659 | 59.3926 | 59.302 | 59.5127 | -63.6597 | -46.5186 | -17.733 | -48.6639 | 59.3073 | 59.4898 | 59.3419 | -63.9242 | -0.11756 | -0.025112 | 14.2615 | 11.7763 | 11.8939 | -0.11571 | 0.09498 | -0.382 | -0.11038 | 17.0235 | 14.8782 | 15.2602 | 0.072028 | -0.075864 | 122.9348 | 122.8442 | 123.0549 | 43.004 | -123.0775 | 122.8495 | 123.0319 | 122.884 | 45.8092 | -123.3419
1547.7969 | 123.0927 | -63.5101 | 59.5001 | 0.0018314 | -0.0011432 | 0.005094 | 0.059216 | 0.0052113 | 0.074761 | -0.001755 | 0.015632 | 0.0073028 | 0.062939 | 0.03195 | 0.074883 | -49.1983 | -20.4924 | -51.6697 | 59.443 | 59.3386 | 59.5539 | -63.614 | -46.45 | -17.7101 | -48.5815 | 59.3486 | 59.5401 | 59.3831 | -63.8875 | -0.10382 | -0.057147 | 14.3118 | 11.8404 | 11.9442 | -0.16148 | 0.05379 | -0.37742 | -0.15157 | 17.0602 | 14.9286 | 15.306 | 0.039996 | -0.11705 | 122.9531 | 122.8488 | 123.064 | 43.0177 | -123.1141 | 122.8587 | 123.0503 | 122.8932 | 45.8 | -123.3877
1548.7969 | 123.0743 | -63.1897 | 59.7885 | 0.0094624 | -0.00092939 | 0.0048804 | 0.05943 | 0.0052113 | 0.075188 | -0.0093855 | 0.015418 | 0.0073028 | 0.062725 | 0.031737 | 0.07467 | -48.8824 | -20.2452 | -51.3492 | 59.6994 | 59.6042 | 59.8012 | -63.353 | -46.1615 | -17.4857 | -48.2793 | 59.6049 | 59.8011 | 59.6028 | -63.6128 | -0.16325 | -0.089148 | 14.3073 | 11.8405 | 12.0037 | -0.18429 | 0.012644 | -0.42312 | -0.18357 | 17.0282 | 14.9104 | 15.3335 | 0.012585 | -0.18567 | 122.8891 | 122.7939 | 122.9909 | 42.9445 | -123.1415 | 122.7946 | 122.9908 | 122.7925 | 45.704 | -123.4013
1549.7969 | 123.1155 | -63.2858 | 59.6741 | 0.0018314 | -0.0011432 | 0.0053078 | 0.05943 | 0.0056385 | 0.075402 | -0.001755 | 0.015845 | 0.0075166 | 0.062939 | 0.031737 | 0.07467 | -48.887 | -20.2543 | -51.3355 | 59.6444 | 59.5584 | 59.7508 | -63.4033 | -46.189 | -17.4766 | -48.2793 | 59.55 | 59.7416 | 59.525 | -63.6723 | -0.11749 | -0.029648 | 14.3989 | 11.9503 | 12.0678 | -0.11564 | 0.07672 | -0.38651 | -0.12407 | 17.0969 | 15.0065 | 15.393 | 0.067504 | -0.14907 | 122.9303 | 122.8443 | 123.0366 | 43.0315 | -123.0774 | 122.8358 | 123.0274 | 122.8108 | 45.8093 | -123.3464
1550.7969 | 123.0789 | -63.2996 | 59.6466 | 0.0018314 | -0.0011432 | 0.0055214 | 0.059216 | 0.0056385 | 0.075188 | 0.0058755 | 0.015418 | 0.0075166 | 0.063152 | 0.032164 | 0.074883 | -48.887 | -20.3322 | -51.3218 | 59.5986 | 59.5081 | 59.7096 | -63.4537 | -46.2165 | -17.4766 | -48.2702 | 59.5088 | 59.7004 | 59.4105 | -63.7273 | -0.15413 | -0.047966 | 14.4126 | 11.9778 | 12.1319 | -0.13854 | 0.062979 | -0.42773 | -0.13781 | 17.0831 | 15.0294 | 15.4571 | 0.053763 | -0.23607 | 122.8982 | 122.8076 | 123.0091 | 42.9674 | -123.1003 | 122.8084 | 122.9999 | 122.7101 | 45.823 | -123.3739
1551.7969 | 123.0972 | -63.1073 | 59.8572 | -0.0057996 | -0.00071579 | 0.0053078 | 0.059216 | 0.0056385 | 0.074974 | -0.0093855 | 0.015845 | 0.0073028 | 0.063152 | 0.032164 | 0.075097 | -48.6397 | -20.1307 | -51.0791 | 59.7772 | 59.7004 | 59.879 | -63.2797 | -45.9646 | -17.2888 | -48.0092 | 59.6782 | 59.8789 | 59.6669 | -63.535 | -0.17239 | -0.079981 | 14.4676 | 12.0282 | 12.2006 | -0.1568 | 0.021815 | -0.42768 | -0.17898 | 17.1427 | 15.0981 | 15.5258 | 0.021756 | -0.19024 | 122.8845 | 122.8077 | 122.9863 | 42.9766 | -123.1369 | 122.7855 | 122.9862 | 122.7742 | 45.8185 | -123.3922
1552.7969 | 123.056 | -63.2126 | 59.7885 | -0.0057996 | -0.00092939 | 0.0053078 | 0.059643 | 0.0056385 | 0.074974 | -0.001755 | 0.015632 | 0.0075166 | 0.063366 | 0.032164 | 0.075097 | -48.5802 | -20.1399 | -51.0196 | 59.7635 | 59.6637 | 59.8744 | -63.2888 | -45.928 | -17.2476 | -47.9634 | 59.6645 | 59.8698 | 59.7081 | -63.5533 | -0.076262 | -0.025051 | 14.6324 | 12.193 | 12.2692 | -0.12477 | 0.085901 | -0.34071 | -0.12405 | 17.2846 | 15.2492 | 15.5899 | 0.081264 | -0.080364 | 122.976 | 122.8763 | 123.087 | 43.0727 | -123.0774 | 122.8771 | 123.0824 | 122.9207 | 45.9649 | -123.3418
1553.7969 | 123.0652 | -63.1485 | 59.8068 | 0.0018314 | -0.00071579 | 0.0053078 | 0.059216 | 0.0054249 | 0.075402 | -0.0093855 | 0.015632 | 0.0070892 | 0.063152 | 0.032378 | 0.074883 | -48.5299 | -20.1261 | -50.9738 | 59.768 | 59.6821 | 59.8836 | -63.2888 | -45.9005 | -17.1835 | -47.8993 | 59.6782 | 59.8744 | 59.6715 | -63.5533 | -0.14035 | -0.038783 | 14.6186 | 12.1747 | 12.315 | -0.12476 | 0.076748 | -0.4048 | -0.12862 | 17.248 | 15.2492 | 15.654 | 0.067532 | -0.1353 | 122.9165 | 122.8306 | 123.0321 | 43.0224 | -123.0957 | 122.8267 | 123.0229 | 122.82 | 45.965 | -123.3601
1554.7969 | 123.0743 | -63.1897 | 59.7977 | 0.0018314 | -0.00071579 | 0.0053078 | 0.059643 | 0.0056385 | 0.075615 | -0.001755 | 0.015845 | 0.0075166 | 0.063366 | 0.03195 | 0.075097 | -48.5024 | -20.1353 | -50.9326 | 59.7406 | 59.6546 | 59.8515 | -63.298 | -45.9005 | -17.2019 | -47.881 | 59.6507 | 59.8469 | 59.5983 | -63.567 | -0.10831 | -0.057098 | 14.6873 | 12.2571 | 12.3654 | -0.14308 | 0.053853 | -0.37733 | -0.14694 | 17.2892 | 15.3087 | 15.6861 | 0.049216 | -0.19941 | 122.9303 | 122.8443 | 123.0412 | 43.0544 | -123.0957 | 122.8404 | 123.0366 | 122.788 | 45.9878 | -123.3647
1555.7969 | 123.0606 | -63.2492 | 59.7427 | -0.0057996 | -0.00071579 | 0.0048804 | 0.059643 | 0.0056385 | 0.075402 | -0.001755 | 0.015632 | 0.0073028 | 0.063366 | 0.032591 | 0.075097 | -48.507 | -20.1765 | -50.9189 | 59.6948 | 59.5996 | 59.8012 | -63.3575 | -45.9143 | -17.2339 | -47.8581 | 59.6004 | 59.7965 | 59.644 | -63.6174 | -0.10832 | -0.047951 | 14.7422 | 12.3303 | 12.4386 | -0.1431 | 0.05842 | -0.36819 | -0.14237 | 17.335 | 15.3911 | 15.7593 | 0.053783 | -0.098689 | 122.944 | 122.8488 | 123.0504 | 43.0727 | -123.1003 | 122.8496 | 123.0457 | 122.8933 | 46.0153 | -123.3601
1556.7969 | 123.1979 | -63.1668 | 59.8343 | -0.0057996 | -0.00028839 | 0.005094 | 0.059857 | 0.0056385 | 0.075402 | -0.001755 | 0.016059 | 0.0075166 | 0.063152 | 0.032378 | 0.075097 | -48.3971 | -20.0895 | -50.7953 | 59.7589 | 59.6637 | 59.879 | -63.2888 | -45.8456 | -17.0874 | -47.7207 | 59.6645 | 59.8652 | 59.6349 | -63.5441 | -0.12204 | -0.075406 | 14.7697 | 12.3715 | 12.4936 | -0.17054 | 0.044703 | -0.37733 | -0.16982 | 17.3212 | 15.4461 | 15.8234 | 0.030909 | -0.1994 | 122.9257 | 122.8306 | 123.0458 | 43.0773 | -123.1231 | 122.8313 | 123.032 | 122.8017 | 46.0794 | -123.3784
1557.7969 | 123.1338 | -63.208 | 59.7656 | -0.0057996 | -0.00050219 | 0.0053078 | 0.059216 | 0.0058523 | 0.076043 | -0.001755 | 0.015632 | 0.0075166 | 0.063152 | 0.032805 | 0.07531 | -48.3467 | -20.0941 | -50.7495 | 59.7497 | 59.6592 | 59.8561 | -63.3072 | -45.8364 | -17.0965 | -47.6887 | 59.6553 | 59.8469 | 59.7081 | -63.567 | -0.099155 | -0.015898 | 14.8613 | 12.4585 | 12.5577 | -0.10646 | 0.090475 | -0.35902 | -0.11032 | 17.3716 | 15.5193 | 15.8784 | 0.081259 | -0.057476 | 122.9577 | 122.8672 | 123.0641 | 43.1139 | -123.0728 | 122.8633 | 123.0549 | 122.9162 | 46.1115 | -123.3327
1558.7969 | 123.1613 | -63.0753 | 59.8068 | 0.0018314 | -0.00028839 | 0.0053078 | 0.059857 | 0.0062795 | 0.075615 | -0.017016 | 0.016059 | 0.0073028 | 0.063366 | 0.032378 | 0.07531 | -48.1911 | -19.9796 | -50.5893 | 59.8413 | 59.7553 | 59.966 | -63.1973 | -45.7174 | -16.9134 | -47.5422 | 59.756 | 59.9522 | 59.7814 | -63.4617 | -0.12201 | 0.034471 | 14.8842 | 12.486 | 12.608 | -0.0515 | 0.15916 | -0.38646 | -0.050788 | 17.3579 | 15.5331 | 15.9196 | 0.14537 | -0.025417 | 122.9166 | 122.8306 | 123.0412 | 43.0956 | -123.0041 | 122.8313 | 123.0274 | 122.8567 | 46.1619 | -123.2685
1559.7969 | 122.9965 | -63.0936 | 59.9075 | -0.0057996 | -0.00028839 | 0.0055214 | 0.059643 | 0.0064933 | 0.075615 | -0.0093855 | 0.016059 | 0.0077302 | 0.063366 | 0.032591 | 0.07531 | -48.159 | -20.0162 | -50.548 | 59.823 | 59.7553 | 59.9385 | -63.2339 | -45.7265 | -16.9638 | -47.5559 | 59.7286 | 59.9247 | 59.7036 | -63.4846 | -0.14033 | -0.084551 | 14.9346 | 12.5455 | 12.6859 | -0.15221 | 0.030983 | -0.39104 | -0.17897 | 17.367 | 15.5377 | 15.9287 | 0.017188 | -0.20396 | 122.9165 | 122.8489 | 123.0321 | 43.0773 | -123.1414 | 122.8221 | 123.0183 | 122.7971 | 46.1298 | -123.3921
1560.7969 | 123.1567 | -63.0386 | 59.8755 | -0.013431 | -0.00050219 | 0.0055214 | 0.059643 | 0.0062795 | 0.076043 | -0.017016 | 0.016059 | 0.0075166 | 0.062939 | 0.032591 | 0.07531 | -48.0766 | -19.9796 | -50.4565 | 59.8459 | 59.7691 | 59.9706 | -63.1927 | -45.6991 | -16.8951 | -47.4094 | 59.7652 | 59.9522 | 59.8089 | -63.448 | -0.15405 | -0.029615 | 14.962 | 12.5822 | 12.7362 | -0.10643 | 0.095077 | -0.40935 | -0.1103 | 17.3396 | 15.6293 | 16.0386 | 0.076704 | -0.06661 | 122.8845 | 122.8077 | 123.0092 | 43.059 | -123.0682 | 122.8038 | 122.9908 | 122.8475 | 46.1436 | -123.3235
1561.7969 | 123.056 | -63.0981 | 59.8709 | 0.0094624 | -0.00028839 | 0.0055214 | 0.059643 | 0.0060659 | 0.076043 | -0.001755 | 0.016486 | 0.0077302 | 0.063366 | 0.032378 | 0.075524 | -48.0171 | -19.9934 | -50.4015 | 59.8276 | 59.7553 | 59.9523 | -63.211 | -45.7128 | -16.9134 | -47.3865 | 59.7423 | 59.9476 | 59.7494 | -63.4663 | -0.11286 | -0.043351 | 15.0811 | 12.6966 | 12.8095 | -0.11559 | 0.08134 | -0.36815 | -0.12861 | 17.3854 | 15.7117 | 16.0798 | 0.076702 | -0.12156 | 122.9257 | 122.8535 | 123.0504 | 43.1048 | -123.0819 | 122.8404 | 123.0458 | 122.8475 | 46.1848 | -123.3372
1562.7969 | 123.175 | -63.1943 | 59.7519 | -0.013431 | 0.00035261 | 0.0053078 | 0.059857 | 0.0060659 | 0.076256 | 0.0058755 | 0.016059 | 0.0077302 | 0.063366 | 0.032805 | 0.07531 | -48.0949 | -20.0575 | -50.4656 | 59.7223 | 59.6317 | 59.8332 | -63.3163 | -45.7815 | -16.9454 | -47.4277 | 59.6324 | 59.824 | 59.5799 | -63.5853 | -0.12205 | -0.029635 | 15.0994 | 12.7286 | 12.8507 | -0.1202 | 0.081315 | -0.39107 | -0.11948 | 17.4128 | 15.7666 | 16.1577 | 0.072099 | -0.17194 | 122.9165 | 122.826 | 123.0275 | 43.1368 | -123.0682 | 122.8267 | 123.0183 | 122.7742 | 46.2488 | -123.3372
1563.7969 | 123.0652 | -63.0844 | 59.8984 | 0.0018314 | -7.4788e-05 | 0.0053078 | 0.059643 | 0.0064933 | 0.075829 | -0.001755 | 0.016273 | 0.0077302 | 0.063152 | 0.032805 | 0.075097 | -48.0766 | -20.0895 | -50.4427 | 59.6856 | 59.5905 | 59.792 | -63.3621 | -45.7677 | -16.9775 | -47.4231 | 59.5866 | 59.7919 | 59.644 | -63.6311 | -0.2777 | -0.21275 | 15.0078 | 12.6417 | 12.9194 | -0.30789 | -0.10638 | -0.54672 | -0.31175 | 17.3167 | 15.6613 | 16.208 | -0.10643 | -0.25433 | 122.77 | 122.6749 | 122.8764 | 42.9949 | -123.2605 | 122.671 | 122.8764 | 122.7285 | 46.1069 | -123.5295
1564.7969 | 123.1155 | -63.0661 | 59.9121 | -0.0057996 | -7.4788e-05 | 0.0055214 | 0.059643 | 0.0062795 | 0.076043 | -0.0093855 | 0.016486 | 0.0077302 | 0.063152 | 0.032591 | 0.075097 | -47.8431 | -19.9064 | -50.2001 | 59.855 | 59.7736 | 59.966 | -63.1881 | -45.5754 | -16.7943 | -47.1987 | 59.7606 | 59.9659 | 59.8089 | -63.4526 | -0.12201 | -0.057079 | 15.223 | 12.866 | 12.988 | -0.13847 | 0.053877 | -0.38646 | -0.1515 | 17.4907 | 15.8674 | 16.2538 | 0.053819 | -0.10323 | 122.9211 | 122.8397 | 123.0321 | 43.1597 | -123.1002 | 122.8267 | 123.032 | 122.875 | 46.2718 | -123.3647
1565.7969 | 123.0194 | -63.2584 | 59.7061 | -0.013431 | 0.00013881 | 0.0055214 | 0.059857 | 0.0062795 | 0.076043 | -0.001755 | 0.016486 | 0.0077302 | 0.063152 | 0.032591 | 0.075524 | -47.9713 | -20.0529 | -50.31 | 59.6856 | 59.6042 | 59.8057 | -63.3667 | -45.7403 | -16.9454 | -47.3315 | 59.5912 | 59.7919 | 59.5662 | -63.6266 | -0.10833 | -0.020486 | 15.2871 | 12.9484 | 13.0567 | -0.1019 | 0.099619 | -0.36819 | -0.11491 | 17.5181 | 15.9268 | 16.295 | 0.085825 | -0.1399 | 122.944 | 122.8626 | 123.0641 | 43.2055 | -123.0728 | 122.8496 | 123.0503 | 122.8246 | 46.3129 | -123.3327
1566.7969 | 123.1842 | -62.8967 | 60.0037 | -0.0057996 | 0.00013881 | 0.0053078 | 0.059643 | 0.0060659 | 0.076256 | -0.017016 | 0.0167 | 0.0075166 | 0.063152 | 0.032805 | 0.07531 | -47.6874 | -19.8331 | -50.0399 | 59.9008 | 59.824 | 60.0255 | -63.1286 | -45.5113 | -16.6936 | -47.0614 | 59.8201 | 60.0163 | 59.8089 | -63.4022 | -0.23186 | -0.10285 | 15.2093 | 12.8569 | 13.0887 | -0.17965 | 0.021846 | -0.50546 | -0.18353 | 17.3854 | 15.8353 | 16.3408 | 0.01263 | -0.19478 | 122.7975 | 122.7207 | 122.9222 | 43.0636 | -123.1322 | 122.7169 | 122.913 | 122.7056 | 46.2031 | -123.4059
1567.7969 | 123.1796 | -62.9425 | 59.9579 | 0.0018314 | 0.00013881 | 0.0053078 | 0.060071 | 0.0064933 | 0.07647 | -0.001755 | 0.016273 | 0.0079438 | 0.063366 | 0.033019 | 0.075524 | -47.7058 | -19.856 | -49.9803 | 59.8825 | 59.7965 | 60.0026 | -63.1606 | -45.5022 | -16.7302 | -47.0568 | 59.7881 | 59.9797 | 59.8043 | -63.4251 | -0.21813 | -0.075386 | 15.2368 | 12.9622 | 13.1803 | -0.16135 | 0.044729 | -0.48258 | -0.1698 | 17.4403 | 15.8857 | 16.3683 | 0.021778 | -0.15359 | 122.825 | 122.739 | 122.9451 | 43.0865 | -123.1185 | 122.7306 | 122.9222 | 122.7468 | 46.2123 | -123.383
1568.7969 | 123.1659 | -62.9105 | 60.0266 | -0.013431 | 0.00035261 | 0.0055214 | 0.060071 | 0.0064933 | 0.07647 | -0.017016 | 0.016273 | 0.0075166 | 0.063152 | 0.033019 | 0.075738 | -47.5455 | -19.7324 | -49.8293 | 59.9924 | 59.9064 | 60.1171 | -63.0324 | -45.3602 | -16.57 | -46.9561 | 59.9025 | 60.1033 | 59.905 | -63.3106 | -0.12197 | -0.034168 | 15.365 | 13.0812 | 13.2032 | -0.12012 | 0.09053 | -0.40016 | -0.124 | 17.5502 | 15.9544 | 16.3545 | 0.076736 | -0.12152 | 122.9028 | 122.8169 | 123.0275 | 43.1781 | -123.059 | 122.813 | 123.0137 | 122.8155 | 46.3405 | -123.3372
1569.7969 | 123.0698 | -62.9929 | 60.0082 | -0.0057996 | 0.00035261 | 0.0055214 | 0.060071 | 0.0064933 | 0.07647 | -0.0093855 | 0.016914 | 0.0075166 | 0.063366 | 0.033233 | 0.075738 | -47.5226 | -19.7415 | -49.7926 | 59.9832 | 59.8973 | 60.085 | -63.0645 | -45.3465 | -16.5654 | -46.9698 | 59.8797 | 60.0804 | 59.8409 | -63.3381 | -0.071621 | -0.025015 | 15.4702 | 13.2002 | 13.2718 | -0.11097 | 0.07679 | -0.34523 | -0.12859 | 17.6464 | 16.023 | 16.3683 | 0.072153 | -0.16731 | 122.9761 | 122.8901 | 123.0779 | 43.2513 | -123.0727 | 122.8725 | 123.0733 | 122.8338 | 46.4274 | -123.3463
1570.7969 | 123.1705 | -62.8464 | 60.0494 | 0.0018314 | 0.00013881 | 0.0053078 | 0.059857 | 0.0062795 | 0.076043 | 0.0058755 | 0.016486 | 0.0073028 | 0.063366 | 0.033446 | 0.075951 | -47.4219 | -19.7141 | -49.6919 | 60.029 | 59.9431 | 60.1354 | -63.0095 | -45.2549 | -16.5425 | -46.8599 | 59.9438 | 60.1308 | 59.9325 | -63.274 | -0.16316 | -0.020429 | 15.4245 | 13.1545 | 13.3176 | -0.10638 | 0.085957 | -0.42761 | -0.10568 | 17.5915 | 15.9865 | 16.4141 | 0.08132 | -0.11694 | 122.8754 | 122.7894 | 122.9818 | 43.1323 | -123.059 | 122.7901 | 122.9771 | 122.7789 | 46.3039 | -123.3234
1571.7969 | 123.1064 | -63.7161 | 59.2346 | -0.0057996 | 0.00035261 | 0.0053078 | 0.059857 | 0.0067069 | 0.076897 | -0.017016 | 0.0167 | 0.0077302 | 0.064007 | 0.033019 | 0.07531 | -48.2277 | -20.5016 | -50.5023 | 59.15 | 59.0547 | 59.27 | -63.8841 | -46.1111 | -17.3667 | -47.7161 | 59.0555 | 59.2562 | 59.058 | -64.1577 | -0.16798 | -0.084661 | 15.4884 | 13.2139 | 13.3818 | -0.17987 | 0.03542 | -0.44157 | -0.17909 | 17.605 | 16 | 16.4416 | 0.021625 | -0.17663 | 122.8661 | 122.7709 | 122.9862 | 43.2145 | -123.1187 | 122.7717 | 122.9724 | 122.7741 | 46.3494 | -123.3923
1572.7969 | 123.1842 | -52.8397 | 70.1157 | 0.0018314 | 0.00035261 | 0.0059488 | 0.060284 | 0.0069205 | 0.076897 | -0.0093855 | 0.016914 | 0.0081574 | 0.063793 | 0.033233 | 0.078088 | -41.731 | -14.3754 | -44.0606 | 65.6238 | 65.6072 | 65.6755 | -57.2401 | -39.6735 | -11.3548 | -41.2235 | 65.6211 | 65.7579 | 65.6741 | -57.4543 | -4.4004 | -4.4919 | 11.1087 | 8.779 | 13.1795 | -4.5085 | -4.4402 | -4.6146 | -4.4946 | 13.1662 | 11.6161 | 16.2308 | -4.3578 | -4.4416 | 118.4635 | 118.4469 | 118.5152 | 38.4643 | -127.3558 | 118.4607 | 118.5975 | 118.5137 | 41.4848 | -127.57
1573.7969 | 123.1888 | -62.7457 | 60.1273 | 0.0018314 | 0.00077981 | 0.0055214 | 0.060071 | 0.0067069 | 0.076684 | 0.0058755 | 0.017127 | 0.0075166 | 0.06358 | 0.033446 | 0.076165 | -47.2021 | -19.6042 | -49.4401 | 60.1068 | 60.0026 | 60.2224 | -62.9408 | -45.1542 | -16.4281 | -46.7042 | 60.017 | 60.2132 | 60.0195 | -63.2053 | -0.19518 | -0.020417 | 15.5435 | 13.3056 | 13.5007 | -0.12467 | 0.09513 | -0.45964 | -0.11025 | 17.5915 | 16.0414 | 16.5011 | 0.085914 | -0.10776 | 122.8525 | 122.7483 | 122.9681 | 43.1415 | -123.0681 | 122.7627 | 122.9588 | 122.7652 | 46.3176 | -123.3326
1574.7969 | 123.1476 | -62.764 | 60.1822 | -0.0057996 | 0.00056621 | 0.0055214 | 0.060284 | 0.0067069 | 0.076897 | -0.001755 | 0.016914 | 0.0079438 | 0.06358 | 0.033019 | 0.075738 | -47.0831 | -19.5355 | -49.3302 | 60.1526 | 60.0667 | 60.2728 | -62.8813 | -45.1176 | -16.4509 | -46.6447 | 60.0582 | 60.2544 | 60.0149 | -63.1641 | -0.11735 | -0.029565 | 15.6809 | 13.4338 | 13.5511 | -0.1155 | 0.090563 | -0.40012 | -0.12397 | 17.6464 | 16.1193 | 16.5194 | 0.07219 | -0.16727 | 122.9166 | 122.8307 | 123.0367 | 43.2285 | -123.0635 | 122.8222 | 123.0184 | 122.7789 | 46.313 | -123.3463
1575.7969 | 123.1796 | -62.851 | 60.0403 | 0.0018314 | 0.00077981 | 0.0055214 | 0.060071 | 0.0064933 | 0.076897 | -0.0093855 | 0.017127 | 0.0077302 | 0.06358 | 0.033446 | 0.075951 | -47.1335 | -19.6179 | -49.376 | 60.0565 | 59.9705 | 60.1629 | -62.9958 | -45.232 | -16.4922 | -46.7226 | 59.9575 | 60.1628 | 59.9554 | -63.2557 | -0.14484 | 0.016196 | 15.7175 | 13.4749 | 13.6198 | -0.069749 | 0.12258 | -0.40472 | -0.082793 | 17.6189 | 16.1284 | 16.5331 | 0.12252 | -0.08489 | 122.9074 | 122.8215 | 123.0138 | 43.233 | -123.0361 | 122.8084 | 123.0138 | 122.8063 | 46.3588 | -123.296
1576.7969 | 123.1247 | -62.7411 | 60.1959 | 0.0018314 | 0.00099361 | 0.005735 | 0.060071 | 0.0067069 | 0.07647 | 0.0058755 | 0.017127 | 0.0075166 | 0.063152 | 0.033019 | 0.075738 | -46.9732 | -19.5309 | -49.2066 | 60.1572 | 60.0896 | 60.2865 | -62.8767 | -45.0718 | -16.3502 | -46.6264 | 60.0765 | 60.2727 | 60.1385 | -63.1366 | -0.13565 | -0.038719 | 15.7679 | 13.5345 | 13.6701 | -0.10634 | 0.090566 | -0.39553 | -0.11939 | 17.6693 | 16.1147 | 16.5102 | 0.076771 | -0.057385 | 122.8983 | 122.8307 | 123.0276 | 43.2102 | -123.0727 | 122.8176 | 123.0138 | 122.8796 | 46.3909 | -123.3325
1577.7969 | 123.1522 | -62.6816 | 60.2463 | 0.0018314 | 0.00077981 | 0.005735 | 0.059643 | 0.0064933 | 0.076897 | -0.001755 | 0.0167 | 0.0077302 | 0.063366 | 0.033233 | 0.075738 | -46.8725 | -19.4302 | -49.1242 | 60.2213 | 60.1354 | 60.3323 | -62.8172 | -45.0443 | -16.2495 | -46.489 | 60.1315 | 60.3231 | 59.9829 | -63.0954 | -0.13564 | -0.024976 | 15.8091 | 13.5574 | 13.693 | -0.1109 | 0.085998 | -0.41383 | -0.1148 | 17.6373 | 16.1925 | 16.6064 | 0.076782 | -0.26341 | 122.9029 | 122.817 | 123.0139 | 43.2514 | -123.0635 | 122.8131 | 123.0046 | 122.6644 | 46.4321 | -123.3417
1578.7969 | 123.1888 | -62.709 | 60.1822 | 0.0018314 | 0.00077981 | 0.005735 | 0.060284 | 0.0067069 | 0.076897 | -0.0093855 | 0.0167 | 0.0075166 | 0.063793 | 0.033233 | 0.075738 | -46.8771 | -19.4668 | -49.115 | 60.1618 | 60.0621 | 60.259 | -62.8813 | -45.0535 | -16.3182 | -46.5211 | 60.0674 | 60.2635 | 60.0561 | -63.1412 | -0.17228 | -0.020408 | 15.832 | 13.594 | 13.7663 | -0.12008 | 0.076827 | -0.43215 | -0.11482 | 17.6556 | 16.1879 | 16.6201 | 0.081347 | -0.12607 | 122.8708 | 122.7712 | 122.9681 | 43.2422 | -123.0635 | 122.7764 | 122.9726 | 122.7652 | 46.3909 | -123.3234
1579.7969 | 123.1888 | -62.6312 | 60.2554 | -0.0057996 | 0.00099361 | 0.005735 | 0.060498 | 0.0071343 | 0.077111 | -0.001755 | 0.017127 | 0.0077302 | 0.062939 | 0.033019 | 0.075738 | -46.7443 | -19.3707 | -48.9914 | 60.2442 | 60.1674 | 60.3597 | -62.7943 | -44.971 | -16.1854 | -46.4066 | 60.1498 | 60.346 | 60.166 | -63.0588 | -0.1631 | -0.011239 | 15.8869 | 13.6398 | 13.8029 | -0.088005 | 0.10431 | -0.42756 | -0.10565 | 17.6602 | 16.2246 | 16.6522 | 0.09052 | -0.089423 | 122.8754 | 122.7987 | 122.991 | 43.2606 | -123.0498 | 122.781 | 122.9772 | 122.7972 | 46.4458 | -123.3142
1580.7969 | 123.1338 | -62.59 | 60.3195 | 0.0094624 | 0.00077981 | 0.0055214 | 0.060284 | 0.0071343 | 0.077111 | 0.0058755 | 0.017341 | 0.0077302 | 0.063366 | 0.033446 | 0.075738 | -46.6436 | -19.302 | -48.877 | 60.3129 | 60.2132 | 60.4193 | -62.7348 | -44.9161 | -16.1671 | -46.3105 | 60.2093 | 60.4101 | 60.253 | -62.9993 | -0.14477 | -0.00665 | 15.9465 | 13.7131 | 13.8578 | -0.1063 | 0.099749 | -0.40923 | -0.11021 | 17.6739 | 16.2795 | 16.6888 | 0.090533 | -0.066516 | 122.9029 | 122.8032 | 123.0093 | 43.288 | -123.0543 | 122.7993 | 123.0001 | 122.843 | 46.423 | -123.3188
1581.7969 | 123.143 | -62.5626 | 60.3333 | -0.0057996 | 0.0012072 | 0.005735 | 0.060071 | 0.0071343 | 0.077538 | -0.0093855 | 0.017341 | 0.0077302 | 0.063793 | 0.032805 | 0.075951 | -46.5932 | -19.2745 | -48.8129 | 60.3083 | 60.227 | 60.4284 | -62.7302 | -44.9115 | -16.1167 | -46.3105 | 60.2139 | 60.4146 | 60.2301 | -62.9901 | -0.16766 | -0.024962 | 15.9694 | 13.7497 | 13.9173 | -0.1063 | 0.095173 | -0.42754 | -0.11937 | 17.651 | 16.2521 | 16.6796 | 0.081379 | -0.10314 | 122.8709 | 122.7895 | 122.991 | 43.2881 | -123.0635 | 122.7764 | 122.9772 | 122.7927 | 46.4459 | -123.3234
1582.7969 | 123.1338 | -62.5946 | 60.3378 | 0.0018314 | 0.0012072 | 0.005735 | 0.060284 | 0.0071343 | 0.077538 | -0.0093855 | 0.017341 | 0.0075166 | 0.06358 | 0.033233 | 0.075738 | -46.5337 | -19.2791 | -48.7579 | 60.2991 | 60.2178 | 60.4147 | -62.7348 | -44.8795 | -16.0755 | -46.2876 | 60.2093 | 60.4101 | 60.1935 | -63.0038 | -0.14019 | -0.038696 | 16.0609 | 13.8367 | 13.9769 | -0.12003 | 0.07686 | -0.40923 | -0.12852 | 17.7151 | 16.307 | 16.7163 | 0.072222 | -0.14435 | 122.8937 | 122.8124 | 123.0093 | 43.3155 | -123.0726 | 122.8039 | 123.0047 | 122.7881 | 46.5191 | -123.3417
1583.7969 | 123.1705 | -62.59 | 60.2966 | -0.0057996 | 0.00099361 | 0.005735 | 0.060071 | 0.0071343 | 0.077325 | 0.0058755 | 0.017127 | 0.0077302 | 0.06358 | 0.033446 | 0.076165 | -46.5016 | -19.2654 | -48.7076 | 60.2808 | 60.2086 | 60.401 | -62.7531 | -44.9298 | -16.1075 | -46.2418 | 60.2002 | 60.3917 | 60.1431 | -63.0222 | -0.16309 | -0.015811 | 16.0884 | 13.8824 | 14.0455 | -0.087993 | 0.10432 | -0.43212 | -0.096481 | 17.6602 | 16.3482 | 16.7804 | 0.095107 | -0.15351 | 122.8708 | 122.7987 | 122.991 | 43.3247 | -123.0497 | 122.7902 | 122.9818 | 122.7331 | 46.4825 | -123.3188
1584.7969 | 123.143 | -62.5534 | 60.3516 | 0.0018314 | 0.0012072 | 0.0055214 | 0.060071 | 0.0071343 | 0.077538 | -0.0093855 | 0.017555 | 0.0077302 | 0.06358 | 0.033446 | 0.075738 | -46.4421 | -19.215 | -48.616 | 60.3174 | 60.2407 | 60.4422 | -62.7165 | -44.9024 | -16.0938 | -46.2738 | 60.2276 | 60.4238 | 60.1614 | -62.9901 | -0.16308 | -0.034115 | 16.1113 | 13.9374 | 14.1005 | -0.11087 | 0.090599 | -0.43669 | -0.12394 | 17.651 | 16.2796 | 16.7163 | 0.072226 | -0.19013 | 122.8709 | 122.7941 | 122.9956 | 43.3384 | -123.068 | 122.781 | 122.9772 | 122.7148 | 46.4596 | -123.3417
1585.7969 | 123.1934 | -62.5992 | 60.2921 | -0.0057996 | 0.001421 | 0.0059488 | 0.060071 | 0.0073479 | 0.077752 | -0.0093855 | 0.017341 | 0.0077302 | 0.06358 | 0.033233 | 0.075738 | -46.4284 | -19.2196 | -48.6069 | 60.2762 | 60.1949 | 60.3872 | -62.7485 | -44.9253 | -16.1442 | -46.251 | 60.191 | 60.3872 | 60.2301 | -63.0176 | -0.14935 | -0.015811 | 16.1708 | 13.9923 | 14.1417 | -0.097152 | 0.095165 | -0.41839 | -0.10106 | 17.6739 | 16.3482 | 16.7666 | 0.095106 | -0.061943 | 122.8754 | 122.7941 | 122.9864 | 43.3796 | -123.0406 | 122.7902 | 122.9863 | 122.8293 | 46.455 | -123.3096
1586.7969 | 123.143 | -62.4435 | 60.4752 | 0.0018314 | 0.001421 | 0.0055214 | 0.060498 | 0.0069205 | 0.077325 | 0.0058755 | 0.016914 | 0.0075166 | 0.063366 | 0.033019 | 0.075738 | -46.2773 | -19.1234 | -48.4787 | 60.3724 | 60.2819 | 60.4879 | -62.6615 | -44.8291 | -16.0618 | -46.1548 | 60.278 | 60.4787 | 60.3125 | -62.9352 | -0.21799 | -0.10277 | 16.1662 | 13.9649 | 14.1829 | -0.19326 | 0.012788 | -0.49161 | -0.19718 | 17.6144 | 16.2887 | 16.7804 | 0.003572 | -0.16263 | 122.8159 | 122.7254 | 122.9315 | 43.3201 | -123.1367 | 122.7215 | 122.9223 | 122.7561 | 46.3818 | -123.4103
1587.7969 | 123.1384 | -62.4664 | 60.4477 | 0.0018314 | 0.001421 | 0.0055214 | 0.060498 | 0.0075615 | 0.077538 | 0.0058755 | 0.016914 | 0.0077302 | 0.063152 | 0.033446 | 0.075951 | -46.172 | -19.1097 | -48.3505 | 60.4273 | 60.3414 | 60.5475 | -62.602 | -44.7284 | -15.9885 | -46.0449 | 60.3421 | 60.5337 | 60.3492 | -62.871 | -0.13558 | -0.020365 | 16.2944 | 14.116 | 14.2515 | -0.10627 | 0.099776 | -0.40462 | -0.10561 | 17.7381 | 16.4215 | 16.8261 | 0.085982 | -0.09854 | 122.8938 | 122.8079 | 123.0139 | 43.3568 | -123.0497 | 122.8085 | 123.0001 | 122.8156 | 46.4779 | -123.3187
1588.7969 | 123.1613 | -62.3566 | 60.553 | -0.013431 | 0.0016346 | 0.005735 | 0.060498 | 0.0073479 | 0.077752 | 0.0058755 | 0.017127 | 0.0077302 | 0.063152 | 0.033446 | 0.075951 | -46.0575 | -19.0318 | -48.2223 | 60.5052 | 60.4101 | 60.6116 | -62.5379 | -44.678 | -15.9152 | -45.9991 | 60.4016 | 60.6024 | 60.4545 | -62.8069 | -0.18134 | -0.047818 | 16.299 | 14.1343 | 14.3156 | -0.14287 | 0.05859 | -0.45038 | -0.15138 | 17.6786 | 16.3574 | 16.8078 | 0.049375 | -0.098518 | 122.8617 | 122.7667 | 122.9681 | 43.3247 | -123.0909 | 122.7582 | 122.9589 | 122.811 | 46.4413 | -123.3599
1589.7969 | 123.1705 | -62.5259 | 60.3699 | -0.0057996 | 0.0016346 | 0.005735 | 0.060071 | 0.0075615 | 0.077752 | -0.001755 | 0.016914 | 0.0075166 | 0.063152 | 0.033446 | 0.076165 | -46.1537 | -19.1372 | -48.3093 | 60.3678 | 60.2911 | 60.4879 | -62.6707 | -44.8154 | -16.0205 | -46.109 | 60.278 | 60.4696 | 60.2851 | -62.9306 | -0.14475 | -0.002064 | 16.3723 | 14.2167 | 14.3614 | -0.078815 | 0.11807 | -0.40463 | -0.091889 | 17.7106 | 16.4169 | 16.8216 | 0.099701 | -0.08482 | 122.8937 | 122.817 | 123.0139 | 43.3888 | -123.0406 | 122.8039 | 122.9955 | 122.811 | 46.5054 | -123.3004
1590.7969 | 123.1201 | -62.2971 | 60.6491 | 0.0018314 | 0.0012072 | 0.0055214 | 0.060498 | 0.0071343 | 0.078179 | -0.001755 | 0.017127 | 0.0077302 | 0.063366 | 0.03366 | 0.075738 | -45.9248 | -18.922 | -48.062 | 60.5601 | 60.4788 | 60.6757 | -62.483 | -44.6139 | -15.8374 | -45.903 | 60.4749 | 60.6665 | 60.4957 | -62.7428 | -0.1859 | -0.089007 | 16.3723 | 14.235 | 14.4209 | -0.17032 | 0.026561 | -0.44579 | -0.17425 | 17.6832 | 16.3941 | 16.8399 | 0.017345 | -0.15344 | 122.8572 | 122.7759 | 122.9727 | 43.3751 | -123.1321 | 122.7719 | 122.9635 | 122.7927 | 46.4597 | -123.392
1591.7969 | 123.1384 | -62.2009 | 60.6903 | 0.0018314 | 0.0022756 | 0.005735 | 0.060498 | 0.0071343 | 0.077752 | -0.0093855 | 0.016914 | 0.0077302 | 0.06358 | 0.033874 | 0.075951 | -45.7187 | -18.7525 | -47.856 | 60.7249 | 60.6299 | 60.8313 | -62.3227 | -44.4353 | -15.7321 | -45.7748 | 60.6305 | 60.8175 | 60.6239 | -62.5917 | -0.12177 | 0.034616 | 16.4822 | 14.3449 | 14.4667 | -0.060409 | 0.14103 | -0.39081 | -0.05978 | 17.7656 | 16.4262 | 16.817 | 0.12724 | -0.066439 | 122.9259 | 122.8308 | 123.0323 | 43.4484 | -123.013 | 122.8315 | 123.0185 | 122.8248 | 46.4688 | -123.282
1592.7969 | 123.1705 | -62.1918 | 60.7269 | -0.013431 | 0.0018482 | 0.0059488 | 0.060925 | 0.0075615 | 0.077966 | -0.001755 | 0.017127 | 0.0077302 | 0.063366 | 0.033446 | 0.075951 | -45.7142 | -18.7113 | -47.8148 | 60.7066 | 60.6162 | 60.813 | -62.3364 | -44.4353 | -15.787 | -45.7702 | 60.6122 | 60.8084 | 60.6239 | -62.5963 | -0.14466 | -0.020319 | 16.4776 | 14.377 | 14.5216 | -0.11077 | 0.086099 | -0.40455 | -0.11471 | 17.7564 | 16.4216 | 16.8261 | 0.081462 | -0.10306 | 122.8984 | 122.8079 | 123.0048 | 43.4804 | -123.0634 | 122.804 | 123.0002 | 122.8156 | 46.4047 | -123.3233
1593.7969 | 123.1293 | -62.2238 | 60.6995 | -0.0057996 | 0.0016346 | 0.0063762 | 0.060712 | 0.0073479 | 0.077538 | -0.001755 | 0.017127 | 0.0077302 | 0.06358 | 0.03366 | 0.075951 | -45.7187 | -18.7754 | -47.8194 | 60.6562 | 60.5658 | 60.7718 | -62.3868 | -44.4811 | -15.8191 | -45.7931 | 60.5573 | 60.7534 | 60.6239 | -62.6421 | -0.16298 | -0.043215 | 16.5051 | 14.4044 | 14.5674 | -0.13367 | 0.072358 | -0.41829 | -0.14219 | 17.7427 | 16.4307 | 16.849 | 0.053985 | -0.075594 | 122.8801 | 122.7896 | 122.9956 | 43.4484 | -123.0863 | 122.7811 | 122.9773 | 122.8477 | 46.4047 | -123.3416
1594.7969 | 123.1567 | -62.2742 | 60.6628 | -0.0057996 | 0.002062 | 0.0061624 | 0.060498 | 0.0075615 | 0.078179 | -0.001755 | 0.017555 | 0.0077302 | 0.06358 | 0.033874 | 0.076379 | -45.7325 | -18.7938 | -47.8331 | 60.5921 | 60.5063 | 60.7077 | -62.4463 | -44.4857 | -15.842 | -45.8663 | 60.5023 | 60.6939 | 60.5323 | -62.7108 | -0.17216 | -0.070692 | 16.5417 | 14.441 | 14.6132 | -0.15657 | 0.044878 | -0.43662 | -0.16051 | 17.7885 | 16.4078 | 16.8444 | 0.031084 | -0.13054 | 122.8663 | 122.7804 | 122.9819 | 43.4804 | -123.1092 | 122.7765 | 122.9681 | 122.8065 | 46.4322 | -123.3736
1595.8594 | 123.0515 | -62.4435 | 60.5255 | -0.0057996 | 0.0018482 | 0.005735 | 0.060284 | 0.0075615 | 0.078179 | 0.0058755 | 0.016914 | 0.0075166 | 0.063366 | 0.033446 | 0.075951 | -45.7783 | -18.8533 | -47.8835 | 60.5097 | 60.4147 | 60.6161 | -62.5425 | -44.6002 | -16.3685 | -46.0129 | 60.4153 | 60.6069 | 60.3904 | -62.8069 | -0.098941 | -0.015774 | 16.6653 | 14.5601 | 14.659 | -0.11082 | 0.090635 | -0.36341 | -0.11017 | 17.8434 | 16.4307 | 16.7941 | 0.081419 | -0.13515 | 122.9533 | 122.8582 | 123.0597 | 43.5903 | -123.068 | 122.8589 | 123.0505 | 122.8339 | 46.075 | -123.3325
1596.7969 | 123.1293 | -62.4481 | 60.4797 | -0.0057996 | 0.0018482 | 0.005735 | 0.060498 | 0.0075615 | 0.078393 | -0.001755 | 0.016914 | 0.0075166 | 0.063793 | 0.03366 | 0.075951 | -45.7691 | -18.8807 | -47.8926 | 60.4456 | 60.3597 | 60.5704 | -62.5791 | -44.6551 | -16.4693 | -46.0861 | 60.3604 | 60.552 | 60.3308 | -62.8482 | -0.13099 | -0.034094 | 16.679 | 14.5555 | 14.6865 | -0.11999 | 0.090626 | -0.40004 | -0.11934 | 17.793 | 16.362 | 16.762 | 0.072253 | -0.1489 | 122.8938 | 122.8079 | 123.0185 | 43.5674 | -123.0589 | 122.8085 | 123.0001 | 122.779 | 45.9789 | -123.3279
1597.7969 | 123.1842 | -62.5031 | 60.3973 | -0.0057996 | 0.0018482 | 0.0061624 | 0.060284 | 0.0077753 | 0.078393 | -0.001755 | 0.0167 | 0.0077302 | 0.063366 | 0.033233 | 0.075951 | -45.7828 | -18.922 | -47.9018 | 60.409 | 60.3277 | 60.5246 | -62.6341 | -44.7238 | -16.515 | -46.1365 | 60.3238 | 60.5154 | 60.2851 | -62.8894 | -0.13101 | 0.011676 | 16.7202 | 14.6012 | 14.7323 | -0.069649 | 0.12724 | -0.38631 | -0.07357 | 17.7793 | 16.3666 | 16.7529 | 0.11802 | -0.11229 | 122.9121 | 122.8307 | 123.0276 | 43.5811 | -123.0314 | 122.8268 | 123.0184 | 122.7881 | 45.988 | -123.2867
1598.7969 | 123.1201 | -62.4527 | 60.4614 | -0.013431 | 0.002062 | 0.005735 | 0.059857 | 0.0077753 | 0.078179 | -0.001755 | 0.016914 | 0.0075166 | 0.063793 | 0.033446 | 0.075951 | -45.7187 | -18.8762 | -47.8331 | 60.4319 | 60.3506 | 60.552 | -62.602 | -44.6276 | -16.5379 | -46.1044 | 60.3375 | 60.5383 | 60.3263 | -62.8665 | -0.14931 | -0.029519 | 16.734 | 14.6196 | 14.7689 | -0.11084 | 0.090622 | -0.41377 | -0.12392 | 17.8251 | 16.3483 | 16.762 | 0.076827 | -0.13517 | 122.8846 | 122.8033 | 123.0047 | 43.5765 | -123.0634 | 122.7902 | 122.991 | 122.779 | 45.9148 | -123.3279
1599.7969 | 123.1659 | -62.5122 | 60.4156 | -0.021062 | 0.0022756 | 0.0059488 | 0.060498 | 0.0077753 | 0.078607 | -0.001755 | 0.016914 | 0.0079438 | 0.06358 | 0.033446 | 0.076165 | -45.7096 | -18.8807 | -47.8102 | 60.4044 | 60.3048 | 60.5108 | -62.6295 | -44.6322 | -16.5608 | -46.1411 | 60.3192 | 60.5062 | 60.34 | -62.9031 | -0.11728 | -0.011213 | 16.8026 | 14.702 | 14.8192 | -0.11085 | 0.095191 | -0.3909 | -0.096458 | 17.88 | 16.3711 | 16.762 | 0.090554 | -0.075653 | 122.9166 | 122.817 | 123.023 | 43.6315 | -123.0451 | 122.8314 | 123.0184 | 122.8522 | 45.9514 | -123.3188
1600.7969 | 123.1384 | -62.5168 | 60.3973 | 0.0094624 | 0.002062 | 0.0059488 | 0.060925 | 0.0075615 | 0.078179 | -0.0093855 | 0.016914 | 0.0077302 | 0.06358 | 0.03366 | 0.076379 | -45.6821 | -18.8991 | -47.7919 | 60.3907 | 60.3002 | 60.4971 | -62.6524 | -44.591 | -16.6066 | -46.2097 | 60.2917 | 60.4879 | 60.3034 | -62.9214 | -0.13559 | -0.006638 | 16.8347 | 14.7249 | 14.8605 | -0.097123 | 0.099765 | -0.40463 | -0.10562 | 17.9258 | 16.307 | 16.7117 | 0.09055 | -0.093972 | 122.9075 | 122.817 | 123.0139 | 43.6177 | -123.0497 | 122.8085 | 123.0047 | 122.8202 | 45.9102 | -123.3188
1601.7969 | 123.143 | -62.4847 | 60.4019 | 0.0094624 | 0.0022756 | 0.005735 | 0.060498 | 0.0077753 | 0.078607 | 0.0058755 | 0.017341 | 0.0075166 | 0.06422 | 0.033446 | 0.075951 | -45.6226 | -18.8212 | -47.7141 | 60.4044 | 60.3185 | 60.5246 | -62.6203 | -44.5177 | -16.5883 | -46.1823 | 60.31 | 60.5154 | 60.3217 | -62.8985 | -0.13558 | 0.002519 | 16.8622 | 14.7706 | 14.9062 | -0.083385 | 0.12266 | -0.41378 | -0.091883 | 17.967 | 16.3025 | 16.7162 | 0.11344 | -0.080235 | 122.8892 | 122.8033 | 123.0093 | 43.6635 | -123.0222 | 122.7948 | 123.0001 | 122.8064 | 45.8964 | -123.3004
1602.7969 | 123.1659 | -62.4161 | 60.5209 | 0.0018314 | 0.0024892 | 0.0059488 | 0.060712 | 0.0077753 | 0.078393 | -0.001755 | 0.016914 | 0.0077302 | 0.063152 | 0.034087 | 0.076379 | -45.5814 | -18.8258 | -47.6775 | 60.4228 | 60.3323 | 60.5292 | -62.6112 | -44.4308 | -16.689 | -46.1731 | 60.3329 | 60.5199 | 60.3263 | -62.8756 | -0.19509 | -0.098185 | 16.8347 | 14.7386 | 14.9337 | -0.18867 | 0.00822 | -0.45955 | -0.18801 | 17.9853 | 16.243 | 16.7025 | -0.000996 | -0.19468 | 122.8388 | 122.7483 | 122.9452 | 43.5903 | -123.1321 | 122.749 | 122.936 | 122.7423 | 45.727 | -123.3966
1603.7969 | 123.143 | -62.4115 | 60.466 | 0.0018314 | 0.0024892 | 0.0059488 | 0.060712 | 0.0077753 | 0.078607 | -0.001755 | 0.016914 | 0.0077302 | 0.06358 | 0.03366 | 0.075951 | -45.5539 | -18.7938 | -47.6317 | 60.4228 | 60.3323 | 60.5292 | -62.6157 | -44.4124 | -16.7257 | -46.2143 | 60.3238 | 60.5199 | 60.3217 | -62.8894 | -0.20425 | -0.043253 | 16.8576 | 14.7798 | 14.9841 | -0.13373 | 0.063152 | -0.47787 | -0.14223 | 17.9991 | 16.1972 | 16.675 | 0.053936 | -0.14432 | 122.8342 | 122.7438 | 122.9407 | 43.6177 | -123.0817 | 122.7353 | 122.9314 | 122.7332 | 45.6858 | -123.3554
1604.7969 | 123.1247 | -62.5671 | 60.3516 | 0.0018314 | 0.002703 | 0.005735 | 0.060712 | 0.0079889 | 0.078607 | -0.001755 | 0.017127 | 0.0077302 | 0.063366 | 0.033446 | 0.076379 | -45.5951 | -18.8624 | -47.6546 | 60.3403 | 60.2544 | 60.4559 | -62.6936 | -44.4445 | -16.9317 | -46.3196 | 60.2414 | 60.4375 | 60.2896 | -62.9672 | -0.12645 | -0.011223 | 16.972 | 14.9126 | 15.039 | -0.097135 | 0.10433 | -0.40007 | -0.11021 | 18.1227 | 16.2475 | 16.6476 | 0.085962 | -0.061931 | 122.9075 | 122.8216 | 123.023 | 43.7047 | -123.0451 | 122.8085 | 123.0047 | 122.8568 | 45.6354 | -123.3188
1605.7969 | 123.143 | -62.4619 | 60.466 | -0.0057996 | 0.002703 | 0.0059488 | 0.060498 | 0.0079889 | 0.07882 | -0.001755 | 0.017127 | 0.0075166 | 0.063793 | 0.03366 | 0.076165 | -45.4852 | -18.78 | -47.531 | 60.4228 | 60.3323 | 60.5383 | -62.6112 | -44.2659 | -16.8905 | -46.2418 | 60.3329 | 60.5291 | 60.3217 | -62.871 | -0.14931 | -0.043253 | 16.9766 | 14.9309 | 15.0802 | -0.13373 | 0.072309 | -0.4092 | -0.13308 | 18.1959 | 16.2201 | 16.6293 | 0.063093 | -0.14432 | 122.8846 | 122.7941 | 123.0002 | 43.6818 | -123.0772 | 122.7948 | 122.9909 | 122.7835 | 45.5714 | -123.3371
1606.7969 | 123.143 | -62.4802 | 60.4385 | -0.0057996 | 0.0024892 | 0.0061624 | 0.061139 | 0.0082025 | 0.078393 | -0.001755 | 0.017341 | 0.0077302 | 0.063366 | 0.033446 | 0.076592 | -45.5631 | -18.8579 | -47.5767 | 60.3358 | 60.2498 | 60.4559 | -62.7027 | -44.2751 | -16.9867 | -46.3517 | 60.2505 | 60.4375 | 60.2622 | -62.9718 | -0.22258 | -0.10278 | 16.9171 | 14.9034 | 15.126 | -0.18869 | 0.017359 | -0.49162 | -0.18803 | 18.2051 | 16.1285 | 16.6201 | -0.001014 | -0.17638 | 122.8159 | 122.73 | 122.9361 | 43.6223 | -123.1413 | 122.7307 | 122.9177 | 122.7423 | 45.4935 | -123.4103
1607.7969 | 123.1018 | -62.4207 | 60.4843 | -0.021062 | 0.0024892 | 0.005735 | 0.060498 | 0.0077753 | 0.079034 | -0.0093855 | 0.017127 | 0.0077302 | 0.06358 | 0.033874 | 0.076379 | -45.357 | -18.7159 | -47.3799 | 60.4868 | 60.3872 | 60.6024 | -62.5516 | -44.1194 | -16.9867 | -46.2235 | 60.397 | 60.584 | 60.3812 | -62.8207 | -0.13099 | 0.002533 | 17.0636 | 15.0408 | 15.1718 | -0.097098 | 0.1181 | -0.40003 | -0.087289 | 18.3013 | 16.1972 | 16.5972 | 0.099725 | -0.10311 | 122.9075 | 122.8079 | 123.0231 | 43.7047 | -123.036 | 122.8177 | 123.0047 | 122.8019 | 45.434 | -123.305
1608.7969 | 123.1705 | -62.4619 | 60.4614 | -0.0057996 | 0.002703 | 0.0061624 | 0.060284 | 0.0082025 | 0.079034 | 0.0058755 | 0.017555 | 0.0077302 | 0.06358 | 0.033233 | 0.076165 | -45.3525 | -18.7342 | -47.3433 | 60.4456 | 60.3552 | 60.552 | -62.5883 | -44.0874 | -17.0416 | -46.283 | 60.3512 | 60.5383 | 60.34 | -62.8573 | -0.12642 | -0.015784 | 17.1094 | 15.1186 | 15.245 | -0.10626 | 0.090622 | -0.39546 | -0.11019 | 18.3745 | 16.1788 | 16.5743 | 0.076827 | -0.12143 | 122.9075 | 122.817 | 123.0139 | 43.7276 | -123.0497 | 122.8131 | 123.0001 | 122.8018 | 45.4203 | -123.3187
1609.7969 | 123.1476 | -62.4298 | 60.4843 | -0.0057996 | 0.0031304 | 0.005735 | 0.060712 | 0.0082025 | 0.078393 | -0.001755 | 0.017127 | 0.0075166 | 0.063152 | 0.03366 | 0.076592 | -45.2884 | -18.6793 | -47.2929 | 60.4731 | 60.3735 | 60.5795 | -62.5608 | -44.0461 | -17.0324 | -46.2326 | 60.3741 | 60.5749 | 60.427 | -62.8298 | -0.13099 | -0.011202 | 17.1414 | 15.1369 | 15.2679 | -0.11083 | 0.095205 | -0.40003 | -0.11018 | 18.3837 | 16.1972 | 16.5972 | 0.090568 | -0.057325 | 122.9029 | 122.8033 | 123.0093 | 43.7505 | -123.0451 | 122.8039 | 123.0047 | 122.8568 | 45.3974 | -123.3142
1610.7969 | 123.1842 | -62.3383 | 60.5576 | 0.0018314 | 0.0024892 | 0.0059488 | 0.060284 | 0.0079889 | 0.07882 | -0.001755 | 0.017127 | 0.0073028 | 0.063366 | 0.033446 | 0.076379 | -45.1281 | -18.5831 | -47.1327 | 60.6013 | 60.5063 | 60.7077 | -62.4326 | -43.8355 | -16.9271 | -46.1548 | 60.5023 | 60.7031 | 60.5506 | -62.7016 | -0.094331 | 0.043751 | 17.2101 | 15.2056 | 15.2999 | -0.051288 | 0.15016 | -0.36338 | -0.055225 | 18.5027 | 16.1835 | 16.5468 | 0.14553 | -0.006944 | 122.9396 | 122.8445 | 123.046 | 43.7551 | -122.9901 | 122.8406 | 123.0413 | 122.8889 | 45.4111 | -123.2592
1611.7969 | 123.1705 | -63.1531 | 59.729 | -0.0057996 | 0.003344 | 0.0059488 | 0.060284 | 0.0077753 | 0.079034 | -0.001755 | 0.017127 | 0.0077302 | 0.063793 | 0.033446 | 0.076592 | -45.966 | -19.3936 | -47.9613 | 59.7085 | 59.6225 | 59.824 | -63.3255 | -44.6414 | -17.8383 | -47.0751 | 59.6233 | 59.8148 | 59.6395 | -63.5899 | -0.1724 | -0.020482 | 17.1871 | 15.1918 | 15.3642 | -0.10647 | 0.095046 | -0.43685 | -0.10575 | 18.5117 | 16.078 | 16.5148 | 0.08583 | -0.089534 | 122.8616 | 122.7756 | 122.9771 | 43.7595 | -123.0545 | 122.7763 | 122.9679 | 122.7925 | 45.3148 | -123.3189
1612.7969 | 123.1018 | -62.6404 | 60.3195 | -0.0057996 | 0.002703 | 0.0059488 | 0.060925 | 0.0079889 | 0.079248 | -0.0093855 | 0.017555 | 0.0075166 | 0.06358 | 0.03366 | 0.076379 | -45.3662 | -18.8762 | -47.3433 | 60.2808 | 60.1995 | 60.401 | -62.7531 | -44.0141 | -17.353 | -46.5257 | 60.1956 | 60.3826 | 60.1797 | -63.0176 | -0.11273 | -0.038699 | 17.2742 | 15.2971 | 15.4099 | -0.12004 | 0.081435 | -0.37719 | -0.12395 | 18.6263 | 16.1147 | 16.4919 | 0.063062 | -0.13977 | 122.9212 | 122.8399 | 123.0413 | 43.7642 | -123.0726 | 122.836 | 123.023 | 122.8201 | 45.2874 | -123.3371
1613.7969 | 123.1247 | -62.4435 | 60.4843 | 0.0018314 | 0.0029166 | 0.005735 | 0.060498 | 0.0079889 | 0.07882 | 0.0058755 | 0.017555 | 0.0075166 | 0.064007 | 0.03366 | 0.076592 | -45.238 | -18.7709 | -47.1967 | 60.377 | 60.2956 | 60.4971 | -62.6707 | -43.808 | -17.2156 | -46.4753 | 60.2871 | 60.4833 | 60.3354 | -62.9168 | -0.22715 | -0.10735 | 17.2055 | 15.2468 | 15.4739 | -0.18868 | 0.01279 | -0.4733 | -0.19717 | 18.6355 | 15.9682 | 16.4415 | -0.001004 | -0.1489 | 122.8205 | 122.7392 | 122.9406 | 43.6727 | -123.155 | 122.7307 | 122.9269 | 122.779 | 45.228 | -123.4012
1614.7969 | 123.1888 | -62.2559 | 60.6354 | 0.0094624 | 0.0029166 | 0.0059488 | 0.060498 | 0.0082025 | 0.079034 | -0.001755 | 0.017768 | 0.0077302 | 0.06358 | 0.03366 | 0.076806 | -45.0137 | -18.5831 | -46.9449 | 60.5876 | 60.5017 | 60.7031 | -62.4417 | -43.5059 | -16.9729 | -46.2876 | 60.4978 | 60.6893 | 60.514 | -62.7245 | -0.18589 | -0.047804 | 17.2422 | 15.3109 | 15.4968 | -0.13369 | 0.067765 | -0.46867 | -0.13762 | 18.75 | 15.9683 | 16.4369 | 0.053971 | -0.12139 | 122.8434 | 122.7575 | 122.959 | 43.6727 | -123.0771 | 122.7536 | 122.9452 | 122.7698 | 45.2829 | -123.3599
1615.7969 | 123.1979 | -62.3154 | 60.585 | 0.0018314 | 0.0031304 | 0.0061624 | 0.060712 | 0.0079889 | 0.079248 | 0.0058755 | 0.017555 | 0.0073028 | 0.06358 | 0.033233 | 0.07702 | -44.9999 | -18.5831 | -46.9312 | 60.5876 | 60.4925 | 60.6986 | -62.4509 | -43.4097 | -16.95 | -46.3334 | 60.4978 | 60.6985 | 60.5231 | -62.7108 | -0.13554 | 0.00255 | 17.3154 | 15.3842 | 15.5197 | -0.092491 | 0.11354 | -0.39542 | -0.08727 | 18.9057 | 15.982 | 16.3774 | 0.11348 | -0.061882 | 122.9029 | 122.8079 | 123.0139 | 43.7322 | -123.0359 | 122.8131 | 123.0139 | 122.8385 | 45.3653 | -123.2958
1616.7969 | 123.2208 | -62.3383 | 60.5484 | 0.0094624 | 0.0029166 | 0.0059488 | 0.060712 | 0.0079889 | 0.079461 | -0.001755 | 0.017555 | 0.0075166 | 0.06358 | 0.033446 | 0.07702 | -45.0411 | -18.6381 | -46.9816 | 60.496 | 60.4055 | 60.607 | -62.5287 | -43.4326 | -16.95 | -46.4249 | 60.4016 | 60.5978 | 60.3995 | -62.8024 | -0.19049 | -0.052397 | 17.2971 | 15.3567 | 15.5472 | -0.14287 | 0.05859 | -0.46411 | -0.1468 | 18.9057 | 15.9133 | 16.3774 | 0.049374 | -0.14888 | 122.8343 | 122.7438 | 122.9452 | 43.7002 | -123.0771 | 122.7399 | 122.936 | 122.7378 | 45.3882 | -123.3508
1617.7969 | 123.1338 | -63.2355 | 59.697 | -0.0057996 | 0.0029166 | 0.005735 | 0.060498 | 0.0082025 | 0.079248 | 0.013506 | 0.017982 | 0.0077302 | 0.064007 | 0.033446 | 0.077233 | -45.9385 | -19.476 | -47.8514 | 59.562 | 59.4714 | 59.6775 | -63.4583 | -44.2522 | -17.7696 | -47.3911 | 59.4676 | 59.6775 | 59.5067 | -63.7364 | -0.22279 | -0.13495 | 17.297 | 15.384 | 15.6068 | -0.22553 | -0.019425 | -0.50097 | -0.22937 | 18.9833 | 15.8444 | 16.3454 | -0.019484 | -0.19027 | 122.7975 | 122.7069 | 122.913 | 43.7595 | -123.1552 | 122.7031 | 122.9129 | 122.7422 | 45.4659 | -123.4334
1618.7969 | 123.1476 | -62.851 | 60.0861 | 0.0094624 | 0.0029166 | 0.0061624 | 0.060712 | 0.0079889 | 0.079675 | -0.0093855 | 0.017768 | 0.0073028 | 0.063366 | 0.033446 | 0.077233 | -45.5539 | -19.1188 | -47.4211 | 59.9466 | 59.8561 | 60.053 | -63.0828 | -43.8035 | -17.4125 | -47.0522 | 59.8476 | 60.0529 | 59.8821 | -63.3472 | -0.23184 | -0.13946 | 17.297 | 15.4299 | 15.6617 | -0.23 | -0.03308 | -0.4963 | -0.23845 | 19.0475 | 15.7987 | 16.295 | -0.033139 | -0.20392 | 122.7976 | 122.707 | 122.9039 | 43.7321 | -123.1689 | 122.6986 | 122.9039 | 122.7331 | 45.4385 | -123.4333
1619.7969 | 123.1247 | -62.6724 | 60.2234 | 0.0018314 | 0.003344 | 0.0059488 | 0.060712 | 0.0082025 | 0.079461 | -0.0093855 | 0.018196 | 0.0073028 | 0.063366 | 0.033446 | 0.077447 | -45.325 | -18.954 | -47.2013 | 60.148 | 60.0667 | 60.2499 | -62.8951 | -43.5425 | -17.2522 | -46.8325 | 60.0582 | 60.2406 | 60.047 | -63.1504 | -0.22264 | -0.075342 | 17.3474 | 15.4711 | 15.6937 | -0.1567 | 0.026471 | -0.47793 | -0.16517 | 19.1299 | 15.84 | 16.3179 | 0.017255 | -0.17642 | 122.8205 | 122.7391 | 122.9223 | 43.7184 | -123.1184 | 122.7306 | 122.9131 | 122.7194 | 45.4202 | -123.3737
1620.7969 | 123.1155 | -62.677 | 60.2783 | 0.0094624 | 0.003344 | 0.0061624 | 0.060284 | 0.0082025 | 0.079461 | 0.0058755 | 0.018409 | 0.0073028 | 0.06358 | 0.033446 | 0.077233 | -45.2701 | -18.9082 | -47.1281 | 60.1938 | 60.1125 | 60.3094 | -62.8447 | -43.3777 | -17.1606 | -46.8096 | 60.0994 | 60.2864 | 59.9966 | -63.1046 | -0.16769 | -0.084489 | 17.407 | 15.5489 | 15.7166 | -0.16584 | 0.031062 | -0.42757 | -0.1789 | 19.2994 | 15.8674 | 16.295 | 0.00811 | -0.28172 | 122.8708 | 122.7895 | 122.9864 | 43.7688 | -123.123 | 122.7764 | 122.9634 | 122.6736 | 45.5164 | -123.3829
1621.7969 | 123.1705 | -62.5031 | 60.3973 | 0.0094624 | 0.0031304 | 0.0059488 | 0.060498 | 0.0082025 | 0.079675 | -0.0093855 | 0.018196 | 0.0075166 | 0.063793 | 0.033233 | 0.077447 | -45.0549 | -18.7159 | -46.89 | 60.3815 | 60.2956 | 60.4971 | -62.6432 | -43.0892 | -16.9271 | -46.631 | 60.2963 | 60.4925 | 60.2713 | -62.9123 | -0.14017 | -0.015794 | 17.4482 | 15.613 | 15.7532 | -0.1017 | 0.099765 | -0.40921 | -0.10104 | 19.4139 | 15.8721 | 16.2813 | 0.095128 | -0.12602 | 122.8846 | 122.7987 | 123.0002 | 43.7871 | -123.0406 | 122.7994 | 122.9955 | 122.7744 | 45.5759 | -123.3096
1622.7969 | 123.1613 | -62.59 | 60.3058 | 0.0018314 | 0.0035576 | 0.0059488 | 0.060712 | 0.0079889 | 0.079675 | -0.0093855 | 0.018409 | 0.0077302 | 0.063366 | 0.033233 | 0.077447 | -45.1739 | -18.8533 | -47.0045 | 60.2442 | 60.1674 | 60.3552 | -62.7806 | -43.0892 | -16.9683 | -46.7638 | 60.1498 | 60.3505 | 60.1523 | -63.0542 | -0.19056 | -0.061593 | 17.4161 | 15.5856 | 15.7761 | -0.13836 | 0.049382 | -0.46418 | -0.156 | 19.5008 | 15.8263 | 16.2904 | 0.044744 | -0.15351 | 122.8342 | 122.7575 | 122.9452 | 43.7367 | -123.0864 | 122.7398 | 122.9406 | 122.7423 | 45.6217 | -123.36
1623.7969 | 123.1888 | -62.7914 | 60.1181 | -0.0057996 | 0.0035576 | 0.0061624 | 0.060712 | 0.0084163 | 0.079461 | 0.0058755 | 0.018623 | 0.0073028 | 0.063793 | 0.03366 | 0.077447 | -45.3113 | -18.9861 | -47.1235 | 60.1023 | 60.0255 | 60.2224 | -62.9363 | -43.1258 | -17.0416 | -46.8874 | 60.0124 | 60.2086 | 60.0103 | -63.1961 | -0.14483 | -0.01584 | 17.4802 | 15.6679 | 15.8128 | -0.092622 | 0.10429 | -0.4047 | -0.10567 | 19.6656 | 15.904 | 16.3088 | 0.090491 | -0.10777 | 122.8937 | 122.8169 | 123.0138 | 43.8054 | -123.0544 | 122.8039 | 123 | 122.8018 | 45.7498 | -123.3142
1624.7969 | 123.0972 | -62.7136 | 60.228 | -0.0057996 | 0.003344 | 0.0059488 | 0.060284 | 0.0082025 | 0.079675 | -0.001755 | 0.018409 | 0.0073028 | 0.063152 | 0.03366 | 0.077447 | -45.2243 | -18.9174 | -47.0136 | 60.1801 | 60.0987 | 60.3048 | -62.8447 | -42.9701 | -16.8447 | -46.7592 | 60.0994 | 60.291 | 60.1111 | -63.1183 | -0.13107 | -0.047871 | 17.4894 | 15.7 | 15.8311 | -0.12922 | 0.076837 | -0.40468 | -0.12854 | 19.7435 | 15.9544 | 16.3591 | 0.063043 | -0.1169 | 122.8937 | 122.8124 | 123.0184 | 43.7962 | -123.0727 | 122.813 | 123.0046 | 122.8247 | 45.8689 | -123.3463
1625.7969 | 123.0972 | -62.7365 | 60.2325 | 0.0094624 | 0.0031304 | 0.0059488 | 0.060498 | 0.0086299 | 0.079889 | -0.001755 | 0.01905 | 0.0073028 | 0.063793 | 0.033446 | 0.077874 | -45.2105 | -18.8807 | -47.0136 | 60.1709 | 60.0804 | 60.2819 | -62.8722 | -42.8374 | -16.8035 | -46.7638 | 60.0811 | 60.2727 | 60.0882 | -63.132 | -0.13565 | -0.061605 | 17.526 | 15.7229 | 15.8585 | -0.15212 | 0.049366 | -0.39553 | -0.15143 | 19.8991 | 15.9727 | 16.3683 | 0.04015 | -0.14437 | 122.9074 | 122.8169 | 123.0184 | 43.8558 | -123.1047 | 122.8176 | 123.0092 | 122.8247 | 45.933 | -123.3646
1626.7969 | 123.1659 | -62.7411 | 60.1501 | 0.0018314 | 0.003344 | 0.0061624 | 0.060498 | 0.0084163 | 0.079889 | -0.001755 | 0.01905 | 0.0075166 | 0.063152 | 0.033446 | 0.078088 | -45.1785 | -18.8853 | -46.977 | 60.1664 | 60.0804 | 60.2911 | -62.8584 | -42.6817 | -16.6341 | -46.6997 | 60.0857 | 60.2773 | 60.0928 | -63.1275 | -0.11734 | 0.016214 | 17.5626 | 15.7641 | 15.8814 | -0.069718 | 0.14092 | -0.38638 | -0.064459 | 20.0594 | 16.0414 | 16.4278 | 0.12713 | -0.057395 | 122.9074 | 122.8215 | 123.0322 | 43.8558 | -123.0086 | 122.8268 | 123.0184 | 122.8338 | 46.107 | -123.2776
1627.7969 | 123.1659 | -62.796 | 60.0998 | 0.0018314 | 0.0035576 | 0.0061624 | 0.060712 | 0.0084163 | 0.079461 | 0.013506 | 0.01905 | 0.0075166 | 0.063793 | 0.033874 | 0.077447 | -45.2334 | -18.9677 | -47.0411 | 60.0839 | 59.9843 | 60.1949 | -62.95 | -42.6679 | -16.7257 | -46.7592 | 59.9941 | 60.1811 | 60.0149 | -63.2236 | -0.15399 | -0.015843 | 17.5626 | 15.7549 | 15.9089 | -0.11552 | 0.095125 | -0.4276 | -0.10567 | 20.1281 | 16.0368 | 16.4644 | 0.08133 | -0.084877 | 122.88 | 122.7803 | 122.9909 | 43.8283 | -123.0498 | 122.7901 | 122.9771 | 122.8109 | 46.0704 | -123.3234
1628.7969 | 123.0972 | -62.7594 | 60.1868 | -0.0057996 | 0.003344 | 0.0059488 | 0.060925 | 0.0084163 | 0.079889 | -0.001755 | 0.019264 | 0.0077302 | 0.06358 | 0.03366 | 0.078088 | -45.1464 | -19.0135 | -46.9861 | 60.1114 | 60.0392 | 60.227 | -62.918 | -42.5123 | -16.4784 | -46.6676 | 60.0216 | 60.2178 | 60.0195 | -63.1824 | -0.15855 | -0.075348 | 17.613 | 15.7733 | 15.9318 | -0.14755 | 0.040199 | -0.42301 | -0.16518 | 20.2471 | 16.0918 | 16.5148 | 0.030983 | -0.16727 | 122.8708 | 122.7986 | 122.9864 | 43.7459 | -123.1047 | 122.781 | 122.9771 | 122.7789 | 46.281 | -123.3692
1629.7969 | 123.0103 | -62.9562 | 59.9991 | -0.0057996 | 0.003344 | 0.0065898 | 0.060071 | 0.0084163 | 0.079889 | -0.001755 | 0.019477 | 0.0075166 | 0.063793 | 0.033446 | 0.077874 | -45.2472 | -19.1051 | -47.0869 | 59.9878 | 59.911 | 60.1033 | -63.0462 | -42.5535 | -16.3182 | -46.6722 | 59.898 | 60.085 | 59.8592 | -63.3198 | -0.089926 | -0.011281 | 17.7091 | 15.8694 | 15.9593 | -0.088076 | 0.10426 | -0.36354 | -0.10112 | 20.4028 | 16.284 | 16.6476 | 0.085888 | -0.13984 | 122.944 | 122.8672 | 123.0596 | 43.8511 | -123.0452 | 122.8542 | 123.0412 | 122.8155 | 46.6381 | -123.3189
1630.8125 | 123.1522 | -64.064 | 58.8455 | -0.013431 | 0.0037714 | 0.0059488 | 0.060498 | 0.0086299 | 0.079889 | -0.0093855 | 0.034859 | 0.0070892 | 0.06358 | 0.033874 | 0.089839 | -46.1354 | -20.0208 | -47.9888 | 59.0401 | 58.9677 | 59.1602 | -64.0215 | -24.5134 | -16.6249 | -47.5238 | 58.9365 | 59.1326 | 58.9389 | -64.1211 | 0.042551 | 0.19456 | 17.9287 | 16.0752 | 16.0327 | 0.12223 | 0.31463 | -0.057041 | 0.090965 | 39.5507 | 16.5402 | 16.5972 | 0.2871 | 0.093424 | 123.1041 | 123.0318 | 123.2242 | 44.0432 | -122.867 | 123.0005 | 123.1966 | 123.003 | 47.4391 | -122.9666
1631.7969 | 123.1934 | -67.4927 | 55.3802 | 0.0094624 | 0.0035576 | 0.0061624 | 0.060925 | 0.0084163 | 0.080102 | 0.0058755 | 0.087628 | 0.0030296 | 0.063366 | 0.034087 | 0.14047 | -49.9034 | -23.6288 | -51.7384 | 55.1576 | 55.0711 | 55.2729 | -67.8678 | 55.0188 | -18.5159 | -50.9716 | 55.0631 | 55.25 | 55.0288 | -68.1367 | -0.3751 | -0.22264 | 17.5893 | 15.7543 | 16.1294 | -0.30917 | -0.10733 | -0.64401 | -0.31717 | 122.5115 | 16.5211 | 17.1651 | -0.13028 | -0.35143 | 122.6503 | 122.5638 | 122.7656 | 43.8639 | -123.248 | 122.5558 | 122.7426 | 122.5215 | 48.9767 | -123.5169
1632.7969 | 123.0331 | -67.6758 | 55.307 | 0.0094624 | 0.003344 | 0.0059488 | 0.060284 | 0.0086299 | 0.080102 | -0.0093855 | 0.088482 | 0.0026024 | 0.063152 | 0.034301 | 0.14154 | -49.7981 | -23.5692 | -51.656 | 55.2263 | 55.1443 | 55.3553 | -67.7991 | 55.1424 | -18.3969 | -50.8571 | 55.1272 | 55.3232 | 55.1387 | -68.0634 | -0.12331 | -0.080727 | 17.8777 | 16.0198 | 16.1431 | -0.16266 | 0.048327 | -0.38765 | -0.17983 | 122.8182 | 16.8186 | 17.2063 | 0.016218 | -0.1683 | 122.9021 | 122.8201 | 123.0311 | 44.1065 | -123.1061 | 122.803 | 122.999 | 122.8145 | 49.2789 | -123.3704
1633.7969 | 123.1796 | -67.6712 | 55.1926 | -0.0057996 | 0.003344 | 0.0059488 | 0.060925 | 0.0086299 | 0.080316 | 0.0058755 | 0.087842 | 0.002816 | 0.063366 | 0.034087 | 0.1409 | -49.7752 | -23.5738 | -51.6651 | 55.2125 | 55.1215 | 55.3324 | -67.8082 | 55.1333 | -18.2824 | -50.8022 | 55.1226 | 55.3049 | 55.0746 | -68.0772 | -0.13704 | 0.019979 | 17.896 | 16.0061 | 16.1431 | -0.071113 | 0.13988 | -0.40596 | -0.069967 | 122.8045 | 16.869 | 17.275 | 0.11234 | -0.11796 | 122.8837 | 122.7927 | 123.0036 | 44.0974 | -123.0008 | 122.7938 | 122.9761 | 122.7458 | 49.3888 | -123.2697
1634.7969 | 123.0515 | -67.7353 | 55.2292 | 0.0018314 | 0.0037714 | 0.0059488 | 0.060712 | 0.0086299 | 0.080316 | -0.001755 | 0.089337 | 0.0026024 | 0.063366 | 0.034087 | 0.14218 | -49.8118 | -23.5876 | -51.6468 | 55.1759 | 55.0802 | 55.2958 | -67.8495 | 55.1058 | -18.2412 | -50.7839 | 55.0768 | 55.2729 | 55.1158 | -68.1184 | -0.11416 | -0.053269 | 17.9235 | 16.0885 | 16.2026 | -0.14895 | 0.066625 | -0.38308 | -0.15237 | 122.8411 | 16.9514 | 17.3345 | 0.043673 | -0.11338 | 122.9112 | 122.8155 | 123.0311 | 44.1477 | -123.0786 | 122.8121 | 123.0082 | 122.8511 | 49.4941 | -123.3476
1635.8125 | 123.1247 | -67.8864 | 54.9957 | 0.0018314 | 0.003985 | 0.0059488 | 0.060925 | 0.0086299 | 0.080102 | -0.001755 | 0.088055 | 0.0026024 | 0.062939 | 0.034515 | 0.14069 | -49.9949 | -23.7524 | -51.8483 | 54.947 | 54.8605 | 55.076 | -68.0784 | 54.886 | -18.3648 | -50.9579 | 54.8479 | 55.0439 | 54.9006 | -68.3382 | -0.19205 | -0.04873 | 17.8914 | 16.0381 | 16.2301 | -0.13527 | 0.080311 | -0.45181 | -0.14784 | 122.7724 | 16.9285 | 17.3803 | 0.048202 | -0.095112 | 122.8334 | 122.7468 | 122.9624 | 44.134 | -123.0741 | 122.7342 | 122.9303 | 122.787 | 49.5215 | -123.3339
1636.7969 | 123.0927 | -67.8223 | 55.1056 | -0.0057996 | 0.003344 | 0.0063762 | 0.060712 | 0.0084163 | 0.080316 | -0.001755 | 0.089123 | 0.002816 | 0.063366 | 0.034087 | 0.14176 | -49.9446 | -23.6883 | -51.7338 | 55.0157 | 54.9383 | 55.1447 | -68.0143 | 54.9456 | -18.2183 | -50.793 | 54.9211 | 55.108 | 54.9693 | -68.2649 | -0.19203 | -0.089917 | 17.8777 | 16.0884 | 16.2805 | -0.16729 | 0.039127 | -0.44263 | -0.18445 | 122.7678 | 17.0292 | 17.4719 | 0.00244 | -0.1363 | 122.8379 | 122.7606 | 122.967 | 44.134 | -123.1199 | 122.7434 | 122.9303 | 122.7916 | 49.6039 | -123.3705
1637.7969 | 123.056 | -67.9321 | 54.982 | 0.0094624 | 0.0037714 | 0.0061624 | 0.060284 | 0.0086299 | 0.079889 | -0.001755 | 0.089337 | 0.0026024 | 0.063152 | 0.034301 | 0.14261 | -49.9308 | -23.6929 | -51.7247 | 54.9974 | 54.9108 | 55.1172 | -68.028 | 54.9273 | -18.1542 | -50.7152 | 54.8983 | 55.0943 | 54.9464 | -68.2832 | -0.095905 | 0.015365 | 18.0013 | 16.2075 | 16.3034 | -0.071173 | 0.13525 | -0.35108 | -0.083743 | 122.8594 | 17.2169 | 17.568 | 0.1123 | -0.035593 | 122.9295 | 122.843 | 123.0494 | 44.2393 | -123.01 | 122.8304 | 123.0264 | 122.8785 | 49.7779 | -123.2652
1638.7969 | 123.0469 | -68.0603 | 54.895 | -0.0057996 | 0.003344 | 0.0059488 | 0.060498 | 0.0088435 | 0.080316 | -0.001755 | 0.089337 | 0.0026024 | 0.063366 | 0.034515 | 0.14176 | -50.0819 | -23.8165 | -51.8254 | 54.8554 | 54.7735 | 54.9753 | -68.17 | 54.7945 | -18.1359 | -50.6969 | 54.7655 | 54.9524 | 54.8136 | -68.4252 | -0.10968 | -0.03959 | 17.9784 | 16.2349 | 16.3446 | -0.12157 | 0.08029 | -0.36485 | -0.12954 | 122.8548 | 17.3634 | 17.7283 | 0.057338 | -0.081397 | 122.9157 | 122.8338 | 123.0356 | 44.2438 | -123.065 | 122.8258 | 123.0127 | 122.8739 | 49.9244 | -123.3202
1639.7969 | 123.0698 | -68.0786 | 54.8355 | -0.0057996 | 0.0035576 | 0.0061624 | 0.060498 | 0.0086299 | 0.080316 | -0.0093855 | 0.089551 | 0.002816 | 0.06358 | 0.034942 | 0.14197 | -50.0957 | -23.8668 | -51.8391 | 54.8142 | 54.7231 | 54.9433 | -68.2066 | 54.7533 | -18.168 | -50.5366 | 54.7197 | 54.902 | 54.7541 | -68.4664 | -0.128 | -0.021285 | 17.9829 | 16.2395 | 16.3675 | -0.11242 | 0.10775 | -0.38775 | -0.11582 | 122.8319 | 17.542 | 17.9297 | 0.066483 | -0.081409 | 122.8928 | 122.8017 | 123.0219 | 44.2118 | -123.0421 | 122.7983 | 122.9806 | 122.8327 | 49.9107 | -123.3019
1640.8125 | 123.0606 | -68.2983 | 54.657 | -0.0057996 | 0.003985 | 0.0061624 | 0.060284 | 0.0088435 | 0.080102 | 0.0058755 | 0.090832 | 0.0026024 | 0.064007 | 0.034942 | 0.14325 | -50.2513 | -24.0225 | -52.0131 | 54.6357 | 54.572 | 54.7739 | -68.376 | 54.593 | -18.3511 | -50.5092 | 54.5411 | 54.7463 | 54.6167 | -68.6312 | -0.077693 | -0.021314 | 18.047 | 16.2852 | 16.3629 | -0.085 | 0.11687 | -0.33286 | -0.11585 | 122.8913 | 17.7892 | 18.122 | 0.089339 | -0.040239 | 122.934 | 122.8703 | 123.0722 | 44.2758 | -123.033 | 122.8395 | 123.0447 | 122.9151 | 49.9472 | -123.2882
1641.7969 | 123.0789 | -68.0695 | 54.8538 | -0.0057996 | 0.0035576 | 0.0065898 | 0.060498 | 0.0088435 | 0.080316 | 0.013506 | 0.089764 | 0.002816 | 0.06422 | 0.034942 | 0.1424 | -50.0728 | -23.8119 | -51.7567 | 54.8051 | 54.7277 | 54.9341 | -68.202 | 54.7441 | -18.1313 | -50.1245 | 54.7151 | 54.9066 | 54.777 | -68.4618 | -0.13258 | -0.048753 | 17.9967 | 16.3127 | 16.4453 | -0.12616 | 0.080281 | -0.39233 | -0.13871 | 122.8136 | 17.9449 | 18.3372 | 0.052751 | -0.076827 | 122.8745 | 122.7971 | 123.0036 | 44.2576 | -123.0559 | 122.7846 | 122.976 | 122.8465 | 49.9381 | -123.3156
1642.7969 | 123.0331 | -68.161 | 54.7577 | 0.0018314 | 0.003985 | 0.0059488 | 0.060498 | 0.0088435 | 0.080102 | 0.0058755 | 0.11754 | 0.0030296 | 0.064434 | 0.034942 | 0.1706 | -50.1918 | -23.9676 | -51.8986 | 54.6586 | 54.5766 | 54.7922 | -68.3577 | 54.593 | -18.3191 | -50.065 | 54.564 | 54.7601 | 54.6259 | -68.6129 | -0.19671 | -0.09913 | 17.9692 | 16.2624 | 16.4591 | -0.18113 | 0.034476 | -0.45188 | -0.19367 | 122.754 | 18.096 | 18.5479 | 0.002367 | -0.13179 | 122.8196 | 122.7376 | 122.9532 | 44.1934 | -123.1154 | 122.725 | 122.9211 | 122.7869 | 49.842 | -123.3706
1643.7969 | 123.0469 | -62.59 | 60.3241 | -0.013431 | 0.003985 | 0.0061624 | 0.060498 | 0.0088435 | 0.08053 | -0.001755 | 0.032509 | -0.0038074 | -0.0075654 | 0.022976 | -0.0056639 | -44.6611 | -18.7113 | -46.3269 | 60.2991 | 60.2224 | 60.4238 | -62.7165 | 0.13383 | 0.027831 | -0.1113 | 0.25849 | 0.42578 | 0.41525 | -0.40683 | -0.12645 | -0.024963 | 17.9289 | 16.2632 | 16.3896 | -0.10172 | 0.09975 | 62.1832 | -60.0656 | 62.7239 | 62.4787 | 0.29553 | -59.8983 | -59.9089 | 122.8892 | 122.8124 | 123.0139 | 43.8787 | -123.0406 | 62.8485 | 63.0158 | 63.0053 | 62.6179 | -60.7309
1644.7969 | 123.1201 | -62.5122 | 60.3745 | -0.013431 | 0.0037714 | 0.0059488 | 0.060712 | 0.0088435 | 0.080102 | -0.001755 | 0.032509 | -0.004021 | -0.007779 | 0.02319 | -0.0058775 | -44.6153 | -18.7113 | -46.2765 | 60.3403 | 60.2544 | 60.4605 | -62.6661 | 0.042256 | 0.023253 | -0.079245 | 0.15318 | 0.34337 | 0.33741 | -0.36104 | -0.15391 | -0.034112 | 17.8969 | 16.2357 | 16.3896 | -0.12002 | 0.086025 | 62.1512 | -60.2213 | 62.5545 | 62.433 | 0.28179 | -60.0311 | -60.037 | 122.8525 | 122.7666 | 122.9727 | 43.8009 | -123.0406 | 62.6654 | 62.8556 | 62.8496 | 62.5355 | -60.7355
1645.8125 | 123.1064 | -62.5717 | 60.3653 | 0.017093 | 0.0037714 | 0.0061624 | 0.060712 | 0.0090573 | 0.08053 | -0.001755 | 0.032296 | -0.0035938 | -0.0075654 | 0.023617 | -0.0058775 | -44.6428 | -18.7251 | -46.2674 | 60.3403 | 60.2682 | 60.4605 | -62.6799 | 0.001048 | 0.023253 | -0.028879 | 0.12571 | 0.30216 | 0.29162 | -0.36104 | -0.10813 | -0.024956 | 17.9289 | 16.3044 | 16.4125 | -0.097131 | 0.095181 | 62.2107 | -60.2396 | 62.5728 | 62.5428 | 0.33216 | -60.0631 | -60.0737 | 122.9121 | 122.8399 | 123.0322 | 43.8466 | -123.0451 | 62.6974 | 62.8739 | 62.8633 | 62.595 | -60.7263
1646.7969 | 123.056 | -62.5305 | 60.4248 | -0.0057996 | 0.003985 | 0.0063762 | 0.060712 | 0.0084163 | 0.080102 | 0.0058755 | 0.032082 | -0.0038074 | -0.0073516 | 0.023617 | -0.0063049 | -44.6016 | -18.7709 | -46.2307 | 60.3678 | 60.2865 | 60.4834 | -62.6615 | -0.00811 | 0.018674 | -0.028879 | 0.12114 | 0.293 | 0.28704 | -0.35188 | -0.13102 | -0.056996 | 17.9289 | 16.2998 | 16.4308 | -0.13833 | 0.058564 | 62.1786 | -60.3037 | 62.5224 | 62.5016 | 0.323 | -60.1318 | -60.1378 | 122.8983 | 122.817 | 123.0139 | 43.7597 | -123.0863 | 62.6517 | 62.8235 | 62.8176 | 62.5492 | -60.7767
1647.7969 | 123.1247 | -62.471 | 60.4294 | -0.0057996 | 0.0041986 | 0.0061624 | 0.060712 | 0.0088435 | 0.080316 | 0.0058755 | 0.032296 | -0.0042346 | -0.0075654 | 0.02319 | -0.0056639 | -44.597 | -18.7297 | -46.1895 | 60.3907 | 60.2956 | 60.52 | -62.6386 | -0.00811 | 0.014095 | -0.042615 | 0.1074 | 0.28842 | 0.28247 | -0.35646 | -0.16763 | -0.038681 | 17.874 | 16.2815 | 16.4491 | -0.13374 | 0.090615 | 62.1145 | -60.322 | 62.4629 | 62.4284 | 0.31384 | -60.141 | -60.1469 | 122.8617 | 122.7666 | 122.991 | 43.7414 | -123.068 | 62.5784 | 62.7594 | 62.7535 | 62.4851 | -60.7858
1648.7969 | 123.0469 | -62.5534 | 60.434 | -0.0057996 | 0.003985 | 0.0059488 | 0.060498 | 0.0088435 | 0.079889 | -0.001755 | 0.032296 | -0.0038074 | -0.007779 | 0.023404 | -0.0058775 | -44.5741 | -18.7068 | -46.1849 | 60.3999 | 60.3185 | 60.5154 | -62.6432 | -0.00811 | 0.018674 | -0.028879 | 0.11198 | 0.293 | 0.28704 | -0.35188 | -0.089813 | -0.034102 | 17.9793 | 16.3685 | 16.4583 | -0.11543 | 0.081459 | 62.2015 | -60.322 | 62.5453 | 62.5245 | 0.323 | -60.141 | -60.1469 | 122.9533 | 122.8719 | 123.0688 | 43.8466 | -123.0772 | 62.6654 | 62.8464 | 62.8405 | 62.5721 | -60.7858
1649.7969 | 123.0881 | -62.5122 | 60.4523 | 0.0094624 | 0.0037714 | 0.005735 | 0.060498 | 0.0090573 | 0.080316 | 0.0058755 | 0.032296 | -0.0035938 | -0.007779 | 0.02319 | -0.0056639 | -44.6016 | -18.7297 | -46.2078 | 60.3815 | 60.2911 | 60.4879 | -62.6615 | -0.00811 | 0.009516 | -0.042615 | 0.10282 | 0.27926 | 0.26873 | -0.35188 | -0.14933 | -0.070726 | 17.9106 | 16.3044 | 16.4537 | -0.16121 | 0.035676 | 62.1603 | -60.3494 | 62.5041 | 62.4696 | 0.30927 | -60.173 | -60.1835 | 122.8938 | 122.8033 | 123.0002 | 43.7826 | -123.1138 | 62.615 | 62.7915 | 62.7809 | 62.5217 | -60.8042
1650.8125 | 123.1247 | -62.5122 | 60.4431 | -0.0057996 | 0.0037714 | 0.0063762 | 0.060498 | 0.0090573 | 0.080316 | -0.0093855 | 0.032082 | -0.0035938 | -0.0073516 | 0.02319 | -0.0058775 | -44.5604 | -18.78 | -46.1712 | 60.409 | 60.3368 | 60.5337 | -62.6341 | -0.017267 | 0.018674 | -0.038036 | 0.098244 | 0.28384 | 0.26873 | -0.3473 | -0.12185 | -0.0341 | 17.9518 | 16.341 | 16.4628 | -0.10627 | 0.090618 | 62.1649 | -60.3449 | 62.4949 | 62.4742 | 0.30927 | -60.1593 | -60.1744 | 122.9212 | 122.8491 | 123.0459 | 43.7322 | -123.0772 | 62.6105 | 62.7961 | 62.7809 | 62.5309 | -60.7904
1651.7969 | 123.1064 | -62.4573 | 60.498 | -0.0057996 | 0.0041986 | 0.0063762 | 0.060712 | 0.0090573 | 0.08053 | -0.0093855 | 0.032296 | -0.004021 | -0.0075654 | 0.02319 | -0.0060913 | -44.4734 | -18.6884 | -46.0796 | 60.4731 | 60.4055 | 60.5933 | -62.5654 | -0.017267 | 0.014095 | -0.038036 | 0.093665 | 0.27926 | 0.27331 | -0.35188 | -0.1081 | -0.024935 | 17.9839 | 16.3776 | 16.4857 | -0.092515 | 0.095208 | 62.1054 | -60.4044 | 62.44 | 62.4192 | 0.31384 | -60.2188 | -60.2247 | 122.9304 | 122.8628 | 123.0505 | 43.7688 | -123.0634 | 62.5509 | 62.7365 | 62.7306 | 62.4714 | -60.8499
1652.7969 | 123.0789 | -62.4252 | 60.5255 | -0.0057996 | 0.0035576 | 0.0063762 | 0.060925 | 0.0086299 | 0.080316 | -0.0093855 | 0.032082 | -0.004021 | -0.0075654 | 0.02319 | -0.0060913 | -44.4459 | -18.7022 | -46.0751 | 60.4914 | 60.4101 | 60.607 | -62.5562 | -0.017267 | 0.018674 | -0.042615 | 0.093665 | 0.27469 | 0.26873 | -0.35646 | -0.13099 | -0.034087 | 17.9793 | 16.3502 | 16.4812 | -0.1154 | 0.081478 | 62.0688 | -60.4318 | 62.408 | 62.3826 | 0.31384 | -60.2508 | -60.2568 | 122.9167 | 122.8353 | 123.0322 | 43.723 | -123.0817 | 62.5189 | 62.6999 | 62.694 | 62.4439 | -60.882
1653.7969 | 123.0652 | -62.4527 | 60.5484 | -0.0057996 | 0.0037714 | 0.0061624 | 0.060498 | 0.0090573 | 0.079889 | 0.0058755 | 0.032296 | -0.0035938 | -0.0075654 | 0.023404 | -0.0060913 | -44.5467 | -18.922 | -46.1163 | 60.4548 | 60.3735 | 60.5704 | -62.5974 | -0.021846 | 0.014095 | -0.038036 | 0.098244 | 0.27011 | 0.26873 | -0.36562 | -0.14473 | -0.093602 | 17.906 | 16.3364 | 16.4812 | -0.17492 | 0.021961 | 62.0871 | -60.4502 | 62.4309 | 62.4147 | 0.32758 | -60.2783 | -60.2797 | 122.9075 | 122.8262 | 123.0231 | 43.5307 | -123.1458 | 62.5509 | 62.7228 | 62.7214 | 62.4668 | -60.914
1654.7969 | 123.0835 | -62.3428 | 60.6628 | -0.0057996 | 0.0037714 | 0.0061624 | 0.060498 | 0.0088435 | 0.08053 | -0.001755 | 0.032509 | -0.0035938 | -0.007779 | 0.02319 | -0.0060913 | -45.3158 | -19.0639 | -46.0384 | 60.5876 | 60.5154 | 60.7169 | -62.4646 | -0.017267 | 0.009516 | -0.047194 | 0.093665 | 0.27469 | -0.074664 | -0.35188 | -0.12181 | -0.07527 | 17.027 | 16.3044 | 16.4262 | -0.14742 | 0.054035 | 61.991 | -60.5692 | 62.3256 | 62.2956 | 0.30469 | -60.3882 | -60.7375 | 122.9304 | 122.8583 | 123.0597 | 43.2789 | -123.1275 | 62.4365 | 62.6175 | 62.2682 | 62.3524 | -61.0147
1655.8125 | 123.1064 | -62.2604 | 60.6995 | -0.0057996 | 0.003344 | 0.0061624 | 0.060284 | 0.0090573 | 0.080102 | 0.013506 | 0.032296 | -0.0038074 | -0.0073516 | 0.022976 | -0.0060913 | -45.3982 | -19.1005 | -45.9972 | 60.6242 | 60.5475 | 60.7443 | -62.428 | -0.026425 | 0.000359 | -0.047194 | 0.07993 | 0.26553 | -0.0884 | -0.35646 | -0.16757 | -0.075264 | 16.8622 | 16.2632 | 16.4308 | -0.15199 | 0.044886 | 61.904 | -60.6195 | 62.234 | 62.2132 | 0.30927 | -60.4339 | -60.7879 | 122.8846 | 122.8079 | 123.0048 | 43.1599 | -123.1275 | 62.3404 | 62.526 | 62.172 | 62.2608 | -61.0559
1656.7969 | 123.0331 | -62.3291 | 60.6583 | -0.0057996 | 0.0035576 | 0.0061624 | 0.060071 | 0.0088435 | 0.08053 | 0.013506 | 0.032937 | -0.0038074 | -0.0073516 | 0.023404 | -0.0058775 | -45.7645 | -19.1921 | -46.0568 | 60.5921 | 60.5063 | 60.7123 | -62.4555 | -0.026425 | 0.009516 | -0.06093 | 0.070773 | 0.25637 | -0.0884 | -0.3702 | -0.12638 | -0.066114 | 16.5646 | 16.2723 | 16.3987 | -0.152 | 0.054035 | 61.9589 | -60.5875 | 62.3027 | 62.2682 | 0.30927 | -60.4019 | -60.7467 | 122.9213 | 122.8354 | 123.0414 | 43.137 | -123.1137 | 62.3999 | 62.5855 | 62.2407 | 62.3386 | -61.0285
1657.7969 | 123.0743 | -62.3199 | 60.6995 | 0.0094624 | 0.0037714 | 0.0068034 | 0.060712 | 0.0088435 | 0.080316 | -0.0093855 | 0.032723 | -0.0038074 | -0.007779 | 0.022763 | -0.0063049 | -45.7416 | -19.2699 | -46.0293 | 60.6379 | 60.5612 | 60.7581 | -62.4143 | -0.031003 | 0.000359 | -0.056351 | 0.084508 | 0.26095 | -0.083821 | -0.36104 | -0.094327 | -0.061529 | 16.5783 | 16.2907 | 16.385 | -0.13825 | 0.058622 | 61.9589 | -60.615 | 62.2889 | 62.2636 | 0.30469 | -60.4385 | -60.7833 | 122.9579 | 122.8812 | 123.078 | 43.05 | -123.1137 | 62.4045 | 62.5809 | 62.2361 | 62.3203 | -61.0605
1658.7969 | 123.0743 | -62.233 | 60.7727 | -0.0057996 | 0.003985 | 0.0063762 | 0.060925 | 0.0088435 | 0.08053 | -0.001755 | 0.032723 | -0.0038074 | -0.0073516 | 0.02319 | -0.0063049 | -46.5886 | -19.2791 | -46.0018 | 60.6883 | 60.6024 | 60.7993 | -62.3685 | -0.031003 | 0.004938 | -0.06093 | 0.075351 | 0.25637 | -0.083821 | -0.36562 | -0.13551 | -0.084408 | 15.6443 | 16.2312 | 16.3667 | -0.17028 | 0.026587 | 61.8674 | -60.6974 | 62.202 | 62.172 | 0.30469 | -60.5163 | -60.8565 | 122.9213 | 122.8354 | 123.0323 | 42.9539 | -123.1412 | 62.3083 | 62.4893 | 62.1491 | 62.2379 | -61.1383
1659.7969 | 123.0927 | -62.2513 | 60.7498 | -0.0057996 | 0.0037714 | 0.0063762 | 0.060712 | 0.0088435 | 0.08053 | -0.001755 | 0.032723 | -0.004021 | -0.0075654 | 0.023404 | -0.0056639 | -46.0209 | -19.3066 | -46.0064 | 60.6654 | 60.5795 | 60.781 | -62.396 | -0.031003 | -0.00422 | -0.065509 | 0.075351 | 0.25637 | -0.079243 | -0.36104 | -0.14467 | -0.084412 | 16.2304 | 16.2449 | 16.3896 | -0.17029 | 0.031161 | 61.8902 | -60.6745 | 62.2203 | 62.1858 | 0.29553 | -60.4934 | -60.8291 | 122.9167 | 122.8308 | 123.0323 | 42.9447 | -123.1458 | 62.3266 | 62.5077 | 62.172 | 62.2471 | -61.1109
1660.7969 | 123.1018 | -62.2787 | 60.7269 | -0.0057996 | 0.0037714 | 0.0061624 | 0.060712 | 0.0086299 | 0.08053 | -0.001755 | 0.03315 | -0.0042346 | -0.0073516 | 0.022976 | -0.0058775 | -45.7233 | -19.3752 | -46.0247 | 60.6791 | 60.5887 | 60.8039 | -62.3731 | -0.031003 | 0.004938 | -0.047194 | 0.070773 | 0.25637 | -0.0884 | -0.36104 | -0.094314 | -0.047789 | 16.5554 | 16.254 | 16.3484 | -0.13824 | 0.076942 | 61.9177 | -60.6562 | 62.2477 | 62.2316 | 0.31384 | -60.4706 | -60.8153 | 122.9579 | 122.8674 | 123.0826 | 42.9035 | -123.1 | 62.3495 | 62.5351 | 62.1903 | 62.2837 | -61.088
1661.7969 | 123.0881 | -62.1826 | 60.7681 | 0.0018314 | 0.0037714 | 0.0076582 | 0.061139 | 0.0086299 | 0.081598 | -0.001755 | 0.032509 | -0.004021 | -0.0073516 | 0.023617 | -0.0058775 | -45.032 | -19.3752 | -46.0705 | 60.6746 | 60.5841 | 60.7993 | -62.3822 | -0.026425 | 0.004938 | -0.047194 | 0.07993 | 0.26095 | -0.092979 | -0.35646 | -0.1996 | -0.093566 | 17.1506 | 16.1121 | 16.3117 | -0.18402 | 0.031165 | 61.8262 | -60.6882 | 62.1562 | 62.1354 | 0.30927 | -60.5072 | -60.8611 | 122.8572 | 122.7667 | 122.9819 | 42.8074 | -123.1503 | 62.2625 | 62.4436 | 62.0896 | 62.1876 | -61.1246
1662.7969 | 123.0835 | -62.2101 | 60.7956 | -0.0057996 | 0.0035576 | 0.0065898 | 0.060498 | 0.0086299 | 0.080743 | 0.0058755 | 0.032937 | -0.004021 | -0.0073516 | 0.02319 | -0.0058775 | -46.7626 | -19.3203 | -45.9927 | 60.7707 | 60.6803 | 60.8817 | -62.2998 | -0.040161 | 0.004938 | -0.047194 | 0.07993 | 0.25637 | -0.0884 | -0.35646 | -0.089717 | -0.024886 | 15.4475 | 16.2174 | 16.3071 | -0.11533 | 0.086114 | 61.8536 | -60.7157 | 62.1699 | 62.1629 | 0.30927 | -60.5392 | -60.884 | 122.9808 | 122.8903 | 123.0918 | 42.8898 | -123.0954 | 62.29 | 62.4665 | 62.1217 | 62.215 | -61.1521
1663.7969 | 123.1293 | -62.027 | 60.9421 | 0.0018314 | 0.0037714 | 0.0063762 | 0.060712 | 0.0088435 | 0.080743 | -0.001755 | 0.033577 | -0.0035938 | -0.0075654 | 0.023404 | -0.0058775 | -47.4448 | -19.247 | -45.8507 | 60.8806 | 60.7902 | 60.9962 | -62.1853 | -0.021846 | 0.014095 | -0.047194 | 0.070773 | 0.24721 | -0.083821 | -0.36562 | -0.15835 | -0.061489 | 14.5822 | 16.1762 | 16.3346 | -0.15192 | 0.054094 | 61.6614 | -60.8713 | 62.0051 | 61.9798 | 0.31842 | -60.6949 | -61.0259 | 122.9076 | 122.8171 | 123.0232 | 42.7799 | -123.1274 | 62.0978 | 62.2742 | 61.9432 | 62.0411 | -61.3077
1664.7969 | 123.1064 | -62.114 | 60.8597 | -0.0057996 | 0.0035576 | 0.0065898 | 0.060498 | 0.0086299 | 0.080957 | -0.0093855 | 0.032937 | -0.004021 | -0.0075654 | 0.02319 | -0.0063049 | -48.072 | -19.3844 | -45.9515 | 60.8211 | 60.7398 | 60.9458 | -62.2449 | -0.044739 | 0.018674 | -0.056351 | 0.066194 | 0.23806 | -0.083821 | -0.3702 | -0.1309 | -0.03861 | 14.0419 | 16.1625 | 16.2934 | -0.11989 | 0.086127 | 61.7438 | -60.7935 | 62.0692 | 62.0576 | 0.31385 | -60.6216 | -60.9435 | 122.935 | 122.8537 | 123.0598 | 42.7296 | -123.1045 | 62.1801 | 62.352 | 62.0301 | 62.1326 | -61.2299
1665.7969 | 123.0698 | -62.0041 | 61.0199 | -0.0057996 | 0.0037714 | 0.0063762 | 0.060498 | 0.0086299 | 0.080957 | 0.0058755 | 0.03315 | -0.0035938 | -0.0075654 | 0.022976 | -0.0056639 | -48.2231 | -19.2974 | -45.7729 | 60.9813 | 60.9001 | 61.0969 | -62.0892 | -0.031003 | 0.014095 | -0.065509 | 0.070773 | 0.24721 | -0.0884 | -0.35646 | -0.08508 | -0.038584 | 13.781 | 16.2312 | 16.3163 | -0.11984 | 0.077004 | 61.6476 | -60.9491 | 61.9731 | 61.9386 | 0.29095 | -60.7727 | -61.1083 | 122.9854 | 122.9041 | 123.101 | 42.7067 | -123.1091 | 62.0749 | 62.2513 | 61.9157 | 62.0182 | -61.3764
1666.7969 | 123.0789 | -62.1414 | 60.8276 | -0.013431 | 0.0035576 | 0.0063762 | 0.060925 | 0.0086299 | 0.080743 | -0.001755 | 0.032937 | -0.0038074 | -0.007779 | 0.023404 | -0.0060913 | -48.6672 | -19.5813 | -46.0613 | 60.789 | 60.7032 | 60.9092 | -62.2861 | -0.031003 | 0.014095 | -0.070087 | 0.066194 | 0.24721 | -0.083821 | -0.35646 | -0.14464 | -0.038616 | 13.4742 | 16.0801 | 16.2247 | -0.12448 | 0.081542 | 61.785 | -60.7614 | 62.1104 | 62.0713 | 0.28637 | -60.5804 | -60.9115 | 122.9304 | 122.8446 | 123.0506 | 42.5601 | -123.1137 | 62.2076 | 62.3886 | 62.0576 | 62.1555 | -61.1841
1667.7969 | 123.0927 | -61.9492 | 61.0977 | 0.0018314 | 0.0035576 | 0.0065898 | 0.060498 | 0.0086299 | 0.080957 | -0.001755 | 0.032937 | -0.004021 | -0.0073516 | 0.023404 | -0.0060913 | -50.4619 | -19.4531 | -45.8874 | 60.9996 | 60.9184 | 61.1198 | -62.08 | -0.044739 | 0.004938 | -0.074666 | 0.061616 | 0.23348 | -0.083821 | -0.3702 | -0.13085 | -0.09809 | 11.4872 | 16.0618 | 16.1927 | -0.17935 | 0.022077 | 61.579 | -61.0361 | 61.9044 | 61.8745 | 0.29553 | -60.8642 | -61.1815 | 122.9488 | 122.8675 | 123.069 | 42.4961 | -123.1777 | 62.0108 | 62.1826 | 61.8653 | 61.9541 | -61.4679
1668.7969 | 123.1384 | -61.9492 | 61.0519 | -0.013431 | 0.003985 | 0.0065898 | 0.060712 | 0.0086299 | 0.081171 | -0.0093855 | 0.032937 | -0.004021 | -0.0075654 | 0.02319 | -0.0060913 | -51.6294 | -19.4622 | -45.8874 | 61.0088 | 60.9367 | 61.1335 | -62.0663 | -0.044739 | 0.000359 | -0.065509 | 0.066194 | 0.23806 | -0.0884 | -0.36562 | -0.11712 | -0.043157 | 10.3197 | 16.0618 | 16.1789 | -0.11525 | 0.081589 | 61.5835 | -60.9857 | 61.9044 | 61.8836 | 0.30011 | -60.8139 | -61.1403 | 122.9579 | 122.8858 | 123.0827 | 42.4869 | -123.1182 | 62.0154 | 62.1872 | 61.8608 | 61.9495 | -61.4176
1669.7969 | 123.111 | -61.9171 | 61.084 | -0.0057996 | 0.0035576 | 0.0065898 | 0.060712 | 0.0086299 | 0.08053 | 0.021136 | 0.032937 | -0.0038074 | -0.007779 | 0.023404 | -0.0056639 | -50.3292 | -19.5859 | -45.9102 | 61.0088 | 60.9184 | 61.1244 | -62.0709 | -0.035582 | 0.009516 | -0.065509 | 0.070773 | 0.23806 | -0.0884 | -0.36562 | -0.15374 | -0.0752 | 11.5879 | 16.0069 | 16.1606 | -0.16561 | 0.040389 | 61.5515 | -61.0132 | 61.8815 | 61.8516 | 0.30011 | -60.8459 | -61.1724 | 122.9259 | 122.8355 | 123.0415 | 42.3313 | -123.1548 | 61.9879 | 62.1552 | 61.8287 | 61.9266 | -61.4496
1670.7969 | 123.175 | -61.9537 | 61.0016 | 0.0018314 | 0.0035576 | 0.0070172 | 0.060925 | 0.0086299 | 0.080957 | -0.001755 | 0.032937 | -0.0038074 | -0.0075654 | 0.023404 | -0.0058775 | -51.0434 | -19.6912 | -45.956 | 60.9859 | 60.8909 | 61.0969 | -62.0892 | -0.044739 | 0.009516 | -0.079245 | 0.057037 | 0.23348 | -0.092979 | -0.3702 | -0.13543 | -0.015695 | 10.9103 | 15.9977 | 16.1331 | -0.11069 | 0.095314 | 61.5835 | -60.9445 | 61.909 | 61.8745 | 0.29095 | -60.7681 | -61.0946 | 122.9396 | 122.8446 | 123.0506 | 42.2626 | -123.0908 | 62.0108 | 62.1872 | 61.8608 | 61.9633 | -61.3718
1671.7969 | 123.2071 | -61.853 | 61.1206 | -0.0057996 | 0.0035576 | 0.0068034 | 0.060712 | 0.0084163 | 0.081171 | 0.0058755 | 0.032723 | -0.0038074 | -0.0075654 | 0.023404 | -0.0060913 | -51.6661 | -19.7873 | -45.9102 | 61.0363 | 60.9413 | 61.1381 | -62.0525 | -0.044739 | 0.004938 | -0.065509 | 0.057037 | 0.23806 | -0.0884 | -0.3702 | -0.19951 | -0.084351 | 10.187 | 15.9428 | 16.1423 | -0.17934 | 0.017504 | 61.4828 | -61.0636 | 61.8083 | 61.7875 | 0.30469 | -60.8825 | -61.209 | 122.8893 | 122.7943 | 122.9911 | 42.0657 | -123.1731 | 61.9101 | 62.0911 | 61.7646 | 61.858 | -61.4908
1672.7969 | 123.111 | -61.8896 | 61.1389 | -0.0057996 | 0.003985 | 0.0063762 | 0.060712 | 0.0084163 | 0.081171 | -0.017016 | 0.032723 | -0.0035938 | -0.0075654 | 0.02319 | -0.0058775 | -51.7668 | -19.7553 | -45.8782 | 61.1004 | 61.0237 | 61.2251 | -61.9747 | -0.040161 | 0.014095 | -0.070087 | 0.057037 | 0.23806 | -0.079243 | -0.36104 | -0.085048 | -0.038565 | 10.1229 | 16.0114 | 16.0965 | -0.11523 | 0.086186 | 61.5286 | -61.0819 | 61.8495 | 61.8196 | 0.29095 | -60.9009 | -61.2182 | 122.99 | 122.9133 | 123.1148 | 42.1344 | -123.1136 | 61.9467 | 62.1277 | 61.8104 | 61.9037 | -61.5
1673.7969 | 123.1064 | -61.7477 | 61.2762 | 0.0094624 | 0.0037714 | 0.0065898 | 0.060712 | 0.0084163 | 0.081384 | 0.0058755 | 0.032937 | -0.0038074 | -0.0079926 | 0.023404 | -0.0058775 | -51.3822 | -19.7598 | -45.8141 | 61.1828 | 61.1061 | 61.2892 | -61.8923 | -0.040161 | 0.009516 | -0.070087 | 0.061616 | 0.23348 | -0.0884 | -0.36104 | -0.14453 | -0.093483 | 10.3655 | 15.9336 | 16.0782 | -0.17014 | 0.012958 | 61.3867 | -61.2146 | 61.7076 | 61.6777 | 0.29095 | -61.0428 | -61.3646 | 122.9305 | 122.8538 | 123.0369 | 41.9879 | -123.1685 | 61.8094 | 61.9812 | 61.6593 | 61.7573 | -61.6373
1674.7969 | 123.1842 | -61.8118 | 61.1069 | 0.0018314 | 0.0037714 | 0.0065898 | 0.060498 | 0.0086299 | 0.080743 | -0.0093855 | 0.033364 | -0.0038074 | -0.007779 | 0.023404 | -0.0058775 | -49.9263 | -20.2818 | -45.9423 | 61.1095 | 61.0145 | 61.2251 | -61.9701 | -0.026425 | 0.018674 | -0.065509 | 0.066194 | 0.24264 | -0.079243 | -0.35188 | -0.15829 | 0.002635 | 11.8856 | 15.8695 | 16.0278 | -0.092344 | 0.11823 | 61.4599 | -61.0407 | 61.7854 | 61.7463 | 0.28637 | -60.8642 | -61.1861 | 122.9213 | 122.8264 | 123.0369 | 41.53 | -123.077 | 61.878 | 62.0545 | 61.7326 | 61.8305 | -61.4588
1675.7969 | 123.111 | -61.6882 | 61.3266 | 0.0018314 | 0.003344 | 0.0065898 | 0.060712 | 0.0084163 | 0.080957 | 0.0058755 | 0.032723 | -0.0038074 | -0.0073516 | 0.022976 | -0.0060913 | -51.7668 | -20.4649 | -45.8416 | 61.2514 | 61.1565 | 61.3579 | -61.8373 | -0.031003 | 0.018674 | -0.06093 | 0.066194 | 0.24721 | -0.092979 | -0.35646 | -0.1491 | -0.075161 | 9.9214 | 15.8467 | 15.9958 | -0.17012 | 0.031283 | 61.3318 | -61.2604 | 61.6572 | 61.6273 | 0.29553 | -61.0794 | -61.4196 | 122.9397 | 122.8447 | 123.0461 | 41.2233 | -123.1639 | 61.7544 | 61.9354 | 61.5953 | 61.7069 | -61.6831
1676.7969 | 123.1247 | -61.7706 | 61.2671 | -0.013431 | 0.0041986 | 0.0065898 | 0.060284 | 0.0084163 | 0.081384 | 0.0058755 | 0.032723 | -0.004021 | -0.0075654 | 0.023617 | -0.0056639 | -52.5085 | -20.062 | -45.8919 | 61.1873 | 61.1198 | 61.3121 | -61.8923 | -0.035582 | 0.023253 | -0.070087 | 0.066194 | 0.25179 | -0.083821 | -0.36104 | -0.12165 | -0.079749 | 9.2621 | 15.8787 | 16.0003 | -0.14725 | 0.045006 | 61.4096 | -61.2009 | 61.735 | 61.7005 | 0.29095 | -61.0153 | -61.3509 | 122.958 | 122.8905 | 123.0827 | 41.7086 | -123.1594 | 61.8368 | 62.0224 | 61.6868 | 61.7939 | -61.6281
1677.7969 | 123.1384 | -61.6425 | 61.377 | -0.0057996 | 0.0037714 | 0.0065898 | 0.060498 | 0.0082025 | 0.081384 | 0.0058755 | 0.032937 | -0.0038074 | -0.0079926 | 0.023617 | -0.0060913 | -51.7714 | -20.6847 | -45.8141 | 61.3064 | 61.2297 | 61.4266 | -61.7686 | -0.031003 | 0.018674 | -0.070087 | 0.066194 | 0.23806 | -0.0884 | -0.35188 | -0.12619 | -0.070574 | 9.8711 | 15.8284 | 15.9545 | -0.14722 | 0.049608 | 61.2906 | -61.3108 | 61.6115 | 61.5724 | 0.28179 | -61.1389 | -61.4654 | 122.9488 | 122.8722 | 123.069 | 40.9577 | -123.1456 | 61.7087 | 61.8805 | 61.5541 | 61.6611 | -61.7288
1678.7969 | 123.1842 | -61.5967 | 61.3541 | -0.0057996 | 0.0037714 | 0.0063762 | 0.060284 | 0.0086299 | 0.080743 | 0.0058755 | 0.03315 | -0.0038074 | -0.007779 | 0.023831 | -0.0060913 | -47.138 | -20.9457 | -45.8278 | 61.3293 | 61.2572 | 61.4403 | -61.7458 | -0.026425 | 0.023253 | -0.065509 | 0.070773 | 0.24264 | -0.092979 | -0.35188 | -0.14907 | -0.024794 | 14.4586 | 15.7688 | 15.9179 | -0.096853 | 0.086231 | 61.2448 | -61.2833 | 61.5703 | 61.5312 | 0.28637 | -61.1114 | -61.447 | 122.926 | 122.8539 | 123.037 | 40.651 | -123.0998 | 61.6675 | 61.8393 | 61.5037 | 61.6199 | -61.7059
1679.7969 | 123.1522 | -61.441 | 61.5738 | -0.0057996 | 0.0035576 | 0.0063762 | 0.060925 | 0.0082025 | 0.081384 | 0.0058755 | 0.032723 | -0.0035938 | -0.0075654 | 0.023617 | -0.0063049 | -50.4162 | -20.6847 | -45.6996 | 61.4849 | 61.3946 | 61.6005 | -61.6084 | -0.031003 | 0.027831 | -0.06093 | 0.070773 | 0.25637 | -0.079243 | -0.3473 | -0.16734 | -0.088856 | 11.0249 | 15.7414 | 15.9087 | -0.17921 | 0.026756 | 61.0937 | -61.503 | 61.41 | 61.3801 | 0.28637 | -61.3174 | -61.653 | 122.926 | 122.8356 | 123.0416 | 40.7563 | -123.1822 | 61.5118 | 61.6974 | 61.3618 | 61.4689 | -61.9211
1680.7969 | 123.2025 | -61.0519 | 61.853 | -0.013431 | 0.003985 | 0.0068034 | 0.060712 | 0.0082025 | 0.081812 | 0.0058755 | 0.032937 | -0.0038074 | -0.0075654 | 0.023617 | -0.0060913 | -52.0186 | -21.4768 | -45.7912 | 61.4895 | 61.4129 | 61.6143 | -61.5809 | -0.035582 | 0.014095 | -0.065509 | 0.066194 | 0.24721 | -0.0884 | -0.36562 | -0.52897 | -0.36351 | 9.0333 | 15.2607 | 15.7897 | -0.44013 | -0.23874 | 60.6863 | -61.7868 | 61.0164 | 60.9864 | 0.30011 | -61.6058 | -61.9414 | 122.5415 | 122.4648 | 122.6662 | 39.5751 | -123.4339 | 61.1181 | 61.2992 | 60.9635 | 61.066 | -62.2186
1681.7969 | 123.0881 | -61.2671 | 61.7615 | 0.0018314 | 0.0037714 | 0.0061624 | 0.060925 | 0.0082025 | 0.082025 | -0.001755 | 0.033364 | -0.004021 | -0.0075654 | 0.02319 | -0.0065185 | -46.5703 | -28.3035 | -46.0659 | 61.636 | 61.5503 | 61.7562 | -61.439 | -0.035582 | 0.018674 | -0.070087 | 0.066194 | 0.24721 | -0.0884 | -0.35646 | -0.17187 | -0.12545 | 14.6968 | 15.2012 | 15.373 | -0.21121 | -0.005255 | 60.9106 | -61.6953 | 61.2315 | 61.197 | 0.28637 | -61.5143 | -61.8499 | 122.9031 | 122.8174 | 123.0233 | 32.9636 | -123.2004 | 61.3333 | 61.5143 | 61.1787 | 61.2858 | -62.1179
1682.7969 | 123.1064 | -61.1343 | 61.8805 | -0.0057996 | 0.0041986 | 0.0061624 | 0.060498 | 0.0075615 | 0.081812 | -0.001755 | 0.032937 | -0.0035938 | -0.0075654 | 0.023404 | -0.0060913 | -46.8221 | -29.6038 | -46.0247 | 61.8329 | 61.7426 | 61.9348 | -61.2558 | -0.031003 | 0.018674 | -0.065509 | 0.066194 | 0.24721 | -0.0884 | -0.35188 | -0.12147 | -0.0476 | 14.3122 | 15.1096 | 15.2311 | -0.13791 | 0.054293 | 60.7825 | -61.8143 | 61.1033 | 61.0688 | 0.28637 | -61.6333 | -61.9689 | 122.9672 | 122.8769 | 123.0691 | 31.5305 | -123.1363 | 61.2005 | 61.3816 | 61.0459 | 61.153 | -62.2324
1683.7969 | 123.143 | -60.4935 | 62.4802 | -0.0057996 | 0.003985 | 0.0061624 | 0.060284 | 0.0075615 | 0.082453 | -0.001755 | 0.03315 | -0.004021 | -0.0075654 | 0.023831 | -0.0058775 | -45.6958 | -31.9572 | -45.6676 | 62.4143 | 62.3287 | 62.5208 | -60.6651 | -0.026425 | 0.018674 | -0.056351 | 0.066194 | 0.25637 | -0.0884 | -0.35188 | -0.17166 | -0.065815 | 14.7976 | 14.8259 | 14.9975 | -0.15148 | 0.040683 | 60.1416 | -62.414 | 60.467 | 60.4371 | 0.29553 | -62.2238 | -62.5686 | 122.9078 | 122.8221 | 123.0143 | 28.5362 | -123.1453 | 60.5597 | 60.7498 | 60.4051 | 60.5121 | -62.832
1684.7969 | 123.1201 | -60.6766 | 62.3474 | -0.0057996 | 0.0041986 | 0.0059488 | 0.060925 | 0.0075615 | 0.082239 | -0.001755 | 0.032937 | -0.0035938 | -0.0073516 | 0.023404 | -0.0056639 | -45.6409 | -32.5296 | -45.8187 | 62.3365 | 62.26 | 62.4476 | -60.7521 | -0.035582 | 0.014095 | -0.065509 | 0.061616 | 0.23806 | -0.0884 | -0.35646 | -0.075548 | -0.010896 | 15.0357 | 14.8579 | 14.9334 | -0.087416 | 0.10018 | 60.3201 | -62.2858 | 60.641 | 60.6111 | 0.29095 | -62.1094 | -62.4358 | 123.0131 | 122.9366 | 123.1242 | 28.147 | -123.0995 | 60.7382 | 60.9146 | 60.5882 | 60.6907 | -62.7039
1685.7969 | 123.2162 | -60.3699 | 62.5534 | -0.013431 | 0.0041986 | 0.0061624 | 0.060284 | 0.0073479 | 0.082666 | -0.001755 | 0.032723 | -0.0035938 | -0.007779 | 0.023404 | -0.0060913 | -44.8717 | -33.9627 | -45.7088 | 62.5425 | 62.4569 | 62.6628 | -60.5461 | -0.035582 | 0.014095 | -0.065509 | 0.061616 | 0.24264 | -0.0884 | -0.35646 | -0.1762 | -0.010862 | 15.4981 | 14.6611 | 14.8373 | -0.096516 | 0.10938 | 60.0134 | -62.4918 | 60.3343 | 60.3044 | 0.29095 | -62.3108 | -62.6418 | 122.9124 | 122.8268 | 123.0327 | 26.4072 | -123.0995 | 60.4315 | 60.6125 | 60.2815 | 60.384 | -62.9099
1686.7969 | 123.2162 | -60.5255 | 62.4527 | -0.013431 | 0.0044124 | 0.0061624 | 0.060712 | 0.0077753 | 0.082239 | 0.0058755 | 0.032937 | -0.0035938 | -0.007779 | 0.02319 | -0.0058775 | -43.0587 | -33.3629 | -45.8187 | 62.3915 | 62.3149 | 62.5071 | -60.7063 | -0.031003 | 0.014095 | -0.056351 | 0.066194 | 0.25179 | -0.092979 | -0.3473 | -0.18082 | -0.061241 | 17.4668 | 14.7068 | 14.8877 | -0.13775 | 0.054413 | 60.1782 | -62.3865 | 60.4945 | 60.4692 | 0.29095 | -62.2009 | -62.5457 | 122.917 | 122.8405 | 123.0326 | 27.1626 | -123.159 | 60.5917 | 60.7773 | 60.4325 | 60.5396 | -62.8
1687.7969 | 123.0423 | -60.4248 | 62.5992 | -0.0057996 | 0.0041986 | 0.0061624 | 0.060284 | 0.0071343 | 0.082239 | -0.001755 | 0.03315 | -0.00338 | -0.007779 | 0.023831 | -0.0060913 | -42.6146 | -35.5835 | -45.8141 | 62.538 | 62.4523 | 62.6536 | -60.5506 | -0.026425 | 0.023253 | -0.065509 | 0.07993 | 0.26095 | -0.092979 | -0.3473 | -0.12584 | -0.061217 | 17.8102 | 14.6107 | 14.7365 | -0.14687 | 0.054444 | 60.0775 | -62.5193 | 60.3984 | 60.3593 | 0.28179 | -62.3382 | -62.6922 | 122.9628 | 122.8771 | 123.0784 | 24.8413 | -123.1498 | 60.5047 | 60.6858 | 60.3318 | 60.4481 | -62.9465
1688.7969 | 123.1018 | -61.4502 | 61.5692 | -0.013431 | 0.0035576 | 0.0059488 | 0.060071 | 0.0082025 | 0.080743 | 0.0058755 | 0.03315 | -0.0038074 | -0.0075654 | 0.023617 | -0.0060913 | -43.4524 | -20.4146 | -45.8141 | 61.5536 | 61.4587 | 61.6692 | -61.5305 | -0.003531 | 0.036989 | -0.028879 | 0.093665 | 0.27926 | -0.079243 | -0.31983 | -0.080345 | -0.015602 | 17.9978 | 15.6361 | 15.7164 | -0.11053 | 0.10001 | 61.1304 | -61.4755 | 61.4467 | 61.4213 | 0.29095 | -61.2899 | -61.6485 | 123.0038 | 122.9089 | 123.1194 | 41.0356 | -123.0998 | 61.5439 | 61.7295 | 61.371 | 61.4872 | -61.889
1689.7969 | 123.1476 | -61.4227 | 61.6058 | 0.0018314 | 0.003344 | 0.0061624 | 0.060712 | 0.0086299 | 0.080743 | 0.013506 | 0.032937 | -0.00338 | -0.0075654 | 0.02319 | -0.0056639 | -43.5165 | -21.0327 | -45.8645 | 61.5673 | 61.477 | 61.6875 | -61.5214 | -0.012689 | 0.036989 | -0.042615 | 0.084508 | 0.26553 | -0.079243 | -0.32441 | -0.098653 | -0.038488 | 17.9062 | 15.5583 | 15.6569 | -0.12884 | 0.081706 | 61.0983 | -61.5213 | 61.41 | 61.3801 | 0.28179 | -61.3403 | -61.6851 | 122.9901 | 122.8997 | 123.1103 | 40.39 | -123.1272 | 61.5072 | 61.6883 | 61.3435 | 61.4597 | -61.9302
1690.7969 | 123.1842 | -62.3383 | 60.6262 | -0.0057996 | 0.0037714 | 0.0065898 | 0.060925 | 0.0084163 | 0.081384 | -0.001755 | 0.03315 | -0.0038074 | -0.007779 | 0.023617 | -0.0058775 | -43.1869 | -20.8541 | -46.1849 | 61.1782 | 61.0832 | 61.2938 | -61.9335 | 0.001048 | 0.036989 | -0.033458 | 0.093665 | 0.26553 | -0.0884 | -0.32899 | 0.40477 | 0.55196 | 19.1514 | 16.1533 | 15.7485 | 0.45699 | 0.66756 | 62.0093 | -60.5326 | 62.3393 | 62.3048 | 0.29553 | -60.3607 | -60.7146 | 123.5164 | 123.4215 | 123.632 | 41.4841 | -122.5597 | 62.4319 | 62.6038 | 62.2499 | 62.3752 | -60.9552
1691.7969 | 123.1293 | -61.8301 | 61.203 | -0.0057996 | 0.0035576 | 0.0059488 | 0.060498 | 0.0082025 | 0.080743 | -0.0093855 | 0.033364 | -0.0035938 | -0.0079926 | 0.023404 | -0.0063049 | -43.8141 | -20.9045 | -46.304 | 61.082 | 61.01 | 61.1976 | -62.0067 | -0.012689 | 0.03241 | -0.047194 | 0.07993 | 0.26095 | -0.092979 | -0.33814 | -0.17661 | -0.12097 | 18.016 | 15.5262 | 15.7028 | -0.19305 | -0.005372 | 61.492 | -61.1231 | 61.8175 | 61.7829 | 0.29095 | -60.9421 | -61.296 | 122.9122 | 122.8401 | 123.0278 | 40.9256 | -123.2098 | 61.9101 | 62.0911 | 61.7372 | 61.8625 | -61.5411
1692.7969 | 123.0972 | -61.9125 | 61.1435 | -0.013431 | 0.0037714 | 0.005735 | 0.060712 | 0.0082025 | 0.080957 | -0.001755 | 0.03315 | -0.0038074 | -0.0079926 | 0.023617 | -0.0060913 | -43.8462 | -20.7763 | -46.2582 | 61.1187 | 61.042 | 61.248 | -61.9701 | -0.003531 | 0.036989 | -0.033458 | 0.093665 | 0.26553 | -0.079243 | -0.32899 | -0.05758 | -0.024829 | 18.0664 | 15.6543 | 15.7119 | -0.10149 | 0.1045 | 61.5836 | -61.0498 | 61.909 | 61.8791 | 0.29553 | -60.878 | -61.2227 | 123.0312 | 122.9545 | 123.1605 | 41.1362 | -123.1136 | 62.0062 | 62.1781 | 61.8333 | 61.9495 | -61.4725
1693.7969 | 123.1522 | -61.3998 | 61.6333 | -0.0057996 | 0.0041986 | 0.0055214 | 0.060712 | 0.0077753 | 0.081384 | -0.001755 | 0.032937 | -0.0038074 | -0.0075654 | 0.023831 | -0.0058775 | -43.37 | -26.5087 | -46.249 | 61.4941 | 61.4175 | 61.6051 | -61.5855 | -0.031003 | 0.03241 | -0.047194 | 0.084508 | 0.25637 | -0.092979 | -0.33357 | -0.18565 | -0.13921 | 18.0298 | 15.1508 | 15.3364 | -0.21583 | -0.028175 | 61.0663 | -61.5488 | 61.3688 | 61.3526 | 0.28637 | -61.3769 | -61.7263 | 122.8939 | 122.8173 | 123.005 | 34.8911 | -123.2188 | 61.4843 | 61.6562 | 61.3069 | 61.4323 | -61.9669
1694.7969 | 123.1201 | -61.647 | 61.3586 | -0.013431 | 0.004626 | 0.0059488 | 0.060925 | 0.0082025 | 0.081812 | -0.0093855 | 0.032937 | -0.0042346 | -0.0075654 | 0.023617 | -0.0056639 | -42.9717 | -24.7047 | -46.336 | 61.2789 | 61.216 | 61.3991 | -61.8144 | -0.031003 | 0.036989 | -0.038036 | 0.084508 | 0.26095 | -0.083821 | -0.32899 | -0.1674 | -0.079734 | 18.6753 | 15.311 | 15.4784 | -0.14264 | 0.040446 | 61.318 | -61.2741 | 61.616 | 61.609 | 0.29095 | -61.0977 | -61.4425 | 122.9259 | 122.863 | 123.0461 | 36.9423 | -123.1731 | 61.7315 | 61.908 | 61.5632 | 61.684 | -61.6876
1695.7969 | 123.2071 | -61.7386 | 61.1984 | -0.0057996 | 0.0061218 | 0.005735 | 0.060284 | 0.0079889 | 0.082666 | -0.001755 | 0.03315 | -0.0038074 | -0.0075654 | 0.023404 | -0.0058775 | -41.0167 | -21.2296 | -46.2765 | 61.1141 | 61.0237 | 61.2205 | -61.993 | -0.021846 | 0.036989 | -0.033458 | 0.093665 | 0.27469 | -0.079243 | -0.32441 | -0.25443 | -0.084338 | 20.7219 | 15.4621 | 15.7165 | -0.17474 | 0.022099 | 61.4142 | -61.1048 | 61.7167 | 61.7051 | 0.29095 | -60.9237 | -61.2777 | 122.8527 | 122.7623 | 122.9591 | 40.509 | -123.1914 | 61.8323 | 62.0133 | 61.6593 | 61.7756 | -61.5228
1696.7969 | 123.0652 | -66.4627 | 56.5613 | -0.0057996 | 0.065523 | 0.0021026 | 0.060071 | 0.0084163 | 0.13886 | -0.0093855 | 0.03315 | -0.0038074 | -0.0079926 | 0.023831 | -0.0060913 | 39.0684 | -26.5362 | -50.0948 | 57.2545 | 57.1591 | 57.3928 | -65.853 | 0.078886 | 0.13772 | 0.071853 | 0.19439 | 0.38 | 0.058115 | -0.20994 | 0.60966 | 0.69323 | 105.5311 | 16.3679 | 15.7582 | 0.59779 | 0.83153 | 66.2528 | -56.3669 | 66.5416 | 66.5346 | 0.28179 | -56.1813 | -56.5032 | 123.7172 | 123.6218 | 123.8555 | 39.9265 | -122.4143 | 66.6571 | 66.8427 | 66.5208 | 66.6004 | -56.7712
1697.7969 | 123.1384 | -66.5131 | 56.4972 | 0.0018314 | 0.073215 | 0.0010342 | 0.060284 | 0.0082025 | 0.14527 | -0.001755 | 0.032723 | -0.0038074 | -0.007779 | 0.023404 | -0.0058775 | 54.8776 | -26.5408 | -50.8823 | 56.4304 | 56.3486 | 56.5503 | -66.6498 | 0.088043 | 0.1423 | 0.090168 | 0.20813 | 0.38457 | 0.090166 | -0.1962 | -0.13672 | -0.066796 | 121.3907 | 15.6308 | 15.7675 | -0.14859 | 0.053157 | 66.3169 | -56.2891 | 66.6011 | 66.6032 | 0.28637 | -56.1126 | -56.407 | 122.9435 | 122.8617 | 123.0634 | 39.9723 | -123.147 | 66.7212 | 66.8976 | 66.6032 | 66.6554 | -56.6934
1698.7969 | 123.2529 | -66.2064 | 56.6803 | 0.0018314 | 0.075565 | 0.0012478 | 0.060498 | 0.0075615 | 0.14805 | -0.001755 | 0.032723 | -0.00338 | -0.007779 | 0.023404 | -0.0060913 | 56.7135 | -34.567 | -51.0105 | 56.7738 | 56.6829 | 56.8937 | -66.3109 | 0.088043 | 0.12856 | 0.067274 | 0.21271 | 0.38 | 0.026065 | -0.20078 | -0.10458 | 0.093477 | 122.9199 | 15.1959 | 15.3005 | 0.002568 | 0.21345 | 66.0056 | -56.4676 | 66.2944 | 66.2736 | 0.26805 | -56.3003 | -56.6542 | 122.9801 | 122.8892 | 123.1001 | 31.6393 | -122.9912 | 66.4191 | 66.5864 | 66.2324 | 66.3349 | -56.8811
1699.7969 | 123.1613 | -66.3712 | 56.6483 | -0.0057996 | 0.075565 | 0.0012478 | 0.060284 | 0.0079889 | 0.14869 | -0.0093855 | 0.032937 | -0.0038074 | -0.0075654 | 0.023404 | -0.0058775 | 56.9425 | -38.0651 | -51.0425 | 56.9523 | 56.866 | 57.0815 | -66.1369 | 0.088043 | 0.13314 | 0.076431 | 0.20813 | 0.38 | 0.12222 | -0.21452 | 0.23422 | 0.30408 | 123.3136 | 15.3287 | 15.0944 | 0.21777 | 0.43321 | 66.1566 | -56.4401 | 66.4592 | 66.4476 | 0.29095 | -56.2683 | -56.526 | 123.3235 | 123.2372 | 123.4526 | 28.3061 | -122.7852 | 66.5793 | 66.7511 | 66.4934 | 66.5043 | -56.8628
1700.7969 | 123.2117 | -66.1835 | 56.7947 | -0.0057996 | 0.073215 | 0.0027436 | 0.060071 | 0.0079889 | 0.14826 | 0.0058755 | 0.032723 | -0.0035938 | -0.0075654 | 0.023617 | -0.0060913 | 56.7135 | -35.611 | -51.1249 | 56.7051 | 56.6142 | 56.8342 | -66.3567 | 0.083464 | 0.12856 | 0.085589 | 0.19897 | 0.38457 | 0.10848 | -0.20536 | -0.17326 | -0.08964 | 122.897 | 15.0586 | 15.2318 | -0.18056 | 0.039483 | 65.9781 | -56.5958 | 66.2669 | 66.2691 | 0.29095 | -56.4102 | -56.6863 | 122.8886 | 122.7977 | 123.0177 | 30.5725 | -123.1515 | 66.3824 | 66.568 | 66.292 | 66.312 | -57.0001
1701.7969 | 123.1018 | -64.7827 | 58.2779 | 0.0018314 | 0.075138 | 0.003171 | 0.060712 | 0.0069205 | 0.15147 | -0.001755 | 0.03315 | -0.0038074 | -0.0082062 | 0.023831 | -0.0060913 | 58.0275 | -48.8477 | -50.7129 | 58.0283 | 57.9512 | 58.1483 | -65.0426 | 0.06515 | 0.11483 | 0.062695 | 0.19439 | 0.37084 | -0.038035 | -0.21452 | -0.25986 | -0.24964 | 122.8102 | 14.0698 | 14.3297 | -0.32666 | -0.12961 | 64.5682 | -58.0835 | 64.8479 | 64.8454 | 0.27721 | -57.9071 | -58.3159 | 122.811 | 122.7339 | 122.931 | 15.935 | -123.3205 | 64.9771 | 65.1536 | 64.7447 | 64.8975 | -58.4924
1702.7969 | 123.0789 | -66.3895 | 56.6071 | -0.021062 | 0.071506 | 0.004453 | 0.060071 | 0.0082025 | 0.14698 | -0.001755 | 0.03315 | -0.0035938 | -0.0075654 | 0.023831 | -0.0058775 | 56.5808 | -29.8969 | -50.9097 | 56.5586 | 56.486 | 56.6969 | -66.5078 | 0.092622 | 0.15146 | 0.094746 | 0.22186 | 0.39373 | 0.12679 | -0.19162 | -0.11837 | -0.048465 | 122.9702 | 15.4797 | 15.5981 | -0.12108 | 0.089808 | 66.1978 | -56.3852 | 66.4821 | 66.4842 | 0.28637 | -56.2133 | -56.4803 | 122.9481 | 122.8754 | 123.0863 | 36.4926 | -123.1149 | 66.6113 | 66.7832 | 66.5163 | 66.5409 | -56.7987
1703.7969 | 123.2117 | -66.5268 | 56.3873 | -0.013431 | 0.070651 | 0.0048804 | 0.060498 | 0.0084163 | 0.14698 | -0.017016 | 0.03315 | -0.00338 | -0.0082062 | 0.023831 | -0.0056639 | 56.4022 | -30.8217 | -51.1341 | 56.38 | 56.2982 | 56.5046 | -66.6818 | 0.083464 | 0.13772 | 0.090168 | 0.21728 | 0.38915 | 0.058115 | -0.20536 | -0.15504 | -0.007295 | 122.929 | 15.3927 | 15.5478 | -0.089093 | 0.11723 | 66.3214 | -56.17 | 66.6103 | 66.617 | 0.29553 | -55.9982 | -56.3292 | 122.9068 | 122.825 | 123.0314 | 35.705 | -123.0692 | 66.7441 | 66.9159 | 66.5849 | 66.6645 | -56.5927
1704.7969 | 123.2025 | -66.4078 | 56.5155 | -0.013431 | 0.069796 | 0.0068034 | 0.060071 | 0.0075615 | 0.14869 | -0.001755 | 0.032937 | -0.0035938 | -0.0079926 | 0.023617 | -0.0063049 | 56.6586 | -34.274 | -51.0929 | 56.6364 | 56.5684 | 56.7518 | -66.4391 | 0.088043 | 0.13772 | 0.085589 | 0.20813 | 0.38457 | 0.039801 | -0.1962 | -0.031371 | 0.12092 | 123.0664 | 15.3149 | 15.3463 | 0.05289 | 0.2363 | 66.2116 | -56.3074 | 66.4958 | 66.4934 | 0.28179 | -56.1309 | -56.4757 | 123.0442 | 122.9762 | 123.1596 | 32.1338 | -122.9547 | 66.6159 | 66.7923 | 66.4476 | 66.5455 | -56.7117
1705.7969 | 123.1155 | -66.1514 | 56.8405 | 0.0018314 | 0.065309 | 0.010222 | 0.060712 | 0.0082025 | 0.14719 | -0.001755 | 0.03315 | -0.00338 | -0.007779 | 0.023831 | -0.0063049 | 56.7776 | -32.7539 | -50.8227 | 56.76 | 56.6829 | 56.8846 | -66.3018 | 0.092622 | 0.1423 | 0.085589 | 0.20813 | 0.39373 | 0.099323 | -0.20078 | -0.15035 | -0.080475 | 122.9291 | 15.3287 | 15.479 | -0.15765 | 0.044072 | 65.9506 | -56.6324 | 66.2441 | 66.237 | 0.28637 | -56.4468 | -56.7412 | 122.9115 | 122.8343 | 123.036 | 33.3975 | -123.1423 | 66.3596 | 66.5452 | 66.2508 | 66.2937 | -57.0413
1706.7969 | 123.1522 | -66.3666 | 56.6757 | -0.0057996 | 0.061249 | 0.014496 | 0.060284 | 0.0077753 | 0.14698 | -0.001755 | 0.032509 | -0.0035938 | -0.007779 | 0.023404 | -0.0060913 | 56.6403 | -31.8702 | -50.9372 | 56.6181 | 56.5272 | 56.7381 | -66.4529 | 0.10636 | 0.15146 | 0.10848 | 0.21271 | 0.38915 | 0.090166 | -0.19162 | -0.086307 | -0.05761 | 123.0069 | 15.4294 | 15.5157 | -0.14854 | 0.062352 | 66.175 | -56.463 | 66.4729 | 66.4751 | 0.3001 | -56.2866 | -56.5856 | 122.9847 | 122.8938 | 123.1046 | 34.4963 | -123.1286 | 66.5793 | 66.7557 | 66.4567 | 66.518 | -56.8673
1707.7969 | 123.1155 | -66.188 | 56.7947 | 0.0018314 | 0.057831 | 0.018342 | 0.060498 | 0.0079889 | 0.14719 | 0.013506 | 0.032937 | -0.0035938 | -0.007779 | 0.023831 | -0.0063049 | 56.8051 | -33.8207 | -50.8685 | 56.7875 | 56.7058 | 56.9121 | -66.2789 | 0.088043 | 0.1423 | 0.085589 | 0.21728 | 0.38 | 0.13595 | -0.1962 | -0.090836 | -0.007229 | 122.9932 | 15.3195 | 15.4104 | -0.088978 | 0.11732 | 65.9918 | -56.5775 | 66.2761 | 66.2736 | 0.28179 | -56.4147 | -56.6588 | 122.9756 | 122.8938 | 123.1001 | 32.3673 | -123.0736 | 66.4053 | 66.568 | 66.324 | 66.3303 | -56.9909
1708.7969 | 123.1338 | -65.744 | 57.2205 | -0.0057996 | 0.053985 | 0.02112 | 0.060284 | 0.0077753 | 0.14612 | -0.0093855 | 0.032937 | -0.00338 | -0.007779 | 0.023831 | -0.0058775 | 57.1668 | -35.0295 | -50.6121 | 57.1492 | 57.0629 | 57.26 | -65.9172 | 0.097201 | 0.15146 | 0.090168 | 0.21728 | 0.38915 | 0.07643 | -0.20078 | -0.17313 | -0.071256 | 122.9108 | 15.1319 | 15.305 | -0.15754 | 0.039573 | 65.5432 | -57.0032 | 65.8412 | 65.8342 | 0.29095 | -56.8313 | -57.144 | 122.8932 | 122.8069 | 123.0041 | 30.7145 | -123.1376 | 65.9613 | 66.1332 | 65.8204 | 65.8955 | -57.4212
1709.7969 | 123.143 | -65.7303 | 57.2708 | 0.0018314 | 0.050352 | 0.02518 | 0.060071 | 0.0077753 | 0.14612 | 0.0058755 | 0.03315 | -0.00338 | -0.007779 | 0.023617 | -0.0056639 | 57.2217 | -36.1192 | -50.5343 | 57.1904 | 57.1087 | 57.315 | -65.8714 | 0.092622 | 0.15146 | 0.094746 | 0.21271 | 0.38 | 0.17258 | -0.19162 | -0.14107 | -0.080405 | 122.952 | 15.196 | 15.337 | -0.16211 | 0.044163 | 65.5387 | -57.0581 | 65.8229 | 65.825 | 0.28637 | -56.8908 | -57.0982 | 122.9207 | 122.839 | 123.0453 | 29.6111 | -123.1422 | 65.943 | 66.1103 | 65.9029 | 65.8817 | -57.4624
1710.7969 | 123.2025 | -65.3549 | 57.5317 | 0.0018314 | 0.047147 | 0.027958 | 0.060712 | 0.0077753 | 0.14612 | -0.001755 | 0.033364 | -0.0031664 | -0.007779 | 0.023831 | -0.0060913 | 57.5834 | -39.718 | -50.3832 | 57.5613 | 57.4659 | 57.6813 | -65.4913 | 0.092622 | 0.14688 | 0.090168 | 0.21271 | 0.38915 | 0.10848 | -0.20078 | -0.13639 | 0.02952 | 122.9384 | 14.9717 | 15.1081 | -0.065876 | 0.14953 | 65.1541 | -57.319 | 65.4475 | 65.4451 | 0.29095 | -57.1426 | -57.4233 | 122.9162 | 122.8208 | 123.0362 | 25.6369 | -123.023 | 65.5676 | 65.7441 | 65.4634 | 65.5018 | -57.7325
1711.7969 | 123.1201 | -65.0162 | 57.9941 | 0.0018314 | 0.044583 | 0.029881 | 0.060071 | 0.0077753 | 0.14634 | -0.001755 | 0.032937 | -0.0038074 | -0.007779 | 0.023617 | -0.0060913 | 57.7345 | -42.1996 | -50.4336 | 57.7078 | 57.6353 | 57.8369 | -65.3448 | 0.088043 | 0.13772 | 0.094746 | 0.20813 | 0.39373 | 0.11306 | -0.1962 | -0.32861 | -0.28631 | 122.7507 | 14.5826 | 14.9112 | -0.3588 | -0.15714 | 64.82 | -57.786 | 65.1042 | 65.1109 | 0.29095 | -57.6003 | -57.881 | 122.7239 | 122.6515 | 122.8531 | 22.8166 | -123.3389 | 65.2243 | 65.4099 | 65.1292 | 65.1539 | -58.1903
1712.7969 | 123.1705 | -64.1235 | 58.8593 | -0.013431 | 0.043728 | 0.032231 | 0.060498 | 0.0064933 | 0.14847 | -0.0093855 | 0.03315 | -0.00338 | -0.0079926 | 0.023831 | -0.0065185 | 58.8608 | -56.0911 | -50.2505 | 58.8249 | 58.7571 | 58.9541 | -64.2184 | 0.055992 | 0.1194 | 0.062695 | 0.18524 | 0.3571 | -0.038035 | -0.22367 | -0.094834 | -0.03436 | 122.9843 | 13.8731 | 13.9679 | -0.10213 | 0.094862 | 63.8999 | -58.674 | 64.1795 | 64.1862 | 0.28637 | -58.5022 | -58.8973 | 122.9484 | 122.8807 | 123.0777 | 8.0325 | -123.0776 | 64.3088 | 64.4806 | 64.0855 | 64.2429 | -59.0829
1713.7969 | 123.1018 | -64.2563 | 58.7311 | -0.0057996 | 0.041378 | 0.033941 | 0.060284 | 0.0069205 | 0.14783 | -0.001755 | 0.032937 | -0.0038074 | -0.0075654 | 0.023617 | -0.0058775 | 58.7509 | -56.2101 | -50.3603 | 58.7196 | 58.6518 | 58.8488 | -64.3374 | 0.078886 | 0.13314 | 0.071853 | 0.19897 | 0.37084 | -0.005985 | -0.20536 | -0.081134 | -0.011489 | 123.0072 | 13.8959 | 13.9771 | -0.079276 | 0.11773 | 64.0509 | -58.5321 | 64.3352 | 64.3281 | 0.27721 | -58.3602 | -58.7371 | 122.9759 | 122.9081 | 123.1051 | 8.0462 | -123.0685 | 64.4553 | 64.6271 | 64.2503 | 64.3894 | -58.9364
1714.7969 | 123.0743 | -64.1373 | 58.8547 | -0.0057996 | 0.040309 | 0.036077 | 0.060498 | 0.0069205 | 0.14847 | -0.0093855 | 0.032723 | -0.0038074 | -0.007779 | 0.023404 | -0.0058775 | 58.8059 | -56.3887 | -50.3283 | 58.7791 | 58.6884 | 58.8992 | -64.2733 | 0.074307 | 0.12398 | 0.062695 | 0.18524 | 0.37084 | 0.058115 | -0.2191 | -0.13605 | -0.075566 | 122.9431 | 13.809 | 13.945 | -0.16624 | 0.044497 | 63.9182 | -58.6694 | 64.2116 | 64.2 | 0.28179 | -58.4838 | -58.7966 | 122.9164 | 122.8257 | 123.0364 | 7.7486 | -123.128 | 64.3225 | 64.5081 | 64.1954 | 64.2613 | -59.0738
1715.7969 | 123.1201 | -66.1652 | 56.8222 | 0.0018314 | 0.038386 | 0.036291 | 0.060284 | 0.0084163 | 0.14484 | 0.013506 | 0.032937 | -0.0035938 | -0.0079926 | 0.024045 | -0.0063049 | 56.9196 | -31.5955 | -50.3466 | 56.8974 | 56.8157 | 57.0265 | -66.1736 | 0.10178 | 0.15604 | 0.099325 | 0.22644 | 0.39831 | 0.094744 | -0.18246 | -0.008409 | 0.075186 | 123.0847 | 15.8186 | 15.827 | -0.00655 | 0.20432 | 65.9827 | -56.5958 | 66.2669 | 66.2645 | 0.28179 | -56.4239 | -56.7275 | 123.0626 | 122.9808 | 123.1917 | 34.5696 | -122.9958 | 66.3916 | 66.5635 | 66.2599 | 66.3212 | -57.0047
1716.7969 | 123.1384 | -66.0599 | 56.9229 | 0.0094624 | 0.037532 | 0.036932 | 0.060284 | 0.0084163 | 0.14441 | 0.0058755 | 0.032937 | -0.0035938 | -0.007779 | 0.023404 | -0.0056639 | 56.915 | -29.906 | -50.3374 | 56.8974 | 56.8019 | 57.0128 | -66.1736 | 0.10636 | 0.16061 | 0.1039 | 0.23102 | 0.40747 | 0.14969 | -0.18704 | -0.11369 | -0.025522 | 122.9749 | 15.7224 | 15.8361 | -0.121 | 0.089875 | 65.8728 | -56.6919 | 66.1662 | 66.1638 | 0.29095 | -56.5154 | -56.7732 | 122.9573 | 122.8618 | 123.0727 | 36.1539 | -123.0965 | 66.2909 | 66.4673 | 66.2096 | 66.2205 | -57.11
1717.7969 | 123.111 | -66.1148 | 56.8909 | -0.0057996 | 0.036463 | 0.037573 | 0.060071 | 0.0084163 | 0.1442 | -0.001755 | 0.03315 | -0.004021 | -0.007779 | 0.023831 | -0.0063049 | 56.9516 | -29.407 | -50.2962 | 56.9249 | 56.8294 | 57.0494 | -66.1278 | 0.10636 | 0.16977 | 0.11764 | 0.23102 | 0.41204 | 0.090166 | -0.17331 | -0.012974 | 0.033993 | 123.0664 | 15.8186 | 15.8315 | -0.061478 | 0.15855 | 65.9415 | -56.6598 | 66.2212 | 66.2324 | 0.29095 | -56.4788 | -56.8007 | 123.0397 | 122.9442 | 123.1642 | 36.7079 | -123.0187 | 66.3458 | 66.5269 | 66.205 | 66.2846 | -57.0642
1718.7969 | 123.111 | -65.1672 | 57.843 | 0.0018314 | 0.03625 | 0.038428 | 0.060071 | 0.010553 | 0.14206 | -0.001755 | 0.033364 | -0.00338 | -0.0079926 | 0.023617 | -0.0060913 | 57.7803 | -44.7315 | -46.2033 | 57.7444 | 57.6673 | 57.8781 | -65.3036 | 0.097201 | 0.15146 | 0.090168 | 0.21271 | 0.39373 | 0.168 | -0.18704 | -0.13634 | -0.098625 | 122.9475 | 18.964 | 19.1003 | -0.17568 | 0.035126 | 64.9802 | -57.6303 | 65.2644 | 65.2574 | 0.27721 | -57.4493 | -57.675 | 122.9116 | 122.8346 | 123.0454 | 20.4357 | -123.1466 | 65.3799 | 65.561 | 65.3352 | 65.3187 | -58.0301
1719.7969 | 123.1247 | -64.9979 | 57.962 | 0.0018314 | 0.036677 | 0.038642 | 0.059216 | 0.010553 | 0.14185 | -0.0093855 | 0.032509 | -0.0038074 | -0.007779 | 0.023831 | -0.0063049 | 57.9268 | -44.6033 | -46.043 | 57.9046 | 57.823 | 58.0292 | -65.1662 | 0.10178 | 0.15146 | 0.099325 | 0.21728 | 0.39373 | 0.1039 | -0.18704 | -0.16834 | -0.057399 | 122.9247 | 18.9548 | 19.1232 | -0.13902 | 0.067202 | 64.8108 | -57.7448 | 65.0996 | 65.0972 | 0.28637 | -57.5683 | -57.8581 | 122.9025 | 122.8209 | 123.0271 | 20.3945 | -123.1282 | 65.2151 | 65.3916 | 65.1018 | 65.1493 | -58.1491
1720.7969 | 123.1842 | -65.0711 | 57.8659 | 0.0018314 | 0.036677 | 0.039924 | 0.058361 | 0.010125 | 0.14228 | -0.0093855 | 0.032937 | -0.0035938 | -0.0075654 | 0.024045 | -0.0060913 | 57.8581 | -45.0017 | -46.7389 | 57.8314 | 57.7314 | 57.956 | -65.2257 | 0.10178 | 0.15604 | 0.094746 | 0.22186 | 0.39831 | 0.13595 | -0.18704 | -0.15463 | -0.034524 | 122.9292 | 18.3322 | 18.4868 | -0.13447 | 0.090074 | 64.8841 | -57.644 | 65.1729 | 65.1659 | 0.28179 | -57.4676 | -57.73 | 122.9025 | 122.8025 | 123.0271 | 20.0694 | -123.0916 | 65.293 | 65.4694 | 65.2071 | 65.2271 | -58.0529
1721.7969 | 123.1613 | -65.625 | 57.399 | 0.0018314 | 0.037532 | 0.041419 | 0.056438 | 0.0099119 | 0.14313 | -0.001755 | 0.032723 | -0.0035938 | -0.007779 | 0.023831 | -0.0060913 | 57.4323 | -44.3698 | -47.5218 | 57.4056 | 57.3193 | 57.5256 | -65.6562 | 0.092622 | 0.14688 | 0.094746 | 0.21728 | 0.38915 | 0.168 | -0.18704 | -0.031151 | 0.006605 | 123.0573 | 18.1032 | 18.1343 | -0.079651 | 0.1266 | 65.438 | -57.1817 | 65.7176 | 65.7197 | 0.28179 | -57.0098 | -57.231 | 123.0306 | 122.9443 | 123.1506 | 21.2552 | -123.0551 | 65.8423 | 66.0142 | 65.793 | 65.7719 | -57.586
1722.7969 | 123.0789 | -65.6433 | 57.3441 | -0.0057996 | 0.038386 | 0.042274 | 0.05537 | 0.010339 | 0.14292 | -0.0093855 | 0.032937 | -0.0035938 | -0.0079926 | 0.023617 | -0.0060913 | 57.2996 | -44.1226 | -46.8992 | 57.282 | 57.2049 | 57.3882 | -65.7844 | 0.10178 | 0.15146 | 0.099325 | 0.22644 | 0.38457 | 0.14511 | -0.19162 | -0.14105 | -0.062079 | 122.9429 | 18.7442 | 18.8852 | -0.13919 | 0.044178 | 65.4517 | -57.1176 | 65.7451 | 65.7426 | 0.29095 | -56.9595 | -57.1989 | 122.9253 | 122.8482 | 123.0315 | 21.5207 | -123.1284 | 65.8698 | 66.0279 | 65.7884 | 65.7948 | -57.5357
1723.7969 | 123.1613 | -65.7669 | 57.2296 | -0.0057996 | 0.038814 | 0.04377 | 0.053019 | 0.010125 | 0.14271 | 0.0058755 | 0.032937 | -0.0038074 | -0.007779 | 0.023831 | -0.0063049 | 57.1531 | -43.5732 | -47.2196 | 57.1309 | 57.04 | 57.2509 | -65.9217 | 0.10178 | 0.1423 | 0.10848 | 0.22644 | 0.39373 | 0.11306 | -0.17788 | -0.15482 | -0.098725 | 122.92 | 18.5473 | 18.7021 | -0.18959 | 0.021261 | 65.589 | -57.0032 | 65.8687 | 65.8754 | 0.28637 | -56.8359 | -57.1166 | 122.8978 | 122.8069 | 123.0178 | 22.1938 | -123.1513 | 65.9933 | 66.1606 | 65.88 | 65.9092 | -57.4075
1724.7969 | 123.2071 | -65.8081 | 57.0923 | -0.0057996 | 0.039668 | 0.044197 | 0.051951 | 0.010339 | 0.14249 | -0.001755 | 0.03315 | -0.0031664 | -0.0079926 | 0.024258 | -0.0058775 | 57.1943 | -43.358 | -47.1281 | 57.1721 | 57.0767 | 57.2921 | -65.8897 | 0.097201 | 0.13772 | 0.099325 | 0.22186 | 0.39373 | 0.13137 | -0.18704 | -0.081571 | 0.07981 | 123.0024 | 18.68 | 18.7616 | -0.015632 | 0.1998 | 65.6211 | -56.8704 | 65.9053 | 65.9074 | 0.28637 | -56.6986 | -56.9609 | 122.9802 | 122.8848 | 123.1002 | 22.4501 | -122.982 | 66.03 | 66.2018 | 65.9395 | 65.9458 | -57.2793
1725.7969 | 123.1064 | -69.7174 | 53.1784 | -0.013431 | 0.041378 | 0.046548 | 0.051951 | 0.014185 | 0.14356 | 0.013506 | 0.032723 | -0.00338 | -0.0075654 | 0.023617 | -0.0060913 | 56.7776 | -38.3307 | -42.6871 | 56.76 | 56.6829 | 56.8754 | -66.3842 | 0.097201 | 0.14688 | 0.11306 | 0.22186 | 0.40289 | 0.099323 | -0.16873 | 3.3332 | 3.5816 | 126.495 | 27.0303 | 23.6971 | 3.5045 | 3.697 | 69.5487 | -52.9565 | 69.8146 | 69.8305 | 0.28179 | -52.7755 | -53.0791 | 126.4774 | 126.4003 | 126.5928 | 31.3868 | -119.5626 | 69.9393 | 70.1203 | 69.8167 | 69.8643 | -53.3471
1726.7969 | 123.1201 | -73.3566 | 49.5758 | 0.0018314 | 0.044797 | 0.049539 | 0.052592 | 0.018245 | 0.14677 | -0.0093855 | 0.032937 | -0.0035938 | -0.007779 | 0.023831 | -0.0060913 | 56.1687 | -35.9315 | -34.7438 | 56.142 | 56.0601 | 56.2665 | -67.0436 | 0.12009 | 0.17435 | 0.12222 | 0.24933 | 0.41662 | 0.1039 | -0.17331 | 6.3131 | 6.5662 | 129.5253 | 38.6128 | 32.2997 | 6.4843 | 6.6907 | 73.1833 | -49.3265 | 73.4767 | 73.4788 | 0.29552 | -49.1592 | -49.4719 | 129.4986 | 129.4168 | 129.6231 | 37.4252 | -116.6194 | 73.606 | 73.7733 | 73.4605 | 73.531 | -49.7491
1727.7969 | 123.1201 | -75.7462 | 47.2046 | 0.0018314 | 0.080266 | 0.079881 | 0.070114 | 0.081275 | 0.16728 | -0.0093855 | 0.032937 | -0.0035938 | -0.007779 | 0.024045 | -0.0067321 | 47.2454 | 35.3207 | 38.8841 | 47.2095 | 47.1358 | 47.3565 | -75.9267 | 0.3124 | 0.39413 | 0.32826 | 0.43705 | 0.62266 | 0.38777 | 0.037319 | -0.18052 | 0.004933 | 122.9916 | 114.6302 | 114.8108 | -0.068782 | 0.15192 | 75.7835 | -46.7675 | 76.0586 | 76.0744 | 0.29094 | -46.5819 | -46.8168 | 122.9557 | 122.882 | 123.1027 | 111.0669 | -123.1313 | 76.1832 | 76.3688 | 76.1339 | 76.1403 | -47.1673
1728.7969 | 123.175 | -68.8797 | 54.0253 | 0.0094624 | 0.077061 | 0.077745 | 0.068832 | 0.083626 | 0.15916 | -0.024647 | 0.032723 | -0.0035938 | -0.007779 | 0.023617 | -0.0058775 | 53.9024 | -62.3317 | 48.3337 | 53.8802 | 53.8027 | 54.0001 | -69.1407 | 0.19793 | 0.24761 | 0.20464 | 0.32259 | 0.49904 | 0.23668 | -0.095467 | -0.26101 | -0.14504 | 122.7821 | 117.2134 | 117.4744 | -0.22255 | -0.025202 | 68.7842 | -53.7027 | 69.0776 | 69.0843 | 0.3001 | -53.5262 | -53.7886 | 122.7599 | 122.6824 | 122.8798 | 6.548 | -123.166 | 69.2023 | 69.3787 | 69.1164 | 69.1273 | -54.1207
1729.7969 | 123.0286 | -69.2688 | 53.7964 | -0.0057996 | 0.078557 | 0.079027 | 0.070114 | 0.083626 | 0.16493 | 0.0058755 | 0.032937 | -0.0038074 | -0.007779 | 0.023831 | -0.0060913 | 53.6918 | -62.2447 | 48.0727 | 53.6742 | 53.5829 | 53.8032 | -69.3605 | 0.19793 | 0.26592 | 0.20464 | 0.32717 | 0.49904 | 0.25957 | -0.08173 | -0.091702 | -0.12218 | 122.9606 | 117.3415 | 117.4332 | -0.21345 | 0.0068 | 69.1871 | -53.4692 | 69.4667 | 69.4734 | 0.28636 | -53.2973 | -53.5368 | 122.943 | 122.8517 | 123.072 | 7.0241 | -123.1569 | 69.596 | 69.7678 | 69.5284 | 69.5347 | -53.8781
1730.8125 | 123.1018 | -75.6454 | 47.3282 | -0.0057996 | 0.099711 | 0.097617 | 0.082294 | 0.08213 | 0.2177 | -0.001755 | 0.03315 | -0.0038074 | -0.007779 | 0.023831 | -0.0060913 | 47.1172 | 34.9087 | 40.0928 | 47.0767 | 47.0076 | 47.2192 | -75.8672 | 0.32156 | 0.38955 | 0.33284 | 0.44621 | 0.61808 | 0.3603 | 0.037319 | -0.22171 | -0.25144 | 122.7627 | 115.7382 | 115.9599 | -0.32059 | -0.10903 | 75.6828 | -46.882 | 75.967 | 75.9783 | 0.29552 | -46.7101 | -46.9679 | 122.7222 | 122.653 | 122.8646 | 110.5541 | -123.1953 | 76.0917 | 76.2635 | 76.0058 | 76.035 | -47.2909
1731.7969 | 123.1522 | -63.2217 | 59.7656 | -0.0057996 | 0.045224 | 0.051035 | 0.052378 | 0.0058523 | 0.16236 | 0.013506 | 0.032723 | -0.0038074 | -0.007779 | 0.024045 | -0.0060913 | 59.1584 | -57.7531 | -52.21 | 59.1408 | 59.096 | 59.2563 | -63.9207 | 0.060571 | 0.10109 | 0.058117 | 0.17608 | 0.3571 | -0.001407 | -0.2191 | -0.699 | -0.62482 | 122.3801 | 11.0118 | 11.7108 | -0.66967 | -0.50932 | 63.0026 | -59.5895 | 63.2823 | 63.2799 | 0.27721 | -59.4085 | -59.767 | 122.3625 | 122.3177 | 122.478 | 5.4687 | -123.6864 | 63.3978 | 63.5788 | 63.2203 | 63.3228 | -59.9847
1732.7969 | 123.6694 | -67.7856 | 55.0827 | -0.0057996 | 0.050352 | 0.055522 | 0.055583 | 0.0045703 | 0.17668 | -0.001755 | 0.03315 | -0.0035938 | -0.0075654 | 0.023617 | -0.0063049 | 59.1676 | -59.8913 | -51.7704 | 59.1362 | 59.0639 | 59.2563 | -63.9345 | 0.051413 | 0.082776 | 0.062695 | 0.1715 | 0.34337 | -0.060928 | -0.23283 | 3.8512 | 4.0535 | 126.9532 | 16.0152 | 12.164 | 3.9812 | 4.1736 | 67.5528 | -54.9112 | 67.8371 | 67.8483 | 0.29553 | -54.7393 | -55.1436 | 126.9219 | 126.8496 | 127.0419 | 7.8944 | -119.0172 | 67.9571 | 68.129 | 67.7247 | 67.8684 | -55.3155
1733.7969 | 123.0972 | -69.635 | 53.3524 | -0.0057996 | 0.07642 | 0.07924 | 0.069686 | 0.05414 | 0.19313 | 0.0058755 | 0.032723 | -0.0035938 | -0.007779 | 0.024472 | -0.0058775 | 54.9829 | -63.2566 | 15.8004 | 54.9745 | 54.8238 | 55.076 | -68.1105 | 0.14299 | 0.19724 | 0.14969 | 0.27223 | 0.43952 | 0.15427 | -0.14583 | 1.5246 | 1.6221 | 124.6179 | 85.4354 | 83.9108 | 1.4715 | 1.7237 | 69.4892 | -53.0801 | 69.778 | 69.7847 | 0.29552 | -52.9128 | -53.1981 | 124.6095 | 124.4588 | 124.711 | 6.3784 | -121.4628 | 69.9072 | 70.0745 | 69.7893 | 69.8323 | -53.4982
1734.7969 | 123.0927 | -69.635 | 53.2196 | -0.013431 | 0.083685 | 0.08501 | 0.073746 | 0.085121 | 0.17711 | -0.0093855 | 0.032937 | -0.0042346 | -0.0075654 | 0.023831 | -0.0063049 | 53.2294 | -67.0431 | 50.3939 | 53.2118 | 53.125 | 53.3453 | -69.7955 | 0.17504 | 0.25219 | 0.1909 | 0.30885 | 0.4853 | 0.28247 | -0.095467 | -0.16049 | -0.007815 | 122.8644 | 120.0289 | 120.1894 | -0.094562 | 0.12572 | 69.5395 | -52.9108 | 69.81 | 69.8259 | 0.28637 | -52.7343 | -52.9371 | 122.8468 | 122.7601 | 122.9803 | 2.5919 | -123.0151 | 69.9439 | 70.1203 | 69.9175 | 69.8872 | -53.3151
1735.7969 | 123.111 | -71.2555 | 51.7044 | 0.0018314 | 0.082403 | 0.084155 | 0.072892 | 0.084908 | 0.17475 | -0.001755 | 0.032937 | -0.0035938 | -0.0075654 | 0.024045 | -0.0060913 | 52.5655 | -67.5742 | 49.7667 | 52.5388 | 52.4565 | 52.6677 | -70.4686 | 0.17046 | 0.22929 | 0.17716 | 0.29512 | 0.47157 | 0.20005 | -0.10462 | 0.78689 | 0.83436 | 123.821 | 121.0222 | 120.2353 | 0.75211 | 0.96329 | 71.1509 | -51.4093 | 71.426 | 71.4327 | 0.28179 | -51.2328 | -51.5044 | 123.7943 | 123.712 | 123.9232 | 3.6813 | -122.173 | 71.5506 | 71.7271 | 71.4555 | 71.4848 | -51.809
1736.7969 | 123.1842 | -70.6329 | 52.2446 | -0.0057996 | 0.087959 | 0.089497 | 0.076311 | 0.084694 | 0.18993 | 0.0058755 | 0.032723 | -0.0038074 | -0.0075654 | 0.024258 | -0.0060913 | 52.2405 | -66.5989 | 49.0662 | 52.2137 | 52.1406 | 52.3518 | -70.7983 | 0.17962 | 0.23845 | 0.18632 | 0.2997 | 0.48072 | 0.25957 | -0.10462 | -0.16535 | -0.030867 | 122.8734 | 119.6991 | 119.8645 | -0.10399 | 0.1072 | 70.5283 | -51.9449 | 70.8126 | 70.8193 | 0.29095 | -51.7638 | -51.985 | 122.8466 | 122.7735 | 122.9847 | 4.034 | -123.0429 | 70.9326 | 71.1137 | 70.8925 | 70.8714 | -52.3492
1737.7969 | 123.024 | -70.0058 | 52.9816 | -0.0057996 | 0.083899 | 0.086292 | 0.074387 | 0.08448 | 0.18074 | 0.0058755 | 0.032937 | -0.0035938 | -0.0079926 | 0.023831 | -0.0060913 | 52.8402 | -67.0934 | 49.1852 | 52.818 | 52.7404 | 52.9424 | -70.1939 | 0.17962 | 0.22929 | 0.17258 | 0.2997 | 0.48072 | 0.19547 | -0.10462 | -0.18807 | -0.16352 | 122.846 | 119.191 | 119.3791 | -0.24115 | -0.039157 | 69.9012 | -52.6819 | 70.1854 | 70.1784 | 0.27721 | -52.5008 | -52.7861 | 122.8238 | 122.7462 | 122.9482 | 2.9124 | -123.1754 | 70.3055 | 70.4865 | 70.2013 | 70.2351 | -53.0862
1738.7969 | 123.111 | -70.1752 | 52.7344 | 0.0018314 | 0.093728 | 0.095266 | 0.080371 | 0.083839 | 0.20745 | -0.001755 | 0.033364 | -0.0035938 | -0.0082062 | 0.024258 | -0.0058775 | 52.7761 | -64.9644 | 48.7915 | 52.7585 | 52.6717 | 52.8875 | -70.2488 | 0.16588 | 0.22929 | 0.16801 | 0.29054 | 0.46241 | 0.21379 | -0.11836 | -0.073642 | 0.024154 | 122.9513 | 118.9667 | 119.0403 | -0.062647 | 0.15309 | 70.0568 | -52.4438 | 70.3411 | 70.3432 | 0.28637 | -52.272 | -52.5206 | 122.9337 | 122.8469 | 123.0626 | 5.2108 | -122.9832 | 70.4657 | 70.6376 | 70.389 | 70.4045 | -52.8527
1739.7969 | 123.0972 | -70.1706 | 52.771 | -0.0057996 | 0.099711 | 0.10082 | 0.083576 | 0.084694 | 0.22197 | -0.001755 | 0.032937 | -0.00338 | -0.0079926 | 0.024045 | -0.0058775 | 52.6067 | -65.903 | 49.112 | 52.5708 | 52.4977 | 52.7181 | -70.3862 | 0.17504 | 0.22014 | 0.16801 | 0.28596 | 0.45783 | 0.20005 | -0.11836 | -0.21559 | -0.20018 | 122.7773 | 119.2826 | 119.4981 | -0.27327 | -0.052937 | 70.0522 | -52.485 | 70.3456 | 70.3386 | 0.28637 | -52.3132 | -52.5709 | 122.7414 | 122.6683 | 122.8887 | 4.2676 | -123.1572 | 70.4566 | 70.6284 | 70.3706 | 70.3907 | -52.8894
1740.8125 | 123.3307 | -69.7906 | 53.1326 | -0.0057996 | 0.12877 | 0.12518 | 0.10067 | 0.06461 | 0.31535 | 0.013506 | 0.032723 | -0.0035938 | -0.0079926 | 0.024045 | -0.0060913 | 53.5178 | -59.8821 | 24.8425 | 53.5735 | 53.5509 | 53.6933 | -69.4017 | 0.14299 | 0.19724 | 0.14969 | 0.25849 | 0.43952 | 0.17258 | -0.14125 | 0.38894 | 0.44085 | 123.3085 | 94.6331 | 94.2442 | 0.41825 | 0.56067 | 69.6494 | -52.8741 | 69.9336 | 69.9403 | 0.29095 | -52.6931 | -52.96 | 123.3641 | 123.3415 | 123.4839 | 9.9085 | -122.5343 | 70.0491 | 70.2302 | 69.9632 | 69.9879 | -53.2739
1741.7969 | 123.2391 | -66.6458 | 55.3986 | -0.013431 | 0.091377 | 0.093343 | 0.080584 | 0.011407 | 0.27753 | -0.0093855 | 0.032723 | -0.0038074 | -0.007779 | 0.024258 | -0.0060913 | 57.4095 | -59.3831 | -45.7592 | 57.3919 | 57.3193 | 57.5027 | -65.6699 | 0.042256 | 0.078197 | 0.048959 | 0.16234 | 0.34794 | -0.060928 | -0.23741 | 0.97593 | 1.9933 | 124.0553 | 20.8866 | 19.9107 | 1.9208 | 2.1041 | 66.4084 | -55.2362 | 66.6881 | 66.6948 | 0.28637 | -55.0506 | -55.4595 | 124.0377 | 123.9651 | 124.1485 | 7.2627 | -121.0684 | 66.8082 | 66.9938 | 66.5849 | 66.724 | -55.636
1742.7969 | 122.8317 | -65.3961 | 57.5226 | -0.0057996 | 0.087745 | 0.090565 | 0.078661 | 0.0064933 | 0.27411 | -0.001755 | 0.032723 | -0.0035938 | -0.0079926 | 0.024045 | -0.0063049 | 57.7208 | -59.5387 | -51.2073 | 57.7032 | 57.6032 | 57.814 | -65.3402 | 0.046835 | 0.06904 | 0.030644 | 0.15776 | 0.33421 | -0.070086 | -0.24657 | 0.055912 | 0.1806 | 123.1169 | 14.1888 | 14.1329 | 0.080647 | 0.29146 | 65.1496 | -57.3648 | 65.443 | 65.4268 | 0.27721 | -57.1884 | -57.5927 | 123.0993 | 122.9993 | 123.2102 | 5.8574 | -122.8628 | 65.5539 | 65.7303 | 65.326 | 65.4652 | -57.7691
1743.7969 | 123.0652 | -73.3475 | 49.5667 | -0.0057996 | 0.10398 | 0.10531 | 0.095115 | 0.027859 | 0.30253 | -0.001755 | 0.032937 | -0.0038074 | -0.0079926 | 0.024045 | -0.0063049 | 52.9318 | -23.8806 | -19.2006 | 52.905 | 52.7633 | 53.0569 | -69.9878 | 0.14757 | 0.19724 | 0.14511 | 0.26307 | 0.43036 | 0.085587 | -0.14583 | 3.3597 | 3.3384 | 126.2793 | 54.1469 | 50.7873 | 3.1967 | 3.4902 | 73.2016 | -49.3036 | 73.495 | 73.4926 | 0.29095 | -49.1363 | -49.4811 | 126.2525 | 126.1108 | 126.4043 | 49.4669 | -119.5545 | 73.6105 | 73.7778 | 73.4331 | 73.5447 | -49.7125
1744.7969 | 122.9965 | -76.8219 | 45.9091 | 0.0094624 | 0.38368 | 0.34677 | 0.30346 | 0.074011 | 1.007 | -0.001755 | 0.032937 | -0.0038074 | -0.0075654 | 0.024045 | -0.0060913 | 43.743 | -30.6798 | 27.5757 | 43.7528 | 43.7611 | 43.8859 | -78.9121 | 0.1613 | 0.21098 | 0.15427 | 0.27223 | 0.4441 | 0.168 | -0.12294 | -2.0902 | -2.1563 | 120.5649 | 104.3976 | 106.4879 | -2.148 | -2.0232 | 76.699 | -45.6369 | 76.9832 | 76.9762 | 0.27721 | -45.465 | -45.7411 | 120.5747 | 120.583 | 120.7078 | 46.1421 | -124.8213 | 77.0941 | 77.266 | 76.9899 | 77.0329 | -46.0321
1745.7969 | 122.7448 | -64.8788 | 58.0948 | 0.0018314 | 0.074283 | 0.078172 | 0.073533 | 0.0015789 | 0.24569 | 0.013506 | 0.03315 | -0.0035938 | -0.0082062 | 0.024258 | -0.0060913 | 56.2099 | -60.8574 | -59.7138 | 56.2244 | 56.2067 | 56.3077 | -66.7734 | 0.005626 | 0.041567 | 0.003172 | 0.11656 | 0.28842 | -0.074664 | -0.29236 | -1.8946 | -1.8704 | 121.0888 | 5.1651 | 7.0596 | -1.8881 | -1.7871 | 64.5865 | -57.9782 | 64.8845 | 64.882 | 0.29553 | -57.8064 | -58.1695 | 121.1032 | 121.0855 | 121.1865 | 4.0215 | -124.8682 | 64.9954 | 65.1673 | 64.8042 | 64.9204 | -58.3871
1746.7969 | 123.1384 | -68.1839 | 54.7897 | 0.0018314 | 0.10527 | 0.10574 | 0.094687 | 0.0039293 | 0.32838 | -0.001755 | 0.03315 | -0.00338 | -0.0084198 | 0.024045 | -0.0063049 | 57.4186 | -57.1441 | -55.4651 | 57.4102 | 57.3422 | 57.521 | -65.6241 | 0.02852 | 0.06904 | 0.035223 | 0.15318 | 0.31589 | -0.051771 | -0.25572 | 2.5598 | 2.6204 | 125.6025 | 12.7188 | 10.159 | 2.5525 | 2.7313 | 67.9282 | -54.6365 | 68.2124 | 68.2191 | 0.29095 | -54.4738 | -54.8415 | 125.5941 | 125.5261 | 125.7049 | 11.0398 | -120.4138 | 68.3371 | 68.4998 | 68.1321 | 68.2529 | -55.0455
1747.7969 | 122.9416 | -65.0848 | 57.9254 | 0.0094624 | 0.13689 | 0.13309 | 0.11029 | 0.0054249 | 0.40359 | -0.0093855 | 0.032937 | -0.0035938 | -0.0082062 | 0.023831 | -0.0060913 | 57.4781 | -56.3749 | -53.9726 | 57.456 | 57.3834 | 57.5805 | -65.5417 | 0.033099 | 0.06904 | 0.035223 | 0.15318 | 0.32963 | -0.05635 | -0.24657 | -0.45684 | -0.46946 | 122.563 | 11.1122 | 11.5691 | -0.54197 | -0.34488 | 64.8383 | -57.7722 | 65.1179 | 65.1201 | 0.28179 | -57.5958 | -57.9818 | 122.5408 | 122.4683 | 122.6654 | 8.7099 | -123.4671 | 65.238 | 65.4145 | 65.0285 | 65.1539 | -58.172
1748.7969 | 123.2529 | -64.7736 | 58.0536 | 0.0018314 | 0.13454 | 0.13138 | 0.1152 | 0.0017927 | 0.40872 | -0.001755 | 0.03315 | -0.00338 | -0.0079926 | 0.024258 | -0.0060913 | 57.8948 | -58.8016 | -57.0446 | 57.8772 | 57.7772 | 57.9926 | -65.1296 | 0.02852 | 0.06904 | 0.039802 | 0.15318 | 0.31589 | -0.065507 | -0.24657 | -0.35601 | -0.17642 | 122.6683 | 7.7289 | 8.0849 | -0.27636 | -0.06098 | 64.527 | -57.9004 | 64.8021 | 64.8134 | 0.28637 | -57.7377 | -58.1191 | 122.6507 | 122.5508 | 122.7662 | 5.972 | -123.1832 | 64.9267 | 65.0895 | 64.7081 | 64.8426 | -58.3002
1749.7969 | 122.9095 | -64.4211 | 58.5342 | -0.0057996 | 0.088172 | 0.088642 | 0.087636 | -0.00098494 | 0.28906 | 0.0058755 | 0.03315 | -0.0035938 | -0.0079926 | 0.024045 | -0.0063049 | 58.4671 | -62.176 | -60.9819 | 58.4449 | 58.3771 | 58.5604 | -64.516 | 0.023941 | 0.06904 | 0.030644 | 0.13945 | 0.31132 | -0.065507 | -0.2603 | -0.094917 | -0.089355 | 122.8881 | 3.4391 | 3.534 | -0.15717 | 0.026115 | 64.1608 | -58.3948 | 64.445 | 64.4517 | 0.29095 | -58.2229 | -58.5997 | 122.866 | 122.7981 | 122.9814 | 2.2451 | -123.0502 | 64.5605 | 64.7324 | 64.3556 | 64.4901 | -58.7945
1750.8125 | 122.9416 | -71.9147 | 50.8392 | 0.0018314 | 0.52385 | 0.48523 | 0.68958 | 0.012476 | 1.7172 | -0.001755 | 0.032937 | -0.0029528 | -0.0082062 | 0.023831 | -0.0065185 | 55.7658 | -46.1005 | -36.8681 | 55.7665 | 55.6251 | 55.891 | -66.8925 | 0.083464 | 0.13314 | 0.085589 | 0.20355 | 0.36168 | 0.058115 | -0.20536 | 5.0222 | 4.9273 | 127.6805 | 35.0465 | 30.0243 | 4.7859 | 5.0518 | 71.7093 | -50.6357 | 71.9981 | 72.0003 | 0.29095 | -50.4776 | -50.7811 | 127.6812 | 127.5398 | 127.8057 | 25.8141 | -117.7317 | 72.1182 | 72.2764 | 71.9728 | 72.0478 | -51.0446
1751.7969 | 123.0286 | -63.9267 | 58.9005 | -0.013431 | 0.16339 | 0.15381 | 0.13913 | 0.0035019 | 0.48029 | -0.001755 | 0.032723 | -0.0035938 | -0.0079926 | 0.023831 | -0.0063049 | 58.1008 | -55.7568 | -54.6548 | 58.0924 | 58.0199 | 58.2032 | -64.8274 | 0.042256 | 0.087354 | 0.048959 | 0.15776 | 0.32963 | -0.05635 | -0.24199 | -0.90067 | -0.8081 | 122.0275 | 9.2719 | 10.1726 | -0.88054 | -0.69723 | 63.6847 | -58.7427 | 63.969 | 63.9757 | 0.29095 | -58.5708 | -58.9568 | 122.019 | 121.9466 | 122.1299 | 8.1699 | -123.7278 | 64.0845 | 64.2563 | 63.8703 | 64.0141 | -59.1424
1752.7969 | 123.024 | -70.5551 | 52.2308 | 0.0094624 | 0.26595 | 0.2427 | 0.24918 | 0.060336 | 0.72942 | -0.001755 | 0.032937 | -0.00338 | -0.0079926 | 0.024472 | -0.0060913 | 48.8204 | 10.7886 | 11.625 | 48.8577 | 48.8254 | 48.9957 | -73.944 | 0.2254 | 0.2934 | 0.23211 | 0.35464 | 0.52651 | 0.31452 | -0.0451 | -3.3889 | -3.3731 | 119.3755 | 82.1801 | 85.569 | -3.4054 | -3.2352 | 70.51 | -51.8762 | 70.7805 | 70.7872 | 0.27721 | -51.7043 | -51.9163 | 119.4129 | 119.3805 | 119.5508 | 81.3437 | -126.1748 | 70.9098 | 71.0816 | 70.8696 | 70.8485 | -52.2759
1753.7969 | 122.9828 | -67.9871 | 54.9362 | -0.013431 | 0.4418 | 0.39869 | 0.36051 | 0.039825 | 1.1854 | 0.0058755 | 0.03315 | -0.00338 | -0.0079926 | 0.024258 | -0.0063049 | 51.398 | -8.9864 | -7.6587 | 51.4628 | 51.4171 | 51.6009 | -70.8487 | 0.17504 | 0.22472 | 0.17716 | 0.2997 | 0.46241 | 0.15427 | -0.10004 | -2.8616 | -3.4734 | 119.3851 | 60.3283 | 63.1899 | -3.5191 | -3.3353 | 67.887 | -54.6365 | 68.1621 | 68.1642 | 0.27721 | -54.4738 | -54.782 | 119.4499 | 119.4042 | 119.5879 | 59.0007 | -125.7849 | 68.2868 | 68.4495 | 68.1413 | 68.2118 | -55.0363
1754.7969 | 122.9233 | -69.1635 | 53.6911 | -0.0057996 | 0.15527 | 0.14591 | 0.1511 | 0.035551 | 0.43884 | -0.0093855 | 0.032723 | -0.0035938 | -0.007779 | 0.024472 | -0.0060913 | 52.9272 | -16.912 | -16.5864 | 52.9096 | 52.8503 | 53.0431 | -69.942 | 0.15672 | 0.21098 | 0.16801 | 0.27223 | 0.4441 | 0.22752 | -0.12752 | -0.77851 | -0.78149 | 122.0907 | 52.5771 | 53.3557 | -0.84079 | -0.64796 | 69.036 | -53.4189 | 69.3202 | 69.3315 | 0.29552 | -53.247 | -53.4636 | 122.0731 | 122.0138 | 122.2067 | 52.2516 | -123.6331 | 69.4357 | 69.6076 | 69.391 | 69.3745 | -53.8186
1755.7969 | 123.024 | -61.3358 | 61.4639 | -0.013431 | 0.31702 | 0.30403 | 0.21285 | 0.015253 | 0.67344 | 0.0058755 | 0.032937 | -0.0035938 | -0.007779 | 0.024258 | -0.0065185 | 18.6626 | -4.0278 | -3.4925 | 19.1303 | 18.6137 | 19.5049 | -24.9404 | 0.088043 | 0.14688 | 0.099325 | 0.21271 | 0.38915 | 0.035222 | -0.18704 | 36.3954 | -42.3337 | 79.9983 | 57.8433 | 21.4479 | -42.8502 | -41.9591 | 61.1487 | -61.2512 | 61.4238 | 61.4351 | 0.28637 | -61.0748 | -61.4287 | 80.466 | 79.9494 | 80.8406 | 57.308 | -86.4043 | 61.5485 | 61.7249 | 61.371 | 61.4826 | -61.651
1756.7969 | 123.0515 | -61.3037 | 61.4914 | 0.0094624 | 0.0091132 | 0.018128 | -0.024548 | -0.0037625 | -0.0013034 | -0.0093855 | 0.032723 | -0.0031664 | -0.0079926 | 0.024045 | -0.0058775 | 0.065145 | 0.17081 | 0.078578 | 0.35888 | 0.38041 | 0.58609 | -0.081373 | 0.051413 | 0.10567 | 0.053538 | 0.17608 | 0.34337 | -0.042614 | -0.22367 | 61.2223 | -61.1325 | 61.3689 | 61.3823 | 0.15995 | -61.111 | -60.9053 | 61.08 | -61.3153 | 61.3551 | 61.3572 | 0.27721 | -61.148 | -61.534 | 61.6626 | 61.6841 | 61.8898 | 61.4745 | -61.5728 | 61.4798 | 61.6471 | 61.2611 | 61.4094 | -61.7151
1757.7969 | 122.9782 | -61.3861 | 61.5189 | -0.013431 | 0.0091132 | 0.018556 | -0.024975 | -0.0035489 | -0.0017306 | -0.001755 | 0.032723 | -0.0035938 | -0.007779 | 0.024472 | -0.0060913 | 0.05141 | 0.17539 | 0.083156 | 0.3543 | 0.35752 | 0.55862 | -0.072215 | 0.055992 | 0.11025 | 0.058117 | 0.17608 | 0.34337 | 0.062694 | -0.22825 | 61.3139 | -61.1646 | 61.4375 | 61.4693 | 0.15537 | -61.1613 | -60.9602 | 61.1579 | -61.3428 | 61.4421 | 61.4442 | 0.28637 | -61.1755 | -61.4562 | 61.7404 | 61.7436 | 61.9447 | 61.5615 | -61.5911 | 61.5622 | 61.7295 | 61.4488 | 61.4964 | -61.7471
1758.7969 | 123.0103 | -61.3312 | 61.5051 | 0.0094624 | 0.0086858 | 0.018769 | -0.024975 | -0.0039763 | -0.0013034 | -0.0093855 | 0.032937 | -0.00338 | -0.0082062 | 0.024258 | -0.0060913 | 0.046831 | 0.16624 | 0.078578 | 0.249 | 0.34836 | 0.5632 | -0.067636 | 0.055992 | 0.11483 | 0.058117 | 0.17608 | 0.35252 | -0.042614 | -0.22825 | 61.2635 | -61.2561 | 61.378 | 61.4098 | 0.14621 | -61.1568 | -60.9419 | 61.1029 | -61.329 | 61.3872 | 61.3893 | 0.28637 | -61.1526 | -61.5477 | 61.5802 | 61.6795 | 61.8944 | 61.4974 | -61.5728 | 61.5073 | 61.6837 | 61.2886 | 61.446 | -61.7334
1759.7969 | 123.0515 | -61.3586 | 61.5326 | -0.0057996 | 0.0086858 | 0.018128 | -0.024548 | -0.0037625 | -0.001517 | -0.0093855 | 0.032723 | -0.00338 | -0.0079926 | 0.024258 | -0.0063049 | 0.042253 | 0.17081 | 0.083156 | 0.24442 | 0.34378 | 0.55404 | -0.067636 | 0.046835 | 0.11025 | 0.058117 | 0.16692 | 0.35252 | -0.05635 | -0.22825 | 61.291 | -61.2882 | 61.4009 | 61.4418 | 0.15079 | -61.1888 | -60.9786 | 61.1304 | -61.3657 | 61.4055 | 61.4168 | 0.28637 | -61.1801 | -61.5889 | 61.6031 | 61.7024 | 61.9127 | 61.5295 | -61.6002 | 61.5256 | 61.7112 | 61.3023 | 61.4689 | -61.7608
1760.7969 | 123.1018 | -61.3358 | 61.528 | -0.0057996 | 0.0088994 | 0.018769 | -0.024975 | -0.0041899 | -0.0013034 | 0.0058755 | 0.03315 | -0.0038074 | -0.0079926 | 0.024045 | -0.0063049 | 0.046831 | 0.15708 | 0.051108 | 0.23984 | 0.35294 | 0.55404 | -0.053899 | 0.051413 | 0.10567 | 0.058117 | 0.18066 | 0.34794 | -0.065507 | -0.23283 | 61.2819 | -61.2882 | 61.3826 | 61.3869 | 0.10501 | -61.1751 | -60.974 | 61.1029 | -61.3474 | 61.3872 | 61.3939 | 0.29095 | -61.1801 | -61.5935 | 61.5756 | 61.6887 | 61.8898 | 61.4928 | -61.5819 | 61.5164 | 61.6837 | 61.2702 | 61.4414 | -61.7608
1761.7969 | 123.1613 | -61.3358 | 61.5234 | 0.0094624 | 0.0099678 | 0.018342 | -0.024975 | -0.0039763 | -0.00066244 | -0.001755 | 0.032937 | -0.0038074 | -0.007779 | 0.024045 | -0.0063049 | 0.042253 | 0.16166 | 0.051108 | 0.23069 | 0.15604 | 0.54946 | -0.058478 | 0.055992 | 0.11025 | 0.058117 | 0.17608 | 0.35252 | 0.039801 | -0.22367 | 61.2773 | -61.2928 | 61.378 | 61.3869 | 0.10959 | -61.3674 | -60.974 | 61.1121 | -61.3474 | 61.3917 | 61.3939 | 0.28179 | -61.1709 | -61.4836 | 61.5664 | 61.4918 | 61.8852 | 61.4974 | -61.5819 | 61.5118 | 61.6883 | 61.3756 | 61.446 | -61.7471
1762.7969 | 123.1247 | -61.377 | 61.496 | 0.0094624 | 0.0099678 | 0.018769 | -0.024975 | -0.0041899 | -0.00023504 | -0.001755 | 0.032937 | -0.00338 | -0.0079926 | 0.024045 | -0.0063049 | 0.037675 | 0.16166 | 0.055687 | 0.23069 | 0.16062 | 0.5403 | -0.058478 | 0.055992 | 0.10109 | 0.067274 | 0.17608 | 0.35252 | -0.070086 | -0.22825 | 61.3185 | -61.2653 | 61.4146 | 61.4326 | 0.11417 | -61.3354 | -60.9557 | 61.1487 | -61.3199 | 61.4329 | 61.4442 | 0.29553 | -61.1434 | -61.5661 | 61.6076 | 61.5376 | 61.9173 | 61.5386 | -61.5545 | 61.553 | 61.7295 | 61.3069 | 61.478 | -61.7242
1763.7969 | 123.1155 | -61.3586 | 61.5234 | -0.0057996 | 0.0095404 | 0.018769 | -0.024762 | -0.0037625 | -0.00066244 | -0.001755 | 0.032937 | -0.0031664 | -0.0079926 | 0.024258 | -0.0060913 | 0.037675 | 0.17081 | 0.04653 | 0.23526 | 0.15146 | 0.54946 | -0.053899 | 0.060571 | 0.11025 | 0.062695 | 0.17608 | 0.35252 | -0.060928 | -0.22367 | 61.3047 | -61.2882 | 61.3963 | 61.4052 | 0.10043 | -61.372 | -60.974 | 61.135 | -61.3474 | 61.4192 | 61.4213 | 0.28637 | -61.1709 | -61.5844 | 61.5939 | 61.5101 | 61.9081 | 61.5295 | -61.5773 | 61.5347 | 61.7112 | 61.2977 | 61.4689 | -61.7471
1764.7969 | 123.111 | -61.3586 | 61.5326 | -0.013431 | 0.0099678 | 0.018556 | -0.024975 | -0.0041899 | -0.00044864 | -0.001755 | 0.032723 | -0.0035938 | -0.0079926 | 0.024258 | -0.0065185 | 0.037675 | 0.16624 | 0.051108 | 0.22611 | 0.15604 | 0.54488 | -0.058478 | 0.051413 | 0.10567 | 0.062695 | 0.16692 | 0.34794 | -0.065507 | -0.22367 | 61.3002 | -61.3065 | 61.3963 | 61.4098 | 0.10959 | -61.3766 | -60.9877 | 61.135 | -61.3657 | 61.4101 | 61.4213 | 0.28637 | -61.1846 | -61.5981 | 61.5847 | 61.5147 | 61.9035 | 61.5249 | -61.5911 | 61.5256 | 61.7066 | 61.2931 | 61.4643 | -61.7563
1765.7969 | 123.2162 | -61.3312 | 61.5326 | 0.0018314 | 0.0095404 | 0.017915 | -0.024762 | -0.0041899 | -0.00066244 | -0.0093855 | 0.03315 | -0.00338 | -0.0082062 | 0.024258 | -0.0060913 | 0.042253 | 0.16624 | 0.04653 | 0.23984 | 0.15604 | 0.54488 | -0.053899 | 0.055992 | 0.11025 | 0.053538 | 0.17608 | 0.35252 | -0.065507 | -0.22367 | 61.2773 | -61.2928 | 61.3734 | 61.3777 | 0.10043 | -61.3766 | -60.9877 | 61.1075 | -61.3565 | 61.3872 | 61.3847 | 0.27721 | -61.1801 | -61.5981 | 61.571 | 61.4872 | 61.8761 | 61.4974 | -61.5865 | 61.5073 | 61.6837 | 61.2657 | 61.4414 | -61.7563
1766.7969 | 123.1384 | -61.3678 | 61.528 | -0.0057996 | 0.0095404 | 0.017915 | -0.024762 | -0.0044035 | -0.00066244 | -0.001755 | 0.032937 | -0.0035938 | -0.0079926 | 0.024686 | -0.0063049 | 0.033096 | 0.16624 | 0.051108 | 0.23526 | 0.15604 | 0.54488 | -0.058478 | 0.060571 | 0.11025 | 0.058117 | 0.1715 | 0.34337 | -0.060928 | -0.22367 | 61.3093 | -61.2928 | 61.4009 | 61.4189 | 0.10959 | -61.372 | -60.9831 | 61.1441 | -61.3565 | 61.4284 | 61.4259 | 0.28179 | -61.1846 | -61.5889 | 61.6031 | 61.5238 | 61.9127 | 61.534 | -61.5865 | 61.5393 | 61.7112 | 61.3069 | 61.478 | -61.7517
1767.7969 | 123.1338 | -61.3953 | 61.5601 | -0.013431 | 0.010182 | 0.018342 | -0.024975 | -0.0035489 | -0.00044864 | 0.013506 | 0.032723 | -0.00338 | -0.0079926 | 0.024258 | -0.0063049 | 0.033096 | 0.16624 | 0.055687 | 0.23069 | 0.15146 | 0.5403 | -0.058478 | 0.060571 | 0.11025 | 0.058117 | 0.17608 | 0.35252 | -0.065507 | -0.22367 | 61.3368 | -61.3294 | 61.4284 | 61.451 | 0.11417 | -61.4086 | -61.0198 | 61.1716 | -61.384 | 61.4558 | 61.4534 | 0.28179 | -61.2075 | -61.6256 | 61.6259 | 61.5467 | 61.9356 | 61.5615 | -61.6185 | 61.5713 | 61.7478 | 61.3298 | 61.5055 | -61.7837
1768.7969 | 123.175 | -61.3541 | 61.5509 | 0.0094624 | 0.0095404 | 0.017915 | -0.024762 | -0.0035489 | -0.00023504 | 0.0058755 | 0.032937 | -0.00338 | -0.0079926 | 0.024258 | -0.0063049 | 0.037675 | 0.17081 | 0.051108 | 0.23069 | 0.14688 | 0.5403 | -0.058478 | 0.055992 | 0.11025 | 0.067274 | 0.18066 | 0.3571 | -0.05635 | -0.22367 | 61.2956 | -61.3202 | 61.3917 | 61.4052 | 0.10959 | -61.404 | -61.0106 | 61.1304 | -61.3702 | 61.4101 | 61.4213 | 0.29095 | -61.1938 | -61.6073 | 61.5847 | 61.5009 | 61.8944 | 61.5249 | -61.6094 | 61.5347 | 61.7112 | 61.2977 | 61.4643 | -61.7746
1769.7969 | 123.1705 | -61.3632 | 61.5189 | 0.0018314 | 0.0097542 | 0.017915 | -0.024548 | -0.0035489 | -0.00023504 | -0.001755 | 0.032937 | -0.0035938 | -0.007779 | 0.024258 | -0.0058775 | 0.028518 | 0.17081 | 0.051108 | 0.22611 | 0.15604 | 0.53573 | -0.058478 | 0.055992 | 0.11025 | 0.048959 | 0.17608 | 0.35252 | -0.042614 | -0.23283 | 61.3047 | -61.2928 | 61.3917 | 61.4143 | 0.10959 | -61.3628 | -60.9831 | 61.1304 | -61.3428 | 61.4192 | 61.4122 | 0.28179 | -61.1663 | -61.5615 | 61.5893 | 61.5193 | 61.8989 | 61.534 | -61.5773 | 61.5393 | 61.7157 | 61.3206 | 61.4735 | -61.7517
1770.7969 | 123.2254 | -61.3403 | 61.5738 | -0.0057996 | 0.0097542 | 0.017915 | -0.024975 | -0.0037625 | -0.00066244 | 0.0058755 | 0.032723 | -0.0038074 | -0.007779 | 0.024472 | -0.0063049 | 0.037675 | 0.16166 | 0.055687 | 0.22611 | 0.15146 | 0.53573 | -0.053899 | 0.06515 | 0.10567 | 0.067274 | 0.16692 | 0.34794 | -0.038035 | -0.22367 | 61.2864 | -61.3477 | 61.378 | 61.396 | 0.10959 | -61.4223 | -61.0381 | 61.1167 | -61.4069 | 61.4055 | 61.4076 | 0.29095 | -61.2258 | -61.6118 | 61.5664 | 61.4918 | 61.8761 | 61.502 | -61.6277 | 61.5073 | 61.6883 | 61.3023 | 61.446 | -61.7975
1771.7969 | 123.1659 | -61.4044 | 61.5417 | 0.0018314 | 0.0095404 | 0.017915 | -0.024762 | -0.0039763 | -0.00044864 | -0.001755 | 0.03315 | -0.0035938 | -0.007779 | 0.024258 | -0.0063049 | 0.033096 | 0.17081 | 0.055687 | 0.23526 | 0.15604 | 0.5403 | -0.058478 | 0.055992 | 0.11025 | 0.058117 | 0.18524 | 0.35252 | -0.065507 | -0.22825 | 61.3459 | -61.3065 | 61.4375 | 61.4601 | 0.11417 | -61.3857 | -61.0014 | 61.1762 | -61.3565 | 61.4604 | 61.4625 | 0.28637 | -61.1892 | -61.6073 | 61.6397 | 61.5605 | 61.9447 | 61.5752 | -61.6002 | 61.5897 | 61.7569 | 61.3389 | 61.5147 | -61.77
1772.7969 | 123.1842 | -61.3861 | 61.5646 | -0.0057996 | 0.0093268 | 0.017915 | -0.024762 | -0.0039763 | -0.00044864 | -0.0093855 | 0.033364 | -0.0035938 | -0.0082062 | 0.024472 | -0.0063049 | 0.033096 | 0.17539 | 0.051108 | 0.22611 | 0.15604 | 0.53573 | -0.058478 | 0.055992 | 0.10567 | 0.053538 | 0.1715 | 0.34337 | -0.074664 | -0.22367 | 61.3276 | -61.3385 | 61.4192 | 61.4372 | 0.10959 | -61.4086 | -61.0289 | 61.1624 | -61.3931 | 61.4421 | 61.4396 | 0.27721 | -61.2213 | -61.6393 | 61.6122 | 61.5421 | 61.9218 | 61.5615 | -61.6231 | 61.5576 | 61.7295 | 61.3114 | 61.4918 | -61.7883
1773.7969 | 123.1796 | -61.3678 | 61.5372 | -0.0057996 | 0.0097542 | 0.017915 | -0.024548 | -0.0035489 | -0.00044864 | -0.001755 | 0.032723 | -0.0038074 | -0.0082062 | 0.024258 | -0.0063049 | 0.028518 | 0.17081 | 0.04653 | 0.23069 | 0.14688 | 0.53573 | -0.058478 | 0.060571 | 0.11025 | 0.062695 | 0.18066 | 0.34794 | -0.065507 | -0.22825 | 61.3093 | -61.3065 | 61.3963 | 61.4143 | 0.10501 | -61.3903 | -61.0014 | 61.1395 | -61.3565 | 61.4284 | 61.4305 | 0.29095 | -61.1892 | -61.6027 | 61.5985 | 61.5147 | 61.9035 | 61.5386 | -61.5956 | 61.5485 | 61.7157 | 61.3023 | 61.478 | -61.7654
1774.7969 | 123.1522 | -61.3815 | 61.5417 | -0.0057996 | 0.0095404 | 0.018342 | -0.024762 | -0.0037625 | -0.00023504 | -0.0093855 | 0.03315 | -0.00338 | -0.007779 | 0.024258 | -0.0063049 | 0.037675 | 0.17081 | 0.055687 | 0.22611 | 0.14688 | 0.53573 | -0.058478 | 0.051413 | 0.11025 | 0.058117 | 0.16692 | 0.34794 | -0.070086 | -0.23283 | 61.3231 | -61.3156 | 61.4192 | 61.4372 | 0.11417 | -61.3949 | -61.006 | 61.1487 | -61.3748 | 61.4329 | 61.4396 | 0.29095 | -61.1938 | -61.6118 | 61.6076 | 61.5284 | 61.9173 | 61.5523 | -61.6002 | 61.5485 | 61.7295 | 61.3114 | 61.4918 | -61.7746
1775.7969 | 123.2025 | -61.3632 | 61.5417 | 0.0094624 | 0.0095404 | 0.017915 | -0.024975 | -0.0041899 | -0.00066244 | -0.001755 | 0.032937 | -0.0035938 | -0.0082062 | 0.024258 | -0.0063049 | 0.033096 | 0.16624 | 0.051108 | 0.22611 | 0.15146 | 0.53115 | -0.058478 | 0.051413 | 0.11483 | 0.062695 | 0.1715 | 0.34794 | -0.070086 | -0.22367 | 61.3047 | -61.3156 | 61.3963 | 61.4143 | 0.10959 | -61.3903 | -61.0106 | 61.1395 | -61.3702 | 61.4146 | 61.4259 | 0.28637 | -61.1938 | -61.6118 | 61.5893 | 61.5147 | 61.8944 | 61.5295 | -61.6002 | 61.5347 | 61.7112 | 61.2931 | 61.478 | -61.7654
1776.7969 | 123.2071 | -61.3495 | 61.5967 | -0.0057996 | 0.0093268 | 0.017915 | -0.025189 | -0.0035489 | -0.00044864 | -0.001755 | 0.032937 | -0.00338 | -0.007779 | 0.024258 | -0.0063049 | 0.033096 | 0.16166 | 0.051108 | 0.22611 | 0.15604 | 0.53115 | -0.053899 | 0.060571 | 0.10567 | 0.058117 | 0.17608 | 0.35252 | -0.001407 | -0.2191 | 61.2956 | -61.3706 | 61.3826 | 61.4006 | 0.10501 | -61.4406 | -61.0655 | 61.1304 | -61.4206 | 61.4101 | 61.4076 | 0.27721 | -61.2442 | -61.5981 | 61.5756 | 61.5055 | 61.8806 | 61.5111 | -61.6506 | 61.5256 | 61.702 | 61.3481 | 61.4552 | -61.8158
1777.7969 | 123.1934 | -61.3586 | 61.5372 | 0.0094624 | 0.0093268 | 0.017701 | -0.024975 | -0.0035489 | -0.00044864 | -0.001755 | 0.032937 | -0.0038074 | -0.0079926 | 0.024258 | -0.0060913 | 0.042253 | 0.16624 | 0.051108 | 0.23069 | 0.16062 | 0.53573 | -0.067636 | 0.055992 | 0.10567 | 0.067274 | 0.17608 | 0.34794 | -0.05635 | -0.22825 | 61.291 | -61.3065 | 61.4009 | 61.4098 | 0.11874 | -61.3765 | -61.0014 | 61.1304 | -61.3611 | 61.4146 | 61.4259 | 0.29553 | -61.1892 | -61.5935 | 61.5893 | 61.5193 | 61.8944 | 61.5249 | -61.6048 | 61.5347 | 61.7066 | 61.3023 | 61.4643 | -61.7654
1778.7969 | 123.1796 | -61.3861 | 61.5555 | -0.0057996 | 0.0093268 | 0.017701 | -0.024548 | -0.0039763 | -0.00066244 | -0.001755 | 0.032509 | -0.00338 | -0.007779 | 0.024472 | -0.0065185 | 0.033096 | 0.17081 | 0.051108 | 0.22611 | 0.15146 | 0.53573 | -0.063057 | 0.051413 | 0.10567 | 0.058117 | 0.1715 | 0.35252 | -0.065507 | -0.2191 | 61.3231 | -61.3294 | 61.4192 | 61.4372 | 0.11417 | -61.404 | -61.0198 | 61.167 | -61.384 | 61.4375 | 61.4442 | 0.27721 | -61.203 | -61.621 | 61.6122 | 61.5376 | 61.9218 | 61.5569 | -61.6185 | 61.5576 | 61.7386 | 61.3206 | 61.4918 | -61.7746
1779.7969 | 123.2208 | -61.3678 | 61.5555 | -0.0057996 | 0.0091132 | 0.018128 | -0.024975 | -0.0041899 | -0.00044864 | -0.001755 | 0.032937 | -0.0038074 | -0.007779 | 0.024472 | -0.0063049 | 0.042253 | 0.17997 | 0.051108 | 0.23069 | 0.1652 | 0.5403 | -0.067636 | 0.060571 | 0.11483 | 0.062695 | 0.17608 | 0.34794 | -0.065507 | -0.23283 | 61.3002 | -61.3248 | 61.4101 | 61.4189 | 0.11874 | -61.3903 | -61.0152 | 61.135 | -61.3794 | 61.4284 | 61.4305 | 0.29553 | -61.2075 | -61.621 | 61.5985 | 61.533 | 61.9081 | 61.5478 | -61.6231 | 61.5439 | 61.7157 | 61.3023 | 61.4826 | -61.7883
1780.7969 | 123.1293 | -61.4044 | 61.6196 | -0.0057996 | 0.0097542 | 0.018342 | -0.024762 | -0.0041899 | -0.00087604 | 0.0058755 | 0.032723 | -0.00338 | -0.0075654 | 0.024045 | -0.0065185 | 0.033096 | 0.17081 | 0.051108 | 0.22611 | 0.16978 | 0.43957 | -0.067636 | 0.060571 | 0.11025 | 0.067274 | 0.17608 | 0.36168 | -0.060928 | -0.2191 | 61.3368 | -61.3935 | 61.4375 | 61.4555 | 0.11874 | -61.4498 | -61.18 | 61.1853 | -61.4435 | 61.465 | 61.4717 | 0.28637 | -61.2579 | -61.6805 | 61.6305 | 61.5742 | 61.844 | 61.5752 | -61.6872 | 61.5805 | 61.7661 | 61.3435 | 61.5147 | -61.8387
1781.7969 | 123.1979 | -61.3998 | 61.5463 | -0.013431 | 0.0093268 | 0.018128 | -0.024975 | -0.0035489 | -0.00023504 | -0.001755 | 0.03315 | -0.0031664 | -0.0079926 | 0.024258 | -0.0065185 | 0.037675 | 0.17081 | 0.060265 | 0.22611 | 0.14231 | 0.43957 | -0.058478 | 0.055992 | 0.11483 | 0.062695 | 0.1715 | 0.34794 | -0.047193 | -0.23283 | 61.3414 | -61.3202 | 61.4375 | 61.4601 | 0.11874 | -61.404 | -61.1068 | 61.167 | -61.3748 | 61.4558 | 61.4625 | 0.29553 | -61.1984 | -61.5935 | 61.6259 | 61.5421 | 61.8394 | 61.5707 | -61.6048 | 61.5713 | 61.7478 | 61.3526 | 61.5147 | -61.7792
1782.7969 | 123.1934 | -61.377 | 61.5692 | 0.0018314 | 0.0095404 | 0.018342 | -0.024975 | -0.0039763 | -0.00044864 | 0.0058755 | 0.032937 | -0.00338 | -0.007779 | 0.024472 | -0.0063049 | 0.037675 | 0.16166 | 0.04653 | 0.23069 | 0.15604 | 0.44415 | -0.063057 | 0.060571 | 0.10567 | 0.067274 | 0.17608 | 0.34794 | -0.019721 | -0.22367 | 61.3139 | -61.3385 | 61.4146 | 61.4235 | 0.10959 | -61.4132 | -61.1251 | 61.1533 | -61.3931 | 61.4375 | 61.4442 | 0.29095 | -61.2213 | -61.5889 | 61.6076 | 61.533 | 61.8211 | 61.5386 | -61.6323 | 61.553 | 61.7249 | 61.3572 | 61.4826 | -61.7929
1783.7969 | 123.23 | -61.3953 | 61.5509 | -0.0057996 | 0.0095404 | 0.017915 | -0.024762 | -0.0037625 | -0.00087604 | -0.0093855 | 0.032723 | -0.0035938 | -0.0079926 | 0.024258 | -0.0063049 | 0.037675 | 0.12961 | 0.060265 | 0.23069 | 0.15604 | 0.43042 | -0.063057 | 0.060571 | 0.10567 | 0.067274 | 0.17608 | 0.36168 | -0.038035 | -0.22825 | 61.3322 | -61.3202 | 61.4329 | 61.4555 | 0.12332 | -61.3949 | -61.1205 | 61.167 | -61.3748 | 61.4558 | 61.4625 | 0.29553 | -61.1892 | -61.5889 | 61.6259 | 61.5513 | 61.8257 | 61.5249 | -61.614 | 61.5713 | 61.7569 | 61.3572 | 61.5009 | -61.7792
1784.7969 | 123.2346 | -61.3953 | 61.5692 | 0.0018314 | 0.0091132 | 0.017701 | -0.024548 | -0.0041899 | -0.00044864 | 0.0058755 | 0.03315 | -0.0035938 | -0.0079926 | 0.024258 | -0.0060913 | 0.037675 | 0.11587 | 0.051108 | 0.22611 | 0.15146 | 0.44415 | -0.058478 | 0.055992 | 0.11025 | 0.058117 | 0.18524 | 0.34794 | -0.038035 | -0.22367 | 61.3368 | -61.3431 | 61.4329 | 61.4464 | 0.10959 | -61.4178 | -61.1251 | 61.1716 | -61.384 | 61.4513 | 61.4534 | 0.28179 | -61.2213 | -61.6072 | 61.6214 | 61.5467 | 61.8394 | 61.5111 | -61.6277 | 61.5805 | 61.7432 | 61.3572 | 61.5055 | -61.7929
1785.7969 | 123.1979 | -61.4044 | 61.5784 | 0.0018314 | 0.0093268 | 0.018128 | -0.024548 | -0.0041899 | -0.00044864 | -0.0093855 | 0.032509 | -0.00338 | -0.007779 | 0.024258 | -0.0060913 | 0.037675 | 0.12961 | 0.055687 | 0.22153 | 0.15146 | 0.435 | -0.063057 | 0.055992 | 0.10567 | 0.058117 | 0.18066 | 0.34794 | -0.070086 | -0.22367 | 61.3414 | -61.3568 | 61.4421 | 61.4601 | 0.11874 | -61.4269 | -61.1434 | 61.1807 | -61.3977 | 61.4604 | 61.4625 | 0.28179 | -61.2304 | -61.6485 | 61.6259 | 61.5559 | 61.8394 | 61.534 | -61.6414 | 61.5851 | 61.7524 | 61.3343 | 61.5101 | -61.802
1786.7969 | 123.1888 | -61.3907 | 61.5875 | 0.0094624 | 0.0095404 | 0.017915 | -0.024762 | -0.0039763 | -0.00087604 | 0.0058755 | 0.032937 | -0.00338 | -0.0082062 | 0.024472 | -0.0063049 | 0.037675 | 0.12961 | 0.055687 | 0.22153 | 0.15146 | 0.435 | -0.053899 | 0.060571 | 0.10567 | 0.062695 | 0.17608 | 0.3571 | -0.0243 | -0.22367 | 61.3368 | -61.366 | 61.4284 | 61.4464 | 0.10959 | -61.4361 | -61.1525 | 61.167 | -61.4114 | 61.4513 | 61.4534 | 0.28637 | -61.2304 | -61.6118 | 61.6122 | 61.5421 | 61.8257 | 61.5203 | -61.6414 | 61.5668 | 61.7478 | 61.3664 | 61.4964 | -61.8112
1787.7969 | 123.23 | -61.3907 | 61.5692 | 0.0018314 | 0.0095404 | 0.017701 | -0.024975 | -0.0035489 | -0.00044864 | -0.001755 | 0.032723 | -0.00338 | -0.0079926 | 0.024686 | -0.0063049 | 0.037675 | 0.12961 | 0.055687 | 0.23069 | 0.15604 | 0.43042 | -0.053899 | 0.060571 | 0.11483 | 0.058117 | 0.1715 | 0.34794 | -0.05635 | -0.22825 | 61.3368 | -61.3385 | 61.4284 | 61.4464 | 0.10959 | -61.4132 | -61.1388 | 61.1624 | -61.3977 | 61.4513 | 61.4488 | 0.28637 | -61.2213 | -61.6256 | 61.6214 | 61.5467 | 61.8211 | 61.5203 | -61.6231 | 61.5622 | 61.7386 | 61.3343 | 61.5055 | -61.7975
1788.7969 | 123.2574 | -61.3998 | 61.6058 | -0.0057996 | 0.0093268 | 0.017915 | -0.024548 | -0.0039763 | -0.00087604 | 0.0058755 | 0.032723 | -0.0035938 | -0.007779 | 0.024045 | -0.0063049 | 0.037675 | 0.12503 | 0.051108 | 0.23069 | 0.14231 | 0.435 | -0.044742 | 0.055992 | 0.11025 | 0.062695 | 0.17608 | 0.34794 | -0.070086 | -0.22825 | 61.3551 | -61.3751 | 61.4375 | 61.4509 | 0.09585 | -61.4635 | -61.1708 | 61.1716 | -61.4298 | 61.4558 | 61.4625 | 0.29095 | -61.2579 | -61.6759 | 61.6305 | 61.5421 | 61.8348 | 61.5249 | -61.6506 | 61.5759 | 61.7478 | 61.3298 | 61.5101 | -61.8341
1789.7969 | 123.2254 | -61.4136 | 61.5875 | -0.013431 | 0.0095404 | 0.017487 | -0.024975 | -0.0041899 | -0.00044864 | 0.0058755 | 0.032509 | -0.00338 | -0.0079926 | 0.024258 | -0.0060913 | 0.042253 | 0.12503 | 0.055687 | 0.22153 | 0.15146 | 0.435 | -0.058478 | 0.051413 | 0.11025 | 0.058117 | 0.17608 | 0.35252 | -0.05635 | -0.22367 | 61.3551 | -61.366 | 61.4558 | 61.4693 | 0.11417 | -61.4361 | -61.1525 | 61.1899 | -61.4114 | 61.465 | 61.4717 | 0.28179 | -61.235 | -61.6439 | 61.6351 | 61.565 | 61.8486 | 61.5386 | -61.646 | 61.5897 | 61.7661 | 61.3572 | 61.5238 | -61.8112
1790.7969 | 123.2666 | -61.3815 | 61.5829 | 0.0094624 | 0.0091132 | 0.017915 | -0.025189 | -0.0041899 | -0.00066244 | -0.001755 | 0.032937 | -0.00338 | -0.0082062 | 0.024472 | -0.0060913 | 0.042253 | 0.12961 | 0.055687 | 0.22611 | 0.15146 | 0.44415 | -0.063057 | 0.055992 | 0.10109 | 0.058117 | 0.18066 | 0.36168 | -0.060928 | -0.21452 | 61.3185 | -61.3568 | 61.4238 | 61.4372 | 0.11874 | -61.4315 | -61.1388 | 61.167 | -61.4023 | 61.4375 | 61.4396 | 0.27263 | -61.2213 | -61.6439 | 61.6076 | 61.533 | 61.8257 | 61.5111 | -61.646 | 61.5622 | 61.7432 | 61.3206 | 61.4826 | -61.7975
1791.7969 | 123.2941 | -61.377 | 61.5784 | -0.013431 | 0.0088994 | 0.017701 | -0.024762 | -0.0039763 | -0.00044864 | -0.001755 | 0.032723 | -0.0035938 | -0.0082062 | 0.024258 | -0.0065185 | 0.033096 | 0.12961 | 0.060265 | 0.23069 | 0.15146 | 0.42584 | -0.049321 | 0.051413 | 0.10567 | 0.067274 | 0.17608 | 0.34794 | -0.05635 | -0.22825 | 61.3276 | -61.3477 | 61.41 | 61.4372 | 0.10959 | -61.4269 | -61.1525 | 61.1487 | -61.4023 | 61.4284 | 61.4442 | 0.29553 | -61.2304 | -61.6347 | 61.6076 | 61.5284 | 61.8028 | 61.5066 | -61.6277 | 61.553 | 61.7249 | 61.3206 | 61.4826 | -61.8066
1792.7969 | 123.2574 | -61.3861 | 61.5967 | 0.0094624 | 0.0091132 | 0.018128 | -0.024975 | -0.0039763 | -0.00023504 | 0.0058755 | 0.032937 | -0.0038074 | -0.0079926 | 0.024472 | -0.0060913 | 0.042253 | 0.12045 | 0.055687 | 0.22611 | 0.14688 | 0.435 | -0.040163 | 0.055992 | 0.11025 | 0.062695 | 0.17608 | 0.34794 | -0.028878 | -0.22367 | 61.3459 | -61.3706 | 61.4284 | 61.4418 | 0.09585 | -61.4498 | -61.1617 | 61.1624 | -61.4206 | 61.4421 | 61.4488 | 0.28637 | -61.2487 | -61.6256 | 61.6122 | 61.533 | 61.8211 | 61.5066 | -61.6368 | 61.5622 | 61.7341 | 61.3572 | 61.4964 | -61.8204
1793.7969 | 123.1842 | -61.409 | 61.6013 | -0.013431 | 0.0093268 | 0.018342 | -0.024762 | -0.0041899 | -0.00066244 | 0.0058755 | 0.03315 | -0.0038074 | -0.0079926 | 0.024258 | -0.0063049 | 0.042253 | 0.12961 | 0.060265 | 0.23069 | 0.14688 | 0.44415 | -0.053899 | 0.060571 | 0.10567 | 0.067274 | 0.18066 | 0.35252 | -0.065507 | -0.2191 | 61.3551 | -61.3706 | 61.4513 | 61.4693 | 0.11416 | -61.4544 | -61.1571 | 61.1899 | -61.4206 | 61.4696 | 61.4763 | 0.28637 | -61.2487 | -61.6668 | 61.6397 | 61.5559 | 61.8532 | 61.5386 | -61.6552 | 61.5897 | 61.7615 | 61.3435 | 61.5147 | -61.8204
1794.7969 | 123.2391 | -61.3632 | 61.5921 | -0.0057996 | 0.0097542 | 0.017915 | -0.025189 | -0.0037625 | -0.00044864 | -0.001755 | 0.032723 | -0.0031664 | -0.0079926 | 0.024258 | -0.0060913 | 0.037675 | 0.12503 | 0.051108 | 0.21695 | 0.14688 | 0.43957 | -0.053899 | 0.055992 | 0.11483 | 0.062695 | 0.18981 | 0.34337 | -0.070086 | -0.22367 | 61.3093 | -61.3752 | 61.4009 | 61.4143 | 0.10501 | -61.4452 | -61.1525 | 61.1395 | -61.4023 | 61.4192 | 61.4259 | 0.28637 | -61.2487 | -61.6622 | 61.5802 | 61.5101 | 61.8028 | 61.4882 | -61.646 | 61.553 | 61.7066 | 61.2931 | 61.478 | -61.8158
1795.7969 | 123.1522 | -61.4273 | 61.5967 | -0.0057996 | 0.0093268 | 0.018128 | -0.024975 | -0.0039763 | -0.00066244 | -0.0093855 | 0.032937 | -0.0035938 | -0.0084198 | 0.024686 | -0.0063049 | 0.042253 | 0.12961 | 0.051108 | 0.22153 | 0.15604 | 0.42584 | -0.058478 | 0.060571 | 0.11025 | 0.062695 | 0.18524 | 0.34337 | -0.019721 | -0.2191 | 61.3688 | -61.3752 | 61.4696 | 61.4784 | 0.10959 | -61.4406 | -61.1708 | 61.2082 | -61.4114 | 61.4879 | 61.49 | 0.28179 | -61.2533 | -61.6164 | 61.6488 | 61.5833 | 61.8531 | 61.5569 | -61.6552 | 61.6125 | 61.7707 | 61.4076 | 61.5376 | -61.8158
1796.7969 | 123.2437 | -61.3861 | 61.615 | 0.0018314 | 0.0093268 | 0.017701 | -0.024975 | -0.0039763 | -0.00044864 | 0.0058755 | 0.032723 | -0.00338 | -0.007779 | 0.024686 | -0.0063049 | 0.042253 | 0.11587 | 0.055687 | 0.22153 | 0.15604 | 0.44873 | -0.053899 | 0.046835 | 0.11483 | 0.062695 | 0.17608 | 0.34794 | -0.065507 | -0.22367 | 61.3322 | -61.3935 | 61.4284 | 61.4418 | 0.10959 | -61.4589 | -61.1663 | 61.1624 | -61.4389 | 61.4329 | 61.4488 | 0.28637 | -61.267 | -61.6805 | 61.6076 | 61.5421 | 61.8348 | 61.502 | -61.6689 | 61.5622 | 61.7341 | 61.3206 | 61.5009 | -61.8387
1797.7969 | 123.3078 | -61.4136 | 61.5829 | 0.017093 | 0.0088994 | 0.017915 | -0.024975 | -0.0037625 | -0.00066244 | 0.0058755 | 0.032723 | -0.0035938 | -0.0079926 | 0.024258 | -0.0063049 | 0.042253 | 0.13419 | 0.055687 | 0.22153 | 0.15146 | 0.42584 | -0.058478 | 0.060571 | 0.11025 | 0.062695 | 0.17608 | 0.35252 | -0.051771 | -0.22825 | 61.3551 | -61.3614 | 61.4558 | 61.4693 | 0.11417 | -61.4315 | -61.1571 | 61.1853 | -61.4069 | 61.4741 | 61.4763 | 0.29095 | -61.2304 | -61.6347 | 61.6351 | 61.565 | 61.8394 | 61.5478 | -61.6414 | 61.5897 | 61.7661 | 61.3618 | 61.5238 | -61.8112
1798.7969 | 123.2666 | -61.3861 | 61.6104 | 0.0018314 | 0.0093268 | 0.017915 | -0.024762 | -0.0037625 | -0.00044864 | 0.013506 | 0.03315 | -0.0035938 | -0.0079926 | 0.024686 | -0.0067321 | 0.042253 | 0.12503 | 0.055687 | 0.23526 | 0.14688 | 0.42584 | -0.058478 | 0.060571 | 0.11025 | 0.062695 | 0.17608 | 0.35252 | -0.042614 | -0.22825 | 61.3276 | -61.3751 | 61.4284 | 61.4418 | 0.11417 | -61.4635 | -61.1846 | 61.1579 | -61.4343 | 61.4467 | 61.4488 | 0.29095 | -61.2579 | -61.653 | 61.6214 | 61.533 | 61.8119 | 61.5111 | -61.6689 | 61.5622 | 61.7386 | 61.3435 | 61.4964 | -61.8387
1799.7969 | 123.2391 | -61.4136 | 61.5967 | 0.0094624 | 0.0088994 | 0.017701 | -0.024975 | -0.0041899 | -0.00044864 | -0.017016 | 0.032723 | -0.00338 | -0.0082062 | 0.024686 | -0.0060913 | 0.042253 | 0.12961 | 0.060265 | 0.22611 | 0.14688 | 0.435 | -0.053899 | 0.051413 | 0.11025 | 0.062695 | 0.18066 | 0.34794 | -0.060928 | -0.22367 | 61.3597 | -61.3706 | 61.4558 | 61.4738 | 0.11416 | -61.4498 | -61.1617 | 61.1899 | -61.416 | 61.465 | 61.4763 | 0.28637 | -61.2487 | -61.6576 | 61.6397 | 61.5605 | 61.8486 | 61.5432 | -61.6506 | 61.5942 | 61.7615 | 61.3526 | 61.5238 | -61.8204
1800.7969 | 123.1888 | -61.4227 | 61.6287 | 0.0018314 | 0.0093268 | 0.017915 | -0.024975 | -0.0041899 | -0.00066244 | -0.001755 | 0.032509 | -0.00338 | -0.0082062 | 0.024472 | -0.0063049 | 0.042253 | 0.12961 | 0.055687 | 0.22153 | 0.15146 | 0.42126 | -0.063057 | 0.060571 | 0.1194 | 0.062695 | 0.17608 | 0.35252 | -0.038035 | -0.2191 | 61.3597 | -61.4072 | 61.465 | 61.4784 | 0.11874 | -61.4773 | -61.2075 | 61.2036 | -61.4526 | 61.4833 | 61.4854 | 0.28179 | -61.2762 | -61.6668 | 61.6443 | 61.5742 | 61.844 | 61.5523 | -61.6918 | 61.5988 | 61.7753 | 61.3847 | 61.5421 | -61.8478
1801.7969 | 123.2529 | -61.3907 | 61.5921 | 0.0018314 | 0.0088994 | 0.017915 | -0.024762 | -0.0037625 | -0.00044864 | -0.001755 | 0.032509 | -0.00338 | -0.0082062 | 0.024258 | -0.0063049 | 0.037675 | 0.12045 | 0.055687 | 0.21695 | 0.14688 | 0.43957 | -0.063057 | 0.055992 | 0.10567 | 0.062695 | 0.18524 | 0.35252 | -0.051771 | -0.22367 | 61.3276 | -61.3752 | 61.4284 | 61.4464 | 0.11874 | -61.4452 | -61.1525 | 61.167 | -61.4069 | 61.4467 | 61.4534 | 0.28637 | -61.2396 | -61.6439 | 61.6076 | 61.5376 | 61.8303 | 61.5111 | -61.6552 | 61.5759 | 61.7432 | 61.3389 | 61.4964 | -61.8158
1802.7969 | 123.2712 | -61.3953 | 61.6104 | -0.0057996 | 0.0093268 | 0.018342 | -0.024762 | -0.0039763 | -0.00044864 | 0.0058755 | 0.032937 | -0.00338 | -0.0079926 | 0.024686 | -0.0067321 | 0.042253 | 0.12503 | 0.060265 | 0.22611 | 0.15604 | 0.435 | -0.053899 | 0.060571 | 0.10567 | 0.067274 | 0.18066 | 0.3571 | -0.042614 | -0.22367 | 61.3414 | -61.3843 | 61.4375 | 61.4555 | 0.11416 | -61.4544 | -61.1754 | 61.1716 | -61.4298 | 61.4558 | 61.4625 | 0.29095 | -61.2533 | -61.653 | 61.6214 | 61.5513 | 61.8303 | 61.5203 | -61.6643 | 61.5759 | 61.7524 | 61.3526 | 61.5009 | -61.8341
1803.7969 | 123.3627 | -61.4136 | 61.5967 | 0.0018314 | 0.0091132 | 0.017701 | -0.025189 | -0.0039763 | -0.00087604 | -0.0093855 | 0.032509 | -0.0029528 | -0.0079926 | 0.024472 | -0.0065185 | 0.046831 | 0.12503 | 0.04653 | 0.22153 | 0.15146 | 0.43042 | -0.053899 | 0.051413 | 0.10567 | 0.067274 | 0.1715 | 0.35252 | -0.05635 | -0.2191 | 61.3597 | -61.3752 | 61.4604 | 61.4601 | 0.10043 | -61.4452 | -61.1663 | 61.1945 | -61.4252 | 61.465 | 61.4808 | 0.28637 | -61.2442 | -61.653 | 61.6351 | 61.565 | 61.844 | 61.5386 | -61.6506 | 61.5851 | 61.7661 | 61.3572 | 61.5192 | -61.8158
1804.7969 | 123.175 | -61.409 | 61.6516 | -0.013431 | 0.0093268 | 0.017915 | -0.024975 | -0.0041899 | -0.00044864 | 0.0058755 | 0.032937 | -0.0038074 | -0.0082062 | 0.024258 | -0.0063049 | 0.037675 | 0.12961 | 0.060265 | 0.23069 | 0.15604 | 0.435 | -0.058478 | 0.060571 | 0.11025 | 0.067274 | 0.18524 | 0.34794 | -0.010564 | -0.22367 | 61.3505 | -61.4209 | 61.4467 | 61.4693 | 0.11874 | -61.4956 | -61.2166 | 61.1853 | -61.4664 | 61.4696 | 61.4763 | 0.29095 | -61.3037 | -61.6622 | 61.6397 | 61.565 | 61.844 | 61.5386 | -61.7101 | 61.5942 | 61.7569 | 61.3984 | 61.5192 | -61.8753
1805.7969 | 123.2391 | -61.4227 | 61.6013 | 0.0018314 | 0.0093268 | 0.018128 | -0.024762 | -0.0039763 | -0.00066244 | 0.0058755 | 0.032723 | -0.00338 | -0.0082062 | 0.024472 | -0.0063049 | 0.042253 | 0.12961 | 0.051108 | 0.22153 | 0.14688 | 0.43042 | -0.049321 | 0.06515 | 0.11483 | 0.058117 | 0.17608 | 0.3571 | -0.065507 | -0.23283 | 61.3734 | -61.3797 | 61.465 | 61.4738 | 0.10043 | -61.4544 | -61.1708 | 61.1899 | -61.4252 | 61.4879 | 61.4808 | 0.29095 | -61.2442 | -61.6668 | 61.6443 | 61.5696 | 61.8531 | 61.5523 | -61.6506 | 61.5988 | 61.7798 | 61.3572 | 61.5376 | -61.8341
1806.7969 | 123.2758 | -61.4136 | 61.6196 | -0.013431 | 0.0093268 | 0.017701 | -0.025189 | -0.0039763 | -0.00087604 | -0.001755 | 0.032723 | -0.00338 | -0.0082062 | 0.024686 | -0.0065185 | 0.042253 | 0.12045 | 0.055687 | 0.22611 | 0.15146 | 0.43042 | -0.053899 | 0.055992 | 0.1194 | 0.058117 | 0.17608 | 0.34337 | -0.019721 | -0.2191 | 61.3597 | -61.3935 | 61.4558 | 61.4693 | 0.10959 | -61.4681 | -61.1891 | 61.1945 | -61.4435 | 61.4696 | 61.4717 | 0.27721 | -61.2762 | -61.6393 | 61.6397 | 61.565 | 61.844 | 61.534 | -61.6735 | 61.5897 | 61.7569 | 61.3939 | 61.533 | -61.8387
1807.7969 | 123.2574 | -61.4136 | 61.5967 | 0.0094624 | 0.0091132 | 0.017915 | -0.025189 | -0.0039763 | -0.00066244 | -0.0093855 | 0.032723 | -0.0038074 | -0.0084198 | 0.024686 | -0.0063049 | 0.042253 | 0.12961 | 0.055687 | 0.22611 | 0.15146 | 0.435 | -0.040163 | 0.051413 | 0.11483 | 0.062695 | 0.1715 | 0.34794 | -0.065507 | -0.2191 | 61.3734 | -61.3706 | 61.4558 | 61.4693 | 0.09585 | -61.4452 | -61.1617 | 61.1945 | -61.4252 | 61.465 | 61.4763 | 0.28179 | -61.2487 | -61.6622 | 61.6397 | 61.565 | 61.8486 | 61.5432 | -61.6368 | 61.5851 | 61.7615 | 61.3481 | 61.5284 | -61.8158
1808.7969 | 123.1613 | -61.4227 | 61.6241 | 0.0094624 | 0.0093268 | 0.017701 | -0.024548 | -0.0041899 | -0.00066244 | 0.013506 | 0.032723 | -0.0035938 | -0.0082062 | 0.024472 | -0.0063049 | 0.042253 | 0.12961 | 0.060265 | 0.23069 | 0.14688 | 0.42584 | -0.035584 | 0.060571 | 0.1194 | 0.062695 | 0.1715 | 0.35252 | -0.05635 | -0.21452 | 61.3871 | -61.3935 | 61.465 | 61.483 | 0.095849 | -61.4773 | -61.1983 | 61.2082 | -61.4526 | 61.4833 | 61.4854 | 0.27721 | -61.2716 | -61.6805 | 61.6534 | 61.5696 | 61.8486 | 61.5523 | -61.6597 | 61.5942 | 61.7753 | 61.3664 | 61.5421 | -61.8387
1809.7969 | 123.2803 | -61.3907 | 61.6013 | 0.0018314 | 0.0091132 | 0.017487 | -0.024762 | -0.0037625 | -0.00044864 | -0.001755 | 0.032723 | -0.00338 | -0.0082062 | 0.024899 | -0.0065185 | 0.046831 | 0.12961 | 0.051108 | 0.21237 | 0.14688 | 0.44415 | -0.044742 | 0.060571 | 0.10567 | 0.053538 | 0.18066 | 0.34337 | -0.051771 | -0.2191 | 61.3459 | -61.3889 | 61.4375 | 61.4418 | 0.09585 | -61.4544 | -61.1571 | 61.1716 | -61.4206 | 61.4513 | 61.4442 | 0.27263 | -61.2579 | -61.653 | 61.6031 | 61.5376 | 61.8348 | 61.5203 | -61.646 | 61.5713 | 61.7341 | 61.3389 | 61.4964 | -61.8204
1810.7969 | 123.143 | -61.4319 | 61.6562 | 0.0094624 | 0.0091132 | 0.017701 | -0.024975 | -0.0041899 | -0.00066244 | -0.001755 | 0.03315 | -0.00338 | -0.0082062 | 0.024899 | -0.0067321 | 0.037675 | 0.13419 | 0.055687 | 0.23526 | 0.15604 | 0.43957 | -0.040163 | 0.055992 | 0.11483 | 0.067274 | 0.17608 | 0.34794 | -0.070086 | -0.22367 | 61.3917 | -61.4209 | 61.4696 | 61.4876 | 0.09585 | -61.5001 | -61.2166 | 61.2082 | -61.4801 | 61.4879 | 61.4992 | 0.29095 | -61.3082 | -61.7263 | 61.6671 | 61.5879 | 61.8715 | 61.5661 | -61.6964 | 61.608 | 61.7798 | 61.3618 | 61.5467 | -61.8799
1811.7969 | 123.2895 | -61.4365 | 61.5829 | -0.0057996 | 0.0088994 | 0.017701 | -0.024975 | -0.0044035 | -0.00023504 | -0.001755 | 0.032509 | -0.0038074 | -0.0082062 | 0.024472 | -0.0063049 | 0.037675 | 0.12503 | 0.060265 | 0.23069 | 0.14688 | 0.435 | -0.053899 | 0.051413 | 0.1194 | 0.067274 | 0.17608 | 0.3571 | -0.028878 | -0.22367 | 61.3826 | -61.3523 | 61.4741 | 61.4967 | 0.11416 | -61.4361 | -61.1479 | 61.2128 | -61.4069 | 61.4879 | 61.5037 | 0.29095 | -61.2258 | -61.6118 | 61.6671 | 61.5833 | 61.8715 | 61.5615 | -61.6368 | 61.6125 | 61.7936 | 61.4076 | 61.5559 | -61.8066
1812.7969 | 123.2986 | -61.3907 | 61.5967 | -0.013431 | 0.0088994 | 0.017915 | -0.024975 | -0.0041899 | -0.00066244 | 0.013506 | 0.032937 | -0.0038074 | -0.0082062 | 0.024899 | -0.0067321 | 0.037675 | 0.12961 | 0.055687 | 0.22153 | 0.14688 | 0.43042 | -0.044742 | 0.055992 | 0.11483 | 0.062695 | 0.18066 | 0.34337 | -0.047193 | -0.2191 | 61.3459 | -61.3752 | 61.4284 | 61.4464 | 0.10043 | -61.4498 | -61.1663 | 61.1716 | -61.416 | 61.4467 | 61.4534 | 0.28179 | -61.2533 | -61.6439 | 61.6122 | 61.5376 | 61.8211 | 61.5203 | -61.6414 | 61.5713 | 61.7341 | 61.3435 | 61.5055 | -61.8158
1813.7969 | 123.262 | -61.4136 | 61.6058 | 0.0018314 | 0.0091132 | 0.017701 | -0.024975 | -0.0039763 | -0.00066244 | -0.001755 | 0.032937 | -0.0038074 | -0.0082062 | 0.024686 | -0.0063049 | 0.042253 | 0.12503 | 0.060265 | 0.22153 | 0.14688 | 0.435 | -0.044742 | 0.060571 | 0.1194 | 0.067274 | 0.18066 | 0.35252 | -0.0243 | -0.21452 | 61.3688 | -61.3843 | 61.4558 | 61.4738 | 0.10501 | -61.459 | -61.1708 | 61.1991 | -61.4252 | 61.4741 | 61.4808 | 0.28179 | -61.2533 | -61.6301 | 61.6351 | 61.5605 | 61.8486 | 61.5386 | -61.6506 | 61.5942 | 61.7661 | 61.3893 | 61.533 | -61.8204
1814.7969 | 123.1888 | -61.4365 | 61.6425 | -0.0057996 | 0.0088994 | 0.017915 | -0.025189 | -0.0039763 | -0.0010896 | -0.001755 | 0.032509 | -0.00338 | -0.0082062 | 0.024472 | -0.0065185 | 0.046831 | 0.13419 | 0.060265 | 0.23069 | 0.15604 | 0.435 | -0.044742 | 0.060571 | 0.11483 | 0.067274 | 0.18066 | 0.34794 | -0.028878 | -0.21452 | 61.3917 | -61.4118 | 61.4833 | 61.4967 | 0.10501 | -61.4864 | -61.2075 | 61.2219 | -61.4618 | 61.497 | 61.5037 | 0.28179 | -61.2945 | -61.6713 | 61.6671 | 61.5925 | 61.8715 | 61.5706 | -61.6872 | 61.6171 | 61.7844 | 61.4076 | 61.5513 | -61.857
1815.7969 | 123.3215 | -61.3998 | 61.6196 | -0.013431 | 0.0091132 | 0.018128 | -0.024548 | -0.0037625 | -0.00087604 | 0.0058755 | 0.032723 | -0.00338 | -0.0082062 | 0.024899 | -0.0065185 | 0.042253 | 0.12961 | 0.055687 | 0.23069 | 0.15146 | 0.435 | -0.035584 | 0.060571 | 0.11025 | 0.067274 | 0.18066 | 0.35252 | -0.070086 | -0.22367 | 61.3643 | -61.3889 | 61.4421 | 61.4555 | 0.091271 | -61.4681 | -61.1846 | 61.1762 | -61.4389 | 61.4604 | 61.4671 | 0.29095 | -61.267 | -61.6897 | 61.6305 | 61.5513 | 61.8348 | 61.5294 | -61.6552 | 61.5805 | 61.7524 | 61.3298 | 61.5101 | -61.8432
1816.7969 | 123.1705 | -61.4456 | 61.6425 | -0.0057996 | 0.0091132 | 0.017915 | -0.024975 | -0.0039763 | -0.00066244 | -0.001755 | 0.032937 | -0.00338 | -0.0079926 | 0.024686 | -0.0063049 | 0.042253 | 0.12961 | 0.060265 | 0.22611 | 0.15604 | 0.43042 | -0.044742 | 0.055992 | 0.11483 | 0.062695 | 0.17608 | 0.35252 | -0.051771 | -0.2191 | 61.4009 | -61.4164 | 61.4879 | 61.5059 | 0.10501 | -61.4864 | -61.212 | 61.2265 | -61.4664 | 61.5016 | 61.5083 | 0.28179 | -61.2899 | -61.6942 | 61.6717 | 61.6017 | 61.876 | 61.5752 | -61.6872 | 61.6217 | 61.7981 | 61.3938 | 61.5604 | -61.8616
1817.7969 | 123.3307 | -61.4182 | 61.6104 | -0.021062 | 0.0091132 | 0.017701 | -0.024975 | -0.0039763 | -0.00066244 | -0.001755 | 0.032509 | -0.0038074 | -0.0079926 | 0.024899 | -0.0063049 | 0.037675 | 0.12045 | 0.055687 | 0.22153 | 0.15146 | 0.43042 | -0.049321 | 0.051413 | 0.11483 | 0.067274 | 0.18066 | 0.35252 | -0.070086 | -0.2191 | 61.3688 | -61.3889 | 61.4558 | 61.4738 | 0.10501 | -61.459 | -61.18 | 61.1991 | -61.4298 | 61.4696 | 61.4854 | 0.28637 | -61.2579 | -61.6805 | 61.6397 | 61.5696 | 61.8486 | 61.5386 | -61.6597 | 61.5988 | 61.7707 | 61.3481 | 61.533 | -61.8295
1818.7969 | 123.2254 | -61.4502 | 61.6516 | 0.0018314 | 0.0093268 | 0.017915 | -0.025189 | -0.0037625 | -0.00066244 | 0.0058755 | 0.032723 | -0.0031664 | -0.0079926 | 0.024899 | -0.0065185 | 0.042253 | 0.12961 | 0.060265 | 0.22153 | 0.15604 | 0.435 | -0.049321 | 0.060571 | 0.11483 | 0.062695 | 0.18066 | 0.35252 | 0.021486 | -0.23283 | 61.4009 | -61.4301 | 61.4924 | 61.5105 | 0.10959 | -61.4956 | -61.2166 | 61.2174 | -61.471 | 61.5108 | 61.5129 | 0.29553 | -61.2991 | -61.6301 | 61.6717 | 61.6062 | 61.8852 | 61.5798 | -61.7009 | 61.6309 | 61.8027 | 61.4717 | 61.565 | -61.8844
1819.7969 | 123.2941 | -61.4136 | 61.615 | -0.013431 | 0.0095404 | 0.018128 | -0.024975 | -0.0041899 | -0.00044864 | -0.001755 | 0.032509 | -0.0035938 | -0.0079926 | 0.024899 | -0.0065185 | 0.037675 | 0.12961 | 0.064843 | 0.22611 | 0.15146 | 0.43042 | -0.049321 | 0.051413 | 0.11025 | 0.062695 | 0.18066 | 0.35252 | -0.060928 | -0.21452 | 61.3643 | -61.3889 | 61.4512 | 61.4784 | 0.11416 | -61.4635 | -61.1846 | 61.1991 | -61.4343 | 61.465 | 61.4763 | 0.27721 | -61.2625 | -61.6759 | 61.6397 | 61.565 | 61.844 | 61.5432 | -61.6643 | 61.5942 | 61.7661 | 61.3526 | 61.5238 | -61.8295
1820.7969 | 123.1842 | -61.441 | 61.615 | -0.0057996 | 0.0088994 | 0.017701 | -0.024975 | -0.0041899 | -0.00066244 | -0.001755 | 0.032937 | -0.0035938 | -0.0082062 | 0.024686 | -0.0065185 | 0.046831 | 0.12503 | 0.055687 | 0.22611 | 0.14688 | 0.42584 | -0.044742 | 0.055992 | 0.11483 | 0.067274 | 0.17608 | 0.35252 | -0.001407 | -0.22367 | 61.3963 | -61.3889 | 61.4879 | 61.4967 | 0.10043 | -61.4681 | -61.1892 | 61.2174 | -61.4389 | 61.497 | 61.5083 | 0.29095 | -61.2625 | -61.6164 | 61.6671 | 61.5879 | 61.8669 | 61.5661 | -61.6597 | 61.6171 | 61.7936 | 61.4396 | 61.5559 | -61.8387
1821.7969 | 123.3078 | -61.3998 | 61.6241 | -0.0057996 | 0.0091132 | 0.017701 | -0.024975 | -0.0039763 | -0.00087604 | -0.001755 | 0.03315 | -0.0035938 | -0.0079926 | 0.024258 | -0.0065185 | 0.042253 | 0.13419 | 0.060265 | 0.23526 | 0.15604 | 0.435 | -0.044742 | 0.055992 | 0.11483 | 0.062695 | 0.1715 | 0.35252 | -0.038035 | -0.22367 | 61.3551 | -61.3889 | 61.4421 | 61.4601 | 0.10501 | -61.4681 | -61.1891 | 61.1762 | -61.4526 | 61.4558 | 61.4625 | 0.28637 | -61.2716 | -61.6622 | 61.6351 | 61.5559 | 61.8348 | 61.534 | -61.6689 | 61.5713 | 61.7524 | 61.3618 | 61.5147 | -61.8478
1822.7969 | 123.2208 | -61.4456 | 61.6562 | -0.0057996 | 0.0088994 | 0.017915 | -0.024762 | -0.0037625 | -0.00066244 | -0.001755 | 0.032723 | -0.00338 | -0.0084198 | 0.024472 | -0.0063049 | 0.046831 | 0.12961 | 0.069421 | 0.22611 | 0.15146 | 0.43957 | -0.053899 | 0.060571 | 0.1194 | 0.058117 | 0.18524 | 0.34794 | -0.015142 | -0.22367 | 61.3917 | -61.4301 | 61.4924 | 61.515 | 0.12332 | -61.5047 | -61.2166 | 61.2219 | -61.471 | 61.5062 | 61.5037 | 0.28179 | -61.3082 | -61.6713 | 61.6717 | 61.5971 | 61.8852 | 61.5752 | -61.7101 | 61.6309 | 61.7936 | 61.4305 | 61.565 | -61.8799
1823.7969 | 123.2162 | -61.4594 | 61.6516 | 0.0018314 | 0.0091132 | 0.017701 | -0.024975 | -0.0044035 | -0.00066244 | 0.0058755 | 0.032937 | -0.00338 | -0.007779 | 0.024686 | -0.0063049 | 0.046831 | 0.13419 | 0.060265 | 0.22611 | 0.16062 | 0.43957 | -0.049321 | 0.060571 | 0.11483 | 0.062695 | 0.17608 | 0.34794 | -0.05635 | -0.22367 | 61.41 | -61.4255 | 61.5062 | 61.5196 | 0.10959 | -61.491 | -61.212 | 61.2357 | -61.4755 | 61.5199 | 61.522 | 0.28637 | -61.3037 | -61.708 | 61.6855 | 61.62 | 61.8989 | 61.5935 | -61.7009 | 61.6354 | 61.8073 | 61.403 | 61.5742 | -61.8753
1824.7969 | 123.1659 | -61.4594 | 61.6699 | -0.0057996 | 0.0093268 | 0.017701 | -0.024975 | -0.0041899 | -0.00066244 | 0.0058755 | 0.032723 | -0.0035938 | -0.0079926 | 0.024472 | -0.0065185 | 0.046831 | 0.13876 | 0.055687 | 0.22153 | 0.14688 | 0.42584 | -0.040163 | 0.055992 | 0.1194 | 0.062695 | 0.18066 | 0.34337 | -0.042614 | -0.22367 | 61.4192 | -61.4484 | 61.5062 | 61.515 | 0.09585 | -61.523 | -61.2441 | 61.2357 | -61.4893 | 61.5153 | 61.522 | 0.28637 | -61.3266 | -61.7125 | 61.6809 | 61.6062 | 61.8852 | 61.5981 | -61.7101 | 61.64 | 61.8027 | 61.4167 | 61.5788 | -61.8936
1825.7969 | 123.1796 | -61.4456 | 61.6562 | -0.0057996 | 0.0091132 | 0.017701 | -0.024762 | -0.0041899 | -0.00066244 | 0.013506 | 0.03315 | -0.0035938 | -0.0082062 | 0.024686 | -0.0065185 | 0.046831 | 0.12503 | 0.064843 | 0.23069 | 0.15146 | 0.435 | -0.049321 | 0.060571 | 0.1194 | 0.062695 | 0.17608 | 0.35252 | -0.065507 | -0.22367 | 61.3963 | -61.4255 | 61.4924 | 61.5105 | 0.11416 | -61.5047 | -61.2212 | 61.2219 | -61.4801 | 61.5062 | 61.5083 | 0.28637 | -61.3037 | -61.7217 | 61.6763 | 61.5971 | 61.8806 | 61.5706 | -61.7055 | 61.6217 | 61.7981 | 61.3801 | 61.565 | -61.8799
1826.7969 | 123.1613 | -61.4594 | 61.6653 | -0.0057996 | 0.0088994 | 0.018128 | -0.024548 | -0.0041899 | -0.00066244 | -0.001755 | 0.032723 | -0.0031664 | -0.0079926 | 0.024899 | -0.0063049 | 0.05141 | 0.13419 | 0.064843 | 0.23526 | 0.064464 | 0.44873 | 0.10636 | 0.055992 | 0.12398 | 0.058117 | 0.1715 | 0.34794 | -0.14334 | -0.2191 | 61.5657 | -61.4301 | 61.5108 | 61.5242 | -0.04152 | -61.6009 | -61.2166 | 61.2403 | -61.4938 | 61.5153 | 61.5175 | 0.27721 | -61.3174 | -61.8087 | 61.6946 | 61.5238 | 61.9081 | 61.5935 | -61.559 | 61.6308 | 61.8073 | 61.316 | 61.5833 | -61.8844
1827.7969 | 123.317 | -61.4319 | 61.6287 | 0.0018314 | 0.0091132 | 0.017915 | -0.024762 | -0.0041899 | -0.00066244 | 0.0058755 | 0.032723 | -0.0035938 | -0.0084198 | 0.024899 | -0.0065185 | 0.046831 | 0.12961 | 0.055687 | 0.22611 | 0.023254 | 0.35716 | 0.14757 | 0.060571 | 0.11483 | 0.067274 | 0.17608 | 0.35252 | -0.17081 | -0.2191 | 61.5795 | -61.4026 | 61.4787 | 61.4876 | -0.091886 | -61.6055 | -61.2716 | 61.2128 | -61.4526 | 61.4925 | 61.4992 | 0.28637 | -61.2762 | -61.7995 | 61.658 | 61.4551 | 61.789 | 61.5615 | -61.4811 | 61.608 | 61.7844 | 61.2611 | 61.5467 | -61.8478
1828.7969 | 123.2117 | -61.4548 | 61.6425 | -0.0057996 | 0.0091132 | 0.017915 | -0.025189 | -0.0041899 | -0.00066244 | 0.0058755 | 0.03315 | -0.0029528 | -0.0082062 | 0.024899 | -0.0065185 | 0.046831 | 0.13419 | 0.064843 | 0.22153 | 0.014096 | 0.42126 | 0.15215 | 0.055992 | 0.11483 | 0.062695 | 0.18066 | 0.34794 | -0.17081 | -0.2191 | 61.6069 | -61.4209 | 61.5016 | 61.5196 | -0.087309 | -61.6284 | -61.2212 | 61.2357 | -61.4618 | 61.5108 | 61.5175 | 0.28179 | -61.2945 | -61.8133 | 61.6763 | 61.4689 | 61.876 | 61.589 | -61.4903 | 61.6354 | 61.8027 | 61.284 | 61.5696 | -61.8616
1829.7969 | 123.2208 | -61.4456 | 61.6287 | 0.0094624 | 0.0091132 | 0.017915 | -0.024762 | -0.0041899 | -0.00044864 | -0.0093855 | 0.032937 | -0.0035938 | -0.0082062 | 0.024686 | -0.0065185 | 0.042253 | 0.12503 | 0.051108 | 0.18032 | 0.023254 | 0.38463 | 0.15215 | 0.055992 | 0.11025 | 0.062695 | 0.17608 | 0.34794 | -0.17539 | -0.22825 | 61.5978 | -61.4484 | 61.4879 | 61.4967 | -0.10104 | -61.6055 | -61.2441 | 61.2174 | -61.4526 | 61.5016 | 61.5083 | 0.29095 | -61.2808 | -61.8041 | 61.6259 | 61.4689 | 61.8303 | 61.5706 | -61.4766 | 61.6217 | 61.7936 | 61.2702 | 61.5559 | -61.857
1830.7969 | 123.1934 | -61.4639 | 61.6241 | 0.0018314 | 0.0088994 | 0.017915 | -0.024975 | -0.0041899 | -0.00066244 | -0.017016 | 0.032937 | -0.0038074 | -0.0082062 | 0.024472 | -0.0063049 | 0.042253 | 0.14334 | 0.060265 | 0.22153 | 0.014096 | 0.31595 | 0.14757 | 0.06515 | 0.12398 | 0.058117 | 0.17608 | 0.35252 | -0.17081 | -0.21452 | 61.6115 | -61.4026 | 61.5062 | 61.5242 | -0.087308 | -61.6101 | -61.3082 | 61.2494 | -61.4481 | 61.5291 | 61.522 | 0.27263 | -61.2716 | -61.795 | 61.6855 | 61.478 | 61.7799 | 61.6073 | -61.4766 | 61.64 | 61.8165 | 61.2931 | 61.5879 | -61.8387

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Cable 3
-0.5896 | 23.6822 | 24.2534 | 24.3993 | 24.1579
0.4104 | 23.6741 | 24.2451 | 24.4012 | 24.1636
1.4104 | 23.6643 | 24.2552 | 24.3983 | 24.1666
2.4104 | 23.6762 | 24.2426 | 24.3982 | 24.1665
3.4104 | 23.6757 | 24.2381 | 24.3966 | 24.1653
4.4104 | 23.6634 | 24.2501 | 24.3951 | 24.1697
5.4104 | 23.6703 | 24.2476 | 24.398 | 24.1583
6.4104 | 23.6613 | 24.2415 | 24.3959 | 24.1594
7.4104 | 23.661 | 24.2429 | 24.3903 | 24.1626
8.4104 | 23.6626 | 24.2362 | 24.3994 | 24.1656
9.4104 | 23.6684 | 24.2403 | 24.3931 | 24.1623
10.4104 | 23.6712 | 24.2376 | 24.392 | 24.1617
11.4104 | 23.6622 | 24.2419 | 24.3899 | 24.1679
12.4104 | 23.6618 | 24.253 | 24.3928 | 24.1669
13.4104 | 23.8746 | 24.2385 | 24.3904 | 24.17
14.4104 | 24.7512 | 24.2523 | 24.3928 | 24.1575
15.4104 | 26.3891 | 24.2572 | 24.3963 | 24.1603
16.4104 | 28.7378 | 24.2489 | 24.405 | 24.1636
17.4104 | 31.6572 | 24.2636 | 24.4079 | 24.1617
18.4104 | 35.0441 | 24.2734 | 24.4247 | 24.1594
19.4104 | 38.8313 | 24.2862 | 24.4335 | 24.1593
20.4104 | 42.9334 | 24.3021 | 24.4544 | 24.1648
21.4104 | 47.2678 | 24.3306 | 24.4709 | 24.1581
22.4104 | 51.8539 | 24.353 | 24.505 | 24.1617
23.4104 | 56.6307 | 24.3767 | 24.5467 | 24.1621
24.4104 | 61.5745 | 24.4163 | 24.6015 | 24.1629
25.4104 | 66.6633 | 24.4605 | 24.6504 | 24.165
26.4104 | 71.9046 | 24.5372 | 24.6836 | 24.1614
27.4104 | 77.3377 | 24.6016 | 24.7387 | 24.1664
28.4104 | 82.8356 | 24.675 | 24.8006 | 24.1659
29.4104 | 88.4126 | 24.7263 | 24.8522 | 24.1608
30.4104 | 94.1034 | 24.8035 | 24.876 | 24.1706
31.4104 | 99.9247 | 24.9044 | 24.9588 | 24.1679
32.4104 | 105.7173 | 24.9659 | 25.0161 | 24.1567
33.4104 | 111.6147 | 25.0445 | 25.1415 | 24.169
34.4104 | 117.5025 | 25.1647 | 25.2378 | 24.1625
35.4104 | 123.4012 | 25.2478 | 25.3124 | 24.1648
36.4104 | 129.3903 | 25.3896 | 25.4042 | 24.1673
37.4104 | 135.4175 | 25.5318 | 25.519 | 24.1709
38.4104 | 141.4647 | 25.7286 | 25.6315 | 24.1741
39.4104 | 147.5295 | 25.8295 | 25.761 | 24.1744
40.4104 | 153.4979 | 25.9308 | 25.8881 | 24.1686
41.4104 | 159.4794 | 26.0722 | 25.9858 | 24.1681
42.4104 | 165.4946 | 26.2319 | 26.1918 | 24.1707
43.4104 | 171.4889 | 26.3788 | 26.3194 | 24.1696
44.4104 | 177.4376 | 26.5613 | 26.4387 | 24.1712
45.4104 | 183.3655 | 26.7791 | 26.6183 | 24.1738
46.4104 | 189.2884 | 27.0123 | 26.8836 | 24.1705
47.4104 | 195.2339 | 27.2274 | 27.0136 | 24.1684
48.4104 | 201.0813 | 27.3367 | 27.2326 | 24.1662
49.4104 | 206.9459 | 27.5778 | 27.4916 | 24.1775
50.4104 | 212.931 | 27.8057 | 27.6888 | 24.1731
51.4104 | 218.942 | 28.0817 | 27.8274 | 24.1699
52.4104 | 224.8527 | 28.4109 | 28.0076 | 24.1679
53.4104 | 230.7897 | 28.6788 | 28.2465 | 24.1719
54.4104 | 236.6005 | 28.9362 | 28.362 | 24.1706
55.4104 | 242.4283 | 29.2102 | 28.5544 | 24.1742
56.4104 | 248.2876 | 29.5728 | 28.7117 | 24.1678
57.4104 | 254.1634 | 29.8453 | 28.9349 | 24.1676
58.4104 | 260.0616 | 30.1898 | 29.3691 | 24.1709
59.4104 | 265.921 | 30.4996 | 29.7664 | 24.1654
60.4104 | 271.7074 | 30.8777 | 30.079 | 24.1664
61.4104 | 277.4387 | 31.2494 | 30.3619 | 24.1738
62.4104 | 283.1602 | 31.6092 | 30.7504 | 24.1781
63.4104 | 288.8548 | 31.9795 | 31.0262 | 24.1737
64.4104 | 294.5287 | 32.4069 | 31.2194 | 24.1779
65.4104 | 300.2896 | 32.8025 | 31.6202 | 24.1726
66.4104 | 305.8804 | 33.2769 | 32.0118 | 24.1724
67.4104 | 311.5255 | 33.738 | 32.3797 | 24.1718
68.4104 | 317.2284 | 34.2096 | 32.6319 | 24.1762
69.4104 | 322.8774 | 34.6866 | 33.0182 | 24.179
70.4104 | 328.4748 | 35.133 | 33.4283 | 24.1772
71.4104 | 333.9317 | 35.7041 | 33.8767 | 24.1794
72.4104 | 339.3459 | 36.2884 | 34.2489 | 24.1872
73.4104 | 344.9165 | 36.8483 | 34.7828 | 24.1817
74.4104 | 350.5063 | 37.3829 | 35.197 | 24.1914
75.4104 | 355.851 | 37.9192 | 35.668 | 24.1867
76.4104 | 361.1911 | 38.4794 | 36.2919 | 24.1893
77.4104 | 366.4957 | 39.1442 | 36.6951 | 24.1908
78.4104 | 371.8347 | 39.7715 | 37.1253 | 24.192
79.4104 | 377.0519 | 40.4646 | 37.7441 | 24.1973
80.4104 | 382.2634 | 41.0254 | 38.5153 | 24.1977
81.4104 | 387.4644 | 41.7375 | 39.2141 | 24.1958
82.4104 | 392.6606 | 42.4043 | 39.8097 | 24.2023
83.4104 | 397.811 | 43.1723 | 40.537 | 24.199
84.4104 | 402.8972 | 43.8713 | 41.0528 | 24.2036
85.4104 | 408.0116 | 44.6326 | 41.5692 | 24.2077
86.4104 | 413.0354 | 45.3932 | 42.1685 | 24.205
87.4104 | 418.1121 | 46.1962 | 42.8884 | 24.2174
88.4104 | 423.1434 | 47.0497 | 43.5407 | 24.219
89.4104 | 428.2073 | 47.8728 | 44.2068 | 24.2218
90.4104 | 433.2587 | 48.7356 | 44.8482 | 24.2206
91.4104 | 438.1241 | 49.5718 | 45.7831 | 24.2258
92.4104 | 442.8909 | 50.4815 | 46.4031 | 24.2286
93.4104 | 447.6948 | 51.4 | 47.18 | 24.2385
94.4104 | 452.5336 | 52.296 | 47.8514 | 24.2384
95.4104 | 457.3526 | 53.2596 | 48.7235 | 24.2392
96.4104 | 462.089 | 54.1914 | 49.8401 | 24.2478
97.4104 | 466.8015 | 55.2221 | 50.6652 | 24.2565
98.4104 | 471.4406 | 56.2892 | 51.4868 | 24.2592
99.4104 | 475.6104 | 57.301 | 52.3888 | 24.2607
100.4104 | 479.3669 | 58.2489 | 53.2097 | 24.2738
101.4104 | 482.8009 | 59.3095 | 54.0587 | 24.2769
102.4104 | 485.9342 | 60.2738 | 55.0084 | 24.2815
103.4104 | 488.8053 | 61.3155 | 55.9168 | 24.293
104.4104 | 491.6011 | 62.4014 | 56.7417 | 24.2908
105.4104 | 494.4003 | 63.4092 | 57.5683 | 24.2952
106.4104 | 497.1885 | 64.4382 | 58.3515 | 24.3112
107.4104 | 499.765 | 65.545 | 59.3979 | 24.3211
108.4104 | 502.2418 | 66.6717 | 60.3394 | 24.3279
109.4104 | 504.6068 | 67.7244 | 61.3646 | 24.3316
110.4104 | 506.825 | 68.8284 | 62.2287 | 24.3432
111.4104 | 508.8052 | 69.8759 | 63.33 | 24.3444
112.4104 | 510.5162 | 70.981 | 64.1438 | 24.3738
113.4104 | 511.966 | 72.1498 | 65.0356 | 24.3722
114.4104 | 512.9849 | 73.1808 | 66.0383 | 24.3903
115.4104 | 513.9628 | 74.2314 | 66.9442 | 24.3927
116.4104 | 514.7461 | 75.2917 | 67.9339 | 24.4125
117.4104 | 515.3756 | 76.249 | 68.8586 | 24.4196
118.4104 | 515.9303 | 77.2921 | 69.7055 | 24.4344
119.4104 | 516.4198 | 78.4105 | 70.6856 | 24.4489
120.4104 | 516.6715 | 79.4439 | 71.607 | 24.4539
121.4104 | 516.83 | 80.5369 | 72.499 | 24.4733
122.4104 | 517.012 | 81.5773 | 73.4204 | 24.4873
123.4104 | 517.1775 | 82.6165 | 74.3175 | 24.505
124.4104 | 517.2252 | 83.7066 | 75.1541 | 24.5245
125.4104 | 517.2877 | 84.7098 | 76.0828 | 24.5361
126.4104 | 517.4119 | 85.7086 | 76.9572 | 24.5586
127.4104 | 517.6088 | 86.7599 | 77.9653 | 24.5719
128.4104 | 517.6551 | 87.7993 | 78.8727 | 24.5904
129.4104 | 517.636 | 88.9172 | 79.8074 | 24.6059
130.4104 | 517.6866 | 89.8999 | 80.7111 | 24.6269
131.4104 | 517.6535 | 90.875 | 81.6551 | 24.6486
132.4104 | 517.7346 | 91.9195 | 82.4866 | 24.6718
133.4104 | 517.7616 | 92.9843 | 83.4311 | 24.6905
134.4104 | 517.7985 | 94.0417 | 84.3736 | 24.7065
135.4104 | 517.8075 | 95.0949 | 85.2755 | 24.7346
136.4104 | 517.9306 | 96.1754 | 86.2169 | 24.7511
137.4104 | 517.9854 | 97.2229 | 87.0862 | 24.7863
138.4104 | 518.2119 | 98.2668 | 88.1042 | 24.8126
139.4104 | 518.3157 | 99.2532 | 89.1048 | 24.8279
140.4104 | 518.4667 | 100.2951 | 89.9225 | 24.8604
141.4104 | 518.6602 | 101.3725 | 90.8704 | 24.8889
142.4104 | 518.8425 | 102.3902 | 91.9132 | 24.9172
143.4104 | 519.079 | 103.4066 | 92.8994 | 24.9413
144.4104 | 519.3112 | 104.4196 | 93.7563 | 24.9739
145.4104 | 519.5493 | 105.4523 | 94.656 | 25.006
146.4104 | 519.6904 | 106.4748 | 95.5927 | 25.0378
147.4104 | 519.8571 | 107.4837 | 96.4271 | 25.0667
148.4104 | 519.9744 | 108.5689 | 97.3869 | 25.1064
149.4104 | 520.0533 | 109.5662 | 98.2812 | 25.1389
150.4104 | 520.1901 | 110.5878 | 99.2387 | 25.1686
151.4104 | 520.4031 | 111.641 | 100.1575 | 25.203
152.4104 | 520.6121 | 112.6383 | 101.1331 | 25.2372
153.4104 | 520.7527 | 113.6949 | 101.948 | 25.2761
154.4104 | 520.9981 | 114.7252 | 102.8799 | 25.3197
155.4104 | 521.1552 | 115.7059 | 103.839 | 25.3521
156.4104 | 521.2101 | 116.6898 | 104.7639 | 25.3968
157.4104 | 521.3068 | 117.7418 | 105.6208 | 25.4384
158.4104 | 521.567 | 118.7907 | 106.6403 | 25.474
159.4104 | 521.7874 | 119.7154 | 107.5285 | 25.5272
160.4104 | 521.8673 | 120.6756 | 108.4439 | 25.5664
161.4104 | 521.8867 | 121.748 | 109.3918 | 25.608
162.4104 | 521.8695 | 122.7567 | 110.3309 | 25.6554
163.4104 | 522.0533 | 123.7514 | 111.1914 | 25.7025
164.4104 | 522.2302 | 124.7353 | 112.0248 | 25.7545
165.4104 | 522.2952 | 125.7712 | 112.9131 | 25.7983
166.4104 | 522.2637 | 126.7468 | 113.7895 | 25.8469
167.4104 | 522.2779 | 127.7613 | 114.6221 | 25.9006
168.4104 | 522.268 | 128.7816 | 115.6208 | 25.9469
169.4104 | 522.409 | 129.7969 | 116.5975 | 25.9875
170.4104 | 522.3607 | 130.8052 | 117.4873 | 26.0321
171.4104 | 522.328 | 131.8134 | 118.4618 | 26.0942
172.4104 | 522.2975 | 132.7717 | 119.3206 | 26.1519
173.4104 | 522.3229 | 133.7157 | 120.1972 | 26.206
174.4104 | 522.4031 | 134.6887 | 121.1134 | 26.2658
175.4104 | 522.5107 | 135.7118 | 121.9681 | 26.3238
176.4104 | 522.6694 | 136.7325 | 122.8741 | 26.3837
177.4104 | 522.7965 | 137.7107 | 123.7762 | 26.4413
178.4104 | 522.8747 | 138.6595 | 124.659 | 26.5027
179.4104 | 522.7736 | 139.5699 | 125.5277 | 26.5615
180.4104 | 522.6302 | 140.5376 | 126.4174 | 26.6263
181.4104 | 522.6404 | 141.4847 | 127.3513 | 26.6935
182.4104 | 522.6444 | 142.4759 | 128.2533 | 26.7559
183.4104 | 522.5988 | 143.4187 | 129.0762 | 26.8251
184.4104 | 522.5721 | 144.3348 | 129.998 | 26.8934
185.4104 | 522.7271 | 145.3248 | 130.9385 | 26.9626
186.4104 | 522.7632 | 146.2613 | 131.8088 | 27.0303
187.4104 | 522.7348 | 147.2245 | 132.6267 | 27.1047
188.4104 | 522.7521 | 148.1917 | 133.4595 | 27.1762
189.4104 | 522.8242 | 149.1118 | 134.3636 | 27.2577
190.4104 | 522.7052 | 150.0811 | 135.225 | 27.3311
191.4104 | 522.5454 | 151.0053 | 136.1452 | 27.4057
192.4104 | 522.5065 | 151.9122 | 136.9494 | 27.4802
193.4104 | 522.4604 | 152.8573 | 137.8318 | 27.5645
194.4104 | 522.528 | 153.7913 | 138.6974 | 27.6469
195.4104 | 522.6648 | 154.7318 | 139.5202 | 27.7266
196.4104 | 522.658 | 155.7284 | 140.3524 | 27.8044
197.4104 | 522.6362 | 156.6005 | 141.2126 | 27.8925
198.4104 | 522.5435 | 157.5113 | 142.0613 | 27.9749
199.4104 | 522.484 | 158.4428 | 142.932 | 28.0579
200.4104 | 522.4204 | 159.348 | 143.8066 | 28.1452
201.4104 | 522.42 | 160.2587 | 144.6817 | 28.2319
202.4104 | 522.3421 | 161.1816 | 145.5933 | 28.3197
203.4104 | 522.3051 | 162.0786 | 146.4343 | 28.4095
204.4104 | 522.2304 | 162.9794 | 147.283 | 28.5076
205.4104 | 522.2193 | 163.895 | 148.0698 | 28.5957
206.4104 | 522.1118 | 164.8027 | 148.9575 | 28.6831
207.4104 | 522.0952 | 165.6858 | 149.7984 | 28.786
208.4104 | 522.1442 | 166.5803 | 150.627 | 28.8819
209.4104 | 522.1351 | 167.4639 | 151.5268 | 28.9783
210.4104 | 522.0657 | 168.3599 | 152.2689 | 29.0773
211.4104 | 522.0304 | 169.2812 | 153.1113 | 29.1815
212.4104 | 522.0129 | 170.1593 | 153.896 | 29.2753
213.4104 | 522.0318 | 171.0369 | 154.7507 | 29.3818
214.4104 | 521.943 | 171.9081 | 155.5765 | 29.4828
215.4104 | 521.8861 | 172.7441 | 156.4361 | 29.5852
216.4104 | 521.9611 | 173.6395 | 157.3384 | 29.6914
217.4104 | 522.0273 | 174.5265 | 158.0927 | 29.8006
218.4104 | 522.0087 | 175.3893 | 158.9518 | 29.91
219.4104 | 522.0702 | 176.2359 | 159.7213 | 30.0172
220.4104 | 522.1919 | 177.0616 | 160.4834 | 30.1294
221.4104 | 522.297 | 177.9404 | 161.3354 | 30.2456
222.4104 | 522.3084 | 178.8049 | 162.1216 | 30.3549
223.4104 | 522.2527 | 179.6686 | 162.9757 | 30.4678
224.4104 | 522.1567 | 180.5367 | 163.7808 | 30.585
225.4104 | 522.1385 | 181.4199 | 164.5677 | 30.701
226.4104 | 522.2067 | 182.2755 | 165.3763 | 30.822
227.4104 | 522.2816 | 183.0871 | 166.2691 | 30.9498
228.4104 | 522.4261 | 183.9905 | 167.033 | 31.0722
229.4104 | 522.4445 | 184.8285 | 167.7524 | 31.192
230.4104 | 522.4654 | 185.6601 | 168.6345 | 31.3205
231.4104 | 522.4719 | 186.4716 | 169.4343 | 31.4468
232.4104 | 522.5696 | 187.2879 | 170.2162 | 31.5709
233.4104 | 522.6844 | 188.0865 | 170.9821 | 31.6937
234.4104 | 522.6721 | 188.8828 | 171.8591 | 31.8221
235.4104 | 522.8035 | 189.7181 | 172.607 | 31.9525
236.4104 | 522.9082 | 190.5734 | 173.36 | 32.0857
237.4104 | 523.0021 | 191.4175 | 174.113 | 32.2141
238.4104 | 523.1225 | 192.2538 | 174.9169 | 32.3399
239.4104 | 523.1993 | 193.0858 | 175.6537 | 32.4759
240.4104 | 523.1083 | 193.8877 | 176.335 | 32.6151
241.4104 | 523.1028 | 194.7383 | 177.1424 | 32.7478
242.4104 | 523.1412 | 195.5529 | 177.9352 | 32.8858
243.4104 | 523.1364 | 196.3724 | 178.684 | 33.0317
244.4104 | 523.1081 | 197.1629 | 179.4472 | 33.1773
245.4104 | 523.0429 | 197.9474 | 180.1964 | 33.3187
246.4104 | 523.0278 | 198.7437 | 180.9276 | 33.4595
247.4104 | 523.0488 | 199.5593 | 181.6815 | 33.6044
248.4104 | 522.9335 | 200.3834 | 182.4635 | 33.7441
249.4104 | 522.8481 | 201.1929 | 183.2179 | 33.8949
250.4104 | 522.8609 | 201.9861 | 184.0256 | 34.0416
251.4104 | 522.8351 | 202.7446 | 184.736 | 34.1887
252.4104 | 522.8199 | 203.5728 | 185.4498 | 34.3413
253.4104 | 522.7619 | 204.3595 | 186.1876 | 34.488
254.4104 | 522.8476 | 205.1623 | 186.9473 | 34.6389
255.4104 | 522.9673 | 205.9475 | 187.6921 | 34.7922
256.4104 | 523.0026 | 206.7275 | 188.4442 | 34.95
257.4104 | 522.8788 | 207.5239 | 189.1683 | 35.1036
258.4104 | 522.9939 | 208.3244 | 189.851 | 35.262
259.4104 | 523.0935 | 209.0716 | 190.6199 | 35.4218
260.4104 | 523.0827 | 209.8619 | 191.3678 | 35.5775
261.4104 | 523.0618 | 210.647 | 192.1183 | 35.7339
262.4104 | 523.0551 | 211.4433 | 192.8746 | 35.903
263.4104 | 523.065 | 212.2301 | 193.6473 | 36.0647
264.4104 | 523.0361 | 213.0127 | 194.3332 | 36.2268
265.4104 | 522.8584 | 213.786 | 195.0846 | 36.3965
266.4104 | 522.7841 | 214.5499 | 195.7798 | 36.5629
267.4104 | 522.8455 | 215.3217 | 196.5205 | 36.724
268.4104 | 522.7911 | 216.1053 | 197.2353 | 36.8985
269.4104 | 522.7375 | 216.8834 | 197.9821 | 37.0638
270.4104 | 522.669 | 217.6598 | 198.6545 | 37.2366
271.4104 | 522.5791 | 218.4346 | 199.3809 | 37.4076
272.4104 | 522.5302 | 219.1879 | 200.1344 | 37.5877
273.4104 | 522.4986 | 219.9444 | 200.8481 | 37.7603
274.4104 | 522.451 | 220.6742 | 201.5278 | 37.9356
275.4104 | 522.4693 | 221.4188 | 202.1988 | 38.105
276.4104 | 522.5983 | 222.1658 | 202.9077 | 38.2812
277.4104 | 522.6637 | 222.9441 | 203.6172 | 38.467
278.4104 | 522.6925 | 223.6681 | 204.3578 | 38.6469
279.4104 | 522.7293 | 224.3813 | 205.0877 | 38.8234
280.4104 | 522.7046 | 225.1497 | 205.7757 | 39.0035
281.4104 | 522.75 | 225.8905 | 206.4819 | 39.1866
282.4104 | 522.8042 | 226.6362 | 207.1899 | 39.3687
283.4104 | 522.7968 | 227.3652 | 207.8713 | 39.5651
284.4104 | 522.831 | 228.0768 | 208.5548 | 39.7512
285.4104 | 522.7942 | 228.8134 | 209.2785 | 39.9369
286.4104 | 522.7222 | 229.5223 | 209.9836 | 40.1191
287.4104 | 522.6496 | 230.2425 | 210.6368 | 40.3079
288.4104 | 522.5645 | 230.9697 | 211.2901 | 40.5193
289.4104 | 522.4013 | 231.7004 | 211.9686 | 40.7064
290.4104 | 522.4445 | 232.4555 | 212.6438 | 40.9026
291.4104 | 522.5138 | 233.1793 | 213.2994 | 41.0918
292.4104 | 522.4685 | 233.8968 | 213.8904 | 41.2858
293.4104 | 522.3795 | 234.6356 | 214.619 | 41.4853
294.4104 | 522.339 | 235.3379 | 215.3165 | 41.6769
295.4104 | 522.2879 | 236.0634 | 215.8872 | 41.8673
296.4104 | 522.1719 | 236.7635 | 216.5269 | 42.0732
297.4104 | 522.1109 | 237.4638 | 217.1415 | 42.2772
298.4104 | 522.0888 | 238.1455 | 217.7986 | 42.4767
299.4104 | 522.0497 | 238.8668 | 218.4303 | 42.6741
300.4104 | 521.9586 | 239.5809 | 219.1501 | 42.8764
301.4104 | 521.9036 | 240.2901 | 219.8807 | 43.0756
302.4104 | 521.7897 | 240.9735 | 220.5824 | 43.2836
303.4104 | 521.7693 | 241.6652 | 221.2759 | 43.4827
304.4104 | 521.8566 | 242.3565 | 221.9407 | 43.6791
305.4104 | 521.9008 | 243.0393 | 222.6156 | 43.8902
306.4104 | 521.8714 | 243.7373 | 223.289 | 44.1009
307.4104 | 521.8056 | 244.4193 | 223.921 | 44.3081
308.4104 | 521.7308 | 245.1039 | 224.5799 | 44.5143
309.4104 | 521.7744 | 245.782 | 225.2287 | 44.7212
310.4104 | 521.7127 | 246.4738 | 225.7654 | 44.9278
311.4104 | 521.7615 | 247.1719 | 226.4459 | 45.1548
312.4104 | 521.765 | 247.8485 | 227.0844 | 45.3635
313.4104 | 521.8176 | 248.5285 | 227.7443 | 45.5689
314.4104 | 521.8529 | 249.2069 | 228.2886 | 45.7804
315.4104 | 521.7465 | 249.8808 | 228.8623 | 46.0121
316.4104 | 521.6867 | 250.5507 | 229.3538 | 46.2255
317.4104 | 521.7902 | 251.2078 | 230.1098 | 46.4396
318.4104 | 521.8779 | 251.8748 | 230.8033 | 46.6587
319.4104 | 521.9428 | 252.5698 | 231.5049 | 46.8786
320.4104 | 522.0299 | 253.2299 | 232.1503 | 47.1002
321.4104 | 522.1426 | 253.887 | 232.8085 | 47.3126
322.4104 | 522.1727 | 254.5441 | 233.3618 | 47.5387
323.4104 | 522.2127 | 255.2103 | 234.0102 | 47.7718
324.4104 | 522.2844 | 255.8683 | 234.6696 | 47.9926
325.4104 | 522.2962 | 256.5634 | 235.2075 | 48.2228
326.4104 | 522.3846 | 257.2097 | 235.7247 | 48.444
327.4104 | 522.4842 | 257.8478 | 236.4472 | 48.6861
328.4104 | 522.4042 | 258.5111 | 237.107 | 48.9161
329.4104 | 522.3734 | 259.1696 | 237.7316 | 49.1497
330.4104 | 522.5028 | 259.8102 | 238.3725 | 49.3832
331.4104 | 522.5445 | 260.4581 | 239.0059 | 49.6176
332.4104 | 522.5273 | 261.1324 | 239.6377 | 49.8521
333.4104 | 522.4473 | 261.7707 | 240.2483 | 50.1049
334.4104 | 522.4432 | 262.4092 | 240.8659 | 50.3406
335.4104 | 522.4224 | 263.0694 | 241.4713 | 50.5849
336.4104 | 522.4233 | 263.6941 | 242.0939 | 50.8198
337.4104 | 522.4025 | 264.3111 | 242.7084 | 51.0588
338.4104 | 522.3777 | 264.9603 | 243.2607 | 51.3067
339.4104 | 522.3876 | 265.5993 | 243.7947 | 51.5449
340.4104 | 522.3213 | 266.2287 | 244.3035 | 51.7884
341.4104 | 522.2062 | 266.8625 | 245.0029 | 52.0299
342.4104 | 522.1955 | 267.4726 | 245.6488 | 52.2781
343.4104 | 522.2071 | 268.0822 | 246.2057 | 52.5246
344.4104 | 522.1773 | 268.7128 | 246.7194 | 52.773
345.4104 | 522.0922 | 269.3343 | 247.1538 | 53.0196
346.4104 | 522.1145 | 269.9507 | 247.6825 | 53.272
347.4104 | 522.2184 | 270.5835 | 248.3711 | 53.5175
348.4104 | 522.368 | 271.2042 | 249.0673 | 53.7699
349.4104 | 522.2804 | 271.8199 | 249.6828 | 54.0194
350.4104 | 522.105 | 272.4289 | 250.281 | 54.2715
351.4104 | 522.0395 | 273.059 | 250.8896 | 54.5196
352.4104 | 522.0989 | 273.6506 | 251.5301 | 54.7795
353.4104 | 522.1336 | 274.2554 | 252.1122 | 55.0242
354.4104 | 522.1237 | 274.8559 | 252.4761 | 55.2724
355.4104 | 521.9616 | 275.4529 | 253.0517 | 55.5246
356.4104 | 521.9922 | 276.0579 | 253.559 | 55.7876
357.4104 | 521.993 | 276.6751 | 254.0788 | 56.0423
358.4104 | 522.0245 | 277.2661 | 254.6151 | 56.2937
359.4104 | 521.9921 | 277.8613 | 255.2039 | 56.5476
360.4104 | 521.7568 | 278.457 | 255.6967 | 56.8084
361.4104 | 521.6975 | 279.0645 | 256.2019 | 57.0737
362.4104 | 521.7124 | 279.661 | 256.7343 | 57.3214
363.4104 | 521.7142 | 280.2421 | 257.4206 | 57.5883
364.4104 | 521.671 | 280.8311 | 257.9589 | 57.8482
365.4104 | 521.6471 | 281.4385 | 258.5441 | 58.1102
366.4104 | 521.6661 | 282.0111 | 259.1644 | 58.3722
367.4104 | 521.6189 | 282.5828 | 259.7451 | 58.6387
368.4104 | 521.6769 | 283.1714 | 260.2736 | 58.9117
369.4104 | 521.6474 | 283.7432 | 260.6364 | 59.1769
370.4104 | 521.5004 | 284.3304 | 261.0383 | 59.4579
371.4104 | 521.3992 | 284.911 | 261.4801 | 59.7313
372.4104 | 521.3549 | 285.472 | 262.1527 | 60.0078
373.4104 | 521.3493 | 286.0348 | 262.8556 | 60.2798
374.4104 | 521.4166 | 286.6052 | 263.3131 | 60.5607
375.4104 | 521.4832 | 287.1668 | 263.894 | 60.8427
376.4104 | 521.3739 | 287.7265 | 264.3995 | 61.1302
377.4104 | 521.2949 | 288.3211 | 264.8144 | 61.4319
378.4104 | 521.3431 | 288.8889 | 265.2493 | 61.7272
379.4104 | 521.3837 | 289.4473 | 265.7817 | 62.0274
380.4104 | 521.5158 | 290.0116 | 266.4957 | 62.3191
381.4104 | 521.5778 | 290.5739 | 267.0982 | 62.6226
382.4104 | 521.56 | 291.1114 | 267.672 | 62.9275
383.4104 | 521.6126 | 291.6798 | 268.1807 | 63.2318
384.4104 | 521.6985 | 292.228 | 268.7095 | 63.5372
385.4104 | 521.7416 | 292.7913 | 269.3044 | 63.8373
386.4104 | 521.7749 | 293.3413 | 269.8529 | 64.1341
387.4104 | 521.752 | 293.9014 | 270.2401 | 64.432
388.4104 | 521.784 | 294.4375 | 270.6933 | 64.7387
389.4104 | 521.7996 | 294.9946 | 271.2873 | 65.0435
390.4104 | 521.6932 | 295.548 | 271.9288 | 65.3407
391.4104 | 521.6218 | 296.0904 | 272.4735 | 65.6498
392.4104 | 521.5152 | 296.6325 | 272.9265 | 65.9498
393.4104 | 521.5094 | 297.1825 | 273.3554 | 66.2541
394.4104 | 521.5842 | 297.7288 | 274.0038 | 66.5599
395.4104 | 521.562 | 298.2738 | 274.5009 | 66.8644
396.4104 | 521.5714 | 298.7902 | 275.0958 | 67.1669
397.4104 | 521.643 | 299.3432 | 275.6204 | 67.4808
398.4104 | 521.6704 | 299.893 | 275.9637 | 67.7888
399.4104 | 521.5583 | 300.4281 | 276.5901 | 68.1
400.4104 | 521.5723 | 300.9553 | 277.0519 | 68.4052
401.4104 | 521.5351 | 301.4888 | 277.4913 | 68.7051
402.4104 | 521.5489 | 302.0193 | 278.1578 | 69.0341
403.4104 | 521.4832 | 302.5042 | 278.642 | 69.3389
404.4104 | 521.3952 | 303.0752 | 278.9738 | 69.6467
405.4104 | 521.269 | 303.5971 | 279.5412 | 69.9618
406.4104 | 521.2138 | 304.121 | 279.744 | 70.2649
407.4104 | 521.1338 | 304.6336 | 280.3234 | 70.5735
408.4104 | 521.0746 | 305.1407 | 280.9526 | 70.8836
409.4104 | 521.1262 | 305.6338 | 281.5692 | 71.2062
410.4104 | 521.0557 | 306.1515 | 281.9589 | 71.5123
411.4104 | 521.0479 | 306.6799 | 282.5244 | 71.8276
412.4104 | 521.0173 | 307.1805 | 283.0403 | 72.141
413.4104 | 521.0503 | 307.708 | 283.4043 | 72.448
414.4104 | 520.9483 | 308.2306 | 283.9879 | 72.7691
415.4104 | 520.8882 | 308.7495 | 284.5843 | 73.0805
416.4104 | 520.9494 | 309.2543 | 285.0046 | 73.3933
417.4104 | 520.8813 | 309.7541 | 285.4596 | 73.7048
418.4104 | 520.8296 | 310.254 | 285.9861 | 74.0206
419.4104 | 520.8574 | 310.7583 | 286.3631 | 74.3367
420.4104 | 520.9206 | 311.2656 | 286.8084 | 74.6487
421.4104 | 521.0098 | 311.772 | 287.4164 | 74.9634
422.4104 | 521.0861 | 312.2647 | 287.9558 | 75.2777
423.4104 | 521.0993 | 312.7555 | 288.389 | 75.6051
424.4104 | 521.1083 | 313.2513 | 288.8513 | 75.9245
425.4104 | 521.0592 | 313.7407 | 289.2127 | 76.2438
426.4104 | 521.0736 | 314.2293 | 289.7327 | 76.5611
427.4104 | 520.9471 | 314.7185 | 290.113 | 76.873
428.4104 | 520.9628 | 315.2099 | 290.5898 | 77.1875
429.4104 | 520.9208 | 315.7044 | 291.1188 | 77.5163
430.4104 | 520.8381 | 316.1961 | 291.4466 | 77.8309
431.4104 | 520.7994 | 316.6756 | 291.8392 | 78.1539
432.4104 | 520.7067 | 317.1698 | 292.3161 | 78.4883
433.4104 | 520.6145 | 317.6438 | 292.9086 | 78.8058
434.4104 | 520.6333 | 318.1279 | 293.4712 | 79.1236
435.4104 | 520.5244 | 318.6216 | 293.9513 | 79.4523
436.4104 | 520.5651 | 319.0887 | 294.3479 | 79.7745
437.4104 | 520.4397 | 319.5556 | 294.789 | 80.0953
438.4104 | 520.3817 | 320.0393 | 295.2882 | 80.4185
439.4104 | 520.3644 | 320.4971 | 295.7607 | 80.7419
440.4104 | 520.3802 | 320.9671 | 296.252 | 81.0655
441.4104 | 520.252 | 321.4428 | 296.5826 | 81.385
442.4104 | 520.0864 | 321.914 | 296.852 | 81.703
443.4104 | 519.954 | 322.3636 | 297.37 | 82.0294
444.4104 | 519.9085 | 322.8315 | 297.9207 | 82.3596
445.4104 | 519.9311 | 323.3165 | 298.3103 | 82.6891
446.4104 | 519.9912 | 323.7729 | 298.6365 | 83.0018
447.4104 | 520.0277 | 324.2354 | 299.1188 | 83.3299
448.4104 | 520.0765 | 324.6771 | 299.3795 | 83.6588
449.4104 | 520.2346 | 325.1539 | 299.8937 | 83.9829
450.4104 | 520.3938 | 325.6022 | 300.2857 | 84.3066
451.4104 | 520.5004 | 326.0553 | 300.7486 | 84.6312
452.4104 | 520.5654 | 326.5099 | 301.347 | 84.9591
453.4104 | 520.761 | 326.9835 | 301.7019 | 85.279
454.4104 | 520.8417 | 327.4478 | 302.2021 | 85.6095
455.4104 | 520.7957 | 327.8896 | 302.5126 | 85.9342
456.4104 | 520.7557 | 328.3389 | 302.8152 | 86.2628
457.4104 | 520.6706 | 328.8073 | 303.3281 | 86.5955
458.4104 | 520.6472 | 329.2525 | 303.7162 | 86.9239
459.4104 | 520.6153 | 329.6935 | 304.14 | 87.2442
460.4104 | 520.6343 | 330.139 | 304.6858 | 87.5733
461.4104 | 520.5468 | 330.5757 | 305.0422 | 87.9077
462.4104 | 520.4718 | 331.0253 | 305.4497 | 88.243
463.4104 | 520.462 | 331.4717 | 306.0152 | 88.5717
464.4104 | 520.4803 | 331.9193 | 306.5391 | 88.8985
465.4104 | 520.4945 | 332.3479 | 306.8864 | 89.2268
466.4104 | 520.4954 | 332.806 | 307.3492 | 89.5539
467.4104 | 520.4872 | 333.2464 | 307.7765 | 89.8913
468.4104 | 520.623 | 333.6748 | 308.0679 | 90.2115
469.4104 | 520.6191 | 334.1142 | 308.3894 | 90.5453
470.4104 | 520.5525 | 334.5331 | 308.9938 | 90.8697
471.4104 | 520.6094 | 334.9836 | 309.5535 | 91.2045
472.4104 | 520.6159 | 335.4125 | 310.0432 | 91.5361
473.4104 | 520.5433 | 335.8272 | 310.4467 | 91.864
474.4104 | 520.5658 | 336.2749 | 310.8684 | 92.1961
475.4104 | 520.5792 | 336.7169 | 311.3272 | 92.5213
476.4104 | 520.5516 | 337.1267 | 311.8021 | 92.8575
477.4104 | 520.5444 | 337.5455 | 312.2712 | 93.1901
478.4104 | 520.5631 | 337.9763 | 312.4966 | 93.5246
479.4104 | 520.6252 | 338.3866 | 312.8063 | 93.8514
480.4104 | 520.6922 | 338.824 | 313.0236 | 94.1827
481.4104 | 520.6938 | 339.2606 | 313.4618 | 94.5253
482.4104 | 520.7034 | 339.6518 | 314.0224 | 94.8544
483.4104 | 520.6074 | 340.0866 | 314.5291 | 95.1873
484.4104 | 520.593 | 340.4976 | 314.9933 | 95.5165
485.4104 | 520.6358 | 340.9146 | 315.499 | 95.8571
486.4104 | 520.6171 | 341.3308 | 315.9187 | 96.1837
487.4104 | 520.6142 | 341.7211 | 316.277 | 96.5262
488.4104 | 520.5415 | 342.1391 | 316.6386 | 96.862
489.4104 | 520.4895 | 342.5442 | 317.1167 | 97.2057
490.4104 | 520.4456 | 342.9385 | 317.5407 | 97.5542
491.4104 | 520.4572 | 343.3707 | 318.0352 | 97.8784
492.4104 | 520.4887 | 343.7737 | 318.3971 | 98.2171
493.4104 | 520.5915 | 344.1638 | 318.8252 | 98.5583
494.4104 | 520.5979 | 344.5546 | 319.1893 | 98.9024
495.4104 | 520.7003 | 344.9636 | 319.5824 | 99.23
496.4104 | 520.7463 | 345.3537 | 320.0587 | 99.5697
497.4104 | 520.7819 | 345.7587 | 320.323 | 99.9051
498.4104 | 520.8449 | 346.1582 | 320.793 | 100.2503
499.4104 | 520.9474 | 346.5613 | 321.2693 | 100.5891
500.4104 | 521.0262 | 346.9877 | 321.6998 | 100.922
501.4104 | 521.1334 | 347.3665 | 322.0321 | 101.2651
502.4104 | 521.1679 | 347.7838 | 322.3654 | 101.597
503.4104 | 521.185 | 348.1715 | 322.8694 | 101.946
504.4104 | 521.1857 | 348.5539 | 323.0642 | 102.2812
505.4104 | 521.0981 | 348.9426 | 323.4412 | 102.6191
506.4104 | 521.0775 | 349.3098 | 324.003 | 102.9571
507.4104 | 521.2003 | 349.7 | 324.4438 | 103.2916
508.4104 | 521.2919 | 350.1182 | 324.8772 | 103.624
509.4104 | 521.3645 | 350.5131 | 325.3098 | 103.9565
510.4104 | 521.4878 | 350.9183 | 325.7788 | 104.2877
511.4104 | 521.5526 | 351.2967 | 326.1827 | 104.6186
512.4104 | 521.5635 | 351.6968 | 326.5889 | 104.9437
513.4104 | 521.6311 | 352.0871 | 327.0627 | 105.275
514.4104 | 521.6234 | 352.4417 | 327.4505 | 105.6
515.4104 | 521.5949 | 352.8231 | 327.8264 | 105.9272
516.4104 | 521.6062 | 353.184 | 328.1605 | 106.244
517.4104 | 521.6973 | 353.5668 | 328.5828 | 106.5719
518.4104 | 521.7856 | 353.9515 | 329.0045 | 106.8742
519.4104 | 521.7535 | 354.3501 | 329.3981 | 107.1767
520.4104 | 521.6781 | 354.7192 | 329.7664 | 107.4862
521.4104 | 521.656 | 355.0892 | 330.1772 | 107.7742
522.4104 | 521.7486 | 355.4776 | 330.5286 | 108.0623
523.4104 | 521.7909 | 355.845 | 330.8803 | 108.3475
524.4104 | 521.6862 | 356.2233 | 331.2833 | 108.6205
525.4104 | 521.6318 | 356.5703 | 331.6852 | 108.9089
526.4104 | 521.6494 | 356.9619 | 332.1357 | 109.1878
527.4104 | 521.6223 | 357.3343 | 332.2543 | 109.4695
528.4104 | 521.4934 | 357.6765 | 332.6419 | 109.75
529.4104 | 521.5264 | 358.0511 | 332.9438 | 110.0426
530.4104 | 521.5489 | 358.4059 | 333.3854 | 110.337
531.4104 | 521.3655 | 358.7798 | 333.861 | 110.6348
532.4104 | 521.2501 | 359.1125 | 333.9003 | 110.9309
533.4104 | 521.0678 | 359.4632 | 334.2813 | 111.2442
534.4104 | 520.8618 | 359.8214 | 334.6662 | 111.5584
535.4104 | 520.9048 | 360.185 | 335.1581 | 111.8807
536.4104 | 521.0855 | 360.5271 | 335.5624 | 112.2046
537.4104 | 521.0343 | 360.8874 | 336.0044 | 112.5274
538.4104 | 520.9686 | 361.2654 | 336.3397 | 112.8612
539.4104 | 520.8911 | 361.6343 | 336.3704 | 113.1889
540.4104 | 520.8174 | 361.9881 | 336.7153 | 113.5286
541.4104 | 520.7833 | 362.3099 | 337.231 | 113.8631
542.4104 | 520.6658 | 362.6587 | 337.6123 | 114.1971
543.4104 | 520.6271 | 363.0098 | 337.9921 | 114.5372
544.4104 | 520.5433 | 363.3413 | 338.3853 | 114.8755
545.4104 | 520.4871 | 363.6954 | 338.816 | 115.2159
546.4104 | 520.4817 | 364.0586 | 339.2291 | 115.5553
547.4104 | 520.5455 | 364.4086 | 339.5678 | 115.8874
548.4104 | 520.5882 | 364.7527 | 339.939 | 116.2374
549.4104 | 520.6354 | 365.0935 | 340.3087 | 116.5771
550.4104 | 520.8024 | 365.443 | 340.6419 | 116.9134
551.4104 | 520.8857 | 365.7559 | 340.9657 | 117.2518
552.4104 | 520.8987 | 366.0615 | 341.1259 | 117.5936
553.4104 | 520.9352 | 366.435 | 341.5293 | 117.9263
554.4104 | 520.9964 | 366.7886 | 341.6723 | 118.2578
555.4104 | 521.0994 | 367.1579 | 342.0321 | 118.5934
556.4104 | 520.9882 | 367.4809 | 342.4762 | 118.9247
557.4104 | 521.0621 | 367.8191 | 342.8304 | 119.2614
558.4104 | 521.0672 | 368.1498 | 343.1919 | 119.5925
559.4104 | 521.0507 | 368.4449 | 343.5665 | 119.9301
560.4104 | 521.0373 | 368.782 | 343.7807 | 120.2588
561.4104 | 521.0318 | 369.0841 | 343.8836 | 120.5921
562.4104 | 520.945 | 369.384 | 343.9394 | 120.922
563.4104 | 520.7912 | 369.7546 | 344.4515 | 121.2545
564.4104 | 520.6565 | 370.0824 | 344.737 | 121.5904
565.4104 | 520.7008 | 370.4068 | 345.1038 | 121.9305
566.4104 | 520.721 | 370.7468 | 345.5902 | 122.2713
567.4104 | 520.7437 | 371.057 | 345.9552 | 122.6091
568.4104 | 520.7115 | 371.3889 | 346.3126 | 122.9548
569.4104 | 520.7234 | 371.7042 | 346.6456 | 123.3099
570.4104 | 520.7132 | 372.0452 | 347.0831 | 123.659
571.4104 | 520.7236 | 372.3737 | 347.3984 | 124.0213
572.4104 | 520.7637 | 372.6866 | 347.6851 | 124.3949
573.4104 | 520.781 | 373.0005 | 347.7558 | 124.7584
574.4104 | 520.7839 | 373.3195 | 348.265 | 125.1483
575.4104 | 520.7311 | 373.643 | 348.5946 | 125.5429
576.4104 | 520.548 | 373.9867 | 348.8075 | 125.9503
577.4104 | 520.486 | 374.2838 | 349.1715 | 126.3549
578.4104 | 520.5043 | 374.59 | 349.5976 | 126.7669
579.4104 | 520.5672 | 374.8909 | 350.0089 | 127.1801
580.4104 | 520.5036 | 375.1904 | 350.4482 | 127.6089
581.4104 | 520.363 | 375.4852 | 350.8318 | 128.0368
582.4104 | 520.2804 | 375.8136 | 351.1641 | 128.465
583.4104 | 520.332 | 376.1307 | 351.3192 | 128.8957
584.4104 | 520.341 | 376.4388 | 351.4172 | 129.3347
585.4104 | 520.487 | 376.7429 | 351.8837 | 129.7807
586.4104 | 520.595 | 377.0508 | 352.1211 | 130.2213
587.4104 | 520.647 | 377.356 | 352.5615 | 130.6626
588.4104 | 520.5508 | 377.675 | 352.5689 | 131.1036
589.4104 | 520.545 | 377.9857 | 352.8527 | 131.5504
590.4104 | 520.6676 | 378.2839 | 353.3832 | 131.9947
591.4104 | 520.7673 | 378.5899 | 353.7954 | 132.4459
592.4104 | 520.6882 | 378.8976 | 354.0096 | 132.8955
593.4104 | 520.6687 | 379.1892 | 354.4376 | 133.342
594.4104 | 520.6671 | 379.4911 | 354.8289 | 133.7907
595.4104 | 520.8167 | 379.7672 | 355.1753 | 134.2479
596.4104 | 520.8468 | 380.093 | 355.4702 | 134.6997
597.4104 | 520.7924 | 380.3506 | 355.6864 | 135.1503
598.4104 | 520.7616 | 380.6484 | 355.9312 | 135.6164
599.4104 | 520.7635 | 380.9537 | 356.0589 | 136.0633
600.4104 | 520.7741 | 381.2627 | 356.5277 | 136.5225
601.4104 | 520.6879 | 381.5181 | 356.5272 | 136.9815
602.4104 | 520.6305 | 381.8436 | 356.9303 | 137.4456
603.4104 | 520.6125 | 382.1031 | 357.4336 | 137.8842
604.4104 | 520.4998 | 382.4171 | 357.7649 | 138.3396
605.4104 | 520.4645 | 382.686 | 357.7782 | 138.8033
606.4104 | 520.4383 | 383.0051 | 358.1238 | 139.2556
607.4104 | 520.2721 | 383.293 | 358.3452 | 139.7141
608.4104 | 520.2349 | 383.5713 | 358.5638 | 140.1659
609.4104 | 520.2075 | 383.845 | 358.7209 | 140.6201
610.4104 | 520.2101 | 384.142 | 359.0595 | 141.0746
611.4104 | 520.1782 | 384.4202 | 359.5472 | 141.5362
612.4104 | 520.0902 | 384.6675 | 359.9386 | 141.9936
613.4104 | 520.0394 | 384.9737 | 360.05 | 142.457
614.4104 | 520.1233 | 385.2159 | 360.0096 | 142.9143
615.4104 | 520.1859 | 385.5348 | 360.167 | 143.3773
616.4104 | 520.1639 | 385.8086 | 360.5365 | 143.8346
617.4104 | 520.0924 | 386.0674 | 361.0459 | 144.2888
618.4104 | 520.0932 | 386.3539 | 361.5507 | 144.7516
619.4104 | 520.0945 | 386.6275 | 361.9303 | 145.2207
620.4104 | 520.2244 | 386.9478 | 362.2746 | 145.6848
621.4104 | 520.2078 | 387.198 | 362.6859 | 146.1429
622.4104 | 520.2203 | 387.4499 | 362.9239 | 146.6026
623.4104 | 520.2764 | 387.7792 | 363.156 | 147.066
624.4104 | 520.2574 | 388.057 | 363.4655 | 147.5322
625.4104 | 520.2133 | 388.3235 | 363.6805 | 147.9898
626.4104 | 520.267 | 388.5915 | 364.0781 | 148.4554
627.4104 | 520.2884 | 388.8788 | 364.4301 | 148.9184
628.4104 | 520.3162 | 389.1179 | 364.7985 | 149.3844
629.4104 | 520.3676 | 389.402 | 365.1449 | 149.8461
630.4104 | 520.419 | 389.6543 | 365.4273 | 150.3166
631.4104 | 520.4005 | 389.9277 | 365.7098 | 150.7787
632.4104 | 520.4166 | 390.1887 | 365.7626 | 151.2355
633.4104 | 520.3358 | 390.4659 | 366.0099 | 151.7034
634.4104 | 520.3381 | 390.7137 | 366.4087 | 152.1707
635.4104 | 520.2334 | 391.0012 | 366.6671 | 152.6375
636.4104 | 520.1225 | 391.2634 | 367.0152 | 153.1036
637.4104 | 520.069 | 391.5143 | 367.0912 | 153.5723
638.4104 | 519.8422 | 391.7592 | 367.4047 | 154.0413
639.4104 | 519.8014 | 392.0277 | 367.5693 | 154.5151
640.4104 | 519.7961 | 392.3108 | 368.007 | 154.9909
641.4104 | 519.8249 | 392.5679 | 368.3824 | 155.4684
642.4104 | 519.7893 | 392.8214 | 368.6475 | 155.9303
643.4104 | 519.8299 | 393.0664 | 368.967 | 156.3946
644.4104 | 519.8669 | 393.3597 | 369.1926 | 156.871
645.4104 | 519.9383 | 393.5791 | 369.4887 | 157.3402
646.4104 | 520.0344 | 393.8673 | 369.7247 | 157.8066
647.4104 | 520.0276 | 394.111 | 369.7376 | 158.2806
648.4104 | 520.1097 | 394.3923 | 369.9131 | 158.7528
649.4104 | 520.1858 | 394.663 | 370.272 | 159.2191
650.4104 | 520.2172 | 394.9091 | 370.709 | 159.6901
651.4104 | 520.2439 | 395.1773 | 370.9243 | 160.1644
652.4104 | 520.2764 | 395.3932 | 371.0505 | 160.6297
653.4104 | 520.3429 | 395.6485 | 371.4359 | 161.1073
654.4104 | 520.3671 | 395.8977 | 371.7419 | 161.5757
655.4104 | 520.4447 | 396.1552 | 372.001 | 162.0432
656.4104 | 520.5351 | 396.412 | 372.3151 | 162.5195
657.4104 | 520.6068 | 396.5844 | 372.6416 | 162.9939
658.4104 | 520.6014 | 396.8748 | 372.9841 | 163.4675
659.4104 | 520.5595 | 397.1531 | 373.2968 | 163.9444
660.4104 | 520.4447 | 397.4225 | 373.6226 | 164.4241
661.4104 | 520.4649 | 397.6944 | 373.8421 | 164.8994
662.4104 | 520.505 | 397.9619 | 374.0919 | 165.3839
663.4104 | 520.4815 | 398.1967 | 374.3765 | 165.8518
664.4104 | 520.4409 | 398.4377 | 374.4929 | 166.3262
665.4104 | 520.4396 | 398.692 | 374.8467 | 166.797
666.4104 | 520.4278 | 398.929 | 375.1163 | 167.2812
667.4104 | 520.376 | 399.1792 | 375.3906 | 167.751
668.4104 | 520.2563 | 399.4252 | 375.6722 | 168.2289
669.4104 | 520.243 | 399.6347 | 375.7358 | 168.7074
670.4104 | 520.2299 | 399.8881 | 375.7304 | 169.1878
671.4104 | 520.1388 | 400.1708 | 376.1859 | 169.6649
672.4104 | 520.0593 | 400.3957 | 376.4697 | 170.1427
673.4104 | 520.0406 | 400.6367 | 376.4933 | 170.6235
674.4104 | 520.1152 | 400.8488 | 376.7343 | 171.1002
675.4104 | 520.094 | 401.1045 | 377.1445 | 171.5737
676.4104 | 520.0922 | 401.3324 | 377.3068 | 172.0586
677.4104 | 520.0917 | 401.5857 | 377.4586 | 172.5375
678.4104 | 520.125 | 401.8036 | 377.7343 | 173.0163
679.4104 | 520.2157 | 402.0481 | 378.1387 | 173.4981
680.4104 | 520.2273 | 402.2865 | 378.3861 | 173.9764
681.4104 | 520.2233 | 402.5515 | 378.5381 | 174.4757
682.4104 | 520.2721 | 402.823 | 378.8673 | 174.9566
683.4104 | 520.3134 | 403.0729 | 378.9389 | 175.4325
684.4104 | 520.3028 | 403.256 | 379.4357 | 175.9129
685.4104 | 520.2147 | 403.5272 | 379.856 | 176.4053
686.4104 | 520.1986 | 403.7311 | 380.1844 | 176.8796
687.4104 | 520.209 | 403.9758 | 380.3954 | 177.3646
688.426 | 520.0492 | 404.2019 | 380.5717 | 177.8475
689.4104 | 519.9349 | 404.4619 | 380.7086 | 178.326
690.4104 | 519.9618 | 404.6666 | 380.9395 | 178.8113
691.4104 | 519.8944 | 404.8786 | 381.2604 | 179.2872
692.4104 | 519.7842 | 405.1017 | 381.6193 | 179.7751
693.4104 | 519.7293 | 405.3315 | 381.8062 | 180.2674
694.4104 | 519.6284 | 405.575 | 382.1249 | 180.7516
695.4104 | 519.7201 | 405.8475 | 382.464 | 181.2364
696.4104 | 519.7722 | 406.0387 | 382.762 | 181.7157
697.4104 | 519.785 | 406.2812 | 382.944 | 182.196
698.4104 | 519.7941 | 406.5409 | 383.1654 | 182.6843
699.4104 | 519.9104 | 406.8034 | 383.5031 | 183.1748
700.4104 | 520.0041 | 407.0304 | 383.8737 | 183.6603
701.4104 | 520.0355 | 407.2771 | 384.1516 | 184.1561
702.4104 | 520.0919 | 407.528 | 384.391 | 184.6373
703.4104 | 520.1328 | 407.7818 | 384.5905 | 185.1226
704.4104 | 520.2274 | 408.0165 | 384.9038 | 185.6084
705.4104 | 520.2219 | 408.2459 | 385.1248 | 186.0969
706.4104 | 520.2049 | 408.4372 | 385.1977 | 186.5729
707.4104 | 520.2826 | 408.7064 | 385.4183 | 187.0611
708.4104 | 520.4041 | 408.9512 | 385.7829 | 187.542
709.4104 | 520.4116 | 409.1903 | 386.1059 | 188.0245
710.4104 | 520.4642 | 409.426 | 386.2009 | 188.5037
711.4104 | 520.4589 | 409.6682 | 386.4121 | 188.991
712.4104 | 520.4685 | 409.9081 | 386.5976 | 189.4747
713.4104 | 520.5448 | 410.1408 | 386.9026 | 189.9526
714.4104 | 520.5432 | 410.3453 | 387.0256 | 190.4295
715.4104 | 520.5237 | 410.6004 | 387.2048 | 190.9065
716.4104 | 520.4904 | 410.868 | 387.3405 | 191.3926
717.4104 | 520.5608 | 411.1101 | 387.7198 | 191.8645
718.4104 | 520.6155 | 411.3309 | 387.9455 | 192.3456
719.4104 | 520.6701 | 411.5533 | 388.2644 | 192.823
720.4104 | 520.7163 | 411.7892 | 388.5928 | 193.3
721.4104 | 520.67 | 411.9834 | 388.9059 | 193.7955
722.4104 | 520.6446 | 412.2623 | 388.9417 | 194.2586
723.4104 | 520.7632 | 412.4518 | 389.176 | 194.7364
724.4104 | 520.7198 | 412.7217 | 389.5941 | 195.2063
725.4104 | 520.7048 | 413.0004 | 389.6898 | 195.6839
726.4104 | 520.5878 | 413.2234 | 389.8107 | 196.1568
727.4104 | 520.6045 | 413.4469 | 390.2403 | 196.6299
728.4104 | 520.5573 | 413.7154 | 390.5361 | 197.0989
729.4104 | 520.5474 | 413.9325 | 390.755 | 197.5689
730.4104 | 520.6135 | 414.1553 | 391.1078 | 198.0434
731.4104 | 520.7296 | 414.4006 | 391.3778 | 198.519
732.4104 | 520.7326 | 414.6096 | 391.5464 | 198.9782
733.4104 | 520.652 | 414.8541 | 391.8471 | 199.4443
734.4104 | 520.6812 | 415.1085 | 392.1058 | 199.9102
735.4104 | 520.735 | 415.3648 | 392.3441 | 200.3821
736.4104 | 520.6825 | 415.613 | 392.4308 | 200.851
737.4104 | 520.7464 | 415.8104 | 392.6272 | 201.3118
738.4104 | 520.7833 | 416.0316 | 392.8094 | 201.7795
739.4104 | 520.7033 | 416.2855 | 393.0842 | 202.2459
740.4104 | 520.6232 | 416.5481 | 393.3745 | 202.7103
741.4104 | 520.5957 | 416.7146 | 393.5366 | 203.1612
742.4104 | 520.5617 | 416.9624 | 393.6774 | 203.6446
743.4104 | 520.4753 | 417.1606 | 393.9038 | 204.1025
744.4104 | 520.5791 | 417.3951 | 393.9135 | 204.5551
745.4104 | 520.5078 | 417.6098 | 394.196 | 205.0175
746.4104 | 520.5937 | 417.8685 | 394.5185 | 205.473
747.4104 | 520.5993 | 418.123 | 394.8757 | 205.9164
748.4104 | 520.5273 | 418.3371 | 394.9961 | 206.3744
749.4104 | 520.4168 | 418.5941 | 395.2537 | 206.8266
750.4104 | 520.4356 | 418.8372 | 395.5841 | 207.2784
751.4104 | 520.4468 | 419.0179 | 395.5665 | 207.7229
752.4104 | 520.3981 | 419.253 | 395.8819 | 208.1751
753.4104 | 520.3539 | 419.4716 | 396.2792 | 208.6147
754.4104 | 520.3745 | 419.6816 | 396.5708 | 209.0631
755.4104 | 520.4085 | 419.9043 | 396.8093 | 209.5127
756.4104 | 520.4255 | 420.1431 | 397.0279 | 209.9437
757.4104 | 520.3642 | 420.3666 | 397.2873 | 210.3838
758.4104 | 520.3537 | 420.5642 | 397.2528 | 210.8235
759.4104 | 520.2401 | 420.8226 | 397.5185 | 211.2573
760.4104 | 520.1987 | 421.0545 | 397.6668 | 211.6917
761.4104 | 520.2633 | 421.256 | 397.9549 | 212.126
762.4104 | 520.2904 | 421.4977 | 398.207 | 212.5646
763.4104 | 520.2511 | 421.7417 | 398.3518 | 212.9878
764.4104 | 520.232 | 421.9383 | 398.6662 | 213.4235
765.4104 | 520.2854 | 422.1352 | 398.7317 | 213.8495
766.4104 | 520.3246 | 422.3325 | 399.0359 | 214.2741
767.4104 | 520.3912 | 422.5589 | 399.3864 | 214.7024
768.4104 | 520.3258 | 422.7666 | 399.6938 | 215.1165
769.4104 | 520.1715 | 422.9655 | 399.8711 | 215.5357
770.4104 | 520.0594 | 423.1671 | 400.0265 | 215.9616
771.4104 | 520.1014 | 423.3982 | 400.2179 | 216.3758
772.4104 | 520.2157 | 423.615 | 400.3895 | 216.7864
773.4104 | 520.2117 | 423.8228 | 400.5487 | 217.203
774.4104 | 520.225 | 424.0178 | 400.8146 | 217.6169
775.4104 | 520.2468 | 424.2368 | 400.9928 | 218.0208
776.4104 | 520.3448 | 424.4619 | 401.2673 | 218.4247
777.4104 | 520.3283 | 424.6895 | 401.5506 | 218.8245
778.4104 | 520.2952 | 424.9168 | 401.7822 | 219.231
779.4104 | 520.3919 | 425.1127 | 401.8426 | 219.6401
780.4104 | 520.4606 | 425.3287 | 401.9939 | 220.0377
781.4104 | 520.5018 | 425.5229 | 402.1835 | 220.4345
782.4104 | 520.4978 | 425.7798 | 402.0554 | 220.8326
783.4104 | 520.5573 | 425.9918 | 402.3106 | 221.2349
784.4104 | 520.6546 | 426.1813 | 402.534 | 221.6379
785.4104 | 520.7749 | 426.4126 | 403.023 | 222.029
786.4104 | 520.843 | 426.5954 | 403.2018 | 222.4325
787.4104 | 520.8754 | 426.7616 | 403.3779 | 222.8249
788.4104 | 520.797 | 426.9874 | 403.653 | 223.2303
789.4104 | 520.6713 | 427.2306 | 403.755 | 223.6272
790.4104 | 520.6686 | 427.4201 | 404.0453 | 224.0252
791.4104 | 520.7342 | 427.6102 | 404.2288 | 224.4211
792.4104 | 520.6809 | 427.8303 | 404.2596 | 224.8141
793.4104 | 520.6978 | 428.0483 | 404.5775 | 225.2057
794.4104 | 520.5521 | 428.2553 | 404.8104 | 225.6059
795.4104 | 520.469 | 428.444 | 405.0727 | 225.996
796.4104 | 520.333 | 428.6377 | 405.2721 | 226.3896
797.4104 | 520.3009 | 428.8012 | 405.5186 | 226.7758
798.4104 | 520.1935 | 428.9839 | 405.4865 | 227.1619
799.4104 | 520.1446 | 429.1897 | 405.8121 | 227.5435
800.4104 | 520.1411 | 429.4023 | 406.1324 | 227.9296
801.4104 | 520.0494 | 429.5455 | 406.4362 | 228.3074
802.4104 | 519.9685 | 429.8115 | 406.423 | 228.684
803.4104 | 519.8936 | 430.0167 | 406.5835 | 229.0627
804.4104 | 519.8057 | 430.2105 | 406.797 | 229.4399
805.4104 | 519.8315 | 430.388 | 407.0575 | 229.8115
806.4104 | 519.921 | 430.597 | 407.1847 | 230.1766
807.4104 | 519.9681 | 430.815 | 407.4208 | 230.5441
808.4104 | 519.9879 | 430.9878 | 407.6552 | 230.9121
809.4104 | 519.9183 | 431.2043 | 407.8034 | 231.2749
810.4104 | 519.8843 | 431.394 | 408.0363 | 231.6437
811.4104 | 519.8805 | 431.591 | 408.1501 | 232.0079
812.4104 | 519.7975 | 431.8073 | 408.2984 | 232.3664
813.4104 | 519.9188 | 432.0397 | 408.629 | 232.7308
814.4104 | 520.0656 | 432.2494 | 408.9022 | 233.0954
815.4104 | 520.042 | 432.4456 | 409.1427 | 233.4475
816.4104 | 520.1147 | 432.6281 | 409.3691 | 233.8045
817.4104 | 520.2024 | 432.8345 | 409.381 | 234.1603
818.4104 | 520.2741 | 433.043 | 409.4019 | 234.5134
819.4104 | 520.2832 | 433.2344 | 409.4722 | 234.8645
820.4104 | 520.2971 | 433.4767 | 409.8699 | 235.2187
821.4104 | 520.3972 | 433.6657 | 409.9863 | 235.5674
822.4104 | 520.5353 | 433.834 | 410.2402 | 235.9204
823.4104 | 520.6007 | 434.01 | 410.4523 | 236.266
824.4104 | 520.6344 | 434.2349 | 410.614 | 236.6145
825.4104 | 520.6754 | 434.4185 | 410.7973 | 236.9564
826.4104 | 520.6242 | 434.6302 | 410.9444 | 237.3069
827.4104 | 520.625 | 434.8285 | 411.2354 | 237.6509
828.4104 | 520.6988 | 434.9228 | 411.4356 | 237.992
829.4104 | 520.6783 | 435.1612 | 411.6265 | 238.3448
830.4104 | 520.6362 | 435.3655 | 411.8646 | 238.6742
831.4104 | 520.6143 | 435.5355 | 412.0566 | 239.0165
832.4104 | 520.4353 | 435.6981 | 412.2502 | 239.35
833.4104 | 520.4353 | 435.8979 | 412.4606 | 239.6853
834.4104 | 520.5118 | 436.0791 | 412.5269 | 240.0241
835.4104 | 520.4461 | 436.2647 | 412.7621 | 240.3598
836.4104 | 520.4172 | 436.4851 | 412.9514 | 240.6954
837.4104 | 520.2854 | 436.6902 | 412.9696 | 241.0274
838.4104 | 520.2202 | 436.8592 | 413.1321 | 241.3608
839.4104 | 520.2978 | 437.0348 | 413.4264 | 241.6878
840.4104 | 520.422 | 437.1993 | 413.3946 | 242.023
841.4104 | 520.3072 | 437.4116 | 413.6834 | 242.3487
842.4104 | 520.2046 | 437.6179 | 413.7634 | 242.6833
843.4104 | 520.2133 | 437.8247 | 414.0423 | 243.0106
844.4104 | 520.2098 | 437.9834 | 414.2101 | 243.3414
845.4104 | 520.093 | 438.1445 | 414.1913 | 243.666
846.4104 | 519.9889 | 438.2927 | 414.1818 | 243.9792
847.4104 | 519.9981 | 438.4832 | 414.4132 | 244.304
848.4104 | 520.0002 | 438.6839 | 414.7816 | 244.6276
849.4104 | 519.9703 | 438.826 | 415.0786 | 244.9493
850.4104 | 519.9424 | 438.9453 | 415.2829 | 245.2759
851.4104 | 519.9321 | 439.1494 | 415.4389 | 245.5946
852.4104 | 519.8863 | 439.3659 | 415.6308 | 245.9047
853.4104 | 519.8007 | 439.538 | 415.8948 | 246.2207
854.4104 | 519.9403 | 439.6785 | 416.129 | 246.537
855.4104 | 520.0878 | 439.8634 | 416.2791 | 246.8574
856.4104 | 520.108 | 440.037 | 416.3247 | 247.1701
857.4104 | 520.2047 | 440.2008 | 416.5219 | 247.4827
858.4104 | 520.3001 | 440.4224 | 416.671 | 247.7928
859.4104 | 520.2743 | 440.6317 | 416.6115 | 248.1021
860.4104 | 520.356 | 440.7651 | 416.8518 | 248.4152
861.4104 | 520.3927 | 440.9738 | 417.1165 | 248.7191
862.4104 | 520.4686 | 441.0942 | 417.3373 | 249.0305
863.4104 | 520.4616 | 441.3137 | 417.5846 | 249.3382
864.4104 | 520.4464 | 441.5189 | 417.6405 | 249.6404
865.4104 | 520.3987 | 441.6212 | 417.9187 | 249.9411
866.4104 | 520.3337 | 441.8044 | 418.0598 | 250.2363
867.4104 | 520.3758 | 442.0222 | 418.1768 | 250.5415
868.4104 | 520.2872 | 442.1833 | 418.2016 | 250.8307
869.4104 | 520.3015 | 442.3818 | 418.4546 | 251.134
870.4104 | 520.4139 | 442.544 | 418.7678 | 251.4231
871.4104 | 520.3826 | 442.7108 | 418.9513 | 251.7176
872.4104 | 520.2788 | 442.8429 | 419.0876 | 252.0092
873.426 | 520.3048 | 443.0487 | 419.0802 | 252.3102
874.4729 | 520.2882 | 443.2107 | 419.2737 | 252.5986
875.426 | 520.3367 | 443.3493 | 419.4902 | 252.8702
876.426 | 520.3054 | 443.5529 | 419.2508 | 253.1425
877.426 | 520.281 | 443.7028 | 419.6352 | 253.4218
878.426 | 520.3286 | 443.8957 | 420.0141 | 253.6904
879.426 | 520.3604 | 444.0217 | 420.2204 | 253.9661
880.4104 | 520.3195 | 444.1385 | 420.278 | 254.2374
881.4104 | 520.2465 | 444.3318 | 420.5043 | 254.5192
882.4104 | 520.2376 | 444.4907 | 420.7328 | 254.8101
883.4104 | 520.1802 | 444.6549 | 420.714 | 255.1129
884.4104 | 520.0847 | 444.8397 | 420.7902 | 255.4198
885.4104 | 520.1525 | 444.9853 | 420.9986 | 255.7212
886.4104 | 520.2235 | 445.1926 | 421.283 | 256.0345
887.4104 | 520.3095 | 445.3329 | 421.5444 | 256.341
888.4104 | 520.3546 | 445.4955 | 421.7732 | 256.6516
889.4104 | 520.3705 | 445.6948 | 421.9356 | 256.9795
890.4104 | 520.3251 | 445.8258 | 422.1188 | 257.2909
891.4104 | 520.3782 | 445.9692 | 422.327 | 257.5966
892.4104 | 520.3581 | 446.1504 | 422.4856 | 257.9091
893.4104 | 520.3069 | 446.3523 | 422.7165 | 258.2149
894.4104 | 520.2662 | 446.5053 | 422.7928 | 258.5227
895.4104 | 520.2061 | 446.6173 | 422.9859 | 258.8223
896.4104 | 520.1444 | 446.7355 | 423.0821 | 259.1217
897.4104 | 520.1032 | 446.8819 | 423.1994 | 259.4186
898.4104 | 520.1645 | 447.0233 | 423.4324 | 259.7115
899.4104 | 520.2462 | 447.1473 | 423.6359 | 260.0119
900.4104 | 520.2687 | 447.3013 | 423.7512 | 260.3132
901.4104 | 520.2732 | 447.511 | 423.6268 | 260.602
902.4104 | 520.1941 | 447.6591 | 423.9095 | 260.893
903.4104 | 520.0738 | 447.7683 | 424.055 | 261.185
904.4104 | 519.9403 | 447.9313 | 424.1846 | 261.4688
905.4104 | 520.0094 | 448.0985 | 424.3612 | 261.7594
906.4104 | 519.9487 | 448.2339 | 424.637 | 262.0444
907.4104 | 519.9799 | 448.4137 | 424.83 | 262.3276
908.4104 | 519.9196 | 448.5629 | 424.9746 | 262.6074
909.4104 | 519.9138 | 448.6537 | 425.0425 | 262.8877
910.4104 | 519.866 | 448.8349 | 425.4125 | 263.1639
911.4104 | 519.8816 | 449.0593 | 425.4517 | 263.4464
912.4104 | 519.8273 | 449.166 | 425.5555 | 263.7197
913.4104 | 519.7782 | 449.29 | 425.7581 | 264.0129
914.4104 | 519.6735 | 449.4306 | 426.0357 | 264.2962
915.4104 | 519.7134 | 449.5239 | 426.2028 | 264.5777
916.4104 | 519.6931 | 449.7096 | 426.3039 | 264.8468
917.4104 | 519.6871 | 449.8853 | 426.4741 | 265.1263
918.4104 | 519.6963 | 449.9798 | 426.5681 | 265.414
919.4104 | 519.7265 | 450.1112 | 426.5112 | 265.6837
920.4104 | 519.6345 | 450.2654 | 426.5726 | 265.9712
921.4104 | 519.6825 | 450.3894 | 426.6626 | 266.2509
922.4104 | 519.6306 | 450.5616 | 426.7229 | 266.5342
923.4104 | 519.5966 | 450.6876 | 427.1247 | 266.8149
924.4104 | 519.5794 | 450.8299 | 427.4234 | 267.0896
925.4104 | 519.6867 | 450.98 | 427.6105 | 267.3724
926.4104 | 519.7343 | 451.0869 | 427.8061 | 267.6558
927.4104 | 519.7317 | 451.266 | 427.86 | 267.9381
928.4104 | 519.784 | 451.3998 | 427.9353 | 268.2252
929.4104 | 519.893 | 451.5502 | 428.1804 | 268.5034
930.4104 | 519.9226 | 451.6888 | 428.3267 | 268.7816
931.4104 | 519.9757 | 451.8482 | 428.2827 | 269.0668
932.4104 | 520.0191 | 452.0096 | 428.5142 | 269.3562
933.4104 | 520.0302 | 452.1356 | 428.738 | 269.6363
934.4104 | 519.9591 | 452.2587 | 428.8737 | 269.9186
935.4104 | 519.9382 | 452.4092 | 428.9506 | 270.2037
936.4104 | 520.086 | 452.4894 | 429.2355 | 270.4928
937.4104 | 520.0848 | 452.6092 | 429.401 | 270.7713
938.4104 | 520.0899 | 452.7594 | 429.5168 | 271.0603
939.4104 | 520.1869 | 452.9451 | 429.7576 | 271.3513
940.4104 | 520.2418 | 453.0122 | 429.9353 | 271.6354
941.4104 | 520.344 | 453.1507 | 430.0617 | 271.9096
942.4104 | 520.49 | 453.2944 | 430.174 | 272.1952
943.4104 | 520.6081 | 453.4218 | 430.2094 | 272.4732
944.4104 | 520.6783 | 453.5984 | 430.4175 | 272.754
945.4104 | 520.6781 | 453.764 | 430.5641 | 273.0477
946.4104 | 520.8046 | 453.915 | 430.7062 | 273.3387
947.4104 | 520.8203 | 454.0351 | 430.7939 | 273.6214
948.4104 | 520.799 | 454.1803 | 430.8552 | 273.909
949.4104 | 520.6765 | 454.3214 | 431.0684 | 274.1989
950.4104 | 520.6675 | 454.4596 | 431.0541 | 274.486
951.4104 | 520.7202 | 454.5714 | 431.2722 | 274.7896
952.4104 | 520.6747 | 454.6684 | 431.4194 | 275.0773
953.4104 | 520.6475 | 454.8 | 431.6233 | 275.3541
954.4104 | 520.5937 | 454.9006 | 431.7372 | 275.6492
955.4104 | 520.5165 | 455.0308 | 431.8449 | 275.9399
956.4104 | 520.5218 | 455.1437 | 432.0804 | 276.2234
957.4104 | 520.5112 | 455.3103 | 432.0965 | 276.5094
958.4104 | 520.4769 | 455.397 | 432.2711 | 276.8017
959.4104 | 520.3439 | 455.5241 | 432.3254 | 277.097
960.4104 | 520.1884 | 455.6687 | 432.5705 | 277.3818
961.4104 | 520.0692 | 455.7485 | 432.7231 | 277.6708
962.4104 | 519.9832 | 455.8397 | 432.8636 | 277.9713
963.4104 | 519.9762 | 456.0371 | 433.0623 | 278.2748
964.4104 | 520.0466 | 456.1543 | 433.2391 | 278.582
965.4104 | 520.0592 | 456.3054 | 433.325 | 278.9021
966.4104 | 519.97 | 456.3786 | 432.9937 | 279.208
967.4104 | 519.973 | 456.5431 | 433.0737 | 279.5235
968.4104 | 519.9946 | 456.6699 | 433.3369 | 279.8112
969.4104 | 519.9469 | 456.7878 | 433.5893 | 280.1249
970.4104 | 519.9822 | 456.9246 | 433.4465 | 280.4386
971.4104 | 519.9651 | 457.0897 | 433.4219 | 280.7641
972.4104 | 520.0808 | 457.1748 | 433.7133 | 281.0749
973.4104 | 520.1006 | 457.331 | 434.0094 | 281.3782
974.4104 | 520.1766 | 457.4202 | 434.1977 | 281.683
975.4104 | 520.2504 | 457.5119 | 434.4227 | 281.9764
976.4104 | 520.3726 | 457.6488 | 434.4314 | 282.255
977.4104 | 520.4224 | 457.7722 | 434.5542 | 282.5375
978.4104 | 520.3007 | 457.8261 | 434.7133 | 282.8049
979.4104 | 520.3198 | 457.9958 | 434.9235 | 283.0695
980.4104 | 520.4553 | 458.0752 | 434.8932 | 283.3417
981.4104 | 520.4646 | 458.1933 | 435.1597 | 283.6196
982.4104 | 520.3646 | 458.3376 | 435.2507 | 283.906
983.4104 | 520.298 | 458.4447 | 435.4456 | 284.1857
984.4104 | 520.372 | 458.5842 | 435.5051 | 284.4524
985.4104 | 520.4079 | 458.649 | 435.6373 | 284.7244
986.4104 | 520.3782 | 458.7472 | 435.7701 | 285.0059
987.4104 | 520.4027 | 458.7914 | 435.9115 | 285.2878
988.4104 | 520.388 | 458.9515 | 436.097 | 285.5615
989.4104 | 520.4548 | 459.061 | 436.2296 | 285.8433
990.4104 | 520.4883 | 459.166 | 436.2716 | 286.125
991.4104 | 520.5443 | 459.3363 | 436.2132 | 286.3958
992.4104 | 520.5539 | 459.4691 | 436.3055 | 286.6591
993.4104 | 520.5107 | 459.5644 | 436.5401 | 286.927
994.4104 | 520.4802 | 459.6924 | 436.7482 | 287.1869
995.4104 | 520.4935 | 459.8232 | 436.9979 | 287.4212
996.4104 | 520.3808 | 459.9036 | 437.138 | 287.6649
997.4104 | 520.3291 | 460.0458 | 437.1804 | 287.8978
998.4104 | 520.3514 | 460.1418 | 437.2317 | 288.1271
999.4104 | 520.3514 | 460.2733 | 437.3546 | 288.3543
1000.4104 | 520.2636 | 460.3623 | 437.41 | 288.568
1001.4104 | 520.2341 | 460.4628 | 437.5389 | 288.7967
1002.4104 | 520.1873 | 460.5957 | 437.7414 | 289.0179
1003.4104 | 520.2778 | 460.7335 | 437.8189 | 289.2386
1004.4104 | 520.2205 | 460.8134 | 437.9327 | 289.4628
1005.4104 | 520.1526 | 460.9067 | 438.0614 | 289.691
1006.4104 | 520.1074 | 461.0891 | 438.349 | 289.9257
1007.4104 | 520.1599 | 461.1758 | 438.4137 | 290.1713
1008.4104 | 520.0197 | 461.2544 | 438.5163 | 290.3813
1009.4104 | 520.1264 | 461.391 | 438.6378 | 290.5998
1010.4104 | 520.1693 | 461.4641 | 438.56 | 290.8262
1011.4104 | 520.143 | 461.5959 | 438.61 | 291.057
1012.4104 | 520.0389 | 461.6754 | 438.7559 | 291.2788
1013.4104 | 520.16 | 461.7673 | 438.9005 | 291.5651
1014.4104 | 520.2174 | 461.8894 | 439.0512 | 291.778
1015.4104 | 520.1881 | 461.9894 | 439.1915 | 291.9923
1016.4104 | 520.1554 | 462.0945 | 439.1085 | 292.2025
1017.4104 | 520.1623 | 462.1761 | 439.1929 | 292.4213
1018.4104 | 520.2439 | 462.3032 | 439.2145 | 292.6446
1019.4104 | 520.3038 | 462.4256 | 439.2375 | 292.8635
1020.4104 | 520.3427 | 462.4962 | 439.0577 | 293.0542
1021.4104 | 520.2723 | 462.6111 | 438.9756 | 293.26
1022.4104 | 520.2094 | 462.6916 | 438.9306 | 293.4534
1023.4104 | 520.166 | 462.7979 | 439.0973 | 293.6518
1024.4104 | 520.2499 | 462.9193 | 439.0923 | 293.8424
1025.4104 | 520.2454 | 462.998 | 439.5513 | 294.0331
1026.4104 | 520.2501 | 463.1228 | 439.8318 | 294.224
1027.4104 | 520.246 | 463.2505 | 440.0652 | 294.4192
1028.4104 | 520.152 | 463.3608 | 440.2464 | 294.6186
1029.4104 | 520.0867 | 463.4925 | 440.4421 | 294.8141
1030.4104 | 520.0947 | 463.5995 | 440.5744 | 295.0039
1031.4104 | 520.0377 | 463.7207 | 440.8264 | 295.211
1032.4104 | 519.8648 | 463.7803 | 440.9553 | 295.4058
1033.4104 | 519.8697 | 463.903 | 440.9922 | 295.6079
1034.4104 | 519.8374 | 463.9841 | 440.9665 | 295.8117
1035.4104 | 519.95 | 464.0422 | 441.1976 | 296.0115
1036.4104 | 519.9832 | 464.158 | 441.2028 | 296.2437
1037.4104 | 520.0143 | 464.2493 | 441.4048 | 296.4542
1038.4104 | 520.106 | 464.3677 | 441.5066 | 296.6777
1039.4104 | 520.1691 | 464.4246 | 441.4521 | 296.9057
1040.4104 | 520.0808 | 464.5061 | 441.1937 | 297.1266
1041.4104 | 520.0547 | 464.6005 | 441.5659 | 297.339
1042.4104 | 520.0664 | 464.713 | 441.7751 | 297.5829
1043.4104 | 520.1505 | 464.8162 | 441.9295 | 297.8006
1044.4104 | 520.1678 | 464.9241 | 442.0228 | 298.016
1045.4104 | 520.2025 | 464.9956 | 441.7789 | 298.3319
1046.4104 | 520.2798 | 465.0876 | 441.9388 | 298.565
1047.4104 | 520.3714 | 465.2049 | 442.1976 | 298.7813
1048.4104 | 520.443 | 465.2949 | 442.2838 | 299.015
1049.4104 | 520.3827 | 465.4015 | 442.5723 | 299.3379
1050.4104 | 520.4512 | 465.4787 | 442.6678 | 299.6062
1051.4104 | 520.3643 | 465.587 | 442.7952 | 299.8554
1052.4104 | 520.1916 | 465.6884 | 442.851 | 300.0881
1053.4104 | 520.269 | 465.7298 | 442.739 | 300.3206
1054.4104 | 520.2889 | 465.8453 | 442.9872 | 300.5677
1055.4104 | 520.2364 | 465.8965 | 443.2517 | 300.815
1056.4104 | 520.2036 | 466.0308 | 443.3726 | 301.0587
1057.4104 | 520.1958 | 466.1488 | 443.4783 | 301.3056
1058.4104 | 520.1374 | 466.1387 | 443.6857 | 301.562
1059.4104 | 520.0832 | 466.289 | 443.8291 | 301.8104
1060.4104 | 519.9967 | 466.3821 | 443.8098 | 302.0693
1061.4104 | 519.9124 | 466.4589 | 443.9594 | 302.3363
1062.4104 | 519.8481 | 466.5458 | 444.0129 | 302.6436
1063.4104 | 519.9532 | 466.6745 | 444.1308 | 302.9229
1064.4104 | 519.8738 | 466.7532 | 444.2413 | 303.246
1065.4104 | 519.8626 | 466.87 | 444.2872 | 303.532
1066.4104 | 519.9434 | 466.9613 | 444.4997 | 303.8068
1067.4104 | 519.8542 | 467.0404 | 444.4812 | 304.0844
1068.4104 | 519.7833 | 467.1447 | 444.6505 | 304.397
1069.4104 | 519.7151 | 467.167 | 444.6042 | 304.7609
1070.4104 | 519.7324 | 467.2436 | 444.7446 | 305.0584
1071.4104 | 519.7747 | 467.3488 | 444.9294 | 305.3498
1072.4104 | 519.9212 | 467.397 | 445.0385 | 305.6346
1073.4104 | 519.9267 | 467.5275 | 445.2118 | 305.9169
1074.4104 | 519.9269 | 467.6573 | 445.3037 | 306.2031
1075.4104 | 520.0053 | 467.7192 | 445.2387 | 306.4804
1076.4104 | 520.052 | 467.7951 | 445.2282 | 306.7427
1077.4104 | 520.1083 | 467.9031 | 445.139 | 307.0224
1078.4104 | 520.0809 | 467.9655 | 445.5081 | 307.294
1079.4104 | 520.021 | 468.0055 | 445.6205 | 307.5727
1080.4104 | 520.0212 | 468.0642 | 445.7661 | 307.8449
1081.4104 | 520.045 | 468.1503 | 445.9789 | 308.1968
1082.4104 | 520.0283 | 468.2719 | 446.097 | 308.4769
1083.4104 | 520.0372 | 468.4002 | 445.9897 | 308.7637
1084.4104 | 519.9644 | 468.475 | 446.0866 | 309.0488
1085.4104 | 519.9107 | 468.5639 | 446.2333 | 309.3799
1086.4104 | 519.9152 | 468.6517 | 446.4181 | 309.7312
1087.4104 | 519.991 | 468.6949 | 446.6703 | 310.0385
1088.4104 | 519.9712 | 468.8275 | 446.6639 | 310.4366
1089.4104 | 520.0947 | 468.8521 | 446.6961 | 310.6856
1090.4104 | 520.0772 | 468.956 | 446.8095 | 310.9705
1091.4104 | 520.1069 | 469.0653 | 446.5402 | 311.2493
1092.4104 | 520.1691 | 469.1916 | 446.4572 | 311.5485
1093.4104 | 520.2481 | 469.311 | 446.8321 | 311.8491
1094.4104 | 520.274 | 469.3724 | 446.7309 | 312.1347
1095.4104 | 520.2566 | 469.4776 | 447.0758 | 312.4435
1096.4104 | 520.2878 | 469.5057 | 447.2928 | 312.8147
1097.4104 | 520.2745 | 469.5806 | 447.0955 | 313.0897
1098.4104 | 520.3041 | 469.7006 | 447.395 | 313.3985
1099.4104 | 520.3567 | 469.8112 | 447.6292 | 313.6944
1100.4104 | 520.3829 | 469.9155 | 447.7109 | 313.9863
1101.4104 | 520.4952 | 469.9886 | 447.8586 | 314.2821
1102.4104 | 520.5274 | 470.0486 | 448.0016 | 314.5815
1103.4104 | 520.5 | 470.1509 | 448.1322 | 314.8935
1104.4104 | 520.4194 | 470.3016 | 448.2492 | 315.1936
1105.4104 | 520.3262 | 470.3413 | 448.2499 | 315.489
1106.4104 | 520.2349 | 470.4092 | 448.436 | 315.8022
1107.4104 | 520.1887 | 470.4928 | 448.5191 | 316.1434
1108.4104 | 520.1125 | 470.5786 | 448.452 | 316.4705
1109.4104 | 520.0326 | 470.6453 | 448.2778 | 316.7878
1110.4104 | 519.9474 | 470.7205 | 448.5799 | 317.1284
1111.4104 | 519.9954 | 470.8244 | 448.6316 | 317.4537
1112.4104 | 520.0297 | 470.8569 | 448.7053 | 317.8083
1113.4104 | 520.1146 | 470.9661 | 448.8402 | 318.127
1114.4104 | 520.2015 | 471.0242 | 448.9338 | 318.4948
1115.4104 | 520.1848 | 471.1138 | 449.0921 | 318.8071
1116.4104 | 520.1824 | 471.2207 | 449.1526 | 319.2137
1117.4104 | 520.1306 | 471.317 | 449.3358 | 319.5163
1118.4104 | 520.156 | 471.4146 | 449.5105 | 319.8358
1119.4104 | 520.3138 | 471.5129 | 449.5708 | 320.1907
1120.4104 | 520.3641 | 471.58 | 449.5605 | 320.5035
1121.4104 | 520.4093 | 471.7132 | 449.4667 | 320.8308
1122.4104 | 520.4232 | 471.7765 | 449.7174 | 321.1688
1123.4104 | 520.4394 | 471.766 | 449.9624 | 321.517
1124.4104 | 520.4511 | 471.8678 | 449.9021 | 321.8697
1125.4104 | 520.4492 | 471.9593 | 449.8457 | 322.2064
1126.4104 | 520.5204 | 472.0568 | 450.143 | 322.5674
1127.4104 | 520.4929 | 472.1556 | 450.3065 | 322.9061
1128.4104 | 520.466 | 472.2618 | 450.2567 | 323.2538
1129.4104 | 520.4544 | 472.3399 | 450.451 | 323.6012
1130.4104 | 520.5067 | 472.4645 | 450.5814 | 323.9378
1131.4104 | 520.4222 | 472.5467 | 450.8664 | 324.2863
1132.4104 | 520.4372 | 472.6409 | 450.9411 | 324.6672
1133.4104 | 520.4814 | 472.7323 | 451.0249 | 325.0069
1134.4104 | 520.4415 | 472.8202 | 451.2369 | 325.3478
1135.4104 | 520.3871 | 472.9017 | 451.3875 | 325.6876
1136.4104 | 520.3655 | 472.9662 | 451.2598 | 326.0564
1137.4104 | 520.3617 | 473.0337 | 451.3732 | 326.4235
1138.4104 | 520.4857 | 473.1281 | 451.4523 | 326.7945
1139.4104 | 520.4557 | 473.2093 | 451.5497 | 327.1457
1140.4104 | 520.4215 | 473.2881 | 451.6343 | 327.5906
1141.4104 | 520.3602 | 473.4147 | 451.7167 | 327.9669
1142.4104 | 520.345 | 473.5183 | 451.8779 | 328.3406
1143.4104 | 520.2892 | 473.558 | 452.057 | 328.6922
1144.4104 | 520.2865 | 473.6278 | 451.9849 | 329.0698
1145.4104 | 520.2436 | 473.7602 | 452.1845 | 329.4296
1146.4104 | 520.2592 | 473.7503 | 452.0413 | 329.7992
1147.4104 | 520.289 | 473.8437 | 452.057 | 330.1783
1148.4104 | 520.3969 | 473.899 | 452.4555 | 330.5804
1149.4104 | 520.3594 | 473.9844 | 452.5402 | 330.9776
1150.4104 | 520.367 | 474.1099 | 452.6455 | 331.3756
1151.4104 | 520.3363 | 474.2196 | 452.6815 | 331.7331
1152.4104 | 520.2882 | 474.2934 | 452.6661 | 332.0829
1153.4104 | 520.2557 | 474.3581 | 452.7635 | 332.4587
1154.4104 | 520.2234 | 474.4332 | 452.8773 | 332.8937
1155.4104 | 520.1234 | 474.4545 | 452.8581 | 333.258
1156.4104 | 520.1381 | 474.5686 | 452.9277 | 333.627
1157.4104 | 520.1928 | 474.679 | 453.109 | 333.9939
1158.4104 | 520.197 | 474.7699 | 453.1492 | 334.3953
1159.4104 | 520.1608 | 474.8476 | 453.2125 | 334.818
1160.4104 | 520.1214 | 474.9522 | 453.3122 | 335.1788
1161.4104 | 520.1177 | 475.0828 | 453.5118 | 335.5502
1162.4104 | 520.0477 | 475.1301 | 453.6341 | 335.9194
1163.4104 | 520.1433 | 475.1594 | 453.6584 | 336.2952
1164.4104 | 520.1888 | 475.2355 | 453.7587 | 336.6827
1165.4104 | 520.1907 | 475.3192 | 453.8253 | 337.0682
1166.4104 | 520.2046 | 475.4321 | 454.0739 | 337.4534
1167.4104 | 520.2201 | 475.5176 | 454.1403 | 337.8493
1168.4104 | 520.3601 | 475.5841 | 454.2493 | 338.2714
1169.4104 | 520.545 | 475.6989 | 454.0387 | 338.6344
1170.4104 | 520.6551 | 475.7838 | 454.2166 | 339.0023
1171.4104 | 520.6543 | 475.8644 | 454.3059 | 339.4092
1172.4104 | 520.5123 | 475.9063 | 454.2289 | 339.7898
1173.4104 | 520.4027 | 476.0252 | 454.3875 | 340.1882
1174.4104 | 520.3843 | 476.1153 | 454.5403 | 340.5693
1175.4104 | 520.1967 | 476.2022 | 454.5823 | 340.9589
1176.4104 | 520.1984 | 476.2608 | 454.5186 | 341.3436
1177.4104 | 520.1928 | 476.3849 | 454.5484 | 341.7445
1178.4104 | 520.0949 | 476.4646 | 454.7424 | 342.1142
1179.4104 | 520.014 | 476.5467 | 454.9195 | 342.508
1180.4104 | 519.9344 | 476.647 | 454.8954 | 342.9021
1181.4104 | 519.9556 | 476.6748 | 454.8049 | 343.2883
1182.4104 | 519.9319 | 476.8073 | 454.9871 | 343.6906
1183.4104 | 519.9583 | 476.8718 | 455.0384 | 344.0779
1184.4104 | 519.9085 | 476.8907 | 455.0534 | 344.4723
1185.4104 | 519.8983 | 477.0158 | 455.2547 | 344.8581
1186.4104 | 519.9495 | 477.1148 | 455.2662 | 345.2537
1187.4104 | 519.9394 | 477.1465 | 455.521 | 345.64
1188.4104 | 519.9381 | 477.2429 | 455.6965 | 346.0227
1189.4104 | 520.104 | 477.349 | 455.7337 | 346.4185
1190.4104 | 520.2102 | 477.4284 | 455.8042 | 346.8007
1191.4104 | 520.3086 | 477.5392 | 455.9072 | 347.1814
1192.4104 | 520.2706 | 477.5988 | 455.7851 | 347.5505
1193.4104 | 520.2568 | 477.6559 | 456.031 | 347.9067
1194.4104 | 520.3027 | 477.7861 | 455.8643 | 348.2732
1195.4104 | 520.2442 | 477.8482 | 455.9337 | 348.6374
1196.4104 | 520.1517 | 477.934 | 456.0881 | 348.9993
1197.4104 | 520.1057 | 477.9744 | 456.2044 | 349.3627
1198.4104 | 520.1598 | 478.0336 | 456.3503 | 349.7046
1199.4104 | 520.2673 | 478.1506 | 456.4823 | 350.063
1200.4104 | 520.3002 | 478.1256 | 456.381 | 350.4158
1201.4104 | 520.2733 | 478.2751 | 456.515 | 350.7402
1202.4104 | 520.3148 | 478.3725 | 456.7748 | 351.0932
1203.4104 | 520.3577 | 478.4487 | 456.8912 | 351.4366
1204.4104 | 520.4377 | 478.504 | 456.7384 | 351.7749
1205.4104 | 520.5115 | 478.6667 | 456.819 | 352.1984
1206.4104 | 520.5653 | 478.7402 | 456.9064 | 352.5493
1207.4104 | 520.6884 | 478.8465 | 456.984 | 352.8871
1208.4104 | 520.6536 | 478.9614 | 457.2079 | 353.2164
1209.4104 | 520.5624 | 478.9945 | 457.1069 | 353.5449
1210.4104 | 520.4428 | 479.1027 | 457.2333 | 353.8794
1211.4104 | 520.4307 | 479.1735 | 457.2588 | 354.1877
1212.4104 | 520.5454 | 479.2476 | 457.4889 | 354.5011
1213.4104 | 520.5356 | 479.3623 | 457.5209 | 354.9191
1214.4104 | 520.5555 | 479.4397 | 457.2512 | 355.266
1215.4104 | 520.4957 | 479.5074 | 457.5735 | 355.6132
1216.4104 | 520.4814 | 479.5874 | 457.7801 | 355.9675
1217.4104 | 520.4917 | 479.7021 | 457.917 | 356.3122
1218.4104 | 520.4498 | 479.7928 | 457.9638 | 356.6451
1219.4104 | 520.3272 | 479.9019 | 458.0717 | 356.9946
1220.4104 | 520.2935 | 480.0107 | 458.1374 | 357.3172
1221.4104 | 520.3406 | 480.0681 | 458.1333 | 357.641
1222.4104 | 520.4024 | 480.089 | 458.0255 | 357.958
1223.4104 | 520.4476 | 480.1579 | 458.2346 | 358.273
1224.4104 | 520.5892 | 480.1842 | 458.3878 | 358.5828
1225.4104 | 520.6549 | 480.3173 | 458.4932 | 358.8913
1226.4104 | 520.6834 | 480.4209 | 458.5675 | 359.1976
1227.4104 | 520.5905 | 480.5979 | 458.6707 | 359.5287
1228.4104 | 520.5811 | 480.6372 | 458.7282 | 360.1499
1229.4104 | 520.6507 | 480.6943 | 458.8219 | 360.4573
1230.4104 | 520.6106 | 480.7498 | 458.9032 | 360.7585
1231.4104 | 520.6573 | 480.8042 | 458.8499 | 361.0501
1232.4104 | 520.7089 | 480.8997 | 458.8058 | 361.3466
1233.4104 | 520.6132 | 481.0278 | 458.9246 | 361.6573
1234.4104 | 520.5236 | 481.1143 | 459.1148 | 361.9537
1235.4104 | 520.5124 | 481.1437 | 459.2886 | 362.2683
1236.4104 | 520.4646 | 481.1708 | 459.3314 | 362.5782
1237.4104 | 520.5387 | 481.277 | 459.3075 | 362.8667
1238.4104 | 520.5162 | 481.3465 | 459.3482 | 363.1589
1239.4104 | 520.4596 | 481.3258 | 459.3257 | 363.4617
1240.4104 | 520.4712 | 481.4167 | 459.4233 | 363.7673
1241.4104 | 520.435 | 481.5515 | 459.6033 | 364.0669
1242.4104 | 520.4167 | 481.6291 | 459.6505 | 364.3152
1243.4104 | 520.3103 | 481.7608 | 459.7548 | 364.5803
1244.4104 | 520.2413 | 481.8698 | 459.7727 | 364.8468
1245.4104 | 520.2613 | 481.9234 | 459.9137 | 365.1039
1246.4104 | 520.3594 | 481.9826 | 459.774 | 365.3826
1247.4104 | 520.358 | 482.0741 | 459.703 | 365.6545
1248.4104 | 520.3447 | 482.1717 | 459.7344 | 365.9669
1249.4104 | 520.4151 | 482.32 | 459.9353 | 366.2894
1250.4104 | 520.4938 | 482.3933 | 460.1092 | 366.5559
1251.4104 | 520.5166 | 482.4648 | 460.1231 | 366.8237
1252.4104 | 520.5259 | 482.5914 | 460.2199 | 367.0786
1253.4104 | 520.5958 | 482.7028 | 460.3336 | 367.3409
1254.4104 | 520.6598 | 482.8122 | 460.4834 | 367.6009
1255.4104 | 520.7415 | 482.8876 | 460.5762 | 367.8811
1256.4104 | 520.6815 | 482.9753 | 460.7472 | 368.1411
1257.4104 | 520.6358 | 482.9854 | 460.714 | 368.3923
1258.4104 | 520.7407 | 483.1288 | 460.7701 | 368.647
1259.4104 | 520.7144 | 483.2241 | 460.9903 | 368.8934
1260.4104 | 520.6729 | 483.3219 | 461.0485 | 369.1485
1261.4104 | 520.6244 | 483.4001 | 461.0629 | 369.3995
1262.4104 | 520.6675 | 483.5097 | 461.2062 | 369.6609
1263.4104 | 520.6702 | 483.5939 | 461.381 | 369.9087
1264.4104 | 520.6635 | 483.597 | 461.4391 | 370.1443
1265.4104 | 520.5527 | 483.7118 | 461.5224 | 370.3969
1266.4104 | 520.4324 | 483.8002 | 461.6534 | 370.5937
1267.4104 | 520.4642 | 483.9037 | 461.6643 | 370.8796
1268.4104 | 520.4502 | 484.0159 | 461.7099 | 371.1193
1269.4104 | 520.3856 | 484.0459 | 461.4166 | 371.346
1270.4104 | 520.3534 | 484.1947 | 461.6894 | 371.575
1271.4104 | 520.3534 | 484.1903 | 461.5666 | 371.8039
1272.4104 | 520.3478 | 484.2918 | 461.7511 | 372.029
1273.4104 | 520.3464 | 484.4457 | 461.7906 | 372.2505
1274.4104 | 520.3947 | 484.4884 | 461.916 | 372.4745
1275.4104 | 520.2955 | 484.5716 | 461.999 | 372.7024
1276.4104 | 520.3301 | 484.7065 | 462.1408 | 372.9214
1277.4104 | 520.3611 | 484.8309 | 462.1465 | 373.1108
1278.4104 | 520.4015 | 484.879 | 462.2063 | 373.3129
1279.4104 | 520.5016 | 484.9336 | 462.0732 | 373.5189
1280.4104 | 520.589 | 485.0041 | 462.183 | 373.6556
1281.4104 | 520.6592 | 485.0853 | 462.2521 | 373.8573
1282.4104 | 520.7143 | 485.261 | 462.2933 | 374.0648
1283.4104 | 520.7799 | 485.4018 | 462.3071 | 374.2986
1284.4104 | 520.7957 | 485.4234 | 462.4594 | 374.4901
1285.4104 | 520.9044 | 485.5502 | 462.2349 | 374.6912
1286.4104 | 521.041 | 485.7577 | 462.4635 | 374.8856
1287.4104 | 521.0818 | 485.8549 | 462.5578 | 375.0638
1288.4104 | 521.0851 | 485.9746 | 462.5699 | 375.2615
1289.4104 | 521.143 | 486.1108 | 462.7502 | 375.4609
1290.4104 | 521.123 | 486.1906 | 462.8099 | 375.6578
1291.4104 | 521.0655 | 486.2552 | 463.0162 | 375.8413
1292.4104 | 521.1077 | 486.374 | 463.0855 | 376.0248
1293.4104 | 521.0659 | 486.4809 | 463.2616 | 376.2192
1294.4104 | 521.093 | 486.5211 | 463.3014 | 376.4073
1295.4104 | 521.0436 | 486.6859 | 463.4718 | 376.5939
1296.4104 | 521.0096 | 486.7327 | 463.4482 | 376.7801
1297.4104 | 520.9772 | 486.7284 | 463.5534 | 377.0357
1298.4104 | 521.0631 | 486.8693 | 463.5206 | 377.2323
1299.4104 | 521.1199 | 487.0192 | 463.5865 | 377.4113
1300.4104 | 521.0446 | 487.1898 | 463.5433 | 377.5983
1301.4104 | 520.979 | 487.2698 | 463.6697 | 377.7679
1302.4104 | 520.9515 | 487.407 | 463.7015 | 377.9418
1303.4104 | 520.8601 | 487.5099 | 463.9152 | 378.1211
1304.4104 | 520.8161 | 487.6699 | 463.9665 | 378.3017
1305.4104 | 520.796 | 487.7535 | 464.0639 | 378.4756
1306.4104 | 520.8499 | 487.8471 | 463.9852 | 378.6583
1307.4104 | 520.9027 | 487.9385 | 463.824 | 378.8354
1308.4104 | 520.9075 | 488.0563 | 464.0531 | 379.0121
1309.4104 | 520.865 | 488.1863 | 464.2583 | 379.1755
1310.4104 | 520.9723 | 488.3495 | 464.3741 | 379.3528
1311.4104 | 520.9794 | 488.5063 | 464.195 | 379.5206
1312.4104 | 520.9055 | 488.6104 | 464.2712 | 379.6626
1313.4104 | 521.0491 | 488.7123 | 464.3959 | 379.8255
1314.4104 | 521.0817 | 488.8104 | 464.2823 | 379.9908
1315.4104 | 521.016 | 488.8948 | 464.4208 | 380.1617
1316.4104 | 520.9213 | 489.0702 | 464.6678 | 380.3247
1317.4104 | 520.7963 | 489.0214 | 464.7434 | 380.4871
1318.4104 | 520.6972 | 489.1734 | 464.5872 | 380.6412
1319.4104 | 520.7157 | 489.3006 | 464.6412 | 380.8083
1320.4104 | 520.8341 | 489.392 | 464.6056 | 380.9708
1321.4104 | 520.9036 | 489.4662 | 464.7451 | 381.1311
1322.4104 | 520.9655 | 489.5968 | 464.983 | 381.3076
1323.4104 | 520.9131 | 489.7141 | 465.1351 | 381.4672
1324.4104 | 520.8871 | 489.7913 | 465.2683 | 381.6252
1325.4104 | 520.8994 | 489.8857 | 465.4515 | 381.7925
1326.4104 | 520.9087 | 490.0548 | 465.2755 | 381.9394
1327.4104 | 520.9685 | 490.1882 | 465.244 | 382.1052
1328.4104 | 520.966 | 490.2962 | 465.4581 | 382.2696
1329.4104 | 520.9132 | 490.4103 | 465.428 | 382.4097
1330.4104 | 520.8111 | 490.5287 | 465.5228 | 382.6259
1331.4104 | 520.7213 | 490.6383 | 465.6831 | 382.7983
1332.4104 | 520.6068 | 490.7099 | 465.6985 | 382.9605
1333.4104 | 520.615 | 490.8211 | 465.6363 | 383.135
1334.4104 | 520.5533 | 490.8866 | 465.7898 | 383.3064
1335.4104 | 520.534 | 491.0032 | 465.9586 | 383.4757
1336.4104 | 520.4776 | 491.0767 | 466.0238 | 383.621
1337.4104 | 520.4133 | 491.0958 | 466.1095 | 383.778
1338.4104 | 520.3506 | 491.2312 | 465.9966 | 383.9531
1339.4104 | 520.2753 | 491.3396 | 465.5749 | 384.114
1340.4104 | 520.279 | 491.4284 | 465.8314 | 384.2821
1341.4104 | 520.3171 | 491.4278 | 465.9787 | 384.4281
1342.4104 | 520.3156 | 491.5089 | 465.9275 | 384.5986
1343.4104 | 520.2767 | 491.5967 | 466.0599 | 384.7653
1344.4104 | 520.2006 | 491.5258 | 466.2947 | 384.9279
1345.4104 | 520.1278 | 491.634 | 466.3389 | 385.0894
1346.4104 | 520.0558 | 491.7073 | 466.4402 | 385.2385
1347.4104 | 519.9723 | 491.8688 | 466.4545 | 385.4045
1348.4104 | 519.9692 | 492.005 | 466.3998 | 385.5585
1349.4104 | 519.8633 | 492.0444 | 466.5528 | 385.7231
1350.4104 | 519.918 | 492.0681 | 466.69 | 385.8792
1351.4104 | 519.9469 | 492.1803 | 466.8226 | 386.0476
1352.4104 | 519.9572 | 492.2242 | 466.8688 | 386.2059
1353.4104 | 520.1306 | 492.3391 | 466.7835 | 386.3658
1354.4104 | 520.155 | 492.4151 | 466.9167 | 386.5217
1355.4104 | 520.2433 | 492.4602 | 467.007 | 386.6798
1356.4104 | 520.2177 | 492.4912 | 467.1425 | 386.8402
1357.4104 | 520.104 | 492.4993 | 467.2135 | 386.9991
1358.4104 | 520.1391 | 492.5337 | 467.2309 | 387.1649
1359.4104 | 520.2524 | 492.6686 | 467.3202 | 387.3223
1360.4104 | 520.4133 | 492.7359 | 467.0763 | 387.4918
1361.4104 | 520.4432 | 492.8167 | 467.0288 | 387.6783
1362.4104 | 520.3443 | 492.8314 | 467.1933 | 387.8363
1363.4104 | 520.368 | 492.928 | 467.3984 | 387.986
1364.4104 | 520.3532 | 493.0055 | 467.5215 | 388.1495
1365.4104 | 520.4565 | 493.0522 | 467.6257 | 388.3049
1366.4104 | 520.4642 | 493.1607 | 467.5791 | 388.4594
1367.4104 | 520.4686 | 493.2542 | 467.6668 | 388.6369
1368.4104 | 520.4838 | 493.3623 | 467.7367 | 388.8045
1369.4104 | 520.5082 | 493.4583 | 467.8029 | 388.9661
1370.4104 | 520.509 | 493.4833 | 467.7961 | 389.144
1371.4104 | 520.4623 | 493.5372 | 467.9139 | 389.303
1372.4104 | 520.4316 | 493.5536 | 467.9305 | 389.4735
1373.4104 | 520.4742 | 493.6682 | 467.933 | 389.6324
1374.4104 | 520.4942 | 493.7423 | 467.8104 | 389.7927
1375.4104 | 520.4473 | 493.7766 | 467.959 | 389.9434
1376.4104 | 520.4394 | 493.7653 | 468.101 | 390.1031
1377.4104 | 520.4206 | 493.8601 | 468.2686 | 390.2714
1378.4104 | 520.458 | 493.9253 | 468.3787 | 390.4333
1379.4104 | 520.451 | 494.0202 | 468.4417 | 390.6018
1380.4104 | 520.2483 | 494.0971 | 468.4983 | 390.7578
1381.4104 | 520.1747 | 494.1495 | 468.5624 | 390.9195
1382.4104 | 520.2045 | 494.216 | 468.607 | 391.069
1383.4104 | 520.1762 | 494.2808 | 468.6397 | 391.2185
1384.4104 | 520.17 | 494.3718 | 468.6364 | 391.3764
1385.4104 | 520.1616 | 494.3542 | 468.6165 | 391.5324
1386.4104 | 520.2259 | 494.4542 | 468.6955 | 391.6937
1387.4104 | 520.2551 | 494.5388 | 468.6791 | 391.8556
1388.4104 | 520.2924 | 494.567 | 468.7183 | 392.0165
1389.4104 | 520.2385 | 494.6527 | 468.931 | 392.1742
1390.4104 | 520.1908 | 494.6899 | 468.8785 | 392.3259
1391.4104 | 520.1256 | 494.7834 | 468.9654 | 392.4923
1392.4104 | 520.1936 | 494.8379 | 469.0722 | 392.6551
1393.4104 | 520.1516 | 494.9581 | 469.0372 | 392.8096
1394.4104 | 520.0215 | 494.9942 | 469.1465 | 392.9721
1395.4104 | 519.9323 | 495.0604 | 469.2606 | 393.1313
1396.4104 | 519.865 | 495.0659 | 468.8516 | 393.2916
1397.4104 | 519.8645 | 495.1263 | 469.1215 | 393.45
1398.4104 | 519.8182 | 495.1145 | 469.3238 | 393.6136
1399.4104 | 519.7479 | 495.186 | 468.9762 | 393.7882
1400.4104 | 519.7303 | 495.2989 | 469.2795 | 393.9464
1401.4104 | 519.8135 | 495.36 | 469.4249 | 394.1036
1402.4104 | 519.8951 | 495.3342 | 469.5599 | 394.2811
1403.4104 | 519.9534 | 495.4033 | 469.6829 | 394.4396
1404.4104 | 519.8865 | 495.4623 | 469.7054 | 394.5996
1405.4104 | 519.8171 | 495.5734 | 469.8019 | 394.761
1406.4104 | 519.7463 | 495.6356 | 469.7947 | 394.922
1407.4104 | 519.6887 | 495.7482 | 469.691 | 395.1164
1408.4104 | 519.7913 | 495.7902 | 469.6912 | 395.2785
1409.4104 | 519.7334 | 495.8239 | 469.8566 | 395.4276
1410.4104 | 519.7302 | 495.919 | 469.9236 | 395.6112
1411.4104 | 519.6716 | 496.0161 | 470.0031 | 395.7779
1412.4104 | 519.7929 | 496.0764 | 470.0342 | 395.9388
1413.4104 | 519.7906 | 496.1521 | 469.9827 | 396.1266
1414.4104 | 519.8203 | 496.2698 | 470.0815 | 396.2996
1415.4104 | 519.8919 | 496.3878 | 470.0378 | 396.4663
1416.4104 | 519.9517 | 496.5264 | 470.2245 | 396.6184
1417.4104 | 519.9877 | 496.5774 | 470.1315 | 396.7876
1418.4104 | 520.0277 | 496.5895 | 470.277 | 396.9634
1419.4104 | 520.0076 | 496.5826 | 470.2595 | 397.1263
1420.4104 | 519.9987 | 496.6208 | 470.2844 | 397.2972
1421.4104 | 520.0725 | 496.6857 | 470.3258 | 397.4831
1422.4104 | 519.9914 | 496.6687 | 470.4187 | 397.6499
1423.4104 | 519.9808 | 496.5968 | 470.5198 | 397.8189
1424.4104 | 520.1343 | 496.7399 | 470.5734 | 397.9888
1425.4104 | 520.2129 | 496.9071 | 470.658 | 398.1508
1426.4104 | 520.2031 | 497.0023 | 470.7687 | 398.3168
1427.4104 | 520.2764 | 497.0255 | 470.6646 | 398.4773
1428.4104 | 520.3178 | 497.0883 | 470.7164 | 398.6592
1429.4104 | 520.4624 | 497.0994 | 470.7143 | 398.8301
1430.4104 | 520.5019 | 497.238 | 470.8749 | 399.0013
1431.4104 | 520.4288 | 497.2487 | 470.797 | 399.1672
1432.4104 | 520.4728 | 497.2955 | 470.9998 | 399.3446
1433.4104 | 520.5788 | 497.4359 | 471.0069 | 399.5152
1434.4104 | 520.5144 | 497.505 | 470.9317 | 399.6822
1435.4104 | 520.4644 | 497.536 | 471.107 | 399.8393
1436.4104 | 520.4913 | 497.5799 | 471.119 | 399.9974
1437.4104 | 520.4587 | 497.6328 | 471.0805 | 400.1742
1438.4104 | 520.4645 | 497.7382 | 471.2548 | 400.3448
1439.4104 | 520.3497 | 497.7606 | 471.3732 | 400.5169
1440.4104 | 520.2936 | 497.7907 | 471.3317 | 400.6811
1441.4104 | 520.2793 | 497.8377 | 471.4037 | 400.8468
1442.4104 | 520.2205 | 497.8817 | 471.3003 | 401.0149
1443.4104 | 520.2536 | 497.9891 | 471.39 | 401.1785
1444.4104 | 520.2728 | 498.0651 | 471.5334 | 401.3644
1445.4104 | 520.2354 | 498.0673 | 471.6144 | 401.5363
1446.4104 | 520.2241 | 498.1475 | 471.6142 | 401.7141
1447.4104 | 520.2024 | 498.2058 | 471.6299 | 401.8903
1448.4104 | 520.1312 | 498.2778 | 471.5234 | 402.0697
1449.4104 | 520.0814 | 498.3328 | 471.6934 | 402.2516
1450.4104 | 520.2455 | 498.4219 | 471.8103 | 402.4259
1451.4104 | 520.3312 | 498.4442 | 471.9475 | 402.6097
1452.4104 | 520.3866 | 498.2987 | 471.9553 | 402.7943
1453.4104 | 520.3821 | 498.3915 | 472.0261 | 402.9859
1454.4104 | 520.3372 | 498.4631 | 472.0331 | 403.1639
1455.4104 | 520.3029 | 498.4939 | 472.0798 | 403.3428
1456.4104 | 520.2446 | 498.5297 | 471.9129 | 403.5264
1457.4104 | 520.4844 | 498.5984 | 471.9184 | 403.6607
1458.4104 | 520.5934 | 498.6722 | 472.022 | 403.8397
1459.4104 | 520.6155 | 498.75 | 472.0213 | 404.0092
1460.4104 | 520.6428 | 498.8199 | 472.1208 | 404.2091
1461.4104 | 520.5818 | 498.8041 | 472.1617 | 404.3921
1462.4104 | 520.5901 | 498.8141 | 472.1486 | 404.5834
1463.4104 | 520.5865 | 498.8061 | 472.2304 | 404.7703
1464.4104 | 520.6118 | 498.8314 | 472.1103 | 404.9499
1465.4104 | 520.568 | 498.8561 | 472.0723 | 405.1393
1466.4104 | 520.5957 | 498.9334 | 471.9727 | 405.3424
1467.4104 | 520.6096 | 498.9726 | 472.1666 | 405.5283
1468.4104 | 520.6303 | 499.0262 | 472.0936 | 405.734
1469.4104 | 520.5399 | 499.1139 | 472.3475 | 405.9295
1470.4104 | 520.5251 | 499.1864 | 472.4537 | 406.1149
1471.4104 | 520.4759 | 499.1926 | 472.5541 | 406.3036
1472.4104 | 520.4211 | 499.2279 | 472.5749 | 406.4512
1473.4104 | 520.3638 | 499.3064 | 472.4457 | 406.6256
1474.4104 | 520.2112 | 499.3202 | 472.5576 | 406.8068
1475.4104 | 520.2019 | 499.4061 | 472.6316 | 406.9674
1476.4104 | 520.1333 | 499.4808 | 472.7148 | 407.1687
1477.4104 | 520.0827 | 499.5183 | 472.8654 | 407.3265
1478.4104 | 520.0481 | 499.3949 | 472.7739 | 407.5087
1479.4104 | 520.0428 | 499.5489 | 472.9083 | 407.6959
1480.4104 | 520.021 | 499.6489 | 472.8504 | 407.8847
1481.4104 | 520.0076 | 499.648 | 472.8801 | 408.0948
1482.4104 | 520.0198 | 499.7224 | 472.9621 | 408.2596
1483.4104 | 520.0437 | 499.7946 | 473.0059 | 408.47
1484.4104 | 520.016 | 499.79 | 472.991 | 408.6672
1485.4104 | 519.8928 | 499.9464 | 473.0312 | 408.8789
1486.4104 | 519.9465 | 499.9927 | 473.0292 | 409.0683
1487.4104 | 519.933 | 499.9807 | 473.0023 | 409.2463
1488.4104 | 519.9188 | 500.0384 | 473.0483 | 409.4375
1489.4104 | 519.9563 | 500.0371 | 473.2153 | 409.6164
1490.4104 | 519.9501 | 500.0577 | 473.2286 | 409.7919
1491.4104 | 519.9301 | 500.0254 | 473.319 | 409.9918
1492.4104 | 519.9164 | 500.1122 | 473.4744 | 410.1926
1493.4104 | 519.9129 | 500.0232 | 473.3777 | 410.3644
1494.4104 | 519.9141 | 500.1043 | 473.4674 | 410.5817
1495.4104 | 519.8026 | 500.1331 | 473.4349 | 410.7886
1496.4104 | 519.7152 | 500.1227 | 473.4903 | 410.9591
1497.4104 | 519.7191 | 500.17 | 473.419 | 411.1424
1498.4104 | 519.7983 | 500.2738 | 473.4072 | 411.3325
1499.4104 | 519.8191 | 500.3118 | 473.5334 | 411.4999
1500.4104 | 519.8249 | 500.4143 | 473.5562 | 411.6838
1501.4104 | 519.8328 | 500.4606 | 473.5803 | 411.8712
1502.4104 | 519.7898 | 500.4916 | 473.667 | 412.0489
1503.4104 | 519.7261 | 500.3699 | 473.7462 | 412.2108
1504.4104 | 519.6448 | 500.4361 | 473.2875 | 412.3799
1505.4104 | 519.6305 | 500.5806 | 473.5316 | 412.5627
1506.4104 | 519.757 | 500.4851 | 473.6386 | 412.7571
1507.4104 | 519.7074 | 500.6232 | 473.6153 | 412.9242
1508.4104 | 519.6412 | 500.5428 | 473.7107 | 413.1086
1509.4104 | 519.5907 | 500.6352 | 473.7786 | 413.2597
1510.4104 | 519.689 | 500.7455 | 473.7552 | 413.419
1511.4104 | 519.6981 | 500.814 | 473.84 | 413.6399
1512.4104 | 519.7504 | 500.8994 | 473.8951 | 413.7746
1513.4104 | 519.7697 | 500.8617 | 473.8913 | 413.9106
1514.4104 | 519.7764 | 500.9476 | 473.7114 | 414.0772
1515.4104 | 519.7236 | 501.051 | 473.7164 | 414.2473
1516.4104 | 519.6125 | 501.0913 | 473.9135 | 414.3787
1517.4104 | 519.5901 | 501.1273 | 473.9351 | 414.558
1518.4104 | 519.5388 | 501.1116 | 473.9682 | 414.719
1519.4104 | 519.4585 | 501.1256 | 474.0255 | 414.893
1520.4104 | 519.4084 | 501.1555 | 474.1084 | 415.0587
1521.4104 | 519.4342 | 501.2325 | 473.7277 | 415.1806
1522.4104 | 519.601 | 501.2701 | 473.9912 | 415.3689
1523.4104 | 519.7651 | 501.3043 | 474.1351 | 415.5519
1524.4104 | 519.8421 | 501.3566 | 474.0758 | 415.7503
1525.4104 | 519.9083 | 501.4441 | 474.0231 | 415.9037
1526.4104 | 520.0333 | 501.553 | 474.1864 | 416.0491
1527.4104 | 520.0599 | 501.5508 | 474.3056 | 416.2029
1528.4104 | 520.1327 | 501.5535 | 474.27 | 416.3648
1529.4104 | 520.1934 | 501.5848 | 474.2314 | 416.5287
1530.4104 | 520.2624 | 501.6809 | 474.4219 | 416.6372
1531.4104 | 520.2895 | 501.714 | 474.4361 | 416.8126
1532.4104 | 520.3124 | 501.7689 | 474.4389 | 416.9565
1533.4104 | 520.4214 | 501.8053 | 474.3824 | 417.1662
1534.4104 | 520.5456 | 501.845 | 474.5007 | 417.3194
1535.4104 | 520.632 | 501.8752 | 474.4204 | 417.5037
1536.4104 | 520.5641 | 501.8683 | 474.0972 | 417.6177
1537.4104 | 520.5288 | 501.9765 | 474.263 | 417.7775
1538.4104 | 520.4685 | 502.0339 | 474.4119 | 417.9609
1539.4104 | 520.4655 | 502.1293 | 474.5205 | 418.094
1540.4104 | 520.4668 | 502.2025 | 474.5529 | 418.229
1541.4104 | 520.5029 | 502.2643 | 474.5724 | 418.3773
1542.4104 | 520.4645 | 502.3326 | 474.5624 | 418.484
1543.4104 | 520.409 | 502.2662 | 474.6673 | 418.6749
1544.4104 | 520.3118 | 502.3155 | 474.7165 | 418.8394
1545.4104 | 520.2588 | 502.3253 | 474.6905 | 418.9997
1546.4104 | 520.1906 | 502.3544 | 474.5496 | 419.103
1547.4104 | 520.2211 | 502.3252 | 474.5921 | 419.1936
1548.4104 | 520.2302 | 502.3712 | 474.7059 | 419.383
1549.4104 | 520.2137 | 502.3672 | 474.8625 | 419.5384
1550.4104 | 520.1332 | 502.4046 | 474.9299 | 419.7581
1551.4104 | 520.084 | 502.4563 | 474.7991 | 419.8911
1552.4104 | 519.9698 | 502.4526 | 474.7711 | 419.9869
1553.4104 | 519.9146 | 502.5093 | 474.812 | 419.9348
1554.4104 | 519.771 | 502.5457 | 474.7019 | 420.0475
1555.4104 | 519.7663 | 502.5178 | 474.5486 | 420.1759
1556.4104 | 519.7701 | 502.5349 | 474.7239 | 420.3187
1557.4104 | 519.7737 | 502.3928 | 474.798 | 420.4466
1558.4104 | 519.7765 | 502.4909 | 474.8923 | 420.591
1559.4104 | 519.8408 | 502.5059 | 474.9734 | 420.7179
1560.4104 | 519.8624 | 502.5336 | 474.8667 | 420.8555
1561.4104 | 519.8546 | 502.5421 | 474.935 | 420.9625
1562.4104 | 519.898 | 502.5026 | 474.9772 | 421.0959
1563.4104 | 519.91 | 502.4951 | 475.0102 | 421.2001
1564.4104 | 519.9058 | 502.4383 | 475.0737 | 421.2316
1565.4104 | 519.941 | 502.481 | 475.2145 | 421.3416
1566.4104 | 520.0383 | 502.4846 | 475.2814 | 421.4848
1567.4104 | 520.0442 | 502.4562 | 475.0431 | 421.4016
1568.4104 | 520.1077 | 502.5319 | 475.0254 | 421.6111
1569.4104 | 520.0389 | 502.5576 | 474.549 | 421.64
1570.4104 | 520.1121 | 502.3937 | 474.7172 | 421.7717
1571.4104 | 520.1582 | 502.3701 | 474.9332 | 421.8909
1572.4104 | 520.1829 | 502.3038 | 475.0595 | 422.0311
1573.4104 | 520.2332 | 502.2141 | 475.1923 | 421.9143
1574.4104 | 520.213 | 502.1685 | 475.1875 | 423.3301
1575.4104 | 520.2587 | 502.0447 | 475.1598 | 422.4364
1576.4104 | 520.3798 | 501.9501 | 475.2088 | 422.5074
1577.4104 | 520.4043 | 501.855 | 475.2199 | 422.6031
1578.4104 | 520.5464 | 501.8527 | 475.2688 | 422.7926
1579.4104 | 520.6794 | 501.7312 | 475.0507 | 422.9855
1580.4104 | 520.8051 | 501.687 | 474.9621 | 423.0891
1581.4104 | 520.8825 | 501.6516 | 474.7697 | 423.2482
1582.4104 | 520.9908 | 501.6731 | 474.9913 | 423.2903
1583.4104 | 521.0585 | 501.517 | 474.8999 | 423.4377
1584.4104 | 520.9881 | 501.4551 | 475.056 | 423.533
1585.4104 | 520.853 | 501.4186 | 475.1294 | 423.6361
1586.4104 | 520.8947 | 501.3441 | 475.2273 | 423.7598
1587.4104 | 520.9035 | 501.2531 | 475.1895 | 423.9481
1588.4104 | 520.8823 | 501.2005 | 475.1929 | 424.0893
1589.4104 | 520.8843 | 501.1497 | 474.9472 | 424.257
1590.4104 | 520.7783 | 501.0825 | 474.9817 | 424.5595
1591.4104 | 520.7679 | 501.0549 | 474.9469 | 424.7182
1592.4104 | 520.8296 | 501.0214 | 475.1034 | 424.9282
1593.4104 | 520.8258 | 500.906 | 475.267 | 425.0642
1594.4104 | 520.8301 | 500.861 | 475.2831 | 425.1708
1595.4104 | 520.7641 | 500.7811 | 474.9805 | 425.3248
1596.4104 | 520.8208 | 500.7321 | 475.2316 | 425.4006
1597.4104 | 520.8964 | 500.6473 | 475.2692 | 425.539
1598.4104 | 520.791 | 500.6362 | 475.0903 | 425.6423
1599.4104 | 520.7946 | 500.5937 | 475.1673 | 425.7487
1600.4104 | 520.7252 | 500.5615 | 475.1324 | 426.0014
1601.4104 | 520.7638 | 500.4677 | 475.3087 | 426.1714
1602.4104 | 520.7836 | 500.3921 | 475.3728 | 426.1972
1603.4104 | 520.8326 | 500.3681 | 475.501 | 426.4065
1604.4104 | 520.8457 | 500.2909 | 475.4405 | 426.4932
1605.4104 | 520.8879 | 500.255 | 475.4076 | 426.5566
1606.4104 | 520.9856 | 500.214 | 475.5366 | 426.7028
1607.4104 | 520.9968 | 500.1724 | 475.4291 | 426.9346
1608.4104 | 520.9448 | 500.1293 | 475.387 | 426.9026
1609.4104 | 521.0129 | 500.0969 | 475.1633 | 427.0358
1610.4104 | 520.9918 | 500.0486 | 475.3354 | 427.167
1611.4104 | 521.0038 | 500.0319 | 475.0438 | 427.33
1612.4104 | 520.9824 | 499.9597 | 475.2289 | 427.4791
1613.4104 | 521.0072 | 500.0434 | 475.3328 | 427.2823
1614.4104 | 520.981 | 500.0094 | 475.39 | 427.6104
1615.4104 | 520.9859 | 499.9675 | 475.4534 | 427.636
1616.4104 | 521.0693 | 499.9184 | 475.5497 | 427.7213
1617.4104 | 521.1121 | 499.8594 | 475.6036 | 427.8788
1618.4104 | 521.2095 | 499.861 | 475.6136 | 428.1091
1619.4104 | 521.1987 | 499.8291 | 475.5147 | 427.7346
1620.4104 | 521.0787 | 499.767 | 475.2005 | 427.9196
1621.4104 | 521.1034 | 499.7414 | 475.3601 | 428.1278
1622.4104 | 521.2049 | 499.6946 | 475.5608 | 428.2153
1623.4104 | 521.0978 | 499.683 | 475.5507 | 428.3593
1624.4104 | 521.0424 | 499.6009 | 475.5883 | 428.4942
1625.4104 | 521.0557 | 499.6115 | 475.6582 | 428.5199
1626.4104 | 521.0373 | 499.5213 | 475.6502 | 428.6762
1627.4104 | 520.992 | 499.5281 | 475.5867 | 428.7228
1628.4104 | 521.0109 | 499.4701 | 475.7844 | 428.9537
1629.4104 | 520.9787 | 499.4168 | 475.7971 | 428.9192
1630.4104 | 520.9771 | 499.3873 | 475.7847 | 429.0157
1631.4104 | 520.9919 | 499.3785 | 475.6998 | 429.1245
1632.4104 | 520.9151 | 499.3595 | 475.5724 | 429.1809
1633.4104 | 520.7594 | 499.3227 | 475.4436 | 429.4576
1634.4104 | 520.6697 | 499.2945 | 475.5015 | 429.6243
1635.4104 | 520.6825 | 499.2474 | 475.8322 | 429.6688
1636.4104 | 520.6007 | 499.1332 | 475.8283 | 429.7849
1637.4104 | 520.6227 | 499.0761 | 475.7349 | 429.8876
1638.4104 | 520.6385 | 499.0684 | 475.6926 | 429.9619
1639.4104 | 520.6598 | 499.0139 | 475.707 | 430.0067
1640.4104 | 520.6561 | 498.9582 | 475.7797 | 430.0395
1641.4104 | 520.7541 | 498.8919 | 475.4055 | 430.1411
1642.4104 | 520.9291 | 498.918 | 475.572 | 430.1237
1643.4104 | 520.8114 | 498.8582 | 475.4897 | 430.2167
1644.4104 | 520.7155 | 498.8861 | 475.5914 | 430.2874
1645.4104 | 520.6767 | 498.8619 | 475.5458 | 431.4651
1646.4104 | 520.6212 | 498.7762 | 475.5913 | 431.6816
1647.4104 | 520.6262 | 498.7767 | 475.7019 | 431.6148
1648.4104 | 520.5199 | 498.7303 | 475.3781 | 431.6961
1649.4104 | 520.4265 | 498.6616 | 475.2648 | 431.5581
1650.4104 | 520.3613 | 498.6469 | 475.4608 | 431.8434
1651.4104 | 520.2843 | 498.5799 | 475.4683 | 431.9048
1652.4104 | 520.2466 | 498.4813 | 475.5431 | 431.9175
1653.4104 | 520.2688 | 498.4789 | 475.3747 | 432.0778
1654.4104 | 520.182 | 498.4362 | 475.5429 | 432.0803
1655.4104 | 520.2304 | 498.4077 | 475.646 | 432.1575
1656.4104 | 520.1919 | 498.3655 | 475.4885 | 432.1563
1657.4104 | 520.074 | 498.3894 | 475.6396 | 432.197
1658.4104 | 520.0462 | 498.37 | 475.6343 | 432.4982
1659.4104 | 520.1251 | 498.2352 | 475.6354 | 432.5765
1660.4104 | 520.1185 | 498.1268 | 475.6502 | 432.5322
1661.4104 | 520.0707 | 498.0906 | 475.5641 | 432.7099
1662.4104 | 519.9712 | 498.0829 | 475.6625 | 432.8548
1663.4104 | 520.0078 | 498.0829 | 475.6785 | 432.8803
1664.4104 | 520.0911 | 498.0808 | 475.5986 | 432.9892
1665.4104 | 520.0678 | 498.0096 | 475.6585 | 433.1465
1666.4104 | 520.1081 | 497.985 | 475.7593 | 433.1564
1667.4104 | 520.1085 | 497.9118 | 475.624 | 433.2031
1668.4104 | 520.2082 | 497.9476 | 475.6451 | 433.2589
1669.4104 | 520.215 | 497.8907 | 475.6543 | 433.2419
1670.4104 | 520.136 | 497.8721 | 475.7703 | 433.397
1671.4104 | 520.0939 | 497.8378 | 475.7856 | 433.6274
1672.4104 | 520.191 | 497.7997 | 475.5916 | 433.5111
1673.4104 | 520.1391 | 497.7482 | 475.7123 | 433.7325
1674.4104 | 520.1967 | 497.7442 | 475.7508 | 433.722
1675.4104 | 520.2638 | 497.72 | 475.5532 | 433.8421
1676.4104 | 520.2745 | 497.6856 | 475.5565 | 433.9653
1677.4104 | 520.3433 | 497.64 | 475.6279 | 434.0663
1678.4104 | 520.4207 | 497.5955 | 475.5224 | 434.0125
1679.426 | 520.4898 | 497.6024 | 475.4488 | 434.0114
1680.4104 | 520.4526 | 497.521 | 475.4813 | 434.3453
1681.4104 | 520.5129 | 497.5141 | 475.488 | 434.4238
1682.4104 | 520.5107 | 497.5073 | 475.4597 | 434.3432
1683.4104 | 520.5355 | 497.4157 | 475.5397 | 434.4829
1684.4104 | 520.725 | 497.431 | 475.6188 | 434.3551
1685.4104 | 520.6502 | 497.4097 | 475.645 | 434.4892
1686.4104 | 520.5437 | 497.3796 | 475.6125 | 434.5458
1687.4104 | 520.4663 | 497.3842 | 475.4816 | 434.6357
1688.4104 | 520.3635 | 497.3364 | 475.5104 | 434.7767
1689.4104 | 520.3819 | 497.3151 | 475.2302 | 434.9199
1690.4104 | 520.4476 | 497.2605 | 475.3462 | 435.6567
1691.4104 | 520.418 | 497.2127 | 475.3107 | 435.4799
1692.4104 | 520.425 | 497.2022 | 475.4107 | 435.6061
1693.4104 | 520.4615 | 497.1557 | 474.9965 | 435.4917
1694.4104 | 520.4614 | 497.1083 | 475.0915 | 435.4663
1695.4104 | 520.3849 | 497.1051 | 475.0029 | 435.1984
1696.4104 | 520.3424 | 497.071 | 475.1708 | 435.3178
1697.4104 | 520.345 | 497.0187 | 475.3032 | 435.4344
1698.4104 | 520.3429 | 497.0159 | 475.3516 | 438.7514
1699.4104 | 520.2934 | 497.0201 | 475.3716 | 439.1798
1700.4104 | 520.1754 | 496.9834 | 475.3078 | 438.8656
1701.4104 | 520.0818 | 496.997 | 475.2479 | 438.9155
1702.4104 | 520.0664 | 496.9464 | 475.3046 | 439.1163
1703.4104 | 520.0408 | 496.911 | 475.3173 | 438.6649
1704.4104 | 520.0494 | 496.8935 | 475.2142 | 439.408
1705.4104 | 519.9975 | 496.9258 | 475.318 | 439.3006
1706.4104 | 519.9754 | 496.8962 | 475.3141 | 439.0777
1707.4104 | 519.956 | 496.9524 | 475.2668 | 439.205
1708.4104 | 519.8016 | 496.9512 | 475.2431 | 439.3119
1709.4104 | 519.8187 | 496.9811 | 475.222 | 439.1674
1710.4104 | 519.8004 | 496.9962 | 475.1689 | 439.1805
1711.4104 | 519.7586 | 497.0468 | 475.3213 | 439.3138
1712.4104 | 519.7422 | 497.057 | 475.1172 | 439.2508
1713.4104 | 519.7404 | 497.0984 | 474.9947 | 439.4051
1714.4104 | 519.8319 | 497.153 | 475.203 | 438.8142
1715.4104 | 519.9463 | 497.2171 | 475.2999 | 438.8874
1716.4104 | 519.9878 | 497.2427 | 475.1328 | 438.7236
1717.4104 | 520.0203 | 497.2639 | 475.2652 | 439.9253
1718.4104 | 520.1123 | 497.326 | 475.1357 | 439.9811
1719.4104 | 520.1905 | 497.3564 | 475.1364 | 440.2302
1720.4104 | 520.2329 | 497.3846 | 475.0542 | 439.7537
1721.4104 | 520.201 | 497.3446 | 474.9454 | 439.8489
1722.4104 | 520.215 | 497.3252 | 475.0523 | 439.8352
1723.4104 | 520.2823 | 497.347 | 475.2032 | 439.8646
1724.4104 | 520.353 | 497.3617 | 475.1337 | 439.8957
1725.4104 | 520.4084 | 497.3974 | 475.1585 | 439.9349
1726.4104 | 520.3595 | 497.4442 | 475.2778 | 439.7838
1727.4104 | 520.2787 | 497.4728 | 475.3017 | 440.1565
1728.4104 | 520.2633 | 497.5232 | 475.2916 | 440.5111
1729.4104 | 520.1804 | 497.5821 | 475.2792 | 448.13
1730.4104 | 520.2451 | 497.6277 | 475.2521 | 443.1847
1731.4104 | 520.2978 | 497.6092 | 475.1044 | 443.3377
1732.4104 | 520.3853 | 497.5756 | 475.3277 | 448.4148
1733.4104 | 520.2569 | 497.6047 | 475.2223 | 438.0915
1734.4104 | 520.1807 | 497.5608 | 475.0891 | 438.0044
1735.4104 | 520.2371 | 497.5809 | 475.1465 | 441.5436
1736.4104 | 520.2821 | 497.5214 | 475.2953 | 443.4353
1737.4104 | 520.3114 | 497.6193 | 475.2879 | 442.9403
1738.4104 | 520.2623 | 497.6926 | 475.1998 | 442.8014
1739.4104 | 520.2902 | 497.6577 | 475.2555 | 442.7706
1740.4104 | 520.3113 | 497.7366 | 475.2083 | 442.9103
1741.4104 | 520.2858 | 497.7257 | 475.2135 | 442.774
1742.4104 | 520.2166 | 497.7015 | 475.2456 | 441.1925
1743.4104 | 520.1643 | 497.6866 | 474.9475 | 437.1984
1744.4104 | 520.2008 | 497.7225 | 475.0019 | 436.706
1745.4104 | 520.3702 | 497.729 | 475.099 | 440.7786
1746.4104 | 520.3657 | 497.7668 | 474.982 | 441.4253
1747.4104 | 520.3421 | 497.7403 | 474.886 | 435.4456
1748.4104 | 520.3369 | 497.7881 | 474.9188 | 436.621
1749.4104 | 520.3607 | 497.7426 | 475.0808 | 436.9068
1750.4104 | 520.4057 | 497.7677 | 474.9012 | 436.6326
1751.4104 | 520.5237 | 497.7906 | 475.0677 | 436.2613
1752.4104 | 520.6478 | 497.7982 | 475.0995 | 437.9254
1753.4104 | 520.7376 | 497.7491 | 475.1131 | 438.1456
1754.4104 | 520.7642 | 497.7837 | 475.1207 | 446.3718
1755.4104 | 520.7763 | 497.8325 | 474.925 | 443.352
1756.4104 | 520.7299 | 497.8444 | 475.0249 | 443.007
1757.4104 | 520.7781 | 497.8406 | 475.0489 | 443.1539
1758.4104 | 520.9075 | 497.8447 | 474.9599 | 442.4703
1759.4104 | 520.8955 | 497.8367 | 475.0563 | 442.4245
1760.4104 | 520.8825 | 497.8703 | 475.0585 | 442.4863
1761.4104 | 520.9964 | 497.8443 | 475.1227 | 442.6991
1762.4104 | 520.9797 | 497.9015 | 474.9725 | 443.0911
1763.4104 | 520.9061 | 497.834 | 474.9073 | 443.3492
1764.4104 | 520.7065 | 497.8925 | 474.896 | 443.4783
1765.4104 | 520.5446 | 497.885 | 474.9002 | 443.6391
1766.4104 | 520.5595 | 497.9537 | 475.0123 | 443.7275
1767.4104 | 520.5588 | 497.9196 | 475.1087 | 443.8161
1768.4104 | 520.4006 | 497.8997 | 475.0371 | 443.8294
1769.4104 | 520.3578 | 497.8358 | 475.0845 | 443.8554
1770.4104 | 520.1968 | 497.8562 | 474.971 | 443.8859
1771.4104 | 520.2227 | 497.8717 | 474.9131 | 443.9032
1772.4104 | 520.3179 | 497.8517 | 474.9586 | 443.9635
1773.4104 | 520.3046 | 497.8416 | 475.0391 | 443.9839
1774.4104 | 520.3565 | 497.8658 | 475.0466 | 443.9894
1775.4104 | 520.3472 | 497.8653 | 474.9482 | 444.0291
1776.4104 | 520.3678 | 497.9065 | 474.9685 | 444.0422
1777.4104 | 520.4207 | 497.8682 | 474.8559 | 444.07
1778.4104 | 520.3113 | 497.8701 | 474.6129 | 444.0905
1779.4104 | 520.3988 | 497.6794 | 474.7957 | 444.1108
1780.4104 | 520.4758 | 497.7102 | 474.7413 | 444.1395
1781.4104 | 520.459 | 497.7158 | 474.8065 | 444.1605
1782.4104 | 520.4287 | 497.7798 | 474.9817 | 444.1967
1783.4104 | 520.4243 | 497.765 | 474.9553 | 444.2177
1784.4104 | 520.4787 | 497.8039 | 475.0491 | 444.263
1785.4104 | 520.4948 | 497.756 | 474.8647 | 444.3322
1786.4104 | 520.3932 | 497.7754 | 475.0153 | 444.3712
1787.4104 | 520.344 | 497.7637 | 475.0425 | 444.4283
1788.4104 | 520.4206 | 497.777 | 474.8576 | 444.4882
1789.4104 | 520.5518 | 497.8001 | 474.8706 | 444.5592
1790.4417 | 520.5966 | 497.8236 | 474.9034 | 444.6308
1791.4104 | 520.5926 | 497.8057 | 474.9427 | 444.6983
1792.4104 | 520.6574 | 497.8419 | 474.9434 | 444.7895
1793.4104 | 520.6137 | 497.8331 | 474.9599 | 444.8283
1794.4104 | 520.6069 | 497.7962 | 474.928 | 444.8455
1795.4104 | 520.6485 | 497.796 | 475.0752 | 444.8991
1796.4104 | 520.656 | 497.7611 | 474.983 | 444.9532
1797.4104 | 520.7587 | 497.7635 | 474.9722 | 445.0189
1798.4104 | 520.7788 | 497.8164 | 474.9833 | 445.0637
1799.4104 | 520.7351 | 497.8393 | 475.0281 | 445.1602
1800.4104 | 520.7242 | 497.7541 | 475.0856 | 445.2106
1801.4104 | 520.7838 | 497.7627 | 474.8641 | 445.2825
1802.4104 | 520.8267 | 497.7936 | 474.7608 | 445.3371
1803.4104 | 520.7513 | 497.8528 | 474.598 | 445.3758
1804.4104 | 520.7408 | 497.7329 | 474.7516 | 445.433
1805.4104 | 520.7377 | 497.7862 | 474.8854 | 445.5025
1806.4104 | 520.8162 | 497.7997 | 474.7631 | 445.598
1807.4104 | 520.8122 | 497.6956 | 474.7323 | 445.7024
1808.4104 | 520.8034 | 497.7457 | 474.7929 | 445.7787
1809.4104 | 520.7407 | 497.8387 | 474.8097 | 445.8457
1810.4104 | 520.7229 | 497.8327 | 474.7797 | 445.9108
1811.4104 | 520.8696 | 497.8461 | 474.6407 | 446.1373
1812.4104 | 520.8847 | 497.8927 | 474.5326 | 446.4155
1813.4104 | 520.8248 | 497.8833 | 474.6805 | 446.5802
1814.4104 | 520.7983 | 497.9042 | 474.7361 | 446.6878
1815.4104 | 520.8396 | 497.9635 | 474.9198 | 446.8222
1816.4104 | 520.8324 | 497.94 | 474.8483 | 446.9181
1817.4104 | 520.784 | 497.8933 | 474.7907 | 447.1443
1818.4104 | 520.8152 | 497.913 | 474.7712 | 447.3681
1819.4104 | 520.8972 | 497.9806 | 474.7511 | 447.8114
1820.4104 | 520.8936 | 497.9988 | 474.651 | 447.9372
1821.4104 | 520.8943 | 497.9777 | 474.4264 | 448.0036
1822.4104 | 520.847 | 498.0004 | 474.4326 | 447.9597
1823.4104 | 520.7296 | 498.0307 | 474.4235 | 447.9959
1824.4104 | 520.6271 | 498.017 | 474.3918 | 448.0882
1825.4104 | 520.5888 | 497.9428 | 474.6664 | 448.2421
1826.4104 | 520.5463 | 497.996 | 474.6677 | 448.5029
1827.4104 | 520.555 | 498.0219 | 474.7507 | 448.6225
1828.4104 | 520.629 | 498.0332 | 474.8497 | 448.5764
1829.4104 | 520.6368 | 497.9924 | 474.9052 | 448.532
1830.4104 | 520.4174 | 498.0202 | 474.8858 | 448.5779