## Test Conditions
DESIREE-FIRE Test Number 35 - Circuit Simulator Data Only
Test Date: | 2009-09-24
DCSim DAQ Start Time | 8:07
DCSim Time for Synchronization | 8:50
Heat Source Synchronization | 0:38 | minutes:seconds
Heat Source DAQ Start Time | 8:12
Heat Source Start Time | 8:57
DCSim Offset | 0:50 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3000 | seconds
Heat Source Offset | 0:45 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2720 | seconds
Heat Source Stop Time | 9:30
Test Duration | 0:33 | minutes:seconds
| 1980 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
El | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.35938 | 125.386 | -62.0178 | 63.2309 | -0.20882 | 0.012042 | 0.0076369 | 0.0032129 | 0.063335 | -0.0014313 | 0.068171 | -62.1231 | 63.1119 | -62.2055 | -62.2055 | 62.8647 | 0.050354 | 0.14648 | 0.15106 | 63.1393 | -62.2467 | -0.18768 | -0.11902 | -0.10529 | -0.18768 | -0.36621 | -0.22888 | -0.091553 | 0.082397 | 62.1643 | 62.1689 | 124.8825 | 125.1297 | -0.10529 | 125.1572 | 62.0682 | -0.22888 | 125.1297 | -0.10529 | 62.0682 | 124.8825 | 125.1572 | -125.4364 | -125.4776
0.64062 | 125.4639 | -61.9904 | 63.1668 | -0.033341 | 0.0047787 | 0.0065689 | -0.0027687 | 0.064617 | -0.00057686 | 0.067317 | -61.8759 | 63.0707 | -62.1826 | -62.1231 | 62.9013 | 0.041199 | -0.07782 | 0.13275 | 63.0844 | -62.2238 | -0.19226 | -0.09613 | 0.11444 | -0.13275 | -0.2655 | -0.23346 | -0.082397 | 0.3067 | 61.9125 | 62.1231 | 124.8917 | 125.061 | 0.11444 | 125.0748 | 62.0316 | -0.23346 | 125.061 | 0.11444 | 62.0316 | 124.8917 | 125.0748 | -125.3494 | -125.3906
1.6406 | 125.4501 | -62.0087 | 63.1851 | -0.018082 | 0.0099057 | 0.0046463 | -0.0025549 | 0.062267 | -0.0010041 | 0.069667 | -62.1323 | 63.0295 | -62.2101 | -62.1872 | 62.9059 | 0.059509 | -0.068665 | 0.17395 | 63.0753 | -62.2147 | -0.20142 | -0.15564 | -0.1236 | -0.17853 | -0.27924 | -0.20599 | -0.10986 | 0.07782 | 61.94 | 62.1826 | 124.9146 | 125.0381 | -0.1236 | 125.0839 | 62.0682 | -0.20599 | 125.0381 | -0.1236 | 62.0682 | 124.9146 | 125.0839 | -125.3952 | -125.3998
2.6406 | 125.4684 | -61.9766 | 63.2034 | -0.2317 | 0.010119 | 0.0095595 | 0.0017175 | 0.06483 | -0.00014946 | 0.069453 | -62.0453 | 63.0798 | -62.2055 | -62.114 | 62.9425 | 0.13733 | 0.022888 | 0.25635 | 63.1073 | -62.2147 | -0.22888 | -0.1236 | -0.068664 | -0.13733 | -0.26093 | -0.23804 | -0.09613 | 0.16022 | 61.9995 | 62.233 | 124.9191 | 125.0565 | -0.068664 | 125.0839 | 62.114 | -0.23804 | 125.0565 | -0.068664 | 62.114 | 124.9191 | 125.0839 | -125.4089 | -125.4181
3.6406 | 125.4959 | -61.9949 | 63.1851 | -0.048599 | 0.0090513 | 0.0087051 | -0.0017005 | 0.063121 | 0.00027774 | 0.067958 | -62.0956 | 63.0295 | -62.1964 | -62.146 | 62.9288 | 0.10071 | -0.068665 | 0.18768 | 63.0936 | -62.2055 | -0.20142 | -0.15564 | -0.10071 | -0.15106 | -0.25635 | -0.21057 | -0.091553 | 0.10071 | 61.9263 | 62.1826 | 124.9237 | 125.0244 | -0.10071 | 125.0885 | 62.0956 | -0.21057 | 125.0244 | -0.10071 | 62.0956 | 124.9237 | 125.0885 | -125.3815 | -125.3906
4.6406 | 125.4959 | -61.9537 | 63.1989 | -0.23933 | 0.0088375 | 0.0093459 | 0.00086295 | 0.062267 | -0.0027131 | 0.069239 | -62.0316 | 63.0478 | -62.1918 | -62.1048 | 62.9837 | 0.16937 | -0.036621 | 0.27466 | 63.0844 | -62.2009 | -0.23804 | -0.15106 | -0.07782 | -0.15106 | -0.21515 | -0.24719 | -0.11444 | 0.16022 | 61.9171 | 62.2284 | 124.9374 | 125.0015 | -0.07782 | 125.0381 | 62.1231 | -0.24719 | 125.0015 | -0.07782 | 62.1231 | 124.9374 | 125.0381 | -125.3906 | -125.3998
5.6406 | 125.5463 | -61.9675 | 63.1805 | -0.17067 | 0.010333 | 0.010414 | -0.0025549 | 0.063549 | -0.0018585 | 0.070735 | -62.0316 | 63.0295 | -62.1735 | -62.0773 | 62.9745 | 0.15564 | -0.068665 | 0.28381 | 63.1119 | -62.1735 | -0.20599 | -0.15106 | -0.064087 | -0.10986 | -0.20599 | -0.20599 | -0.068665 | 0.14191 | 61.8988 | 62.2513 | 124.942 | 124.9969 | -0.064087 | 125.0793 | 62.1231 | -0.20599 | 124.9969 | -0.064087 | 62.1231 | 124.942 | 125.0793 | -125.354 | -125.354
6.6406 | 125.5371 | -61.9537 | 63.2034 | -0.16304 | 0.0067013 | 0.010201 | -0.0010597 | 0.063335 | -0.00014946 | 0.067958 | -62.0132 | 63.0432 | -62.1689 | -62.0911 | 62.9745 | 0.16022 | -0.050354 | 0.29755 | 63.0798 | -62.2009 | -0.21515 | -0.16022 | -0.05951 | -0.13733 | -0.22888 | -0.24719 | -0.1236 | 0.15564 | 61.9034 | 62.2513 | 124.9283 | 124.9969 | -0.05951 | 125.0336 | 62.114 | -0.24719 | 124.9969 | -0.05951 | 62.114 | 124.9283 | 125.0336 | -125.3723 | -125.4044
7.6406 | 125.5188 | -61.9766 | 63.1989 | -0.20119 | 0.0077695 | 0.0099869 | 0.0019311 | 0.063976 | -0.0035675 | 0.069239 | -62.0499 | 63.0341 | -62.1826 | -62.1048 | 62.9654 | 0.15564 | -0.041199 | 0.28381 | 63.0936 | -62.1964 | -0.20599 | -0.16479 | -0.073242 | -0.12817 | -0.23346 | -0.21973 | -0.10529 | 0.13275 | 61.9354 | 62.2604 | 124.942 | 125.0107 | -0.073242 | 125.0702 | 62.1323 | -0.21973 | 125.0107 | -0.073242 | 62.1323 | 124.942 | 125.0702 | -125.3815 | -125.3952
8.6406 | 125.4913 | -61.9675 | 63.2034 | -0.15541 | 0.0086239 | 0.01191 | 0.00043575 | 0.063762 | -0.0031403 | 0.070308 | -62.0361 | 63.0569 | -62.1872 | -62.0865 | 62.9608 | 0.16479 | -0.041199 | 0.28839 | 63.0844 | -62.1826 | -0.21973 | -0.14648 | -0.068665 | -0.11902 | -0.24262 | -0.21515 | -0.11902 | 0.15106 | 61.9263 | 62.2559 | 124.9283 | 125.0244 | -0.068665 | 125.0519 | 62.1323 | -0.21515 | 125.0244 | -0.068665 | 62.1323 | 124.9283 | 125.0519 | -125.3906 | -125.386
9.6406 | 125.4868 | -61.972 | 63.2172 | -0.24696 | 0.0077695 | 0.011696 | -0.00084605 | 0.062481 | -0.0029267 | 0.068599 | -62.0361 | 63.0478 | -62.2009 | -62.1048 | 62.9745 | 0.16022 | -0.027466 | 0.2655 | 63.089 | -62.2101 | -0.22888 | -0.16937 | -0.064087 | -0.13275 | -0.24262 | -0.23804 | -0.12817 | 0.16479 | 61.9446 | 62.2375 | 124.9466 | 125.0198 | -0.064087 | 125.061 | 62.1323 | -0.23804 | 125.0198 | -0.064087 | 62.1323 | 124.9466 | 125.061 | -125.4181 | -125.4272
10.6406 | 125.5051 | -61.9766 | 63.1805 | -0.16304 | 0.0090513 | 0.012978 | -0.00063225 | 0.062053 | -0.0010041 | 0.068385 | -62.0041 | 63.0478 | -62.1918 | -62.0865 | 62.97 | 0.16937 | -0.050354 | 0.27008 | 63.089 | -62.1964 | -0.21515 | -0.13275 | -0.027465 | -0.10986 | -0.21057 | -0.21973 | -0.091553 | 0.18768 | 61.9263 | 62.2467 | 124.9466 | 125.0244 | -0.027465 | 125.0656 | 62.146 | -0.21973 | 125.0244 | -0.027465 | 62.146 | 124.9466 | 125.0656 | -125.3723 | -125.3769
11.6406 | 125.4822 | -62.0132 | 63.2034 | -0.26222 | 0.0086239 | 0.0097733 | -0.00041865 | 0.063762 | -0.0029267 | 0.069026 | -62.0316 | 63.0936 | -62.1964 | -62.1277 | 62.9517 | 0.12817 | 0.013733 | 0.23804 | 63.1027 | -62.2284 | -0.18311 | -0.10986 | -0.01831 | -0.11444 | -0.25177 | -0.21515 | -0.10071 | 0.1648 | 62.027 | 62.2513 | 124.9649 | 125.1068 | -0.01831 | 125.116 | 62.1414 | -0.21515 | 125.1068 | -0.01831 | 62.1414 | 124.9649 | 125.116 | -125.3998 | -125.4318
12.6406 | 125.3952 | -62.0316 | 63.2309 | -0.26222 | 0.010119 | 0.010414 | 0.0040673 | 0.065685 | -0.0014313 | 0.066462 | -62.114 | 63.121 | -62.1964 | -62.1735 | 62.8601 | 0.050354 | 0.11902 | 0.16479 | 63.1302 | -62.265 | -0.1648 | -0.10986 | -0.082398 | -0.14191 | -0.37079 | -0.23346 | -0.10071 | 0.082397 | 62.1506 | 62.1963 | 124.8917 | 125.1526 | -0.082398 | 125.1617 | 62.0819 | -0.23346 | 125.1526 | -0.082398 | 62.0819 | 124.8917 | 125.1617 | -125.4272 | -125.4959
13.6406 | 125.4044 | -62.0087 | 63.2263 | -0.26985 | 0.012256 | 0.01255 | 0.0051355 | 0.064403 | -0.00057686 | 0.068385 | -62.114 | 63.1302 | -62.2009 | -62.2009 | 62.8647 | 0.059509 | 0.13275 | 0.13733 | 63.1577 | -62.2559 | -0.19226 | -0.09613 | -0.10529 | -0.19226 | -0.36163 | -0.24719 | -0.068664 | 0.086975 | 62.1414 | 62.146 | 124.8734 | 125.1389 | -0.10529 | 125.1663 | 62.0682 | -0.24719 | 125.1389 | -0.10529 | 62.0682 | 124.8734 | 125.1663 | -125.4272 | -125.4822
14.6406 | 125.4044 | -62.0453 | 63.2172 | -0.26985 | 0.0073423 | 0.010841 | 0.0029993 | 0.065685 | -0.0016449 | 0.06988 | -62.1277 | 63.1256 | -62.2147 | -62.2009 | 62.8601 | 0.068665 | 0.14648 | 0.14191 | 63.1485 | -62.233 | -0.16937 | -0.091553 | -0.082398 | -0.15564 | -0.35706 | -0.18768 | -0.068664 | 0.086975 | 62.1918 | 62.1872 | 124.9054 | 125.1709 | -0.082398 | 125.1938 | 62.114 | -0.18768 | 125.1709 | -0.082398 | 62.114 | 124.9054 | 125.1938 | -125.4318 | -125.4501
15.6406 | 125.3906 | -62.027 | 63.2217 | -0.28511 | 0.010333 | 0.011055 | 0.00022215 | 0.06419 | 0.00091854 | 0.069453 | -62.1094 | 63.1622 | -62.1918 | -62.2055 | 62.8784 | 0.054932 | 0.13733 | 0.13733 | 63.1256 | -62.265 | -0.16479 | -0.05951 | -0.082397 | -0.17853 | -0.34332 | -0.23804 | -0.096131 | 0.082397 | 62.1643 | 62.1643 | 124.9054 | 125.1892 | -0.082397 | 125.1526 | 62.0819 | -0.23804 | 125.1892 | -0.082397 | 62.0819 | 124.9054 | 125.1526 | -125.4135 | -125.4868
16.6406 | 125.3906 | -62.0132 | 63.2309 | -0.24696 | 0.0099057 | 0.015541 | 0.0023583 | 0.065899 | -0.0012177 | 0.067531 | -62.1277 | 63.1668 | -62.2238 | -62.1918 | 62.8647 | 0.054932 | 0.13275 | 0.13275 | 63.1348 | -62.2467 | -0.21057 | -0.064087 | -0.11444 | -0.17853 | -0.36621 | -0.23346 | -0.09613 | 0.09613 | 62.146 | 62.146 | 124.8779 | 125.1801 | -0.11444 | 125.148 | 62.0682 | -0.23346 | 125.1801 | -0.11444 | 62.0682 | 124.8779 | 125.148 | -125.4547 | -125.4776
17.6406 | 125.3998 | -62.0224 | 63.1851 | -0.086746 | 0.011188 | 0.017891 | 0.0051355 | 0.068462 | -0.0020721 | 0.067531 | -62.059 | 63.1531 | -62.2192 | -62.1872 | 62.8922 | 0.032043 | 0.013733 | 0.10986 | 63.1439 | -62.2559 | -0.19684 | -0.032044 | -0.036621 | -0.1648 | -0.29297 | -0.23346 | -0.041199 | 0.16022 | 62.0361 | 62.1323 | 124.9146 | 125.1755 | -0.036621 | 125.1663 | 62.0544 | -0.23346 | 125.1755 | -0.036621 | 62.0544 | 124.9146 | 125.1663 | -125.4044 | -125.441
18.6406 | 125.3906 | -61.9949 | 63.2126 | -0.2317 | 0.01311 | 0.013832 | 0.0027855 | 0.065044 | -0.0027131 | 0.069026 | -62.114 | 63.1577 | -62.2055 | -62.1918 | 62.8647 | 0.064087 | 0.14191 | 0.14191 | 63.1622 | -62.2513 | -0.21057 | -0.054931 | -0.11902 | -0.19684 | -0.3479 | -0.25635 | -0.050354 | 0.091552 | 62.1368 | 62.1368 | 124.8596 | 125.1526 | -0.11902 | 125.1572 | 62.059 | -0.25635 | 125.1526 | -0.11902 | 62.059 | 124.8596 | 125.1572 | -125.4181 | -125.4639
19.6406 | 125.4227 | -62.0178 | 63.1943 | -0.27748 | 0.014392 | 0.014473 | 0.0049219 | 0.06718 | 0.00049134 | 0.069239 | -62.059 | 63.1668 | -62.2192 | -62.1689 | 62.9242 | 0.086975 | 0.068665 | 0.17395 | 63.1393 | -62.2513 | -0.20142 | -0.027466 | -0.041199 | -0.15106 | -0.27008 | -0.23346 | -0.054932 | 0.16022 | 62.0865 | 62.1918 | 124.942 | 125.1846 | -0.041199 | 125.1572 | 62.1048 | -0.23346 | 125.1846 | -0.041199 | 62.1048 | 124.942 | 125.1572 | -125.4135 | -125.4456
20.6406 | 125.4044 | -62.0178 | 63.1714 | -0.17067 | 0.013537 | 0.015968 | 0.0051355 | 0.066753 | -0.0016449 | 0.06988 | -62.0544 | 63.1668 | -62.2009 | -62.1735 | 62.915 | 0.091553 | 0.059509 | 0.16479 | 63.1348 | -62.2742 | -0.18311 | -0.004578 | -0.036621 | -0.15564 | -0.25635 | -0.25635 | -0.036621 | 0.14648 | 62.0773 | 62.1826 | 124.9329 | 125.1846 | -0.036621 | 125.1526 | 62.1094 | -0.25635 | 125.1846 | -0.036621 | 62.1094 | 124.9329 | 125.1526 | -125.3723 | -125.4456
21.6406 | 125.4227 | -62.0132 | 63.2034 | -0.11726 | 0.010547 | 0.011696 | 0.0032129 | 0.068462 | -0.0020721 | 0.070735 | -62.0636 | 63.1531 | -62.2055 | -62.1552 | 62.9105 | 0.09613 | 0.036621 | 0.16937 | 63.1393 | -62.2421 | -0.19226 | -0.050354 | -0.050354 | -0.14191 | -0.29297 | -0.22888 | -0.064087 | 0.14191 | 62.0499 | 62.1826 | 124.9237 | 125.1663 | -0.050354 | 125.1526 | 62.1094 | -0.22888 | 125.1663 | -0.050354 | 62.1094 | 124.9237 | 125.1526 | -125.4089 | -125.4456
22.6406 | 125.3906 | -62.0224 | 63.1577 | 0.14214 | 0.010547 | 0.012764 | 0.00086295 | 0.068676 | 0.0017731 | 0.069239 | -62.1368 | 63.1393 | -62.2375 | -62.2375 | 62.8464 | -0.041199 | -0.050354 | 0.013733 | 63.121 | -62.2833 | -0.21515 | -0.018311 | -0.11444 | -0.21515 | -0.31128 | -0.26093 | -0.036621 | 0.10071 | 61.972 | 62.0361 | 124.8688 | 125.1617 | -0.11444 | 125.1434 | 61.9812 | -0.26093 | 125.1617 | -0.11444 | 61.9812 | 124.8688 | 125.1434 | -125.3952 | -125.441
23.6406 | 125.4272 | -62.0178 | 63.1851 | -0.14778 | 0.011401 | 0.014046 | 0.0036401 | 0.067608 | -0.00079046 | 0.069453 | -62.0407 | 63.1897 | -62.2055 | -62.1872 | 62.9242 | 0.082397 | 0.027466 | 0.15564 | 63.1165 | -62.2787 | -0.18768 | 0.004577 | -0.022888 | -0.16937 | -0.26093 | -0.26093 | -0.068665 | 0.1648 | 62.0453 | 62.1735 | 124.942 | 125.2075 | -0.022888 | 125.1343 | 62.1002 | -0.26093 | 125.2075 | -0.022888 | 62.1002 | 124.942 | 125.1343 | -125.3906 | -125.4639
24.6406 | 125.3998 | -62.0224 | 63.2126 | -0.12489 | 0.011615 | 0.014687 | 0.0019311 | 0.066967 | 0.00049134 | 0.06988 | -62.0682 | 63.1851 | -62.2009 | -62.1643 | 62.915 | 0.10529 | 0.064087 | 0.16937 | 63.1165 | -62.2742 | -0.17853 | -0.027465 | -0.045776 | -0.14191 | -0.29755 | -0.25177 | -0.09613 | 0.13275 | 62.0865 | 62.1918 | 124.9374 | 125.2075 | -0.045776 | 125.1389 | 62.1277 | -0.25177 | 125.2075 | -0.045776 | 62.1277 | 124.9374 | 125.1389 | -125.4135 | -125.4868
25.6406 | 125.3906 | -62.0178 | 63.1897 | -0.094376 | 0.013751 | 0.0149 | 0.0044945 | 0.066539 | -0.00014946 | 0.070308 | -62.0544 | 63.1485 | -62.2147 | -62.2055 | 62.9013 | 0.059509 | 0.032043 | 0.14191 | 63.121 | -62.2925 | -0.19684 | -0.041198 | -0.036621 | -0.18768 | -0.28839 | -0.27466 | -0.068664 | 0.16022 | 62.0499 | 62.1597 | 124.9191 | 125.1663 | -0.036621 | 125.1389 | 62.0773 | -0.27466 | 125.1663 | -0.036621 | 62.0773 | 124.9191 | 125.1389 | -125.4044 | -125.4822
26.6406 | 125.3448 | -62.0224 | 63.1943 | -0.048599 | 0.012683 | 0.013405 | 0.0023583 | 0.068035 | -0.00057686 | 0.070521 | -62.0819 | 63.1897 | -62.2055 | -62.2375 | 62.851 | -0.009155 | 0.032043 | 0.064087 | 63.1439 | -62.2787 | -0.18311 | -0.004578 | -0.059509 | -0.21515 | -0.34332 | -0.25635 | -0.050354 | 0.1236 | 62.0544 | 62.0865 | 124.8734 | 125.2121 | -0.059509 | 125.1663 | 62.0132 | -0.25635 | 125.2121 | -0.059509 | 62.0132 | 124.8734 | 125.1663 | -125.3998 | -125.473
27.6406 | 125.5005 | -62.0041 | 63.1302 | 0.16502 | 0.0096921 | 0.012764 | -0.0059729 | 0.068462 | -0.00057686 | 0.069667 | -62.1048 | 63.0249 | -62.2284 | -62.2055 | 62.9059 | 0.09613 | -0.13275 | 0.018311 | 63.0798 | -62.2467 | -0.22431 | -0.10529 | -0.10071 | -0.20142 | -0.2243 | -0.24262 | -0.050354 | 0.1236 | 61.8713 | 62.0224 | 124.91 | 125.029 | -0.10071 | 125.0839 | 62.1002 | -0.24262 | 125.029 | -0.10071 | 62.1002 | 124.91 | 125.0839 | -125.3586 | -125.3769
28.6406 | 125.3586 | -62.0407 | 63.1851 | 0.035324 | 0.011615 | 0.016823 | 0.0042809 | 0.06718 | 0.00070494 | 0.070948 | -62.1185 | 63.1668 | -62.2238 | -62.2696 | 62.8189 | -0.032043 | 0.041199 | 0.018311 | 63.1073 | -62.3245 | -0.18311 | -0.018311 | -0.07782 | -0.22888 | -0.36621 | -0.28381 | -0.07782 | 0.10529 | 62.0819 | 62.059 | 124.8596 | 125.2075 | -0.07782 | 125.148 | 62.0087 | -0.28381 | 125.2075 | -0.07782 | 62.0087 | 124.8596 | 125.148 | -125.4089 | -125.5096
29.6406 | 125.3723 | -62.0361 | 63.1897 | 0.096359 | 0.013965 | 0.014259 | 0.0019311 | 0.068035 | -0.0033539 | 0.06988 | -62.146 | 63.1805 | -62.233 | -62.2833 | 62.7914 | -0.032043 | 0 | 0.027466 | 63.1302 | -62.3154 | -0.19684 | -0.009155 | -0.10986 | -0.24719 | -0.39825 | -0.27924 | -0.059509 | 0.086975 | 62.0361 | 62.0636 | 124.8276 | 125.2167 | -0.10986 | 125.1663 | 62.0041 | -0.27924 | 125.2167 | -0.10986 | 62.0041 | 124.8276 | 125.1663 | -125.4227 | -125.5051
30.6406 | 125.3906 | -62.0499 | 63.1668 | 0.096359 | 0.012469 | 0.013191 | 0.0010767 | 0.068676 | 0.0019867 | 0.069453 | -62.1414 | 63.1577 | -62.2513 | -62.2787 | 62.8098 | -0.027466 | 0.009155 | 0 | 63.1119 | -62.3154 | -0.20142 | -0.009155 | -0.091552 | -0.22888 | -0.35706 | -0.2655 | -0.054932 | 0.10986 | 62.059 | 62.0499 | 124.8596 | 125.2075 | -0.091552 | 125.1617 | 62.0224 | -0.2655 | 125.2075 | -0.091552 | 62.0224 | 124.8596 | 125.1617 | -125.4181 | -125.4822
31.6406 | 125.4135 | -62.027 | 63.1851 | 0.11925 | 0.01076 | 0.015328 | 0.0027855 | 0.068462 | -0.00079046 | 0.071376 | -62.1414 | 63.1485 | -62.233 | -62.2742 | 62.8143 | -0.036621 | -0.018311 | 0.009155 | 63.089 | -62.2971 | -0.20599 | -0.036621 | -0.11444 | -0.24719 | -0.37079 | -0.27008 | -0.096131 | 0.091553 | 62.0087 | 62.0361 | 124.8413 | 125.1755 | -0.11444 | 125.116 | 61.9904 | -0.27008 | 125.1755 | -0.11444 | 61.9904 | 124.8413 | 125.116 | -125.4181 | -125.4822
32.6406 | 125.473 | -61.9995 | 63.1622 | 0.065841 | 0.0088375 | 0.013191 | -0.0068275 | 0.065899 | -0.00057686 | 0.069239 | -62.1231 | 63.0432 | -62.1964 | -62.2147 | 62.8922 | 0.064087 | -0.045776 | 0.14191 | 63.1119 | -62.2055 | -0.19684 | -0.11902 | -0.1236 | -0.21515 | -0.27008 | -0.20599 | -0.050354 | 0.073242 | 61.9537 | 62.1414 | 124.8917 | 125.0427 | -0.1236 | 125.1114 | 62.0636 | -0.20599 | 125.0427 | -0.1236 | 62.0636 | 124.8917 | 125.1114 | -125.3586 | -125.3677
33.6406 | 125.4913 | -62.0041 | 63.1577 | 0.14214 | 0.013751 | 0.020027 | 0.0015039 | 0.066753 | 6.414e-05 | 0.067531 | -62.0728 | 63.0936 | -62.2147 | -62.1597 | 62.8967 | 0.041199 | -0.16479 | 0.13733 | 63.0478 | -62.2742 | -0.21057 | -0.064087 | -0.068665 | -0.15564 | -0.26093 | -0.27008 | -0.10986 | 0.14191 | 61.8393 | 62.1414 | 124.9008 | 125.0977 | -0.068665 | 125.0519 | 62.0453 | -0.27008 | 125.0977 | -0.068665 | 62.0453 | 124.9008 | 125.0519 | -125.3723 | -125.4318
34.6406 | 125.4959 | -62.0087 | 63.1348 | 0.20317 | 0.010974 | 0.016182 | 0.0017175 | 0.067394 | 0.00070494 | 0.068385 | -62.0636 | 63.0569 | -62.2055 | -62.1552 | 62.9059 | 0.068665 | -0.19684 | 0.14191 | 63.0661 | -62.2467 | -0.19684 | -0.07782 | -0.054932 | -0.14648 | -0.22888 | -0.23804 | -0.068665 | 0.14191 | 61.8118 | 62.1506 | 124.9146 | 125.0656 | -0.054932 | 125.0748 | 62.0773 | -0.23804 | 125.0656 | -0.054932 | 62.0773 | 124.9146 | 125.0748 | -125.3403 | -125.3815
35.6406 | 125.5234 | -61.9995 | 63.1439 | 0.11925 | 0.011828 | 0.01191 | 0.0025719 | 0.065899 | 0.0019867 | 0.070735 | -62.0407 | 63.0569 | -62.233 | -62.146 | 62.915 | 0.059509 | -0.17853 | 0.14191 | 63.0707 | -62.2879 | -0.23346 | -0.086975 | -0.041198 | -0.14648 | -0.22888 | -0.28839 | -0.073242 | 0.19226 | 61.821 | 62.1414 | 124.9146 | 125.0565 | -0.041198 | 125.0702 | 62.059 | -0.28839 | 125.0565 | -0.041198 | 62.059 | 124.9146 | 125.0702 | -125.3769 | -125.4318
36.6406 | 125.5188 | -61.9766 | 63.1439 | 0.15739 | 0.0084103 | 0.010841 | 0.0032129 | 0.066753 | -0.0018585 | 0.071803 | -62.0407 | 63.0386 | -62.2009 | -62.146 | 62.9196 | 0.050354 | -0.15564 | 0.14648 | 63.0569 | -62.2604 | -0.2243 | -0.10529 | -0.064086 | -0.16937 | -0.2243 | -0.28381 | -0.086975 | 0.16022 | 61.821 | 62.1231 | 124.8962 | 125.0153 | -0.064086 | 125.0336 | 62.027 | -0.28381 | 125.0153 | -0.064086 | 62.027 | 124.8962 | 125.0336 | -125.3448 | -125.4044
37.6406 | 125.4822 | -61.9904 | 63.1668 | 0.15739 | 0.0088375 | 0.0074233 | 0.00043575 | 0.062481 | -0.0020721 | 0.070308 | -62.0682 | 63.0707 | -62.2192 | -62.146 | 62.9013 | 0.068665 | -0.16479 | 0.15564 | 63.0798 | -62.2238 | -0.22888 | -0.09613 | -0.07782 | -0.15564 | -0.2655 | -0.23346 | -0.086975 | 0.15106 | 61.8256 | 62.146 | 124.8917 | 125.061 | -0.07782 | 125.0702 | 62.059 | -0.23346 | 125.061 | -0.07782 | 62.059 | 124.8917 | 125.0702 | -125.386 | -125.3906
38.6406 | 125.4593 | -62.0041 | 63.1439 | 0.18028 | 0.0071285 | 0.0084915 | 0.00022215 | 0.063976 | 0.0022003 | 0.06988 | -62.0544 | 63.0478 | -62.2101 | -62.1689 | 62.9059 | 0.059509 | -0.17853 | 0.14191 | 63.0203 | -62.233 | -0.20599 | -0.09613 | -0.050354 | -0.16479 | -0.23804 | -0.22888 | -0.1236 | 0.15564 | 61.8256 | 62.146 | 124.91 | 125.0519 | -0.050354 | 125.0244 | 62.0636 | -0.22888 | 125.0519 | -0.050354 | 62.0636 | 124.91 | 125.0244 | -125.354 | -125.3769
39.6406 | 125.4272 | -62.0041 | 63.1348 | 0.14214 | 0.010547 | 0.013405 | -0.0025549 | 0.063976 | 0.00049134 | 0.071162 | -62.0819 | 63.0203 | -62.2101 | -62.1643 | 62.8876 | 0.045776 | -0.15106 | 0.31586 | 63.0661 | -62.2238 | -0.20599 | -0.11444 | -0.07782 | -0.16022 | -0.24719 | -0.21973 | -0.068665 | 0.12817 | 61.853 | 62.3199 | 124.8917 | 125.0244 | -0.07782 | 125.0702 | 62.0499 | -0.21973 | 125.0244 | -0.07782 | 62.0499 | 124.8917 | 125.0702 | -125.3448 | -125.3586
40.6406 | 125.473 | -62.0041 | 63.1622 | 0.012436 | 0.01076 | 0.014259 | -0.0012733 | 0.06419 | 0.0011321 | 0.06988 | -62.1094 | 63.0478 | -62.2101 | -62.2055 | 62.8693 | 0.022888 | -0.086975 | 0.13733 | 63.0707 | -62.2467 | -0.20599 | -0.11444 | -0.10529 | -0.20142 | -0.29297 | -0.24262 | -0.091552 | 0.10071 | 61.9171 | 62.1414 | 124.8734 | 125.0519 | -0.10529 | 125.0748 | 62.027 | -0.24262 | 125.0519 | -0.10529 | 62.027 | 124.8734 | 125.0748 | -125.3723 | -125.4089
41.6406 | 125.4593 | -61.972 | 63.1805 | 0.012436 | 0.0092649 | 0.011055 | -0.0012733 | 0.063335 | 0.00070494 | 0.069667 | -62.1323 | 63.0341 | -62.2055 | -62.1826 | 62.8784 | 0.036621 | -0.050354 | 0.14648 | 63.0661 | -62.2467 | -0.23346 | -0.14648 | -0.16022 | -0.21057 | -0.30212 | -0.27466 | -0.11444 | 0.073242 | 61.9217 | 62.1185 | 124.8505 | 125.0061 | -0.16022 | 125.0381 | 62.0087 | -0.27466 | 125.0061 | -0.16022 | 62.0087 | 124.8505 | 125.0381 | -125.386 | -125.4272
42.6406 | 125.3632 | -62.0224 | 63.2263 | -0.22408 | 0.0096921 | 0.0091323 | 0.0025719 | 0.061626 | 0.00027774 | 0.067531 | -62.1323 | 63.1165 | -62.2238 | -62.1872 | 62.8555 | 0.032043 | 0.14191 | 0.14191 | 63.121 | -62.2513 | -0.20142 | -0.10986 | -0.10986 | -0.1648 | -0.37079 | -0.22888 | -0.10529 | 0.091553 | 62.1643 | 62.1643 | 124.8779 | 125.1389 | -0.10986 | 125.1434 | 62.0544 | -0.22888 | 125.1389 | -0.10986 | 62.0544 | 124.8779 | 125.1434 | -125.4501 | -125.4776
43.6406 | 125.4547 | -61.9904 | 63.1668 | -0.018082 | 0.0090513 | 0.0087051 | -0.0021277 | 0.064617 | -0.0022859 | 0.068171 | -62.0956 | 63.0295 | -62.1872 | -62.1552 | 62.915 | 0.068665 | -0.064087 | 0.17395 | 63.0844 | -62.2147 | -0.19684 | -0.13733 | -0.10529 | -0.16479 | -0.25177 | -0.22431 | -0.082397 | 0.091553 | 61.9263 | 62.1643 | 124.9054 | 125.0198 | -0.10529 | 125.0748 | 62.059 | -0.22431 | 125.0198 | -0.10529 | 62.059 | 124.9054 | 125.0748 | -125.354 | -125.3815
44.6406 | 125.4868 | -61.9812 | 63.1851 | -0.025711 | 0.0088375 | 0.011482 | -0.00063225 | 0.062481 | 0.0019867 | 0.06988 | -62.1002 | 63.0203 | -62.2101 | -62.1506 | 62.9242 | 0.09613 | -0.086975 | 0.20599 | 63.0753 | -62.2009 | -0.22888 | -0.16479 | -0.11902 | -0.16937 | -0.26093 | -0.21973 | -0.10986 | 0.10986 | 61.8942 | 62.1872 | 124.9054 | 125.0015 | -0.11902 | 125.0565 | 62.0773 | -0.21973 | 125.0015 | -0.11902 | 62.0773 | 124.9054 | 125.0565 | -125.3952 | -125.386
45.6406 | 125.5051 | -61.9812 | 63.1714 | -0.079117 | 0.0094785 | 0.01191 | 0.0017175 | 0.062694 | -0.0016449 | 0.069026 | -62.0636 | 63.0386 | -62.2101 | -62.1368 | 62.9105 | 0.091553 | -0.068665 | 0.21057 | 63.0707 | -62.233 | -0.22888 | -0.13275 | -0.082398 | -0.15564 | -0.26093 | -0.25177 | -0.10071 | 0.14648 | 61.9125 | 62.1918 | 124.8917 | 125.0198 | -0.082398 | 125.0519 | 62.0728 | -0.25177 | 125.0198 | -0.082398 | 62.0728 | 124.8917 | 125.0519 | -125.3815 | -125.4044
46.6406 | 125.5142 | -61.9629 | 63.1622 | 0.065841 | 0.0081967 | 0.013191 | 8.546e-06 | 0.062694 | -0.0014313 | 0.068385 | -62.0224 | 63.0203 | -62.2101 | -62.114 | 62.9517 | 0.1236 | -0.086975 | 0.23804 | 63.0524 | -62.2101 | -0.24719 | -0.14191 | -0.059509 | -0.15106 | -0.21057 | -0.24719 | -0.10986 | 0.18768 | 61.8759 | 62.2009 | 124.9146 | 124.9832 | -0.059509 | 125.0153 | 62.0865 | -0.24719 | 124.9832 | -0.059509 | 62.0865 | 124.9146 | 125.0153 | -125.3723 | -125.3723
47.6406 | 125.3632 | -62.0132 | 63.2217 | -0.21645 | 0.010119 | 0.0095595 | 0.0019311 | 0.063549 | 0.00027774 | 0.068171 | -62.1094 | 63.0936 | -62.1964 | -62.1918 | 62.8555 | 0.054932 | 0.13275 | 0.16479 | 63.1302 | -62.2467 | -0.18311 | -0.12817 | -0.09613 | -0.17853 | -0.36621 | -0.23346 | -0.091553 | 0.086975 | 62.146 | 62.178 | 124.8688 | 125.1068 | -0.09613 | 125.1434 | 62.0682 | -0.23346 | 125.1068 | -0.09613 | 62.0682 | 124.8688 | 125.1434 | -125.4181 | -125.4684
48.6406 | 125.4913 | -61.9675 | 63.2172 | -0.22408 | 0.0088375 | 0.012123 | -0.00063225 | 0.065258 | -0.0016449 | 0.068599 | -62.027 | 63.0615 | -62.178 | -62.0728 | 62.9562 | 0.16479 | -0.032043 | 0.28839 | 63.0798 | -62.1872 | -0.21057 | -0.15564 | -0.05951 | -0.10529 | -0.26093 | -0.21973 | -0.13733 | 0.15106 | 61.9354 | 62.2559 | 124.9237 | 125.029 | -0.05951 | 125.0473 | 62.1323 | -0.21973 | 125.029 | -0.05951 | 62.1323 | 124.9237 | 125.0473 | -125.3952 | -125.4044
49.6406 | 125.4318 | -61.9629 | 63.1989 | -0.30037 | 0.0069149 | 0.010414 | 0.00086295 | 0.06419 | -0.00057686 | 0.06689 | -62.0453 | 63.0615 | -62.1826 | -62.0911 | 62.9562 | 0.14648 | -0.013733 | 0.26093 | 63.1073 | -62.1964 | -0.21973 | -0.13733 | -0.082397 | -0.12817 | -0.24262 | -0.23346 | -0.091553 | 0.13733 | 61.9492 | 62.2238 | 124.9191 | 125.0244 | -0.082397 | 125.0702 | 62.1094 | -0.23346 | 125.0244 | -0.082397 | 62.1094 | 124.9191 | 125.0702 | -125.3815 | -125.3952
50.6406 | 125.473 | -61.9995 | 63.2172 | -0.26222 | 0.0077695 | 0.0091323 | 8.546e-06 | 0.064403 | -0.0024995 | 0.067531 | -62.0453 | 63.0615 | -62.1689 | -62.1231 | 62.9471 | 0.1236 | 0.045776 | 0.22888 | 63.1119 | -62.2055 | -0.16937 | -0.15564 | -0.045776 | -0.1236 | -0.27008 | -0.20599 | -0.10529 | 0.1236 | 62.0453 | 62.2284 | 124.9466 | 125.061 | -0.045776 | 125.1114 | 62.1231 | -0.20599 | 125.061 | -0.045776 | 62.1231 | 124.9466 | 125.1114 | -125.386 | -125.4227
51.6406 | 125.3815 | -61.9995 | 63.2126 | -0.26985 | 0.0096921 | 0.010841 | 0.0034265 | 0.065685 | -0.0024995 | 0.066676 | -62.1506 | 63.0707 | -62.2192 | -62.1277 | 62.9105 | 0.086975 | 0.10529 | 0.20599 | 63.1439 | -62.1964 | -0.21973 | -0.14191 | -0.15106 | -0.12817 | -0.30212 | -0.19684 | -0.068664 | 0.068664 | 62.1048 | 62.2055 | 124.91 | 125.0702 | -0.15106 | 125.1434 | 62.0865 | -0.19684 | 125.0702 | -0.15106 | 62.0865 | 124.91 | 125.1434 | -125.4318 | -125.4089
52.6406 | 125.3448 | -62.0316 | 63.1851 | 0.073471 | 0.010547 | 0.015328 | 0.0083397 | 0.065258 | 0.00070494 | 0.067958 | -62.1002 | 63.1531 | -62.2055 | -62.233 | 62.8098 | -0.050354 | 0.004578 | 0.013733 | 63.1256 | -62.2971 | -0.17395 | -0.032044 | -0.068665 | -0.20142 | -0.37537 | -0.2655 | -0.05951 | 0.10529 | 62.0361 | 62.0453 | 124.8413 | 125.1846 | -0.068665 | 125.1572 | 61.9812 | -0.2655 | 125.1846 | -0.068665 | 61.9812 | 124.8413 | 125.1572 | -125.3906 | -125.4822
53.6406 | 125.3906 | -62.0087 | 63.2126 | -0.20882 | 0.011188 | 0.01255 | -0.00020505 | 0.066539 | 0.00027774 | 0.070521 | -62.1002 | 63.1302 | -62.2101 | -62.1826 | 62.8693 | 0.064087 | 0.13275 | 0.15106 | 63.1393 | -62.2513 | -0.20142 | -0.082397 | -0.091553 | -0.17395 | -0.34332 | -0.24262 | -0.073242 | 0.10986 | 62.1414 | 62.1597 | 124.8779 | 125.1389 | -0.091553 | 125.148 | 62.0728 | -0.24262 | 125.1389 | -0.091553 | 62.0728 | 124.8779 | 125.148 | -125.4227 | -125.4639
54.6406 | 125.4135 | -62.0178 | 63.2263 | -0.23933 | 0.011401 | 0.0095595 | 0.0036401 | 0.066539 | -0.00057686 | 0.067531 | -62.1002 | 63.1714 | -62.2147 | -62.1872 | 62.8784 | 0.073242 | 0.13733 | 0.14648 | 63.1439 | -62.2375 | -0.19684 | -0.054931 | -0.082398 | -0.16937 | -0.3479 | -0.21973 | -0.082397 | 0.11444 | 62.1552 | 62.1643 | 124.8962 | 125.1892 | -0.082398 | 125.1617 | 62.0911 | -0.21973 | 125.1892 | -0.082398 | 62.0911 | 124.8962 | 125.1617 | -125.441 | -125.4639
55.6406 | 125.4364 | -62.0316 | 63.176 | -0.20882 | 0.011188 | 0.016823 | 0.0017175 | 0.066326 | -0.0016449 | 0.069026 | -62.0956 | 63.1622 | -62.2055 | -62.1597 | 62.8876 | 0.059509 | 0.10986 | 0.13733 | 63.1439 | -62.2467 | -0.17395 | -0.013733 | -0.064087 | -0.12817 | -0.28839 | -0.21515 | -0.032043 | 0.10986 | 62.1414 | 62.1689 | 124.9191 | 125.1938 | -0.064087 | 125.1755 | 62.0911 | -0.21515 | 125.1938 | -0.064087 | 62.0911 | 124.9191 | 125.1755 | -125.3815 | -125.4227
56.6406 | 125.3998 | -62.0087 | 63.1989 | -0.25459 | 0.011828 | 0.018318 | 0.0049219 | 0.066967 | -0.0037811 | 0.067958 | -62.0682 | 63.1622 | -62.2101 | -62.1689 | 62.8738 | 0.10986 | 0.091553 | 0.17395 | 63.1439 | -62.233 | -0.20142 | -0.036622 | -0.059509 | -0.16022 | -0.32501 | -0.2243 | -0.054932 | 0.14191 | 62.1002 | 62.1826 | 124.8825 | 125.1709 | -0.059509 | 125.1526 | 62.1185 | -0.2243 | 125.1709 | -0.059509 | 62.1185 | 124.8825 | 125.1526 | -125.4089 | -125.4318
57.6406 | 125.3952 | -62.027 | 63.2034 | 0.027695 | 0.012256 | 0.018105 | 0.0040673 | 0.067821 | -0.00079046 | 0.067958 | -62.0636 | 63.1531 | -62.2421 | -62.2009 | 62.8738 | 0.027466 | 0.022888 | 0.091553 | 63.1439 | -62.2604 | -0.21515 | -0.050354 | -0.036621 | -0.17395 | -0.32959 | -0.23346 | -0.059509 | 0.17853 | 62.0499 | 62.1185 | 124.9008 | 125.1801 | -0.036621 | 125.1709 | 62.0544 | -0.23346 | 125.1801 | -0.036621 | 62.0544 | 124.9008 | 125.1709 | -125.4456 | -125.4639
58.6406 | 125.3952 | -62.0132 | 63.1622 | -0.14778 | 0.011401 | 0.014046 | 0.0034265 | 0.067394 | -0.0010041 | 0.070094 | -62.0407 | 63.1485 | -62.233 | -62.1414 | 62.9059 | 0.10529 | 0.027466 | 0.16479 | 63.1393 | -62.2467 | -0.21973 | -0.013732 | -0.027465 | -0.12817 | -0.25635 | -0.23346 | -0.022888 | 0.19226 | 62.0407 | 62.178 | 124.9191 | 125.1617 | -0.027465 | 125.1526 | 62.1185 | -0.23346 | 125.1617 | -0.027465 | 62.1185 | 124.9191 | 125.1526 | -125.3952 | -125.4089
59.6406 | 125.4501 | -61.9949 | 63.1851 | -0.14778 | 0.012042 | 0.013619 | 0.0047081 | 0.068889 | -0.00036306 | 0.070735 | -62.0407 | 63.1622 | -62.2238 | -62.1597 | 62.8876 | 0.091553 | 0.045776 | 0.16479 | 63.1348 | -62.2467 | -0.22888 | -0.022889 | -0.045776 | -0.16479 | -0.29755 | -0.25177 | -0.050354 | 0.18311 | 62.0407 | 62.1597 | 124.8825 | 125.1572 | -0.045776 | 125.1297 | 62.0865 | -0.25177 | 125.1572 | -0.045776 | 62.0865 | 124.8825 | 125.1297 | -125.4089 | -125.4318
60.6406 | 125.4272 | -61.9858 | 63.1851 | -0.063858 | 0.012683 | 0.014046 | 0.0034265 | 0.069744 | -0.0018585 | 0.069026 | -62.0316 | 63.1668 | -62.2147 | -62.1506 | 62.8967 | 0.091553 | 0.013733 | 0.14648 | 63.1165 | -62.233 | -0.22888 | -0.018311 | -0.045776 | -0.16479 | -0.28839 | -0.24719 | -0.068665 | 0.18311 | 61.9995 | 62.1323 | 124.8825 | 125.1526 | -0.045776 | 125.1022 | 62.0773 | -0.24719 | 125.1526 | -0.045776 | 62.0773 | 124.8825 | 125.1022 | -125.3998 | -125.4181
61.6406 | 125.3677 | -62.027 | 63.1851 | -0.018082 | 0.011615 | 0.013619 | 0.0032129 | 0.070385 | -0.0010041 | 0.068385 | -62.0773 | 63.1622 | -62.2238 | -62.2009 | 62.8464 | 0.027466 | 0.027466 | 0.09613 | 63.121 | -62.2559 | -0.19684 | -0.022889 | -0.050354 | -0.17395 | -0.33874 | -0.22888 | -0.064087 | 0.14648 | 62.0544 | 62.1231 | 124.8734 | 125.1892 | -0.050354 | 125.148 | 62.0544 | -0.22888 | 125.1892 | -0.050354 | 62.0544 | 124.8734 | 125.148 | -125.4089 | -125.441
62.6406 | 125.4456 | -61.9812 | 63.1348 | 0.14976 | 0.010333 | 0.01725 | -0.0038367 | 0.067821 | 0.0013457 | 0.073298 | -62.059 | 63.0432 | -62.2467 | -62.1643 | 62.9333 | 0.064087 | -0.15564 | 0.13733 | 63.0798 | -62.2238 | -0.2655 | -0.091553 | -0.07782 | -0.18311 | -0.20142 | -0.24262 | -0.054932 | 0.18768 | 61.8256 | 62.1185 | 124.9146 | 125.0244 | -0.07782 | 125.061 | 62.0453 | -0.24262 | 125.0244 | -0.07782 | 62.0453 | 124.9146 | 125.061 | -125.3815 | -125.3586
63.6406 | 125.3586 | -62.0361 | 63.1714 | 0.08873 | 0.011615 | 0.015968 | 0.0034265 | 0.068462 | 0.0015595 | 0.068385 | -62.1277 | 63.1577 | -62.2375 | -62.265 | 62.796 | -0.036621 | 0.018311 | 0.009155 | 63.1073 | -62.2971 | -0.20142 | -0.013733 | -0.091553 | -0.22888 | -0.37537 | -0.26093 | -0.064087 | 0.10986 | 62.0544 | 62.0453 | 124.8322 | 125.1938 | -0.091553 | 125.1434 | 61.9995 | -0.26093 | 125.1938 | -0.091553 | 61.9995 | 124.8322 | 125.1434 | -125.4089 | -125.4684
64.6406 | 125.3723 | -62.0407 | 63.176 | 0.12688 | 0.011188 | 0.014473 | 0.0042809 | 0.066967 | 0.00070494 | 0.069026 | -62.0956 | 63.1622 | -62.233 | -62.2421 | 62.8143 | -0.009155 | 0.022888 | 0.050354 | 63.1027 | -62.2879 | -0.19226 | -0.013733 | -0.054932 | -0.20142 | -0.36163 | -0.24719 | -0.073242 | 0.13733 | 62.0636 | 62.0911 | 124.855 | 125.2029 | -0.054932 | 125.1434 | 62.0316 | -0.24719 | 125.2029 | -0.054932 | 62.0316 | 124.855 | 125.1434 | -125.4089 | -125.4639
65.6406 | 125.3494 | -62.0544 | 63.1989 | 0.065841 | 0.011188 | 0.012123 | 0.0042809 | 0.071453 | 6.414e-05 | 0.068171 | -62.1094 | 63.1668 | -62.2421 | -62.2513 | 62.8235 | -0.013733 | 0.045776 | 0.032043 | 63.1165 | -62.2787 | -0.18768 | -0.032044 | -0.054932 | -0.19684 | -0.37537 | -0.22431 | -0.082398 | 0.13275 | 62.1002 | 62.0865 | 124.8779 | 125.2213 | -0.054932 | 125.1709 | 62.0407 | -0.22431 | 125.2213 | -0.054932 | 62.0407 | 124.8779 | 125.1709 | -125.441 | -125.4776
66.6406 | 125.3769 | -62.0499 | 63.1622 | 0.027695 | 0.010974 | 0.015114 | 0.0036401 | 0.068889 | -0.0010041 | 0.069667 | -62.1185 | 63.176 | -62.2421 | -62.2604 | 62.8143 | -0.045776 | 0.050354 | 0.050354 | 63.1119 | -62.2833 | -0.19226 | 0.013733 | -0.068664 | -0.21057 | -0.3479 | -0.23346 | -0.050354 | 0.1236 | 62.1002 | 62.1002 | 124.8642 | 125.2258 | -0.068664 | 125.1617 | 62.0041 | -0.23346 | 125.2258 | -0.068664 | 62.0041 | 124.8642 | 125.1617 | -125.4044 | -125.4456
67.6406 | 125.441 | -61.9766 | 63.1165 | 0.14214 | 0.0088375 | 0.018959 | -0.0031959 | 0.068676 | -0.0010041 | 0.068812 | -62.0728 | 63.0386 | -62.2284 | -62.1552 | 62.9059 | 0.064087 | -0.16937 | 0.12817 | 63.0798 | -62.2238 | -0.25177 | -0.07782 | -0.09613 | -0.17853 | -0.21057 | -0.24719 | -0.036621 | 0.15564 | 61.8073 | 62.1048 | 124.8825 | 125.0153 | -0.09613 | 125.0565 | 62.0407 | -0.24719 | 125.0153 | -0.09613 | 62.0407 | 124.8825 | 125.0565 | -125.3448 | -125.3403
68.6406 | 125.3952 | -62.059 | 63.1531 | 0.14214 | 0.010119 | 0.015968 | 0.0017175 | 0.066539 | -0.00057686 | 0.070521 | -62.1185 | 63.1027 | -62.2238 | -62.2513 | 62.8098 | -0.032043 | -0.013733 | 0.009155 | 63.0981 | -62.2833 | -0.16479 | -0.050354 | -0.059509 | -0.19226 | -0.34332 | -0.2243 | -0.054931 | 0.10529 | 62.0453 | 62.0682 | 124.8688 | 125.1617 | -0.059509 | 125.1572 | 62.027 | -0.2243 | 125.1617 | -0.059509 | 62.027 | 124.8688 | 125.1572 | -125.3769 | -125.4364
69.6406 | 125.3586 | -62.0499 | 63.1714 | 0.11162 | 0.014178 | 0.012337 | 0.0029993 | 0.066112 | 0.0017731 | 0.069453 | -62.1185 | 63.1302 | -62.2375 | -62.233 | 62.8052 | -0.027466 | -0.041199 | 0.032043 | 63.1073 | -62.2787 | -0.18768 | -0.041199 | -0.068664 | -0.1831 | -0.36621 | -0.22888 | -0.064087 | 0.11902 | 62.0087 | 62.0819 | 124.855 | 125.1801 | -0.068664 | 125.1572 | 62.0224 | -0.22888 | 125.1801 | -0.068664 | 62.0224 | 124.855 | 125.1572 | -125.4089 | -125.4501
70.6406 | 125.3677 | -62.0224 | 63.1439 | 0.24132 | 0.013537 | 0.011696 | 0.0025719 | 0.067608 | 0.00027774 | 0.069667 | -62.1231 | 63.1165 | -62.2238 | -62.2513 | 62.8189 | -0.050354 | -0.032043 | 0.036621 | 63.0936 | -62.2925 | -0.20142 | -0.027466 | -0.10071 | -0.22888 | -0.32501 | -0.27008 | -0.050354 | 0.10071 | 61.9904 | 62.059 | 124.8413 | 125.1389 | -0.10071 | 125.116 | 61.972 | -0.27008 | 125.1389 | -0.10071 | 61.972 | 124.8413 | 125.116 | -125.3677 | -125.4364
71.6406 | 125.3815 | -62.0316 | 63.1577 | 0.15739 | 0.014606 | 0.0149 | 0.0029993 | 0.066326 | 0.00091854 | 0.070521 | -62.114 | 63.1348 | -62.2559 | -62.2513 | 62.8235 | -0.018311 | -0.050354 | 0.032043 | 63.0981 | -62.2879 | -0.2243 | -0.022888 | -0.082398 | -0.21973 | -0.33417 | -0.25635 | -0.059509 | 0.14191 | 61.9812 | 62.0636 | 124.855 | 125.1663 | -0.082398 | 125.1297 | 62.0132 | -0.25635 | 125.1663 | -0.082398 | 62.0132 | 124.855 | 125.1297 | -125.4135 | -125.4456
72.6406 | 125.4181 | -61.9904 | 63.1439 | 0.08873 | 0.0088375 | 0.014046 | -0.0064003 | 0.067608 | 6.414e-05 | 0.070735 | -62.1094 | 63.0524 | -62.2192 | -62.2147 | 62.883 | 0.041199 | -0.064087 | 0.11444 | 63.0615 | -62.2467 | -0.22888 | -0.091553 | -0.11902 | -0.22431 | -0.26093 | -0.25635 | -0.082398 | 0.10986 | 61.9263 | 62.1048 | 124.8734 | 125.0427 | -0.11902 | 125.0519 | 62.0316 | -0.25635 | 125.0427 | -0.11902 | 62.0316 | 124.8734 | 125.0519 | -125.3632 | -125.3906
73.6406 | 125.4639 | -62.0041 | 63.1577 | 0.12688 | 0.011615 | 0.013191 | 0.0012903 | 0.06718 | 0.0017731 | 0.070521 | -62.114 | 63.1165 | -62.2375 | -62.2238 | 62.8235 | -0.027466 | -0.086975 | 0.050354 | 63.0798 | -62.265 | -0.23346 | -0.041199 | -0.10986 | -0.21973 | -0.33417 | -0.26093 | -0.07782 | 0.1236 | 61.9171 | 62.0544 | 124.8276 | 125.1205 | -0.10986 | 125.0839 | 61.9766 | -0.26093 | 125.1205 | -0.10986 | 61.9766 | 124.8276 | 125.0839 | -125.3952 | -125.4227
74.6406 | 125.4089 | -62.0224 | 63.1439 | 0.15739 | 0.013751 | 0.016396 | 0.0010767 | 0.06718 | -0.00079046 | 0.070735 | -62.1094 | 63.1165 | -62.2375 | -62.2238 | 62.7823 | -0.004578 | 0.027466 | -0.050354 | 63.1073 | -62.2879 | -0.21515 | -0.027466 | -0.086975 | -0.20142 | -0.36163 | -0.2655 | -0.036621 | 0.12817 | 62.0499 | 61.972 | 124.8047 | 125.1389 | -0.086975 | 125.1297 | 62.0178 | -0.2655 | 125.1389 | -0.086975 | 62.0178 | 124.8047 | 125.1297 | -125.3815 | -125.4318
75.6406 | 125.4684 | -61.9858 | 63.1348 | 0.19554 | 0.01076 | 0.012978 | 0.0010767 | 0.066112 | 0.00049134 | 0.070308 | -62.0407 | 63.0707 | -62.2101 | -62.1552 | 62.8922 | 0.059509 | -0.19226 | 0.14648 | 63.0432 | -62.2787 | -0.2243 | -0.064087 | -0.054931 | -0.16937 | -0.24262 | -0.29297 | -0.091553 | 0.16937 | 61.7935 | 62.1323 | 124.8779 | 125.0565 | -0.054931 | 125.029 | 62.0453 | -0.29297 | 125.0565 | -0.054931 | 62.0453 | 124.8779 | 125.029 | -125.3448 | -125.4135
76.6406 | 125.4593 | -61.972 | 63.1165 | 0.17265 | 0.011401 | 0.012764 | 0.00043575 | 0.066326 | 0.0015595 | 0.070735 | -62.0224 | 63.0753 | -62.2055 | -62.1552 | 62.9196 | 0.050354 | -0.17853 | 0.15106 | 63.0661 | -62.2604 | -0.23346 | -0.041199 | -0.050354 | -0.1831 | -0.19684 | -0.28839 | -0.050354 | 0.18311 | 61.7935 | 62.1231 | 124.8917 | 125.0473 | -0.050354 | 125.0381 | 62.0224 | -0.28839 | 125.0473 | -0.050354 | 62.0224 | 124.8917 | 125.0381 | -125.322 | -125.3769
77.6406 | 125.4822 | -61.9675 | 63.1714 | -0.033341 | 0.0094785 | 0.015114 | -0.0042639 | 0.062908 | -0.00014946 | 0.069239 | -62.0911 | 63.0478 | -62.2101 | -62.1689 | 62.9105 | 0.11444 | -0.041199 | 0.20142 | 63.1073 | -62.2101 | -0.24262 | -0.1236 | -0.1236 | -0.20142 | -0.26093 | -0.24262 | -0.064087 | 0.11902 | 61.9263 | 62.1689 | 124.8779 | 125.0153 | -0.1236 | 125.0748 | 62.0819 | -0.24262 | 125.0153 | -0.1236 | 62.0819 | 124.8779 | 125.0748 | -125.3815 | -125.3815
78.6406 | 125.4913 | -61.9583 | 63.1531 | 0.21843 | 0.0096921 | 0.013832 | 0.0034265 | 0.063976 | -0.0018585 | 0.070094 | -62.0407 | 63.0524 | -62.1918 | -62.1277 | 62.9059 | 0.054932 | -0.17853 | 0.15564 | 63.0569 | -62.2467 | -0.23346 | -0.10071 | -0.082397 | -0.16937 | -0.24719 | -0.28839 | -0.09613 | 0.15106 | 61.7798 | 62.114 | 124.8642 | 125.0107 | -0.082397 | 125.0153 | 62.0132 | -0.28839 | 125.0107 | -0.082397 | 62.0132 | 124.8642 | 125.0153 | -125.3448 | -125.3998
79.6406 | 125.4639 | -62.0132 | 63.1393 | 0.042953 | 0.012256 | 0.014687 | 0.0036401 | 0.065899 | -0.0016449 | 0.068171 | -62.0819 | 63.0707 | -62.2284 | -62.1552 | 62.883 | 0.027466 | -0.15564 | 0.11902 | 63.0386 | -62.2421 | -0.21515 | -0.068664 | -0.068664 | -0.14191 | -0.25635 | -0.22888 | -0.10071 | 0.14648 | 61.8576 | 62.1323 | 124.8962 | 125.0839 | -0.068664 | 125.0519 | 62.0407 | -0.22888 | 125.0839 | -0.068664 | 62.0407 | 124.8962 | 125.0519 | -125.3677 | -125.3815
80.6406 | 125.473 | -61.9904 | 63.1531 | 0.18028 | 0.0094785 | 0.0149 | 0.0010767 | 0.065258 | -0.0010041 | 0.072017 | -62.0407 | 63.0157 | -62.1918 | -62.146 | 62.9242 | 0.041199 | -0.18768 | 0.15106 | 63.0341 | -62.2375 | -0.20142 | -0.13733 | -0.050354 | -0.15564 | -0.22888 | -0.24719 | -0.11902 | 0.15106 | 61.8027 | 62.1414 | 124.9145 | 125.0061 | -0.050354 | 125.0244 | 62.0316 | -0.24719 | 125.0061 | -0.050354 | 62.0316 | 124.9145 | 125.0244 | -125.3448 | -125.3906
81.6406 | 125.4456 | -61.9675 | 63.1348 | 0.14976 | 0.0077695 | 0.013405 | 0.0010767 | 0.063121 | -0.0014313 | 0.069667 | -62.0499 | 63.0066 | -62.2101 | -62.1368 | 62.9105 | 0.064087 | -0.20599 | 0.15106 | 63.0615 | -62.2559 | -0.24262 | -0.12817 | -0.082398 | -0.16937 | -0.22431 | -0.28839 | -0.073243 | 0.16022 | 61.7615 | 62.1185 | 124.8779 | 124.9741 | -0.082398 | 125.029 | 62.0316 | -0.28839 | 124.9741 | -0.082398 | 62.0316 | 124.8779 | 125.029 | -125.3448 | -125.3906
82.6406 | 125.4959 | -61.9537 | 63.1577 | -0.04097 | 0.0092649 | 0.0080643 | -0.0012733 | 0.063549 | -0.00079046 | 0.070735 | -62.0728 | 63.0341 | -62.1735 | -62.1002 | 62.9471 | 0.13275 | -0.073242 | 0.25177 | 63.0798 | -62.1918 | -0.21973 | -0.1236 | -0.11902 | -0.14648 | -0.21057 | -0.23804 | -0.07782 | 0.10071 | 61.8805 | 62.2055 | 124.9008 | 124.9878 | -0.11902 | 125.0336 | 62.0865 | -0.23804 | 124.9878 | -0.11902 | 62.0865 | 124.9008 | 125.0336 | -125.3311 | -125.3494
83.6406 | 125.4456 | -61.9904 | 63.1622 | -1.4677 | 0.011188 | 0.011269 | 0.0010767 | 0.064617 | 6.414e-05 | 0.069026 | -62.146 | 63.0341 | -62.1918 | -62.1918 | 62.8464 | 0.032043 | -0.1236 | 0.11902 | 63.0569 | -62.2284 | -0.20142 | -0.12817 | -0.15564 | -0.20142 | -0.31586 | -0.23804 | -0.10528 | 0.045776 | 61.8668 | 62.1094 | 124.8367 | 125.0244 | -0.15564 | 125.0473 | 62.0224 | -0.23804 | 125.0244 | -0.15564 | 62.0224 | 124.8367 | 125.0473 | -125.354 | -125.3906
84.6406 | 125.4272 | -61.9949 | 63.1668 | -0.26222 | 0.0090513 | 0.011269 | -0.0012733 | 0.06419 | -0.00014946 | 0.068599 | -62.1094 | 63.0386 | -62.2375 | -62.178 | 62.851 | 0.013733 | -0.11444 | 0.13275 | 63.1027 | -62.2055 | -0.24262 | -0.12817 | -0.11444 | -0.18311 | -0.31586 | -0.21057 | -0.064087 | 0.12817 | 61.8805 | 62.1277 | 124.8459 | 125.0336 | -0.11444 | 125.0977 | 62.0087 | -0.21057 | 125.0336 | -0.11444 | 62.0087 | 124.8459 | 125.0977 | -125.4044 | -125.3723
85.6406 | 125.4593 | -61.9583 | 63.176 | -0.22408 | 0.0056333 | 0.012123 | -0.0012733 | 0.062267 | -0.0022859 | 0.069239 | -62.027 | 63.0203 | -62.1826 | -62.0865 | 62.9471 | 0.17395 | -0.032043 | 0.30212 | 63.0661 | -62.178 | -0.2243 | -0.15564 | -0.068665 | -0.12817 | -0.22888 | -0.21973 | -0.10986 | 0.15564 | 61.9263 | 62.2604 | 124.9054 | 124.9786 | -0.068665 | 125.0244 | 62.1323 | -0.21973 | 124.9786 | -0.068665 | 62.1323 | 124.9054 | 125.0244 | -125.3586 | -125.354
86.6406 | 125.3723 | -62.0041 | 63.1348 | 0.14976 | 0.0092649 | 0.012764 | 0.0036401 | 0.066326 | -0.0016449 | 0.069667 | -62.0407 | 62.9974 | -62.2009 | -62.1552 | 62.8876 | 0.041199 | 0.064087 | 0.55389 | 63.1119 | -62.178 | -0.19684 | -0.13733 | -0.036621 | -0.15106 | -0.24719 | -0.17395 | -0.022889 | 0.16022 | 62.0682 | 62.558 | 124.8917 | 125.0015 | -0.036621 | 125.116 | 62.0453 | -0.17395 | 125.0015 | -0.036621 | 62.0453 | 124.8917 | 125.116 | -125.3357 | -125.3128
87.6406 | 125.3906 | -61.972 | 63.2126 | 0.035324 | 0.0086239 | 0.010201 | 0.0015039 | 0.062694 | -0.0014313 | 0.064967 | -62.0636 | 63.0936 | -62.1643 | -62.146 | 62.9059 | 0.09613 | 0.082397 | 0.2243 | 63.1165 | -62.2284 | -0.19226 | -0.11902 | -0.091553 | -0.17395 | -0.3067 | -0.25635 | -0.09613 | 0.10071 | 62.0544 | 62.1963 | 124.8779 | 125.0656 | -0.091553 | 125.0885 | 62.0682 | -0.25635 | 125.0656 | -0.091553 | 62.0682 | 124.8779 | 125.0885 | -125.3769 | -125.441
88.6406 | 125.4044 | -61.9858 | 63.1668 | -0.018082 | 0.010333 | 0.01191 | -0.0012733 | 0.061626 | 0.0011321 | 0.068171 | -62.1002 | 63.0249 | -62.2055 | -62.1506 | 62.8967 | 0.064087 | -0.059509 | 0.16479 | 63.089 | -62.233 | -0.21973 | -0.14191 | -0.11444 | -0.16479 | -0.27008 | -0.24719 | -0.07782 | 0.10529 | 61.9263 | 62.1506 | 124.8825 | 125.0107 | -0.11444 | 125.0748 | 62.0499 | -0.24719 | 125.0107 | -0.11444 | 62.0499 | 124.8825 | 125.0748 | -125.3723 | -125.3998
89.6406 | 125.4501 | -61.9492 | 63.176 | -0.025711 | 0.0069149 | 0.010841 | -0.0027687 | 0.06184 | 0.00070494 | 0.067958 | -62.0865 | 63.0249 | -62.1918 | -62.1552 | 62.8922 | 0.073242 | -0.07782 | 0.17853 | 63.0569 | -62.2284 | -0.24261 | -0.15106 | -0.13733 | -0.20599 | -0.28381 | -0.27924 | -0.11902 | 0.10529 | 61.8713 | 62.1277 | 124.8413 | 124.9741 | -0.13733 | 125.0061 | 62.0224 | -0.27924 | 124.9741 | -0.13733 | 62.0224 | 124.8413 | 125.0061 | -125.3677 | -125.4044
90.6562 | 125.3815 | -62.0041 | 63.1851 | -0.071488 | 0.010974 | 0.014046 | 0.0079125 | 0.066539 | -0.0012177 | 0.067958 | -62.0087 | 63.1393 | -62.1872 | -62.146 | 62.851 | 0.027466 | 0.009155 | 0.13275 | 63.0981 | -62.2513 | -0.18311 | -0.045777 | -0.004578 | -0.14191 | -0.33417 | -0.24719 | -0.086975 | 0.17853 | 62.0132 | 62.1368 | 124.855 | 125.1434 | -0.004578 | 125.1022 | 62.0316 | -0.24719 | 125.1434 | -0.004578 | 62.0316 | 124.855 | 125.1022 | -125.3723 | -125.4364
91.6406 | 125.4639 | -61.9858 | 63.1577 | 0.0048064 | 0.0092649 | 0.012123 | -0.0019141 | 0.065685 | -0.0012177 | 0.065608 | -62.0865 | 63.0249 | -62.2147 | -61.7706 | 63.1714 | -0.022888 | -0.09613 | 0.19226 | 63.0844 | -62.1826 | -0.22888 | -0.13275 | -0.10071 | 0.21515 | 0.013733 | -0.19684 | -0.073242 | 0.12817 | 61.8896 | 62.178 | 125.1572 | 125.0107 | -0.10071 | 125.0702 | 61.9629 | -0.19684 | 125.0107 | -0.10071 | 61.9629 | 125.1572 | 125.0702 | -125.3723 | -125.3403
92.6406 | 125.4272 | -61.9858 | 63.1393 | -3.5429 | 0.0086239 | 0.013832 | -0.0012733 | 0.063549 | -0.0022859 | 0.068599 | -62.3154 | 63.0249 | -62.2192 | -62.1414 | 62.9059 | 0.11444 | -0.073242 | 0.1831 | 63.0569 | -62.2009 | -0.23346 | -0.11444 | -0.32959 | -0.15564 | -0.23346 | -0.21515 | -0.082397 | -0.096131 | 61.9125 | 62.1689 | 124.8917 | 125.0107 | -0.32959 | 125.0427 | 62.1002 | -0.21515 | 125.0107 | -0.32959 | 62.1002 | 124.8917 | 125.0427 | -125.3586 | -125.3403
93.6406 | 125.4913 | -61.9308 | 63.1805 | -0.11726 | 0.0084103 | 0.0095595 | -0.0012733 | 0.063549 | -0.0018585 | 0.068171 | -62.0316 | 63.0341 | -62.1643 | -62.059 | 62.97 | 0.16022 | -0.07782 | 0.27008 | 63.0661 | -62.2009 | -0.23346 | -0.14648 | -0.10071 | -0.12817 | -0.21057 | -0.27008 | -0.11444 | 0.13275 | 61.853 | 62.2009 | 124.9008 | 124.9649 | -0.10071 | 124.9969 | 62.0911 | -0.27008 | 124.9649 | -0.10071 | 62.0911 | 124.9008 | 124.9969 | -125.3448 | -125.3815
94.6406 | 125.473 | -61.9812 | 63.1531 | -0.063858 | 0.0084103 | 0.011696 | -0.0023413 | 0.06483 | 0.00070494 | 0.070521 | -62.0728 | 63.0157 | -62.2055 | -62.1231 | 62.9379 | 0.12817 | -0.068665 | 0.2243 | 63.0707 | -62.1872 | -0.2243 | -0.13733 | -0.091553 | -0.14191 | -0.21515 | -0.20599 | -0.082397 | 0.13275 | 61.9125 | 62.2055 | 124.9191 | 124.9969 | -0.091553 | 125.0519 | 62.1094 | -0.20599 | 124.9969 | -0.091553 | 62.1094 | 124.9191 | 125.0519 | -125.3586 | -125.3403
95.6406 | 125.4089 | -61.9766 | 63.1897 | -0.20882 | 0.012042 | 0.014473 | 0.0019311 | 0.06718 | 0.0015595 | 0.067317 | -61.94 | 63.1531 | -62.2192 | -62.0224 | 62.9471 | -0.009155 | 0.19226 | 0.18768 | 63.1485 | -62.2467 | -0.24261 | -0.036621 | 0.036622 | -0.045776 | -0.24261 | -0.27008 | -0.041198 | 0.27924 | 62.1689 | 62.1643 | 124.9237 | 125.1297 | 0.036622 | 125.1251 | 61.9675 | -0.27008 | 125.1297 | 0.036622 | 61.9675 | 124.9237 | 125.1251 | -125.4089 | -125.4364
96.6406 | 125.4684 | -61.9492 | 63.1668 | -0.25459 | 0.0071285 | 0.015968 | -0.0019141 | 0.066326 | -0.0022859 | 0.070735 | -62.0132 | 63.0432 | -62.1735 | -62.0682 | 62.9608 | 0.16022 | -0.036621 | 0.27008 | 63.089 | -62.1918 | -0.2243 | -0.1236 | -0.064087 | -0.11902 | -0.20599 | -0.24261 | -0.07782 | 0.16022 | 61.9125 | 62.2192 | 124.91 | 124.9924 | -0.064087 | 125.0381 | 62.1094 | -0.24261 | 124.9924 | -0.064087 | 62.1094 | 124.91 | 125.0381 | -125.3403 | -125.3586
97.6406 | 125.3494 | -61.9995 | 63.1989 | -0.22408 | 0.0099057 | 0.013405 | 0.0023583 | 0.065258 | 0.00049134 | 0.067958 | -62.0728 | 63.1485 | -62.2101 | -62.1826 | 62.8555 | 0.050354 | 0.12817 | 0.14191 | 63.1439 | -62.2284 | -0.21057 | -0.050354 | -0.073242 | -0.1831 | -0.34332 | -0.22888 | -0.054932 | 0.13733 | 62.1277 | 62.1414 | 124.855 | 125.148 | -0.073242 | 125.1434 | 62.0499 | -0.22888 | 125.148 | -0.073242 | 62.0499 | 124.855 | 125.1434 | -125.4089 | -125.4272
98.6406 | 125.4318 | -61.9446 | 63.1622 | -0.24696 | 0.01076 | 0.011055 | -0.0021277 | 0.065899 | -0.0012177 | 0.067744 | -62.0224 | 63.0203 | -62.2055 | -62.1002 | 62.9654 | 0.16022 | 0 | 0.2655 | 63.0981 | -62.1872 | -0.26093 | -0.14191 | -0.07782 | -0.15564 | -0.19684 | -0.24262 | -0.064086 | 0.18311 | 61.9446 | 62.2101 | 124.91 | 124.9649 | -0.07782 | 125.0427 | 62.1048 | -0.24262 | 124.9649 | -0.07782 | 62.1048 | 124.91 | 125.0427 | -125.3677 | -125.3494
99.6406 | 125.4547 | -61.972 | 63.2034 | -0.22408 | 0.0073423 | 0.0076369 | 0.0021447 | 0.065471 | -0.0024995 | 0.067958 | -62.0453 | 63.0569 | -62.1689 | -62.0956 | 62.9288 | 0.15106 | 0.027466 | 0.23804 | 63.0798 | -62.1872 | -0.19684 | -0.14648 | -0.073242 | -0.1236 | -0.27466 | -0.21515 | -0.1236 | 0.1236 | 61.9995 | 62.2101 | 124.9008 | 125.029 | -0.073242 | 125.0519 | 62.1231 | -0.21515 | 125.029 | -0.073242 | 62.1231 | 124.9008 | 125.0519 | -125.3723 | -125.3906
100.6406 | 125.4639 | -62.0499 | 63.2355 | 0.042953 | 0.01076 | 0.0149 | 0.0070581 | 0.068889 | -0.0035675 | 0.069453 | -62.0865 | 63.1577 | -62.2009 | -62.2101 | 62.8006 | -0.045776 | -0.11902 | -0.52185 | 63.0295 | -62.2971 | -0.15106 | -0.07782 | -0.036621 | -0.16022 | -0.43488 | -0.24719 | -0.20599 | 0.11444 | 61.9308 | 61.528 | 124.8505 | 125.2075 | -0.036621 | 125.0793 | 62.0041 | -0.24719 | 125.2075 | -0.036621 | 62.0041 | 124.8505 | 125.0793 | -125.4364 | -125.5325
101.6406 | 125.3952 | -61.9492 | 63.1897 | -0.23933 | 0.0075559 | 0.011696 | -0.00084605 | 0.065471 | 6.414e-05 | 0.068599 | -62.0407 | 63.0936 | -62.1826 | -62.1597 | 62.9059 | 0.09613 | 0.11444 | 0.1831 | 63.1165 | -62.2101 | -0.23346 | -0.09613 | -0.091552 | -0.21057 | -0.28381 | -0.26093 | -0.073242 | 0.14191 | 62.0636 | 62.1323 | 124.855 | 125.0427 | -0.091552 | 125.0656 | 62.0453 | -0.26093 | 125.0427 | -0.091552 | 62.0453 | 124.855 | 125.0656 | -125.3723 | -125.3998
102.6406 | 125.386 | -61.9904 | 63.176 | -0.16304 | 0.0099057 | 0.011055 | 0.0034265 | 0.070171 | -0.0027131 | 0.067958 | -62.0224 | 63.1256 | -62.1826 | -61.9629 | 62.9288 | 0.041199 | 0.10986 | 0.20599 | 63.0981 | -62.233 | -0.19226 | -0.050354 | -0.032044 | 0.027465 | -0.24719 | -0.24262 | -0.077819 | 0.16022 | 62.1002 | 62.1963 | 124.9191 | 125.116 | -0.032044 | 125.0885 | 62.0316 | -0.24262 | 125.116 | -0.032044 | 62.0316 | 124.9191 | 125.0885 | -125.3586 | -125.4089
103.6406 | 125.3723 | -62.0178 | 63.1851 | -0.20882 | 0.012042 | 0.013405 | 0.0025719 | 0.068248 | -0.0044221 | 0.068812 | -62.0819 | 63.1485 | -62.2192 | -62.1826 | 62.8601 | 0.045776 | 0.14191 | 0.14648 | 63.1256 | -62.2284 | -0.20142 | -0.036621 | -0.064087 | -0.16479 | -0.32501 | -0.21057 | -0.05951 | 0.13733 | 62.1597 | 62.1643 | 124.8779 | 125.1663 | -0.064087 | 125.1434 | 62.0636 | -0.21057 | 125.1663 | -0.064087 | 62.0636 | 124.8779 | 125.1434 | -125.4044 | -125.4135
104.6406 | 125.3677 | -61.9904 | 63.1989 | -0.1783 | 0.011401 | 0.010628 | 0.0027855 | 0.066326 | -0.0016449 | 0.067103 | -62.0956 | 63.1622 | -62.2284 | -62.1735 | 62.8738 | 0.073242 | 0.13733 | 0.15106 | 63.1439 | -62.2284 | -0.23804 | -0.036622 | -0.10529 | -0.18311 | -0.32501 | -0.23804 | -0.054932 | 0.13275 | 62.1277 | 62.1414 | 124.8642 | 125.1526 | -0.10529 | 125.1343 | 62.0636 | -0.23804 | 125.1526 | -0.10529 | 62.0636 | 124.8642 | 125.1343 | -125.4272 | -125.4272
105.6406 | 125.3403 | -62.0041 | 63.1805 | 0.11162 | 0.011615 | 0.013191 | 0.0021447 | 0.064617 | -0.0020721 | 0.06988 | -62.1231 | 63.1348 | -62.2284 | -62.2696 | 62.8738 | 0.064087 | -0.013733 | 0.036621 | 63.1531 | -62.2513 | -0.22431 | -0.045776 | -0.11902 | -0.2655 | -0.3067 | -0.24719 | -0.027466 | 0.10529 | 61.9904 | 62.0407 | 124.8779 | 125.1389 | -0.11902 | 125.1572 | 62.0682 | -0.24719 | 125.1389 | -0.11902 | 62.0682 | 124.8779 | 125.1572 | -125.4089 | -125.4318
106.6406 | 125.3769 | -61.9995 | 63.1989 | -0.20119 | 0.011401 | 0.01191 | 0.0036401 | 0.065685 | 0.00049134 | 0.069026 | -62.0682 | 63.1668 | -62.2009 | -62.1552 | 62.883 | 0.091553 | 0.09613 | 0.15564 | 63.1439 | -62.233 | -0.20142 | -0.032044 | -0.068664 | -0.15564 | -0.31586 | -0.23346 | -0.054932 | 0.13275 | 62.0956 | 62.1552 | 124.8825 | 125.1663 | -0.068664 | 125.1434 | 62.0911 | -0.23346 | 125.1663 | -0.068664 | 62.0911 | 124.8825 | 125.1434 | -125.3998 | -125.4318
107.6406 | 125.3906 | -62.0178 | 63.1805 | -0.11726 | 0.010547 | 0.013832 | 0.0023583 | 0.068248 | -0.0016449 | 0.067531 | -62.0407 | 63.1485 | -62.1872 | -62.146 | 62.8967 | 0.10529 | 0.086975 | 0.16937 | 63.1439 | -62.2421 | -0.16937 | -0.032043 | -0.022888 | -0.12817 | -0.28381 | -0.2243 | -0.036621 | 0.14649 | 62.1048 | 62.1872 | 124.9146 | 125.1663 | -0.022888 | 125.1617 | 62.1231 | -0.2243 | 125.1663 | -0.022888 | 62.1231 | 124.9146 | 125.1617 | -125.3677 | -125.4227
108.6406 | 125.2625 | -62.0224 | 63.1668 | -0.13252 | 0.015246 | 0.011482 | 0.0027855 | 0.068676 | -0.00014946 | 0.068171 | -62.0361 | 63.1531 | -62.2009 | -62.146 | 62.9059 | 0.091553 | 0.041199 | 0.16937 | 63.1485 | -62.2467 | -0.17853 | -0.013733 | -0.013733 | -0.1236 | -0.26093 | -0.2243 | -0.01831 | 0.16479 | 62.0636 | 62.1918 | 124.9283 | 125.1755 | -0.013733 | 125.1709 | 62.114 | -0.2243 | 125.1755 | -0.013733 | 62.114 | 124.9283 | 125.1709 | -125.3677 | -125.4135
109.6406 | 125.3952 | -61.9812 | 63.176 | -0.056229 | 0.013324 | 0.01191 | 0.0023583 | 0.068462 | -0.00014946 | 0.069239 | -62.0316 | 63.1302 | -62.2101 | -62.1918 | 62.8555 | 0.050354 | 0.022888 | 0.12817 | 63.121 | -62.2467 | -0.22888 | -0.045776 | -0.050354 | -0.21057 | -0.32043 | -0.2655 | -0.054931 | 0.17853 | 62.0041 | 62.1094 | 124.8367 | 125.1114 | -0.050354 | 125.1022 | 62.0316 | -0.2655 | 125.1114 | -0.050354 | 62.0316 | 124.8367 | 125.1022 | -125.386 | -125.4227
110.6406 | 125.3632 | -62.0087 | 63.1714 | -0.010452 | 0.011401 | 0.013832 | 0.0027855 | 0.069316 | -0.00079046 | 0.068812 | -62.0544 | 63.1668 | -62.2192 | -62.1826 | 62.8601 | 0.027466 | 0.032043 | 0.09613 | 63.121 | -62.2696 | -0.21057 | -0.004578 | -0.045776 | -0.17395 | -0.31128 | -0.26093 | -0.050354 | 0.16479 | 62.0407 | 62.1048 | 124.8688 | 125.1755 | -0.045776 | 125.1297 | 62.0361 | -0.26093 | 125.1755 | -0.045776 | 62.0361 | 124.8688 | 125.1297 | -125.3906 | -125.441
111.6406 | 125.3677 | -62.0224 | 63.1622 | -0.010452 | 0.014392 | 0.017464 | 0.0029993 | 0.068035 | -0.0016449 | 0.069239 | -62.0636 | 63.1393 | -62.2192 | -62.2192 | 62.8464 | 0.018311 | 0.027466 | 0.09613 | 63.1119 | -62.2833 | -0.19684 | -0.022888 | -0.041199 | -0.19684 | -0.31586 | -0.26093 | -0.050354 | 0.15564 | 62.0499 | 62.1185 | 124.8688 | 125.1617 | -0.041199 | 125.1343 | 62.0407 | -0.26093 | 125.1617 | -0.041199 | 62.0407 | 124.8688 | 125.1343 | -125.3815 | -125.4456
112.6406 | 125.4776 | -61.972 | 63.1302 | 0.19554 | 0.010333 | 0.0149 | -0.0021277 | 0.068676 | 0.0013457 | 0.069239 | -62.0132 | 63.0661 | -62.2055 | -62.1506 | 62.9288 | 0.068665 | -0.17395 | 0.15106 | 63.0524 | -62.2147 | -0.23346 | -0.064087 | -0.041199 | -0.17853 | -0.20142 | -0.24262 | -0.07782 | 0.19226 | 61.7981 | 62.1231 | 124.9008 | 125.0381 | -0.041199 | 125.0244 | 62.0407 | -0.24262 | 125.0381 | -0.041199 | 62.0407 | 124.9008 | 125.0244 | -125.3357 | -125.3448
113.6406 | 125.3311 | -62.0132 | 63.1577 | 0.012436 | 0.011828 | 0.014687 | 0.0040673 | 0.066326 | 6.414e-05 | 0.069026 | -62.1048 | 63.1439 | -62.2101 | -62.2421 | 62.8143 | -0.009155 | 0.041199 | 0.027466 | 63.0936 | -62.3062 | -0.19684 | -0.013733 | -0.091552 | -0.22888 | -0.34332 | -0.29297 | -0.064087 | 0.10529 | 62.0544 | 62.0407 | 124.8276 | 125.1572 | -0.091552 | 125.1068 | 62.0041 | -0.29297 | 125.1572 | -0.091552 | 62.0041 | 124.8276 | 125.1068 | -125.3677 | -125.4639
114.6406 | 125.3586 | -62.0041 | 63.1073 | 0.058212 | 0.014606 | 0.015968 | 0.0027855 | 0.068035 | 0.00091854 | 0.070521 | -62.1094 | 63.1577 | -62.2101 | -62.2513 | 62.8189 | -0.022888 | 0.032043 | 0.022888 | 63.1393 | -62.265 | -0.20599 | 0.050354 | -0.10529 | -0.24719 | -0.28839 | -0.26093 | 0.032043 | 0.10071 | 62.0361 | 62.027 | 124.823 | 125.1617 | -0.10529 | 125.1434 | 61.9812 | -0.26093 | 125.1617 | -0.10529 | 61.9812 | 124.823 | 125.1434 | -125.3174 | -125.3723
115.6406 | 125.3494 | -62.0132 | 63.1897 | 0.012436 | 0.011615 | 0.017464 | 0.0017175 | 0.071666 | 0.00070494 | 0.069453 | -62.1323 | 63.1439 | -62.2284 | -61.9354 | 62.9379 | -0.11444 | 0.13275 | 0.13733 | 63.121 | -62.2513 | -0.21515 | -0.045776 | -0.11902 | 0.07782 | -0.25177 | -0.23804 | -0.068664 | 0.096131 | 62.146 | 62.1506 | 124.9512 | 125.1572 | -0.11902 | 125.1343 | 61.8988 | -0.23804 | 125.1572 | -0.11902 | 61.8988 | 124.9512 | 125.1343 | -125.4181 | -125.441
116.6406 | 125.3632 | -62.0316 | 63.1714 | 0.17265 | 0.011401 | 0.014046 | 0.00086295 | 0.068248 | 0.0015595 | 0.069239 | -62.1277 | 63.1485 | -62.2421 | -62.2513 | 62.7914 | -0.041199 | -0.032043 | 0.032043 | 63.089 | -62.2742 | -0.21057 | -0.022888 | -0.096131 | -0.21973 | -0.37994 | -0.24262 | -0.082398 | 0.11444 | 61.9995 | 62.0636 | 124.823 | 125.1801 | -0.096131 | 125.1205 | 61.9904 | -0.24262 | 125.1801 | -0.096131 | 61.9904 | 124.823 | 125.1205 | -125.4135 | -125.4456
117.6406 | 125.386 | -62.0041 | 63.1577 | 0.12688 | 0.011401 | 0.013191 | 0.0010767 | 0.070598 | -0.0010041 | 0.071376 | -62.1048 | 63.1302 | -62.2284 | -62.2284 | 62.8098 | -0.018311 | -0.054932 | 0.054932 | 63.0844 | -62.2925 | -0.22431 | -0.027466 | -0.10071 | -0.22431 | -0.3479 | -0.28839 | -0.073242 | 0.1236 | 61.9492 | 62.059 | 124.8138 | 125.1343 | -0.10071 | 125.0885 | 61.9858 | -0.28839 | 125.1343 | -0.10071 | 61.9858 | 124.8138 | 125.0885 | -125.386 | -125.4501
118.6406 | 125.3952 | -62.0224 | 63.1256 | 0.14214 | 0.01076 | 0.0082779 | 0.0034265 | 0.069316 | 0.00027774 | 0.071162 | -62.1094 | 63.1256 | -62.2147 | -62.2101 | 62.8235 | -0.027466 | -0.086975 | 0.064087 | 63.0753 | -62.2513 | -0.19226 | 0 | -0.086975 | -0.18768 | -0.30212 | -0.22888 | -0.050354 | 0.10529 | 61.9354 | 62.0865 | 124.8459 | 125.148 | -0.086975 | 125.0977 | 61.9949 | -0.22888 | 125.148 | -0.086975 | 61.9949 | 124.8459 | 125.0977 | -125.3403 | -125.3769
119.6406 | 125.4044 | -62.0041 | 63.1302 | 0.18791 | 0.010974 | 0.012978 | -0.00084605 | 0.067821 | 0.0013457 | 0.070308 | -62.0819 | 63.0936 | -62.2009 | -62.1964 | 62.8601 | -0.004578 | -0.12817 | 0.07782 | 63.0981 | -62.265 | -0.19684 | -0.036621 | -0.07782 | -0.19226 | -0.27008 | -0.26093 | -0.032043 | 0.11902 | 61.8759 | 62.0819 | 124.8642 | 125.0977 | -0.07782 | 125.1022 | 61.9995 | -0.26093 | 125.0977 | -0.07782 | 61.9995 | 124.8642 | 125.1022 | -125.3311 | -125.3952
120.6406 | 125.4639 | -61.9995 | 63.1256 | 0.16502 | 0.010974 | 0.015541 | 8.546e-06 | 0.068248 | -0.00014946 | 0.070094 | -62.0728 | 63.0844 | -62.2238 | -62.178 | 62.8738 | 0.045776 | -0.14191 | 0.09613 | 63.0661 | -62.2696 | -0.2243 | -0.041198 | -0.073242 | -0.17853 | -0.25177 | -0.27008 | -0.059509 | 0.15106 | 61.8576 | 62.0956 | 124.8734 | 125.0839 | -0.073242 | 125.0656 | 62.0453 | -0.27008 | 125.0839 | -0.073242 | 62.0453 | 124.8734 | 125.0656 | -125.3494 | -125.3952
121.6406 | 125.5371 | -61.9766 | 63.0753 | 0.15739 | 0.011615 | 0.015328 | -0.00020505 | 0.067608 | 0.00049134 | 0.071376 | -62.0682 | 63.0615 | -62.2284 | -62.1643 | 62.883 | 0.032043 | -0.16937 | 0.13733 | 63.0295 | -62.2604 | -0.25177 | -0.013733 | -0.091552 | -0.18768 | -0.19226 | -0.28381 | -0.045776 | 0.16022 | 61.8073 | 62.114 | 124.8596 | 125.0381 | -0.091552 | 125.0061 | 62.0087 | -0.28381 | 125.0381 | -0.091552 | 62.0087 | 124.8596 | 125.0061 | -125.3037 | -125.3357
122.6406 | 125.4135 | -61.9675 | 63.1577 | 0.012436 | 0.0086239 | 0.011269 | -0.0031959 | 0.065685 | -0.0010041 | 0.071162 | -62.1872 | 63.0341 | -62.1918 | -62.2375 | 62.8693 | 0.032043 | -0.086975 | 0.11902 | 63.0753 | -62.2284 | -0.2243 | -0.1236 | -0.21973 | -0.27008 | -0.28839 | -0.26093 | -0.082398 | 0.004577 | 61.8805 | 62.0865 | 124.8367 | 125.0015 | -0.21973 | 125.0427 | 61.9995 | -0.26093 | 125.0015 | -0.21973 | 61.9995 | 124.8367 | 125.0427 | -125.3494 | -125.386
123.6406 | 125.4456 | -61.9812 | 63.1348 | 0.14214 | 0.010333 | 0.014259 | 0.00043575 | 0.064617 | 6.414e-05 | 0.070094 | -62.0453 | 63.0432 | -62.178 | -62.1231 | 62.8693 | 0.059509 | -0.17395 | 0.15564 | 63.0478 | -62.233 | -0.19684 | -0.091553 | -0.064087 | -0.14191 | -0.2655 | -0.25177 | -0.086975 | 0.13275 | 61.8073 | 62.1368 | 124.8505 | 125.0244 | -0.064087 | 125.029 | 62.0407 | -0.25177 | 125.0244 | -0.064087 | 62.0407 | 124.8505 | 125.029 | -125.3128 | -125.3677
124.6406 | 125.3952 | -61.972 | 63.1485 | 0.14214 | 0.0092649 | 0.011696 | -0.0012733 | 0.06184 | -0.0022859 | 0.071376 | -62.0956 | 63.0066 | -62.1964 | -62.1826 | 62.851 | 0.027466 | -0.10529 | 0.10071 | 63.0478 | -62.2238 | -0.2243 | -0.14191 | -0.1236 | -0.21057 | -0.29755 | -0.25177 | -0.10071 | 0.10071 | 61.8668 | 62.0728 | 124.823 | 124.9786 | -0.1236 | 125.0198 | 61.9995 | -0.25177 | 124.9786 | -0.1236 | 61.9995 | 124.823 | 125.0198 | -125.3448 | -125.3723
125.6406 | 125.4272 | -61.9629 | 63.1348 | 0.12688 | 0.0090513 | 0.011055 | 0.00086295 | 0.06419 | -0.00079046 | 0.070094 | -62.0453 | 63.0066 | -62.1964 | -62.1506 | 62.8738 | 0.045776 | -0.16937 | 0.13733 | 63.0432 | -62.2192 | -0.23346 | -0.12817 | -0.082397 | -0.18768 | -0.26093 | -0.25635 | -0.091553 | 0.15106 | 61.7935 | 62.1002 | 124.8367 | 124.9695 | -0.082397 | 125.0061 | 62.0087 | -0.25635 | 124.9695 | -0.082397 | 62.0087 | 124.8367 | 125.0061 | -125.3311 | -125.354
126.6406 | 125.4501 | -61.9858 | 63.1119 | 0.0811 | 0.0094785 | 0.015114 | 0.00064935 | 0.06718 | -0.0018585 | 0.070521 | -62.0316 | 63.0157 | -62.1872 | -62.1506 | 62.8555 | 0.050354 | -0.15106 | 0.14191 | 63.0569 | -62.2147 | -0.20142 | -0.09613 | -0.045776 | -0.16479 | -0.25635 | -0.22888 | -0.054931 | 0.15564 | 61.8347 | 62.1277 | 124.8413 | 125.0015 | -0.045776 | 125.0427 | 62.0361 | -0.22888 | 125.0015 | -0.045776 | 62.0361 | 124.8413 | 125.0427 | -125.2991 | -125.3265
127.6406 | 125.4776 | -61.9125 | 63.1622 | -0.14015 | 0.010547 | 0.012337 | 0.0070581 | 0.065471 | -0.0035675 | 0.069239 | -61.9949 | 63.0249 | -62.1506 | -62.1323 | 62.7869 | 0.11902 | 0 | 0.21515 | 63.0981 | -62.2147 | -0.23804 | -0.13733 | -0.082397 | -0.21973 | -0.37537 | -0.30212 | -0.064086 | 0.15564 | 61.9125 | 62.1277 | 124.6994 | 124.9374 | -0.082397 | 125.0107 | 62.0316 | -0.30212 | 124.9374 | -0.082397 | 62.0316 | 124.6994 | 125.0107 | -125.3128 | -125.3769
128.6406 | 125.4181 | -61.9995 | 63.1393 | 0.027695 | 0.0075559 | 0.0097733 | 0.0015039 | 0.063976 | -0.0018585 | 0.068599 | -62.0865 | 62.9974 | -62.2055 | -62.0636 | 62.6175 | -0.036621 | -0.041199 | 0.07782 | 63.0753 | -62.2147 | -0.20599 | -0.14191 | -0.086975 | -0.064087 | -0.52185 | -0.21515 | -0.064087 | 0.11902 | 61.9583 | 62.0773 | 124.617 | 124.9969 | -0.086975 | 125.0748 | 61.9629 | -0.21515 | 124.9969 | -0.086975 | 61.9629 | 124.617 | 125.0748 | -125.3448 | -125.354
129.6406 | 125.4272 | -61.9858 | 63.1439 | 0.11162 | 0.0079831 | 0.011696 | 0.0019311 | 0.064617 | 0.00049134 | 0.068171 | -62.0544 | 63.0066 | -62.1872 | -62.1597 | 62.851 | 0.032043 | -0.16479 | 0.13275 | 63.0707 | -62.2467 | -0.20142 | -0.13733 | -0.068664 | -0.17395 | -0.29297 | -0.26093 | -0.073242 | 0.13275 | 61.821 | 62.1185 | 124.8367 | 124.9924 | -0.068664 | 125.0565 | 62.0178 | -0.26093 | 124.9924 | -0.068664 | 62.0178 | 124.8367 | 125.0565 | -125.3311 | -125.3906
130.6406 | 125.4181 | -61.9766 | 63.1531 | 0.073471 | 0.01076 | 0.013832 | -0.00020505 | 0.062267 | -0.0012177 | 0.06988 | -62.027 | 63.0386 | -62.178 | -62.1964 | 62.883 | 0.013733 | -0.07782 | 0.11444 | 63.0707 | -62.2238 | -0.20142 | -0.11444 | -0.050354 | -0.21973 | -0.27008 | -0.24719 | -0.082397 | 0.15106 | 61.8988 | 62.0911 | 124.8596 | 125.0153 | -0.050354 | 125.0473 | 61.9904 | -0.24719 | 125.0153 | -0.050354 | 61.9904 | 124.8596 | 125.0473 | -125.3311 | -125.3769
131.6406 | 125.4227 | -61.9812 | 63.1439 | -1.1167 | 0.0094785 | 0.013191 | 0.0017175 | 0.062481 | 0.00049134 | 0.070521 | -62.1368 | 63.0203 | -62.178 | -62.1964 | 62.8418 | 0.018311 | -0.091553 | 0.10071 | 63.0249 | -62.2055 | -0.19684 | -0.1236 | -0.15564 | -0.21515 | -0.30212 | -0.2243 | -0.11902 | 0.041199 | 61.8896 | 62.0819 | 124.823 | 125.0015 | -0.15564 | 125.0061 | 61.9995 | -0.2243 | 125.0015 | -0.15564 | 61.9995 | 124.823 | 125.0061 | -125.322 | -125.3494
132.6406 | 125.3906 | -61.9812 | 63.1897 | -0.27748 | 0.010333 | 0.010841 | 0.0025719 | 0.061626 | -0.00036306 | 0.067744 | -62.0499 | 63.0661 | -62.1826 | -62.1597 | 62.8647 | 0.064087 | 0.11902 | 0.17853 | 63.0981 | -62.2147 | -0.20142 | -0.1236 | -0.068665 | -0.17853 | -0.32501 | -0.23346 | -0.091552 | 0.13275 | 62.1002 | 62.1597 | 124.8459 | 125.0473 | -0.068665 | 125.0793 | 62.0453 | -0.23346 | 125.0473 | -0.068665 | 62.0453 | 124.8459 | 125.0793 | -125.3723 | -125.4044
133.6406 | 125.3998 | -61.9675 | 63.1485 | 0.012436 | 0.0086239 | 0.010628 | 8.546e-06 | 0.06483 | 0.00049134 | 0.069026 | -61.9217 | 63.0661 | -62.1597 | -62.2055 | 62.883 | 0 | -0.059509 | 0.10071 | 63.0661 | -62.233 | -0.19226 | -0.082398 | 0.045776 | -0.23804 | -0.2655 | -0.2655 | -0.082398 | 0.23804 | 61.908 | 62.0682 | 124.8505 | 125.0336 | 0.045776 | 125.0336 | 61.9675 | -0.2655 | 125.0336 | 0.045776 | 61.9675 | 124.8505 | 125.0336 | -125.3082 | -125.3815
134.6406 | 125.4135 | -61.9949 | 63.1393 | 0.073471 | 0.0086239 | 0.0082779 | -0.0053321 | 0.060985 | -0.00036306 | 0.068599 | -62.0865 | 63.0341 | -62.1735 | -62.178 | 62.9471 | 0.013733 | -0.1236 | 0.10986 | 63.0249 | -62.2101 | -0.17853 | -0.10528 | -0.091553 | -0.18311 | -0.19226 | -0.21515 | -0.11444 | 0.086975 | 61.8713 | 62.1048 | 124.942 | 125.029 | -0.091553 | 125.0198 | 62.0087 | -0.21515 | 125.029 | -0.091553 | 62.0087 | 124.942 | 125.0198 | -125.3128 | -125.3494
135.6406 | 125.3815 | -61.9995 | 63.1439 | 0.096359 | 0.0077695 | 0.0087051 | 8.546e-06 | 0.063121 | -0.0016449 | 0.065608 | -62.0956 | 63.0157 | -62.2009 | -61.9675 | 63.0936 | 0.13733 | -0.16022 | 0.1831 | 63.0386 | -62.2101 | -0.20142 | -0.12817 | -0.09613 | 0.032044 | -0.050354 | -0.21057 | -0.10529 | 0.10529 | 61.8393 | 62.1826 | 125.0931 | 125.0153 | -0.09613 | 125.0381 | 62.1368 | -0.21057 | 125.0153 | -0.09613 | 62.1368 | 125.0931 | 125.0381 | -125.3448 | -125.354
136.6406 | 125.4227 | -61.9949 | 63.1531 | 0.10399 | 0.011401 | 0.0099869 | 0.0010767 | 0.063121 | -0.00014946 | 0.069453 | -62.1002 | 63.0203 | -62.1872 | -62.1414 | 62.8693 | -0.082397 | 0.28381 | 0.2243 | 63.1027 | -62.178 | -0.19226 | -0.13275 | -0.10529 | -0.14648 | -0.28381 | -0.18311 | -0.050354 | 0.086975 | 62.2787 | 62.2192 | 124.8642 | 125.0153 | -0.10529 | 125.0977 | 61.9125 | -0.18311 | 125.0153 | -0.10529 | 61.9125 | 124.8642 | 125.0977 | -125.3403 | -125.3311
137.6406 | 125.441 | -61.9492 | 63.1577 | -0.25459 | 0.0099057 | 0.0076369 | 0.00022215 | 0.06184 | -0.0014313 | 0.070308 | -62.027 | 63.0478 | -62.178 | -62.0636 | 62.9517 | 0.16022 | -0.041199 | 0.28839 | 63.0707 | -62.1918 | -0.22888 | -0.10986 | -0.07782 | -0.11444 | -0.20599 | -0.24261 | -0.086975 | 0.15106 | 61.908 | 62.2375 | 124.9008 | 124.9969 | -0.07782 | 125.0198 | 62.1094 | -0.24261 | 124.9969 | -0.07782 | 62.1094 | 124.9008 | 125.0198 | -125.3357 | -125.3494
138.6406 | 125.4364 | -61.9583 | 63.1485 | 0.042953 | 0.0088375 | 0.0097733 | -0.0014869 | 0.062481 | -0.00014946 | 0.070308 | -62.1002 | 63.0341 | -62.2101 | -62.1552 | 62.8784 | 0.036621 | -0.064087 | 0.14648 | 63.0432 | -62.2055 | -0.25177 | -0.11444 | -0.14191 | -0.19684 | -0.27008 | -0.24719 | -0.10529 | 0.10986 | 61.8942 | 62.1048 | 124.8367 | 124.9924 | -0.14191 | 125.0015 | 61.9949 | -0.24719 | 124.9924 | -0.14191 | 61.9949 | 124.8367 | 125.0015 | -125.3586 | -125.354
139.6406 | 125.4227 | -61.9675 | 63.1531 | 0.27184 | 0.0092649 | 0.014259 | -0.00084605 | 0.062053 | -0.0010041 | 0.067317 | -62.0956 | 63.0295 | -62.1918 | -62.1323 | 62.8647 | 0.050354 | -0.07782 | 0.13275 | 63.0478 | -62.1918 | -0.2243 | -0.1236 | -0.12817 | -0.1648 | -0.28839 | -0.2243 | -0.10529 | 0.09613 | 61.8896 | 62.1002 | 124.8322 | 124.9969 | -0.12817 | 125.0153 | 62.0178 | -0.2243 | 124.9969 | -0.12817 | 62.0178 | 124.8322 | 125.0153 | -125.3448 | -125.3448
140.6406 | 125.3815 | -61.9675 | 63.1577 | 0.22606 | 0.0096921 | 0.01255 | -0.0019141 | 0.062267 | 0.00049134 | 0.068599 | -62.0865 | 63.0066 | -62.2055 | -62.1506 | 62.8601 | 0.036621 | -0.068665 | 0.13275 | 63.0478 | -62.2238 | -0.23804 | -0.15106 | -0.11902 | -0.18311 | -0.29755 | -0.25635 | -0.10986 | 0.11902 | 61.8988 | 62.1002 | 124.8276 | 124.9741 | -0.11902 | 125.0153 | 62.0041 | -0.25635 | 124.9741 | -0.11902 | 62.0041 | 124.8276 | 125.0153 | -125.3632 | -125.3815
141.6406 | 125.386 | -61.9858 | 63.1622 | 0.08873 | 0.0067013 | 0.012123 | 0.00043575 | 0.062481 | -0.0027131 | 0.068599 | -61.8713 | 63.0478 | -62.1414 | -62.146 | 62.8555 | 0.018311 | -0.086975 | 0.10986 | 63.0295 | -62.2192 | -0.15564 | -0.11444 | 0.11444 | -0.16022 | -0.3067 | -0.23346 | -0.13275 | 0.27008 | 61.8988 | 62.0956 | 124.8413 | 125.0336 | 0.11444 | 125.0153 | 62.0041 | -0.23346 | 125.0336 | 0.11444 | 62.0041 | 124.8413 | 125.0153 | -125.3036 | -125.3815
142.6406 | 125.4272 | -61.9904 | 63.1302 | -0.056229 | 0.0096921 | 0.010414 | -0.0023413 | 0.061199 | 6.414e-05 | 0.070094 | -62.0956 | 62.9974 | -62.1872 | -62.1277 | 62.8738 | 0.07782 | -0.073242 | 0.16022 | 63.0569 | -62.1826 | -0.19684 | -0.13275 | -0.10529 | -0.13733 | -0.25635 | -0.19226 | -0.073242 | 0.091553 | 61.9171 | 62.1506 | 124.8642 | 124.9878 | -0.10529 | 125.0473 | 62.0682 | -0.19226 | 124.9878 | -0.10529 | 62.0682 | 124.8642 | 125.0473 | -125.3174 | -125.3128
143.6406 | 125.4318 | -61.9537 | 63.1577 | 0.012436 | 0.0096921 | 0.015968 | -0.00084605 | 0.063335 | -0.0018585 | 0.066035 | -62.0911 | 63.0112 | -62.1964 | -62.0087 | 62.7548 | -0.10071 | -0.032043 | 0.064087 | 63.0432 | -62.178 | -0.24262 | -0.14648 | -0.13733 | -0.054932 | -0.40283 | -0.22431 | -0.11444 | 0.10529 | 61.9217 | 62.0178 | 124.7086 | 124.9649 | -0.13733 | 124.9969 | 61.853 | -0.22431 | 124.9649 | -0.13733 | 61.853 | 124.7086 | 124.9969 | -125.354 | -125.3357
144.6406 | 125.4684 | -61.972 | 63.1622 | -0.086746 | 0.0081967 | 0.01191 | -0.0014869 | 0.062908 | 0.0022003 | 0.068599 | -62.0407 | 63.0295 | -62.178 | -62.0956 | 62.9288 | 0.10986 | -0.082397 | 0.22888 | 63.0707 | -62.178 | -0.20599 | -0.13275 | -0.068664 | -0.1236 | -0.23346 | -0.20599 | -0.091552 | 0.13733 | 61.8896 | 62.2009 | 124.9008 | 125.0015 | -0.068664 | 125.0427 | 62.0819 | -0.20599 | 125.0015 | -0.068664 | 62.0819 | 124.9008 | 125.0427 | -125.3403 | -125.3403
145.6406 | 125.4501 | -61.9675 | 63.1577 | -0.048599 | 0.0069149 | 0.013405 | -0.0027687 | 0.060558 | 0.00070494 | 0.068599 | -62.0819 | 62.9745 | -62.2147 | -62.1506 | 62.8922 | 0.050354 | -0.068665 | 0.16479 | 63.0569 | -62.1964 | -0.24719 | -0.18311 | -0.11444 | -0.18311 | -0.2655 | -0.22888 | -0.10071 | 0.13275 | 61.8988 | 62.1323 | 124.8596 | 124.942 | -0.11444 | 125.0244 | 62.0178 | -0.22888 | 124.942 | -0.11444 | 62.0178 | 124.8596 | 125.0244 | -125.3723 | -125.354
146.6406 | 125.4044 | -61.9675 | 63.1439 | 0.0048064 | 0.0086239 | 0.0076369 | -0.0051185 | 0.063549 | -0.0016449 | 0.069667 | -62.1094 | 63.0157 | -62.1872 | -62.1323 | 62.883 | 0.054932 | -0.073242 | 0.17395 | 63.0569 | -62.2055 | -0.21973 | -0.12817 | -0.14191 | -0.1648 | -0.26093 | -0.23804 | -0.086975 | 0.07782 | 61.8942 | 62.1414 | 124.8505 | 124.9832 | -0.14191 | 125.0244 | 62.0224 | -0.23804 | 124.9832 | -0.14191 | 62.0224 | 124.8505 | 125.0244 | -125.3311 | -125.3494
147.6406 | 125.441 | -61.9629 | 63.1668 | -0.010452 | 0.0084103 | 0.013191 | -0.0010597 | 0.060131 | -0.0035675 | 0.06988 | -62.0728 | 62.9883 | -62.1689 | -62.114 | 62.9105 | 0.09613 | -0.068665 | 0.19684 | 63.0661 | -62.1964 | -0.20599 | -0.17853 | -0.10986 | -0.15106 | -0.25635 | -0.23346 | -0.10071 | 0.09613 | 61.8942 | 62.1597 | 124.8734 | 124.9512 | -0.10986 | 125.029 | 62.059 | -0.23346 | 124.9512 | -0.10986 | 62.059 | 124.8734 | 125.029 | -125.3357 | -125.3632
148.6406 | 125.4272 | -61.972 | 63.1577 | -0.033341 | 0.0090513 | 0.010414 | -0.0021277 | 0.062908 | 6.414e-05 | 0.068171 | -62.0636 | 63.0203 | -62.1689 | -62.0956 | 62.9013 | 0.086975 | -0.073242 | 0.20599 | 63.0341 | -62.1826 | -0.19684 | -0.13733 | -0.091553 | -0.1236 | -0.25635 | -0.21057 | -0.1236 | 0.10528 | 61.8988 | 62.178 | 124.8734 | 124.9924 | -0.091553 | 125.0061 | 62.059 | -0.21057 | 124.9924 | -0.091553 | 62.059 | 124.8734 | 125.0061 | -125.3265 | -125.3403
149.6406 | 125.4364 | -61.9583 | 63.1393 | -0.018082 | 0.0092649 | 0.013405 | -0.0019141 | 0.06184 | -0.0024995 | 0.068171 | -62.0682 | 63.0157 | -62.1872 | -62.1231 | 62.9013 | 0.086975 | -0.07782 | 0.19684 | 63.0478 | -62.1826 | -0.22888 | -0.1236 | -0.10986 | -0.1648 | -0.23804 | -0.2243 | -0.091552 | 0.11902 | 61.8805 | 62.1552 | 124.8596 | 124.9741 | -0.10986 | 125.0061 | 62.0453 | -0.2243 | 124.9741 | -0.10986 | 62.0453 | 124.8596 | 125.0061 | -125.3265 | -125.322
150.6406 | 125.4227 | -61.972 | 63.1485 | -0.018082 | 0.0052059 | 0.01191 | -0.0023413 | 0.060344 | -0.00057686 | 0.070521 | -62.0773 | 63.0203 | -62.1872 | -62.1277 | 62.8967 | 0.09613 | -0.09613 | 0.17395 | 63.0707 | -62.1872 | -0.21515 | -0.12817 | -0.10529 | -0.15564 | -0.25177 | -0.21515 | -0.07782 | 0.10986 | 61.8759 | 62.146 | 124.8688 | 124.9924 | -0.10529 | 125.0427 | 62.0682 | -0.21515 | 124.9924 | -0.10529 | 62.0682 | 124.8688 | 125.0427 | -125.3357 | -125.3357
151.6406 | 125.4456 | -61.9492 | 63.1531 | -0.063858 | 0.0081967 | 0.0089187 | -0.0010597 | 0.061412 | 0.0030547 | 0.068599 | -62.0407 | 63.002 | -62.178 | -62.0728 | 62.9288 | 0.13733 | -0.086975 | 0.23346 | 63.0432 | -62.1918 | -0.22888 | -0.15106 | -0.091552 | -0.1236 | -0.2243 | -0.24261 | -0.10986 | 0.13733 | 61.8622 | 62.1826 | 124.8779 | 124.9512 | -0.091552 | 124.9924 | 62.0865 | -0.24261 | 124.9512 | -0.091552 | 62.0865 | 124.8779 | 124.9924 | -125.3311 | -125.3448
152.6406 | 125.3586 | -61.9995 | 63.1943 | -0.26222 | 0.012683 | 0.0084915 | 0.0040673 | 0.062694 | -0.00057686 | 0.067103 | -62.059 | 63.1439 | -62.1872 | -62.1506 | 62.8555 | 0.059509 | 0.11444 | 0.15564 | 63.1027 | -62.2147 | -0.18768 | -0.050354 | -0.059509 | -0.15106 | -0.33874 | -0.21515 | -0.091553 | 0.12817 | 62.114 | 62.1552 | 124.855 | 125.1434 | -0.059509 | 125.1022 | 62.059 | -0.21515 | 125.1434 | -0.059509 | 62.059 | 124.855 | 125.1022 | -125.3815 | -125.4089
153.6406 | 125.4227 | -61.9537 | 63.1485 | -0.086746 | 0.0071285 | 0.010628 | -0.0021277 | 0.065899 | 0.0013457 | 0.06988 | -62.0682 | 63.0295 | -62.2009 | -62.1094 | 62.9196 | 0.13275 | -0.082397 | 0.21057 | 63.0936 | -62.1597 | -0.24719 | -0.11902 | -0.11444 | -0.15564 | -0.22888 | -0.20599 | -0.054932 | 0.13275 | 61.8713 | 62.1643 | 124.8734 | 124.9832 | -0.11444 | 125.0473 | 62.0865 | -0.20599 | 124.9832 | -0.11444 | 62.0865 | 124.8734 | 125.0473 | -125.3494 | -125.3082
154.6406 | 125.4639 | -61.9675 | 63.1393 | -0.048599 | 0.0084103 | 0.010628 | -0.0017005 | 0.062694 | -0.00057686 | 0.070735 | -62.0773 | 63.0341 | -62.1826 | -62.114 | 62.9059 | 0.10986 | -0.082397 | 0.21057 | 63.0661 | -62.1872 | -0.21515 | -0.10528 | -0.10986 | -0.14649 | -0.23346 | -0.21973 | -0.073242 | 0.10529 | 61.8851 | 62.178 | 124.8734 | 125.0015 | -0.10986 | 125.0336 | 62.0773 | -0.21973 | 125.0015 | -0.10986 | 62.0773 | 124.8734 | 125.0336 | -125.322 | -125.3265
155.6406 | 125.4868 | -61.94 | 63.1256 | -0.11726 | 0.0079831 | 0.0059281 | -0.0023413 | 0.064617 | 0.0013457 | 0.068599 | -62.0407 | 62.9883 | -62.1597 | -62.0499 | 62.9425 | 0.16022 | -0.10071 | 0.26093 | 63.0249 | -62.1735 | -0.21973 | -0.13733 | -0.10071 | -0.10986 | -0.18311 | -0.23346 | -0.10071 | 0.11902 | 61.8393 | 62.2009 | 124.8825 | 124.9283 | -0.10071 | 124.9649 | 62.1002 | -0.23346 | 124.9283 | -0.10071 | 62.1002 | 124.8825 | 124.9649 | -125.2853 | -125.2991
156.6406 | 125.4181 | -61.9904 | 63.176 | -0.018082 | 0.0052059 | 0.013619 | -0.00020505 | 0.063121 | -0.00036306 | 0.069453 | -62.0911 | 63.0157 | -62.1918 | -62.1506 | 62.883 | 0.068665 | -0.073242 | 0.17395 | 63.0203 | -62.1826 | -0.20142 | -0.16022 | -0.10071 | -0.16022 | -0.29297 | -0.19226 | -0.15564 | 0.10071 | 61.9171 | 62.1643 | 124.8734 | 125.0061 | -0.10071 | 125.0107 | 62.059 | -0.19226 | 125.0061 | -0.10071 | 62.059 | 124.8734 | 125.0107 | -125.3677 | -125.3586
157.6406 | 125.3815 | -61.9629 | 63.1851 | -0.24696 | 0.0096921 | 0.014046 | 8.546e-06 | 0.061412 | 0.00027774 | 0.068171 | -62.027 | 63.0478 | -62.1597 | -62.1094 | 62.8876 | 0.12817 | 0.073242 | 0.21515 | 63.0615 | -62.2101 | -0.19684 | -0.13733 | -0.064087 | -0.14648 | -0.29755 | -0.24719 | -0.1236 | 0.13275 | 62.0361 | 62.178 | 124.8505 | 125.0107 | -0.064087 | 125.0244 | 62.0911 | -0.24719 | 125.0107 | -0.064087 | 62.0911 | 124.8505 | 125.0244 | -125.3448 | -125.3952
158.6406 | 125.4272 | -61.9629 | 63.1439 | -0.056229 | 0.0096921 | 0.0078507 | -0.0019141 | 0.063762 | -0.00014946 | 0.069239 | -62.0956 | 63.0386 | -62.1735 | -62.1277 | 62.9059 | 0.07782 | -0.059509 | 0.18768 | 63.0203 | -62.1735 | -0.21057 | -0.10529 | -0.13275 | -0.16479 | -0.23804 | -0.21057 | -0.1236 | 0.07782 | 61.9034 | 62.1506 | 124.8688 | 125.0015 | -0.13275 | 124.9832 | 62.0407 | -0.21057 | 125.0015 | -0.13275 | 62.0407 | 124.8688 | 124.9832 | -125.3174 | -125.3174
159.6406 | 125.4135 | -61.9675 | 63.1668 | -0.056229 | 0.0075559 | 0.0074233 | -0.00084605 | 0.063549 | -0.0010041 | 0.06988 | -62.0819 | 63.0249 | -62.1826 | -62.1231 | 62.8876 | 0.068665 | -0.064087 | 0.18768 | 63.0386 | -62.2192 | -0.21515 | -0.14191 | -0.11444 | -0.15564 | -0.27924 | -0.25177 | -0.12817 | 0.10071 | 61.9034 | 62.1552 | 124.855 | 124.9924 | -0.11444 | 125.0061 | 62.0361 | -0.25177 | 124.9924 | -0.11444 | 62.0361 | 124.855 | 125.0061 | -125.3494 | -125.386
160.6406 | 125.4639 | -61.94 | 63.1485 | -0.04097 | 0.0088375 | 0.012123 | -0.00041865 | 0.063335 | -0.0010041 | 0.067531 | -62.0636 | 63.0112 | -62.1872 | -62.0819 | 62.9059 | 0.1236 | -0.068665 | 0.22888 | 63.0478 | -62.1872 | -0.24719 | -0.13733 | -0.1236 | -0.14191 | -0.24262 | -0.24719 | -0.10071 | 0.1236 | 61.8713 | 62.1689 | 124.8459 | 124.9512 | -0.1236 | 124.9878 | 62.0636 | -0.24719 | 124.9512 | -0.1236 | 62.0636 | 124.8459 | 124.9878 | -125.3357 | -125.3357
161.6406 | 125.4089 | -61.9629 | 63.1851 | -0.17067 | 0.0092649 | 0.012337 | -0.0034095 | 0.060985 | -0.0012177 | 0.069239 | -62.0911 | 63.002 | -62.1735 | -62.146 | 62.8601 | 0.045776 | -0.045776 | 0.14191 | 63.0478 | -62.2238 | -0.21057 | -0.18311 | -0.12817 | -0.1831 | -0.32501 | -0.26093 | -0.13733 | 0.082398 | 61.9171 | 62.1048 | 124.823 | 124.9649 | -0.12817 | 125.0107 | 62.0087 | -0.26093 | 124.9649 | -0.12817 | 62.0087 | 124.823 | 125.0107 | -125.3586 | -125.4089
162.6406 | 125.3723 | -61.9858 | 63.1805 | -0.18593 | 0.010333 | 0.010414 | 0.0047081 | 0.063976 | -0.0012177 | 0.06689 | -62.0316 | 63.1119 | -62.1964 | -62.1002 | 62.8784 | 0.082397 | 0.045776 | 0.15106 | 63.0386 | -62.2147 | -0.21057 | -0.068665 | -0.045776 | -0.11444 | -0.30212 | -0.22888 | -0.14191 | 0.1648 | 62.0316 | 62.1368 | 124.8642 | 125.0977 | -0.045776 | 125.0244 | 62.0682 | -0.22888 | 125.0977 | -0.045776 | 62.0682 | 124.8642 | 125.0244 | -125.3769 | -125.3952
163.6406 | 125.3998 | -61.972 | 63.1348 | 0.096359 | 0.0073423 | 0.0074233 | -0.0010597 | 0.065258 | -0.00079046 | 0.067531 | -62.0865 | 63.002 | -62.1872 | -62.1597 | 62.8647 | 0.050354 | 0.11902 | 0.33417 | 63.0798 | -62.1414 | -0.21515 | -0.13275 | -0.11444 | -0.18768 | -0.27008 | -0.16937 | -0.054932 | 0.10071 | 62.0911 | 62.3062 | 124.8367 | 124.9741 | -0.11444 | 125.0519 | 62.0224 | -0.16937 | 124.9741 | -0.11444 | 62.0224 | 124.8367 | 125.0519 | -125.322 | -125.2762
164.6406 | 125.4044 | -61.9492 | 63.1485 | 0.065841 | 0.0084103 | 0.010628 | 0.00086295 | 0.06184 | -0.0020721 | 0.067958 | -62.0773 | 63.0112 | -62.1918 | -62.1597 | 62.8693 | 0.027466 | -0.086975 | 0.11902 | 63.0157 | -62.1826 | -0.24261 | -0.13733 | -0.12817 | -0.21057 | -0.27924 | -0.23346 | -0.13275 | 0.11444 | 61.8622 | 62.0682 | 124.8184 | 124.9603 | -0.12817 | 124.9649 | 61.9766 | -0.23346 | 124.9603 | -0.12817 | 61.9766 | 124.8184 | 124.9649 | -125.3403 | -125.3311
165.6406 | 125.3906 | -61.9629 | 63.1393 | -0.42244 | 0.010333 | 0.014259 | -0.00084605 | 0.062908 | -0.00036306 | 0.069667 | -62.1048 | 63.0203 | -62.178 | -62.178 | 62.8647 | 0.027466 | -0.059509 | 0.1236 | 63.0203 | -62.1872 | -0.21515 | -0.11902 | -0.14191 | -0.21515 | -0.27466 | -0.2243 | -0.11902 | 0.073243 | 61.9034 | 62.0865 | 124.8276 | 124.9832 | -0.14191 | 124.9832 | 61.9904 | -0.2243 | 124.9832 | -0.14191 | 61.9904 | 124.8276 | 124.9832 | -125.3174 | -125.3265
166.6406 | 125.3906 | -61.9583 | 63.1393 | -0.010452 | 0.0088375 | 0.012978 | -0.00084605 | 0.062694 | -0.00014946 | 0.06988 | -62.0865 | 63.0066 | -62.1918 | -62.1368 | 62.883 | 0.082397 | -0.059509 | 0.1831 | 63.0386 | -62.2101 | -0.23346 | -0.13275 | -0.12817 | -0.17853 | -0.25635 | -0.25177 | -0.10071 | 0.10529 | 61.8988 | 62.1414 | 124.8413 | 124.9649 | -0.12817 | 124.9969 | 62.0407 | -0.25177 | 124.9649 | -0.12817 | 62.0407 | 124.8413 | 124.9969 | -125.3311 | -125.3494
167.6562 | 125.354 | -61.9812 | 63.1897 | -0.24696 | 0.010119 | 0.015114 | 0.0053491 | 0.060985 | -0.00036306 | 0.067531 | -62.2055 | 63.1027 | -62.2055 | -62.2055 | 62.8281 | 0.073242 | 0.10986 | 0.13275 | 63.0798 | -62.2147 | -0.2243 | -0.086975 | -0.2243 | -0.2243 | -0.36163 | -0.23346 | -0.10986 | 0 | 62.0911 | 62.114 | 124.8093 | 125.0839 | -0.2243 | 125.061 | 62.0544 | -0.23346 | 125.0839 | -0.2243 | 62.0544 | 124.8093 | 125.061 | -125.3952 | -125.4044
168.6406 | 125.3906 | -61.9812 | 63.1439 | -0.20119 | 0.0094785 | 0.012337 | -0.0017005 | 0.063549 | 0.00027774 | 0.068812 | -62.114 | 63.0203 | -62.1872 | -62.1552 | 62.8555 | 0.027466 | -0.054932 | 0.13733 | 63.0524 | -62.1689 | -0.20599 | -0.1236 | -0.13275 | -0.17395 | -0.28839 | -0.18768 | -0.091553 | 0.073242 | 61.9263 | 62.1185 | 124.8367 | 125.0015 | -0.13275 | 125.0336 | 62.0087 | -0.18768 | 125.0015 | -0.13275 | 62.0087 | 124.8367 | 125.0336 | -125.3311 | -125.3128
169.6406 | 125.3998 | -61.9629 | 63.1119 | 0.15739 | 0.0086239 | 0.0099869 | 0.0010767 | 0.063762 | 0.0015595 | 0.068385 | -62.059 | 63.0295 | -62.1918 | -62.146 | 62.8876 | 0.054932 | -0.14648 | 0.14191 | 63.0295 | -62.2055 | -0.22888 | -0.082397 | -0.09613 | -0.1831 | -0.2243 | -0.24261 | -0.082397 | 0.13275 | 61.8164 | 62.1048 | 124.8505 | 124.9924 | -0.09613 | 124.9924 | 62.0178 | -0.24261 | 124.9924 | -0.09613 | 62.0178 | 124.8505 | 124.9924 | -125.3036 | -125.3174
170.6406 | 125.4044 | -61.9537 | 63.1485 | 0.042953 | 0.0081967 | 0.01255 | -0.0029823 | 0.063335 | -0.00014946 | 0.068812 | -62.0865 | 63.0295 | -62.1964 | -62.1368 | 62.8738 | 0.045776 | -0.050354 | 0.15564 | 63.0478 | -62.178 | -0.24262 | -0.11902 | -0.13275 | -0.18311 | -0.27466 | -0.22431 | -0.10071 | 0.10986 | 61.9034 | 62.1094 | 124.8276 | 124.9832 | -0.13275 | 125.0015 | 61.9995 | -0.22431 | 124.9832 | -0.13275 | 61.9995 | 124.8276 | 125.0015 | -125.3448 | -125.3265
171.6406 | 125.4501 | -61.9629 | 63.1256 | 0.11925 | 0.010333 | 0.012337 | 0.0029993 | 0.065044 | -0.0012177 | 0.067744 | -62.027 | 63.0295 | -62.1918 | -62.1323 | 62.8876 | 0.054932 | -0.17853 | 0.13733 | 63.0341 | -62.1735 | -0.22888 | -0.09613 | -0.064087 | -0.16937 | -0.23804 | -0.21057 | -0.091552 | 0.16479 | 61.7844 | 62.1002 | 124.8505 | 124.9924 | -0.064087 | 124.9969 | 62.0178 | -0.21057 | 124.9924 | -0.064087 | 62.0178 | 124.8505 | 124.9969 | -125.3174 | -125.2991
172.6406 | 125.4501 | -61.9446 | 63.1348 | -0.15541 | 0.0075559 | 0.010628 | 0.0012903 | 0.064617 | 0.00091854 | 0.070948 | -61.6791 | 63.0844 | -62.1643 | -62.0224 | 62.9013 | 0.10986 | -0.032043 | 0.2655 | 63.0524 | -62.1872 | -0.21973 | -0.050354 | 0.2655 | -0.07782 | -0.23346 | -0.24262 | -0.082398 | 0.48523 | 61.9125 | 62.2101 | 124.8459 | 125.029 | 0.2655 | 124.9969 | 62.0544 | -0.24262 | 125.029 | 0.2655 | 62.0544 | 124.8459 | 124.9969 | -125.2991 | -125.322
173.6406 | 125.4135 | -61.9949 | 63.121 | 0.11162 | 0.010119 | 0.012123 | 0.0029993 | 0.062053 | 6.414e-05 | 0.069667 | -62.0407 | 63.0066 | -62.178 | -62.1231 | 62.883 | 0.064087 | -0.17853 | 0.16479 | 63.0341 | -62.2192 | -0.18311 | -0.11444 | -0.045776 | -0.12817 | -0.23804 | -0.2243 | -0.086975 | 0.13733 | 61.8164 | 62.1597 | 124.8779 | 125.0015 | -0.045776 | 125.029 | 62.059 | -0.2243 | 125.0015 | -0.045776 | 62.059 | 124.8779 | 125.029 | -125.2991 | -125.3403
174.6406 | 125.3998 | -61.9766 | 63.1485 | 0.16502 | 0.0096921 | 0.012978 | -0.0014869 | 0.063762 | 0.00027774 | 0.070308 | -62.0636 | 62.9974 | -62.1964 | -62.146 | 62.8601 | 0.050354 | -0.1236 | 0.11902 | 63.0341 | -62.1964 | -0.21973 | -0.15106 | -0.086975 | -0.16937 | -0.28839 | -0.21973 | -0.11444 | 0.13275 | 61.853 | 62.0956 | 124.8367 | 124.9741 | -0.086975 | 125.0107 | 62.027 | -0.21973 | 124.9741 | -0.086975 | 62.027 | 124.8367 | 125.0107 | -125.3448 | -125.3448
175.6406 | 125.4593 | -61.9583 | 63.1165 | 0.19554 | 0.0099057 | 0.014687 | 0.0027855 | 0.063549 | -0.00014946 | 0.070735 | -62.0087 | 63.0341 | -62.1735 | -62.1094 | 62.8967 | 0.054932 | -0.18768 | 0.14648 | 63.0203 | -62.2055 | -0.21515 | -0.082397 | -0.050354 | -0.15106 | -0.21973 | -0.24719 | -0.09613 | 0.16479 | 61.7706 | 62.1048 | 124.855 | 124.9924 | -0.050354 | 124.9786 | 62.0132 | -0.24719 | 124.9924 | -0.050354 | 62.0132 | 124.855 | 124.9786 | -125.2899 | -125.322
176.6406 | 125.386 | -61.9629 | 63.1348 | 0.08873 | 0.011615 | 0.010201 | 0.00022215 | 0.064403 | -0.0014313 | 0.067531 | -62.0819 | 63.0295 | -62.1689 | -62.146 | 62.8464 | 0.045776 | -0.11444 | 0.12817 | 63.0341 | -62.2147 | -0.20599 | -0.10529 | -0.11902 | -0.1831 | -0.28839 | -0.25177 | -0.10071 | 0.086975 | 61.8484 | 62.0911 | 124.8093 | 124.9924 | -0.11902 | 124.9969 | 62.0087 | -0.25177 | 124.9924 | -0.11902 | 62.0087 | 124.8093 | 124.9969 | -125.3037 | -125.3494
177.6406 | 125.4318 | -61.94 | 63.1439 | -0.056229 | 0.0099057 | 0.0078507 | -0.0014869 | 0.06184 | -0.0020721 | 0.069239 | -62.0361 | 63.0249 | -62.1826 | -62.0865 | 62.9242 | 0.1236 | -0.086975 | 0.25177 | 63.0432 | -62.1597 | -0.24262 | -0.11902 | -0.096131 | -0.14648 | -0.21973 | -0.21973 | -0.10071 | 0.14648 | 61.853 | 62.1918 | 124.8642 | 124.9649 | -0.096131 | 124.9832 | 62.0636 | -0.21973 | 124.9649 | -0.096131 | 62.0636 | 124.8642 | 124.9832 | -125.3265 | -125.3037
178.6406 | 125.4227 | -61.9904 | 63.1119 | 0.27946 | 0.010333 | 0.01255 | 0.0029993 | 0.065258 | -0.00036306 | 0.069239 | -61.9858 | 63.0066 | -62.1597 | -62.1002 | 62.8876 | 0.068665 | -0.1831 | 0.15564 | 63.0203 | -62.1918 | -0.16937 | -0.10529 | 0.004577 | -0.10986 | -0.2243 | -0.20142 | -0.091552 | 0.17395 | 61.8073 | 62.146 | 124.8779 | 124.9969 | 0.004577 | 125.0107 | 62.059 | -0.20142 | 124.9969 | 0.004577 | 62.059 | 124.8779 | 125.0107 | -125.2716 | -125.3036
179.6406 | 125.4639 | -61.972 | 63.1256 | 0.19554 | 0.011401 | 0.014687 | 0.0047081 | 0.063976 | -0.0029267 | 0.069667 | -62.0087 | 63.0203 | -62.1826 | -62.0865 | 62.8876 | 0.082397 | -0.20142 | 0.12817 | 63.0112 | -62.2147 | -0.21057 | -0.10529 | -0.036621 | -0.11444 | -0.23804 | -0.24262 | -0.11444 | 0.17395 | 61.7706 | 62.1002 | 124.8596 | 124.9924 | -0.036621 | 124.9832 | 62.0544 | -0.24262 | 124.9924 | -0.036621 | 62.0544 | 124.8596 | 124.9832 | -125.3082 | -125.3403
180.6406 | 125.4044 | -61.972 | 63.0615 | 0.18028 | 0.011828 | 0.011269 | 0.0038537 | 0.067608 | -0.00014946 | 0.068599 | -62.0316 | 63.0569 | -62.178 | -62.1185 | 62.8876 | 0.059509 | -0.1831 | 0.13275 | 63.0157 | -62.2101 | -0.20599 | -0.004577 | -0.059509 | -0.14648 | -0.17395 | -0.23804 | -0.045776 | 0.14649 | 61.7889 | 62.1048 | 124.8596 | 125.029 | -0.059509 | 124.9878 | 62.0316 | -0.23804 | 125.029 | -0.059509 | 62.0316 | 124.8596 | 124.9878 | -125.2396 | -125.2716
181.6406 | 125.4135 | -61.9904 | 63.1073 | 0.18028 | 0.011615 | 0.013405 | 0.0044945 | 0.066753 | -0.00014946 | 0.068599 | -62.0544 | 63.089 | -62.2101 | -62.1231 | 62.8647 | 0.018311 | -0.13275 | 0.10986 | 63.0478 | -62.2284 | -0.21973 | -0.018311 | -0.064087 | -0.13275 | -0.24262 | -0.23804 | -0.059509 | 0.15564 | 61.8576 | 62.1002 | 124.855 | 125.0793 | -0.064087 | 125.0381 | 62.0087 | -0.23804 | 125.0793 | -0.064087 | 62.0087 | 124.855 | 125.0381 | -125.3174 | -125.3357
182.6406 | 125.4272 | -61.9263 | 63.1439 | -0.25459 | 0.0090513 | 0.014046 | -0.0014869 | 0.063549 | -0.0012177 | 0.069239 | -62.0224 | 63.0432 | -62.1872 | -62.0728 | 62.9379 | 0.15564 | -0.009155 | 0.27008 | 63.0569 | -62.178 | -0.26093 | -0.10071 | -0.09613 | -0.14648 | -0.20599 | -0.25177 | -0.086975 | 0.1648 | 61.9171 | 62.1964 | 124.8642 | 124.9695 | -0.09613 | 124.9832 | 62.0819 | -0.25177 | 124.9695 | -0.09613 | 62.0819 | 124.8642 | 124.9832 | -125.3311 | -125.322
183.6406 | 125.4318 | -61.9904 | 63.121 | 0.17265 | 0.011828 | 0.012123 | 0.0032129 | 0.065685 | -0.0024995 | 0.071162 | -62.027 | 63.0569 | -62.2009 | -62.1185 | 62.8967 | 0.054932 | -0.18768 | 0.1236 | 62.9929 | -62.2375 | -0.21057 | -0.064087 | -0.036622 | -0.12817 | -0.2243 | -0.24719 | -0.12817 | 0.17395 | 61.8027 | 62.114 | 124.8871 | 125.0473 | -0.036622 | 124.9832 | 62.0453 | -0.24719 | 125.0473 | -0.036622 | 62.0453 | 124.8871 | 124.9832 | -125.322 | -125.3586
184.6406 | 125.4227 | -61.9766 | 63.1165 | 0.19554 | 0.0099057 | 0.015968 | 0.0032129 | 0.06718 | -0.0029267 | 0.06988 | -62.0636 | 63.0386 | -62.233 | -62.1323 | 62.8647 | 0.032043 | -0.16479 | 0.091553 | 63.0295 | -62.2101 | -0.25635 | -0.07782 | -0.086975 | -0.15564 | -0.25177 | -0.23346 | -0.086975 | 0.16937 | 61.8118 | 62.0682 | 124.8413 | 125.0153 | -0.086975 | 125.0061 | 62.0087 | -0.23346 | 125.0153 | -0.086975 | 62.0087 | 124.8413 | 125.0061 | -125.3494 | -125.3265
185.6406 | 125.3586 | -62.0178 | 63.1348 | 0.10399 | 0.012256 | 0.013405 | 0.0066309 | 0.066326 | -0.0014313 | 0.068385 | -62.1048 | 63.1256 | -62.2238 | -62.2192 | 62.7777 | -0.036621 | -0.013733 | 0.004578 | 63.0844 | -62.2696 | -0.20599 | -0.009156 | -0.086975 | -0.20142 | -0.35706 | -0.25177 | -0.050354 | 0.11902 | 62.0041 | 62.0224 | 124.7955 | 125.1434 | -0.086975 | 125.1022 | 61.9812 | -0.25177 | 125.1434 | -0.086975 | 61.9812 | 124.7955 | 125.1022 | -125.3586 | -125.4044
186.6406 | 125.4181 | -61.9766 | 63.0661 | 0.13451 | 0.0088375 | 0.014259 | 0.00086295 | 0.068462 | -0.0012177 | 0.069453 | -62.0316 | 63.0432 | -62.2101 | -62.1277 | 62.9013 | 0.068665 | -0.1831 | 0.13733 | 63.0386 | -62.2055 | -0.23346 | -0.022888 | -0.054931 | -0.15106 | -0.1648 | -0.22888 | -0.027466 | 0.17853 | 61.7935 | 62.114 | 124.8779 | 125.0198 | -0.054931 | 125.0153 | 62.0453 | -0.22888 | 125.0198 | -0.054931 | 62.0453 | 124.8779 | 125.0153 | -125.2762 | -125.2716
187.6562 | 125.3952 | -61.94 | 63.1256 | -0.086746 | 0.0077695 | 0.012978 | -0.0036231 | 0.064617 | -0.0010041 | 0.070521 | -62.059 | 63.0203 | -62.2055 | -62.1002 | 62.915 | 0.1236 | -0.068665 | 0.23804 | 63.0432 | -62.1964 | -0.2655 | -0.10529 | -0.11902 | -0.16022 | -0.21057 | -0.25635 | -0.082397 | 0.14648 | 61.8713 | 62.178 | 124.855 | 124.9603 | -0.11902 | 124.9832 | 62.0636 | -0.25635 | 124.9603 | -0.11902 | 62.0636 | 124.855 | 124.9832 | -125.3311 | -125.322
188.6406 | 125.3265 | -62.0132 | 63.1577 | 0.17265 | 0.012256 | 0.0095595 | 0.0089807 | 0.063976 | 0.00027774 | 0.072657 | -62.0956 | 63.0844 | -62.2421 | -62.2009 | 62.7869 | -0.045776 | -0.036621 | 0.032043 | 63.0798 | -62.2513 | -0.22888 | -0.073242 | -0.082397 | -0.18768 | -0.37079 | -0.23804 | -0.07782 | 0.14648 | 61.9766 | 62.0453 | 124.8001 | 125.0977 | -0.082397 | 125.0931 | 61.9675 | -0.23804 | 125.0977 | -0.082397 | 61.9675 | 124.8001 | 125.0931 | -125.3998 | -125.4089
189.6406 | 125.3494 | -61.9995 | 63.1348 | 0.13451 | 0.013965 | 0.01725 | 0.0055627 | 0.06718 | -0.0012177 | 0.069667 | -62.0911 | 63.1302 | -62.2101 | -62.2238 | 62.7914 | -0.045776 | -0.004578 | 0.022888 | 63.0798 | -62.2879 | -0.21057 | -0.004578 | -0.091552 | -0.2243 | -0.34332 | -0.28839 | -0.054932 | 0.11902 | 61.9949 | 62.0224 | 124.791 | 125.1297 | -0.091552 | 125.0793 | 61.9537 | -0.28839 | 125.1297 | -0.091552 | 61.9537 | 124.791 | 125.0793 | -125.3448 | -125.4227
190.6406 | 125.3769 | -61.972 | 63.1256 | 0.17265 | 0.014392 | 0.015114 | 0.0029993 | 0.068462 | -0.00079046 | 0.067744 | -62.0819 | 63.1027 | -62.2192 | -62.1872 | 62.8143 | -0.013733 | -0.07782 | 0.050354 | 63.0936 | -62.2421 | -0.24719 | -0.022888 | -0.10986 | -0.21515 | -0.31128 | -0.27008 | -0.032043 | 0.13733 | 61.8942 | 62.0224 | 124.7864 | 125.0748 | -0.10986 | 125.0656 | 61.9583 | -0.27008 | 125.0748 | -0.10986 | 61.9583 | 124.7864 | 125.0656 | -125.3448 | -125.3677
191.6562 | 125.354 | -61.9766 | 63.1622 | -0.26985 | 0.0099057 | 0.012764 | 0.00064935 | 0.066753 | -0.00036306 | 0.068599 | -62.0361 | 63.0798 | -62.178 | -62.114 | 62.8876 | 0.10986 | 0.10986 | 0.21515 | 63.1073 | -62.1872 | -0.20142 | -0.082397 | -0.059509 | -0.13733 | -0.27466 | -0.21057 | -0.054931 | 0.14191 | 62.0865 | 62.1918 | 124.8642 | 125.0565 | -0.059509 | 125.0839 | 62.0865 | -0.21057 | 125.0565 | -0.059509 | 62.0865 | 124.8642 | 125.0839 | -125.3403 | -125.3494
192.6406 | 125.4639 | -61.9537 | 63.1165 | -0.14778 | 0.011615 | 0.0149 | -0.00020505 | 0.065258 | -0.0010041 | 0.070308 | -62.0407 | 63.0432 | -62.1689 | -62.1231 | 62.9059 | 0.059509 | -0.17395 | 0.15564 | 63.0157 | -62.1872 | -0.21515 | -0.073242 | -0.086975 | -0.16937 | -0.21057 | -0.23346 | -0.10071 | 0.12817 | 61.7798 | 62.1094 | 124.8596 | 124.9969 | -0.086975 | 124.9695 | 62.0132 | -0.23346 | 124.9969 | -0.086975 | 62.0132 | 124.8596 | 124.9695 | -125.2853 | -125.3037
193.6406 | 125.2991 | -61.9995 | 63.1348 | 0.14214 | 0.013751 | 0.014259 | 0.0053491 | 0.068035 | -0.0014313 | 0.068599 | -62.0911 | 63.1165 | -62.1964 | -62.2055 | 62.7823 | -0.041199 | -0.013733 | 0.032043 | 63.0661 | -62.2604 | -0.19684 | -0.018311 | -0.091552 | -0.20599 | -0.35248 | -0.26093 | -0.068665 | 0.10529 | 61.9858 | 62.0316 | 124.7818 | 125.116 | -0.091552 | 125.0656 | 61.9583 | -0.26093 | 125.116 | -0.091552 | 61.9583 | 124.7818 | 125.0656 | -125.3311 | -125.3952
194.6406 | 125.3632 | -61.9858 | 63.1348 | 0.11925 | 0.012897 | 0.016823 | 0.0032129 | 0.069103 | 0.00027774 | 0.06988 | -62.0911 | 63.0936 | -62.2192 | -62.178 | 62.8143 | -0.009155 | -0.073242 | 0.050354 | 63.0844 | -62.2559 | -0.23346 | -0.041199 | -0.10529 | -0.19226 | -0.32043 | -0.27008 | -0.050354 | 0.12817 | 61.9125 | 62.0361 | 124.8001 | 125.0793 | -0.10529 | 125.0702 | 61.9766 | -0.27008 | 125.0793 | -0.10529 | 61.9766 | 124.8001 | 125.0702 | -125.354 | -125.3906
195.6406 | 125.3357 | -62.0224 | 63.1622 | -0.92598 | 0.012042 | 0.014473 | 0.0062035 | 0.067608 | -0.00036306 | 0.069239 | -62.0773 | 63.1393 | -62.2009 | -62.2284 | 62.7869 | -0.054932 | 0.013733 | 0.018311 | 63.0753 | -62.2513 | -0.17853 | -0.022888 | -0.054932 | -0.20599 | -0.37537 | -0.22888 | -0.086975 | 0.1236 | 62.0361 | 62.0407 | 124.8093 | 125.1617 | -0.054932 | 125.0977 | 61.9675 | -0.22888 | 125.1617 | -0.054932 | 61.9675 | 124.8093 | 125.0977 | -125.3632 | -125.4135
196.6406 | 125.4501 | -61.9217 | 63.1348 | -0.17067 | 0.0088375 | 0.0099869 | -0.0038367 | 0.066753 | -0.00057686 | 0.068812 | -62.0499 | 63.0157 | -62.1872 | -62.0911 | 62.9242 | 0.14648 | -0.073242 | 0.25635 | 63.0432 | -62.1597 | -0.2655 | -0.11902 | -0.12817 | -0.16937 | -0.21057 | -0.23804 | -0.091553 | 0.13733 | 61.8484 | 62.178 | 124.8459 | 124.9374 | -0.12817 | 124.9649 | 62.0682 | -0.23804 | 124.9374 | -0.12817 | 62.0682 | 124.8459 | 124.9649 | -125.322 | -125.2945
197.6406 | 125.3769 | -61.9583 | 63.1165 | 0.08873 | 0.0094785 | 0.01191 | -0.0010597 | 0.063976 | 0.00027774 | 0.069667 | -62.0728 | 63.0203 | -62.1689 | -62.1735 | 62.8555 | 0.036621 | -0.11902 | 0.11444 | 63.0203 | -62.2147 | -0.21057 | -0.09613 | -0.11444 | -0.21515 | -0.26093 | -0.25635 | -0.09613 | 0.09613 | 61.8393 | 62.0728 | 124.8138 | 124.9786 | -0.11444 | 124.9786 | 61.9949 | -0.25635 | 124.9786 | -0.11444 | 61.9949 | 124.8138 | 124.9786 | -125.2853 | -125.3311
198.6406 | 125.3174 | -62.0087 | 63.1714 | 0.096359 | 0.011401 | 0.013832 | 0.0079125 | 0.064403 | 0.00091854 | 0.068812 | -62.0682 | 63.1348 | -62.2101 | -62.2238 | 62.7823 | -0.027466 | 0.050354 | 0.036621 | 63.089 | -62.2604 | -0.20142 | -0.036621 | -0.059509 | -0.21515 | -0.3891 | -0.25177 | -0.082398 | 0.14191 | 62.059 | 62.0453 | 124.791 | 125.1434 | -0.059509 | 125.0977 | 61.9812 | -0.25177 | 125.1434 | -0.059509 | 61.9812 | 124.791 | 125.0977 | -125.3815 | -125.4318
199.6406 | 125.3037 | -61.9995 | 63.1485 | 0.020065 | 0.011615 | 0.014259 | 0.0057763 | 0.068035 | 6.414e-05 | 0.069026 | -62.027 | 63.1302 | -62.1964 | -62.1872 | 62.796 | -0.027466 | 0.013733 | 0.07782 | 63.121 | -62.2513 | -0.19684 | -0.018311 | -0.027466 | -0.18768 | -0.35248 | -0.25177 | -0.027466 | 0.16937 | 62.0132 | 62.0773 | 124.7955 | 125.1297 | -0.027466 | 125.1205 | 61.972 | -0.25177 | 125.1297 | -0.027466 | 61.972 | 124.7955 | 125.1205 | -125.3448 | -125.3998
200.6406 | 125.3128 | -62.0132 | 63.1393 | 0.15739 | 0.011401 | 0.016182 | 0.0021447 | 0.067394 | -0.00036306 | 0.070308 | -62.1048 | 63.1348 | -62.2147 | -62.2284 | 62.796 | -0.054932 | -0.004578 | 0.013733 | 63.089 | -62.265 | -0.20142 | -0.004577 | -0.091552 | -0.21515 | -0.34332 | -0.25177 | -0.050354 | 0.10986 | 62.0087 | 62.027 | 124.8093 | 125.148 | -0.091552 | 125.1022 | 61.9583 | -0.25177 | 125.148 | -0.091552 | 61.9583 | 124.8093 | 125.1022 | -125.354 | -125.4044
201.6406 | 125.3815 | -61.9629 | 63.121 | 0.14214 | 0.010333 | 0.012337 | -0.0042639 | 0.067821 | -0.00079046 | 0.06988 | -62.059 | 63.0112 | -62.2009 | -62.1597 | 62.8784 | 0.064087 | -0.14191 | 0.13733 | 63.0524 | -62.1964 | -0.23804 | -0.10986 | -0.09613 | -0.19684 | -0.24261 | -0.23346 | -0.068665 | 0.14191 | 61.821 | 62.1002 | 124.8413 | 124.9741 | -0.09613 | 125.0153 | 62.027 | -0.23346 | 124.9741 | -0.09613 | 62.027 | 124.8413 | 125.0153 | -125.322 | -125.3174
202.6406 | 125.4089 | -61.9446 | 63.1027 | -0.056229 | 0.0096921 | 0.016182 | 0.0010767 | 0.066967 | -0.0027131 | 0.067531 | -61.9904 | 63.0432 | -62.1643 | -62.1323 | 62.8922 | 0.068665 | -0.17853 | 0.15564 | 63.0524 | -62.2101 | -0.21973 | -0.059509 | -0.045776 | -0.18768 | -0.21057 | -0.2655 | -0.050354 | 0.17395 | 61.7661 | 62.1002 | 124.8367 | 124.9878 | -0.045776 | 124.9969 | 62.0132 | -0.2655 | 124.9878 | -0.045776 | 62.0132 | 124.8367 | 124.9969 | -125.267 | -125.3128
203.6406 | 125.3128 | -61.9904 | 63.1577 | -0.025711 | 0.014606 | 0.015541 | 0.0049219 | 0.066539 | -0.00014946 | 0.070094 | -62.0407 | 63.1302 | -62.1918 | -62.1689 | 62.8052 | 0.013733 | 0.027466 | 0.086975 | 63.0753 | -62.2604 | -0.20142 | -0.027466 | -0.050354 | -0.17853 | -0.35248 | -0.27008 | -0.082398 | 0.15106 | 62.0178 | 62.0773 | 124.7955 | 125.1205 | -0.050354 | 125.0656 | 62.0041 | -0.27008 | 125.1205 | -0.050354 | 62.0041 | 124.7955 | 125.0656 | -125.3494 | -125.4181
204.6406 | 125.2625 | -61.9949 | 63.1485 | 0.0811 | 0.011401 | 0.012978 | 0.0038537 | 0.068035 | -0.0012177 | 0.06988 | -62.059 | 63.1256 | -62.2009 | -62.2147 | 62.7914 | -0.032043 | 0.027466 | 0.041199 | 63.0936 | -62.2513 | -0.20599 | -0.022889 | -0.064087 | -0.21973 | -0.35706 | -0.25635 | -0.054932 | 0.14191 | 62.0224 | 62.0361 | 124.7864 | 125.1205 | -0.064087 | 125.0885 | 61.9629 | -0.25635 | 125.1205 | -0.064087 | 61.9629 | 124.7864 | 125.0885 | -125.3494 | -125.3998
205.6406 | 125.3494 | -61.9583 | 63.1668 | -0.063858 | 0.01311 | 0.018532 | 0.0055627 | 0.069103 | -0.0022859 | 0.069667 | -62.0041 | 63.1485 | -62.1964 | -62.1506 | 62.8601 | 0.054932 | 0.018311 | 0.1236 | 63.1256 | -62.265 | -0.23804 | -0.01831 | -0.045776 | -0.19226 | -0.3067 | -0.3067 | -0.041199 | 0.19226 | 61.9766 | 62.0819 | 124.8184 | 125.1068 | -0.045776 | 125.0839 | 62.0132 | -0.3067 | 125.1068 | -0.045776 | 62.0132 | 124.8184 | 125.0839 | -125.3632 | -125.4318
206.6562 | 125.3952 | -61.9858 | 63.1119 | 0.15739 | 0.0096921 | 0.011482 | -0.0042639 | 0.067608 | -0.00014946 | 0.071162 | -62.0636 | 63.002 | -62.2147 | -62.1597 | 62.8601 | 0.036621 | -0.1236 | 0.1236 | 63.0478 | -62.1872 | -0.22888 | -0.10986 | -0.07782 | -0.17395 | -0.25177 | -0.20142 | -0.064086 | 0.15106 | 61.8622 | 62.1094 | 124.8459 | 124.9878 | -0.07782 | 125.0336 | 62.0224 | -0.20142 | 124.9878 | -0.07782 | 62.0224 | 124.8459 | 125.0336 | -125.3265 | -125.2991
207.6406 | 125.3357 | -61.9904 | 63.1256 | 0.12688 | 0.012042 | 0.015328 | 0.0040673 | 0.066326 | -0.0024995 | 0.068171 | -62.0911 | 63.1256 | -62.2192 | -62.2101 | 62.7823 | -0.036621 | -0.050354 | 0.036621 | 63.0569 | -62.2696 | -0.22888 | 0 | -0.10071 | -0.21973 | -0.34332 | -0.27924 | -0.068664 | 0.12817 | 61.94 | 62.027 | 124.7726 | 125.116 | -0.10071 | 125.0473 | 61.9537 | -0.27924 | 125.116 | -0.10071 | 61.9537 | 124.7726 | 125.0473 | -125.3448 | -125.3952
208.6406 | 125.3769 | -62.0178 | 63.1577 | 0.18028 | 0.012897 | 0.016182 | 0.0047081 | 0.067608 | -0.0020721 | 0.069026 | -62.0682 | 63.1485 | -62.2009 | -62.233 | 62.764 | -0.054932 | 0.045776 | -0.11444 | 63.0707 | -62.2696 | -0.18311 | -0.009155 | -0.050354 | -0.21515 | -0.39368 | -0.25177 | -0.086975 | 0.13275 | 62.0636 | 61.9034 | 124.7818 | 125.1663 | -0.050354 | 125.0885 | 61.9629 | -0.25177 | 125.1663 | -0.050354 | 61.9629 | 124.7818 | 125.0885 | -125.3586 | -125.4272
209.6406 | 125.3494 | -61.9904 | 63.1668 | -0.16304 | 0.012683 | 0.018318 | 0.0036401 | 0.067608 | -0.00014946 | 0.070521 | -61.9812 | 63.1119 | -62.2192 | -62.114 | 62.8555 | 0.086975 | 0.050354 | 0.18768 | 63.1073 | -62.2421 | -0.22888 | -0.054932 | 0.009155 | -0.1236 | -0.31128 | -0.25177 | -0.059509 | 0.23804 | 62.0407 | 62.178 | 124.8459 | 125.1022 | 0.009155 | 125.0977 | 62.0773 | -0.25177 | 125.1022 | 0.009155 | 62.0773 | 124.8459 | 125.0977 | -125.386 | -125.4089
210.6406 | 125.4593 | -61.9629 | 63.1302 | -0.18593 | 0.011401 | 0.016182 | 0.0017175 | 0.068676 | -0.00036306 | 0.06988 | -62.0224 | 63.1256 | -62.1689 | -62.1323 | 62.8555 | 0.082397 | 0.050354 | 0.17395 | 63.121 | -62.2238 | -0.20599 | -0.004578 | -0.059509 | -0.16937 | -0.27466 | -0.26093 | -0.009155 | 0.14648 | 62.0132 | 62.1368 | 124.8184 | 125.0885 | -0.059509 | 125.0839 | 62.0453 | -0.26093 | 125.0885 | -0.059509 | 62.0453 | 124.8184 | 125.0839 | -125.2991 | -125.354
211.6406 | 125.3357 | -62.0041 | 63.1165 | 0.11925 | 0.011615 | 0.015755 | 0.0015039 | 0.06953 | 0.00070494 | 0.070094 | -62.0819 | 63.121 | -62.2009 | -62.2192 | 62.7914 | -0.027466 | -0.064087 | 0.032043 | 63.121 | -62.2559 | -0.19684 | 0.004578 | -0.07782 | -0.21515 | -0.32501 | -0.25177 | 0.004578 | 0.11902 | 61.94 | 62.0361 | 124.7955 | 125.1251 | -0.07782 | 125.1251 | 61.9766 | -0.25177 | 125.1251 | -0.07782 | 61.9766 | 124.7955 | 125.1251 | -125.3174 | -125.3723
212.6406 | 125.267 | -61.9812 | 63.1485 | -0.21645 | 0.015033 | 0.014473 | 0.0038537 | 0.067608 | -0.0010041 | 0.069453 | -62.0178 | 63.1485 | -62.1689 | -62.1368 | 62.8647 | 0.068665 | 0.050354 | 0.17853 | 63.1073 | -62.2559 | -0.18768 | 0 | -0.036621 | -0.15564 | -0.28381 | -0.27466 | -0.041199 | 0.15106 | 62.0316 | 62.1597 | 124.8459 | 125.1297 | -0.036621 | 125.0885 | 62.0499 | -0.27466 | 125.1297 | -0.036621 | 62.0499 | 124.8459 | 125.0885 | -125.3174 | -125.4044
213.6406 | 125.354 | -61.9446 | 63.1668 | -0.18593 | 0.011615 | 0.0099869 | 0.0012903 | 0.068676 | -0.0020721 | 0.068599 | -62.0316 | 63.1393 | -62.2192 | -62.1414 | 62.8372 | 0.086975 | 0.068665 | 0.17395 | 63.1073 | -62.233 | -0.27466 | -0.027466 | -0.086975 | -0.19684 | -0.32959 | -0.28839 | -0.059509 | 0.18768 | 62.0132 | 62.1185 | 124.7818 | 125.0839 | -0.086975 | 125.0519 | 62.0316 | -0.28839 | 125.0839 | -0.086975 | 62.0316 | 124.7818 | 125.0519 | -125.386 | -125.3998
214.6406 | 125.441 | -61.9949 | 63.1668 | -0.14015 | 0.011615 | 0.018105 | 0.0027855 | 0.067821 | 0.0013457 | 0.070521 | -62.0087 | 63.1439 | -62.1872 | -62.1277 | 62.8601 | 0.07782 | 0.064087 | -0.09613 | 63.1073 | -62.2604 | -0.19226 | -0.022888 | -0.013733 | -0.13275 | -0.3067 | -0.2655 | -0.059509 | 0.17853 | 62.059 | 61.8988 | 124.855 | 125.1389 | -0.013733 | 125.1022 | 62.0728 | -0.2655 | 125.1389 | -0.013733 | 62.0728 | 124.855 | 125.1022 | -125.354 | -125.4272
215.6406 | 125.2945 | -61.9858 | 63.1805 | -0.23933 | 0.010974 | 0.010414 | -0.00063225 | 0.066753 | -0.00079046 | 0.070948 | -62.0773 | 63.1393 | -62.1964 | -62.1689 | 62.8372 | 0.054932 | 0.14648 | 0.14648 | 63.1485 | -62.2055 | -0.21057 | -0.041199 | -0.091553 | -0.1831 | -0.34332 | -0.21973 | -0.032043 | 0.11902 | 62.1323 | 62.1323 | 124.823 | 125.1251 | -0.091553 | 125.1343 | 62.0407 | -0.21973 | 125.1251 | -0.091553 | 62.0407 | 124.823 | 125.1343 | -125.3769 | -125.386
216.6406 | 125.3448 | -61.9766 | 63.1577 | -0.28511 | 0.01311 | 0.0095595 | 0.00064935 | 0.067821 | -0.0010041 | 0.069453 | -62.0544 | 63.1393 | -62.1964 | -62.1689 | 62.8235 | 0.068665 | 0.11902 | 0.16479 | 63.1531 | -62.2192 | -0.21973 | -0.018311 | -0.077819 | -0.19226 | -0.33417 | -0.24261 | -0.004578 | 0.14191 | 62.0956 | 62.1414 | 124.8001 | 125.116 | -0.077819 | 125.1297 | 62.0453 | -0.24261 | 125.116 | -0.077819 | 62.0453 | 124.8001 | 125.1297 | -125.354 | -125.3769
217.6406 | 125.3311 | -61.9858 | 63.1577 | -0.056229 | 0.011401 | 0.016823 | 0.0032129 | 0.068676 | -0.0012177 | 0.068599 | -62.0407 | 63.121 | -62.1918 | -62.1689 | 62.8326 | 0.041199 | 0.032043 | 0.091553 | 63.121 | -62.2604 | -0.20599 | -0.036621 | -0.054931 | -0.1831 | -0.32501 | -0.27466 | -0.036621 | 0.15106 | 62.0178 | 62.0773 | 124.8184 | 125.1068 | -0.054931 | 125.1068 | 62.027 | -0.27466 | 125.1068 | -0.054931 | 62.027 | 124.8184 | 125.1068 | -125.3494 | -125.4181
218.6406 | 125.322 | -61.9949 | 63.1668 | -0.20882 | 0.0096921 | 0.0089187 | 0.00086295 | 0.068248 | -0.00079046 | 0.070308 | -62.0956 | 63.1119 | -62.1826 | -62.1826 | 62.8281 | 0.059509 | 0.14648 | 0.14191 | 63.1485 | -62.233 | -0.18768 | -0.054932 | -0.10071 | -0.18768 | -0.33875 | -0.23804 | -0.01831 | 0.086975 | 62.1414 | 62.1368 | 124.823 | 125.1068 | -0.10071 | 125.1434 | 62.0544 | -0.23804 | 125.1068 | -0.10071 | 62.0544 | 124.823 | 125.1434 | -125.3494 | -125.3998
219.6406 | 125.3265 | -61.9629 | 63.176 | -0.25459 | 0.010119 | 0.0095595 | -0.0038367 | 0.066112 | -0.0016449 | 0.068385 | -62.0224 | 63.0753 | -62.1735 | -62.1552 | 62.8784 | 0.10071 | 0.11444 | 0.21057 | 63.1256 | -62.2009 | -0.21057 | -0.10071 | -0.059509 | -0.19226 | -0.29755 | -0.23804 | -0.050354 | 0.15106 | 62.0773 | 62.1735 | 124.8413 | 125.0381 | -0.059509 | 125.0885 | 62.0636 | -0.23804 | 125.0381 | -0.059509 | 62.0636 | 124.8413 | 125.0885 | -125.3494 | -125.3769
220.6406 | 125.3128 | -61.9629 | 63.1851 | -0.24696 | 0.010547 | 0.011269 | 0.0012903 | 0.06483 | -0.0033539 | 0.069239 | -62.0819 | 63.1073 | -62.2009 | -62.1872 | 62.8326 | 0.064087 | 0.14191 | 0.15564 | 63.1622 | -62.2101 | -0.23804 | -0.07782 | -0.11902 | -0.2243 | -0.35248 | -0.24719 | -0.022889 | 0.11902 | 62.1048 | 62.1185 | 124.7955 | 125.0702 | -0.11902 | 125.1251 | 62.027 | -0.24719 | 125.0702 | -0.11902 | 62.027 | 124.7955 | 125.1251 | -125.386 | -125.3952
221.6406 | 125.3265 | -61.9858 | 63.1577 | -0.2317 | 0.0094785 | 0.012764 | 0.00043575 | 0.066539 | -0.0022859 | 0.069239 | -62.0453 | 63.0432 | -62.178 | -62.1552 | 62.8601 | 0.082397 | 0.10986 | 0.21057 | 63.1256 | -62.2147 | -0.19226 | -0.11444 | -0.059509 | -0.16937 | -0.29755 | -0.22888 | -0.032044 | 0.13275 | 62.0956 | 62.1964 | 124.8459 | 125.029 | -0.059509 | 125.1114 | 62.0682 | -0.22888 | 125.029 | -0.059509 | 62.0682 | 124.8459 | 125.1114 | -125.3357 | -125.3723
222.6562 | 125.2762 | -62.0041 | 63.1577 | -0.010452 | 0.014606 | 0.012764 | 0.0068445 | 0.068676 | 0.0019867 | 0.068171 | -62.059 | 63.1393 | -62.1872 | -62.2009 | 62.7823 | -0.036621 | 0.032043 | 0.036621 | 63.1393 | -62.2604 | -0.18311 | -0.018311 | -0.054932 | -0.19684 | -0.37537 | -0.25635 | -0.018311 | 0.12817 | 62.0361 | 62.0407 | 124.7864 | 125.1434 | -0.054932 | 125.1434 | 61.9675 | -0.25635 | 125.1434 | -0.054932 | 61.9675 | 124.7864 | 125.1434 | -125.3448 | -125.4181
223.6406 | 125.3769 | -61.9263 | 63.1668 | -0.20119 | 0.0056333 | 0.01255 | -0.0025549 | 0.066112 | 0.0017731 | 0.067958 | -62.0087 | 63.0249 | -62.178 | -62.0865 | 62.8922 | 0.14648 | 0.018311 | 0.27466 | 63.121 | -62.178 | -0.25177 | -0.14191 | -0.082397 | -0.16022 | -0.27466 | -0.25177 | -0.045776 | 0.16937 | 61.9446 | 62.2009 | 124.8184 | 124.9512 | -0.082397 | 125.0473 | 62.0728 | -0.25177 | 124.9512 | -0.082397 | 62.0728 | 124.8184 | 125.0473 | -125.3448 | -125.3448
224.6406 | 125.3494 | -61.9812 | 63.1622 | -0.26222 | 0.0075559 | 0.0084915 | -0.0014869 | 0.066967 | -0.0016449 | 0.069026 | -62.027 | 63.0478 | -62.178 | -62.1414 | 62.8876 | 0.1236 | 0.086975 | 0.23346 | 63.1165 | -62.1918 | -0.19684 | -0.11444 | -0.045777 | -0.16022 | -0.27466 | -0.21057 | -0.045776 | 0.15106 | 62.0682 | 62.2147 | 124.8688 | 125.029 | -0.045777 | 125.0977 | 62.1048 | -0.21057 | 125.029 | -0.045777 | 62.1048 | 124.8688 | 125.0977 | -125.3403 | -125.354
225.6406 | 125.4593 | -61.8988 | 63.1439 | -0.14778 | 0.0077695 | 0.010841 | -0.0014869 | 0.065471 | 0.00070494 | 0.070521 | -61.9995 | 63.0066 | -62.1506 | -62.0544 | 62.9379 | 0.15564 | -0.041199 | 0.28381 | 63.0936 | -62.1735 | -0.25177 | -0.13733 | -0.10071 | -0.15564 | -0.20599 | -0.27466 | -0.050354 | 0.15106 | 61.8576 | 62.1826 | 124.8367 | 124.9054 | -0.10071 | 124.9924 | 62.0544 | -0.27466 | 124.9054 | -0.10071 | 62.0544 | 124.8367 | 124.9924 | -125.2945 | -125.3174
226.6406 | 125.4135 | -61.9354 | 63.1531 | -0.19356 | 0.010119 | 0.0072097 | 0.0015039 | 0.06419 | -0.00079046 | 0.069453 | -62.0041 | 63.0386 | -62.178 | -62.0773 | 62.9196 | 0.15564 | 0.004578 | 0.2655 | 63.089 | -62.1964 | -0.24262 | -0.11444 | -0.068664 | -0.14191 | -0.23346 | -0.26093 | -0.064087 | 0.17395 | 61.94 | 62.2009 | 124.855 | 124.9741 | -0.068664 | 125.0244 | 62.0911 | -0.26093 | 124.9741 | -0.068664 | 62.0911 | 124.855 | 125.0244 | -125.3311 | -125.3494
227.6406 | 125.3037 | -61.9812 | 63.1714 | -0.20882 | 0.012256 | 0.011696 | 0.0034265 | 0.065899 | -0.0016449 | 0.067531 | -62.0499 | 63.1073 | -62.1552 | -62.1552 | 62.8098 | 0.050354 | 0.13733 | 0.16937 | 63.1256 | -62.2009 | -0.17395 | -0.064087 | -0.068665 | -0.17395 | -0.36163 | -0.21973 | -0.045777 | 0.10528 | 62.1185 | 62.1506 | 124.791 | 125.0885 | -0.068665 | 125.1068 | 62.0316 | -0.21973 | 125.0885 | -0.068665 | 62.0316 | 124.791 | 125.1068 | -125.3265 | -125.3723
228.6406 | 125.4135 | -61.9492 | 63.1531 | -0.20119 | 0.0073423 | 0.010414 | 0.00043575 | 0.063121 | -0.0010041 | 0.069453 | -61.9995 | 63.0157 | -62.1597 | -62.0636 | 62.9105 | 0.13733 | -0.004578 | 0.27466 | 63.0981 | -62.1735 | -0.21057 | -0.13733 | -0.050354 | -0.11444 | -0.24262 | -0.2243 | -0.054931 | 0.16022 | 61.9446 | 62.2238 | 124.8596 | 124.9649 | -0.050354 | 125.0473 | 62.0865 | -0.2243 | 124.9649 | -0.050354 | 62.0865 | 124.8596 | 125.0473 | -125.3128 | -125.3265
229.6406 | 125.5417 | -61.8851 | 63.1439 | -0.22408 | 0.0088375 | 0.010628 | -0.0023413 | 0.06483 | 0.0017731 | 0.068812 | -62.0041 | 63.0386 | -62.1826 | -62.0682 | 62.9471 | 0.16937 | -0.086975 | 0.28839 | 63.0569 | -62.1643 | -0.29755 | -0.10529 | -0.11902 | -0.1831 | -0.19684 | -0.27924 | -0.086975 | 0.17853 | 61.7981 | 62.1735 | 124.8322 | 124.9237 | -0.11902 | 124.942 | 62.0544 | -0.27924 | 124.9237 | -0.11902 | 62.0544 | 124.8322 | 124.942 | -125.3265 | -125.3082
230.6406 | 125.4227 | -61.9263 | 63.1531 | -0.12489 | 0.0090513 | 0.01191 | -0.0036231 | 0.063121 | -0.00014946 | 0.069239 | -62.0361 | 62.9974 | -62.1368 | -62.0956 | 62.9059 | 0.14191 | -0.073242 | 0.24719 | 63.0569 | -62.1964 | -0.21057 | -0.15564 | -0.10986 | -0.16937 | -0.24719 | -0.27008 | -0.09613 | 0.10071 | 61.853 | 62.1735 | 124.8322 | 124.9237 | -0.10986 | 124.9832 | 62.0682 | -0.27008 | 124.9237 | -0.10986 | 62.0682 | 124.8322 | 124.9832 | -125.2899 | -125.3494
231.6406 | 125.4089 | -61.9446 | 63.1302 | -0.063858 | 0.0073423 | 0.0099869 | -0.00084605 | 0.060558 | -0.00057686 | 0.069453 | -62.0499 | 62.9837 | -62.1918 | -62.1002 | 62.8876 | 0.10986 | -0.07782 | 0.22888 | 63.0615 | -62.1643 | -0.24719 | -0.14648 | -0.10529 | -0.15564 | -0.24261 | -0.21973 | -0.068665 | 0.14191 | 61.8668 | 62.1735 | 124.8322 | 124.9283 | -0.10529 | 125.0061 | 62.0544 | -0.21973 | 124.9283 | -0.10529 | 62.0544 | 124.8322 | 125.0061 | -125.322 | -125.2945
232.6562 | 125.3632 | -61.9766 | 63.1622 | -0.1783 | 0.0099057 | 0.0149 | 0.0076989 | 0.063335 | -0.0010041 | 0.06689 | -61.9904 | 63.1165 | -62.1689 | -62.1094 | 62.8464 | 0.12817 | -0.20142 | 0.17395 | 63.0615 | -62.2604 | -0.19226 | -0.045776 | -0.013732 | -0.13275 | -0.31586 | -0.28381 | -0.10071 | 0.17853 | 61.7752 | 62.1506 | 124.823 | 125.0931 | -0.013732 | 125.0381 | 62.1048 | -0.28381 | 125.0931 | -0.013732 | 62.1048 | 124.823 | 125.0381 | -125.3311 | -125.4227
233.6406 | 125.3998 | -61.9675 | 63.1256 | 0.035324 | 0.0067013 | 0.014259 | -0.0021277 | 0.065471 | 0.00070494 | 0.069667 | -62.0819 | 62.9974 | -62.1872 | -62.1414 | 62.8647 | 0.059509 | -0.073242 | 0.16022 | 63.0981 | -62.1643 | -0.21973 | -0.12817 | -0.11444 | -0.17395 | -0.26093 | -0.19684 | -0.027465 | 0.10529 | 61.8942 | 62.1277 | 124.8322 | 124.9649 | -0.11444 | 125.0656 | 62.027 | -0.19684 | 124.9649 | -0.11444 | 62.027 | 124.8322 | 125.0656 | -125.3128 | -125.2899
234.6406 | 125.4181 | -61.9629 | 63.1439 | -0.010452 | 0.010974 | 0.011482 | -0.0025549 | 0.063762 | 0.00027774 | 0.069667 | -62.0407 | 62.9883 | -62.2101 | -62.114 | 62.8693 | 0.082397 | -0.059509 | 0.1831 | 63.0661 | -62.1872 | -0.24719 | -0.15564 | -0.077819 | -0.15106 | -0.27466 | -0.2243 | -0.07782 | 0.16937 | 61.9034 | 62.146 | 124.8322 | 124.9512 | -0.077819 | 125.029 | 62.0453 | -0.2243 | 124.9512 | -0.077819 | 62.0453 | 124.8322 | 125.029 | -125.354 | -125.3311
235.6406 | 125.3632 | -61.9308 | 63.1485 | -0.048599 | 0.0081967 | 0.013191 | 0.00043575 | 0.062267 | 0.00070494 | 0.069453 | -62.0682 | 62.9974 | -62.1872 | -62.1231 | 62.851 | 0.068665 | -0.064087 | 0.18768 | 63.0569 | -62.1826 | -0.25635 | -0.15106 | -0.13733 | -0.19226 | -0.29755 | -0.25177 | -0.091553 | 0.11902 | 61.8668 | 62.1185 | 124.7818 | 124.9283 | -0.13733 | 124.9878 | 61.9995 | -0.25177 | 124.9283 | -0.13733 | 61.9995 | 124.7818 | 124.9878 | -125.3357 | -125.3311
236.6406 | 125.3769 | -61.9492 | 63.1165 | -0.048599 | 0.0081967 | 0.010414 | -0.00063225 | 0.062908 | -0.0012177 | 0.069239 | -62.0544 | 62.9837 | -62.1643 | -62.1094 | 62.883 | 0.082397 | -0.068665 | 0.19684 | 63.0341 | -62.1964 | -0.21515 | -0.13275 | -0.10529 | -0.16022 | -0.23346 | -0.24719 | -0.082397 | 0.10986 | 61.8805 | 62.146 | 124.8322 | 124.9329 | -0.10529 | 124.9832 | 62.0316 | -0.24719 | 124.9329 | -0.10529 | 62.0316 | 124.8322 | 124.9832 | -125.2808 | -125.3128
237.6406 | 125.3128 | -61.9537 | 63.1897 | -0.30037 | 0.0077695 | 0.01191 | 0.00086295 | 0.060985 | -0.0012177 | 0.06988 | -62.0316 | 63.0798 | -62.1735 | -62.1368 | 62.8418 | 0.073242 | 0.1236 | 0.21057 | 63.1165 | -62.2147 | -0.21973 | -0.10986 | -0.07782 | -0.18311 | -0.3479 | -0.26093 | -0.073242 | 0.14191 | 62.0773 | 62.1643 | 124.7955 | 125.0336 | -0.07782 | 125.0702 | 62.027 | -0.26093 | 125.0336 | -0.07782 | 62.027 | 124.7955 | 125.0702 | -125.3632 | -125.4044
238.6406 | 125.3952 | -61.9583 | 63.121 | 0.10399 | 0.0090513 | 0.010841 | 0.00022215 | 0.062053 | -0.0012177 | 0.070308 | -62.0682 | 62.9929 | -62.1918 | -62.1552 | 62.8235 | 0.027466 | -0.10986 | 0.11902 | 63.0157 | -62.1918 | -0.23346 | -0.12817 | -0.10986 | -0.19684 | -0.29755 | -0.23346 | -0.10529 | 0.1236 | 61.8484 | 62.0773 | 124.7818 | 124.9512 | -0.10986 | 124.9741 | 61.9858 | -0.23346 | 124.9512 | -0.10986 | 61.9858 | 124.7818 | 124.9741 | -125.3128 | -125.3128
239.6406 | 125.3906 | -61.9446 | 63.1348 | 0.17265 | 0.0096921 | 0.01191 | 0.00086295 | 0.062908 | -0.00036306 | 0.068171 | -62.0361 | 62.9745 | -62.1872 | -62.1231 | 62.8601 | 0.027466 | -0.13733 | 0.12817 | 63.0249 | -62.2055 | -0.24262 | -0.16022 | -0.091553 | -0.17853 | -0.27466 | -0.26093 | -0.10986 | 0.15106 | 61.8073 | 62.0728 | 124.8047 | 124.9191 | -0.091553 | 124.9695 | 61.972 | -0.26093 | 124.9191 | -0.091553 | 61.972 | 124.8047 | 124.9695 | -125.322 | -125.3403
240.6406 | 125.3632 | -61.9492 | 63.121 | 0.14976 | 0.010547 | 0.0095595 | 0.00043575 | 0.063335 | -0.0031403 | 0.068385 | -62.0132 | 62.9837 | -62.1872 | -62.0956 | 62.8693 | 0.041199 | -0.16479 | 0.14648 | 63.0112 | -62.1918 | -0.23804 | -0.13733 | -0.064087 | -0.14648 | -0.25177 | -0.24261 | -0.10986 | 0.17395 | 61.7844 | 62.0956 | 124.8184 | 124.9329 | -0.064087 | 124.9603 | 61.9904 | -0.24261 | 124.9329 | -0.064087 | 61.9904 | 124.8184 | 124.9603 | -125.3082 | -125.3128
241.6406 | 125.3586 | -61.9537 | 63.1119 | 0.13451 | 0.0069149 | 0.01191 | 0.0023583 | 0.063549 | -0.00036306 | 0.070521 | -62.0544 | 62.9883 | -62.1964 | -62.1368 | 62.8555 | 0.022888 | -0.14648 | 0.12817 | 63.0295 | -62.2055 | -0.24262 | -0.1236 | -0.10071 | -0.18311 | -0.25635 | -0.25177 | -0.082397 | 0.14191 | 61.8073 | 62.0819 | 124.8093 | 124.942 | -0.10071 | 124.9832 | 61.9766 | -0.25177 | 124.942 | -0.10071 | 61.9766 | 124.8093 | 124.9832 | -125.3082 | -125.3174
242.6562 | 125.2945 | -61.9949 | 63.1622 | -0.2317 | 0.010974 | 0.011696 | 8.546e-06 | 0.063762 | 0.0015595 | 0.067531 | -62.0728 | 63.0936 | -62.1689 | -62.2101 | 62.8555 | 0.032043 | 0.12817 | 0.16022 | 63.0798 | -62.2421 | -0.17395 | -0.068664 | -0.07782 | -0.21515 | -0.3067 | -0.24719 | -0.082397 | 0.09613 | 62.1231 | 62.1552 | 124.8505 | 125.0885 | -0.07782 | 125.0748 | 62.027 | -0.24719 | 125.0885 | -0.07782 | 62.027 | 124.8505 | 125.0748 | -125.3311 | -125.4044
243.6406 | 125.4044 | -61.9308 | 63.1027 | 0.17265 | 0.0092649 | 0.012123 | 0.0015039 | 0.063121 | -0.0016449 | 0.069667 | -61.9995 | 63.0112 | -62.178 | -62.0956 | 62.8738 | 0.054932 | -0.17853 | 0.14648 | 63.0157 | -62.2101 | -0.24719 | -0.091553 | -0.068665 | -0.16479 | -0.22888 | -0.27924 | -0.086975 | 0.17853 | 61.7523 | 62.0773 | 124.8047 | 124.942 | -0.068665 | 124.9466 | 61.9858 | -0.27924 | 124.942 | -0.068665 | 61.9858 | 124.8047 | 124.9466 | -125.2808 | -125.3128
244.6406 | 125.3998 | -61.9537 | 63.0981 | 0.12688 | 0.0096921 | 0.0093459 | 0.0012903 | 0.063549 | -0.0018585 | 0.068385 | -62.0087 | 63.0066 | -62.1964 | -62.114 | 62.8693 | 0.045776 | -0.17853 | 0.13275 | 63.0112 | -62.1918 | -0.24262 | -0.091553 | -0.054932 | -0.16022 | -0.22888 | -0.23804 | -0.086976 | 0.18768 | 61.7752 | 62.0865 | 124.823 | 124.9603 | -0.054932 | 124.9649 | 61.9995 | -0.23804 | 124.9603 | -0.054932 | 61.9995 | 124.823 | 124.9649 | -125.2945 | -125.2899
245.6406 | 125.4135 | -61.9446 | 63.0798 | 0.11925 | 0.011401 | 0.012978 | 0.0040673 | 0.063976 | 0.00070494 | 0.069667 | -62.0132 | 63.0066 | -62.1689 | -62.0865 | 62.8647 | 0.054932 | -0.18768 | 0.14191 | 63.0157 | -62.2009 | -0.2243 | -0.073242 | -0.068665 | -0.14191 | -0.21515 | -0.25635 | -0.064087 | 0.15564 | 61.7569 | 62.0865 | 124.8093 | 124.9512 | -0.068665 | 124.9603 | 61.9995 | -0.25635 | 124.9512 | -0.068665 | 61.9995 | 124.8093 | 124.9603 | -125.2487 | -125.2808
246.6406 | 125.4181 | -61.9537 | 63.1165 | -0.12489 | 0.0062741 | 0.012764 | 0.0025719 | 0.066326 | -0.0039947 | 0.069026 | -61.821 | 63.0112 | -62.146 | -62.0728 | 62.8784 | 0.027466 | -0.18768 | 0.14191 | 63.002 | -62.1918 | -0.19226 | -0.10529 | 0.13275 | -0.11902 | -0.23804 | -0.23804 | -0.11444 | 0.32501 | 61.7661 | 62.0956 | 124.8322 | 124.9649 | 0.13275 | 124.9557 | 61.9812 | -0.23804 | 124.9649 | 0.13275 | 61.9812 | 124.8322 | 124.9557 | -125.2625 | -125.3082
247.6406 | 125.3723 | -61.9583 | 63.0936 | 0.027695 | 0.0096921 | 0.014473 | -0.00084605 | 0.063762 | -0.00014946 | 0.067958 | -62.0819 | 62.9974 | -62.1735 | -61.9583 | 63.0524 | 0.18768 | -0.17395 | 0.14648 | 63.0707 | -62.1735 | -0.21515 | -0.09613 | -0.1236 | 0 | -0.041199 | -0.21515 | -0.022888 | 0.091553 | 61.7844 | 62.1048 | 125.0107 | 124.9557 | -0.1236 | 125.029 | 62.146 | -0.21515 | 124.9557 | -0.1236 | 62.146 | 125.0107 | 125.029 | -125.267 | -125.267
248.6406 | 125.3632 | -61.9675 | 63.0981 | 0.19554 | 0.01076 | 0.014687 | 0.0047081 | 0.065258 | 0.0015595 | 0.068599 | -62.0544 | 63.0707 | -62.178 | -62.1277 | 62.8189 | -0.004578 | -0.13275 | 0.068665 | 63.0203 | -62.2696 | -0.21057 | -0.027466 | -0.086975 | -0.16022 | -0.27924 | -0.30212 | -0.07782 | 0.1236 | 61.8347 | 62.0361 | 124.7864 | 125.0381 | -0.086975 | 124.9878 | 61.9629 | -0.30212 | 125.0381 | -0.086975 | 61.9629 | 124.7864 | 124.9878 | -125.2762 | -125.3677
249.6406 | 125.3265 | -61.9858 | 63.1119 | 0.16502 | 0.015033 | 0.014259 | 0.0053491 | 0.066326 | -0.00036306 | 0.069239 | -62.0682 | 63.0844 | -62.2055 | -62.178 | 62.7869 | -0.032043 | -0.064087 | 0.032043 | 63.0386 | -62.2375 | -0.21973 | -0.027465 | -0.082397 | -0.19226 | -0.32501 | -0.25177 | -0.073242 | 0.13733 | 61.9217 | 62.0178 | 124.7726 | 125.0702 | -0.082397 | 125.0244 | 61.9537 | -0.25177 | 125.0702 | -0.082397 | 61.9537 | 124.7726 | 125.0244 | -125.3174 | -125.3494
250.6406 | 125.3265 | -61.9766 | 63.1165 | 0.18791 | 0.014178 | 0.014687 | 0.0049219 | 0.066753 | -0.00079046 | 0.069453 | -62.0773 | 63.089 | -62.1964 | -62.2009 | 62.7869 | -0.054932 | -0.013733 | 0.009155 | 63.089 | -62.233 | -0.21973 | -0.027466 | -0.10071 | -0.2243 | -0.32959 | -0.25635 | -0.027466 | 0.11902 | 61.9629 | 61.9858 | 124.7635 | 125.0656 | -0.10071 | 125.0656 | 61.9217 | -0.25635 | 125.0656 | -0.10071 | 61.9217 | 124.7635 | 125.0656 | -125.3128 | -125.3494
251.6406 | 125.2899 | -61.9812 | 63.1165 | 0.10399 | 0.011401 | 0.017891 | -0.0012733 | 0.068462 | -0.0018585 | 0.069026 | -62.0956 | 63.1119 | -62.2055 | -62.1643 | 62.9013 | -0.009155 | -0.041199 | 0.073242 | 63.089 | -62.2421 | -0.2243 | -0.004578 | -0.11444 | -0.18311 | -0.21515 | -0.26093 | -0.027466 | 0.10986 | 61.94 | 62.0544 | 124.8825 | 125.0931 | -0.11444 | 125.0702 | 61.972 | -0.26093 | 125.0931 | -0.11444 | 61.972 | 124.8825 | 125.0702 | -125.322 | -125.3586
252.6406 | 125.473 | -61.9858 | 63.1073 | 0.18791 | 0.0092649 | 0.013832 | 0.0023583 | 0.067394 | -0.0016449 | 0.069026 | -62.0178 | 63.0386 | -62.1826 | -62.1002 | 62.8738 | 0.068665 | -0.1831 | 0.1236 | 63.0249 | -62.2055 | -0.19684 | -0.068665 | -0.032043 | -0.11444 | -0.23346 | -0.21973 | -0.082398 | 0.16479 | 61.8027 | 62.1094 | 124.8596 | 125.0244 | -0.032043 | 125.0107 | 62.0544 | -0.21973 | 125.0244 | -0.032043 | 62.0544 | 124.8596 | 125.0107 | -125.2899 | -125.3128
253.6406 | 125.2853 | -61.9904 | 63.1302 | 0.0048064 | 0.012469 | 0.013619 | 0.0066309 | 0.068889 | 0.00027774 | 0.06988 | -62.0361 | 63.1485 | -62.1689 | -62.1689 | 62.8006 | -0.009155 | 0.036621 | 0.054932 | 63.0981 | -62.2467 | -0.17853 | 0.018311 | -0.045777 | -0.17853 | -0.32959 | -0.25635 | -0.032043 | 0.13275 | 62.027 | 62.0453 | 124.791 | 125.1389 | -0.045777 | 125.0885 | 61.9812 | -0.25635 | 125.1389 | -0.045777 | 61.9812 | 124.791 | 125.0885 | -125.2991 | -125.3769
254.6406 | 125.2441 | -62.0224 | 63.1073 | 0.08873 | 0.012042 | 0.015541 | 0.0036401 | 0.066967 | -0.0016449 | 0.071376 | -62.0865 | 63.1393 | -62.1872 | -62.2055 | 62.7777 | -0.032043 | 0.050354 | 0.041199 | 63.1073 | -62.2467 | -0.1648 | 0.032043 | -0.064087 | -0.18311 | -0.32959 | -0.2243 | 0 | 0.10071 | 62.0728 | 62.0636 | 124.8001 | 125.1617 | -0.064087 | 125.1297 | 61.9904 | -0.2243 | 125.1617 | -0.064087 | 61.9904 | 124.8001 | 125.1297 | -125.2945 | -125.354
255.6406 | 125.2533 | -61.9904 | 63.1439 | 0.027695 | 0.012469 | 0.01255 | 0.0051355 | 0.068676 | -0.0020721 | 0.06988 | -62.0316 | 63.121 | -62.1872 | -62.1643 | 62.8143 | 0.013733 | 0.041199 | 0.073242 | 63.1165 | -62.2192 | -0.19684 | -0.022888 | -0.041199 | -0.17395 | -0.32959 | -0.22888 | -0.027466 | 0.15564 | 62.0316 | 62.0636 | 124.8047 | 125.1114 | -0.041199 | 125.1068 | 62.0041 | -0.22888 | 125.1114 | -0.041199 | 62.0041 | 124.8047 | 125.1068 | -125.3311 | -125.3632
256.6406 | 125.3174 | -61.9995 | 63.1256 | -0.025711 | 0.01311 | 0.010841 | 0.0029993 | 0.069316 | -0.0018585 | 0.070094 | -62.0407 | 63.1073 | -62.2009 | -62.1552 | 62.8372 | 0.045776 | 0.027466 | 0.09613 | 63.089 | -62.2238 | -0.20142 | -0.01831 | -0.041198 | -0.15564 | -0.28839 | -0.2243 | -0.036621 | 0.16022 | 62.027 | 62.0956 | 124.8367 | 125.1068 | -0.041198 | 125.0885 | 62.0453 | -0.2243 | 125.1068 | -0.041198 | 62.0453 | 124.8367 | 125.0885 | -125.3265 | -125.3494
257.6406 | 125.3448 | -61.972 | 63.0936 | 0.15739 | 0.01311 | 0.011269 | 0.00086295 | 0.068035 | -0.0012177 | 0.068385 | -62.0636 | 63.0936 | -62.2009 | -62.1506 | 62.8418 | 0.027466 | -0.1236 | 0.09613 | 63.0524 | -62.2009 | -0.22888 | 0 | -0.091553 | -0.17853 | -0.25177 | -0.22888 | -0.041199 | 0.13733 | 61.8484 | 62.0682 | 124.8138 | 125.0656 | -0.091553 | 125.0244 | 61.9995 | -0.22888 | 125.0656 | -0.091553 | 61.9995 | 124.8138 | 125.0244 | -125.2945 | -125.2945
258.6406 | 125.3723 | -61.9583 | 63.1531 | 0.027695 | 0.011828 | 0.012978 | 0.0049219 | 0.068889 | -0.0016449 | 0.069667 | -61.972 | 63.1439 | -62.1597 | -62.114 | 62.8555 | 0.086975 | 0.013733 | 0.17853 | 63.089 | -62.2238 | -0.20142 | -0.009155 | -0.013733 | -0.15564 | -0.29755 | -0.2655 | -0.064087 | 0.18768 | 61.972 | 62.1368 | 124.8138 | 125.1022 | -0.013733 | 125.0473 | 62.0453 | -0.2655 | 125.1022 | -0.013733 | 62.0453 | 124.8138 | 125.0473 | -125.3128 | -125.3769
259.6406 | 125.3128 | -61.9446 | 63.1668 | -0.086746 | 0.010119 | 0.013191 | 0.0012903 | 0.070171 | 0.0051911 | 0.072871 | -62.0041 | 63.121 | -62.1826 | -62.2879 | 62.8784 | 0.26093 | -0.013733 | 0.20599 | 63.0936 | -62.2467 | -0.23804 | -0.045776 | -0.059509 | -0.34332 | -0.28839 | -0.30212 | -0.073242 | 0.17853 | 61.9308 | 62.1506 | 124.823 | 125.0656 | -0.059509 | 125.0381 | 62.2055 | -0.30212 | 125.0656 | -0.059509 | 62.2055 | 124.823 | 125.0381 | -125.3494 | -125.4135
260.6406 | 125.322 | -61.9675 | 63.1577 | -0.18593 | 0.011188 | 0.0149 | 0.0049219 | 0.068035 | -0.0037811 | 0.068171 | -62.0041 | 63.1393 | -62.2055 | -62.1323 | 62.8647 | 0.086975 | 0.059509 | 0.1831 | 63.1119 | -62.2375 | -0.23804 | -0.018311 | -0.036621 | -0.1648 | -0.29297 | -0.27008 | -0.045777 | 0.20142 | 62.027 | 62.1506 | 124.8322 | 125.1068 | -0.036621 | 125.0793 | 62.0544 | -0.27008 | 125.1068 | -0.036621 | 62.0544 | 124.8322 | 125.0793 | -125.3632 | -125.3952
261.6406 | 125.3494 | -61.9812 | 63.1714 | -0.13252 | 0.012683 | 0.014687 | 0.0025719 | 0.070171 | -0.00014946 | 0.069453 | -62.027 | 63.1485 | -62.1918 | -62.1277 | 62.851 | 0.086975 | 0.086975 | 0.19226 | 63.1165 | -62.2009 | -0.21057 | -0.022888 | -0.045777 | -0.14648 | -0.32044 | -0.21973 | -0.054932 | 0.16479 | 62.0682 | 62.1735 | 124.8322 | 125.1297 | -0.045777 | 125.0977 | 62.0682 | -0.21973 | 125.1297 | -0.045777 | 62.0682 | 124.8322 | 125.0977 | -125.3632 | -125.3723
262.6406 | 125.2808 | -61.9812 | 63.1485 | 0.020065 | 0.01311 | 0.01255 | 0.0040673 | 0.068462 | -0.0022859 | 0.06988 | -62.0316 | 63.1165 | -62.2009 | -62.178 | 62.7823 | 0.009155 | 0.041199 | 0.068665 | 63.1027 | -62.233 | -0.21973 | -0.032044 | -0.050354 | -0.19684 | -0.36621 | -0.25177 | -0.045777 | 0.16937 | 62.0224 | 62.0499 | 124.7635 | 125.0977 | -0.050354 | 125.0839 | 61.9904 | -0.25177 | 125.0977 | -0.050354 | 61.9904 | 124.7635 | 125.0839 | -125.3494 | -125.3815
263.6406 | 125.3677 | -61.94 | 63.1302 | -0.20119 | 0.014392 | 0.014687 | 0.0025719 | 0.071453 | -0.0018585 | 0.068171 | -62.0087 | 63.1256 | -62.1872 | -62.114 | 62.8555 | 0.11444 | 0.059509 | 0.17853 | 63.1256 | -62.1964 | -0.24719 | -0.004578 | -0.068665 | -0.17395 | -0.27466 | -0.25635 | -0.004578 | 0.17853 | 61.9995 | 62.1185 | 124.7955 | 125.0656 | -0.068665 | 125.0656 | 62.0544 | -0.25635 | 125.0656 | -0.068665 | 62.0544 | 124.7955 | 125.0656 | -125.3174 | -125.3265
264.6406 | 125.3174 | -61.9492 | 63.1714 | -0.24696 | 0.01076 | 0.014473 | -0.00084605 | 0.068035 | 0.00027774 | 0.070308 | -62.0316 | 63.1348 | -62.1826 | -62.1323 | 62.8372 | 0.086975 | 0.073242 | 0.19684 | 63.1439 | -62.2284 | -0.23346 | -0.036621 | -0.082397 | -0.18311 | -0.33417 | -0.27924 | -0.027466 | 0.15106 | 62.0224 | 62.146 | 124.7864 | 125.0839 | -0.082397 | 125.0931 | 62.0361 | -0.27924 | 125.0839 | -0.082397 | 62.0361 | 124.7864 | 125.0931 | -125.354 | -125.3998
265.6406 | 125.3494 | -61.9629 | 63.1577 | -0.11726 | 0.011188 | 0.018745 | 0.0012903 | 0.066753 | -0.0022859 | 0.067744 | -61.9995 | 63.1302 | -62.2101 | -62.1689 | 62.8922 | 0.11444 | 0.059509 | 0.19226 | 63.1302 | -62.2238 | -0.24719 | -0.027466 | -0.036621 | -0.20599 | -0.2655 | -0.26093 | -0.027466 | 0.21057 | 62.0224 | 62.1552 | 124.855 | 125.0931 | -0.036621 | 125.0931 | 62.0773 | -0.26093 | 125.0931 | -0.036621 | 62.0773 | 124.855 | 125.0931 | -125.3677 | -125.3815
266.6406 | 125.2762 | -61.9858 | 63.1714 | -0.17067 | 0.011188 | 0.015541 | 0.0021447 | 0.069957 | -0.00036306 | 0.070948 | -62.0087 | 63.1393 | -62.146 | -62.1323 | 62.8464 | 0.082397 | 0.054932 | 0.17395 | 63.1348 | -62.2284 | -0.16022 | -0.032044 | -0.022888 | -0.14648 | -0.32501 | -0.24262 | -0.036621 | 0.13733 | 62.0407 | 62.1597 | 124.8322 | 125.1251 | -0.022888 | 125.1205 | 62.0682 | -0.24262 | 125.1251 | -0.022888 | 62.0682 | 124.8322 | 125.1205 | -125.3174 | -125.3998
267.6406 | 125.2991 | -61.9858 | 63.1393 | 0.16502 | 0.012683 | 0.015541 | 0.0025719 | 0.067608 | -0.00014946 | 0.069667 | -62.0865 | 63.1073 | -62.2147 | -62.233 | 62.7686 | -0.032043 | 0.004578 | 0.013733 | 63.121 | -62.2421 | -0.22888 | -0.032043 | -0.10071 | -0.24719 | -0.37079 | -0.25635 | -0.01831 | 0.12817 | 61.9904 | 61.9995 | 124.7543 | 125.0931 | -0.10071 | 125.1068 | 61.9537 | -0.25635 | 125.0931 | -0.10071 | 61.9537 | 124.7543 | 125.1068 | -125.354 | -125.3815
268.6406 | 125.3311 | -61.9995 | 63.1393 | -0.24696 | 0.01076 | 0.013191 | 0.0038537 | 0.067821 | 0.0024139 | 0.071162 | -62.0224 | 63.1393 | -62.1506 | -62.1552 | 62.8372 | 0.082397 | 0.086975 | 0.17395 | 63.121 | -62.2375 | -0.15106 | 0 | -0.022888 | -0.15564 | -0.30212 | -0.23804 | -0.01831 | 0.12817 | 62.0865 | 62.1735 | 124.8367 | 125.1389 | -0.022888 | 125.1205 | 62.0819 | -0.23804 | 125.1389 | -0.022888 | 62.0819 | 124.8367 | 125.1205 | -125.2899 | -125.3769
269.6406 | 125.3494 | -61.9675 | 63.176 | -0.18593 | 0.0086239 | 0.014473 | 0.0034265 | 0.066539 | -0.0022859 | 0.070735 | -62.0453 | 63.1348 | -62.2009 | -62.1506 | 62.8281 | 0.07782 | 0.13275 | 0.16479 | 63.1393 | -62.2101 | -0.23346 | -0.041198 | -0.07782 | -0.18311 | -0.3479 | -0.24262 | -0.036621 | 0.15564 | 62.1002 | 62.1323 | 124.7955 | 125.1022 | -0.07782 | 125.1068 | 62.0453 | -0.24262 | 125.1022 | -0.07782 | 62.0453 | 124.7955 | 125.1068 | -125.3769 | -125.386
270.6406 | 125.3311 | -61.9812 | 63.176 | -0.22408 | 0.010119 | 0.015328 | 0.0017175 | 0.068889 | -0.0012177 | 0.070948 | -62.0407 | 63.1165 | -62.2009 | -62.1506 | 62.8143 | 0.064087 | 0.11902 | 0.16937 | 63.1348 | -62.2192 | -0.21973 | -0.059509 | -0.059509 | -0.16937 | -0.36163 | -0.23804 | -0.041198 | 0.16022 | 62.1002 | 62.1506 | 124.7955 | 125.0977 | -0.059509 | 125.116 | 62.0453 | -0.23804 | 125.0977 | -0.059509 | 62.0453 | 124.7955 | 125.116 | -125.3769 | -125.3952
271.6406 | 125.3082 | -61.9492 | 63.1622 | -0.25459 | 0.011615 | 0.012123 | 0.0019311 | 0.068462 | -0.0016449 | 0.067958 | -62.059 | 63.1256 | -62.178 | -62.1689 | 62.8143 | 0.064087 | 0.13733 | 0.16022 | 63.1348 | -62.2421 | -0.22888 | -0.036621 | -0.10986 | -0.21973 | -0.3479 | -0.29297 | -0.027465 | 0.11902 | 62.0865 | 62.1094 | 124.7635 | 125.0748 | -0.10986 | 125.0839 | 62.0132 | -0.29297 | 125.0748 | -0.10986 | 62.0132 | 124.7635 | 125.0839 | -125.3403 | -125.4044
272.6406 | 125.2762 | -61.9904 | 63.1348 | 0.15739 | 0.010333 | 0.015114 | 0.0034265 | 0.069957 | -0.00057686 | 0.070308 | -62.0819 | 63.1165 | -62.2284 | -62.2192 | 62.7502 | -0.041199 | -0.004578 | 0.027466 | 63.1027 | -62.2375 | -0.23804 | -0.018311 | -0.091553 | -0.22888 | -0.38452 | -0.24719 | -0.032044 | 0.14648 | 61.9858 | 62.0178 | 124.7406 | 125.1068 | -0.091553 | 125.0931 | 61.9492 | -0.24719 | 125.1068 | -0.091553 | 61.9492 | 124.7406 | 125.0931 | -125.3632 | -125.3723
273.6406 | 125.2991 | -61.9904 | 63.1531 | -0.2317 | 0.012683 | 0.013405 | 0.0021447 | 0.068462 | -0.0010041 | 0.067531 | -62.0544 | 63.121 | -62.1872 | -62.1597 | 62.8235 | 0.064087 | 0.11902 | 0.16022 | 63.1485 | -62.2238 | -0.19684 | -0.032043 | -0.064087 | -0.16937 | -0.32959 | -0.23346 | -0.004577 | 0.13275 | 62.1094 | 62.1506 | 124.8138 | 125.1114 | -0.064087 | 125.1389 | 62.0544 | -0.23346 | 125.1114 | -0.064087 | 62.0544 | 124.8138 | 125.1389 | -125.3403 | -125.3769
274.6406 | 125.3128 | -61.9812 | 63.1348 | -0.24696 | 0.011188 | 0.013619 | 0.0021447 | 0.067608 | -0.0014313 | 0.069026 | -62.0453 | 63.1439 | -62.178 | -62.146 | 62.8235 | 0.059509 | 0.11444 | 0.17395 | 63.1485 | -62.2192 | -0.19684 | 0.009155 | -0.064087 | -0.16479 | -0.31128 | -0.23804 | 0.013733 | 0.13275 | 62.0956 | 62.1552 | 124.8047 | 125.1251 | -0.064087 | 125.1297 | 62.0407 | -0.23804 | 125.1251 | -0.064087 | 62.0407 | 124.8047 | 125.1297 | -125.3128 | -125.354
275.6406 | 125.3037 | -61.972 | 63.1805 | -0.2317 | 0.01076 | 0.017891 | 0.0027855 | 0.068248 | 0.00027774 | 0.070094 | -62.0316 | 63.1393 | -62.1918 | -62.1368 | 62.8418 | 0.073242 | 0.10071 | 0.16937 | 63.1393 | -62.2147 | -0.21973 | -0.041199 | -0.059509 | -0.16479 | -0.33875 | -0.24262 | -0.041199 | 0.16022 | 62.0728 | 62.1414 | 124.8138 | 125.1114 | -0.059509 | 125.1114 | 62.0453 | -0.24262 | 125.1114 | -0.059509 | 62.0453 | 124.8138 | 125.1114 | -125.3723 | -125.3952
276.6406 | 125.2808 | -61.9949 | 63.1577 | -0.063858 | 0.011615 | 0.012123 | 0.0015039 | 0.06953 | -0.0014313 | 0.070094 | -62.0132 | 63.1165 | -62.1643 | -62.1552 | 62.8189 | 0.036621 | 0.036621 | 0.11902 | 63.1165 | -62.233 | -0.16937 | -0.041199 | -0.018311 | -0.16022 | -0.33875 | -0.23804 | -0.041199 | 0.15106 | 62.0316 | 62.114 | 124.8138 | 125.1114 | -0.018311 | 125.1114 | 62.0316 | -0.23804 | 125.1114 | -0.018311 | 62.0316 | 124.8138 | 125.1114 | -125.322 | -125.3906
277.6406 | 125.441 | -61.9446 | 63.0981 | 0.19554 | 0.010547 | 0.0149 | -0.0021277 | 0.067821 | -0.0018585 | 0.069667 | -62.0041 | 63.0432 | -62.1826 | -62.1277 | 62.8647 | 0.059509 | -0.27008 | -0.11902 | 63.0524 | -62.2192 | -0.23804 | -0.054932 | -0.059509 | -0.18311 | -0.23346 | -0.27466 | -0.045777 | 0.17853 | 61.6745 | 61.8256 | 124.8093 | 124.9878 | -0.059509 | 124.9969 | 62.0041 | -0.27466 | 124.9878 | -0.059509 | 62.0041 | 124.8093 | 124.9969 | -125.2808 | -125.3174
278.6406 | 125.3311 | -61.9858 | 63.1393 | -0.10201 | 0.013965 | 0.016609 | 0.0040673 | 0.067608 | -0.0010041 | 0.070308 | -61.9949 | 63.1302 | -62.1735 | -62.1368 | 62.8281 | 0.068665 | 0.013733 | 0.15106 | 63.1348 | -62.2467 | -0.18768 | -0.009155 | -0.009155 | -0.15106 | -0.31128 | -0.26093 | -0.004577 | 0.17853 | 61.9995 | 62.1368 | 124.8138 | 125.116 | -0.009155 | 125.1205 | 62.0544 | -0.26093 | 125.116 | -0.009155 | 62.0544 | 124.8138 | 125.1205 | -125.3128 | -125.386
279.6406 | 125.3265 | -61.9492 | 63.1256 | -0.033341 | 0.010119 | 0.013832 | 0.0021447 | 0.068248 | -0.00079046 | 0.069239 | -62.0041 | 63.1119 | -62.1872 | -62.1414 | 62.8189 | 0.036621 | 0.018311 | 0.11902 | 63.1348 | -62.2284 | -0.23804 | -0.013733 | -0.054931 | -0.19226 | -0.3067 | -0.27924 | 0.009156 | 0.18311 | 61.9675 | 62.0682 | 124.7681 | 125.061 | -0.054931 | 125.0839 | 61.9858 | -0.27924 | 125.061 | -0.054931 | 61.9858 | 124.7681 | 125.0839 | -125.3128 | -125.354
280.6406 | 125.2716 | -61.9904 | 63.1531 | 0.020065 | 0.014178 | 0.013191 | 0.0025719 | 0.069103 | 0.0011321 | 0.070308 | -62.0361 | 63.1348 | -62.1872 | -62.1872 | 62.7731 | -0.022888 | 0.032043 | 0.036621 | 63.1165 | -62.2467 | -0.19684 | -0.01831 | -0.045777 | -0.19684 | -0.37994 | -0.25635 | -0.036621 | 0.15106 | 62.0224 | 62.027 | 124.7635 | 125.1251 | -0.045777 | 125.1068 | 61.9675 | -0.25635 | 125.1251 | -0.045777 | 61.9675 | 124.7635 | 125.1068 | -125.3403 | -125.3998
281.6406 | 125.2945 | -61.972 | 63.1485 | -0.056229 | 0.01076 | 0.01725 | 0.0021447 | 0.071453 | -0.0027131 | 0.069667 | -62.0316 | 63.1256 | -62.1872 | -62.1735 | 62.8143 | 0.032043 | 0.027466 | 0.11902 | 63.1348 | -62.2467 | -0.21515 | -0.022889 | -0.059509 | -0.20142 | -0.33417 | -0.27466 | -0.013733 | 0.15564 | 61.9995 | 62.0911 | 124.7864 | 125.0977 | -0.059509 | 125.1068 | 62.0041 | -0.27466 | 125.0977 | -0.059509 | 62.0041 | 124.7864 | 125.1068 | -125.3357 | -125.3952
282.6406 | 125.4227 | -61.94 | 63.089 | 0.096359 | 0.0094785 | 0.014046 | -0.0017005 | 0.066753 | 0.0015595 | 0.06988 | -62.0087 | 63.0066 | -62.2101 | -62.0773 | 62.6312 | -0.11444 | 0.027466 | 0.22888 | 63.0569 | -62.1964 | -0.27008 | -0.082397 | -0.068665 | -0.13733 | -0.45776 | -0.25635 | -0.032043 | 0.20142 | 61.9675 | 62.1689 | 124.5712 | 124.9466 | -0.068665 | 124.9969 | 61.8256 | -0.25635 | 124.9466 | -0.068665 | 61.8256 | 124.5712 | 124.9969 | -125.2991 | -125.2853
283.6406 | 125.2853 | -61.972 | 63.1485 | 0.065841 | 0.012469 | 0.018105 | 0.0021447 | 0.066753 | -0.0020721 | 0.071589 | -62.0728 | 63.121 | -62.2009 | -62.2375 | 62.59 | -0.4303 | 0.18768 | 0.32959 | 63.0798 | -62.2604 | -0.22888 | -0.027466 | -0.10071 | -0.2655 | -0.55847 | -0.28839 | -0.068665 | 0.12817 | 62.1597 | 62.3016 | 124.5621 | 125.0931 | -0.10071 | 125.0519 | 61.5417 | -0.28839 | 125.0931 | -0.10071 | 61.5417 | 124.5621 | 125.0519 | -125.3494 | -125.4089
284.6406 | 125.2899 | -61.9629 | 63.1119 | 0.15739 | 0.011401 | 0.017891 | 0.0017175 | 0.068676 | -0.00014946 | 0.070735 | -62.0636 | 63.089 | -62.1964 | -62.2147 | 62.7686 | -0.036621 | -0.045776 | 0.013733 | 63.0936 | -62.2513 | -0.23346 | -0.022888 | -0.10071 | -0.25177 | -0.34332 | -0.28839 | -0.01831 | 0.13275 | 61.9171 | 61.9766 | 124.7314 | 125.0519 | -0.10071 | 125.0565 | 61.9263 | -0.28839 | 125.0519 | -0.10071 | 61.9263 | 124.7314 | 125.0565 | -125.3082 | -125.3632
285.6406 | 125.2808 | -61.9766 | 63.121 | 0.065841 | 0.01311 | 0.016182 | 0.0025719 | 0.069957 | -0.00057686 | 0.070308 | -61.9812 | 63.1256 | -62.1872 | -62.2192 | 62.764 | -0.050354 | 0.004578 | 0.009155 | 63.1119 | -62.2559 | -0.21057 | 0.004577 | -0.004577 | -0.24261 | -0.35706 | -0.27923 | -0.009156 | 0.20599 | 61.9812 | 61.9858 | 124.7406 | 125.1022 | -0.004577 | 125.0885 | 61.9263 | -0.27923 | 125.1022 | -0.004577 | 61.9263 | 124.7406 | 125.0885 | -125.3082 | -125.3769
286.6406 | 125.2853 | -61.9904 | 63.1256 | 0.0048064 | 0.01076 | 0.012978 | 0.0017175 | 0.070171 | 6.414e-05 | 0.070521 | -62.1002 | 63.1073 | -62.2101 | -62.2238 | 62.7548 | -0.045776 | -0.009155 | 0.022888 | 63.1256 | -62.265 | -0.21973 | -0.01831 | -0.10986 | -0.23346 | -0.37079 | -0.27466 | 0 | 0.10986 | 61.9812 | 62.0132 | 124.7452 | 125.0977 | -0.10986 | 125.116 | 61.9446 | -0.27466 | 125.0977 | -0.10986 | 61.9446 | 124.7452 | 125.116 | -125.3357 | -125.3906
287.6562 | 125.3082 | -61.9583 | 63.1439 | -0.27748 | 0.011401 | 0.014473 | 0.0010767 | 0.066539 | -0.00079046 | 0.067531 | -62.0453 | 63.1393 | -62.2009 | -62.1368 | 62.8235 | 0.068665 | 0.09613 | 0.16022 | 63.1439 | -62.2238 | -0.24262 | -0.004578 | -0.086975 | -0.17853 | -0.32043 | -0.2655 | 0 | 0.15564 | 62.0544 | 62.1185 | 124.7818 | 125.0977 | -0.086975 | 125.1022 | 62.027 | -0.2655 | 125.0977 | -0.086975 | 62.027 | 124.7818 | 125.1022 | -125.3448 | -125.3677
288.6406 | 125.2579 | -61.9949 | 63.1073 | 0.19554 | 0.010119 | 0.012978 | 0.0021447 | 0.068676 | -0.0016449 | 0.072017 | -62.0911 | 63.0844 | -62.2147 | -62.2101 | 62.7731 | -0.041199 | -0.032043 | 0.050354 | 63.0981 | -62.2467 | -0.21973 | -0.022888 | -0.09613 | -0.21515 | -0.33417 | -0.25177 | -0.009155 | 0.1236 | 61.9629 | 62.0453 | 124.7681 | 125.0793 | -0.09613 | 125.0931 | 61.9537 | -0.25177 | 125.0793 | -0.09613 | 61.9537 | 124.7681 | 125.0931 | -125.322 | -125.354
289.6406 | 125.3037 | -61.9629 | 63.1119 | 0.17265 | 0.01076 | 0.014687 | 0.0010767 | 0.068248 | -0.00036306 | 0.067958 | -62.0865 | 63.0936 | -62.2147 | -62.2009 | 62.7777 | -0.036621 | -0.054932 | 0.041199 | 63.1119 | -62.2375 | -0.25177 | -0.01831 | -0.1236 | -0.23804 | -0.33417 | -0.27466 | 0 | 0.12817 | 61.908 | 62.0041 | 124.7406 | 125.0565 | -0.1236 | 125.0748 | 61.9263 | -0.27466 | 125.0565 | -0.1236 | 61.9263 | 124.7406 | 125.0748 | -125.3265 | -125.3494
290.6406 | 125.473 | -61.9583 | 63.0798 | 0.14214 | 0.0086239 | 0.013619 | -0.0010597 | 0.068462 | -0.00014946 | 0.06988 | -62.0087 | 63.0524 | -62.1964 | -62.1323 | 62.8693 | 0.054932 | -0.1831 | 0.10071 | 63.0432 | -62.2375 | -0.23804 | -0.027466 | -0.050354 | -0.17395 | -0.21057 | -0.27924 | -0.036621 | 0.18768 | 61.7752 | 62.059 | 124.8276 | 125.0107 | -0.050354 | 125.0015 | 62.0132 | -0.27924 | 125.0107 | -0.050354 | 62.0132 | 124.8276 | 125.0015 | -125.2762 | -125.3174
291.6406 | 125.3403 | -61.9583 | 63.0936 | 0.18028 | 0.0086239 | 0.011269 | 0.00043575 | 0.06718 | 0.0019867 | 0.068599 | -61.9949 | 63.0341 | -62.1826 | -62.0956 | 63.0295 | 0.21973 | -0.21973 | 0.17853 | 63.0707 | -62.1918 | -0.2243 | -0.059509 | -0.036621 | -0.13733 | -0.064087 | -0.23346 | -0.022888 | 0.18768 | 61.7386 | 62.1368 | 124.9878 | 124.9924 | -0.036621 | 125.029 | 62.178 | -0.23346 | 124.9924 | -0.036621 | 62.178 | 124.9878 | 125.029 | -125.2762 | -125.2853
292.6562 | 125.2396 | -62.0041 | 63.0981 | -3.5429 | 0.012042 | 0.015114 | 0.0044945 | 0.066539 | -0.00079046 | 0.068171 | -62.1277 | 63.1027 | -62.2055 | -62.2192 | 62.7411 | -0.041199 | 0.004578 | 0.009155 | 63.0936 | -62.2833 | -0.20142 | 0.004577 | -0.1236 | -0.21515 | -0.35706 | -0.27924 | -0.004578 | 0.077819 | 62.0087 | 62.0132 | 124.7452 | 125.1068 | -0.1236 | 125.0977 | 61.9629 | -0.27924 | 125.1068 | -0.1236 | 61.9629 | 124.7452 | 125.0977 | -125.3037 | -125.3815
293.6406 | 125.3677 | -61.9217 | 63.0936 | 0.13451 | 0.010119 | 0.012337 | -0.0029823 | 0.066112 | 0.00049134 | 0.070094 | -62.0087 | 62.9929 | -62.1964 | -62.1185 | 62.8647 | 0.054932 | -0.15106 | 0.14648 | 63.0569 | -62.178 | -0.27466 | -0.10071 | -0.086975 | -0.19684 | -0.22888 | -0.25635 | -0.036621 | 0.18768 | 61.7706 | 62.0682 | 124.7864 | 124.9146 | -0.086975 | 124.9786 | 61.9766 | -0.25635 | 124.9146 | -0.086975 | 61.9766 | 124.7864 | 124.9786 | -125.2899 | -125.2716
294.6406 | 125.3677 | -61.9354 | 63.0844 | 0.08873 | 0.0084103 | 0.011269 | -0.0029823 | 0.063121 | 0.0024139 | 0.069667 | -62.0224 | 62.9974 | -62.2009 | -62.1185 | 62.8372 | 0.041199 | -0.15106 | 0.12817 | 63.0615 | -62.2375 | -0.2655 | -0.086975 | -0.086975 | -0.1831 | -0.24719 | -0.30212 | -0.022889 | 0.17853 | 61.7844 | 62.0636 | 124.7726 | 124.9329 | -0.086975 | 124.9969 | 61.9766 | -0.30212 | 124.9329 | -0.086975 | 61.9766 | 124.7726 | 124.9969 | -125.2853 | -125.322
295.6406 | 125.3998 | -61.9308 | 63.089 | 0.17265 | 0.0088375 | 0.0093459 | 0.0012903 | 0.064617 | 6.414e-05 | 0.068812 | -62.0178 | 62.9654 | -62.1643 | -62.1048 | 62.8464 | 0.064087 | -0.19226 | 0.15106 | 63.0341 | -62.2055 | -0.23346 | -0.1236 | -0.086975 | -0.17395 | -0.24261 | -0.27466 | -0.054931 | 0.14648 | 61.7386 | 62.0819 | 124.7772 | 124.8962 | -0.086975 | 124.9649 | 61.9949 | -0.27466 | 124.8962 | -0.086975 | 61.9949 | 124.7772 | 124.9649 | -125.2533 | -125.2945
296.6406 | 125.386 | -61.9537 | 63.0753 | 0.11925 | 0.010333 | 0.015541 | 8.546e-06 | 0.065685 | 0.00027774 | 0.068812 | -62.0041 | 62.9929 | -62.1689 | -62.1002 | 62.8372 | 0.050354 | -0.19684 | 0.15106 | 63.0386 | -62.2101 | -0.21515 | -0.082397 | -0.050354 | -0.14648 | -0.23804 | -0.25635 | -0.036621 | 0.16479 | 61.7569 | 62.1048 | 124.791 | 124.9466 | -0.050354 | 124.9924 | 62.0041 | -0.25635 | 124.9466 | -0.050354 | 62.0041 | 124.791 | 124.9924 | -125.2441 | -125.2853
297.6562 | 125.2991 | -61.9675 | 63.0936 | 0.24132 | 0.012683 | 0.012123 | 0.0051355 | 0.06483 | -0.0010041 | 0.069026 | -62.0819 | 63.0798 | -62.2055 | -62.2055 | 62.7594 | -0.050354 | -0.022888 | 0.022888 | 63.1027 | -62.2375 | -0.23804 | -0.013733 | -0.11444 | -0.23804 | -0.33417 | -0.27008 | 0.009155 | 0.1236 | 61.9446 | 61.9904 | 124.7269 | 125.0473 | -0.11444 | 125.0702 | 61.9171 | -0.27008 | 125.0473 | -0.11444 | 61.9171 | 124.7269 | 125.0702 | -125.2991 | -125.3311
298.6406 | 125.3586 | -61.9354 | 63.0844 | 0.096359 | 0.0084103 | 0.013619 | -0.0012733 | 0.066967 | -0.00036306 | 0.068812 | -62.0407 | 63.002 | -62.1872 | -62.1414 | 62.8235 | 0.027466 | -0.14191 | 0.1236 | 63.0432 | -62.1826 | -0.25177 | -0.082398 | -0.10528 | -0.20599 | -0.26093 | -0.24719 | -0.041199 | 0.14649 | 61.7935 | 62.059 | 124.7589 | 124.9374 | -0.10528 | 124.9786 | 61.9629 | -0.24719 | 124.9374 | -0.10528 | 61.9629 | 124.7589 | 124.9786 | -125.2716 | -125.267
299.6406 | 125.322 | -61.94 | 63.1119 | 0.10399 | 0.010119 | 0.01191 | -0.0012733 | 0.065471 | -0.00079046 | 0.067531 | -62.0728 | 62.97 | -62.1735 | -62.1414 | 62.8143 | 0.022888 | -0.11902 | 0.12817 | 63.0432 | -62.2147 | -0.23346 | -0.14191 | -0.13275 | -0.20142 | -0.29755 | -0.27466 | -0.068664 | 0.10071 | 61.821 | 62.0682 | 124.7543 | 124.91 | -0.13275 | 124.9832 | 61.9629 | -0.27466 | 124.91 | -0.13275 | 61.9629 | 124.7543 | 124.9832 | -125.2853 | -125.3265
300.6406 | 125.3357 | -61.94 | 63.1165 | 0.5999 | 0.0077695 | 0.01255 | -0.0025549 | 0.064403 | 0.00091854 | 0.069667 | -62.0499 | 62.9837 | -62.178 | -62.1506 | 62.8235 | 0.036621 | -0.07782 | 0.14191 | 63.0707 | -62.1918 | -0.23804 | -0.13275 | -0.10986 | -0.21057 | -0.29297 | -0.25177 | -0.045776 | 0.12817 | 61.8622 | 62.0819 | 124.7635 | 124.9237 | -0.10986 | 125.0107 | 61.9766 | -0.25177 | 124.9237 | -0.10986 | 61.9766 | 124.7635 | 125.0107 | -125.2945 | -125.3082
301.6406 | 125.3586 | -61.9217 | 63.1073 | -0.048599 | 0.0096921 | 0.011482 | -0.0021277 | 0.06184 | 0.00049134 | 0.069667 | -62.0865 | 62.9974 | -62.1872 | -62.1323 | 62.8326 | 0.045776 | -0.036621 | 0.14648 | 63.0478 | -62.1826 | -0.2655 | -0.10986 | -0.16479 | -0.21057 | -0.27466 | -0.26093 | -0.059509 | 0.10071 | 61.8851 | 62.0682 | 124.7543 | 124.9191 | -0.16479 | 124.9695 | 61.9675 | -0.26093 | 124.9191 | -0.16479 | 61.9675 | 124.7543 | 124.9695 | -125.2945 | -125.2899
302.6562 | 125.2853 | -61.9583 | 63.1485 | -0.0028231 | 0.012256 | 0.01255 | 0.0089807 | 0.065685 | 0.00027774 | 0.069453 | -62.0407 | 63.121 | -62.1872 | -62.1689 | 62.7548 | -0.054932 | -0.004578 | 0.027466 | 63.0707 | -62.2696 | -0.22888 | -0.027466 | -0.082397 | -0.21057 | -0.39368 | -0.31128 | -0.07782 | 0.14649 | 61.9537 | 61.9858 | 124.7131 | 125.0793 | -0.082397 | 125.029 | 61.9034 | -0.31128 | 125.0793 | -0.082397 | 61.9034 | 124.7131 | 125.029 | -125.3357 | -125.4181
303.6406 | 125.3494 | -61.9125 | 63.0981 | 0.0811 | 0.0075559 | 0.01255 | -0.0021277 | 0.066326 | -0.00014946 | 0.06988 | -62.0544 | 62.9837 | -62.1689 | -62.146 | 62.8143 | 0.009155 | -0.10529 | 0.12817 | 63.0661 | -62.1735 | -0.25635 | -0.11444 | -0.14191 | -0.23346 | -0.28381 | -0.26093 | -0.032044 | 0.11444 | 61.8073 | 62.0407 | 124.7269 | 124.8962 | -0.14191 | 124.9786 | 61.9217 | -0.26093 | 124.8962 | -0.14191 | 61.9217 | 124.7269 | 124.9786 | -125.267 | -125.2716
304.6406 | 125.3632 | -61.94 | 63.1119 | 0.042953 | 0.010333 | 0.0099869 | -0.0012733 | 0.062908 | -0.0024995 | 0.069239 | -62.0773 | 62.9654 | -62.1964 | -62.1323 | 62.8281 | 0.032043 | -0.054932 | 0.15106 | 63.0661 | -62.178 | -0.25635 | -0.14648 | -0.13733 | -0.19226 | -0.28381 | -0.23804 | -0.045776 | 0.11902 | 61.8851 | 62.0911 | 124.7681 | 124.9054 | -0.13733 | 125.0061 | 61.972 | -0.23804 | 124.9054 | -0.13733 | 61.972 | 124.7681 | 125.0061 | -125.3082 | -125.2899
305.6406 | 125.3632 | -61.9308 | 63.1302 | 0.050583 | 0.0088375 | 0.0059281 | -0.0012733 | 0.062053 | -0.0010041 | 0.070735 | -62.0544 | 63.002 | -62.1689 | -62.1185 | 62.8189 | 0.036621 | -0.068665 | 0.16479 | 63.0432 | -62.2101 | -0.23804 | -0.12817 | -0.1236 | -0.18768 | -0.31128 | -0.27924 | -0.086975 | 0.11444 | 61.8622 | 62.0956 | 124.7498 | 124.9329 | -0.1236 | 124.9741 | 61.9675 | -0.27924 | 124.9329 | -0.1236 | 61.9675 | 124.7498 | 124.9741 | -125.2991 | -125.3403
306.6406 | 125.3677 | -61.94 | 63.1439 | -0.19356 | 0.0096921 | 0.014259 | -0.0027687 | 0.062694 | -0.0022859 | 0.067958 | -62.0636 | 63.002 | -62.178 | -62.1414 | 62.851 | 0.041199 | -0.059509 | 0.14191 | 63.0524 | -62.2147 | -0.23804 | -0.14191 | -0.1236 | -0.20142 | -0.29297 | -0.27466 | -0.091553 | 0.11444 | 61.8805 | 62.0819 | 124.791 | 124.942 | -0.1236 | 124.9924 | 61.9812 | -0.27466 | 124.942 | -0.1236 | 61.9812 | 124.791 | 124.9924 | -125.322 | -125.3586
307.6406 | 125.3265 | -61.9583 | 63.1485 | -0.22408 | 0.0099057 | 0.0082779 | 0.0017175 | 0.064617 | -0.0014313 | 0.068599 | -61.9904 | 63.0249 | -62.1506 | -62.0544 | 62.8876 | 0.12817 | 0.027466 | 0.23346 | 63.0615 | -62.178 | -0.19226 | -0.1236 | -0.032043 | -0.09613 | -0.26093 | -0.21973 | -0.086976 | 0.16022 | 61.9858 | 62.1918 | 124.8459 | 124.9832 | -0.032043 | 125.0198 | 62.0865 | -0.21973 | 124.9832 | -0.032043 | 62.0865 | 124.8459 | 125.0198 | -125.2991 | -125.3265
308.6406 | 125.3677 | -61.9354 | 63.121 | -0.010452 | 0.0071285 | 0.0099869 | -0.0021277 | 0.063976 | -0.00057686 | 0.069453 | -62.0361 | 62.9837 | -62.178 | -62.1002 | 62.8464 | 0.073242 | -0.082397 | 0.19684 | 63.089 | -62.1552 | -0.24262 | -0.13733 | -0.10071 | -0.16479 | -0.27466 | -0.21973 | -0.032044 | 0.14191 | 61.853 | 62.1323 | 124.7818 | 124.9191 | -0.10071 | 125.0244 | 62.0087 | -0.21973 | 124.9191 | -0.10071 | 62.0087 | 124.7818 | 125.0244 | -125.2991 | -125.2762
309.6406 | 125.3586 | -61.9263 | 63.1348 | -0.018082 | 0.0092649 | 0.010414 | -0.00063225 | 0.061412 | -0.0012177 | 0.066249 | -61.9034 | 63.0066 | -62.1552 | -62.1368 | 62.8052 | 0.027466 | -0.068665 | 0.13733 | 63.0478 | -62.1643 | -0.22888 | -0.12817 | 0.022889 | -0.21057 | -0.32959 | -0.23804 | -0.086975 | 0.25177 | 61.8576 | 62.0636 | 124.7314 | 124.9329 | 0.022889 | 124.9741 | 61.9537 | -0.23804 | 124.9329 | 0.022889 | 61.9537 | 124.7314 | 124.9741 | -125.2899 | -125.2991
310.6406 | 125.3403 | -61.9354 | 63.1256 | 0.12688 | 0.0094785 | 0.0097733 | 0.0017175 | 0.062267 | 0.00070494 | 0.06988 | -62.0453 | 62.9883 | -62.1552 | -62.1552 | 62.8372 | 0.045776 | -0.086975 | 0.1236 | 63.0295 | -62.1735 | -0.21973 | -0.13733 | -0.10986 | -0.21973 | -0.28839 | -0.23804 | -0.09613 | 0.10986 | 61.8484 | 62.059 | 124.7726 | 124.9237 | -0.10986 | 124.9649 | 61.9812 | -0.23804 | 124.9237 | -0.10986 | 61.9812 | 124.7726 | 124.9649 | -125.2808 | -125.2991
311.6406 | 125.3723 | -61.9308 | 63.1302 | -0.010452 | 0.0086239 | 0.01191 | -0.00084605 | 0.062481 | 0.0017731 | 0.069667 | -62.0453 | 62.97 | -62.1506 | -62.1048 | 62.8601 | 0.054932 | -0.082397 | 0.18768 | 63.0295 | -62.178 | -0.21973 | -0.16022 | -0.11444 | -0.17395 | -0.27008 | -0.24719 | -0.10071 | 0.10529 | 61.8484 | 62.1185 | 124.791 | 124.9008 | -0.11444 | 124.9603 | 61.9858 | -0.24719 | 124.9008 | -0.11444 | 61.9858 | 124.791 | 124.9603 | -125.2808 | -125.3082
312.6406 | 125.2716 | -61.972 | 63.1531 | 0.050583 | 0.012042 | 0.013832 | 0.0034265 | 0.063335 | -0.0016449 | 0.067531 | -62.0682 | 63.0798 | -62.1597 | -62.1368 | 62.8143 | 0.054932 | 0.1236 | 0.14191 | 63.0936 | -62.1918 | -0.18768 | -0.073242 | -0.09613 | -0.16479 | -0.33874 | -0.21973 | -0.059509 | 0.091553 | 62.0956 | 62.114 | 124.7864 | 125.0519 | -0.09613 | 125.0656 | 62.027 | -0.21973 | 125.0519 | -0.09613 | 62.027 | 124.7864 | 125.0656 | -125.3128 | -125.3448
313.6406 | 125.354 | -61.9171 | 63.1165 | 0.0048064 | 0.0079831 | 0.01191 | -0.0019141 | 0.063335 | 0.0011321 | 0.069026 | -62.0682 | 62.9883 | -62.1872 | -62.1094 | 62.8326 | 0.059509 | -0.07782 | 0.16479 | 63.0569 | -62.1597 | -0.27008 | -0.12817 | -0.15106 | -0.19226 | -0.28381 | -0.24262 | -0.059509 | 0.11902 | 61.8393 | 62.0819 | 124.7498 | 124.9054 | -0.15106 | 124.9741 | 61.9766 | -0.24262 | 124.9054 | -0.15106 | 61.9766 | 124.7498 | 124.9741 | -125.3037 | -125.2762
314.6406 | 125.3357 | -61.9354 | 63.1348 | 0.020065 | 0.0084103 | 0.014046 | -0.00041865 | 0.062053 | -0.0010041 | 0.070308 | -62.059 | 62.9837 | -62.1918 | -62.1277 | 62.8555 | 0.041199 | -0.054932 | 0.15106 | 63.0295 | -62.1552 | -0.25635 | -0.15106 | -0.1236 | -0.19226 | -0.27924 | -0.21973 | -0.10529 | 0.13275 | 61.8805 | 62.0865 | 124.791 | 124.9191 | -0.1236 | 124.9649 | 61.9766 | -0.21973 | 124.9191 | -0.1236 | 61.9766 | 124.791 | 124.9649 | -125.3265 | -125.2899
315.6406 | 125.386 | -61.9354 | 63.1119 | -0.018082 | 0.0058469 | 0.0099869 | -0.0031959 | 0.060772 | 0.00027774 | 0.070094 | -62.0361 | 62.9883 | -62.1552 | -62.0911 | 62.8967 | 0.10529 | -0.086975 | 0.21515 | 63.0386 | -62.1872 | -0.21973 | -0.1236 | -0.10071 | -0.15564 | -0.21515 | -0.25177 | -0.073242 | 0.11902 | 61.8484 | 62.1506 | 124.8322 | 124.9237 | -0.10071 | 124.9741 | 62.0407 | -0.25177 | 124.9237 | -0.10071 | 62.0407 | 124.8322 | 124.9741 | -125.267 | -125.2991
316.6406 | 125.3677 | -61.9492 | 63.1256 | -0.14015 | 0.01076 | 0.0095595 | -0.0014869 | 0.061412 | -0.0010041 | 0.067744 | -62.0911 | 62.9883 | -62.1597 | -62.1185 | 62.8281 | 0.050354 | -0.068665 | 0.15106 | 63.0295 | -62.1735 | -0.21057 | -0.13733 | -0.14191 | -0.16937 | -0.29755 | -0.2243 | -0.09613 | 0.068665 | 61.8805 | 62.1002 | 124.7772 | 124.9374 | -0.14191 | 124.9786 | 61.9995 | -0.2243 | 124.9374 | -0.14191 | 61.9995 | 124.7772 | 124.9786 | -125.2853 | -125.2991
317.6406 | 125.3448 | -61.9354 | 63.1302 | -0.22408 | 0.0084103 | 0.015755 | 0.0019311 | 0.062481 | -0.00057686 | 0.068171 | -61.9949 | 63.0157 | -62.178 | -62.059 | 62.883 | 0.1236 | 0.018311 | 0.2655 | 63.0524 | -62.178 | -0.24262 | -0.11444 | -0.059509 | -0.1236 | -0.24719 | -0.24262 | -0.07782 | 0.18311 | 61.9537 | 62.2009 | 124.8184 | 124.9512 | -0.059509 | 124.9878 | 62.059 | -0.24262 | 124.9512 | -0.059509 | 62.059 | 124.8184 | 124.9878 | -125.3082 | -125.3082
318.6406 | 125.3632 | -61.9354 | 63.1073 | -0.025711 | 0.0081967 | 0.013405 | -0.0010597 | 0.06483 | -0.0012177 | 0.067103 | -62.0224 | 62.9791 | -62.178 | -62.1002 | 62.851 | 0.082397 | -0.073242 | 0.1831 | 63.0432 | -62.1552 | -0.24262 | -0.12817 | -0.086975 | -0.16479 | -0.25635 | -0.21973 | -0.064087 | 0.15564 | 61.8622 | 62.1185 | 124.7864 | 124.9146 | -0.086975 | 124.9786 | 62.0178 | -0.21973 | 124.9146 | -0.086975 | 62.0178 | 124.7864 | 124.9786 | -125.2853 | -125.2625
319.6406 | 125.3448 | -61.94 | 63.1027 | -0.063858 | 0.0071285 | 0.0099869 | -0.0010597 | 0.062481 | 0.0015595 | 0.069453 | -62.0361 | 63.0066 | -62.1414 | -62.1048 | 62.8601 | 0.082397 | -0.073242 | 0.18768 | 63.0112 | -62.178 | -0.20142 | -0.09613 | -0.096131 | -0.16479 | -0.24262 | -0.23804 | -0.091553 | 0.10529 | 61.8668 | 62.1277 | 124.8001 | 124.9466 | -0.096131 | 124.9512 | 62.0224 | -0.23804 | 124.9466 | -0.096131 | 62.0224 | 124.8001 | 124.9512 | -125.2441 | -125.2808
320.6406 | 125.3494 | -61.9629 | 63.1165 | -0.04097 | 0.0092649 | 0.012764 | -0.0023413 | 0.062694 | 6.414e-05 | 0.06988 | -62.0499 | 63.0066 | -62.1689 | -62.1048 | 62.8555 | 0.07782 | -0.068665 | 0.16937 | 63.0295 | -62.1735 | -0.20599 | -0.10986 | -0.086975 | -0.14191 | -0.26093 | -0.21057 | -0.086975 | 0.11902 | 61.8942 | 62.1323 | 124.8184 | 124.9695 | -0.086975 | 124.9924 | 62.0407 | -0.21057 | 124.9695 | -0.086975 | 62.0407 | 124.8184 | 124.9924 | -125.2853 | -125.2899
321.6406 | 125.3906 | -61.8942 | 63.0981 | -0.063858 | 0.0086239 | 0.0080643 | -0.0014869 | 0.06184 | -0.0010041 | 0.070521 | -62.0132 | 63.0066 | -62.1414 | -62.0544 | 62.9013 | 0.1236 | -0.09613 | 0.25177 | 63.0249 | -62.1414 | -0.24719 | -0.091553 | -0.11902 | -0.16022 | -0.19684 | -0.24719 | -0.073243 | 0.12817 | 61.7981 | 62.146 | 124.7955 | 124.9008 | -0.11902 | 124.9191 | 62.0178 | -0.24719 | 124.9008 | -0.11902 | 62.0178 | 124.7955 | 124.9191 | -125.2396 | -125.2396
322.6406 | 125.3128 | -61.9675 | 63.1485 | -0.10963 | 0.0092649 | 0.0084915 | 0.0076989 | 0.062053 | -0.00057686 | 0.067958 | -61.9492 | 63.0661 | -62.1872 | -62.0636 | 62.8372 | 0.082397 | 0.018311 | 0.16937 | 63.0524 | -62.1872 | -0.21973 | -0.082398 | 0.01831 | -0.096131 | -0.31128 | -0.21973 | -0.096131 | 0.23804 | 61.9858 | 62.1368 | 124.8047 | 125.0336 | 0.01831 | 125.0198 | 62.0499 | -0.21973 | 125.0336 | 0.01831 | 62.0499 | 124.8047 | 125.0198 | -125.3357 | -125.3357
323.6406 | 125.3586 | -61.9308 | 63.1165 | -0.033341 | 0.01076 | 0.0093459 | -0.0036231 | 0.062481 | 0.0013457 | 0.070094 | -62.0682 | 63.002 | -62.1735 | -62.0865 | 62.8555 | 0.073242 | -0.054932 | 0.17853 | 63.0066 | -62.1597 | -0.24262 | -0.11444 | -0.13733 | -0.15564 | -0.26093 | -0.22888 | -0.10986 | 0.10529 | 61.8759 | 62.1094 | 124.7864 | 124.9329 | -0.13733 | 124.9374 | 62.0041 | -0.22888 | 124.9329 | -0.13733 | 62.0041 | 124.7864 | 124.9374 | -125.2899 | -125.2762
324.6406 | 125.4089 | -61.9446 | 63.1302 | -0.056229 | 0.0079831 | 0.011269 | -0.0034095 | 0.062053 | -0.00036306 | 0.070094 | -62.0178 | 63.002 | -62.1597 | -62.0682 | 62.8922 | 0.1236 | -0.068665 | 0.2243 | 63.0157 | -62.146 | -0.21515 | -0.12817 | -0.073242 | -0.1236 | -0.23804 | -0.20142 | -0.11444 | 0.14191 | 61.8759 | 62.1689 | 124.8367 | 124.9466 | -0.073242 | 124.9603 | 62.0682 | -0.20142 | 124.9466 | -0.073242 | 62.0682 | 124.8367 | 124.9603 | -125.2899 | -125.2762
325.6406 | 125.4181 | -61.9217 | 63.1027 | -0.071488 | 0.0075559 | 0.01255 | 8.546e-06 | 0.063549 | 0.00049134 | 0.069667 | -62.0316 | 62.9745 | -62.1597 | -62.0728 | 62.9013 | 0.13733 | -0.07782 | 0.21515 | 63.0157 | -62.1506 | -0.23804 | -0.12817 | -0.10986 | -0.15106 | -0.20142 | -0.22888 | -0.086975 | 0.12817 | 61.8439 | 62.1368 | 124.823 | 124.8962 | -0.10986 | 124.9374 | 62.059 | -0.22888 | 124.8962 | -0.10986 | 62.059 | 124.823 | 124.9374 | -125.2625 | -125.2533
326.6406 | 125.3952 | -61.9263 | 63.1256 | -0.22408 | 0.0088375 | 0.010201 | 0.0025719 | 0.06184 | -0.00014946 | 0.068812 | -61.9766 | 63.0066 | -62.114 | -62.0316 | 62.9013 | 0.15106 | -0.018311 | 0.28381 | 63.0569 | -62.1323 | -0.18768 | -0.11902 | -0.050354 | -0.10528 | -0.2243 | -0.20599 | -0.068664 | 0.13733 | 61.908 | 62.2101 | 124.8276 | 124.9329 | -0.050354 | 124.9832 | 62.0773 | -0.20599 | 124.9329 | -0.050354 | 62.0773 | 124.8276 | 124.9832 | -125.2396 | -125.2579
327.6562 | 125.3128 | -61.9308 | 63.1439 | -0.17067 | 0.0094785 | 0.013405 | 0.0042809 | 0.06419 | -0.00036306 | 0.070308 | -61.9949 | 63.121 | -62.1414 | -62.0819 | 62.8418 | 0.11444 | 0.041199 | 0.17853 | 63.0661 | -62.1826 | -0.21057 | -0.022888 | -0.064087 | -0.15106 | -0.30212 | -0.25177 | -0.07782 | 0.14648 | 61.972 | 62.1094 | 124.7726 | 125.0519 | -0.064087 | 124.9969 | 62.0453 | -0.25177 | 125.0519 | -0.064087 | 62.0453 | 124.7726 | 124.9969 | -125.2853 | -125.3265
328.6406 | 125.3632 | -61.9263 | 63.1119 | -0.063858 | 0.0079831 | 0.01191 | -0.0038367 | 0.064617 | -0.00014946 | 0.070094 | -62.0316 | 62.9883 | -62.1643 | -62.0682 | 62.883 | 0.11444 | -0.07782 | 0.22888 | 63.0295 | -62.1597 | -0.23804 | -0.1236 | -0.10528 | -0.14191 | -0.22888 | -0.23346 | -0.082397 | 0.13275 | 61.8484 | 62.1552 | 124.8093 | 124.9146 | -0.10528 | 124.9557 | 62.0407 | -0.23346 | 124.9146 | -0.10528 | 62.0407 | 124.8093 | 124.9557 | -125.2762 | -125.2716
329.6406 | 125.3677 | -61.9217 | 63.1165 | -0.094376 | 0.0075559 | 0.0095595 | 0.00086295 | 0.063121 | -0.0024995 | 0.070094 | -62.0316 | 63.0157 | -62.1597 | -62.0911 | 62.9013 | 0.1236 | -0.068665 | 0.23804 | 63.0295 | -62.1506 | -0.23804 | -0.10071 | -0.10986 | -0.16937 | -0.21515 | -0.22888 | -0.086975 | 0.12817 | 61.853 | 62.1597 | 124.823 | 124.9374 | -0.10986 | 124.9512 | 62.0453 | -0.22888 | 124.9374 | -0.10986 | 62.0453 | 124.823 | 124.9512 | -125.2762 | -125.267
330.6406 | 125.386 | -61.8988 | 63.1348 | -0.10963 | 0.0086239 | 0.011269 | -0.0010597 | 0.062267 | -0.00036306 | 0.069026 | -62.0407 | 62.9745 | -62.1643 | -62.059 | 62.8738 | 0.11902 | -0.073242 | 0.20599 | 63.0157 | -62.1368 | -0.2655 | -0.16022 | -0.14191 | -0.16022 | -0.26093 | -0.23804 | -0.11902 | 0.1236 | 61.8256 | 62.1048 | 124.7726 | 124.8734 | -0.14191 | 124.9146 | 62.0178 | -0.23804 | 124.8734 | -0.14191 | 62.0178 | 124.7726 | 124.9146 | -125.2991 | -125.2716
331.6406 | 125.4501 | -61.9308 | 63.0936 | -0.10963 | 0.0073423 | 0.013405 | -0.00063225 | 0.060772 | -0.0010041 | 0.067531 | -61.9675 | 62.9745 | -62.1323 | -62.0316 | 62.6175 | 0.29297 | 0.26093 | -0.086975 | 63.0569 | -62.1506 | -0.20142 | -0.11902 | -0.036621 | -0.10071 | -0.47607 | -0.21973 | -0.036621 | 0.1648 | 62.1918 | 61.8439 | 124.5483 | 124.9054 | -0.036621 | 124.9878 | 62.2238 | -0.21973 | 124.9054 | -0.036621 | 62.2238 | 124.5483 | 124.9878 | -125.2258 | -125.2441
332.6406 | 125.267 | -61.9629 | 63.1622 | -0.2317 | 0.010974 | 0.013832 | 0.0049219 | 0.063549 | -0.00057686 | 0.069026 | -62.0682 | 63.0981 | -62.1643 | -62.146 | 62.8006 | 0.054932 | 0.13275 | 0.15106 | 63.0661 | -62.1826 | -0.20142 | -0.064086 | -0.10529 | -0.1831 | -0.36163 | -0.21973 | -0.09613 | 0.096131 | 62.0956 | 62.114 | 124.7635 | 125.061 | -0.10529 | 125.029 | 62.0178 | -0.21973 | 125.061 | -0.10529 | 62.0178 | 124.7635 | 125.029 | -125.3265 | -125.3448
333.6406 | 125.3998 | -61.8896 | 63.1348 | -0.2317 | 0.0075559 | 0.0082779 | -0.0055457 | 0.063549 | 0.00049134 | 0.068812 | -61.9904 | 62.9791 | -62.1597 | -62.0316 | 62.9059 | 0.15564 | -0.082397 | 0.27008 | 63.0157 | -62.1323 | -0.27008 | -0.15564 | -0.10071 | -0.14191 | -0.22888 | -0.24262 | -0.11902 | 0.16937 | 61.8073 | 62.1597 | 124.7955 | 124.8688 | -0.10071 | 124.9054 | 62.0453 | -0.24262 | 124.8688 | -0.10071 | 62.0453 | 124.7955 | 124.9054 | -125.2945 | -125.267
334.6406 | 125.4318 | -61.8942 | 63.1393 | -0.13252 | 0.010547 | 0.0095595 | -0.0027687 | 0.062908 | 0.00049134 | 0.068385 | -61.9949 | 62.9929 | -62.1643 | -62.0316 | 62.915 | 0.12817 | -0.073242 | 0.27466 | 62.9929 | -62.1277 | -0.27008 | -0.14648 | -0.10071 | -0.13733 | -0.2243 | -0.23346 | -0.14648 | 0.16937 | 61.821 | 62.1689 | 124.8093 | 124.8871 | -0.10071 | 124.8871 | 62.0224 | -0.23346 | 124.8871 | -0.10071 | 62.0224 | 124.8093 | 124.8871 | -125.3037 | -125.267
335.6406 | 125.4044 | -61.908 | 63.1256 | -0.1783 | 0.0049923 | 0.0084915 | 0.00043575 | 0.063976 | 0.0011321 | 0.070948 | -61.9995 | 62.9974 | -62.1323 | -62.0499 | 62.915 | 0.13733 | -0.07782 | 0.26093 | 63.0341 | -62.1231 | -0.2243 | -0.12817 | -0.091553 | -0.14191 | -0.21057 | -0.21515 | -0.091552 | 0.13275 | 61.8301 | 62.1689 | 124.823 | 124.9054 | -0.091553 | 124.942 | 62.0453 | -0.21515 | 124.9054 | -0.091553 | 62.0453 | 124.823 | 124.942 | -125.2579 | -125.2487
336.6406 | 125.3769 | -61.9125 | 63.121 | -0.094376 | 0.0060605 | 0.010201 | -0.0019141 | 0.063335 | 0.0011321 | 0.070094 | -62.0178 | 62.9974 | -62.1552 | -62.0453 | 62.8967 | 0.13275 | -0.07782 | 0.24719 | 62.9929 | -62.1597 | -0.24261 | -0.1236 | -0.10529 | -0.13275 | -0.2243 | -0.24719 | -0.12817 | 0.13733 | 61.8347 | 62.1597 | 124.8093 | 124.91 | -0.10529 | 124.9054 | 62.0453 | -0.24719 | 124.91 | -0.10529 | 62.0453 | 124.8093 | 124.9054 | -125.2762 | -125.2808
337.6406 | 125.2853 | -61.9583 | 63.1805 | -0.30037 | 0.010333 | 0.013832 | 0.0029993 | 0.063762 | 0.00049134 | 0.069667 | -62.0865 | 63.0844 | -62.1643 | -62.1094 | 62.7869 | 0.041199 | 0.13733 | 0.14648 | 63.1073 | -62.2055 | -0.20599 | -0.09613 | -0.12817 | -0.15106 | -0.39368 | -0.24719 | -0.073242 | 0.07782 | 62.0956 | 62.1048 | 124.7452 | 125.0427 | -0.12817 | 125.0656 | 61.9995 | -0.24719 | 125.0427 | -0.12817 | 61.9995 | 124.7452 | 125.0656 | -125.3448 | -125.386
338.6406 | 125.3448 | -61.9446 | 63.0981 | -0.1783 | 0.0079831 | 0.01255 | -0.00020505 | 0.06419 | -0.0016449 | 0.069453 | -61.9904 | 62.9745 | -62.1552 | -62.0224 | 63.3362 | 0.49896 | -0.50812 | 0.09613 | 63.0157 | -62.1323 | -0.21057 | -0.1236 | -0.045776 | -0.07782 | 0.23804 | -0.18768 | -0.082398 | 0.16479 | 61.4365 | 62.0407 | 125.2808 | 124.9191 | -0.045776 | 124.9603 | 62.4435 | -0.18768 | 124.9191 | -0.045776 | 62.4435 | 125.2808 | 124.9603 | -125.2533 | -125.2304
339.6406 | 125.6012 | -61.8851 | 63.1805 | -0.17067 | 0.010547 | 0.010414 | -0.00084605 | 0.06419 | -0.0018585 | 0.069026 | -62.0041 | 62.9883 | -62.1368 | -62.0224 | 62.9242 | 0.16479 | -0.082397 | 0.28839 | 63.0386 | -62.114 | -0.25177 | -0.19226 | -0.11902 | -0.13733 | -0.25635 | -0.22888 | -0.14191 | 0.13275 | 61.8027 | 62.1735 | 124.8093 | 124.8734 | -0.11902 | 124.9237 | 62.0499 | -0.22888 | 124.8734 | -0.11902 | 62.0499 | 124.8093 | 124.9237 | -125.3174 | -125.2945
340.6406 | 125.3632 | -61.9034 | 63.0936 | -0.10963 | 0.0090513 | 0.013619 | -0.0021277 | 0.063121 | -0.00036306 | 0.069239 | -61.9949 | 62.9974 | -62.1414 | -62.0499 | 62.9196 | 0.15564 | -0.07782 | 0.27924 | 63.0295 | -62.1506 | -0.23804 | -0.09613 | -0.091553 | -0.14648 | -0.17395 | -0.24719 | -0.064087 | 0.14648 | 61.8256 | 62.1826 | 124.823 | 124.9008 | -0.091553 | 124.9329 | 62.059 | -0.24719 | 124.9008 | -0.091553 | 62.059 | 124.823 | 124.9329 | -125.235 | -125.2441
341.6406 | 125.3906 | -61.908 | 63.1119 | -0.10963 | 0.0075559 | 0.0089187 | -0.0023413 | 0.062694 | -0.0022859 | 0.069453 | -62.0041 | 63.002 | -62.1368 | -62.0407 | 62.9013 | 0.16937 | -0.073242 | 0.26093 | 63.0295 | -62.146 | -0.22888 | -0.10986 | -0.09613 | -0.13275 | -0.21057 | -0.23804 | -0.082397 | 0.13275 | 61.8347 | 62.1689 | 124.8093 | 124.91 | -0.09613 | 124.9374 | 62.0773 | -0.23804 | 124.91 | -0.09613 | 62.0773 | 124.8093 | 124.9374 | -125.2487 | -125.2579
342.6406 | 125.2625 | -61.9629 | 63.1531 | -0.048599 | 0.011188 | 0.015541 | 0.0076989 | 0.065258 | -0.0022859 | 0.068812 | -61.9949 | 63.0936 | -62.1872 | -62.1094 | 62.8006 | 0.027466 | 0.022888 | 0.10071 | 63.0524 | -62.233 | -0.2243 | -0.059509 | -0.032043 | -0.14648 | -0.35248 | -0.27008 | -0.10071 | 0.19226 | 61.9858 | 62.0636 | 124.7635 | 125.0565 | -0.032043 | 125.0153 | 61.9904 | -0.27008 | 125.0565 | -0.032043 | 61.9904 | 124.7635 | 125.0153 | -125.3403 | -125.386
343.6406 | 125.3815 | -61.9034 | 63.1027 | -0.086746 | 0.0054197 | 0.011696 | -0.0029823 | 0.06483 | 0.00049134 | 0.067103 | -62.0132 | 62.9974 | -62.1597 | -62.0499 | 62.8876 | 0.13275 | -0.086975 | 0.23346 | 63.0524 | -62.1323 | -0.25635 | -0.10529 | -0.10986 | -0.14648 | -0.21515 | -0.22888 | -0.050354 | 0.14648 | 61.8164 | 62.1368 | 124.791 | 124.9008 | -0.10986 | 124.9557 | 62.0361 | -0.22888 | 124.9008 | -0.10986 | 62.0361 | 124.791 | 124.9557 | -125.2625 | -125.235
344.6406 | 125.3815 | -61.9263 | 63.1119 | -0.063858 | 0.0092649 | 0.010841 | -0.0036231 | 0.062694 | 0.0015595 | 0.069026 | -62.0316 | 62.9929 | -62.1506 | -62.0865 | 62.8693 | 0.10529 | -0.07782 | 0.21515 | 63.0386 | -62.1506 | -0.2243 | -0.11902 | -0.10528 | -0.16022 | -0.24261 | -0.2243 | -0.073242 | 0.11902 | 61.8484 | 62.1414 | 124.7955 | 124.9191 | -0.10528 | 124.9649 | 62.0316 | -0.2243 | 124.9191 | -0.10528 | 62.0316 | 124.7955 | 124.9649 | -125.2625 | -125.2625
345.6406 | 125.4318 | -61.908 | 63.1119 | -0.10201 | 0.0064877 | 0.014046 | -0.0012733 | 0.063549 | -0.00036306 | 0.068599 | -61.9904 | 62.9837 | -62.1643 | -62.0224 | 62.9105 | 0.16479 | -0.086975 | 0.28381 | 62.9974 | -62.1368 | -0.25635 | -0.12817 | -0.082397 | -0.11444 | -0.20142 | -0.22888 | -0.11444 | 0.17395 | 61.821 | 62.1918 | 124.8184 | 124.8917 | -0.082397 | 124.9054 | 62.0728 | -0.22888 | 124.8917 | -0.082397 | 62.0728 | 124.8184 | 124.9054 | -125.2762 | -125.2487
346.6406 | 125.386 | -61.8988 | 63.1073 | -0.17067 | 0.0067013 | 0.01191 | -0.0017005 | 0.062481 | -0.00057686 | 0.06988 | -61.9949 | 62.9745 | -62.1552 | -62.0499 | 62.9059 | 0.16479 | -0.091553 | 0.24719 | 63.0157 | -62.1277 | -0.25635 | -0.13275 | -0.09613 | -0.15106 | -0.20142 | -0.22888 | -0.091553 | 0.16022 | 61.8073 | 62.146 | 124.8047 | 124.8734 | -0.09613 | 124.9146 | 62.0636 | -0.22888 | 124.8734 | -0.09613 | 62.0636 | 124.8047 | 124.9146 | -125.2625 | -125.235
347.6406 | 125.2899 | -61.9492 | 63.1622 | -0.19356 | 0.01311 | 0.012123 | 0.0053491 | 0.064617 | 6.414e-05 | 0.067531 | -62.0361 | 63.0798 | -62.1689 | -62.1048 | 62.8006 | 0.059509 | 0.11902 | 0.16479 | 63.089 | -62.2055 | -0.21973 | -0.082397 | -0.086975 | -0.15564 | -0.36163 | -0.25635 | -0.073242 | 0.13275 | 62.0682 | 62.114 | 124.7498 | 125.029 | -0.086975 | 125.0381 | 62.0087 | -0.25635 | 125.029 | -0.086975 | 62.0087 | 124.7498 | 125.0381 | -125.3311 | -125.3677
348.6406 | 125.3952 | -61.9217 | 63.1256 | -0.071488 | 0.0079831 | 0.0097733 | -0.0029823 | 0.06419 | -0.0014313 | 0.067531 | -62.0224 | 62.97 | -62.1323 | -62.0636 | 62.8784 | 0.14191 | -0.07782 | 0.21973 | 63.0249 | -62.1185 | -0.21057 | -0.15564 | -0.10071 | -0.14191 | -0.24719 | -0.19684 | -0.10071 | 0.10986 | 61.8439 | 62.1414 | 124.8001 | 124.8917 | -0.10071 | 124.9466 | 62.0636 | -0.19684 | 124.8917 | -0.10071 | 62.0636 | 124.8001 | 124.9466 | -125.2579 | -125.2441
349.6406 | 125.3769 | -61.9263 | 63.1302 | -0.071488 | 0.0064877 | 0.011055 | 8.546e-06 | 0.063762 | -0.00057686 | 0.069453 | -62.0316 | 62.9883 | -62.1552 | -62.0911 | 62.8693 | 0.10986 | -0.059509 | 0.21057 | 63.0295 | -62.1414 | -0.22888 | -0.14191 | -0.10528 | -0.16479 | -0.26093 | -0.21515 | -0.10071 | 0.1236 | 61.8668 | 62.1368 | 124.7955 | 124.9146 | -0.10528 | 124.9557 | 62.0361 | -0.21515 | 124.9146 | -0.10528 | 62.0361 | 124.7955 | 124.9557 | -125.2853 | -125.2716
350.6406 | 125.386 | -61.9217 | 63.089 | -0.14015 | 0.0094785 | 0.0095595 | -0.00063225 | 0.063762 | 0.00027774 | 0.069239 | -62.0041 | 62.9791 | -62.1506 | -62.027 | 62.8922 | 0.13733 | -0.082397 | 0.27008 | 62.9974 | -62.1414 | -0.22888 | -0.10986 | -0.082397 | -0.10529 | -0.19684 | -0.21973 | -0.091552 | 0.14648 | 61.8393 | 62.1918 | 124.8138 | 124.9008 | -0.082397 | 124.9191 | 62.059 | -0.21973 | 124.9008 | -0.082397 | 62.059 | 124.8138 | 124.9191 | -125.2396 | -125.2304
351.6406 | 125.322 | -61.9217 | 63.1073 | -0.048599 | 0.011615 | 0.0097733 | -0.0019141 | 0.06419 | -0.00057686 | 0.069453 | -62.0407 | 63.0112 | -62.1643 | -62.1002 | 62.8326 | 0.064087 | -0.054932 | 0.17395 | 62.9974 | -62.146 | -0.24262 | -0.096131 | -0.11902 | -0.17853 | -0.27466 | -0.2243 | -0.10986 | 0.1236 | 61.8668 | 62.0956 | 124.7543 | 124.9329 | -0.11902 | 124.9191 | 61.9858 | -0.2243 | 124.9329 | -0.11902 | 61.9858 | 124.7543 | 124.9191 | -125.2716 | -125.2533
352.6406 | 125.3723 | -61.9034 | 63.1302 | -0.19356 | 0.0090513 | 0.010841 | 0.00086295 | 0.060772 | -0.00057686 | 0.06988 | -61.9766 | 63.0203 | -62.1323 | -62.0453 | 62.8967 | 0.15564 | -0.018311 | 0.28381 | 63.0249 | -62.1506 | -0.22888 | -0.10986 | -0.073243 | -0.14191 | -0.23346 | -0.24719 | -0.10529 | 0.15564 | 61.8851 | 62.1872 | 124.8001 | 124.9237 | -0.073243 | 124.9283 | 62.059 | -0.24719 | 124.9237 | -0.073243 | 62.059 | 124.8001 | 124.9283 | -125.2625 | -125.2808
353.6406 | 125.3311 | -61.9308 | 63.1165 | -0.079117 | 0.0084103 | 0.0035781 | -0.0010597 | 0.061199 | 0.0013457 | 0.068599 | -62.0316 | 63.0066 | -62.178 | -62.0728 | 62.8738 | 0.091553 | -0.054932 | 0.20599 | 63.0203 | -62.1826 | -0.24719 | -0.10986 | -0.10071 | -0.14191 | -0.24262 | -0.25177 | -0.09613 | 0.14649 | 61.8759 | 62.1368 | 124.8047 | 124.9374 | -0.10071 | 124.9512 | 62.0224 | -0.25177 | 124.9374 | -0.10071 | 62.0224 | 124.8047 | 124.9512 | -125.2945 | -125.2991
354.6406 | 125.3494 | -61.9537 | 63.1119 | -0.071488 | 0.0084103 | 0.010628 | -0.0029823 | 0.061626 | 0.0011321 | 0.069239 | -62.0453 | 62.9974 | -62.178 | -62.0865 | 62.851 | 0.07782 | -0.054932 | 0.17395 | 63.0066 | -62.1506 | -0.22431 | -0.11444 | -0.091553 | -0.13275 | -0.26093 | -0.19684 | -0.10529 | 0.13275 | 61.8988 | 62.1277 | 124.8047 | 124.9512 | -0.091553 | 124.9603 | 62.0316 | -0.19684 | 124.9512 | -0.091553 | 62.0316 | 124.8047 | 124.9603 | -125.2899 | -125.2625
355.6406 | 125.322 | -61.9308 | 63.1027 | 0.050583 | 0.0088375 | 0.0076369 | 0.00022215 | 0.063335 | -0.0018585 | 0.067317 | -62.0453 | 62.97 | -62.1735 | -62.114 | 62.7411 | 0.24719 | -0.10986 | -0.009155 | 63.002 | -62.1414 | -0.24262 | -0.13275 | -0.11444 | -0.18311 | -0.36163 | -0.21057 | -0.10071 | 0.12817 | 61.821 | 61.9217 | 124.6719 | 124.9008 | -0.11444 | 124.9329 | 62.178 | -0.21057 | 124.9008 | -0.11444 | 62.178 | 124.6719 | 124.9329 | -125.2762 | -125.2441
356.6406 | 125.3677 | -61.9308 | 63.1165 | -0.04097 | 0.0096921 | 0.0067825 | -0.0029823 | 0.060131 | 0.00027774 | 0.067317 | -62.0361 | 62.9837 | -62.1826 | -62.0682 | 62.8738 | 0.11902 | -0.091553 | 0.2243 | 63.0112 | -62.1689 | -0.25177 | -0.13275 | -0.10529 | -0.13733 | -0.24262 | -0.23804 | -0.10529 | 0.14648 | 61.8393 | 62.1552 | 124.8047 | 124.9146 | -0.10529 | 124.942 | 62.0499 | -0.23804 | 124.9146 | -0.10529 | 62.0499 | 124.8047 | 124.942 | -125.2991 | -125.2853
357.6406 | 125.2808 | -61.9308 | 63.1668 | -0.29274 | 0.010119 | 0.01191 | 0.0025719 | 0.06184 | -0.00057686 | 0.070094 | -62.027 | 63.0524 | -62.1552 | -62.114 | 62.8052 | 0.07782 | 0.12817 | 0.16022 | 63.0753 | -62.2009 | -0.2243 | -0.11444 | -0.096131 | -0.18311 | -0.36163 | -0.27008 | -0.091553 | 0.12817 | 62.059 | 62.0911 | 124.736 | 124.9832 | -0.096131 | 125.0061 | 62.0087 | -0.27008 | 124.9832 | -0.096131 | 62.0087 | 124.736 | 125.0061 | -125.322 | -125.3677
358.6406 | 125.3494 | -61.9034 | 63.1027 | 0.21843 | 0.010119 | 0.014259 | 0.00064935 | 0.065471 | -0.0014313 | 0.070948 | -62.0041 | 62.9745 | -62.1918 | -62.0911 | 62.8418 | 0.050354 | -0.14648 | 0.15106 | 62.9837 | -62.146 | -0.28839 | -0.12817 | -0.10071 | -0.18768 | -0.26093 | -0.24261 | -0.11902 | 0.18768 | 61.7569 | 62.0544 | 124.7452 | 124.8779 | -0.10071 | 124.8871 | 61.9537 | -0.24261 | 124.8779 | -0.10071 | 61.9537 | 124.7452 | 124.8871 | -125.2945 | -125.2487
359.6406 | 125.3494 | -61.9446 | 63.1073 | 0.11925 | 0.010119 | 0.012337 | 8.546e-06 | 0.063976 | 0.00049134 | 0.06988 | -62.0453 | 62.9883 | -62.178 | -62.1323 | 62.8235 | 0.022888 | -0.10986 | 0.11444 | 63.0157 | -62.1918 | -0.23346 | -0.11902 | -0.10071 | -0.18768 | -0.28381 | -0.24719 | -0.091553 | 0.13275 | 61.8347 | 62.059 | 124.7681 | 124.9329 | -0.10071 | 124.9603 | 61.9675 | -0.24719 | 124.9329 | -0.10071 | 61.9675 | 124.7681 | 124.9603 | -125.2853 | -125.2991
360.6406 | 125.3357 | -61.9263 | 63.1119 | 0.050583 | 0.0084103 | 0.011269 | 0.0025719 | 0.063762 | -0.00079046 | 0.069667 | -62.0819 | 62.9883 | -62.1597 | -62.1414 | 62.8189 | 0.050354 | -0.082397 | 0.12817 | 63.002 | -62.1964 | -0.23346 | -0.1236 | -0.15564 | -0.21515 | -0.29297 | -0.27008 | -0.10986 | 0.07782 | 61.8439 | 62.0544 | 124.7452 | 124.9146 | -0.15564 | 124.9283 | 61.9766 | -0.27008 | 124.9146 | -0.15564 | 61.9766 | 124.7452 | 124.9283 | -125.2716 | -125.3082
361.6406 | 125.3403 | -61.94 | 63.0798 | 0.11162 | 0.01076 | 0.0149 | 8.546e-06 | 0.063549 | 0.0013457 | 0.069667 | -61.9995 | 62.9608 | -62.1735 | -62.0956 | 62.8372 | 0.036621 | -0.14648 | 0.13733 | 63.0066 | -62.1689 | -0.23346 | -0.11902 | -0.05951 | -0.15564 | -0.24262 | -0.22888 | -0.073242 | 0.17395 | 61.7935 | 62.0773 | 124.7772 | 124.9008 | -0.05951 | 124.9466 | 61.9766 | -0.22888 | 124.9008 | -0.05951 | 61.9766 | 124.7772 | 124.9466 | -125.2533 | -125.2487
362.6406 | 125.3586 | -61.9217 | 63.1302 | -0.086746 | 0.0079831 | 0.013405 | -0.0029823 | 0.062694 | 0.00091854 | 0.068599 | -62.0178 | 62.9791 | -62.1552 | -62.0865 | 62.8738 | 0.09613 | -0.068665 | 0.21057 | 63.0203 | -62.1368 | -0.23346 | -0.15106 | -0.09613 | -0.16479 | -0.25635 | -0.21515 | -0.10986 | 0.13733 | 61.853 | 62.1323 | 124.7955 | 124.9008 | -0.09613 | 124.942 | 62.0178 | -0.21515 | 124.9008 | -0.09613 | 62.0178 | 124.7955 | 124.942 | -125.2853 | -125.267
363.6406 | 125.3311 | -61.94 | 63.089 | 0.11925 | 0.0077695 | 0.0055007 | -0.0010597 | 0.062481 | 0.00049134 | 0.068171 | -61.8347 | 63.0157 | -62.1323 | -62.1048 | 62.8189 | 0.032043 | -0.064087 | 0.1236 | 63.0112 | -62.1506 | -0.19226 | -0.073242 | 0.10529 | -0.16479 | -0.27008 | -0.21057 | -0.07782 | 0.29755 | 61.8759 | 62.0636 | 124.7589 | 124.9557 | 0.10529 | 124.9512 | 61.972 | -0.21057 | 124.9557 | 0.10529 | 61.972 | 124.7589 | 124.9512 | -125.2213 | -125.2396
364.6406 | 125.3037 | -61.9308 | 63.0753 | 0.14214 | 0.0081967 | 0.01191 | -0.00063225 | 0.061626 | 0.00049134 | 0.068171 | -62.0132 | 62.9837 | -62.178 | -62.0956 | 62.8418 | 0.041199 | -0.14648 | 0.14191 | 62.9837 | -62.1689 | -0.24719 | -0.091552 | -0.082398 | -0.16479 | -0.23346 | -0.23804 | -0.091552 | 0.1648 | 61.7844 | 62.0728 | 124.7726 | 124.9146 | -0.082398 | 124.9146 | 61.972 | -0.23804 | 124.9146 | -0.082398 | 61.972 | 124.7726 | 124.9146 | -125.2533 | -125.2441
365.6406 | 125.386 | -61.9125 | 63.089 | -0.079117 | 0.0096921 | 0.0072097 | 0.0029993 | 0.063762 | -0.00057686 | 0.06988 | -61.9675 | 62.9883 | -62.1231 | -62.0682 | 62.8647 | 0.064087 | -0.16937 | 0.14648 | 62.9974 | -62.1368 | -0.21057 | -0.10071 | -0.054931 | -0.15564 | -0.2243 | -0.2243 | -0.091552 | 0.15564 | 61.7432 | 62.059 | 124.7772 | 124.9008 | -0.054931 | 124.91 | 61.9766 | -0.2243 | 124.9008 | -0.054931 | 61.9766 | 124.7772 | 124.91 | -125.2121 | -125.2258
366.6406 | 125.3632 | -61.9446 | 63.0798 | 0.14976 | 0.01076 | 0.013405 | 0.0010767 | 0.065685 | -0.0014313 | 0.067317 | -62.0087 | 62.9745 | -62.1552 | -62.0865 | 62.8464 | 0.050354 | -0.17395 | 0.14191 | 62.9929 | -62.1735 | -0.21057 | -0.10529 | -0.064087 | -0.14191 | -0.23346 | -0.22888 | -0.086975 | 0.14648 | 61.7706 | 62.0865 | 124.791 | 124.9191 | -0.064087 | 124.9374 | 61.9949 | -0.22888 | 124.9191 | -0.064087 | 61.9949 | 124.791 | 124.9374 | -125.235 | -125.2533
367.6406 | 125.3952 | -61.9034 | 63.1348 | -1.6508 | 0.011401 | 0.0149 | -0.00020505 | 0.062908 | -0.00079046 | 0.070735 | -62.1094 | 62.9745 | -62.1506 | -62.0316 | 62.9013 | 0.16479 | -0.036621 | 0.29297 | 63.002 | -62.1368 | -0.24719 | -0.16022 | -0.20599 | -0.12817 | -0.23346 | -0.23346 | -0.13275 | 0.041199 | 61.8668 | 62.1964 | 124.8047 | 124.8779 | -0.20599 | 124.9054 | 62.0682 | -0.23346 | 124.8779 | -0.20599 | 62.0682 | 124.8047 | 124.9054 | -125.2853 | -125.2716
368.6406 | 125.3769 | -61.9354 | 63.0707 | 0.17265 | 0.0084103 | 0.01255 | 0.0021447 | 0.065258 | -0.00014946 | 0.067531 | -61.972 | 62.9654 | -62.1506 | -62.0682 | 62.8555 | 0.050354 | -0.17853 | 0.15106 | 62.9837 | -62.1597 | -0.21515 | -0.10529 | -0.036621 | -0.13275 | -0.21515 | -0.2243 | -0.086975 | 0.17853 | 61.7569 | 62.0865 | 124.791 | 124.9008 | -0.036621 | 124.9191 | 61.9858 | -0.2243 | 124.9008 | -0.036621 | 61.9858 | 124.791 | 124.9191 | -125.2213 | -125.2304
369.6406 | 125.386 | -61.9171 | 63.0661 | 0.42442 | 0.01076 | 0.013832 | 0.0042809 | 0.063762 | 0.00091854 | 0.069453 | -61.94 | 62.9974 | -62.1552 | -62.0636 | 62.8647 | 0.059509 | -0.19226 | 0.15564 | 63.0112 | -62.1872 | -0.23804 | -0.068664 | -0.022888 | -0.14649 | -0.20142 | -0.27008 | -0.054932 | 0.21515 | 61.7249 | 62.0728 | 124.7818 | 124.9146 | -0.022888 | 124.9283 | 61.9766 | -0.27008 | 124.9146 | -0.022888 | 61.9766 | 124.7818 | 124.9283 | -125.2213 | -125.2533
370.6406 | 125.3265 | -61.9263 | 63.0615 | 0.15739 | 0.0090513 | 0.012337 | 0.0032129 | 0.065044 | -0.0022859 | 0.070521 | -61.9995 | 62.9745 | -62.1552 | -62.0728 | 62.8418 | 0.045776 | -0.17853 | 0.16022 | 62.9929 | -62.1689 | -0.22888 | -0.086975 | -0.073242 | -0.14648 | -0.21973 | -0.24261 | -0.068664 | 0.15564 | 61.7477 | 62.0865 | 124.7681 | 124.9008 | -0.073242 | 124.9191 | 61.972 | -0.24261 | 124.9008 | -0.073242 | 61.972 | 124.7681 | 124.9191 | -125.2167 | -125.2304
371.6406 | 125.3723 | -61.9171 | 63.0936 | 0.11925 | 0.011188 | 0.012123 | 0.0047081 | 0.066967 | -0.0022859 | 0.069453 | -61.9904 | 62.9883 | -62.1597 | -62.0682 | 62.9791 | 0.022888 | -0.40741 | 0.36163 | 62.9562 | -62.1964 | -0.24262 | -0.10529 | -0.073242 | -0.15106 | -0.11444 | -0.27924 | -0.13733 | 0.16937 | 61.5097 | 62.2787 | 124.8962 | 124.9054 | -0.073242 | 124.8734 | 61.94 | -0.27924 | 124.9054 | -0.073242 | 61.94 | 124.8962 | 124.8734 | -125.2533 | -125.2899
372.6406 | 125.3448 | -61.9125 | 63.089 | 0.13451 | 0.0075559 | 0.014687 | 0.00086295 | 0.06419 | -0.0016449 | 0.070094 | -62.0041 | 62.9608 | -62.1735 | -62.0956 | 62.851 | 0.068665 | -0.16022 | 0.13733 | 62.9929 | -62.1689 | -0.26093 | -0.12817 | -0.091552 | -0.1831 | -0.23804 | -0.25635 | -0.09613 | 0.16937 | 61.7523 | 62.0499 | 124.7635 | 124.8734 | -0.091552 | 124.9054 | 61.9812 | -0.25635 | 124.8734 | -0.091552 | 61.9812 | 124.7635 | 124.9054 | -125.2625 | -125.2579
373.6406 | 125.354 | -61.9217 | 63.0798 | -1.4982 | 0.0092649 | 0.015541 | 0.0032129 | 0.065685 | 0.0019867 | 0.069667 | -62.0224 | 63.0341 | -62.1368 | -62.0819 | 62.8464 | 0.059509 | -0.1831 | 0.16022 | 62.9837 | -62.178 | -0.21515 | -0.045776 | -0.10071 | -0.16022 | -0.23346 | -0.25635 | -0.09613 | 0.11444 | 61.7386 | 62.0819 | 124.7681 | 124.9557 | -0.10071 | 124.9054 | 61.9812 | -0.25635 | 124.9557 | -0.10071 | 61.9812 | 124.7681 | 124.9054 | -125.2167 | -125.2579
374.6406 | 125.3403 | -61.9537 | 63.0661 | 0.20317 | 0.01076 | 0.013191 | 0.0057763 | 0.065899 | 0.00070494 | 0.069026 | -61.972 | 63.0112 | -62.1414 | -61.9675 | 63.0295 | 0.22888 | -0.23346 | 0.20142 | 63.0112 | -62.1597 | -0.18768 | -0.054932 | -0.018311 | -0.013733 | -0.036621 | -0.20599 | -0.054932 | 0.16937 | 61.7203 | 62.1552 | 124.9832 | 124.9649 | -0.018311 | 124.9649 | 62.1826 | -0.20599 | 124.9649 | -0.018311 | 62.1826 | 124.9832 | 124.9649 | -125.2075 | -125.2258
375.6406 | 125.3632 | -61.9308 | 63.089 | 0.20317 | 0.010547 | 0.012123 | 0.0053491 | 0.066326 | -0.0014313 | 0.068171 | -61.9949 | 63.0112 | -62.146 | -62.0865 | 62.8326 | 0.050354 | -0.16022 | 0.13275 | 63.0066 | -62.1689 | -0.21515 | -0.07782 | -0.064087 | -0.15564 | -0.25635 | -0.23804 | -0.082397 | 0.15106 | 61.7706 | 62.0636 | 124.7635 | 124.942 | -0.064087 | 124.9374 | 61.9812 | -0.23804 | 124.942 | -0.064087 | 61.9812 | 124.7635 | 124.9374 | -125.235 | -125.2579
376.6406 | 125.3448 | -61.94 | 63.0798 | 0.18791 | 0.011188 | 0.011055 | 0.0051355 | 0.065044 | -0.00014946 | 0.068171 | -62.0087 | 63.0478 | -62.1643 | -62.1002 | 62.8281 | 0.041199 | -0.16479 | 0.10071 | 63.0386 | -62.1826 | -0.22431 | -0.032043 | -0.068665 | -0.16022 | -0.25177 | -0.24262 | -0.041199 | 0.15564 | 61.7752 | 62.0407 | 124.7681 | 124.9878 | -0.068665 | 124.9786 | 61.9812 | -0.24262 | 124.9878 | -0.068665 | 61.9812 | 124.7681 | 124.9786 | -125.2441 | -125.2625
377.6406 | 125.3632 | -61.9354 | 63.0798 | -0.04097 | 0.0086239 | 0.0099869 | -0.0034095 | 0.065471 | -0.0012177 | 0.06988 | -62.0499 | 62.97 | -62.1872 | -62.0956 | 62.851 | 0.10986 | -0.086975 | 0.20142 | 63.0249 | -62.1689 | -0.25177 | -0.10986 | -0.11444 | -0.16022 | -0.22888 | -0.23346 | -0.054932 | 0.13733 | 61.8484 | 62.1368 | 124.7864 | 124.9054 | -0.11444 | 124.9603 | 62.0453 | -0.23346 | 124.9054 | -0.11444 | 62.0453 | 124.7864 | 124.9603 | -125.267 | -125.2487
378.6406 | 125.3952 | -61.9217 | 63.0661 | 0.13451 | 0.0086239 | 0.013191 | 0.0021447 | 0.065044 | -0.0010041 | 0.069667 | -61.9858 | 63.0066 | -62.1506 | -62.2238 | 62.9883 | 0.19226 | -0.16479 | 0.16022 | 62.9929 | -62.1597 | -0.22888 | -0.059509 | -0.064087 | -0.30212 | -0.07782 | -0.23804 | -0.073242 | 0.16479 | 61.7569 | 62.0819 | 124.91 | 124.9283 | -0.064087 | 124.9146 | 62.114 | -0.23804 | 124.9283 | -0.064087 | 62.114 | 124.91 | 124.9146 | -125.2167 | -125.2258
379.6406 | 125.3037 | -61.9675 | 63.089 | 0.18791 | 0.0084103 | 0.013619 | 0.0064171 | 0.06483 | 0.00049134 | 0.069667 | -62.0453 | 63.0569 | -62.1552 | -62.1643 | 62.7777 | -0.004578 | -0.068665 | 0.041199 | 63.0249 | -62.2147 | -0.18768 | -0.032043 | -0.07782 | -0.19684 | -0.31128 | -0.24719 | -0.064087 | 0.10986 | 61.8988 | 62.0087 | 124.7452 | 125.0244 | -0.07782 | 124.9924 | 61.9629 | -0.24719 | 125.0244 | -0.07782 | 61.9629 | 124.7452 | 124.9924 | -125.2441 | -125.3037
380.6406 | 125.3998 | -61.9446 | 63.0753 | 0.18791 | 0.0094785 | 0.016182 | 0.0021447 | 0.065044 | 0.00091854 | 0.070735 | -61.9766 | 62.9974 | -62.178 | -62.0773 | 62.8601 | 0.073242 | -0.20599 | 0.14648 | 63.0066 | -62.178 | -0.23346 | -0.077819 | -0.032044 | -0.13275 | -0.21515 | -0.23346 | -0.068664 | 0.20142 | 61.7386 | 62.0911 | 124.8047 | 124.942 | -0.032044 | 124.9512 | 62.0178 | -0.23346 | 124.942 | -0.032044 | 62.0178 | 124.8047 | 124.9512 | -125.2533 | -125.2533
381.6406 | 125.3677 | -61.94 | 63.0753 | 0.23369 | 0.012469 | 0.017464 | 0.0036401 | 0.065258 | 0.00091854 | 0.071162 | -61.9949 | 63.0386 | -62.1826 | -62.0911 | 62.8281 | 0.036621 | -0.1831 | 0.11444 | 63.0112 | -62.2147 | -0.24262 | -0.036621 | -0.054932 | -0.15106 | -0.24719 | -0.27466 | -0.064087 | 0.18768 | 61.7569 | 62.0544 | 124.7681 | 124.9786 | -0.054932 | 124.9512 | 61.9766 | -0.27466 | 124.9786 | -0.054932 | 61.9766 | 124.7681 | 124.9512 | -125.2579 | -125.2899
382.6406 | 125.3128 | -61.9354 | 63.1073 | 0.11925 | 0.0090513 | 0.014473 | -0.0012733 | 0.063335 | -0.0020721 | 0.069667 | -62.0316 | 62.9883 | -62.1506 | -62.1277 | 62.8326 | 0.036621 | -0.10071 | 0.1236 | 63.0432 | -62.1689 | -0.21515 | -0.11902 | -0.09613 | -0.19226 | -0.27466 | -0.23346 | -0.064087 | 0.11902 | 61.8347 | 62.059 | 124.7681 | 124.9237 | -0.09613 | 124.9786 | 61.972 | -0.23346 | 124.9237 | -0.09613 | 61.972 | 124.7681 | 124.9786 | -125.2579 | -125.2762
383.6406 | 125.322 | -61.9583 | 63.0753 | 0.12688 | 0.0092649 | 0.015968 | 0.0032129 | 0.065471 | -0.00057686 | 0.06988 | -62.0361 | 63.0524 | -62.1735 | -62.1185 | 62.7914 | 0.004578 | -0.13733 | 0.082397 | 63.0066 | -62.233 | -0.21515 | -0.022888 | -0.07782 | -0.16022 | -0.28381 | -0.27466 | -0.068664 | 0.13733 | 61.821 | 62.0407 | 124.7498 | 125.0107 | -0.07782 | 124.9649 | 61.9629 | -0.27466 | 125.0107 | -0.07782 | 61.9629 | 124.7498 | 124.9649 | -125.2487 | -125.3082
384.6406 | 125.3586 | -61.9263 | 63.0524 | 0.18791 | 0.010333 | 0.018318 | 0.00086295 | 0.062694 | -0.0014313 | 0.070521 | -61.9675 | 63.0157 | -62.1506 | -62.114 | 62.9059 | 0.09613 | -0.19226 | 0.15106 | 63.002 | -62.1735 | -0.2243 | -0.036621 | -0.041198 | -0.18768 | -0.14648 | -0.24719 | -0.050354 | 0.18311 | 61.734 | 62.0773 | 124.8322 | 124.942 | -0.041198 | 124.9283 | 62.0224 | -0.24719 | 124.942 | -0.041198 | 62.0224 | 124.8322 | 124.9283 | -125.2029 | -125.2258
385.6406 | 125.3082 | -61.9675 | 63.0569 | 0.18791 | 0.011615 | 0.011482 | 0.0051355 | 0.066326 | -0.0029267 | 0.069453 | -62.027 | 63.0615 | -62.2055 | -62.1506 | 62.7823 | -0.004578 | -0.10529 | 0.059509 | 62.9974 | -62.1826 | -0.23804 | 0.004577 | -0.05951 | -0.18311 | -0.27466 | -0.21515 | -0.059509 | 0.17853 | 61.8622 | 62.027 | 124.7498 | 125.029 | -0.05951 | 124.9649 | 61.9629 | -0.21515 | 125.029 | -0.05951 | 61.9629 | 124.7498 | 124.9649 | -125.2625 | -125.2396
386.6406 | 125.322 | -61.9446 | 63.0936 | 0.16502 | 0.011401 | 0.0093459 | 0.0044945 | 0.065685 | 0.0022003 | 0.069667 | -62.0636 | 63.0386 | -62.1964 | -62.1368 | 62.7914 | 0.004578 | -0.10071 | 0.073242 | 63.0157 | -62.2284 | -0.25177 | -0.054932 | -0.11902 | -0.19226 | -0.30212 | -0.28381 | -0.07782 | 0.13275 | 61.8439 | 62.0178 | 124.736 | 124.9832 | -0.11902 | 124.9603 | 61.9492 | -0.28381 | 124.9832 | -0.11902 | 61.9492 | 124.736 | 124.9603 | -125.2899 | -125.322
387.6406 | 125.3128 | -61.9171 | 63.0981 | -0.086746 | 0.0073423 | 0.0082779 | -0.0012733 | 0.063121 | -0.0016449 | 0.069026 | -62.0407 | 62.9837 | -62.1414 | -62.1002 | 62.8464 | 0.07782 | -0.045776 | 0.1831 | 63.0478 | -62.1552 | -0.2243 | -0.11444 | -0.1236 | -0.18311 | -0.25177 | -0.23804 | -0.050354 | 0.10071 | 61.8713 | 62.1002 | 124.7635 | 124.9008 | -0.1236 | 124.9649 | 61.9949 | -0.23804 | 124.9008 | -0.1236 | 61.9949 | 124.7635 | 124.9649 | -125.2396 | -125.2533
388.6406 | 125.3632 | -61.908 | 63.0615 | 0.18028 | 0.0084103 | 0.012337 | 0.00064935 | 0.064403 | 0.0017731 | 0.070948 | -61.9858 | 62.9837 | -62.1368 | -62.0865 | 62.8418 | 0.064087 | -0.1831 | 0.15106 | 62.9837 | -62.1735 | -0.22888 | -0.077819 | -0.07782 | -0.17853 | -0.21973 | -0.2655 | -0.077819 | 0.15106 | 61.7249 | 62.059 | 124.7498 | 124.8917 | -0.07782 | 124.8917 | 61.972 | -0.2655 | 124.8917 | -0.07782 | 61.972 | 124.7498 | 124.8917 | -125.1984 | -125.235
389.6406 | 125.3815 | -61.9034 | 63.0753 | 0.20317 | 0.013965 | 0.014046 | 0.0081261 | 0.066112 | -0.0014313 | 0.068171 | -61.9766 | 63.0157 | -62.1506 | -61.9537 | 62.8372 | 0.045776 | -0.14191 | 0.12817 | 63.002 | -62.178 | -0.24719 | -0.059509 | -0.073243 | -0.050354 | -0.23804 | -0.27466 | -0.073242 | 0.17395 | 61.7615 | 62.0316 | 124.7406 | 124.9191 | -0.073243 | 124.9054 | 61.9492 | -0.27466 | 124.9191 | -0.073243 | 61.9492 | 124.7406 | 124.9054 | -125.2258 | -125.2533
390.6406 | 125.3311 | -61.9125 | 63.0936 | 0.20317 | 0.010974 | 0.014687 | 0.0027855 | 0.064403 | -0.0029267 | 0.069667 | -61.9629 | 62.9883 | -62.1643 | -62.1048 | 62.8876 | 0.086975 | -0.19684 | 0.14191 | 63.0249 | -62.178 | -0.25177 | -0.10529 | -0.050354 | -0.19226 | -0.20599 | -0.2655 | -0.068665 | 0.20142 | 61.7157 | 62.0544 | 124.8001 | 124.9008 | -0.050354 | 124.9374 | 61.9995 | -0.2655 | 124.9008 | -0.050354 | 61.9995 | 124.8001 | 124.9374 | -125.2579 | -125.2716
391.6406 | 125.3403 | -61.9308 | 63.0707 | 0.14214 | 0.0096921 | 0.010201 | 0.0023583 | 0.064617 | -0.00014946 | 0.069453 | -61.9904 | 62.9837 | -62.1597 | -62.0819 | 62.8189 | 0.064087 | -0.17395 | 0.15564 | 62.9929 | -62.1918 | -0.22888 | -0.086975 | -0.059509 | -0.15106 | -0.25177 | -0.26093 | -0.07782 | 0.16937 | 61.7569 | 62.0865 | 124.7498 | 124.9146 | -0.059509 | 124.9237 | 61.9949 | -0.26093 | 124.9146 | -0.059509 | 61.9949 | 124.7498 | 124.9237 | -125.2304 | -125.2625
392.6406 | 125.3723 | -61.9263 | 63.089 | -0.025711 | 0.0084103 | 0.010841 | -0.0019141 | 0.063549 | 6.414e-05 | 0.067744 | -62.0132 | 62.9837 | -62.1735 | -62.0819 | 62.8647 | 0.09613 | -0.073242 | 0.21515 | 63.0203 | -62.1689 | -0.24719 | -0.10528 | -0.086975 | -0.15564 | -0.2243 | -0.24261 | -0.068664 | 0.16022 | 61.853 | 62.1414 | 124.791 | 124.91 | -0.086975 | 124.9466 | 62.0224 | -0.24261 | 124.91 | -0.086975 | 62.0224 | 124.791 | 124.9466 | -125.2625 | -125.2579
393.6406 | 125.3632 | -61.9171 | 63.1027 | -0.23933 | 0.0062741 | 0.011696 | 0.0019311 | 0.062908 | -0.00079046 | 0.068171 | -61.9766 | 63.002 | -62.1368 | -62.027 | 62.9013 | 0.16022 | -0.036621 | 0.30212 | 63.0249 | -62.1414 | -0.21973 | -0.10071 | -0.05951 | -0.10986 | -0.20142 | -0.2243 | -0.07782 | 0.16022 | 61.8805 | 62.2192 | 124.8184 | 124.9191 | -0.05951 | 124.942 | 62.0773 | -0.2243 | 124.9191 | -0.05951 | 62.0773 | 124.8184 | 124.942 | -125.2396 | -125.2441
394.6406 | 125.3403 | -61.9308 | 63.089 | 0.19554 | 0.0099057 | 0.0149 | 0.0021447 | 0.064403 | -0.00014946 | 0.068599 | -61.9949 | 62.9654 | -62.1689 | -62.0773 | 62.8326 | 0.054932 | -0.17395 | 0.15106 | 63.002 | -62.178 | -0.23804 | -0.1236 | -0.064087 | -0.14648 | -0.25635 | -0.24719 | -0.086975 | 0.17395 | 61.7569 | 62.0819 | 124.7635 | 124.8962 | -0.064087 | 124.9329 | 61.9858 | -0.24719 | 124.8962 | -0.064087 | 61.9858 | 124.7635 | 124.9329 | -125.2579 | -125.267
395.6406 | 125.3448 | -61.94 | 63.0844 | 0.16502 | 0.0090513 | 0.01191 | 0.0021447 | 0.063976 | -0.0012177 | 0.069453 | -61.9995 | 62.9837 | -62.1643 | -62.0865 | 62.8372 | 0.041199 | -0.15564 | 0.13275 | 63.002 | -62.178 | -0.22431 | -0.10071 | -0.05951 | -0.14648 | -0.24719 | -0.23804 | -0.082398 | 0.16479 | 61.7844 | 62.0728 | 124.7772 | 124.9237 | -0.05951 | 124.942 | 61.9812 | -0.23804 | 124.9237 | -0.05951 | 61.9812 | 124.7772 | 124.942 | -125.2487 | -125.2625
396.6406 | 125.3494 | -61.908 | 63.0707 | 0.058212 | 0.01076 | 0.0084915 | 0.00064935 | 0.062267 | -0.0031403 | 0.068812 | -62.0453 | 62.9745 | -62.1643 | -62.114 | 62.7914 | 0.022888 | -0.09613 | 0.12817 | 63.0066 | -62.1643 | -0.25635 | -0.096131 | -0.13733 | -0.20599 | -0.27924 | -0.25635 | -0.064087 | 0.11902 | 61.8118 | 62.0361 | 124.6994 | 124.8825 | -0.13733 | 124.9146 | 61.9308 | -0.25635 | 124.8825 | -0.13733 | 61.9308 | 124.6994 | 124.9146 | -125.235 | -125.235
397.6406 | 125.3311 | -61.8988 | 63.1302 | -0.21645 | 0.0094785 | 0.010201 | 0.00022215 | 0.061412 | -0.0027131 | 0.068385 | -61.9537 | 62.9974 | -62.1323 | -62.0316 | 62.8967 | 0.14191 | -0.032043 | 0.28839 | 63.0295 | -62.1368 | -0.23346 | -0.13275 | -0.054931 | -0.13275 | -0.23346 | -0.23804 | -0.10071 | 0.17853 | 61.8668 | 62.1872 | 124.7955 | 124.8962 | -0.054931 | 124.9283 | 62.0407 | -0.23804 | 124.8962 | -0.054931 | 62.0407 | 124.7955 | 124.9283 | -125.2625 | -125.267
398.6406 | 125.2487 | -61.908 | 63.1348 | -0.26222 | 0.0079831 | 0.011055 | 0.0015039 | 0.063335 | -0.0018585 | 0.069239 | -61.9949 | 63.0478 | -62.1323 | -62.0819 | 62.8189 | 0.10071 | 0.091553 | 0.21973 | 63.0798 | -62.1735 | -0.2243 | -0.086975 | -0.086975 | -0.17395 | -0.31586 | -0.2655 | -0.054932 | 0.13733 | 61.9995 | 62.1277 | 124.7269 | 124.9557 | -0.086975 | 124.9878 | 62.0087 | -0.2655 | 124.9557 | -0.086975 | 62.0087 | 124.7269 | 124.9878 | -125.267 | -125.3082
399.6406 | 125.3082 | -61.9446 | 63.089 | 0.19554 | 0.0075559 | 0.01191 | -0.00063225 | 0.060985 | -0.0020721 | 0.070735 | -62.0041 | 62.9745 | -62.1643 | -62.1048 | 62.8235 | 0.022888 | -0.13733 | 0.14191 | 63.0203 | -62.1597 | -0.21973 | -0.11444 | -0.059509 | -0.16022 | -0.2655 | -0.21515 | -0.068664 | 0.16022 | 61.8073 | 62.0865 | 124.7681 | 124.9191 | -0.059509 | 124.9649 | 61.9675 | -0.21515 | 124.9191 | -0.059509 | 61.9675 | 124.7681 | 124.9649 | -125.2533 | -125.2487
400.6406 | 125.2899 | -61.8988 | 63.0844 | 0.058212 | 0.0092649 | 0.010414 | 0.0012903 | 0.063762 | -0.0020721 | 0.071162 | -62.0453 | 62.9974 | -62.1597 | -61.9812 | 62.7594 | -0.086975 | -0.059509 | 0.091553 | 63.002 | -62.1689 | -0.26093 | -0.086975 | -0.14648 | -0.082397 | -0.32501 | -0.27008 | -0.082398 | 0.11444 | 61.8393 | 61.9904 | 124.6582 | 124.8962 | -0.14648 | 124.9008 | 61.8118 | -0.27008 | 124.8962 | -0.14648 | 61.8118 | 124.6582 | 124.9008 | -125.2441 | -125.2533
401.6406 | 125.3037 | -61.9308 | 63.0981 | 0.12688 | 0.0086239 | 0.0095595 | 0.00022215 | 0.062481 | 0.0022003 | 0.070308 | -62.0636 | 62.9974 | -62.1826 | -62.1552 | 62.7869 | 0.032043 | -0.086975 | 0.1236 | 63.0295 | -62.1689 | -0.25177 | -0.10071 | -0.13275 | -0.2243 | -0.31128 | -0.23804 | -0.068665 | 0.11902 | 61.8439 | 62.0544 | 124.7177 | 124.9283 | -0.13275 | 124.9603 | 61.9629 | -0.23804 | 124.9283 | -0.13275 | 61.9629 | 124.7177 | 124.9603 | -125.2808 | -125.267
402.6406 | 125.2213 | -61.9217 | 63.1393 | -0.23933 | 0.010333 | 0.0078507 | 0.0032129 | 0.063549 | -0.0010041 | 0.069239 | -62.0178 | 63.0524 | -62.1597 | -62.1048 | 62.8006 | 0.064087 | 0.1236 | 0.16479 | 63.089 | -62.1918 | -0.23804 | -0.086975 | -0.09613 | -0.1831 | -0.33874 | -0.27008 | -0.050354 | 0.14191 | 62.0453 | 62.0865 | 124.7223 | 124.9741 | -0.09613 | 125.0107 | 61.9858 | -0.27008 | 124.9741 | -0.09613 | 61.9858 | 124.7223 | 125.0107 | -125.2991 | -125.3311
403.6562 | 125.2991 | -61.9492 | 63.1302 | -0.14015 | 0.011188 | 0.014046 | 0.0083397 | 0.06718 | -0.00036306 | 0.067744 | -61.9675 | 63.1027 | -62.1506 | -61.972 | 62.8876 | 0.064087 | 0.086975 | 0.17853 | 63.0707 | -62.1826 | -0.20142 | -0.027466 | -0.01831 | -0.022888 | -0.24261 | -0.23346 | -0.059509 | 0.18311 | 62.0361 | 62.1277 | 124.8367 | 125.0519 | -0.01831 | 125.0198 | 62.0132 | -0.23346 | 125.0519 | -0.01831 | 62.0132 | 124.8367 | 125.0198 | -125.2808 | -125.3128
404.6406 | 125.3586 | -61.9034 | 63.0936 | -0.071488 | 0.0088375 | 0.0084915 | -0.0014869 | 0.065044 | -0.0012177 | 0.069667 | -62.027 | 62.9745 | -62.1643 | -62.0865 | 62.8647 | 0.10529 | -0.064087 | 0.19684 | 63.0066 | -62.1323 | -0.26093 | -0.11902 | -0.1236 | -0.18311 | -0.22888 | -0.22888 | -0.086975 | 0.13733 | 61.8393 | 62.1002 | 124.7681 | 124.8779 | -0.1236 | 124.91 | 62.0087 | -0.22888 | 124.8779 | -0.1236 | 62.0087 | 124.7681 | 124.91 | -125.2579 | -125.2258
405.6406 | 125.3128 | -61.9217 | 63.1119 | -0.048599 | 0.0088375 | 0.012764 | -0.0012733 | 0.063335 | -0.0014313 | 0.069026 | -62.027 | 62.9791 | -62.1506 | -62.0728 | 62.8464 | 0.10529 | -0.059509 | 0.19684 | 63.0112 | -62.146 | -0.22888 | -0.13275 | -0.10529 | -0.15106 | -0.2655 | -0.2243 | -0.10071 | 0.1236 | 61.8622 | 62.1185 | 124.7681 | 124.9008 | -0.10529 | 124.9329 | 62.027 | -0.2243 | 124.9008 | -0.10529 | 62.027 | 124.7681 | 124.9329 | -125.2625 | -125.2579
406.6406 | 125.3357 | -61.9125 | 63.0981 | -0.048599 | 0.0077695 | 0.010414 | -0.00063225 | 0.06419 | 0.00049134 | 0.070735 | -62.0132 | 62.9654 | -62.1643 | -62.0544 | 62.8555 | 0.09613 | -0.068665 | 0.21973 | 63.0112 | -62.1689 | -0.25177 | -0.13275 | -0.10071 | -0.14191 | -0.24262 | -0.25635 | -0.086976 | 0.15106 | 61.8439 | 62.1323 | 124.7681 | 124.8779 | -0.10071 | 124.9237 | 62.0087 | -0.25635 | 124.8779 | -0.10071 | 62.0087 | 124.7681 | 124.9237 | -125.2625 | -125.267
407.6406 | 125.2853 | -61.9537 | 63.1348 | -0.23933 | 0.010974 | 0.012337 | 0.0042809 | 0.063335 | 0.00027774 | 0.067103 | -62.0178 | 63.0936 | -62.1597 | -62.1185 | 62.796 | 0.050354 | 0.11902 | 0.16937 | 63.0707 | -62.2055 | -0.20599 | -0.041199 | -0.064087 | -0.16479 | -0.33874 | -0.25177 | -0.064087 | 0.14191 | 62.0728 | 62.1231 | 124.7498 | 125.0473 | -0.064087 | 125.0244 | 62.0041 | -0.25177 | 125.0473 | -0.064087 | 62.0041 | 124.7498 | 125.0244 | -125.2945 | -125.3403
408.6406 | 125.2762 | -61.9492 | 63.1165 | -0.18593 | 0.011828 | 0.013832 | 0.0053491 | 0.065899 | 0.00049134 | 0.067103 | -61.9858 | 63.1073 | -62.1323 | -62.0682 | 62.8281 | 0.082397 | 0.068665 | 0.17853 | 63.0936 | -62.1552 | -0.18311 | -0.009155 | -0.036621 | -0.11902 | -0.28839 | -0.20599 | -0.022888 | 0.14648 | 62.0178 | 62.1277 | 124.7772 | 125.0565 | -0.036621 | 125.0427 | 62.0316 | -0.20599 | 125.0565 | -0.036621 | 62.0316 | 124.7772 | 125.0427 | -125.2487 | -125.2716
409.6406 | 125.3265 | -61.9034 | 63.0936 | -0.10963 | 0.0084103 | 0.0069961 | -0.0019141 | 0.064403 | 0.00027774 | 0.06689 | -61.9995 | 62.9974 | -62.146 | -62.059 | 62.883 | 0.14191 | -0.073242 | 0.22888 | 63.0249 | -62.1277 | -0.24261 | -0.09613 | -0.096131 | -0.15564 | -0.21057 | -0.2243 | -0.068665 | 0.14648 | 61.8301 | 62.1323 | 124.7864 | 124.9008 | -0.096131 | 124.9283 | 62.0453 | -0.2243 | 124.9008 | -0.096131 | 62.0453 | 124.7864 | 124.9283 | -125.2396 | -125.2213
410.6406 | 125.3448 | -61.9171 | 63.1073 | -0.079117 | 0.01076 | 0.012123 | -0.0023413 | 0.062694 | -0.0014313 | 0.069453 | -62.0224 | 62.97 | -62.146 | -62.0636 | 62.8693 | 0.13275 | -0.068665 | 0.23804 | 63.0341 | -62.1323 | -0.22888 | -0.13733 | -0.10529 | -0.14649 | -0.23804 | -0.21515 | -0.073242 | 0.1236 | 61.8484 | 62.1552 | 124.7864 | 124.8871 | -0.10529 | 124.9512 | 62.0499 | -0.21515 | 124.8871 | -0.10529 | 62.0499 | 124.7864 | 124.9512 | -125.2533 | -125.2396
411.6406 | 125.3448 | -61.8896 | 63.1027 | -0.079117 | 0.0079831 | 0.0097733 | 0.0010767 | 0.063335 | -0.0014313 | 0.06988 | -62.0087 | 62.9471 | -62.1643 | -62.0453 | 62.8464 | 0.1236 | -0.073242 | 0.25177 | 62.9837 | -62.1506 | -0.27466 | -0.15564 | -0.11902 | -0.15564 | -0.25635 | -0.26093 | -0.11902 | 0.15564 | 61.8164 | 62.1414 | 124.736 | 124.8367 | -0.11902 | 124.8734 | 62.0132 | -0.26093 | 124.8367 | -0.11902 | 62.0132 | 124.736 | 124.8734 | -125.267 | -125.2533
412.6406 | 125.267 | -61.9492 | 63.1577 | -0.22408 | 0.011828 | 0.010628 | 0.0055627 | 0.065258 | -0.00079046 | 0.068599 | -62.0224 | 63.0936 | -62.1597 | -62.1002 | 62.7869 | 0.064087 | 0.14191 | 0.16479 | 63.0615 | -62.1826 | -0.21057 | -0.064087 | -0.073242 | -0.15106 | -0.37079 | -0.23346 | -0.096131 | 0.13733 | 62.0911 | 62.114 | 124.736 | 125.0427 | -0.073242 | 125.0107 | 62.0132 | -0.23346 | 125.0427 | -0.073242 | 62.0132 | 124.736 | 125.0107 | -125.3174 | -125.3403
413.6406 | 125.2945 | -61.94 | 63.1531 | -0.22408 | 0.0092649 | 0.012764 | 0.0047081 | 0.063762 | -0.0010041 | 0.06689 | -61.9995 | 63.0478 | -62.1689 | -62.0544 | 62.8189 | 0.086975 | 0.059509 | 0.19226 | 63.089 | -62.1506 | -0.22888 | -0.10529 | -0.05951 | -0.11444 | -0.33417 | -0.21057 | -0.064087 | 0.16937 | 61.9995 | 62.1323 | 124.7589 | 124.9878 | -0.05951 | 125.029 | 62.027 | -0.21057 | 124.9878 | -0.05951 | 62.027 | 124.7589 | 125.029 | -125.322 | -125.3037
414.6406 | 125.3403 | -61.8896 | 63.1165 | -0.23933 | 0.010333 | 0.0097733 | -0.0031959 | 0.065258 | -0.0018585 | 0.069239 | -61.9675 | 62.9791 | -62.1094 | -62.0361 | 62.883 | 0.15564 | -0.004578 | 0.27924 | 63.0341 | -62.114 | -0.21973 | -0.13733 | -0.07782 | -0.14648 | -0.23346 | -0.22431 | -0.082397 | 0.14191 | 61.8851 | 62.1689 | 124.7726 | 124.8688 | -0.07782 | 124.9237 | 62.0453 | -0.22431 | 124.8688 | -0.07782 | 62.0453 | 124.7726 | 124.9237 | -125.2258 | -125.2304
415.6406 | 125.3494 | -61.9125 | 63.0981 | -0.16304 | 0.0067013 | 0.010628 | 8.546e-06 | 0.063335 | -0.0031403 | 0.066676 | -61.9629 | 62.9608 | -62.1231 | -61.6653 | 62.9791 | -0.10071 | -0.073242 | 0.28381 | 62.9974 | -62.1368 | -0.21057 | -0.13733 | -0.050354 | 0.24719 | -0.11902 | -0.2243 | -0.10071 | 0.16022 | 61.8393 | 62.1964 | 124.8917 | 124.8734 | -0.050354 | 124.91 | 61.8118 | -0.2243 | 124.8734 | -0.050354 | 61.8118 | 124.8917 | 124.91 | -125.2213 | -125.235
416.6406 | 125.3494 | -61.8988 | 63.0798 | -0.15541 | 0.0084103 | 0.0082779 | -0.00020505 | 0.063335 | -0.0020721 | 0.065608 | -61.9492 | 62.9654 | -62.1002 | -61.615 | 63.121 | 0.004578 | -0.16022 | 0.35248 | 63.002 | -62.1506 | -0.20142 | -0.11444 | -0.050354 | 0.28381 | 0.041199 | -0.25177 | -0.07782 | 0.15106 | 61.7386 | 62.2513 | 125.0198 | 124.8642 | -0.050354 | 124.9008 | 61.9034 | -0.25177 | 124.8642 | -0.050354 | 61.9034 | 125.0198 | 124.9008 | -125.1801 | -125.2304
417.6406 | 125.2075 | -61.9034 | 63.1714 | -0.23933 | 0.0058469 | 0.0093459 | 0.0027855 | 0.06419 | -0.0012177 | 0.070948 | -62.0041 | 63.0432 | -62.1552 | -62.1002 | 62.8326 | 0.10529 | 0.10529 | 0.20599 | 63.0661 | -62.1414 | -0.25177 | -0.12817 | -0.10071 | -0.19684 | -0.33875 | -0.23804 | -0.10529 | 0.15106 | 62.0087 | 62.1094 | 124.736 | 124.9466 | -0.10071 | 124.9695 | 62.0087 | -0.23804 | 124.9466 | -0.10071 | 62.0087 | 124.736 | 124.9695 | -125.3265 | -125.3128
418.6406 | 125.3769 | -61.8988 | 63.0844 | -0.18593 | 0.0084103 | 0.010628 | -0.0014869 | 0.061412 | -0.0046357 | 0.069667 | -61.9629 | 62.9608 | -62.1323 | -62.114 | 62.5168 | -0.027466 | -0.045776 | 0.16022 | 62.9974 | -62.1368 | -0.23346 | -0.1236 | -0.064087 | -0.21515 | -0.56763 | -0.23804 | -0.086975 | 0.16937 | 61.853 | 62.059 | 124.4156 | 124.8596 | -0.064087 | 124.8962 | 61.8713 | -0.23804 | 124.8596 | -0.064087 | 61.8713 | 124.4156 | 124.8962 | -125.2167 | -125.2213
419.6406 | 125.3494 | -61.8896 | 63.1119 | -0.26222 | 0.0084103 | 0.011696 | 8.546e-06 | 0.065044 | -0.0016449 | 0.066676 | -61.9492 | 62.9974 | -62.1185 | -62.0361 | 62.8967 | 0.13733 | -0.004578 | 0.28381 | 63.0707 | -62.1368 | -0.22888 | -0.11444 | -0.05951 | -0.14648 | -0.21515 | -0.24719 | -0.041198 | 0.16937 | 61.8851 | 62.1735 | 124.7864 | 124.8871 | -0.05951 | 124.9603 | 62.027 | -0.24719 | 124.8871 | -0.05951 | 62.027 | 124.7864 | 124.9603 | -125.2304 | -125.2487
420.6406 | 125.3723 | -61.8988 | 63.1027 | -0.17067 | 0.0094785 | 0.016182 | 0.00064935 | 0.060985 | -0.00057686 | 0.06988 | -62.0041 | 63.0203 | -62.0773 | -62.1231 | 62.915 | 0.20599 | -0.11902 | 0.25177 | 63.002 | -62.1231 | -0.17853 | -0.082397 | -0.10529 | -0.2243 | -0.18768 | -0.2243 | -0.10071 | 0.073243 | 61.7798 | 62.1506 | 124.8138 | 124.9191 | -0.10529 | 124.9008 | 62.1048 | -0.2243 | 124.9191 | -0.10529 | 62.1048 | 124.8138 | 124.9008 | -125.1801 | -125.2258
421.6406 | 125.3174 | -61.9263 | 63.1531 | -0.22408 | 0.0077695 | 0.010841 | -0.0012733 | 0.063335 | 6.414e-05 | 0.070094 | -61.9446 | 62.97 | -62.1323 | -62.0224 | 62.8738 | 0.12817 | -0.013733 | 0.28839 | 63.0341 | -62.1368 | -0.20599 | -0.1831 | -0.01831 | -0.09613 | -0.27924 | -0.21057 | -0.11902 | 0.18768 | 61.9125 | 62.2147 | 124.8001 | 124.8962 | -0.01831 | 124.9603 | 62.0544 | -0.21057 | 124.8962 | -0.01831 | 62.0544 | 124.8001 | 124.9603 | -125.2853 | -125.2899
422.6406 | 125.267 | -61.9308 | 63.1302 | -0.094376 | 0.013965 | 0.015114 | 0.0070581 | 0.065685 | -0.0010041 | 0.06988 | -61.9583 | 63.089 | -62.1552 | -62.0819 | 62.796 | 0.050354 | 0.009155 | 0.14191 | 63.0524 | -62.1689 | -0.2243 | -0.041199 | -0.027466 | -0.15106 | -0.33417 | -0.23804 | -0.07782 | 0.19684 | 61.94 | 62.0728 | 124.7269 | 125.0198 | -0.027466 | 124.9832 | 61.9812 | -0.23804 | 125.0198 | -0.027466 | 61.9812 | 124.7269 | 124.9832 | -125.2853 | -125.2991
423.6406 | 125.3311 | -61.908 | 63.121 | -0.24696 | 0.0094785 | 0.01191 | -0.0027687 | 0.064617 | 0.0013457 | 0.069667 | -61.9766 | 62.9974 | -62.1414 | -62.0407 | 62.8784 | 0.14191 | 0.004578 | 0.27466 | 63.0661 | -62.1231 | -0.23346 | -0.1236 | -0.068665 | -0.13275 | -0.24261 | -0.21515 | -0.054932 | 0.16479 | 61.9125 | 62.1826 | 124.7864 | 124.9054 | -0.068665 | 124.9741 | 62.0499 | -0.21515 | 124.9054 | -0.068665 | 62.0499 | 124.7864 | 124.9741 | -125.2625 | -125.2441
424.6406 | 125.3403 | -61.908 | 63.0936 | -0.1783 | 0.0079831 | 0.011269 | 0.00022215 | 0.064403 | -0.00079046 | 0.070521 | -61.9583 | 62.9837 | -62.114 | -62.0361 | 62.883 | 0.14191 | 0.009155 | 0.27466 | 63.0432 | -62.114 | -0.20599 | -0.10986 | -0.050354 | -0.12817 | -0.21057 | -0.20599 | -0.050354 | 0.15564 | 61.9171 | 62.1826 | 124.791 | 124.8917 | -0.050354 | 124.9512 | 62.0499 | -0.20599 | 124.8917 | -0.050354 | 62.0499 | 124.791 | 124.9512 | -125.2075 | -125.2075
425.6406 | 125.3128 | -61.9171 | 63.1165 | -0.2317 | 0.0084103 | 0.010201 | 0.0015039 | 0.06419 | -0.0012177 | 0.069239 | -61.972 | 63.0203 | -62.1231 | -62.0407 | 62.8738 | 0.14648 | 0.004578 | 0.27008 | 63.0432 | -62.1552 | -0.20599 | -0.09613 | -0.054932 | -0.1236 | -0.24262 | -0.23804 | -0.073242 | 0.15106 | 61.9217 | 62.1872 | 124.791 | 124.9374 | -0.054932 | 124.9603 | 62.0636 | -0.23804 | 124.9374 | -0.054932 | 62.0636 | 124.791 | 124.9603 | -125.2396 | -125.2716
426.6406 | 125.235 | -61.94 | 63.176 | -0.21645 | 0.0090513 | 0.010414 | 0.0042809 | 0.064617 | -0.0016449 | 0.069453 | -62.0361 | 63.0478 | -62.1552 | -62.114 | 62.796 | 0.050354 | 0.14191 | 0.16022 | 63.0707 | -62.2009 | -0.21515 | -0.12817 | -0.096131 | -0.17395 | -0.37994 | -0.26093 | -0.10529 | 0.11902 | 62.0819 | 62.1002 | 124.736 | 124.9878 | -0.096131 | 125.0107 | 61.9904 | -0.26093 | 124.9878 | -0.096131 | 61.9904 | 124.736 | 125.0107 | -125.3311 | -125.3769
427.6406 | 125.2899 | -61.9446 | 63.1393 | -0.21645 | 0.011828 | 0.013832 | 0.0064171 | 0.066326 | -0.0012177 | 0.069239 | -61.9537 | 63.1027 | -62.1506 | -62.0682 | 62.8281 | 0.091553 | -0.29755 | 0.041199 | 63.0203 | -62.2147 | -0.20599 | -0.036621 | -0.009155 | -0.1236 | -0.31128 | -0.27008 | -0.11902 | 0.19684 | 61.647 | 61.9858 | 124.7726 | 125.0473 | -0.009155 | 124.9649 | 62.0361 | -0.27008 | 125.0473 | -0.009155 | 62.0361 | 124.7726 | 124.9649 | -125.2899 | -125.354
428.6406 | 125.235 | -61.9354 | 63.1348 | -0.26222 | 0.011188 | 0.012123 | 8.546e-06 | 0.066112 | -0.0029267 | 0.069239 | -62.0224 | 63.0112 | -62.1323 | -62.1002 | 62.8189 | 0.082397 | 0.1236 | 0.19684 | 63.0936 | -62.1323 | -0.19684 | -0.1236 | -0.086975 | -0.16479 | -0.31586 | -0.19684 | -0.041199 | 0.10986 | 62.059 | 62.1323 | 124.7543 | 124.9466 | -0.086975 | 125.029 | 62.0178 | -0.19684 | 124.9466 | -0.086975 | 62.0178 | 124.7543 | 125.029 | -125.267 | -125.267
429.6406 | 125.2716 | -61.9171 | 63.1439 | -0.25459 | 0.0086239 | 0.011696 | -0.00020505 | 0.065044 | -0.0022859 | 0.069667 | -62.0041 | 63.0386 | -62.1323 | -62.1185 | 62.8052 | 0.086975 | 0.11902 | 0.18768 | 63.0981 | -62.1277 | -0.21515 | -0.10529 | -0.086975 | -0.20142 | -0.33874 | -0.21057 | -0.045776 | 0.12817 | 62.0361 | 62.1048 | 124.7223 | 124.9557 | -0.086975 | 125.0153 | 62.0041 | -0.21057 | 124.9557 | -0.086975 | 62.0041 | 124.7223 | 125.0153 | -125.2762 | -125.2716
430.6406 | 125.2304 | -61.9263 | 63.1393 | -0.29274 | 0.010333 | 0.012123 | 0.0015039 | 0.064403 | -0.0020721 | 0.068171 | -62.0087 | 63.0386 | -62.1414 | -62.1185 | 62.8235 | 0.086975 | 0.13275 | 0.20599 | 63.0936 | -62.1597 | -0.21515 | -0.10071 | -0.082397 | -0.19226 | -0.31586 | -0.23346 | -0.045776 | 0.13275 | 62.059 | 62.1323 | 124.7498 | 124.9649 | -0.082397 | 125.0198 | 62.0132 | -0.23346 | 124.9649 | -0.082397 | 62.0132 | 124.7498 | 125.0198 | -125.2808 | -125.2991
431.6406 | 125.2487 | -61.9308 | 63.1439 | -0.26222 | 0.0092649 | 0.010414 | 0.0017175 | 0.063121 | -0.0020721 | 0.071376 | -61.9904 | 63.0386 | -62.1323 | -62.1002 | 62.8372 | 0.091553 | 0.09613 | 0.19226 | 63.0661 | -62.146 | -0.20142 | -0.10529 | -0.059509 | -0.16937 | -0.3067 | -0.21515 | -0.07782 | 0.14191 | 62.027 | 62.1231 | 124.7681 | 124.9695 | -0.059509 | 124.9969 | 62.0224 | -0.21515 | 124.9695 | -0.059509 | 62.0224 | 124.7681 | 124.9969 | -125.2762 | -125.2899
432.6406 | 125.2121 | -61.9446 | 63.1348 | -0.063858 | 0.011828 | 0.015114 | 0.0059899 | 0.065899 | -0.0029267 | 0.069667 | -61.9949 | 63.0844 | -62.146 | -62.1231 | 62.7686 | 0.022888 | 0.018311 | 0.082397 | 63.0432 | -62.233 | -0.20142 | -0.050354 | -0.050354 | -0.17853 | -0.36621 | -0.28839 | -0.091553 | 0.15106 | 61.9629 | 62.027 | 124.7131 | 125.029 | -0.050354 | 124.9878 | 61.9675 | -0.28839 | 125.029 | -0.050354 | 61.9675 | 124.7131 | 124.9878 | -125.2808 | -125.3677
433.6406 | 125.267 | -61.9263 | 63.1531 | -0.26985 | 0.0092649 | 0.011269 | -0.0019141 | 0.065685 | -0.0014313 | 0.072017 | -61.9858 | 63.0478 | -62.1231 | -62.0819 | 62.8464 | 0.12817 | 0.10986 | 0.21973 | 63.0478 | -62.1597 | -0.19684 | -0.10529 | -0.059509 | -0.15564 | -0.3067 | -0.23346 | -0.10529 | 0.13733 | 62.0361 | 62.146 | 124.7726 | 124.9741 | -0.059509 | 124.9741 | 62.0544 | -0.23346 | 124.9741 | -0.059509 | 62.0544 | 124.7726 | 124.9741 | -125.2762 | -125.3128
434.6406 | 125.235 | -61.94 | 63.1531 | -0.25459 | 0.011401 | 0.012764 | 0.0012903 | 0.068035 | -0.0014313 | 0.069453 | -62.0453 | 63.0753 | -62.1643 | -62.1414 | 62.7411 | 0.022888 | 0.16479 | 0.14191 | 63.0981 | -62.1964 | -0.22431 | -0.07782 | -0.10529 | -0.20142 | -0.41199 | -0.25635 | -0.054931 | 0.11902 | 62.1048 | 62.0819 | 124.6811 | 125.0153 | -0.10529 | 125.0381 | 61.9629 | -0.25635 | 125.0153 | -0.10529 | 61.9629 | 124.6811 | 125.0381 | -125.3174 | -125.3494
435.6406 | 125.2441 | -61.9354 | 63.1302 | -0.21645 | 0.0096921 | 0.011482 | 0.0025719 | 0.065044 | -0.0063447 | 0.072444 | -62.0453 | 63.0707 | -62.1414 | -62.1872 | 62.6266 | -0.10071 | 0.16937 | 0.10071 | 63.089 | -62.2101 | -0.20599 | -0.059509 | -0.10986 | -0.25177 | -0.50354 | -0.27466 | -0.041199 | 0.09613 | 62.1048 | 62.0361 | 124.5621 | 125.0061 | -0.10986 | 125.0244 | 61.8347 | -0.27466 | 125.0061 | -0.10986 | 61.8347 | 124.5621 | 125.0244 | -125.2716 | -125.3403
436.6406 | 125.235 | -61.9263 | 63.1302 | -0.19356 | 0.0099057 | 0.0082779 | 8.546e-06 | 0.065044 | -0.0024995 | 0.068599 | -62.059 | 63.0615 | -62.1689 | -62.1277 | 62.7457 | 0.24719 | 0.17395 | -0.032043 | 63.1165 | -62.178 | -0.24261 | -0.068665 | -0.13275 | -0.20142 | -0.38452 | -0.25177 | -0.013733 | 0.10986 | 62.1002 | 61.8942 | 124.6719 | 124.9878 | -0.13275 | 125.0427 | 62.1735 | -0.25177 | 124.9878 | -0.13275 | 62.1735 | 124.6719 | 125.0427 | -125.2991 | -125.3082
437.6406 | 125.2304 | -61.9263 | 63.1348 | -0.010452 | 0.011828 | 0.0095595 | 0.0064171 | 0.066326 | -0.0014313 | 0.068171 | -61.9812 | 63.0661 | -62.1368 | -62.1185 | 62.8052 | 0.036621 | 0.018311 | 0.12817 | 63.0615 | -62.1918 | -0.21057 | -0.068665 | -0.054931 | -0.19226 | -0.32959 | -0.2655 | -0.073243 | 0.15564 | 61.9446 | 62.0544 | 124.7314 | 124.9924 | -0.054931 | 124.9878 | 61.9629 | -0.2655 | 124.9924 | -0.054931 | 61.9629 | 124.7314 | 124.9878 | -125.2716 | -125.3265
438.6406 | 125.1938 | -61.9492 | 63.1348 | -0.27748 | 0.0092649 | 0.013191 | 0.00022215 | 0.06718 | -0.00036306 | 0.067744 | -62.0132 | 63.0753 | -62.1643 | -62.1368 | 62.8006 | 0.068665 | 0.13733 | 0.17395 | 63.1073 | -62.1597 | -0.21515 | -0.05951 | -0.064087 | -0.18768 | -0.33417 | -0.21057 | -0.027466 | 0.15106 | 62.0865 | 62.1231 | 124.7498 | 125.0244 | -0.064087 | 125.0565 | 62.0178 | -0.21057 | 125.0244 | -0.064087 | 62.0178 | 124.7498 | 125.0565 | -125.2991 | -125.2945
439.6406 | 125.2213 | -61.9492 | 63.1577 | -0.04097 | 0.011615 | 0.012123 | 0.0010767 | 0.06718 | -0.00057686 | 0.068812 | -62.0316 | 63.0707 | -62.1597 | -62.1368 | 62.7914 | 0.054932 | 0.15106 | 0.15106 | 63.0936 | -62.1597 | -0.21057 | -0.086975 | -0.082397 | -0.18768 | -0.36621 | -0.21057 | -0.064087 | 0.12817 | 62.1002 | 62.1002 | 124.7406 | 125.0198 | -0.082397 | 125.0427 | 62.0041 | -0.21057 | 125.0198 | -0.082397 | 62.0041 | 124.7406 | 125.0427 | -125.3174 | -125.3174
440.6406 | 125.2258 | -61.9263 | 63.1439 | -0.29274 | 0.0090513 | 0.011482 | -0.00041865 | 0.066112 | 0.0013457 | 0.068599 | -61.9904 | 63.0249 | -62.1552 | -62.1094 | 62.8098 | 0.073242 | 0.14648 | 0.20599 | 63.089 | -62.1597 | -0.22888 | -0.11902 | -0.064086 | -0.1831 | -0.33417 | -0.23346 | -0.054932 | 0.16479 | 62.0728 | 62.1323 | 124.736 | 124.9512 | -0.064086 | 125.0153 | 61.9995 | -0.23346 | 124.9512 | -0.064086 | 61.9995 | 124.736 | 125.0153 | -125.2991 | -125.3037
441.6406 | 125.2396 | -61.94 | 63.1393 | -0.25459 | 0.0064877 | 0.0095595 | -0.00041865 | 0.065685 | -0.0016449 | 0.069239 | -61.8301 | 63.1073 | -62.1552 | -62.1185 | 62.7823 | 0.036621 | 0.13275 | 0.16937 | 63.0936 | -62.1735 | -0.21515 | -0.032043 | 0.10986 | -0.17853 | -0.35705 | -0.23346 | -0.045776 | 0.32501 | 62.0728 | 62.1094 | 124.7223 | 125.0473 | 0.10986 | 125.0336 | 61.9766 | -0.23346 | 125.0473 | 0.10986 | 61.9766 | 124.7223 | 125.0336 | -125.2945 | -125.3128
442.6406 | 125.235 | -61.9766 | 63.1348 | -0.056229 | 0.012469 | 0.013832 | 0.0070581 | 0.067394 | -0.00079046 | 0.067744 | -61.9812 | 63.1073 | -62.1368 | -62.1185 | 62.7869 | 0.027466 | 0.022888 | 0.11444 | 63.0569 | -62.2147 | -0.16022 | -0.027466 | -0.004577 | -0.14191 | -0.3479 | -0.23804 | -0.07782 | 0.15564 | 61.9995 | 62.0911 | 124.7635 | 125.0839 | -0.004577 | 125.0336 | 62.0041 | -0.23804 | 125.0839 | -0.004577 | 62.0041 | 124.7635 | 125.0336 | -125.2716 | -125.3494
443.6406 | 125.1938 | -61.9217 | 63.1027 | -0.1783 | 0.010547 | 0.016396 | -0.0029823 | 0.066539 | 0.00070494 | 0.068385 | -62.0407 | 63.0432 | -62.1643 | -62.1368 | 62.796 | 0.068665 | 0.21515 | 0.40283 | 63.1531 | -62.1414 | -0.24262 | -0.059509 | -0.11902 | -0.21515 | -0.3067 | -0.21973 | 0.050354 | 0.1236 | 62.1368 | 62.3245 | 124.7177 | 124.9649 | -0.11902 | 125.0748 | 61.9904 | -0.21973 | 124.9649 | -0.11902 | 61.9904 | 124.7177 | 125.0748 | -125.267 | -125.2441
444.6406 | 125.2533 | -61.9446 | 63.1393 | -0.30037 | 0.0088375 | 0.0091323 | -0.0017005 | 0.064617 | -0.0016449 | 0.068812 | -62.0316 | 63.0432 | -62.1231 | -62.1368 | 62.7823 | 0.064087 | 0.14648 | 0.17853 | 63.0844 | -62.1689 | -0.17853 | -0.09613 | -0.086975 | -0.19226 | -0.35705 | -0.2243 | -0.054931 | 0.091553 | 62.0911 | 62.1231 | 124.7269 | 124.9878 | -0.086975 | 125.029 | 62.0087 | -0.2243 | 124.9878 | -0.086975 | 62.0087 | 124.7269 | 125.029 | -125.2625 | -125.3082
445.6406 | 125.235 | -61.94 | 63.121 | -0.24696 | 0.0069149 | 0.012337 | -0.0010597 | 0.06419 | -0.00014946 | 0.069667 | -62.0087 | 63.0615 | -62.146 | -62.1048 | 62.796 | 0.086975 | 0.13733 | 0.19226 | 63.0753 | -62.1643 | -0.20599 | -0.05951 | -0.068665 | -0.16479 | -0.32501 | -0.22431 | -0.045777 | 0.13733 | 62.0773 | 62.1323 | 124.736 | 125.0015 | -0.068665 | 125.0153 | 62.027 | -0.22431 | 125.0015 | -0.068665 | 62.027 | 124.736 | 125.0153 | -125.267 | -125.2853
446.6406 | 125.2121 | -61.9308 | 63.1302 | -2.5816 | 0.010333 | 0.014259 | 0.0021447 | 0.064617 | -0.0020721 | 0.068812 | -62.1048 | 63.0936 | -62.1872 | -62.1552 | 62.7548 | 0.045776 | 0.17853 | 0.16479 | 63.0661 | -62.1735 | -0.25635 | -0.036621 | -0.17395 | -0.2243 | -0.37537 | -0.24262 | -0.064087 | 0.082398 | 62.1094 | 62.0956 | 124.6857 | 125.0244 | -0.17395 | 124.9969 | 61.9766 | -0.24262 | 125.0244 | -0.17395 | 61.9766 | 124.6857 | 124.9969 | -125.3174 | -125.3037
447.6406 | 125.2258 | -61.9766 | 63.1393 | 0.012436 | 0.010974 | 0.01191 | 0.0040673 | 0.067821 | -0.00036306 | 0.069026 | -62.0224 | 63.1073 | -62.1689 | -62.178 | 62.7182 | -0.041199 | 0.036621 | 0.041199 | 63.0844 | -62.2147 | -0.19226 | -0.032043 | -0.045776 | -0.20142 | -0.42114 | -0.23804 | -0.054931 | 0.14648 | 62.0132 | 62.0178 | 124.6948 | 125.0839 | -0.045776 | 125.061 | 61.9354 | -0.23804 | 125.0839 | -0.045776 | 61.9354 | 124.6948 | 125.061 | -125.3082 | -125.354
448.6406 | 125.3174 | -61.9308 | 63.1302 | -0.2317 | 0.0092649 | 0.012123 | -0.0023413 | 0.065044 | -0.00036306 | 0.068385 | -61.9766 | 63.0157 | -62.1506 | -62.0544 | 62.8601 | 0.13733 | 0.045776 | 0.2655 | 63.089 | -62.1506 | -0.21973 | -0.11444 | -0.045777 | -0.1236 | -0.27008 | -0.21973 | -0.041199 | 0.17395 | 61.9766 | 62.1964 | 124.791 | 124.9466 | -0.045777 | 125.0198 | 62.0682 | -0.21973 | 124.9466 | -0.045777 | 62.0682 | 124.791 | 125.0198 | -125.2808 | -125.2808
449.6406 | 125.2258 | -61.9308 | 63.1302 | -0.23933 | 0.01076 | 0.0072097 | -0.00041865 | 0.063335 | -0.0035675 | 0.068812 | -62.027 | 63.0341 | -62.2101 | -62.1231 | 62.796 | 0.082397 | 0.13275 | 0.16937 | 63.0936 | -62.1643 | -0.27924 | -0.09613 | -0.096131 | -0.19226 | -0.33417 | -0.23346 | -0.036621 | 0.1831 | 62.0636 | 62.1002 | 124.7269 | 124.9649 | -0.096131 | 125.0244 | 62.0132 | -0.23346 | 124.9649 | -0.096131 | 62.0132 | 124.7269 | 125.0244 | -125.3403 | -125.2945
450.6406 | 125.2304 | -61.9308 | 63.1485 | -0.50636 | 0.010119 | 0.011269 | 0.0017175 | 0.065044 | 0.00070494 | 0.069026 | -62.0636 | 63.0661 | -62.1735 | -62.1368 | 62.7823 | 0.064087 | 0.15564 | 0.15564 | 63.0798 | -62.1872 | -0.24262 | -0.082398 | -0.13275 | -0.20599 | -0.36621 | -0.25635 | -0.068665 | 0.10986 | 62.0865 | 62.0865 | 124.7131 | 124.9969 | -0.13275 | 125.0107 | 61.9949 | -0.25635 | 124.9969 | -0.13275 | 61.9949 | 124.7131 | 125.0107 | -125.322 | -125.3357
451.6406 | 125.2441 | -61.9217 | 63.121 | -0.23933 | 0.0084103 | 0.0057143 | 0.0017175 | 0.065044 | -0.0010041 | 0.067958 | -62.0178 | 63.0341 | -62.1185 | -62.114 | 62.8235 | 0.09613 | 0.10986 | 0.20142 | 63.089 | -62.1552 | -0.19684 | -0.086975 | -0.09613 | -0.19226 | -0.29755 | -0.23346 | -0.032044 | 0.10071 | 62.0316 | 62.1231 | 124.7452 | 124.9557 | -0.09613 | 125.0107 | 62.0178 | -0.23346 | 124.9557 | -0.09613 | 62.0178 | 124.7452 | 125.0107 | -125.2396 | -125.2762
452.6406 | 125.1984 | -61.9583 | 63.1119 | 0.020065 | 0.010333 | 0.014473 | 0.0057763 | 0.06718 | 0.00091854 | 0.069453 | -62.0316 | 63.089 | -62.178 | -62.1689 | 62.7274 | -0.027466 | 0.022888 | 0.036621 | 63.0981 | -62.2375 | -0.21973 | -0.022888 | -0.073242 | -0.21057 | -0.38452 | -0.27924 | -0.013732 | 0.14649 | 61.9812 | 61.9949 | 124.6857 | 125.0473 | -0.073242 | 125.0565 | 61.9308 | -0.27924 | 125.0473 | -0.073242 | 61.9308 | 124.6857 | 125.0565 | -125.2899 | -125.3494
453.6406 | 125.1709 | -61.9308 | 63.1302 | -0.23933 | 0.010333 | 0.013191 | 0.0012903 | 0.063976 | -0.0035675 | 0.068385 | -62.027 | 63.0524 | -62.1643 | -62.1231 | 62.7777 | 0.050354 | 0.22888 | 0.41657 | 63.1302 | -62.1552 | -0.23346 | -0.07782 | -0.096131 | -0.19226 | -0.35248 | -0.2243 | 0 | 0.13733 | 62.1597 | 62.3474 | 124.7086 | 124.9832 | -0.096131 | 125.061 | 61.9812 | -0.2243 | 124.9832 | -0.096131 | 61.9812 | 124.7086 | 125.061 | -125.2945 | -125.2853
454.6406 | 125.2991 | -61.8988 | 63.1073 | -0.20119 | 0.011188 | 0.0099869 | -0.00063225 | 0.065471 | -0.0010041 | 0.067103 | -61.9812 | 63.0249 | -62.1185 | -62.0407 | 62.8601 | 0.14191 | 0.018311 | 0.27008 | 63.0615 | -62.1185 | -0.21973 | -0.082398 | -0.082397 | -0.14191 | -0.24719 | -0.21973 | -0.045777 | 0.13733 | 61.9171 | 62.1689 | 124.7589 | 124.9237 | -0.082397 | 124.9603 | 62.0407 | -0.21973 | 124.9237 | -0.082397 | 62.0407 | 124.7589 | 124.9603 | -125.2258 | -125.2258
455.6406 | 125.3265 | -61.8896 | 63.0981 | -0.25459 | 0.0084103 | 0.01191 | 0.00043575 | 0.065044 | -0.0027131 | 0.067744 | -61.9675 | 62.9974 | -62.1231 | -62.0453 | 62.8738 | 0.14648 | 0.004578 | 0.27466 | 63.0615 | -62.1414 | -0.23346 | -0.10071 | -0.07782 | -0.15564 | -0.22431 | -0.25177 | -0.036622 | 0.15564 | 61.8942 | 62.1643 | 124.7635 | 124.8871 | -0.07782 | 124.9512 | 62.0361 | -0.25177 | 124.8871 | -0.07782 | 62.0361 | 124.7635 | 124.9512 | -125.2213 | -125.2396
456.6406 | 125.2899 | -61.9217 | 63.1485 | -0.31563 | 0.0086239 | 0.0078507 | 0.00043575 | 0.06483 | -0.0010041 | 0.067531 | -61.9858 | 62.9745 | -62.1231 | -62.0773 | 62.8281 | 0.11902 | 0.091553 | 0.23346 | 63.0478 | -62.1643 | -0.20142 | -0.17395 | -0.064087 | -0.15564 | -0.32044 | -0.24262 | -0.10071 | 0.13733 | 62.0132 | 62.1552 | 124.7498 | 124.8962 | -0.064087 | 124.9695 | 62.0407 | -0.24262 | 124.8962 | -0.064087 | 62.0407 | 124.7498 | 124.9695 | -125.2716 | -125.3128
457.6406 | 125.148 | -61.9263 | 63.1393 | -0.2317 | 0.010333 | 0.0080643 | 0.0019311 | 0.062694 | 0.0013457 | 0.069239 | -62.0453 | 63.0478 | -62.1506 | -62.1231 | 62.7731 | 0.045776 | 0.13275 | 0.36163 | 63.0798 | -62.146 | -0.2243 | -0.091552 | -0.11902 | -0.19684 | -0.36621 | -0.21973 | -0.059509 | 0.10529 | 62.059 | 62.2879 | 124.6994 | 124.9741 | -0.11902 | 125.0061 | 61.972 | -0.21973 | 124.9741 | -0.11902 | 61.972 | 124.6994 | 125.0061 | -125.2899 | -125.2853
458.6406 | 125.2075 | -61.9263 | 63.1714 | -0.24696 | 0.0079831 | 0.012764 | 0.00064935 | 0.066112 | -0.0014313 | 0.067531 | -62.0178 | 63.0615 | -62.1323 | -62.1002 | 62.7914 | 0.068665 | 0.11902 | 0.18768 | 63.0936 | -62.1597 | -0.20599 | -0.10986 | -0.091552 | -0.17395 | -0.37994 | -0.23346 | -0.07782 | 0.11444 | 62.0453 | 62.114 | 124.7177 | 124.9878 | -0.091552 | 125.0198 | 61.9949 | -0.23346 | 124.9878 | -0.091552 | 61.9949 | 124.7177 | 125.0198 | -125.3037 | -125.3311
459.6406 | 125.3128 | -61.8896 | 63.121 | -0.27748 | 0.0092649 | 0.012764 | -0.00084605 | 0.063762 | -0.0027131 | 0.067744 | -61.9629 | 63.0249 | -62.1185 | -62.0361 | 62.8693 | 0.15106 | -0.018311 | 0.27466 | 63.0478 | -62.1185 | -0.22888 | -0.096131 | -0.073243 | -0.14648 | -0.25177 | -0.22888 | -0.073242 | 0.15564 | 61.8713 | 62.1643 | 124.7589 | 124.9145 | -0.073243 | 124.9374 | 62.0407 | -0.22888 | 124.9145 | -0.073243 | 62.0407 | 124.7589 | 124.9374 | -125.2396 | -125.2396
460.6406 | 125.2167 | -61.9492 | 63.1439 | -0.2317 | 0.0096921 | 0.012337 | 0.00086295 | 0.062908 | -0.0012177 | 0.071589 | -62.0544 | 63.0661 | -62.1506 | -62.2238 | 62.7411 | 0.082397 | 0.07782 | 0.15564 | 63.089 | -62.1964 | -0.20142 | -0.07782 | -0.10529 | -0.27466 | -0.40283 | -0.24719 | -0.054932 | 0.096131 | 62.027 | 62.1048 | 124.6902 | 125.0153 | -0.10529 | 125.0381 | 62.0316 | -0.24719 | 125.0153 | -0.10529 | 62.0316 | 124.6902 | 125.0381 | -125.2945 | -125.3403
461.6406 | 125.3494 | -61.908 | 63.1073 | -0.033341 | 0.0079831 | 0.0080643 | -0.00020505 | 0.065044 | -0.0024995 | 0.069026 | -61.9217 | 62.9608 | -62.146 | -62.0224 | 62.883 | 0.16022 | -0.036621 | 0.28839 | 63.0341 | -62.1323 | -0.23804 | -0.14649 | -0.013733 | -0.11444 | -0.2243 | -0.2243 | -0.073242 | 0.2243 | 61.8713 | 62.1963 | 124.791 | 124.8688 | -0.013733 | 124.942 | 62.0682 | -0.2243 | 124.8688 | -0.013733 | 62.0682 | 124.791 | 124.942 | -125.2533 | -125.2396
462.6406 | 125.2213 | -61.9629 | 63.1302 | -0.52925 | 0.0096921 | 0.011055 | 0.0023583 | 0.063549 | 0.00070494 | 0.067103 | -62.0773 | 63.0798 | -62.1414 | -62.1277 | 62.7457 | 0.045776 | 0.13275 | 0.16022 | 63.0936 | -62.1918 | -0.17853 | -0.050354 | -0.11444 | -0.16479 | -0.38452 | -0.22888 | -0.036621 | 0.064086 | 62.0956 | 62.1231 | 124.7086 | 125.0427 | -0.11444 | 125.0565 | 62.0087 | -0.22888 | 125.0427 | -0.11444 | 62.0087 | 124.7086 | 125.0565 | -125.2716 | -125.322
463.6406 | 125.3357 | -61.9217 | 63.1027 | -0.20119 | 0.0084103 | 0.013405 | -0.0017005 | 0.063976 | -0.0020721 | 0.066676 | -61.9492 | 62.9791 | -62.1277 | -62.0224 | 62.8876 | 0.15564 | -0.022888 | 0.27008 | 63.0524 | -62.1414 | -0.20599 | -0.1236 | -0.027466 | -0.10071 | -0.21515 | -0.21973 | -0.050354 | 0.17853 | 61.8988 | 62.1918 | 124.8093 | 124.9008 | -0.027466 | 124.9741 | 62.0773 | -0.21973 | 124.9008 | -0.027466 | 62.0773 | 124.8093 | 124.9741 | -125.2304 | -125.2441
464.6406 | 125.3632 | -61.8988 | 63.1119 | -0.14778 | 0.0090513 | 0.0076369 | 0.00043575 | 0.062053 | -0.0014313 | 0.070094 | -61.9537 | 62.9929 | -62.1277 | -62.0178 | 62.8738 | 0.16022 | -0.050354 | 0.28839 | 63.0432 | -62.146 | -0.22888 | -0.11902 | -0.054931 | -0.11902 | -0.23804 | -0.24719 | -0.068664 | 0.17395 | 61.8484 | 62.1872 | 124.7726 | 124.8917 | -0.054931 | 124.942 | 62.059 | -0.24719 | 124.8917 | -0.054931 | 62.059 | 124.7726 | 124.942 | -125.2396 | -125.2579
465.6406 | 125.3815 | -61.8713 | 63.089 | -0.61317 | 0.0081967 | 0.0078507 | -0.0014869 | 0.063335 | -0.0020721 | 0.068171 | -61.9766 | 62.9654 | -62.1323 | -62.027 | 62.8738 | 0.16479 | -0.045776 | 0.28381 | 63.0432 | -62.114 | -0.26093 | -0.1236 | -0.10529 | -0.15564 | -0.21515 | -0.24262 | -0.045776 | 0.15564 | 61.8256 | 62.1552 | 124.7452 | 124.8367 | -0.10529 | 124.9146 | 62.0361 | -0.24262 | 124.8367 | -0.10529 | 62.0361 | 124.7452 | 124.9146 | -125.2213 | -125.2029
466.6406 | 125.3265 | -61.9034 | 63.0936 | -0.25459 | 0.0090513 | 0.01191 | 0.0021447 | 0.063121 | 0.00049134 | 0.069667 | -61.9583 | 62.9837 | -62.1231 | -62.0041 | 62.8693 | 0.15106 | -0.018311 | 0.27924 | 63.0478 | -62.1414 | -0.21973 | -0.10986 | -0.054932 | -0.10071 | -0.2243 | -0.23804 | -0.045776 | 0.1648 | 61.8851 | 62.1826 | 124.7726 | 124.8871 | -0.054932 | 124.9512 | 62.0544 | -0.23804 | 124.8871 | -0.054932 | 62.0544 | 124.7726 | 124.9512 | -125.2167 | -125.235
467.6406 | 125.2167 | -61.9354 | 63.1073 | -0.24696 | 0.010974 | 0.013619 | 0.0085535 | 0.064403 | -0.0012177 | 0.067744 | -61.9125 | 63.0707 | -62.1597 | -62.0499 | 62.8143 | 0.064087 | 0.027466 | 0.15106 | 63.0707 | -62.1964 | -0.2243 | -0.036621 | 0.022888 | -0.11444 | -0.29297 | -0.26093 | -0.036621 | 0.24719 | 61.9629 | 62.0865 | 124.7498 | 125.0061 | 0.022888 | 125.0061 | 61.9995 | -0.26093 | 125.0061 | 0.022888 | 61.9995 | 124.7498 | 125.0061 | -125.267 | -125.3037
468.6406 | 125.3265 | -61.8713 | 63.0936 | -0.1783 | 0.010333 | 0.01191 | -0.0010597 | 0.062694 | -0.00057686 | 0.06988 | -61.9812 | 62.9608 | -62.1277 | -62.027 | 62.8876 | 0.16022 | -0.091553 | 0.27008 | 63.0203 | -62.1277 | -0.25635 | -0.13275 | -0.10986 | -0.15564 | -0.20599 | -0.25635 | -0.073242 | 0.14648 | 61.7798 | 62.1414 | 124.7589 | 124.8322 | -0.10986 | 124.8917 | 62.0316 | -0.25635 | 124.8322 | -0.10986 | 62.0316 | 124.7589 | 124.8917 | -125.2213 | -125.2213
469.6406 | 125.3494 | -61.8942 | 63.1119 | -0.094376 | 0.0077695 | 0.011055 | -0.00063225 | 0.063762 | -0.0012177 | 0.069239 | -61.9904 | 62.9837 | -62.1231 | -62.0499 | 62.8555 | 0.12817 | -0.059509 | 0.2655 | 63.0341 | -62.1323 | -0.22888 | -0.12817 | -0.09613 | -0.15564 | -0.25635 | -0.23804 | -0.077819 | 0.13275 | 61.8347 | 62.1597 | 124.7498 | 124.8779 | -0.09613 | 124.9283 | 62.0224 | -0.23804 | 124.8779 | -0.09613 | 62.0224 | 124.7498 | 124.9283 | -125.235 | -125.2441
470.6406 | 125.3311 | -61.8851 | 63.1302 | -0.14015 | 0.0090513 | 0.0012283 | -0.0034095 | 0.063121 | 0.0028411 | 0.068599 | -61.5601 | 63.0432 | -62.0956 | -62.0132 | 62.9379 | 0.16937 | -0.11444 | 0.3067 | 62.9974 | -62.1552 | -0.21057 | -0.086975 | 0.32501 | -0.12817 | -0.19226 | -0.27008 | -0.13275 | 0.53558 | 61.7706 | 62.1918 | 124.823 | 124.9283 | 0.32501 | 124.8825 | 62.0544 | -0.27008 | 124.9283 | 0.32501 | 62.0544 | 124.823 | 124.8825 | -125.2258 | -125.2853
471.6406 | 125.3677 | -61.9171 | 63.0798 | -0.17067 | 0.0088375 | 0.0067825 | 0.00043575 | 0.060772 | -0.0084809 | 0.068599 | -61.9583 | 62.9654 | -62.1231 | -61.7706 | 62.5717 | -0.12817 | 0.054932 | 0.21515 | 62.9974 | -62.1277 | -0.20599 | -0.11444 | -0.041199 | 0.14648 | -0.50812 | -0.21057 | -0.082397 | 0.1648 | 61.972 | 62.1323 | 124.4888 | 124.8825 | -0.041199 | 124.9146 | 61.7889 | -0.21057 | 124.8825 | -0.041199 | 61.7889 | 124.4888 | 124.9146 | -125.2029 | -125.2075
472.6406 | 125.2762 | -61.8942 | 63.1485 | -0.21645 | 0.010119 | 0.0097733 | 0.0032129 | 0.061626 | -0.0029267 | 0.068812 | -61.9629 | 63.0112 | -62.1277 | -62.0773 | 62.8235 | 0.11902 | 0.050354 | 0.22888 | 63.0524 | -62.1506 | -0.23346 | -0.13733 | -0.068665 | -0.18311 | -0.32501 | -0.25635 | -0.096131 | 0.16479 | 61.9446 | 62.1231 | 124.7177 | 124.9054 | -0.068665 | 124.9466 | 62.0132 | -0.25635 | 124.9054 | -0.068665 | 62.0132 | 124.7177 | 124.9466 | -125.2762 | -125.2991
473.6406 | 125.3448 | -61.8805 | 63.0844 | -0.12489 | 0.0081967 | 0.0093459 | -0.00084605 | 0.06184 | 0.00049134 | 0.069026 | -61.9492 | 62.9425 | -62.1414 | -61.9995 | 62.8876 | 0.15564 | -0.050354 | 0.31128 | 63.0249 | -62.1597 | -0.26093 | -0.14191 | -0.068665 | -0.11902 | -0.19684 | -0.27924 | -0.05951 | 0.19226 | 61.8301 | 62.1918 | 124.7681 | 124.823 | -0.068665 | 124.9054 | 62.0361 | -0.27924 | 124.823 | -0.068665 | 62.0361 | 124.7681 | 124.9054 | -125.2258 | -125.2441
474.6406 | 125.354 | -61.853 | 63.089 | -0.40718 | 0.0077695 | 0.012978 | 0.00043575 | 0.063976 | -0.00079046 | 0.067744 | -61.9858 | 62.9517 | -62.1368 | -62.0132 | 62.883 | 0.16937 | -0.036621 | 0.27008 | 63.0157 | -62.1231 | -0.28381 | -0.13733 | -0.13275 | -0.16022 | -0.20599 | -0.27008 | -0.073242 | 0.15106 | 61.8164 | 62.1231 | 124.736 | 124.8047 | -0.13275 | 124.8688 | 62.0224 | -0.27008 | 124.8047 | -0.13275 | 62.0224 | 124.736 | 124.8688 | -125.2258 | -125.2121
475.6406 | 125.3403 | -61.8988 | 63.0753 | -0.11726 | 0.0081967 | 0.0095595 | -0.0019141 | 0.062267 | -0.0016449 | 0.069026 | -61.972 | 62.9837 | -62.1323 | -62.0453 | 62.883 | 0.1236 | -0.07782 | 0.26093 | 63.0112 | -62.1506 | -0.23346 | -0.091552 | -0.073242 | -0.14648 | -0.19226 | -0.25177 | -0.064087 | 0.16022 | 61.821 | 62.1597 | 124.7818 | 124.8825 | -0.073242 | 124.91 | 62.0224 | -0.25177 | 124.8825 | -0.073242 | 62.0224 | 124.7818 | 124.91 | -125.2075 | -125.2258
476.6406 | 125.3128 | -61.8942 | 63.0936 | -0.10963 | 0.0079831 | 0.013832 | -0.00020505 | 0.063976 | -0.0022859 | 0.066249 | -61.9858 | 62.97 | -62.1277 | -62.027 | 62.8601 | 0.1236 | -0.068665 | 0.23804 | 63.0112 | -62.1277 | -0.23346 | -0.1236 | -0.091553 | -0.13275 | -0.23346 | -0.23346 | -0.082398 | 0.14191 | 61.8256 | 62.1323 | 124.7543 | 124.8642 | -0.091553 | 124.9054 | 62.0178 | -0.23346 | 124.8642 | -0.091553 | 62.0178 | 124.7543 | 124.9054 | -125.2213 | -125.2213
477.6406 | 125.2075 | -61.9263 | 63.1485 | -0.49873 | 0.01076 | 0.013832 | 0.0032129 | 0.063335 | -0.0012177 | 0.070948 | -62.0544 | 63.0478 | -62.1597 | -62.1002 | 62.7686 | 0.045776 | 0.14648 | 0.14648 | 63.0707 | -62.1643 | -0.23346 | -0.10071 | -0.12817 | -0.17395 | -0.37994 | -0.23804 | -0.07782 | 0.10529 | 62.0728 | 62.0728 | 124.6948 | 124.9741 | -0.12817 | 124.9969 | 61.972 | -0.23804 | 124.9741 | -0.12817 | 61.972 | 124.6948 | 124.9969 | -125.3082 | -125.3128
478.6406 | 125.3403 | -61.8851 | 63.1027 | -0.11726 | 0.0071285 | 0.012337 | -0.0014869 | 0.059917 | -0.0031403 | 0.073085 | -61.94 | 62.9791 | -62.1277 | -62.3337 | 62.6678 | 0.16022 | -0.13733 | 0.15564 | 62.9883 | -62.1368 | -0.24261 | -0.1236 | -0.054931 | -0.44861 | -0.43487 | -0.25177 | -0.11444 | 0.18768 | 61.7477 | 62.0407 | 124.5529 | 124.8642 | -0.054931 | 124.8734 | 62.0453 | -0.25177 | 124.8642 | -0.054931 | 62.0453 | 124.5529 | 124.8734 | -125.2304 | -125.2396
479.6406 | 125.3632 | -61.8851 | 63.0707 | -0.17067 | 0.0090513 | 0.010628 | -0.0017005 | 0.063762 | -0.0018585 | 0.067103 | -61.9492 | 62.9837 | -62.1323 | -61.9995 | 62.9242 | 0.35248 | 0.19226 | -0.10986 | 63.0524 | -62.1094 | -0.24719 | -0.086975 | -0.064087 | -0.11444 | -0.14648 | -0.2243 | -0.018311 | 0.18311 | 62.0773 | 61.7752 | 124.8093 | 124.8688 | -0.064087 | 124.9374 | 62.2375 | -0.2243 | 124.8688 | -0.064087 | 62.2375 | 124.8093 | 124.9374 | -125.2029 | -125.1801
480.6406 | 125.4913 | -61.8622 | 63.0981 | -0.18593 | 0.0096921 | 0.01191 | -0.0010597 | 0.06419 | -0.0014313 | 0.069667 | -61.9766 | 62.9517 | -62.1323 | -61.9949 | 62.8876 | 0.15564 | -0.091553 | 0.30212 | 63.002 | -62.1185 | -0.27008 | -0.14649 | -0.11444 | -0.13275 | -0.21057 | -0.25635 | -0.096131 | 0.15564 | 61.7706 | 62.1643 | 124.7498 | 124.8138 | -0.11444 | 124.8642 | 62.0178 | -0.25635 | 124.8138 | -0.11444 | 62.0178 | 124.7498 | 124.8642 | -125.2304 | -125.2167
481.6406 | 125.3265 | -61.8668 | 63.1119 | -0.11726 | 0.0071285 | 0.0149 | 0.00022215 | 0.062481 | -0.0010041 | 0.068812 | -61.9446 | 62.97 | -62.114 | -62.0041 | 62.8647 | 0.16937 | -0.041199 | 0.29755 | 63.0112 | -62.1414 | -0.24719 | -0.14191 | -0.07782 | -0.13733 | -0.24719 | -0.27466 | -0.10071 | 0.16937 | 61.8256 | 62.1643 | 124.7314 | 124.8367 | -0.07782 | 124.8779 | 62.0361 | -0.27466 | 124.8367 | -0.07782 | 62.0361 | 124.7314 | 124.8779 | -125.2258 | -125.2533
482.6406 | 125.2396 | -61.94 | 63.1348 | -0.18593 | 0.0096921 | 0.011696 | 0.0070581 | 0.065258 | -0.0010041 | 0.066249 | -61.9812 | 63.0798 | -62.1277 | -62.0728 | 62.8281 | 0.068665 | 0.082397 | 0.1831 | 63.0478 | -62.1643 | -0.18768 | -0.054932 | -0.041199 | -0.13275 | -0.3067 | -0.22431 | -0.086975 | 0.14648 | 62.0224 | 62.1231 | 124.7681 | 125.0198 | -0.041199 | 124.9878 | 62.0087 | -0.22431 | 125.0198 | -0.041199 | 62.0087 | 124.7681 | 124.9878 | -125.2625 | -125.2991
483.6406 | 125.3448 | -61.8805 | 63.0753 | -0.086746 | 0.0069149 | 0.0097733 | -0.00084605 | 0.064403 | -0.0020721 | 0.067531 | -61.972 | 62.9654 | -62.1597 | -62.0224 | 62.8876 | 0.15106 | -0.07782 | 0.26093 | 63.0249 | -62.1368 | -0.27924 | -0.10986 | -0.091553 | -0.14191 | -0.18768 | -0.25635 | -0.050354 | 0.18768 | 61.8027 | 62.1414 | 124.7681 | 124.8459 | -0.091553 | 124.9054 | 62.0316 | -0.25635 | 124.8459 | -0.091553 | 62.0316 | 124.7681 | 124.9054 | -125.235 | -125.2121
484.6406 | 125.3265 | -61.8851 | 63.089 | -0.24696 | 0.01076 | 0.0089187 | 0.0012903 | 0.06419 | -0.0022859 | 0.067317 | -62.0316 | 62.9791 | -62.1277 | -61.9904 | 62.8876 | 0.16022 | -0.041199 | 0.29297 | 63.0386 | -62.1277 | -0.24261 | -0.10986 | -0.14648 | -0.10528 | -0.20142 | -0.24261 | -0.050354 | 0.096131 | 61.8439 | 62.178 | 124.7726 | 124.8642 | -0.14648 | 124.9237 | 62.0453 | -0.24261 | 124.8642 | -0.14648 | 62.0453 | 124.7726 | 124.9237 | -125.2167 | -125.2167
485.6406 | 125.3448 | -61.8759 | 63.1165 | 2.2402 | 0.0064877 | 0.010628 | -0.0012733 | 0.063121 | -0.0031403 | 0.068812 | -61.8668 | 62.9654 | -62.1231 | -61.9812 | 62.883 | 0.15106 | -0.045776 | 0.29755 | 63.0341 | -62.1231 | -0.24719 | -0.15106 | 0.009156 | -0.10529 | -0.23346 | -0.24719 | -0.082397 | 0.25635 | 61.8301 | 62.1735 | 124.7589 | 124.8413 | 0.009156 | 124.91 | 62.027 | -0.24719 | 124.8413 | 0.009156 | 62.027 | 124.7589 | 124.91 | -125.2396 | -125.2396
486.6406 | 125.3357 | -61.8713 | 63.1165 | -4.7636 | 0.0099057 | 0.0097733 | 0.00064935 | 0.063549 | -0.0022859 | 0.068812 | -62.0819 | 63.0066 | -62.1277 | -62.0132 | 62.8326 | 0.13733 | -0.032043 | 0.28381 | 63.0066 | -62.0911 | -0.25635 | -0.10986 | -0.21057 | -0.14191 | -0.28381 | -0.21973 | -0.10986 | 0.045777 | 61.8393 | 62.1552 | 124.704 | 124.8779 | -0.21057 | 124.8779 | 62.0087 | -0.21973 | 124.8779 | -0.21057 | 62.0087 | 124.704 | 124.8779 | -125.2441 | -125.2075
487.6406 | 125.267 | -61.9125 | 63.1485 | -0.2317 | 0.012256 | 0.012764 | 0.0055627 | 0.065044 | -0.0042085 | 0.066035 | -62.0132 | 63.0798 | -62.1414 | -62.0865 | 62.7731 | 0.064087 | 0.11444 | 0.16022 | 63.0798 | -62.1918 | -0.22888 | -0.068665 | -0.10071 | -0.17395 | -0.37537 | -0.27923 | -0.068665 | 0.12817 | 62.027 | 62.0728 | 124.6857 | 124.9924 | -0.10071 | 124.9924 | 61.9766 | -0.27923 | 124.9924 | -0.10071 | 61.9766 | 124.6857 | 124.9924 | -125.2899 | -125.3403
488.6406 | 125.3082 | -61.8942 | 63.1165 | -0.23933 | 0.0092649 | 0.0095595 | -0.0031959 | 0.065471 | -0.0029267 | 0.068599 | -61.9446 | 62.9745 | -62.1094 | -62.0132 | 62.8876 | 0.16022 | -0.022888 | 0.27924 | 63.0432 | -62.1323 | -0.21515 | -0.14191 | -0.050354 | -0.11902 | -0.22888 | -0.23804 | -0.073242 | 0.16479 | 61.8713 | 62.1735 | 124.7818 | 124.8688 | -0.050354 | 124.9374 | 62.0544 | -0.23804 | 124.8688 | -0.050354 | 62.0544 | 124.7818 | 124.9374 | -125.2258 | -125.2487
489.6406 | 125.3769 | -61.8896 | 63.0707 | -0.12489 | 0.0075559 | 0.0093459 | -0.0017005 | 0.063976 | -0.0022859 | 0.068171 | -61.9446 | 62.97 | -62.1323 | -61.8256 | 62.5351 | -0.10986 | 0.050354 | 0.21515 | 62.9883 | -62.1185 | -0.24262 | -0.10071 | -0.054932 | 0.064086 | -0.53558 | -0.22888 | -0.082398 | 0.18768 | 61.94 | 62.1048 | 124.4247 | 124.8596 | -0.054932 | 124.8779 | 61.7798 | -0.22888 | 124.8596 | -0.054932 | 61.7798 | 124.4247 | 124.8779 | -125.2029 | -125.1892
490.6406 | 125.3174 | -61.8942 | 63.0936 | -0.21645 | 0.0090513 | 0.010414 | 0.00022215 | 0.061626 | 0.00070494 | 0.071376 | -61.94 | 62.9929 | -62.1231 | -61.9949 | 62.8693 | 0.16479 | -0.032043 | 0.29297 | 63.0203 | -62.1231 | -0.22888 | -0.10071 | -0.045776 | -0.10071 | -0.2243 | -0.22888 | -0.073242 | 0.18311 | 61.8622 | 62.1872 | 124.7635 | 124.8871 | -0.045776 | 124.9146 | 62.059 | -0.22888 | 124.8871 | -0.045776 | 62.059 | 124.7635 | 124.9146 | -125.2167 | -125.2167
491.6406 | 125.3357 | -61.8668 | 63.1119 | -0.2317 | 0.0084103 | 0.013405 | -0.00084605 | 0.064403 | -0.00057686 | 0.069239 | -61.9675 | 62.9654 | -62.1323 | -61.9995 | 62.8693 | 0.16479 | -0.032043 | 0.28381 | 63.0066 | -62.0865 | -0.2655 | -0.14648 | -0.10071 | -0.13275 | -0.24261 | -0.21973 | -0.10529 | 0.1648 | 61.8347 | 62.1506 | 124.736 | 124.8322 | -0.10071 | 124.8734 | 62.0316 | -0.21973 | 124.8322 | -0.10071 | 62.0316 | 124.736 | 124.8734 | -125.2441 | -125.1984
492.6406 | 125.2167 | -61.9217 | 63.1302 | -0.26222 | 0.0084103 | 0.0082779 | 0.0023583 | 0.063549 | -0.0050629 | 0.069453 | -62.0178 | 63.0569 | -62.1185 | -62.0361 | 62.6404 | -0.07782 | 0.14191 | 0.15106 | 63.0478 | -62.2055 | -0.19684 | -0.073242 | -0.09613 | -0.11444 | -0.48981 | -0.28381 | -0.082397 | 0.10071 | 62.0636 | 62.0728 | 124.5621 | 124.9786 | -0.09613 | 124.9695 | 61.8439 | -0.28381 | 124.9786 | -0.09613 | 61.8439 | 124.5621 | 124.9695 | -125.2487 | -125.3357
493.6406 | 125.3265 | -61.8759 | 63.1027 | -0.24696 | 0.0060605 | 0.011055 | -0.0014869 | 0.062694 | -0.0029267 | 0.069026 | -61.9492 | 62.9608 | -62.1368 | -61.9995 | 62.8967 | 0.16937 | -0.022888 | 0.29297 | 63.0249 | -62.1094 | -0.26093 | -0.14191 | -0.073242 | -0.1236 | -0.20599 | -0.23346 | -0.07782 | 0.18768 | 61.853 | 62.1689 | 124.7726 | 124.8367 | -0.073242 | 124.9008 | 62.0453 | -0.23346 | 124.8367 | -0.073242 | 62.0453 | 124.7726 | 124.9008 | -125.2396 | -125.2121
494.6406 | 125.3357 | -61.8713 | 63.089 | -0.29274 | 0.0094785 | 0.0087051 | 0.00043575 | 0.064403 | -0.0027131 | 0.06689 | -61.9492 | 62.9654 | -62.1277 | -62.0316 | 62.9013 | 0.16022 | -0.036621 | 0.29297 | 63.0295 | -62.0911 | -0.25635 | -0.1236 | -0.07782 | -0.16022 | -0.18768 | -0.21973 | -0.059509 | 0.17853 | 61.8347 | 62.1643 | 124.7726 | 124.8367 | -0.07782 | 124.9008 | 62.0316 | -0.21973 | 124.8367 | -0.07782 | 62.0316 | 124.7726 | 124.9008 | -125.2167 | -125.1801
495.6406 | 125.2991 | -61.8805 | 63.1073 | -0.22408 | 0.0073423 | 0.012764 | 8.546e-06 | 0.063335 | -0.0014313 | 0.068171 | -61.9583 | 63.002 | -62.1323 | -62.0316 | 62.8555 | 0.12817 | 0.027466 | 0.2655 | 63.0066 | -62.1368 | -0.25177 | -0.10529 | -0.07782 | -0.15106 | -0.25177 | -0.25635 | -0.10071 | 0.17395 | 61.908 | 62.146 | 124.736 | 124.8825 | -0.07782 | 124.8871 | 62.0087 | -0.25635 | 124.8825 | -0.07782 | 62.0087 | 124.736 | 124.8871 | -125.2396 | -125.2441
496.6406 | 125.3128 | -61.8896 | 63.1119 | 0.63042 | 0.0092649 | 0.010414 | -0.0036231 | 0.062694 | -0.0012177 | 0.066462 | -61.9125 | 62.97 | -62.146 | -61.9949 | 62.8876 | 0.15564 | -0.050354 | 0.29755 | 63.0112 | -62.1506 | -0.25635 | -0.14191 | -0.022889 | -0.10529 | -0.2243 | -0.26093 | -0.10071 | 0.23346 | 61.8393 | 62.1872 | 124.7772 | 124.8596 | -0.022889 | 124.9008 | 62.0453 | -0.26093 | 124.8596 | -0.022889 | 62.0453 | 124.7772 | 124.9008 | -125.2579 | -125.2625
497.6406 | 125.2075 | -61.94 | 63.1393 | -0.29274 | 0.010547 | 0.011696 | 0.0059899 | 0.065471 | 0.00049134 | 0.068812 | -62.0087 | 63.0844 | -62.1368 | -62.1048 | 62.7548 | 0.050354 | 0.15106 | 0.15564 | 63.0615 | -62.1643 | -0.19684 | -0.054931 | -0.068665 | -0.16479 | -0.38452 | -0.22431 | -0.07782 | 0.12817 | 62.0911 | 62.0956 | 124.6948 | 125.0244 | -0.068665 | 125.0015 | 61.9904 | -0.22431 | 125.0244 | -0.068665 | 61.9904 | 124.6948 | 125.0015 | -125.2762 | -125.3037
498.6406 | 125.2167 | -61.9171 | 63.1348 | -0.22408 | 0.0086239 | 0.012123 | -0.0014869 | 0.065044 | -0.0014313 | 0.067744 | -61.9949 | 63.0157 | -62.1552 | -62.0682 | 62.8052 | 0.064087 | 0.11902 | 0.19684 | 63.0753 | -62.1414 | -0.23804 | -0.11902 | -0.07782 | -0.15106 | -0.32959 | -0.2243 | -0.05951 | 0.16022 | 62.0361 | 62.114 | 124.7223 | 124.9329 | -0.07782 | 124.9924 | 61.9812 | -0.2243 | 124.9329 | -0.07782 | 61.9812 | 124.7223 | 124.9924 | -125.2899 | -125.2762
499.6406 | 125.2853 | -61.8851 | 63.1073 | -0.2317 | 0.0084103 | 0.010841 | -0.00084605 | 0.062053 | -0.0012177 | 0.067317 | -61.9583 | 62.9745 | -62.1048 | -62.027 | 62.883 | 0.15106 | 0.009155 | 0.27008 | 63.0249 | -62.1185 | -0.21973 | -0.13275 | -0.073242 | -0.14191 | -0.2243 | -0.23346 | -0.082398 | 0.14648 | 61.8942 | 62.1552 | 124.7681 | 124.8596 | -0.073242 | 124.91 | 62.0361 | -0.23346 | 124.8596 | -0.073242 | 62.0361 | 124.7681 | 124.91 | -125.2121 | -125.2258
500.6406 | 125.2991 | -61.8851 | 63.1073 | -0.24696 | 0.0099057 | 0.0084915 | -0.0017005 | 0.062267 | -0.0029267 | 0.070308 | -61.9583 | 62.9654 | -62.1277 | -62.0132 | 62.8647 | 0.13733 | -0.004578 | 0.27008 | 63.0203 | -62.1048 | -0.24261 | -0.14191 | -0.073242 | -0.12817 | -0.24262 | -0.21973 | -0.086975 | 0.16937 | 61.8805 | 62.1552 | 124.7498 | 124.8505 | -0.073242 | 124.9054 | 62.0224 | -0.21973 | 124.8505 | -0.073242 | 62.0224 | 124.7498 | 124.9054 | -125.235 | -125.2121
501.6406 | 125.2991 | -61.9034 | 63.1119 | -0.25459 | 0.0099057 | 0.0082779 | 8.546e-06 | 0.063335 | -0.0027131 | 0.068812 | -61.9537 | 62.9791 | -62.1277 | -62.0178 | 62.8693 | 0.15106 | -0.004578 | 0.27924 | 63.0249 | -62.1185 | -0.2243 | -0.13275 | -0.050354 | -0.11444 | -0.24261 | -0.21515 | -0.086975 | 0.17395 | 61.8988 | 62.1826 | 124.7726 | 124.8825 | -0.050354 | 124.9283 | 62.0544 | -0.21515 | 124.8825 | -0.050354 | 62.0544 | 124.7726 | 124.9283 | -125.2396 | -125.2304
502.6406 | 125.2441 | -61.9446 | 63.0936 | 0.19554 | 0.010974 | 0.012764 | 0.0068445 | 0.063762 | 0.00027774 | 0.068171 | -62.0316 | 63.0524 | -62.1643 | -62.1414 | 62.7319 | -0.032043 | -0.054932 | 0.050354 | 63.0157 | -62.2009 | -0.21973 | -0.041199 | -0.086975 | -0.19684 | -0.36163 | -0.25635 | -0.07782 | 0.13275 | 61.8896 | 61.9949 | 124.6765 | 124.9969 | -0.086975 | 124.9603 | 61.9125 | -0.25635 | 124.9969 | -0.086975 | 61.9125 | 124.6765 | 124.9603 | -125.2579 | -125.2945
503.6406 | 125.2853 | -61.8805 | 63.0798 | -0.1783 | 0.0092649 | 0.011696 | -0.0012733 | 0.064403 | -0.00057686 | 0.070735 | -61.9675 | 62.9791 | -62.1185 | -62.0087 | 62.8876 | 0.16937 | -0.013733 | 0.28839 | 63.0203 | -62.1277 | -0.23804 | -0.10071 | -0.086975 | -0.12817 | -0.19226 | -0.24719 | -0.059509 | 0.15106 | 61.8668 | 62.1689 | 124.7681 | 124.8596 | -0.086975 | 124.9008 | 62.0499 | -0.24719 | 124.8596 | -0.086975 | 62.0499 | 124.7681 | 124.9008 | -125.1984 | -125.2075
504.6562 | 125.1801 | -61.9217 | 63.1027 | 0.020065 | 0.01311 | 0.0149 | 0.0064171 | 0.065899 | -0.0016449 | 0.067744 | -62.0407 | 63.0478 | -62.178 | -62.146 | 62.7274 | -0.036621 | 0.036621 | 0.045776 | 63.0615 | -62.1872 | -0.25635 | -0.054931 | -0.11902 | -0.2243 | -0.37537 | -0.2655 | -0.041199 | 0.13733 | 61.9583 | 61.9675 | 124.649 | 124.9695 | -0.11902 | 124.9832 | 61.8851 | -0.2655 | 124.9695 | -0.11902 | 61.8851 | 124.649 | 124.9832 | -125.2808 | -125.2899
505.6406 | 125.267 | -61.8668 | 63.1165 | -0.2317 | 0.010333 | 0.010201 | -0.0012733 | 0.065899 | -0.0022859 | 0.068599 | -61.972 | 62.9883 | -62.1277 | -62.0407 | 62.851 | 0.1236 | 0.041199 | 0.24719 | 63.0661 | -62.114 | -0.26093 | -0.12817 | -0.10529 | -0.17395 | -0.2655 | -0.24719 | -0.050354 | 0.15564 | 61.908 | 62.114 | 124.7177 | 124.855 | -0.10529 | 124.9329 | 61.9904 | -0.24719 | 124.855 | -0.10529 | 61.9904 | 124.7177 | 124.9329 | -125.2441 | -125.2304
506.6406 | 125.2625 | -61.9308 | 63.1119 | -0.22408 | 0.0079831 | 0.012978 | 0.0015039 | 0.063335 | -0.0033539 | 0.068385 | -61.9812 | 62.9929 | -62.1231 | -62.0499 | 62.8601 | 0.16022 | 0.032043 | 0.25635 | 63.0249 | -62.1231 | -0.19226 | -0.11902 | -0.050354 | -0.11902 | -0.25177 | -0.19226 | -0.086975 | 0.14191 | 61.9629 | 62.1872 | 124.791 | 124.9237 | -0.050354 | 124.9557 | 62.0911 | -0.19226 | 124.9237 | -0.050354 | 62.0911 | 124.791 | 124.9557 | -125.235 | -125.235
507.6406 | 125.2625 | -61.9171 | 63.1073 | -0.094376 | 0.013751 | 0.011269 | 0.0055627 | 0.06483 | 6.414e-05 | 0.06988 | -61.9629 | 63.0753 | -62.1368 | -62.0636 | 62.8098 | -0.10529 | 0.15106 | 0.25635 | 63.0386 | -62.178 | -0.21973 | -0.032044 | -0.045777 | -0.14649 | -0.29755 | -0.26093 | -0.068665 | 0.17395 | 62.0682 | 62.1735 | 124.7269 | 124.9924 | -0.045777 | 124.9557 | 61.8118 | -0.26093 | 124.9924 | -0.045777 | 61.8118 | 124.7269 | 124.9557 | -125.2441 | -125.2853
508.6406 | 125.1892 | -61.9308 | 63.1348 | -0.1783 | 0.0094785 | 0.012978 | 0.0015039 | 0.066967 | -0.0033539 | 0.069026 | -62.027 | 63.0524 | -62.1552 | -62.1231 | 62.7823 | 0.041199 | 0.15106 | 0.15564 | 63.0844 | -62.1323 | -0.2243 | -0.082398 | -0.096131 | -0.19226 | -0.35248 | -0.20142 | -0.050354 | 0.12817 | 62.0819 | 62.0865 | 124.7131 | 124.9832 | -0.096131 | 125.0153 | 61.972 | -0.20142 | 124.9832 | -0.096131 | 61.972 | 124.7131 | 125.0153 | -125.2899 | -125.267
509.6406 | 125.2487 | -61.9354 | 63.0798 | 0.18791 | 0.010333 | 0.0074233 | 0.0034265 | 0.066967 | 6.414e-05 | 0.067744 | -62.0224 | 63.0615 | -62.1552 | -62.1277 | 62.7457 | -0.009155 | -0.082397 | 0.050354 | 63.0203 | -62.178 | -0.21973 | -0.018311 | -0.086975 | -0.19226 | -0.33417 | -0.24262 | -0.059509 | 0.13275 | 61.853 | 61.9858 | 124.6811 | 124.9969 | -0.086975 | 124.9557 | 61.9263 | -0.24262 | 124.9969 | -0.086975 | 61.9263 | 124.6811 | 124.9557 | -125.235 | -125.2579
510.6406 | 125.3082 | -61.8942 | 63.0844 | -0.22408 | 0.0086239 | 0.0093459 | -0.0034095 | 0.065471 | -0.00079046 | 0.069026 | -61.9675 | 63.0157 | -62.1414 | -62.0316 | 62.883 | 0.15106 | 0.009155 | 0.28381 | 63.0386 | -62.1185 | -0.24719 | -0.068665 | -0.073242 | -0.13733 | -0.20142 | -0.2243 | -0.045777 | 0.17395 | 61.9034 | 62.178 | 124.7772 | 124.91 | -0.073242 | 124.9329 | 62.0453 | -0.2243 | 124.91 | -0.073242 | 62.0453 | 124.7772 | 124.9329 | -125.2258 | -125.2029
511.6406 | 125.2533 | -61.908 | 63.1439 | -0.2317 | 0.0081967 | 0.0099869 | 0.00043575 | 0.063121 | 0.00027774 | 0.070094 | -61.9766 | 63.0066 | -62.1368 | -62.0728 | 62.8189 | 0.12817 | 0.091553 | 0.22888 | 63.0569 | -62.1552 | -0.22888 | -0.13733 | -0.068665 | -0.1648 | -0.32501 | -0.24719 | -0.086975 | 0.16022 | 61.9995 | 62.1368 | 124.7269 | 124.9146 | -0.068665 | 124.9649 | 62.0361 | -0.24719 | 124.9146 | -0.068665 | 62.0361 | 124.7269 | 124.9649 | -125.2808 | -125.2991
512.6406 | 125.235 | -61.9171 | 63.1165 | -0.14015 | 0.01311 | 0.012978 | 0.0076989 | 0.066753 | -0.0022859 | 0.068171 | -62.1597 | 63.0203 | -62.1506 | -62.0682 | 62.8052 | 0.086975 | 0.027466 | 0.19226 | 63.0341 | -62.1735 | -0.23346 | -0.09613 | -0.24262 | -0.15106 | -0.31128 | -0.25635 | -0.082397 | -0.009155 | 61.9446 | 62.1094 | 124.7223 | 124.9374 | -0.24262 | 124.9512 | 62.0041 | -0.25635 | 124.9374 | -0.24262 | 62.0041 | 124.7223 | 124.9512 | -125.267 | -125.2899
513.6406 | 125.2991 | -61.8942 | 63.1393 | -0.2317 | 0.0084103 | 0.013832 | 8.546e-06 | 0.065899 | -0.0024995 | 0.069453 | -61.9675 | 63.0112 | -62.1643 | -62.0499 | 62.8601 | 0.14648 | 0.036621 | 0.24719 | 63.0753 | -62.1094 | -0.27008 | -0.12817 | -0.073242 | -0.15564 | -0.27924 | -0.21515 | -0.064087 | 0.19684 | 61.9308 | 62.1414 | 124.7543 | 124.9054 | -0.073242 | 124.9695 | 62.0407 | -0.21515 | 124.9054 | -0.073242 | 62.0407 | 124.7543 | 124.9695 | -125.3037 | -125.2487
514.6562 | 125.2396 | -61.9675 | 63.089 | 0.14976 | 0.012042 | 0.012337 | 0.0042809 | 0.066753 | -0.00057686 | 0.070308 | -62.0316 | 63.0569 | -62.1643 | -62.1643 | 62.7457 | -0.032043 | -0.032043 | 0.041199 | 63.0432 | -62.1872 | -0.19684 | -0.032043 | -0.064087 | -0.19684 | -0.34332 | -0.21973 | -0.045776 | 0.13275 | 61.9354 | 62.0087 | 124.7131 | 125.0244 | -0.064087 | 125.0107 | 61.9354 | -0.21973 | 125.0244 | -0.064087 | 61.9354 | 124.7131 | 125.0107 | -125.2533 | -125.2762
515.6406 | 125.2991 | -61.9034 | 63.0798 | -0.20882 | 0.0064877 | 0.012764 | -0.0027687 | 0.064403 | 0.00027774 | 0.069453 | -61.9492 | 62.9745 | -62.1552 | -62.027 | 62.8693 | 0.16479 | 0 | 0.27008 | 63.0386 | -62.1277 | -0.25177 | -0.10529 | -0.045777 | -0.1236 | -0.21057 | -0.2243 | -0.041199 | 0.20599 | 61.9034 | 62.1735 | 124.7726 | 124.8779 | -0.045777 | 124.942 | 62.0682 | -0.2243 | 124.8779 | -0.045777 | 62.0682 | 124.7726 | 124.942 | -125.235 | -125.2075
516.6406 | 125.1984 | -61.9263 | 63.1485 | -0.26222 | 0.0062741 | 0.010841 | -0.0027687 | 0.068248 | -0.00036306 | 0.070521 | -62.0316 | 63.0432 | -62.1323 | -62.0819 | 62.7045 | 0.041199 | 0.16022 | 0.15564 | 63.0753 | -62.1689 | -0.20599 | -0.10529 | -0.10528 | -0.15564 | -0.44403 | -0.24261 | -0.073243 | 0.10071 | 62.0865 | 62.0819 | 124.6307 | 124.9695 | -0.10528 | 125.0015 | 61.9675 | -0.24261 | 124.9695 | -0.10528 | 61.9675 | 124.6307 | 125.0015 | -125.2808 | -125.3174
517.6406 | 125.2121 | -61.9171 | 63.1302 | -0.24696 | 0.011401 | 0.014046 | 0.0055627 | 0.06483 | -0.0020721 | 0.068171 | -61.9766 | 63.0936 | -62.1414 | -62.0682 | 62.764 | 0.07782 | 0.091553 | 0.18768 | 63.0936 | -62.1826 | -0.2243 | -0.036621 | -0.05951 | -0.15106 | -0.36621 | -0.2655 | -0.036621 | 0.16479 | 62.0087 | 62.1048 | 124.6811 | 125.0107 | -0.05951 | 125.0107 | 61.9949 | -0.2655 | 125.0107 | -0.05951 | 61.9949 | 124.6811 | 125.0107 | -125.2716 | -125.3128
518.6406 | 125.2991 | -61.8759 | 63.1119 | -0.20882 | 0.0073423 | 0.015114 | -0.0019141 | 0.066967 | -0.0012177 | 0.069239 | -61.9492 | 62.9929 | -62.1368 | -62.0453 | 62.8647 | 0.14648 | 0.022888 | 0.25635 | 63.0615 | -62.1094 | -0.26093 | -0.11902 | -0.073242 | -0.16937 | -0.24719 | -0.23346 | -0.050354 | 0.18768 | 61.8988 | 62.1323 | 124.7406 | 124.8688 | -0.073242 | 124.9374 | 62.0224 | -0.23346 | 124.8688 | -0.073242 | 62.0224 | 124.7406 | 124.9374 | -125.2487 | -125.2213
519.6406 | 125.2487 | -61.9354 | 63.1073 | -0.25459 | 0.010333 | 0.014259 | 0.0064171 | 0.065899 | -0.0018585 | 0.067103 | -61.9675 | 63.0844 | -62.1231 | -62.0773 | 62.8006 | 0.086975 | 0.073242 | 0.18768 | 63.0478 | -62.1597 | -0.18768 | -0.022888 | -0.032043 | -0.14191 | -0.3067 | -0.2243 | -0.059509 | 0.15564 | 62.0087 | 62.1231 | 124.736 | 125.0198 | -0.032043 | 124.9832 | 62.0224 | -0.2243 | 125.0198 | -0.032043 | 62.0224 | 124.736 | 124.9832 | -125.2304 | -125.267
520.6406 | 125.2853 | -61.853 | 63.0936 | -0.086746 | 0.0073423 | 0.012123 | -0.0036231 | 0.063762 | -0.0020721 | 0.070308 | -61.9446 | 62.9883 | -62.1185 | -62.0316 | 62.8738 | 0.1831 | -0.013733 | 0.30212 | 63.0432 | -62.114 | -0.2655 | -0.10529 | -0.091553 | -0.17853 | -0.21973 | -0.26093 | -0.050354 | 0.17395 | 61.8393 | 62.1552 | 124.7269 | 124.8413 | -0.091553 | 124.8962 | 62.0361 | -0.26093 | 124.8413 | -0.091553 | 62.0361 | 124.7269 | 124.8962 | -125.2121 | -125.2075
521.6406 | 125.322 | -61.8713 | 63.1165 | 3.4914 | 0.0073423 | 0.0089187 | -0.0017005 | 0.063976 | -0.0012177 | 0.070308 | -61.8759 | 62.9608 | -62.1368 | -62.0132 | 62.8922 | 0.16937 | -0.059509 | 0.28839 | 63.0295 | -62.1323 | -0.2655 | -0.15564 | -0.004578 | -0.14191 | -0.2243 | -0.26093 | -0.086975 | 0.26093 | 61.8118 | 62.1597 | 124.7635 | 124.8322 | -0.004578 | 124.9008 | 62.0407 | -0.26093 | 124.8322 | -0.004578 | 62.0407 | 124.7635 | 124.9008 | -125.2533 | -125.2487
522.6406 | 125.2167 | -61.9354 | 63.1439 | -0.30037 | 0.0088375 | 0.0050735 | 0.0049219 | 0.063762 | -0.0024995 | 0.068385 | -62.0911 | 63.0432 | -62.1277 | -62.1552 | 62.7548 | 0.091553 | 0.10986 | 0.16479 | 63.0798 | -62.1735 | -0.19226 | -0.10071 | -0.15564 | -0.21973 | -0.3891 | -0.23804 | -0.064087 | 0.036622 | 62.0453 | 62.1002 | 124.6902 | 124.9786 | -0.15564 | 125.0153 | 62.027 | -0.23804 | 124.9786 | -0.15564 | 62.027 | 124.6902 | 125.0153 | -125.2716 | -125.3174
523.6406 | 125.2625 | -61.908 | 63.0936 | -0.22408 | 0.0064877 | 0.011696 | 0.00022215 | 0.062481 | -0.00014946 | 0.067958 | -61.9492 | 63.0066 | -62.1231 | -62.0453 | 62.8372 | 0.12817 | 0.036621 | 0.2655 | 63.0478 | -62.1185 | -0.21515 | -0.086975 | -0.041199 | -0.13733 | -0.25635 | -0.21057 | -0.045776 | 0.17395 | 61.9446 | 62.1735 | 124.7452 | 124.9146 | -0.041199 | 124.9557 | 62.0361 | -0.21057 | 124.9146 | -0.041199 | 62.0361 | 124.7452 | 124.9557 | -125.2167 | -125.2121
524.6406 | 125.3174 | -61.8622 | 63.089 | -0.19356 | 0.0084103 | 0.010201 | -0.00041865 | 0.062481 | 6.414e-05 | 0.070094 | -61.7661 | 63.0203 | -62.0865 | -62.0682 | 62.9013 | 0.20599 | -0.1236 | 0.27924 | 63.002 | -62.1277 | -0.2243 | -0.068664 | 0.096131 | -0.20599 | -0.18768 | -0.2655 | -0.086975 | 0.32043 | 61.7386 | 62.1414 | 124.7635 | 124.8825 | 0.096131 | 124.8642 | 62.0682 | -0.2655 | 124.8825 | 0.096131 | 62.0682 | 124.7635 | 124.8642 | -125.1755 | -125.2167
525.6406 | 125.2533 | -61.8851 | 63.0753 | -0.086746 | 0.0094785 | 0.01191 | -0.0017005 | 0.062694 | -0.00079046 | 0.070308 | -61.9125 | 62.9288 | -62.1368 | -61.9949 | 62.8738 | 0.17395 | 0.37994 | 0.64545 | 63.1073 | -62.0407 | -0.25177 | -0.14648 | -0.027466 | -0.10986 | -0.20142 | -0.15564 | 0.032044 | 0.2243 | 62.265 | 62.5305 | 124.7589 | 124.8138 | -0.027466 | 124.9924 | 62.059 | -0.15564 | 124.8138 | -0.027466 | 62.059 | 124.7589 | 124.9924 | -125.2121 | -125.116
526.6406 | 125.3357 | -61.8942 | 63.0753 | -0.079117 | 0.0067013 | 0.0082779 | -0.0025549 | 0.063549 | -0.0029267 | 0.069239 | -61.94 | 62.9654 | -62.114 | -62.0178 | 62.883 | 0.13733 | -0.07782 | 0.27008 | 63.002 | -62.1231 | -0.21973 | -0.10986 | -0.045776 | -0.1236 | -0.19226 | -0.22888 | -0.073242 | 0.17395 | 61.8164 | 62.1643 | 124.7772 | 124.8596 | -0.045776 | 124.8962 | 62.0316 | -0.22888 | 124.8596 | -0.045776 | 62.0316 | 124.7772 | 124.8962 | -125.1892 | -125.1984
527.6406 | 125.2075 | -61.9263 | 63.1165 | 0.042953 | 0.011401 | 0.0084915 | 0.0023583 | 0.063335 | -0.0014313 | 0.067744 | -61.9858 | 63.0707 | -62.1643 | -62.1094 | 62.7686 | 0.045776 | 0.1236 | 0.15564 | 63.0798 | -62.1918 | -0.23804 | -0.045776 | -0.059509 | -0.1831 | -0.3479 | -0.2655 | -0.036621 | 0.17853 | 62.0499 | 62.0819 | 124.6948 | 124.9969 | -0.059509 | 125.0061 | 61.972 | -0.2655 | 124.9969 | -0.059509 | 61.972 | 124.6948 | 125.0061 | -125.2808 | -125.3082
528.6406 | 125.3082 | -61.8622 | 63.0615 | -0.086746 | 0.0071285 | 0.0029373 | -0.0014869 | 0.064617 | 6.414e-05 | 0.069667 | -61.9904 | 62.9425 | -62.1368 | -62.059 | 62.8372 | 0.11444 | -0.054932 | 0.22888 | 63.0157 | -62.1323 | -0.27466 | -0.11902 | -0.12817 | -0.19684 | -0.2243 | -0.27008 | -0.045776 | 0.14648 | 61.8073 | 62.0911 | 124.6994 | 124.8047 | -0.12817 | 124.8779 | 61.9766 | -0.27008 | 124.8047 | -0.12817 | 61.9766 | 124.6994 | 124.8779 | -125.1984 | -125.1938
529.6406 | 125.3265 | -61.853 | 63.0753 | -0.14015 | 0.0081967 | 0.010841 | -0.0010597 | 0.061412 | -0.0024995 | 0.068812 | -61.9629 | 62.9562 | -62.114 | -62.0178 | 62.8647 | 0.14191 | -0.07782 | 0.27924 | 62.9974 | -62.114 | -0.26093 | -0.11902 | -0.10986 | -0.1648 | -0.21057 | -0.26093 | -0.077819 | 0.15106 | 61.7752 | 62.1323 | 124.7177 | 124.8093 | -0.10986 | 124.8505 | 61.9949 | -0.26093 | 124.8093 | -0.10986 | 61.9949 | 124.7177 | 124.8505 | -125.1892 | -125.1892
530.6406 | 125.3037 | -61.8805 | 63.0936 | -0.16304 | 0.010119 | 0.0087051 | 0.00043575 | 0.064617 | -0.0031403 | 0.066462 | -62.1918 | 62.9517 | -62.1414 | -62.0544 | 62.8738 | 0.17395 | -0.07782 | 0.29755 | 63.0066 | -62.1048 | -0.26093 | -0.14191 | -0.31128 | -0.17395 | -0.21973 | -0.2243 | -0.086975 | -0.050354 | 61.8027 | 62.178 | 124.7543 | 124.8322 | -0.31128 | 124.8871 | 62.0544 | -0.2243 | 124.8322 | -0.31128 | 62.0544 | 124.7543 | 124.8871 | -125.235 | -125.1984
531.6406 | 125.2808 | -61.9034 | 63.0936 | 0.020065 | 0.0090513 | 0.0074233 | -0.0021277 | 0.063335 | -0.00057686 | 0.068171 | -62.0041 | 62.9562 | -62.1185 | -62.0865 | 62.8052 | 0.050354 | -0.045776 | 0.17395 | 63.0157 | -62.1368 | -0.21515 | -0.13733 | -0.10071 | -0.18311 | -0.28839 | -0.23346 | -0.07782 | 0.11444 | 61.8576 | 62.0773 | 124.7086 | 124.8596 | -0.10071 | 124.9191 | 61.9537 | -0.23346 | 124.8596 | -0.10071 | 61.9537 | 124.7086 | 124.9191 | -125.2121 | -125.2304
532.6406 | 125.1846 | -61.94 | 63.1256 | -0.24696 | 0.010119 | 0.0099869 | 0.0029993 | 0.062694 | -0.0010041 | 0.069667 | -62.0087 | 63.0432 | -62.1506 | -62.1002 | 62.7777 | 0.27466 | 0.091553 | -0.013733 | 63.0753 | -62.178 | -0.21057 | -0.082397 | -0.068665 | -0.16022 | -0.3479 | -0.23804 | -0.050354 | 0.14191 | 62.0316 | 61.9263 | 124.7177 | 124.9832 | -0.068665 | 125.0153 | 62.2147 | -0.23804 | 124.9832 | -0.068665 | 62.2147 | 124.7177 | 125.0153 | -125.2762 | -125.3037
533.6406 | 125.3174 | -61.8805 | 63.0661 | -0.033341 | 0.0079831 | 0.010414 | -0.0025549 | 0.063335 | -0.0016449 | 0.066462 | -61.9904 | 62.9608 | -62.1597 | -62.059 | 62.8143 | 0.064087 | -0.07782 | 0.19226 | 63.0066 | -62.114 | -0.27924 | -0.10529 | -0.10986 | -0.17853 | -0.25177 | -0.23346 | -0.059509 | 0.16937 | 61.8027 | 62.0728 | 124.6948 | 124.8413 | -0.10986 | 124.8871 | 61.9446 | -0.23346 | 124.8413 | -0.10986 | 61.9446 | 124.6948 | 124.8871 | -125.2258 | -125.1801
534.6406 | 125.3174 | -61.8942 | 63.089 | -0.033341 | 0.0079831 | 0.0097733 | -0.00063225 | 0.06184 | -0.00014946 | 0.068599 | -62.0178 | 62.9425 | -62.146 | -62.0682 | 62.8098 | 0.073242 | -0.064087 | 0.17853 | 62.9837 | -62.146 | -0.25177 | -0.14648 | -0.1236 | -0.17395 | -0.27924 | -0.25177 | -0.10528 | 0.12817 | 61.8301 | 62.0728 | 124.704 | 124.8367 | -0.1236 | 124.8779 | 61.9675 | -0.25177 | 124.8367 | -0.1236 | 61.9675 | 124.704 | 124.8779 | -125.235 | -125.235
535.6406 | 125.3037 | -61.908 | 63.0981 | 0.065841 | 0.0079831 | 0.0093459 | -0.0012733 | 0.066112 | 6.414e-05 | 0.069026 | -62.0132 | 62.9562 | -62.1323 | -62.0819 | 62.8098 | 0.050354 | -0.064087 | 0.16022 | 63.0386 | -62.1323 | -0.2243 | -0.14191 | -0.10529 | -0.17395 | -0.28839 | -0.2243 | -0.05951 | 0.11902 | 61.8439 | 62.0682 | 124.7177 | 124.8642 | -0.10529 | 124.9466 | 61.9583 | -0.2243 | 124.8642 | -0.10529 | 61.9583 | 124.7177 | 124.9466 | -125.2304 | -125.2304
536.6406 | 125.3174 | -61.908 | 63.0569 | -0.018082 | 0.0099057 | 0.014259 | -0.0014869 | 0.062694 | 0.0011321 | 0.068385 | -61.9858 | 62.9608 | -62.1323 | -62.0316 | 62.8372 | 0.09613 | -0.059509 | 0.21057 | 62.9929 | -62.114 | -0.2243 | -0.096131 | -0.07782 | -0.1236 | -0.21973 | -0.20599 | -0.064087 | 0.14648 | 61.8484 | 62.1185 | 124.7452 | 124.8688 | -0.07782 | 124.9008 | 62.0041 | -0.20599 | 124.8688 | -0.07782 | 62.0041 | 124.7452 | 124.9008 | -125.1892 | -125.1709
537.6406 | 125.1755 | -61.9171 | 63.1393 | -0.23933 | 0.0088375 | 0.010841 | 0.0042809 | 0.062267 | -0.00014946 | 0.066462 | -61.9949 | 63.0615 | -62.1368 | -62.1002 | 62.7457 | 0.064087 | 0.1236 | 0.16022 | 63.0798 | -62.1552 | -0.21973 | -0.07782 | -0.07782 | -0.18311 | -0.39368 | -0.23804 | -0.059509 | 0.14191 | 62.0407 | 62.0773 | 124.6628 | 124.9786 | -0.07782 | 124.9969 | 61.9812 | -0.23804 | 124.9786 | -0.07782 | 61.9812 | 124.6628 | 124.9969 | -125.2762 | -125.2945
538.6406 | 125.2716 | -61.8759 | 63.0753 | 0.065841 | 0.0096921 | 0.0063553 | -0.00041865 | 0.063762 | -0.00057686 | 0.070094 | -62.0178 | 62.9562 | -62.1368 | -62.0773 | 62.7869 | -0.050354 | 0.21515 | 0.2243 | 63.0569 | -62.0911 | -0.26093 | -0.11902 | -0.14191 | -0.20142 | -0.28839 | -0.21515 | -0.01831 | 0.11902 | 62.0911 | 62.1002 | 124.6628 | 124.8322 | -0.14191 | 124.9329 | 61.8256 | -0.21515 | 124.8322 | -0.14191 | 61.8256 | 124.6628 | 124.9329 | -125.2121 | -125.1663
539.6406 | 125.2716 | -61.9125 | 63.1027 | 0.012436 | 0.0088375 | 0.010841 | -0.0014869 | 0.062908 | -0.00014946 | 0.069026 | -62.0224 | 62.9517 | -62.1323 | -62.0911 | 62.8006 | 0.050354 | -0.068665 | 0.16022 | 63.0157 | -62.1368 | -0.21973 | -0.15106 | -0.10986 | -0.17853 | -0.30212 | -0.2243 | -0.086975 | 0.10986 | 61.8439 | 62.0728 | 124.7131 | 124.8642 | -0.10986 | 124.9283 | 61.9629 | -0.2243 | 124.8642 | -0.10986 | 61.9629 | 124.7131 | 124.9283 | -125.235 | -125.2396
540.6406 | 125.2808 | -61.8896 | 63.0798 | 0.027695 | 0.0092649 | 0.0095595 | -0.0017005 | 0.063121 | -0.00036306 | 0.069667 | -62.0041 | 62.9608 | -62.1368 | -62.0636 | 62.8143 | 0.10071 | -0.07782 | 0.21515 | 63.0249 | -62.1414 | -0.24719 | -0.11902 | -0.11444 | -0.17395 | -0.2655 | -0.25177 | -0.054932 | 0.13275 | 61.8118 | 62.1048 | 124.704 | 124.8505 | -0.11444 | 124.9145 | 61.9904 | -0.25177 | 124.8505 | -0.11444 | 61.9904 | 124.704 | 124.9145 | -125.2167 | -125.2213
541.6406 | 125.2258 | -61.9034 | 63.0661 | 0.065841 | 0.0092649 | 0.01255 | 0.0012903 | 0.059276 | -0.00036306 | 0.068385 | -62.0041 | 62.9562 | -62.1597 | -62.1964 | 62.7365 | 0.045776 | -0.13275 | 0.14648 | 62.9929 | -62.1414 | -0.25635 | -0.10986 | -0.10071 | -0.29297 | -0.32959 | -0.23804 | -0.073242 | 0.15564 | 61.7706 | 62.0499 | 124.6399 | 124.8596 | -0.10071 | 124.8962 | 61.9492 | -0.23804 | 124.8596 | -0.10071 | 61.9492 | 124.6399 | 124.8962 | -125.2258 | -125.2075
542.6406 | 125.3174 | -61.8576 | 63.0615 | -0.23933 | 0.0079831 | 0.012123 | 0.00064935 | 0.063762 | -0.0020721 | 0.068599 | -61.9308 | 62.9791 | -62.1185 | -62.0041 | 62.8601 | 0.16479 | -0.022888 | 0.27466 | 63.0066 | -62.1231 | -0.26093 | -0.082397 | -0.073242 | -0.14648 | -0.20142 | -0.2655 | -0.054931 | 0.18768 | 61.8347 | 62.1323 | 124.7177 | 124.8367 | -0.073242 | 124.8642 | 62.0224 | -0.2655 | 124.8367 | -0.073242 | 62.0224 | 124.7177 | 124.8642 | -125.1801 | -125.1846
543.6406 | 125.267 | -61.8805 | 63.0753 | -0.056229 | 0.0099057 | 0.011055 | -0.0021277 | 0.062481 | -0.00057686 | 0.067103 | -61.9995 | 62.9745 | -62.1094 | -62.0636 | 62.8281 | 0.086975 | -0.07782 | 0.20599 | 62.9929 | -62.1094 | -0.22888 | -0.10071 | -0.11902 | -0.18311 | -0.24719 | -0.22888 | -0.082397 | 0.10986 | 61.8027 | 62.0865 | 124.7086 | 124.855 | -0.11902 | 124.8734 | 61.9675 | -0.22888 | 124.855 | -0.11902 | 61.9675 | 124.7086 | 124.8734 | -125.1846 | -125.1846
544.6406 | 125.2808 | -61.8759 | 63.0569 | 0.11925 | 0.010974 | 0.013191 | 0.0010767 | 0.063335 | -0.00036306 | 0.067958 | -61.972 | 62.9288 | -62.1872 | -62.0682 | 62.7914 | 0.041199 | -0.13733 | 0.13733 | 62.9745 | -62.1323 | -0.31128 | -0.12817 | -0.09613 | -0.19226 | -0.2655 | -0.25635 | -0.082398 | 0.21515 | 61.7386 | 62.0132 | 124.6674 | 124.8047 | -0.09613 | 124.8505 | 61.9171 | -0.25635 | 124.8047 | -0.09613 | 61.9171 | 124.6674 | 124.8505 | -125.2441 | -125.1892
545.6406 | 125.2762 | -61.8942 | 63.0341 | 0.16502 | 0.0092649 | 0.013832 | 8.546e-06 | 0.064403 | 6.414e-05 | 0.067317 | -61.9537 | 62.9288 | -62.1323 | -62.0453 | 62.8235 | 0.045776 | -0.15564 | 0.14191 | 62.9608 | -62.1368 | -0.23804 | -0.10529 | -0.059509 | -0.15106 | -0.21057 | -0.24261 | -0.073243 | 0.17853 | 61.7386 | 62.0361 | 124.7177 | 124.823 | -0.059509 | 124.855 | 61.94 | -0.24261 | 124.823 | -0.059509 | 61.94 | 124.7177 | 124.855 | -125.1663 | -125.1709
546.6406 | 125.2945 | -61.8851 | 63.0478 | 0.073471 | 0.0079831 | 0.010628 | -0.0010597 | 0.062267 | -0.00036306 | 0.068812 | -61.9949 | 62.9425 | -62.1094 | -62.0865 | 62.796 | 0.027466 | -0.1236 | 0.1236 | 62.9745 | -62.1368 | -0.2243 | -0.10529 | -0.10986 | -0.20142 | -0.25177 | -0.25177 | -0.073243 | 0.11444 | 61.7615 | 62.0087 | 124.6811 | 124.8276 | -0.10986 | 124.8596 | 61.9125 | -0.25177 | 124.8276 | -0.10986 | 61.9125 | 124.6811 | 124.8596 | -125.1572 | -125.1846
547.6406 | 125.2808 | -61.8942 | 63.0661 | 0.13451 | 0.010333 | 0.011696 | 0.0017175 | 0.063976 | 0.0026275 | 0.070521 | -61.9629 | 62.9425 | -62.1414 | -62.0636 | 62.8006 | 0.045776 | -0.16022 | 0.14648 | 62.97 | -62.146 | -0.24719 | -0.1236 | -0.068665 | -0.16937 | -0.2655 | -0.25177 | -0.09613 | 0.17853 | 61.734 | 62.0407 | 124.6948 | 124.8367 | -0.068665 | 124.8642 | 61.94 | -0.25177 | 124.8367 | -0.068665 | 61.94 | 124.6948 | 124.8642 | -125.2075 | -125.2121
548.6406 | 125.2716 | -61.8805 | 63.0798 | 0.13451 | 0.0084103 | 0.010841 | -0.0019141 | 0.064617 | -0.00036306 | 0.067531 | -61.9949 | 62.9745 | -62.1506 | -62.0773 | 62.7869 | 0.018311 | -0.09613 | 0.12817 | 62.9654 | -62.1506 | -0.27008 | -0.10529 | -0.11444 | -0.19684 | -0.29297 | -0.27008 | -0.11444 | 0.15564 | 61.7844 | 62.0087 | 124.6674 | 124.855 | -0.11444 | 124.8459 | 61.8988 | -0.27008 | 124.855 | -0.11444 | 61.8988 | 124.6674 | 124.8459 | -125.2304 | -125.2304
549.6406 | 125.2716 | -61.9217 | 63.0478 | 0.12688 | 0.0086239 | 0.012123 | -0.00063225 | 0.063549 | 0.0011321 | 0.071162 | -61.9904 | 62.9562 | -62.146 | -62.0773 | 62.796 | 0.036621 | -0.11902 | 0.13733 | 62.9837 | -62.1597 | -0.2243 | -0.091553 | -0.068664 | -0.15564 | -0.25177 | -0.23804 | -0.064087 | 0.15564 | 61.8027 | 62.059 | 124.7177 | 124.8779 | -0.068664 | 124.9054 | 61.9583 | -0.23804 | 124.8779 | -0.068664 | 61.9583 | 124.7177 | 124.9054 | -125.1938 | -125.2075
550.6406 | 125.2716 | -61.8988 | 63.0478 | 0.020065 | 0.0092649 | 0.010628 | -0.0014869 | 0.06184 | 0.00027774 | 0.071376 | -62.0178 | 62.9837 | -62.1552 | -62.233 | 62.7731 | 0.073242 | -0.13275 | 0.1236 | 62.9837 | -62.1323 | -0.25635 | -0.064087 | -0.11902 | -0.33417 | -0.27466 | -0.23346 | -0.064087 | 0.13733 | 61.7661 | 62.0224 | 124.6719 | 124.8825 | -0.11902 | 124.8825 | 61.972 | -0.23346 | 124.8825 | -0.11902 | 61.972 | 124.6719 | 124.8825 | -125.2029 | -125.1801
551.6406 | 125.2396 | -61.8805 | 63.0569 | 0.14214 | 0.0090513 | 0.012337 | 0.00086295 | 0.066326 | 0.0030547 | 0.069026 | -61.972 | 62.9242 | -62.1323 | -62.0407 | 62.8006 | 0.050354 | -0.15106 | 0.14191 | 62.9471 | -62.1277 | -0.25177 | -0.13275 | -0.091553 | -0.16022 | -0.25635 | -0.24719 | -0.10986 | 0.16022 | 61.7294 | 62.0224 | 124.6811 | 124.8047 | -0.091553 | 124.8276 | 61.9308 | -0.24719 | 124.8047 | -0.091553 | 61.9308 | 124.6811 | 124.8276 | -125.1892 | -125.1846
552.6406 | 125.3082 | -61.9125 | 63.0707 | 0.0048064 | 0.0062741 | 0.0074233 | -0.0021277 | 0.06184 | -0.00057686 | 0.070094 | -61.9949 | 62.9654 | -62.1414 | -62.0407 | 62.8235 | 0.10071 | -0.064087 | 0.21515 | 62.9974 | -62.1368 | -0.22888 | -0.10529 | -0.082397 | -0.12817 | -0.24719 | -0.2243 | -0.073242 | 0.14648 | 61.8484 | 62.1277 | 124.736 | 124.8779 | -0.082397 | 124.91 | 62.0132 | -0.2243 | 124.8779 | -0.082397 | 62.0132 | 124.736 | 124.91 | -125.2121 | -125.2075
553.6406 | 125.2899 | -61.8942 | 63.0707 | 0.15739 | 0.0094785 | 0.013405 | 0.00086295 | 0.063121 | -0.00079046 | 0.069453 | -61.9583 | 62.9608 | -62.114 | -62.0453 | 62.8235 | 0.054932 | -0.18768 | 0.16479 | 62.9471 | -62.1506 | -0.21973 | -0.10986 | -0.064087 | -0.15106 | -0.24719 | -0.25635 | -0.1236 | 0.15564 | 61.7065 | 62.059 | 124.7177 | 124.855 | -0.064087 | 124.8413 | 61.9492 | -0.25635 | 124.855 | -0.064087 | 61.9492 | 124.7177 | 124.8413 | -125.1846 | -125.2213
554.6406 | 125.322 | -61.8805 | 63.0295 | -0.0028231 | 0.0090513 | 0.012764 | 0.0036401 | 0.065044 | 0.0015595 | 0.068599 | -61.9446 | 62.9745 | -62.1277 | -62.0544 | 62.8235 | 0.045776 | -0.17853 | 0.15106 | 62.9745 | -62.1552 | -0.24719 | -0.054932 | -0.064087 | -0.17395 | -0.20599 | -0.27466 | -0.054932 | 0.18311 | 61.702 | 62.0316 | 124.704 | 124.855 | -0.064087 | 124.855 | 61.9263 | -0.27466 | 124.855 | -0.064087 | 61.9263 | 124.704 | 124.855 | -125.1572 | -125.1846
555.6406 | 125.2991 | -61.8805 | 63.0524 | 0.20317 | 0.011828 | 0.0089187 | 0.0034265 | 0.063549 | -0.00079046 | 0.068171 | -61.94 | 62.9654 | -62.1323 | -62.0132 | 62.8647 | 0.09613 | -0.20599 | 0.21057 | 62.97 | -62.1552 | -0.25177 | -0.086975 | -0.059509 | -0.13275 | -0.18768 | -0.27466 | -0.082397 | 0.19226 | 61.6745 | 62.0911 | 124.7452 | 124.8459 | -0.059509 | 124.8505 | 61.9766 | -0.27466 | 124.8459 | -0.059509 | 61.9766 | 124.7452 | 124.8505 | -125.1846 | -125.2075
556.6406 | 125.2258 | -61.8988 | 63.002 | 0.12688 | 0.0092649 | 0.014046 | 0.0042809 | 0.066326 | -0.00057686 | 0.068812 | -61.94 | 62.9837 | -62.146 | -62.0316 | 62.8143 | 0.050354 | -0.17853 | 0.14191 | 62.9517 | -62.1506 | -0.24719 | -0.01831 | -0.041198 | -0.13275 | -0.18768 | -0.25177 | -0.050354 | 0.20599 | 61.7203 | 62.0407 | 124.7131 | 124.8825 | -0.041198 | 124.8505 | 61.9492 | -0.25177 | 124.8825 | -0.041198 | 61.9492 | 124.7131 | 124.8505 | -125.148 | -125.1526
557.6406 | 125.2762 | -61.8851 | 63.0524 | 0.096359 | 0.01076 | 0.0097733 | 0.00043575 | 0.06483 | 0.00049134 | 0.067958 | -62.0316 | 62.9837 | -62.1231 | -62.0911 | 62.7869 | 0.032043 | -0.091553 | 0.13733 | 62.9929 | -62.1277 | -0.23804 | -0.068664 | -0.14648 | -0.20599 | -0.2655 | -0.24261 | -0.059509 | 0.091553 | 61.7935 | 62.0224 | 124.6719 | 124.8688 | -0.14648 | 124.8779 | 61.9171 | -0.24261 | 124.8688 | -0.14648 | 61.9171 | 124.6719 | 124.8779 | -125.1755 | -125.1801
558.6406 | 125.2899 | -61.9217 | 63.0661 | 0.14214 | 0.012683 | 0.015968 | 0.0068445 | 0.067608 | -0.0014313 | 0.068385 | -62.0087 | 63.0157 | -62.1368 | -62.0819 | 62.7594 | 0 | -0.11902 | 0.086975 | 62.9745 | -62.1826 | -0.21515 | -0.050354 | -0.086975 | -0.16022 | -0.3067 | -0.26093 | -0.091553 | 0.12817 | 61.8027 | 62.0087 | 124.6811 | 124.9374 | -0.086975 | 124.8962 | 61.9217 | -0.26093 | 124.9374 | -0.086975 | 61.9217 | 124.6811 | 124.8962 | -125.2029 | -125.2487
559.6406 | 125.235 | -61.9125 | 63.0707 | 0.16502 | 0.012469 | 0.013405 | 0.0055627 | 0.065258 | -0.0012177 | 0.067958 | -62.0178 | 63.0386 | -62.1414 | -62.114 | 62.7411 | -0.009155 | -0.091553 | 0.050354 | 63.002 | -62.178 | -0.22888 | -0.032044 | -0.10529 | -0.20142 | -0.32959 | -0.2655 | -0.068665 | 0.1236 | 61.821 | 61.9629 | 124.6536 | 124.9512 | -0.10529 | 124.9146 | 61.9034 | -0.2655 | 124.9512 | -0.10529 | 61.9034 | 124.6536 | 124.9146 | -125.2121 | -125.2487
560.6406 | 125.2853 | -61.9263 | 63.0661 | 0.21843 | 0.010974 | 0.011482 | 0.0019311 | 0.068248 | -0.0014313 | 0.068385 | -61.9766 | 63.0112 | -62.1368 | -62.059 | 62.8052 | 0.036621 | -0.16479 | 0.091553 | 62.9883 | -62.1597 | -0.21057 | -0.054932 | -0.050354 | -0.13275 | -0.26093 | -0.23346 | -0.07782 | 0.16022 | 61.7615 | 62.0178 | 124.7314 | 124.9374 | -0.050354 | 124.9146 | 61.9629 | -0.23346 | 124.9374 | -0.050354 | 61.9629 | 124.7314 | 124.9146 | -125.2029 | -125.2258
561.6406 | 125.2258 | -61.9125 | 63.0615 | 0.17265 | 0.011828 | 0.014687 | 0.0053491 | 0.066753 | -0.0035675 | 0.070521 | -62.0178 | 63.0341 | -62.1414 | -62.0956 | 62.7548 | 0.004578 | -0.10986 | 0.082397 | 63.0066 | -62.1826 | -0.22888 | -0.027465 | -0.10529 | -0.1831 | -0.3067 | -0.27008 | -0.054931 | 0.1236 | 61.8027 | 61.9949 | 124.6674 | 124.9466 | -0.10529 | 124.9191 | 61.9171 | -0.27008 | 124.9466 | -0.10529 | 61.9171 | 124.6674 | 124.9191 | -125.2029 | -125.2441
562.6406 | 125.2579 | -61.9034 | 63.0432 | 0.19554 | 0.0081967 | 0.013619 | -0.0012733 | 0.065899 | -0.00057686 | 0.070094 | -61.9675 | 62.9471 | -62.1414 | -62.0728 | 62.8098 | 0.064087 | -0.14191 | 0.14191 | 62.9745 | -62.1414 | -0.23804 | -0.09613 | -0.064087 | -0.16937 | -0.23346 | -0.23804 | -0.068665 | 0.17395 | 61.7615 | 62.0453 | 124.7131 | 124.8505 | -0.064087 | 124.8779 | 61.9675 | -0.23804 | 124.8505 | -0.064087 | 61.9675 | 124.7131 | 124.8779 | -125.1846 | -125.1846
563.6406 | 125.1846 | -61.9171 | 63.0707 | 0.15739 | 0.010119 | 0.015755 | 0.0044945 | 0.065044 | -0.00014946 | 0.069026 | -62.027 | 63.0615 | -62.1506 | -62.1414 | 62.7274 | -0.027466 | -0.027466 | 0.018311 | 63.0249 | -62.1872 | -0.23346 | -0.009156 | -0.10986 | -0.2243 | -0.34332 | -0.27008 | -0.045777 | 0.1236 | 61.8896 | 61.9354 | 124.6445 | 124.9786 | -0.10986 | 124.942 | 61.8896 | -0.27008 | 124.9786 | -0.10986 | 61.8896 | 124.6445 | 124.942 | -125.2213 | -125.2579
564.6406 | 125.2121 | -61.908 | 63.0981 | 0.17265 | 0.010547 | 0.015968 | 0.0042809 | 0.067394 | -0.00014946 | 0.070094 | -61.9995 | 63.0386 | -62.1552 | -62.1048 | 62.764 | -0.009155 | -0.10071 | 0.059509 | 63.0249 | -62.1735 | -0.24719 | -0.05951 | -0.091553 | -0.19684 | -0.33417 | -0.2655 | -0.073243 | 0.15564 | 61.8073 | 61.9675 | 124.6719 | 124.9466 | -0.091553 | 124.9329 | 61.8988 | -0.2655 | 124.9466 | -0.091553 | 61.8988 | 124.6719 | 124.9329 | -125.2533 | -125.2716
565.6406 | 125.3128 | -61.8988 | 63.0386 | 0.19554 | 0.0090513 | 0.01191 | 0.0021447 | 0.068676 | -0.0024995 | 0.070094 | -61.9766 | 63.0112 | -62.1414 | -62.0453 | 62.8143 | 0.036621 | -0.16937 | 0.11444 | 62.9929 | -62.1552 | -0.24261 | -0.027466 | -0.07782 | -0.14648 | -0.2243 | -0.25635 | -0.045776 | 0.16479 | 61.7294 | 62.0132 | 124.7131 | 124.91 | -0.07782 | 124.8917 | 61.9354 | -0.25635 | 124.91 | -0.07782 | 61.9354 | 124.7131 | 124.8917 | -125.1801 | -125.1938
566.6406 | 125.1984 | -61.9171 | 63.1165 | 0.073471 | 0.010333 | 0.018318 | 0.0053491 | 0.066753 | 0.00027774 | 0.069239 | -62.0316 | 63.0798 | -62.1323 | -62.0819 | 62.4115 | -0.36621 | 0.36163 | 0.24261 | 63.0112 | -62.178 | -0.21515 | -0.036621 | -0.11444 | -0.1648 | -0.70496 | -0.26093 | -0.10529 | 0.10071 | 62.2787 | 62.1597 | 124.3286 | 124.9969 | -0.11444 | 124.9283 | 61.5509 | -0.26093 | 124.9969 | -0.11444 | 61.5509 | 124.3286 | 124.9283 | -125.2487 | -125.2945
567.6406 | 125.2716 | -61.8942 | 63.0615 | 0.14976 | 0.010547 | 0.017464 | -0.0027687 | 0.066326 | -0.00079046 | 0.070735 | -61.9537 | 62.9654 | -62.1552 | -62.0544 | 62.8281 | 0.059509 | -0.16937 | 0.16022 | 62.9883 | -62.1597 | -0.26092 | -0.09613 | -0.059509 | -0.16022 | -0.23346 | -0.2655 | -0.073242 | 0.20142 | 61.7249 | 62.0544 | 124.7223 | 124.8596 | -0.059509 | 124.8825 | 61.9537 | -0.2655 | 124.8596 | -0.059509 | 61.9537 | 124.7223 | 124.8825 | -125.2167 | -125.2213
568.6406 | 125.1892 | -61.9354 | 63.0707 | -0.73524 | 0.011188 | 0.011696 | 0.0042809 | 0.067394 | -0.0018585 | 0.06988 | -62.0499 | 63.0753 | -62.1414 | -62.1414 | 62.6999 | -0.032043 | -0.004578 | 0.009155 | 63.0112 | -62.2192 | -0.20599 | 0.004577 | -0.11444 | -0.20599 | -0.37079 | -0.28381 | -0.05951 | 0.091552 | 61.9308 | 61.9446 | 124.6353 | 125.0107 | -0.11444 | 124.9466 | 61.9034 | -0.28381 | 125.0107 | -0.11444 | 61.9034 | 124.6353 | 124.9466 | -125.2121 | -125.2899
569.6406 | 125.1846 | -61.9537 | 63.0707 | 0.13451 | 0.012256 | 0.014687 | 0.0051355 | 0.066967 | -0.0014313 | 0.069026 | -62.2101 | 63.0203 | -62.1735 | -62.1048 | 62.677 | -0.10071 | 0.082397 | 0.018311 | 63.0478 | -62.2055 | -0.21973 | -0.050354 | -0.25635 | -0.15106 | -0.39368 | -0.25177 | -0.022888 | -0.036621 | 62.0361 | 61.972 | 124.6307 | 124.9741 | -0.25635 | 125.0015 | 61.853 | -0.25177 | 124.9741 | -0.25635 | 61.853 | 124.6307 | 125.0015 | -125.2441 | -125.2762
570.6406 | 125.1572 | -61.9171 | 63.0981 | 0.10399 | 0.011401 | 0.012123 | 0.0042809 | 0.065471 | -0.0022859 | 0.073298 | -62.0316 | 63.0569 | -62.1643 | -62.4115 | 62.8967 | 0.26093 | -0.068665 | 0.086975 | 63.0661 | -62.2238 | -0.24719 | -0.041199 | -0.11444 | -0.49439 | -0.20142 | -0.3067 | -0.032044 | 0.13275 | 61.8484 | 62.0041 | 124.8138 | 124.9741 | -0.11444 | 124.9832 | 62.178 | -0.3067 | 124.9741 | -0.11444 | 62.178 | 124.8138 | 124.9832 | -125.2625 | -125.322
571.6406 | 125.1984 | -61.9446 | 63.0524 | 0.17265 | 0.011401 | 0.014046 | 0.0040673 | 0.068035 | -0.0014313 | 0.068171 | -62.0132 | 63.0569 | -62.1414 | -62.1506 | 62.7182 | -0.032043 | -0.018311 | 0.018311 | 63.0478 | -62.2101 | -0.19684 | 0.004578 | -0.068665 | -0.20599 | -0.33417 | -0.2655 | -0.004577 | 0.12817 | 61.9263 | 61.9629 | 124.6628 | 125.0015 | -0.068665 | 124.9924 | 61.9125 | -0.2655 | 125.0015 | -0.068665 | 61.9125 | 124.6628 | 124.9924 | -125.1938 | -125.2625
572.6406 | 125.235 | -61.8851 | 63.0661 | -0.0028231 | 0.0077695 | 0.012764 | -0.0061865 | 0.065044 | 6.414e-05 | 0.067744 | -62.0316 | 62.9883 | -62.1231 | -62.1094 | 62.7914 | 0.009155 | -0.064087 | 0.11902 | 63.0066 | -62.1231 | -0.23804 | -0.07782 | -0.14648 | -0.2243 | -0.27466 | -0.23804 | -0.059509 | 0.091553 | 61.821 | 62.0041 | 124.6765 | 124.8734 | -0.14648 | 124.8917 | 61.8942 | -0.23804 | 124.8734 | -0.14648 | 61.8942 | 124.6765 | 124.8917 | -125.1892 | -125.1892
573.6406 | 125.1526 | -61.9446 | 63.0844 | 0.050583 | 0.01311 | 0.017677 | 0.0047081 | 0.066539 | -0.0020721 | 0.069026 | -62.0087 | 63.0798 | -62.114 | -62.1506 | 62.6999 | -0.032043 | 0.041199 | 0.041199 | 63.0432 | -62.233 | -0.16937 | -0.004578 | -0.064087 | -0.20599 | -0.38452 | -0.28839 | -0.041199 | 0.10529 | 61.9858 | 61.9858 | 124.6445 | 125.0244 | -0.064087 | 124.9878 | 61.9125 | -0.28839 | 125.0244 | -0.064087 | 61.9125 | 124.6445 | 124.9878 | -125.1984 | -125.3174
574.6406 | 125.1938 | -61.9263 | 63.0707 | -0.84969 | 0.011188 | 0.012337 | 0.0053491 | 0.067394 | 0.0015595 | 0.069239 | -62.0819 | 63.0981 | -62.146 | -62.1872 | 62.709 | -0.022888 | -0.004578 | 0.036621 | 63.0432 | -62.2101 | -0.21973 | 0.027466 | -0.15564 | -0.26093 | -0.36163 | -0.28381 | -0.027466 | 0.064087 | 61.9217 | 61.9629 | 124.6353 | 125.0244 | -0.15564 | 124.9695 | 61.9034 | -0.28381 | 125.0244 | -0.15564 | 61.9034 | 124.6353 | 124.9695 | -125.2167 | -125.2808
575.6406 | 125.1572 | -61.94 | 63.0936 | 0.11162 | 0.011615 | 0.013619 | 0.0066309 | 0.068462 | -0.0012177 | 0.071589 | -62.4207 | 62.9883 | -62.1735 | -62.2055 | 62.6907 | 0 | 0.027466 | 0.004578 | 63.0661 | -62.2147 | -0.23346 | -0.10529 | -0.48065 | -0.2655 | -0.40283 | -0.27466 | -0.027466 | -0.24719 | 61.9675 | 61.9446 | 124.6307 | 124.9283 | -0.48065 | 125.0061 | 61.94 | -0.27466 | 124.9283 | -0.48065 | 61.94 | 124.6307 | 125.0061 | -125.267 | -125.3082
576.6406 | 125.1709 | -61.9263 | 63.089 | 0.12688 | 0.01311 | 0.01255 | 0.0059899 | 0.065685 | -0.0050629 | 0.071376 | -62.0361 | 63.0569 | -62.1918 | -62.1689 | 62.6678 | 0.018311 | 0.050354 | 0 | 63.0707 | -62.2147 | -0.2655 | -0.032043 | -0.10986 | -0.24261 | -0.42114 | -0.28839 | -0.01831 | 0.15564 | 61.9766 | 61.9263 | 124.5941 | 124.9832 | -0.10986 | 124.9969 | 61.9446 | -0.28839 | 124.9832 | -0.10986 | 61.9446 | 124.5941 | 124.9969 | -125.2808 | -125.3037
577.6406 | 125.2945 | -61.8988 | 63.0432 | 0.11925 | 0.010119 | 0.013191 | -0.0012733 | 0.069316 | 0.0011321 | 0.071376 | -61.9675 | 62.9745 | -62.1552 | -62.0911 | 62.8098 | 0.064087 | -0.15564 | 0.16022 | 63.0203 | -62.146 | -0.25635 | -0.068665 | -0.068664 | -0.19226 | -0.23346 | -0.24719 | -0.022888 | 0.18768 | 61.7432 | 62.059 | 124.7086 | 124.8734 | -0.068664 | 124.9191 | 61.9629 | -0.24719 | 124.8734 | -0.068664 | 61.9629 | 124.7086 | 124.9191 | -125.1984 | -125.1892
578.6406 | 125.1755 | -61.9263 | 63.0707 | 0.14976 | 0.010119 | 0.012764 | 0.0032129 | 0.067394 | -0.0012177 | 0.069239 | -62.0407 | 63.0478 | -62.1552 | -62.1552 | 62.709 | -0.041199 | 0 | 0.018311 | 63.0569 | -62.2284 | -0.22888 | -0.022888 | -0.11444 | -0.22888 | -0.36163 | -0.30212 | -0.013733 | 0.11444 | 61.9263 | 61.9446 | 124.6353 | 124.9741 | -0.11444 | 124.9832 | 61.8851 | -0.30212 | 124.9741 | -0.11444 | 61.8851 | 124.6353 | 124.9832 | -125.2258 | -125.2991
579.6406 | 125.1572 | -61.9354 | 63.0936 | 0.16502 | 0.013965 | 0.015968 | 0.0036401 | 0.065899 | 0.00091854 | 0.069667 | -62.0224 | 63.0524 | -62.1735 | -62.178 | 62.7136 | -0.045776 | -0.009155 | 0.022888 | 63.0432 | -62.2055 | -0.23804 | -0.041199 | -0.086975 | -0.24262 | -0.37994 | -0.27008 | -0.050354 | 0.15106 | 61.9263 | 61.9583 | 124.649 | 124.9878 | -0.086975 | 124.9786 | 61.8896 | -0.27008 | 124.9878 | -0.086975 | 61.8896 | 124.649 | 124.9786 | -125.267 | -125.2991
580.6406 | 125.2258 | -61.908 | 63.0569 | 0.18791 | 0.012469 | 0.013619 | 0.0029993 | 0.068035 | 0.00070494 | 0.068385 | -62.0178 | 63.0478 | -62.1552 | -62.1185 | 62.7411 | -0.027466 | -0.086975 | 0.064087 | 63.0295 | -62.2101 | -0.24719 | -0.009155 | -0.10986 | -0.21057 | -0.31586 | -0.30212 | -0.027466 | 0.13733 | 61.821 | 61.972 | 124.649 | 124.9557 | -0.10986 | 124.9374 | 61.8805 | -0.30212 | 124.9557 | -0.10986 | 61.8805 | 124.649 | 124.9374 | -125.2121 | -125.267
581.6406 | 125.1709 | -61.9308 | 63.0569 | 0.24132 | 0.012469 | 0.012123 | 0.0042809 | 0.068248 | 0.0015595 | 0.068599 | -62.0453 | 63.0844 | -62.146 | -62.1597 | 62.6953 | -0.050354 | -0.009155 | 0.041199 | 63.0432 | -62.2192 | -0.21515 | 0.027466 | -0.11444 | -0.22888 | -0.36163 | -0.28839 | -0.013733 | 0.10071 | 61.9217 | 61.972 | 124.6262 | 125.0153 | -0.11444 | 124.9741 | 61.8805 | -0.28839 | 125.0153 | -0.11444 | 61.8805 | 124.6262 | 124.9741 | -125.2029 | -125.2762
582.6406 | 125.2487 | -61.9125 | 63.0478 | 0.0811 | 0.0088375 | 0.014687 | -0.0040503 | 0.065685 | -0.0018585 | 0.068171 | -62.027 | 62.9333 | -62.1506 | -61.9629 | 63.0066 | 0.20142 | -0.17853 | 0.15106 | 63.0524 | -62.1643 | -0.23804 | -0.11444 | -0.11444 | -0.050354 | -0.041199 | -0.25177 | 0.004577 | 0.1236 | 61.734 | 62.0636 | 124.9191 | 124.8459 | -0.11444 | 124.9649 | 62.114 | -0.25177 | 124.8459 | -0.11444 | 62.114 | 124.9191 | 124.9649 | -125.1984 | -125.2121
583.6406 | 125.1709 | -61.9217 | 63.0707 | -0.81154 | 0.013537 | 0.0149 | 0.0040673 | 0.068248 | 6.414e-05 | 0.068385 | -62.0682 | 63.0798 | -62.1414 | -62.1643 | 62.6953 | -0.059509 | 0.027466 | 0.018311 | 63.0341 | -62.2284 | -0.21973 | 0.009155 | -0.14648 | -0.24262 | -0.37537 | -0.3067 | -0.036621 | 0.073242 | 61.9492 | 61.94 | 124.617 | 125.0015 | -0.14648 | 124.9557 | 61.8622 | -0.3067 | 125.0015 | -0.14648 | 61.8622 | 124.617 | 124.9557 | -125.2121 | -125.2991
584.6406 | 125.1343 | -61.9446 | 63.0844 | 1.2103 | 0.01311 | 0.010841 | 0.0042809 | 0.066112 | 0.00049134 | 0.071589 | -61.9308 | 63.089 | -62.1368 | -62.1552 | 62.6862 | -0.045776 | -0.009155 | 0.050354 | 63.0524 | -62.2375 | -0.19226 | 0.004577 | 0.013733 | -0.21057 | -0.39825 | -0.29297 | -0.032044 | 0.20599 | 61.9354 | 61.9949 | 124.6307 | 125.0336 | 0.013733 | 124.9969 | 61.8988 | -0.29297 | 125.0336 | 0.013733 | 61.8988 | 124.6307 | 124.9969 | -125.2213 | -125.322
585.6406 | 125.1938 | -61.908 | 63.0615 | 0.16502 | 0.010974 | 0.012764 | 0.0027855 | 0.065685 | 0.00027774 | 0.069026 | -62.0224 | 63.0524 | -62.1643 | -62.1414 | 62.7274 | -0.018311 | -0.041199 | 0.045776 | 63.0661 | -62.2009 | -0.25635 | -0.009155 | -0.11444 | -0.23346 | -0.33417 | -0.29297 | 0.004578 | 0.14191 | 61.8668 | 61.9537 | 124.6353 | 124.9603 | -0.11444 | 124.9741 | 61.8896 | -0.29297 | 124.9603 | -0.11444 | 61.8896 | 124.6353 | 124.9741 | -125.2258 | -125.2625
586.6406 | 125.1572 | -61.9308 | 63.0707 | 0.11925 | 0.018664 | 0.016182 | 0.0057763 | 0.066967 | -0.0018585 | 0.070521 | -62.4481 | 62.9883 | -62.1964 | -62.1872 | 62.6724 | -0.032043 | 0.027466 | 0.004578 | 63.0478 | -62.2238 | -0.2655 | -0.082398 | -0.51727 | -0.25635 | -0.39825 | -0.29297 | -0.022888 | -0.25177 | 61.9583 | 61.9354 | 124.6033 | 124.9191 | -0.51727 | 124.9786 | 61.8988 | -0.29297 | 124.9191 | -0.51727 | 61.8988 | 124.6033 | 124.9786 | -125.267 | -125.2945
587.6406 | 125.2579 | -61.8988 | 63.0661 | 0.14214 | 0.0086239 | 0.017464 | -0.0046913 | 0.067821 | -0.0012177 | 0.070521 | -62.0087 | 62.9562 | -62.1368 | -62.1094 | 62.8006 | 0.018311 | -0.09613 | 0.13733 | 63.002 | -62.1323 | -0.23804 | -0.10986 | -0.10986 | -0.21057 | -0.2655 | -0.23346 | -0.064087 | 0.12817 | 61.8027 | 62.0361 | 124.6994 | 124.855 | -0.10986 | 124.9008 | 61.9171 | -0.23346 | 124.855 | -0.10986 | 61.9171 | 124.6994 | 124.9008 | -125.2029 | -125.1984
588.6406 | 125.2121 | -61.9263 | 63.0478 | 0.16502 | 0.015246 | 0.01255 | 0.0047081 | 0.06419 | -0.00057686 | 0.069667 | -62.027 | 63.0661 | -62.1689 | -62.1597 | 62.7136 | -0.041199 | -0.027466 | 0.022888 | 63.0478 | -62.2055 | -0.24261 | 0.01831 | -0.10071 | -0.23346 | -0.33417 | -0.27923 | 0 | 0.14191 | 61.8988 | 61.9492 | 124.6399 | 124.9924 | -0.10071 | 124.9741 | 61.8851 | -0.27923 | 124.9924 | -0.10071 | 61.8851 | 124.6399 | 124.9741 | -125.2167 | -125.2533
589.6406 | 125.2029 | -61.9217 | 63.0707 | 0.15739 | 0.011188 | 0.011696 | 0.0051355 | 0.067394 | -0.0010041 | 0.068385 | -62.027 | 63.0707 | -62.1689 | -62.1552 | 62.7045 | -0.041199 | -0.027466 | 0.041199 | 63.0569 | -62.2192 | -0.24719 | 0 | -0.10529 | -0.23346 | -0.36621 | -0.29755 | -0.013733 | 0.14191 | 61.8942 | 61.9629 | 124.6262 | 124.9924 | -0.10529 | 124.9786 | 61.8805 | -0.29755 | 124.9924 | -0.10529 | 61.8805 | 124.6262 | 124.9786 | -125.2396 | -125.2899
590.6406 | 125.1892 | -61.9171 | 63.0524 | 0.13451 | 0.010333 | 0.012978 | 0.0047081 | 0.069103 | 0.0013457 | 0.068171 | -62.0224 | 63.0386 | -62.1826 | -62.146 | 62.7136 | -0.045776 | -0.027466 | 0.041199 | 63.0707 | -62.2101 | -0.2655 | -0.013733 | -0.10529 | -0.22888 | -0.33875 | -0.29297 | 0.018311 | 0.16022 | 61.8896 | 61.9583 | 124.6307 | 124.9557 | -0.10529 | 124.9878 | 61.8713 | -0.29297 | 124.9557 | -0.10529 | 61.8713 | 124.6307 | 124.9878 | -125.235 | -125.2625
591.6406 | 125.1663 | -61.9308 | 63.0753 | 0.11925 | 0.011828 | 0.014259 | 0.0038537 | 0.068248 | -0.0018585 | 0.070948 | -62.027 | 63.0844 | -62.1506 | -62.1643 | 62.7136 | -0.059509 | -0.013733 | 0.036621 | 63.0707 | -62.2238 | -0.21973 | 0.009156 | -0.096131 | -0.23346 | -0.36163 | -0.29297 | -0.004577 | 0.1236 | 61.9171 | 61.9675 | 124.6445 | 125.0153 | -0.096131 | 125.0015 | 61.8713 | -0.29297 | 125.0153 | -0.096131 | 61.8713 | 124.6445 | 125.0015 | -125.2258 | -125.2991
592.6406 | 125.2579 | -61.8988 | 63.0569 | -0.6971 | 0.010119 | 0.011696 | -0.0051185 | 0.066753 | 0.00027774 | 0.071162 | -62.0636 | 62.97 | -62.1689 | -62.1048 | 62.7686 | 0.036621 | -0.059509 | 0.15564 | 63.0341 | -62.1597 | -0.27008 | -0.086975 | -0.1648 | -0.20599 | -0.28839 | -0.26093 | -0.022888 | 0.10528 | 61.8393 | 62.0544 | 124.6674 | 124.8688 | -0.1648 | 124.9329 | 61.9354 | -0.26093 | 124.8688 | -0.1648 | 61.9354 | 124.6674 | 124.9329 | -125.2258 | -125.2167
593.6406 | 125.1801 | -61.9171 | 63.0615 | 0.13451 | 0.012469 | 0.016823 | 0.0036401 | 0.066967 | -0.0010041 | 0.072017 | -62.0132 | 63.0569 | -62.1643 | -62.1597 | 62.709 | -0.041199 | -0.018311 | 0.032043 | 63.0524 | -62.1918 | -0.24719 | -0.004577 | -0.096131 | -0.24262 | -0.35248 | -0.27466 | -0.009155 | 0.15106 | 61.8988 | 61.9492 | 124.6262 | 124.9741 | -0.096131 | 124.9695 | 61.8759 | -0.27466 | 124.9741 | -0.096131 | 61.8759 | 124.6262 | 124.9695 | -125.2258 | -125.2533
594.6406 | 125.1526 | -61.9308 | 63.0707 | 0.14976 | 0.011401 | 0.0149 | 0.0034265 | 0.067394 | 0.0011321 | 0.069239 | -62.0316 | 63.0524 | -62.1597 | -62.1506 | 62.709 | -0.045776 | -0.009155 | 0.022888 | 63.0432 | -62.2238 | -0.22888 | -0.018311 | -0.10071 | -0.21973 | -0.36163 | -0.29297 | -0.027466 | 0.12817 | 61.9217 | 61.9537 | 124.6399 | 124.9832 | -0.10071 | 124.9741 | 61.8851 | -0.29297 | 124.9832 | -0.10071 | 61.8851 | 124.6399 | 124.9741 | -125.2304 | -125.2945
595.6406 | 125.2396 | -61.9263 | 63.0753 | 0.24132 | 0.010547 | 0.014046 | 0.0029993 | 0.068035 | -0.0018585 | 0.069453 | -62.0041 | 63.0432 | -62.1597 | -62.1231 | 62.7319 | -0.018311 | -0.091553 | 0.064087 | 63.0569 | -62.1964 | -0.23346 | -0.032043 | -0.077819 | -0.19684 | -0.34332 | -0.27008 | -0.01831 | 0.15564 | 61.8347 | 61.9904 | 124.6582 | 124.9695 | -0.077819 | 124.9832 | 61.908 | -0.27008 | 124.9695 | -0.077819 | 61.908 | 124.6582 | 124.9832 | -125.235 | -125.2716
596.6406 | 125.2304 | -61.9263 | 63.0249 | 0.19554 | 0.0099057 | 0.013619 | 0.0036401 | 0.066967 | -0.0016449 | 0.070948 | -62.0041 | 63.0524 | -62.146 | -62.1277 | 62.7228 | -0.018311 | -0.059509 | 0.041199 | 63.0432 | -62.1826 | -0.21973 | 0.027466 | -0.077819 | -0.20142 | -0.30212 | -0.25635 | 0.018311 | 0.14191 | 61.8668 | 61.9675 | 124.649 | 124.9786 | -0.077819 | 124.9695 | 61.908 | -0.25635 | 124.9786 | -0.077819 | 61.908 | 124.649 | 124.9695 | -125.1709 | -125.2075
597.6406 | 125.2487 | -61.9034 | 63.0478 | 0.10399 | 0.01076 | 0.014473 | -0.0012733 | 0.065258 | -0.0010041 | 0.068599 | -61.9675 | 62.97 | -62.1552 | -62.0865 | 62.7914 | 0.064087 | -0.16022 | 0.14648 | 62.9974 | -62.146 | -0.25177 | -0.07782 | -0.064087 | -0.18311 | -0.25635 | -0.24261 | -0.050354 | 0.18768 | 61.7432 | 62.0499 | 124.6948 | 124.8734 | -0.064087 | 124.9008 | 61.9675 | -0.24261 | 124.8734 | -0.064087 | 61.9675 | 124.6948 | 124.9008 | -125.2029 | -125.1938
598.6406 | 125.1892 | -61.9354 | 63.0524 | 0.14976 | 0.013324 | 0.014687 | 0.0034265 | 0.065258 | -0.0012177 | 0.069026 | -62.0224 | 63.0661 | -62.1506 | -62.146 | 62.709 | -0.032043 | -0.032043 | 0.032043 | 63.0295 | -62.2147 | -0.21515 | 0.013733 | -0.086975 | -0.21057 | -0.34332 | -0.27924 | -0.022888 | 0.12817 | 61.9034 | 61.9675 | 124.6445 | 125.0015 | -0.086975 | 124.9649 | 61.9034 | -0.27924 | 125.0015 | -0.086975 | 61.9034 | 124.6445 | 124.9649 | -125.2029 | -125.267
599.6406 | 125.2533 | -61.8942 | 63.0478 | 0.18791 | 0.011615 | 0.014046 | 0.0036401 | 0.068889 | -0.00057686 | 0.067531 | -61.9949 | 63.0112 | -62.1506 | -62.0773 | 62.764 | -0.004578 | -0.13733 | 0.082397 | 63.0295 | -62.1826 | -0.25635 | -0.036622 | -0.10071 | -0.18311 | -0.28381 | -0.28839 | -0.018311 | 0.15564 | 61.7569 | 61.9766 | 124.6582 | 124.9054 | -0.10071 | 124.9237 | 61.8896 | -0.28839 | 124.9054 | -0.10071 | 61.8896 | 124.6582 | 124.9237 | -125.1984 | -125.2304
600.6406 | 125.1755 | -61.9263 | 63.0615 | 0.16502 | 0.011615 | 0.015541 | 0.0032129 | 0.067394 | -0.0022859 | 0.06988 | -62.0361 | 63.0524 | -62.1826 | -62.1597 | 62.7045 | -0.064087 | -0.022888 | 0.022888 | 63.0295 | -62.2101 | -0.25635 | -0.009155 | -0.10986 | -0.23346 | -0.35706 | -0.28381 | -0.032043 | 0.14648 | 61.9034 | 61.9492 | 124.6307 | 124.9786 | -0.10986 | 124.9557 | 61.8622 | -0.28381 | 124.9786 | -0.10986 | 61.8622 | 124.6307 | 124.9557 | -125.2441 | -125.2716
601.6406 | 125.1801 | -61.9263 | 63.0569 | 0.14976 | 0.012897 | 0.011055 | 0.0038537 | 0.068248 | 0.0013457 | 0.068385 | -62.0224 | 63.0615 | -62.1552 | -62.1689 | 62.6953 | -0.050354 | -0.013733 | 0.022888 | 63.0432 | -62.2009 | -0.22888 | 0.004577 | -0.09613 | -0.24261 | -0.36163 | -0.27466 | -0.013733 | 0.13275 | 61.9125 | 61.9492 | 124.6216 | 124.9878 | -0.09613 | 124.9695 | 61.8759 | -0.27466 | 124.9878 | -0.09613 | 61.8759 | 124.6216 | 124.9695 | -125.2121 | -125.2579
602.6406 | 125.2213 | -61.8713 | 63.0569 | 0.08873 | 0.0088375 | 0.0082779 | -0.0049049 | 0.067608 | 0.00027774 | 0.068385 | -62.027 | 62.97 | -62.1643 | -62.0956 | 62.7731 | 0.041199 | -0.022888 | 0.42114 | 63.0615 | -62.1048 | -0.29297 | -0.086975 | -0.15564 | -0.2243 | -0.28381 | -0.23346 | 0.004577 | 0.13733 | 61.8484 | 62.2925 | 124.6445 | 124.8413 | -0.15564 | 124.9329 | 61.9125 | -0.23346 | 124.8413 | -0.15564 | 61.9125 | 124.6445 | 124.9329 | -125.2213 | -125.1617
603.6406 | 125.1846 | -61.9171 | 63.0661 | 0.15739 | 0.012897 | 0.0095595 | 0.0038537 | 0.066753 | 0.0013457 | 0.070094 | -62.0178 | 63.0341 | -62.1414 | -62.146 | 62.709 | -0.045776 | -0.041199 | 0.036621 | 63.0203 | -62.1964 | -0.2243 | -0.032043 | -0.10071 | -0.22888 | -0.35706 | -0.27924 | -0.045776 | 0.1236 | 61.8759 | 61.9537 | 124.6262 | 124.9512 | -0.10071 | 124.9374 | 61.8713 | -0.27924 | 124.9512 | -0.10071 | 61.8713 | 124.6262 | 124.9374 | -125.2075 | -125.2625
604.6406 | 125.1892 | -61.9263 | 63.0615 | 0.14214 | 0.012683 | 0.014046 | 0.0027855 | 0.066112 | -0.0018585 | 0.067958 | -62.027 | 63.0569 | -62.1506 | -62.1643 | 62.6907 | -0.041199 | -0.018311 | 0.018311 | 63.0615 | -62.2147 | -0.2243 | -0.004577 | -0.10071 | -0.23804 | -0.37079 | -0.28839 | 0 | 0.1236 | 61.908 | 61.9446 | 124.617 | 124.9832 | -0.10071 | 124.9878 | 61.8851 | -0.28839 | 124.9832 | -0.10071 | 61.8851 | 124.617 | 124.9878 | -125.2121 | -125.2762
605.6562 | 125.3037 | -61.853 | 63.0798 | -0.73524 | 0.0081967 | 0.011482 | -0.0010597 | 0.066326 | 6.414e-05 | 0.070094 | -61.9904 | 62.9379 | -62.146 | -61.9995 | 62.8738 | 0.15564 | -0.045776 | 0.28839 | 63.0203 | -62.1094 | -0.29297 | -0.14191 | -0.13733 | -0.14649 | -0.20599 | -0.25635 | -0.059509 | 0.15564 | 61.8073 | 62.1414 | 124.7269 | 124.791 | -0.13733 | 124.8734 | 62.0087 | -0.25635 | 124.791 | -0.13733 | 62.0087 | 124.7269 | 124.8734 | -125.2258 | -125.1892
606.6406 | 125.1892 | -61.9217 | 63.0386 | 0.16502 | 0.012683 | 0.013832 | 0.0047081 | 0.067608 | -0.0018585 | 0.071589 | -62.0178 | 63.0386 | -62.1323 | -62.1506 | 62.7228 | -0.036621 | -0.068665 | 0.050354 | 63.0157 | -62.2009 | -0.21057 | 0 | -0.09613 | -0.22888 | -0.31586 | -0.27924 | -0.022888 | 0.11444 | 61.853 | 61.972 | 124.6445 | 124.9603 | -0.09613 | 124.9374 | 61.8851 | -0.27924 | 124.9603 | -0.09613 | 61.8851 | 124.6445 | 124.9374 | -125.1709 | -125.2396
607.6406 | 125.2625 | -61.9034 | 63.0295 | 0.18028 | 0.0088375 | 0.013405 | -0.00084605 | 0.064617 | 0.00027774 | 0.070521 | -61.972 | 62.9379 | -62.1414 | -62.059 | 62.8052 | 0.041199 | -0.16022 | 0.15106 | 62.9837 | -62.1277 | -0.23804 | -0.091553 | -0.068665 | -0.15564 | -0.2243 | -0.2243 | -0.045776 | 0.16937 | 61.7432 | 62.0544 | 124.7086 | 124.8413 | -0.068665 | 124.8871 | 61.9446 | -0.2243 | 124.8413 | -0.068665 | 61.9446 | 124.7086 | 124.8871 | -125.1709 | -125.1572
608.6406 | 125.1663 | -61.9034 | 63.0981 | 0.13451 | 0.013537 | 0.015328 | 0.0057763 | 0.069316 | 0.00049134 | 0.067317 | -62.0407 | 63.0341 | -62.1368 | -61.8347 | 62.8235 | -0.11902 | 0.11444 | 0.1236 | 63.0661 | -62.1918 | -0.23346 | -0.064087 | -0.13733 | 0.068664 | -0.27466 | -0.28839 | -0.032044 | 0.096131 | 62.0178 | 62.027 | 124.7269 | 124.9374 | -0.13733 | 124.9695 | 61.7844 | -0.28839 | 124.9374 | -0.13733 | 61.7844 | 124.7269 | 124.9695 | -125.235 | -125.2899
609.6406 | 125.1938 | -61.9125 | 63.0432 | 0.12688 | 0.013537 | 0.0099869 | 0.0040673 | 0.067394 | -0.00057686 | 0.069453 | -62.0087 | 63.0478 | -62.1735 | -62.1552 | 62.7045 | -0.041199 | -0.013733 | 0.013733 | 63.0341 | -62.2147 | -0.26093 | 0.004578 | -0.09613 | -0.24261 | -0.33875 | -0.30212 | -0.009155 | 0.16479 | 61.8988 | 61.9263 | 124.617 | 124.9603 | -0.09613 | 124.9466 | 61.8713 | -0.30212 | 124.9603 | -0.09613 | 61.8713 | 124.617 | 124.9466 | -125.2167 | -125.2579
610.6406 | 125.2945 | -61.8988 | 63.0707 | 0.012436 | 0.0069149 | 0.0084915 | -0.0055457 | 0.065899 | -0.00014946 | 0.069667 | -61.9995 | 62.9288 | -62.1414 | -62.0682 | 62.8189 | 0.073242 | -0.064087 | 0.19684 | 63.0249 | -62.1323 | -0.24261 | -0.14191 | -0.10071 | -0.16937 | -0.25177 | -0.23346 | -0.045777 | 0.14191 | 61.8347 | 62.0956 | 124.7177 | 124.8276 | -0.10071 | 124.9237 | 61.972 | -0.23346 | 124.8276 | -0.10071 | 61.972 | 124.7177 | 124.9237 | -125.2121 | -125.2029
611.6406 | 125.1755 | -61.9171 | 63.0753 | 0.15739 | 0.011188 | 0.0095595 | 0.0057763 | 0.065685 | 0.0017731 | 0.071589 | -62.0132 | 63.0798 | -62.1277 | -62.1414 | 62.7045 | -0.045776 | -0.018311 | 0.022888 | 63.0249 | -62.2147 | -0.21057 | 0.004578 | -0.096131 | -0.2243 | -0.37079 | -0.29755 | -0.050354 | 0.11444 | 61.8988 | 61.94 | 124.6216 | 124.9969 | -0.096131 | 124.942 | 61.8713 | -0.29755 | 124.9969 | -0.096131 | 61.8713 | 124.6216 | 124.942 | -125.2029 | -125.2899
612.6406 | 125.3037 | -61.8851 | 63.0341 | 0.13451 | 0.010547 | 0.010201 | 0.0017175 | 0.065471 | -0.0022859 | 0.070308 | -61.9537 | 62.9562 | -62.1185 | -62.0361 | 62.7914 | 0.054932 | -0.17853 | 0.16022 | 62.9929 | -62.1506 | -0.23346 | -0.07782 | -0.068664 | -0.15106 | -0.24262 | -0.2655 | -0.041199 | 0.16479 | 61.7065 | 62.0453 | 124.6765 | 124.8413 | -0.068664 | 124.8779 | 61.94 | -0.2655 | 124.8413 | -0.068664 | 61.94 | 124.6765 | 124.8779 | -125.1526 | -125.1846
613.6406 | 125.2258 | -61.9034 | 63.0524 | 0.14214 | 0.012683 | 0.011482 | 0.0038537 | 0.06718 | -0.00014946 | 0.068599 | -62.0041 | 63.0295 | -62.1552 | -62.1231 | 62.7365 | -0.027466 | -0.07782 | 0.059509 | 63.0203 | -62.2055 | -0.25177 | -0.022888 | -0.10071 | -0.21973 | -0.31586 | -0.30212 | -0.032043 | 0.15106 | 61.8256 | 61.9629 | 124.6399 | 124.9329 | -0.10071 | 124.9237 | 61.8759 | -0.30212 | 124.9329 | -0.10071 | 61.8759 | 124.6399 | 124.9237 | -125.2075 | -125.2579
614.6406 | 125.1572 | -61.9263 | 63.0569 | 0.36339 | 0.0099057 | 0.017677 | 0.0027855 | 0.067394 | -0.00079046 | 0.066035 | -61.9812 | 63.0615 | -62.1552 | -62.1506 | 62.6953 | -0.045776 | -0.018311 | 0.032043 | 63.0341 | -62.2055 | -0.22888 | 0.004577 | -0.054931 | -0.2243 | -0.36163 | -0.27923 | -0.022888 | 0.17395 | 61.908 | 61.9583 | 124.6216 | 124.9878 | -0.054931 | 124.9603 | 61.8805 | -0.27923 | 124.9878 | -0.054931 | 61.8805 | 124.6216 | 124.9603 | -125.2121 | -125.2625
615.6562 | 125.2762 | -61.853 | 63.0249 | -0.14015 | 0.0090513 | 0.015328 | -0.0034095 | 0.069316 | -0.0014313 | 0.069026 | -61.9446 | 62.97 | -62.1048 | -61.9354 | 62.851 | 0.054932 | -0.032043 | 0.3067 | 63.0386 | -62.1185 | -0.25177 | -0.054931 | -0.091553 | -0.082398 | -0.17395 | -0.2655 | 0.013733 | 0.16022 | 61.821 | 62.1597 | 124.704 | 124.823 | -0.091553 | 124.8917 | 61.908 | -0.2655 | 124.823 | -0.091553 | 61.908 | 124.704 | 124.8917 | -125.1297 | -125.1434
616.6406 | 125.1663 | -61.8896 | 63.0844 | 0.14214 | 0.01311 | 0.011696 | 0.0044945 | 0.065044 | -0.0016449 | 0.069026 | -62.0041 | 63.0524 | -62.1552 | -62.1185 | 62.709 | -0.027466 | -0.054932 | 0.059509 | 63.0249 | -62.1964 | -0.2655 | -0.032044 | -0.11444 | -0.22888 | -0.37537 | -0.3067 | -0.05951 | 0.15106 | 61.8347 | 61.9492 | 124.5987 | 124.942 | -0.11444 | 124.9145 | 61.8622 | -0.3067 | 124.942 | -0.11444 | 61.8622 | 124.5987 | 124.9145 | -125.2396 | -125.2808
617.6406 | 125.1755 | -61.8942 | 63.0569 | 0.073471 | 0.0092649 | 0.013619 | -0.0025549 | 0.066967 | -0.00057686 | 0.070521 | -62.0178 | 62.9517 | -62.146 | -62.0911 | 62.764 | 0.022888 | -0.073242 | 0.38452 | 63.0386 | -62.1231 | -0.25177 | -0.10529 | -0.1236 | -0.19684 | -0.29297 | -0.22888 | -0.018311 | 0.12817 | 61.821 | 62.2787 | 124.6582 | 124.8459 | -0.1236 | 124.9329 | 61.9171 | -0.22888 | 124.8459 | -0.1236 | 61.9171 | 124.6582 | 124.9329 | -125.2029 | -125.1801
618.6406 | 125.235 | -61.94 | 63.0478 | 0.17265 | 0.011615 | 0.0093459 | 0.0059899 | 0.066326 | -0.0024995 | 0.069667 | -62.0132 | 63.0249 | -62.1597 | -62.1185 | 62.6953 | -0.022888 | -0.082397 | 0.059509 | 63.002 | -62.1872 | -0.21973 | -0.022889 | -0.073243 | -0.17853 | -0.35248 | -0.24719 | -0.045777 | 0.14648 | 61.8576 | 61.9995 | 124.6353 | 124.9649 | -0.073243 | 124.942 | 61.9171 | -0.24719 | 124.9649 | -0.073243 | 61.9171 | 124.6353 | 124.942 | -125.2075 | -125.235
619.6406 | 125.3082 | -61.9034 | 63.0295 | 0.17265 | 0.012469 | 0.015968 | 0.0044945 | 0.065258 | 0.0015595 | 0.071376 | -61.9537 | 63.002 | -62.1323 | -62.0499 | 62.7686 | 0.022888 | -0.17853 | 0.1236 | 62.9974 | -62.1506 | -0.22888 | -0.027466 | -0.050354 | -0.14648 | -0.26093 | -0.24719 | -0.032043 | 0.17853 | 61.7249 | 62.027 | 124.6719 | 124.9054 | -0.050354 | 124.9008 | 61.9263 | -0.24719 | 124.9054 | -0.050354 | 61.9263 | 124.6719 | 124.9008 | -125.1617 | -125.1801
620.6406 | 125.235 | -61.8713 | 63.0569 | 0.050583 | 0.0054197 | 0.0095595 | -0.0038367 | 0.065685 | -0.0014313 | 0.068385 | -61.9995 | 62.9517 | -62.1323 | -62.0819 | 62.8006 | 0.059509 | -0.064087 | 0.16479 | 63.0112 | -62.1185 | -0.26093 | -0.10529 | -0.12817 | -0.21057 | -0.25635 | -0.24719 | -0.045777 | 0.13275 | 61.8073 | 62.0361 | 124.6719 | 124.823 | -0.12817 | 124.8825 | 61.9308 | -0.24719 | 124.823 | -0.12817 | 61.9308 | 124.6719 | 124.8825 | -125.1892 | -125.1755
621.6406 | 125.2716 | -61.8851 | 63.0295 | 0.18028 | 0.0099057 | 0.014046 | 0.0057763 | 0.063121 | 0.00049134 | 0.068599 | -61.9537 | 62.9791 | -62.1185 | -62.0316 | 62.796 | 0.032043 | -0.1831 | 0.13733 | 63.0112 | -62.1597 | -0.23346 | -0.050354 | -0.068664 | -0.14648 | -0.23346 | -0.27466 | -0.018311 | 0.16479 | 61.702 | 62.0224 | 124.6811 | 124.8642 | -0.068664 | 124.8962 | 61.9171 | -0.27466 | 124.8642 | -0.068664 | 61.9171 | 124.6811 | 124.8962 | -125.148 | -125.1892
622.6406 | 125.2304 | -61.9125 | 63.0249 | 0.0811 | 0.0094785 | 0.01255 | -0.0027687 | 0.064403 | -0.00014946 | 0.070735 | -62.0132 | 62.9517 | -62.1277 | -62.0773 | 62.764 | 0.027466 | -0.09613 | 0.13733 | 62.9974 | -62.1414 | -0.21515 | -0.073242 | -0.10071 | -0.16479 | -0.26093 | -0.22888 | -0.027465 | 0.11444 | 61.8164 | 62.0499 | 124.6765 | 124.8642 | -0.10071 | 124.91 | 61.94 | -0.22888 | 124.8642 | -0.10071 | 61.94 | 124.6765 | 124.91 | -125.1526 | -125.1663
623.6406 | 125.2808 | -61.8805 | 63.0386 | 0.14976 | 0.010547 | 0.011269 | 0.0049219 | 0.062481 | -0.00036306 | 0.069026 | -61.9629 | 63.002 | -62.1094 | -62.059 | 62.7823 | 0.032043 | -0.16022 | 0.11902 | 62.97 | -62.1826 | -0.22888 | -0.036621 | -0.082398 | -0.17853 | -0.25635 | -0.30212 | -0.068664 | 0.14648 | 61.7203 | 61.9995 | 124.6628 | 124.8825 | -0.082398 | 124.8505 | 61.9125 | -0.30212 | 124.8825 | -0.082398 | 61.9125 | 124.6628 | 124.8505 | -125.148 | -125.2213
624.6406 | 125.2808 | -61.8805 | 63.0432 | 0.16502 | 0.011828 | 0.012978 | 0.0049219 | 0.064617 | -0.00057686 | 0.069667 | -61.9629 | 63.002 | -62.1506 | -62.0544 | 62.7548 | 0.009155 | -0.16022 | 0.12817 | 62.9929 | -62.1552 | -0.27008 | -0.041199 | -0.082398 | -0.17395 | -0.28839 | -0.27466 | -0.050354 | 0.18768 | 61.7203 | 62.0087 | 124.6353 | 124.8825 | -0.082398 | 124.8734 | 61.8896 | -0.27466 | 124.8825 | -0.082398 | 61.8896 | 124.6353 | 124.8734 | -125.1938 | -125.1984
625.6406 | 125.2762 | -61.8988 | 63.0295 | 0.22606 | 0.011828 | 0.014473 | 0.0047081 | 0.066112 | 0.00027774 | 0.068599 | -61.972 | 63.0112 | -62.1414 | -62.0636 | 62.7686 | 0.050354 | -0.16022 | 0.1236 | 63.0066 | -62.178 | -0.24261 | -0.018311 | -0.073242 | -0.1648 | -0.26093 | -0.27924 | -0.022888 | 0.16937 | 61.7386 | 62.0224 | 124.6674 | 124.91 | -0.073242 | 124.9054 | 61.9492 | -0.27924 | 124.91 | -0.073242 | 61.9492 | 124.6674 | 124.9054 | -125.1709 | -125.2075
626.6406 | 125.2853 | -61.8896 | 63.0249 | 0.20317 | 0.0096921 | 0.0099869 | 0.0019311 | 0.066967 | 0.00070494 | 0.069239 | -61.9034 | 62.9745 | -62.1002 | -62.027 | 62.8143 | 0.050354 | -0.18768 | 0.15106 | 62.9791 | -62.1506 | -0.21057 | -0.050354 | -0.013733 | -0.13733 | -0.21057 | -0.26093 | -0.045776 | 0.19684 | 61.702 | 62.0407 | 124.704 | 124.8642 | -0.013733 | 124.8688 | 61.94 | -0.26093 | 124.8642 | -0.013733 | 61.94 | 124.704 | 124.8688 | -125.1251 | -125.1755
627.6406 | 125.2533 | -61.8759 | 63.0341 | 0.14214 | 0.0096921 | 0.0095595 | 8.546e-06 | 0.063121 | 0.0013457 | 0.068385 | -61.9537 | 62.9562 | -62.1506 | -62.0453 | 62.7823 | 0.050354 | -0.16479 | 0.14191 | 62.9745 | -62.1597 | -0.27466 | -0.07782 | -0.077819 | -0.16937 | -0.25177 | -0.28381 | -0.05951 | 0.19684 | 61.7111 | 62.0178 | 124.6582 | 124.8322 | -0.077819 | 124.8505 | 61.9263 | -0.28381 | 124.8322 | -0.077819 | 61.9263 | 124.6582 | 124.8505 | -125.1846 | -125.1938
628.6406 | 125.2533 | -61.8942 | 63.0295 | 0.17265 | 0.0099057 | 0.012764 | 0.0032129 | 0.06483 | -0.0014313 | 0.069239 | -61.9858 | 63.002 | -62.146 | -62.0499 | 62.7686 | 0.018311 | -0.17853 | 0.09613 | 62.9883 | -62.1735 | -0.25177 | -0.027466 | -0.091553 | -0.15564 | -0.26093 | -0.27924 | -0.041199 | 0.16022 | 61.7157 | 61.9904 | 124.6628 | 124.8962 | -0.091553 | 124.8825 | 61.9125 | -0.27924 | 124.8962 | -0.091553 | 61.9125 | 124.6628 | 124.8825 | -125.1755 | -125.2029
629.6406 | 125.2625 | -61.9034 | 63.0203 | -1.5592 | 0.0088375 | 0.013405 | 0.0019311 | 0.065899 | -0.0027131 | 0.06988 | -61.9629 | 62.9654 | -62.1048 | -62.0407 | 62.7823 | 0.045776 | -0.18768 | 0.15106 | 62.9745 | -62.1323 | -0.20142 | -0.054932 | -0.05951 | -0.13733 | -0.23804 | -0.22888 | -0.045777 | 0.14191 | 61.7157 | 62.0544 | 124.6857 | 124.8688 | -0.05951 | 124.8779 | 61.9492 | -0.22888 | 124.8688 | -0.05951 | 61.9492 | 124.6857 | 124.8779 | -125.1251 | -125.1526
630.6406 | 125.2716 | -61.8896 | 63.0249 | -0.1783 | 0.0099057 | 0.0095595 | 0.0023583 | 0.065258 | 0.0017731 | 0.069026 | -61.7844 | 62.9883 | -62.0956 | -62.0132 | 62.8098 | 0.036621 | -0.17395 | 0.14648 | 62.9654 | -62.1323 | -0.20599 | -0.036621 | 0.10529 | -0.1236 | -0.21515 | -0.24262 | -0.059509 | 0.31128 | 61.7157 | 62.0361 | 124.6994 | 124.8779 | 0.10529 | 124.855 | 61.9263 | -0.24262 | 124.8779 | 0.10529 | 61.9263 | 124.6994 | 124.855 | -125.1205 | -125.1572
631.6406 | 125.2441 | -61.8759 | 63.0569 | 1.6222 | 0.0099057 | 0.014473 | 0.0023583 | 0.06483 | -0.0037811 | 0.068812 | -61.8118 | 62.9608 | -62.114 | -61.9949 | 62.8235 | 0.050354 | -0.19684 | 0.16022 | 62.9837 | -62.1323 | -0.23804 | -0.096131 | 0.064087 | -0.11902 | -0.23346 | -0.25635 | -0.073242 | 0.30212 | 61.6791 | 62.0361 | 124.6994 | 124.8367 | 0.064087 | 124.8596 | 61.9263 | -0.25635 | 124.8367 | 0.064087 | 61.9263 | 124.6994 | 124.8596 | -125.1709 | -125.1892
632.6406 | 125.2533 | -61.853 | 63.0478 | -0.056229 | 0.0071285 | 0.0087051 | -0.0017005 | 0.063335 | 6.414e-05 | 0.069667 | -61.9904 | 62.9379 | -62.1185 | -62.027 | 62.8052 | 0.10529 | -0.064087 | 0.21973 | 63.0112 | -62.1048 | -0.2655 | -0.10986 | -0.13733 | -0.17395 | -0.24261 | -0.25177 | -0.036622 | 0.12817 | 61.7889 | 62.0728 | 124.6582 | 124.791 | -0.13733 | 124.8642 | 61.9583 | -0.25177 | 124.791 | -0.13733 | 61.9583 | 124.6582 | 124.8642 | -125.1663 | -125.1526
633.6406 | 125.2487 | -61.8576 | 63.0386 | 0.15739 | 0.0086239 | 0.0093459 | 0.0012903 | 0.063121 | -0.0016449 | 0.067103 | -61.9537 | 62.9425 | -62.1094 | -62.059 | 62.7869 | 0.050354 | -0.17853 | 0.15564 | 62.9379 | -62.178 | -0.25177 | -0.09613 | -0.09613 | -0.20142 | -0.25177 | -0.32044 | -0.10071 | 0.15564 | 61.6791 | 62.0132 | 124.6445 | 124.8001 | -0.09613 | 124.7955 | 61.908 | -0.32044 | 124.8001 | -0.09613 | 61.908 | 124.6445 | 124.7955 | -125.148 | -125.2167
634.6406 | 125.2899 | -61.8713 | 63.0341 | 0.12688 | 0.0084103 | 0.014259 | 0.0049219 | 0.066326 | -0.00036306 | 0.069667 | -61.9217 | 62.97 | -62.114 | -61.9263 | 62.7457 | 0.059509 | -0.16479 | 0.13733 | 62.9791 | -62.1414 | -0.24262 | -0.064087 | -0.050354 | -0.054932 | -0.28839 | -0.27008 | -0.054932 | 0.19226 | 61.7065 | 62.0087 | 124.617 | 124.8413 | -0.050354 | 124.8505 | 61.9308 | -0.27008 | 124.8413 | -0.050354 | 61.9308 | 124.617 | 124.8505 | -125.148 | -125.1755
635.6406 | 125.2579 | -61.8576 | 63.0157 | 0.17265 | 0.010974 | 0.01255 | 0.0032129 | 0.065471 | -0.0042085 | 0.070948 | -61.9354 | 62.9608 | -62.1323 | -62.2101 | 62.6175 | 0.059509 | -0.068665 | 0.14648 | 62.9837 | -62.1094 | -0.27466 | -0.054932 | -0.07782 | -0.35248 | -0.39825 | -0.25177 | -0.032043 | 0.19684 | 61.7889 | 62.0041 | 124.4751 | 124.8184 | -0.07782 | 124.8413 | 61.9171 | -0.25177 | 124.8184 | -0.07782 | 61.9171 | 124.4751 | 124.8413 | -125.148 | -125.1251
636.6406 | 125.2945 | -61.8805 | 63.0203 | 0.13451 | 0.0088375 | 0.0089187 | 0.0015039 | 0.06419 | -0.0010041 | 0.06988 | -61.9354 | 62.9791 | -62.1323 | -62.0407 | 62.796 | 0.050354 | -0.18768 | 0.14648 | 62.9379 | -62.1552 | -0.25177 | -0.041199 | -0.054932 | -0.16022 | -0.2243 | -0.27466 | -0.082398 | 0.19684 | 61.6928 | 62.027 | 124.6765 | 124.8596 | -0.054932 | 124.8184 | 61.9308 | -0.27466 | 124.8596 | -0.054932 | 61.9308 | 124.6765 | 124.8184 | -125.1526 | -125.1755
637.6406 | 125.2762 | -61.853 | 63.0432 | -0.21645 | 0.0073423 | 0.0091323 | 0.00064935 | 0.060558 | 6.414e-05 | 0.071803 | -61.8896 | 63.0157 | -62.059 | -62.0682 | 62.8967 | 0.21973 | -0.11902 | 0.26093 | 62.9974 | -62.1277 | -0.20599 | -0.027466 | -0.036621 | -0.21515 | -0.14648 | -0.27466 | -0.045776 | 0.16937 | 61.734 | 62.114 | 124.7498 | 124.8688 | -0.036621 | 124.8505 | 62.0728 | -0.27466 | 124.8688 | -0.036621 | 62.0728 | 124.7498 | 124.8505 | -125.1022 | -125.1709
638.6406 | 125.2625 | -61.8713 | 63.0341 | 0.16502 | 0.01076 | 0.012123 | 0.0040673 | 0.063762 | -0.0020721 | 0.069667 | -61.9446 | 62.9517 | -62.114 | -62.0316 | 62.8143 | 0.054932 | -0.19226 | 0.16022 | 62.97 | -62.1597 | -0.24262 | -0.082398 | -0.073242 | -0.16022 | -0.21973 | -0.28839 | -0.064087 | 0.16937 | 61.6791 | 62.0316 | 124.6857 | 124.823 | -0.073242 | 124.8413 | 61.9263 | -0.28839 | 124.823 | -0.073242 | 61.9263 | 124.6857 | 124.8413 | -125.148 | -125.1938
639.6406 | 125.2625 | -61.8622 | 63.0157 | 0.40153 | 0.011401 | 0.0095595 | 0.0012903 | 0.06419 | -0.0018585 | 0.069667 | -61.8942 | 62.9288 | -62.1185 | -62.027 | 62.8098 | 0.07782 | -0.18768 | 0.16479 | 62.9654 | -62.1506 | -0.25635 | -0.086975 | -0.032043 | -0.16479 | -0.20599 | -0.28839 | -0.050354 | 0.2243 | 61.6745 | 62.027 | 124.6719 | 124.791 | -0.032043 | 124.8276 | 61.94 | -0.28839 | 124.791 | -0.032043 | 61.94 | 124.6719 | 124.8276 | -125.1343 | -125.1663
640.6406 | 125.2533 | -61.8805 | 63.0295 | 0.11925 | 0.0094785 | 0.014046 | -0.00020505 | 0.061199 | -0.0010041 | 0.069026 | -61.9446 | 62.9242 | -62.1689 | -62.0361 | 62.7914 | 0.036621 | -0.16479 | 0.15106 | 62.9608 | -62.1323 | -0.28839 | -0.10529 | -0.064087 | -0.15564 | -0.23804 | -0.25177 | -0.068665 | 0.2243 | 61.7157 | 62.0316 | 124.6719 | 124.8047 | -0.064087 | 124.8413 | 61.9171 | -0.25177 | 124.8047 | -0.064087 | 61.9171 | 124.6719 | 124.8413 | -125.1984 | -125.1617
641.6406 | 125.3037 | -61.8713 | 63.0249 | 0.17265 | 0.010333 | 0.012978 | 0.0019311 | 0.064617 | -0.0022859 | 0.068171 | -62.1735 | 62.9105 | -62.1277 | -62.027 | 62.7686 | 0.064087 | -0.17395 | 0.14648 | 62.9517 | -62.146 | -0.25635 | -0.11444 | -0.30212 | -0.15564 | -0.25635 | -0.27466 | -0.073242 | -0.045776 | 61.6974 | 62.0178 | 124.6399 | 124.7818 | -0.30212 | 124.823 | 61.9354 | -0.27466 | 124.7818 | -0.30212 | 61.9354 | 124.6399 | 124.823 | -125.1526 | -125.1709
642.6406 | 125.2075 | -61.908 | 63.0753 | -1.8262 | 0.0062741 | 0.016182 | -0.0014869 | 0.061626 | 0.0011321 | 0.067103 | -62.146 | 62.9562 | -62.114 | -62.0773 | 62.7686 | 0.045776 | -0.054932 | 0.14191 | 63.002 | -62.1277 | -0.20599 | -0.11902 | -0.23804 | -0.16937 | -0.3067 | -0.21973 | -0.073242 | -0.032043 | 61.853 | 62.0499 | 124.6765 | 124.8642 | -0.23804 | 124.91 | 61.9537 | -0.21973 | 124.8642 | -0.23804 | 61.9537 | 124.6765 | 124.91 | -125.1892 | -125.2029
643.6406 | 125.2579 | -61.8713 | 63.0341 | 0.14976 | 0.012469 | 0.011269 | 0.0034265 | 0.065044 | -0.00079046 | 0.069453 | -61.9537 | 62.9654 | -62.114 | -62.0316 | 62.796 | 0.054932 | -0.1831 | 0.14191 | 62.9379 | -62.1643 | -0.24262 | -0.068665 | -0.082397 | -0.16022 | -0.23804 | -0.29297 | -0.096131 | 0.16022 | 61.6882 | 62.0132 | 124.6674 | 124.8367 | -0.082397 | 124.8093 | 61.9263 | -0.29297 | 124.8367 | -0.082397 | 61.9263 | 124.6674 | 124.8093 | -125.148 | -125.1984
644.6406 | 125.2579 | -61.8896 | 63.0341 | 0.19554 | 0.010974 | 0.0095595 | 0.0029993 | 0.063762 | -0.0014313 | 0.069026 | -61.9492 | 62.9471 | -62.1048 | -62.0316 | 62.8052 | 0.068665 | -0.18768 | 0.15106 | 62.9471 | -62.1552 | -0.21515 | -0.086975 | -0.05951 | -0.14191 | -0.22888 | -0.2655 | -0.086975 | 0.15564 | 61.702 | 62.0407 | 124.6948 | 124.8367 | -0.05951 | 124.8367 | 61.9583 | -0.2655 | 124.8367 | -0.05951 | 61.9583 | 124.6948 | 124.8367 | -125.1389 | -125.1892
645.6406 | 125.2762 | -61.8713 | 63.0386 | -0.048599 | 0.0086239 | 0.0099869 | 0.0034265 | 0.062694 | -0.00036306 | 0.069239 | -61.9537 | 62.9471 | -62.114 | -62.027 | 62.8235 | 0.064087 | -0.19684 | 0.15106 | 62.9791 | -62.146 | -0.24262 | -0.091552 | -0.082397 | -0.15564 | -0.21515 | -0.27466 | -0.059509 | 0.16022 | 61.6745 | 62.0224 | 124.6948 | 124.8184 | -0.082397 | 124.8505 | 61.9354 | -0.27466 | 124.8184 | -0.082397 | 61.9354 | 124.6948 | 124.8505 | -125.1526 | -125.1846
646.6406 | 125.2625 | -61.8713 | 63.0386 | -0.19356 | 0.0090513 | 0.012978 | 0.0042809 | 0.064403 | -0.00036306 | 0.068812 | -61.9263 | 62.9654 | -62.1094 | -62.027 | 62.8098 | 0.068665 | -0.20142 | 0.16022 | 62.9608 | -62.1643 | -0.23804 | -0.073242 | -0.054932 | -0.15564 | -0.22888 | -0.29297 | -0.07782 | 0.1831 | 61.6699 | 62.0316 | 124.6811 | 124.8367 | -0.054932 | 124.8322 | 61.94 | -0.29297 | 124.8367 | -0.054932 | 61.94 | 124.6811 | 124.8322 | -125.148 | -125.2029
647.6406 | 125.2533 | -61.8576 | 63.0478 | -0.21645 | 0.0071285 | 0.012764 | 0.00043575 | 0.064617 | -0.0018585 | 0.070308 | -61.908 | 62.9562 | -62.0956 | -61.9904 | 62.8418 | 0.16479 | -0.041199 | 0.29755 | 63.002 | -62.1094 | -0.23804 | -0.091553 | -0.050354 | -0.13275 | -0.20599 | -0.25177 | -0.045777 | 0.18768 | 61.8164 | 62.1552 | 124.6994 | 124.8138 | -0.050354 | 124.8596 | 62.0224 | -0.25177 | 124.8138 | -0.050354 | 62.0224 | 124.6994 | 124.8596 | -125.1434 | -125.1572
648.6406 | 125.2762 | -61.853 | 63.0386 | 0.19554 | 0.011401 | 0.010841 | 0.0068445 | 0.063762 | -0.0035675 | 0.067958 | -61.9263 | 62.9288 | -62.114 | -61.9858 | 62.764 | 0.07782 | -0.19684 | 0.13733 | 62.9791 | -62.1277 | -0.26093 | -0.10986 | -0.073243 | -0.13275 | -0.27466 | -0.27466 | -0.059509 | 0.18768 | 61.6562 | 61.9904 | 124.617 | 124.7818 | -0.073243 | 124.8322 | 61.9308 | -0.27466 | 124.7818 | -0.073243 | 61.9308 | 124.617 | 124.8322 | -125.1526 | -125.1663
649.6406 | 125.2991 | -61.8622 | 63.0615 | 0.16502 | 0.012042 | 0.014259 | 0.0062035 | 0.064617 | -0.0012177 | 0.068812 | -61.9446 | 62.9517 | -62.1231 | -61.972 | 62.558 | -0.10986 | 0.041199 | 0.22888 | 62.9791 | -62.0956 | -0.26093 | -0.10986 | -0.082397 | -0.10986 | -0.50354 | -0.23346 | -0.082397 | 0.17853 | 61.9034 | 62.0911 | 124.4202 | 124.8138 | -0.082397 | 124.8413 | 61.7523 | -0.23346 | 124.8138 | -0.082397 | 61.7523 | 124.4202 | 124.8413 | -125.1846 | -125.1572
650.6406 | 125.2487 | -61.8576 | 63.0295 | 0.14976 | 0.011615 | 0.014687 | 0.0036401 | 0.065258 | -0.00036306 | 0.069453 | -61.9308 | 62.9562 | -62.114 | -62.027 | 62.8006 | 0.050354 | -0.1831 | 0.16479 | 62.9745 | -62.1323 | -0.25635 | -0.073242 | -0.073242 | -0.16937 | -0.22888 | -0.27466 | -0.054932 | 0.18311 | 61.6745 | 62.0224 | 124.6582 | 124.8138 | -0.073242 | 124.8322 | 61.908 | -0.27466 | 124.8138 | -0.073242 | 61.908 | 124.6582 | 124.8322 | -125.1434 | -125.1617
651.6406 | 125.2579 | -61.8622 | 63.0295 | 0.16502 | 0.011401 | 0.012123 | 0.0029993 | 0.063762 | -0.00057686 | 0.06988 | -61.9308 | 62.9379 | -62.1185 | -62.0316 | 62.8052 | 0.045776 | -0.19226 | 0.15106 | 62.9883 | -62.1414 | -0.25635 | -0.091553 | -0.068664 | -0.16937 | -0.2243 | -0.27923 | -0.041199 | 0.18768 | 61.6699 | 62.0132 | 124.6674 | 124.8001 | -0.068664 | 124.8505 | 61.908 | -0.27923 | 124.8001 | -0.068664 | 61.908 | 124.6674 | 124.8505 | -125.148 | -125.1709
652.6406 | 125.2945 | -61.8988 | 63.0661 | -0.18593 | 0.0084103 | 0.010414 | 0.0010767 | 0.062908 | -0.0080537 | 0.066676 | -61.9034 | 62.9517 | -62.1002 | -61.7523 | 62.5626 | -0.11902 | 0.068665 | 0.21973 | 62.9654 | -62.1231 | -0.20142 | -0.11444 | -0.004577 | 0.14648 | -0.50354 | -0.2243 | -0.10071 | 0.19684 | 61.9675 | 62.1185 | 124.4614 | 124.8505 | -0.004577 | 124.8642 | 61.7798 | -0.2243 | 124.8505 | -0.004577 | 61.7798 | 124.4614 | 124.8642 | -125.1663 | -125.1892
653.6406 | 125.267 | -61.8759 | 63.0295 | 0.26421 | 0.0090513 | 0.011482 | 0.0049219 | 0.063976 | -0.0010041 | 0.067958 | -61.8988 | 62.9654 | -62.0956 | -62.0178 | 62.8006 | 0.054932 | -0.19226 | 0.16022 | 62.9517 | -62.1231 | -0.21973 | -0.064087 | -0.022888 | -0.14191 | -0.22888 | -0.24719 | -0.07782 | 0.19684 | 61.6837 | 62.0361 | 124.6765 | 124.8413 | -0.022888 | 124.8276 | 61.9308 | -0.24719 | 124.8413 | -0.022888 | 61.9308 | 124.6765 | 124.8276 | -125.1251 | -125.1526
654.6406 | 125.2213 | -61.8851 | 63.0157 | 0.12688 | 0.010974 | 0.0097733 | 0.0017175 | 0.063335 | -0.0022859 | 0.070948 | -61.9537 | 62.9196 | -62.1277 | -62.0407 | 62.7869 | 0.064087 | -0.16479 | 0.14648 | 62.9608 | -62.1323 | -0.24261 | -0.09613 | -0.068664 | -0.15564 | -0.22888 | -0.24719 | -0.054932 | 0.17395 | 61.7203 | 62.0316 | 124.6719 | 124.8047 | -0.068664 | 124.8459 | 61.9492 | -0.24719 | 124.8047 | -0.068664 | 61.9492 | 124.6719 | 124.8459 | -125.1434 | -125.148
655.6406 | 125.2441 | -61.8759 | 63.0203 | 0.3405 | 0.01076 | 0.0149 | 0.0010767 | 0.064403 | -0.0020721 | 0.069453 | -61.9171 | 62.9608 | -62.1094 | -62.059 | 62.796 | 0.059509 | -0.18768 | 0.14648 | 62.9837 | -62.1231 | -0.23346 | -0.05951 | -0.041198 | -0.18311 | -0.2243 | -0.24719 | -0.036621 | 0.19226 | 61.6882 | 62.0224 | 124.6719 | 124.8367 | -0.041198 | 124.8596 | 61.9354 | -0.24719 | 124.8367 | -0.041198 | 61.9354 | 124.6719 | 124.8596 | -125.1297 | -125.1434
656.6406 | 125.2899 | -61.8576 | 63.0341 | 0.70671 | 0.0092649 | 0.0084915 | 0.0040673 | 0.066112 | -0.0014313 | 0.069026 | -61.7706 | 62.9379 | -62.114 | -61.9812 | 62.8098 | 0.041199 | -0.20599 | 0.15106 | 62.9608 | -62.1277 | -0.25635 | -0.096131 | 0.086975 | -0.1236 | -0.22431 | -0.27008 | -0.073243 | 0.34332 | 61.6516 | 62.0087 | 124.6674 | 124.7955 | 0.086975 | 124.8184 | 61.8988 | -0.27008 | 124.7955 | 0.086975 | 61.8988 | 124.6674 | 124.8184 | -125.148 | -125.1617
657.6406 | 125.2625 | -61.853 | 63.0524 | -0.048599 | 0.0084103 | 0.014473 | -0.00084605 | 0.063976 | -0.0018585 | 0.068385 | -61.9583 | 62.9425 | -62.1323 | -62.0361 | 62.8281 | 0.09613 | -0.073242 | 0.21973 | 62.9837 | -62.1048 | -0.27924 | -0.10986 | -0.10529 | -0.18311 | -0.2243 | -0.25177 | -0.068664 | 0.17395 | 61.7798 | 62.0728 | 124.6811 | 124.7955 | -0.10529 | 124.8367 | 61.9492 | -0.25177 | 124.7955 | -0.10529 | 61.9492 | 124.6811 | 124.8367 | -125.1846 | -125.1572
658.6406 | 125.2808 | -61.8713 | 63.0569 | 0.14214 | 0.0092649 | 0.010201 | 0.0012903 | 0.064403 | -0.0012177 | 0.068171 | -61.9446 | 62.9288 | -62.114 | -62.0361 | 62.7869 | 0.041199 | -0.16937 | 0.14648 | 62.9471 | -62.1414 | -0.24262 | -0.12817 | -0.073242 | -0.16479 | -0.27008 | -0.27008 | -0.10986 | 0.16937 | 61.702 | 62.0178 | 124.6582 | 124.8001 | -0.073242 | 124.8184 | 61.9125 | -0.27008 | 124.8001 | -0.073242 | 61.9125 | 124.6582 | 124.8184 | -125.1709 | -125.1984
659.6406 | 125.2808 | -61.8805 | 63.0203 | 0.17265 | 0.010547 | 0.013405 | 0.0015039 | 0.06419 | -0.0022859 | 0.069667 | -61.9446 | 62.9379 | -62.114 | -62.0224 | 62.7869 | 0.050354 | -0.20599 | 0.15564 | 62.9745 | -62.1277 | -0.23346 | -0.082398 | -0.064087 | -0.14191 | -0.23346 | -0.24719 | -0.045777 | 0.16937 | 61.6745 | 62.0361 | 124.6674 | 124.8184 | -0.064087 | 124.855 | 61.9308 | -0.24719 | 124.8184 | -0.064087 | 61.9308 | 124.6674 | 124.855 | -125.1343 | -125.148
660.6406 | 125.2762 | -61.8759 | 63.0249 | 0.11925 | 0.010119 | 0.01191 | 0.0027855 | 0.063335 | 6.414e-05 | 0.067531 | -61.9537 | 62.9425 | -62.1277 | -62.0361 | 62.7869 | 0.050354 | -0.17853 | 0.15106 | 62.9517 | -62.146 | -0.25177 | -0.082397 | -0.077819 | -0.16022 | -0.23804 | -0.27008 | -0.073242 | 0.17395 | 61.6974 | 62.027 | 124.6628 | 124.8184 | -0.077819 | 124.8276 | 61.9263 | -0.27008 | 124.8184 | -0.077819 | 61.9263 | 124.6628 | 124.8276 | -125.1526 | -125.1709
661.6406 | 125.235 | -61.8759 | 63.0295 | 0.15739 | 0.011401 | 0.01255 | 0.0010767 | 0.063335 | -0.0018585 | 0.068385 | -61.9766 | 62.9517 | -62.1185 | -62.059 | 62.7777 | 0.036621 | -0.11902 | 0.13733 | 62.9562 | -62.1277 | -0.24261 | -0.07782 | -0.10071 | -0.18311 | -0.25177 | -0.25177 | -0.073242 | 0.14191 | 61.7569 | 62.0132 | 124.6536 | 124.8276 | -0.10071 | 124.8322 | 61.9125 | -0.25177 | 124.8276 | -0.10071 | 61.9125 | 124.6536 | 124.8322 | -125.148 | -125.1572
662.6406 | 125.2487 | -61.8668 | 63.0341 | -0.033341 | 0.0077695 | 0.0091323 | -0.0019141 | 0.063121 | -0.0027131 | 0.069239 | -62.0041 | 62.9425 | -62.1185 | -62.0453 | 62.7914 | 0.091553 | -0.068665 | 0.21057 | 62.9883 | -62.114 | -0.25177 | -0.091553 | -0.13733 | -0.17853 | -0.24262 | -0.24719 | -0.045777 | 0.11444 | 61.7981 | 62.0773 | 124.6582 | 124.8093 | -0.13733 | 124.855 | 61.9583 | -0.24719 | 124.8093 | -0.13733 | 61.9583 | 124.6582 | 124.855 | -125.1526 | -125.148
663.6406 | 125.2533 | -61.8759 | 63.0112 | 0.096359 | 0.0096921 | 0.0095595 | 0.0032129 | 0.064403 | -0.0020721 | 0.068385 | -61.9263 | 62.9333 | -62.1231 | -62.0178 | 62.796 | 0.050354 | -0.18768 | 0.15564 | 62.9517 | -62.1552 | -0.24719 | -0.077819 | -0.050354 | -0.14191 | -0.21515 | -0.27923 | -0.059509 | 0.19684 | 61.6882 | 62.0316 | 124.6719 | 124.8093 | -0.050354 | 124.8276 | 61.9263 | -0.27923 | 124.8093 | -0.050354 | 61.9263 | 124.6719 | 124.8276 | -125.1343 | -125.1663
664.6406 | 125.2167 | -61.8713 | 63.0341 | 0.14976 | 0.0086239 | 0.0087051 | 0.0017175 | 0.06718 | 0.0015595 | 0.067958 | -61.9492 | 62.9471 | -62.1185 | -62.0453 | 62.796 | 0.054932 | -0.16479 | 0.14648 | 62.9608 | -62.1368 | -0.24719 | -0.086975 | -0.07782 | -0.17395 | -0.23804 | -0.2655 | -0.073243 | 0.16937 | 61.7065 | 62.0178 | 124.6674 | 124.8184 | -0.07782 | 124.8322 | 61.9263 | -0.2655 | 124.8184 | -0.07782 | 61.9263 | 124.6674 | 124.8322 | -125.1526 | -125.1709
665.6406 | 125.2533 | -61.8713 | 63.0341 | 0.10399 | 0.0086239 | 0.011055 | 0.0015039 | 0.062694 | 0.0028411 | 0.069239 | -61.94 | 62.9333 | -62.1323 | -62.0407 | 62.7777 | 0.050354 | -0.17395 | 0.16022 | 62.9562 | -62.1277 | -0.26093 | -0.10071 | -0.068664 | -0.16937 | -0.25635 | -0.25635 | -0.07782 | 0.19226 | 61.6974 | 62.0316 | 124.649 | 124.8047 | -0.068664 | 124.8276 | 61.9217 | -0.25635 | 124.8047 | -0.068664 | 61.9217 | 124.649 | 124.8276 | -125.1663 | -125.1617
666.6406 | 125.2487 | -61.8576 | 63.0112 | 0.16502 | 0.01076 | 0.01255 | 0.0015039 | 0.065685 | -0.00079046 | 0.068385 | -61.9492 | 62.9288 | -62.1231 | -62.0224 | 62.7914 | 0.064087 | -0.16937 | 0.15106 | 62.9471 | -62.1414 | -0.2655 | -0.082397 | -0.091553 | -0.16479 | -0.21973 | -0.28381 | -0.064086 | 0.17395 | 61.6882 | 62.0087 | 124.649 | 124.7864 | -0.091553 | 124.8047 | 61.9217 | -0.28381 | 124.7864 | -0.091553 | 61.9217 | 124.649 | 124.8047 | -125.1343 | -125.1526
667.6406 | 125.2121 | -61.8668 | 63.0661 | 0.13451 | 0.0073423 | 0.0076369 | 0.0010767 | 0.062481 | 0.00070494 | 0.067531 | -62.0087 | 62.9288 | -62.0956 | -62.0636 | 62.7594 | 0.036621 | -0.064087 | 0.16022 | 62.9654 | -62.1185 | -0.22888 | -0.13733 | -0.14191 | -0.19684 | -0.3067 | -0.25177 | -0.10071 | 0.086975 | 61.8027 | 62.027 | 124.6262 | 124.7955 | -0.14191 | 124.8322 | 61.9034 | -0.25177 | 124.7955 | -0.14191 | 61.9034 | 124.6262 | 124.8322 | -125.1617 | -125.1846
668.6406 | 125.235 | -61.8439 | 63.0569 | 0.11925 | 0.0096921 | 0.010628 | 0.00086295 | 0.063762 | -0.0014313 | 0.06988 | -61.9858 | 62.9333 | -62.1277 | -62.059 | 62.7548 | 0.027466 | -0.1236 | 0.13275 | 62.9425 | -62.1231 | -0.28381 | -0.1236 | -0.14191 | -0.21515 | -0.30212 | -0.27924 | -0.11444 | 0.14191 | 61.7203 | 61.9766 | 124.5987 | 124.7772 | -0.14191 | 124.7864 | 61.8713 | -0.27924 | 124.7772 | -0.14191 | 61.8713 | 124.5987 | 124.7864 | -125.1846 | -125.1801
669.6406 | 125.267 | -61.8576 | 63.0203 | 0.16502 | 0.0092649 | 0.010414 | 0.0021447 | 0.063121 | -0.00079046 | 0.067317 | -61.9354 | 62.9288 | -62.1323 | -62.0361 | 62.796 | 0.045776 | -0.19226 | 0.15106 | 62.9425 | -62.1368 | -0.27466 | -0.091553 | -0.07782 | -0.17853 | -0.2243 | -0.27924 | -0.07782 | 0.19684 | 61.6653 | 62.0087 | 124.6536 | 124.7864 | -0.07782 | 124.8001 | 61.9034 | -0.27924 | 124.7864 | -0.07782 | 61.9034 | 124.6536 | 124.8001 | -125.1526 | -125.1572
670.6406 | 125.2533 | -61.8805 | 63.0203 | 0.14214 | 0.0079831 | 0.010841 | 0.0029993 | 0.06483 | 0.0017731 | 0.069667 | -61.94 | 62.9333 | -62.1185 | -62.0224 | 62.796 | 0.054932 | -0.1831 | 0.15106 | 62.9288 | -62.1368 | -0.23804 | -0.086975 | -0.059509 | -0.14191 | -0.2243 | -0.25635 | -0.091553 | 0.17853 | 61.6974 | 62.0316 | 124.6765 | 124.8138 | -0.059509 | 124.8093 | 61.9354 | -0.25635 | 124.8138 | -0.059509 | 61.9354 | 124.6765 | 124.8093 | -125.1389 | -125.1572
671.6406 | 125.2304 | -61.8805 | 63.0066 | 0.14214 | 0.0096921 | 0.01255 | 0.0012903 | 0.063335 | -0.00079046 | 0.06988 | -61.972 | 62.9379 | -62.1048 | -62.0499 | 62.7777 | 0.045776 | -0.14648 | 0.14648 | 62.9745 | -62.1002 | -0.2243 | -0.068665 | -0.091553 | -0.16937 | -0.22888 | -0.21973 | -0.032044 | 0.13275 | 61.734 | 62.027 | 124.6582 | 124.8184 | -0.091553 | 124.855 | 61.9263 | -0.21973 | 124.8184 | -0.091553 | 61.9263 | 124.6582 | 124.855 | -125.1114 | -125.1068
672.6406 | 125.3494 | -61.8439 | 63.0341 | -0.16304 | 0.0071285 | 0.012978 | -0.00041865 | 0.062267 | -0.0091217 | 0.070308 | -61.9125 | 62.9425 | -62.1185 | -61.7615 | 62.5442 | -0.11902 | 0.054932 | 0.21973 | 62.9654 | -62.1002 | -0.27466 | -0.091553 | -0.068665 | 0.082397 | -0.48981 | -0.25635 | -0.068665 | 0.20599 | 61.8988 | 62.0636 | 124.3881 | 124.7864 | -0.068665 | 124.8093 | 61.7249 | -0.25635 | 124.7864 | -0.068665 | 61.7249 | 124.3881 | 124.8093 | -125.1526 | -125.1343
673.6406 | 125.2441 | -61.8576 | 63.0203 | 0.16502 | 0.0084103 | 0.010414 | 0.0012903 | 0.063976 | 0.00049134 | 0.069667 | -61.9492 | 62.9333 | -62.1277 | -62.0316 | 62.7869 | 0.050354 | -0.16479 | 0.15106 | 62.9379 | -62.1368 | -0.27008 | -0.086975 | -0.091553 | -0.17395 | -0.23346 | -0.27924 | -0.082398 | 0.17853 | 61.6928 | 62.0087 | 124.6445 | 124.791 | -0.091553 | 124.7955 | 61.908 | -0.27924 | 124.791 | -0.091553 | 61.908 | 124.6445 | 124.7955 | -125.148 | -125.1572
674.6406 | 125.2304 | -61.8713 | 63.0524 | 0.096359 | 0.0099057 | 0.010628 | -0.00063225 | 0.062267 | -0.0018585 | 0.069026 | -62.0041 | 62.9333 | -62.1277 | -62.0636 | 62.7548 | 0.027466 | -0.091553 | 0.1236 | 62.9608 | -62.1414 | -0.25635 | -0.11902 | -0.13275 | -0.19226 | -0.29755 | -0.27008 | -0.091553 | 0.1236 | 61.7798 | 61.9949 | 124.6262 | 124.8047 | -0.13275 | 124.8322 | 61.8988 | -0.27008 | 124.8047 | -0.13275 | 61.8988 | 124.6262 | 124.8322 | -125.1801 | -125.1938
675.6406 | 125.2075 | -61.8896 | 63.0524 | 0.11162 | 0.0096921 | 0.013405 | 0.0012903 | 0.062267 | -0.0014313 | 0.070521 | -61.9949 | 62.9288 | -62.1094 | -62.0544 | 62.7457 | 0.032043 | -0.11902 | 0.12817 | 62.9745 | -62.1231 | -0.21973 | -0.1236 | -0.10529 | -0.16479 | -0.3067 | -0.23346 | -0.07782 | 0.11444 | 61.7706 | 62.0178 | 124.6353 | 124.8184 | -0.10529 | 124.8642 | 61.9217 | -0.23346 | 124.8184 | -0.10529 | 61.9217 | 124.6353 | 124.8642 | -125.1617 | -125.1755
676.6406 | 125.235 | -61.8713 | 63.0295 | 0.14976 | 0.0081967 | 0.010628 | 0.0015039 | 0.062908 | -0.00079046 | 0.067744 | -61.94 | 62.9425 | -62.114 | -62.0087 | 62.796 | 0.045776 | -0.1831 | 0.14191 | 62.9517 | -62.1231 | -0.24262 | -0.086975 | -0.068664 | -0.13733 | -0.23346 | -0.25177 | -0.07782 | 0.17395 | 61.6882 | 62.0132 | 124.6674 | 124.8138 | -0.068664 | 124.823 | 61.9171 | -0.25177 | 124.8138 | -0.068664 | 61.9171 | 124.6674 | 124.823 | -125.1434 | -125.1526
677.6406 | 125.267 | -61.8439 | 63.0707 | 3.3846 | 0.0071285 | 0.0080643 | -0.0021277 | 0.061626 | -0.0010041 | 0.067103 | -61.8668 | 62.9517 | -62.1094 | -61.9675 | 62.8693 | 0.16937 | -0.073242 | 0.28381 | 62.9654 | -62.1231 | -0.2655 | -0.11902 | -0.022888 | -0.1236 | -0.20142 | -0.27924 | -0.10529 | 0.24262 | 61.7706 | 62.1277 | 124.7131 | 124.7955 | -0.022888 | 124.8093 | 62.0132 | -0.27924 | 124.7955 | -0.022888 | 62.0132 | 124.7131 | 124.8093 | -125.1801 | -125.1938
678.6406 | 125.1984 | -61.8759 | 63.0432 | 0.058212 | 0.01076 | 0.0095595 | 0.00064935 | 0.062267 | -0.00036306 | 0.068171 | -61.9629 | 62.9288 | -62.1185 | -62.0499 | 62.764 | 0.036621 | -0.13733 | 0.13733 | 62.9425 | -62.0956 | -0.24261 | -0.11444 | -0.086975 | -0.17395 | -0.27924 | -0.21973 | -0.10071 | 0.15564 | 61.7386 | 62.0132 | 124.6399 | 124.8047 | -0.086975 | 124.8184 | 61.9125 | -0.21973 | 124.8047 | -0.086975 | 61.9125 | 124.6399 | 124.8184 | -125.1617 | -125.1389
679.6406 | 125.2304 | -61.8713 | 63.0203 | 0.042953 | 0.010119 | 0.010201 | 0.0019311 | 0.062053 | 0.00049134 | 0.069453 | -61.9583 | 62.9517 | -62.1277 | -62.027 | 62.764 | 0.036621 | -0.17395 | 0.14648 | 62.9425 | -62.1231 | -0.25635 | -0.068665 | -0.086975 | -0.15564 | -0.25635 | -0.25177 | -0.07782 | 0.16937 | 61.6974 | 62.0178 | 124.6353 | 124.823 | -0.086975 | 124.8138 | 61.908 | -0.25177 | 124.823 | -0.086975 | 61.908 | 124.6353 | 124.8138 | -125.148 | -125.1434
680.6406 | 125.235 | -61.8713 | 63.0341 | 0.14214 | 0.011188 | 0.0089187 | 0.0019311 | 0.062481 | -0.00057686 | 0.068385 | -61.9446 | 62.9471 | -62.1094 | -62.0224 | 62.7914 | 0.054932 | -0.1831 | 0.14648 | 62.9379 | -62.1323 | -0.23804 | -0.086975 | -0.073242 | -0.15106 | -0.24262 | -0.26093 | -0.096131 | 0.16479 | 61.6882 | 62.0178 | 124.6628 | 124.8184 | -0.073242 | 124.8093 | 61.9263 | -0.26093 | 124.8184 | -0.073242 | 61.9263 | 124.6628 | 124.8093 | -125.1434 | -125.1663
681.6406 | 125.2167 | -61.8988 | 63.0249 | 0.18028 | 0.0084103 | 0.012764 | -0.00084605 | 0.063762 | -0.0020721 | 0.068599 | -61.9675 | 62.9013 | -62.1552 | -62.059 | 62.764 | 0.032043 | -0.10529 | 0.11444 | 62.9654 | -62.1414 | -0.25635 | -0.1236 | -0.068664 | -0.16022 | -0.26093 | -0.24261 | -0.059509 | 0.18768 | 61.7935 | 62.0132 | 124.6628 | 124.8001 | -0.068664 | 124.8642 | 61.9308 | -0.24261 | 124.8001 | -0.068664 | 61.9308 | 124.6628 | 124.8642 | -125.1801 | -125.1663
682.6406 | 125.235 | -61.8439 | 63.0249 | -0.056229 | 0.0084103 | 0.0080643 | -0.0017005 | 0.062053 | -0.00079046 | 0.069239 | -61.9537 | 62.9288 | -62.114 | -62.0041 | 62.8326 | 0.13275 | -0.082397 | 0.24261 | 62.9654 | -62.1185 | -0.27008 | -0.09613 | -0.10986 | -0.16022 | -0.19226 | -0.27466 | -0.059509 | 0.16022 | 61.7615 | 62.0865 | 124.6765 | 124.7726 | -0.10986 | 124.8093 | 61.9766 | -0.27466 | 124.7726 | -0.10986 | 61.9766 | 124.6765 | 124.8093 | -125.1389 | -125.1434
683.6406 | 125.2579 | -61.8668 | 63.0157 | -0.14015 | 0.0096921 | 0.011269 | 0.0032129 | 0.065044 | -0.00014946 | 0.069026 | -61.9492 | 62.9471 | -62.114 | -62.0224 | 62.8052 | 0.050354 | -0.1831 | 0.16479 | 62.9608 | -62.1277 | -0.24719 | -0.068664 | -0.082398 | -0.15564 | -0.21057 | -0.26093 | -0.054932 | 0.1648 | 61.6837 | 62.0316 | 124.6719 | 124.8138 | -0.082398 | 124.8276 | 61.9171 | -0.26093 | 124.8138 | -0.082398 | 61.9171 | 124.6719 | 124.8276 | -125.1297 | -125.1434
684.6406 | 125.2396 | -61.8713 | 63.0341 | 0.10399 | 0.0084103 | 0.020668 | 0.0021447 | 0.065044 | -0.0035675 | 0.069239 | -61.9217 | 62.9425 | -62.1597 | -61.9858 | 62.7777 | 0.045776 | -0.15106 | 0.16022 | 62.9745 | -62.1185 | -0.28839 | -0.091553 | -0.050354 | -0.11444 | -0.25635 | -0.24719 | -0.05951 | 0.23804 | 61.7203 | 62.0316 | 124.649 | 124.8138 | -0.050354 | 124.8459 | 61.9171 | -0.24719 | 124.8138 | -0.050354 | 61.9171 | 124.649 | 124.8459 | -125.1938 | -125.1526
685.6406 | 125.2487 | -61.8896 | 63.0341 | 0.18028 | 0.0096921 | 0.010201 | 0.0034265 | 0.064403 | -0.0016449 | 0.06689 | -61.9354 | 62.9425 | -62.114 | -62.0132 | 62.8052 | 0.059509 | -0.17395 | 0.15564 | 62.9471 | -62.1185 | -0.22431 | -0.091553 | -0.045777 | -0.1236 | -0.22888 | -0.22888 | -0.086975 | 0.17853 | 61.7157 | 62.0453 | 124.6948 | 124.8322 | -0.045777 | 124.8367 | 61.9492 | -0.22888 | 124.8322 | -0.045777 | 61.9492 | 124.6948 | 124.8367 | -125.148 | -125.1526
686.6406 | 125.2579 | -61.8713 | 62.9974 | 0.23369 | 0.011188 | 0.015968 | 0.0032129 | 0.062481 | 0.00070494 | 0.068385 | -61.9308 | 62.9471 | -62.0911 | -62.0316 | 62.8052 | 0.064087 | -0.20142 | 0.16022 | 62.9425 | -62.1414 | -0.21973 | -0.050354 | -0.059509 | -0.16022 | -0.19226 | -0.27008 | -0.054932 | 0.16022 | 61.6699 | 62.0316 | 124.6765 | 124.8184 | -0.059509 | 124.8138 | 61.9354 | -0.27008 | 124.8184 | -0.059509 | 61.9354 | 124.6765 | 124.8138 | -125.0885 | -125.1389
687.6406 | 125.2213 | -61.8713 | 63.0341 | -0.04097 | 0.0084103 | 0.0076369 | -0.0023413 | 0.063335 | -0.0010041 | 0.068599 | -61.9904 | 62.9242 | -62.146 | -62.0636 | 62.7777 | 0.050354 | -0.054932 | 0.16022 | 62.97 | -62.1048 | -0.27466 | -0.10986 | -0.11902 | -0.19226 | -0.25635 | -0.23346 | -0.064087 | 0.15564 | 61.8164 | 62.0316 | 124.649 | 124.7955 | -0.11902 | 124.8413 | 61.9217 | -0.23346 | 124.7955 | -0.11902 | 61.9217 | 124.649 | 124.8413 | -125.1801 | -125.1389
688.6406 | 125.2258 | -61.8759 | 63.0341 | 0.15739 | 0.01076 | 0.012123 | 0.00064935 | 0.063549 | 0.00027774 | 0.069667 | -61.9446 | 62.9425 | -62.114 | -62.0316 | 62.7914 | 0.068665 | -0.17853 | 0.14191 | 62.9379 | -62.1506 | -0.23804 | -0.091553 | -0.068664 | -0.15564 | -0.24262 | -0.27466 | -0.096131 | 0.16937 | 61.6974 | 62.0178 | 124.6674 | 124.8184 | -0.068664 | 124.8138 | 61.9446 | -0.27466 | 124.8184 | -0.068664 | 61.9446 | 124.6674 | 124.8138 | -125.148 | -125.1846
689.6406 | 125.267 | -61.8622 | 62.9929 | 0.26421 | 0.01076 | 0.0093459 | 0.00086295 | 0.066539 | 0.0011321 | 0.067744 | -61.9308 | 62.9288 | -62.1185 | -62.0087 | 62.8006 | 0.068665 | -0.21515 | 0.15106 | 62.9517 | -62.1323 | -0.25635 | -0.064087 | -0.068664 | -0.14648 | -0.19226 | -0.27008 | -0.041199 | 0.18768 | 61.647 | 62.0132 | 124.6628 | 124.791 | -0.068664 | 124.8138 | 61.9308 | -0.27008 | 124.791 | -0.068664 | 61.9308 | 124.6628 | 124.8138 | -125.1114 | -125.1251
690.6406 | 125.2258 | -61.8668 | 62.9974 | 0.2108 | 0.011828 | 0.011055 | 0.0034265 | 0.066326 | -0.0027131 | 0.069667 | -61.9583 | 62.9837 | -62.1231 | -62.0453 | 62.7502 | 0.036621 | -0.15564 | 0.10529 | 62.9791 | -62.1689 | -0.25635 | -0.013733 | -0.091553 | -0.17853 | -0.24719 | -0.30212 | -0.018311 | 0.1648 | 61.7111 | 61.972 | 124.617 | 124.8505 | -0.091553 | 124.8459 | 61.9034 | -0.30212 | 124.8505 | -0.091553 | 61.9034 | 124.617 | 124.8459 | -125.1205 | -125.1663
691.6406 | 125.1617 | -61.8896 | 63.0432 | 0.11162 | 0.012469 | 0.010841 | 0.0076989 | 0.06483 | -0.0010041 | 0.069667 | -61.9858 | 63.002 | -62.1506 | -62.0911 | 62.7548 | -0.009155 | -0.10986 | 0.059509 | 62.9837 | -62.1689 | -0.26093 | -0.041199 | -0.096131 | -0.20142 | -0.28839 | -0.27924 | -0.059509 | 0.16479 | 61.7798 | 61.9492 | 124.6445 | 124.8917 | -0.096131 | 124.8734 | 61.8805 | -0.27924 | 124.8917 | -0.096131 | 61.8805 | 124.6445 | 124.8734 | -125.1938 | -125.2121
692.6406 | 125.2533 | -61.8576 | 63.0203 | -0.056229 | 0.0090513 | 0.0093459 | -0.0010597 | 0.065471 | -0.00079046 | 0.068385 | -61.9949 | 62.9517 | -62.114 | -62.059 | 62.796 | 0.059509 | -0.064087 | 0.16937 | 62.9929 | -62.1094 | -0.25635 | -0.068665 | -0.13733 | -0.20142 | -0.2243 | -0.25177 | -0.027466 | 0.11902 | 61.7935 | 62.027 | 124.6536 | 124.8093 | -0.13733 | 124.8505 | 61.9171 | -0.25177 | 124.8093 | -0.13733 | 61.9171 | 124.6536 | 124.8505 | -125.1343 | -125.1297
693.6406 | 125.1938 | -61.8851 | 63.0386 | 0.16502 | 0.011188 | 0.011482 | 0.0066309 | 0.063549 | -0.00014946 | 0.069239 | -61.9766 | 63.0112 | -62.1231 | -62.0682 | 62.7365 | 0 | -0.15564 | 0.086975 | 62.9608 | -62.1552 | -0.23804 | -0.027466 | -0.091553 | -0.1831 | -0.30212 | -0.27008 | -0.07782 | 0.14648 | 61.7294 | 61.972 | 124.6216 | 124.8962 | -0.091553 | 124.8459 | 61.8851 | -0.27008 | 124.8962 | -0.091553 | 61.8851 | 124.6216 | 124.8459 | -125.1617 | -125.1938
694.6406 | 125.1892 | -61.9125 | 63.0478 | 0.11925 | 0.010974 | 0.014473 | 0.0057763 | 0.066539 | -0.0020721 | 0.067103 | -61.9995 | 63.0249 | -62.1231 | -62.0911 | 62.6999 | -0.013733 | -0.073242 | 0.045776 | 62.9883 | -62.1597 | -0.21057 | -0.022889 | -0.086975 | -0.17853 | -0.3479 | -0.24719 | -0.05951 | 0.1236 | 61.8393 | 61.9583 | 124.6124 | 124.9374 | -0.086975 | 124.9008 | 61.8988 | -0.24719 | 124.9374 | -0.086975 | 61.8988 | 124.6124 | 124.9008 | -125.1709 | -125.2075
695.6406 | 125.2167 | -61.8805 | 63.0295 | 0.21843 | 0.013324 | 0.010414 | 0.0032129 | 0.065899 | -0.0010041 | 0.069026 | -61.972 | 62.9929 | -62.1277 | -62.059 | 62.7502 | 0.018311 | -0.14191 | 0.10529 | 62.9791 | -62.1735 | -0.24719 | -0.036621 | -0.091553 | -0.17853 | -0.27924 | -0.29297 | -0.050354 | 0.15564 | 61.7386 | 61.9858 | 124.6307 | 124.8734 | -0.091553 | 124.8596 | 61.8988 | -0.29297 | 124.8734 | -0.091553 | 61.8988 | 124.6307 | 124.8596 | -125.1572 | -125.2029
696.6406 | 125.1892 | -61.8942 | 63.0341 | 0.19554 | 0.01311 | 0.014259 | 0.0059899 | 0.069744 | -0.0022859 | 0.068171 | -61.9949 | 63.0203 | -62.1323 | -62.0819 | 62.7411 | -0.013733 | -0.086975 | 0.059509 | 63.002 | -62.178 | -0.23804 | -0.013733 | -0.10071 | -0.18768 | -0.29297 | -0.28381 | -0.032044 | 0.13733 | 61.8073 | 61.9537 | 124.6353 | 124.9146 | -0.10071 | 124.8962 | 61.8805 | -0.28381 | 124.9146 | -0.10071 | 61.8805 | 124.6353 | 124.8962 | -125.1663 | -125.2121
697.6406 | 125.2625 | -61.8622 | 62.9974 | 0.24132 | 0.010333 | 0.011269 | 0.00043575 | 0.067608 | 6.414e-05 | 0.069453 | -61.9125 | 62.9654 | -62.1185 | -62.0132 | 62.796 | 0.064087 | -0.1831 | 0.14191 | 62.97 | -62.1094 | -0.25635 | -0.032044 | -0.050354 | -0.15106 | -0.20142 | -0.24719 | -0.027466 | 0.20599 | 61.6791 | 62.0041 | 124.6582 | 124.8276 | -0.050354 | 124.8322 | 61.9263 | -0.24719 | 124.8276 | -0.050354 | 61.9263 | 124.6582 | 124.8322 | -125.116 | -125.1068
698.6406 | 125.1572 | -61.9171 | 63.0432 | 0.18791 | 0.011615 | 0.0149 | 0.0042809 | 0.066539 | 0.00049134 | 0.069667 | -62.0041 | 63.0341 | -62.1506 | -62.1277 | 62.6724 | -0.045776 | -0.027466 | 0.022888 | 63.002 | -62.1826 | -0.23346 | -0.009155 | -0.086975 | -0.21057 | -0.37079 | -0.2655 | -0.041199 | 0.14648 | 61.8896 | 61.94 | 124.5895 | 124.9512 | -0.086975 | 124.9191 | 61.8713 | -0.2655 | 124.9512 | -0.086975 | 61.8713 | 124.5895 | 124.9191 | -125.1938 | -125.2258
699.6406 | 125.1526 | -61.9171 | 63.0661 | -0.32326 | 0.011615 | 0.015968 | 0.0047081 | 0.067394 | -0.0022859 | 0.068599 | -61.8073 | 63.0386 | -62.1002 | -62.1094 | 62.677 | -0.045776 | 0.018311 | 0.022888 | 63.0203 | -62.1643 | -0.18311 | -0.027466 | 0.10986 | -0.19226 | -0.3891 | -0.24719 | -0.045776 | 0.29297 | 61.9354 | 61.94 | 124.5941 | 124.9557 | 0.10986 | 124.9374 | 61.8713 | -0.24719 | 124.9557 | 0.10986 | 61.8713 | 124.5941 | 124.9374 | -125.1663 | -125.2304
700.6406 | 125.1984 | -61.8851 | 63.0249 | 0.20317 | 0.012042 | 0.011696 | 0.0053491 | 0.067608 | -0.00079046 | 0.071162 | -61.9812 | 63.0203 | -62.1323 | -62.0956 | 62.7502 | -0.004578 | -0.10071 | 0.064087 | 62.9974 | -62.146 | -0.24719 | -0.004577 | -0.09613 | -0.21057 | -0.27466 | -0.26092 | -0.027465 | 0.15106 | 61.7844 | 61.9492 | 124.6353 | 124.9054 | -0.09613 | 124.8825 | 61.8805 | -0.26092 | 124.9054 | -0.09613 | 61.8805 | 124.6353 | 124.8825 | -125.1572 | -125.1709
701.6406 | 125.116 | -61.9125 | 63.0707 | 0.042953 | 0.011188 | 0.01255 | 0.0032129 | 0.067608 | -0.0018585 | 0.069026 | -61.9629 | 63.0615 | -62.1185 | -62.1002 | 62.6999 | -0.013733 | 0.036621 | 0.059509 | 63.0295 | -62.1689 | -0.20599 | -0.009156 | -0.050354 | -0.18768 | -0.37079 | -0.25635 | -0.041199 | 0.15564 | 61.9492 | 61.972 | 124.6124 | 124.9741 | -0.050354 | 124.942 | 61.8988 | -0.25635 | 124.9741 | -0.050354 | 61.8988 | 124.6124 | 124.942 | -125.1892 | -125.2396
702.6406 | 125.1434 | -61.9217 | 63.0249 | 0.16502 | 0.012897 | 0.011269 | 0.0029993 | 0.069316 | -0.0010041 | 0.067958 | -61.9995 | 63.0478 | -62.1368 | -62.1277 | 62.7182 | -0.041199 | -0.013733 | 0.027466 | 63.0432 | -62.1872 | -0.21515 | 0.022889 | -0.07782 | -0.20599 | -0.3067 | -0.2655 | 0.018311 | 0.13733 | 61.908 | 61.9492 | 124.6399 | 124.9695 | -0.07782 | 124.9649 | 61.8805 | -0.2655 | 124.9695 | -0.07782 | 61.8805 | 124.6399 | 124.9649 | -125.1617 | -125.2121
703.6406 | 125.1205 | -61.9125 | 63.0707 | 0.027695 | 0.012256 | 0.014259 | 0.0040673 | 0.068248 | -0.00057686 | 0.067958 | -61.9766 | 63.0753 | -62.146 | -62.1094 | 62.6907 | -0.036621 | 0.045776 | 0.041199 | 63.0295 | -62.1689 | -0.23346 | 0.004577 | -0.064087 | -0.19684 | -0.37994 | -0.25635 | -0.041199 | 0.16937 | 61.9583 | 61.9537 | 124.6033 | 124.9878 | -0.064087 | 124.942 | 61.8759 | -0.25635 | 124.9878 | -0.064087 | 61.8759 | 124.6033 | 124.942 | -125.2167 | -125.2396
704.6406 | 125.1709 | -61.8942 | 63.0524 | -0.025711 | 0.012042 | 0.016609 | 0.0038537 | 0.068035 | -0.0018585 | 0.068385 | -61.9263 | 63.0615 | -62.1185 | -62.0544 | 62.7502 | 0.064087 | 0.018311 | 0.14191 | 63.0569 | -62.1597 | -0.2243 | 0.009155 | -0.032044 | -0.16022 | -0.30212 | -0.2655 | 0.004578 | 0.19226 | 61.9125 | 62.0361 | 124.6445 | 124.9557 | -0.032044 | 124.9512 | 61.9583 | -0.2655 | 124.9557 | -0.032044 | 61.9583 | 124.6445 | 124.9512 | -125.1709 | -125.2121
705.6406 | 125.1617 | -61.8942 | 63.0661 | -0.048599 | 0.011401 | 0.012123 | 0.0032129 | 0.070171 | -0.0012177 | 0.070308 | -61.9492 | 63.0844 | -62.1094 | -62.0773 | 62.7457 | 0.041199 | 0.036621 | 0.11902 | 63.0524 | -62.1506 | -0.21515 | 0.018311 | -0.054932 | -0.18311 | -0.32043 | -0.25635 | -0.013733 | 0.16022 | 61.9308 | 62.0132 | 124.6399 | 124.9786 | -0.054932 | 124.9466 | 61.9354 | -0.25635 | 124.9786 | -0.054932 | 61.9354 | 124.6399 | 124.9466 | -125.1755 | -125.2167
706.6562 | 125.2258 | -61.8668 | 63.0341 | -0.063858 | 0.0079831 | 0.011269 | -0.0059729 | 0.066753 | -0.0020721 | 0.071589 | -62.0178 | 62.9333 | -62.1185 | -62.1048 | 62.7823 | 0.054932 | -0.036621 | 0.16022 | 63.0157 | -62.1277 | -0.25177 | -0.10071 | -0.15106 | -0.23804 | -0.25177 | -0.26093 | -0.018311 | 0.10071 | 61.8301 | 62.027 | 124.649 | 124.8001 | -0.15106 | 124.8825 | 61.9217 | -0.26093 | 124.8001 | -0.15106 | 61.9217 | 124.649 | 124.8825 | -125.1526 | -125.1617
707.6406 | 125.2121 | -61.9034 | 63.0341 | 0.17265 | 0.011828 | 0.016182 | 0.0038537 | 0.066539 | -0.00057686 | 0.070735 | -61.9949 | 63.002 | -62.1185 | -62.1002 | 62.6999 | -0.013733 | -0.09613 | 0.073242 | 63.0112 | -62.1826 | -0.21515 | -0.032044 | -0.091553 | -0.19684 | -0.33417 | -0.27924 | -0.022889 | 0.1236 | 61.8073 | 61.9766 | 124.6033 | 124.9054 | -0.091553 | 124.9146 | 61.8896 | -0.27924 | 124.9054 | -0.091553 | 61.8896 | 124.6033 | 124.9146 | -125.1526 | -125.2167
708.6406 | 125.1755 | -61.908 | 63.0707 | -0.14778 | 0.010333 | 0.012978 | 0.0044945 | 0.065685 | -0.0012177 | 0.07458 | -61.9034 | 63.0524 | -62.1094 | -62.2513 | 62.5992 | 0.10986 | 0.050354 | 0.16937 | 63.0386 | -62.1872 | -0.20142 | -0.018311 | 0.004578 | -0.34332 | -0.4715 | -0.27924 | -0.032044 | 0.20599 | 61.9583 | 62.0773 | 124.5071 | 124.9603 | 0.004578 | 124.9466 | 62.0178 | -0.27924 | 124.9603 | 0.004578 | 62.0178 | 124.5071 | 124.9466 | -125.1801 | -125.2579
709.6406 | 125.1526 | -61.8896 | 63.0432 | -0.04097 | 0.011188 | 0.015541 | 0.0062035 | 0.06718 | 6.414e-05 | 0.067744 | -61.9171 | 63.0524 | -62.1185 | -62.0682 | 62.7502 | 0.082397 | 0.032043 | 0.16022 | 63.0295 | -62.1735 | -0.22888 | 0.009155 | -0.027466 | -0.17853 | -0.29297 | -0.28381 | -0.013733 | 0.20142 | 61.9217 | 62.0499 | 124.6399 | 124.942 | -0.027466 | 124.9191 | 61.972 | -0.28381 | 124.942 | -0.027466 | 61.972 | 124.6399 | 124.9191 | -125.1617 | -125.2167
710.6406 | 125.1709 | -61.9308 | 63.0157 | 0.14214 | 0.012897 | 0.012978 | 0.0044945 | 0.06718 | -0.00079046 | 0.068171 | -61.9904 | 63.0432 | -62.1414 | -62.1094 | 62.709 | -0.018311 | -0.045776 | 0.059509 | 63.0295 | -62.1735 | -0.21057 | 0.027466 | -0.059509 | -0.17853 | -0.3067 | -0.24262 | 0.013733 | 0.15106 | 61.8851 | 61.9904 | 124.6399 | 124.9741 | -0.059509 | 124.9603 | 61.9125 | -0.24262 | 124.9741 | -0.059509 | 61.9125 | 124.6399 | 124.9603 | -125.1572 | -125.1892
711.6562 | 125.2396 | -61.8622 | 63.0432 | 0.14214 | 0.0088375 | 0.0097733 | -0.0029823 | 0.066967 | -0.0014313 | 0.069026 | -61.94 | 62.9517 | -62.1368 | -62.0407 | 62.7777 | 0.059509 | -0.15564 | 0.15564 | 62.97 | -62.1368 | -0.27466 | -0.091553 | -0.077819 | -0.17853 | -0.2655 | -0.27466 | -0.073242 | 0.19684 | 61.7065 | 62.0178 | 124.6399 | 124.8138 | -0.077819 | 124.8322 | 61.9217 | -0.27466 | 124.8138 | -0.077819 | 61.9217 | 124.6399 | 124.8322 | -125.1801 | -125.1801
712.6406 | 125.1205 | -61.8851 | 63.0478 | 0.096359 | 0.011401 | 0.011482 | 0.0029993 | 0.066326 | 0.00091854 | 0.068812 | -62.0178 | 63.0112 | -62.1277 | -62.1643 | 62.6724 | -0.050354 | 0 | 0.027466 | 63.0066 | -62.1872 | -0.24261 | -0.036622 | -0.13275 | -0.27924 | -0.37537 | -0.30212 | -0.041199 | 0.10986 | 61.8851 | 61.9125 | 124.5575 | 124.8962 | -0.13275 | 124.8917 | 61.8347 | -0.30212 | 124.8962 | -0.13275 | 61.8347 | 124.5575 | 124.8917 | -125.1755 | -125.235
713.6406 | 125.148 | -61.8805 | 63.0753 | -0.26222 | 0.011615 | 0.015541 | 0.0023583 | 0.06483 | -0.0018585 | 0.06689 | -61.9492 | 63.0753 | -62.114 | -62.059 | 62.7502 | 0.086975 | 0.086975 | 0.18768 | 63.0524 | -62.1597 | -0.23346 | 0 | -0.068665 | -0.17853 | -0.32501 | -0.27924 | -0.022888 | 0.1648 | 61.9675 | 62.0682 | 124.6307 | 124.9557 | -0.068665 | 124.9329 | 61.9675 | -0.27924 | 124.9557 | -0.068665 | 61.9675 | 124.6307 | 124.9329 | -125.1892 | -125.235
714.6406 | 125.1617 | -61.8851 | 63.1073 | -0.18593 | 0.012256 | 0.01191 | 0.0036401 | 0.067394 | 0.00049134 | 0.070094 | -61.9675 | 63.0753 | -62.1231 | -62.0819 | 62.7411 | 0.064087 | 0.10529 | 0.17853 | 63.0569 | -62.1368 | -0.23804 | -0.032044 | -0.082397 | -0.19684 | -0.36621 | -0.25177 | -0.050354 | 0.15564 | 61.9904 | 62.0636 | 124.6262 | 124.9603 | -0.082397 | 124.942 | 61.9492 | -0.25177 | 124.9603 | -0.082397 | 61.9492 | 124.6262 | 124.942 | -125.2304 | -125.2441
715.6562 | 125.1984 | -61.8576 | 63.0615 | 0.12688 | 0.012469 | 0.013832 | 0.0019311 | 0.066967 | -0.00014946 | 0.068385 | -61.9308 | 62.9929 | -62.114 | -62.0499 | 62.8418 | 0.009155 | -0.37537 | 0.37079 | 62.9837 | -62.1506 | -0.25635 | -0.068664 | -0.073242 | -0.19226 | -0.21973 | -0.29297 | -0.077819 | 0.18311 | 61.4822 | 62.2284 | 124.6994 | 124.8505 | -0.073242 | 124.8413 | 61.8668 | -0.29297 | 124.8505 | -0.073242 | 61.8668 | 124.6994 | 124.8413 | -125.1755 | -125.2121
716.6562 | 125.1984 | -61.8393 | 63.0844 | 0.096359 | 0.0069149 | 0.013405 | -0.0029823 | 0.066753 | -0.00014946 | 0.071589 | -61.9858 | 62.9333 | -62.1231 | -62.0773 | 62.7548 | 0.032043 | -0.086975 | 0.14191 | 62.9929 | -62.1277 | -0.28381 | -0.15106 | -0.14648 | -0.23804 | -0.32959 | -0.28839 | -0.091553 | 0.13733 | 61.7523 | 61.9812 | 124.5941 | 124.7726 | -0.14648 | 124.8322 | 61.8713 | -0.28839 | 124.7726 | -0.14648 | 61.8713 | 124.5941 | 124.8322 | -125.2075 | -125.2121
717.6406 | 125.1297 | -61.8759 | 63.0524 | 0.18028 | 0.012897 | 0.015328 | 0.0047081 | 0.065685 | -0.00079046 | 0.067531 | -62.0041 | 63.0341 | -62.146 | -62.1277 | 62.677 | -0.041199 | -0.018311 | 0.036621 | 63.002 | -62.2055 | -0.27008 | -0.01831 | -0.12817 | -0.25177 | -0.37537 | -0.32959 | -0.050354 | 0.14191 | 61.8576 | 61.9125 | 124.5529 | 124.91 | -0.12817 | 124.8779 | 61.8347 | -0.32959 | 124.91 | -0.12817 | 61.8347 | 124.5529 | 124.8779 | -125.1984 | -125.2579
718.6406 | 125.1617 | -61.8851 | 63.089 | -0.26985 | 0.011828 | 0.013191 | -0.0012733 | 0.063549 | -0.0027131 | 0.071589 | -61.9904 | 63.0432 | -62.1048 | -62.233 | 62.5854 | 0.059509 | 0.10071 | 0.13275 | 63.0615 | -62.1597 | -0.21973 | -0.045776 | -0.10528 | -0.3479 | -0.50354 | -0.27466 | -0.027466 | 0.11444 | 61.9858 | 62.0178 | 124.4705 | 124.9283 | -0.10528 | 124.9466 | 61.9446 | -0.27466 | 124.9283 | -0.10528 | 61.9446 | 124.4705 | 124.9466 | -125.1938 | -125.2487
719.6406 | 125.148 | -61.8896 | 63.0798 | -0.27748 | 0.0099057 | 0.0091323 | 0.00022215 | 0.065258 | -0.00057686 | 0.071376 | -61.9858 | 63.0341 | -62.1185 | -62.0819 | 62.7457 | 0.064087 | 0.12817 | 0.16937 | 63.0615 | -62.1552 | -0.22888 | -0.045776 | -0.096131 | -0.19226 | -0.33417 | -0.2655 | -0.018311 | 0.13275 | 62.0178 | 62.059 | 124.6353 | 124.9237 | -0.096131 | 124.9512 | 61.9537 | -0.2655 | 124.9237 | -0.096131 | 61.9537 | 124.6353 | 124.9512 | -125.1984 | -125.235
720.6562 | 125.2487 | -61.8622 | 63.0341 | 0.15739 | 0.010547 | 0.011696 | 0.0015039 | 0.066539 | -0.00057686 | 0.069667 | -61.9171 | 62.97 | -62.1185 | -62.0911 | 62.9288 | 0.20599 | -0.21057 | 0.1831 | 63.002 | -62.1094 | -0.25635 | -0.064087 | -0.054931 | -0.22888 | -0.10529 | -0.24719 | -0.032044 | 0.20142 | 61.6516 | 62.0453 | 124.791 | 124.8322 | -0.054931 | 124.8642 | 62.0682 | -0.24719 | 124.8322 | -0.054931 | 62.0682 | 124.791 | 124.8642 | -125.1526 | -125.1434
721.6562 | 125.1709 | -61.908 | 63.0341 | 0.14976 | 0.011188 | 0.011055 | 0.0032129 | 0.06419 | -0.0010041 | 0.070948 | -61.9995 | 63.002 | -62.1323 | -62.114 | 62.709 | -0.032043 | -0.064087 | 0.064087 | 63.0341 | -62.178 | -0.2243 | -0.032044 | -0.091553 | -0.20599 | -0.32501 | -0.27008 | 0 | 0.13275 | 61.8439 | 61.972 | 124.617 | 124.91 | -0.091553 | 124.942 | 61.8759 | -0.27008 | 124.91 | -0.091553 | 61.8759 | 124.617 | 124.942 | -125.1663 | -125.2121
722.6406 | 125.1663 | -61.908 | 63.0707 | -0.010452 | 0.011401 | 0.0084915 | 0.0068445 | 0.065899 | -0.0016449 | 0.06988 | -61.9263 | 63.0203 | -62.1185 | -62.0453 | 62.7365 | 0.041199 | 0.027466 | 0.13733 | 63.0432 | -62.1597 | -0.21057 | -0.050354 | -0.018311 | -0.13733 | -0.33417 | -0.25177 | -0.027466 | 0.19226 | 61.9354 | 62.0453 | 124.6445 | 124.9283 | -0.018311 | 124.9512 | 61.9492 | -0.25177 | 124.9283 | -0.018311 | 61.9492 | 124.6445 | 124.9512 | -125.1892 | -125.2304
723.6406 | 125.1526 | -61.8759 | 63.0936 | -0.21645 | 0.0092649 | 0.0091323 | 0.0019311 | 0.066967 | -0.00036306 | 0.069667 | -61.9812 | 63.0203 | -62.1231 | -62.0728 | 62.7319 | 0.064087 | 0.11444 | 0.16479 | 63.0981 | -62.1506 | -0.24719 | -0.073242 | -0.10529 | -0.19684 | -0.36163 | -0.27466 | 0.004578 | 0.14191 | 61.9904 | 62.0407 | 124.6078 | 124.8962 | -0.10529 | 124.9741 | 61.94 | -0.27466 | 124.8962 | -0.10529 | 61.94 | 124.6078 | 124.9741 | -125.2167 | -125.2441
724.6406 | 125.1205 | -61.908 | 63.0844 | -0.24696 | 0.01076 | 0.011055 | -0.0038367 | 0.065685 | 0.00091854 | 0.068812 | -61.9995 | 63.0341 | -62.114 | -62.1323 | 62.7777 | 0.032043 | 0.13275 | 0.17853 | 63.0707 | -62.1323 | -0.20599 | -0.050354 | -0.091553 | -0.2243 | -0.3067 | -0.2243 | -0.013733 | 0.11444 | 62.0407 | 62.0865 | 124.6857 | 124.942 | -0.091553 | 124.9786 | 61.94 | -0.2243 | 124.942 | -0.091553 | 61.94 | 124.6857 | 124.9786 | -125.1984 | -125.2167
725.6562 | 125.2899 | -61.8484 | 63.0386 | -0.21645 | 0.0064877 | 0.0095595 | -0.0046913 | 0.065899 | -0.0037811 | 0.067103 | -61.8896 | 62.9517 | -62.0956 | -61.7935 | 62.5076 | -0.11902 | 0.054932 | 0.21057 | 63.0203 | -62.1048 | -0.24719 | -0.086975 | -0.041198 | 0.054932 | -0.53101 | -0.25635 | -0.01831 | 0.20599 | 61.9034 | 62.059 | 124.3561 | 124.8001 | -0.041198 | 124.8688 | 61.7294 | -0.25635 | 124.8001 | -0.041198 | 61.7294 | 124.3561 | 124.8688 | -125.1343 | -125.1434
726.6406 | 125.2075 | -61.8622 | 63.0798 | -0.24696 | 0.0079831 | 0.0065689 | -0.0017005 | 0.065685 | 0.0011321 | 0.067744 | -61.9125 | 62.9883 | -62.0911 | -62.0132 | 62.8143 | 0.14191 | 0.032043 | 0.26093 | 63.0295 | -62.1185 | -0.22888 | -0.091553 | -0.050354 | -0.15106 | -0.2655 | -0.25635 | -0.050354 | 0.17853 | 61.8942 | 62.1231 | 124.6765 | 124.8505 | -0.050354 | 124.8917 | 62.0041 | -0.25635 | 124.8505 | -0.050354 | 62.0041 | 124.6765 | 124.8917 | -125.1709 | -125.1984
727.6406 | 125.1251 | -61.8988 | 63.0844 | 0.0811 | 0.011401 | 0.015114 | 0.0074853 | 0.065899 | -0.00057686 | 0.070308 | -61.9904 | 63.0432 | -62.114 | -62.0956 | 62.4161 | -0.37537 | 0.31586 | 0.27008 | 63.0524 | -62.1552 | -0.21515 | -0.041199 | -0.091552 | -0.19684 | -0.66833 | -0.25635 | -0.032044 | 0.1236 | 62.2147 | 62.1689 | 124.3149 | 124.942 | -0.091552 | 124.9512 | 61.5234 | -0.25635 | 124.942 | -0.091552 | 61.5234 | 124.3149 | 124.9512 | -125.1984 | -125.2396
728.6406 | 125.1343 | -61.8851 | 63.0615 | -0.21645 | 0.0092649 | 0.012978 | 0.0010767 | 0.066539 | -0.0018585 | 0.067744 | -61.9446 | 63.0798 | -62.0956 | -62.0682 | 62.7411 | 0.059509 | 0.13733 | 0.14648 | 63.0569 | -62.1506 | -0.21057 | 0.018311 | -0.059509 | -0.1831 | -0.32043 | -0.2655 | -0.004577 | 0.15106 | 62.0224 | 62.0316 | 124.6262 | 124.9649 | -0.059509 | 124.942 | 61.9446 | -0.2655 | 124.9649 | -0.059509 | 61.9446 | 124.6262 | 124.942 | -125.1572 | -125.2121
729.6406 | 125.1572 | -61.8805 | 63.0661 | -0.13252 | 0.011615 | 0.012337 | 0.0047081 | 0.066326 | -0.00079046 | 0.067317 | -61.9263 | 63.0753 | -62.1323 | -62.0361 | 62.7823 | 0.10986 | 0.050354 | 0.1831 | 63.0478 | -62.1735 | -0.25177 | 0.009155 | -0.045777 | -0.15564 | -0.28381 | -0.29297 | -0.01831 | 0.20599 | 61.9308 | 62.0636 | 124.6628 | 124.9557 | -0.045777 | 124.9283 | 61.9904 | -0.29297 | 124.9557 | -0.045777 | 61.9904 | 124.6628 | 124.9283 | -125.1984 | -125.2396
730.6562 | 125.1663 | -61.8759 | 63.0798 | -0.20882 | 0.01076 | 0.010414 | 0.0044945 | 0.068248 | -0.00057686 | 0.068599 | -61.9125 | 63.0386 | -62.1185 | -62.0407 | 62.7686 | 0.068665 | 0.050354 | 0.18768 | 63.0569 | -62.1643 | -0.24261 | -0.041199 | -0.036621 | -0.16479 | -0.31128 | -0.28839 | -0.022888 | 0.20599 | 61.9263 | 62.0636 | 124.6445 | 124.9146 | -0.036621 | 124.9329 | 61.9446 | -0.28839 | 124.9146 | -0.036621 | 61.9446 | 124.6445 | 124.9329 | -125.1984 | -125.2441
731.6406 | 125.1572 | -61.8759 | 63.0707 | -0.21645 | 0.0090513 | 0.013832 | -0.0014869 | 0.066112 | -0.0035675 | 0.070308 | -61.9904 | 63.0295 | -62.1414 | -62.0865 | 62.7228 | 0.073242 | 0.13733 | 0.16479 | 63.0798 | -62.146 | -0.2655 | -0.041199 | -0.11444 | -0.21057 | -0.3479 | -0.27008 | 0.009155 | 0.15106 | 62.0132 | 62.0407 | 124.5987 | 124.9054 | -0.11444 | 124.9557 | 61.9492 | -0.27008 | 124.9054 | -0.11444 | 61.9492 | 124.5987 | 124.9557 | -125.2121 | -125.2167
732.6406 | 125.2075 | -61.8988 | 63.0295 | 0.14976 | 0.01311 | 0.0149 | 0.00086295 | 0.068035 | 6.414e-05 | 0.068812 | -61.9537 | 63.0112 | -62.1231 | -62.0728 | 62.7411 | -0.018311 | -0.11902 | 0.07782 | 63.0295 | -62.1643 | -0.2243 | -0.018311 | -0.054931 | -0.17395 | -0.28839 | -0.2655 | 0 | 0.16937 | 61.7798 | 61.9766 | 124.6399 | 124.91 | -0.054931 | 124.9283 | 61.8805 | -0.2655 | 124.91 | -0.054931 | 61.8805 | 124.6399 | 124.9283 | -125.1526 | -125.1938
733.6406 | 125.1205 | -61.8851 | 63.0936 | -0.23933 | 0.010333 | 0.0099869 | 0.00043575 | 0.066967 | -0.00057686 | 0.069667 | -61.9995 | 63.0478 | -62.1368 | -62.0956 | 62.7411 | 0.068665 | 0.14648 | 0.17395 | 63.0936 | -62.1414 | -0.25177 | -0.045776 | -0.11444 | -0.21057 | -0.35248 | -0.25635 | 0 | 0.13733 | 62.0316 | 62.059 | 124.6262 | 124.9329 | -0.11444 | 124.9786 | 61.9537 | -0.25635 | 124.9329 | -0.11444 | 61.9537 | 124.6262 | 124.9786 | -125.2304 | -125.235
734.6406 | 125.1434 | -61.8851 | 63.0798 | -0.20119 | 0.011188 | 0.014473 | 0.0038537 | 0.069744 | -0.00057686 | 0.06988 | -61.9034 | 63.0524 | -62.1048 | -62.0361 | 62.7777 | 0.082397 | 0.027466 | 0.17853 | 63.0569 | -62.146 | -0.21973 | -0.027466 | -0.01831 | -0.15106 | -0.30212 | -0.26092 | -0.022888 | 0.20142 | 61.9125 | 62.0636 | 124.6628 | 124.9374 | -0.01831 | 124.942 | 61.9675 | -0.26092 | 124.9374 | -0.01831 | 61.9675 | 124.6628 | 124.942 | -125.1846 | -125.2258
735.6562 | 125.1572 | -61.8805 | 63.1073 | -0.1783 | 0.012469 | 0.0097733 | 0.0021447 | 0.066967 | -0.0016449 | 0.069026 | -61.9537 | 63.0524 | -62.1094 | -62.0682 | 62.7502 | 0.082397 | 0.10071 | 0.16479 | 63.0707 | -62.1643 | -0.22888 | -0.054932 | -0.073242 | -0.18768 | -0.35706 | -0.28381 | -0.036621 | 0.15564 | 61.9812 | 62.0453 | 124.6307 | 124.9329 | -0.073242 | 124.9512 | 61.9629 | -0.28381 | 124.9329 | -0.073242 | 61.9629 | 124.6307 | 124.9512 | -125.2167 | -125.2716
736.6406 | 125.148 | -61.8713 | 63.1073 | -0.19356 | 0.010547 | 0.0087051 | 0.00022215 | 0.06718 | -0.00036306 | 0.069239 | -61.972 | 63.0524 | -62.1094 | -62.0865 | 62.7411 | 0.068665 | 0.11444 | 0.16479 | 63.089 | -62.146 | -0.23804 | -0.054932 | -0.10071 | -0.21515 | -0.36621 | -0.27466 | -0.018311 | 0.13733 | 61.9858 | 62.0361 | 124.6124 | 124.9237 | -0.10071 | 124.9603 | 61.94 | -0.27466 | 124.9237 | -0.10071 | 61.94 | 124.6124 | 124.9603 | -125.2167 | -125.2533
737.6406 | 125.2029 | -61.8805 | 63.0112 | 0.20317 | 0.011615 | 0.01191 | 0.00086295 | 0.068248 | 0.00027774 | 0.06988 | -61.9537 | 62.9745 | -62.114 | -62.0544 | 62.764 | 0.027466 | -0.16937 | 0.11902 | 62.9929 | -62.1414 | -0.23346 | -0.036621 | -0.073242 | -0.17395 | -0.24719 | -0.26093 | -0.01831 | 0.16022 | 61.7111 | 61.9995 | 124.6445 | 124.855 | -0.073242 | 124.8734 | 61.908 | -0.26093 | 124.855 | -0.073242 | 61.908 | 124.6445 | 124.8734 | -125.1251 | -125.1526
738.6406 | 125.1389 | -61.8805 | 63.0524 | -0.056229 | 0.010974 | 0.015541 | 0.0055627 | 0.06718 | -0.0010041 | 0.071162 | -61.9263 | 63.0432 | -62.1231 | -62.0682 | 62.7182 | 0.032043 | 0.022888 | 0.12817 | 63.0478 | -62.1918 | -0.24262 | -0.009155 | -0.045777 | -0.18768 | -0.33417 | -0.31128 | -0.004577 | 0.19684 | 61.9034 | 62.0087 | 124.5987 | 124.9237 | -0.045777 | 124.9283 | 61.9125 | -0.31128 | 124.9237 | -0.045777 | 61.9125 | 124.5987 | 124.9283 | -125.1755 | -125.2441
739.6406 | 125.148 | -61.8805 | 63.0524 | -0.2317 | 0.010333 | 0.015328 | 0.00022215 | 0.066753 | -0.00079046 | 0.070308 | -61.9904 | 63.0615 | -62.1368 | -62.0773 | 62.7457 | 0.064087 | 0.13733 | 0.15106 | 63.089 | -62.1918 | -0.25635 | 0.009155 | -0.10986 | -0.19684 | -0.3067 | -0.31128 | 0.036621 | 0.14648 | 62.0178 | 62.0316 | 124.6262 | 124.942 | -0.10986 | 124.9695 | 61.9446 | -0.31128 | 124.942 | -0.10986 | 61.9446 | 124.6262 | 124.9695 | -125.1892 | -125.2441
740.6562 | 125.235 | -61.8576 | 63.0615 | -0.22408 | 0.010119 | 0.010414 | -0.0040503 | 0.065258 | -0.00014946 | 0.070948 | -61.9217 | 62.9425 | -62.0819 | -62.0087 | 62.851 | 0.14648 | -0.018311 | 0.27924 | 63.002 | -62.1094 | -0.2243 | -0.11902 | -0.064087 | -0.15106 | -0.21057 | -0.25177 | -0.059509 | 0.16022 | 61.8393 | 62.1368 | 124.7086 | 124.8001 | -0.064087 | 124.8596 | 62.0041 | -0.25177 | 124.8001 | -0.064087 | 62.0041 | 124.7086 | 124.8596 | -125.1434 | -125.1709
741.6406 | 125.1846 | -61.8896 | 63.0707 | -0.26222 | 0.011828 | 0.011055 | 0.0019311 | 0.066753 | 0.00027774 | 0.068385 | -61.9629 | 63.0524 | -62.1048 | -62.0499 | 62.7502 | 0.086975 | 0.091553 | 0.17853 | 63.0524 | -62.1277 | -0.21515 | -0.018311 | -0.073243 | -0.16022 | -0.32043 | -0.23804 | -0.018311 | 0.14191 | 61.9812 | 62.0682 | 124.6399 | 124.942 | -0.073243 | 124.942 | 61.9766 | -0.23804 | 124.942 | -0.073243 | 61.9766 | 124.6399 | 124.942 | -125.1755 | -125.1984
742.6562 | 125.116 | -61.8988 | 63.0524 | 0.14976 | 0.010974 | 0.015755 | 0.0055627 | 0.06718 | -0.00057686 | 0.070308 | -61.9904 | 63.0203 | -62.1323 | -62.1277 | 62.6907 | -0.032043 | -0.036621 | 0.032043 | 63.0432 | -62.1689 | -0.23346 | -0.032043 | -0.091552 | -0.22888 | -0.36163 | -0.27008 | -0.009155 | 0.14191 | 61.8622 | 61.9308 | 124.5895 | 124.9191 | -0.091552 | 124.942 | 61.8668 | -0.27008 | 124.9191 | -0.091552 | 61.8668 | 124.5895 | 124.942 | -125.1846 | -125.2213
743.6406 | 125.1663 | -61.8805 | 63.0661 | 0.020065 | 0.013965 | 0.015114 | 0.0053491 | 0.068035 | -0.0016449 | 0.069667 | -61.9308 | 63.0341 | -62.1002 | -62.0499 | 62.7411 | 0.064087 | 0.027466 | 0.14648 | 63.0524 | -62.1597 | -0.21973 | -0.032043 | -0.050354 | -0.16937 | -0.32501 | -0.27924 | -0.013733 | 0.16937 | 61.908 | 62.027 | 124.6216 | 124.9146 | -0.050354 | 124.9329 | 61.9446 | -0.27924 | 124.9146 | -0.050354 | 61.9446 | 124.6216 | 124.9329 | -125.1663 | -125.2258
744.6562 | 125.267 | -61.8668 | 63.0524 | -0.14778 | 0.0096921 | 0.010414 | -0.0055457 | 0.06718 | -0.00036306 | 0.070735 | -61.9171 | 62.9608 | -62.1048 | -61.9904 | 62.8555 | 0.15564 | -0.086975 | 0.29755 | 63.0249 | -62.0865 | -0.23804 | -0.091553 | -0.050354 | -0.1236 | -0.19684 | -0.21973 | -0.027466 | 0.18768 | 61.7798 | 62.1643 | 124.7223 | 124.8276 | -0.050354 | 124.8917 | 62.0224 | -0.21973 | 124.8276 | -0.050354 | 62.0224 | 124.7223 | 124.8917 | -125.1572 | -125.1389
745.6562 | 125.116 | -61.8622 | 63.089 | -0.25459 | 0.011615 | 0.0099869 | 0.0038537 | 0.066326 | -0.0010041 | 0.070308 | -61.9858 | 63.0341 | -62.1048 | -62.0819 | 62.7182 | 0.050354 | 0.13733 | 0.16479 | 63.0524 | -62.1689 | -0.24261 | -0.054931 | -0.1236 | -0.21973 | -0.37079 | -0.3067 | -0.036621 | 0.11902 | 61.9995 | 62.027 | 124.5804 | 124.8962 | -0.1236 | 124.9146 | 61.9125 | -0.3067 | 124.8962 | -0.1236 | 61.9125 | 124.5804 | 124.9146 | -125.1938 | -125.2579
746.6406 | 125.116 | -61.8805 | 63.0569 | -0.086746 | 0.010547 | 0.014473 | 0.0070581 | 0.065258 | -0.0024995 | 0.067744 | -61.8942 | 63.0295 | -62.1185 | -62.0407 | 62.7411 | 0.073242 | 0.018311 | 0.15564 | 63.0432 | -62.178 | -0.23804 | -0.027466 | -0.013733 | -0.16022 | -0.31586 | -0.29755 | -0.013733 | 0.2243 | 61.8988 | 62.0361 | 124.6216 | 124.91 | -0.013733 | 124.9237 | 61.9537 | -0.29755 | 124.91 | -0.013733 | 61.9537 | 124.6216 | 124.9237 | -125.1755 | -125.235
747.6406 | 125.1114 | -61.8896 | 63.0569 | -0.018082 | 0.010974 | 0.0093459 | 0.0049219 | 0.067608 | -0.00079046 | 0.070094 | -61.9629 | 63.0432 | -62.1277 | -62.0911 | 62.6953 | -0.004578 | 0.018311 | 0.07782 | 63.0203 | -62.1918 | -0.23804 | -0.013733 | -0.073243 | -0.20142 | -0.36163 | -0.30212 | -0.036621 | 0.16479 | 61.908 | 61.9675 | 124.585 | 124.9329 | -0.073243 | 124.91 | 61.8851 | -0.30212 | 124.9329 | -0.073243 | 61.8851 | 124.585 | 124.91 | -125.1846 | -125.2487
748.6406 | 125.1297 | -61.8988 | 63.0936 | -0.19356 | 0.011615 | 0.0149 | 0.0025719 | 0.067608 | -0.0014313 | 0.070308 | -61.9812 | 63.0753 | -62.1185 | -62.0728 | 62.7365 | 0.073242 | 0.11902 | 0.15564 | 63.0844 | -62.1506 | -0.21973 | -0.018311 | -0.082397 | -0.17395 | -0.35706 | -0.25177 | -0.009155 | 0.13733 | 62.0178 | 62.0544 | 124.6353 | 124.9741 | -0.082397 | 124.9832 | 61.972 | -0.25177 | 124.9741 | -0.082397 | 61.972 | 124.6353 | 124.9832 | -125.2121 | -125.2441
749.6406 | 125.1663 | -61.8759 | 63.0661 | -0.086746 | 0.010974 | 0.014687 | 0.0032129 | 0.06953 | -0.0018585 | 0.067958 | -61.9263 | 63.0524 | -62.0911 | -62.0407 | 62.7686 | 0.091553 | 0.045776 | 0.18768 | 63.0524 | -62.1368 | -0.21515 | -0.013733 | -0.050354 | -0.16479 | -0.29755 | -0.26093 | -0.013733 | 0.16479 | 61.9217 | 62.0636 | 124.6445 | 124.9283 | -0.050354 | 124.9283 | 61.9675 | -0.26093 | 124.9283 | -0.050354 | 61.9675 | 124.6445 | 124.9283 | -125.1572 | -125.2029
750.6562 | 125.2304 | -61.8576 | 63.0249 | 0.13451 | 0.010974 | 0.016182 | -0.00063225 | 0.066112 | 0.0045501 | 0.070948 | -61.9125 | 62.9608 | -62.1368 | -62.2238 | 62.8967 | 0.1831 | -0.15564 | 0.13275 | 62.9929 | -62.1094 | -0.27924 | -0.064087 | -0.054932 | -0.36621 | -0.12817 | -0.25177 | -0.032043 | 0.2243 | 61.702 | 61.9904 | 124.7543 | 124.8184 | -0.054932 | 124.8505 | 62.0407 | -0.25177 | 124.8184 | -0.054932 | 62.0407 | 124.7543 | 124.8505 | -125.1617 | -125.1343
751.6406 | 125.1572 | -61.8484 | 63.0478 | -0.079117 | 0.013324 | 0.011055 | 0.0023583 | 0.067394 | -0.00014946 | 0.069239 | -61.9308 | 63.0341 | -62.0956 | -62.0361 | 62.7686 | 0.10071 | 0.059509 | 0.19684 | 63.0569 | -62.1689 | -0.24719 | -0.013733 | -0.082397 | -0.18768 | -0.27924 | -0.32043 | 0.009155 | 0.16479 | 61.908 | 62.0453 | 124.617 | 124.8825 | -0.082397 | 124.9054 | 61.9492 | -0.32043 | 124.8825 | -0.082397 | 61.9492 | 124.617 | 124.9054 | -125.1434 | -125.2167
752.6406 | 125.1389 | -61.8988 | 63.0478 | 0.096359 | 0.011401 | 0.014687 | 0.0029993 | 0.066112 | 0.00091854 | 0.069453 | -61.9766 | 63.0386 | -62.1552 | -62.1277 | 62.6816 | -0.045776 | 0.013733 | 0.018311 | 63.0569 | -62.1643 | -0.25635 | -0.009156 | -0.07782 | -0.22888 | -0.36621 | -0.2655 | 0.009155 | 0.17853 | 61.9125 | 61.9171 | 124.5804 | 124.9374 | -0.07782 | 124.9557 | 61.853 | -0.2655 | 124.9374 | -0.07782 | 61.853 | 124.5804 | 124.9557 | -125.2029 | -125.2121
753.6406 | 125.1801 | -61.8759 | 63.0569 | 0.24895 | 0.01311 | 0.015114 | 0.0040673 | 0.066326 | -0.00057686 | 0.068171 | -61.8805 | 63.0432 | -62.114 | -62.0178 | 62.764 | 0.073242 | 0 | 0.17395 | 63.0478 | -62.1552 | -0.23804 | -0.013733 | -0.004577 | -0.14191 | -0.29297 | -0.27923 | -0.009155 | 0.23346 | 61.8759 | 62.0499 | 124.6399 | 124.9191 | -0.004577 | 124.9237 | 61.9492 | -0.27923 | 124.9191 | -0.004577 | 61.9492 | 124.6399 | 124.9237 | -125.1709 | -125.2121
754.6406 | 125.1617 | -61.8805 | 63.0661 | -1.0938 | 0.012256 | 0.016823 | 0.0034265 | 0.068462 | -0.0016449 | 0.070948 | -61.908 | 63.0569 | -62.1323 | -62.0361 | 62.7548 | 0.086975 | 0.027466 | 0.16937 | 63.0569 | -62.1506 | -0.25177 | -0.009155 | -0.027466 | -0.15564 | -0.31128 | -0.27008 | -0.009155 | 0.2243 | 61.908 | 62.0499 | 124.6353 | 124.9374 | -0.027466 | 124.9374 | 61.9675 | -0.27008 | 124.9374 | -0.027466 | 61.9675 | 124.6353 | 124.9374 | -125.1984 | -125.2167
755.6562 | 125.235 | -61.8484 | 63.0112 | 0.17265 | 0.013965 | 0.013191 | 0.00043575 | 0.068248 | -0.0012177 | 0.068385 | -61.9217 | 62.9517 | -62.1231 | -62.0224 | 62.7777 | 0.045776 | -0.17395 | 0.13733 | 63.0157 | -62.1368 | -0.27466 | -0.059509 | -0.073242 | -0.17395 | -0.23346 | -0.28839 | 0.004578 | 0.20142 | 61.6745 | 61.9858 | 124.6262 | 124.8001 | -0.073242 | 124.8642 | 61.8942 | -0.28839 | 124.8001 | -0.073242 | 61.8942 | 124.6262 | 124.8642 | -125.1343 | -125.148
756.6406 | 125.1205 | -61.8713 | 63.0569 | -0.16304 | 0.0096921 | 0.014259 | 0.0029993 | 0.067394 | -0.00079046 | 0.070521 | -61.9308 | 63.0569 | -62.1277 | -62.0453 | 62.7594 | 0.082397 | 0.064087 | 0.20142 | 63.0524 | -62.1597 | -0.25635 | 0 | -0.059509 | -0.17395 | -0.29755 | -0.28839 | -0.004578 | 0.19684 | 61.9354 | 62.0728 | 124.6307 | 124.9283 | -0.059509 | 124.9237 | 61.9537 | -0.28839 | 124.9283 | -0.059509 | 61.9537 | 124.6307 | 124.9237 | -125.1846 | -125.2167
757.6406 | 125.1526 | -61.8668 | 63.0478 | -0.033341 | 0.012042 | 0.015755 | 0.0036401 | 0.068035 | 6.414e-05 | 0.069026 | -62.1048 | 63.0112 | -62.114 | -62.0453 | 62.7411 | 0.091553 | 0.027466 | 0.17853 | 63.0386 | -62.146 | -0.24719 | -0.036622 | -0.23804 | -0.17853 | -0.3067 | -0.27924 | -0.009156 | 0.009156 | 61.8942 | 62.0453 | 124.6078 | 124.8779 | -0.23804 | 124.9054 | 61.9583 | -0.27924 | 124.8779 | -0.23804 | 61.9583 | 124.6078 | 124.9054 | -125.1617 | -125.1938
758.6562 | 125.2258 | -61.8668 | 63.0295 | 0.11162 | 0.010333 | 0.012123 | -0.0042639 | 0.068676 | 6.414e-05 | 0.068812 | -61.9263 | 62.9608 | -62.0865 | -62.0453 | 62.7777 | 0.064087 | -0.19226 | 0.15564 | 62.9974 | -62.1002 | -0.21973 | -0.068665 | -0.05951 | -0.17853 | -0.25177 | -0.23346 | -0.032043 | 0.16022 | 61.6745 | 62.0224 | 124.6445 | 124.8276 | -0.05951 | 124.8642 | 61.9308 | -0.23346 | 124.8276 | -0.05951 | 61.9308 | 124.6445 | 124.8642 | -125.116 | -125.1297
759.6406 | 125.148 | -61.8805 | 63.0707 | 2.0342 | 0.01076 | 0.010414 | 0.0040673 | 0.068462 | -0.0016449 | 0.070308 | -61.7615 | 63.0432 | -62.1185 | -62.0361 | 62.7457 | 0.073242 | 0.027466 | 0.1831 | 63.0341 | -62.1597 | -0.23804 | -0.027466 | 0.11902 | -0.15564 | -0.32501 | -0.27924 | -0.036621 | 0.35706 | 61.908 | 62.0636 | 124.6262 | 124.9237 | 0.11902 | 124.9146 | 61.9537 | -0.27924 | 124.9237 | 0.11902 | 61.9537 | 124.6262 | 124.9146 | -125.1892 | -125.2304
760.6406 | 125.1572 | -61.8805 | 63.0661 | -0.20119 | 0.012469 | 0.011482 | 0.0032129 | 0.06953 | -0.0018585 | 0.069026 | -61.9263 | 63.0569 | -62.1048 | -62.027 | 62.764 | 0.07782 | 0.07782 | 0.21515 | 63.0615 | -62.1323 | -0.2243 | -0.009155 | -0.045777 | -0.14648 | -0.30212 | -0.25177 | -0.004578 | 0.17853 | 61.9583 | 62.0956 | 124.6445 | 124.9374 | -0.045777 | 124.942 | 61.9583 | -0.25177 | 124.9374 | -0.045777 | 61.9583 | 124.6445 | 124.942 | -125.1709 | -125.1984
761.6562 | 125.2029 | -61.8851 | 62.9517 | 0.13451 | 0.0099057 | 0.010841 | 0.0015039 | 0.06718 | -0.00014946 | 0.070308 | -61.9263 | 62.9608 | -62.1185 | -62.0316 | 62.7731 | 0.054932 | -0.16479 | 0.13275 | 62.9837 | -62.1048 | -0.23346 | 0.009155 | -0.041199 | -0.14648 | -0.17853 | -0.21973 | 0.032044 | 0.19226 | 61.7203 | 62.0178 | 124.6582 | 124.8459 | -0.041199 | 124.8688 | 61.94 | -0.21973 | 124.8459 | -0.041199 | 61.94 | 124.6582 | 124.8688 | -125.0702 | -125.0565
762.6406 | 125.116 | -61.8988 | 63.0615 | 0.027695 | 0.013751 | 0.014473 | 0.0044945 | 0.06718 | 6.414e-05 | 0.06988 | -61.972 | 63.0569 | -62.1323 | -62.1323 | 62.6678 | -0.032043 | 0.036621 | 0.032043 | 63.0432 | -62.1918 | -0.23346 | -0.004577 | -0.073242 | -0.23346 | -0.39368 | -0.29297 | -0.01831 | 0.16022 | 61.9354 | 61.9308 | 124.5667 | 124.9557 | -0.073242 | 124.942 | 61.8668 | -0.29297 | 124.9557 | -0.073242 | 61.8668 | 124.5667 | 124.942 | -125.1938 | -125.2533
763.6406 | 125.1389 | -61.8759 | 63.0386 | -0.46059 | 0.012256 | 0.012978 | 0.0021447 | 0.065685 | -0.0022859 | 0.069453 | -61.9263 | 63.0432 | -62.0911 | -62.0453 | 62.7457 | 0.07782 | 0.009155 | 0.16022 | 63.0569 | -62.178 | -0.21515 | 0.004578 | -0.050354 | -0.16937 | -0.29297 | -0.30212 | 0.018311 | 0.16479 | 61.8851 | 62.0361 | 124.6216 | 124.9191 | -0.050354 | 124.9329 | 61.9537 | -0.30212 | 124.9191 | -0.050354 | 61.9537 | 124.6216 | 124.9329 | -125.1297 | -125.2167
764.6562 | 125.1755 | -61.8622 | 63.0157 | 0.12688 | 0.01076 | 0.010841 | -0.0061865 | 0.06718 | -0.00014946 | 0.070948 | -61.9583 | 62.9425 | -62.1094 | -62.0819 | 62.7548 | 0.045776 | -0.11902 | 0.1236 | 62.9883 | -62.1048 | -0.24719 | -0.073242 | -0.09613 | -0.21973 | -0.26093 | -0.24261 | -0.027466 | 0.15106 | 61.7432 | 61.9858 | 124.617 | 124.8047 | -0.09613 | 124.8505 | 61.908 | -0.24261 | 124.8047 | -0.09613 | 61.908 | 124.617 | 124.8505 | -125.1251 | -125.1205
765.6406 | 125.1251 | -61.8759 | 63.0707 | 0.0048064 | 0.013324 | 0.018105 | 0.0044945 | 0.067394 | 0.00070494 | 0.067531 | -61.9308 | 63.0524 | -62.114 | -62.0773 | 62.7136 | 0.004578 | 0.036621 | 0.07782 | 63.0341 | -62.1918 | -0.23804 | -0.018311 | -0.054931 | -0.20142 | -0.35706 | -0.31586 | -0.036621 | 0.18311 | 61.9125 | 61.9537 | 124.5895 | 124.9283 | -0.054931 | 124.91 | 61.8805 | -0.31586 | 124.9283 | -0.054931 | 61.8805 | 124.5895 | 124.91 | -125.1846 | -125.2625
766.6406 | 125.2029 | -61.908 | 62.9974 | 0.050583 | 0.013751 | 0.015968 | 0.0025719 | 0.067821 | -0.0012177 | 0.069239 | -61.9812 | 63.0478 | -62.1506 | -62.1368 | 62.6816 | -0.054932 | 0.045776 | 0.032043 | 63.0569 | -62.1826 | -0.24262 | 0.050354 | -0.073242 | -0.22888 | -0.31586 | -0.27466 | 0.059509 | 0.16937 | 61.9537 | 61.94 | 124.5895 | 124.9557 | -0.073242 | 124.9649 | 61.853 | -0.27466 | 124.9557 | -0.073242 | 61.853 | 124.5895 | 124.9649 | -125.148 | -125.1801
767.6406 | 125.1984 | -61.8439 | 63.0157 | 0.18028 | 0.010119 | 0.013405 | -0.00020505 | 0.065685 | -0.0012177 | 0.070948 | -61.908 | 62.9379 | -62.1094 | -62.0361 | 62.8006 | 0.004578 | -0.36621 | 0.37537 | 62.9654 | -62.1552 | -0.2655 | -0.07782 | -0.064087 | -0.19226 | -0.21515 | -0.31128 | -0.050354 | 0.20142 | 61.4777 | 62.2192 | 124.6445 | 124.7818 | -0.064087 | 124.8093 | 61.8484 | -0.31128 | 124.7818 | -0.064087 | 61.8484 | 124.6445 | 124.8093 | -125.1251 | -125.1709
768.6406 | 125.1205 | -61.9125 | 63.0432 | -0.033341 | 0.010974 | 0.010628 | 0.0053491 | 0.068035 | -0.0018585 | 0.068599 | -61.9354 | 63.0569 | -62.1048 | -62.0773 | 62.7045 | 0.022888 | 0.018311 | 0.10071 | 63.0249 | -62.178 | -0.19226 | 0.013733 | -0.022888 | -0.16479 | -0.33875 | -0.2655 | -0.018311 | 0.16937 | 61.9308 | 62.0132 | 124.617 | 124.9695 | -0.022888 | 124.9374 | 61.9354 | -0.2655 | 124.9695 | -0.022888 | 61.9354 | 124.617 | 124.9374 | -125.148 | -125.2213
769.6406 | 125.1251 | -61.8942 | 63.0661 | -0.056229 | 0.012469 | 0.010628 | 0.0049219 | 0.068035 | -0.0020721 | 0.070948 | -61.9308 | 63.0478 | -62.114 | -62.0819 | 62.709 | 0.022888 | 0.027466 | 0.086975 | 63.0569 | -62.1506 | -0.21973 | -0.01831 | -0.036621 | -0.18768 | -0.35706 | -0.25635 | -0.009155 | 0.18311 | 61.9217 | 61.9812 | 124.6033 | 124.942 | -0.036621 | 124.9512 | 61.9171 | -0.25635 | 124.942 | -0.036621 | 61.9171 | 124.6033 | 124.9512 | -125.1801 | -125.2167
770.6562 | 125.2029 | -61.8393 | 63.0341 | -0.033341 | 0.0064877 | 0.0082779 | -0.0070411 | 0.066753 | -0.00036306 | 0.068599 | -61.9858 | 62.9425 | -62.114 | -62.0682 | 62.7777 | 0.068665 | -0.068665 | 0.18768 | 63.0295 | -62.1094 | -0.27466 | -0.091553 | -0.14648 | -0.22888 | -0.25635 | -0.27008 | -0.004578 | 0.12817 | 61.7706 | 62.027 | 124.617 | 124.7818 | -0.14648 | 124.8688 | 61.908 | -0.27008 | 124.7818 | -0.14648 | 61.908 | 124.617 | 124.8688 | -125.148 | -125.1434
771.6406 | 125.1068 | -61.908 | 63.0569 | 0.050583 | 0.013965 | 0.010841 | 0.0051355 | 0.066112 | -0.0027131 | 0.070521 | -61.9629 | 63.0295 | -62.1185 | -62.1277 | 62.6633 | -0.027466 | 0.032043 | 0.045776 | 63.0203 | -62.2192 | -0.21057 | -0.027466 | -0.054932 | -0.21973 | -0.39368 | -0.31128 | -0.036621 | 0.15564 | 61.94 | 61.9537 | 124.5712 | 124.9374 | -0.054932 | 124.9283 | 61.8805 | -0.31128 | 124.9374 | -0.054932 | 61.8805 | 124.5712 | 124.9283 | -125.1755 | -125.2762
772.6406 | 125.1389 | -61.9125 | 63.0341 | 0.56938 | 0.01076 | 0.016823 | 0.0040673 | 0.066753 | -0.0014313 | 0.068385 | -61.9583 | 63.0615 | -62.1368 | -62.1368 | 62.6587 | -0.050354 | 0.004578 | 0.022888 | 63.0386 | -62.1643 | -0.2243 | 0.027465 | -0.045776 | -0.2243 | -0.37537 | -0.25177 | 0.004577 | 0.17853 | 61.9171 | 61.9354 | 124.5712 | 124.9741 | -0.045776 | 124.9512 | 61.8622 | -0.25177 | 124.9741 | -0.045776 | 61.8622 | 124.5712 | 124.9512 | -125.1709 | -125.1984
773.6406 | 125.1297 | -61.8896 | 63.0524 | -0.0028231 | 0.014178 | 0.015755 | 0.0064171 | 0.067394 | 0.0013457 | 0.06689 | -61.9354 | 63.0615 | -62.0956 | -62.0544 | 62.7136 | 0.027466 | 0.022888 | 0.13275 | 63.0707 | -62.1689 | -0.20599 | 0.009155 | -0.045777 | -0.16479 | -0.33875 | -0.27924 | 0.018311 | 0.16022 | 61.9125 | 62.0224 | 124.6033 | 124.9512 | -0.045777 | 124.9603 | 61.9171 | -0.27924 | 124.9512 | -0.045777 | 61.9171 | 124.6033 | 124.9603 | -125.148 | -125.2213
774.6406 | 125.2213 | -61.8484 | 62.9791 | 0.20317 | 0.010974 | 0.012123 | 8.546e-06 | 0.06718 | -0.0024995 | 0.069667 | -61.9354 | 62.9791 | -62.1368 | -62.027 | 62.7686 | 0.041199 | -0.19226 | 0.13733 | 63.0112 | -62.1048 | -0.28839 | 0 | -0.086975 | -0.17853 | -0.21057 | -0.25635 | 0.032043 | 0.20142 | 61.6562 | 61.9858 | 124.617 | 124.8276 | -0.086975 | 124.8596 | 61.8896 | -0.25635 | 124.8276 | -0.086975 | 61.8896 | 124.617 | 124.8596 | -125.116 | -125.0839
775.6406 | 125.0931 | -61.908 | 63.0249 | 0.035324 | 0.0096921 | 0.011696 | 0.0027855 | 0.067821 | -0.00036306 | 0.068385 | -61.7477 | 63.0295 | -62.1048 | -62.0682 | 62.6358 | -0.050354 | 0.013733 | 0.027466 | 63.0524 | -62.178 | -0.19684 | 0.004578 | 0.16022 | -0.16022 | -0.3891 | -0.27008 | 0.027466 | 0.35705 | 61.9217 | 61.9354 | 124.5438 | 124.9374 | 0.16022 | 124.9603 | 61.8576 | -0.27008 | 124.9374 | 0.16022 | 61.8576 | 124.5438 | 124.9603 | -125.1297 | -125.2029
776.6562 | 125.1984 | -61.8668 | 63.0112 | 0.0811 | 0.0058469 | 0.0087051 | -0.0046913 | 0.065258 | 6.414e-05 | 0.067317 | -61.9858 | 62.9242 | -62.1002 | -62.0544 | 62.7731 | 0.07782 | -0.064087 | 0.16022 | 63.0157 | -62.1323 | -0.23346 | -0.086975 | -0.11902 | -0.18768 | -0.23804 | -0.2655 | 0.004578 | 0.11444 | 61.8027 | 62.027 | 124.6399 | 124.791 | -0.11902 | 124.8825 | 61.9446 | -0.2655 | 124.791 | -0.11902 | 61.9446 | 124.6399 | 124.8825 | -125.1114 | -125.1434
777.6406 | 125.1114 | -61.8851 | 63.0249 | 0.16502 | 0.013751 | 0.013619 | 0.0047081 | 0.063976 | 0.0022003 | 0.071162 | -61.9904 | 63.0432 | -62.1231 | -62.1277 | 62.677 | -0.036621 | -0.045776 | 0.045776 | 63.0295 | -62.1826 | -0.23804 | 0.018311 | -0.10528 | -0.24261 | -0.3479 | -0.29755 | 0.004578 | 0.13275 | 61.8393 | 61.9308 | 124.5621 | 124.9283 | -0.10528 | 124.9146 | 61.8485 | -0.29755 | 124.9283 | -0.10528 | 61.8485 | 124.5621 | 124.9146 | -125.148 | -125.2075
778.6406 | 125.0931 | -61.8988 | 63.0386 | -0.033341 | 0.013537 | 0.010414 | 0.0064171 | 0.067608 | -0.00057686 | 0.069239 | -61.9537 | 63.0432 | -62.1185 | -62.0865 | 62.6816 | -0.009155 | 0.022888 | 0.073242 | 63.0386 | -62.1964 | -0.21973 | 0.004578 | -0.054931 | -0.18768 | -0.35706 | -0.29755 | 0 | 0.16479 | 61.9217 | 61.972 | 124.5804 | 124.942 | -0.054931 | 124.9374 | 61.8896 | -0.29755 | 124.942 | -0.054931 | 61.8896 | 124.5804 | 124.9374 | -125.1572 | -125.235
779.6562 | 125.2121 | -61.8301 | 63.0203 | -0.04097 | 0.0086239 | 0.0099869 | -0.0046913 | 0.064617 | -0.00057686 | 0.069239 | -61.972 | 62.9608 | -62.1277 | -62.0361 | 62.7869 | 0.091553 | -0.059509 | 0.2243 | 63.0066 | -62.1185 | -0.29755 | -0.05951 | -0.14191 | -0.20599 | -0.23346 | -0.28839 | -0.013733 | 0.15564 | 61.7706 | 62.0544 | 124.617 | 124.791 | -0.14191 | 124.8367 | 61.9217 | -0.28839 | 124.791 | -0.14191 | 61.9217 | 124.617 | 124.8367 | -125.148 | -125.1389
780.6406 | 125.0977 | -61.8759 | 63.0341 | -0.018082 | 0.013751 | 0.013619 | 0.0076989 | 0.065471 | 0.00027774 | 0.069026 | -61.9263 | 63.0707 | -62.1048 | -62.0773 | 62.7045 | 0.009155 | 0.027466 | 0.09613 | 63.0432 | -62.1872 | -0.22888 | 0.036621 | -0.050354 | -0.20142 | -0.32959 | -0.31128 | 0.009155 | 0.17853 | 61.9034 | 61.972 | 124.5804 | 124.9466 | -0.050354 | 124.9191 | 61.8851 | -0.31128 | 124.9466 | -0.050354 | 61.8851 | 124.5804 | 124.9191 | -125.1389 | -125.2213
781.6406 | 125.0977 | -61.8942 | 63.0432 | 0.0811 | 0.011401 | 0.011055 | 0.0062035 | 0.069316 | -0.0010041 | 0.068812 | -61.972 | 63.0295 | -62.1231 | -62.1094 | 62.677 | -0.041199 | 0.032043 | 0.045776 | 63.0661 | -62.1826 | -0.22888 | -0.013733 | -0.07782 | -0.21515 | -0.36621 | -0.28839 | 0.022888 | 0.15106 | 61.9263 | 61.94 | 124.5712 | 124.9237 | -0.07782 | 124.9603 | 61.853 | -0.28839 | 124.9237 | -0.07782 | 61.853 | 124.5712 | 124.9603 | -125.1663 | -125.2258
782.6406 | 125.2441 | -61.8713 | 63.002 | 0.28709 | 0.0099057 | 0.0093459 | -0.0019141 | 0.066326 | -0.0037811 | 0.06988 | -61.9171 | 62.9288 | -62.1323 | -62.0132 | 62.7914 | 0.059509 | -0.18768 | 0.15106 | 62.9562 | -62.114 | -0.26093 | -0.073242 | -0.045776 | -0.14191 | -0.21057 | -0.24262 | -0.045776 | 0.21515 | 61.6837 | 62.0224 | 124.6628 | 124.8001 | -0.045776 | 124.8276 | 61.9308 | -0.24262 | 124.8001 | -0.045776 | 61.9308 | 124.6628 | 124.8276 | -125.1343 | -125.116
783.6406 | 125.1068 | -61.9034 | 63.0432 | 0.12688 | 0.011828 | 0.013832 | 0.0057763 | 0.065471 | -0.0020721 | 0.06988 | -62.384 | 62.9608 | -62.1277 | -62.1643 | 62.6541 | -0.018311 | -0.018311 | -0.004578 | 63.0112 | -62.2147 | -0.2243 | -0.082398 | -0.48065 | -0.26093 | -0.3891 | -0.31128 | -0.032044 | -0.25635 | 61.8851 | 61.8988 | 124.5575 | 124.8642 | -0.48065 | 124.9146 | 61.8851 | -0.31128 | 124.8642 | -0.48065 | 61.8851 | 124.5575 | 124.9146 | -125.1709 | -125.2579
784.6406 | 125.1434 | -61.8805 | 63.0249 | 0.17265 | 0.013324 | 0.014046 | 0.0019311 | 0.066326 | -0.0012177 | 0.069026 | -61.9995 | 63.0249 | -62.114 | -62.114 | 62.6724 | -0.045776 | -0.041199 | 0.036621 | 63.0341 | -62.1872 | -0.23346 | 0 | -0.11902 | -0.23346 | -0.35248 | -0.3067 | 0.009156 | 0.11444 | 61.8393 | 61.9171 | 124.5529 | 124.9054 | -0.11902 | 124.9146 | 61.8347 | -0.3067 | 124.9054 | -0.11902 | 61.8347 | 124.5529 | 124.9146 | -125.1389 | -125.2121
785.6406 | 125.2075 | -61.8393 | 62.9974 | 0.11925 | 0.011828 | 0.011696 | 0.00022215 | 0.06718 | -0.0031403 | 0.071162 | -61.9171 | 62.9425 | -62.1094 | -62.0453 | 62.7548 | 0.059509 | -0.1831 | 0.15106 | 62.9974 | -62.1368 | -0.27008 | -0.054932 | -0.07782 | -0.20599 | -0.24262 | -0.29755 | 0 | 0.19226 | 61.6562 | 61.9904 | 124.5941 | 124.7818 | -0.07782 | 124.8367 | 61.8988 | -0.29755 | 124.7818 | -0.07782 | 61.8988 | 124.5941 | 124.8367 | -125.1068 | -125.1343
786.6406 | 125.1434 | -61.8759 | 63.0295 | 0.16502 | 0.012042 | 0.013405 | 0.0029993 | 0.066539 | 0.00091854 | 0.071803 | -61.972 | 62.9974 | -62.1414 | -62.0865 | 62.6953 | -0.045776 | -0.082397 | 0.064087 | 63.0066 | -62.1872 | -0.2655 | -0.032043 | -0.09613 | -0.21057 | -0.33417 | -0.31128 | -0.022888 | 0.16937 | 61.7935 | 61.94 | 124.5712 | 124.8734 | -0.09613 | 124.8825 | 61.8301 | -0.31128 | 124.8734 | -0.09613 | 61.8301 | 124.5712 | 124.8825 | -125.1709 | -125.2167
787.6406 | 125.1114 | -61.9034 | 63.0386 | 0.042953 | 0.010333 | 0.013832 | 0.0047081 | 0.067821 | -0.0010041 | 0.069239 | -61.9537 | 63.0386 | -62.146 | -62.1002 | 62.6907 | 0 | 0.036621 | 0.059509 | 63.0478 | -62.1918 | -0.24261 | 0 | -0.050354 | -0.19684 | -0.3479 | -0.28839 | 0.009156 | 0.19226 | 61.94 | 61.9629 | 124.5941 | 124.942 | -0.050354 | 124.9512 | 61.9034 | -0.28839 | 124.942 | -0.050354 | 61.9034 | 124.5941 | 124.9512 | -125.1846 | -125.2304
788.6406 | 125.1846 | -61.8439 | 62.9837 | 0.22606 | 0.013537 | 0.015755 | 0.0012903 | 0.068462 | -0.00057686 | 0.068171 | -61.9766 | 62.9929 | -62.1323 | -62.0544 | 62.7274 | 0.013733 | -0.16022 | 0.091553 | 63.0066 | -62.1597 | -0.28839 | 0.009155 | -0.13275 | -0.21057 | -0.25635 | -0.31586 | 0.022888 | 0.15564 | 61.6837 | 61.9354 | 124.5712 | 124.8367 | -0.13275 | 124.8505 | 61.8576 | -0.31586 | 124.8367 | -0.13275 | 61.8576 | 124.5712 | 124.8505 | -125.116 | -125.1434
789.6406 | 125.1068 | -61.9034 | 63.0432 | 0.2108 | 0.010333 | 0.013405 | 0.0019311 | 0.06718 | 6.414e-05 | 0.070094 | -61.9949 | 63.0386 | -62.1323 | -62.1368 | 62.677 | -0.036621 | -0.018311 | 0.027466 | 63.0112 | -62.2055 | -0.22888 | -0.004578 | -0.091553 | -0.23346 | -0.36621 | -0.30212 | -0.032044 | 0.13733 | 61.8851 | 61.9308 | 124.5804 | 124.942 | -0.091553 | 124.9146 | 61.8668 | -0.30212 | 124.942 | -0.091553 | 61.8668 | 124.5804 | 124.9146 | -125.1755 | -125.2487
790.6406 | 125.1068 | -61.908 | 63.0295 | 0.3405 | 0.012256 | 0.01191 | 0.0042809 | 0.066753 | 0.0017731 | 0.069667 | -61.908 | 63.0524 | -62.1094 | -62.1185 | 62.677 | -0.050354 | -0.009155 | 0.018311 | 63.0203 | -62.1689 | -0.20142 | 0.022888 | 0 | -0.21057 | -0.35248 | -0.26093 | -0.009155 | 0.20142 | 61.8988 | 61.9263 | 124.585 | 124.9603 | 0 | 124.9283 | 61.8576 | -0.26093 | 124.9603 | 0 | 61.8576 | 124.585 | 124.9283 | -125.1389 | -125.1984
791.6406 | 125.2258 | -61.853 | 62.9974 | 0.89745 | 0.010119 | 0.010201 | -0.0017005 | 0.065685 | -0.00036306 | 0.070094 | -61.7798 | 62.9425 | -62.0636 | -61.9949 | 62.7914 | 0.045776 | -0.18768 | 0.16022 | 62.9745 | -62.1323 | -0.21057 | -0.054932 | 0.073242 | -0.14191 | -0.20599 | -0.27924 | -0.022889 | 0.28381 | 61.6653 | 62.0132 | 124.6445 | 124.7955 | 0.073242 | 124.8276 | 61.8988 | -0.27924 | 124.7955 | 0.073242 | 61.8988 | 124.6445 | 124.8276 | -125.061 | -125.1297
792.6406 | 125.1251 | -61.8622 | 63.0478 | -0.04097 | 0.011401 | 0.015541 | 0.0040673 | 0.069316 | -0.00079046 | 0.069026 | -61.9308 | 63.0798 | -62.0956 | -62.0819 | 62.709 | 0.009155 | 0.018311 | 0.07782 | 63.0249 | -62.1826 | -0.23346 | 0.032043 | -0.068664 | -0.21973 | -0.33875 | -0.32043 | -0.022889 | 0.16479 | 61.8805 | 61.94 | 124.5712 | 124.942 | -0.068664 | 124.8871 | 61.8713 | -0.32043 | 124.942 | -0.068664 | 61.8713 | 124.5712 | 124.8871 | -125.1434 | -125.2304
793.6406 | 125.0885 | -61.8988 | 63.0707 | 0.096359 | 0.012256 | 0.01255 | 0.0034265 | 0.067394 | -0.0012177 | 0.069667 | -61.9583 | 63.0569 | -62.1185 | -62.114 | 62.6678 | -0.032043 | 0.032043 | 0.032043 | 63.0341 | -62.1735 | -0.21973 | -0.013733 | -0.059509 | -0.21515 | -0.40283 | -0.27466 | -0.036621 | 0.16022 | 61.9308 | 61.9308 | 124.5667 | 124.9557 | -0.059509 | 124.9329 | 61.8668 | -0.27466 | 124.9557 | -0.059509 | 61.8668 | 124.5667 | 124.9329 | -125.1892 | -125.2441
794.6562 | 125.1892 | -61.8622 | 62.9791 | 0.11925 | 0.0099057 | 0.014046 | -0.0034095 | 0.067821 | -0.00036306 | 0.070735 | -61.94 | 62.9242 | -62.1185 | -62.0499 | 62.7869 | 0.073242 | -0.16479 | 0.13733 | 62.9974 | -62.1048 | -0.25635 | -0.054932 | -0.077819 | -0.18768 | -0.19226 | -0.24261 | 0.018311 | 0.17853 | 61.6974 | 61.9995 | 124.649 | 124.7864 | -0.077819 | 124.8596 | 61.9354 | -0.24261 | 124.7864 | -0.077819 | 61.9354 | 124.649 | 124.8596 | -125.0977 | -125.0839
795.6406 | 125.1297 | -61.8576 | 63.0661 | -0.10963 | 0.01076 | 0.012123 | 0.0034265 | 0.066326 | -0.0010041 | 0.07223 | -61.9034 | 63.0432 | -62.1094 | -62.0224 | 62.7548 | 0.09613 | 0.036621 | 0.1831 | 63.0386 | -62.1597 | -0.25177 | -0.022888 | -0.045776 | -0.16479 | -0.31128 | -0.30212 | -0.027466 | 0.20599 | 61.8942 | 62.0407 | 124.6124 | 124.9008 | -0.045776 | 124.8962 | 61.9537 | -0.30212 | 124.9008 | -0.045776 | 61.9537 | 124.6124 | 124.8962 | -125.1755 | -125.2258
796.6406 | 125.1434 | -61.8576 | 63.0341 | 0.24132 | 0.010333 | 0.0095595 | 0.0049219 | 0.068035 | -0.00057686 | 0.067103 | -61.8393 | 63.0203 | -62.114 | -62.0132 | 62.7548 | 0.082397 | 0.032043 | 0.16937 | 63.0569 | -62.1597 | -0.25635 | -0.013733 | 0.018311 | -0.15564 | -0.27924 | -0.30212 | 0.022888 | 0.27466 | 61.8896 | 62.027 | 124.6124 | 124.8779 | 0.018311 | 124.9146 | 61.94 | -0.30212 | 124.8779 | 0.018311 | 61.94 | 124.6124 | 124.9146 | -125.148 | -125.1938
797.6406 | 125.1755 | -61.8576 | 63.0203 | 0.17265 | 0.012256 | 0.011482 | 0.00064935 | 0.067821 | -0.0014313 | 0.067958 | -61.9446 | 63.002 | -62.1231 | -62.0499 | 62.7457 | 0.041199 | -0.15564 | 0.11902 | 62.9929 | -62.1689 | -0.2655 | -0.018311 | -0.086975 | -0.19226 | -0.27466 | -0.31128 | -0.027466 | 0.17853 | 61.702 | 61.9766 | 124.6033 | 124.8596 | -0.086975 | 124.8505 | 61.8988 | -0.31128 | 124.8596 | -0.086975 | 61.8988 | 124.6033 | 124.8505 | -125.1434 | -125.1892
798.6406 | 125.0931 | -61.8988 | 63.0432 | 0.042953 | 0.011615 | 0.014046 | 0.0032129 | 0.068462 | -0.0022859 | 0.069453 | -61.9537 | 63.0295 | -62.0911 | -62.0819 | 62.6816 | 0 | 0.013733 | 0.086975 | 63.0249 | -62.1872 | -0.19226 | -0.013733 | -0.054931 | -0.18311 | -0.36163 | -0.28839 | -0.018311 | 0.13733 | 61.9125 | 61.9858 | 124.5804 | 124.9283 | -0.054931 | 124.9237 | 61.8988 | -0.28839 | 124.9283 | -0.054931 | 61.8988 | 124.5804 | 124.9237 | -125.1343 | -125.2304
799.6562 | 125.1709 | -61.8622 | 63.0112 | 0.073471 | 0.0086239 | 0.010628 | -0.0061865 | 0.065258 | -0.00079046 | 0.06988 | -62.0361 | 62.9745 | -62.1002 | -62.0819 | 62.7594 | 0.041199 | -0.068665 | 0.13733 | 62.9974 | -62.1094 | -0.23804 | -0.036621 | -0.17395 | -0.21973 | -0.25177 | -0.24719 | -0.013732 | 0.064087 | 61.7935 | 61.9995 | 124.6216 | 124.8367 | -0.17395 | 124.8596 | 61.9034 | -0.24719 | 124.8367 | -0.17395 | 61.9034 | 124.6216 | 124.8596 | -125.1114 | -125.1205
800.6406 | 125.1068 | -61.8805 | 63.0569 | -0.018082 | 0.012469 | 0.018105 | 0.0053491 | 0.066326 | 6.414e-05 | 0.069026 | -61.9217 | 63.0249 | -62.1048 | -62.059 | 62.7182 | 0.041199 | 0.018311 | 0.1236 | 63.0066 | -62.1735 | -0.2243 | -0.032044 | -0.041199 | -0.17853 | -0.33875 | -0.29297 | -0.050354 | 0.1831 | 61.8988 | 62.0041 | 124.5987 | 124.9054 | -0.041199 | 124.8871 | 61.9217 | -0.29297 | 124.9054 | -0.041199 | 61.9217 | 124.5987 | 124.8871 | -125.1617 | -125.2304
801.6406 | 125.1709 | -61.8713 | 63.0661 | -0.17067 | 0.012683 | 0.016182 | 0.0057763 | 0.068889 | -0.0027131 | 0.069453 | -61.8988 | 63.0661 | -62.114 | -61.9812 | 62.851 | 0.086975 | 0.082397 | 0.18768 | 63.0569 | -62.1735 | -0.24262 | 0 | -0.027466 | -0.10986 | -0.21515 | -0.30212 | -0.009155 | 0.21515 | 61.9537 | 62.059 | 124.7223 | 124.9374 | -0.027466 | 124.9283 | 61.9583 | -0.30212 | 124.9374 | -0.027466 | 61.9583 | 124.7223 | 124.9283 | -125.1801 | -125.2396
802.6406 | 125.1434 | -61.8805 | 63.0295 | -0.063858 | 0.010547 | 0.013832 | 0.0032129 | 0.070171 | -0.0016449 | 0.069026 | -61.9034 | 63.0341 | -62.1277 | -62.0407 | 62.7457 | 0.059509 | 0.018311 | 0.12817 | 63.0341 | -62.146 | -0.24719 | 0.004578 | -0.022888 | -0.16022 | -0.28381 | -0.2655 | 0.004578 | 0.2243 | 61.8988 | 62.0087 | 124.6262 | 124.9146 | -0.022888 | 124.9146 | 61.94 | -0.2655 | 124.9146 | -0.022888 | 61.94 | 124.6262 | 124.9146 | -125.1572 | -125.1755
803.6406 | 125.1343 | -61.8942 | 63.0478 | -0.025711 | 0.011615 | 0.011696 | 0.0034265 | 0.068462 | 0.00049134 | 0.068812 | -61.9171 | 63.0295 | -62.0911 | -62.0361 | 62.7319 | 0.082397 | 0 | 0.14648 | 63.0707 | -62.1368 | -0.19684 | -0.018311 | -0.022888 | -0.14191 | -0.31586 | -0.24261 | 0.022888 | 0.17395 | 61.8942 | 62.0407 | 124.6262 | 124.9237 | -0.022888 | 124.9649 | 61.9766 | -0.24261 | 124.9237 | -0.022888 | 61.9766 | 124.6262 | 124.9649 | -125.1389 | -125.1846
804.6562 | 125.2213 | -61.8027 | 63.0295 | -0.15541 | 0.0090513 | 0.0057143 | -0.0044775 | 0.063549 | -0.0014313 | 0.069239 | -61.9171 | 63.002 | -62.0544 | -62.1048 | 62.8555 | 0.21515 | -0.11444 | 0.24719 | 62.9883 | -62.0865 | -0.25177 | -0.027466 | -0.11444 | -0.30212 | -0.17395 | -0.28381 | -0.041199 | 0.13733 | 61.6882 | 62.0499 | 124.6582 | 124.8047 | -0.11444 | 124.791 | 62.0178 | -0.28381 | 124.8047 | -0.11444 | 62.0178 | 124.6582 | 124.791 | -125.0839 | -125.116
805.6406 | 125.148 | -61.8622 | 63.0661 | -0.16304 | 0.012256 | 0.013619 | 0.0027855 | 0.066326 | 0.0028411 | 0.069453 | -61.908 | 62.9974 | -62.1048 | -62.1002 | 62.9379 | 0.10529 | 0.050354 | 0.20142 | 63.0386 | -62.146 | -0.24261 | -0.068664 | -0.045776 | -0.23804 | -0.12817 | -0.28381 | -0.027466 | 0.19684 | 61.9125 | 62.0636 | 124.8001 | 124.8596 | -0.045776 | 124.9008 | 61.9675 | -0.28381 | 124.8596 | -0.045776 | 61.9675 | 124.8001 | 124.9008 | -125.1709 | -125.2121
806.6406 | 125.1755 | -61.8713 | 63.0615 | -0.056229 | 0.01076 | 0.012337 | 0.0044945 | 0.068676 | -0.0031403 | 0.069667 | -61.9125 | 63.0386 | -62.1323 | -62.0499 | 62.7228 | 0.045776 | 0.018311 | 0.13733 | 63.0432 | -62.1506 | -0.26093 | -0.022888 | -0.041199 | -0.17853 | -0.33875 | -0.27924 | -0.01831 | 0.21973 | 61.8896 | 62.0087 | 124.5941 | 124.91 | -0.041199 | 124.9146 | 61.9171 | -0.27924 | 124.91 | -0.041199 | 61.9171 | 124.5941 | 124.9146 | -125.1938 | -125.2121
807.6562 | 125.0839 | -61.8759 | 63.0707 | -0.25459 | 0.010333 | 0.011055 | -0.0029823 | 0.066539 | -0.00014946 | 0.068812 | -61.9675 | 63.0066 | -62.114 | -62.0911 | 62.7319 | 0.073242 | 0.14191 | 0.16937 | 63.0615 | -62.1185 | -0.23804 | -0.064087 | -0.091552 | -0.21515 | -0.33874 | -0.24261 | -0.009156 | 0.14649 | 62.0178 | 62.0453 | 124.6078 | 124.8825 | -0.091552 | 124.9374 | 61.9492 | -0.24261 | 124.8825 | -0.091552 | 61.9492 | 124.6078 | 124.9374 | -125.1846 | -125.1892
808.6406 | 125.0977 | -61.8896 | 63.089 | -0.25459 | 0.013324 | 0.012337 | 0.00043575 | 0.066326 | 0.0019867 | 0.070521 | -61.9629 | 63.0569 | -62.0819 | -62.0773 | 62.7045 | 0.068665 | 0.12817 | 0.16022 | 63.0661 | -62.1689 | -0.19226 | -0.032043 | -0.073243 | -0.18768 | -0.38452 | -0.27924 | -0.022888 | 0.11902 | 62.0178 | 62.0499 | 124.5941 | 124.9466 | -0.073243 | 124.9557 | 61.9583 | -0.27924 | 124.9466 | -0.073243 | 61.9583 | 124.5941 | 124.9557 | -125.1709 | -125.2579
809.6406 | 125.1205 | -61.8942 | 63.0524 | -0.04097 | 0.011615 | 0.011696 | 0.0051355 | 0.069103 | -0.00014946 | 0.070735 | -61.9171 | 63.0203 | -62.1323 | -62.0544 | 62.7182 | 0.041199 | 0.004578 | 0.13733 | 63.0661 | -62.1506 | -0.23804 | -0.032043 | -0.022888 | -0.16022 | -0.33417 | -0.25635 | 0.013733 | 0.21515 | 61.8988 | 62.0316 | 124.6124 | 124.9146 | -0.022888 | 124.9603 | 61.9354 | -0.25635 | 124.9146 | -0.022888 | 61.9354 | 124.6124 | 124.9603 | -125.1846 | -125.2029
810.6406 | 125.1297 | -61.8851 | 63.0341 | -0.025711 | 0.0099057 | 0.017037 | 0.0044945 | 0.069744 | 6.414e-05 | 0.069667 | -61.9125 | 63.0249 | -62.0911 | -62.0453 | 62.7365 | 0.068665 | 0.018311 | 0.1236 | 63.0707 | -62.1735 | -0.20599 | -0.009156 | -0.027466 | -0.16022 | -0.29755 | -0.28839 | 0.036621 | 0.17853 | 61.9034 | 62.0087 | 124.6216 | 124.91 | -0.027466 | 124.9557 | 61.9537 | -0.28839 | 124.91 | -0.027466 | 61.9537 | 124.6216 | 124.9557 | -125.1251 | -125.2075
811.6406 | 125.116 | -61.8805 | 63.0981 | -0.20882 | 0.010974 | 0.013405 | -0.00020505 | 0.066967 | 0.0013457 | 0.069026 | -61.9492 | 63.0478 | -62.1231 | -62.0682 | 62.7228 | 0.050354 | 0.1236 | 0.16937 | 63.089 | -62.146 | -0.24262 | -0.050354 | -0.068665 | -0.18768 | -0.37537 | -0.2655 | -0.009156 | 0.17395 | 62.0041 | 62.0499 | 124.6033 | 124.9283 | -0.068665 | 124.9695 | 61.9308 | -0.2655 | 124.9283 | -0.068665 | 61.9308 | 124.6033 | 124.9695 | -125.2213 | -125.2441
812.6562 | 125.2396 | -61.8347 | 63.0341 | -0.10201 | 0.010974 | 0.011055 | -0.0064003 | 0.065258 | 6.414e-05 | 0.070308 | -61.94 | 62.9196 | -62.0956 | -62.0132 | 62.796 | 0.13275 | -0.073242 | 0.24261 | 63.0157 | -62.1048 | -0.26093 | -0.11444 | -0.10529 | -0.17853 | -0.23804 | -0.27008 | -0.018311 | 0.15564 | 61.7615 | 62.0773 | 124.6307 | 124.7543 | -0.10529 | 124.8505 | 61.9675 | -0.27008 | 124.7543 | -0.10529 | 61.9675 | 124.6307 | 124.8505 | -125.1297 | -125.1389
813.6406 | 125.1526 | -61.8851 | 63.0615 | -0.10963 | 0.0094785 | 0.013405 | 0.0044945 | 0.065899 | -0.00036306 | 0.066462 | -61.8942 | 63.0295 | -62.0819 | -62.0316 | 62.764 | -0.13733 | 0.07782 | 0.27008 | 63.0341 | -62.1872 | -0.19684 | -0.032043 | -0.009155 | -0.14648 | -0.29755 | -0.30212 | -0.027465 | 0.18768 | 61.9629 | 62.1552 | 124.649 | 124.9146 | -0.009155 | 124.9191 | 61.7477 | -0.30212 | 124.9146 | -0.009155 | 61.7477 | 124.649 | 124.9191 | -125.1434 | -125.2487
814.6406 | 125.1663 | -61.8805 | 62.9837 | 0.16502 | 0.010333 | 0.01255 | 0.00022215 | 0.06718 | 0.00027774 | 0.068171 | -61.9125 | 62.9745 | -62.0956 | -62.0224 | 62.7731 | 0.041199 | -0.16937 | 0.13733 | 62.9837 | -62.1368 | -0.21515 | -0.009156 | -0.032044 | -0.14191 | -0.21057 | -0.25635 | 0 | 0.1831 | 61.7111 | 62.0178 | 124.6536 | 124.855 | -0.032044 | 124.8642 | 61.9217 | -0.25635 | 124.855 | -0.032044 | 61.9217 | 124.6536 | 124.8642 | -125.0793 | -125.1205
815.6406 | 125.1389 | -61.8576 | 63.0524 | -0.20119 | 0.011401 | 0.012123 | 0.0021447 | 0.066326 | -0.00079046 | 0.067317 | -61.9171 | 63.0569 | -62.0911 | -62.0178 | 62.7457 | 0.091553 | 0.064087 | 0.19684 | 63.0478 | -62.146 | -0.23346 | 0.004578 | -0.059509 | -0.16022 | -0.3067 | -0.28839 | -0.004577 | 0.17395 | 61.9217 | 62.0544 | 124.6033 | 124.9146 | -0.059509 | 124.9054 | 61.9492 | -0.28839 | 124.9146 | -0.059509 | 61.9492 | 124.6033 | 124.9054 | -125.1434 | -125.1984
816.6406 | 125.0748 | -61.8713 | 63.089 | -0.17067 | 0.0099057 | 0.014259 | 0.00022215 | 0.066112 | 0.0013457 | 0.069026 | -61.9629 | 63.0524 | -62.114 | -62.0819 | 62.7182 | 0.059509 | 0.12817 | 0.14191 | 63.0569 | -62.146 | -0.24262 | -0.036621 | -0.091553 | -0.21057 | -0.37079 | -0.27466 | -0.032043 | 0.15106 | 61.9995 | 62.0132 | 124.5895 | 124.9237 | -0.091553 | 124.9283 | 61.9308 | -0.27466 | 124.9237 | -0.091553 | 61.9308 | 124.5895 | 124.9283 | -125.2029 | -125.235
817.6562 | 125.2396 | -61.821 | 63.0157 | -0.13252 | 0.0064877 | 0.0050735 | -0.0040503 | 0.066326 | 0.00027774 | 0.069667 | -61.9217 | 62.9425 | -62.0911 | -61.9812 | 62.8326 | 0.14648 | -0.10071 | 0.26093 | 62.9837 | -62.0682 | -0.27008 | -0.073242 | -0.10071 | -0.16022 | -0.1831 | -0.24719 | -0.032043 | 0.16937 | 61.7203 | 62.0819 | 124.6536 | 124.7635 | -0.10071 | 124.8047 | 61.9675 | -0.24719 | 124.7635 | -0.10071 | 61.9675 | 124.6536 | 124.8047 | -125.1068 | -125.0839
818.6406 | 125.1297 | -61.8713 | 63.0524 | -0.079117 | 0.011188 | 0.012764 | 0.0070581 | 0.064617 | -0.0016449 | 0.067531 | -61.9171 | 63.0386 | -62.0728 | -62.0544 | 62.7411 | 0.10986 | 0.009155 | 0.16479 | 63.0066 | -62.1643 | -0.20142 | -0.013733 | -0.045776 | -0.1831 | -0.31128 | -0.29297 | -0.045776 | 0.15564 | 61.8805 | 62.0361 | 124.6124 | 124.91 | -0.045776 | 124.8779 | 61.9812 | -0.29297 | 124.91 | -0.045776 | 61.9812 | 124.6124 | 124.8779 | -125.1251 | -125.2167
819.6406 | 125.1205 | -61.8668 | 63.0753 | -0.19356 | 0.010119 | 0.010841 | 0.0027855 | 0.066753 | -0.0027131 | 0.070094 | -61.9492 | 63.0478 | -62.1185 | -62.0453 | 62.7365 | 0.064087 | 0.10986 | 0.16937 | 63.0569 | -62.1414 | -0.25177 | -0.027465 | -0.082398 | -0.17853 | -0.33875 | -0.27466 | -0.01831 | 0.16937 | 61.9766 | 62.0361 | 124.6033 | 124.9146 | -0.082398 | 124.9237 | 61.9308 | -0.27466 | 124.9146 | -0.082398 | 61.9308 | 124.6033 | 124.9237 | -125.1938 | -125.2167
820.6406 | 125.0793 | -61.8759 | 63.0661 | -0.22408 | 0.011401 | 0.015114 | 0.00043575 | 0.065471 | -0.0031403 | 0.067531 | -61.9904 | 63.0203 | -62.1094 | -61.9217 | 62.5854 | -0.068665 | 0.1236 | 0.15564 | 63.0478 | -62.1231 | -0.23346 | -0.045776 | -0.11444 | -0.045776 | -0.48065 | -0.24719 | -0.01831 | 0.11902 | 61.9995 | 62.0316 | 124.4614 | 124.8962 | -0.11444 | 124.9237 | 61.8073 | -0.24719 | 124.8962 | -0.11444 | 61.8073 | 124.4614 | 124.9237 | -125.1755 | -125.1892
821.6406 | 125.0748 | -61.8668 | 63.0844 | -0.308 | 0.0081967 | 0.0084915 | -0.0019141 | 0.065685 | -0.00079046 | 0.067958 | -61.9675 | 63.002 | -62.0911 | -62.0453 | 62.7319 | 0.073242 | 0.1236 | 0.1831 | 63.0432 | -62.1323 | -0.2243 | -0.082398 | -0.10071 | -0.17853 | -0.35248 | -0.2655 | -0.041199 | 0.1236 | 61.9904 | 62.0499 | 124.5987 | 124.8688 | -0.10071 | 124.91 | 61.94 | -0.2655 | 124.8688 | -0.10071 | 61.94 | 124.5987 | 124.91 | -125.1755 | -125.2167
822.6562 | 125.1617 | -61.8576 | 62.9791 | 0.13451 | 0.010119 | 0.010414 | 0.0025719 | 0.067394 | -0.0027131 | 0.06988 | -61.9034 | 62.9471 | -62.1094 | -62.0224 | 62.7594 | 0.050354 | -0.17853 | 0.13733 | 62.9608 | -62.1231 | -0.25177 | -0.032043 | -0.045776 | -0.16479 | -0.21973 | -0.2655 | -0.018311 | 0.20599 | 61.6791 | 61.9949 | 124.617 | 124.8047 | -0.045776 | 124.8184 | 61.908 | -0.2655 | 124.8047 | -0.045776 | 61.908 | 124.617 | 124.8184 | -125.0885 | -125.1022
823.6406 | 125.1068 | -61.8668 | 63.0615 | -0.25459 | 0.010547 | 0.0072097 | 0.00043575 | 0.062481 | -0.0016449 | 0.069667 | -61.9537 | 63.0203 | -62.0819 | -62.059 | 62.7136 | 0.068665 | 0.1236 | 0.16937 | 63.0478 | -62.1414 | -0.21515 | -0.041198 | -0.086975 | -0.19226 | -0.3479 | -0.27466 | -0.013732 | 0.12817 | 61.9904 | 62.0361 | 124.5804 | 124.8871 | -0.086975 | 124.9146 | 61.9354 | -0.27466 | 124.8871 | -0.086975 | 61.9354 | 124.5804 | 124.9146 | -125.1434 | -125.2029
824.6562 | 125.116 | -61.8668 | 63.0661 | -0.13252 | 0.01076 | 0.010841 | 0.0059899 | 0.066753 | -0.0014313 | 0.070094 | -61.8896 | 63.0203 | -62.0728 | -62.0361 | 62.7319 | 0.073242 | -0.009155 | 0.15564 | 63.0203 | -62.1277 | -0.20599 | -0.045776 | -0.022888 | -0.16937 | -0.33417 | -0.26093 | -0.045776 | 0.18311 | 61.8576 | 62.0224 | 124.5987 | 124.8871 | -0.022888 | 124.8871 | 61.94 | -0.26093 | 124.8871 | -0.022888 | 61.94 | 124.5987 | 124.8871 | -125.1389 | -125.1938
825.6406 | 125.148 | -61.8347 | 63.0524 | -0.24696 | 0.0090513 | 0.011482 | -0.0027687 | 0.063976 | 6.414e-05 | 0.068599 | -61.9171 | 62.9654 | -62.0911 | -62.0087 | 62.7777 | 0.13275 | 0.041199 | 0.25635 | 63.0569 | -62.0682 | -0.25635 | -0.086975 | -0.082397 | -0.17395 | -0.27466 | -0.23346 | 0.004578 | 0.17395 | 61.8759 | 62.0911 | 124.6124 | 124.8001 | -0.082397 | 124.8917 | 61.9675 | -0.23346 | 124.8001 | -0.082397 | 61.9675 | 124.6124 | 124.8917 | -125.1434 | -125.1205
826.6406 | 125.1114 | -61.853 | 63.0569 | -0.2317 | 0.010119 | 0.0091323 | -0.00020505 | 0.06184 | -0.0010041 | 0.069453 | -61.9354 | 62.9654 | -62.0773 | -62.0499 | 62.7274 | 0.086975 | 0.09613 | 0.18768 | 63.0569 | -62.0911 | -0.22431 | -0.091553 | -0.082398 | -0.19684 | -0.32959 | -0.23804 | 0 | 0.14191 | 61.9492 | 62.0407 | 124.5804 | 124.8184 | -0.082398 | 124.91 | 61.94 | -0.23804 | 124.8184 | -0.082398 | 61.94 | 124.5804 | 124.91 | -125.1343 | -125.148
827.6562 | 125.1297 | -61.8988 | 63.0386 | 0.020065 | 0.010974 | 0.012123 | 0.0083397 | 0.067394 | -0.00079046 | 0.068812 | -61.9034 | 63.0432 | -62.1185 | -62.0636 | 62.709 | 0.032043 | 0.004578 | 0.11444 | 63.0524 | -62.1185 | -0.21973 | 0.004578 | -0.004577 | -0.1648 | -0.32959 | -0.21973 | 0.013733 | 0.21515 | 61.9034 | 62.0132 | 124.6078 | 124.942 | -0.004577 | 124.9512 | 61.9308 | -0.21973 | 124.942 | -0.004577 | 61.9308 | 124.6078 | 124.9512 | -125.1572 | -125.1572
828.6406 | 125.2167 | -61.8347 | 63.0432 | -0.41481 | 0.0090513 | 0.011482 | -0.0055457 | 0.063121 | -0.0010041 | 0.070094 | -61.9537 | 62.8967 | -62.1002 | -61.9812 | 62.8052 | 0.1831 | -0.054932 | 0.29755 | 63.002 | -62.0911 | -0.2655 | -0.14648 | -0.11902 | -0.14648 | -0.23804 | -0.25635 | -0.041199 | 0.14648 | 61.7798 | 62.1323 | 124.6399 | 124.7314 | -0.11902 | 124.8367 | 62.0178 | -0.25635 | 124.7314 | -0.11902 | 62.0178 | 124.6399 | 124.8367 | -125.1434 | -125.1343
829.6406 | 125.1068 | -61.8759 | 63.0753 | -0.40718 | 0.0084103 | 0.012764 | 0.0027855 | 0.065685 | 0.0015595 | 0.067958 | -62.0132 | 63.0157 | -62.1231 | -62.0499 | 62.7045 | 0.045776 | 0.12817 | 0.15564 | 63.0432 | -62.1368 | -0.24719 | -0.059509 | -0.13733 | -0.17395 | -0.37079 | -0.26093 | -0.032043 | 0.10986 | 62.0041 | 62.0316 | 124.5804 | 124.8917 | -0.13733 | 124.9191 | 61.9217 | -0.26093 | 124.8917 | -0.13733 | 61.9217 | 124.5804 | 124.9191 | -125.1984 | -125.2121
830.6406 | 125.4044 | -61.8073 | 63.0615 | -0.12489 | 0.0073423 | 0.011269 | -0.0031959 | 0.063335 | -0.0018585 | 0.070521 | -61.8942 | 62.915 | -62.0773 | -61.9766 | 62.8418 | 0.16479 | -0.068665 | 0.27466 | 62.9974 | -62.0682 | -0.27008 | -0.14648 | -0.086975 | -0.16937 | -0.21973 | -0.26093 | -0.064086 | 0.18311 | 61.7386 | 62.0819 | 124.649 | 124.7223 | -0.086975 | 124.8047 | 61.972 | -0.26093 | 124.7223 | -0.086975 | 61.972 | 124.649 | 124.8047 | -125.1389 | -125.1297
831.6406 | 125.0656 | -61.8713 | 63.1027 | -0.24696 | 0.010547 | 0.0076369 | 0.0010767 | 0.064403 | -0.0012177 | 0.070308 | -61.9583 | 62.9883 | -62.0911 | -62.059 | 62.7182 | 0.07782 | 0.12817 | 0.17853 | 63.0341 | -62.1323 | -0.21973 | -0.11444 | -0.086975 | -0.18768 | -0.38452 | -0.26093 | -0.068664 | 0.13275 | 61.9995 | 62.0499 | 124.5895 | 124.8596 | -0.086975 | 124.9054 | 61.9492 | -0.26093 | 124.8596 | -0.086975 | 61.9492 | 124.5895 | 124.9054 | -125.1938 | -125.235
832.6406 | 125.1068 | -61.8851 | 63.0844 | -0.45296 | 0.010547 | 0.011055 | 0.0047081 | 0.062694 | -0.0018585 | 0.066676 | -61.9995 | 63.0112 | -62.1048 | -62.0636 | 62.6907 | 0.059509 | 0.14648 | 0.15564 | 63.0341 | -62.1185 | -0.21973 | -0.073243 | -0.11444 | -0.17853 | -0.39368 | -0.23346 | -0.050354 | 0.10528 | 62.0316 | 62.0407 | 124.5758 | 124.8962 | -0.11444 | 124.9191 | 61.9446 | -0.23346 | 124.8962 | -0.11444 | 61.9446 | 124.5758 | 124.9191 | -125.1892 | -125.2029
833.6406 | 125.2213 | -61.8393 | 63.0249 | -0.056229 | 0.0075559 | 0.012764 | -0.0027687 | 0.063762 | 0.0011321 | 0.068171 | -61.9354 | 62.915 | -62.1002 | -62.0132 | 62.7777 | 0.10071 | -0.086975 | 0.21515 | 63.0157 | -62.0819 | -0.26093 | -0.10986 | -0.096131 | -0.17395 | -0.24719 | -0.24262 | -0.009155 | 0.16479 | 61.7523 | 62.0544 | 124.617 | 124.7543 | -0.096131 | 124.855 | 61.94 | -0.24262 | 124.7543 | -0.096131 | 61.94 | 124.617 | 124.855 | -125.1251 | -125.1068
834.6406 | 125.1572 | -61.8439 | 63.0524 | -0.24696 | 0.0090513 | 0.011055 | -0.0010597 | 0.062908 | -0.0016449 | 0.066676 | -61.8988 | 62.9379 | -62.0316 | -61.9766 | 62.7914 | 0.13275 | 0 | 0.25635 | 63.002 | -62.114 | -0.18768 | -0.11444 | -0.054932 | -0.13275 | -0.26093 | -0.27008 | -0.050354 | 0.13275 | 61.8439 | 62.1002 | 124.6353 | 124.7818 | -0.054932 | 124.8459 | 61.9766 | -0.27008 | 124.7818 | -0.054932 | 61.9766 | 124.6353 | 124.8459 | -125.0839 | -125.1663
835.6406 | 125.2258 | -61.7935 | 63.0432 | -0.18593 | 0.0086239 | 0.0091323 | 0.0025719 | 0.061626 | -0.0022859 | 0.069239 | -62.059 | 62.9379 | -62.0316 | -62.0682 | 62.7686 | 0.16479 | -0.10529 | 0.23346 | 62.9745 | -62.0682 | -0.23804 | -0.10529 | -0.2655 | -0.27466 | -0.27466 | -0.27466 | -0.068665 | -0.027466 | 61.6882 | 62.027 | 124.5621 | 124.7314 | -0.2655 | 124.7681 | 61.9583 | -0.27466 | 124.7314 | -0.2655 | 61.9583 | 124.5621 | 124.7681 | -125.0748 | -125.1114
836.6406 | 125.1572 | -61.8439 | 63.0341 | -0.048599 | 0.010333 | 0.0091323 | 0.00086295 | 0.062694 | -0.0012177 | 0.069239 | -61.972 | 62.9105 | -62.1185 | -62.0361 | 62.7502 | 0.041199 | -0.068665 | 0.16022 | 62.9791 | -62.0956 | -0.27466 | -0.1236 | -0.12817 | -0.19226 | -0.28381 | -0.25177 | -0.054932 | 0.14648 | 61.7752 | 62.0041 | 124.5941 | 124.7543 | -0.12817 | 124.823 | 61.8851 | -0.25177 | 124.7543 | -0.12817 | 61.8851 | 124.5941 | 124.823 | -125.1526 | -125.1297
837.6406 | 125.1572 | -61.8484 | 63.0707 | -0.26222 | 0.0088375 | 0.0099869 | 0.0044945 | 0.060985 | -0.00057686 | 0.06988 | -61.8942 | 62.9517 | -62.059 | -61.9949 | 62.7777 | 0.1236 | 0.027466 | 0.24261 | 62.9974 | -62.1094 | -0.21057 | -0.11902 | -0.045776 | -0.14648 | -0.29297 | -0.26093 | -0.073242 | 0.16479 | 61.8759 | 62.0911 | 124.6262 | 124.8001 | -0.045776 | 124.8459 | 61.972 | -0.26093 | 124.8001 | -0.045776 | 61.972 | 124.6262 | 124.8459 | -125.1297 | -125.1801
838.6406 | 125.2029 | -61.821 | 63.0478 | -0.10201 | 0.011188 | 0.010841 | -0.00063225 | 0.061412 | -0.0020721 | 0.066249 | -61.9034 | 62.9105 | -62.0728 | -61.9675 | 62.8052 | 0.13275 | -0.086975 | 0.26093 | 62.97 | -62.0682 | -0.25177 | -0.13733 | -0.082397 | -0.14648 | -0.24261 | -0.24719 | -0.07782 | 0.16937 | 61.734 | 62.0819 | 124.6262 | 124.7314 | -0.082397 | 124.791 | 61.9537 | -0.24719 | 124.7314 | -0.082397 | 61.9537 | 124.6262 | 124.791 | -125.1205 | -125.116
839.6406 | 125.1114 | -61.8668 | 63.0844 | -0.23933 | 0.0071285 | 0.0087051 | 0.0038537 | 0.062053 | -0.00014946 | 0.068171 | -61.9263 | 62.9608 | -62.0865 | -62.0041 | 62.7228 | 0.091553 | 0.10071 | 0.20142 | 63.0432 | -62.1002 | -0.21973 | -0.1236 | -0.05951 | -0.13733 | -0.36163 | -0.23346 | -0.041199 | 0.16022 | 61.9675 | 62.0682 | 124.5895 | 124.8276 | -0.05951 | 124.91 | 61.9583 | -0.23346 | 124.8276 | -0.05951 | 61.9583 | 124.5895 | 124.91 | -125.1709 | -125.1846
840.6406 | 125.2075 | -61.8301 | 63.0203 | -0.048599 | 0.0079831 | 0.010841 | -0.0025549 | 0.062053 | -0.0022859 | 0.068171 | -61.9354 | 62.9196 | -62.0773 | -61.9904 | 62.7869 | 0.10529 | -0.086975 | 0.21057 | 62.9837 | -62.0773 | -0.24719 | -0.10071 | -0.10529 | -0.16022 | -0.23346 | -0.24719 | -0.036621 | 0.14191 | 61.7432 | 62.0407 | 124.617 | 124.7498 | -0.10529 | 124.8138 | 61.9354 | -0.24719 | 124.7498 | -0.10529 | 61.9354 | 124.617 | 124.8138 | -125.0977 | -125.0977
841.6406 | 125.1846 | -61.8164 | 63.0066 | -0.018082 | 0.0088375 | 0.011269 | -0.00063225 | 0.060985 | 0.00091854 | 0.069026 | -61.9583 | 62.9059 | -62.0956 | -62.0224 | 62.7777 | 0.10071 | -0.073242 | 0.19684 | 62.9654 | -62.0819 | -0.27924 | -0.10071 | -0.14191 | -0.20599 | -0.22888 | -0.2655 | -0.041199 | 0.13733 | 61.7432 | 62.0132 | 124.5941 | 124.7223 | -0.14191 | 124.7818 | 61.9171 | -0.2655 | 124.7223 | -0.14191 | 61.9171 | 124.5941 | 124.7818 | -125.1022 | -125.0885
842.6406 | 125.2304 | -61.821 | 63.0249 | -1.1854 | 0.0064877 | 0.012764 | 0.0015039 | 0.062053 | -0.0018585 | 0.068599 | -61.972 | 62.9013 | -62.0911 | -61.94 | 62.8189 | 0.16479 | -0.050354 | 0.28381 | 62.9791 | -62.0865 | -0.27008 | -0.1236 | -0.15106 | -0.11902 | -0.20599 | -0.2655 | -0.045776 | 0.11902 | 61.7706 | 62.1048 | 124.6399 | 124.7223 | -0.15106 | 124.8001 | 61.9858 | -0.2655 | 124.7223 | -0.15106 | 61.9858 | 124.6399 | 124.8001 | -125.116 | -125.1114
843.6406 | 125.1846 | -61.821 | 63.0295 | -0.086746 | 0.010333 | 0.0097733 | -0.0021277 | 0.060558 | 0.0017731 | 0.069239 | -61.8942 | 62.9105 | -62.0865 | -61.9583 | 62.796 | 0.13733 | -0.082397 | 0.22888 | 62.9837 | -62.0728 | -0.2655 | -0.11902 | -0.073242 | -0.13733 | -0.23346 | -0.25177 | -0.045776 | 0.19226 | 61.7386 | 62.0499 | 124.617 | 124.7314 | -0.073242 | 124.8047 | 61.9583 | -0.25177 | 124.7314 | -0.073242 | 61.9583 | 124.617 | 124.8047 | -125.116 | -125.1022
844.6406 | 125.2029 | -61.8256 | 63.0524 | -0.20119 | 0.0084103 | 0.0093459 | 0.00043575 | 0.064403 | 0.0019867 | 0.067958 | -61.8668 | 62.9288 | -62.0544 | -61.9583 | 62.8281 | 0.15564 | -0.041199 | 0.27924 | 62.9791 | -62.0865 | -0.22888 | -0.1236 | -0.041198 | -0.13275 | -0.2243 | -0.26093 | -0.073242 | 0.18768 | 61.7844 | 62.1048 | 124.6536 | 124.7543 | -0.041198 | 124.8047 | 61.9812 | -0.26093 | 124.7543 | -0.041198 | 61.9812 | 124.6536 | 124.8047 | -125.1068 | -125.1389
845.6406 | 125.1663 | -61.8439 | 63.0341 | 0.012436 | 0.0062741 | 0.011269 | -0.0017005 | 0.062267 | -0.00036306 | 0.06689 | -61.9675 | 62.9059 | -62.0865 | -62.0087 | 62.7228 | 0.073242 | -0.082397 | 0.16479 | 62.9745 | -62.0728 | -0.24262 | -0.12817 | -0.1236 | -0.1648 | -0.31128 | -0.22888 | -0.05951 | 0.11902 | 61.7615 | 62.0087 | 124.5666 | 124.7498 | -0.1236 | 124.8184 | 61.9171 | -0.22888 | 124.7498 | -0.1236 | 61.9171 | 124.5666 | 124.8184 | -125.1205 | -125.1068
846.6406 | 125.2487 | -61.8118 | 63.0295 | -0.13252 | 0.0099057 | 0.0089187 | -0.0023413 | 0.060558 | -0.0014313 | 0.067958 | -61.8942 | 62.8967 | -62.0728 | -61.94 | 62.8189 | 0.15564 | -0.11902 | 0.27008 | 62.9517 | -62.0911 | -0.26093 | -0.13275 | -0.082397 | -0.12817 | -0.21057 | -0.27923 | -0.07782 | 0.17853 | 61.6928 | 62.0819 | 124.6307 | 124.7086 | -0.082397 | 124.7635 | 61.9675 | -0.27923 | 124.7086 | -0.082397 | 61.9675 | 124.6307 | 124.7635 | -125.1022 | -125.1205
847.6562 | 125.0885 | -61.8576 | 63.0981 | -0.16304 | 0.010119 | 0.0084915 | 0.0015039 | 0.06184 | -0.0012177 | 0.068599 | -61.9217 | 63.0203 | -62.1002 | -62.0453 | 62.7136 | 0.059509 | 0.1236 | 0.15106 | 63.0157 | -62.1231 | -0.24262 | -0.07782 | -0.064087 | -0.18768 | -0.38452 | -0.2655 | -0.082398 | 0.17853 | 61.9812 | 62.0087 | 124.5712 | 124.8779 | -0.064087 | 124.8734 | 61.9171 | -0.2655 | 124.8779 | -0.064087 | 61.9171 | 124.5712 | 124.8734 | -125.1984 | -125.2213
848.6406 | 125.2121 | -61.8164 | 63.0203 | -0.20882 | 0.0094785 | 0.010201 | 8.546e-06 | 0.063335 | -0.00057686 | 0.067958 | -61.8759 | 62.9425 | -62.0911 | -61.9492 | 62.8189 | 0.15564 | -0.036621 | 0.27924 | 62.9929 | -62.0819 | -0.27466 | -0.07782 | -0.05951 | -0.13275 | -0.20142 | -0.2655 | -0.027466 | 0.21515 | 61.7798 | 62.0956 | 124.6353 | 124.7589 | -0.05951 | 124.8093 | 61.972 | -0.2655 | 124.7589 | -0.05951 | 61.972 | 124.6353 | 124.8093 | -125.1114 | -125.1022
849.6562 | 125.0931 | -61.8439 | 63.0753 | -0.30037 | 0.011828 | 0.010414 | 0.0044945 | 0.063335 | -0.0014313 | 0.066462 | -61.9492 | 63.0341 | -62.0956 | -62.0361 | 62.7274 | 0.068665 | 0.10529 | 0.16022 | 63.0524 | -62.1094 | -0.25177 | -0.041198 | -0.10529 | -0.19226 | -0.3479 | -0.2655 | -0.022888 | 0.14648 | 61.9492 | 62.0041 | 124.5712 | 124.8779 | -0.10529 | 124.8962 | 61.9125 | -0.2655 | 124.8779 | -0.10529 | 61.9125 | 124.5712 | 124.8962 | -125.1709 | -125.1846
850.6406 | 125.1709 | -61.8347 | 63.0112 | 0.10399 | 0.0081967 | 0.0097733 | -0.00084605 | 0.064403 | 0.00070494 | 0.070308 | -61.9354 | 62.9196 | -62.1002 | -62.0407 | 62.7319 | 0.036621 | -0.13733 | 0.11444 | 62.9562 | -62.0499 | -0.2655 | -0.091552 | -0.10071 | -0.20599 | -0.27923 | -0.21515 | -0.054931 | 0.16479 | 61.6974 | 61.9492 | 124.5667 | 124.7543 | -0.10071 | 124.791 | 61.8713 | -0.21515 | 124.7543 | -0.10071 | 61.8713 | 124.5667 | 124.791 | -125.1114 | -125.061
851.6406 | 125.1755 | -61.853 | 63.0432 | 0.042953 | 0.0086239 | 0.0095595 | -0.0017005 | 0.063762 | -0.0014313 | 0.067958 | -61.9675 | 62.9242 | -62.0773 | -61.9629 | 62.9791 | 0.23804 | -0.21057 | 0.15564 | 62.9562 | -62.0865 | -0.22431 | -0.11902 | -0.11444 | -0.10986 | -0.064087 | -0.23346 | -0.086975 | 0.10986 | 61.6425 | 62.0087 | 124.8322 | 124.7772 | -0.11444 | 124.8093 | 62.0911 | -0.23346 | 124.7772 | -0.11444 | 62.0911 | 124.8322 | 124.8093 | -125.1205 | -125.1297
852.6562 | 125.0656 | -61.8805 | 63.0661 | -0.22408 | 0.010547 | 0.010628 | 0.0025719 | 0.063549 | 0.0022003 | 0.069667 | -61.972 | 63.0386 | -62.0773 | -62.0544 | 62.7228 | 0.036621 | 0.14648 | 0.16022 | 63.0157 | -62.1368 | -0.19684 | -0.027466 | -0.091553 | -0.17395 | -0.34332 | -0.25635 | -0.050354 | 0.10529 | 62.027 | 62.0407 | 124.6033 | 124.9191 | -0.091553 | 124.8962 | 61.9171 | -0.25635 | 124.9191 | -0.091553 | 61.9171 | 124.6033 | 124.8962 | -125.1434 | -125.2029
853.6406 | 125.1389 | -61.8439 | 63.0249 | 0.035324 | 0.0099057 | 0.0080643 | -0.0025549 | 0.063549 | -0.0014313 | 0.069026 | -61.9537 | 62.9196 | -62.1048 | -62.0544 | 62.7502 | 0.054932 | -0.10529 | 0.10986 | 62.97 | -62.0911 | -0.26093 | -0.10528 | -0.10986 | -0.21057 | -0.27466 | -0.24719 | -0.054931 | 0.15106 | 61.7386 | 61.9537 | 124.5941 | 124.7635 | -0.10986 | 124.8138 | 61.8988 | -0.24719 | 124.7635 | -0.10986 | 61.8988 | 124.5941 | 124.8138 | -125.1297 | -125.116
854.6406 | 125.1846 | -61.8256 | 63.0432 | -0.20119 | 0.010547 | 0.0099869 | 0.0019311 | 0.063976 | -0.0018585 | 0.066676 | -61.908 | 62.9608 | -62.0819 | -61.9766 | 62.796 | 0.15564 | 0.013733 | 0.24719 | 62.9791 | -62.0911 | -0.25635 | -0.082398 | -0.082397 | -0.15106 | -0.24719 | -0.2655 | -0.064087 | 0.17395 | 61.8393 | 62.0728 | 124.6216 | 124.7864 | -0.082397 | 124.8047 | 61.9812 | -0.2655 | 124.7864 | -0.082397 | 61.9812 | 124.6216 | 124.8047 | -125.1251 | -125.1343
855.6406 | 125.1709 | -61.8301 | 63.0203 | -0.071488 | 0.0060605 | 0.010841 | 8.546e-06 | 0.06184 | -0.0033539 | 0.067958 | -61.9492 | 62.9105 | -62.0911 | -62.0178 | 62.764 | 0.073242 | -0.082397 | 0.16479 | 62.9562 | -62.1048 | -0.26093 | -0.10986 | -0.11902 | -0.18768 | -0.25635 | -0.27466 | -0.064087 | 0.14191 | 61.7477 | 61.9949 | 124.5941 | 124.7406 | -0.11902 | 124.7864 | 61.9034 | -0.27466 | 124.7406 | -0.11902 | 61.9034 | 124.5941 | 124.7864 | -125.1114 | -125.1251
856.6406 | 125.1892 | -61.8164 | 63.0249 | -0.086746 | 0.010119 | 0.011482 | -0.0021277 | 0.062908 | -0.00079046 | 0.069239 | -61.9171 | 62.9379 | -62.0911 | -61.9812 | 62.7869 | 0.13733 | -0.091553 | 0.23804 | 62.9471 | -62.059 | -0.27466 | -0.086975 | -0.10071 | -0.16479 | -0.23804 | -0.24262 | -0.077819 | 0.17395 | 61.7249 | 62.0544 | 124.6033 | 124.7543 | -0.10071 | 124.7635 | 61.9537 | -0.24262 | 124.7543 | -0.10071 | 61.9537 | 124.6033 | 124.7635 | -125.116 | -125.0839
857.6406 | 125.2808 | -61.8393 | 63.0432 | -0.16304 | 0.0077695 | 0.0080643 | -0.0017005 | 0.060344 | -0.00079046 | 0.068812 | -61.8759 | 62.9379 | -62.1002 | -61.9354 | 62.8235 | 0.091553 | 0.37079 | 0.086975 | 63.0066 | -62.0636 | -0.26093 | -0.10529 | -0.036622 | -0.096131 | -0.21973 | -0.22431 | -0.036621 | 0.2243 | 62.2101 | 61.9263 | 124.6628 | 124.7772 | -0.036622 | 124.8459 | 61.9308 | -0.22431 | 124.7772 | -0.036622 | 61.9308 | 124.6628 | 124.8459 | -125.1434 | -125.1068
858.6406 | 125.1389 | -61.8622 | 63.0341 | 0.15739 | 0.0088375 | 0.0072097 | -0.00020505 | 0.062053 | -0.00079046 | 0.069026 | -61.9675 | 62.9105 | -62.0773 | -62.0361 | 62.7228 | 0.036621 | -0.11902 | 0.12817 | 62.9517 | -62.114 | -0.21515 | -0.1236 | -0.10528 | -0.17395 | -0.31128 | -0.25177 | -0.082398 | 0.10986 | 61.7432 | 61.9904 | 124.585 | 124.7726 | -0.10528 | 124.8138 | 61.8988 | -0.25177 | 124.7726 | -0.10528 | 61.8988 | 124.585 | 124.8138 | -125.1114 | -125.148
859.6406 | 125.1846 | -61.7844 | 63.0478 | 0.2108 | 0.010547 | 0.0078507 | -0.0017005 | 0.063549 | -0.00036306 | 0.069453 | -61.853 | 62.9333 | -62.0682 | -61.94 | 62.8189 | 0.17395 | -0.050354 | 0.29297 | 62.9745 | -62.0682 | -0.28381 | -0.11444 | -0.068664 | -0.15564 | -0.22888 | -0.28381 | -0.073243 | 0.21515 | 61.734 | 62.0773 | 124.6033 | 124.7177 | -0.068664 | 124.7589 | 61.9583 | -0.28381 | 124.7177 | -0.068664 | 61.9583 | 124.6033 | 124.7589 | -125.116 | -125.116
860.6406 | 125.1846 | -61.8484 | 63.0066 | 0.12688 | 0.0077695 | 0.010414 | -0.00020505 | 0.062481 | 6.414e-05 | 0.067958 | -61.94 | 62.883 | -62.0956 | -62.0224 | 62.7319 | 0.032043 | -0.13733 | 0.11902 | 62.9471 | -62.0865 | -0.24719 | -0.1236 | -0.091552 | -0.17395 | -0.27466 | -0.23804 | -0.059509 | 0.15564 | 61.7111 | 61.9675 | 124.5804 | 124.7314 | -0.091552 | 124.7955 | 61.8805 | -0.23804 | 124.7314 | -0.091552 | 61.8805 | 124.5804 | 124.7955 | -125.1022 | -125.0931
861.6406 | 125.1617 | -61.8622 | 62.9745 | 0.14976 | 0.0096921 | 0.014046 | 0.00086295 | 0.062908 | 0.00049134 | 0.068812 | -61.9308 | 62.9105 | -62.1002 | -62.027 | 62.7274 | 0.054932 | -0.1236 | 0.1236 | 62.9471 | -62.0956 | -0.23804 | -0.064087 | -0.068664 | -0.16479 | -0.24719 | -0.23346 | -0.027465 | 0.16937 | 61.7386 | 61.9858 | 124.5895 | 124.7726 | -0.068664 | 124.8093 | 61.9171 | -0.23346 | 124.7726 | -0.068664 | 61.9171 | 124.5895 | 124.8093 | -125.0748 | -125.0702
862.6406 | 125.1801 | -61.821 | 63.0478 | -0.20119 | 0.0058469 | 0.011482 | 0.0027855 | 0.061199 | -0.0027131 | 0.068171 | -61.9171 | 62.9379 | -62.0499 | -61.9629 | 62.8098 | 0.15564 | -0.027466 | 0.26093 | 62.9883 | -62.0682 | -0.22888 | -0.10986 | -0.09613 | -0.14191 | -0.23804 | -0.24719 | -0.05951 | 0.13275 | 61.7935 | 62.0819 | 124.6307 | 124.7589 | -0.09613 | 124.8093 | 61.9766 | -0.24719 | 124.7589 | -0.09613 | 61.9766 | 124.6307 | 124.8093 | -125.0977 | -125.116
863.6406 | 125.1617 | -61.821 | 63.0386 | -0.010452 | 0.011188 | 0.014687 | -0.0019141 | 0.062481 | -0.0024995 | 0.070094 | -61.972 | 62.9196 | -62.0773 | -62.0132 | 62.764 | 0.07782 | -0.086975 | 0.16937 | 62.9608 | -62.0819 | -0.25635 | -0.11902 | -0.15106 | -0.19226 | -0.27466 | -0.26093 | -0.07782 | 0.10529 | 61.734 | 61.9904 | 124.585 | 124.7406 | -0.15106 | 124.7818 | 61.8988 | -0.26093 | 124.7406 | -0.15106 | 61.8988 | 124.585 | 124.7818 | -125.116 | -125.1205
864.6562 | 125.0977 | -61.8759 | 63.0203 | 0.20317 | 0.012683 | 0.015755 | 0.0057763 | 0.065258 | -0.00057686 | 0.069453 | -61.9537 | 62.9745 | -62.114 | -62.0499 | 62.7045 | -0.009155 | -0.10529 | 0.068665 | 62.9608 | -62.1231 | -0.23804 | -0.045777 | -0.077819 | -0.17395 | -0.31586 | -0.24719 | -0.05951 | 0.16022 | 61.7706 | 61.9446 | 124.5804 | 124.8505 | -0.077819 | 124.8367 | 61.8668 | -0.24719 | 124.8505 | -0.077819 | 61.8668 | 124.5804 | 124.8367 | -125.1343 | -125.1434
865.6406 | 125.1389 | -61.8256 | 63.0157 | 0.12688 | 0.0099057 | 0.012337 | -0.00063225 | 0.06419 | -0.00079046 | 0.068812 | -61.9583 | 62.9105 | -62.0865 | -62.0407 | 62.7457 | 0.032043 | -0.09613 | 0.12817 | 62.9745 | -62.0682 | -0.26093 | -0.10529 | -0.13275 | -0.21515 | -0.27008 | -0.24261 | -0.041199 | 0.12817 | 61.7294 | 61.9537 | 124.5712 | 124.736 | -0.13275 | 124.8001 | 61.8576 | -0.24261 | 124.736 | -0.13275 | 61.8576 | 124.5712 | 124.8001 | -125.1022 | -125.0839
866.6406 | 125.1572 | -61.8256 | 63.0157 | 0.13451 | 0.011401 | 0.0061417 | 0.00043575 | 0.062053 | -0.0018585 | 0.068171 | -61.9629 | 62.9059 | -62.1048 | -62.0453 | 62.7411 | 0.022888 | -0.11444 | 0.11902 | 62.9471 | -62.1048 | -0.27923 | -0.10986 | -0.13733 | -0.21973 | -0.27466 | -0.27923 | -0.068664 | 0.14191 | 61.7111 | 61.9446 | 124.5667 | 124.7314 | -0.13733 | 124.7726 | 61.8484 | -0.27923 | 124.7314 | -0.13733 | 61.8484 | 124.5667 | 124.7726 | -125.1205 | -125.1205
867.6406 | 125.2075 | -61.8256 | 63.0386 | -0.24696 | 0.0096921 | 0.011055 | -0.0014869 | 0.062908 | -0.0020721 | 0.068385 | -61.8622 | 62.915 | -62.059 | -61.9492 | 62.8189 | 0.16022 | -0.027466 | 0.27008 | 62.9654 | -62.0499 | -0.23346 | -0.1236 | -0.036621 | -0.1236 | -0.21973 | -0.2243 | -0.073242 | 0.19684 | 61.7981 | 62.0956 | 124.6445 | 124.7406 | -0.036621 | 124.791 | 61.9858 | -0.2243 | 124.7406 | -0.036621 | 61.9858 | 124.6445 | 124.791 | -125.0977 | -125.0885
868.6406 | 125.1343 | -61.8668 | 63.0157 | 0.16502 | 0.0094785 | 0.011696 | -0.0012733 | 0.063121 | -0.00079046 | 0.069453 | -61.9446 | 62.9059 | -62.0911 | -62.0224 | 62.7319 | 0.054932 | -0.12817 | 0.11444 | 62.9654 | -62.1048 | -0.2243 | -0.10986 | -0.07782 | -0.15564 | -0.28381 | -0.23804 | -0.050354 | 0.14648 | 61.7386 | 61.9812 | 124.5987 | 124.7726 | -0.07782 | 124.8322 | 61.9217 | -0.23804 | 124.7726 | -0.07782 | 61.9217 | 124.5987 | 124.8322 | -125.1068 | -125.1205
869.6406 | 125.1617 | -61.8027 | 63.0569 | -0.86494 | 0.0075559 | 0.0076369 | 0.0012903 | 0.062908 | -0.0018585 | 0.069239 | -61.9583 | 62.9059 | -62.0865 | -61.9263 | 62.8098 | 0.16022 | -0.068665 | 0.29755 | 62.9379 | -62.0544 | -0.28381 | -0.15106 | -0.15564 | -0.1236 | -0.24719 | -0.25177 | -0.11902 | 0.12817 | 61.734 | 62.1002 | 124.6124 | 124.7086 | -0.15564 | 124.7406 | 61.9629 | -0.25177 | 124.7086 | -0.15564 | 61.9629 | 124.6124 | 124.7406 | -125.1434 | -125.1114
870.6406 | 125.1617 | -61.8484 | 63.0112 | 0.073471 | 0.0081967 | 0.0072097 | 8.546e-06 | 0.063335 | -0.0014313 | 0.068812 | -61.9354 | 62.9013 | -62.0773 | -62.0041 | 62.7319 | 0.050354 | -0.13733 | 0.12817 | 62.9242 | -62.0865 | -0.22888 | -0.10986 | -0.086975 | -0.15564 | -0.27923 | -0.23804 | -0.086975 | 0.14191 | 61.7111 | 61.9766 | 124.5804 | 124.7498 | -0.086975 | 124.7726 | 61.8988 | -0.23804 | 124.7498 | -0.086975 | 61.8988 | 124.5804 | 124.7726 | -125.0885 | -125.0977
871.6406 | 125.1251 | -61.8301 | 63.0203 | 0.0811 | 0.0079831 | 0.0093459 | 0.00043575 | 0.062694 | -0.0020721 | 0.067744 | -61.9446 | 62.9105 | -62.0956 | -62.027 | 62.7823 | 0.25177 | -0.2243 | 0.091553 | 62.9608 | -62.0773 | -0.2655 | -0.10986 | -0.11444 | -0.19684 | -0.23804 | -0.24719 | -0.05951 | 0.15106 | 61.6058 | 61.9217 | 124.6124 | 124.7406 | -0.11444 | 124.791 | 62.0819 | -0.24719 | 124.7406 | -0.11444 | 62.0819 | 124.6124 | 124.791 | -125.116 | -125.0977
872.6406 | 125.1755 | -61.8439 | 63.0066 | 0.035324 | 0.0075559 | 0.01255 | -0.0023413 | 0.062694 | -0.0018585 | 0.066462 | -61.9583 | 62.9013 | -62.0773 | -62.0178 | 62.7686 | 0.07782 | -0.068665 | 0.16937 | 62.9288 | -62.0773 | -0.23346 | -0.10529 | -0.11444 | -0.17395 | -0.23804 | -0.23346 | -0.07782 | 0.11902 | 61.7752 | 62.0132 | 124.6124 | 124.7452 | -0.11444 | 124.7726 | 61.9217 | -0.23346 | 124.7452 | -0.11444 | 61.9217 | 124.6124 | 124.7726 | -125.0839 | -125.0839
873.6406 | 125.2121 | -61.821 | 63.0478 | 0.11162 | 0.010974 | 0.010628 | -0.00084605 | 0.063121 | -0.0012177 | 0.070735 | -61.9537 | 62.9105 | -62.0911 | -62.027 | 62.7365 | 0.050354 | -0.10071 | 0.13275 | 62.9333 | -62.0636 | -0.27008 | -0.13733 | -0.13275 | -0.20599 | -0.31128 | -0.24262 | -0.11444 | 0.13733 | 61.7203 | 61.9537 | 124.5575 | 124.7314 | -0.13275 | 124.7543 | 61.8713 | -0.24262 | 124.7314 | -0.13275 | 61.8713 | 124.5575 | 124.7543 | -125.1389 | -125.1114
874.6562 | 125.1755 | -61.8301 | 62.9791 | 0.18791 | 0.010119 | 0.011269 | 0.0032129 | 0.06419 | -0.0024995 | 0.070521 | -61.8896 | 62.9425 | -62.0636 | -61.9858 | 62.7594 | 0.1831 | -0.53558 | 0.1236 | 62.883 | -62.114 | -0.23346 | -0.036621 | -0.059509 | -0.15564 | -0.21973 | -0.28381 | -0.09613 | 0.17395 | 61.2946 | 61.9537 | 124.5895 | 124.7726 | -0.059509 | 124.7131 | 62.0132 | -0.28381 | 124.7726 | -0.059509 | 62.0132 | 124.5895 | 124.7131 | -125.0427 | -125.0931
875.6406 | 125.1801 | -61.8347 | 63.0249 | -0.025711 | 0.010547 | 0.010414 | -0.0010597 | 0.063762 | 0.0024139 | 0.067744 | -61.9537 | 62.9013 | -62.1002 | -62.0224 | 62.764 | 0.064087 | -0.07782 | 0.16022 | 62.9791 | -62.1048 | -0.2655 | -0.1236 | -0.11902 | -0.18768 | -0.26093 | -0.27008 | -0.045776 | 0.14648 | 61.7569 | 61.9949 | 124.5987 | 124.736 | -0.11902 | 124.8138 | 61.8988 | -0.27008 | 124.736 | -0.11902 | 61.8988 | 124.5987 | 124.8138 | -125.1251 | -125.1297
876.6406 | 125.1984 | -61.8073 | 63.0203 | -0.13252 | 0.0075559 | 0.012337 | -0.0012733 | 0.063121 | -0.0020721 | 0.072017 | -61.9263 | 62.9242 | -62.0819 | -61.9675 | 62.7731 | 0.13733 | -0.07782 | 0.24719 | 62.9837 | -62.0636 | -0.27466 | -0.096131 | -0.11902 | -0.16022 | -0.24719 | -0.25635 | -0.036621 | 0.15564 | 61.7294 | 62.0544 | 124.5804 | 124.7314 | -0.11902 | 124.791 | 61.9446 | -0.25635 | 124.7314 | -0.11902 | 61.9446 | 124.5804 | 124.791 | -125.1022 | -125.0839
877.6562 | 125.1022 | -61.8347 | 63.0524 | -0.1783 | 0.010547 | 0.013191 | 0.0079125 | 0.065685 | 0.00049134 | 0.068385 | -61.8942 | 63.0112 | -62.0865 | -61.9766 | 62.764 | 0.10071 | 0.050354 | 0.20599 | 63.0341 | -62.1231 | -0.25177 | -0.041199 | -0.059509 | -0.14191 | -0.28839 | -0.28839 | -0.01831 | 0.19226 | 61.8851 | 62.0407 | 124.5987 | 124.8459 | -0.059509 | 124.8688 | 61.9354 | -0.28839 | 124.8459 | -0.059509 | 61.9354 | 124.5987 | 124.8688 | -125.1389 | -125.1755
878.6406 | 125.1343 | -61.8576 | 63.0341 | 0.20317 | 0.0077695 | 0.013405 | -0.0017005 | 0.063976 | -0.0018585 | 0.069667 | -61.9812 | 62.8738 | -62.1048 | -62.0224 | 62.7365 | 0.050354 | -0.10529 | 0.12817 | 62.9379 | -62.0819 | -0.24719 | -0.16022 | -0.1236 | -0.16479 | -0.29755 | -0.2243 | -0.096131 | 0.1236 | 61.7523 | 61.9858 | 124.5941 | 124.7314 | -0.1236 | 124.7955 | 61.908 | -0.2243 | 124.7314 | -0.1236 | 61.908 | 124.5941 | 124.7955 | -125.1389 | -125.116
879.6406 | 125.1755 | -61.8439 | 63.002 | -0.18593 | 0.0075559 | 0.0074233 | 0.00022215 | 0.063549 | -0.00079046 | 0.068171 | -61.8622 | 62.915 | -62.0636 | -61.9217 | 62.8693 | 0.50354 | -0.16937 | -0.027466 | 62.9883 | -62.0361 | -0.21973 | -0.086975 | -0.018311 | -0.07782 | -0.13275 | -0.19226 | -0.013733 | 0.20142 | 61.6745 | 61.8164 | 124.7131 | 124.7589 | -0.018311 | 124.8322 | 62.3474 | -0.19226 | 124.7589 | -0.018311 | 62.3474 | 124.7131 | 124.8322 | -125.0656 | -125.0381
880.6406 | 125.2441 | -61.8256 | 63.0203 | -0.094376 | 0.0081967 | 0.010414 | 0.00064935 | 0.064617 | -0.0020721 | 0.068385 | -61.8668 | 62.9105 | -62.059 | -61.908 | 62.8281 | 0.082397 | 0.51727 | 0.39825 | 63.0432 | -62.0499 | -0.23346 | -0.10986 | -0.041198 | -0.082397 | -0.19226 | -0.2243 | 0.022888 | 0.19226 | 62.3428 | 62.2238 | 124.6536 | 124.736 | -0.041198 | 124.8688 | 61.908 | -0.2243 | 124.736 | -0.041198 | 61.908 | 124.6536 | 124.8688 | -125.0793 | -125.0702
881.6406 | 125.1709 | -61.8484 | 63.0203 | 0.0048064 | 0.0088375 | 0.014687 | -0.0012733 | 0.062908 | 6.414e-05 | 0.069026 | -61.9675 | 62.915 | -62.1002 | -62.0041 | 62.7548 | 0.068665 | -0.054932 | 0.17853 | 62.9562 | -62.0728 | -0.25177 | -0.10529 | -0.11902 | -0.15564 | -0.2655 | -0.2243 | -0.064087 | 0.13275 | 61.7935 | 62.027 | 124.6033 | 124.7635 | -0.11902 | 124.8047 | 61.9171 | -0.2243 | 124.7635 | -0.11902 | 61.9171 | 124.6033 | 124.8047 | -125.1205 | -125.0931
882.6406 | 125.0519 | -61.8439 | 63.0707 | -0.25459 | 0.0096921 | 0.0093459 | -0.0010597 | 0.062908 | -0.00057686 | 0.067744 | -61.9629 | 62.9929 | -62.1002 | -62.1323 | 62.764 | 0.050354 | 0.091553 | 0.19226 | 62.9791 | -62.114 | -0.25635 | -0.07782 | -0.11902 | -0.28839 | -0.3067 | -0.27008 | -0.091553 | 0.13733 | 61.9354 | 62.0361 | 124.6078 | 124.8367 | -0.11902 | 124.823 | 61.8942 | -0.27008 | 124.8367 | -0.11902 | 61.8942 | 124.6078 | 124.823 | -125.1709 | -125.1846
883.6406 | 125.0519 | -61.7523 | 63.0295 | -0.1783 | 0.0077695 | 0.0084915 | -0.00020505 | 0.064617 | -0.0010041 | 0.069667 | -61.8713 | 62.8922 | -62.0682 | -61.9217 | 62.8464 | 0.18768 | -0.10071 | 0.69122 | 63.002 | -62.0316 | -0.31586 | -0.13733 | -0.11902 | -0.16937 | -0.1831 | -0.27924 | -0.027466 | 0.19684 | 61.6516 | 62.4435 | 124.5987 | 124.6445 | -0.11902 | 124.7543 | 61.94 | -0.27924 | 124.6445 | -0.11902 | 61.94 | 124.5987 | 124.7543 | -125.0977 | -125.061
884.6406 | 125.116 | -61.8164 | 63.0295 | -0.26222 | 0.0077695 | 0.0095595 | 0.0012903 | 0.061626 | -0.0020721 | 0.06988 | -61.8759 | 62.9745 | -62.0911 | -61.9812 | 62.7777 | 0.12817 | 0.064087 | 0.23804 | 62.9745 | -62.0773 | -0.27466 | -0.054932 | -0.05951 | -0.16479 | -0.25177 | -0.26093 | -0.054932 | 0.21515 | 61.8805 | 62.0544 | 124.5941 | 124.791 | -0.05951 | 124.791 | 61.9446 | -0.26093 | 124.791 | -0.05951 | 61.9446 | 124.5941 | 124.791 | -125.1205 | -125.1068
885.6406 | 125.1434 | -61.8439 | 63.0386 | 0.012436 | 0.0096921 | 0.0087051 | -0.0012733 | 0.063335 | -0.0014313 | 0.067744 | -61.972 | 62.9105 | -62.0865 | -62.0132 | 62.7502 | 0.073242 | -0.064087 | 0.15106 | 62.9608 | -62.0819 | -0.24262 | -0.12817 | -0.12817 | -0.16937 | -0.28839 | -0.23804 | -0.07782 | 0.11444 | 61.7798 | 61.9949 | 124.5941 | 124.7543 | -0.12817 | 124.8047 | 61.9171 | -0.23804 | 124.7543 | -0.12817 | 61.9171 | 124.5941 | 124.8047 | -125.1251 | -125.1205
886.6406 | 125.1801 | -61.7844 | 63.0295 | -0.04097 | 0.010547 | 0.0099869 | -0.0010597 | 0.063121 | -0.00079046 | 0.068599 | -61.9217 | 62.9105 | -62.0682 | -61.972 | 62.764 | 0.1236 | -0.073242 | 0.22888 | 62.9379 | -62.0773 | -0.28381 | -0.11902 | -0.13733 | -0.18768 | -0.2655 | -0.29297 | -0.091553 | 0.14648 | 61.7111 | 62.0132 | 124.5483 | 124.6948 | -0.13733 | 124.7223 | 61.908 | -0.29297 | 124.6948 | -0.13733 | 61.908 | 124.5483 | 124.7223 | -125.0977 | -125.1068
887.6406 | 125.386 | -61.7798 | 63.0478 | -0.10201 | 0.0088375 | 0.0076369 | -0.00063225 | 0.060985 | 0.0011321 | 0.06988 | -61.8851 | 62.8967 | -62.0865 | -61.9171 | 62.8281 | 0.19684 | -0.091553 | 0.31128 | 62.9517 | -62.059 | -0.3067 | -0.15106 | -0.10529 | -0.13733 | -0.21973 | -0.27924 | -0.096131 | 0.20142 | 61.6882 | 62.0911 | 124.6078 | 124.6765 | -0.10529 | 124.7314 | 61.9766 | -0.27924 | 124.6765 | -0.10529 | 61.9766 | 124.6078 | 124.7314 | -125.1343 | -125.1068
888.6406 | 125.1938 | -61.7935 | 63.0478 | -0.29274 | 0.010547 | 0.0067825 | -0.0010597 | 0.06184 | 0.00070494 | 0.069239 | -61.8805 | 62.9242 | -62.0682 | -61.94 | 62.8143 | 0.17395 | -0.036621 | 0.29755 | 62.9562 | -62.059 | -0.27466 | -0.1236 | -0.086975 | -0.14648 | -0.23346 | -0.2655 | -0.091553 | 0.18768 | 61.7569 | 62.0911 | 124.6078 | 124.7177 | -0.086975 | 124.7498 | 61.9675 | -0.2655 | 124.7177 | -0.086975 | 61.9675 | 124.6078 | 124.7498 | -125.116 | -125.1068
889.6406 | 125.0839 | -61.8484 | 63.0798 | -0.26222 | 0.011615 | 0.012123 | 0.0027855 | 0.063976 | 0.00070494 | 0.068385 | -61.9629 | 63.0112 | -62.0865 | -61.8164 | 62.8006 | 0.041199 | 0.013733 | 0.18768 | 63.002 | -62.1277 | -0.23804 | -0.068665 | -0.11444 | 0.032044 | -0.27924 | -0.27924 | -0.07782 | 0.1236 | 61.8622 | 62.0361 | 124.649 | 124.8596 | -0.11444 | 124.8505 | 61.8896 | -0.27924 | 124.8596 | -0.11444 | 61.8896 | 124.649 | 124.8505 | -125.1663 | -125.2075
890.6406 | 125.1434 | -61.8118 | 63.1256 | -0.16304 | 0.0088375 | 0.0067825 | -0.0014869 | 0.062908 | -0.0020721 | 0.067744 | -61.8851 | 62.9288 | -62.0728 | -61.9308 | 62.8235 | 0.16937 | -0.082397 | 0.28839 | 62.9837 | -62.0316 | -0.26093 | -0.19684 | -0.073242 | -0.11902 | -0.30212 | -0.21973 | -0.14191 | 0.18768 | 61.7294 | 62.1002 | 124.6353 | 124.7406 | -0.073242 | 124.7955 | 61.9812 | -0.21973 | 124.7406 | -0.073242 | 61.9812 | 124.6353 | 124.7955 | -125.1984 | -125.1572
891.6406 | 125.1938 | -61.7935 | 63.0249 | -0.21645 | 0.0052059 | 0.0099869 | 0.0015039 | 0.062481 | -0.0020721 | 0.06689 | -61.8988 | 62.9242 | -62.0682 | -61.9354 | 62.8052 | 0.17395 | -0.082397 | 0.29297 | 62.9517 | -62.0407 | -0.27466 | -0.10071 | -0.10529 | -0.14191 | -0.21973 | -0.24719 | -0.073242 | 0.16937 | 61.7111 | 62.0865 | 124.5987 | 124.7177 | -0.10529 | 124.7452 | 61.9675 | -0.24719 | 124.7177 | -0.10529 | 61.9675 | 124.5987 | 124.7452 | -125.0931 | -125.0656
892.6406 | 125.0977 | -61.8484 | 63.0524 | -0.23933 | 0.0094785 | 0.010841 | 0.0044945 | 0.063335 | 0.0019867 | 0.069239 | -61.9492 | 63.0432 | -62.0728 | -62.0224 | 62.709 | 0.068665 | 0.13275 | 0.16022 | 63.0112 | -62.1185 | -0.2243 | -0.009155 | -0.10071 | -0.17395 | -0.34332 | -0.27008 | -0.041199 | 0.1236 | 61.9812 | 62.0087 | 124.5575 | 124.8917 | -0.10071 | 124.8596 | 61.9171 | -0.27008 | 124.8917 | -0.10071 | 61.9171 | 124.5575 | 124.8596 | -125.1251 | -125.1709
893.6406 | 125.1892 | -61.821 | 63.0524 | -0.23933 | 0.0092649 | 0.011269 | -0.00041865 | 0.063549 | -0.00079046 | 0.067317 | -61.8668 | 62.9196 | -62.0728 | -61.9308 | 62.8281 | 0.16937 | -0.050354 | 0.29755 | 62.9654 | -62.0499 | -0.25177 | -0.13275 | -0.045776 | -0.10986 | -0.2243 | -0.22888 | -0.086975 | 0.20599 | 61.7706 | 62.1185 | 124.649 | 124.7406 | -0.045776 | 124.7864 | 61.9904 | -0.22888 | 124.7406 | -0.045776 | 61.9904 | 124.649 | 124.7864 | -125.1251 | -125.1022
894.6406 | 125.0931 | -61.853 | 63.0615 | -0.26985 | 0.010547 | 0.010201 | 0.0062035 | 0.063121 | -0.0014313 | 0.066676 | -61.9492 | 62.9837 | -62.114 | -62.0316 | 62.7136 | 0.091553 | 0.1236 | 0.16022 | 63.0157 | -62.1048 | -0.26093 | -0.077819 | -0.096131 | -0.17853 | -0.3479 | -0.25177 | -0.045776 | 0.1648 | 61.9766 | 62.0132 | 124.5666 | 124.8367 | -0.096131 | 124.8688 | 61.9446 | -0.25177 | 124.8367 | -0.096131 | 61.9446 | 124.5666 | 124.8688 | -125.1755 | -125.1663
895.6406 | 125.1755 | -61.8073 | 63.0341 | -0.26222 | 0.0056333 | 0.0078507 | -0.0017005 | 0.064617 | -0.00079046 | 0.06689 | -61.8805 | 62.9242 | -62.0636 | -61.9354 | 62.8235 | 0.16937 | -0.036621 | 0.28381 | 62.9883 | -62.0407 | -0.25635 | -0.10986 | -0.073242 | -0.12817 | -0.21057 | -0.23346 | -0.045777 | 0.18311 | 61.7706 | 62.0911 | 124.6307 | 124.7314 | -0.073242 | 124.7955 | 61.9766 | -0.23346 | 124.7314 | -0.073242 | 61.9766 | 124.6307 | 124.7955 | -125.0977 | -125.0748
896.6406 | 125.1389 | -61.8073 | 63.0753 | -0.26222 | 0.0064877 | 0.013405 | 0.0019311 | 0.063549 | -0.0014313 | 0.068812 | -61.9034 | 62.9745 | -62.0499 | -61.9904 | 62.764 | 0.13733 | 0.064087 | 0.25177 | 63.002 | -62.0773 | -0.24262 | -0.10071 | -0.09613 | -0.1831 | -0.31128 | -0.27008 | -0.073242 | 0.14648 | 61.8713 | 62.059 | 124.5712 | 124.7818 | -0.09613 | 124.8093 | 61.9446 | -0.27008 | 124.7818 | -0.09613 | 61.9446 | 124.5712 | 124.8093 | -125.1251 | -125.1526
897.6562 | 125.0839 | -61.8622 | 63.0524 | -0.033341 | 0.012683 | 0.011269 | 0.0070581 | 0.065044 | -0.00079046 | 0.067317 | -61.9034 | 63.0203 | -62.0682 | -62.0178 | 62.6999 | 0.059509 | 0 | 0.11444 | 62.9974 | -62.1368 | -0.20599 | -0.032043 | -0.041198 | -0.15564 | -0.35248 | -0.27466 | -0.054931 | 0.16479 | 61.8622 | 61.9766 | 124.5621 | 124.8825 | -0.041198 | 124.8596 | 61.9217 | -0.27466 | 124.8825 | -0.041198 | 61.9217 | 124.5621 | 124.8596 | -125.1205 | -125.1892
898.6406 | 125.148 | -61.821 | 63.0615 | -0.23933 | 0.0081967 | 0.0091323 | 0.00022215 | 0.065685 | -0.0018585 | 0.068385 | -61.8896 | 62.9425 | -62.0773 | -61.9446 | 62.8052 | 0.16937 | -0.027466 | 0.28839 | 62.9745 | -62.0453 | -0.25635 | -0.11902 | -0.068664 | -0.1236 | -0.25635 | -0.2243 | -0.086975 | 0.18768 | 61.7935 | 62.1094 | 124.6262 | 124.7635 | -0.068664 | 124.7955 | 61.9904 | -0.2243 | 124.7635 | -0.068664 | 61.9904 | 124.6262 | 124.7955 | -125.1389 | -125.1068
899.6406 | 125.1068 | -61.8393 | 63.0707 | -0.19356 | 0.0099057 | 0.0089187 | 0.0012903 | 0.065044 | -0.0044221 | 0.070094 | -61.9446 | 63.0249 | -62.1048 | -62.0316 | 62.7228 | 0.068665 | 0.10986 | 0.16479 | 63.0295 | -62.0911 | -0.2655 | -0.045777 | -0.10529 | -0.19226 | -0.3479 | -0.25177 | -0.041199 | 0.16022 | 61.9492 | 62.0041 | 124.5621 | 124.8642 | -0.10529 | 124.8688 | 61.908 | -0.25177 | 124.8642 | -0.10529 | 61.908 | 124.5621 | 124.8688 | -125.1755 | -125.1617
900.6406 | 125.0427 | -61.853 | 63.0707 | 0.073471 | 0.010119 | 0.011055 | 0.0023583 | 0.064403 | -0.0020721 | 0.068599 | -61.9675 | 62.9929 | -62.0911 | -62.0499 | 62.7045 | 0.086975 | 0.14191 | 0.17395 | 63.0478 | -62.1002 | -0.23804 | -0.07782 | -0.11444 | -0.19684 | -0.36621 | -0.24719 | -0.022888 | 0.1236 | 61.9949 | 62.027 | 124.5575 | 124.8459 | -0.11444 | 124.9008 | 61.94 | -0.24719 | 124.8459 | -0.11444 | 61.94 | 124.5575 | 124.9008 | -125.1617 | -125.1709
901.6406 | 125.1892 | -61.821 | 63.0615 | -0.19356 | 0.010333 | 0.010841 | 0.00064935 | 0.064403 | -0.0010041 | 0.067317 | -61.8759 | 62.9425 | -62.0499 | -61.972 | 62.7914 | 0.16479 | 0.018311 | 0.25635 | 62.9929 | -62.0453 | -0.22888 | -0.11902 | -0.054932 | -0.15106 | -0.27008 | -0.2243 | -0.068664 | 0.17395 | 61.8393 | 62.0773 | 124.6124 | 124.7635 | -0.054932 | 124.8138 | 61.9858 | -0.2243 | 124.7635 | -0.054932 | 61.9858 | 124.6124 | 124.8138 | -125.1114 | -125.1068
902.6406 | 125.1114 | -61.853 | 63.0753 | -0.071488 | 0.011188 | 0.016182 | 0.0062035 | 0.065258 | 0.00091854 | 0.069667 | -61.8805 | 63.0066 | -62.0956 | -61.9949 | 62.4893 | -0.10986 | 0.26093 | 0.17395 | 63.0066 | -62.1277 | -0.24262 | -0.068664 | -0.027466 | -0.14191 | -0.58594 | -0.27466 | -0.068664 | 0.21515 | 62.114 | 62.027 | 124.3423 | 124.8596 | -0.027466 | 124.8596 | 61.7432 | -0.27466 | 124.8596 | -0.027466 | 61.7432 | 124.3423 | 124.8596 | -125.1709 | -125.2029
903.6406 | 125.0793 | -61.853 | 63.0661 | -0.25459 | 0.0099057 | 0.014473 | 0.0036401 | 0.062694 | -0.0035675 | 0.06988 | -61.9446 | 63.0112 | -62.0956 | -62.059 | 62.7274 | 0.073242 | 0.12817 | 0.16479 | 63.0295 | -62.0819 | -0.24262 | -0.054932 | -0.091553 | -0.20599 | -0.33875 | -0.22888 | -0.036621 | 0.15106 | 61.9812 | 62.0178 | 124.5804 | 124.8642 | -0.091553 | 124.8825 | 61.9263 | -0.22888 | 124.8642 | -0.091553 | 61.9263 | 124.5804 | 124.8825 | -125.1617 | -125.148
904.6406 | 125.0519 | -61.8439 | 63.0478 | -0.071488 | 0.011188 | 0.013619 | 0.0055627 | 0.068889 | 0.00091854 | 0.069453 | -61.8896 | 63.0341 | -62.0911 | -62.0224 | 62.7274 | 0.059509 | 0.027466 | 0.11902 | 63.002 | -62.1231 | -0.24719 | -0.013733 | -0.045776 | -0.17853 | -0.32043 | -0.27924 | -0.045777 | 0.20142 | 61.8713 | 61.9629 | 124.5712 | 124.8779 | -0.045776 | 124.8459 | 61.9034 | -0.27924 | 124.8779 | -0.045776 | 61.9034 | 124.5712 | 124.8459 | -125.1389 | -125.1709
905.6406 | 125.0793 | -61.8759 | 63.0478 | -0.26222 | 0.012897 | 0.013619 | 0.0032129 | 0.066967 | -0.0016449 | 0.071162 | -61.94 | 63.0569 | -62.0865 | -62.0544 | 62.7182 | 0.082397 | 0.13733 | 0.16022 | 63.0478 | -62.114 | -0.21057 | 0.009155 | -0.064086 | -0.17853 | -0.32959 | -0.23804 | 0 | 0.14648 | 62.0132 | 62.0361 | 124.5941 | 124.9329 | -0.064086 | 124.9237 | 61.9583 | -0.23804 | 124.9329 | -0.064086 | 61.9583 | 124.5941 | 124.9237 | -125.1343 | -125.1617
906.6406 | 125.0839 | -61.8668 | 63.0753 | -0.2317 | 0.011188 | 0.0089187 | 0.0015039 | 0.065685 | -0.0042085 | 0.067958 | -61.9492 | 63.002 | -62.0819 | -61.8668 | 62.6129 | -0.041199 | 0.11902 | 0.16479 | 63.0249 | -62.1185 | -0.21515 | -0.073242 | -0.082398 | 0 | -0.46234 | -0.25177 | -0.050354 | 0.13275 | 61.9858 | 62.0316 | 124.4797 | 124.8688 | -0.082398 | 124.8917 | 61.8256 | -0.25177 | 124.8688 | -0.082398 | 61.8256 | 124.4797 | 124.8917 | -125.1572 | -125.1938
907.6562 | 125.0381 | -61.8622 | 63.0798 | 0.035324 | 0.012683 | 0.011696 | 0.0047081 | 0.066753 | 0.00049134 | 0.067744 | -61.9583 | 63.0386 | -62.1048 | -62.0956 | 62.6587 | -0.004578 | 0.027466 | 0.059509 | 63.0157 | -62.1323 | -0.24261 | -0.041199 | -0.09613 | -0.23346 | -0.42114 | -0.27008 | -0.064087 | 0.14648 | 61.8896 | 61.9217 | 124.5209 | 124.9008 | -0.09613 | 124.8779 | 61.8576 | -0.27008 | 124.9008 | -0.09613 | 61.8576 | 124.5209 | 124.8779 | -125.1846 | -125.2121
908.6406 | 125.1297 | -61.8484 | 63.0478 | -0.26222 | 0.013537 | 0.012337 | 0.0029993 | 0.066753 | -0.0033539 | 0.067531 | -61.9125 | 63.0386 | -62.0773 | -62.0132 | 62.7411 | 0.10986 | 0.068665 | 0.1831 | 63.0341 | -62.1002 | -0.22888 | -0.009156 | -0.064087 | -0.16479 | -0.3067 | -0.25177 | -0.013733 | 0.16479 | 61.9171 | 62.0316 | 124.5895 | 124.8871 | -0.064087 | 124.8825 | 61.9583 | -0.25177 | 124.8871 | -0.064087 | 61.9583 | 124.5895 | 124.8825 | -125.1251 | -125.148
909.6406 | 125.1114 | -61.8301 | 63.0341 | -0.071488 | 0.0099057 | 0.011482 | 0.0038537 | 0.066967 | -0.0024995 | 0.068599 | -61.9858 | 62.9883 | -62.114 | -62.0132 | 62.7457 | 0.11444 | 0.036621 | 0.16937 | 63.0203 | -62.0911 | -0.28381 | -0.045777 | -0.15564 | -0.18311 | -0.28839 | -0.26093 | -0.013733 | 0.12817 | 61.8668 | 61.9995 | 124.5758 | 124.8184 | -0.15564 | 124.8505 | 61.9446 | -0.26093 | 124.8184 | -0.15564 | 61.9446 | 124.5758 | 124.8505 | -125.148 | -125.1251
910.6406 | 125.0702 | -61.8347 | 63.0707 | -0.25459 | 0.010547 | 0.0087051 | 0.00043575 | 0.068248 | -0.00014946 | 0.068599 | -61.9354 | 63.0203 | -62.0773 | -62.0636 | 62.709 | 0.082397 | 0.12817 | 0.16937 | 63.0569 | -62.1277 | -0.24262 | -0.050354 | -0.10071 | -0.22888 | -0.36163 | -0.29297 | -0.013733 | 0.14191 | 61.9629 | 62.0041 | 124.5438 | 124.855 | -0.10071 | 124.8917 | 61.9171 | -0.29297 | 124.855 | -0.10071 | 61.9171 | 124.5438 | 124.8917 | -125.148 | -125.1984
911.6406 | 125.0885 | -61.8347 | 63.0569 | -0.2317 | 0.0094785 | 0.0091323 | -0.00041865 | 0.065258 | -0.0018585 | 0.067958 | -61.9492 | 63.0203 | -62.0819 | -62.059 | 62.7136 | 0.07782 | 0.14191 | 0.16937 | 63.0432 | -62.1185 | -0.24719 | -0.036621 | -0.11444 | -0.2243 | -0.34332 | -0.28381 | -0.013733 | 0.13275 | 61.9766 | 62.0041 | 124.5483 | 124.855 | -0.11444 | 124.8779 | 61.9125 | -0.28381 | 124.855 | -0.11444 | 61.9125 | 124.5483 | 124.8779 | -125.1389 | -125.1755
912.6562 | 125.061 | -61.8668 | 62.9974 | 0.18028 | 0.010333 | 0.012123 | 0.0032129 | 0.066112 | -0.00014946 | 0.069453 | -61.94 | 63.0112 | -62.0956 | -62.0911 | 62.6816 | -0.004578 | -0.050354 | 0.054932 | 62.9974 | -62.1368 | -0.22888 | 0.013732 | -0.073242 | -0.2243 | -0.31586 | -0.27008 | 0 | 0.15564 | 61.8164 | 61.9217 | 124.5483 | 124.8779 | -0.073242 | 124.8642 | 61.8622 | -0.27008 | 124.8779 | -0.073242 | 61.8622 | 124.5483 | 124.8642 | -125.0931 | -125.1343
913.6562 | 125.0793 | -61.8393 | 63.0157 | 0.11162 | 0.012469 | 0.012978 | 0.0032129 | 0.067394 | -0.00014946 | 0.068599 | -61.972 | 63.0203 | -62.114 | -62.0865 | 62.6724 | -0.004578 | -0.041199 | 0.041199 | 63.0112 | -62.1323 | -0.27466 | 0.004578 | -0.13275 | -0.24719 | -0.34332 | -0.29297 | -0.004578 | 0.14191 | 61.7981 | 61.8805 | 124.5117 | 124.8596 | -0.13275 | 124.8505 | 61.8347 | -0.29297 | 124.8596 | -0.13275 | 61.8347 | 124.5117 | 124.8505 | -125.1297 | -125.148
914.6406 | 125.0885 | -61.853 | 63.0386 | -0.22408 | 0.011615 | 0.0084915 | 0.0062035 | 0.069316 | -0.00079046 | 0.069453 | -61.8988 | 63.002 | -62.0728 | -62.0041 | 62.7457 | 0.10529 | 0.041199 | 0.19226 | 63.0203 | -62.114 | -0.21973 | -0.036621 | -0.045777 | -0.15106 | -0.29297 | -0.26093 | -0.01831 | 0.17395 | 61.8942 | 62.0453 | 124.5987 | 124.855 | -0.045777 | 124.8734 | 61.9583 | -0.26093 | 124.855 | -0.045777 | 61.9583 | 124.5987 | 124.8734 | -125.1114 | -125.1526
915.6406 | 125.0519 | -61.8393 | 63.0707 | -0.36903 | 0.010974 | 0.0084915 | -0.00084605 | 0.066753 | -0.0024995 | 0.069667 | -61.9858 | 62.9883 | -62.1002 | -62.0407 | 62.709 | 0.07782 | 0.13733 | 0.14191 | 63.0524 | -62.1094 | -0.26093 | -0.082398 | -0.14648 | -0.20142 | -0.36163 | -0.27008 | -0.018311 | 0.11444 | 61.9766 | 61.9812 | 124.5483 | 124.8276 | -0.14648 | 124.8917 | 61.9171 | -0.27008 | 124.8276 | -0.14648 | 61.9171 | 124.5483 | 124.8917 | -125.1709 | -125.1801
916.6406 | 125.1022 | -61.8393 | 63.0707 | -0.2317 | 0.0092649 | 0.010201 | 0.00022215 | 0.065044 | -0.00079046 | 0.069453 | -61.9308 | 63.0203 | -62.0911 | -62.059 | 62.6999 | 0.091553 | 0.10986 | 0.17395 | 63.0341 | -62.1002 | -0.25177 | -0.050354 | -0.091553 | -0.21973 | -0.37079 | -0.26093 | -0.036621 | 0.16022 | 61.9492 | 62.0132 | 124.5392 | 124.8596 | -0.091553 | 124.8734 | 61.9308 | -0.26093 | 124.8596 | -0.091553 | 61.9308 | 124.5392 | 124.8734 | -125.1617 | -125.1709
917.6562 | 125.1297 | -61.8484 | 63.0112 | 0.14976 | 0.010974 | 0.013405 | 0.0027855 | 0.067821 | 0.0015595 | 0.069667 | -61.9308 | 63.002 | -62.1002 | -62.0636 | 62.6907 | 0.013733 | -0.10071 | 0.082397 | 63.0112 | -62.1414 | -0.25177 | -0.009155 | -0.082397 | -0.21515 | -0.32043 | -0.29297 | 0 | 0.16937 | 61.7477 | 61.9308 | 124.5392 | 124.8505 | -0.082397 | 124.8596 | 61.8622 | -0.29297 | 124.8505 | -0.082397 | 61.8622 | 124.5392 | 124.8596 | -125.1114 | -125.1526
918.6562 | 125.1297 | -61.8256 | 63.0341 | -0.025711 | 0.0086239 | 0.0078507 | -0.0057593 | 0.064617 | -0.0022859 | 0.067744 | -61.9446 | 62.9013 | -62.1094 | -62.0453 | 62.7502 | 0.09613 | -0.064087 | 0.18768 | 62.9974 | -62.0819 | -0.28381 | -0.13275 | -0.11902 | -0.21973 | -0.28381 | -0.25635 | -0.036621 | 0.16479 | 61.7615 | 62.0132 | 124.5758 | 124.7269 | -0.11902 | 124.823 | 61.9217 | -0.25635 | 124.7269 | -0.11902 | 61.9217 | 124.5758 | 124.823 | -125.1434 | -125.116
919.6406 | 125.061 | -61.8622 | 63.0432 | -0.048599 | 0.0090513 | 0.016396 | 0.0038537 | 0.065685 | -0.0018585 | 0.067531 | -61.9171 | 63.0203 | -62.1048 | -62.0316 | 62.6999 | 0.050354 | 0.027466 | 0.1236 | 63.002 | -62.1231 | -0.24261 | -0.022888 | -0.054931 | -0.16937 | -0.34332 | -0.26093 | -0.041199 | 0.18768 | 61.8896 | 61.9858 | 124.5621 | 124.8825 | -0.054931 | 124.8642 | 61.9125 | -0.26093 | 124.8825 | -0.054931 | 61.9125 | 124.5621 | 124.8642 | -125.148 | -125.1663
920.6406 | 125.0931 | -61.853 | 63.0203 | -0.26222 | 0.010119 | 0.012764 | 0.0019311 | 0.065471 | -0.0018585 | 0.068171 | -61.9492 | 63.0615 | -62.0956 | -62.0453 | 62.7045 | 0.07782 | 0.1236 | 0.16022 | 63.0615 | -62.1094 | -0.24262 | 0.041198 | -0.096131 | -0.19226 | -0.31586 | -0.25635 | 0.041198 | 0.14648 | 61.9766 | 62.0132 | 124.5575 | 124.9145 | -0.096131 | 124.9145 | 61.9308 | -0.25635 | 124.9145 | -0.096131 | 61.9308 | 124.5575 | 124.9145 | -125.116 | -125.1297
921.6406 | 125.1114 | -61.8393 | 63.0478 | -0.14778 | 0.0094785 | 0.019386 | 0.0036401 | 0.06419 | -0.0042085 | 0.067958 | -61.8942 | 63.0203 | -62.0819 | -62.0041 | 62.7365 | 0.09613 | 0.032043 | 0.19684 | 63.0249 | -62.1231 | -0.24262 | -0.027466 | -0.054932 | -0.16479 | -0.31128 | -0.28381 | -0.022889 | 0.18768 | 61.8713 | 62.0361 | 124.5758 | 124.8596 | -0.054932 | 124.8642 | 61.9354 | -0.28381 | 124.8596 | -0.054932 | 61.9354 | 124.5758 | 124.8642 | -125.1297 | -125.1709
922.6406 | 125.0656 | -61.8805 | 63.0295 | 0.058212 | 0.010547 | 0.014046 | 0.0042809 | 0.068462 | -0.00079046 | 0.068812 | -61.9263 | 63.0112 | -62.1002 | -62.0819 | 62.6633 | -0.004578 | 0.027466 | 0.059509 | 63.0203 | -62.1506 | -0.21973 | -0.018311 | -0.045777 | -0.20142 | -0.36621 | -0.27008 | -0.009155 | 0.17395 | 61.908 | 61.94 | 124.5438 | 124.8917 | -0.045777 | 124.9008 | 61.8759 | -0.27008 | 124.8917 | -0.045777 | 61.8759 | 124.5438 | 124.9008 | -125.1297 | -125.1801
923.6562 | 125.1846 | -61.8256 | 62.9791 | 0.096359 | 0.0088375 | 0.0095595 | -0.0027687 | 0.068035 | -0.0020721 | 0.067531 | -61.8759 | 62.9379 | -62.0911 | -62.0041 | 62.7777 | 0.073242 | -0.18768 | 0.15564 | 62.9837 | -62.0819 | -0.2655 | -0.041199 | -0.050354 | -0.17853 | -0.20142 | -0.25635 | 0.004578 | 0.21515 | 61.6379 | 61.9812 | 124.6033 | 124.7635 | -0.050354 | 124.8093 | 61.8988 | -0.25635 | 124.7635 | -0.050354 | 61.8988 | 124.6033 | 124.8093 | -125.0702 | -125.061
924.6406 | 125.148 | -61.8027 | 63.0936 | -0.28511 | 0.0092649 | 0.013405 | -0.0012733 | 0.064617 | -0.00057686 | 0.069667 | -61.9354 | 63.0203 | -62.0728 | -62.0682 | 62.7182 | 0.086975 | 0.13275 | 0.17395 | 63.0569 | -62.1185 | -0.27008 | -0.073242 | -0.13275 | -0.2655 | -0.37537 | -0.31586 | -0.036621 | 0.13733 | 61.9354 | 61.9766 | 124.5209 | 124.823 | -0.13275 | 124.8596 | 61.8896 | -0.31586 | 124.823 | -0.13275 | 61.8896 | 124.5209 | 124.8596 | -125.1663 | -125.2121
925.6406 | 125.0793 | -61.8484 | 63.0203 | -0.048599 | 0.01311 | 0.017464 | 0.0040673 | 0.068889 | -0.0037811 | 0.068171 | -61.8896 | 63.0066 | -62.0636 | -62.0224 | 62.709 | 0.073242 | 0.018311 | 0.15106 | 63.0203 | -62.1368 | -0.21515 | -0.013733 | -0.041198 | -0.17395 | -0.31128 | -0.28839 | 0 | 0.17395 | 61.8668 | 61.9995 | 124.5575 | 124.855 | -0.041198 | 124.8688 | 61.9217 | -0.28839 | 124.855 | -0.041198 | 61.9217 | 124.5575 | 124.8688 | -125.0839 | -125.1572
926.6406 | 125.0748 | -61.8576 | 63.0661 | -0.24696 | 0.010119 | 0.015114 | 0.0023583 | 0.066112 | -0.00014946 | 0.06988 | -61.94 | 63.0341 | -62.0773 | -62.0407 | 62.7182 | 0.082397 | 0.13275 | 0.17395 | 63.089 | -62.1277 | -0.21973 | -0.032043 | -0.082397 | -0.1831 | -0.3479 | -0.27008 | 0.022888 | 0.13733 | 61.9904 | 62.0316 | 124.5758 | 124.8917 | -0.082397 | 124.9466 | 61.94 | -0.27008 | 124.8917 | -0.082397 | 61.94 | 124.5758 | 124.9466 | -125.1434 | -125.1938
927.6406 | 125.0381 | -61.853 | 63.0295 | 0.012436 | 0.010974 | 0.014473 | 0.0025719 | 0.068248 | -0.0018585 | 0.068385 | -61.9171 | 63.0295 | -62.0865 | -62.0773 | 62.6587 | 0.018311 | 0.036621 | 0.073242 | 63.0432 | -62.1231 | -0.23346 | 0 | -0.064087 | -0.22431 | -0.37079 | -0.27008 | 0.013733 | 0.16937 | 61.8896 | 61.9263 | 124.5117 | 124.8825 | -0.064087 | 124.8962 | 61.8713 | -0.27008 | 124.8825 | -0.064087 | 61.8713 | 124.5117 | 124.8962 | -125.116 | -125.1526
928.6562 | 125.1617 | -61.8622 | 62.97 | 0.14214 | 0.011401 | 0.01191 | -0.0025549 | 0.06718 | 0.00070494 | 0.067317 | -61.8851 | 62.915 | -62.0911 | -62.0041 | 62.7548 | 0.059509 | -0.16479 | 0.15564 | 62.9791 | -62.1094 | -0.22888 | -0.054932 | -0.022888 | -0.14191 | -0.21515 | -0.24719 | 0.009155 | 0.20599 | 61.6974 | 62.0178 | 124.617 | 124.7772 | -0.022888 | 124.8413 | 61.9217 | -0.24719 | 124.7772 | -0.022888 | 61.9217 | 124.617 | 124.8413 | -125.061 | -125.0793
929.6406 | 125.0931 | -61.8576 | 63.0478 | -0.048599 | 0.010974 | 0.0067825 | 0.0055627 | 0.066326 | -0.0014313 | 0.070308 | -61.8851 | 63.0112 | -62.1002 | -62.0132 | 62.709 | 0.068665 | 0.013733 | 0.14191 | 63.0203 | -62.1414 | -0.24262 | -0.036622 | -0.027466 | -0.15564 | -0.33875 | -0.28381 | -0.027466 | 0.21515 | 61.8713 | 61.9995 | 124.5667 | 124.8688 | -0.027466 | 124.8779 | 61.9263 | -0.28381 | 124.8688 | -0.027466 | 61.9263 | 124.5667 | 124.8779 | -125.148 | -125.1892
930.6406 | 125.0931 | -61.8622 | 63.0707 | -0.24696 | 0.0086239 | 0.01191 | 0.0032129 | 0.065471 | -0.0012177 | 0.067744 | -61.9308 | 63.0341 | -62.0865 | -62.0316 | 62.7274 | 0.091553 | 0.07782 | 0.1831 | 63.0661 | -62.1185 | -0.2243 | -0.036621 | -0.068664 | -0.16937 | -0.34332 | -0.25635 | -0.004578 | 0.15564 | 61.94 | 62.0453 | 124.5895 | 124.8962 | -0.068664 | 124.9283 | 61.9537 | -0.25635 | 124.8962 | -0.068664 | 61.9537 | 124.5895 | 124.9283 | -125.1572 | -125.1892
931.6406 | 125.1022 | -61.8347 | 63.0386 | -0.086746 | 0.011401 | 0.013191 | 0.0038537 | 0.067821 | 6.414e-05 | 0.068599 | -61.8668 | 63.0341 | -62.0773 | -61.9949 | 62.7457 | 0.1831 | -0.2655 | 0.10529 | 63.002 | -62.146 | -0.24262 | -0.004577 | -0.032043 | -0.16022 | -0.29297 | -0.31128 | -0.036621 | 0.21057 | 61.5692 | 61.94 | 124.5804 | 124.8688 | -0.032043 | 124.8367 | 62.0178 | -0.31128 | 124.8688 | -0.032043 | 62.0178 | 124.5804 | 124.8367 | -125.116 | -125.1846
932.6406 | 125.0748 | -61.8393 | 63.0386 | -0.063858 | 0.012042 | 0.011482 | 0.0059899 | 0.068248 | -0.0016449 | 0.070094 | -61.8896 | 63.0157 | -62.0728 | -62.0087 | 62.7182 | 0.082397 | 0.013733 | 0.14648 | 63.0341 | -62.114 | -0.23346 | -0.022888 | -0.050354 | -0.16937 | -0.32043 | -0.27466 | -0.004577 | 0.18311 | 61.853 | 61.9858 | 124.5575 | 124.855 | -0.050354 | 124.8734 | 61.9217 | -0.27466 | 124.855 | -0.050354 | 61.9217 | 124.5575 | 124.8734 | -125.1114 | -125.1526
933.6406 | 125.1846 | -61.8027 | 63.0157 | -0.26985 | 0.0096921 | 0.0093459 | -0.0034095 | 0.066967 | -0.0010041 | 0.069453 | -61.8256 | 62.9791 | -62.059 | -61.9537 | 62.8189 | 0.16937 | -0.036621 | 0.3067 | 63.0066 | -62.0911 | -0.25635 | -0.036621 | -0.022889 | -0.15106 | -0.19684 | -0.28839 | -0.009155 | 0.23346 | 61.7661 | 62.1094 | 124.6216 | 124.7818 | -0.022889 | 124.8093 | 61.972 | -0.28839 | 124.7818 | -0.022889 | 61.972 | 124.6216 | 124.8093 | -125.0748 | -125.1068
934.6406 | 125.0519 | -61.8576 | 63.0661 | -0.033341 | 0.014178 | 0.015114 | 0.0051355 | 0.066753 | -0.0014313 | 0.069667 | -61.8851 | 63.0203 | -62.0819 | -62.0041 | 62.7136 | 0.068665 | 0.009155 | 0.16479 | 62.9929 | -62.1368 | -0.2243 | -0.045776 | -0.027466 | -0.14648 | -0.35248 | -0.27924 | -0.073242 | 0.19684 | 61.8668 | 62.0224 | 124.5712 | 124.8779 | -0.027466 | 124.8505 | 61.9263 | -0.27924 | 124.8779 | -0.027466 | 61.9263 | 124.5712 | 124.8505 | -125.148 | -125.2029
935.6406 | 125.0839 | -61.8301 | 63.0249 | -0.1783 | 0.011828 | 0.012764 | 0.0044945 | 0.066326 | -0.0037811 | 0.068171 | -61.8851 | 63.0386 | -62.0819 | -62.0087 | 62.7365 | 0.10529 | 0.041199 | 0.17853 | 63.0386 | -62.1185 | -0.25177 | 0.013733 | -0.054932 | -0.17853 | -0.28839 | -0.28839 | 0.013733 | 0.19684 | 61.8713 | 62.0087 | 124.5667 | 124.8688 | -0.054932 | 124.8688 | 61.9354 | -0.28839 | 124.8688 | -0.054932 | 61.9354 | 124.5667 | 124.8688 | -125.1068 | -125.1434
936.6406 | 125.1068 | -61.8576 | 63.0341 | -0.033341 | 0.01076 | 0.012764 | 0.0025719 | 0.069316 | -0.0014313 | 0.068812 | -61.8668 | 63.0066 | -62.0865 | -62.0224 | 62.7228 | 0.09613 | 0.004578 | 0.16937 | 63.0615 | -62.114 | -0.22888 | -0.027466 | -0.009155 | -0.16479 | -0.31128 | -0.25635 | 0.027465 | 0.21973 | 61.8622 | 62.027 | 124.5804 | 124.8642 | -0.009155 | 124.9191 | 61.9537 | -0.25635 | 124.8642 | -0.009155 | 61.9537 | 124.5804 | 124.9191 | -125.1205 | -125.148
937.6406 | 125.1205 | -61.8439 | 62.9929 | 0.073471 | 0.010974 | 0.013191 | -0.0059729 | 0.066539 | 0.00027774 | 0.070308 | -61.8896 | 62.9929 | -62.0865 | -62.0178 | 62.7411 | 0.073242 | -0.14648 | 0.15564 | 62.9654 | -62.1368 | -0.24262 | 0 | -0.045776 | -0.17395 | -0.25177 | -0.29297 | -0.027466 | 0.19684 | 61.6974 | 61.9995 | 124.585 | 124.8367 | -0.045776 | 124.8093 | 61.9171 | -0.29297 | 124.8367 | -0.045776 | 61.9171 | 124.585 | 124.8093 | -125.0793 | -125.1297
938.6406 | 125.061 | -61.8713 | 63.0386 | 0.050583 | 0.0092649 | 0.01255 | 0.0044945 | 0.068035 | -0.0010041 | 0.069453 | -61.9446 | 63.0295 | -62.0956 | -62.0956 | 62.6495 | -0.013733 | 0.032043 | 0.032043 | 63.0386 | -62.1918 | -0.2243 | -0.009155 | -0.073242 | -0.2243 | -0.3891 | -0.32043 | 0 | 0.15106 | 61.9034 | 61.9034 | 124.5209 | 124.9008 | -0.073242 | 124.91 | 61.8576 | -0.32043 | 124.9008 | -0.073242 | 61.8576 | 124.5209 | 124.91 | -125.1343 | -125.2304
939.6406 | 125.0885 | -61.8622 | 63.0386 | -0.04097 | 0.010547 | 0.01191 | 0.0036401 | 0.068248 | -0.0018585 | 0.068812 | -61.9125 | 63.0249 | -62.0728 | -62.0407 | 62.6953 | 0.050354 | 0.018311 | 0.11902 | 63.0066 | -62.1506 | -0.21057 | -0.013733 | -0.050354 | -0.17853 | -0.34332 | -0.28839 | -0.032043 | 0.16022 | 61.8805 | 61.9812 | 124.5575 | 124.8871 | -0.050354 | 124.8688 | 61.9125 | -0.28839 | 124.8871 | -0.050354 | 61.9125 | 124.5575 | 124.8688 | -125.1114 | -125.1892
940.6406 | 125.0931 | -61.8622 | 63.0341 | -0.20882 | 0.011615 | 0.012123 | 0.0038537 | 0.068889 | -0.0012177 | 0.069667 | -61.8942 | 63.0569 | -62.0636 | -62.027 | 62.7457 | 0.10529 | 0.07782 | 0.19684 | 63.0432 | -62.1231 | -0.20142 | 0.022888 | -0.032043 | -0.16479 | -0.28839 | -0.26093 | 0.009155 | 0.16937 | 61.94 | 62.059 | 124.6078 | 124.9191 | -0.032043 | 124.9054 | 61.9675 | -0.26093 | 124.9191 | -0.032043 | 61.9675 | 124.6078 | 124.9054 | -125.0977 | -125.1572
941.6406 | 125.0748 | -61.8256 | 63.0157 | -0.12489 | 0.010974 | 0.013832 | 0.00043575 | 0.06718 | -0.00014946 | 0.070948 | -61.8668 | 63.0295 | -62.0865 | -62.0178 | 62.7686 | 0.086975 | 0.032043 | 0.1831 | 63.0295 | -62.1277 | -0.26093 | 0.013733 | -0.041198 | -0.19226 | -0.24719 | -0.30212 | 0.013733 | 0.21973 | 61.8576 | 62.0087 | 124.5941 | 124.855 | -0.041198 | 124.855 | 61.9125 | -0.30212 | 124.855 | -0.041198 | 61.9125 | 124.5941 | 124.855 | -125.1022 | -125.1434
942.6406 | 125.0656 | -61.8622 | 63.0341 | 1.6375 | 0.011615 | 0.0080643 | 0.0010767 | 0.06953 | -0.0014313 | 0.069239 | -61.6837 | 62.9974 | -62.1048 | -62.0682 | 62.6724 | -0.032043 | -0.004578 | 0.022888 | 63.0249 | -62.146 | -0.24261 | -0.036621 | 0.17853 | -0.20599 | -0.36163 | -0.28381 | -0.009156 | 0.42114 | 61.8576 | 61.8851 | 124.5346 | 124.8596 | 0.17853 | 124.8871 | 61.8301 | -0.28381 | 124.8596 | 0.17853 | 61.8301 | 124.5346 | 124.8871 | -125.1389 | -125.1801
943.6406 | 125.0885 | -61.8301 | 63.0386 | -0.15541 | 0.012469 | 0.01255 | 0.0025719 | 0.06718 | -0.0014313 | 0.069026 | -61.8622 | 63.0341 | -62.0819 | -62.0819 | 62.5076 | -0.082397 | 0.15106 | 0.18768 | 63.0478 | -62.1231 | -0.25177 | -0.004577 | -0.032044 | -0.25177 | -0.53101 | -0.29297 | 0.009156 | 0.21973 | 61.9812 | 62.0178 | 124.3378 | 124.8642 | -0.032044 | 124.8779 | 61.7477 | -0.29297 | 124.8642 | -0.032044 | 61.7477 | 124.3378 | 124.8779 | -125.1205 | -125.1617
944.6406 | 125.061 | -61.8301 | 63.0478 | -0.025711 | 0.0099057 | 0.0089187 | 0.0032129 | 0.068462 | 0.0011321 | 0.06988 | -61.8851 | 63.0295 | -62.0865 | -62.0178 | 62.7182 | 0.07782 | 0.013733 | 0.14648 | 63.002 | -62.1506 | -0.25635 | -0.018311 | -0.054932 | -0.18768 | -0.32959 | -0.32043 | -0.045777 | 0.20142 | 61.8439 | 61.9766 | 124.5483 | 124.8596 | -0.054932 | 124.8322 | 61.908 | -0.32043 | 124.8596 | -0.054932 | 61.908 | 124.5483 | 124.8322 | -125.1343 | -125.1984
945.6406 | 125.0977 | -61.8622 | 63.0249 | -0.056229 | 0.012042 | 0.01255 | 0.0023583 | 0.068248 | -0.00079046 | 0.068385 | -61.8942 | 63.0249 | -62.0773 | -62.0316 | 62.6953 | 0.091553 | 0.013733 | 0.16937 | 63.0249 | -62.1185 | -0.21515 | 0 | -0.032043 | -0.16937 | -0.32959 | -0.25635 | 0 | 0.18311 | 61.8759 | 62.0316 | 124.5575 | 124.8871 | -0.032043 | 124.8871 | 61.9537 | -0.25635 | 124.8871 | -0.032043 | 61.9537 | 124.5575 | 124.8871 | -125.1022 | -125.1434
946.6406 | 125.1068 | -61.8484 | 63.0386 | -0.079117 | 0.012256 | 0.013619 | 0.0019311 | 0.068889 | -0.00014946 | 0.069026 | -61.8896 | 63.0478 | -62.0636 | -62.027 | 62.7182 | 0.091553 | 0.018311 | 0.16479 | 63.0295 | -62.1231 | -0.21515 | 0.009156 | -0.041198 | -0.17853 | -0.32043 | -0.27466 | -0.009155 | 0.17395 | 61.8668 | 62.0132 | 124.5667 | 124.8962 | -0.041198 | 124.8779 | 61.94 | -0.27466 | 124.8962 | -0.041198 | 61.94 | 124.5667 | 124.8779 | -125.1022 | -125.1617
947.6562 | 125.1572 | -61.8256 | 62.9929 | 0.16502 | 0.010333 | 0.010841 | -0.0029823 | 0.068889 | -0.00036306 | 0.069026 | -61.8896 | 62.9059 | -62.0773 | -61.9995 | 62.7548 | 0.082397 | -0.19226 | 0.17395 | 62.97 | -62.1048 | -0.25177 | -0.086975 | -0.064086 | -0.17395 | -0.23804 | -0.27923 | -0.022888 | 0.18768 | 61.6333 | 61.9995 | 124.5804 | 124.7314 | -0.064086 | 124.7955 | 61.908 | -0.27923 | 124.7314 | -0.064086 | 61.908 | 124.5804 | 124.7955 | -125.0702 | -125.0977
948.6406 | 125.1114 | -61.8256 | 63.0432 | -0.071488 | 0.011401 | 0.015328 | 0.0053491 | 0.065258 | -0.0020721 | 0.068385 | -62.0407 | 62.9974 | -62.1002 | -62.0132 | 62.7274 | 0.10071 | 0.032043 | 0.1831 | 63.0112 | -62.1368 | -0.27466 | -0.045776 | -0.21515 | -0.18768 | -0.31586 | -0.31128 | -0.032044 | 0.05951 | 61.8576 | 62.0087 | 124.5529 | 124.823 | -0.21515 | 124.8367 | 61.9263 | -0.31128 | 124.823 | -0.21515 | 61.9263 | 124.5529 | 124.8367 | -125.1434 | -125.1801
949.6406 | 125.0519 | -61.8713 | 62.9974 | 0.11925 | 0.012469 | 0.012764 | 0.0019311 | 0.066112 | -0.0014313 | 0.071376 | -61.9492 | 63.0524 | -62.0911 | -62.0819 | 62.677 | -0.018311 | -0.054932 | 0.045776 | 62.9929 | -62.1872 | -0.21973 | 0.054931 | -0.07782 | -0.21057 | -0.32043 | -0.31586 | -0.004578 | 0.14191 | 61.8164 | 61.9171 | 124.5483 | 124.9237 | -0.07782 | 124.8642 | 61.853 | -0.31586 | 124.9237 | -0.07782 | 61.853 | 124.5483 | 124.8642 | -125.0885 | -125.1846
950.6406 | 125.0656 | -61.8301 | 63.0341 | -0.11726 | 0.012683 | 0.011482 | 0.0027855 | 0.065899 | -0.0029267 | 0.067958 | -61.8805 | 63.0615 | -62.0773 | -61.9904 | 62.7365 | 0.17395 | -0.27008 | 0.11444 | 63.0112 | -62.1643 | -0.24719 | 0.027465 | -0.050354 | -0.16022 | -0.29755 | -0.33417 | -0.022889 | 0.19684 | 61.5601 | 61.9446 | 124.5667 | 124.8917 | -0.050354 | 124.8413 | 62.0041 | -0.33417 | 124.8917 | -0.050354 | 62.0041 | 124.5667 | 124.8413 | -125.1114 | -125.1984
951.6406 | 125.0702 | -61.8301 | 63.0295 | -0.071488 | 0.012897 | 0.012978 | 0.0032129 | 0.066112 | -0.0020721 | 0.068812 | -61.8805 | 63.0341 | -62.0911 | -62.0087 | 62.709 | 0.086975 | 0.032043 | 0.16022 | 63.0569 | -62.1414 | -0.26093 | 0.004578 | -0.050354 | -0.17853 | -0.32043 | -0.31128 | 0.027466 | 0.21057 | 61.8622 | 61.9904 | 124.5392 | 124.8642 | -0.050354 | 124.8871 | 61.9171 | -0.31128 | 124.8642 | -0.050354 | 61.9171 | 124.5392 | 124.8871 | -125.1205 | -125.1709
952.6562 | 125.1343 | -61.8118 | 62.9883 | 0.16502 | 0.010119 | 0.012123 | -0.0014869 | 0.068035 | -0.0010041 | 0.068171 | -61.8896 | 62.9288 | -62.0956 | -62.0041 | 62.7502 | 0.07782 | -0.17395 | 0.15564 | 62.9837 | -62.0911 | -0.28381 | -0.059509 | -0.077819 | -0.19226 | -0.23804 | -0.27923 | -0.004577 | 0.20599 | 61.6379 | 61.9675 | 124.5621 | 124.7406 | -0.077819 | 124.7955 | 61.8896 | -0.27923 | 124.7406 | -0.077819 | 61.8896 | 124.5621 | 124.7955 | -125.0839 | -125.0793
953.6406 | 125.0061 | -61.853 | 63.0112 | 0.073471 | 0.011828 | 0.014046 | 0.0053491 | 0.067821 | -0.0012177 | 0.069026 | -61.9354 | 63.0569 | -62.0728 | -62.0728 | 62.6312 | -0.027466 | 0.045776 | 0.059509 | 63.0341 | -62.1323 | -0.21973 | 0.045777 | -0.082398 | -0.21973 | -0.37994 | -0.27924 | 0.022889 | 0.13733 | 61.8988 | 61.9125 | 124.4843 | 124.91 | -0.082398 | 124.8871 | 61.8256 | -0.27924 | 124.91 | -0.082398 | 61.8256 | 124.4843 | 124.8871 | -125.0839 | -125.1434
954.6406 | 125.1022 | -61.8256 | 63.0936 | -0.14778 | 0.012256 | 0.01255 | 0.0010767 | 0.065685 | -0.00036306 | 0.068385 | -61.9217 | 63.0432 | -62.0911 | -62.0041 | 62.7182 | 0.11444 | 0.086975 | 0.1831 | 63.0432 | -62.1506 | -0.2655 | -0.050354 | -0.09613 | -0.17853 | -0.37537 | -0.32501 | -0.050354 | 0.16937 | 61.9125 | 62.0087 | 124.5438 | 124.8688 | -0.09613 | 124.8688 | 61.94 | -0.32501 | 124.8688 | -0.09613 | 61.94 | 124.5438 | 124.8688 | -125.1846 | -125.2441
955.6406 | 125.1068 | -61.8393 | 63.0661 | -0.2317 | 0.01076 | 0.011055 | 0.0015039 | 0.066753 | -0.0014313 | 0.06988 | -61.9217 | 63.0524 | -62.0819 | -62.0453 | 62.709 | 0.073242 | 0.11444 | 0.15106 | 63.0524 | -62.1368 | -0.24262 | -0.013733 | -0.082398 | -0.20599 | -0.35706 | -0.29755 | -0.013733 | 0.16022 | 61.9537 | 61.9904 | 124.5483 | 124.8917 | -0.082398 | 124.8917 | 61.9125 | -0.29755 | 124.8917 | -0.082398 | 61.9125 | 124.5483 | 124.8917 | -125.148 | -125.2029
956.6406 | 125.0793 | -61.8484 | 63.0615 | -0.18593 | 0.0096921 | 0.0099869 | 0.0044945 | 0.065258 | -0.0014313 | 0.067744 | -61.908 | 63.0524 | -62.0819 | -62.0132 | 62.7274 | 0.10529 | 0.07782 | 0.21515 | 63.0615 | -62.1048 | -0.23346 | -0.009155 | -0.059509 | -0.16479 | -0.33417 | -0.25635 | 0 | 0.17395 | 61.9263 | 62.0636 | 124.5758 | 124.9008 | -0.059509 | 124.91 | 61.9537 | -0.25635 | 124.9008 | -0.059509 | 61.9537 | 124.5758 | 124.91 | -125.1434 | -125.1663
957.6562 | 125.1938 | -61.8256 | 62.9745 | 0.24895 | 0.0086239 | 0.0080643 | -0.0019141 | 0.066753 | 0.00027774 | 0.068812 | -61.8393 | 62.9608 | -62.0819 | -61.9949 | 62.7594 | 0.082397 | -0.17853 | 0.16479 | 62.9837 | -62.0956 | -0.25635 | -0.013733 | -0.013732 | -0.16937 | -0.21515 | -0.27008 | 0.009156 | 0.24262 | 61.647 | 61.9904 | 124.585 | 124.7864 | -0.013732 | 124.8093 | 61.908 | -0.27008 | 124.7864 | -0.013732 | 61.908 | 124.585 | 124.8093 | -125.0565 | -125.0702
958.6406 | 125.061 | -61.8393 | 63.0478 | -0.22408 | 0.013537 | 0.013405 | 0.0029993 | 0.066753 | -0.0014313 | 0.068385 | -61.9125 | 63.0157 | -62.0682 | -62.0316 | 62.7182 | 0.09613 | 0.10986 | 0.16937 | 63.0524 | -62.114 | -0.22888 | -0.032044 | -0.073243 | -0.19226 | -0.32959 | -0.27466 | 0.004577 | 0.15564 | 61.9492 | 62.0087 | 124.5575 | 124.855 | -0.073243 | 124.8917 | 61.9354 | -0.27466 | 124.855 | -0.073243 | 61.9354 | 124.5575 | 124.8917 | -125.116 | -125.1617
959.6406 | 125.1022 | -61.8393 | 63.0478 | -0.20119 | 0.010333 | 0.014687 | 0.0044945 | 0.065899 | -0.0016449 | 0.069667 | -61.8759 | 63.0341 | -62.0682 | -61.9904 | 62.7457 | 0.10986 | 0.073242 | 0.19226 | 63.0569 | -62.0956 | -0.22888 | -0.013733 | -0.036622 | -0.15106 | -0.30212 | -0.25635 | 0.009155 | 0.19226 | 61.9125 | 62.0316 | 124.585 | 124.8734 | -0.036622 | 124.8962 | 61.9492 | -0.25635 | 124.8734 | -0.036622 | 61.9492 | 124.585 | 124.8962 | -125.116 | -125.1434
960.6406 | 125.1205 | -61.8256 | 63.0432 | -0.26222 | 0.012897 | 0.0097733 | 0.0023583 | 0.06718 | -0.0018585 | 0.069026 | -61.8942 | 63.0432 | -62.0728 | -62.0132 | 62.7319 | 0.091553 | 0.07782 | 0.18768 | 63.0661 | -62.1094 | -0.24719 | 0 | -0.068664 | -0.18768 | -0.31128 | -0.28381 | 0.022888 | 0.17853 | 61.9034 | 62.0132 | 124.5575 | 124.8688 | -0.068664 | 124.8917 | 61.9171 | -0.28381 | 124.8688 | -0.068664 | 61.9171 | 124.5575 | 124.8917 | -125.116 | -125.1526
961.6406 | 125.0519 | -61.8484 | 63.0386 | 0.042953 | 0.010547 | 0.010628 | -0.00063225 | 0.066753 | -0.0029267 | 0.066676 | -61.9171 | 63.0341 | -62.0819 | -62.0407 | 62.709 | 0.068665 | 0.14648 | 0.16479 | 63.0615 | -62.1185 | -0.23346 | -0.004577 | -0.068664 | -0.19226 | -0.32959 | -0.27008 | 0.022888 | 0.1648 | 61.9949 | 62.0132 | 124.5575 | 124.8825 | -0.068664 | 124.91 | 61.9171 | -0.27008 | 124.8825 | -0.068664 | 61.9171 | 124.5575 | 124.91 | -125.1205 | -125.1572
962.6406 | 125.0793 | -61.8393 | 63.0432 | -0.22408 | 0.010974 | 0.013191 | 0.0042809 | 0.06718 | -0.0016449 | 0.071162 | -61.8713 | 63.0478 | -62.0773 | -62.0041 | 62.7502 | 0.10529 | 0.045776 | 0.20142 | 63.0341 | -62.1414 | -0.23804 | 0.004578 | -0.032044 | -0.16479 | -0.29297 | -0.30212 | -0.009155 | 0.20599 | 61.8851 | 62.0407 | 124.5895 | 124.8871 | -0.032044 | 124.8734 | 61.9446 | -0.30212 | 124.8871 | -0.032044 | 61.9446 | 124.5895 | 124.8734 | -125.1205 | -125.1846
963.6406 | 125.0427 | -61.8347 | 63.0615 | -0.2317 | 0.0090513 | 0.013619 | -0.00041865 | 0.067821 | 0.00049134 | 0.069667 | -61.9354 | 63.0386 | -62.0773 | -62.0453 | 62.6907 | 0.10071 | 0.14191 | 0.16937 | 63.0844 | -62.1048 | -0.24262 | -0.022888 | -0.10071 | -0.21057 | -0.37079 | -0.27008 | 0.022889 | 0.14191 | 61.9766 | 62.0041 | 124.5255 | 124.8734 | -0.10071 | 124.9191 | 61.9354 | -0.27008 | 124.8734 | -0.10071 | 61.9354 | 124.5255 | 124.9191 | -125.1389 | -125.1663
964.6406 | 125.0656 | -61.8668 | 63.0707 | 0.035324 | 0.012042 | 0.0089187 | 0.0010767 | 0.066967 | -0.0016449 | 0.069453 | -61.9217 | 63.002 | -62.114 | -62.059 | 62.6999 | 0.07782 | 0.12817 | 0.17853 | 63.0615 | -62.1094 | -0.24719 | -0.068665 | -0.054932 | -0.19226 | -0.37079 | -0.24262 | -0.009156 | 0.19226 | 61.9949 | 62.0453 | 124.5667 | 124.8688 | -0.054932 | 124.9283 | 61.9446 | -0.24262 | 124.8688 | -0.054932 | 61.9446 | 124.5667 | 124.9283 | -125.1846 | -125.1801
965.6406 | 125.061 | -61.8439 | 63.0569 | -0.24696 | 0.010333 | 0.013405 | 0.0010767 | 0.067608 | 0.00091854 | 0.068812 | -61.9308 | 63.002 | -62.0728 | -62.0773 | 62.6724 | 0.064087 | 0.15106 | 0.13733 | 63.0753 | -62.1002 | -0.22888 | -0.054932 | -0.086975 | -0.23346 | -0.38452 | -0.25635 | 0.01831 | 0.14191 | 61.9949 | 61.9812 | 124.5163 | 124.8459 | -0.086975 | 124.9191 | 61.908 | -0.25635 | 124.8459 | -0.086975 | 61.908 | 124.5163 | 124.9191 | -125.1297 | -125.1572
966.6406 | 125.0839 | -61.8301 | 63.0615 | -0.2317 | 0.010119 | 0.0087051 | 8.546e-06 | 0.065258 | -0.0018585 | 0.067958 | -61.9354 | 63.0295 | -62.0682 | -62.0407 | 62.6907 | 0.091553 | 0.13275 | 0.16479 | 63.0432 | -62.1094 | -0.23804 | -0.032043 | -0.10529 | -0.21057 | -0.37079 | -0.27924 | -0.01831 | 0.13275 | 61.9629 | 61.9949 | 124.5209 | 124.8596 | -0.10529 | 124.8734 | 61.9217 | -0.27924 | 124.8596 | -0.10529 | 61.9217 | 124.5209 | 124.8734 | -125.1297 | -125.1709
967.6406 | 125.1343 | -61.853 | 63.0295 | -0.20119 | 0.010974 | 0.012978 | 0.0053491 | 0.066967 | -0.00036306 | 0.069239 | -61.853 | 63.0112 | -62.0728 | -61.9904 | 62.7274 | 0.10986 | 0.036621 | 0.18768 | 63.0478 | -62.114 | -0.21973 | -0.018311 | 0 | -0.13733 | -0.30212 | -0.26093 | 0.018311 | 0.21973 | 61.8896 | 62.0407 | 124.5804 | 124.8642 | 0 | 124.9008 | 61.9629 | -0.26093 | 124.8642 | 0 | 61.9629 | 124.5804 | 124.9008 | -125.1022 | -125.1434
968.6406 | 125.0519 | -61.8164 | 63.0478 | -0.28511 | 0.0081967 | 0.013405 | -0.0042639 | 0.065044 | -0.00036306 | 0.070521 | -61.8851 | 62.97 | -62.0499 | -62.0041 | 62.7457 | 0.11444 | 0.10071 | 0.2243 | 63.0615 | -62.0773 | -0.23346 | -0.07782 | -0.068665 | -0.18768 | -0.30212 | -0.26093 | 0.013732 | 0.16479 | 61.9171 | 62.0407 | 124.5621 | 124.7864 | -0.068665 | 124.8779 | 61.9308 | -0.26093 | 124.7864 | -0.068665 | 61.9308 | 124.5621 | 124.8779 | -125.0977 | -125.1251
969.6406 | 125.0015 | -61.8439 | 63.0798 | -0.30037 | 0.0090513 | 0.010841 | 0.00064935 | 0.06718 | -0.0016449 | 0.068171 | -61.9492 | 63.0157 | -62.0819 | -62.1002 | 62.9517 | 0.23346 | -0.054932 | 0.10529 | 63.0569 | -62.1231 | -0.23804 | -0.064087 | -0.10529 | -0.25635 | -0.12817 | -0.27924 | -0.022888 | 0.13275 | 61.7889 | 61.9492 | 124.7955 | 124.8596 | -0.10529 | 124.9008 | 62.0773 | -0.27924 | 124.8596 | -0.10529 | 62.0773 | 124.7955 | 124.9008 | -125.1617 | -125.2029
970.6406 | 125.061 | -61.8301 | 63.0432 | -0.26222 | 0.0073423 | 0.0091323 | -0.00020505 | 0.064617 | -0.00057686 | 0.06988 | -61.9217 | 62.9837 | -62.0728 | -62.0224 | 62.6816 | 0.07782 | 0.11902 | 0.18768 | 63.0569 | -62.0956 | -0.24262 | -0.059509 | -0.091553 | -0.19226 | -0.36163 | -0.2655 | 0.013733 | 0.15106 | 61.9492 | 62.0178 | 124.5117 | 124.8138 | -0.091553 | 124.8871 | 61.908 | -0.2655 | 124.8138 | -0.091553 | 61.908 | 124.5117 | 124.8871 | -125.116 | -125.1389
971.6406 | 125.0519 | -61.8118 | 63.0844 | -0.26222 | 0.0090513 | 0.0080643 | -0.0017005 | 0.065044 | -0.0010041 | 0.06988 | -61.908 | 62.9562 | -62.0636 | -62.0224 | 62.7365 | 0.10986 | 0.11902 | 0.18768 | 63.0386 | -62.0819 | -0.25177 | -0.12817 | -0.09613 | -0.21057 | -0.3479 | -0.27008 | -0.045777 | 0.15564 | 61.9308 | 61.9995 | 124.5483 | 124.7681 | -0.09613 | 124.8505 | 61.9217 | -0.27008 | 124.7681 | -0.09613 | 61.9217 | 124.5483 | 124.8505 | -125.148 | -125.1663
972.6562 | 125.0473 | -61.8668 | 63.0341 | 0.042953 | 0.010119 | 0.012764 | 0.0083397 | 0.068248 | -0.0012177 | 0.069026 | -61.9217 | 63.0295 | -62.0728 | -62.0682 | 62.6404 | 0.004578 | 0.018311 | 0.036621 | 63.0295 | -62.1368 | -0.20599 | -0.004578 | -0.054932 | -0.20142 | -0.39368 | -0.27008 | -0.004578 | 0.15106 | 61.8851 | 61.9034 | 124.5071 | 124.8962 | -0.054932 | 124.8962 | 61.8713 | -0.27008 | 124.8962 | -0.054932 | 61.8713 | 124.5071 | 124.8962 | -125.1068 | -125.1709
973.6406 | 125.061 | -61.8347 | 63.0432 | -0.31563 | 0.011615 | 0.0087051 | -0.0014869 | 0.064617 | -0.0016449 | 0.069453 | -61.94 | 62.9929 | -62.0544 | -62.0361 | 62.7045 | -0.032043 | 0.4715 | 0.10529 | 63.0844 | -62.0773 | -0.21973 | -0.050354 | -0.10529 | -0.20142 | -0.33875 | -0.24262 | 0.041199 | 0.11444 | 62.3062 | 61.94 | 124.5392 | 124.8276 | -0.10529 | 124.9191 | 61.8027 | -0.24262 | 124.8276 | -0.10529 | 61.8027 | 124.5392 | 124.9191 | -125.0977 | -125.1205
974.6406 | 125.0839 | -61.8164 | 63.0661 | -0.28511 | 0.0092649 | 0.0074233 | 0.00064935 | 0.063976 | -0.00036306 | 0.06988 | -61.94 | 62.9837 | -62.059 | -62.0453 | 62.6999 | 0.086975 | 0.1236 | 0.18768 | 63.0341 | -62.1002 | -0.24262 | -0.082397 | -0.1236 | -0.22888 | -0.36621 | -0.28381 | -0.032043 | 0.11902 | 61.94 | 62.0041 | 124.5163 | 124.8001 | -0.1236 | 124.8505 | 61.9034 | -0.28381 | 124.8001 | -0.1236 | 61.9034 | 124.5163 | 124.8505 | -125.1251 | -125.1663
975.6406 | 125.1572 | -61.7935 | 63.0157 | -0.20119 | 0.0071285 | 0.012123 | -0.0019141 | 0.065471 | -0.0016449 | 0.067531 | -61.853 | 62.9517 | -62.0361 | -61.9537 | 62.7777 | 0.16479 | 0.004578 | 0.28839 | 63.0249 | -62.0453 | -0.24262 | -0.064087 | -0.059509 | -0.16022 | -0.23804 | -0.25177 | 0.009155 | 0.18311 | 61.7981 | 62.0819 | 124.5712 | 124.7452 | -0.059509 | 124.8184 | 61.9583 | -0.25177 | 124.7452 | -0.059509 | 61.9583 | 124.5712 | 124.8184 | -125.0519 | -125.061
976.6406 | 125.0977 | -61.7981 | 63.0753 | -0.27748 | 0.0081967 | 0.0069961 | 0.00022215 | 0.065685 | 0.00070494 | 0.068171 | -61.8759 | 62.9196 | -62.0453 | -61.972 | 62.7686 | 0.14648 | 0.064087 | 0.24719 | 63.0112 | -62.059 | -0.24719 | -0.15564 | -0.07782 | -0.17395 | -0.3067 | -0.26093 | -0.064087 | 0.16937 | 61.8622 | 62.0453 | 124.5667 | 124.7177 | -0.07782 | 124.8093 | 61.9446 | -0.26093 | 124.7177 | -0.07782 | 61.9446 | 124.5667 | 124.8093 | -125.1205 | -125.1343
977.6406 | 125.0748 | -61.8347 | 63.0432 | -0.1783 | 0.012042 | 0.01191 | 0.0062035 | 0.06483 | -0.0016449 | 0.067103 | -61.853 | 63.002 | -62.0499 | -61.9858 | 62.7274 | 0.09613 | -0.07782 | 0.24719 | 63.0203 | -62.1323 | -0.21515 | -0.041199 | -0.01831 | -0.15106 | -0.31586 | -0.29755 | -0.022888 | 0.19684 | 61.7569 | 62.0819 | 124.5621 | 124.8367 | -0.01831 | 124.855 | 61.9308 | -0.29755 | 124.8367 | -0.01831 | 61.9308 | 124.5621 | 124.855 | -125.0931 | -125.1755
978.6406 | 125.1343 | -61.8118 | 63.0341 | -0.21645 | 0.0069149 | 0.0089187 | -0.0014869 | 0.065899 | -0.0022859 | 0.070308 | -61.853 | 62.9333 | -62.0453 | -61.9537 | 62.796 | 0.16479 | 0 | 0.29755 | 63.0157 | -62.0499 | -0.23346 | -0.10071 | -0.041198 | -0.14191 | -0.23804 | -0.23804 | -0.018311 | 0.19226 | 61.8118 | 62.1094 | 124.6079 | 124.7452 | -0.041198 | 124.8276 | 61.9766 | -0.23804 | 124.7452 | -0.041198 | 61.9766 | 124.6079 | 124.8276 | -125.0793 | -125.0839
979.6406 | 125.0977 | -61.853 | 63.0478 | -0.26985 | 0.0090513 | 0.0099869 | -0.00041865 | 0.063549 | -0.0016449 | 0.070948 | -61.8622 | 62.9745 | -62.059 | -61.9904 | 62.7411 | 0.13733 | 0.073242 | 0.26093 | 63.0203 | -62.0819 | -0.20599 | -0.073243 | -0.009156 | -0.13733 | -0.3067 | -0.22888 | -0.027466 | 0.19684 | 61.9263 | 62.114 | 124.5941 | 124.8276 | -0.009156 | 124.8734 | 61.9904 | -0.22888 | 124.8276 | -0.009156 | 61.9904 | 124.5941 | 124.8734 | -125.1068 | -125.1297
980.6406 | 125.1205 | -61.8118 | 63.0341 | -0.23933 | 0.0069149 | 0.0089187 | 0.0010767 | 0.064403 | 0.00027774 | 0.068385 | -61.8576 | 62.9471 | -62.059 | -61.9629 | 62.7594 | 0.16022 | 0.027466 | 0.2655 | 63.002 | -62.059 | -0.24719 | -0.086975 | -0.045776 | -0.15106 | -0.27466 | -0.24719 | -0.032044 | 0.20142 | 61.8393 | 62.0773 | 124.5712 | 124.7589 | -0.045776 | 124.8138 | 61.972 | -0.24719 | 124.7589 | -0.045776 | 61.972 | 124.5712 | 124.8138 | -125.0931 | -125.0931
981.6406 | 125.1801 | -61.7889 | 63.0295 | -0.1783 | 0.0088375 | 0.0082779 | 0.0023583 | 0.065044 | -0.0016449 | 0.069239 | -61.8484 | 62.9105 | -62.0224 | -61.94 | 62.6816 | 0.14191 | -0.004578 | 0.24719 | 62.9608 | -62.0316 | -0.23346 | -0.11902 | -0.05951 | -0.15106 | -0.3479 | -0.24262 | -0.068665 | 0.17395 | 61.7844 | 62.0361 | 124.4705 | 124.6994 | -0.05951 | 124.7498 | 61.9308 | -0.24262 | 124.6994 | -0.05951 | 61.9308 | 124.4705 | 124.7498 | -125.0519 | -125.061
982.6406 | 125.0427 | -61.8576 | 63.0661 | -0.24696 | 0.010547 | 0.012337 | 0.0068445 | 0.063549 | -0.0010041 | 0.069026 | -61.9125 | 63.0203 | -62.0499 | -62.0224 | 62.6816 | 0.068665 | 0.13733 | 0.16022 | 63.0112 | -62.1094 | -0.19226 | -0.045776 | -0.054932 | -0.16479 | -0.38452 | -0.25177 | -0.054932 | 0.13733 | 61.9949 | 62.0178 | 124.5392 | 124.8779 | -0.054932 | 124.8688 | 61.9263 | -0.25177 | 124.8779 | -0.054932 | 61.9263 | 124.5392 | 124.8688 | -125.116 | -125.1755
983.6406 | 125.1709 | -61.8073 | 63.0203 | 0.16502 | 0.0073423 | 0.0069961 | 8.546e-06 | 0.064617 | -0.00079046 | 0.071376 | -61.8393 | 62.9059 | -62.059 | -61.9217 | 62.8006 | 0.17853 | -0.041199 | 0.30212 | 63.0066 | -62.0361 | -0.25177 | -0.11444 | -0.032043 | -0.11444 | -0.21973 | -0.22888 | -0.013733 | 0.21973 | 61.7661 | 62.1094 | 124.6078 | 124.7131 | -0.032043 | 124.8138 | 61.9858 | -0.22888 | 124.7131 | -0.032043 | 61.9858 | 124.6078 | 124.8138 | -125.0793 | -125.0565
984.6406 | 125.1801 | -61.7661 | 63.0249 | -0.88783 | 0.0099057 | 0.011269 | -0.00020505 | 0.065044 | -0.0031403 | 0.069026 | -61.6516 | 62.9425 | -62.027 | -61.9034 | 62.7548 | 0.13733 | -0.027466 | 0.31128 | 62.9562 | -62.0316 | -0.26093 | -0.082397 | 0.11444 | -0.13733 | -0.27008 | -0.2655 | -0.068664 | 0.37537 | 61.7386 | 62.0773 | 124.5209 | 124.7086 | 0.11444 | 124.7223 | 61.9034 | -0.2655 | 124.7086 | 0.11444 | 61.9034 | 124.5209 | 124.7223 | -125.0519 | -125.0565
985.6406 | 125.2167 | -61.7935 | 62.9974 | -0.063858 | 0.0090513 | 0.0082779 | 8.546e-06 | 0.06419 | -0.00057686 | 0.067744 | -61.8347 | 62.8922 | -62.0407 | -61.908 | 62.5259 | 0.26093 | 0.2655 | -0.032043 | 63.0249 | -62.0316 | -0.24719 | -0.10529 | -0.041199 | -0.11444 | -0.4715 | -0.23804 | 0.027465 | 0.20599 | 62.059 | 61.7615 | 124.3195 | 124.6857 | -0.041199 | 124.8184 | 62.0544 | -0.23804 | 124.6857 | -0.041199 | 62.0544 | 124.3195 | 124.8184 | -125.0381 | -125.029
986.6406 | 125.1434 | -61.7706 | 63.0249 | -0.20119 | 0.0081967 | 0.010414 | 0.0034265 | 0.062694 | -0.0035675 | 0.06988 | -61.8301 | 62.9105 | -62.0499 | -61.9263 | 62.8235 | 0.18768 | -0.041199 | 0.30212 | 63.002 | -62.0453 | -0.27924 | -0.11444 | -0.059509 | -0.15564 | -0.20142 | -0.27466 | -0.022888 | 0.21973 | 61.7294 | 62.0728 | 124.5941 | 124.6811 | -0.059509 | 124.7726 | 61.9583 | -0.27466 | 124.6811 | -0.059509 | 61.9583 | 124.5941 | 124.7726 | -125.0748 | -125.0702
987.6406 | 125.0565 | -61.8164 | 63.0844 | -0.33852 | 0.0094785 | 0.012337 | 0.0038537 | 0.06419 | -0.0027131 | 0.069026 | -61.9125 | 63.0249 | -62.0773 | -62.0132 | 62.6907 | 0.068665 | 0.14648 | 0.17395 | 63.0295 | -62.0865 | -0.26093 | -0.05951 | -0.096131 | -0.19684 | -0.39368 | -0.27008 | -0.054932 | 0.16479 | 61.9629 | 61.9904 | 124.5071 | 124.8413 | -0.096131 | 124.8459 | 61.8851 | -0.27008 | 124.8413 | -0.096131 | 61.8851 | 124.5071 | 124.8459 | -125.1617 | -125.1709
988.6406 | 125.1205 | -61.7935 | 62.9929 | -0.11726 | 0.0077695 | 0.012337 | -0.0046913 | 0.063335 | 0.00049134 | 0.067744 | -61.8896 | 62.8922 | -62.0544 | -61.9537 | 62.7914 | 0.16022 | -0.068665 | 0.26093 | 62.9745 | -62.0407 | -0.26093 | -0.10071 | -0.09613 | -0.16022 | -0.20142 | -0.24719 | -0.018311 | 0.16479 | 61.7249 | 62.0544 | 124.585 | 124.6857 | -0.09613 | 124.7681 | 61.9537 | -0.24719 | 124.6857 | -0.09613 | 61.9537 | 124.585 | 124.7681 | -125.0473 | -125.0336
989.6406 | 125.1709 | -61.7889 | 63.0157 | -0.071488 | 0.0077695 | 0.013191 | -0.0010597 | 0.063335 | -0.0018585 | 0.070308 | -61.8988 | 62.8967 | -62.0499 | -61.9675 | 62.764 | 0.15106 | -0.059509 | 0.2243 | 62.97 | -62.0407 | -0.26093 | -0.11902 | -0.10986 | -0.17853 | -0.25177 | -0.25177 | -0.045776 | 0.15106 | 61.7294 | 62.0132 | 124.5529 | 124.6857 | -0.10986 | 124.7589 | 61.94 | -0.25177 | 124.6857 | -0.10986 | 61.94 | 124.5529 | 124.7589 | -125.0656 | -125.0565
990.6406 | 125.1526 | -61.7935 | 63.0112 | -0.086746 | 0.0077695 | 0.0065689 | -0.00041865 | 0.061412 | -0.0020721 | 0.071376 | -61.8576 | 62.8693 | -62.0453 | -61.9034 | 62.8098 | 0.17395 | -0.07782 | 0.28839 | 62.9608 | -62.0224 | -0.25177 | -0.14191 | -0.064087 | -0.10986 | -0.20142 | -0.22888 | -0.050354 | 0.18768 | 61.7157 | 62.0819 | 124.6033 | 124.6628 | -0.064087 | 124.7543 | 61.9675 | -0.22888 | 124.6628 | -0.064087 | 61.9675 | 124.6033 | 124.7543 | -125.0565 | -125.0336
991.6406 | 125.1526 | -61.7889 | 63.0157 | -0.11726 | 0.0073423 | 0.010414 | -0.0010597 | 0.063121 | -0.00079046 | 0.064967 | -61.8576 | 62.883 | -62.027 | -61.9217 | 62.8052 | 0.19226 | -0.091553 | 0.28839 | 62.9471 | -62.0544 | -0.23804 | -0.13275 | -0.068665 | -0.13275 | -0.21057 | -0.2655 | -0.068664 | 0.16937 | 61.6974 | 62.0773 | 124.5941 | 124.6719 | -0.068665 | 124.736 | 61.9812 | -0.2655 | 124.6719 | -0.068665 | 61.9812 | 124.5941 | 124.736 | -125.0427 | -125.0702
992.6406 | 125.0793 | -61.8576 | 63.0615 | -0.21645 | 0.012469 | 0.010628 | 0.0038537 | 0.065044 | -0.00079046 | 0.068171 | -61.8896 | 63.0203 | -62.0361 | -61.9904 | 62.6953 | 0.082397 | 0.10071 | 0.17395 | 63.0249 | -62.0865 | -0.17853 | -0.041198 | -0.032043 | -0.13275 | -0.36621 | -0.22888 | -0.036621 | 0.14648 | 61.9583 | 62.0316 | 124.5529 | 124.8779 | -0.032043 | 124.8825 | 61.94 | -0.22888 | 124.8779 | -0.032043 | 61.94 | 124.5529 | 124.8825 | -125.0977 | -125.148
993.6406 | 125.2075 | -61.7752 | 63.0341 | -0.20882 | 0.0077695 | 0.0097733 | -0.0049049 | 0.062053 | -0.0022859 | 0.066676 | -61.8393 | 62.8967 | -62.0407 | -61.734 | 62.5122 | -0.064087 | 0.032043 | 0.21515 | 62.9745 | -62.0224 | -0.2655 | -0.13733 | -0.064086 | 0.041199 | -0.52185 | -0.24719 | -0.05951 | 0.20142 | 61.8073 | 61.9904 | 124.2874 | 124.6719 | -0.064086 | 124.7498 | 61.7111 | -0.24719 | 124.6719 | -0.064086 | 61.7111 | 124.2874 | 124.7498 | -125.0748 | -125.0565
994.6406 | 125.4135 | -61.7523 | 63.0844 | -0.10201 | 0.0054197 | 0.0093459 | -0.0012733 | 0.060985 | -0.0010041 | 0.071803 | -61.8484 | 62.9242 | -62.027 | -61.9125 | 62.8235 | 0.19226 | -0.086975 | 0.32501 | 62.9837 | -62.0178 | -0.27466 | -0.16022 | -0.096131 | -0.16022 | -0.26093 | -0.2655 | -0.10071 | 0.17853 | 61.6653 | 62.0773 | 124.5758 | 124.6765 | -0.096131 | 124.736 | 61.9446 | -0.2655 | 124.6765 | -0.096131 | 61.9446 | 124.5758 | 124.736 | -125.1114 | -125.1022
995.6406 | 125.1617 | -61.8118 | 63.0295 | -0.0028231 | 0.0079831 | 0.0076369 | -0.00063225 | 0.063549 | -0.0031403 | 0.069453 | -61.9034 | 62.9105 | -62.0499 | -61.9537 | 62.7548 | 0.11902 | -0.064087 | 0.2243 | 62.9654 | -62.0407 | -0.23804 | -0.11902 | -0.091552 | -0.14191 | -0.27466 | -0.22888 | -0.064087 | 0.14648 | 61.7477 | 62.0361 | 124.5667 | 124.7223 | -0.091552 | 124.7772 | 61.9308 | -0.22888 | 124.7223 | -0.091552 | 61.9308 | 124.5667 | 124.7772 | -125.0793 | -125.0702
996.6406 | 125.1297 | -61.7844 | 63.0524 | -0.048599 | 0.0073423 | 0.010628 | -0.00063225 | 0.060772 | 0.0022003 | 0.069026 | -61.9125 | 62.8922 | -62.059 | -61.9583 | 62.7365 | 0.10529 | -0.07782 | 0.20142 | 62.9471 | -62.059 | -0.27466 | -0.16022 | -0.12817 | -0.17395 | -0.31586 | -0.27466 | -0.10529 | 0.14648 | 61.7065 | 61.9858 | 124.5209 | 124.6765 | -0.12817 | 124.7314 | 61.8896 | -0.27466 | 124.6765 | -0.12817 | 61.8896 | 124.5209 | 124.7314 | -125.1114 | -125.1114
997.6406 | 125.0702 | -61.7981 | 63.0798 | -0.24696 | 0.0092649 | 0.012123 | 0.0025719 | 0.063549 | -0.0016449 | 0.069026 | -61.8759 | 62.9974 | -62.0407 | -61.9858 | 62.7182 | 0.086975 | 0.13733 | 0.20599 | 63.0203 | -62.0773 | -0.24261 | -0.082397 | -0.07782 | -0.18768 | -0.36163 | -0.27924 | -0.059509 | 0.16479 | 61.9354 | 62.0041 | 124.5163 | 124.7955 | -0.07782 | 124.8184 | 61.8851 | -0.27924 | 124.7955 | -0.07782 | 61.8851 | 124.5163 | 124.8184 | -125.1205 | -125.1572
998.6406 | 125.1434 | -61.7706 | 63.0249 | -0.13252 | 0.0075559 | 0.0065689 | -0.00063225 | 0.062481 | 0.00049134 | 0.069453 | -61.8896 | 62.9242 | -62.0544 | -61.9308 | 62.7823 | 0.14648 | -0.068665 | 0.23804 | 62.9517 | -62.0224 | -0.28381 | -0.10071 | -0.11902 | -0.16022 | -0.24261 | -0.25177 | -0.073242 | 0.16479 | 61.702 | 62.0087 | 124.5529 | 124.6948 | -0.11902 | 124.7223 | 61.9171 | -0.25177 | 124.6948 | -0.11902 | 61.9171 | 124.5529 | 124.7223 | -125.0793 | -125.0473
999.6406 | 125.1434 | -61.7798 | 63.0249 | -0.079117 | 0.0088375 | 0.0063553 | 0.00022215 | 0.063762 | -0.0014313 | 0.069239 | -61.8851 | 62.9013 | -62.0361 | -61.9629 | 62.7869 | 0.13275 | -0.073242 | 0.2243 | 62.9791 | -62.0316 | -0.25635 | -0.1236 | -0.10529 | -0.18311 | -0.23804 | -0.25177 | -0.045776 | 0.15106 | 61.7065 | 62.0041 | 124.5666 | 124.6811 | -0.10529 | 124.7589 | 61.9125 | -0.25177 | 124.6811 | -0.10529 | 61.9125 | 124.5666 | 124.7589 | -125.061 | -125.0565
1000.6406 | 125.148 | -61.7981 | 63.0478 | -0.094376 | 0.0062741 | 0.012764 | -0.0031959 | 0.063335 | -0.00014946 | 0.068599 | -61.8622 | 62.8738 | -62.0407 | -61.8942 | 62.8098 | 0.1831 | -0.082397 | 0.28381 | 62.9608 | -62.0087 | -0.24261 | -0.17395 | -0.064087 | -0.09613 | -0.23804 | -0.21057 | -0.086976 | 0.17853 | 61.7157 | 62.0819 | 124.6078 | 124.6719 | -0.064087 | 124.7589 | 61.9812 | -0.21057 | 124.6719 | -0.064087 | 61.9812 | 124.6078 | 124.7589 | -125.0885 | -125.0565
1001.6406 | 125.1801 | -61.7935 | 63.0066 | -0.079117 | 0.0054197 | 0.0099869 | -0.0010597 | 0.062053 | -0.00014946 | 0.069667 | -61.8439 | 62.9242 | -62.0361 | -61.9217 | 62.8006 | 0.18768 | -0.073242 | 0.27466 | 62.97 | -62.0132 | -0.24262 | -0.082398 | -0.050354 | -0.12817 | -0.20599 | -0.21973 | -0.036621 | 0.19226 | 61.7203 | 62.0682 | 124.5941 | 124.7177 | -0.050354 | 124.7635 | 61.9812 | -0.21973 | 124.7177 | -0.050354 | 61.9812 | 124.5941 | 124.7635 | -125.0427 | -125.0198
1002.6406 | 125.0427 | -61.8164 | 63.0798 | -0.65895 | 0.011188 | 0.0091323 | 0.0049219 | 0.061626 | -0.0027131 | 0.067531 | -61.9446 | 62.9929 | -62.0865 | -61.9904 | 62.6907 | 0.068665 | 0.14191 | 0.15564 | 62.9974 | -62.0819 | -0.27008 | -0.086975 | -0.12817 | -0.17395 | -0.3891 | -0.2655 | -0.082397 | 0.14191 | 61.9583 | 61.972 | 124.5071 | 124.8093 | -0.12817 | 124.8138 | 61.8851 | -0.2655 | 124.8093 | -0.12817 | 61.8851 | 124.5071 | 124.8138 | -125.1663 | -125.1617
1003.6406 | 125.1297 | -61.7981 | 63.0341 | -0.056229 | 0.0060605 | 0.010841 | -0.0017005 | 0.063976 | 0.00027774 | 0.067103 | -61.9171 | 62.9105 | -62.0636 | -61.9629 | 62.7548 | 0.082397 | -0.059509 | 0.17853 | 62.9791 | -62.0407 | -0.2655 | -0.1236 | -0.11902 | -0.16479 | -0.27924 | -0.24261 | -0.054932 | 0.14649 | 61.7386 | 61.9766 | 124.5529 | 124.7086 | -0.11902 | 124.7772 | 61.8805 | -0.24261 | 124.7086 | -0.11902 | 61.8805 | 124.5529 | 124.7772 | -125.0977 | -125.0748
1004.6406 | 125.1434 | -61.7661 | 63.0157 | -0.048599 | 0.0064877 | 0.0078507 | -0.00020505 | 0.063121 | -0.0022859 | 0.069453 | -61.8759 | 62.915 | -62.0224 | -61.9354 | 62.7914 | 0.15564 | -0.091553 | 0.2243 | 62.97 | -62.0361 | -0.25635 | -0.10071 | -0.10986 | -0.16937 | -0.2243 | -0.27008 | -0.045776 | 0.14648 | 61.6745 | 61.9904 | 124.5575 | 124.6811 | -0.10986 | 124.736 | 61.9217 | -0.27008 | 124.6811 | -0.10986 | 61.9217 | 124.5575 | 124.736 | -125.0381 | -125.0519
1005.6406 | 125.1297 | -61.8027 | 63.0341 | -0.063858 | 0.0084103 | 0.0097733 | -0.0023413 | 0.06184 | -0.00014946 | 0.069239 | -61.8851 | 62.9242 | -62.0453 | -61.9492 | 62.7777 | 0.12817 | -0.068665 | 0.22888 | 62.9608 | -62.0361 | -0.24262 | -0.10986 | -0.082398 | -0.14648 | -0.25635 | -0.23346 | -0.073243 | 0.16022 | 61.734 | 62.0316 | 124.5804 | 124.7269 | -0.082398 | 124.7635 | 61.9308 | -0.23346 | 124.7269 | -0.082398 | 61.9308 | 124.5804 | 124.7635 | -125.0793 | -125.0702
1006.6406 | 125.1343 | -61.7889 | 63.0249 | -0.048599 | 0.0067013 | 0.0046463 | -0.0017005 | 0.060985 | 0.0015595 | 0.068599 | -61.8896 | 62.915 | -62.0499 | -61.9492 | 62.7594 | 0.10529 | -0.073242 | 0.21057 | 62.9425 | -62.0361 | -0.26093 | -0.10986 | -0.10071 | -0.16022 | -0.2655 | -0.24719 | -0.082397 | 0.16022 | 61.7157 | 61.9995 | 124.5483 | 124.704 | -0.10071 | 124.7314 | 61.8942 | -0.24719 | 124.704 | -0.10071 | 61.8942 | 124.5483 | 124.7314 | -125.0748 | -125.061
1007.6406 | 125.0656 | -61.8393 | 63.0707 | -0.0028231 | 0.0094785 | 0.0097733 | 0.0044945 | 0.062694 | -0.0010041 | 0.067744 | -61.9263 | 63.0157 | -62.0865 | -62.0041 | 62.6953 | 0.068665 | 0.14191 | 0.15564 | 63.0066 | -62.0773 | -0.24719 | -0.054932 | -0.086976 | -0.16479 | -0.37537 | -0.23804 | -0.064087 | 0.16022 | 61.9812 | 61.9949 | 124.5346 | 124.855 | -0.086976 | 124.8459 | 61.908 | -0.23804 | 124.855 | -0.086976 | 61.908 | 124.5346 | 124.8459 | -125.1572 | -125.148
1008.6406 | 125.1526 | -61.7935 | 63.0249 | -0.10201 | 0.0058469 | 0.013405 | -0.0046913 | 0.064617 | 0.0011321 | 0.068599 | -61.8805 | 62.9242 | -62.027 | -61.9125 | 62.7914 | 0.15564 | -0.082397 | 0.2243 | 62.9837 | -61.9949 | -0.23346 | -0.10071 | -0.086975 | -0.11902 | -0.23346 | -0.20142 | -0.041198 | 0.14648 | 61.7111 | 62.0178 | 124.585 | 124.7177 | -0.086975 | 124.7772 | 61.9492 | -0.20142 | 124.7177 | -0.086975 | 61.9492 | 124.585 | 124.7772 | -125.0519 | -125.0198
1009.6406 | 125.1022 | -61.7706 | 63.0249 | 0.18791 | 0.0090513 | 0.0084915 | -0.0012733 | 0.063121 | -0.0044221 | 0.070948 | -61.9034 | 62.915 | -62.0407 | -61.9583 | 62.7594 | 0.073242 | -0.073242 | 0.15564 | 62.97 | -62.027 | -0.27008 | -0.10986 | -0.13275 | -0.18768 | -0.2655 | -0.25635 | -0.054931 | 0.13733 | 61.6974 | 61.9263 | 124.53 | 124.6857 | -0.13275 | 124.7406 | 61.8439 | -0.25635 | 124.6857 | -0.13275 | 61.8439 | 124.53 | 124.7406 | -125.0656 | -125.0519
1010.6406 | 125.1114 | -61.7752 | 63.0478 | 0.54649 | 0.0086239 | 0.01191 | -0.00020505 | 0.063762 | -0.0016449 | 0.068599 | -61.9125 | 62.915 | -62.0407 | -61.9858 | 62.7274 | 0.064087 | -0.068665 | 0.14191 | 62.9654 | -61.9995 | -0.2655 | -0.13275 | -0.13733 | -0.21057 | -0.32043 | -0.2243 | -0.082398 | 0.12817 | 61.7065 | 61.9171 | 124.5026 | 124.6902 | -0.13733 | 124.7406 | 61.8393 | -0.2243 | 124.6902 | -0.13733 | 61.8393 | 124.5026 | 124.7406 | -125.0885 | -125.0473
1011.6406 | 125.1205 | -61.7981 | 63.0524 | 0.0048064 | 0.0084103 | 0.0080643 | -0.00063225 | 0.063335 | -0.0018585 | 0.067958 | -61.9034 | 62.9333 | -62.0407 | -61.9492 | 62.7686 | 0.09613 | -0.068665 | 0.20599 | 62.9379 | -62.0316 | -0.24261 | -0.11902 | -0.10529 | -0.15106 | -0.28381 | -0.23346 | -0.11444 | 0.13733 | 61.7294 | 62.0041 | 124.5667 | 124.7314 | -0.10529 | 124.736 | 61.8942 | -0.23346 | 124.7314 | -0.10529 | 61.8942 | 124.5667 | 124.736 | -125.0931 | -125.0839
1012.6406 | 125.029 | -61.8164 | 63.0798 | -0.51399 | 0.0090513 | 0.010841 | 0.0044945 | 0.060558 | -0.0016449 | 0.067531 | -61.9217 | 63.0249 | -62.0499 | -61.9766 | 62.7228 | 0.07782 | 0.11902 | 0.15564 | 63.0295 | -62.0682 | -0.23346 | -0.054932 | -0.10529 | -0.16022 | -0.35706 | -0.25177 | -0.050354 | 0.12817 | 61.9354 | 61.972 | 124.5392 | 124.8413 | -0.10529 | 124.8459 | 61.8942 | -0.25177 | 124.8413 | -0.10529 | 61.8942 | 124.5392 | 124.8459 | -125.1297 | -125.148
1013.6406 | 125.1343 | -61.7981 | 63.0249 | 0.027695 | 0.0073423 | 0.010414 | -0.0036231 | 0.063976 | -0.00036306 | 0.069453 | -61.9125 | 62.9242 | -62.0499 | -61.9629 | 62.764 | 0.073242 | -0.054932 | 0.16022 | 62.9837 | -62.0361 | -0.25177 | -0.10071 | -0.11444 | -0.16479 | -0.26093 | -0.23804 | -0.041198 | 0.13733 | 61.7432 | 61.9583 | 124.5621 | 124.7223 | -0.11444 | 124.7818 | 61.8713 | -0.23804 | 124.7223 | -0.11444 | 61.8713 | 124.5621 | 124.7818 | -125.0748 | -125.061
1014.6406 | 125.1801 | -61.7615 | 63.0203 | -0.11726 | 0.0090513 | 0.0067825 | -0.0021277 | 0.060985 | -0.0018585 | 0.070094 | -61.8805 | 62.9379 | -62.0178 | -61.9354 | 62.8006 | 0.1236 | -0.09613 | 0.21973 | 62.9654 | -62.0087 | -0.25635 | -0.082398 | -0.11902 | -0.17395 | -0.21973 | -0.24719 | -0.054932 | 0.13733 | 61.6653 | 61.9812 | 124.5621 | 124.6994 | -0.11902 | 124.7269 | 61.8851 | -0.24719 | 124.6994 | -0.11902 | 61.8851 | 124.5621 | 124.7269 | -125.0381 | -125.029
1015.6406 | 125.148 | -61.7752 | 63.0524 | -0.056229 | 0.0079831 | 0.010628 | -0.00041865 | 0.062481 | -0.0029267 | 0.068385 | -61.8713 | 62.9242 | -62.0132 | -61.9217 | 62.7777 | 0.12817 | -0.07782 | 0.21057 | 62.97 | -62.0178 | -0.23804 | -0.12817 | -0.09613 | -0.14648 | -0.27466 | -0.24261 | -0.082397 | 0.14191 | 61.6974 | 61.9858 | 124.5529 | 124.6994 | -0.09613 | 124.7452 | 61.9034 | -0.24261 | 124.6994 | -0.09613 | 61.9034 | 124.5529 | 124.7452 | -125.0656 | -125.0702
1016.6406 | 125.1205 | -61.7935 | 63.0249 | -0.46822 | 0.0090513 | 0.0099869 | -0.00063225 | 0.061626 | -0.00014946 | 0.071589 | -61.9354 | 62.9379 | -62.027 | -61.9812 | 62.7411 | 0.059509 | -0.068665 | 0.13275 | 62.97 | -62.0407 | -0.23346 | -0.086975 | -0.14191 | -0.18768 | -0.28381 | -0.24719 | -0.054931 | 0.091553 | 61.7249 | 61.9263 | 124.5346 | 124.7314 | -0.14191 | 124.7635 | 61.853 | -0.24719 | 124.7314 | -0.14191 | 61.853 | 124.5346 | 124.7635 | -125.0519 | -125.0656
1017.6406 | 125.148 | -61.7706 | 63.0615 | -0.056229 | 0.0079831 | 0.0095595 | -0.00084605 | 0.061626 | 0.00027774 | 0.06988 | -61.8805 | 62.915 | -62.0407 | -61.9675 | 62.7777 | 0.091553 | -0.07782 | 0.17853 | 62.9425 | -62.0224 | -0.27008 | -0.14648 | -0.10986 | -0.19684 | -0.28381 | -0.25177 | -0.11902 | 0.16022 | 61.6928 | 61.9492 | 124.5483 | 124.6857 | -0.10986 | 124.7131 | 61.8622 | -0.25177 | 124.6857 | -0.10986 | 61.8622 | 124.5483 | 124.7131 | -125.1022 | -125.0839
1018.6406 | 125.1343 | -61.7752 | 63.0569 | -0.04097 | 0.0086239 | 0.0082779 | -0.00084605 | 0.063762 | -0.00014946 | 0.069239 | -61.8805 | 62.9333 | -62.0499 | -61.94 | 62.7686 | 0.082397 | -0.09613 | 0.17395 | 62.9883 | -62.027 | -0.27466 | -0.1236 | -0.10529 | -0.16479 | -0.28839 | -0.25177 | -0.068665 | 0.16937 | 61.6791 | 61.9492 | 124.5438 | 124.7086 | -0.10529 | 124.7635 | 61.8576 | -0.25177 | 124.7086 | -0.10529 | 61.8576 | 124.5438 | 124.7635 | -125.1068 | -125.0839
1019.6562 | 125.0748 | -61.7981 | 63.0661 | -0.18593 | 0.0090513 | 0.0097733 | 0.0083397 | 0.064403 | -0.00036306 | 0.068812 | -61.8118 | 63.0478 | -61.9949 | -61.9263 | 62.7502 | 0.086975 | 0.018311 | 0.14191 | 63.0066 | -62.0728 | -0.19684 | -0.01831 | -0.013733 | -0.12817 | -0.31586 | -0.27466 | -0.059509 | 0.1831 | 61.8164 | 61.94 | 124.5483 | 124.8459 | -0.013733 | 124.8047 | 61.8851 | -0.27466 | 124.8459 | -0.013733 | 61.8851 | 124.5483 | 124.8047 | -125.061 | -125.1389
1020.6406 | 125.116 | -61.8118 | 63.0386 | -0.063858 | 0.0054197 | 0.0076369 | -0.0029823 | 0.063335 | -0.0010041 | 0.068599 | -61.9125 | 62.9196 | -62.0316 | -61.9446 | 62.764 | 0.054932 | -0.082397 | 0.12817 | 62.9883 | -62.027 | -0.21973 | -0.11902 | -0.10071 | -0.13275 | -0.27466 | -0.21515 | -0.050354 | 0.11902 | 61.7294 | 61.94 | 124.5758 | 124.7314 | -0.10071 | 124.8001 | 61.8668 | -0.21515 | 124.7314 | -0.10071 | 61.8668 | 124.5758 | 124.8001 | -125.0702 | -125.0656
1021.6406 | 125.148 | -61.7661 | 63.0524 | -0.094376 | 0.0084103 | 0.0076369 | -0.0021277 | 0.063121 | -0.0024995 | 0.06689 | -61.8713 | 62.9242 | -62.0316 | -61.9217 | 62.8098 | 0.10986 | -0.073242 | 0.20142 | 62.9562 | -62.0178 | -0.2655 | -0.12817 | -0.10529 | -0.15564 | -0.24262 | -0.25177 | -0.09613 | 0.16022 | 61.6928 | 61.9675 | 124.5758 | 124.6902 | -0.10529 | 124.7223 | 61.8759 | -0.25177 | 124.6902 | -0.10529 | 61.8759 | 124.5758 | 124.7223 | -125.0839 | -125.0702
1022.6406 | 125.116 | -61.7432 | 63.0341 | -0.04097 | 0.0071285 | 0.0074233 | -0.0025549 | 0.062053 | -0.00057686 | 0.06689 | -61.8668 | 62.915 | -62.027 | -61.9263 | 62.796 | 0.10071 | -0.086975 | 0.17395 | 62.9883 | -62.0041 | -0.28381 | -0.11902 | -0.1236 | -0.18311 | -0.23804 | -0.26093 | -0.045777 | 0.16022 | 61.6562 | 61.9171 | 124.5392 | 124.6582 | -0.1236 | 124.7314 | 61.8439 | -0.26093 | 124.6582 | -0.1236 | 61.8439 | 124.5392 | 124.7314 | -125.061 | -125.0381
1023.6406 | 125.0839 | -61.7569 | 63.0432 | -0.34615 | 0.0096921 | 0.011269 | 8.546e-06 | 0.063121 | -0.0016449 | 0.069453 | -61.908 | 62.9379 | -62.027 | -61.9492 | 62.7411 | 0.036621 | -0.07782 | 0.10071 | 62.9791 | -62.0224 | -0.27008 | -0.10529 | -0.15106 | -0.19226 | -0.30212 | -0.2655 | -0.064087 | 0.11902 | 61.6791 | 61.8576 | 124.498 | 124.6948 | -0.15106 | 124.736 | 61.7935 | -0.2655 | 124.6948 | -0.15106 | 61.7935 | 124.498 | 124.736 | -125.0702 | -125.0656
1024.6406 | 124.9649 | -61.7981 | 63.1348 | -0.27748 | 0.0088375 | 0.011269 | 0.0019311 | 0.063121 | 0.0011321 | 0.067103 | -61.8713 | 63.0295 | -62.0453 | -61.9766 | 62.7182 | 0.050354 | 0.10071 | 0.11444 | 63.0295 | -62.027 | -0.24719 | -0.10529 | -0.073242 | -0.17853 | -0.41656 | -0.22888 | -0.10529 | 0.17395 | 61.8988 | 61.9125 | 124.5163 | 124.8276 | -0.073242 | 124.8276 | 61.8484 | -0.22888 | 124.8276 | -0.073242 | 61.8484 | 124.5163 | 124.8276 | -125.1801 | -125.1617
1025.6406 | 125.1343 | -61.7615 | 63.0386 | -0.0028231 | 0.0067013 | 0.010628 | -0.0031959 | 0.063549 | -0.0020721 | 0.068599 | -61.8851 | 62.9105 | -62.0224 | -61.9446 | 62.764 | 0.059509 | -0.091553 | 0.13275 | 62.9883 | -62.0224 | -0.26093 | -0.12817 | -0.1236 | -0.18311 | -0.27466 | -0.26093 | -0.050354 | 0.13733 | 61.6699 | 61.8942 | 124.5255 | 124.6719 | -0.1236 | 124.7498 | 61.821 | -0.26093 | 124.6719 | -0.1236 | 61.821 | 124.5255 | 124.7498 | -125.061 | -125.061
1026.6406 | 125.1251 | -61.7523 | 63.0661 | -0.025711 | 0.0075559 | 0.0087051 | -0.0014869 | 0.061412 | -0.00014946 | 0.068385 | -61.8713 | 62.915 | -62.0407 | -61.9263 | 62.764 | 0.064087 | -0.10071 | 0.10986 | 62.9929 | -62.027 | -0.28839 | -0.15106 | -0.11902 | -0.17395 | -0.30212 | -0.27466 | -0.073242 | 0.16937 | 61.6516 | 61.8622 | 124.5163 | 124.6674 | -0.11902 | 124.7452 | 61.8164 | -0.27466 | 124.6674 | -0.11902 | 61.8164 | 124.5163 | 124.7452 | -125.1068 | -125.0931
1027.6406 | 125.1205 | -61.7569 | 63.0615 | -0.0028231 | 0.0077695 | 0.010841 | -0.0017005 | 0.062267 | -0.00014946 | 0.067531 | -61.8759 | 62.9333 | -62.0132 | -61.9537 | 62.7594 | 0.041199 | -0.10529 | 0.073242 | 62.9654 | -61.9949 | -0.25635 | -0.12817 | -0.11902 | -0.19684 | -0.30212 | -0.23804 | -0.09613 | 0.13733 | 61.6516 | 61.8301 | 124.5163 | 124.6902 | -0.11902 | 124.7223 | 61.7981 | -0.23804 | 124.6902 | -0.11902 | 61.7981 | 124.5163 | 124.7223 | -125.0748 | -125.0565
1028.6406 | 125.1709 | -61.7294 | 63.0524 | -0.04097 | 0.0079831 | 0.0091323 | -0.0021277 | 0.061626 | 0.0030547 | 0.068812 | -61.8484 | 62.9517 | -62.0041 | -61.908 | 62.796 | 0.091553 | -0.13275 | 0.13275 | 62.9837 | -62.0041 | -0.27466 | -0.10071 | -0.11902 | -0.17853 | -0.25635 | -0.27466 | -0.068664 | 0.15564 | 61.5967 | 61.8622 | 124.5255 | 124.6811 | -0.11902 | 124.7131 | 61.821 | -0.27466 | 124.6811 | -0.11902 | 61.821 | 124.5255 | 124.7131 | -125.0565 | -125.0565
1029.6562 | 125.0748 | -61.7477 | 63.1027 | -0.086746 | 0.011615 | 0.012123 | 0.0068445 | 0.065471 | -0.00079046 | 0.065608 | -61.7752 | 63.0661 | -61.9858 | -61.8896 | 62.7319 | 0.068665 | -0.036621 | 0.082397 | 63.0203 | -62.0499 | -0.23804 | -0.036621 | -0.027466 | -0.14191 | -0.37079 | -0.30212 | -0.082397 | 0.21057 | 61.7111 | 61.8301 | 124.4797 | 124.8138 | -0.027466 | 124.7681 | 61.8164 | -0.30212 | 124.8138 | -0.027466 | 61.8164 | 124.4797 | 124.7681 | -125.0885 | -125.1526
1030.6406 | 125.1068 | -61.7477 | 63.0432 | 1.0043 | 0.0081967 | 0.0087051 | -0.0038367 | 0.063549 | 0.00027774 | 0.069239 | -61.8622 | 62.9517 | -61.9949 | -61.9629 | 62.7594 | 0.013733 | -0.11444 | 0.022888 | 62.9791 | -61.9995 | -0.24719 | -0.091553 | -0.11444 | -0.21515 | -0.28381 | -0.25177 | -0.064087 | 0.13275 | 61.6333 | 61.7706 | 124.5071 | 124.6994 | -0.11444 | 124.7269 | 61.7615 | -0.25177 | 124.6994 | -0.11444 | 61.7615 | 124.5071 | 124.7269 | -125.0381 | -125.0427
1031.6406 | 125.1114 | -61.7661 | 63.0432 | 0.050583 | 0.0090513 | 0.0072097 | 0.0015039 | 0.062053 | -0.0022859 | 0.069667 | -61.972 | 62.9562 | -62.0041 | -61.9766 | 62.7686 | 0.018311 | -0.11444 | 0 | 62.9791 | -62.0178 | -0.23804 | -0.086975 | -0.20599 | -0.21057 | -0.27466 | -0.25177 | -0.064087 | 0.032043 | 61.6516 | 61.7661 | 124.5346 | 124.7223 | -0.20599 | 124.7452 | 61.7844 | -0.25177 | 124.7223 | -0.20599 | 61.7844 | 124.5346 | 124.7452 | -125.0473 | -125.061
1032.6406 | 125.0427 | -61.7615 | 63.0981 | -0.33089 | 0.010547 | 0.011269 | 0.0012903 | 0.063335 | 0.00027774 | 0.067958 | -61.8484 | 63.0295 | -62.0132 | -61.9446 | 62.764 | 0.045776 | 0.041199 | 0.041199 | 63.0524 | -62.0132 | -0.25177 | -0.068665 | -0.086975 | -0.18311 | -0.33417 | -0.25177 | -0.045777 | 0.16479 | 61.8027 | 61.8027 | 124.5255 | 124.791 | -0.086975 | 124.8138 | 61.8073 | -0.25177 | 124.791 | -0.086975 | 61.8073 | 124.5255 | 124.8138 | -125.1114 | -125.1114
1033.6406 | 125.116 | -61.7249 | 63.0661 | -0.010452 | 0.0086239 | 0.010628 | -0.00063225 | 0.063121 | -0.0016449 | 0.069026 | -61.8805 | 62.9791 | -62.0132 | -61.9308 | 62.764 | 0.027466 | -0.12817 | 0.009155 | 63.002 | -61.9949 | -0.28839 | -0.086975 | -0.15564 | -0.20599 | -0.30212 | -0.27008 | -0.064087 | 0.13275 | 61.5967 | 61.734 | 124.4888 | 124.704 | -0.15564 | 124.7269 | 61.7523 | -0.27008 | 124.704 | -0.15564 | 61.7523 | 124.4888 | 124.7269 | -125.0793 | -125.061
1034.6562 | 125.0473 | -61.7569 | 63.0707 | -0.89546 | 0.01076 | 0.010201 | 0.0062035 | 0.063976 | 6.414e-05 | 0.067744 | -61.8073 | 63.0661 | -62.0361 | -61.8988 | 62.7594 | 0.036621 | -0.054932 | -0.022888 | 63.0478 | -62.0316 | -0.27924 | -0.004578 | -0.050354 | -0.14191 | -0.31128 | -0.27466 | -0.022888 | 0.22888 | 61.702 | 61.734 | 124.5163 | 124.823 | -0.050354 | 124.8047 | 61.7935 | -0.27466 | 124.823 | -0.050354 | 61.7935 | 124.5163 | 124.8047 | -125.1068 | -125.1022
1035.6406 | 125.1068 | -61.7386 | 63.0432 | -0.071488 | 0.0079831 | 0.0093459 | -0.0029823 | 0.065044 | -0.0010041 | 0.070735 | -61.8576 | 62.9517 | -61.9995 | -61.908 | 62.796 | 0.07782 | -0.15106 | 0.041199 | 63.0249 | -61.9949 | -0.26093 | -0.091553 | -0.11902 | -0.16937 | -0.24719 | -0.25635 | -0.018311 | 0.14191 | 61.5875 | 61.7798 | 124.5346 | 124.6902 | -0.11902 | 124.7635 | 61.8164 | -0.25635 | 124.6902 | -0.11902 | 61.8164 | 124.5346 | 124.7635 | -125.0427 | -125.0381
1036.6406 | 125.1068 | -61.7432 | 63.0661 | -0.033341 | 0.0056333 | 0.011055 | -0.0046913 | 0.062267 | 0.00049134 | 0.069026 | -61.853 | 62.9517 | -61.9995 | -61.9034 | 62.796 | 0.036621 | -0.16937 | -0.004578 | 62.9883 | -61.9904 | -0.25635 | -0.11444 | -0.10986 | -0.16022 | -0.27008 | -0.24719 | -0.07782 | 0.14649 | 61.5738 | 61.7386 | 124.5392 | 124.6948 | -0.10986 | 124.7314 | 61.7798 | -0.24719 | 124.6948 | -0.10986 | 61.7798 | 124.5392 | 124.7314 | -125.0656 | -125.0565
1037.6406 | 125.1068 | -61.7111 | 63.089 | -3.1156 | 0.0069149 | 0.011482 | 0.0029993 | 0.061626 | -0.0016449 | 0.068599 | -62.0407 | 63.0066 | -61.9766 | -61.8713 | 62.8006 | 0.10986 | -0.14191 | 0.068665 | 62.9929 | -61.9675 | -0.2655 | -0.082397 | -0.32959 | -0.16022 | -0.28839 | -0.25635 | -0.09613 | -0.064086 | 61.5692 | 61.7798 | 124.5117 | 124.7177 | -0.32959 | 124.704 | 61.821 | -0.25635 | 124.7177 | -0.32959 | 61.821 | 124.5117 | 124.704 | -125.0656 | -125.0565
1038.6406 | 125.0198 | -61.7569 | 63.0707 | 0.10399 | 0.0092649 | 0.010841 | -0.00063225 | 0.063549 | -0.0012177 | 0.067958 | -61.8668 | 62.9517 | -62.0041 | -61.9492 | 62.7548 | -0.004578 | -0.19226 | 0.018311 | 63.0112 | -61.9949 | -0.24719 | -0.11902 | -0.10986 | -0.19226 | -0.31586 | -0.23804 | -0.05951 | 0.13733 | 61.5646 | 61.7752 | 124.5117 | 124.7086 | -0.10986 | 124.7681 | 61.7523 | -0.23804 | 124.7086 | -0.10986 | 61.7523 | 124.5117 | 124.7681 | -125.0748 | -125.0656
1039.6406 | 125.1068 | -61.7249 | 63.0661 | 0.012436 | 0.0086239 | 0.0084915 | -0.0019141 | 0.062267 | -0.0016449 | 0.070948 | -61.8622 | 62.9745 | -61.9858 | -61.9171 | 62.7731 | 0.004578 | -0.1831 | -0.10529 | 63.0157 | -61.9858 | -0.26093 | -0.091553 | -0.13733 | -0.19226 | -0.29297 | -0.26093 | -0.050354 | 0.1236 | 61.5417 | 61.6196 | 124.498 | 124.6994 | -0.13733 | 124.7406 | 61.7294 | -0.26093 | 124.6994 | -0.13733 | 61.7294 | 124.498 | 124.7406 | -125.0519 | -125.0519
1040.6406 | 125.1251 | -61.7294 | 63.0798 | -0.46059 | 0.0081967 | 0.01191 | -0.0019141 | 0.062694 | 6.414e-05 | 0.068171 | -61.9034 | 62.97 | -61.9766 | -61.9263 | 62.7411 | -0.013733 | -0.20599 | -0.15106 | 63.0341 | -61.972 | -0.24719 | -0.10986 | -0.17395 | -0.19684 | -0.33874 | -0.24262 | -0.045776 | 0.073243 | 61.5234 | 61.5784 | 124.4705 | 124.6994 | -0.17395 | 124.7635 | 61.7157 | -0.24262 | 124.6994 | -0.17395 | 61.7157 | 124.4705 | 124.7635 | -125.0565 | -125.0519
1041.6406 | 125.1114 | -61.7386 | 63.0936 | 0.12688 | 0.0069149 | 0.0074233 | -0.00041865 | 0.060344 | -0.0016449 | 0.070735 | -61.8439 | 62.9333 | -61.9858 | -61.9812 | 62.6999 | 0.013733 | -0.29297 | -0.15564 | 63.0112 | -61.9766 | -0.24719 | -0.16022 | -0.10529 | -0.24262 | -0.39368 | -0.23804 | -0.082398 | 0.14191 | 61.4456 | 61.5829 | 124.4385 | 124.6719 | -0.10529 | 124.7498 | 61.7523 | -0.23804 | 124.6719 | -0.10529 | 61.7523 | 124.4385 | 124.7498 | -125.0793 | -125.0702
1042.6406 | 125.0519 | -61.7157 | 63.121 | -0.24696 | 0.0088375 | 0.0067825 | 0.0015039 | 0.062481 | -0.0016449 | 0.069026 | -61.8027 | 63.002 | -61.9904 | -61.9171 | 62.7686 | 0.032043 | -0.059509 | -0.1236 | 63.0661 | -61.9629 | -0.27466 | -0.11902 | -0.086975 | -0.20142 | -0.35248 | -0.24719 | -0.054932 | 0.18768 | 61.6562 | 61.5921 | 124.4843 | 124.7177 | -0.086975 | 124.7818 | 61.7477 | -0.24719 | 124.7177 | -0.086975 | 61.7477 | 124.4843 | 124.7818 | -125.1114 | -125.0839
1043.6406 | 125.1114 | -61.7294 | 63.089 | -0.010452 | 0.0075559 | 0.0084915 | -0.0010597 | 0.063762 | -0.0014313 | 0.067531 | -61.8393 | 62.9883 | -62.0041 | -61.8942 | 62.7823 | 0.004578 | -0.24261 | -0.18768 | 63.0203 | -61.9537 | -0.27466 | -0.10071 | -0.10986 | -0.1648 | -0.3067 | -0.2243 | -0.068664 | 0.16479 | 61.4868 | 61.5417 | 124.5117 | 124.7177 | -0.10986 | 124.7498 | 61.734 | -0.2243 | 124.7177 | -0.10986 | 61.734 | 124.5117 | 124.7498 | -125.0931 | -125.0427
1044.6406 | 125.0839 | -61.734 | 63.0798 | 0.11925 | 0.0094785 | 0.0095595 | -0.00020505 | 0.062053 | -0.0014313 | 0.070521 | -61.8301 | 62.9562 | -61.9675 | -61.9354 | 62.7457 | -0.018311 | -0.31586 | -0.24261 | 62.9929 | -61.9949 | -0.23346 | -0.1236 | -0.09613 | -0.20142 | -0.33417 | -0.26093 | -0.086975 | 0.13733 | 61.4182 | 61.4914 | 124.4797 | 124.6902 | -0.09613 | 124.7269 | 61.7157 | -0.26093 | 124.6902 | -0.09613 | 61.7157 | 124.4797 | 124.7269 | -125.0473 | -125.0748
1045.6406 | 125.0793 | -61.7157 | 63.0707 | 0.16502 | 0.0099057 | 0.012123 | 0.0023583 | 0.062481 | -0.0010041 | 0.067744 | -61.7844 | 62.9333 | -61.9766 | -61.9125 | 62.7731 | 0 | -0.3067 | -0.25177 | 63.0203 | -61.9583 | -0.26093 | -0.13733 | -0.068665 | -0.19684 | -0.29755 | -0.24261 | -0.050354 | 0.19226 | 61.409 | 61.4639 | 124.4888 | 124.649 | -0.068665 | 124.736 | 61.7157 | -0.24261 | 124.649 | -0.068665 | 61.7157 | 124.4888 | 124.736 | -125.0473 | -125.029
1046.6406 | 125.0244 | -61.7157 | 63.0936 | 0.073471 | 0.010333 | 0.010628 | 0.00022215 | 0.062267 | 0.00027774 | 0.070094 | -61.8347 | 62.9562 | -61.9766 | -61.9217 | 62.764 | 0.004578 | -0.29297 | -0.28381 | 62.97 | -61.9858 | -0.26093 | -0.13733 | -0.11902 | -0.20599 | -0.32959 | -0.27008 | -0.1236 | 0.14191 | 61.4227 | 61.4319 | 124.4797 | 124.6719 | -0.11902 | 124.6857 | 61.7203 | -0.27008 | 124.6719 | -0.11902 | 61.7203 | 124.4797 | 124.6857 | -125.0702 | -125.0793
1047.6406 | 125.061 | -61.6882 | 63.1302 | -0.22408 | 0.0081967 | 0.012764 | -0.0019141 | 0.059917 | -0.00079046 | 0.068171 | -61.7569 | 63.0386 | -61.9537 | -61.853 | 62.8006 | 0.09613 | -0.17395 | -0.21973 | 63.0661 | -61.972 | -0.2655 | -0.091553 | -0.068665 | -0.16479 | -0.32959 | -0.28381 | -0.064087 | 0.19684 | 61.5143 | 61.4685 | 124.4888 | 124.7269 | -0.068665 | 124.7543 | 61.7844 | -0.28381 | 124.7269 | -0.068665 | 61.7844 | 124.4888 | 124.7543 | -125.0839 | -125.1022
1048.6406 | 125.1068 | -61.7157 | 63.0844 | 0.17265 | 0.0086239 | 0.0076369 | -0.00020505 | 0.063121 | 0.00049134 | 0.071162 | -61.8027 | 62.9837 | -61.9812 | -61.908 | 62.7686 | 0.009155 | -0.35248 | -0.36163 | 63.0341 | -61.9629 | -0.2655 | -0.10071 | -0.086975 | -0.19226 | -0.31586 | -0.24719 | -0.050354 | 0.17853 | 61.3632 | 61.3541 | 124.4843 | 124.6994 | -0.086975 | 124.7498 | 61.7249 | -0.24719 | 124.6994 | -0.086975 | 61.7249 | 124.4843 | 124.7498 | -125.0656 | -125.0473
1049.6406 | 125.0656 | -61.7294 | 63.0936 | 0.073471 | 0.0099057 | 0.012337 | -0.0023413 | 0.062481 | -0.0010041 | 0.067103 | -61.8118 | 62.9745 | -61.972 | -61.7386 | 62.8235 | -0.09613 | -0.31128 | -0.37994 | 62.9974 | -61.9675 | -0.24262 | -0.11902 | -0.082398 | -0.009155 | -0.27008 | -0.23804 | -0.09613 | 0.16022 | 61.4182 | 61.3495 | 124.5529 | 124.704 | -0.082398 | 124.7269 | 61.6333 | -0.23804 | 124.704 | -0.082398 | 61.6333 | 124.5529 | 124.7269 | -125.0656 | -125.061
1050.6406 | 125.1297 | -61.6928 | 63.0753 | 0.0048064 | 0.0067013 | 0.0091323 | 0.0012903 | 0.064617 | -0.0012177 | 0.066676 | -61.821 | 62.9974 | -61.9766 | -61.9034 | 62.7686 | 0.032043 | -0.36163 | -0.3891 | 63.0569 | -61.9492 | -0.28381 | -0.077819 | -0.12817 | -0.21057 | -0.3067 | -0.25635 | -0.01831 | 0.15564 | 61.3312 | 61.3037 | 124.4614 | 124.6902 | -0.12817 | 124.7498 | 61.7249 | -0.25635 | 124.6902 | -0.12817 | 61.7249 | 124.4614 | 124.7498 | -125.0519 | -125.0244
1051.6406 | 125.0931 | -61.7203 | 63.0661 | 0.18028 | 0.0096921 | 0.011696 | 0.00064935 | 0.063335 | -0.00057686 | 0.069667 | -61.7798 | 62.9608 | -61.9354 | -61.8576 | 62.7869 | 0.045776 | -0.4715 | -0.39368 | 63.002 | -61.9446 | -0.21515 | -0.10529 | -0.059509 | -0.13733 | -0.27924 | -0.2243 | -0.064087 | 0.15564 | 61.2488 | 61.3266 | 124.5071 | 124.6811 | -0.059509 | 124.7223 | 61.7661 | -0.2243 | 124.6811 | -0.059509 | 61.7661 | 124.5071 | 124.7223 | -125.0015 | -125.0107
1052.6406 | 125.1251 | -61.6791 | 63.089 | -0.048599 | 0.0079831 | 0.010628 | -0.00063225 | 0.062694 | 0.00070494 | 0.070094 | -61.7935 | 63.0112 | -61.9675 | -61.8393 | 62.8143 | 0.11444 | -0.41199 | -0.37079 | 63.0295 | -61.9583 | -0.28839 | -0.07782 | -0.11444 | -0.16022 | -0.27466 | -0.27924 | -0.059509 | 0.17395 | 61.2671 | 61.3083 | 124.4934 | 124.6902 | -0.11444 | 124.7086 | 61.7935 | -0.27924 | 124.6902 | -0.11444 | 61.7935 | 124.4934 | 124.7086 | -125.0565 | -125.0473
1053.6406 | 125.0931 | -61.702 | 63.089 | 0.14976 | 0.0099057 | 0.011482 | -0.0014869 | 0.064403 | -0.0012177 | 0.072017 | -61.7935 | 62.9654 | -61.9629 | -61.8896 | 62.7823 | 0.036621 | -0.44403 | -0.49439 | 63.0112 | -61.9446 | -0.26093 | -0.1236 | -0.091553 | -0.18768 | -0.3067 | -0.24262 | -0.07782 | 0.16937 | 61.2579 | 61.2076 | 124.4843 | 124.6674 | -0.091553 | 124.7131 | 61.7386 | -0.24262 | 124.6674 | -0.091553 | 61.7386 | 124.4843 | 124.7131 | -125.0519 | -125.0336
1054.6406 | 125.0885 | -61.702 | 63.0936 | 0.0811 | 0.0075559 | 0.0078507 | -0.00020505 | 0.06184 | 6.414e-05 | 0.067744 | -61.7706 | 62.97 | -61.9446 | -61.8942 | 62.7731 | 0.036621 | -0.48523 | -0.51727 | 62.9974 | -61.9675 | -0.24262 | -0.1236 | -0.068665 | -0.19226 | -0.32044 | -0.2655 | -0.09613 | 0.17395 | 61.2167 | 61.1847 | 124.4751 | 124.6719 | -0.068665 | 124.6994 | 61.7386 | -0.2655 | 124.6719 | -0.068665 | 61.7386 | 124.4751 | 124.6994 | -125.0381 | -125.061
1055.6406 | 125.0885 | -61.702 | 63.1027 | 0.0811 | 0.0088375 | 0.01191 | -0.0014869 | 0.06419 | -0.0012177 | 0.067531 | -61.7752 | 62.9974 | -61.9583 | -61.8759 | 62.7731 | 0.073242 | -0.50354 | -0.5127 | 63.0203 | -61.9492 | -0.25635 | -0.10529 | -0.073243 | -0.17395 | -0.32959 | -0.24719 | -0.082397 | 0.1831 | 61.1984 | 61.1893 | 124.4751 | 124.6994 | -0.073243 | 124.7223 | 61.7752 | -0.24719 | 124.6994 | -0.073243 | 61.7752 | 124.4751 | 124.7223 | -125.061 | -125.0519
1056.6406 | 125.0244 | -61.6882 | 63.1256 | 0.020065 | 0.0075559 | 0.0084915 | -0.00063225 | 0.06184 | 0.00027774 | 0.069453 | -61.821 | 63.0112 | -61.9446 | -61.8851 | 62.7914 | 0.068665 | -0.47607 | -0.54474 | 63.0341 | -61.9537 | -0.25635 | -0.11444 | -0.13275 | -0.19684 | -0.33417 | -0.2655 | -0.091552 | 0.1236 | 61.2122 | 61.1435 | 124.4797 | 124.6994 | -0.13275 | 124.7223 | 61.7569 | -0.2655 | 124.6994 | -0.13275 | 61.7569 | 124.4797 | 124.7223 | -125.0702 | -125.0793
1057.6406 | 125.1526 | -61.6882 | 63.1302 | -0.056229 | 0.0086239 | 0.0072097 | -0.0025549 | 0.062694 | -0.0018585 | 0.070094 | -61.7661 | 62.9974 | -61.9354 | -61.8439 | 62.8281 | 0.15106 | -0.48981 | -0.50812 | 63.0341 | -61.9629 | -0.24719 | -0.13275 | -0.07782 | -0.15564 | -0.30212 | -0.27466 | -0.09613 | 0.16937 | 61.1984 | 61.1801 | 124.5163 | 124.6857 | -0.07782 | 124.7223 | 61.8393 | -0.27466 | 124.6857 | -0.07782 | 61.8393 | 124.5163 | 124.7223 | -125.0656 | -125.0931
1058.6406 | 125.0931 | -61.702 | 63.0936 | 0.16502 | 0.0081967 | 0.013191 | 0.0010767 | 0.063976 | -0.0014313 | 0.068385 | -61.7432 | 62.9974 | -61.9537 | -61.8439 | 62.8006 | 0.11444 | -0.60425 | -0.5722 | 63.0249 | -61.9583 | -0.25177 | -0.09613 | -0.041199 | -0.14191 | -0.29297 | -0.25635 | -0.068665 | 0.21057 | 61.0977 | 61.1298 | 124.5026 | 124.6994 | -0.041199 | 124.7269 | 61.8164 | -0.25635 | 124.6994 | -0.041199 | 61.8164 | 124.5026 | 124.7269 | -125.0473 | -125.0519
1059.6406 | 125.1251 | -61.6745 | 63.0936 | 0.15739 | 0.0075559 | 0.011269 | 0.0017175 | 0.063976 | -0.0010041 | 0.067531 | -61.7432 | 62.9883 | -61.94 | -61.821 | 62.8098 | 0.15106 | -0.64087 | -0.57678 | 63.0249 | -61.9583 | -0.2655 | -0.10529 | -0.068664 | -0.14648 | -0.28381 | -0.28381 | -0.068665 | 0.19684 | 61.0336 | 61.0977 | 124.4843 | 124.6628 | -0.068664 | 124.6994 | 61.8256 | -0.28381 | 124.6628 | -0.068664 | 61.8256 | 124.4843 | 124.6994 | -125.0336 | -125.0519
1060.6406 | 125.0839 | -61.6653 | 63.1073 | 0.10399 | 0.010333 | 0.011482 | 0.00086295 | 0.06419 | -0.0016449 | 0.06689 | -61.7661 | 62.9929 | -61.9446 | -61.8622 | 62.7869 | 0.11902 | -0.59967 | -0.63629 | 63.0569 | -61.9125 | -0.27924 | -0.11444 | -0.10071 | -0.19684 | -0.32044 | -0.24719 | -0.050354 | 0.17853 | 61.0657 | 61.0291 | 124.4522 | 124.6582 | -0.10071 | 124.7223 | 61.7844 | -0.24719 | 124.6582 | -0.10071 | 61.7844 | 124.4522 | 124.7223 | -125.0519 | -125.0198
1061.6406 | 125.0885 | -61.6745 | 63.0753 | 0.065841 | 0.0092649 | 0.011482 | 0.0021447 | 0.063121 | -0.00057686 | 0.069667 | -61.7386 | 63.0112 | -61.9263 | -61.8576 | 62.7914 | 0.14191 | -0.63629 | -0.61798 | 63.0112 | -61.9308 | -0.25177 | -0.064087 | -0.064086 | -0.1831 | -0.28381 | -0.25635 | -0.064087 | 0.18768 | 61.0382 | 61.0565 | 124.4659 | 124.6857 | -0.064086 | 124.6857 | 61.8164 | -0.25635 | 124.6857 | -0.064086 | 61.8164 | 124.4659 | 124.6857 | -125.0015 | -125.0061
1062.6562 | 125.0198 | -61.7065 | 63.1622 | -0.2317 | 0.0084103 | 0.01191 | 0.00064935 | 0.06419 | -0.0024995 | 0.06988 | -61.7981 | 63.1165 | -61.9263 | -61.9446 | 62.8555 | 0.35248 | -0.54932 | -0.79193 | 63.1073 | -61.9766 | -0.21973 | -0.045776 | -0.091553 | -0.23804 | -0.3067 | -0.27008 | -0.054931 | 0.12817 | 61.1572 | 60.9146 | 124.5621 | 124.823 | -0.091553 | 124.8138 | 62.059 | -0.27008 | 124.823 | -0.091553 | 62.059 | 124.5621 | 124.8138 | -125.0885 | -125.1389
1063.6406 | 125.0885 | -61.6882 | 63.121 | 0.10399 | 0.011188 | 0.0087051 | 0.0012903 | 0.06419 | -0.0014313 | 0.06988 | -61.7706 | 63.002 | -61.9446 | -61.853 | 62.796 | 0.14648 | -0.65002 | -0.69122 | 63.0569 | -61.9171 | -0.25635 | -0.11902 | -0.082398 | -0.16479 | -0.32501 | -0.22888 | -0.064087 | 0.17395 | 61.0382 | 60.997 | 124.4843 | 124.6902 | -0.082398 | 124.7452 | 61.8347 | -0.22888 | 124.6902 | -0.082398 | 61.8347 | 124.4843 | 124.7452 | -125.0656 | -125.0381
1064.6406 | 125.1251 | -61.6837 | 63.1165 | 0.11925 | 0.0081967 | 0.011696 | 0.0017175 | 0.064403 | -0.0010041 | 0.070094 | -61.7477 | 63.0112 | -61.9125 | -61.8484 | 62.8006 | 0.17853 | -0.68207 | -0.70038 | 63.0478 | -61.9308 | -0.22888 | -0.10529 | -0.064087 | -0.16479 | -0.31586 | -0.24719 | -0.068664 | 0.16479 | 61.0016 | 60.9833 | 124.4843 | 124.6948 | -0.064087 | 124.7314 | 61.8622 | -0.24719 | 124.6948 | -0.064087 | 61.8622 | 124.4843 | 124.7314 | -125.029 | -125.0473
1065.6406 | 125.1389 | -61.6425 | 63.1165 | -0.37666 | 0.0090513 | 0.0087051 | 0.0034265 | 0.063549 | -0.0012177 | 0.06988 | -61.7477 | 63.0386 | -61.9125 | -61.8484 | 62.8143 | 0.20599 | -0.71411 | -0.67749 | 63.0203 | -61.94 | -0.27008 | -0.07782 | -0.10529 | -0.20599 | -0.30212 | -0.29755 | -0.09613 | 0.16479 | 60.9283 | 60.965 | 124.4568 | 124.6811 | -0.10529 | 124.6628 | 61.8484 | -0.29755 | 124.6811 | -0.10529 | 61.8484 | 124.4568 | 124.6628 | -125.029 | -125.0565
1066.6406 | 125.116 | -61.6608 | 63.1027 | 0.17265 | 0.0099057 | 0.010841 | 0.0062035 | 0.06419 | -0.0012177 | 0.069026 | -61.7065 | 63.0432 | -61.9171 | -62.0407 | 62.851 | 0.33417 | -0.70496 | -0.68207 | 63.0478 | -61.9308 | -0.25635 | -0.059509 | -0.045776 | -0.37994 | -0.25177 | -0.27008 | -0.054931 | 0.21057 | 60.9558 | 60.9787 | 124.5117 | 124.704 | -0.045776 | 124.7086 | 61.9949 | -0.27008 | 124.704 | -0.045776 | 61.9949 | 124.5117 | 124.7086 | -125.0198 | -125.0336
1067.6406 | 125.0931 | -61.6241 | 63.1531 | -0.018082 | 0.0086239 | 0.0089187 | -0.00063225 | 0.062481 | -0.00079046 | 0.068812 | -61.7798 | 63.0386 | -61.908 | -61.8484 | 62.8098 | 0.24261 | -0.62256 | -0.6958 | 63.089 | -61.9263 | -0.28381 | -0.11444 | -0.15564 | -0.2243 | -0.34332 | -0.30212 | -0.064087 | 0.12817 | 61.0016 | 60.9283 | 124.4339 | 124.6628 | -0.15564 | 124.7131 | 61.8668 | -0.30212 | 124.6628 | -0.15564 | 61.8668 | 124.4339 | 124.7131 | -125.061 | -125.0793
1068.6406 | 125.1251 | -61.6516 | 63.0981 | 0.16502 | 0.01076 | 0.013619 | 0.0042809 | 0.063121 | 0.00027774 | 0.068171 | -61.8759 | 63.0249 | -61.8988 | -61.8256 | 62.8326 | 0.30212 | -0.75531 | -0.72327 | 63.0478 | -61.9308 | -0.24719 | -0.073243 | -0.2243 | -0.17395 | -0.2655 | -0.27924 | -0.050354 | 0.022888 | 60.8963 | 60.9283 | 124.4843 | 124.6765 | -0.2243 | 124.6994 | 61.9537 | -0.27924 | 124.6765 | -0.2243 | 61.9537 | 124.4843 | 124.6994 | -124.9969 | -125.029
1069.6406 | 125.1022 | -61.6837 | 63.0981 | 0.17265 | 0.0096921 | 0.0095595 | 0.00064935 | 0.06419 | -0.0012177 | 0.068385 | -61.7157 | 63.0524 | -61.9217 | -61.8118 | 62.8143 | 0.29297 | -0.76446 | -0.71411 | 63.0569 | -61.9171 | -0.23804 | -0.045777 | -0.032043 | -0.12817 | -0.28381 | -0.23346 | -0.041199 | 0.20599 | 60.9192 | 60.9695 | 124.498 | 124.736 | -0.032043 | 124.7406 | 61.9766 | -0.23346 | 124.736 | -0.032043 | 61.9766 | 124.498 | 124.7406 | -125.0198 | -125.0153
1070.6406 | 125.1434 | -61.6653 | 63.0981 | -0.20119 | 0.011615 | 0.011055 | 0.0032129 | 0.062908 | -0.0020721 | 0.06988 | -61.7111 | 63.0844 | -61.908 | -61.8164 | 62.8006 | 0.31586 | -0.75989 | -0.70953 | 63.0569 | -61.9537 | -0.24262 | -0.013733 | -0.045777 | -0.15106 | -0.29755 | -0.28839 | -0.041199 | 0.19684 | 60.9055 | 60.9558 | 124.4659 | 124.7498 | -0.045777 | 124.7223 | 61.9812 | -0.28839 | 124.7498 | -0.045777 | 61.9812 | 124.4659 | 124.7223 | -125.0061 | -125.0519
1071.6406 | 125.1068 | -61.6287 | 63.121 | 0.2108 | 0.0090513 | 0.016182 | 0.0038537 | 0.063121 | -0.0012177 | 0.069453 | -61.702 | 63.0707 | -61.9217 | -61.8118 | 62.8098 | 0.42114 | -1.0391 | -0.88806 | 63.0341 | -61.9583 | -0.29297 | -0.050354 | -0.073242 | -0.18311 | -0.31128 | -0.32959 | -0.086975 | 0.21973 | 60.5896 | 60.7407 | 124.4385 | 124.6994 | -0.073242 | 124.6628 | 62.0499 | -0.32959 | 124.6994 | -0.073242 | 62.0499 | 124.4385 | 124.6628 | -125.0427 | -125.0793
1072.6406 | 125.0885 | -61.647 | 63.1485 | 0.065841 | 0.0086239 | 0.0048599 | -0.0023413 | 0.063121 | -0.00036306 | 0.070308 | -61.7752 | 63.0569 | -61.8988 | -61.8256 | 62.8006 | 0.33417 | -0.63171 | -0.70496 | 63.0844 | -61.9125 | -0.25177 | -0.091553 | -0.12817 | -0.17853 | -0.3479 | -0.2655 | -0.064087 | 0.1236 | 61.0153 | 60.9421 | 124.4476 | 124.704 | -0.12817 | 124.7314 | 61.9812 | -0.2655 | 124.704 | -0.12817 | 61.9812 | 124.4476 | 124.7314 | -125.0473 | -125.061
1073.6406 | 125.0885 | -61.6699 | 63.1393 | 0.19554 | 0.010333 | 0.010628 | 0.0053491 | 0.063335 | -0.0010041 | 0.069453 | -61.7523 | 63.1027 | -61.9217 | -61.8576 | 62.7594 | 0.27924 | -0.67291 | -0.79193 | 63.0707 | -61.9446 | -0.25177 | -0.036621 | -0.082397 | -0.18768 | -0.37994 | -0.27466 | -0.068664 | 0.16937 | 60.997 | 60.878 | 124.4293 | 124.7726 | -0.082397 | 124.7406 | 61.9492 | -0.27466 | 124.7726 | -0.082397 | 61.9492 | 124.4293 | 124.7406 | -125.061 | -125.0839
1074.6406 | 125.0702 | -61.6653 | 63.1439 | 0.14976 | 0.011615 | 0.012764 | 0.0057763 | 0.065044 | -0.00079046 | 0.071162 | -61.7523 | 63.1577 | -61.9217 | -61.8713 | 62.7319 | 0.28839 | -0.60883 | -0.77362 | 63.1302 | -61.9675 | -0.25635 | 0.013733 | -0.086975 | -0.20599 | -0.41199 | -0.30212 | -0.013733 | 0.16937 | 61.0565 | 60.8917 | 124.3973 | 124.823 | -0.086975 | 124.7955 | 61.9537 | -0.30212 | 124.823 | -0.086975 | 61.9537 | 124.3973 | 124.7955 | -125.0656 | -125.1114
1075.6406 | 125.029 | -61.6928 | 63.1531 | 0.18028 | 0.011188 | 0.016396 | 0.0057763 | 0.065471 | -0.00014946 | 0.06988 | -61.7615 | 63.1805 | -61.9308 | -61.8759 | 62.7228 | 0.29755 | -0.56763 | -0.78735 | 63.1485 | -61.9629 | -0.23804 | 0.027466 | -0.068665 | -0.18311 | -0.4303 | -0.27008 | -0.004577 | 0.16937 | 61.1252 | 60.9055 | 124.4156 | 124.8734 | -0.068665 | 124.8413 | 61.9904 | -0.27008 | 124.8734 | -0.068665 | 61.9904 | 124.4156 | 124.8413 | -125.0839 | -125.116
1076.6406 | 125.0473 | -61.6653 | 63.1393 | 0.18791 | 0.012256 | 0.013832 | 0.0042809 | 0.066753 | -0.00057686 | 0.06988 | -61.7477 | 63.1302 | -61.9125 | -61.8668 | 62.7411 | 0.37537 | -0.6134 | -0.73242 | 63.1256 | -61.9492 | -0.24719 | -0.009155 | -0.082398 | -0.20142 | -0.39825 | -0.28381 | -0.013733 | 0.16479 | 61.0519 | 60.9329 | 124.4064 | 124.7955 | -0.082398 | 124.791 | 62.0407 | -0.28381 | 124.7955 | -0.082398 | 62.0407 | 124.4064 | 124.791 | -125.0519 | -125.0885
1077.6406 | 125.1251 | -61.6379 | 63.1439 | -0.086746 | 0.0090513 | 0.01255 | -0.0049049 | 0.06419 | -0.0016449 | 0.071376 | -61.702 | 63.0844 | -61.8942 | -61.7752 | 62.8738 | 0.54932 | -0.59509 | -0.48065 | 63.1073 | -61.8805 | -0.25635 | -0.059509 | -0.064087 | -0.13733 | -0.27008 | -0.24262 | -0.036621 | 0.19226 | 61.0428 | 61.1572 | 124.5117 | 124.7223 | -0.064087 | 124.7452 | 62.1872 | -0.24262 | 124.7223 | -0.064087 | 62.1872 | 124.5117 | 124.7452 | -125.0381 | -125.0244
1078.6406 | 125.0565 | -61.6745 | 63.1668 | 0.13451 | 0.010547 | 0.011269 | 0.0057763 | 0.06483 | -0.0027131 | 0.068812 | -61.734 | 63.1714 | -61.8942 | -61.8988 | 62.7182 | 0.42114 | -0.51727 | -0.70038 | 63.1393 | -61.9492 | -0.21973 | 0.004578 | -0.059509 | -0.2243 | -0.44861 | -0.27466 | -0.027466 | 0.16022 | 61.1572 | 60.9741 | 124.3927 | 124.8459 | -0.059509 | 124.8138 | 62.0956 | -0.27466 | 124.8459 | -0.059509 | 62.0956 | 124.3927 | 124.8138 | -125.061 | -125.116
1079.6406 | 124.9878 | -61.6699 | 63.1897 | 0.020065 | 0.015246 | 0.015968 | 0.0072717 | 0.065899 | -0.00036306 | 0.067317 | -61.734 | 63.1943 | -61.8851 | -61.8622 | 62.7045 | 0.43488 | -0.4715 | -0.68665 | 63.1805 | -61.9492 | -0.21515 | 0.004578 | -0.064087 | -0.19226 | -0.48523 | -0.27924 | -0.009155 | 0.15106 | 61.1984 | 60.9833 | 124.3744 | 124.8642 | -0.064087 | 124.8505 | 62.1048 | -0.27924 | 124.8642 | -0.064087 | 62.1048 | 124.3744 | 124.8505 | -125.0748 | -125.1389
1080.6406 | 125.0061 | -61.6653 | 63.2217 | 0.10399 | 0.010119 | 0.01191 | 0.0051355 | 0.069316 | 0.00091854 | 0.067103 | -61.7661 | 63.1897 | -61.908 | -61.6058 | 62.8647 | 0.40741 | -0.40283 | -0.63171 | 63.1668 | -61.9583 | -0.24262 | -0.032044 | -0.10071 | 0.059509 | -0.35706 | -0.29297 | -0.054932 | 0.14191 | 61.2625 | 61.0336 | 124.53 | 124.855 | -0.10071 | 124.8322 | 62.0728 | -0.29297 | 124.855 | -0.10071 | 62.0728 | 124.53 | 124.8322 | -125.1297 | -125.1801
1081.6406 | 124.8322 | -61.6837 | 63.1348 | 0.0811 | 0.012042 | 0.015328 | 0.0055627 | 0.070171 | -0.0027131 | 0.070948 | -61.7386 | 63.1989 | -61.8988 | -61.908 | 62.7136 | 0.46692 | -0.46234 | -0.71869 | 63.1485 | -61.9354 | -0.21515 | 0.064087 | -0.054931 | -0.2243 | -0.42114 | -0.25177 | 0.013733 | 0.16022 | 61.2213 | 60.965 | 124.3973 | 124.8825 | -0.054931 | 124.8322 | 62.1506 | -0.25177 | 124.8825 | -0.054931 | 62.1506 | 124.3973 | 124.8322 | -125.0336 | -125.0702
1082.6406 | 125.0748 | -61.615 | 63.1439 | 0.08873 | 0.0058469 | 0.011269 | -0.0021277 | 0.065899 | -0.0024995 | 0.069667 | -61.7157 | 63.0981 | -61.9217 | -61.8256 | 62.8052 | 0.59509 | -0.65002 | -0.59509 | 63.1302 | -61.8668 | -0.3067 | -0.045776 | -0.10071 | -0.21057 | -0.33874 | -0.25177 | -0.013733 | 0.20599 | 60.965 | 61.0199 | 124.4202 | 124.7131 | -0.10071 | 124.7452 | 62.2101 | -0.25177 | 124.7131 | -0.10071 | 62.2101 | 124.4202 | 124.7452 | -125.0656 | -125.0107
1083.6406 | 124.9969 | -61.6287 | 63.1851 | 0.096359 | 0.010547 | 0.013832 | 0.0051355 | 0.066967 | -0.0014313 | 0.068385 | -61.5646 | 63.1943 | -61.8988 | -61.8622 | 62.6999 | 0.53558 | -0.5127 | -0.66834 | 63.1714 | -61.9675 | -0.27008 | 0.009155 | 0.064087 | -0.23346 | -0.48523 | -0.33874 | -0.013733 | 0.33417 | 61.116 | 60.9604 | 124.3286 | 124.823 | 0.064087 | 124.8001 | 62.1643 | -0.33874 | 124.823 | 0.064087 | 62.1643 | 124.3286 | 124.8001 | -125.0839 | -125.1526
1084.6406 | 125.0015 | -61.647 | 63.1851 | 0.0811 | 0.011401 | 0.015968 | 0.0034265 | 0.069103 | -0.0027131 | 0.06689 | -61.7523 | 63.1805 | -61.8988 | -61.6333 | 62.7548 | 0.48981 | -0.37537 | -0.62256 | 63.1851 | -61.9446 | -0.25177 | -0.004578 | -0.10529 | 0.013733 | -0.4303 | -0.29755 | 0 | 0.14648 | 61.2717 | 61.0245 | 124.4019 | 124.8276 | -0.10529 | 124.8322 | 62.1368 | -0.29755 | 124.8276 | -0.10529 | 62.1368 | 124.4019 | 124.8322 | -125.0839 | -125.1297
1085.6406 | 125.0061 | -61.6379 | 63.2034 | 0.050583 | 0.013965 | 0.013832 | 0.0047081 | 0.066539 | 0.00070494 | 0.069453 | -61.6928 | 63.1897 | -61.908 | -61.853 | 62.7411 | 0.62714 | -0.50812 | -0.62256 | 63.1622 | -61.9308 | -0.27008 | -0.013733 | -0.054932 | -0.21515 | -0.46234 | -0.29297 | -0.041199 | 0.21515 | 61.1298 | 61.0153 | 124.379 | 124.8276 | -0.054932 | 124.8001 | 62.265 | -0.29297 | 124.8276 | -0.054932 | 62.265 | 124.379 | 124.8001 | -125.1114 | -125.1343
1086.6406 | 125.0153 | -61.6699 | 63.1943 | 0.020065 | 0.011188 | 0.012764 | 0.0042809 | 0.069316 | -0.00014946 | 0.069453 | -61.6928 | 63.2309 | -61.8851 | -61.8393 | 62.7365 | 0.67291 | -0.50812 | -0.59967 | 63.1805 | -61.9308 | -0.21515 | 0.036621 | -0.022888 | -0.16937 | -0.45776 | -0.26093 | -0.013733 | 0.19226 | 61.1618 | 61.0703 | 124.4064 | 124.9008 | -0.022888 | 124.8505 | 62.3428 | -0.26093 | 124.9008 | -0.022888 | 62.3428 | 124.4064 | 124.8505 | -125.0793 | -125.1251
1087.6406 | 125.1434 | -61.6058 | 63.1439 | 0.17265 | 0.0099057 | 0.0149 | -0.0014869 | 0.068248 | -0.0020721 | 0.06988 | -61.6653 | 63.121 | -61.9034 | -61.7981 | 62.8098 | 0.78278 | -0.72784 | -0.52185 | 63.1256 | -61.8851 | -0.29755 | -0.022888 | -0.059509 | -0.19226 | -0.33417 | -0.27924 | -0.018311 | 0.23804 | 60.878 | 61.084 | 124.4156 | 124.7269 | -0.059509 | 124.7314 | 62.3886 | -0.27924 | 124.7269 | -0.059509 | 62.3886 | 124.4156 | 124.7314 | -125.0473 | -125.029
1088.6406 | 125.0153 | -61.6562 | 63.208 | 0.012436 | 0.011188 | 0.013191 | 0.0053491 | 0.067608 | 0.00027774 | 0.06988 | -61.7111 | 63.2217 | -61.8896 | -61.8576 | 62.7319 | 0.72327 | -0.49896 | -0.61798 | 63.1943 | -61.9354 | -0.23346 | 0.013733 | -0.054932 | -0.20142 | -0.47607 | -0.27924 | -0.013733 | 0.17853 | 61.1572 | 61.0382 | 124.3881 | 124.8779 | -0.054932 | 124.8505 | 62.3795 | -0.27924 | 124.8779 | -0.054932 | 62.3795 | 124.3881 | 124.8505 | -125.0977 | -125.1434
1089.6406 | 125.0381 | -61.6425 | 63.1943 | 0.0811 | 0.011615 | 0.015114 | 0.0044945 | 0.066753 | -0.0020721 | 0.070094 | -61.6928 | 63.2126 | -61.8713 | -61.8668 | 62.7411 | 0.76904 | -0.52185 | -0.64545 | 63.1805 | -61.9171 | -0.22888 | 0.01831 | -0.050354 | -0.2243 | -0.45319 | -0.27466 | -0.013733 | 0.17853 | 61.1206 | 60.997 | 124.3835 | 124.855 | -0.050354 | 124.823 | 62.4115 | -0.27466 | 124.855 | -0.050354 | 62.4115 | 124.3835 | 124.823 | -125.0656 | -125.1114
1090.6406 | 124.9969 | -61.6379 | 63.1943 | 0.0811 | 0.01311 | 0.011482 | 0.0047081 | 0.068889 | 0.0036957 | 0.074366 | -61.734 | 63.208 | -61.8896 | -62.1643 | 62.764 | 1.03 | -0.60425 | -0.65002 | 63.1943 | -61.9217 | -0.25177 | 0.013733 | -0.096131 | -0.52643 | -0.4303 | -0.28381 | 0 | 0.15564 | 61.0336 | 60.9879 | 124.4019 | 124.8459 | -0.096131 | 124.8322 | 62.6678 | -0.28381 | 124.8459 | -0.096131 | 62.6678 | 124.4019 | 124.8322 | -125.0839 | -125.116
1091.6406 | 125.0977 | -61.6379 | 63.2217 | 0.08873 | 0.010974 | 0.011055 | 0.0038537 | 0.068462 | -0.0016449 | 0.070094 | -61.7386 | 63.1989 | -61.8896 | -61.8988 | 62.6816 | 0.81482 | -0.68665 | -1.0941 | 63.1668 | -61.972 | -0.25177 | -0.022888 | -0.10071 | -0.26093 | -0.54016 | -0.33417 | -0.054932 | 0.15106 | 60.9512 | 60.5438 | 124.3195 | 124.8367 | -0.10071 | 124.8047 | 62.4527 | -0.33417 | 124.8367 | -0.10071 | 62.4527 | 124.3195 | 124.8047 | -125.1114 | -125.1938
1092.6406 | 125.0977 | -61.6013 | 63.1668 | 0.012436 | 0.0084103 | 0.012764 | -0.0061865 | 0.06718 | -0.00057686 | 0.071803 | -61.734 | 63.1073 | -61.8622 | -61.8301 | 62.796 | 0.95215 | -0.65002 | -0.52643 | 63.1622 | -61.8805 | -0.26093 | -0.059509 | -0.13275 | -0.22888 | -0.37079 | -0.27924 | -0.004578 | 0.12817 | 60.9512 | 61.0748 | 124.3973 | 124.7086 | -0.13275 | 124.7635 | 62.5534 | -0.27924 | 124.7086 | -0.13275 | 62.5534 | 124.3973 | 124.7635 | -125.029 | -125.0473
1093.6406 | 125.0198 | -61.647 | 63.2034 | 0.0048064 | 0.011401 | 0.016609 | 0.0044945 | 0.066753 | -0.0010041 | 0.068599 | -61.6562 | 63.2355 | -61.8805 | -61.8164 | 62.7274 | 0.92468 | -0.58594 | -0.59509 | 63.1851 | -61.9308 | -0.23346 | 0.032044 | -0.009155 | -0.16937 | -0.47607 | -0.28381 | -0.01831 | 0.2243 | 61.0611 | 61.0519 | 124.3744 | 124.8825 | -0.009155 | 124.8322 | 62.5717 | -0.28381 | 124.8825 | -0.009155 | 62.5717 | 124.3744 | 124.8322 | -125.0839 | -125.1343
1094.6406 | 124.9832 | -61.647 | 63.2217 | 0.042953 | 0.0090513 | 0.017037 | 0.0051355 | 0.067608 | -0.0029267 | 0.067317 | -61.702 | 63.2172 | -61.8668 | -61.8622 | 62.6999 | 0.92468 | -0.55847 | -0.66376 | 63.208 | -61.9446 | -0.21973 | -0.004578 | -0.054931 | -0.21515 | -0.52185 | -0.29755 | -0.013733 | 0.16479 | 61.0886 | 60.9833 | 124.3469 | 124.8642 | -0.054931 | 124.855 | 62.5717 | -0.29755 | 124.8642 | -0.054931 | 62.5717 | 124.3469 | 124.855 | -125.0885 | -125.1663
1095.6406 | 124.9649 | -61.6516 | 63.2263 | 0.096359 | 0.010974 | 0.015968 | 0.0036401 | 0.068035 | -0.0027131 | 0.06689 | -61.6974 | 63.1943 | -61.8896 | -61.8484 | 62.709 | 0.96588 | -0.55847 | -0.67291 | 63.1805 | -61.9446 | -0.23804 | -0.032043 | -0.045777 | -0.19684 | -0.51727 | -0.29297 | -0.045776 | 0.19226 | 61.0931 | 60.9787 | 124.3607 | 124.8459 | -0.045777 | 124.8322 | 62.6175 | -0.29297 | 124.8459 | -0.045777 | 62.6175 | 124.3607 | 124.8322 | -125.116 | -125.1709
1096.6406 | 124.9786 | -61.6379 | 63.2263 | 0.065841 | 0.01311 | 0.0149 | 0.0029993 | 0.067821 | 0.0028411 | 0.069026 | -61.6837 | 63.2126 | -61.8713 | -61.8484 | 62.709 | 1.0025 | -0.55847 | -0.68207 | 63.208 | -61.9354 | -0.23346 | -0.013733 | -0.045777 | -0.21057 | -0.51727 | -0.29755 | -0.01831 | 0.18768 | 61.0794 | 60.9558 | 124.3469 | 124.8505 | -0.045777 | 124.8459 | 62.6404 | -0.29755 | 124.8505 | -0.045777 | 62.6404 | 124.3469 | 124.8459 | -125.0977 | -125.1617
1097.6562 | 125.1114 | -61.5875 | 63.1943 | 0.10399 | 0.011188 | 0.0095595 | -0.0057593 | 0.065471 | -0.00079046 | 0.06988 | -61.7249 | 63.1393 | -61.853 | -61.821 | 62.7548 | 1.1627 | -0.70038 | -0.61798 | 63.1622 | -61.8668 | -0.2655 | -0.054932 | -0.13733 | -0.23346 | -0.43945 | -0.27924 | -0.032044 | 0.12817 | 60.8871 | 60.9695 | 124.3423 | 124.7269 | -0.13733 | 124.7498 | 62.7502 | -0.27924 | 124.7269 | -0.13733 | 62.7502 | 124.3423 | 124.7498 | -125.0473 | -125.061
1098.6406 | 124.9924 | -61.6562 | 63.208 | 0.096359 | 0.011188 | 0.013191 | 0.0051355 | 0.061626 | -0.00036306 | 0.071376 | -61.7203 | 63.2355 | -61.8759 | -61.9125 | 62.6999 | 1.1948 | -0.59967 | -0.77362 | 63.2126 | -61.9263 | -0.21973 | 0.027466 | -0.064087 | -0.25635 | -0.50812 | -0.27008 | 0.004577 | 0.15564 | 61.0565 | 60.8826 | 124.3561 | 124.8917 | -0.064087 | 124.8688 | 62.851 | -0.27008 | 124.8917 | -0.064087 | 62.851 | 124.3561 | 124.8688 | -125.0839 | -125.1343
1099.6406 | 125.0061 | -61.6058 | 63.2309 | -0.0028231 | 0.012256 | 0.015541 | 0.0055627 | 0.066753 | -0.00079046 | 0.06689 | -61.6562 | 63.208 | -61.8576 | -61.8347 | 62.7136 | 1.1856 | -0.59967 | -0.737 | 63.1989 | -61.9263 | -0.25177 | -0.022888 | -0.050354 | -0.22888 | -0.51727 | -0.32044 | -0.032043 | 0.20142 | 61.0062 | 60.8688 | 124.3195 | 124.8138 | -0.050354 | 124.8047 | 62.7914 | -0.32044 | 124.8138 | -0.050354 | 62.7914 | 124.3195 | 124.8047 | -125.0885 | -125.1572
1100.6406 | 125.0381 | -61.6196 | 63.2172 | -0.025711 | 0.012256 | 0.01191 | 0.0023583 | 0.069744 | -0.00057686 | 0.068171 | -61.6745 | 63.2309 | -61.8576 | -61.8347 | 62.709 | 1.2726 | -0.59052 | -0.72784 | 63.2355 | -61.9217 | -0.23804 | 0.013733 | -0.054932 | -0.21515 | -0.50812 | -0.30212 | 0.018311 | 0.1831 | 61.0291 | 60.8917 | 124.3286 | 124.8505 | -0.054932 | 124.855 | 62.8922 | -0.30212 | 124.8505 | -0.054932 | 62.8922 | 124.3286 | 124.855 | -125.0748 | -125.1389
1101.6406 | 125.0656 | -61.6333 | 63.2217 | 0.073471 | 0.012042 | 0.013832 | 0.0034265 | 0.067821 | -0.0010041 | 0.068385 | -61.702 | 63.1851 | -61.8805 | -61.8713 | 62.677 | 1.2589 | -1.0666 | -1.0895 | 63.1805 | -61.9766 | -0.24719 | -0.036621 | -0.068664 | -0.23804 | -0.54474 | -0.34332 | -0.041199 | 0.17853 | 60.5667 | 60.5438 | 124.3103 | 124.8184 | -0.068664 | 124.8138 | 62.8922 | -0.34332 | 124.8184 | -0.068664 | 62.8922 | 124.3103 | 124.8138 | -125.1022 | -125.1984
1102.6406 | 125.061 | -61.6104 | 63.1897 | 0.08873 | 0.0094785 | 0.0097733 | -0.0070411 | 0.066539 | -0.00057686 | 0.070735 | -61.6791 | 63.1119 | -61.8668 | -61.8118 | 62.7686 | 1.3779 | -0.76904 | -0.70953 | 63.1851 | -61.8668 | -0.25635 | -0.07782 | -0.068664 | -0.20142 | -0.42114 | -0.25635 | -0.004577 | 0.18768 | 60.8414 | 60.9009 | 124.379 | 124.7223 | -0.068664 | 124.7955 | 62.9883 | -0.25635 | 124.7223 | -0.068664 | 62.9883 | 124.379 | 124.7955 | -125.0565 | -125.0565
1103.6406 | 124.9603 | -61.6241 | 63.2217 | 0.11162 | 0.011615 | 0.0149 | 0.0053491 | 0.065899 | -0.00079046 | 0.067744 | -61.6928 | 63.2172 | -61.8576 | -61.8713 | 62.6816 | 1.3321 | -0.63629 | -0.79193 | 63.1989 | -61.9537 | -0.23346 | -0.004578 | -0.068664 | -0.24719 | -0.54016 | -0.32959 | -0.022888 | 0.16479 | 60.9879 | 60.8322 | 124.3057 | 124.8413 | -0.068664 | 124.823 | 62.9562 | -0.32959 | 124.8413 | -0.068664 | 62.9562 | 124.3057 | 124.823 | -125.0793 | -125.1755
1104.6406 | 124.9924 | -61.647 | 63.1943 | 0.30235 | 0.01076 | 0.014687 | 0.0042809 | 0.066539 | -0.00014946 | 0.070735 | -61.7065 | 63.2217 | -61.8622 | -61.853 | 62.6862 | 1.4053 | -0.67749 | -0.82398 | 63.1851 | -61.9263 | -0.21515 | 0.027466 | -0.059509 | -0.20599 | -0.50812 | -0.27924 | -0.009155 | 0.15564 | 60.9695 | 60.8231 | 124.3332 | 124.8688 | -0.059509 | 124.8322 | 63.0524 | -0.27924 | 124.8688 | -0.059509 | 63.0524 | 124.3332 | 124.8322 | -125.0565 | -125.1205
1105.6406 | 125.029 | -61.6241 | 63.2126 | 0.24132 | 0.012683 | 0.012978 | 0.0038537 | 0.067608 | 0.00027774 | 0.068385 | -61.6653 | 63.2263 | -61.8622 | -61.8576 | 62.6816 | 1.4282 | -0.68207 | -0.83771 | 63.2172 | -61.908 | -0.23804 | 0.013733 | -0.041198 | -0.23346 | -0.53101 | -0.28381 | 0.004578 | 0.19684 | 60.9421 | 60.7864 | 124.3057 | 124.8505 | -0.041198 | 124.8413 | 63.0524 | -0.28381 | 124.8505 | -0.041198 | 63.0524 | 124.3057 | 124.8413 | -125.0748 | -125.1205
1106.6406 | 124.9832 | -61.6196 | 63.2355 | 0.058212 | 0.012897 | 0.01255 | 0.0047081 | 0.067608 | -0.0024995 | 0.069667 | -61.6699 | 63.2126 | -61.8759 | -61.853 | 62.6999 | 1.5198 | -0.62714 | -0.82398 | 63.2217 | -61.9263 | -0.25635 | -0.022889 | -0.050354 | -0.23346 | -0.53558 | -0.3067 | -0.013733 | 0.20599 | 60.9924 | 60.7956 | 124.3195 | 124.8322 | -0.050354 | 124.8413 | 63.1393 | -0.3067 | 124.8322 | -0.050354 | 63.1393 | 124.3195 | 124.8413 | -125.1114 | -125.1617
1107.6406 | 125.1297 | -61.5875 | 63.1714 | 0.29472 | 0.010333 | 0.014046 | -0.0029823 | 0.066753 | -0.00036306 | 0.072444 | -61.6287 | 63.0981 | -61.8622 | -61.7432 | 62.8052 | 1.6891 | -0.85602 | -0.72327 | 63.1989 | -61.821 | -0.27466 | -0.073242 | -0.041199 | -0.15564 | -0.36621 | -0.23346 | 0.027466 | 0.23346 | 60.7315 | 60.8643 | 124.3927 | 124.6857 | -0.041199 | 124.7864 | 63.2767 | -0.23346 | 124.6857 | -0.041199 | 63.2767 | 124.3927 | 124.7864 | -125.0336 | -124.9924
1108.6406 | 124.9649 | -61.6196 | 63.2126 | 0.096359 | 0.011828 | 0.011055 | 0.0012903 | 0.066753 | 6.414e-05 | 0.072017 | -61.7111 | 63.2446 | -61.8439 | -61.8393 | 62.6724 | 1.6113 | -0.67749 | -0.8606 | 63.2172 | -61.908 | -0.2243 | 0.032044 | -0.091553 | -0.21973 | -0.54016 | -0.28839 | 0.004578 | 0.13275 | 60.9421 | 60.759 | 124.292 | 124.8642 | -0.091553 | 124.8367 | 63.2309 | -0.28839 | 124.8642 | -0.091553 | 63.2309 | 124.292 | 124.8367 | -125.0565 | -125.1205
1109.6406 | 125.0107 | -61.615 | 63.2217 | 0.096359 | 0.010974 | 0.011696 | 0.0027855 | 0.068462 | 0.00027774 | 0.068812 | -61.4502 | 63.2584 | -61.8668 | -61.8118 | 62.6724 | 1.6388 | -0.67749 | -0.86517 | 63.2355 | -61.9171 | -0.25177 | 0.036621 | 0.16479 | -0.19684 | -0.54932 | -0.30212 | 0.013733 | 0.41656 | 60.9375 | 60.7498 | 124.2874 | 124.8734 | 0.16479 | 124.8505 | 63.2538 | -0.30212 | 124.8734 | 0.16479 | 63.2538 | 124.2874 | 124.8505 | -125.0885 | -125.1389
1110.6406 | 124.9741 | -61.5967 | 63.2263 | 0.10399 | 0.010333 | 0.013619 | 0.0062035 | 0.068035 | -0.00079046 | 0.071376 | -62.0407 | 63.1851 | -61.8668 | -61.8439 | 62.645 | 1.7258 | -0.62256 | -0.87891 | 63.2446 | -61.9125 | -0.27008 | -0.041198 | -0.44403 | -0.24719 | -0.58136 | -0.31586 | 0.018311 | -0.17395 | 60.9741 | 60.7178 | 124.2416 | 124.7818 | -0.44403 | 124.8413 | 63.3224 | -0.31586 | 124.7818 | -0.44403 | 63.3224 | 124.2416 | 124.8413 | -125.0931 | -125.1389
1111.6406 | 125.0107 | -61.6013 | 63.2263 | 0.10399 | 0.012897 | 0.016396 | 0.0021447 | 0.068462 | 0.0024139 | 0.06988 | -61.6837 | 63.2401 | -61.8576 | -61.821 | 62.7045 | 1.7944 | -0.6958 | -0.87891 | 63.2355 | -61.908 | -0.25635 | 0.013733 | -0.082398 | -0.21973 | -0.52185 | -0.3067 | 0.009156 | 0.17395 | 60.9055 | 60.7224 | 124.3057 | 124.8413 | -0.082398 | 124.8367 | 63.3957 | -0.3067 | 124.8413 | -0.082398 | 63.3957 | 124.3057 | 124.8367 | -125.0839 | -125.1343
1112.6562 | 125.1205 | -61.5417 | 63.2309 | -0.056229 | 0.010119 | 0.013619 | -0.0064003 | 0.064403 | 0.0011321 | 0.070735 | -61.6516 | 63.1439 | -61.8164 | -61.7477 | 62.8189 | 1.9592 | -0.72784 | -0.737 | 63.1989 | -61.821 | -0.27466 | -0.086975 | -0.10986 | -0.20599 | -0.41199 | -0.27924 | -0.032043 | 0.16479 | 60.8139 | 60.8047 | 124.3607 | 124.6857 | -0.10986 | 124.7406 | 63.501 | -0.27924 | 124.6857 | -0.10986 | 63.501 | 124.3607 | 124.7406 | -125.0473 | -125.0519
1113.6406 | 124.9329 | -61.5738 | 63.2675 | 0.073471 | 0.011401 | 0.012978 | 0.0047081 | 0.065685 | -0.0012177 | 0.068812 | -61.6608 | 63.2401 | -61.8301 | -61.8393 | 62.6816 | 1.9409 | -1.0483 | -0.6958 | 63.1714 | -61.9217 | -0.25635 | -0.027466 | -0.086975 | -0.2655 | -0.58594 | -0.3479 | -0.09613 | 0.16937 | 60.5255 | 60.878 | 124.2554 | 124.8138 | -0.086975 | 124.7452 | 63.5147 | -0.3479 | 124.8138 | -0.086975 | 63.5147 | 124.2554 | 124.7452 | -125.0977 | -125.1892
1114.6406 | 124.7955 | -61.6241 | 63.1851 | 0.065841 | 0.015033 | 0.013832 | 0.0057763 | 0.065899 | -0.0018585 | 0.06988 | -61.6516 | 63.2584 | -61.8301 | -61.8256 | 62.6816 | 1.9089 | -0.6546 | -0.9201 | 63.2629 | -61.9125 | -0.20599 | 0.073242 | -0.027465 | -0.20142 | -0.50354 | -0.28839 | 0.077819 | 0.17853 | 60.9695 | 60.704 | 124.3057 | 124.8825 | -0.027465 | 124.8871 | 63.533 | -0.28839 | 124.8825 | -0.027465 | 63.533 | 124.3057 | 124.8871 | -125.0153 | -125.0977
1115.6406 | 125.0107 | -61.5875 | 63.2309 | 0.30235 | 0.01311 | 0.01255 | 0.0040673 | 0.066753 | 0.00027774 | 0.068171 | -61.6745 | 63.2538 | -61.8347 | -61.8301 | 62.6953 | 1.9638 | -0.69122 | -0.93384 | 63.2126 | -61.9125 | -0.24719 | 0.022888 | -0.086976 | -0.24262 | -0.53558 | -0.32501 | -0.018311 | 0.16022 | 60.8963 | 60.6537 | 124.2828 | 124.8413 | -0.086976 | 124.8001 | 63.5513 | -0.32501 | 124.8413 | -0.086976 | 63.5513 | 124.2828 | 124.8001 | -125.0656 | -125.1434
1116.6406 | 124.9832 | -61.5921 | 63.2492 | 0.31761 | 0.01311 | 0.012978 | 0.0051355 | 0.066112 | -0.0010041 | 0.068171 | -61.6562 | 63.2767 | -61.821 | -61.8118 | 62.6907 | 2.0004 | -0.68207 | -0.93842 | 63.2401 | -61.9125 | -0.22888 | 0.027465 | -0.064087 | -0.21973 | -0.55847 | -0.32044 | -0.009156 | 0.1648 | 60.91 | 60.6537 | 124.2828 | 124.8688 | -0.064087 | 124.8322 | 63.5925 | -0.32044 | 124.8688 | -0.064087 | 63.5925 | 124.2828 | 124.8322 | -125.0702 | -125.1617
1117.6406 | 125.1068 | -61.5143 | 63.2172 | 0.0811 | 0.0077695 | 0.01191 | -0.0040503 | 0.065899 | 0.0017731 | 0.068385 | -61.6058 | 63.1439 | -61.8256 | -61.7569 | 62.7731 | 2.1652 | -0.82855 | -0.83313 | 63.1943 | -61.8073 | -0.31128 | -0.073242 | -0.091553 | -0.24262 | -0.44403 | -0.29297 | -0.022888 | 0.21973 | 60.6857 | 60.6812 | 124.2874 | 124.6582 | -0.091553 | 124.7086 | 63.6795 | -0.29297 | 124.6582 | -0.091553 | 63.6795 | 124.2874 | 124.7086 | -125.0427 | -125.0244
1118.6406 | 125.0244 | -61.5555 | 63.2538 | 0.12688 | 0.014392 | 0.013832 | 0.0032129 | 0.065899 | 6.414e-05 | 0.070308 | -61.6379 | 63.2584 | -61.8073 | -61.8073 | 62.709 | 2.0874 | -0.737 | -0.93384 | 63.2446 | -61.8668 | -0.25177 | 0.004578 | -0.082397 | -0.25177 | -0.54474 | -0.31128 | -0.009155 | 0.16937 | 60.8185 | 60.6216 | 124.2645 | 124.8138 | -0.082397 | 124.8001 | 63.6429 | -0.31128 | 124.8138 | -0.082397 | 63.6429 | 124.2645 | 124.8001 | -125.061 | -125.1205
1119.6406 | 125.0153 | -61.5784 | 63.2355 | 0.11925 | 0.013965 | 0.011696 | 0.0032129 | 0.068462 | -0.00036306 | 0.067103 | -61.6333 | 63.2492 | -61.8073 | -61.7889 | 62.6999 | 2.0828 | -0.73242 | -0.95215 | 63.2355 | -61.8759 | -0.22888 | 0.013733 | -0.054932 | -0.21057 | -0.53558 | -0.29755 | 0 | 0.17395 | 60.8459 | 60.6262 | 124.2783 | 124.8276 | -0.054932 | 124.8138 | 63.6612 | -0.29755 | 124.8276 | -0.054932 | 63.6612 | 124.2783 | 124.8138 | -125.0427 | -125.1114
1120.6406 | 125.0198 | -61.5692 | 63.2675 | 0.058212 | 0.011188 | 0.0093459 | 0.0076989 | 0.064617 | -0.0016449 | 0.067531 | -61.6699 | 63.2584 | -61.8347 | -61.6745 | 62.6175 | 2.0966 | -0.56763 | -1.0071 | 63.2401 | -61.8668 | -0.2655 | -0.009155 | -0.10071 | -0.10529 | -0.65002 | -0.29755 | -0.027466 | 0.16479 | 61.0016 | 60.5621 | 124.1867 | 124.8276 | -0.10071 | 124.8093 | 63.6658 | -0.29755 | 124.8276 | -0.10071 | 63.6658 | 124.1867 | 124.8093 | -125.1022 | -125.1343
1121.6406 | 125.0061 | -61.5417 | 63.2812 | 0.11925 | 0.011188 | 0.010414 | 0.0021447 | 0.066753 | -0.00057686 | 0.073939 | -61.6425 | 63.2767 | -61.8301 | -62.1323 | 62.4023 | 2.211 | -0.48981 | -1.0666 | 63.2858 | -61.8439 | -0.28839 | -0.004578 | -0.10071 | -0.59052 | -0.87891 | -0.30212 | 0.004578 | 0.18768 | 61.0519 | 60.4752 | 123.9441 | 124.8184 | -0.10071 | 124.8276 | 63.7527 | -0.30212 | 124.8184 | -0.10071 | 63.7527 | 123.9441 | 124.8276 | -125.1114 | -125.1251
1122.6406 | 125.0885 | -61.5097 | 63.2355 | 0.11925 | 0.0088375 | 0.010414 | -0.00020505 | 0.066967 | -0.0012177 | 0.069667 | -61.5921 | 63.1485 | -61.7844 | -61.6974 | 62.8006 | 2.3163 | -0.86975 | -0.88806 | 63.2217 | -61.7935 | -0.27466 | -0.086975 | -0.082397 | -0.18768 | -0.43488 | -0.28381 | -0.013733 | 0.19226 | 60.64 | 60.6216 | 124.3103 | 124.6582 | -0.082397 | 124.7314 | 63.826 | -0.28381 | 124.6582 | -0.082397 | 63.826 | 124.3103 | 124.7314 | -125.0198 | -125.029
1123.6406 | 125.029 | -61.5646 | 63.2812 | 0.14976 | 0.012683 | 0.0099869 | 0.0049219 | 0.065044 | -0.00079046 | 0.068812 | -61.6241 | 63.2812 | -61.7844 | -61.7798 | 62.7136 | 2.2522 | -0.74158 | -1.0391 | 63.2584 | -61.8622 | -0.21973 | 0 | -0.05951 | -0.21515 | -0.56763 | -0.29755 | -0.022888 | 0.16022 | 60.8231 | 60.5255 | 124.2783 | 124.8459 | -0.05951 | 124.823 | 63.8168 | -0.29755 | 124.8459 | -0.05951 | 63.8168 | 124.2783 | 124.823 | -125.0656 | -125.1434
1124.6406 | 125.0061 | -61.5784 | 63.295 | 0.14976 | 0.012042 | 0.010201 | 0.0027855 | 0.067394 | 0.00049134 | 0.068812 | -61.6058 | 63.2584 | -61.7844 | -61.7798 | 62.709 | 2.2568 | -0.737 | -1.0071 | 63.2812 | -61.8484 | -0.20599 | -0.036621 | -0.027466 | -0.20142 | -0.58594 | -0.27008 | -0.013733 | 0.17853 | 60.8414 | 60.5713 | 124.2874 | 124.8367 | -0.027466 | 124.8596 | 63.8351 | -0.27008 | 124.8367 | -0.027466 | 63.8351 | 124.2874 | 124.8596 | -125.0793 | -125.1434
1125.6562 | 124.9832 | -61.5417 | 63.3362 | -0.34615 | 0.0090513 | 0.01255 | 0.00043575 | 0.065471 | -0.00014946 | 0.066676 | -61.6058 | 63.2675 | -61.7523 | -61.7432 | 62.7502 | 2.3758 | -0.64545 | -0.9201 | 63.2812 | -61.8073 | -0.21057 | -0.068665 | -0.064087 | -0.20142 | -0.58594 | -0.2655 | -0.054932 | 0.14648 | 60.8963 | 60.6216 | 124.292 | 124.8093 | -0.064087 | 124.823 | 63.9175 | -0.2655 | 124.8093 | -0.064087 | 63.9175 | 124.292 | 124.823 | -125.0885 | -125.1434
1126.6406 | 125.061 | -61.5143 | 63.2538 | 0.20317 | 0.0084103 | 0.013191 | 0.00086295 | 0.067608 | 6.414e-05 | 0.069453 | -61.5829 | 63.2629 | -61.7798 | -61.7432 | 62.7457 | 2.4353 | -0.87433 | -1.0025 | 63.2355 | -61.8027 | -0.2655 | 0.009155 | -0.068665 | -0.22888 | -0.50812 | -0.28839 | -0.01831 | 0.19684 | 60.64 | 60.5118 | 124.2599 | 124.7772 | -0.068665 | 124.7498 | 63.9496 | -0.28839 | 124.7772 | -0.068665 | 63.9496 | 124.2599 | 124.7498 | -125.0336 | -125.0565
1127.6406 | 125.061 | -61.5234 | 63.2721 | -1.3303 | 0.0096921 | 0.0084915 | -0.0042639 | 0.06419 | -0.0024995 | 0.071376 | -61.5875 | 63.2034 | -61.7661 | -61.7294 | 62.7823 | 2.4307 | -0.82398 | -0.9613 | 63.2492 | -61.7752 | -0.24262 | -0.068665 | -0.064087 | -0.20599 | -0.48981 | -0.25177 | -0.022888 | 0.17853 | 60.6995 | 60.5621 | 124.3057 | 124.7269 | -0.064087 | 124.7726 | 63.9542 | -0.25177 | 124.7269 | -0.064087 | 63.9542 | 124.3057 | 124.7726 | -125.0381 | -125.0473
1128.6406 | 125.0061 | -61.5326 | 63.295 | 0.17265 | 0.012897 | 0.016182 | 0.0055627 | 0.065471 | 0.0013457 | 0.069239 | -61.6058 | 63.2767 | -61.7523 | -61.7477 | 62.7045 | 2.3941 | -0.7782 | -1.0757 | 63.2812 | -61.8576 | -0.21973 | -0.018311 | -0.073242 | -0.21515 | -0.59052 | -0.32501 | -0.013733 | 0.14648 | 60.7544 | 60.4568 | 124.2371 | 124.8093 | -0.073242 | 124.8138 | 63.9267 | -0.32501 | 124.8093 | -0.073242 | 63.9267 | 124.2371 | 124.8138 | -125.0473 | -125.1526
1129.6406 | 125.0885 | -61.5051 | 63.2767 | 0.11162 | 0.012042 | 0.014259 | 0.0021447 | 0.066539 | 0.00049134 | 0.068385 | -61.5738 | 63.2721 | -61.7661 | -61.7157 | 62.7319 | 2.4628 | -0.86975 | -1.0071 | 63.2492 | -61.821 | -0.26093 | -0.004577 | -0.068665 | -0.21057 | -0.54474 | -0.31586 | -0.027465 | 0.19226 | 60.6354 | 60.498 | 124.2371 | 124.7772 | -0.068665 | 124.7543 | 63.9679 | -0.31586 | 124.7772 | -0.068665 | 63.9679 | 124.2371 | 124.7543 | -125.0427 | -125.0977
1130.6562 | 125.0656 | -61.4685 | 63.3133 | -0.23933 | 0.0088375 | 0.011055 | -0.0023413 | 0.066326 | -0.0016449 | 0.069026 | -61.5051 | 63.2355 | -61.7294 | -61.6379 | 62.8189 | 2.5955 | -0.78735 | -0.86517 | 63.2767 | -61.7294 | -0.26093 | -0.077819 | -0.036621 | -0.16937 | -0.49438 | -0.26093 | -0.036621 | 0.2243 | 60.6812 | 60.6033 | 124.2874 | 124.704 | -0.036621 | 124.7452 | 64.064 | -0.26093 | 124.704 | -0.036621 | 64.064 | 124.2874 | 124.7452 | -125.0427 | -125.0427
1131.6406 | 125.0748 | -61.4685 | 63.2767 | 0.073471 | 0.0096921 | 0.01255 | 0.0034265 | 0.068248 | -0.0014313 | 0.069667 | -61.4914 | 63.2263 | -61.7432 | -61.6287 | 62.8189 | 2.6505 | -1.3046 | -0.88348 | 63.2034 | -61.7935 | -0.27466 | -0.050354 | -0.022888 | -0.16022 | -0.45776 | -0.32501 | -0.073242 | 0.25177 | 60.1639 | 60.585 | 124.2874 | 124.6948 | -0.022888 | 124.6719 | 64.119 | -0.32501 | 124.6948 | -0.022888 | 64.119 | 124.2874 | 124.6719 | -125.0198 | -125.0702
1132.6406 | 125.0885 | -61.4777 | 63.2996 | -0.018082 | 0.010119 | 0.0072097 | -0.0034095 | 0.063549 | -0.00057686 | 0.07223 | -61.5463 | 63.2217 | -61.7386 | -61.6837 | 62.8052 | 2.6505 | -0.89264 | -0.93842 | 63.2904 | -61.7249 | -0.26093 | -0.07782 | -0.068665 | -0.20599 | -0.49438 | -0.24719 | -0.009156 | 0.19226 | 60.585 | 60.5392 | 124.2828 | 124.6994 | -0.068665 | 124.7681 | 64.1281 | -0.24719 | 124.6994 | -0.068665 | 64.1281 | 124.2828 | 124.7681 | -125.0381 | -125.0244
1133.6406 | 125.0748 | -61.4868 | 63.2538 | 0.14214 | 0.012042 | 0.011055 | 0.0034265 | 0.065044 | -0.0029267 | 0.068599 | -61.5005 | 63.2263 | -61.702 | -61.6287 | 62.8052 | 2.6276 | -1.0208 | -0.97961 | 63.2492 | -61.7752 | -0.21515 | -0.027466 | -0.013733 | -0.14191 | -0.44861 | -0.28839 | -0.004577 | 0.20142 | 60.466 | 60.5072 | 124.292 | 124.7131 | -0.013733 | 124.736 | 64.1144 | -0.28839 | 124.7131 | -0.013733 | 64.1144 | 124.292 | 124.736 | -124.9557 | -125.029
1134.6406 | 125.0244 | -61.4731 | 63.327 | 0.11925 | 0.010547 | 0.014259 | 0.0055627 | 0.068248 | -0.0016449 | 0.069667 | -61.5463 | 63.2904 | -61.734 | -61.7111 | 62.7365 | 2.5864 | -0.91553 | -1.0849 | 63.2904 | -61.8027 | -0.26093 | -0.036621 | -0.073243 | -0.23804 | -0.59051 | -0.32959 | -0.036621 | 0.18768 | 60.5576 | 60.3882 | 124.2096 | 124.7635 | -0.073243 | 124.7635 | 64.0594 | -0.32959 | 124.7635 | -0.073243 | 64.0594 | 124.2096 | 124.7635 | -125.061 | -125.1297
1135.6562 | 125.1251 | -61.4319 | 63.3224 | -0.13252 | 0.0094785 | 0.0069961 | -0.0023413 | 0.065471 | 0.0013457 | 0.067531 | -61.5097 | 63.2263 | -61.7111 | -61.5829 | 62.8555 | 2.742 | -0.93384 | -0.93842 | 63.2767 | -61.7203 | -0.27924 | -0.096131 | -0.07782 | -0.15106 | -0.46692 | -0.28839 | -0.045777 | 0.20142 | 60.498 | 60.4935 | 124.2874 | 124.6582 | -0.07782 | 124.7086 | 64.1739 | -0.28839 | 124.6582 | -0.07782 | 64.1739 | 124.2874 | 124.7086 | -125.0336 | -125.0427
1136.6406 | 125.1251 | -61.4822 | 63.295 | 0.24132 | 0.010333 | 0.013832 | 0.0042809 | 0.064403 | -0.00014946 | 0.070521 | -61.5051 | 63.2675 | -61.7157 | -61.6333 | 62.7823 | 2.7328 | -1.0208 | -1.0666 | 63.2355 | -61.7752 | -0.23346 | -0.027466 | -0.022888 | -0.15106 | -0.5127 | -0.29297 | -0.059509 | 0.21057 | 60.4614 | 60.4156 | 124.2645 | 124.7498 | -0.022888 | 124.7177 | 64.2151 | -0.29297 | 124.7498 | -0.022888 | 64.2151 | 124.2645 | 124.7177 | -125.0107 | -125.0702
1137.6406 | 125.0702 | -61.4594 | 63.3087 | 0.10399 | 0.0086239 | 0.012978 | -0.00084605 | 0.062694 | 0.00027774 | 0.070521 | -61.5601 | 63.2034 | -61.734 | -61.6562 | 62.7869 | 2.8152 | -0.94757 | -1.0437 | 63.2675 | -61.7294 | -0.27466 | -0.10529 | -0.10071 | -0.19684 | -0.52185 | -0.27008 | -0.041199 | 0.17395 | 60.5118 | 60.4156 | 124.2462 | 124.6628 | -0.10071 | 124.7269 | 64.2746 | -0.27008 | 124.6628 | -0.10071 | 64.2746 | 124.2462 | 124.7269 | -125.0427 | -125.0381
1138.6406 | 125.1343 | -61.441 | 63.3087 | 0.14214 | 0.0099057 | 0.015541 | 0.0017175 | 0.065044 | -0.00036306 | 0.067958 | -61.4777 | 63.2492 | -61.7203 | -61.4731 | 62.9105 | 2.8427 | -1.0208 | -1.0117 | 63.2629 | -61.7477 | -0.27924 | -0.059509 | -0.036621 | -0.032043 | -0.39825 | -0.3067 | -0.045777 | 0.24262 | 60.4202 | 60.4294 | 124.3515 | 124.6902 | -0.036621 | 124.704 | 64.2838 | -0.3067 | 124.6902 | -0.036621 | 64.2838 | 124.3515 | 124.704 | -125.029 | -125.0565
1139.6406 | 125.1434 | -61.4182 | 63.327 | 0.13451 | 0.013324 | 0.013832 | 0.0040673 | 0.06419 | -0.0014313 | 0.068599 | -61.4594 | 63.2401 | -61.734 | -61.6241 | 62.7914 | 2.8885 | -1.3184 | -1.3092 | 63.2034 | -61.7523 | -0.31586 | -0.086975 | -0.041199 | -0.20599 | -0.53558 | -0.33417 | -0.1236 | 0.27466 | 60.0998 | 60.1089 | 124.2096 | 124.6582 | -0.041199 | 124.6216 | 64.3066 | -0.33417 | 124.6582 | -0.041199 | 64.3066 | 124.2096 | 124.6216 | -125.061 | -125.0793
1140.6562 | 125.0244 | -61.4685 | 63.3636 | -0.21645 | 0.0088375 | 0.0057143 | -0.00063225 | 0.063549 | -0.0018585 | 0.069026 | -61.4868 | 63.2996 | -61.6974 | -61.6608 | 62.7731 | 2.9114 | -0.81024 | -1.0712 | 63.3362 | -61.7477 | -0.22888 | -0.064086 | -0.01831 | -0.19226 | -0.59052 | -0.27924 | -0.027465 | 0.21057 | 60.6583 | 60.3973 | 124.2416 | 124.7681 | -0.01831 | 124.8047 | 64.3799 | -0.27924 | 124.7681 | -0.01831 | 64.3799 | 124.2416 | 124.8047 | -125.061 | -125.1114
1141.6406 | 125.0061 | -61.4594 | 63.327 | 0.14976 | 0.011828 | 0.011269 | 0.0049219 | 0.065685 | -0.00057686 | 0.06988 | -61.5234 | 63.295 | -61.734 | -61.6974 | 62.6999 | 2.8793 | -0.98877 | -1.2268 | 63.2996 | -61.7844 | -0.27466 | -0.032043 | -0.064086 | -0.23804 | -0.62714 | -0.32501 | -0.027465 | 0.21057 | 60.4706 | 60.2325 | 124.1592 | 124.7543 | -0.064086 | 124.7589 | 64.3387 | -0.32501 | 124.7543 | -0.064086 | 64.3387 | 124.1592 | 124.7589 | -125.061 | -125.1114
1142.6406 | 125.0977 | -61.4456 | 63.3133 | 0.14214 | 0.0096921 | 0.014687 | 0.0023583 | 0.06419 | -0.0010041 | 0.068812 | -61.6333 | 63.2034 | -61.702 | -61.6104 | 62.8143 | 3.0167 | -1.1536 | -1.1398 | 63.2675 | -61.7294 | -0.25635 | -0.10986 | -0.18768 | -0.16479 | -0.49896 | -0.28381 | -0.045776 | 0.068664 | 60.2921 | 60.3058 | 124.2599 | 124.649 | -0.18768 | 124.7131 | 64.4623 | -0.28381 | 124.649 | -0.18768 | 64.4623 | 124.2599 | 124.7131 | -125.0153 | -125.0427
1143.6406 | 125.0565 | -61.4456 | 63.3133 | 0.20317 | 0.012469 | 0.014046 | 0.0047081 | 0.066539 | -0.0014313 | 0.069453 | -61.4914 | 63.3362 | -61.7157 | -61.6425 | 62.7502 | 3.0441 | -1.0941 | -1.2177 | 63.295 | -61.7386 | -0.27008 | 0.022889 | -0.045776 | -0.19684 | -0.56305 | -0.29297 | -0.01831 | 0.2243 | 60.3516 | 60.228 | 124.1959 | 124.7818 | -0.045776 | 124.7406 | 64.4897 | -0.29297 | 124.7818 | -0.045776 | 64.4897 | 124.1959 | 124.7406 | -125.029 | -125.0519
1144.6406 | 125.0198 | -61.4731 | 63.3133 | 0.16502 | 0.0096921 | 0.011696 | 0.0059899 | 0.065471 | -0.0014313 | 0.071162 | -61.5051 | 63.3224 | -61.7294 | -61.6608 | 62.7274 | 3.1128 | -1.0574 | -1.2543 | 63.3133 | -61.7477 | -0.25635 | 0.009156 | -0.032044 | -0.18768 | -0.58594 | -0.27466 | 0 | 0.2243 | 60.4156 | 60.2188 | 124.2004 | 124.7955 | -0.032044 | 124.7864 | 64.5859 | -0.27466 | 124.7955 | -0.032044 | 64.5859 | 124.2004 | 124.7864 | -125.0427 | -125.061
1145.6406 | 125.0977 | -61.4365 | 63.327 | 0.2108 | 0.0099057 | 0.013619 | 0.0032129 | 0.06483 | -0.00079046 | 0.067958 | -61.4777 | 63.2904 | -61.7249 | -61.6104 | 62.8006 | 3.2089 | -1.1581 | -1.2177 | 63.2675 | -61.7432 | -0.28839 | -0.036621 | -0.041199 | -0.17395 | -0.52643 | -0.3067 | -0.059509 | 0.24719 | 60.2783 | 60.2188 | 124.2371 | 124.7269 | -0.041199 | 124.704 | 64.6454 | -0.3067 | 124.7269 | -0.041199 | 64.6454 | 124.2371 | 124.704 | -125.0519 | -125.0702
1146.6406 | 125.1068 | -61.4365 | 63.327 | 0.20317 | 0.012256 | 0.0095595 | 0.0015039 | 0.066112 | -0.0010041 | 0.069239 | -61.4731 | 63.3316 | -61.7203 | -61.6287 | 62.7686 | 3.186 | -1.1673 | -1.2451 | 63.2858 | -61.7523 | -0.28381 | 0.004578 | -0.036621 | -0.19226 | -0.55847 | -0.31586 | -0.041198 | 0.24719 | 60.2692 | 60.1913 | 124.205 | 124.7681 | -0.036621 | 124.7223 | 64.6225 | -0.31586 | 124.7681 | -0.036621 | 64.6225 | 124.205 | 124.7223 | -125.0473 | -125.0793
1147.6406 | 125.1297 | -61.3953 | 63.327 | -0.16304 | 0.0099057 | 0.013832 | -0.0021277 | 0.065258 | -0.0014313 | 0.06988 | -61.4136 | 63.2492 | -61.6425 | -61.528 | 62.7457 | 3.3188 | -1.0849 | -1.1902 | 63.3224 | -61.6837 | -0.24719 | -0.077819 | -0.01831 | -0.13275 | -0.58136 | -0.28839 | -0.004577 | 0.22888 | 60.3104 | 60.2051 | 124.1409 | 124.6445 | -0.01831 | 124.7177 | 64.7141 | -0.28839 | 124.6445 | -0.01831 | 64.7141 | 124.1409 | 124.7177 | -124.9695 | -125.0107
1148.6406 | 124.9832 | -61.4639 | 63.3728 | -0.071488 | 0.010547 | 0.01191 | 0.0038537 | 0.066326 | -0.00057686 | 0.069026 | -61.5417 | 63.3591 | -61.6928 | -61.6928 | 62.6862 | 3.186 | -1.0712 | -1.4008 | 63.3362 | -61.7752 | -0.22888 | -0.013733 | -0.07782 | -0.22888 | -0.68665 | -0.31128 | -0.036621 | 0.15106 | 60.3928 | 60.0632 | 124.1501 | 124.823 | -0.07782 | 124.8001 | 64.65 | -0.31128 | 124.823 | -0.07782 | 64.65 | 124.1501 | 124.8001 | -125.0656 | -125.148
1149.6406 | 124.9603 | -61.4456 | 63.3728 | -3.1538 | 0.011615 | 0.016823 | 0.0047081 | 0.065258 | -0.0016449 | 0.070094 | -61.5509 | 63.3682 | -61.702 | -61.6791 | 62.6724 | 3.2318 | -1.0712 | -1.4236 | 63.3591 | -61.7203 | -0.25635 | -0.004578 | -0.10528 | -0.23346 | -0.70038 | -0.27466 | -0.013733 | 0.15106 | 60.3745 | 60.022 | 124.118 | 124.8138 | -0.10528 | 124.8047 | 64.6774 | -0.27466 | 124.8138 | -0.10528 | 64.6774 | 124.118 | 124.8047 | -125.0748 | -125.0931
1150.6406 | 125.0198 | -61.4365 | 63.3453 | 0.15739 | 0.013324 | 0.010201 | 0.0032129 | 0.066112 | -0.0012177 | 0.070521 | -61.496 | 63.3499 | -61.6791 | -61.6745 | 62.709 | 3.3142 | -1.1169 | -1.4236 | 63.3682 | -61.7386 | -0.24262 | 0.004578 | -0.05951 | -0.23804 | -0.63629 | -0.30212 | 0.022888 | 0.1831 | 60.3195 | 60.0128 | 124.1455 | 124.7864 | -0.05951 | 124.8047 | 64.7507 | -0.30212 | 124.7864 | -0.05951 | 64.7507 | 124.1455 | 124.8047 | -125.0244 | -125.0839
1151.6406 | 124.9741 | -61.4502 | 63.3728 | 0.10399 | 0.015246 | 0.0089187 | 0.0029993 | 0.066753 | -0.0010041 | 0.067958 | -61.4914 | 63.3865 | -61.6928 | -61.6745 | 62.7136 | 3.2547 | -1.1261 | -1.442 | 63.3545 | -61.7569 | -0.24262 | 0.013733 | -0.041199 | -0.22431 | -0.65918 | -0.3067 | -0.018311 | 0.20142 | 60.3241 | 60.0082 | 124.1638 | 124.8367 | -0.041199 | 124.8047 | 64.7049 | -0.3067 | 124.8367 | -0.041199 | 64.7049 | 124.1638 | 124.8047 | -125.0656 | -125.1297
1152.6406 | 125.1297 | -61.3953 | 63.3453 | 0.16502 | 0.010974 | 0.013619 | 0.00043575 | 0.066112 | 0.0011321 | 0.071589 | -61.4319 | 63.2996 | -61.6608 | -61.5875 | 62.8006 | 3.479 | -1.5564 | -1.5656 | 63.2538 | -61.7157 | -0.2655 | -0.045776 | -0.036621 | -0.19226 | -0.54474 | -0.32043 | -0.091553 | 0.22888 | 59.8389 | 59.8297 | 124.1959 | 124.6948 | -0.036621 | 124.649 | 64.8743 | -0.32043 | 124.6948 | -0.036621 | 64.8743 | 124.1959 | 124.649 | -125.0061 | -125.061
1153.6406 | 125.0473 | -61.4136 | 63.3682 | 0.12688 | 0.012897 | 0.012978 | 0.0042809 | 0.065685 | -0.00057686 | 0.069239 | -61.4777 | 63.3636 | -61.702 | -61.647 | 62.7182 | 3.3783 | -1.1993 | -1.474 | 63.3636 | -61.7203 | -0.28839 | -0.004578 | -0.064087 | -0.23346 | -0.65002 | -0.3067 | -0.004578 | 0.2243 | 60.2142 | 59.9396 | 124.1318 | 124.7772 | -0.064087 | 124.7772 | 64.7919 | -0.3067 | 124.7772 | -0.064087 | 64.7919 | 124.1318 | 124.7772 | -125.0702 | -125.0885
1154.6406 | 125.0015 | -61.4456 | 63.382 | 0.11162 | 0.012897 | 0.013619 | 0.0038537 | 0.068676 | -0.00014946 | 0.070094 | -61.4822 | 63.3957 | -61.6699 | -61.6608 | 62.709 | 3.4012 | -1.1948 | -1.5381 | 63.3728 | -61.7203 | -0.2243 | 0.013733 | -0.036621 | -0.21515 | -0.67291 | -0.27466 | -0.009155 | 0.18768 | 60.2509 | 59.9075 | 124.1547 | 124.8413 | -0.036621 | 124.8184 | 64.8468 | -0.27466 | 124.8413 | -0.036621 | 64.8468 | 124.1547 | 124.8184 | -125.0519 | -125.1022
1155.6406 | 124.9191 | -61.441 | 63.4003 | 0.012436 | 0.010974 | 0.011269 | 0.0019311 | 0.067394 | -0.0012177 | 0.069667 | -61.4685 | 63.3957 | -61.6745 | -61.6653 | 62.7045 | 3.4744 | -1.1719 | -1.5839 | 63.3911 | -61.7203 | -0.23346 | -0.004578 | -0.027466 | -0.2243 | -0.6958 | -0.27924 | -0.009156 | 0.20599 | 60.2692 | 59.8572 | 124.1455 | 124.8367 | -0.027466 | 124.8322 | 64.9155 | -0.27924 | 124.8367 | -0.027466 | 64.9155 | 124.1455 | 124.8322 | -125.0748 | -125.1205
1156.6406 | 125.0061 | -61.4182 | 63.4277 | 0.065841 | 0.010547 | 0.014473 | 0.0023583 | 0.06718 | -0.0014313 | 0.06988 | -61.441 | 63.3957 | -61.6745 | -61.647 | 62.709 | 3.479 | -1.1948 | -1.6205 | 63.3911 | -61.7386 | -0.25635 | -0.032043 | -0.022888 | -0.22888 | -0.71869 | -0.32043 | -0.036621 | 0.23346 | 60.2234 | 59.7977 | 124.1272 | 124.8138 | -0.022888 | 124.8093 | 64.8972 | -0.32043 | 124.8138 | -0.022888 | 64.8972 | 124.1272 | 124.8093 | -125.1022 | -125.1663
1157.6406 | 125.0656 | -61.3861 | 63.3911 | 0.11925 | 0.0094785 | 0.0099869 | -0.0051185 | 0.065685 | -0.00036306 | 0.070308 | -61.496 | 63.2812 | -61.6425 | -61.615 | 62.7502 | 3.6163 | -1.3412 | -1.4923 | 63.3682 | -61.647 | -0.25635 | -0.10986 | -0.10986 | -0.22888 | -0.64087 | -0.26093 | -0.022888 | 0.14648 | 60.0449 | 59.8938 | 124.1364 | 124.6674 | -0.10986 | 124.7543 | 65.0024 | -0.26093 | 124.6674 | -0.10986 | 65.0024 | 124.1364 | 124.7543 | -125.0336 | -125.0381
1158.6406 | 124.8734 | -61.4548 | 63.3865 | 0.065841 | 0.013751 | 0.011482 | 0.0057763 | 0.067394 | 0.00091854 | 0.067103 | -61.4685 | 63.4048 | -61.6837 | -61.6791 | 62.677 | 3.5202 | -1.236 | -1.6342 | 63.3728 | -61.7386 | -0.22888 | 0.01831 | -0.013733 | -0.2243 | -0.70953 | -0.28381 | -0.013733 | 0.21515 | 60.2188 | 59.8206 | 124.1318 | 124.8596 | -0.013733 | 124.8276 | 64.975 | -0.28381 | 124.8596 | -0.013733 | 64.975 | 124.1318 | 124.8276 | -125.0702 | -125.1251
1159.6406 | 124.9649 | -61.4182 | 63.3957 | 0.28709 | 0.012256 | 0.013405 | 0.0021447 | 0.066967 | -0.0010041 | 0.067317 | -61.4685 | 63.4094 | -61.6562 | -61.6608 | 62.6678 | 3.5751 | -1.2955 | -1.6846 | 63.3865 | -61.7065 | -0.23804 | 0.013733 | -0.050354 | -0.24262 | -0.72784 | -0.28839 | -0.009155 | 0.18768 | 60.1227 | 59.7336 | 124.086 | 124.8276 | -0.050354 | 124.8047 | 64.9933 | -0.28839 | 124.8276 | -0.050354 | 64.9933 | 124.086 | 124.8047 | -125.0519 | -125.1022
1160.6406 | 124.9649 | -61.4136 | 63.4003 | 0.11162 | 0.012042 | 0.016609 | 0.0019311 | 0.066112 | 0.00027774 | 0.068171 | -61.4685 | 63.4186 | -61.647 | -61.6241 | 62.8006 | 3.6484 | -1.3641 | -1.6479 | 63.4048 | -61.6974 | -0.23346 | 0.01831 | -0.054932 | -0.21057 | -0.59967 | -0.28381 | 0.004577 | 0.17853 | 60.0494 | 59.7656 | 124.2142 | 124.8322 | -0.054932 | 124.8184 | 65.0619 | -0.28381 | 124.8322 | -0.054932 | 65.0619 | 124.2142 | 124.8184 | -125.0473 | -125.0977
1161.6406 | 124.8322 | -61.441 | 63.3957 | 0.050583 | 0.0099057 | 0.011696 | 0.0034265 | 0.066326 | -0.0012177 | 0.070948 | -61.4548 | 63.4186 | -61.6516 | -61.6425 | 62.6633 | 3.6484 | -1.355 | -1.7578 | 63.3957 | -61.7249 | -0.21057 | 0.022888 | -0.013733 | -0.20142 | -0.73242 | -0.28381 | 0 | 0.19684 | 60.0861 | 59.6832 | 124.1043 | 124.8596 | -0.013733 | 124.8367 | 65.0894 | -0.28381 | 124.8596 | -0.013733 | 65.0894 | 124.1043 | 124.8367 | -125.0473 | -125.1205
1162.6406 | 124.9924 | -61.3815 | 63.414 | -0.071488 | 0.013537 | 0.0097733 | 0.0042809 | 0.068676 | -0.0022859 | 0.068599 | -61.3998 | 63.4323 | -61.6333 | -61.5646 | 62.7182 | 3.7445 | -1.4191 | -1.7349 | 63.4232 | -61.6974 | -0.25177 | 0.018311 | -0.01831 | -0.1831 | -0.6958 | -0.31586 | 0.009156 | 0.23346 | 59.9625 | 59.6466 | 124.0997 | 124.8138 | -0.01831 | 124.8047 | 65.126 | -0.31586 | 124.8138 | -0.01831 | 65.126 | 124.0997 | 124.8047 | -125.0473 | -125.1114
1163.6406 | 124.9969 | -61.4136 | 63.4323 | 0.11162 | 0.012042 | 0.019814 | 0.0023583 | 0.069957 | -0.0012177 | 0.070735 | -61.5143 | 63.382 | -61.6653 | -61.5692 | 62.6587 | 3.6804 | -1.3916 | -1.8494 | 63.4506 | -61.6882 | -0.25177 | -0.050354 | -0.10071 | -0.15564 | -0.77362 | -0.27466 | 0.018311 | 0.15106 | 60.022 | 59.5642 | 124.0723 | 124.7955 | -0.10071 | 124.8642 | 65.094 | -0.27466 | 124.7955 | -0.10071 | 65.094 | 124.0723 | 124.8642 | -125.0977 | -125.1205
1164.6406 | 124.9924 | -61.4044 | 63.4186 | -0.0028231 | 0.01546 | 0.01255 | 0.0036401 | 0.068889 | -0.0033539 | 0.069239 | -61.3953 | 63.4323 | -61.6425 | -61.5921 | 62.7045 | 3.7765 | -1.4923 | -1.8448 | 63.4323 | -61.6745 | -0.23804 | 0.013733 | 0.009155 | -0.18768 | -0.71411 | -0.27008 | 0.013733 | 0.24719 | 59.9121 | 59.5596 | 124.1089 | 124.8367 | 0.009155 | 124.8367 | 65.181 | -0.27008 | 124.8367 | 0.009155 | 65.181 | 124.1089 | 124.8367 | -125.061 | -125.0931
1165.6406 | 124.9969 | -61.3998 | 63.4369 | -0.056229 | 0.012042 | 0.014473 | 0.0038537 | 0.066539 | -0.0020721 | 0.068599 | -61.3678 | 63.4644 | -61.6287 | -61.5555 | 62.7228 | 3.804 | -1.5289 | -1.8768 | 63.4415 | -61.6562 | -0.22888 | 0.027465 | 0.032043 | -0.15564 | -0.71411 | -0.25635 | 0.004577 | 0.26093 | 59.8709 | 59.523 | 124.1226 | 124.8642 | 0.032043 | 124.8413 | 65.2039 | -0.25635 | 124.8642 | 0.032043 | 65.2039 | 124.1226 | 124.8413 | -125.0656 | -125.0931
1166.6406 | 124.9878 | -61.377 | 63.4277 | 0.0048064 | 0.012256 | 0.012123 | 0.0044945 | 0.068035 | -0.0012177 | 0.068599 | -61.409 | 63.4506 | -61.6287 | -61.6104 | 62.6724 | 3.7903 | -1.561 | -1.973 | 63.4232 | -61.6882 | -0.25177 | 0.022889 | -0.032044 | -0.23346 | -0.75531 | -0.31128 | -0.004577 | 0.21973 | 59.816 | 59.404 | 124.0494 | 124.8276 | -0.032044 | 124.8001 | 65.1672 | -0.31128 | 124.8276 | -0.032044 | 65.1672 | 124.0494 | 124.8001 | -125.0565 | -125.116
1167.6406 | 125.1205 | -61.3312 | 63.3865 | 0.14976 | 0.0099057 | 0.017037 | -0.0010597 | 0.066753 | -0.0018585 | 0.070521 | -61.5372 | 63.327 | -61.6104 | -61.5143 | 62.764 | 3.9413 | -1.767 | -1.9043 | 63.3911 | -61.6241 | -0.27924 | -0.05951 | -0.20599 | -0.18311 | -0.62256 | -0.29297 | 0.004577 | 0.073243 | 59.5642 | 59.4269 | 124.0952 | 124.6582 | -0.20599 | 124.7223 | 65.2725 | -0.29297 | 124.6582 | -0.20599 | 65.2725 | 124.0952 | 124.7223 | -124.9969 | -125.0107
1168.6406 | 124.9695 | -61.3632 | 63.4277 | -0.056229 | 0.012469 | 0.012764 | 0.0053491 | 0.066326 | -0.0016449 | 0.068599 | -61.3724 | 63.4644 | -61.6013 | -61.5829 | 62.6999 | 3.8406 | -1.6434 | -2.0233 | 63.4735 | -61.6653 | -0.23804 | 0.036621 | -0.009155 | -0.21973 | -0.72784 | -0.30212 | 0.045777 | 0.22888 | 59.7198 | 59.3399 | 124.0631 | 124.8276 | -0.009155 | 124.8367 | 65.2039 | -0.30212 | 124.8276 | -0.009155 | 65.2039 | 124.0631 | 124.8367 | -125.029 | -125.0931
1169.6406 | 125.029 | -61.3403 | 63.4644 | -0.10963 | 0.012042 | 0.0082779 | 0.0040673 | 0.068676 | -0.00036306 | 0.067531 | -61.5234 | 63.4323 | -61.6104 | -61.5143 | 62.7502 | 3.9185 | -1.6754 | -2.0142 | 63.4644 | -61.6287 | -0.27008 | -0.032043 | -0.18311 | -0.17395 | -0.71411 | -0.28839 | 0 | 0.086976 | 59.6649 | 59.3262 | 124.0906 | 124.7726 | -0.18311 | 124.8047 | 65.2588 | -0.28839 | 124.7726 | -0.18311 | 65.2588 | 124.0906 | 124.8047 | -125.0748 | -125.0931
1170.6406 | 125.0153 | -61.3541 | 63.4506 | -0.048599 | 0.013751 | 0.016609 | 0.0034265 | 0.068248 | -0.0014313 | 0.069026 | -61.3312 | 63.4598 | -61.6104 | -61.5463 | 62.7365 | 3.9963 | -1.7212 | -2.1103 | 63.4781 | -61.6379 | -0.25635 | 0.009155 | 0.022888 | -0.19226 | -0.71411 | -0.28381 | 0.027465 | 0.27924 | 59.6329 | 59.2438 | 124.0906 | 124.8138 | 0.022888 | 124.8322 | 65.3503 | -0.28381 | 124.8138 | 0.022888 | 65.3503 | 124.0906 | 124.8322 | -125.061 | -125.0885
1171.6406 | 125.0427 | -61.3541 | 63.4644 | -0.079117 | 0.010974 | 0.015968 | 0.0044945 | 0.070171 | -0.0016449 | 0.069453 | -61.322 | 63.4689 | -61.615 | -61.5234 | 62.7319 | 3.9642 | -1.7761 | -2.1469 | 63.501 | -61.6516 | -0.26093 | 0.004578 | 0.032044 | -0.16937 | -0.73242 | -0.29755 | 0.036622 | 0.29297 | 59.5779 | 59.2072 | 124.086 | 124.823 | 0.032044 | 124.855 | 65.3183 | -0.29755 | 124.823 | 0.032044 | 65.3183 | 124.086 | 124.855 | -125.0793 | -125.116
1172.6406 | 125.029 | -61.3449 | 63.4415 | 0.18028 | 0.0094785 | 0.017464 | 0.00086295 | 0.066112 | -0.0014313 | 0.071376 | -61.3861 | 63.4415 | -61.5967 | -61.5555 | 62.7274 | 4.01 | -1.9592 | -2.2293 | 63.4598 | -61.6516 | -0.25177 | 0 | -0.041198 | -0.21057 | -0.71411 | -0.3067 | 0.018311 | 0.21057 | 59.3857 | 59.1156 | 124.0723 | 124.7864 | -0.041198 | 124.8047 | 65.3549 | -0.3067 | 124.7864 | -0.041198 | 65.3549 | 124.0723 | 124.8047 | -125.0381 | -125.0931
1173.6406 | 124.9924 | -61.3312 | 63.4644 | -0.033341 | 0.012469 | 0.0097733 | 0.0044945 | 0.06718 | -0.0027131 | 0.071162 | -61.322 | 63.4918 | -61.5601 | -61.528 | 62.7274 | 4.0741 | -1.8951 | -2.2751 | 63.4735 | -61.6425 | -0.22888 | 0.027466 | 0.009156 | -0.19684 | -0.737 | -0.31128 | 0.009156 | 0.23804 | 59.436 | 59.0561 | 124.0585 | 124.823 | 0.009156 | 124.8047 | 65.4053 | -0.31128 | 124.823 | 0.009156 | 65.4053 | 124.0585 | 124.8047 | -125.0244 | -125.1068
1174.6406 | 125.0381 | -61.3312 | 63.4689 | -0.056229 | 0.011401 | 0.013405 | 0.0025719 | 0.069103 | -0.0018585 | 0.069026 | -61.2946 | 63.4644 | -61.5555 | -61.5097 | 62.7136 | 4.097 | -1.8951 | -2.3026 | 63.4644 | -61.6333 | -0.2243 | -0.004578 | 0.036621 | -0.17853 | -0.75531 | -0.30212 | -0.004578 | 0.26093 | 59.436 | 59.0286 | 124.0448 | 124.7955 | 0.036621 | 124.7955 | 65.4282 | -0.30212 | 124.7955 | 0.036621 | 65.4282 | 124.0448 | 124.7955 | -125.0244 | -125.1022
1175.6406 | 125.0061 | -61.3037 | 63.4872 | -0.14015 | 0.012683 | 0.0078507 | 0.0012903 | 0.06718 | -0.0010041 | 0.070948 | -61.2762 | 63.5284 | -61.5601 | -61.5097 | 62.7228 | 4.1428 | -1.973 | -2.3483 | 63.501 | -61.6013 | -0.25635 | 0.041198 | 0.027466 | -0.20599 | -0.76447 | -0.29755 | 0.013733 | 0.28381 | 59.3308 | 58.9554 | 124.0265 | 124.8322 | 0.027466 | 124.8047 | 65.4465 | -0.29755 | 124.8322 | 0.027466 | 65.4465 | 124.0265 | 124.8047 | -125.0473 | -125.0885
1176.6406 | 125.0519 | -61.3083 | 63.4964 | -0.26985 | 0.011828 | 0.011696 | 0.00086295 | 0.068462 | 6.414e-05 | 0.067531 | -61.3174 | 63.5056 | -61.5417 | -61.4868 | 62.7319 | 4.1245 | -1.9867 | -2.3895 | 63.533 | -61.5784 | -0.23346 | 0.009155 | -0.009155 | -0.17853 | -0.76446 | -0.27008 | 0.036621 | 0.2243 | 59.3216 | 58.9188 | 124.0402 | 124.8138 | -0.009155 | 124.8413 | 65.4327 | -0.27008 | 124.8138 | -0.009155 | 65.4327 | 124.0402 | 124.8413 | -125.0381 | -125.0748
1177.6406 | 124.942 | -61.3358 | 63.5056 | 0.10399 | 0.01076 | 0.013619 | 0.0036401 | 0.06953 | 0.0041229 | 0.071589 | -61.3815 | 63.4872 | -61.5875 | -61.5143 | 63.0386 | 4.2984 | -2.092 | -2.4261 | 63.5193 | -61.5829 | -0.25177 | -0.01831 | -0.045777 | -0.17853 | -0.46692 | -0.24719 | 0.013733 | 0.20599 | 59.2438 | 58.9096 | 124.3744 | 124.823 | -0.045777 | 124.855 | 65.6342 | -0.24719 | 124.823 | -0.045777 | 65.6342 | 124.3744 | 124.855 | -125.0931 | -125.0885
1178.6406 | 125.0565 | -61.29 | 63.5056 | -0.19356 | 0.010547 | 0.014046 | 0.0012903 | 0.066967 | -0.0010041 | 0.070094 | -61.2854 | 63.5239 | -61.5555 | -61.4594 | 62.7594 | 4.2206 | -2.1378 | -2.5131 | 63.501 | -61.5601 | -0.2655 | 0.018311 | 0.004578 | -0.16937 | -0.74615 | -0.27008 | -0.004577 | 0.27008 | 59.1522 | 58.7769 | 124.0494 | 124.8138 | 0.004578 | 124.791 | 65.5106 | -0.27008 | 124.8138 | 0.004578 | 65.5106 | 124.0494 | 124.791 | -125.061 | -125.0656
1179.6406 | 125.0565 | -61.2991 | 63.5284 | -0.14778 | 0.010333 | 0.011269 | 0.0040673 | 0.067608 | 0.00049134 | 0.069026 | -61.3083 | 63.4918 | -61.5509 | -61.496 | 62.7411 | 4.2252 | -2.1286 | -2.5726 | 63.5193 | -61.5646 | -0.25177 | -0.036621 | -0.009156 | -0.19684 | -0.78735 | -0.2655 | -0.009155 | 0.24261 | 59.1705 | 58.7265 | 124.0402 | 124.791 | -0.009156 | 124.8184 | 65.5243 | -0.2655 | 124.791 | -0.009156 | 65.5243 | 124.0402 | 124.8184 | -125.0793 | -125.0931
1180.6406 | 125.0336 | -61.3037 | 63.501 | -0.13252 | 0.012469 | 0.011269 | 0.0040673 | 0.066753 | -0.0016449 | 0.069453 | -61.2762 | 63.5284 | -61.528 | -61.4639 | 62.7457 | 4.2801 | -2.2202 | -2.6276 | 63.5239 | -61.5829 | -0.2243 | 0.027465 | 0.027466 | -0.16022 | -0.75531 | -0.27924 | 0.022888 | 0.25177 | 59.0836 | 58.6761 | 124.0494 | 124.8322 | 0.027466 | 124.8276 | 65.5838 | -0.27924 | 124.8322 | 0.027466 | 65.5838 | 124.0494 | 124.8276 | -125.029 | -125.0839
1181.6406 | 125.0473 | -61.2946 | 63.533 | -0.26985 | 0.013537 | 0.0093459 | 0.0025719 | 0.066539 | -0.00079046 | 0.070735 | -61.2946 | 63.5239 | -61.5234 | -61.4731 | 62.7457 | 4.2618 | -2.2476 | -2.7054 | 63.5513 | -61.5738 | -0.22888 | -0.009155 | 0 | -0.17853 | -0.78735 | -0.27924 | 0.018311 | 0.22888 | 59.0469 | 58.5892 | 124.0402 | 124.8184 | 0 | 124.8459 | 65.5563 | -0.27924 | 124.8184 | 0 | 65.5563 | 124.0402 | 124.8459 | -125.0565 | -125.1068
1182.6406 | 124.9924 | -61.3083 | 63.4872 | -0.010452 | 0.013965 | 0.015114 | 0.0027855 | 0.068035 | -0.00014946 | 0.067531 | -61.29 | 63.5193 | -61.5509 | -61.5189 | 62.6816 | 4.216 | -2.3346 | -2.8473 | 63.5376 | -61.5921 | -0.24261 | 0.032043 | 0.018311 | -0.21057 | -0.80566 | -0.28381 | 0.050354 | 0.26093 | 58.9737 | 58.461 | 123.9899 | 124.8276 | 0.018311 | 124.8459 | 65.5243 | -0.28381 | 124.8276 | 0.018311 | 65.5243 | 123.9899 | 124.8459 | -125.0381 | -125.0793
1183.6406 | 124.9832 | -61.2671 | 63.5513 | -0.26222 | 0.010119 | 0.011696 | -0.0012733 | 0.069316 | 6.414e-05 | 0.071803 | -61.3312 | 63.5147 | -61.5417 | -61.4777 | 62.6495 | 4.2389 | -2.3163 | -2.829 | 63.5788 | -61.5601 | -0.27466 | -0.036622 | -0.064087 | -0.21057 | -0.90179 | -0.29297 | 0.027465 | 0.21057 | 58.9508 | 58.4381 | 123.9166 | 124.7818 | -0.064087 | 124.8459 | 65.506 | -0.29297 | 124.7818 | -0.064087 | 65.506 | 123.9166 | 124.8459 | -125.0931 | -125.1114
1184.6406 | 124.9924 | -61.2854 | 63.5559 | -0.2317 | 0.011401 | 0.011482 | 0.0015039 | 0.067394 | -0.0010041 | 0.070735 | -61.3174 | 63.5239 | -61.5463 | -61.4914 | 62.7045 | 4.2435 | -2.4353 | -2.9297 | 63.5788 | -61.5417 | -0.26093 | -0.032043 | -0.032044 | -0.20599 | -0.85144 | -0.25635 | 0.022888 | 0.22888 | 58.8501 | 58.3557 | 123.9899 | 124.8093 | -0.032044 | 124.8642 | 65.5289 | -0.25635 | 124.8093 | -0.032044 | 65.5289 | 123.9899 | 124.8642 | -125.1022 | -125.0977
1185.6406 | 124.9878 | -61.2534 | 63.5742 | -0.025711 | 0.011828 | 0.013619 | 0.0010767 | 0.066112 | -0.00036306 | 0.071162 | -61.29 | 63.5376 | -61.5143 | -61.4914 | 62.7045 | 4.2892 | -2.417 | -2.9938 | 63.5742 | -61.528 | -0.26093 | -0.036621 | -0.036621 | -0.23804 | -0.86975 | -0.27466 | 0 | 0.2243 | 58.8364 | 58.2596 | 123.9578 | 124.791 | -0.036621 | 124.8276 | 65.5426 | -0.27466 | 124.791 | -0.036621 | 65.5426 | 123.9578 | 124.8276 | -125.0885 | -125.1022
1186.6406 | 124.9878 | -61.2671 | 63.588 | 1.4925 | 0.0086239 | 0.0080643 | -0.00041865 | 0.065044 | -0.00057686 | 0.069453 | -61.3358 | 63.5147 | -61.5463 | -61.4822 | 62.7319 | 4.2938 | -2.4857 | -3.0899 | 63.5651 | -61.528 | -0.27924 | -0.073243 | -0.068664 | -0.21515 | -0.85602 | -0.26093 | -0.022889 | 0.21057 | 58.7814 | 58.1772 | 123.999 | 124.7818 | -0.068664 | 124.8322 | 65.5609 | -0.26093 | 124.7818 | -0.068664 | 65.5609 | 123.999 | 124.8322 | -125.1343 | -125.116
1187.6562 | 124.9695 | -61.2762 | 63.5468 | 0.39391 | 0.012256 | 0.0082779 | 0.0023583 | 0.066753 | 0.00049134 | 0.068599 | -61.2854 | 63.5284 | -61.5097 | -61.5097 | 62.6495 | 4.2938 | -2.6733 | -3.2501 | 63.5376 | -61.5646 | -0.23346 | -0.018311 | -0.009155 | -0.23346 | -0.89722 | -0.28839 | -0.009155 | 0.2243 | 58.6029 | 58.0261 | 123.9258 | 124.8047 | -0.009155 | 124.8138 | 65.5701 | -0.28839 | 124.8047 | -0.009155 | 65.5701 | 123.9258 | 124.8138 | -125.0565 | -125.1114
1188.6406 | 124.9969 | -61.2442 | 63.5696 | -0.2317 | 0.010333 | 0.012123 | 0.0025719 | 0.066326 | -0.0012177 | 0.06988 | -61.2762 | 63.5559 | -61.4685 | -61.4639 | 62.7136 | 4.3945 | -2.6413 | -3.2364 | 63.5651 | -61.5326 | -0.2243 | -0.013733 | -0.032043 | -0.21973 | -0.85602 | -0.28839 | -0.004578 | 0.19226 | 58.6029 | 58.0078 | 123.9578 | 124.8001 | -0.032043 | 124.8093 | 65.6387 | -0.28839 | 124.8001 | -0.032043 | 65.6387 | 123.9578 | 124.8093 | -125.0381 | -125.1022
1189.6406 | 124.9603 | -61.2671 | 63.588 | -0.26985 | 0.011401 | 0.015755 | 8.546e-06 | 0.064617 | -0.0012177 | 0.069453 | -61.2808 | 63.5422 | -61.4868 | -61.3541 | 62.9379 | 4.5319 | -2.8839 | -3.2776 | 63.5925 | -61.5372 | -0.21973 | -0.045777 | -0.013733 | -0.086975 | -0.65002 | -0.27008 | 0.004577 | 0.20599 | 58.3832 | 57.9895 | 124.205 | 124.8093 | -0.013733 | 124.8596 | 65.799 | -0.27008 | 124.8093 | -0.013733 | 65.799 | 124.205 | 124.8596 | -125.0748 | -125.1251
1190.6406 | 124.9649 | -61.2762 | 63.5925 | -0.25459 | 0.0090513 | 0.0097733 | 0.0015039 | 0.065471 | 0.00049134 | 0.06988 | -61.2717 | 63.5513 | -61.4685 | -61.4548 | 62.6907 | 4.6555 | -2.8107 | -3.5843 | 63.5925 | -61.5097 | -0.19226 | -0.041198 | 0.004578 | -0.17853 | -0.90179 | -0.23346 | 0 | 0.19684 | 58.4656 | 57.692 | 123.967 | 124.8276 | 0.004578 | 124.8688 | 65.9317 | -0.23346 | 124.8276 | 0.004578 | 65.9317 | 123.967 | 124.8688 | -125.061 | -125.1022
1191.6406 | 124.9741 | -61.2259 | 63.5834 | -0.24696 | 0.0090513 | 0.011482 | 0.0012903 | 0.06419 | -0.0024995 | 0.069453 | -61.2579 | 63.5742 | -61.4731 | -61.441 | 62.6816 | 4.509 | -2.8107 | -3.479 | 63.6017 | -61.5051 | -0.24719 | -0.009155 | -0.032044 | -0.21515 | -0.90179 | -0.27924 | 0.018311 | 0.21515 | 58.4152 | 57.7469 | 123.9075 | 124.8001 | -0.032044 | 124.8276 | 65.7349 | -0.27924 | 124.8001 | -0.032044 | 65.7349 | 123.9075 | 124.8276 | -125.0565 | -125.0885
1192.6406 | 125.0107 | -61.2213 | 63.5971 | -0.29274 | 0.010333 | 0.012764 | 0.00086295 | 0.065471 | -0.0031403 | 0.06988 | -61.235 | 63.5834 | -61.4548 | -61.4319 | 62.6816 | 4.5731 | -2.8793 | -3.5156 | 63.6246 | -61.5189 | -0.23346 | -0.013733 | -0.013733 | -0.21057 | -0.91553 | -0.29755 | 0.027466 | 0.21973 | 58.342 | 57.7057 | 123.9029 | 124.8047 | -0.013733 | 124.8459 | 65.7944 | -0.29755 | 124.8047 | -0.013733 | 65.7944 | 123.9029 | 124.8459 | -125.0519 | -125.116
1193.6406 | 124.9878 | -61.2305 | 63.5971 | -0.30037 | 0.012042 | 0.0065689 | 0.0010767 | 0.06718 | -0.00036306 | 0.070308 | -61.2442 | 63.5651 | -61.4548 | -61.4227 | 62.6907 | 4.5868 | -2.9434 | -3.5889 | 63.6246 | -61.4868 | -0.2243 | -0.032044 | -0.013733 | -0.19226 | -0.90637 | -0.25635 | 0.027466 | 0.21057 | 58.287 | 57.6416 | 123.9212 | 124.7955 | -0.013733 | 124.855 | 65.8173 | -0.25635 | 124.7955 | -0.013733 | 65.8173 | 123.9212 | 124.855 | -125.0519 | -125.0839
1194.6406 | 125.0427 | -61.2076 | 63.6017 | -0.18593 | 0.011828 | 0.013405 | 0.0040673 | 0.066753 | 0.00049134 | 0.068812 | -61.1847 | 63.5834 | -61.441 | -61.3678 | 62.7136 | 4.6417 | -3.0716 | -3.6392 | 63.6063 | -61.4914 | -0.23346 | -0.018311 | 0.022889 | -0.16022 | -0.88806 | -0.28381 | 0.004577 | 0.25635 | 58.136 | 57.5684 | 123.9212 | 124.791 | 0.022889 | 124.8138 | 65.8493 | -0.28381 | 124.791 | 0.022889 | 65.8493 | 123.9212 | 124.8138 | -125.0427 | -125.0931
1195.6406 | 125.0153 | -61.1938 | 63.6292 | -0.14778 | 0.012683 | 0.012978 | 0.0051355 | 0.066326 | -0.0014313 | 0.068812 | -61.1801 | 63.6292 | -61.441 | -61.3495 | 62.7365 | 4.6783 | -3.1311 | -3.717 | 63.6292 | -61.4731 | -0.24719 | 0 | 0.013733 | -0.15564 | -0.89264 | -0.27923 | 0 | 0.26093 | 58.0627 | 57.4768 | 123.9304 | 124.823 | 0.013733 | 124.823 | 65.8722 | -0.27923 | 124.823 | 0.013733 | 65.8722 | 123.9304 | 124.823 | -125.0702 | -125.1022
1196.6406 | 124.9741 | -61.1938 | 63.6337 | -0.27748 | 0.011401 | 0.010414 | 0.0027855 | 0.066753 | 6.414e-05 | 0.068812 | -61.2122 | 63.6108 | -61.4273 | -61.3998 | 62.6862 | 4.66 | -3.1494 | -3.8452 | 63.6337 | -61.4868 | -0.23346 | -0.022888 | -0.01831 | -0.20599 | -0.94757 | -0.29297 | 0 | 0.21515 | 58.0444 | 57.3486 | 123.88 | 124.8047 | -0.01831 | 124.8276 | 65.8539 | -0.29297 | 124.8047 | -0.01831 | 65.8539 | 123.88 | 124.8276 | -125.061 | -125.1205
1197.6406 | 124.9649 | -61.203 | 63.5925 | -0.23933 | 0.01076 | 0.0149 | 0.0032129 | 0.066112 | -0.00014946 | 0.070521 | -61.2488 | 63.6154 | -61.441 | -61.4639 | 62.6404 | 4.6143 | -3.3234 | -4.0054 | 63.6246 | -61.4777 | -0.23804 | 0.022888 | -0.045776 | -0.26093 | -0.95215 | -0.27466 | 0.032044 | 0.19226 | 57.8796 | 57.1976 | 123.8434 | 124.8184 | -0.045776 | 124.8276 | 65.8173 | -0.27466 | 124.8184 | -0.045776 | 65.8173 | 123.8434 | 124.8276 | -125.0336 | -125.0702
1198.6406 | 125.0381 | -61.1526 | 63.5971 | -0.18593 | 0.010974 | 0.014046 | 0.0025719 | 0.068248 | -0.0010041 | 0.067103 | -61.1389 | 63.6337 | -61.4136 | -61.3449 | 62.7457 | 4.7104 | -3.36 | -3.9597 | 63.6337 | -61.4319 | -0.26093 | 0.036621 | 0.013733 | -0.19226 | -0.85144 | -0.27924 | 0.036621 | 0.27466 | 57.7927 | 57.193 | 123.8983 | 124.7864 | 0.013733 | 124.7864 | 65.863 | -0.27924 | 124.7864 | 0.013733 | 65.863 | 123.8983 | 124.7864 | -125.0107 | -125.029
1199.6406 | 125.029 | -61.1572 | 63.6292 | -0.14778 | 0.01076 | 0.014473 | 0.0051355 | 0.068462 | -0.00079046 | 0.070521 | -61.1252 | 63.62 | -61.4044 | -61.3312 | 62.7548 | 4.7607 | -3.4561 | -4.0558 | 63.6292 | -61.4456 | -0.24719 | -0.009155 | 0.032044 | -0.17395 | -0.87433 | -0.28839 | 0 | 0.27924 | 57.7011 | 57.1014 | 123.912 | 124.7772 | 0.032044 | 124.7864 | 65.918 | -0.28839 | 124.7772 | 0.032044 | 65.918 | 123.912 | 124.7864 | -125.0336 | -125.0748
1200.6406 | 125.0198 | -61.1618 | 63.652 | -0.19356 | 0.011401 | 0.016396 | 0.0038537 | 0.068676 | -0.0039947 | 0.070094 | -61.1298 | 63.6337 | -61.3861 | -61.322 | 62.7365 | 4.7562 | -3.5706 | -4.1428 | 63.6383 | -61.4365 | -0.2243 | -0.018311 | 0.032043 | -0.16022 | -0.91553 | -0.27466 | -0.013733 | 0.25635 | 57.5912 | 57.019 | 123.8983 | 124.7955 | 0.032043 | 124.8001 | 65.918 | -0.27466 | 124.7955 | 0.032043 | 65.918 | 123.8983 | 124.8001 | -125.0381 | -125.0885
1201.6406 | 125.0336 | -61.1664 | 63.6246 | -0.094376 | 0.011188 | 0.014259 | 0.0025719 | 0.067394 | -0.00057686 | 0.069026 | -61.116 | 63.6154 | -61.4273 | -61.3495 | 62.7136 | 4.7562 | -3.6667 | -4.248 | 63.6429 | -61.4456 | -0.26093 | -0.009156 | 0.050354 | -0.18311 | -0.91095 | -0.27924 | 0.01831 | 0.31128 | 57.4997 | 56.9183 | 123.88 | 124.7818 | 0.050354 | 124.8093 | 65.9225 | -0.27924 | 124.7818 | 0.050354 | 65.9225 | 123.88 | 124.8093 | -125.0519 | -125.0702
1202.6406 | 124.9969 | -61.1572 | 63.6292 | 0.11925 | 0.011828 | 0.012337 | 0.0025719 | 0.068462 | 0.0013457 | 0.069239 | -61.1801 | 63.6292 | -61.4044 | -61.4136 | 62.6312 | 4.6509 | -3.7399 | -4.3716 | 63.6246 | -61.4548 | -0.24719 | 0 | -0.022888 | -0.25635 | -0.99792 | -0.29755 | -0.004577 | 0.2243 | 57.4173 | 56.7856 | 123.7885 | 124.7864 | -0.022888 | 124.7818 | 65.8081 | -0.29755 | 124.7864 | -0.022888 | 65.8081 | 123.7885 | 124.7818 | -125.0336 | -125.0839
1203.6406 | 125.0061 | -61.1664 | 63.6429 | -0.20119 | 0.010974 | 0.0093459 | 0.0042809 | 0.067394 | 6.414e-05 | 0.069026 | -61.0794 | 63.6383 | -61.4044 | -61.3129 | 62.7274 | 4.7607 | -3.804 | -4.3671 | 63.6475 | -61.4456 | -0.23804 | -0.004577 | 0.086975 | -0.14648 | -0.91553 | -0.27924 | 0.004578 | 0.32501 | 57.3624 | 56.7993 | 123.8937 | 124.8047 | 0.086975 | 124.8138 | 65.9271 | -0.27924 | 124.8047 | 0.086975 | 65.9271 | 123.8937 | 124.8138 | -125.0473 | -125.0885
1204.6406 | 124.9832 | -61.1481 | 63.6429 | -0.14778 | 0.01076 | 0.011269 | 0.0029993 | 0.068889 | -0.0012177 | 0.070308 | -61.0886 | 63.6475 | -61.3724 | -61.322 | 62.7136 | 4.7516 | -3.9047 | -4.4769 | 63.6475 | -61.4319 | -0.2243 | 0.004578 | 0.059509 | -0.17395 | -0.92926 | -0.28381 | 0.004578 | 0.28381 | 57.2433 | 56.6711 | 123.8617 | 124.7955 | 0.059509 | 124.7955 | 65.8997 | -0.28381 | 124.7955 | 0.059509 | 65.8997 | 123.8617 | 124.7955 | -125.0153 | -125.0748
1205.6406 | 125.0015 | -61.1298 | 63.6475 | -0.04097 | 0.010547 | 0.012764 | 0.0036401 | 0.069316 | -0.0014313 | 0.069667 | -61.0977 | 63.6612 | -61.3998 | -61.3174 | 62.6862 | 4.8019 | -3.9551 | -4.541 | 63.6566 | -61.4227 | -0.27008 | 0.013733 | 0.032044 | -0.18768 | -0.9613 | -0.29297 | 0.009155 | 0.30212 | 57.1747 | 56.5887 | 123.8159 | 124.791 | 0.032044 | 124.7864 | 65.9317 | -0.29297 | 124.791 | 0.032044 | 65.9317 | 123.8159 | 124.7864 | -125.0473 | -125.0702
1206.6406 | 125.0015 | -61.1343 | 63.6612 | -0.14015 | 0.011188 | 0.014046 | 0.0027855 | 0.068676 | -0.0010041 | 0.069239 | -61.0794 | 63.6475 | -61.3724 | -61.3037 | 62.6907 | 4.8843 | -4.0283 | -4.628 | 63.6749 | -61.4182 | -0.23804 | -0.013733 | 0.054931 | -0.16937 | -0.97046 | -0.28381 | 0.013733 | 0.29297 | 57.106 | 56.5063 | 123.8251 | 124.7818 | 0.054931 | 124.8093 | 66.0187 | -0.28381 | 124.7818 | 0.054931 | 66.0187 | 123.8251 | 124.8093 | -125.0336 | -125.0793
1207.6406 | 125.061 | -61.1298 | 63.6246 | 0.19554 | 0.010119 | 0.011482 | 0.00022215 | 0.068248 | 0.0011321 | 0.070948 | -61.1435 | 63.6154 | -61.4044 | -61.3312 | 62.677 | 4.8798 | -4.2572 | -4.7653 | 63.62 | -61.4319 | -0.27466 | -0.009156 | -0.013733 | -0.20142 | -0.94757 | -0.30212 | -0.004578 | 0.26093 | 56.8726 | 56.3644 | 123.8068 | 124.7452 | -0.013733 | 124.7498 | 66.0095 | -0.30212 | 124.7452 | -0.013733 | 66.0095 | 123.8068 | 124.7498 | -125.029 | -125.0565
1208.6406 | 124.9924 | -61.1343 | 63.6749 | -0.033341 | 0.012469 | 0.014259 | 0.0036401 | 0.068035 | -0.00014946 | 0.068385 | -61.1069 | 63.6612 | -61.3724 | -61.3266 | 62.6541 | 4.8248 | -4.2023 | -4.9118 | 63.6612 | -61.4273 | -0.23804 | -0.013733 | 0.027465 | -0.19226 | -1.0208 | -0.29297 | -0.013733 | 0.2655 | 56.9321 | 56.2225 | 123.7885 | 124.7955 | 0.027465 | 124.7955 | 65.9592 | -0.29297 | 124.7955 | 0.027465 | 65.9592 | 123.7885 | 124.7955 | -125.0473 | -125.1022
1209.6406 | 124.9741 | -61.1252 | 63.6749 | -0.04097 | 0.01076 | 0.010841 | 0.0027855 | 0.067821 | 6.414e-05 | 0.070094 | -61.0886 | 63.6703 | -61.3907 | -61.3266 | 62.6541 | 4.8523 | -4.3121 | -4.9484 | 63.6887 | -61.4136 | -0.2655 | -0.004578 | 0.036621 | -0.20142 | -1.0208 | -0.28839 | 0.013733 | 0.30212 | 56.813 | 56.1768 | 123.7793 | 124.7955 | 0.036621 | 124.8138 | 65.9775 | -0.28839 | 124.7955 | 0.036621 | 65.9775 | 123.7793 | 124.8138 | -125.0656 | -125.0885
1210.6406 | 125.0015 | -61.1023 | 63.6703 | -1.5821 | 0.012042 | 0.014687 | 0.0010767 | 0.067608 | -0.0031403 | 0.069239 | -61.1023 | 63.6841 | -61.3861 | -61.2854 | 62.6953 | 4.9118 | -4.4037 | -4.9988 | 63.7024 | -61.4182 | -0.28381 | 0.013733 | 0 | -0.18311 | -0.97504 | -0.31586 | 0.032044 | 0.28381 | 56.6986 | 56.1035 | 123.7976 | 124.7864 | 0 | 124.8047 | 66.0141 | -0.31586 | 124.7864 | 0 | 66.0141 | 123.7976 | 124.8047 | -125.0565 | -125.0885
1211.6406 | 124.9924 | -61.1023 | 63.6749 | -0.10201 | 0.010119 | 0.013619 | 0.0029993 | 0.068248 | -0.0016449 | 0.070521 | -61.2808 | 63.6749 | -61.3907 | -61.3037 | 62.6816 | 4.921 | -4.4632 | -5.0674 | 63.6749 | -61.409 | -0.28839 | 0 | -0.17853 | -0.20142 | -0.99335 | -0.3067 | 0 | 0.10986 | 56.6391 | 56.0349 | 123.7839 | 124.7772 | -0.17853 | 124.7772 | 66.0233 | -0.3067 | 124.7772 | -0.17853 | 66.0233 | 123.7839 | 124.7772 | -125.0656 | -125.0839
1212.6562 | 125.1068 | -61.084 | 63.6337 | 0.12688 | 0.010333 | 0.016609 | -0.0040503 | 0.068248 | -0.0020721 | 0.070308 | -61.0474 | 63.588 | -61.3632 | -61.2579 | 62.7228 | 4.9942 | -4.7562 | -5.1865 | 63.6383 | -61.3586 | -0.27924 | -0.045776 | 0.036621 | -0.17395 | -0.91095 | -0.27466 | 0.004578 | 0.31586 | 56.3278 | 55.8975 | 123.8068 | 124.6719 | 0.036621 | 124.7223 | 66.0782 | -0.27466 | 124.6719 | 0.036621 | 66.0782 | 123.8068 | 124.7223 | -124.9969 | -124.9924
1213.6406 | 124.9741 | -61.0794 | 63.6978 | -0.11726 | 0.012256 | 0.01255 | 0.0036401 | 0.068248 | -0.0020721 | 0.070308 | -61.0519 | 63.6887 | -61.3358 | -61.2991 | 62.6495 | 4.8889 | -4.6646 | -5.3467 | 63.6749 | -61.4182 | -0.25635 | -0.009155 | 0.027466 | -0.21973 | -1.0483 | -0.33874 | -0.022888 | 0.28381 | 56.4148 | 55.7327 | 123.7289 | 124.7681 | 0.027466 | 124.7543 | 65.9683 | -0.33874 | 124.7681 | 0.027466 | 65.9683 | 123.7289 | 124.7543 | -125.0336 | -125.116
1214.6406 | 124.9878 | -61.0886 | 63.6932 | -0.063858 | 0.012683 | 0.010201 | 0.0034265 | 0.067608 | -0.0014313 | 0.06988 | -61.0428 | 63.7024 | -61.3403 | -61.2762 | 62.6495 | 4.9667 | -4.747 | -5.4611 | 63.6932 | -61.3815 | -0.25177 | 0.009156 | 0.045776 | -0.18768 | -1.0437 | -0.29297 | 0 | 0.29755 | 56.3416 | 55.6274 | 123.7381 | 124.791 | 0.045776 | 124.7818 | 66.0553 | -0.29297 | 124.791 | 0.045776 | 66.0553 | 123.7381 | 124.7818 | -125.0336 | -125.0748
1215.6406 | 124.9969 | -61.116 | 63.7024 | -0.025711 | 0.012042 | 0.013619 | 0.0032129 | 0.06718 | -0.0020721 | 0.070948 | -61.0611 | 63.7161 | -61.3449 | -61.3129 | 62.6221 | 4.8798 | -4.8294 | -5.6213 | 63.7482 | -61.3953 | -0.22888 | 0.013732 | 0.054932 | -0.19684 | -1.0803 | -0.27924 | 0.045776 | 0.28381 | 56.2866 | 55.4947 | 123.7381 | 124.8322 | 0.054932 | 124.8642 | 65.9958 | -0.27924 | 124.8322 | 0.054932 | 65.9958 | 123.7381 | 124.8642 | -125.0473 | -125.0977
1216.6406 | 124.9878 | -61.1114 | 63.6978 | 0.020065 | 0.012683 | 0.013832 | 0.0027855 | 0.068462 | 0.0019867 | 0.070948 | -61.0519 | 63.7161 | -61.3174 | -61.3083 | 62.6221 | 4.9393 | -4.953 | -5.7312 | 63.7253 | -61.3678 | -0.20599 | 0.01831 | 0.059509 | -0.19684 | -1.0757 | -0.25635 | 0.027466 | 0.2655 | 56.1584 | 55.3802 | 123.7335 | 124.8276 | 0.059509 | 124.8367 | 66.0507 | -0.25635 | 124.8276 | 0.059509 | 66.0507 | 123.7335 | 124.8367 | -125.0153 | -125.0656
1217.6406 | 125.1068 | -61.0245 | 63.7024 | 0.13451 | 0.01076 | 0.011482 | -0.0014869 | 0.068889 | 0.00070494 | 0.06988 | -61.0153 | 63.6475 | -61.3037 | -61.1664 | 62.6175 | 4.7745 | -5.0354 | -5.6076 | 63.6703 | -61.3129 | -0.27924 | -0.054932 | 0.009155 | -0.14191 | -1.0849 | -0.28839 | -0.032044 | 0.28839 | 55.9891 | 55.4169 | 123.642 | 124.6719 | 0.009155 | 124.6948 | 65.799 | -0.28839 | 124.6719 | 0.009155 | 65.799 | 123.642 | 124.6948 | -125.0061 | -125.0153
1218.6406 | 125.0153 | -61.0703 | 63.7161 | -0.72762 | 0.012683 | 0.01191 | 0.0032129 | 0.068676 | -0.00014946 | 0.069667 | -61.0199 | 63.7344 | -61.3037 | -61.2167 | 62.6678 | 5.0034 | -5.1636 | -5.9006 | 63.7436 | -61.3861 | -0.23346 | 0.018311 | 0.050354 | -0.14648 | -1.0483 | -0.31586 | 0.027466 | 0.28381 | 55.9067 | 55.1697 | 123.7381 | 124.8047 | 0.050354 | 124.8138 | 66.0736 | -0.31586 | 124.8047 | 0.050354 | 66.0736 | 123.7381 | 124.8138 | -125.0198 | -125.1022
1219.6406 | 125.0015 | -61.0748 | 63.7436 | -0.033341 | 0.01076 | 0.011696 | 0.0036401 | 0.067394 | -0.0014313 | 0.069667 | -61.0153 | 63.7527 | -61.2991 | -61.2625 | 62.6221 | 5.0262 | -5.2551 | -6.0516 | 63.7482 | -61.3678 | -0.2243 | 0.009156 | 0.059509 | -0.18768 | -1.1215 | -0.29297 | 0.004578 | 0.28381 | 55.8197 | 55.0232 | 123.6969 | 124.8276 | 0.059509 | 124.823 | 66.1011 | -0.29297 | 124.8276 | 0.059509 | 66.1011 | 123.6969 | 124.823 | -125.0427 | -125.1114
1220.6406 | 124.9878 | -61.0748 | 63.7253 | -0.071488 | 0.01076 | 0.013619 | 0.0027855 | 0.069316 | -0.0027131 | 0.069026 | -61.0062 | 63.7482 | -61.2946 | -61.2534 | 62.6312 | 5.0308 | -5.3513 | -6.1478 | 63.7619 | -61.3586 | -0.21973 | 0.022888 | 0.068664 | -0.17853 | -1.0941 | -0.28381 | 0.036621 | 0.28839 | 55.7236 | 54.9271 | 123.7061 | 124.823 | 0.068664 | 124.8367 | 66.1057 | -0.28381 | 124.823 | 0.068664 | 66.1057 | 123.7061 | 124.8367 | -125.0198 | -125.0839
1221.6406 | 124.9649 | -61.0519 | 63.7299 | -0.018082 | 0.012897 | 0.01191 | 0.0032129 | 0.068676 | -0.0016449 | 0.069453 | -61.0428 | 63.7665 | -61.2854 | -61.2946 | 62.59 | 4.9667 | -5.4108 | -6.2897 | 63.7802 | -61.3724 | -0.23346 | 0.036621 | 0.009155 | -0.24262 | -1.1398 | -0.32043 | 0.050354 | 0.24261 | 55.6412 | 54.7623 | 123.642 | 124.8184 | 0.009155 | 124.8322 | 66.0187 | -0.32043 | 124.8184 | 0.009155 | 66.0187 | 123.642 | 124.8322 | -125.0153 | -125.1022
1222.6406 | 125.0748 | -61.0062 | 63.7024 | 0.11162 | 0.0075559 | 0.016396 | -0.0029823 | 0.067821 | -0.0014313 | 0.071162 | -60.9741 | 63.6932 | -61.3037 | -61.171 | 62.6907 | 5.0949 | -5.7083 | -6.2897 | 63.707 | -61.2991 | -0.29755 | -0.009156 | 0.032044 | -0.16479 | -1.0117 | -0.29297 | 0.004577 | 0.32959 | 55.2979 | 54.7165 | 123.6969 | 124.6994 | 0.032044 | 124.7131 | 66.1011 | -0.29297 | 124.6994 | 0.032044 | 66.1011 | 123.6969 | 124.7131 | -125.0061 | -125.0015
1223.6406 | 124.9832 | -61.0519 | 63.7436 | -0.018082 | 0.01311 | 0.013191 | 0.0057763 | 0.068035 | 0.00049134 | 0.070308 | -61.0153 | 63.7665 | -61.29 | -61.2488 | 62.5671 | 5.0034 | -5.6122 | -6.5369 | 63.7711 | -61.3815 | -0.23804 | 0.022888 | 0.036621 | -0.19684 | -1.1765 | -0.32959 | 0.027466 | 0.27466 | 55.4398 | 54.5151 | 123.6191 | 124.8184 | 0.036621 | 124.823 | 66.0553 | -0.32959 | 124.8184 | 0.036621 | 66.0553 | 123.6191 | 124.823 | -125.0336 | -125.1251
1224.6406 | 124.9786 | -61.0428 | 63.7619 | -0.071488 | 0.012469 | 0.010201 | 0.0036401 | 0.066753 | -0.0027131 | 0.070308 | -60.965 | 63.7665 | -61.2625 | -61.2213 | 62.6129 | 5.04 | -5.7449 | -6.5964 | 63.7894 | -61.3358 | -0.21973 | 0.004577 | 0.07782 | -0.17853 | -1.149 | -0.29297 | 0.027466 | 0.29755 | 55.2979 | 54.4464 | 123.6557 | 124.8093 | 0.07782 | 124.8322 | 66.0828 | -0.29297 | 124.8093 | 0.07782 | 66.0828 | 123.6557 | 124.8322 | -125.0244 | -125.0977
1225.6406 | 124.9878 | -61.0107 | 63.7711 | -0.079117 | 0.013324 | 0.012764 | 0.0015039 | 0.069316 | 0.0015595 | 0.069239 | -60.9604 | 63.7802 | -61.2671 | -61.2076 | 62.6083 | 5.1498 | -5.8136 | -6.6833 | 63.7756 | -61.2808 | -0.25635 | 0.009155 | 0.050354 | -0.19684 | -1.1627 | -0.27008 | 0.004578 | 0.3067 | 55.1971 | 54.3274 | 123.6191 | 124.791 | 0.050354 | 124.7864 | 66.1606 | -0.27008 | 124.791 | 0.050354 | 66.1606 | 123.6191 | 124.7864 | -125.0381 | -125.0519
1226.6406 | 124.9557 | -61.0291 | 63.7711 | 0.027695 | 0.012042 | 0.016609 | 0.0025719 | 0.068889 | 0.00027774 | 0.069026 | -61.0062 | 63.7939 | -61.2854 | -61.2534 | 62.5717 | 5.1041 | -5.8914 | -6.8848 | 63.7802 | -61.3541 | -0.25635 | 0.022888 | 0.022888 | -0.2243 | -1.1993 | -0.32501 | 0.009155 | 0.27923 | 55.1376 | 54.1443 | 123.6008 | 124.823 | 0.022888 | 124.8093 | 66.1331 | -0.32501 | 124.823 | 0.022888 | 66.1331 | 123.6008 | 124.8093 | -125.0565 | -125.1251
1227.6562 | 125.0565 | -60.9787 | 63.7527 | 0.08873 | 0.0090513 | 0.0078507 | -0.0061865 | 0.06718 | -0.0050629 | 0.071589 | -61.0062 | 63.6887 | -61.2717 | -61.171 | 62.4527 | 5.2185 | -6.1661 | -6.9214 | 63.7711 | -61.2488 | -0.29297 | -0.064087 | -0.027466 | -0.19226 | -1.3 | -0.27008 | 0.01831 | 0.2655 | 54.8126 | 54.0573 | 123.4314 | 124.6674 | -0.027466 | 124.7498 | 66.1972 | -0.27008 | 124.6674 | -0.027466 | 66.1972 | 123.4314 | 124.7498 | -125.0244 | -125.0015
1228.6406 | 124.9603 | -61.0245 | 63.7711 | 0.11925 | 0.014178 | 0.014687 | 0.0064171 | 0.066112 | -0.0024995 | 0.070308 | -60.9787 | 63.7711 | -61.2625 | -61.2579 | 62.5351 | 5.1132 | -6.0974 | -7.1091 | 63.7756 | -61.3495 | -0.23804 | 0 | 0.045776 | -0.23346 | -1.236 | -0.32501 | 0.004578 | 0.28381 | 54.9271 | 53.9154 | 123.5596 | 124.7955 | 0.045776 | 124.8001 | 66.1377 | -0.32501 | 124.7955 | 0.045776 | 66.1377 | 123.5596 | 124.8001 | -125.0336 | -125.1205
1229.6406 | 124.9786 | -61.0153 | 63.7848 | 0.08873 | 0.014819 | 0.012123 | 0.0055627 | 0.066967 | -0.00057686 | 0.070094 | -61.0016 | 63.7665 | -61.2488 | -61.2579 | 62.5305 | 5.1544 | -6.2988 | -7.2647 | 63.8031 | -61.3266 | -0.23346 | -0.018311 | 0.013733 | -0.24262 | -1.2543 | -0.31128 | 0.018311 | 0.24719 | 54.7165 | 53.7506 | 123.5458 | 124.7818 | 0.013733 | 124.8184 | 66.1697 | -0.31128 | 124.7818 | 0.013733 | 66.1697 | 123.5458 | 124.8184 | -125.0336 | -125.1114
1230.6406 | 124.9878 | -60.9879 | 63.7711 | 0.096359 | 0.012683 | 0.01255 | 0.0042809 | 0.068462 | -0.00079046 | 0.069239 | -60.9924 | 63.7802 | -61.2579 | -61.2305 | 62.5397 | 5.1956 | -6.4178 | -7.3425 | 63.7894 | -61.2991 | -0.27008 | 0.009155 | -0.004578 | -0.24262 | -1.2314 | -0.31128 | 0.018311 | 0.2655 | 54.57 | 53.6453 | 123.5275 | 124.7681 | -0.004578 | 124.7772 | 66.1835 | -0.31128 | 124.7681 | -0.004578 | 66.1835 | 123.5275 | 124.7772 | -125.029 | -125.0702
1231.6406 | 125.0427 | -60.9421 | 63.7756 | 0.10399 | 0.0075559 | 0.01255 | -0.0031959 | 0.067821 | 0.0013457 | 0.06988 | -60.9833 | 63.6932 | -61.2488 | -61.1938 | 62.6083 | 5.3009 | -6.6605 | -7.3975 | 63.7527 | -61.2167 | -0.3067 | -0.082398 | -0.041198 | -0.25177 | -1.1673 | -0.27466 | -0.022888 | 0.2655 | 54.2816 | 53.5446 | 123.5504 | 124.6353 | -0.041198 | 124.6948 | 66.243 | -0.27466 | 124.6353 | -0.041198 | 66.243 | 123.5504 | 124.6948 | -125.0244 | -124.9924
1232.6562 | 125.0519 | -60.9512 | 63.7939 | -0.010452 | 0.0073423 | 0.010201 | -0.0014869 | 0.062694 | -0.00057686 | 0.070308 | -60.9695 | 63.6978 | -61.2122 | -61.171 | 62.59 | 5.3604 | -6.7383 | -7.489 | 63.7711 | -61.2488 | -0.26093 | -0.09613 | -0.01831 | -0.21973 | -1.2039 | -0.29755 | -0.022888 | 0.24262 | 54.213 | 53.4622 | 123.5413 | 124.649 | -0.01831 | 124.7223 | 66.3116 | -0.29755 | 124.649 | -0.01831 | 66.3116 | 123.5413 | 124.7223 | -125.0061 | -125.0427
1233.6406 | 125.0015 | -60.965 | 63.8123 | 0.18791 | 0.011188 | 0.011482 | 0.0053491 | 0.066112 | -0.0020721 | 0.070521 | -60.9467 | 63.7756 | -61.2167 | -61.203 | 62.5351 | 5.2872 | -6.8436 | -7.7087 | 63.8031 | -61.29 | -0.25177 | -0.036621 | 0.018311 | -0.23804 | -1.2772 | -0.32501 | -0.009155 | 0.27008 | 54.1214 | 53.2562 | 123.5001 | 124.7406 | 0.018311 | 124.7681 | 66.2521 | -0.32501 | 124.7406 | 0.018311 | 66.2521 | 123.5001 | 124.7681 | -125.029 | -125.1022
1234.6406 | 125.029 | -60.965 | 63.8077 | 0.14976 | 0.011615 | 0.0099869 | 0.0051355 | 0.066967 | 0.00070494 | 0.070735 | -60.9283 | 63.8077 | -61.2259 | -61.1618 | 62.5351 | 5.3284 | -7.0312 | -7.8186 | 63.7939 | -61.2762 | -0.26093 | 0 | 0.036621 | -0.19684 | -1.2726 | -0.31128 | -0.013733 | 0.29755 | 53.9337 | 53.1464 | 123.5001 | 124.7726 | 0.036621 | 124.7589 | 66.2933 | -0.31128 | 124.7726 | 0.036621 | 66.2933 | 123.5001 | 124.7589 | -125.0336 | -125.0839
1235.6406 | 125.0885 | -60.9192 | 63.8123 | 0.13451 | 0.0099057 | 0.014473 | 0.00064935 | 0.068035 | -0.00057686 | 0.070521 | -60.8734 | 63.7436 | -61.1984 | -61.1069 | 62.5763 | 5.2139 | -7.2739 | -7.6309 | 63.7573 | -61.2167 | -0.27924 | -0.068665 | 0.045776 | -0.18768 | -1.236 | -0.29755 | -0.054932 | 0.32501 | 53.6453 | 53.2883 | 123.4955 | 124.6628 | 0.045776 | 124.6765 | 66.1331 | -0.29755 | 124.6628 | 0.045776 | 66.1331 | 123.4955 | 124.6765 | -125.0107 | -125.029
1236.6406 | 125.0427 | -60.9283 | 63.8123 | -0.22408 | 0.0086239 | 0.0084915 | -0.0019141 | 0.063976 | -0.0020721 | 0.06988 | -60.9009 | 63.7115 | -61.1801 | -61.0748 | 62.59 | 5.484 | -7.2235 | -7.9147 | 63.8214 | -61.1847 | -0.25177 | -0.10071 | 0.027466 | -0.14648 | -1.2222 | -0.25635 | 0.009155 | 0.27924 | 53.7048 | 53.0136 | 123.5184 | 124.6399 | 0.027466 | 124.7498 | 66.4124 | -0.25635 | 124.6399 | 0.027466 | 66.4124 | 123.5184 | 124.7498 | -124.9924 | -124.9969
1237.6406 | 125.0839 | -60.9238 | 63.826 | -0.056229 | 0.0081967 | 0.013619 | -0.0017005 | 0.063549 | -0.0012177 | 0.070308 | -60.9329 | 63.7161 | -61.171 | -61.0977 | 62.5854 | 5.5115 | -7.4203 | -8.0887 | 63.7985 | -61.1938 | -0.24719 | -0.10986 | -0.009155 | -0.17395 | -1.2405 | -0.27008 | -0.027466 | 0.23804 | 53.5034 | 52.8351 | 123.5092 | 124.6399 | -0.009155 | 124.7223 | 66.4352 | -0.27008 | 124.6399 | -0.009155 | 66.4352 | 123.5092 | 124.7223 | -124.9969 | -125.0198
1238.6406 | 125.0519 | -60.9329 | 63.8031 | 0.2108 | 0.011188 | 0.0149 | 0.0049219 | 0.063549 | 6.414e-05 | 0.071162 | -60.9009 | 63.7711 | -61.1984 | -61.116 | 62.5214 | 5.452 | -7.6447 | -8.3405 | 63.7711 | -61.2442 | -0.2655 | -0.032044 | 0.032043 | -0.18311 | -1.2817 | -0.31128 | -0.032044 | 0.29755 | 53.2883 | 52.5925 | 123.4543 | 124.704 | 0.032043 | 124.704 | 66.3849 | -0.31128 | 124.704 | 0.032043 | 66.3849 | 123.4543 | 124.704 | -125.0015 | -125.0473
1239.6406 | 125.0565 | -60.9283 | 63.826 | 0.17265 | 0.010974 | 0.013405 | 0.0029993 | 0.06483 | 6.414e-05 | 0.068599 | -60.8963 | 63.7619 | -61.2167 | -61.0931 | 62.5305 | 5.4611 | -7.814 | -8.4366 | 63.7985 | -61.2076 | -0.28839 | -0.064087 | 0.032044 | -0.16479 | -1.2955 | -0.27924 | -0.027466 | 0.32043 | 53.1143 | 52.4918 | 123.4589 | 124.6902 | 0.032044 | 124.7269 | 66.3895 | -0.27924 | 124.6902 | 0.032044 | 66.3895 | 123.4589 | 124.7269 | -125.0427 | -125.0336
1240.6406 | 125.061 | -60.8688 | 63.7802 | 0.36339 | 0.0099057 | 0.014687 | 0.00064935 | 0.064617 | -0.0012177 | 0.070521 | -60.8276 | 63.7344 | -61.1481 | -61.0565 | 62.5534 | 5.5389 | -7.9697 | -8.5373 | 63.7848 | -61.1801 | -0.27924 | -0.045776 | 0.041198 | -0.18768 | -1.2268 | -0.31128 | 0.004578 | 0.32043 | 52.8992 | 52.3315 | 123.4222 | 124.6033 | 0.041198 | 124.6536 | 66.4078 | -0.31128 | 124.6033 | 0.041198 | 66.4078 | 123.4222 | 124.6536 | -124.9283 | -124.9603
1241.6562 | 125.0793 | -60.8826 | 63.8535 | -0.23933 | 0.0073423 | 0.011696 | 0.00064935 | 0.062694 | -0.0014313 | 0.067744 | -60.8139 | 63.7756 | -61.1481 | -61.0336 | 62.5992 | 5.6442 | -8.0063 | -8.5831 | 63.8351 | -61.1618 | -0.2655 | -0.07782 | 0.068664 | -0.15106 | -1.2543 | -0.27924 | -0.018311 | 0.33417 | 52.8763 | 52.2995 | 123.4818 | 124.6582 | 0.068664 | 124.7177 | 66.5268 | -0.27924 | 124.6582 | 0.068664 | 66.5268 | 123.4818 | 124.7177 | -125.0015 | -125.0153
1242.6406 | 125.0839 | -60.8643 | 63.8489 | -0.19356 | 0.0081967 | 0.010201 | -0.00063225 | 0.060772 | -0.00014946 | 0.068812 | -60.8139 | 63.7482 | -61.1252 | -60.6766 | 62.6678 | 5.3879 | -8.1619 | -8.7112 | 63.8214 | -61.1481 | -0.26093 | -0.10071 | 0.050354 | 0.18768 | -1.181 | -0.28381 | -0.027466 | 0.31128 | 52.7023 | 52.153 | 123.5321 | 124.6124 | 0.050354 | 124.6857 | 66.2521 | -0.28381 | 124.6124 | 0.050354 | 66.2521 | 123.5321 | 124.6857 | -124.9741 | -124.9969
1243.6406 | 125.0793 | -60.8826 | 63.8763 | 0.18791 | 0.0081967 | 0.01255 | 0.0017175 | 0.061626 | -0.00014946 | 0.069453 | -60.8368 | 63.7619 | -61.1526 | -61.0794 | 62.5259 | 5.6625 | -8.4183 | -8.9767 | 63.7894 | -61.1893 | -0.27008 | -0.11444 | 0.045776 | -0.19684 | -1.3504 | -0.3067 | -0.086975 | 0.31586 | 52.4643 | 51.9058 | 123.4085 | 124.6445 | 0.045776 | 124.6719 | 66.5451 | -0.3067 | 124.6445 | 0.045776 | 66.5451 | 123.4085 | 124.6719 | -125.029 | -125.0656
1244.6406 | 125.0565 | -60.8734 | 63.8489 | 0.11162 | 0.01076 | 0.014046 | 0.00086295 | 0.062908 | 0.00027774 | 0.069239 | -60.8185 | 63.7848 | -61.1252 | -61.0428 | 62.4939 | 5.6671 | -8.5373 | -9.1141 | 63.7848 | -61.1481 | -0.25177 | -0.064087 | 0.054932 | -0.16937 | -1.355 | -0.27466 | -0.064087 | 0.3067 | 52.3361 | 51.7593 | 123.3673 | 124.6582 | 0.054932 | 124.6582 | 66.5405 | -0.27466 | 124.6582 | 0.054932 | 66.5405 | 123.3673 | 124.6582 | -124.9741 | -124.9969
1245.6406 | 125.0885 | -60.8505 | 63.8489 | -0.071488 | 0.010119 | 0.014259 | 0.0044945 | 0.062694 | -0.00079046 | 0.067317 | -60.8002 | 63.7756 | -61.116 | -61.0199 | 62.5351 | 5.6992 | -8.7158 | -9.2285 | 63.8031 | -61.1572 | -0.2655 | -0.073242 | 0.050354 | -0.16937 | -1.3138 | -0.3067 | -0.045776 | 0.31586 | 52.1347 | 51.622 | 123.3856 | 124.6262 | 0.050354 | 124.6536 | 66.5497 | -0.3067 | 124.6262 | 0.050354 | 66.5497 | 123.3856 | 124.6536 | -124.9649 | -125.0061
1246.6406 | 125.0061 | -60.8734 | 63.9175 | -0.22408 | 0.010974 | 0.011696 | 0.0017175 | 0.06184 | -0.0027131 | 0.069026 | -60.8414 | 63.8443 | -61.1252 | -61.0657 | 62.3932 | 5.6671 | -8.2672 | -9.5901 | 63.9404 | -61.0931 | -0.25177 | -0.073243 | 0.032043 | -0.19226 | -1.5244 | -0.21973 | 0.022888 | 0.28381 | 52.6062 | 51.2833 | 123.2666 | 124.7177 | 0.032043 | 124.8138 | 66.5405 | -0.21973 | 124.7177 | 0.032043 | 66.5405 | 123.2666 | 124.8138 | -125.0427 | -125.0107
1247.6406 | 125.0656 | -60.8231 | 63.9084 | -0.086746 | 0.0077695 | 0.0099869 | 0.0012903 | 0.06184 | 0.00049134 | 0.070094 | -60.7956 | 63.7894 | -61.0931 | -60.9833 | 62.5259 | 5.7724 | -8.9401 | -9.4025 | 63.8489 | -61.116 | -0.27008 | -0.11902 | 0.027466 | -0.16022 | -1.3824 | -0.29297 | -0.059509 | 0.29755 | 51.8829 | 51.4206 | 123.349 | 124.6124 | 0.027466 | 124.6719 | 66.5955 | -0.29297 | 124.6124 | 0.027466 | 66.5955 | 123.349 | 124.6719 | -125.0015 | -125.0244
1248.6406 | 125.1663 | -60.8414 | 63.9221 | 0.0811 | 0.0084103 | 0.0091323 | 0.00086295 | 0.063549 | -0.0016449 | 0.070094 | -60.8185 | 63.7848 | -61.116 | -61.0382 | 62.4619 | 5.69 | -9.0958 | -9.6497 | 63.8763 | -61.116 | -0.27466 | -0.13733 | 0.022889 | -0.19684 | -1.4603 | -0.27466 | -0.045776 | 0.29755 | 51.7456 | 51.1917 | 123.3032 | 124.6262 | 0.022889 | 124.7177 | 66.5314 | -0.27466 | 124.6262 | 0.022889 | 66.5314 | 123.3032 | 124.7177 | -125.0381 | -125.0381
1249.6406 | 125.1617 | -60.8505 | 63.9084 | 0.0811 | 0.0094785 | 0.010201 | 8.546e-06 | 0.060344 | -0.00079046 | 0.070521 | -60.8002 | 63.7848 | -61.0977 | -61.0153 | 62.4664 | 5.7404 | -9.2331 | -9.7549 | 63.8489 | -61.0886 | -0.24719 | -0.1236 | 0.050354 | -0.1648 | -1.442 | -0.23804 | -0.059509 | 0.29755 | 51.6174 | 51.0956 | 123.317 | 124.6353 | 0.050354 | 124.6994 | 66.5909 | -0.23804 | 124.6353 | 0.050354 | 66.5909 | 123.317 | 124.6994 | -125.0061 | -124.9969
1250.6406 | 125.0519 | -60.8414 | 63.9084 | -0.048599 | 0.010547 | 0.0080643 | 0.00043575 | 0.063121 | 6.414e-05 | 0.069453 | -60.8047 | 63.8306 | -61.0886 | -60.9924 | 62.4664 | 5.7816 | -9.3796 | -9.8648 | 63.8397 | -61.0886 | -0.24719 | -0.07782 | 0.036621 | -0.15106 | -1.442 | -0.24719 | -0.068664 | 0.28381 | 51.4618 | 50.9766 | 123.3078 | 124.6719 | 0.036621 | 124.6811 | 66.6229 | -0.24719 | 124.6719 | 0.036621 | 66.6229 | 123.3078 | 124.6811 | -124.9969 | -124.9969
1251.6406 | 124.9878 | -60.8459 | 63.9359 | 0.058212 | 0.010119 | 0.0087051 | 0.00064935 | 0.062908 | 6.414e-05 | 0.068171 | -60.791 | 63.8397 | -61.0886 | -60.9879 | 62.4481 | 5.7632 | -9.5901 | -9.819 | 63.8855 | -61.0519 | -0.24262 | -0.09613 | 0.054931 | -0.14191 | -1.4877 | -0.20599 | -0.050354 | 0.29755 | 51.2558 | 51.0269 | 123.2941 | 124.6857 | 0.054931 | 124.7314 | 66.6092 | -0.20599 | 124.6857 | 0.054931 | 66.6092 | 123.2941 | 124.7314 | -125.0244 | -124.9878
1252.6562 | 124.9741 | -60.8139 | 64.0137 | -0.056229 | 0.010547 | 0.0091323 | 0.0051355 | 0.06419 | -0.0014313 | 0.068812 | -60.91 | 63.913 | -61.0931 | -61.0382 | 62.4161 | 5.7312 | -9.5764 | -10.2676 | 63.9633 | -61.0794 | -0.27924 | -0.10071 | -0.09613 | -0.2243 | -1.5976 | -0.2655 | -0.050354 | 0.18311 | 51.2375 | 50.5463 | 123.23 | 124.7269 | -0.09613 | 124.7772 | 66.5451 | -0.2655 | 124.7269 | -0.09613 | 66.5451 | 123.23 | 124.7772 | -125.1068 | -125.0931
1253.6406 | 125.0473 | -60.7956 | 63.9404 | 0.13451 | 0.0064877 | 0.012337 | 0.0023583 | 0.064403 | -0.00079046 | 0.069026 | -60.7315 | 63.8306 | -61.0474 | -60.9558 | 62.4344 | 5.8136 | -10.0113 | -10.3867 | 63.8855 | -61.0519 | -0.25177 | -0.10986 | 0.064087 | -0.16022 | -1.506 | -0.25635 | -0.054932 | 0.31586 | 50.7843 | 50.4089 | 123.23 | 124.6262 | 0.064087 | 124.6811 | 66.6092 | -0.25635 | 124.6262 | 0.064087 | 66.6092 | 123.23 | 124.6811 | -124.9878 | -124.9924
1254.6406 | 125.1663 | -60.7681 | 63.9496 | 0.058212 | 0.011401 | 0.0076369 | -0.00084605 | 0.062694 | 0.0028411 | 0.070308 | -60.7544 | 63.8489 | -61.0428 | -60.9695 | 62.439 | 5.8228 | -10.0754 | -10.5469 | 63.9084 | -61.0428 | -0.27466 | -0.10071 | 0.013732 | -0.20142 | -1.5106 | -0.27466 | -0.041199 | 0.28839 | 50.6927 | 50.2213 | 123.2071 | 124.617 | 0.013732 | 124.6765 | 66.5909 | -0.27466 | 124.617 | 0.013732 | 66.5909 | 123.2071 | 124.6765 | -124.9924 | -124.9924
1255.6406 | 125.0748 | -60.7727 | 63.9679 | 0.027695 | 0.0090513 | 0.014687 | -0.0019141 | 0.063121 | -0.00014946 | 0.070948 | -60.7361 | 63.8535 | -61.0291 | -60.9604 | 62.4207 | 5.8044 | -10.2402 | -10.73 | 63.9175 | -61.0291 | -0.25635 | -0.11444 | 0.036621 | -0.18768 | -1.5472 | -0.25635 | -0.050354 | 0.29297 | 50.5325 | 50.0427 | 123.1934 | 124.6262 | 0.036621 | 124.6902 | 66.5771 | -0.25635 | 124.6262 | 0.036621 | 66.5771 | 123.1934 | 124.6902 | -124.9969 | -124.9969
1256.6406 | 125.0565 | -60.759 | 63.9862 | -0.018082 | 0.0073423 | 0.0087051 | 0.00022215 | 0.060344 | -0.00057686 | 0.072017 | -60.7224 | 63.8855 | -61.0336 | -60.9375 | 62.439 | 5.8228 | -10.405 | -10.849 | 63.9221 | -61.0153 | -0.27466 | -0.10071 | 0.036621 | -0.17853 | -1.5472 | -0.25635 | -0.064087 | 0.31128 | 50.354 | 49.91 | 123.1979 | 124.6445 | 0.036621 | 124.6811 | 66.5817 | -0.25635 | 124.6445 | 0.036621 | 66.5817 | 123.1979 | 124.6811 | -125.0198 | -125.0015
1257.6406 | 125.0656 | -60.7224 | 63.9862 | -0.20882 | 0.0073423 | 0.010628 | 0.0010767 | 0.06184 | -0.00079046 | 0.071589 | -60.64 | 63.913 | -60.9833 | -60.8688 | 62.471 | 5.8731 | -10.5652 | -10.9268 | 63.9359 | -61.0107 | -0.26092 | -0.073242 | 0.082397 | -0.14648 | -1.5152 | -0.28839 | -0.050354 | 0.34332 | 50.1572 | 49.7955 | 123.1934 | 124.6353 | 0.082397 | 124.6582 | 66.5955 | -0.28839 | 124.6353 | 0.082397 | 66.5955 | 123.1934 | 124.6582 | -124.9695 | -124.9969
1258.6406 | 125.0702 | -60.7361 | 64.0091 | -0.079117 | 0.0099057 | 0.012978 | -0.0010597 | 0.062694 | -0.00014946 | 0.070735 | -60.6995 | 63.8855 | -61.0107 | -60.9421 | 62.3932 | 5.8182 | -10.7529 | -11.1694 | 63.9633 | -61.0199 | -0.27466 | -0.1236 | 0.036621 | -0.20599 | -1.6159 | -0.28381 | -0.045776 | 0.31128 | 49.9832 | 49.5666 | 123.1293 | 124.6216 | 0.036621 | 124.6994 | 66.5543 | -0.28381 | 124.6216 | 0.036621 | 66.5543 | 123.1293 | 124.6994 | -125.0198 | -125.029
1259.6406 | 125.0381 | -60.7407 | 63.9908 | 0.08873 | 0.0088375 | 0.0065689 | 0.00064935 | 0.062694 | 0.00091854 | 0.070521 | -60.6949 | 63.8763 | -60.997 | -60.9329 | 62.384 | 5.7999 | -10.9314 | -11.3251 | 63.9542 | -61.0062 | -0.25635 | -0.11444 | 0.045777 | -0.19226 | -1.6068 | -0.2655 | -0.036621 | 0.30212 | 49.8093 | 49.4156 | 123.1247 | 124.617 | 0.045777 | 124.6948 | 66.5405 | -0.2655 | 124.617 | 0.045777 | 66.5405 | 123.1247 | 124.6948 | -124.9878 | -124.9969
1260.6406 | 125.0198 | -60.7132 | 64.0182 | -0.079117 | 0.011615 | 0.0095595 | -0.0034095 | 0.062053 | -0.00036306 | 0.067744 | -60.6903 | 63.8901 | -60.9833 | -60.9055 | 62.3886 | 5.8731 | -11.0916 | -11.4441 | 63.945 | -60.9741 | -0.27008 | -0.12817 | 0.022888 | -0.19226 | -1.6296 | -0.26092 | -0.073243 | 0.29297 | 49.6216 | 49.2691 | 123.1018 | 124.6033 | 0.022888 | 124.6582 | 66.5863 | -0.26092 | 124.6033 | 0.022888 | 66.5863 | 123.1018 | 124.6582 | -125.0015 | -124.9924
1261.6406 | 125.0473 | -60.6995 | 64.0228 | 0.058212 | 0.0084103 | 0.011055 | -0.00041865 | 0.063121 | -0.0018585 | 0.072017 | -60.672 | 63.9267 | -60.9833 | -60.9009 | 62.3611 | 5.896 | -11.2152 | -11.5677 | 63.9587 | -60.9833 | -0.28381 | -0.09613 | 0.027466 | -0.20142 | -1.6617 | -0.28381 | -0.064087 | 0.31128 | 49.4843 | 49.1318 | 123.0606 | 124.6262 | 0.027466 | 124.6582 | 66.5955 | -0.28381 | 124.6262 | 0.027466 | 66.5955 | 123.0606 | 124.6582 | -125.0061 | -125.0061
1262.6406 | 124.9512 | -60.7315 | 64.0778 | -0.22408 | 0.011615 | 0.010628 | 0.0027855 | 0.062694 | -0.0029267 | 0.072017 | -60.6583 | 64.0411 | -60.965 | -60.8093 | 62.146 | 5.6854 | -11.1786 | -11.7691 | 64.0182 | -60.9833 | -0.23346 | -0.036621 | 0.073242 | -0.07782 | -1.9318 | -0.25177 | -0.059509 | 0.3067 | 49.5529 | 48.9624 | 122.8775 | 124.7726 | 0.073242 | 124.7498 | 66.4169 | -0.25177 | 124.7726 | 0.073242 | 66.4169 | 122.8775 | 124.7498 | -125.0427 | -125.061
1263.6406 | 125.0839 | -60.6766 | 64.064 | -0.063858 | 0.0079831 | 0.0099869 | -0.0014869 | 0.063121 | 0.0011321 | 0.069026 | -60.6171 | 63.945 | -60.9467 | -60.8505 | 62.384 | 5.9418 | -11.5814 | -11.8149 | 63.9862 | -60.9329 | -0.27008 | -0.11902 | 0.05951 | -0.17395 | -1.68 | -0.25635 | -0.07782 | 0.32959 | 49.0952 | 48.8617 | 123.0606 | 124.6216 | 0.05951 | 124.6628 | 66.6183 | -0.25635 | 124.6216 | 0.05951 | 66.6183 | 123.0606 | 124.6628 | -125.0107 | -124.9969
1264.6406 | 125.0793 | -60.6812 | 64.032 | -0.094376 | 0.0092649 | 0.0076369 | 0.00064935 | 0.061626 | -0.0010041 | 0.06988 | -60.5896 | 63.9313 | -60.9604 | -60.8414 | 62.3795 | 5.9509 | -11.7645 | -11.9797 | 63.9908 | -60.9512 | -0.27924 | -0.10071 | 0.091552 | -0.16022 | -1.6525 | -0.27008 | -0.041198 | 0.37079 | 48.9166 | 48.7015 | 123.0606 | 124.6124 | 0.091552 | 124.6719 | 66.6321 | -0.27008 | 124.6124 | 0.091552 | 66.6321 | 123.0606 | 124.6719 | -124.9924 | -124.9832
1265.6406 | 125.0519 | -60.6857 | 64.0594 | -0.04097 | 0.0096921 | 0.0091323 | -0.0012733 | 0.062694 | -0.0010041 | 0.069239 | -60.6079 | 63.9679 | -60.9375 | -60.8276 | 62.3337 | 5.9647 | -11.9019 | -12.1353 | 63.9771 | -60.9238 | -0.25177 | -0.091552 | 0.07782 | -0.14191 | -1.7258 | -0.23804 | -0.082397 | 0.32959 | 48.7839 | 48.5504 | 123.0194 | 124.6536 | 0.07782 | 124.6628 | 66.6504 | -0.23804 | 124.6536 | 0.07782 | 66.6504 | 123.0194 | 124.6628 | -124.9969 | -124.9832
1266.6406 | 125.0427 | -60.6903 | 64.064 | 0.53123 | 0.010547 | 0.0087051 | -0.00041865 | 0.062908 | -0.00014946 | 0.068599 | -60.5988 | 63.9313 | -60.9467 | -60.8597 | 62.2879 | 5.9509 | -12.0575 | -12.323 | 64.0091 | -60.9238 | -0.25635 | -0.13275 | 0.091553 | -0.16937 | -1.7761 | -0.23346 | -0.054932 | 0.3479 | 48.6328 | 48.3673 | 122.9782 | 124.6216 | 0.091553 | 124.6994 | 66.6412 | -0.23346 | 124.6216 | 0.091553 | 66.6412 | 122.9782 | 124.6994 | -125.0107 | -124.9878
1267.6406 | 124.9878 | -60.6628 | 64.1739 | -0.22408 | 0.011401 | 0.01255 | 0.00086295 | 0.062053 | -0.00036306 | 0.069239 | -60.5942 | 64.032 | -60.9467 | -60.8597 | 62.2604 | 5.8823 | -12.0758 | -12.4924 | 64.0411 | -60.9512 | -0.28381 | -0.14191 | 0.068665 | -0.19684 | -1.9135 | -0.28839 | -0.13275 | 0.35248 | 48.587 | 48.1705 | 122.9233 | 124.6948 | 0.068665 | 124.704 | 66.5451 | -0.28839 | 124.6948 | 0.068665 | 66.5451 | 122.9233 | 124.704 | -125.1205 | -125.1251
1268.6406 | 125.0565 | -60.6628 | 64.0869 | -0.048599 | 0.0099057 | 0.0074233 | -0.0023413 | 0.062267 | 0.00070494 | 0.069453 | -60.585 | 63.9496 | -60.9238 | -60.8276 | 62.2696 | 5.9738 | -12.4054 | -12.5473 | 64.0228 | -60.8917 | -0.26093 | -0.13733 | 0.07782 | -0.1648 | -1.8173 | -0.22888 | -0.064087 | 0.33874 | 48.2574 | 48.1155 | 122.9324 | 124.6124 | 0.07782 | 124.6857 | 66.6367 | -0.22888 | 124.6124 | 0.07782 | 66.6367 | 122.9324 | 124.6857 | -125.0107 | -124.9786
1269.6406 | 125.0748 | -60.6171 | 64.0961 | -0.14778 | 0.0088375 | 0.011482 | -0.0014869 | 0.062694 | 0.00027774 | 0.070094 | -60.5392 | 63.9771 | -60.8826 | -60.7681 | 62.3154 | 6.0608 | -12.5885 | -12.6572 | 64.0182 | -60.9055 | -0.2655 | -0.11902 | 0.077819 | -0.15106 | -1.7807 | -0.28839 | -0.077819 | 0.34332 | 48.0286 | 47.9599 | 122.9324 | 124.5941 | 0.077819 | 124.6353 | 66.6779 | -0.28839 | 124.5941 | 0.077819 | 66.6779 | 122.9324 | 124.6353 | -124.9786 | -125.0015
1270.6406 | 125.061 | -60.6537 | 64.0915 | -0.13252 | 0.0077695 | 0.0099869 | -0.0023413 | 0.061412 | -0.00079046 | 0.070948 | -60.5209 | 63.9816 | -60.8917 | -60.7681 | 62.2696 | 6.0471 | -12.767 | -12.8174 | 64.0366 | -60.8734 | -0.23804 | -0.10986 | 0.13275 | -0.11444 | -1.8219 | -0.21973 | -0.054932 | 0.37079 | 47.8867 | 47.8363 | 122.9233 | 124.6353 | 0.13275 | 124.6902 | 66.7007 | -0.21973 | 124.6353 | 0.13275 | 66.7007 | 122.9233 | 124.6902 | -124.9832 | -124.9649
1271.6406 | 125.0656 | -60.6354 | 64.1006 | -0.10963 | 0.0099057 | 0.0097733 | -0.0019141 | 0.062267 | 0.00049134 | 0.070308 | -60.5164 | 63.9862 | -60.8871 | -60.7819 | 62.2467 | 6.0837 | -12.9135 | -12.9639 | 64.0366 | -60.9009 | -0.25177 | -0.11444 | 0.11902 | -0.14648 | -1.8539 | -0.2655 | -0.064087 | 0.37079 | 47.7219 | 47.6715 | 122.8821 | 124.6216 | 0.11902 | 124.6719 | 66.7191 | -0.2655 | 124.6216 | 0.11902 | 66.7191 | 122.8821 | 124.6719 | -124.9878 | -125.0015
1272.6406 | 124.9329 | -60.6491 | 64.1556 | -0.1783 | 0.010547 | 0.010628 | 0.00043575 | 0.062267 | 6.414e-05 | 0.069239 | -60.553 | 64.0869 | -60.9146 | -60.6491 | 62.3428 | 5.9189 | -12.9959 | -13.1653 | 64.0915 | -60.91 | -0.2655 | -0.068665 | 0.09613 | 0 | -1.8127 | -0.26093 | -0.064087 | 0.36163 | 47.6532 | 47.4838 | 122.9919 | 124.736 | 0.09613 | 124.7406 | 66.568 | -0.26093 | 124.736 | 0.09613 | 66.568 | 122.9919 | 124.7406 | -125.0702 | -125.0656
1273.6406 | 125.0244 | -60.5988 | 64.1144 | -0.68947 | 0.0090513 | 0.0082779 | -0.0036231 | 0.062908 | -0.00014946 | 0.069453 | -60.6033 | 64.0137 | -60.8963 | -60.8139 | 62.1689 | 6.0242 | -13.2019 | -13.2797 | 64.0732 | -60.8597 | -0.29755 | -0.10071 | -0.004578 | -0.21515 | -1.9455 | -0.26093 | -0.041199 | 0.29297 | 47.3969 | 47.319 | 122.7676 | 124.6124 | -0.004578 | 124.6719 | 66.6229 | -0.26093 | 124.6124 | -0.004578 | 66.6229 | 122.7676 | 124.6719 | -125.0107 | -124.9741
1274.6406 | 125.0153 | -60.6216 | 64.1281 | 0.027695 | 0.0094785 | 0.011482 | 0.0019311 | 0.063762 | 0.0011321 | 0.07223 | -60.5301 | 64.0091 | -60.8597 | -60.8505 | 62.1826 | 6.0745 | -13.3896 | -13.4399 | 64.0823 | -60.8551 | -0.23804 | -0.11902 | 0.091553 | -0.22888 | -1.9455 | -0.23346 | -0.045777 | 0.32959 | 47.2321 | 47.1817 | 122.8043 | 124.6307 | 0.091553 | 124.704 | 66.6962 | -0.23346 | 124.6307 | 0.091553 | 66.6962 | 122.8043 | 124.704 | -124.9878 | -124.9832
1275.6406 | 125.0427 | -60.6125 | 64.1693 | -0.033341 | 0.0079831 | 0.012337 | -0.0029823 | 0.06184 | 6.414e-05 | 0.068385 | -60.4889 | 64.0137 | -60.8414 | -60.7681 | 62.1735 | 6.0928 | -13.5132 | -13.5452 | 64.0732 | -60.8551 | -0.22888 | -0.15564 | 0.1236 | -0.15564 | -1.9959 | -0.24262 | -0.096131 | 0.35248 | 47.0993 | 47.0673 | 122.7859 | 124.6262 | 0.1236 | 124.6857 | 66.7053 | -0.24262 | 124.6262 | 0.1236 | 66.7053 | 122.7859 | 124.6857 | -125.0107 | -125.0244
1276.6406 | 125.0427 | -60.585 | 64.151 | -0.071488 | 0.0094785 | 0.0078507 | -0.0036231 | 0.061199 | 0.0024139 | 0.069667 | -60.4889 | 64.064 | -60.8597 | -60.7636 | 62.1552 | 6.1066 | -13.6734 | -13.6688 | 64.0778 | -60.8276 | -0.27466 | -0.086975 | 0.09613 | -0.17853 | -1.9958 | -0.24262 | -0.073242 | 0.37079 | 46.9116 | 46.9162 | 122.7402 | 124.649 | 0.09613 | 124.6628 | 66.6916 | -0.24262 | 124.649 | 0.09613 | 66.6916 | 122.7402 | 124.6628 | -125.0107 | -124.9786
1277.6406 | 124.9695 | -60.6216 | 64.1876 | -0.26222 | 0.01076 | 0.010628 | 0.0040673 | 0.062694 | 0.00070494 | 0.06988 | -60.4752 | 64.1602 | -60.8551 | -60.5621 | 62.1643 | 6.0059 | -13.6826 | -13.8199 | 64.1327 | -60.8551 | -0.23346 | -0.027466 | 0.14648 | 0.059509 | -2.0233 | -0.23346 | -0.054932 | 0.37994 | 46.9391 | 46.8018 | 122.7859 | 124.7818 | 0.14648 | 124.7543 | 66.6275 | -0.23346 | 124.7818 | 0.14648 | 66.6275 | 122.7859 | 124.7543 | -125.0427 | -125.0427
1278.6406 | 125.0793 | -60.5438 | 64.1647 | -0.086746 | 0.0062741 | 0.012337 | -0.0027687 | 0.063549 | -0.00057686 | 0.072657 | -60.4523 | 64.0549 | -60.8047 | -60.7315 | 62.1277 | 6.2576 | -13.9389 | -13.916 | 64.1052 | -60.8093 | -0.26093 | -0.10986 | 0.091552 | -0.18768 | -2.037 | -0.2655 | -0.059509 | 0.35248 | 46.6049 | 46.6278 | 122.6715 | 124.5987 | 0.091552 | 124.649 | 66.8015 | -0.2655 | 124.5987 | 0.091552 | 66.8015 | 122.6715 | 124.649 | -124.9695 | -124.9741
1279.6406 | 125.0885 | -60.5255 | 64.1739 | -0.086746 | 0.0075559 | 0.01191 | -0.0010597 | 0.060344 | -0.00079046 | 0.06988 | -60.4019 | 64.064 | -60.8276 | -60.6766 | 62.1231 | 6.3721 | -14.1129 | -13.9572 | 64.0823 | -60.8047 | -0.30212 | -0.10986 | 0.1236 | -0.15106 | -2.0508 | -0.27924 | -0.091553 | 0.42572 | 46.4127 | 46.5683 | 122.6486 | 124.5895 | 0.1236 | 124.6078 | 66.8976 | -0.27924 | 124.5895 | 0.1236 | 66.8976 | 122.6486 | 124.6078 | -125.0015 | -124.9786
1280.6406 | 125.0473 | -60.6216 | 64.1144 | -0.010452 | 0.0071285 | 0.0093459 | -0.00041865 | 0.060985 | 0.00049134 | 0.06689 | -60.5026 | 64.0137 | -60.8459 | -60.6079 | 62.1506 | 6.1386 | -14.0442 | -13.9389 | 64.064 | -60.8414 | -0.2243 | -0.10071 | 0.11902 | 0.013733 | -1.9638 | -0.21973 | -0.050354 | 0.34332 | 46.5775 | 46.6827 | 122.7722 | 124.6353 | 0.11902 | 124.6857 | 66.7603 | -0.21973 | 124.6353 | 0.11902 | 66.7603 | 122.7722 | 124.6857 | -124.9603 | -124.9557
1281.6406 | 125.0519 | -60.5988 | 64.1052 | -0.079117 | 0.0090513 | 0.0097733 | -0.0010597 | 0.062267 | 0.0024139 | 0.069667 | -60.4935 | 64.0503 | -60.8963 | -60.7727 | 61.9949 | 6.2988 | -14.0579 | -13.9252 | 64.064 | -60.8643 | -0.29755 | -0.054932 | 0.10529 | -0.17395 | -2.1103 | -0.2655 | -0.041199 | 0.40283 | 46.5408 | 46.6736 | 122.5937 | 124.649 | 0.10529 | 124.6628 | 66.8976 | -0.2655 | 124.649 | 0.10529 | 66.8976 | 122.5937 | 124.6628 | -125.0015 | -124.9695
1282.6406 | 125.1389 | -60.5896 | 64.1876 | -0.14778 | 0.0099057 | 0.010201 | -0.0010597 | 0.062481 | 0.00027774 | 0.069667 | -60.4248 | 64.032 | -60.8414 | -60.704 | 62.0499 | 6.4545 | -14.1632 | -13.8702 | 64.0457 | -60.8688 | -0.25177 | -0.15564 | 0.16479 | -0.11444 | -2.1378 | -0.27923 | -0.14191 | 0.41656 | 46.4264 | 46.7194 | 122.6395 | 124.6216 | 0.16479 | 124.6353 | 67.0441 | -0.27923 | 124.6216 | 0.16479 | 67.0441 | 122.6395 | 124.6353 | -125.029 | -125.0565
1283.6406 | 125.029 | -60.6308 | 64.1327 | 1.462 | 0.011615 | 0.0084915 | -0.0019141 | 0.060344 | 0.0011321 | 0.070521 | -60.4843 | 64.0228 | -60.8917 | -60.8185 | 61.9217 | 6.427 | -14.0808 | -13.9343 | 64.0457 | -60.8826 | -0.26093 | -0.10986 | 0.14648 | -0.18768 | -2.211 | -0.25177 | -0.086975 | 0.40741 | 46.55 | 46.6965 | 122.5525 | 124.6536 | 0.14648 | 124.6765 | 67.0578 | -0.25177 | 124.6536 | 0.14648 | 67.0578 | 122.5525 | 124.6765 | -125.0244 | -125.0153
1284.6406 | 125.029 | -60.6445 | 64.0961 | -0.0028231 | 0.010974 | 0.0084915 | -0.0021277 | 0.061626 | 0.0022003 | 0.069667 | -60.5026 | 64.0137 | -60.8963 | -60.8047 | 61.9171 | 6.5735 | -14.1357 | -13.8794 | 64.0228 | -60.8734 | -0.25177 | -0.082397 | 0.14191 | -0.16022 | -2.179 | -0.22888 | -0.073242 | 0.39368 | 46.5088 | 46.7651 | 122.5616 | 124.6582 | 0.14191 | 124.6674 | 67.218 | -0.22888 | 124.6582 | 0.14191 | 67.218 | 122.5616 | 124.6674 | -124.9924 | -124.9695
1285.6406 | 125.0519 | -60.6491 | 64.0961 | -0.010452 | 0.0094785 | 0.0097733 | -0.00084605 | 0.063335 | 0.0011321 | 0.072017 | -60.5072 | 63.9908 | -60.9009 | -60.8002 | 61.8851 | 6.6742 | -14.1083 | -13.8107 | 64.032 | -60.91 | -0.25177 | -0.10529 | 0.14191 | -0.15106 | -2.211 | -0.26093 | -0.064087 | 0.39368 | 46.5408 | 46.8384 | 122.5342 | 124.6399 | 0.14191 | 124.6811 | 67.3233 | -0.26093 | 124.6399 | 0.14191 | 67.3233 | 122.5342 | 124.6811 | -124.9969 | -125.0061
1286.6406 | 125.061 | -60.64 | 64.1098 | -0.056229 | 0.0084103 | 0.0095595 | -0.00063225 | 0.060344 | 6.414e-05 | 0.070094 | -60.498 | 63.9679 | -60.8871 | -60.8231 | 61.8393 | 6.7337 | -14.1083 | -13.8519 | 64.0411 | -60.8917 | -0.24719 | -0.14191 | 0.14191 | -0.1831 | -2.2705 | -0.25177 | -0.068664 | 0.3891 | 46.5317 | 46.788 | 122.4792 | 124.6079 | 0.14191 | 124.6811 | 67.3737 | -0.25177 | 124.6079 | 0.14191 | 67.3737 | 122.4792 | 124.6811 | -124.9969 | -125.0015
1287.6406 | 125.0519 | -60.6262 | 64.1281 | -0.23933 | 0.0090513 | 0.0082779 | 0.0015039 | 0.062908 | -0.00014946 | 0.068599 | -60.4156 | 64.0045 | -60.8597 | -60.7498 | 61.8942 | 6.8665 | -14.1541 | -13.7695 | 64.0366 | -60.8688 | -0.23346 | -0.1236 | 0.21057 | -0.1236 | -2.2339 | -0.24261 | -0.091553 | 0.44403 | 46.4722 | 46.8567 | 122.5204 | 124.6307 | 0.21057 | 124.6628 | 67.4927 | -0.24261 | 124.6307 | 0.21057 | 67.4927 | 122.5204 | 124.6628 | -124.9878 | -124.9969
1288.6406 | 125.0107 | -60.6445 | 64.0961 | -0.17067 | 0.0096921 | 0.0059281 | 0.0010767 | 0.063335 | -0.00057686 | 0.072017 | -60.5255 | 63.9771 | -60.9192 | -60.8231 | 61.7661 | 6.9077 | -14.1586 | -13.8107 | 64.0228 | -60.9055 | -0.27466 | -0.11902 | 0.11902 | -0.17853 | -2.33 | -0.26093 | -0.073242 | 0.39368 | 46.4859 | 46.8338 | 122.4106 | 124.6216 | 0.11902 | 124.6674 | 67.5522 | -0.26093 | 124.6216 | 0.11902 | 67.5522 | 122.4106 | 124.6674 | -125.0153 | -125.0015
1289.6406 | 125.0519 | -60.6354 | 64.1098 | 0.11162 | 0.0096921 | 0.0099869 | -0.0010597 | 0.060558 | -0.0012177 | 0.070521 | -60.5347 | 63.9908 | -60.8963 | -60.8185 | 61.7157 | 6.9992 | -14.1815 | -13.7878 | 64.0182 | -60.9009 | -0.26093 | -0.11902 | 0.10071 | -0.1831 | -2.3941 | -0.2655 | -0.091552 | 0.36163 | 46.4539 | 46.8475 | 122.3511 | 124.6262 | 0.10071 | 124.6536 | 67.6346 | -0.2655 | 124.6262 | 0.10071 | 67.6346 | 122.3511 | 124.6536 | -125.0061 | -125.0107
1290.6406 | 125.0244 | -60.6766 | 64.0503 | 0.012436 | 0.0092649 | 0.0057143 | 0.00064935 | 0.061412 | 0.0015595 | 0.068599 | -60.3378 | 64.0182 | -60.9055 | -60.8505 | 61.6608 | 7.1777 | -14.209 | -13.8199 | 63.9954 | -60.9192 | -0.22888 | -0.032043 | 0.33875 | -0.17395 | -2.3895 | -0.24261 | -0.054932 | 0.56763 | 46.4676 | 46.8567 | 122.3373 | 124.6948 | 0.33875 | 124.6719 | 67.8543 | -0.24261 | 124.6948 | 0.33875 | 67.8543 | 122.3373 | 124.6719 | -124.9557 | -124.9695
1291.6406 | 125.0793 | -60.6628 | 64.0594 | -0.048599 | 0.010974 | 0.01191 | -0.0010597 | 0.062053 | 0.0015595 | 0.069667 | -60.5072 | 63.9633 | -60.9146 | -60.8276 | 61.6745 | 7.4478 | -14.2136 | -13.7558 | 63.9771 | -60.91 | -0.25177 | -0.09613 | 0.15564 | -0.1648 | -2.3849 | -0.24719 | -0.082397 | 0.40741 | 46.4493 | 46.907 | 122.3373 | 124.6262 | 0.15564 | 124.6399 | 68.1107 | -0.24719 | 124.6262 | 0.15564 | 68.1107 | 122.3373 | 124.6399 | -124.9741 | -124.9695
1292.6406 | 125.0473 | -60.6491 | 64.0778 | -0.25459 | 0.0086239 | 0.010628 | 0.0017175 | 0.062267 | 0.00027774 | 0.073085 | -60.4156 | 63.9908 | -60.9146 | -60.7773 | 61.7111 | 7.5027 | -14.2273 | -13.71 | 63.9999 | -60.9283 | -0.2655 | -0.086975 | 0.23346 | -0.12817 | -2.3666 | -0.27924 | -0.07782 | 0.49896 | 46.4218 | 46.9391 | 122.3602 | 124.6399 | 0.23346 | 124.649 | 68.1519 | -0.27924 | 124.6399 | 0.23346 | 68.1519 | 122.3602 | 124.649 | -124.9924 | -125.0061
1293.6406 | 125.0656 | -60.6674 | 64.064 | -0.15541 | 0.010974 | 0.0087051 | -0.00063225 | 0.060131 | 0.0028411 | 0.070308 | -60.466 | 63.9404 | -60.9055 | -60.8002 | 61.6562 | 7.6675 | -14.2593 | -13.6551 | 63.9816 | -60.9009 | -0.23804 | -0.1236 | 0.20142 | -0.13275 | -2.4078 | -0.23346 | -0.082398 | 0.43945 | 46.4081 | 47.0123 | 122.3236 | 124.6078 | 0.20142 | 124.649 | 68.335 | -0.23346 | 124.6078 | 0.20142 | 68.335 | 122.3236 | 124.649 | -124.9695 | -124.9649
1294.6406 | 125.0153 | -60.7086 | 64.032 | 0.0811 | 0.0075559 | 0.010841 | 0.00022215 | 0.061626 | 0.0022003 | 0.071162 | -60.5209 | 63.8992 | -60.9695 | -60.8688 | 61.5601 | 7.6859 | -14.2502 | -13.7146 | 63.945 | -60.9375 | -0.26093 | -0.13275 | 0.18768 | -0.16022 | -2.4719 | -0.22888 | -0.086975 | 0.44861 | 46.4584 | 46.994 | 122.2687 | 124.6078 | 0.18768 | 124.6536 | 68.3945 | -0.22888 | 124.6078 | 0.18768 | 68.3945 | 122.2687 | 124.6536 | -125.0015 | -124.9695
1295.6406 | 125.0336 | -60.704 | 64.0411 | -0.10201 | 0.0088375 | 0.0091323 | -0.0010597 | 0.062694 | 0.0024139 | 0.072657 | -60.5118 | 63.9175 | -60.9329 | -60.8643 | 61.5417 | 7.7957 | -14.2685 | -13.7192 | 63.9862 | -60.9558 | -0.22888 | -0.1236 | 0.19226 | -0.16022 | -2.4994 | -0.25177 | -0.054932 | 0.42114 | 46.4355 | 46.9849 | 122.2458 | 124.6216 | 0.19226 | 124.6902 | 68.4998 | -0.25177 | 124.6216 | 0.19226 | 68.4998 | 122.2458 | 124.6902 | -124.9741 | -124.9969
1296.6406 | 125.029 | -60.7086 | 64.0182 | 0.52361 | 0.0096921 | 0.01191 | 0.00022215 | 0.062908 | 0.0011321 | 0.070308 | -60.4797 | 63.8947 | -60.9833 | -60.91 | 61.4731 | 7.9376 | -14.3005 | -13.678 | 63.9359 | -60.9787 | -0.27466 | -0.1236 | 0.22888 | -0.20142 | -2.5452 | -0.27008 | -0.082398 | 0.50354 | 46.4081 | 47.0306 | 122.1817 | 124.6033 | 0.22888 | 124.6445 | 68.6462 | -0.27008 | 124.6033 | 0.22888 | 68.6462 | 122.1817 | 124.6445 | -125.0015 | -124.9969
1297.6406 | 125.0702 | -60.6812 | 64.0045 | -0.14015 | 0.0086239 | 0.0091323 | -0.00084605 | 0.060558 | 0.0013457 | 0.071589 | -60.4568 | 63.8947 | -60.9512 | -60.8414 | 61.5646 | 7.8827 | -14.3372 | -13.4995 | 63.9359 | -60.9467 | -0.27008 | -0.10986 | 0.2243 | -0.16022 | -2.4399 | -0.2655 | -0.068665 | 0.49439 | 46.344 | 47.1817 | 122.2458 | 124.5758 | 0.2243 | 124.617 | 68.5638 | -0.2655 | 124.5758 | 0.2243 | 68.5638 | 122.2458 | 124.617 | -124.9558 | -124.9512
1298.6406 | 125.0656 | -60.7315 | 63.9954 | -0.033341 | 0.0081967 | 0.012764 | 0.00064935 | 0.062481 | 0.0019867 | 0.072017 | -60.4935 | 63.9267 | -60.9741 | -60.8917 | 61.4868 | 7.9605 | -14.2319 | -13.4766 | 63.9267 | -60.9604 | -0.24261 | -0.068664 | 0.23804 | -0.16022 | -2.5085 | -0.22888 | -0.068664 | 0.48065 | 46.4996 | 47.2549 | 122.2183 | 124.6582 | 0.23804 | 124.6582 | 68.692 | -0.22888 | 124.6582 | 0.23804 | 68.692 | 122.2183 | 124.6582 | -124.9695 | -124.9557
1299.6406 | 125.029 | -60.7178 | 63.9771 | -0.010452 | 0.0096921 | 0.0095595 | -0.0019141 | 0.060558 | 0.0026275 | 0.069026 | -60.5072 | 63.8855 | -60.9833 | -60.9055 | 61.4456 | 8.1116 | -14.1632 | -13.4079 | 63.9267 | -60.9741 | -0.2655 | -0.091553 | 0.21057 | -0.18768 | -2.5314 | -0.25635 | -0.050354 | 0.47607 | 46.5546 | 47.3099 | 122.1634 | 124.6033 | 0.21057 | 124.6445 | 68.8293 | -0.25635 | 124.6033 | 0.21057 | 68.8293 | 122.1634 | 124.6445 | -124.9603 | -124.9512
1300.6406 | 125.0748 | -60.7452 | 63.9633 | 0.035324 | 0.0084103 | 0.011055 | -0.0017005 | 0.06184 | 0.0024139 | 0.068812 | -60.5164 | 63.8672 | -61.0199 | -60.9467 | 61.3815 | 8.1848 | -14.0808 | -13.3484 | 63.9267 | -60.9695 | -0.27466 | -0.096131 | 0.22888 | -0.20142 | -2.5818 | -0.2243 | -0.036621 | 0.50354 | 46.6644 | 47.3969 | 122.1268 | 124.6124 | 0.22888 | 124.6719 | 68.9301 | -0.2243 | 124.6124 | 0.22888 | 68.9301 | 122.1268 | 124.6719 | -124.9832 | -124.9329
1301.6406 | 125.0336 | -60.7544 | 63.9725 | 0.14976 | 0.01076 | 0.012123 | 0.0012903 | 0.063549 | -0.00036306 | 0.070521 | -60.5347 | 63.8397 | -61.0336 | -60.9512 | 61.3449 | 8.3221 | -13.9801 | -13.2477 | 63.8809 | -60.997 | -0.27923 | -0.13275 | 0.21973 | -0.19684 | -2.6276 | -0.24261 | -0.091553 | 0.49896 | 46.7743 | 47.5067 | 122.0993 | 124.5941 | 0.21973 | 124.6353 | 69.0765 | -0.24261 | 124.5941 | 0.21973 | 69.0765 | 122.0993 | 124.6353 | -125.0061 | -124.9695
1302.6406 | 125.0153 | -60.7864 | 63.9359 | -0.063858 | 0.010547 | 0.01191 | -0.00063225 | 0.063121 | 0.0013457 | 0.071162 | -60.5164 | 63.8626 | -61.0428 | -60.9604 | 61.3266 | 8.5281 | -13.829 | -13.0966 | 63.8855 | -61.0336 | -0.25635 | -0.073242 | 0.27008 | -0.17395 | -2.6093 | -0.24719 | -0.050354 | 0.52643 | 46.9574 | 47.6898 | 122.113 | 124.649 | 0.27008 | 124.6719 | 69.3146 | -0.24719 | 124.649 | 0.27008 | 69.3146 | 122.113 | 124.6719 | -124.9786 | -124.9695
1303.6406 | 125.0244 | -60.7773 | 63.9404 | 0.28709 | 0.0086239 | 0.0099869 | -0.00084605 | 0.060344 | 0.0024139 | 0.071376 | -60.5209 | 63.8306 | -61.0428 | -60.965 | 61.2854 | 8.6243 | -13.7054 | -12.973 | 63.8763 | -61.0657 | -0.2655 | -0.10986 | 0.25635 | -0.18768 | -2.655 | -0.28839 | -0.064087 | 0.52185 | 47.0718 | 47.8043 | 122.0627 | 124.6078 | 0.25635 | 124.6536 | 69.4016 | -0.28839 | 124.6078 | 0.25635 | 69.4016 | 122.0627 | 124.6536 | -124.9832 | -125.0061
1304.6406 | 125.0473 | -60.791 | 63.9175 | -0.063858 | 0.0088375 | 0.0087051 | -0.00084605 | 0.062053 | 0.00070494 | 0.068812 | -60.4935 | 63.8214 | -61.0565 | -60.9375 | 61.2671 | 8.8531 | -13.6185 | -12.8586 | 63.858 | -61.0336 | -0.2655 | -0.096131 | 0.29755 | -0.14648 | -2.6505 | -0.24261 | -0.05951 | 0.56305 | 47.1725 | 47.9324 | 122.0581 | 124.6124 | 0.29755 | 124.649 | 69.6442 | -0.24261 | 124.6124 | 0.29755 | 69.6442 | 122.0581 | 124.649 | -124.9741 | -124.9512
1305.6406 | 125.029 | -60.8093 | 63.9221 | -0.056229 | 0.012683 | 0.0087051 | -0.0010597 | 0.062481 | 0.0019867 | 0.073085 | -60.5026 | 63.8123 | -61.0931 | -60.9604 | 61.235 | 9.0179 | -13.504 | -12.7213 | 63.8397 | -61.0336 | -0.28381 | -0.10986 | 0.3067 | -0.15106 | -2.6871 | -0.2243 | -0.082397 | 0.59051 | 47.3053 | 48.0881 | 122.0444 | 124.6216 | 0.3067 | 124.649 | 69.8273 | -0.2243 | 124.6216 | 0.3067 | 69.8273 | 122.0444 | 124.649 | -125.0153 | -124.9557
1306.6406 | 125.0381 | -60.8139 | 63.9175 | -0.04097 | 0.011188 | 0.011055 | -0.00020505 | 0.061626 | 0.00091854 | 0.071803 | -60.5118 | 63.7985 | -61.0474 | -61.0016 | 61.1938 | 9.2148 | -13.3575 | -12.5748 | 63.8443 | -61.0657 | -0.23346 | -0.11902 | 0.30212 | -0.18768 | -2.7237 | -0.25177 | -0.073243 | 0.53558 | 47.4564 | 48.2391 | 122.0078 | 124.6124 | 0.30212 | 124.6582 | 70.0287 | -0.25177 | 124.6124 | 0.30212 | 70.0287 | 122.0078 | 124.6582 | -124.9649 | -124.9832
1307.6406 | 125.0061 | -60.8047 | 63.9175 | -0.2317 | 0.0094785 | 0.010628 | 0.0021447 | 0.063549 | -0.00036306 | 0.069667 | -60.4614 | 63.8306 | -61.0703 | -60.9421 | 61.1618 | 9.3796 | -13.147 | -12.3642 | 63.858 | -61.0931 | -0.2655 | -0.086976 | 0.34332 | -0.13733 | -2.7557 | -0.28839 | -0.05951 | 0.60882 | 47.6578 | 48.4406 | 121.9666 | 124.6353 | 0.34332 | 124.6628 | 70.1843 | -0.28839 | 124.6353 | 0.34332 | 70.1843 | 121.9666 | 124.6628 | -124.9878 | -125.0107
1308.6406 | 125.0107 | -60.8322 | 63.8718 | 0.08873 | 0.012469 | 0.010201 | -0.00084605 | 0.060558 | 0.00049134 | 0.072017 | -60.4019 | 63.8031 | -61.0657 | -61.0199 | 61.0657 | 9.462 | -13.0646 | -12.291 | 63.826 | -61.0657 | -0.23346 | -0.068664 | 0.4303 | -0.18768 | -2.8061 | -0.23346 | -0.045776 | 0.66376 | 47.7676 | 48.5413 | 121.8979 | 124.6353 | 0.4303 | 124.6582 | 70.2942 | -0.23346 | 124.6353 | 0.4303 | 70.2942 | 121.8979 | 124.6582 | -124.9374 | -124.9374
1309.6406 | 125.0381 | -60.8459 | 63.8718 | -0.018082 | 0.010547 | 0.010201 | 0.0017175 | 0.061199 | -0.0020721 | 0.073298 | -60.5255 | 63.7802 | -61.0931 | -61.0199 | 61.0748 | 9.6313 | -12.8998 | -12.0529 | 63.8168 | -61.0886 | -0.24719 | -0.091553 | 0.32043 | -0.17395 | -2.7969 | -0.24262 | -0.054932 | 0.56763 | 47.9462 | 48.793 | 121.9208 | 124.6262 | 0.32043 | 124.6628 | 70.4773 | -0.24262 | 124.6262 | 0.32043 | 70.4773 | 121.9208 | 124.6628 | -124.9649 | -124.9603
1310.6406 | 125.0244 | -60.878 | 63.8672 | -0.018082 | 0.0096921 | 0.0093459 | -0.0025549 | 0.062267 | 0.0017731 | 0.070735 | -60.5209 | 63.7482 | -61.1206 | -61.0153 | 61.0291 | 9.7183 | -12.6892 | -11.8561 | 63.7894 | -61.1114 | -0.24261 | -0.11902 | 0.35706 | -0.13733 | -2.8381 | -0.23346 | -0.077819 | 0.59967 | 48.1888 | 49.0219 | 121.907 | 124.6262 | 0.35706 | 124.6674 | 70.5963 | -0.23346 | 124.6262 | 0.35706 | 70.5963 | 121.907 | 124.6674 | -124.9878 | -124.9786
1311.6406 | 125.0473 | -60.8597 | 63.8443 | -0.063858 | 0.0094785 | 0.010628 | -0.0014869 | 0.05949 | 0.0028411 | 0.071589 | -60.4752 | 63.7299 | -61.0886 | -60.9924 | 61.0291 | 9.8419 | -12.5015 | -11.6272 | 63.7848 | -61.084 | -0.22888 | -0.11444 | 0.38452 | -0.13275 | -2.8152 | -0.2243 | -0.059509 | 0.6134 | 48.3582 | 49.2325 | 121.8887 | 124.5895 | 0.38452 | 124.6445 | 70.7016 | -0.2243 | 124.5895 | 0.38452 | 70.7016 | 121.8887 | 124.6445 | -124.9329 | -124.9283
1312.6406 | 124.9466 | -60.9055 | 63.8855 | -2.2993 | 0.010333 | 0.0095595 | 0.0032129 | 0.062694 | 0.0011321 | 0.071376 | -60.5118 | 63.8351 | -61.1252 | -61.0657 | 60.8505 | 9.8419 | -12.0438 | -11.5219 | 63.826 | -61.1755 | -0.21973 | -0.050354 | 0.39368 | -0.16022 | -3.035 | -0.27008 | -0.059509 | 0.6134 | 48.8617 | 49.3835 | 121.756 | 124.7406 | 0.39368 | 124.7314 | 70.7474 | -0.27008 | 124.7406 | 0.39368 | 70.7474 | 121.756 | 124.7314 | -125.0107 | -125.061
1313.6406 | 125.0748 | -60.9055 | 63.8168 | -0.14015 | 0.0092649 | 0.0095595 | -0.0010597 | 0.064403 | 0.0019867 | 0.070521 | -60.4568 | 63.6978 | -61.1343 | -61.0062 | 60.6949 | 10.4599 | -11.9568 | -11.7645 | 63.7711 | -61.1069 | -0.22888 | -0.11902 | 0.44861 | -0.10071 | -3.1219 | -0.20142 | -0.045776 | 0.67749 | 48.9487 | 49.1409 | 121.6003 | 124.6033 | 0.44861 | 124.6765 | 71.3654 | -0.20142 | 124.6033 | 0.44861 | 71.3654 | 121.6003 | 124.6765 | -124.9512 | -124.9237
1314.6406 | 125.0198 | -60.9512 | 63.7985 | 0.050583 | 0.01076 | 0.0099869 | -0.00020505 | 0.060558 | -0.00014946 | 0.071162 | -60.5576 | 63.6887 | -61.1801 | -61.116 | 60.8368 | 10.4324 | -11.7691 | -11.0596 | 63.7482 | -61.1755 | -0.22888 | -0.10986 | 0.39368 | -0.16479 | -2.9617 | -0.2243 | -0.050354 | 0.62256 | 49.1821 | 49.8917 | 121.788 | 124.6399 | 0.39368 | 124.6994 | 71.3837 | -0.2243 | 124.6399 | 0.39368 | 71.3837 | 121.788 | 124.6994 | -124.9786 | -124.9741
1315.6406 | 125.029 | -60.9283 | 63.7756 | -0.063858 | 0.010974 | 0.010628 | -0.0017005 | 0.060344 | 0.0026275 | 0.071162 | -60.5209 | 63.6703 | -61.1801 | -61.0748 | 60.8276 | 10.6018 | -11.6135 | -10.8215 | 63.707 | -61.1984 | -0.25177 | -0.10529 | 0.40741 | -0.14648 | -2.948 | -0.27008 | -0.068665 | 0.65918 | 49.3149 | 50.1068 | 121.756 | 124.5987 | 0.40741 | 124.6353 | 71.5302 | -0.27008 | 124.5987 | 0.40741 | 71.5302 | 121.756 | 124.6353 | -124.9557 | -124.9741
1316.6406 | 125.0565 | -60.9467 | 63.7939 | -0.056229 | 0.01076 | 0.013405 | 0.00043575 | 0.062694 | 0.0032683 | 0.072657 | -60.5209 | 63.6658 | -61.235 | -61.1114 | 60.7819 | 10.8032 | -11.3571 | -10.5972 | 63.707 | -61.203 | -0.28839 | -0.12817 | 0.42572 | -0.16479 | -3.0121 | -0.25635 | -0.086975 | 0.71411 | 49.5895 | 50.3494 | 121.7285 | 124.6124 | 0.42572 | 124.6536 | 71.7499 | -0.25635 | 124.6124 | 0.42572 | 71.7499 | 121.7285 | 124.6536 | -125.029 | -124.9969
1317.6406 | 125.0656 | -60.9421 | 63.7573 | -0.14015 | 0.0084103 | 0.010414 | 0.00022215 | 0.061412 | -0.0012177 | 0.071376 | -60.4843 | 63.6566 | -61.203 | -61.0886 | 60.7864 | 11.1099 | -11.2335 | -10.405 | 63.6703 | -61.1984 | -0.26093 | -0.10071 | 0.45776 | -0.14648 | -2.9709 | -0.25635 | -0.086975 | 0.71869 | 49.7086 | 50.5371 | 121.7285 | 124.5987 | 0.45776 | 124.6124 | 72.052 | -0.25635 | 124.5987 | 0.45776 | 72.052 | 121.7285 | 124.6124 | -124.9603 | -124.9557
1318.6406 | 125.0885 | -60.965 | 63.7344 | -0.048599 | 0.013324 | 0.011482 | -0.00020505 | 0.061412 | 0.0017731 | 0.072444 | -60.4889 | 63.6246 | -61.2122 | -61.1069 | 60.7407 | 11.3434 | -11.055 | -10.1486 | 63.6841 | -61.2076 | -0.24719 | -0.10986 | 0.47607 | -0.14191 | -2.9938 | -0.24262 | -0.050354 | 0.72327 | 49.91 | 50.8163 | 121.7056 | 124.5895 | 0.47607 | 124.649 | 72.3083 | -0.24262 | 124.5895 | 0.47607 | 72.3083 | 121.7056 | 124.649 | -124.9466 | -124.942
1319.6406 | 125.0793 | -60.9833 | 63.7207 | -0.10201 | 0.0092649 | 0.01191 | -0.0012733 | 0.060772 | 0.0036957 | 0.073085 | -60.5026 | 63.6154 | -61.2625 | -61.1114 | 60.6628 | 11.6226 | -10.7941 | -9.9289 | 63.6658 | -61.2305 | -0.27924 | -0.10529 | 0.48065 | -0.12817 | -3.0579 | -0.24719 | -0.054932 | 0.75989 | 50.1892 | 51.0544 | 121.6461 | 124.5987 | 0.48065 | 124.649 | 72.6059 | -0.24719 | 124.5987 | 0.48065 | 72.6059 | 121.6461 | 124.649 | -124.9832 | -124.9512
1320.6406 | 125.0656 | -60.997 | 63.6795 | -0.10201 | 0.0086239 | 0.010201 | -0.00084605 | 0.061626 | -0.00057686 | 0.072017 | -60.5026 | 63.6017 | -61.2762 | -61.1664 | 60.5896 | 11.8607 | -10.4507 | -9.6817 | 63.6337 | -61.235 | -0.27924 | -0.077819 | 0.49438 | -0.16937 | -3.0899 | -0.23804 | -0.045776 | 0.77362 | 50.5463 | 51.3153 | 121.5866 | 124.5987 | 0.49438 | 124.6307 | 72.8577 | -0.23804 | 124.5987 | 0.49438 | 72.8577 | 121.5866 | 124.6307 | -124.9557 | -124.9145
1321.6406 | 124.9878 | -61.0291 | 63.7024 | 0.27184 | 0.0086239 | 0.010628 | 0.0017175 | 0.063762 | 0.0017731 | 0.073939 | -60.553 | 63.588 | -61.3083 | -61.2213 | 60.553 | 12.0071 | -10.1807 | -9.4803 | 63.6337 | -61.2625 | -0.27924 | -0.11444 | 0.47607 | -0.19226 | -3.1494 | -0.23346 | -0.068665 | 0.75531 | 50.8484 | 51.5488 | 121.582 | 124.617 | 0.47607 | 124.6628 | 73.0362 | -0.23346 | 124.617 | 0.47607 | 73.0362 | 121.582 | 124.6628 | -125.0107 | -124.9649
1322.6406 | 125.0244 | -61.0291 | 63.6795 | -0.23933 | 0.0094785 | 0.013191 | 0.0010767 | 0.062908 | 6.414e-05 | 0.070948 | -60.466 | 63.6063 | -61.2991 | -61.1572 | 60.5072 | 12.2864 | -9.7229 | -9.0775 | 63.6292 | -61.3037 | -0.27008 | -0.073242 | 0.56305 | -0.12817 | -3.1723 | -0.27466 | -0.050354 | 0.83313 | 51.3062 | 51.9516 | 121.5363 | 124.6353 | 0.56305 | 124.6582 | 73.3154 | -0.27466 | 124.6353 | 0.56305 | 73.3154 | 121.5363 | 124.6582 | -124.9786 | -124.9832
1323.6406 | 125.0244 | -61.0703 | 63.6566 | 0.012436 | 0.0094785 | 0.0076369 | -0.00084605 | 0.062694 | 0.00049134 | 0.073298 | -60.5347 | 63.5696 | -61.3403 | -61.2396 | 60.4568 | 12.4832 | -9.5123 | -8.8211 | 63.5834 | -61.3083 | -0.27008 | -0.086975 | 0.53558 | -0.16937 | -3.1998 | -0.23804 | -0.073242 | 0.80566 | 51.5579 | 52.2491 | 121.5271 | 124.6399 | 0.53558 | 124.6536 | 73.5535 | -0.23804 | 124.6399 | 0.53558 | 73.5535 | 121.5271 | 124.6536 | -124.9969 | -124.9649
1324.6406 | 125.0473 | -61.0703 | 63.6246 | -0.04097 | 0.0090513 | 0.014259 | 0.00043575 | 0.062267 | 0.0024139 | 0.071803 | -60.553 | 63.5101 | -61.3403 | -61.2579 | 60.3928 | 12.7029 | -9.1141 | -8.519 | 63.5651 | -61.322 | -0.27008 | -0.11444 | 0.51727 | -0.18768 | -3.2318 | -0.25177 | -0.05951 | 0.78735 | 51.9562 | 52.5513 | 121.463 | 124.5804 | 0.51727 | 124.6353 | 73.7732 | -0.25177 | 124.5804 | 0.51727 | 73.7732 | 121.463 | 124.6353 | -124.9649 | -124.9466
1325.6406 | 125.061 | -61.0886 | 63.6063 | -0.071488 | 0.01076 | 0.010201 | 8.546e-06 | 0.060772 | 0.00091854 | 0.07223 | -60.5301 | 63.5101 | -61.3449 | -61.2396 | 60.3745 | 12.9227 | -8.8028 | -8.1345 | 63.5376 | -61.3495 | -0.25635 | -0.09613 | 0.55847 | -0.15106 | -3.2318 | -0.26093 | -0.068664 | 0.81482 | 52.2858 | 52.9541 | 121.463 | 124.5987 | 0.55847 | 124.6262 | 74.0112 | -0.26093 | 124.5987 | 0.55847 | 74.0112 | 121.463 | 124.6262 | -124.9512 | -124.9557
1326.6406 | 125.0702 | -61.1114 | 63.6063 | 0.0048064 | 0.010119 | 0.014259 | -0.00084605 | 0.062053 | 0.0013457 | 0.07223 | -60.5255 | 63.4964 | -61.3815 | -61.2717 | 60.3241 | 13.1287 | -8.4457 | -7.8094 | 63.5239 | -61.3632 | -0.27008 | -0.10986 | 0.58594 | -0.16022 | -3.2822 | -0.25177 | -0.082397 | 0.85602 | 52.6657 | 53.302 | 121.4355 | 124.6078 | 0.58594 | 124.6353 | 74.2401 | -0.25177 | 124.6078 | 0.58594 | 74.2401 | 121.4355 | 124.6353 | -124.9878 | -124.9695
1327.6562 | 124.8962 | -61.1801 | 63.6154 | 0.058212 | 0.014606 | 0.016182 | 0.0079125 | 0.064617 | 0.0041229 | 0.073726 | -60.5576 | 63.5788 | -61.441 | -61.6745 | 60.2234 | 13.4216 | -8.0704 | -7.6401 | 63.5559 | -61.4319 | -0.26093 | -0.036621 | 0.62256 | -0.49439 | -3.392 | -0.25177 | -0.059509 | 0.88348 | 53.1097 | 53.54 | 121.4035 | 124.7589 | 0.62256 | 124.736 | 74.6017 | -0.25177 | 124.7589 | 0.62256 | 74.6017 | 121.4035 | 124.736 | -125.0565 | -125.0473
1328.6406 | 125.0107 | -61.1618 | 63.5513 | 0.073471 | 0.010119 | 0.015968 | 0.0010767 | 0.064617 | -0.00036306 | 0.073298 | -60.5804 | 63.4644 | -61.4136 | -61.3495 | 60.1868 | 13.3804 | -7.6904 | -6.9077 | 63.5559 | -61.377 | -0.25177 | -0.086976 | 0.58136 | -0.18768 | -3.3646 | -0.21515 | 0.004577 | 0.83313 | 53.4714 | 54.2541 | 121.3486 | 124.6262 | 0.58136 | 124.7177 | 74.5422 | -0.21515 | 124.6262 | 0.58136 | 74.5422 | 121.3486 | 124.7177 | -124.9649 | -124.9283
1329.6406 | 125.0107 | -61.1481 | 63.5422 | 0.13451 | 0.010974 | 0.012764 | 0.0017175 | 0.063121 | 0.0015595 | 0.06988 | -60.585 | 63.446 | -61.4365 | -61.3632 | 60.1547 | 13.4583 | -7.3975 | -6.9031 | 63.4644 | -61.4136 | -0.28839 | -0.09613 | 0.56305 | -0.21515 | -3.3875 | -0.2655 | -0.07782 | 0.85144 | 53.7506 | 54.245 | 121.3028 | 124.5941 | 0.56305 | 124.6124 | 74.6063 | -0.2655 | 124.5941 | 0.56305 | 74.6063 | 121.3028 | 124.6124 | -124.9786 | -124.9557
1330.6406 | 124.9786 | -61.1893 | 63.501 | 0.10399 | 0.013537 | 0.011269 | 8.546e-06 | 0.062481 | -0.00014946 | 0.071376 | -60.5804 | 63.4277 | -61.4456 | -61.3907 | 60.1227 | 13.6185 | -7.0221 | -6.5964 | 63.4506 | -61.441 | -0.25635 | -0.073243 | 0.60883 | -0.20142 | -3.3783 | -0.25177 | -0.050354 | 0.86517 | 54.1672 | 54.5929 | 121.312 | 124.617 | 0.60883 | 124.6399 | 74.8077 | -0.25177 | 124.617 | 0.60883 | 74.8077 | 121.312 | 124.6399 | -124.9466 | -124.942
1331.6406 | 125.0107 | -61.2167 | 63.4918 | 0.073471 | 0.010974 | 0.01255 | 0.0034265 | 0.062908 | 0.00091854 | 0.07458 | -60.5713 | 63.3911 | -61.441 | -61.4456 | 60.0815 | 13.8565 | -6.6422 | -6.3446 | 63.4232 | -61.4731 | -0.2243 | -0.10071 | 0.64545 | -0.22888 | -3.4103 | -0.25635 | -0.068664 | 0.86975 | 54.5746 | 54.8721 | 121.2982 | 124.6078 | 0.64545 | 124.6399 | 75.0732 | -0.25635 | 124.6078 | 0.64545 | 75.0732 | 121.2982 | 124.6399 | -124.9329 | -124.9649
1332.6562 | 124.9741 | -61.2534 | 63.4964 | 0.027695 | 0.015033 | 0.013832 | 0.0068445 | 0.062481 | 0.0019867 | 0.072017 | -60.5118 | 63.5147 | -61.4685 | -61.3907 | 60.0082 | 14.0259 | -6.1981 | -5.9647 | 63.4552 | -61.5417 | -0.21515 | 0.01831 | 0.74158 | -0.13733 | -3.4882 | -0.28839 | -0.041199 | 0.95673 | 55.0552 | 55.2887 | 121.2616 | 124.7681 | 0.74158 | 124.7086 | 75.2792 | -0.28839 | 124.7681 | 0.74158 | 75.2792 | 121.2616 | 124.7086 | -124.9649 | -125.0381
1333.6406 | 125.0153 | -61.2579 | 63.4506 | -0.018082 | 0.011401 | 0.0095595 | -0.0017005 | 0.065899 | 0.0013457 | 0.074366 | -60.585 | 63.3865 | -61.528 | -61.4319 | 59.9945 | 14.2914 | -5.9143 | -5.6122 | 63.414 | -61.4685 | -0.27008 | -0.064087 | 0.67291 | -0.17395 | -3.4561 | -0.21057 | -0.036622 | 0.94299 | 55.3436 | 55.6458 | 121.2524 | 124.6445 | 0.67291 | 124.6719 | 75.5493 | -0.21057 | 124.6445 | 0.67291 | 75.5493 | 121.2524 | 124.6719 | -124.9786 | -124.9191
1334.6406 | 125.0153 | -61.2808 | 63.4415 | -0.20119 | 0.0096921 | 0.013191 | -0.00041865 | 0.063121 | 0.0011321 | 0.073298 | -60.6308 | 63.3545 | -61.5234 | -61.4548 | 59.9121 | 14.4974 | -5.4794 | -5.2094 | 63.382 | -61.528 | -0.24261 | -0.086975 | 0.65002 | -0.17395 | -3.5294 | -0.24719 | -0.059509 | 0.89264 | 55.8014 | 56.0715 | 121.1929 | 124.6353 | 0.65002 | 124.6628 | 75.7782 | -0.24719 | 124.6353 | 0.65002 | 75.7782 | 121.1929 | 124.6628 | -124.9649 | -124.9695
1335.6406 | 125.0015 | -61.2946 | 63.4415 | 0.065841 | 0.013751 | 0.012978 | 0.0017175 | 0.06184 | 0.0034821 | 0.073298 | -60.5804 | 63.3179 | -61.5417 | -61.4822 | 59.8938 | 14.7308 | -5.2414 | -4.9622 | 63.3728 | -61.5509 | -0.24719 | -0.1236 | 0.71411 | -0.18768 | -3.5477 | -0.25635 | -0.068664 | 0.9613 | 56.0532 | 56.3324 | 121.1884 | 124.6124 | 0.71411 | 124.6674 | 76.0254 | -0.25635 | 124.6124 | 0.71411 | 76.0254 | 121.1884 | 124.6674 | -124.9832 | -124.9924
1336.6406 | 124.9969 | -61.2991 | 63.3774 | 0.073471 | 0.012469 | 0.012978 | 0.0019311 | 0.063335 | 0.0024139 | 0.073085 | -60.553 | 63.3179 | -61.5601 | -61.4685 | 59.8755 | 14.946 | -4.8935 | -4.6143 | 63.3179 | -61.5417 | -0.26093 | -0.059509 | 0.74615 | -0.16937 | -3.5019 | -0.24262 | -0.059509 | 1.0071 | 56.4056 | 56.6849 | 121.1746 | 124.617 | 0.74615 | 124.617 | 76.2451 | -0.24262 | 124.617 | 0.74615 | 76.2451 | 121.1746 | 124.617 | -124.9374 | -124.9191
1337.6562 | 124.9146 | -61.3129 | 63.4323 | -0.23933 | 0.014819 | 0.011696 | 0.0047081 | 0.063549 | 0.0036957 | 0.073298 | -60.5667 | 63.4277 | -61.5417 | -61.5051 | 59.8022 | 15.0421 | -4.3671 | -4.335 | 63.4048 | -61.5784 | -0.22888 | -0.004578 | 0.74616 | -0.19226 | -3.6301 | -0.2655 | -0.027466 | 0.97504 | 56.9458 | 56.9778 | 121.1151 | 124.7406 | 0.74616 | 124.7177 | 76.355 | -0.2655 | 124.7406 | 0.74616 | 76.355 | 121.1151 | 124.7177 | -124.9741 | -125.0107
1338.6406 | 125.0153 | -61.3083 | 63.4048 | 0.073471 | 0.012469 | 0.01191 | 8.546e-06 | 0.063976 | 0.0017731 | 0.071803 | -60.5759 | 63.2996 | -61.5784 | -61.5326 | 59.7839 | 15.3076 | -4.2114 | -4.0054 | 63.3545 | -61.5417 | -0.27008 | -0.10529 | 0.73242 | -0.2243 | -3.6209 | -0.23346 | -0.050354 | 1.0025 | 57.0969 | 57.3029 | 121.0922 | 124.6078 | 0.73242 | 124.6628 | 76.6159 | -0.23346 | 124.6078 | 0.73242 | 76.6159 | 121.0922 | 124.6628 | -124.9832 | -124.9466
1339.6406 | 125.0107 | -61.3403 | 63.3636 | 0.0811 | 0.012897 | 0.015968 | 0.0034265 | 0.062908 | -0.00057686 | 0.072657 | -60.5942 | 63.2721 | -61.615 | -61.5326 | 59.8846 | 15.6876 | -4.1153 | -3.6758 | 63.3133 | -61.5646 | -0.27466 | -0.091552 | 0.74615 | -0.19226 | -3.479 | -0.2243 | -0.050354 | 1.0208 | 57.225 | 57.6645 | 121.225 | 124.6124 | 0.74615 | 124.6536 | 77.0279 | -0.2243 | 124.6124 | 0.74615 | 77.0279 | 121.225 | 124.6536 | -124.9786 | -124.9283
1340.6406 | 125.0198 | -61.3403 | 63.3636 | 0.096359 | 0.014178 | 0.016823 | 0.0021447 | 0.06483 | 0.00027774 | 0.07458 | -60.5942 | 63.2629 | -61.6104 | -61.5463 | 59.7107 | 15.7288 | -3.5294 | -3.3829 | 63.2904 | -61.6196 | -0.27008 | -0.10071 | 0.74615 | -0.20599 | -3.653 | -0.27924 | -0.073242 | 1.0162 | 57.811 | 57.9575 | 121.051 | 124.6033 | 0.74615 | 124.6307 | 77.0691 | -0.27924 | 124.6033 | 0.74615 | 77.0691 | 121.051 | 124.6307 | -124.9741 | -124.9832
1341.6406 | 125.0107 | -61.3907 | 63.3087 | 0.12688 | 0.014392 | 0.012123 | 0.0017175 | 0.062481 | -0.00036306 | 0.075007 | -60.5942 | 63.2217 | -61.6425 | -61.5738 | 59.697 | 15.9485 | -3.2318 | -3.0441 | 63.2767 | -61.6287 | -0.25177 | -0.086975 | 0.79651 | -0.18311 | -3.6118 | -0.23804 | -0.032044 | 1.0483 | 58.1589 | 58.3466 | 121.0876 | 124.6124 | 0.79651 | 124.6674 | 77.3392 | -0.23804 | 124.6124 | 0.79651 | 77.3392 | 121.0876 | 124.6674 | -124.9512 | -124.9374
1342.6562 | 124.942 | -61.3907 | 63.3728 | -0.04097 | 0.013965 | 0.012123 | 0.010049 | 0.063335 | 0.00070494 | 0.07458 | -60.5392 | 63.2858 | -61.6837 | -61.5417 | 59.6741 | 16.0767 | -3.1128 | -2.8702 | 63.2721 | -61.6974 | -0.29297 | -0.086975 | 0.85144 | -0.15106 | -3.6987 | -0.3067 | -0.10071 | 1.1444 | 58.2779 | 58.5205 | 121.0648 | 124.6765 | 0.85144 | 124.6628 | 77.4673 | -0.3067 | 124.6765 | 0.85144 | 77.4673 | 121.0648 | 124.6628 | -125.0565 | -125.0702
1343.6406 | 125.0336 | -61.3998 | 63.2858 | 0.14214 | 0.01311 | 0.015541 | 0.0027855 | 0.065044 | 0.0013457 | 0.07458 | -60.5301 | 63.1805 | -61.615 | -61.5463 | 59.6695 | 16.3467 | -2.7145 | -2.5681 | 63.2355 | -61.6562 | -0.21515 | -0.10529 | 0.86975 | -0.14648 | -3.6163 | -0.25635 | -0.050354 | 1.0849 | 58.6853 | 58.8318 | 121.0693 | 124.5804 | 0.86975 | 124.6353 | 77.7466 | -0.25635 | 124.5804 | 0.86975 | 77.7466 | 121.0693 | 124.6353 | -124.9008 | -124.942
1344.6406 | 124.9969 | -61.3998 | 63.2904 | 0.18028 | 0.013965 | 0.016396 | 0.0036401 | 0.064617 | 0.0024139 | 0.076289 | -60.5438 | 63.2217 | -61.6745 | -61.5921 | 59.6191 | 16.5024 | -2.3849 | -2.3209 | 63.2172 | -61.6745 | -0.27466 | -0.068664 | 0.85602 | -0.19226 | -3.6713 | -0.27466 | -0.073242 | 1.1307 | 59.0149 | 59.079 | 121.019 | 124.6216 | 0.85602 | 124.617 | 77.9022 | -0.27466 | 124.6216 | 0.85602 | 77.9022 | 121.019 | 124.617 | -124.9649 | -124.9649
1345.6406 | 124.9924 | -61.3998 | 63.2858 | 0.17265 | 0.014606 | 0.016396 | 0.0023583 | 0.061626 | 0.00091854 | 0.073298 | -60.5438 | 63.2034 | -61.6745 | -61.5784 | 59.6054 | 16.6351 | -2.0874 | -2.037 | 63.2172 | -61.6791 | -0.27466 | -0.082398 | 0.85602 | -0.17853 | -3.6804 | -0.27924 | -0.068665 | 1.1307 | 59.3124 | 59.3628 | 121.0052 | 124.6033 | 0.85602 | 124.617 | 78.035 | -0.27924 | 124.6033 | 0.85602 | 78.035 | 121.0052 | 124.617 | -124.9603 | -124.9649
1346.6406 | 124.9741 | -61.4227 | 63.2812 | 0.13451 | 0.013751 | 0.012123 | 0.0025719 | 0.061626 | 0.0022003 | 0.073939 | -60.5942 | 63.176 | -61.6791 | -61.6013 | 59.5688 | 16.7862 | -1.7166 | -1.8402 | 63.2172 | -61.6882 | -0.25635 | -0.10529 | 0.82855 | -0.17853 | -3.7125 | -0.2655 | -0.064087 | 1.0849 | 59.7061 | 59.5825 | 120.9915 | 124.5987 | 0.82855 | 124.6399 | 78.2089 | -0.2655 | 124.5987 | 0.82855 | 78.2089 | 120.9915 | 124.6399 | -124.9603 | -124.9695
1347.6406 | 125.0336 | -61.4182 | 63.2812 | -0.056229 | 0.012042 | 0.013405 | 0.0027855 | 0.063549 | -0.00036306 | 0.073726 | -60.5942 | 63.1668 | -61.702 | -61.6013 | 59.5596 | 16.951 | -1.474 | -1.5289 | 63.2401 | -61.6928 | -0.28381 | -0.11444 | 0.82397 | -0.1831 | -3.7216 | -0.27466 | -0.041199 | 1.1078 | 59.9442 | 59.8892 | 120.9778 | 124.585 | 0.82397 | 124.6582 | 78.3691 | -0.27466 | 124.585 | 0.82397 | 78.3691 | 120.9778 | 124.6582 | -124.9832 | -124.9741
1348.6406 | 125.0061 | -61.4914 | 63.2355 | 0.18028 | 0.012683 | 0.012978 | 0.0038537 | 0.063762 | 0.0015595 | 0.072871 | -60.585 | 63.1439 | -61.734 | -61.6516 | 59.4772 | 17.1021 | -1.2543 | -1.3458 | 63.176 | -61.7111 | -0.24262 | -0.091553 | 0.90637 | -0.16022 | -3.7582 | -0.21973 | -0.05951 | 1.149 | 60.2371 | 60.1456 | 120.9686 | 124.6353 | 0.90637 | 124.6674 | 78.5934 | -0.21973 | 124.6353 | 0.90637 | 78.5934 | 120.9686 | 124.6674 | -124.9695 | -124.9466
1349.6406 | 125.061 | -61.4456 | 63.2034 | 0.15739 | 0.013751 | 0.015968 | 0.0055627 | 0.062694 | 0.0015595 | 0.075862 | -60.5438 | 63.1348 | -61.7249 | -61.615 | 59.4864 | 17.2806 | -1.1078 | -1.1215 | 63.1485 | -61.7432 | -0.27924 | -0.068664 | 0.90179 | -0.16937 | -3.717 | -0.29755 | -0.054931 | 1.181 | 60.3378 | 60.3241 | 120.932 | 124.5804 | 0.90179 | 124.5941 | 78.7262 | -0.29755 | 124.5804 | 0.90179 | 78.7262 | 120.932 | 124.5941 | -124.9283 | -124.9466
1350.6406 | 125.0473 | -61.4777 | 63.1897 | 0.16502 | 0.014606 | 0.018318 | 0.0068445 | 0.065044 | -0.00014946 | 0.073512 | -60.5392 | 63.1119 | -61.7203 | -61.6287 | 59.4543 | 17.4179 | -0.87433 | -0.94299 | 63.1485 | -61.7432 | -0.24262 | -0.07782 | 0.93841 | -0.15106 | -3.7354 | -0.2655 | -0.041198 | 1.181 | 60.6033 | 60.5347 | 120.932 | 124.5895 | 0.93841 | 124.6262 | 78.8956 | -0.2655 | 124.5895 | 0.93841 | 78.8956 | 120.932 | 124.6262 | -124.91 | -124.9329
1351.6406 | 125.0336 | -61.4731 | 63.2217 | 0.14976 | 0.011615 | 0.012337 | 0.0027855 | 0.062481 | 0.0019867 | 0.072871 | -60.5667 | 63.121 | -61.7294 | -61.6653 | 59.4269 | 17.4591 | -0.60883 | -0.78278 | 63.1714 | -61.7477 | -0.25635 | -0.10071 | 0.90637 | -0.19226 | -3.7949 | -0.27466 | -0.050354 | 1.1627 | 60.8643 | 60.6903 | 120.9 | 124.5941 | 0.90637 | 124.6445 | 78.9322 | -0.27466 | 124.5941 | 0.90637 | 78.9322 | 120.9 | 124.6445 | -124.9512 | -124.9695
1352.6406 | 125.0519 | -61.4365 | 63.2629 | -0.20882 | 0.011615 | 0.011696 | -0.0038367 | 0.063549 | 0.0011321 | 0.076075 | -60.4935 | 63.1485 | -61.7203 | -61.6379 | 59.5642 | 17.6743 | -0.45776 | -0.41199 | 63.1622 | -61.7157 | -0.28381 | -0.11444 | 0.94299 | -0.20142 | -3.6987 | -0.27924 | -0.10071 | 1.2268 | 60.9787 | 61.0245 | 121.0007 | 124.585 | 0.94299 | 124.5987 | 79.1107 | -0.27924 | 124.585 | 0.94299 | 79.1107 | 121.0007 | 124.5987 | -124.9832 | -124.9786
1353.6406 | 125.0061 | -61.4822 | 63.176 | 0.058212 | 0.011188 | 0.0149 | 0.0015039 | 0.063335 | 0.00027774 | 0.07458 | -60.5988 | 63.1027 | -61.7615 | -61.6791 | 59.3582 | 17.7017 | -0.1236 | -0.40283 | 63.176 | -61.7386 | -0.27924 | -0.073242 | 0.88348 | -0.19684 | -3.8177 | -0.25635 | 0 | 1.1627 | 61.3586 | 61.0794 | 120.8405 | 124.585 | 0.88348 | 124.6582 | 79.184 | -0.25635 | 124.585 | 0.88348 | 79.184 | 120.8405 | 124.6582 | -124.9374 | -124.9145
1354.6406 | 125.1343 | -61.4777 | 63.2172 | 0.14214 | 0.013537 | 0.011482 | 0.0029993 | 0.063976 | 0.0028411 | 0.076289 | -60.5804 | 63.089 | -61.7523 | -61.6837 | 59.3445 | 17.7612 | 0.036621 | -0.24261 | 63.1531 | -61.7523 | -0.27466 | -0.12817 | 0.89722 | -0.20599 | -3.8727 | -0.27466 | -0.064087 | 1.1719 | 61.5143 | 61.235 | 120.8221 | 124.5666 | 0.89722 | 124.6307 | 79.2389 | -0.27466 | 124.5666 | 0.89722 | 79.2389 | 120.8221 | 124.6307 | -124.9695 | -124.9695
1355.6406 | 124.9146 | -61.5189 | 63.2355 | 0.08873 | 0.010974 | 0.013405 | -0.00020505 | 0.063976 | 0.0034821 | 0.073512 | -60.5942 | 63.1073 | -61.7569 | -61.7111 | 59.317 | 17.8528 | 0.20599 | -0.07782 | 63.1393 | -61.7752 | -0.23804 | -0.12817 | 0.92468 | -0.19226 | -3.9185 | -0.25635 | -0.096131 | 1.1627 | 61.7249 | 61.441 | 120.8359 | 124.6262 | 0.92468 | 124.6582 | 79.3716 | -0.25635 | 124.6262 | 0.92468 | 79.3716 | 120.8359 | 124.6582 | -124.9924 | -125.0107
1356.6406 | 125.0107 | -61.5143 | 63.1897 | 0.12688 | 0.012683 | 0.012123 | 0.0036401 | 0.062908 | -0.0014313 | 0.074153 | -60.553 | 63.089 | -61.7752 | -61.6745 | 59.3353 | 17.9352 | 0.30212 | 0.10071 | 63.1256 | -61.7844 | -0.26093 | -0.10071 | 0.9613 | -0.16022 | -3.8544 | -0.27008 | -0.064087 | 1.2222 | 61.8164 | 61.615 | 120.8496 | 124.6033 | 0.9613 | 124.6399 | 79.4495 | -0.27008 | 124.6033 | 0.9613 | 79.4495 | 120.8496 | 124.6399 | -124.9649 | -124.9741
1357.6406 | 124.9969 | -61.4777 | 63.1805 | -0.010452 | 0.012256 | 0.011269 | 0.00043575 | 0.063121 | 0.00091854 | 0.075221 | -60.5576 | 63.1027 | -61.734 | -61.6837 | 59.3262 | 18.013 | 0.53101 | 0.27008 | 63.121 | -61.7477 | -0.25635 | -0.07782 | 0.9201 | -0.20599 | -3.8544 | -0.27008 | -0.059509 | 1.1765 | 62.0087 | 61.7477 | 120.8038 | 124.5804 | 0.9201 | 124.5987 | 79.4907 | -0.27008 | 124.5804 | 0.9201 | 79.4907 | 120.8038 | 124.5987 | -124.9146 | -124.9283
1358.6406 | 125.0793 | -61.496 | 63.1943 | 0.096359 | 0.01076 | 0.015114 | 0.00064935 | 0.06419 | 0.0015595 | 0.073512 | -60.5438 | 63.0798 | -61.7569 | -61.6928 | 59.2804 | 18.0817 | 0.67291 | 0.3891 | 63.1439 | -61.7294 | -0.26093 | -0.11444 | 0.95215 | -0.19684 | -3.9139 | -0.23346 | -0.050354 | 1.2131 | 62.1689 | 61.8851 | 120.7764 | 124.5758 | 0.95215 | 124.6399 | 79.5776 | -0.23346 | 124.5758 | 0.95215 | 79.5776 | 120.7764 | 124.6399 | -124.9512 | -124.9237
1359.6406 | 125.1251 | -61.5005 | 63.2034 | 0.096359 | 0.013751 | 0.015541 | 0.0027855 | 0.061626 | -0.00014946 | 0.072657 | -60.5301 | 63.1119 | -61.7615 | -61.702 | 59.2758 | 18.1732 | 0.79651 | 0.50354 | 63.1393 | -61.7477 | -0.26093 | -0.091553 | 0.97046 | -0.20142 | -3.9276 | -0.24719 | -0.064087 | 1.2314 | 62.2971 | 62.0041 | 120.7764 | 124.6124 | 0.97046 | 124.6399 | 79.6738 | -0.24719 | 124.6124 | 0.97046 | 79.6738 | 120.7764 | 124.6399 | -124.9649 | -124.9512
1360.6406 | 125.0107 | -61.4731 | 63.1668 | -0.018082 | 0.011828 | 0.013191 | 0.0036401 | 0.063549 | 0.00091854 | 0.073512 | -60.5209 | 63.1073 | -61.7523 | -61.6699 | 59.2804 | 18.219 | 0.94757 | 0.67749 | 63.1256 | -61.7706 | -0.27924 | -0.059509 | 0.95215 | -0.19684 | -3.8864 | -0.29755 | -0.041199 | 1.2314 | 62.4207 | 62.1506 | 120.7535 | 124.5804 | 0.95215 | 124.5987 | 79.6921 | -0.29755 | 124.5804 | 0.95215 | 79.6921 | 120.7535 | 124.5987 | -124.9191 | -124.9374
1361.6406 | 125.0336 | -61.5189 | 63.1805 | -0.048599 | 0.010974 | 0.015328 | 0.0010767 | 0.060344 | 0.0043365 | 0.073939 | -60.5347 | 63.0844 | -61.7706 | -61.702 | 59.2712 | 18.3243 | 1.0757 | 0.81024 | 63.1348 | -61.7569 | -0.25177 | -0.09613 | 0.98419 | -0.18311 | -3.9093 | -0.23804 | -0.045776 | 1.236 | 62.5946 | 62.3291 | 120.7901 | 124.6033 | 0.98419 | 124.6536 | 79.8431 | -0.23804 | 124.6033 | 0.98419 | 79.8431 | 120.7901 | 124.6536 | -124.9512 | -124.9374
1362.6406 | 124.9512 | -61.5097 | 63.2401 | -0.21645 | 0.011828 | 0.014687 | 0.0051355 | 0.060772 | 0.0015595 | 0.075007 | -60.4889 | 63.1165 | -61.7706 | -61.6745 | 59.2163 | 18.3197 | 1.2772 | 0.91553 | 63.1805 | -61.8118 | -0.26093 | -0.1236 | 1.0208 | -0.1648 | -4.0237 | -0.30212 | -0.059509 | 1.2817 | 62.7869 | 62.4252 | 120.726 | 124.6262 | 1.0208 | 124.6902 | 79.8294 | -0.30212 | 124.6262 | 1.0208 | 79.8294 | 120.726 | 124.6902 | -125.0107 | -125.0519
1363.6406 | 124.9969 | -61.5372 | 63.1668 | 0.13451 | 0.014178 | 0.016396 | 0.0040673 | 0.064617 | -0.00079046 | 0.07458 | -60.4935 | 63.0753 | -61.7752 | -61.6882 | 59.1888 | 18.3746 | 1.1581 | 1.0071 | 63.1165 | -61.7661 | -0.23804 | -0.091553 | 1.0437 | -0.15106 | -3.978 | -0.22888 | -0.050354 | 1.2817 | 62.6953 | 62.5443 | 120.726 | 124.6124 | 1.0437 | 124.6536 | 79.9118 | -0.22888 | 124.6124 | 1.0437 | 79.9118 | 120.726 | 124.6536 | -124.942 | -124.9329
1364.6406 | 124.9878 | -61.5326 | 63.1668 | 0.11925 | 0.014392 | 0.015328 | 0.0047081 | 0.063549 | -0.00079046 | 0.074153 | -60.466 | 63.0341 | -61.8164 | -61.7065 | 59.1751 | 18.4204 | 1.2268 | 1.0757 | 63.1027 | -61.7981 | -0.28381 | -0.13275 | 1.0666 | -0.17395 | -3.9917 | -0.2655 | -0.064087 | 1.3504 | 62.7594 | 62.6083 | 120.7077 | 124.5667 | 1.0666 | 124.6353 | 79.953 | -0.2655 | 124.5667 | 1.0666 | 79.953 | 120.7077 | 124.6353 | -124.9832 | -124.9649
1365.6406 | 125.0153 | -61.4914 | 63.1805 | -0.04097 | 0.011828 | 0.014046 | 0.0027855 | 0.062908 | 0.0022003 | 0.073512 | -60.5209 | 63.0524 | -61.7798 | -61.7294 | 59.1385 | 18.425 | 1.3641 | 1.1627 | 63.1302 | -61.7615 | -0.28839 | -0.12817 | 0.97046 | -0.23804 | -4.0421 | -0.27008 | -0.050354 | 1.2588 | 62.8555 | 62.6541 | 120.6299 | 124.5438 | 0.97046 | 124.6216 | 79.9164 | -0.27008 | 124.5438 | 0.97046 | 79.9164 | 120.6299 | 124.6216 | -124.9603 | -124.942
1366.6406 | 124.9878 | -61.4914 | 63.1897 | 0.035324 | 0.011188 | 0.01255 | 0.0023583 | 0.061626 | 0.0015595 | 0.076075 | -60.5118 | 63.0936 | -61.7844 | -61.6745 | 59.1385 | 18.4525 | 1.4145 | 1.2268 | 63.121 | -61.7752 | -0.29297 | -0.09613 | 0.97961 | -0.18311 | -4.0512 | -0.28381 | -0.068664 | 1.2726 | 62.9059 | 62.7182 | 120.6299 | 124.585 | 0.97961 | 124.6124 | 79.9438 | -0.28381 | 124.585 | 0.97961 | 79.9438 | 120.6299 | 124.6124 | -124.9741 | -124.9649
1367.6406 | 125.0244 | -61.4868 | 63.1989 | -0.21645 | 0.011188 | 0.014259 | 0.0036401 | 0.059276 | 0.0013457 | 0.075862 | -60.4065 | 63.121 | -61.7477 | -61.6196 | 59.1888 | 18.5394 | 1.5244 | 1.387 | 63.1348 | -61.7706 | -0.26093 | -0.07782 | 1.0803 | -0.13275 | -4.01 | -0.28381 | -0.064087 | 1.3412 | 63.0112 | 62.8738 | 120.6757 | 124.6078 | 1.0803 | 124.6216 | 80.0262 | -0.28381 | 124.6078 | 1.0803 | 80.0262 | 120.6757 | 124.6216 | -124.9466 | -124.9695
1368.6406 | 125.0107 | -61.496 | 63.1714 | -0.071488 | 0.013965 | 0.013832 | 0.0012903 | 0.061626 | -0.00079046 | 0.073512 | -60.466 | 63.0936 | -61.7844 | -61.702 | 59.111 | 18.5257 | 1.593 | 1.4282 | 63.1165 | -61.7798 | -0.28839 | -0.07782 | 1.03 | -0.20599 | -4.0604 | -0.28381 | -0.054932 | 1.3184 | 63.089 | 62.9242 | 120.607 | 124.5895 | 1.03 | 124.6124 | 80.0217 | -0.28381 | 124.5895 | 1.03 | 80.0217 | 120.607 | 124.6124 | -124.9557 | -124.9512
1369.6406 | 125.0107 | -61.5051 | 63.1531 | -0.025711 | 0.01546 | 0.014687 | 0.0036401 | 0.061412 | 0.0028411 | 0.075221 | -60.466 | 63.0936 | -61.7752 | -61.6882 | 59.1019 | 18.5486 | 1.6571 | 1.4969 | 63.1302 | -61.7615 | -0.27008 | -0.059509 | 1.0391 | -0.1831 | -4.0512 | -0.25635 | -0.022888 | 1.3092 | 63.1622 | 63.002 | 120.607 | 124.5987 | 1.0391 | 124.6353 | 80.0537 | -0.25635 | 124.5987 | 1.0391 | 80.0537 | 120.607 | 124.6353 | -124.9283 | -124.9146
1370.6406 | 124.9741 | -61.5097 | 63.1805 | 0.15739 | 0.012469 | 0.012978 | 0.0029993 | 0.061626 | 0.0019867 | 0.074794 | -60.4706 | 63.0524 | -61.7981 | -61.7065 | 59.0698 | 18.6035 | 1.7166 | 1.5656 | 63.1348 | -61.7798 | -0.28839 | -0.12817 | 1.0391 | -0.19684 | -4.1107 | -0.27008 | -0.045776 | 1.3275 | 63.2263 | 63.0753 | 120.5795 | 124.5621 | 1.0391 | 124.6445 | 80.1132 | -0.27008 | 124.5621 | 1.0391 | 80.1132 | 120.5795 | 124.6445 | -124.9786 | -124.9603
1371.6406 | 124.9969 | -61.5234 | 63.176 | -0.086746 | 0.014392 | 0.015541 | 0.0029993 | 0.063762 | 0.0026275 | 0.073512 | -60.4752 | 63.0844 | -61.7844 | -61.7157 | 59.0378 | 18.6859 | 1.918 | 1.7761 | 63.1165 | -61.7752 | -0.26093 | -0.091552 | 1.0483 | -0.19226 | -4.1382 | -0.25177 | -0.059509 | 1.3092 | 63.4415 | 63.2996 | 120.5612 | 124.6078 | 1.0483 | 124.6399 | 80.2094 | -0.25177 | 124.6078 | 1.0483 | 80.2094 | 120.5612 | 124.6399 | -124.9603 | -124.9512
1372.6406 | 125.0198 | -61.4914 | 63.1805 | 0.27184 | 0.011615 | 0.01255 | 0.0029993 | 0.060558 | 0.0017731 | 0.075648 | -60.3653 | 63.0844 | -61.7661 | -61.6287 | 59.1156 | 18.75 | 1.9409 | 1.9272 | 63.0981 | -61.7569 | -0.27466 | -0.09613 | 1.1261 | -0.13733 | -4.0649 | -0.2655 | -0.082397 | 1.4008 | 63.4323 | 63.4186 | 120.607 | 124.5758 | 1.1261 | 124.5895 | 80.2414 | -0.2655 | 124.5758 | 1.1261 | 80.2414 | 120.607 | 124.5895 | -124.9466 | -124.9374
1373.6406 | 124.9832 | -61.5051 | 63.1897 | -0.0028231 | 0.012042 | 0.013191 | 0.0012903 | 0.062053 | 0.0015595 | 0.073939 | -60.2325 | 63.0981 | -61.7477 | -61.7249 | 59.0149 | 18.6539 | 1.9958 | 1.9272 | 63.121 | -61.7889 | -0.24262 | -0.091552 | 1.2726 | -0.21973 | -4.1748 | -0.28381 | -0.068664 | 1.5152 | 63.501 | 63.4323 | 120.52 | 124.6033 | 1.2726 | 124.6262 | 80.159 | -0.28381 | 124.6033 | 1.2726 | 80.159 | 120.52 | 124.6262 | -124.9374 | -124.9786
1374.6406 | 125.0061 | -61.5372 | 63.1714 | -0.010452 | 0.01311 | 0.012123 | 0.0025719 | 0.061412 | 0.0015595 | 0.074794 | -60.4568 | 63.0661 | -61.8118 | -61.7111 | 58.9966 | 18.8095 | 2.1103 | 2.0554 | 63.0936 | -61.7615 | -0.27466 | -0.10529 | 1.0803 | -0.17395 | -4.1748 | -0.2243 | -0.07782 | 1.355 | 63.6475 | 63.5925 | 120.5338 | 124.6033 | 1.0803 | 124.6307 | 80.3467 | -0.2243 | 124.6033 | 1.0803 | 80.3467 | 120.5338 | 124.6307 | -124.9832 | -124.9329
1375.6406 | 125.0061 | -61.5097 | 63.1622 | -0.04097 | 0.012469 | 0.010414 | 0.0027855 | 0.060558 | 6.414e-05 | 0.073512 | -60.4431 | 63.0661 | -61.7889 | -61.7111 | 58.9874 | 18.8004 | 2.1332 | 2.0966 | 63.0753 | -61.7889 | -0.27923 | -0.09613 | 1.0666 | -0.20142 | -4.1748 | -0.27923 | -0.086975 | 1.3458 | 63.6429 | 63.6063 | 120.4971 | 124.5758 | 1.0666 | 124.585 | 80.3101 | -0.27923 | 124.5758 | 1.0666 | 80.3101 | 120.4971 | 124.585 | -124.9512 | -124.9512
1376.6406 | 125.0107 | -61.5463 | 63.1851 | -0.056229 | 0.014392 | 0.012123 | 0.0032129 | 0.061199 | 0.0019867 | 0.075221 | -60.4294 | 63.0569 | -61.7798 | -61.6974 | 58.9737 | 18.7912 | 2.1515 | 2.124 | 63.1073 | -61.7706 | -0.23346 | -0.12817 | 1.1169 | -0.15106 | -4.2114 | -0.2243 | -0.07782 | 1.3504 | 63.6978 | 63.6703 | 120.52 | 124.6033 | 1.1169 | 124.6536 | 80.3375 | -0.2243 | 124.6033 | 1.1169 | 80.3375 | 120.52 | 124.6536 | -124.9649 | -124.9557
1377.6406 | 124.9557 | -61.5234 | 63.208 | -0.27748 | 0.015033 | 0.014046 | 0.0029993 | 0.060985 | 0.00027774 | 0.075221 | -60.3653 | 63.1485 | -61.7752 | -61.6791 | 58.9737 | 18.7271 | 2.2842 | 2.179 | 63.1531 | -61.7844 | -0.25177 | -0.059509 | 1.1581 | -0.15564 | -4.2343 | -0.26093 | -0.054932 | 1.4099 | 63.8077 | 63.7024 | 120.4971 | 124.6719 | 1.1581 | 124.6765 | 80.2505 | -0.26093 | 124.6719 | 1.1581 | 80.2505 | 120.4971 | 124.6765 | -124.9832 | -124.9924
1378.6406 | 125.0107 | -61.5097 | 63.208 | 0.0811 | 0.013324 | 0.013619 | 0.0034265 | 0.062908 | 0.00070494 | 0.074794 | -60.3882 | 63.1073 | -61.7706 | -61.6837 | 58.9554 | 18.837 | 2.1927 | 2.0966 | 63.1439 | -61.7706 | -0.26093 | -0.10071 | 1.1215 | -0.17395 | -4.2526 | -0.26093 | -0.064087 | 1.3824 | 63.7024 | 63.6063 | 120.4651 | 124.617 | 1.1215 | 124.6536 | 80.3467 | -0.26093 | 124.617 | 1.1215 | 80.3467 | 120.4651 | 124.6536 | -124.9786 | -124.9786
1379.6406 | 125.0015 | -61.4868 | 63.2126 | 0.17265 | 0.012683 | 0.014473 | 0.0023583 | 0.062053 | 0.0011321 | 0.075435 | -60.379 | 63.1165 | -61.7661 | -61.6791 | 58.9508 | 18.8141 | 2.1378 | 2.0874 | 63.1439 | -61.734 | -0.27924 | -0.09613 | 1.1078 | -0.19226 | -4.2618 | -0.24719 | -0.068664 | 1.387 | 63.6246 | 63.5742 | 120.4376 | 124.6033 | 1.1078 | 124.6307 | 80.3009 | -0.24719 | 124.6033 | 1.1078 | 80.3009 | 120.4376 | 124.6307 | -124.9786 | -124.9466
1380.6406 | 125.0427 | -61.5143 | 63.176 | -0.033341 | 0.01546 | 0.014046 | 0.00086295 | 0.062694 | 0.0015595 | 0.074794 | -60.3745 | 63.0798 | -61.7844 | -61.6562 | 58.9371 | 18.9651 | 2.2476 | 2.1561 | 63.1165 | -61.7386 | -0.27008 | -0.09613 | 1.1398 | -0.14191 | -4.2389 | -0.2243 | -0.059509 | 1.4099 | 63.7619 | 63.6703 | 120.4514 | 124.5941 | 1.1398 | 124.6307 | 80.4794 | -0.2243 | 124.5941 | 1.1398 | 80.4794 | 120.4514 | 124.6307 | -124.9603 | -124.9145
1381.6406 | 125.0381 | -61.5189 | 63.176 | -0.056229 | 0.014606 | 0.016609 | 0.0023583 | 0.063762 | 0.0024139 | 0.075007 | -60.3745 | 63.0569 | -61.8027 | -61.6699 | 58.8959 | 19.0384 | 2.2705 | 2.1606 | 63.121 | -61.7477 | -0.28381 | -0.11902 | 1.1444 | -0.15106 | -4.2801 | -0.22888 | -0.054931 | 1.4282 | 63.7894 | 63.6795 | 120.4147 | 124.5758 | 1.1444 | 124.6399 | 80.5573 | -0.22888 | 124.5758 | 1.1444 | 80.5573 | 120.4147 | 124.6399 | -124.9786 | -124.9237
1382.6406 | 124.9649 | -61.5005 | 63.1943 | -0.25459 | 0.013324 | 0.013619 | 0.0036401 | 0.062694 | 0.0022003 | 0.075007 | -60.3058 | 63.1027 | -61.7615 | -61.6608 | 58.9096 | 19.0521 | 2.3941 | 2.2018 | 63.1531 | -61.7844 | -0.26093 | -0.091553 | 1.1948 | -0.16022 | -4.2847 | -0.28381 | -0.041199 | 1.4557 | 63.8947 | 63.7024 | 120.4102 | 124.6033 | 1.1948 | 124.6536 | 80.5527 | -0.28381 | 124.6033 | 1.1948 | 80.5527 | 120.4102 | 124.6536 | -124.9557 | -124.9786
1383.6406 | 125.0153 | -61.5051 | 63.1943 | -0.033341 | 0.011828 | 0.014687 | 0.0038537 | 0.061199 | 0.0017731 | 0.074153 | -60.3241 | 63.0707 | -61.7615 | -61.6653 | 58.8821 | 19.0887 | 2.3209 | 2.1927 | 63.1256 | -61.7294 | -0.25635 | -0.1236 | 1.181 | -0.16022 | -4.3121 | -0.2243 | -0.068665 | 1.4374 | 63.826 | 63.6978 | 120.3873 | 124.5758 | 1.181 | 124.6307 | 80.5939 | -0.2243 | 124.5758 | 1.181 | 80.5939 | 120.3873 | 124.6307 | -124.9557 | -124.9237
1384.6406 | 124.9649 | -61.5051 | 63.1805 | -0.025711 | 0.01311 | 0.015968 | 0.00086295 | 0.065471 | -0.00014946 | 0.075648 | -60.3516 | 63.0615 | -61.7889 | -61.6745 | 58.7631 | 19.0796 | 2.298 | 2.1286 | 63.121 | -61.7569 | -0.28381 | -0.11902 | 1.1536 | -0.16937 | -4.4174 | -0.25177 | -0.059509 | 1.4374 | 63.8031 | 63.6337 | 120.2682 | 124.5667 | 1.1536 | 124.6262 | 80.5847 | -0.25177 | 124.5667 | 1.1536 | 80.5847 | 120.2682 | 124.6262 | -124.9695 | -124.9374
1385.6406 | 125.0015 | -61.528 | 63.1943 | -0.025711 | 0.011828 | 0.018532 | 0.0015039 | 0.061199 | 0.0028411 | 0.074794 | -60.3378 | 63.0753 | -61.7706 | -61.6653 | 58.8318 | 19.0704 | 2.3163 | 2.1652 | 63.1165 | -61.7523 | -0.24261 | -0.11902 | 1.1902 | -0.13733 | -4.3625 | -0.2243 | -0.07782 | 1.4328 | 63.8443 | 63.6932 | 120.3598 | 124.6033 | 1.1902 | 124.6445 | 80.5984 | -0.2243 | 124.6033 | 1.1902 | 80.5984 | 120.3598 | 124.6445 | -124.9649 | -124.9466
1386.6406 | 125.0107 | -61.496 | 63.1714 | 0.020065 | 0.012469 | 0.016182 | 0.0021447 | 0.061412 | 0.0034821 | 0.075435 | -60.3195 | 63.089 | -61.7523 | -61.6608 | 58.8089 | 19.0796 | 2.3163 | 2.1606 | 63.1256 | -61.7569 | -0.25635 | -0.082398 | 1.1765 | -0.16479 | -4.3625 | -0.26093 | -0.045777 | 1.4328 | 63.8123 | 63.6566 | 120.3049 | 124.585 | 1.1765 | 124.6216 | 80.5756 | -0.26093 | 124.585 | 1.1765 | 80.5756 | 120.3049 | 124.6216 | -124.9237 | -124.9283
1387.6406 | 124.9695 | -61.5234 | 63.2217 | -0.14778 | 0.014819 | 0.018959 | 0.0098351 | 0.063121 | 0.0011321 | 0.07223 | -60.2692 | 63.1943 | -61.7386 | -61.6608 | 58.7494 | 19.0201 | 2.4536 | 2.1286 | 63.1989 | -61.7661 | -0.21515 | -0.027466 | 1.2543 | -0.13733 | -4.4724 | -0.24262 | -0.022888 | 1.4694 | 63.977 | 63.652 | 120.2728 | 124.7177 | 1.2543 | 124.7223 | 80.5435 | -0.24262 | 124.7177 | 1.2543 | 80.5435 | 120.2728 | 124.7223 | -124.9603 | -124.9878
1388.6406 | 125.0198 | -61.4868 | 63.2172 | -0.13252 | 0.013537 | 0.016396 | 8.546e-06 | 0.062694 | 0.00091854 | 0.074366 | -60.2509 | 63.0798 | -61.734 | -61.6104 | 58.8272 | 19.0796 | 2.2568 | 2.2339 | 63.1485 | -61.6974 | -0.24719 | -0.13733 | 1.236 | -0.1236 | -4.39 | -0.21057 | -0.068664 | 1.4832 | 63.7436 | 63.7207 | 120.314 | 124.5666 | 1.236 | 124.6353 | 80.5664 | -0.21057 | 124.5666 | 1.236 | 80.5664 | 120.314 | 124.6353 | -124.9512 | -124.9146
1389.6406 | 125.0473 | -61.4594 | 63.1943 | -0.10201 | 0.012683 | 0.011269 | 0.0019311 | 0.060131 | 0.0011321 | 0.073939 | -60.228 | 63.1073 | -61.7752 | -61.5921 | 58.7906 | 19.0659 | 2.243 | 2.2018 | 63.1393 | -61.7157 | -0.31586 | -0.086975 | 1.2314 | -0.13275 | -4.4037 | -0.25635 | -0.054932 | 1.5472 | 63.7024 | 63.6612 | 120.2499 | 124.5667 | 1.2314 | 124.5987 | 80.5252 | -0.25635 | 124.5667 | 1.2314 | 80.5252 | 120.2499 | 124.5987 | -124.9695 | -124.91
1390.6406 | 124.9832 | -61.4822 | 63.2263 | -0.0028231 | 0.013751 | 0.014046 | 0.0023583 | 0.061626 | 0.00070494 | 0.075221 | -60.2692 | 63.0798 | -61.6974 | -61.6516 | 58.7265 | 19.0155 | 2.2293 | 2.1286 | 63.1531 | -61.734 | -0.21515 | -0.14648 | 1.2131 | -0.16937 | -4.4998 | -0.25177 | -0.073242 | 1.4282 | 63.7115 | 63.6108 | 120.2087 | 124.5621 | 1.2131 | 124.6353 | 80.4977 | -0.25177 | 124.5621 | 1.2131 | 80.4977 | 120.2087 | 124.6353 | -124.9237 | -124.9603
1391.6406 | 125.0381 | -61.4548 | 63.2309 | 0.0048064 | 0.014819 | 0.013191 | 0.0027855 | 0.061626 | 0.0030547 | 0.075007 | -60.2463 | 63.0981 | -61.7294 | -61.6562 | 58.7173 | 18.988 | 2.2018 | 2.092 | 63.1302 | -61.7203 | -0.27466 | -0.13275 | 1.2085 | -0.20142 | -4.5136 | -0.2655 | -0.10071 | 1.4832 | 63.6566 | 63.5468 | 120.1721 | 124.5529 | 1.2085 | 124.585 | 80.4428 | -0.2655 | 124.5529 | 1.2085 | 80.4428 | 120.1721 | 124.585 | -124.9603 | -124.9512
1392.6406 | 125.0565 | -61.4502 | 63.2126 | -0.62843 | 0.012897 | 0.015114 | 0.0038537 | 0.060985 | 0.0017731 | 0.074366 | -60.1959 | 63.1348 | -61.7157 | -61.5738 | 58.7402 | 19.0201 | 2.1561 | 2.1423 | 63.1622 | -61.6882 | -0.2655 | -0.077819 | 1.2543 | -0.1236 | -4.4724 | -0.23804 | -0.050354 | 1.5198 | 63.6063 | 63.5925 | 120.1904 | 124.585 | 1.2543 | 124.6124 | 80.4703 | -0.23804 | 124.585 | 1.2543 | 80.4703 | 120.1904 | 124.6124 | -124.9283 | -124.9008
1393.6406 | 125.0427 | -61.4594 | 63.2126 | -0.094376 | 0.011615 | 0.012337 | 0.0025719 | 0.061412 | 0.00070494 | 0.076289 | -60.173 | 63.0981 | -61.7157 | -61.6013 | 58.7082 | 19.0109 | 2.1149 | 2.1011 | 63.1622 | -61.702 | -0.25635 | -0.11444 | 1.2863 | -0.14191 | -4.5044 | -0.24261 | -0.050354 | 1.5427 | 63.5742 | 63.5605 | 120.1675 | 124.5575 | 1.2863 | 124.6216 | 80.4703 | -0.24261 | 124.5575 | 1.2863 | 80.4703 | 120.1675 | 124.6216 | -124.9283 | -124.9145
1394.6406 | 124.9649 | -61.4456 | 63.2538 | -0.24696 | 0.012897 | 0.018959 | 0.0047081 | 0.061199 | 0.0015595 | 0.075221 | -60.1593 | 63.1439 | -61.7065 | -61.6058 | 58.6624 | 18.9377 | 2.1881 | 2.0279 | 63.1805 | -61.7111 | -0.26093 | -0.10986 | 1.2863 | -0.16022 | -4.5914 | -0.2655 | -0.073242 | 1.5472 | 63.6337 | 63.4735 | 120.108 | 124.5895 | 1.2863 | 124.6262 | 80.3833 | -0.2655 | 124.5895 | 1.2863 | 80.3833 | 120.108 | 124.6262 | -124.9603 | -124.9649
1395.6406 | 124.9466 | -61.4502 | 63.2767 | -0.23933 | 0.013537 | 0.012978 | 0.0066309 | 0.060131 | 0.00049134 | 0.074366 | -60.1501 | 63.1577 | -61.6928 | -61.5875 | 58.6349 | 18.9102 | 2.179 | 1.9913 | 63.1897 | -61.6928 | -0.24262 | -0.11902 | 1.3 | -0.13733 | -4.6417 | -0.24262 | -0.086975 | 1.5427 | 63.6292 | 63.4415 | 120.0851 | 124.6078 | 1.3 | 124.6399 | 80.3604 | -0.24262 | 124.6078 | 1.3 | 80.3604 | 120.0851 | 124.6399 | -124.9695 | -124.9695
1396.6406 | 124.942 | -61.4502 | 63.2996 | -0.21645 | 0.013751 | 0.011482 | 0.0064171 | 0.062908 | 0.0022003 | 0.075221 | -60.1364 | 63.1668 | -61.6882 | -61.5921 | 58.6166 | 18.8828 | 2.1057 | 1.9272 | 63.2309 | -61.6882 | -0.23804 | -0.13275 | 1.3138 | -0.14191 | -4.6829 | -0.23804 | -0.068665 | 1.5518 | 63.5559 | 63.3774 | 120.0668 | 124.617 | 1.3138 | 124.6811 | 80.3329 | -0.23804 | 124.617 | 1.3138 | 80.3329 | 120.0668 | 124.6811 | -124.9878 | -124.9878
1397.6562 | 124.8734 | -61.4777 | 63.2584 | 0.065841 | 0.017383 | 0.021095 | 0.012612 | 0.065471 | 0.0013457 | 0.073512 | -60.1639 | 63.2629 | -61.7432 | -61.702 | 58.4793 | 18.7363 | 2.1103 | 1.7624 | 63.2309 | -61.7661 | -0.2655 | 0.004577 | 1.3138 | -0.2243 | -4.7791 | -0.28839 | -0.027466 | 1.5793 | 63.588 | 63.2401 | 119.957 | 124.7406 | 1.3138 | 124.7086 | 80.2139 | -0.28839 | 124.7406 | 1.3138 | 80.2139 | 119.957 | 124.7086 | -125.0015 | -125.0244
1398.6406 | 125.0244 | -61.4273 | 63.2538 | -0.22408 | 0.014178 | 0.012123 | 0.0036401 | 0.064403 | -0.00057686 | 0.075221 | -60.0952 | 63.176 | -61.6928 | -61.5509 | 58.6029 | 18.8736 | 2.037 | 1.9592 | 63.2309 | -61.6653 | -0.2655 | -0.07782 | 1.3321 | -0.1236 | -4.6509 | -0.23804 | -0.022888 | 1.5976 | 63.4644 | 63.3865 | 120.0302 | 124.6033 | 1.3321 | 124.6582 | 80.3009 | -0.23804 | 124.6033 | 1.3321 | 80.3009 | 120.0302 | 124.6582 | -124.9466 | -124.9191
1399.6406 | 124.9054 | -61.4594 | 63.2812 | -0.2317 | 0.01546 | 0.014473 | 0.0042809 | 0.06419 | 0.0019867 | 0.075221 | -60.1135 | 63.2355 | -61.6928 | -61.6287 | 58.5205 | 18.7454 | 2.1057 | 1.8082 | 63.2492 | -61.7065 | -0.23346 | -0.045776 | 1.3458 | -0.16937 | -4.7607 | -0.24719 | -0.032043 | 1.5793 | 63.5651 | 63.2675 | 119.9799 | 124.6948 | 1.3458 | 124.7086 | 80.2048 | -0.24719 | 124.6948 | 1.3458 | 80.2048 | 119.9799 | 124.7086 | -124.9741 | -124.9878
1400.6406 | 124.9557 | -61.4685 | 63.295 | -0.32326 | 0.013537 | 0.015328 | 0.0062035 | 0.065471 | 0.00091854 | 0.076075 | -60.1089 | 63.2355 | -61.6882 | -61.615 | 58.4839 | 18.6859 | 2.0599 | 1.7624 | 63.2446 | -61.6928 | -0.21973 | -0.059509 | 1.3596 | -0.14648 | -4.8111 | -0.2243 | -0.050354 | 1.5793 | 63.5284 | 63.2309 | 119.9524 | 124.704 | 1.3596 | 124.7131 | 80.1544 | -0.2243 | 124.704 | 1.3596 | 80.1544 | 119.9524 | 124.7131 | -124.9832 | -124.9878
1401.6406 | 124.91 | -61.4365 | 63.3179 | -0.079117 | 0.017169 | 0.017464 | 0.0064171 | 0.060985 | 0.00027774 | 0.07693 | -60.0952 | 63.2767 | -61.6974 | -61.6379 | 58.4427 | 18.6722 | 2.0737 | 1.7075 | 63.2584 | -61.7249 | -0.26093 | -0.041199 | 1.3412 | -0.20142 | -4.8752 | -0.28839 | -0.059509 | 1.6022 | 63.5101 | 63.1439 | 119.8791 | 124.7131 | 1.3412 | 124.6948 | 80.1086 | -0.28839 | 124.7131 | 1.3412 | 80.1086 | 119.8791 | 124.6948 | -125.0153 | -125.0427
1402.6406 | 124.9512 | -61.4639 | 63.295 | -0.17067 | 0.01781 | 0.017464 | 0.010903 | 0.06483 | -0.00036306 | 0.07458 | -60.0357 | 63.2858 | -61.6699 | -61.5784 | 58.4656 | 18.6493 | 1.7578 | 1.5015 | 63.2217 | -61.7294 | -0.20599 | -0.009155 | 1.4282 | -0.11444 | -4.8294 | -0.2655 | -0.073242 | 1.6342 | 63.2217 | 62.9654 | 119.9295 | 124.7498 | 1.4282 | 124.6857 | 80.1132 | -0.2655 | 124.7498 | 1.4282 | 80.1132 | 119.9295 | 124.6857 | -124.9649 | -125.0244
1403.6406 | 124.9283 | -61.4319 | 63.327 | -0.27748 | 0.014819 | 0.012337 | 0.0066309 | 0.063976 | 0.0011321 | 0.075007 | -60.0952 | 63.2904 | -61.6974 | -61.647 | 58.4198 | 18.6035 | 1.9592 | 1.6205 | 63.3041 | -61.6791 | -0.2655 | -0.036621 | 1.3367 | -0.21515 | -4.9072 | -0.24719 | -0.022888 | 1.6022 | 63.3911 | 63.0524 | 119.8517 | 124.7223 | 1.3367 | 124.736 | 80.0354 | -0.24719 | 124.7223 | 1.3367 | 80.0354 | 119.8517 | 124.736 | -125.0244 | -125.0061
1404.6406 | 124.9603 | -61.409 | 63.3453 | -0.20882 | 0.013965 | 0.015541 | 0.0053491 | 0.065685 | 0.00027774 | 0.076075 | -60.0952 | 63.2675 | -61.6699 | -61.6516 | 58.3832 | 18.5806 | 1.9363 | 1.6067 | 63.2904 | -61.7065 | -0.26093 | -0.07782 | 1.3138 | -0.24261 | -4.9622 | -0.29755 | -0.054932 | 1.5747 | 63.3453 | 63.0157 | 119.7922 | 124.6765 | 1.3138 | 124.6994 | 79.9896 | -0.29755 | 124.6765 | 1.3138 | 79.9896 | 119.7922 | 124.6994 | -125.0153 | -125.0519
1405.6406 | 124.9603 | -61.3998 | 63.2858 | -0.23933 | 0.014606 | 0.017891 | 0.0055627 | 0.063121 | -0.00079046 | 0.077571 | -60.022 | 63.2172 | -61.6653 | -61.5829 | 58.4152 | 18.6172 | 1.8173 | 1.6434 | 63.2584 | -61.6562 | -0.2655 | -0.068665 | 1.3779 | -0.18311 | -4.8706 | -0.25635 | -0.027466 | 1.6434 | 63.2172 | 63.0432 | 119.8151 | 124.617 | 1.3779 | 124.6582 | 80.0171 | -0.25635 | 124.617 | 1.3779 | 80.0171 | 119.8151 | 124.6582 | -124.9512 | -124.942
1406.6406 | 124.8962 | -61.4273 | 63.3316 | -0.1783 | 0.017596 | 0.017037 | 0.0066309 | 0.063549 | 0.0015595 | 0.076289 | -60.0769 | 63.295 | -61.6745 | -61.4456 | 58.2001 | 18.3609 | 1.8494 | 1.5335 | 63.2904 | -61.6745 | -0.24719 | -0.036621 | 1.3504 | -0.018311 | -5.1315 | -0.24719 | -0.041199 | 1.5976 | 63.2767 | 62.9608 | 119.6274 | 124.7223 | 1.3504 | 124.7177 | 79.7882 | -0.24719 | 124.7223 | 1.3504 | 79.7882 | 119.6274 | 124.7177 | -125.0061 | -125.0061
1407.6406 | 124.9191 | -61.3998 | 63.3408 | -0.21645 | 0.014819 | 0.017464 | 0.0079125 | 0.06419 | 0.0013457 | 0.075435 | -60.0266 | 63.295 | -61.6608 | -61.615 | 58.3054 | 18.5806 | 1.7899 | 1.4923 | 63.3041 | -61.6837 | -0.26093 | -0.045776 | 1.3733 | -0.21515 | -5.0354 | -0.28381 | -0.036621 | 1.6342 | 63.1897 | 62.8922 | 119.7052 | 124.6948 | 1.3733 | 124.704 | 79.9805 | -0.28381 | 124.6948 | 1.3733 | 79.9805 | 119.7052 | 124.704 | -125.0015 | -125.0244
1408.6406 | 124.9329 | -61.4182 | 63.3224 | -0.29274 | 0.017169 | 0.012978 | 0.0091943 | 0.064403 | -0.0014313 | 0.077144 | -60.0266 | 63.3041 | -61.6562 | -61.6013 | 58.2825 | 18.4708 | 1.8036 | 1.4694 | 63.2996 | -61.6837 | -0.23804 | -0.018311 | 1.3916 | -0.1831 | -5.04 | -0.2655 | -0.022888 | 1.6296 | 63.2217 | 62.8876 | 119.7006 | 124.7223 | 1.3916 | 124.7177 | 79.8889 | -0.2655 | 124.7223 | 1.3916 | 79.8889 | 119.7006 | 124.7177 | -124.9786 | -125.0061
1409.6406 | 124.9329 | -61.4227 | 63.3362 | -0.16304 | 0.016528 | 0.017677 | 0.0074853 | 0.065258 | 0.00049134 | 0.074366 | -59.9899 | 63.2996 | -61.6379 | -61.6013 | 58.2825 | 18.457 | 1.7349 | 1.4328 | 63.3041 | -61.6928 | -0.21515 | -0.036621 | 1.4328 | -0.17853 | -5.0537 | -0.27008 | -0.032044 | 1.6479 | 63.1577 | 62.8555 | 119.7052 | 124.7223 | 1.4328 | 124.7269 | 79.8798 | -0.27008 | 124.7223 | 1.4328 | 79.8798 | 119.7052 | 124.7269 | -124.9741 | -125.029
1410.6406 | 124.9557 | -61.3953 | 63.3453 | -0.23933 | 0.016742 | 0.017891 | 0.0079125 | 0.066539 | 0.0017731 | 0.077357 | -59.9854 | 63.3362 | -61.6608 | -61.5875 | 58.2458 | 18.4158 | 1.6663 | 1.4282 | 63.3133 | -61.6653 | -0.2655 | -0.009155 | 1.4099 | -0.19226 | -5.0995 | -0.27008 | -0.032044 | 1.6754 | 63.0615 | 62.8235 | 119.6411 | 124.7314 | 1.4099 | 124.7086 | 79.8111 | -0.27008 | 124.7314 | 1.4099 | 79.8111 | 119.6411 | 124.7086 | -125.0061 | -125.0107
1411.6406 | 124.9191 | -61.3815 | 63.3636 | -0.28511 | 0.014819 | 0.017891 | 0.0074853 | 0.06483 | 0.00049134 | 0.077144 | -59.9899 | 63.3499 | -61.6425 | -61.5921 | 58.223 | 18.2648 | 1.5152 | 1.3321 | 63.3362 | -61.6791 | -0.26093 | -0.013732 | 1.3916 | -0.21057 | -5.1407 | -0.29755 | -0.027465 | 1.6525 | 62.8967 | 62.7136 | 119.6045 | 124.7314 | 1.3916 | 124.7177 | 79.6463 | -0.29755 | 124.7314 | 1.3916 | 79.6463 | 119.6045 | 124.7177 | -125.0061 | -125.0427
1412.6406 | 124.9008 | -61.3861 | 63.3636 | 0.020065 | 0.01781 | 0.019386 | 0.0089807 | 0.068248 | 0.00091854 | 0.076075 | -59.9167 | 63.3636 | -61.6379 | -61.6104 | 58.1818 | 18.1686 | 1.355 | 1.236 | 63.3453 | -61.6608 | -0.25177 | 0 | 1.4694 | -0.22431 | -5.1819 | -0.27466 | -0.01831 | 1.7212 | 62.7411 | 62.6221 | 119.5679 | 124.7498 | 1.4694 | 124.7314 | 79.5547 | -0.27466 | 124.7498 | 1.4694 | 79.5547 | 119.5679 | 124.7314 | -125.0015 | -125.0244
1413.6406 | 124.9283 | -61.3495 | 63.3774 | -0.22408 | 0.017383 | 0.018532 | 0.0096215 | 0.066753 | -0.0014313 | 0.076075 | -59.8892 | 63.3728 | -61.5921 | -61.5463 | 58.1909 | 18.1274 | 1.2863 | 1.2543 | 63.382 | -61.615 | -0.24261 | -0.004577 | 1.4603 | -0.19684 | -5.1865 | -0.2655 | 0.004578 | 1.7029 | 62.6358 | 62.6038 | 119.5404 | 124.7223 | 1.4603 | 124.7314 | 79.4769 | -0.2655 | 124.7223 | 1.4603 | 79.4769 | 119.5404 | 124.7314 | -124.9695 | -124.9924
1414.6406 | 124.9512 | -61.3403 | 63.382 | -0.13252 | 0.017383 | 0.017037 | 0.0070581 | 0.066112 | 0.00027774 | 0.076716 | -59.8801 | 63.3774 | -61.5784 | -61.5143 | 58.1955 | 18.0725 | 1.2497 | 1.2405 | 63.4003 | -61.5967 | -0.23804 | -0.004578 | 1.4603 | -0.17395 | -5.1865 | -0.25635 | 0.018311 | 1.6983 | 62.59 | 62.5809 | 119.5358 | 124.7177 | 1.4603 | 124.7406 | 79.4128 | -0.25635 | 124.7177 | 1.4603 | 79.4128 | 119.5358 | 124.7406 | -124.9603 | -124.9786
1415.6406 | 124.9512 | -61.3358 | 63.3957 | -0.086746 | 0.017596 | 0.018959 | 0.0083397 | 0.073375 | 6.414e-05 | 0.077144 | -59.8114 | 63.414 | -61.5646 | -61.4182 | 58.1406 | 18.0176 | 1.1444 | 1.1948 | 63.4003 | -61.615 | -0.22888 | 0.01831 | 1.5244 | -0.082398 | -5.2551 | -0.27924 | 0.004578 | 1.7532 | 62.4802 | 62.5305 | 119.4763 | 124.7498 | 1.5244 | 124.736 | 79.3533 | -0.27924 | 124.7498 | 1.5244 | 79.3533 | 119.4763 | 124.736 | -124.9603 | -125.0107
1416.6406 | 124.9512 | -61.322 | 63.4094 | -0.094376 | 0.017169 | 0.01725 | 0.0066309 | 0.066326 | 0.0011321 | 0.077784 | -59.6924 | 63.4094 | -61.5555 | -61.4731 | 58.1314 | 17.981 | 1.062 | 1.1627 | 63.4094 | -61.6058 | -0.23346 | 0 | 1.6296 | -0.15106 | -5.278 | -0.28381 | 0 | 1.8631 | 62.384 | 62.4847 | 119.4534 | 124.7314 | 1.6296 | 124.7314 | 79.303 | -0.28381 | 124.7314 | 1.6296 | 79.303 | 119.4534 | 124.7314 | -124.9649 | -125.0153
1417.6406 | 125.0198 | -61.3174 | 63.3362 | 0.18791 | 0.016101 | 0.017677 | 0.0049219 | 0.067608 | 0.00070494 | 0.077998 | -59.7794 | 63.3224 | -61.5601 | -61.4777 | 58.1726 | 17.9489 | 0.84228 | 1.0986 | 63.3591 | -61.5921 | -0.24262 | -0.013733 | 1.5381 | -0.16022 | -5.1636 | -0.27466 | 0.022888 | 1.7807 | 62.1597 | 62.4161 | 119.4901 | 124.6399 | 1.5381 | 124.6765 | 79.2664 | -0.27466 | 124.6399 | 1.5381 | 79.2664 | 119.4901 | 124.6765 | -124.8962 | -124.9283
1418.6406 | 124.9329 | -61.3037 | 63.3774 | -0.20119 | 0.018878 | 0.019386 | 0.0083397 | 0.067394 | 0.00091854 | 0.077998 | -59.761 | 63.4186 | -61.5463 | -61.4639 | 58.1177 | 17.8116 | 0.96588 | 1.0757 | 63.4415 | -61.5921 | -0.24262 | 0.041199 | 1.5427 | -0.16022 | -5.2597 | -0.28839 | 0.064087 | 1.7853 | 62.2696 | 62.3795 | 119.4214 | 124.7223 | 1.5427 | 124.7452 | 79.1153 | -0.28839 | 124.7223 | 1.5427 | 79.1153 | 119.4214 | 124.7452 | -124.9237 | -124.9695
1419.6406 | 124.9512 | -61.2946 | 63.4369 | -0.12489 | 0.019946 | 0.01725 | 0.0083397 | 0.066967 | 0.00027774 | 0.076289 | -59.7794 | 63.4415 | -61.5463 | -61.4731 | 58.0856 | 17.7704 | 0.86975 | 1.0025 | 63.4506 | -61.6058 | -0.25177 | 0.004577 | 1.5152 | -0.17853 | -5.3513 | -0.31128 | 0.013733 | 1.767 | 62.1643 | 62.2971 | 119.3802 | 124.736 | 1.5152 | 124.7452 | 79.0649 | -0.31128 | 124.736 | 1.5152 | 79.0649 | 119.3802 | 124.7452 | -124.9832 | -125.0427
1420.6406 | 124.9374 | -61.2854 | 63.414 | -0.079117 | 0.019519 | 0.0243 | 0.010476 | 0.06718 | 0.0017731 | 0.07693 | -59.9075 | 63.3957 | -61.5555 | -61.4548 | 58.0444 | 17.6788 | 0.79193 | 0.94299 | 63.4552 | -61.5692 | -0.27008 | -0.01831 | 1.3779 | -0.16937 | -5.3696 | -0.28381 | 0.041199 | 1.6479 | 62.0773 | 62.2284 | 119.3298 | 124.6811 | 1.3779 | 124.7406 | 78.9642 | -0.28381 | 124.6811 | 1.3779 | 78.9642 | 119.3298 | 124.7406 | -124.9695 | -124.9832
1421.6406 | 124.9283 | -61.2671 | 63.4644 | -0.15541 | 0.022723 | 0.020241 | 0.0059899 | 0.068889 | 0.0013457 | 0.077998 | -59.8755 | 63.4094 | -61.5692 | -61.4548 | 58.0215 | 17.5964 | 0.70496 | 0.91095 | 63.446 | -61.5784 | -0.30212 | -0.054931 | 1.3916 | -0.18768 | -5.4428 | -0.31128 | -0.01831 | 1.6937 | 61.972 | 62.178 | 119.2886 | 124.6765 | 1.3916 | 124.7131 | 78.8635 | -0.31128 | 124.6765 | 1.3916 | 78.8635 | 119.2886 | 124.7131 | -125.0336 | -125.0427
1422.6406 | 125.0107 | -61.2442 | 63.3728 | 0.17265 | 0.015246 | 0.018105 | 0.0036401 | 0.066539 | 0.0013457 | 0.077144 | -59.7015 | 63.3224 | -61.5372 | -61.4365 | 58.0215 | 17.5919 | 0.48981 | 0.88806 | 63.3911 | -61.5417 | -0.29297 | -0.050354 | 1.5427 | -0.19226 | -5.3513 | -0.29755 | 0.01831 | 1.8356 | 61.734 | 62.1323 | 119.2657 | 124.5667 | 1.5427 | 124.6353 | 78.8361 | -0.29755 | 124.5667 | 1.5427 | 78.8361 | 119.2657 | 124.6353 | -124.91 | -124.9146
1423.6406 | 124.8962 | -61.29 | 63.4369 | -0.025711 | 0.015887 | 0.020454 | 0.011544 | 0.066753 | 0.0034821 | 0.076716 | -59.6832 | 63.4644 | -61.5189 | -61.4777 | 57.9391 | 17.4683 | 0.58136 | 0.74616 | 63.4506 | -61.5784 | -0.22888 | 0.027465 | 1.6067 | -0.18768 | -5.4977 | -0.28839 | 0.013733 | 1.8356 | 61.8713 | 62.0361 | 119.2291 | 124.7543 | 1.6067 | 124.7406 | 78.7582 | -0.28839 | 124.7543 | 1.6067 | 78.7582 | 119.2291 | 124.7406 | -124.9557 | -125.0153
1424.6406 | 124.8962 | -61.2762 | 63.446 | -0.025711 | 0.019732 | 0.022163 | 0.01069 | 0.068889 | 0.0026275 | 0.079066 | -59.6786 | 63.4644 | -61.5143 | -61.4594 | 57.8888 | 17.3813 | 0.54474 | 0.72327 | 63.4552 | -61.5921 | -0.23804 | 0.01831 | 1.5976 | -0.18311 | -5.5573 | -0.31586 | 0.009155 | 1.8356 | 61.821 | 61.9995 | 119.165 | 124.7406 | 1.5976 | 124.7314 | 78.6575 | -0.31586 | 124.7406 | 1.5976 | 78.6575 | 119.165 | 124.7314 | -124.9603 | -125.0381
1425.6406 | 124.9466 | -61.2671 | 63.4689 | 0.61516 | 0.019732 | 0.0196 | 0.0096215 | 0.066539 | 0.0017731 | 0.078212 | -59.5917 | 63.4689 | -61.5097 | -61.4227 | 57.8934 | 17.3721 | 0.44861 | 0.737 | 63.4735 | -61.5372 | -0.24261 | 0 | 1.6754 | -0.15564 | -5.5756 | -0.27008 | 0.004578 | 1.918 | 61.7157 | 62.0041 | 119.1605 | 124.736 | 1.6754 | 124.7406 | 78.6392 | -0.27008 | 124.736 | 1.6754 | 78.6392 | 119.1605 | 124.7406 | -124.9786 | -125.0061
1426.6406 | 124.9512 | -61.235 | 63.4552 | 0.47783 | 0.017596 | 0.016823 | 0.0081261 | 0.070171 | 0.0013457 | 0.078212 | -59.5917 | 63.4827 | -61.496 | -61.4227 | 57.8751 | 17.3218 | 0.39368 | 0.6958 | 63.4781 | -61.5555 | -0.26093 | 0.027466 | 1.6434 | -0.18768 | -5.5801 | -0.32044 | 0.022888 | 1.9043 | 61.6287 | 61.9308 | 119.1101 | 124.7177 | 1.6434 | 124.7131 | 78.5568 | -0.32044 | 124.7177 | 1.6434 | 78.5568 | 119.1101 | 124.7131 | -124.9512 | -125.0107
1427.6406 | 124.9695 | -61.2579 | 63.3774 | 0.12688 | 0.015887 | 0.017891 | 0.0040673 | 0.071025 | 6.414e-05 | 0.078853 | -59.6283 | 63.3682 | -61.5097 | -61.4227 | 57.8705 | 17.3172 | 0.20142 | 0.68665 | 63.4186 | -61.5097 | -0.25177 | -0.009155 | 1.6296 | -0.16479 | -5.5069 | -0.25177 | 0.041199 | 1.8814 | 61.4594 | 61.9446 | 119.1284 | 124.6262 | 1.6296 | 124.6765 | 78.5751 | -0.25177 | 124.6262 | 1.6296 | 78.5751 | 119.1284 | 124.6765 | -124.8871 | -124.8871
1428.6406 | 124.9649 | -61.2076 | 63.4506 | 0.14976 | 0.015246 | 0.016823 | 0.0015039 | 0.06483 | 0.0019867 | 0.077998 | -59.6237 | 63.3591 | -61.4914 | -61.4365 | 57.7927 | 17.2119 | 0.20599 | 0.65918 | 63.4415 | -61.5143 | -0.28381 | -0.091553 | 1.5839 | -0.22888 | -5.658 | -0.3067 | -0.009156 | 1.8677 | 61.4136 | 61.8668 | 119.0002 | 124.5667 | 1.5839 | 124.649 | 78.4195 | -0.3067 | 124.5667 | 1.5839 | 78.4195 | 119.0002 | 124.649 | -124.942 | -124.9649
1429.6406 | 124.9008 | -61.2305 | 63.5193 | 0.035324 | 0.016955 | 0.020882 | 0.010903 | 0.063549 | 0.0017731 | 0.077784 | -59.61 | 63.4964 | -61.4777 | -61.4777 | 57.7148 | 17.0609 | 0.31128 | 0.49896 | 63.4735 | -61.5509 | -0.24719 | -0.022888 | 1.6205 | -0.24719 | -5.8044 | -0.32043 | -0.045776 | 1.8677 | 61.5417 | 61.7294 | 118.9453 | 124.7269 | 1.6205 | 124.704 | 78.2913 | -0.32043 | 124.7269 | 1.6205 | 78.2913 | 118.9453 | 124.704 | -124.9969 | -125.0702
1430.6406 | 124.8779 | -61.2534 | 63.5193 | 0.020065 | 0.018878 | 0.021736 | 0.011117 | 0.066967 | 0.0015595 | 0.079066 | -59.6146 | 63.5101 | -61.4822 | -61.4456 | 57.6782 | 17.0197 | 0.24719 | 0.45319 | 63.5239 | -61.5417 | -0.22888 | -0.009155 | 1.6388 | -0.19226 | -5.8411 | -0.28839 | 0.004578 | 1.8677 | 61.5005 | 61.7065 | 118.9316 | 124.7635 | 1.6388 | 124.7772 | 78.273 | -0.28839 | 124.7635 | 1.6388 | 78.273 | 118.9316 | 124.7772 | -125.0015 | -125.061
1431.6406 | 124.8779 | -61.2076 | 63.5056 | 0.0048064 | 0.018023 | 0.023232 | 0.0087671 | 0.068676 | 0.0013457 | 0.077784 | -59.5734 | 63.5147 | -61.4731 | -61.4502 | 57.6645 | 16.9647 | 0.17395 | 0.38452 | 63.5239 | -61.5051 | -0.2655 | 0.009155 | 1.6342 | -0.24261 | -5.8411 | -0.29755 | 0.018311 | 1.8997 | 61.3815 | 61.5921 | 118.8721 | 124.7223 | 1.6342 | 124.7314 | 78.1723 | -0.29755 | 124.7223 | 1.6342 | 78.1723 | 118.8721 | 124.7314 | -124.9786 | -125.0107
1432.6406 | 124.9008 | -61.235 | 63.4964 | 0.6533 | 0.019946 | 0.020027 | 0.0085535 | 0.065471 | 0.0034821 | 0.076289 | -59.5551 | 63.5376 | -61.4777 | -61.4594 | 57.6233 | 16.8915 | 0.073242 | 0.3067 | 63.5056 | -61.5463 | -0.24262 | 0.041199 | 1.68 | -0.22431 | -5.8731 | -0.31128 | 0.009155 | 1.9226 | 61.3083 | 61.5417 | 118.8583 | 124.7726 | 1.68 | 124.7406 | 78.1265 | -0.31128 | 124.7726 | 1.68 | 78.1265 | 118.8583 | 124.7406 | -124.9741 | -125.0427
1433.6562 | 124.9969 | -61.1755 | 63.5056 | 0.10399 | 0.017596 | 0.018105 | 0.0010767 | 0.066539 | 0.0030547 | 0.079493 | -59.5779 | 63.3911 | -61.4502 | -61.3907 | 57.6691 | 16.9098 | -0.054932 | 0.36621 | 63.4872 | -61.4456 | -0.27466 | -0.11444 | 1.5976 | -0.21515 | -5.8365 | -0.27008 | -0.01831 | 1.8723 | 61.1206 | 61.5417 | 118.8446 | 124.5666 | 1.5976 | 124.6628 | 78.0853 | -0.27008 | 124.5666 | 1.5976 | 78.0853 | 118.8446 | 124.6628 | -124.9557 | -124.9512
1434.6406 | 124.8734 | -61.203 | 63.5193 | 0.0811 | 0.024219 | 0.023872 | 0.0098351 | 0.064403 | 0.0034821 | 0.078212 | -59.8801 | 63.4552 | -61.4639 | -61.4639 | 57.5363 | 16.8182 | -0.036621 | 0.16937 | 63.5056 | -61.528 | -0.26093 | -0.064087 | 1.3229 | -0.26093 | -5.983 | -0.32501 | -0.013733 | 1.5839 | 61.1664 | 61.3724 | 118.7393 | 124.6582 | 1.3229 | 124.7086 | 78.0212 | -0.32501 | 124.6582 | 1.3229 | 78.0212 | 118.7393 | 124.7086 | -124.9832 | -125.0473
1435.6406 | 124.8917 | -61.1984 | 63.5513 | 0.13451 | 0.018451 | 0.021095 | 0.0089807 | 0.064403 | 0.0022003 | 0.07928 | -59.5505 | 63.5193 | -61.4319 | -61.4456 | 57.5958 | 16.7908 | -0.15564 | 0.17395 | 63.5468 | -61.4822 | -0.23346 | -0.032044 | 1.6479 | -0.24719 | -5.9555 | -0.28381 | -0.004578 | 1.8814 | 61.0428 | 61.3724 | 118.7943 | 124.7177 | 1.6479 | 124.7452 | 77.9892 | -0.28381 | 124.7177 | 1.6479 | 77.9892 | 118.7943 | 124.7452 | -124.9832 | -125.0336
1436.6406 | 124.942 | -61.1984 | 63.5468 | 0.15739 | 0.019092 | 0.022591 | 0.0076989 | 0.069744 | 0.0045501 | 0.079921 | -59.5139 | 63.5239 | -61.4685 | -61.4136 | 57.4951 | 16.6809 | -0.18768 | 0.10986 | 63.5513 | -61.5005 | -0.27008 | -0.022888 | 1.6846 | -0.21515 | -6.0516 | -0.30212 | 0.004578 | 1.9547 | 61.0107 | 61.3083 | 118.6935 | 124.7223 | 1.6846 | 124.7498 | 77.8793 | -0.30212 | 124.7223 | 1.6846 | 77.8793 | 118.6935 | 124.7498 | -125.0153 | -125.0473
1437.6406 | 124.9695 | -61.1481 | 63.5101 | 0.027695 | 0.013751 | 0.017677 | 0.00022215 | 0.065685 | 0.0036957 | 0.079921 | -59.4864 | 63.446 | -61.4227 | -61.377 | 57.4951 | 16.6718 | -0.36163 | 0.10986 | 63.4964 | -61.4227 | -0.27466 | -0.064087 | 1.6617 | -0.22888 | -6.015 | -0.27466 | -0.013733 | 1.9363 | 60.7864 | 61.2579 | 118.6432 | 124.5941 | 1.6617 | 124.6445 | 77.8198 | -0.27466 | 124.5941 | 1.6617 | 77.8198 | 118.6432 | 124.6445 | -124.9329 | -124.9329
1438.6406 | 125.0336 | -61.1206 | 63.533 | -0.063858 | 0.013751 | 0.014687 | 0.0012903 | 0.063549 | 0.0015595 | 0.079066 | -59.4315 | 63.4598 | -61.3678 | -61.2854 | 57.5455 | 16.6992 | -0.42572 | 0.14191 | 63.5193 | -61.3998 | -0.24719 | -0.073242 | 1.6891 | -0.1648 | -5.9875 | -0.27924 | -0.013733 | 1.9363 | 60.6949 | 61.2625 | 118.6661 | 124.5804 | 1.6891 | 124.6399 | 77.8198 | -0.27924 | 124.5804 | 1.6891 | 77.8198 | 118.6661 | 124.6399 | -124.9008 | -124.9329
1439.6406 | 124.9146 | -61.1664 | 63.5605 | 0.18028 | 0.015246 | 0.0149 | 0.014108 | 0.064617 | 0.0051911 | 0.077144 | -59.4543 | 63.5468 | -61.4136 | -61.4044 | 57.3898 | 16.4932 | -0.39368 | -0.082397 | 63.5422 | -61.4777 | -0.24719 | -0.013733 | 1.712 | -0.23804 | -6.1707 | -0.31128 | -0.018311 | 1.9592 | 60.7727 | 61.084 | 118.5562 | 124.7131 | 1.712 | 124.7086 | 77.6596 | -0.31128 | 124.7131 | 1.712 | 77.6596 | 118.5562 | 124.7086 | -124.9741 | -125.0381
1440.6406 | 124.8688 | -61.1389 | 63.5788 | 0.15739 | 0.016528 | 0.022804 | 0.011117 | 0.065258 | 0.0019867 | 0.07693 | -59.4177 | 63.5925 | -61.409 | -61.3724 | 57.3303 | 16.3971 | -0.42572 | -0.16479 | 63.5742 | -61.4548 | -0.27008 | 0.013733 | 1.7212 | -0.23346 | -6.2485 | -0.31586 | -0.004577 | 1.9913 | 60.7132 | 60.9741 | 118.4692 | 124.7314 | 1.7212 | 124.7131 | 77.536 | -0.31586 | 124.7314 | 1.7212 | 77.536 | 118.4692 | 124.7131 | -124.9878 | -125.0336
1441.6406 | 124.8871 | -61.1298 | 63.5696 | 0.19554 | 0.019946 | 0.019814 | 0.010476 | 0.065685 | 0.0026275 | 0.077357 | -59.4177 | 63.5742 | -61.3861 | -61.3678 | 57.312 | 16.3467 | -0.52185 | -0.19684 | 63.5788 | -61.4456 | -0.25635 | 0.004578 | 1.712 | -0.23804 | -6.2576 | -0.31586 | 0.009155 | 1.9684 | 60.6079 | 60.9329 | 118.4418 | 124.704 | 1.712 | 124.7086 | 77.4765 | -0.31586 | 124.704 | 1.712 | 77.4765 | 118.4418 | 124.7086 | -124.9557 | -125.0153
1442.6406 | 124.9741 | -61.0931 | 63.5239 | 0.17265 | 0.016742 | 0.018959 | 0.0012903 | 0.06419 | 0.0028411 | 0.080134 | -59.3628 | 63.4872 | -61.3541 | -61.3174 | 57.3807 | 16.3788 | -0.69122 | -0.16022 | 63.533 | -61.377 | -0.26093 | -0.036621 | 1.7303 | -0.2243 | -6.1432 | -0.28381 | 0.009155 | 1.9913 | 60.4019 | 60.9329 | 118.4738 | 124.5804 | 1.7303 | 124.6262 | 77.4719 | -0.28381 | 124.5804 | 1.7303 | 77.4719 | 118.4738 | 124.6262 | -124.8779 | -124.9008
1443.6562 | 124.9146 | -61.1069 | 63.6383 | -0.25459 | 0.016955 | 0.019173 | 0.0072717 | 0.063335 | 0.0032683 | 0.078212 | -59.3353 | 63.533 | -61.3495 | -61.3083 | 57.3074 | 16.2689 | -0.5722 | -0.22888 | 63.6017 | -61.4044 | -0.24261 | -0.10529 | 1.7715 | -0.20142 | -6.3309 | -0.29755 | -0.036621 | 2.0142 | 60.5347 | 60.878 | 118.4143 | 124.6399 | 1.7715 | 124.7086 | 77.3758 | -0.29755 | 124.6399 | 1.7715 | 77.3758 | 118.4143 | 124.7086 | -124.9878 | -125.0427
1444.6406 | 124.9146 | -61.1298 | 63.5788 | 0.18028 | 0.020587 | 0.021309 | 0.0094079 | 0.066539 | 0.0045501 | 0.079066 | -59.3536 | 63.5559 | -61.3495 | -61.3312 | 57.225 | 16.1865 | -0.75531 | -0.3479 | 63.5834 | -61.4273 | -0.21973 | -0.022888 | 1.7761 | -0.20142 | -6.3538 | -0.29755 | 0.004578 | 1.9958 | 60.3745 | 60.7819 | 118.3548 | 124.6857 | 1.7761 | 124.7131 | 77.3163 | -0.29755 | 124.6857 | 1.7761 | 77.3163 | 118.3548 | 124.7131 | -124.9283 | -125.0061
1445.6406 | 124.942 | -61.0931 | 63.5925 | 0.10399 | 0.018664 | 0.02195 | 0.011544 | 0.065899 | 0.0034821 | 0.077998 | -59.317 | 63.6017 | -61.3953 | -61.3266 | 57.1793 | 16.1041 | -0.8194 | -0.3891 | 63.5971 | -61.4136 | -0.30212 | 0.009156 | 1.7761 | -0.23346 | -6.4133 | -0.32043 | 0.004578 | 2.0782 | 60.2737 | 60.704 | 118.2724 | 124.6948 | 1.7761 | 124.6902 | 77.1973 | -0.32043 | 124.6948 | 1.7761 | 77.1973 | 118.2724 | 124.6902 | -124.9878 | -125.0061
1446.6406 | 124.8779 | -61.1069 | 63.6017 | 0.08873 | 0.019946 | 0.021736 | 0.0070581 | 0.063976 | 0.0028411 | 0.07928 | -59.3491 | 63.6108 | -61.3861 | -61.3632 | 57.2296 | 16.1133 | -0.8606 | -0.44403 | 63.6383 | -61.3907 | -0.27923 | 0.009155 | 1.7578 | -0.25635 | -6.3721 | -0.28381 | 0.036621 | 2.037 | 60.2463 | 60.6628 | 118.3365 | 124.7177 | 1.7578 | 124.7452 | 77.2202 | -0.28381 | 124.7177 | 1.7578 | 77.2202 | 118.3365 | 124.7452 | -124.9878 | -124.9924
1447.6406 | 124.9924 | -61.0428 | 63.5788 | 0.30235 | 0.018664 | 0.02195 | 0.0066309 | 0.067394 | 0.0034821 | 0.080348 | -59.3124 | 63.4918 | -61.3449 | -61.2442 | 57.2159 | 16.1362 | -1.0666 | -0.39368 | 63.5834 | -61.3312 | -0.30212 | -0.086975 | 1.7303 | -0.20142 | -6.3629 | -0.28839 | 0.004578 | 2.0325 | 59.9762 | 60.6491 | 118.2587 | 124.5346 | 1.7303 | 124.6262 | 77.179 | -0.28839 | 124.5346 | 1.7303 | 77.179 | 118.2587 | 124.6262 | -124.9237 | -124.91
1448.6406 | 125.0244 | -61.0382 | 63.5925 | 0.13451 | 0.018023 | 0.022591 | 0.0070581 | 0.065685 | 0.0036957 | 0.079707 | -59.2072 | 63.5605 | -61.29 | -61.2122 | 57.1518 | 16.0492 | -1.0803 | -0.41657 | 63.5788 | -61.3358 | -0.25177 | -0.032043 | 1.8311 | -0.17395 | -6.4407 | -0.29755 | -0.013733 | 2.0828 | 59.9579 | 60.6216 | 118.19 | 124.5987 | 1.8311 | 124.617 | 77.0874 | -0.29755 | 124.5987 | 1.8311 | 77.0874 | 118.19 | 124.617 | -124.8825 | -124.9283
1449.6406 | 124.9969 | -61.0428 | 63.5925 | 0.15739 | 0.018451 | 0.0196 | 0.010476 | 0.06483 | 0.0013457 | 0.078425 | -59.2346 | 63.6292 | -61.322 | -61.2625 | 57.0694 | 15.9348 | -1.0757 | -0.54932 | 63.5834 | -61.3861 | -0.27923 | 0.036621 | 1.8082 | -0.21973 | -6.5231 | -0.34332 | -0.009155 | 2.0874 | 59.967 | 60.4935 | 118.1122 | 124.6719 | 1.8082 | 124.6262 | 76.9775 | -0.34332 | 124.6719 | 1.8082 | 76.9775 | 118.1122 | 124.6262 | -124.9145 | -124.9786
1450.6406 | 124.942 | -61.0703 | 63.6383 | 0.13451 | 0.019092 | 0.021736 | 0.010903 | 0.066753 | 0.0028411 | 0.077357 | -59.2117 | 63.6246 | -61.3129 | -61.2671 | 57.019 | 15.8752 | -1.1169 | -0.59509 | 63.6108 | -61.3266 | -0.24262 | -0.013733 | 1.8585 | -0.19684 | -6.6193 | -0.25635 | -0.027466 | 2.1011 | 59.9533 | 60.4752 | 118.0893 | 124.6948 | 1.8585 | 124.6811 | 76.9455 | -0.25635 | 124.6948 | 1.8585 | 76.9455 | 118.0893 | 124.6811 | -124.9512 | -124.9649
1451.6406 | 124.9008 | -61.0153 | 63.6475 | 0.18028 | 0.018237 | 0.023659 | 0.011758 | 0.06718 | 0.0039093 | 0.079707 | -59.1888 | 63.652 | -61.2991 | -61.2442 | 57.0007 | 15.8249 | -1.1307 | -0.65002 | 63.6749 | -61.3129 | -0.28381 | 0.004578 | 1.8265 | -0.22888 | -6.6467 | -0.29755 | 0.027466 | 2.1103 | 59.8846 | 60.3653 | 118.0161 | 124.6674 | 1.8265 | 124.6902 | 76.8402 | -0.29755 | 124.6674 | 1.8265 | 76.8402 | 118.0161 | 124.6902 | -124.9466 | -124.9603
1452.6406 | 124.8779 | -60.9741 | 63.6978 | -0.033341 | 0.017383 | 0.018318 | 0.0023583 | 0.065471 | 0.0019867 | 0.080989 | -59.1797 | 63.5834 | -61.2808 | -61.203 | 56.9962 | 15.8478 | -1.2039 | -0.63171 | 63.6475 | -61.2625 | -0.3067 | -0.11444 | 1.7944 | -0.22888 | -6.7017 | -0.28839 | -0.050354 | 2.1011 | 59.7702 | 60.3424 | 117.9703 | 124.5575 | 1.7944 | 124.6216 | 76.8219 | -0.28839 | 124.5575 | 1.7944 | 76.8219 | 117.9703 | 124.6216 | -124.9786 | -124.9603
1453.6406 | 124.8871 | -61.0107 | 63.6841 | 0.11162 | 0.019946 | 0.020241 | 0.012612 | 0.063335 | 0.0028411 | 0.080134 | -59.1522 | 63.7115 | -61.2625 | -61.2946 | 56.8497 | 15.7562 | -1.1719 | -0.84228 | 63.6841 | -61.3174 | -0.25177 | 0.027466 | 1.8585 | -0.28381 | -6.8344 | -0.3067 | 0 | 2.1103 | 59.8389 | 60.1685 | 117.8604 | 124.7223 | 1.8585 | 124.6948 | 76.767 | -0.3067 | 124.7223 | 1.8585 | 76.767 | 117.8604 | 124.6948 | -124.9466 | -125.0015
1454.6406 | 124.9466 | -60.997 | 63.7436 | 0.11162 | 0.019946 | 0.018959 | 0.012185 | 0.065471 | 0.0041229 | 0.081843 | -59.1431 | 63.739 | -61.2442 | -61.2991 | 56.4331 | 15.3488 | -0.7782 | -0.7782 | 63.6841 | -61.3037 | -0.24719 | -0.004577 | 1.8539 | -0.30212 | -7.3105 | -0.3067 | -0.059509 | 2.1011 | 60.2188 | 60.2188 | 117.4301 | 124.736 | 1.8539 | 124.6811 | 76.3458 | -0.3067 | 124.736 | 1.8539 | 76.3458 | 117.4301 | 124.6811 | -124.9878 | -125.0473
1455.6406 | 124.9054 | -61.0199 | 63.7161 | 0.2108 | 0.020587 | 0.021095 | 0.0083397 | 0.066326 | 0.0036957 | 0.078425 | -59.1019 | 63.7024 | -61.2671 | -61.2213 | 56.8405 | 15.5731 | -1.3138 | -0.88806 | 63.6978 | -61.2946 | -0.24719 | -0.013732 | 1.918 | -0.20142 | -6.8756 | -0.27466 | -0.01831 | 2.1652 | 59.7061 | 60.1318 | 117.8604 | 124.7223 | 1.918 | 124.7177 | 76.593 | -0.27466 | 124.7223 | 1.918 | 76.593 | 117.8604 | 124.7177 | -124.9832 | -125.0107
1456.6406 | 124.8917 | -61.0016 | 63.7436 | 0.2108 | 0.021655 | 0.017037 | 0.010903 | 0.066753 | 0.0039093 | 0.081202 | -59.0973 | 63.7482 | -61.2442 | -61.2213 | 56.7856 | 15.5136 | -1.3687 | -0.93384 | 63.7115 | -61.3083 | -0.24262 | 0.004578 | 1.9043 | -0.21973 | -6.958 | -0.3067 | -0.032043 | 2.1469 | 59.6329 | 60.0677 | 117.7872 | 124.7498 | 1.9043 | 124.7131 | 76.5152 | -0.3067 | 124.7498 | 1.9043 | 76.5152 | 117.7872 | 124.7131 | -124.9878 | -125.0519
1457.6406 | 124.9557 | -60.9558 | 63.6795 | 0.035324 | 0.016955 | 0.014687 | 0.0021447 | 0.066539 | 0.0026275 | 0.07928 | -59.0469 | 63.6246 | -61.235 | -61.1801 | 56.8314 | 15.4907 | -1.4511 | -0.67291 | 63.7253 | -61.1984 | -0.27923 | -0.054931 | 1.9089 | -0.2243 | -6.8481 | -0.24261 | 0.045777 | 2.1881 | 59.5047 | 60.2829 | 117.7872 | 124.5804 | 1.9089 | 124.6811 | 76.4465 | -0.24261 | 124.5804 | 1.9089 | 76.4465 | 117.7872 | 124.6811 | -124.9145 | -124.8779
1458.6406 | 124.9237 | -60.9833 | 63.739 | 0.12688 | 0.018878 | 0.022163 | 0.011971 | 0.06483 | 0.0051911 | 0.081843 | -59.0378 | 63.7299 | -61.2396 | -61.1847 | 56.694 | 15.39 | -1.5244 | -1.0437 | 63.6932 | -61.3083 | -0.25635 | -0.009156 | 1.9455 | -0.20142 | -7.045 | -0.32501 | -0.045777 | 2.2018 | 59.4589 | 59.9396 | 117.6773 | 124.7131 | 1.9455 | 124.6765 | 76.3733 | -0.32501 | 124.7131 | 1.9455 | 76.3733 | 117.6773 | 124.6765 | -124.9786 | -125.0473
1459.6406 | 124.91 | -60.9695 | 63.7482 | 0.14976 | 0.019946 | 0.021523 | 0.010262 | 0.06483 | 0.0032683 | 0.079921 | -59.0286 | 63.7482 | -61.2076 | -61.203 | 56.6757 | 15.3259 | -1.5656 | -1.1215 | 63.7253 | -61.2717 | -0.23804 | 0 | 1.9409 | -0.23346 | -7.0724 | -0.30212 | -0.022888 | 2.179 | 59.404 | 59.848 | 117.6453 | 124.7177 | 1.9409 | 124.6948 | 76.2955 | -0.30212 | 124.7177 | 1.9409 | 76.2955 | 117.6453 | 124.6948 | -124.9557 | -125.0198
1460.6406 | 124.8276 | -60.965 | 63.6795 | 0.042953 | 0.022723 | 0.020668 | 0.011971 | 0.065471 | 0.0026275 | 0.079921 | -58.9783 | 63.7711 | -61.2076 | -61.1984 | 56.6116 | 15.2206 | -1.5793 | -1.1948 | 63.7619 | -61.2671 | -0.24262 | 0.091553 | 1.9867 | -0.23346 | -7.0679 | -0.30212 | 0.082398 | 2.2293 | 59.3857 | 59.7702 | 117.5766 | 124.736 | 1.9867 | 124.7269 | 76.1856 | -0.30212 | 124.736 | 1.9867 | 76.1856 | 117.5766 | 124.7269 | -124.8871 | -124.9466
1461.6406 | 124.8734 | -60.9375 | 63.7985 | 0.035324 | 0.021869 | 0.020454 | 0.010262 | 0.068035 | 0.0015595 | 0.079707 | -58.9645 | 63.7848 | -61.2122 | -61.1618 | 56.5842 | 15.184 | -1.6113 | -1.2543 | 63.7848 | -61.235 | -0.27466 | -0.013733 | 1.973 | -0.2243 | -7.2144 | -0.29755 | -0.013733 | 2.2476 | 59.3262 | 59.6832 | 117.5217 | 124.7223 | 1.973 | 124.7223 | 76.1215 | -0.29755 | 124.7223 | 1.973 | 76.1215 | 117.5217 | 124.7223 | -125.0107 | -125.0336
1462.6406 | 124.9832 | -60.878 | 63.7436 | 0.12688 | 0.017169 | 0.017464 | 0.00022215 | 0.065471 | 0.0026275 | 0.080134 | -58.8821 | 63.6841 | -61.1755 | -61.0931 | 56.6345 | 15.2344 | -1.8494 | -1.1719 | 63.7436 | -61.171 | -0.29755 | -0.059509 | 1.9959 | -0.21515 | -7.1091 | -0.29297 | 0 | 2.2934 | 59.0286 | 59.7061 | 117.5125 | 124.5621 | 1.9959 | 124.6216 | 76.1124 | -0.29297 | 124.5621 | 1.9959 | 76.1124 | 117.5125 | 124.6216 | -124.9191 | -124.9146
1463.6406 | 124.9054 | -60.9055 | 63.7802 | 0.16502 | 0.019305 | 0.018745 | 0.010049 | 0.066326 | 0.0045501 | 0.080775 | -58.9096 | 63.8077 | -61.1893 | -61.1526 | 56.5109 | 15.0742 | -1.7944 | -1.3504 | 63.7894 | -61.1938 | -0.28381 | 0.027466 | 1.9958 | -0.24719 | -7.2693 | -0.28839 | 0.009156 | 2.2797 | 59.111 | 59.5551 | 117.4164 | 124.7131 | 1.9958 | 124.6948 | 75.9796 | -0.28839 | 124.7131 | 1.9958 | 75.9796 | 117.4164 | 124.6948 | -124.9695 | -124.9741
1464.6406 | 124.8962 | -60.91 | 63.8123 | 0.18791 | 0.018451 | 0.022804 | 0.010262 | 0.065044 | 0.0060455 | 0.081843 | -58.9096 | 63.8168 | -61.1481 | -61.1618 | 56.4514 | 15.0238 | -1.8494 | -1.4236 | 63.7711 | -61.2534 | -0.23804 | 0.004577 | 2.0004 | -0.25177 | -7.3608 | -0.34332 | -0.041199 | 2.2385 | 59.0607 | 59.4864 | 117.3615 | 124.7269 | 2.0004 | 124.6811 | 75.9338 | -0.34332 | 124.7269 | 2.0004 | 75.9338 | 117.3615 | 124.6811 | -124.9603 | -125.0656
1465.6406 | 124.8962 | -60.9192 | 63.8123 | 0.38628 | 0.020587 | 0.020027 | 0.011971 | 0.06718 | 0.00091854 | 0.078639 | -58.873 | 63.826 | -61.1893 | -61.1481 | 56.4514 | 14.9597 | -1.9547 | -1.5198 | 63.8031 | -61.2259 | -0.27008 | 0.013733 | 2.0462 | -0.22888 | -7.3608 | -0.3067 | -0.009155 | 2.3163 | 58.9645 | 59.3994 | 117.3706 | 124.7452 | 2.0462 | 124.7223 | 75.8789 | -0.3067 | 124.7452 | 2.0462 | 75.8789 | 117.3706 | 124.7223 | -125.0015 | -125.0381
1466.6406 | 124.8779 | -60.91 | 63.8031 | -0.14015 | 0.019946 | 0.018532 | 0.010903 | 0.068248 | 0.0036957 | 0.078853 | -58.7906 | 63.8123 | -61.1481 | -61.1481 | 56.4011 | 14.9002 | -2.0233 | -1.5747 | 63.8123 | -61.1984 | -0.23804 | 0.009155 | 2.1194 | -0.23804 | -7.402 | -0.28839 | 0.009155 | 2.3575 | 58.8867 | 59.3353 | 117.3111 | 124.7223 | 2.1194 | 124.7223 | 75.8102 | -0.28839 | 124.7223 | 2.1194 | 75.8102 | 117.3111 | 124.7223 | -124.9512 | -125.0015
1467.6406 | 125.0015 | -60.8688 | 63.7802 | 0.23369 | 0.018664 | 0.022591 | 0.0076989 | 0.068035 | 0.0015595 | 0.08227 | -58.786 | 63.7711 | -61.1343 | -61.0703 | 56.4423 | 14.9551 | -2.2934 | -1.5427 | 63.7619 | -61.1572 | -0.2655 | -0.009155 | 2.0828 | -0.20142 | -7.338 | -0.28839 | -0.01831 | 2.3483 | 58.5754 | 59.3262 | 117.3111 | 124.6399 | 2.0828 | 124.6307 | 75.824 | -0.28839 | 124.6399 | 2.0828 | 75.824 | 117.3111 | 124.6307 | -124.9145 | -124.9374
1468.6406 | 124.8642 | -60.8826 | 63.8306 | 0.0048064 | 0.021014 | 0.025581 | 0.012826 | 0.06483 | 0.0036957 | 0.081202 | -58.7723 | 63.826 | -61.1252 | -61.0886 | 56.3461 | 14.8087 | -2.2064 | -1.6754 | 63.8168 | -61.1801 | -0.24262 | -0.004577 | 2.1103 | -0.20599 | -7.4844 | -0.29755 | -0.013733 | 2.3529 | 58.6761 | 59.2072 | 117.2287 | 124.7086 | 2.1103 | 124.6994 | 75.6912 | -0.29755 | 124.7086 | 2.1103 | 75.6912 | 117.2287 | 124.6994 | -124.9557 | -125.0107
1469.6406 | 124.8779 | -60.9146 | 63.8214 | 0.073471 | 0.018664 | 0.020668 | 0.010903 | 0.067608 | 0.0024139 | 0.080989 | -58.786 | 63.8718 | -61.1206 | -61.1206 | 56.2775 | 14.7125 | -2.2339 | -1.7212 | 63.8306 | -61.1847 | -0.20599 | 0.050354 | 2.1286 | -0.20599 | -7.5439 | -0.27008 | 0.009155 | 2.3346 | 58.6807 | 59.1934 | 117.1921 | 124.7864 | 2.1286 | 124.7452 | 75.6271 | -0.27008 | 124.7864 | 2.1286 | 75.6271 | 117.1921 | 124.7452 | -124.942 | -125.0061
1470.6406 | 124.8825 | -60.8505 | 63.826 | 0.08873 | 0.021228 | 0.023872 | 0.0087671 | 0.066967 | 0.0030547 | 0.079921 | -58.7723 | 63.8535 | -61.1252 | -61.0977 | 56.2546 | 14.6713 | -2.3254 | -1.7899 | 63.8626 | -61.1938 | -0.27466 | 0.027466 | 2.0782 | -0.24719 | -7.5714 | -0.34332 | 0.036621 | 2.3529 | 58.5251 | 59.0607 | 117.1051 | 124.704 | 2.0782 | 124.7131 | 75.5219 | -0.34332 | 124.704 | 2.0782 | 75.5219 | 117.1051 | 124.7131 | -124.9512 | -125.0198
1471.6406 | 124.9054 | -60.8826 | 63.8443 | 0.40916 | 0.022082 | 0.022377 | 0.011758 | 0.066967 | 0.0045501 | 0.082057 | -58.7448 | 63.8535 | -61.1069 | -61.0977 | 56.1905 | 14.6255 | -2.3941 | -1.8723 | 63.8809 | -61.1389 | -0.22431 | 0.009156 | 2.1378 | -0.21515 | -7.6538 | -0.25635 | 0.036621 | 2.3621 | 58.4885 | 59.0103 | 117.0731 | 124.736 | 2.1378 | 124.7635 | 75.5081 | -0.25635 | 124.736 | 2.1378 | 75.5081 | 117.0731 | 124.7635 | -124.9512 | -124.9832
1472.6406 | 125.0153 | -60.8093 | 63.8123 | 0.23369 | 0.02016 | 0.023232 | 0.0064171 | 0.067394 | 0.0039093 | 0.08227 | -58.6349 | 63.7619 | -61.084 | -60.997 | 56.2592 | 14.6988 | -2.5818 | -1.7624 | 63.8214 | -61.0886 | -0.27466 | -0.050354 | 2.1744 | -0.18768 | -7.5531 | -0.27924 | 0.009155 | 2.449 | 58.2275 | 59.0469 | 117.0685 | 124.5712 | 2.1744 | 124.6307 | 75.5081 | -0.27924 | 124.5712 | 2.1744 | 75.5081 | 117.0685 | 124.6307 | -124.8962 | -124.9008
1473.6406 | 124.8688 | -60.8826 | 63.8535 | 0.14214 | 0.020801 | 0.020454 | 0.0066309 | 0.064617 | 0.0030547 | 0.078639 | -58.7265 | 63.8718 | -61.1069 | -61.0657 | 56.2408 | 14.5248 | -2.5177 | -1.9226 | 63.8763 | -61.1572 | -0.22431 | 0.01831 | 2.1561 | -0.18311 | -7.6126 | -0.27466 | 0.022888 | 2.3804 | 58.3649 | 58.96 | 117.1234 | 124.7543 | 2.1561 | 124.7589 | 75.4074 | -0.27466 | 124.7543 | 2.1561 | 75.4074 | 117.1234 | 124.7589 | -124.9603 | -125.0107
1474.6406 | 124.91 | -60.8459 | 63.8947 | 0.050583 | 0.021869 | 0.02195 | 0.01304 | 0.066753 | 0.0013457 | 0.082484 | -58.7082 | 63.8947 | -61.1023 | -61.0474 | 55.6778 | 14.1907 | -2.0554 | -1.8677 | 63.8672 | -61.1252 | -0.25635 | 0 | 2.1378 | -0.20142 | -8.2169 | -0.27924 | -0.027466 | 2.3941 | 58.7906 | 58.9783 | 116.5237 | 124.7406 | 2.1378 | 124.7131 | 75.0366 | -0.27924 | 124.7406 | 2.1378 | 75.0366 | 116.5237 | 124.7131 | -124.9969 | -125.0198
1475.6406 | 124.8825 | -60.8139 | 63.8718 | 0.0048064 | 0.022937 | 0.024086 | 0.012612 | 0.069103 | 0.0017731 | 0.081416 | -58.6075 | 63.8763 | -61.0794 | -61.0336 | 56.0532 | 14.4699 | -2.5406 | -1.973 | 63.8855 | -61.1343 | -0.2655 | 0.004578 | 2.2064 | -0.21973 | -7.8186 | -0.32043 | 0.013733 | 2.4719 | 58.2733 | 58.8409 | 116.8671 | 124.6902 | 2.2064 | 124.6994 | 75.2838 | -0.32043 | 124.6902 | 2.2064 | 75.2838 | 116.8671 | 124.6994 | -124.9512 | -125.0061
1476.6406 | 124.8459 | -60.8414 | 63.8855 | 0.050583 | 0.021869 | 0.024086 | 0.010262 | 0.068676 | 0.0028411 | 0.081202 | -58.6212 | 63.9175 | -61.0428 | -61.0474 | 55.9845 | 14.36 | -2.6505 | -2.1057 | 63.9267 | -61.116 | -0.20142 | 0.032044 | 2.2202 | -0.20599 | -7.901 | -0.27466 | 0.041199 | 2.4216 | 58.1909 | 58.7357 | 116.8259 | 124.7589 | 2.2202 | 124.7681 | 75.2014 | -0.27466 | 124.7589 | 2.2202 | 75.2014 | 116.8259 | 124.7681 | -124.9283 | -125.0015
1477.6406 | 124.9969 | -60.7681 | 63.8351 | 0.23369 | 0.018451 | 0.023018 | 0.0064171 | 0.06718 | 0.0024139 | 0.083766 | -58.5434 | 63.8077 | -61.0428 | -60.9512 | 56.0715 | 14.4608 | -2.8976 | -1.9958 | 63.8535 | -61.0565 | -0.27466 | -0.027466 | 2.2247 | -0.18311 | -7.7637 | -0.28839 | 0.018311 | 2.4994 | 57.8705 | 58.7723 | 116.8396 | 124.5758 | 2.2247 | 124.6216 | 75.2289 | -0.28839 | 124.5758 | 2.2247 | 75.2289 | 116.8396 | 124.6216 | -124.8779 | -124.8917
1478.6406 | 124.8962 | -60.8139 | 63.9084 | 0.11925 | 0.021869 | 0.022591 | 0.0094079 | 0.068035 | 0.0022003 | 0.081416 | -58.4793 | 63.9038 | -61.0703 | -60.9467 | 55.9387 | 14.2456 | -2.742 | -2.1561 | 63.9175 | -61.1069 | -0.25635 | -0.004577 | 2.3346 | -0.13275 | -7.9697 | -0.29297 | 0.009156 | 2.5909 | 58.0719 | 58.6578 | 116.7526 | 124.7177 | 2.3346 | 124.7314 | 75.0595 | -0.29297 | 124.7177 | 2.3346 | 75.0595 | 116.7526 | 124.7314 | -124.9786 | -125.0153
1479.6406 | 124.855 | -60.7773 | 63.9267 | 0.08873 | 0.022723 | 0.023445 | 0.011117 | 0.067821 | 0.0092499 | 0.084407 | -58.5663 | 63.9313 | -61.0336 | -61.2762 | 55.9982 | 14.5432 | -2.9022 | -2.1698 | 63.9587 | -61.0611 | -0.25635 | 0.004577 | 2.211 | -0.49896 | -7.9285 | -0.28381 | 0.032043 | 2.4673 | 57.8751 | 58.6075 | 116.7755 | 124.7086 | 2.211 | 124.736 | 75.3204 | -0.28381 | 124.7086 | 2.211 | 75.3204 | 116.7755 | 124.736 | -124.9603 | -124.9878
1480.6406 | 124.9786 | -60.8093 | 63.945 | 0.08873 | 0.021441 | 0.023232 | 0.011544 | 0.06718 | 0.0030547 | 0.081202 | -58.5205 | 63.9359 | -61.0153 | -61.0199 | 55.8151 | 14.1861 | -2.8519 | -2.449 | 63.9359 | -61.0977 | -0.20599 | -0.009155 | 2.2888 | -0.21057 | -8.1299 | -0.28839 | -0.009155 | 2.4948 | 57.9575 | 58.3603 | 116.6245 | 124.7452 | 2.2888 | 124.7452 | 74.9954 | -0.28839 | 124.7452 | 2.2888 | 74.9954 | 116.6245 | 124.7452 | -124.9603 | -125.0427
1481.6406 | 124.8734 | -60.7636 | 63.9359 | -0.033341 | 0.022723 | 0.024086 | 0.013894 | 0.068889 | 0.0047637 | 0.083125 | -58.4518 | 63.9816 | -61.0062 | -60.965 | 55.8243 | 14.2136 | -2.9022 | -2.2247 | 63.9679 | -61.0565 | -0.24262 | 0.045776 | 2.3117 | -0.20142 | -8.1116 | -0.29297 | 0.032044 | 2.5543 | 57.8613 | 58.5388 | 116.5878 | 124.7452 | 2.3117 | 124.7314 | 74.9771 | -0.29297 | 124.7452 | 2.3117 | 74.9771 | 116.5878 | 124.7314 | -124.942 | -124.9924
1482.6406 | 124.9832 | -60.7315 | 63.9175 | 0.32524 | 0.02016 | 0.020668 | 0.0076989 | 0.067821 | 0.0017731 | 0.082911 | -58.4152 | 63.8672 | -60.997 | -60.8963 | 55.8792 | 14.2822 | -3.0853 | -2.179 | 63.9084 | -60.9787 | -0.2655 | -0.050355 | 2.3163 | -0.16479 | -8.0383 | -0.24719 | -0.009156 | 2.5818 | 57.6462 | 58.5526 | 116.6107 | 124.5987 | 2.3163 | 124.6399 | 75.0137 | -0.24719 | 124.5987 | 2.3163 | 75.0137 | 116.6107 | 124.6399 | -124.9146 | -124.8962
1483.6406 | 124.8871 | -60.7361 | 63.9908 | 0.10399 | 0.02251 | 0.020668 | 0.013253 | 0.068676 | 0.0030547 | 0.083125 | -58.4015 | 63.9771 | -60.9604 | -60.9512 | 55.7098 | 14.1266 | -2.9297 | -2.3163 | 63.9862 | -61.0382 | -0.2243 | -0.013733 | 2.3346 | -0.21515 | -8.2809 | -0.30212 | -0.004578 | 2.5589 | 57.8064 | 58.4198 | 116.4459 | 124.7131 | 2.3346 | 124.7223 | 74.8627 | -0.30212 | 124.7131 | 2.3346 | 74.8627 | 116.4459 | 124.7223 | -124.9512 | -125.029
1484.6406 | 124.9329 | -60.7224 | 64.0182 | 0.11925 | 0.021655 | 0.022804 | 0.011331 | 0.068035 | 0.0017731 | 0.083125 | -58.4061 | 64.0091 | -60.9741 | -61.0703 | 55.2658 | 13.7695 | -2.5955 | -2.3026 | 64.0274 | -61.0107 | -0.25177 | -0.009156 | 2.3163 | -0.3479 | -8.7524 | -0.28839 | 0.009155 | 2.5681 | 58.1268 | 58.4198 | 115.9882 | 124.7314 | 2.3163 | 124.7498 | 74.4919 | -0.28839 | 124.7314 | 2.3163 | 74.4919 | 115.9882 | 124.7498 | -124.9924 | -125.029
1485.6406 | 124.8413 | -60.7224 | 63.9633 | -0.018082 | 0.021869 | 0.023872 | 0.011758 | 0.068889 | 0.0039093 | 0.08163 | -58.3923 | 64.0091 | -60.9787 | -60.965 | 55.5908 | 14.0625 | -2.9846 | -2.4353 | 63.9999 | -61.0062 | -0.25635 | 0.045776 | 2.33 | -0.24261 | -8.3725 | -0.28381 | 0.036621 | 2.5864 | 57.7377 | 58.287 | 116.3132 | 124.7314 | 2.33 | 124.7223 | 74.7849 | -0.28381 | 124.7314 | 2.33 | 74.7849 | 116.3132 | 124.7223 | -124.942 | -124.9695
1486.6406 | 124.8825 | -60.6995 | 63.9999 | 0.0811 | 0.021655 | 0.021095 | 0.010903 | 0.06953 | 0.0019867 | 0.079493 | -58.3374 | 64.0274 | -60.9421 | -60.9329 | 55.5771 | 13.9938 | -3.0396 | -2.4353 | 64.0503 | -61.0199 | -0.24262 | 0.027466 | 2.3621 | -0.23346 | -8.4229 | -0.32043 | 0.050354 | 2.6047 | 57.6599 | 58.2642 | 116.2766 | 124.7269 | 2.3621 | 124.7498 | 74.6933 | -0.32043 | 124.7269 | 2.3621 | 74.6933 | 116.2766 | 124.7498 | -124.942 | -125.0198
1487.6562 | 124.9237 | -60.6308 | 63.9908 | 0.12688 | 0.019946 | 0.020241 | 0.0036401 | 0.065899 | 0.0030547 | 0.08163 | -58.3282 | 63.8992 | -60.9192 | -60.8826 | 55.6366 | 14.0533 | -3.2089 | -2.3712 | 63.9862 | -60.9192 | -0.28839 | -0.091553 | 2.3026 | -0.25177 | -8.3542 | -0.28839 | -0.004578 | 2.5909 | 57.4219 | 58.2596 | 116.2674 | 124.53 | 2.3026 | 124.617 | 74.6841 | -0.28839 | 124.53 | 2.3026 | 74.6841 | 116.2674 | 124.617 | -124.91 | -124.91
1488.6406 | 124.91 | -60.6583 | 64.0457 | -0.048599 | 0.020373 | 0.021095 | 0.014108 | 0.068462 | 0.0049773 | 0.08163 | -58.2321 | 64.0503 | -60.9146 | -60.8505 | 55.5588 | 14.0213 | -3.1448 | -2.417 | 64.0503 | -60.9695 | -0.25635 | 0.004578 | 2.4261 | -0.19226 | -8.4869 | -0.31128 | 0.004578 | 2.6825 | 57.5134 | 58.2413 | 116.217 | 124.7086 | 2.4261 | 124.7086 | 74.6796 | -0.31128 | 124.7086 | 2.4261 | 74.6796 | 116.217 | 124.7086 | -124.9603 | -125.0153
1489.6406 | 124.8962 | -60.6491 | 64.032 | -0.04097 | 0.02315 | 0.022804 | 0.012612 | 0.067608 | 0.0024139 | 0.082698 | -58.1955 | 64.0411 | -60.9009 | -60.8231 | 55.5038 | 14.035 | -3.186 | -2.4307 | 64.0411 | -60.9467 | -0.25177 | 0.009156 | 2.4536 | -0.17395 | -8.5281 | -0.29755 | 0.009156 | 2.7054 | 57.4631 | 58.2184 | 116.153 | 124.6902 | 2.4536 | 124.6902 | 74.6841 | -0.29755 | 124.6902 | 2.4536 | 74.6841 | 116.153 | 124.6902 | -124.9329 | -124.9786
1490.6406 | 124.9008 | -60.6583 | 64.0457 | -0.0028231 | 0.021869 | 0.026436 | 0.012185 | 0.06718 | 0.0041229 | 0.083766 | -58.2047 | 64.0411 | -60.8734 | -60.8414 | 55.4489 | 13.9572 | -3.2089 | -2.5177 | 64.0457 | -60.9512 | -0.21515 | -0.004577 | 2.4536 | -0.18311 | -8.5968 | -0.29297 | 0 | 2.6688 | 57.4493 | 58.1406 | 116.1072 | 124.6994 | 2.4536 | 124.704 | 74.6155 | -0.29297 | 124.6994 | 2.4536 | 74.6155 | 116.1072 | 124.704 | -124.9191 | -124.9969
1491.6406 | 124.8825 | -60.6537 | 64.0732 | 0.027695 | 0.021869 | 0.02665 | 0.013253 | 0.068676 | 0.0032683 | 0.083979 | -58.2184 | 64.0778 | -60.9192 | -60.878 | 55.3665 | 13.9664 | -3.2272 | -2.5726 | 64.0549 | -60.9695 | -0.2655 | 0.004578 | 2.4353 | -0.2243 | -8.7067 | -0.31586 | -0.01831 | 2.7008 | 57.4265 | 58.0811 | 116.0202 | 124.7314 | 2.4353 | 124.7086 | 74.6201 | -0.31586 | 124.7314 | 2.4353 | 74.6201 | 116.0202 | 124.7086 | -124.9924 | -125.0427
1492.6406 | 124.9283 | -60.6171 | 63.9999 | 0.17265 | 0.021869 | 0.016823 | 0.0094079 | 0.067821 | 0.0051911 | 0.082911 | -58.1863 | 64.0228 | -60.9009 | -60.8505 | 55.3574 | 13.9526 | -3.3829 | -2.5543 | 64.0503 | -60.9329 | -0.28381 | 0.022888 | 2.4307 | -0.23346 | -8.6426 | -0.31586 | 0.050354 | 2.7145 | 57.2342 | 58.0627 | 115.9744 | 124.6399 | 2.4307 | 124.6674 | 74.5697 | -0.31586 | 124.6399 | 2.4307 | 74.5697 | 115.9744 | 124.6674 | -124.9008 | -124.9329
1493.6406 | 124.8779 | -60.64 | 64.0686 | -0.048599 | 0.022937 | 0.023659 | 0.012826 | 0.065685 | 0.0032683 | 0.081202 | -58.1223 | 64.0732 | -60.878 | -60.8414 | 55.3024 | 13.9343 | -3.2684 | -2.6001 | 64.0503 | -60.9329 | -0.23804 | 0.004577 | 2.5177 | -0.20142 | -8.7662 | -0.29297 | -0.018311 | 2.7557 | 57.3715 | 58.0399 | 115.9424 | 124.7131 | 2.5177 | 124.6902 | 74.5743 | -0.29297 | 124.7131 | 2.5177 | 74.5743 | 115.9424 | 124.6902 | -124.9466 | -125.0015
1494.6406 | 124.8688 | -60.6216 | 64.0732 | -0.063858 | 0.022296 | 0.025154 | 0.010476 | 0.067608 | 0.0032683 | 0.081843 | -58.0856 | 64.0915 | -60.8368 | -60.8093 | 55.2795 | 13.9618 | -3.2547 | -2.5681 | 64.0869 | -60.9421 | -0.21515 | 0.018311 | 2.536 | -0.18768 | -8.7936 | -0.32044 | 0.013733 | 2.7512 | 57.3669 | 58.0536 | 115.9012 | 124.7131 | 2.536 | 124.7086 | 74.5834 | -0.32044 | 124.7131 | 2.536 | 74.5834 | 115.9012 | 124.7086 | -124.91 | -125.0153
1495.6406 | 124.8642 | -60.6125 | 64.1006 | -0.19356 | 0.021441 | 0.0243 | 0.012612 | 0.071239 | 0.0015595 | 0.083339 | -58.0399 | 64.1052 | -60.8597 | -60.7864 | 55.2612 | 13.9938 | -3.2547 | -2.5452 | 64.0961 | -60.878 | -0.24719 | 0.004578 | 2.5726 | -0.17395 | -8.8394 | -0.2655 | -0.004578 | 2.8198 | 57.3578 | 58.0673 | 115.8737 | 124.7177 | 2.5726 | 124.7086 | 74.6063 | -0.2655 | 124.7177 | 2.5726 | 74.6063 | 115.8737 | 124.7086 | -124.9603 | -124.9786
1496.6406 | 124.9237 | -60.5896 | 64.1052 | -0.38429 | 0.021014 | 0.025154 | 0.011331 | 0.06953 | 0.0036957 | 0.082911 | -58.0124 | 64.0961 | -60.8276 | -60.7681 | 55.1926 | 13.9893 | -3.3005 | -2.6001 | 64.1144 | -60.9055 | -0.23804 | -0.009156 | 2.5772 | -0.17853 | -8.9127 | -0.31586 | 0.009155 | 2.8152 | 57.2891 | 57.9895 | 115.7822 | 124.6857 | 2.5772 | 124.704 | 74.5789 | -0.31586 | 124.6857 | 2.5772 | 74.5789 | 115.7822 | 124.704 | -124.9329 | -125.0107
1497.6406 | 125.0015 | -60.585 | 64.0549 | 0.2108 | 0.021014 | 0.021309 | 0.010049 | 0.068035 | 0.0039093 | 0.08462 | -58.0215 | 64.032 | -60.8643 | -60.7681 | 55.188 | 14.0213 | -3.4561 | -2.6001 | 64.0457 | -60.8688 | -0.27924 | -0.022889 | 2.5635 | -0.1831 | -8.8669 | -0.28381 | -0.009156 | 2.8427 | 57.1289 | 57.9849 | 115.773 | 124.617 | 2.5635 | 124.6307 | 74.6063 | -0.28381 | 124.617 | 2.5635 | 74.6063 | 115.773 | 124.6307 | -124.9191 | -124.9237
1498.6406 | 124.9008 | -60.5759 | 64.1144 | -0.048599 | 0.022082 | 0.025154 | 0.012826 | 0.065685 | 0.0030547 | 0.083339 | -57.9712 | 64.1098 | -60.8139 | -60.7727 | 55.1147 | 13.9206 | -3.3829 | -2.6642 | 64.1418 | -60.8597 | -0.23804 | -0.004578 | 2.6047 | -0.19684 | -8.9996 | -0.28381 | 0.027466 | 2.8427 | 57.193 | 57.9117 | 115.6906 | 124.6857 | 2.6047 | 124.7177 | 74.4965 | -0.28381 | 124.6857 | 2.6047 | 74.4965 | 115.6906 | 124.7177 | -124.9283 | -124.9741
1499.6406 | 124.9329 | -60.5667 | 64.1464 | -0.13252 | 0.024005 | 0.021736 | 0.012185 | 0.067608 | 0.0028411 | 0.082698 | -57.9391 | 64.1327 | -60.8231 | -60.7269 | 55.0873 | 13.9297 | -3.4103 | -2.6642 | 64.151 | -60.8414 | -0.25635 | -0.013733 | 2.6276 | -0.16022 | -9.0591 | -0.27466 | 0.004578 | 2.8839 | 57.1564 | 57.9025 | 115.654 | 124.6994 | 2.6276 | 124.7177 | 74.4965 | -0.27466 | 124.6994 | 2.6276 | 74.4965 | 115.654 | 124.7177 | -124.9695 | -124.9878
1500.6406 | 124.9008 | -60.5301 | 64.1373 | -0.13252 | 0.02315 | 0.024086 | 0.0098351 | 0.068889 | 0.0039093 | 0.083339 | -57.9208 | 64.1464 | -60.8002 | -60.704 | 55.0323 | 13.8702 | -3.4287 | -2.6779 | 64.1647 | -60.8322 | -0.27008 | 0.009155 | 2.6093 | -0.17395 | -9.1049 | -0.30212 | 0.027466 | 2.8793 | 57.1014 | 57.8522 | 115.5624 | 124.6765 | 2.6093 | 124.6948 | 74.4003 | -0.30212 | 124.6765 | 2.6093 | 74.4003 | 115.5624 | 124.6948 | -124.9374 | -124.9695
1501.6406 | 124.8917 | -60.553 | 64.1693 | -0.094376 | 0.021228 | 0.022591 | 0.011971 | 0.067608 | 0.0019867 | 0.084407 | -57.9071 | 64.1602 | -60.791 | -60.6995 | 55.0095 | 13.8519 | -3.7354 | -2.7786 | 64.1464 | -60.8459 | -0.23804 | -0.009156 | 2.6459 | -0.14648 | -9.1599 | -0.29297 | -0.022889 | 2.8839 | 56.8176 | 57.7744 | 115.5624 | 124.7131 | 2.6459 | 124.6994 | 74.4049 | -0.29297 | 124.7131 | 2.6459 | 74.4049 | 115.5624 | 124.6994 | -124.9603 | -125.0153
1502.6406 | 124.6719 | -60.5896 | 64.1052 | 0.065841 | 0.022937 | 0.024086 | 0.01368 | 0.068248 | 0.0015595 | 0.085688 | -57.9346 | 64.1373 | -60.8185 | -60.8185 | 54.8721 | 13.7421 | -3.4241 | -2.8519 | 64.1785 | -60.8414 | -0.22888 | 0.032043 | 2.655 | -0.22888 | -9.2331 | -0.25177 | 0.073242 | 2.8839 | 57.1655 | 57.7377 | 115.4617 | 124.7269 | 2.655 | 124.7681 | 74.3317 | -0.25177 | 124.7269 | 2.655 | 74.3317 | 115.4617 | 124.7681 | -124.9237 | -124.9466
1503.6406 | 124.9237 | -60.5347 | 64.1556 | -0.22408 | 0.022082 | 0.022804 | 0.01304 | 0.065685 | 0.0028411 | 0.085261 | -57.8476 | 64.1739 | -60.7864 | -60.704 | 54.95 | 13.8519 | -3.4287 | -2.7466 | 64.1876 | -60.8185 | -0.25177 | 0.01831 | 2.6871 | -0.16937 | -9.2056 | -0.28381 | 0.032043 | 2.9388 | 57.106 | 57.7881 | 115.4846 | 124.7086 | 2.6871 | 124.7223 | 74.3866 | -0.28381 | 124.7086 | 2.6871 | 74.3866 | 115.4846 | 124.7223 | -124.942 | -124.9741
1504.6406 | 124.9283 | -60.5026 | 64.1876 | -0.14015 | 0.022723 | 0.023232 | 0.010903 | 0.065685 | 0.0039093 | 0.083979 | -57.8339 | 64.2059 | -60.7498 | -60.672 | 54.9088 | 13.829 | -3.4241 | -2.7603 | 64.1922 | -60.8002 | -0.24719 | 0.018311 | 2.6688 | -0.16937 | -9.2789 | -0.29755 | 0.004578 | 2.916 | 57.0786 | 57.7423 | 115.4114 | 124.7086 | 2.6688 | 124.6948 | 74.3317 | -0.29755 | 124.7086 | 2.6688 | 74.3317 | 115.4114 | 124.6948 | -124.9374 | -124.9878
1505.6406 | 124.9054 | -60.5072 | 64.1739 | -0.13252 | 0.024005 | 0.023232 | 0.012185 | 0.066539 | 0.0028411 | 0.083766 | -57.7927 | 64.1876 | -60.7544 | -60.6766 | 54.7897 | 13.6688 | -3.3554 | -2.6688 | 64.2059 | -60.8002 | -0.24719 | 0.013733 | 2.7145 | -0.16937 | -9.3842 | -0.29297 | 0.032044 | 2.9617 | 57.1518 | 57.8384 | 115.2969 | 124.6948 | 2.7145 | 124.7131 | 74.176 | -0.29297 | 124.6948 | 2.7145 | 74.176 | 115.2969 | 124.7131 | -124.9283 | -124.9741
1506.6406 | 124.7589 | -60.5118 | 64.1876 | -0.20882 | 0.020587 | 0.0243 | 0.012612 | 0.068889 | 0.0041229 | 0.085261 | -57.756 | 64.2105 | -60.7224 | -60.672 | 54.7989 | 13.8245 | -3.5248 | -2.7969 | 64.2105 | -60.8093 | -0.21057 | 0.022888 | 2.7557 | -0.16022 | -9.3887 | -0.29755 | 0.022888 | 2.9663 | 56.987 | 57.7148 | 115.3107 | 124.7223 | 2.7557 | 124.7223 | 74.3362 | -0.29755 | 124.7223 | 2.7557 | 74.3362 | 115.3107 | 124.7223 | -124.91 | -124.9969
1507.6406 | 124.8779 | -60.498 | 64.1922 | 0.11925 | 0.02315 | 0.022591 | 0.011758 | 0.067608 | 0.0015595 | 0.082484 | -57.8018 | 64.1647 | -60.7636 | -60.7498 | 54.6707 | 13.7787 | -3.5294 | -2.8931 | 64.2197 | -60.8139 | -0.2655 | -0.027466 | 2.6962 | -0.25177 | -9.5215 | -0.31586 | 0.027466 | 2.9617 | 56.9687 | 57.605 | 115.1688 | 124.6628 | 2.6962 | 124.7177 | 74.2767 | -0.31586 | 124.6628 | 2.6962 | 74.2767 | 115.1688 | 124.7177 | -124.9557 | -125.0061
1508.6406 | 124.9146 | -60.4706 | 64.2014 | -0.21645 | 0.022723 | 0.020668 | 0.012185 | 0.067394 | 0.0028411 | 0.084407 | -57.7103 | 64.1922 | -60.7315 | -60.6766 | 54.6844 | 13.7924 | -3.5385 | -2.8198 | 64.2059 | -60.7819 | -0.26093 | -0.009155 | 2.7603 | -0.20599 | -9.5169 | -0.31128 | 0.004578 | 3.0212 | 56.9321 | 57.6508 | 115.155 | 124.6628 | 2.7603 | 124.6765 | 74.263 | -0.31128 | 124.6628 | 2.7603 | 74.263 | 115.155 | 124.6765 | -124.9329 | -124.9832
1509.6406 | 124.8779 | -60.498 | 64.1876 | -0.25459 | 0.022296 | 0.021309 | 0.011971 | 0.066326 | 0.0054047 | 0.084407 | -57.7606 | 64.2059 | -60.7452 | -60.704 | 54.6021 | 13.7512 | -3.4836 | -2.8748 | 64.238 | -60.791 | -0.24719 | 0.018311 | 2.7374 | -0.20599 | -9.5856 | -0.29297 | 0.050354 | 2.9846 | 57.0145 | 57.6233 | 115.1001 | 124.704 | 2.7374 | 124.736 | 74.2493 | -0.29297 | 124.704 | 2.7374 | 74.2493 | 115.1001 | 124.736 | -124.9329 | -124.9786
1510.6406 | 124.8825 | -60.5026 | 64.2014 | -0.18593 | 0.023578 | 0.022804 | 0.013467 | 0.06718 | 0.0030547 | 0.082698 | -57.6828 | 64.2105 | -60.7452 | -60.6812 | 54.5746 | 13.7741 | -3.5477 | -2.8427 | 64.1968 | -60.7956 | -0.24261 | 0.009155 | 2.8198 | -0.17853 | -9.6268 | -0.29297 | -0.004578 | 3.0624 | 56.955 | 57.6599 | 115.0772 | 124.7131 | 2.8198 | 124.6994 | 74.2767 | -0.29297 | 124.7131 | 2.8198 | 74.2767 | 115.0772 | 124.6994 | -124.9466 | -124.9969
1511.6406 | 124.8962 | -60.5438 | 64.151 | -0.2317 | 0.02315 | 0.019386 | 0.013253 | 0.066753 | 0.0041229 | 0.08227 | -57.7103 | 64.1602 | -60.7727 | -60.6949 | 54.5013 | 13.7009 | -3.598 | -2.8564 | 64.1876 | -60.8231 | -0.22888 | 0.009155 | 2.8336 | -0.15106 | -9.6497 | -0.27924 | 0.036621 | 3.0624 | 56.9458 | 57.6874 | 115.0452 | 124.704 | 2.8336 | 124.7314 | 74.2447 | -0.27924 | 124.704 | 2.8336 | 74.2447 | 115.0452 | 124.7314 | -124.9237 | -124.9741
1512.6562 | 124.9695 | -60.498 | 64.1098 | 0.13451 | 0.021869 | 0.0243 | 0.0091943 | 0.065899 | 0.0036957 | 0.084834 | -57.6965 | 64.0549 | -60.7636 | -60.7132 | 54.3777 | 13.4674 | -3.7903 | -2.6321 | 64.0961 | -60.8231 | -0.2655 | -0.054931 | 2.8015 | -0.21515 | -9.7321 | -0.32501 | -0.013733 | 3.067 | 56.7078 | 57.8659 | 114.8758 | 124.5529 | 2.8015 | 124.5941 | 73.9655 | -0.32501 | 124.5529 | 2.8015 | 73.9655 | 114.8758 | 124.5941 | -124.8734 | -124.9329
1513.6406 | 124.8825 | -60.5301 | 64.1327 | -0.0028231 | 0.023578 | 0.024727 | 0.014108 | 0.068676 | 0.0041229 | 0.085902 | -57.6736 | 64.1602 | -60.7864 | -60.7178 | 54.332 | 13.6368 | -3.6621 | -2.916 | 64.1464 | -60.8368 | -0.25635 | 0.027466 | 2.8564 | -0.18768 | -9.8007 | -0.3067 | 0.013733 | 3.1128 | 56.868 | 57.6141 | 114.8621 | 124.6902 | 2.8564 | 124.6765 | 74.1669 | -0.3067 | 124.6902 | 2.8564 | 74.1669 | 114.8621 | 124.6765 | -124.9191 | -124.9695
1514.6406 | 124.9191 | -60.5576 | 64.1373 | -0.17067 | 0.026782 | 0.02195 | 0.013467 | 0.068248 | 0.0032683 | 0.085261 | -57.6508 | 64.1418 | -60.7819 | -60.7407 | 54.2999 | 13.6047 | -3.6667 | -2.9251 | 64.1647 | -60.8231 | -0.2243 | 0.004578 | 2.9068 | -0.18311 | -9.8373 | -0.2655 | 0.027466 | 3.1311 | 56.8909 | 57.6324 | 114.8575 | 124.6994 | 2.9068 | 124.7223 | 74.1623 | -0.2655 | 124.6994 | 2.9068 | 74.1623 | 114.8575 | 124.7223 | -124.9191 | -124.9603
1515.6406 | 124.9054 | -60.5164 | 64.1556 | -0.14778 | 0.023791 | 0.025368 | 0.014108 | 0.066112 | 0.0034821 | 0.084193 | -57.6324 | 64.1556 | -60.7681 | -60.7086 | 54.2862 | 13.5727 | -3.685 | -2.9526 | 64.1785 | -60.8276 | -0.25177 | 0 | 2.8839 | -0.19226 | -9.8694 | -0.31128 | 0.022888 | 3.1357 | 56.8314 | 57.5638 | 114.8026 | 124.6719 | 2.8839 | 124.6948 | 74.0891 | -0.31128 | 124.6719 | 2.8839 | 74.0891 | 114.8026 | 124.6948 | -124.9237 | -124.9832
1516.6406 | 124.8871 | -60.5438 | 64.1739 | -0.18593 | 0.022937 | 0.022591 | 0.014321 | 0.068676 | 0.0041229 | 0.084407 | -57.6233 | 64.1785 | -60.7636 | -60.7086 | 54.213 | 13.5635 | -3.7262 | -2.9617 | 64.2059 | -60.8231 | -0.21973 | 0.004578 | 2.9205 | -0.16479 | -9.9609 | -0.27924 | 0.032044 | 3.1403 | 56.8176 | 57.5821 | 114.7568 | 124.7223 | 2.9205 | 124.7498 | 74.1074 | -0.27924 | 124.7223 | 2.9205 | 74.1074 | 114.7568 | 124.7498 | -124.9374 | -124.9969
1517.6406 | 124.855 | -60.5484 | 64.1144 | 0.14214 | 0.024859 | 0.021095 | 0.013253 | 0.067821 | 0.0030547 | 0.087184 | -57.6736 | 64.1235 | -60.8047 | -60.7864 | 54.071 | 13.5223 | -3.7857 | -3.0808 | 64.1556 | -60.8231 | -0.25635 | 0.009155 | 2.8748 | -0.23804 | -10.0433 | -0.27466 | 0.041199 | 3.1311 | 56.7627 | 57.4677 | 114.6194 | 124.6719 | 2.8748 | 124.704 | 74.0707 | -0.27466 | 124.6719 | 2.8748 | 74.0707 | 114.6194 | 124.704 | -124.9191 | -124.9374
1518.6406 | 124.8962 | -60.5164 | 64.151 | -0.10201 | 0.022723 | 0.024086 | 0.014962 | 0.067608 | 0.0054047 | 0.085048 | -57.5546 | 64.1693 | -60.7773 | -60.7132 | 54.1122 | 13.5452 | -3.7857 | -3.0121 | 64.1785 | -60.8231 | -0.26093 | 0.018311 | 2.9617 | -0.19684 | -10.0388 | -0.3067 | 0.027466 | 3.2227 | 56.7307 | 57.5043 | 114.6286 | 124.6857 | 2.9617 | 124.6948 | 74.0616 | -0.3067 | 124.6857 | 2.9617 | 74.0616 | 114.6286 | 124.6948 | -124.9283 | -124.9741
1519.6406 | 124.855 | -60.4935 | 64.2014 | -0.010452 | 0.024005 | 0.027504 | 0.012826 | 0.068889 | 0.0041229 | 0.08697 | -57.55 | 64.2014 | -60.7315 | -60.7086 | 54.0344 | 13.4949 | -3.7903 | -3.067 | 64.2288 | -60.8093 | -0.23804 | 0 | 2.9434 | -0.21515 | -10.1669 | -0.31586 | 0.027466 | 3.1815 | 56.7032 | 57.4265 | 114.5279 | 124.6948 | 2.9434 | 124.7223 | 73.9883 | -0.31586 | 124.6948 | 2.9434 | 73.9883 | 114.5279 | 124.7223 | -124.9329 | -125.0107
1520.6406 | 124.8642 | -60.4889 | 64.2059 | 0.035324 | 0.024005 | 0.022804 | 0.014962 | 0.067608 | 0.0045501 | 0.086543 | -57.5317 | 64.1968 | -60.7269 | -60.6903 | 53.9749 | 13.4674 | -3.8223 | -3.0853 | 64.2288 | -60.7956 | -0.23804 | -0.009156 | 2.9572 | -0.20142 | -10.231 | -0.3067 | 0.022888 | 3.1952 | 56.6666 | 57.4036 | 114.4638 | 124.6857 | 2.9572 | 124.7177 | 73.9563 | -0.3067 | 124.6857 | 2.9572 | 73.9563 | 114.4638 | 124.7177 | -124.9329 | -125.0015
1521.6406 | 124.8642 | -60.5026 | 64.2059 | -0.033341 | 0.025287 | 0.0243 | 0.01304 | 0.070385 | 0.0036957 | 0.086757 | -57.5043 | 64.1968 | -60.7407 | -60.6949 | 53.9291 | 13.472 | -3.7994 | -3.067 | 64.2517 | -60.7727 | -0.23804 | -0.009156 | 2.9984 | -0.19226 | -10.2768 | -0.27008 | 0.045776 | 3.2364 | 56.7032 | 57.4356 | 114.4318 | 124.6994 | 2.9984 | 124.7543 | 73.9746 | -0.27008 | 124.6994 | 2.9984 | 73.9746 | 114.4318 | 124.7543 | -124.9466 | -124.9786
1522.6406 | 124.8779 | -60.5026 | 64.1922 | 0.13451 | 0.023791 | 0.026436 | 0.014749 | 0.069957 | 0.0045501 | 0.086116 | -57.5317 | 64.1922 | -60.759 | -60.7452 | 53.8559 | 13.4674 | -3.8223 | -3.0991 | 64.2197 | -60.7773 | -0.25635 | 0 | 2.9709 | -0.24261 | -10.3363 | -0.27466 | 0.027466 | 3.2272 | 56.6803 | 57.4036 | 114.3585 | 124.6948 | 2.9709 | 124.7223 | 73.97 | -0.27466 | 124.6948 | 2.9709 | 73.97 | 114.3585 | 124.7223 | -124.9512 | -124.9695
1523.6406 | 124.9008 | -60.4431 | 64.2334 | -0.010452 | 0.02785 | 0.025795 | 0.014535 | 0.066753 | 0.0026275 | 0.083339 | -57.4036 | 64.2426 | -60.6857 | -60.6216 | 53.8925 | 13.5223 | -3.8315 | -3.0121 | 64.2334 | -60.7544 | -0.24262 | 0.009156 | 3.0396 | -0.17853 | -10.3409 | -0.31128 | 0 | 3.2822 | 56.6116 | 57.431 | 114.3356 | 124.6857 | 3.0396 | 124.6765 | 73.9655 | -0.31128 | 124.6857 | 3.0396 | 73.9655 | 114.3356 | 124.6765 | -124.9191 | -124.9878
1524.6406 | 124.8734 | -60.4477 | 64.2288 | 0.027695 | 0.026996 | 0.027504 | 0.013253 | 0.069957 | 0.0032683 | 0.086757 | -57.399 | 64.2426 | -60.6903 | -60.6628 | 53.8055 | 13.4674 | -3.8132 | -3.0624 | 64.2746 | -60.7452 | -0.24262 | 0.013733 | 3.0487 | -0.21515 | -10.4233 | -0.29755 | 0.045776 | 3.2913 | 56.6345 | 57.3853 | 114.2532 | 124.6902 | 3.0487 | 124.7223 | 73.9151 | -0.29755 | 124.6902 | 3.0487 | 73.9151 | 114.2532 | 124.7223 | -124.9191 | -124.9741
1525.6406 | 124.8367 | -60.4431 | 64.2334 | 0.020065 | 0.025287 | 0.026436 | 0.016244 | 0.067821 | 0.0039093 | 0.085475 | -57.3944 | 64.2517 | -60.6628 | -60.6491 | 53.7598 | 13.4537 | -3.8269 | -3.0762 | 64.27 | -60.7544 | -0.21973 | 0.018311 | 3.0487 | -0.20599 | -10.4736 | -0.31128 | 0.036622 | 3.2684 | 56.6162 | 57.3669 | 114.2029 | 124.6948 | 3.0487 | 124.7131 | 73.8968 | -0.31128 | 124.6948 | 3.0487 | 73.8968 | 114.2029 | 124.7131 | -124.8962 | -124.9878
1526.6406 | 124.823 | -60.4385 | 64.2609 | 0.012436 | 0.0255 | 0.022377 | 0.012612 | 0.067821 | 0.0054047 | 0.08697 | -57.3853 | 64.2838 | -60.6903 | -60.6857 | 53.6865 | 13.3804 | -3.7949 | -3.1448 | 64.27 | -60.7407 | -0.25177 | 0.022888 | 3.0533 | -0.24719 | -10.5743 | -0.30212 | 0.009156 | 3.3051 | 56.6437 | 57.2937 | 114.1251 | 124.7223 | 3.0533 | 124.7086 | 73.819 | -0.30212 | 124.7223 | 3.0533 | 73.819 | 114.1251 | 124.7086 | -124.9512 | -125.0015
1527.6562 | 124.91 | -60.3973 | 64.2426 | 0.12688 | 0.022723 | 0.02195 | 0.0044945 | 0.065471 | 0.0064727 | 0.086329 | -57.3349 | 64.1556 | -60.6491 | -60.5942 | 53.7048 | 13.5178 | -3.9413 | -3.0258 | 64.27 | -60.6766 | -0.25177 | -0.086975 | 3.0624 | -0.19684 | -10.5377 | -0.27924 | 0.027466 | 3.3142 | 56.456 | 57.3715 | 114.1022 | 124.5529 | 3.0624 | 124.6674 | 73.9151 | -0.27924 | 124.5529 | 3.0624 | 73.9151 | 114.1022 | 124.6674 | -124.8917 | -124.9191
1528.6406 | 124.8184 | -60.4202 | 64.2654 | -0.033341 | 0.02315 | 0.023232 | 0.014108 | 0.067821 | 0.0045501 | 0.085048 | -57.3486 | 64.2838 | -60.6674 | -60.6537 | 53.5538 | 13.4308 | -3.7903 | -3.1174 | 64.27 | -60.6995 | -0.24719 | 0.01831 | 3.0716 | -0.23346 | -10.7117 | -0.27924 | 0.004578 | 3.3188 | 56.6299 | 57.3029 | 113.974 | 124.704 | 3.0716 | 124.6902 | 73.851 | -0.27924 | 124.704 | 3.0716 | 73.851 | 113.974 | 124.6902 | -124.9329 | -124.9649
1529.6406 | 124.9832 | -60.3607 | 64.238 | 0.13451 | 0.022937 | 0.029427 | 0.0087671 | 0.064403 | 0.0028411 | 0.086116 | -57.2571 | 64.1693 | -60.6491 | -60.5667 | 53.627 | 13.5406 | -4.0192 | -2.9984 | 64.2471 | -60.6491 | -0.28839 | -0.068664 | 3.1036 | -0.20599 | -10.611 | -0.28839 | 0.009155 | 3.392 | 56.3416 | 57.3624 | 113.9877 | 124.53 | 3.1036 | 124.6078 | 73.9014 | -0.28839 | 124.53 | 3.1036 | 73.9014 | 113.9877 | 124.6078 | -124.8871 | -124.8871
1530.6406 | 124.8642 | -60.4019 | 64.2654 | -0.010452 | 0.024646 | 0.023872 | 0.017739 | 0.065899 | 0.0060455 | 0.083766 | -57.2617 | 64.3066 | -60.6308 | -60.6079 | 53.4897 | 13.3804 | -3.8589 | -3.1174 | 64.2746 | -60.7269 | -0.22888 | 0.041199 | 3.1403 | -0.20599 | -10.7758 | -0.32501 | 0.009155 | 3.3691 | 56.543 | 57.2845 | 113.8916 | 124.7086 | 3.1403 | 124.6765 | 73.7823 | -0.32501 | 124.7086 | 3.1403 | 73.7823 | 113.8916 | 124.6765 | -124.8962 | -124.9924
1531.6406 | 124.9146 | -60.4202 | 64.2975 | 0.050583 | 0.026141 | 0.025795 | 0.014749 | 0.068676 | 0.0039093 | 0.087184 | -57.2525 | 64.2975 | -60.6583 | -60.6628 | 53.4119 | 13.4125 | -4.0283 | -3.4882 | 64.2426 | -60.7269 | -0.23804 | 0 | 3.1677 | -0.24262 | -10.8856 | -0.3067 | -0.054931 | 3.4058 | 56.3919 | 56.9321 | 113.8321 | 124.7177 | 3.1677 | 124.6628 | 73.8327 | -0.3067 | 124.7177 | 3.1677 | 73.8327 | 113.8321 | 124.6628 | -124.9557 | -125.0244
1532.6406 | 124.9237 | -60.3424 | 64.2838 | 0.073471 | 0.021441 | 0.019386 | 0.0064171 | 0.066967 | 0.0051911 | 0.086116 | -57.2296 | 64.183 | -60.6216 | -60.585 | 53.4576 | 13.4811 | -4.01 | -3.0304 | 64.2838 | -60.6445 | -0.27924 | -0.10071 | 3.1128 | -0.24262 | -10.8261 | -0.30212 | 0 | 3.392 | 56.3324 | 57.312 | 113.8 | 124.5255 | 3.1128 | 124.6262 | 73.8235 | -0.30212 | 124.5255 | 3.1128 | 73.8235 | 113.8 | 124.6262 | -124.9054 | -124.9283
1533.6406 | 124.8413 | -60.4019 | 64.2975 | 0.11162 | 0.026141 | 0.033058 | 0.016244 | 0.06718 | 0.0049773 | 0.089106 | -57.193 | 64.3021 | -60.6262 | -60.6033 | 53.3569 | 13.3942 | -3.891 | -3.1357 | 64.2975 | -60.6949 | -0.2243 | 0.004578 | 3.2089 | -0.20142 | -10.9406 | -0.29297 | 0 | 3.4332 | 56.5109 | 57.2662 | 113.7589 | 124.704 | 3.2089 | 124.6994 | 73.7961 | -0.29297 | 124.704 | 3.2089 | 73.7961 | 113.7589 | 124.6994 | -124.9237 | -124.9924
1534.6562 | 124.91 | -60.3287 | 64.2975 | -0.24696 | 0.022296 | 0.02665 | 0.01069 | 0.066539 | 0.0034821 | 0.086116 | -57.1426 | 64.238 | -60.6079 | -60.5164 | 53.4073 | 13.4949 | -3.8818 | -2.9984 | 64.2975 | -60.6491 | -0.27924 | -0.059509 | 3.186 | -0.18768 | -10.8902 | -0.32044 | 0 | 3.4653 | 56.4468 | 57.3303 | 113.736 | 124.5667 | 3.186 | 124.6262 | 73.8235 | -0.32044 | 124.5667 | 3.186 | 73.8235 | 113.736 | 124.6262 | -124.9054 | -124.9466
1535.6406 | 124.8962 | -60.3745 | 64.3112 | 0.10399 | 0.025928 | 0.02729 | 0.017953 | 0.066326 | 0.0045501 | 0.087611 | -57.1426 | 64.2929 | -60.5988 | -60.5942 | 53.2745 | 13.3713 | -3.891 | -3.1311 | 64.3524 | -60.6583 | -0.2243 | -0.01831 | 3.2318 | -0.21973 | -11.0367 | -0.28381 | 0.041199 | 3.4561 | 56.4835 | 57.2433 | 113.649 | 124.6674 | 3.2318 | 124.7269 | 73.7457 | -0.28381 | 124.6674 | 3.2318 | 73.7457 | 113.649 | 124.7269 | -124.91 | -124.9695
1536.6406 | 124.8505 | -60.3561 | 64.3524 | 0.065841 | 0.026141 | 0.026863 | 0.017312 | 0.065258 | 0.0060455 | 0.087825 | -57.1518 | 64.2975 | -60.6537 | -60.6171 | 52.9449 | 13.0829 | -3.6255 | -2.8656 | 64.325 | -60.6583 | -0.29755 | -0.054932 | 3.2043 | -0.26092 | -11.4075 | -0.30212 | -0.027466 | 3.5019 | 56.7307 | 57.4905 | 113.3011 | 124.6536 | 3.2043 | 124.6811 | 73.439 | -0.30212 | 124.6536 | 3.2043 | 73.439 | 113.3011 | 124.6811 | -125.0061 | -125.0107
1537.6406 | 124.9466 | -60.3149 | 64.2838 | 0.14214 | 0.024646 | 0.021095 | 0.010262 | 0.067821 | 0.0054047 | 0.088466 | -57.0602 | 64.2105 | -60.5942 | -60.5026 | 53.2608 | 13.4628 | -4.0558 | -3.035 | 64.3021 | -60.5942 | -0.27924 | -0.073242 | 3.2547 | -0.18768 | -11.0229 | -0.27924 | 0.018311 | 3.5339 | 56.2592 | 57.28 | 113.5757 | 124.5255 | 3.2547 | 124.617 | 73.7778 | -0.27924 | 124.5255 | 3.2547 | 73.7778 | 113.5757 | 124.617 | -124.8779 | -124.8779
1538.6406 | 124.8688 | -60.3333 | 64.2975 | 0.19554 | 0.026355 | 0.02665 | 0.017526 | 0.064617 | 0.0043365 | 0.087184 | -57.0786 | 64.3204 | -60.5896 | -60.5713 | 53.1235 | 13.353 | -3.891 | -3.1357 | 64.325 | -60.6491 | -0.25635 | 0.022889 | 3.2547 | -0.23804 | -11.174 | -0.31586 | 0.027466 | 3.511 | 56.4423 | 57.1976 | 113.4567 | 124.6536 | 3.2547 | 124.6582 | 73.6862 | -0.31586 | 124.6536 | 3.2547 | 73.6862 | 113.4567 | 124.6582 | -124.8871 | -124.9466
1539.6406 | 124.9512 | -60.2829 | 64.3158 | 0.073471 | 0.023364 | 0.030068 | 0.01069 | 0.065044 | 0.0058319 | 0.088893 | -57.0328 | 64.2288 | -60.5896 | -60.5072 | 53.1509 | 13.3942 | -4.0283 | -3.0304 | 64.3112 | -60.5713 | -0.3067 | -0.086975 | 3.2501 | -0.2243 | -11.1649 | -0.28839 | -0.004578 | 3.5568 | 56.2546 | 57.2525 | 113.4338 | 124.5117 | 3.2501 | 124.5941 | 73.6771 | -0.28839 | 124.5117 | 3.2501 | 73.6771 | 113.4338 | 124.5941 | -124.9054 | -124.8871
1540.6406 | 124.9557 | -60.3058 | 64.3387 | 0.17265 | 0.025287 | 0.030495 | 0.017526 | 0.06483 | 0.0043365 | 0.087825 | -56.9824 | 64.3433 | -60.5438 | -60.4843 | 53.0869 | 13.4079 | -4.0146 | -3.0487 | 64.3616 | -60.6171 | -0.23804 | 0.004578 | 3.3234 | -0.17853 | -11.2518 | -0.31128 | 0.022888 | 3.5614 | 56.2912 | 57.2571 | 113.3926 | 124.649 | 3.3234 | 124.6674 | 73.7137 | -0.31128 | 124.649 | 3.3234 | 73.7137 | 113.3926 | 124.6674 | -124.8825 | -124.9557
1541.6406 | 124.942 | -60.2692 | 64.3341 | 0.14976 | 0.024646 | 0.027077 | 0.014749 | 0.065899 | 0.0073273 | 0.088038 | -56.9595 | 64.3524 | -60.553 | -60.4843 | 53.0548 | 13.4354 | -4.0329 | -3.0579 | 64.3204 | -60.585 | -0.28381 | 0.018311 | 3.3096 | -0.21515 | -11.2793 | -0.31586 | -0.013732 | 3.5934 | 56.2363 | 57.2113 | 113.324 | 124.6216 | 3.3096 | 124.5895 | 73.7045 | -0.31586 | 124.6216 | 3.3096 | 73.7045 | 113.324 | 124.5895 | -124.8871 | -124.9191
1542.6406 | 124.9283 | -60.2554 | 64.3524 | 0.11162 | 0.02315 | 0.023018 | 0.011331 | 0.065471 | 0.0043365 | 0.088466 | -56.9458 | 64.2975 | -60.5255 | -60.4843 | 53.0136 | 13.4171 | -4.0283 | -3.0487 | 64.3524 | -60.553 | -0.27008 | -0.054932 | 3.3096 | -0.22888 | -11.3388 | -0.29755 | 0 | 3.5797 | 56.2271 | 57.2067 | 113.269 | 124.5529 | 3.3096 | 124.6078 | 73.6725 | -0.29755 | 124.5529 | 3.3096 | 73.6725 | 113.269 | 124.6078 | -124.8779 | -124.9054
1543.6406 | 124.8596 | -60.2829 | 64.3707 | 0.18028 | 0.027637 | 0.025795 | 0.018594 | 0.064617 | 0.0051911 | 0.087825 | -56.9504 | 64.3616 | -60.5621 | -60.5164 | 52.8854 | 13.3163 | -3.9825 | -3.1357 | 64.3707 | -60.6033 | -0.27924 | -0.009156 | 3.3325 | -0.23346 | -11.4853 | -0.32043 | 0 | 3.6118 | 56.3004 | 57.1472 | 113.1683 | 124.6445 | 3.3325 | 124.6536 | 73.5992 | -0.32043 | 124.6445 | 3.3325 | 73.5992 | 113.1683 | 124.6536 | -124.9329 | -124.9741
1544.6562 | 124.8322 | -60.2325 | 64.4485 | -0.22408 | 0.026568 | 0.026009 | 0.013253 | 0.064403 | 0.0058319 | 0.089534 | -56.868 | 64.4348 | -60.4706 | -60.3745 | 53.2288 | 13.4125 | -4.1061 | -3.1036 | 64.4348 | -60.553 | -0.23804 | -0.013733 | 3.3646 | -0.14191 | -11.2198 | -0.32044 | -0.013733 | 3.6026 | 56.1264 | 57.1289 | 113.4613 | 124.6674 | 3.3646 | 124.6674 | 73.645 | -0.32044 | 124.6674 | 3.3646 | 73.645 | 113.4613 | 124.6674 | -124.9191 | -125.0015
1545.6406 | 124.9603 | -60.228 | 64.3845 | 0.21843 | 0.023791 | 0.027931 | 0.017098 | 0.065471 | 0.0068999 | 0.087825 | -56.813 | 64.3799 | -60.4935 | -60.4156 | 52.8946 | 13.3804 | -4.1565 | -3.0808 | 64.357 | -60.5301 | -0.2655 | -0.004577 | 3.4149 | -0.18768 | -11.4899 | -0.30212 | -0.027465 | 3.6804 | 56.0715 | 57.1472 | 113.1226 | 124.6078 | 3.4149 | 124.585 | 73.6084 | -0.30212 | 124.6078 | 3.4149 | 73.6084 | 113.1226 | 124.585 | -124.8779 | -124.9146
1546.6406 | 124.9741 | -60.2005 | 64.4211 | 0.79826 | 0.023791 | 0.021309 | 0.013253 | 0.06419 | 0.0056183 | 0.089961 | -56.7078 | 64.357 | -60.466 | -60.3561 | 52.8854 | 13.4216 | -4.1702 | -3.0533 | 64.3799 | -60.5026 | -0.2655 | -0.064087 | 3.4927 | -0.15564 | -11.5356 | -0.30213 | -0.041199 | 3.7582 | 56.0303 | 57.1472 | 113.0859 | 124.5575 | 3.4927 | 124.5804 | 73.6221 | -0.30213 | 124.5575 | 3.4927 | 73.6221 | 113.0859 | 124.5804 | -124.8871 | -124.9237
1547.6406 | 124.9466 | -60.228 | 64.3936 | 0.85167 | 0.025287 | 0.028786 | 0.012612 | 0.06419 | 0.0051911 | 0.087184 | -56.7032 | 64.3433 | -60.4797 | -60.379 | 52.8305 | 13.4216 | -4.1748 | -3.0762 | 64.3753 | -60.5164 | -0.25177 | -0.050354 | 3.5248 | -0.15106 | -11.5631 | -0.28839 | -0.018311 | 3.7766 | 56.0532 | 57.1518 | 113.0585 | 124.5712 | 3.5248 | 124.6033 | 73.6496 | -0.28839 | 124.5712 | 3.5248 | 73.6496 | 113.0585 | 124.6033 | -124.8734 | -124.91
1548.6406 | 124.9557 | -60.1959 | 64.3707 | 0.43205 | 0.02315 | 0.022377 | 0.014535 | 0.063762 | 0.0047637 | 0.088252 | -56.6757 | 64.325 | -60.4568 | -60.3699 | 52.7756 | 13.4033 | -4.1885 | -3.0716 | 64.3753 | -60.5026 | -0.26093 | -0.045777 | 3.5202 | -0.17395 | -11.5952 | -0.3067 | 0.004577 | 3.7811 | 56.0074 | 57.1243 | 112.9715 | 124.5209 | 3.5202 | 124.5712 | 73.5992 | -0.3067 | 124.5209 | 3.5202 | 73.5992 | 112.9715 | 124.5712 | -124.8276 | -124.8734
1549.6406 | 124.9786 | -60.1822 | 64.3982 | -0.048599 | 0.023791 | 0.027504 | 0.015389 | 0.06419 | 0.0054047 | 0.087825 | -56.7123 | 64.3341 | -60.4385 | -60.3653 | 52.7069 | 13.3759 | -4.216 | -3.0808 | 64.3662 | -60.4935 | -0.25635 | -0.064087 | 3.4698 | -0.18311 | -11.6913 | -0.31128 | -0.032043 | 3.7262 | 55.9662 | 57.1014 | 112.8891 | 124.5163 | 3.4698 | 124.5483 | 73.558 | -0.31128 | 124.5163 | 3.4698 | 73.558 | 112.8891 | 124.5483 | -124.8367 | -124.8917
1550.6406 | 124.9557 | -60.1685 | 64.4119 | 0.15739 | 0.024859 | 0.023872 | 0.015389 | 0.063549 | 0.0043365 | 0.088038 | -56.6574 | 64.389 | -60.466 | -60.3424 | 52.6657 | 13.3667 | -4.2068 | -3.1036 | 64.4073 | -60.4843 | -0.29755 | -0.022888 | 3.511 | -0.17395 | -11.7462 | -0.31586 | -0.004577 | 3.8086 | 55.9616 | 57.0648 | 112.8342 | 124.5575 | 3.511 | 124.5758 | 73.5352 | -0.31586 | 124.5575 | 3.511 | 73.5352 | 112.8342 | 124.5758 | -124.8779 | -124.8962
1551.6406 | 124.942 | -60.1685 | 64.4394 | 0.18791 | 0.023791 | 0.025581 | 0.015176 | 0.065044 | 0.0041229 | 0.087611 | -56.6345 | 64.3707 | -60.4477 | -60.3287 | 52.6566 | 13.4079 | -4.1702 | -3.1174 | 64.4028 | -60.4385 | -0.27924 | -0.068664 | 3.5339 | -0.16022 | -11.7828 | -0.27008 | -0.036621 | 3.8132 | 55.9982 | 57.0511 | 112.825 | 124.5392 | 3.5339 | 124.5712 | 73.5764 | -0.27008 | 124.5392 | 3.5339 | 73.5764 | 112.825 | 124.5712 | -124.8871 | -124.8779
1552.6406 | 124.9557 | -60.1593 | 64.3799 | 0.15739 | 0.025287 | 0.025368 | 0.012826 | 0.065471 | 0.0058319 | 0.088038 | -56.6254 | 64.3478 | -60.4477 | -60.3516 | 52.5787 | 13.3484 | -4.2068 | -3.1036 | 64.357 | -60.466 | -0.28839 | -0.032044 | 3.5339 | -0.19226 | -11.8011 | -0.3067 | -0.022888 | 3.8223 | 55.9525 | 57.0557 | 112.738 | 124.5071 | 3.5339 | 124.5163 | 73.5077 | -0.3067 | 124.5071 | 3.5339 | 73.5077 | 112.738 | 124.5163 | -124.8276 | -124.8459
1553.6406 | 124.9191 | -60.1822 | 64.4211 | 0.14214 | 0.024859 | 0.029854 | 0.012185 | 0.06184 | 0.0066863 | 0.089747 | -56.6208 | 64.3433 | -60.466 | -60.379 | 52.5009 | 13.2706 | -4.1794 | -3.1586 | 64.3982 | -60.4889 | -0.28381 | -0.07782 | 3.5614 | -0.19684 | -11.9202 | -0.3067 | -0.022889 | 3.8452 | 56.0028 | 57.0236 | 112.6831 | 124.5255 | 3.5614 | 124.5804 | 73.4528 | -0.3067 | 124.5255 | 3.5614 | 73.4528 | 112.6831 | 124.5804 | -124.8871 | -124.91
1554.6406 | 124.9283 | -60.1822 | 64.4348 | 0.16502 | 0.024859 | 0.026863 | 0.01304 | 0.06419 | 0.0051911 | 0.088679 | -56.6162 | 64.3387 | -60.4156 | -60.3561 | 52.4597 | 13.3255 | -4.1931 | -3.1494 | 64.4119 | -60.466 | -0.23346 | -0.09613 | 3.566 | -0.17395 | -11.9751 | -0.28381 | -0.022888 | 3.7994 | 55.9891 | 57.0328 | 112.6419 | 124.5209 | 3.566 | 124.5941 | 73.5077 | -0.28381 | 124.5209 | 3.566 | 73.5077 | 112.6419 | 124.5941 | -124.8505 | -124.9008
1555.6406 | 124.91 | -60.1685 | 64.4623 | 0.08873 | 0.024219 | 0.028359 | 0.014962 | 0.062908 | 0.0036957 | 0.090175 | -56.575 | 64.3616 | -60.4156 | -60.3653 | 52.4094 | 13.3118 | -4.184 | -3.154 | 64.4348 | -60.434 | -0.24719 | -0.10071 | 3.5934 | -0.19684 | -12.0529 | -0.2655 | -0.027466 | 3.8406 | 55.9845 | 57.0145 | 112.5778 | 124.53 | 3.5934 | 124.6033 | 73.4802 | -0.2655 | 124.53 | 3.5934 | 73.4802 | 112.5778 | 124.6033 | -124.8779 | -124.8962
1556.6406 | 124.9191 | -60.1227 | 64.4577 | 0.20317 | 0.025714 | 0.024941 | 0.015817 | 0.062053 | 0.0064727 | 0.089106 | -56.5338 | 64.3753 | -60.3973 | -60.3424 | 52.3727 | 13.3118 | -4.1656 | -3.1174 | 64.4394 | -60.4111 | -0.27466 | -0.082398 | 3.5889 | -0.21973 | -12.085 | -0.28839 | -0.018311 | 3.8635 | 55.957 | 57.0053 | 112.4954 | 124.498 | 3.5889 | 124.5621 | 73.4344 | -0.28839 | 124.498 | 3.5889 | 73.4344 | 112.4954 | 124.5621 | -124.855 | -124.8688
1557.6406 | 124.9786 | -60.1181 | 64.444 | -0.33089 | 0.021869 | 0.026436 | 0.012826 | 0.060985 | 0.0047637 | 0.088679 | -56.456 | 64.3799 | -60.4019 | -60.2417 | 52.3819 | 13.3347 | -4.1428 | -3.0121 | 64.4348 | -60.3836 | -0.28381 | -0.064087 | 3.6621 | -0.1236 | -12.0621 | -0.2655 | -0.009156 | 3.9459 | 55.9753 | 57.106 | 112.5 | 124.498 | 3.6621 | 124.5529 | 73.4528 | -0.2655 | 124.498 | 3.6621 | 73.4528 | 112.5 | 124.5529 | -124.8459 | -124.8276
1558.6406 | 124.942 | -60.1273 | 64.4577 | 0.18028 | 0.024646 | 0.025581 | 0.017098 | 0.062908 | 0.0047637 | 0.088893 | -56.4606 | 64.3616 | -60.4019 | -60.3012 | 52.2949 | 13.3209 | -4.1977 | -3.0853 | 64.4119 | -60.4156 | -0.27466 | -0.096131 | 3.6667 | -0.17395 | -12.1628 | -0.28839 | -0.045777 | 3.9413 | 55.9296 | 57.0419 | 112.4222 | 124.4888 | 3.6667 | 124.5392 | 73.4482 | -0.28839 | 124.4888 | 3.6667 | 73.4482 | 112.4222 | 124.5392 | -124.8596 | -124.8734
1559.6406 | 124.8871 | -60.1227 | 64.4714 | 0.17265 | 0.024859 | 0.027077 | 0.014321 | 0.062053 | 0.0071137 | 0.089106 | -56.456 | 64.3936 | -60.3745 | -60.3195 | 52.2308 | 13.2889 | -4.1199 | -3.1174 | 64.444 | -60.3973 | -0.25177 | -0.07782 | 3.6667 | -0.19684 | -12.2406 | -0.27466 | -0.027466 | 3.9185 | 56.0028 | 57.0053 | 112.3535 | 124.5163 | 3.6667 | 124.5667 | 73.4116 | -0.27466 | 124.5163 | 3.6667 | 73.4116 | 112.3535 | 124.5667 | -124.8459 | -124.8688
1560.6406 | 124.9191 | -60.1364 | 64.476 | -0.0028231 | 0.024646 | 0.022804 | 0.01368 | 0.062267 | 0.0062591 | 0.089747 | -56.2958 | 64.3845 | -60.3836 | -60.3516 | 52.1347 | 13.2385 | -4.1382 | -3.0945 | 64.4257 | -60.4385 | -0.24719 | -0.091553 | 3.8406 | -0.21515 | -12.3413 | -0.30212 | -0.050354 | 4.0878 | 55.9982 | 57.0419 | 112.2711 | 124.5209 | 3.8406 | 124.5621 | 73.3749 | -0.30212 | 124.5209 | 3.8406 | 73.3749 | 112.2711 | 124.5621 | -124.8596 | -124.9146
1561.6406 | 124.9191 | -60.1227 | 64.4714 | -1.2083 | 0.02251 | 0.027077 | 0.0087671 | 0.061412 | 0.0039093 | 0.090388 | -56.6071 | 64.3799 | -60.4065 | -60.3149 | 52.0889 | 13.2431 | -4.1702 | -3.1265 | 64.4531 | -60.4111 | -0.28381 | -0.091553 | 3.5156 | -0.19226 | -12.3825 | -0.28839 | -0.018311 | 3.7994 | 55.9525 | 56.9962 | 112.2116 | 124.5026 | 3.5156 | 124.5758 | 73.3658 | -0.28839 | 124.5026 | 3.5156 | 73.3658 | 112.2116 | 124.5758 | -124.8779 | -124.8825
1562.6406 | 124.8734 | -60.1135 | 64.5401 | -0.27748 | 0.027209 | 0.027077 | 0.019021 | 0.062908 | 0.0041229 | 0.088893 | -56.3965 | 64.4989 | -60.3607 | -60.3104 | 52.0477 | 13.1882 | -3.9551 | -3.1265 | 64.5218 | -60.3973 | -0.24719 | -0.041199 | 3.717 | -0.19684 | -12.4924 | -0.28381 | -0.01831 | 3.9642 | 56.1584 | 56.987 | 112.1613 | 124.6124 | 3.717 | 124.6353 | 73.3017 | -0.28381 | 124.6124 | 3.717 | 73.3017 | 112.1613 | 124.6353 | -124.9008 | -124.9374
1563.6406 | 124.9054 | -60.1318 | 64.5081 | -0.063858 | 0.024219 | 0.024941 | 0.012612 | 0.064617 | 0.0068999 | 0.090815 | -56.4606 | 64.357 | -60.4065 | -60.3241 | 52.0111 | 13.2111 | -4.1107 | -3.1357 | 64.4714 | -60.3882 | -0.27466 | -0.15106 | 3.6713 | -0.19226 | -12.4969 | -0.25635 | -0.036621 | 3.9459 | 56.0211 | 56.9962 | 112.1429 | 124.4888 | 3.6713 | 124.6033 | 73.3429 | -0.25635 | 124.4888 | 3.6713 | 73.3429 | 112.1429 | 124.6033 | -124.9146 | -124.8962
1564.6406 | 124.9191 | -60.141 | 64.4714 | 0.08873 | 0.023791 | 0.028999 | 0.011971 | 0.062053 | 0.0071137 | 0.088893 | -56.3873 | 64.3707 | -60.3928 | -60.3378 | 51.9424 | 13.1927 | -4.184 | -3.1586 | 64.4623 | -60.4065 | -0.25177 | -0.10071 | 3.7537 | -0.19684 | -12.529 | -0.2655 | -0.009156 | 4.0054 | 55.957 | 56.9824 | 112.0834 | 124.5117 | 3.7537 | 124.6033 | 73.3337 | -0.2655 | 124.5117 | 3.7537 | 73.3337 | 112.0834 | 124.6033 | -124.8642 | -124.8779
1565.6406 | 124.9283 | -60.1135 | 64.5035 | 0.10399 | 0.02315 | 0.024513 | 0.014108 | 0.062053 | 0.0049773 | 0.089747 | -56.3507 | 64.3936 | -60.379 | -60.3149 | 51.9058 | 13.179 | -4.1473 | -3.1265 | 64.444 | -60.3882 | -0.2655 | -0.10986 | 3.7628 | -0.20142 | -12.5977 | -0.27466 | -0.059509 | 4.0283 | 55.9662 | 56.987 | 112.0193 | 124.5071 | 3.7628 | 124.5575 | 73.2925 | -0.27466 | 124.5071 | 3.7628 | 73.2925 | 112.0193 | 124.5575 | -124.8825 | -124.8917
1566.6406 | 124.91 | -60.1135 | 64.5309 | -0.094376 | 0.025073 | 0.024727 | 0.011758 | 0.062908 | 0.0077545 | 0.090175 | -56.337 | 64.4302 | -60.3607 | -60.2875 | 51.8967 | 13.1882 | -4.1656 | -3.1357 | 64.4714 | -60.347 | -0.24719 | -0.10071 | 3.7766 | -0.17395 | -12.6343 | -0.23346 | -0.059509 | 4.0237 | 55.9479 | 56.9778 | 112.0102 | 124.5438 | 3.7766 | 124.585 | 73.3017 | -0.23346 | 124.5438 | 3.7766 | 73.3017 | 112.0102 | 124.585 | -124.8917 | -124.8779
1567.6406 | 124.9786 | -60.1089 | 64.5081 | -0.10963 | 0.023364 | 0.023232 | 0.012399 | 0.061199 | 0.0047637 | 0.091029 | -56.2454 | 64.4165 | -60.3378 | -60.1959 | 51.8784 | 13.1058 | -3.6484 | -2.9617 | 64.5081 | -60.3333 | -0.22888 | -0.091553 | 3.8635 | -0.086975 | -12.6297 | -0.2243 | 0 | 4.0924 | 56.4606 | 57.1472 | 111.9873 | 124.5255 | 3.8635 | 124.617 | 73.2147 | -0.2243 | 124.5255 | 3.8635 | 73.2147 | 111.9873 | 124.617 | -124.8459 | -124.8413
1568.6406 | 124.9557 | -60.0677 | 64.5035 | -0.10201 | 0.024859 | 0.023659 | 0.011758 | 0.061626 | 0.0081817 | 0.090175 | -56.2546 | 64.4257 | -60.379 | -60.2417 | 51.8051 | 13.1744 | -4.1885 | -3.067 | 64.4669 | -60.347 | -0.31128 | -0.07782 | 3.8132 | -0.17395 | -12.6984 | -0.27924 | -0.036621 | 4.1244 | 55.8792 | 57.0007 | 111.8729 | 124.4934 | 3.8132 | 124.5346 | 73.2422 | -0.27924 | 124.4934 | 3.8132 | 73.2422 | 111.8729 | 124.5346 | -124.8825 | -124.8505
1569.6406 | 124.9466 | -60.0677 | 64.5355 | -0.071488 | 0.023791 | 0.024941 | 0.013253 | 0.060131 | 0.0056183 | 0.090815 | -56.2088 | 64.4257 | -60.3333 | -60.2234 | 51.7685 | 13.1653 | -4.1748 | -3.0396 | 64.4806 | -60.3424 | -0.2655 | -0.10986 | 3.8589 | -0.15564 | -12.767 | -0.27466 | -0.054931 | 4.1245 | 55.8929 | 57.0282 | 111.8362 | 124.4934 | 3.8589 | 124.5483 | 73.233 | -0.27466 | 124.4934 | 3.8589 | 73.233 | 111.8362 | 124.5483 | -124.8688 | -124.8779
1570.6406 | 124.9649 | -60.0906 | 64.4989 | -0.11726 | 0.024005 | 0.024727 | 0.014108 | 0.05949 | 0.0060455 | 0.091456 | -56.2454 | 64.3982 | -60.3928 | -60.2417 | 51.6907 | 13.1424 | -4.1748 | -3.0441 | 64.4348 | -60.3424 | -0.30212 | -0.10071 | 3.8452 | -0.15106 | -12.8082 | -0.25177 | -0.064087 | 4.1473 | 55.9158 | 57.0465 | 111.7813 | 124.4888 | 3.8452 | 124.5255 | 73.233 | -0.25177 | 124.4888 | 3.8452 | 73.233 | 111.7813 | 124.5255 | -124.8917 | -124.8413
1571.6406 | 124.9237 | -60.0723 | 64.4989 | -0.025711 | 0.023791 | 0.025795 | 0.013253 | 0.059917 | 0.0083953 | 0.089534 | -56.2408 | 64.4257 | -60.3561 | -60.2646 | 51.6174 | 13.1058 | -4.0924 | -3.0716 | 64.4623 | -60.3516 | -0.28381 | -0.073242 | 3.8315 | -0.19226 | -12.8815 | -0.27923 | -0.036621 | 4.1153 | 55.9799 | 57.0007 | 111.6898 | 124.498 | 3.8315 | 124.5346 | 73.1781 | -0.27923 | 124.498 | 3.8315 | 73.1781 | 111.6898 | 124.5346 | -124.855 | -124.8505
1572.6406 | 124.8596 | -60.1089 | 64.5584 | -0.24696 | 0.025073 | 0.023445 | 0.018167 | 0.060772 | 0.0058319 | 0.089961 | -56.1401 | 64.5035 | -60.3333 | -60.2554 | 51.5579 | 13.0325 | -3.9734 | -3.0762 | 64.5126 | -60.3745 | -0.2243 | -0.054932 | 3.9688 | -0.14648 | -13.0005 | -0.2655 | -0.045777 | 4.1931 | 56.1356 | 57.0328 | 111.6669 | 124.6124 | 3.9688 | 124.6216 | 73.1415 | -0.2655 | 124.6124 | 3.9688 | 73.1415 | 111.6669 | 124.6216 | -124.8917 | -124.9329
1573.6406 | 124.9557 | -60.0723 | 64.5309 | -0.086746 | 0.022937 | 0.022591 | 0.012399 | 0.060985 | 0.0060455 | 0.091456 | -56.1493 | 64.4211 | -60.3424 | -60.2051 | 51.5808 | 13.0875 | -4.1245 | -2.9846 | 64.4897 | -60.3241 | -0.27008 | -0.10986 | 3.923 | -0.13275 | -12.9501 | -0.25177 | -0.041199 | 4.1931 | 55.9479 | 57.0877 | 111.6531 | 124.4934 | 3.923 | 124.5621 | 73.1598 | -0.25177 | 124.4934 | 3.923 | 73.1598 | 111.6531 | 124.5621 | -124.8734 | -124.855
1574.6406 | 124.91 | -60.0311 | 64.5538 | -0.16304 | 0.024646 | 0.025368 | 0.013253 | 0.061199 | 0.0075409 | 0.091884 | -56.0623 | 64.4531 | -60.2921 | -59.7977 | 51.8738 | 13.0646 | -4.39 | -2.8793 | 64.476 | -60.3195 | -0.26093 | -0.10071 | 3.9688 | 0.23346 | -12.6801 | -0.28839 | -0.07782 | 4.2297 | 55.6412 | 57.1518 | 111.9049 | 124.4843 | 3.9688 | 124.5071 | 73.0957 | -0.28839 | 124.4843 | 3.9688 | 73.0957 | 111.9049 | 124.5071 | -124.8459 | -124.8734
1575.6406 | 125.0107 | -60.0174 | 64.5721 | -0.12489 | 0.023364 | 0.025368 | 0.01304 | 0.060558 | 0.0045501 | 0.088679 | -56.0165 | 64.4485 | -60.2737 | -60.141 | 51.535 | 13.0554 | -3.5294 | -2.8519 | 64.5813 | -60.26 | -0.25635 | -0.1236 | 4.0009 | -0.1236 | -13.0371 | -0.24262 | 0.009155 | 4.2572 | 56.488 | 57.1655 | 111.5524 | 124.4659 | 4.0009 | 124.5987 | 73.0728 | -0.24262 | 124.4659 | 4.0009 | 73.0728 | 111.5524 | 124.5987 | -124.8459 | -124.8322
1576.6406 | 124.9832 | -60.0037 | 64.5584 | -0.1783 | 0.024432 | 0.027931 | 0.014321 | 0.061412 | 0.0068999 | 0.08932 | -56.0303 | 64.4623 | -60.3149 | -60.1318 | 51.4618 | 13.1378 | -4.1107 | -2.9251 | 64.4852 | -60.2875 | -0.31128 | -0.096131 | 3.9734 | -0.12817 | -13.0966 | -0.28381 | -0.073243 | 4.2847 | 55.8929 | 57.0786 | 111.4655 | 124.4659 | 3.9734 | 124.4888 | 73.1415 | -0.28381 | 124.4659 | 3.9734 | 73.1415 | 111.4655 | 124.4888 | -124.8734 | -124.8459
1577.6406 | 124.7955 | -60.0632 | 64.6179 | -0.25459 | 0.027209 | 0.031776 | 0.016671 | 0.062908 | 0.0054047 | 0.090602 | -56.0257 | 64.5767 | -60.3012 | -60.2188 | 51.297 | 12.9547 | -3.9459 | -3.0899 | 64.6088 | -60.3149 | -0.23804 | -0.041199 | 4.0375 | -0.15564 | -13.3209 | -0.25177 | -0.009155 | 4.2755 | 56.1172 | 56.9733 | 111.3602 | 124.6399 | 4.0375 | 124.6719 | 73.0179 | -0.25177 | 124.6399 | 4.0375 | 73.0179 | 111.3602 | 124.6719 | -124.9191 | -124.9329
1578.6406 | 124.9191 | -60.0266 | 64.563 | -0.063858 | 0.021655 | 0.02964 | 0.014749 | 0.063121 | 0.0054047 | 0.090602 | -56.0211 | 64.476 | -60.2921 | -60.1822 | 51.3519 | 13.0371 | -4.0878 | -2.9709 | 64.5493 | -60.2325 | -0.2655 | -0.086975 | 4.0054 | -0.15564 | -13.2111 | -0.20599 | -0.013733 | 4.2709 | 55.9387 | 57.0557 | 111.3785 | 124.5026 | 4.0054 | 124.5758 | 73.0637 | -0.20599 | 124.5026 | 4.0054 | 73.0637 | 111.3785 | 124.5758 | -124.855 | -124.7955
1579.6406 | 124.9466 | -60.0082 | 64.5859 | -0.094376 | 0.022082 | 0.025154 | 0.016885 | 0.06184 | 0.0045501 | 0.091884 | -55.9845 | 64.4943 | -60.2783 | -60.1685 | 51.2878 | 13.06 | -4.1153 | -2.9892 | 64.5355 | -60.2509 | -0.27008 | -0.091552 | 4.0237 | -0.16022 | -13.298 | -0.24261 | -0.050354 | 4.2938 | 55.8929 | 57.019 | 111.2961 | 124.5026 | 4.0237 | 124.5438 | 73.0682 | -0.24261 | 124.5026 | 4.0237 | 73.0682 | 111.2961 | 124.5438 | -124.8642 | -124.8367
1580.6406 | 124.9741 | -60.0082 | 64.5721 | -0.14015 | 0.023791 | 0.028359 | 0.015603 | 0.060985 | 0.0064727 | 0.091243 | -55.9341 | 64.4989 | -60.2921 | -60.1273 | 51.2558 | 13.0966 | -4.1382 | -2.948 | 64.5081 | -60.2417 | -0.28381 | -0.073243 | 4.0741 | -0.11902 | -13.3163 | -0.23346 | -0.064087 | 4.3579 | 55.8701 | 57.0602 | 111.264 | 124.5071 | 4.0741 | 124.5163 | 73.1049 | -0.23346 | 124.5071 | 4.0741 | 73.1049 | 111.264 | 124.5163 | -124.8642 | -124.8138
1581.6406 | 124.9603 | -59.9899 | 64.6133 | -0.44533 | 0.024432 | 0.024086 | 0.014321 | 0.06184 | 0.0056183 | 0.092524 | -55.8975 | 64.4943 | -60.2463 | -60.1044 | 51.2375 | 13.0692 | -4.1061 | -2.9617 | 64.5493 | -60.2554 | -0.25635 | -0.11902 | 4.0924 | -0.11444 | -13.3759 | -0.2655 | -0.064087 | 4.3488 | 55.8838 | 57.0282 | 111.2274 | 124.4843 | 4.0924 | 124.5392 | 73.0591 | -0.2655 | 124.4843 | 4.0924 | 73.0591 | 111.2274 | 124.5392 | -124.8596 | -124.8688
1582.6406 | 124.9191 | -59.9854 | 64.6271 | -0.20882 | 0.024432 | 0.023018 | 0.015389 | 0.061199 | 0.0060455 | 0.092311 | -55.8746 | 64.5126 | -60.2417 | -60.1501 | 51.1642 | 13.06 | -4.0329 | -2.9892 | 64.6042 | -60.2509 | -0.25635 | -0.11444 | 4.1107 | -0.16479 | -13.4628 | -0.2655 | -0.022888 | 4.3671 | 55.9525 | 56.9962 | 111.1496 | 124.498 | 4.1107 | 124.5895 | 73.0453 | -0.2655 | 124.498 | 4.1107 | 73.0453 | 111.1496 | 124.5895 | -124.8688 | -124.8779
1583.6406 | 124.942 | -59.935 | 64.6454 | 0.77538 | 0.026996 | 0.022804 | 0.015389 | 0.062267 | 0.0054047 | 0.092311 | -55.8197 | 64.5401 | -60.2097 | -60.0861 | 51.1871 | 13.0966 | -4.0924 | -2.916 | 64.595 | -60.1913 | -0.27466 | -0.10529 | 4.1153 | -0.15106 | -13.4583 | -0.25635 | -0.050354 | 4.39 | 55.8426 | 57.019 | 111.1221 | 124.4751 | 4.1153 | 124.53 | 73.0316 | -0.25635 | 124.4751 | 4.1153 | 73.0316 | 111.1221 | 124.53 | -124.855 | -124.8367
1584.6406 | 124.9512 | -59.935 | 64.65 | -0.46059 | 0.02251 | 0.027077 | 0.01368 | 0.061626 | 0.0058319 | 0.091456 | -55.8014 | 64.5264 | -60.2234 | -60.0586 | 51.1047 | 13.1012 | -4.1061 | -2.9114 | 64.5813 | -60.1776 | -0.28839 | -0.1236 | 4.1336 | -0.1236 | -13.5452 | -0.24261 | -0.068664 | 4.422 | 55.8289 | 57.0236 | 111.0397 | 124.4614 | 4.1336 | 124.5163 | 73.0362 | -0.24261 | 124.4614 | 4.1336 | 73.0362 | 111.0397 | 124.5163 | -124.8734 | -124.8276
1585.6406 | 124.9466 | -59.9716 | 64.6179 | -0.15541 | 0.025073 | 0.024941 | 0.014749 | 0.060131 | 0.0064727 | 0.091456 | -55.8105 | 64.5309 | -60.2463 | -60.0998 | 51.059 | 13.0737 | -4.1107 | -2.9388 | 64.563 | -60.2234 | -0.27466 | -0.086975 | 4.1611 | -0.12817 | -13.559 | -0.25177 | -0.054932 | 4.4357 | 55.8609 | 57.0328 | 111.0306 | 124.5026 | 4.1611 | 124.5346 | 73.0453 | -0.25177 | 124.5026 | 4.1611 | 73.0453 | 111.0306 | 124.5346 | -124.8642 | -124.8413
1586.6406 | 124.9832 | -59.9625 | 64.6408 | -0.086746 | 0.022937 | 0.02665 | 0.015389 | 0.059276 | 0.0045501 | 0.091029 | -55.8014 | 64.5264 | -60.2097 | -60.1089 | 50.9857 | 13.092 | -4.1336 | -2.9343 | 64.5584 | -60.2417 | -0.24719 | -0.11444 | 4.1611 | -0.14648 | -13.6551 | -0.27924 | -0.082397 | 4.4083 | 55.8289 | 57.0282 | 110.9482 | 124.4888 | 4.1611 | 124.5209 | 73.0545 | -0.27924 | 124.4888 | 4.1611 | 73.0545 | 110.9482 | 124.5209 | -124.8505 | -124.8825
1587.6406 | 124.8871 | -60.0037 | 64.6912 | -0.24696 | 0.029132 | 0.024941 | 0.020089 | 0.063549 | 0.0088225 | 0.090175 | -55.7922 | 64.6591 | -60.2234 | -60.1685 | 50.853 | 12.973 | -3.9734 | -3.035 | 64.6133 | -60.26 | -0.21973 | -0.032043 | 4.2114 | -0.16479 | -13.8382 | -0.25635 | -0.07782 | 4.4312 | 56.0303 | 56.9687 | 110.8566 | 124.6628 | 4.2114 | 124.617 | 72.9767 | -0.25635 | 124.6628 | 4.2114 | 72.9767 | 110.8566 | 124.617 | -124.9146 | -124.9512
1588.6406 | 124.9466 | -59.9396 | 64.6454 | -0.20119 | 0.02785 | 0.032845 | 0.01304 | 0.062694 | 0.0064727 | 0.091029 | -55.719 | 64.5721 | -60.2097 | -60.0861 | 50.8896 | 13.0142 | -4.129 | -2.9114 | 64.6271 | -60.1913 | -0.27008 | -0.073242 | 4.2206 | -0.14649 | -13.7558 | -0.25177 | -0.018311 | 4.4907 | 55.8105 | 57.0282 | 110.8292 | 124.5117 | 4.2206 | 124.5667 | 72.9538 | -0.25177 | 124.5117 | 4.2206 | 72.9538 | 110.8292 | 124.5667 | -124.855 | -124.8367
1589.6406 | 124.9512 | -59.9396 | 64.65 | -0.26985 | 0.02785 | 0.031349 | 0.017526 | 0.061199 | 0.0071137 | 0.092952 | -55.7144 | 64.563 | -60.1959 | -60.0677 | 50.8575 | 13.0508 | -4.097 | -2.916 | 64.595 | -60.1822 | -0.25635 | -0.086975 | 4.2252 | -0.12817 | -13.7924 | -0.24262 | -0.054931 | 4.4815 | 55.8426 | 57.0236 | 110.7971 | 124.5026 | 4.2252 | 124.5346 | 72.9904 | -0.24262 | 124.5026 | 4.2252 | 72.9904 | 110.7971 | 124.5346 | -124.8459 | -124.8322
1590.6406 | 124.9283 | -59.935 | 64.6729 | -0.58266 | 0.028277 | 0.026009 | 0.018594 | 0.062481 | 0.0066863 | 0.093165 | -55.6915 | 64.5721 | -60.2005 | -60.0632 | 50.8163 | 13.0692 | -4.0878 | -2.8931 | 64.6133 | -60.1822 | -0.2655 | -0.10071 | 4.2435 | -0.12817 | -13.8565 | -0.24719 | -0.05951 | 4.509 | 55.8472 | 57.0419 | 110.7513 | 124.5071 | 4.2435 | 124.5483 | 73.0042 | -0.24719 | 124.5071 | 4.2435 | 73.0042 | 110.7513 | 124.5483 | -124.8734 | -124.855
1591.6406 | 124.9603 | -59.9442 | 64.6408 | -2.1848 | 0.023791 | 0.029427 | 0.016244 | 0.06184 | 0.0060455 | 0.092311 | -55.6503 | 64.5767 | -60.2051 | -60.0586 | 50.6973 | 12.973 | -4.1336 | -2.8748 | 64.5721 | -60.2097 | -0.26093 | -0.064087 | 4.2938 | -0.11444 | -13.9435 | -0.2655 | -0.068664 | 4.5547 | 55.8105 | 57.0694 | 110.6415 | 124.5209 | 4.2938 | 124.5163 | 72.9172 | -0.2655 | 124.5209 | 4.2938 | 72.9172 | 110.6415 | 124.5163 | -124.8459 | -124.8505
1592.6406 | 124.8322 | -59.9487 | 64.6866 | -0.28511 | 0.026568 | 0.028145 | 0.017312 | 0.063335 | 0.0060455 | 0.093593 | -55.6824 | 64.595 | -60.2051 | -60.141 | 50.6195 | 12.9135 | -3.9917 | -2.9663 | 64.6591 | -60.2325 | -0.25635 | -0.091552 | 4.2664 | -0.19226 | -14.0671 | -0.28381 | -0.027465 | 4.5227 | 55.957 | 56.9824 | 110.5682 | 124.5438 | 4.2664 | 124.6078 | 72.8622 | -0.28381 | 124.5438 | 4.2664 | 72.8622 | 110.5682 | 124.6078 | -124.8917 | -124.9191
1593.6406 | 124.9603 | -59.8801 | 64.7186 | -0.025711 | 0.023364 | 0.02964 | 0.014962 | 0.062694 | 0.0075409 | 0.092738 | -55.6366 | 64.6133 | -60.173 | -60.0723 | 50.6699 | 13.0371 | -4.0878 | -2.8839 | 64.6591 | -60.141 | -0.29297 | -0.10529 | 4.2435 | -0.19226 | -14.0488 | -0.26093 | -0.059509 | 4.5364 | 55.7922 | 56.9962 | 110.5499 | 124.4934 | 4.2435 | 124.5392 | 72.9172 | -0.26093 | 124.4934 | 4.2435 | 72.9172 | 110.5499 | 124.5392 | -124.8917 | -124.8596
1594.6406 | 124.9603 | -59.8892 | 64.7095 | -0.12489 | 0.025287 | 0.028572 | 0.013894 | 0.062481 | 0.0075409 | 0.092952 | -55.5725 | 64.6225 | -60.1501 | -60.0082 | 50.679 | 13.1012 | -4.1382 | -2.8519 | 64.6317 | -60.1318 | -0.26093 | -0.086975 | 4.3167 | -0.11902 | -14.0305 | -0.24262 | -0.07782 | 4.5776 | 55.751 | 57.0374 | 110.5682 | 124.5117 | 4.3167 | 124.5209 | 72.9904 | -0.24262 | 124.5117 | 4.3167 | 72.9904 | 110.5682 | 124.5209 | -124.8596 | -124.8413
1595.6406 | 124.9374 | -59.903 | 64.7415 | -0.17067 | 0.0255 | 0.025581 | 0.010476 | 0.059276 | 0.0083953 | 0.094661 | -55.5359 | 64.6088 | -60.1593 | -60.1822 | 50.6699 | 13.0966 | -4.2526 | -2.7924 | 64.6225 | -60.1593 | -0.25635 | -0.13275 | 4.3671 | -0.27924 | -14.0717 | -0.25635 | -0.11902 | 4.6234 | 55.6503 | 57.1106 | 110.5728 | 124.5117 | 4.3671 | 124.5255 | 72.9996 | -0.25635 | 124.5117 | 4.3671 | 72.9996 | 110.5728 | 124.5255 | -124.9008 | -124.9008
1596.6406 | 125.0015 | -59.8663 | 64.6957 | -0.10963 | 0.025714 | 0.02665 | 0.014962 | 0.062908 | 0.0071137 | 0.093593 | -55.5313 | 64.5905 | -60.1456 | -59.9991 | 50.5554 | 13.0737 | -4.0833 | -2.8152 | 64.6271 | -60.1089 | -0.27924 | -0.10529 | 4.335 | -0.13275 | -14.1403 | -0.24262 | -0.068665 | 4.6143 | 55.7831 | 57.0511 | 110.4218 | 124.4568 | 4.335 | 124.4934 | 72.9401 | -0.24262 | 124.4568 | 4.335 | 72.9401 | 110.4218 | 124.4934 | -124.8413 | -124.8047
1597.6406 | 124.8138 | -59.9121 | 64.7644 | -0.26985 | 0.030414 | 0.030495 | 0.022225 | 0.061626 | 0.0066863 | 0.092524 | -55.5908 | 64.6912 | -60.173 | -60.1044 | 50.4044 | 12.8723 | -3.9001 | -2.9388 | 64.682 | -60.2051 | -0.26093 | -0.073242 | 4.3213 | -0.19226 | -14.36 | -0.29297 | -0.082397 | 4.5822 | 56.012 | 56.9733 | 110.3165 | 124.6033 | 4.3213 | 124.5941 | 72.7844 | -0.29297 | 124.6033 | 4.3213 | 72.7844 | 110.3165 | 124.5941 | -124.9374 | -124.9695
1598.6406 | 124.9466 | -59.8618 | 64.7232 | -0.079117 | 0.025714 | 0.030281 | 0.012612 | 0.06184 | 0.0066863 | 0.095515 | -55.4993 | 64.6179 | -60.1227 | -60.0037 | 50.4868 | 13.0325 | -4.0558 | -2.7878 | 64.6774 | -60.0906 | -0.26093 | -0.10529 | 4.3625 | -0.14191 | -14.2365 | -0.22888 | -0.045777 | 4.6234 | 55.806 | 57.074 | 110.3485 | 124.4797 | 4.3625 | 124.5392 | 72.8943 | -0.22888 | 124.4797 | 4.3625 | 72.8943 | 110.3485 | 124.5392 | -124.8459 | -124.8138
1599.6406 | 124.8779 | -59.8801 | 64.7598 | -0.033341 | 0.025928 | 0.026436 | 0.015817 | 0.062267 | 0.0064727 | 0.09402 | -55.4993 | 64.6454 | -60.1135 | -60.0357 | 50.4364 | 13.0005 | -3.978 | -2.8061 | 64.7003 | -60.1181 | -0.23346 | -0.11444 | 4.3808 | -0.15564 | -14.3234 | -0.23804 | -0.05951 | 4.6143 | 55.9021 | 57.074 | 110.3165 | 124.5255 | 4.3808 | 124.5804 | 72.8806 | -0.23804 | 124.5255 | 4.3808 | 72.8806 | 110.3165 | 124.5804 | -124.8734 | -124.8779
1600.6406 | 124.9008 | -59.8526 | 64.7369 | -0.61317 | 0.028064 | 0.029854 | 0.015176 | 0.062908 | 0.0064727 | 0.094233 | -55.5542 | 64.6362 | -60.1135 | -60.0586 | 50.3723 | 13.0096 | -3.9505 | -2.7878 | 64.7141 | -60.1273 | -0.26093 | -0.10071 | 4.2984 | -0.20599 | -14.3646 | -0.27466 | -0.022888 | 4.5593 | 55.9021 | 57.0648 | 110.2249 | 124.4888 | 4.2984 | 124.5667 | 72.8622 | -0.27466 | 124.4888 | 4.2984 | 72.8622 | 110.2249 | 124.5667 | -124.8505 | -124.8642
1601.6406 | 124.8871 | -59.848 | 64.7552 | -0.025711 | 0.0255 | 0.024727 | 0.014962 | 0.061412 | 0.0092499 | 0.092311 | -55.4352 | 64.6591 | -60.1135 | -60.022 | 50.3815 | 13.0142 | -3.9642 | -2.7786 | 64.6866 | -60.1135 | -0.2655 | -0.09613 | 4.4128 | -0.17395 | -14.3738 | -0.2655 | -0.068665 | 4.6783 | 55.8838 | 57.0694 | 110.2295 | 124.5071 | 4.4128 | 124.5346 | 72.8622 | -0.2655 | 124.5071 | 4.4128 | 72.8622 | 110.2295 | 124.5346 | -124.8688 | -124.8688
1602.6406 | 124.9466 | -59.8343 | 64.7369 | -0.12489 | 0.023364 | 0.025581 | 0.014749 | 0.06184 | 0.0073273 | 0.092738 | -55.4123 | 64.6637 | -60.0998 | -59.9854 | 50.3769 | 13.0966 | -3.9688 | -2.6825 | 64.6729 | -60.0998 | -0.2655 | -0.073242 | 4.422 | -0.15106 | -14.36 | -0.2655 | -0.064086 | 4.6875 | 55.8655 | 57.1518 | 110.2112 | 124.498 | 4.422 | 124.5071 | 72.9309 | -0.2655 | 124.498 | 4.422 | 72.9309 | 110.2112 | 124.5071 | -124.8367 | -124.8367
1603.6406 | 124.9374 | -59.8618 | 64.7461 | -0.033341 | 0.025073 | 0.028786 | 0.016885 | 0.060985 | 0.0066863 | 0.094447 | -55.4443 | 64.65 | -60.1181 | -60.0174 | 50.2945 | 13.0417 | -3.9459 | -2.6962 | 64.7003 | -60.0815 | -0.25635 | -0.096131 | 4.4174 | -0.15564 | -14.4516 | -0.21973 | -0.045777 | 4.6738 | 55.9158 | 57.1655 | 110.1562 | 124.5117 | 4.4174 | 124.5621 | 72.9034 | -0.21973 | 124.5117 | 4.4174 | 72.9034 | 110.1562 | 124.5621 | -124.8642 | -124.8276
1604.6406 | 124.9374 | -59.8434 | 64.7507 | -0.04097 | 0.026782 | 0.028359 | 0.015603 | 0.062481 | 0.0081817 | 0.095302 | -55.4306 | 64.65 | -60.1044 | -60.0266 | 50.235 | 13.0417 | -3.9276 | -2.71 | 64.6774 | -60.1273 | -0.26093 | -0.10071 | 4.4128 | -0.1831 | -14.5157 | -0.28381 | -0.073242 | 4.6738 | 55.9158 | 57.1335 | 110.0784 | 124.4934 | 4.4128 | 124.5209 | 72.8851 | -0.28381 | 124.4934 | 4.4128 | 72.8851 | 110.0784 | 124.5209 | -124.855 | -124.8779
1605.6406 | 124.8917 | -59.8938 | 64.7003 | -0.010452 | 0.027209 | 0.030495 | 0.012826 | 0.062267 | 0.0088225 | 0.093379 | -55.4489 | 64.5996 | -60.1273 | -60.0586 | 50.2121 | 13.0142 | -3.8864 | -2.7008 | 64.6362 | -60.141 | -0.23346 | -0.10071 | 4.4449 | -0.16479 | -14.4882 | -0.24719 | -0.064087 | 4.6783 | 56.0074 | 57.193 | 110.1059 | 124.4934 | 4.4449 | 124.53 | 72.908 | -0.24719 | 124.4934 | 4.4449 | 72.908 | 110.1059 | 124.53 | -124.8276 | -124.8413
1606.6406 | 124.8962 | -59.8389 | 64.7369 | 0.14214 | 0.026568 | 0.027931 | 0.015176 | 0.059703 | 0.0043365 | 0.093593 | -55.3757 | 64.65 | -60.0952 | -60.0357 | 50.1617 | 13.0005 | -3.9276 | -2.7054 | 64.6957 | -60.0998 | -0.25635 | -0.086975 | 4.4632 | -0.19684 | -14.5752 | -0.26093 | -0.041198 | 4.7195 | 55.9113 | 57.1335 | 110.0006 | 124.4888 | 4.4632 | 124.5346 | 72.8394 | -0.26093 | 124.4888 | 4.4632 | 72.8394 | 110.0006 | 124.5346 | -124.8322 | -124.8367
1607.6406 | 124.9557 | -59.7977 | 64.7736 | -0.071488 | 0.025928 | 0.026009 | 0.01603 | 0.060558 | 0.0088225 | 0.096156 | -55.3253 | 64.6774 | -60.1044 | -59.9442 | 50.2167 | 13.1241 | -3.8406 | -2.6047 | 64.6912 | -60.0861 | -0.3067 | -0.096131 | 4.4724 | -0.14648 | -14.5569 | -0.28839 | -0.082398 | 4.7791 | 55.957 | 57.193 | 110.0143 | 124.4751 | 4.4724 | 124.4888 | 72.9218 | -0.28839 | 124.4751 | 4.4724 | 72.9218 | 110.0143 | 124.4888 | -124.8779 | -124.8596
1608.6406 | 124.9008 | -59.816 | 64.769 | 0.10399 | 0.026782 | 0.030068 | 0.020089 | 0.063335 | 0.0081817 | 0.094874 | -55.3528 | 64.6774 | -60.0723 | -60.0082 | 50.116 | 13.0829 | -3.8086 | -2.6688 | 64.6912 | -60.0861 | -0.25635 | -0.091553 | 4.4632 | -0.19226 | -14.653 | -0.27008 | -0.07782 | 4.7195 | 56.0074 | 57.1472 | 109.9319 | 124.4934 | 4.4632 | 124.5071 | 72.8989 | -0.27008 | 124.4934 | 4.4632 | 72.8989 | 109.9319 | 124.5071 | -124.8413 | -124.855
1609.6406 | 124.91 | -59.7885 | 64.7827 | -0.0028231 | 0.02785 | 0.030068 | 0.015176 | 0.062267 | 0.0075409 | 0.093806 | -55.1376 | 64.7278 | -60.0357 | -60.0082 | 50.116 | 13.1104 | -3.7582 | -2.6184 | 64.7415 | -60.0357 | -0.24719 | -0.054932 | 4.6509 | -0.21973 | -14.6667 | -0.24719 | -0.041199 | 4.8981 | 56.0303 | 57.1701 | 109.9045 | 124.5163 | 4.6509 | 124.53 | 72.8989 | -0.24719 | 124.5163 | 4.6509 | 72.8989 | 109.9045 | 124.53 | -124.8184 | -124.8184
1610.6406 | 124.8322 | -59.8114 | 64.7507 | 0.12688 | 0.026141 | 0.028786 | 0.015817 | 0.060772 | 0.0056183 | 0.095729 | -55.3024 | 64.6774 | -60.0723 | -60.0082 | 50.0885 | 13.1058 | -3.7994 | -2.5909 | 64.7095 | -60.0861 | -0.26093 | -0.073242 | 4.509 | -0.19684 | -14.6622 | -0.27466 | -0.041198 | 4.7699 | 56.012 | 57.2205 | 109.8999 | 124.4888 | 4.509 | 124.5209 | 72.9172 | -0.27466 | 124.4888 | 4.509 | 72.9172 | 109.8999 | 124.5209 | -124.823 | -124.8367
1611.6406 | 124.8596 | -59.8343 | 64.7415 | 0.20317 | 0.028918 | 0.030495 | 0.017312 | 0.060985 | 0.0079681 | 0.095302 | -55.2979 | 64.6774 | -60.0998 | -60.0266 | 50.0427 | 13.0692 | -3.8132 | -2.6321 | 64.6866 | -60.0952 | -0.2655 | -0.064087 | 4.5364 | -0.19226 | -14.6988 | -0.26093 | -0.054932 | 4.8019 | 56.0211 | 57.2021 | 109.877 | 124.5117 | 4.5364 | 124.5209 | 72.9034 | -0.26093 | 124.5117 | 4.5364 | 72.9034 | 109.877 | 124.5209 | -124.8413 | -124.8367
1612.6406 | 124.823 | -59.8434 | 64.7919 | -0.21645 | 0.031482 | 0.02964 | 0.022866 | 0.063762 | 0.0060455 | 0.094233 | -55.3162 | 64.7461 | -60.0861 | -60.0266 | 49.9008 | 13.0188 | -3.5751 | -2.6688 | 64.7552 | -60.1181 | -0.24262 | -0.045776 | 4.5273 | -0.1831 | -14.8911 | -0.27466 | -0.036621 | 4.7699 | 56.2683 | 57.1747 | 109.7443 | 124.5895 | 4.5273 | 124.5987 | 72.8622 | -0.27466 | 124.5895 | 4.5273 | 72.8622 | 109.7443 | 124.5987 | -124.8779 | -124.91
1613.6406 | 124.9146 | -59.8297 | 64.7415 | 0.51598 | 0.030414 | 0.029427 | 0.023294 | 0.063549 | 0.0051911 | 0.093379 | -55.2292 | 64.6683 | -60.0861 | -59.9899 | 50.0244 | 13.1744 | -3.8315 | -2.5772 | 64.6591 | -60.0861 | -0.25635 | -0.073242 | 4.6005 | -0.16022 | -14.7171 | -0.25635 | -0.082397 | 4.8569 | 55.9982 | 57.2525 | 109.8541 | 124.498 | 4.6005 | 124.4888 | 73.0041 | -0.25635 | 124.498 | 4.6005 | 73.0041 | 109.8541 | 124.4888 | -124.8276 | -124.8276
1614.6406 | 124.9146 | -59.816 | 64.7278 | 0.16502 | 0.029345 | 0.034554 | 0.018807 | 0.063335 | 0.0064727 | 0.095729 | -55.2338 | 64.6545 | -60.0998 | -59.9854 | 49.9695 | 13.1424 | -3.8269 | -2.5589 | 64.6683 | -60.1181 | -0.28381 | -0.073242 | 4.5822 | -0.16937 | -14.7583 | -0.30212 | -0.059509 | 4.866 | 55.9891 | 57.2571 | 109.7855 | 124.4705 | 4.5822 | 124.4843 | 72.9584 | -0.30212 | 124.4705 | 4.5822 | 72.9584 | 109.7855 | 124.4843 | -124.8276 | -124.8459
1615.6406 | 124.9283 | -59.8526 | 64.7095 | 0.0048064 | 0.031695 | 0.030495 | 0.021798 | 0.063762 | 0.0064727 | 0.093593 | -55.2338 | 64.6637 | -60.1227 | -59.9854 | 49.9191 | 13.1195 | -3.8589 | -2.5818 | 64.682 | -60.1089 | -0.27008 | -0.045777 | 4.6188 | -0.13275 | -14.7903 | -0.25635 | -0.027466 | 4.8889 | 55.9937 | 57.2708 | 109.7717 | 124.5163 | 4.6188 | 124.5346 | 72.9721 | -0.25635 | 124.5163 | 4.6188 | 72.9721 | 109.7717 | 124.5346 | -124.8322 | -124.8184
1616.6406 | 124.9008 | -59.8572 | 64.7049 | 0.10399 | 0.030414 | 0.033272 | 0.019662 | 0.063976 | 0.0049773 | 0.098292 | -55.2246 | 64.6545 | -60.1135 | -60.0128 | 49.8962 | 13.1104 | -3.8086 | -2.536 | 64.6637 | -60.0998 | -0.25635 | -0.050354 | 4.6326 | -0.15564 | -14.8087 | -0.24261 | -0.041199 | 4.8889 | 56.0486 | 57.3212 | 109.7534 | 124.5117 | 4.6326 | 124.5209 | 72.9675 | -0.24261 | 124.5117 | 4.6326 | 72.9675 | 109.7534 | 124.5209 | -124.8184 | -124.8047
1617.6406 | 124.9237 | -59.8206 | 64.7507 | -0.018082 | 0.028064 | 0.030708 | 0.015389 | 0.060985 | 0.0056183 | 0.095942 | -55.2429 | 64.6729 | -60.0952 | -59.9991 | 49.8962 | 13.1607 | -3.685 | -2.4673 | 64.6774 | -60.0723 | -0.27466 | -0.077819 | 4.5776 | -0.17853 | -14.8544 | -0.25177 | -0.073242 | 4.8523 | 56.1356 | 57.3532 | 109.7168 | 124.4934 | 4.5776 | 124.498 | 72.9813 | -0.25177 | 124.4934 | 4.5776 | 72.9813 | 109.7168 | 124.498 | -124.8459 | -124.823
1618.6406 | 124.9329 | -59.8709 | 64.6866 | 0.08873 | 0.028064 | 0.033913 | 0.022012 | 0.062053 | 0.0071137 | 0.096797 | -55.22 | 64.6271 | -60.1273 | -60.0311 | 49.7864 | 13.1699 | -3.8269 | -2.5131 | 64.6225 | -60.173 | -0.25635 | -0.059509 | 4.6509 | -0.16022 | -14.9002 | -0.30212 | -0.064086 | 4.9072 | 56.044 | 57.3578 | 109.6573 | 124.498 | 4.6509 | 124.4934 | 73.0408 | -0.30212 | 124.498 | 4.6509 | 73.0408 | 109.6573 | 124.4934 | -124.8138 | -124.8596
1619.6406 | 124.91 | -59.8434 | 64.7003 | 0.20317 | 0.029773 | 0.030495 | 0.025002 | 0.063549 | 0.0071137 | 0.09637 | -55.2292 | 64.6454 | -60.1227 | -60.0266 | 49.7452 | 13.1653 | -3.7582 | -2.5223 | 64.6591 | -60.1364 | -0.27924 | -0.054931 | 4.6143 | -0.1831 | -14.9551 | -0.29297 | -0.041198 | 4.8935 | 56.0852 | 57.3212 | 109.5886 | 124.4888 | 4.6143 | 124.5026 | 73.0087 | -0.29297 | 124.4888 | 4.6143 | 73.0087 | 109.5886 | 124.5026 | -124.823 | -124.8367
1620.6406 | 124.9054 | -59.8709 | 64.7186 | 0.19554 | 0.032123 | 0.03434 | 0.024789 | 0.063121 | 0.0071137 | 0.097224 | -55.2109 | 64.7003 | -60.1227 | -60.0403 | 49.7406 | 13.1882 | -3.7125 | -2.5085 | 64.6683 | -60.1501 | -0.25177 | -0.018311 | 4.66 | -0.16937 | -14.978 | -0.27923 | -0.050354 | 4.9118 | 56.1584 | 57.3624 | 109.6115 | 124.5712 | 4.66 | 124.5392 | 73.0591 | -0.27923 | 124.5712 | 4.66 | 73.0591 | 109.6115 | 124.5392 | -124.8413 | -124.8688
1621.6406 | 124.9466 | -59.848 | 64.6774 | 0.10399 | 0.029559 | 0.032631 | 0.020089 | 0.065258 | 0.0058319 | 0.097651 | -55.1697 | 64.6637 | -60.1089 | -60.1959 | 49.5621 | 13.3255 | -3.6026 | -2.4811 | 64.6637 | -60.1318 | -0.26093 | -0.013733 | 4.6783 | -0.3479 | -15.1154 | -0.28381 | -0.013733 | 4.9393 | 56.2454 | 57.3669 | 109.4101 | 124.5117 | 4.6783 | 124.5117 | 73.1735 | -0.28381 | 124.5117 | 4.6783 | 73.1735 | 109.4101 | 124.5117 | -124.7864 | -124.8093
1622.6406 | 124.9146 | -59.8114 | 64.769 | -0.010452 | 0.029559 | 0.02964 | 0.017098 | 0.063335 | 0.0060455 | 0.096156 | -55.188 | 64.6957 | -60.0723 | -59.9854 | 49.7635 | 13.2202 | -3.5568 | -2.3758 | 64.7186 | -60.0632 | -0.26093 | -0.073242 | 4.6234 | -0.17395 | -15.0055 | -0.25177 | -0.050354 | 4.8843 | 56.2546 | 57.4356 | 109.5749 | 124.5071 | 4.6234 | 124.53 | 73.0316 | -0.25177 | 124.5071 | 4.6234 | 73.0316 | 109.5749 | 124.53 | -124.8413 | -124.8322
1623.6406 | 124.9329 | -59.8297 | 64.7644 | 0.25658 | 0.029345 | 0.032845 | 0.02308 | 0.065044 | 0.0071137 | 0.097224 | -55.1468 | 64.6637 | -60.0906 | -59.9716 | 49.7406 | 13.3163 | -3.6575 | -2.3895 | 64.7003 | -60.1227 | -0.26093 | -0.10071 | 4.6829 | -0.14191 | -15.0238 | -0.29297 | -0.064087 | 4.9438 | 56.1722 | 57.4402 | 109.5703 | 124.4934 | 4.6829 | 124.53 | 73.1461 | -0.29297 | 124.4934 | 4.6829 | 73.1461 | 109.5703 | 124.53 | -124.855 | -124.8871
1624.6406 | 124.9054 | -59.7977 | 64.7415 | 0.82878 | 0.029559 | 0.030281 | 0.021371 | 0.062694 | 0.0045501 | 0.095942 | -55.0735 | 64.6866 | -60.0494 | -59.9625 | 49.7223 | 13.3163 | -3.6484 | -2.3712 | 64.6957 | -60.0952 | -0.25177 | -0.054932 | 4.7241 | -0.16479 | -15.0192 | -0.29755 | -0.045776 | 4.9759 | 56.1493 | 57.4265 | 109.52 | 124.4843 | 4.7241 | 124.4934 | 73.114 | -0.29755 | 124.4843 | 4.7241 | 73.114 | 109.52 | 124.4934 | -124.791 | -124.8367
1625.6406 | 124.9329 | -59.8251 | 64.7141 | -0.033341 | 0.028918 | 0.028786 | 0.015817 | 0.062694 | 0.0086089 | 0.095729 | -55.1743 | 64.6454 | -60.0952 | -59.9762 | 49.6719 | 13.3026 | -3.5614 | -2.3529 | 64.7141 | -60.0815 | -0.27008 | -0.068664 | 4.6509 | -0.15106 | -15.0421 | -0.25635 | 0 | 4.921 | 56.2637 | 57.4722 | 109.4971 | 124.4705 | 4.6509 | 124.5392 | 73.1277 | -0.25635 | 124.4705 | 4.6509 | 73.1277 | 109.4971 | 124.5392 | -124.8093 | -124.7955
1626.6406 | 124.9008 | -59.8663 | 64.7552 | 0.14976 | 0.031268 | 0.033913 | 0.023507 | 0.064617 | 0.0066863 | 0.095088 | -55.1559 | 64.7232 | -60.1089 | -60.0266 | 49.5895 | 13.2935 | -3.5522 | -2.4399 | 64.6957 | -60.1273 | -0.24262 | -0.032043 | 4.7104 | -0.16022 | -15.1657 | -0.26093 | -0.059509 | 4.953 | 56.3141 | 57.4265 | 109.4559 | 124.5895 | 4.7104 | 124.5621 | 73.1598 | -0.26093 | 124.5895 | 4.7104 | 73.1598 | 109.4559 | 124.5621 | -124.8642 | -124.8825
1627.6406 | 124.8825 | -59.7839 | 64.769 | -0.056229 | 0.027209 | 0.028145 | 0.017739 | 0.062053 | 0.0058319 | 0.094661 | -55.1468 | 64.6957 | -60.0769 | -59.9808 | 49.6536 | 13.3804 | -3.4195 | -2.2385 | 64.7461 | -60.0677 | -0.29297 | -0.073242 | 4.6371 | -0.19684 | -15.1154 | -0.28381 | -0.022888 | 4.9301 | 56.3644 | 57.5455 | 109.4376 | 124.4797 | 4.6371 | 124.53 | 73.1644 | -0.28381 | 124.4797 | 4.6371 | 73.1644 | 109.4376 | 124.53 | -124.8459 | -124.8367
1628.6406 | 124.9329 | -59.7839 | 64.7598 | 0.14214 | 0.030627 | 0.03434 | 0.023721 | 0.063762 | 0.0062591 | 0.096583 | -55.0964 | 64.7369 | -60.0723 | -59.9625 | 49.5758 | 13.3987 | -3.4927 | -2.2888 | 64.6912 | -60.0952 | -0.28839 | -0.022889 | 4.6875 | -0.17853 | -15.184 | -0.31128 | -0.068665 | 4.9759 | 56.2912 | 57.4951 | 109.3597 | 124.5209 | 4.6875 | 124.4751 | 73.1827 | -0.31128 | 124.5209 | 4.6875 | 73.1827 | 109.3597 | 124.4751 | -124.8322 | -124.855
1629.6406 | 124.8871 | -59.7885 | 64.7873 | 0.18028 | 0.031054 | 0.030068 | 0.024575 | 0.065044 | 0.0086089 | 0.096583 | -55.0827 | 64.7644 | -60.0769 | -59.9625 | 49.6033 | 13.4216 | -3.3783 | -2.2064 | 64.7461 | -60.0677 | -0.28839 | -0.022888 | 4.7058 | -0.17395 | -15.184 | -0.27924 | -0.041198 | 4.9942 | 56.4102 | 57.5821 | 109.3918 | 124.5529 | 4.7058 | 124.5346 | 73.2101 | -0.27924 | 124.5529 | 4.7058 | 73.2101 | 109.3918 | 124.5346 | -124.8642 | -124.855
1630.6406 | 124.8962 | -59.7702 | 64.7827 | -0.048599 | 0.027209 | 0.026222 | 0.017312 | 0.062694 | 0.0081817 | 0.098292 | -55.1147 | 64.7141 | -60.0357 | -59.9396 | 49.5804 | 13.4857 | -3.2913 | -2.1652 | 64.7736 | -60.022 | -0.2655 | -0.068665 | 4.6555 | -0.16937 | -15.2023 | -0.25177 | -0.009155 | 4.921 | 56.4789 | 57.605 | 109.3506 | 124.4843 | 4.6555 | 124.5438 | 73.2559 | -0.25177 | 124.4843 | 4.6555 | 73.2559 | 109.3506 | 124.5438 | -124.8184 | -124.8047
1631.6406 | 124.9374 | -59.7656 | 64.8056 | 0.18028 | 0.029132 | 0.028359 | 0.022653 | 0.065258 | 0.0064727 | 0.098506 | -55.0369 | 64.7552 | -60.0174 | -60.0311 | 49.292 | 13.5361 | -3.154 | -2.1378 | 64.7507 | -60.0449 | -0.25177 | -0.050354 | 4.7287 | -0.2655 | -15.5136 | -0.27924 | -0.054932 | 4.9805 | 56.6116 | 57.6279 | 109.0576 | 124.5209 | 4.7287 | 124.5163 | 73.3017 | -0.27924 | 124.5209 | 4.7287 | 73.3017 | 109.0576 | 124.5163 | -124.823 | -124.8505
1632.6406 | 124.9237 | -59.7794 | 64.7919 | -0.04097 | 0.028491 | 0.028572 | 0.018167 | 0.062481 | 0.0075409 | 0.098079 | -55.1376 | 64.6912 | -60.0632 | -59.9945 | 49.4934 | 13.5178 | -3.2455 | -2.0828 | 64.7324 | -60.054 | -0.28381 | -0.10071 | 4.6417 | -0.21515 | -15.2985 | -0.27466 | -0.059509 | 4.9255 | 56.5338 | 57.6965 | 109.2728 | 124.4705 | 4.6417 | 124.5117 | 73.2971 | -0.27466 | 124.4705 | 4.6417 | 73.2971 | 109.2728 | 124.5117 | -124.855 | -124.8459
1633.6406 | 124.8322 | -59.761 | 64.856 | 0.18028 | 0.032123 | 0.030922 | 0.026498 | 0.06419 | 0.0051911 | 0.095302 | -55.0644 | 64.8376 | -60.0174 | -59.967 | 49.4751 | 13.5498 | -3.154 | -2.2018 | 64.801 | -60.0449 | -0.25635 | -0.018311 | 4.6967 | -0.20599 | -15.3809 | -0.28381 | -0.054932 | 4.953 | 56.6071 | 57.5592 | 109.2361 | 124.5987 | 4.6967 | 124.5621 | 73.3109 | -0.28381 | 124.5987 | 4.6967 | 73.3109 | 109.2361 | 124.5621 | -124.8734 | -124.9008
1634.6406 | 124.8322 | -59.7977 | 64.8102 | 0.14976 | 0.031909 | 0.031776 | 0.025002 | 0.06483 | 0.0064727 | 0.096797 | -55.1285 | 64.7827 | -60.0632 | -60.0174 | 49.3698 | 13.5086 | -3.1952 | -2.2202 | 64.7598 | -60.0723 | -0.2655 | -0.027466 | 4.6692 | -0.21973 | -15.4404 | -0.27466 | -0.050354 | 4.9347 | 56.6025 | 57.5775 | 109.1675 | 124.5804 | 4.6692 | 124.5575 | 73.3063 | -0.27466 | 124.5804 | 4.6692 | 73.3063 | 109.1675 | 124.5575 | -124.8734 | -124.8825
1635.6562 | 124.9191 | -59.7336 | 64.8422 | -0.010452 | 0.028918 | 0.027718 | 0.016244 | 0.062694 | 0.0062591 | 0.098292 | -55.0598 | 64.7507 | -60.0174 | -59.9213 | 49.5026 | 13.6276 | -3.2089 | -2.0554 | 64.8102 | -59.9991 | -0.28381 | -0.091553 | 4.6738 | -0.18768 | -15.3397 | -0.2655 | -0.032043 | 4.9576 | 56.5247 | 57.6782 | 109.2361 | 124.4843 | 4.6738 | 124.5438 | 73.3612 | -0.2655 | 124.4843 | 4.6738 | 73.3612 | 109.2361 | 124.5438 | -124.8596 | -124.8413
1636.6406 | 124.9557 | -59.7473 | 64.8056 | 0.11925 | 0.031054 | 0.033699 | 0.02543 | 0.062694 | 0.0051911 | 0.095942 | -55.0232 | 64.7736 | -59.9991 | -59.8618 | 49.3881 | 13.623 | -3.2135 | -2.0737 | 64.7324 | -60.0449 | -0.25177 | -0.032043 | 4.7241 | -0.11444 | -15.4175 | -0.29755 | -0.073242 | 4.9759 | 56.5338 | 57.6736 | 109.1354 | 124.5209 | 4.7241 | 124.4797 | 73.3704 | -0.29755 | 124.5209 | 4.7241 | 73.3704 | 109.1354 | 124.4797 | -124.8047 | -124.8505
1637.6562 | 124.9146 | -59.7153 | 64.8193 | -0.10963 | 0.028491 | 0.028359 | 0.017312 | 0.060985 | 0.0058319 | 0.096583 | -55.0003 | 64.7461 | -60.0082 | -59.8572 | 49.5117 | 13.7238 | -3.1769 | -1.9684 | 64.7736 | -59.9762 | -0.29297 | -0.073242 | 4.715 | -0.14191 | -15.3076 | -0.26093 | -0.045776 | 5.0079 | 56.5384 | 57.7469 | 109.227 | 124.4614 | 4.715 | 124.4888 | 73.439 | -0.26093 | 124.4614 | 4.715 | 73.439 | 109.227 | 124.4888 | -124.8276 | -124.7955
1638.6406 | 124.8917 | -59.7748 | 64.7552 | 0.2108 | 0.031909 | 0.032417 | 0.024362 | 0.06483 | 0.0062591 | 0.096797 | -55.0095 | 64.7415 | -60.0037 | -59.9167 | 49.4019 | 13.6963 | -3.2364 | -2.1149 | 64.7461 | -60.0632 | -0.22888 | -0.013733 | 4.7653 | -0.14191 | -15.3534 | -0.28839 | -0.009155 | 4.9942 | 56.5384 | 57.6599 | 109.1766 | 124.5163 | 4.7653 | 124.5209 | 73.4711 | -0.28839 | 124.5163 | 4.7653 | 73.4711 | 109.1766 | 124.5209 | -124.7589 | -124.8184
1639.6406 | 124.8962 | -59.7015 | 64.8422 | 0.14976 | 0.032763 | 0.032631 | 0.024362 | 0.063549 | 0.0062591 | 0.095515 | -54.982 | 64.8193 | -59.9808 | -59.8618 | 49.4522 | 13.6917 | -3.1815 | -2.0691 | 64.8239 | -60.0128 | -0.27924 | -0.022888 | 4.7195 | -0.16022 | -15.39 | -0.31128 | -0.01831 | 4.9988 | 56.5201 | 57.6324 | 109.1537 | 124.5209 | 4.7195 | 124.5255 | 73.3932 | -0.31128 | 124.5209 | 4.7195 | 73.3932 | 109.1537 | 124.5255 | -124.823 | -124.855
1640.6406 | 124.9146 | -59.7702 | 64.801 | -0.29274 | 0.027637 | 0.030708 | 0.02073 | 0.062908 | 0.0075409 | 0.096583 | -55.0049 | 64.7644 | -59.9899 | -59.8938 | 49.4247 | 13.6734 | -3.1265 | -2.0096 | 64.7873 | -60.0586 | -0.21973 | -0.036621 | 4.7653 | -0.1236 | -15.3763 | -0.28839 | -0.013733 | 4.985 | 56.6437 | 57.7606 | 109.1949 | 124.5346 | 4.7653 | 124.5575 | 73.4436 | -0.28839 | 124.5346 | 4.7653 | 73.4436 | 109.1949 | 124.5575 | -124.791 | -124.8596
1641.6406 | 124.8459 | -59.8251 | 64.8331 | 0.13451 | 0.031909 | 0.034554 | 0.02543 | 0.06483 | 0.0068999 | 0.098079 | -55.1102 | 64.8102 | -60.0906 | -60.0266 | 49.2416 | 13.4903 | -3.0716 | -2.2476 | 64.7964 | -60.1227 | -0.2655 | -0.022888 | 4.715 | -0.20142 | -15.5914 | -0.29755 | -0.036621 | 4.9805 | 56.7535 | 57.5775 | 109.0668 | 124.6353 | 4.715 | 124.6216 | 73.3154 | -0.29755 | 124.6353 | 4.715 | 73.3154 | 109.0668 | 124.6216 | -124.9237 | -124.9557
1642.6406 | 124.9054 | -59.7107 | 64.8514 | 0.21843 | 0.031268 | 0.029213 | 0.024148 | 0.065899 | 0.0064727 | 0.098506 | -55.0278 | 64.8651 | -59.967 | -59.903 | 49.3607 | 13.6963 | -3.0808 | -2.1378 | 64.8285 | -60.0037 | -0.25635 | 0.013733 | 4.6829 | -0.19226 | -15.4907 | -0.29297 | -0.022888 | 4.9393 | 56.6299 | 57.5729 | 109.0713 | 124.5758 | 4.6829 | 124.5392 | 73.407 | -0.29297 | 124.5758 | 4.6829 | 73.407 | 109.0713 | 124.5392 | -124.8184 | -124.855
1643.6406 | 124.9466 | -59.7061 | 64.8376 | 0.15739 | 0.032123 | 0.030495 | 0.021798 | 0.065258 | 0.011173 | 0.099788 | -54.9866 | 64.7964 | -59.9762 | -60.0632 | 49.4751 | 13.9023 | -3.1631 | -2.1469 | 64.8056 | -59.9899 | -0.27008 | -0.041198 | 4.7195 | -0.35705 | -15.3625 | -0.28381 | -0.032043 | 4.9896 | 56.543 | 57.5592 | 109.1812 | 124.5026 | 4.7195 | 124.5117 | 73.6084 | -0.28381 | 124.5026 | 4.7195 | 73.6084 | 109.1812 | 124.5117 | -124.8138 | -124.8276
1644.6406 | 125.0015 | -59.7839 | 64.769 | 0.16502 | 0.029773 | 0.030495 | 0.023934 | 0.065044 | 0.0068999 | 0.096797 | -55.0369 | 64.7552 | -60.054 | -59.9213 | 49.3057 | 13.6642 | -3.2639 | -2.3712 | 64.7461 | -60.0677 | -0.27008 | -0.013733 | 4.747 | -0.13733 | -15.4633 | -0.28381 | -0.022888 | 5.0171 | 56.5201 | 57.4127 | 109.0897 | 124.5392 | 4.747 | 124.53 | 73.4482 | -0.28381 | 124.5392 | 4.747 | 73.4482 | 109.0897 | 124.53 | -124.823 | -124.8367
1645.6406 | 124.8871 | -59.7015 | 64.7964 | 0.10399 | 0.031482 | 0.034554 | 0.022653 | 0.066112 | 0.0049773 | 0.096797 | -54.9866 | 64.7964 | -59.9808 | -59.8801 | 49.3103 | 13.7604 | -3.2318 | -2.2614 | 64.7873 | -60.0174 | -0.27924 | 0 | 4.715 | -0.17853 | -15.4861 | -0.31586 | -0.009156 | 4.9942 | 56.4697 | 57.4402 | 109.0118 | 124.498 | 4.715 | 124.4888 | 73.4619 | -0.31586 | 124.498 | 4.715 | 73.4619 | 109.0118 | 124.4888 | -124.7772 | -124.8138
1646.6406 | 124.9008 | -59.697 | 64.8193 | 0.13451 | 0.031909 | 0.034981 | 0.023721 | 0.065685 | 0.0064727 | 0.097651 | -55.0003 | 64.7964 | -59.9899 | -59.8938 | 49.2737 | 13.7375 | -3.1403 | -2.2247 | 64.7736 | -60.0128 | -0.29297 | -0.022888 | 4.6967 | -0.19684 | -15.5457 | -0.31586 | -0.045776 | 4.9896 | 56.5567 | 57.4722 | 108.9706 | 124.4934 | 4.6967 | 124.4705 | 73.4344 | -0.31586 | 124.4934 | 4.6967 | 73.4344 | 108.9706 | 124.4705 | -124.8093 | -124.8322
1647.6406 | 124.8459 | -59.729 | 64.8788 | 0.11925 | 0.030841 | 0.033058 | 0.018807 | 0.063549 | 0.0081817 | 0.09701 | -55.0323 | 64.7736 | -59.9899 | -59.9258 | 49.2599 | 13.6871 | -3.0533 | -2.3209 | 64.8148 | -59.9945 | -0.26092 | -0.10528 | 4.6967 | -0.19684 | -15.6189 | -0.2655 | -0.064087 | 4.9576 | 56.6757 | 57.4081 | 108.989 | 124.5026 | 4.6967 | 124.5438 | 73.4161 | -0.2655 | 124.5026 | 4.6967 | 73.4161 | 108.989 | 124.5438 | -124.8688 | -124.8734
1648.6406 | 124.8138 | -59.7473 | 64.8468 | 0.0811 | 0.035113 | 0.036263 | 0.027993 | 0.064403 | 0.0090363 | 0.098292 | -55.0781 | 64.8193 | -60.022 | -60.0082 | 49.1409 | 13.6047 | -2.7969 | -2.1698 | 64.8148 | -60.0449 | -0.27466 | -0.027466 | 4.6692 | -0.26093 | -15.7059 | -0.29755 | -0.032044 | 4.9438 | 56.9504 | 57.5775 | 108.8882 | 124.5667 | 4.6692 | 124.5621 | 73.3521 | -0.29755 | 124.5667 | 4.6692 | 73.3521 | 108.8882 | 124.5621 | -124.8688 | -124.8917
1649.6406 | 124.8825 | -59.7382 | 64.8193 | 0.2108 | 0.031909 | 0.032845 | 0.023934 | 0.065685 | 0.0079681 | 0.098506 | -55.0095 | 64.8331 | -59.9991 | -59.9213 | 49.173 | 13.6734 | -2.916 | -2.1606 | 64.7827 | -60.0403 | -0.26093 | 0.013733 | 4.7287 | -0.18311 | -15.6464 | -0.30212 | -0.036621 | 4.9896 | 56.8222 | 57.5775 | 108.9111 | 124.5712 | 4.7287 | 124.5209 | 73.4116 | -0.30212 | 124.5712 | 4.7287 | 73.4116 | 108.9111 | 124.5209 | -124.8184 | -124.8596
1650.6406 | 124.8688 | -59.7656 | 64.7552 | 0.18791 | 0.032336 | 0.032845 | 0.023507 | 0.065258 | 0.0073273 | 0.09637 | -54.9957 | 64.7278 | -60.0357 | -60.1364 | 49.2783 | 13.9114 | -2.916 | -2.092 | 64.7415 | -60.0586 | -0.27008 | -0.027466 | 4.7699 | -0.37079 | -15.477 | -0.29297 | -0.013733 | 5.04 | 56.8497 | 57.6736 | 109.0439 | 124.4934 | 4.7699 | 124.5071 | 73.6771 | -0.29297 | 124.4934 | 4.7699 | 73.6771 | 109.0439 | 124.5071 | -124.791 | -124.8138
1651.6406 | 124.9832 | -59.761 | 64.8239 | 0.15739 | 0.028705 | 0.033058 | 0.024148 | 0.066753 | 0.0077545 | 0.09936 | -54.95 | 64.7781 | -60.0082 | -59.9075 | 49.1821 | 13.8886 | -2.948 | -2.33 | 64.7552 | -60.0861 | -0.24719 | -0.045777 | 4.8111 | -0.14649 | -15.6418 | -0.32501 | -0.068665 | 5.0583 | 56.813 | 57.431 | 108.9432 | 124.5392 | 4.8111 | 124.5163 | 73.6496 | -0.32501 | 124.5392 | 4.8111 | 73.6496 | 108.9432 | 124.5163 | -124.8322 | -124.91
1652.6406 | 124.9191 | -59.7473 | 64.8239 | -0.018082 | 0.028064 | 0.029427 | 0.01838 | 0.062908 | 0.0064727 | 0.098933 | -55.0095 | 64.7415 | -60.0174 | -59.935 | 49.1821 | 13.9206 | -2.8519 | -2.1423 | 64.8102 | -60.0174 | -0.27008 | -0.082398 | 4.7379 | -0.18768 | -15.6418 | -0.27008 | -0.013733 | 5.0079 | 56.8954 | 57.605 | 108.9294 | 124.4888 | 4.7379 | 124.5575 | 73.6679 | -0.27008 | 124.4888 | 4.7379 | 73.6679 | 108.9294 | 124.5575 | -124.8413 | -124.8413
1653.6406 | 124.8917 | -59.7153 | 64.8331 | 0.18791 | 0.029986 | 0.035194 | 0.027139 | 0.063549 | 0.0083953 | 0.099147 | -54.9133 | 64.8422 | -59.9533 | -59.8755 | 49.1913 | 13.8931 | -2.8793 | -2.092 | 64.7736 | -60.0311 | -0.23804 | 0.009155 | 4.8019 | -0.16022 | -15.6418 | -0.31586 | -0.059509 | 5.04 | 56.8359 | 57.6233 | 108.9066 | 124.5575 | 4.8019 | 124.4888 | 73.6084 | -0.31586 | 124.5575 | 4.8019 | 73.6084 | 108.9066 | 124.4888 | -124.7864 | -124.8642
1654.6406 | 124.8001 | -59.7885 | 64.7964 | 0.14976 | 0.031909 | 0.033485 | 0.026925 | 0.065044 | 0.0075409 | 0.09936 | -55.0369 | 64.7736 | -60.0861 | -60.0174 | 49.0219 | 13.7787 | -2.8244 | -2.2339 | 64.7552 | -60.1135 | -0.29755 | -0.022888 | 4.7516 | -0.22888 | -15.7745 | -0.32501 | -0.041199 | 5.0491 | 56.9641 | 57.5546 | 108.8104 | 124.5621 | 4.7516 | 124.5438 | 73.5672 | -0.32501 | 124.5621 | 4.7516 | 73.5672 | 108.8104 | 124.5438 | -124.8825 | -124.91
1655.6406 | 124.8047 | -59.7885 | 64.7964 | 0.12688 | 0.033832 | 0.034126 | 0.023934 | 0.067821 | 0.0062591 | 0.098292 | -55.0003 | 64.8239 | -60.0586 | -60.0174 | 48.999 | 13.8702 | -2.7603 | -2.211 | 64.7781 | -60.0815 | -0.27008 | 0.027466 | 4.7882 | -0.22888 | -15.7974 | -0.29297 | -0.018311 | 5.0583 | 57.0282 | 57.5775 | 108.7875 | 124.6124 | 4.7882 | 124.5667 | 73.6588 | -0.29297 | 124.6124 | 4.7882 | 73.6588 | 108.7875 | 124.5667 | -124.855 | -124.8779
1656.6406 | 124.8596 | -59.7748 | 64.769 | 0.16502 | 0.031268 | 0.031349 | 0.024789 | 0.063976 | 0.0058319 | 0.097865 | -54.9774 | 64.769 | -60.0815 | -59.9899 | 49.0585 | 13.884 | -2.8885 | -2.2018 | 64.7232 | -60.0906 | -0.3067 | 0 | 4.7974 | -0.21515 | -15.7104 | -0.31586 | -0.045776 | 5.1041 | 56.8863 | 57.5729 | 108.8333 | 124.5438 | 4.7974 | 124.498 | 73.6588 | -0.31586 | 124.5438 | 4.7974 | 73.6588 | 108.8333 | 124.498 | -124.8505 | -124.8596
1657.6406 | 124.91 | -59.7702 | 64.7552 | -0.04097 | 0.028064 | 0.030708 | 0.015389 | 0.065258 | 0.0079681 | 0.09701 | -54.9957 | 64.7003 | -60.0677 | -59.9716 | 49.0906 | 13.9847 | -2.829 | -2.1194 | 64.7598 | -60.0449 | -0.29755 | -0.054932 | 4.7745 | -0.20142 | -15.6647 | -0.27466 | 0.004578 | 5.072 | 56.9412 | 57.6508 | 108.8608 | 124.4705 | 4.7745 | 124.53 | 73.7549 | -0.27466 | 124.4705 | 4.7745 | 73.7549 | 108.8608 | 124.53 | -124.823 | -124.8001
1658.6406 | 124.8962 | -59.7656 | 64.7781 | 0.14976 | 0.03255 | 0.037758 | 0.023934 | 0.063762 | 0.0079681 | 0.098506 | -54.895 | 64.7232 | -60.0311 | -60.1685 | 48.9532 | 14.035 | -2.7328 | -2.1378 | 64.7415 | -60.0586 | -0.2655 | -0.054931 | 4.8706 | -0.40283 | -15.8249 | -0.29297 | -0.036621 | 5.1361 | 57.0328 | 57.6279 | 108.7189 | 124.4888 | 4.8706 | 124.5071 | 73.8007 | -0.29297 | 124.4888 | 4.8706 | 73.8007 | 108.7189 | 124.5071 | -124.8093 | -124.8367
1659.6406 | 124.8962 | -59.697 | 64.8376 | 0.16502 | 0.029986 | 0.030708 | 0.025216 | 0.06483 | 0.0064727 | 0.098079 | -54.8126 | 64.7964 | -59.9762 | -59.8755 | 49.0814 | 14.0808 | -3.1082 | -2.0325 | 64.7461 | -60.0357 | -0.27924 | -0.041198 | 4.8843 | -0.17853 | -15.7562 | -0.33875 | -0.091552 | 5.1636 | 56.5887 | 57.6645 | 108.7784 | 124.4934 | 4.8843 | 124.4431 | 73.7778 | -0.33875 | 124.4934 | 4.8843 | 73.7778 | 108.7784 | 124.4431 | -124.8138 | -124.8734
1660.6406 | 124.855 | -59.7656 | 64.7095 | 0.14976 | 0.031268 | 0.033272 | 0.024789 | 0.064403 | 0.0041229 | 0.098506 | -54.863 | 64.769 | -60.0449 | -59.9304 | 49.0631 | 14.0579 | -2.6962 | -2.0554 | 64.7369 | -60.0677 | -0.27924 | 0.059509 | 4.9026 | -0.16479 | -15.6464 | -0.30212 | 0.027465 | 5.1819 | 57.0694 | 57.7103 | 108.8287 | 124.5346 | 4.9026 | 124.5026 | 73.8235 | -0.30212 | 124.5346 | 4.9026 | 73.8235 | 108.8287 | 124.5026 | -124.7543 | -124.7772
1661.6406 | 124.8322 | -59.7656 | 64.8056 | 0.11162 | 0.032123 | 0.03434 | 0.025643 | 0.066753 | 0.0066863 | 0.099147 | -54.9133 | 64.7827 | -60.0586 | -59.9991 | 48.9761 | 13.9755 | -2.6047 | -2.1927 | 64.7598 | -60.0906 | -0.29297 | -0.022888 | 4.8523 | -0.23346 | -15.8295 | -0.32501 | -0.045776 | 5.1453 | 57.1609 | 57.5729 | 108.7418 | 124.5483 | 4.8523 | 124.5255 | 73.7412 | -0.32501 | 124.5483 | 4.8523 | 73.7412 | 108.7418 | 124.5255 | -124.8642 | -124.8962
1662.6406 | 124.9146 | -59.7473 | 64.7873 | 0.073471 | 0.030627 | 0.032417 | 0.017953 | 0.063549 | 0.0060455 | 0.09936 | -54.8859 | 64.7186 | -60.0311 | -59.935 | 49.0128 | 14.0762 | -2.655 | -2.124 | 64.7873 | -60.0082 | -0.28381 | -0.068664 | 4.8615 | -0.18768 | -15.7745 | -0.26093 | 0 | 5.1453 | 57.0923 | 57.6233 | 108.7601 | 124.4659 | 4.8615 | 124.5346 | 73.8235 | -0.26093 | 124.4659 | 4.8615 | 73.8235 | 108.7601 | 124.5346 | -124.8184 | -124.7955
1663.6406 | 124.8734 | -59.7702 | 64.7736 | 0.22606 | 0.0302 | 0.033913 | 0.025857 | 0.064403 | 0.0058319 | 0.098079 | -54.8126 | 64.7781 | -60.022 | -59.9121 | 48.999 | 14.0167 | -2.6642 | -2.1286 | 64.7324 | -60.0677 | -0.25177 | 0.004577 | 4.9576 | -0.14191 | -15.7745 | -0.29755 | -0.041199 | 5.2094 | 57.106 | 57.6416 | 108.7692 | 124.5483 | 4.9576 | 124.5026 | 73.7869 | -0.29755 | 124.5483 | 4.9576 | 73.7869 | 108.7692 | 124.5026 | -124.7955 | -124.8413
1664.6406 | 124.8825 | -59.8251 | 64.7049 | -0.079117 | 0.029132 | 0.035194 | 0.020303 | 0.06483 | 0.0073273 | 0.097865 | -54.8355 | 64.6545 | -60.0769 | -59.9854 | 48.9441 | 14.0991 | -2.7145 | -2.1515 | 64.7049 | -60.1273 | -0.25177 | -0.050354 | 4.9896 | -0.16022 | -15.7608 | -0.30212 | 0 | 5.2414 | 57.1106 | 57.6736 | 108.7692 | 124.4797 | 4.9896 | 124.53 | 73.9243 | -0.30212 | 124.4797 | 4.9896 | 73.9243 | 108.7692 | 124.53 | -124.7818 | -124.8322
1665.6406 | 124.8825 | -59.7519 | 64.7507 | -1.6584 | 0.028918 | 0.033485 | 0.023507 | 0.064403 | 0.0077545 | 0.098079 | -54.776 | 64.7232 | -60.0174 | -59.9442 | 48.9807 | 14.0991 | -2.6779 | -2.1835 | 64.7369 | -60.0586 | -0.2655 | -0.027465 | 4.9759 | -0.19226 | -15.77 | -0.3067 | -0.013733 | 5.2414 | 57.074 | 57.5684 | 108.7326 | 124.4751 | 4.9759 | 124.4888 | 73.851 | -0.3067 | 124.4751 | 4.9759 | 73.851 | 108.7326 | 124.4888 | -124.7681 | -124.8093
1666.6406 | 124.8779 | -59.7473 | 64.7598 | 2.4386 | 0.030841 | 0.030068 | 0.021585 | 0.063976 | 0.0081817 | 0.099147 | -54.6249 | 64.7278 | -59.9945 | -59.8755 | 49.0585 | 14.1769 | -2.6642 | -2.179 | 64.7461 | -60.0403 | -0.24719 | -0.032044 | 5.1224 | -0.12817 | -15.7013 | -0.29297 | -0.013733 | 5.3696 | 57.0831 | 57.5684 | 108.8058 | 124.4751 | 5.1224 | 124.4934 | 73.9243 | -0.29297 | 124.4751 | 5.1224 | 73.9243 | 108.8058 | 124.4934 | -124.7543 | -124.8001
1667.6406 | 124.8871 | -59.7473 | 64.7781 | -0.033341 | 0.028064 | 0.029213 | 0.019448 | 0.062053 | 0.0090363 | 0.099574 | -54.7485 | 64.7278 | -60.054 | -59.9396 | 49.0219 | 14.1266 | -2.4445 | -2.0599 | 64.7736 | -60.0174 | -0.3067 | -0.050354 | 4.9988 | -0.19226 | -15.7562 | -0.27008 | -0.004577 | 5.3055 | 57.3029 | 57.6874 | 108.7692 | 124.4751 | 4.9988 | 124.5209 | 73.8739 | -0.27008 | 124.4751 | 4.9988 | 73.8739 | 108.7692 | 124.5209 | -124.8322 | -124.7955
1668.6406 | 124.8505 | -59.7153 | 64.8193 | 0.14976 | 0.031054 | 0.03434 | 0.026498 | 0.062694 | 0.0096771 | 0.099147 | -54.6799 | 64.7964 | -60.0174 | -59.9075 | 48.9899 | 14.0808 | -2.4765 | -2.1194 | 64.7873 | -60.0128 | -0.30212 | -0.022888 | 5.0354 | -0.19226 | -15.8295 | -0.29755 | -0.032044 | 5.3375 | 57.2388 | 57.5958 | 108.7051 | 124.5117 | 5.0354 | 124.5026 | 73.7961 | -0.29755 | 124.5117 | 5.0354 | 73.7961 | 108.7051 | 124.5026 | -124.8367 | -124.8322
1669.6406 | 124.8825 | -59.7153 | 64.8239 | 0.21843 | 0.03255 | 0.034767 | 0.026711 | 0.065258 | 0.0056183 | 0.10043 | -54.6341 | 64.801 | -59.9854 | -59.8801 | 49.0402 | 14.1083 | -2.3849 | -2.092 | 64.8056 | -60.0037 | -0.27008 | -0.022889 | 5.0812 | -0.16479 | -15.7837 | -0.28839 | -0.018311 | 5.3513 | 57.3303 | 57.6233 | 108.7555 | 124.5163 | 5.0812 | 124.5209 | 73.8235 | -0.28839 | 124.5163 | 5.0812 | 73.8235 | 108.7555 | 124.5209 | -124.8093 | -124.8276
1670.6406 | 124.8962 | -59.6649 | 64.8468 | 0.14214 | 0.032336 | 0.035194 | 0.019876 | 0.06718 | 0.0077545 | 0.09701 | -54.4144 | 64.7919 | -59.9487 | -59.7885 | 49.0906 | 14.1312 | -2.2751 | -1.9913 | 64.8422 | -59.9396 | -0.28381 | -0.054932 | 5.2505 | -0.1236 | -15.7562 | -0.27466 | -0.004578 | 5.5344 | 57.3898 | 57.6736 | 108.7555 | 124.4568 | 5.2505 | 124.5071 | 73.7961 | -0.27466 | 124.4568 | 5.2505 | 73.7961 | 108.7555 | 124.5071 | -124.7955 | -124.7864
1671.6406 | 124.8688 | -59.642 | 64.9017 | 0.12688 | 0.031054 | 0.033485 | 0.020303 | 0.066967 | 0.0077545 | 0.099574 | -54.5105 | 64.8285 | -59.8938 | -59.8068 | 49.1135 | 14.2364 | -2.243 | -1.9318 | 64.8743 | -59.9121 | -0.25177 | -0.073242 | 5.1315 | -0.16479 | -15.7883 | -0.27008 | -0.027465 | 5.3833 | 57.399 | 57.7103 | 108.7555 | 124.4705 | 5.1315 | 124.5163 | 73.8785 | -0.27008 | 124.4705 | 5.1315 | 73.8785 | 108.7555 | 124.5163 | -124.7955 | -124.8138
1672.6406 | 124.8917 | -59.6832 | 64.888 | -0.033341 | 0.028918 | 0.035194 | 0.020516 | 0.062053 | 0.0079681 | 0.1 | -54.5883 | 64.7873 | -59.9487 | -59.848 | 49.118 | 14.2181 | -2.1561 | -1.9135 | 64.856 | -59.9396 | -0.2655 | -0.10071 | 5.0949 | -0.16479 | -15.77 | -0.25635 | -0.032043 | 5.3604 | 57.5272 | 57.7698 | 108.8013 | 124.4705 | 5.0949 | 124.5392 | 73.9014 | -0.25635 | 124.4705 | 5.0949 | 73.9014 | 108.8013 | 124.5392 | -124.8367 | -124.8276
1673.6406 | 124.8779 | -59.697 | 64.8697 | 0.13451 | 0.031909 | 0.033699 | 0.024362 | 0.062481 | 0.0071137 | 0.099147 | -54.4922 | 64.7964 | -59.9442 | -59.8434 | 49.1135 | 14.2319 | -2.2247 | -1.9318 | 64.7964 | -59.9625 | -0.24719 | -0.073242 | 5.2048 | -0.14649 | -15.7562 | -0.2655 | -0.073242 | 5.452 | 57.4722 | 57.7652 | 108.8104 | 124.4934 | 5.2048 | 124.4934 | 73.9288 | -0.2655 | 124.4934 | 5.2048 | 73.9288 | 108.8104 | 124.4934 | -124.8138 | -124.8322
1674.6406 | 124.8917 | -59.7015 | 64.8193 | 0.16502 | 0.031054 | 0.034554 | 0.023294 | 0.063976 | 0.0077545 | 0.097651 | -54.5334 | 64.7598 | -59.9625 | -59.8709 | 49.054 | 14.1861 | -2.1332 | -1.886 | 64.8102 | -59.9945 | -0.26093 | -0.059509 | 5.1682 | -0.16937 | -15.7654 | -0.29297 | -0.009155 | 5.4291 | 57.5684 | 57.8156 | 108.7555 | 124.4614 | 5.1682 | 124.5117 | 73.8876 | -0.29297 | 124.4614 | 5.1682 | 73.8876 | 108.7555 | 124.5117 | -124.7818 | -124.8138
1675.6406 | 124.9008 | -59.729 | 64.8285 | 0.16502 | 0.030627 | 0.034767 | 0.025216 | 0.063762 | 0.0064727 | 0.097865 | -54.483 | 64.8148 | -59.9442 | -59.8526 | 49.0768 | 14.3372 | -2.0279 | -1.8768 | 64.8331 | -59.9625 | -0.21515 | -0.013733 | 5.246 | -0.1236 | -15.7516 | -0.23346 | 0.004578 | 5.4611 | 57.7011 | 57.8522 | 108.8058 | 124.5438 | 5.246 | 124.5621 | 74.0662 | -0.23346 | 124.5438 | 5.246 | 74.0662 | 108.8058 | 124.5621 | -124.7726 | -124.791
1676.6406 | 124.9237 | -59.6603 | 64.8422 | 0.10399 | 0.031909 | 0.033913 | 0.023721 | 0.06483 | 0.0062591 | 0.09936 | -54.3915 | 64.8239 | -59.935 | -59.8251 | 49.1455 | 14.3875 | -2.0187 | -1.9226 | 64.8468 | -59.9533 | -0.27466 | -0.01831 | 5.2689 | -0.16479 | -15.6967 | -0.29297 | 0.004578 | 5.5435 | 57.6416 | 57.7377 | 108.8058 | 124.4843 | 5.2689 | 124.5071 | 74.0479 | -0.29297 | 124.4843 | 5.2689 | 74.0479 | 108.8058 | 124.5071 | -124.7772 | -124.7955
1677.6406 | 124.8825 | -59.6558 | 64.8834 | -0.056229 | 0.028277 | 0.029854 | 0.019876 | 0.061626 | 0.0056183 | 0.098933 | -54.3594 | 64.7919 | -59.9304 | -59.7931 | 49.1592 | 14.447 | -1.9135 | -1.8539 | 64.8468 | -59.9213 | -0.27466 | -0.091553 | 5.2963 | -0.13733 | -15.7242 | -0.2655 | -0.036621 | 5.571 | 57.7423 | 57.8018 | 108.815 | 124.4476 | 5.2963 | 124.5026 | 74.1028 | -0.2655 | 124.4476 | 5.2963 | 74.1028 | 108.815 | 124.5026 | -124.8138 | -124.8047
1678.6406 | 124.8779 | -59.6741 | 64.8972 | 0.14976 | 0.031482 | 0.030708 | 0.022653 | 0.061412 | 0.0071137 | 0.098933 | -54.3365 | 64.8102 | -59.935 | -59.8434 | 49.1501 | 14.4516 | -1.9089 | -1.8677 | 64.8193 | -59.9487 | -0.26093 | -0.086975 | 5.3375 | -0.16937 | -15.7471 | -0.27466 | -0.07782 | 5.5984 | 57.7652 | 57.8064 | 108.8242 | 124.4843 | 5.3375 | 124.4934 | 74.1257 | -0.27466 | 124.4843 | 5.3375 | 74.1257 | 108.8242 | 124.4934 | -124.8322 | -124.8459
1679.6406 | 124.8688 | -59.7382 | 64.8376 | 0.08873 | 0.032763 | 0.032417 | 0.020303 | 0.062694 | 0.0056183 | 0.097651 | -54.3686 | 64.7461 | -59.9716 | -59.8892 | 49.0906 | 14.3646 | -1.8723 | -1.8265 | 64.7873 | -59.9854 | -0.23346 | -0.091552 | 5.3696 | -0.15106 | -15.7471 | -0.24719 | -0.050354 | 5.603 | 57.8659 | 57.9117 | 108.8287 | 124.4843 | 5.3696 | 124.5255 | 74.1028 | -0.24719 | 124.4843 | 5.3696 | 74.1028 | 108.8287 | 124.5255 | -124.8093 | -124.823
1680.6406 | 124.8413 | -59.7382 | 64.8193 | 0.15739 | 0.032977 | 0.03199 | 0.022653 | 0.062481 | 0.0077545 | 0.099147 | -54.3457 | 64.7278 | -60.0082 | -59.8892 | 49.0723 | 14.415 | -1.8173 | -1.7761 | 64.7598 | -60.0037 | -0.27008 | -0.091553 | 5.3925 | -0.15106 | -15.7471 | -0.2655 | -0.059509 | 5.6625 | 57.9208 | 57.962 | 108.8104 | 124.4659 | 5.3925 | 124.498 | 74.1531 | -0.2655 | 124.4659 | 5.3925 | 74.1531 | 108.8104 | 124.498 | -124.8276 | -124.823
1681.6406 | 124.8688 | -59.6786 | 64.8605 | 0.11162 | 0.030841 | 0.032845 | 0.020516 | 0.062481 | 0.0086089 | 0.098292 | -54.2679 | 64.7919 | -59.9304 | -59.8389 | 49.0997 | 14.4608 | -1.6663 | -1.6891 | 64.8239 | -59.935 | -0.25177 | -0.068665 | 5.4108 | -0.16022 | -15.7608 | -0.25635 | -0.036621 | 5.6625 | 58.0124 | 57.9895 | 108.7784 | 124.4705 | 5.4108 | 124.5026 | 74.1394 | -0.25635 | 124.4705 | 5.4108 | 74.1394 | 108.7784 | 124.5026 | -124.791 | -124.7955
1682.6406 | 124.8596 | -59.729 | 64.7827 | 0.012436 | 0.028705 | 0.027931 | 0.020303 | 0.062053 | 0.0081817 | 0.097865 | -54.3869 | 64.7507 | -60.0357 | -59.9304 | 49.0448 | 14.2914 | -1.5656 | -1.7303 | 64.7873 | -60.022 | -0.3067 | -0.032044 | 5.3421 | -0.20142 | -15.7379 | -0.29297 | 0.004577 | 5.6488 | 58.1635 | 57.9987 | 108.7738 | 124.4797 | 5.3421 | 124.5163 | 74.0204 | -0.29297 | 124.4797 | 5.3421 | 74.0204 | 108.7738 | 124.5163 | -124.8184 | -124.8047
1683.6406 | 124.8138 | -59.6878 | 64.8514 | 0.14214 | 0.030627 | 0.031563 | 0.020303 | 0.06184 | 0.0073273 | 0.099574 | -54.277 | 64.769 | -59.9487 | -59.8801 | 49.0768 | 14.3646 | -1.4923 | -1.7212 | 64.8376 | -59.9533 | -0.26093 | -0.082397 | 5.4108 | -0.19226 | -15.7745 | -0.2655 | -0.013733 | 5.6717 | 58.1955 | 57.9666 | 108.7646 | 124.4568 | 5.4108 | 124.5255 | 74.0524 | -0.2655 | 124.4568 | 5.4108 | 74.0524 | 108.7646 | 124.5255 | -124.8001 | -124.8047
1684.6406 | 124.8688 | -59.6878 | 64.8788 | 0.12688 | 0.032763 | 0.032417 | 0.021585 | 0.063762 | 0.0094635 | 0.098079 | -54.1946 | 64.7873 | -59.9396 | -59.8434 | 49.0494 | 14.4012 | -1.5518 | -1.7212 | 64.8193 | -59.9487 | -0.25177 | -0.091553 | 5.4932 | -0.15564 | -15.8295 | -0.26093 | -0.059509 | 5.7449 | 58.136 | 57.9666 | 108.7372 | 124.4751 | 5.4932 | 124.5071 | 74.0891 | -0.26093 | 124.4751 | 5.4932 | 74.0891 | 108.7372 | 124.5071 | -124.8184 | -124.8276
1685.6406 | 124.8596 | -59.6741 | 64.8788 | 0.14976 | 0.028705 | 0.032417 | 0.018807 | 0.061412 | 0.0073273 | 0.097651 | -54.2313 | 64.7964 | -59.935 | -59.8709 | 49.054 | 14.3051 | -1.4603 | -1.6983 | 64.8285 | -59.9487 | -0.26093 | -0.082397 | 5.4428 | -0.19684 | -15.8249 | -0.27466 | -0.050354 | 5.7037 | 58.2138 | 57.9758 | 108.728 | 124.4705 | 5.4428 | 124.5026 | 73.9792 | -0.27466 | 124.4705 | 5.4428 | 73.9792 | 108.728 | 124.5026 | -124.8138 | -124.8276
1686.6406 | 124.8642 | -59.6283 | 64.9292 | 0.08873 | 0.031054 | 0.03199 | 0.019876 | 0.061626 | 0.0047637 | 0.098506 | -54.1672 | 64.8376 | -59.8938 | -59.8297 | 49.0952 | 14.4012 | -1.2909 | -1.5472 | 64.8605 | -59.9167 | -0.2655 | -0.091553 | 5.4611 | -0.20142 | -15.834 | -0.28839 | -0.068664 | 5.7266 | 58.3374 | 58.0811 | 108.7234 | 124.4659 | 5.4611 | 124.4888 | 74.0295 | -0.28839 | 124.4659 | 5.4611 | 74.0295 | 108.7234 | 124.4888 | -124.823 | -124.8459
1687.6406 | 124.8962 | -59.642 | 64.8926 | -0.14015 | 0.029986 | 0.031136 | 0.020944 | 0.06184 | 0.0079681 | 0.096583 | -54.1122 | 64.7964 | -59.9167 | -59.761 | 49.1364 | 14.4928 | -1.1169 | -1.3092 | 64.8376 | -59.9121 | -0.27466 | -0.09613 | 5.5298 | -0.11902 | -15.7562 | -0.27008 | -0.054932 | 5.8044 | 58.5251 | 58.3328 | 108.7784 | 124.4385 | 5.5298 | 124.4797 | 74.1348 | -0.27008 | 124.4385 | 5.5298 | 74.1348 | 108.7784 | 124.4797 | -124.8093 | -124.8047
1688.6406 | 124.8871 | -59.6466 | 64.9292 | 0.10399 | 0.029986 | 0.032417 | 0.019876 | 0.063121 | 0.0060455 | 0.097651 | -54.1672 | 64.8148 | -59.9304 | -59.8526 | 49.0311 | 14.3005 | -0.92468 | -1.2131 | 64.8422 | -59.935 | -0.28381 | -0.11444 | 5.4794 | -0.20599 | -15.8981 | -0.28839 | -0.086975 | 5.7632 | 58.7219 | 58.4335 | 108.6777 | 124.4614 | 5.4794 | 124.4888 | 73.9471 | -0.28839 | 124.4614 | 5.4794 | 73.9471 | 108.6777 | 124.4888 | -124.8596 | -124.8642
1689.6406 | 124.8734 | -59.6146 | 64.888 | 0.14214 | 0.031909 | 0.030922 | 0.02308 | 0.062267 | 0.0075409 | 0.097438 | -54.0482 | 64.8239 | -59.9213 | -59.8022 | 49.0768 | 14.3097 | -0.78735 | -0.95673 | 64.8514 | -59.8984 | -0.3067 | -0.064086 | 5.5664 | -0.18768 | -15.8112 | -0.28381 | -0.036621 | 5.8731 | 58.8272 | 58.6578 | 108.6914 | 124.4385 | 5.5664 | 124.4659 | 73.9243 | -0.28381 | 124.4385 | 5.5664 | 73.9243 | 108.6914 | 124.4659 | -124.8093 | -124.7864
1690.6406 | 124.8871 | -59.6466 | 64.8834 | 0.15739 | 0.031482 | 0.03199 | 0.021157 | 0.06419 | 0.0081817 | 0.096583 | -54.0344 | 64.7873 | -59.9304 | -59.8022 | 49.0402 | 14.2914 | -0.55389 | -0.75073 | 64.8468 | -59.9396 | -0.28381 | -0.096131 | 5.6122 | -0.15564 | -15.8432 | -0.29297 | -0.036621 | 5.896 | 59.0927 | 58.8959 | 108.6868 | 124.4339 | 5.6122 | 124.4934 | 73.938 | -0.29297 | 124.4339 | 5.6122 | 73.938 | 108.6868 | 124.4934 | -124.8138 | -124.823
1691.6406 | 124.8596 | -59.7427 | 64.7919 | 0.0811 | 0.034045 | 0.036903 | 0.021585 | 0.06419 | 0.0081817 | 0.098079 | -59.1522 | 64.8697 | -59.6832 | -59.7885 | 49.0311 | 14.0854 | -0.70953 | -0.9201 | 64.7644 | -60.0082 | 0.059509 | 0.07782 | 0.59051 | -0.045776 | -15.7608 | -0.2655 | -0.027466 | 0.53101 | 59.0332 | 58.8226 | 108.7738 | 124.6124 | 0.59051 | 124.5071 | 73.8281 | -0.2655 | 124.6124 | 0.59051 | 73.8281 | 108.7738 | 124.5071 | -124.4751 | -124.8001
1692.6406 | 124.8459 | -64.9887 | 59.4955 | -0.16304 | 1.0763 | 1.0901 | 0.017526 | 0.0005297 | 0.010959 | 0.035273 | 58.992 | 59.3033 | -65.1535 | 47.818 | 38.9465 | -60.26 | 32.666 | 7.4112 | 59.436 | -65.2588 | -0.16479 | -0.19226 | 123.9807 | 112.8067 | -20.549 | -0.27008 | -0.059509 | 124.1455 | 97.6547 | 72.3999 | 103.9352 | 124.292 | 123.9807 | 124.4247 | 4.7287 | -0.27008 | 124.292 | 123.9807 | 4.7287 | 103.9352 | 124.4247 | -124.649 | -124.7543
1693.6406 | 124.8917 | -64.9567 | 59.5001 | 0.058212 | 1.1216 | 1.1176 | 0.014108 | -0.0011793 | 0.0096771 | 0.031001 | 59.2255 | 59.3216 | -65.126 | 47.7722 | 38.9465 | -60.2921 | 32.6752 | 7.3792 | 59.4498 | -65.2542 | -0.16937 | -0.17853 | 124.1821 | 112.7289 | -20.5536 | -0.29755 | -0.050354 | 124.3515 | 97.6318 | 72.3358 | 103.9032 | 124.2783 | 124.1821 | 124.4064 | 4.6646 | -0.29755 | 124.2783 | 124.1821 | 4.6646 | 103.9032 | 124.4064 | -124.6262 | -124.7543
1694.6406 | 124.6765 | -64.9796 | 59.4315 | 0.14976 | 1.4732 | 1.5049 | 0.014321 | -0.0011793 | 0.010104 | 0.032283 | 59.1156 | 59.2209 | -65.1123 | 47.6807 | 38.9145 | -60.2966 | 32.7347 | 7.4387 | 59.3857 | -65.2496 | -0.13275 | -0.21057 | 124.0952 | 112.6602 | -20.517 | -0.27008 | -0.045777 | 124.2279 | 97.7142 | 72.4182 | 103.894 | 124.2004 | 124.0952 | 124.3652 | 4.6829 | -0.27008 | 124.2004 | 124.0952 | 4.6829 | 103.894 | 124.3652 | -124.5438 | -124.6811
1695.6406 | 124.6948 | -64.9109 | 59.4452 | 0.08873 | 1.7958 | 1.7957 | 0.015817 | 0.0005297 | 0.012027 | 0.034205 | 59.1934 | 59.2484 | -65.0436 | 47.7173 | 38.9465 | -60.2554 | 32.7896 | 7.4615 | 59.3948 | -65.1947 | -0.13275 | -0.19684 | 124.1043 | 112.6282 | -20.4987 | -0.28381 | -0.050354 | 124.2371 | 97.7005 | 72.3724 | 103.8574 | 124.1592 | 124.1043 | 124.3057 | 4.6555 | -0.28381 | 124.1592 | 124.1043 | 4.6555 | 103.8574 | 124.3057 | -124.4888 | -124.6399
1696.6406 | 124.7772 | -65.007 | 59.3948 | 0.18028 | 0.044085 | 0.048866 | 0.016244 | 0.0024523 | 0.0092499 | 0.032069 | 59.4498 | 59.3353 | -65.2634 | 47.7814 | 38.9648 | -60.2875 | 32.8217 | 7.7362 | 59.3491 | -65.2634 | -0.25635 | -0.059509 | 124.4568 | 112.7884 | -20.43 | -0.25635 | -0.045776 | 124.7131 | 97.8287 | 72.7432 | 103.9719 | 124.3423 | 124.4568 | 124.3561 | 4.7195 | -0.25635 | 124.3423 | 124.4568 | 4.7195 | 103.9719 | 124.3561 | -124.6582 | -124.6582
1697.6406 | 124.8047 | -64.9384 | 59.491 | -0.071488 | 0.044726 | 0.043099 | 0.015603 | -0.0001111 | 0.012882 | 0.032283 | 59.5322 | 59.436 | -65.1993 | 47.8821 | 39.1388 | -60.2325 | 33.0185 | 7.9422 | 59.4315 | -65.213 | -0.26093 | -0.054932 | 124.4705 | 112.8204 | -20.3522 | -0.27466 | -0.059509 | 124.7314 | 97.9568 | 72.8806 | 104.0771 | 124.3744 | 124.4705 | 124.3698 | 4.7058 | -0.27466 | 124.3744 | 124.4705 | 4.7058 | 104.0771 | 124.3698 | -124.6902 | -124.704
1698.6406 | 124.7864 | -64.8972 | 59.5505 | 0.11162 | 0.045794 | 0.045021 | 0.014321 | -0.0009655 | 0.0096771 | 0.032283 | 59.6146 | 59.5184 | -65.1489 | 47.9324 | 39.1708 | -60.2142 | 33.1329 | 7.9971 | 59.5276 | -65.1855 | -0.25177 | -0.032043 | 124.5117 | 112.8296 | -20.3796 | -0.28839 | -0.022888 | 124.7635 | 98.0301 | 72.8943 | 104.068 | 124.4156 | 124.5117 | 124.4247 | 4.6829 | -0.28839 | 124.4156 | 124.5117 | 4.6829 | 104.068 | 124.4247 | -124.6994 | -124.736
1699.6406 | 124.8001 | -64.9521 | 59.5184 | 0.0811 | 0.045581 | 0.042458 | 0.015603 | 0.0007435 | 0.0116 | 0.031642 | 59.5139 | 59.4406 | -65.1993 | 47.8226 | 39.0152 | -60.3012 | 33.1741 | 7.869 | 59.4589 | -65.2222 | -0.24719 | -0.07782 | 124.4659 | 112.7747 | -20.5032 | -0.27008 | -0.05951 | 124.7131 | 98.1262 | 72.821 | 103.9673 | 124.3927 | 124.4659 | 124.411 | 4.6509 | -0.27008 | 124.3927 | 124.4659 | 4.6509 | 103.9673 | 124.411 | -124.7177 | -124.7406
1700.6406 | 124.8276 | -65.0162 | 59.4681 | -0.6208 | 0.045154 | 0.049934 | 0.01368 | 0.0003161 | 0.0098907 | 0.032069 | 59.3948 | 59.404 | -65.2908 | 47.7859 | 39.0015 | -60.3745 | 33.3069 | 8.3176 | 59.4177 | -65.2817 | -0.27466 | -0.064087 | 124.411 | 112.8021 | -20.4666 | -0.2655 | -0.050354 | 124.6857 | 98.3231 | 73.3337 | 104.0176 | 124.4202 | 124.411 | 124.4339 | 4.6417 | -0.2655 | 124.4202 | 124.411 | 4.6417 | 104.0176 | 124.4339 | -124.7589 | -124.7498
1701.6406 | 124.8001 | -64.9384 | 59.5184 | 0.18791 | 0.043231 | 0.044594 | 0.016458 | -0.0024609 | 0.011386 | 0.031215 | 59.5367 | 59.4498 | -65.2313 | 47.9233 | 39.1113 | -60.3333 | 33.5312 | 8.6014 | 59.4498 | -65.2451 | -0.29297 | -0.068665 | 124.4751 | 112.8616 | -20.4071 | -0.3067 | -0.068665 | 124.7681 | 98.4695 | 73.5397 | 104.0497 | 124.3881 | 124.4751 | 124.3881 | 4.6051 | -0.3067 | 124.3881 | 124.4751 | 4.6051 | 104.0497 | 124.3881 | -124.7498 | -124.7635
1702.6406 | 124.8276 | -65.2359 | 59.2392 | -0.071488 | 0.043445 | 0.04673 | 0.014321 | -0.0016065 | 0.0077545 | 0.032924 | 59.2896 | 59.1614 | -65.506 | 47.7448 | 38.9877 | -60.5576 | 33.4854 | 9.1049 | 59.2392 | -65.4922 | -0.27008 | -0.07782 | 124.5255 | 112.9807 | -20.2515 | -0.25635 | 0 | 124.7955 | 98.7213 | 74.3408 | 104.2236 | 124.3973 | 124.5255 | 124.4751 | 4.6783 | -0.25635 | 124.3973 | 124.5255 | 4.6783 | 104.2236 | 124.4751 | -124.7452 | -124.7314
1703.6406 | 124.7955 | -65.2634 | 59.2209 | -0.28511 | 0.046435 | 0.045662 | 0.019235 | 0.0009571 | 0.010318 | 0.033351 | 59.2712 | 59.1339 | -65.5289 | 47.7173 | 38.9648 | -60.64 | 33.5678 | 9.2972 | 59.1476 | -65.538 | -0.2655 | -0.086975 | 124.5346 | 112.9807 | -20.256 | -0.27466 | -0.073242 | 124.8001 | 98.8312 | 74.5605 | 104.2282 | 124.3973 | 124.5346 | 124.411 | 4.6234 | -0.27466 | 124.3973 | 124.5346 | 4.6234 | 104.2282 | 124.411 | -124.7498 | -124.7589
1704.6406 | 124.8322 | -65.2542 | 59.2117 | 0.18028 | 0.045154 | 0.049507 | 0.017526 | -0.0011793 | 0.0116 | 0.03271 | 59.2987 | 59.1522 | -65.5243 | 47.7036 | 38.9969 | -60.5896 | 33.6914 | 9.6909 | 59.1888 | -65.5426 | -0.27008 | -0.059509 | 124.5529 | 112.9578 | -20.2148 | -0.28839 | -0.022888 | 124.823 | 98.9456 | 74.9451 | 104.2511 | 124.4064 | 124.5529 | 124.4431 | 4.6646 | -0.28839 | 124.4064 | 124.5529 | 4.6646 | 104.2511 | 124.4431 | -124.736 | -124.7543
1705.6562 | 124.8047 | -65.2679 | 59.2621 | -0.22408 | 0.043445 | 0.045876 | 0.014962 | 0.0028797 | 0.0079681 | 0.033992 | 59.2758 | 59.1751 | -65.538 | 47.7905 | 39.0747 | -60.6583 | 34.2041 | 10.3226 | 59.2163 | -65.538 | -0.27008 | -0.086975 | 124.5438 | 113.0585 | -20.1874 | -0.27008 | -0.045776 | 124.8138 | 99.472 | 75.5905 | 104.3427 | 124.4431 | 124.5438 | 124.4843 | 4.6097 | -0.27008 | 124.4431 | 124.5438 | 4.6097 | 104.3427 | 124.4843 | -124.8001 | -124.8001
1706.6406 | 124.9329 | -65.2817 | 59.2392 | 0.0048064 | 0.045367 | 0.04673 | 0.012399 | -0.0005383 | 0.010104 | 0.030146 | 59.2255 | 59.166 | -65.5197 | 47.7585 | 39.0244 | -60.6857 | 34.2865 | 10.6888 | 59.1934 | -65.5243 | -0.23804 | -0.073242 | 124.5071 | 113.0402 | -20.2148 | -0.24262 | -0.045777 | 124.7452 | 99.5682 | 75.9705 | 104.306 | 124.4476 | 124.5071 | 124.4751 | 4.5959 | -0.24262 | 124.4476 | 124.5071 | 4.5959 | 104.306 | 124.4751 | -124.7589 | -124.7635
1707.6562 | 124.8367 | -65.1352 | 59.3674 | -0.29274 | 0.046008 | 0.043739 | 0.015389 | -0.0031019 | 0.0090363 | 0.032283 | 59.4086 | 59.2987 | -65.4007 | 47.9645 | 39.1983 | -60.5347 | 34.6298 | 11.293 | 59.317 | -65.4465 | -0.2655 | -0.068665 | 124.5438 | 113.0997 | -20.1691 | -0.31128 | -0.050354 | 124.8093 | 99.765 | 76.4282 | 104.3335 | 124.4339 | 124.5438 | 124.4522 | 4.6005 | -0.31128 | 124.4339 | 124.5438 | 4.6005 | 104.3335 | 124.4522 | -124.7681 | -124.8138
1708.6406 | 124.855 | -65.2359 | 59.2804 | 0.17265 | 0.04494 | 0.044594 | 0.016458 | 0.0024523 | 0.010532 | 0.03271 | 59.3308 | 59.1934 | -65.4877 | 47.8912 | 39.1159 | -60.6262 | 34.8221 | 11.6318 | 59.2072 | -65.4785 | -0.25177 | -0.086976 | 124.5667 | 113.1271 | -20.1645 | -0.24262 | -0.073243 | 124.8184 | 100.058 | 76.8677 | 104.3518 | 124.4293 | 124.5667 | 124.4431 | 4.6097 | -0.24262 | 124.4293 | 124.5667 | 4.6097 | 104.3518 | 124.4431 | -124.7681 | -124.7589
1709.6406 | 124.8505 | -65.1947 | 59.3033 | 0.16502 | 0.046435 | 0.050362 | 0.018167 | 0.0018115 | 0.0088225 | 0.033137 | 59.3628 | 59.2621 | -65.4602 | 47.9004 | 39.1571 | -60.6216 | 35.2066 | 12.1857 | 59.2484 | -65.4922 | -0.2655 | -0.041199 | 124.5575 | 113.0951 | -20.1462 | -0.29755 | -0.054932 | 124.823 | 100.4013 | 77.3804 | 104.3518 | 124.4568 | 124.5575 | 124.4431 | 4.5731 | -0.29755 | 124.4568 | 124.5575 | 4.5731 | 104.3518 | 124.4431 | -124.7635 | -124.7955
1710.6406 | 124.9695 | -67.5201 | 56.9824 | 0.020065 | 0.043445 | 0.043526 | 0.02073 | 0.0001025 | 0.011173 | 0.034419 | 56.9778 | 56.9 | -67.7765 | 46.7743 | 37.0926 | -62.9425 | 47.3877 | 57.0465 | 56.955 | -67.7948 | -0.25635 | -0.082398 | 124.498 | 114.2944 | -19.8898 | -0.27466 | -0.027466 | 124.7543 | 114.9078 | 124.5667 | 104.6127 | 124.4202 | 124.498 | 124.4751 | 4.5776 | -0.27466 | 124.4202 | 124.498 | 4.5776 | 104.6127 | 124.4751 | -124.7589 | -124.7772
1711.6406 | 124.8688 | -67.543 | 56.9183 | 0.63042 | 0.044085 | 0.044808 | 0.022439 | 0.0007435 | 0.010959 | 0.035914 | 57.0511 | 56.8359 | -67.8314 | 46.7926 | 37.0926 | -62.9333 | 47.287 | 57.0419 | 56.8771 | -67.8497 | -0.28839 | -0.082398 | 124.5941 | 114.3356 | -19.8257 | -0.3067 | -0.041199 | 124.8825 | 114.83 | 124.585 | 104.6356 | 124.379 | 124.5941 | 124.4202 | 4.6097 | -0.3067 | 124.379 | 124.5941 | 4.6097 | 104.6356 | 124.4202 | -124.7498 | -124.7681
1712.6406 | 124.8367 | -67.5568 | 56.9366 | -0.048599 | 0.045581 | 0.04673 | 0.017739 | 0.0001025 | 0.0096771 | 0.033992 | 56.9504 | 56.8451 | -67.8543 | 46.7011 | 37.0697 | -62.915 | 47.4976 | 57.0831 | 56.9183 | -67.8131 | -0.29755 | -0.091553 | 124.5071 | 114.2578 | -19.8669 | -0.25635 | -0.018311 | 124.8047 | 115.0543 | 124.6399 | 104.6265 | 124.4019 | 124.5071 | 124.4751 | 4.6417 | -0.25635 | 124.4019 | 124.5071 | 4.6417 | 104.6265 | 124.4751 | -124.791 | -124.7498
1713.6406 | 124.7864 | -67.5568 | 56.9504 | 0.058212 | 0.042163 | 0.047157 | 0.019662 | -0.0007519 | 0.010318 | 0.035487 | 56.9778 | 56.8817 | -67.8406 | 46.6827 | 37.0148 | -62.9379 | 47.4838 | 57.0099 | 56.868 | -67.836 | -0.28381 | -0.068664 | 124.5346 | 114.2395 | -19.9356 | -0.27924 | -0.082397 | 124.8184 | 115.0406 | 124.5667 | 104.5715 | 124.4385 | 124.5346 | 124.4247 | 4.6188 | -0.27924 | 124.4385 | 124.5346 | 4.6188 | 104.5715 | 124.4247 | -124.791 | -124.7864
1714.6406 | 124.8871 | -67.7444 | 56.7535 | 0.18028 | 0.044299 | 0.049721 | 0.024148 | 0.0009571 | 0.0092499 | 0.037623 | 56.8268 | 56.6757 | -68.0145 | 46.5363 | 36.8866 | -63.1073 | 47.3236 | 56.868 | 56.7169 | -68.0328 | -0.27008 | -0.07782 | 124.5712 | 114.2807 | -19.8669 | -0.28839 | -0.036621 | 124.8413 | 115.0681 | 124.6124 | 104.631 | 124.4202 | 124.5712 | 124.4614 | 4.6371 | -0.28839 | 124.4202 | 124.5712 | 4.6371 | 104.631 | 124.4614 | -124.7681 | -124.7864
1715.6406 | 124.7635 | -67.6437 | 56.8863 | -0.22408 | 0.044299 | 0.040535 | 0.019021 | 0.0009571 | 0.0098907 | 0.035701 | 56.8909 | 56.7902 | -67.9321 | 46.637 | 36.9324 | -63.0341 | 47.6532 | 56.9778 | 56.8542 | -67.9367 | -0.28839 | -0.096131 | 124.5346 | 114.2807 | -19.9539 | -0.29297 | -0.032044 | 124.823 | 115.2969 | 124.6216 | 104.5761 | 124.4339 | 124.5346 | 124.498 | 4.6097 | -0.29297 | 124.4339 | 124.5346 | 4.6097 | 104.5761 | 124.498 | -124.8184 | -124.823
1716.6406 | 124.8322 | -67.5705 | 56.9504 | 0.18791 | 0.046649 | 0.048653 | 0.021798 | -0.0003247 | 0.0096771 | 0.036128 | 56.9733 | 56.8542 | -67.8177 | 46.6782 | 36.9965 | -62.915 | 47.5891 | 57.0282 | 56.8771 | -67.8452 | -0.24719 | -0.09613 | 124.5438 | 114.2487 | -19.9539 | -0.27466 | -0.073242 | 124.791 | 115.1596 | 124.5987 | 104.567 | 124.4247 | 124.5438 | 124.4476 | 4.6555 | -0.27466 | 124.4247 | 124.5438 | 4.6555 | 104.567 | 124.4476 | -124.7681 | -124.7955
1717.6406 | 124.8413 | -67.9367 | 56.5796 | -0.048599 | 0.043658 | 0.043099 | 0.01838 | -0.0007519 | 0.0090363 | 0.035487 | 56.5659 | 56.5109 | -68.2205 | 46.2799 | 36.6394 | -63.2675 | 47.374 | 56.6757 | 56.543 | -68.2022 | -0.28381 | -0.068665 | 124.5026 | 114.2166 | -19.9402 | -0.2655 | -0.036621 | 124.7864 | 115.3107 | 124.6124 | 104.5761 | 124.4476 | 124.5026 | 124.4797 | 4.6692 | -0.2655 | 124.4476 | 124.5026 | 4.6692 | 104.5761 | 124.4797 | -124.8001 | -124.7818
1718.6406 | 124.855 | -68.042 | 56.4651 | -0.91072 | 0.046863 | 0.051643 | 0.025643 | -0.0003247 | 0.011173 | 0.035701 | 56.4972 | 56.4148 | -68.2663 | 46.2296 | 36.47 | -63.3499 | 47.2458 | 56.5933 | 56.4331 | -68.3212 | -0.2243 | -0.050354 | 124.5392 | 114.2715 | -19.9951 | -0.27924 | -0.032044 | 124.7635 | 115.2878 | 124.6353 | 104.512 | 124.4568 | 124.5392 | 124.4751 | 4.6921 | -0.27924 | 124.4568 | 124.5392 | 4.6921 | 104.512 | 124.4751 | -124.7314 | -124.7864
1719.6406 | 124.8688 | -68.0145 | 56.488 | 0.16502 | 0.046649 | 0.048866 | 0.025216 | 0.0022387 | 0.0081817 | 0.035273 | 56.4377 | 56.4331 | -68.3166 | 46.2799 | 36.4243 | -63.2812 | 47.374 | 56.6071 | 56.4651 | -68.2846 | -0.30212 | -0.054932 | 124.4522 | 114.2944 | -20.0638 | -0.27008 | -0.022888 | 124.7543 | 115.3885 | 124.6216 | 104.4388 | 124.4476 | 124.4522 | 124.4797 | 4.7333 | -0.27008 | 124.4476 | 124.4522 | 4.7333 | 104.4388 | 124.4797 | -124.8047 | -124.7726
1720.6562 | 124.8825 | -67.9367 | 56.5613 | -0.51399 | 0.045154 | 0.044167 | 0.019021 | -0.0007519 | 0.0071137 | 0.035914 | 56.6208 | 56.488 | -68.2159 | 46.2891 | 36.4746 | -63.1531 | 47.6349 | 56.7581 | 56.543 | -68.1839 | -0.27923 | -0.073242 | 124.5575 | 114.2258 | -20.0867 | -0.24719 | -0.01831 | 124.8367 | 115.5716 | 124.6948 | 104.4113 | 124.4247 | 124.5575 | 124.4797 | 4.7836 | -0.24719 | 124.4247 | 124.5575 | 4.7836 | 104.4113 | 124.4797 | -124.7772 | -124.7452
1721.6406 | 124.8276 | -68.2892 | 56.25 | 0.18791 | 0.045794 | 0.046303 | 0.020944 | 0.0009571 | 0.0071137 | 0.037623 | 56.2775 | 56.1447 | -68.5318 | 46.4996 | 36.0352 | -63.4918 | 56.1493 | 56.3232 | 56.1996 | -68.5547 | -0.24261 | -0.10529 | 124.5667 | 114.7888 | -20.2148 | -0.2655 | -0.050354 | 124.8093 | 124.4385 | 124.6124 | 104.3243 | 124.4339 | 124.5667 | 124.4888 | 4.7974 | -0.2655 | 124.4339 | 124.5667 | 4.7974 | 104.3243 | 124.4888 | -124.7818 | -124.8047
1722.6406 | 124.8138 | -68.042 | 56.5018 | -0.033341 | 0.043231 | 0.04438 | 0.019876 | -0.0018201 | 0.010532 | 0.035487 | 56.4835 | 56.3919 | -68.3075 | 46.6049 | 36.1725 | -63.2217 | 56.4011 | 56.5979 | 56.4468 | -68.3212 | -0.2655 | -0.10986 | 124.5255 | 114.6469 | -20.3293 | -0.27924 | -0.054932 | 124.791 | 124.4431 | 124.6399 | 104.2145 | 124.4339 | 124.5255 | 124.4888 | 4.8203 | -0.27924 | 124.4339 | 124.5255 | 4.8203 | 104.2145 | 124.4888 | -124.8093 | -124.823
1723.6406 | 124.8642 | -67.749 | 56.749 | 0.096359 | 0.044726 | 0.044808 | 0.02842 | -0.0020337 | 0.010104 | 0.043605 | 56.7856 | 56.6528 | -68.0511 | 46.788 | 36.232 | -62.9059 | 56.6162 | 56.8497 | 56.694 | -68.0557 | -0.30212 | -0.09613 | 124.5346 | 114.537 | -20.517 | -0.3067 | -0.054931 | 124.8367 | 124.3652 | 124.5987 | 103.981 | 124.4019 | 124.5346 | 124.4431 | 4.8431 | -0.3067 | 124.4019 | 124.5346 | 4.8431 | 103.981 | 124.4431 | -124.8001 | -124.8047
1724.6406 | 124.8917 | -67.6849 | 56.8085 | 0.11925 | 0.047076 | 0.048653 | 0.026071 | 0.0013843 | 0.010532 | 0.041682 | 56.9092 | 56.7307 | -67.955 | 46.9254 | 36.2 | -62.7594 | 56.6437 | 56.9641 | 56.7535 | -68.0008 | -0.27008 | -0.07782 | 124.5941 | 114.6103 | -20.6085 | -0.31586 | -0.054932 | 124.8642 | 124.3286 | 124.649 | 103.8849 | 124.4156 | 124.5941 | 124.4385 | 4.9255 | -0.31586 | 124.4156 | 124.5941 | 4.9255 | 103.8849 | 124.4385 | -124.7635 | -124.8093
1725.6562 | 124.7955 | -67.9092 | 56.6391 | -0.1783 | 0.045794 | 0.045021 | 0.029061 | 0.0015979 | 0.010318 | 0.039119 | 56.6574 | 56.6666 | -68.1747 | 46.6782 | 35.9116 | -63.0341 | 56.6391 | 56.7078 | 56.6345 | -68.2297 | -0.2655 | 0.027466 | 124.5667 | 114.5874 | -20.7275 | -0.32043 | -0.004578 | 124.8322 | 124.5483 | 124.617 | 103.8208 | 124.5758 | 124.5667 | 124.5438 | 4.8752 | -0.32043 | 124.5758 | 124.5667 | 4.8752 | 103.8208 | 124.5438 | -124.8138 | -124.8688
1726.6562 | 124.8917 | -67.7994 | 56.6803 | -0.17067 | 0.044726 | 0.040321 | 0.024148 | 0.0015979 | 0.0092499 | 0.038264 | 56.7398 | 56.6254 | -68.0923 | 46.7743 | 36.0031 | -62.8693 | 56.6071 | 56.8588 | 56.662 | -68.1015 | -0.29297 | -0.054932 | 124.5392 | 114.5737 | -20.6772 | -0.30212 | -0.018311 | 124.8322 | 124.4064 | 124.6582 | 103.8025 | 124.4247 | 124.5392 | 124.4614 | 4.9301 | -0.30212 | 124.4247 | 124.5392 | 4.9301 | 103.8025 | 124.4614 | -124.7726 | -124.7818
1727.6406 | 124.8413 | -67.8406 | 56.6666 | -0.048599 | 0.041308 | 0.045876 | 0.022866 | 0.0001025 | 0.0096771 | 0.038264 | 56.6666 | 56.5842 | -68.129 | 46.6644 | 35.9528 | -62.8922 | 56.5979 | 56.8222 | 56.6299 | -68.0969 | -0.28839 | -0.082398 | 124.5071 | 114.505 | -20.7138 | -0.25635 | -0.036621 | 124.7955 | 124.4385 | 124.6628 | 103.7933 | 124.4247 | 124.5071 | 124.4705 | 4.9484 | -0.25635 | 124.4247 | 124.5071 | 4.9484 | 103.7933 | 124.4705 | -124.7955 | -124.7635
1728.6406 | 124.8367 | -67.7628 | 56.7307 | 0.11925 | 0.045367 | 0.044594 | 0.023507 | -0.0003247 | 0.010532 | 0.037837 | 56.7902 | 56.6757 | -68.0695 | 46.8658 | 35.939 | -62.851 | 56.575 | 56.8588 | 56.6849 | -68.1015 | -0.3067 | -0.054932 | 124.5529 | 114.6286 | -20.7916 | -0.33875 | -0.045777 | 124.8596 | 124.3378 | 124.6216 | 103.7018 | 124.4385 | 124.5529 | 124.4476 | 4.9118 | -0.33875 | 124.4385 | 124.5529 | 4.9118 | 103.7018 | 124.4476 | -124.8001 | -124.8322
1729.6406 | 124.8642 | -67.7628 | 56.7444 | 0.16502 | 0.045581 | 0.050789 | 0.024362 | -0.0009655 | 0.0096771 | 0.038051 | 56.8039 | 56.6895 | -68.0237 | 46.8842 | 36.0123 | -62.8189 | 56.6208 | 56.8817 | 56.7352 | -68.0466 | -0.26093 | -0.054932 | 124.5666 | 114.6469 | -20.7321 | -0.28381 | -0.009156 | 124.8276 | 124.3835 | 124.6445 | 103.775 | 124.4522 | 124.5666 | 124.498 | 4.9438 | -0.28381 | 124.4522 | 124.5666 | 4.9438 | 103.775 | 124.498 | -124.7681 | -124.791
1730.6562 | 124.8779 | -67.543 | 56.955 | 0.17265 | 0.048785 | 0.047157 | 0.026925 | 0.0009571 | 0.010318 | 0.039332 | 56.9504 | 56.8909 | -67.8177 | 47.1725 | 36.1679 | -62.5534 | 56.7764 | 57.0877 | 56.9046 | -67.836 | -0.27466 | -0.064087 | 124.4934 | 114.7156 | -20.787 | -0.29297 | -0.050354 | 124.7681 | 124.3195 | 124.6307 | 103.7109 | 124.4339 | 124.4934 | 124.4476 | 4.9896 | -0.29297 | 124.4339 | 124.4934 | 4.9896 | 103.7109 | 124.4476 | -124.7726 | -124.791
1731.6562 | 124.8505 | -67.6483 | 56.8634 | -0.30037 | 0.046222 | 0.047798 | 0.021585 | -0.0003247 | 0.0096771 | 0.037196 | 56.7078 | 56.7764 | -67.9459 | 47.1909 | 36.1725 | -62.7182 | 56.7627 | 57.0465 | 56.8497 | -67.9321 | -0.29755 | -0.086975 | 124.3561 | 114.8392 | -20.6909 | -0.28381 | -0.013733 | 124.6536 | 124.411 | 124.6948 | 103.8208 | 124.4247 | 124.3561 | 124.498 | 4.9301 | -0.28381 | 124.4247 | 124.3561 | 4.9301 | 103.8208 | 124.498 | -124.8093 | -124.7955
1732.6406 | 124.8459 | -67.5842 | 56.9275 | 0.12688 | 0.046222 | 0.048866 | 0.024148 | 0.0005297 | 0.010959 | 0.036982 | 56.9321 | 56.8405 | -67.8726 | 47.3465 | 36.2595 | -62.7686 | 56.813 | 57.0236 | 56.868 | -67.868 | -0.28839 | -0.086975 | 124.5163 | 114.9307 | -20.668 | -0.28381 | -0.059509 | 124.8047 | 124.3973 | 124.6078 | 103.8437 | 124.4247 | 124.5163 | 124.4522 | 4.8157 | -0.28381 | 124.4247 | 124.5163 | 4.8157 | 103.8437 | 124.4522 | -124.8001 | -124.7955
1733.6406 | 124.8322 | -67.7261 | 56.7947 | -0.018082 | 0.045367 | 0.041817 | 0.019448 | -0.0024609 | 0.0096771 | 0.037623 | 56.7902 | 56.6986 | -68.0008 | 47.2961 | 36.2732 | -62.9196 | 56.7032 | 56.9138 | 56.749 | -67.9962 | -0.27466 | -0.096131 | 124.5163 | 115.0223 | -20.5215 | -0.27008 | -0.045777 | 124.791 | 124.4293 | 124.6399 | 103.9993 | 124.4247 | 124.5163 | 124.4751 | 4.8065 | -0.27008 | 124.4247 | 124.5163 | 4.8065 | 103.9993 | 124.4751 | -124.7955 | -124.791
1734.6406 | 124.9191 | -67.7216 | 56.7902 | -0.079117 | 0.046649 | 0.04203 | 0.028848 | -0.0011793 | 0.010318 | 0.047023 | 56.8359 | 56.7123 | -67.9871 | 47.438 | 36.5204 | -62.9425 | 56.6986 | 56.955 | 56.7307 | -67.9871 | -0.2655 | -0.07782 | 124.5575 | 115.1596 | -20.2698 | -0.2655 | -0.059509 | 124.823 | 124.4202 | 124.6765 | 104.2419 | 124.4339 | 124.5575 | 124.4522 | 4.7791 | -0.2655 | 124.4339 | 124.5575 | 4.7791 | 104.2419 | 124.4522 | -124.7772 | -124.7772
1735.6562 | 116.5192 | -60.8459 | 55.4169 | 0.096359 | 0.043658 | 0.043099 | 6.9276 | -0.0018201 | 0.017581 | 7.0052 | 55.3207 | 55.3116 | -61.0657 | 12.4237 | -17.3584 | 1.8402 | 12.291 | 8.1757 | 30.3955 | -36.145 | -0.21973 | -0.10529 | 116.1667 | 73.2697 | -72.7753 | 24.7009 | -25.0214 | 116.3864 | 73.1369 | 69.0216 | 43.4875 | 116.1575 | 116.1667 | 91.2415 | 62.6862 | 24.7009 | 116.1575 | 116.1667 | 62.6862 | 43.4875 | 91.2415 | -116.4825 | -91.5619
1736.6562 | 123.9807 | -70.7703 | 52.9678 | 0.27184 | 0.046863 | 0.038185 | 0.041024 | 0.0035205 | 0.068424 | 0.11068 | 52.977 | 52.8809 | -71.0999 | 40.86 | -70.9946 | -70.7611 | 52.7298 | 53.1281 | 52.8442 | -71.0678 | -0.32959 | -0.086975 | 123.7473 | 111.6302 | -123.9624 | -0.29755 | -0.1236 | 124.0768 | 123.5001 | 123.8983 | -0.2243 | 123.6511 | 123.7473 | 123.6145 | 0.009156 | -0.29755 | 123.6511 | 123.7473 | 0.009156 | -0.2243 | 123.6145 | -124.0677 | -124.0356
1737.6406 | 123.7152 | -98.378 | 25.2274 | -0.32326 | 0.042163 | 0.03904 | 0.15595 | 0.0041613 | 0.06821 | 0.24099 | 25.1404 | 25.2045 | -98.6801 | 15.1062 | -98.3688 | -98.7213 | 25.2045 | 25.1816 | 25.2045 | -98.6481 | -0.30212 | -0.022888 | 123.5184 | 113.4842 | -123.5962 | -0.27008 | -0.022888 | 123.8205 | 123.5825 | 123.5596 | 0.009156 | 123.5825 | 123.5184 | 123.5825 | -0.34332 | -0.27008 | 123.5825 | 123.5184 | -0.34332 | 0.009156 | 123.5825 | -123.9075 | -123.8754
1738.6406 | 115.1093 | -103.0289 | 1.4648 | 0.096359 | 0.043658 | 0.038826 | 0.020516 | -0.0020337 | 0.0011321 | 0.008357 | 1.3184 | 1.3596 | -121.9757 | 1.3596 | 1.3641 | 1.4191 | 1.1902 | 1.5289 | 1.506 | 1.0391 | -18.9468 | -0.10529 | 104.3472 | 104.3884 | -0.10071 | 104.068 | 0.041198 | 123.2941 | 104.2191 | 104.5578 | 104.393 | 104.3884 | 104.3472 | 104.5349 | 104.4479 | 104.068 | 104.3884 | 104.3472 | 104.4479 | 104.393 | 104.5349 | -123.4406 | -0.42572
1739.6406 | 123.8251 | -122.5204 | 1.1353 | -0.14015 | 0.041308 | 0.039894 | 0.019876 | -0.0052381 | 0.0032683 | 0.009425 | 0.93842 | 1.0208 | -122.7905 | 0.98877 | 0.99335 | 1.0071 | 0.9201 | 1.1627 | 1.1627 | 0.70953 | -0.27008 | -0.11444 | 123.4589 | 123.5092 | -0.14191 | 123.23 | 0.027466 | 123.7289 | 123.4406 | 123.6832 | 123.5138 | 123.5413 | 123.4589 | 123.6832 | 123.5275 | 123.23 | 123.5413 | 123.4589 | 123.5275 | 123.5138 | 123.6832 | -123.9258 | -0.42572
1740.6562 | 123.9441 | -122.3099 | 1.3641 | -0.063858 | 0.044726 | 0.045021 | 0.019876 | -0.0054517 | 0.00049134 | 0.008357 | 1.3229 | 1.4282 | -122.4747 | 1.2863 | 1.2634 | 1.2909 | 1.1215 | 1.4603 | 1.4191 | 0.95673 | -0.16479 | 0.064087 | 123.6328 | 123.5962 | -0.10071 | 123.2666 | 0.054931 | 123.7976 | 123.4314 | 123.7701 | 123.5733 | 123.7381 | 123.6328 | 123.7289 | 123.6008 | 123.2666 | 123.7381 | 123.6328 | 123.6008 | 123.5733 | 123.7289 | -123.8388 | -0.40741
1741.6562 | 123.9029 | -122.3282 | 1.4648 | -0.2317 | 0.047076 | 0.049721 | 0.025002 | -0.0058789 | -0.0010041 | 0.0079296 | 1.149 | 1.3275 | -122.6761 | 1.2222 | 1.1993 | 1.2131 | 1.3092 | 1.3687 | 1.4282 | 0.92468 | -0.3479 | -0.13733 | 123.4772 | 123.5504 | -0.2655 | 123.2529 | -0.036621 | 123.8251 | 123.6374 | 123.6969 | 123.5275 | 123.6557 | 123.4772 | 123.7564 | 123.5413 | 123.2529 | 123.6557 | 123.4772 | 123.5413 | 123.5275 | 123.7564 | -124.1409 | -0.54016
1742.6406 | 123.9944 | -122.438 | 1.2955 | -0.14015 | 0.046008 | 0.042458 | 0.022225 | -0.0071607 | -0.00057686 | 0.0098522 | 1.2085 | 1.2543 | -122.6669 | 1.2589 | 1.2497 | 1.268 | 1.0117 | 1.4008 | 1.3412 | 0.88806 | -0.22888 | -0.041199 | 123.6465 | 123.6969 | -0.045776 | 123.3261 | 0.045777 | 123.8754 | 123.4497 | 123.8388 | 123.6877 | 123.6923 | 123.6465 | 123.7793 | 123.7061 | 123.3261 | 123.6923 | 123.6465 | 123.7061 | 123.6877 | 123.7793 | -123.9624 | -0.40741
1743.6406 | 123.9487 | -122.4655 | 1.3046 | 0.096359 | 0.049212 | 0.049507 | 0.022225 | -0.0050245 | -0.0027131 | 0.0092114 | 1.1124 | 1.2039 | -122.7768 | 1.1719 | 1.181 | 1.2085 | 1.0941 | 1.3275 | 1.3184 | 0.86517 | -0.31128 | -0.10071 | 123.5779 | 123.6374 | -0.1236 | 123.3307 | 0.013733 | 123.8892 | 123.5596 | 123.793 | 123.6465 | 123.6694 | 123.5779 | 123.7839 | 123.674 | 123.3307 | 123.6694 | 123.5779 | 123.674 | 123.6465 | 123.7839 | -124.0814 | -0.43945
1744.6406 | 124.0219 | -122.2824 | 1.4969 | -0.018082 | 0.047931 | 0.046303 | 0.024789 | -0.0060925 | -0.00014946 | 0.0070752 | 1.3412 | 1.4511 | -122.5388 | 1.3916 | 1.3916 | 1.4099 | 1.2772 | 1.5472 | 1.5198 | 1.0895 | -0.25635 | -0.045776 | 123.6237 | 123.674 | -0.10529 | 123.3719 | 0.022888 | 123.88 | 123.5596 | 123.8297 | 123.674 | 123.7335 | 123.6237 | 123.8022 | 123.6923 | 123.3719 | 123.7335 | 123.6237 | 123.6923 | 123.674 | 123.8022 | -124.0356 | -0.40741
1745.6562 | 124.0311 | -122.2961 | 1.5335 | -0.079117 | 0.048785 | 0.045235 | 0.023507 | -0.0071607 | -0.0014313 | 0.0075024 | 1.355 | 1.4603 | -122.5342 | 1.4145 | 1.3962 | 1.4374 | 1.3184 | 1.5518 | 1.561 | 1.1124 | -0.23804 | -0.073242 | 123.6511 | 123.7106 | -0.13733 | 123.4085 | 0.027466 | 123.8892 | 123.6145 | 123.848 | 123.6923 | 123.7564 | 123.6511 | 123.8571 | 123.7335 | 123.4085 | 123.7564 | 123.6511 | 123.7335 | 123.6923 | 123.8571 | -124.0677 | -0.42114
1746.6406 | 123.9944 | -122.1313 | 1.6708 | 0.11162 | 0.047717 | 0.045021 | 0.025002 | -0.0058789 | -0.00057686 | 0.0087842 | 1.5381 | 1.5884 | -122.374 | 1.5564 | 1.5335 | 1.5747 | 1.4008 | 1.6983 | 1.68 | 1.2589 | -0.24261 | -0.082397 | 123.6694 | 123.6877 | -0.13733 | 123.3902 | 0.009156 | 123.912 | 123.5321 | 123.8297 | 123.6649 | 123.7198 | 123.6694 | 123.8113 | 123.7061 | 123.3902 | 123.7198 | 123.6694 | 123.7061 | 123.6649 | 123.8113 | -124.0448 | -0.41199
1747.6406 | 124.0906 | -122.081 | 1.6983 | -0.11726 | 0.045154 | 0.048225 | 0.022439 | -0.0045971 | -0.0020721 | 0.008357 | 1.6067 | 1.6617 | -122.3465 | 1.6708 | 1.6434 | 1.68 | 1.442 | 1.8219 | 1.7303 | 1.3046 | -0.2655 | -0.036621 | 123.6877 | 123.7518 | -0.054931 | 123.3856 | 0.032044 | 123.9532 | 123.523 | 123.9029 | 123.7244 | 123.7427 | 123.6877 | 123.8113 | 123.761 | 123.3856 | 123.7427 | 123.6877 | 123.761 | 123.7244 | 123.8113 | -124.0448 | -0.39368
1748.6406 | 124.0631 | -122.0535 | 1.7624 | 0.0048064 | 0.045794 | 0.045021 | 0.023934 | -0.0069471 | -0.0012177 | 0.0081432 | 1.6983 | 1.6937 | -122.319 | 1.7441 | 1.7166 | 1.7303 | 1.5244 | 1.886 | 1.799 | 1.355 | -0.2655 | -0.068664 | 123.7518 | 123.7976 | -0.045776 | 123.4085 | 0.036621 | 124.0173 | 123.5779 | 123.9395 | 123.7701 | 123.7473 | 123.7518 | 123.8525 | 123.7839 | 123.4085 | 123.7473 | 123.7518 | 123.7839 | 123.7701 | 123.8525 | -124.0814 | -0.40741
1749.6406 | 124.086 | -122.0947 | 1.7349 | -0.6208 | 0.048785 | 0.050148 | 0.024148 | -0.0063061 | 0.00070494 | 0.0096386 | 1.6571 | 1.6708 | -122.3145 | 1.7212 | 1.7029 | 1.7029 | 1.4969 | 1.8585 | 1.767 | 1.3321 | -0.21973 | -0.064087 | 123.7518 | 123.8159 | -0.032043 | 123.4268 | 0.032044 | 123.9716 | 123.5916 | 123.9532 | 123.7976 | 123.7656 | 123.7518 | 123.8617 | 123.7976 | 123.4268 | 123.7656 | 123.7518 | 123.7976 | 123.7976 | 123.8617 | -124.0494 | -0.40283
1750.6406 | 124.0265 | -122.1359 | 1.7807 | -0.24696 | 0.04964 | 0.051857 | 0.028207 | -0.0056653 | -0.0024995 | 0.0092114 | 1.5884 | 1.7532 | -122.3694 | 1.6251 | 1.593 | 1.593 | 1.6571 | 1.7349 | 1.8219 | 1.3138 | -0.23346 | -0.027466 | 123.7244 | 123.761 | -0.18768 | 123.4497 | 0.041198 | 123.9578 | 123.793 | 123.8708 | 123.7289 | 123.8892 | 123.7244 | 123.9578 | 123.7289 | 123.4497 | 123.8892 | 123.7244 | 123.7289 | 123.7289 | 123.9578 | -124.1501 | -0.46692
1751.6406 | 124.054 | -122.0032 | 1.8356 | 0.042953 | 0.067584 | 0.067879 | 0.021157 | -0.0043835 | -0.0014313 | 0.009425 | 1.6754 | 1.7578 | -122.2733 | 1.6937 | 1.6937 | 1.7395 | 1.5701 | 1.8265 | 1.8311 | 1.4236 | -0.27008 | -0.07782 | 123.6786 | 123.6969 | -0.14191 | 123.4268 | -0.004577 | 123.9487 | 123.5733 | 123.8297 | 123.6969 | 123.761 | 123.6786 | 123.8342 | 123.7427 | 123.4268 | 123.761 | 123.6786 | 123.7427 | 123.6969 | 123.8342 | -124.1089 | -0.41199
1752.6406 | 124.0356 | -122.0947 | 1.8173 | -0.2317 | 0.04729 | 0.047371 | 0.025857 | -0.0037427 | -0.0022859 | 0.0079296 | 1.6891 | 1.7578 | -122.2961 | 1.7075 | 1.6891 | 1.6983 | 1.6388 | 1.8356 | 1.8494 | 1.3824 | -0.20142 | -0.05951 | 123.7839 | 123.8022 | -0.12817 | 123.4772 | 0.032043 | 123.9853 | 123.7335 | 123.9304 | 123.7839 | 123.8525 | 123.7839 | 123.9441 | 123.793 | 123.4772 | 123.8525 | 123.7839 | 123.793 | 123.7839 | 123.9441 | -124.1135 | -0.43488
1753.6406 | 124.3057 | -122.0764 | 1.799 | -0.10201 | 0.047076 | 0.049507 | 0.024789 | -0.0037427 | -0.0029267 | 0.0079296 | 1.7303 | 1.7487 | -122.2778 | 1.7715 | 1.7899 | 1.799 | 1.5244 | 1.9272 | 1.8402 | 1.4191 | -0.20142 | -0.050354 | 123.8068 | 123.848 | -0.009155 | 123.4955 | 0.041199 | 124.0082 | 123.6008 | 124.0036 | 123.8663 | 123.8251 | 123.8068 | 123.9166 | 123.8754 | 123.4955 | 123.8251 | 123.8068 | 123.8754 | 123.8663 | 123.9166 | -124.0768 | -0.37994
1754.6406 | 124.1318 | -122.0169 | 1.8356 | -0.26222 | 0.044726 | 0.044167 | 0.023507 | -0.0058789 | -0.00057686 | 0.0081432 | 1.7303 | 1.7807 | -122.287 | 1.7899 | 1.7624 | 1.7944 | 1.6022 | 1.9318 | 1.8631 | 1.4236 | -0.27008 | -0.054931 | 123.7473 | 123.8068 | -0.073242 | 123.4406 | 0.027466 | 124.0173 | 123.6191 | 123.9487 | 123.7793 | 123.7976 | 123.7473 | 123.88 | 123.8113 | 123.4406 | 123.7976 | 123.7473 | 123.8113 | 123.7793 | 123.88 | -124.1226 | -0.41199
1755.6562 | 124.0448 | -122.0444 | 1.8768 | 0.71434 | 0.049212 | 0.050148 | 0.032266 | -0.0024609 | -0.0012177 | 0.006648 | 1.8127 | 1.8814 | -122.2549 | 1.7715 | 1.7349 | 1.7532 | 1.6937 | 1.8585 | 1.918 | 1.4374 | -0.21057 | 0.004578 | 123.8571 | 123.8159 | -0.14191 | 123.4818 | 0.041199 | 124.0677 | 123.7381 | 123.9029 | 123.7793 | 123.9258 | 123.8571 | 123.9624 | 123.7976 | 123.4818 | 123.9258 | 123.8571 | 123.7976 | 123.7793 | 123.9624 | -124.1318 | -0.43945
1756.6406 | 124.1272 | -122.0169 | 1.8631 | -0.063858 | 0.047076 | 0.044594 | 0.021371 | -0.0052381 | -0.0016449 | 0.0092114 | 1.7166 | 1.8127 | -122.2961 | 1.7853 | 1.7761 | 1.8173 | 1.6296 | 1.9363 | 1.8723 | 1.4511 | -0.27924 | -0.050354 | 123.7335 | 123.8022 | -0.086975 | 123.468 | 0.009155 | 124.0128 | 123.6465 | 123.9532 | 123.793 | 123.8297 | 123.7335 | 123.8892 | 123.8342 | 123.468 | 123.8297 | 123.7335 | 123.8342 | 123.793 | 123.8892 | -124.1592 | -0.41199
1757.6406 | 124.0906 | -121.994 | 1.8631 | -0.1783 | 0.044513 | 0.040535 | 0.022866 | -0.0048107 | -0.0024995 | 0.0075024 | 1.7715 | 1.8082 | -122.2595 | 1.7029 | 2.0279 | 2.0233 | 1.1673 | 1.9363 | 1.8723 | 1.442 | -0.2655 | -0.054931 | 123.7656 | 123.6969 | 0.1648 | 123.436 | 0.009155 | 124.0311 | 123.1613 | 123.9304 | 124.0219 | 123.8022 | 123.7656 | 123.8663 | 124.0173 | 123.436 | 123.8022 | 123.7656 | 124.0173 | 124.0219 | 123.8663 | -124.1226 | -0.42114
1758.6562 | 124.086 | -122.0718 | 1.8585 | -0.20882 | 0.047717 | 0.048225 | 0.031198 | -0.0063061 | -0.0024995 | 0.0087842 | 1.7303 | 1.8356 | -122.3236 | 1.7624 | 1.7303 | 1.7258 | 1.7029 | 1.8585 | 1.886 | 1.4053 | -0.25177 | -0.022889 | 123.8022 | 123.8342 | -0.12817 | 123.4772 | 0.027465 | 124.054 | 123.7747 | 123.9304 | 123.8022 | 123.9075 | 123.8022 | 123.9578 | 123.7976 | 123.4772 | 123.9075 | 123.8022 | 123.7976 | 123.8022 | 123.9578 | -124.1821 | -0.45319
1759.6406 | 124.1364 | -121.9986 | 1.8814 | -0.10963 | 0.046649 | 0.043739 | 0.021371 | -0.0039563 | 0.00027774 | 0.010066 | 1.7303 | 1.8219 | -122.2733 | 1.799 | 1.799 | 1.8356 | 1.6479 | 1.9592 | 1.9043 | 1.4648 | -0.27466 | -0.05951 | 123.7289 | 123.7976 | -0.082398 | 123.4634 | 0.022888 | 124.0036 | 123.6465 | 123.9578 | 123.7976 | 123.8205 | 123.7289 | 123.9029 | 123.8342 | 123.4634 | 123.8205 | 123.7289 | 123.8342 | 123.7976 | 123.9029 | -124.1547 | -0.41657
1760.6406 | 124.1318 | -122.0169 | 1.8723 | -0.19356 | 0.043872 | 0.045448 | 0.024148 | -0.0069471 | -0.0027131 | 0.006648 | 1.767 | 1.8082 | -122.2687 | 1.8311 | 1.8173 | 1.8265 | 1.6479 | 1.9684 | 1.8997 | 1.4694 | -0.25177 | -0.064086 | 123.7839 | 123.848 | -0.054931 | 123.4863 | 0.027466 | 124.0356 | 123.6649 | 123.9853 | 123.8342 | 123.8251 | 123.7839 | 123.9166 | 123.8434 | 123.4863 | 123.8251 | 123.7839 | 123.8434 | 123.8342 | 123.9166 | -124.1409 | -0.40283
1761.6562 | 124.0768 | -122.0398 | 1.8906 | -0.51399 | 0.048358 | 0.049507 | 0.031625 | -0.0045971 | 6.414e-05 | 0.0053662 | 1.7944 | 1.9226 | -122.2412 | 1.7944 | 1.7487 | 1.7715 | 1.7258 | 1.8906 | 1.9409 | 1.4648 | -0.20142 | 0.032043 | 123.8342 | 123.8342 | -0.14191 | 123.5046 | 0.050354 | 124.0356 | 123.7656 | 123.9304 | 123.7885 | 123.9624 | 123.8342 | 123.9807 | 123.8113 | 123.5046 | 123.9624 | 123.8342 | 123.8113 | 123.7885 | 123.9807 | -124.1318 | -0.42572
1762.6406 | 124.0952 | -122.0444 | 1.8906 | -0.23933 | 0.045581 | 0.046303 | 0.023294 | -0.0067335 | 0.00049134 | 0.0072888 | 1.7487 | 1.8539 | -122.3099 | 1.7761 | 1.7944 | 1.7807 | 1.767 | 1.9089 | 1.9455 | 1.4603 | -0.2655 | -0.036621 | 123.793 | 123.8205 | -0.09613 | 123.5046 | 0.054932 | 124.0585 | 123.8113 | 123.9532 | 123.8388 | 123.8983 | 123.793 | 123.9899 | 123.8251 | 123.5046 | 123.8983 | 123.793 | 123.8251 | 123.8388 | 123.9899 | -124.2004 | -0.4303
1763.6406 | 124.1364 | -121.9803 | 1.9455 | -0.25459 | 0.043872 | 0.042244 | 0.024362 | -0.0063061 | -0.0020721 | 0.0079296 | 1.8173 | 1.8723 | -122.2412 | 1.8723 | 1.8723 | 1.886 | 1.7029 | 2.0279 | 1.9409 | 1.5289 | -0.26093 | -0.073243 | 123.7976 | 123.8525 | -0.073243 | 123.5092 | -0.004578 | 124.0585 | 123.6832 | 124.0082 | 123.8525 | 123.8525 | 123.7976 | 123.9212 | 123.8663 | 123.5092 | 123.8525 | 123.7976 | 123.8663 | 123.8525 | 123.9212 | -124.1867 | -0.41656
1764.6562 | 124.0402 | -122.0444 | 1.9226 | -0.063858 | 0.048144 | 0.045876 | 0.032693 | -0.0026745 | -0.0014313 | 0.0079296 | 1.7899 | 1.8768 | -122.2549 | 1.7761 | 1.7395 | 1.7578 | 1.7578 | 1.8723 | 1.9547 | 1.4603 | -0.21057 | -0.045776 | 123.8342 | 123.8205 | -0.1831 | 123.5046 | 0.032044 | 124.0448 | 123.8022 | 123.9166 | 123.7839 | 123.9212 | 123.8342 | 123.999 | 123.8022 | 123.5046 | 123.9212 | 123.8342 | 123.8022 | 123.7839 | 123.999 | -124.1776 | -0.46234
1765.6562 | 123.848 | -122.0215 | 1.9318 | 0.81352 | 0.052844 | 0.053139 | 0.029489 | -0.0022473 | 0.0011321 | 0.0075024 | 1.7578 | 1.9043 | -122.1954 | 1.7258 | 1.712 | 1.7487 | 1.7624 | 1.8311 | 1.9684 | 1.4786 | -0.17395 | -0.027466 | 123.7793 | 123.7473 | -0.21973 | 123.5001 | 0.036621 | 123.9532 | 123.7839 | 123.8525 | 123.7335 | 123.9258 | 123.7793 | 123.9899 | 123.7701 | 123.5001 | 123.9258 | 123.7793 | 123.7701 | 123.7335 | 123.9899 | -124.1272 | -0.45319
1766.6406 | 124.1409 | -121.994 | 1.8997 | -0.0028231 | 0.047076 | 0.047371 | 0.019448 | -0.0024609 | -0.0010041 | 0.01092 | 1.7624 | 1.8402 | -122.2778 | 1.8127 | 1.8265 | 1.8814 | 1.6937 | 1.9821 | 1.9409 | 1.5015 | -0.28381 | -0.059509 | 123.7564 | 123.8068 | -0.073242 | 123.4955 | 0.041199 | 124.0402 | 123.6877 | 123.9761 | 123.8205 | 123.8342 | 123.7564 | 123.9349 | 123.8754 | 123.4955 | 123.8342 | 123.7564 | 123.8754 | 123.8205 | 123.9349 | -124.1776 | -0.39825
1767.6406 | 124.1547 | -122.0123 | 1.9089 | 0.2108 | 0.050494 | 0.048653 | 0.022653 | -0.0058789 | 0.00027774 | 0.0075024 | 1.8173 | 1.8265 | -122.2733 | 1.8494 | 1.8402 | 1.8814 | 1.6663 | 2.0279 | 1.9409 | 1.5106 | -0.26093 | -0.082398 | 123.8297 | 123.8617 | -0.068665 | 123.5229 | 0.032043 | 124.0906 | 123.6786 | 124.0402 | 123.8525 | 123.8388 | 123.8297 | 123.9532 | 123.8937 | 123.5229 | 123.8388 | 123.8297 | 123.8937 | 123.8525 | 123.9532 | -124.1821 | -0.39826
1768.6406 | 124.2645 | -121.8246 | 2.1011 | -0.6971 | 0.050281 | 0.050362 | 0.024575 | -0.0058789 | -0.0024995 | 0.0068616 | 2.005 | 2.0187 | -122.0718 | 2.0599 | 2.0416 | 2.0737 | 1.8631 | 2.2202 | 2.1286 | 1.7166 | -0.24719 | -0.082397 | 123.8297 | 123.8846 | -0.059509 | 123.5413 | 0.027466 | 124.0768 | 123.6877 | 124.0448 | 123.8663 | 123.8434 | 123.8297 | 123.9532 | 123.8983 | 123.5413 | 123.8434 | 123.8297 | 123.8983 | 123.8663 | 123.9532 | -124.173 | -0.38452
1769.6406 | 124.0723 | -121.9254 | 2.037 | -0.20119 | 0.050921 | 0.048866 | 0.024789 | -0.0071607 | 0.00091854 | 0.006648 | 1.9089 | 1.9547 | -122.1542 | 1.9547 | 1.9226 | 1.9547 | 1.8448 | 2.0966 | 2.0508 | 1.6067 | -0.22888 | -0.082397 | 123.8342 | 123.88 | -0.11444 | 123.5321 | 0.013733 | 124.0631 | 123.7701 | 124.0219 | 123.848 | 123.88 | 123.8342 | 123.9761 | 123.88 | 123.5321 | 123.88 | 123.8342 | 123.88 | 123.848 | 123.9761 | -124.1913 | -0.4303
1770.6562 | 124.086 | -121.8933 | 2.092 | 0.058212 | 0.06438 | 0.06852 | 0.032266 | -0.0039563 | -0.00079046 | 0.0070752 | 1.9455 | 2.0737 | -122.1268 | 1.9409 | 1.886 | 1.9043 | 1.9638 | 2.0187 | 2.1378 | 1.6296 | -0.23346 | -0.018311 | 123.8388 | 123.8342 | -0.20599 | 123.5229 | 0.045776 | 124.0723 | 123.8571 | 123.912 | 123.7793 | 123.967 | 123.8388 | 124.0311 | 123.7976 | 123.5229 | 123.967 | 123.8388 | 123.7976 | 123.7793 | 124.0311 | -124.2188 | -0.46234
1771.6406 | 124.1913 | -121.8887 | 2.037 | -0.19356 | 0.053912 | 0.052925 | 0.021585 | -0.0041699 | -0.0018585 | 0.0062206 | 2.1835 | 1.9821 | -122.1542 | 2.0416 | 2.0004 | 2.0004 | 1.8356 | 2.179 | 2.0645 | 1.6617 | -0.2655 | -0.054931 | 124.0723 | 123.9304 | -0.036621 | 123.5504 | 0.027466 | 124.3378 | 123.7244 | 124.0677 | 123.8892 | 123.8709 | 124.0723 | 123.9532 | 123.8892 | 123.5504 | 123.8709 | 124.0723 | 123.8892 | 123.8892 | 123.9532 | -124.1913 | -0.37537
1772.6406 | 124.1501 | -121.9162 | 2.0187 | -0.056229 | 0.094073 | 0.093514 | 0.02073 | -0.0058789 | -0.0018585 | 0.0064344 | 1.8814 | 1.9684 | -122.1771 | 1.9592 | 1.9455 | 1.9821 | 1.7807 | 2.1149 | 2.0416 | 1.6251 | -0.26093 | -0.050354 | 123.7976 | 123.8754 | -0.073242 | 123.5413 | 0.022888 | 124.0585 | 123.6969 | 124.0311 | 123.8617 | 123.8846 | 123.7976 | 123.9578 | 123.8983 | 123.5413 | 123.8846 | 123.7976 | 123.8983 | 123.8617 | 123.9578 | -124.1959 | -0.39368
1773.6562 | 124.0997 | -122.0261 | 1.9409 | -0.056229 | 0.050494 | 0.047157 | 0.032052 | -0.0050245 | -0.00079046 | 0.006648 | 1.8311 | 1.9409 | -122.2366 | 1.8356 | 1.7899 | 1.8265 | 1.7715 | 1.9363 | 1.9775 | 1.506 | -0.21057 | 0 | 123.8571 | 123.8617 | -0.15106 | 123.5321 | 0.036621 | 124.0677 | 123.7976 | 123.9624 | 123.8159 | 123.967 | 123.8571 | 124.0036 | 123.8525 | 123.5321 | 123.967 | 123.8571 | 123.8525 | 123.8159 | 124.0036 | -124.1776 | -0.43488
1774.6406 | 124.1821 | -121.9254 | 1.9547 | -0.15541 | 0.048785 | 0.049721 | 0.02073 | -0.0086561 | -0.0057037 | 0.010066 | 1.918 | 1.918 | -122.1725 | 1.8494 | 1.6617 | 1.8448 | 1.7944 | 1.9821 | 1.9958 | 1.561 | -0.24719 | -0.036621 | 123.8434 | 123.7747 | -0.29297 | 123.4863 | 0.041199 | 124.0906 | 123.7198 | 123.9075 | 123.587 | 123.8434 | 123.8434 | 123.9212 | 123.7701 | 123.4863 | 123.8434 | 123.8434 | 123.7701 | 123.587 | 123.9212 | -124.1272 | -0.39368
1775.6406 | 124.1959 | -121.9437 | 1.9913 | -0.19356 | 0.050281 | 0.050362 | 0.024575 | -0.0073743 | -0.0020721 | 0.0096386 | 1.8906 | 1.9272 | -122.2092 | 1.9226 | 1.918 | 1.9318 | 1.7578 | 2.0966 | 2.005 | 1.5976 | -0.2655 | -0.064087 | 123.8342 | 123.8663 | -0.073242 | 123.5413 | 0.013733 | 124.0997 | 123.7015 | 124.0402 | 123.8617 | 123.8708 | 123.8342 | 123.9487 | 123.8754 | 123.5413 | 123.8708 | 123.8342 | 123.8754 | 123.8617 | 123.9487 | -124.2004 | -0.39368
1776.6562 | 124.1089 | -122.0261 | 1.9821 | 0.027695 | 0.057971 | 0.072151 | 0.032052 | -0.0020337 | 6.414e-05 | 0.0062206 | 1.8448 | 1.9501 | -122.0444 | 1.8219 | 1.7853 | 1.8082 | 1.8173 | 1.9363 | 1.9913 | 1.5472 | -0.018311 | -0.032044 | 123.8708 | 123.848 | -0.19684 | 123.5733 | 0.009155 | 123.8892 | 123.8434 | 123.9624 | 123.8113 | 123.9761 | 123.8708 | 124.0173 | 123.8342 | 123.5733 | 123.9761 | 123.8708 | 123.8342 | 123.8113 | 124.0173 | -124.0265 | -0.43488
1777.6406 | 123.9441 | -121.9894 | 2.0554 | -0.29274 | 0.1353 | 0.13902 | 0.023721 | -0.0045971 | 0.0013457 | 0.0072888 | 1.8036 | 2.0004 | -122.2229 | 1.7853 | 1.8723 | 1.8723 | 1.886 | 2.0142 | 2.1149 | 1.5839 | -0.23346 | -0.054932 | 123.793 | 123.7747 | -0.18311 | 123.5733 | 0.059509 | 124.0265 | 123.8754 | 124.0036 | 123.8617 | 123.9899 | 123.793 | 124.1043 | 123.8617 | 123.5733 | 123.9899 | 123.793 | 123.8617 | 123.8617 | 124.1043 | -124.2783 | -0.4715
1778.6406 | 124.2325 | -121.9986 | 1.9272 | -0.22408 | 0.081256 | 0.089668 | 0.023721 | -0.0052381 | -0.0024995 | 0.006648 | 1.8311 | 1.8997 | -122.2549 | 1.8768 | 1.8951 | 1.8951 | 1.712 | 2.0508 | 1.9638 | 1.5335 | -0.25635 | -0.027466 | 123.8297 | 123.8754 | -0.032043 | 123.5321 | 0.036621 | 124.086 | 123.7106 | 124.0494 | 123.8937 | 123.8983 | 123.8297 | 123.9624 | 123.8937 | 123.5321 | 123.8983 | 123.8297 | 123.8937 | 123.8937 | 123.9624 | -124.1821 | -0.39368
1779.6406 | 124.0814 | -122.0993 | 1.9455 | 0.058212 | 0.0045651 | 0.0012283 | 0.02543 | -0.0041699 | -0.0018585 | 0.007716 | 1.7899 | 1.9135 | 1.4282 | 1.7578 | 1.7166 | 1.7349 | 1.799 | 1.8539 | 1.9638 | 1.4832 | 123.5275 | -0.032044 | 123.8892 | 123.8571 | -0.22888 | 123.5825 | 0.01831 | 0.36163 | 123.8983 | 123.9532 | 123.8159 | 124.0128 | 123.8892 | 124.0631 | 123.8342 | 123.5825 | 124.0128 | 123.8892 | 123.8342 | 123.8159 | 124.0631 | -0.51727 | -0.46234
1780.6406 | 124.1364 | -122.0032 | 1.9821 | -0.23933 | 0.0049923 | -0.0017625 | 0.019876 | -0.0045971 | -0.0020721 | 0.006007 | 1.8723 | 1.9226 | 1.5015 | 1.8585 | 1.8585 | 1.886 | 1.799 | 2.0142 | 2.0279 | 1.5518 | 123.5046 | -0.05951 | 123.8754 | 123.8617 | -0.1236 | 123.555 | 0.045776 | 0.37079 | 123.8022 | 124.0173 | 123.8617 | 123.9258 | 123.8754 | 124.0311 | 123.8892 | 123.555 | 123.9258 | 123.8754 | 123.8892 | 123.8617 | 124.0311 | -0.48065 | -0.4303
1781.6406 | 124.1959 | -121.994 | 1.9547 | -0.44533 | 0.0024289 | -0.0030441 | 0.020303 | -0.0071607 | -0.0014313 | 0.0085706 | 1.8127 | 1.8539 | 1.474 | 1.8814 | 1.8585 | 1.8906 | 1.6846 | 2.0508 | 1.9318 | 1.5244 | 123.468 | -0.10071 | 123.8068 | 123.8754 | -0.09613 | 123.5184 | -0.022888 | 0.33874 | 123.6786 | 124.0448 | 123.8525 | 123.848 | 123.8068 | 123.9258 | 123.8846 | 123.5184 | 123.848 | 123.8068 | 123.8846 | 123.8525 | 123.9258 | -0.48065 | -0.4303
1782.6562 | 124.0906 | -122.0306 | 1.9638 | 0.035324 | 0.0094785 | 0.00080115 | 0.027352 | -0.0039563 | -0.00014946 | 0.0064344 | 1.8356 | 1.9547 | 1.4877 | 1.7899 | 1.7532 | 1.7761 | 1.8127 | 1.8906 | 1.9821 | 1.5015 | 123.5184 | -0.009155 | 123.8663 | 123.8205 | -0.21057 | 123.5321 | 0.018311 | 0.3479 | 123.8434 | 123.9212 | 123.7839 | 123.9853 | 123.8663 | 124.0128 | 123.8068 | 123.5321 | 123.9853 | 123.8663 | 123.8068 | 123.7839 | 124.0128 | -0.47607 | -0.46234
1783.6406 | 124.1684 | -121.8979 | 2.0828 | -0.1783 | 0.0022153 | -0.0017625 | 0.022866 | -0.0056653 | -0.0024995 | 0.0068616 | 1.9363 | 1.9913 | 1.6113 | 1.9775 | 1.9775 | 2.0004 | 1.8677 | 2.1423 | 2.0874 | 1.6388 | 123.5092 | -0.091553 | 123.8342 | 123.8754 | -0.10529 | 123.5367 | 0.004577 | 0.32501 | 123.7656 | 124.0402 | 123.8754 | 123.8892 | 123.8342 | 123.9853 | 123.8983 | 123.5367 | 123.8892 | 123.8342 | 123.8983 | 123.8754 | 123.9853 | -0.4715 | -0.44403
1784.6406 | 124.1913 | -121.9391 | 2.0233 | -0.20119 | 0.0041379 | -0.0028305 | 0.019876 | -0.0054517 | -0.0014313 | 0.0079296 | 1.9226 | 1.9547 | 1.5793 | 1.9363 | 1.9409 | 1.9592 | 1.7944 | 2.1057 | 2.0325 | 1.6022 | 123.5184 | -0.068664 | 123.8617 | 123.8754 | -0.082397 | 123.5413 | 0.009156 | 0.34332 | 123.7335 | 124.0448 | 123.88 | 123.8937 | 123.8617 | 123.9716 | 123.8983 | 123.5413 | 123.8937 | 123.8617 | 123.8983 | 123.88 | 123.9716 | -0.44403 | -0.42114
1785.6562 | 124.1043 | -122.0032 | 2.0142 | -0.018082 | 0.0088375 | 0.00058755 | 0.031411 | -0.0054517 | -0.00057686 | 0.0064344 | 1.886 | 2.0004 | 1.5289 | 1.8539 | 1.8036 | 1.8448 | 1.8448 | 1.9775 | 2.0416 | 1.5427 | 123.5321 | -0.013733 | 123.8892 | 123.8571 | -0.21057 | 123.5458 | 0.027466 | 0.35705 | 123.848 | 123.9807 | 123.8068 | 124.0036 | 123.8892 | 124.0448 | 123.848 | 123.5458 | 124.0036 | 123.8892 | 123.848 | 123.8068 | 124.0448 | -0.48523 | -0.4715
1786.6406 | 124.0768 | -121.8384 | 2.1194 | -0.14778 | 0.0041379 | -0.0073167 | 0.01838 | -0.0043835 | -0.0012177 | 0.0072888 | 2.0462 | 2.0508 | 1.7075 | 2.0874 | 2.1011 | 2.124 | 1.8677 | 2.504 | 2.1561 | 1.7303 | 123.5458 | -0.068665 | 123.8846 | 123.9258 | -0.018311 | 123.5687 | 0.036621 | 0.33875 | 123.7061 | 124.3423 | 123.9395 | 123.8892 | 123.8846 | 123.9944 | 123.9624 | 123.5687 | 123.8892 | 123.8846 | 123.9624 | 123.9395 | 123.9944 | -0.41199 | -0.3891
1787.6406 | 124.2233 | -121.7743 | 2.1835 | -0.23933 | 0.0047787 | -0.0030441 | 0.021371 | -0.0045971 | -0.0050629 | 0.0087842 | 2.1057 | 2.124 | 1.7532 | 2.124 | 2.124 | 2.1423 | 1.9501 | 2.3071 | 2.2064 | 1.7715 | 123.5275 | -0.05951 | 123.88 | 123.8983 | -0.05951 | 123.5458 | 0.022888 | 0.35248 | 123.7244 | 124.0814 | 123.8983 | 123.8983 | 123.88 | 123.9807 | 123.9166 | 123.5458 | 123.8983 | 123.88 | 123.9166 | 123.8983 | 123.9807 | -0.4303 | -0.41199
1788.6406 | 124.1638 | -121.9803 | 2.0599 | -0.20119 | 0.0056333 | -0.0043259 | 0.027352 | -0.0054517 | -0.00079046 | 0.0053662 | 1.9089 | 2.0187 | 1.5701 | 1.9089 | 1.8814 | 1.8997 | 1.9318 | 2.0462 | 2.0874 | 1.5884 | 123.5504 | -0.041199 | 123.8892 | 123.8892 | -0.17853 | 123.5687 | 0.027465 | 0.33875 | 123.912 | 124.0265 | 123.8617 | 123.999 | 123.8892 | 124.0677 | 123.88 | 123.5687 | 123.999 | 123.8892 | 123.88 | 123.8617 | 124.0677 | -0.48981 | -0.4715
1789.6406 | 124.118 | -122.0261 | 2.0279 | -0.24696 | 0.0030697 | -0.0043259 | 0.022866 | -0.0043835 | -0.00036306 | 0.0064344 | 1.8402 | 1.9958 | 1.5244 | 1.8448 | 1.8219 | 1.8448 | 1.9089 | 1.9775 | 2.0416 | 1.5656 | 123.5504 | -0.032043 | 123.8663 | 123.8708 | -0.20599 | 123.5916 | 0.013733 | 0.31586 | 123.9349 | 124.0036 | 123.848 | 124.0219 | 123.8663 | 124.0677 | 123.8708 | 123.5916 | 124.0219 | 123.8663 | 123.8708 | 123.848 | 124.0677 | -0.50354 | -0.46234
1790.6406 | 124.1913 | -121.9345 | 2.0554 | -0.18593 | 0.0022153 | -0.0032577 | 0.018807 | -0.0065197 | -0.0018585 | 0.0089978 | 1.9409 | 1.973 | 1.5884 | 1.9592 | 1.9455 | 1.9592 | 1.8448 | 2.1332 | 2.0782 | 1.6205 | 123.5229 | -0.082398 | 123.8754 | 123.8937 | -0.10986 | 123.555 | 0.022888 | 0.35248 | 123.7793 | 124.0677 | 123.88 | 123.9075 | 123.8754 | 124.0128 | 123.8937 | 123.555 | 123.9075 | 123.8754 | 123.8937 | 123.88 | 124.0128 | -0.46692 | -0.43488
1791.6406 | 124.1547 | -122.0169 | 2.005 | -0.18593 | 0.0075559 | 0.00037395 | 0.026284 | -0.0020337 | -0.00057686 | 0.0053662 | 1.918 | 1.9867 | 1.5289 | 1.8814 | 1.8539 | 1.8768 | 1.8402 | 2.0325 | 2.0508 | 1.561 | 123.5458 | -0.018311 | 123.9349 | 123.8983 | -0.15106 | 123.5779 | 0.045776 | 0.3891 | 123.8571 | 124.0494 | 123.8709 | 124.0036 | 123.9349 | 124.0677 | 123.8937 | 123.5779 | 124.0036 | 123.9349 | 123.8937 | 123.8709 | 124.0677 | -0.47607 | -0.44403
1792.6406 | 124.2096 | -122.0306 | 1.9455 | -0.19356 | 0.0049923 | -0.0038987 | 0.022225 | -0.0045971 | -0.0010041 | 0.0075024 | 1.8631 | 1.8951 | 1.506 | 1.8814 | 1.8723 | 1.8997 | 1.7303 | 2.0325 | 1.9867 | 1.5518 | 123.5367 | -0.050354 | 123.8937 | 123.912 | -0.073243 | 123.5825 | 0.041198 | 0.35706 | 123.761 | 124.0631 | 123.9029 | 123.9258 | 123.8937 | 124.0173 | 123.9304 | 123.5825 | 123.9258 | 123.8937 | 123.9304 | 123.9029 | 124.0173 | -0.43945 | -0.39368
1793.6406 | 124.1135 | -122.0169 | 2.0325 | -0.26222 | 0.0077695 | -0.0011215 | 0.02543 | -0.0073743 | -0.00014946 | 0.0064344 | 1.9226 | 2.005 | 1.5244 | 1.8127 | 1.8311 | 1.8585 | 1.9089 | 1.9684 | 2.0874 | 1.5656 | 123.5413 | -0.027466 | 123.9395 | 123.8297 | -0.20142 | 123.5825 | 0.054931 | 0.39825 | 123.9258 | 123.9853 | 123.848 | 124.0219 | 123.9395 | 124.1043 | 123.8754 | 123.5825 | 124.0219 | 123.9395 | 123.8754 | 123.848 | 124.1043 | -0.50812 | -0.46692
1794.6562 | 124.1592 | -121.907 | 2.0966 | 0.67619 | 0.0092649 | -0.0028305 | 0.029916 | -0.0033155 | -0.0029267 | 0.0072888 | 2.0416 | 2.1286 | 1.68 | 1.9592 | 1.9501 | 1.9592 | 1.9089 | 2.0782 | 2.1378 | 1.6525 | 123.587 | 0.032043 | 123.9487 | 123.8663 | -0.14648 | 123.5596 | 0.041198 | 0.36163 | 123.8159 | 123.9853 | 123.8571 | 124.0356 | 123.9487 | 124.0448 | 123.8663 | 123.5596 | 124.0356 | 123.9487 | 123.8663 | 123.8571 | 124.0448 | -0.41656 | -0.44403
1795.6406 | 124.1409 | -121.9345 | 2.1057 | -0.23933 | 0.0047787 | -0.0058213 | 0.022439 | -0.0041699 | -0.00036306 | 0.007716 | 1.9638 | 2.0325 | 1.6479 | 1.9684 | 1.9501 | 1.9821 | 1.9684 | 2.1149 | 2.1515 | 1.68 | 123.5825 | -0.073242 | 123.8983 | 123.9029 | -0.15564 | 123.6145 | 0.045776 | 0.31586 | 123.9029 | 124.0494 | 123.8846 | 123.967 | 123.8983 | 124.086 | 123.9166 | 123.6145 | 123.967 | 123.8983 | 123.9166 | 123.8846 | 124.086 | -0.45776 | -0.42572
1796.6406 | 124.1638 | -121.9711 | 2.0874 | -0.30037 | 0.0034971 | -0.0049667 | 0.019876 | -0.0048107 | -0.0018585 | 0.0053662 | 1.8997 | 1.9913 | 1.593 | 1.9089 | 1.9226 | 1.9363 | 1.8997 | 2.0782 | 2.0782 | 1.6159 | 123.5641 | -0.09613 | 123.8708 | 123.88 | -0.1648 | 123.587 | -0.009155 | 0.3067 | 123.8708 | 124.0494 | 123.8937 | 123.9624 | 123.8708 | 124.0494 | 123.9075 | 123.587 | 123.9624 | 123.8708 | 123.9075 | 123.8937 | 124.0494 | -0.49438 | -0.4715
1797.6562 | 124.1089 | -121.9666 | 2.1103 | 0.035324 | 0.0081967 | -0.0028305 | 0.026284 | -0.0028881 | -0.0018585 | 0.0079296 | 1.9363 | 2.0599 | 1.5976 | 1.8997 | 1.8768 | 1.8997 | 1.9775 | 2.0142 | 2.1332 | 1.6205 | 123.5641 | -0.050354 | 123.9029 | 123.8663 | -0.23346 | 123.587 | 0.022888 | 0.33874 | 123.9441 | 123.9807 | 123.8434 | 124.0265 | 123.9029 | 124.0997 | 123.8663 | 123.587 | 124.0265 | 123.9029 | 123.8663 | 123.8434 | 124.0997 | -0.5127 | -0.48981
1798.6406 | 124.1776 | -121.9391 | 2.0782 | -0.26222 | 0.0058469 | -0.00069425 | 0.020516 | -0.0050245 | -0.0018585 | 0.0047254 | 1.9501 | 2.0325 | 1.6251 | 1.9592 | 1.9501 | 1.9867 | 1.9135 | 2.1194 | 2.1103 | 1.6617 | 123.5641 | -0.045776 | 123.8892 | 123.8983 | -0.12817 | 123.6008 | 0.032044 | 0.32501 | 123.8525 | 124.0585 | 123.8892 | 123.9716 | 123.8892 | 124.0494 | 123.9258 | 123.6008 | 123.9716 | 123.8892 | 123.9258 | 123.8892 | 124.0494 | -0.45319 | -0.41657
1799.6406 | 124.1867 | -121.9391 | 2.0874 | -0.24696 | 0.0043515 | -0.0024033 | 0.021371 | -0.0050245 | -0.0012177 | 0.0098522 | 1.9455 | 2.0142 | 1.6342 | 1.9638 | 1.9547 | 1.9638 | 1.9043 | 2.124 | 2.092 | 1.6479 | 123.5733 | -0.073242 | 123.8846 | 123.9029 | -0.13275 | 123.587 | 0.004578 | 0.31128 | 123.8434 | 124.0631 | 123.8937 | 123.9532 | 123.8846 | 124.0311 | 123.9029 | 123.587 | 123.9532 | 123.8846 | 123.9029 | 123.8937 | 124.0311 | -0.45319 | -0.43945
1800.6406 | 124.1592 | -122.0078 | 2.0782 | -0.25459 | 0.0086239 | 0.0018691 | 0.029061 | -0.0041699 | -0.0029267 | 0.0062206 | 1.9135 | 2.0279 | 1.5747 | 1.8951 | 1.8814 | 1.9043 | 1.9043 | 2.0416 | 2.0874 | 1.5976 | 123.5825 | -0.050354 | 123.9212 | 123.9029 | -0.19684 | 123.6053 | 0.009155 | 0.33874 | 123.912 | 124.0494 | 123.8892 | 124.0356 | 123.9212 | 124.0952 | 123.912 | 123.6053 | 124.0356 | 123.9212 | 123.912 | 123.8892 | 124.0952 | -0.50354 | -0.48065
1801.6406 | 124.1089 | -121.8704 | 2.2156 | -0.25459 | 0.0069149 | -0.0047531 | 0.022012 | -0.0039563 | -0.0020721 | 0.008357 | 1.9547 | 2.1286 | 1.6754 | 1.9638 | 1.9592 | 1.9592 | 2.449 | 2.298 | 2.2339 | 1.6983 | 123.5458 | -0.086975 | 123.8251 | 123.8342 | -0.25635 | 123.5687 | 0.018311 | 0.27924 | 124.3195 | 124.1684 | 123.8297 | 123.999 | 123.8251 | 124.1043 | 123.8297 | 123.5687 | 123.999 | 123.8251 | 123.8297 | 123.8297 | 124.1043 | -0.54016 | -0.51727
1802.6562 | 124.1547 | -121.9299 | 2.1194 | -0.025711 | 0.010333 | 0.0042191 | 0.027993 | -0.0016065 | -0.00014946 | 0.0087842 | 2.0142 | 2.1103 | 1.6571 | 1.9821 | 1.9547 | 1.9775 | 1.9592 | 2.0966 | 2.1698 | 1.6937 | 123.587 | -0.009155 | 123.9441 | 123.912 | -0.1648 | 123.6237 | 0.050354 | 0.35706 | 123.8892 | 124.0265 | 123.8846 | 124.0402 | 123.9441 | 124.0997 | 123.9075 | 123.6237 | 124.0402 | 123.9441 | 123.9075 | 123.8846 | 124.0997 | -0.46234 | -0.42572
1803.6406 | 124.0585 | -121.875 | 2.2018 | -0.28511 | 0.0049923 | 0.0025101 | 0.020303 | -0.0026745 | -0.00014946 | 0.0075024 | 1.9363 | 2.1103 | 1.6571 | 1.9409 | 1.9318 | 1.9455 | 2.037 | 2.1927 | 2.1881 | 1.6983 | 123.5321 | -0.091552 | 123.8113 | 123.8159 | -0.27008 | 123.5733 | -0.013733 | 0.27924 | 123.912 | 124.0677 | 123.8068 | 123.9853 | 123.8113 | 124.0631 | 123.8205 | 123.5733 | 123.9853 | 123.8113 | 123.8205 | 123.8068 | 124.0631 | -0.54474 | -0.50354
1804.6406 | 124.0997 | -121.9116 | 2.1469 | -0.2317 | 0.0069149 | -0.0036851 | 0.023507 | -0.0035291 | -0.00057686 | 0.0070752 | 1.8494 | 2.0325 | 1.5656 | 1.8997 | 1.8814 | 1.8951 | 1.9867 | 2.0508 | 2.124 | 1.6342 | 123.4772 | -0.11444 | 123.761 | 123.8113 | -0.2655 | 123.5458 | -0.022889 | 0.28381 | 123.8983 | 123.9624 | 123.793 | 123.9441 | 123.761 | 124.0356 | 123.8068 | 123.5458 | 123.9441 | 123.761 | 123.8068 | 123.793 | 124.0356 | -0.58136 | -0.5127
1805.6406 | 124.1867 | -121.9757 | 2.0737 | -0.25459 | 0.0064877 | 0.00016015 | 0.023721 | -0.0020337 | 6.414e-05 | 0.0068616 | 1.8814 | 2.0554 | 1.593 | 1.9135 | 1.9135 | 1.9318 | 1.9409 | 2.0691 | 2.1286 | 1.6205 | 123.5687 | -0.01831 | 123.8571 | 123.8892 | -0.16022 | 123.5962 | 0.054932 | 0.28839 | 123.9166 | 124.0448 | 123.8892 | 124.0311 | 123.8571 | 124.1043 | 123.9075 | 123.5962 | 124.0311 | 123.8571 | 123.9075 | 123.8892 | 124.1043 | -0.48065 | -0.45319
1806.6406 | 124.2142 | -121.907 | 2.1194 | -0.26985 | 0.0054197 | -0.0028305 | 0.020516 | -0.0031019 | -0.0022859 | 0.006648 | 1.7624 | 2.0508 | 1.4969 | 1.8906 | 1.886 | 1.8951 | 1.9775 | 2.0325 | 2.1423 | 1.6296 | 123.4039 | -0.068665 | 123.6694 | 123.7976 | -0.23346 | 123.5367 | 0.022888 | 0.2655 | 123.8846 | 123.9395 | 123.793 | 123.9578 | 123.6694 | 124.0494 | 123.8022 | 123.5367 | 123.9578 | 123.6694 | 123.8022 | 123.793 | 124.0494 | -0.62256 | -0.48981
1807.6406 | 124.1501 | -122.0673 | 2.0233 | 0.18028 | 0.0094785 | -0.0013351 | 0.026498 | -0.0028881 | 6.414e-05 | 0.0087842 | 1.8173 | 1.9867 | 1.5289 | 1.8127 | 1.7899 | 1.8219 | 1.8585 | 1.9318 | 2.0508 | 1.5518 | 123.5962 | -0.036621 | 123.8846 | 123.88 | -0.23346 | 123.6191 | 0.027466 | 0.28839 | 123.9258 | 123.999 | 123.8571 | 124.054 | 123.8846 | 124.118 | 123.8892 | 123.6191 | 124.054 | 123.8846 | 123.8892 | 123.8571 | 124.118 | -0.49438 | -0.4715
1808.6406 | 124.1409 | -122.0764 | 1.9821 | -0.31563 | 0.0069149 | -0.0032577 | 0.020944 | -0.0035291 | -0.00079046 | 0.0062206 | 1.7349 | 1.9409 | 1.4603 | 1.7899 | 1.7944 | 1.799 | 1.8723 | 1.9501 | 2.0279 | 1.5106 | 123.5367 | -0.041199 | 123.8113 | 123.8663 | -0.18768 | 123.587 | 0.045776 | 0.27466 | 123.9487 | 124.0265 | 123.8708 | 124.0173 | 123.8113 | 124.1043 | 123.8754 | 123.587 | 124.0173 | 123.8113 | 123.8754 | 123.8708 | 124.1043 | -0.52185 | -0.4715
1809.6406 | 124.1684 | -122.0947 | 1.9501 | -0.24696 | 0.0081967 | 0.0027237 | 0.024789 | -0.0033155 | -0.0035675 | 0.0072888 | 1.6846 | 1.9135 | 1.3962 | 1.7944 | 1.7807 | 1.7807 | 1.8631 | 1.9363 | 2.0096 | 1.5015 | 123.4909 | -0.036621 | 123.7793 | 123.8892 | -0.16937 | 123.5962 | 0.05951 | 0.28839 | 123.9578 | 124.0311 | 123.8754 | 124.0082 | 123.7793 | 124.1043 | 123.8754 | 123.5962 | 124.0082 | 123.7793 | 123.8754 | 123.8754 | 124.1043 | -0.55389 | -0.44861
1810.6406 | 124.1821 | -122.1039 | 1.9318 | 0.042953 | 0.0064877 | 0.0010147 | 0.027139 | -0.0024609 | -0.00079046 | 0.008357 | 1.8219 | 1.9547 | 1.4832 | 1.8173 | 1.8036 | 1.8219 | 1.7761 | 1.9409 | 1.9867 | 1.4923 | 123.587 | 0.022888 | 123.9258 | 123.9212 | -0.12817 | 123.5962 | 0.054931 | 0.33874 | 123.88 | 124.0448 | 123.9075 | 124.0585 | 123.9258 | 124.0906 | 123.9258 | 123.5962 | 124.0585 | 123.9258 | 123.9258 | 123.9075 | 124.0906 | -0.44861 | -0.43945
1811.6406 | 124.1547 | -122.0947 | 1.9913 | -0.26985 | 0.0052059 | -0.0028305 | 0.022012 | -0.0013929 | 0.00027774 | 0.0062206 | 1.7349 | 1.9363 | 1.442 | 1.8036 | 1.8402 | 1.7807 | 1.9043 | 1.9547 | 2.0508 | 1.5427 | 123.5367 | -0.054932 | 123.8297 | 123.8983 | -0.15106 | 123.6374 | 0.059509 | 0.29297 | 123.999 | 124.0494 | 123.9349 | 124.0311 | 123.8297 | 124.1455 | 123.8754 | 123.6374 | 124.0311 | 123.8297 | 123.8754 | 123.9349 | 124.1455 | -0.54932 | -0.44861
1812.6406 | 124.1959 | -122.0535 | 2.005 | -0.079117 | 0.0056333 | 0.0012283 | 0.026284 | -0.0026745 | -0.0031403 | 0.0057934 | 1.7258 | 1.9638 | 1.3916 | 1.8631 | 1.8768 | 1.8448 | 1.8494 | 1.9958 | 2.0554 | 1.5793 | 123.4451 | -0.041199 | 123.7793 | 123.9166 | -0.12817 | 123.6328 | 0.050354 | 0.33417 | 123.9029 | 124.0494 | 123.9304 | 124.0173 | 123.7793 | 124.1089 | 123.8983 | 123.6328 | 124.0173 | 123.7793 | 123.8983 | 123.9304 | 124.1089 | -0.6134 | -0.42572
1813.6406 | 124.1547 | -122.049 | 2.005 | -0.15541 | 0.0058469 | -0.0045395 | 0.022866 | -0.0013929 | -0.00079046 | 0.0075024 | 1.6663 | 1.9867 | 1.4008 | 1.8127 | 1.8219 | 1.8311 | 1.9318 | 1.973 | 2.0691 | 1.5564 | 123.4497 | -0.018311 | 123.7152 | 123.8617 | -0.18311 | 123.6053 | 0.064087 | 0.2655 | 123.9807 | 124.0219 | 123.8708 | 124.0356 | 123.7152 | 124.118 | 123.88 | 123.6053 | 124.0356 | 123.7152 | 123.88 | 123.8708 | 124.118 | -0.60425 | -0.44861
1814.6406 | 124.2325 | -122.0856 | 1.9409 | -0.19356 | 0.0037107 | -0.0017625 | 0.020303 | -0.0050245 | -0.00057686 | 0.0064344 | 1.8265 | 1.8768 | 1.4969 | 1.8585 | 1.8631 | 1.8768 | 1.7349 | 2.0279 | 1.9638 | 1.5289 | 123.5825 | -0.064087 | 123.912 | 123.9441 | -0.07782 | 123.6145 | 0.022888 | 0.32959 | 123.8205 | 124.1135 | 123.9487 | 123.9624 | 123.912 | 124.0494 | 123.9624 | 123.6145 | 123.9624 | 123.912 | 123.9624 | 123.9487 | 124.0494 | -0.44403 | -0.41199
1815.6562 | 124.1409 | -122.168 | 1.9135 | 0.16502 | 0.0056333 | -0.0017625 | 0.026284 | -0.0033155 | 0.00027774 | 0.0092114 | 1.7303 | 1.9043 | 1.4282 | 1.7029 | 1.6983 | 1.7441 | 1.7624 | 1.8356 | 1.9501 | 1.4603 | 123.5962 | -0.009155 | 123.8983 | 123.8709 | -0.21515 | 123.6282 | 0.036621 | 0.30212 | 123.9304 | 124.0036 | 123.8663 | 124.0723 | 123.8983 | 124.118 | 123.912 | 123.6282 | 124.0723 | 123.8983 | 123.912 | 123.8663 | 124.118 | -0.48523 | -0.45319
1816.6406 | 124.1272 | -122.1359 | 1.9775 | -0.26985 | 0.0064877 | -0.0028305 | 0.021798 | -0.0031019 | -0.0012177 | 0.0030164 | 1.712 | 1.8906 | 1.4236 | 1.918 | 1.9501 | 1.8173 | 1.68 | 1.9638 | 2.0142 | 1.4786 | 123.5596 | -0.086975 | 123.848 | 124.054 | -0.027466 | 123.6145 | 0.036621 | 0.28839 | 123.8159 | 124.0997 | 124.086 | 124.0265 | 123.848 | 124.1501 | 123.9532 | 123.6145 | 124.0265 | 123.848 | 123.9532 | 124.086 | 124.1501 | -0.55389 | -0.49896
1817.6406 | 124.1959 | -122.1725 | 1.918 | -0.14778 | 0.0069149 | -0.0021897 | 0.027566 | -0.0031019 | -0.0010041 | 0.0085706 | 1.6342 | 1.9135 | 1.3275 | 1.7624 | 1.7578 | 1.767 | 1.7899 | 1.9089 | 1.9547 | 1.4603 | 123.5001 | -0.004578 | 123.8068 | 123.9349 | -0.16022 | 123.6328 | 0.036621 | 0.3067 | 123.9624 | 124.0814 | 123.9304 | 124.086 | 123.8068 | 124.1272 | 123.9395 | 123.6328 | 124.086 | 123.8068 | 123.9395 | 123.9304 | 124.1272 | -0.59051 | -0.45776
1818.6406 | 124.1821 | -122.1313 | 1.9501 | -0.11726 | 0.0071285 | -0.0032577 | 0.025857 | -0.0028881 | -0.0024995 | 0.0075024 | 1.6434 | 1.918 | 1.3504 | 1.7761 | 1.7761 | 1.7853 | 1.8402 | 1.9226 | 1.9913 | 1.5015 | 123.4818 | -0.032043 | 123.7747 | 123.9075 | -0.17395 | 123.6328 | 0.041199 | 0.29297 | 123.9716 | 124.054 | 123.9075 | 124.0494 | 123.7747 | 124.1226 | 123.9166 | 123.6328 | 124.0494 | 123.7747 | 123.9166 | 123.9075 | 124.1226 | -0.59967 | -0.44861
1819.6406 | 124.1638 | -122.1405 | 1.9409 | 0.012436 | 0.0032833 | -0.0021897 | 0.022866 | -0.0016065 | 6.414e-05 | 0.0070752 | 1.6342 | 1.918 | 1.3412 | 1.7349 | 1.7303 | 1.7303 | 1.8356 | 1.8768 | 1.9684 | 1.4786 | 123.4818 | -0.022888 | 123.7747 | 123.8754 | -0.21057 | 123.6191 | 0.027466 | 0.29297 | 123.9761 | 124.0173 | 123.8708 | 124.0585 | 123.7747 | 124.1089 | 123.8708 | 123.6191 | 124.0585 | 123.7747 | 123.8708 | 123.8708 | 124.1089 | -0.59967 | -0.46234
1820.6562 | 124.1409 | -122.1909 | 1.9043 | 0.042953 | 0.0073423 | -0.0011215 | 0.026498 | -0.0033155 | -0.0020721 | 0.0070752 | 1.561 | 1.8814 | 1.3046 | 1.6891 | 1.6663 | 1.7029 | 1.767 | 1.8219 | 1.9226 | 1.442 | 123.4955 | -0.022888 | 123.7518 | 123.88 | -0.23804 | 123.6328 | 0.01831 | 0.25635 | 123.9578 | 124.0128 | 123.8571 | 124.0723 | 123.7518 | 124.1135 | 123.8937 | 123.6328 | 124.0723 | 123.7518 | 123.8937 | 123.8571 | 124.1135 | -0.59967 | -0.46234
1821.6406 | 124.2233 | -122.1451 | 1.8997 | -0.24696 | 0.0052059 | 0.0014419 | 0.019662 | -0.0024609 | -0.0020721 | 0.0072888 | 1.6296 | 1.8219 | 1.3367 | 1.7761 | 1.7853 | 1.799 | 1.7258 | 1.9455 | 1.918 | 1.4923 | 123.4818 | -0.07782 | 123.7747 | 123.9212 | -0.11444 | 123.6374 | 0.018311 | 0.29297 | 123.8709 | 124.0906 | 123.9304 | 123.967 | 123.7747 | 124.0631 | 123.9441 | 123.6374 | 123.967 | 123.7747 | 123.9441 | 123.9304 | 124.0631 | -0.56305 | -0.40741
1822.6406 | 124.1913 | -122.1451 | 1.9363 | -0.10963 | 0.0071285 | 0.0010147 | 0.02778 | -0.0037427 | -0.00036306 | 0.008357 | 1.6251 | 1.9089 | 1.3229 | 1.7624 | 1.7532 | 1.7807 | 1.8082 | 1.918 | 1.9592 | 1.4832 | 123.468 | -0.027465 | 123.7701 | 123.9075 | -0.1831 | 123.6282 | 0.022889 | 0.30212 | 123.9532 | 124.0631 | 123.8983 | 124.054 | 123.7701 | 124.1043 | 123.9258 | 123.6282 | 124.054 | 123.7701 | 123.9258 | 123.8983 | 124.1043 | -0.6134 | -0.45319
1823.6406 | 124.2599 | -122.1725 | 1.8723 | -0.22408 | 0.0047787 | -0.0036851 | 0.020089 | -0.0039563 | 0.00027774 | 0.0075024 | 1.6113 | 1.799 | 1.3092 | 1.7807 | 1.7853 | 1.8127 | 1.6617 | 1.9638 | 1.9043 | 1.4557 | 123.4817 | -0.073242 | 123.7839 | 123.9532 | -0.086975 | 123.6282 | 0.032044 | 0.30212 | 123.8342 | 124.1364 | 123.9578 | 123.9716 | 123.7839 | 124.0768 | 123.9853 | 123.6282 | 123.9716 | 123.7839 | 123.9853 | 123.9578 | 124.0768 | -0.56305 | -0.41656
1824.6406 | 124.2004 | -122.2321 | 1.8814 | -0.26985 | 0.0045651 | -0.0015489 | 0.02073 | -0.0052381 | -0.00014946 | 0.008357 | 1.5839 | 1.799 | 1.2772 | 1.7075 | 1.7166 | 1.7166 | 1.7166 | 1.8585 | 1.9043 | 1.4053 | 123.5092 | -0.082398 | 123.8159 | 123.9395 | -0.1648 | 123.6374 | 0.022888 | 0.3067 | 123.9487 | 124.0906 | 123.9487 | 124.0311 | 123.8159 | 124.1364 | 123.9487 | 123.6374 | 124.0311 | 123.8159 | 123.9487 | 123.9487 | 124.1364 | -0.60425 | -0.47608
1825.6562 | 124.1592 | -122.2458 | 1.8494 | 3.9492 | 0.0086239 | -0.0045395 | 0.025216 | -0.0016065 | 6.414e-05 | 0.0072888 | 1.7166 | 1.8265 | 1.268 | 1.6571 | 1.6617 | 1.6434 | 1.6846 | 1.767 | 1.8997 | 1.3916 | 123.5138 | -0.022888 | 123.9624 | 123.9029 | -0.18768 | 123.6374 | 0.050354 | 0.44861 | 123.9304 | 124.0128 | 123.9075 | 124.0723 | 123.9624 | 124.1455 | 123.8892 | 123.6374 | 124.0723 | 123.9624 | 123.8892 | 123.9075 | 124.1455 | -0.58136 | -0.45776
1826.6406 | 124.1364 | -122.2549 | 1.8356 | -0.13252 | 0.0062741 | 0.00080115 | 0.023721 | -0.0033155 | -0.0016449 | 0.007716 | 1.5198 | 1.8082 | 1.236 | 1.6388 | 1.6251 | 1.6251 | 1.7258 | 1.7899 | 1.886 | 1.3733 | 123.4909 | -0.027465 | 123.7747 | 123.8937 | -0.21057 | 123.6282 | 0.050354 | 0.28381 | 123.9807 | 124.0448 | 123.88 | 124.0631 | 123.7747 | 124.1409 | 123.88 | 123.6282 | 124.0631 | 123.7747 | 123.88 | 123.88 | 124.1409 | -0.59967 | -0.46234
1827.6562 | 124.2371 | -122.168 | 1.8723 | 0.11925 | 0.0041379 | -0.0013351 | 0.020089 | -0.0031019 | 0.00027774 | 0.0098522 | 1.5884 | 1.8082 | 1.3046 | 1.712 | 1.7303 | 1.767 | 1.6113 | 1.8951 | 1.886 | 1.4603 | 123.4726 | -0.064086 | 123.7564 | 123.88 | -0.14191 | 123.6282 | 0.013733 | 0.28381 | 123.7793 | 124.0631 | 123.8983 | 123.9761 | 123.7564 | 124.054 | 123.9349 | 123.6282 | 123.9761 | 123.7564 | 123.9349 | 123.8983 | 124.054 | -0.56763 | -0.41199
1828.6406 | 124.3149 | -122.1954 | 1.8265 | -0.12489 | 0.0049923 | -0.0038987 | 0.017526 | -0.0043835 | -0.0014313 | 0.0072888 | 1.6113 | 1.7807 | 1.3046 | 1.799 | 1.7899 | 1.8448 | 1.561 | 1.9958 | 1.8539 | 1.4511 | 123.5001 | -0.045776 | 123.8068 | 123.9944 | -0.036621 | 123.6465 | 0.027466 | 0.3067 | 123.7564 | 124.1913 | 123.9853 | 123.9761 | 123.8068 | 124.0494 | 124.0402 | 123.6465 | 123.9761 | 123.8068 | 124.0402 | 123.9853 | 124.0494 | -0.52185 | -0.37537
1829.6406 | 124.2966 | -122.1542 | 1.8814 | -0.2317 | 0.0020017 | -0.0049667 | 0.022012 | -0.0043835 | -0.00079046 | 0.007716 | 1.7075 | 1.7944 | 1.3321 | 1.8402 | 1.799 | 1.8356 | 1.6388 | 2.0096 | 1.9318 | 1.474 | 123.4863 | -0.086975 | 123.8617 | 123.9944 | -0.082398 | 123.6282 | 0.050354 | 0.37537 | 123.793 | 124.1638 | 123.9532 | 123.9487 | 123.8617 | 124.086 | 123.9899 | 123.6282 | 123.9487 | 123.8617 | 123.9899 | 123.9532 | 124.086 | -0.54932 | -0.40741
1830.6406 | 124.1776 | -122.1497 | 1.9455 | -0.22408 | 0.0073423 | -0.0034715 | 0.028207 | -0.0060925 | -0.0014313 | 0.0081432 | 1.6205 | 1.9135 | 1.3641 | 1.767 | 1.7532 | 1.7578 | 1.8219 | 1.9135 | 2.0096 | 1.4832 | 123.5138 | -0.032044 | 123.7701 | 123.9166 | -0.19226 | 123.6328 | 0.064087 | 0.25635 | 123.9716 | 124.0631 | 123.9029 | 124.0631 | 123.7701 | 124.1592 | 123.9075 | 123.6328 | 124.0631 | 123.7701 | 123.9075 | 123.9029 | 124.1592 | -0.58136 | -0.46234
1831.6406 | 124.292 | -122.1588 | 1.8951 | -0.26222 | 0.0041379 | -0.0062485 | 0.020089 | -0.0056653 | -0.0012177 | 0.008357 | 1.6708 | 1.8082 | 1.3321 | 1.8127 | 1.7853 | 1.8173 | 1.6251 | 1.9958 | 1.9226 | 1.4603 | 123.4909 | -0.086975 | 123.8297 | 123.9716 | -0.10986 | 123.6191 | 0.027465 | 0.33874 | 123.7839 | 124.1547 | 123.9441 | 123.967 | 123.8297 | 124.0814 | 123.9761 | 123.6191 | 123.967 | 123.8297 | 123.9761 | 123.9441 | 124.0814 | -0.56305 | -0.43488
1832.6562 | 124.2554 | -122.113 | 1.9363 | 0.14214 | 0.0088375 | -0.0019761 | 0.027352 | -0.0037427 | -0.0016449 | 0.0089978 | 1.68 | 1.9043 | 1.3596 | 1.7761 | 1.7303 | 1.7761 | 1.6022 | 1.9684 | 1.973 | 1.4694 | 123.4726 | -0.032043 | 123.793 | 123.8892 | -0.20599 | 123.5825 | 0.036621 | 0.32044 | 123.7152 | 124.0814 | 123.8434 | 124.0173 | 123.793 | 124.086 | 123.8892 | 123.5825 | 124.0173 | 123.793 | 123.8892 | 123.8434 | 124.086 | -0.57678 | -0.46692
1833.6406 | 124.2874 | -122.0901 | 1.9547 | -0.23933 | 0.0047787 | -0.0049667 | 0.019876 | -0.0048107 | -0.0012177 | 0.007716 | 1.6983 | 1.8814 | 1.3916 | 1.8311 | 1.8127 | 1.8356 | 1.6022 | 2.0599 | 1.9775 | 1.4969 | 123.4818 | -0.073242 | 123.7885 | 123.9212 | -0.14191 | 123.587 | 0.022888 | 0.3067 | 123.6923 | 124.1501 | 123.9029 | 123.9716 | 123.7885 | 124.0677 | 123.9258 | 123.587 | 123.9716 | 123.7885 | 123.9258 | 123.9029 | 124.0677 | -0.56305 | -0.45776
1834.6406 | 124.2462 | -122.0856 | 1.9592 | -0.22408 | 0.0058469 | -0.00069425 | 0.023507 | -0.0065197 | -0.0033539 | 0.0081432 | 1.6983 | 1.8951 | 1.387 | 1.8173 | 1.799 | 1.8127 | 1.68 | 2.0416 | 1.9775 | 1.4969 | 123.4726 | -0.064087 | 123.7839 | 123.9029 | -0.16022 | 123.5825 | 0.01831 | 0.31128 | 123.7656 | 124.1272 | 123.8846 | 123.9807 | 123.7839 | 124.0631 | 123.8983 | 123.5825 | 123.9807 | 123.7839 | 123.8983 | 123.8846 | 124.0631 | -0.57221 | -0.46234
1835.6406 | 124.1547 | -122.1405 | 1.9867 | -0.26222 | 0.0034971 | -0.0064621 | 0.024362 | -0.0065197 | 0.00070494 | 0.006648 | 1.8082 | 1.9547 | 1.3687 | 1.7487 | 1.7395 | 1.7303 | 1.767 | 1.9318 | 2.037 | 1.4786 | 123.5092 | -0.032043 | 123.9487 | 123.8892 | -0.24719 | 123.6191 | 0.050354 | 0.43945 | 123.9075 | 124.0723 | 123.88 | 124.0952 | 123.9487 | 124.1776 | 123.8708 | 123.6191 | 124.0952 | 123.9487 | 123.8708 | 123.88 | 124.1776 | -0.61798 | -0.50812
1836.6406 | 124.3057 | -122.0444 | 2.005 | -0.056229 | 0.0037107 | -0.0056077 | 0.02073 | -0.0041699 | 0.00091854 | 0.0085706 | 1.6983 | 1.9547 | 1.4236 | 1.8539 | 1.8677 | 1.8814 | 1.6708 | 2.0737 | 2.0416 | 1.5472 | 123.468 | -0.050354 | 123.7427 | 123.8983 | -0.13733 | 123.5916 | 0.036621 | 0.27466 | 123.7152 | 124.118 | 123.912 | 123.999 | 123.7427 | 124.086 | 123.9258 | 123.5916 | 123.999 | 123.7427 | 123.9258 | 123.912 | 124.086 | -0.58136 | -0.45776
1837.6562 | 124.1684 | -122.1313 | 1.9913 | 0.012436 | 0.0088375 | -0.00069425 | 0.032693 | -0.0037427 | -0.00036306 | 0.0072888 | 1.7075 | 1.9363 | 1.3779 | 1.767 | 1.7166 | 1.7349 | 1.7075 | 1.9226 | 2.0187 | 1.474 | 123.5092 | -0.054932 | 123.8388 | 123.8983 | -0.27466 | 123.6053 | 0.027466 | 0.32959 | 123.8388 | 124.054 | 123.848 | 124.0677 | 123.8388 | 124.1501 | 123.8663 | 123.6053 | 124.0677 | 123.8388 | 123.8663 | 123.848 | 124.1501 | -0.6134 | -0.51727
1838.6406 | 124.2142 | -122.0718 | 1.973 | -0.1783 | 0.0047787 | -0.0058213 | 0.020089 | -0.0052381 | 6.414e-05 | 0.0055798 | 1.7395 | 1.9089 | 1.4236 | 1.8677 | 1.8677 | 1.886 | 1.5884 | 2.1103 | 2.0004 | 1.5198 | 123.4955 | -0.064086 | 123.8113 | 123.9395 | -0.10529 | 123.5916 | 0.027466 | 0.31586 | 123.6603 | 124.1821 | 123.9395 | 123.9807 | 123.8113 | 124.0723 | 123.9578 | 123.5916 | 123.9807 | 123.8113 | 123.9578 | 123.9395 | 124.0723 | -0.54932 | -0.45319
1839.6406 | 124.2874 | -122.1176 | 1.9684 | -0.0028231 | 0.0047787 | -0.0030441 | 0.020303 | -0.0035291 | -0.00057686 | 0.0072888 | 1.6617 | 1.9089 | 1.4236 | 1.7899 | 1.8082 | 1.8265 | 1.6296 | 2.0416 | 1.9684 | 1.5106 | 123.5413 | -0.059509 | 123.7793 | 123.9075 | -0.16022 | 123.6282 | 0 | 0.23804 | 123.7473 | 124.1592 | 123.9258 | 124.0265 | 123.7793 | 124.086 | 123.9441 | 123.6282 | 124.0265 | 123.7793 | 123.9441 | 123.9258 | 124.086 | -0.54474 | -0.45776
1840.6406 | 124.2874 | -122.0444 | 2.005 | -0.094376 | 0.0045651 | -0.0043259 | 0.020944 | -0.0075879 | 0.0017731 | 0.0070752 | 1.7395 | 1.9272 | 1.4511 | 1.8585 | 1.8402 | 1.8814 | 1.6388 | 2.0737 | 2.0142 | 1.5427 | 123.4955 | -0.07782 | 123.7839 | 123.9029 | -0.1648 | 123.587 | 0.009155 | 0.28839 | 123.6832 | 124.118 | 123.8846 | 123.9716 | 123.7839 | 124.0585 | 123.9258 | 123.587 | 123.9716 | 123.7839 | 123.9258 | 123.8846 | 124.0585 | -0.55389 | -0.46234
1841.6406 | 124.292 | -122.0306 | 2.0279 | -0.04097 | 0.0032833 | -0.0019761 | 0.020944 | -0.0065197 | -0.00079046 | 0.0051526 | 1.7258 | 1.9501 | 1.442 | 1.8585 | 1.8539 | 1.886 | 1.6571 | 2.1057 | 2.0279 | 1.5518 | 123.4726 | -0.07782 | 123.7564 | 123.8892 | -0.17395 | 123.5825 | 0 | 0.28381 | 123.6877 | 124.1364 | 123.8846 | 123.9807 | 123.7564 | 124.0585 | 123.9166 | 123.5825 | 123.9807 | 123.7564 | 123.9166 | 123.8846 | 124.0585 | -0.58594 | -0.47607
1842.6562 | 124.2279 | -122.1405 | 1.9775 | 0.12688 | 0.0073423 | -0.0026169 | 0.028634 | -0.0054517 | -0.0022859 | 0.0087842 | 1.6159 | 1.9272 | 1.3504 | 1.7395 | 1.442 | 1.5106 | 2.0737 | 1.8173 | 2.0142 | 1.474 | 123.4909 | -0.050354 | 123.7564 | 123.88 | -0.53558 | 123.6145 | 0.036621 | 0.2655 | 124.2142 | 123.9578 | 123.5825 | 124.0677 | 123.7564 | 124.1547 | 123.6511 | 123.6145 | 124.0677 | 123.7564 | 123.6511 | 123.5825 | 124.1547 | -0.62714 | -0.50354
1843.6406 | 124.2462 | -122.1817 | 1.9089 | 0.073471 | 0.0045651 | -0.00048065 | 0.02073 | -0.0056653 | -0.0010041 | 0.0089978 | 1.6571 | 1.8951 | 1.3779 | 1.7624 | 1.7624 | 1.7761 | 1.6251 | 1.9775 | 1.9592 | 1.4786 | 123.5596 | -0.013733 | 123.8388 | 123.9441 | -0.14649 | 123.6603 | 0.050354 | 0.27923 | 123.8068 | 124.1592 | 123.9441 | 124.0768 | 123.8388 | 124.1409 | 123.9578 | 123.6603 | 124.0768 | 123.8388 | 123.9578 | 123.9441 | 124.1409 | -0.53101 | -0.4303
1844.6406 | 124.2966 | -122.1085 | 1.9363 | -0.025711 | 0.0039243 | -0.0043259 | 0.021585 | -0.0056653 | -0.00079046 | 0.008357 | 1.6754 | 1.8951 | 1.4053 | 1.8082 | 1.799 | 1.8173 | 1.5976 | 2.0508 | 1.973 | 1.4786 | 123.5138 | -0.041198 | 123.7839 | 123.9166 | -0.13733 | 123.587 | 0.036621 | 0.27008 | 123.7061 | 124.1592 | 123.9075 | 124.0036 | 123.7839 | 124.0814 | 123.9258 | 123.587 | 124.0036 | 123.7839 | 123.9258 | 123.9075 | 124.0814 | -0.53101 | -0.45776
1845.6406 | 124.3011 | -122.0764 | 1.973 | -0.20119 | 0.0037107 | -0.0064621 | 0.023934 | -0.0069471 | -0.00036306 | 0.0092114 | 1.7441 | 1.9043 | 1.4465 | 1.8311 | 1.8082 | 1.8311 | 1.6663 | 2.0554 | 1.9958 | 1.4969 | 123.5229 | -0.068664 | 123.8205 | 123.9075 | -0.16479 | 123.5733 | 0.022889 | 0.29755 | 123.7427 | 124.1318 | 123.8846 | 123.9807 | 123.8205 | 124.0723 | 123.9075 | 123.5733 | 123.9807 | 123.8205 | 123.9075 | 123.8846 | 124.0723 | -0.52643 | -0.47607
1846.6406 | 124.3011 | -122.113 | 1.9638 | -0.04097 | 0.0047787 | -0.0056077 | 0.019235 | -0.0071607 | -0.00014946 | 0.007716 | 1.6571 | 1.8951 | 1.3824 | 1.7807 | 1.7807 | 1.799 | 1.6342 | 2.0096 | 2.005 | 1.506 | 123.4955 | -0.068664 | 123.7701 | 123.8937 | -0.1831 | 123.6191 | 0.041199 | 0.27466 | 123.7473 | 124.1226 | 123.8937 | 124.0082 | 123.7701 | 124.118 | 123.912 | 123.6191 | 124.0082 | 123.7701 | 123.912 | 123.8937 | 124.118 | -0.58136 | -0.45776
1847.6406 | 124.3423 | -122.0215 | 1.9913 | -0.079117 | 0.0015743 | 0.00080115 | 0.021157 | -0.0078015 | 0.00027774 | 0.0081432 | 1.7349 | 1.9135 | 1.4465 | 1.8723 | 1.8631 | 1.8951 | 1.6113 | 2.1103 | 1.9958 | 1.5244 | 123.468 | -0.07782 | 123.7564 | 123.8937 | -0.12817 | 123.5458 | 0.004578 | 0.28839 | 123.6328 | 124.1318 | 123.8846 | 123.9349 | 123.7564 | 124.0173 | 123.9166 | 123.5458 | 123.9349 | 123.7564 | 123.9166 | 123.8846 | 124.0173 | -0.54474 | -0.46692
1848.6406 | 124.2966 | -122.0306 | 1.9867 | 0.14976 | 0.0034971 | 0.00058755 | 0.025216 | -0.0024609 | -0.0020721 | 0.0079296 | 1.9089 | 1.9089 | 1.593 | 1.8723 | 1.8265 | 1.8723 | 1.5884 | 2.0599 | 1.9821 | 1.5427 | 123.6237 | -0.077819 | 123.9395 | 123.9029 | -0.16022 | 123.5733 | -0.004577 | 0.31586 | 123.6191 | 124.0906 | 123.8571 | 123.9395 | 123.9395 | 124.0128 | 123.9029 | 123.5733 | 123.9395 | 123.9395 | 123.9029 | 123.8571 | 124.0128 | -0.39368 | -0.44403
1849.6406 | 124.2737 | -122.0215 | 2.0142 | 0.11162 | 0.0054197 | -0.0019761 | 0.021371 | -0.0069471 | -0.0014313 | 0.01028 | 1.7853 | 1.9684 | 1.4694 | 1.8494 | 1.8311 | 1.8768 | 1.6296 | 2.0691 | 2.0187 | 1.5518 | 123.4909 | -0.045776 | 123.8068 | 123.8708 | -0.1831 | 123.5733 | 0.004578 | 0.31586 | 123.6511 | 124.0906 | 123.8525 | 123.9899 | 123.8068 | 124.0402 | 123.8983 | 123.5733 | 123.9899 | 123.8068 | 123.8983 | 123.8525 | 124.0402 | -0.54474 | -0.46234
1850.6562 | 124.3011 | -122.0215 | 2.0142 | -0.13252 | 0.0028561 | -0.0026169 | 0.020089 | -0.0048107 | -0.00079046 | 0.0062206 | 1.7807 | 1.9455 | 1.4648 | 1.9043 | 1.886 | 1.8997 | 1.6663 | 2.1423 | 2.0462 | 1.5427 | 123.4863 | -0.068664 | 123.8022 | 123.9258 | -0.12817 | 123.5641 | 0.032044 | 0.31586 | 123.6877 | 124.1638 | 123.9075 | 123.967 | 123.8022 | 124.0677 | 123.9212 | 123.5641 | 123.967 | 123.8022 | 123.9212 | 123.9075 | 124.0677 | -0.54932 | -0.4715
1851.6406 | 124.3011 | -122.0261 | 2.0233 | -0.025711 | 0.0034971 | -0.0036851 | 0.022012 | -0.0065197 | -0.0012177 | 0.0068616 | 1.7166 | 1.9363 | 1.4236 | 1.8265 | 1.8082 | 1.8494 | 1.6571 | 2.0782 | 2.0462 | 1.5289 | 123.4497 | -0.086975 | 123.7427 | 123.8525 | -0.21515 | 123.555 | 0.022889 | 0.29297 | 123.6832 | 124.1043 | 123.8342 | 123.9624 | 123.7427 | 124.0723 | 123.8754 | 123.555 | 123.9624 | 123.7427 | 123.8754 | 123.8342 | 124.0723 | -0.59967 | -0.49438
1852.6406 | 124.2325 | -122.1359 | 1.9318 | 0.08873 | 0.0043515 | -0.0062485 | 0.022225 | -0.0075879 | 0.00049134 | 0.0089978 | 1.7075 | 1.9135 | 1.4328 | 1.7899 | 1.7853 | 1.8311 | 1.6617 | 2.0279 | 1.9867 | 1.4786 | 123.5687 | -0.018311 | 123.8434 | 123.9258 | -0.14648 | 123.6145 | 0.054931 | 0.27466 | 123.7976 | 124.1638 | 123.9212 | 124.0494 | 123.8434 | 124.1226 | 123.967 | 123.6145 | 124.0494 | 123.8434 | 123.967 | 123.9212 | 124.1226 | -0.49896 | -0.45319
1853.6406 | 124.2874 | -122.0306 | 2.0004 | 0.15739 | 0.0043515 | -0.0015489 | 0.02308 | -0.0033155 | -0.0010041 | 0.0070752 | 1.7532 | 1.8906 | 1.4374 | 1.8219 | 1.8127 | 1.8539 | 1.5747 | 2.0554 | 2.005 | 1.5198 | 123.468 | -0.10986 | 123.7839 | 123.8525 | -0.18768 | 123.5504 | 0.004578 | 0.31586 | 123.6053 | 124.086 | 123.8434 | 123.9212 | 123.7839 | 124.0356 | 123.8846 | 123.5504 | 123.9212 | 123.7839 | 123.8846 | 123.8434 | 124.0356 | -0.56305 | -0.48065
1854.6406 | 124.2645 | -122.0764 | 1.9684 | 0.14976 | 0.0052059 | -0.0015489 | 0.021585 | -0.0052381 | -0.0014313 | 0.006648 | 1.712 | 1.918 | 1.4282 | 1.8036 | 1.7899 | 1.8173 | 1.6251 | 2.005 | 2.0004 | 1.5335 | 123.5046 | -0.050354 | 123.7885 | 123.88 | -0.17853 | 123.6099 | 0.032043 | 0.28381 | 123.7015 | 124.0814 | 123.8663 | 123.9944 | 123.7885 | 124.0768 | 123.8937 | 123.6099 | 123.9944 | 123.7885 | 123.8937 | 123.8663 | 124.0768 | -0.54016 | -0.43488
1855.6406 | 124.2828 | -122.0215 | 2.0554 | -0.0028231 | 0.0039243 | -0.0064621 | 0.020089 | -0.0092969 | -0.00079046 | 0.0092114 | 1.7578 | 1.9821 | 1.4923 | 1.8906 | 1.9043 | 1.9318 | 1.7258 | 2.1286 | 2.0737 | 1.5976 | 123.5138 | -0.073242 | 123.7793 | 123.912 | -0.15106 | 123.6191 | 0.01831 | 0.2655 | 123.7473 | 124.1501 | 123.9258 | 124.0036 | 123.7793 | 124.0952 | 123.9532 | 123.6191 | 124.0036 | 123.7793 | 123.9532 | 123.9258 | 124.0952 | -0.56305 | -0.45776
1856.6406 | 124.3011 | -122.049 | 2.0142 | 0.073471 | 0.0075559 | 0.0027237 | 0.024148 | -0.0056653 | 6.414e-05 | 0.01028 | 1.7715 | 1.9272 | 1.4603 | 1.8951 | 1.886 | 1.8997 | 1.6113 | 2.0782 | 2.0187 | 1.5656 | 123.5092 | -0.086975 | 123.8205 | 123.9441 | -0.12817 | 123.6145 | 0.004578 | 0.31128 | 123.6603 | 124.1272 | 123.9349 | 123.9761 | 123.8205 | 124.0677 | 123.9487 | 123.6145 | 123.9761 | 123.8205 | 123.9487 | 123.9349 | 124.0677 | -0.55389 | -0.44861
1857.6406 | 124.2874 | -122.0444 | 2.0416 | 0.10399 | 0.0060605 | -0.0015489 | 0.022012 | -0.0054517 | -0.0010041 | 0.0072888 | 1.7807 | 1.9638 | 1.5289 | 1.8631 | 1.8448 | 1.8906 | 1.7075 | 2.0416 | 2.0508 | 1.5564 | 123.5733 | -0.07782 | 123.8251 | 123.9075 | -0.19684 | 123.6008 | 0.009155 | 0.25177 | 123.7518 | 124.086 | 123.8892 | 124.0082 | 123.8251 | 124.0952 | 123.9349 | 123.6008 | 124.0082 | 123.8251 | 123.9349 | 123.8892 | 124.0952 | -0.51269 | -0.48523
1858.6406 | 124.2599 | -122.0306 | 2.0554 | 0.14976 | 0.0041379 | -0.00069425 | 0.019662 | -0.0048107 | -0.00014946 | 0.01092 | 1.8356 | 1.9775 | 1.561 | 1.8951 | 1.8723 | 1.918 | 1.7212 | 2.0691 | 2.0599 | 1.6022 | 123.5916 | -0.07782 | 123.8663 | 123.9258 | -0.18311 | 123.6328 | 0.004578 | 0.27466 | 123.7518 | 124.0997 | 123.9029 | 124.0082 | 123.8663 | 124.0906 | 123.9487 | 123.6328 | 124.0082 | 123.8663 | 123.9487 | 123.9029 | 124.0906 | -0.49439 | -0.45319
1859.6406 | 124.2828 | -122.0581 | 2.0599 | 0.11162 | 0.0054197 | -0.00026705 | 0.021157 | -0.0071607 | -0.00079046 | 0.0092114 | 1.886 | 1.9821 | 1.5976 | 1.9135 | 1.886 | 1.9089 | 1.712 | 2.0645 | 2.0828 | 1.6159 | 123.6557 | -0.07782 | 123.9441 | 123.9716 | -0.17395 | 123.674 | 0.022888 | 0.28839 | 123.7701 | 124.1226 | 123.9441 | 124.0402 | 123.9441 | 124.1409 | 123.967 | 123.674 | 124.0402 | 123.9441 | 123.967 | 123.9441 | 124.1409 | -0.46234 | -0.44403
1860.6406 | 124.3195 | -122.1176 | 1.9272 | -0.086746 | 0.0030697 | -0.0038987 | 0.021371 | -0.0080151 | -0.0016449 | 0.0053662 | 1.7075 | 1.8723 | 1.4145 | 1.8494 | 1.8356 | 1.8585 | 1.561 | 2.037 | 1.9501 | 1.4877 | 123.5321 | -0.054932 | 123.8251 | 123.967 | -0.091553 | 123.6053 | 0.022888 | 0.29297 | 123.6786 | 124.1547 | 123.9532 | 123.9899 | 123.8251 | 124.0677 | 123.9761 | 123.6053 | 123.9899 | 123.8251 | 123.9761 | 123.9532 | 124.0677 | -0.51269 | -0.43945
1861.6406 | 124.2783 | -122.1222 | 1.9363 | 0.10399 | 0.0054197 | 0.0020827 | 0.022225 | -0.0058789 | 0.00091854 | 0.0087842 | 1.712 | 1.8997 | 1.3962 | 1.8082 | 1.7944 | 1.8311 | 1.593 | 1.9913 | 1.9684 | 1.5289 | 123.5184 | -0.036621 | 123.8342 | 123.9304 | -0.14191 | 123.6511 | 0.032044 | 0.31586 | 123.7152 | 124.1135 | 123.9166 | 124.0219 | 123.8342 | 124.0906 | 123.9532 | 123.6511 | 124.0219 | 123.8342 | 123.9532 | 123.9166 | 124.0906 | -0.54016 | -0.40741
1862.6406 | 124.2966 | -122.081 | 1.9592 | -0.04097 | 0.0047787 | -0.0017625 | 0.020944 | -0.0056653 | 6.414e-05 | 0.006648 | 1.6891 | 1.9226 | 1.4191 | 1.8173 | 1.8082 | 1.8402 | 1.6205 | 2.0233 | 1.973 | 1.5335 | 123.5001 | -0.036622 | 123.7701 | 123.8983 | -0.15106 | 123.6145 | 0.013732 | 0.27008 | 123.7015 | 124.1043 | 123.8892 | 124.0036 | 123.7701 | 124.054 | 123.9212 | 123.6145 | 124.0036 | 123.7701 | 123.9212 | 123.8892 | 124.054 | -0.54016 | -0.42572
1863.6406 | 124.2874 | -122.081 | 1.9684 | 0.11162 | 0.0043515 | -0.0024033 | 0.024148 | -0.0041699 | -0.00057686 | 0.0070752 | 1.7715 | 1.8951 | 1.4557 | 1.8631 | 1.8494 | 1.8814 | 1.5976 | 2.0554 | 2.005 | 1.5564 | 123.5367 | -0.073242 | 123.8525 | 123.9441 | -0.11902 | 123.6374 | 0.036621 | 0.31586 | 123.6786 | 124.1364 | 123.9304 | 123.9761 | 123.8525 | 124.086 | 123.9624 | 123.6374 | 123.9761 | 123.8525 | 123.9624 | 123.9304 | 124.086 | -0.5127 | -0.41199
1864.6406 | 124.3332 | -122.0352 | 1.9958 | 0.058212 | 0.0060605 | -0.00069425 | 0.024575 | -0.0033155 | -0.0016449 | 0.0085706 | 1.8539 | 1.9043 | 1.506 | 1.9135 | 1.8814 | 1.9135 | 1.593 | 2.0828 | 2.0142 | 1.5656 | 123.5413 | -0.091553 | 123.8892 | 123.9487 | -0.11444 | 123.6008 | 0.01831 | 0.3479 | 123.6282 | 124.118 | 123.9166 | 123.9395 | 123.8892 | 124.0494 | 123.9487 | 123.6008 | 123.9395 | 123.8892 | 123.9487 | 123.9166 | 124.0494 | -0.48981 | -0.4303
1865.6562 | 124.3286 | -122.0535 | 2.0004 | -0.29274 | 0.0058469 | -0.0056077 | 0.021371 | -0.0054517 | 0.00049134 | 0.0072888 | 1.8265 | 1.9272 | 1.5381 | 1.9226 | 1.8997 | 1.918 | 1.6617 | 2.1149 | 2.0142 | 1.5793 | 123.5916 | -0.073242 | 123.88 | 123.9761 | -0.10071 | 123.6328 | 0.013733 | 0.28839 | 123.7152 | 124.1684 | 123.9532 | 123.9807 | 123.88 | 124.0677 | 123.9716 | 123.6328 | 123.9807 | 123.88 | 123.9716 | 123.9532 | 124.0677 | -0.46234 | -0.42114
1866.6406 | 124.2783 | -122.0673 | 2.0325 | 0.10399 | 0.0022153 | -5.3452e-05 | 0.022225 | -0.0078015 | -0.0020721 | 0.0070752 | 1.8036 | 1.9455 | 1.5244 | 1.8631 | 1.8539 | 1.8814 | 1.6754 | 2.037 | 2.0233 | 1.5793 | 123.5916 | -0.086975 | 123.8709 | 123.9304 | -0.17853 | 123.6465 | -0.009156 | 0.27924 | 123.7427 | 124.1043 | 123.9212 | 124.0128 | 123.8709 | 124.0906 | 123.9487 | 123.6465 | 124.0128 | 123.8709 | 123.9487 | 123.9212 | 124.0906 | -0.50812 | -0.45319
1867.6406 | 124.3103 | -122.0352 | 2.0416 | -0.04097 | 0.0041379 | -0.0053941 | 0.022866 | -0.0050245 | 0.00070494 | 0.007716 | 1.8173 | 1.9638 | 1.5564 | 1.9089 | 1.8997 | 1.9272 | 1.7029 | 2.1194 | 2.0599 | 1.593 | 123.5916 | -0.07782 | 123.8525 | 123.9441 | -0.14191 | 123.6282 | 0.018311 | 0.26093 | 123.7381 | 124.1547 | 123.9349 | 123.999 | 123.8525 | 124.0952 | 123.9624 | 123.6282 | 123.999 | 123.8525 | 123.9624 | 123.9349 | 124.0952 | -0.48523 | -0.44861
1868.6406 | 124.2783 | -121.9894 | 2.0554 | 0.035324 | 0.0047787 | -0.00048065 | 0.02073 | -0.0054517 | 6.414e-05 | 0.0081432 | 1.886 | 2.005 | 1.6205 | 1.918 | 1.9135 | 1.9409 | 1.712 | 2.0782 | 2.0737 | 1.6342 | 123.6099 | -0.050354 | 123.8754 | 123.9075 | -0.14191 | 123.6237 | 0.01831 | 0.2655 | 123.7015 | 124.0677 | 123.9029 | 123.9944 | 123.8754 | 124.0631 | 123.9304 | 123.6237 | 123.9944 | 123.8754 | 123.9304 | 123.9029 | 124.0631 | -0.43488 | -0.42114
1869.6406 | 124.3378 | -122.0444 | 1.9958 | 0.17265 | 0.0073423 | -0.0026169 | 0.026498 | -0.0043835 | -0.0016449 | 0.0068616 | 1.9272 | 1.973 | 1.5976 | 2.0096 | 1.6983 | 1.767 | 1.8127 | 2.211 | 2.0142 | 1.5839 | 123.642 | -0.022889 | 123.9716 | 124.054 | -0.29755 | 123.6282 | 0.01831 | 0.32959 | 123.8571 | 124.2554 | 123.7427 | 124.0173 | 123.9716 | 124.0585 | 123.8113 | 123.6282 | 124.0173 | 123.9716 | 123.8113 | 123.7427 | 124.0585 | -0.39825 | -0.41199
1870.6406 | 124.3378 | -122.0032 | 2.0691 | -0.11726 | 0.0034971 | -0.0053941 | 0.01838 | -0.0060925 | -0.0010041 | 0.0085706 | 1.9043 | 2.0187 | 1.6022 | 1.9867 | 1.9821 | 2.0096 | 1.712 | 2.179 | 2.0966 | 1.6525 | 123.6053 | -0.050354 | 123.9075 | 123.9899 | -0.086975 | 123.6557 | 0.027466 | 0.30212 | 123.7152 | 124.1821 | 123.9853 | 124.0219 | 123.9075 | 124.0997 | 124.0128 | 123.6557 | 124.0219 | 123.9075 | 124.0128 | 123.9853 | 124.0997 | -0.46692 | -0.41656
1871.6406 | 124.2691 | -121.9986 | 2.0279 | 0.08873 | 0.0034971 | 0.00037395 | 0.020516 | -0.0065197 | 6.414e-05 | 0.006648 | 1.8539 | 2.0554 | 1.5839 | 1.9547 | 1.7624 | 1.8631 | 1.5381 | 1.9592 | 2.0645 | 1.6388 | 123.5825 | 0.027466 | 123.8525 | 123.9532 | -0.2655 | 123.6374 | 0.036621 | 0.27008 | 123.5367 | 123.9578 | 123.761 | 124.054 | 123.8525 | 124.0631 | 123.8617 | 123.6374 | 124.054 | 123.8525 | 123.8617 | 123.761 | 124.0631 | -0.44403 | -0.3891
1872.6406 | 124.2737 | -121.9666 | 2.1332 | 0.042953 | 0.0039243 | -0.0060349 | 0.019662 | -0.0075879 | -0.00014946 | 0.0092114 | 1.9684 | 2.1011 | 1.7166 | 2.005 | 1.9958 | 2.0233 | 1.8265 | 2.1835 | 2.1652 | 1.7258 | 123.6832 | -0.032044 | 123.9349 | 123.9716 | -0.13733 | 123.6923 | 0.032043 | 0.25177 | 123.793 | 124.1501 | 123.9624 | 124.0677 | 123.9349 | 124.1318 | 123.9899 | 123.6923 | 124.0677 | 123.9349 | 123.9899 | 123.9624 | 124.1318 | -0.41657 | -0.40741
1873.6406 | 124.3149 | -121.9299 | 2.1057 | 0.10399 | 0.0047787 | -0.00069425 | 0.021371 | -0.0052381 | -0.0027131 | 0.010066 | 1.9135 | 2.0691 | 1.6067 | 2.0142 | 1.973 | 2.0142 | 1.7441 | 2.1881 | 2.1103 | 1.6754 | 123.5367 | -0.036621 | 123.8434 | 123.9441 | -0.13275 | 123.6053 | 0.004578 | 0.3067 | 123.674 | 124.118 | 123.9029 | 123.999 | 123.8434 | 124.0402 | 123.9441 | 123.6053 | 123.999 | 123.8434 | 123.9441 | 123.9029 | 124.0402 | -0.49896 | -0.4303
1874.6406 | 124.3103 | -121.9299 | 2.1332 | 0.10399 | 0.0062741 | -0.0019761 | 0.022439 | -0.0090833 | -0.0014313 | 0.0075024 | 1.918 | 2.0737 | 1.6205 | 2.0233 | 2.0096 | 2.0462 | 1.7029 | 2.2064 | 2.1378 | 1.7075 | 123.5504 | -0.05951 | 123.848 | 123.9532 | -0.1236 | 123.6374 | 0.004577 | 0.29755 | 123.6328 | 124.1364 | 123.9395 | 124.0036 | 123.848 | 124.0677 | 123.9761 | 123.6374 | 124.0036 | 123.848 | 123.9761 | 123.9395 | 124.0677 | -0.5127 | -0.42572
1875.6562 | 124.2279 | -121.9803 | 2.1561 | -0.17067 | 0.0054197 | -0.0013351 | 0.025857 | -0.0065197 | -0.00057686 | 0.0064344 | 1.8539 | 2.1103 | 1.5839 | 1.9501 | 1.9272 | 1.9272 | 1.9318 | 2.1194 | 2.179 | 1.6663 | 123.5641 | -0.045776 | 123.8342 | 123.9304 | -0.22888 | 123.6465 | 0.022888 | 0.27008 | 123.912 | 124.0997 | 123.9075 | 124.0906 | 123.8342 | 124.1592 | 123.9075 | 123.6465 | 124.0906 | 123.8342 | 123.9075 | 123.9075 | 124.1592 | -0.57221 | -0.48981
1876.6406 | 124.3423 | -121.9299 | 2.1194 | 0.11925 | 0.0062741 | 0.0014419 | 0.025216 | -0.0058789 | -0.0010041 | 0.0087842 | 1.9363 | 2.0737 | 1.6067 | 2.0416 | 2.0325 | 2.0599 | 1.7258 | 2.211 | 2.1423 | 1.7212 | 123.5367 | -0.045777 | 123.8663 | 123.9716 | -0.086975 | 123.6511 | 0.022888 | 0.32959 | 123.6557 | 124.1409 | 123.9624 | 124.0036 | 123.8663 | 124.0723 | 123.9899 | 123.6511 | 124.0036 | 123.8663 | 123.9899 | 123.9624 | 124.0723 | -0.5127 | -0.39826
1877.6406 | 124.3011 | -121.9437 | 2.1194 | 0.11162 | 0.0084103 | -0.0015489 | 0.02308 | -0.0058789 | -0.00036306 | 0.0072888 | 1.8997 | 2.0508 | 1.593 | 2.0096 | 1.9958 | 2.0416 | 1.7212 | 2.1927 | 2.1423 | 1.7029 | 123.5367 | -0.068665 | 123.8434 | 123.9532 | -0.1236 | 123.6465 | 0.022888 | 0.3067 | 123.6649 | 124.1364 | 123.9395 | 123.9944 | 123.8434 | 124.086 | 123.9853 | 123.6465 | 123.9944 | 123.8434 | 123.9853 | 123.9395 | 124.086 | -0.52643 | -0.41656
1878.6406 | 124.2966 | -121.9299 | 2.1332 | 0.18028 | 0.0058469 | -0.0026169 | 0.022439 | -0.0052381 | -0.00079046 | 0.0081432 | 1.9043 | 2.0508 | 1.6205 | 2.0142 | 2.0233 | 2.0416 | 1.7349 | 2.1927 | 2.1515 | 1.7075 | 123.5504 | -0.082398 | 123.8342 | 123.9441 | -0.10986 | 123.6374 | 0.01831 | 0.28381 | 123.6649 | 124.1226 | 123.9532 | 123.9807 | 123.8342 | 124.0814 | 123.9716 | 123.6374 | 123.9807 | 123.8342 | 123.9716 | 123.9532 | 124.0814 | -0.5127 | -0.42572
1879.6406 | 124.292 | -121.9482 | 2.1378 | 0.11925 | 0.0058469 | -0.0013351 | 0.02308 | -0.0045971 | 0.0017731 | 0.0098522 | 1.8631 | 2.0691 | 1.6113 | 1.9775 | 1.9958 | 2.0142 | 1.7761 | 2.1744 | 2.1469 | 1.712 | 123.5596 | -0.068664 | 123.8113 | 123.9258 | -0.14191 | 123.6603 | 0.009156 | 0.25177 | 123.7244 | 124.1226 | 123.9441 | 124.0173 | 123.8113 | 124.0952 | 123.9624 | 123.6603 | 124.0173 | 123.8113 | 123.9624 | 123.9441 | 124.0952 | -0.52643 | -0.42572
1880.6406 | 124.324 | -121.9894 | 2.0828 | 0.17265 | 0.0054197 | -0.00026705 | 0.025643 | -0.0043835 | -0.0018585 | 0.007716 | 1.886 | 2.0325 | 1.5884 | 2.0187 | 1.9958 | 2.037 | 1.6937 | 2.1881 | 2.124 | 1.6891 | 123.5779 | -0.050354 | 123.8754 | 124.0082 | -0.086975 | 123.6786 | 0.041198 | 0.29755 | 123.6832 | 124.1776 | 123.9853 | 124.0219 | 123.8754 | 124.1135 | 124.0265 | 123.6786 | 124.0219 | 123.8754 | 124.0265 | 123.9853 | 124.1135 | -0.49439 | -0.39368
1881.6406 | 124.2828 | -121.962 | 2.1057 | 0.18028 | 0.0039243 | -0.0064621 | 0.022439 | -0.0048107 | -0.0012177 | 0.007716 | 1.8768 | 2.037 | 1.6022 | 1.9958 | 1.9958 | 2.0187 | 1.7395 | 2.1561 | 2.1103 | 1.6846 | 123.5641 | -0.068665 | 123.8388 | 123.9578 | -0.10986 | 123.6465 | 0.004578 | 0.27466 | 123.7015 | 124.118 | 123.9578 | 123.999 | 123.8388 | 124.0723 | 123.9807 | 123.6465 | 123.999 | 123.8388 | 123.9807 | 123.9578 | 124.0723 | -0.50354 | -0.42114
1882.6406 | 124.292 | -121.9666 | 2.1378 | 0.18028 | 0.0037107 | -0.0041123 | 0.021371 | -0.0071607 | -0.0010041 | 0.0075024 | 1.8631 | 2.0599 | 1.6251 | 2.0004 | 2.0004 | 2.0279 | 1.8036 | 2.1744 | 2.1469 | 1.7075 | 123.5916 | -0.077819 | 123.8297 | 123.967 | -0.13733 | 123.674 | 0.009156 | 0.23804 | 123.7701 | 124.1409 | 123.967 | 124.0265 | 123.8297 | 124.1135 | 123.9944 | 123.674 | 124.0265 | 123.8297 | 123.9944 | 123.967 | 124.1135 | -0.51269 | -0.4303
1883.6406 | 124.3332 | -121.9345 | 2.1103 | 1.3552 | 0.0090513 | -0.0017625 | 0.026925 | -0.0063061 | -0.0018585 | 0.006648 | 1.7944 | 2.0279 | 1.593 | 2.0279 | 2.0187 | 2.0737 | 1.6937 | 2.1881 | 2.124 | 1.7029 | 123.5275 | -0.082398 | 123.7289 | 123.9624 | -0.091553 | 123.6374 | 0.013732 | 0.20142 | 123.6282 | 124.1226 | 123.9532 | 123.9624 | 123.7289 | 124.0585 | 124.0082 | 123.6374 | 123.9624 | 123.7289 | 124.0082 | 123.9532 | 124.0585 | -0.51727 | -0.40741
1884.6406 | 124.3057 | -122.1176 | 1.9958 | 0.17265 | 0.0058469 | -0.00069425 | 0.02543 | -0.0037427 | -0.00014946 | 0.0085706 | 1.7761 | 1.9684 | 1.4923 | 1.8631 | 1.8311 | 1.8814 | 1.6388 | 2.0096 | 2.0233 | 1.5701 | 123.6099 | -0.027466 | 123.8937 | 123.9807 | -0.16479 | 123.6877 | 0.027465 | 0.28381 | 123.7564 | 124.1272 | 123.9487 | 124.086 | 123.8937 | 124.1409 | 123.999 | 123.6877 | 124.086 | 123.8937 | 123.999 | 123.9487 | 124.1409 | -0.50354 | -0.42572
1885.6562 | 124.3149 | -122.1039 | 2.0096 | -0.20119 | 0.0049923 | -0.0021897 | 0.021585 | -0.0052381 | 0.0024139 | 0.0062206 | 1.7578 | 1.9043 | 1.4511 | 1.8723 | 1.8906 | 1.8814 | 1.6937 | 2.0737 | 2.0096 | 1.5427 | 123.555 | -0.10529 | 123.8617 | 123.9761 | -0.11902 | 123.6465 | 0 | 0.3067 | 123.7976 | 124.1776 | 123.9944 | 124.0082 | 123.8617 | 124.1135 | 123.9853 | 123.6465 | 124.0082 | 123.8617 | 123.9853 | 123.9944 | 124.1135 | -0.55847 | -0.46692
1886.6406 | 124.3332 | -122.1085 | 1.9547 | 0.17265 | 0.0052059 | -0.0034715 | 0.022866 | -0.0045971 | 6.414e-05 | 0.0092114 | 1.7624 | 1.8997 | 1.474 | 1.8677 | 1.8585 | 1.9089 | 1.5793 | 2.0508 | 1.9684 | 1.5472 | 123.5825 | -0.054932 | 123.8708 | 123.9761 | -0.09613 | 123.6557 | 0.013733 | 0.28839 | 123.6877 | 124.1592 | 123.967 | 124.0082 | 123.8708 | 124.0768 | 124.0173 | 123.6557 | 124.0082 | 123.8708 | 124.0173 | 123.967 | 124.0768 | -0.48065 | -0.40741
1887.6406 | 124.2966 | -122.1085 | 1.9821 | 0.065841 | 0.0064877 | -0.0019761 | 0.024148 | -0.0063061 | -0.00057686 | 0.006648 | 1.767 | 1.9135 | 1.474 | 1.8402 | 1.8265 | 1.8723 | 1.6342 | 2.005 | 1.9913 | 1.5656 | 123.5825 | -0.068665 | 123.8754 | 123.9487 | -0.15564 | 123.674 | 0.009155 | 0.29297 | 123.7427 | 124.1135 | 123.9349 | 124.0219 | 123.8754 | 124.0997 | 123.9807 | 123.674 | 124.0219 | 123.8754 | 123.9807 | 123.9349 | 124.0997 | -0.50812 | -0.41656
1888.6406 | 124.3332 | -122.0993 | 1.9592 | 0.11162 | 0.0052059 | -0.0038987 | 0.024789 | -0.0037427 | 6.414e-05 | 0.0087842 | 1.7715 | 1.8906 | 1.4832 | 1.8768 | 1.8494 | 1.8997 | 1.5839 | 2.0416 | 1.9638 | 1.5472 | 123.5825 | -0.068665 | 123.8708 | 123.9761 | -0.10986 | 123.6465 | 0.004577 | 0.28839 | 123.6832 | 124.1409 | 123.9487 | 123.9899 | 123.8708 | 124.0631 | 123.999 | 123.6465 | 123.9899 | 123.8708 | 123.999 | 123.9487 | 124.0631 | -0.47608 | -0.41199
1889.6406 | 124.3378 | -122.1085 | 1.9821 | 0.14214 | 0.0052059 | -0.0021897 | 0.024575 | -0.0039563 | -0.00036306 | 0.006648 | 1.8036 | 1.9135 | 1.506 | 1.8906 | 1.8723 | 1.9363 | 1.6067 | 2.0691 | 1.9867 | 1.5839 | 123.6145 | -0.068665 | 123.912 | 123.999 | -0.10986 | 123.6923 | 0.004577 | 0.29755 | 123.7152 | 124.1776 | 123.9807 | 124.0219 | 123.912 | 124.0952 | 124.0448 | 123.6923 | 124.0219 | 123.912 | 124.0448 | 123.9807 | 124.0952 | -0.47607 | -0.39825
1890.6406 | 124.3652 | -122.049 | 2.0187 | -0.094376 | 0.0041379 | -0.0028305 | 0.022653 | -0.0063061 | -0.0029267 | 0.007716 | 1.7853 | 1.9501 | 1.5198 | 1.918 | 1.9043 | 1.9455 | 1.6525 | 2.1423 | 2.0279 | 1.6022 | 123.5687 | -0.068665 | 123.8342 | 123.967 | -0.11444 | 123.6511 | 0.009155 | 0.2655 | 123.7015 | 124.1913 | 123.9532 | 123.999 | 123.8342 | 124.0768 | 123.9944 | 123.6511 | 123.999 | 123.8342 | 123.9944 | 123.9532 | 124.0768 | -0.49896 | -0.41656
1891.6406 | 124.3469 | -122.0764 | 2.0004 | 0.19554 | 0.0043515 | -0.0041123 | 0.023721 | -0.0065197 | -0.00014946 | 0.0085706 | 1.8082 | 1.9455 | 1.506 | 1.8814 | 1.8677 | 1.9089 | 1.6022 | 2.0737 | 2.0187 | 1.5564 | 123.5825 | -0.054931 | 123.8846 | 123.9578 | -0.13275 | 123.6328 | 0.018311 | 0.30212 | 123.6786 | 124.1501 | 123.9441 | 124.0219 | 123.8846 | 124.0952 | 123.9853 | 123.6328 | 124.0219 | 123.8846 | 123.9853 | 123.9441 | 124.0952 | -0.49439 | -0.44403
1892.6406 | 124.324 | -122.0993 | 2.0096 | -0.033341 | 0.0049923 | -0.0047531 | 0.021157 | -0.0052381 | 0.00027774 | 0.0087842 | 1.799 | 1.9363 | 1.5518 | 1.8631 | 1.8585 | 1.8906 | 1.6846 | 2.0691 | 2.0233 | 1.5518 | 123.6511 | -0.073243 | 123.8983 | 123.9624 | -0.15106 | 123.6511 | 0.013732 | 0.24719 | 123.7839 | 124.1684 | 123.9578 | 124.0356 | 123.8983 | 124.1226 | 123.9899 | 123.6511 | 124.0356 | 123.8983 | 123.9899 | 123.9578 | 124.1226 | -0.45776 | -0.45776
1893.6406 | 124.3057 | -122.113 | 2.0187 | 0.14976 | 0.0058469 | -0.0034715 | 0.023934 | -0.0071607 | -0.00014946 | 0.0072888 | 1.7807 | 1.9318 | 1.5152 | 1.8631 | 1.8402 | 1.8814 | 1.6663 | 2.037 | 2.0233 | 1.5656 | 123.6282 | -0.086975 | 123.8937 | 123.9761 | -0.17853 | 123.6786 | 0.004577 | 0.2655 | 123.7793 | 124.1501 | 123.9532 | 124.0448 | 123.8937 | 124.1364 | 123.9944 | 123.6786 | 124.0448 | 123.8937 | 123.9944 | 123.9532 | 124.1364 | -0.50354 | -0.45319
1894.6406 | 124.2874 | -122.1085 | 2.0096 | 0.18791 | 0.0056333 | -0.0058213 | 0.020303 | -0.0095105 | 0.00070494 | 0.0075024 | 1.7899 | 1.9501 | 1.5335 | 1.9043 | 1.8723 | 1.9089 | 1.68 | 2.0554 | 2.0416 | 1.5884 | 123.642 | -0.05951 | 123.8983 | 124.0128 | -0.13733 | 123.6969 | 0.032043 | 0.25635 | 123.7885 | 124.1638 | 123.9807 | 124.0585 | 123.8983 | 124.1501 | 124.0173 | 123.6969 | 124.0585 | 123.8983 | 124.0173 | 123.9807 | 124.1501 | -0.47608 | -0.42114
1895.6406 | 124.3835 | -122.0306 | 2.0645 | -0.10963 | 0.0054197 | -0.0019761 | 0.021585 | -0.0065197 | 0.00091854 | 0.0092114 | 1.8768 | 2.005 | 1.5793 | 1.9821 | 1.9409 | 1.9775 | 1.6891 | 2.1835 | 2.0599 | 1.6342 | 123.6099 | -0.059509 | 123.9075 | 124.0128 | -0.1236 | 123.6649 | -0.004577 | 0.29755 | 123.7198 | 124.2142 | 123.9716 | 124.0356 | 123.9075 | 124.0906 | 124.0082 | 123.6649 | 124.0356 | 123.9075 | 124.0082 | 123.9716 | 124.0906 | -0.48523 | -0.4303
1896.6406 | 124.3286 | -122.049 | 2.0508 | -0.063858 | 0.0039243 | -0.0094529 | 0.021371 | -0.0069471 | -0.00014946 | 0.0092114 | 1.7899 | 1.9409 | 1.5381 | 1.886 | 1.8951 | 1.9135 | 1.6937 | 2.1057 | 2.0554 | 1.5884 | 123.587 | -0.10986 | 123.8388 | 123.9349 | -0.15564 | 123.6374 | 0.004578 | 0.25177 | 123.7427 | 124.1547 | 123.9441 | 123.9899 | 123.8388 | 124.1043 | 123.9624 | 123.6374 | 123.9899 | 123.8388 | 123.9624 | 123.9441 | 124.1043 | -0.5127 | -0.46234
1897.6406 | 124.3195 | -122.0947 | 2.0325 | 0.35576 | 0.0045651 | -0.0036851 | 0.021798 | -0.0075879 | -0.00036306 | 0.007716 | 1.7441 | 1.9135 | 1.474 | 1.8631 | 1.8539 | 1.8768 | 1.7212 | 2.0554 | 2.037 | 1.5701 | 123.5687 | -0.11902 | 123.8388 | 123.9578 | -0.17853 | 123.6649 | 0.004577 | 0.27008 | 123.8159 | 124.1501 | 123.9487 | 124.0082 | 123.8388 | 124.1318 | 123.9716 | 123.6649 | 124.0082 | 123.8388 | 123.9716 | 123.9487 | 124.1318 | -0.55847 | -0.46234
1898.6406 | 124.3652 | -122.0901 | 2.0096 | 0.0811 | 0.0017881 | -0.0034715 | 0.024789 | -0.0058789 | -0.0010041 | 0.009425 | 1.8082 | 1.9409 | 1.5244 | 1.8906 | 1.8677 | 1.9089 | 1.6342 | 2.0737 | 2.0142 | 1.5839 | 123.6145 | -0.068665 | 123.8983 | 123.9807 | -0.14191 | 123.674 | 0.004577 | 0.28381 | 123.7244 | 124.1638 | 123.9578 | 124.0311 | 123.8983 | 124.1043 | 123.999 | 123.674 | 124.0311 | 123.8983 | 123.999 | 123.9578 | 124.1043 | -0.48523 | -0.42572
1899.6562 | 124.2371 | -122.113 | 2.0233 | -0.079117 | 0.0075559 | -0.0045395 | 0.028848 | -0.0045971 | -0.0010041 | 0.0062206 | 1.8036 | 1.9867 | 1.4832 | 1.8356 | 1.7899 | 1.8173 | 1.7578 | 1.9913 | 2.0645 | 1.5289 | 123.5962 | -0.036621 | 123.9166 | 123.9487 | -0.23346 | 123.642 | 0.041199 | 0.32044 | 123.8708 | 124.1043 | 123.9029 | 124.0997 | 123.9166 | 124.1776 | 123.9304 | 123.642 | 124.0997 | 123.9166 | 123.9304 | 123.9029 | 124.1776 | -0.54016 | -0.49438
1900.6562 | 124.2416 | -122.1085 | 2.0599 | -0.21645 | 0.0077695 | -0.0045395 | 0.026284 | -0.0020337 | -0.0020721 | 0.0068616 | 1.7395 | 2.0279 | 1.506 | 1.8219 | 1.8219 | 1.8036 | 1.8494 | 2.0187 | 2.0874 | 1.5427 | 123.6145 | -0.032044 | 123.848 | 123.9304 | -0.23804 | 123.6511 | 0.027465 | 0.23346 | 123.9578 | 124.1272 | 123.9304 | 124.1364 | 123.848 | 124.1959 | 123.912 | 123.6511 | 124.1364 | 123.848 | 123.912 | 123.9304 | 124.1959 | -0.5539 | -0.51727
1901.6406 | 124.3332 | -122.0764 | 2.0233 | -0.018082 | 0.0045651 | 0.00080115 | 0.019876 | -0.0058789 | -0.00057686 | 0.0092114 | 1.7441 | 1.9318 | 1.4832 | 1.8402 | 1.8448 | 1.8631 | 1.6891 | 2.037 | 2.0554 | 1.561 | 123.5596 | -0.091552 | 123.8205 | 123.9166 | -0.17853 | 123.6374 | 0.032044 | 0.26093 | 123.7656 | 124.1135 | 123.9212 | 124.0082 | 123.8205 | 124.1318 | 123.9395 | 123.6374 | 124.0082 | 123.8205 | 123.9395 | 123.9212 | 124.1318 | -0.54016 | -0.46234
1902.6406 | 124.2874 | -122.1268 | 2.037 | -0.28511 | 0.0041379 | -0.0011215 | 0.025002 | -0.0071607 | -0.0020721 | 0.0057934 | 1.7944 | 1.9455 | 1.5198 | 1.8356 | 1.8402 | 1.8402 | 1.7899 | 2.0508 | 2.0325 | 1.5701 | 123.6465 | -0.091552 | 123.9212 | 123.9624 | -0.19684 | 123.6969 | -0.004577 | 0.27466 | 123.9166 | 124.1776 | 123.967 | 124.0723 | 123.9212 | 124.1592 | 123.967 | 123.6969 | 124.0723 | 123.9212 | 123.967 | 123.967 | 124.1592 | -0.51727 | -0.46692
1903.6406 | 124.3744 | -122.0901 | 1.9913 | -0.056229 | 0.0024289 | -0.0071029 | 0.020303 | -0.0060925 | -0.00079046 | 0.0092114 | 1.7578 | 1.9135 | 1.5152 | 1.886 | 1.8768 | 1.9135 | 1.6708 | 2.0782 | 1.9958 | 1.5701 | 123.6053 | -0.07782 | 123.848 | 123.9761 | -0.11444 | 123.6603 | 0.004578 | 0.24261 | 123.761 | 124.1684 | 123.967 | 124.0036 | 123.848 | 124.086 | 124.0036 | 123.6603 | 124.0036 | 123.848 | 124.0036 | 123.967 | 124.086 | -0.47607 | -0.42114
1904.6406 | 124.3607 | -122.081 | 2.0187 | -0.063858 | 0.0037107 | -0.0032577 | 0.017953 | -0.0082287 | -0.0018585 | 0.0068616 | 1.7853 | 1.9592 | 1.5152 | 1.9318 | 1.9409 | 1.9547 | 1.6891 | 2.1103 | 2.0416 | 1.6113 | 123.5962 | -0.059509 | 123.8663 | 124.0128 | -0.07782 | 123.6923 | 0.022888 | 0.27008 | 123.7701 | 124.1913 | 124.0219 | 124.0402 | 123.8663 | 124.1226 | 124.0356 | 123.6923 | 124.0402 | 123.8663 | 124.0356 | 124.0219 | 124.1226 | -0.50354 | -0.40741
1905.6562 | 124.2462 | -122.1405 | 2.0142 | -0.20882 | 0.0099057 | -0.0041123 | 0.028634 | -0.0054517 | 0.0013457 | 0.0051526 | 1.7487 | 1.973 | 1.4557 | 1.8219 | 1.7944 | 1.8127 | 1.8082 | 1.9821 | 2.0508 | 1.5472 | 123.5962 | -0.041199 | 123.8892 | 123.9624 | -0.21973 | 123.6877 | 0.036621 | 0.29297 | 123.9487 | 124.1226 | 123.9349 | 124.1135 | 123.8892 | 124.1913 | 123.9532 | 123.6877 | 124.1135 | 123.8892 | 123.9532 | 123.9349 | 124.1913 | -0.55847 | -0.46692
1906.6406 | 124.4476 | -122.0993 | 2.005 | -0.14778 | 0.0056333 | -0.00069425 | 0.022012 | -0.0058789 | 0.00049134 | 0.0085706 | 1.8311 | 1.9592 | 1.5427 | 1.9318 | 1.9226 | 1.7487 | 1.9821 | 1.8677 | 2.0416 | 1.5884 | 123.642 | -0.045776 | 123.9304 | 124.0311 | -0.082398 | 123.6877 | 0.036621 | 0.28839 | 124.0814 | 123.967 | 124.0219 | 124.0585 | 123.9304 | 124.1409 | 123.848 | 123.6877 | 124.0585 | 123.9304 | 123.848 | 124.0219 | 124.1409 | -0.46234 | -0.41657
1907.6406 | 124.3011 | -122.081 | 2.0828 | -0.094376 | 0.0032833 | 0.0029373 | 0.028634 | -0.0043835 | -0.0014313 | 0.007716 | 1.8082 | 1.9775 | 1.506 | 1.9272 | 1.8997 | 1.9821 | 1.7578 | 2.0874 | 2.1057 | 1.6113 | 123.587 | -0.10529 | 123.8892 | 124.0082 | -0.18311 | 123.6923 | 0.022888 | 0.30212 | 123.8388 | 124.1684 | 123.9807 | 124.0585 | 123.8892 | 124.1867 | 124.0631 | 123.6923 | 124.0585 | 123.8892 | 124.0631 | 123.9807 | 124.1867 | -0.57678 | -0.4715
1908.6406 | 124.3515 | -122.0901 | 2.0279 | -0.24696 | 0.0028561 | -0.0075303 | 0.022225 | -0.0045971 | -0.0014313 | 0.0075024 | 1.8356 | 1.9547 | 1.5335 | 1.9318 | 1.9318 | 1.9547 | 1.6983 | 2.124 | 2.037 | 1.6067 | 123.6237 | -0.073242 | 123.9258 | 124.0219 | -0.09613 | 123.6969 | 0.009155 | 0.30212 | 123.7885 | 124.2142 | 124.0219 | 124.0448 | 123.9258 | 124.1272 | 124.0448 | 123.6969 | 124.0448 | 123.9258 | 124.0448 | 124.0219 | 124.1272 | -0.49439 | -0.42114
1909.6406 | 124.3607 | -122.0581 | 2.0554 | -0.086746 | 0.0052059 | -0.0030441 | 0.019235 | -0.0054517 | -0.0012177 | 0.0079296 | 1.799 | 1.9913 | 1.5381 | 1.9363 | 1.9363 | 1.9775 | 1.7212 | 2.1469 | 2.0828 | 1.6388 | 123.5962 | -0.064087 | 123.8571 | 123.9944 | -0.11902 | 123.6969 | 0.027466 | 0.26092 | 123.7793 | 124.205 | 123.9944 | 124.0494 | 123.8571 | 124.1409 | 124.0356 | 123.6969 | 124.0494 | 123.8571 | 124.0356 | 123.9944 | 124.1409 | -0.51727 | -0.41657
1910.6406 | 124.4385 | -122.1085 | 2.0462 | -0.094376 | 0.0047787 | -0.0068893 | 0.022653 | -0.0075879 | -0.0031403 | 0.0075024 | 1.8402 | 1.9455 | 1.5518 | 1.9638 | 1.9547 | 1.973 | 1.6525 | 2.1744 | 2.0508 | 1.6159 | 123.6603 | -0.10071 | 123.9487 | 124.0723 | -0.091553 | 123.7244 | 0.004577 | 0.28839 | 123.761 | 124.2828 | 124.0631 | 124.054 | 123.9487 | 124.1592 | 124.0814 | 123.7244 | 124.054 | 123.9487 | 124.0814 | 124.0631 | 124.1592 | -0.49438 | -0.4303
1911.6406 | 124.3652 | -122.0901 | 2.0142 | -0.056229 | 0.0032833 | -0.0026169 | 0.02308 | -0.0071607 | 6.414e-05 | 0.007716 | 1.8173 | 1.9592 | 1.5472 | 1.8906 | 1.9043 | 1.9363 | 1.6708 | 2.1057 | 2.0416 | 1.593 | 123.6374 | -0.054931 | 123.9075 | 123.9807 | -0.10986 | 123.6832 | 0.027466 | 0.27008 | 123.761 | 124.1959 | 123.9944 | 124.0494 | 123.9075 | 124.1318 | 124.0265 | 123.6832 | 124.0494 | 123.9075 | 124.0265 | 123.9944 | 124.1318 | -0.46692 | -0.42114
1912.6406 | 124.2462 | -122.1313 | 2.0279 | -0.010452 | 0.0067013 | 0.00016015 | 0.030343 | -0.0073743 | -0.0014313 | 0.0081432 | 1.7715 | 1.973 | 1.4832 | 1.8219 | 1.767 | 1.799 | 1.7761 | 1.9501 | 2.037 | 1.5381 | 123.6145 | -0.054932 | 123.9029 | 123.9532 | -0.26093 | 123.6694 | 0.009155 | 0.28839 | 123.9075 | 124.0814 | 123.8983 | 124.1043 | 123.9029 | 124.1684 | 123.9304 | 123.6694 | 124.1043 | 123.9029 | 123.9304 | 123.8983 | 124.1684 | -0.54474 | -0.48981
1913.6406 | 124.3561 | -122.0856 | 2.0416 | -0.048599 | 0.0041379 | -0.0019761 | 0.019021 | -0.0073743 | -0.0020721 | 0.0070752 | 1.7761 | 1.973 | 1.5427 | 1.9043 | 1.9089 | 1.9363 | 1.7029 | 2.124 | 2.0554 | 1.5884 | 123.6282 | -0.068665 | 123.8617 | 123.9899 | -0.13275 | 123.674 | 0.013733 | 0.23346 | 123.7885 | 124.2096 | 123.9944 | 124.0585 | 123.8617 | 124.1409 | 124.0219 | 123.674 | 124.0585 | 123.8617 | 124.0219 | 123.9944 | 124.1409 | -0.49896 | -0.45319
1914.6406 | 124.379 | -122.0856 | 1.9958 | -0.10963 | 0.0017881 | -0.0030441 | 0.020944 | -0.0090833 | -0.00036306 | 0.006007 | 1.8311 | 1.9455 | 1.5244 | 1.9135 | 1.9135 | 1.9318 | 1.6205 | 2.1378 | 2.0096 | 1.5747 | 123.6099 | -0.050354 | 123.9166 | 123.999 | -0.082398 | 123.6603 | 0.013733 | 0.3067 | 123.7061 | 124.2233 | 123.999 | 124.0311 | 123.9166 | 124.0952 | 124.0173 | 123.6603 | 124.0311 | 123.9166 | 124.0173 | 123.999 | 124.0952 | -0.4715 | -0.42114
1915.6562 | 124.2966 | -122.1313 | 2.0096 | -0.25459 | 0.0056333 | -0.0028305 | 0.02842 | -0.0043835 | -0.00057686 | 0.0053662 | 1.7624 | 1.9775 | 1.4694 | 1.8356 | 1.7944 | 1.8036 | 1.7761 | 2.005 | 2.0187 | 1.5427 | 123.6008 | -0.032044 | 123.8937 | 123.967 | -0.21515 | 123.674 | 0.009155 | 0.29297 | 123.9075 | 124.1364 | 123.9258 | 124.1089 | 123.8937 | 124.1501 | 123.9349 | 123.674 | 124.1089 | 123.8937 | 123.9349 | 123.9258 | 124.1501 | -0.54016 | -0.46692
1916.6406 | 124.3103 | -122.1268 | 2.0004 | -0.17067 | 0.0047787 | -0.0032577 | 0.020516 | -0.0054517 | -0.0031403 | 0.0081432 | 1.8677 | 1.9501 | 1.5976 | 1.8677 | 1.8585 | 1.8677 | 1.7441 | 2.0737 | 2.0279 | 1.5472 | 123.7244 | -0.050354 | 123.9944 | 123.9944 | -0.14191 | 123.674 | 0.027466 | 0.27008 | 123.8708 | 124.2004 | 123.9853 | 124.0768 | 123.9944 | 124.1547 | 123.9944 | 123.674 | 124.0768 | 123.9944 | 123.9944 | 123.9853 | 124.1547 | -0.40283 | -0.45319
1917.6406 | 124.2554 | -122.1817 | 2.0233 | -0.2317 | 0.0047787 | -0.0030441 | 0.026711 | -0.0031019 | -0.0027131 | 0.008357 | 1.7761 | 1.9592 | 1.5427 | 1.7807 | 1.7487 | 1.7807 | 1.8173 | 1.9592 | 2.0325 | 1.506 | 123.7244 | -0.064086 | 123.9578 | 123.9624 | -0.27466 | 123.6877 | 0.009156 | 0.23346 | 123.999 | 124.1409 | 123.9304 | 124.1409 | 123.9578 | 124.2142 | 123.9624 | 123.6877 | 124.1409 | 123.9578 | 123.9624 | 123.9304 | 124.2142 | -0.48065 | -0.51727
1918.6406 | 124.3515 | -122.1039 | 2.0416 | -0.056229 | 0.0030697 | -0.0032577 | 0.019876 | -0.0054517 | -0.0022859 | 0.0062206 | 1.8539 | 1.9409 | 1.6159 | 1.8814 | 1.8768 | 1.9226 | 1.7029 | 2.0874 | 2.0462 | 1.5976 | 123.7198 | -0.10071 | 123.9578 | 123.9853 | -0.1648 | 123.7015 | 0.004578 | 0.23804 | 123.8068 | 124.1913 | 123.9807 | 124.0448 | 123.9578 | 124.1501 | 124.0265 | 123.7015 | 124.0448 | 123.9578 | 124.0265 | 123.9807 | 124.1501 | -0.42572 | -0.44403
1919.6406 | 124.379 | -122.0673 | 2.0416 | -0.12489 | 0.0041379 | -0.0011215 | 0.019662 | -0.0069471 | -0.0010041 | 0.0070752 | 1.9363 | 1.9592 | 1.6434 | 1.9409 | 1.9409 | 1.973 | 1.6525 | 2.1606 | 2.0462 | 1.6205 | 123.7106 | -0.082397 | 124.0036 | 124.0082 | -0.10071 | 123.6877 | 0.004578 | 0.29297 | 123.7198 | 124.2279 | 124.0082 | 124.0265 | 124.0036 | 124.1135 | 124.0402 | 123.6877 | 124.0265 | 124.0036 | 124.0402 | 124.0082 | 124.1135 | -0.39825 | -0.42114
1920.6562 | 124.3561 | -122.081 | 2.092 | -0.20119 | 0.0067013 | -0.00069425 | 0.029275 | -0.0043835 | -0.0029267 | 0.0075024 | 1.9363 | 2.0233 | 1.6296 | 1.8997 | 1.8677 | 1.8814 | 1.7715 | 2.0554 | 2.0782 | 1.5747 | 123.7106 | -0.068665 | 124.0173 | 123.9807 | -0.2243 | 123.6557 | -0.013733 | 0.3067 | 123.8525 | 124.1364 | 123.9487 | 124.1043 | 124.0173 | 124.1592 | 123.9624 | 123.6557 | 124.1043 | 124.0173 | 123.9624 | 123.9487 | 124.1592 | -0.46234 | -0.51727
1921.6406 | 124.2462 | -122.113 | 2.0691 | -0.29274 | 0.0039243 | 0.0010147 | 0.023294 | -0.0056653 | -0.0012177 | 0.0081432 | 1.8814 | 1.9913 | 1.6251 | 1.8723 | 1.8677 | 1.8494 | 1.8311 | 2.0508 | 2.1011 | 1.5839 | 123.7381 | -0.07782 | 123.9944 | 123.9853 | -0.20142 | 123.6969 | 0.032043 | 0.25635 | 123.9441 | 124.1638 | 123.9807 | 124.1043 | 123.9944 | 124.2142 | 123.9624 | 123.6969 | 124.1043 | 123.9944 | 123.9624 | 123.9807 | 124.2142 | -0.44403 | -0.48523
1922.6406 | 124.3561 | -122.0856 | 2.0599 | -0.20882 | 0.0045651 | -5.3452e-05 | 0.022439 | -0.0041699 | -0.0016449 | 0.0070752 | 1.9363 | 1.973 | 1.6525 | 1.9318 | 1.9318 | 1.9501 | 1.712 | 2.1469 | 2.0691 | 1.593 | 123.7381 | -0.086976 | 124.0219 | 124.0173 | -0.12817 | 123.6786 | 0.009155 | 0.28381 | 123.7976 | 124.2325 | 124.0173 | 124.0585 | 124.0219 | 124.1547 | 124.0356 | 123.6786 | 124.0585 | 124.0219 | 124.0356 | 124.0173 | 124.1547 | -0.40741 | -0.46692
1923.6406 | 124.2828 | -122.1725 | 1.9913 | -0.079117 | 0.0060605 | -0.00048065 | 0.027566 | -0.0039563 | -0.0020721 | 0.0079296 | 1.8631 | 1.9318 | 1.5656 | 1.8219 | 1.7807 | 1.7899 | 1.7029 | 1.9684 | 2.005 | 1.5152 | 123.7381 | -0.059509 | 124.0356 | 123.9944 | -0.21057 | 123.6877 | 0.013733 | 0.29755 | 123.8754 | 124.1409 | 123.9532 | 124.1043 | 124.0356 | 124.1776 | 123.9624 | 123.6877 | 124.1043 | 124.0356 | 123.9624 | 123.9532 | 124.1776 | -0.42572 | -0.47607
1924.6406 | 124.379 | -122.1634 | 1.9684 | -0.24696 | 0.0030697 | -0.0028305 | 0.020516 | -0.0060925 | -0.00079046 | 0.006648 | 1.8494 | 1.8814 | 1.593 | 1.8631 | 1.8723 | 1.8997 | 1.6113 | 2.0966 | 1.9958 | 1.561 | 123.7564 | -0.086975 | 124.0128 | 124.0265 | -0.096131 | 123.7244 | 0.027466 | 0.25635 | 123.7747 | 124.2599 | 124.0356 | 124.0448 | 124.0128 | 124.1592 | 124.0631 | 123.7244 | 124.0448 | 124.0128 | 124.0631 | 124.0356 | 124.1592 | -0.37537 | -0.40741
1925.6406 | 124.3378 | -122.1725 | 1.9592 | -0.20882 | 0.0056333 | -0.0015489 | 0.022866 | -0.0039563 | -0.0033539 | 0.008357 | 1.8448 | 1.8951 | 1.5747 | 1.8311 | 1.8265 | 1.8402 | 1.6891 | 2.0462 | 1.9867 | 1.5289 | 123.7473 | -0.064087 | 124.0173 | 124.0036 | -0.13275 | 123.7015 | 0.027465 | 0.27008 | 123.8617 | 124.2188 | 123.999 | 124.0677 | 124.0173 | 124.1592 | 124.0128 | 123.7015 | 124.0677 | 124.0173 | 124.0128 | 123.999 | 124.1592 | -0.38452 | -0.4303
1926.6406 | 124.3927 | -122.1817 | 1.9318 | -0.14015 | 0.0039243 | -0.0047531 | 0.023294 | -0.0075879 | 0.00049134 | 0.0087842 | 1.8448 | 1.886 | 1.593 | 1.8585 | 1.8494 | 1.8814 | 1.5793 | 2.0508 | 1.9684 | 1.5472 | 123.7747 | -0.045777 | 124.0265 | 124.0402 | -0.082398 | 123.7289 | 0.036621 | 0.25177 | 123.761 | 124.2325 | 124.0311 | 124.0677 | 124.0265 | 124.1501 | 124.0631 | 123.7289 | 124.0677 | 124.0265 | 124.0631 | 124.0311 | 124.1501 | -0.33874 | -0.38452
1927.6406 | 124.2554 | -122.2137 | 2.005 | 1.4162 | 0.0060605 | -0.0034715 | 0.025857 | -0.0058789 | -0.0010041 | 0.0055798 | 1.7944 | 1.9867 | 1.5701 | 1.7624 | 1.7715 | 1.7532 | 1.7578 | 1.9409 | 2.037 | 1.5015 | 123.7839 | -0.018311 | 124.0082 | 123.9761 | -0.23346 | 123.7152 | 0.032043 | 0.2243 | 123.9716 | 124.1547 | 123.9853 | 124.2004 | 124.0082 | 124.2508 | 123.967 | 123.7152 | 124.2004 | 124.0082 | 123.967 | 123.9853 | 124.2508 | -0.43488 | -0.50354
1928.6562 | 124.2737 | -122.1954 | 2.0096 | 0.0048064 | 0.0069149 | -0.0015489 | 0.029489 | -0.0033155 | 0.00070494 | 0.0081432 | 1.8127 | 1.9821 | 1.5793 | 1.7624 | 1.7441 | 1.7715 | 1.7349 | 1.9226 | 2.0233 | 1.5244 | 123.7747 | -0.027466 | 124.0082 | 123.9578 | -0.2655 | 123.7198 | 0.013732 | 0.23346 | 123.9304 | 124.118 | 123.9395 | 124.1776 | 124.0082 | 124.2188 | 123.967 | 123.7198 | 124.1776 | 124.0082 | 123.967 | 123.9395 | 124.2188 | -0.4303 | -0.48523
1929.6406 | 124.3149 | -122.1725 | 1.9638 | -0.27748 | 0.0015743 | -0.0019761 | 0.022225 | -0.0035291 | -0.0014313 | 0.00323 | 1.8402 | 1.8997 | 1.5656 | 1.8448 | 1.8219 | 1.8448 | 1.6983 | 2.0142 | 1.9867 | 1.5244 | 123.7381 | -0.064087 | 124.0128 | 124.0173 | -0.14191 | 123.6969 | 0.022888 | 0.27466 | 123.8708 | 124.1867 | 123.9944 | 124.0723 | 124.0128 | 124.1592 | 124.0173 | 123.6969 | 124.0723 | 124.0128 | 124.0173 | 123.9944 | 124.1592 | -0.39825 | -0.43945
1930.6406 | 124.2874 | -122.2 | 1.9547 | -0.10201 | 0.0056333 | -0.0017625 | 0.028848 | -0.0048107 | -0.0035675 | 0.0064344 | 1.8494 | 1.9363 | 1.5564 | 1.8219 | 1.7624 | 1.7853 | 1.6983 | 1.9547 | 1.973 | 1.4877 | 123.7564 | -0.018311 | 124.0494 | 124.0219 | -0.19226 | 123.6877 | 0.01831 | 0.29297 | 123.8983 | 124.1547 | 123.9624 | 124.1364 | 124.0494 | 124.173 | 123.9853 | 123.6877 | 124.1364 | 124.0494 | 123.9853 | 123.9624 | 124.173 | -0.39826 | -0.46692
1931.6406 | 124.3744 | -122.1588 | 1.9501 | -0.079117 | 0.0043515 | -0.0032577 | 0.021798 | -0.0043835 | 0.0015595 | 0.0096386 | 1.8448 | 1.8997 | 1.5701 | 1.8585 | 1.8585 | 1.8997 | 1.6022 | 2.0828 | 1.9638 | 1.5381 | 123.7289 | -0.050354 | 124.0036 | 124.0173 | -0.091552 | 123.6969 | 0.013733 | 0.27466 | 123.761 | 124.2416 | 124.0173 | 124.0585 | 124.0036 | 124.1226 | 124.0585 | 123.6969 | 124.0585 | 124.0036 | 124.0585 | 124.0173 | 124.1226 | -0.37994 | -0.41199
1932.6406 | 124.2508 | -122.1863 | 1.9867 | 0.9127 | 0.0054197 | 0.00016015 | 0.027139 | -0.0078015 | -0.0018585 | 0.0072888 | 1.7487 | 1.973 | 1.5747 | 1.7532 | 1.7532 | 1.7578 | 1.7761 | 1.9501 | 2.0187 | 1.5198 | 123.761 | -0.013733 | 123.9349 | 123.9395 | -0.23346 | 123.7061 | 0.032044 | 0.17395 | 123.9624 | 124.1364 | 123.9395 | 124.1592 | 123.9349 | 124.205 | 123.9441 | 123.7061 | 124.1592 | 123.9349 | 123.9441 | 123.9395 | 124.205 | -0.41199 | -0.46692
1933.6562 | 124.292 | -122.2046 | 1.9592 | -0.21645 | 0.0067013 | -0.0030441 | 0.029702 | -0.0013929 | -0.0031403 | 0.0081432 | 1.9089 | 2.0004 | 1.6113 | 1.8036 | 1.7853 | 1.8082 | 1.6937 | 1.9913 | 2.0004 | 1.5152 | 123.8159 | 0.041198 | 124.1135 | 124.0082 | -0.17395 | 123.7198 | 0.041198 | 0.29755 | 123.8983 | 124.1959 | 123.9899 | 124.205 | 124.1135 | 124.205 | 124.0128 | 123.7198 | 124.205 | 124.1135 | 124.0128 | 123.9899 | 124.205 | -0.3479 | -0.44403
1934.6406 | 124.4385 | -122.1954 | 1.9501 | -0.18593 | 0.0047787 | -0.0045395 | 0.01838 | -0.0039563 | -0.0022859 | 0.0062206 | 1.8814 | 1.8997 | 1.6067 | 1.8768 | 1.886 | 1.8997 | 1.6022 | 2.1103 | 1.9821 | 1.561 | 123.8022 | -0.050354 | 124.0768 | 124.0723 | -0.064087 | 123.7564 | 0.032044 | 0.27466 | 123.7976 | 124.3057 | 124.0814 | 124.0952 | 124.0768 | 124.1776 | 124.0952 | 123.7564 | 124.0952 | 124.0768 | 124.0952 | 124.0814 | 124.1776 | -0.34332 | -0.3891
1935.6406 | 124.3011 | -122.1817 | 2.005 | -0.16304 | 0.0056333 | -5.3452e-05 | 0.028634 | -0.0045971 | -0.0033539 | 0.0072888 | 1.8951 | 1.9638 | 1.5884 | 1.8448 | 1.7944 | 1.8311 | 1.7212 | 1.9958 | 2.0187 | 1.5198 | 123.7701 | -0.041199 | 124.0768 | 124.0265 | -0.21057 | 123.7015 | 0.013733 | 0.3067 | 123.9029 | 124.1776 | 123.9761 | 124.1455 | 124.0768 | 124.2004 | 124.0128 | 123.7015 | 124.1455 | 124.0768 | 124.0128 | 123.9761 | 124.2004 | -0.41657 | -0.48523
1936.6406 | 124.3881 | -122.113 | 1.9913 | -0.88783 | 0.0056333 | -0.0024033 | 0.022653 | -0.0037427 | -0.0012177 | 0.0089978 | 1.6846 | 1.9135 | 1.5976 | 1.8814 | 1.8997 | 1.9455 | 1.6434 | 2.1149 | 2.0096 | 1.5884 | 123.7106 | -0.07782 | 123.7976 | 123.9944 | -0.091553 | 123.7015 | 0.018311 | 0.086975 | 123.7564 | 124.2279 | 124.0128 | 124.0265 | 123.7976 | 124.1226 | 124.0585 | 123.7015 | 124.0265 | 123.7976 | 124.0585 | 124.0128 | 124.1226 | -0.39368 | -0.40283
1937.6406 | 124.2828 | -122.1771 | 1.9867 | -0.19356 | 0.0052059 | -0.00048065 | 0.026711 | -0.0035291 | -0.0042085 | 0.006007 | 1.8173 | 1.9592 | 1.5839 | 1.7944 | 1.7761 | 1.7899 | 1.7853 | 1.973 | 2.037 | 1.5289 | 123.761 | -0.027465 | 123.9944 | 123.9716 | -0.21057 | 123.7061 | 0.050354 | 0.23346 | 123.9624 | 124.1501 | 123.9532 | 124.1364 | 123.9944 | 124.2142 | 123.967 | 123.7061 | 124.1364 | 123.9944 | 123.967 | 123.9532 | 124.2142 | -0.40283 | -0.45776
1938.6562 | 124.2416 | -122.2 | 1.9913 | 0.065841 | 0.0060605 | -0.0013351 | 0.027993 | -0.0022473 | -0.0035675 | 0.007716 | 1.8082 | 1.9409 | 1.5427 | 1.7532 | 1.7395 | 1.7578 | 1.767 | 1.9135 | 2.0187 | 1.5152 | 123.7427 | -0.050354 | 124.0082 | 123.9532 | -0.25177 | 123.7152 | 0.027466 | 0.2655 | 123.967 | 124.1135 | 123.9395 | 124.1409 | 124.0082 | 124.2188 | 123.9578 | 123.7152 | 124.1409 | 124.0082 | 123.9578 | 123.9395 | 124.2188 | -0.44861 | -0.47607
1939.6406 | 124.3744 | -122.1634 | 1.9684 | -0.048599 | 0.0032833 | -0.00026705 | 0.019448 | -0.0043835 | -0.0018585 | 0.0075024 | 1.8494 | 1.9226 | 1.5976 | 1.8311 | 1.8631 | 1.8906 | 1.6159 | 2.0599 | 2.0142 | 1.561 | 123.761 | -0.045777 | 124.0128 | 123.9944 | -0.10529 | 123.7244 | 0.045776 | 0.25177 | 123.7793 | 124.2233 | 124.0265 | 124.086 | 124.0128 | 124.1776 | 124.054 | 123.7244 | 124.086 | 124.0128 | 124.054 | 124.0265 | 124.1776 | -0.37079 | -0.40741
1940.6562 | 124.2599 | -122.2092 | 2.005 | -0.41481 | 0.0043515 | -0.0021897 | 0.026711 | -0.0078015 | -0.00057686 | 0.009425 | 1.8127 | 1.9684 | 1.5793 | 1.7807 | 1.767 | 1.7715 | 1.7899 | 1.9501 | 2.0233 | 1.5244 | 123.7885 | -0.036621 | 124.0219 | 123.9899 | -0.23804 | 123.7335 | 0.01831 | 0.23346 | 123.999 | 124.1592 | 123.9761 | 124.1776 | 124.0219 | 124.2325 | 123.9807 | 123.7335 | 124.1776 | 124.0219 | 123.9807 | 123.9761 | 124.2325 | -0.42572 | -0.48065
1941.6406 | 124.3561 | -122.1542 | 1.9775 | -0.22408 | 0.0039243 | -0.0013351 | 0.021585 | -0.0056653 | -0.0012177 | 0.0081432 | 1.8723 | 1.9089 | 1.6022 | 1.8723 | 1.8768 | 1.886 | 1.6525 | 2.092 | 1.9821 | 1.5427 | 123.7564 | -0.068664 | 124.0265 | 124.0265 | -0.10071 | 123.6969 | 0.004578 | 0.27008 | 123.8068 | 124.2462 | 124.0311 | 124.0631 | 124.0265 | 124.1364 | 124.0402 | 123.6969 | 124.0631 | 124.0265 | 124.0402 | 124.0311 | 124.1364 | -0.37537 | -0.43487
1942.6406 | 124.4293 | -122.1405 | 1.9592 | -0.19356 | 0.0024289 | 0.00037395 | 0.021585 | -0.0052381 | -0.0033539 | 0.0072888 | 1.9089 | 1.9043 | 1.6159 | 1.9684 | 1.6846 | 1.7303 | 1.7761 | 2.0416 | 1.9867 | 1.5564 | 123.7564 | -0.054932 | 124.0494 | 124.1089 | -0.27466 | 123.6969 | 0.027465 | 0.29297 | 123.9166 | 124.1821 | 123.8251 | 124.0448 | 124.0494 | 124.1272 | 123.8708 | 123.6969 | 124.0448 | 124.0494 | 123.8708 | 123.8251 | 124.1272 | -0.34332 | -0.40283
1943.6406 | 124.3927 | -122.0764 | 2.0142 | -0.094376 | 0.0045651 | -0.0030441 | 0.020944 | -0.0075879 | -0.0031403 | 0.006007 | 1.9089 | 1.9501 | 1.6251 | 1.8997 | 1.8997 | 1.9363 | 1.6525 | 2.1332 | 2.0325 | 1.5839 | 123.7015 | -0.064087 | 123.9853 | 123.9761 | -0.11444 | 123.6603 | 0.018311 | 0.28381 | 123.7289 | 124.2096 | 123.9761 | 124.0265 | 123.9853 | 124.1089 | 124.0128 | 123.6603 | 124.0265 | 123.9853 | 124.0128 | 123.9761 | 124.1089 | -0.3891 | -0.4303
1944.6406 | 124.3698 | -122.1176 | 2.0325 | -0.071488 | 0.0013607 | -0.0019761 | 0.021798 | -0.0069471 | -0.0018585 | 0.0072888 | 1.8906 | 1.9409 | 1.6159 | 1.9043 | 1.886 | 1.9272 | 1.6434 | 2.1011 | 2.037 | 1.5976 | 123.7335 | -0.091553 | 124.0082 | 124.0219 | -0.14649 | 123.7152 | 0.004577 | 0.27466 | 123.761 | 124.2188 | 124.0036 | 124.0585 | 124.0082 | 124.1547 | 124.0448 | 123.7152 | 124.0585 | 124.0082 | 124.0448 | 124.0036 | 124.1547 | -0.41657 | -0.43488
1945.6406 | 124.3607 | -122.1085 | 2.0462 | 0.15739 | 0.0056333 | -0.0041123 | 0.021371 | -0.0043835 | -0.00057686 | 0.0062206 | 1.9363 | 1.9913 | 1.6663 | 1.8906 | 1.8677 | 1.918 | 1.6663 | 2.0828 | 2.0645 | 1.6159 | 123.7747 | -0.054932 | 124.0448 | 123.999 | -0.17853 | 123.7244 | 0.01831 | 0.27008 | 123.7747 | 124.1913 | 123.9761 | 124.0997 | 124.0448 | 124.173 | 124.0265 | 123.7244 | 124.0997 | 124.0448 | 124.0265 | 123.9761 | 124.173 | -0.37994 | -0.4303
1946.6406 | 124.379 | -122.0901 | 2.037 | 0.0048064 | 0.0043515 | -0.00026705 | 0.020303 | -0.0069471 | -0.0010041 | 0.008357 | 1.8951 | 1.9638 | 1.6525 | 1.9089 | 1.8997 | 1.9272 | 1.6754 | 2.1194 | 2.0599 | 1.6205 | 123.7427 | -0.073242 | 123.9853 | 123.999 | -0.13733 | 123.7106 | 0.022889 | 0.24262 | 123.7656 | 124.2096 | 123.9899 | 124.054 | 123.9853 | 124.1501 | 124.0173 | 123.7106 | 124.054 | 123.9853 | 124.0173 | 123.9899 | 124.1501 | -0.38452 | -0.41657
1947.6406 | 124.379 | -122.0901 | 2.0462 | -0.033341 | 0.0041379 | -0.0060349 | 0.022653 | -0.0071607 | 0.00027774 | 0.007716 | 1.9043 | 1.9821 | 1.6617 | 1.918 | 1.8997 | 1.9409 | 1.6846 | 2.1194 | 2.0691 | 1.6113 | 123.7518 | -0.064087 | 123.9944 | 124.0082 | -0.14648 | 123.7015 | 0.022888 | 0.24261 | 123.7747 | 124.2096 | 123.9899 | 124.0723 | 123.9944 | 124.1592 | 124.0311 | 123.7015 | 124.0723 | 123.9944 | 124.0311 | 123.9899 | 124.1592 | -0.38452 | -0.43488
1948.6406 | 124.4019 | -122.081 | 2.0325 | -0.11726 | 0.0039243 | -0.0019761 | 0.021157 | -0.0082287 | -0.0018585 | 0.008357 | 1.9226 | 1.9684 | 1.6663 | 1.9409 | 1.9135 | 1.973 | 1.6617 | 2.1469 | 2.0554 | 1.6067 | 123.7473 | -0.064087 | 124.0036 | 124.0219 | -0.11902 | 123.6877 | 0.022888 | 0.25635 | 123.7427 | 124.2279 | 123.9944 | 124.0494 | 124.0036 | 124.1364 | 124.054 | 123.6877 | 124.0494 | 124.0036 | 124.054 | 123.9944 | 124.1364 | -0.36621 | -0.42572
1949.6406 | 124.4156 | -122.0856 | 2.0462 | -0.063858 | 0.0045651 | -0.0058213 | 0.020944 | -0.0073743 | -0.0027131 | 0.0081432 | 1.9455 | 1.9821 | 1.6754 | 1.9409 | 1.918 | 1.9501 | 1.6525 | 2.1515 | 2.0554 | 1.6022 | 123.761 | -0.064087 | 124.0311 | 124.0265 | -0.12817 | 123.6877 | 0.009155 | 0.27008 | 123.7381 | 124.2371 | 124.0036 | 124.0677 | 124.0311 | 124.1409 | 124.0356 | 123.6877 | 124.0677 | 124.0311 | 124.0356 | 124.0036 | 124.1409 | -0.37079 | -0.44403
1950.6406 | 124.2599 | -122.1222 | 2.1011 | -0.18593 | 0.0052059 | -0.00026705 | 0.022653 | -0.010365 | -0.00036306 | 0.0081432 | 1.8814 | 2.0142 | 1.6525 | 1.7441 | 1.7624 | 1.8906 | 1.7899 | 2.0187 | 2.1286 | 1.6113 | 123.7747 | -0.086975 | 124.0036 | 123.8663 | -0.33875 | 123.7335 | 0.027466 | 0.22888 | 123.912 | 124.1409 | 123.8846 | 124.1364 | 124.0036 | 124.2508 | 124.0128 | 123.7335 | 124.1364 | 124.0036 | 124.0128 | 123.8846 | 124.2508 | -0.44861 | -0.48981
1951.6406 | 124.3744 | -122.0718 | 2.0416 | -0.10201 | 0.0028561 | -0.0011215 | 0.020516 | -0.0045971 | 6.414e-05 | 0.0072888 | 1.9501 | 2.0004 | 1.6891 | 1.9318 | 1.9363 | 1.9547 | 1.6891 | 2.1469 | 2.0828 | 1.6205 | 123.761 | -0.041199 | 124.0219 | 124.0036 | -0.10529 | 123.6923 | 0.041199 | 0.26092 | 123.761 | 124.2188 | 124.0082 | 124.0723 | 124.0219 | 124.1547 | 124.0265 | 123.6923 | 124.0723 | 124.0219 | 124.0265 | 124.0082 | 124.1547 | -0.35248 | -0.42114
1952.6406 | 124.3744 | -122.0581 | 2.0554 | -0.048599 | 0.0041379 | -0.0056077 | 0.018807 | -0.0075879 | -0.0014313 | 0.0089978 | 1.9455 | 2.0187 | 1.6891 | 1.9318 | 1.9135 | 1.9501 | 1.6937 | 2.1606 | 2.1011 | 1.6525 | 123.7473 | -0.036621 | 124.0036 | 123.9899 | -0.14191 | 123.7106 | 0.045776 | 0.25635 | 123.7518 | 124.2188 | 123.9716 | 124.0768 | 124.0036 | 124.1592 | 124.0082 | 123.7106 | 124.0768 | 124.0036 | 124.0082 | 123.9716 | 124.1592 | -0.36621 | -0.40283
1953.6406 | 124.3607 | -122.0718 | 2.0874 | -0.010452 | 0.0056333 | -0.0024033 | 0.020089 | -0.0065197 | 0.00070494 | 0.0072888 | 1.9363 | 2.0279 | 1.6983 | 1.9409 | 1.9226 | 1.9638 | 1.6891 | 2.1515 | 2.0874 | 1.6434 | 123.7701 | -0.059509 | 124.0082 | 124.0128 | -0.1648 | 123.7152 | 0 | 0.23804 | 123.761 | 124.2233 | 123.9944 | 124.0997 | 124.0082 | 124.1592 | 124.0356 | 123.7152 | 124.0997 | 124.0082 | 124.0356 | 123.9944 | 124.1592 | -0.3891 | -0.44403
1954.6406 | 124.3469 | -122.0444 | 2.0691 | -0.048599 | 0.0039243 | -0.0038987 | 0.021157 | -0.0056653 | 6.414e-05 | 0.009425 | 1.9501 | 2.005 | 1.6891 | 1.9043 | 1.918 | 1.9226 | 1.6891 | 2.1149 | 2.0828 | 1.6251 | 123.7335 | -0.064087 | 123.9944 | 123.9487 | -0.15106 | 123.6694 | 0.013733 | 0.26092 | 123.7335 | 124.1592 | 123.9624 | 124.0494 | 123.9944 | 124.1272 | 123.967 | 123.6694 | 124.0494 | 123.9944 | 123.967 | 123.9624 | 124.1272 | -0.37994 | -0.44403
1955.6562 | 124.2783 | -122.1039 | 2.124 | -0.25459 | 0.0058469 | -0.0015489 | 0.028207 | -0.0058789 | -0.00057686 | 0.007716 | 1.9501 | 2.0599 | 1.6525 | 1.8814 | 1.8494 | 1.8448 | 1.8311 | 2.0782 | 2.1332 | 1.6113 | 123.7564 | -0.064086 | 124.054 | 123.9853 | -0.27466 | 123.7152 | 0.009156 | 0.29755 | 123.9349 | 124.1821 | 123.9532 | 124.1638 | 124.054 | 124.2371 | 123.9487 | 123.7152 | 124.1638 | 124.054 | 123.9487 | 123.9532 | 124.2371 | -0.4715 | -0.5127
1956.6406 | 124.3973 | -122.0352 | 2.1011 | -0.16304 | 0.0032833 | -0.0019761 | 0.022866 | -0.0069471 | -0.0029267 | 0.0064344 | 2.0096 | 2.0279 | 1.7075 | 1.9958 | 1.973 | 1.9821 | 1.6983 | 2.211 | 2.1057 | 1.6525 | 123.7427 | -0.073242 | 124.0448 | 124.0311 | -0.12817 | 123.6877 | 0.004578 | 0.30213 | 123.7335 | 124.2462 | 124.0082 | 124.0631 | 124.0448 | 124.1409 | 124.0173 | 123.6877 | 124.0631 | 124.0448 | 124.0173 | 124.0082 | 124.1409 | -0.39368 | -0.44861
1957.6406 | 124.3607 | -122.0627 | 2.0966 | -0.25459 | 0.0032833 | -0.0024033 | 0.022866 | -0.0073743 | -0.00036306 | 0.0070752 | 1.9867 | 2.005 | 1.712 | 1.9592 | 1.9363 | 1.9501 | 1.7441 | 2.1561 | 2.1011 | 1.6479 | 123.7747 | -0.091553 | 124.0494 | 124.0219 | -0.16022 | 123.7106 | 0.004577 | 0.27466 | 123.8068 | 124.2188 | 123.999 | 124.0677 | 124.0494 | 124.1638 | 124.0128 | 123.7106 | 124.0677 | 124.0494 | 124.0128 | 123.999 | 124.1638 | -0.38452 | -0.44861
1958.6406 | 124.3744 | -122.0856 | 2.092 | -0.018082 | 0.0049923 | -0.0066757 | 0.018807 | -0.0045971 | 6.414e-05 | 0.0079296 | 1.9455 | 2.0096 | 1.6983 | 1.9455 | 1.9318 | 1.9547 | 1.6937 | 2.1561 | 2.092 | 1.6479 | 123.7839 | -0.082397 | 124.0311 | 124.0311 | -0.16022 | 123.7335 | 0 | 0.24719 | 123.7793 | 124.2416 | 124.0173 | 124.0952 | 124.0311 | 124.1776 | 124.0402 | 123.7335 | 124.0952 | 124.0311 | 124.0402 | 124.0173 | 124.1776 | -0.39368 | -0.44403
1959.6406 | 124.4476 | -122.1542 | 2.0508 | 0.035324 | 0.0060605 | -0.0036851 | 0.022012 | -0.0048107 | -0.0010041 | 0.0081432 | 1.9684 | 2.0233 | 1.7075 | 1.9226 | 1.9135 | 1.9455 | 1.6983 | 2.1286 | 2.1149 | 1.6525 | 123.8617 | -0.027466 | 124.1226 | 124.0768 | -0.13733 | 123.8068 | 0.064087 | 0.26093 | 123.8525 | 124.2828 | 124.0677 | 124.1776 | 124.1226 | 124.2691 | 124.0997 | 123.8068 | 124.1776 | 124.1226 | 124.0997 | 124.0677 | 124.2691 | -0.34332 | -0.39825
1960.6562 | 124.3195 | -122.1085 | 2.0828 | -0.17067 | 0.0067013 | -0.0024033 | 0.02842 | -0.0022473 | -0.0010041 | 0.0070752 | 1.9592 | 2.0599 | 1.6617 | 1.9226 | 1.8997 | 1.9089 | 1.7899 | 2.0828 | 2.1286 | 1.6067 | 123.7701 | -0.022888 | 124.0677 | 124.0311 | -0.18311 | 123.7152 | 0.045776 | 0.29755 | 123.8983 | 124.1913 | 124.0082 | 124.1684 | 124.0677 | 124.2371 | 124.0173 | 123.7152 | 124.1684 | 124.0677 | 124.0173 | 124.0082 | 124.2371 | -0.42114 | -0.47608
1961.6406 | 124.3927 | -122.0398 | 2.1423 | -0.056229 | 0.0043515 | -0.0015489 | 0.02073 | -0.0045971 | -0.0024995 | 0.0096386 | 2.0142 | 2.0691 | 1.7441 | 1.9958 | 2.005 | 2.0233 | 1.712 | 2.211 | 2.1423 | 1.712 | 123.7839 | -0.073242 | 124.054 | 124.0356 | -0.13733 | 123.7518 | 0 | 0.27008 | 123.7518 | 124.2508 | 124.0448 | 124.1089 | 124.054 | 124.1821 | 124.0631 | 123.7518 | 124.1089 | 124.054 | 124.0631 | 124.0448 | 124.1821 | -0.39825 | -0.4303
1962.6406 | 124.3744 | -122.0123 | 2.1515 | -0.025711 | 0.0041379 | -0.00048065 | 0.020516 | -0.0056653 | -0.0016449 | 0.0072888 | 2.0004 | 2.0737 | 1.767 | 1.9867 | 1.9821 | 2.0233 | 1.7303 | 2.1973 | 2.1698 | 1.7075 | 123.7793 | -0.07782 | 124.0128 | 123.999 | -0.16937 | 123.7198 | 0.018311 | 0.23346 | 123.7427 | 124.2096 | 123.9944 | 124.086 | 124.0128 | 124.1821 | 124.0356 | 123.7198 | 124.086 | 124.0128 | 124.0356 | 123.9944 | 124.1821 | -0.38452 | -0.44403
1963.6406 | 124.3835 | -122.0032 | 2.1423 | -0.018082 | 0.0043515 | -0.0026169 | 0.021798 | -0.0060925 | -0.00079046 | 0.0098522 | 1.9913 | 2.0645 | 1.7441 | 1.9821 | 1.9638 | 2.0004 | 1.7166 | 2.1881 | 2.1606 | 1.712 | 123.7473 | -0.07782 | 123.9944 | 123.9853 | -0.17853 | 123.7152 | 0.018311 | 0.24719 | 123.7198 | 124.1913 | 123.967 | 124.0677 | 123.9944 | 124.1638 | 124.0036 | 123.7152 | 124.0677 | 123.9944 | 124.0036 | 123.967 | 124.1638 | -0.39825 | -0.4303
1964.6406 | 124.3744 | -122.0032 | 2.1469 | -0.048599 | 0.0043515 | -0.0062485 | 0.021371 | -0.0039563 | -0.00014946 | 0.0085706 | 1.9958 | 2.0691 | 1.7395 | 2.0004 | 1.9684 | 2.0187 | 1.7441 | 2.1927 | 2.1378 | 1.7075 | 123.7427 | -0.07782 | 123.999 | 124.0036 | -0.17853 | 123.7106 | -0.009156 | 0.25635 | 123.7473 | 124.1959 | 123.9716 | 124.0723 | 123.999 | 124.1409 | 124.0219 | 123.7106 | 124.0723 | 123.999 | 124.0219 | 123.9716 | 124.1409 | -0.40741 | -0.43945
1965.6406 | 124.379 | -122.0581 | 2.1378 | -0.1783 | 0.0064877 | -0.00069425 | 0.020089 | -0.0060925 | 0.00070494 | 0.0087842 | 1.9638 | 2.0325 | 1.7029 | 1.9684 | 1.9638 | 2.005 | 1.7395 | 2.1606 | 2.1378 | 1.6663 | 123.761 | -0.10528 | 124.0219 | 124.0265 | -0.17395 | 123.7244 | 0 | 0.26092 | 123.7976 | 124.2188 | 124.0219 | 124.0906 | 124.0219 | 124.1959 | 124.0631 | 123.7244 | 124.0906 | 124.0219 | 124.0631 | 124.0219 | 124.1959 | -0.43487 | -0.4715
1966.6406 | 124.3561 | -122.0215 | 2.1561 | 0.17265 | 0.0060605 | -0.0019761 | 0.022866 | -0.0065197 | 0.0015595 | 0.0092114 | 2.0279 | 2.0737 | 1.7441 | 2.005 | 1.9775 | 2.0233 | 1.712 | 2.1698 | 2.1332 | 1.7166 | 123.7656 | -0.082398 | 124.0494 | 124.0265 | -0.17853 | 123.7381 | -0.022888 | 0.28381 | 123.7335 | 124.1913 | 123.999 | 124.0952 | 124.0494 | 124.1547 | 124.0448 | 123.7381 | 124.0952 | 124.0494 | 124.0448 | 123.999 | 124.1547 | -0.41199 | -0.43945
1967.6406 | 124.3515 | -122.0123 | 2.1378 | 0.20317 | 0.0032833 | -5.3452e-05 | 0.02308 | -0.0069471 | 0.00049134 | 0.008357 | 2.0508 | 2.0828 | 1.767 | 2.0142 | 1.9867 | 2.0508 | 1.7212 | 2.1973 | 2.1561 | 1.7029 | 123.7793 | -0.054931 | 124.0631 | 124.0265 | -0.15106 | 123.7152 | 0.018311 | 0.28381 | 123.7335 | 124.2096 | 123.999 | 124.0952 | 124.0631 | 124.1684 | 124.0631 | 123.7152 | 124.0952 | 124.0631 | 124.0631 | 123.999 | 124.1684 | -0.37079 | -0.43487
1968.6406 | 124.2966 | -122.0718 | 2.0782 | 0.058212 | 0.0058469 | -0.00069425 | 0.021371 | -0.0052381 | -0.00079046 | 0.0079296 | 2.0187 | 2.092 | 1.7578 | 1.9958 | 1.9821 | 2.0187 | 1.712 | 2.1835 | 2.1423 | 1.6891 | 123.8297 | 0.013733 | 124.0906 | 124.0677 | -0.09613 | 123.761 | 0.064087 | 0.26093 | 123.7839 | 124.2554 | 124.054 | 124.1638 | 124.0906 | 124.2142 | 124.0906 | 123.761 | 124.1638 | 124.0906 | 124.0906 | 124.054 | 124.2142 | -0.32044 | -0.3891
1969.6406 | 124.3607 | -122.0169 | 2.1469 | 0.035324 | 0.0032833 | -0.0036851 | 0.020303 | -0.0073743 | -0.00014946 | 0.0070752 | 2.005 | 2.0828 | 1.7395 | 2.005 | 1.9958 | 2.0233 | 1.7349 | 2.2018 | 2.1515 | 1.7258 | 123.7564 | -0.064087 | 124.0219 | 124.0219 | -0.15106 | 123.7427 | 0.004577 | 0.2655 | 123.7518 | 124.2188 | 124.0128 | 124.0997 | 124.0219 | 124.1684 | 124.0402 | 123.7427 | 124.0997 | 124.0219 | 124.0402 | 124.0128 | 124.1684 | -0.40741 | -0.42114
1970.6562 | 124.3011 | -122.0169 | 2.2156 | -0.2317 | 0.0049923 | -0.0028305 | 0.023507 | -0.0071607 | -0.0016449 | 0.0081432 | 1.9638 | 2.1103 | 1.7029 | 1.9363 | 2.0416 | 2.1286 | 1.8127 | 1.9592 | 2.2247 | 1.68 | 123.7198 | -0.10528 | 123.9807 | 123.9532 | -0.17395 | 123.6969 | 0.009155 | 0.26092 | 123.8297 | 123.9761 | 124.0585 | 124.1272 | 123.9807 | 124.2416 | 124.1455 | 123.6969 | 124.1272 | 123.9807 | 124.1455 | 124.0585 | 124.2416 | -0.51269 | -0.53558
1971.6406 | 124.3561 | -122.0306 | 2.1332 | 1.7214 | 0.0028561 | -0.0049667 | 0.018594 | -0.0056653 | -0.0010041 | 0.0072888 | 2.0142 | 2.0187 | 1.6983 | 1.9684 | 1.973 | 1.9958 | 1.7212 | 2.179 | 2.124 | 1.6846 | 123.7289 | -0.11444 | 124.0448 | 123.999 | -0.16022 | 123.7152 | -0.009156 | 0.31586 | 123.7518 | 124.2096 | 124.0036 | 124.0494 | 124.0448 | 124.1547 | 124.0265 | 123.7152 | 124.0494 | 124.0448 | 124.0265 | 124.0036 | 124.1547 | -0.43488 | -0.44861
1972.6406 | 124.3561 | -122.0444 | 2.1103 | -0.025711 | 0.0056333 | -0.0011215 | 0.025002 | -0.0043835 | -0.00014946 | 0.0064344 | 1.9913 | 2.0508 | 1.7212 | 1.9363 | 1.9272 | 1.9958 | 1.6708 | 2.1469 | 2.0966 | 1.6479 | 123.7656 | -0.05951 | 124.0356 | 123.9807 | -0.18311 | 123.6923 | -0.013733 | 0.27008 | 123.7152 | 124.1913 | 123.9716 | 124.0952 | 124.0356 | 124.1409 | 124.0402 | 123.6923 | 124.0952 | 124.0356 | 124.0402 | 123.9716 | 124.1409 | -0.3891 | -0.46234
1973.6406 | 124.3744 | -122.0032 | 2.124 | 0.11925 | 0.0052059 | -0.0015489 | 0.023507 | -0.0065197 | -0.00036306 | 0.008357 | 2.0462 | 2.0325 | 1.7395 | 2.0004 | 1.9913 | 2.0325 | 1.6846 | 2.1744 | 2.1194 | 1.7029 | 123.7427 | -0.091552 | 124.0494 | 124.0036 | -0.13275 | 123.7061 | -0.004577 | 0.3067 | 123.6877 | 124.1776 | 123.9944 | 124.0356 | 124.0494 | 124.1226 | 124.0356 | 123.7061 | 124.0356 | 124.0494 | 124.0356 | 123.9944 | 124.1226 | -0.38452 | -0.42114
1974.6406 | 124.379 | -122.0215 | 2.1103 | 0.11925 | 0.0039243 | -0.0030441 | 0.022012 | -0.0063061 | -0.0014313 | 0.007716 | 2.037 | 2.0462 | 1.7349 | 2.0142 | 2.005 | 2.0233 | 1.6617 | 2.1744 | 2.1378 | 1.7029 | 123.7564 | -0.064087 | 124.0585 | 124.0356 | -0.10529 | 123.7244 | 0.027465 | 0.30212 | 123.6832 | 124.1959 | 124.0265 | 124.0677 | 124.0585 | 124.1592 | 124.0448 | 123.7244 | 124.0677 | 124.0585 | 124.0448 | 124.0265 | 124.1592 | -0.37537 | -0.40741
1975.6406 | 124.4019 | -122.0444 | 2.1378 | -0.094376 | 0.0032833 | -0.0064621 | 0.020089 | -0.0060925 | -0.00014946 | 0.0085706 | 2.0142 | 2.0691 | 1.7441 | 2.0279 | 2.0142 | 2.0325 | 1.68 | 2.2247 | 2.1469 | 1.7212 | 123.7885 | -0.068664 | 124.0585 | 124.0723 | -0.1236 | 123.7656 | 0.009156 | 0.27008 | 123.7244 | 124.2691 | 124.0585 | 124.1135 | 124.0585 | 124.1913 | 124.0768 | 123.7656 | 124.1135 | 124.0585 | 124.0768 | 124.0585 | 124.1913 | -0.39368 | -0.41657
1976.6406 | 124.3698 | -122.0718 | 2.124 | 0.60753 | 0.0049923 | -0.0013351 | 0.021585 | -0.0069471 | 0.00049134 | 0.0070752 | 1.973 | 1.9821 | 1.6937 | 1.9775 | 1.9638 | 1.9958 | 1.7212 | 2.1652 | 2.1286 | 1.6891 | 123.7656 | -0.14191 | 124.0448 | 124.0494 | -0.16022 | 123.761 | 0.004578 | 0.27923 | 123.793 | 124.2371 | 124.0356 | 124.054 | 124.0448 | 124.2004 | 124.0677 | 123.761 | 124.054 | 124.0448 | 124.0677 | 124.0356 | 124.2004 | -0.4303 | -0.43488
1977.6406 | 124.3698 | -121.9849 | 2.1927 | 0.0811 | 0.0028561 | -0.0088119 | 0.019876 | -0.0073743 | -0.00057686 | 0.0087842 | 2.0187 | 2.124 | 1.7853 | 2.0279 | 1.9958 | 2.0599 | 1.7578 | 2.2385 | 2.1927 | 1.7441 | 123.7701 | -0.068665 | 124.0036 | 124.0128 | -0.19684 | 123.7289 | 0 | 0.23346 | 123.7427 | 124.2233 | 123.9807 | 124.1089 | 124.0036 | 124.1776 | 124.0448 | 123.7289 | 124.1089 | 124.0036 | 124.0448 | 123.9807 | 124.1776 | -0.40741 | -0.44861
1978.6406 | 124.3378 | -121.994 | 2.1194 | -0.0028231 | 0.0049923 | -0.0041123 | 0.022225 | -0.0075879 | 0.00049134 | 0.0057934 | 2.0599 | 2.1149 | 1.8036 | 2.0004 | 1.886 | 1.9958 | 1.7303 | 2.1606 | 2.1561 | 1.712 | 123.7976 | -0.004578 | 124.054 | 123.9944 | -0.23346 | 123.7061 | 0.036621 | 0.25635 | 123.7244 | 124.1547 | 123.88 | 124.1089 | 124.054 | 124.1501 | 123.9899 | 123.7061 | 124.1089 | 124.054 | 123.9899 | 123.88 | 124.1501 | -0.31586 | -0.40741
1979.6406 | 124.4431 | -122.0718 | 2.1149 | 0.08873 | 0.0030697 | 0.00016015 | 0.020944 | -0.0067335 | 0.00049134 | 0.006648 | 2.037 | 2.1103 | 1.7899 | 2.0187 | 2.0142 | 2.0508 | 1.7075 | 2.2064 | 2.179 | 1.7349 | 123.8617 | -0.004577 | 124.1089 | 124.0906 | -0.10071 | 123.8068 | 0.064087 | 0.24719 | 123.7793 | 124.2783 | 124.086 | 124.1821 | 124.1089 | 124.2508 | 124.1226 | 123.8068 | 124.1821 | 124.1089 | 124.1226 | 124.086 | 124.2508 | -0.32501 | -0.37994
1980.6406 | 124.4522 | -121.9437 | 2.1652 | -0.033341 | 0.0056333 | -0.0047531 | 0.022012 | -0.0056653 | -0.00057686 | 0.0068616 | 2.1194 | 2.1057 | 1.8082 | 2.1194 | 2.0874 | 2.1332 | 1.6846 | 2.3071 | 2.2018 | 1.7624 | 123.7518 | -0.059509 | 124.0631 | 124.0631 | -0.07782 | 123.7061 | 0.036621 | 0.31128 | 123.6282 | 124.2508 | 124.0311 | 124.0494 | 124.0631 | 124.1455 | 124.0768 | 123.7061 | 124.0494 | 124.0631 | 124.0768 | 124.0311 | 124.1455 | -0.35705 | -0.40283

## Thermal Data
Fire Time | North 25 C | Conduit Top | Conduit Bottom | TC Cable
-0.824 | 23.8082 | 22.7508 | 22.9046 | 22.2893
0.176 | 23.8073 | 22.7674 | 22.9046 | 22.2881
1.176 | 23.8033 | 22.7632 | 22.9049 | 22.2875
2.176 | 23.8052 | 22.7605 | 22.9005 | 22.2899
3.176 | 24.0253 | 22.7594 | 22.906 | 22.2912
4.176 | 24.9385 | 22.7728 | 22.909 | 22.2918
5.176 | 26.6427 | 22.7647 | 22.9164 | 22.2913
6.176 | 29.0783 | 22.7805 | 22.9205 | 22.2919
7.176 | 32.0576 | 22.7775 | 22.9282 | 22.2862
8.176 | 35.546 | 22.8035 | 22.9381 | 22.2839
9.176 | 39.4142 | 22.8144 | 22.9516 | 22.2879
10.176 | 43.589 | 22.835 | 22.9769 | 22.2906
11.176 | 48.0659 | 22.8492 | 23.0059 | 22.2892
12.176 | 52.7588 | 22.8732 | 23.034 | 22.2871
13.176 | 57.6006 | 22.896 | 23.0642 | 22.2851
14.176 | 62.5974 | 22.937 | 23.0962 | 22.2884
15.176 | 67.78 | 22.97 | 23.1434 | 22.2902
16.176 | 73.1168 | 23.0337 | 23.1903 | 22.2898
17.176 | 78.5508 | 23.0743 | 23.2645 | 22.2885
18.176 | 84.1174 | 23.113 | 23.3297 | 22.2964
19.176 | 89.7647 | 23.1862 | 23.3915 | 22.2858
20.176 | 95.4626 | 23.2501 | 23.445 | 22.2906
21.176 | 101.2272 | 23.322 | 23.4873 | 22.287
22.176 | 107.0899 | 23.3845 | 23.5527 | 22.2883
23.176 | 113.0355 | 23.5897 | 23.6183 | 22.2952
24.176 | 118.9253 | 23.6648 | 23.671 | 22.2925
25.176 | 124.8599 | 23.7466 | 23.7383 | 22.286
26.176 | 130.8554 | 23.8365 | 23.9072 | 22.2887
27.176 | 136.8864 | 23.9471 | 24.0739 | 22.2856
28.176 | 142.9565 | 24.1335 | 24.166 | 22.2809
29.176 | 148.996 | 24.2245 | 24.3047 | 22.2884
30.176 | 154.9367 | 24.3197 | 24.3992 | 22.294
31.176 | 160.9327 | 24.5243 | 24.4776 | 22.289
32.176 | 166.9331 | 24.7645 | 24.5755 | 22.2876
33.176 | 172.879 | 24.8968 | 24.7319 | 22.2897
34.176 | 178.8833 | 25.0189 | 24.9264 | 22.2879
35.176 | 184.9323 | 25.1262 | 25.1324 | 22.2855
36.176 | 190.9424 | 25.3363 | 25.2472 | 22.2826
37.176 | 197.0094 | 25.7476 | 25.3628 | 22.2853
38.176 | 202.9357 | 25.9428 | 25.6378 | 22.2913
39.176 | 208.8835 | 26.0938 | 25.9573 | 22.2777
40.176 | 214.8716 | 26.2596 | 26.1553 | 22.2871
41.176 | 220.8774 | 26.4698 | 26.5134 | 22.289
42.176 | 226.8338 | 26.6436 | 26.804 | 22.2877
43.176 | 232.6823 | 26.8745 | 27.0066 | 22.2853
44.176 | 238.6713 | 27.1488 | 27.1513 | 22.2814
45.176 | 244.5169 | 27.3608 | 27.3904 | 22.2851
46.176 | 250.2855 | 27.6518 | 27.7931 | 22.2838
47.176 | 256.1959 | 27.9635 | 28.2157 | 22.2903
48.176 | 262.1413 | 28.3377 | 28.4477 | 22.2863
49.176 | 268.0398 | 28.7887 | 28.6945 | 22.2845
50.176 | 273.9471 | 29.0654 | 28.9652 | 22.287
51.176 | 279.7172 | 29.4025 | 29.2586 | 22.2931
52.176 | 285.4075 | 29.7842 | 29.5578 | 22.2902
53.176 | 291.1233 | 30.1205 | 29.8647 | 22.2923
54.176 | 296.8871 | 30.4068 | 30.3108 | 22.2831
55.176 | 302.5909 | 30.7533 | 30.5443 | 22.2895
56.176 | 308.1283 | 31.2184 | 30.7539 | 22.2975
57.176 | 313.6502 | 31.6374 | 31.3523 | 22.2945
58.176 | 319.2974 | 32.057 | 31.7134 | 22.2971
59.176 | 325.005 | 32.4796 | 32.0493 | 22.2997
60.176 | 330.4519 | 32.9548 | 32.5745 | 22.3012
61.176 | 336.0436 | 33.5107 | 33.1714 | 22.2963
62.176 | 341.5508 | 33.9964 | 33.5343 | 22.3024
63.176 | 347.0417 | 34.6094 | 34.1685 | 22.3005
64.176 | 352.6234 | 35.0839 | 34.7654 | 22.3114
65.176 | 358.2017 | 35.5976 | 35.4696 | 22.3026
66.176 | 363.6504 | 36.1138 | 36.117 | 22.3074
67.176 | 368.9578 | 36.7566 | 36.6244 | 22.3087
68.176 | 374.2123 | 37.355 | 36.8846 | 22.3141
69.176 | 379.3683 | 37.9271 | 37.2191 | 22.3085
70.176 | 384.5789 | 38.5488 | 37.7551 | 22.3063
71.176 | 389.8498 | 39.1851 | 38.3778 | 22.3113
72.176 | 395.0375 | 39.8252 | 39.1178 | 22.319
73.176 | 400.1735 | 40.4743 | 39.6825 | 22.3181
74.176 | 405.2334 | 41.1493 | 40.2256 | 22.3204
75.176 | 410.4043 | 41.8623 | 40.7962 | 22.3297
76.176 | 415.4574 | 42.574 | 41.3351 | 22.3261
77.176 | 420.3121 | 43.4079 | 42.1783 | 22.33
78.176 | 425.451 | 44.2077 | 42.9308 | 22.3306
79.176 | 430.5281 | 44.9613 | 43.9479 | 22.3295
80.176 | 435.5085 | 45.7914 | 44.9066 | 22.3337
81.176 | 440.4545 | 46.6843 | 45.6043 | 22.3379
82.176 | 445.4214 | 47.526 | 46.4567 | 22.339
83.176 | 450.4818 | 48.3698 | 47.1361 | 22.3411
84.176 | 455.5181 | 49.243 | 47.9807 | 22.3492
85.176 | 460.3924 | 50.1393 | 49.1128 | 22.3551
86.176 | 465.2361 | 51.2021 | 49.9176 | 22.3531
87.176 | 470.1138 | 52.0488 | 50.7203 | 22.367
88.176 | 474.4553 | 52.9668 | 51.5066 | 22.3712
89.176 | 478.1716 | 53.9397 | 52.4865 | 22.3798
90.176 | 481.7494 | 54.8421 | 53.5579 | 22.3797
91.176 | 485.0639 | 55.7213 | 54.1743 | 22.3895
92.176 | 488.0642 | 56.6444 | 55.1646 | 22.3948
93.176 | 490.8737 | 57.6375 | 56.1837 | 22.4024
94.176 | 493.6261 | 58.5915 | 57.1437 | 22.412
95.176 | 496.3275 | 59.6059 | 58.0375 | 22.4146
96.176 | 498.8451 | 60.5375 | 59.0397 | 22.4255
97.176 | 501.4 | 61.5385 | 60.16 | 22.4336
98.176 | 503.9905 | 62.6807 | 61.1595 | 22.4413
99.176 | 506.2273 | 63.6848 | 61.9639 | 22.4517
100.176 | 508.3762 | 64.621 | 63.0387 | 22.4612
101.176 | 510.2183 | 65.6055 | 64.0755 | 22.4679
102.176 | 511.7888 | 66.4718 | 65.0872 | 22.4781
103.176 | 513.0002 | 67.5235 | 65.8852 | 22.4876
104.176 | 514.181 | 68.5433 | 66.5964 | 22.4944
105.176 | 515.2198 | 69.5586 | 67.5773 | 22.5155
106.176 | 516.096 | 70.6551 | 68.4679 | 22.5266
107.176 | 516.657 | 71.5383 | 69.3783 | 22.5333
108.176 | 517.0675 | 72.3923 | 70.1773 | 22.5546
109.176 | 517.5543 | 73.3245 | 71.1192 | 22.575
110.176 | 518.0245 | 74.3108 | 72.0133 | 22.5813
111.176 | 518.4487 | 75.3406 | 72.8886 | 22.5952
112.176 | 518.8571 | 76.3479 | 73.8953 | 22.6118
113.176 | 518.9737 | 77.2789 | 75.0082 | 22.625
114.176 | 519.178 | 78.2398 | 76.0145 | 22.6426
115.176 | 519.2467 | 79.1956 | 76.7672 | 22.6555
116.176 | 519.3778 | 80.2779 | 77.6639 | 22.679
117.176 | 519.628 | 81.2009 | 78.5815 | 22.707
118.176 | 519.7916 | 82.0845 | 79.4628 | 22.7233
119.176 | 519.9846 | 83.1435 | 80.2201 | 22.7416
120.176 | 520.1167 | 84.1213 | 81.0764 | 22.757
121.176 | 520.1506 | 85.0924 | 82.2544 | 22.7892
122.176 | 520.2801 | 86.0524 | 83.1752 | 22.8118
123.176 | 520.3811 | 87.0297 | 84.204 | 22.8341
124.176 | 520.4793 | 88.0315 | 85.1628 | 22.863
125.176 | 520.5592 | 88.993 | 85.9391 | 22.8793
126.176 | 520.7382 | 89.9021 | 86.8883 | 22.911
127.176 | 520.9493 | 90.9491 | 87.8697 | 22.9392
128.176 | 521.2047 | 91.936 | 88.7744 | 22.9709
129.176 | 521.2523 | 92.8963 | 89.4434 | 23.0012
130.176 | 521.3806 | 93.7979 | 90.2167 | 23.0308
131.176 | 521.4053 | 94.8142 | 91.0529 | 23.0602
132.176 | 521.4597 | 95.7803 | 92.1468 | 23.0942
133.176 | 521.6852 | 96.7967 | 93.1013 | 23.1281
134.176 | 522.006 | 97.7124 | 94.0145 | 23.1597
135.176 | 522.0884 | 98.7632 | 95.0969 | 23.1936
136.176 | 522.4375 | 99.6818 | 95.9869 | 23.2265
137.176 | 522.6772 | 100.6121 | 96.9849 | 23.2763
138.176 | 522.7802 | 101.6255 | 97.8091 | 23.3165
139.176 | 522.9479 | 102.5282 | 98.787 | 23.3524
140.176 | 523.2433 | 103.4893 | 99.8106 | 23.3927
141.176 | 523.2909 | 104.4465 | 100.4578 | 23.4354
142.176 | 523.3213 | 105.4424 | 101.2944 | 23.4789
143.176 | 523.5176 | 106.3017 | 102.269 | 23.5288
144.176 | 523.7174 | 107.28 | 103.1549 | 23.5737
145.176 | 523.9084 | 108.2611 | 104.0197 | 23.6266
146.176 | 524.2016 | 109.2437 | 105.0529 | 23.6743
147.176 | 524.4299 | 110.1935 | 105.8544 | 23.7149
148.176 | 524.6046 | 111.0865 | 106.7792 | 23.7812
149.176 | 524.6251 | 112.0165 | 107.7471 | 23.8314
150.176 | 524.6394 | 112.9587 | 108.5634 | 23.8863
151.176 | 524.7506 | 113.8881 | 109.3197 | 23.9489
152.176 | 524.8141 | 114.8518 | 110.2382 | 24.0043
153.176 | 524.7848 | 115.8579 | 111.1909 | 24.0676
154.176 | 524.8668 | 116.7985 | 112.0884 | 24.1207
155.176 | 524.9635 | 117.736 | 113.0729 | 24.1828
156.176 | 525.0763 | 118.6427 | 113.9434 | 24.2515
157.176 | 525.2888 | 119.5932 | 114.7646 | 24.3157
158.176 | 525.3593 | 120.6322 | 115.4779 | 24.385
159.176 | 525.2924 | 121.5012 | 116.3604 | 24.4572
160.176 | 525.1553 | 122.4572 | 117.325 | 24.5231
161.176 | 525.1804 | 123.3678 | 118.1836 | 24.5921
162.176 | 525.2154 | 124.1659 | 119.116 | 24.6654
163.176 | 525.143 | 125.0969 | 119.8978 | 24.745
164.176 | 525.0299 | 126.0129 | 120.7344 | 24.8252
165.176 | 524.9048 | 126.8785 | 121.5688 | 24.9091
166.176 | 524.8124 | 127.853 | 122.3591 | 24.9872
167.176 | 524.6728 | 128.8424 | 123.3504 | 25.0693
168.176 | 524.6823 | 129.6556 | 124.0757 | 25.1484
169.176 | 524.6433 | 130.5098 | 125.0125 | 25.241
170.176 | 524.64 | 131.3618 | 125.9459 | 25.3271
171.176 | 524.5674 | 132.2575 | 126.5846 | 25.4106
172.176 | 524.622 | 133.2876 | 127.3333 | 25.51
173.176 | 524.667 | 134.2401 | 128.0978 | 25.6022
174.176 | 524.8167 | 135.2083 | 128.9398 | 25.7045
175.176 | 524.7461 | 136.1699 | 129.8378 | 25.7989
176.176 | 524.7423 | 137.0688 | 130.591 | 25.8996
177.176 | 524.8299 | 138.0273 | 131.4033 | 26.014
178.176 | 524.9714 | 138.8912 | 132.2116 | 26.1102
179.176 | 525.0045 | 139.815 | 133.1436 | 26.2163
180.176 | 525.0017 | 140.6625 | 133.9124 | 26.3205
181.176 | 525.1132 | 141.4791 | 134.7663 | 26.4291
182.176 | 525.1885 | 142.2993 | 135.6065 | 26.5434
183.176 | 525.3756 | 143.1831 | 136.4611 | 26.6557
184.176 | 525.5003 | 144.0352 | 137.3067 | 26.7758
185.176 | 525.4028 | 144.8696 | 137.9935 | 26.877
186.176 | 525.386 | 145.724 | 138.9557 | 27.0003
187.176 | 525.5507 | 146.6582 | 139.906 | 27.1182
188.176 | 525.4471 | 147.4595 | 140.7013 | 27.2428
189.176 | 525.5185 | 148.2311 | 141.4807 | 27.3701
190.176 | 525.5401 | 149.1066 | 142.3423 | 27.4885
191.176 | 525.3238 | 149.9489 | 143.0798 | 27.6186
192.176 | 525.127 | 150.7022 | 143.9545 | 27.7483
193.176 | 524.9805 | 151.5367 | 144.7788 | 27.8795
194.176 | 525.0822 | 152.423 | 145.6284 | 28.0142
195.176 | 525.1346 | 153.3062 | 146.3611 | 28.1471
196.176 | 525.0054 | 154.1598 | 146.9989 | 28.2926
197.176 | 525.1429 | 155.0785 | 147.7988 | 28.4234
198.176 | 525.3504 | 155.932 | 148.604 | 28.5668
199.176 | 525.3846 | 156.7076 | 149.3766 | 28.7067
200.176 | 525.3935 | 157.5501 | 150.1621 | 28.8503
201.176 | 525.4567 | 158.4139 | 151.0855 | 29.001
202.176 | 525.3701 | 159.303 | 151.8739 | 29.1436
203.176 | 525.3965 | 160.1806 | 152.6476 | 29.289
204.176 | 525.4334 | 161.0067 | 153.475 | 29.4502
205.176 | 525.4514 | 161.778 | 154.2539 | 29.6033
206.176 | 525.3262 | 162.5807 | 155.1127 | 29.7609
207.176 | 525.3936 | 163.3818 | 155.8248 | 29.9151
208.176 | 525.3607 | 164.2535 | 156.6132 | 30.0739
209.176 | 525.1718 | 165.138 | 157.2921 | 30.2374
210.176 | 525.1235 | 165.902 | 157.905 | 30.3991
211.176 | 525.3894 | 166.6136 | 158.6425 | 30.5639
212.176 | 525.4047 | 167.4425 | 159.4658 | 30.7328
213.176 | 525.3637 | 168.2475 | 160.3301 | 30.8938
214.176 | 525.4024 | 169.1138 | 161.118 | 31.0671
215.176 | 525.5826 | 169.895 | 161.9099 | 31.2344
216.176 | 525.4945 | 170.5618 | 162.6392 | 31.413
217.176 | 525.5455 | 171.2885 | 163.358 | 31.5868
218.176 | 525.5372 | 172.142 | 164.1517 | 31.7674
219.176 | 525.4488 | 172.9709 | 164.9145 | 31.9454
220.176 | 525.3659 | 173.7091 | 165.7409 | 32.1204
221.176 | 525.2993 | 174.445 | 166.4586 | 32.3122
222.176 | 525.2646 | 175.2561 | 167.1062 | 32.4895
223.176 | 525.3081 | 176.0399 | 167.7751 | 32.6763
224.176 | 525.1701 | 176.9324 | 168.4784 | 32.8595
225.176 | 525.2002 | 177.6272 | 169.1948 | 33.0579
226.176 | 525.3319 | 178.427 | 169.9056 | 33.2361
227.176 | 525.5183 | 179.438 | 170.6807 | 33.4288
228.176 | 525.708 | 180.1395 | 171.4699 | 33.6194
229.176 | 525.7047 | 180.8863 | 172.2638 | 33.8226
230.176 | 525.7918 | 181.6494 | 172.9694 | 34.0153
231.176 | 525.8118 | 182.3823 | 173.667 | 34.2155
232.176 | 525.8681 | 183.0828 | 174.3587 | 34.4074
233.176 | 525.9839 | 183.7838 | 175.0879 | 34.6176
234.176 | 525.9476 | 184.5593 | 175.8692 | 34.8178
235.176 | 526.0202 | 185.3076 | 176.5986 | 35.0235
236.176 | 525.9519 | 186.0154 | 177.2524 | 35.2216
237.176 | 525.8385 | 186.783 | 177.9517 | 35.4323
238.176 | 525.7535 | 187.5436 | 178.6978 | 35.653
239.176 | 525.7044 | 188.3167 | 179.4832 | 35.8625
240.176 | 525.7159 | 189.1081 | 180.1724 | 36.072
241.176 | 525.5912 | 189.8425 | 180.8795 | 36.2782
242.176 | 525.6722 | 190.6263 | 181.5668 | 36.4958
243.176 | 525.6146 | 191.3533 | 182.3089 | 36.7092
244.176 | 525.849 | 192.0981 | 182.9968 | 36.9221
245.176 | 526.1165 | 192.8276 | 183.6883 | 37.1423
246.176 | 526.0669 | 193.5155 | 184.408 | 37.357
247.176 | 526.0077 | 194.2715 | 185.1094 | 37.574
248.176 | 526.0119 | 194.9883 | 185.7898 | 37.7956
249.176 | 526.1255 | 195.6947 | 186.499 | 38.0096
250.176 | 526.1749 | 196.4244 | 187.152 | 38.2333
251.176 | 526.1429 | 197.1443 | 187.8009 | 38.4628
252.176 | 526.1549 | 197.9715 | 188.482 | 38.6872
253.176 | 526.0976 | 198.719 | 189.1859 | 38.9123
254.176 | 526.1863 | 199.3507 | 189.8488 | 39.1324
255.176 | 526.3216 | 200.0301 | 190.5129 | 39.361
256.176 | 526.4567 | 200.7526 | 191.2608 | 39.5811
257.176 | 526.3616 | 201.4255 | 191.929 | 39.8073
258.176 | 526.2117 | 202.105 | 192.5639 | 40.0399
259.176 | 526.2738 | 202.7894 | 193.2366 | 40.2654
260.176 | 526.1921 | 203.468 | 193.8946 | 40.49
261.176 | 526.0224 | 204.2119 | 194.5516 | 40.7212
262.176 | 525.9571 | 204.8877 | 195.1797 | 40.9474
263.176 | 525.9531 | 205.6325 | 195.8355 | 41.1761
264.176 | 525.8506 | 206.2883 | 196.4857 | 41.4201
265.176 | 525.8429 | 206.9816 | 197.142 | 41.6533
266.176 | 525.8763 | 207.6773 | 197.7853 | 41.8771
267.176 | 526.0235 | 208.3441 | 198.4376 | 42.1052
268.176 | 526.1702 | 209.0149 | 199.0875 | 42.3493
269.176 | 526.2505 | 209.6592 | 199.695 | 42.58
270.176 | 526.3488 | 210.2668 | 200.3412 | 42.8218
271.176 | 526.2864 | 210.9326 | 200.9784 | 43.0506
272.176 | 526.1808 | 211.5558 | 201.5943 | 43.28
273.176 | 526.0268 | 212.1574 | 202.2207 | 43.5243
274.176 | 525.7419 | 212.7115 | 202.8592 | 43.754
275.176 | 525.6369 | 213.3005 | 203.4741 | 43.9958
276.176 | 525.4144 | 213.928 | 204.1019 | 44.2348
277.176 | 525.3269 | 214.5615 | 204.7105 | 44.4681
278.176 | 525.3839 | 215.1637 | 205.3049 | 44.7122
279.176 | 525.3066 | 215.7118 | 205.9134 | 44.9544
280.176 | 525.3886 | 216.3927 | 206.5044 | 45.2071
281.176 | 525.5047 | 217.0086 | 207.1126 | 45.4489
282.1917 | 525.2782 | 217.6321 | 207.7121 | 45.696
283.176 | 525.1988 | 218.2336 | 208.3545 | 45.9363
284.176 | 525.2452 | 218.8526 | 208.9488 | 46.1807
285.176 | 525.3333 | 219.3964 | 209.5244 | 46.4297
286.176 | 525.5431 | 219.969 | 210.1174 | 46.6797
287.176 | 525.7388 | 220.5646 | 210.724 | 46.9306
288.176 | 525.9242 | 221.1311 | 211.294 | 47.1863
289.176 | 525.9508 | 221.7377 | 211.848 | 47.4327
290.176 | 525.8466 | 222.3043 | 212.4058 | 47.6923
291.176 | 525.6057 | 222.8874 | 212.9082 | 47.9446
292.176 | 525.6357 | 223.473 | 213.4319 | 48.2004
293.176 | 525.5915 | 224.0494 | 213.964 | 48.4633
294.176 | 525.7134 | 224.6551 | 214.4921 | 48.7237
295.176 | 525.6249 | 225.2093 | 215.0124 | 48.9924
296.176 | 525.662 | 225.8036 | 215.4892 | 49.2529
297.176 | 525.588 | 226.3594 | 215.9759 | 49.5262
298.176 | 525.6613 | 226.9708 | 216.4977 | 49.8047
299.176 | 525.8002 | 227.5918 | 217.0551 | 50.0755
300.176 | 525.8133 | 228.1565 | 217.5463 | 50.3642
301.176 | 526.019 | 228.7802 | 218.05 | 50.6429
302.176 | 526.1316 | 229.3967 | 218.5866 | 50.9322
303.176 | 526.1534 | 230.0669 | 219.0808 | 51.2133
304.176 | 526.3347 | 230.6817 | 219.6069 | 51.5148
305.176 | 526.4937 | 231.3268 | 220.0982 | 51.8145
306.176 | 526.3758 | 231.9503 | 220.5681 | 52.1184
307.176 | 526.3352 | 232.5618 | 221.0519 | 52.4323
308.176 | 526.2615 | 233.1581 | 221.5575 | 52.7433
309.176 | 526.2131 | 233.7691 | 222.0497 | 53.0641
310.176 | 526.1126 | 234.3585 | 222.5236 | 53.4033
311.176 | 526.0358 | 235.0332 | 222.9732 | 53.7416
312.1917 | 525.7822 | 235.6637 | 223.485 | 54.0756
313.176 | 525.6508 | 236.2928 | 223.9596 | 54.4197
314.176 | 525.5434 | 236.947 | 224.4796 | 54.7923
315.176 | 525.546 | 237.6106 | 224.9738 | 55.1471
316.176 | 525.6044 | 238.2123 | 225.4917 | 55.5186
317.176 | 525.7209 | 238.8617 | 225.9438 | 55.8889
318.176 | 525.4952 | 239.5321 | 226.4738 | 56.2667
319.176 | 525.5362 | 240.162 | 227.0118 | 56.6419
320.176 | 525.5365 | 240.8189 | 227.5363 | 57.0182
321.176 | 525.7387 | 241.4448 | 228.0497 | 57.3841
322.176 | 525.8951 | 242.0756 | 228.5528 | 57.7641
323.176 | 526.089 | 242.7626 | 229.1222 | 58.1467
324.176 | 526.2675 | 243.4209 | 229.6283 | 58.5312
325.176 | 526.2439 | 244.046 | 230.1309 | 58.9283
326.176 | 526.1905 | 244.6891 | 230.6523 | 59.3338
327.176 | 526.1541 | 245.3146 | 231.2083 | 59.7351
328.176 | 526.1362 | 245.9315 | 231.7419 | 60.1511
329.176 | 525.9043 | 246.6192 | 232.2375 | 60.5598
330.176 | 525.8234 | 247.2519 | 232.7894 | 60.9648
331.176 | 525.8435 | 247.8717 | 233.3776 | 61.36
332.176 | 525.9098 | 248.5405 | 233.9612 | 61.7488
333.176 | 526.0417 | 249.1696 | 234.5134 | 62.1304
334.176 | 526.0562 | 249.8076 | 235.1303 | 62.4996
335.176 | 525.9942 | 250.4472 | 235.7034 | 62.8673
336.176 | 525.8747 | 251.1345 | 236.3017 | 63.2176
337.176 | 525.9142 | 251.7534 | 236.9511 | 63.5695
338.176 | 525.9894 | 252.405 | 237.6108 | 63.8981
339.176 | 526.1613 | 253.0547 | 238.1976 | 64.2496
340.176 | 526.319 | 253.7137 | 238.8128 | 64.5666
341.176 | 526.4751 | 254.3243 | 239.4208 | 64.8774
342.176 | 526.5139 | 254.9213 | 239.9971 | 65.1889
343.176 | 526.4266 | 255.5525 | 240.5645 | 65.4888
344.176 | 526.4699 | 256.2115 | 241.1847 | 65.7804
345.176 | 526.6029 | 256.8242 | 241.7717 | 66.0526
346.176 | 526.6947 | 257.457 | 242.3388 | 66.3281
347.176 | 526.6834 | 258.0797 | 242.9216 | 66.5957
348.176 | 526.6789 | 258.7227 | 243.4837 | 66.8541
349.176 | 526.6309 | 259.2952 | 244.025 | 67.109
350.176 | 526.4904 | 259.8791 | 244.5707 | 67.3455
351.176 | 526.2124 | 260.4423 | 245.242 | 67.5972
352.176 | 526.1814 | 261.0401 | 245.7232 | 67.8205
353.176 | 526.1744 | 261.6685 | 246.3207 | 68.0486
354.176 | 526.121 | 262.2732 | 246.8357 | 68.2741
355.176 | 525.8802 | 262.8613 | 247.4212 | 68.4927
356.176 | 525.612 | 263.446 | 248.0498 | 68.7013
357.176 | 525.6408 | 264.0279 | 248.5959 | 68.9106
358.176 | 525.7417 | 264.6378 | 249.1859 | 69.1129
359.176 | 525.927 | 265.2103 | 249.7276 | 69.3192
360.176 | 525.8685 | 265.8838 | 250.3247 | 69.5142
361.176 | 525.8452 | 266.4392 | 250.9268 | 69.7025
362.176 | 525.8883 | 266.993 | 251.476 | 69.9014
363.176 | 525.9281 | 267.5724 | 252.0093 | 70.0885
364.176 | 525.8854 | 268.1535 | 252.5784 | 70.2745
365.176 | 525.8271 | 268.7208 | 253.1334 | 70.4515
366.176 | 525.8019 | 269.27 | 253.7273 | 70.6362
367.176 | 525.7602 | 269.7743 | 254.3606 | 70.8118
368.176 | 525.8095 | 270.3558 | 254.8909 | 70.9834
369.176 | 525.6001 | 270.9426 | 255.5402 | 71.1583
370.176 | 525.5137 | 271.5357 | 256.0677 | 71.3315
371.176 | 525.5214 | 272.1002 | 256.5756 | 71.5016
372.176 | 525.3325 | 272.5945 | 257.0428 | 71.6624
373.176 | 525.268 | 273.109 | 257.5379 | 71.8266
374.176 | 525.3968 | 273.7548 | 258.1179 | 71.9904
375.176 | 525.5171 | 274.3314 | 258.6857 | 72.153
376.176 | 525.5771 | 274.9075 | 259.2151 | 72.315
377.176 | 525.5951 | 275.4419 | 259.7234 | 72.4711
378.176 | 525.6991 | 276.0527 | 260.3335 | 72.6264
379.176 | 525.7529 | 276.6108 | 260.8203 | 72.7846
380.176 | 525.8916 | 277.1306 | 261.358 | 72.9373
381.176 | 525.9256 | 277.7025 | 261.8329 | 73.09
382.176 | 525.8604 | 278.2636 | 262.3754 | 73.2327
383.176 | 525.7424 | 278.8689 | 262.7721 | 73.3864
384.176 | 525.6658 | 279.4176 | 263.315 | 73.5423
385.176 | 525.7082 | 280.0012 | 263.9887 | 73.6906
386.176 | 525.8822 | 280.5428 | 264.6186 | 73.8318
387.176 | 526.0182 | 281.0443 | 265.2072 | 73.9673
388.176 | 526.0298 | 281.6582 | 265.7781 | 74.1162
389.176 | 526.0541 | 282.1967 | 266.3316 | 74.2567
390.176 | 525.8694 | 282.7601 | 266.832 | 74.3957
391.176 | 525.9632 | 283.3237 | 267.2897 | 74.532
392.176 | 526.1071 | 283.7714 | 267.6682 | 74.663
393.176 | 526.2512 | 284.3546 | 268.0415 | 74.7991
394.176 | 526.3301 | 284.9553 | 268.5717 | 74.9308
395.176 | 526.3788 | 285.5088 | 269.0665 | 75.0503
396.176 | 526.3793 | 286.1054 | 269.513 | 75.1874
397.176 | 526.4543 | 286.6786 | 269.8893 | 75.3127
398.176 | 526.4581 | 287.2569 | 270.43 | 75.4434
399.176 | 526.491 | 287.8096 | 270.9666 | 75.5661
400.176 | 526.4683 | 288.3543 | 271.5139 | 75.6923
401.176 | 526.4659 | 288.8667 | 271.8556 | 75.8143
402.176 | 526.2535 | 289.3962 | 272.2976 | 75.9305
403.176 | 526.2662 | 289.9689 | 272.7897 | 76.0485
404.176 | 526.3641 | 290.5203 | 273.4721 | 76.1708
405.176 | 526.4464 | 291.0266 | 274.0328 | 76.291
406.176 | 526.156 | 291.5972 | 274.4141 | 76.4082
407.176 | 526.1899 | 292.132 | 274.8266 | 76.5283
408.176 | 526.2682 | 292.686 | 275.2563 | 76.6522
409.176 | 526.274 | 293.2103 | 275.7414 | 76.7706
410.176 | 526.2043 | 293.7638 | 276.2391 | 76.8893
411.176 | 526.3074 | 294.3151 | 276.7318 | 77.0047
412.176 | 526.1026 | 294.8732 | 277.1681 | 77.1233
413.176 | 525.7649 | 295.442 | 277.6035 | 77.2463
414.176 | 525.6473 | 295.9617 | 278.0956 | 77.366
415.176 | 525.5392 | 296.538 | 278.5773 | 77.4823
416.176 | 525.5181 | 297.0549 | 279.1134 | 77.6001
417.176 | 525.4118 | 297.6059 | 279.5621 | 77.7226
418.176 | 525.4809 | 298.1401 | 280.0295 | 77.8503
419.176 | 525.4895 | 298.695 | 280.5983 | 77.9707
420.176 | 525.2664 | 299.2234 | 281.0869 | 78.0875
421.176 | 525.2734 | 299.7379 | 281.4512 | 78.2214
422.176 | 525.2507 | 300.2075 | 281.9947 | 78.3415
423.176 | 525.3245 | 300.7309 | 282.4229 | 78.4675
424.176 | 525.4054 | 301.2731 | 282.7855 | 78.5941
425.176 | 525.571 | 301.8206 | 283.2689 | 78.7178
426.176 | 525.6976 | 302.3701 | 283.7097 | 78.8477
427.176 | 525.7349 | 302.8849 | 284.3177 | 78.9849
428.176 | 525.8474 | 303.4269 | 284.8747 | 79.1209
429.176 | 525.9874 | 303.9962 | 285.2371 | 79.2487
430.176 | 526.1711 | 304.5432 | 285.4967 | 79.3883
431.176 | 526.3057 | 305.0685 | 285.9862 | 79.5258
432.176 | 526.5118 | 305.5929 | 286.7041 | 79.6618
433.176 | 526.5033 | 306.1543 | 287.1483 | 79.8011
434.176 | 526.4898 | 306.6604 | 287.7493 | 79.9406
435.176 | 526.4974 | 307.0926 | 288.3195 | 80.0886
436.176 | 526.529 | 307.6697 | 288.918 | 80.2319
437.176 | 526.3351 | 308.2089 | 289.2193 | 80.3777
438.176 | 526.3341 | 308.7343 | 289.4661 | 80.5276
439.176 | 526.3461 | 309.2832 | 289.7752 | 80.6666
440.176 | 526.2998 | 309.774 | 290.1882 | 80.8247
441.176 | 526.238 | 310.2933 | 290.7709 | 80.9712
442.176 | 526.2178 | 310.8027 | 291.2046 | 81.1232
443.176 | 526.1973 | 311.3127 | 291.6182 | 81.2788
444.176 | 526.1717 | 311.8455 | 292.1168 | 81.4331
445.176 | 526.2641 | 312.3627 | 292.6514 | 81.5835
446.176 | 526.2448 | 312.9143 | 293.1394 | 81.734
447.176 | 526.3076 | 313.4049 | 293.442 | 81.8852
448.176 | 526.4546 | 313.9499 | 293.8805 | 82.0408
449.176 | 526.4313 | 314.4896 | 294.4968 | 82.188
450.176 | 526.3466 | 315.0177 | 295.0554 | 82.3474
451.176 | 526.4553 | 315.4819 | 295.4269 | 82.503
452.176 | 526.4539 | 316.0099 | 296.003 | 82.6621
453.176 | 526.3982 | 316.5587 | 296.6422 | 82.8255
454.176 | 526.4304 | 317.0483 | 296.919 | 82.9808
455.176 | 526.4478 | 317.5611 | 297.2983 | 83.1308
456.176 | 526.4309 | 318.0553 | 297.797 | 83.2886
457.176 | 526.2734 | 318.5632 | 298.2513 | 83.4534
458.176 | 526.3024 | 319.0444 | 298.6106 | 83.6099
459.176 | 526.3395 | 319.5271 | 299.0491 | 83.773
460.176 | 526.2938 | 320.0575 | 299.4756 | 83.9333
461.176 | 526.2184 | 320.5629 | 299.8544 | 84.0892
462.176 | 526.2401 | 321.0566 | 300.2116 | 84.2515
463.176 | 526.2945 | 321.5766 | 300.8544 | 84.4067
464.176 | 526.3607 | 322.0916 | 301.3091 | 84.5641
465.176 | 526.2916 | 322.5179 | 301.8138 | 84.7231
466.176 | 526.2205 | 323.0132 | 302.3678 | 84.8852
467.176 | 526.2394 | 323.4903 | 302.7932 | 85.0359
468.176 | 526.0703 | 323.9858 | 303.2708 | 85.1946
469.176 | 526.0419 | 324.4712 | 303.6569 | 85.3532
470.176 | 526.022 | 324.9279 | 304.1541 | 85.5078
471.176 | 525.9045 | 325.4007 | 304.6751 | 85.6637
472.176 | 525.8645 | 325.9145 | 305.0148 | 85.8188
473.176 | 525.9869 | 326.3975 | 305.4538 | 85.9797
474.176 | 526.2621 | 326.8385 | 305.9942 | 86.1438
475.176 | 526.4326 | 327.3394 | 306.3869 | 86.3082
476.176 | 526.5184 | 327.8623 | 306.6649 | 86.4635
477.176 | 526.5878 | 328.3692 | 307.0449 | 86.6203
478.176 | 526.7237 | 328.8852 | 307.5891 | 86.7807
479.176 | 526.6367 | 329.3886 | 307.8106 | 86.94
480.176 | 526.535 | 329.8604 | 308.2629 | 87.1059
481.176 | 526.4756 | 330.2837 | 308.809 | 87.2715
482.176 | 526.3248 | 330.7658 | 309.2419 | 87.427
483.176 | 526.4044 | 331.2369 | 309.6705 | 87.5917
484.176 | 526.3546 | 331.7285 | 309.9977 | 87.7524
485.176 | 526.3307 | 332.2308 | 310.3801 | 87.9084
486.176 | 526.2228 | 332.6861 | 311.0329 | 88.075
487.176 | 526.1526 | 333.0814 | 311.5147 | 88.2339
488.176 | 525.9714 | 333.5833 | 311.9938 | 88.3976
489.176 | 525.9682 | 334.0304 | 312.3777 | 88.5529
490.176 | 525.9446 | 334.5182 | 312.7953 | 88.7189
491.176 | 525.903 | 335.0401 | 313.169 | 88.8758
492.176 | 526.0132 | 335.4858 | 313.681 | 89.0399
493.176 | 525.905 | 335.9474 | 314.0862 | 89.1962
494.176 | 525.8654 | 336.4322 | 314.3545 | 89.3583
495.176 | 526.0659 | 336.8521 | 314.8671 | 89.5274
496.176 | 526.2881 | 337.3153 | 315.4802 | 89.6856
497.176 | 526.4769 | 337.8161 | 316.0202 | 89.8479
498.176 | 526.6686 | 338.2555 | 316.5202 | 90.0094
499.176 | 526.9047 | 338.7372 | 316.7794 | 90.1706
500.176 | 527.0039 | 339.1991 | 317.0861 | 90.3284
501.176 | 527.0179 | 339.6428 | 317.5517 | 90.5007
502.176 | 527.0757 | 340.1329 | 317.8074 | 90.6655
503.176 | 527.1364 | 340.6217 | 318.1357 | 90.8233
504.176 | 527.1274 | 341.0554 | 318.4424 | 90.9871
505.176 | 526.9226 | 341.4769 | 318.9185 | 91.1578
506.176 | 526.8728 | 341.8878 | 319.2783 | 91.3191
507.176 | 526.7883 | 342.3621 | 319.7148 | 91.48
508.176 | 526.6843 | 342.8316 | 320.1817 | 91.6447
509.176 | 526.5603 | 343.2492 | 320.8283 | 91.8119
510.176 | 526.4062 | 343.6642 | 321.2183 | 91.9783
511.176 | 526.2738 | 344.083 | 321.4896 | 92.1576
512.176 | 526.2336 | 344.5466 | 321.9734 | 92.324
513.176 | 526.2186 | 344.9389 | 322.5034 | 92.4901
514.176 | 526.225 | 345.4374 | 323.0552 | 92.652
515.176 | 526.2734 | 345.9096 | 323.5624 | 92.8179
516.176 | 526.189 | 346.343 | 323.9582 | 92.9881
517.176 | 526.2528 | 346.796 | 324.3504 | 93.1585
518.176 | 526.2697 | 347.2212 | 324.8033 | 93.3262
519.176 | 526.1515 | 347.6755 | 325.3134 | 93.4983
520.176 | 526.2871 | 348.0851 | 325.4935 | 93.6715
521.176 | 526.4047 | 348.5343 | 325.7579 | 93.8371
522.176 | 526.6004 | 348.9506 | 326.344 | 94.0134
523.176 | 526.6401 | 349.306 | 326.8756 | 94.1881
524.176 | 526.6507 | 349.7654 | 327.311 | 94.3683
525.176 | 526.7155 | 350.2472 | 327.8813 | 94.5364
526.176 | 526.8212 | 350.7222 | 328.1949 | 94.7138
527.176 | 526.7962 | 351.1547 | 328.5029 | 94.895
528.176 | 526.8698 | 351.5808 | 329.0277 | 95.0663
529.176 | 526.8295 | 351.9819 | 329.2957 | 95.2425
530.176 | 526.7335 | 352.4072 | 329.5607 | 95.4234
531.176 | 526.729 | 352.8174 | 329.8658 | 95.5961
532.176 | 526.7723 | 353.2491 | 330.3797 | 95.7778
533.176 | 526.7427 | 353.6875 | 330.8986 | 95.9567
534.176 | 526.8102 | 354.0587 | 331.1665 | 96.1383
535.176 | 526.7843 | 354.5342 | 331.5878 | 96.317
536.176 | 526.7246 | 354.963 | 332.1226 | 96.4907
537.176 | 526.6703 | 355.3251 | 332.605 | 96.6696
538.176 | 526.6349 | 355.748 | 332.8367 | 96.8585
539.176 | 526.4301 | 356.1614 | 333.0886 | 97.0483
540.176 | 526.2652 | 356.5859 | 333.3788 | 97.2164
541.176 | 526.0078 | 357.0318 | 333.6472 | 97.3978
542.176 | 526.0143 | 357.4688 | 334.192 | 97.5808
543.176 | 525.9665 | 357.8629 | 334.7438 | 97.7622
544.176 | 525.9454 | 358.2885 | 335.2638 | 97.9393
545.176 | 525.9958 | 358.7114 | 335.798 | 98.1173
546.176 | 526.1817 | 359.1518 | 336.3138 | 98.2961
547.176 | 526.2671 | 359.5124 | 336.7463 | 98.4739
548.176 | 526.1068 | 359.9078 | 336.8713 | 98.6486
549.176 | 526.214 | 360.2938 | 337.2889 | 98.8228
550.176 | 526.5514 | 360.765 | 337.6192 | 98.9958
551.176 | 526.6163 | 361.2077 | 338.1736 | 99.17
552.176 | 526.8089 | 361.6614 | 338.3269 | 99.3412
553.176 | 526.707 | 361.9789 | 338.5142 | 99.512
554.176 | 526.7921 | 362.3813 | 338.9016 | 99.68
555.176 | 526.955 | 362.875 | 339.2416 | 99.8502
556.176 | 527.0822 | 363.3225 | 339.568 | 100.0035
557.176 | 527.1966 | 363.7777 | 339.9144 | 100.1727
558.176 | 527.3259 | 364.1896 | 340.4108 | 100.3203
559.176 | 527.3313 | 364.5757 | 340.8295 | 100.4779
560.176 | 527.2066 | 365.0078 | 341.3067 | 100.6321
561.176 | 527.1034 | 365.4159 | 341.5673 | 100.7863
562.176 | 526.8061 | 365.8234 | 341.8732 | 100.9352
563.176 | 526.6261 | 366.2225 | 342.3241 | 101.0871
564.176 | 526.5955 | 366.6275 | 342.5698 | 101.233
565.176 | 526.445 | 367.0085 | 342.7777 | 101.375
566.176 | 526.4173 | 367.3464 | 343.2043 | 101.5234
567.176 | 526.3849 | 367.8024 | 343.6491 | 101.6762
568.176 | 526.1413 | 368.1959 | 343.8678 | 101.8198
569.176 | 526.0277 | 368.5983 | 344.3325 | 101.9635
570.176 | 525.9648 | 368.9983 | 344.7465 | 102.1099
571.176 | 525.7936 | 369.3227 | 345.1231 | 102.253
572.176 | 525.7347 | 369.6873 | 345.437 | 102.4067
573.176 | 525.8047 | 370.0368 | 345.7135 | 102.5659
574.176 | 525.7022 | 370.4315 | 346.1968 | 102.7193
575.176 | 525.4649 | 370.869 | 346.7678 | 102.8813
576.176 | 525.2949 | 371.2683 | 347.1146 | 103.0511
577.176 | 525.2252 | 371.6085 | 347.6774 | 103.2295
578.176 | 525.0664 | 371.9719 | 348.0266 | 103.4195
579.176 | 525.0761 | 372.361 | 348.1506 | 103.6122
580.176 | 525.0524 | 372.7548 | 348.3552 | 103.8157
581.176 | 525.2014 | 373.1121 | 348.8208 | 104.0192
582.176 | 525.1281 | 373.4111 | 349.1104 | 104.2485
583.176 | 525.2232 | 373.7437 | 349.5489 | 104.4691
584.176 | 525.3345 | 374.1054 | 349.9808 | 104.6964
585.176 | 525.4255 | 374.3944 | 350.3776 | 104.9399
586.176 | 525.3785 | 374.7822 | 350.9177 | 105.1731
587.176 | 525.3132 | 375.0499 | 351.3663 | 105.4075
588.176 | 525.2586 | 375.5168 | 351.6275 | 105.6454
589.176 | 525.2 | 375.942 | 351.7266 | 105.8863
590.176 | 525.1143 | 376.2909 | 352.1216 | 106.1215
591.176 | 525.2018 | 376.6925 | 352.6141 | 106.3703
592.176 | 525.3662 | 377.0919 | 353.16 | 106.6085
593.176 | 525.4486 | 377.4427 | 353.3828 | 106.8522
594.176 | 525.4598 | 377.8283 | 353.4318 | 107.1014
595.176 | 525.4663 | 378.1915 | 353.7712 | 107.3503
596.176 | 525.5562 | 378.5635 | 354.0963 | 107.6054
597.176 | 525.7282 | 378.9198 | 354.6562 | 107.8606
598.176 | 525.7559 | 379.2887 | 355.2102 | 108.1199
599.176 | 525.6952 | 379.6877 | 355.4106 | 108.3768
600.176 | 525.7407 | 380.0131 | 355.8355 | 108.6346
601.176 | 525.9503 | 380.3527 | 356.0514 | 108.8986
602.176 | 526.1513 | 380.6842 | 356.3649 | 109.1681
603.176 | 526.4021 | 380.9908 | 356.8084 | 109.4399
604.176 | 526.4469 | 381.3481 | 357.3043 | 109.7125
605.176 | 526.5101 | 381.7956 | 357.3295 | 109.9992
606.176 | 526.4405 | 382.1714 | 357.4621 | 110.2743
607.176 | 526.3369 | 382.5354 | 357.9642 | 110.5561
608.176 | 526.1485 | 382.9218 | 358.311 | 110.8477
609.176 | 526.0911 | 383.1888 | 358.4507 | 111.1571
610.176 | 525.8771 | 383.6147 | 358.6572 | 111.4546
611.176 | 525.9115 | 383.9819 | 358.9937 | 111.7573
612.176 | 526.0031 | 384.3258 | 359.3334 | 112.0723
613.176 | 526.0449 | 384.4745 | 359.684 | 112.3918
614.176 | 526.1794 | 384.8764 | 359.984 | 112.7187
615.176 | 526.3421 | 385.2835 | 360.1406 | 113.0607
616.176 | 526.4264 | 385.611 | 360.6133 | 113.4003
617.176 | 526.415 | 386.0375 | 361.0134 | 113.7573
618.176 | 526.4865 | 386.4173 | 361.2087 | 114.1201
619.176 | 526.5191 | 386.7296 | 361.2737 | 114.4817
620.176 | 526.4547 | 387.0447 | 361.7359 | 114.8621
621.176 | 526.4986 | 387.4166 | 362.1911 | 115.2565
622.176 | 526.4972 | 387.7715 | 362.7624 | 115.6548
623.176 | 526.4099 | 388.0629 | 362.9307 | 116.0649
624.176 | 526.3478 | 388.4092 | 363.0649 | 116.4963
625.176 | 526.2537 | 388.7868 | 363.2775 | 116.9327
626.176 | 526.1348 | 389.1124 | 363.7723 | 117.3895
627.176 | 525.9799 | 389.4732 | 364.0102 | 117.8634
628.176 | 525.6759 | 389.8238 | 364.5014 | 118.3657
629.176 | 525.6427 | 390.1494 | 364.7526 | 118.8716
630.176 | 525.63 | 390.5221 | 365.0298 | 119.3973
631.176 | 525.7245 | 390.8418 | 365.3698 | 119.9335
632.176 | 525.669 | 391.0948 | 365.5788 | 120.4761
633.176 | 525.5974 | 391.3876 | 365.6124 | 121.0384
634.176 | 525.5964 | 391.7562 | 365.9897 | 121.5767
635.176 | 525.4525 | 392.114 | 366.201 | 122.1245
636.176 | 525.3994 | 392.4559 | 366.4239 | 122.6802
637.176 | 525.2597 | 392.7751 | 366.7548 | 123.2236
638.176 | 525.3318 | 393.0577 | 367.2111 | 123.7664
639.176 | 525.4007 | 393.3693 | 367.7807 | 124.3079
640.176 | 525.4304 | 393.5781 | 367.9956 | 124.8474
641.176 | 525.2167 | 393.8834 | 368.5085 | 125.3809
642.176 | 525.2107 | 394.2778 | 368.9794 | 125.9161
643.176 | 525.1389 | 394.5852 | 369.4535 | 126.44
644.176 | 525.2102 | 394.8953 | 369.6447 | 126.9711
645.176 | 525.2537 | 395.2627 | 369.8966 | 127.4881
646.176 | 525.193 | 395.5677 | 370.3365 | 128.008
647.176 | 525.2494 | 395.9057 | 370.6314 | 128.5416
648.176 | 525.4315 | 396.1597 | 370.6326 | 129.0602
649.176 | 525.4138 | 396.4977 | 370.9948 | 129.5762
650.176 | 525.446 | 396.828 | 371.4079 | 130.0886
651.176 | 525.3485 | 397.1776 | 371.5519 | 130.6168
652.176 | 525.4311 | 397.5112 | 371.804 | 131.1242
653.176 | 525.4456 | 397.8449 | 371.9831 | 131.6437
654.176 | 525.3826 | 398.1499 | 372.2795 | 132.1439
655.176 | 525.252 | 398.4117 | 372.4755 | 132.6526
656.176 | 525.3365 | 398.6967 | 372.748 | 133.1519
657.176 | 525.4953 | 399.0185 | 372.9094 | 133.657
658.176 | 525.4087 | 399.3506 | 373.3465 | 134.1609
659.176 | 525.4479 | 399.6035 | 373.8369 | 134.6686
660.176 | 525.624 | 399.9391 | 374.2435 | 135.1589
661.176 | 525.6527 | 400.1975 | 374.4912 | 135.6592
662.176 | 525.7231 | 400.3989 | 374.7353 | 136.1495
663.176 | 525.8178 | 400.8102 | 374.9663 | 136.6493
664.176 | 525.895 | 401.1205 | 375.2017 | 137.1496
665.176 | 525.9564 | 401.4635 | 375.4803 | 137.6393
666.176 | 526.0331 | 401.8129 | 375.7788 | 138.1394
667.176 | 525.9199 | 402.1222 | 375.838 | 138.6281
668.176 | 525.7739 | 402.3178 | 376.3906 | 139.1159
669.176 | 525.6892 | 402.5613 | 376.821 | 139.6064
670.176 | 525.5691 | 402.8456 | 377.1614 | 140.1098
671.176 | 525.5839 | 403.1689 | 377.5012 | 140.5924
672.176 | 525.5885 | 403.4763 | 377.6475 | 141.0777
673.176 | 525.5784 | 403.8192 | 377.9913 | 141.5568
674.176 | 525.644 | 404.0834 | 378.3125 | 142.0505
675.176 | 525.5598 | 404.3901 | 378.6343 | 142.5355
676.176 | 525.5855 | 404.6643 | 378.5355 | 143.0082
677.176 | 525.49 | 404.9812 | 378.4442 | 143.5012
678.176 | 525.4668 | 405.2341 | 378.8175 | 143.9757
679.176 | 525.3846 | 405.5583 | 379.0512 | 144.4537
680.176 | 525.4087 | 405.7833 | 379.588 | 144.9314
681.176 | 525.338 | 406.0873 | 379.8842 | 145.4101
682.176 | 525.2209 | 406.4383 | 380.3197 | 145.8797
683.176 | 525.2136 | 406.6292 | 380.515 | 146.3626
684.176 | 525.0524 | 407.0082 | 381.0342 | 146.8307
685.176 | 524.9337 | 407.3639 | 381.1105 | 147.3122
686.176 | 525.0089 | 407.6827 | 381.5512 | 147.7874
687.176 | 525.1212 | 407.9498 | 381.7258 | 148.2595
688.176 | 524.9458 | 408.2401 | 381.9815 | 148.7253
689.176 | 524.776 | 408.5292 | 382.3664 | 149.2026
690.176 | 524.7848 | 408.755 | 382.8739 | 149.685
691.176 | 524.6389 | 409.0552 | 383.145 | 150.1513
692.176 | 524.5788 | 409.3351 | 383.3441 | 150.6173
693.176 | 524.551 | 409.5716 | 383.8159 | 151.0893
694.176 | 524.5046 | 409.8592 | 384.0605 | 151.556
695.176 | 524.5292 | 410.165 | 384.0506 | 152.0294
696.176 | 524.6381 | 410.4406 | 384.2128 | 152.4919
697.176 | 524.7196 | 410.7388 | 384.3489 | 152.9533
698.176 | 524.7407 | 410.98 | 384.4641 | 153.4241
699.176 | 524.603 | 411.2423 | 384.5001 | 153.8929
700.176 | 524.4967 | 411.438 | 384.5236 | 154.355
701.176 | 524.5438 | 411.6616 | 384.9733 | 154.8101
702.176 | 524.5158 | 411.8953 | 385.4291 | 155.2854
703.176 | 524.5974 | 412.2297 | 385.644 | 155.7381
704.176 | 524.7404 | 412.4527 | 386.0428 | 156.1954
705.176 | 524.8098 | 412.8095 | 386.619 | 156.667
706.176 | 524.9455 | 413.0495 | 386.813 | 157.1224
707.176 | 524.9184 | 413.2764 | 387.2707 | 157.5774
708.176 | 524.8874 | 413.5851 | 387.588 | 158.0482
709.176 | 524.9699 | 413.8305 | 387.8579 | 158.5036
710.176 | 525.1059 | 414.163 | 387.8258 | 158.9663
711.176 | 525.0768 | 414.4015 | 388.1355 | 159.4354
712.176 | 524.8963 | 414.7034 | 388.2895 | 159.8912
713.176 | 524.8487 | 414.9459 | 388.5976 | 160.3444
714.176 | 524.9042 | 415.2136 | 388.9735 | 160.803
715.176 | 524.9185 | 415.4531 | 389.3 | 161.2622
716.176 | 524.9878 | 415.7047 | 389.5607 | 161.7209
717.176 | 525.0674 | 415.9742 | 389.7725 | 162.1733
718.176 | 525.1099 | 416.13 | 389.9779 | 162.6334
719.176 | 525.2109 | 416.4442 | 389.9892 | 163.0946
720.176 | 525.354 | 416.6984 | 390.3104 | 163.5406
721.176 | 525.3843 | 416.954 | 390.4858 | 163.9962
722.176 | 525.4719 | 417.1974 | 390.7191 | 164.4454
723.176 | 525.6265 | 417.4679 | 391.0976 | 164.9051
724.176 | 525.7253 | 417.7597 | 391.2131 | 165.3599
725.176 | 525.6929 | 418.0284 | 391.4221 | 165.8073
726.176 | 525.7641 | 418.3218 | 391.614 | 166.2608
727.176 | 525.9179 | 418.5857 | 391.5272 | 166.7175
728.176 | 526.0015 | 418.8227 | 391.5718 | 167.1725
729.176 | 526.0065 | 419.0223 | 392.2132 | 167.6265
730.176 | 525.8714 | 419.3312 | 392.4002 | 168.0809
731.176 | 525.8226 | 419.5934 | 392.8126 | 168.5313
732.176 | 525.8757 | 419.8547 | 393.2054 | 169.0022
733.176 | 525.8056 | 420.0707 | 393.5124 | 169.4527
734.176 | 525.8775 | 420.1889 | 393.67 | 169.9043
735.176 | 525.7761 | 420.4417 | 394.0748 | 170.3566
736.176 | 525.6809 | 420.7385 | 394.3706 | 170.8109
737.176 | 525.6608 | 421.0061 | 394.5134 | 171.2583
738.176 | 525.7141 | 421.2289 | 394.7324 | 171.7156
739.176 | 525.6539 | 421.4841 | 394.9446 | 172.1704
740.176 | 525.7229 | 421.7251 | 395.3954 | 172.6102
741.176 | 525.758 | 422.0033 | 395.7254 | 173.07
742.176 | 525.6199 | 422.2813 | 395.7712 | 173.518
743.176 | 525.4801 | 422.5349 | 395.9764 | 173.9652
744.176 | 525.4281 | 422.8153 | 396.4102 | 174.4194
745.176 | 525.2191 | 423.0723 | 396.7094 | 174.8717
746.176 | 525.1436 | 423.3092 | 396.6694 | 175.3236
747.176 | 525.2017 | 423.556 | 396.7 | 175.7644
748.176 | 525.4196 | 423.8136 | 396.8744 | 176.2235
749.176 | 525.5512 | 423.9777 | 397.0231 | 176.6705
750.176 | 525.5898 | 424.2262 | 397.4579 | 177.121
751.176 | 525.6981 | 424.4775 | 398.0048 | 177.58
752.176 | 525.7221 | 424.6233 | 398.3428 | 178.0291
753.176 | 525.6962 | 424.8929 | 398.5495 | 178.4858
754.176 | 525.7513 | 425.1655 | 398.6442 | 178.9458
755.176 | 525.6545 | 425.405 | 398.8346 | 179.4008
756.176 | 525.8197 | 425.5442 | 398.9106 | 179.8489
757.176 | 525.8709 | 425.8693 | 399.3259 | 180.3019
758.176 | 526.0637 | 426.1882 | 399.5767 | 180.7545
759.176 | 526.0182 | 426.4908 | 399.7637 | 181.2029
760.176 | 525.8854 | 426.7261 | 399.8419 | 181.6545
761.176 | 525.9311 | 426.953 | 399.8722 | 182.1051
762.176 | 525.7619 | 427.1773 | 400.3312 | 182.5621
763.176 | 525.8436 | 427.4324 | 400.8174 | 183.0069
764.176 | 525.7057 | 427.5477 | 400.6807 | 183.4658
765.176 | 525.4819 | 427.6927 | 401.001 | 183.917
766.176 | 525.4599 | 427.9623 | 401.3402 | 184.3769
767.176 | 525.5832 | 428.1991 | 401.7874 | 184.8294
768.176 | 525.6095 | 428.3633 | 402.0508 | 185.2874
769.176 | 525.6157 | 428.6743 | 402.4394 | 185.7383
770.176 | 525.531 | 428.9492 | 402.4975 | 186.1954
771.176 | 525.4424 | 429.2349 | 402.6054 | 186.6499
772.176 | 525.3722 | 429.4021 | 402.3891 | 187.1129
773.176 | 525.5117 | 429.6672 | 402.766 | 187.568
774.176 | 525.5874 | 429.8928 | 403.3717 | 188.0162
775.176 | 525.6779 | 430.1809 | 403.2694 | 188.4815
776.176 | 525.7179 | 430.3612 | 403.5772 | 188.9445
777.176 | 525.775 | 430.5779 | 404.063 | 189.4012
778.176 | 525.7791 | 430.8318 | 404.2201 | 189.8638
779.176 | 525.7599 | 431.0797 | 404.1412 | 190.3143
780.176 | 525.6841 | 431.3121 | 404.0527 | 190.7732
781.176 | 525.5979 | 431.5201 | 404.1879 | 191.2336
782.176 | 525.5403 | 431.7337 | 404.4986 | 191.6874
783.176 | 525.6251 | 431.8588 | 404.9788 | 192.1392
784.176 | 525.5855 | 432.062 | 405.2589 | 192.5889
785.176 | 525.3728 | 432.2787 | 405.5591 | 193.0504
786.176 | 525.3745 | 432.5162 | 405.5968 | 193.4898
787.176 | 525.4837 | 432.7965 | 405.6052 | 193.9523
788.176 | 525.3448 | 432.9892 | 406.0342 | 194.4063
789.176 | 525.1188 | 433.1724 | 405.943 | 194.8589
790.176 | 525.0681 | 433.3505 | 406.293 | 195.303
791.176 | 524.9307 | 433.6539 | 406.4463 | 195.7631
792.176 | 525.0742 | 433.8022 | 406.4927 | 196.2065
793.176 | 525.2335 | 434.018 | 406.7816 | 196.6572
794.176 | 525.3668 | 434.2775 | 407.3008 | 197.1062
795.176 | 525.4283 | 434.4528 | 407.6211 | 197.5506
796.176 | 525.4703 | 434.6383 | 408.1154 | 197.9955
797.176 | 525.4743 | 434.8415 | 408.2746 | 198.4555
798.176 | 525.562 | 435.1367 | 408.2507 | 198.9016
799.176 | 525.5358 | 435.2477 | 408.2087 | 199.3454
800.176 | 525.6192 | 435.4842 | 408.2629 | 199.7916
801.176 | 525.5782 | 435.7255 | 408.3253 | 200.23
802.176 | 525.7175 | 435.9892 | 408.6841 | 200.6714
803.176 | 525.6949 | 436.2737 | 409.1396 | 201.1083
804.176 | 525.6367 | 436.4457 | 409.3889 | 201.5413
805.176 | 525.6669 | 436.5948 | 409.4033 | 201.9827
806.176 | 525.7838 | 436.7638 | 409.5893 | 202.4189
807.176 | 525.7474 | 436.9673 | 409.6898 | 202.8597
808.176 | 525.7851 | 437.253 | 410.0838 | 203.2895
809.176 | 525.8205 | 437.4852 | 410.4972 | 203.7257
810.176 | 525.7634 | 437.7226 | 410.8101 | 204.1525
811.176 | 525.8257 | 437.9174 | 411.0411 | 204.58
812.176 | 525.7294 | 438.1357 | 411.2514 | 205.0088
813.176 | 525.5796 | 438.2828 | 411.249 | 205.4329
814.176 | 525.7292 | 438.4767 | 411.485 | 205.8605
815.176 | 525.7348 | 438.7451 | 411.5492 | 206.2941
816.176 | 525.7759 | 438.8938 | 411.9259 | 206.7066
817.176 | 525.5842 | 439.1481 | 411.913 | 207.1359
818.176 | 525.5638 | 439.3005 | 412.3339 | 207.5487
819.176 | 525.3852 | 439.5662 | 412.4472 | 207.9693
820.176 | 525.1932 | 439.704 | 412.6959 | 208.3943
821.176 | 525.1435 | 439.9214 | 412.9638 | 208.802
822.176 | 525.2145 | 440.1448 | 413.1377 | 209.2151
823.176 | 525.1681 | 440.4011 | 413.5011 | 209.6273
824.176 | 525.2136 | 440.6331 | 413.835 | 210.0311
825.176 | 525.0287 | 440.8033 | 414.0089 | 210.4417
826.176 | 524.899 | 441.0013 | 413.9686 | 210.8487
827.176 | 524.821 | 441.1986 | 414.1399 | 211.2462
828.176 | 524.8455 | 441.3766 | 414.1224 | 211.6451
829.176 | 524.9338 | 441.507 | 414.1222 | 212.0479
830.176 | 525.1057 | 441.7085 | 414.1743 | 212.4415
831.176 | 525.254 | 441.9504 | 414.524 | 212.8258
832.176 | 525.4769 | 442.1962 | 415.1196 | 213.2145
833.176 | 525.5467 | 442.4334 | 415.3887 | 213.5986
834.176 | 525.5234 | 442.4487 | 415.643 | 213.987
835.176 | 525.5511 | 442.6507 | 415.7476 | 214.3764
836.176 | 525.4099 | 442.8734 | 415.637 | 214.7497
837.176 | 525.6069 | 443.1262 | 416.2182 | 215.1237
838.176 | 525.6505 | 443.3848 | 416.58 | 215.4997
839.176 | 525.694 | 443.558 | 416.594 | 215.8752
840.176 | 525.6484 | 443.696 | 416.7811 | 216.2414
841.176 | 525.5715 | 443.9334 | 416.9385 | 216.6169
842.176 | 525.7523 | 443.9625 | 417.0659 | 216.9816
843.176 | 525.6375 | 444.1253 | 417.2986 | 217.3414
844.176 | 525.5909 | 444.402 | 417.658 | 217.7087
845.176 | 525.5326 | 444.595 | 417.9348 | 218.0745
846.176 | 525.5742 | 444.8287 | 417.716 | 218.4239
847.176 | 525.4986 | 444.9565 | 417.8514 | 218.7769
848.176 | 525.5275 | 445.075 | 417.8506 | 219.1234
849.176 | 525.4702 | 445.2416 | 417.9257 | 219.4748
850.176 | 525.3977 | 445.4099 | 418.1528 | 219.8133
851.176 | 525.4441 | 445.6217 | 418.6269 | 220.164
852.176 | 525.4806 | 445.8117 | 418.8486 | 220.5003
853.176 | 525.5152 | 445.8821 | 418.9205 | 220.8361
854.176 | 525.5105 | 446.0063 | 419.0512 | 221.1683
855.176 | 525.6529 | 446.3052 | 419.11 | 221.508
856.176 | 525.6419 | 446.5095 | 419.4755 | 221.8394
857.176 | 525.7255 | 446.8104 | 419.6812 | 222.1753
858.176 | 525.8148 | 446.9907 | 419.7009 | 222.503
859.176 | 525.8051 | 447.191 | 419.7964 | 222.8392
860.176 | 525.804 | 447.3942 | 420.1383 | 223.1608
861.176 | 525.9183 | 447.5546 | 420.3093 | 223.4861
862.176 | 525.9724 | 447.7755 | 420.7669 | 223.8065
863.176 | 526.084 | 447.9657 | 421.0163 | 224.1298
864.176 | 525.8925 | 448.1144 | 420.9794 | 224.451
865.176 | 525.8625 | 448.2813 | 421.29 | 224.7761
866.176 | 525.9332 | 448.3984 | 421.3353 | 225.0946
867.176 | 525.9093 | 448.561 | 421.4821 | 225.4095
868.176 | 525.9635 | 448.7371 | 421.2511 | 225.7206
869.176 | 525.8283 | 448.8038 | 421.3534 | 226.0376
870.176 | 525.7344 | 448.9889 | 421.8124 | 226.3441
871.176 | 525.5815 | 449.1461 | 422.2762 | 226.6569
872.176 | 525.7316 | 449.3773 | 422.6131 | 226.974
873.176 | 525.7949 | 449.5688 | 422.7099 | 227.2775
874.176 | 525.7784 | 449.8085 | 422.8348 | 227.5972
875.176 | 525.761 | 450.0063 | 423.0842 | 227.9061
876.176 | 525.8345 | 450.1529 | 423.3499 | 228.2069
877.176 | 525.8685 | 450.3506 | 423.6097 | 228.5089
878.176 | 525.8063 | 450.4979 | 423.5976 | 228.8104
879.176 | 525.8471 | 450.6122 | 423.642 | 229.1161
880.176 | 525.7496 | 450.733 | 423.8914 | 229.4158
881.176 | 525.7896 | 450.8714 | 424.2072 | 229.7123
882.176 | 525.9173 | 451.078 | 424.4803 | 230.0143
883.176 | 525.9702 | 451.3388 | 424.656 | 230.3143
884.176 | 525.8834 | 451.4368 | 425.0549 | 230.6074
885.176 | 525.7774 | 451.6204 | 425.2464 | 230.9009
886.176 | 525.9226 | 451.8052 | 425.3355 | 231.1915
887.176 | 525.9166 | 452.0428 | 425.6192 | 231.4849
888.176 | 526.1086 | 452.2412 | 425.6417 | 231.7692
889.176 | 526.1146 | 452.3358 | 425.4984 | 232.0687
890.176 | 526.1778 | 452.4888 | 425.7231 | 232.3488
891.176 | 526.2409 | 452.6846 | 425.852 | 232.6307
892.176 | 526.4069 | 452.7908 | 426.1102 | 232.9191
893.176 | 526.4357 | 452.7458 | 426.4392 | 233.1981
894.176 | 526.5451 | 452.9443 | 426.76 | 233.4803
895.176 | 526.4217 | 453.2109 | 426.649 | 233.762
896.176 | 526.4598 | 453.3294 | 426.8058 | 234.0368
897.176 | 526.5111 | 453.5372 | 426.6948 | 234.3193
898.176 | 526.5994 | 453.7272 | 426.8438 | 234.5944
899.176 | 526.4907 | 453.8442 | 426.8215 | 234.8761
900.176 | 526.3694 | 453.9071 | 426.7454 | 235.153
901.176 | 526.3761 | 454.0816 | 426.9755 | 235.437
902.176 | 526.4128 | 454.2968 | 427.2112 | 235.7092
903.176 | 526.4345 | 454.4923 | 427.3126 | 235.9871
904.176 | 526.4303 | 454.4594 | 427.3569 | 236.2645
905.176 | 526.5027 | 454.6219 | 427.652 | 236.5423
906.176 | 526.4252 | 454.8854 | 427.7611 | 236.8168
907.176 | 526.5553 | 455.0198 | 427.81 | 237.1082
908.176 | 526.5462 | 455.1083 | 428.1298 | 237.3802
909.176 | 526.673 | 455.3296 | 428.3194 | 237.6428
910.176 | 526.6366 | 455.4438 | 428.5552 | 237.9155
911.176 | 526.4828 | 455.6483 | 428.6525 | 238.1939
912.176 | 526.4927 | 455.9102 | 428.6516 | 238.4626
913.176 | 526.4716 | 456.0129 | 428.7445 | 238.7325
914.176 | 526.5333 | 456.2076 | 428.8872 | 238.9977
915.176 | 526.4686 | 456.3411 | 428.8968 | 239.2649
916.176 | 526.4636 | 456.4257 | 429.273 | 239.5441
917.176 | 526.4341 | 456.5268 | 429.3963 | 239.8064
918.176 | 526.0714 | 456.6989 | 429.1643 | 240.068
919.176 | 526.0086 | 456.8296 | 429.4597 | 240.3316
920.176 | 525.9009 | 457.0497 | 429.573 | 240.6
921.176 | 525.7425 | 457.1099 | 429.7264 | 240.8634
922.176 | 525.6155 | 457.1874 | 430.1453 | 241.1266
923.176 | 525.7052 | 457.4539 | 430.3471 | 241.3894
924.176 | 525.8507 | 457.615 | 430.5518 | 241.6471
925.176 | 525.9352 | 457.7928 | 430.5031 | 241.9119
926.176 | 525.9041 | 457.9367 | 430.5231 | 242.1673
927.176 | 525.9426 | 458.0825 | 430.4485 | 242.4216
928.176 | 525.9595 | 458.2134 | 430.5754 | 242.6798
929.176 | 525.7691 | 458.3195 | 430.9114 | 242.9392
930.176 | 525.7254 | 458.4669 | 431.0062 | 243.1991
931.176 | 525.7626 | 458.5888 | 431.1594 | 243.4557
932.176 | 525.806 | 458.7591 | 431.4268 | 243.721
933.176 | 525.8334 | 458.8422 | 431.5408 | 243.9682
934.176 | 525.9033 | 458.9151 | 431.7647 | 244.2315
935.176 | 526.0682 | 459.095 | 431.3397 | 244.4881
936.176 | 526.0388 | 459.174 | 431.4215 | 244.7429
937.176 | 526.113 | 459.3907 | 431.4435 | 244.9993
938.176 | 525.9775 | 459.5965 | 431.5101 | 245.2535
939.176 | 525.8313 | 459.6936 | 431.7438 | 245.5109
940.176 | 525.7632 | 459.8199 | 431.591 | 245.7698
941.176 | 525.7188 | 459.9453 | 431.9194 | 246.026
942.176 | 525.7039 | 460.0341 | 432.0093 | 246.275
943.176 | 525.6155 | 460.2037 | 432.519 | 246.525
944.176 | 525.5778 | 460.298 | 432.6803 | 246.7849
945.176 | 525.5935 | 460.3902 | 432.581 | 247.0357
946.176 | 525.7924 | 460.5472 | 432.6513 | 247.2927
947.176 | 525.806 | 460.78 | 432.647 | 247.5393
948.176 | 525.716 | 460.9047 | 432.9322 | 247.7876
949.176 | 525.6452 | 461.0024 | 432.9822 | 248.0412
950.176 | 525.5462 | 461.0469 | 433.492 | 248.2861
951.176 | 525.4325 | 461.3235 | 433.8128 | 248.539
952.176 | 525.5183 | 461.4944 | 434.0001 | 248.7827
953.176 | 525.5321 | 461.6095 | 434.0106 | 249.0337
954.176 | 525.6527 | 461.7324 | 434.3102 | 249.2837
955.176 | 525.692 | 461.8819 | 434.3639 | 249.5297
956.176 | 525.7486 | 462.0391 | 434.0802 | 249.7794
957.176 | 525.8636 | 462.1356 | 434.2022 | 250.0317
958.176 | 525.8789 | 462.2434 | 433.954 | 250.278
959.176 | 525.775 | 462.3129 | 434.0169 | 250.5182
960.176 | 525.4877 | 462.4554 | 434.0537 | 250.7732
961.176 | 525.4367 | 462.6078 | 434.0454 | 251.0234
962.176 | 525.3789 | 462.5932 | 434.2785 | 251.2813
963.176 | 525.3917 | 462.7298 | 434.5801 | 251.5454
964.176 | 525.2632 | 462.8365 | 434.6414 | 251.8012
965.176 | 525.2851 | 462.9786 | 434.9312 | 252.0679
966.176 | 525.4074 | 463.195 | 435.2378 | 252.3323
967.176 | 525.4239 | 463.2128 | 435.4067 | 252.6009
968.176 | 525.389 | 463.2995 | 435.384 | 252.8706
969.176 | 525.3921 | 463.3706 | 435.3168 | 253.1349
970.176 | 525.1392 | 463.5908 | 435.25 | 253.3995
971.176 | 525.0163 | 463.7113 | 435.3272 | 253.6592
972.176 | 525.1248 | 463.8036 | 435.7416 | 253.9175
973.176 | 525.1836 | 463.9848 | 436.0987 | 254.1764
974.176 | 525.3058 | 464.0727 | 436.2777 | 254.4324
975.176 | 525.3829 | 464.2051 | 436.0938 | 254.7013
976.176 | 525.3535 | 464.3249 | 436.3801 | 254.9583
977.176 | 525.3068 | 464.3407 | 436.4721 | 255.2219
978.176 | 525.432 | 464.3661 | 436.5203 | 255.4808
979.176 | 525.5901 | 464.4322 | 436.836 | 255.7419
980.176 | 525.5613 | 464.6515 | 436.8969 | 256.0046
981.176 | 525.3431 | 464.771 | 436.9017 | 256.2729
982.176 | 525.2664 | 464.9595 | 436.8901 | 256.5619
983.176 | 525.2983 | 465.1159 | 437.2481 | 256.8429
984.176 | 525.4018 | 465.2562 | 437.3412 | 257.1419
985.176 | 525.5999 | 465.3571 | 437.5393 | 257.4287
986.176 | 525.6459 | 465.4749 | 437.6269 | 257.718
987.176 | 525.6815 | 465.6551 | 437.9408 | 257.9889
988.176 | 525.828 | 465.7912 | 438.0463 | 258.2688
989.176 | 526.0249 | 465.9197 | 438.2556 | 258.5557
990.176 | 526.1786 | 465.9713 | 438.3195 | 258.8511
991.176 | 526.2283 | 466.1655 | 438.3849 | 259.1364
992.176 | 526.3022 | 466.2786 | 438.6871 | 259.4263
993.176 | 526.2836 | 466.3781 | 438.5646 | 259.7085
994.176 | 526.392 | 466.4286 | 438.8168 | 259.9926
995.176 | 526.4027 | 466.4467 | 438.9592 | 260.276
996.176 | 526.5008 | 466.5151 | 438.8962 | 260.5543
997.176 | 526.3765 | 466.6701 | 438.9763 | 260.8281
998.176 | 526.1207 | 466.8358 | 438.9959 | 261.1097
999.176 | 526.2397 | 467.0039 | 439.1484 | 261.3823
1000.176 | 526.2306 | 467.2014 | 439.2823 | 261.6652
1001.176 | 526.2833 | 467.1679 | 439.4728 | 261.9281
1002.176 | 526.2314 | 467.2366 | 439.7179 | 262.2066
1003.176 | 526.1114 | 467.387 | 439.6099 | 262.4703
1004.176 | 526.0264 | 467.4729 | 439.4317 | 262.7308
1005.176 | 525.929 | 467.5395 | 439.8397 | 262.9901
1006.176 | 525.6449 | 467.7399 | 439.9906 | 263.2555
1007.176 | 525.4722 | 467.8292 | 440.0166 | 263.5126
1008.176 | 525.3357 | 467.9059 | 440.1554 | 263.7584
1009.176 | 525.2505 | 467.9537 | 440.0759 | 264.0047
1010.176 | 525.0929 | 468.0206 | 440.1028 | 264.2528
1011.176 | 525.0085 | 468.0832 | 440.2983 | 264.5068
1012.176 | 524.8539 | 468.2595 | 440.4943 | 264.7556
1013.176 | 524.818 | 468.3947 | 440.6642 | 265.0086
1014.176 | 524.72 | 468.4256 | 440.9037 | 265.2502
1015.176 | 524.6663 | 468.6247 | 441.0853 | 265.4998
1016.176 | 524.6915 | 468.661 | 441.2249 | 265.7538
1017.176 | 524.775 | 468.7789 | 441.3056 | 266.0279
1018.176 | 524.8389 | 468.9906 | 441.5319 | 266.2886
1019.176 | 524.7375 | 469.1175 | 441.2176 | 266.5524
1020.176 | 524.8543 | 469.2412 | 441.2719 | 266.8085
1021.176 | 524.832 | 469.3458 | 441.4533 | 267.0703
1022.176 | 524.8137 | 469.3924 | 441.5281 | 267.3329
1023.176 | 524.9059 | 469.4538 | 441.8216 | 267.593
1024.176 | 524.9835 | 469.5114 | 442.0228 | 267.8616
1025.176 | 525.1616 | 469.6037 | 441.64 | 268.1257
1026.176 | 525.4206 | 469.7309 | 441.8318 | 268.3827
1027.176 | 525.552 | 469.8602 | 441.9052 | 268.6385
1028.176 | 525.7498 | 469.9659 | 441.9868 | 268.9033
1029.176 | 525.6647 | 470.1064 | 442.2573 | 269.1629
1030.176 | 525.6865 | 470.175 | 442.2008 | 269.4204
1031.176 | 525.6934 | 470.1916 | 442.227 | 269.6772
1032.176 | 525.6512 | 470.3768 | 442.3978 | 269.944
1033.176 | 525.6878 | 470.4871 | 442.5875 | 270.2102
1034.176 | 525.7196 | 470.5637 | 442.6652 | 270.4657
1035.176 | 525.872 | 470.679 | 442.5966 | 270.734
1036.176 | 526.0686 | 470.7645 | 442.6946 | 270.9814
1037.176 | 526.1711 | 470.8311 | 443.0378 | 271.2514
1038.176 | 526.179 | 470.9463 | 442.9332 | 271.5095
1039.176 | 526.1165 | 471.021 | 443.118 | 271.7565
1040.176 | 526.1 | 471.0856 | 442.9539 | 272.027
1041.176 | 526.1349 | 471.145 | 442.9485 | 272.2939
1042.176 | 526.1313 | 471.2323 | 442.8197 | 272.559
1043.176 | 525.8811 | 471.3272 | 442.8103 | 272.8302
1044.176 | 525.8083 | 471.3306 | 442.8792 | 273.0947
1045.176 | 525.8199 | 471.3835 | 443.0624 | 273.3678
1046.176 | 525.7582 | 471.5717 | 443.0138 | 273.6359
1047.176 | 525.8771 | 471.6669 | 443.211 | 273.8992
1048.176 | 525.7917 | 471.6925 | 443.1085 | 274.1632
1049.176 | 525.7464 | 471.5264 | 443.5999 | 274.4314
1050.176 | 525.6089 | 471.7916 | 443.8903 | 274.6999
1051.176 | 525.5487 | 472.028 | 443.7833 | 274.9577
1052.176 | 525.4214 | 472.1399 | 444.22 | 275.2225
1053.176 | 525.2671 | 472.3279 | 444.4276 | 275.4951
1054.176 | 525.354 | 472.3749 | 444.5532 | 275.7587
1055.176 | 525.3904 | 472.5012 | 444.5453 | 276.0174
1056.176 | 525.3978 | 472.4254 | 444.9203 | 276.2921
1057.176 | 525.3712 | 472.5573 | 444.676 | 276.5475
1058.176 | 525.3947 | 472.6695 | 444.6567 | 276.8144
1059.176 | 525.3446 | 472.8372 | 444.868 | 277.0598
1060.176 | 525.3204 | 472.8846 | 445.1116 | 277.321
1061.176 | 525.3713 | 473.0513 | 445.428 | 277.5641
1062.176 | 525.3392 | 473.1241 | 445.522 | 277.8139
1063.176 | 525.3093 | 473.2002 | 445.4814 | 278.0727
1064.176 | 525.0599 | 473.2443 | 445.7114 | 278.3338
1065.176 | 524.9694 | 473.4282 | 445.8263 | 278.5765
1066.176 | 524.984 | 473.369 | 445.8722 | 278.822
1067.176 | 525.0809 | 473.501 | 446.0372 | 279.0667
1068.176 | 525.2246 | 473.6664 | 446.1938 | 279.3218
1069.176 | 525.4032 | 473.7791 | 446.2589 | 279.5765
1070.176 | 525.5004 | 473.9106 | 446.2676 | 279.829
1071.176 | 525.6128 | 474.035 | 446.4752 | 280.085
1072.176 | 525.7101 | 474.0397 | 446.4491 | 280.3412
1073.176 | 525.8016 | 474.1642 | 446.3886 | 280.5762
1074.176 | 525.9069 | 474.2529 | 446.5129 | 280.8257
1075.176 | 525.934 | 474.2589 | 446.843 | 281.0852
1076.176 | 525.944 | 474.2976 | 446.8803 | 281.3508
1077.176 | 525.7298 | 474.4014 | 446.909 | 281.6036
1078.176 | 525.7245 | 474.4652 | 446.4308 | 281.8585
1079.176 | 525.6489 | 474.6087 | 446.4041 | 282.1145
1080.176 | 525.7222 | 474.7662 | 446.5498 | 282.3885
1081.176 | 525.7244 | 474.7775 | 446.3598 | 282.6607
1082.176 | 525.8467 | 474.7096 | 446.1653 | 282.9217
1083.176 | 525.9153 | 474.8229 | 446.3567 | 283.1701
1084.176 | 525.9284 | 475.0473 | 446.4182 | 283.4257
1085.176 | 525.9296 | 475.1975 | 446.4449 | 283.7015
1086.176 | 525.9994 | 475.2596 | 446.7109 | 283.9441
1087.176 | 525.9939 | 475.3384 | 446.8125 | 284.2124
1088.176 | 525.9967 | 475.4104 | 447.1119 | 284.498
1089.176 | 526.0108 | 475.4218 | 447.4273 | 284.7329
1090.176 | 526.0087 | 475.5188 | 447.6013 | 284.984
1091.176 | 525.9012 | 475.5533 | 447.6491 | 285.2096
1092.176 | 525.853 | 475.5953 | 447.6907 | 285.4392
1093.176 | 525.6974 | 475.6395 | 447.4804 | 285.6801
1094.176 | 525.5803 | 475.7104 | 447.2472 | 285.9061
1095.176 | 525.4274 | 475.7114 | 447.3246 | 286.1418
1096.176 | 525.2057 | 475.7737 | 447.2463 | 286.3854
1097.176 | 525.0814 | 475.9065 | 447.6004 | 286.634
1098.176 | 525.1034 | 476.0492 | 447.2731 | 286.8392
1099.176 | 525.0925 | 476.0962 | 447.1984 | 287.0581
1100.176 | 525.1777 | 476.2031 | 447.4667 | 287.271
1101.176 | 525.0575 | 476.1919 | 447.7413 | 287.4862
1102.176 | 525.0563 | 476.2925 | 448.057 | 287.7016
1103.176 | 525.0277 | 476.3984 | 448.4167 | 287.9159
1104.176 | 525.0406 | 476.5387 | 448.3506 | 288.0778
1105.176 | 525.144 | 476.5857 | 448.6167 | 288.3223
1106.176 | 525.1926 | 476.635 | 448.4484 | 288.5281
1107.176 | 525.2492 | 476.6483 | 448.5301 | 288.7494
1108.176 | 525.1154 | 476.7373 | 448.2594 | 288.9551
1109.176 | 525.001 | 476.8079 | 448.2708 | 289.1187
1110.176 | 524.9772 | 476.8069 | 448.3266 | 289.3171
1111.176 | 525.0815 | 476.9492 | 448.6807 | 289.5163
1112.176 | 525.18 | 477.0175 | 449.1498 | 289.7116
1113.176 | 525.1763 | 477.1859 | 449.3586 | 289.8981
1114.176 | 525.3171 | 477.2675 | 449.1524 | 290.0652
1115.176 | 525.4183 | 477.2952 | 449.219 | 290.271
1116.176 | 525.5687 | 477.2405 | 448.9765 | 290.4138
1117.176 | 525.5981 | 477.2161 | 449.3355 | 290.5681
1118.176 | 525.6503 | 477.3405 | 449.4703 | 290.7498
1119.176 | 525.7504 | 477.4755 | 449.5627 | 290.9068
1120.176 | 525.8156 | 477.5401 | 449.8777 | 291.0852
1121.176 | 526.0281 | 477.5803 | 449.7571 | 291.241
1122.176 | 525.9568 | 477.6659 | 449.8028 | 291.3996
1123.176 | 525.7963 | 477.6289 | 449.7956 | 291.5494
1124.176 | 525.7477 | 477.7764 | 450.0615 | 291.7028
1125.176 | 525.7976 | 477.9098 | 449.9998 | 291.8528
1126.176 | 525.8794 | 477.9029 | 449.893 | 292.0201
1127.176 | 525.8186 | 477.8954 | 449.9497 | 292.166
1128.176 | 525.7465 | 478.1053 | 449.864 | 292.3192
1129.176 | 525.6516 | 478.1439 | 449.9255 | 292.4506
1130.176 | 525.815 | 478.3144 | 450.2496 | 292.5992
1131.176 | 525.8879 | 478.3558 | 450.3848 | 292.7479
1132.176 | 525.8406 | 478.484 | 450.6264 | 292.8975
1133.176 | 525.7455 | 478.5001 | 450.9396 | 293.0443
1134.176 | 525.6781 | 478.5967 | 450.9483 | 293.18
1135.176 | 525.6723 | 478.599 | 450.9742 | 293.3196
1136.176 | 525.6041 | 478.6088 | 451.2815 | 293.4463
1137.176 | 525.5914 | 478.6589 | 451.3773 | 293.5934
1138.176 | 525.5991 | 478.7768 | 451.2626 | 293.7307
1139.176 | 525.617 | 478.9324 | 451.1912 | 293.8863
1140.176 | 525.6629 | 479.0389 | 450.9972 | 294.0473
1141.176 | 525.5972 | 479.0715 | 450.8639 | 294.1709
1142.176 | 525.6384 | 479.1593 | 451.1563 | 294.3131
1143.176 | 525.5104 | 479.2173 | 451.3888 | 294.4651
1144.176 | 525.4922 | 479.324 | 451.5394 | 294.6106
1145.176 | 525.437 | 479.4405 | 451.6416 | 294.7367
1146.176 | 525.409 | 479.4745 | 451.5276 | 294.8896
1147.176 | 525.4043 | 479.4864 | 451.729 | 295.0481
1148.176 | 525.4025 | 479.5507 | 451.8469 | 295.1897
1149.176 | 525.2878 | 479.5981 | 451.8864 | 295.3335
1150.176 | 525.4053 | 479.7078 | 451.9281 | 295.4942
1151.176 | 525.3451 | 479.8241 | 451.8017 | 295.6418
1152.176 | 525.2701 | 479.8974 | 451.8458 | 295.8102
1153.176 | 525.36 | 479.9232 | 451.7591 | 295.9719
1154.176 | 525.5117 | 479.9546 | 451.8981 | 296.1337
1155.176 | 525.5005 | 479.9442 | 452.06 | 296.2914
1156.176 | 525.3373 | 480.1447 | 452.4396 | 296.4607
1157.176 | 525.3883 | 480.1864 | 452.6665 | 296.6177
1158.176 | 525.4946 | 480.2915 | 452.5783 | 296.7843
1159.176 | 525.5533 | 480.4064 | 452.7343 | 296.9848
1160.176 | 525.5676 | 480.4468 | 453.0254 | 297.1474
1161.176 | 525.6224 | 480.4985 | 453.1569 | 297.3094
1162.176 | 525.7306 | 480.4799 | 452.9714 | 297.4913
1163.176 | 525.7709 | 480.5119 | 452.9347 | 297.6681
1164.176 | 525.798 | 480.6036 | 452.8976 | 297.8662
1165.176 | 525.7604 | 480.6164 | 452.9613 | 298.036
1166.176 | 525.8779 | 480.6169 | 453.2724 | 298.2308
1167.176 | 525.847 | 480.5199 | 453.1212 | 298.42
1168.176 | 525.7475 | 480.7244 | 453.4382 | 298.6079
1169.176 | 525.7637 | 480.843 | 453.2352 | 298.8273
1170.176 | 525.7365 | 480.9083 | 453.2693 | 299.0194
1171.176 | 525.8792 | 481.0142 | 453.4559 | 299.2341
1172.176 | 525.9325 | 481.0991 | 453.7245 | 299.4463
1173.176 | 526.0005 | 481.1827 | 453.9568 | 299.6604
1174.176 | 526.012 | 481.2705 | 453.8886 | 299.8821
1175.176 | 525.9207 | 481.3947 | 453.9673 | 300.0886
1176.176 | 525.9042 | 481.4544 | 454.2489 | 300.3241
1177.176 | 525.8252 | 481.4096 | 454.2497 | 300.5623
1178.176 | 525.7635 | 481.4315 | 454.0444 | 300.777
1179.176 | 525.8579 | 481.4492 | 454.0259 | 300.9916
1180.176 | 525.745 | 481.5147 | 454.3168 | 301.218
1181.176 | 525.9392 | 481.619 | 454.1895 | 301.4664
1182.176 | 526.0384 | 481.6066 | 454.2316 | 301.7034
1183.176 | 526.1501 | 481.7389 | 454.1822 | 301.9602
1184.176 | 526.1686 | 481.7223 | 454.476 | 302.205
1185.176 | 526.2205 | 481.7757 | 454.1512 | 302.4409
1186.176 | 526.3469 | 481.8469 | 454.3304 | 302.6874
1187.176 | 526.3572 | 481.9466 | 454.8 | 302.9249
1188.176 | 526.3731 | 482.0729 | 454.9445 | 303.1678
1189.176 | 526.3729 | 482.0905 | 454.9395 | 303.401
1190.176 | 526.2987 | 482.2262 | 454.7659 | 303.6627
1191.176 | 526.1719 | 482.2974 | 454.813 | 303.9488
1192.176 | 526.135 | 482.2659 | 454.4355 | 304.2103
1193.176 | 526.1371 | 482.342 | 454.5651 | 304.4573
1194.176 | 526.2353 | 482.4186 | 454.9486 | 304.742
1195.176 | 526.2794 | 482.5006 | 455.041 | 304.9858
1196.176 | 526.2292 | 482.5871 | 455.1723 | 305.2698
1197.176 | 526.2148 | 482.628 | 455.1588 | 305.5503
1198.176 | 526.3111 | 482.6444 | 455.006 | 305.8334
1199.176 | 526.3704 | 482.636 | 455.1244 | 306.1364
1200.176 | 526.4085 | 482.7095 | 454.876 | 306.4236
1201.176 | 526.5408 | 482.7213 | 455.0661 | 306.7195
1202.176 | 526.634 | 482.7838 | 455.0848 | 307.0069
1203.176 | 526.5098 | 482.902 | 454.9132 | 307.2945
1204.176 | 526.4739 | 483.0616 | 455.1329 | 307.5636
1205.176 | 526.4253 | 483.1417 | 455.5048 | 307.8322
1206.176 | 526.4228 | 483.225 | 455.7035 | 308.1235
1207.176 | 526.3848 | 483.1691 | 455.5527 | 308.4234
1208.176 | 526.1823 | 483.1137 | 455.6986 | 308.7278
1209.176 | 526.027 | 483.2505 | 455.985 | 309.0586
1210.176 | 525.8884 | 483.343 | 456.02 | 309.4194
1211.176 | 525.7186 | 483.3685 | 455.6726 | 309.9289
1212.176 | 525.5872 | 483.3226 | 455.7043 | 310.2561
1213.176 | 525.4616 | 483.3663 | 455.6062 | 310.6082
1214.176 | 525.3846 | 483.4855 | 455.7621 | 310.9581
1215.176 | 525.2843 | 483.5545 | 455.9335 | 311.2916
1216.176 | 525.0441 | 483.5961 | 455.9709 | 311.6412
1217.176 | 525.0485 | 483.6885 | 456.3022 | 311.9282
1218.176 | 525.0798 | 483.7886 | 456.5536 | 312.2115
1219.176 | 524.9414 | 483.8253 | 456.4203 | 312.4739
1220.176 | 524.8395 | 483.779 | 456.3661 | 312.7411
1221.176 | 524.9 | 483.8609 | 456.5484 | 313.0135
1222.176 | 524.9367 | 484.0144 | 456.4838 | 313.3087
1223.176 | 524.8113 | 484.0754 | 456.4943 | 313.5629
1224.176 | 524.8429 | 484.1448 | 456.4605 | 313.8433
1225.176 | 524.8772 | 484.2182 | 456.5657 | 314.1545
1226.176 | 525.0137 | 484.2179 | 456.5331 | 314.3813
1227.176 | 525.107 | 484.3205 | 456.8238 | 314.6463
1228.176 | 525.1399 | 484.4046 | 456.7649 | 314.9233
1229.176 | 525.262 | 484.3892 | 457.0203 | 315.241
1230.176 | 525.3024 | 484.3484 | 456.7918 | 315.5556
1231.176 | 525.24 | 484.4435 | 456.42 | 315.8922
1232.176 | 525.2532 | 484.4921 | 456.4162 | 316.2118
1233.176 | 525.3554 | 484.6578 | 456.6453 | 316.5365
1234.176 | 525.5135 | 484.7641 | 456.8748 | 316.8573
1235.176 | 525.4948 | 484.872 | 456.9035 | 317.2125
1236.176 | 525.4467 | 484.8294 | 457.1411 | 317.5636
1237.176 | 525.4133 | 484.903 | 457.1669 | 317.9565
1238.176 | 525.2756 | 484.9353 | 457.1108 | 318.2647
1239.176 | 525.3616 | 485.0238 | 457.1167 | 318.632
1240.176 | 525.422 | 485.114 | 457.1015 | 318.9592
1241.176 | 525.443 | 485.193 | 457.3011 | 319.2671
1242.176 | 525.3216 | 485.1684 | 457.2446 | 319.6032
1243.176 | 525.3328 | 485.1845 | 457.5293 | 319.9128
1244.176 | 525.3714 | 485.3228 | 457.6627 | 320.2235
1245.176 | 525.4695 | 485.3742 | 457.3185 | 320.5329
1246.176 | 525.454 | 485.4597 | 457.4135 | 320.8386
1247.176 | 525.3176 | 485.5133 | 457.6679 | 321.1558
1248.176 | 525.2877 | 485.5577 | 457.7063 | 321.4724
1249.176 | 525.3393 | 485.6689 | 457.9631 | 321.8
1250.176 | 525.3748 | 485.7418 | 458.125 | 322.1131
1251.176 | 525.4639 | 485.8163 | 458.332 | 322.4231
1252.176 | 525.5531 | 485.8464 | 458.295 | 322.759
1253.176 | 525.5614 | 485.8597 | 458.5326 | 323.084
1254.176 | 525.6905 | 486.0158 | 458.3736 | 323.3845
1255.176 | 525.7196 | 486.0407 | 458.71 | 323.7
1256.176 | 525.6313 | 486.1664 | 458.8546 | 323.9877
1257.176 | 525.4859 | 486.2483 | 459.1255 | 324.2712
1258.176 | 525.5489 | 486.3093 | 459.2934 | 324.5616
1259.176 | 525.7512 | 486.3563 | 459.0903 | 324.8208
1260.176 | 525.8971 | 486.3917 | 459.1668 | 325.0777
1261.176 | 526.0461 | 486.3752 | 459.0834 | 325.3424
1262.176 | 526.1485 | 486.4319 | 458.9713 | 325.5924
1263.176 | 526.318 | 486.5526 | 458.9065 | 325.8633
1264.176 | 526.4685 | 486.6279 | 458.9269 | 326.1421
1265.176 | 526.5641 | 486.5754 | 459.2285 | 326.4309
1266.176 | 526.4065 | 486.6863 | 458.9599 | 326.7184
1267.176 | 526.3453 | 486.803 | 458.5118 | 327.0002
1268.176 | 526.1649 | 486.9256 | 458.4472 | 327.2725
1269.176 | 526.2485 | 486.9529 | 458.6693 | 327.5659
1270.176 | 526.4319 | 486.9751 | 458.7522 | 327.8749
1271.176 | 526.5534 | 487.0571 | 458.8647 | 328.1684
1272.176 | 526.6524 | 487.1032 | 459.0689 | 328.4705
1273.176 | 526.6455 | 487.1592 | 459.2389 | 328.7759
1274.176 | 526.6283 | 487.1776 | 459.4041 | 329.0644
1275.176 | 526.6226 | 487.2131 | 459.5373 | 329.3955
1276.176 | 526.6005 | 487.3543 | 459.2894 | 329.6997
1277.176 | 526.7171 | 487.4557 | 459.5189 | 329.9878
1278.176 | 526.6821 | 487.516 | 459.3814 | 330.2889
1279.176 | 526.5252 | 487.2615 | 459.5243 | 330.588
1280.176 | 526.3289 | 487.4018 | 459.6952 | 330.9089
1281.176 | 526.1369 | 487.4629 | 459.6853 | 331.2466
1282.176 | 525.8707 | 487.5777 | 459.8447 | 331.5681
1283.176 | 525.6631 | 487.6676 | 460.088 | 331.8845
1284.176 | 525.6081 | 487.7015 | 460 | 332.2154
1285.176 | 525.6269 | 487.6447 | 460.0336 | 332.5665
1286.176 | 525.4276 | 487.7438 | 459.9359 | 332.8913
1287.176 | 525.4704 | 487.8411 | 460.2215 | 333.2227
1288.176 | 525.3607 | 487.9627 | 460.4809 | 333.5355
1289.176 | 525.0846 | 487.8829 | 460.6807 | 333.8671
1290.176 | 524.8355 | 487.9485 | 460.7029 | 334.1953
1291.176 | 524.8671 | 488.0196 | 460.6389 | 334.5468
1292.176 | 525.0137 | 488.1089 | 460.4122 | 334.9136
1293.176 | 525.1556 | 488.2005 | 460.1112 | 335.2995
1294.176 | 525.2467 | 488.2475 | 460.1023 | 335.6508
1295.176 | 525.3167 | 488.2464 | 460.4787 | 335.9724
1296.176 | 525.4088 | 488.2718 | 460.5194 | 336.319
1297.176 | 525.5035 | 488.3354 | 460.6784 | 336.6606
1298.176 | 525.5459 | 488.2652 | 460.784 | 336.9983
1299.176 | 525.5909 | 488.3155 | 460.7831 | 337.335
1300.176 | 525.6564 | 488.3819 | 460.452 | 337.6273
1301.176 | 525.695 | 488.4705 | 460.4682 | 337.9441
1302.176 | 525.6799 | 488.5611 | 460.6512 | 338.2107
1303.1917 | 525.4323 | 488.5781 | 460.7486 | 338.4755
1304.176 | 525.4356 | 488.5519 | 461.0473 | 338.7292
1305.176 | 525.4415 | 488.6725 | 461.2749 | 338.9759
1306.176 | 525.4576 | 488.7121 | 461.4602 | 339.2332
1307.176 | 525.4488 | 488.7749 | 461.564 | 339.4839
1308.176 | 525.2746 | 488.6308 | 461.7351 | 339.7507
1309.176 | 525.2379 | 488.6969 | 461.8099 | 340.0213
1310.176 | 525.2364 | 488.7076 | 461.8417 | 340.3246
1311.176 | 525.2588 | 488.7744 | 461.8069 | 340.6287
1312.176 | 525.4328 | 488.6584 | 461.3924 | 340.9171
1313.176 | 525.5564 | 488.6938 | 461.1696 | 341.2382
1314.176 | 525.5841 | 488.817 | 461.3607 | 341.5
1315.176 | 525.6004 | 488.8293 | 461.4438 | 341.7671
1316.176 | 525.6943 | 488.8497 | 461.5316 | 342.0546
1317.176 | 525.4668 | 488.8536 | 461.5963 | 342.3575
1318.176 | 525.3983 | 488.8802 | 461.6209 | 342.6422
1319.176 | 525.3935 | 488.88 | 461.61 | 342.9531
1320.176 | 525.5887 | 488.8405 | 461.7874 | 343.2637
1321.176 | 525.7041 | 488.8216 | 461.82 | 343.5662
1322.176 | 525.7539 | 488.8215 | 462.1294 | 343.9043
1323.176 | 525.8289 | 488.9209 | 462.1673 | 344.1708
1324.176 | 525.8455 | 488.9183 | 462.345 | 344.4525
1325.176 | 525.7782 | 488.9469 | 462.2309 | 344.7459
1326.176 | 525.7539 | 488.9749 | 462.263 | 345.0067
1327.176 | 525.6658 | 488.974 | 462.3209 | 345.281
1328.176 | 525.8041 | 488.8671 | 462.4972 | 345.5453
1329.176 | 525.8876 | 488.8803 | 462.5372 | 345.8035
1330.176 | 525.9469 | 488.8236 | 462.3557 | 346.0923
1331.176 | 525.9611 | 488.8591 | 462.4973 | 346.4113
1332.176 | 526.0165 | 488.7862 | 462.4799 | 346.747
1333.176 | 526.0974 | 488.7946 | 462.3202 | 347.0822
1334.176 | 526.1433 | 488.8944 | 462.4998 | 347.4179
1335.176 | 526.1098 | 488.8993 | 462.873 | 347.7479
1336.176 | 526.1609 | 488.9069 | 463.1523 | 348.0758
1337.176 | 526.1499 | 488.9474 | 463.1647 | 348.4043
1338.176 | 526.1054 | 488.8262 | 462.9219 | 348.746
1339.176 | 526.1909 | 488.7346 | 462.8446 | 349.0849
1340.176 | 526.0658 | 488.8277 | 462.8927 | 349.4247
1341.176 | 525.9409 | 488.8966 | 462.833 | 349.7677
1342.176 | 525.6633 | 488.8578 | 462.6702 | 350.1028
1343.176 | 525.3413 | 488.8194 | 462.8783 | 350.4494
1344.6292 | 525.4488 | 488.8357 | 463.2655 | 350.9447
1345.1917 | 525.5397 | 488.9115 | 463.3144 | 351.1405
1346.176 | 525.7124 | 488.8955 | 463.4554 | 351.4627
1347.176 | 525.7924 | 488.8299 | 463.6762 | 351.7806
1348.176 | 525.8756 | 488.9473 | 463.7284 | 352.0914
1349.176 | 525.8953 | 488.9258 | 463.2762 | 352.4132
1350.176 | 525.8252 | 488.8226 | 463.3379 | 352.7391
1351.2854 | 525.9534 | 488.9567 | 462.9935 | 353.0909
1352.176 | 525.9551 | 489.0625 | 462.9851 | 353.3798
1353.176 | 525.9347 | 489.0189 | 463.0307 | 353.7098
1354.176 | 525.8594 | 488.8734 | 463.0664 | 354.0435
1355.176 | 525.7419 | 488.9298 | 462.9695 | 354.3829
1356.1917 | 525.7557 | 488.9724 | 463.231 | 354.6994
1357.1917 | 525.6905 | 489.1005 | 463.4777 | 355.0284
1358.176 | 525.6696 | 489.1533 | 463.7567 | 355.3541
1359.176 | 525.6375 | 489.1732 | 463.9875 | 355.6819
1360.176 | 525.6415 | 489.0991 | 464.1283 | 356.0068
1361.176 | 525.6397 | 489.1153 | 464.1958 | 356.3374
1362.176 | 525.6404 | 489.2267 | 464.2797 | 356.669
1363.1917 | 525.7385 | 489.2166 | 463.9175 | 356.9895
1364.176 | 525.6522 | 489.1738 | 463.9009 | 357.3125
1365.176 | 525.7161 | 489.1742 | 463.9395 | 357.6297
1366.176 | 525.9312 | 489.1724 | 463.8211 | 357.9462
1367.176 | 526.1475 | 489.0677 | 463.6676 | 358.258
1368.176 | 526.1401 | 489.0948 | 464.1164 | 358.575
1369.176 | 526.2047 | 489.1548 | 464.4178 | 358.8852
1370.176 | 526.2009 | 489.2724 | 464.6795 | 359.2142
1371.176 | 526.2448 | 489.3363 | 464.5468 | 359.5284
1372.176 | 526.3852 | 489.3855 | 464.3687 | 359.8375
1373.176 | 526.555 | 489.3649 | 464.4277 | 360.1494
1374.176 | 526.6946 | 489.3066 | 464.3606 | 360.4279
1375.176 | 526.8385 | 489.4277 | 464.2824 | 360.7243
1376.176 | 526.9473 | 489.3403 | 464.4154 | 361.0124
1377.176 | 527.1493 | 489.3792 | 464.4312 | 361.2898
1378.176 | 527.2092 | 489.4604 | 464.652 | 361.5756
1379.176 | 527.0029 | 489.569 | 464.697 | 361.8478
1380.176 | 526.8609 | 489.6276 | 464.9353 | 362.141
1381.176 | 526.9315 | 489.6195 | 464.9045 | 362.4192
1382.176 | 526.8588 | 489.6677 | 465.1219 | 362.6965
1383.176 | 526.8246 | 489.7217 | 465.1717 | 362.9839
1384.176 | 526.8173 | 489.7907 | 465.0955 | 363.2525
1385.176 | 526.6406 | 489.6844 | 465.238 | 363.5238
1386.176 | 526.499 | 489.6607 | 465.4988 | 363.7889
1387.176 | 526.4826 | 489.7168 | 465.1946 | 364.052
1388.176 | 526.4603 | 489.739 | 465.2972 | 364.3103
1389.176 | 526.3154 | 489.7405 | 465.4058 | 364.5695
1390.176 | 526.1736 | 489.7489 | 465.4789 | 364.802
1391.176 | 526.0799 | 489.6698 | 465.2917 | 365.054
1392.176 | 526.1408 | 489.8114 | 465.4885 | 365.3073
1393.1917 | 526.1615 | 489.881 | 465.269 | 365.5945
1394.176 | 526.2507 | 489.9664 | 465.2385 | 365.8564
1395.176 | 526.3008 | 489.9559 | 465.6173 | 366.1238
1396.176 | 526.2779 | 489.8931 | 465.5726 | 366.3769
1397.176 | 526.0881 | 489.8368 | 465.5674 | 366.6246
1398.176 | 526.1253 | 489.8656 | 465.4689 | 366.8805
1399.176 | 526.0191 | 489.9547 | 465.5613 | 367.1267
1400.176 | 525.9542 | 489.9274 | 465.0957 | 367.3883
1401.176 | 526.028 | 489.759 | 465.0639 | 367.6223
1402.176 | 526.0441 | 489.9171 | 465.4313 | 367.8447
1403.176 | 526.0278 | 489.9567 | 465.5462 | 368.1015
1404.176 | 525.9483 | 489.8115 | 465.7428 | 368.3635
1405.176 | 525.8827 | 489.8513 | 465.6488 | 368.6106
1406.176 | 525.8973 | 489.9045 | 465.6583 | 368.8439
1407.176 | 525.6824 | 489.8194 | 465.7623 | 369.0828
1408.176 | 525.6411 | 489.8806 | 465.4085 | 369.3314
1409.176 | 525.7565 | 489.738 | 465.5147 | 369.5714
1410.176 | 525.7202 | 489.8909 | 465.739 | 369.8096
1411.176 | 525.8066 | 489.9007 | 466.1312 | 370.0322
1412.1917 | 525.7877 | 489.9134 | 466.1778 | 370.2533
1413.176 | 525.9537 | 489.9086 | 466.2502 | 370.4859
1414.176 | 525.8845 | 489.924 | 466.1215 | 370.6965
1415.176 | 525.8121 | 489.9402 | 466.2107 | 370.9115
1416.176 | 525.8196 | 489.9481 | 465.9915 | 371.1398
1417.176 | 525.9383 | 489.9538 | 465.7169 | 371.35
1418.176 | 526.0993 | 490.0025 | 465.5389 | 371.5467
1419.176 | 526.225 | 489.9588 | 465.4965 | 371.7586
1420.176 | 526.2522 | 490.0867 | 465.7296 | 371.9794
1421.176 | 526.2528 | 490.0836 | 465.6563 | 372.1896
1422.176 | 526.344 | 490.1742 | 466.0185 | 372.383
1423.1917 | 526.4336 | 490.2355 | 466.164 | 372.5726
1424.176 | 526.3973 | 490.2076 | 466.3584 | 372.754
1425.176 | 526.418 | 490.2403 | 466.5185 | 372.9592
1426.176 | 526.2819 | 490.1941 | 466.5368 | 373.1543
1427.176 | 526.3246 | 490.1993 | 466.5962 | 373.3511
1428.176 | 526.1339 | 490.278 | 466.7206 | 373.5234
1429.176 | 526.0081 | 490.3147 | 466.4799 | 373.6987
1430.176 | 525.9931 | 490.3957 | 466.488 | 373.8867
1431.176 | 526.0079 | 490.2002 | 466.4334 | 374.0772
1432.176 | 526.1463 | 490.2718 | 466.6248 | 374.2527
1433.176 | 526.2575 | 490.3345 | 466.5585 | 374.4403
1434.176 | 526.1091 | 490.3936 | 466.8414 | 374.6231
1435.176 | 526.1603 | 490.4457 | 466.8897 | 374.7892
1436.176 | 526.1929 | 490.4693 | 466.8641 | 374.9576
1437.176 | 526.1557 | 490.5414 | 466.8389 | 375.1393
1438.176 | 526.1905 | 490.5279 | 466.9413 | 375.3037
1439.176 | 526.2308 | 490.671 | 467.1239 | 375.4758
1440.176 | 526.0033 | 490.6542 | 467.2407 | 375.6412
1441.176 | 525.8123 | 490.6101 | 467.2675 | 375.8103
1442.176 | 525.8613 | 490.677 | 467.3006 | 375.9957
1443.176 | 525.9213 | 490.7187 | 467.1117 | 376.1522
1444.176 | 526.1402 | 490.7109 | 467.0013 | 376.3282
1445.176 | 526.2075 | 490.7699 | 467.1183 | 376.5011
1446.176 | 526.2258 | 490.7774 | 467.3947 | 376.6533
1447.176 | 526.0956 | 490.7908 | 467.4018 | 376.8088
1448.176 | 526.0674 | 490.7523 | 467.3634 | 376.9837
1449.176 | 525.9363 | 490.7226 | 467.4347 | 377.1267
1450.176 | 525.8596 | 490.7804 | 467.4034 | 377.2906
1451.176 | 525.7028 | 490.8534 | 467.3633 | 377.4557
1452.176 | 525.6167 | 490.7607 | 467.2747 | 377.6232
1453.1917 | 525.8219 | 490.803 | 467.3287 | 377.7834
1454.176 | 525.8233 | 490.8093 | 467.4372 | 377.9381
1455.176 | 525.7602 | 490.8207 | 467.4407 | 378.0915
1456.176 | 525.7083 | 490.8687 | 467.5123 | 378.2401
1457.176 | 525.563 | 490.9926 | 467.2855 | 378.3938
1458.176 | 525.54 | 490.9912 | 467.0897 | 378.5607
1459.176 | 525.4833 | 491.0657 | 467.2322 | 378.7157
1460.176 | 525.4242 | 491.1446 | 467.4506 | 378.8641
1461.176 | 525.3949 | 491.0923 | 467.5492 | 379.0181
1462.176 | 525.3651 | 491.1092 | 467.5986 | 379.1669
1463.176 | 525.4342 | 491.1207 | 467.2103 | 379.3178
1464.176 | 525.4893 | 491.0626 | 467.1664 | 379.4658
1465.176 | 525.5874 | 491.189 | 467.3014 | 379.6195
1466.176 | 525.6224 | 491.3438 | 467.3797 | 379.7745
1467.176 | 525.6942 | 491.4361 | 467.2665 | 379.93
1468.176 | 525.8279 | 491.421 | 467.4764 | 380.0743
1469.176 | 525.9836 | 491.434 | 467.6609 | 380.2248
1470.176 | 525.9893 | 491.5311 | 467.8691 | 380.3639
1471.176 | 525.9151 | 491.534 | 468.0231 | 380.5026
1472.176 | 525.9806 | 491.5327 | 468.1722 | 380.637
1473.176 | 526.0555 | 491.5359 | 468.1319 | 380.7876
1474.176 | 526.1037 | 491.5932 | 467.784 | 380.9226
1475.176 | 526.1268 | 491.577 | 467.4977 | 381.0751
1476.176 | 526.1632 | 491.5625 | 467.7339 | 381.2102
1477.176 | 526.0837 | 491.6365 | 467.641 | 381.3502
1478.176 | 526.1164 | 491.5966 | 467.587 | 381.4887
1479.176 | 526.0091 | 491.7104 | 467.4313 | 381.6229
1480.176 | 526.0391 | 491.7683 | 467.2748 | 381.7598
1481.176 | 526.0141 | 491.8258 | 467.1801 | 381.8926
1482.176 | 525.9865 | 491.8666 | 467.3584 | 382.0306
1483.1917 | 526.0576 | 491.8352 | 467.6298 | 382.177
1484.176 | 525.9572 | 491.8695 | 467.7714 | 382.3079
1485.176 | 525.8493 | 491.9246 | 468.0676 | 382.445
1486.176 | 525.7466 | 491.9245 | 468.2217 | 382.5811
1487.176 | 525.5601 | 492.0347 | 468.1595 | 382.711
1488.176 | 525.562 | 492.0177 | 468.1997 | 382.8435
1489.176 | 525.5985 | 492.127 | 468.1123 | 382.981
1490.176 | 525.6003 | 492.0722 | 468.2626 | 383.1121
1491.176 | 525.6439 | 492.15 | 468.2272 | 383.2408
1492.176 | 525.6942 | 492.2075 | 467.9419 | 383.3663
1493.176 | 525.6781 | 492.2051 | 467.8056 | 383.5039
1494.176 | 525.5868 | 492.0037 | 468.0164 | 383.6426
1495.176 | 525.5101 | 492.1306 | 468.0618 | 383.7696
1496.176 | 525.4543 | 492.0916 | 468.3165 | 383.9033
1497.176 | 525.4524 | 492.1478 | 468.1308 | 384.0392
1498.176 | 525.5124 | 492.1412 | 468.1546 | 384.1596
1499.176 | 525.6621 | 492.3148 | 468.3291 | 384.2896
1500.176 | 525.8932 | 492.4104 | 468.6083 | 384.4166
1501.176 | 526.0153 | 492.4071 | 468.7763 | 384.5415
1502.176 | 526.2319 | 492.5367 | 468.4281 | 384.673
1503.176 | 526.3763 | 492.5921 | 468.4592 | 384.7974
1504.176 | 526.4536 | 492.6401 | 468.4552 | 384.9314
1505.176 | 526.4517 | 492.6387 | 468.4556 | 385.0577
1506.176 | 526.5531 | 492.648 | 468.3039 | 385.187
1507.176 | 526.6357 | 492.6705 | 468.3338 | 385.3117
1508.176 | 526.6737 | 492.6847 | 468.6531 | 385.443
1509.176 | 526.6425 | 492.6514 | 468.8756 | 385.5615
1510.176 | 526.6409 | 492.7334 | 468.8371 | 385.68
1511.176 | 526.6866 | 492.8132 | 469.0106 | 385.81
1512.176 | 526.7181 | 492.8765 | 468.833 | 385.9284
1513.1917 | 526.7131 | 492.8379 | 468.7375 | 386.0597
1514.176 | 526.5916 | 492.9453 | 468.5012 | 386.1801
1515.176 | 526.4821 | 492.9904 | 468.669 | 386.3111
1516.176 | 526.4893 | 493.0393 | 468.6108 | 386.4467
1517.176 | 526.3639 | 493.0633 | 468.4941 | 386.56
1518.176 | 526.2203 | 492.9548 | 468.7437 | 386.699
1519.176 | 526.0965 | 492.9699 | 469.0881 | 386.8201
1520.176 | 526.1444 | 493.1039 | 468.727 | 386.9485
1521.176 | 526.1934 | 493.1147 | 468.7659 | 387.0808
1522.176 | 526.2255 | 493.1964 | 469.1106 | 387.2051
1523.176 | 526.3545 | 493.2546 | 468.7198 | 387.3282
1524.176 | 526.2437 | 493.2207 | 468.5147 | 387.4549
1525.176 | 526.2812 | 493.3115 | 468.7405 | 387.5789
1526.176 | 526.3116 | 493.3983 | 468.69 | 387.7165
1527.176 | 526.3096 | 493.4522 | 468.8701 | 387.8493
1528.176 | 526.3049 | 493.4133 | 469.0073 | 387.9787
1529.176 | 526.3021 | 493.492 | 469.1212 | 388.1112
1530.176 | 526.2804 | 493.5102 | 469.1559 | 388.2376
1531.176 | 526.119 | 493.4542 | 468.8591 | 388.3556
1532.176 | 526.1125 | 493.6177 | 469.0346 | 388.4765
1533.176 | 526.1395 | 493.5176 | 469.2711 | 388.5995
1534.176 | 526.2338 | 493.5735 | 469.355 | 388.7309
1535.176 | 526.2907 | 493.6809 | 469.4737 | 388.8438
1536.176 | 526.3723 | 493.7815 | 469.5725 | 388.9731
1537.176 | 526.266 | 493.7756 | 469.5304 | 389.0973
1538.176 | 526.2436 | 493.7909 | 469.372 | 389.227
1539.176 | 526.1979 | 493.8659 | 469.5278 | 389.3444
1540.176 | 526.052 | 493.8887 | 469.604 | 389.4629
1541.176 | 525.9281 | 493.8988 | 469.3858 | 389.59
1542.176 | 525.9822 | 493.9555 | 469.2968 | 389.713
1543.176 | 526.1131 | 494.0362 | 469.4637 | 389.8434
1544.176 | 526.2344 | 494.0378 | 469.5214 | 389.9661
1545.176 | 526.4208 | 494.0908 | 469.4986 | 390.0973
1546.176 | 526.5672 | 494.0872 | 469.5007 | 390.2171
1547.176 | 526.6865 | 494.1708 | 469.0514 | 390.3423
1548.176 | 526.6527 | 494.1003 | 469.2437 | 390.4673
1549.176 | 526.7589 | 494.1607 | 469.306 | 390.5946
1550.176 | 526.6519 | 494.2043 | 469.308 | 390.7148
1551.176 | 526.3034 | 494.1425 | 469.4979 | 390.8435
1552.176 | 526.2022 | 494.1965 | 469.5142 | 390.9683
1553.176 | 526.1738 | 494.2982 | 469.1682 | 391.0974
1554.176 | 526.1813 | 494.3557 | 469.3633 | 391.2241
1555.176 | 526.2362 | 494.4028 | 469.1197 | 391.3389
1556.176 | 526.3075 | 494.3702 | 469.1878 | 391.4673
1557.176 | 526.3274 | 494.4864 | 469.1045 | 391.5858
1558.176 | 526.2341 | 494.4755 | 468.8161 | 391.7056
1559.176 | 526.2329 | 494.5256 | 469.0302 | 391.8339
1560.176 | 526.1254 | 494.5201 | 469.2078 | 391.9592
1561.176 | 525.9625 | 494.6137 | 469.0683 | 392.0788
1562.176 | 525.9437 | 494.6139 | 468.9978 | 392.2033
1563.176 | 525.9131 | 494.6871 | 469.3404 | 392.3307
1564.176 | 525.99 | 494.7173 | 469.5555 | 392.4547
1565.176 | 526.0542 | 494.8221 | 469.307 | 392.5767
1566.176 | 526.0698 | 494.9082 | 469.2009 | 392.7019
1567.176 | 526.1067 | 494.9188 | 469.2423 | 392.8247
1568.176 | 526.1294 | 494.9944 | 469.1625 | 392.9508
1569.176 | 526.211 | 495.014 | 469.507 | 393.0706
1570.176 | 526.2175 | 495.063 | 469.7215 | 393.1973
1571.176 | 526.3 | 495.2212 | 469.8442 | 393.3249
1572.176 | 526.2372 | 495.2692 | 469.8673 | 393.4499
1573.176 | 526.1751 | 495.2763 | 470.1184 | 393.5715
1574.176 | 526.2028 | 495.3376 | 470.2507 | 393.7013
1575.176 | 526.2788 | 495.3629 | 470.3095 | 393.8264
1576.176 | 526.2852 | 495.4117 | 470.0115 | 393.9499
1577.176 | 526.2627 | 495.3392 | 469.8878 | 394.0701
1578.176 | 526.2309 | 495.4287 | 470.3851 | 394.1981
1579.176 | 526.2844 | 495.5317 | 470.6535 | 394.3207
1580.176 | 526.335 | 495.5457 | 470.6749 | 394.4443
1581.176 | 526.3447 | 495.5518 | 470.754 | 394.5675
1582.176 | 526.2973 | 495.6054 | 470.665 | 394.6925
1583.176 | 526.4028 | 495.6485 | 470.748 | 394.8091
1584.176 | 526.459 | 495.7161 | 470.8012 | 394.9314
1585.176 | 526.5785 | 495.762 | 470.6645 | 395.0541
1586.176 | 526.7709 | 495.8128 | 470.662 | 395.1757
1587.176 | 526.8883 | 495.8483 | 470.3721 | 395.2983
1588.176 | 527.0171 | 495.8312 | 470.4696 | 395.4175
1589.176 | 527.1179 | 495.8726 | 470.7852 | 395.5454
1590.176 | 527.0755 | 495.9509 | 470.7849 | 395.6672
1591.176 | 527.0518 | 496.0094 | 471.0095 | 395.7793
1592.176 | 526.9346 | 496.0282 | 471.0441 | 395.9053
1593.176 | 526.8788 | 496.0338 | 471.1642 | 396.0201
1594.176 | 526.7001 | 496.0097 | 470.8196 | 396.1392
1595.176 | 526.506 | 495.9961 | 470.9223 | 396.25
1596.176 | 526.4762 | 496.083 | 471.0337 | 396.3688
1597.176 | 526.278 | 496.1404 | 470.7784 | 396.4848
1598.176 | 526.3423 | 496.1311 | 470.6705 | 396.6053
1599.176 | 526.421 | 496.1547 | 470.8834 | 396.7142
1600.176 | 526.491 | 496.1126 | 470.7978 | 396.8369
1601.176 | 526.5328 | 496.154 | 470.7334 | 396.9478
1602.176 | 526.3813 | 496.1568 | 470.672 | 397.0828
1603.176 | 526.1436 | 496.1834 | 470.753 | 397.2015
1604.176 | 526.012 | 496.2476 | 470.76 | 397.3107
1605.176 | 525.9976 | 496.2369 | 470.9888 | 397.4358
1606.176 | 525.8876 | 496.3005 | 470.7302 | 397.5586
1607.176 | 525.7755 | 496.2623 | 470.5437 | 397.6749
1608.176 | 525.7937 | 496.3211 | 470.4284 | 397.7858
1609.176 | 525.8675 | 496.4286 | 470.7981 | 397.9082
1610.176 | 525.9475 | 496.3169 | 471.136 | 398.0178
1611.176 | 526.0233 | 496.3421 | 471.2199 | 398.1409
1612.176 | 526.0273 | 496.49 | 470.9631 | 398.2484
1613.176 | 526.0974 | 496.5185 | 470.8228 | 398.3728
1614.176 | 526.0357 | 496.4414 | 470.9203 | 398.4897
1615.176 | 525.7572 | 496.5976 | 471.3115 | 398.6055
1616.176 | 525.6119 | 496.6558 | 471.5783 | 398.7184
1617.176 | 525.5497 | 496.6395 | 471.5094 | 398.8407
1618.176 | 525.5867 | 496.6385 | 471.7239 | 398.9493
1619.176 | 525.6509 | 496.7079 | 471.858 | 399.0628
1620.176 | 525.605 | 496.7823 | 471.8029 | 399.18
1621.176 | 525.4371 | 496.5693 | 471.9941 | 399.2641
1622.176 | 525.4704 | 496.7697 | 472.0047 | 399.3757
1623.176 | 525.3626 | 496.8354 | 471.7365 | 399.4818
1624.176 | 525.4572 | 496.7422 | 471.6522 | 399.5916
1625.176 | 525.6298 | 496.8146 | 471.8084 | 399.7058
1626.176 | 525.8477 | 496.8224 | 471.6718 | 399.8055
1627.176 | 526.0003 | 496.891 | 471.381 | 399.9286
1628.176 | 526.1208 | 496.9161 | 471.3602 | 400.0421
1629.176 | 526.1807 | 496.981 | 471.2369 | 400.1571
1630.176 | 526.2271 | 496.9979 | 471.3028 | 400.2528
1631.176 | 526.1853 | 497.101 | 471.3951 | 400.3471
1632.176 | 526.2338 | 497.1952 | 471.769 | 400.4346
1633.176 | 526.0408 | 497.2107 | 471.7855 | 400.5196
1634.176 | 525.927 | 497.2353 | 471.7347 | 400.627
1635.176 | 525.916 | 497.238 | 471.5502 | 400.7226
1636.176 | 525.77 | 497.1968 | 471.8229 | 400.8283
1637.176 | 525.7659 | 497.2565 | 471.9035 | 400.9276
1638.176 | 525.8693 | 497.3472 | 471.5973 | 401.0272
1639.176 | 525.8378 | 497.4224 | 471.6001 | 401.1457
1640.176 | 525.7396 | 497.3779 | 471.751 | 401.2353
1641.176 | 525.7276 | 497.3527 | 471.7374 | 401.3516
1642.176 | 525.7553 | 497.4446 | 471.4917 | 401.4632
1643.176 | 525.7488 | 497.4105 | 471.5843 | 401.5749
1644.176 | 525.8224 | 497.4808 | 471.8301 | 401.6869
1645.176 | 525.8468 | 497.6036 | 471.8979 | 401.7869
1646.176 | 525.7129 | 497.6518 | 471.9436 | 401.8544
1647.176 | 525.4713 | 497.5602 | 471.7778 | 401.8125
1648.176 | 525.2783 | 497.4469 | 471.7827 | 401.8864
1649.176 | 525.3229 | 497.4985 | 471.7619 | 401.9526
1650.176 | 525.3143 | 497.5475 | 471.4202 | 402.0798
1651.176 | 525.327 | 497.5182 | 471.4972 | 402.1869
1652.176 | 525.312 | 497.7127 | 471.5786 | 402.2654
1653.176 | 525.1413 | 497.723 | 471.5313 | 402.3755
1654.176 | 524.9274 | 497.7426 | 471.6228 | 402.4857
1655.176 | 524.7277 | 497.8049 | 471.2933 | 402.5822
1656.176 | 524.8535 | 497.8632 | 471.2248 | 402.708
1657.176 | 524.7113 | 497.8409 | 471.5661 | 402.8165
1658.176 | 524.6386 | 497.8229 | 471.982 | 402.9395
1659.176 | 524.7044 | 497.9136 | 472.1432 | 403.0318
1660.176 | 524.7555 | 498.0348 | 472.2126 | 403.1319
1661.176 | 524.8179 | 498.0748 | 472.3758 | 403.2326
1662.176 | 525.0191 | 498.1368 | 472.3417 | 403.2277
1663.176 | 525.1457 | 498.1679 | 472.4504 | 403.3402
1664.176 | 525.1326 | 498.152 | 472.3424 | 403.4741
1665.176 | 525.1645 | 498.1464 | 472.333 | 403.5701
1666.176 | 525.3462 | 498.2148 | 472.4421 | 403.6937
1667.176 | 525.3686 | 498.1878 | 472.4055 | 403.7739
1668.176 | 525.2932 | 498.2256 | 472.3019 | 403.3599
1669.176 | 525.2625 | 498.216 | 472.2919 | 403.1139
1670.176 | 525.23 | 498.281 | 472.2966 | 403.0856
1671.176 | 525.1581 | 498.2454 | 472.3633 | 403.0816
1672.176 | 525.157 | 498.2246 | 472.5837 | 402.9742
1673.176 | 525.0727 | 498.2594 | 472.2058 | 403.1533
1674.176 | 524.9644 | 498.2536 | 472.2087 | 403.1522
1675.176 | 525.0138 | 498.2957 | 472.3733 | 402.9527
1676.176 | 524.9507 | 498.3094 | 472.4904 | 402.9795
1677.1917 | 524.9368 | 498.41 | 472.0348 | 403.0405
1678.176 | 524.9035 | 498.278 | 472.3156 | 403.204
1679.176 | 525.0025 | 498.373 | 472.2016 | 403.316
1680.176 | 524.9496 | 498.4003 | 472.1583 | 403.3352
1681.176 | 524.9261 | 498.3559 | 472.4149 | 403.2733
1682.176 | 524.9621 | 498.3156 | 472.4447 | 403.6117
1683.176 | 524.9931 | 498.2059 | 472.3839 | 403.4043
1684.176 | 525.0974 | 498.3064 | 472.5275 | 403.463
1685.176 | 525.1917 | 498.3393 | 472.7503 | 403.405
1686.176 | 525.1964 | 498.3724 | 472.7148 | 403.5719
1687.176 | 525.2053 | 498.4636 | 472.8072 | 403.5252
1688.176 | 525.0943 | 498.4813 | 472.7073 | 403.5445
1689.176 | 525.1607 | 498.4669 | 472.6484 | 403.3917
1690.176 | 525.1505 | 498.4216 | 472.5813 | 403.3381
1691.176 | 525.2248 | 498.4597 | 472.2911 | 403.2784
1692.176 | 525.2742 | 498.3024 | 472.4602 | 404.6178
1693.176 | 525.2037 | 498.3887 | 472.5822 | 419.9565
1694.176 | 525.0825 | 498.5005 | 472.8049 | 420.2871
1695.176 | 525.1267 | 498.5167 | 472.5493 | 420.9805
1696.176 | 525.1991 | 498.4852 | 472.3921 | 421.2848
1697.176 | 525.346 | 498.6198 | 472.7748 | 421.3898
1698.176 | 525.2856 | 498.5852 | 472.6497 | 421.427
1699.176 | 525.3632 | 498.4735 | 472.4736 | 421.5953
1700.176 | 525.4255 | 498.546 | 472.2987 | 421.8639
1701.176 | 525.3827 | 498.6248 | 472.1747 | 421.8319
1702.176 | 525.4831 | 498.621 | 472.2769 | 422.0891
1703.176 | 525.4824 | 498.5438 | 472.2936 | 424.7243
1704.176 | 525.5872 | 498.5703 | 472.0582 | 425.5474
1705.176 | 525.6794 | 498.5482 | 472.0616 | 425.6887
1706.176 | 525.8432 | 498.6978 | 472.061 | 425.4782
1707.176 | 525.8554 | 498.7189 | 472.1188 | 425.4196
1708.176 | 525.8989 | 498.6993 | 472.3577 | 425.8894
1709.176 | 525.9738 | 498.7476 | 472.3753 | 426.1697
1710.176 | 526.017 | 498.8318 | 472.4053 | 426.7829
1711.176 | 526.0159 | 498.8158 | 472.4964 | 426.0128
1712.1917 | 525.8864 | 498.9225 | 472.6375 | 426.6029
1713.176 | 525.84 | 498.8901 | 472.5138 | 426.1555
1714.176 | 525.9376 | 498.9376 | 472.3401 | 426.6779
1715.176 | 525.9831 | 498.8285 | 472.2336 | 427.0447
1716.176 | 526.0957 | 498.9457 | 472.4581 | 427.7529
1717.176 | 526.1424 | 498.988 | 472.4655 | 429.5591
1718.176 | 526.1834 | 498.9546 | 472.075 | 429.4717
1719.176 | 526.1792 | 498.8905 | 471.912 | 429.1491
1720.176 | 526.2717 | 498.9455 | 471.7217 | 429.7204
1721.176 | 526.0668 | 499.0288 | 471.8581 | 429.7603
1722.176 | 526.0447 | 498.9632 | 471.921 | 430.09
1723.176 | 526.1545 | 499.0093 | 471.92 | 430.4629
1724.176 | 526.1287 | 499.1017 | 472.0692 | 430.2079
1725.176 | 526.1935 | 499.0529 | 471.9361 | 430.4381
1726.176 | 526.1834 | 499.1722 | 472.0756 | 430.8201
1727.176 | 526.1674 | 499.208 | 472.4338 | 430.8235
1728.176 | 526.1909 | 499.2664 | 472.1449 | 431.0805
1729.176 | 526.1531 | 499.1269 | 471.9755 | 431.2392
1730.176 | 526.1977 | 499.1711 | 471.9898 | 431.0685
1731.176 | 526.2715 | 499.1829 | 472.0706 | 431.6395
1732.176 | 526.3249 | 499.2427 | 472.2081 | 431.2618
1733.176 | 526.3992 | 499.2657 | 471.9169 | 430.9826
1734.176 | 526.4222 | 499.2508 | 472.0232 | 431.6174
1735.176 | 526.4359 | 499.1759 | 472.1577 | 431.6091
1736.176 | 526.3969 | 499.2463 | 472.1132 | 431.4174
1737.1917 | 526.2347 | 499.3857 | 472.2666 | 429.7589
1738.176 | 526.2384 | 499.4865 | 472.5349 | 411.1616
1739.176 | 526.1329 | 499.6378 | 472.4432 | 396.6828
1740.176 | 526.1712 | 499.6824 | 472.2078 | 396.2967
1741.176 | 526.1016 | 499.7295 | 472.3703 | 392.4697
1742.176 | 526.0816 | 499.8566 | 472.4486 | 392.3848
1743.176 | 526.1359 | 499.9257 | 472.4594 | 392.8818
1744.176 | 526.1474 | 500.0732 | 472.2629 | 393.1856
1745.176 | 526.1229 | 499.9886 | 472.3295 | 393.2065
1746.176 | 526.1634 | 500.0057 | 472.1528 | 393.3794
1747.176 | 526.2572 | 500.0343 | 472.1891 | 393.5508
1748.176 | 526.3143 | 499.9888 | 472.4615 | 393.9705
1749.176 | 526.3795 | 500.0956 | 472.0794 | 393.8645
1750.176 | 526.4336 | 500.0078 | 472.2496 | 397.5071
1751.176 | 526.3959 | 500.1584 | 472.3376 | 397.804
1752.176 | 526.4495 | 500.2538 | 472.5671 | 396.4385
1753.176 | 526.5249 | 500.2012 | 473.0555 | 404.5946
1754.176 | 526.3356 | 500.1231 | 472.9851 | 404.6491
1755.176 | 526.1871 | 500.0943 | 472.908 | 404.8828
1756.176 | 526.212 | 500.1242 | 472.8153 | 405.0603
1757.176 | 526.2049 | 500.1937 | 473.0741 | 404.7704
1758.176 | 526.2407 | 500.0601 | 472.8989 | 405.0435
1759.176 | 526.2608 | 500.0912 | 472.9577 | 406.8113
1760.176 | 526.3488 | 500.1373 | 473.1459 | 406.5988
1761.176 | 526.3782 | 500.1297 | 473.3533 | 406.8573
1762.176 | 526.349 | 500.1403 | 473.3507 | 406.8407
1763.176 | 526.2308 | 500.1253 | 473.1813 | 406.3333
1764.176 | 526.0469 | 500.0916 | 473.1429 | 406.7581
1765.176 | 525.9441 | 500.072 | 473.2295 | 406.2264
1766.176 | 525.8939 | 500.0983 | 473.5957 | 401.5258
1767.176 | 525.9759 | 500.059 | 473.8671 | 407.3405
1768.176 | 525.9308 | 499.9686 | 473.8659 | 400.8475
1769.176 | 525.9595 | 499.9966 | 473.8472 | 407.4274
1770.176 | 526.0631 | 500.0504 | 473.7483 | 407.3145
1771.176 | 526.1764 | 499.9702 | 473.6119 | 407.8162
1772.176 | 526.117 | 500.0496 | 473.8126 | 407.9095
1773.176 | 526.1038 | 500.0029 | 473.6895 | 406.2939
1774.176 | 526.2005 | 499.9187 | 473.7091 | 408.5223
1775.176 | 526.2155 | 499.973 | 473.7024 | 408.753
1776.176 | 526.136 | 499.9898 | 473.8005 | 409.0644
1777.176 | 526.2094 | 499.8649 | 474.0152 | 407.6252
1778.176 | 526.2994 | 499.9268 | 474.1478 | 397.5179
1779.176 | 526.3421 | 499.9746 | 473.9636 | 410.1088
1780.176 | 526.4277 | 499.9057 | 473.6563 | 416.6849
1781.176 | 526.3526 | 499.8869 | 473.5629 | 416.7617
1782.176 | 526.2274 | 499.8031 | 473.4808 | 416.7901
1783.176 | 526.2091 | 499.7953 | 473.4303 | 416.8791
1784.176 | 526.2339 | 499.7526 | 473.5594 | 416.9972
1785.176 | 526.0784 | 499.7121 | 473.8466 | 417.0375
1786.176 | 526.0609 | 499.6345 | 473.813 | 417.2071
1787.176 | 526.1192 | 499.6931 | 473.7888 | 417.2987
1788.176 | 526.1361 | 499.7351 | 473.624 | 417.4131
1789.176 | 526.2694 | 499.6384 | 473.9202 | 417.4085
1790.176 | 526.4345 | 499.683 | 474.0337 | 417.4464
1791.176 | 526.341 | 499.681 | 474.3312 | 417.5299
1792.176 | 526.2432 | 499.6743 | 474.5007 | 417.6141
1793.176 | 526.1617 | 499.7038 | 474.1797 | 417.6009
1794.176 | 526.0099 | 499.6477 | 474.0754 | 417.7241
1795.176 | 525.9838 | 499.5745 | 474.2199 | 417.8364
1796.176 | 525.805 | 499.5701 | 474.2651 | 417.8757
1797.1917 | 525.7256 | 499.5763 | 474.3247 | 417.941
1798.176 | 525.8031 | 499.588 | 474.0642 | 418.0301
1799.176 | 525.9099 | 499.5396 | 473.8598 | 418.1061
1800.176 | 525.9644 | 499.5675 | 473.886 | 418.1358
1801.176 | 526.0593 | 499.6099 | 473.6654 | 418.1835
1802.176 | 526.0136 | 499.5572 | 473.2833 | 418.2818
1803.176 | 526.0431 | 499.4574 | 473.423 | 418.3337
1804.176 | 526.0342 | 499.4812 | 473.9322 | 418.3922
1805.176 | 526.0158 | 499.4755 | 474.0146 | 418.4608
1806.176 | 526.0269 | 499.4889 | 473.8703 | 418.5234
1807.176 | 525.9513 | 499.4926 | 473.8796 | 418.5886
1808.176 | 525.9839 | 499.5624 | 473.9015 | 418.6258
1809.176 | 526.0738 | 499.5652 | 474.1573 | 418.6995
1810.176 | 526.1905 | 499.5135 | 474.3169 | 418.7535
1811.176 | 526.1772 | 499.4131 | 474.1861 | 418.8102
1812.176 | 526.1743 | 499.4862 | 474.2641 | 418.8923
1813.176 | 526.3288 | 499.515 | 474.2291 | 418.963
1814.176 | 526.4323 | 499.2912 | 473.807 | 419.0246
1815.176 | 526.4442 | 499.3182 | 473.6258 | 419.0795
1816.176 | 526.2613 | 499.3988 | 473.4757 | 419.1612
1817.176 | 526.0803 | 499.3832 | 473.943 | 419.1852
1818.176 | 525.7458 | 499.4506 | 474.0554 | 419.2527
1819.176 | 525.6759 | 499.3917 | 474.1372 | 419.3384
1820.176 | 525.6978 | 499.4133 | 474.0256 | 419.3944
1821.176 | 525.7231 | 499.4684 | 474.2522 | 419.4968
1822.176 | 525.68 | 499.5142 | 474.0268 | 419.5804
1823.176 | 525.7813 | 499.4982 | 474.1134 | 419.6456
1824.176 | 525.9177 | 499.4481 | 473.9738 | 419.6484
1825.176 | 526.1035 | 499.3983 | 473.7817 | 419.7028
1826.176 | 526.2943 | 499.2593 | 473.8192 | 419.7727
1827.176 | 526.3654 | 499.1888 | 474.0351 | 419.8401
1828.176 | 526.3989 | 499.1819 | 473.8451 | 419.9343
1829.176 | 526.474 | 499.3199 | 473.8471 | 419.9818
1830.176 | 526.5567 | 499.3903 | 474.0197 | 420.063
1831.176 | 526.5428 | 499.386 | 474.2819 | 420.136
1832.176 | 526.5554 | 499.3739 | 474.2359 | 420.2218
1833.176 | 526.4572 | 499.4053 | 473.9666 | 420.3083
1834.176 | 526.5386 | 499.3883 | 473.7292 | 420.3625
1835.176 | 526.5347 | 499.3169 | 473.8151 | 420.4498
1836.176 | 526.5643 | 499.3387 | 473.7674 | 420.5217
1837.176 | 526.5275 | 499.3577 | 473.9605 | 420.5909
1838.176 | 526.4501 | 499.3981 | 473.8114 | 420.6666
1839.176 | 526.4539 | 499.2841 | 473.6903 | 420.7428
1840.176 | 526.4406 | 499.3812 | 473.9327 | 420.8056
1841.176 | 526.5917 | 499.4322 | 473.558 | 420.857
1842.176 | 526.6664 | 499.3885 | 473.4748 | 420.9312
1843.176 | 526.5529 | 499.3748 | 473.5379 | 420.9645
1844.176 | 526.3969 | 499.3933 | 474.0724 | 421.0262
1845.176 | 526.3218 | 499.3706 | 474.0945 | 421.0988
1846.176 | 526.2408 | 499.3364 | 473.8138 | 421.201
1847.176 | 526.2931 | 499.2968 | 473.9501 | 421.2145
1848.176 | 526.3368 | 499.3043 | 473.8617 | 421.3
1849.176 | 526.2988 | 499.3593 | 473.9482 | 421.3694
1850.176 | 526.0927 | 499.4016 | 474.2809 | 421.4568
1851.176 | 526.1276 | 499.3039 | 474.598 | 421.5066
1852.176 | 526.2006 | 499.2691 | 474.7141 | 421.594
1853.176 | 526.1832 | 499.2677 | 474.5865 | 421.6178
1854.176 | 526.0694 | 499.2855 | 474.4512 | 421.6916
1855.176 | 526.0987 | 499.3171 | 474.4653 | 421.7501
1856.176 | 526.2545 | 499.322 | 474.5153 | 421.8298
1857.176 | 526.184 | 499.2926 | 474.592 | 421.8675
1858.176 | 526.2555 | 499.2466 | 474.625 | 421.9425
1859.176 | 526.1719 | 499.3203 | 474.1858 | 422.0211
1860.176 | 526.2082 | 499.3875 | 474.0959 | 422.0266
1861.176 | 526.2237 | 499.3808 | 473.9711 | 422.035
1862.176 | 526.1952 | 499.359 | 474.0489 | 422.0866
1863.176 | 526.3165 | 499.2969 | 474.3605 | 422.16
1864.176 | 526.1025 | 499.3724 | 474.4501 | 422.224
1865.176 | 525.9483 | 499.3518 | 474.1883 | 422.3028
1866.176 | 525.9231 | 499.4019 | 474.2191 | 422.3009
1867.176 | 525.8819 | 499.4142 | 474.2734 | 422.3846
1868.176 | 525.9047 | 499.3262 | 474.1576 | 422.4767
1869.176 | 525.8275 | 499.2837 | 474.3374 | 422.4972
1870.176 | 525.7755 | 499.305 | 474.3384 | 422.5855
1871.176 | 525.9066 | 499.3686 | 474.1703 | 422.6593
1872.176 | 526.0121 | 499.3101 | 474.2872 | 422.7143
1873.176 | 526.0073 | 499.3048 | 473.9792 | 422.7842
1874.176 | 525.9975 | 499.3374 | 474.0726 | 422.8225
1875.176 | 526.0297 | 499.3715 | 473.8082 | 422.889
1876.176 | 526.1356 | 499.4536 | 473.5568 | 422.9233
1877.176 | 526.1256 | 499.4973 | 473.175 | 422.9656
1878.176 | 526.1481 | 499.5179 | 473.3381 | 422.9917
1879.176 | 526.2153 | 499.5425 | 473.6657 | 423.051
1880.176 | 526.1822 | 499.5147 | 473.8823 | 423.071
1881.176 | 526.0539 | 499.5316 | 474.0726 | 423.1411
1882.176 | 525.9975 | 499.5008 | 473.8113 | 423.1607
1883.176 | 525.8027 | 499.4854 | 473.733 | 423.2067
1884.176 | 525.899 | 499.5052 | 473.9102 | 423.2381
1885.176 | 525.798 | 499.4637 | 474.0419 | 423.2256
1886.176 | 525.6201 | 499.4635 | 474.1 | 423.2456
1887.176 | 525.7826 | 499.4538 | 474.1493 | 423.2913
1888.176 | 525.8893 | 499.4258 | 474.1242 | 423.3311
1889.176 | 525.9895 | 499.4719 | 474.0636 | 423.3654
1890.176 | 526.0135 | 499.3939 | 473.7158 | 423.4505
1891.176 | 526.1098 | 499.394 | 473.3885 | 423.4673
1892.176 | 526.2233 | 499.4105 | 473.6467 | 423.5136
1893.176 | 526.2916 | 499.4787 | 473.6686 | 423.5652
1894.176 | 526.3334 | 499.4781 | 473.7568 | 423.6238
1895.176 | 526.4329 | 499.4539 | 474.0165 | 423.6533
1896.176 | 526.3628 | 499.3968 | 473.9034 | 423.6866
1897.176 | 526.3366 | 499.4713 | 473.6492 | 423.7077
1898.176 | 526.3065 | 499.5029 | 473.6866 | 423.7351
1899.176 | 526.1428 | 499.4481 | 473.8277 | 423.7689
1900.176 | 526.2682 | 499.4851 | 473.8539 | 423.798
1901.176 | 526.3638 | 499.4642 | 473.8556 | 423.8348
1902.176 | 526.1235 | 499.4272 | 473.6529 | 423.8762
1903.176 | 526.1414 | 499.2845 | 473.5335 | 423.9109
1904.176 | 526.0599 | 499.3401 | 473.5353 | 423.9474
1905.176 | 526.0848 | 499.3821 | 473.734 | 423.9924
1906.176 | 526.0258 | 499.3858 | 473.8105 | 424.0153
1907.176 | 525.9711 | 499.4066 | 473.8713 | 424.0397
1908.176 | 525.9141 | 499.3149 | 473.856 | 424.0812
1909.176 | 525.9452 | 499.3706 | 474.0761 | 424.1047
1910.176 | 525.9002 | 499.3639 | 473.6014 | 424.1799
1911.176 | 525.9612 | 499.2856 | 473.499 | 424.2334
1912.176 | 525.8907 | 499.2953 | 473.7611 | 424.2578
1913.176 | 525.7893 | 499.3035 | 473.9864 | 424.3088
1914.176 | 525.7821 | 499.35 | 474.1912 | 424.3334
1915.176 | 525.8551 | 499.3845 | 474.3125 | 424.3693
1916.176 | 525.7997 | 499.2386 | 474.2039 | 424.3981
1917.176 | 525.7972 | 499.2493 | 474.2833 | 424.4384
1918.176 | 525.7395 | 499.249 | 473.9505 | 424.4753
1919.176 | 525.5439 | 499.2162 | 473.9988 | 424.5248
1920.176 | 525.5317 | 499.2771 | 473.7338 | 424.5824
1921.176 | 525.4106 | 499.34 | 473.8627 | 424.5849
1922.176 | 525.4419 | 499.3428 | 473.8369 | 424.6198
1923.176 | 525.3386 | 499.367 | 473.6319 | 424.6236
1924.176 | 525.3834 | 499.43 | 473.7006 | 424.6356
1925.176 | 525.4359 | 499.5142 | 473.8586 | 424.6713
1926.176 | 525.4987 | 499.423 | 473.8335 | 424.6949
1927.176 | 525.5347 | 499.3318 | 473.7341 | 424.7232
1928.176 | 525.4213 | 499.4328 | 473.5928 | 424.7528
1929.176 | 525.3904 | 499.4527 | 473.9053 | 424.7782
1930.176 | 525.311 | 499.4509 | 473.8029 | 424.8205
1931.176 | 525.2955 | 499.4724 | 473.5613 | 424.8144
1932.176 | 525.177 | 499.5153 | 473.5037 | 424.8737
1933.176 | 525.043 | 499.5859 | 473.7621 | 424.8986
1934.176 | 524.99 | 499.4623 | 473.5732 | 424.9209
1935.176 | 525.0077 | 499.5152 | 473.5435 | 424.9575
1936.176 | 524.9096 | 499.5854 | 473.9231 | 424.9547
1937.176 | 524.8694 | 499.5906 | 474.0342 | 424.9973
1938.176 | 524.8489 | 499.5337 | 474.1892 | 425.0311
1939.176 | 524.906 | 499.5939 | 474.2818 | 425.049
1940.176 | 524.9645 | 499.6222 | 473.9757 | 425.0694
1941.176 | 525.149 | 499.4651 | 473.8783 | 425.0994
1942.176 | 525.2343 | 499.5377 | 473.7996 | 425.1236
1943.176 | 525.3292 | 499.6089 | 473.8578 | 425.102
1944.176 | 525.3324 | 499.6216 | 473.9437 | 425.1375
1945.176 | 525.3877 | 499.594 | 473.8847 | 425.1463
1946.176 | 525.38 | 499.6572 | 474.0392 | 425.2021
1947.176 | 525.286 | 499.6428 | 473.9341 | 425.2363
1948.176 | 525.2069 | 499.4793 | 474.0497 | 425.2302
1949.176 | 525.0498 | 499.5474 | 473.6675 | 425.2753
1950.176 | 525.1646 | 499.5994 | 473.2564 | 425.3371
1951.176 | 525.1298 | 499.502 | 473.5386 | 425.3557
1952.176 | 525.0765 | 499.4902 | 473.6298 | 425.413
1953.176 | 524.9949 | 499.4443 | 473.4171 | 425.4338
1954.176 | 525.1193 | 499.5553 | 473.4166 | 425.439
1955.176 | 525.1966 | 499.6162 | 473.4055 | 425.5157
1956.176 | 525.2321 | 499.6746 | 473.4988 | 425.514
1957.176 | 525.3912 | 499.699 | 473.2442 | 425.5782
1958.176 | 525.4288 | 499.7066 | 473.1986 | 425.5961
1959.176 | 525.4693 | 499.4942 | 472.9407 | 425.6484
1960.176 | 525.535 | 499.4706 | 472.7623 | 425.6852
1961.176 | 525.5406 | 499.5964 | 473.3301 | 425.689
1962.176 | 525.5691 | 499.7706 | 473.8048 | 425.7415
1963.176 | 525.4965 | 499.8478 | 473.9544 | 425.7698
1964.176 | 525.6223 | 499.8626 | 473.8153 | 425.8004
1965.176 | 525.7002 | 499.9126 | 473.6707 | 425.7768
1966.176 | 525.808 | 499.8528 | 473.5192 | 425.8169
1967.176 | 525.7812 | 499.8573 | 473.3512 | 425.8837
1968.176 | 525.8316 | 499.837 | 473.3742 | 425.9266
1969.176 | 525.6675 | 499.8266 | 473.2902 | 425.9757
1970.176 | 525.7092 | 499.9032 | 473.581 | 426.0048
1971.176 | 525.6725 | 499.9307 | 473.8215 | 426.0255
1972.176 | 525.7424 | 499.8771 | 474.0411 | 426.0595
1973.176 | 525.6969 | 499.8794 | 473.9944 | 426.1126
1974.176 | 525.6597 | 499.9657 | 473.7264 | 426.1399
1975.176 | 525.7815 | 499.914 | 473.8095 | 426.1757
1976.176 | 525.8546 | 499.8952 | 474.0478 | 426.2044
1977.176 | 525.8218 | 499.9675 | 473.9622 | 426.2547
1978.176 | 525.8311 | 499.9935 | 473.7075 | 426.3305
1979.176 | 525.8881 | 499.9665 | 473.712 | 426.3391
1980.176 | 525.8119 | 500.017 | 473.5659 | 426.3603